## Front
Hello world
Expanding NSW-QLD transmission transfer capacity
Inputs and Methodology Assumptions Workbook
December 2018

## Table of Contents
Table of Contents
| Worksheet Name | Worksheet Heading | Description | Source
| Scenarios | Scenarios | Scenario Overview | Inputs and Methodology Consulation Report
| Renewable Energy Zones | Renewable Energy Zones | Geographical map of the Renewable Energy Zones | AEMO 2018 ISP Assumptions Workbook
| Energy forecasts | Annual energy (GWh per annum sent out) | Annual operational energy forecast for each region for each scenario | AEMO Electricity Statement of Opportunities 2018
| Peak demand forecasts | Peak demand (MW) | 10% PoE and 50%PoE maximum regional demand forecast | AEMO Electricity Statement of Opportunities 2018
| Rooftop PV forecast | Rooftop PV installed capacity forecast (MW) | Regional Rooftop PV Installed Capacity forecast | AEMO Electricity Statement of Opportunities 2018
| Battery storage uptake | Behind-the-meter storage uptake (MWh) | Regional behind-the-meter storage uptake | AEMO Electricity Statement of Opportunities 2018
| EV demand forecast | Electric vehicles demand projections (GWh) | Regional electric vehicles demand projections | AEMO Electricity Statement of Opportunities 2018
| DSP | Demand-side participation (MW) | Electricity demand that will be removed from the market when modelled prices reach specified limits | AEMO 2018 ISP Assumptions Workbook
| Effective LRET | Large-scale Renewable Energy Target (LRET) | Large-scale renewable energy target including several adjustments | AEMO 2018 ISP Assumptions Workbook
| VRET | Victorian Renewable Energy Target (VRET) | Capacity target to meet VRET | AEMO 2018 ISP Assumptions Workbook
| QRET | Queensland Renewable Energy Target (QRET) | Renewable energy target to meet QRET | AEMO 2018 ISP Assumptions Workbook
| Emission Trajectory | Emissions target trajectories | Emission costraints that represents Australia's potential Paris commitment | AEMO 2018 ISP Assumptions Workbook
| Financial assumptions | Weighted average cost of capital (WACC) | WACC, Discount Rates, Value of Customer Reliability | AER Determinations
| Build cost | Build cost ($/kW) real June 2018 dollars | Cost to construct new generation excluding connection costs. | AEMO 2018 ISP Assumptions Workbook
| Refurbishment | Refurbishment | Refurbishment costs from the 2018 ISP are scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase. | AEMO 2018 ISP Assumptions Workbook
| Retirement | Retirement | Announced Retirement, End-of-Life, and Retirement Cost | 2018 AEMO ISP, AEMO generation information page, AGL announcements
| Gas prices | Gas prices ($/GJ) real June 2018 dollars | Forecast gas prices | AEMO 2018 ISP Assumptions Workbook
| Coal prices | Coal prices ($/GJ) real June 2018 dollars | Forecast coal prices | AEMO 2018 ISP Assumptions Workbook
| Fixed OPEX | Fixed operating cost ($/kW/year) real June 2018 dollars | Power stations' fixed operation and maintenance cost | AEMO 2018 ISP Assumptions Workbook
| Variable OPEX | Variable operating cost ($/MWh) real June 2018 dollars | Power stations' variable operation and maintenance cost | AEMO 2018 ISP Assumptions Workbook
| Connection cost | Initial connection costs ($/kW) real June 2018 dollars | Additional build cost that represents proximity to existing network | AEMO 2018 ISP Assumptions Workbook
| Lead time | Lead time (years) | Amount of time from start of simulation before specific technologies that are not already committed/advanced can first be built. | AEMO 2018 ISP Assumptions Workbook
| Storage properties | Storage properties | Relevant properties of pump hydro and battery storage | AEMO 2018 ISP Assumptions Workbook
| Hydro storage inflows | Hydro storage inflows (GWh) | Reservoir inflows | AEMO 2018 ISP Assumptions Workbook
| Storage initial level | Storage initial level | Reservoir initial volume and capacities | AEMO 2018 ISP Assumptions Workbook
| Interconnector capability | Interconnector capability (MW) | Existing notional interconnector limits for Long-term Investment Planning | AEMO 2018 ISP Assumptions Workbook
| Proportioning factors | Proportioning factors for Inter-Regional losses | Distribution of inter-connector lossess between adjacent regions | Regions and Marginal Loss Factors: FY 2018-19
| Augmentation options | Augmentation options | QNI augmentation options | TransGrid and Powerlink's Expanding NSW-QLD transmission transfer capacity - Project Specification Consultation Report
| Transmission limits | Transmission limits | Intra-regional capacity considerations. | AEMO Electricity Statement of Opportunities 2018
| Generator capacity | Generator capacity | Maximum capacity is used to report capacity factors and calculate fixed operating costs. It may not correspond to "installed capacity" listed in Generation Information workbooks, when maximum seasonal ratings differ. Generator capacity may vary with weather conditions. The ISP uses AEMO Generation Information page (2017 December release) for seasonal ratings for the first 10 years of the model period. Not all committed or advanced projects have ratings listed in Generation Information. Where information is absent Maximum Capacity is used. This will be updated with the most recent information from the AEMO Generation Information Page. | AEMO Generation Information November 2018
| Generation limits | Generator modelling assumptions | Generator minimum capacities, minimum and maximum capacity factors | AEMO 2018 ISP Assumptions Workbook
| Generator reliability settings | Generator reliability settings | Generator technology forced outage parameters | AEMO Electricity Statement of Opportunities 2018
| Maintenance | Maintenance rate | Generator technology maintenance outage parameters | AEMO 2018 ISP Assumptions Workbook
| Heat rates | Heat rates | Generator heatrates | AEMO 2018 ISP Assumptions Workbook
| Auxiliary | Auxiliary load | Generator auxiliary load | AEMO 2018 ISP Assumptions Workbook
| Emissions | Emissions | Generator emission rates | AEMO 2018 ISP Assumptions Workbook
| MLF | Marginal Loss Factors (MLFs) | Generator marginal loss factors | Regions and Marginal Loss Factors: FY 2018-19
|  |  | Hyperlinks | Can modify to local path
|  |  | AEMO 2018 ISP Assumptions Workbook | https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/ISP/2018/2018-Integrated-System-Plan--Modelling-Assumptions.xlsx
|  |  | AEMO Electricity Statement of Opportunities 2018 | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/NEM-Electricity-Statement-of-Opportunities
|  |  | Regions and Marginal Loss Factors: FY 2018-19 | https://www.aemo.com.au/-/media/Files/Electricity/NEM/Security_and_Reliability/Loss_Factors_and_Regional_Boundaries/2018/Marginal-Loss-Factors-for-the-2018-19-Financial-Year---updated-11-July-2018.pdf
|  |  | TransGrid and Powerlink's Expanding NSW-QLD transmission transfer capacity - Project Specification Consultation Report | https://www.powerlink.com.au/sites/default/files/2018-11/Project%20Specification%20Consultation%20Report%20-%20Expanding%20NSW%20Qld%20Transmission%20Transfer%20Capacity.pdf
|  |  | AEMO Generation Information November 2018 | http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information

## Scenarios
TOC
Scenarios
| Assumptions | Fast change scenario | Neutral scenario with proportionate share of emissions reduction target | Neutral scenario with stronger share of emissions reduction target | Slow change scenario
Consumption forecast and consumer behaviour
| Underlying consumption | 2018 AEMO ESOO Strong | 2018 AEMO ESOO Neutral | 2018 AEMO ESOO Neutral | 2018 AEMO ESOO Weak
| Rooftop photo-voltaic (PV) penetration | 2018 AEMO ESOO Neutral
| Small-scale battery penetration and charging and discharging pattern | 2018 AEMO ESOO Neutral
| Demand-side participation (DSP) | 2018 AEMO ISP Weak | 2018 AEMO ISP Neutral | 2018 AEMO ISP Neutral | 2018 AEMO ISP Strong
| Electric vehicles | 2018 AEMO ESOO Strong | 2018 AEMO ESOO Neutral | 2018 AEMO ESOO Neutral | 2018 AEMO ESOO Weak
| Value of customer reliability (VCR) | Aggregate NEM wide value of $33,460/MWh
Generation technology cost projections
| New entrant capital costs | 2018 AEMO ISP Rapid (for applicable technology) | 2018 AEMO ISP Neutral | 2018 AEMO ISP Neutral | 2018 AEMO ISP Slow (for applicable technology)
| Coal plant retirements | Half of coal power stations’ capacity is retired 5 years earlier than end-of-technical-lives | Retired by announced retirement date or end-of-technical-lives | Half of coal power stations’ capacity is retired 2 years earlier than end-of-technical-lives | Half of coal power stations’ capacity is retired 5 years later than end-of-technical-lives
Fuel supply forecast
| Coal fuel cost | 2018 AEMO ISP Coal Price
| Gas fuel cost | 2018 AEMO ISP Strong | 2018 AEMO ISP Neutral | 2018 AEMO ISP Neutral | 2018 AEMO ISP Weak
Climate and energy policies
| LRET | 33 TWh by 2020 to 2030 or a penalty of $92.86 for every MWh of violation (including GreenPower and ACT scheme).
| Paris commitment | 52 % 2005 - 2030 90 % 2005 - 2050 | 28 % 2005 - 2030 70 % 2016 - 2050 | 52 % 2005 - 2030 90 % 2005 - 2050 | 28 % 2005 - 2030 70 % 2016 - 2050
| VRET | 25 % by 2020 40 % by 2025 50 % by 2030
| QRET | 50 % by 2030
Industry developments
| South Australia Energy Transformation RIT-T | The proposed SA to NSW interconnector is assumed constructed by 2023 and the timing will be tested as a sensitivity
| Victoria to NSW Interconnector Upgrade | The preferred option is assumed constructed by 2020 and the timing will be tested as a sensitivity
| Western Victoria Renewable Integration RIT-T | The preferred option is assumed constructed by 2023 and the timing will be tested as a sensitivity
| MarinusLink and Battery of the Nation | The preferred option is assumed constructed by 2033 and the timing will be tested as a sensitivity | Excluded
| Snowy 2.0, SnowyLink North, and SnowyLink South | Snowy 2.0 generation and SnowyLink North will be included by 2025 and the timing will be tested as a sensitivity SnowyLink South will be included by 2034 and the timing will be tested as a sensitivity

## Renewable Energy Zones
TOC
Renewable Energy Zones
Source: AEMO 2018 ISP Assumptions Workbook
As used in the AEMO 2018 ISP
| REZ ID | Name | NEM Region | NEM Zone
| 0 | Far North QLD | Qld | NQ
| 1 | North Qld Clean Energy Hub | Qld | NQ
| 2 | Northern Qld | Qld | NQ
| 3 | Barcaldine | Qld | CQ
| 4 | Isaac | Qld | NQ
| 5 | Fitzroy | Qld | CQ
| 6 | Darling Downs | Qld | SWQ
| 7 | North West NSW | NSW | NNS
| 8 | Northern NSW Tablelands | NSW | NNS
| 9 | Central NSW Tablelands | NSW | NCEN
| 10 | Central West NSW | NSW | NCEN
| 11 | Southern NSW Tablelands | NSW | CAN
| 12 | Broken Hill | NSW | SWNSW
| 13 | Murray River (NSW) | NSW | SWNSW
| 13 | Murray River (Vic) | Vic | NVIC
| 14 | Western Victoria | Vic | CVIC
| 15 | Moyne | Vic | MEL
| 16 | Gippsland | Vic | LV
| 17 | South East SA | SA | SESA
| 18 | Riverland (SA) | SA | NSA
| 18 | Riverland (NSW) | NSW | SWNSW
| 19 | Mid-North SA | SA | NSA
| 20 | Yorke Peninsula | SA | NSA
| 21 | Northern SA | SA | NSA
| 22 | Leigh Creek | SA | NSA
| 23 | Roxby Downs | SA | NSA
| 24 | Eastern Eyre Peninsula | SA | NSA
| 25 | Western Eyre Peninsula | SA | NSA
| 26 | King island | Tas | TAS
| 27 | North East Tasmania | Tas | TAS
| 28 | North West Tasmania | Tas | TAS
| 29 | Tasmania Midlands | Tas | TAS
| 30 | New England | NSW | NNS
| 31 | Tumut | NSW | CAN
| 32 | Cooma-Monaro | NSW | CAN
| 33 | Ovens Murray | Vic | NVIC

## Energy forecasts
TOC
Annual energy (GWh per annum sent out)
| Source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
Targets shown are 'Operational, sent-out'
| Fast: | To be used in Fast change scenario
| Neutral: | To be used in Neutral scenario with proportionate share of emissions reduction target and Neutral scenario with stronger share of emissions reduction target
| Slow: | To be used in Slow change scenario
| Scenario and Region | AEMO forecast | [18 empty] | Extrapolated
| Operational energy (GWh p.a. sent-out) | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Historical profile | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12
| Fast QLD | 49904 | 49951 | 50190 | 50457 | 50615 | 51382 | 51666 | 53583 | 54013 | 54459 | 54910 | 55236 | 55615 | 55532 | 55777 | 55996 | 56427 | 56975 | 57533 | 58151.5258 | 58872.3157 | 59556.9973 | 59605.6806 | 59663.5852 | 59780.0941 | 59813.4311
| Fast NSW | 66413 | 66371 | 66352 | 66873 | 67222 | 68330 | 69604 | 70990 | 72557 | 74127 | 75842 | 77602 | 78953 | 80635 | 82247 | 83686 | 85279 | 87159 | 89008 | 90913.7187 | 92909.931 | 93981.2138 | 95085.1818 | 96193.7222 | 97336.6074 | 98427.6793
| Fast VIC | 43666 | 44091 | 44773 | 45570 | 45946 | 47092 | 47794 | 49025 | 50411 | 51875 | 53354 | 54802 | 56080 | 57481 | 58824 | 60037 | 61388 | 62882 | 64341 | 65923.8849 | 66789.9744 | 67638.1722 | 68500.6596 | 69367.9113 | 70251.1818 | 71120.0002
| Fast SA | 11895 | 11913 | 12372 | 12451 | 12433 | 12588 | 12634 | 12782 | 12945 | 13142 | 13319 | 13508 | 13650 | 13825 | 13863 | 13995 | 14140 | 14369 | 14606 | 14834.1961 | 15073.1895 | 15314.9436 | 15575.2813 | 15648.4928 | 15728.6363 | 15801.1557
| Fast TAS | 10449 | 10538 | 10648 | 10717 | 10756 | 10836 | 10825 | 10943 | 11067 | 11171 | 11222 | 11335 | 11468 | 11606 | 11743 | 11862 | 12003 | 12168 | 12339 | 12500.907 | 12680.9683 | 12832.254 | 13002.0165 | 13174.7314 | 13366.2729 | 13529.7389
| Neutral QLD | 49363 | 49334 | 49622 | 49912 | 50202 | 50407 | 50388 | 50304 | 50415 | 50542 | 50738 | 50935 | 51030 | 51072 | 51085 | 51039 | 51156 | 51340 | 51514 | 51758.4632 | 52080.8636 | 52351.9171 | 52708.2048 | 53109.1175 | 53602.6661 | 54059.6464
| Neutral NSW | 66441 | 66505 | 66662 | 66267 | 66557 | 67238 | 68010 | 68803 | 69645 | 70594 | 71738 | 72947 | 73952 | 74826 | 75824 | 76637 | 77534 | 78686 | 79796 | 80970.2641 | 82215.0588 | 83449.2433 | 84760.5454 | 86124.2783 | 87572.106 | 89023.2752
| Neutral VIC | 43184 | 43468 | 43995 | 44145 | 44552 | 45294 | 45264 | 45298 | 46051 | 46738 | 47474 | 48299 | 49150 | 50038 | 50846 | 51515 | 52265 | 53139 | 53958 | 54897.3233 | 55886.6481 | 56897.8882 | 57965.5476 | 59082.557 | 60262.767 | 60753.4882
| Neutral SA | 11834 | 11826 | 12210 | 12167 | 12184 | 12248 | 12032 | 11839 | 11856 | 11860 | 11895 | 11990 | 12001 | 12055 | 11960 | 11967 | 11993 | 12078 | 12167 | 12249.7887 | 12338.9478 | 12426.6749 | 12528.5479 | 12640.3766 | 12767.8642 | 12896.9418
| Neutral TAS | 10412 | 10474 | 10546 | 10429 | 10460 | 10510 | 10417 | 10343 | 10388 | 10401 | 10368 | 10383 | 10439 | 10498 | 10550 | 10594 | 10643 | 10712 | 10784 | 10853.0527 | 10938.8557 | 10995.2774 | 11068.6373 | 11143.6255 | 11235.7514 | 11298.8946
| Slow QLD | 48546 | 48012 | 47812 | 47840 | 47287 | 46820 | 45908 | 45402 | 44887 | 36795 | 36319 | 35325 | 35286 | 34890 | 34818 | 34762 | 34723 | 34840 | 34921 | 35086.6064 | 35306.2145 | 35509.742 | 35774.0108 | 36077.9308 | 36449.3652 | 36818.2381
| Slow NSW | 65877 | 66091 | 66081 | 66270 | 65080 | 65458 | 65861 | 66212 | 66510 | 63883 | 60896 | 57913 | 56792 | 56709 | 57159 | 57542 | 57979 | 58655 | 59295 | 60012.7788 | 60774.5341 | 61571.3272 | 62418.3583 | 63314.8824 | 64268.2548 | 65269.8819
| Slow VIC | 43250 | 43513 | 41686 | 39370 | 38462 | 38950 | 38550 | 38506 | 38877 | 39229 | 39135 | 38457 | 37922 | 38405 | 38875 | 39298 | 39717 | 40327 | 40884 | 41547.2374 | 42247.1263 | 42984.8617 | 43765.1742 | 44590.565 | 45464.758 | 46389.2419
| Slow SA | 11509 | 11481 | 11846 | 11665 | 11367 | 11369 | 11089 | 10895 | 10820 | 10761 | 10576 | 10287 | 9851 | 9770 | 9580 | 9521 | 9460 | 9474 | 9492 | 9499.3376 | 9512.2542 | 9523.4886 | 9548.5791 | 9583.2939 | 9633.2927 | 9684.4603
| Slow TAS | 9967 | 9995 | 10026 | 9911 | 9736 | 9729 | 8950 | 8941 | 8925 | 8907 | 8741 | 8457 | 8160 | 8059 | 8045 | 7905 | 7880 | 7885 | 7893 | 7988.5183 | 8098.5765 | 8182.638 | 8281.384 | 8381.3532 | 8496.1576 | 8585.2665

## Peak demand forecasts
TOC
Peak demand (MW)
| Source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
Targets shown are 'Operational, sent-out'
| Fast: | To be used in Fast change scenario
| Neutral: | To be used in Neutral scenario with proportionate share of emissions reduction target and Neutral scenario with stronger share of emissions reduction target
| Slow: | To be used in Slow change scenario
| Scenario and Region | AEMO forecast | [18 empty] | Extrapolated
| Operational Annual peak demand (MW) 10% POE | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Fast QLD | 9117 | 9161 | 9132 | 9189 | 9246 | 9365 | 9399 | 9676 | 9765 | 9898 | 10090 | 10218 | 10360 | 10476 | 10582 | 10795 | 10924 | 11110 | 11231 | 11170 | 11157 | 11191 | 11198 | 11202 | 11178 | 11201
| Fast NSW | 13980 | 14078 | 14172 | 14365 | 14551 | 14676 | 14952 | 15217 | 15604 | 15865 | 16278 | 16499 | 16720 | 17066 | 17295 | 17634 | 17885 | 18183 | 18301 | 18449 | 18577 | 18801 | 18975 | 19146 | 19261 | 19473
| Fast VIC | 9830 | 9938 | 10092 | 10169 | 10302 | 10601 | 10753 | 10990 | 11137 | 11392 | 11764 | 11989 | 12253 | 12537 | 12830 | 13214 | 13373 | 13712 | 13851 | 14000 | 14099 | 14270 | 14403 | 14533 | 14621 | 14780
| Fast SA | 3200 | 3216 | 3273 | 3296 | 3303 | 3362 | 3351 | 3460 | 3509 | 3513 | 3597 | 3714 | 3741 | 3778 | 3800 | 3822 | 3882 | 3961 | 4040 | 4030 | 4039 | 4068 | 4086 | 4104 | 4111 | 4138
| Fast TAS | 1732 | 1746 | 1758 | 1772 | 1786 | 1799 | 1800 | 1819 | 1844 | 1866 | 1880 | 1898 | 1922 | 1940 | 1965 | 1987 | 2011 | 2033 | 2093 | 2118 | 2139 | 2168 | 2192 | 2217 | 2238 | 2267
| Neutral QLD | 9076 | 9006 | 9080 | 9091 | 9103 | 9246 | 9161 | 9249 | 9287 | 9323 | 9438 | 9572 | 9692 | 9767 | 9874 | 9962 | 10109 | 10183 | 10258 | 10269 | 10262 | 10304 | 10320 | 10336 | 10325 | 10363
| Neutral NSW | 13975 | 13994 | 14202 | 14260 | 14454 | 14579 | 14644 | 14938 | 15062 | 15357 | 15500 | 15693 | 15972 | 16147 | 16291 | 16536 | 16656 | 16804 | 16965 | 17149.7695 | 17237.3055 | 17424.6703 | 17563.1933 | 17702.6725 | 17791.6205 | 17985.1606
| Neutral VIC | 9721 | 9791 | 9965 | 9959 | 10084 | 10278 | 10318 | 10277 | 10455 | 10567 | 10764 | 10962 | 11234 | 11293 | 11554 | 11752 | 12002 | 12106 | 12126 | 12327.8084 | 12392.8709 | 12535.6112 | 12640.7909 | 12747.1102 | 12814.5102 | 12963.9554
| Neutral SA | 3170 | 3185 | 3259 | 3228 | 3265 | 3292 | 3289 | 3272 | 3309 | 3326 | 3352 | 3406 | 3470 | 3490 | 3482 | 3492 | 3524 | 3593 | 3639 | 3626.3187 | 3623.3647 | 3641.4989 | 3649.2295 | 3657.0853 | 3654.43 | 3673.2592
| Neutral TAS | 1723 | 1734 | 1747 | 1729 | 1737 | 1749 | 1737 | 1730 | 1742 | 1746 | 1750 | 1752 | 1767 | 1776 | 1784 | 1794 | 1808 | 1816 | 1858 | 1869 | 1876 | 1890 | 1901 | 1912 | 1919 | 1933
| Slow QLD | 8944 | 8888 | 8855 | 8874 | 8765 | 8752 | 8656 | 8632 | 8602 | 7441 | 7413 | 7387 | 7440 | 7441 | 7518 | 7556 | 7682 | 7778 | 7840 | 7895 | 7907 | 7960 | 7984 | 8007 | 8005 | 8032
| Slow NSW | 13976 | 14048 | 14124 | 14201 | 14206 | 14228 | 14212 | 14469 | 14590 | 14394 | 13812 | 13466 | 13342 | 13534 | 13671 | 13792 | 13777 | 13889 | 14028 | 14170 | 14191 | 14262 | 14250 | 14232 | 14163 | 14170
| Slow VIC | 9734 | 9766 | 9485 | 9255 | 9208 | 9355 | 9390 | 9286 | 9330 | 9444 | 9560 | 9473 | 9496 | 9625 | 9647 | 9897 | 10024 | 10100 | 10145 | 10276 | 10284 | 10335 | 10315 | 10285 | 10210 | 10189
| Slow SA | 3118 | 3160 | 3182 | 3183 | 3133 | 3179 | 3128 | 3117 | 3121 | 3117 | 3153 | 3128 | 3115 | 3114 | 3066 | 3105 | 3136 | 3164 | 3209 | 3187 | 3168 | 3167 | 3150 | 3132 | 3104 | 3094
| Slow TAS | 1660 | 1663 | 1668 | 1651 | 1628 | 1629 | 1516 | 1520 | 1524 | 1523 | 1505 | 1468 | 1424 | 1406 | 1410 | 1393 | 1392 | 1392 | 1430 | 1422 | 1412 | 1406 | 1398 | 1391 | 1381 | 1376
| Scenario and Region | AEMO forecast 2019-20: AEMO forecast; Extrapolated 2038-39: Extrapolated
| Operational Annual peak demand (MW) 50% POE | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Fast QLD | 8622 | 8623 | 8662 | 8718 | 8757 | 8886 | 8939 | 9223 | 9340 | 9501 | 9668 | 9793 | 9963 | 10045 | 10191 | 10346 | 10485 | 10662 | 10773 | 10753.8963 | 10743.0305 | 10777.3305 | 10785.8465 | 10792.0039 | 10771.1232 | 10795.7262
| Fast NSW | 12319.6161 | 12398.8227 | 12451.4755 | 12529.1549 | 12631.3633 | 12875.9659 | 13170.6784 | 13444.4055 | 13656.9914 | 13819.6111 | 14213.5426 | 14452.6397 | 14723.5281 | 15052.8347 | 15212.3026 | 15505.6661 | 15747.0563 | 16012.2718 | 16232.0876 | 16367.3855 | 16468.1211 | 16651.732 | 16791.3407 | 16928.3849 | 17017.3184 | 17188.6644
| Fast VIC | 9107 | 9198 | 9278 | 9483 | 9609 | 9849 | 9971 | 10178 | 10419 | 10676 | 11016 | 11274 | 11450 | 11769 | 12094 | 12388 | 12587 | 12868 | 13032 | 13137.5537 | 13225.1964 | 13379.907 | 13499.3818 | 13616.5875 | 13694.3069 | 13838.2922
| Fast SA | 2891 | 2924 | 2970 | 3012 | 3028 | 3080 | 3084 | 3143 | 3174 | 3256 | 3303 | 3358 | 3407 | 3455 | 3495 | 3542 | 3581 | 3641 | 3700 | 3684.6039 | 3691.6961 | 3717.5299 | 3733.5348 | 3749.147 | 3754.3319 | 3778.4081
| Fast TAS | 1695 | 1709 | 1724 | 1734 | 1745 | 1761 | 1762 | 1782 | 1805 | 1825 | 1840 | 1860 | 1879 | 1902 | 1925 | 1947 | 1971 | 1994 | 2053.7808 | 2078.0729 | 2098.4293 | 2126.4024 | 2150.5671 | 2174.7318 | 2194.8143 | 2222.9763
| Neutral QLD | 8531 | 8513 | 8554 | 8626 | 8663 | 8710 | 8742 | 8788 | 8857 | 8943 | 9037 | 9145 | 9257 | 9347 | 9454 | 9561 | 9662 | 9762 | 9835 | 9841.9651 | 9835.6372 | 9875.839 | 9891.8151 | 9907.551 | 9897.9808 | 9934.2186
| Neutral NSW | 12322.4126 | 12346.2209 | 12400.3173 | 12442.3526 | 12545.913 | 12733.1937 | 12770.1529 | 12986.9279 | 13172.0349 | 13297.9351 | 13502.0129 | 13692.1622 | 13986.8005 | 14083.4345 | 14265.1088 | 14423.1408 | 14587.8468 | 14739.0852 | 14869.5284 | 15068.9482 | 15134.904 | 15283.1623 | 15391.7446 | 15500.6219 | 15566.9661 | 15713.9508
| Neutral VIC | 8997 | 9009 | 9221 | 9249 | 9330 | 9519 | 9480 | 9499 | 9679 | 9856 | 10009 | 10164 | 10413 | 10522 | 10770 | 10977 | 11144 | 11290 | 11371 | 11485.8403 | 11534.7635 | 11647.9783 | 11730.1886 | 11812.3989 | 11861.1364 | 11971.6022
| Neutral SA | 2893 | 2895 | 2954 | 2951 | 2978 | 2997 | 2985 | 2968 | 3004 | 3044 | 3046 | 3096 | 3117 | 3155 | 3174 | 3200 | 3250 | 3249 | 3305 | 3297.1219 | 3293.771 | 3308.2549 | 3313.9967 | 3319.5632 | 3316.0826 | 3330.3456
| Neutral TAS | 1687 | 1697 | 1707 | 1692 | 1700 | 1710 | 1699 | 1691 | 1703 | 1710 | 1712 | 1717 | 1729 | 1736 | 1747 | 1757 | 1768 | 1780 | 1824.8082 | 1835.2149 | 1842.3166 | 1855.9527 | 1866.435 | 1876.8417 | 1883.9751 | 1897.8062
| Slow QLD | 8444 | 8373 | 8333 | 8403 | 8342 | 8321 | 8213 | 8201 | 8189 | 7050 | 7045 | 6966 | 7002 | 7031 | 7105 | 7175 | 7265 | 7349 | 7408 | 7467.7724 | 7479.2855 | 7528.8158 | 7552.2605 | 7573.4534 | 7572.4846 | 7598.79
| Slow NSW | 12258.9462 | 12304.6446 | 12418.0659 | 12489.1387 | 12298.6886 | 12364.3224 | 12474.8309 | 12567.9968 | 12694.3251 | 12291.8319 | 11960.7895 | 11540.4026 | 11466.7883 | 11511.7789 | 11592.8187 | 11656.3361 | 11705.9245 | 11884.1913 | 12061.2263 | 12094.1488 | 12109.8501 | 12165.608 | 12146.3039 | 12121.2066 | 12051.6296 | 12046.3918
| Slow VIC | 9027 | 9034 | 8790 | 8583 | 8506 | 8589 | 8522 | 8557 | 8600 | 8737 | 8757 | 8664 | 8694 | 8809 | 8924 | 9122 | 9229 | 9315 | 9382 | 9425.6721 | 9432.69 | 9479.2021 | 9460.514 | 9432.5022 | 9363.3484 | 9343.263
| Slow SA | 2846 | 2837 | 2883 | 2879 | 2857 | 2882 | 2834 | 2813 | 2839 | 2850 | 2841 | 2833 | 2788 | 2800 | 2804 | 2830 | 2833 | 2874 | 2905 | 2880.6983 | 2863.4324 | 2861.9395 | 2846.1115 | 2828.8679 | 2803.281 | 2793.5911
| Slow TAS | 1620 | 1625 | 1629 | 1613 | 1591 | 1594 | 1480 | 1481 | 1485 | 1487 | 1469 | 1430 | 1388 | 1373 | 1372 | 1355 | 1355 | 1356 | 1392.8539 | 1384.8259 | 1374.8042 | 1369.293 | 1361.4163 | 1353.5348 | 1343.927 | 1338.6037

## Rooftop PV forecast
TOC
Rooftop PV installed capacity forecast (MW)
| Source: AEMO Electricity Statement of Opportunities 2018 |  |  |  | AEMO's forecasting data portal
| 2018 CSIRO Moderate: | AEMO's ESOO 2018 CSIRO Moderate rooftop PV uptake is used in AEMO's Neutral, Fast change and Slow change ESOO 2018 demand scenarios. Non-scheduled PV between 100kW - 30MW will be modelled explicitly.
| Capacity (MW) | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| QLD | 3002.69 | 3065.32 | 3129.74 | 3196.04 | 3264.28 | 3334.58 | 3524.5 | 3680.53 | 3844.17 | 4017.61 | 4198.62 | 4389.04 | 4623.18 | 4870.17 | 5143.75 | 5503.25 | 5642.13 | 5783.42 | 5928.38 | 6079.76 | 6231.53 | 6386.91 | 6543.54 | 6702.5 | 6864.08 | 7038.29 | 7699 | 7765 | 7826 | 7883 | 7935 | 7983 | 8027 | 8066 | 8102 | 8134 | 8163 | 8189 | 8212 | 8232 | 8250 | 8265 | 8279 | 8291 | 8301 | 8310 | 8317 | 8323 | 8329 | 8333
| NSW | 3370.94 | 3434.98 | 3500.83 | 3568.62 | 3638.33 | 3710.07 | 3903.36 | 4051.55 | 4206.33 | 4369.82 | 4539.52 | 4717.26 | 4939.03 | 5171.61 | 5467.13 | 5932.14 | 6088.64 | 6244.01 | 6398.2 | 6553.12 | 6708.75 | 6863.01 | 7012.81 | 7161.5 | 7310.16 | 7473.33 | 7993 | 8093 | 8186 | 8272 | 8352 | 8424 | 8490 | 8551 | 8605 | 8654 | 8698 | 8737 | 8771 | 8802 | 8829 | 8853 | 8873 | 8891 | 8907 | 8920 | 8931 | 8941 | 8949 | 8956
| VIC | 2670.09 | 2722.86 | 2777.11 | 2832.9 | 2890.33 | 2949.4 | 3107.83 | 3235.95 | 3371.17 | 3563.75 | 3735.05 | 3926.39 | 4182.48 | 4458.09 | 4772.7 | 5209.71 | 5365.87 | 5525.62 | 5688.44 | 5856.38 | 6027.73 | 6198.25 | 6365.45 | 6532.34 | 6699.77 | 6882.9 | 6397 | 6453 | 6506 | 6554 | 6599 | 6639 | 6677 | 6710 | 6741 | 6768 | 6793 | 6815 | 6834 | 6852 | 6867 | 6880 | 6892 | 6902 | 6910 | 6918 | 6924 | 6930 | 6934 | 6938
| SA | 1237.6 | 1249.67 | 1262.11 | 1274.9 | 1288.04 | 1301.59 | 1357.6 | 1405.64 | 1455.67 | 1508.45 | 1563.07 | 1620.17 | 1692.07 | 1767.25 | 1846.38 | 1944.1 | 1976.47 | 2009.06 | 2041.79 | 2074.77 | 2107.98 | 2140.97 | 2173.48 | 2206.01 | 2238.73 | 2273.83 | 2241 | 2253 | 2265 | 2275 | 2285 | 2293 | 2301 | 2309 | 2315 | 2321 | 2326 | 2331 | 2335 | 2339 | 2342 | 2345 | 2348 | 2350 | 2352 | 2353 | 2355 | 2356 | 2357 | 2358
| TAS | 218 | 219.02 | 220.1 | 221.2 | 222.36 | 223.55 | 232.45 | 239.85 | 247.55 | 260.3 | 271.75 | 283.57 | 300.37 | 317.57 | 335.41 | 361.82 | 368.54 | 375.34 | 382.34 | 389.65 | 397.15 | 404.34 | 411.09 | 417.58 | 423.83 | 430.72 | 559 | 560 | 561 | 562 | 563 | 564 | 565 | 566 | 567 | 567 | 568 | 569 | 569 | 569 | 570 | 570 | 570 | 571 | 571 | 571 | 571 | 571 | 571 | 571
[28 empty] | 7038.29 | 7211.39 | 7368.96 | 7534.41 | 7705.52 | 7885.36 | 0 | 0
[28 empty] | 7473.33 | 7629.69 | 7759.14 | 7896.05 | 8039.28 | 8192.93 | 0 | 0
[28 empty] | 6882.9 | 7059.7 | 7208.89 | 7366.51 | 7528.67 | 7699.8 | 0 | 0
[28 empty] | 2273.83 | 2308.21 | 2338.69 | 2370.39 | 2402.6 | 2435.97 | 0 | 0
[28 empty] | 430.72 | 437.03 | 441.54 | 446.28 | 450.92 | 455.69 | 0 | 0

## Battery storage uptake
TOC
Behind-the-meter storage uptake (MWh)
| Source: AEMO Electricity Statement of Opportunities 2018 |  |  |  | AEMO's forecasting data portal
Behind-the-meter storage includes battery uptakes for residential and commercial use.
| 2018 CSIRO Moderate: | AEMO's ESOO 2018 CSIRO Moderate storage uptake is used in AEMO's Neutral, Fast change and Slow change ESOO 2018 demand scenarios.
| Storage uptake (MWh) | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| QLD | 155.38 | 172.98 | 186.15 | 209.21 | 256.55 | 312.01 | 342.01 | 368.57 | 413.16 | 462.92 | 526.48 | 583.06 | 666.76 | 767.52 | 879.52 | 1006.16 | 1115.48 | 1233.77 | 1362.2 | 1501.58 | 1646.63 | 1800.36 | 1964.94 | 2141.01 | 2329.11 | 2534.53
| NSW | 397.25 | 450.01 | 491.15 | 564.9 | 689.51 | 825.17 | 891.89 | 933.17 | 1006 | 1087.31 | 1209.85 | 1308.97 | 1459.09 | 1641.9 | 1850.24 | 2071.32 | 2252.27 | 2441.51 | 2640.04 | 2847.99 | 3067.04 | 3293.94 | 3531.76 | 3780.91 | 4041.59 | 4321.2
| VIC | 192 | 215.69 | 234.65 | 268.74 | 326.99 | 403.04 | 447.7 | 482.87 | 556.5 | 634.84 | 727.54 | 815.68 | 935.68 | 1070.58 | 1219.58 | 1383.48 | 1521.37 | 1669.23 | 1828.42 | 1999.69 | 2184.97 | 2379.84 | 2586.9 | 2806.73 | 3039.7 | 3292.21
| SA | 223.27 | 440.61 | 443.34 | 446.36 | 449.85 | 453.44 | 456.58 | 460.57 | 466.29 | 471.74 | 476.98 | 482.52 | 489.45 | 508.18 | 546.45 | 602.87 | 652.51 | 705.06 | 760.76 | 819.71 | 882.51 | 947.35 | 1015.03 | 1085.64 | 1159.18 | 1237.65
| TAS | 31.86 | 34.9 | 37.2 | 41.4 | 48.49 | 56.52 | 61.62 | 66.52 | 75.43 | 85.31 | 96.77 | 106.64 | 119.61 | 133.35 | 147.53 | 162.64 | 174.94 | 188.04 | 202.08 | 217.1 | 233.27 | 249.86 | 267.08 | 284.9 | 303.32 | 322.8

## EV demand forecast
TOC
Electric vehicles demand projections (GWh)
| Source: AEMO Electricity Statement of Opportunities 2018 |  |  |  |  | AEMO's forecasting data portal
| Fast: | To be used in Fast change scenario
| Neutral: | To be used in Neutral scenario with proportionate share of emissions reduction target and Neutral scenario with stronger share of emissions reduction target
| Slow: | To be used in Slow change scenario
|  | AEMO forecast | [18 empty] | Extrapolated
| EV demand (GWh) | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Fast QLD | 11 | 27 | 59 | 117 | 218 | 390 | 619 | 941 | 1395 | 1908 | 2419 | 2933 | 3449 | 3982 | 4536 | 5091 | 5727 | 6390 | 7072 | 7801.8058 | 8582.291 | 9416.4969 | 10307.6424 | 11259.1339 | 12274.576 | 13357.783
| Fast NSW | 28 | 58 | 111 | 206 | 370 | 646 | 1015 | 1526 | 2237 | 3082 | 3907 | 4718 | 5513 | 6306 | 7106 | 7877 | 8745 | 9629 | 10515 | 11457.3667 | 12459.3626 | 13524.4354 | 14656.2287 | 15858.5926 | 17135.5956 | 18491.5363
| Fast VIC | 33 | 66 | 124 | 226 | 394 | 660 | 1008 | 1481 | 2127 | 2878 | 3625 | 4369 | 5104 | 5844 | 6593 | 7316 | 8124 | 8944 | 9767 | 10644.8929 | 11580.9399 | 12578.591 | 13641.4959 | 14773.5154 | 15978.7329 | 17261.4677
| Fast SA | 4 | 10 | 20 | 39 | 72 | 125 | 196 | 292 | 422 | 568 | 709 | 848 | 982 | 1118 | 1255 | 1388 | 1540 | 1697 | 1858 | 2028.9879 | 2210.5326 | 2403.2353 | 2607.7304 | 2824.6884 | 3054.8169 | 3298.8634
| Fast TAS | 1 | 3 | 6 | 11 | 20 | 34 | 53 | 78 | 110 | 142 | 171 | 199 | 226 | 254 | 283 | 313 | 347 | 384 | 422 | 462.283 | 504.9765 | 550.2152 | 598.1411 | 648.904 | 702.6621 | 759.5823
| Neutral QLD | 6 | 13 | 26 | 48 | 82 | 135 | 216 | 340 | 521 | 778 | 1128 | 1484 | 1842 | 2205 | 2577 | 2941 | 3342 | 3750 | 4163 | 4604.1432 | 5075.095 | 5577.6167 | 6113.5717 | 6684.9303 | 7293.7766 | 7942.3144
| Neutral NSW | 20 | 32 | 53 | 88 | 147 | 235 | 371 | 575 | 873 | 1305 | 1902 | 2508 | 3105 | 3698 | 4290 | 4851 | 5461 | 6073 | 6681 | 7327.3121 | 8014.1304 | 8743.7727 | 9518.6874 | 10341.4605 | 11214.8235 | 12141.6615
| Neutral VIC | 21 | 33 | 54 | 89 | 146 | 231 | 360 | 552 | 832 | 1230 | 1764 | 2309 | 2850 | 3392 | 3934 | 4447 | 5002 | 5553 | 6096 | 6674.5313 | 7290.6721 | 7946.6197 | 8644.6972 | 9387.3603 | 10177.2052 | 11016.9758
| Neutral SA | 3 | 5 | 9 | 15 | 26 | 42 | 67 | 103 | 155 | 229 | 326 | 422 | 516 | 611 | 707 | 798 | 899 | 1002 | 1105 | 1214.2362 | 1330.0578 | 1452.8336 | 1582.9524 | 1720.825 | 1866.8846 | 2021.5882
| Neutral TAS | 1 | 1 | 2 | 4 | 7 | 11 | 16 | 25 | 36 | 50 | 67 | 83 | 99 | 115 | 133 | 151 | 171 | 193 | 215 | 238.2287 | 262.7519 | 288.6387 | 315.9618 | 344.7982 | 375.2286 | 407.338
| Slow QLD | 3 | 4 | 7 | 14 | 26 | 41 | 64 | 97 | 144 | 210 | 299 | 428 | 591 | 799 | 1063 | 1386 | 1729 | 2080 | 2436 | 2816.2864 | 3222.2699 | 3655.4417 | 4117.3777 | 4609.7436 | 5134.2997 | 5692.9061
| Slow NSW | 11 | 15 | 20 | 31 | 49 | 72 | 107 | 157 | 228 | 329 | 468 | 691 | 971 | 1325 | 1764 | 2289 | 2839 | 3395 | 3955 | 4551.0268 | 5185.1257 | 5859.4567 | 6576.3002 | 7338.0646 | 8147.2923 | 9006.6682
| Slow VIC | 12 | 16 | 21 | 32 | 50 | 75 | 111 | 162 | 234 | 334 | 471 | 715 | 1007 | 1356 | 1768 | 2239 | 2731 | 3224 | 3713 | 4234.2454 | 4789.5902 | 5380.9932 | 6010.5238 | 6680.3683 | 7392.8362 | 8150.3671
| Slow SA | 1 | 2 | 3 | 5 | 9 | 15 | 23 | 35 | 51 | 73 | 103 | 148 | 200 | 263 | 338 | 428 | 524 | 621 | 717 | 818.7674 | 926.6202 | 1040.8938 | 1161.9421 | 1290.1381 | 1425.8752 | 1569.5685
| Slow TAS | 1 | 1 | 1 | 1 | 2 | 3 | 5 | 8 | 11 | 15 | 20 | 27 | 35 | 44 | 57 | 73 | 90 | 107 | 125 | 143.9103 | 163.7767 | 184.6472 | 206.5726 | 229.6059 | 253.8028 | 279.2219

## DSP
TOC
Demand-side participation (MW)
Source: AEMO 2018 ISP Assumptions Workbook
Electricity demand that will be removed from the market when modelled prices reach specified limits
MPC is currently set at $14,500/MWh
Neutral
Queensland
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 34.0523 | 35.0223 | 37.4238 | 38.8108 | 40.3889 | 42.3314 | 43.1421 | 45.3484 | 48.2758 | 50.3232 | 51.5702 | 53.0035 | 53.8757 | 55.23 | 57.875 | 59.6883 | 61.6696 | 63.3588 | 63.0905 | 64.9843 | 66.8961 | 66.8961 | 66.8961 | 66.8961 | 66.8961 | 66.8961
| $500 - $1,000 | 0.37766 | 0.38842 | 0.41505 | 0.43043 | 0.44794 | 0.46948 | 0.47847 | 0.50294 | 0.53541 | 0.55811 | 0.57194 | 0.58784 | 0.59751 | 0.61253 | 0.64187 | 0.66198 | 0.68395 | 0.70269 | 0.69971 | 0.72071 | 0.74192 | 0.74192 | 0.74192 | 0.74192 | 0.74192 | 0.74192
| $1,000 - $7,500 | 1.1435 | 1.176 | 1.2567 | 1.3033 | 1.3563 | 1.4215 | 1.4487 | 1.5228 | 1.6211 | 1.6898 | 1.7317 | 1.7798 | 1.8091 | 1.8546 | 1.9434 | 2.0043 | 2.0709 | 2.1276 | 2.1186 | 2.1822 | 2.2464 | 2.2464 | 2.2464 | 2.2464 | 2.2464 | 2.2464
| $7,500 - MPC | 6.7034 | 6.8944 | 7.3672 | 7.6402 | 7.9509 | 8.3333 | 8.4929 | 8.9272 | 9.5035 | 9.9065 | 10.152 | 10.4342 | 10.6059 | 10.8724 | 11.3931 | 11.7501 | 12.1401 | 12.4727 | 12.4198 | 12.7927 | 13.169 | 13.169 | 13.169 | 13.169 | 13.169 | 13.169
| MPC | 184.7068 | 189.9683 | 202.9947 | 210.5183 | 219.0782 | 229.6145 | 234.0121 | 245.9797 | 261.858 | 272.9639 | 279.728 | 287.5026 | 292.2335 | 299.5793 | 313.9262 | 323.7621 | 334.5094 | 343.6718 | 342.2164 | 352.4887 | 362.8588 | 362.8588 | 362.8588 | 362.8588 | 362.8588 | 362.8588
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 34.1414 | 35.6642 | 37.5711 | 39.4311 | 41.0965 | 42.5687 | 44.3402 | 47.1498 | 49.1788 | 50.8992 | 52.2082 | 54.2172 | 56.2999 | 58.3806 | 60.1988 | 61.6958 | 63.0391 | 65.8321 | 67.0766 | 69.0425 | 71.0277 | 71.0277 | 71.0277 | 71.0277 | 71.0277 | 71.0277
| $500 - $1,000 | 0.37865 | 0.39554 | 0.41669 | 0.43731 | 0.45578 | 0.47211 | 0.49176 | 0.52292 | 0.54542 | 0.5645 | 0.57902 | 0.6013 | 0.6244 | 0.64747 | 0.66764 | 0.68424 | 0.69914 | 0.73012 | 0.74392 | 0.76572 | 0.78774 | 0.78774 | 0.78774 | 0.78774 | 0.78774 | 0.78774
| $1,000 - $7,500 | 1.1465 | 1.1976 | 1.2616 | 1.3241 | 1.38 | 1.4294 | 1.4889 | 1.5833 | 1.6514 | 1.7092 | 1.7531 | 1.8206 | 1.8905 | 1.9604 | 2.0215 | 2.0717 | 2.1168 | 2.2106 | 2.2524 | 2.3184 | 2.3851 | 2.3851 | 2.3851 | 2.3851 | 2.3851 | 2.3851
| $7,500 - MPC | 6.721 | 7.0208 | 7.3962 | 7.7623 | 8.0902 | 8.38 | 8.7287 | 9.2818 | 9.6812 | 10.0199 | 10.2776 | 10.6731 | 11.0831 | 11.4927 | 11.8506 | 12.1453 | 12.4097 | 12.9596 | 13.2045 | 13.5915 | 13.9823 | 13.9823 | 13.9823 | 13.9823 | 13.9823 | 13.9823
| MPC | 164.1542 | 171.4761 | 180.6447 | 189.5878 | 197.5948 | 204.6733 | 213.1909 | 226.6995 | 236.455 | 244.727 | 251.0206 | 260.6801 | 270.6941 | 280.6981 | 289.4399 | 296.638 | 303.0966 | 316.5254 | 322.5089 | 331.9612 | 341.5062 | 341.5062 | 341.5062 | 341.5062 | 341.5062 | 341.5062
New South Wales
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 92.8563 | 108.0428 | 124.3374 | 139.6579 | 155.3028 | 170.6709 | 189.0836 | 208.1586 | 227.304 | 242.2635 | 257.6907 | 278.0438 | 292.7794 | 309.5983 | 328.5481 | 345.6494 | 363.7884 | 389.4479 | 404.0981 | 423.5158 | 443.1456 | 443.1456 | 443.1456 | 443.1456 | 443.1456 | 443.1456
| $500 - $1,000 | 0.32254 | 0.37529 | 0.43189 | 0.48511 | 0.53945 | 0.59284 | 0.65679 | 0.72305 | 0.78955 | 0.84152 | 0.8951 | 0.9658 | 1.017 | 1.0754 | 1.1412 | 1.2006 | 1.2636 | 1.3528 | 1.4037 | 1.4711 | 1.5393 | 1.5393 | 1.5393 | 1.5393 | 1.5393 | 1.5393
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 32.2662 | 37.5432 | 43.2054 | 48.529 | 53.9654 | 59.3056 | 65.7037 | 72.332 | 78.9847 | 84.1829 | 89.5436 | 96.616 | 101.7364 | 107.5807 | 114.1655 | 120.1079 | 126.411 | 135.3273 | 140.418 | 147.1653 | 153.9864 | 153.9864 | 153.9864 | 153.9864 | 153.9864 | 153.9864
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 91.1095 | 106.5544 | 121.6801 | 137.0607 | 153.3086 | 167.8506 | 185.994 | 204.6604 | 222.6753 | 240.9582 | 255.9211 | 273.4598 | 293.9347 | 312.0123 | 332.788 | 355.1466 | 371.3282 | 397.058 | 414.3212 | 435.5603 | 457.1417 | 457.1417 | 457.1417 | 457.1417 | 457.1417 | 457.1417
| $500 - $1,000 | 0.31647 | 0.37012 | 0.42266 | 0.47609 | 0.53253 | 0.58304 | 0.64606 | 0.7109 | 0.77348 | 0.83698 | 0.88896 | 0.94988 | 1.021 | 1.0838 | 1.156 | 1.2336 | 1.2898 | 1.3792 | 1.4392 | 1.5129 | 1.5879 | 1.5879 | 1.5879 | 1.5879 | 1.5879 | 1.5879
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 31.6592 | 37.0261 | 42.282 | 47.6265 | 53.2724 | 58.3256 | 64.6301 | 71.1164 | 77.3763 | 83.7293 | 88.9287 | 95.0231 | 102.1379 | 108.4195 | 115.6388 | 123.4081 | 129.031 | 137.9716 | 143.9703 | 151.3506 | 158.8498 | 158.8498 | 158.8498 | 158.8498 | 158.8498 | 158.8498
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 33.5 | 38.1748 | 43.9435 | 47.927 | 51.5418 | 57.3114 | 62.2751 | 67.5559 | 73.2614 | 78.4449 | 84.3275 | 89.0691 | 95.2638 | 101.2641 | 105.7532 | 109.7958 | 117.4408 | 124.6182 | 128.8018 | 134.6841 | 140.6145 | 140.6145 | 140.6145 | 140.6145 | 140.6145 | 140.6145
| $500 - $1,000 | 3.5888 | 4.0896 | 4.7075 | 5.1343 | 5.5215 | 6.1396 | 6.6714 | 7.2371 | 7.8483 | 8.4036 | 9.0338 | 9.5417 | 10.2053 | 10.8481 | 11.329 | 11.7621 | 12.5811 | 13.35 | 13.7982 | 14.4283 | 15.0636 | 15.0636 | 15.0636 | 15.0636 | 15.0636 | 15.0636
| $1,000 - $7,500 | 1.8888 | 2.1524 | 2.4777 | 2.7023 | 2.9061 | 3.2314 | 3.5112 | 3.809 | 4.1307 | 4.4229 | 4.7546 | 5.022 | 5.3712 | 5.7095 | 5.9627 | 6.1906 | 6.6216 | 7.0263 | 7.2622 | 7.5939 | 7.9282 | 7.9282 | 7.9282 | 7.9282 | 7.9282 | 7.9282
| $7,500 - MPC | 0.77914 | 0.88787 | 1.022 | 1.1147 | 1.1988 | 1.3329 | 1.4484 | 1.5712 | 1.7039 | 1.8245 | 1.9613 | 2.0716 | 2.2156 | 2.3552 | 2.4596 | 2.5536 | 2.7314 | 2.8984 | 2.9957 | 3.1325 | 3.2704 | 3.2704 | 3.2704 | 3.2704 | 3.2704 | 3.2704
| MPC | 51.3524 | 58.5184 | 67.3612 | 73.4676 | 79.0087 | 87.8531 | 95.4619 | 103.5568 | 112.3029 | 120.2486 | 129.2661 | 136.5345 | 146.0304 | 155.2283 | 162.1097 | 168.3067 | 180.0256 | 191.028 | 197.4411 | 206.4581 | 215.5488 | 215.5488 | 215.5488 | 215.5488 | 215.5488 | 215.5488
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 37.231 | 46.2061 | 55.1565 | 63.3412 | 71.9342 | 80.2684 | 88.2698 | 99.0359 | 108.6035 | 119.0805 | 128.508 | 137.1636 | 149.2975 | 159.8409 | 169.5051 | 180.5924 | 191.5764 | 203.6471 | 216.1936 | 228.4049 | 240.8319 | 240.8319 | 240.8319 | 240.8319 | 240.8319 | 240.8319
| $500 - $1,000 | 3.9885 | 4.9499 | 5.9088 | 6.7856 | 7.7061 | 8.5989 | 9.4561 | 10.6094 | 11.6344 | 12.7568 | 13.7667 | 14.694 | 15.9938 | 17.1233 | 18.1586 | 19.3464 | 20.523 | 21.8161 | 23.1602 | 24.4684 | 25.7997 | 25.7997 | 25.7997 | 25.7997 | 25.7997 | 25.7997
| $1,000 - $7,500 | 2.0992 | 2.6052 | 3.1099 | 3.5714 | 4.0558 | 4.5258 | 4.9769 | 5.5839 | 6.1234 | 6.7141 | 7.2456 | 7.7337 | 8.4178 | 9.0123 | 9.5572 | 10.1823 | 10.8016 | 11.4822 | 12.1896 | 12.8781 | 13.5788 | 13.5788 | 13.5788 | 13.5788 | 13.5788 | 13.5788
| $7,500 - MPC | 0.86591 | 1.0747 | 1.2828 | 1.4732 | 1.673 | 1.8669 | 2.053 | 2.3034 | 2.5259 | 2.7696 | 2.9888 | 3.1901 | 3.4723 | 3.7176 | 3.9423 | 4.2002 | 4.4557 | 4.7364 | 5.0282 | 5.3122 | 5.6012 | 5.6012 | 5.6012 | 5.6012 | 5.6012 | 5.6012
| MPC | 8.5279 | 10.5837 | 12.6339 | 14.5086 | 16.4769 | 18.3859 | 20.2186 | 22.6846 | 24.8762 | 27.276 | 29.4354 | 31.418 | 34.1973 | 36.6123 | 38.826 | 41.3656 | 43.8815 | 46.6464 | 49.5202 | 52.3173 | 55.1637 | 55.1637 | 55.1637 | 55.1637 | 55.1637 | 55.1637
South Australia
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 2.1927 | 3.1942 | 4.1003 | 5.0211 | 6.0119 | 6.8831 | 7.9672 | 8.9668 | 9.8215 | 10.7647 | 11.6576 | 12.7598 | 13.8323 | 14.7823 | 15.6548 | 16.5292 | 17.477 | 18.6323 | 19.7909 | 20.8426 | 21.9016 | 21.9016 | 21.9016 | 21.9016 | 21.9016 | 21.9016
| $500 - $1,000 | 1.5455 | 2.2515 | 2.8902 | 3.5392 | 4.2376 | 4.8516 | 5.6158 | 6.3204 | 6.9228 | 7.5876 | 8.217 | 8.9939 | 9.7499 | 10.4195 | 11.0345 | 11.6508 | 12.3189 | 13.1332 | 13.9498 | 14.6912 | 15.4376 | 15.4376 | 15.4376 | 15.4376 | 15.4376 | 15.4376
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 7.8176 | 11.3882 | 14.6189 | 17.9017 | 21.4343 | 24.5402 | 28.4056 | 31.9693 | 35.0164 | 38.3791 | 41.5628 | 45.4923 | 49.3163 | 52.7033 | 55.8141 | 58.9315 | 62.3105 | 66.4296 | 70.5602 | 74.3101 | 78.0855 | 78.0855 | 78.0855 | 78.0855 | 78.0855 | 78.0855
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 2.038 | 2.93 | 3.762 | 4.6431 | 5.5506 | 6.4077 | 7.312 | 8.2695 | 9.2163 | 10.1806 | 11.0565 | 11.9581 | 13.0218 | 14.0519 | 15.0213 | 16.0601 | 17.1054 | 18.0892 | 19.1628 | 20.2283 | 21.3057 | 21.3057 | 21.3057 | 21.3057 | 21.3057 | 21.3057
| $500 - $1,000 | 1.4365 | 2.0653 | 2.6517 | 3.2728 | 3.9124 | 4.5165 | 5.1539 | 5.8289 | 6.4962 | 7.1759 | 7.7933 | 8.4288 | 9.1786 | 9.9047 | 10.5879 | 11.3202 | 12.0569 | 12.7504 | 13.5072 | 14.2582 | 15.0176 | 15.0176 | 15.0176 | 15.0176 | 15.0176 | 15.0176
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 7.2661 | 10.4464 | 13.4125 | 16.5541 | 19.7896 | 22.8452 | 26.0693 | 29.4832 | 32.8587 | 36.2967 | 39.4198 | 42.6342 | 46.4266 | 50.0991 | 53.5552 | 57.2589 | 60.9856 | 64.4932 | 68.3212 | 72.1197 | 75.9611 | 75.9611 | 75.9611 | 75.9611 | 75.9611 | 75.9611
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 5.726 | 5.8484 | 6.0165 | 5.9282 | 6.0508 | 6.2067 | 6.3571 | 6.5266 | 6.6833 | 6.8983 | 7.0787 | 7.2692 | 7.3901 | 7.4919 | 7.6263 | 7.82 | 8.0395 | 8.1791 | 8.3766 | 8.5688 | 8.7628 | 8.7628 | 8.7628 | 8.7628 | 8.7628 | 8.7628
| $500 - $1,000 | 13.6185 | 13.9097 | 14.3095 | 14.0995 | 14.3912 | 14.7618 | 15.1196 | 15.5228 | 15.8953 | 16.4067 | 16.8358 | 17.2888 | 17.5765 | 17.8185 | 18.1383 | 18.599 | 19.121 | 19.4531 | 19.9228 | 20.3799 | 20.8413 | 20.8413 | 20.8413 | 20.8413 | 20.8413 | 20.8413
| $1,000 - $7,500 | 0.51585 | 0.52688 | 0.54203 | 0.53407 | 0.54512 | 0.55916 | 0.57271 | 0.58799 | 0.6021 | 0.62147 | 0.63772 | 0.65488 | 0.66578 | 0.67494 | 0.68706 | 0.70451 | 0.72428 | 0.73686 | 0.75465 | 0.77196 | 0.78944 | 0.78944 | 0.78944 | 0.78944 | 0.78944 | 0.78944
| $7,500 - MPC | 2.3626 | 2.4131 | 2.4825 | 2.446 | 2.4966 | 2.561 | 2.623 | 2.693 | 2.7576 | 2.8463 | 2.9208 | 2.9994 | 3.0493 | 3.0912 | 3.1467 | 3.2267 | 3.3172 | 3.3748 | 3.4563 | 3.5356 | 3.6157 | 3.6157 | 3.6157 | 3.6157 | 3.6157 | 3.6157
| MPC | 1.7198 | 1.7566 | 1.8071 | 1.7805 | 1.8174 | 1.8642 | 1.9094 | 1.9603 | 2.0073 | 2.0719 | 2.1261 | 2.1833 | 2.2196 | 2.2502 | 2.2906 | 2.3488 | 2.4147 | 2.4566 | 2.5159 | 2.5737 | 2.6319 | 2.6319 | 2.6319 | 2.6319 | 2.6319 | 2.6319
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 5.8179 | 6.0326 | 6.2787 | 6.3105 | 6.5137 | 6.7633 | 6.9532 | 7.2233 | 7.5291 | 7.7943 | 8.086 | 8.3041 | 8.5499 | 8.7832 | 8.9899 | 9.2229 | 9.5133 | 9.7964 | 10.0695 | 10.3458 | 10.6246 | 10.6246 | 10.6246 | 10.6246 | 10.6246 | 10.6246
| $500 - $1,000 | 13.8372 | 14.3478 | 14.933 | 15.0088 | 15.492 | 16.0856 | 16.5373 | 17.1798 | 17.907 | 18.5378 | 19.2315 | 19.7504 | 20.3348 | 20.8897 | 21.3814 | 21.9355 | 22.6263 | 23.2995 | 23.9492 | 24.6062 | 25.2692 | 25.2692 | 25.2692 | 25.2692 | 25.2692 | 25.2692
| $1,000 - $7,500 | 0.52413 | 0.54348 | 0.56565 | 0.56851 | 0.58682 | 0.6093 | 0.62641 | 0.65075 | 0.67829 | 0.70219 | 0.72847 | 0.74812 | 0.77026 | 0.79128 | 0.8099 | 0.83089 | 0.85705 | 0.88256 | 0.90717 | 0.93205 | 0.95717 | 0.95717 | 0.95717 | 0.95717 | 0.95717 | 0.95717
| $7,500 - MPC | 2.4005 | 2.4891 | 2.5907 | 2.6038 | 2.6876 | 2.7906 | 2.869 | 2.9804 | 3.1066 | 3.216 | 3.3364 | 3.4264 | 3.5278 | 3.6241 | 3.7094 | 3.8055 | 3.9253 | 4.0421 | 4.1548 | 4.2688 | 4.3838 | 4.3838 | 4.3838 | 4.3838 | 4.3838 | 4.3838
| MPC | 1.7474 | 1.8119 | 1.8858 | 1.8954 | 1.9564 | 2.0314 | 2.0884 | 2.1695 | 2.2614 | 2.341 | 2.4286 | 2.4942 | 2.568 | 2.638 | 2.7001 | 2.7701 | 2.8573 | 2.9424 | 3.0244 | 3.1074 | 3.1911 | 3.1911 | 3.1911 | 3.1911 | 3.1911 | 3.1911
Strong
Queensland
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 35.2097 | 37.1698 | 40.7993 | 43.4656 | 46.9013 | 49.7357 | 52.0509 | 55.5269 | 60.1367 | 63.3705 | 65.9977 | 69.376 | 71.4842 | 74.2128 | 79.2005 | 82.8291 | 86.2015 | 90.0765 | 90.8142 | 94.3351 | 97.8911 | 94.3351 | 97.8911 | 97.8911 | 97.8911 | 97.8911
| $500 - $1,000 | 0.3905 | 0.41223 | 0.45249 | 0.48206 | 0.52016 | 0.5516 | 0.57727 | 0.61582 | 0.66695 | 0.70281 | 0.73195 | 0.76942 | 0.7928 | 0.82306 | 0.87838 | 0.91862 | 0.95602 | 0.999 | 1.0072 | 1.0462 | 1.0857 | 1.0462 | 1.0857 | 1.0857 | 1.0857 | 1.0857
| $1,000 - $7,500 | 1.1823 | 1.2482 | 1.37 | 1.4596 | 1.5749 | 1.6701 | 1.7479 | 1.8646 | 2.0194 | 2.128 | 2.2162 | 2.3296 | 2.4004 | 2.4921 | 2.6595 | 2.7814 | 2.8946 | 3.0248 | 3.0495 | 3.1678 | 3.2872 | 3.1678 | 3.2872 | 3.2872 | 3.2872 | 3.2872
| $7,500 - MPC | 6.9313 | 7.3172 | 8.0316 | 8.5565 | 9.2329 | 9.7909 | 10.2466 | 10.9309 | 11.8384 | 12.475 | 12.9921 | 13.6572 | 14.0722 | 14.6094 | 15.5912 | 16.3056 | 16.9694 | 17.7323 | 17.8775 | 18.5706 | 19.2706 | 18.5706 | 19.2706 | 19.2706 | 19.2706 | 19.2706
| MPC | 190.985 | 201.617 | 221.3039 | 235.7667 | 254.4029 | 269.7773 | 282.3354 | 301.1896 | 326.1944 | 343.7351 | 357.9855 | 376.3101 | 387.7459 | 402.5462 | 429.6007 | 449.283 | 467.5756 | 488.5944 | 492.5957 | 511.6937 | 530.9821 | 511.6937 | 530.9821 | 530.9821 | 530.9821 | 530.9821
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 35.0274 | 38.0183 | 41.1759 | 44.1916 | 47.0181 | 49.6679 | 52.621 | 56.9188 | 60.0547 | 62.9765 | 65.5708 | 68.4285 | 71.8373 | 75.2761 | 78.2355 | 81.1959 | 83.8149 | 87.3673 | 90.8072 | 94.3267 | 97.8842 | 94.3267 | 97.8842 | 97.8842 | 97.8842 | 97.8842
| $500 - $1,000 | 0.38847 | 0.42164 | 0.45666 | 0.49011 | 0.52146 | 0.55085 | 0.5836 | 0.63126 | 0.66604 | 0.69844 | 0.72722 | 0.75891 | 0.79672 | 0.83486 | 0.86768 | 0.90051 | 0.92956 | 0.96895 | 1.0071 | 1.0461 | 1.0856 | 1.0461 | 1.0856 | 1.0856 | 1.0856 | 1.0856
| $1,000 - $7,500 | 1.1762 | 1.2766 | 1.3827 | 1.4839 | 1.5789 | 1.6678 | 1.767 | 1.9113 | 2.0166 | 2.1147 | 2.2019 | 2.2978 | 2.4123 | 2.5278 | 2.6271 | 2.7265 | 2.8145 | 2.9338 | 3.0493 | 3.1675 | 3.2869 | 3.1675 | 3.2869 | 3.2869 | 3.2869 | 3.2869
| $7,500 - MPC | 6.8954 | 7.4842 | 8.1058 | 8.6995 | 9.2559 | 9.7775 | 10.3589 | 11.2049 | 11.8222 | 12.3974 | 12.9081 | 13.4707 | 14.1417 | 14.8187 | 15.4013 | 15.984 | 16.4996 | 17.1989 | 17.8761 | 18.5689 | 19.2693 | 18.5689 | 19.2693 | 19.2693 | 19.2693 | 19.2693
| MPC | 168.4143 | 182.7945 | 197.9768 | 212.4763 | 226.0664 | 238.807 | 253.0057 | 273.6697 | 288.7471 | 302.7953 | 315.269 | 329.0093 | 345.3991 | 361.9329 | 376.1618 | 390.3955 | 402.9881 | 420.0684 | 436.6076 | 453.5294 | 470.6343 | 453.5294 | 470.6343 | 470.6343 | 470.6343 | 470.6343
New South Wales
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 103.0066 | 126.8519 | 151.8192 | 176.5757 | 199.9942 | 225.9737 | 253.9989 | 278.5219 | 309.1274 | 333.1624 | 358.1545 | 387.5127 | 412.5448 | 439.2906 | 469.7517 | 492.0782 | 523.2652 | 559.3418 | 590.8385 | 622.0772 | 653.7028 | 622.0772 | 653.7028 | 653.7028 | 653.7028 | 653.7028
| $500 - $1,000 | 0.3578 | 0.44063 | 0.52735 | 0.61335 | 0.69469 | 0.78493 | 0.88228 | 0.96746 | 1.0738 | 1.1573 | 1.2441 | 1.346 | 1.433 | 1.5259 | 1.6317 | 1.7093 | 1.8176 | 1.9429 | 2.0523 | 2.1608 | 2.2707 | 2.1608 | 2.2707 | 2.2707 | 2.2707 | 2.2707
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 35.7932 | 44.0791 | 52.7549 | 61.3574 | 69.495 | 78.5225 | 88.2608 | 96.7821 | 107.4171 | 115.7689 | 124.4533 | 134.6548 | 143.3531 | 152.6468 | 163.2316 | 170.9897 | 181.8267 | 194.3628 | 205.3074 | 216.1624 | 227.1519 | 216.1624 | 227.1519 | 227.1519 | 227.1519 | 227.1519
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 99.7444 | 123.2241 | 146.852 | 170.0697 | 194.4421 | 215.5349 | 240.6048 | 266.5367 | 290.9246 | 316.3731 | 336.7103 | 361.6822 | 384.5123 | 410.448 | 435.4217 | 461.4406 | 483.1775 | 511.1711 | 535.8229 | 561.2308 | 586.7618 | 561.2308 | 586.7618 | 586.7618 | 586.7618 | 586.7618
| $500 - $1,000 | 0.34647 | 0.42803 | 0.5101 | 0.59075 | 0.67541 | 0.74867 | 0.83576 | 0.92583 | 1.0105 | 1.0989 | 1.1696 | 1.2563 | 1.3356 | 1.4257 | 1.5125 | 1.6028 | 1.6783 | 1.7756 | 1.8612 | 1.9495 | 2.0382 | 1.9495 | 2.0382 | 2.0382 | 2.0382 | 2.0382
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 34.6597 | 42.8185 | 51.0289 | 59.0967 | 67.5657 | 74.8951 | 83.6065 | 92.6175 | 101.0919 | 109.9349 | 117.0017 | 125.6791 | 133.6122 | 142.6245 | 151.3024 | 160.3436 | 167.8969 | 177.6242 | 186.1904 | 195.0192 | 203.8908 | 195.0192 | 203.8908 | 203.8908 | 203.8908 | 203.8908
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 36.477 | 44.655 | 52.9262 | 61.1607 | 68.83 | 79.1677 | 88.382 | 97.5547 | 107.5022 | 115.6123 | 123.798 | 133.9254 | 142.2641 | 151.6663 | 159.6314 | 166.2229 | 182.4354 | 192.7905 | 202.7611 | 214.0022 | 225.4268 | 214.0022 | 225.4268 | 225.4268 | 225.4268 | 225.4268
| $500 - $1,000 | 3.9077 | 4.7838 | 5.6698 | 6.552 | 7.3736 | 8.481 | 9.4681 | 10.4508 | 11.5164 | 12.3852 | 13.2621 | 14.3471 | 15.2404 | 16.2476 | 17.1009 | 17.807 | 19.5438 | 20.6531 | 21.7212 | 22.9255 | 24.1493 | 22.9255 | 24.1493 | 24.1493 | 24.1493 | 24.1493
| $1,000 - $7,500 | 2.0567 | 2.5178 | 2.9841 | 3.4484 | 3.8808 | 4.4637 | 4.9832 | 5.5004 | 6.0613 | 6.5185 | 6.9801 | 7.5511 | 8.0212 | 8.5514 | 9.0005 | 9.3721 | 10.2862 | 10.8701 | 11.4322 | 12.066 | 12.7102 | 12.066 | 12.7102 | 12.7102 | 12.7102 | 12.7102
| $7,500 - MPC | 0.84838 | 1.0386 | 1.231 | 1.4225 | 1.6008 | 1.8413 | 2.0556 | 2.2689 | 2.5003 | 2.6889 | 2.8793 | 3.1148 | 3.3088 | 3.5274 | 3.7127 | 3.866 | 4.2431 | 4.4839 | 4.7158 | 4.9772 | 5.243 | 4.9772 | 5.243 | 5.243 | 5.243 | 5.243
| MPC | 55.9159 | 68.4519 | 81.1309 | 93.7536 | 105.5099 | 121.3566 | 135.4813 | 149.5422 | 164.7907 | 177.2227 | 189.7706 | 205.2951 | 218.0775 | 232.4901 | 244.6999 | 254.804 | 279.6564 | 295.5296 | 310.8137 | 328.0453 | 345.5581 | 328.0453 | 345.5581 | 345.5581 | 345.5581 | 345.5581
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 42.0027 | 55.8353 | 69.5673 | 84.0319 | 98.4561 | 113.2009 | 128.7267 | 143.2602 | 158.0867 | 174.0511 | 187.0908 | 201.6314 | 217.202 | 232.053 | 247.5899 | 262.2023 | 277.5009 | 294.4607 | 311.0968 | 327.2947 | 343.6211 | 327.2947 | 343.6211 | 343.6211 | 343.6211 | 343.6211
| $500 - $1,000 | 4.4996 | 5.9815 | 7.4526 | 9.0021 | 10.5473 | 12.1269 | 13.7901 | 15.3471 | 16.9354 | 18.6456 | 20.0425 | 21.6002 | 23.2682 | 24.8592 | 26.5236 | 28.089 | 29.7279 | 31.5448 | 33.3269 | 35.0622 | 36.8112 | 35.0622 | 36.8112 | 36.8112 | 36.8112 | 36.8112
| $1,000 - $7,500 | 2.3682 | 3.1481 | 3.9224 | 4.738 | 5.5512 | 6.3826 | 7.258 | 8.0774 | 8.9134 | 9.8135 | 10.5487 | 11.3685 | 12.2464 | 13.0838 | 13.9598 | 14.7837 | 15.6463 | 16.6025 | 17.5405 | 18.4538 | 19.3743 | 18.4538 | 19.3743 | 19.3743 | 19.3743 | 19.3743
| $7,500 - MPC | 0.97689 | 1.2986 | 1.618 | 1.9544 | 2.2899 | 2.6328 | 2.9939 | 3.3319 | 3.6768 | 4.0481 | 4.3513 | 4.6895 | 5.0517 | 5.3971 | 5.7584 | 6.0983 | 6.4541 | 6.8485 | 7.2355 | 7.6122 | 7.9919 | 7.6122 | 7.9919 | 7.9919 | 7.9919 | 7.9919
| MPC | 9.6209 | 12.7893 | 15.9347 | 19.2479 | 22.5519 | 25.9292 | 29.4855 | 32.8144 | 36.2105 | 39.8673 | 42.8541 | 46.1847 | 49.7512 | 53.1529 | 56.7117 | 60.0587 | 63.5629 | 67.4477 | 71.2582 | 74.9685 | 78.7081 | 74.9685 | 78.7081 | 78.7081 | 78.7081 | 78.7081
South Australia
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 2.6899 | 4.206 | 5.5475 | 6.9365 | 8.3085 | 9.7354 | 11.351 | 12.8297 | 14.144 | 15.5487 | 16.7871 | 18.3041 | 19.7434 | 21.2268 | 22.4805 | 23.7152 | 25.3123 | 27.1335 | 28.6408 | 30.2105 | 31.7922 | 30.2105 | 31.7922 | 31.7922 | 31.7922 | 31.7922
| $500 - $1,000 | 1.896 | 2.9647 | 3.9103 | 4.8893 | 5.8564 | 6.8622 | 8.0009 | 9.0432 | 9.9696 | 10.9597 | 11.8326 | 12.9019 | 13.9164 | 14.962 | 15.8457 | 16.7159 | 17.8417 | 19.1254 | 20.1878 | 21.2943 | 22.4091 | 21.2943 | 22.4091 | 22.4091 | 22.4091 | 22.4091
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 9.5904 | 14.9956 | 19.7786 | 24.7306 | 29.6223 | 34.7097 | 40.4697 | 45.7415 | 50.4276 | 55.4358 | 59.851 | 65.2595 | 70.391 | 75.6799 | 80.1495 | 84.5515 | 90.2459 | 96.739 | 102.1127 | 107.7094 | 113.3486 | 107.7094 | 113.3486 | 113.3486 | 113.3486 | 113.3486
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 2.4973 | 3.883 | 5.1948 | 6.4998 | 7.8362 | 9.101 | 10.4031 | 11.7923 | 13.163 | 14.4541 | 15.6651 | 16.8378 | 18.1251 | 19.5999 | 20.8973 | 22.2441 | 23.6157 | 24.7861 | 26.1414 | 27.4524 | 28.7632 | 27.4524 | 28.7632 | 28.7632 | 28.7632 | 28.7632
| $500 - $1,000 | 1.7603 | 2.737 | 3.6616 | 4.5815 | 5.5235 | 6.4149 | 7.3327 | 8.3119 | 9.2781 | 10.1882 | 11.0417 | 11.8683 | 12.7757 | 13.8152 | 14.7297 | 15.6791 | 16.6458 | 17.4708 | 18.4261 | 19.3501 | 20.2741 | 19.3501 | 20.2741 | 20.2741 | 20.2741 | 20.2741
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 8.9036 | 13.844 | 18.521 | 23.1737 | 27.9385 | 32.4477 | 37.0901 | 42.0429 | 46.9298 | 51.5332 | 55.8507 | 60.0317 | 64.6213 | 69.8795 | 74.505 | 79.3069 | 84.197 | 88.3698 | 93.2019 | 97.8757 | 102.5494 | 97.8757 | 102.5494 | 102.5494 | 102.5494 | 102.5494
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 5.8719 | 6.1368 | 6.4151 | 6.4474 | 6.7338 | 6.9858 | 7.2793 | 7.6076 | 7.9156 | 8.2754 | 8.6004 | 8.8678 | 9.1692 | 9.4339 | 9.6614 | 10.0128 | 10.3676 | 10.7166 | 10.9872 | 11.3252 | 11.6656 | 11.3252 | 11.6656 | 11.6656 | 11.6656 | 11.6656
| $500 - $1,000 | 13.9656 | 14.5957 | 15.2575 | 15.3343 | 16.0155 | 16.6148 | 17.313 | 18.0936 | 18.8264 | 19.682 | 20.455 | 21.091 | 21.8078 | 22.4374 | 22.9784 | 23.8143 | 24.6581 | 25.488 | 26.1318 | 26.9355 | 27.7453 | 26.9355 | 27.7453 | 27.7453 | 27.7453 | 27.7453
| $1,000 - $7,500 | 0.529 | 0.55287 | 0.57793 | 0.58084 | 0.60665 | 0.62935 | 0.65579 | 0.68537 | 0.71312 | 0.74553 | 0.77481 | 0.7989 | 0.82605 | 0.8499 | 0.8704 | 0.90206 | 0.93402 | 0.96546 | 0.98984 | 1.0203 | 1.051 | 1.0203 | 1.051 | 1.051 | 1.051 | 1.051
| $7,500 - MPC | 2.4228 | 2.5321 | 2.6469 | 2.6603 | 2.7784 | 2.8824 | 3.0035 | 3.139 | 3.2661 | 3.4145 | 3.5486 | 3.659 | 3.7833 | 3.8925 | 3.9864 | 4.1314 | 4.2778 | 4.4218 | 4.5335 | 4.6729 | 4.8134 | 4.6729 | 4.8134 | 4.8134 | 4.8134 | 4.8134
| MPC | 1.7636 | 1.8432 | 1.9268 | 1.9365 | 2.0225 | 2.0982 | 2.1864 | 2.2849 | 2.3775 | 2.4855 | 2.5832 | 2.6635 | 2.754 | 2.8335 | 2.9018 | 3.0074 | 3.1139 | 3.2187 | 3.3 | 3.4015 | 3.5038 | 3.4015 | 3.5038 | 3.5038 | 3.5038 | 3.5038
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 5.9812 | 6.3293 | 6.709 | 6.8833 | 7.2426 | 7.6369 | 8.0365 | 8.4674 | 8.9292 | 9.342 | 9.7796 | 10.197 | 10.5463 | 10.9239 | 11.289 | 11.7284 | 12.1782 | 12.6026 | 13.0134 | 13.4504 | 13.8897 | 13.4504 | 13.8897 | 13.8897 | 13.8897 | 13.8897
| $500 - $1,000 | 14.2257 | 15.0534 | 15.9566 | 16.371 | 17.2256 | 18.1634 | 19.1138 | 20.1387 | 21.2369 | 22.2189 | 23.2595 | 24.2522 | 25.0831 | 25.9812 | 26.8495 | 27.8945 | 28.9643 | 29.9737 | 30.9507 | 31.9901 | 33.0351 | 31.9901 | 33.0351 | 33.0351 | 33.0351 | 33.0351
| $1,000 - $7,500 | 0.53885 | 0.5702 | 0.60442 | 0.62011 | 0.65249 | 0.68801 | 0.72401 | 0.76283 | 0.80443 | 0.84162 | 0.88104 | 0.91864 | 0.95012 | 0.98414 | 1.017 | 1.0566 | 1.0971 | 1.1354 | 1.1724 | 1.2117 | 1.2513 | 1.2117 | 1.2513 | 1.2513 | 1.2513 | 1.2513
| $7,500 - MPC | 2.4679 | 2.6115 | 2.7682 | 2.8401 | 2.9884 | 3.1511 | 3.316 | 3.4938 | 3.6843 | 3.8546 | 4.0352 | 4.2074 | 4.3515 | 4.5073 | 4.658 | 4.8393 | 5.0249 | 5.2 | 5.3695 | 5.5498 | 5.7311 | 5.5498 | 5.7311 | 5.7311 | 5.7311 | 5.7311
| MPC | 1.7965 | 1.901 | 2.0151 | 2.0674 | 2.1753 | 2.2937 | 2.4138 | 2.5432 | 2.6819 | 2.8059 | 2.9373 | 3.0627 | 3.1676 | 3.281 | 3.3907 | 3.5226 | 3.6577 | 3.7852 | 3.9086 | 4.0398 | 4.1718 | 4.0398 | 4.1718 | 4.1718 | 4.1718 | 4.1718
Weak
Queensland
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 32.6254 | 32.2053 | 33.0832 | 33.0322 | 33.1417 | 33.5322 | 33.0302 | 33.5945 | 34.6407 | 35.0112 | 34.8193 | 34.7606 | 34.3475 | 34.2557 | 34.9482 | 35.1158 | 35.3714 | 35.451 | 34.4576 | 34.664 | 34.8703 | 34.664 | 34.8703 | 34.8703 | 34.8703 | 34.8703
| $500 - $1,000 | 0.36183 | 0.35718 | 0.36691 | 0.36635 | 0.36756 | 0.37189 | 0.36632 | 0.37258 | 0.38419 | 0.38829 | 0.38617 | 0.38552 | 0.38093 | 0.37992 | 0.3876 | 0.38945 | 0.39229 | 0.39317 | 0.38215 | 0.38444 | 0.38673 | 0.38444 | 0.38673 | 0.38673 | 0.38673 | 0.38673
| $1,000 - $7,500 | 1.0956 | 1.0814 | 1.1109 | 1.1092 | 1.1129 | 1.126 | 1.1091 | 1.1281 | 1.1632 | 1.1757 | 1.1692 | 1.1673 | 1.1534 | 1.1503 | 1.1736 | 1.1792 | 1.1878 | 1.1904 | 1.1571 | 1.164 | 1.1709 | 1.164 | 1.1709 | 1.1709 | 1.1709 | 1.1709
| $7,500 - MPC | 6.4226 | 6.3399 | 6.5127 | 6.5026 | 6.5242 | 6.6011 | 6.5022 | 6.6133 | 6.8193 | 6.8922 | 6.8544 | 6.8429 | 6.7616 | 6.7435 | 6.8798 | 6.9128 | 6.9631 | 6.9788 | 6.7832 | 6.8239 | 6.8645 | 6.8239 | 6.8645 | 6.8645 | 6.8645 | 6.8645
| MPC | 176.9672 | 174.6884 | 179.4501 | 179.1739 | 179.7678 | 181.8861 | 179.1627 | 182.2237 | 187.8988 | 189.9082 | 188.8674 | 188.549 | 186.308 | 185.8103 | 189.5667 | 190.4758 | 191.862 | 192.2936 | 186.9056 | 188.0247 | 189.1438 | 188.0247 | 189.1438 | 189.1438 | 189.1438 | 189.1438
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 32.8114 | 32.9898 | 33.4978 | 33.93 | 34.1711 | 34.2412 | 34.54 | 35.6044 | 36.0336 | 36.2186 | 36.1085 | 36.4755 | 36.8712 | 37.2451 | 37.437 | 37.4246 | 37.3218 | 38.062 | 37.8934 | 38.1309 | 38.3684 | 38.1309 | 38.3684 | 38.3684 | 38.3684 | 38.3684
| $500 - $1,000 | 0.3639 | 0.36588 | 0.37151 | 0.3763 | 0.37898 | 0.37975 | 0.38307 | 0.39487 | 0.39963 | 0.40168 | 0.40046 | 0.40453 | 0.40892 | 0.41307 | 0.4152 | 0.41506 | 0.41392 | 0.42213 | 0.42026 | 0.42289 | 0.42553 | 0.42289 | 0.42553 | 0.42553 | 0.42553 | 0.42553
| $1,000 - $7,500 | 1.1018 | 1.1078 | 1.1248 | 1.1394 | 1.1475 | 1.1498 | 1.1598 | 1.1956 | 1.21 | 1.2162 | 1.2125 | 1.2248 | 1.2381 | 1.2507 | 1.2571 | 1.2567 | 1.2533 | 1.2781 | 1.2725 | 1.2804 | 1.2884 | 1.2804 | 1.2884 | 1.2884 | 1.2884 | 1.2884
| $7,500 - MPC | 6.4592 | 6.4943 | 6.5943 | 6.6794 | 6.7268 | 6.7406 | 6.7995 | 7.009 | 7.0935 | 7.1299 | 7.1082 | 7.1805 | 7.2584 | 7.332 | 7.3698 | 7.3673 | 7.3471 | 7.4928 | 7.4596 | 7.5064 | 7.5531 | 7.5064 | 7.5531 | 7.5531 | 7.5531 | 7.5531
| MPC | 157.7596 | 158.6175 | 161.0598 | 163.1376 | 164.2971 | 164.6341 | 166.0709 | 171.1885 | 173.2523 | 174.1414 | 173.6124 | 175.3766 | 177.2794 | 179.0773 | 179.9997 | 179.9403 | 179.4459 | 183.0047 | 182.1944 | 183.3362 | 184.478 | 183.3362 | 184.478 | 184.478 | 184.478 | 184.478
New South Wales
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 77.6823 | 77.6913 | 78.3968 | 78.4007 | 78.568 | 78.5777 | 79.8719 | 81.2272 | 82.4161 | 82.0305 | 81.8411 | 83.147 | 82.7215 | 82.8984 | 83.5999 | 83.7869 | 84.1972 | 86.2372 | 85.7714 | 86.3142 | 86.8571 | 86.3142 | 86.8571 | 86.8571 | 86.8571 | 86.8571
| $500 - $1,000 | 0.26983 | 0.26987 | 0.27232 | 0.27233 | 0.27291 | 0.27294 | 0.27744 | 0.28215 | 0.28628 | 0.28494 | 0.28428 | 0.28882 | 0.28734 | 0.28795 | 0.29039 | 0.29104 | 0.29246 | 0.29955 | 0.29793 | 0.29982 | 0.3017 | 0.29982 | 0.3017 | 0.3017 | 0.3017 | 0.3017
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 26.9934 | 26.9966 | 27.2417 | 27.2431 | 27.3012 | 27.3046 | 27.7543 | 28.2252 | 28.6384 | 28.5043 | 28.4386 | 28.8923 | 28.7445 | 28.8059 | 29.0497 | 29.1147 | 29.2572 | 29.9661 | 29.8043 | 29.9929 | 30.1815 | 29.9929 | 30.1815 | 30.1815 | 30.1815 | 30.1815
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 77.2433 | 78.405 | 79.0881 | 79.7768 | 80.7923 | 80.8109 | 82.4225 | 84.0113 | 85.1329 | 86.2064 | 86.0342 | 86.6982 | 88.1715 | 88.8118 | 90.1206 | 91.7168 | 91.647 | 93.8397 | 93.9344 | 94.8879 | 95.8413 | 94.8879 | 95.8413 | 95.8413 | 95.8413 | 95.8413
| $500 - $1,000 | 0.26831 | 0.27234 | 0.27472 | 0.27711 | 0.28064 | 0.2807 | 0.2863 | 0.29182 | 0.29571 | 0.29944 | 0.29885 | 0.30115 | 0.30627 | 0.30849 | 0.31304 | 0.31858 | 0.31834 | 0.32596 | 0.32629 | 0.3296 | 0.33291 | 0.3296 | 0.33291 | 0.33291 | 0.33291 | 0.33291
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 26.8409 | 27.2445 | 27.4819 | 27.7212 | 28.0741 | 28.0806 | 28.6406 | 29.1927 | 29.5824 | 29.9554 | 29.8956 | 30.1263 | 30.6383 | 30.8608 | 31.3155 | 31.8702 | 31.8459 | 32.6079 | 32.6408 | 32.9721 | 33.3034 | 32.9721 | 33.3034 | 33.3034 | 33.3034 | 33.3034
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 28.2944 | 27.9064 | 28.3152 | 27.609 | 26.8461 | 27.2408 | 27.2198 | 27.3301 | 27.5852 | 27.6233 | 27.8881 | 27.7667 | 28.0869 | 28.3199 | 28.128 | 27.8409 | 28.4521 | 28.9027 | 28.6505 | 28.7811 | 28.9117 | 28.7811 | 28.9117 | 28.9117 | 28.9117 | 28.9117
| $500 - $1,000 | 3.0311 | 2.9895 | 3.0333 | 2.9577 | 2.8759 | 2.9182 | 2.916 | 2.9278 | 2.9551 | 2.9592 | 2.9876 | 2.9746 | 3.0089 | 3.0338 | 3.0133 | 2.9825 | 3.048 | 3.0963 | 3.0692 | 3.0832 | 3.0972 | 3.0832 | 3.0972 | 3.0972 | 3.0972 | 3.0972
| $1,000 - $7,500 | 1.5953 | 1.5734 | 1.5965 | 1.5567 | 1.5137 | 1.5359 | 1.5347 | 1.5409 | 1.5553 | 1.5575 | 1.5724 | 1.5656 | 1.5836 | 1.5968 | 1.5859 | 1.5697 | 1.6042 | 1.6296 | 1.6154 | 1.6228 | 1.6301 | 1.6228 | 1.6301 | 1.6301 | 1.6301 | 1.6301
| $7,500 - MPC | 0.65807 | 0.64904 | 0.65855 | 0.64213 | 0.62438 | 0.63356 | 0.63307 | 0.63564 | 0.64157 | 0.64246 | 0.64862 | 0.64579 | 0.65324 | 0.65866 | 0.6542 | 0.64752 | 0.66174 | 0.67222 | 0.66635 | 0.66939 | 0.67242 | 0.66939 | 0.67242 | 0.67242 | 0.67242 | 0.67242
| MPC | 43.3727 | 42.7779 | 43.4045 | 42.322 | 41.1525 | 41.7576 | 41.7254 | 41.8945 | 42.2855 | 42.344 | 42.7498 | 42.5637 | 43.0546 | 43.4117 | 43.1176 | 42.6775 | 43.6144 | 44.3051 | 43.9185 | 44.1187 | 44.3189 | 44.1187 | 44.3189 | 44.3189 | 44.3189 | 44.3189
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 28.5491 | 28.7314 | 28.8428 | 28.5782 | 28.5394 | 28.4173 | 28.2126 | 28.8496 | 29.0621 | 29.4677 | 29.575 | 29.5023 | 30.1406 | 30.4026 | 30.4779 | 30.788 | 31.0508 | 31.4567 | 31.8964 | 32.251 | 32.6057 | 32.251 | 32.6057 | 32.6057 | 32.6057 | 32.6057
| $500 - $1,000 | 3.0584 | 3.0779 | 3.0898 | 3.0615 | 3.0573 | 3.0443 | 3.0223 | 3.0906 | 3.1133 | 3.1568 | 3.1683 | 3.1605 | 3.2289 | 3.257 | 3.265 | 3.2982 | 3.3264 | 3.3699 | 3.417 | 3.455 | 3.493 | 3.455 | 3.493 | 3.493 | 3.493 | 3.493
| $1,000 - $7,500 | 1.6097 | 1.62 | 1.6262 | 1.6113 | 1.6091 | 1.6022 | 1.5907 | 1.6266 | 1.6386 | 1.6615 | 1.6675 | 1.6634 | 1.6994 | 1.7142 | 1.7184 | 1.7359 | 1.7507 | 1.7736 | 1.7984 | 1.8184 | 1.8384 | 1.8184 | 1.8384 | 1.8384 | 1.8384 | 1.8384
| $7,500 - MPC | 0.66399 | 0.66823 | 0.67082 | 0.66467 | 0.66377 | 0.66093 | 0.65617 | 0.67098 | 0.67592 | 0.68536 | 0.68785 | 0.68616 | 0.70101 | 0.7071 | 0.70885 | 0.71606 | 0.72217 | 0.73162 | 0.74184 | 0.75009 | 0.75834 | 0.75009 | 0.75834 | 0.75834 | 0.75834 | 0.75834
| MPC | 6.5393 | 6.5811 | 6.6066 | 6.546 | 6.5371 | 6.5091 | 6.4622 | 6.6081 | 6.6568 | 6.7497 | 6.7743 | 6.7576 | 6.9039 | 6.9639 | 6.9811 | 7.0521 | 7.1123 | 7.2053 | 7.306 | 7.3873 | 7.4685 | 7.3873 | 7.4685 | 7.4685 | 7.4685 | 7.4685
South Australia
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 1.229 | 1.2437 | 1.2231 | 1.2138 | 1.2218 | 1.2065 | 1.2278 | 1.2329 | 1.219 | 1.2175 | 1.2111 | 1.2258 | 1.2357 | 1.2341 | 1.2267 | 1.2202 | 1.2196 | 1.2328 | 1.2448 | 1.2494 | 1.2539 | 1.2494 | 1.2539 | 1.2539 | 1.2539 | 1.2539
| $500 - $1,000 | 0.86628 | 0.87665 | 0.86212 | 0.85559 | 0.86118 | 0.85045 | 0.86545 | 0.86901 | 0.85921 | 0.8582 | 0.85368 | 0.864 | 0.87101 | 0.8699 | 0.86464 | 0.86009 | 0.85964 | 0.86892 | 0.87743 | 0.88063 | 0.88383 | 0.88063 | 0.88383 | 0.88383 | 0.88383 | 0.88383
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 4.3817 | 4.4342 | 4.3607 | 4.3277 | 4.356 | 4.3017 | 4.3776 | 4.3956 | 4.346 | 4.3409 | 4.318 | 4.3702 | 4.4057 | 4.4001 | 4.3735 | 4.3504 | 4.3482 | 4.3951 | 4.4382 | 4.4543 | 4.4705 | 4.4543 | 4.4705 | 4.4705 | 4.4705 | 4.4705
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 1.2103 | 1.2375 | 1.2328 | 1.243 | 1.256 | 1.2556 | 1.2635 | 1.278 | 1.2881 | 1.2988 | 1.2973 | 1.2989 | 1.3166 | 1.3289 | 1.3343 | 1.3449 | 1.3548 | 1.3591 | 1.3694 | 1.3782 | 1.387 | 1.3782 | 1.387 | 1.387 | 1.387 | 1.387
| $500 - $1,000 | 0.85311 | 0.87226 | 0.86895 | 0.87614 | 0.88531 | 0.88505 | 0.89061 | 0.90079 | 0.90796 | 0.91546 | 0.91445 | 0.91555 | 0.92806 | 0.9367 | 0.94049 | 0.94795 | 0.95496 | 0.958 | 0.96526 | 0.97145 | 0.97765 | 0.97145 | 0.97765 | 0.97765 | 0.97765 | 0.97765
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 4.3151 | 4.412 | 4.3953 | 4.4317 | 4.478 | 4.4767 | 4.5048 | 4.5563 | 4.5926 | 4.6305 | 4.6254 | 4.631 | 4.6942 | 4.738 | 4.7571 | 4.7949 | 4.8303 | 4.8457 | 4.8824 | 4.9137 | 4.9451 | 4.9137 | 4.9451 | 4.9451 | 4.9451 | 4.9451
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
| Price band | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| $300 - $500 | 5.5982 | 5.5931 | 5.6309 | 5.4322 | 5.431 | 5.4591 | 5.4813 | 5.5189 | 5.5443 | 5.6163 | 5.6581 | 5.7062 | 5.699 | 5.6775 | 5.6812 | 5.7281 | 5.792 | 5.7973 | 5.8427 | 5.8831 | 5.9235 | 5.8831 | 5.9235 | 5.9235 | 5.9235 | 5.9235
| $500 - $1,000 | 13.3146 | 13.3024 | 13.3924 | 12.9199 | 12.917 | 12.9837 | 13.0367 | 13.126 | 13.1864 | 13.3577 | 13.457 | 13.5715 | 13.5544 | 13.5034 | 13.512 | 13.6236 | 13.7756 | 13.7881 | 13.8962 | 13.9923 | 14.0883 | 13.9923 | 14.0883 | 14.0883 | 14.0883 | 14.0883
| $1,000 - $7,500 | 0.50434 | 0.50388 | 0.50729 | 0.48939 | 0.48928 | 0.49181 | 0.49381 | 0.4972 | 0.49949 | 0.50597 | 0.50973 | 0.51407 | 0.51343 | 0.51149 | 0.51182 | 0.51604 | 0.5218 | 0.52228 | 0.52637 | 0.53001 | 0.53365 | 0.53001 | 0.53365 | 0.53365 | 0.53365 | 0.53365
| $7,500 - MPC | 2.3099 | 2.3078 | 2.3234 | 2.2414 | 2.2409 | 2.2525 | 2.2617 | 2.2772 | 2.2876 | 2.3174 | 2.3346 | 2.3545 | 2.3515 | 2.3426 | 2.3441 | 2.3635 | 2.3899 | 2.392 | 2.4108 | 2.4274 | 2.4441 | 2.4274 | 2.4441 | 2.4441 | 2.4441 | 2.4441
| MPC | 1.6814 | 1.6799 | 1.6913 | 1.6316 | 1.6312 | 1.6396 | 1.6463 | 1.6576 | 1.6652 | 1.6869 | 1.6994 | 1.7139 | 1.7117 | 1.7053 | 1.7064 | 1.7204 | 1.7396 | 1.7412 | 1.7549 | 1.767 | 1.7791 | 1.767 | 1.7791 | 1.7791 | 1.7791 | 1.7791
Winter
| Price band | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
| $300 - $500 | 5.6148 | 5.6257 | 5.6642 | 5.513 | 5.5163 | 5.5574 | 5.5486 | 5.6025 | 5.6803 | 5.7243 | 5.7848 | 5.7911 | 5.8158 | 5.8311 | 5.8284 | 5.8424 | 5.8915 | 5.9339 | 5.9686 | 6.0036 | 6.0387 | 6.0036 | 6.0387 | 6.0387 | 6.0387 | 6.0387
| $500 - $1,000 | 13.3542 | 13.38 | 13.4715 | 13.1121 | 13.1198 | 13.2177 | 13.1967 | 13.3249 | 13.51 | 13.6145 | 13.7585 | 13.7734 | 13.8321 | 13.8685 | 13.8621 | 13.8955 | 14.0121 | 14.113 | 14.1956 | 14.2789 | 14.3623 | 14.2789 | 14.3623 | 14.3623 | 14.3623 | 14.3623
| $1,000 - $7,500 | 0.50584 | 0.50682 | 0.51029 | 0.49667 | 0.49696 | 0.50067 | 0.49988 | 0.50473 | 0.51174 | 0.5157 | 0.52116 | 0.52172 | 0.52394 | 0.52532 | 0.52508 | 0.52635 | 0.53076 | 0.53458 | 0.53771 | 0.54087 | 0.54403 | 0.54087 | 0.54403 | 0.54403 | 0.54403 | 0.54403
| $7,500 - MPC | 2.3168 | 2.3212 | 2.3371 | 2.2748 | 2.2761 | 2.2931 | 2.2894 | 2.3117 | 2.3438 | 2.3619 | 2.3869 | 2.3895 | 2.3997 | 2.406 | 2.4049 | 2.4107 | 2.4309 | 2.4484 | 2.4627 | 2.4772 | 2.4916 | 2.4772 | 2.4916 | 2.4916 | 2.4916 | 2.4916
| MPC | 1.6864 | 1.6897 | 1.7012 | 1.6559 | 1.6568 | 1.6692 | 1.6665 | 1.6827 | 1.7061 | 1.7193 | 1.7375 | 1.7394 | 1.7468 | 1.7514 | 1.7506 | 1.7548 | 1.7695 | 1.7822 | 1.7927 | 1.8032 | 1.8137 | 1.8032 | 1.8137 | 1.8137 | 1.8137 | 1.8137

## Effective LRET
TOC
Large-scale Renewable Energy Target (LRET)
Source: AEMO 2018 ISP Assumptions Workbook
Effective LRET as used in the 2018 AEMO ISP. For details of the underlying components, please refer to the ISP Assumptions Workbook
| Financial year | Base Target (including grandfathered hydro) (GWh) | GreenPower (GWh) | Desalination (GWh) | Effective Target (GWh) | Penalty Price ($/MWh)1
| 2018-19 | 39546.0595 | 656.5 | 103.0796 | 40306 | 90.5923
| 2019-20 | 41732.913 | 566 | 101.9204 | 42401 | 88.3828
| 2020-21 | 42469.555 | 487.5 | 101.189 | 43058 | 86.2271
| 2021-22 | 42112.98 | 420 | 101.189 | 42634 | 84.124
| 2022-23 | 42112.98 | 362 | 101.189 | 42576 | 82.0722
| 2023-24 | 42112.98 | 312 | 101.353 | 42526 | 80.0704
| 2024-25 | 42112.98 | 269 | 101.189 | 42483 | 78.1175
| 2025-26 | 42112.98 | 232 | 101.189 | 42446 | 76.2122
| 2026-27 | 42112.98 | 200 | 101.189 | 42414 | 74.3533
| 2027-28 | 42112.98 | 172.5 | 101.353 | 42387 | 72.5399
| 2028-29 | 42112.98 | 149 | 101.189 | 42363 | 70.7706
| 2029-30 | 42112.98 | 128.5 | 101.189 | 42343 | 69.0445
1. Penalty price is calculated as an uplift of the $65 nominal penalty scaled by a 30% corporate tax rate and a 2.5% annual CPI adjustment

## VRET
TOC
Victorian Renewable Energy Target (VRET)
Source: AEMO 2018 ISP Assumptions Workbook
25 % renewable energy generation by 2020, 40 % renewable energy generation by 2025 and 50 % by 2030. This is indicative (as per the ISP) and the build out to meet the VRET will vary across scenarios and will be updated during the modelling.
New entry renewable capacity (MW)
| Financial year | Solar | Wind | Total
| 2019-20 | 200 | 500 | 700
| 2020-21 | 360 | 900 | 1260
| 2021-22 | 520 | 1300 | 1820
| 2022-23 | 680 | 1700 | 2380
| 2023-24 | 840 | 2100 | 2940
| 2024-25 | 1000 | 2500 | 3500
| 2025-26 | 1160 | 2900 | 4060
| 2026-27 | 1320 | 3300 | 4620
| 2027-28 | 1480 | 3700 | 5180
| 2028-29 | 1640 | 4100 | 5740
| 2029-30 | 1800 | 4500 | 6300

## QRET
TOC
Queensland Renewable Energy Target (QRET)
Source: AEMO 2018 ISP Assumptions Workbook
50% of Queensland consumption to be provided by renewable generation by 2030 target
The trajectory to achieve the 2030 target across each scenario is as assumed in the 2018 AEMO ISP Assumptions Workbook. The build out to meet the QRET target across all scenarios will be updated by the modelling.
Queensland large-scale renewable generation (GWh)
|  | Financial year | Neutral | Fast Change | Slow Change
|  | 2020-21 | 0 | 0 | 0
|  | 2021-22 | 0 | 400 | 0
|  | 2022-23 | 2400 | 2900 | 1400
|  | 2023-24 | 4700 | 5500 | 3400
|  | 2024-25 | 7200 | 8200 | 5400
|  | 2025-26 | 10100 | 11000 | 7500
|  | 2026-27 | 12600 | 14300 | 9600
|  | 2027-28 | 15200 | 17300 | 11500
|  | 2028-29 | 17800 | 20300 | 13400
|  | 2029-30 | 20500 | 23600 | 15500
Trajectory of total large scale generation of renewable energy required, including Q400 auction eligible, as calculated by the QLD Government Expert Panel report:
https://www.dnrm.qld.gov.au/__data/assets/pdf_file/0018/1259010/qreep-renewable-energy-target-report.pdf

## Emission Trajectory
TOC
Emissions target trajectories
Source: AEMO 2018 ISP Assumptions Workbook
Emissions reduction targets are expressed as a percentage of total emissions across all sectors. This table includes electricity NEM generation emissions only.
| Financial Year | 28% to 70% Emissions Reduction Target | 52% to 90% Emissions Reduction Target
(Mt CO2-e)
| 2020-21 | 142 | 142
| 2021-22 | 140.5296 | 136.2446
| 2022-23 | 139.0592 | 130.4891
| 2023-24 | 137.5887 | 124.7337
| 2024-25 | 136.1183 | 118.9783
| 2025-26 | 134.6479 | 113.2228
| 2026-27 | 133.1775 | 107.4674
| 2027-28 | 131.7071 | 101.712
| 2028-29 | 130.2366 | 95.9566
| 2029-30 | 128.7662 | 90.2011
| 2030-31 | 127.2958 | 84.4764
| 2031-32 | 123.3412 | 81.065
| 2032-33 | 119.3866 | 77.6536
| 2033-34 | 115.4319 | 74.2423
| 2034-35 | 111.4773 | 70.8309
| 2035-36 | 107.5227 | 67.4195
| 2036-37 | 103.5681 | 64.0081
| 2037-38 | 99.6134 | 60.5968
| 2038-39 | 95.6588 | 57.1854
| 2039-40 | 91.7042 | 53.774
| 2040-41 | 87.7496 | 50.3627
| 2041-42 | 83.7949 | 46.9513
| 2042-43 | 79.8403 | 43.5399
| 2043-44 | 75.8857 | 40.1285
| 2044-45 | 71.9311 | 36.7172
| 2045-46 | 67.9764 | 33.3058
| 2046-47 | 64.0218 | 29.8944
| 2047-48 | 60.0672 | 26.483
| 2048-49 | 56.1125 | 23.0717
| 2049-50 | 52.1579 | 19.6603
2030 emissions reduction targets are calculated from 2005 levels.
2050 emissions reduction targets are calculated from 2005 levels for the 90% trajectory, and 2016 levels for the 70% trajectory.
The emissions trajectory starts at estimated emissions for 2020-21.

## Financial assumptions
TOC
Weighted average cost of capital (WACC)
Value represents real, pre tax WACC.
| Asset Class | WACC
| Transmission network capital costs | 4.6%
| Generator capital costs | 6%
| System | Value of customer reliability (VCR $/MWh)
| VCR (NEM aggregate) | 33460
* This is based on the last NEM wide review of VCR undertaken in 2014 by AEMO.
| Asset Class | Discount Rate
| System | 7.04% | * Sensitivities will be conducted to this value.

## Build cost
TOC
Build cost ($/kW) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Cost to construct new generation, not including connection costs. Battery installations assumes 2 hours of storage. Pumped hydro installations assumes 6 hours of storage
Slow and rapid scenarios use the Neutral cost trajectories, except for technologies specified
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
| Neutral | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Biomass | 3812.573 | 3810.8215 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.633 | 3807.4023 | 3807.0011 | 3806.991 | 3806.9801 | 3806.9521 | 3806.9404 | 3806.9281 | 3806.9154 | 3806.9154 | 3806.8825 | 3806.8825 | 3806.8825 | 3806.8825 | 3806.8204
| CCGT | 1522.597 | 1522.3455 | 1522.2333 | 1521.9143 | 1521.6068 | 1521.3106 | 1521.0253 | 1520.3583 | 1519.3399 | 1518.3593 | 1517.4153 | 1516.5067 | 1515.6324 | 1514.7912 | 1513.982 | 1513.2038 | 1512.4555 | 1512.0988 | 1510.5564 | 1509.0771 | 1507.6585 | 1506.2983 | 1504.9943 | 1503.7444 | 1502.5464 | 1501.3986
| OCGT | 1024.191 | 1019.07 | 1013.9747 | 1008.9048 | 1003.8603 | 998.841 | 993.8468 | 988.8775 | 983.9331 | 979.0135 | 974.1184 | 969.2478 | 964.4016 | 959.5796 | 954.7817 | 950.0078 | 945.2577 | 940.5314 | 935.8288 | 931.1496 | 926.4939 | 921.8614 | 917.2521 | 912.6658 | 908.1025 | 903.562
| Single-axis Tracking Solar PV2 | 1658.5597 | 1514.3147 | 1442.1673 | 1382.9355 | 1335.8678 | 1288.6271 | 1246.5478 | 1201.0589 | 1165.0481 | 1097.3554 | 1048.8028 | 1004.113 | 967.614 | 926.7615 | 883.1078 | 862.981 | 828.3659 | 809.9948 | 793.0354 | 777.3249 | 762.6566 | 748.5026 | 735.9584 | 725.3187 | 713.5689 | 702.4491
| Solar Thermal Central Receiver (6 hrs storage) | 3347.4193 | 3347.4193 | 3347.4193 | 3347.4193 | 3347.4193 | 3347.4193 | 3344.4842 | 3183.3405 | 3076.0878 | 2947.784 | 2877.4435 | 2835.1113 | 2830.5544 | 2732.1485 | 2661.0726 | 2607.3749 | 2565.4125 | 2531.7472 | 2504.1646 | 2481.1738 | 2461.7346 | 2445.0989 | 2430.7149 | 2418.1667 | 2407.1349 | 2368.2344
| Wind | 1962.198 | 1952.9152 | 1949.1801 | 1936.4747 | 1929.0627 | 1927.4373 | 1926.854 | 1926.7673 | 1926.6731 | 1926.5223 | 1903.3766 | 1879.6497 | 1864.0069 | 1851.3111 | 1841.4001 | 1822.6868 | 1791.7975 | 1780.5975 | 1770.513 | 1761.7294 | 1753.5092 | 1735.7746 | 1732.1319 | 1729.1091 | 1726.6038 | 1724.4679
| Pumped Hydro (6hrs storage) | 1392.3437 | 1385.382 | 1378.455 | 1371.5628 | 1364.705 | 1357.8814 | 1351.092 | 1344.3366 | 1337.6149 | 1330.9268 | 1324.2722 | 1317.6508 | 1311.0626 | 1304.5072 | 1297.9847 | 1291.4948 | 1285.0373 | 1278.6121 | 1272.2191 | 1265.858 | 1259.5287 | 1253.231 | 1246.9649 | 1240.7301 | 1234.5264 | 1228.3538
| Large Scale Battery Storage (2hrs storage) | 1226.0533 | 1183.8196 | 1160.1378 | 1137.1024 | 1115.4295 | 1093.9749 | 1072.7521 | 1051.9371 | 1022.8382 | 1001.4106 | 981.1461 | 962.1686 | 942.5852 | 923.4768 | 904.5434 | 885.908 | 868.8697 | 852.637 | 837.0261 | 822.0987 | 807.5106 | 793.3348 | 779.3779 | 765.3244 | 751.9561 | 738.9443
| Black Coal (HELE) | 3296.9207 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7678 | 3280.7636 | 3280.7636 | 3280.7636 | 3280.7636 | 3280.7636
| Slow | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Single-axis Tracking Solar PV2 | 1819.5705 | 1747.448 | 1711.3743 | 1681.7584 | 1658.2245 | 1634.6042 | 1613.5646 | 1590.8201 | 1572.8147 | 1538.9684 | 1514.692 | 1492.3471 | 1474.0977 | 1453.6714 | 1431.8446 | 1421.7812 | 1404.4736 | 1395.288 | 1386.8084 | 1378.9531 | 1371.619 | 1364.542 | 1358.2699 | 1352.95 | 1347.0751 | 1341.5152
| Solar Thermal Central Receiver (6 hrs storage) | 3923.3215 | 3923.3215 | 3923.3215 | 3923.3215 | 3923.3215 | 3923.3215 | 3921.854 | 3841.2821 | 3787.6558 | 3723.5039 | 3688.3336 | 3667.1675 | 3664.889 | 3615.6861 | 3580.1482 | 3553.2993 | 3532.3181 | 3515.4855 | 3501.6942 | 3490.1988 | 3480.4792 | 3472.1613 | 3464.9693 | 3458.6952 | 3453.1793 | 3433.7291
| Wind | 1967.8424 | 1963.201 | 1961.3335 | 1954.9808 | 1951.2748 | 1950.462 | 1950.1704 | 1950.1271 | 1950.0799 | 1950.0045 | 1938.4317 | 1926.5683 | 1918.7469 | 1912.399 | 1907.4435 | 1898.0868 | 1882.6422 | 1877.0422 | 1871.9999 | 1867.6081 | 1863.498 | 1854.6307 | 1852.8094 | 1851.298 | 1850.0453 | 1848.9774
| Large Scale Battery Storage (2hrs storage) | 1363.933 | 1342.8161 | 1330.9752 | 1319.4575 | 1308.6211 | 1297.8938 | 1287.2824 | 1276.8749 | 1262.3254 | 1251.6116 | 1241.4794 | 1231.9906 | 1222.1989 | 1212.6447 | 1203.178 | 1193.8603 | 1185.3412 | 1177.2248 | 1169.4194 | 1161.9557 | 1154.6616 | 1147.5737 | 1140.5953 | 1133.5685 | 1126.8844 | 1120.3785
| Fast | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Solar Thermal Central Receiver (6 hrs storage) | 2771.517 | 2771.517 | 2771.517 | 2771.517 | 2771.517 | 2771.517 | 2767.1145 | 2525.3989 | 2364.5199 | 2172.0642 | 2066.5534 | 2003.0551 | 1996.2197 | 1848.6108 | 1741.997 | 1661.4505 | 1598.5069 | 1548.009 | 1506.635 | 1472.1488 | 1442.99 | 1418.0364 | 1396.4604 | 1377.6381 | 1361.0905 | 1302.7397
| Pumped Hydro (6hrs storage) | 1385.3294 | 1374.8868 | 1364.4965 | 1354.158 | 1343.8713 | 1333.636 | 1323.4519 | 1313.3187 | 1303.2362 | 1293.2041 | 1283.2221 | 1273.2901 | 1263.4077 | 1253.5748 | 1243.7909 | 1234.0561 | 1224.3699 | 1214.7321 | 1205.1425 | 1195.6008 | 1186.1069 | 1176.6604 | 1167.2612 | 1157.909 | 1148.6035 | 1139.3445
| Large Scale Battery Storage (2hrs storage) | 1088.1736 | 1024.8231 | 989.3004 | 954.7473 | 922.2379 | 890.056 | 858.2218 | 826.9993 | 783.351 | 751.2095 | 720.8128 | 692.3465 | 662.9715 | 634.3089 | 605.9088 | 577.9557 | 552.3982 | 528.0492 | 504.6329 | 482.2418 | 460.3596 | 439.0959 | 418.1606 | 397.0802 | 377.0278 | 357.5102

## Refurbishment
TOC
Refurbishment
Source: AEMO 2018 ISP Assumptions Workbook
Refurbishment costs from the 2018 ISP are scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
Refurbishment timing
Refurbishment costs are incurred at the following dates for the existing generators shown below. Unit refurbishment is staggered within a power station, one unit at a time at six month intervals.
| Generator | First refurbishment | Second refurbishment
| Bayswater | 2025
| Eraring | 2024
| Mount Piper | 2023 | 2033
| Vales Point | 2022
| Callide B | 2028
| Callide Power Plant | 2031 | 2041
| Kogan Creek | 2037 | 2047
| Millmerran | 2032 | 2042
| Stanwell | 2026 | 2036
| Tarong | 2026
| Tarong North | 2033 | 2043
| Loy Yang A | 2028 | 2038
| Loy Yang B | 2026 | 2036
| Yallourn | 2022 | 2032
Refurbishment cost
| Generator class | Refurbishment cost ($/MW) - June 2018 dollars
| Black coal | 154774.6886
| Brown coal | 252997.6919
| Steam Turbine Gas | 103183.1257

## Retirement
TOC
Retirement
Source: 2018 AEMO ISP, AEMO generation information page, AGL announcements
| End of technical life | [7 empty] | Retirement cost
| As per the 2018 AEMO ISP. The model may retire these units earlier if economic to do so. | [7 empty] | As per the 2018 AEMO ISP, this is the retirement/rehabilitation cost. The costs have been scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
| Generator | Financial year beginning | Announced | Row | Fuel | Region | Capacity (MW) |  | Technology Type | Cost (June 2018 $/MW)
| Torrens Island A | 2021 | 0 | 155 | Gas | SA | 480 |  | Black Coal | 53206.3928
| Mackay GT | 2021 | 1 | 13 | Gas | QLD | 34 |  | Brown Coal | 85130.2285
| Liddell | 2022 | 1 | 53 | Coal | NSW | 1800 |  | CCGT | 10641.2786
| Vales Point | 2028 | 0 | 55 | Coal | NSW | 1320 |  | Pumped hydro | 106412.7856
| Gladstone | 2029 | 0 | 3 | Coal | QLD | 1680 |  | Wind | 10641.2786
| Eraring | 2031 | 0 | 52 | Coal | NSW | 2880 |  | Single-axis tracking solar | 21282.5571
| Newport | 2031 | 0 | 105 | Gas | VIC | 510
| Yallourn | 2032 | 0 | 99 | Coal | VIC | 1528
| Bayswater | 2035 | 1 | 51 | Coal | NSW | 2740
| Tarong | 2036 | 0 | 7 | Coal | QLD | 1400
| Callide B | 2038 | 0 | 1 | Coal | QLD | 700
| Mount Piper | 2043 | 0 | 54 | Coal | NSW | 1400
| Stanwell | 2046 | 0 | 6 | Coal | QLD | 1460
| Loy Yang A | 2048 | 1 | 97 | Coal | VIC | 2210
| Callide Power Plant | 2051 | 0 | 2 | Coal | QLD | 840
| Millmerran | 2052 | 0 | 5 | Coal | QLD | 852
| Tarong North | 2053 | 0 | 8 | Coal | QLD | 443
| Loy Yang B | 2056 | 0 | 98 | Coal | VIC | 1150
| Kogan Creek | 2057 | 0 | 4 | Coal | QLD | 750
[5 empty] | Coal |  | 23153
[9 empty] | Financial Year | Remaining Coal Capacity | QLD | NSW | VIC
[8 empty] | 2019 | 2019-20 | 23153 | 0 | 0 | 0
[8 empty] | 2020 | 2020-21 | 23153 | 0 | 0 | 0
[8 empty] | 2021 | 2021-22 | 23153 | 0 | 0 | 0
[8 empty] | 2022 | 2022-23 | 21353 | 0 | 1800 | 0
[8 empty] | 2023 | 2023-24 | 21353 | 0 | 0 | 0
[8 empty] | 2024 | 2024-25 | 21353 | 0 | 0 | 0
[8 empty] | 2025 | 2025-26 | 21353 | 0 | 0 | 0
[8 empty] | 2026 | 2026-27 | 21353 | 0 | 0 | 0
[8 empty] | 2027 | 2027-28 | 21353 | 0 | 0 | 0
[8 empty] | 2028 | 2028-29 | 20033 | 0 | 1320 | 0
[8 empty] | 2029 | 2029-30 | 18353 | 1680 | 0 | 0
[8 empty] | 2030 | 2030-31 | 18353 | 0 | 0 | 0
[8 empty] | 2031 | 2031-32 | 15473 | 0 | 2880 | 0
[8 empty] | 2032 | 2032-33 | 13945 | 0 | 0 | 1528
[8 empty] | 2033 | 2033-34 | 13945 | 0 | 0 | 0
[8 empty] | 2034 | 2034-35 | 13945 | 0 | 0 | 0
[8 empty] | 2035 | 2035-36 | 11205 | 0 | 2740 | 0
[8 empty] | 2036 | 2036-37 | 9805 | 1400 | 0 | 0
[8 empty] | 2037 | 2037-38 | 9805 | 0 | 0 | 0
[8 empty] | 2038 | 2038-39 | 9105 | 700 | 0 | 0
[8 empty] | 2039 | 2039-40 | 9105 | 0 | 0 | 0
[8 empty] | 2040 | 2040-41 | 9105 | 0 | 0 | 0
[8 empty] | 2041 | 2041-42 | 9105 | 0 | 0 | 0
[8 empty] | 2042 | 2042-43 | 9105 | 0 | 0 | 0
[8 empty] | 2043 | 2043-44 | 7705 | 0 | 1400 | 0
[8 empty] | 2044 | 2044-45 | 7705 | 0 | 0 | 0
[8 empty] | 2045 | 2045-46 | 7705 | 0 | 0 | 0
[8 empty] | 2046 | 2046-47 | 6245 | 1460 | 0 | 0
[8 empty] | 2047 | 2047-48 | 6245 | 0 | 0 | 0
[8 empty] | 2048 | 2048-49 | 4035 | 0 | 0 | 2210
[8 empty] | 2049 | 2049-50 | 4035 | 0 | 0 | 0
[8 empty] | 2050 | 2050-51 | 4035 | 0 | 0 | 0
[8 empty] | 2051 | 2051-52 | 3195 | 840 | 0 | 0
[8 empty] | 2052 | 2052-53 | 2343 | 852 | 0 | 0
[8 empty] | 2053 | 2053-54 | 1900 | 443 | 0 | 0
[8 empty] | 2054 | 2054-55 | 1900 | 0 | 0 | 0
[8 empty] | 2055 | 2055-56 | 1900 | 0 | 0 | 0
[8 empty] | 2056 | 2056-57 | 750 | 0 | 0 | 1150
[8 empty] | 2057 | 2057-58 | 0 | 750 | 0 | 0

## Gas prices
TOC
Gas prices ($/GJ) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
Real June 2018 AUD/GJ
For new entrant gas plant:
| Neutral | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| QLD | 9.4867 | 9.4867 | 9.4867 | 9.4867 | 9.0098 | 8.5228 | 8.0459 | 7.569 | 7.569 | 7.6502 | 7.6502 | 8.0358 | 8.2387 | 8.2387 | 8.2387 | 8.2387 | 8.2387 | 8.5126 | 8.5126 | 8.5126 | 8.5126 | 8.5126 | 8.5126 | 8.5126 | 8.5126 | 8.5126
| NSW | 10.1563 | 10.1563 | 10.1563 | 10.1563 | 9.8621 | 9.5678 | 9.2837 | 8.9895 | 8.9895 | 8.9895 | 8.9895 | 8.9895 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3345 | 9.3243 | 9.3243 | 9.3243 | 9.3243 | 9.3243
| VIC | 10.2578 | 10.7651 | 11.2724 | 10.7651 | 10.481 | 10.1868 | 9.9027 | 9.6186 | 9.6186 | 9.72 | 9.72 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012 | 9.8012
| SA | 10.065 | 10.065 | 10.065 | 10.065 | 9.7505 | 9.4258 | 9.1011 | 8.7764 | 8.7764 | 8.9591 | 8.9591 | 8.9591 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939 | 9.2939
| TAS | 10.15 | 10.15 | 10.15 | 10.15 | 10.353 | 10.556 | 10.759 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962 | 10.962
| Strong | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| QLD | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 9.9432 | 9.3852 | 8.8272 | 8.2691 | 8.2691 | 8.3706 | 8.3706 | 8.8576 | 9.1214 | 9.1214 | 9.1214 | 9.1214 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968 | 9.4968
| NSW | 11.1709 | 11.1709 | 11.1709 | 11.1709 | 10.8564 | 10.5419 | 10.2273 | 9.9128 | 9.9128 | 9.9128 | 9.9128 | 9.9128 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3288 | 10.3288 | 10.3288 | 10.3288 | 10.3288
| VIC | 11.2724 | 11.7797 | 12.287 | 11.7797 | 11.5159 | 11.2521 | 10.9883 | 10.7245 | 10.7346 | 10.8564 | 10.8564 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376 | 10.9376
| SA | 10.7042 | 10.7042 | 10.7042 | 10.7042 | 10.4506 | 10.1868 | 9.9331 | 9.6794 | 9.6794 | 9.9027 | 9.9027 | 9.9027 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389 | 10.3389
| TAS | 11.4492 | 11.4492 | 11.4492 | 11.4492 | 11.5913 | 11.7233 | 11.8552 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973 | 11.9973
| Weak | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| QLD | 8.6953 | 8.6953 | 8.6953 | 8.6953 | 8.259 | 7.8328 | 7.3966 | 6.9704 | 6.9704 | 6.9704 | 6.9704 | 7.2444 | 7.2444 | 7.2444 | 7.2444 | 7.2444 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168 | 7.4168
| NSW | 9.2229 | 9.2229 | 9.2229 | 9.2229 | 8.9692 | 8.7054 | 8.4518 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.1981 | 8.188 | 8.188 | 8.188 | 8.188 | 8.188
| VIC | 9.2736 | 9.7809 | 10.2882 | 9.7809 | 9.4461 | 9.1113 | 8.7866 | 8.4518 | 8.4518 | 8.4518 | 8.4518 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329 | 8.5329
| SA | 9.0199 | 9.0199 | 9.0199 | 9.0199 | 8.7967 | 8.5735 | 8.3503 | 8.1271 | 8.1271 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372 | 8.1372
| TAS | 9.135 | 9.135 | 9.135 | 9.135 | 9.3075 | 9.4699 | 9.6425 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815 | 9.815
For new entrant liquid fuel plant:
| All scenarios | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| All Regions | 35.5351 | 35.0784 | 34.5404 | 34.0025 | 33.5051 | 33.0382 | 32.612 | 32.2364 | 31.9116 | 31.5766 | 31.2518 | 30.9473 | 30.6733 | 30.4297 | 30.1962 | 29.9729 | 29.7598 | 29.5568 | 29.3639 | 29.1609 | 28.9782 | 28.6027 | 28.6027 | 28.6027 | 28.6027 | 28.6027
Existing Gas Plant
Neutral
| Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Bairnsdale | 10.6673 | 11.1748 | 10.6673 | 10.4356 | 10.2039 | 9.9722 | 9.7406 | 9.7406 | 9.7406 | 9.7406 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213
| Barcaldine | 9.837 | 9.837 | 9.837 | 9.4966 | 9.1561 | 8.8157 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752 | 8.4752
| Barker Inlet | 9.6425 | 9.6425 | 9.6425 | 9.3529 | 9.0632 | 8.7736 | 8.4839 | 8.5078 | 9.3033 | 9.3033 | 9.303 | 9.3033 | 9.3032 | 9.3032 | 9.3032 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031
| Bell Bay Three | 10.15 | 10.15 | 10.15 | 10.3542 | 10.5584 | 10.7626 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669
| Braemar | 9.2353 | 9.2353 | 9.2353 | 9.0726 | 8.9099 | 8.7472 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Braemar 2 | 9.2353 | 9.2353 | 9.2353 | 9.0726 | 8.9099 | 8.7472 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Colongra | 10.1635 | 10.1635 | 10.1635 | 9.9609 | 9.7582 | 9.5556 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353
| Condamine | 9.2353 | 9.2353 | 9.2353 | 9.0726 | 8.9099 | 8.7472 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Darling Downs | 9.8533 | 9.8533 | 9.8533 | 9.2785 | 8.7037 | 8.1289 | 7.5541 | 7.5541 | 7.5541 | 7.5541 | 7.5541 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Dry Creek | 10.7974 | 10.7974 | 10.7974 | 10.4195 | 10.0417 | 9.6639 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861
| Hallett | 9.8273 | 9.8273 | 9.8273 | 9.6996 | 9.5719 | 9.4442 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165
| Jeeralang | 10.8291 | 11.3366 | 10.8291 | 10.557 | 10.2848 | 10.0127 | 9.7406 | 9.7406 | 9.7406 | 9.7406 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213
| Ladbroke Grove | 9.7102 | 9.7102 | 9.7102 | 9.3508 | 8.9913 | 8.6319 | 8.2724 | 8.2726 | 8.2729 | 8.2728 | 8.2726 | 9.3033 | 9.3032 | 9.3032 | 9.3032 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031
| Laverton North | 10.665 | 11.1725 | 10.665 | 10.4335 | 10.2019 | 9.9703 | 9.7388 | 9.7388 | 9.7389 | 9.7388 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196
| Mintaro | 10.8246 | 10.8246 | 10.8246 | 10.4476 | 10.0706 | 9.6936 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165 | 9.3165
| Mortlake OCGT | 11.0113 | 11.5188 | 11.0113 | 10.6605 | 10.3097 | 9.9589 | 9.6081 | 9.6081 | 9.6081 | 9.6081 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888 | 9.6888
| Newport | 10.8269 | 11.3344 | 10.8269 | 10.5549 | 10.2828 | 10.0108 | 9.7388 | 9.7388 | 9.7389 | 9.7388 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196
| Oakey | 9.7856 | 9.7856 | 9.7856 | 9.2806 | 8.7756 | 8.2706 | 7.7656 | 7.7894 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Osborne | 9.7102 | 9.7102 | 9.7102 | 9.3508 | 8.9913 | 8.6319 | 8.2724 | 8.2726 | 8.2729 | 8.2728 | 8.2726 | 9.3033 | 9.3032 | 9.3032 | 9.3032 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031
| Pelican Point | 10.7974 | 10.7974 | 10.7974 | 10.4195 | 10.0417 | 9.6639 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861 | 9.2861
| Quarantine | 9.7102 | 9.7102 | 9.7102 | 9.3508 | 8.9913 | 8.6319 | 8.2724 | 8.2726 | 8.2729 | 8.2728 | 8.2726 | 9.3033 | 9.3032 | 9.3032 | 9.3032 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031
| Roma | 9.135 | 9.135 | 9.135 | 8.5602 | 7.9854 | 7.4106 | 6.8358 | 6.8358 | 6.8358 | 6.8358 | 6.8358 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662 | 7.8662
| Smithfield | 10.159 | 10.159 | 10.159 | 9.8677 | 9.5765 | 9.2853 | 8.994 | 8.9943 | 8.9959 | 8.9959 | 8.9953 | 9.3376 | 9.3377 | 9.3377 | 9.3378 | 9.3379 | 9.3379 | 9.3379 | 9.3379 | 9.3379 | 9.3278 | 9.3278 | 9.3278 | 9.3278 | 9.3278 | 9.3278
| Somerton | 10.6575 | 11.165 | 10.6575 | 10.2231 | 9.7887 | 9.3543 | 8.9199 | 8.9436 | 9.7389 | 9.7388 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196 | 9.8196
| Swanbank E | 9.135 | 9.135 | 9.135 | 8.9974 | 8.8598 | 8.7222 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846 | 8.5846
| Tallawarra | 10.1635 | 10.1635 | 10.1635 | 9.9609 | 9.7582 | 9.5556 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353 | 9.353
| Tamar Valley | 10.15 | 10.15 | 10.15 | 10.3542 | 10.5584 | 10.7626 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669 | 10.9669
| Torrens Island | 9.6425 | 9.6425 | 9.6425 | 9.3529 | 9.0632 | 8.7736 | 8.4839 | 8.5078 | 9.3033 | 9.3033 | 9.303 | 9.3033 | 9.3032 | 9.3032 | 9.3032 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031 | 9.3031
| Townsville | 10.1345 | 10.1345 | 10.1345 | 9.035 | 7.9356 | 6.8361 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199 | 8.5199
| Uranquinty | 10.15 | 10.15 | 10.15 | 9.6815 | 9.2131 | 8.7446 | 8.2761 | 8.2769 | 8.2818 | 8.2816 | 8.28 | 9.3069 | 9.3071 | 9.3072 | 9.3073 | 9.3077 | 9.3077 | 9.3077 | 9.3077 | 9.3077 | 9.2774 | 9.2774 | 9.2774 | 9.2774 | 9.2774 | 9.2774
| Valley Power | 10.6673 | 11.1748 | 10.6673 | 10.4356 | 10.2039 | 9.9722 | 9.7406 | 9.7406 | 9.7406 | 9.7406 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213 | 9.8213
| Yarwun | 9.363 | 9.363 | 9.363 | 8.2635 | 7.1641 | 6.0646 | 4.9652 | 4.9652 | 4.9652 | 4.9652 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305 | 8.8305
Strong
| Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Bairnsdale | 11.6822 | 12.1897 | 11.6822 | 11.4816 | 11.281 | 11.0804 | 10.8798 | 10.8798 | 10.8798 | 10.8798 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605
| Barcaldine | 10.852 | 10.852 | 10.852 | 10.5021 | 10.1521 | 9.8021 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522 | 9.4522
| Barker Inlet | 10.6619 | 10.6619 | 10.6619 | 10.3236 | 9.9854 | 9.6472 | 9.3089 | 9.3395 | 10.3429 | 10.3428 | 10.3426 | 10.3429 | 10.3428 | 10.3428 | 10.3428 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427
| Bell Bay Three | 11.165 | 11.165 | 11.165 | 11.3724 | 11.5798 | 11.7872 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946
| Braemar | 10.2503 | 10.2503 | 10.2503 | 10.0781 | 9.9059 | 9.7337 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Braemar 2 | 10.2503 | 10.2503 | 10.2503 | 10.0781 | 9.9059 | 9.7337 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Colongra | 11.1785 | 11.1785 | 11.1785 | 10.9741 | 10.7698 | 10.5655 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612
| Condamine | 10.2503 | 10.2503 | 10.2503 | 10.0781 | 9.9059 | 9.7337 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Darling Downs | 10.8683 | 10.8683 | 10.8683 | 10.2168 | 9.5654 | 8.9139 | 8.2624 | 8.2624 | 8.2624 | 8.2624 | 8.2624 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Dry Creek | 10.6575 | 10.6575 | 10.6575 | 10.5745 | 10.4916 | 10.4086 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257
| Hallett | 10.8466 | 10.8466 | 10.8466 | 10.724 | 10.6014 | 10.4787 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561
| Jeeralang | 11.8441 | 12.3516 | 11.8441 | 11.603 | 11.3619 | 11.1209 | 10.8798 | 10.8798 | 10.8798 | 10.8798 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605
| Ladbroke Grove | 10.7296 | 10.7296 | 10.7296 | 10.308 | 9.8864 | 9.4649 | 9.0433 | 9.0435 | 9.0438 | 9.0437 | 9.0435 | 10.3429 | 10.3428 | 10.3428 | 10.3428 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427
| Laverton North | 11.68 | 12.1875 | 11.68 | 11.4795 | 11.279 | 11.0785 | 10.878 | 10.878 | 10.8781 | 10.878 | 10.9588 | 10.9588 | 10.9589 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588
| Mintaro | 10.6848 | 10.6848 | 10.6848 | 10.6026 | 10.5204 | 10.4383 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561 | 10.3561
| Mortlake OCGT | 12.0263 | 12.5338 | 12.0263 | 11.7066 | 11.3868 | 11.067 | 10.7473 | 10.7473 | 10.7473 | 10.7473 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828 | 10.828
| Newport | 11.8418 | 12.3493 | 11.8418 | 11.6009 | 11.3599 | 11.119 | 10.878 | 10.878 | 10.8781 | 10.878 | 10.9588 | 10.9588 | 10.9589 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588
| Oakey | 10.8006 | 10.8006 | 10.8006 | 10.2325 | 9.6643 | 9.0962 | 8.528 | 8.5584 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Osborne | 10.7296 | 10.7296 | 10.7296 | 10.308 | 9.8864 | 9.4649 | 9.0433 | 9.0435 | 9.0438 | 9.0437 | 9.0435 | 10.3429 | 10.3428 | 10.3428 | 10.3428 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427
| Pelican Point | 10.6575 | 10.6575 | 10.6575 | 10.5745 | 10.4916 | 10.4086 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257 | 10.3257
| Quarantine | 10.7296 | 10.7296 | 10.7296 | 10.308 | 9.8864 | 9.4649 | 9.0433 | 9.0435 | 9.0438 | 9.0437 | 9.0435 | 10.3429 | 10.3428 | 10.3428 | 10.3428 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427
| Roma | 10.15 | 10.15 | 10.15 | 9.4985 | 8.847 | 8.1956 | 7.5441 | 7.5441 | 7.5441 | 7.5441 | 7.5441 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432 | 8.8432
| Smithfield | 11.174 | 11.174 | 11.174 | 10.8586 | 10.5433 | 10.228 | 9.9126 | 9.9129 | 9.9145 | 9.9145 | 9.9139 | 10.3458 | 10.3459 | 10.3459 | 10.3459 | 10.3461 | 10.3461 | 10.3461 | 10.3461 | 10.3461 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336
| Somerton | 11.6725 | 12.18 | 11.6725 | 11.2155 | 10.7585 | 10.3015 | 9.8445 | 9.875 | 10.8781 | 10.878 | 10.9588 | 10.9588 | 10.9589 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588 | 10.9588
| Swanbank E | 10.15 | 10.15 | 10.15 | 10.0029 | 9.8557 | 9.7086 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615 | 9.5615
| Tallawarra | 11.1785 | 11.1785 | 11.1785 | 10.9741 | 10.7698 | 10.5655 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612 | 10.3612
| Tamar Valley | 11.7431 | 11.7431 | 11.7431 | 11.8059 | 11.8688 | 11.9317 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946 | 11.9946
| Torrens Island | 10.6619 | 10.6619 | 10.6619 | 10.3236 | 9.9854 | 9.6472 | 9.3089 | 9.3395 | 10.3429 | 10.3428 | 10.3426 | 10.3429 | 10.3428 | 10.3428 | 10.3428 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427 | 10.3427
| Townsville | 11.1495 | 11.1495 | 11.1495 | 9.7963 | 8.4431 | 7.0899 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969 | 9.4969
| Uranquinty | 11.165 | 11.165 | 11.165 | 10.6277 | 10.0903 | 9.553 | 9.0156 | 9.0164 | 9.0213 | 9.0211 | 9.0195 | 10.315 | 10.3152 | 10.3153 | 10.3154 | 10.3158 | 10.3158 | 10.3158 | 10.3158 | 10.3158 | 10.2856 | 10.2856 | 10.2856 | 10.2856 | 10.2856 | 10.2856
| Valley Power | 11.6822 | 12.1897 | 11.6822 | 11.4816 | 11.281 | 11.0804 | 10.8798 | 10.8798 | 10.8798 | 10.8798 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605 | 10.9605
| Yarwun | 10.378 | 10.378 | 10.378 | 9.0248 | 7.6716 | 6.3184 | 4.9652 | 4.9652 | 4.9652 | 4.9652 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074 | 9.8074
Weak
| Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Bairnsdale | 9.6447 | 10.1522 | 9.6447 | 9.3522 | 9.0596 | 8.767 | 8.4745 | 8.4745 | 8.4745 | 8.4745 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552
| Barcaldine | 8.5941 | 8.5941 | 8.5941 | 8.2884 | 7.9828 | 7.6771 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714 | 7.3714
| Barker Inlet | 8.7075 | 8.7075 | 8.7075 | 8.5621 | 8.4168 | 8.2715 | 8.1261 | 8.1314 | 8.1369 | 8.1368 | 8.1366 | 8.1369 | 8.1368 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367
| Bell Bay Three | 9.135 | 9.135 | 9.135 | 9.3043 | 9.4737 | 9.643 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123
| Braemar | 9.1282 | 9.1282 | 9.1282 | 8.7164 | 8.3045 | 7.8926 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Braemar 2 | 9.1282 | 9.1282 | 9.1282 | 8.7164 | 8.3045 | 7.8926 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Colongra | 9.135 | 9.135 | 9.135 | 8.9057 | 8.6765 | 8.4472 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218
| Condamine | 9.1282 | 9.1282 | 9.1282 | 8.7164 | 8.3045 | 7.8926 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Darling Downs | 8.8918 | 8.8918 | 8.8918 | 8.539 | 8.1863 | 7.8335 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Dry Creek | 9.5976 | 9.5976 | 9.5976 | 9.2281 | 8.8586 | 8.4891 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196
| Hallett | 8.6275 | 8.6275 | 8.6275 | 8.5081 | 8.3888 | 8.2694 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501
| Jeeralang | 9.8066 | 10.3141 | 9.8066 | 9.4736 | 9.1405 | 8.8075 | 8.4745 | 8.4745 | 8.4745 | 8.4745 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552
| Ladbroke Grove | 8.7919 | 8.7919 | 8.7919 | 8.628 | 8.4641 | 8.3003 | 8.1364 | 8.1365 | 8.1369 | 8.1368 | 8.1366 | 8.1369 | 8.1368 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367
| Laverton North | 9.6425 | 10.15 | 9.6425 | 9.3501 | 9.0576 | 8.7652 | 8.4727 | 8.4727 | 8.4728 | 8.4727 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535
| Mintaro | 9.6249 | 9.6249 | 9.6249 | 9.2562 | 8.8875 | 8.5188 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501 | 8.1501
| Mortlake OCGT | 9.9888 | 10.4963 | 9.9888 | 9.5771 | 9.1654 | 8.7537 | 8.342 | 8.342 | 8.342 | 8.342 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 8.4227
| Newport | 9.8044 | 10.3119 | 9.8044 | 9.4714 | 9.1385 | 8.8056 | 8.4727 | 8.4727 | 8.4728 | 8.4727 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535
| Oakey | 8.8074 | 8.8074 | 8.8074 | 8.4732 | 8.1389 | 7.8047 | 7.4705 | 7.4756 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Osborne | 8.7919 | 8.7919 | 8.7919 | 8.628 | 8.4641 | 8.3003 | 8.1364 | 8.1365 | 8.1369 | 8.1368 | 8.1366 | 8.1369 | 8.1368 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367
| Pelican Point | 9.5976 | 9.5976 | 9.5976 | 9.2281 | 8.8586 | 8.4891 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196 | 8.1196
| Quarantine | 8.7919 | 8.7919 | 8.7919 | 8.628 | 8.4641 | 8.3003 | 8.1364 | 8.1365 | 8.1369 | 8.1368 | 8.1366 | 8.1369 | 8.1368 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367
| Roma | 8.1735 | 8.1735 | 8.1735 | 7.8207 | 7.468 | 7.1152 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624 | 6.7624
| Smithfield | 9.2243 | 9.2243 | 9.2243 | 8.9689 | 8.7134 | 8.458 | 8.2025 | 8.2028 | 8.2044 | 8.2043 | 8.2038 | 8.2026 | 8.2027 | 8.2027 | 8.2027 | 8.2029 | 8.2029 | 8.2029 | 8.2029 | 8.2029 | 8.1928 | 8.1928 | 8.1928 | 8.1928 | 8.1928 | 8.1928
| Somerton | 9.8997 | 10.4072 | 9.8997 | 9.5404 | 9.1811 | 8.8217 | 8.4624 | 8.4676 | 8.4728 | 8.4727 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535 | 8.5535
| Swanbank E | 8.12 | 8.12 | 8.12 | 7.9602 | 7.8004 | 7.6406 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807 | 7.4807
| Tallawarra | 9.135 | 9.135 | 9.135 | 8.9057 | 8.6765 | 8.4472 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218 | 8.218
| Tamar Valley | 9.135 | 9.135 | 9.135 | 9.3043 | 9.4737 | 9.643 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123 | 9.8123
| Torrens Island | 8.7075 | 8.7075 | 8.7075 | 8.5621 | 8.4168 | 8.2715 | 8.1261 | 8.1314 | 8.1369 | 8.1368 | 8.1366 | 8.1369 | 8.1368 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367 | 8.1367
| Townsville | 8.8915 | 8.8915 | 8.8915 | 8.1028 | 7.3141 | 6.5254 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 5.7367 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161 | 7.4161
| Uranquinty | 9.403 | 9.403 | 9.403 | 9.0951 | 8.7872 | 8.4794 | 8.1715 | 8.1723 | 8.1772 | 8.177 | 8.1754 | 8.1718 | 8.1721 | 8.1721 | 8.1722 | 8.1726 | 8.1726 | 8.1726 | 8.1726 | 8.1726 | 8.1424 | 8.1424 | 8.1424 | 8.1424 | 8.1424 | 8.1424
| Valley Power | 9.6447 | 10.1522 | 9.6447 | 9.3522 | 9.0596 | 8.767 | 8.4745 | 8.4745 | 8.4745 | 8.4745 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552 | 8.5552
| Yarwun | 8.12 | 8.12 | 8.12 | 7.3313 | 6.5426 | 5.7539 | 4.9652 | 4.9652 | 4.9652 | 4.9652 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267 | 7.7267

## Coal prices
TOC
Coal prices ($/GJ) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
Real June 2018 AUD/GJ
Existing Coal ($/GJ)
| All scenarios | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Bayswater | 1.6538 | 1.6538 | 1.6741 | 1.7248 | 1.7756 | 1.8466 | 1.8466 | 2.0292 | 2.4351 | 2.6989 | 2.8308 | 2.9322 | 2.9728 | 3.0236 | 3.0743 | 3.1453 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859
| Callide | 2.1104 | 2.151 | 2.1916 | 2.2119 | 2.2322 | 2.2524 | 2.3032 | 2.3336 | 2.3438 | 2.3742 | 2.4046 | 2.4554 | 2.709 | 2.9424 | 3.0033 | 3.0844 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149 | 3.1149
| Eraring | 2.709 | 2.8815 | 2.9424 | 2.9931 | 3.0743 | 3.2265 | 3.3584 | 3.3888 | 3.4903 | 3.612 | 3.7439 | 3.8353 | 3.8961 | 3.957 | 4.028 | 4.1193 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701
| Gladstone | 2.709 | 2.8511 | 2.9018 | 2.9728 | 3.0438 | 3.196 | 3.3178 | 3.3482 | 3.4091 | 3.5106 | 3.6628 | 3.7541 | 3.8048 | 3.8657 | 3.9367 | 4.028 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788 | 4.0788
| Kogan Creek | 1.5828 | 1.5828 | 1.5828 | 1.6031 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234 | 1.6234
| Loy Yang A & B | 0.6595 | 0.6595 | 0.6595 | 0.6595 | 0.66965 | 0.66965 | 0.66965 | 0.66965 | 0.67979 | 0.67979 | 0.67979 | 0.68994 | 0.68994 | 0.70009 | 0.70009 | 0.71023 | 0.71023 | 0.72038 | 0.72038 | 0.73052 | 0.74067 | 0.74067 | 0.74067 | 0.74067 | 0.74067 | 0.74067
| Millmerran | 1.2987 | 1.3089 | 1.3089 | 1.319 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3393 | 1.3494 | 1.3494 | 1.3494 | 1.3494 | 1.3494 | 1.3494 | 1.3596 | 1.3596 | 1.3596 | 1.3596 | 1.3596 | 1.3596 | 1.3596
| Mt Piper | 2.3133 | 2.4351 | 2.4858 | 2.5467 | 2.6076 | 2.7496 | 2.8612 | 2.9424 | 3.0946 | 3.2163 | 3.3584 | 3.4801 | 3.5309 | 3.5715 | 3.6222 | 3.7034 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541 | 3.7541
| Stanwell | 2.3945 | 2.4554 | 2.4858 | 2.5061 | 2.5264 | 2.5467 | 2.567 | 2.7192 | 3.0946 | 3.3787 | 3.5207 | 3.6526 | 3.7034 | 3.7541 | 3.815 | 3.9164 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957
| Tarong | 2.8409 | 2.8511 | 2.8511 | 2.8714 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917
| Vales Point | 2.6076 | 2.78 | 2.8409 | 2.9931 | 3.0743 | 3.2265 | 3.3584 | 3.3888 | 3.4903 | 3.612 | 3.7439 | 3.8353 | 3.8961 | 3.957 | 4.028 | 4.1193 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701 | 4.1701
| Yallourn | 0.63921 | 0.64935 | 0.64935 | 0.6595 | 0.6595 | 0.6595 | 0.6595 | 0.66965 | 0.66965 | 0.66965 | 0.67979 | 0.67979 | 0.67979 | 0.68994 | 0.68994 | 0.70009 | 0.70009 | 0.71023 | 0.71023 | 0.72038 | 0.73052 | 0.73052 | 0.73052 | 0.73052 | 0.73052 | 0.73052
| Liddell | 1.6538 | 1.6538 | 1.6741 | 1.7248 | 1.7756 | 1.8466 | 1.8466 | 2.0292 | 2.4351 | 2.6989 | 2.8308 | 2.9322 | 2.9728 | 3.0236 | 3.0743 | 3.1453 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859 | 3.1859
New Entrant Coal ($/GJ)
| All scenarios | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| Lower estimate | 2.8409 | 2.8511 | 2.8511 | 2.8714 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917 | 2.8917
| Central estimate | 4.1231 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267 | 3.8267

## Fixed OPEX
TOC
Fixed operating cost ($/kW/year) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Costs that are incurred regardless of energy generated.
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
| Existing and Committed generators |  | New entrant technologies
| Generator | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW/year)
| Bayswater | 55.6654 | Wind | 47.8899
| Eraring | 55.6654 | Solar PV | 30.8849
| Liddell | 59.1054 | OCGT | 4.1193
| Mount Piper | 55.6654 | CCGT | 10.2984
| Vales Point | 55.6654 | Pumped hydro | 5.0731
| Callide B | 56.2909 | Biomass | 128.7041
| Callide Power Plant | 56.2909 | Solar Thermal 6hr Storage | 76.705
| Gladstone | 59.1054 | Reciprocating engine | 15.341
| Kogan Creek | 56.8225 | Black Coal (HELE) | 54.5188
| Millmerran | 54.5188 | Large Scale Battery Storage (2hrs storage) | 0
| Stanwell | 55.6654
| Tarong | 56.2909
| Tarong North | 54.5188
| Loy Yang A | 147.7114
| Loy Yang B | 116.7515
| Yallourn | 153.4448
| Colongra | 14.8024
| Smithfield | 10.4242
| Tallawarra | 10.4242
| Uranquinty | 14.8024
| Barcaldine | 14.8024
| Braemar | 14.8024
| Condamine | 10.4242
| Darling Downs | 10.4242
| Oakey | 14.8024
| Roma | 14.8024
| Swanbank E | 10.4242
| Yabulu (Townsville) | 10.4242
| Yarwun | 10.4242
| Somerton | 14.8024
| Bairnsdale | 14.8024
| Jeeralang A | 14.8024
| Jeeralang B | 14.8024
| Laverton North | 14.8024
| Mortlake | 14.8024
| Newport | 45.4497
| Valley Power | 14.8024
| Hallett GT | 14.8024
| Dry Creek | 14.8024
| Ladbroke Grove | 14.8024
| Mintaro | 14.8024
| Osborne | 10.4242
| Pelican Point | 10.4242
| Quarantine | 14.8024
| Torrens Island A | 44.303
| Torrens Island B | 44.303
| Bell Bay Three | 14.8024
| Tamar Valley | 14.8024
| Hunter Valley GT | 14.8024
| Mackay GT | 14.8024
| Mount Stuart | 14.8024
| Angaston | 15.3445
| Lonsdale | 14.8024
| Port Lincoln | 14.8024
| Port Lincoln 3 | 14.8024
| Port Stanvac | 15.3445
| Snuggery | 14.8024
| All hydro | 59.1054
| All wind | 45.7592
| All solar | 26.0756

## Variable OPEX
TOC
Variable operating cost ($/MWh) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Costs that can be expressed in terms of energy generated, not including fuel costs.
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
| Existing and Committed generators |  | New entrant technologies
| Generator | Variable OPEX ($/MWh)1 | Generator | Variable OPEX ($/MWh)
| Bayswater | 1.0451 | Wind | 15.9599
| Eraring | 1.0451 | Solar PV | 0
| Liddell | 1.0451 | OCGT | 10.2984
| Mount Piper | 1.0451 | CCGT | 7.2038
| Vales Point | 1.0451 | Pumped hydro | 5.0731
| Callide B | 1.0451 | Biomass | 8.2387
| Callide Power Plant | 1.0451 | Solar Thermal 6hr Storage | 6.0725
| Gladstone | 1.0451 | Reciprocating engine | 11.3434
| Kogan Creek | 0.51745 | Black Coal (HELE) | 1.0451
| Millmerran | 3.2265 | Large Scale Battery Storage (2hrs storage) | 0
| Stanwell | 3.2265
| Tarong | 3.2265
| Tarong North | 1.0451
| Loy Yang A | 1.0451
| Loy Yang B | 1.0451
| Yallourn | 1.0451
| Colongra | 8.6547
| Smithfield | 7.2951
| Tallawarra | 7.2951
| Uranquinty | 10.8463
| Barcaldine | 10.8463
| Braemar | 10.8463
| Condamine | 7.2951
| Darling Downs | 7.2951
| Oakey | 10.8463
| Roma | 10.8463
| Swanbank E | 7.2951
| Yabulu (Townsville) | 7.2951
| Yarwun | 7.2951
| Somerton | 10.8463
| Bairnsdale | 10.8463
| Jeeralang A | 10.8463
| Jeeralang B | 10.8463
| Laverton North | 10.8463
| Mortlake | 10.8463
| Newport | 13.0277
| Valley Power | 10.8463
| Hallett GT | 10.8463
| Dry Creek | 10.8463
| Ladbroke Grove | 10.8463
| Mintaro | 10.8463
| Osborne | 7.2951
| Pelican Point | 7.2951
| Quarantine | 10.8463
| Torrens Island A | 2.1916
| Torrens Island B | 2.1916
| Bell Bay Three | 10.8463
| Tamar Valley | 10.8463
| Hunter Valley GT | 10.8463
| Mackay GT | 10.8463
| Mount Stuart | 10.8463
| Angaston | 11.3434
| Lonsdale | 11.3434
| Port Lincoln | 10.8463
| Port Lincoln 3 | 10.8463
| Port Stanvac | 11.3434
| Snuggery | 10.8463
| All hydro | 7.2951
| All wind | 10.5419
| All solar | 0
1. In capacity expansion simulations, variable OPEX may be varied by a small amount ($0.01) on a unit-by-unit basis within a power station to encourage model-driven retirement to occur on a per-unit basis

## Connection cost
TOC
Initial connection costs ($/kW) real June 2018 dollars
Source: AEMO 2018 ISP Assumptions Workbook
Build costs are adjusted according to NEM planning zone to account for proximity to transmission assets
Final connection costs will be subject to modelling outcomes
Scaled by 1.5 % from 2017 dollars to June 2018 dollars to account for CPI increase.
| Renewable Energy Zone | Wind | Solar | Biomass | Batteries | Pumped hydro | NEM Zone | Gas |  | System Strength Remeditation | $k/MW Connected *
| Broken Hill | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | NQ | 84.5258 |  | Synchronous Condensers for 330/275/220kV connected | 120
| Central NSW Tablelands | 92.668 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | CQ | 84.5258 |  | Synchronous Condensers for 132kV connected | 105
| Central West NSW | 92.668 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | SWQ | 83.1436
| Murray River | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | SEQ | 84.5258 |  | * Assumes SCR = 3, Xd''=0.2
| North West NSW | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | NNS | 79.0121
| Northern NSW Tablelands | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | NCEN | 76.6532
| Riverland | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | CAN | 75.2424
| Southern NSW Tablelands | 102.9644 | 82.3716 | 82.3716 | 102.9644 | 102.9644 | SWNSW | 79.0121
| Barcaldine | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | NVIC | 68.0171
| Darling Downs | 98.1178 | 72.7506 | 82.3716 | 102.9644 | 102.9644 | LV | 66.5986
| Fitzroy | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | MEL | 83.1436
| Isaac | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | CVIC | 83.1436
| North Qld Clean Energy Hub | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | NSA | 72.0751
| Northern Qld | 102.9644 | 102.9644 | 82.3716 | 102.9644 | 102.9644 | ADE | 72.0751
| Eastern Eyre Peninsula | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644 | SESA | 195.6325
| Leigh Creek | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644 | TAS | 92.668
| Mid-North SA | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644
| Northern SA | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644
| Roxby Downs | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644
| South East SA | 175.0396 | 175.0396 | 82.3716 | 102.9644 | 102.9644
| Western Eyre Peninsula | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644 | NEM Region | Gas | Shadow NEM zone for Gas | Black Coal (HELE)
| Yorke Peninsula | 133.8538 | 82.3716 | 82.3716 | 102.9644 | 102.9644 | TAS | 92.668 | TAS
| King island | 123.5573 | 123.5573 | 82.3716 | 102.9644 | 102.9644 | QLD | 84.5258 | NQ/CQ/SEQ | 138.3328
| North East Tasmania | 123.5573 | 123.5573 | 82.3716 | 102.9644 | 102.9644 | SA | 72.0751 | NSA/ADE | 138.3328
| North West Tasmania | 123.5573 | 123.5573 | 82.3716 | 102.9644 | 102.9644 | NSW | 79.0121 | NNS/SWNSW | 138.3328
| Tasmania Midlands | 123.5573 | 123.5573 | 82.3716 | 102.9644 | 102.9644 | VIC | 66.5986 | LV
| Gippsland | 123.5573 | 123.5573 | 82.3716 | 102.9644 | 102.9644
| Moyne | 113.2609 | 92.668 | 82.3716 | 102.9644 | 102.9644 | 1. Regional connection costs for gas are derived from shadow NEM zone connection cost.
| Western Victoria | 113.2609 | 92.668 | 82.3716 | 102.9644 | 102.9644

## Lead time
TOC
Lead time (years)
Source: AEMO 2018 ISP Assumptions Workbook
Amount of time from start of simulation before specific technologies that are not already committed/advanced can first be built.
| Technology | Lead time (years)
| Batteries | 1
| Solar PV | 1
| Wind | 1
| OCGT | 2
| CCGT | 4
| Pumped hydro | 6
| Black Coal (HELE) | 8
| Biomass | 1
| Solar Thermal Central Receiver (6 hrs storage) | 1

## Storage properties
TOC
Storage properties
Source: AEMO 2018 ISP Assumptions Workbook
Battery properties
| Property | Value | Unit
| Maximum Power | 1 | MW
| Energy capacity | 2 | hours
| Charge efficiency (household) | 0.9
| Charge efficiency (utility) | 0.8
| Technical life | 15 | years
Pumped hydro properties
`
| Property | Value | Unit
| Maximum power | 100 | MW
| Energy capacity | 6 | hours
| Pump efficiency | 0.8
| Economic life | 50 | years
For those scenarios which explore specific large scale storage projects:
Snowy 2.0 properties
| Property | Value | Unit
| Maximum power / Maximum pump load | 2000 / 2000 | MW
| Storage capacity | 168 | hours
| Pump efficiency | 0.8
| Economic life | 50 | years
| Transmission connection | Includes 500kV development from Snowy 2.0/Wagga to Bannaby and 330kV connection of Snowy 2.0
Battery of the Nation properties
| Property | Value | Unit
| Maximum power / Maximum pump load | 1500 / 1500 | MW
| Storage capacity | 24 | hours
| Pump efficiency | 0.8
| Economic life | 50 | years
| Transmission connection | Includes commitment of 700MW bi-directional Basslink augmentation. Model decision as to whether to expand Basslink capacity beyond a second link

## Hydro Storage Inflows
TOC
Hydro storage inflows (GWh)
Source: AEMO 2018 ISP Assumptions Workbook
| Reservoir | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Blowering | - | - | - | - | - | - | - | - | 6.3 | 24.6 | 30.7 | 34.3
| Eucumbene | 328 | 330 | 100 | 329 | 434 | 750 | 749 | 434 | 435 | 434 | 154 | 293
Fitzroy Falls | bar: Jan to Dec
| Guthega | 4.6 | 1.6 | 0.3 | 0.8 | 4 | 7.3 | 9.3 | 14.8 | 20.6 | 33.5 | 25.3 | 14.2
| Koombooloomba Dam | 15.6 | 21.5 | 22.6 | 16.8 | 22.5 | 40 | 35.9 | 72.8 | 62.7 | 50.7 | 35.9 | 44.5
| Kuranda Weir | 31.2 | 25.3 | 29.4 | 17 | 28.7 | 27.3 | 17.4 | 12.5 | 30 | 18.5 | 16.3 | 12.6
Split Yard Creek Dam | bar: Jan to Dec
| Eildon | 3.8 | 1.8 | 1.9 | 3.4 | 5.5 | 18.8 | 33.7 | 45.7 | 48.6 | 33.4 | 16.5 | 6.5
| Dartmouth | 10.1 | 7.7 | 4.1 | 5 | 9.7 | 20.9 | 32.1 | 42.7 | 58.8 | 50.8 | 26.4 | 16.7
| Derwent | 13.3 | 11.5 | 4.1 | 44 | 281.4 | 263.7 | 297.5 | 254.9 | 537.3 | 541.2 | 102.6 | 118.6
| Anthony/Pieman Pond | 46.3 | 35.6 | 45.7 | 66.3 | 324.2 | 211.9 | 246.8 | 136.4 | 323.9 | 277.3 | 54.6 | 103.2
| Burbury | 9.3 | 14.4 | 15.1 | 35.3 | 132 | 65.9 | 65.1 | 35.1 | 114.1 | 86.6 | 5.3 | 42.4
| Lake Gordon | 23.9 | 26 | 34.3 | 69.4 | 264.7 | 143 | 156.4 | 75.1 | 242.1 | 191.5 | 11.8 | 119.5
| Great Lake/Trevallyn pond | 3.7 | 2.7 | 3.7 | 9.3 | 197.2 | 133.9 | 312.5 | 144 | 295.2 | 163.7 | 92.2 | 5.2
| Mersey Forth Pond | 7.9 | 8.8 | 10.3 | 26.4 | 163.7 | 141.5 | 260.2 | 133 | 272.1 | 237.6 | 93.1 | 60.6

## Storage initial level
TOC
Storage initial level
Source: AEMO 2018 ISP Assumptions Workbook
Values will be verified and updated as necessary.
Hydroelectric Storage Initial Reservoir Levels
| Reservoir | Initial Volume (1000 m³) | Maximum capacity (1000 m³)
| Blowering | 1100667 | 1610000
| Guthega | 739 | 1400
| Koombooloomba Dam | 94427.1 | 184500
| Kuranda Weir | 1179 | 1387
| Jounama Pondage | 5705 | 27800
| Murray Pondage | 5895 | 13100
| Murray2Pondage | 677 | 1500
| Talbingo | 113741 | 160400
| Tumut Pondage | 31111 | 50000
| Tumut2Pondage | 788 | 1500
| Bendeela Pondage | 343 | 780
| Fitzroy Falls | 711.04 | 880
| Lake Yarrunga | 21600 | 36000
| Split Yard Creek Dam | 4408 | 10018
| Wivenhoe | 1145999 | 1165000
| Anthony-Pieman Pond | 262961 | 294430
| Burbury | 103219 | 233000
| Derwent | 686778 | 1848200
| Great Lake-Trevallyn Pond | 1008330 | 6567000
| Lake Gordon | 103219 | 4699000
| Mersey Forth Pond | 104582 | 227000
| Dartmouth | 3002437 | 3906000
| Eildon | 2176144 | 3387000
| Hume Dam | 1874062 | 3040000

## Interconnector capability
TOC
Interconnector capability (MW)
Source: AEMO 2018 ISP Assumptions Workbook
These notional limits are applied for the Long-term Investment Planning model.
The Market Dispatch Simulation will use NEMDE constraint equations to limit interconnector flows.
| Interconnector | Forward Direction | Forward capability | Reverse Capability
| QNI | NSW to QLD | Dynamic Limit* | Dynamic Limit*
| Terranora | NSW to QLD | 50 | 150
| VIC-NSW | VIC to NSW | 700 870** | 400
| Heywood | VIC to SA | 650 | 650
| Murraylink | VIC to SA | 220 | 200
| Basslink | TAS to VIC | 478 | 478
| Proposed SA NSW Interconnector | VIC to SA | 800*** | 800***
| Proposed Marinus Link | TAS to VIC | 478 | 478
* TransGrid and Powerlink will use values calculated in the System Technical Assessment which
account for the larger influences in the limit, including a) credible option b) season c) load level
d) influential genreator dispatch
** Assumed new interconnector transfer capacity after upgrade of the Vic NSW interconnector
*** Assumed SA_NSW new interconnector transfer capacity

## Proportioning factors
TOC
Proportioning factors for Inter-Regional losses
Source: Regions and Marginal Loss Factors: FY 2018-19
Losses due to interconnector flow are assigned asymmetrically to regions either side of the interconnector1
| Notional Interconnector | Proportioning Factor | Region applied to
| Queensland - New South Wales (QNI) | 68% | New South Wales
| Queensland - New South Wales (Terranora) | 66% | New South Wales
| Victoria - New South Wales | 32% | Victoria
| Victoria - South Australia (Heywood) | 78% | Victoria
| Victoria - South Australia (Murraylink) | 67% | Victoria
| Tasmania - Victoria (Basslink)* | 50% | Victoria
| South Australia - New South Wales | 50%** | New South Wales
| Tasmania - Victoria (Marinus Link)* | 50%** | Victoria
* A value of 50% has been assumed for Basslink as done in the 2018 AEMO ISP.
** A value of 50% has been assumed.

## Augmentation options
TOC
Augmentation options
Source: TransGrid and Powerlink's Expanding NSW-QLD transmission transfer capacity - Project Specification Consultation Report
Summary of potential credible options
| Option Description | Indicative total transfer capacity (MW)1 |  | Estimated capex ($m)2 | Expected delivery time
|  | Northward | Southward
Incremental upgrades to the existing network to increase transfer capacity
| Option 1A – Uprate Liddell to Tamworth Lines and install new dynamic reactive support at Tamworth and Dumaresq and shunt capacitor banks* | 770 | 1215 | 142 | 2-3 years
| Option 1B – Uprate Liddell to Tamworth Lines only | 535 | 1030 | 28 | 2-3 years
| Option 1C - Install new dynamic reactive support at Tamworth and Dumaresq and shunt capacitor banks | 595 | 1180 | 114 | 2-3 years
| Option 1D – Sapphire substation cut into line 8C and a mid-point switching station between Dumaresq and Bulli Creek | 535 | 1165 | 45 | 1-2 years
A new single-circuit line from NSW to Queensland
| Option 2 – 330 kV single circuit between Braemar and Liddell | 980 | 1865 | 855 | 3-4 years
A new double-circuit line from NSW to Queensland
| Option 3A – 330 kV double circuit between Bulli Creek and Armidale* | 770 | 1593 | 560 | 3-4 years
| Option 3B – 330 kV double circuit line between Braemar and Liddell via Uralla (and establishment of a Uralla 330 kV substation) | 1530 | 2160 | 1505 | 4-5 years
| Option 3C – 330 kV double circuit line between Braemar and Uralla, 500 kV single circuits between Uralla and Wollar and between Uralla and Bayswater (and establishment of Uralla 500/330 kV substation) | 1695 | 2540 | 2039 | 5-6 years
High Voltage Direct Current Options
| Option 4A – HVDC back-to-back | 1195 | 1780 | 825 | 2-3 years
| Option 4B – HVDC between Mudgeeraba and Lismore** | 765 | 1190 | 600 | 3-4 years
| Option 4C – HVDC between Western Downs and Bayswater** | 2590 | 2990 | 2100 | 4-5 years
A grid-connected battery system
| Option 5 - Battery energy storage system | 1135 | 1635 | 1000 | 1-3 years
* Option 1A is the ISP recommended Group 1 investment and Option 3A is the ISP recommended Group 2 investment. These are based on the ISP modelling assumptions. The capacity improvements and cost estimates for these options is continuing to be reviewed and will be revised in the PADR. ** Power transfer capacities are defined for both the existing HVAC interconnector and for the new HVDC option.
1 The transfer capacities shown in this table are indicative for one operating state only (daytime, medium demand) and serve to summarise the notional differences between options. 2 All cost estimates are to be treated as indicative at this stage and TransGrid and Powerlink will further refine these estimates as part of the PADR.

## Transmission limits
TOC
Transmission limits
|  | Source Location | Source
| Ratings | http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings | http://www.nemweb.com.au/Reports/Current/Alt_Limits/
| NEM Constraint Equations | http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/NEM-Electricity-Statement-of-Opportunities | 2018 ESOO Model
TransGrid and Powerlink will consider the impact of lengthy/material outages on transmission limits associated with outages to perform transmission works including:
Transmission works affecting Transmission Limits
Line refit/replacement of Bouldercombe - Raglan/Larcom Creek - Calliope River 275kV lines
Line refit/replacement of eastern Central Queensland - Southern Queensland 275kV transmission line corridor
Replacement of Armidale - Tamworth 330kV transmission line
Retension of Liddell - Muswellbrook - Tamworth 330kV lines (if applicable in credible option)

## Generator capacity
TOC
Generator capacity
Source: AEMO Generation Information November 2018
Maximum capacity is used to report capacity factors and calculate fixed operating costs. It may not correspond to "installed capacity" listed in Generation Information workbooks, when maximum seasonal ratings differ. Generator capacity may vary with weather conditions. The ISP uses AEMO Generation Information page (2017 December release) for seasonal ratings for the first 10 years of the model period. Not all committed or advanced projects have ratings listed in Generation Information. Where information is absent Maximum Capacity is used. This will be updated with the most recent information from the AEMO Generation Information Page at the end of the PSCR consultation period.
The list from the 2018 ISP Assumptions book has been updated by TransGrid and Powerlink
| Region | Status | Fuel Type | Description | Installed capacity (MW) | Summer (MW) | Winter (MW) | Classification | Indicative Commissioning Date
| QLD | Existing | Coal | Callide B | 700 | 700 | 700 | Scheduled
| QLD | Existing | Coal | Callide Power Plant | 840 | 840 | 840 | Scheduled
| QLD | Existing | Coal | Gladstone | 1680 | 1680 | 1680 | Scheduled
| QLD | Existing | Coal | Kogan Creek | 750 | 730 | 750 | Scheduled
| QLD | Existing | Coal | Millmerran | 852 | 760 | 852 | Scheduled
| QLD | Existing | Coal | Stanwell | 1460 | 1460 | 1460 | Scheduled
| QLD | Existing | Coal | Tarong | 1400 | 1400 | 1400 | Scheduled
| QLD | Existing | Coal | Tarong North | 443 | 443 | 443 | Scheduled
| QLD | Existing | Gas | Barcaldine | 37 | 34 | 37 | Scheduled
| QLD | Existing | Gas | Braemar 1 and 2 | 1023 | 966 | 1023 | Scheduled
| QLD | Existing | Gas | Condamine | 100 | 89.5 | 100 | Scheduled
| QLD | Existing | Gas | Darling Downs | 633 | 580 | 633 | Scheduled
| QLD | Existing | Gas | Mackay GT | 34 | 34 | 34 | Scheduled
| QLD | Existing | Gas | Oakey | 346 | 282 | 346 | Scheduled
| QLD | Existing | Gas | Roma | 68 | 54 | 68 | Scheduled
| QLD | Existing | Gas | Swanbank E | 365 | 350 | 365 | Scheduled
| QLD | Existing | Gas | Townsville (Yabulu) | 240 | 231 | 240 | Scheduled
| QLD | Existing | Gas | Yarwun | 180 | 180 | 180 | Non-scheduled
| QLD | Existing | Liquid fuel | Mount Stuart | 428 | 400 | 428 | Scheduled
| QLD | Existing | Hydro | Barron Gorge | 66 | 66 | 66 | Scheduled
| QLD | Existing | Hydro | Kareeya | 86.4 | 86.4 | 86.4 | Scheduled
| QLD | Existing | Hydro | Wivenhoe | 570 | 570 | 570 | Scheduled
| QLD | Existing | Wind | Mt Emerald | 180.45 | 180.45 | 180.45 | Semi-scheduled
| QLD | Existing | Solar | Childers | 56 | 56 | 56 | Semi-scheduled
| QLD | Existing | Solar | Clare | 100 | 100 | 100 | Semi-scheduled
| QLD | Existing | Solar | Clermont | 75 | 75 | 75 | Semi-scheduled
| QLD | Existing | Solar | Collinsville | 42.5 | 42.5 | 42.5 | Semi-scheduled
| QLD | Existing | Solar | Darling Downs SF | 108.5 | 108.5 | 108.5 | Semi-scheduled
| QLD | Existing | Solar | Daydream | 150 | 150 | 150 | Semi-scheduled
| QLD | Existing | Solar | Emerald | 72 | 72 | 72 | Semi-scheduled
| QLD | Existing | Solar | Hamilton | 57.5 | 57.5 | 57.5 | Semi-scheduled
| QLD | Existing | Solar | Hayman | 50 | 50 | 50 | Semi-scheduled
| QLD | Existing | Solar | Kidston | 48.5 | 48.5 | 48.5 | Semi-scheduled
| QLD | Existing | Solar | Oakey 2 SF | 55 | 55 | 55 | Semi-scheduled
| QLD | Existing | Solar | Oakey SF | 25 | 25 | 25 | Semi-scheduled
| QLD | Existing | Solar | Ross River | 116 | 116 | 116 | Semi-scheduled
| QLD | Existing | Solar | Sun Metals | 107 | 107 | 107 | Semi-scheduled
| QLD | Existing | Solar | Susan River | 75 | 75 | 75 | Semi-scheduled
| QLD | Existing | Solar | Whitsunday | 57.5 | 57.5 | 57.5 | Semi-scheduled
| QLD | Committed | Wind | Coopers Gap | 440 | 440 | 440 | Semi-scheduled | Summer 2019/20
| QLD | Committed | Wind | Kennedy Energy Park WF | 43.2 | 43.2 | 43.2 | Semi-scheduled | Winter 2019
| QLD | Committed | Solar | Aramara | 101 | 101 | 101 | Semi-scheduled | Summer 2019/20
| QLD | Committed | Solar | Blackwater | 150 | 150 | 150 | Semi-scheduled | Summer 2019/20
| QLD | Committed | Solar | Cape York | 53 | 53 | 53 | Semi-scheduled | Summer 2019/20
| QLD | Committed | Solar | Haughton | 100 | 100 | 100 | Semi-scheduled | Winter 2019
| QLD | Committed | Solar | Kennedy Energy Park SF | 15 | 15 | 15 | Semi-scheduled | Winter 2019
| QLD | Committed | Solar | Lilyvale | 100 | 100 | 100 | Semi-scheduled | Summer 2019/20
| QLD | Committed | Solar | Rugby Run | 65 | 65 | 65 | Semi-scheduled | Winter 2019
| QLD | Committed | Solar | Yarranlea | 102.5 | 102.5 | 102.5 | Semi-scheduled | Winter 2019
| QLD | Committed | Battery | Kennedy Energy Park BESS | 2 | 2 | 2 | Semi-scheduled | Winter 2019
| NSW | Existing | Coal | Bayswater | 2740 | 2620 | 2740 | Scheduled
| NSW | Existing | Coal | Eraring | 2880 | 2720 | 2880 | Scheduled
| NSW | Existing | Coal | Liddell | 1800 | 1800 | 1800 | Scheduled
| NSW | Existing | Coal | Mount Piper | 1400 | 1300 | 1400 | Scheduled
| NSW | Existing | Coal | Vales Point | 1320 | 1320 | 1320 | Scheduled
| NSW | Existing | Gas | Colongra | 724 | 648 | 724 | Scheduled
| NSW | Existing | Gas | Hunter Valley GT | 40 | 30 | 40 | Scheduled
| NSW | Existing | Gas | Smithfield | 108.999 | 108.999 | 108.999 | Scheduled
| NSW | Existing | Gas | Tallawarra | 440 | 378 | 440 | Scheduled
| NSW | Existing | Gas | Uranquinty | 664 | 640 | 664 | Scheduled
| NSW | Existing | Hydro | Blowering | 80 | 80 | 80 | Scheduled
| NSW | Existing | Hydro | Guthega | 68 | 68 | 68 | Scheduled
| NSW | Existing | Hydro | Hume NSW | 29 | 29 | 29 | Scheduled
| NSW | Existing | Hydro | Shoalhaven | 240 | 240 | 240 | Scheduled
| NSW | Existing | Hydro | Tumut 1 | 328 | 328 | 328 | Scheduled
| NSW | Existing | Hydro | Tumut 2 | 288 | 288 | 288 | Scheduled
| NSW | Existing | Hydro | Tumut 3 | 1800 | 1800 | 1800 | Scheduled
| NSW | Existing | Wind | Boco Rock | 113.18 | 104.09 | 113.18 | Scheduled
| NSW | Existing | Wind | Capital | 141 | 141 | 141 | Non-scheduled
| NSW | Existing | Wind | Cullerin Range | 30 | 30 | 30 | Non-scheduled
| NSW | Existing | Wind | Gullen Range | 165.5 | 165.5 | 165.5 | Semi-scheduled
| NSW | Existing | Wind | Gunning | 46.5 | 46.5 | 46.5 | Semi-scheduled
| NSW | Existing | Wind | Sapphire | 270 | 187 | 270 | Semi-scheduled
| NSW | Existing | Wind | Silverton | 198 | 198 | 198 | Semi-scheduled
| NSW | Existing | Wind | Taralga | 106.8 | 106.8 | 106.8 | Semi-scheduled
| NSW | Existing | Wind | White Rock | 172.5 | 172.5 | 172.5 | Semi-scheduled
| NSW | Existing | Wind | Woodlawn | 48.3 | 48.3 | 48.3 | Semi-scheduled
| NSW | Existing | Solar | Broken Hill | 53 | 53 | 53 | Semi-scheduled
| NSW | Existing | Solar | Coleambally | 150 | 150 | 130 | Semi-scheduled
| NSW | Existing | Solar | Griffith | 30 | 30 | 30 | Non-scheduled
| NSW | Existing | Solar | Gullen Range SF | 10 | 10 | 10 | Semi-scheduled
| NSW | Existing | Solar | Manildra | 46.7 | 46.7 | 45 | Semi-scheduled
| NSW | Existing | Solar | Moree | 52.2 | 52.2 | 41.9 | Semi-scheduled
| NSW | Existing | Solar | Nyngan | 102 | 102 | 102 | Semi-scheduled
| NSW | Existing | Solar | Parkes | 55 | 55 | 51.8 | Semi-scheduled
| NSW | Existing | Solar | White Rock SF | 20 | 20 | 20 | Semi-scheduled
| NSW | Committed | Wind | Bodongora | 113.19 | 113.19 | 113.19 | Semi-scheduled | Winter 2019
| NSW | Committed | Wind | Crookwell 2 | 91 | 91 | 91 | Semi-scheduled | Winter 2019
| NSW | Committed | Wind | Crudine Ridge | 135 | 135 | 135 | Semi-scheduled | Summer 2019/20
| NSW | Committed | Solar | Beryl | 100 | 100 | 100 | Semi-scheduled | Winter 2019
| NSW | Committed | Solar | Finnley | 133 | 133 | 133 | Semi-scheduled | ???
| NSW | Committed | Solar | Goonumbla | 70 | 70 | 70 | Semi-scheduled | ???
| NSW | Committed | Solar | Limondale Plant 1 | 220 | 220 | 220 | Semi-scheduled | Winter 2020
| NSW | Committed | Solar | Limondale Plant 2 | 29 | 29 | 29 | Semi-scheduled | Winter 2019
| NSW | Committed | Solar | Nevertire | 105 | 105 | 105 | Semi-scheduled | Winter 2019
| NSW | Committed | Solar | Sunraysia | 200 | 200 | 200 | Semi-scheduled | Summer 2019/20
| VIC | Existing | Coal | Loy Yang A | 2210 | 2136 | 2210 | Scheduled
| VIC | Existing | Coal | Loy Yang B | 1150 | 980 | 1150 | Scheduled
| VIC | Existing | Coal | Yallourn | 1528 | 1420 | 1528 | Scheduled
| VIC | Existing | Gas | Bairnsdale | 84 | 78 | 84 | Scheduled
| VIC | Existing | Gas | Jeeralang A | 224 | 192 | 224 | Scheduled
| VIC | Existing | Gas | Jeeralang B | 255 | 216 | 255 | Scheduled
| VIC | Existing | Gas | Laverton North | 340 | 300 | 340 | Scheduled
| VIC | Existing | Gas | Mortlake | 584 | 518 | 584 | Scheduled
| VIC | Existing | Gas | Newport | 510 | 475 | 510 | Scheduled
| VIC | Existing | Gas | Somerton | 160 | 140 | 160 | Scheduled
| VIC | Existing | Gas | Valley Power | 336 | 270 | 336 | Scheduled
| VIC | Existing | Hydro | Bogong | 150 | 150 | 150 | Scheduled
| VIC | Existing | Hydro | Dartmouth | 165 | 165 | 165 | Scheduled
| VIC | Existing | Hydro | Eildon | 100 | 100 | 100 | Scheduled
| VIC | Existing | Hydro | Hume VIC | 29 | 29 | 29 | Scheduled
| VIC | Existing | Hydro | McKay Creek | 150 | 150 | 150 | Scheduled
| VIC | Existing | Hydro | Murray 1 | 950 | 950 | 950 | Scheduled
| VIC | Existing | Hydro | Murray 2 | 560 | 560 | 560 | Scheduled
| VIC | Existing | Hydro | West Kiewa | 68 | 68 | 68 | Scheduled
| VIC | Existing | Wind | Ararat | 240 | 195 | 240 | Semi-scheduled
| VIC | Existing | Wind | Bald Hills | 106.6 | 106.6 | 106.6 | Semi-scheduled
| VIC | Existing | Wind | Challicum Hills | 52.5 | 52.5 | 52.5 | Non-scheduled
| VIC | Existing | Wind | Kiata | 31.05 | 31.05 | 31.05 | Semi-scheduled
| VIC | Existing | Wind | Macarthur | 420 | 420 | 420 | Semi-scheduled
| VIC | Existing | Wind | Mount Mercer | 131.2 | 131.2 | 131.2 | Semi-scheduled
| VIC | Existing | Wind | Oaklands Hill | 63 | 41.6 | 63 | Semi-scheduled
| VIC | Existing | Wind | Portland | 151.7 | 151.7 | 151.7 | Non-scheduled
| VIC | Existing | Wind | PWEP 1 Yambuk | 30 | 30 | 30 | Non-scheduled
| VIC | Existing | Wind | PWEP 2 Cape Bridgewater | 58 | 58 | 58 | Non-scheduled
| VIC | Existing | Wind | PWEP 3 Cape Nelson South | 44 | 44 | 44 | Non-scheduled
| VIC | Existing | Wind | PWEP 4 Cape Nelson North | 47.2 | 47.2 | 47.2 | Non-scheduled
| VIC | Existing | Wind | Salt Creek | 54 | 54 | 54 | Semi-scheduled
| VIC | Existing | Wind | Waubra | 192 | 192 | 192 | Non-scheduled
| VIC | Existing | Solar | Gannawarra | 50 | 50 | 50 | Semi-scheduled
| VIC | Committed | Wind | Bulgana | 194 | 194 | 194 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Crowlands | 79.95 | 79.95 | 79.95 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Lal Lal - Elaine end | 83.6 | 83.6 | 83.6 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Lal Lal - Yendon end | 144.4 | 144.4 | 144.4 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Moorabool | 320 | 320 | 320 | Semi-scheduled | Summer 2019/20
| VIC | Committed | Wind | Mt Gellibrand | 132 | 132 | 132 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Murra Warra | 226 | 226 | 226 | Semi-scheduled | Winter 2019
| VIC | Committed | Wind | Stockyard Hill | 532 | 532 | 532 | Semi-scheduled | Summer 2019/20
| VIC | Committed | Solar | Bannerton | 88 | 88 | 88 | Semi-scheduled | Winter 2019
| VIC | Committed | Solar | Karadoc | 90 | 90 | 90 | Semi-scheduled | Winter 2019
| VIC | Committed | Solar | Kiamal | 200 | 200 | 200 | Semi-scheduled | Winter 2019
| VIC | Committed | Solar | Numurkah | 100 | 100 | 100 | Semi-scheduled | Winter 2019
| VIC | Committed | Solar | Wemen | 87.75 | 87.75 | 87.75 | Semi-scheduled | Winter 2019
| VIC | Committed | Solar | Yatpool | 81 | 81 | 81 | Semi-scheduled | Winter 2019
| VIC | Committed | Battery | Ballarat | 29.9 | 28.8 | 29.9 | Semi-scheduled | Winter 2019
| VIC | Committed | Battery | Bulgana BESS | 20 | 20 | 20 | Semi-scheduled | Summer 2019/20
| VIC | Committed | Battery | Gannawarra BESS | 25.33 | 25.33 | 25.33 | Semi-scheduled | Winter 2019
| SA | Existing | Gas | Dry Creek | 143 | 112 | 143 | Scheduled
| SA | Existing | Gas | Hallett GT | 216 | 193 | 216 | Scheduled
| SA | Existing | Gas | Ladbroke Grove | 84 | 68 | 84 | Scheduled
| SA | Existing | Gas | Mintaro | 90 | 68 | 90 | Scheduled
| SA | Existing | Gas | Osborne | 188 | 172 | 188 | Scheduled
| SA | Existing | Gas | Pelican Point | 474 | 458 | 474 | Scheduled
| SA | Existing | Gas | Quarantine | 221 | 189 | 221 | Scheduled
| SA | Existing | Gas | Torrens Island A | 480 | 480 | 480 | Scheduled
| SA | Existing | Gas | Torrens Island B | 800 | 780 | 800 | Scheduled
| SA | Existing | Liquid fuel | Angaston | 50 | 50 | 50 | Scheduled
| SA | Existing | Liquid fuel | Lonsdale | 20.7 | 20.7 | 20.7 | Scheduled
| SA | Existing | Liquid fuel | Port Lincoln | 50 | 38 | 50 | Scheduled
| SA | Existing | Liquid fuel | Port Lincoln 3 | 23.5 | 18 | 23.5 | Scheduled
| SA | Existing | Liquid fuel | Port Stanvac | 57.6 | 57.6 | 57.6 | Scheduled
| SA | Existing | Liquid fuel | Snuggery | 63 | 54 | 63 | Scheduled
| SA | Existing | Liquid fuel | Temporary Generation North | 154 | 154 | 154 | Semi-scheduled
| SA | Existing | Liquid fuel | Temporary Generation South | 123 | 123 | 123 | Semi-scheduled
| SA | Existing | Wind | Canunda | 46 | 46 | 46 | Non-scheduled
| SA | Existing | Wind | Cathedral Rocks | 66 | 66 | 66 | Non-scheduled
| SA | Existing | Wind | Clements Gap | 56.7 | 56.7 | 56.7 | Semi-scheduled
| SA | Existing | Wind | Hallett 1 Brown Hill | 94.5 | 58.5 | 94.5 | Semi-scheduled
| SA | Existing | Wind | Hallett 2 Hallett Hill | 71.4 | 44.2 | 71.4 | Semi-scheduled
| SA | Existing | Wind | Hallett 3 North Brown Hill | 132.3 | 81.9 | 132.3 | Semi-scheduled
| SA | Existing | Wind | Hallett 4 The Bluff | 52.5 | 32.5 | 52.5 | Semi-scheduled
| SA | Existing | Wind | Hornsdale S1 | 100 | 100 | 100 | Semi-scheduled
| SA | Existing | Wind | Hornsdale S2 | 100 | 100 | 100 | Semi-scheduled
| SA | Existing | Wind | Hornsdale S3 | 109 | 109 | 109 | Semi-scheduled
| SA | Existing | Wind | Lake Bonney 1 | 81 | 81 | 81 | Non-scheduled
| SA | Existing | Wind | Lake Bonney 2 | 159 | 159 | 159 | Semi-scheduled
| SA | Existing | Wind | Lake Bonney 3 | 39 | 39 | 39 | Semi-scheduled
| SA | Existing | Wind | Mount Millar | 70 | 70 | 70 | Non-scheduled
| SA | Existing | Wind | Snowtown 1 | 98.7 | 98.7 | 98.7 | Semi-scheduled
| SA | Existing | Wind | Snowtown 2 North | 144 | 144 | 144 | Semi-scheduled
| SA | Existing | Wind | Snowtown 2 South | 126 | 126 | 126 | Semi-scheduled
| SA | Existing | Wind | Starfish Hill | 35 | 35 | 35 | Non-scheduled
| SA | Existing | Wind | Waterloo | 130.8 | 130.8 | 130.8 | Semi-scheduled
| SA | Existing | Wind | Waterloo S2 | 19 | 19 | 19 | Semi-scheduled
| SA | Existing | Wind | Wattle Point | 91 | 91 | 91 | Non-scheduled
| SA | Existing | Solar | Bungala | 110 | 110 | 110 | Semi-scheduled
| SA | Existing | Battery | ESCRI Dalrymple | 30 | 30 | 30 | Semi-scheduled
| SA | Existing | Battery | Hornsdale BESS | 100 | 100 | 100 | Scheduled
| SA | Committed | Liquid fuel | Barker Inlet | 210 | 210 | 210 | Semi-scheduled | Summer 2019/20
| SA | Committed | Wind | Lincoln Gap | 126 | 126 | 126 | Semi-scheduled | Winter 2019
| SA | Committed | Wind | Willogoleche | 119 | 119 | 119 | Semi-scheduled | Winter 2019
| SA | Committed | Solar | Bungala S2 | 110 | 110 | 110 | Semi-scheduled | Winter 2019
| SA | Committed | Solar | Tailem Bend | 95 | 95 | 95 | Semi-scheduled | Winter 2019
| TAS | Existing | Gas | Bell Bay Three | 105 | 105 | 105 | Scheduled
| TAS | Existing | Gas | Tamar Valley CCGT | 208 | 208 | 208 | Scheduled
| TAS | Existing | Gas | Tamar Valley OCGT | 58 | 58 | 58 | Scheduled
| TAS | Existing | Hydro | Bastyan | 81 | 81 | 81 | Scheduled
| TAS | Existing | Hydro | Catagunya | 173.7 | 173.7 | 173.7 | Scheduled
| TAS | Existing | Hydro | Cethana | 95 | 95 | 95 | Scheduled
| TAS | Existing | Hydro | Devils Gate | 63 | 63 | 63 | Scheduled
| TAS | Existing | Hydro | Fisher | 46 | 46 | 46 | Scheduled
| TAS | Existing | Hydro | Gordon | 370.8 | 370.8 | 370.8 | Scheduled
| TAS | Existing | Hydro | John Butters | 140 | 140 | 140 | Scheduled
| TAS | Existing | Hydro | Lake Echo | 30 | 30 | 30 | Scheduled
| TAS | Existing | Hydro | Lemonthyme | 86 | 86 | 86 | Scheduled
| TAS | Existing | Hydro | Liapootah | 84 | 84 | 84 | Scheduled
| TAS | Existing | Hydro | Mackintosh | 81 | 81 | 81 | Scheduled
| TAS | Existing | Hydro | Meadowbank | 43.8 | 43.8 | 43.8 | Scheduled
| TAS | Existing | Hydro | Poatina | 342 | 342 | 342 | Scheduled
| TAS | Existing | Hydro | Reece | 232 | 232 | 232 | Scheduled
| TAS | Existing | Hydro | Tarraleah | 90 | 90 | 90 | Scheduled
| TAS | Existing | Hydro | Trevallyn | 102.8 | 102.8 | 102.8 | Scheduled
| TAS | Existing | Hydro | Tribute | 88 | 88 | 88 | Scheduled
| TAS | Existing | Hydro | Tungatinah | 130.5 | 130.5 | 130.5 | Scheduled
| TAS | Existing | Hydro | Wayatinah | 40 | 40 | 40 | Scheduled
| TAS | Existing | Hydro | Wilmot | 32 | 32 | 32 | Scheduled
| TAS | Existing | Wind | Musselroe | 168 | 168 | 168 | Semi-scheduled
| TAS | Existing | Wind | Woolnorth | 140 | 140 | 140 | Non-scheduled
| TAS | Committed | Wind | Ganville Harbour | 111.6 | 111.6 | 111.6 | Semi-scheduled | Summer 2019/20
| TAS | Committed | Wind | Wild Cattle Hill | 144 | 144 | 144 | Semi-scheduled | Summer 2019/20
* Powerlink and TransGrid will consider anticipated projects (close to reaching commitment) in the assessment. These are not included in the list above due to confidentiality restrictions.

## Generation limits
TOC
Generator modelling assumptions
Source: AEMO 2018 ISP Assumptions Workbook
| Generating unit | Minimum Load (MW) | Generator | Minimum Capacity Factors | End time | Generator | Max Capacity Factors
| BW01 | 310.5 | Tallawarra | 40% | 2020-07-01 | Liddell | 50%
| BW02 | 310.5 | Condamine | 50% | 2020-07-01 | Biomass | 50%
| BW03 | 310.5 | Darling Downs | 50% | 2020-07-01
| BW04 | 310.5 | Yabulu | 25% | 2020-07-01
| ER01 | 230 | Yarwun | 70% | 2020-07-01
| ER02 | 230 | Osborne* | 60% | Depending on timing of SA interconnector expansion
| ER03 | 230 | Pelican Point* | 50% | Depending on timing of SA interconnector expansion
| ER04 | 230 | Torrens Island A* | 15% | Until retirement
| LD01 | 260
| LD02 | 260 | * South Australian minimum capacity factors are reduced consistent with the timing of a possible second synchronous interconnector.
| MP1 | 280
| MP2 | 280
| VP5 | 250
| VP6 | 250
| CALL_B_1 | 175
| CALL_B_2 | 175
| CPP_3 | 225
| CPP_4 | 225
| GSTONE1 | 120
| GSTONE2 | 120
| GSTONE3 | 120
| GSTONE4 | 120
| GSTONE5 | 120
| GSTONE6 | 120
| KPP_1 | 362
| MPP_1 | 170
| MPP_2 | 170
| STAN-1 | 180
| STAN-2 | 180
| STAN-3 | 180
| STAN-4 | 180
| TARONG#1 | 175
| TARONG#2 | 175
| TARONG#3 | 175
| TARONG#4 | 175
| TNPS1 | 220
| LOYYB1 | 240
| LOYYB2 | 240
| LYA1 | 410
| LYA2 | 300
| LYA3 | 410
| LYA4 | 410
| YWPS1 | 216
| YWPS2 | 216
| YWPS3 | 228
| YWPS4 | 228
| CPSA | 60
| YARWUN_1 | 118
| Torrens Island B* | 160
* Torrens Island B minimum load is reduced upon the development of a second synchronous interconnector (as appropriate)

## Generator reliability settings
TOC
Generator reliability settings
Source: AEMO Electricity Statement of Opportunities 2018
All units take the outage rate of their respective fuel type.
Forced outage assumptions used for the 2018 AEMO ESOO
| Fuel type | Forced Outage Rate (%) * |  | Mean time to repair (hrs) ** |  | Partial Outage Derating Factor ***
|  | Full outage | Partial outage | Full outage | Partial outage
| Black coal (QLD) | 2.42% | 13.51% | 53 | 16 | 16.94%
| Black coal (NSW) - Until 2022 | 6.56% | 25.81% | 135 | 19 | 19.98%
| Black coal (NSW) - After 2022 | 3.88% | 23.45% | 102 | 16 | 17.76%
| Brown coal (VIC) | 5.34% | 13.32% | 40 | 7 | 19.18%
| CCGT | 1.33% | 0.36% | 17 | 36 | 42.76%
| OCGT | 3.56% | 0.28% | 15 | 21 | 26.91%
| Steam Turbine | 4.58% | 11.25% | 124 | 75 | 22.85%
| Hydro | 1.58% | 0.01% | 15 | 7 | 17.26%
* The percentage of time per year that a generator is expected to be out of service due to forced outage.
** The average time take to return a generating unit to service.
*** The loss of capacity during a partial outage, relative to generator unit rating. If the outage factor is 20%, the generator will operate at 80% capacity during a partial outage.

## Maintenance
TOC
Maintenance rate
Source: AEMO 2018 ISP Assumptions Workbook
The percentage of time per year that a generator is expected to be out of service for maintenance.
All units take the maintenance rate of their respective fuel type
| Fuel type | % of time out | Events per year | Total days out
| Black Coal | 5.48% | 5 | 20.002
| Brown Coal | 5.48% | 5 | 20.002
| Hydro | 0% | 5 | 0
| Liquid Fuel | 1.37% | 5 | 5.0005
| CCGT | 5.48% | 5 | 20.002
| OCGT | 1.37% | 5 | 5.0005

## Heat rates
TOC
Heat rates
Source: AEMO 2018 ISP Assumptions Workbook
Encapsulates the efficiency of thermal generators (as-generated, HHV)
| Existing generators |  | Generic new entrant units
| Generator | Heat rate (GJ/MWh) | Generator | Heat rate (GJ/MWh)
| Bayswater | 9.46 | OCGT | 10.15
| Eraring | 9.549 | CCGT | 6.93
| Liddell | 10.144 | Biomass | 12.66
| Mount Piper | 9.266 | Black Coal (HELE) | 8.664
| Vales Point | 9.685
| Callide B | 9.149
| Callide Power Plant | 9.305
| Gladstone | 9.47
| Kogan Creek | 8.807
| Millmerran | 9.204
| Stanwell | 9.073
| Tarong | 9.208
| Tarong North | 8.664
| Loy Yang A | 12.142
| Loy Yang B | 12.531
| Yallourn | 13.926
| Colongra | 11.139
| Smithfield | 8.362
| Tallawarra | 6.99
| Uranquinty | 11.139
| Barcaldine | 12.73
| Braemar | 11.881
| Condamine | 7.282
| Darling Downs | 7.383
| Oakey | 10.934
| Roma | 11.881
| Swanbank E | 7.436
| Yabulu (Townsville) | 7.598
| Yarwun | 10.381
| Somerton | 14.851
| Bairnsdale | 10.483
| Jeeralang A | 15.263
| Jeeralang B | 15.263
| Laverton North | 11.497
| Mortlake | 11.139
| Newport | 10.296
| Valley Power | 14.851
| Hallett GT | 14.851
| Barker Inlet | 7.411
| Dry Creek | 13.709
| Ladbroke Grove | 11.881
| Mintaro | 12.73
| Osborne | 8.163
| Pelican Point | 7.353
| Quarantine | 10.714
| Torrens Island A | 11.429
| Torrens Island B | 10.714
| Bell Bay Three | 12.052
| Tamar Valley CCGT | 7.282
| Tamar Valley OCGT | 12.73
| Hunter Valley GT | 12.73
| Mackay GT | 12.73
| Mount Stuart | 11.881
| Angaston | 13
| Lonsdale | 13
| Port Lincoln | 12.821
| Port Lincoln 3 | 12.821
| Port Stanvac | 13
| Snuggery | 13.443
| Tailem Bend | 13

## Auxiliary
TOC
Auxiliary load
Source: AEMO 2018 ISP Assumptions Workbook
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated for use within power stations
| Existing generators |  | New entrants
| Generator | % auxiliary load | Generator | % auxiliary load
| Bayswater | 6% | Wind | 1%
| Eraring | 6% | Solar PV | 1%
| Liddell | 5% | CCGT | 3%
| Mount Piper | 5% | OCGT | 1%
| Vales Point | 5% | Reciprocating engine | 3%
| Callide B | 9% | Biomass | 8%
| Callide Power Plant | 6% | Pumped Hydro | 1%
| Gladstone | 8% | Black Coal (HELE) | 6%
| Kogan Creek | 9% | Solar Thermal Central Receiver (6 hrs storage) | 1%
| Millmerran | 6%
| Stanwell | 9%
| Tarong | 8%
| Tarong North | 6%
| Loy Yang A | 9%
| Loy Yang B | 8%
| Yallourn | 10%
| Colongra | 1%
| Smithfield | 5%
| Tallawarra | 3%
| Uranquinty | 1%
| Barcaldine | 1%
| Braemar | 1%
| Condamine | 3%
| Darling Downs | 6%
| Oakey | 1%
| Roma | 1%
| Swanbank E | 3%
| Yabulu (Townsville) | 3%
| Yarwun | 2%
| Somerton | 1%
| Bairnsdale | 1%
| Jeeralang A | 3%
| Jeeralang B | 3%
| Laverton North | 3%
| Mortlake | 1%
| Newport | 5%
| Valley Power | 1%
| Hallett GT | 1%
| Dry Creek | 1%
| Ladbroke Grove | 1%
| Mintaro | 1%
| Osborne | 5%
| Pelican Point | 2%
| Quarantine | 5%
| Torrens Island A | 5%
| Torrens Island B | 5%
| Bell Bay Three | 3%
| Tamar Valley | 1%
| Hunter Valley GT | 1%
| Mackay GT | 1%
| Mount Stuart | 1%
| Angaston | 2.5%
| Lonsdale | 2.5%
| Port Lincoln | 8%
| Port Lincoln 3 | 8%
| Port Stanvac | 2.5%
| Snuggery | 3%
| All hydro | 1%
| All wind | 1%
| All solar | 1%

## Emissions
TOC
Emissions
Source: AEMO 2018 ISP Assumptions Workbook
| Existing generators |  |  |  | Generic new entrant units, committed and advanced projects
| Generator | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh) | Generator | Emissions (kg/MWh)
| Bayswater | 865.5122 | 47.1309 | 912.6431 | Wind | 0
| Eraring | 862.3464 | 47.7966 | 910.1431 | Solar PV | 0
| Liddell | 930 | 50.5917 | 980.5917 | Biomass | 57.13
| Mount Piper | 862.3022 | 46.2162 | 908.5184 | Barker Inlet2 | 500.46
| Vales Point | 860 | 48.3051 | 908.3051 | Solar Thermal Central Receiver (6 hrs storage) | 0
| Callide B | 920 | 11.3435 | 931.3435 | Pumped Hydro (6hrs storage) / Large Scale Battery Storage (2hrs storage) | 0
| Callide Power Plant | 895.323 | 11.589 | 906.912
| Gladstone | 960 | 11.7614 | 971.7614 | New entrant combustion emissions3
| Kogan Creek | 820 | 11.04 | 831.04 |  | Emissions (kg/GJ)
| Millmerran | 830.1346 | 11.4634 | 841.598 | OCGT | 51.53
| Stanwell | 860.94 | 11.25 | 872.19 | CCGT | 51.53
| Tarong | 860.0221 | 11.4365 | 871.4586 | Black Coal (HELE) | 96.14
| Tarong North | 832.9647 | 10.7908 | 843.7555
| Loy Yang A | 1150 | 4.8176 | 1154.8176 | New entrant fugitive emissions
| Loy Yang B | 1136.0409 | 4.9805 | 1141.0214 |  | Gas Emissions (kg/GJ) | Coal Emissions (kg/GJ)
| Yallourn | 1310 | 5.5149 | 1315.5149 | Qld | 7.8 | 1.25
| Colongra | 640 | 142.56 | 782.56 | NSW | 12.8 | 5
| Smithfield | 480.9688 | 106.7707 | 587.7395 | Vic | 3.9
| Tallawarra | 358.1395 | 89.3952 | 447.5347 | SA | 10.4 | 2.5
| Uranquinty | 581.7116 | 142.56 | 724.2716 | Tas | 3.9
| Barcaldine | 999.9566 | 99.2829 | 1099.2394
| Braemar | 570.4776 | 92.664 | 663.1416 | Derived new entrant emissions (kg/MWh)
| Condamine | 454.3237 | 56.745 | 511.0687 | New entrant | Emissions4
| Darling Downs | 420.2045 | 57.3809 | 477.5854 | Qld OCGT | 602.1995
| Oakey | 760 | 85.2736 | 845.2736 | Qld CCGT | 411.1569
| Roma | 663.8544 | 92.664 | 756.5184 | NSW OCGT | 652.9495
| Swanbank E | 370 | 57.9523 | 427.9523 | NSW CCGT | 445.8069
| Yabulu | 450 | 59.2122 | 509.2122 | Vic OCGT | 562.6145
| Yabulu Steam Turbine | 450 | 59.2122 | 509.2122 | Vic CCGT | 384.1299
| Yarwun | 532.3129 | 80.9365 | 613.2494 | SA OCGT | 628.5895
| Somerton | 760 | 57.915 | 817.915 | SA CCGT | 429.1749
| Bairnsdale | 524.3273 | 40.8812 | 565.2085 | Tas OCGT | 562.6145
| Jeeralang A | 819.9338 | 59.4707 | 879.4045 | Tas CCGT | 384.1299
| Jeeralang B | 819.9338 | 59.4707 | 879.4045 | Qld Coal (HELE) | 843.787
| Laverton North | 745.3812 | 44.7987 | 790.1799 | NSW Coal (HELE) | 876.277
| Mortlake | 530 | 43.4362 | 573.4362 | SA Coal (HELE) | 854.617
| Newport | 530 | 40.0541 | 570.0541
| Valley Power | 813.6315 | 57.915 | 871.5465
| Hallett GT | 1020 | 154.44 | 1174.44
| Dry Creek | 1200 | 142.56 | 1342.56
| Ladbroke Grove | 530 | 123.552 | 653.552 | 2. Based on emissions factor of gas, modelled heat rate and fugitive emissions profile of Torrens Island A
| Mintaro | 820 | 132.3771 | 952.3771 | 3. New entrant gas units use standard emissions rate for natural gas combined with heat rates to derive emissions.
| Osborne | 460 | 84.6857 | 544.6857 | 4. Based on a new entrant with 2017 heat rate
| Pelican Point | 397.2675 | 76.44 | 473.7075
| Quarantine | 688.8094 | 111.15 | 799.9594
| Torrens Island A | 590 | 118.56 | 708.56
| Torrens Island B | 570 | 111.15 | 681.15
| Bell Bay Three | 617.7228 | 46.9614 | 664.6841
| Tamar Valley GT | 652.9757 | 49.6414 | 702.6171
| Tamar Valley ST | 410.3827 | 28.3725 | 438.7552
| Hunter Valley GT | 887.1814 | 45.8229 | 933.0043
| Mackay GT | 1000 | 45.8229 | 1045.8229
| Mount Stuart | 955.8648 | 42.768 | 998.6328
| Angaston1 | 940.2 | 73.4 | 1013.6
| Lonsdale1 | 1442 | 49.8 | 1491.8
| Port Lincoln | 1400 | 45.8585 | 1445.8585
| Port Lincoln 3 | 1400 | 45.8585 | 1445.8585
| Port Stanvac1 | 1442 | 49.8 | 1491.8
| Snuggery | 1400 | 48.3508 | 1448.3508
| Tailem Bend | 940.2 | 73.4 | 1013.6
| All hydro | 0 | 0 | 0
| All wind | 0 | 0 | 0
| All solar | 0 | 0 | 0
1. Not present in source material; previous (2014) value retained
No price on carbon emissions has been assumed in the modelling

## MLF
TOC
Marginal Loss Factors (MLFs)
Source: Regions and Marginal Loss Factors: FY 2018-19
Existing Generators*
Note:The MLF will be updated every 5 years in the long term modelling starting from the first year of the study and every subsequent 5 years after. The 2018-19 MLFs will only be used in the first pass of the Long-Term Investment Planning model.
* Using published values from the 2018-19 MLFs
| Generator | Marginal loss factor (2018-19)
| Barcaldine Solar at Lilyvale (132) | 0.8934
| Barron Gorge Power Station (PS) Unit 1 | 0.9346
| Barron Gorge PS Unit 2 | 0.9346
| Braemar PS Unit 1 | 0.9709
| Braemar PS Unit 2 | 0.9709
| Braemar PS Unit 3 | 0.9709
| Braemar Stage 2 PS Unit 5 | 0.9709
| Braemar Stage 2 PS Unit 6 | 0.9709
| Braemar Stage 2 PS Unit 7 | 0.9709
| Callide PS Load | 0.9048
| Callide A PS Unit 4 | 0.9074
| Callide A PS Unit 4 Load | 0.9074
| Callide B PS Unit 1 | 0.9069
| Callide B PS Unit 2 | 0.9069
| Callide C PS Unit 3 | 0.908
| Callide C PS Unit 4 | 0.908
| Clare Solar Farm | 0.8727
| Columboola – Condamine PS | 0.9882
| Darling Downs PS | 0.9709
| Gladstone PS (132 kV) Unit 3 | 0.9206
| Darling Downs Solar Farm | 0.9812
| Gladstone PS (132 kV) Unit 4 | 0.9206
| Gladstone PS (132kV) Load | 0.9206
| Gladstone PS (275 kV) Unit 1 | 0.924
| Gladstone PS (275 kV) Unit 2 | 0.924
| Gladstone PS (275 kV) Unit 5 | 0.924
| Gladstone PS (275 kV) Unit 6 | 0.924
| Hamilton Solar Farm | 0.8741
| Hughenden SF | 0.8842
| Kareeya PS Unit 1 | 0.9523
| Kareeya PS Unit 2 | 0.9523
| Kareeya PS Unit 3 | 0.9523
| Kareeya PS Unit 4 | 0.9523
| Kidston Solar Farm | 0.8842
| Kogan Creek PS | 0.9743
| Koombooloomba | 0.9523
| Millmerran PS Unit 1 | 0.9812
| Millmerran PS Unit 2 | 0.9812
| Mt Stuart PS Unit 1 | 0.8842
| Mt Stuart PS Unit 2 | 0.8842
| Mt Stuart PS Unit 3 | 0.8842
| Oakey PS Unit 1 | 0.9562
| Oakey PS Unit 2 | 0.9562
| Ross River Solar Farm | 0.8842
| Stanwell PS Load | 0.9104
| Stanwell PS Unit 1 | 0.9075
| Stanwell PS Unit 2 | 0.9075
| Stanwell PS Unit 3 | 0.9075
| Stanwell PS Unit 4 | 0.9075
| Staplyton | 1.0116
| Sun Metals Solar Farm | 1.0092
| Swanbank E GT | 1.0009
| Tarong North PS | 0.9755
| Tarong PS Unit 1 | 0.9752
| Tarong PS Unit 2 | 0.9752
| Tarong PS Unit 3 | 0.9752
| Tarong PS Unit 4 | 0.9752
| Whitsunday Solar Farm | 0.8741
| Wivenhoe Generation Unit 1 | 0.9939
| Wivenhoe Generation Unit 2 | 0.9939
| Wivenhoe Pump 1 | 0.9974
| Wivenhoe Pump 2 | 0.9974
| Yabulu PS | 0.9346
| Yarwun PS | 0.9245
| Bayswater PS Unit 1 | 0.9538
| Bayswater PS Unit 2 | 0.9538
| Bayswater PS Unit 3 | 0.9555
| Bayswater PS Unit 4 | 0.9555
| Blowering | 0.99
| Bodangora Wind Farm | 0.9819
| Broken Hill GT 1 | 1.0603
| Burrinjuck | 1.0124
| Capital Wind Farm | 1.01
| Colongra PS Unit 1 | 0.9827
| Colongra PS Unit 2 | 0.9827
| Colongra PS Unit 3 | 0.9827
| Colongra PS Unit 4 | 0.9827
| Eraring 330 PS Unit 1 | 0.9828
| Eraring 330 PS Unit 2 | 0.9828
| Eraring 500 PS Unit 3 | 0.9853
| Eraring 500 PS Unit 4 | 0.9853
| Eraring PS Load | 0.9853
| Griffith Solar Farm | 1.0603
| Gullen Range Solar Farm | 0.9959
| Gullen Range Wind Farm | 0.9959
| Guthega | 0.9537
| Guthega Auxiliary Supply | 1.0256
| Hume (New South Wales Share) | 1.0675
| Kangaroo Valley – Bendeela (Shoalhaven) Generation – dual MLF | 0.9981
| Kangaroo Valley (Shoalhaven) Pumps – dual MLF | 1.0137
| Liddell 330 PS Load | 0.9537
| Liddell 330 PS Unit 1 | 0.9537
| Liddell 330 PS Unit 2 | 0.9537
| Liddell 330 PS Unit 3 | 0.9537
| Liddell 330 PS Unit 4 | 0.9537
| Lower Tumut Generation – dual MLF | 0.9954
| Lower Tumut Pipeline Auxiliary | 1.0438
| Lower Tumut Pumps – dual MLF | 1.0545
| Lower Tumut T2 Auxiliary | 1.0438
| Lower Tumut T4 Auxiliary | 1.0438
| Mt Piper PS Load | 0.9738
| Mt Piper PS Unit 1 | 0.9738
| Mt Piper PS Unit 2 | 0.9738
| Murray (Geehi Tee off Auxiliary) | 0.9069
| Murray Power Station M1 Auxiliary | 0.9069
| Murray Power Station M2 Auxiliary | 0.9069
| Parkes Solar Farm | 0.9964
| Sapphire Wind Farm | 0.8821
| Silverton Wind Farm | 1.0062
| Upper Tumut | 1.0112
| Uranquinty PS Unit 11 | 0.9609
| Uranquinty PS Unit 12 | 0.9609
| Uranquinty PS Unit 13 | 0.9609
| Uranquinty PS Unit 14 | 0.9609
| Vales Point 330 PS Load | 0.9851
| Vales Point 330 PS Unit 5 | 0.9851
| Vales Point 330 PS Unit 6 | 0.9851
| Woodlawn Wind Farm | 1.01
| White Rock Wind Farm | 0.8413
| Ararat WF | 0.9691
| Banimboola | 0.9249
| Bannerton Solar Farm | 1.0062
| Basslink (Loy Yang Power Station Switchyard) Tasmania to Victoria | 0.9839
| Dartmouth PS | 0.9249
| Eildon PS Unit 1 | 0.9782
| Eildon PS Unit 2 | 0.9782
| Hazelwood PS Load | 0.9813
| Jeeralang A PS Unit 1 | 0.9783
| Jeeralang A PS Unit 2 | 0.9783
| Jeeralang A PS Unit 3 | 0.9783
| Jeeralang A PS Unit 4 | 0.9783
| Jeeralang B PS Unit 1 | 0.9783
| Jeeralang B PS Unit 2 | 0.9783
| Jeeralang B PS Unit 3 | 0.9783
| Jindabyne pump at Guthega | 1.0124
| Kiata Wind Farm | 0.9911
| Laverton PS (LNGS1) | 1.0018
| Laverton PS (LNGS2) | 1.0018
| Loy Yang A PS Load | 0.9798
| Loy Yang A PS Unit 1 | 0.9798
| Loy Yang A PS Unit 2 | 0.9798
| Loy Yang A PS Unit 3 | 0.9798
| Loy Yang A PS Unit 4 | 0.9798
| Loy Yang B PS Unit 1 | 0.9798
| Loy Yang B PS Unit 2 | 0.9798
| MacArthur Wind Farm | 0.9971
| McKay Creek / Bogong PS | 0.9265
| Mortlake Unit 1 | 0.9961
| Mortlake Unit 2 | 0.9961
| Mt Mercer Windfarm | 0.9909
| Murray | 0.9069
| Newport PS | 0.9962
| Salt Creek Wind Farm | 1.0076
| Valley Power Unit 1 | 0.9798
| Valley Power Unit 2 | 0.9798
| Valley Power Unit 3 | 0.9798
| Valley Power Unit 4 | 0.9798
| Valley Power Unit 5 | 0.9798
| Valley Power Unit 6 | 0.9798
| Waubra Wind Farm | 0.9784
| West Kiewa PS Unit 1 | 0.9607
| West Kiewa PS Unit 2 | 0.9607
| Yallourn W PS 220 Load | 0.9573
| Yallourn W PS 220 Unit 1 | 0.9696
| Yallourn W PS 220 Unit 2 | 0.9573
| Yallourn W PS 220 Unit 3 | 0.9573
| Yallourn W PS 220 Unit 4 | 0.9573
| Yaloak South WF | 1.0016
| Bungala one Solar Farm | 0.97
| Cathedral Rocks Wind Farm | 0.886
| Clements Gap Wind Farm | 0.9683
| Dry Creek PS Unit 1 | 1.003
| Dry Creek PS Unit 2 | 1.003
| Dry Creek PS Unit 3 | 1.003
| Dalrymple North BESS - Gen | 0.888
| Dalrymple North BESS - Load | 0.9326
| Hallett 2 Wind Farm | 0.9715
| Hallett PS | 0.9715
| Hallett Wind Farm | 0.9715
| Hornsdale Wind Farm Stage 1 | 0.9744
| Hornsdale Wind Farm Stage 2 | 0.9744
| Hornsdale Wind Farm Stage 3 | 0.9744
| Hornsdale Battery – generation | 0.9771
| Hornsdale Battery – load | 0.9853
| Ladbroke Grove PS Unit 1 | 0.9474
| Ladbroke Grove PS Unit 2 | 0.9474
| Lake Bonney Wind Farm | 0.9144
| Lake Bonney Wind Farm Stage 2 | 0.9144
| Lake Bonney Wind Farm Stage 3 | 0.9144
| Mintaro PS | 0.9942
| Mt Millar Wind Farm | 0.9055
| North Brown Hill Wind Farm | 0.9674
| O.C.P.L. Unit 1 | 0.9992
| Pelican Point PS | 1.0005
| Port Lincoln 3 | 1.0383
| Port Lincoln PS | 0.9691
| Quarantine PS Unit 1 | 0.9854
| Quarantine PS Unit 2 | 0.9854
| Quarantine PS Unit 3 | 0.9854
| Quarantine PS Unit 4 | 0.9854
| Quarantine PS Unit 5 | 0.9854
| Snowtown WF Stage 2 – North | 0.9813
| Snowtown WF Stage 2 – South | 0.9813
| Snowtown Wind Farm | 0.9203
| Snuggery PS Units 1 to 3 | 0.9325
| The Bluff wind Farm | 0.9674
| Torrens Island PS A Unit 1 | 1.0009
| Torrens Island PS A Unit 2 | 1.0009
| Torrens Island PS A Unit 3 | 1.0009
| Torrens Island PS A Unit 4 | 1.0009
| Torrens Island PS B Unit 1 | 1.0009
| Torrens Island PS B Unit 2 | 1.0009
| Torrens Island PS B Unit 3 | 1.0009
| Torrens Island PS B Unit 4 | 1.0009
| Torrens Island PS Load | 1
| Waterloo Wind Farm | 0.9712
| Wattle Point Wind Farm | 0.8279
| Basslink (George Town) | 1
| Bastyan | 0.941
| Bell Bay No.3 | 1.0003
| Bell Bay No.3 | 1.0003
| Bell Bay No.3 | 1.0003
| Bluff Point and Studland Bay Wind Farms | 0.8952
| Butlers Gorge | 0.935
| Catagunya | 0.9977
| Cethana | 0.9628
| Cluny | 1.0019
| Devils gate | 0.9692
| Fisher | 0.966
| Gordon | 0.9868
| John Butters | 0.9365
| Lake Echo | 0.9385
| Lemonthyme | 0.9701
| Liapootah | 0.9977
| Mackintosh | 0.9282
| Meadowbank | 0.9773
| Musselroe | 0.9105
| Paloona | 0.9771
| Poatina | 0.9912
| Poatina | 0.9799
| Reece No.1 | 0.935
| Reece No.2 | 0.9264
| Repulse | 1.0019
| Rowallan | 0.966
| Tamar Valley CCGT | 0.9999
| Tamar Valley OCGT | 1.0003
| Tarraleah | 0.9405
| Trevallyn | 0.9909
| Tribute | 0.9377
| Tungatinah | 0.9184
| Wayatinah | 0.9977
| Wilmot | 0.9701