## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Blackwater
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -23.586
| Constrained connection point longitude (decimal degrees) | 148.825
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 208.3453 | 212.68 | 216.3121 | 216.0913 | 216.7801 | 218.3953 | 219.3575 | 220.122 | 220.8844 | 221.4312 | 221.9885
| 50% PoE | 198.126 | 202.248 | 205.702 | 205.492 | 206.147 | 207.683 | 208.598 | 209.325 | 210.05 | 210.57 | 211.1
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 89.679 | 89.638 | 89.55 | 89.498 | 89.451 | 89.404 | 89.358 | 89.312 | 89.252 | 89.2 | 89.153
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 194.5423 | 198.3848 | 198.2092 | 198.9127 | 200.5268 | 201.4996 | 202.2756 | 203.0506 | 203.6195 | 204.2316 | 204.1905
| 50% PoE | 185 | 188.654 | 188.487 | 189.156 | 190.691 | 191.616 | 192.354 | 193.091 | 193.632 | 194.214 | 194.175
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | 19.803 | 21.389 | 21.39 | 21.391 | 21.392 | 21.393 | 21.394 | 21.395 | 21.396 | 21.398 | 21.398
12 | Voltage Level (kV) | 132
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.8 | 169.4 | 169.4
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.5 | 188.2 | 188.2
14 | Load duration curve
15 | Preferred investment | Blackwater 132kV secondary systems replacement
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) | [8 empty] | 13
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) | [8 empty] | 0.26 | 0.26 | 0.26
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2029-06-30
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Secondary systems
26 | Unplanned outages
27 | Maximum fault level (kA) | 7.1
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.4791 | 25.4911 | 25.4871
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.5 | 636.8 | 636.7

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 121.904 | 121.904 | 105.001 | 104.994 | 104.99 | 104.986 | 104.982 | 104.979 | 104.975 | 104.97 | 104.965
1:00 | 128.101 | 128.101 | 108.874 | 108.868 | 108.864 | 108.86 | 108.856 | 108.852 | 108.848 | 108.844 | 108.838
1:30 | 133.216 | 133.217 | 116.087 | 116.081 | 116.077 | 116.073 | 116.069 | 116.065 | 116.061 | 116.056 | 116.051
2:00 | 123.369 | 123.369 | 110.547 | 110.541 | 110.537 | 110.533 | 110.529 | 110.525 | 110.522 | 110.517 | 110.511
2:30 | 116.421 | 116.421 | 93.22 | 93.214 | 93.21 | 93.206 | 93.202 | 93.199 | 93.195 | 93.191 | 93.185
3:00 | 119.336 | 119.336 | 94.388 | 94.382 | 94.379 | 94.375 | 94.371 | 94.367 | 94.363 | 94.359 | 94.353
3:30 | 116.899 | 116.899 | 86.487 | 86.481 | 86.477 | 86.473 | 86.47 | 86.466 | 86.463 | 86.458 | 86.453
4:00 | 116.473 | 116.473 | 94.208 | 94.202 | 94.198 | 94.194 | 94.191 | 94.187 | 94.184 | 94.179 | 94.174
4:30 | 118.315 | 118.314 | 98.938 | 98.933 | 98.928 | 98.924 | 98.921 | 98.917 | 98.913 | 98.909 | 98.904
5:00 | 128.52 | 128.52 | 94.061 | 94.055 | 94.052 | 94.048 | 94.044 | 94.041 | 94.037 | 94.033 | 94.028
5:30 | 127.479 | 127.479 | 96.814 | 96.808 | 96.805 | 96.801 | 96.797 | 96.794 | 96.79 | 96.786 | 96.78
6:00 | 128.752 | 128.752 | 94.487 | 94.481 | 94.477 | 94.473 | 94.47 | 94.467 | 94.463 | 94.46 | 94.455
6:30 | 111.613 | 111.613 | 96.407 | 96.402 | 96.398 | 96.395 | 96.391 | 96.389 | 96.385 | 96.382 | 96.378
7:00 | 141.976 | 141.966 | 102.101 | 102.094 | 102.09 | 102.086 | 102.082 | 102.079 | 102.076 | 102.073 | 102.068
7:30 | 148.953 | 148.929 | 127.125 | 127.107 | 127.096 | 127.084 | 127.073 | 127.063 | 127.052 | 127.04 | 127.024
8:00 | 141.802 | 141.758 | 141.728 | 141.7 | 141.683 | 141.665 | 141.649 | 141.634 | 141.618 | 141.6 | 141.579
8:30 | 151.639 | 151.577 | 166.507 | 166.415 | 166.972 | 168.263 | 169.043 | 169.673 | 170.299 | 170.769 | 171.221
9:00 | 161.603 | 161.522 | 141.441 | 141.309 | 141.857 | 143.103 | 143.851 | 144.452 | 145.049 | 145.49 | 145.91
9:30 | 154.11 | 157.902 | 151.797 | 151.649 | 152.231 | 153.562 | 154.358 | 154.998 | 155.633 | 156.099 | 156.543
10:00 | 175.052 | 178.915 | 147.37 | 147.198 | 147.762 | 149.071 | 149.849 | 150.47 | 151.087 | 151.53 | 151.952
10:30 | 198.126 | 202.248 | 166.672 | 166.478 | 167.079 | 168.488 | 169.324 | 169.99 | 170.652 | 171.126 | 171.59
11:00 | 179.872 | 183.854 | 160.307 | 160.095 | 160.707 | 162.152 | 163.007 | 163.686 | 164.362 | 164.842 | 165.312
11:30 | 182.873 | 186.692 | 160.254 | 160.042 | 160.629 | 162.02 | 162.844 | 163.496 | 164.146 | 164.607 | 165.071
12:00 | 183.026 | 186.98 | 169.62 | 169.399 | 170.012 | 171.466 | 172.328 | 173.009 | 173.69 | 174.171 | 174.656
12:30 | 185.99 | 189.979 | 170.263 | 170.044 | 170.666 | 172.135 | 173.007 | 173.697 | 174.384 | 174.873 | 175.365
13:00 | 190.441 | 194.391 | 181.41 | 181.188 | 181.802 | 183.259 | 184.122 | 184.805 | 185.487 | 185.968 | 186.454
13:30 | 178.906 | 182.886 | 173.756 | 173.544 | 174.179 | 175.674 | 176.565 | 177.27 | 177.975 | 178.478 | 178.99
14:00 | 192.448 | 196.502 | 205.702 | 205.492 | 206.147 | 207.683 | 208.598 | 209.325 | 210.05 | 210.57 | 211.1
14:30 | 184.725 | 188.812 | 167.832 | 167.644 | 168.273 | 169.739 | 170.615 | 171.313 | 172.008 | 172.511 | 173.021
15:00 | 185.567 | 189.579 | 162.682 | 162.523 | 163.144 | 164.573 | 165.433 | 166.118 | 166.803 | 167.305 | 167.819
15:30 | 187.236 | 191.326 | 160.094 | 159.95 | 160.581 | 162.02 | 162.889 | 163.584 | 164.278 | 164.792 | 165.316
16:00 | 197.461 | 201.755 | 170.305 | 170.186 | 170.841 | 172.311 | 173.205 | 173.922 | 174.64 | 175.179 | 175.724
16:30 | 193.581 | 197.806 | 155.327 | 155.242 | 155.85 | 157.197 | 158.021 | 158.684 | 159.348 | 159.854 | 160.364
17:00 | 183.832 | 187.868 | 146.506 | 146.483 | 146.47 | 146.458 | 146.447 | 146.436 | 146.425 | 146.645 | 147.143
17:30 | 170.253 | 174.224 | 131.282 | 131.272 | 131.266 | 131.262 | 131.257 | 131.253 | 131.249 | 131.244 | 131.242
18:00 | 161.358 | 163.35 | 123.444 | 123.441 | 123.44 | 123.442 | 123.444 | 123.445 | 123.447 | 123.448 | 123.457
18:30 | 126.154 | 126.147 | 109.363 | 109.367 | 109.37 | 109.376 | 109.382 | 109.386 | 109.392 | 109.398 | 109.411
19:00 | 134.609 | 134.613 | 112.251 | 112.249 | 112.248 | 112.25 | 112.252 | 112.252 | 112.253 | 112.254 | 112.262
19:30 | 141.455 | 141.459 | 116.113 | 116.11 | 116.109 | 116.111 | 116.113 | 116.114 | 116.115 | 116.116 | 116.124
20:00 | 141.572 | 141.576 | 112.782 | 112.78 | 112.78 | 112.783 | 112.785 | 112.787 | 112.788 | 112.79 | 112.799
20:30 | 132.125 | 132.129 | 102.411 | 102.409 | 102.409 | 102.412 | 102.414 | 102.415 | 102.417 | 102.418 | 102.427
21:00 | 138.753 | 138.757 | 109.062 | 109.06 | 109.06 | 109.062 | 109.065 | 109.066 | 109.067 | 109.069 | 109.078
21:30 | 137.71 | 137.713 | 109.445 | 109.442 | 109.441 | 109.442 | 109.444 | 109.444 | 109.444 | 109.444 | 109.45
22:00 | 146.506 | 146.507 | 95.635 | 95.632 | 95.63 | 95.631 | 95.632 | 95.631 | 95.632 | 95.631 | 95.636
22:30 | 139.389 | 139.391 | 97.652 | 97.649 | 97.647 | 97.647 | 97.647 | 97.646 | 97.645 | 97.644 | 97.647
23:00 | 139.549 | 139.55 | 97.877 | 97.873 | 97.872 | 97.871 | 97.871 | 97.87 | 97.87 | 97.868 | 97.871
23:30 | 122.589 | 122.59 | 104.609 | 104.605 | 104.603 | 104.603 | 104.602 | 104.601 | 104.6 | 104.598 | 104.6
0:00 | 125.35 | 125.351 | 100.775 | 100.769 | 100.766 | 100.762 | 100.758 | 100.754 | 100.75 | 100.746 | 100.74

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 26.308 | 27.994 | 27.995 | 27.996 | 27.998 | 28 | 28.001 | 28.003 | 28.004 | 28.008 | 28.008
1:00 | 27.403 | 29.065 | 29.067 | 29.068 | 29.069 | 29.071 | 29.072 | 29.073 | 29.075 | 29.078 | 29.079
1:30 | 26.563 | 28.226 | 28.227 | 28.228 | 28.229 | 28.231 | 28.232 | 28.233 | 28.234 | 28.237 | 28.237
2:00 | 37.561 | 39.211 | 39.212 | 39.213 | 39.214 | 39.215 | 39.216 | 39.218 | 39.219 | 39.222 | 39.222
2:30 | 35.79 | 37.446 | 37.446 | 37.447 | 37.448 | 37.45 | 37.45 | 37.451 | 37.452 | 37.455 | 37.455
3:00 | 30.058 | 31.664 | 31.665 | 31.666 | 31.667 | 31.668 | 31.669 | 31.67 | 31.671 | 31.673 | 31.673
3:30 | 32.224 | 33.845 | 33.845 | 33.846 | 33.846 | 33.847 | 33.847 | 33.848 | 33.848 | 33.85 | 33.85
4:00 | 29.959 | 31.576 | 31.576 | 31.577 | 31.577 | 31.578 | 31.578 | 31.579 | 31.579 | 31.58 | 31.58
4:30 | 30.713 | 32.352 | 32.352 | 32.353 | 32.353 | 32.354 | 32.354 | 32.355 | 32.355 | 32.357 | 32.357
5:00 | 28.38 | 29.993 | 29.993 | 29.994 | 29.994 | 29.995 | 29.995 | 29.996 | 29.997 | 29.998 | 29.998
5:30 | 26.367 | 27.948 | 27.948 | 27.949 | 27.95 | 27.95 | 27.951 | 27.951 | 27.952 | 27.954 | 27.954
6:00 | 27.721 | 29.314 | 29.314 | 29.313 | 29.313 | 29.313 | 29.313 | 29.312 | 29.313 | 29.312 | 29.313
6:30 | 33.636 | 35.277 | 35.274 | 35.271 | 35.269 | 35.266 | 35.264 | 35.262 | 35.26 | 35.257 | 35.256
7:00 | 53.304 | 53.405 | 53.393 | 53.384 | 53.376 | 53.367 | 53.36 | 53.352 | 53.343 | 53.332 | 53.328
7:30 | 60.72 | 60.805 | 60.782 | 60.768 | 60.753 | 60.739 | 60.726 | 60.713 | 60.697 | 60.679 | 60.67
8:00 | 74.84 | 74.906 | 74.866 | 74.842 | 74.816 | 74.792 | 74.77 | 74.747 | 74.72 | 74.688 | 74.671
8:30 | 86.675 | 86.712 | 86.655 | 86.618 | 86.579 | 86.543 | 86.51 | 86.475 | 86.434 | 86.381 | 86.356
9:00 | 81.056 | 81.136 | 81.065 | 81.02 | 80.973 | 80.927 | 80.886 | 80.842 | 80.791 | 80.726 | 80.694
9:30 | 79.628 | 79.697 | 79.617 | 79.567 | 79.513 | 79.463 | 79.416 | 79.367 | 79.309 | 79.236 | 79.198
10:00 | 89.006 | 89.05 | 88.955 | 88.896 | 88.834 | 88.773 | 88.717 | 88.659 | 88.588 | 88.502 | 88.455
10:30 | 84.997 | 85.018 | 84.92 | 84.859 | 84.8 | 84.742 | 84.687 | 84.629 | 84.559 | 84.482 | 84.432
11:00 | 92.777 | 92.783 | 92.677 | 92.612 | 92.549 | 92.486 | 92.426 | 92.365 | 92.29 | 92.208 | 92.152
11:30 | 80.458 | 80.453 | 80.353 | 80.292 | 80.235 | 80.18 | 80.125 | 80.07 | 80 | 79.933 | 79.878
12:00 | 86.779 | 86.759 | 86.657 | 86.595 | 86.537 | 86.48 | 86.426 | 86.37 | 86.298 | 86.231 | 86.176
12:30 | 93.022 | 93.001 | 92.896 | 92.832 | 92.774 | 92.716 | 92.659 | 92.601 | 92.529 | 92.46 | 92.403
13:00 | 83.959 | 83.934 | 83.833 | 83.772 | 83.714 | 83.657 | 83.603 | 83.547 | 83.477 | 83.41 | 83.355
13:30 | 91.707 | 91.677 | 91.578 | 91.519 | 91.465 | 91.412 | 91.359 | 91.306 | 91.239 | 91.177 | 91.124
14:00 | 95.845 | 95.816 | 95.722 | 95.664 | 95.613 | 95.563 | 95.513 | 95.463 | 95.398 | 95.34 | 95.289
14:30 | 89.371 | 89.354 | 89.272 | 89.221 | 89.177 | 89.134 | 89.09 | 89.047 | 88.991 | 88.942 | 88.897
15:00 | 93.803 | 93.765 | 93.677 | 93.625 | 93.577 | 93.53 | 93.484 | 93.438 | 93.378 | 93.326 | 93.278
15:30 | 84.371 | 84.343 | 84.266 | 84.22 | 84.179 | 84.138 | 84.098 | 84.057 | 84.006 | 83.958 | 83.917
16:00 | 96.658 | 96.643 | 96.578 | 96.539 | 96.504 | 96.47 | 96.436 | 96.402 | 96.358 | 96.318 | 96.283
16:30 | 91.945 | 91.934 | 91.88 | 91.849 | 91.821 | 91.795 | 91.768 | 91.742 | 91.707 | 91.68 | 91.652
17:00 | 84.91 | 84.911 | 84.874 | 84.852 | 84.834 | 84.818 | 84.8 | 84.783 | 84.76 | 84.746 | 84.726
17:30 | 66.45 | 66.454 | 66.431 | 66.417 | 66.407 | 66.397 | 66.386 | 66.376 | 66.363 | 66.356 | 66.343
18:00 | 64.208 | 64.229 | 64.221 | 64.218 | 64.217 | 64.217 | 64.215 | 64.214 | 64.212 | 64.218 | 64.214
18:30 | 42.796 | 43.545 | 43.543 | 43.542 | 43.544 | 43.546 | 43.546 | 43.547 | 43.548 | 43.555 | 43.553
19:00 | 31.899 | 33.529 | 33.531 | 33.533 | 33.538 | 33.542 | 33.545 | 33.549 | 33.553 | 33.563 | 33.563
19:30 | 37.698 | 39.212 | 39.215 | 39.218 | 39.224 | 39.23 | 39.234 | 39.239 | 39.244 | 39.258 | 39.258
20:00 | 38.389 | 39.869 | 39.872 | 39.875 | 39.881 | 39.886 | 39.89 | 39.895 | 39.9 | 39.912 | 39.913
20:30 | 32.372 | 34.045 | 34.048 | 34.051 | 34.057 | 34.062 | 34.066 | 34.071 | 34.077 | 34.089 | 34.09
21:00 | 32.564 | 34.323 | 34.327 | 34.33 | 34.336 | 34.341 | 34.345 | 34.35 | 34.355 | 34.368 | 34.368
21:30 | 30.046 | 31.769 | 31.772 | 31.774 | 31.778 | 31.782 | 31.785 | 31.789 | 31.792 | 31.802 | 31.802
22:00 | 27.98 | 29.759 | 29.76 | 29.762 | 29.764 | 29.767 | 29.769 | 29.771 | 29.773 | 29.779 | 29.779
22:30 | 40.357 | 42.222 | 42.224 | 42.225 | 42.228 | 42.23 | 42.232 | 42.234 | 42.236 | 42.242 | 42.242
23:00 | 38.758 | 40.577 | 40.578 | 40.58 | 40.583 | 40.586 | 40.588 | 40.59 | 40.593 | 40.599 | 40.6
23:30 | 33.133 | 34.981 | 34.983 | 34.984 | 34.987 | 34.989 | 34.991 | 34.994 | 34.996 | 35.002 | 35.002
0:00 | 25.269 | 26.903 | 26.904 | 26.905 | 26.906 | 26.907 | 26.908 | 26.909 | 26.911 | 26.914 | 26.914

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 106 | 105.856 | 105.856 | 105.857 | 105.857 | 105.858 | 105.858 | 105.858 | 105.859 | 114.832 | 114.832
1:00 | 102 | 102.019 | 102.019 | 102.019 | 102.019 | 102.019 | 102.019 | 102.019 | 102.019 | 111.978 | 111.978
1:30 | 108 | 107.842 | 107.842 | 107.843 | 107.843 | 107.844 | 107.845 | 107.845 | 107.846 | 111.988 | 111.988
2:00 | 111 | 110.974 | 110.974 | 110.974 | 110.974 | 110.974 | 110.974 | 110.974 | 110.974 | 109.848 | 109.849
2:30 | 111 | 111.114 | 111.114 | 111.114 | 111.115 | 111.116 | 111.116 | 111.117 | 111.117 | 112.538 | 112.538
3:00 | 114 | 114.331 | 114.331 | 114.331 | 114.331 | 114.33 | 114.33 | 114.33 | 114.33 | 108.426 | 108.426
3:30 | 118 | 118.273 | 118.272 | 118.272 | 118.272 | 118.272 | 118.272 | 118.271 | 118.271 | 101.955 | 101.955
4:00 | 110 | 109.654 | 109.654 | 109.654 | 109.654 | 109.653 | 109.653 | 109.653 | 109.653 | 114.665 | 114.666
4:30 | 123 | 122.975 | 122.975 | 122.975 | 122.974 | 122.974 | 122.973 | 122.973 | 122.973 | 103.962 | 103.963
5:00 | 114 | 114.123 | 114.123 | 114.123 | 114.122 | 114.122 | 114.122 | 114.122 | 114.122 | 105.559 | 105.56
5:30 | 117 | 117.306 | 117.305 | 117.305 | 117.305 | 117.304 | 117.304 | 117.304 | 117.304 | 103.51 | 103.511
6:00 | 119 | 119.444 | 119.443 | 119.443 | 119.443 | 119.443 | 119.443 | 119.443 | 119.443 | 98.792 | 98.793
6:30 | 109 | 109.393 | 109.392 | 109.392 | 109.392 | 109.392 | 109.392 | 109.392 | 109.393 | 96.997 | 96.998
7:00 | 111 | 111.322 | 111.322 | 111.322 | 111.321 | 111.322 | 111.322 | 111.323 | 111.324 | 97.839 | 97.838
7:30 | 132 | 132.452 | 132.444 | 132.439 | 132.434 | 132.43 | 132.426 | 132.422 | 132.418 | 113.313 | 113.308
8:00 | 133 | 133.307 | 133.288 | 133.278 | 133.267 | 133.258 | 133.249 | 133.239 | 133.229 | 131.917 | 131.901
8:30 | 133 | 132.754 | 132.722 | 132.701 | 132.678 | 132.657 | 132.639 | 132.618 | 132.596 | 149.755 | 149.734
9:00 | 137 | 136.459 | 136.414 | 136.387 | 136.357 | 136.33 | 136.304 | 136.283 | 136.756 | 151.394 | 151.368
9:30 | 144 | 143.65 | 143.594 | 143.559 | 143.522 | 143.487 | 143.623 | 144.253 | 144.723 | 163.996 | 163.952
10:00 | 147 | 147.33 | 147.195 | 147.766 | 149.065 | 149.845 | 150.471 | 151.094 | 151.553 | 163.797 | 163.751
10:30 | 148 | 148.268 | 148.192 | 148.471 | 149.766 | 150.541 | 151.16 | 151.776 | 152.225 | 167.956 | 167.903
11:00 | 159 | 162.281 | 162.093 | 162.698 | 164.11 | 164.95 | 165.619 | 166.284 | 166.763 | 166.237 | 166.172
11:30 | 151 | 152.622 | 152.437 | 153.023 | 154.394 | 155.211 | 155.86 | 156.507 | 156.972 | 162.125 | 162.054
12:00 | 158 | 161.986 | 161.791 | 162.396 | 163.811 | 164.654 | 165.324 | 165.991 | 166.47 | 164.664 | 164.587
12:30 | 149 | 153.056 | 152.878 | 153.466 | 154.835 | 155.652 | 156.303 | 156.951 | 157.419 | 157.471 | 157.392
13:00 | 153 | 156.582 | 156.402 | 156.982 | 158.337 | 159.144 | 159.786 | 160.427 | 160.887 | 168.272 | 168.19
13:30 | 165 | 168.345 | 168.158 | 168.753 | 170.144 | 170.972 | 171.631 | 172.288 | 172.759 | 172.733 | 172.661
14:00 | 159 | 162.865 | 162.701 | 163.301 | 164.684 | 165.513 | 166.175 | 166.835 | 167.315 | 176.832 | 176.76
14:30 | 174 | 178.252 | 178.078 | 178.713 | 180.18 | 181.06 | 181.761 | 182.462 | 182.972 | 186.284 | 186.217
15:00 | 185 | 188.654 | 188.487 | 189.156 | 190.691 | 191.616 | 192.354 | 193.091 | 193.632 | 182.897 | 182.836
15:30 | 163 | 167.038 | 166.909 | 167.559 | 169.027 | 169.917 | 170.631 | 171.344 | 171.877 | 180.264 | 180.216
16:00 | 177 | 180.831 | 180.711 | 181.359 | 182.815 | 183.699 | 184.409 | 185.119 | 185.651 | 194.214 | 194.175
16:30 | 167 | 171.103 | 171.004 | 171.657 | 173.111 | 173.999 | 174.714 | 175.429 | 175.972 | 184.721 | 184.695
17:00 | 165 | 169.014 | 168.932 | 169.572 | 170.984 | 171.85 | 172.548 | 173.247 | 173.781 | 182.18 | 182.168
17:30 | 147 | 150.58 | 150.523 | 151.148 | 152.513 | 153.356 | 154.037 | 154.72 | 155.249 | 175.693 | 175.697
18:00 | 137 | 136.991 | 136.984 | 136.982 | 136.983 | 136.984 | 136.983 | 136.984 | 136.983 | 144.916 | 144.93
18:30 | 112 | 111.954 | 111.958 | 111.962 | 111.969 | 111.975 | 111.98 | 111.986 | 111.993 | 119.201 | 119.2
19:00 | 115 | 115.203 | 115.206 | 115.209 | 115.215 | 115.22 | 115.223 | 115.228 | 115.233 | 121.163 | 121.164
19:30 | 128 | 127.906 | 127.909 | 127.913 | 127.919 | 127.925 | 127.929 | 127.934 | 127.94 | 139.58 | 139.581
20:00 | 130 | 129.603 | 129.607 | 129.61 | 129.617 | 129.623 | 129.627 | 129.632 | 129.638 | 128.671 | 128.672
20:30 | 131 | 131.463 | 131.466 | 131.47 | 131.476 | 131.482 | 131.486 | 131.492 | 131.497 | 122.895 | 122.896
21:00 | 123 | 122.795 | 122.798 | 122.802 | 122.808 | 122.814 | 122.818 | 122.823 | 122.828 | 120.291 | 120.291
21:30 | 120 | 120.125 | 120.127 | 120.129 | 120.133 | 120.137 | 120.14 | 120.143 | 120.146 | 124.521 | 124.522
22:00 | 117 | 117.415 | 117.417 | 117.418 | 117.42 | 117.422 | 117.423 | 117.425 | 117.427 | 122.846 | 122.847
22:30 | 112 | 112.453 | 112.455 | 112.456 | 112.458 | 112.46 | 112.462 | 112.463 | 112.465 | 127.232 | 127.232
23:00 | 112 | 112.211 | 112.212 | 112.214 | 112.216 | 112.218 | 112.219 | 112.221 | 112.223 | 123.298 | 123.298
23:30 | 111 | 110.927 | 110.928 | 110.928 | 110.929 | 110.93 | 110.93 | 110.931 | 110.932 | 116.114 | 116.114
0:00 | 101 | 101.162 | 101.162 | 101.162 | 101.163 | 101.163 | 101.163 | 101.164 | 101.164 | 120.161 | 120.161

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 23.919 | 25.587 | 25.588 | 25.589 | 25.591 | 25.593 | 25.594 | 25.596 | 25.597 | 25.601 | 25.601
1:00 | 24.284 | 25.926 | 25.928 | 25.929 | 25.93 | 25.932 | 25.933 | 25.934 | 25.936 | 25.939 | 25.94
1:30 | 23.029 | 24.672 | 24.673 | 24.674 | 24.675 | 24.677 | 24.678 | 24.679 | 24.68 | 24.683 | 24.683
2:00 | 29.661 | 31.291 | 31.292 | 31.293 | 31.294 | 31.295 | 31.296 | 31.298 | 31.299 | 31.302 | 31.302
2:30 | 29.021 | 30.655 | 30.655 | 30.656 | 30.657 | 30.659 | 30.659 | 30.66 | 30.661 | 30.664 | 30.664
3:00 | 19.803 | 21.389 | 21.39 | 21.391 | 21.392 | 21.393 | 21.394 | 21.395 | 21.396 | 21.398 | 21.398
3:30 | 27.332 | 28.931 | 28.931 | 28.932 | 28.932 | 28.933 | 28.933 | 28.934 | 28.934 | 28.936 | 28.936
4:00 | 25.768 | 27.366 | 27.366 | 27.367 | 27.367 | 27.368 | 27.368 | 27.369 | 27.369 | 27.37 | 27.37
4:30 | 26.191 | 27.811 | 27.811 | 27.812 | 27.812 | 27.813 | 27.813 | 27.814 | 27.814 | 27.816 | 27.816
5:00 | 24.264 | 25.856 | 25.856 | 25.857 | 25.857 | 25.858 | 25.858 | 25.859 | 25.86 | 25.861 | 25.861
5:30 | 22.807 | 24.368 | 24.368 | 24.369 | 24.37 | 24.37 | 24.371 | 24.371 | 24.372 | 24.374 | 24.374
6:00 | 23.928 | 25.499 | 25.499 | 25.498 | 25.498 | 25.498 | 25.498 | 25.497 | 25.498 | 25.497 | 25.498
6:30 | 29.596 | 31.216 | 31.213 | 31.21 | 31.208 | 31.205 | 31.203 | 31.201 | 31.199 | 31.196 | 31.195
7:00 | 47.8 | 47.886 | 47.874 | 47.866 | 47.857 | 47.849 | 47.842 | 47.834 | 47.825 | 47.814 | 47.81
7:30 | 56.015 | 56.085 | 56.062 | 56.048 | 56.033 | 56.019 | 56.006 | 55.993 | 55.977 | 55.959 | 55.95
8:00 | 68.98 | 69.03 | 68.99 | 68.966 | 68.94 | 68.916 | 68.895 | 68.872 | 68.845 | 68.813 | 68.796
8:30 | 79.001 | 79.025 | 78.968 | 78.932 | 78.893 | 78.857 | 78.824 | 78.789 | 78.748 | 78.695 | 78.671
9:00 | 74.845 | 74.85 | 74.779 | 74.734 | 74.687 | 74.641 | 74.601 | 74.557 | 74.506 | 74.441 | 74.409
9:30 | 74.92 | 74.912 | 74.832 | 74.782 | 74.729 | 74.679 | 74.632 | 74.583 | 74.525 | 74.453 | 74.415
10:00 | 82.281 | 82.252 | 82.157 | 82.098 | 82.036 | 81.976 | 81.92 | 81.862 | 81.791 | 81.706 | 81.659
10:30 | 79.256 | 79.219 | 79.122 | 79.061 | 79.002 | 78.944 | 78.889 | 78.832 | 78.762 | 78.685 | 78.635
11:00 | 85.619 | 85.57 | 85.465 | 85.4 | 85.337 | 85.274 | 85.215 | 85.154 | 85.079 | 84.997 | 84.942
11:30 | 76.349 | 76.302 | 76.202 | 76.141 | 76.084 | 76.029 | 75.975 | 75.92 | 75.85 | 75.783 | 75.729
12:00 | 81.039 | 80.988 | 80.886 | 80.824 | 80.767 | 80.71 | 80.656 | 80.6 | 80.529 | 80.462 | 80.407
12:30 | 85.442 | 85.387 | 85.283 | 85.219 | 85.161 | 85.103 | 85.047 | 84.989 | 84.917 | 84.848 | 84.792
13:00 | 79.941 | 79.89 | 79.789 | 79.728 | 79.67 | 79.614 | 79.56 | 79.504 | 79.434 | 79.367 | 79.313
13:30 | 84.609 | 84.56 | 84.461 | 84.402 | 84.348 | 84.295 | 84.243 | 84.19 | 84.123 | 84.061 | 84.008
14:00 | 87.777 | 87.733 | 87.639 | 87.582 | 87.531 | 87.481 | 87.431 | 87.381 | 87.317 | 87.259 | 87.208
14:30 | 83.455 | 83.426 | 83.344 | 83.294 | 83.25 | 83.207 | 83.163 | 83.12 | 83.064 | 83.016 | 82.971
15:00 | 89.679 | 89.638 | 89.55 | 89.498 | 89.451 | 89.404 | 89.358 | 89.312 | 89.252 | 89.2 | 89.153
15:30 | 80.688 | 80.654 | 80.578 | 80.532 | 80.491 | 80.45 | 80.41 | 80.369 | 80.318 | 80.271 | 80.23
16:00 | 87.287 | 87.265 | 87.201 | 87.162 | 87.127 | 87.093 | 87.059 | 87.025 | 86.981 | 86.941 | 86.907
16:30 | 86.065 | 86.051 | 85.997 | 85.966 | 85.939 | 85.913 | 85.886 | 85.86 | 85.825 | 85.798 | 85.77
17:00 | 79.785 | 79.78 | 79.743 | 79.722 | 79.704 | 79.688 | 79.67 | 79.653 | 79.63 | 79.616 | 79.596
17:30 | 62.689 | 62.688 | 62.665 | 62.652 | 62.642 | 62.632 | 62.621 | 62.611 | 62.598 | 62.591 | 62.578
18:00 | 50.99 | 51.006 | 50.998 | 50.995 | 50.994 | 50.994 | 50.992 | 50.991 | 50.989 | 50.995 | 50.991
18:30 | 37.935 | 38.676 | 38.674 | 38.673 | 38.675 | 38.677 | 38.677 | 38.678 | 38.679 | 38.686 | 38.684
19:00 | 28.279 | 29.898 | 29.9 | 29.902 | 29.907 | 29.911 | 29.914 | 29.918 | 29.922 | 29.932 | 29.932
19:30 | 32.701 | 34.206 | 34.209 | 34.212 | 34.218 | 34.224 | 34.228 | 34.233 | 34.238 | 34.252 | 34.252
20:00 | 32.42 | 33.889 | 33.892 | 33.895 | 33.901 | 33.906 | 33.91 | 33.915 | 33.92 | 33.932 | 33.933
20:30 | 29.055 | 30.717 | 30.72 | 30.723 | 30.729 | 30.734 | 30.738 | 30.743 | 30.748 | 30.76 | 30.761
21:00 | 29.011 | 30.756 | 30.76 | 30.763 | 30.769 | 30.774 | 30.778 | 30.783 | 30.788 | 30.801 | 30.801
21:30 | 27.532 | 29.241 | 29.244 | 29.246 | 29.25 | 29.254 | 29.257 | 29.261 | 29.264 | 29.274 | 29.274
22:00 | 25.355 | 27.118 | 27.119 | 27.121 | 27.123 | 27.126 | 27.128 | 27.13 | 27.132 | 27.138 | 27.138
22:30 | 33.23 | 35.076 | 35.078 | 35.079 | 35.082 | 35.084 | 35.086 | 35.088 | 35.09 | 35.096 | 35.096
23:00 | 32.551 | 34.35 | 34.351 | 34.353 | 34.356 | 34.359 | 34.361 | 34.363 | 34.366 | 34.372 | 34.373
23:30 | 28.496 | 30.324 | 30.326 | 30.327 | 30.33 | 30.332 | 30.334 | 30.336 | 30.338 | 30.344 | 30.344
0:00 | 23.39 | 25.006 | 25.007 | 25.008 | 25.009 | 25.01 | 25.011 | 25.012 | 25.013 | 25.016 | 25.016

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 136.17 | 117.29
2017-03-01 01:00 | 134.81 | 115.27
2017-03-01 01:30 | 126.5 | 107.42
2017-03-01 02:00 | 128.45 | 109.58
2017-03-01 02:30 | 128.02 | 108.14
2017-03-01 03:00 | 129.65 | 109.54
2017-03-01 03:30 | 130.51 | 111.43
2017-03-01 04:00 | 128.53 | 109.56
2017-03-01 04:30 | 123.34 | 104.68
2017-03-01 05:00 | 116.84 | 97.12
2017-03-01 05:30 | 112.87 | 93.36
2017-03-01 06:00 | 120.17 | 101.28
2017-03-01 06:30 | 105.76 | 85.07
2017-03-01 07:00 | 113.81 | 93.95
2017-03-01 07:30 | 122.85 | 102.88
2017-03-01 08:00 | 121.49 | 100.32
2017-03-01 08:30 | 123.43 | 102.49
2017-03-01 09:00 | 122.28 | 100.67
2017-03-01 09:30 | 120.23 | 98.96
2017-03-01 10:00 | 120.7 | 99.41
2017-03-01 10:30 | 115.15 | 92.83
2017-03-01 11:00 | 117.55 | 95.38
2017-03-01 11:30 | 116.73 | 94.47
2017-03-01 12:00 | 120.58 | 98.6
2017-03-01 12:30 | 117.02 | 96.65
2017-03-01 13:00 | 120.52 | 100.42
2017-03-01 13:30 | 116.92 | 96.51
2017-03-01 14:00 | 115.34 | 96.82
2017-03-01 14:30 | 115.72 | 95.39
2017-03-01 15:00 | 122.25 | 100.42
2017-03-01 15:30 | 122.12 | 100.63
2017-03-01 16:00 | 123.75 | 102.42
2017-03-01 16:30 | 128.26 | 108.9
2017-03-01 17:00 | 116.86 | 99.69
2017-03-01 17:30 | 110.5 | 93.9
2017-03-01 18:00 | 110.08 | 94.36
2017-03-01 18:30 | 107.92 | 90.49
2017-03-01 19:00 | 118.35 | 101.77
2017-03-01 19:30 | 121.7 | 103.75
2017-03-01 20:00 | 117.14 | 100.35
2017-03-01 20:30 | 116.59 | 99.13
2017-03-01 21:00 | 108.01 | 91.29
2017-03-01 21:30 | 107.8 | 91.56
2017-03-01 22:00 | 104.09 | 90.24
2017-03-01 22:30 | 99.18 | 85.81
2017-03-01 23:00 | 96.31 | 83.47
2017-03-01 23:30 | 95.52 | 82.2
2017-03-02 | 99.55 | 86.11
2017-03-02 00:30 | 106.9 | 92.48
2017-03-02 01:00 | 104.34 | 90.64
2017-03-02 01:30 | 104.19 | 91.91
2017-03-02 02:00 | 99.59 | 85.58
2017-03-02 02:30 | 107.59 | 93.44
2017-03-02 03:00 | 103.85 | 88.52
2017-03-02 03:30 | 101.92 | 88.88
2017-03-02 04:00 | 99.46 | 87.19
2017-03-02 04:30 | 100.23 | 88.18
2017-03-02 05:00 | 95.5 | 82.61
2017-03-02 05:30 | 93.52 | 80.28
2017-03-02 06:00 | 99.37 | 86.88
2017-03-02 06:30 | 86.32 | 72.96
2017-03-02 07:00 | 90.83 | 77.99
2017-03-02 07:30 | 92.56 | 78.33
2017-03-02 08:00 | 94.46 | 78.77
2017-03-02 08:30 | 96.19 | 81.07
2017-03-02 09:00 | 93.18 | 77.86
2017-03-02 09:30 | 88.39 | 73.57
2017-03-02 10:00 | 89.74 | 76.15
2017-03-02 10:30 | 94.31 | 79.87
2017-03-02 11:00 | 95.09 | 80.91
2017-03-02 11:30 | 90.86 | 77.42
2017-03-02 12:00 | 93.47 | 79.47
2017-03-02 12:30 | 95.44 | 81.49
2017-03-02 13:00 | 98.41 | 85.4
2017-03-02 13:30 | 101.3 | 88.97
2017-03-02 14:00 | 108.89 | 95.71
2017-03-02 14:30 | 108.24 | 93.36
2017-03-02 15:00 | 101.32 | 85.26
2017-03-02 15:30 | 105.48 | 88.44
2017-03-02 16:00 | 106.74 | 90.07
2017-03-02 16:30 | 106.8 | 90.99
2017-03-02 17:00 | 113.7 | 97.26
2017-03-02 17:30 | 111.83 | 96.18
2017-03-02 18:00 | 120.15 | 104.21
2017-03-02 18:30 | 116.8 | 97.7
2017-03-02 19:00 | 122.92 | 104.16
2017-03-02 19:30 | 134.63 | 115.8
2017-03-02 20:00 | 129.43 | 109.38
2017-03-02 20:30 | 132.6 | 112.51
2017-03-02 21:00 | 128.56 | 109.87
2017-03-02 21:30 | 128.66 | 110.76
2017-03-02 22:00 | 121.4 | 103.49
2017-03-02 22:30 | 120.72 | 103.21
2017-03-02 23:00 | 119.32 | 102.07
2017-03-02 23:30 | 122.26 | 105.41
2017-03-03 | 123.09 | 105.79
2017-03-03 00:30 | 118.31 | 100.5
2017-03-03 01:00 | 121.35 | 104.91
2017-03-03 01:30 | 115.33 | 98.62
2017-03-03 02:00 | 110.9 | 96.37
2017-03-03 02:30 | 108.14 | 95.54
2017-03-03 03:00 | 113 | 99.29
2017-03-03 03:30 | 115.26 | 101.58
2017-03-03 04:00 | 117.98 | 103.93
2017-03-03 04:30 | 116.89 | 101.76
2017-03-03 05:00 | 109.31 | 94.47
2017-03-03 05:30 | 106.91 | 91.69
2017-03-03 06:00 | 117.41 | 102.48
2017-03-03 06:30 | 108.8 | 91.45
2017-03-03 07:00 | 109.74 | 93.34
2017-03-03 07:30 | 118.26 | 101.68
2017-03-03 08:00 | 114.79 | 97.8
2017-03-03 08:30 | 117.04 | 100.31
2017-03-03 09:00 | 117.85 | 101.96
2017-03-03 09:30 | 126.24 | 108.86
2017-03-03 10:00 | 120.04 | 102.6
2017-03-03 10:30 | 125.05 | 106.9
2017-03-03 11:00 | 116.7 | 98.01
2017-03-03 11:30 | 118.93 | 101.16
2017-03-03 12:00 | 120.96 | 106.5
2017-03-03 12:30 | 123.44 | 108.29
2017-03-03 13:00 | 129.28 | 112.86
2017-03-03 13:30 | 136.88 | 117.52
2017-03-03 14:00 | 136.5 | 117.28
2017-03-03 14:30 | 133.04 | 114.03
2017-03-03 15:00 | 138.29 | 119.16
2017-03-03 15:30 | 139.42 | 121.92
2017-03-03 16:00 | 133.58 | 115.92
2017-03-03 16:30 | 128.91 | 110.37
2017-03-03 17:00 | 126.22 | 106.21
2017-03-03 17:30 | 127.92 | 108.85
2017-03-03 18:00 | 129.17 | 111.53
2017-03-03 18:30 | 124.09 | 103.52
2017-03-03 19:00 | 127.81 | 110.2
2017-03-03 19:30 | 131.72 | 115.37
2017-03-03 20:00 | 126.42 | 110.1
2017-03-03 20:30 | 123.4 | 105.29
2017-03-03 21:00 | 120.67 | 101.48
2017-03-03 21:30 | 118.19 | 100.6
2017-03-03 22:00 | 118.43 | 101.64
2017-03-03 22:30 | 122.3 | 104.67
2017-03-03 23:00 | 122.4 | 104.66
2017-03-03 23:30 | 117.82 | 99.99
2017-03-04 | 111.28 | 94.07
2017-03-04 00:30 | 105.18 | 88.64
2017-03-04 01:00 | 107.79 | 91.89
2017-03-04 01:30 | 105.63 | 89.15
2017-03-04 02:00 | 103.07 | 88.17
2017-03-04 02:30 | 105.75 | 90.08
2017-03-04 03:00 | 108.97 | 93.05
2017-03-04 03:30 | 106.93 | 91.18
2017-03-04 04:00 | 107.53 | 91.54
2017-03-04 04:30 | 112.88 | 97.14
2017-03-04 05:00 | 117.16 | 101.91
2017-03-04 05:30 | 113.95 | 98.43
2017-03-04 06:00 | 110.17 | 95.49
2017-03-04 06:30 | 100.21 | 84
2017-03-04 07:00 | 101.71 | 85.76
2017-03-04 07:30 | 110.65 | 95.76
2017-03-04 08:00 | 105.21 | 90.84
2017-03-04 08:30 | 110.13 | 94.88
2017-03-04 09:00 | 104.22 | 86.82
2017-03-04 09:30 | 109.66 | 92.42
2017-03-04 10:00 | 108 | 90.99
2017-03-04 10:30 | 107.29 | 89.04
2017-03-04 11:00 | 108.84 | 91.29
2017-03-04 11:30 | 107.16 | 89.33
2017-03-04 12:00 | 116.43 | 99.08
2017-03-04 12:30 | 113.95 | 96.64
2017-03-04 13:00 | 116.22 | 99.51
2017-03-04 13:30 | 127.23 | 109.92
2017-03-04 14:00 | 117.22 | 99.97
2017-03-04 14:30 | 112.48 | 93.92
2017-03-04 15:00 | 119.82 | 100.85
2017-03-04 15:30 | 118.83 | 99.67
2017-03-04 16:00 | 118.56 | 100.2
2017-03-04 16:30 | 119.95 | 101.41
2017-03-04 17:00 | 118.58 | 100.19
2017-03-04 17:30 | 119.16 | 101.14
2017-03-04 18:00 | 116.35 | 98.67
2017-03-04 18:30 | 112.66 | 93.82
2017-03-04 19:00 | 117.2 | 101.47
2017-03-04 19:30 | 119.2 | 101.74
2017-03-04 20:00 | 120.5 | 102.1
2017-03-04 20:30 | 122.18 | 103.82
2017-03-04 21:00 | 117.77 | 100.87
2017-03-04 21:30 | 115 | 99.27
2017-03-04 22:00 | 114.64 | 98.37
2017-03-04 22:30 | 116.51 | 98.68
2017-03-04 23:00 | 120.98 | 103.44
2017-03-04 23:30 | 120.54 | 103.78
2017-03-05 | 121.54 | 105.35
2017-03-05 00:30 | 117.11 | 100.57
2017-03-05 01:00 | 108.8 | 93.51
2017-03-05 01:30 | 109.05 | 93.94
2017-03-05 02:00 | 109.47 | 93.9
2017-03-05 02:30 | 112.53 | 95.27
2017-03-05 03:00 | 121.59 | 105
2017-03-05 03:30 | 123.13 | 106.15
2017-03-05 04:00 | 118.07 | 101.67
2017-03-05 04:30 | 113.86 | 96.97
2017-03-05 05:00 | 115.92 | 98.29
2017-03-05 05:30 | 119 | 100.35
2017-03-05 06:00 | 116.78 | 99.18
2017-03-05 06:30 | 113.1 | 94.33
2017-03-05 07:00 | 122.47 | 104.03
2017-03-05 07:30 | 117.76 | 100.24
2017-03-05 08:00 | 111.96 | 93.18
2017-03-05 08:30 | 108.83 | 91.38
2017-03-05 09:00 | 107.76 | 90.46
2017-03-05 09:30 | 110.71 | 92.72
2017-03-05 10:00 | 115.83 | 98.11
2017-03-05 10:30 | 117.5 | 99.41
2017-03-05 11:00 | 118.16 | 100.48
2017-03-05 11:30 | 115.4 | 96.79
2017-03-05 12:00 | 113.84 | 94.75
2017-03-05 12:30 | 116.27 | 98.09
2017-03-05 13:00 | 123.58 | 103.64
2017-03-05 13:30 | 131.89 | 112.19
2017-03-05 14:00 | 124.65 | 104.73
2017-03-05 14:30 | 127.07 | 107.32
2017-03-05 15:00 | 121.59 | 103.2
2017-03-05 15:30 | 124.1 | 106.39
2017-03-05 16:00 | 121.05 | 103.22
2017-03-05 16:30 | 120.21 | 101.7
2017-03-05 17:00 | 119.54 | 100.91
2017-03-05 17:30 | 123.45 | 105
2017-03-05 18:00 | 126.94 | 109.78
2017-03-05 18:30 | 113.58 | 95.02
2017-03-05 19:00 | 114.31 | 96.11
2017-03-05 19:30 | 117.58 | 99.3
2017-03-05 20:00 | 124.11 | 104.38
2017-03-05 20:30 | 119.57 | 101.04
2017-03-05 21:00 | 114.54 | 96.52
2017-03-05 21:30 | 112.87 | 95.46
2017-03-05 22:00 | 118.78 | 100.62
2017-03-05 22:30 | 108.69 | 89.33
2017-03-05 23:00 | 112.91 | 95.35
2017-03-05 23:30 | 107.74 | 91.83
2017-03-06 | 108.98 | 92.67
2017-03-06 00:30 | 110.91 | 93.22
2017-03-06 01:00 | 111.27 | 94.88
2017-03-06 01:30 | 109.74 | 93.38
2017-03-06 02:00 | 114.71 | 98.23
2017-03-06 02:30 | 109.75 | 92.51
2017-03-06 03:00 | 112.01 | 93.78
2017-03-06 03:30 | 115.28 | 96.63
2017-03-06 04:00 | 112.08 | 93.92
2017-03-06 04:30 | 111.6 | 93.74
2017-03-06 05:00 | 113.92 | 95.71
2017-03-06 05:30 | 117.05 | 102.22
2017-03-06 06:00 | 114.04 | 97.52
2017-03-06 06:30 | 107.52 | 89.78
2017-03-06 07:00 | 107.3 | 90.42
2017-03-06 07:30 | 105.03 | 87.43
2017-03-06 08:00 | 112.21 | 95.36
2017-03-06 08:30 | 113.67 | 96.17
2017-03-06 09:00 | 113.89 | 96.62
2017-03-06 09:30 | 107.63 | 91.63
2017-03-06 10:00 | 99.52 | 84.71
2017-03-06 10:30 | 104.09 | 88.42
2017-03-06 11:00 | 106.83 | 90.59
2017-03-06 11:30 | 107.98 | 91.32
2017-03-06 12:00 | 118.55 | 102.93
2017-03-06 12:30 | 127.62 | 111.5
2017-03-06 13:00 | 123.41 | 107.43
2017-03-06 13:30 | 112.4 | 94.33
2017-03-06 14:00 | 110.49 | 92.39
2017-03-06 14:30 | 112.48 | 92.37
2017-03-06 15:00 | 118.66 | 97
2017-03-06 15:30 | 121.06 | 99.31
2017-03-06 16:00 | 121.03 | 99.67
2017-03-06 16:30 | 127.8 | 105.33
2017-03-06 17:00 | 130.84 | 110.16
2017-03-06 17:30 | 128.98 | 109.28
2017-03-06 18:00 | 125.93 | 106.39
2017-03-06 18:30 | 124.81 | 102.46
2017-03-06 19:00 | 126.95 | 105.43
2017-03-06 19:30 | 138.66 | 116.05
2017-03-06 20:00 | 133.48 | 110.24
2017-03-06 20:30 | 132.1 | 110.17
2017-03-06 21:00 | 128.87 | 107.91
2017-03-06 21:30 | 122.65 | 102.13
2017-03-06 22:00 | 118.63 | 98.24
2017-03-06 22:30 | 124.4 | 105.3
2017-03-06 23:00 | 121.07 | 101.27
2017-03-06 23:30 | 115.43 | 94.21
2017-03-07 | 118.57 | 97.44
2017-03-07 00:30 | 115.53 | 96.1
2017-03-07 01:00 | 114.17 | 94.84
2017-03-07 01:30 | 112.71 | 91.58
2017-03-07 02:00 | 119.14 | 97
2017-03-07 02:30 | 125.93 | 105.15
2017-03-07 03:00 | 121.97 | 100.89
2017-03-07 03:30 | 123.19 | 102.47
2017-03-07 04:00 | 115.85 | 94.24
2017-03-07 04:30 | 118.56 | 97
2017-03-07 05:00 | 114.37 | 92.89
2017-03-07 05:30 | 121.7 | 101.17
2017-03-07 06:00 | 124.22 | 103.96
2017-03-07 06:30 | 107.14 | 85.81
2017-03-07 07:00 | 115.95 | 98.25
2017-03-07 07:30 | 114.03 | 96.27
2017-03-07 08:00 | 122.76 | 104.03
2017-03-07 08:30 | 111.3 | 92.93
2017-03-07 09:00 | 120.28 | 102.16
2017-03-07 09:30 | 120.61 | 102.27
2017-03-07 10:00 | 120.11 | 102.46
2017-03-07 10:30 | 121.85 | 102.47
2017-03-07 11:00 | 119.96 | 101.17
2017-03-07 11:30 | 121.21 | 102.53
2017-03-07 12:00 | 124.22 | 106.43
2017-03-07 12:30 | 129.99 | 114.52
2017-03-07 13:00 | 131.87 | 117.14
2017-03-07 13:30 | 129.99 | 113.98
2017-03-07 14:00 | 126.46 | 108.82
2017-03-07 14:30 | 127.47 | 110.27
2017-03-07 15:00 | 124.19 | 108.32
2017-03-07 15:30 | 127.69 | 111.31
2017-03-07 16:00 | 133.41 | 116.99
2017-03-07 16:30 | 130.56 | 114.55
2017-03-07 17:00 | 127.73 | 111.49
2017-03-07 17:30 | 127.74 | 112.62
2017-03-07 18:00 | 126.63 | 111.65
2017-03-07 18:30 | 115.64 | 98.99
2017-03-07 19:00 | 133.32 | 117.98
2017-03-07 19:30 | 133.13 | 116.4
2017-03-07 20:00 | 133.53 | 116.12
2017-03-07 20:30 | 131.79 | 115.21
2017-03-07 21:00 | 125.32 | 109.3
2017-03-07 21:30 | 119.56 | 103.56
2017-03-07 22:00 | 125.78 | 109.82
2017-03-07 22:30 | 122.13 | 107.47
2017-03-07 23:00 | 119.27 | 104.59
2017-03-07 23:30 | 112.73 | 96.97
2017-03-08 | 112.83 | 97.51
2017-03-08 00:30 | 116.56 | 102.05
2017-03-08 01:00 | 120.99 | 106.66
2017-03-08 01:30 | 109.95 | 95.94
2017-03-08 02:00 | 113.32 | 99.39
2017-03-08 02:30 | 113.08 | 98.64
2017-03-08 03:00 | 107.87 | 93.28
2017-03-08 03:30 | 112.28 | 97.94
2017-03-08 04:00 | 114.88 | 101.28
2017-03-08 04:30 | 112.74 | 97.95
2017-03-08 05:00 | 110.37 | 95.96
2017-03-08 05:30 | 113.55 | 99.46
2017-03-08 06:00 | 117.17 | 102.89
2017-03-08 06:30 | 102.8 | 86.65
2017-03-08 07:00 | 114.06 | 99.38
2017-03-08 07:30 | 115.53 | 101.56
2017-03-08 08:00 | 114.78 | 100.93
2017-03-08 08:30 | 112.36 | 97.71
2017-03-08 09:00 | 114.52 | 99.08
2017-03-08 09:30 | 113.36 | 97.1
2017-03-08 10:00 | 105.81 | 89.68
2017-03-08 10:30 | 106.33 | 90.3
2017-03-08 11:00 | 113.48 | 97.31
2017-03-08 11:30 | 107.9 | 91.07
2017-03-08 12:00 | 114.14 | 97.23
2017-03-08 12:30 | 113.32 | 96.74
2017-03-08 13:00 | 117.54 | 102.08
2017-03-08 13:30 | 116.89 | 102.68
2017-03-08 14:00 | 110.86 | 97.7
2017-03-08 14:30 | 106.03 | 92.22
2017-03-08 15:00 | 102.83 | 87.58
2017-03-08 15:30 | 108.2 | 92.59
2017-03-08 16:00 | 111.11 | 97.39
2017-03-08 16:30 | 110.28 | 95.17
2017-03-08 17:00 | 117.36 | 102.16
2017-03-08 17:30 | 117.28 | 101.74
2017-03-08 18:00 | 114.76 | 100.26
2017-03-08 18:30 | 115.61 | 99.69
2017-03-08 19:00 | 123.83 | 107.21
2017-03-08 19:30 | 117.73 | 100.98
2017-03-08 20:00 | 118.31 | 101.49
2017-03-08 20:30 | 114.83 | 98.71
2017-03-08 21:00 | 111.72 | 96.23
2017-03-08 21:30 | 107.87 | 93.41
2017-03-08 22:00 | 116 | 101.92
2017-03-08 22:30 | 102.5 | 88.13
2017-03-08 23:00 | 103.1 | 88.76
2017-03-08 23:30 | 103.29 | 88.79
2017-03-09 | 97.68 | 83.87
2017-03-09 00:30 | 102.41 | 87.94
2017-03-09 01:00 | 101.35 | 86.15
2017-03-09 01:30 | 100.37 | 85.6
2017-03-09 02:00 | 100.97 | 87.21
2017-03-09 02:30 | 106.16 | 91.84
2017-03-09 03:00 | 101.93 | 87.34
2017-03-09 03:30 | 109.49 | 95.48
2017-03-09 04:00 | 112.64 | 98.81
2017-03-09 04:30 | 105.81 | 91.51
2017-03-09 05:00 | 107.67 | 93.15
2017-03-09 05:30 | 107.56 | 90.39
2017-03-09 06:00 | 103.85 | 87.07
2017-03-09 06:30 | 104.51 | 86.2
2017-03-09 07:00 | 101.84 | 84.88
2017-03-09 07:30 | 107.39 | 91.34
2017-03-09 08:00 | 102.15 | 85.59
2017-03-09 08:30 | 96.35 | 80.63
2017-03-09 09:00 | 95.24 | 80.38
2017-03-09 09:30 | 103.39 | 89.13
2017-03-09 10:00 | 102.21 | 87.59
2017-03-09 10:30 | 98.19 | 84.02
2017-03-09 11:00 | 93.66 | 79.92
2017-03-09 11:30 | 104.71 | 90.71
2017-03-09 12:00 | 102.73 | 88.49
2017-03-09 12:30 | 106.99 | 92.76
2017-03-09 13:00 | 107.8 | 91.42
2017-03-09 13:30 | 107.85 | 92.86
2017-03-09 14:00 | 106.41 | 90.37
2017-03-09 14:30 | 112.84 | 96.56
2017-03-09 15:00 | 109.47 | 93.65
2017-03-09 15:30 | 111.99 | 95.52
2017-03-09 16:00 | 113.07 | 96.6
2017-03-09 16:30 | 114.03 | 98.91
2017-03-09 17:00 | 115.03 | 100.17
2017-03-09 17:30 | 121.64 | 106.23
2017-03-09 18:00 | 114.66 | 99.78
2017-03-09 18:30 | 111.03 | 95.3
2017-03-09 19:00 | 117.05 | 101.24
2017-03-09 19:30 | 124.95 | 109.75
2017-03-09 20:00 | 124.78 | 108.71
2017-03-09 20:30 | 115.28 | 97.89
2017-03-09 21:00 | 112.04 | 94.19
2017-03-09 21:30 | 112.25 | 95.86
2017-03-09 22:00 | 114.53 | 98.79
2017-03-09 22:30 | 111.91 | 97.45
2017-03-09 23:00 | 111.87 | 98.82
2017-03-09 23:30 | 116.53 | 103.06
2017-03-10 | 119.97 | 107.06
2017-03-10 00:30 | 113.88 | 101.17
2017-03-10 01:00 | 110.23 | 97.4
2017-03-10 01:30 | 114.58 | 101.51
2017-03-10 02:00 | 116.94 | 103.95
2017-03-10 02:30 | 121.07 | 106.45
2017-03-10 03:00 | 115.3 | 99.85
2017-03-10 03:30 | 117.44 | 102.08
2017-03-10 04:00 | 115.42 | 100.1
2017-03-10 04:30 | 115.87 | 100.72
2017-03-10 05:00 | 112.76 | 97.82
2017-03-10 05:30 | 112.9 | 98.59
2017-03-10 06:00 | 112.73 | 98.78
2017-03-10 06:30 | 113.17 | 98.73
2017-03-10 07:00 | 114.66 | 100.42
2017-03-10 07:30 | 118.42 | 103.93
2017-03-10 08:00 | 119.45 | 104.57
2017-03-10 08:30 | 122.13 | 106.93
2017-03-10 09:00 | 117.79 | 103.78
2017-03-10 09:30 | 115.69 | 100.7
2017-03-10 10:00 | 104.31 | 91.25
2017-03-10 10:30 | 105.75 | 92.17
2017-03-10 11:00 | 100.98 | 86.67
2017-03-10 11:30 | 110.16 | 95.95
2017-03-10 12:00 | 110.02 | 96.25
2017-03-10 12:30 | 107.97 | 94.45
2017-03-10 13:00 | 114.19 | 100.87
2017-03-10 13:30 | 121.59 | 109.86
2017-03-10 14:00 | 112.54 | 99.66
2017-03-10 14:30 | 119.23 | 103.72
2017-03-10 15:00 | 111.13 | 96.8
2017-03-10 15:30 | 119.08 | 105.03
2017-03-10 16:00 | 126.91 | 112.66
2017-03-10 16:30 | 119.11 | 104.45
2017-03-10 17:00 | 120.36 | 107.15
2017-03-10 17:30 | 129.89 | 116.51
2017-03-10 18:00 | 120.84 | 107.09
2017-03-10 18:30 | 110.02 | 95.06
2017-03-10 19:00 | 114.65 | 99.28
2017-03-10 19:30 | 119.1 | 103.81
2017-03-10 20:00 | 119.95 | 104.05
2017-03-10 20:30 | 116.02 | 98.9
2017-03-10 21:00 | 109.26 | 92.15
2017-03-10 21:30 | 111.17 | 94.21
2017-03-10 22:00 | 115.75 | 99.98
2017-03-10 22:30 | 120.09 | 105.28
2017-03-10 23:00 | 116.31 | 101.8
2017-03-10 23:30 | 108.15 | 93.63
2017-03-11 | 113.32 | 99.19
2017-03-11 00:30 | 107.38 | 93
2017-03-11 01:00 | 110.38 | 96.11
2017-03-11 01:30 | 108.96 | 94.52
2017-03-11 02:00 | 111.37 | 97.33
2017-03-11 02:30 | 114.14 | 98.52
2017-03-11 03:00 | 117.21 | 101.32
2017-03-11 03:30 | 120.38 | 103.29
2017-03-11 04:00 | 123.39 | 107.73
2017-03-11 04:30 | 122.36 | 107.29
2017-03-11 05:00 | 117.54 | 102.48
2017-03-11 05:30 | 118.01 | 103.17
2017-03-11 06:00 | 114.28 | 99.75
2017-03-11 06:30 | 100.87 | 85.18
2017-03-11 07:00 | 105.83 | 91.01
2017-03-11 07:30 | 112.34 | 97.82
2017-03-11 08:00 | 114.94 | 100.32
2017-03-11 08:30 | 113.22 | 97.5
2017-03-11 09:00 | 113.82 | 99.61
2017-03-11 09:30 | 118.82 | 103.91
2017-03-11 10:00 | 114.27 | 98.46
2017-03-11 10:30 | 108.75 | 92.03
2017-03-11 11:00 | 113.62 | 97.92
2017-03-11 11:30 | 113.99 | 98.26
2017-03-11 12:00 | 123.62 | 107.36
2017-03-11 12:30 | 128.71 | 111.11
2017-03-11 13:00 | 129.88 | 112.66
2017-03-11 13:30 | 128.11 | 112.58
2017-03-11 14:00 | 120.61 | 106.51
2017-03-11 14:30 | 127.23 | 113.29
2017-03-11 15:00 | 125.24 | 110.63
2017-03-11 15:30 | 121.69 | 107.18
2017-03-11 16:00 | 129.14 | 114.28
2017-03-11 16:30 | 121.19 | 106.14
2017-03-11 17:00 | 121.84 | 106.94
2017-03-11 17:30 | 119.03 | 105.13
2017-03-11 18:00 | 121.14 | 106.57
2017-03-11 18:30 | 112.85 | 97
2017-03-11 19:00 | 111.22 | 96.16
2017-03-11 19:30 | 118.37 | 101.04
2017-03-11 20:00 | 120.64 | 103.62
2017-03-11 20:30 | 124.85 | 109.22
2017-03-11 21:00 | 122.12 | 107.99
2017-03-11 21:30 | 126.05 | 110.11
2017-03-11 22:00 | 125.03 | 109.8
2017-03-11 22:30 | 124.63 | 109.91
2017-03-11 23:00 | 125.99 | 111.75
2017-03-11 23:30 | 124.68 | 111.28
2017-03-12 | 118.83 | 105.11
2017-03-12 00:30 | 124.52 | 110.2
2017-03-12 01:00 | 117.68 | 104.19
2017-03-12 01:30 | 114.56 | 100.03
2017-03-12 02:00 | 115.98 | 101.51
2017-03-12 02:30 | 121.59 | 106.59
2017-03-12 03:00 | 122.34 | 106.98
2017-03-12 03:30 | 117.99 | 102.84
2017-03-12 04:00 | 117.46 | 103.75
2017-03-12 04:30 | 122.24 | 108.12
2017-03-12 05:00 | 115.11 | 101.47
2017-03-12 05:30 | 106.98 | 93.52
2017-03-12 06:00 | 121.83 | 109.33
2017-03-12 06:30 | 102.08 | 87.91
2017-03-12 07:00 | 104.34 | 91.55
2017-03-12 07:30 | 109.24 | 95.8
2017-03-12 08:00 | 110.11 | 95.79
2017-03-12 08:30 | 117.72 | 103.73
2017-03-12 09:00 | 111.32 | 97.12
2017-03-12 09:30 | 106.81 | 91.89
2017-03-12 10:00 | 101.23 | 89.04
2017-03-12 10:30 | 102.92 | 90.16
2017-03-12 11:00 | 100.75 | 87.99
2017-03-12 11:30 | 94.26 | 80.1
2017-03-12 12:00 | 99.86 | 86.32
2017-03-12 12:30 | 103.7 | 90.06
2017-03-12 13:00 | 111.53 | 97.74
2017-03-12 13:30 | 111.07 | 96
2017-03-12 14:00 | 121.81 | 107.36
2017-03-12 14:30 | 117.07 | 103.17
2017-03-12 15:00 | 120.52 | 106.08
2017-03-12 15:30 | 119.48 | 104.18
2017-03-12 16:00 | 121.48 | 108.08
2017-03-12 16:30 | 121.06 | 107
2017-03-12 17:00 | 128.44 | 114.12
2017-03-12 17:30 | 124.12 | 110.39
2017-03-12 18:00 | 126.25 | 112.21
2017-03-12 18:30 | 119.02 | 102.93
2017-03-12 19:00 | 117.13 | 102.4
2017-03-12 19:30 | 126.29 | 112.08
2017-03-12 20:00 | 122.66 | 107.01
2017-03-12 20:30 | 120.68 | 103.56
2017-03-12 21:00 | 120.29 | 103.37
2017-03-12 21:30 | 116.94 | 99.06
2017-03-12 22:00 | 118.33 | 100.29
2017-03-12 22:30 | 123.26 | 106.66
2017-03-12 23:00 | 125.19 | 108.12
2017-03-12 23:30 | 122.77 | 107.15
2017-03-13 | 125.23 | 110.03
2017-03-13 00:30 | 121.5 | 106.51
2017-03-13 01:00 | 120.49 | 104.83
2017-03-13 01:30 | 114.12 | 99.18
2017-03-13 02:00 | 118.48 | 103.19
2017-03-13 02:30 | 119.78 | 104.19
2017-03-13 03:00 | 120.85 | 105.8
2017-03-13 03:30 | 122.34 | 107.11
2017-03-13 04:00 | 123.71 | 109.26
2017-03-13 04:30 | 117.52 | 103.44
2017-03-13 05:00 | 108.37 | 94.12
2017-03-13 05:30 | 98.42 | 88.41
2017-03-13 06:00 | 100.52 | 92.13
2017-03-13 06:30 | 98.19 | 88.28
2017-03-13 07:00 | 103.84 | 93.9
2017-03-13 07:30 | 112.2 | 101.16
2017-03-13 08:00 | 105.51 | 94.49
2017-03-13 08:30 | 112.41 | 102.28
2017-03-13 09:00 | 111.76 | 101.02
2017-03-13 09:30 | 107.29 | 97.63
2017-03-13 10:00 | 110.72 | 99.85
2017-03-13 10:30 | 112.65 | 101.4
2017-03-13 11:00 | 109.16 | 97.73
2017-03-13 11:30 | 112.95 | 101.86
2017-03-13 12:00 | 115.08 | 103.88
2017-03-13 12:30 | 115.51 | 103.61
2017-03-13 13:00 | 114.43 | 102.32
2017-03-13 13:30 | 114.58 | 100.92
2017-03-13 14:00 | 117.48 | 103.86
2017-03-13 14:30 | 118.08 | 103.94
2017-03-13 15:00 | 123.35 | 106.85
2017-03-13 15:30 | 123.78 | 108.42
2017-03-13 16:00 | 129.56 | 114.93
2017-03-13 16:30 | 128.61 | 114.3
2017-03-13 17:00 | 128.58 | 114.27
2017-03-13 17:30 | 115.02 | 100.31
2017-03-13 18:00 | 120.36 | 106.93
2017-03-13 18:30 | 114.48 | 99.8
2017-03-13 19:00 | 118.36 | 103.58
2017-03-13 19:30 | 125.73 | 111.71
2017-03-13 20:00 | 124.49 | 110.13
2017-03-13 20:30 | 117.64 | 104.16
2017-03-13 21:00 | 117.44 | 104.85
2017-03-13 21:30 | 111.67 | 100.78
2017-03-13 22:00 | 117.61 | 107
2017-03-13 22:30 | 109.09 | 99.21
2017-03-13 23:00 | 98.64 | 88.07
2017-03-13 23:30 | 100.32 | 91.72
2017-03-14 | 103.22 | 94.7
2017-03-14 00:30 | 101.66 | 93.49
2017-03-14 01:00 | 100.4 | 90.84
2017-03-14 01:30 | 101.38 | 91.15
2017-03-14 02:00 | 101.41 | 91.67
2017-03-14 02:30 | 102.77 | 93.23
2017-03-14 03:00 | 97.34 | 86.37
2017-03-14 03:30 | 96.73 | 84.22
2017-03-14 04:00 | 96.13 | 83.75
2017-03-14 04:30 | 99.23 | 86.81
2017-03-14 05:00 | 99.59 | 88.46
2017-03-14 05:30 | 95.26 | 84.44
2017-03-14 06:00 | 94.63 | 84.86
2017-03-14 06:30 | 88.58 | 79.27
2017-03-14 07:00 | 94.18 | 85.86
2017-03-14 07:30 | 94.36 | 86.06
2017-03-14 08:00 | 92.36 | 82.74
2017-03-14 08:30 | 94.05 | 84.66
2017-03-14 09:00 | 90.98 | 81.99
2017-03-14 09:30 | 92.09 | 83.07
2017-03-14 10:00 | 90.83 | 81.09
2017-03-14 10:30 | 101.74 | 91.38
2017-03-14 11:00 | 98.96 | 87.6
2017-03-14 11:30 | 102.21 | 90.83
2017-03-14 12:00 | 108.12 | 97.53
2017-03-14 12:30 | 108.64 | 98.01
2017-03-14 13:00 | 108.17 | 96.84
2017-03-14 13:30 | 113.48 | 101.81
2017-03-14 14:00 | 114.04 | 102.37
2017-03-14 14:30 | 110.56 | 99.03
2017-03-14 15:00 | 112.28 | 101.12
2017-03-14 15:30 | 111.9 | 101.01
2017-03-14 16:00 | 117.28 | 105.92
2017-03-14 16:30 | 115.34 | 105
2017-03-14 17:00 | 111.22 | 101.26
2017-03-14 17:30 | 104.85 | 96.64
2017-03-14 18:00 | 117.23 | 101.87
2017-03-14 18:30 | 110.69 | 93.83
2017-03-14 19:00 | 118.61 | 102.37
2017-03-14 19:30 | 91.72 | 75.92
2017-03-14 20:00 | 90.88 | 74.56
2017-03-14 20:30 | 97.91 | 82.69
2017-03-14 21:00 | 101.3 | 87.95
2017-03-14 21:30 | 99.62 | 86.83
2017-03-14 22:00 | 100.7 | 88.16
2017-03-14 22:30 | 94.98 | 82.07
2017-03-14 23:00 | 102.81 | 90.38
2017-03-14 23:30 | 98.4 | 85.76
2017-03-15 | 95.56 | 81.22
2017-03-15 00:30 | 95.07 | 81.22
2017-03-15 01:00 | 92.38 | 78.16
2017-03-15 01:30 | 93.17 | 79.91
2017-03-15 02:00 | 102.54 | 90.22
2017-03-15 02:30 | 105.52 | 93.87
2017-03-15 03:00 | 103.64 | 91.28
2017-03-15 03:30 | 100.41 | 86.92
2017-03-15 04:00 | 94.96 | 80.81
2017-03-15 04:30 | 96.06 | 81.3
2017-03-15 05:00 | 97.62 | 83.93
2017-03-15 05:30 | 97.74 | 84.11
2017-03-15 06:00 | 100.85 | 87.87
2017-03-15 06:30 | 90.77 | 75.38
2017-03-15 07:00 | 97.62 | 83.6
2017-03-15 07:30 | 102.84 | 90.71
2017-03-15 08:00 | 100.16 | 87.36
2017-03-15 08:30 | 96.29 | 82.22
2017-03-15 09:00 | 101.08 | 88.06
2017-03-15 09:30 | 92.9 | 78.67
2017-03-15 10:00 | 94.32 | 80.61
2017-03-15 10:30 | 90.04 | 76.23
2017-03-15 11:00 | 93.57 | 79.22
2017-03-15 11:30 | 93.65 | 79.53
2017-03-15 12:00 | 100.09 | 86.03
2017-03-15 12:30 | 102.11 | 88.52
2017-03-15 13:00 | 99.14 | 85.41
2017-03-15 13:30 | 100.34 | 86.53
2017-03-15 14:00 | 101.5 | 87.47
2017-03-15 14:30 | 98.73 | 83.39
2017-03-15 15:00 | 97.11 | 81.67
2017-03-15 15:30 | 95.59 | 80.38
2017-03-15 16:00 | 99.71 | 84.65
2017-03-15 16:30 | 101.71 | 87.15
2017-03-15 17:00 | 95.51 | 81.22
2017-03-15 17:30 | 98.51 | 84.83
2017-03-15 18:00 | 99.65 | 86.5
2017-03-15 18:30 | 87.99 | 73.54
2017-03-15 19:00 | 92.83 | 78.89
2017-03-15 19:30 | 102.27 | 88.94
2017-03-15 20:00 | 99.09 | 85.47
2017-03-15 20:30 | 94.3 | 80.63
2017-03-15 21:00 | 97.58 | 84.5
2017-03-15 21:30 | 95.56 | 81.6
2017-03-15 22:00 | 95.87 | 81.89
2017-03-15 22:30 | 95.43 | 82.05
2017-03-15 23:00 | 97.95 | 84.33
2017-03-15 23:30 | 100.74 | 88.08
2017-03-16 | 100.44 | 87.73
2017-03-16 00:30 | 103.16 | 90.7
2017-03-16 01:00 | 104.92 | 92.39
2017-03-16 01:30 | 100.64 | 87.68
2017-03-16 02:00 | 100.62 | 87.97
2017-03-16 02:30 | 104.62 | 92.19
2017-03-16 03:00 | 103.06 | 90.56
2017-03-16 03:30 | 94.97 | 81.56
2017-03-16 04:00 | 101.49 | 89.13
2017-03-16 04:30 | 105.91 | 93.77
2017-03-16 05:00 | 102.57 | 89.94
2017-03-16 05:30 | 105.5 | 92.54
2017-03-16 06:00 | 107.9 | 94.71
2017-03-16 06:30 | 98.54 | 84.47
2017-03-16 07:00 | 108.89 | 95.44
2017-03-16 07:30 | 107.47 | 94.01
2017-03-16 08:00 | 112.47 | 99.49
2017-03-16 08:30 | 109.42 | 95.74
2017-03-16 09:00 | 106.87 | 94.01
2017-03-16 09:30 | 104.38 | 91.29
2017-03-16 10:00 | 99.32 | 85.16
2017-03-16 10:30 | 97.82 | 83.94
2017-03-16 11:00 | 100.47 | 87.2
2017-03-16 11:30 | 104.53 | 90.01
2017-03-16 12:00 | 100.97 | 86.1
2017-03-16 12:30 | 106.11 | 93.22
2017-03-16 13:00 | 106.46 | 93.78
2017-03-16 13:30 | 111.63 | 97.58
2017-03-16 14:00 | 110.79 | 96.64
2017-03-16 14:30 | 107.87 | 94.12
2017-03-16 15:00 | 106.9 | 92.13
2017-03-16 15:30 | 103.93 | 88.81
2017-03-16 16:00 | 108.05 | 92.14
2017-03-16 16:30 | 106.12 | 89.76
2017-03-16 17:00 | 116.53 | 102.28
2017-03-16 17:30 | 109.34 | 95.73
2017-03-16 18:00 | 112.55 | 98.44
2017-03-16 18:30 | 104.09 | 89.51
2017-03-16 19:00 | 114.47 | 100.97
2017-03-16 19:30 | 113.98 | 99.83
2017-03-16 20:00 | 114.77 | 99.8
2017-03-16 20:30 | 118.93 | 105.1
2017-03-16 21:00 | 113.14 | 99.18
2017-03-16 21:30 | 109.86 | 95.82
2017-03-16 22:00 | 113.67 | 98.79
2017-03-16 22:30 | 113.9 | 99.81
2017-03-16 23:00 | 116.88 | 102.15
2017-03-16 23:30 | 115.45 | 101.16
2017-03-17 | 114.26 | 100.83
2017-03-17 00:30 | 115.19 | 101.24
2017-03-17 01:00 | 110.91 | 96.07
2017-03-17 01:30 | 115.67 | 101.01
2017-03-17 02:00 | 116.52 | 102.73
2017-03-17 02:30 | 114.75 | 101.05
2017-03-17 03:00 | 114.93 | 101.13
2017-03-17 03:30 | 115.35 | 101.6
2017-03-17 04:00 | 118.26 | 103.78
2017-03-17 04:30 | 121.67 | 106.79
2017-03-17 05:00 | 123.88 | 108.88
2017-03-17 05:30 | 124.08 | 108.69
2017-03-17 06:00 | 123.32 | 107.37
2017-03-17 06:30 | 102.93 | 85.55
2017-03-17 07:00 | 111.83 | 95.99
2017-03-17 07:30 | 123.91 | 107.54
2017-03-17 08:00 | 125.66 | 109.29
2017-03-17 08:30 | 124.55 | 107.78
2017-03-17 09:00 | 132.66 | 113.8
2017-03-17 09:30 | 129.84 | 111.32
2017-03-17 10:00 | 131.03 | 114.07
2017-03-17 10:30 | 134.34 | 117.8
2017-03-17 11:00 | 118.2 | 100.58
2017-03-17 11:30 | 116.15 | 98.46
2017-03-17 12:00 | 115.84 | 97.75
2017-03-17 12:30 | 125.8 | 105.68
2017-03-17 13:00 | 124.45 | 104.78
2017-03-17 13:30 | 123.89 | 103.32
2017-03-17 14:00 | 132.21 | 111.37
2017-03-17 14:30 | 132.84 | 112.61
2017-03-17 15:00 | 136.08 | 116.02
2017-03-17 15:30 | 130.21 | 109.08
2017-03-17 16:00 | 139.8 | 119.94
2017-03-17 16:30 | 137.42 | 118.62
2017-03-17 17:00 | 130.48 | 109.94
2017-03-17 17:30 | 136.61 | 117.94
2017-03-17 18:00 | 134.54 | 117.74
2017-03-17 18:30 | 121.12 | 104.44
2017-03-17 19:00 | 126.56 | 110.22
2017-03-17 19:30 | 135.12 | 117.88
2017-03-17 20:00 | 135.05 | 116.55
2017-03-17 20:30 | 133.98 | 116.19
2017-03-17 21:00 | 129.97 | 112.78
2017-03-17 21:30 | 122.59 | 106.31
2017-03-17 22:00 | 127.05 | 111.41
2017-03-17 22:30 | 121.83 | 106.29
2017-03-17 23:00 | 120.41 | 104.17
2017-03-17 23:30 | 115.34 | 101.05
2017-03-18 | 122.83 | 108.76
2017-03-18 00:30 | 122.8 | 107.9
2017-03-18 01:00 | 121.54 | 105.98
2017-03-18 01:30 | 120.37 | 104.6
2017-03-18 02:00 | 118.22 | 102.32
2017-03-18 02:30 | 117.48 | 100.69
2017-03-18 03:00 | 119.93 | 103.7
2017-03-18 03:30 | 118.71 | 101.64
2017-03-18 04:00 | 130.42 | 114.41
2017-03-18 04:30 | 123.35 | 107.87
2017-03-18 05:00 | 124.98 | 109.76
2017-03-18 05:30 | 122.18 | 105.72
2017-03-18 06:00 | 118.95 | 101.42
2017-03-18 06:30 | 106.78 | 86.59
2017-03-18 07:00 | 118.28 | 100.35
2017-03-18 07:30 | 121.35 | 103.03
2017-03-18 08:00 | 126.08 | 108.13
2017-03-18 08:30 | 132.71 | 114.63
2017-03-18 09:00 | 140.1 | 121.71
2017-03-18 09:30 | 128.43 | 109.39
2017-03-18 10:00 | 131.73 | 113.64
2017-03-18 10:30 | 128.88 | 110.91
2017-03-18 11:00 | 123.71 | 106.13
2017-03-18 11:30 | 124.54 | 107.01
2017-03-18 12:00 | 122.15 | 105.36
2017-03-18 12:30 | 119.8 | 102.2
2017-03-18 13:00 | 125.39 | 108.69
2017-03-18 13:30 | 117.64 | 101.48
2017-03-18 14:00 | 116.67 | 99.89
2017-03-18 14:30 | 114.72 | 97.84
2017-03-18 15:00 | 118.69 | 101.75
2017-03-18 15:30 | 126.73 | 110.91
2017-03-18 16:00 | 127.96 | 112.99
2017-03-18 16:30 | 123.77 | 106.97
2017-03-18 17:00 | 122.53 | 106.12
2017-03-18 17:30 | 121.87 | 105.42
2017-03-18 18:00 | 137.45 | 120.22
2017-03-18 18:30 | 122.93 | 103.5
2017-03-18 19:00 | 134.55 | 116.52
2017-03-18 19:30 | 139.02 | 121.67
2017-03-18 20:00 | 138.87 | 121.59
2017-03-18 20:30 | 136.08 | 118.34
2017-03-18 21:00 | 130.07 | 112.35
2017-03-18 21:30 | 125.98 | 109.45
2017-03-18 22:00 | 125.43 | 109.37
2017-03-18 22:30 | 130.21 | 113.9
2017-03-18 23:00 | 127.37 | 110.88
2017-03-18 23:30 | 128.8 | 111.78
2017-03-19 | 127.35 | 109.99
2017-03-19 00:30 | 127.07 | 109.88
2017-03-19 01:00 | 122.92 | 106.93
2017-03-19 01:30 | 116.49 | 99.63
2017-03-19 02:00 | 113.06 | 96.49
2017-03-19 02:30 | 122.77 | 107.1
2017-03-19 03:00 | 115 | 99.2
2017-03-19 03:30 | 117.46 | 102.61
2017-03-19 04:00 | 124.95 | 111.04
2017-03-19 04:30 | 121.92 | 106.58
2017-03-19 05:00 | 122.98 | 107.31
2017-03-19 05:30 | 124.76 | 108.65
2017-03-19 06:00 | 116.68 | 100.28
2017-03-19 06:30 | 105.63 | 88.14
2017-03-19 07:00 | 112.8 | 97.08
2017-03-19 07:30 | 120.16 | 104.4
2017-03-19 08:00 | 115.26 | 98.97
2017-03-19 08:30 | 112.33 | 96.33
2017-03-19 09:00 | 115.79 | 100.32
2017-03-19 09:30 | 124.4 | 108.61
2017-03-19 10:00 | 114.55 | 97.94
2017-03-19 10:30 | 113.22 | 94.91
2017-03-19 11:00 | 112.73 | 94.36
2017-03-19 11:30 | 110.92 | 92.32
2017-03-19 12:00 | 116.72 | 98.71
2017-03-19 12:30 | 122.88 | 104.79
2017-03-19 13:00 | 126.47 | 107.41
2017-03-19 13:30 | 128.2 | 109.45
2017-03-19 14:00 | 129.37 | 111.8
2017-03-19 14:30 | 126.04 | 107.82
2017-03-19 15:00 | 126.27 | 108.42
2017-03-19 15:30 | 123.89 | 106.16
2017-03-19 16:00 | 119.62 | 101.22
2017-03-19 16:30 | 120.2 | 102.44
2017-03-19 17:00 | 128.81 | 111.57
2017-03-19 17:30 | 124.18 | 106.29
2017-03-19 18:00 | 128.74 | 110.52
2017-03-19 18:30 | 123.88 | 105.37
2017-03-19 19:00 | 126.97 | 109.21
2017-03-19 19:30 | 122.69 | 103.93
2017-03-19 20:00 | 118.68 | 99.84
2017-03-19 20:30 | 131.15 | 112.82
2017-03-19 21:00 | 133.43 | 116.32
2017-03-19 21:30 | 129.39 | 111.43
2017-03-19 22:00 | 122.23 | 103.58
2017-03-19 22:30 | 122.48 | 104.56
2017-03-19 23:00 | 118.18 | 101.93
2017-03-19 23:30 | 113.93 | 97.11
2017-03-20 | 115.88 | 98.89
2017-03-20 00:30 | 110.81 | 94.18
2017-03-20 01:00 | 104.96 | 88.28
2017-03-20 01:30 | 111.87 | 96.89
2017-03-20 02:00 | 109.09 | 92.34
2017-03-20 02:30 | 114.43 | 96.58
2017-03-20 03:00 | 115.16 | 97.87
2017-03-20 03:30 | 118.01 | 100.28
2017-03-20 04:00 | 113.24 | 96.73
2017-03-20 04:30 | 115.38 | 98.17
2017-03-20 05:00 | 112.55 | 95.61
2017-03-20 05:30 | 114.9 | 97.96
2017-03-20 06:00 | 112.66 | 96.43
2017-03-20 06:30 | 105.63 | 87.15
2017-03-20 07:00 | 117.06 | 99.5
2017-03-20 07:30 | 126.57 | 108.81
2017-03-20 08:00 | 125.37 | 106.24
2017-03-20 08:30 | 120.35 | 102.16
2017-03-20 09:00 | 120.1 | 101.48
2017-03-20 09:30 | 118.1 | 100.09
2017-03-20 10:00 | 114.7 | 97.34
2017-03-20 10:30 | 122.7 | 106.82
2017-03-20 11:00 | 125.64 | 108.7
2017-03-20 11:30 | 122.26 | 104.87
2017-03-20 12:00 | 122.21 | 104.22
2017-03-20 12:30 | 126.03 | 107.73
2017-03-20 13:00 | 119.55 | 101.97
2017-03-20 13:30 | 128.12 | 111.02
2017-03-20 14:00 | 122.61 | 105.91
2017-03-20 14:30 | 129.02 | 113.21
2017-03-20 15:00 | 118.7 | 101.78
2017-03-20 15:30 | 123.81 | 107.41
2017-03-20 16:00 | 123.81 | 107.65
2017-03-20 16:30 | 123.47 | 106.74
2017-03-20 17:00 | 126.01 | 108.85
2017-03-20 17:30 | 120.43 | 103.98
2017-03-20 18:00 | 121.45 | 104.41
2017-03-20 18:30 | 118.19 | 98.93
2017-03-20 19:00 | 126.85 | 109.38
2017-03-20 19:30 | 126.8 | 107.96
2017-03-20 20:00 | 132.42 | 114.21
2017-03-20 20:30 | 123.78 | 106.52
2017-03-20 21:00 | 118.57 | 101.04
2017-03-20 21:30 | 121.93 | 103.46
2017-03-20 22:00 | 130.54 | 112.74
2017-03-20 22:30 | 126.33 | 108.08
2017-03-20 23:00 | 133.64 | 115.11
2017-03-20 23:30 | 124.65 | 107.34
2017-03-21 | 115.62 | 97.46
2017-03-21 00:30 | 123.53 | 105.62
2017-03-21 01:00 | 131.35 | 113.43
2017-03-21 01:30 | 123.02 | 105.23
2017-03-21 02:00 | 129.47 | 111.2
2017-03-21 02:30 | 121.96 | 104.17
2017-03-21 03:00 | 120.82 | 101.72
2017-03-21 03:30 | 116.08 | 97.08
2017-03-21 04:00 | 118.29 | 99.75
2017-03-21 04:30 | 119.72 | 101.56
2017-03-21 05:00 | 122.48 | 103.72
2017-03-21 05:30 | 120.67 | 102.2
2017-03-21 06:00 | 123.96 | 105.84
2017-03-21 06:30 | 119.85 | 100.42
2017-03-21 07:00 | 116.17 | 96.89
2017-03-21 07:30 | 118.18 | 96.78
2017-03-21 08:00 | 116.82 | 96.61
2017-03-21 08:30 | 111.4 | 89.98
2017-03-21 09:00 | 115.72 | 96.09
2017-03-21 09:30 | 114.75 | 95.24
2017-03-21 10:00 | 118.86 | 99.37
2017-03-21 10:30 | 116.13 | 98.56
2017-03-21 11:00 | 114.32 | 97.77
2017-03-21 11:30 | 96.22 | 81.55
2017-03-21 12:00 | 94.81 | 79.1
2017-03-21 12:30 | 94.71 | 79.49
2017-03-21 13:00 | 91.2 | 76.19
2017-03-21 13:30 | 88.7 | 73.23
2017-03-21 14:00 | 93.17 | 78.63
2017-03-21 14:30 | 95.97 | 81.76
2017-03-21 15:00 | 106.37 | 89.26
2017-03-21 15:30 | 114.18 | 98.13
2017-03-21 16:00 | 118.43 | 102.75
2017-03-21 16:30 | 120.6 | 104.22
2017-03-21 17:00 | 113.92 | 97.54
2017-03-21 17:30 | 114.32 | 97.8
2017-03-21 18:00 | 118.48 | 101.25
2017-03-21 18:30 | 119.1 | 100.84
2017-03-21 19:00 | 123.09 | 105.85
2017-03-21 19:30 | 129.87 | 112.87
2017-03-21 20:00 | 123.38 | 106.15
2017-03-21 20:30 | 121.29 | 104.29
2017-03-21 21:00 | 113.68 | 96.46
2017-03-21 21:30 | 112.86 | 94.32
2017-03-21 22:00 | 110.77 | 93.48
2017-03-21 22:30 | 113.29 | 96.54
2017-03-21 23:00 | 111.93 | 94.97
2017-03-21 23:30 | 111.64 | 95.15
2017-03-22 | 117.49 | 100.13
2017-03-22 00:30 | 111.34 | 94.5
2017-03-22 01:00 | 111.05 | 94.72
2017-03-22 01:30 | 113.43 | 96.24
2017-03-22 02:00 | 114.45 | 97.03
2017-03-22 02:30 | 115.91 | 97.76
2017-03-22 03:00 | 109.26 | 91.32
2017-03-22 03:30 | 117.48 | 100.49
2017-03-22 04:00 | 117.06 | 100.13
2017-03-22 04:30 | 108.41 | 90.9
2017-03-22 05:00 | 109.18 | 91.84
2017-03-22 05:30 | 107.23 | 90.37
2017-03-22 06:00 | 108.34 | 92.11
2017-03-22 06:30 | 99.31 | 83.75
2017-03-22 07:00 | 87.19 | 72.7
2017-03-22 07:30 | 99.58 | 87.3
2017-03-22 08:00 | 100.44 | 88.05
2017-03-22 08:30 | 105.34 | 92.64
2017-03-22 09:00 | 93.27 | 80.07
2017-03-22 09:30 | 90.76 | 77.79
2017-03-22 10:00 | 86.21 | 71.73
2017-03-22 10:30 | 90.01 | 75.3
2017-03-22 11:00 | 91.43 | 76.53
2017-03-22 11:30 | 88.33 | 73.62
2017-03-22 12:00 | 93.3 | 79.87
2017-03-22 12:30 | 96.88 | 83.93
2017-03-22 13:00 | 90.92 | 77.05
2017-03-22 13:30 | 90.94 | 76.91
2017-03-22 14:00 | 87.16 | 71.43
2017-03-22 14:30 | 90.78 | 75.35
2017-03-22 15:00 | 90.14 | 74.65
2017-03-22 15:30 | 93.53 | 78.21
2017-03-22 16:00 | 97.19 | 83.65
2017-03-22 16:30 | 95.51 | 81.36
2017-03-22 17:00 | 88.02 | 72.44
2017-03-22 17:30 | 89 | 73.66
2017-03-22 18:00 | 91.99 | 77.9
2017-03-22 18:30 | 87.8 | 73
2017-03-22 19:00 | 88.69 | 74.69
2017-03-22 19:30 | 94.02 | 81.1
2017-03-22 20:00 | 91.62 | 78.21
2017-03-22 20:30 | 95.97 | 82.48
2017-03-22 21:00 | 94.96 | 81.43
2017-03-22 21:30 | 93.03 | 77.65
2017-03-22 22:00 | 87.28 | 70.72
2017-03-22 22:30 | 87.57 | 70.75
2017-03-22 23:00 | 88.37 | 72.75
2017-03-22 23:30 | 90.14 | 74.48
2017-03-23 | 88.33 | 71.61
2017-03-23 00:30 | 91.67 | 76.73
2017-03-23 01:00 | 96.09 | 82.73
2017-03-23 01:30 | 98.13 | 85.71
2017-03-23 02:00 | 96.98 | 84.19
2017-03-23 02:30 | 92.52 | 78.33
2017-03-23 03:00 | 91.53 | 77.44
2017-03-23 03:30 | 90.66 | 77.02
2017-03-23 04:00 | 91.01 | 76.55
2017-03-23 04:30 | 92.74 | 79.47
2017-03-23 05:00 | 93.75 | 80.92
2017-03-23 05:30 | 92.87 | 79.65
2017-03-23 06:00 | 92.84 | 80.79
2017-03-23 06:30 | 87.31 | 73.68
2017-03-23 07:00 | 96.26 | 83.38
2017-03-23 07:30 | 96.57 | 83.22
2017-03-23 08:00 | 97.73 | 84.29
2017-03-23 08:30 | 94.81 | 80.6
2017-03-23 09:00 | 89.4 | 74.61
2017-03-23 09:30 | 93.29 | 79.28
2017-03-23 10:00 | 94.38 | 81.12
2017-03-23 10:30 | 91.15 | 77.16
2017-03-23 11:00 | 90.8 | 76.92
2017-03-23 11:30 | 97.9 | 84.21
2017-03-23 12:00 | 98.25 | 84.9
2017-03-23 12:30 | 93.28 | 79.42
2017-03-23 13:00 | 90.49 | 76.74
2017-03-23 13:30 | 94.67 | 81.22
2017-03-23 14:00 | 94.16 | 80.79
2017-03-23 14:30 | 99.29 | 87.02
2017-03-23 15:00 | 103.6 | 91.58
2017-03-23 15:30 | 105.09 | 92.74
2017-03-23 16:00 | 103.25 | 90.94
2017-03-23 16:30 | 102.54 | 90.12
2017-03-23 17:00 | 103.51 | 91.51
2017-03-23 17:30 | 98.37 | 86.69
2017-03-23 18:00 | 97.35 | 85.22
2017-03-23 18:30 | 98.37 | 85.43
2017-03-23 19:00 | 100.71 | 87.61
2017-03-23 19:30 | 102.03 | 89.66
2017-03-23 20:00 | 102.71 | 90.03
2017-03-23 20:30 | 97.9 | 85.32
2017-03-23 21:00 | 98.18 | 85.37
2017-03-23 21:30 | 97.82 | 85.49
2017-03-23 22:00 | 95.89 | 83.51
2017-03-23 22:30 | 97.39 | 85.37
2017-03-23 23:00 | 103.96 | 90.44
2017-03-23 23:30 | 99.98 | 87.29
2017-03-24 | 98.18 | 84.85
2017-03-24 00:30 | 100.06 | 87.71
2017-03-24 01:00 | 102.27 | 89.81
2017-03-24 01:30 | 101.04 | 88.88
2017-03-24 02:00 | 101.29 | 88.94
2017-03-24 02:30 | 102.06 | 89.72
2017-03-24 03:00 | 102.08 | 90.42
2017-03-24 03:30 | 100.46 | 88.53
2017-03-24 04:00 | 107.33 | 96.24
2017-03-24 04:30 | 107.45 | 95.98
2017-03-24 05:00 | 106.84 | 94.95
2017-03-24 05:30 | 103.19 | 91.24
2017-03-24 06:00 | 106.76 | 94.62
2017-03-24 06:30 | 97.95 | 84.68
2017-03-24 07:00 | 99.31 | 86.2
2017-03-24 07:30 | 113.83 | 102.15
2017-03-24 08:00 | 107.04 | 94.46
2017-03-24 08:30 | 112.77 | 99.45
2017-03-24 09:00 | 108.18 | 95.64
2017-03-24 09:30 | 109.62 | 96.78
2017-03-24 10:00 | 111.27 | 99.53
2017-03-24 10:30 | 96.98 | 83.85
2017-03-24 11:00 | 95.55 | 81.89
2017-03-24 11:30 | 99.68 | 86.77
2017-03-24 12:00 | 109.14 | 96.57
2017-03-24 12:30 | 102.47 | 89.01
2017-03-24 13:00 | 101.15 | 87.53
2017-03-24 13:30 | 109.42 | 95.54
2017-03-24 14:00 | 112.76 | 99.31
2017-03-24 14:30 | 116.85 | 102.47
2017-03-24 15:00 | 109.66 | 95.33
2017-03-24 15:30 | 106.71 | 92.32
2017-03-24 16:00 | 105.96 | 91.61
2017-03-24 16:30 | 97.98 | 85.6
2017-03-24 17:00 | 96.31 | 84.05
2017-03-24 17:30 | 95.25 | 82.66
2017-03-24 18:00 | 96.68 | 84.47
2017-03-24 18:30 | 91.97 | 78.82
2017-03-24 19:00 | 98.93 | 86.12
2017-03-24 19:30 | 96.27 | 83.25
2017-03-24 20:00 | 99.07 | 85.28
2017-03-24 20:30 | 103.78 | 90.68
2017-03-24 21:00 | 102.9 | 89.46
2017-03-24 21:30 | 97.99 | 84.26
2017-03-24 22:00 | 98.48 | 85.46
2017-03-24 22:30 | 100.66 | 88.21
2017-03-24 23:00 | 102.96 | 90.36
2017-03-24 23:30 | 94.62 | 81.36
2017-03-25 | 97.53 | 85.08
2017-03-25 00:30 | 96.76 | 84.07
2017-03-25 01:00 | 97.73 | 83.94
2017-03-25 01:30 | 96.89 | 83.89
2017-03-25 02:00 | 95.49 | 82.59
2017-03-25 02:30 | 101.17 | 88.75
2017-03-25 03:00 | 98.02 | 85.24
2017-03-25 03:30 | 93.55 | 81.03
2017-03-25 04:00 | 96.74 | 84.75
2017-03-25 04:30 | 103.27 | 90.97
2017-03-25 05:00 | 100.21 | 88.26
2017-03-25 05:30 | 105.17 | 93.06
2017-03-25 06:00 | 106.43 | 95.58
2017-03-25 06:30 | 96.02 | 83.12
2017-03-25 07:00 | 98.85 | 85.94
2017-03-25 07:30 | 90.16 | 75.34
2017-03-25 08:00 | 85.16 | 70.09
2017-03-25 08:30 | 87.39 | 72.95
2017-03-25 09:00 | 90.9 | 77.01
2017-03-25 09:30 | 93.97 | 79.7
2017-03-25 10:00 | 96.49 | 82.49
2017-03-25 10:30 | 102.73 | 89.5
2017-03-25 11:00 | 110.41 | 97.96
2017-03-25 11:30 | 112.22 | 99.96
2017-03-25 12:00 | 104.98 | 92.33
2017-03-25 12:30 | 107.11 | 92.51
2017-03-25 13:00 | 104.24 | 89.09
2017-03-25 13:30 | 107.65 | 92.23
2017-03-25 14:00 | 106.32 | 90.85
2017-03-25 14:30 | 107.26 | 91.81
2017-03-25 15:00 | 107.05 | 91.56
2017-03-25 15:30 | 107.5 | 92.05
2017-03-25 16:00 | 111.3 | 96.51
2017-03-25 16:30 | 107.85 | 92.49
2017-03-25 17:00 | 109.76 | 95.65
2017-03-25 17:30 | 105.79 | 92.2
2017-03-25 18:00 | 109.12 | 94.66
2017-03-25 18:30 | 109.5 | 92.83
2017-03-25 19:00 | 122.36 | 105.74
2017-03-25 19:30 | 124.84 | 107.93
2017-03-25 20:00 | 117.35 | 100.34
2017-03-25 20:30 | 116.24 | 99.85
2017-03-25 21:00 | 119.07 | 103.23
2017-03-25 21:30 | 123.61 | 107.6
2017-03-25 22:00 | 118.52 | 102.87
2017-03-25 22:30 | 119.56 | 103.2
2017-03-25 23:00 | 115.55 | 99.55
2017-03-25 23:30 | 115.94 | 100.42
2017-03-26 | 112.52 | 95.95
2017-03-26 00:30 | 115.37 | 98.72
2017-03-26 01:00 | 114.01 | 98.9
2017-03-26 01:30 | 102.9 | 88.92
2017-03-26 02:00 | 106.44 | 93.22
2017-03-26 02:30 | 110.76 | 97.32
2017-03-26 03:00 | 108.05 | 95.1
2017-03-26 03:30 | 106.91 | 94.26
2017-03-26 04:00 | 110.28 | 98
2017-03-26 04:30 | 107.33 | 95.1
2017-03-26 05:00 | 106.21 | 93.54
2017-03-26 05:30 | 98.85 | 85.41
2017-03-26 06:00 | 100.24 | 87.55
2017-03-26 06:30 | 95.6 | 81.18
2017-03-26 07:00 | 95.99 | 82.91
2017-03-26 07:30 | 101.04 | 88.5
2017-03-26 08:00 | 102.85 | 89.35
2017-03-26 08:30 | 106.55 | 93.99
2017-03-26 09:00 | 101.39 | 87.7
2017-03-26 09:30 | 105.99 | 91.84
2017-03-26 10:00 | 103.69 | 90.49
2017-03-26 10:30 | 94.68 | 81.78
2017-03-26 11:00 | 91.8 | 77.23
2017-03-26 11:30 | 100.23 | 85.94
2017-03-26 12:00 | 106.84 | 91.92
2017-03-26 12:30 | 106.23 | 91.61
2017-03-26 13:00 | 109.72 | 94.92
2017-03-26 13:30 | 115.47 | 100.97
2017-03-26 14:00 | 112.36 | 97.72
2017-03-26 14:30 | 115.41 | 101.07
2017-03-26 15:00 | 113.49 | 99.65
2017-03-26 15:30 | 112.9 | 98.52
2017-03-26 16:00 | 116.36 | 102
2017-03-26 16:30 | 112.6 | 98.14
2017-03-26 17:00 | 106.33 | 93.14
2017-03-26 17:30 | 108.66 | 94.4
2017-03-26 18:00 | 113.42 | 100.21
2017-03-26 18:30 | 114.89 | 99.77
2017-03-26 19:00 | 111.52 | 95.49
2017-03-26 19:30 | 114.96 | 99.18
2017-03-26 20:00 | 117.81 | 101.81
2017-03-26 20:30 | 111.26 | 94.92
2017-03-26 21:00 | 110.03 | 95.05
2017-03-26 21:30 | 111.59 | 96.24
2017-03-26 22:00 | 108.07 | 93.54
2017-03-26 22:30 | 108.94 | 94.91
2017-03-26 23:00 | 104.77 | 90.43
2017-03-26 23:30 | 104.44 | 90.67
2017-03-27 | 105.22 | 92.51
2017-03-27 00:30 | 104.34 | 91.29
2017-03-27 01:00 | 102.78 | 90
2017-03-27 01:30 | 104.62 | 91.52
2017-03-27 02:00 | 109.57 | 97.46
2017-03-27 02:30 | 116.71 | 104.82
2017-03-27 03:00 | 109.82 | 96.79
2017-03-27 03:30 | 100.34 | 85.89
2017-03-27 04:00 | 101.09 | 87.51
2017-03-27 04:30 | 100.8 | 88.1
2017-03-27 05:00 | 99.1 | 85.89
2017-03-27 05:30 | 98.25 | 84.48
2017-03-27 06:00 | 100.93 | 88.1
2017-03-27 06:30 | 96.48 | 82.43
2017-03-27 07:00 | 96.13 | 82.26
2017-03-27 07:30 | 108.75 | 97.06
2017-03-27 08:00 | 105.62 | 93.58
2017-03-27 08:30 | 101.7 | 88.97
2017-03-27 09:00 | 102.8 | 90.43
2017-03-27 09:30 | 104.34 | 92.73
2017-03-27 10:00 | 98.6 | 87.1
2017-03-27 10:30 | 94.62 | 81.71
2017-03-27 11:00 | 93.41 | 80.63
2017-03-27 11:30 | 92.41 | 79.93
2017-03-27 12:00 | 88.4 | 76.65
2017-03-27 12:30 | 89.5 | 77.8
2017-03-27 13:00 | 94.67 | 83.29
2017-03-27 13:30 | 97.22 | 85.11
2017-03-27 14:00 | 96.69 | 84.2
2017-03-27 14:30 | 97.76 | 84.01
2017-03-27 15:00 | 101.47 | 86.32
2017-03-27 15:30 | 112.92 | 99.37
2017-03-27 16:00 | 118.83 | 105.46
2017-03-27 16:30 | 114.67 | 100.93
2017-03-27 17:00 | 107.41 | 92.22
2017-03-27 17:30 | 111.63 | 97.57
2017-03-27 18:00 | 115.8 | 101.89
2017-03-27 18:30 | 107.14 | 92.38
2017-03-27 19:00 | 116.62 | 103.6
2017-03-27 19:30 | 117.45 | 104.7
2017-03-27 20:00 | 118.32 | 104.62
2017-03-27 20:30 | 110.92 | 96.36
2017-03-27 21:00 | 107.55 | 93.77
2017-03-27 21:30 | 112.44 | 99.66
2017-03-27 22:00 | 110.4 | 97.67
2017-03-27 22:30 | 113.61 | 101.68
2017-03-27 23:00 | 113.2 | 100.25
2017-03-27 23:30 | 107.17 | 92.85
2017-03-28 | 116.57 | 103.95
2017-03-28 00:30 | 113.2 | 99.77
2017-03-28 01:00 | 104.82 | 91.14
2017-03-28 01:30 | 110.11 | 97.04
2017-03-28 02:00 | 113.42 | 101.01
2017-03-28 02:30 | 112.46 | 99.44
2017-03-28 03:00 | 103.06 | 89.46
2017-03-28 03:30 | 100.42 | 85.96
2017-03-28 04:00 | 108.1 | 94.96
2017-03-28 04:30 | 111.5 | 98.93
2017-03-28 05:00 | 106.27 | 91.9
2017-03-28 05:30 | 108.1 | 93.76
2017-03-28 06:00 | 113 | 99.32
2017-03-28 06:30 | 106.79 | 92.47
2017-03-28 07:00 | 101.33 | 85.92
2017-03-28 07:30 | 110.71 | 95.84
2017-03-28 08:00 | 103.96 | 89.01
2017-03-28 08:30 | 108.18 | 93.01
2017-03-28 09:00 | 101.83 | 87.33
2017-03-28 09:30 | 102 | 86.86
2017-03-28 10:00 | 109.79 | 96.15
2017-03-28 10:30 | 114.18 | 100.34
2017-03-28 11:00 | 106.9 | 92.31
2017-03-28 11:30 | 97.41 | 81.94
2017-03-28 12:00 | 96.82 | 81.57
2017-03-28 12:30 | 94.87 | 79.3
2017-03-28 13:00 | 101.47 | 87.18
2017-03-28 13:30 | 101.01 | 87.01
2017-03-28 14:00 | 103.76 | 89.57
2017-03-28 14:30 | 100.88 | 85.78
2017-03-28 15:00 | 102.18 | 87.07
2017-03-28 15:30 | 96.07 | 79.7
2017-03-28 16:00 | 107.09 | 92.64
2017-03-28 16:30 | 110.84 | 96.91
2017-03-28 17:00 | 106.62 | 92.47
2017-03-28 17:30 | 104.86 | 90.91
2017-03-28 18:00 | 106.82 | 93.19
2017-03-28 18:30 | 108.32 | 94.35
2017-03-28 19:00 | 107.6 | 94.43
2017-03-28 19:30 | 103.04 | 89.46
2017-03-28 20:00 | 99.97 | 86.86
2017-03-28 20:30 | 104.11 | 90.13
2017-03-28 21:00 | 101.33 | 86.36
2017-03-28 21:30 | 105.17 | 91.2
2017-03-28 22:00 | 98.66 | 83.36
2017-03-28 22:30 | 103.04 | 87.64
2017-03-28 23:00 | 99.44 | 83.58
2017-03-28 23:30 | 98.51 | 83.4
2017-03-29 | 95.29 | 78.81
2017-03-29 00:30 | 95.81 | 80.21
2017-03-29 01:00 | 99.83 | 84.88
2017-03-29 01:30 | 94.96 | 79.43
2017-03-29 02:00 | 97.57 | 83.15
2017-03-29 02:30 | 97.66 | 83.52
2017-03-29 03:00 | 97.94 | 83.43
2017-03-29 03:30 | 101.37 | 87.22
2017-03-29 04:00 | 101.18 | 87.55
2017-03-29 04:30 | 98.99 | 85.57
2017-03-29 05:00 | 97.74 | 83.84
2017-03-29 05:30 | 100.79 | 87.1
2017-03-29 06:00 | 103.69 | 88.82
2017-03-29 06:30 | 102.87 | 87.15
2017-03-29 07:00 | 105.72 | 90.34
2017-03-29 07:30 | 106.72 | 91.85
2017-03-29 08:00 | 105.32 | 89.58
2017-03-29 08:30 | 115.16 | 100.11
2017-03-29 09:00 | 105.54 | 90.89
2017-03-29 09:30 | 100.05 | 86.4
2017-03-29 10:00 | 105.83 | 93.14
2017-03-29 10:30 | 107.64 | 94.68
2017-03-29 11:00 | 112.46 | 99.92
2017-03-29 11:30 | 113.47 | 100.45
2017-03-29 12:00 | 115.3 | 102.41
2017-03-29 12:30 | 104.64 | 90.47
2017-03-29 13:00 | 100.21 | 85.8
2017-03-29 13:30 | 101.22 | 87.44
2017-03-29 14:00 | 104.74 | 91.12
2017-03-29 14:30 | 98.89 | 84.79
2017-03-29 15:00 | 94.56 | 78.95
2017-03-29 15:30 | 87.13 | 70.21
2017-03-29 16:00 | 84.36 | 65.71
2017-03-29 16:30 | 81.28 | 61.72
2017-03-29 17:00 | 82.86 | 64.13
2017-03-29 17:30 | 79.55 | 57.52
2017-03-29 18:00 | 77.62 | 55.73
2017-03-29 18:30 | 73.37 | 49.79
2017-03-29 19:00 | 72.56 | 51.04
2017-03-29 19:30 | 69.6 | 45.83
2017-03-29 20:00 | 65.86 | 42.09
2017-03-29 20:30 | 67.13 | 42.16
2017-03-29 21:00 | 67.14 | 40.83
2017-03-29 21:30 | 65 | 36.88
2017-03-29 22:00 | 64.55 | 36.01
2017-03-29 22:30 | 62.21 | 33.96
2017-03-29 23:00 | 61.03 | 32.59
2017-03-29 23:30 | 61.04 | 31.93
2017-03-30 | 61.33 | 31.4
2017-03-30 00:30 | 61.07 | 31.12
2017-03-30 01:00 | 60.63 | 30.59
2017-03-30 01:30 | 60.87 | 30.15
2017-03-30 02:00 | 60.78 | 30.38
2017-03-30 02:30 | 62.46 | 33.81
2017-03-30 03:00 | 63.12 | 34.61
2017-03-30 03:30 | 64.14 | 34.71
2017-03-30 04:00 | 62.7 | 34.24
2017-03-30 04:30 | 63.54 | 35.61
2017-03-30 05:00 | 63.67 | 35.64
2017-03-30 05:30 | 62.01 | 31.92
2017-03-30 06:00 | 62.16 | 33.26
2017-03-30 06:30 | 62.05 | 31.68
2017-03-30 07:00 | 62.96 | 31.39
2017-03-30 07:30 | 66.3 | 35.2
2017-03-30 08:00 | 66.43 | 36.02
2017-03-30 08:30 | 67.03 | 37.35
2017-03-30 09:00 | 63.47 | 33.94
2017-03-30 09:30 | 65.49 | 38.53
2017-03-30 10:00 | 66.65 | 40.36
2017-03-30 10:30 | 67.75 | 39.29
2017-03-30 11:00 | 65.01 | 36.14
2017-03-30 11:30 | 64.77 | 36.47
2017-03-30 12:00 | 66.64 | 39.64
2017-03-30 12:30 | 65.63 | 38.19
2017-03-30 13:00 | 66.47 | 39.03
2017-03-30 13:30 | 66.36 | 39.45
2017-03-30 14:00 | 67.82 | 42.29
2017-03-30 14:30 | 68.24 | 44.95
2017-03-30 15:00 | 70.58 | 50.07
2017-03-30 15:30 | 69.36 | 47.95
2017-03-30 16:00 | 75.28 | 55.7
2017-03-30 16:30 | 82.15 | 62.91
2017-03-30 17:00 | 81.54 | 63.37
2017-03-30 17:30 | 81.11 | 61.88
2017-03-30 18:00 | 79.55 | 60.35
2017-03-30 18:30 | 79.1 | 59.91
2017-03-30 19:00 | 84.25 | 64.95
2017-03-30 19:30 | 88.94 | 71.9
2017-03-30 20:00 | 91.56 | 74.42
2017-03-30 20:30 | 92.35 | 74.69
2017-03-30 21:00 | 93.09 | 74.46
2017-03-30 21:30 | 92.61 | 74.34
2017-03-30 22:00 | 90.71 | 72.16
2017-03-30 22:30 | 90.05 | 72.39
2017-03-30 23:00 | 91.13 | 73.69
2017-03-30 23:30 | 90.38 | 72.96
2017-03-31 | 93.66 | 77
2017-03-31 00:30 | 92.75 | 76.62
2017-03-31 01:00 | 88.53 | 71.77
2017-03-31 01:30 | 88.78 | 72.08
2017-03-31 02:00 | 86.15 | 69.25
2017-03-31 02:30 | 82.53 | 65.65
2017-03-31 03:00 | 82.49 | 64.88
2017-03-31 03:30 | 85.19 | 69.02
2017-03-31 04:00 | 86.88 | 70.73
2017-03-31 04:30 | 88.19 | 71.06
2017-03-31 05:00 | 89.89 | 72.62
2017-03-31 05:30 | 85.01 | 66.6
2017-03-31 06:00 | 82.62 | 62.83
2017-03-31 06:30 | 77.94 | 53.59
2017-03-31 07:00 | 79.78 | 56.31
2017-03-31 07:30 | 81.46 | 61.45
2017-03-31 08:00 | 83.84 | 65.58
2017-03-31 08:30 | 87.03 | 70.9
2017-03-31 09:00 | 87.19 | 70.72
2017-03-31 09:30 | 85.02 | 67.54
2017-03-31 10:00 | 81.24 | 64.3
2017-03-31 10:30 | 86.14 | 69.69
2017-03-31 11:00 | 85.08 | 69.26
2017-03-31 11:30 | 85.72 | 70.05
2017-03-31 12:00 | 84.78 | 67.89
2017-03-31 12:30 | 85.97 | 70.2
2017-03-31 13:00 | 85.74 | 69.95
2017-03-31 13:30 | 86.69 | 70.67
2017-03-31 14:00 | 87.62 | 72.33
2017-03-31 14:30 | 95.84 | 81.61
2017-03-31 15:00 | 98.27 | 84.26
2017-03-31 15:30 | 100.39 | 85.43
2017-03-31 16:00 | 98.91 | 84.06
2017-03-31 16:30 | 100.69 | 86.67
2017-03-31 17:00 | 100.18 | 86.66
2017-03-31 17:30 | 100.97 | 87.74
2017-03-31 18:00 | 103.83 | 89.29
2017-03-31 18:30 | 97.95 | 82.94
2017-03-31 19:00 | 97.96 | 84.33
2017-03-31 19:30 | 104 | 90.74
2017-03-31 20:00 | 98.39 | 84.58
2017-03-31 20:30 | 99.1 | 85.63
2017-03-31 21:00 | 99.53 | 85.18
2017-03-31 21:30 | 101.32 | 87.48
2017-03-31 22:00 | 109.73 | 96.31
2017-03-31 22:30 | 107.72 | 93.99
2017-03-31 23:00 | 102.03 | 88.18
2017-03-31 23:30 | 104.93 | 91
2017-04-01 | 100.25 | 86.37
2017-04-01 00:30 | 102.1 | 87.76
2017-04-01 01:00 | 109.1 | 93.23
2017-04-01 01:30 | 110.49 | 94.24
2017-04-01 02:00 | 106.1 | 90.44
2017-04-01 02:30 | 107.92 | 92.2
2017-04-01 03:00 | 108.59 | 90.71
2017-04-01 03:30 | 105.79 | 87.58
2017-04-01 04:00 | 110.59 | 93.51
2017-04-01 04:30 | 106.78 | 89.49
2017-04-01 05:00 | 102.17 | 84.81
2017-04-01 05:30 | 101.93 | 86.02
2017-04-01 06:00 | 105.7 | 90.37
2017-04-01 06:30 | 94.2 | 77.24
2017-04-01 07:00 | 98.39 | 83.15
2017-04-01 07:30 | 102.58 | 86.77
2017-04-01 08:00 | 101.38 | 84.95
2017-04-01 08:30 | 99.87 | 84.13
2017-04-01 09:00 | 116.86 | 99.32
2017-04-01 09:30 | 108.27 | 91.02
2017-04-01 10:00 | 109.59 | 92.41
2017-04-01 10:30 | 116.72 | 98.51
2017-04-01 11:00 | 112.63 | 94.48
2017-04-01 11:30 | 110.36 | 92.05
2017-04-01 12:00 | 107.91 | 91.22
2017-04-01 12:30 | 102.65 | 83.61
2017-04-01 13:00 | 109.52 | 91.05
2017-04-01 13:30 | 113.58 | 95.06
2017-04-01 14:00 | 106.05 | 86.58
2017-04-01 14:30 | 103.92 | 84.35
2017-04-01 15:00 | 103.14 | 84.06
2017-04-01 15:30 | 104.45 | 85.22
2017-04-01 16:00 | 102.28 | 82.94
2017-04-01 16:30 | 106.37 | 89.1
2017-04-01 17:00 | 106.33 | 88.56
2017-04-01 17:30 | 104.03 | 87.01
2017-04-01 18:00 | 112.99 | 96.06
2017-04-01 18:30 | 98.2 | 80.51
2017-04-01 19:00 | 100.38 | 84
2017-04-01 19:30 | 104.14 | 88.59
2017-04-01 20:00 | 100.92 | 85
2017-04-01 20:30 | 102.32 | 86.66
2017-04-01 21:00 | 97.54 | 81.85
2017-04-01 21:30 | 90.34 | 76.34
2017-04-01 22:00 | 88.35 | 74.42
2017-04-01 22:30 | 86.53 | 72.19
2017-04-01 23:00 | 86.83 | 72.3
2017-04-01 23:30 | 85.89 | 70.06
2017-04-02 | 88.06 | 73.31
2017-04-02 00:30 | 93.67 | 78.31
2017-04-02 01:00 | 91.84 | 75.72
2017-04-02 01:30 | 93.19 | 76.7
2017-04-02 02:00 | 93.41 | 77.8
2017-04-02 02:30 | 87.76 | 73.11
2017-04-02 03:00 | 85.12 | 69.97
2017-04-02 03:30 | 89.32 | 73.76
2017-04-02 04:00 | 88.16 | 73.16
2017-04-02 04:30 | 88.46 | 73.17
2017-04-02 05:00 | 88.02 | 72.13
2017-04-02 05:30 | 91.37 | 76.97
2017-04-02 06:00 | 89.48 | 74.17
2017-04-02 06:30 | 83.9 | 66.43
2017-04-02 07:00 | 90.4 | 74.67
2017-04-02 07:30 | 86.17 | 70.85
2017-04-02 08:00 | 85.48 | 70.2
2017-04-02 08:30 | 89.13 | 74.41
2017-04-02 09:00 | 87.54 | 71.8
2017-04-02 09:30 | 85.49 | 68.5
2017-04-02 10:00 | 84.53 | 68.11
2017-04-02 10:30 | 88.43 | 72.01
2017-04-02 11:00 | 88.82 | 71.07
2017-04-02 11:30 | 87.43 | 70.43
2017-04-02 12:00 | 92.57 | 75.79
2017-04-02 12:30 | 98.85 | 82.24
2017-04-02 13:00 | 95.87 | 79.19
2017-04-02 13:30 | 98.54 | 81.31
2017-04-02 14:00 | 101.38 | 85.11
2017-04-02 14:30 | 99.72 | 82.96
2017-04-02 15:00 | 100.37 | 84.42
2017-04-02 15:30 | 92.18 | 77.37
2017-04-02 16:00 | 88.27 | 75.28
2017-04-02 16:30 | 86.05 | 72.62
2017-04-02 17:00 | 85.15 | 71.08
2017-04-02 17:30 | 84.92 | 70.93
2017-04-02 18:00 | 88.44 | 74.76
2017-04-02 18:30 | 84.36 | 69.61
2017-04-02 19:00 | 84.99 | 70.91
2017-04-02 19:30 | 87.5 | 74.1
2017-04-02 20:00 | 90.04 | 76.63
2017-04-02 20:30 | 86.96 | 72.66
2017-04-02 21:00 | 84.31 | 70.17
2017-04-02 21:30 | 86.82 | 72.51
2017-04-02 22:00 | 87.21 | 72.52
2017-04-02 22:30 | 88.64 | 73.98
2017-04-02 23:00 | 84.63 | 68.73
2017-04-02 23:30 | 83.05 | 66.57
2017-04-03 | 86.15 | 71.14
2017-04-03 00:30 | 88.75 | 73.41
2017-04-03 01:00 | 88.62 | 72.56
2017-04-03 01:30 | 84.56 | 68
2017-04-03 02:00 | 84.32 | 67.89
2017-04-03 02:30 | 85.04 | 69.41
2017-04-03 03:00 | 82.47 | 66.1
2017-04-03 03:30 | 85.13 | 69.17
2017-04-03 04:00 | 89.7 | 74.66
2017-04-03 04:30 | 88.76 | 72.84
2017-04-03 05:00 | 87.24 | 70.67
2017-04-03 05:30 | 85.31 | 68.36
2017-04-03 06:00 | 89.42 | 73.99
2017-04-03 06:30 | 81.48 | 63.77
2017-04-03 07:00 | 83.05 | 67.12
2017-04-03 07:30 | 88.21 | 72.94
2017-04-03 08:00 | 91.89 | 69.89
2017-04-03 08:30 | 99.88 | 71.4
2017-04-03 09:00 | 103.29 | 75.01
2017-04-03 09:30 | 102.65 | 74.76
2017-04-03 10:00 | 101.33 | 72.95
2017-04-03 10:30 | 101.92 | 74.76
2017-04-03 11:00 | 101.39 | 73.04
2017-04-03 11:30 | 97.88 | 72.04
2017-04-03 12:00 | 99.27 | 78.22
2017-04-03 12:30 | 99.54 | 78.03
2017-04-03 13:00 | 96.77 | 75.08
2017-04-03 13:30 | 98.72 | 76.74
2017-04-03 14:00 | 96.77 | 73.8
2017-04-03 14:30 | 98.71 | 76.58
2017-04-03 15:00 | 95.49 | 73.07
2017-04-03 15:30 | 100.71 | 79.4
2017-04-03 16:00 | 99.21 | 78.58
2017-04-03 16:30 | 99.05 | 76.86
2017-04-03 17:00 | 97.73 | 74.7
2017-04-03 17:30 | 98.9 | 76.75
2017-04-03 18:00 | 98.54 | 76.5
2017-04-03 18:30 | 93.27 | 68.26
2017-04-03 19:00 | 96.97 | 73.51
2017-04-03 19:30 | 99.31 | 77.14
2017-04-03 20:00 | 97.3 | 74.04
2017-04-03 20:30 | 98.75 | 76.58
2017-04-03 21:00 | 98.28 | 75.26
2017-04-03 21:30 | 95.46 | 72.91
2017-04-03 22:00 | 96.72 | 74.53
2017-04-03 22:30 | 95.21 | 70.31
2017-04-03 23:00 | 93.04 | 65.99
2017-04-03 23:30 | 95.2 | 68.02
2017-04-04 | 95.34 | 67.97
2017-04-04 00:30 | 98.2 | 71.66
2017-04-04 01:00 | 95.2 | 68.26
2017-04-04 01:30 | 93.89 | 65.77
2017-04-04 02:00 | 96.29 | 69.21
2017-04-04 02:30 | 93.89 | 66.6
2017-04-04 03:00 | 90.69 | 62.6
2017-04-04 03:30 | 91.32 | 63.63
2017-04-04 04:00 | 93.37 | 66.61
2017-04-04 04:30 | 92.55 | 65.77
2017-04-04 05:00 | 91.19 | 64.39
2017-04-04 05:30 | 90.27 | 62.41
2017-04-04 06:00 | 89.23 | 61.37
2017-04-04 06:30 | 86.35 | 56.13
2017-04-04 07:00 | 86.61 | 56.6
2017-04-04 07:30 | 89.77 | 61.86
2017-04-04 08:00 | 91.21 | 63.57
2017-04-04 08:30 | 89.96 | 61.21
2017-04-04 09:00 | 87.56 | 58.93
2017-04-04 09:30 | 89.08 | 60.08
2017-04-04 10:00 | 86.71 | 55.92
2017-04-04 10:30 | 86.74 | 55.99
2017-04-04 11:00 | 86.98 | 54.72
2017-04-04 11:30 | 86.83 | 55.89
2017-04-04 12:00 | 86.67 | 53.82
2017-04-04 12:30 | 89.64 | 59.39
2017-04-04 13:00 | 93.87 | 65.19
2017-04-04 13:30 | 93.44 | 64.68
2017-04-04 14:00 | 92.77 | 62.9
2017-04-04 14:30 | 92.67 | 62.48
2017-04-04 15:00 | 93.55 | 65.32
2017-04-04 15:30 | 87.84 | 58.85
2017-04-04 16:00 | 88.65 | 59.55
2017-04-04 16:30 | 91.78 | 62.26
2017-04-04 17:00 | 90.29 | 60.12
2017-04-04 17:30 | 92.68 | 64.26
2017-04-04 18:00 | 95.26 | 68.98
2017-04-04 18:30 | 93.56 | 66.46
2017-04-04 19:00 | 95.95 | 72.21
2017-04-04 19:30 | 96.42 | 73.39
2017-04-04 20:00 | 95.95 | 72.05
2017-04-04 20:30 | 90.55 | 67.37
2017-04-04 21:00 | 93.5 | 69.12
2017-04-04 21:30 | 96.46 | 71.57
2017-04-04 22:00 | 95.53 | 69.47
2017-04-04 22:30 | 93.22 | 65.84
2017-04-04 23:00 | 94.97 | 67.77
2017-04-04 23:30 | 97.68 | 71.73
2017-04-05 | 99.53 | 74.98
2017-04-05 00:30 | 100.94 | 77.15
2017-04-05 01:00 | 100.76 | 76.77
2017-04-05 01:30 | 98.2 | 74.22
2017-04-05 02:00 | 101.45 | 77.18
2017-04-05 02:30 | 100.9 | 75.69
2017-04-05 03:00 | 100.8 | 75.17
2017-04-05 03:30 | 98.13 | 77.01
2017-04-05 04:00 | 97.89 | 76.57
2017-04-05 04:30 | 97.97 | 75.75
2017-04-05 05:00 | 97.08 | 74.8
2017-04-05 05:30 | 91.51 | 69.05
2017-04-05 06:00 | 94.36 | 72.08
2017-04-05 06:30 | 90.99 | 63.88
2017-04-05 07:00 | 94.6 | 68.79
2017-04-05 07:30 | 94.61 | 70.11
2017-04-05 08:00 | 91.56 | 66.8
2017-04-05 08:30 | 96.45 | 73.15
2017-04-05 09:00 | 97.39 | 72.88
2017-04-05 09:30 | 98.61 | 75.14
2017-04-05 10:00 | 100.41 | 76.66
2017-04-05 10:30 | 102.07 | 78.65
2017-04-05 11:00 | 99.57 | 74.65
2017-04-05 11:30 | 100.77 | 76.95
2017-04-05 12:00 | 102.66 | 78.87
2017-04-05 12:30 | 104.24 | 81.71
2017-04-05 13:00 | 100.31 | 76.23
2017-04-05 13:30 | 98.66 | 74.88
2017-04-05 14:00 | 96.81 | 73.91
2017-04-05 14:30 | 101.2 | 77.58
2017-04-05 15:00 | 103.24 | 81.37
2017-04-05 15:30 | 103 | 80.68
2017-04-05 16:00 | 104.75 | 83.41
2017-04-05 16:30 | 100.66 | 78.63
2017-04-05 17:00 | 101.81 | 79.48
2017-04-05 17:30 | 103.39 | 82.35
2017-04-05 18:00 | 103.28 | 83.68
2017-04-05 18:30 | 104.39 | 84.09
2017-04-05 19:00 | 109.35 | 91.36
2017-04-05 19:30 | 110.88 | 93.25
2017-04-05 20:00 | 107.21 | 90.47
2017-04-05 20:30 | 107.26 | 90.4
2017-04-05 21:00 | 105.67 | 88.35
2017-04-05 21:30 | 104.75 | 86.38
2017-04-05 22:00 | 105.5 | 87.63
2017-04-05 22:30 | 110.66 | 91.56
2017-04-05 23:00 | 109.23 | 88.48
2017-04-05 23:30 | 110.75 | 91.12
2017-04-06 | 111.93 | 93.79
2017-04-06 00:30 | 110.1 | 91.44
2017-04-06 01:00 | 107.74 | 88.68
2017-04-06 01:30 | 107.14 | 87.55
2017-04-06 02:00 | 106.95 | 86.94
2017-04-06 02:30 | 105.17 | 83.66
2017-04-06 03:00 | 106.91 | 85.85
2017-04-06 03:30 | 103.48 | 82.28
2017-04-06 04:00 | 103.6 | 82.46
2017-04-06 04:30 | 101.74 | 79.96
2017-04-06 05:00 | 103.13 | 80.62
2017-04-06 05:30 | 104.08 | 81.06
2017-04-06 06:00 | 104.71 | 82.7
2017-04-06 06:30 | 101.42 | 76.59
2017-04-06 07:00 | 94.68 | 69.11
2017-04-06 07:30 | 92.48 | 68.25
2017-04-06 08:00 | 95.06 | 71.09
2017-04-06 08:30 | 100.91 | 79.69
2017-04-06 09:00 | 98.74 | 76.68
2017-04-06 09:30 | 98.48 | 75.72
2017-04-06 10:00 | 97.49 | 74.89
2017-04-06 10:30 | 98.13 | 75.21
2017-04-06 11:00 | 102.23 | 78.39
2017-04-06 11:30 | 103.85 | 79.29
2017-04-06 12:00 | 103.31 | 79.9
2017-04-06 12:30 | 102.92 | 79.87
2017-04-06 13:00 | 100.74 | 79.85
2017-04-06 13:30 | 101.39 | 80.84
2017-04-06 14:00 | 101.71 | 78.41
2017-04-06 14:30 | 106.13 | 85.48
2017-04-06 15:00 | 104.81 | 82.65
2017-04-06 15:30 | 102.79 | 80.15
2017-04-06 16:00 | 97.04 | 74.4
2017-04-06 16:30 | 100.91 | 79.14
2017-04-06 17:00 | 103.53 | 82.39
2017-04-06 17:30 | 105.12 | 85.32
2017-04-06 18:00 | 104.58 | 86.04
2017-04-06 18:30 | 101.16 | 80.79
2017-04-06 19:00 | 102.82 | 85.08
2017-04-06 19:30 | 104.57 | 86.62
2017-04-06 20:00 | 102.39 | 83.52
2017-04-06 20:30 | 101.98 | 82.39
2017-04-06 21:00 | 102.01 | 82.53
2017-04-06 21:30 | 96.68 | 76.9
2017-04-06 22:00 | 95.91 | 76.04
2017-04-06 22:30 | 100.78 | 79.2
2017-04-06 23:00 | 96.18 | 72.77
2017-04-06 23:30 | 97.23 | 75.05
2017-04-07 | 102.04 | 81.64
2017-04-07 00:30 | 99.71 | 77.85
2017-04-07 01:00 | 103.38 | 81.47
2017-04-07 01:30 | 99.84 | 77.28
2017-04-07 02:00 | 103.14 | 82.2
2017-04-07 02:30 | 103.41 | 83.43
2017-04-07 03:00 | 101.03 | 79.75
2017-04-07 03:30 | 98.76 | 76.99
2017-04-07 04:00 | 101.12 | 80.17
2017-04-07 04:30 | 102.79 | 83.79
2017-04-07 05:00 | 100.98 | 81.2
2017-04-07 05:30 | 101.49 | 82.07
2017-04-07 06:00 | 100.67 | 82.51
2017-04-07 06:30 | 94.63 | 71.88
2017-04-07 07:00 | 97.66 | 77.5
2017-04-07 07:30 | 101.06 | 82.29
2017-04-07 08:00 | 98.14 | 78.13
2017-04-07 08:30 | 98.3 | 79.4
2017-04-07 09:00 | 100.81 | 82.09
2017-04-07 09:30 | 100.81 | 81.22
2017-04-07 10:00 | 99.19 | 79.28
2017-04-07 10:30 | 99.94 | 79.72
2017-04-07 11:00 | 100.29 | 79.6
2017-04-07 11:30 | 101.76 | 81.71
2017-04-07 12:00 | 100.24 | 79.41
2017-04-07 12:30 | 101.72 | 81.52
2017-04-07 13:00 | 100.69 | 80.54
2017-04-07 13:30 | 100.74 | 79.72
2017-04-07 14:00 | 101.51 | 82.42
2017-04-07 14:30 | 100.15 | 80.26
2017-04-07 15:00 | 101.24 | 80.46
2017-04-07 15:30 | 100.9 | 79.57
2017-04-07 16:00 | 102.72 | 82.13
2017-04-07 16:30 | 103.48 | 83.99
2017-04-07 17:00 | 105.26 | 86.57
2017-04-07 17:30 | 102.66 | 84.4
2017-04-07 18:00 | 102.93 | 85.46
2017-04-07 18:30 | 99.5 | 78.23
2017-04-07 19:00 | 102.66 | 85.41
2017-04-07 19:30 | 106.7 | 90.73
2017-04-07 20:00 | 110.58 | 94.4
2017-04-07 20:30 | 108.55 | 91.85
2017-04-07 21:00 | 109.15 | 92.28
2017-04-07 21:30 | 103.36 | 84.93
2017-04-07 22:00 | 104.71 | 85.09
2017-04-07 22:30 | 101.78 | 80.62
2017-04-07 23:00 | 99.87 | 79.54
2017-04-07 23:30 | 98.63 | 79.48
2017-04-08 | 98.63 | 79.61
2017-04-08 00:30 | 98.06 | 78.73
2017-04-08 01:00 | 100.66 | 81.76
2017-04-08 01:30 | 98.54 | 78.45
2017-04-08 02:00 | 93.12 | 72.61
2017-04-08 02:30 | 92.99 | 73.98
2017-04-08 03:00 | 97.79 | 77.96
2017-04-08 03:30 | 97.45 | 77.65
2017-04-08 04:00 | 96.53 | 77.39
2017-04-08 04:30 | 96.08 | 76.35
2017-04-08 05:00 | 96.51 | 76.31
2017-04-08 05:30 | 93.79 | 72.56
2017-04-08 06:00 | 98.71 | 79.81
2017-04-08 06:30 | 93.66 | 70.92
2017-04-08 07:00 | 92.67 | 70.92
2017-04-08 07:30 | 96.4 | 75.47
2017-04-08 08:00 | 98.11 | 77.36
2017-04-08 08:30 | 101.09 | 81.02
2017-04-08 09:00 | 100.37 | 81.02
2017-04-08 09:30 | 96.49 | 77.17
2017-04-08 10:00 | 94.54 | 75.67
2017-04-08 10:30 | 95.14 | 76.41
2017-04-08 11:00 | 93.77 | 74.36
2017-04-08 11:30 | 97.35 | 79.5
2017-04-08 12:00 | 97.04 | 78.82
2017-04-08 12:30 | 96.14 | 78.13
2017-04-08 13:00 | 96.7 | 79.02
2017-04-08 13:30 | 95.5 | 77.25
2017-04-08 14:00 | 99.1 | 81.58
2017-04-08 14:30 | 99.52 | 82.68
2017-04-08 15:00 | 99.52 | 82.25
2017-04-08 15:30 | 96.96 | 79.34
2017-04-08 16:00 | 98.67 | 81.53
2017-04-08 16:30 | 95.23 | 77.09
2017-04-08 17:00 | 95.68 | 77.98
2017-04-08 17:30 | 98.21 | 80.86
2017-04-08 18:00 | 96.71 | 79.25
2017-04-08 18:30 | 89.93 | 68
2017-04-08 19:00 | 96 | 77.96
2017-04-08 19:30 | 101.32 | 84.56
2017-04-08 20:00 | 96.41 | 78.66
2017-04-08 20:30 | 95.16 | 76.16
2017-04-08 21:00 | 96.81 | 76.09
2017-04-08 21:30 | 95.31 | 72.96
2017-04-08 22:00 | 91.33 | 68.02
2017-04-08 22:30 | 88.14 | 62.89
2017-04-08 23:00 | 88.41 | 62.82
2017-04-08 23:30 | 87.36 | 61.03
2017-04-09 | 86.4 | 60.75
2017-04-09 00:30 | 89.08 | 65.13
2017-04-09 01:00 | 89.39 | 65.66
2017-04-09 01:30 | 91.77 | 69.24
2017-04-09 02:00 | 92.58 | 70.7
2017-04-09 02:30 | 88.28 | 63.61
2017-04-09 03:00 | 91.77 | 68.58
2017-04-09 03:30 | 90.57 | 67.88
2017-04-09 04:00 | 91.11 | 68.9
2017-04-09 04:30 | 92.6 | 70.61
2017-04-09 05:00 | 92.26 | 69.7
2017-04-09 05:30 | 90.34 | 66.55
2017-04-09 06:00 | 91.76 | 68.06
2017-04-09 06:30 | 83.37 | 55.29
2017-04-09 07:00 | 88.35 | 62.58
2017-04-09 07:30 | 88.42 | 64.11
2017-04-09 08:00 | 86.38 | 63.4
2017-04-09 08:30 | 82.59 | 56.83
2017-04-09 09:00 | 81.14 | 57.29
2017-04-09 09:30 | 81.17 | 58.55
2017-04-09 10:00 | 83.13 | 61.91
2017-04-09 10:30 | 87.34 | 67.08
2017-04-09 11:00 | 85.74 | 64.14
2017-04-09 11:30 | 86.19 | 64.87
2017-04-09 12:00 | 88.19 | 68.36
2017-04-09 12:30 | 83.4 | 64.81
2017-04-09 13:00 | 85.77 | 66.92
2017-04-09 13:30 | 83.58 | 64.75
2017-04-09 14:00 | 83.93 | 65.93
2017-04-09 14:30 | 87.83 | 69.58
2017-04-09 15:00 | 88.06 | 69.75
2017-04-09 15:30 | 88.59 | 70.47
2017-04-09 16:00 | 90.68 | 73.44
2017-04-09 16:30 | 92.03 | 75.54
2017-04-09 17:00 | 88.51 | 72.02
2017-04-09 17:30 | 88.66 | 72.93
2017-04-09 18:00 | 91.92 | 77.08
2017-04-09 18:30 | 87.49 | 70.74
2017-04-09 19:00 | 93.28 | 79.36
2017-04-09 19:30 | 94.52 | 81.01
2017-04-09 20:00 | 96.89 | 83.57
2017-04-09 20:30 | 91.07 | 75.48
2017-04-09 21:00 | 95.03 | 77.81
2017-04-09 21:30 | 96.88 | 79.43
2017-04-09 22:00 | 95.42 | 76.49
2017-04-09 22:30 | 98.28 | 79.32
2017-04-09 23:00 | 93.07 | 73.29
2017-04-09 23:30 | 97.6 | 77.06
2017-04-10 | 96.68 | 75.13
2017-04-10 00:30 | 100.32 | 79.48
2017-04-10 01:00 | 101.74 | 80.84
2017-04-10 01:30 | 98.46 | 77.23
2017-04-10 02:00 | 98.83 | 76.65
2017-04-10 02:30 | 99.86 | 78.96
2017-04-10 03:00 | 99.82 | 78.62
2017-04-10 03:30 | 100.3 | 79.32
2017-04-10 04:00 | 99.76 | 80.22
2017-04-10 04:30 | 100.01 | 81.49
2017-04-10 05:00 | 99.32 | 78.27
2017-04-10 05:30 | 101.11 | 80.16
2017-04-10 06:00 | 102.16 | 81.98
2017-04-10 06:30 | 95.59 | 71.15
2017-04-10 07:00 | 90.57 | 67.12
2017-04-10 07:30 | 93.12 | 71.2
2017-04-10 08:00 | 93.74 | 72.29
2017-04-10 08:30 | 96.74 | 76.61
2017-04-10 09:00 | 106.42 | 87.69
2017-04-10 09:30 | 101.76 | 82.38
2017-04-10 10:00 | 105.38 | 85.76
2017-04-10 10:30 | 107.36 | 89.34
2017-04-10 11:00 | 106.02 | 86.91
2017-04-10 11:30 | 105.02 | 84.95
2017-04-10 12:00 | 107.79 | 89.18
2017-04-10 12:30 | 105.52 | 87.02
2017-04-10 13:00 | 104.59 | 85.58
2017-04-10 13:30 | 104.55 | 85.36
2017-04-10 14:00 | 107.72 | 88.83
2017-04-10 14:30 | 106.36 | 87.93
2017-04-10 15:00 | 104.84 | 86.07
2017-04-10 15:30 | 104.96 | 85.4
2017-04-10 16:00 | 106.94 | 88.26
2017-04-10 16:30 | 106.83 | 89.08
2017-04-10 17:00 | 104.51 | 86.03
2017-04-10 17:30 | 103.99 | 84.37
2017-04-10 18:00 | 109.28 | 92.89
2017-04-10 18:30 | 104.47 | 84.03
2017-04-10 19:00 | 102.23 | 84.2
2017-04-10 19:30 | 105.61 | 88.37
2017-04-10 20:00 | 104.54 | 86.31
2017-04-10 20:30 | 106.97 | 89.13
2017-04-10 21:00 | 107.78 | 89.87
2017-04-10 21:30 | 102.92 | 83.54
2017-04-10 22:00 | 101.49 | 81.81
2017-04-10 22:30 | 104.45 | 84.05
2017-04-10 23:00 | 106 | 85.6
2017-04-10 23:30 | 102.44 | 80.86
2017-04-11 | 102.44 | 80.03
2017-04-11 00:30 | 108.39 | 88.47
2017-04-11 01:00 | 102.38 | 79.49
2017-04-11 01:30 | 104.83 | 81.97
2017-04-11 02:00 | 105.24 | 83.62
2017-04-11 02:30 | 105.73 | 84.98
2017-04-11 03:00 | 103.74 | 80.37
2017-04-11 03:30 | 104.08 | 81.06
2017-04-11 04:00 | 101.11 | 82.34
2017-04-11 04:30 | 100.85 | 83
2017-04-11 05:00 | 98.21 | 79.89
2017-04-11 05:30 | 94.71 | 75.56
2017-04-11 06:00 | 91.17 | 70.41
2017-04-11 06:30 | 86.21 | 60.99
2017-04-11 07:00 | 93.05 | 71.36
2017-04-11 07:30 | 94.22 | 74.35
2017-04-11 08:00 | 89.73 | 68.03
2017-04-11 08:30 | 89.17 | 67.24
2017-04-11 09:00 | 86.7 | 65.11
2017-04-11 09:30 | 84.95 | 62.84
2017-04-11 10:00 | 88.63 | 67.43
2017-04-11 10:30 | 93.36 | 73.03
2017-04-11 11:00 | 95.04 | 74.82
2017-04-11 11:30 | 93.36 | 72.88
2017-04-11 12:00 | 92.7 | 70.4
2017-04-11 12:30 | 94.35 | 72.39
2017-04-11 13:00 | 96.92 | 74.05
2017-04-11 13:30 | 96.53 | 74.45
2017-04-11 14:00 | 103.27 | 82.74
2017-04-11 14:30 | 104.94 | 85.26
2017-04-11 15:00 | 93.94 | 72.11
2017-04-11 15:30 | 94.13 | 71.1
2017-04-11 16:00 | 97.55 | 77.26
2017-04-11 16:30 | 96.84 | 77.23
2017-04-11 17:00 | 99.8 | 81.52
2017-04-11 17:30 | 103.9 | 87.07
2017-04-11 18:00 | 102.43 | 83.45
2017-04-11 18:30 | 97.97 | 76.88
2017-04-11 19:00 | 104.67 | 86.84
2017-04-11 19:30 | 106.57 | 90.51
2017-04-11 20:00 | 107.31 | 92.16
2017-04-11 20:30 | 101.92 | 84.13
2017-04-11 21:00 | 111.53 | 95.12
2017-04-11 21:30 | 104.22 | 85.9
2017-04-11 22:00 | 106.23 | 88.06
2017-04-11 22:30 | 101.88 | 82.24
2017-04-11 23:00 | 102.18 | 81.55
2017-04-11 23:30 | 103.3 | 82.57
2017-04-12 | 102.86 | 81.31
2017-04-12 00:30 | 100.27 | 79.79
2017-04-12 01:00 | 102.55 | 82.19
2017-04-12 01:30 | 103.31 | 82.85
2017-04-12 02:00 | 107.7 | 87.69
2017-04-12 02:30 | 104.08 | 83.28
2017-04-12 03:00 | 103.13 | 81.06
2017-04-12 03:30 | 107.27 | 87.16
2017-04-12 04:00 | 104.1 | 83.16
2017-04-12 04:30 | 101.36 | 80.48
2017-04-12 05:00 | 107.01 | 86.49
2017-04-12 05:30 | 102.95 | 81.94
2017-04-12 06:00 | 101.47 | 79.52
2017-04-12 06:30 | 97.79 | 74.29
2017-04-12 07:00 | 104.98 | 84.61
2017-04-12 07:30 | 105.85 | 86.53
2017-04-12 08:00 | 103.57 | 81.29
2017-04-12 08:30 | 97.3 | 75.51
2017-04-12 09:00 | 101.79 | 77.64
2017-04-12 09:30 | 106.25 | 83.23
2017-04-12 10:00 | 109.02 | 87.92
2017-04-12 10:30 | 104.25 | 81.97
2017-04-12 11:00 | 102.8 | 78.39
2017-04-12 11:30 | 112.57 | 91.19
2017-04-12 12:00 | 110.3 | 88.08
2017-04-12 12:30 | 108.81 | 85.86
2017-04-12 13:00 | 106.01 | 82.55
2017-04-12 13:30 | 101.14 | 76.78
2017-04-12 14:00 | 104.3 | 81.75
2017-04-12 14:30 | 106.04 | 84.46
2017-04-12 15:00 | 104.26 | 82.44
2017-04-12 15:30 | 98.03 | 75.13
2017-04-12 16:00 | 98.1 | 73.58
2017-04-12 16:30 | 103.84 | 82.89
2017-04-12 17:00 | 104.99 | 85.53
2017-04-12 17:30 | 102.14 | 82.51
2017-04-12 18:00 | 105.99 | 86.46
2017-04-12 18:30 | 99.09 | 76.61
2017-04-12 19:00 | 104.99 | 84.84
2017-04-12 19:30 | 104.78 | 85.19
2017-04-12 20:00 | 103.95 | 84.13
2017-04-12 20:30 | 110.61 | 92.24
2017-04-12 21:00 | 108.8 | 89.52
2017-04-12 21:30 | 105.53 | 84.68
2017-04-12 22:00 | 99.7 | 76.83
2017-04-12 22:30 | 100.11 | 76.04
2017-04-12 23:00 | 101.3 | 77.84
2017-04-12 23:30 | 100.79 | 75.07
2017-04-13 | 105.43 | 80.94
2017-04-13 00:30 | 103.31 | 78.37
2017-04-13 01:00 | 107.84 | 85.17
2017-04-13 01:30 | 113.44 | 92.95
2017-04-13 02:00 | 109.04 | 86.33
2017-04-13 02:30 | 108.58 | 86.77
2017-04-13 03:00 | 106.86 | 83.13
2017-04-13 03:30 | 108.47 | 87.72
2017-04-13 04:00 | 108.65 | 86.88
2017-04-13 04:30 | 107.45 | 84.55
2017-04-13 05:00 | 110.2 | 88.41
2017-04-13 05:30 | 112.88 | 91.87
2017-04-13 06:00 | 113.5 | 92.92
2017-04-13 06:30 | 106.57 | 82.84
2017-04-13 07:00 | 111.71 | 90.42
2017-04-13 07:30 | 114.34 | 93.91
2017-04-13 08:00 | 108.33 | 86.6
2017-04-13 08:30 | 106.38 | 82.87
2017-04-13 09:00 | 109.07 | 86.19
2017-04-13 09:30 | 108.73 | 84.22
2017-04-13 10:00 | 109.98 | 85.78
2017-04-13 10:30 | 109.39 | 85.55
2017-04-13 11:00 | 106.25 | 80.49
2017-04-13 11:30 | 107.97 | 85.1
2017-04-13 12:00 | 105.03 | 80.84
2017-04-13 12:30 | 97.29 | 70.77
2017-04-13 13:00 | 99.4 | 75.77
2017-04-13 13:30 | 100.11 | 74.38
2017-04-13 14:00 | 98.94 | 72.56
2017-04-13 14:30 | 99.48 | 73.32
2017-04-13 15:00 | 94.5 | 66.22
2017-04-13 15:30 | 101.87 | 76.56
2017-04-13 16:00 | 101.57 | 77.4
2017-04-13 16:30 | 101.47 | 78.19
2017-04-13 17:00 | 101.85 | 78.88
2017-04-13 17:30 | 100.7 | 78.19
2017-04-13 18:00 | 101.28 | 78.87
2017-04-13 18:30 | 99.07 | 76.24
2017-04-13 19:00 | 101.51 | 79.83
2017-04-13 19:30 | 106.94 | 88.08
2017-04-13 20:00 | 111.41 | 93.54
2017-04-13 20:30 | 112.61 | 94.65
2017-04-13 21:00 | 111.36 | 93.03
2017-04-13 21:30 | 114.45 | 95.67
2017-04-13 22:00 | 116.25 | 97.85
2017-04-13 22:30 | 116.17 | 97.23
2017-04-13 23:00 | 115.68 | 96.45
2017-04-13 23:30 | 115.51 | 94.99
2017-04-14 | 117.41 | 98.04
2017-04-14 00:30 | 116.13 | 98.09
2017-04-14 01:00 | 115.88 | 97.39
2017-04-14 01:30 | 118.22 | 100.18
2017-04-14 02:00 | 123.42 | 106.91
2017-04-14 02:30 | 118.33 | 100.09
2017-04-14 03:00 | 113.29 | 92.98
2017-04-14 03:30 | 111.43 | 92.26
2017-04-14 04:00 | 118.33 | 101.41
2017-04-14 04:30 | 117.18 | 98.26
2017-04-14 05:00 | 116.05 | 96.99
2017-04-14 05:30 | 117.44 | 98.96
2017-04-14 06:00 | 113.26 | 92.97
2017-04-14 06:30 | 108.3 | 85.97
2017-04-14 07:00 | 108.91 | 87.54
2017-04-14 07:30 | 114.78 | 96.78
2017-04-14 08:00 | 114.82 | 98.14
2017-04-14 08:30 | 109.86 | 89.9
2017-04-14 09:00 | 107.2 | 88.11
2017-04-14 09:30 | 114.56 | 98.2
2017-04-14 10:00 | 110.57 | 90.73
2017-04-14 10:30 | 117.32 | 99.57
2017-04-14 11:00 | 113.01 | 94.27
2017-04-14 11:30 | 111.49 | 92.21
2017-04-14 12:00 | 114.34 | 96.8
2017-04-14 12:30 | 114.95 | 97.92
2017-04-14 13:00 | 113.08 | 95.08
2017-04-14 13:30 | 111.05 | 93.64
2017-04-14 14:00 | 121.29 | 105.71
2017-04-14 14:30 | 119.13 | 102.73
2017-04-14 15:00 | 116.27 | 98.06
2017-04-14 15:30 | 116.81 | 97.5
2017-04-14 16:00 | 114.75 | 97.62
2017-04-14 16:30 | 111.69 | 93.83
2017-04-14 17:00 | 115.87 | 97.63
2017-04-14 17:30 | 109.85 | 88.63
2017-04-14 18:00 | 107.3 | 86.12
2017-04-14 18:30 | 107.71 | 86.41
2017-04-14 19:00 | 109.75 | 91.98
2017-04-14 19:30 | 113.4 | 94.15
2017-04-14 20:00 | 115.26 | 96.21
2017-04-14 20:30 | 113.85 | 94.68
2017-04-14 21:00 | 110.41 | 90.05
2017-04-14 21:30 | 112.24 | 92.72
2017-04-14 22:00 | 112.79 | 94.21
2017-04-14 22:30 | 116.42 | 98.3
2017-04-14 23:00 | 112.95 | 94.51
2017-04-14 23:30 | 112.41 | 91.41
2017-04-15 | 114.65 | 94.52
2017-04-15 00:30 | 112.52 | 94.45
2017-04-15 01:00 | 112.72 | 96.2
2017-04-15 01:30 | 111.92 | 94.93
2017-04-15 02:00 | 109.77 | 92.08
2017-04-15 02:30 | 105.79 | 87.31
2017-04-15 03:00 | 106.44 | 87.96
2017-04-15 03:30 | 103.33 | 81.94
2017-04-15 04:00 | 106.34 | 86.97
2017-04-15 04:30 | 109.16 | 89.47
2017-04-15 05:00 | 107.85 | 88.83
2017-04-15 05:30 | 110.94 | 91.76
2017-04-15 06:00 | 116.78 | 98.23
2017-04-15 06:30 | 112.64 | 91.81
2017-04-15 07:00 | 115.55 | 95.56
2017-04-15 07:30 | 115.35 | 98.08
2017-04-15 08:00 | 112.06 | 93.26
2017-04-15 08:30 | 113.57 | 95.35
2017-04-15 09:00 | 110.72 | 93.41
2017-04-15 09:30 | 106.72 | 89.53
2017-04-15 10:00 | 113.72 | 96.51
2017-04-15 10:30 | 111.15 | 93.64
2017-04-15 11:00 | 105.69 | 86.02
2017-04-15 11:30 | 108.98 | 90.18
2017-04-15 12:00 | 114.95 | 97.78
2017-04-15 12:30 | 120.08 | 103.64
2017-04-15 13:00 | 118.44 | 102.56
2017-04-15 13:30 | 111.79 | 95.09
2017-04-15 14:00 | 116.56 | 101.45
2017-04-15 14:30 | 116.17 | 100.7
2017-04-15 15:00 | 114.41 | 98.08
2017-04-15 15:30 | 105.17 | 87.58
2017-04-15 16:00 | 114.64 | 97.37
2017-04-15 16:30 | 112.75 | 95.63
2017-04-15 17:00 | 117.4 | 101.73
2017-04-15 17:30 | 118.05 | 103.68
2017-04-15 18:00 | 116.72 | 101.29
2017-04-15 18:30 | 107.52 | 90.04
2017-04-15 19:00 | 108.1 | 91.19
2017-04-15 19:30 | 111.52 | 95.26
2017-04-15 20:00 | 109.05 | 92.08
2017-04-15 20:30 | 111.39 | 95.11
2017-04-15 21:00 | 110.91 | 94.2
2017-04-15 21:30 | 108.88 | 92.8
2017-04-15 22:00 | 106.99 | 89.7
2017-04-15 22:30 | 108.79 | 89.76
2017-04-15 23:00 | 110.47 | 93.84
2017-04-15 23:30 | 109.52 | 92.3
2017-04-16 | 111.96 | 94.35
2017-04-16 00:30 | 106.09 | 87.18
2017-04-16 01:00 | 108.55 | 89.15
2017-04-16 01:30 | 108.8 | 88.08
2017-04-16 02:00 | 109.34 | 90.11
2017-04-16 02:30 | 108.7 | 88.95
2017-04-16 03:00 | 105.39 | 85.4
2017-04-16 03:30 | 103.42 | 81.66
2017-04-16 04:00 | 104.08 | 83.13
2017-04-16 04:30 | 109.97 | 91.24
2017-04-16 05:00 | 102.76 | 80.45
2017-04-16 05:30 | 105.05 | 84.48
2017-04-16 06:00 | 105.59 | 83.93
2017-04-16 06:30 | 100.24 | 73.84
2017-04-16 07:00 | 101.31 | 78.36
2017-04-16 07:30 | 97.04 | 71.97
2017-04-16 08:00 | 99.59 | 76.96
2017-04-16 08:30 | 99.63 | 80.24
2017-04-16 09:00 | 100.18 | 80.74
2017-04-16 09:30 | 96.36 | 77.94
2017-04-16 10:00 | 93.85 | 74.43
2017-04-16 10:30 | 98.99 | 80.57
2017-04-16 11:00 | 99.33 | 79.97
2017-04-16 11:30 | 97.07 | 73.35
2017-04-16 12:00 | 97.74 | 76.69
2017-04-16 12:30 | 99.8 | 80.92
2017-04-16 13:00 | 105.91 | 89.3
2017-04-16 13:30 | 104.2 | 86.23
2017-04-16 14:00 | 106.86 | 90.31
2017-04-16 14:30 | 98.3 | 80.59
2017-04-16 15:00 | 100.97 | 81.59
2017-04-16 15:30 | 99.36 | 78.17
2017-04-16 16:00 | 106.3 | 89.19
2017-04-16 16:30 | 105.18 | 89.35
2017-04-16 17:00 | 100.52 | 82.63
2017-04-16 17:30 | 102.51 | 84.53
2017-04-16 18:00 | 106.35 | 89.3
2017-04-16 18:30 | 95.48 | 75.15
2017-04-16 19:00 | 100.05 | 82.16
2017-04-16 19:30 | 101.86 | 84.28
2017-04-16 20:00 | 103.98 | 85.08
2017-04-16 20:30 | 105.16 | 87.1
2017-04-16 21:00 | 101.42 | 82.16
2017-04-16 21:30 | 98.48 | 78.24
2017-04-16 22:00 | 103.19 | 85.85
2017-04-16 22:30 | 101.76 | 82.11
2017-04-16 23:00 | 103.19 | 83.84
2017-04-16 23:30 | 109.04 | 89.33
2017-04-17 | 113 | 95.9
2017-04-17 00:30 | 109.21 | 90.18
2017-04-17 01:00 | 110.92 | 93.08
2017-04-17 01:30 | 109.09 | 89.5
2017-04-17 02:00 | 106.78 | 86.37
2017-04-17 02:30 | 109.95 | 90.89
2017-04-17 03:00 | 107.29 | 87.83
2017-04-17 03:30 | 105.65 | 86.08
2017-04-17 04:00 | 102.32 | 81.14
2017-04-17 04:30 | 101.83 | 79.88
2017-04-17 05:00 | 103.2 | 83.25
2017-04-17 05:30 | 98.54 | 76.5
2017-04-17 06:00 | 106.48 | 86.72
2017-04-17 06:30 | 101.27 | 77.49
2017-04-17 07:00 | 106.37 | 85.39
2017-04-17 07:30 | 101.53 | 79.26
2017-04-17 08:00 | 101.06 | 79.53
2017-04-17 08:30 | 103.24 | 83.55
2017-04-17 09:00 | 103.98 | 85.16
2017-04-17 09:30 | 103.76 | 85.8
2017-04-17 10:00 | 100.9 | 82.4
2017-04-17 10:30 | 99.19 | 79.54
2017-04-17 11:00 | 103.11 | 84.1
2017-04-17 11:30 | 107.54 | 88.44
2017-04-17 12:00 | 102.09 | 81.34
2017-04-17 12:30 | 101.29 | 81.75
2017-04-17 13:00 | 100.36 | 80.95
2017-04-17 13:30 | 102.9 | 84.21
2017-04-17 14:00 | 101.85 | 82.95
2017-04-17 14:30 | 102.87 | 85.35
2017-04-17 15:00 | 100.66 | 82.82
2017-04-17 15:30 | 106.16 | 88.98
2017-04-17 16:00 | 107.8 | 91.61
2017-04-17 16:30 | 108.64 | 92.53
2017-04-17 17:00 | 111.32 | 94.03
2017-04-17 17:30 | 114.62 | 98.47
2017-04-17 18:00 | 117.62 | 102.77
2017-04-17 18:30 | 109.73 | 92.67
2017-04-17 19:00 | 113.27 | 97.61
2017-04-17 19:30 | 112.55 | 95.76
2017-04-17 20:00 | 113.94 | 97.95
2017-04-17 20:30 | 109.92 | 93.32
2017-04-17 21:00 | 110.41 | 95.53
2017-04-17 21:30 | 117.22 | 100.79
2017-04-17 22:00 | 115.37 | 98.1
2017-04-17 22:30 | 112.67 | 94.23
2017-04-17 23:00 | 106.23 | 87.68
2017-04-17 23:30 | 107.25 | 87.21
2017-04-18 | 111.54 | 92.91
2017-04-18 00:30 | 108.22 | 87.19
2017-04-18 01:00 | 108.78 | 87.89
2017-04-18 01:30 | 106.31 | 84.47
2017-04-18 02:00 | 108.7 | 86.04
2017-04-18 02:30 | 109.27 | 87.77
2017-04-18 03:00 | 104.2 | 81.75
2017-04-18 03:30 | 106.48 | 85.46
2017-04-18 04:00 | 105.6 | 84.1
2017-04-18 04:30 | 107.23 | 88.18
2017-04-18 05:00 | 103.17 | 81.34
2017-04-18 05:30 | 106.35 | 87.09
2017-04-18 06:00 | 109.87 | 93.16
2017-04-18 06:30 | 108.13 | 89.42
2017-04-18 07:00 | 108.6 | 89.91
2017-04-18 07:30 | 107.62 | 90.27
2017-04-18 08:00 | 103.49 | 83.99
2017-04-18 08:30 | 105.76 | 85.66
2017-04-18 09:00 | 111.99 | 93.83
2017-04-18 09:30 | 108.54 | 88.85
2017-04-18 10:00 | 112.81 | 94.34
2017-04-18 10:30 | 112.95 | 95.02
2017-04-18 11:00 | 106.46 | 86.73
2017-04-18 11:30 | 105.19 | 84.57
2017-04-18 12:00 | 100.6 | 78.88
2017-04-18 12:30 | 102.53 | 82.74
2017-04-18 13:00 | 102.41 | 83.53
2017-04-18 13:30 | 101.76 | 80.88
2017-04-18 14:00 | 105.65 | 86.85
2017-04-18 14:30 | 106.78 | 88.98
2017-04-18 15:00 | 111.72 | 94.72
2017-04-18 15:30 | 105.9 | 90.3
2017-04-18 16:00 | 103.41 | 85.82
2017-04-18 16:30 | 108.96 | 93.84
2017-04-18 17:00 | 110.58 | 95.26
2017-04-18 17:30 | 114.57 | 100.61
2017-04-18 18:00 | 112.58 | 99.03
2017-04-18 18:30 | 106.83 | 91.56
2017-04-18 19:00 | 104.3 | 89.23
2017-04-18 19:30 | 109.99 | 96.89
2017-04-18 20:00 | 105.53 | 92.23
2017-04-18 20:30 | 110.24 | 96.48
2017-04-18 21:00 | 106.7 | 90.25
2017-04-18 21:30 | 110.43 | 92.86
2017-04-18 22:00 | 110.95 | 93.32
2017-04-18 22:30 | 106.6 | 87.84
2017-04-18 23:00 | 105.08 | 85.28
2017-04-18 23:30 | 106.6 | 88.73
2017-04-19 | 110.65 | 94.62
2017-04-19 00:30 | 111.62 | 95.1
2017-04-19 01:00 | 110.18 | 91.76
2017-04-19 01:30 | 109.57 | 92.12
2017-04-19 02:00 | 105.76 | 86.1
2017-04-19 02:30 | 101.51 | 83.11
2017-04-19 03:00 | 99.43 | 79.4
2017-04-19 03:30 | 95.94 | 75.71
2017-04-19 04:00 | 101.32 | 84.16
2017-04-19 04:30 | 101.47 | 82.68
2017-04-19 05:00 | 97.07 | 77.37
2017-04-19 05:30 | 92.18 | 68.73
2017-04-19 06:00 | 102.11 | 83.94
2017-04-19 06:30 | 93.61 | 69.3
2017-04-19 07:00 | 93.04 | 70.2
2017-04-19 07:30 | 100.5 | 81.5
2017-04-19 08:00 | 101.39 | 82.14
2017-04-19 08:30 | 96.2 | 75.17
2017-04-19 09:00 | 95.83 | 73.46
2017-04-19 09:30 | 101.69 | 81.85
2017-04-19 10:00 | 99.69 | 78.85
2017-04-19 10:30 | 99.47 | 79.51
2017-04-19 11:00 | 95.35 | 73.8
2017-04-19 11:30 | 92.25 | 70.17
2017-04-19 12:00 | 95.08 | 75.76
2017-04-19 12:30 | 93.9 | 74.26
2017-04-19 13:00 | 90.63 | 69.84
2017-04-19 13:30 | 96.98 | 78.81
2017-04-19 14:00 | 102.29 | 85.33
2017-04-19 14:30 | 100.8 | 83.02
2017-04-19 15:00 | 99.29 | 81.72
2017-04-19 15:30 | 98.58 | 79.34
2017-04-19 16:00 | 98.84 | 79.31
2017-04-19 16:30 | 104.56 | 86.04
2017-04-19 17:00 | 97.29 | 76.43
2017-04-19 17:30 | 101.76 | 82.75
2017-04-19 18:00 | 104.64 | 87.6
2017-04-19 18:30 | 101.42 | 82.04
2017-04-19 19:00 | 100.17 | 79.53
2017-04-19 19:30 | 105.68 | 87.5
2017-04-19 20:00 | 109.01 | 91.84
2017-04-19 20:30 | 110.45 | 93.16
2017-04-19 21:00 | 113.92 | 97.45
2017-04-19 21:30 | 105.38 | 84.24
2017-04-19 22:00 | 108.6 | 89.13
2017-04-19 22:30 | 109.37 | 89.72
2017-04-19 23:00 | 108.47 | 86.6
2017-04-19 23:30 | 108.74 | 87.3
2017-04-20 | 110.66 | 89.96
2017-04-20 00:30 | 103.76 | 81.87
2017-04-20 01:00 | 103.79 | 81.66
2017-04-20 01:30 | 104.45 | 81.33
2017-04-20 02:00 | 103.81 | 79.1
2017-04-20 02:30 | 104.34 | 79.06
2017-04-20 03:00 | 101.21 | 75.28
2017-04-20 03:30 | 101.92 | 76.63
2017-04-20 04:00 | 103.32 | 78.69
2017-04-20 04:30 | 104.22 | 79.6
2017-04-20 05:00 | 105.77 | 83.94
2017-04-20 05:30 | 102.39 | 78.81
2017-04-20 06:00 | 104.92 | 84.21
2017-04-20 06:30 | 99.35 | 74.78
2017-04-20 07:00 | 99.97 | 75.6
2017-04-20 07:30 | 106.33 | 85.76
2017-04-20 08:00 | 103.16 | 80.83
2017-04-20 08:30 | 105.42 | 83.38
2017-04-20 09:00 | 105.15 | 82.21
2017-04-20 09:30 | 108.65 | 86.68
2017-04-20 10:00 | 108.67 | 86.28
2017-04-20 10:30 | 106.31 | 84.58
2017-04-20 11:00 | 104.77 | 81.95
2017-04-20 11:30 | 102.3 | 77.51
2017-04-20 12:00 | 98.8 | 73.91
2017-04-20 12:30 | 103.8 | 82.68
2017-04-20 13:00 | 100.76 | 78.24
2017-04-20 13:30 | 104.34 | 84.09
2017-04-20 14:00 | 105.95 | 85.12
2017-04-20 14:30 | 102.8 | 80.54
2017-04-20 15:00 | 104.93 | 80.54
2017-04-20 15:30 | 102.52 | 77.56
2017-04-20 16:00 | 100.63 | 74.84
2017-04-20 16:30 | 106.47 | 84.27
2017-04-20 17:00 | 104.4 | 82.78
2017-04-20 17:30 | 104.37 | 82.33
2017-04-20 18:00 | 107.39 | 87.05
2017-04-20 18:30 | 106.67 | 85.91
2017-04-20 19:00 | 109.27 | 89.66
2017-04-20 19:30 | 105.51 | 87.42
2017-04-20 20:00 | 105.15 | 86.84
2017-04-20 20:30 | 107.45 | 89.19
2017-04-20 21:00 | 111.45 | 92.45
2017-04-20 21:30 | 112.96 | 93.44
2017-04-20 22:00 | 112.37 | 93.52
2017-04-20 22:30 | 115.52 | 97.22
2017-04-20 23:00 | 110.61 | 86.92
2017-04-20 23:30 | 115.58 | 93.3
2017-04-21 | 115.59 | 93.69
2017-04-21 00:30 | 118.33 | 99.33
2017-04-21 01:00 | 121.24 | 102.18
2017-04-21 01:30 | 119.45 | 99.69
2017-04-21 02:00 | 118.12 | 98.42
2017-04-21 02:30 | 117.66 | 98.25
2017-04-21 03:00 | 116.14 | 95.61
2017-04-21 03:30 | 118.53 | 98.5
2017-04-21 04:00 | 126.93 | 108.86
2017-04-21 04:30 | 124.7 | 105.44
2017-04-21 05:00 | 126.05 | 108.67
2017-04-21 05:30 | 124.48 | 105.82
2017-04-21 06:00 | 123.61 | 106.42
2017-04-21 06:30 | 117.26 | 97.83
2017-04-21 07:00 | 104.28 | 82.17
2017-04-21 07:30 | 110.71 | 91.99
2017-04-21 08:00 | 109.59 | 90.35
2017-04-21 08:30 | 107.82 | 89.31
2017-04-21 09:00 | 102.61 | 81.92
2017-04-21 09:30 | 104.91 | 85.2
2017-04-21 10:00 | 108.7 | 89.54
2017-04-21 10:30 | 113.99 | 97.07
2017-04-21 11:00 | 110.02 | 91.53
2017-04-21 11:30 | 108.62 | 89.16
2017-04-21 12:00 | 115.24 | 97.81
2017-04-21 12:30 | 107.38 | 87.09
2017-04-21 13:00 | 102.82 | 83.19
2017-04-21 13:30 | 108.93 | 90.53
2017-04-21 14:00 | 107.87 | 88.19
2017-04-21 14:30 | 105.88 | 86.01
2017-04-21 15:00 | 115.29 | 96.5
2017-04-21 15:30 | 116.53 | 97.31
2017-04-21 16:00 | 114.91 | 94.9
2017-04-21 16:30 | 110.86 | 89.63
2017-04-21 17:00 | 109.8 | 89.15
2017-04-21 17:30 | 111.43 | 91.81
2017-04-21 18:00 | 116.12 | 97.41
2017-04-21 18:30 | 115.72 | 97.02
2017-04-21 19:00 | 118.82 | 100.96
2017-04-21 19:30 | 115.64 | 97.35
2017-04-21 20:00 | 122.53 | 106.84
2017-04-21 20:30 | 122.17 | 104.81
2017-04-21 21:00 | 120.3 | 101.94
2017-04-21 21:30 | 116.98 | 97.24
2017-04-21 22:00 | 119.51 | 101.88
2017-04-21 22:30 | 120.65 | 104.6
2017-04-21 23:00 | 120.47 | 102.97
2017-04-21 23:30 | 122.44 | 104.33
2017-04-22 | 118.88 | 99.81
2017-04-22 00:30 | 116.66 | 97.82
2017-04-22 01:00 | 121.08 | 104.04
2017-04-22 01:30 | 115.19 | 95.93
2017-04-22 02:00 | 114.71 | 94.88
2017-04-22 02:30 | 116.34 | 97.51
2017-04-22 03:00 | 117.94 | 98.99
2017-04-22 03:30 | 119.55 | 101.3
2017-04-22 04:00 | 121.13 | 103.1
2017-04-22 04:30 | 119.99 | 101.82
2017-04-22 05:00 | 122.82 | 106.52
2017-04-22 05:30 | 124.7 | 109.23
2017-04-22 06:00 | 117.5 | 100.86
2017-04-22 06:30 | 109.94 | 88.35
2017-04-22 07:00 | 114.22 | 96.04
2017-04-22 07:30 | 119.83 | 104.08
2017-04-22 08:00 | 122.21 | 106.35
2017-04-22 08:30 | 120.44 | 102.23
2017-04-22 09:00 | 124.34 | 107.24
2017-04-22 09:30 | 128.9 | 112.55
2017-04-22 10:00 | 118.74 | 99.43
2017-04-22 10:30 | 119.92 | 101.86
2017-04-22 11:00 | 121.94 | 104.32
2017-04-22 11:30 | 118.94 | 102.11
2017-04-22 12:00 | 115.12 | 96.25
2017-04-22 12:30 | 116.81 | 98.45
2017-04-22 13:00 | 123.47 | 106.99
2017-04-22 13:30 | 123.78 | 107.48
2017-04-22 14:00 | 124.77 | 108.52
2017-04-22 14:30 | 122.58 | 105.87
2017-04-22 15:00 | 122.1 | 104.3
2017-04-22 15:30 | 123.19 | 106.41
2017-04-22 16:00 | 114.93 | 98.83
2017-04-22 16:30 | 116.48 | 99.13
2017-04-22 17:00 | 119.75 | 101.66
2017-04-22 17:30 | 125.29 | 109.67
2017-04-22 18:00 | 123.85 | 109.16
2017-04-22 18:30 | 122.25 | 105.66
2017-04-22 19:00 | 119.25 | 102.15
2017-04-22 19:30 | 126.52 | 111.39
2017-04-22 20:00 | 130.56 | 117.38
2017-04-22 20:30 | 127.51 | 111.6
2017-04-22 21:00 | 127.53 | 111.7
2017-04-22 21:30 | 124.62 | 108.09
2017-04-22 22:00 | 127.43 | 111.46
2017-04-22 22:30 | 122.76 | 104.41
2017-04-22 23:00 | 119.75 | 101.65
2017-04-22 23:30 | 117.25 | 96.45
2017-04-23 | 119.53 | 101.02
2017-04-23 00:30 | 123.19 | 105.93
2017-04-23 01:00 | 122.01 | 103.29
2017-04-23 01:30 | 121.34 | 102.7
2017-04-23 02:00 | 120.7 | 102.92
2017-04-23 02:30 | 123.78 | 107.08
2017-04-23 03:00 | 124.67 | 107.1
2017-04-23 03:30 | 121.59 | 102.41
2017-04-23 04:00 | 124.73 | 107.61
2017-04-23 04:30 | 122.39 | 104.09
2017-04-23 05:00 | 120.18 | 101.86
2017-04-23 05:30 | 114.71 | 94.81
2017-04-23 06:00 | 114.31 | 95.24
2017-04-23 06:30 | 110.66 | 86.89
2017-04-23 07:00 | 118.49 | 99.07
2017-04-23 07:30 | 120.92 | 102.95
2017-04-23 08:00 | 126.5 | 110.82
2017-04-23 08:30 | 120.89 | 103.89
2017-04-23 09:00 | 119.62 | 100.7
2017-04-23 09:30 | 119.95 | 103.93
2017-04-23 10:00 | 112.62 | 94.96
2017-04-23 10:30 | 120.09 | 103.72
2017-04-23 11:00 | 114.23 | 97.3
2017-04-23 11:30 | 113.24 | 94.19
2017-04-23 12:00 | 122.68 | 107.1
2017-04-23 12:30 | 118.71 | 102.27
2017-04-23 13:00 | 121.08 | 104.87
2017-04-23 13:30 | 121.9 | 105.97
2017-04-23 14:00 | 118.91 | 101.24
2017-04-23 14:30 | 123.2 | 106.91
2017-04-23 15:00 | 121.25 | 103.96
2017-04-23 15:30 | 122.44 | 106.11
2017-04-23 16:00 | 119.01 | 100.92
2017-04-23 16:30 | 120.25 | 102.05
2017-04-23 17:00 | 123.45 | 106.68
2017-04-23 17:30 | 114.2 | 95.47
2017-04-23 18:00 | 116.12 | 98.5
2017-04-23 18:30 | 110.44 | 89.75
2017-04-23 19:00 | 117.52 | 99.77
2017-04-23 19:30 | 121.38 | 105.88
2017-04-23 20:00 | 116.46 | 99.67
2017-04-23 20:30 | 122.59 | 106.37
2017-04-23 21:00 | 122.47 | 105.29
2017-04-23 21:30 | 118.59 | 101.47
2017-04-23 22:00 | 116.23 | 99.69
2017-04-23 22:30 | 118.36 | 101.85
2017-04-23 23:00 | 121.98 | 104.35
2017-04-23 23:30 | 124.23 | 106.52
2017-04-24 | 126.33 | 109.08
2017-04-24 00:30 | 126.56 | 109.47
2017-04-24 01:00 | 120.07 | 101.74
2017-04-24 01:30 | 117.78 | 98.46
2017-04-24 02:00 | 117.29 | 97.35
2017-04-24 02:30 | 125.63 | 108.36
2017-04-24 03:00 | 121.85 | 102.88
2017-04-24 03:30 | 118.86 | 98.75
2017-04-24 04:00 | 122.69 | 103.01
2017-04-24 04:30 | 123.41 | 105.06
2017-04-24 05:00 | 121.77 | 103.7
2017-04-24 05:30 | 123.88 | 105.45
2017-04-24 06:00 | 119.18 | 101.68
2017-04-24 06:30 | 116.03 | 95.97
2017-04-24 07:00 | 115.44 | 98.03
2017-04-24 07:30 | 121.03 | 103.99
2017-04-24 08:00 | 119.26 | 102.75
2017-04-24 08:30 | 117.41 | 101.69
2017-04-24 09:00 | 119.34 | 102.94
2017-04-24 09:30 | 120.56 | 104.88
2017-04-24 10:00 | 120.64 | 104.57
2017-04-24 10:30 | 128.08 | 112.62
2017-04-24 11:00 | 123.86 | 106.01
2017-04-24 11:30 | 122 | 103.27
2017-04-24 12:00 | 124.71 | 107.36
2017-04-24 12:30 | 123.21 | 105.61
2017-04-24 13:00 | 120.49 | 103.45
2017-04-24 13:30 | 124.53 | 107.87
2017-04-24 14:00 | 118.91 | 101.41
2017-04-24 14:30 | 119.66 | 102.51
2017-04-24 15:00 | 125.12 | 109.08
2017-04-24 15:30 | 125.74 | 109.84
2017-04-24 16:00 | 132.99 | 118.21
2017-04-24 16:30 | 128.98 | 114.21
2017-04-24 17:00 | 124.68 | 109.13
2017-04-24 17:30 | 124.2 | 108.11
2017-04-24 18:00 | 126.96 | 113.22
2017-04-24 18:30 | 131.88 | 117.75
2017-04-24 19:00 | 134.92 | 121.29
2017-04-24 19:30 | 132.52 | 118.48
2017-04-24 20:00 | 126.42 | 111.81
2017-04-24 20:30 | 128.17 | 113.34
2017-04-24 21:00 | 127.51 | 112.28
2017-04-24 21:30 | 121.63 | 105.64
2017-04-24 22:00 | 120.58 | 103.12
2017-04-24 22:30 | 125.05 | 108.29
2017-04-24 23:00 | 123.99 | 106.36
2017-04-24 23:30 | 127.73 | 110.61
2017-04-25 | 115.9 | 96.81
2017-04-25 00:30 | 115.74 | 95.44
2017-04-25 01:00 | 122.13 | 103.67
2017-04-25 01:30 | 123.41 | 105.53
2017-04-25 02:00 | 122.79 | 102.42
2017-04-25 02:30 | 125.39 | 106.47
2017-04-25 03:00 | 123.56 | 103.97
2017-04-25 03:30 | 120.96 | 103.29
2017-04-25 04:00 | 120.95 | 102.14
2017-04-25 04:30 | 118.67 | 98.3
2017-04-25 05:00 | 125.8 | 108.65
2017-04-25 05:30 | 125.36 | 107.11
2017-04-25 06:00 | 123.33 | 106.77
2017-04-25 06:30 | 112.36 | 90.32
2017-04-25 07:00 | 111.49 | 88.87
2017-04-25 07:30 | 116.52 | 97.21
2017-04-25 08:00 | 113.44 | 94.84
2017-04-25 08:30 | 113.53 | 93.42
2017-04-25 09:00 | 113.29 | 92.68
2017-04-25 09:30 | 113.9 | 95.71
2017-04-25 10:00 | 120.61 | 104.05
2017-04-25 10:30 | 110.89 | 92.47
2017-04-25 11:00 | 111.42 | 90.91
2017-04-25 11:30 | 117.83 | 98.31
2017-04-25 12:00 | 120.31 | 103.33
2017-04-25 12:30 | 123.08 | 106.15
2017-04-25 13:00 | 123.81 | 107
2017-04-25 13:30 | 123.58 | 106.45
2017-04-25 14:00 | 118.66 | 100.49
2017-04-25 14:30 | 116.52 | 96.48
2017-04-25 15:00 | 117.14 | 98.07
2017-04-25 15:30 | 119.12 | 98.89
2017-04-25 16:00 | 118.14 | 96.87
2017-04-25 16:30 | 124.49 | 106
2017-04-25 17:00 | 124.14 | 106.27
2017-04-25 17:30 | 123.64 | 106.44
2017-04-25 18:00 | 122.24 | 105.96
2017-04-25 18:30 | 116.46 | 97.19
2017-04-25 19:00 | 125.75 | 110.75
2017-04-25 19:30 | 127.93 | 113.6
2017-04-25 20:00 | 127.37 | 113.02
2017-04-25 20:30 | 127.26 | 112.64
2017-04-25 21:00 | 123.42 | 106.56
2017-04-25 21:30 | 129.4 | 114.86
2017-04-25 22:00 | 122.06 | 105.95
2017-04-25 22:30 | 124.94 | 108.98
2017-04-25 23:00 | 128.85 | 115.27
2017-04-25 23:30 | 121.09 | 105.35
2017-04-26 | 111.47 | 93.3
2017-04-26 00:30 | 119.84 | 104.62
2017-04-26 01:00 | 120.77 | 104.5
2017-04-26 01:30 | 118.54 | 102.85
2017-04-26 02:00 | 124.53 | 108.63
2017-04-26 02:30 | 126.72 | 111.27
2017-04-26 03:00 | 123 | 105.75
2017-04-26 03:30 | 126.89 | 109.94
2017-04-26 04:00 | 125.28 | 109.49
2017-04-26 04:30 | 123.16 | 105.57
2017-04-26 05:00 | 114.79 | 95.37
2017-04-26 05:30 | 114.52 | 94.86
2017-04-26 06:00 | 109.19 | 88.58
2017-04-26 06:30 | 105.31 | 81.6
2017-04-26 07:00 | 107.98 | 85.91
2017-04-26 07:30 | 107.54 | 86.92
2017-04-26 08:00 | 107.41 | 85.54
2017-04-26 08:30 | 111.19 | 91.06
2017-04-26 09:00 | 107.32 | 86.62
2017-04-26 09:30 | 104.64 | 81.8
2017-04-26 10:00 | 101.79 | 78.52
2017-04-26 10:30 | 106.02 | 84.39
2017-04-26 11:00 | 103.58 | 79.74
2017-04-26 11:30 | 110.95 | 85.46
2017-04-26 12:00 | 109.89 | 82.32
2017-04-26 12:30 | 112.22 | 87.07
2017-04-26 13:00 | 109.66 | 84.48
2017-04-26 13:30 | 110.78 | 88.22
2017-04-26 14:00 | 114.62 | 96.24
2017-04-26 14:30 | 111.19 | 89.75
2017-04-26 15:00 | 107.55 | 84.2
2017-04-26 15:30 | 106.35 | 82.78
2017-04-26 16:00 | 104.31 | 81.7
2017-04-26 16:30 | 105.73 | 83.33
2017-04-26 17:00 | 108.29 | 85.11
2017-04-26 17:30 | 108.29 | 86.01
2017-04-26 18:00 | 108.5 | 87.09
2017-04-26 18:30 | 106.96 | 83.43
2017-04-26 19:00 | 110.41 | 88.79
2017-04-26 19:30 | 115.46 | 96.8
2017-04-26 20:00 | 119.54 | 102.17
2017-04-26 20:30 | 118 | 99.6
2017-04-26 21:00 | 113.07 | 95.74
2017-04-26 21:30 | 111.64 | 91.49
2017-04-26 22:00 | 116.41 | 97.99
2017-04-26 22:30 | 121.65 | 104.93
2017-04-26 23:00 | 121.01 | 104.97
2017-04-26 23:30 | 117.93 | 98.61
2017-04-27 | 116.93 | 98
2017-04-27 00:30 | 123.35 | 106.66
2017-04-27 01:00 | 126.68 | 110.43
2017-04-27 01:30 | 125.69 | 108.93
2017-04-27 02:00 | 129.9 | 114.81
2017-04-27 02:30 | 123.38 | 104.44
2017-04-27 03:00 | 115.45 | 95.03
2017-04-27 03:30 | 116.85 | 97.12
2017-04-27 04:00 | 121.16 | 102.32
2017-04-27 04:30 | 124.98 | 107.48
2017-04-27 05:00 | 123.97 | 105.59
2017-04-27 05:30 | 121.47 | 103.69
2017-04-27 06:00 | 127.31 | 107.78
2017-04-27 06:30 | 115.9 | 94.4
2017-04-27 07:00 | 114.92 | 93.86
2017-04-27 07:30 | 119.71 | 101.87
2017-04-27 08:00 | 121.59 | 103.46
2017-04-27 08:30 | 117.31 | 98.42
2017-04-27 09:00 | 119.87 | 100.48
2017-04-27 09:30 | 117.03 | 96.15
2017-04-27 10:00 | 116.12 | 93.99
2017-04-27 10:30 | 110.21 | 88.69
2017-04-27 11:00 | 110.08 | 87.39
2017-04-27 11:30 | 110.42 | 89.49
2017-04-27 12:00 | 111.08 | 89.07
2017-04-27 12:30 | 115.53 | 95.19
2017-04-27 13:00 | 120.34 | 99.58
2017-04-27 13:30 | 123.18 | 103.83
2017-04-27 14:00 | 117.96 | 97.82
2017-04-27 14:30 | 119.64 | 100.27
2017-04-27 15:00 | 124.83 | 106.94
2017-04-27 15:30 | 123.93 | 105.91
2017-04-27 16:00 | 123.01 | 105.03
2017-04-27 16:30 | 119.95 | 100.08
2017-04-27 17:00 | 120.66 | 101.41
2017-04-27 17:30 | 125.05 | 107.3
2017-04-27 18:00 | 121.56 | 102.47
2017-04-27 18:30 | 117.8 | 97.24
2017-04-27 19:00 | 125.68 | 109.01
2017-04-27 19:30 | 129 | 115.42
2017-04-27 20:00 | 129.63 | 113.26
2017-04-27 20:30 | 125.61 | 109.33
2017-04-27 21:00 | 117.93 | 98.19
2017-04-27 21:30 | 118.27 | 100.03
2017-04-27 22:00 | 125 | 109.07
2017-04-27 22:30 | 124.32 | 107.98
2017-04-27 23:00 | 122.59 | 104.51
2017-04-27 23:30 | 125.69 | 106.83
2017-04-28 | 123.36 | 104.52
2017-04-28 00:30 | 125.07 | 106.97
2017-04-28 01:00 | 124.26 | 107.33
2017-04-28 01:30 | 121.09 | 103.07
2017-04-28 02:00 | 127.43 | 111.11
2017-04-28 02:30 | 119.45 | 101.63
2017-04-28 03:00 | 115.28 | 95.89
2017-04-28 03:30 | 113.78 | 94.17
2017-04-28 04:00 | 115.68 | 94.75
2017-04-28 04:30 | 120.2 | 99.92
2017-04-28 05:00 | 111.51 | 89.57
2017-04-28 05:30 | 117.33 | 99.85
2017-04-28 06:00 | 119.34 | 103.04
2017-04-28 06:30 | 109.53 | 88.42
2017-04-28 07:00 | 112.44 | 93.81
2017-04-28 07:30 | 128.7 | 113.56
2017-04-28 08:00 | 118.89 | 102.91
2017-04-28 08:30 | 121.62 | 104.6
2017-04-28 09:00 | 117.97 | 98.04
2017-04-28 09:30 | 112.97 | 93.17
2017-04-28 10:00 | 118.89 | 99.45
2017-04-28 10:30 | 121.7 | 103.18
2017-04-28 11:00 | 123.38 | 105.88
2017-04-28 11:30 | 121.79 | 101.91
2017-04-28 12:00 | 119.55 | 99.86
2017-04-28 12:30 | 112.82 | 92.3
2017-04-28 13:00 | 120 | 100.23
2017-04-28 13:30 | 114.26 | 95.11
2017-04-28 14:00 | 112.46 | 93.15
2017-04-28 14:30 | 116.45 | 98.31
2017-04-28 15:00 | 113.9 | 96.2
2017-04-28 15:30 | 111.62 | 94.65
2017-04-28 16:00 | 104.88 | 88.55
2017-04-28 16:30 | 107.97 | 89.37
2017-04-28 17:00 | 108.79 | 90.97
2017-04-28 17:30 | 111.31 | 93.68
2017-04-28 18:00 | 110.94 | 95.42
2017-04-28 18:30 | 108.47 | 91.91
2017-04-28 19:00 | 112.02 | 96.29
2017-04-28 19:30 | 112.39 | 97.42
2017-04-28 20:00 | 111.97 | 95.56
2017-04-28 20:30 | 117.39 | 101.63
2017-04-28 21:00 | 113.16 | 97.53
2017-04-28 21:30 | 111.64 | 95.75
2017-04-28 22:00 | 117.31 | 102.67
2017-04-28 22:30 | 115.65 | 100.13
2017-04-28 23:00 | 116.07 | 100.26
2017-04-28 23:30 | 115.24 | 98.59
2017-04-29 | 115.67 | 99.18
2017-04-29 00:30 | 121.81 | 106.37
2017-04-29 01:00 | 110.93 | 91.16
2017-04-29 01:30 | 115.51 | 98.26
2017-04-29 02:00 | 123.69 | 108.62
2017-04-29 02:30 | 121.78 | 105.9
2017-04-29 03:00 | 118.77 | 102
2017-04-29 03:30 | 112.91 | 94.16
2017-04-29 04:00 | 114.9 | 97.52
2017-04-29 04:30 | 114.11 | 97.02
2017-04-29 05:00 | 111.36 | 94.79
2017-04-29 05:30 | 116.59 | 100.62
2017-04-29 06:00 | 112.35 | 95.78
2017-04-29 06:30 | 106.87 | 87.71
2017-04-29 07:00 | 109.31 | 92.84
2017-04-29 07:30 | 113.82 | 97.64
2017-04-29 08:00 | 122.12 | 107.51
2017-04-29 08:30 | 119.32 | 102.94
2017-04-29 09:00 | 122.05 | 102.5
2017-04-29 09:30 | 127.19 | 105.09
2017-04-29 10:00 | 124.19 | 100.81
2017-04-29 10:30 | 121.56 | 97.34
2017-04-29 11:00 | 121.25 | 97.67
2017-04-29 11:30 | 122.28 | 99.86
2017-04-29 12:00 | 119.22 | 100.42
2017-04-29 12:30 | 113.2 | 95.06
2017-04-29 13:00 | 113.88 | 95.36
2017-04-29 13:30 | 111.47 | 92.51
2017-04-29 14:00 | 114.15 | 96.54
2017-04-29 14:30 | 114.37 | 96.95
2017-04-29 15:00 | 112.66 | 94.6
2017-04-29 15:30 | 116.48 | 99.57
2017-04-29 16:00 | 114.3 | 97.74
2017-04-29 16:30 | 116.01 | 99.72
2017-04-29 17:00 | 115 | 98.53
2017-04-29 17:30 | 114.95 | 99.13
2017-04-29 18:00 | 116.87 | 100.38
2017-04-29 18:30 | 111.48 | 94.75
2017-04-29 19:00 | 116.84 | 100.82
2017-04-29 19:30 | 119.75 | 104.43
2017-04-29 20:00 | 121.44 | 107.17
2017-04-29 20:30 | 124.12 | 109.92
2017-04-29 21:00 | 126.7 | 112.13
2017-04-29 21:30 | 125.27 | 110.06
2017-04-29 22:00 | 120.16 | 103.71
2017-04-29 22:30 | 122.56 | 107.55
2017-04-29 23:00 | 114.1 | 97.16
2017-04-29 23:30 | 112.35 | 93.23
2017-04-30 | 112.99 | 94.8
2017-04-30 00:30 | 115.16 | 97.15
2017-04-30 01:00 | 112.23 | 91.54
2017-04-30 01:30 | 112.13 | 92.86
2017-04-30 02:00 | 115.36 | 96.8
2017-04-30 02:30 | 116.44 | 98.42
2017-04-30 03:00 | 117.85 | 100.69
2017-04-30 03:30 | 116.57 | 98.67
2017-04-30 04:00 | 115.12 | 96.9
2017-04-30 04:30 | 113.65 | 94.82
2017-04-30 05:00 | 111.39 | 91.89
2017-04-30 05:30 | 110.85 | 90.56
2017-04-30 06:00 | 113.85 | 94.17
2017-04-30 06:30 | 107.61 | 86.82
2017-04-30 07:00 | 104.09 | 82.34
2017-04-30 07:30 | 106.96 | 85.09
2017-04-30 08:00 | 112.11 | 92.84
2017-04-30 08:30 | 116.05 | 98.01
2017-04-30 09:00 | 117.94 | 101.03
2017-04-30 09:30 | 114.43 | 97.66
2017-04-30 10:00 | 107.86 | 89.06
2017-04-30 10:30 | 110.39 | 92.32
2017-04-30 11:00 | 109.53 | 89.97
2017-04-30 11:30 | 106.32 | 86.46
2017-04-30 12:00 | 107.28 | 87.21
2017-04-30 12:30 | 108.46 | 89.09
2017-04-30 13:00 | 108.61 | 89.52
2017-04-30 13:30 | 111.42 | 92.4
2017-04-30 14:00 | 118.56 | 101.41
2017-04-30 14:30 | 122.39 | 105.57
2017-04-30 15:00 | 118.5 | 102.18
2017-04-30 15:30 | 111.11 | 92.48
2017-04-30 16:00 | 110.25 | 92.4
2017-04-30 16:30 | 112.96 | 97.44
2017-04-30 17:00 | 108.95 | 92.65
2017-04-30 17:30 | 113.02 | 97.79
2017-04-30 18:00 | 112.32 | 96.71
2017-04-30 18:30 | 104.07 | 83.85
2017-04-30 19:00 | 108.26 | 87.87
2017-04-30 19:30 | 110.81 | 91.84
2017-04-30 20:00 | 111.29 | 93.13
2017-04-30 20:30 | 114.89 | 97.03
2017-04-30 21:00 | 113.56 | 95.82
2017-04-30 21:30 | 116.43 | 98.45
2017-04-30 22:00 | 121.06 | 104.55
2017-04-30 22:30 | 119.05 | 101.85
2017-04-30 23:00 | 115.03 | 96
2017-04-30 23:30 | 119.73 | 102.6
2017-05-01 | 115.8 | 97.2
2017-05-01 00:30 | 115.84 | 95.66
2017-05-01 01:00 | 116.44 | 98.1
2017-05-01 01:30 | 113.31 | 94.85
2017-05-01 02:00 | 114.6 | 96.82
2017-05-01 02:30 | 117.2 | 99.91
2017-05-01 03:00 | 115.76 | 96.82
2017-05-01 03:30 | 113.52 | 93.18
2017-05-01 04:00 | 115.27 | 97.42
2017-05-01 04:30 | 116.07 | 97.67
2017-05-01 05:00 | 111.39 | 92.25
2017-05-01 05:30 | 112.82 | 93.91
2017-05-01 06:00 | 109.88 | 90.12
2017-05-01 06:30 | 103.98 | 82.59
2017-05-01 07:00 | 108.58 | 88.36
2017-05-01 07:30 | 109.82 | 90.87
2017-05-01 08:00 | 121.58 | 105.75
2017-05-01 08:30 | 117.15 | 100.5
2017-05-01 09:00 | 113.02 | 94.14
2017-05-01 09:30 | 117.3 | 100.56
2017-05-01 10:00 | 116.52 | 99.63
2017-05-01 10:30 | 114.5 | 96.66
2017-05-01 11:00 | 108.64 | 88.28
2017-05-01 11:30 | 112.62 | 94.84
2017-05-01 12:00 | 110.91 | 92.64
2017-05-01 12:30 | 110.62 | 91.94
2017-05-01 13:00 | 114.98 | 98.64
2017-05-01 13:30 | 109.2 | 89.41
2017-05-01 14:00 | 109.36 | 92.48
2017-05-01 14:30 | 111.75 | 95.99
2017-05-01 15:00 | 116.26 | 99.55
2017-05-01 15:30 | 116.77 | 99.53
2017-05-01 16:00 | 116.54 | 99.43
2017-05-01 16:30 | 115.85 | 99.06
2017-05-01 17:00 | 112.38 | 94.78
2017-05-01 17:30 | 114.16 | 97.42
2017-05-01 18:00 | 114.21 | 98.77
2017-05-01 18:30 | 108.17 | 90.46
2017-05-01 19:00 | 110.15 | 94.37
2017-05-01 19:30 | 110.76 | 95.95
2017-05-01 20:00 | 121.36 | 108.05
2017-05-01 20:30 | 120.17 | 106.74
2017-05-01 21:00 | 115.18 | 99.49
2017-05-01 21:30 | 116.14 | 101.1
2017-05-01 22:00 | 113.71 | 98.26
2017-05-01 22:30 | 108.44 | 90.55
2017-05-01 23:00 | 109.45 | 91.09
2017-05-01 23:30 | 116.06 | 98.32
2017-05-02 | 111.17 | 92.91
2017-05-02 00:30 | 113.59 | 97.13
2017-05-02 01:00 | 109.88 | 91.53
2017-05-02 01:30 | 112.8 | 95.3
2017-05-02 02:00 | 110.74 | 92.35
2017-05-02 02:30 | 108.61 | 89.01
2017-05-02 03:00 | 110 | 90.98
2017-05-02 03:30 | 104.01 | 81.94
2017-05-02 04:00 | 107.63 | 87.9
2017-05-02 04:30 | 108.07 | 88.5
2017-05-02 05:00 | 111.05 | 92.53
2017-05-02 05:30 | 106.69 | 87.51
2017-05-02 06:00 | 104.46 | 85.13
2017-05-02 06:30 | 101.82 | 79.39
2017-05-02 07:00 | 108.37 | 89.3
2017-05-02 07:30 | 108.75 | 89.44
2017-05-02 08:00 | 116.91 | 98.96
2017-05-02 08:30 | 113.75 | 95.22
2017-05-02 09:00 | 115.56 | 98.41
2017-05-02 09:30 | 115.34 | 98.01
2017-05-02 10:00 | 113.21 | 94.78
2017-05-02 10:30 | 117.08 | 101.1
2017-05-02 11:00 | 117.16 | 100.43
2017-05-02 11:30 | 110.3 | 91.02
2017-05-02 12:00 | 111.87 | 92.33
2017-05-02 12:30 | 112.93 | 93.2
2017-05-02 13:00 | 116.21 | 98.52
2017-05-02 13:30 | 120.49 | 104.53
2017-05-02 14:00 | 117.44 | 101.42
2017-05-02 14:30 | 124.13 | 109.39
2017-05-02 15:00 | 119.27 | 102.09
2017-05-02 15:30 | 114.11 | 95.7
2017-05-02 16:00 | 117.52 | 100.46
2017-05-02 16:30 | 118.06 | 102.37
2017-05-02 17:00 | 118.94 | 103.24
2017-05-02 17:30 | 114.1 | 97.71
2017-05-02 18:00 | 118.09 | 101.87
2017-05-02 18:30 | 111.22 | 92.54
2017-05-02 19:00 | 115.7 | 98.88
2017-05-02 19:30 | 119.03 | 103.74
2017-05-02 20:00 | 118.05 | 100.97
2017-05-02 20:30 | 118.78 | 101.66
2017-05-02 21:00 | 116.76 | 98.75
2017-05-02 21:30 | 119.09 | 102.42
2017-05-02 22:00 | 122.09 | 105.07
2017-05-02 22:30 | 118.55 | 100.16
2017-05-02 23:00 | 113.96 | 95.58
2017-05-02 23:30 | 115.49 | 96.2
2017-05-03 | 118.07 | 99.89
2017-05-03 00:30 | 119.11 | 101.64
2017-05-03 01:00 | 116.22 | 98.24
2017-05-03 01:30 | 114.54 | 94.84
2017-05-03 02:00 | 118.84 | 101.01
2017-05-03 02:30 | 118.96 | 101.47
2017-05-03 03:00 | 115.52 | 94.69
2017-05-03 03:30 | 115.27 | 95.56
2017-05-03 04:00 | 113.77 | 94.1
2017-05-03 04:30 | 116.61 | 96.91
2017-05-03 05:00 | 115.33 | 95.54
2017-05-03 05:30 | 117.42 | 99.4
2017-05-03 06:00 | 113.26 | 94.62
2017-05-03 06:30 | 104.53 | 79.6
2017-05-03 07:00 | 112.43 | 92.28
2017-05-03 07:30 | 117.44 | 97.65
2017-05-03 08:00 | 113.52 | 93.39
2017-05-03 08:30 | 106.38 | 85.44
2017-05-03 09:00 | 108.73 | 87.22
2017-05-03 09:30 | 105.41 | 82.7
2017-05-03 10:00 | 99.94 | 77.27
2017-05-03 10:30 | 104.66 | 83.45
2017-05-03 11:00 | 107.29 | 84.54
2017-05-03 11:30 | 99.8 | 76.65
2017-05-03 12:00 | 101.38 | 78.08
2017-05-03 12:30 | 103.75 | 80.95
2017-05-03 13:00 | 101.3 | 79.2
2017-05-03 13:30 | 104.75 | 82.94
2017-05-03 14:00 | 109.68 | 90.51
2017-05-03 14:30 | 112.66 | 95.96
2017-05-03 15:00 | 111.02 | 93.93
2017-05-03 15:30 | 112.44 | 96.08
2017-05-03 16:00 | 115.69 | 98.92
2017-05-03 16:30 | 113.84 | 95.97
2017-05-03 17:00 | 116.87 | 98
2017-05-03 17:30 | 121.56 | 104.48
2017-05-03 18:00 | 118.71 | 102.67
2017-05-03 18:30 | 118.29 | 100.63
2017-05-03 19:00 | 117.41 | 100.93
2017-05-03 19:30 | 113.44 | 94.48
2017-05-03 20:00 | 115.2 | 97.31
2017-05-03 20:30 | 112.48 | 94.93
2017-05-03 21:00 | 108.74 | 89.32
2017-05-03 21:30 | 111.96 | 92.87
2017-05-03 22:00 | 106.8 | 85.84
2017-05-03 22:30 | 111.93 | 92.35
2017-05-03 23:00 | 111.78 | 90.87
2017-05-03 23:30 | 111.08 | 89.68
2017-05-04 | 119.44 | 101.91
2017-05-04 00:30 | 113.8 | 92.06
2017-05-04 01:00 | 114.21 | 92.29
2017-05-04 01:30 | 112.04 | 89.24
2017-05-04 02:00 | 113.84 | 93.09
2017-05-04 02:30 | 116.75 | 97.65
2017-05-04 03:00 | 111.46 | 90.27
2017-05-04 03:30 | 114.55 | 93.49
2017-05-04 04:00 | 115.89 | 96.42
2017-05-04 04:30 | 116.35 | 96.32
2017-05-04 05:00 | 111.29 | 88.41
2017-05-04 05:30 | 112.19 | 90.58
2017-05-04 06:00 | 109.46 | 89.29
2017-05-04 06:30 | 104.59 | 80.69
2017-05-04 07:00 | 115.8 | 95.02
2017-05-04 07:30 | 120.28 | 101.25
2017-05-04 08:00 | 121.92 | 104.24
2017-05-04 08:30 | 119.24 | 99.81
2017-05-04 09:00 | 112.01 | 88.95
2017-05-04 09:30 | 111.14 | 87.79
2017-05-04 10:00 | 108.93 | 85.09
2017-05-04 10:30 | 115.32 | 93.43
2017-05-04 11:00 | 119.92 | 97.84
2017-05-04 11:30 | 116.1 | 91.17
2017-05-04 12:00 | 115.14 | 92.84
2017-05-04 12:30 | 112.55 | 88.45
2017-05-04 13:00 | 119.58 | 98.23
2017-05-04 13:30 | 112.32 | 89.49
2017-05-04 14:00 | 115.33 | 92.67
2017-05-04 14:30 | 119.57 | 99.15
2017-05-04 15:00 | 116.46 | 93.29
2017-05-04 15:30 | 119.52 | 98.93
2017-05-04 16:00 | 118.35 | 99.38
2017-05-04 16:30 | 115.74 | 95.59
2017-05-04 17:00 | 120.47 | 103.17
2017-05-04 17:30 | 120.4 | 103.32
2017-05-04 18:00 | 117.23 | 99.58
2017-05-04 18:30 | 114.45 | 94.6
2017-05-04 19:00 | 119.85 | 103.41
2017-05-04 19:30 | 124.6 | 109.26
2017-05-04 20:00 | 122.58 | 106.85
2017-05-04 20:30 | 120.48 | 104.18
2017-05-04 21:00 | 118.65 | 101.47
2017-05-04 21:30 | 118.89 | 100.49
2017-05-04 22:00 | 117.32 | 98.82
2017-05-04 22:30 | 123.18 | 106.83
2017-05-04 23:00 | 122.46 | 106.19
2017-05-04 23:30 | 122.62 | 105.99
2017-05-05 | 125.98 | 110.3
2017-05-05 00:30 | 125.63 | 109.78
2017-05-05 01:00 | 121.54 | 104.3
2017-05-05 01:30 | 122.94 | 105.68
2017-05-05 02:00 | 120.69 | 102.89
2017-05-05 02:30 | 122.99 | 107.5
2017-05-05 03:00 | 116.91 | 98.52
2017-05-05 03:30 | 123.28 | 106.59
2017-05-05 04:00 | 122.27 | 105.29
2017-05-05 04:30 | 118.65 | 101.5
2017-05-05 05:00 | 117.72 | 99.4
2017-05-05 05:30 | 118.41 | 100.11
2017-05-05 06:00 | 122.34 | 106.11
2017-05-05 06:30 | 113.81 | 94.73
2017-05-05 07:00 | 112.21 | 94.19
2017-05-05 07:30 | 115.53 | 98.81
2017-05-05 08:00 | 118.63 | 101.08
2017-05-05 08:30 | 113.39 | 93.54
2017-05-05 09:00 | 109.58 | 89.77
2017-05-05 09:30 | 111.32 | 93.26
2017-05-05 10:00 | 115.04 | 97.4
2017-05-05 10:30 | 117.31 | 100.93
2017-05-05 11:00 | 116.42 | 98.8
2017-05-05 11:30 | 116.84 | 98.91
2017-05-05 12:00 | 121.09 | 105.52
2017-05-05 12:30 | 121.53 | 104.76
2017-05-05 13:00 | 118.05 | 101.1
2017-05-05 13:30 | 115.08 | 96.8
2017-05-05 14:00 | 122.57 | 106.57
2017-05-05 14:30 | 125.64 | 110.71
2017-05-05 15:00 | 121.76 | 106.36
2017-05-05 15:30 | 120.78 | 106.43
2017-05-05 16:00 | 120.54 | 106.3
2017-05-05 16:30 | 117.37 | 101.99
2017-05-05 17:00 | 119.56 | 104.98
2017-05-05 17:30 | 118.61 | 103.51
2017-05-05 18:00 | 114.99 | 99.54
2017-05-05 18:30 | 109.04 | 90.98
2017-05-05 19:00 | 111.15 | 94.92
2017-05-05 19:30 | 114.25 | 99.12
2017-05-05 20:00 | 114.41 | 97.69
2017-05-05 20:30 | 123.77 | 107.94
2017-05-05 21:00 | 117.48 | 99.88
2017-05-05 21:30 | 119.52 | 102.01
2017-05-05 22:00 | 121.2 | 104.56
2017-05-05 22:30 | 122.8 | 106.61
2017-05-05 23:00 | 117.85 | 98.77
2017-05-05 23:30 | 113.98 | 94.53
2017-05-06 | 113.49 | 95.04
2017-05-06 00:30 | 118.7 | 102.75
2017-05-06 01:00 | 113.28 | 95.73
2017-05-06 01:30 | 114.88 | 96.84
2017-05-06 02:00 | 110.22 | 89.89
2017-05-06 02:30 | 117.08 | 100.07
2017-05-06 03:00 | 108.75 | 89.06
2017-05-06 03:30 | 110.45 | 91.49
2017-05-06 04:00 | 113.18 | 95.9
2017-05-06 04:30 | 114.07 | 96.65
2017-05-06 05:00 | 114.9 | 97.78
2017-05-06 05:30 | 116.66 | 100.09
2017-05-06 06:00 | 112.69 | 94.32
2017-05-06 06:30 | 109.68 | 89.25
2017-05-06 07:00 | 109.28 | 89.4
2017-05-06 07:30 | 112.33 | 94.14
2017-05-06 08:00 | 115.5 | 98.25
2017-05-06 08:30 | 114.7 | 97.49
2017-05-06 09:00 | 119 | 103.06
2017-05-06 09:30 | 119.84 | 105.12
2017-05-06 10:00 | 120.83 | 106.97
2017-05-06 10:30 | 120.09 | 104.57
2017-05-06 11:00 | 118.1 | 101.51
2017-05-06 11:30 | 114.15 | 95.83
2017-05-06 12:00 | 117.26 | 100.63
2017-05-06 12:30 | 121.05 | 106.81
2017-05-06 13:00 | 118.61 | 103.61
2017-05-06 13:30 | 121.59 | 107.24
2017-05-06 14:00 | 117.4 | 101.59
2017-05-06 14:30 | 119.62 | 104.46
2017-05-06 15:00 | 116.63 | 101.92
2017-05-06 15:30 | 116.3 | 99.92
2017-05-06 16:00 | 119.54 | 104.55
2017-05-06 16:30 | 117.33 | 100.98
2017-05-06 17:00 | 116.64 | 100.31
2017-05-06 17:30 | 117.71 | 102.84
2017-05-06 18:00 | 118.35 | 103.99
2017-05-06 18:30 | 114.68 | 98.1
2017-05-06 19:00 | 115.03 | 101.07
2017-05-06 19:30 | 122.42 | 108.91
2017-05-06 20:00 | 124.98 | 111.39
2017-05-06 20:30 | 118.59 | 104.18
2017-05-06 21:00 | 116.31 | 100.39
2017-05-06 21:30 | 119.82 | 103.66
2017-05-06 22:00 | 119.67 | 104.6
2017-05-06 22:30 | 120.76 | 106.16
2017-05-06 23:00 | 121.7 | 105.34
2017-05-06 23:30 | 125.02 | 109.57
2017-05-07 | 120.94 | 104.34
2017-05-07 00:30 | 120.21 | 104.15
2017-05-07 01:00 | 120.67 | 103.21
2017-05-07 01:30 | 120.36 | 101.65
2017-05-07 02:00 | 123.69 | 107.87
2017-05-07 02:30 | 118.03 | 99.84
2017-05-07 03:00 | 121.55 | 104.5
2017-05-07 03:30 | 123.75 | 107.26
2017-05-07 04:00 | 124.05 | 107.09
2017-05-07 04:30 | 122.35 | 105.28
2017-05-07 05:00 | 116.11 | 97.9
2017-05-07 05:30 | 118.09 | 101.38
2017-05-07 06:00 | 117.33 | 100.25
2017-05-07 06:30 | 110.33 | 88.73
2017-05-07 07:00 | 112.95 | 92.75
2017-05-07 07:30 | 114.27 | 95.78
2017-05-07 08:00 | 112.41 | 93.88
2017-05-07 08:30 | 115.32 | 98.64
2017-05-07 09:00 | 113.32 | 96.86
2017-05-07 09:30 | 114.67 | 97.72
2017-05-07 10:00 | 114.82 | 97.5
2017-05-07 10:30 | 113.62 | 96.12
2017-05-07 11:00 | 104.45 | 85.06
2017-05-07 11:30 | 109.97 | 93.57
2017-05-07 12:00 | 113.46 | 97.3
2017-05-07 12:30 | 113.11 | 97.29
2017-05-07 13:00 | 114.78 | 99.18
2017-05-07 13:30 | 116.99 | 100.44
2017-05-07 14:00 | 113.35 | 96.91
2017-05-07 14:30 | 113.07 | 96.96
2017-05-07 15:00 | 115.27 | 97.92
2017-05-07 15:30 | 114.78 | 97.65
2017-05-07 16:00 | 119.22 | 104.11
2017-05-07 16:30 | 117.86 | 101.97
2017-05-07 17:00 | 113.42 | 97.09
2017-05-07 17:30 | 121.46 | 107.47
2017-05-07 18:00 | 116.04 | 101.98
2017-05-07 18:30 | 113.23 | 96.92
2017-05-07 19:00 | 113.61 | 97.47
2017-05-07 19:30 | 115.93 | 101.04
2017-05-07 20:00 | 115.36 | 99.89
2017-05-07 20:30 | 107.63 | 90.32
2017-05-07 21:00 | 111.73 | 94.06
2017-05-07 21:30 | 110.38 | 92.79
2017-05-07 22:00 | 111.47 | 93.03
2017-05-07 22:30 | 116.53 | 99.93
2017-05-07 23:00 | 113.34 | 95.56
2017-05-07 23:30 | 116.04 | 97.97
2017-05-08 | 118.69 | 101.69
2017-05-08 00:30 | 117.54 | 101.59
2017-05-08 01:00 | 115.27 | 97.73
2017-05-08 01:30 | 111.17 | 94.37
2017-05-08 02:00 | 111.91 | 95.17
2017-05-08 02:30 | 109.02 | 91.62
2017-05-08 03:00 | 113.19 | 94.39
2017-05-08 03:30 | 117.47 | 100.64
2017-05-08 04:00 | 116.73 | 99.86
2017-05-08 04:30 | 116.58 | 98.39
2017-05-08 05:00 | 110.01 | 89.63
2017-05-08 05:30 | 108.12 | 88.91
2017-05-08 06:00 | 110.2 | 92.3
2017-05-08 06:30 | 105.24 | 82.93
2017-05-08 07:00 | 105.74 | 84.86
2017-05-08 07:30 | 116.85 | 100.44
2017-05-08 08:00 | 116.09 | 98.93
2017-05-08 08:30 | 111.16 | 92.51
2017-05-08 09:00 | 109.94 | 90.8
2017-05-08 09:30 | 112.1 | 92.58
2017-05-08 10:00 | 106.18 | 83.71
2017-05-08 10:30 | 111.76 | 92.76
2017-05-08 11:00 | 113.15 | 93.11
2017-05-08 11:30 | 115.36 | 96.75
2017-05-08 12:00 | 119.39 | 101.05
2017-05-08 12:30 | 116.58 | 97.69
2017-05-08 13:00 | 109.46 | 88.68
2017-05-08 13:30 | 110.29 | 90.77
2017-05-08 14:00 | 109.05 | 88.73
2017-05-08 14:30 | 110.42 | 88.49
2017-05-08 15:00 | 110.94 | 89.18
2017-05-08 15:30 | 114.49 | 94.59
2017-05-08 16:00 | 110.31 | 90.83
2017-05-08 16:30 | 111.54 | 91.37
2017-05-08 17:00 | 109.92 | 89.52
2017-05-08 17:30 | 110.98 | 92.24
2017-05-08 18:00 | 110.07 | 91.68
2017-05-08 18:30 | 110.98 | 91.84
2017-05-08 19:00 | 112.86 | 95.96
2017-05-08 19:30 | 110.97 | 96.34
2017-05-08 20:00 | 110.75 | 94.6
2017-05-08 20:30 | 112.13 | 94.39
2017-05-08 21:00 | 113.55 | 94.92
2017-05-08 21:30 | 108.45 | 88.47
2017-05-08 22:00 | 106.05 | 84.77
2017-05-08 22:30 | 109.52 | 87.74
2017-05-08 23:00 | 112.83 | 92
2017-05-08 23:30 | 110.23 | 88.13
2017-05-09 | 112.53 | 92.28
2017-05-09 00:30 | 116.27 | 97.82
2017-05-09 01:00 | 117.42 | 99.29
2017-05-09 01:30 | 116.02 | 96.59
2017-05-09 02:00 | 114.96 | 95.54
2017-05-09 02:30 | 107.3 | 86.5
2017-05-09 03:00 | 103.02 | 81.42
2017-05-09 03:30 | 104.13 | 82
2017-05-09 04:00 | 112.09 | 93.34
2017-05-09 04:30 | 107.06 | 85.59
2017-05-09 05:00 | 108.38 | 88.81
2017-05-09 05:30 | 107.83 | 87.5
2017-05-09 06:00 | 107.19 | 86.42
2017-05-09 06:30 | 101.96 | 79.33
2017-05-09 07:00 | 104.35 | 82.78
2017-05-09 07:30 | 111.2 | 91.66
2017-05-09 08:00 | 109.21 | 89.39
2017-05-09 08:30 | 105.44 | 84.88
2017-05-09 09:00 | 101.84 | 81.22
2017-05-09 09:30 | 96.98 | 76.05
2017-05-09 10:00 | 103.3 | 82.12
2017-05-09 10:30 | 101.68 | 79.99
2017-05-09 11:00 | 104.63 | 83.79
2017-05-09 11:30 | 103.23 | 79.65
2017-05-09 12:00 | 101.07 | 78.34
2017-05-09 12:30 | 104.09 | 83.15
2017-05-09 13:00 | 106.87 | 85.92
2017-05-09 13:30 | 107 | 86.39
2017-05-09 14:00 | 109.32 | 89.77
2017-05-09 14:30 | 107.65 | 87.37
2017-05-09 15:00 | 107.14 | 86.35
2017-05-09 15:30 | 107.45 | 86.87
2017-05-09 16:00 | 106.32 | 85.95
2017-05-09 16:30 | 109.78 | 91.66
2017-05-09 17:00 | 102.74 | 82.8
2017-05-09 17:30 | 99.22 | 77.94
2017-05-09 18:00 | 104.11 | 86.02
2017-05-09 18:30 | 99.07 | 80.84
2017-05-09 19:00 | 106.28 | 90.64
2017-05-09 19:30 | 108.01 | 91.59
2017-05-09 20:00 | 105.33 | 89.08
2017-05-09 20:30 | 103.35 | 85.13
2017-05-09 21:00 | 98.01 | 77.99
2017-05-09 21:30 | 101.16 | 81.9
2017-05-09 22:00 | 103.13 | 84.36
2017-05-09 22:30 | 105.4 | 87.35
2017-05-09 23:00 | 97.84 | 74.93
2017-05-09 23:30 | 98.35 | 76
2017-05-10 | 102.04 | 80.8
2017-05-10 00:30 | 101.79 | 81.35
2017-05-10 01:00 | 100.17 | 78.44
2017-05-10 01:30 | 97.33 | 73.94
2017-05-10 02:00 | 97.92 | 74.04
2017-05-10 02:30 | 99.93 | 77.35
2017-05-10 03:00 | 100.56 | 78.74
2017-05-10 03:30 | 101.89 | 80.59
2017-05-10 04:00 | 98.27 | 75.64
2017-05-10 04:30 | 99.22 | 76.56
2017-05-10 05:00 | 103.27 | 82.11
2017-05-10 05:30 | 103.53 | 83.69
2017-05-10 06:00 | 106.5 | 87.47
2017-05-10 06:30 | 101.23 | 80.89
2017-05-10 07:00 | 101.94 | 80.79
2017-05-10 07:30 | 103.93 | 83.58
2017-05-10 08:00 | 98.66 | 76.57
2017-05-10 08:30 | 90.83 | 67.07
2017-05-10 09:00 | 88.44 | 65.54
2017-05-10 09:30 | 89.72 | 66.36
2017-05-10 10:00 | 95.22 | 71.56
2017-05-10 10:30 | 95.94 | 75.35
2017-05-10 11:00 | 96.44 | 74.78
2017-05-10 11:30 | 100.6 | 79.41
2017-05-10 12:00 | 99.58 | 77.15
2017-05-10 12:30 | 92.49 | 67.46
2017-05-10 13:00 | 93.15 | 70.36
2017-05-10 13:30 | 95.26 | 73.75
2017-05-10 14:00 | 94.96 | 72.12
2017-05-10 14:30 | 101.49 | 80.32
2017-05-10 15:00 | 97.98 | 75
2017-05-10 15:30 | 100.08 | 79.14
2017-05-10 16:00 | 100.99 | 77.25
2017-05-10 16:30 | 100.89 | 79.68
2017-05-10 17:00 | 101.22 | 78.55
2017-05-10 17:30 | 98.1 | 75.34
2017-05-10 18:00 | 101.12 | 79.58
2017-05-10 18:30 | 95.16 | 70.7
2017-05-10 19:00 | 100.63 | 79.43
2017-05-10 19:30 | 105.09 | 85.99
2017-05-10 20:00 | 104.54 | 83.68
2017-05-10 20:30 | 104.16 | 83.31
2017-05-10 21:00 | 100.32 | 77.91
2017-05-10 21:30 | 107.24 | 87.55
2017-05-10 22:00 | 103 | 80.57
2017-05-10 22:30 | 107.39 | 86.08
2017-05-10 23:00 | 105.69 | 84.67
2017-05-10 23:30 | 103.88 | 82.52
2017-05-11 | 106.92 | 85.92
2017-05-11 00:30 | 110 | 90.9
2017-05-11 01:00 | 104.09 | 82.18
2017-05-11 01:30 | 104.23 | 82.38
2017-05-11 02:00 | 107.5 | 85.21
2017-05-11 02:30 | 110.04 | 88.49
2017-05-11 03:00 | 109.57 | 87.22
2017-05-11 03:30 | 110.43 | 89.33
2017-05-11 04:00 | 112.5 | 89.79
2017-05-11 04:30 | 113.24 | 91.8
2017-05-11 05:00 | 110.91 | 87.83
2017-05-11 05:30 | 112.6 | 88.94
2017-05-11 06:00 | 110.43 | 86.49
2017-05-11 06:30 | 108.32 | 84.71
2017-05-11 07:00 | 112.74 | 91.28
2017-05-11 07:30 | 112.22 | 90.33
2017-05-11 08:00 | 115.09 | 93.21
2017-05-11 08:30 | 112.26 | 88.53
2017-05-11 09:00 | 108.68 | 82.88
2017-05-11 09:30 | 111.23 | 84.61
2017-05-11 10:00 | 112.79 | 86.56
2017-05-11 10:30 | 115.04 | 89.46
2017-05-11 11:00 | 113.79 | 86.95
2017-05-11 11:30 | 111.11 | 84.54
2017-05-11 12:00 | 107.82 | 79.96
2017-05-11 12:30 | 108.85 | 79.69
2017-05-11 13:00 | 108.17 | 79.61
2017-05-11 13:30 | 105.58 | 77.12
2017-05-11 14:00 | 107.49 | 79.43
2017-05-11 14:30 | 109.94 | 84.46
2017-05-11 15:00 | 113.91 | 91.93
2017-05-11 15:30 | 108.34 | 83.22
2017-05-11 16:00 | 108.98 | 83.84
2017-05-11 16:30 | 111.71 | 88.1
2017-05-11 17:00 | 114.13 | 91.95
2017-05-11 17:30 | 120.3 | 100.51
2017-05-11 18:00 | 120.9 | 101.12
2017-05-11 18:30 | 111.68 | 89
2017-05-11 19:00 | 116.13 | 96.38
2017-05-11 19:30 | 117.99 | 97.45
2017-05-11 20:00 | 121.34 | 102.74
2017-05-11 20:30 | 120.29 | 102.01
2017-05-11 21:00 | 116.81 | 96.96
2017-05-11 21:30 | 116.63 | 96.48
2017-05-11 22:00 | 113.07 | 93.16
2017-05-11 22:30 | 117.44 | 98.54
2017-05-11 23:00 | 119.52 | 100.87
2017-05-11 23:30 | 116.49 | 96.32
2017-05-12 | 115.64 | 94.73
2017-05-12 00:30 | 117.47 | 97.3
2017-05-12 01:00 | 118.87 | 100.83
2017-05-12 01:30 | 116.87 | 97.94
2017-05-12 02:00 | 118.27 | 100.53
2017-05-12 02:30 | 118.25 | 99.87
2017-05-12 03:00 | 119.96 | 103.74
2017-05-12 03:30 | 120.58 | 102.56
2017-05-12 04:00 | 115.66 | 96.27
2017-05-12 04:30 | 114.76 | 95.92
2017-05-12 05:00 | 116.3 | 98.04
2017-05-12 05:30 | 116.3 | 98.77
2017-05-12 06:00 | 119.69 | 104.16
2017-05-12 06:30 | 118.55 | 100.3
2017-05-12 07:00 | 113.01 | 94.99
2017-05-12 07:30 | 115.82 | 100.09
2017-05-12 08:00 | 118.68 | 102.78
2017-05-12 08:30 | 119.92 | 103.42
2017-05-12 09:00 | 115.99 | 99.19
2017-05-12 09:30 | 119.64 | 103.92
2017-05-12 10:00 | 111.59 | 91.23
2017-05-12 10:30 | 112.88 | 94.11
2017-05-12 11:00 | 114.12 | 97.08
2017-05-12 11:30 | 109.19 | 89.05
2017-05-12 12:00 | 108.25 | 87.62
2017-05-12 12:30 | 105.38 | 83.6
2017-05-12 13:00 | 104.2 | 82.73
2017-05-12 13:30 | 104.83 | 83.81
2017-05-12 14:00 | 109.44 | 90.48
2017-05-12 14:30 | 108.66 | 89.85
2017-05-12 15:00 | 112.22 | 94.35
2017-05-12 15:30 | 118.97 | 102.67
2017-05-12 16:00 | 116.66 | 99.78
2017-05-12 16:30 | 114.08 | 96.88
2017-05-12 17:00 | 110.78 | 93.37
2017-05-12 17:30 | 115.77 | 99.46
2017-05-12 18:00 | 116.06 | 100.64
2017-05-12 18:30 | 110.87 | 93.76
2017-05-12 19:00 | 118.3 | 103.19
2017-05-12 19:30 | 115.9 | 100.36
2017-05-12 20:00 | 112.6 | 97.21
2017-05-12 20:30 | 110.53 | 96.52
2017-05-12 21:00 | 108.03 | 92.55
2017-05-12 21:30 | 108.99 | 92.71
2017-05-12 22:00 | 110.37 | 93.02
2017-05-12 22:30 | 109.97 | 91.05
2017-05-12 23:00 | 108.53 | 89.89
2017-05-12 23:30 | 108.25 | 90.06
2017-05-13 | 111.69 | 94.16
2017-05-13 00:30 | 120.24 | 105.76
2017-05-13 01:00 | 111.42 | 94.07
2017-05-13 01:30 | 110.5 | 93.29
2017-05-13 02:00 | 108.48 | 90.79
2017-05-13 02:30 | 112.87 | 97.29
2017-05-13 03:00 | 116.46 | 101.51
2017-05-13 03:30 | 114.05 | 98.19
2017-05-13 04:00 | 116.98 | 102.5
2017-05-13 04:30 | 116.19 | 101.31
2017-05-13 05:00 | 112.41 | 95.65
2017-05-13 05:30 | 112.38 | 95.98
2017-05-13 06:00 | 110.23 | 92.25
2017-05-13 06:30 | 105.47 | 85.67
2017-05-13 07:00 | 110.04 | 92.75
2017-05-13 07:30 | 115.55 | 100.73
2017-05-13 08:00 | 110.71 | 93.93
2017-05-13 08:30 | 104.03 | 88
2017-05-13 09:00 | 108.97 | 92.41
2017-05-13 09:30 | 105.27 | 83.91
2017-05-13 10:00 | 112.2 | 93.62
2017-05-13 10:30 | 106.73 | 87.93
2017-05-13 11:00 | 110.4 | 93.21
2017-05-13 11:30 | 110.78 | 92.21
2017-05-13 12:00 | 110.48 | 92.7
2017-05-13 12:30 | 107.32 | 88.24
2017-05-13 13:00 | 107.92 | 88.06
2017-05-13 13:30 | 108.23 | 89.32
2017-05-13 14:00 | 110.72 | 92.01
2017-05-13 14:30 | 109.9 | 91.77
2017-05-13 15:00 | 113.82 | 98.21
2017-05-13 15:30 | 110.4 | 92.85
2017-05-13 16:00 | 105.98 | 86.2
2017-05-13 16:30 | 104.57 | 85.07
2017-05-13 17:00 | 109.03 | 92.68
2017-05-13 17:30 | 111.68 | 96.69
2017-05-13 18:00 | 116.1 | 102.63
2017-05-13 18:30 | 106.47 | 90
2017-05-13 19:00 | 109.83 | 96.38
2017-05-13 19:30 | 110.3 | 96.45
2017-05-13 20:00 | 116.15 | 102.68
2017-05-13 20:30 | 116.11 | 103.27
2017-05-13 21:00 | 112.17 | 98.17
2017-05-13 21:30 | 107.03 | 91.3
2017-05-13 22:00 | 108.27 | 92.32
2017-05-13 22:30 | 107.31 | 90.88
2017-05-13 23:00 | 109.34 | 93.47
2017-05-13 23:30 | 112.25 | 96.4
2017-05-14 | 115.1 | 99.13
2017-05-14 00:30 | 111.75 | 94.81
2017-05-14 01:00 | 109.76 | 92.09
2017-05-14 01:30 | 112.62 | 95.92
2017-05-14 02:00 | 112.79 | 95.93
2017-05-14 02:30 | 112.19 | 95.5
2017-05-14 03:00 | 115.47 | 99.42
2017-05-14 03:30 | 114.53 | 97.86
2017-05-14 04:00 | 110.78 | 93.46
2017-05-14 04:30 | 114.8 | 99.37
2017-05-14 05:00 | 114.23 | 98.22
2017-05-14 05:30 | 113.1 | 96.49
2017-05-14 06:00 | 114.56 | 98.3
2017-05-14 06:30 | 110.08 | 91.32
2017-05-14 07:00 | 106.67 | 86.1
2017-05-14 07:30 | 109.6 | 90.94
2017-05-14 08:00 | 112.51 | 95.57
2017-05-14 08:30 | 114.69 | 97.8
2017-05-14 09:00 | 111.95 | 93.49
2017-05-14 09:30 | 112.18 | 94
2017-05-14 10:00 | 113.03 | 94.66
2017-05-14 10:30 | 108.1 | 89.49
2017-05-14 11:00 | 109.34 | 90.81
2017-05-14 11:30 | 109.69 | 90.49
2017-05-14 12:00 | 105.88 | 86.89
2017-05-14 12:30 | 108.96 | 91.15
2017-05-14 13:00 | 117.2 | 101.26
2017-05-14 13:30 | 117.23 | 102.32
2017-05-14 14:00 | 113.17 | 96.84
2017-05-14 14:30 | 111.81 | 94.89
2017-05-14 15:00 | 115.9 | 100.65
2017-05-14 15:30 | 119.11 | 105.07
2017-05-14 16:00 | 117.99 | 101.96
2017-05-14 16:30 | 118.01 | 103.23
2017-05-14 17:00 | 113.33 | 97.55
2017-05-14 17:30 | 111.24 | 95.92
2017-05-14 18:00 | 112.48 | 98.21
2017-05-14 18:30 | 105.59 | 89.2
2017-05-14 19:00 | 112.79 | 98.62
2017-05-14 19:30 | 113.44 | 98.48
2017-05-14 20:00 | 114.65 | 99.63
2017-05-14 20:30 | 116.85 | 101.53
2017-05-14 21:00 | 118.38 | 103.54
2017-05-14 21:30 | 113.74 | 97.63
2017-05-14 22:00 | 115.72 | 100.01
2017-05-14 22:30 | 113.39 | 97.6
2017-05-14 23:00 | 105.25 | 85.5
2017-05-14 23:30 | 107.31 | 88.4
2017-05-15 | 109.79 | 91.52
2017-05-15 00:30 | 111.2 | 93.27
2017-05-15 01:00 | 113.2 | 95.35
2017-05-15 01:30 | 120.71 | 105.57
2017-05-15 02:00 | 118.52 | 102.7
2017-05-15 02:30 | 113.41 | 96.29
2017-05-15 03:00 | 109.54 | 90.31
2017-05-15 03:30 | 107.84 | 88.9
2017-05-15 04:00 | 110.56 | 92.12
2017-05-15 04:30 | 118.86 | 104.06
2017-05-15 05:00 | 115.38 | 99.53
2017-05-15 05:30 | 119.2 | 103.79
2017-05-15 06:00 | 117.14 | 100.6
2017-05-15 06:30 | 106.66 | 86.66
2017-05-15 07:00 | 109.14 | 91.36
2017-05-15 07:30 | 115.28 | 98.91
2017-05-15 08:00 | 119.15 | 101.19
2017-05-15 08:30 | 113.48 | 93.8
2017-05-15 09:00 | 115.22 | 96.97
2017-05-15 09:30 | 115.37 | 97.34
2017-05-15 10:00 | 113.71 | 97.36
2017-05-15 10:30 | 112.94 | 96.67
2017-05-15 11:00 | 115.89 | 100.11
2017-05-15 11:30 | 113.19 | 94.03
2017-05-15 12:00 | 113.84 | 95.15
2017-05-15 12:30 | 109.86 | 90.77
2017-05-15 13:00 | 108.7 | 89.83
2017-05-15 13:30 | 107.76 | 87.79
2017-05-15 14:00 | 112.15 | 93.92
2017-05-15 14:30 | 111.69 | 91.87
2017-05-15 15:00 | 114.28 | 95.05
2017-05-15 15:30 | 113.58 | 94.58
2017-05-15 16:00 | 110.14 | 89.78
2017-05-15 16:30 | 109.62 | 89.76
2017-05-15 17:00 | 108.87 | 88.75
2017-05-15 17:30 | 112.74 | 93.93
2017-05-15 18:00 | 112.76 | 94.73
2017-05-15 18:30 | 108.45 | 89.1
2017-05-15 19:00 | 116.27 | 100.85
2017-05-15 19:30 | 120.09 | 106.11
2017-05-15 20:00 | 114.93 | 99
2017-05-15 20:30 | 105.29 | 88.26
2017-05-15 21:00 | 101.18 | 81
2017-05-15 21:30 | 106.41 | 86.29
2017-05-15 22:00 | 107.74 | 88.42
2017-05-15 22:30 | 107.37 | 86.99
2017-05-15 23:00 | 107.95 | 88.07
2017-05-15 23:30 | 109.05 | 88.9
2017-05-16 | 105.39 | 82.57
2017-05-16 00:30 | 106.89 | 87.01
2017-05-16 01:00 | 111.66 | 93.15
2017-05-16 01:30 | 109.65 | 88.43
2017-05-16 02:00 | 114 | 95.97
2017-05-16 02:30 | 108.26 | 86.66
2017-05-16 03:00 | 107.29 | 89.38
2017-05-16 03:30 | 110.66 | 92.57
2017-05-16 04:00 | 113.92 | 96.49
2017-05-16 04:30 | 112.78 | 96.54
2017-05-16 05:00 | 118.13 | 102.64
2017-05-16 05:30 | 114.63 | 98.39
2017-05-16 06:00 | 114.01 | 96.29
2017-05-16 06:30 | 110.11 | 90.84
2017-05-16 07:00 | 111.02 | 92
2017-05-16 07:30 | 116.32 | 99.19
2017-05-16 08:00 | 111.75 | 93.73
2017-05-16 08:30 | 106.78 | 89.22
2017-05-16 09:00 | 106.85 | 89.5
2017-05-16 09:30 | 100.57 | 80.61
2017-05-16 10:00 | 104.59 | 85.33
2017-05-16 10:30 | 109.6 | 91.13
2017-05-16 11:00 | 113.53 | 93.7
2017-05-16 11:30 | 111.79 | 92.12
2017-05-16 12:00 | 118.89 | 101.52
2017-05-16 12:30 | 113.63 | 94.96
2017-05-16 13:00 | 112.09 | 90.87
2017-05-16 13:30 | 110.89 | 90.77
2017-05-16 14:00 | 111.72 | 90.97
2017-05-16 14:30 | 108.24 | 87.95
2017-05-16 15:00 | 106.71 | 85.45
2017-05-16 15:30 | 104.65 | 82.79
2017-05-16 16:00 | 103.37 | 82.65
2017-05-16 16:30 | 105.09 | 84.55
2017-05-16 17:00 | 101.81 | 82.05
2017-05-16 17:30 | 103.33 | 82.47
2017-05-16 18:00 | 103.26 | 83.21
2017-05-16 18:30 | 103.71 | 82
2017-05-16 19:00 | 106.72 | 88.05
2017-05-16 19:30 | 109.09 | 91.36
2017-05-16 20:00 | 111.94 | 94.64
2017-05-16 20:30 | 109.84 | 91.35
2017-05-16 21:00 | 106.95 | 87.81
2017-05-16 21:30 | 108.06 | 89.35
2017-05-16 22:00 | 109.91 | 92.02
2017-05-16 22:30 | 109.33 | 90.9
2017-05-16 23:00 | 110.35 | 90.88
2017-05-16 23:30 | 111.86 | 94.45
2017-05-17 | 103.33 | 82.88
2017-05-17 00:30 | 105.02 | 84.57
2017-05-17 01:00 | 105.78 | 83.72
2017-05-17 01:30 | 106.04 | 84.37
2017-05-17 02:00 | 105.51 | 82.42
2017-05-17 02:30 | 107.68 | 86.93
2017-05-17 03:00 | 106.35 | 85.03
2017-05-17 03:30 | 104.35 | 82.97
2017-05-17 04:00 | 107.74 | 88.14
2017-05-17 04:30 | 108.55 | 89.6
2017-05-17 05:00 | 101.99 | 80.42
2017-05-17 05:30 | 106.66 | 87.29
2017-05-17 06:00 | 111.45 | 93.45
2017-05-17 06:30 | 98.72 | 75.54
2017-05-17 07:00 | 98.2 | 75.45
2017-05-17 07:30 | 96.68 | 76.25
2017-05-17 08:00 | 90.27 | 68.55
2017-05-17 08:30 | 86.65 | 62.97
2017-05-17 09:00 | 89.73 | 65.22
2017-05-17 09:30 | 89.7 | 65.27
2017-05-17 10:00 | 90.08 | 66.42
2017-05-17 10:30 | 93.33 | 70.9
2017-05-17 11:00 | 95.41 | 71.25
2017-05-17 11:30 | 95.91 | 72.89
2017-05-17 12:00 | 94.75 | 70.2
2017-05-17 12:30 | 98.37 | 76.19
2017-05-17 13:00 | 97.13 | 75.97
2017-05-17 13:30 | 93.88 | 71.44
2017-05-17 14:00 | 89.33 | 63.63
2017-05-17 14:30 | 90.41 | 66
2017-05-17 15:00 | 88.09 | 61.58
2017-05-17 15:30 | 90.1 | 63.85
2017-05-17 16:00 | 91.07 | 66.2
2017-05-17 16:30 | 95.97 | 75.11
2017-05-17 17:00 | 95.94 | 74.68
2017-05-17 17:30 | 93.28 | 71.81
2017-05-17 18:00 | 96.24 | 76.95
2017-05-17 18:30 | 92.15 | 72.15
2017-05-17 19:00 | 93.67 | 73.2
2017-05-17 19:30 | 101 | 83.75
2017-05-17 20:00 | 96.53 | 77.37
2017-05-17 20:30 | 100.57 | 81.72
2017-05-17 21:00 | 105.13 | 87.48
2017-05-17 21:30 | 102.09 | 83.37
2017-05-17 22:00 | 96.34 | 76.31
2017-05-17 22:30 | 99.3 | 77.76
2017-05-17 23:00 | 102.03 | 78.94
2017-05-17 23:30 | 101.61 | 76.55
2017-05-18 | 100.18 | 75.05
2017-05-18 00:30 | 103.85 | 80.43
2017-05-18 01:00 | 104.83 | 82.81
2017-05-18 01:30 | 104.29 | 82.02
2017-05-18 02:00 | 103.13 | 80.2
2017-05-18 02:30 | 105.12 | 81.83
2017-05-18 03:00 | 105.15 | 80.59
2017-05-18 03:30 | 106.77 | 81.77
2017-05-18 04:00 | 108.48 | 86.95
2017-05-18 04:30 | 110.51 | 89.14
2017-05-18 05:00 | 111.59 | 91.12
2017-05-18 05:30 | 109.98 | 90.37
2017-05-18 06:00 | 114.24 | 96.49
2017-05-18 06:30 | 111.53 | 91.17
2017-05-18 07:00 | 106.3 | 84.65
2017-05-18 07:30 | 108.21 | 87.98
2017-05-18 08:00 | 104.24 | 81.88
2017-05-18 08:30 | 114.84 | 96.74
2017-05-18 09:00 | 109.41 | 86.1
2017-05-18 09:30 | 105.4 | 81.03
2017-05-18 10:00 | 104.11 | 80.51
2017-05-18 10:30 | 110.77 | 87.9
2017-05-18 11:00 | 110.38 | 86.17
2017-05-18 11:30 | 108.95 | 84.89
2017-05-18 12:00 | 113.84 | 90.78
2017-05-18 12:30 | 117.57 | 96.59
2017-05-18 13:00 | 110.99 | 85.71
2017-05-18 13:30 | 114.91 | 93.61
2017-05-18 14:00 | 108.65 | 86.58
2017-05-18 14:30 | 111.33 | 88.01
2017-05-18 15:00 | 109.38 | 87.08
2017-05-18 15:30 | 114.92 | 95.02
2017-05-18 16:00 | 113.27 | 91.82
2017-05-18 16:30 | 115.37 | 95.64
2017-05-18 17:00 | 113.92 | 94.41
2017-05-18 17:30 | 111.11 | 90.6
2017-05-18 18:00 | 112.63 | 93.64
2017-05-18 18:30 | 112.14 | 91.05
2017-05-18 19:00 | 115.37 | 98.57
2017-05-18 19:30 | 118.22 | 100.99
2017-05-18 20:00 | 114.83 | 96.89
2017-05-18 20:30 | 117.13 | 99.97
2017-05-18 21:00 | 116.51 | 100.53
2017-05-18 21:30 | 116.27 | 97.98
2017-05-18 22:00 | 109.91 | 90.56
2017-05-18 22:30 | 106.13 | 84.93
2017-05-18 23:00 | 105.66 | 85.98
2017-05-18 23:30 | 104.01 | 82.73
2017-05-19 | 105.59 | 82.96
2017-05-19 00:30 | 110.16 | 87.98
2017-05-19 01:00 | 107.16 | 84.78
2017-05-19 01:30 | 110.16 | 89.21
2017-05-19 02:00 | 114.52 | 94.5
2017-05-19 02:30 | 114.57 | 95.24
2017-05-19 03:00 | 109.21 | 88.33
2017-05-19 03:30 | 109.93 | 88.64
2017-05-19 04:00 | 107.23 | 85.77
2017-05-19 04:30 | 113.19 | 92.37
2017-05-19 05:00 | 109.72 | 87.74
2017-05-19 05:30 | 115.75 | 97.01
2017-05-19 06:00 | 109.76 | 91.41
2017-05-19 06:30 | 106.05 | 82.8
2017-05-19 07:00 | 114.28 | 96.29
2017-05-19 07:30 | 113.43 | 95.97
2017-05-19 08:00 | 110.78 | 92.21
2017-05-19 08:30 | 112.11 | 94.3
2017-05-19 09:00 | 110.58 | 91.59
2017-05-19 09:30 | 105.42 | 86.69
2017-05-19 10:00 | 98.33 | 78.91
2017-05-19 10:30 | 103.52 | 84.25
2017-05-19 11:00 | 108.86 | 89.17
2017-05-19 11:30 | 108.26 | 88.55
2017-05-19 12:00 | 110.02 | 90.92
2017-05-19 12:30 | 112 | 93.95
2017-05-19 13:00 | 111.77 | 94.54
2017-05-19 13:30 | 114.03 | 94.37
2017-05-19 14:00 | 115.62 | 97.64
2017-05-19 14:30 | 113.77 | 94.38
2017-05-19 15:00 | 111.42 | 90.99
2017-05-19 15:30 | 111.06 | 91
2017-05-19 16:00 | 115.54 | 97.32
2017-05-19 16:30 | 121.12 | 105.25
2017-05-19 17:00 | 120.25 | 105.61
2017-05-19 17:30 | 116.55 | 98.41
2017-05-19 18:00 | 121.32 | 106.32
2017-05-19 18:30 | 113.94 | 94.42
2017-05-19 19:00 | 115.09 | 96.85
2017-05-19 19:30 | 119 | 101.9
2017-05-19 20:00 | 119.15 | 102.8
2017-05-19 20:30 | 116.05 | 98.52
2017-05-19 21:00 | 112.63 | 93.35
2017-05-19 21:30 | 117.53 | 98.8
2017-05-19 22:00 | 114.63 | 95.35
2017-05-19 22:30 | 117.9 | 98.46
2017-05-19 23:00 | 117.97 | 98.69
2017-05-19 23:30 | 117.45 | 97.34
2017-05-20 | 108.18 | 85.17
2017-05-20 00:30 | 108.86 | 87.96
2017-05-20 01:00 | 113.49 | 91.79
2017-05-20 01:30 | 116.2 | 96.18
2017-05-20 02:00 | 118.71 | 98.82
2017-05-20 02:30 | 118.92 | 98.97
2017-05-20 03:00 | 114.71 | 93.94
2017-05-20 03:30 | 112.06 | 90.01
2017-05-20 04:00 | 113.09 | 91.89
2017-05-20 04:30 | 114.91 | 94.73
2017-05-20 05:00 | 112.01 | 92.24
2017-05-20 05:30 | 115.33 | 94.58
2017-05-20 06:00 | 117.6 | 98.25
2017-05-20 06:30 | 105.63 | 82.35
2017-05-20 07:00 | 113.52 | 92.98
2017-05-20 07:30 | 116.65 | 96.63
2017-05-20 08:00 | 107.67 | 87.03
2017-05-20 08:30 | 105.81 | 86.2
2017-05-20 09:00 | 110.7 | 90.29
2017-05-20 09:30 | 111.79 | 89.46
2017-05-20 10:00 | 105.79 | 81.05
2017-05-20 10:30 | 110.23 | 87.86
2017-05-20 11:00 | 108.79 | 85.31
2017-05-20 11:30 | 106.3 | 84.64
2017-05-20 12:00 | 112.87 | 92.7
2017-05-20 12:30 | 105.11 | 81.98
2017-05-20 13:00 | 109.82 | 86.86
2017-05-20 13:30 | 108.36 | 82.41
2017-05-20 14:00 | 111.52 | 89.35
2017-05-20 14:30 | 112.02 | 89.19
2017-05-20 15:00 | 110.45 | 85.7
2017-05-20 15:30 | 109.31 | 83.21
2017-05-20 16:00 | 111 | 88.63
2017-05-20 16:30 | 103.57 | 77.84
2017-05-20 17:00 | 105.21 | 80.67
2017-05-20 17:30 | 113.73 | 91.54
2017-05-20 18:00 | 114.38 | 93.26
2017-05-20 18:30 | 112.45 | 87.76
2017-05-20 19:00 | 114.6 | 92.97
2017-05-20 19:30 | 117.31 | 97.24
2017-05-20 20:00 | 117.44 | 95.84
2017-05-20 20:30 | 119.13 | 99.49
2017-05-20 21:00 | 108.62 | 85.21
2017-05-20 21:30 | 110.65 | 86.38
2017-05-20 22:00 | 115.37 | 91.64
2017-05-20 22:30 | 112.34 | 88
2017-05-20 23:00 | 111.14 | 86.11
2017-05-20 23:30 | 109.85 | 85.03
2017-05-21 | 118.19 | 95.68
2017-05-21 00:30 | 115.79 | 93.17
2017-05-21 01:00 | 110.51 | 85.1
2017-05-21 01:30 | 111.6 | 85.99
2017-05-21 02:00 | 111.94 | 86.41
2017-05-21 02:30 | 112.37 | 88.22
2017-05-21 03:00 | 110.26 | 85.07
2017-05-21 03:30 | 110.85 | 84.41
2017-05-21 04:00 | 110.87 | 85.22
2017-05-21 04:30 | 109.8 | 85.08
2017-05-21 05:00 | 106.99 | 81.79
2017-05-21 05:30 | 111.35 | 87.19
2017-05-21 06:00 | 104.49 | 78.47
2017-05-21 06:30 | 108.4 | 81.17
2017-05-21 07:00 | 112.07 | 88.02
2017-05-21 07:30 | 112.74 | 89.54
2017-05-21 08:00 | 108.87 | 84.08
2017-05-21 08:30 | 110.8 | 88.16
2017-05-21 09:00 | 109.81 | 87.62
2017-05-21 09:30 | 112.16 | 89.16
2017-05-21 10:00 | 112.94 | 88.71
2017-05-21 10:30 | 114.26 | 92.73
2017-05-21 11:00 | 106.94 | 83.28
2017-05-21 11:30 | 107.66 | 85.63
2017-05-21 12:00 | 108.69 | 86.65
2017-05-21 12:30 | 101.72 | 77.97
2017-05-21 13:00 | 105.78 | 83.5
2017-05-21 13:30 | 103.13 | 79.4
2017-05-21 14:00 | 103.49 | 79.61
2017-05-21 14:30 | 100.39 | 75.62
2017-05-21 15:00 | 101.16 | 76.49
2017-05-21 15:30 | 102 | 79.21
2017-05-21 16:00 | 110.06 | 90.25
2017-05-21 16:30 | 108.16 | 84.78
2017-05-21 17:00 | 116.35 | 95.88
2017-05-21 17:30 | 109.93 | 88.07
2017-05-21 18:00 | 109.3 | 89.45
2017-05-21 18:30 | 100.6 | 74.89
2017-05-21 19:00 | 107.42 | 86.73
2017-05-21 19:30 | 106.55 | 86.86
2017-05-21 20:00 | 104.57 | 86.82
2017-05-21 20:30 | 108.77 | 92.1
2017-05-21 21:00 | 107.02 | 86.52
2017-05-21 21:30 | 105.57 | 86.08
2017-05-21 22:00 | 102.61 | 82.02
2017-05-21 22:30 | 101.96 | 78.77
2017-05-21 23:00 | 106.52 | 84.72
2017-05-21 23:30 | 107.7 | 86.31
2017-05-22 | 103.31 | 81.4
2017-05-22 00:30 | 106.46 | 86.36
2017-05-22 01:00 | 109.53 | 91.51
2017-05-22 01:30 | 105.66 | 84.69
2017-05-22 02:00 | 111.44 | 91.49
2017-05-22 02:30 | 116.9 | 99.73
2017-05-22 03:00 | 116.86 | 99.64
2017-05-22 03:30 | 113.45 | 94.93
2017-05-22 04:00 | 105.15 | 83.79
2017-05-22 04:30 | 110.29 | 91.17
2017-05-22 05:00 | 103.54 | 82.43
2017-05-22 05:30 | 105.82 | 84.49
2017-05-22 06:00 | 105.38 | 85.55
2017-05-22 06:30 | 103.37 | 81.63
2017-05-22 07:00 | 105.39 | 85.35
2017-05-22 07:30 | 108.09 | 91.46
2017-05-22 08:00 | 103.74 | 84.89
2017-05-22 08:30 | 108.19 | 90.26
2017-05-22 09:00 | 109.15 | 91.52
2017-05-22 09:30 | 107.63 | 89.74
2017-05-22 10:00 | 104.89 | 86.61
2017-05-22 10:30 | 103.16 | 84.4
2017-05-22 11:00 | 111.1 | 93.32
2017-05-22 11:30 | 107.54 | 88.56
2017-05-22 12:00 | 105.72 | 86.26
2017-05-22 12:30 | 104.39 | 85.11
2017-05-22 13:00 | 101.69 | 80.39
2017-05-22 13:30 | 107.29 | 87.41
2017-05-22 14:00 | 113.96 | 97.02
2017-05-22 14:30 | 108.72 | 91.21
2017-05-22 15:00 | 109.13 | 91.28
2017-05-22 15:30 | 110.36 | 93.43
2017-05-22 16:00 | 103.8 | 85.9
2017-05-22 16:30 | 104.37 | 86.12
2017-05-22 17:00 | 104.98 | 86.37
2017-05-22 17:30 | 108.91 | 92.75
2017-05-22 18:00 | 112.75 | 96.33
2017-05-22 18:30 | 112.62 | 95.49
2017-05-22 19:00 | 112.85 | 97.66
2017-05-22 19:30 | 114.92 | 100.43
2017-05-22 20:00 | 113.85 | 99.03
2017-05-22 20:30 | 115.02 | 100.13
2017-05-22 21:00 | 112 | 95.71
2017-05-22 21:30 | 113.77 | 96.81
2017-05-22 22:00 | 115.74 | 98.65
2017-05-22 22:30 | 111.03 | 92.92
2017-05-22 23:00 | 113.81 | 96.38
2017-05-22 23:30 | 119.11 | 102.39
2017-05-23 | 119.53 | 104.13
2017-05-23 00:30 | 118.34 | 101.07
2017-05-23 01:00 | 128 | 112.87
2017-05-23 01:30 | 120.02 | 102.18
2017-05-23 02:00 | 120.78 | 103.76
2017-05-23 02:30 | 118.88 | 101.56
2017-05-23 03:00 | 121.2 | 104.12
2017-05-23 03:30 | 119.53 | 101.99
2017-05-23 04:00 | 117.31 | 100.52
2017-05-23 04:30 | 117.94 | 100.32
2017-05-23 05:00 | 120.93 | 103.57
2017-05-23 05:30 | 120.13 | 103.48
2017-05-23 06:00 | 126.21 | 111.09
2017-05-23 06:30 | 112.53 | 93.3
2017-05-23 07:00 | 119.18 | 101.8
2017-05-23 07:30 | 118.26 | 100.12
2017-05-23 08:00 | 118.95 | 102.16
2017-05-23 08:30 | 114.12 | 93.81
2017-05-23 09:00 | 111.36 | 90.67
2017-05-23 09:30 | 106.37 | 83.62
2017-05-23 10:00 | 107.98 | 86.85
2017-05-23 10:30 | 113.6 | 93.04
2017-05-23 11:00 | 112.33 | 89.43
2017-05-23 11:30 | 113.91 | 92.71
2017-05-23 12:00 | 120.07 | 100.98
2017-05-23 12:30 | 120.48 | 102.14
2017-05-23 13:00 | 119.15 | 99.16
2017-05-23 13:30 | 114.66 | 93.85
2017-05-23 14:00 | 113.6 | 90.42
2017-05-23 14:30 | 113.54 | 90.88
2017-05-23 15:00 | 107.06 | 82.33
2017-05-23 15:30 | 113.78 | 90.52
2017-05-23 16:00 | 119.8 | 97.84
2017-05-23 16:30 | 124.11 | 104.49
2017-05-23 17:00 | 129.56 | 112.47
2017-05-23 17:30 | 121.99 | 102.69
2017-05-23 18:00 | 126.04 | 108.83
2017-05-23 18:30 | 124.78 | 106.31
2017-05-23 19:00 | 122.59 | 104.63
2017-05-23 19:30 | 118.4 | 99.05
2017-05-23 20:00 | 125.61 | 107.25
2017-05-23 20:30 | 133.34 | 117.9
2017-05-23 21:00 | 126.13 | 109.61
2017-05-23 21:30 | 123.98 | 107.27
2017-05-23 22:00 | 121.94 | 104.7
2017-05-23 22:30 | 121.44 | 104.61
2017-05-23 23:00 | 121.7 | 103.52
2017-05-23 23:30 | 121.94 | 102.71
2017-05-24 | 118.45 | 99.35
2017-05-24 00:30 | 125.11 | 107.79
2017-05-24 01:00 | 121.47 | 103.29
2017-05-24 01:30 | 114.47 | 93.72
2017-05-24 02:00 | 113.39 | 92.4
2017-05-24 02:30 | 116.41 | 97.42
2017-05-24 03:00 | 120.15 | 101.34
2017-05-24 03:30 | 113.2 | 91.92
2017-05-24 04:00 | 112.57 | 91.35
2017-05-24 04:30 | 113.41 | 92.03
2017-05-24 05:00 | 117.14 | 96.83
2017-05-24 05:30 | 116.98 | 97.44
2017-05-24 06:00 | 114.08 | 92.69
2017-05-24 06:30 | 112.39 | 90.02
2017-05-24 07:00 | 112.18 | 91.29
2017-05-24 07:30 | 107.37 | 87.81
2017-05-24 08:00 | 111.38 | 91.91
2017-05-24 08:30 | 109.23 | 87.41
2017-05-24 09:00 | 111.67 | 92.95
2017-05-24 09:30 | 111.52 | 90.15
2017-05-24 10:00 | 110.17 | 88
2017-05-24 10:30 | 105.86 | 83.75
2017-05-24 11:00 | 115.76 | 95.61
2017-05-24 11:30 | 117.64 | 98.24
2017-05-24 12:00 | 117.59 | 98.63
2017-05-24 12:30 | 118.53 | 99.65
2017-05-24 13:00 | 113.03 | 92.62
2017-05-24 13:30 | 112.31 | 91.09
2017-05-24 14:00 | 113.16 | 92.3
2017-05-24 14:30 | 114.63 | 93.71
2017-05-24 15:00 | 110.57 | 90.78
2017-05-24 15:30 | 105.84 | 84.11
2017-05-24 16:00 | 112.88 | 92.05
2017-05-24 16:30 | 109.93 | 88.44
2017-05-24 17:00 | 111.37 | 91.27
2017-05-24 17:30 | 112.1 | 91.23
2017-05-24 18:00 | 113.89 | 92.64
2017-05-24 18:30 | 114.56 | 93.6
2017-05-24 19:00 | 110.44 | 89.91
2017-05-24 19:30 | 111.87 | 94.14
2017-05-24 20:00 | 110.23 | 92
2017-05-24 20:30 | 114.64 | 94.12
2017-05-24 21:00 | 114.92 | 93.4
2017-05-24 21:30 | 112.81 | 91.3
2017-05-24 22:00 | 114.25 | 93.3
2017-05-24 22:30 | 117.14 | 97.14
2017-05-24 23:00 | 115.15 | 94.88
2017-05-24 23:30 | 117.13 | 95.76
2017-05-25 | 118.8 | 98.02
2017-05-25 00:30 | 121.76 | 102.16
2017-05-25 01:00 | 126.37 | 109.81
2017-05-25 01:30 | 118.81 | 98.75
2017-05-25 02:00 | 120.34 | 100.14
2017-05-25 02:30 | 119.25 | 96.67
2017-05-25 03:00 | 117.89 | 94.69
2017-05-25 03:30 | 118.17 | 95.69
2017-05-25 04:00 | 122.14 | 101.02
2017-05-25 04:30 | 122.16 | 101.04
2017-05-25 05:00 | 122.03 | 100.82
2017-05-25 05:30 | 116.71 | 94.31
2017-05-25 06:00 | 118.82 | 97.72
2017-05-25 06:30 | 108.06 | 80.85
2017-05-25 07:00 | 110.3 | 84.54
2017-05-25 07:30 | 115.96 | 91.82
2017-05-25 08:00 | 112.85 | 86.15
2017-05-25 08:30 | 112.53 | 88.35
2017-05-25 09:00 | 114.3 | 90.11
2017-05-25 09:30 | 112.1 | 86.63
2017-05-25 10:00 | 110.63 | 84.57
2017-05-25 10:30 | 115.06 | 93.06
2017-05-25 11:00 | 116.11 | 93.64
2017-05-25 11:30 | 114.24 | 90.48
2017-05-25 12:00 | 114.98 | 90.61
2017-05-25 12:30 | 122.8 | 102.12
2017-05-25 13:00 | 125.54 | 106.53
2017-05-25 13:30 | 111.49 | 85.23
2017-05-25 14:00 | 115.42 | 92.4
2017-05-25 14:30 | 117.07 | 93.84
2017-05-25 15:00 | 114.18 | 90.71
2017-05-25 15:30 | 110.77 | 84.9
2017-05-25 16:00 | 111.08 | 85.14
2017-05-25 16:30 | 109.1 | 82.88
2017-05-25 17:00 | 110.77 | 86.87
2017-05-25 17:30 | 115.75 | 93.26
2017-05-25 18:00 | 118.51 | 98.41
2017-05-25 18:30 | 118.31 | 96.82
2017-05-25 19:00 | 128.02 | 110.76
2017-05-25 19:30 | 126.85 | 108.19
2017-05-25 20:00 | 127.95 | 109.98
2017-05-25 20:30 | 124.66 | 105.81
2017-05-25 21:00 | 124.18 | 104.52
2017-05-25 21:30 | 121.48 | 101.16
2017-05-25 22:00 | 116.82 | 94.68
2017-05-25 22:30 | 119.23 | 97.34
2017-05-25 23:00 | 119.97 | 98.22
2017-05-25 23:30 | 123.97 | 103.68
2017-05-26 | 124.07 | 102.28
2017-05-26 00:30 | 121.72 | 99.48
2017-05-26 01:00 | 120.35 | 97.32
2017-05-26 01:30 | 124.49 | 104.59
2017-05-26 02:00 | 121.63 | 101.43
2017-05-26 02:30 | 122.85 | 102.75
2017-05-26 03:00 | 115.95 | 94.24
2017-05-26 03:30 | 115.62 | 94.1
2017-05-26 04:00 | 118.51 | 97.83
2017-05-26 04:30 | 121.43 | 101.6
2017-05-26 05:00 | 115.76 | 93.79
2017-05-26 05:30 | 117.01 | 95.2
2017-05-26 06:00 | 118.25 | 97.49
2017-05-26 06:30 | 116.18 | 94.37
2017-05-26 07:00 | 119.06 | 99.19
2017-05-26 07:30 | 127.37 | 112.03
2017-05-26 08:00 | 115.3 | 96.06
2017-05-26 08:30 | 113.76 | 94.2
2017-05-26 09:00 | 114.23 | 94.45
2017-05-26 09:30 | 112.88 | 91.29
2017-05-26 10:00 | 110.61 | 90.3
2017-05-26 10:30 | 113.78 | 94.24
2017-05-26 11:00 | 114.91 | 95.01
2017-05-26 11:30 | 116.79 | 97.69
2017-05-26 12:00 | 112.69 | 92.82
2017-05-26 12:30 | 117.12 | 99.94
2017-05-26 13:00 | 114.75 | 95.67
2017-05-26 13:30 | 115.55 | 96.6
2017-05-26 14:00 | 113.4 | 93.8
2017-05-26 14:30 | 113.12 | 93.02
2017-05-26 15:00 | 113.25 | 93.05
2017-05-26 15:30 | 114.58 | 94.27
2017-05-26 16:00 | 111.93 | 94.6
2017-05-26 16:30 | 115.8 | 99.34
2017-05-26 17:00 | 116.13 | 98.82
2017-05-26 17:30 | 120.84 | 103.81
2017-05-26 18:00 | 116.76 | 97.12
2017-05-26 18:30 | 115.28 | 95.51
2017-05-26 19:00 | 117.37 | 98.87
2017-05-26 19:30 | 119.31 | 100.92
2017-05-26 20:00 | 114.93 | 94.32
2017-05-26 20:30 | 116.73 | 98.59
2017-05-26 21:00 | 114.15 | 93.15
2017-05-26 21:30 | 112.62 | 92.26
2017-05-26 22:00 | 113.88 | 92.24
2017-05-26 22:30 | 114.89 | 92.67
2017-05-26 23:00 | 113.36 | 90.52
2017-05-26 23:30 | 110.85 | 86.52
2017-05-27 | 115.63 | 94.73
2017-05-27 00:30 | 114.77 | 93.43
2017-05-27 01:00 | 120.51 | 102.71
2017-05-27 01:30 | 121.11 | 103.33
2017-05-27 02:00 | 119.32 | 100.23
2017-05-27 02:30 | 115.65 | 94.96
2017-05-27 03:00 | 119.94 | 100.04
2017-05-27 03:30 | 116.44 | 94.72
2017-05-27 04:00 | 115.99 | 94.78
2017-05-27 04:30 | 116.19 | 95.27
2017-05-27 05:00 | 113.41 | 92.47
2017-05-27 05:30 | 112.16 | 90.57
2017-05-27 06:00 | 116.83 | 97.45
2017-05-27 06:30 | 108.98 | 86.12
2017-05-27 07:00 | 111.24 | 90.91
2017-05-27 07:30 | 114.8 | 95.34
2017-05-27 08:00 | 113.37 | 94.44
2017-05-27 08:30 | 108.54 | 89.22
2017-05-27 09:00 | 107.18 | 87.82
2017-05-27 09:30 | 110.14 | 90.7
2017-05-27 10:00 | 112.73 | 93.86
2017-05-27 10:30 | 111.77 | 92.79
2017-05-27 11:00 | 108.49 | 88.51
2017-05-27 11:30 | 106.85 | 83.79
2017-05-27 12:00 | 115.92 | 97.37
2017-05-27 12:30 | 121.46 | 104.62
2017-05-27 13:00 | 120.85 | 103.67
2017-05-27 13:30 | 117.96 | 99.98
2017-05-27 14:00 | 117.67 | 99.01
2017-05-27 14:30 | 112.81 | 92.7
2017-05-27 15:00 | 113.3 | 94.28
2017-05-27 15:30 | 121.45 | 103.33
2017-05-27 16:00 | 119.74 | 100.86
2017-05-27 16:30 | 119.83 | 103.15
2017-05-27 17:00 | 115.89 | 96.82
2017-05-27 17:30 | 112.18 | 92.61
2017-05-27 18:00 | 112.82 | 93.84
2017-05-27 18:30 | 109.57 | 86.47
2017-05-27 19:00 | 117.12 | 98.88
2017-05-27 19:30 | 122.46 | 105.79
2017-05-27 20:00 | 117.57 | 98.67
2017-05-27 20:30 | 121.51 | 104.03
2017-05-27 21:00 | 114.9 | 95.37
2017-05-27 21:30 | 119.41 | 101.25
2017-05-27 22:00 | 115.18 | 95.59
2017-05-27 22:30 | 109.97 | 90.42
2017-05-27 23:00 | 108.3 | 87.55
2017-05-27 23:30 | 115.79 | 95.92
2017-05-28 | 118.12 | 98.18
2017-05-28 00:30 | 117.65 | 97.11
2017-05-28 01:00 | 116.37 | 94.69
2017-05-28 01:30 | 118.48 | 98.96
2017-05-28 02:00 | 118.98 | 98.62
2017-05-28 02:30 | 119.01 | 98.19
2017-05-28 03:00 | 116.8 | 95.67
2017-05-28 03:30 | 120.57 | 101.04
2017-05-28 04:00 | 122.35 | 102.48
2017-05-28 04:30 | 122.52 | 102.7
2017-05-28 05:00 | 121.98 | 102.15
2017-05-28 05:30 | 122.26 | 102.4
2017-05-28 06:00 | 119.5 | 98.15
2017-05-28 06:30 | 114.56 | 92.41
2017-05-28 07:00 | 110.74 | 88.32
2017-05-28 07:30 | 115.29 | 94.16
2017-05-28 08:00 | 117.37 | 96.26
2017-05-28 08:30 | 120.88 | 101.99
2017-05-28 09:00 | 122.8 | 104.4
2017-05-28 09:30 | 120.48 | 100.6
2017-05-28 10:00 | 120.2 | 101.5
2017-05-28 10:30 | 119.9 | 101.23
2017-05-28 11:00 | 115.58 | 96.57
2017-05-28 11:30 | 116.66 | 97.12
2017-05-28 12:00 | 114.13 | 93.67
2017-05-28 12:30 | 118.31 | 100.19
2017-05-28 13:00 | 122.42 | 106.44
2017-05-28 13:30 | 115.64 | 97.73
2017-05-28 14:00 | 122.15 | 106.28
2017-05-28 14:30 | 119.44 | 102.71
2017-05-28 15:00 | 118.74 | 100.99
2017-05-28 15:30 | 116.94 | 100.14
2017-05-28 16:00 | 119.74 | 102.87
2017-05-28 16:30 | 124.9 | 109.23
2017-05-28 17:00 | 119.58 | 102.92
2017-05-28 17:30 | 119.95 | 104.84
2017-05-28 18:00 | 120.22 | 105.94
2017-05-28 18:30 | 117.85 | 101.8
2017-05-28 19:00 | 114.11 | 97.38
2017-05-28 19:30 | 110.43 | 91.25
2017-05-28 20:00 | 115.64 | 98.23
2017-05-28 20:30 | 119.88 | 103.41
2017-05-28 21:00 | 116.03 | 99.84
2017-05-28 21:30 | 111.22 | 94.06
2017-05-28 22:00 | 109.54 | 91.75
2017-05-28 22:30 | 106.03 | 86.07
2017-05-28 23:00 | 111.44 | 93.05
2017-05-28 23:30 | 113.03 | 93.64
2017-05-29 | 111.72 | 92.69
2017-05-29 00:30 | 106.79 | 86.33
2017-05-29 01:00 | 107.32 | 85.74
2017-05-29 01:30 | 109.68 | 89.16
2017-05-29 02:00 | 109.72 | 88.86
2017-05-29 02:30 | 106.92 | 85.58
2017-05-29 03:00 | 110.14 | 89.4
2017-05-29 03:30 | 107.58 | 85.27
2017-05-29 04:00 | 109.08 | 88.46
2017-05-29 04:30 | 106.9 | 85.89
2017-05-29 05:00 | 102.59 | 80.8
2017-05-29 05:30 | 99.19 | 78.06
2017-05-29 06:00 | 96.7 | 76.87
2017-05-29 06:30 | 87.8 | 65.65
2017-05-29 07:00 | 90.64 | 73.85
2017-05-29 07:30 | 86.5 | 79.27
2017-05-29 08:00 | 87.52 | 80.42
2017-05-29 08:30 | 85.99 | 77.99
2017-05-29 09:00 | 80.68 | 71.11
2017-05-29 09:30 | 79.75 | 69.82
2017-05-29 10:00 | 79.39 | 69.07
2017-05-29 10:30 | 81.8 | 72.58
2017-05-29 11:00 | 82.96 | 73.71
2017-05-29 11:30 | 79.28 | 69.85
2017-05-29 12:00 | 82.22 | 71.95
2017-05-29 12:30 | 82.89 | 71.15
2017-05-29 13:00 | 85.14 | 73.04
2017-05-29 13:30 | 86.44 | 74.64
2017-05-29 14:00 | 90.3 | 79.63
2017-05-29 14:30 | 89.4 | 76.81
2017-05-29 15:00 | 91.28 | 79.03
2017-05-29 15:30 | 91.39 | 79.41
2017-05-29 16:00 | 87.59 | 75.65
2017-05-29 16:30 | 95.04 | 83.31
2017-05-29 17:00 | 98.07 | 80.98
2017-05-29 17:30 | 105.46 | 85.81
2017-05-29 18:00 | 105.96 | 88.13
2017-05-29 18:30 | 100.92 | 80.37
2017-05-29 19:00 | 109.38 | 92.18
2017-05-29 19:30 | 112.34 | 95.68
2017-05-29 20:00 | 110.44 | 91.94
2017-05-29 20:30 | 112.36 | 94.09
2017-05-29 21:00 | 111.11 | 91.62
2017-05-29 21:30 | 109.04 | 88.7
2017-05-29 22:00 | 109.73 | 88.99
2017-05-29 22:30 | 107.4 | 86.39
2017-05-29 23:00 | 111.85 | 90.84
2017-05-29 23:30 | 114.03 | 94.1
2017-05-30 | 114.6 | 94.27
2017-05-30 00:30 | 103.73 | 79.84
2017-05-30 01:00 | 102.42 | 78.61
2017-05-30 01:30 | 105.4 | 82.52
2017-05-30 02:00 | 113.09 | 91.74
2017-05-30 02:30 | 113.98 | 93.2
2017-05-30 03:00 | 111.74 | 90.43
2017-05-30 03:30 | 109.27 | 87.49
2017-05-30 04:00 | 109.99 | 86.26
2017-05-30 04:30 | 111.77 | 89.2
2017-05-30 05:00 | 109.82 | 88.13
2017-05-30 05:30 | 105.92 | 82.88
2017-05-30 06:00 | 111.82 | 91.6
2017-05-30 06:30 | 112.84 | 92.27
2017-05-30 07:00 | 117.25 | 98.85
2017-05-30 07:30 | 116.98 | 98.94
2017-05-30 08:00 | 111.68 | 93.15
2017-05-30 08:30 | 116 | 96.52
2017-05-30 09:00 | 107.78 | 89.34
2017-05-30 09:30 | 101.83 | 81.48
2017-05-30 10:00 | 107.31 | 86.99
2017-05-30 10:30 | 114.37 | 94.31
2017-05-30 11:00 | 113.03 | 92.55
2017-05-30 11:30 | 113.33 | 93.31
2017-05-30 12:00 | 111.95 | 90.83
2017-05-30 12:30 | 111.75 | 91.43
2017-05-30 13:00 | 114.03 | 95.07
2017-05-30 13:30 | 109.83 | 89.66
2017-05-30 14:00 | 113.34 | 93.74
2017-05-30 14:30 | 119.17 | 101.18
2017-05-30 15:00 | 120.85 | 103.34
2017-05-30 15:30 | 116.42 | 94.95
2017-05-30 16:00 | 119.87 | 100.57
2017-05-30 16:30 | 128.47 | 112.79
2017-05-30 17:00 | 126.61 | 110.4
2017-05-30 17:30 | 125.39 | 109.11
2017-05-30 18:00 | 125.66 | 110.62
2017-05-30 18:30 | 123.56 | 105.15
2017-05-30 19:00 | 129.07 | 112.83
2017-05-30 19:30 | 126.26 | 110.36
2017-05-30 20:00 | 123.68 | 107.74
2017-05-30 20:30 | 128.05 | 112.38
2017-05-30 21:00 | 124.2 | 106.52
2017-05-30 21:30 | 128.81 | 112.92
2017-05-30 22:00 | 127.46 | 110.85
2017-05-30 22:30 | 126.53 | 109.07
2017-05-30 23:00 | 126.37 | 107.95
2017-05-30 23:30 | 120.37 | 101.02
2017-05-31 | 119.54 | 99.8
2017-05-31 00:30 | 120.42 | 101.75
2017-05-31 01:00 | 128.42 | 111.47
2017-05-31 01:30 | 136.28 | 121.35
2017-05-31 02:00 | 130.66 | 114.2
2017-05-31 02:30 | 124.71 | 105.57
2017-05-31 03:00 | 122.14 | 103.82
2017-05-31 03:30 | 123.49 | 102.62
2017-05-31 04:00 | 126.29 | 107.46
2017-05-31 04:30 | 124.93 | 104.49
2017-05-31 05:00 | 115.44 | 94.07
2017-05-31 05:30 | 114.05 | 93.23
2017-05-31 06:00 | 115.04 | 94.74
2017-05-31 06:30 | 110.91 | 86.51
2017-05-31 07:00 | 106.18 | 81.5
2017-05-31 07:30 | 110.36 | 88.9
2017-05-31 08:00 | 110.53 | 88.33
2017-05-31 08:30 | 105.65 | 80.22
2017-05-31 09:00 | 111.02 | 85.8
2017-05-31 09:30 | 105.76 | 80.05
2017-05-31 10:00 | 108.83 | 85.36
2017-05-31 10:30 | 105.54 | 83.7
2017-05-31 11:00 | 105.4 | 82.56
2017-05-31 11:30 | 114.19 | 90.97
2017-05-31 12:00 | 107.61 | 81.13
2017-05-31 12:30 | 106.37 | 82.96
2017-05-31 13:00 | 111.45 | 89.97
2017-05-31 13:30 | 101.91 | 83.93
2017-05-31 14:00 | 108.17 | 83.86
2017-05-31 14:30 | 110.23 | 87.15
2017-05-31 15:00 | 110.03 | 85.7
2017-05-31 15:30 | 108.42 | 82.03
2017-05-31 16:00 | 112.79 | 92.82
2017-05-31 16:30 | 109.24 | 85.67
2017-05-31 17:00 | 110.2 | 86.09
2017-05-31 17:30 | 109.34 | 83.61
2017-05-31 18:00 | 110.55 | 86.95
2017-05-31 18:30 | 109.24 | 84.39
2017-05-31 19:00 | 112.98 | 92.16
2017-05-31 19:30 | 112.18 | 89.68
2017-05-31 20:00 | 114.89 | 92.85
2017-05-31 20:30 | 117.05 | 96.52
2017-05-31 21:00 | 118.27 | 98.5
2017-05-31 21:30 | 119.88 | 100.73
2017-05-31 22:00 | 119.95 | 99.44
2017-05-31 22:30 | 118.59 | 99.37
2017-05-31 23:00 | 117.31 | 96.61
2017-05-31 23:30 | 121.59 | 100.71
2017-06-01 | 115.22 | 94.55
2017-06-01 00:30 | 121.3 | 101.64
2017-06-01 01:00 | 125.08 | 105.47
2017-06-01 01:30 | 126.58 | 106.72
2017-06-01 02:00 | 120.06 | 98.85
2017-06-01 02:30 | 119.37 | 99.1
2017-06-01 03:00 | 113.97 | 90.17
2017-06-01 03:30 | 118.47 | 96.82
2017-06-01 04:00 | 122.35 | 102.27
2017-06-01 04:30 | 123.06 | 102.71
2017-06-01 05:00 | 123.24 | 103.55
2017-06-01 05:30 | 121.84 | 101.77
2017-06-01 06:00 | 119.25 | 98.96
2017-06-01 06:30 | 117.94 | 93.6
2017-06-01 07:00 | 116.27 | 93.61
2017-06-01 07:30 | 118.24 | 95.25
2017-06-01 08:00 | 118.85 | 95.47
2017-06-01 08:30 | 113.36 | 92.3
2017-06-01 09:00 | 118.37 | 100.18
2017-06-01 09:30 | 114.21 | 93.61
2017-06-01 10:00 | 116.75 | 95.48
2017-06-01 10:30 | 119.58 | 99.95
2017-06-01 11:00 | 112.29 | 88.04
2017-06-01 11:30 | 115.9 | 92.27
2017-06-01 12:00 | 119.35 | 97.26
2017-06-01 12:30 | 120.6 | 98.54
2017-06-01 13:00 | 120.07 | 99.94
2017-06-01 13:30 | 116.38 | 93.45
2017-06-01 14:00 | 124 | 103.2
2017-06-01 14:30 | 123.9 | 101.24
2017-06-01 15:00 | 121.72 | 97.48
2017-06-01 15:30 | 117.07 | 90.72
2017-06-01 16:00 | 122.42 | 99.94
2017-06-01 16:30 | 121.62 | 99.17
2017-06-01 17:00 | 117.69 | 93.78
2017-06-01 17:30 | 127.95 | 107.36
2017-06-01 18:00 | 128.03 | 110.24
2017-06-01 18:30 | 123.05 | 101.92
2017-06-01 19:00 | 128.73 | 111.06
2017-06-01 19:30 | 130.66 | 113.3
2017-06-01 20:00 | 131.45 | 114.75
2017-06-01 20:30 | 131.84 | 116.32
2017-06-01 21:00 | 130.3 | 113.88
2017-06-01 21:30 | 130.11 | 113.38
2017-06-01 22:00 | 129.43 | 112.68
2017-06-01 22:30 | 129.15 | 112.12
2017-06-01 23:00 | 123.8 | 106.67
2017-06-01 23:30 | 122.71 | 104.96
2017-06-02 | 121.91 | 104.07
2017-06-02 00:30 | 126.51 | 109.37
2017-06-02 01:00 | 125.81 | 109.19
2017-06-02 01:30 | 125.82 | 109.03
2017-06-02 02:00 | 125.68 | 109.58
2017-06-02 02:30 | 132.97 | 118.84
2017-06-02 03:00 | 128.81 | 111.66
2017-06-02 03:30 | 124.15 | 105.93
2017-06-02 04:00 | 119.15 | 101.2
2017-06-02 04:30 | 126.5 | 110.44
2017-06-02 05:00 | 126.36 | 109.25
2017-06-02 05:30 | 128.72 | 111.85
2017-06-02 06:00 | 121.43 | 103.68
2017-06-02 06:30 | 116.12 | 94.46
2017-06-02 07:00 | 122.88 | 104.1
2017-06-02 07:30 | 119.69 | 102.74
2017-06-02 08:00 | 124.69 | 107.81
2017-06-02 08:30 | 121.69 | 105.21
2017-06-02 09:00 | 120.43 | 103.57
2017-06-02 09:30 | 114.13 | 94.64
2017-06-02 10:00 | 120.59 | 102.39
2017-06-02 10:30 | 117.56 | 98.72
2017-06-02 11:00 | 113.62 | 92.37
2017-06-02 11:30 | 108.33 | 87.18
2017-06-02 12:00 | 106.13 | 83.43
2017-06-02 12:30 | 106.78 | 86.8
2017-06-02 13:00 | 112.55 | 92.91
2017-06-02 13:30 | 116.39 | 98.21
2017-06-02 14:00 | 116.57 | 99.94
2017-06-02 14:30 | 116.62 | 101.23
2017-06-02 15:00 | 118.13 | 100.94
2017-06-02 15:30 | 108.81 | 87.16
2017-06-02 16:00 | 122.18 | 103.51
2017-06-02 16:30 | 125.52 | 108.14
2017-06-02 17:00 | 121.19 | 102.44
2017-06-02 17:30 | 124.3 | 105.95
2017-06-02 18:00 | 124.5 | 107.43
2017-06-02 18:30 | 119.74 | 99.64
2017-06-02 19:00 | 127.63 | 111.27
2017-06-02 19:30 | 122.13 | 104.55
2017-06-02 20:00 | 124.22 | 106.23
2017-06-02 20:30 | 126.26 | 109.39
2017-06-02 21:00 | 125.35 | 107.83
2017-06-02 21:30 | 123.75 | 106.43
2017-06-02 22:00 | 119.27 | 101.7
2017-06-02 22:30 | 124.78 | 107.02
2017-06-02 23:00 | 127.91 | 110.71
2017-06-02 23:30 | 120.09 | 100.19
2017-06-03 | 122.2 | 103.07
2017-06-03 00:30 | 121.26 | 102.31
2017-06-03 01:00 | 116.61 | 96.73
2017-06-03 01:30 | 118.56 | 98.57
2017-06-03 02:00 | 115.47 | 96.65
2017-06-03 02:30 | 121.07 | 103.69
2017-06-03 03:00 | 120.25 | 101.24
2017-06-03 03:30 | 117.5 | 97.86
2017-06-03 04:00 | 122.64 | 104.55
2017-06-03 04:30 | 115.76 | 96.05
2017-06-03 05:00 | 114.95 | 94.53
2017-06-03 05:30 | 112.23 | 91
2017-06-03 06:00 | 116.1 | 95.93
2017-06-03 06:30 | 107.45 | 82.97
2017-06-03 07:00 | 115.06 | 94.2
2017-06-03 07:30 | 119.39 | 100.58
2017-06-03 08:00 | 117.06 | 97.69
2017-06-03 08:30 | 115.47 | 95.95
2017-06-03 09:00 | 118.87 | 100.16
2017-06-03 09:30 | 118.08 | 100.92
2017-06-03 10:00 | 119.21 | 101.87
2017-06-03 10:30 | 118.59 | 101.92
2017-06-03 11:00 | 112.67 | 93.64
2017-06-03 11:30 | 115.22 | 96.35
2017-06-03 12:00 | 112.61 | 91.48
2017-06-03 12:30 | 122.46 | 104.71
2017-06-03 13:00 | 125.96 | 110.7
2017-06-03 13:30 | 116.93 | 98.71
2017-06-03 14:00 | 120.15 | 105.06
2017-06-03 14:30 | 119.09 | 101.9
2017-06-03 15:00 | 121.15 | 104.73
2017-06-03 15:30 | 107.72 | 86.96
2017-06-03 16:00 | 111.9 | 92.81
2017-06-03 16:30 | 118.52 | 100.01
2017-06-03 17:00 | 121.25 | 103.01
2017-06-03 17:30 | 126.46 | 110.16
2017-06-03 18:00 | 130.56 | 116.44
2017-06-03 18:30 | 123.17 | 106.53
2017-06-03 19:00 | 123.44 | 107.87
2017-06-03 19:30 | 130.54 | 116.26
2017-06-03 20:00 | 126.75 | 111.66
2017-06-03 20:30 | 120.21 | 103.5
2017-06-03 21:00 | 119.67 | 103.77
2017-06-03 21:30 | 124.55 | 108.86
2017-06-03 22:00 | 118.67 | 101.87
2017-06-03 22:30 | 116.52 | 97.8
2017-06-03 23:00 | 111.39 | 92.16
2017-06-03 23:30 | 105.6 | 85.63
2017-06-04 | 109.53 | 89.05
2017-06-04 00:30 | 113.24 | 94.31
2017-06-04 01:00 | 119.06 | 100.95
2017-06-04 01:30 | 118.53 | 99.76
2017-06-04 02:00 | 126.5 | 110.29
2017-06-04 02:30 | 119.43 | 100.25
2017-06-04 03:00 | 124.18 | 105.09
2017-06-04 03:30 | 117.63 | 98.13
2017-06-04 04:00 | 125.54 | 107.65
2017-06-04 04:30 | 123.63 | 106.08
2017-06-04 05:00 | 127 | 110.53
2017-06-04 05:30 | 119.16 | 99.63
2017-06-04 06:00 | 127.58 | 111.07
2017-06-04 06:30 | 118.35 | 96.58
2017-06-04 07:00 | 119.32 | 99.02
2017-06-04 07:30 | 123.6 | 106.73
2017-06-04 08:00 | 127.45 | 109.71
2017-06-04 08:30 | 124.53 | 105.24
2017-06-04 09:00 | 119.87 | 98.9
2017-06-04 09:30 | 118.33 | 98.57
2017-06-04 10:00 | 119.29 | 100.79
2017-06-04 10:30 | 122.44 | 103.96
2017-06-04 11:00 | 117.29 | 97.4
2017-06-04 11:30 | 118.21 | 98.61
2017-06-04 12:00 | 116.72 | 97.05
2017-06-04 12:30 | 113.89 | 94.44
2017-06-04 13:00 | 110.29 | 86.12
2017-06-04 13:30 | 113.6 | 92.83
2017-06-04 14:00 | 114.84 | 95.18
2017-06-04 14:30 | 116.8 | 98.43
2017-06-04 15:00 | 118.76 | 101.15
2017-06-04 15:30 | 122.63 | 105.93
2017-06-04 16:00 | 125.05 | 109.45
2017-06-04 16:30 | 123.07 | 106.65
2017-06-04 17:00 | 121.4 | 106.37
2017-06-04 17:30 | 122.02 | 108.37
2017-06-04 18:00 | 116.54 | 102.3
2017-06-04 18:30 | 117.81 | 99.49
2017-06-04 19:00 | 126.66 | 110.02
2017-06-04 19:30 | 123.39 | 107
2017-06-04 20:00 | 124.34 | 107.77
2017-06-04 20:30 | 121.98 | 104.19
2017-06-04 21:00 | 129.04 | 112.75
2017-06-04 21:30 | 121.47 | 105.2
2017-06-04 22:00 | 128.82 | 114.56
2017-06-04 22:30 | 120.74 | 103.89
2017-06-04 23:00 | 115.6 | 96.38
2017-06-04 23:30 | 122.37 | 105.56
2017-06-05 | 121.28 | 102.92
2017-06-05 00:30 | 123.33 | 105.26
2017-06-05 01:00 | 117.73 | 97.64
2017-06-05 01:30 | 121.85 | 102.91
2017-06-05 02:00 | 123.67 | 106.5
2017-06-05 02:30 | 118.34 | 99.53
2017-06-05 03:00 | 112.51 | 92.24
2017-06-05 03:30 | 106.01 | 84.25
2017-06-05 04:00 | 112.57 | 93.08
2017-06-05 04:30 | 116.51 | 98.4
2017-06-05 05:00 | 117.22 | 98.84
2017-06-05 05:30 | 116.91 | 100.2
2017-06-05 06:00 | 117.6 | 100.97
2017-06-05 06:30 | 116.07 | 97.3
2017-06-05 07:00 | 108.18 | 88.1
2017-06-05 07:30 | 111.27 | 93.7
2017-06-05 08:00 | 118.05 | 102.05
2017-06-05 08:30 | 120.16 | 104.78
2017-06-05 09:00 | 124.08 | 109.69
2017-06-05 09:30 | 122.94 | 107.8
2017-06-05 10:00 | 114.14 | 96.61
2017-06-05 10:30 | 119.5 | 102.84
2017-06-05 11:00 | 117.31 | 100.15
2017-06-05 11:30 | 119.56 | 101.81
2017-06-05 12:00 | 117.99 | 100.53
2017-06-05 12:30 | 115.81 | 98.59
2017-06-05 13:00 | 114.61 | 95.91
2017-06-05 13:30 | 116.4 | 97.34
2017-06-05 14:00 | 112.85 | 93.06
2017-06-05 14:30 | 109.59 | 89.42
2017-06-05 15:00 | 107.09 | 85.23
2017-06-05 15:30 | 106.28 | 88.16
2017-06-05 16:00 | 106.55 | 88.63
2017-06-05 16:30 | 112.73 | 96.32
2017-06-05 17:00 | 110.13 | 92.51
2017-06-05 17:30 | 111.24 | 94.43
2017-06-05 18:00 | 112.11 | 96.28
2017-06-05 18:30 | 111.7 | 96.01
2017-06-05 19:00 | 113.94 | 99.38
2017-06-05 19:30 | 116.98 | 102.58
2017-06-05 20:00 | 115.49 | 100.07
2017-06-05 20:30 | 118.57 | 103.51
2017-06-05 21:00 | 116.79 | 102.1
2017-06-05 21:30 | 116.37 | 101.77
2017-06-05 22:00 | 114.77 | 99.37
2017-06-05 22:30 | 121.07 | 106.49
2017-06-05 23:00 | 117.45 | 100.79
2017-06-05 23:30 | 119.69 | 104.09
2017-06-06 | 113.41 | 96.45
2017-06-06 00:30 | 113.17 | 95.77
2017-06-06 01:00 | 108.55 | 89.75
2017-06-06 01:30 | 116.53 | 99.72
2017-06-06 02:00 | 118.19 | 102.4
2017-06-06 02:30 | 113.64 | 97.15
2017-06-06 03:00 | 110.29 | 91.52
2017-06-06 03:30 | 114.92 | 98.21
2017-06-06 04:00 | 113.26 | 96.57
2017-06-06 04:30 | 112.29 | 95.35
2017-06-06 05:00 | 117.65 | 101.84
2017-06-06 05:30 | 118.69 | 103.77
2017-06-06 06:00 | 114.74 | 99.7
2017-06-06 06:30 | 111.31 | 94.81
2017-06-06 07:00 | 114.97 | 100.2
2017-06-06 07:30 | 121.36 | 108.64
2017-06-06 08:00 | 115.12 | 101.34
2017-06-06 08:30 | 104.99 | 85.58
2017-06-06 09:00 | 115.67 | 99.7
2017-06-06 09:30 | 103.15 | 83.27
2017-06-06 10:00 | 104.21 | 85.03
2017-06-06 10:30 | 108.79 | 89.92
2017-06-06 11:00 | 104.2 | 82.99
2017-06-06 11:30 | 104.09 | 83.64
2017-06-06 12:00 | 107.23 | 87.56
2017-06-06 12:30 | 106.23 | 85.32
2017-06-06 13:00 | 111.36 | 92.33
2017-06-06 13:30 | 110.83 | 91.9
2017-06-06 14:00 | 114.38 | 96.52
2017-06-06 14:30 | 117.79 | 100.9
2017-06-06 15:00 | 118.04 | 98.73
2017-06-06 15:30 | 114.41 | 96.1
2017-06-06 16:00 | 119.13 | 101.53
2017-06-06 16:30 | 118.86 | 100.23
2017-06-06 17:00 | 117.73 | 97.71
2017-06-06 17:30 | 120.59 | 101.93
2017-06-06 18:00 | 119.71 | 101.64
2017-06-06 18:30 | 115.02 | 97.32
2017-06-06 19:00 | 120.88 | 104.83
2017-06-06 19:30 | 125.42 | 110.55
2017-06-06 20:00 | 122.77 | 107.79
2017-06-06 20:30 | 121.26 | 106.04
2017-06-06 21:00 | 117 | 99.85
2017-06-06 21:30 | 113.53 | 95.28
2017-06-06 22:00 | 114.98 | 98.18
2017-06-06 22:30 | 119.18 | 103.93
2017-06-06 23:00 | 117.6 | 101.46
2017-06-06 23:30 | 113.6 | 94.79
2017-06-07 | 122.63 | 106.4
2017-06-07 00:30 | 127.74 | 113.22
2017-06-07 01:00 | 121.7 | 106.37
2017-06-07 01:30 | 120.47 | 104.68
2017-06-07 02:00 | 127.1 | 112.79
2017-06-07 02:30 | 118.84 | 102.67
2017-06-07 03:00 | 116.9 | 100.42
2017-06-07 03:30 | 116.58 | 99.74
2017-06-07 04:00 | 120.8 | 106.24
2017-06-07 04:30 | 119.9 | 105.51
2017-06-07 05:00 | 117.6 | 101.68
2017-06-07 05:30 | 119.63 | 103.8
2017-06-07 06:00 | 122.06 | 108.22
2017-06-07 06:30 | 112.59 | 96.65
2017-06-07 07:00 | 112.81 | 97.35
2017-06-07 07:30 | 116.3 | 101.58
2017-06-07 08:00 | 115.2 | 98.22
2017-06-07 08:30 | 117.58 | 101.26
2017-06-07 09:00 | 121.64 | 107.31
2017-06-07 09:30 | 120.35 | 106.48
2017-06-07 10:00 | 115.14 | 98.88
2017-06-07 10:30 | 112.16 | 92.77
2017-06-07 11:00 | 107 | 85.61
2017-06-07 11:30 | 107.72 | 85.75
2017-06-07 12:00 | 110.63 | 89.6
2017-06-07 12:30 | 108.72 | 88.08
2017-06-07 13:00 | 105.6 | 83.73
2017-06-07 13:30 | 106.38 | 85.85
2017-06-07 14:00 | 97.06 | 75.18
2017-06-07 14:30 | 101.94 | 81.46
2017-06-07 15:00 | 109.96 | 92.99
2017-06-07 15:30 | 115.01 | 98.75
2017-06-07 16:00 | 112.99 | 95.05
2017-06-07 16:30 | 111.57 | 92.91
2017-06-07 17:00 | 118.02 | 101.06
2017-06-07 17:30 | 118.44 | 101.89
2017-06-07 18:00 | 113.9 | 97.26
2017-06-07 18:30 | 109.99 | 91.71
2017-06-07 19:00 | 109.52 | 92.15
2017-06-07 19:30 | 117.81 | 102.87
2017-06-07 20:00 | 120.41 | 105.38
2017-06-07 20:30 | 118.25 | 103.13
2017-06-07 21:00 | 117.63 | 101.99
2017-06-07 21:30 | 119.1 | 104.09
2017-06-07 22:00 | 111.23 | 94.01
2017-06-07 22:30 | 117.25 | 100.59
2017-06-07 23:00 | 117.34 | 99.93
2017-06-07 23:30 | 115.05 | 96.57
2017-06-08 | 117.52 | 101.85
2017-06-08 00:30 | 114.24 | 97.34
2017-06-08 01:00 | 112.46 | 94.78
2017-06-08 01:30 | 118.51 | 102.22
2017-06-08 02:00 | 119.29 | 102.97
2017-06-08 02:30 | 120.35 | 104.77
2017-06-08 03:00 | 112.38 | 94.49
2017-06-08 03:30 | 109.1 | 90.18
2017-06-08 04:00 | 118.08 | 102.96
2017-06-08 04:30 | 116.07 | 100.06
2017-06-08 05:00 | 109.42 | 90.67
2017-06-08 05:30 | 109.68 | 91.88
2017-06-08 06:00 | 122.99 | 109.12
2017-06-08 06:30 | 112.89 | 96.41
2017-06-08 07:00 | 115.08 | 100.46
2017-06-08 07:30 | 115.45 | 100.49
2017-06-08 08:00 | 113.41 | 96.91
2017-06-08 08:30 | 108.79 | 92.25
2017-06-08 09:00 | 106.01 | 88.12
2017-06-08 09:30 | 108.1 | 89.77
2017-06-08 10:00 | 112.96 | 96.31
2017-06-08 10:30 | 113.55 | 96.2
2017-06-08 11:00 | 109.2 | 89.79
2017-06-08 11:30 | 109.44 | 89.56
2017-06-08 12:00 | 104.84 | 82.93
2017-06-08 12:30 | 107.25 | 86.52
2017-06-08 13:00 | 113.12 | 94.99
2017-06-08 13:30 | 107.86 | 88.25
2017-06-08 14:00 | 106.29 | 86.76
2017-06-08 14:30 | 98 | 73.95
2017-06-08 15:00 | 104.46 | 84.11
2017-06-08 15:30 | 99.87 | 77.3
2017-06-08 16:00 | 100.51 | 78.52
2017-06-08 16:30 | 104.98 | 85.03
2017-06-08 17:00 | 107.99 | 90.02
2017-06-08 17:30 | 109.37 | 92.66
2017-06-08 18:00 | 115.25 | 98.43
2017-06-08 18:30 | 110.56 | 93.03
2017-06-08 19:00 | 109.93 | 93.42
2017-06-08 19:30 | 110.68 | 94.43
2017-06-08 20:00 | 120.89 | 107.17
2017-06-08 20:30 | 119.09 | 105.14
2017-06-08 21:00 | 115.13 | 99.57
2017-06-08 21:30 | 113.96 | 97.6
2017-06-08 22:00 | 110.95 | 93.1
2017-06-08 22:30 | 118.08 | 101.57
2017-06-08 23:00 | 120.39 | 104.03
2017-06-08 23:30 | 123.74 | 108.73
2017-06-09 | 113.61 | 97.04
2017-06-09 00:30 | 111.18 | 94.15
2017-06-09 01:00 | 117.87 | 101.04
2017-06-09 01:30 | 118.42 | 102.61
2017-06-09 02:00 | 109.03 | 90.74
2017-06-09 02:30 | 113.09 | 95.13
2017-06-09 03:00 | 112.39 | 94.33
2017-06-09 03:30 | 114.99 | 96.75
2017-06-09 04:00 | 111.69 | 92.59
2017-06-09 04:30 | 117.23 | 100.2
2017-06-09 05:00 | 113.21 | 95.23
2017-06-09 05:30 | 117.67 | 101.3
2017-06-09 06:00 | 112.87 | 94.83
2017-06-09 06:30 | 110.92 | 92.53
2017-06-09 07:00 | 113.43 | 96.9
2017-06-09 07:30 | 116.21 | 101.73
2017-06-09 08:00 | 117.27 | 101.04
2017-06-09 08:30 | 112.53 | 95.15
2017-06-09 09:00 | 108.89 | 90.57
2017-06-09 09:30 | 110.44 | 91.49
2017-06-09 10:00 | 112.59 | 95.13
2017-06-09 10:30 | 115.82 | 98.71
2017-06-09 11:00 | 118.32 | 102.25
2017-06-09 11:30 | 108.46 | 90.05
2017-06-09 12:00 | 107.04 | 86.4
2017-06-09 12:30 | 105.27 | 85.61
2017-06-09 13:00 | 109.96 | 92.33
2017-06-09 13:30 | 109.34 | 92.25
2017-06-09 14:00 | 111.32 | 95.06
2017-06-09 14:30 | 125.24 | 112.1
2017-06-09 15:00 | 116.19 | 100.66
2017-06-09 15:30 | 114.17 | 97.88
2017-06-09 16:00 | 112.07 | 94.72
2017-06-09 16:30 | 113.59 | 96.79
2017-06-09 17:00 | 110.89 | 94.1
2017-06-09 17:30 | 112.89 | 97.35
2017-06-09 18:00 | 121.56 | 107.04
2017-06-09 18:30 | 114.4 | 98.03
2017-06-09 19:00 | 117.66 | 102.62
2017-06-09 19:30 | 121.45 | 106.73
2017-06-09 20:00 | 113.94 | 98.81
2017-06-09 20:30 | 115.48 | 99.67
2017-06-09 21:00 | 119.41 | 103.94
2017-06-09 21:30 | 111.31 | 94.57
2017-06-09 22:00 | 110.96 | 94.41
2017-06-09 22:30 | 111.06 | 95.15
2017-06-09 23:00 | 112.79 | 98.56
2017-06-09 23:30 | 118.84 | 104.69
2017-06-10 | 117.37 | 102.7
2017-06-10 00:30 | 114.81 | 98.96
2017-06-10 01:00 | 109.41 | 92.36
2017-06-10 01:30 | 107.55 | 89.11
2017-06-10 02:00 | 113.14 | 96.42
2017-06-10 02:30 | 115.31 | 99.42
2017-06-10 03:00 | 109.95 | 92.6
2017-06-10 03:30 | 109.17 | 91.68
2017-06-10 04:00 | 108.79 | 91.72
2017-06-10 04:30 | 110.25 | 93.86
2017-06-10 05:00 | 112.6 | 97.51
2017-06-10 05:30 | 116.46 | 101.43
2017-06-10 06:00 | 120.45 | 106.24
2017-06-10 06:30 | 113.18 | 96.3
2017-06-10 07:00 | 114.3 | 97.57
2017-06-10 07:30 | 124.67 | 111.55
2017-06-10 08:00 | 119.07 | 104.16
2017-06-10 08:30 | 110.73 | 96.07
2017-06-10 09:00 | 107.66 | 94.03
2017-06-10 09:30 | 106.14 | 89.39
2017-06-10 10:00 | 104.13 | 85.64
2017-06-10 10:30 | 102.45 | 84.52
2017-06-10 11:00 | 105.55 | 85.35
2017-06-10 11:30 | 104.45 | 84.04
2017-06-10 12:00 | 102 | 80.39
2017-06-10 12:30 | 100.98 | 79.78
2017-06-10 13:00 | 99.64 | 78.68
2017-06-10 13:30 | 102.97 | 84.65
2017-06-10 14:00 | 105.06 | 87.33
2017-06-10 14:30 | 109.99 | 94.42
2017-06-10 15:00 | 107.13 | 89.25
2017-06-10 15:30 | 111.83 | 95.29
2017-06-10 16:00 | 112.67 | 95.6
2017-06-10 16:30 | 110.38 | 93.66
2017-06-10 17:00 | 113.27 | 96.41
2017-06-10 17:30 | 114.17 | 97.71
2017-06-10 18:00 | 109.38 | 92.63
2017-06-10 18:30 | 103.89 | 86.19
2017-06-10 19:00 | 108.66 | 92.89
2017-06-10 19:30 | 113.89 | 100.03
2017-06-10 20:00 | 115.93 | 101.34
2017-06-10 20:30 | 118.11 | 103.53
2017-06-10 21:00 | 114.28 | 98.4
2017-06-10 21:30 | 114.2 | 98.21
2017-06-10 22:00 | 115.41 | 100.11
2017-06-10 22:30 | 120.19 | 106.47
2017-06-10 23:00 | 119.98 | 105.87
2017-06-10 23:30 | 124.08 | 110.4
2017-06-11 | 117.29 | 102.07
2017-06-11 00:30 | 116.77 | 101.3
2017-06-11 01:00 | 115.24 | 99.59
2017-06-11 01:30 | 113.27 | 96.04
2017-06-11 02:00 | 115.77 | 100.43
2017-06-11 02:30 | 116.09 | 100.08
2017-06-11 03:00 | 113.71 | 97.34
2017-06-11 03:30 | 115.99 | 100.47
2017-06-11 04:00 | 112.78 | 96.38
2017-06-11 04:30 | 113.01 | 97.41
2017-06-11 05:00 | 112.31 | 96.28
2017-06-11 05:30 | 118.42 | 103.54
2017-06-11 06:00 | 118.55 | 103.53
2017-06-11 06:30 | 105.45 | 85.73
2017-06-11 07:00 | 112.46 | 94.79
2017-06-11 07:30 | 112.61 | 96.18
2017-06-11 08:00 | 115.87 | 100.33
2017-06-11 08:30 | 115.32 | 99.89
2017-06-11 09:00 | 120.04 | 107.17
2017-06-11 09:30 | 112.85 | 97.44
2017-06-11 10:00 | 109.88 | 94.67
2017-06-11 10:30 | 113.54 | 99.42
2017-06-11 11:00 | 114.03 | 99.16
2017-06-11 11:30 | 115.7 | 100.72
2017-06-11 12:00 | 114.76 | 98.36
2017-06-11 12:30 | 112.94 | 96.19
2017-06-11 13:00 | 110.48 | 93.73
2017-06-11 13:30 | 116.32 | 100.83
2017-06-11 14:00 | 111.04 | 94.45
2017-06-11 14:30 | 110.02 | 93.12
2017-06-11 15:00 | 110.59 | 91.63
2017-06-11 15:30 | 113.85 | 96.48
2017-06-11 16:00 | 111.28 | 93.66
2017-06-11 16:30 | 109.95 | 93.23
2017-06-11 17:00 | 108.74 | 93.14
2017-06-11 17:30 | 113.66 | 98.1
2017-06-11 18:00 | 114.01 | 99.71
2017-06-11 18:30 | 107.63 | 91.21
2017-06-11 19:00 | 113.01 | 98.4
2017-06-11 19:30 | 113.59 | 99.17
2017-06-11 20:00 | 114.11 | 98.98
2017-06-11 20:30 | 118.14 | 104.26
2017-06-11 21:00 | 115.93 | 100.78
2017-06-11 21:30 | 117.84 | 103.8
2017-06-11 22:00 | 112.25 | 96.09
2017-06-11 22:30 | 113.07 | 98.06
2017-06-11 23:00 | 107.19 | 89.16
2017-06-11 23:30 | 108.83 | 91.68
2017-06-12 | 116.15 | 100.83
2017-06-12 00:30 | 110.36 | 92.91
2017-06-12 01:00 | 108.19 | 90.03
2017-06-12 01:30 | 108.71 | 90.98
2017-06-12 02:00 | 104.5 | 84.73
2017-06-12 02:30 | 107.71 | 89.06
2017-06-12 03:00 | 105.72 | 87.06
2017-06-12 03:30 | 100.61 | 79.39
2017-06-12 04:00 | 106.28 | 87.72
2017-06-12 04:30 | 108.48 | 91.46
2017-06-12 05:00 | 105.77 | 88.32
2017-06-12 05:30 | 107.58 | 91.01
2017-06-12 06:00 | 105.63 | 88.62
2017-06-12 06:30 | 96.56 | 76.28
2017-06-12 07:00 | 102.72 | 85.34
2017-06-12 07:30 | 106.43 | 90.98
2017-06-12 08:00 | 108 | 91.61
2017-06-12 08:30 | 109.37 | 92.92
2017-06-12 09:00 | 99.82 | 82.02
2017-06-12 09:30 | 101.06 | 80.95
2017-06-12 10:00 | 102.03 | 82.18
2017-06-12 10:30 | 101.76 | 81.7
2017-06-12 11:00 | 101.91 | 82.24
2017-06-12 11:30 | 99.89 | 79.6
2017-06-12 12:00 | 106.58 | 87.89
2017-06-12 12:30 | 107.09 | 89.01
2017-06-12 13:00 | 105.96 | 87.77
2017-06-12 13:30 | 111.91 | 95.19
2017-06-12 14:00 | 102.31 | 81.09
2017-06-12 14:30 | 106.04 | 86.16
2017-06-12 15:00 | 105.81 | 86.41
2017-06-12 15:30 | 102.27 | 82.42
2017-06-12 16:00 | 102.99 | 81.81
2017-06-12 16:30 | 102.48 | 81.9
2017-06-12 17:00 | 106.18 | 86.54
2017-06-12 17:30 | 105.58 | 86.46
2017-06-12 18:00 | 106.48 | 88.44
2017-06-12 18:30 | 100.82 | 81.9
2017-06-12 19:00 | 105.99 | 88.75
2017-06-12 19:30 | 112.31 | 97.16
2017-06-12 20:00 | 111.95 | 96.16
2017-06-12 20:30 | 110.28 | 93.97
2017-06-12 21:00 | 106.64 | 87.59
2017-06-12 21:30 | 109.32 | 91.47
2017-06-12 22:00 | 115.89 | 100.03
2017-06-12 22:30 | 111.59 | 93.15
2017-06-12 23:00 | 108.84 | 88.95
2017-06-12 23:30 | 108.17 | 88.57
2017-06-13 | 112.85 | 94.37
2017-06-13 00:30 | 109.81 | 90.45
2017-06-13 01:00 | 106.15 | 85.83
2017-06-13 01:30 | 104.99 | 83.43
2017-06-13 02:00 | 108.48 | 90.44
2017-06-13 02:30 | 106 | 87.63
2017-06-13 03:00 | 100.32 | 79.81
2017-06-13 03:30 | 95.03 | 71.74
2017-06-13 04:00 | 90.47 | 65.92
2017-06-13 04:30 | 93.56 | 70.55
2017-06-13 05:00 | 94.22 | 71.44
2017-06-13 05:30 | 96.45 | 74.18
2017-06-13 06:00 | 95.02 | 71.7
2017-06-13 06:30 | 95.12 | 71.69
2017-06-13 07:00 | 100.84 | 80.55
2017-06-13 07:30 | 96.88 | 75.21
2017-06-13 08:00 | 95.13 | 71.92
2017-06-13 08:30 | 93.65 | 68.53
2017-06-13 09:00 | 93.59 | 69.1
2017-06-13 09:30 | 91.58 | 64.11
2017-06-13 10:00 | 90.29 | 62.39
2017-06-13 10:30 | 89.68 | 61.15
2017-06-13 11:00 | 89.82 | 61.71
2017-06-13 11:30 | 93.2 | 63.78
2017-06-13 12:00 | 94.4 | 68.33
2017-06-13 12:30 | 93.32 | 65.37
2017-06-13 13:00 | 97.15 | 72.04
2017-06-13 13:30 | 96.11 | 70.07
2017-06-13 14:00 | 94.92 | 68.5
2017-06-13 14:30 | 99.82 | 76
2017-06-13 15:00 | 99.99 | 77.33
2017-06-13 15:30 | 99.23 | 75.65
2017-06-13 16:00 | 102.22 | 80.4
2017-06-13 16:30 | 106.04 | 86.93
2017-06-13 17:00 | 99.97 | 79.98
2017-06-13 17:30 | 101.29 | 82.61
2017-06-13 18:00 | 109.2 | 92.52
2017-06-13 18:30 | 103.36 | 84.09
2017-06-13 19:00 | 102.84 | 83.75
2017-06-13 19:30 | 107.46 | 90.67
2017-06-13 20:00 | 105.21 | 87.61
2017-06-13 20:30 | 105.73 | 87.79
2017-06-13 21:00 | 103.24 | 84.31
2017-06-13 21:30 | 105.68 | 87.56
2017-06-13 22:00 | 107.02 | 89.35
2017-06-13 22:30 | 110.78 | 94.68
2017-06-13 23:00 | 108.35 | 90.73
2017-06-13 23:30 | 105.01 | 85.46
2017-06-14 | 110.83 | 92.87
2017-06-14 00:30 | 110.75 | 92.94
2017-06-14 01:00 | 101.72 | 81.17
2017-06-14 01:30 | 104.48 | 84.45
2017-06-14 02:00 | 108.94 | 89.77
2017-06-14 02:30 | 106.19 | 85.67
2017-06-14 03:00 | 98.15 | 73.18
2017-06-14 03:30 | 105.04 | 84.38
2017-06-14 04:00 | 106.23 | 87.95
2017-06-14 04:30 | 106.38 | 87.2
2017-06-14 05:00 | 104.28 | 83.96
2017-06-14 05:30 | 103.66 | 82.71
2017-06-14 06:00 | 96.8 | 73.96
2017-06-14 06:30 | 97.24 | 75.8
2017-06-14 07:00 | 95.43 | 74.03
2017-06-14 07:30 | 94.99 | 72.35
2017-06-14 08:00 | 95.74 | 74.05
2017-06-14 08:30 | 89.94 | 65.52
2017-06-14 09:00 | 90.05 | 63.69
2017-06-14 09:30 | 90.59 | 64
2017-06-14 10:00 | 87.75 | 58.05
2017-06-14 10:30 | 90.58 | 63.91
2017-06-14 11:00 | 91.27 | 65.15
2017-06-14 11:30 | 89.45 | 62.12
2017-06-14 12:00 | 89.73 | 62.3
2017-06-14 12:30 | 90.92 | 65.76
2017-06-14 13:00 | 90.94 | 66.31
2017-06-14 13:30 | 91.84 | 67.98
2017-06-14 14:00 | 91.1 | 65.32
2017-06-14 14:30 | 90.82 | 64.75
2017-06-14 15:00 | 89.92 | 64.11
2017-06-14 15:30 | 89.3 | 62.78
2017-06-14 16:00 | 94.92 | 71.49
2017-06-14 16:30 | 95.66 | 73.45
2017-06-14 17:00 | 90.09 | 66.65
2017-06-14 17:30 | 90.21 | 67.84
2017-06-14 18:00 | 96.81 | 76.42
2017-06-14 18:30 | 95.95 | 74.39
2017-06-14 19:00 | 93.14 | 71.78
2017-06-14 19:30 | 96.25 | 75.55
2017-06-14 20:00 | 101.91 | 82.68
2017-06-14 20:30 | 106.39 | 87.75
2017-06-14 21:00 | 103.5 | 83.87
2017-06-14 21:30 | 106.06 | 87.42
2017-06-14 22:00 | 103.69 | 83.68
2017-06-14 22:30 | 112.75 | 95.37
2017-06-14 23:00 | 106.67 | 86.94
2017-06-14 23:30 | 105.46 | 82.97
2017-06-15 | 108.36 | 89.07
2017-06-15 00:30 | 108.55 | 89.95
2017-06-15 01:00 | 106.62 | 88.08
2017-06-15 01:30 | 102.21 | 82.59
2017-06-15 02:00 | 109.04 | 91.11
2017-06-15 02:30 | 107.8 | 88.58
2017-06-15 03:00 | 105.24 | 85.36
2017-06-15 03:30 | 107.56 | 88.8
2017-06-15 04:00 | 107.29 | 87
2017-06-15 04:30 | 106.2 | 85.89
2017-06-15 05:00 | 101.3 | 78.76
2017-06-15 05:30 | 103.55 | 82.42
2017-06-15 06:00 | 105.17 | 84.83
2017-06-15 06:30 | 97.05 | 73.56
2017-06-15 07:00 | 103.11 | 82.97
2017-06-15 07:30 | 102.86 | 81.57
2017-06-15 08:00 | 101.55 | 80.41
2017-06-15 08:30 | 99.12 | 76.69
2017-06-15 09:00 | 96.67 | 69.89
2017-06-15 09:30 | 97.28 | 71.51
2017-06-15 10:00 | 99.59 | 74.28
2017-06-15 10:30 | 101.25 | 76.89
2017-06-15 11:00 | 95.57 | 68.26
2017-06-15 11:30 | 105.79 | 84.13
2017-06-15 12:00 | 104.58 | 82.12
2017-06-15 12:30 | 106.14 | 82.53
2017-06-15 13:00 | 105.46 | 81.53
2017-06-15 13:30 | 105.38 | 81.97
2017-06-15 14:00 | 108.5 | 84.87
2017-06-15 14:30 | 112.91 | 91.01
2017-06-15 15:00 | 111.17 | 89.95
2017-06-15 15:30 | 101.24 | 86.9
2017-06-15 16:00 | 96.22 | 80.76
2017-06-15 16:30 | 104.45 | 91.86
2017-06-15 17:00 | 112.25 | 91.4
2017-06-15 17:30 | 103.76 | 82.77
2017-06-15 18:00 | 110.35 | 91.67
2017-06-15 18:30 | 109.18 | 90.01
2017-06-15 19:00 | 117 | 100.96
2017-06-15 19:30 | 121.56 | 106.63
2017-06-15 20:00 | 119 | 103.98
2017-06-15 20:30 | 116.54 | 100.26
2017-06-15 21:00 | 113.65 | 95.98
2017-06-15 21:30 | 116.46 | 99.42
2017-06-15 22:00 | 112.98 | 94.6
2017-06-15 22:30 | 115.9 | 98.65
2017-06-15 23:00 | 113.53 | 94.81
2017-06-15 23:30 | 112.34 | 93.27
2017-06-16 | 112.26 | 92.67
2017-06-16 00:30 | 113.74 | 95.19
2017-06-16 01:00 | 117.51 | 100.23
2017-06-16 01:30 | 113.59 | 95.75
2017-06-16 02:00 | 114.92 | 96.21
2017-06-16 02:30 | 120.78 | 105.35
2017-06-16 03:00 | 115.5 | 97.13
2017-06-16 03:30 | 112.27 | 93.48
2017-06-16 04:00 | 107.72 | 87.83
2017-06-16 04:30 | 109.66 | 90.28
2017-06-16 05:00 | 111.64 | 93.83
2017-06-16 05:30 | 113.59 | 97.05
2017-06-16 06:00 | 114.55 | 97.9
2017-06-16 06:30 | 112.21 | 94.2
2017-06-16 07:00 | 116.13 | 99.74
2017-06-16 07:30 | 117.44 | 101.05
2017-06-16 08:00 | 116.26 | 98.97
2017-06-16 08:30 | 115.8 | 99.35
2017-06-16 09:00 | 115.25 | 100.18
2017-06-16 09:30 | 116.19 | 101.01
2017-06-16 10:00 | 116.71 | 101.75
2017-06-16 10:30 | 115.26 | 99.9
2017-06-16 11:00 | 113.88 | 97.25
2017-06-16 11:30 | 119.97 | 104.31
2017-06-16 12:00 | 119.66 | 104.47
2017-06-16 12:30 | 118.94 | 102.61
2017-06-16 13:00 | 114.59 | 96.43
2017-06-16 13:30 | 108.37 | 90.39
2017-06-16 14:00 | 113.32 | 96.27
2017-06-16 14:30 | 114.05 | 96.8
2017-06-16 15:00 | 112.84 | 94.72
2017-06-16 15:30 | 117.8 | 101.62
2017-06-16 16:00 | 116.6 | 99.37
2017-06-16 16:30 | 117.24 | 99.94
2017-06-16 17:00 | 123.48 | 109.31
2017-06-16 17:30 | 117.09 | 101.31
2017-06-16 18:00 | 117.5 | 102.2
2017-06-16 18:30 | 116.91 | 101.73
2017-06-16 19:00 | 121.16 | 106.6
2017-06-16 19:30 | 126.78 | 113.34
2017-06-16 20:00 | 122.33 | 107.43
2017-06-16 20:30 | 115.76 | 100.72
2017-06-16 21:00 | 117.62 | 101.6
2017-06-16 21:30 | 119.85 | 103.77
2017-06-16 22:00 | 115.69 | 99.17
2017-06-16 22:30 | 121.38 | 105.33
2017-06-16 23:00 | 124.06 | 109.2
2017-06-16 23:30 | 119.8 | 102.84
2017-06-17 | 116.29 | 98.39
2017-06-17 00:30 | 115.52 | 97.11
2017-06-17 01:00 | 115.2 | 96.81
2017-06-17 01:30 | 116.02 | 97.39
2017-06-17 02:00 | 114.98 | 95.75
2017-06-17 02:30 | 115.17 | 96.33
2017-06-17 03:00 | 115.45 | 98.12
2017-06-17 03:30 | 112.6 | 95.18
2017-06-17 04:00 | 116.17 | 98.14
2017-06-17 04:30 | 114.84 | 97.22
2017-06-17 05:00 | 114.01 | 96.08
2017-06-17 05:30 | 120.6 | 104.49
2017-06-17 06:00 | 117.3 | 100.33
2017-06-17 06:30 | 112.04 | 92.8
2017-06-17 07:00 | 120.71 | 105.47
2017-06-17 07:30 | 114.64 | 95.92
2017-06-17 08:00 | 115.66 | 100.15
2017-06-17 08:30 | 113.49 | 95.45
2017-06-17 09:00 | 109.31 | 90.43
2017-06-17 09:30 | 111.28 | 93.54
2017-06-17 10:00 | 113.03 | 96.19
2017-06-17 10:30 | 114.01 | 97.54
2017-06-17 11:00 | 110.83 | 91.68
2017-06-17 11:30 | 111.07 | 91.48
2017-06-17 12:00 | 112.18 | 94.24
2017-06-17 12:30 | 111.38 | 93.42
2017-06-17 13:00 | 109.52 | 90.2
2017-06-17 13:30 | 118.77 | 102.99
2017-06-17 14:00 | 117.73 | 101.24
2017-06-17 14:30 | 115.04 | 96.37
2017-06-17 15:00 | 114.09 | 96.69
2017-06-17 15:30 | 108.55 | 89.04
2017-06-17 16:00 | 112.46 | 95.46
2017-06-17 16:30 | 113.97 | 98.18
2017-06-17 17:00 | 114.24 | 98.1
2017-06-17 17:30 | 116.19 | 101.28
2017-06-17 18:00 | 109.01 | 92.05
2017-06-17 18:30 | 107.64 | 89.9
2017-06-17 19:00 | 114.34 | 99.3
2017-06-17 19:30 | 119.47 | 105.52
2017-06-17 20:00 | 119.97 | 106.31
2017-06-17 20:30 | 119.48 | 105.1
2017-06-17 21:00 | 122.29 | 108.6
2017-06-17 21:30 | 122.09 | 109.7
2017-06-17 22:00 | 115.14 | 100.27
2017-06-17 22:30 | 121.03 | 107.35
2017-06-17 23:00 | 120.71 | 106.09
2017-06-17 23:30 | 121.69 | 107.19
2017-06-18 | 119.73 | 105.13
2017-06-18 00:30 | 114.03 | 96.95
2017-06-18 01:00 | 120.03 | 104.61
2017-06-18 01:30 | 117.89 | 102.12
2017-06-18 02:00 | 121.99 | 107.87
2017-06-18 02:30 | 115.48 | 98.51
2017-06-18 03:00 | 110.36 | 91.43
2017-06-18 03:30 | 114.96 | 98.69
2017-06-18 04:00 | 118.45 | 101.26
2017-06-18 04:30 | 111.89 | 93.08
2017-06-18 05:00 | 115.82 | 98.5
2017-06-18 05:30 | 114.59 | 96.56
2017-06-18 06:00 | 111.85 | 94.38
2017-06-18 06:30 | 104.42 | 82.69
2017-06-18 07:00 | 110.02 | 91.2
2017-06-18 07:30 | 115.43 | 98.46
2017-06-18 08:00 | 113.07 | 95.06
2017-06-18 08:30 | 114.52 | 96.25
2017-06-18 09:00 | 116.65 | 99.59
2017-06-18 09:30 | 116.27 | 98.82
2017-06-18 10:00 | 111.15 | 92.59
2017-06-18 10:30 | 113.05 | 94.61
2017-06-18 11:00 | 114.23 | 95.38
2017-06-18 11:30 | 118.07 | 100.92
2017-06-18 12:00 | 119.72 | 103.27
2017-06-18 12:30 | 112.01 | 92.95
2017-06-18 13:00 | 110.38 | 90.84
2017-06-18 13:30 | 112.37 | 92.69
2017-06-18 14:00 | 113.19 | 94.35
2017-06-18 14:30 | 113.77 | 94.6
2017-06-18 15:00 | 111.14 | 91.63
2017-06-18 15:30 | 107.44 | 88.1
2017-06-18 16:00 | 110.68 | 92.96
2017-06-18 16:30 | 112.92 | 95.63
2017-06-18 17:00 | 119.13 | 103.33
2017-06-18 17:30 | 125.85 | 112.1
2017-06-18 18:00 | 123.32 | 109.55
2017-06-18 18:30 | 119.81 | 103.79
2017-06-18 19:00 | 126.05 | 112.72
2017-06-18 19:30 | 129.25 | 115.95
2017-06-18 20:00 | 125.04 | 112.24
2017-06-18 20:30 | 127.09 | 114.01
2017-06-18 21:00 | 124.84 | 111.86
2017-06-18 21:30 | 120.68 | 105.07
2017-06-18 22:00 | 119.67 | 104.18
2017-06-18 22:30 | 119.21 | 102.52
2017-06-18 23:00 | 112.63 | 93.06
2017-06-18 23:30 | 119.75 | 103.62
2017-06-19 | 124.42 | 109.8
2017-06-19 00:30 | 119.07 | 102.52
2017-06-19 01:00 | 116.76 | 100.78
2017-06-19 01:30 | 119.74 | 103.14
2017-06-19 02:00 | 121.13 | 104.49
2017-06-19 02:30 | 111.53 | 93.38
2017-06-19 03:00 | 116.28 | 98.33
2017-06-19 03:30 | 114.67 | 95.9
2017-06-19 04:00 | 118.61 | 101.24
2017-06-19 04:30 | 123.66 | 108.67
2017-06-19 05:00 | 121.49 | 105.22
2017-06-19 05:30 | 119.95 | 103.16
2017-06-19 06:00 | 122.51 | 106.6
2017-06-19 06:30 | 114.7 | 96.49
2017-06-19 07:00 | 120.39 | 104.2
2017-06-19 07:30 | 121.04 | 104.8
2017-06-19 08:00 | 113.85 | 94.33
2017-06-19 08:30 | 118.33 | 99.74
2017-06-19 09:00 | 112.49 | 92.43
2017-06-19 09:30 | 116.32 | 96.28
2017-06-19 10:00 | 115.14 | 96.32
2017-06-19 10:30 | 118.92 | 100.96
2017-06-19 11:00 | 118.44 | 98.85
2017-06-19 11:30 | 119.81 | 101.13
2017-06-19 12:00 | 120.09 | 100.73
2017-06-19 12:30 | 117.18 | 96.98
2017-06-19 13:00 | 119.38 | 100.55
2017-06-19 13:30 | 119.84 | 101.39
2017-06-19 14:00 | 119.16 | 100.61
2017-06-19 14:30 | 119.64 | 99.89
2017-06-19 15:00 | 123.08 | 104.05
2017-06-19 15:30 | 121.97 | 102.06
2017-06-19 16:00 | 123.24 | 105.21
2017-06-19 16:30 | 122.29 | 104.11
2017-06-19 17:00 | 123.6 | 105.44
2017-06-19 17:30 | 123.51 | 105.93
2017-06-19 18:00 | 124.96 | 108.5
2017-06-19 18:30 | 119.26 | 101.24
2017-06-19 19:00 | 129 | 113.98
2017-06-19 19:30 | 123.49 | 107.51
2017-06-19 20:00 | 123.16 | 105.41
2017-06-19 20:30 | 118.88 | 100.46
2017-06-19 21:00 | 115.42 | 96.92
2017-06-19 21:30 | 122.86 | 105.53
2017-06-19 22:00 | 124.15 | 107.13
2017-06-19 22:30 | 126.95 | 110.2
2017-06-19 23:00 | 118.88 | 99.72
2017-06-19 23:30 | 123.24 | 106.87
2017-06-20 | 116.46 | 98.8
2017-06-20 00:30 | 118.39 | 100.39
2017-06-20 01:00 | 128.32 | 112.27
2017-06-20 01:30 | 128.84 | 113.05
2017-06-20 02:00 | 121.39 | 102.43
2017-06-20 02:30 | 124.71 | 107.1
2017-06-20 03:00 | 112.44 | 91.5
2017-06-20 03:30 | 114.63 | 92.89
2017-06-20 04:00 | 121.79 | 103.07
2017-06-20 04:30 | 124.09 | 105.97
2017-06-20 05:00 | 122.79 | 104.76
2017-06-20 05:30 | 121.26 | 103.96
2017-06-20 06:00 | 107.68 | 85.91
2017-06-20 06:30 | 108.25 | 84.5
2017-06-20 07:00 | 115.8 | 94.64
2017-06-20 07:30 | 114.79 | 94.9
2017-06-20 08:00 | 115.2 | 94.87
2017-06-20 08:30 | 105 | 82.23
2017-06-20 09:00 | 110.32 | 89.55
2017-06-20 09:30 | 107.92 | 85.57
2017-06-20 10:00 | 103.72 | 79.5
2017-06-20 10:30 | 108.77 | 82.18
2017-06-20 11:00 | 111.7 | 86.39
2017-06-20 11:30 | 113.32 | 90.23
2017-06-20 12:00 | 113.78 | 89.6
2017-06-20 12:30 | 111.68 | 87.83
2017-06-20 13:00 | 111.39 | 87.81
2017-06-20 13:30 | 111.87 | 89.22
2017-06-20 14:00 | 113.88 | 90.66
2017-06-20 14:30 | 113.03 | 90
2017-06-20 15:00 | 113.44 | 90.42
2017-06-20 15:30 | 120.17 | 100.16
2017-06-20 16:00 | 123.5 | 103
2017-06-20 16:30 | 120.11 | 99.76
2017-06-20 17:00 | 117.53 | 95.69
2017-06-20 17:30 | 117.42 | 95.97
2017-06-20 18:00 | 121.28 | 100.87
2017-06-20 18:30 | 114.47 | 89.82
2017-06-20 19:00 | 125.98 | 108.57
2017-06-20 19:30 | 121.6 | 103.28
2017-06-20 20:00 | 125.1 | 108.3
2017-06-20 20:30 | 120.51 | 102.47
2017-06-20 21:00 | 118.6 | 101.22
2017-06-20 21:30 | 120.32 | 102.07
2017-06-20 22:00 | 115.17 | 95.12
2017-06-20 22:30 | 114.4 | 94.01
2017-06-20 23:00 | 115.46 | 96.15
2017-06-20 23:30 | 118.95 | 100.01
2017-06-21 | 118.25 | 99.58
2017-06-21 00:30 | 116.75 | 97.78
2017-06-21 01:00 | 117.54 | 98.75
2017-06-21 01:30 | 119.01 | 100.88
2017-06-21 02:00 | 117.61 | 97.78
2017-06-21 02:30 | 117.38 | 98.2
2017-06-21 03:00 | 120.86 | 102.31
2017-06-21 03:30 | 118.44 | 98.97
2017-06-21 04:00 | 113.25 | 91.19
2017-06-21 04:30 | 110.68 | 90.67
2017-06-21 05:00 | 111.02 | 91.06
2017-06-21 05:30 | 114.15 | 96.14
2017-06-21 06:00 | 119.81 | 102.94
2017-06-21 06:30 | 108.51 | 86.62
2017-06-21 07:00 | 112.52 | 93.5
2017-06-21 07:30 | 107.56 | 88.77
2017-06-21 08:00 | 107.12 | 89.05
2017-06-21 08:30 | 99.73 | 77.16
2017-06-21 09:00 | 102.33 | 81.01
2017-06-21 09:30 | 96.32 | 72.39
2017-06-21 10:00 | 100.44 | 75.2
2017-06-21 10:30 | 108 | 84.95
2017-06-21 11:00 | 112.46 | 89.8
2017-06-21 11:30 | 112.86 | 89.16
2017-06-21 12:00 | 111.47 | 89.84
2017-06-21 12:30 | 114.15 | 92.94
2017-06-21 13:00 | 113.4 | 92.17
2017-06-21 13:30 | 112.09 | 90.38
2017-06-21 14:00 | 107.74 | 85.67
2017-06-21 14:30 | 108.74 | 87.29
2017-06-21 15:00 | 114.91 | 94.97
2017-06-21 15:30 | 113.93 | 93.88
2017-06-21 16:00 | 112.94 | 91.97
2017-06-21 16:30 | 121.94 | 103.7
2017-06-21 17:00 | 121.62 | 103.56
2017-06-21 17:30 | 121.8 | 104.23
2017-06-21 18:00 | 123.64 | 107.76
2017-06-21 18:30 | 111.67 | 92.01
2017-06-21 19:00 | 123.6 | 107.16
2017-06-21 19:30 | 129.45 | 114.9
2017-06-21 20:00 | 134.06 | 119.88
2017-06-21 20:30 | 128.69 | 112.6
2017-06-21 21:00 | 120.57 | 103.94
2017-06-21 21:30 | 124.12 | 106.5
2017-06-21 22:00 | 126.86 | 109.76
2017-06-21 22:30 | 125.8 | 109.31
2017-06-21 23:00 | 122.51 | 104.13
2017-06-21 23:30 | 127.35 | 110.04
2017-06-22 | 128.94 | 111.71
2017-06-22 00:30 | 123.07 | 105.6
2017-06-22 01:00 | 121.35 | 101.04
2017-06-22 01:30 | 115.48 | 93.11
2017-06-22 02:00 | 112.46 | 89.85
2017-06-22 02:30 | 117.85 | 97.43
2017-06-22 03:00 | 114.63 | 93.4
2017-06-22 03:30 | 121.54 | 102.84
2017-06-22 04:00 | 126.01 | 108.4
2017-06-22 04:30 | 122.97 | 104.1
2017-06-22 05:00 | 125.57 | 108.41
2017-06-22 05:30 | 123.4 | 105.45
2017-06-22 06:00 | 118.95 | 99.85
2017-06-22 06:30 | 112.22 | 90.63
2017-06-22 07:00 | 118.62 | 100.36
2017-06-22 07:30 | 126.21 | 110.14
2017-06-22 08:00 | 118.51 | 98.89
2017-06-22 08:30 | 120.78 | 100.77
2017-06-22 09:00 | 119.16 | 97.78
2017-06-22 09:30 | 119.29 | 98.06
2017-06-22 10:00 | 119.85 | 98.66
2017-06-22 10:30 | 117.17 | 93.54
2017-06-22 11:00 | 110.71 | 86.23
2017-06-22 11:30 | 118.38 | 95.49
2017-06-22 12:00 | 114.92 | 90.62
2017-06-22 12:30 | 114.41 | 90.96
2017-06-22 13:00 | 116.47 | 94.35
2017-06-22 13:30 | 116.23 | 93.49
2017-06-22 14:00 | 110.84 | 84.95
2017-06-22 14:30 | 112.02 | 86.7
2017-06-22 15:00 | 114.16 | 89.65
2017-06-22 15:30 | 110.64 | 86.02
2017-06-22 16:00 | 118.08 | 95.78
2017-06-22 16:30 | 121.94 | 101.23
2017-06-22 17:00 | 120.78 | 101.42
2017-06-22 17:30 | 117.86 | 98.24
2017-06-22 18:00 | 125.99 | 108.84
2017-06-22 18:30 | 118.05 | 97.7
2017-06-22 19:00 | 123.42 | 106.65
2017-06-22 19:30 | 124.76 | 107.81
2017-06-22 20:00 | 123.93 | 107.09
2017-06-22 20:30 | 125.86 | 109.22
2017-06-22 21:00 | 126.48 | 109.95
2017-06-22 21:30 | 122.19 | 103.88
2017-06-22 22:00 | 121.83 | 103.07
2017-06-22 22:30 | 120.68 | 101.16
2017-06-22 23:00 | 129.53 | 113.45
2017-06-22 23:30 | 124.56 | 105.89
2017-06-23 | 123.41 | 104.17
2017-06-23 00:30 | 123.29 | 104.33
2017-06-23 01:00 | 123.29 | 105
2017-06-23 01:30 | 120.89 | 100.39
2017-06-23 02:00 | 121.6 | 102.55
2017-06-23 02:30 | 122.18 | 103.15
2017-06-23 03:00 | 124.64 | 105.85
2017-06-23 03:30 | 120.39 | 99.38
2017-06-23 04:00 | 120.75 | 100.69
2017-06-23 04:30 | 126.13 | 108.85
2017-06-23 05:00 | 125.57 | 108.11
2017-06-23 05:30 | 126.98 | 109.09
2017-06-23 06:00 | 127.92 | 110.89
2017-06-23 06:30 | 117.41 | 97.46
2017-06-23 07:00 | 114.83 | 95.79
2017-06-23 07:30 | 120.75 | 104.6
2017-06-23 08:00 | 115.09 | 96.91
2017-06-23 08:30 | 107.33 | 85.16
2017-06-23 09:00 | 109.19 | 86.46
2017-06-23 09:30 | 109.59 | 85.34
2017-06-23 10:00 | 109.19 | 85.77
2017-06-23 10:30 | 113.9 | 91.22
2017-06-23 11:00 | 114.21 | 92.81
2017-06-23 11:30 | 114.47 | 92.75
2017-06-23 12:00 | 116.8 | 96.04
2017-06-23 12:30 | 120.41 | 101.83
2017-06-23 13:00 | 115.25 | 94.14
2017-06-23 13:30 | 118.49 | 98.71
2017-06-23 14:00 | 116.33 | 96.13
2017-06-23 14:30 | 115.76 | 94.97
2017-06-23 15:00 | 122.46 | 104.64
2017-06-23 15:30 | 113.35 | 91.73
2017-06-23 16:00 | 115.78 | 96.05
2017-06-23 16:30 | 115.55 | 95.91
2017-06-23 17:00 | 117.74 | 99.27
2017-06-23 17:30 | 114.61 | 96.14
2017-06-23 18:00 | 116.15 | 98.13
2017-06-23 18:30 | 118.18 | 99.98
2017-06-23 19:00 | 120.79 | 104.11
2017-06-23 19:30 | 126.08 | 110.88
2017-06-23 20:00 | 121.09 | 104.83
2017-06-23 20:30 | 122.57 | 107.57
2017-06-23 21:00 | 121.28 | 104.92
2017-06-23 21:30 | 117.38 | 98.08
2017-06-23 22:00 | 120.07 | 101.46
2017-06-23 22:30 | 120.02 | 101.37
2017-06-23 23:00 | 123.75 | 104.56
2017-06-23 23:30 | 125.24 | 105.67
2017-06-24 | 122.37 | 101.58
2017-06-24 00:30 | 123.63 | 103.9
2017-06-24 01:00 | 125.59 | 107.31
2017-06-24 01:30 | 125.58 | 106.95
2017-06-24 02:00 | 123.62 | 104.68
2017-06-24 02:30 | 128.78 | 112.49
2017-06-24 03:00 | 122.77 | 103.94
2017-06-24 03:30 | 122.09 | 104.57
2017-06-24 04:00 | 120.41 | 101.43
2017-06-24 04:30 | 123.09 | 105.05
2017-06-24 05:00 | 124.22 | 107.44
2017-06-24 05:30 | 124.35 | 107.84
2017-06-24 06:00 | 128.22 | 111.21
2017-06-24 06:30 | 119.26 | 99.85
2017-06-24 07:00 | 121.65 | 104.51
2017-06-24 07:30 | 125.02 | 109.37
2017-06-24 08:00 | 120.86 | 105.79
2017-06-24 08:30 | 119.78 | 103.99
2017-06-24 09:00 | 121.6 | 104.66
2017-06-24 09:30 | 120.79 | 104.34
2017-06-24 10:00 | 120.25 | 101.96
2017-06-24 10:30 | 120.33 | 103.31
2017-06-24 11:00 | 121.48 | 104.64
2017-06-24 11:30 | 116.98 | 97.25
2017-06-24 12:00 | 121.42 | 102.88
2017-06-24 12:30 | 120.9 | 104.33
2017-06-24 13:00 | 120.69 | 104.08
2017-06-24 13:30 | 121.51 | 104.74
2017-06-24 14:00 | 119.44 | 101.91
2017-06-24 14:30 | 112.12 | 92.9
2017-06-24 15:00 | 111.55 | 91.89
2017-06-24 15:30 | 114.12 | 94.12
2017-06-24 16:00 | 117.12 | 98.41
2017-06-24 16:30 | 122.82 | 106
2017-06-24 17:00 | 123.38 | 107.68
2017-06-24 17:30 | 125.26 | 110
2017-06-24 18:00 | 123.68 | 108.83
2017-06-24 18:30 | 114.28 | 96.08
2017-06-24 19:00 | 121.42 | 106.14
2017-06-24 19:30 | 123.92 | 109.02
2017-06-24 20:00 | 124.22 | 110.12
2017-06-24 20:30 | 123.36 | 109.23
2017-06-24 21:00 | 128.6 | 114.53
2017-06-24 21:30 | 122.21 | 106.28
2017-06-24 22:00 | 123 | 107.1
2017-06-24 22:30 | 123.23 | 108.03
2017-06-24 23:00 | 121.2 | 105.04
2017-06-24 23:30 | 120.27 | 102.59
2017-06-25 | 125.57 | 108.7
2017-06-25 00:30 | 127.59 | 111
2017-06-25 01:00 | 127.71 | 110.71
2017-06-25 01:30 | 131.26 | 115.48
2017-06-25 02:00 | 127.44 | 110.37
2017-06-25 02:30 | 120.06 | 100.39
2017-06-25 03:00 | 125.34 | 107.44
2017-06-25 03:30 | 126.96 | 110.1
2017-06-25 04:00 | 124.91 | 106.62
2017-06-25 04:30 | 122.44 | 103.66
2017-06-25 05:00 | 127.53 | 110.62
2017-06-25 05:30 | 124.56 | 108.52
2017-06-25 06:00 | 130.85 | 115.82
2017-06-25 06:30 | 122.3 | 101.53
2017-06-25 07:00 | 125.43 | 106.99
2017-06-25 07:30 | 122.16 | 104.22
2017-06-25 08:00 | 121.44 | 103.62
2017-06-25 08:30 | 120.14 | 101.35
2017-06-25 09:00 | 120.8 | 101.13
2017-06-25 09:30 | 119.31 | 99.79
2017-06-25 10:00 | 124.89 | 106.63
2017-06-25 10:30 | 125.95 | 107.73
2017-06-25 11:00 | 121.93 | 102.08
2017-06-25 11:30 | 120.05 | 98.54
2017-06-25 12:00 | 119.94 | 98.49
2017-06-25 12:30 | 123.81 | 105.03
2017-06-25 13:00 | 129.92 | 113.21
2017-06-25 13:30 | 118.49 | 98.53
2017-06-25 14:00 | 121.44 | 104.27
2017-06-25 14:30 | 124.37 | 108.08
2017-06-25 15:00 | 120.04 | 100.39
2017-06-25 15:30 | 126.6 | 109.8
2017-06-25 16:00 | 128.8 | 112.38
2017-06-25 16:30 | 126.77 | 108.53
2017-06-25 17:00 | 126.63 | 109.49
2017-06-25 17:30 | 121.71 | 101.89
2017-06-25 18:00 | 124.59 | 106.3
2017-06-25 18:30 | 118.2 | 97.9
2017-06-25 19:00 | 121.19 | 103.34
2017-06-25 19:30 | 127.31 | 111.16
2017-06-25 20:00 | 127.02 | 110.52
2017-06-25 20:30 | 122.27 | 104.35
2017-06-25 21:00 | 119.03 | 100.31
2017-06-25 21:30 | 123.31 | 105.91
2017-06-25 22:00 | 125.95 | 109.06
2017-06-25 22:30 | 127.1 | 110.84
2017-06-25 23:00 | 126.48 | 109.53
2017-06-25 23:30 | 128.01 | 111.57
2017-06-26 | 128.64 | 112.74
2017-06-26 00:30 | 120.46 | 103.67
2017-06-26 01:00 | 124.28 | 107.92
2017-06-26 01:30 | 123.6 | 107.02
2017-06-26 02:00 | 126.2 | 109.5
2017-06-26 02:30 | 126.21 | 108.59
2017-06-26 03:00 | 126.67 | 108.88
2017-06-26 03:30 | 126.08 | 108.29
2017-06-26 04:00 | 120.06 | 100.94
2017-06-26 04:30 | 122.11 | 103.91
2017-06-26 05:00 | 121.97 | 103.71
2017-06-26 05:30 | 125.89 | 108.79
2017-06-26 06:00 | 129.59 | 113.36
2017-06-26 06:30 | 117.67 | 97.95
2017-06-26 07:00 | 121.12 | 103.61
2017-06-26 07:30 | 123.3 | 108.27
2017-06-26 08:00 | 123.91 | 107.18
2017-06-26 08:30 | 127.67 | 112.2
2017-06-26 09:00 | 128.24 | 111.35
2017-06-26 09:30 | 129.38 | 112.83
2017-06-26 10:00 | 124.14 | 106.48
2017-06-26 10:30 | 127.05 | 109.69
2017-06-26 11:00 | 124.76 | 106.55
2017-06-26 11:30 | 131.11 | 114.53
2017-06-26 12:00 | 124.04 | 105.62
2017-06-26 12:30 | 128.38 | 112.06
2017-06-26 13:00 | 127.43 | 110.52
2017-06-26 13:30 | 123.71 | 106.68
2017-06-26 14:00 | 120.86 | 104.8
2017-06-26 14:30 | 122.59 | 105.84
2017-06-26 15:00 | 123.32 | 105.55
2017-06-26 15:30 | 121.66 | 103.67
2017-06-26 16:00 | 130.01 | 115.58
2017-06-26 16:30 | 124.88 | 109.66
2017-06-26 17:00 | 122.52 | 105.86
2017-06-26 17:30 | 129.95 | 114.43
2017-06-26 18:00 | 125.5 | 109.79
2017-06-26 18:30 | 120.63 | 102.16
2017-06-26 19:00 | 123.54 | 106.86
2017-06-26 19:30 | 123.55 | 107.74
2017-06-26 20:00 | 122.89 | 106.35
2017-06-26 20:30 | 118.03 | 98.49
2017-06-26 21:00 | 118.94 | 99.53
2017-06-26 21:30 | 114.13 | 94.98
2017-06-26 22:00 | 121.85 | 103.89
2017-06-26 22:30 | 123.85 | 106.88
2017-06-26 23:00 | 122.93 | 106.73
2017-06-26 23:30 | 123.35 | 106.69
2017-06-27 | 121.9 | 104.05
2017-06-27 00:30 | 120.94 | 103.71
2017-06-27 01:00 | 123.84 | 108.55
2017-06-27 01:30 | 121.94 | 104
2017-06-27 02:00 | 125.85 | 109.07
2017-06-27 02:30 | 126.64 | 110.19
2017-06-27 03:00 | 127.93 | 111.16
2017-06-27 03:30 | 119.6 | 101.4
2017-06-27 04:00 | 120.4 | 101.57
2017-06-27 04:30 | 118.52 | 98.26
2017-06-27 05:00 | 123.04 | 103.77
2017-06-27 05:30 | 127.98 | 110.85
2017-06-27 06:00 | 124.18 | 106.08
2017-06-27 06:30 | 121.01 | 101.17
2017-06-27 07:00 | 126.5 | 110.04
2017-06-27 07:30 | 126.25 | 109.88
2017-06-27 08:00 | 117.02 | 98.48
2017-06-27 08:30 | 119.87 | 100.64
2017-06-27 09:00 | 118.28 | 97.14
2017-06-27 09:30 | 121.75 | 102.19
2017-06-27 10:00 | 120.95 | 100.93
2017-06-27 10:30 | 121.38 | 100
2017-06-27 11:00 | 127.52 | 108.13
2017-06-27 11:30 | 121.8 | 100.95
2017-06-27 12:00 | 129.63 | 111.56
2017-06-27 12:30 | 125.93 | 106.98
2017-06-27 13:00 | 127.61 | 110.46
2017-06-27 13:30 | 124.42 | 106.96
2017-06-27 14:00 | 124.54 | 106.93
2017-06-27 14:30 | 114.27 | 91.32
2017-06-27 15:00 | 115.54 | 94.48
2017-06-27 15:30 | 117.54 | 97.31
2017-06-27 16:00 | 119.6 | 100.72
2017-06-27 16:30 | 120.83 | 102.42
2017-06-27 17:00 | 129.76 | 114.05
2017-06-27 17:30 | 125.75 | 108.85
2017-06-27 18:00 | 121.33 | 104.6
2017-06-27 18:30 | 118.15 | 99.4
2017-06-27 19:00 | 122.49 | 106.01
2017-06-27 19:30 | 128.13 | 112.98
2017-06-27 20:00 | 128.93 | 113.56
2017-06-27 20:30 | 124.53 | 108.27
2017-06-27 21:00 | 123.3 | 106.55
2017-06-27 21:30 | 129.6 | 113.04
2017-06-27 22:00 | 132.22 | 117.56
2017-06-27 22:30 | 125.12 | 109.39
2017-06-27 23:00 | 123.36 | 105.17
2017-06-27 23:30 | 127.35 | 110.31
2017-06-28 | 123.88 | 105.64
2017-06-28 00:30 | 126.58 | 109.33
2017-06-28 01:00 | 125.55 | 107.77
2017-06-28 01:30 | 126.82 | 108.89
2017-06-28 02:00 | 126.91 | 109
2017-06-28 02:30 | 123.78 | 106.37
2017-06-28 03:00 | 124.42 | 106.5
2017-06-28 03:30 | 121.86 | 102.93
2017-06-28 04:00 | 125.81 | 108.95
2017-06-28 04:30 | 125.57 | 107.7
2017-06-28 05:00 | 126.49 | 107.98
2017-06-28 05:30 | 121.34 | 101.11
2017-06-28 06:00 | 122.88 | 103.64
2017-06-28 06:30 | 118.82 | 95.65
2017-06-28 07:00 | 122.45 | 100.17
2017-06-28 07:30 | 124.94 | 103.68
2017-06-28 08:00 | 125.28 | 105.29
2017-06-28 08:30 | 125.66 | 104.52
2017-06-28 09:00 | 124.57 | 103.53
2017-06-28 09:30 | 115.82 | 93.85
2017-06-28 10:00 | 121.17 | 100.96
2017-06-28 10:30 | 119.11 | 97.83
2017-06-28 11:00 | 115.53 | 93.03
2017-06-28 11:30 | 115.55 | 91.02
2017-06-28 12:00 | 119.14 | 95.68
2017-06-28 12:30 | 116.46 | 92.78
2017-06-28 13:00 | 121.59 | 100.11
2017-06-28 13:30 | 121.24 | 100.68
2017-06-28 14:00 | 113.33 | 90.56
2017-06-28 14:30 | 117.24 | 97.17
2017-06-28 15:00 | 119.82 | 100.22
2017-06-28 15:30 | 122.79 | 104.47
2017-06-28 16:00 | 121.85 | 103.3
2017-06-28 16:30 | 119.54 | 99.82
2017-06-28 17:00 | 118.13 | 97.05
2017-06-28 17:30 | 119.47 | 98.98
2017-06-28 18:00 | 124.46 | 106.53
2017-06-28 18:30 | 119 | 99.59
2017-06-28 19:00 | 123.78 | 105.46
2017-06-28 19:30 | 130.07 | 113.63
2017-06-28 20:00 | 129.45 | 114.24
2017-06-28 20:30 | 131.65 | 117.31
2017-06-28 21:00 | 122.55 | 105.17
2017-06-28 21:30 | 120.59 | 101.49
2017-06-28 22:00 | 130.13 | 112.42
2017-06-28 22:30 | 128.91 | 112.15
2017-06-28 23:00 | 125.41 | 106.91
2017-06-28 23:30 | 125.25 | 106.62
2017-06-29 | 122.53 | 103.49
2017-06-29 00:30 | 121.26 | 101.48
2017-06-29 01:00 | 122.19 | 103.16
2017-06-29 01:30 | 123.7 | 105.85
2017-06-29 02:00 | 118.56 | 98.82
2017-06-29 02:30 | 121.99 | 103.29
2017-06-29 03:00 | 119.95 | 99.19
2017-06-29 03:30 | 122.18 | 103.05
2017-06-29 04:00 | 123.28 | 104.91
2017-06-29 04:30 | 124.42 | 107.17
2017-06-29 05:00 | 122.84 | 104.87
2017-06-29 05:30 | 126.6 | 110.3
2017-06-29 06:00 | 119.19 | 101.04
2017-06-29 06:30 | 112.72 | 91.92
2017-06-29 07:00 | 111.55 | 89.72
2017-06-29 07:30 | 112.35 | 89.49
2017-06-29 08:00 | 112.47 | 90.73
2017-06-29 08:30 | 108.95 | 87.62
2017-06-29 09:00 | 115.58 | 97.8
2017-06-29 09:30 | 103.41 | 82.55
2017-06-29 10:00 | 108.7 | 87.99
2017-06-29 10:30 | 112.25 | 93.15
2017-06-29 11:00 | 113.84 | 93.9
2017-06-29 11:30 | 125.54 | 107.5
2017-06-29 12:00 | 120.14 | 99.35
2017-06-29 12:30 | 126.44 | 108.58
2017-06-29 13:00 | 125.73 | 107.02
2017-06-29 13:30 | 122.42 | 103.73
2017-06-29 14:00 | 127.36 | 110.13
2017-06-29 14:30 | 125.85 | 108.46
2017-06-29 15:00 | 128.82 | 111.55
2017-06-29 15:30 | 126.72 | 108.59
2017-06-29 16:00 | 126 | 107.8
2017-06-29 16:30 | 120.36 | 100.23
2017-06-29 17:00 | 118.67 | 99.11
2017-06-29 17:30 | 120.86 | 102.65
2017-06-29 18:00 | 121.98 | 105.79
2017-06-29 18:30 | 119.72 | 101.05
2017-06-29 19:00 | 117.8 | 99.37
2017-06-29 19:30 | 120.2 | 102.59
2017-06-29 20:00 | 121.32 | 103.25
2017-06-29 20:30 | 117.61 | 98.84
2017-06-29 21:00 | 117.23 | 98.33
2017-06-29 21:30 | 119.4 | 100.74
2017-06-29 22:00 | 123.44 | 106.39
2017-06-29 22:30 | 116.7 | 97.32
2017-06-29 23:00 | 117.34 | 97.79
2017-06-29 23:30 | 120.55 | 101.1
2017-06-30 | 122.93 | 103.98
2017-06-30 00:30 | 115.55 | 92.99
2017-06-30 01:00 | 119.59 | 101.32
2017-06-30 01:30 | 116.92 | 97.62
2017-06-30 02:00 | 120.71 | 102.97
2017-06-30 02:30 | 116.43 | 98.31
2017-06-30 03:00 | 107.1 | 88.34
2017-06-30 03:30 | 107.7 | 88.67
2017-06-30 04:00 | 110.43 | 91.48
2017-06-30 04:30 | 113.66 | 94.38
2017-06-30 05:00 | 112.07 | 92.83
2017-06-30 05:30 | 120.13 | 102.59
2017-06-30 06:00 | 118.55 | 101.27
2017-06-30 06:30 | 113.69 | 93.39
2017-06-30 07:00 | 114.22 | 94.05
2017-06-30 07:30 | 115.62 | 98.46
2017-06-30 08:00 | 119.17 | 102.12
2017-06-30 08:30 | 118.39 | 102.26
2017-06-30 09:00 | 117.34 | 102.64
2017-06-30 09:30 | 106.99 | 91.53
2017-06-30 10:00 | 101.98 | 86.39
2017-06-30 10:30 | 95.62 | 76.88
2017-06-30 11:00 | 102.12 | 85.6
2017-06-30 11:30 | 105.73 | 88.66
2017-06-30 12:00 | 111.14 | 94.98
2017-06-30 12:30 | 121.78 | 108.34
2017-06-30 13:00 | 126.54 | 111.93
2017-06-30 13:30 | 126.69 | 110.81
2017-06-30 14:00 | 115.42 | 97.2
2017-06-30 14:30 | 119.61 | 102.19
2017-06-30 15:00 | 120.26 | 103
2017-06-30 15:30 | 120.81 | 103.5
2017-06-30 16:00 | 120.06 | 102.85
2017-06-30 16:30 | 120.79 | 103.51
2017-06-30 17:00 | 120.71 | 104.92
2017-06-30 17:30 | 125.03 | 108.97
2017-06-30 18:00 | 119.8 | 104.01
2017-06-30 18:30 | 116.38 | 99.03
2017-06-30 19:00 | 121 | 106.4
2017-06-30 19:30 | 120.08 | 105.21
2017-06-30 20:00 | 127.3 | 111.88
2017-06-30 20:30 | 126.96 | 111.56
2017-06-30 21:00 | 122.78 | 106.79
2017-06-30 21:30 | 116.99 | 99.85
2017-06-30 22:00 | 119.39 | 104.09
2017-06-30 22:30 | 122.15 | 106.74
2017-06-30 23:00 | 120.38 | 104.7
2017-06-30 23:30 | 128.57 | 113.72
2017-07-01 | 128.56 | 114.43
2017-07-01 00:30 | 129.03 | 115.62
2017-07-01 01:00 | 123.68 | 108.92
2017-07-01 01:30 | 124.6 | 108.91
2017-07-01 02:00 | 121.72 | 105.14
2017-07-01 02:30 | 117.79 | 101.39
2017-07-01 03:00 | 117.66 | 101.29
2017-07-01 03:30 | 121.82 | 106.75
2017-07-01 04:00 | 119.38 | 104.81
2017-07-01 04:30 | 118.13 | 103.96
2017-07-01 05:00 | 115.33 | 101.47
2017-07-01 05:30 | 123.28 | 108.85
2017-07-01 06:00 | 117.12 | 101.07
2017-07-01 06:30 | 114.54 | 96.92
2017-07-01 07:00 | 113.78 | 95.9
2017-07-01 07:30 | 108.18 | 89.87
2017-07-01 08:00 | 105.8 | 88.28
2017-07-01 08:30 | 109.51 | 93.94
2017-07-01 09:00 | 106.68 | 89.93
2017-07-01 09:30 | 111.34 | 95.51
2017-07-01 10:00 | 114.4 | 99.95
2017-07-01 10:30 | 113.72 | 96.85
2017-07-01 11:00 | 114.63 | 98.45
2017-07-01 11:30 | 109.9 | 93.21
2017-07-01 12:00 | 112.83 | 96.97
2017-07-01 12:30 | 118.29 | 103.87
2017-07-01 13:00 | 113.53 | 97.15
2017-07-01 13:30 | 114.5 | 98.23
2017-07-01 14:00 | 115.73 | 101.88
2017-07-01 14:30 | 115.58 | 102.04
2017-07-01 15:00 | 111.13 | 96.02
2017-07-01 15:30 | 111.96 | 95.83
2017-07-01 16:00 | 109.51 | 92.73
2017-07-01 16:30 | 115.38 | 100.99
2017-07-01 17:00 | 121.1 | 107.34
2017-07-01 17:30 | 121.99 | 108.16
2017-07-01 18:00 | 117.36 | 104.24
2017-07-01 18:30 | 115.33 | 99.32
2017-07-01 19:00 | 122.86 | 108.35
2017-07-01 19:30 | 124.58 | 110.55
2017-07-01 20:00 | 121.73 | 107.76
2017-07-01 20:30 | 116.39 | 101.47
2017-07-01 21:00 | 118.08 | 103.07
2017-07-01 21:30 | 120.55 | 106.56
2017-07-01 22:00 | 122.92 | 108.27
2017-07-01 22:30 | 119.41 | 103.97
2017-07-01 23:00 | 117.74 | 101.78
2017-07-01 23:30 | 123.82 | 109.06
2017-07-02 | 119.25 | 104.07
2017-07-02 00:30 | 125.96 | 112.07
2017-07-02 01:00 | 125.61 | 110.57
2017-07-02 01:30 | 124.86 | 110.09
2017-07-02 02:00 | 119.25 | 103.81
2017-07-02 02:30 | 118.85 | 103.57
2017-07-02 03:00 | 121.38 | 106.43
2017-07-02 03:30 | 120.11 | 103.4
2017-07-02 04:00 | 114.25 | 97.68
2017-07-02 04:30 | 109.58 | 92.44
2017-07-02 05:00 | 108.74 | 92.02
2017-07-02 05:30 | 115.66 | 101.29
2017-07-02 06:00 | 120.11 | 105.82
2017-07-02 06:30 | 115.68 | 98.07
2017-07-02 07:00 | 120.4 | 104.86
2017-07-02 07:30 | 120.52 | 105.5
2017-07-02 08:00 | 118.8 | 104.56
2017-07-02 08:30 | 111.53 | 96.27
2017-07-02 09:00 | 117.74 | 103.3
2017-07-02 09:30 | 119.06 | 104.65
2017-07-02 10:00 | 113.43 | 97.27
2017-07-02 10:30 | 113.61 | 97.81
2017-07-02 11:00 | 119.79 | 105.21
2017-07-02 11:30 | 113.58 | 97.35
2017-07-02 12:00 | 114.61 | 97.74
2017-07-02 12:30 | 121.22 | 106.95
2017-07-02 13:00 | 118.05 | 103.03
2017-07-02 13:30 | 117.27 | 101.56
2017-07-02 14:00 | 111.97 | 95
2017-07-02 14:30 | 110.61 | 94.02
2017-07-02 15:00 | 110.41 | 95.07
2017-07-02 15:30 | 112.59 | 97.44
2017-07-02 16:00 | 111.85 | 96.86
2017-07-02 16:30 | 121.09 | 107.53
2017-07-02 17:00 | 120.73 | 107.01
2017-07-02 17:30 | 118.76 | 105.66
2017-07-02 18:00 | 128.85 | 114.9
2017-07-02 18:30 | 117.77 | 101.66
2017-07-02 19:00 | 120.32 | 106.02
2017-07-02 19:30 | 124.78 | 110.35
2017-07-02 20:00 | 126.58 | 111.42
2017-07-02 20:30 | 131.12 | 115.27
2017-07-02 21:00 | 124.54 | 109.05
2017-07-02 21:30 | 120.23 | 104.69
2017-07-02 22:00 | 123.92 | 108.71
2017-07-02 22:30 | 123.64 | 107.67
2017-07-02 23:00 | 117.16 | 100.67
2017-07-02 23:30 | 121.86 | 106.15
2017-07-03 | 116.21 | 99.61
2017-07-03 00:30 | 120.04 | 104.33
2017-07-03 01:00 | 120.03 | 103.26
2017-07-03 01:30 | 120.92 | 103.34
2017-07-03 02:00 | 114.58 | 96.59
2017-07-03 02:30 | 116.93 | 99.57
2017-07-03 03:00 | 115.96 | 98.34
2017-07-03 03:30 | 122.22 | 106.92
2017-07-03 04:00 | 118.57 | 103.14
2017-07-03 04:30 | 117.02 | 102.53
2017-07-03 05:00 | 109.75 | 93.1
2017-07-03 05:30 | 114.02 | 98.04
2017-07-03 06:00 | 113.44 | 97.21
2017-07-03 06:30 | 108.56 | 89.71
2017-07-03 07:00 | 111 | 93.21
2017-07-03 07:30 | 120.81 | 106.45
2017-07-03 08:00 | 117.71 | 102.45
2017-07-03 08:30 | 124.17 | 110.47
2017-07-03 09:00 | 119.53 | 103.95
2017-07-03 09:30 | 119.47 | 103.53
2017-07-03 10:00 | 114.78 | 97.78
2017-07-03 10:30 | 121.66 | 105.28
2017-07-03 11:00 | 120.51 | 103.21
2017-07-03 11:30 | 116.71 | 97.96
2017-07-03 12:00 | 116.68 | 98.7
2017-07-03 12:30 | 122.38 | 104.28
2017-07-03 13:00 | 126.37 | 109.53
2017-07-03 13:30 | 120.44 | 102.98
2017-07-03 14:00 | 122.98 | 105.91
2017-07-03 14:30 | 126.27 | 109.53
2017-07-03 15:00 | 122.14 | 104.9
2017-07-03 15:30 | 123.43 | 105.89
2017-07-03 16:00 | 113.55 | 95.19
2017-07-03 16:30 | 117.29 | 100.9
2017-07-03 17:00 | 120.06 | 104.2
2017-07-03 17:30 | 121.57 | 106.96
2017-07-03 18:00 | 124.31 | 109.75
2017-07-03 18:30 | 113.89 | 96.49
2017-07-03 19:00 | 125.43 | 109.65
2017-07-03 19:30 | 129.01 | 113.71
2017-07-03 20:00 | 130 | 114.89
2017-07-03 20:30 | 126.02 | 111.45
2017-07-03 21:00 | 125.87 | 110.17
2017-07-03 21:30 | 122.62 | 107.11
2017-07-03 22:00 | 128.13 | 113.69
2017-07-03 22:30 | 127.89 | 113.21
2017-07-03 23:00 | 127.65 | 112.2
2017-07-03 23:30 | 121.55 | 106.02
2017-07-04 | 126.02 | 110.92
2017-07-04 00:30 | 118.06 | 102.21
2017-07-04 01:00 | 117.38 | 100.76
2017-07-04 01:30 | 117.89 | 101.65
2017-07-04 02:00 | 119.88 | 103.4
2017-07-04 02:30 | 120.9 | 105.08
2017-07-04 03:00 | 109.66 | 90.42
2017-07-04 03:30 | 109.84 | 90.91
2017-07-04 04:00 | 111.04 | 92.43
2017-07-04 04:30 | 117.44 | 101.24
2017-07-04 05:00 | 119.15 | 103.55
2017-07-04 05:30 | 120.98 | 106.83
2017-07-04 06:00 | 119.78 | 104.21
2017-07-04 06:30 | 120.23 | 104.73
2017-07-04 07:00 | 114.84 | 96.66
2017-07-04 07:30 | 116.08 | 98.66
2017-07-04 08:00 | 115.85 | 98.23
2017-07-04 08:30 | 114.49 | 98.33
2017-07-04 09:00 | 117.47 | 102.33
2017-07-04 09:30 | 117.64 | 102.76
2017-07-04 10:00 | 117.6 | 102.24
2017-07-04 10:30 | 115.4 | 97.65
2017-07-04 11:00 | 112.02 | 94.57
2017-07-04 11:30 | 115.6 | 98.07
2017-07-04 12:00 | 120.86 | 105.51
2017-07-04 12:30 | 119.49 | 103.18
2017-07-04 13:00 | 121.76 | 106.14
2017-07-04 13:30 | 123.83 | 108.3
2017-07-04 14:00 | 135.66 | 122.95
2017-07-04 14:30 | 125.15 | 110.4
2017-07-04 15:00 | 125.17 | 110.64
2017-07-04 15:30 | 127.55 | 113.29
2017-07-04 16:00 | 123.43 | 109.17
2017-07-04 16:30 | 126.91 | 112.8
2017-07-04 17:00 | 131.95 | 118.68
2017-07-04 17:30 | 131.61 | 118
2017-07-04 18:00 | 130.97 | 117.29
2017-07-04 18:30 | 127.18 | 112.36
2017-07-04 19:00 | 133.77 | 120.18
2017-07-04 19:30 | 135.29 | 122.82
2017-07-04 20:00 | 139.24 | 127.47
2017-07-04 20:30 | 134.28 | 123.26
2017-07-04 21:00 | 135.68 | 124.47
2017-07-04 21:30 | 135.48 | 124.79
2017-07-04 22:00 | 131.14 | 119.46
2017-07-04 22:30 | 130.18 | 117.87
2017-07-04 23:00 | 123.06 | 109.29
2017-07-04 23:30 | 121.75 | 106.44
2017-07-05 | 129.42 | 115.78
2017-07-05 00:30 | 119.18 | 103.88
2017-07-05 01:00 | 116.59 | 101.31
2017-07-05 01:30 | 124.59 | 112.01
2017-07-05 02:00 | 123 | 110.15
2017-07-05 02:30 | 122.92 | 110.16
2017-07-05 03:00 | 125.02 | 112.87
2017-07-05 03:30 | 124.33 | 112.02
2017-07-05 04:00 | 127.17 | 115.21
2017-07-05 04:30 | 127.18 | 115.56
2017-07-05 05:00 | 129.39 | 118.62
2017-07-05 05:30 | 128.2 | 117.32
2017-07-05 06:00 | 120.13 | 107.49
2017-07-05 06:30 | 107.93 | 90.29
2017-07-05 07:00 | 109.04 | 92.82
2017-07-05 07:30 | 113.23 | 99.41
2017-07-05 08:00 | 114.67 | 101.28
2017-07-05 08:30 | 115.6 | 101.16
2017-07-05 09:00 | 120.3 | 107.6
2017-07-05 09:30 | 113.41 | 99.64
2017-07-05 10:00 | 110.44 | 97.74
2017-07-05 10:30 | 115.79 | 103.03
2017-07-05 11:00 | 117.7 | 103.51
2017-07-05 11:30 | 118.94 | 102.35
2017-07-05 12:00 | 123.26 | 106.71
2017-07-05 12:30 | 119.33 | 103.18
2017-07-05 13:00 | 112.89 | 95.18
2017-07-05 13:30 | 121.12 | 106.05
2017-07-05 14:00 | 117.79 | 102.75
2017-07-05 14:30 | 112.43 | 94.98
2017-07-05 15:00 | 116.91 | 100.56
2017-07-05 15:30 | 121.31 | 106.72
2017-07-05 16:00 | 111.57 | 95.75
2017-07-05 16:30 | 114.72 | 100.99
2017-07-05 17:00 | 108.91 | 91.51
2017-07-05 17:30 | 115.11 | 99.35
2017-07-05 18:00 | 124.13 | 112.51
2017-07-05 18:30 | 117.09 | 103.28
2017-07-05 19:00 | 125.09 | 112.71
2017-07-05 19:30 | 122.36 | 108.95
2017-07-05 20:00 | 121.54 | 107.68
2017-07-05 20:30 | 121.67 | 109.06
2017-07-05 21:00 | 126.53 | 115.35
2017-07-05 21:30 | 125.06 | 113.52
2017-07-05 22:00 | 122.31 | 110.53
2017-07-05 22:30 | 116.38 | 103.07
2017-07-05 23:00 | 116.22 | 102.26
2017-07-05 23:30 | 116.06 | 101.49
2017-07-06 | 116.72 | 102.32
2017-07-06 00:30 | 111.55 | 95.48
2017-07-06 01:00 | 113.13 | 98.25
2017-07-06 01:30 | 113.33 | 99.21
2017-07-06 02:00 | 119.9 | 107.72
2017-07-06 02:30 | 118.49 | 105.71
2017-07-06 03:00 | 120.12 | 107.51
2017-07-06 03:30 | 115.58 | 101.78
2017-07-06 04:00 | 121.14 | 107.38
2017-07-06 04:30 | 118.01 | 104.58
2017-07-06 05:00 | 123.5 | 110.77
2017-07-06 05:30 | 120.75 | 106.66
2017-07-06 06:00 | 122.9 | 109.3
2017-07-06 06:30 | 116.47 | 100.55
2017-07-06 07:00 | 123.07 | 108.55
2017-07-06 07:30 | 132.16 | 119.6
2017-07-06 08:00 | 135.08 | 122.3
2017-07-06 08:30 | 123.74 | 109.84
2017-07-06 09:00 | 125.99 | 111.92
2017-07-06 09:30 | 126.69 | 112.57
2017-07-06 10:00 | 125.76 | 110.89
2017-07-06 10:30 | 123.79 | 107.22
2017-07-06 11:00 | 125.94 | 110.27
2017-07-06 11:30 | 128.84 | 113.41
2017-07-06 12:00 | 127.13 | 111.16
2017-07-06 12:30 | 124.07 | 107.83
2017-07-06 13:00 | 127.84 | 112.21
2017-07-06 13:30 | 128.63 | 113.98
2017-07-06 14:00 | 125.47 | 109.81
2017-07-06 14:30 | 129.52 | 115.34
2017-07-06 15:00 | 122.85 | 106.58
2017-07-06 15:30 | 122.19 | 105.61
2017-07-06 16:00 | 119.8 | 103.51
2017-07-06 16:30 | 128.34 | 112.96
2017-07-06 17:00 | 133.81 | 119.53
2017-07-06 17:30 | 131.75 | 118.1
2017-07-06 18:00 | 142.2 | 128.97
2017-07-06 18:30 | 126.6 | 109.88
2017-07-06 19:00 | 137.36 | 123.61
2017-07-06 19:30 | 133.13 | 120.36
2017-07-06 20:00 | 133.96 | 122.23
2017-07-06 20:30 | 123.72 | 110.86
2017-07-06 21:00 | 128.63 | 117.03
2017-07-06 21:30 | 126.08 | 113.53
2017-07-06 22:00 | 133.86 | 121.39
2017-07-06 22:30 | 129 | 116.59
2017-07-06 23:00 | 132.09 | 120.2
2017-07-06 23:30 | 128.6 | 116.47
2017-07-07 | 120.72 | 105.71
2017-07-07 00:30 | 117.62 | 101.93
2017-07-07 01:00 | 117.58 | 101.66
2017-07-07 01:30 | 116.79 | 100.29
2017-07-07 02:00 | 116.67 | 101.16
2017-07-07 02:30 | 118.92 | 104.13
2017-07-07 03:00 | 121.14 | 106.41
2017-07-07 03:30 | 119.83 | 103.92
2017-07-07 04:00 | 116.34 | 100.29
2017-07-07 04:30 | 113.39 | 98.69
2017-07-07 05:00 | 119.31 | 106.14
2017-07-07 05:30 | 121.81 | 109.75
2017-07-07 06:00 | 117.82 | 103.51
2017-07-07 06:30 | 109.75 | 93.13
2017-07-07 07:00 | 112.58 | 97.02
2017-07-07 07:30 | 115.43 | 101.45
2017-07-07 08:00 | 120.62 | 106.25
2017-07-07 08:30 | 122.61 | 108.29
2017-07-07 09:00 | 114.93 | 99.41
2017-07-07 09:30 | 109.94 | 91.61
2017-07-07 10:00 | 106.8 | 88.25
2017-07-07 10:30 | 108.04 | 90.39
2017-07-07 11:00 | 115.27 | 97.65
2017-07-07 11:30 | 115.32 | 98.24
2017-07-07 12:00 | 117.49 | 101.01
2017-07-07 12:30 | 118.34 | 103.16
2017-07-07 13:00 | 115.7 | 99.5
2017-07-07 13:30 | 113.58 | 98.48
2017-07-07 14:00 | 117.9 | 103.76
2017-07-07 14:30 | 113.11 | 98.38
2017-07-07 15:00 | 111.93 | 96.03
2017-07-07 15:30 | 108.89 | 93.68
2017-07-07 16:00 | 116.19 | 101.02
2017-07-07 16:30 | 124.26 | 110.55
2017-07-07 17:00 | 102.85 | 83.6
2017-07-07 17:30 | 108.18 | 90.43
2017-07-07 18:00 | 110.98 | 93.89
2017-07-07 18:30 | 104.85 | 88.42
2017-07-07 19:00 | 108.02 | 91.81
2017-07-07 19:30 | 110.22 | 94.76
2017-07-07 20:00 | 109.68 | 92.74
2017-07-07 20:30 | 113.2 | 98.35
2017-07-07 21:00 | 114.59 | 98.12
2017-07-07 21:30 | 113.01 | 95.69
2017-07-07 22:00 | 109.18 | 90.16
2017-07-07 22:30 | 110.2 | 92
2017-07-07 23:00 | 106.24 | 87.06
2017-07-07 23:30 | 106.17 | 88.86
2017-07-08 | 111.1 | 95.75
2017-07-08 00:30 | 110.83 | 95.25
2017-07-08 01:00 | 110.19 | 93.93
2017-07-08 01:30 | 107.61 | 90.28
2017-07-08 02:00 | 107.92 | 91.19
2017-07-08 02:30 | 107.56 | 90.06
2017-07-08 03:00 | 106.52 | 87.86
2017-07-08 03:30 | 106.99 | 88.74
2017-07-08 04:00 | 105.73 | 87.39
2017-07-08 04:30 | 104.22 | 85.52
2017-07-08 05:00 | 108.98 | 92.5
2017-07-08 05:30 | 109.84 | 93.63
2017-07-08 06:00 | 110.37 | 94.38
2017-07-08 06:30 | 103 | 83.62
2017-07-08 07:00 | 107.56 | 89.71
2017-07-08 07:30 | 110.41 | 93.32
2017-07-08 08:00 | 110.29 | 94.03
2017-07-08 08:30 | 107.26 | 91.21
2017-07-08 09:00 | 107.77 | 90.58
2017-07-08 09:30 | 110.15 | 93.92
2017-07-08 10:00 | 109.83 | 94.14
2017-07-08 10:30 | 102.56 | 82.67
2017-07-08 11:00 | 98.86 | 76.09
2017-07-08 11:30 | 100.82 | 77.13
2017-07-08 12:00 | 100.2 | 77.05
2017-07-08 12:30 | 101.1 | 79.28
2017-07-08 13:00 | 101.75 | 80.06
2017-07-08 13:30 | 102.52 | 80.45
2017-07-08 14:00 | 108.7 | 89.6
2017-07-08 14:30 | 111.13 | 92.67
2017-07-08 15:00 | 105.79 | 86.65
2017-07-08 15:30 | 110.64 | 92.94
2017-07-08 16:00 | 115.83 | 98.68
2017-07-08 16:30 | 112.76 | 95.4
2017-07-08 17:00 | 122.91 | 108.11
2017-07-08 17:30 | 122.44 | 107.49
2017-07-08 18:00 | 122.63 | 108.27
2017-07-08 18:30 | 113.17 | 96.63
2017-07-08 19:00 | 116.49 | 101.93
2017-07-08 19:30 | 112.18 | 96.75
2017-07-08 20:00 | 111.39 | 95.89
2017-07-08 20:30 | 108.27 | 92.11
2017-07-08 21:00 | 111.58 | 95.73
2017-07-08 21:30 | 114.72 | 99.45
2017-07-08 22:00 | 115.01 | 99.19
2017-07-08 22:30 | 111.42 | 94.54
2017-07-08 23:00 | 114.2 | 97.61
2017-07-08 23:30 | 116.14 | 98.52
2017-07-09 | 118.71 | 103.22
2017-07-09 00:30 | 119.09 | 102.9
2017-07-09 01:00 | 118.61 | 101.65
2017-07-09 01:30 | 115.81 | 98.06
2017-07-09 02:00 | 119.35 | 103.26
2017-07-09 02:30 | 116.64 | 99.83
2017-07-09 03:00 | 116.32 | 98.92
2017-07-09 03:30 | 115.37 | 97.51
2017-07-09 04:00 | 112.96 | 94.28
2017-07-09 04:30 | 111.42 | 92.18
2017-07-09 05:00 | 96.17 | 75.54
2017-07-09 05:30 | 92.62 | 68.32
2017-07-09 06:00 | 98.26 | 76.23
2017-07-09 06:30 | 91.58 | 64.25
2017-07-09 07:00 | 95.49 | 70.61
2017-07-09 07:30 | 95.13 | 70.36
2017-07-09 08:00 | 99.78 | 78.38
2017-07-09 08:30 | 105.25 | 87.35
2017-07-09 09:00 | 101.32 | 82.47
2017-07-09 09:30 | 95.68 | 75
2017-07-09 10:00 | 97.51 | 77.84
2017-07-09 10:30 | 96.4 | 76.21
2017-07-09 11:00 | 99.98 | 81.15
2017-07-09 11:30 | 99.99 | 79.19
2017-07-09 12:00 | 97.45 | 74.72
2017-07-09 12:30 | 96.2 | 73.56
2017-07-09 13:00 | 101.24 | 83.11
2017-07-09 13:30 | 97.3 | 76.16
2017-07-09 14:00 | 102.38 | 83.59
2017-07-09 14:30 | 105.29 | 86.93
2017-07-09 15:00 | 105.92 | 87.95
2017-07-09 15:30 | 105.48 | 87.32
2017-07-09 16:00 | 109.19 | 90.77
2017-07-09 16:30 | 106.9 | 88.07
2017-07-09 17:00 | 108.47 | 90.91
2017-07-09 17:30 | 108.52 | 92.2
2017-07-09 18:00 | 108.54 | 93.15
2017-07-09 18:30 | 109.93 | 93.45
2017-07-09 19:00 | 112.38 | 97.72
2017-07-09 19:30 | 112.77 | 97.62
2017-07-09 20:00 | 115.14 | 101.01
2017-07-09 20:30 | 118.59 | 104.51
2017-07-09 21:00 | 110.54 | 96.47
2017-07-09 21:30 | 111.89 | 97.86
2017-07-09 22:00 | 107.73 | 92.48
2017-07-09 22:30 | 106.86 | 91.56
2017-07-09 23:00 | 102.97 | 85.97
2017-07-09 23:30 | 101.87 | 83.43
2017-07-10 | 99.15 | 79.96
2017-07-10 00:30 | 99.56 | 81.01
2017-07-10 01:00 | 100.13 | 82.17
2017-07-10 01:30 | 100.32 | 81.75
2017-07-10 02:00 | 102.35 | 85.23
2017-07-10 02:30 | 100.44 | 82.66
2017-07-10 03:00 | 96.41 | 77.53
2017-07-10 03:30 | 96.43 | 77.27
2017-07-10 04:00 | 97.34 | 78.72
2017-07-10 04:30 | 95.14 | 76.45
2017-07-10 05:00 | 97.09 | 78.99
2017-07-10 05:30 | 97.62 | 80.12
2017-07-10 06:00 | 77.08 | 73.56
2017-07-10 06:30 | 58.29 | 56.76
2017-07-10 07:00 | 67.48 | 66.01
2017-07-10 07:30 | 70.18 | 68.15
2017-07-10 08:00 | 71.32 | 69.41
2017-07-10 08:30 | 70.97 | 68.97
2017-07-10 09:00 | 75.61 | 72.64
2017-07-10 09:30 | 78.32 | 75.52
2017-07-10 10:00 | 79.33 | 76.19
2017-07-10 10:30 | 78.68 | 75.36
2017-07-10 11:00 | 80.43 | 76.81
2017-07-10 11:30 | 80.81 | 77.12
2017-07-10 12:00 | 83.41 | 80.06
2017-07-10 12:30 | 84.9 | 80.92
2017-07-10 13:00 | 85.67 | 81.8
2017-07-10 13:30 | 84.53 | 80.67
2017-07-10 14:00 | 83.52 | 79.02
2017-07-10 14:30 | 87.7 | 83.64
2017-07-10 15:00 | 81.85 | 78.21
2017-07-10 15:30 | 80.11 | 76.01
2017-07-10 16:00 | 87.5 | 83.12
2017-07-10 16:30 | 86.73 | 83.08
2017-07-10 17:00 | 83.72 | 79.74
2017-07-10 17:30 | 83.07 | 79.96
2017-07-10 18:00 | 88.88 | 85.61
2017-07-10 18:30 | 81.59 | 77.49
2017-07-10 19:00 | 89.53 | 86.33
2017-07-10 19:30 | 92.9 | 89.56
2017-07-10 20:00 | 90.32 | 86.71
2017-07-10 20:30 | 88.52 | 84.79
2017-07-10 21:00 | 87.45 | 84.22
2017-07-10 21:30 | 88.79 | 85.65
2017-07-10 22:00 | 88.12 | 84.97
2017-07-10 22:30 | 79.57 | 76.71
2017-07-10 23:00 | 79.41 | 76.83
2017-07-10 23:30 | 76.58 | 74.22
2017-07-11 | 78.82 | 76.67
2017-07-11 00:30 | 81.53 | 79.32
2017-07-11 01:00 | 79.32 | 77.2
2017-07-11 01:30 | 84.53 | 82.51
2017-07-11 02:00 | 85.84 | 83.79
2017-07-11 02:30 | 83.09 | 81.17
2017-07-11 03:00 | 82.06 | 80.25
2017-07-11 03:30 | 79.62 | 77.38
2017-07-11 04:00 | 81.39 | 79.25
2017-07-11 04:30 | 84.56 | 82.51
2017-07-11 05:00 | 82.43 | 80.42
2017-07-11 05:30 | 86.02 | 84.04
2017-07-11 06:00 | 76.64 | 75
2017-07-11 06:30 | 74.14 | 71.98
2017-07-11 07:00 | 83.25 | 81.54
2017-07-11 07:30 | 84.1 | 81.94
2017-07-11 08:00 | 79.63 | 77.46
2017-07-11 08:30 | 79.63 | 76.89
2017-07-11 09:00 | 81.46 | 78.73
2017-07-11 09:30 | 74.06 | 70.88
2017-07-11 10:00 | 69.65 | 66.6
2017-07-11 10:30 | 68.74 | 65.65
2017-07-11 11:00 | 70.66 | 67.27
2017-07-11 11:30 | 69.04 | 65.42
2017-07-11 12:00 | 69.23 | 65.49
2017-07-11 12:30 | 69.35 | 65.31
2017-07-11 13:00 | 78.72 | 76.01
2017-07-11 13:30 | 81.9 | 78.98
2017-07-11 14:00 | 78.55 | 75.32
2017-07-11 14:30 | 82.77 | 79.41
2017-07-11 15:00 | 83.22 | 79.89
2017-07-11 15:30 | 81.34 | 78.23
2017-07-11 16:00 | 77.7 | 74.23
2017-07-11 16:30 | 75.36 | 72.41
2017-07-11 17:00 | 82.46 | 80
2017-07-11 17:30 | 92.48 | 79.57
2017-07-11 18:00 | 106.25 | 83.83
2017-07-11 18:30 | 101.5 | 74.48
2017-07-11 19:00 | 106.89 | 84.28
2017-07-11 19:30 | 106.14 | 83.93
2017-07-11 20:00 | 110.07 | 90.99
2017-07-11 20:30 | 106.67 | 86.05
2017-07-11 21:00 | 109.32 | 88.67
2017-07-11 21:30 | 106.05 | 83.56
2017-07-11 22:00 | 108.35 | 86.66
2017-07-11 22:30 | 106.03 | 84.34
2017-07-11 23:00 | 105.12 | 83.02
2017-07-11 23:30 | 103.26 | 80.36
2017-07-12 | 105.97 | 84.83
2017-07-12 00:30 | 106.63 | 85.15
2017-07-12 01:00 | 105.86 | 84.4
2017-07-12 01:30 | 101.79 | 78.64
2017-07-12 02:00 | 101.55 | 77.63
2017-07-12 02:30 | 101.09 | 76.5
2017-07-12 03:00 | 103.56 | 80.69
2017-07-12 03:30 | 101.66 | 77.82
2017-07-12 04:00 | 106.81 | 85.18
2017-07-12 04:30 | 110.49 | 89.98
2017-07-12 05:00 | 108.08 | 86.66
2017-07-12 05:30 | 106.13 | 84.04
2017-07-12 06:00 | 102.98 | 81.93
2017-07-12 06:30 | 98.35 | 72.47
2017-07-12 07:00 | 100.67 | 76.39
2017-07-12 07:30 | 100.39 | 76.62
2017-07-12 08:00 | 101.31 | 77.53
2017-07-12 08:30 | 101.12 | 76.98
2017-07-12 09:00 | 108.91 | 86.79
2017-07-12 09:30 | 104.05 | 78.52
2017-07-12 10:00 | 102.64 | 80.32
2017-07-12 10:30 | 108 | 85.05
2017-07-12 11:00 | 109.43 | 89.17
2017-07-12 11:30 | 107.42 | 86.4
2017-07-12 12:00 | 107.86 | 87.19
2017-07-12 12:30 | 108.06 | 89.2
2017-07-12 13:00 | 112.87 | 96.25
2017-07-12 13:30 | 99.1 | 78.55
2017-07-12 14:00 | 99.78 | 80.04
2017-07-12 14:30 | 94.14 | 71.97
2017-07-12 15:00 | 91.91 | 67.87
2017-07-12 15:30 | 96.1 | 75.44
2017-07-12 16:00 | 100.41 | 81.24
2017-07-12 16:30 | 103.1 | 85.08
2017-07-12 17:00 | 102.46 | 83.85
2017-07-12 17:30 | 107.2 | 90.92
2017-07-12 18:00 | 108.96 | 94.44
2017-07-12 18:30 | 103.81 | 85.04
2017-07-12 19:00 | 105.16 | 88.61
2017-07-12 19:30 | 102.02 | 84.09
2017-07-12 20:00 | 108.27 | 92.22
2017-07-12 20:30 | 106.63 | 89.88
2017-07-12 21:00 | 106.92 | 90.18
2017-07-12 21:30 | 100.35 | 81.64
2017-07-12 22:00 | 103 | 84.93
2017-07-12 22:30 | 106.31 | 89.22
2017-07-12 23:00 | 103.22 | 86.1
2017-07-12 23:30 | 98.93 | 78.34
2017-07-13 | 100.57 | 81.07
2017-07-13 00:30 | 99.03 | 79.77
2017-07-13 01:00 | 101.15 | 83.11
2017-07-13 01:30 | 107.86 | 92.34
2017-07-13 02:00 | 101.46 | 84.51
2017-07-13 02:30 | 95.94 | 75.94
2017-07-13 03:00 | 99.01 | 80.09
2017-07-13 03:30 | 97.06 | 77.02
2017-07-13 04:00 | 97.05 | 77.06
2017-07-13 04:30 | 98.27 | 81.36
2017-07-13 05:00 | 95.66 | 78.81
2017-07-13 05:30 | 99.61 | 84.12
2017-07-13 06:00 | 96.95 | 80.13
2017-07-13 06:30 | 100.27 | 83.98
2017-07-13 07:00 | 97.28 | 81.21
2017-07-13 07:30 | 95.49 | 77.2
2017-07-13 08:00 | 94.29 | 75.93
2017-07-13 08:30 | 95.15 | 78.38
2017-07-13 09:00 | 99.37 | 83.49
2017-07-13 09:30 | 102.07 | 86.84
2017-07-13 10:00 | 95.76 | 76.01
2017-07-13 10:30 | 93.15 | 72.67
2017-07-13 11:00 | 92.36 | 70.7
2017-07-13 11:30 | 95.98 | 77.07
2017-07-13 12:00 | 93.68 | 74.2
2017-07-13 12:30 | 96.42 | 78.43
2017-07-13 13:00 | 99.21 | 82.03
2017-07-13 13:30 | 97.27 | 79.15
2017-07-13 14:00 | 97.85 | 79.51
2017-07-13 14:30 | 97.6 | 78.62
2017-07-13 15:00 | 93.86 | 73.6
2017-07-13 15:30 | 89.31 | 69.24
2017-07-13 16:00 | 94.65 | 77.09
2017-07-13 16:30 | 96.15 | 80.02
2017-07-13 17:00 | 96.01 | 80.08
2017-07-13 17:30 | 105.77 | 92.78
2017-07-13 18:00 | 97.34 | 82.09
2017-07-13 18:30 | 99.1 | 84.69
2017-07-13 19:00 | 98.17 | 85.09
2017-07-13 19:30 | 108.66 | 97.9
2017-07-13 20:00 | 100.5 | 87.98
2017-07-13 20:30 | 108.42 | 96.22
2017-07-13 21:00 | 109.98 | 98.16
2017-07-13 21:30 | 106.57 | 93.75
2017-07-13 22:00 | 105.83 | 91.96
2017-07-13 22:30 | 106.47 | 92.54
2017-07-13 23:00 | 104.73 | 89.38
2017-07-13 23:30 | 101.5 | 85.61
2017-07-14 | 102.04 | 86.76
2017-07-14 00:30 | 103.58 | 89.36
2017-07-14 01:00 | 104.61 | 91.86
2017-07-14 01:30 | 110.11 | 98.33
2017-07-14 02:00 | 111.53 | 99.46
2017-07-14 02:30 | 104.5 | 90.67
2017-07-14 03:00 | 107.32 | 92.56
2017-07-14 03:30 | 108.1 | 93.62
2017-07-14 04:00 | 107.41 | 93.29
2017-07-14 04:30 | 106.36 | 91.88
2017-07-14 05:00 | 113.08 | 100.82
2017-07-14 05:30 | 106.47 | 93.93
2017-07-14 06:00 | 105.11 | 92.17
2017-07-14 06:30 | 98.02 | 83.31
2017-07-14 07:00 | 104.93 | 92.14
2017-07-14 07:30 | 111.93 | 100.48
2017-07-14 08:00 | 101.23 | 87.09
2017-07-14 08:30 | 104.23 | 91.22
2017-07-14 09:00 | 99.47 | 84.71
2017-07-14 09:30 | 94.47 | 77.57
2017-07-14 10:00 | 99.03 | 84.17
2017-07-14 10:30 | 103.57 | 89.23
2017-07-14 11:00 | 100.41 | 85.6
2017-07-14 11:30 | 100.23 | 85.53
2017-07-14 12:00 | 101.95 | 87.36
2017-07-14 12:30 | 104.23 | 90.44
2017-07-14 13:00 | 104.25 | 90.67
2017-07-14 13:30 | 102.71 | 87.75
2017-07-14 14:00 | 99.68 | 84.7
2017-07-14 14:30 | 100.69 | 85.77
2017-07-14 15:00 | 99.53 | 83.97
2017-07-14 15:30 | 99.72 | 86.29
2017-07-14 16:00 | 111.32 | 99.67
2017-07-14 16:30 | 108.85 | 96.9
2017-07-14 17:00 | 104.64 | 90.86
2017-07-14 17:30 | 102.35 | 89.15
2017-07-14 18:00 | 102.68 | 89.43
2017-07-14 18:30 | 96.85 | 81.86
2017-07-14 19:00 | 103.45 | 90.62
2017-07-14 19:30 | 106.27 | 92.58
2017-07-14 20:00 | 110.02 | 96.96
2017-07-14 20:30 | 110.28 | 97.49
2017-07-14 21:00 | 110.26 | 97.43
2017-07-14 21:30 | 119.12 | 107.4
2017-07-14 22:00 | 117.25 | 105.33
2017-07-14 22:30 | 119.14 | 107.02
2017-07-14 23:00 | 113.83 | 101.17
2017-07-14 23:30 | 108.93 | 95.12
2017-07-15 | 115.14 | 103.17
2017-07-15 00:30 | 121.58 | 110.45
2017-07-15 01:00 | 118.15 | 105.56
2017-07-15 01:30 | 118.58 | 106.38
2017-07-15 02:00 | 118.33 | 105.94
2017-07-15 02:30 | 120.45 | 108.81
2017-07-15 03:00 | 117.09 | 105.11
2017-07-15 03:30 | 115.92 | 101.82
2017-07-15 04:00 | 111.66 | 98.65
2017-07-15 04:30 | 109.97 | 96.02
2017-07-15 05:00 | 111.14 | 97.42
2017-07-15 05:30 | 114.89 | 101.83
2017-07-15 06:00 | 109.8 | 96.39
2017-07-15 06:30 | 99.15 | 81.17
2017-07-15 07:00 | 111.1 | 96.91
2017-07-15 07:30 | 115.35 | 105.89
2017-07-15 08:00 | 109.28 | 101.09
2017-07-15 08:30 | 103.47 | 90.97
2017-07-15 09:00 | 107.75 | 94.97
2017-07-15 09:30 | 103.58 | 89.97
2017-07-15 10:00 | 105.99 | 91.71
2017-07-15 10:30 | 103.89 | 88.43
2017-07-15 11:00 | 107.08 | 91.87
2017-07-15 11:30 | 106.65 | 91.7
2017-07-15 12:00 | 104.81 | 89.43
2017-07-15 12:30 | 111.72 | 97.08
2017-07-15 13:00 | 105.86 | 91.55
2017-07-15 13:30 | 111.01 | 96.98
2017-07-15 14:00 | 113.31 | 100.21
2017-07-15 14:30 | 111.79 | 98.42
2017-07-15 15:00 | 111.77 | 97.14
2017-07-15 15:30 | 110.01 | 95.68
2017-07-15 16:00 | 104.31 | 90.12
2017-07-15 16:30 | 110.29 | 96.95
2017-07-15 17:00 | 114.1 | 101.02
2017-07-15 17:30 | 119.84 | 107.56
2017-07-15 18:00 | 114.17 | 101.99
2017-07-15 18:30 | 109.24 | 95.71
2017-07-15 19:00 | 109.71 | 97.11
2017-07-15 19:30 | 115.53 | 103.17
2017-07-15 20:00 | 118.94 | 106.25
2017-07-15 20:30 | 106.32 | 92.49
2017-07-15 21:00 | 112.01 | 99.46
2017-07-15 21:30 | 114.81 | 102.34
2017-07-15 22:00 | 120.29 | 108.34
2017-07-15 22:30 | 107.1 | 94.47
2017-07-15 23:00 | 106.38 | 93.32
2017-07-15 23:30 | 104.94 | 92.11
2017-07-16 | 108.1 | 95.76
2017-07-16 00:30 | 109.92 | 97.4
2017-07-16 01:00 | 112.12 | 99.37
2017-07-16 01:30 | 108.58 | 94.25
2017-07-16 02:00 | 109.87 | 94.55
2017-07-16 02:30 | 110.85 | 96.9
2017-07-16 03:00 | 105.79 | 91.09
2017-07-16 03:30 | 106.6 | 91.51
2017-07-16 04:00 | 109.6 | 95.35
2017-07-16 04:30 | 110.38 | 95.63
2017-07-16 05:00 | 108.33 | 93.4
2017-07-16 05:30 | 105.17 | 91.44
2017-07-16 06:00 | 108.36 | 95.61
2017-07-16 06:30 | 101.85 | 85.18
2017-07-16 07:00 | 107.84 | 92.89
2017-07-16 07:30 | 111.58 | 98.15
2017-07-16 08:00 | 108.01 | 94.36
2017-07-16 08:30 | 100.17 | 92.37
2017-07-16 09:00 | 98.99 | 91.06
2017-07-16 09:30 | 102.99 | 85.95
2017-07-16 10:00 | 102.09 | 85.43
2017-07-16 10:30 | 104.07 | 88.09
2017-07-16 11:00 | 105.66 | 90.32
2017-07-16 11:30 | 107.3 | 92.28
2017-07-16 12:00 | 103.3 | 86.72
2017-07-16 12:30 | 96.79 | 80.05
2017-07-16 13:00 | 101.87 | 86.72
2017-07-16 13:30 | 101.36 | 85.47
2017-07-16 14:00 | 106.08 | 91.58
2017-07-16 14:30 | 105.29 | 91.63
2017-07-16 15:00 | 105.44 | 91.55
2017-07-16 15:30 | 106.66 | 91.05
2017-07-16 16:00 | 109.49 | 95.6
2017-07-16 16:30 | 117.52 | 104.68
2017-07-16 17:00 | 114.48 | 101.27
2017-07-16 17:30 | 112.56 | 100.08
2017-07-16 18:00 | 118.84 | 106.47
2017-07-16 18:30 | 115.37 | 101.93
2017-07-16 19:00 | 116.1 | 103.62
2017-07-16 19:30 | 116.49 | 104.11
2017-07-16 20:00 | 120.77 | 108.57
2017-07-16 20:30 | 118.84 | 106.84
2017-07-16 21:00 | 115.22 | 102.77
2017-07-16 21:30 | 117.06 | 104.7
2017-07-16 22:00 | 118.28 | 106
2017-07-16 22:30 | 110.38 | 95.84
2017-07-16 23:00 | 113.59 | 99.58
2017-07-16 23:30 | 108.02 | 93.63
2017-07-17 | 114.55 | 101.54
2017-07-17 00:30 | 111.82 | 98.78
2017-07-17 01:00 | 111.55 | 97.63
2017-07-17 01:30 | 111.8 | 97.34
2017-07-17 02:00 | 110.85 | 96.18
2017-07-17 02:30 | 108.45 | 94.81
2017-07-17 03:00 | 102.48 | 87.77
2017-07-17 03:30 | 106.32 | 91.68
2017-07-17 04:00 | 105.77 | 90.84
2017-07-17 04:30 | 108.23 | 94.41
2017-07-17 05:00 | 113.45 | 100.89
2017-07-17 05:30 | 108.98 | 94.76
2017-07-17 06:00 | 106.81 | 92.64
2017-07-17 06:30 | 102.78 | 86.36
2017-07-17 07:00 | 105.24 | 90.07
2017-07-17 07:30 | 109.84 | 97.21
2017-07-17 08:00 | 115.76 | 103.76
2017-07-17 08:30 | 112.75 | 100.36
2017-07-17 09:00 | 107.64 | 94.77
2017-07-17 09:30 | 104.81 | 91.24
2017-07-17 10:00 | 99.83 | 85.79
2017-07-17 10:30 | 98.12 | 82.27
2017-07-17 11:00 | 101.43 | 86.14
2017-07-17 11:30 | 104.87 | 87.89
2017-07-17 12:00 | 106.41 | 90.42
2017-07-17 12:30 | 106.49 | 91.06
2017-07-17 13:00 | 102.48 | 85.63
2017-07-17 13:30 | 106.59 | 90.07
2017-07-17 14:00 | 107.25 | 90.46
2017-07-17 14:30 | 109.24 | 93.62
2017-07-17 15:00 | 113.42 | 98.74
2017-07-17 15:30 | 108.73 | 91.71
2017-07-17 16:00 | 108.29 | 92.11
2017-07-17 16:30 | 113.82 | 100.21
2017-07-17 17:00 | 113.65 | 100.91
2017-07-17 17:30 | 116.41 | 102.8
2017-07-17 18:00 | 116.41 | 103.01
2017-07-17 18:30 | 103.25 | 85.56
2017-07-17 19:00 | 119.39 | 106.17
2017-07-17 19:30 | 117.44 | 103.96
2017-07-17 20:00 | 119.26 | 105.99
2017-07-17 20:30 | 114.3 | 100.57
2017-07-17 21:00 | 118.11 | 104.66
2017-07-17 21:30 | 107.97 | 91.45
2017-07-17 22:00 | 105.69 | 89.01
2017-07-17 22:30 | 106.69 | 90
2017-07-17 23:00 | 103.87 | 84.95
2017-07-17 23:30 | 113.24 | 98.68
2017-07-18 | 107.34 | 90.68
2017-07-18 00:30 | 109.51 | 93.98
2017-07-18 01:00 | 107.45 | 89.82
2017-07-18 01:30 | 106.76 | 89.02
2017-07-18 02:00 | 108.77 | 93.51
2017-07-18 02:30 | 105.91 | 89.66
2017-07-18 03:00 | 105.83 | 89.68
2017-07-18 03:30 | 109.7 | 93.06
2017-07-18 04:00 | 109.74 | 93.98
2017-07-18 04:30 | 111.59 | 96.13
2017-07-18 05:00 | 117.83 | 103.89
2017-07-18 05:30 | 113.99 | 98.66
2017-07-18 06:00 | 117.81 | 103.91
2017-07-18 06:30 | 109.89 | 92.46
2017-07-18 07:00 | 113.2 | 97.48
2017-07-18 07:30 | 117.45 | 103.21
2017-07-18 08:00 | 115.22 | 100.32
2017-07-18 08:30 | 110.72 | 94.93
2017-07-18 09:00 | 116.32 | 102.77
2017-07-18 09:30 | 114.49 | 97.91
2017-07-18 10:00 | 112.7 | 97.16
2017-07-18 10:30 | 113.79 | 96.39
2017-07-18 11:00 | 106.64 | 85.83
2017-07-18 11:30 | 104.24 | 83.39
2017-07-18 12:00 | 104.55 | 86.62
2017-07-18 12:30 | 106.86 | 89.56
2017-07-18 13:00 | 105.46 | 86.11
2017-07-18 13:30 | 115.76 | 100.68
2017-07-18 14:00 | 116.87 | 100.65
2017-07-18 14:30 | 122.81 | 108.58
2017-07-18 15:00 | 120.31 | 106.37
2017-07-18 15:30 | 112.9 | 95.99
2017-07-18 16:00 | 114.51 | 98.78
2017-07-18 16:30 | 117.49 | 101.63
2017-07-18 17:00 | 118.96 | 103.83
2017-07-18 17:30 | 118.03 | 103.5
2017-07-18 18:00 | 121.81 | 108.04
2017-07-18 18:30 | 115.59 | 100.27
2017-07-18 19:00 | 114.09 | 99.48
2017-07-18 19:30 | 122.76 | 110.82
2017-07-18 20:00 | 122.97 | 110.59
2017-07-18 20:30 | 126.45 | 113.88
2017-07-18 21:00 | 119.17 | 105.53
2017-07-18 21:30 | 123.7 | 109.72
2017-07-18 22:00 | 124.02 | 110.31
2017-07-18 22:30 | 125.34 | 112
2017-07-18 23:00 | 119.42 | 105.16
2017-07-18 23:30 | 123.06 | 108.71
2017-07-19 | 113.78 | 97.14
2017-07-19 00:30 | 117.11 | 100.9
2017-07-19 01:00 | 123.03 | 108.58
2017-07-19 01:30 | 124.82 | 110.32
2017-07-19 02:00 | 121.43 | 105.35
2017-07-19 02:30 | 118.45 | 102.24
2017-07-19 03:00 | 117.58 | 101.02
2017-07-19 03:30 | 117.62 | 101.54
2017-07-19 04:00 | 121.67 | 106.29
2017-07-19 04:30 | 116.46 | 99.82
2017-07-19 05:00 | 114.89 | 98.6
2017-07-19 05:30 | 118.38 | 102.31
2017-07-19 06:00 | 120.03 | 106.26
2017-07-19 06:30 | 106.76 | 87.7
2017-07-19 07:00 | 106.84 | 88.45
2017-07-19 07:30 | 110.21 | 94.25
2017-07-19 08:00 | 110.73 | 96.13
2017-07-19 08:30 | 102.31 | 85.84
2017-07-19 09:00 | 106.05 | 88.95
2017-07-19 09:30 | 104.15 | 86.6
2017-07-19 10:00 | 103.28 | 84.11
2017-07-19 10:30 | 106.58 | 88.34
2017-07-19 11:00 | 107.49 | 89.23
2017-07-19 11:30 | 110.76 | 92.25
2017-07-19 12:00 | 113.68 | 95.57
2017-07-19 12:30 | 112.36 | 94.45
2017-07-19 13:00 | 120.4 | 104.48
2017-07-19 13:30 | 122.23 | 106.23
2017-07-19 14:00 | 116.34 | 100.55
2017-07-19 14:30 | 110.57 | 93.19
2017-07-19 15:00 | 105.91 | 87.9
2017-07-19 15:30 | 109.11 | 92.73
2017-07-19 16:00 | 105.57 | 87.66
2017-07-19 16:30 | 111.21 | 94.51
2017-07-19 17:00 | 115.41 | 101.2
2017-07-19 17:30 | 115.03 | 99.32
2017-07-19 18:00 | 115.84 | 100.24
2017-07-19 18:30 | 108.9 | 92.63
2017-07-19 19:00 | 111.65 | 95.78
2017-07-19 19:30 | 117.67 | 103.06
2017-07-19 20:00 | 121.68 | 107.48
2017-07-19 20:30 | 127.15 | 113.6
2017-07-19 21:00 | 122.13 | 106.96
2017-07-19 21:30 | 118.67 | 102.7
2017-07-19 22:00 | 124.88 | 110.75
2017-07-19 22:30 | 120.37 | 104.43
2017-07-19 23:00 | 119.48 | 102.87
2017-07-19 23:30 | 119.59 | 103.38
2017-07-20 | 127.1 | 112.42
2017-07-20 00:30 | 121.51 | 104.28
2017-07-20 01:00 | 120.46 | 102.64
2017-07-20 01:30 | 124.57 | 107.51
2017-07-20 02:00 | 124.05 | 106.23
2017-07-20 02:30 | 125.28 | 109.09
2017-07-20 03:00 | 121.47 | 103.37
2017-07-20 03:30 | 114.64 | 94.63
2017-07-20 04:00 | 116.31 | 96.46
2017-07-20 04:30 | 116.38 | 97.77
2017-07-20 05:00 | 116.81 | 97.84
2017-07-20 05:30 | 119 | 100.18
2017-07-20 06:00 | 112.68 | 92.41
2017-07-20 06:30 | 109.31 | 87.53
2017-07-20 07:00 | 101.84 | 79.81
2017-07-20 07:30 | 113.35 | 96.68
2017-07-20 08:00 | 110.59 | 94.63
2017-07-20 08:30 | 113.96 | 98.47
2017-07-20 09:00 | 112.67 | 96.61
2017-07-20 09:30 | 106.79 | 88.25
2017-07-20 10:00 | 101.77 | 81.72
2017-07-20 10:30 | 102.93 | 83.16
2017-07-20 11:00 | 111.13 | 92.41
2017-07-20 11:30 | 105.89 | 84.97
2017-07-20 12:00 | 111.62 | 93.33
2017-07-20 12:30 | 114.94 | 97.14
2017-07-20 13:00 | 105.88 | 84.89
2017-07-20 13:30 | 107.23 | 88.06
2017-07-20 14:00 | 102.92 | 83.58
2017-07-20 14:30 | 101.42 | 80.7
2017-07-20 15:00 | 106.26 | 88.3
2017-07-20 15:30 | 107.63 | 89.47
2017-07-20 16:00 | 105.13 | 85.46
2017-07-20 16:30 | 112.38 | 95.7
2017-07-20 17:00 | 111.2 | 94.82
2017-07-20 17:30 | 116.45 | 100.34
2017-07-20 18:00 | 120.13 | 105.01
2017-07-20 18:30 | 109.66 | 91.19
2017-07-20 19:00 | 118.14 | 103.4
2017-07-20 19:30 | 117.04 | 102.48
2017-07-20 20:00 | 118.29 | 104.74
2017-07-20 20:30 | 121.19 | 107.32
2017-07-20 21:00 | 122.58 | 109.25
2017-07-20 21:30 | 117.02 | 101.89
2017-07-20 22:00 | 119.37 | 104.61
2017-07-20 22:30 | 118.76 | 103.12
2017-07-20 23:00 | 120.73 | 105.83
2017-07-20 23:30 | 118.81 | 103.18
2017-07-21 | 122.84 | 105.91
2017-07-21 00:30 | 127 | 110.21
2017-07-21 01:00 | 124.26 | 106.75
2017-07-21 01:30 | 127.38 | 109.89
2017-07-21 02:00 | 125.78 | 107.16
2017-07-21 02:30 | 123.48 | 106.4
2017-07-21 03:00 | 120.63 | 103.11
2017-07-21 03:30 | 122.18 | 104.18
2017-07-21 04:00 | 117.39 | 99.6
2017-07-21 04:30 | 118.87 | 101.02
2017-07-21 05:00 | 124.63 | 108.91
2017-07-21 05:30 | 127.68 | 112.62
2017-07-21 06:00 | 131.47 | 117.82
2017-07-21 06:30 | 123.16 | 106.93
2017-07-21 07:00 | 123.97 | 108.88
2017-07-21 07:30 | 127.85 | 113.75
2017-07-21 08:00 | 131.32 | 117.75
2017-07-21 08:30 | 118.78 | 100.99
2017-07-21 09:00 | 111.33 | 91.82
2017-07-21 09:30 | 119.84 | 101.8
2017-07-21 10:00 | 117.74 | 98.64
2017-07-21 10:30 | 117.92 | 100.01
2017-07-21 11:00 | 115.71 | 95.87
2017-07-21 11:30 | 109.51 | 86.47
2017-07-21 12:00 | 114.28 | 93.92
2017-07-21 12:30 | 116.49 | 96.89
2017-07-21 13:00 | 115.9 | 95.38
2017-07-21 13:30 | 112.91 | 93.66
2017-07-21 14:00 | 110.83 | 90.81
2017-07-21 14:30 | 110.95 | 90.65
2017-07-21 15:00 | 110.26 | 92.6
2017-07-21 15:30 | 110.91 | 93.35
2017-07-21 16:00 | 114.28 | 96.25
2017-07-21 16:30 | 114.16 | 96.58
2017-07-21 17:00 | 114.67 | 97.21
2017-07-21 17:30 | 115.19 | 97.75
2017-07-21 18:00 | 119.08 | 103.36
2017-07-21 18:30 | 114.28 | 96.31
2017-07-21 19:00 | 116.11 | 100.84
2017-07-21 19:30 | 118.52 | 104.08
2017-07-21 20:00 | 118.5 | 103.38
2017-07-21 20:30 | 112.23 | 96.78
2017-07-21 21:00 | 117.04 | 101.77
2017-07-21 21:30 | 127.13 | 112.72
2017-07-21 22:00 | 122.82 | 108.1
2017-07-21 22:30 | 125.53 | 112.57
2017-07-21 23:00 | 119.41 | 104.36
2017-07-21 23:30 | 118.54 | 102.93
2017-07-22 | 123.4 | 108.25
2017-07-22 00:30 | 128.85 | 115.48
2017-07-22 01:00 | 122.41 | 107.76
2017-07-22 01:30 | 120.53 | 103.67
2017-07-22 02:00 | 124.58 | 109.44
2017-07-22 02:30 | 119.12 | 102.73
2017-07-22 03:00 | 118.58 | 102.12
2017-07-22 03:30 | 119.92 | 103.26
2017-07-22 04:00 | 122.3 | 105.29
2017-07-22 04:30 | 122.43 | 106.91
2017-07-22 05:00 | 117.13 | 101.7
2017-07-22 05:30 | 116.65 | 100.43
2017-07-22 06:00 | 120.64 | 104.57
2017-07-22 06:30 | 116.28 | 98.33
2017-07-22 07:00 | 113.58 | 95.91
2017-07-22 07:30 | 116.03 | 99.64
2017-07-22 08:00 | 116.43 | 99.42
2017-07-22 08:30 | 120.44 | 104.78
2017-07-22 09:00 | 117.79 | 100.36
2017-07-22 09:30 | 116.73 | 99.62
2017-07-22 10:00 | 120.24 | 104.39
2017-07-22 10:30 | 117.95 | 101.17
2017-07-22 11:00 | 115.54 | 99.37
2017-07-22 11:30 | 120.94 | 104.72
2017-07-22 12:00 | 116.86 | 100.81
2017-07-22 12:30 | 115.82 | 99.06
2017-07-22 13:00 | 114.09 | 96.79
2017-07-22 13:30 | 110.23 | 94.4
2017-07-22 14:00 | 111.59 | 95.98
2017-07-22 14:30 | 119.82 | 105
2017-07-22 15:00 | 119.12 | 103.16
2017-07-22 15:30 | 128.32 | 114.1
2017-07-22 16:00 | 123.17 | 107.77
2017-07-22 16:30 | 125.66 | 112.46
2017-07-22 17:00 | 128.56 | 114.48
2017-07-22 17:30 | 126.46 | 112.95
2017-07-22 18:00 | 127.61 | 114.21
2017-07-22 18:30 | 122.36 | 107.35
2017-07-22 19:00 | 129.56 | 117.02
2017-07-22 19:30 | 130.59 | 118.46
2017-07-22 20:00 | 131.13 | 118.79
2017-07-22 20:30 | 117.74 | 103.42
2017-07-22 21:00 | 127.29 | 114.21
2017-07-22 21:30 | 125.26 | 111.55
2017-07-22 22:00 | 130.4 | 118.32
2017-07-22 22:30 | 132.06 | 120.59
2017-07-22 23:00 | 121.93 | 108.53
2017-07-22 23:30 | 123.94 | 110.82
2017-07-23 | 121.59 | 106.15
2017-07-23 00:30 | 121.13 | 106.6
2017-07-23 01:00 | 125.37 | 111.94
2017-07-23 01:30 | 118.27 | 102.68
2017-07-23 02:00 | 119.58 | 105.31
2017-07-23 02:30 | 120.17 | 105.73
2017-07-23 03:00 | 124.11 | 111.09
2017-07-23 03:30 | 118.85 | 104.83
2017-07-23 04:00 | 120.76 | 107.68
2017-07-23 04:30 | 113.53 | 97.82
2017-07-23 05:00 | 115.88 | 101.93
2017-07-23 05:30 | 120.08 | 107.28
2017-07-23 06:00 | 120.67 | 107.74
2017-07-23 06:30 | 110.97 | 93.9
2017-07-23 07:00 | 117.02 | 102.31
2017-07-23 07:30 | 121.83 | 107.38
2017-07-23 08:00 | 116.15 | 101.09
2017-07-23 08:30 | 114.5 | 100.17
2017-07-23 09:00 | 120.45 | 106.47
2017-07-23 09:30 | 114.64 | 100.22
2017-07-23 10:00 | 119.6 | 106.54
2017-07-23 10:30 | 121.31 | 108.48
2017-07-23 11:00 | 116.01 | 101.77
2017-07-23 11:30 | 118.69 | 104.16
2017-07-23 12:00 | 117.46 | 102.85
2017-07-23 12:30 | 113.45 | 99.7
2017-07-23 13:00 | 111.26 | 96.79
2017-07-23 13:30 | 112.84 | 97.27
2017-07-23 14:00 | 112.36 | 96.93
2017-07-23 14:30 | 115.91 | 100.08
2017-07-23 15:00 | 111.62 | 94.25
2017-07-23 15:30 | 113 | 97.02
2017-07-23 16:00 | 108.15 | 91.96
2017-07-23 16:30 | 108.86 | 93.78
2017-07-23 17:00 | 112.9 | 99.16
2017-07-23 17:30 | 115.85 | 102.62
2017-07-23 18:00 | 117.75 | 105.08
2017-07-23 18:30 | 114.18 | 100.82
2017-07-23 19:00 | 115.43 | 102.36
2017-07-23 19:30 | 117.95 | 105.09
2017-07-23 20:00 | 116.92 | 105.03
2017-07-23 20:30 | 119.58 | 107.89
2017-07-23 21:00 | 116.95 | 103.9
2017-07-23 21:30 | 120.85 | 107.72
2017-07-23 22:00 | 121.55 | 108.95
2017-07-23 22:30 | 117.54 | 102.94
2017-07-23 23:00 | 112.71 | 97.58
2017-07-23 23:30 | 113.28 | 98.85
2017-07-24 | 121.45 | 108.16
2017-07-24 00:30 | 121.25 | 107.37
2017-07-24 01:00 | 121.11 | 107.05
2017-07-24 01:30 | 122.44 | 108.75
2017-07-24 02:00 | 122.51 | 109.12
2017-07-24 02:30 | 127.75 | 116.21
2017-07-24 03:00 | 119.91 | 107.03
2017-07-24 03:30 | 114.52 | 100.83
2017-07-24 04:00 | 121.2 | 107.92
2017-07-24 04:30 | 124.54 | 111.96
2017-07-24 05:00 | 126.21 | 114.75
2017-07-24 05:30 | 119.98 | 107.28
2017-07-24 06:00 | 122.3 | 109.18
2017-07-24 06:30 | 113.88 | 98.11
2017-07-24 07:00 | 121.11 | 107.61
2017-07-24 07:30 | 125.91 | 114.1
2017-07-24 08:00 | 116.9 | 103.8
2017-07-24 08:30 | 123.02 | 111.09
2017-07-24 09:00 | 116.72 | 102.16
2017-07-24 09:30 | 124.43 | 111.22
2017-07-24 10:00 | 116.96 | 102.74
2017-07-24 10:30 | 120.82 | 105.47
2017-07-24 11:00 | 118.21 | 102.82
2017-07-24 11:30 | 114.75 | 96.54
2017-07-24 12:00 | 115.46 | 97.91
2017-07-24 12:30 | 117.94 | 102.21
2017-07-24 13:00 | 121.64 | 107.98
2017-07-24 13:30 | 121.16 | 106.35
2017-07-24 14:00 | 122.72 | 108.45
2017-07-24 14:30 | 121.98 | 107.18
2017-07-24 15:00 | 126.18 | 112.04
2017-07-24 15:30 | 117.09 | 99.97
2017-07-24 16:00 | 119.63 | 103.76
2017-07-24 16:30 | 115.67 | 99.26
2017-07-24 17:00 | 118.02 | 102.23
2017-07-24 17:30 | 123.21 | 109.71
2017-07-24 18:00 | 121.09 | 107.23
2017-07-24 18:30 | 115.88 | 100.29
2017-07-24 19:00 | 117.71 | 101.78
2017-07-24 19:30 | 119.74 | 105.39
2017-07-24 20:00 | 123.16 | 108.88
2017-07-24 20:30 | 123.68 | 110.42
2017-07-24 21:00 | 115.82 | 100.06
2017-07-24 21:30 | 124.22 | 109.62
2017-07-24 22:00 | 123.99 | 108.16
2017-07-24 22:30 | 124.33 | 108.74
2017-07-24 23:00 | 122.34 | 106.49
2017-07-24 23:30 | 117.08 | 99.71
2017-07-25 | 116.2 | 98.5
2017-07-25 00:30 | 111.93 | 91.72
2017-07-25 01:00 | 113.87 | 94.03
2017-07-25 01:30 | 117.49 | 98.77
2017-07-25 02:00 | 113.17 | 93.47
2017-07-25 02:30 | 115.96 | 97.95
2017-07-25 03:00 | 117.69 | 99.75
2017-07-25 03:30 | 119.33 | 101.82
2017-07-25 04:00 | 118.19 | 99.75
2017-07-25 04:30 | 119.27 | 101.23
2017-07-25 05:00 | 116.75 | 97.98
2017-07-25 05:30 | 121.44 | 104.65
2017-07-25 06:00 | 120.09 | 103.06
2017-07-25 06:30 | 114.79 | 94.22
2017-07-25 07:00 | 127.92 | 112.93
2017-07-25 07:30 | 124.17 | 108.68
2017-07-25 08:00 | 115.97 | 98.27
2017-07-25 08:30 | 117.66 | 99.79
2017-07-25 09:00 | 114.63 | 95.05
2017-07-25 09:30 | 110.39 | 88.13
2017-07-25 10:00 | 113.68 | 92.44
2017-07-25 10:30 | 113.15 | 91.14
2017-07-25 11:00 | 117.76 | 97.66
2017-07-25 11:30 | 111.84 | 89.7
2017-07-25 12:00 | 115.96 | 96.18
2017-07-25 12:30 | 111.9 | 90.09
2017-07-25 13:00 | 115.98 | 97.19
2017-07-25 13:30 | 114.21 | 95.89
2017-07-25 14:00 | 112.8 | 93.81
2017-07-25 14:30 | 114.16 | 95.53
2017-07-25 15:00 | 114.48 | 95.98
2017-07-25 15:30 | 109.25 | 89.71
2017-07-25 16:00 | 108.43 | 88.1
2017-07-25 16:30 | 115.63 | 96.96
2017-07-25 17:00 | 118.26 | 101.4
2017-07-25 17:30 | 118.67 | 102.96
2017-07-25 18:00 | 112.25 | 95.04
2017-07-25 18:30 | 109.64 | 91.86
2017-07-25 19:00 | 120.23 | 107.31
2017-07-25 19:30 | 118.87 | 105.59
2017-07-25 20:00 | 117.63 | 103.68
2017-07-25 20:30 | 125.34 | 111.96
2017-07-25 21:00 | 127.8 | 114.81
2017-07-25 21:30 | 120.32 | 105.52
2017-07-25 22:00 | 120.42 | 105.47
2017-07-25 22:30 | 121.48 | 107.12
2017-07-25 23:00 | 118.57 | 104.12
2017-07-25 23:30 | 120.19 | 105.37
2017-07-26 | 119.44 | 104.59
2017-07-26 00:30 | 117.46 | 101.5
2017-07-26 01:00 | 118.73 | 102.59
2017-07-26 01:30 | 109.52 | 90.04
2017-07-26 02:00 | 111.88 | 93.93
2017-07-26 02:30 | 117.59 | 101.61
2017-07-26 03:00 | 113.87 | 95.7
2017-07-26 03:30 | 106.9 | 87.01
2017-07-26 04:00 | 113.24 | 95.05
2017-07-26 04:30 | 115.59 | 98.01
2017-07-26 05:00 | 116.25 | 99.58
2017-07-26 05:30 | 117.14 | 100.37
2017-07-26 06:00 | 114 | 96.22
2017-07-26 06:30 | 108.9 | 88.78
2017-07-26 07:00 | 112.2 | 94.63
2017-07-26 07:30 | 114.94 | 100.09
2017-07-26 08:00 | 113.66 | 97.09
2017-07-26 08:30 | 116.35 | 100.58
2017-07-26 09:00 | 111.92 | 90.86
2017-07-26 09:30 | 113.02 | 92.88
2017-07-26 10:00 | 108.39 | 86.96
2017-07-26 10:30 | 108.85 | 88.88
2017-07-26 11:00 | 109.19 | 87.3
2017-07-26 11:30 | 109.28 | 89.25
2017-07-26 12:00 | 101.47 | 76.49
2017-07-26 12:30 | 97.66 | 69.75
2017-07-26 13:00 | 104.26 | 81.64
2017-07-26 13:30 | 103.53 | 81.65
2017-07-26 14:00 | 106.32 | 85.66
2017-07-26 14:30 | 103.97 | 81.62
2017-07-26 15:00 | 110.36 | 88.3
2017-07-26 15:30 | 111.76 | 92.31
2017-07-26 16:00 | 115.03 | 97.29
2017-07-26 16:30 | 109.33 | 89.37
2017-07-26 17:00 | 109.44 | 88.94
2017-07-26 17:30 | 105.68 | 84.88
2017-07-26 18:00 | 107.75 | 90.21
2017-07-26 18:30 | 100.59 | 80.49
2017-07-26 19:00 | 112.44 | 96.54
2017-07-26 19:30 | 112.26 | 98.29
2017-07-26 20:00 | 112.37 | 98.46
2017-07-26 20:30 | 118.12 | 105.13
2017-07-26 21:00 | 119.98 | 105.56
2017-07-26 21:30 | 117.1 | 100.81
2017-07-26 22:00 | 114.65 | 99.27
2017-07-26 22:30 | 114.31 | 98.36
2017-07-26 23:00 | 114.24 | 97.63
2017-07-26 23:30 | 107.17 | 87.48
2017-07-27 | 111.41 | 94.15
2017-07-27 00:30 | 114.83 | 97.95
2017-07-27 01:00 | 111.32 | 91.7
2017-07-27 01:30 | 111.45 | 93.72
2017-07-27 02:00 | 114.03 | 96.8
2017-07-27 02:30 | 109.29 | 89.74
2017-07-27 03:00 | 111.03 | 93.46
2017-07-27 03:30 | 103.1 | 83.67
2017-07-27 04:00 | 109.13 | 92.7
2017-07-27 04:30 | 112.61 | 98.2
2017-07-27 05:00 | 113.28 | 96.78
2017-07-27 05:30 | 115.52 | 99.81
2017-07-27 06:00 | 110.56 | 93.97
2017-07-27 06:30 | 107.54 | 87.9
2017-07-27 07:00 | 113.68 | 96.57
2017-07-27 07:30 | 109.43 | 91.09
2017-07-27 08:00 | 115.4 | 98.36
2017-07-27 08:30 | 114.64 | 95.55
2017-07-27 09:00 | 109.81 | 89.6
2017-07-27 09:30 | 109.35 | 88.6
2017-07-27 10:00 | 108.68 | 88.88
2017-07-27 10:30 | 111.9 | 92.73
2017-07-27 11:00 | 112.73 | 94.29
2017-07-27 11:30 | 109.77 | 88.43
2017-07-27 12:00 | 109.99 | 87.36
2017-07-27 12:30 | 112.61 | 89.54
2017-07-27 13:00 | 114.96 | 91.86
2017-07-27 13:30 | 109.93 | 85.46
2017-07-27 14:00 | 108.95 | 86.07
2017-07-27 14:30 | 112.33 | 91.3
2017-07-27 15:00 | 110.37 | 87.53
2017-07-27 15:30 | 113.55 | 93.64
2017-07-27 16:00 | 113.06 | 92.71
2017-07-27 16:30 | 120.77 | 102.59
2017-07-27 17:00 | 114.06 | 95.28
2017-07-27 17:30 | 119.74 | 101.9
2017-07-27 18:00 | 118.49 | 103.02
2017-07-27 18:30 | 114.34 | 96.02
2017-07-27 19:00 | 114.44 | 97.39
2017-07-27 19:30 | 115.17 | 98.94
2017-07-27 20:00 | 113.18 | 96.76
2017-07-27 20:30 | 115.9 | 98.82
2017-07-27 21:00 | 115.05 | 97.73
2017-07-27 21:30 | 112.77 | 95.67
2017-07-27 22:00 | 114.71 | 98.32
2017-07-27 22:30 | 119.03 | 103.61
2017-07-27 23:00 | 114.07 | 97.42
2017-07-27 23:30 | 113 | 96.27
2017-07-28 | 117.18 | 100.13
2017-07-28 00:30 | 119.2 | 101.75
2017-07-28 01:00 | 124.14 | 109.37
2017-07-28 01:30 | 120.95 | 104.77
2017-07-28 02:00 | 122.68 | 107.14
2017-07-28 02:30 | 126.48 | 112.4
2017-07-28 03:00 | 121.74 | 105.81
2017-07-28 03:30 | 120.45 | 105.08
2017-07-28 04:00 | 120.51 | 104.98
2017-07-28 04:30 | 123.44 | 109.64
2017-07-28 05:00 | 123.78 | 109.02
2017-07-28 05:30 | 124.54 | 110.46
2017-07-28 06:00 | 126.74 | 113.31
2017-07-28 06:30 | 119.96 | 102.93
2017-07-28 07:00 | 124.12 | 110.11
2017-07-28 07:30 | 130.82 | 119.06
2017-07-28 08:00 | 123.89 | 111.35
2017-07-28 08:30 | 118.58 | 104.19
2017-07-28 09:00 | 123.68 | 110.5
2017-07-28 09:30 | 122.95 | 109.21
2017-07-28 10:00 | 112.83 | 97.05
2017-07-28 10:30 | 117.71 | 101.68
2017-07-28 11:00 | 115.67 | 99.15
2017-07-28 11:30 | 115.39 | 99.16
2017-07-28 12:00 | 119.42 | 103.61
2017-07-28 12:30 | 118.13 | 102.87
2017-07-28 13:00 | 117.46 | 102.9
2017-07-28 13:30 | 110.12 | 92.66
2017-07-28 14:00 | 113.18 | 95.67
2017-07-28 14:30 | 113.45 | 96.69
2017-07-28 15:00 | 112.17 | 94.77
2017-07-28 15:30 | 109.4 | 91.75
2017-07-28 16:00 | 116.65 | 101.9
2017-07-28 16:30 | 117.71 | 102.49
2017-07-28 17:00 | 121.29 | 107.14
2017-07-28 17:30 | 117.5 | 102.33
2017-07-28 18:00 | 116.74 | 102.69
2017-07-28 18:30 | 120.69 | 105.49
2017-07-28 19:00 | 122.57 | 108.34
2017-07-28 19:30 | 122.09 | 108.24
2017-07-28 20:00 | 127.72 | 115.02
2017-07-28 20:30 | 127.02 | 114.16
2017-07-28 21:00 | 133.85 | 121.71
2017-07-28 21:30 | 128.99 | 114.45
2017-07-28 22:00 | 123.61 | 108.43
2017-07-28 22:30 | 119.76 | 105.39
2017-07-28 23:00 | 122.72 | 107.64
2017-07-28 23:30 | 124.7 | 110.45
2017-07-29 | 122.65 | 107.61
2017-07-29 00:30 | 125.69 | 111.5
2017-07-29 01:00 | 126.12 | 112.14
2017-07-29 01:30 | 123.49 | 107.39
2017-07-29 02:00 | 120.93 | 105.24
2017-07-29 02:30 | 122.56 | 107.28
2017-07-29 03:00 | 116.7 | 100.31
2017-07-29 03:30 | 116.6 | 100.48
2017-07-29 04:00 | 118.21 | 103.79
2017-07-29 04:30 | 122.59 | 108.95
2017-07-29 05:00 | 124.69 | 111.8
2017-07-29 05:30 | 117.35 | 102.54
2017-07-29 06:00 | 115.24 | 99.95
2017-07-29 06:30 | 111.85 | 93.39
2017-07-29 07:00 | 108.4 | 91.11
2017-07-29 07:30 | 116.91 | 103.07
2017-07-29 08:00 | 118.54 | 104.27
2017-07-29 08:30 | 113.65 | 97.45
2017-07-29 09:00 | 115.75 | 100.69
2017-07-29 09:30 | 118.51 | 104.38
2017-07-29 10:00 | 120.25 | 106.89
2017-07-29 10:30 | 117.11 | 102.7
2017-07-29 11:00 | 124.99 | 112.08
2017-07-29 11:30 | 121.36 | 107.16
2017-07-29 12:00 | 124.2 | 110.16
2017-07-29 12:30 | 120.26 | 107.04
2017-07-29 13:00 | 117.11 | 101.67
2017-07-29 13:30 | 113.73 | 98.28
2017-07-29 14:00 | 110.58 | 93.94
2017-07-29 14:30 | 109.29 | 92.64
2017-07-29 15:00 | 107.71 | 90.25
2017-07-29 15:30 | 120.39 | 105.89
2017-07-29 16:00 | 115.33 | 100.3
2017-07-29 16:30 | 118.03 | 104.11
2017-07-29 17:00 | 118.68 | 104.85
2017-07-29 17:30 | 124.13 | 111.58
2017-07-29 18:00 | 125.06 | 113.96
2017-07-29 18:30 | 110.31 | 95.21
2017-07-29 19:00 | 118.57 | 105.77
2017-07-29 19:30 | 120.69 | 108.45
2017-07-29 20:00 | 120.84 | 108.61
2017-07-29 20:30 | 123.46 | 110.64
2017-07-29 21:00 | 118.55 | 104.85
2017-07-29 21:30 | 122.37 | 108.52
2017-07-29 22:00 | 125.12 | 111.17
2017-07-29 22:30 | 130.54 | 116.97
2017-07-29 23:00 | 116.74 | 99.9
2017-07-29 23:30 | 120.55 | 104.31
2017-07-30 | 130.45 | 117.35
2017-07-30 00:30 | 128.47 | 115.62
2017-07-30 01:00 | 126.81 | 113.73
2017-07-30 01:30 | 118.24 | 103.19
2017-07-30 02:00 | 123.71 | 109.27
2017-07-30 02:30 | 127.84 | 115.27
2017-07-30 03:00 | 123.67 | 110.56
2017-07-30 03:30 | 121.41 | 107.4
2017-07-30 04:00 | 123.94 | 109.25
2017-07-30 04:30 | 120.06 | 105.09
2017-07-30 05:00 | 119.27 | 103.37
2017-07-30 05:30 | 116.31 | 100.55
2017-07-30 06:00 | 120.22 | 104.86
2017-07-30 06:30 | 117.45 | 100.89
2017-07-30 07:00 | 115.13 | 98.22
2017-07-30 07:30 | 119.52 | 103.77
2017-07-30 08:00 | 122.74 | 108.61
2017-07-30 08:30 | 126.49 | 113.51
2017-07-30 09:00 | 116.49 | 100.57
2017-07-30 09:30 | 111.51 | 95.15
2017-07-30 10:00 | 114.03 | 97.91
2017-07-30 10:30 | 112.17 | 96.18
2017-07-30 11:00 | 112.2 | 96.15
2017-07-30 11:30 | 116.38 | 100.33
2017-07-30 12:00 | 115.87 | 99.5
2017-07-30 12:30 | 112.34 | 95.43
2017-07-30 13:00 | 116.14 | 100.29
2017-07-30 13:30 | 115.32 | 99.17
2017-07-30 14:00 | 117.28 | 102.63
2017-07-30 14:30 | 118.42 | 104.41
2017-07-30 15:00 | 120.08 | 105.5
2017-07-30 15:30 | 114.57 | 98.68
2017-07-30 16:00 | 112.2 | 96.12
2017-07-30 16:30 | 122.06 | 107.23
2017-07-30 17:00 | 122.11 | 108.24
2017-07-30 17:30 | 120.95 | 107.55
2017-07-30 18:00 | 125.76 | 112.87
2017-07-30 18:30 | 112.77 | 97.86
2017-07-30 19:00 | 118.31 | 104.62
2017-07-30 19:30 | 119.16 | 106.49
2017-07-30 20:00 | 122.47 | 109.61
2017-07-30 20:30 | 124.87 | 110.72
2017-07-30 21:00 | 116.07 | 99.7
2017-07-30 21:30 | 120.81 | 106.07
2017-07-30 22:00 | 120.74 | 104.9
2017-07-30 22:30 | 121.6 | 106.52
2017-07-30 23:00 | 121.01 | 106.37
2017-07-30 23:30 | 120.3 | 104.8
2017-07-31 | 126.8 | 112.66
2017-07-31 00:30 | 132.1 | 118.9
2017-07-31 01:00 | 134.35 | 121.4
2017-07-31 01:30 | 131.7 | 117.6
2017-07-31 02:00 | 126.63 | 112.05
2017-07-31 02:30 | 130.16 | 115.91
2017-07-31 03:00 | 122.2 | 105.12
2017-07-31 03:30 | 118.98 | 100.98
2017-07-31 04:00 | 121.74 | 105.05
2017-07-31 04:30 | 124.4 | 107.61
2017-07-31 05:00 | 120.65 | 105.35
2017-07-31 05:30 | 122.26 | 107.72
2017-07-31 06:00 | 126.9 | 112.99
2017-07-31 06:30 | 122.69 | 106.73
2017-07-31 07:00 | 120.9 | 103.53
2017-07-31 07:30 | 123.62 | 108.81
2017-07-31 08:00 | 122.9 | 107.69
2017-07-31 08:30 | 118.56 | 101.97
2017-07-31 09:00 | 115.93 | 98.82
2017-07-31 09:30 | 117.36 | 101.05
2017-07-31 10:00 | 117.23 | 100.37
2017-07-31 10:30 | 119.31 | 101.92
2017-07-31 11:00 | 121.7 | 104.94
2017-07-31 11:30 | 123.74 | 105.76
2017-07-31 12:00 | 121.61 | 102.67
2017-07-31 12:30 | 121.87 | 105.25
2017-07-31 13:00 | 119.04 | 100.96
2017-07-31 13:30 | 117.21 | 98.98
2017-07-31 14:00 | 119.46 | 99.79
2017-07-31 14:30 | 123.86 | 104.16
2017-07-31 15:00 | 124.23 | 105.56
2017-07-31 15:30 | 122.09 | 103.13
2017-07-31 16:00 | 130.38 | 114.48
2017-07-31 16:30 | 128.61 | 112.52
2017-07-31 17:00 | 123.47 | 106.27
2017-07-31 17:30 | 124.42 | 106.32
2017-07-31 18:00 | 126.58 | 109.73
2017-07-31 18:30 | 119.67 | 100.81
2017-07-31 19:00 | 124.65 | 107.56
2017-07-31 19:30 | 128.97 | 112.91
2017-07-31 20:00 | 125.65 | 111.03
2017-07-31 20:30 | 127.01 | 112.5
2017-07-31 21:00 | 126.47 | 109.94
2017-07-31 21:30 | 130.95 | 116.56
2017-07-31 22:00 | 130.43 | 114.74
2017-07-31 22:30 | 130.65 | 115.35
2017-07-31 23:00 | 129.88 | 113.41
2017-07-31 23:30 | 131.57 | 115.24
2017-08-01 | 132.75 | 116.79
2017-08-01 00:30 | 127.93 | 111.36
2017-08-01 01:00 | 127.34 | 110.39
2017-08-01 01:30 | 125 | 106.13
2017-08-01 02:00 | 123.94 | 106.57
2017-08-01 02:30 | 129.45 | 114.58
2017-08-01 03:00 | 123.22 | 107.59
2017-08-01 03:30 | 134.24 | 121.24
2017-08-01 04:00 | 125.46 | 110.06
2017-08-01 04:30 | 125.76 | 110.71
2017-08-01 05:00 | 121.75 | 107.03
2017-08-01 05:30 | 122.1 | 106.48
2017-08-01 06:00 | 128.14 | 113.81
2017-08-01 06:30 | 114.73 | 95.34
2017-08-01 07:00 | 126.7 | 109.47
2017-08-01 07:30 | 127.14 | 111.47
2017-08-01 08:00 | 118.14 | 100.31
2017-08-01 08:30 | 122.31 | 105.19
2017-08-01 09:00 | 118.33 | 100.72
2017-08-01 09:30 | 120.88 | 102.07
2017-08-01 10:00 | 123.06 | 103.52
2017-08-01 10:30 | 123.19 | 103.5
2017-08-01 11:00 | 118.54 | 96.47
2017-08-01 11:30 | 117.3 | 96.27
2017-08-01 12:00 | 109.08 | 86.14
2017-08-01 12:30 | 113.87 | 93.85
2017-08-01 13:00 | 115.22 | 94.43
2017-08-01 13:30 | 120.25 | 102.02
2017-08-01 14:00 | 118.94 | 99.98
2017-08-01 14:30 | 118.12 | 99.17
2017-08-01 15:00 | 118.1 | 98.52
2017-08-01 15:30 | 119.88 | 100.65
2017-08-01 16:00 | 119.58 | 100.29
2017-08-01 16:30 | 120.6 | 102.14
2017-08-01 17:00 | 124.53 | 108.09
2017-08-01 17:30 | 122.52 | 107.18
2017-08-01 18:00 | 126.67 | 111.8
2017-08-01 18:30 | 116.62 | 99.73
2017-08-01 19:00 | 122.95 | 108.22
2017-08-01 19:30 | 126.12 | 112.17
2017-08-01 20:00 | 126.7 | 112.45
2017-08-01 20:30 | 128.41 | 114.69
2017-08-01 21:00 | 128.54 | 114.73
2017-08-01 21:30 | 126 | 111.32
2017-08-01 22:00 | 127.38 | 112.99
2017-08-01 22:30 | 125.7 | 110.93
2017-08-01 23:00 | 125.12 | 109.72
2017-08-01 23:30 | 126.58 | 111.59
2017-08-02 | 123.23 | 108.02
2017-08-02 00:30 | 115.48 | 100.24
2017-08-02 01:00 | 115.66 | 101.17
2017-08-02 01:30 | 123.07 | 109.03
2017-08-02 02:00 | 121.04 | 106.92
2017-08-02 02:30 | 119.12 | 104.44
2017-08-02 03:00 | 115.41 | 99.53
2017-08-02 03:30 | 118.37 | 104.22
2017-08-02 04:00 | 119.25 | 105.09
2017-08-02 04:30 | 121.94 | 109.4
2017-08-02 05:00 | 117.32 | 104.02
2017-08-02 05:30 | 116.8 | 102.13
2017-08-02 06:00 | 117.17 | 102.26
2017-08-02 06:30 | 113.5 | 96.31
2017-08-02 07:00 | 117.21 | 101.77
2017-08-02 07:30 | 118.65 | 104.88
2017-08-02 08:00 | 113.67 | 99.32
2017-08-02 08:30 | 117.93 | 103.08
2017-08-02 09:00 | 114.62 | 98.14
2017-08-02 09:30 | 115.15 | 100.37
2017-08-02 10:00 | 110.13 | 93.88
2017-08-02 10:30 | 114.43 | 98.26
2017-08-02 11:00 | 111.39 | 97.69
2017-08-02 11:30 | 109.47 | 94.4
2017-08-02 12:00 | 113.87 | 97.75
2017-08-02 12:30 | 114.25 | 97.36
2017-08-02 13:00 | 124.6 | 108.72
2017-08-02 13:30 | 123.63 | 107.4
2017-08-02 14:00 | 121.47 | 104.75
2017-08-02 14:30 | 124.86 | 109.82
2017-08-02 15:00 | 122.16 | 106.65
2017-08-02 15:30 | 115.12 | 98.39
2017-08-02 16:00 | 116.72 | 101.86
2017-08-02 16:30 | 116.96 | 102.16
2017-08-02 17:00 | 127.66 | 114.13
2017-08-02 17:30 | 120.89 | 105.91
2017-08-02 18:00 | 128.69 | 114.17
2017-08-02 18:30 | 119.92 | 104.23
2017-08-02 19:00 | 122.39 | 108.42
2017-08-02 19:30 | 129.11 | 115.61
2017-08-02 20:00 | 131.57 | 117.54
2017-08-02 20:30 | 130.68 | 116.53
2017-08-02 21:00 | 125.64 | 110.86
2017-08-02 21:30 | 127.99 | 113.82
2017-08-02 22:00 | 122.85 | 108.76
2017-08-02 22:30 | 130.06 | 117.19
2017-08-02 23:00 | 118.62 | 103.64
2017-08-02 23:30 | 118.4 | 102.15
2017-08-03 | 114.27 | 97.79
2017-08-03 00:30 | 116.94 | 101.58
2017-08-03 01:00 | 116.86 | 102.44
2017-08-03 01:30 | 114.91 | 99.94
2017-08-03 02:00 | 116.41 | 100.5
2017-08-03 02:30 | 113.95 | 98.35
2017-08-03 03:00 | 114.83 | 99.15
2017-08-03 03:30 | 113.44 | 97.05
2017-08-03 04:00 | 120.27 | 103.35
2017-08-03 04:30 | 121.28 | 104.96
2017-08-03 05:00 | 117.48 | 102.54
2017-08-03 05:30 | 113.09 | 99.36
2017-08-03 06:00 | 113.37 | 99.37
2017-08-03 06:30 | 106.17 | 89.52
2017-08-03 07:00 | 102.48 | 85.29
2017-08-03 07:30 | 100.55 | 83.12
2017-08-03 08:00 | 95.79 | 76.33
2017-08-03 08:30 | 96.05 | 78.03
2017-08-03 09:00 | 99.15 | 81.68
2017-08-03 09:30 | 101.98 | 85.62
2017-08-03 10:00 | 102.88 | 87.09
2017-08-03 10:30 | 103.54 | 87.66
2017-08-03 11:00 | 105.05 | 88.93
2017-08-03 11:30 | 109.24 | 93.87
2017-08-03 12:00 | 108.16 | 92.09
2017-08-03 12:30 | 104.54 | 88.87
2017-08-03 13:00 | 112.24 | 97.99
2017-08-03 13:30 | 107.49 | 92.44
2017-08-03 14:00 | 104.41 | 88.61
2017-08-03 14:30 | 105.18 | 89.61
2017-08-03 15:00 | 103.89 | 87.61
2017-08-03 15:30 | 113.03 | 97.55
2017-08-03 16:00 | 114.83 | 99.77
2017-08-03 16:30 | 109.27 | 94.34
2017-08-03 17:00 | 113.46 | 99.12
2017-08-03 17:30 | 112.43 | 97.7
2017-08-03 18:00 | 115.24 | 101.3
2017-08-03 18:30 | 109.6 | 94.74
2017-08-03 19:00 | 108.1 | 93.07
2017-08-03 19:30 | 117.47 | 102.03
2017-08-03 20:00 | 115.94 | 101.32
2017-08-03 20:30 | 118.06 | 103.53
2017-08-03 21:00 | 116.46 | 101.05
2017-08-03 21:30 | 119.23 | 103.69
2017-08-03 22:00 | 121.09 | 105.79
2017-08-03 22:30 | 122.86 | 106.74
2017-08-03 23:00 | 120.34 | 103.93
2017-08-03 23:30 | 120.67 | 104.41
2017-08-04 | 120.15 | 104.23
2017-08-04 00:30 | 120.84 | 105.44
2017-08-04 01:00 | 118.6 | 103.02
2017-08-04 01:30 | 114.26 | 98.73
2017-08-04 02:00 | 118.65 | 103.2
2017-08-04 02:30 | 114.26 | 97.81
2017-08-04 03:00 | 109.69 | 92.63
2017-08-04 03:30 | 111.17 | 95.4
2017-08-04 04:00 | 114.06 | 97.66
2017-08-04 04:30 | 115.41 | 99.67
2017-08-04 05:00 | 118.76 | 103.82
2017-08-04 05:30 | 114.14 | 99.01
2017-08-04 06:00 | 116.16 | 101.27
2017-08-04 06:30 | 99.94 | 84.22
2017-08-04 07:00 | 100.57 | 84.88
2017-08-04 07:30 | 102.64 | 86.64
2017-08-04 08:00 | 98.52 | 81.35
2017-08-04 08:30 | 92.81 | 75.78
2017-08-04 09:00 | 97.22 | 81.63
2017-08-04 09:30 | 99.54 | 84.97
2017-08-04 10:00 | 100.86 | 87.23
2017-08-04 10:30 | 102.36 | 88.01
2017-08-04 11:00 | 104.47 | 89.97
2017-08-04 11:30 | 102.27 | 88.2
2017-08-04 12:00 | 111.78 | 97.98
2017-08-04 12:30 | 109.78 | 95.28
2017-08-04 13:00 | 103.02 | 87.69
2017-08-04 13:30 | 110.54 | 96.95
2017-08-04 14:00 | 112.8 | 99.39
2017-08-04 14:30 | 102.01 | 88.44
2017-08-04 15:00 | 103 | 89.07
2017-08-04 15:30 | 107.15 | 94.57
2017-08-04 16:00 | 103.31 | 89.63
2017-08-04 16:30 | 107.21 | 93.65
2017-08-04 17:00 | 99.59 | 86.07
2017-08-04 17:30 | 101.36 | 86.75
2017-08-04 18:00 | 108.53 | 95.44
2017-08-04 18:30 | 100.51 | 85.76
2017-08-04 19:00 | 99.38 | 85.41
2017-08-04 19:30 | 101.67 | 87.87
2017-08-04 20:00 | 104.56 | 90.39
2017-08-04 20:30 | 102.13 | 88.06
2017-08-04 21:00 | 106.04 | 92.6
2017-08-04 21:30 | 104.72 | 91.37
2017-08-04 22:00 | 108.76 | 95.92
2017-08-04 22:30 | 107.59 | 93.65
2017-08-04 23:00 | 108.22 | 94.25
2017-08-04 23:30 | 107.19 | 92.87
2017-08-05 | 109.66 | 95.54
2017-08-05 00:30 | 105.31 | 92.04
2017-08-05 01:00 | 104.95 | 91.6
2017-08-05 01:30 | 104.36 | 89.99
2017-08-05 02:00 | 108.82 | 94.54
2017-08-05 02:30 | 107.67 | 93.13
2017-08-05 03:00 | 107.37 | 92.57
2017-08-05 03:30 | 102.78 | 86.12
2017-08-05 04:00 | 104.98 | 89.46
2017-08-05 04:30 | 108.72 | 94.96
2017-08-05 05:00 | 111.22 | 97.65
2017-08-05 05:30 | 105.47 | 90.33
2017-08-05 06:00 | 105.93 | 91.3
2017-08-05 06:30 | 102.33 | 85.95
2017-08-05 07:00 | 102.64 | 87.2
2017-08-05 07:30 | 105.42 | 90.58
2017-08-05 08:00 | 101.71 | 86.4
2017-08-05 08:30 | 96.62 | 81.88
2017-08-05 09:00 | 98.98 | 84.05
2017-08-05 09:30 | 106.45 | 91.91
2017-08-05 10:00 | 101.18 | 87.05
2017-08-05 10:30 | 98.4 | 83.8
2017-08-05 11:00 | 94.9 | 78.68
2017-08-05 11:30 | 91.65 | 73.75
2017-08-05 12:00 | 96.42 | 79.4
2017-08-05 12:30 | 98.06 | 82.67
2017-08-05 13:00 | 98.15 | 81.86
2017-08-05 13:30 | 100.37 | 83.84
2017-08-05 14:00 | 106.62 | 91.87
2017-08-05 14:30 | 107.52 | 93.2
2017-08-05 15:00 | 103.72 | 89.17
2017-08-05 15:30 | 102.87 | 88.19
2017-08-05 16:00 | 101.6 | 87.08
2017-08-05 16:30 | 105.9 | 91.38
2017-08-05 17:00 | 108.14 | 93.79
2017-08-05 17:30 | 107.65 | 93.28
2017-08-05 18:00 | 113.54 | 100.28
2017-08-05 18:30 | 110.76 | 96.09
2017-08-05 19:00 | 108.69 | 95.16
2017-08-05 19:30 | 110.65 | 97.17
2017-08-05 20:00 | 105.98 | 90.7
2017-08-05 20:30 | 112.07 | 97.23
2017-08-05 21:00 | 109.72 | 94.65
2017-08-05 21:30 | 108.76 | 93.84
2017-08-05 22:00 | 108.21 | 93.89
2017-08-05 22:30 | 102.61 | 88.17
2017-08-05 23:00 | 104.23 | 90.12
2017-08-05 23:30 | 104.14 | 89
2017-08-06 | 101.08 | 84.76
2017-08-06 00:30 | 100.83 | 85.47
2017-08-06 01:00 | 103.76 | 88.87
2017-08-06 01:30 | 110.17 | 97
2017-08-06 02:00 | 113.18 | 99.31
2017-08-06 02:30 | 110.82 | 96.73
2017-08-06 03:00 | 109.47 | 94.97
2017-08-06 03:30 | 106.96 | 92.25
2017-08-06 04:00 | 105.08 | 89.55
2017-08-06 04:30 | 110.67 | 96.37
2017-08-06 05:00 | 109.31 | 94.61
2017-08-06 05:30 | 110.29 | 95.7
2017-08-06 06:00 | 113.96 | 99.91
2017-08-06 06:30 | 106.37 | 88.41
2017-08-06 07:00 | 115.59 | 100.41
2017-08-06 07:30 | 115.66 | 101.04
2017-08-06 08:00 | 114.43 | 100.23
2017-08-06 08:30 | 112.65 | 98.56
2017-08-06 09:00 | 114.7 | 99.84
2017-08-06 09:30 | 115.17 | 100.05
2017-08-06 10:00 | 117.01 | 101.94
2017-08-06 10:30 | 122.11 | 106.81
2017-08-06 11:00 | 116.53 | 101.05
2017-08-06 11:30 | 111.27 | 95.78
2017-08-06 12:00 | 118.16 | 102.05
2017-08-06 12:30 | 125.96 | 110.45
2017-08-06 13:00 | 115.01 | 99.39
2017-08-06 13:30 | 110.98 | 94.63
2017-08-06 14:00 | 109.26 | 92.74
2017-08-06 14:30 | 110.32 | 94.89
2017-08-06 15:00 | 112.2 | 97.25
2017-08-06 15:30 | 99.07 | 84.62
2017-08-06 16:00 | 99.34 | 86.3
2017-08-06 16:30 | 93.2 | 78.23
2017-08-06 17:00 | 93.93 | 79.32
2017-08-06 17:30 | 96.09 | 81.6
2017-08-06 18:00 | 100.86 | 87.74
2017-08-06 18:30 | 96.96 | 82.57
2017-08-06 19:00 | 101.24 | 87.77
2017-08-06 19:30 | 100.45 | 87.45
2017-08-06 20:00 | 109.48 | 96.41
2017-08-06 20:30 | 101.51 | 87.64
2017-08-06 21:00 | 110.84 | 97.04
2017-08-06 21:30 | 106.25 | 92.12
2017-08-06 22:00 | 107.48 | 93.14
2017-08-06 22:30 | 106.03 | 91.36
2017-08-06 23:00 | 104.72 | 89.43
2017-08-06 23:30 | 101.16 | 85.46
2017-08-07 | 106.15 | 92.44
2017-08-07 00:30 | 107.44 | 93.29
2017-08-07 01:00 | 113.31 | 99.35
2017-08-07 01:30 | 107.18 | 93.61
2017-08-07 02:00 | 105.44 | 91.83
2017-08-07 02:30 | 113.58 | 100.58
2017-08-07 03:00 | 116.05 | 103.13
2017-08-07 03:30 | 110.73 | 97.05
2017-08-07 04:00 | 108.08 | 94.33
2017-08-07 04:30 | 105.08 | 91.14
2017-08-07 05:00 | 105.86 | 92.29
2017-08-07 05:30 | 108.66 | 95.59
2017-08-07 06:00 | 105.5 | 91.93
2017-08-07 06:30 | 107.45 | 93.61
2017-08-07 07:00 | 107.2 | 95.18
2017-08-07 07:30 | 109.43 | 97.62
2017-08-07 08:00 | 108.87 | 96.81
2017-08-07 08:30 | 111.59 | 99.26
2017-08-07 09:00 | 108.03 | 94.89
2017-08-07 09:30 | 113.06 | 100.14
2017-08-07 10:00 | 111.09 | 98.66
2017-08-07 10:30 | 112.98 | 99.12
2017-08-07 11:00 | 107.43 | 92.91
2017-08-07 11:30 | 104.05 | 90.67
2017-08-07 12:00 | 97.02 | 82.5
2017-08-07 12:30 | 101.42 | 88.32
2017-08-07 13:00 | 107.11 | 95.48
2017-08-07 13:30 | 104.78 | 93.03
2017-08-07 14:00 | 108.18 | 94.81
2017-08-07 14:30 | 98.54 | 84.31
2017-08-07 15:00 | 103.19 | 90.67
2017-08-07 15:30 | 105.29 | 92.03
2017-08-07 16:00 | 101.57 | 88.76
2017-08-07 16:30 | 106.51 | 94.52
2017-08-07 17:00 | 112.04 | 99.56
2017-08-07 17:30 | 115.39 | 102.38
2017-08-07 18:00 | 118.75 | 105.23
2017-08-07 18:30 | 110.91 | 95.36
2017-08-07 19:00 | 115.82 | 100.66
2017-08-07 19:30 | 126.82 | 112.21
2017-08-07 20:00 | 120.81 | 105.54
2017-08-07 20:30 | 118.65 | 103.78
2017-08-07 21:00 | 119.68 | 104.3
2017-08-07 21:30 | 124.68 | 109.83
2017-08-07 22:00 | 120.6 | 106.47
2017-08-07 22:30 | 114.85 | 100.24
2017-08-07 23:00 | 117.02 | 103.52
2017-08-07 23:30 | 113.34 | 98.59
2017-08-08 | 118.35 | 104.13
2017-08-08 00:30 | 122.63 | 109.56
2017-08-08 01:00 | 116.86 | 103.53
2017-08-08 01:30 | 110.97 | 97.95
2017-08-08 02:00 | 112.95 | 100.39
2017-08-08 02:30 | 111.68 | 100.6
2017-08-08 03:00 | 115.63 | 103.62
2017-08-08 03:30 | 111.97 | 99.39
2017-08-08 04:00 | 108.74 | 96.1
2017-08-08 04:30 | 114.02 | 101.89
2017-08-08 05:00 | 111.69 | 100.01
2017-08-08 05:30 | 108.38 | 96.13
2017-08-08 06:00 | 106.99 | 95.66
2017-08-08 06:30 | 103.45 | 90.77
2017-08-08 07:00 | 103.34 | 89.82
2017-08-08 07:30 | 107.96 | 96.73
2017-08-08 08:00 | 97.32 | 84.48
2017-08-08 08:30 | 96.89 | 82.86
2017-08-08 09:00 | 96.76 | 82.37
2017-08-08 09:30 | 96.23 | 81.95
2017-08-08 10:00 | 97.01 | 82.85
2017-08-08 10:30 | 95.56 | 80
2017-08-08 11:00 | 103.68 | 89.86
2017-08-08 11:30 | 100.36 | 85.97
2017-08-08 12:00 | 98.83 | 84.4
2017-08-08 12:30 | 97.39 | 82.91
2017-08-08 13:00 | 102.94 | 89.4
2017-08-08 13:30 | 100.2 | 86.21
2017-08-08 14:00 | 99.96 | 85.14
2017-08-08 14:30 | 103.76 | 90.24
2017-08-08 15:00 | 102.56 | 88.44
2017-08-08 15:30 | 97.3 | 81.02
2017-08-08 16:00 | 97.1 | 81.42
2017-08-08 16:30 | 101.34 | 87.47
2017-08-08 17:00 | 102.61 | 89.24
2017-08-08 17:30 | 103.8 | 91.5
2017-08-08 18:00 | 106.42 | 94.5
2017-08-08 18:30 | 96.95 | 81.9
2017-08-08 19:00 | 111.94 | 100.74
2017-08-08 19:30 | 114.31 | 103.19
2017-08-08 20:00 | 115.54 | 104.35
2017-08-08 20:30 | 105.46 | 93.15
2017-08-08 21:00 | 114.31 | 103.09
2017-08-08 21:30 | 117.67 | 106.92
2017-08-08 22:00 | 112.52 | 101.17
2017-08-08 22:30 | 116.22 | 104.4
2017-08-08 23:00 | 110.79 | 98.5
2017-08-08 23:30 | 109.04 | 95.96
2017-08-09 | 105.84 | 92.48
2017-08-09 00:30 | 108.88 | 96.11
2017-08-09 01:00 | 107.97 | 95.6
2017-08-09 01:30 | 110.69 | 98.94
2017-08-09 02:00 | 114.12 | 102.98
2017-08-09 02:30 | 111.16 | 99.69
2017-08-09 03:00 | 107.16 | 95.98
2017-08-09 03:30 | 99.32 | 85.77
2017-08-09 04:00 | 97.64 | 84.37
2017-08-09 04:30 | 95.33 | 80.09
2017-08-09 05:00 | 95.94 | 80.42
2017-08-09 05:30 | 100.81 | 86.01
2017-08-09 06:00 | 101.51 | 86.36
2017-08-09 06:30 | 94.06 | 74.91
2017-08-09 07:00 | 97.97 | 81.41
2017-08-09 07:30 | 99.01 | 80.38
2017-08-09 08:00 | 101.34 | 83.6
2017-08-09 08:30 | 94.78 | 75.99
2017-08-09 09:00 | 91.68 | 72.97
2017-08-09 09:30 | 86.1 | 62.98
2017-08-09 10:00 | 84.21 | 59.75
2017-08-09 10:30 | 77.36 | 52.8
2017-08-09 11:00 | 84.75 | 61.26
2017-08-09 11:30 | 87.92 | 66.52
2017-08-09 12:00 | 96.93 | 78.34
2017-08-09 12:30 | 91.31 | 72.19
2017-08-09 13:00 | 89.86 | 67.74
2017-08-09 13:30 | 92.68 | 69.53
2017-08-09 14:00 | 88.87 | 65.8
2017-08-09 14:30 | 85.89 | 60.43
2017-08-09 15:00 | 85.33 | 57.3
2017-08-09 15:30 | 84.74 | 57.83
2017-08-09 16:00 | 90.07 | 67.43
2017-08-09 16:30 | 93.03 | 70.14
2017-08-09 17:00 | 91.49 | 68.45
2017-08-09 17:30 | 89 | 66.8
2017-08-09 18:00 | 95.35 | 75.05
2017-08-09 18:30 | 95.02 | 75.29
2017-08-09 19:00 | 98.93 | 82.15
2017-08-09 19:30 | 99.25 | 83.92
2017-08-09 20:00 | 95.48 | 78.85
2017-08-09 20:30 | 96.15 | 77.96
2017-08-09 21:00 | 96.87 | 80.21
2017-08-09 21:30 | 96.42 | 79.26
2017-08-09 22:00 | 100.7 | 84.89
2017-08-09 22:30 | 96.72 | 78.86
2017-08-09 23:00 | 94.66 | 75.81
2017-08-09 23:30 | 96.09 | 76.29
2017-08-10 | 99.04 | 81.73
2017-08-10 00:30 | 96.12 | 78.61
2017-08-10 01:00 | 98.79 | 81.71
2017-08-10 01:30 | 97.91 | 79.83
2017-08-10 02:00 | 105.83 | 89.92
2017-08-10 02:30 | 107.24 | 90.43
2017-08-10 03:00 | 99.78 | 80.9
2017-08-10 03:30 | 96.31 | 77.24
2017-08-10 04:00 | 98.69 | 79.99
2017-08-10 04:30 | 102.4 | 85.52
2017-08-10 05:00 | 98.73 | 79.29
2017-08-10 05:30 | 98.37 | 81.4
2017-08-10 06:00 | 99.79 | 84.34
2017-08-10 06:30 | 92.01 | 73.69
2017-08-10 07:00 | 84.54 | 64.87
2017-08-10 07:30 | 86.82 | 69.46
2017-08-10 08:00 | 86.73 | 68.13
2017-08-10 08:30 | 85.95 | 66.07
2017-08-10 09:00 | 84.68 | 62.27
2017-08-10 09:30 | 83.31 | 59.79
2017-08-10 10:00 | 88.85 | 66.52
2017-08-10 10:30 | 94.28 | 72.1
2017-08-10 11:00 | 94.37 | 71.33
2017-08-10 11:30 | 90.47 | 66.57
2017-08-10 12:00 | 91.39 | 69.81
2017-08-10 12:30 | 88.97 | 67.11
2017-08-10 13:00 | 92.32 | 73.51
2017-08-10 13:30 | 94.18 | 75.95
2017-08-10 14:00 | 95.37 | 77.09
2017-08-10 14:30 | 93.58 | 73.48
2017-08-10 15:00 | 93.22 | 74
2017-08-10 15:30 | 87.59 | 67.21
2017-08-10 16:00 | 93.08 | 73.83
2017-08-10 16:30 | 96.94 | 79.28
2017-08-10 17:00 | 99.36 | 82.71
2017-08-10 17:30 | 99.15 | 81.9
2017-08-10 18:00 | 105.47 | 91.98
2017-08-10 18:30 | 98.67 | 82.7
2017-08-10 19:00 | 98.77 | 83.3
2017-08-10 19:30 | 96.41 | 84.02
2017-08-10 20:00 | 94.39 | 81.5
2017-08-10 20:30 | 98.05 | 83.51
2017-08-10 21:00 | 100.64 | 87.15
2017-08-10 21:30 | 99.17 | 85.18
2017-08-10 22:00 | 102.66 | 89.89
2017-08-10 22:30 | 104.89 | 93.1
2017-08-10 23:00 | 102.37 | 90.49
2017-08-10 23:30 | 101.5 | 88.62
2017-08-11 | 103.12 | 90.14
2017-08-11 00:30 | 106.56 | 94.3
2017-08-11 01:00 | 101.26 | 87.51
2017-08-11 01:30 | 104.94 | 92.81
2017-08-11 02:00 | 106.1 | 95.2
2017-08-11 02:30 | 105.44 | 94.61
2017-08-11 03:00 | 100.54 | 88.18
2017-08-11 03:30 | 109.19 | 98.87
2017-08-11 04:00 | 112.26 | 101.32
2017-08-11 04:30 | 113.13 | 102.14
2017-08-11 05:00 | 104.3 | 92.55
2017-08-11 05:30 | 112.08 | 100.5
2017-08-11 06:00 | 110.25 | 97.68
2017-08-11 06:30 | 104.36 | 90.55
2017-08-11 07:00 | 108.67 | 95.96
2017-08-11 07:30 | 115.75 | 103.77
2017-08-11 08:00 | 109.73 | 97.4
2017-08-11 08:30 | 103.34 | 92.22
2017-08-11 09:00 | 101.33 | 89.99
2017-08-11 09:30 | 96.06 | 83.59
2017-08-11 10:00 | 105.4 | 92.15
2017-08-11 10:30 | 102.25 | 88.45
2017-08-11 11:00 | 106.58 | 92.83
2017-08-11 11:30 | 105.19 | 91.29
2017-08-11 12:00 | 108.32 | 94.18
2017-08-11 12:30 | 107.43 | 93.68
2017-08-11 13:00 | 110.89 | 97.22
2017-08-11 13:30 | 97.36 | 81.35
2017-08-11 14:00 | 107.75 | 92.61
2017-08-11 14:30 | 104.4 | 88.87
2017-08-11 15:00 | 106.32 | 91.08
2017-08-11 15:30 | 106.3 | 90.7
2017-08-11 16:00 | 115.11 | 100.12
2017-08-11 16:30 | 115.34 | 99.85
2017-08-11 17:00 | 108.3 | 94.08
2017-08-11 17:30 | 119.09 | 103.96
2017-08-11 18:00 | 122.92 | 107.87
2017-08-11 18:30 | 118.76 | 102.2
2017-08-11 19:00 | 120.41 | 105.01
2017-08-11 19:30 | 123.33 | 107.67
2017-08-11 20:00 | 119.79 | 104.15
2017-08-11 20:30 | 126.55 | 111.13
2017-08-11 21:00 | 118.77 | 103.86
2017-08-11 21:30 | 113.16 | 96.91
2017-08-11 22:00 | 111.14 | 95.7
2017-08-11 22:30 | 116.46 | 101.34
2017-08-11 23:00 | 111.19 | 95
2017-08-11 23:30 | 116.06 | 100.31
2017-08-12 | 114.07 | 98.23
2017-08-12 00:30 | 112.09 | 97
2017-08-12 01:00 | 115.38 | 100.35
2017-08-12 01:30 | 112.77 | 97.64
2017-08-12 02:00 | 112.98 | 97.22
2017-08-12 02:30 | 108.7 | 93.34
2017-08-12 03:00 | 109.53 | 93.78
2017-08-12 03:30 | 108.23 | 91.56
2017-08-12 04:00 | 120.21 | 103.36
2017-08-12 04:30 | 115.34 | 99.65
2017-08-12 05:00 | 116.71 | 101.57
2017-08-12 05:30 | 117.6 | 101.25
2017-08-12 06:00 | 118.9 | 102.97
2017-08-12 06:30 | 107.41 | 91.19
2017-08-12 07:00 | 122.57 | 107.55
2017-08-12 07:30 | 119.07 | 104.83
2017-08-12 08:00 | 117.42 | 102.81
2017-08-12 08:30 | 110.27 | 95.03
2017-08-12 09:00 | 109.51 | 98.17
2017-08-12 09:30 | 110.71 | 96.88
2017-08-12 10:00 | 109.1 | 95.22
2017-08-12 10:30 | 105.25 | 91.15
2017-08-12 11:00 | 101.32 | 86.92
2017-08-12 11:30 | 109.51 | 95.9
2017-08-12 12:00 | 109.4 | 95.62
2017-08-12 12:30 | 108.39 | 94.43
2017-08-12 13:00 | 110.65 | 95.93
2017-08-12 13:30 | 109.89 | 95.75
2017-08-12 14:00 | 115.87 | 102.61
2017-08-12 14:30 | 114.52 | 100.25
2017-08-12 15:00 | 112.22 | 96.85
2017-08-12 15:30 | 112.79 | 97.35
2017-08-12 16:00 | 112.02 | 97.16
2017-08-12 16:30 | 115.09 | 100.29
2017-08-12 17:00 | 114.57 | 99.52
2017-08-12 17:30 | 118.63 | 104.61
2017-08-12 18:00 | 117.79 | 101.7
2017-08-12 18:30 | 110.14 | 93.22
2017-08-12 19:00 | 113.59 | 98.19
2017-08-12 19:30 | 117.77 | 101.17
2017-08-12 20:00 | 125.1 | 107.68
2017-08-12 20:30 | 118.21 | 100.49
2017-08-12 21:00 | 118.08 | 99.81
2017-08-12 21:30 | 118.82 | 101.18
2017-08-12 22:00 | 117.94 | 102.18
2017-08-12 22:30 | 116.92 | 99.87
2017-08-12 23:00 | 119.57 | 102.68
2017-08-12 23:30 | 117.15 | 101.06
2017-08-13 | 109.71 | 92.8
2017-08-13 00:30 | 117.85 | 102.03
2017-08-13 01:00 | 118.94 | 103.43
2017-08-13 01:30 | 123.09 | 107.37
2017-08-13 02:00 | 124.97 | 111.24
2017-08-13 02:30 | 116.47 | 102.7
2017-08-13 03:00 | 119.24 | 105.8
2017-08-13 03:30 | 112.76 | 98.29
2017-08-13 04:00 | 117.74 | 103.03
2017-08-13 04:30 | 116.1 | 101.24
2017-08-13 05:00 | 120.48 | 105.28
2017-08-13 05:30 | 117.55 | 102.58
2017-08-13 06:00 | 112.74 | 97.53
2017-08-13 06:30 | 111.02 | 96.69
2017-08-13 07:00 | 106.48 | 91.87
2017-08-13 07:30 | 105.47 | 92
2017-08-13 08:00 | 109.05 | 95.63
2017-08-13 08:30 | 113.52 | 99.42
2017-08-13 09:00 | 100.09 | 84.96
2017-08-13 09:30 | 106.71 | 92.64
2017-08-13 10:00 | 110.67 | 97.01
2017-08-13 10:30 | 105.18 | 90.94
2017-08-13 11:00 | 112.34 | 98.74
2017-08-13 11:30 | 109.51 | 94.6
2017-08-13 12:00 | 110.83 | 96
2017-08-13 12:30 | 107.51 | 93.5
2017-08-13 13:00 | 107.81 | 94.07
2017-08-13 13:30 | 109.56 | 96.01
2017-08-13 14:00 | 109.35 | 95.91
2017-08-13 14:30 | 105.78 | 91.89
2017-08-13 15:00 | 111.76 | 97.88
2017-08-13 15:30 | 103.39 | 88.99
2017-08-13 16:00 | 110.53 | 96.11
2017-08-13 16:30 | 105.58 | 89.79
2017-08-13 17:00 | 113.64 | 98.7
2017-08-13 17:30 | 116.26 | 100.92
2017-08-13 18:00 | 112.05 | 97
2017-08-13 18:30 | 112.78 | 96.56
2017-08-13 19:00 | 111.67 | 95.53
2017-08-13 19:30 | 116.83 | 101.02
2017-08-13 20:00 | 117.63 | 101.63
2017-08-13 20:30 | 119.15 | 102.18
2017-08-13 21:00 | 116.38 | 101.61
2017-08-13 21:30 | 114.95 | 100.03
2017-08-13 22:00 | 112.98 | 97.87
2017-08-13 22:30 | 110.19 | 94.02
2017-08-13 23:00 | 115.11 | 100.16
2017-08-13 23:30 | 111.21 | 96.11
2017-08-14 | 113.34 | 98.84
2017-08-14 00:30 | 117.18 | 102.47
2017-08-14 01:00 | 115.05 | 100.1
2017-08-14 01:30 | 112.99 | 97.76
2017-08-14 02:00 | 116.59 | 102.06
2017-08-14 02:30 | 113.24 | 99.15
2017-08-14 03:00 | 111.84 | 98.12
2017-08-14 03:30 | 107.25 | 92.91
2017-08-14 04:00 | 103.94 | 90.39
2017-08-14 04:30 | 104.38 | 91.25
2017-08-14 05:00 | 104.73 | 91.96
2017-08-14 05:30 | 104.13 | 91.19
2017-08-14 06:00 | 109.96 | 96.68
2017-08-14 06:30 | 102.32 | 88.54
2017-08-14 07:00 | 107.78 | 94.96
2017-08-14 07:30 | 121.25 | 108.54
2017-08-14 08:00 | 115.91 | 101.9
2017-08-14 08:30 | 103.55 | 88.91
2017-08-14 09:00 | 105.66 | 90.15
2017-08-14 09:30 | 105.53 | 90.26
2017-08-14 10:00 | 101.09 | 85.9
2017-08-14 10:30 | 105.63 | 90.74
2017-08-14 11:00 | 104.04 | 89.4
2017-08-14 11:30 | 107.6 | 92.23
2017-08-14 12:00 | 101.56 | 85.68
2017-08-14 12:30 | 104.2 | 88.47
2017-08-14 13:00 | 105.89 | 90.11
2017-08-14 13:30 | 108.47 | 92.59
2017-08-14 14:00 | 101.63 | 83.71
2017-08-14 14:30 | 110.16 | 94.78
2017-08-14 15:00 | 112.77 | 96.74
2017-08-14 15:30 | 114.23 | 98.05
2017-08-14 16:00 | 113.25 | 96.39
2017-08-14 16:30 | 118.8 | 103.82
2017-08-14 17:00 | 115.06 | 99.32
2017-08-14 17:30 | 117.56 | 100.48
2017-08-14 18:00 | 118.08 | 102.22
2017-08-14 18:30 | 113.8 | 96.55
2017-08-14 19:00 | 113.31 | 97.51
2017-08-14 19:30 | 123.13 | 107.03
2017-08-14 20:00 | 114.53 | 98.22
2017-08-14 20:30 | 110.43 | 96.23
2017-08-14 21:00 | 105.32 | 90.66
2017-08-14 21:30 | 108.2 | 94.04
2017-08-14 22:00 | 111.35 | 98.19
2017-08-14 22:30 | 114.53 | 100.63
2017-08-14 23:00 | 105.39 | 91.71
2017-08-14 23:30 | 101.86 | 88.06
2017-08-15 | 101.95 | 88.29
2017-08-15 00:30 | 100.65 | 86.78
2017-08-15 01:00 | 98.99 | 83.94
2017-08-15 01:30 | 104.41 | 90.24
2017-08-15 02:00 | 104.24 | 90.56
2017-08-15 02:30 | 97.68 | 83.53
2017-08-15 03:00 | 100.95 | 85.15
2017-08-15 03:30 | 101.32 | 85.74
2017-08-15 04:00 | 102.77 | 87.77
2017-08-15 04:30 | 109.35 | 93.72
2017-08-15 05:00 | 103.61 | 89.3
2017-08-15 05:30 | 117.63 | 103.51
2017-08-15 06:00 | 112.15 | 97.42
2017-08-15 06:30 | 103.24 | 87.62
2017-08-15 07:00 | 113.71 | 99.33
2017-08-15 07:30 | 113.48 | 98.77
2017-08-15 08:00 | 110.94 | 95.11
2017-08-15 08:30 | 103.31 | 87.15
2017-08-15 09:00 | 103.92 | 87.73
2017-08-15 09:30 | 105.27 | 88.07
2017-08-15 10:00 | 106.07 | 89.74
2017-08-15 10:30 | 108.31 | 92.68
2017-08-15 11:00 | 102.84 | 85.98
2017-08-15 11:30 | 108.85 | 93.03
2017-08-15 12:00 | 106.18 | 88.99
2017-08-15 12:30 | 102.92 | 85.07
2017-08-15 13:00 | 108.87 | 90.97
2017-08-15 13:30 | 112.85 | 95.36
2017-08-15 14:00 | 117.41 | 100.42
2017-08-15 14:30 | 115.49 | 97.55
2017-08-15 15:00 | 108.54 | 88.94
2017-08-15 15:30 | 105.46 | 86.55
2017-08-15 16:00 | 114.15 | 95.88
2017-08-15 16:30 | 110.45 | 92.11
2017-08-15 17:00 | 112.22 | 94.05
2017-08-15 17:30 | 112.53 | 95.1
2017-08-15 18:00 | 113.41 | 97.32
2017-08-15 18:30 | 106.87 | 86.84
2017-08-15 19:00 | 115.61 | 96.59
2017-08-15 19:30 | 113.86 | 97.13
2017-08-15 20:00 | 117.08 | 99.92
2017-08-15 20:30 | 113.44 | 97.15
2017-08-15 21:00 | 107.89 | 93.25
2017-08-15 21:30 | 110.63 | 96.44
2017-08-15 22:00 | 107.76 | 93.13
2017-08-15 22:30 | 107.72 | 93.28
2017-08-15 23:00 | 108.55 | 93.6
2017-08-15 23:30 | 109.41 | 96.2
2017-08-16 | 105.85 | 92.41
2017-08-16 00:30 | 102.68 | 88.35
2017-08-16 01:00 | 111.19 | 96.14
2017-08-16 01:30 | 115.97 | 100.44
2017-08-16 02:00 | 115.67 | 100.61
2017-08-16 02:30 | 117.01 | 102.7
2017-08-16 03:00 | 123.54 | 108.5
2017-08-16 03:30 | 117.58 | 102.88
2017-08-16 04:00 | 112.98 | 98
2017-08-16 04:30 | 113.34 | 100.02
2017-08-16 05:00 | 111.47 | 95.44
2017-08-16 05:30 | 122.86 | 108.16
2017-08-16 06:00 | 122.31 | 107.66
2017-08-16 06:30 | 106.27 | 90.61
2017-08-16 07:00 | 108.25 | 92.75
2017-08-16 07:30 | 109.51 | 94.64
2017-08-16 08:00 | 111.22 | 95.65
2017-08-16 08:30 | 116.48 | 99.76
2017-08-16 09:00 | 109.55 | 92.23
2017-08-16 09:30 | 113.04 | 95.85
2017-08-16 10:00 | 104.13 | 87.18
2017-08-16 10:30 | 105.02 | 87.85
2017-08-16 11:00 | 112.62 | 95.79
2017-08-16 11:30 | 106.21 | 90.5
2017-08-16 12:00 | 108.99 | 91.95
2017-08-16 12:30 | 113.96 | 97.82
2017-08-16 13:00 | 114.37 | 97.42
2017-08-16 13:30 | 113.44 | 96.01
2017-08-16 14:00 | 106.37 | 88
2017-08-16 14:30 | 120.52 | 103.34
2017-08-16 15:00 | 107.19 | 89.27
2017-08-16 15:30 | 101.35 | 83.77
2017-08-16 16:00 | 103.42 | 85.2
2017-08-16 16:30 | 112.75 | 95.96
2017-08-16 17:00 | 107.66 | 91.52
2017-08-16 17:30 | 110.22 | 93.62
2017-08-16 18:00 | 115.93 | 100.39
2017-08-16 18:30 | 111.58 | 96.67
2017-08-16 19:00 | 112.29 | 97.28
2017-08-16 19:30 | 120.85 | 105.73
2017-08-16 20:00 | 123.37 | 108.41
2017-08-16 20:30 | 125.15 | 110.08
2017-08-16 21:00 | 116.68 | 101.95
2017-08-16 21:30 | 120.13 | 104.19
2017-08-16 22:00 | 120.6 | 106.99
2017-08-16 22:30 | 113.26 | 100.2
2017-08-16 23:00 | 122.59 | 108.14
2017-08-16 23:30 | 118.64 | 104.26
2017-08-17 | 120.02 | 105.96
2017-08-17 00:30 | 117.07 | 103.22
2017-08-17 01:00 | 114.87 | 101.39
2017-08-17 01:30 | 115.01 | 101
2017-08-17 02:00 | 111.34 | 97.09
2017-08-17 02:30 | 104.94 | 90.22
2017-08-17 03:00 | 107.05 | 92.62
2017-08-17 03:30 | 109.49 | 94.68
2017-08-17 04:00 | 119.51 | 105.55
2017-08-17 04:30 | 114.29 | 100.1
2017-08-17 05:00 | 110.81 | 96.83
2017-08-17 05:30 | 110.95 | 97.31
2017-08-17 06:00 | 112.95 | 99.35
2017-08-17 06:30 | 106.86 | 91.55
2017-08-17 07:00 | 103.26 | 88.81
2017-08-17 07:30 | 101.26 | 86.07
2017-08-17 08:00 | 104.95 | 90.34
2017-08-17 08:30 | 103.82 | 89.76
2017-08-17 09:00 | 94.28 | 78.86
2017-08-17 09:30 | 90.14 | 72.85
2017-08-17 10:00 | 95.45 | 77.24
2017-08-17 10:30 | 96.35 | 79.25
2017-08-17 11:00 | 99.29 | 82.69
2017-08-17 11:30 | 102.84 | 85.37
2017-08-17 12:00 | 100.52 | 84.25
2017-08-17 12:30 | 104.19 | 87.71
2017-08-17 13:00 | 106.27 | 89.93
2017-08-17 13:30 | 112.12 | 96.46
2017-08-17 14:00 | 116.43 | 100.74
2017-08-17 14:30 | 119.23 | 102.95
2017-08-17 15:00 | 114.3 | 97.56
2017-08-17 15:30 | 104.63 | 85.82
2017-08-17 16:00 | 101.17 | 82.86
2017-08-17 16:30 | 115.36 | 98.37
2017-08-17 17:00 | 112.85 | 96.36
2017-08-17 17:30 | 117.01 | 101.04
2017-08-17 18:00 | 115.66 | 99.65
2017-08-17 18:30 | 113.2 | 94.86
2017-08-17 19:00 | 115.84 | 97.75
2017-08-17 19:30 | 115.15 | 97.38
2017-08-17 20:00 | 120.77 | 101.95
2017-08-17 20:30 | 117.43 | 98.09
2017-08-17 21:00 | 110.01 | 92.38
2017-08-17 21:30 | 112.86 | 97.02
2017-08-17 22:00 | 114.96 | 98.96
2017-08-17 22:30 | 118.74 | 103.45
2017-08-17 23:00 | 115.79 | 100.65
2017-08-17 23:30 | 118.86 | 103.69
2017-08-18 | 117.87 | 103.27
2017-08-18 00:30 | 111.33 | 95.67
2017-08-18 01:00 | 112.62 | 95.85
2017-08-18 01:30 | 111 | 95.22
2017-08-18 02:00 | 108.82 | 93.66
2017-08-18 02:30 | 118.41 | 103.06
2017-08-18 03:00 | 111.52 | 95.58
2017-08-18 03:30 | 109.87 | 94.01
2017-08-18 04:00 | 117.88 | 101.07
2017-08-18 04:30 | 117.69 | 102.37
2017-08-18 05:00 | 116.63 | 100.84
2017-08-18 05:30 | 113.11 | 98.06
2017-08-18 06:00 | 112.17 | 96.79
2017-08-18 06:30 | 106.64 | 90.41
2017-08-18 07:00 | 111.5 | 96.63
2017-08-18 07:30 | 117.36 | 103.09
2017-08-18 08:00 | 112.16 | 96.67
2017-08-18 08:30 | 114.94 | 99.42
2017-08-18 09:00 | 121.36 | 105.66
2017-08-18 09:30 | 119.04 | 102.83
2017-08-18 10:00 | 117.75 | 102.62
2017-08-18 10:30 | 117.17 | 101.73
2017-08-18 11:00 | 114.32 | 97.79
2017-08-18 11:30 | 117.32 | 100.56
2017-08-18 12:00 | 120.97 | 104.18
2017-08-18 12:30 | 117.08 | 99.65
2017-08-18 13:00 | 113.55 | 94.51
2017-08-18 13:30 | 117.23 | 99.26
2017-08-18 14:00 | 120.51 | 101.84
2017-08-18 14:30 | 117.05 | 98.55
2017-08-18 15:00 | 118.28 | 101.36
2017-08-18 15:30 | 115.1 | 97.59
2017-08-18 16:00 | 120.37 | 103.76
2017-08-18 16:30 | 117.61 | 101.3
2017-08-18 17:00 | 120.59 | 104.07
2017-08-18 17:30 | 124.73 | 106.77
2017-08-18 18:00 | 115.45 | 96.91
2017-08-18 18:30 | 111.47 | 95.69
2017-08-18 19:00 | 120.89 | 106.44
2017-08-18 19:30 | 120.92 | 105.85
2017-08-18 20:00 | 126.44 | 111.83
2017-08-18 20:30 | 124.25 | 110.79
2017-08-18 21:00 | 112.83 | 99.02
2017-08-18 21:30 | 118.41 | 105.54
2017-08-18 22:00 | 114.34 | 100.28
2017-08-18 22:30 | 117.18 | 103.47
2017-08-18 23:00 | 116.49 | 102.01
2017-08-18 23:30 | 120.98 | 107.42
2017-08-19 | 120.56 | 108.01
2017-08-19 00:30 | 116.47 | 103.72
2017-08-19 01:00 | 114.22 | 101.03
2017-08-19 01:30 | 115.47 | 101.98
2017-08-19 02:00 | 116.57 | 103.4
2017-08-19 02:30 | 116.13 | 103.09
2017-08-19 03:00 | 113.91 | 100.21
2017-08-19 03:30 | 117.25 | 102.69
2017-08-19 04:00 | 114.9 | 99.84
2017-08-19 04:30 | 111.66 | 96.96
2017-08-19 05:00 | 111.51 | 96.67
2017-08-19 05:30 | 116.56 | 101.63
2017-08-19 06:00 | 115.44 | 101.33
2017-08-19 06:30 | 114.39 | 99.41
2017-08-19 07:00 | 114.67 | 100.5
2017-08-19 07:30 | 114.14 | 100.51
2017-08-19 08:00 | 109.09 | 94.86
2017-08-19 08:30 | 108.29 | 95.02
2017-08-19 09:00 | 108.04 | 92.95
2017-08-19 09:30 | 106.06 | 91.05
2017-08-19 10:00 | 102.76 | 86.96
2017-08-19 10:30 | 102.75 | 86.73
2017-08-19 11:00 | 101.5 | 84.66
2017-08-19 11:30 | 103.09 | 86.56
2017-08-19 12:00 | 106.54 | 91.7
2017-08-19 12:30 | 106.7 | 92.46
2017-08-19 13:00 | 104.35 | 89.76
2017-08-19 13:30 | 106.42 | 91.33
2017-08-19 14:00 | 104.68 | 88.22
2017-08-19 14:30 | 107.73 | 92.45
2017-08-19 15:00 | 104.68 | 88.96
2017-08-19 15:30 | 100.66 | 84.56
2017-08-19 16:00 | 102.22 | 86.44
2017-08-19 16:30 | 106.72 | 91.63
2017-08-19 17:00 | 102.47 | 87.93
2017-08-19 17:30 | 105.64 | 92.23
2017-08-19 18:00 | 107.31 | 93.47
2017-08-19 18:30 | 106.82 | 92.09
2017-08-19 19:00 | 111.31 | 96.52
2017-08-19 19:30 | 119.18 | 104.41
2017-08-19 20:00 | 114.8 | 99.27
2017-08-19 20:30 | 112.57 | 97.55
2017-08-19 21:00 | 114.2 | 100.05
2017-08-19 21:30 | 116.23 | 102.39
2017-08-19 22:00 | 114.29 | 101.45
2017-08-19 22:30 | 110.21 | 96.9
2017-08-19 23:00 | 114.71 | 101.43
2017-08-19 23:30 | 111.24 | 97.23
2017-08-20 | 107.16 | 92.57
2017-08-20 00:30 | 107.37 | 92.43
2017-08-20 01:00 | 110.63 | 96.81
2017-08-20 01:30 | 109.86 | 95.46
2017-08-20 02:00 | 114.08 | 100.87
2017-08-20 02:30 | 114.72 | 100.93
2017-08-20 03:00 | 114.3 | 100.11
2017-08-20 03:30 | 114.08 | 100.13
2017-08-20 04:00 | 113.55 | 99.49
2017-08-20 04:30 | 113.16 | 99.67
2017-08-20 05:00 | 112.77 | 98.29
2017-08-20 05:30 | 114.48 | 99.83
2017-08-20 06:00 | 116.25 | 101.95
2017-08-20 06:30 | 107.17 | 90.93
2017-08-20 07:00 | 109.24 | 94.42
2017-08-20 07:30 | 114.08 | 101.28
2017-08-20 08:00 | 116.03 | 102.77
2017-08-20 08:30 | 113.73 | 99.63
2017-08-20 09:00 | 102.43 | 87.18
2017-08-20 09:30 | 106.68 | 92.52
2017-08-20 10:00 | 111.07 | 96.58
2017-08-20 10:30 | 117.35 | 102.32
2017-08-20 11:00 | 111.09 | 95.12
2017-08-20 11:30 | 111.14 | 94.83
2017-08-20 12:00 | 121.19 | 106.23
2017-08-20 12:30 | 118.88 | 104.1
2017-08-20 13:00 | 114.22 | 98.63
2017-08-20 13:30 | 110.46 | 94.69
2017-08-20 14:00 | 111.2 | 95.57
2017-08-20 14:30 | 112.54 | 96.85
2017-08-20 15:00 | 118.09 | 103.63
2017-08-20 15:30 | 114.95 | 99.88
2017-08-20 16:00 | 115.35 | 99.74
2017-08-20 16:30 | 113.16 | 97.6
2017-08-20 17:00 | 116.66 | 101.2
2017-08-20 17:30 | 122.04 | 105.19
2017-08-20 18:00 | 117.32 | 100.75
2017-08-20 18:30 | 117.47 | 99.14
2017-08-20 19:00 | 120.64 | 103.81
2017-08-20 19:30 | 119.07 | 101.73
2017-08-20 20:00 | 112.83 | 94.84
2017-08-20 20:30 | 112.09 | 94.32
2017-08-20 21:00 | 113.66 | 97.06
2017-08-20 21:30 | 107.08 | 91.65
2017-08-20 22:00 | 110.08 | 95.36
2017-08-20 22:30 | 113.92 | 97.81
2017-08-20 23:00 | 112.8 | 96.76
2017-08-20 23:30 | 107.86 | 92.63
2017-08-21 | 110.15 | 94.81
2017-08-21 00:30 | 111.59 | 95.53
2017-08-21 01:00 | 106.04 | 90.91
2017-08-21 01:30 | 110.5 | 94.91
2017-08-21 02:00 | 115.19 | 99.72
2017-08-21 02:30 | 110.37 | 95.34
2017-08-21 03:00 | 106.41 | 90.51
2017-08-21 03:30 | 110.82 | 94.73
2017-08-21 04:00 | 105.71 | 90.13
2017-08-21 04:30 | 105.08 | 89.11
2017-08-21 05:00 | 104.14 | 87.85
2017-08-21 05:30 | 103.85 | 87.25
2017-08-21 06:00 | 104.69 | 88.32
2017-08-21 06:30 | 97.24 | 80.73
2017-08-21 07:00 | 95.64 | 80.84
2017-08-21 07:30 | 96.2 | 82.01
2017-08-21 08:00 | 92.24 | 78.22
2017-08-21 08:30 | 96.25 | 81.96
2017-08-21 09:00 | 93.68 | 78.86
2017-08-21 09:30 | 95.96 | 79.97
2017-08-21 10:00 | 96.94 | 79.1
2017-08-21 10:30 | 98.77 | 81.6
2017-08-21 11:00 | 95.85 | 78.95
2017-08-21 11:30 | 92.91 | 75.95
2017-08-21 12:00 | 92.33 | 75.9
2017-08-21 12:30 | 99.24 | 81.81
2017-08-21 13:00 | 100.98 | 83.55
2017-08-21 13:30 | 105.39 | 88.28
2017-08-21 14:00 | 100.73 | 83.26
2017-08-21 14:30 | 94.18 | 77.69
2017-08-21 15:00 | 93.53 | 76.72
2017-08-21 15:30 | 96.32 | 79.36
2017-08-21 16:00 | 97.45 | 81.08
2017-08-21 16:30 | 95.86 | 80.04
2017-08-21 17:00 | 102.94 | 87.33
2017-08-21 17:30 | 107.18 | 90.63
2017-08-21 18:00 | 106.39 | 89.94
2017-08-21 18:30 | 103.47 | 85.46
2017-08-21 19:00 | 102.3 | 84.65
2017-08-21 19:30 | 105.07 | 87.25
2017-08-21 20:00 | 103.97 | 86.27
2017-08-21 20:30 | 109.82 | 93
2017-08-21 21:00 | 104.07 | 86.76
2017-08-21 21:30 | 101.81 | 84.74
2017-08-21 22:00 | 107.93 | 91.37
2017-08-21 22:30 | 106.12 | 90.71
2017-08-21 23:00 | 107.02 | 89.64
2017-08-21 23:30 | 100.51 | 82.81
2017-08-22 | 102.6 | 85.06
2017-08-22 00:30 | 106.94 | 89.65
2017-08-22 01:00 | 108.07 | 90.83
2017-08-22 01:30 | 110.8 | 93.88
2017-08-22 02:00 | 102.81 | 85.5
2017-08-22 02:30 | 111.27 | 94.16
2017-08-22 03:00 | 104.19 | 86.57
2017-08-22 03:30 | 103.23 | 86.7
2017-08-22 04:00 | 101.95 | 85.12
2017-08-22 04:30 | 105.85 | 89.35
2017-08-22 05:00 | 106.33 | 90.23
2017-08-22 05:30 | 100.04 | 82.78
2017-08-22 06:00 | 100.77 | 84.07
2017-08-22 06:30 | 97.46 | 79.52
2017-08-22 07:00 | 104.49 | 89.1
2017-08-22 07:30 | 97.36 | 81.15
2017-08-22 08:00 | 93.68 | 77.86
2017-08-22 08:30 | 91.74 | 74.74
2017-08-22 09:00 | 95.61 | 80.16
2017-08-22 09:30 | 96.82 | 80.66
2017-08-22 10:00 | 94.89 | 78.11
2017-08-22 10:30 | 96.41 | 79.38
2017-08-22 11:00 | 94.98 | 77.69
2017-08-22 11:30 | 99.89 | 82.64
2017-08-22 12:00 | 100.88 | 83.89
2017-08-22 12:30 | 100.8 | 83.69
2017-08-22 13:00 | 106.49 | 89.03
2017-08-22 13:30 | 100.1 | 83.23
2017-08-22 14:00 | 94.08 | 75.69
2017-08-22 14:30 | 96.59 | 78.48
2017-08-22 15:00 | 97.02 | 79.65
2017-08-22 15:30 | 100.14 | 82.64
2017-08-22 16:00 | 96.91 | 77.73
2017-08-22 16:30 | 104.61 | 86.71
2017-08-22 17:00 | 101.46 | 83.77
2017-08-22 17:30 | 102.19 | 84.14
2017-08-22 18:00 | 105.7 | 87.52
2017-08-22 18:30 | 106.68 | 87.68
2017-08-22 19:00 | 115.63 | 98.48
2017-08-22 19:30 | 117.06 | 98.87
2017-08-22 20:00 | 118.88 | 101.26
2017-08-22 20:30 | 121.32 | 104.18
2017-08-22 21:00 | 119.02 | 100.44
2017-08-22 21:30 | 120.28 | 100.92
2017-08-22 22:00 | 118.75 | 101.01
2017-08-22 22:30 | 114.93 | 97.41
2017-08-22 23:00 | 108.34 | 89.78
2017-08-22 23:30 | 110.83 | 91.55
2017-08-23 | 106.04 | 87.08
2017-08-23 00:30 | 110.04 | 92.72
2017-08-23 01:00 | 105 | 87.73
2017-08-23 01:30 | 115.14 | 99.44
2017-08-23 02:00 | 118.13 | 101.74
2017-08-23 02:30 | 110.68 | 93.24
2017-08-23 03:00 | 105.68 | 88.05
2017-08-23 03:30 | 106.03 | 88.97
2017-08-23 04:00 | 106.65 | 89.18
2017-08-23 04:30 | 111.69 | 93.99
2017-08-23 05:00 | 108.18 | 90.75
2017-08-23 05:30 | 106.43 | 88.83
2017-08-23 06:00 | 109.5 | 91.67
2017-08-23 06:30 | 97.9 | 79.81
2017-08-23 07:00 | 109.69 | 92.92
2017-08-23 07:30 | 110.87 | 94
2017-08-23 08:00 | 103.76 | 86.43
2017-08-23 08:30 | 106.78 | 90.18
2017-08-23 09:00 | 106.26 | 89.48
2017-08-23 09:30 | 104.4 | 87.44
2017-08-23 10:00 | 107.5 | 91.59
2017-08-23 10:30 | 100.88 | 83.98
2017-08-23 11:00 | 103.78 | 88.38
2017-08-23 11:30 | 104.53 | 88.8
2017-08-23 12:00 | 101.39 | 83.69
2017-08-23 12:30 | 101.5 | 84.34
2017-08-23 13:00 | 99.51 | 82.94
2017-08-23 13:30 | 100.09 | 85.55
2017-08-23 14:00 | 96.57 | 80.64
2017-08-23 14:30 | 92.36 | 76.33
2017-08-23 15:00 | 94.51 | 78.5
2017-08-23 15:30 | 87.77 | 72.6
2017-08-23 16:00 | 84.12 | 67.8
2017-08-23 16:30 | 95.59 | 77.82
2017-08-23 17:00 | 105.09 | 89.11
2017-08-23 17:30 | 109.48 | 92.11
2017-08-23 18:00 | 108.16 | 90.35
2017-08-23 18:30 | 94.75 | 76.19
2017-08-23 19:00 | 110.64 | 92.03
2017-08-23 19:30 | 116.8 | 96.93
2017-08-23 20:00 | 112.92 | 92.16
2017-08-23 20:30 | 117.74 | 97.97
2017-08-23 21:00 | 116.1 | 96.91
2017-08-23 21:30 | 127.43 | 109.8
2017-08-23 22:00 | 120.07 | 102.08
2017-08-23 22:30 | 117.32 | 98.05
2017-08-23 23:00 | 120.83 | 101.2
2017-08-23 23:30 | 120.79 | 102.48
2017-08-24 | 125.09 | 107.11
2017-08-24 00:30 | 109.67 | 91.01
2017-08-24 01:00 | 103.69 | 85.23
2017-08-24 01:30 | 112.19 | 95.06
2017-08-24 02:00 | 112.3 | 92.94
2017-08-24 02:30 | 116.8 | 97.81
2017-08-24 03:00 | 115.46 | 97.04
2017-08-24 03:30 | 114.69 | 96.73
2017-08-24 04:00 | 116.71 | 98.34
2017-08-24 04:30 | 120.57 | 103.32
2017-08-24 05:00 | 117.14 | 98.82
2017-08-24 05:30 | 122.18 | 103.22
2017-08-24 06:00 | 120.22 | 103.05
2017-08-24 06:30 | 111.27 | 93.61
2017-08-24 07:00 | 110.01 | 92.4
2017-08-24 07:30 | 110 | 91.52
2017-08-24 08:00 | 107.65 | 89.3
2017-08-24 08:30 | 108.9 | 92.75
2017-08-24 09:00 | 99.82 | 83.32
2017-08-24 09:30 | 120.33 | 103.89
2017-08-24 10:00 | 116.05 | 100.11
2017-08-24 10:30 | 121.39 | 102.87
2017-08-24 11:00 | 118.94 | 101.27
2017-08-24 11:30 | 103.01 | 85.9
2017-08-24 12:00 | 102.15 | 84.73
2017-08-24 12:30 | 106.97 | 90.1
2017-08-24 13:00 | 105.49 | 87.42
2017-08-24 13:30 | 109.17 | 91.53
2017-08-24 14:00 | 113.44 | 96.48
2017-08-24 14:30 | 102.02 | 85.11
2017-08-24 15:00 | 103.69 | 85.84
2017-08-24 15:30 | 101.67 | 83.74
2017-08-24 16:00 | 96.19 | 77.7
2017-08-24 16:30 | 99.34 | 81.18
2017-08-24 17:00 | 101.57 | 83.65
2017-08-24 17:30 | 102.41 | 84.25
2017-08-24 18:00 | 118.18 | 99.99
2017-08-24 18:30 | 112.06 | 91.92
2017-08-24 19:00 | 119.4 | 99.75
2017-08-24 19:30 | 120.31 | 100.53
2017-08-24 20:00 | 120.86 | 101.03
2017-08-24 20:30 | 114.04 | 94.55
2017-08-24 21:00 | 120.55 | 101.98
2017-08-24 21:30 | 117.04 | 97.88
2017-08-24 22:00 | 112.94 | 94.95
2017-08-24 22:30 | 112.3 | 93.63
2017-08-24 23:00 | 108.23 | 88.53
2017-08-24 23:30 | 111.87 | 91.97
2017-08-25 | 110.52 | 91.64
2017-08-25 00:30 | 114.87 | 95.48
2017-08-25 01:00 | 114.27 | 96.23
2017-08-25 01:30 | 117.78 | 100.84
2017-08-25 02:00 | 122.12 | 105.84
2017-08-25 02:30 | 125.39 | 109.47
2017-08-25 03:00 | 109.86 | 93.33
2017-08-25 03:30 | 107.02 | 90.35
2017-08-25 04:00 | 111.17 | 95.25
2017-08-25 04:30 | 114.5 | 98.44
2017-08-25 05:00 | 114.24 | 99.04
2017-08-25 05:30 | 115.08 | 99.5
2017-08-25 06:00 | 112.14 | 96.89
2017-08-25 06:30 | 112.06 | 95.87
2017-08-25 07:00 | 123.15 | 107.78
2017-08-25 07:30 | 100.35 | 82.64
2017-08-25 08:00 | 95.68 | 76.34
2017-08-25 08:30 | 99.57 | 81.07
2017-08-25 09:00 | 99.61 | 83.37
2017-08-25 09:30 | 93.1 | 77.28
2017-08-25 10:00 | 94.48 | 79.41
2017-08-25 10:30 | 100.46 | 85.41
2017-08-25 11:00 | 105.26 | 90.01
2017-08-25 11:30 | 100.35 | 82.71
2017-08-25 12:00 | 104.48 | 88.34
2017-08-25 12:30 | 105.06 | 89.14
2017-08-25 13:00 | 98.28 | 81.52
2017-08-25 13:30 | 101.78 | 86.01
2017-08-25 14:00 | 115.22 | 100.26
2017-08-25 14:30 | 104.02 | 88.81
2017-08-25 15:00 | 97.81 | 84.15
2017-08-25 15:30 | 94.64 | 80.63
2017-08-25 16:00 | 95.78 | 81.1
2017-08-25 16:30 | 99.81 | 85.24
2017-08-25 17:00 | 104.98 | 90.82
2017-08-25 17:30 | 110.84 | 96
2017-08-25 18:00 | 109.63 | 93.94
2017-08-25 18:30 | 102.06 | 84.18
2017-08-25 19:00 | 110.88 | 95.01
2017-08-25 19:30 | 110.74 | 95.48
2017-08-25 20:00 | 111.22 | 96.64
2017-08-25 20:30 | 114 | 98.96
2017-08-25 21:00 | 117.96 | 103.26
2017-08-25 21:30 | 108.83 | 92.51
2017-08-25 22:00 | 110.54 | 95.44
2017-08-25 22:30 | 113.75 | 97.58
2017-08-25 23:00 | 104.47 | 87.57
2017-08-25 23:30 | 105.25 | 88.6
2017-08-26 | 103.09 | 86.77
2017-08-26 00:30 | 104.23 | 88.4
2017-08-26 01:00 | 107.96 | 91.48
2017-08-26 01:30 | 111.98 | 96.51
2017-08-26 02:00 | 117.68 | 101.76
2017-08-26 02:30 | 112.35 | 96.16
2017-08-26 03:00 | 112.05 | 95.65
2017-08-26 03:30 | 111.06 | 95.07
2017-08-26 04:00 | 115.53 | 99.79
2017-08-26 04:30 | 114.65 | 95.64
2017-08-26 05:00 | 115.6 | 96.66
2017-08-26 05:30 | 110.58 | 90.4
2017-08-26 06:00 | 110.08 | 91.23
2017-08-26 06:30 | 106.7 | 85.03
2017-08-26 07:00 | 108.44 | 88.73
2017-08-26 07:30 | 109.21 | 90.63
2017-08-26 08:00 | 105.46 | 87.52
2017-08-26 08:30 | 100.45 | 81.53
2017-08-26 09:00 | 99.04 | 79.94
2017-08-26 09:30 | 98.1 | 79.86
2017-08-26 10:00 | 92.57 | 78.16
2017-08-26 10:30 | 87.27 | 73.42
2017-08-26 11:00 | 86.65 | 73.66
2017-08-26 11:30 | 84.73 | 70.95
2017-08-26 12:00 | 92.52 | 78.14
2017-08-26 12:30 | 86.93 | 72.73
2017-08-26 13:00 | 87.9 | 73.29
2017-08-26 13:30 | 93.92 | 80.4
2017-08-26 14:00 | 88.15 | 74.56
2017-08-26 14:30 | 87.92 | 73.44
2017-08-26 15:00 | 85.75 | 70.22
2017-08-26 15:30 | 91.7 | 74.86
2017-08-26 16:00 | 93.87 | 75.98
2017-08-26 16:30 | 99.23 | 81.54
2017-08-26 17:00 | 96.19 | 77.26
2017-08-26 17:30 | 97.82 | 79.66
2017-08-26 18:00 | 98.85 | 80.92
2017-08-26 18:30 | 94.67 | 74.41
2017-08-26 19:00 | 103.72 | 85.72
2017-08-26 19:30 | 101.87 | 81.69
2017-08-26 20:00 | 109.95 | 89.35
2017-08-26 20:30 | 111.76 | 90.38
2017-08-26 21:00 | 106.43 | 86.01
2017-08-26 21:30 | 106.62 | 86.35
2017-08-26 22:00 | 115.48 | 96.1
2017-08-26 22:30 | 118.65 | 98.71
2017-08-26 23:00 | 119.25 | 98.71
2017-08-26 23:30 | 118.61 | 98.02
2017-08-27 | 121.23 | 100.98
2017-08-27 00:30 | 121.38 | 101.89
2017-08-27 01:00 | 116.83 | 98.12
2017-08-27 01:30 | 112.9 | 94.35
2017-08-27 02:00 | 112.41 | 93.64
2017-08-27 02:30 | 114.58 | 96.21
2017-08-27 03:00 | 115.35 | 96.19
2017-08-27 03:30 | 115.52 | 96.68
2017-08-27 04:00 | 116.33 | 96.25
2017-08-27 04:30 | 110.26 | 90.85
2017-08-27 05:00 | 110.92 | 93.77
2017-08-27 05:30 | 106.55 | 87.53
2017-08-27 06:00 | 118.2 | 100.77
2017-08-27 06:30 | 111.08 | 93.23
2017-08-27 07:00 | 106.22 | 88.97
2017-08-27 07:30 | 110.6 | 93.89
2017-08-27 08:00 | 104.2 | 87.83
2017-08-27 08:30 | 108.43 | 89.79
2017-08-27 09:00 | 111.61 | 93.91
2017-08-27 09:30 | 113.66 | 94.18
2017-08-27 10:00 | 111.87 | 92.7
2017-08-27 10:30 | 118.75 | 100.32
2017-08-27 11:00 | 116.61 | 97.96
2017-08-27 11:30 | 112.66 | 92.8
2017-08-27 12:00 | 109.18 | 91.6
2017-08-27 12:30 | 109.75 | 92.12
2017-08-27 13:00 | 112.59 | 95.16
2017-08-27 13:30 | 126.36 | 107.24
2017-08-27 14:00 | 115.33 | 95.76
2017-08-27 14:30 | 113.45 | 94.11
2017-08-27 15:00 | 112.9 | 93.31
2017-08-27 15:30 | 116.94 | 96.4
2017-08-27 16:00 | 118.86 | 99.52
2017-08-27 16:30 | 108.71 | 91.25
2017-08-27 17:00 | 105.49 | 85.73
2017-08-27 17:30 | 118.01 | 98.4
2017-08-27 18:00 | 117.94 | 97.35
2017-08-27 18:30 | 113.9 | 94.17
2017-08-27 19:00 | 115.83 | 98.96
2017-08-27 19:30 | 120.08 | 103.6
2017-08-27 20:00 | 120.42 | 102.33
2017-08-27 20:30 | 111.17 | 92.29
2017-08-27 21:00 | 115.63 | 97.04
2017-08-27 21:30 | 114.61 | 95.74
2017-08-27 22:00 | 112.33 | 94.18
2017-08-27 22:30 | 111.45 | 93.8
2017-08-27 23:00 | 113.05 | 96.15
2017-08-27 23:30 | 111.34 | 94.21
2017-08-28 | 115.28 | 98.28
2017-08-28 00:30 | 104.87 | 87.74
2017-08-28 01:00 | 114.99 | 97.04
2017-08-28 01:30 | 111.04 | 93.79
2017-08-28 02:00 | 108.08 | 90.24
2017-08-28 02:30 | 111.36 | 94.69
2017-08-28 03:00 | 100.66 | 82.69
2017-08-28 03:30 | 111.48 | 93.76
2017-08-28 04:00 | 114.28 | 96.99
2017-08-28 04:30 | 112.58 | 95.43
2017-08-28 05:00 | 108.75 | 92
2017-08-28 05:30 | 110.29 | 92.93
2017-08-28 06:00 | 113.27 | 94.75
2017-08-28 06:30 | 109.09 | 89.99
2017-08-28 07:00 | 109.69 | 91.4
2017-08-28 07:30 | 108.78 | 90.36
2017-08-28 08:00 | 110.85 | 92.51
2017-08-28 08:30 | 118.98 | 100.8
2017-08-28 09:00 | 109.38 | 91.78
2017-08-28 09:30 | 100.26 | 83.21
2017-08-28 10:00 | 96.65 | 79.37
2017-08-28 10:30 | 105.31 | 89.73
2017-08-28 11:00 | 105.05 | 89.27
2017-08-28 11:30 | 105.67 | 88.24
2017-08-28 12:00 | 107.19 | 90.91
2017-08-28 12:30 | 109.52 | 92.67
2017-08-28 13:00 | 110.33 | 95.27
2017-08-28 13:30 | 109.05 | 93.42
2017-08-28 14:00 | 111.19 | 92.86
2017-08-28 14:30 | 115.76 | 97.93
2017-08-28 15:00 | 110.76 | 93.09
2017-08-28 15:30 | 105.6 | 85.7
2017-08-28 16:00 | 111.61 | 94.46
2017-08-28 16:30 | 113.83 | 96.58
2017-08-28 17:00 | 109.27 | 92.25
2017-08-28 17:30 | 118.13 | 100.08
2017-08-28 18:00 | 116.72 | 98.41
2017-08-28 18:30 | 118.87 | 100.67
2017-08-28 19:00 | 129.92 | 111.02
2017-08-28 19:30 | 126.89 | 107.77
2017-08-28 20:00 | 123.99 | 105.26
2017-08-28 20:30 | 126.02 | 106.65
2017-08-28 21:00 | 119.74 | 102.04
2017-08-28 21:30 | 114.5 | 97.07
2017-08-28 22:00 | 116.27 | 99.38
2017-08-28 22:30 | 122.25 | 104.29
2017-08-28 23:00 | 113.63 | 96.04
2017-08-28 23:30 | 115.55 | 99.27
2017-08-29 | 117.9 | 101.67
2017-08-29 00:30 | 122.5 | 105.5
2017-08-29 01:00 | 117.31 | 101.09
2017-08-29 01:30 | 108.89 | 92
2017-08-29 02:00 | 113.13 | 96.71
2017-08-29 02:30 | 111.32 | 93.77
2017-08-29 03:00 | 111.28 | 93.72
2017-08-29 03:30 | 116.89 | 100.93
2017-08-29 04:00 | 118.44 | 102.52
2017-08-29 04:30 | 120.66 | 104.15
2017-08-29 05:00 | 116.47 | 99.74
2017-08-29 05:30 | 116.56 | 99.53
2017-08-29 06:00 | 108.88 | 93.24
2017-08-29 06:30 | 104.25 | 87.16
2017-08-29 07:00 | 112.23 | 96.51
2017-08-29 07:30 | 111.72 | 95.76
2017-08-29 08:00 | 111.18 | 94.61
2017-08-29 08:30 | 102.62 | 86.09
2017-08-29 09:00 | 96.15 | 81.15
2017-08-29 09:30 | 100.32 | 87.13
2017-08-29 10:00 | 90.02 | 75.99
2017-08-29 10:30 | 97.4 | 81.01
2017-08-29 11:00 | 99 | 81.75
2017-08-29 11:30 | 102.65 | 85.23
2017-08-29 12:00 | 108.58 | 92.54
2017-08-29 12:30 | 111.9 | 97.29
2017-08-29 13:00 | 111.7 | 96.58
2017-08-29 13:30 | 120.79 | 103.9
2017-08-29 14:00 | 121.9 | 102.21
2017-08-29 14:30 | 116.04 | 94.13
2017-08-29 15:00 | 116.34 | 95.25
2017-08-29 15:30 | 117.49 | 95.33
2017-08-29 16:00 | 122.03 | 100.82
2017-08-29 16:30 | 126.87 | 107.11
2017-08-29 17:00 | 117.83 | 96.76
2017-08-29 17:30 | 121.35 | 100.24
2017-08-29 18:00 | 118.56 | 96.72
2017-08-29 18:30 | 112.55 | 90.59
2017-08-29 19:00 | 124.76 | 104.26
2017-08-29 19:30 | 123.35 | 101.22
2017-08-29 20:00 | 127.07 | 104.38
2017-08-29 20:30 | 133.36 | 111.22
2017-08-29 21:00 | 124.69 | 100.55
2017-08-29 21:30 | 125.79 | 102.37
2017-08-29 22:00 | 129.43 | 106.57
2017-08-29 22:30 | 124.58 | 100.41
2017-08-29 23:00 | 121.35 | 98.13
2017-08-29 23:30 | 123.33 | 101.16
2017-08-30 | 122.05 | 100.53
2017-08-30 00:30 | 122.74 | 100.36
2017-08-30 01:00 | 119.08 | 96.77
2017-08-30 01:30 | 119.06 | 95.71
2017-08-30 02:00 | 116.42 | 93.02
2017-08-30 02:30 | 112.12 | 89.77
2017-08-30 03:00 | 116.27 | 95.36
2017-08-30 03:30 | 121.1 | 99.34
2017-08-30 04:00 | 116.41 | 94.53
2017-08-30 04:30 | 119.7 | 96.55
2017-08-30 05:00 | 115.77 | 93.44
2017-08-30 05:30 | 121.89 | 100.34
2017-08-30 06:00 | 118.85 | 96.88
2017-08-30 06:30 | 111.17 | 86.9
2017-08-30 07:00 | 108.79 | 87.29
2017-08-30 07:30 | 114.49 | 94.63
2017-08-30 08:00 | 113.73 | 93.78
2017-08-30 08:30 | 104.33 | 83.23
2017-08-30 09:00 | 111.09 | 89.79
2017-08-30 09:30 | 114.77 | 93.2
2017-08-30 10:00 | 119.09 | 97.7
2017-08-30 10:30 | 115.46 | 94.19
2017-08-30 11:00 | 119.73 | 98.07
2017-08-30 11:30 | 119.11 | 95.55
2017-08-30 12:00 | 112.5 | 87.54
2017-08-30 12:30 | 110.03 | 85.85
2017-08-30 13:00 | 117.36 | 93.64
2017-08-30 13:30 | 113.58 | 88.6
2017-08-30 14:00 | 115.85 | 92.31
2017-08-30 14:30 | 112.92 | 89.29
2017-08-30 15:00 | 123.79 | 101.11
2017-08-30 15:30 | 115.23 | 92.49
2017-08-30 16:00 | 113.51 | 90.61
2017-08-30 16:30 | 114.74 | 92.16
2017-08-30 17:00 | 110.94 | 88.46
2017-08-30 17:30 | 110.41 | 86.66
2017-08-30 18:00 | 118.25 | 95.1
2017-08-30 18:30 | 113.5 | 88.39
2017-08-30 19:00 | 124.33 | 99.37
2017-08-30 19:30 | 119.09 | 94.6
2017-08-30 20:00 | 126.16 | 101.22
2017-08-30 20:30 | 117.03 | 91.83
2017-08-30 21:00 | 118.82 | 93.77
2017-08-30 21:30 | 120.46 | 95.82
2017-08-30 22:00 | 118.96 | 94.46
2017-08-30 22:30 | 118.24 | 93.13
2017-08-30 23:00 | 117.26 | 93.3
2017-08-30 23:30 | 124.06 | 100.68
2017-08-31 | 116.79 | 93.06
2017-08-31 00:30 | 117.69 | 92.74
2017-08-31 01:00 | 117.22 | 92.55
2017-08-31 01:30 | 108.87 | 85.43
2017-08-31 02:00 | 106.9 | 84.07
2017-08-31 02:30 | 109.15 | 87.06
2017-08-31 03:00 | 109.69 | 89.09
2017-08-31 03:30 | 105.31 | 83.39
2017-08-31 04:00 | 106.07 | 86.04
2017-08-31 04:30 | 108.19 | 86.76
2017-08-31 05:00 | 104.91 | 83.5
2017-08-31 05:30 | 108.04 | 87.15
2017-08-31 06:00 | 111.58 | 91.73
2017-08-31 06:30 | 100.97 | 79.65
2017-08-31 07:00 | 104.42 | 84.91
2017-08-31 07:30 | 111.03 | 91.58
2017-08-31 08:00 | 112.02 | 91.89
2017-08-31 08:30 | 115.44 | 96.14
2017-08-31 09:00 | 117.9 | 100.25
2017-08-31 09:30 | 108.94 | 90.14
2017-08-31 10:00 | 117.5 | 98.42
2017-08-31 10:30 | 110.37 | 91.97
2017-08-31 11:00 | 111.79 | 92.71
2017-08-31 11:30 | 118.49 | 99.24
2017-08-31 12:00 | 107.38 | 87.63
2017-08-31 12:30 | 111.87 | 90.76
2017-08-31 13:00 | 109.65 | 90.51
2017-08-31 13:30 | 105.32 | 88.75
2017-08-31 14:00 | 97.06 | 82.93
2017-08-31 14:30 | 97.46 | 83.5
2017-08-31 15:00 | 94.44 | 82.25
2017-08-31 15:30 | 94.4 | 79.88
2017-08-31 16:00 | 99.95 | 84.95
2017-08-31 16:30 | 94.09 | 79.54
2017-08-31 17:00 | 94.8 | 79.94
2017-08-31 17:30 | 98.6 | 83.46
2017-08-31 18:00 | 98.77 | 81.87
2017-08-31 18:30 | 105.31 | 87.06
2017-08-31 19:00 | 116.78 | 99.4
2017-08-31 19:30 | 121.61 | 102.73
2017-08-31 20:00 | 125.04 | 105.53
2017-08-31 20:30 | 126.27 | 108.03
2017-08-31 21:00 | 129.25 | 112.78
2017-08-31 21:30 | 128.63 | 110.01
2017-08-31 22:00 | 126.54 | 107.7
2017-08-31 22:30 | 120.91 | 101.4
2017-08-31 23:00 | 117.85 | 98.31
2017-08-31 23:30 | 116.7 | 97.08
2017-09-01 | 117.16 | 99.12
2017-09-01 00:30 | 118.49 | 101.38
2017-09-01 01:00 | 114.7 | 96.78
2017-09-01 01:30 | 110.87 | 91.43
2017-09-01 02:00 | 114.53 | 96.58
2017-09-01 02:30 | 107.9 | 88.74
2017-09-01 03:00 | 115.44 | 96.85
2017-09-01 03:30 | 111.57 | 93.31
2017-09-01 04:00 | 102.74 | 88.36
2017-09-01 04:30 | 104.24 | 90.96
2017-09-01 05:00 | 117.53 | 101.43
2017-09-01 05:30 | 116.93 | 100.65
2017-09-01 06:00 | 115.04 | 98.5
2017-09-01 06:30 | 110.8 | 92.64
2017-09-01 07:00 | 106.23 | 91.4
2017-09-01 07:30 | 116.57 | 101.65
2017-09-01 08:00 | 113.03 | 97.74
2017-09-01 08:30 | 108.35 | 93.74
2017-09-01 09:00 | 108.74 | 93.23
2017-09-01 09:30 | 102.38 | 87.52
2017-09-01 10:00 | 110 | 93.21
2017-09-01 10:30 | 109.33 | 92.42
2017-09-01 11:00 | 109.6 | 92.43
2017-09-01 11:30 | 105.2 | 88.14
2017-09-01 12:00 | 105.17 | 88.01
2017-09-01 12:30 | 109.63 | 93.73
2017-09-01 13:00 | 115.16 | 97.29
2017-09-01 13:30 | 108.94 | 90.79
2017-09-01 14:00 | 111.27 | 91.76
2017-09-01 14:30 | 119.87 | 101.04
2017-09-01 15:00 | 113.01 | 94.28
2017-09-01 15:30 | 113.79 | 94.64
2017-09-01 16:00 | 109.83 | 90.65
2017-09-01 16:30 | 113.16 | 93.05
2017-09-01 17:00 | 112.55 | 93.48
2017-09-01 17:30 | 114.52 | 95.85
2017-09-01 18:00 | 117.37 | 99.67
2017-09-01 18:30 | 117.81 | 99.05
2017-09-01 19:00 | 121.12 | 101.87
2017-09-01 19:30 | 122.08 | 102.45
2017-09-01 20:00 | 126.61 | 105.89
2017-09-01 20:30 | 115.72 | 96.13
2017-09-01 21:00 | 113.45 | 95.93
2017-09-01 21:30 | 113.84 | 97.48
2017-09-01 22:00 | 120.42 | 102.47
2017-09-01 22:30 | 117.53 | 100.06
2017-09-01 23:00 | 123.55 | 104.41
2017-09-01 23:30 | 116.3 | 97.85
2017-09-02 | 115.78 | 98.3
2017-09-02 00:30 | 118.57 | 102.67
2017-09-02 01:00 | 117.74 | 100.37
2017-09-02 01:30 | 116.46 | 99.24
2017-09-02 02:00 | 114.64 | 97.52
2017-09-02 02:30 | 118.29 | 100.93
2017-09-02 03:00 | 114.23 | 96.13
2017-09-02 03:30 | 111.92 | 94.62
2017-09-02 04:00 | 109.64 | 92.91
2017-09-02 04:30 | 105.26 | 89.57
2017-09-02 05:00 | 110.16 | 94.93
2017-09-02 05:30 | 110.26 | 93.96
2017-09-02 06:00 | 111.25 | 94.98
2017-09-02 06:30 | 105.78 | 86.93
2017-09-02 07:00 | 108.18 | 91.77
2017-09-02 07:30 | 112.09 | 95.88
2017-09-02 08:00 | 112 | 97.2
2017-09-02 08:30 | 106.43 | 90.95
2017-09-02 09:00 | 99.43 | 82.35
2017-09-02 09:30 | 96.55 | 82.16
2017-09-02 10:00 | 96.07 | 82.36
2017-09-02 10:30 | 97.47 | 83.59
2017-09-02 11:00 | 96.32 | 82.98
2017-09-02 11:30 | 97.11 | 83.02
2017-09-02 12:00 | 93.65 | 79.27
2017-09-02 12:30 | 92.76 | 78.73
2017-09-02 13:00 | 98.94 | 84.91
2017-09-02 13:30 | 100.18 | 86.28
2017-09-02 14:00 | 99.47 | 84.75
2017-09-02 14:30 | 95.64 | 81.63
2017-09-02 15:00 | 99.01 | 86.71
2017-09-02 15:30 | 98.36 | 85.38
2017-09-02 16:00 | 91.04 | 77.91
2017-09-02 16:30 | 93.96 | 79.8
2017-09-02 17:00 | 97.77 | 83.14
2017-09-02 17:30 | 109.53 | 95.34
2017-09-02 18:00 | 111.99 | 95.6
2017-09-02 18:30 | 105.67 | 87.71
2017-09-02 19:00 | 114.73 | 97.74
2017-09-02 19:30 | 122.13 | 103.74
2017-09-02 20:00 | 118.3 | 98.73
2017-09-02 20:30 | 124.38 | 104.93
2017-09-02 21:00 | 118.87 | 99.54
2017-09-02 21:30 | 117.05 | 97.78
2017-09-02 22:00 | 124.51 | 106.05
2017-09-02 22:30 | 119.78 | 101.9
2017-09-02 23:00 | 120.26 | 102.67
2017-09-02 23:30 | 113.9 | 97.16
2017-09-03 | 115.17 | 97.5
2017-09-03 00:30 | 119.22 | 103.02
2017-09-03 01:00 | 118.49 | 103.48
2017-09-03 01:30 | 122.34 | 106.23
2017-09-03 02:00 | 124 | 106.83
2017-09-03 02:30 | 119.61 | 102.21
2017-09-03 03:00 | 119.1 | 103.12
2017-09-03 03:30 | 114.77 | 98.14
2017-09-03 04:00 | 112.07 | 95.87
2017-09-03 04:30 | 121.06 | 105.43
2017-09-03 05:00 | 117.6 | 101.78
2017-09-03 05:30 | 114.24 | 97.99
2017-09-03 06:00 | 121.47 | 105.67
2017-09-03 06:30 | 109.42 | 91.58
2017-09-03 07:00 | 110.18 | 93.95
2017-09-03 07:30 | 111.11 | 93.66
2017-09-03 08:00 | 112.15 | 94.95
2017-09-03 08:30 | 114.01 | 96.76
2017-09-03 09:00 | 116.52 | 98.15
2017-09-03 09:30 | 116.8 | 98.21
2017-09-03 10:00 | 117.14 | 99.49
2017-09-03 10:30 | 107.37 | 89.91
2017-09-03 11:00 | 106.1 | 88.96
2017-09-03 11:30 | 109.57 | 90.8
2017-09-03 12:00 | 110.7 | 91.64
2017-09-03 12:30 | 114.4 | 96.46
2017-09-03 13:00 | 118.77 | 100.67
2017-09-03 13:30 | 114.87 | 96.47
2017-09-03 14:00 | 115.63 | 96.65
2017-09-03 14:30 | 114.89 | 94.07
2017-09-03 15:00 | 114.18 | 93.88
2017-09-03 15:30 | 120.03 | 101.16
2017-09-03 16:00 | 115.34 | 94.78
2017-09-03 16:30 | 122.57 | 102.4
2017-09-03 17:00 | 125.76 | 106.82
2017-09-03 17:30 | 121.76 | 102.4
2017-09-03 18:00 | 128.36 | 108.73
2017-09-03 18:30 | 118.47 | 97.97
2017-09-03 19:00 | 122.01 | 103.24
2017-09-03 19:30 | 129.09 | 110.11
2017-09-03 20:00 | 124 | 104.01
2017-09-03 20:30 | 125.77 | 107.52
2017-09-03 21:00 | 127.37 | 108.19
2017-09-03 21:30 | 119.29 | 99.32
2017-09-03 22:00 | 109.92 | 88.96
2017-09-03 22:30 | 109.89 | 90.94
2017-09-03 23:00 | 110.74 | 91.56
2017-09-03 23:30 | 113.8 | 93.73
2017-09-04 | 111.58 | 90.7
2017-09-04 00:30 | 113.73 | 94.75
2017-09-04 01:00 | 122.22 | 103.5
2017-09-04 01:30 | 117.16 | 97.8
2017-09-04 02:00 | 126.8 | 109.38
2017-09-04 02:30 | 123.3 | 106.56
2017-09-04 03:00 | 117.51 | 101.21
2017-09-04 03:30 | 119.83 | 102.17
2017-09-04 04:00 | 125.63 | 107.84
2017-09-04 04:30 | 112.42 | 94.05
2017-09-04 05:00 | 127.44 | 110.23
2017-09-04 05:30 | 119.39 | 102.16
2017-09-04 06:00 | 118.3 | 100.59
2017-09-04 06:30 | 117.96 | 98.92
2017-09-04 07:00 | 110.72 | 90.22
2017-09-04 07:30 | 112.1 | 91.9
2017-09-04 08:00 | 108.62 | 88.21
2017-09-04 08:30 | 107.2 | 86.77
2017-09-04 09:00 | 110.5 | 92.13
2017-09-04 09:30 | 110.2 | 94.3
2017-09-04 10:00 | 106.98 | 90.85
2017-09-04 10:30 | 105.27 | 89.36
2017-09-04 11:00 | 104.82 | 89.38
2017-09-04 11:30 | 106.27 | 91.19
2017-09-04 12:00 | 115.84 | 100.12
2017-09-04 12:30 | 105.93 | 89.43
2017-09-04 13:00 | 106.83 | 90.21
2017-09-04 13:30 | 108.07 | 90.76
2017-09-04 14:00 | 100.69 | 82.82
2017-09-04 14:30 | 103.64 | 87.42
2017-09-04 15:00 | 101.65 | 83.92
2017-09-04 15:30 | 106.91 | 90.11
2017-09-04 16:00 | 105.02 | 89.07
2017-09-04 16:30 | 102.18 | 86.19
2017-09-04 17:00 | 112.42 | 95.94
2017-09-04 17:30 | 106.64 | 90.59
2017-09-04 18:00 | 116.12 | 100.32
2017-09-04 18:30 | 103.86 | 86.79
2017-09-04 19:00 | 110.72 | 92.83
2017-09-04 19:30 | 109.26 | 91.38
2017-09-04 20:00 | 116.89 | 96.7
2017-09-04 20:30 | 118.22 | 97.87
2017-09-04 21:00 | 119.43 | 99.3
2017-09-04 21:30 | 114.71 | 93.9
2017-09-04 22:00 | 119.39 | 98.82
2017-09-04 22:30 | 118.54 | 97.36
2017-09-04 23:00 | 121.77 | 101.72
2017-09-04 23:30 | 116.98 | 97.52
2017-09-05 | 113.07 | 94.02
2017-09-05 00:30 | 114.49 | 95.17
2017-09-05 01:00 | 106.38 | 86.18
2017-09-05 01:30 | 108.16 | 88.41
2017-09-05 02:00 | 108.45 | 89.82
2017-09-05 02:30 | 110.23 | 91.81
2017-09-05 03:00 | 111.75 | 92.67
2017-09-05 03:30 | 115.25 | 96.52
2017-09-05 04:00 | 119.54 | 102.57
2017-09-05 04:30 | 118.12 | 101.46
2017-09-05 05:00 | 115.13 | 97.67
2017-09-05 05:30 | 110.3 | 93.73
2017-09-05 06:00 | 109.73 | 93.2
2017-09-05 06:30 | 108.32 | 90.22
2017-09-05 07:00 | 110.1 | 93.12
2017-09-05 07:30 | 107.85 | 91.86
2017-09-05 08:00 | 98.81 | 83.1
2017-09-05 08:30 | 94.95 | 81.24
2017-09-05 09:00 | 95.66 | 80.57
2017-09-05 09:30 | 95.01 | 80.21
2017-09-05 10:00 | 102.97 | 89.55
2017-09-05 10:30 | 97.49 | 84.38
2017-09-05 11:00 | 106.04 | 91.83
2017-09-05 11:30 | 105.62 | 91.98
2017-09-05 12:00 | 96.1 | 81.11
2017-09-05 12:30 | 94.14 | 81.39
2017-09-05 13:00 | 85.19 | 71.22
2017-09-05 13:30 | 94.63 | 81.54
2017-09-05 14:00 | 99.85 | 86.35
2017-09-05 14:30 | 99.47 | 83.65
2017-09-05 15:00 | 99.51 | 83.37
2017-09-05 15:30 | 101.43 | 85.53
2017-09-05 16:00 | 105.66 | 89.15
2017-09-05 16:30 | 104.64 | 88.49
2017-09-05 17:00 | 100.79 | 85.03
2017-09-05 17:30 | 94.63 | 79.13
2017-09-05 18:00 | 98.66 | 82.73
2017-09-05 18:30 | 96.78 | 79.33
2017-09-05 19:00 | 106.51 | 89.31
2017-09-05 19:30 | 111.27 | 95.58
2017-09-05 20:00 | 104.16 | 86.86
2017-09-05 20:30 | 109.21 | 93.38
2017-09-05 21:00 | 107.65 | 91.63
2017-09-05 21:30 | 105.87 | 89.77
2017-09-05 22:00 | 114.51 | 99.61
2017-09-05 22:30 | 110.15 | 94.99
2017-09-05 23:00 | 102.56 | 87.62
2017-09-05 23:30 | 104.95 | 89.78
2017-09-06 | 97.8 | 83.13
2017-09-06 00:30 | 107.78 | 92.42
2017-09-06 01:00 | 112.69 | 96.93
2017-09-06 01:30 | 101.08 | 85.45
2017-09-06 02:00 | 108.66 | 93.62
2017-09-06 02:30 | 111.66 | 96.19
2017-09-06 03:00 | 109.65 | 93.11
2017-09-06 03:30 | 111.05 | 95.22
2017-09-06 04:00 | 107.72 | 92.39
2017-09-06 04:30 | 108.57 | 92.94
2017-09-06 05:00 | 111.9 | 96.66
2017-09-06 05:30 | 108.43 | 92.53
2017-09-06 06:00 | 108.95 | 93.55
2017-09-06 06:30 | 92.17 | 76.82
2017-09-06 07:00 | 95.29 | 80.99
2017-09-06 07:30 | 96.48 | 82.82
2017-09-06 08:00 | 87.65 | 73.28
2017-09-06 08:30 | 89 | 74.3
2017-09-06 09:00 | 91.99 | 77.28
2017-09-06 09:30 | 93.79 | 77.88
2017-09-06 10:00 | 84.98 | 67.71
2017-09-06 10:30 | 83.18 | 65.42
2017-09-06 11:00 | 85.24 | 66.11
2017-09-06 11:30 | 87.87 | 69.09
2017-09-06 12:00 | 87.46 | 69.48
2017-09-06 12:30 | 86.89 | 70.18
2017-09-06 13:00 | 84.89 | 68.37
2017-09-06 13:30 | 91.31 | 75.87
2017-09-06 14:00 | 86.08 | 69.35
2017-09-06 14:30 | 92.82 | 75.43
2017-09-06 15:00 | 92.4 | 75.34
2017-09-06 15:30 | 90.22 | 74.61
2017-09-06 16:00 | 98.83 | 84.01
2017-09-06 16:30 | 95.37 | 80.6
2017-09-06 17:00 | 104.26 | 90.14
2017-09-06 17:30 | 100.18 | 86.05
2017-09-06 18:00 | 101.2 | 86.04
2017-09-06 18:30 | 106.34 | 90.27
2017-09-06 19:00 | 104.43 | 89.7
2017-09-06 19:30 | 109.44 | 95.27
2017-09-06 20:00 | 104.57 | 90.29
2017-09-06 20:30 | 108.71 | 93.1
2017-09-06 21:00 | 103.57 | 87.86
2017-09-06 21:30 | 106.44 | 89.74
2017-09-06 22:00 | 102.44 | 86.36
2017-09-06 22:30 | 118.6 | 103.29
2017-09-06 23:00 | 111.99 | 94.9
2017-09-06 23:30 | 109.22 | 92.86
2017-09-07 | 108.01 | 92
2017-09-07 00:30 | 106.98 | 89.99
2017-09-07 01:00 | 103.79 | 86
2017-09-07 01:30 | 110.82 | 93.47
2017-09-07 02:00 | 117.4 | 100.71
2017-09-07 02:30 | 113.85 | 97.22
2017-09-07 03:00 | 108.32 | 92.14
2017-09-07 03:30 | 112.68 | 95.81
2017-09-07 04:00 | 114.48 | 98.59
2017-09-07 04:30 | 116.78 | 100.58
2017-09-07 05:00 | 114.73 | 98.96
2017-09-07 05:30 | 114.47 | 98.27
2017-09-07 06:00 | 112.02 | 96.03
2017-09-07 06:30 | 104.47 | 87.23
2017-09-07 07:00 | 107.78 | 91.99
2017-09-07 07:30 | 107.04 | 89.86
2017-09-07 08:00 | 108.38 | 91.87
2017-09-07 08:30 | 102.67 | 87.87
2017-09-07 09:00 | 102.98 | 85.49
2017-09-07 09:30 | 100.66 | 84.42
2017-09-07 10:00 | 108.99 | 93.43
2017-09-07 10:30 | 97.4 | 81.9
2017-09-07 11:00 | 93.5 | 78.04
2017-09-07 11:30 | 92.23 | 77.21
2017-09-07 12:00 | 98.23 | 83.37
2017-09-07 12:30 | 96.65 | 81.36
2017-09-07 13:00 | 93.42 | 78.03
2017-09-07 13:30 | 100.44 | 84.19
2017-09-07 14:00 | 104.3 | 85.89
2017-09-07 14:30 | 107.2 | 89.82
2017-09-07 15:00 | 106.8 | 88.91
2017-09-07 15:30 | 116.47 | 99.43
2017-09-07 16:00 | 111.88 | 93.58
2017-09-07 16:30 | 121.31 | 103.77
2017-09-07 17:00 | 120.52 | 103.48
2017-09-07 17:30 | 117.37 | 100.74
2017-09-07 18:00 | 118.86 | 102.18
2017-09-07 18:30 | 112.68 | 94.56
2017-09-07 19:00 | 122.94 | 106.34
2017-09-07 19:30 | 120.96 | 104.35
2017-09-07 20:00 | 124.42 | 107.12
2017-09-07 20:30 | 122.28 | 105.02
2017-09-07 21:00 | 122.94 | 104.75
2017-09-07 21:30 | 114.48 | 96.72
2017-09-07 22:00 | 118.13 | 100.63
2017-09-07 22:30 | 118.71 | 102.19
2017-09-07 23:00 | 116.53 | 100.26
2017-09-07 23:30 | 107.84 | 91.17
2017-09-08 | 111.07 | 94.99
2017-09-08 00:30 | 115.34 | 98.81
2017-09-08 01:00 | 116.09 | 99.29
2017-09-08 01:30 | 114.09 | 96.8
2017-09-08 02:00 | 105.78 | 89.14
2017-09-08 02:30 | 110.08 | 93.48
2017-09-08 03:00 | 112.17 | 93.79
2017-09-08 03:30 | 106.57 | 86.95
2017-09-08 04:00 | 108.24 | 90.52
2017-09-08 04:30 | 111.75 | 94.55
2017-09-08 05:00 | 110.63 | 92.68
2017-09-08 05:30 | 112.29 | 95.6
2017-09-08 06:00 | 120.14 | 103.39
2017-09-08 06:30 | 104.78 | 85.69
2017-09-08 07:00 | 113.12 | 96.1
2017-09-08 07:30 | 111.78 | 94.83
2017-09-08 08:00 | 113.55 | 96.71
2017-09-08 08:30 | 112.23 | 96.12
2017-09-08 09:00 | 109.26 | 92.11
2017-09-08 09:30 | 98.83 | 80.79
2017-09-08 10:00 | 97.78 | 80.65
2017-09-08 10:30 | 102.89 | 85.86
2017-09-08 11:00 | 103.9 | 86.78
2017-09-08 11:30 | 101.98 | 85.84
2017-09-08 12:00 | 103.74 | 89.74
2017-09-08 12:30 | 106.01 | 93.12
2017-09-08 13:00 | 105.76 | 90.53
2017-09-08 13:30 | 103.59 | 87.19
2017-09-08 14:00 | 95.6 | 78.17
2017-09-08 14:30 | 92.71 | 76.78
2017-09-08 15:00 | 95.71 | 79.88
2017-09-08 15:30 | 91.51 | 77.64
2017-09-08 16:00 | 97.6 | 84.26
2017-09-08 16:30 | 91.08 | 75.71
2017-09-08 17:00 | 110.71 | 94.12
2017-09-08 17:30 | 109.07 | 94.95
2017-09-08 18:00 | 112.05 | 97.85
2017-09-08 18:30 | 101.82 | 86.54
2017-09-08 19:00 | 108.68 | 94.25
2017-09-08 19:30 | 110.49 | 94.93
2017-09-08 20:00 | 114.66 | 98.88
2017-09-08 20:30 | 111.75 | 96.9
2017-09-08 21:00 | 113.91 | 99.01
2017-09-08 21:30 | 106.29 | 91.06
2017-09-08 22:00 | 104.02 | 88.64
2017-09-08 22:30 | 109.33 | 94.67
2017-09-08 23:00 | 111.53 | 97.49
2017-09-08 23:30 | 105.2 | 91.33
2017-09-09 | 101.49 | 87.31
2017-09-09 00:30 | 105.18 | 90.91
2017-09-09 01:00 | 109.37 | 95.1
2017-09-09 01:30 | 105.48 | 90.77
2017-09-09 02:00 | 101.19 | 86.49
2017-09-09 02:30 | 108.94 | 95.34
2017-09-09 03:00 | 105.31 | 93.32
2017-09-09 03:30 | 101.53 | 88.91
2017-09-09 04:00 | 102.67 | 89.63
2017-09-09 04:30 | 97.61 | 84.28
2017-09-09 05:00 | 100.24 | 86.36
2017-09-09 05:30 | 100.13 | 87.17
2017-09-09 06:00 | 103.76 | 90.96
2017-09-09 06:30 | 98 | 84.4
2017-09-09 07:00 | 105.46 | 93.2
2017-09-09 07:30 | 112.79 | 100.76
2017-09-09 08:00 | 105.43 | 93.25
2017-09-09 08:30 | 104.66 | 91.75
2017-09-09 09:00 | 109.42 | 96.57
2017-09-09 09:30 | 110.61 | 97.14
2017-09-09 10:00 | 106.08 | 93
2017-09-09 10:30 | 105.49 | 91.6
2017-09-09 11:00 | 100.61 | 86.06
2017-09-09 11:30 | 99.43 | 84.83
2017-09-09 12:00 | 100.26 | 85.89
2017-09-09 12:30 | 115.18 | 102.74
2017-09-09 13:00 | 109.7 | 97.21
2017-09-09 13:30 | 101.11 | 87.48
2017-09-09 14:00 | 105.47 | 91.19
2017-09-09 14:30 | 104.76 | 90.52
2017-09-09 15:00 | 103.69 | 89.73
2017-09-09 15:30 | 103.43 | 89.42
2017-09-09 16:00 | 108.28 | 95.37
2017-09-09 16:30 | 109.36 | 96.37
2017-09-09 17:00 | 116.81 | 103.3
2017-09-09 17:30 | 120.02 | 106.62
2017-09-09 18:00 | 126.52 | 112.8
2017-09-09 18:30 | 116.08 | 99.81
2017-09-09 19:00 | 120.52 | 104.98
2017-09-09 19:30 | 124.71 | 109.7
2017-09-09 20:00 | 123.8 | 108.4
2017-09-09 20:30 | 113.97 | 99.48
2017-09-09 21:00 | 123.23 | 109.08
2017-09-09 21:30 | 113.58 | 98.37
2017-09-09 22:00 | 119.63 | 103.77
2017-09-09 22:30 | 112.73 | 97.86
2017-09-09 23:00 | 107.83 | 92.58
2017-09-09 23:30 | 106.99 | 92.27
2017-09-10 | 103.78 | 89.96
2017-09-10 00:30 | 110.09 | 97.22
2017-09-10 01:00 | 112.67 | 100.69
2017-09-10 01:30 | 111.27 | 99.09
2017-09-10 02:00 | 112.14 | 99.07
2017-09-10 02:30 | 107.08 | 92.57
2017-09-10 03:00 | 109.73 | 95.86
2017-09-10 03:30 | 108.69 | 95.4
2017-09-10 04:00 | 106.61 | 92.82
2017-09-10 04:30 | 107.65 | 93.81
2017-09-10 05:00 | 109.35 | 95.89
2017-09-10 05:30 | 115.68 | 102.53
2017-09-10 06:00 | 114.57 | 100.59
2017-09-10 06:30 | 101.63 | 85.71
2017-09-10 07:00 | 111.16 | 97.47
2017-09-10 07:30 | 105.62 | 90.63
2017-09-10 08:00 | 111.97 | 97.86
2017-09-10 08:30 | 109.64 | 94.82
2017-09-10 09:00 | 106.43 | 91.44
2017-09-10 09:30 | 103.4 | 86.99
2017-09-10 10:00 | 104.71 | 87.86
2017-09-10 10:30 | 109.56 | 93.26
2017-09-10 11:00 | 100.47 | 82.44
2017-09-10 11:30 | 107.81 | 90.74
2017-09-10 12:00 | 111.32 | 95.63
2017-09-10 12:30 | 110.94 | 96.06
2017-09-10 13:00 | 104.48 | 88.82
2017-09-10 13:30 | 105.15 | 89.96
2017-09-10 14:00 | 104.44 | 88.3
2017-09-10 14:30 | 106.04 | 90.79
2017-09-10 15:00 | 111.47 | 95.66
2017-09-10 15:30 | 117.82 | 102.28
2017-09-10 16:00 | 115.36 | 98.17
2017-09-10 16:30 | 110.45 | 92.21
2017-09-10 17:00 | 115.31 | 96.7
2017-09-10 17:30 | 110.67 | 94.87
2017-09-10 18:00 | 118.5 | 101.92
2017-09-10 18:30 | 106.8 | 88.21
2017-09-10 19:00 | 108.5 | 90.08
2017-09-10 19:30 | 126.05 | 107.71
2017-09-10 20:00 | 122.5 | 104.87
2017-09-10 20:30 | 120.64 | 104.36
2017-09-10 21:00 | 114 | 96.76
2017-09-10 21:30 | 114.14 | 98.09
2017-09-10 22:00 | 116.08 | 101.18
2017-09-10 22:30 | 113.31 | 97.23
2017-09-10 23:00 | 114.71 | 98.15
2017-09-10 23:30 | 116.63 | 100.87
2017-09-11 | 118.23 | 103.41
2017-09-11 00:30 | 119.5 | 104.93
2017-09-11 01:00 | 117.15 | 102.91
2017-09-11 01:30 | 124.27 | 109.89
2017-09-11 02:00 | 116.96 | 103.36
2017-09-11 02:30 | 117.82 | 103.76
2017-09-11 03:00 | 107.98 | 93.91
2017-09-11 03:30 | 109.16 | 95.54
2017-09-11 04:00 | 114.48 | 100.49
2017-09-11 04:30 | 114.85 | 101.51
2017-09-11 05:00 | 112.89 | 98.33
2017-09-11 05:30 | 111.93 | 98.42
2017-09-11 06:00 | 106.34 | 92.57
2017-09-11 06:30 | 105.57 | 91.29
2017-09-11 07:00 | 108.34 | 95.67
2017-09-11 07:30 | 107.78 | 94.04
2017-09-11 08:00 | 108.91 | 94.25
2017-09-11 08:30 | 106.47 | 92.31
2017-09-11 09:00 | 108.52 | 95.48
2017-09-11 09:30 | 101.59 | 88.81
2017-09-11 10:00 | 103.09 | 89.63
2017-09-11 10:30 | 107.42 | 93.51
2017-09-11 11:00 | 109.1 | 94.42
2017-09-11 11:30 | 106.51 | 91.68
2017-09-11 12:00 | 101.77 | 86.56
2017-09-11 12:30 | 106.53 | 92.17
2017-09-11 13:00 | 109.74 | 95.32
2017-09-11 13:30 | 107.75 | 92.42
2017-09-11 14:00 | 109.87 | 93.68
2017-09-11 14:30 | 103.39 | 87.98
2017-09-11 15:00 | 104.99 | 88.18
2017-09-11 15:30 | 107.79 | 91.85
2017-09-11 16:00 | 117.36 | 101.38
2017-09-11 16:30 | 119.71 | 103.13
2017-09-11 17:00 | 113.64 | 98.32
2017-09-11 17:30 | 118.48 | 103.15
2017-09-11 18:00 | 111.76 | 96.89
2017-09-11 18:30 | 106.15 | 89.17
2017-09-11 19:00 | 113.78 | 98.18
2017-09-11 19:30 | 119.44 | 102.49
2017-09-11 20:00 | 116.49 | 98.3
2017-09-11 20:30 | 124.83 | 109.12
2017-09-11 21:00 | 126.07 | 109.41
2017-09-11 21:30 | 131.73 | 117.08
2017-09-11 22:00 | 115 | 100.04
2017-09-11 22:30 | 114.59 | 99.04
2017-09-11 23:00 | 112.37 | 97.46
2017-09-11 23:30 | 115.41 | 99.69
2017-09-12 | 116.76 | 102.18
2017-09-12 00:30 | 125.49 | 111.23
2017-09-12 01:00 | 115.67 | 102.28
2017-09-12 01:30 | 111.86 | 98.44
2017-09-12 02:00 | 113.7 | 101.48
2017-09-12 02:30 | 107.98 | 97.21
2017-09-12 03:00 | 98.79 | 86.94
2017-09-12 03:30 | 97.28 | 84.31
2017-09-12 04:00 | 96.16 | 83.85
2017-09-12 04:30 | 99.44 | 89.46
2017-09-12 05:00 | 99.57 | 89.05
2017-09-12 05:30 | 96.68 | 85.7
2017-09-12 06:00 | 99.1 | 88.65
2017-09-12 06:30 | 86.73 | 73.29
2017-09-12 07:00 | 89.63 | 77.51
2017-09-12 07:30 | 94.23 | 83.07
2017-09-12 08:00 | 93.24 | 81.28
2017-09-12 08:30 | 89.69 | 77.71
2017-09-12 09:00 | 90.82 | 77.15
2017-09-12 09:30 | 89.01 | 74.19
2017-09-12 10:00 | 86.56 | 71.58
2017-09-12 10:30 | 90.48 | 75.87
2017-09-12 11:00 | 93.65 | 80.1
2017-09-12 11:30 | 95.28 | 83.33
2017-09-12 12:00 | 99.57 | 88.55
2017-09-12 12:30 | 96.82 | 84.79
2017-09-12 13:00 | 98.45 | 86.72
2017-09-12 13:30 | 94.99 | 83.44
2017-09-12 14:00 | 92.01 | 79.44
2017-09-12 14:30 | 95.52 | 83.35
2017-09-12 15:00 | 88.3 | 73.91
2017-09-12 15:30 | 89.35 | 76.28
2017-09-12 16:00 | 92.96 | 80.6
2017-09-12 16:30 | 88.49 | 75.54
2017-09-12 17:00 | 90.64 | 78.64
2017-09-12 17:30 | 91.11 | 78.45
2017-09-12 18:00 | 92.5 | 80.45
2017-09-12 18:30 | 89.91 | 76.74
2017-09-12 19:00 | 93.38 | 81.56
2017-09-12 19:30 | 98.13 | 87.09
2017-09-12 20:00 | 95.09 | 84.58
2017-09-12 20:30 | 99.82 | 89.64
2017-09-12 21:00 | 99.39 | 88.43
2017-09-12 21:30 | 98 | 86.7
2017-09-12 22:00 | 104.15 | 92.84
2017-09-12 22:30 | 104.93 | 93.82
2017-09-12 23:00 | 101.89 | 89.34
2017-09-12 23:30 | 100.14 | 88.3
2017-09-13 | 101.02 | 90.31
2017-09-13 00:30 | 96.22 | 84.95
2017-09-13 01:00 | 100.58 | 89.53
2017-09-13 01:30 | 97.48 | 84.77
2017-09-13 02:00 | 100.14 | 88
2017-09-13 02:30 | 101.27 | 89.32
2017-09-13 03:00 | 97 | 84.42
2017-09-13 03:30 | 95.13 | 81.51
2017-09-13 04:00 | 94.82 | 82.86
2017-09-13 04:30 | 94.62 | 83.48
2017-09-13 05:00 | 101.21 | 89.02
2017-09-13 05:30 | 98.72 | 86.49
2017-09-13 06:00 | 98.41 | 85.15
2017-09-13 06:30 | 95.12 | 80.09
2017-09-13 07:00 | 95.73 | 80.29
2017-09-13 07:30 | 98.38 | 83.51
2017-09-13 08:00 | 96.65 | 80.8
2017-09-13 08:30 | 98.29 | 82.01
2017-09-13 09:00 | 98.94 | 82.08
2017-09-13 09:30 | 101.94 | 85.85
2017-09-13 10:00 | 106.17 | 89.49
2017-09-13 10:30 | 97.21 | 79.78
2017-09-13 11:00 | 98.12 | 81.1
2017-09-13 11:30 | 100.45 | 83.59
2017-09-13 12:00 | 105.16 | 89.55
2017-09-13 12:30 | 97.11 | 81.44
2017-09-13 13:00 | 101.66 | 86.99
2017-09-13 13:30 | 102.23 | 87.83
2017-09-13 14:00 | 102.31 | 86.82
2017-09-13 14:30 | 101.45 | 84.08
2017-09-13 15:00 | 105.72 | 88.68
2017-09-13 15:30 | 109.03 | 91.95
2017-09-13 16:00 | 107.85 | 90.39
2017-09-13 16:30 | 112.17 | 96.22
2017-09-13 17:00 | 110.28 | 95.5
2017-09-13 17:30 | 107.85 | 92.62
2017-09-13 18:00 | 118.61 | 103.14
2017-09-13 18:30 | 110.2 | 93.57
2017-09-13 19:00 | 113.54 | 97.37
2017-09-13 19:30 | 121.51 | 105.65
2017-09-13 20:00 | 119.49 | 103.1
2017-09-13 20:30 | 121.55 | 105.89
2017-09-13 21:00 | 122.94 | 107.52
2017-09-13 21:30 | 116.24 | 101.34
2017-09-13 22:00 | 114.25 | 99.7
2017-09-13 22:30 | 115.58 | 101.08
2017-09-13 23:00 | 110.66 | 95.32
2017-09-13 23:30 | 106.96 | 91.61
2017-09-14 | 104.23 | 89.38
2017-09-14 00:30 | 110.92 | 96.78
2017-09-14 01:00 | 111.04 | 98.25
2017-09-14 01:30 | 105.02 | 91.17
2017-09-14 02:00 | 108.36 | 93.78
2017-09-14 02:30 | 110.03 | 95.55
2017-09-14 03:00 | 110.74 | 96.14
2017-09-14 03:30 | 107.83 | 93.32
2017-09-14 04:00 | 108.7 | 93.84
2017-09-14 04:30 | 116.44 | 102.61
2017-09-14 05:00 | 106.82 | 93.49
2017-09-14 05:30 | 110.67 | 95.87
2017-09-14 06:00 | 110 | 96.18
2017-09-14 06:30 | 97.53 | 81.48
2017-09-14 07:00 | 91.19 | 73.96
2017-09-14 07:30 | 97 | 81.42
2017-09-14 08:00 | 99.95 | 82.43
2017-09-14 08:30 | 108.72 | 90.37
2017-09-14 09:00 | 110.83 | 90.97
2017-09-14 09:30 | 101.56 | 82.05
2017-09-14 10:00 | 108.87 | 89.87
2017-09-14 10:30 | 108.15 | 89.08
2017-09-14 11:00 | 105.09 | 86.69
2017-09-14 11:30 | 100.35 | 80.5
2017-09-14 12:00 | 106.42 | 88.05
2017-09-14 12:30 | 106.66 | 87.41
2017-09-14 13:00 | 107.59 | 88.95
2017-09-14 13:30 | 110.62 | 92.45
2017-09-14 14:00 | 100.64 | 80.84
2017-09-14 14:30 | 106.16 | 86.41
2017-09-14 15:00 | 108.08 | 87.81
2017-09-14 15:30 | 106.43 | 85.32
2017-09-14 16:00 | 106.9 | 88.31
2017-09-14 16:30 | 116.78 | 98.63
2017-09-14 17:00 | 115.94 | 98.11
2017-09-14 17:30 | 117.02 | 99.67
2017-09-14 18:00 | 108.2 | 92.49
2017-09-14 18:30 | 96.79 | 80.23
2017-09-14 19:00 | 91.21 | 73.32
2017-09-14 19:30 | 96.13 | 79.2
2017-09-14 20:00 | 94.9 | 78.3
2017-09-14 20:30 | 100.08 | 84.45
2017-09-14 21:00 | 105.82 | 91.5
2017-09-14 21:30 | 104.51 | 90.53
2017-09-14 22:00 | 102.3 | 88.15
2017-09-14 22:30 | 102.63 | 88.6
2017-09-14 23:00 | 99.86 | 86.02
2017-09-14 23:30 | 97.31 | 84.52
2017-09-15 | 94.41 | 82.31
2017-09-15 00:30 | 94.59 | 82.36
2017-09-15 01:00 | 100.56 | 88.1
2017-09-15 01:30 | 104.64 | 92.53
2017-09-15 02:00 | 100.88 | 88.01
2017-09-15 02:30 | 103.54 | 90.64
2017-09-15 03:00 | 104.53 | 91.41
2017-09-15 03:30 | 108.47 | 95.03
2017-09-15 04:00 | 111.81 | 96.74
2017-09-15 04:30 | 108.86 | 92.25
2017-09-15 05:00 | 113.51 | 96.73
2017-09-15 05:30 | 113.61 | 95.87
2017-09-15 06:00 | 117.98 | 101
2017-09-15 06:30 | 113.86 | 96.62
2017-09-15 07:00 | 117.64 | 101.43
2017-09-15 07:30 | 124.48 | 108.06
2017-09-15 08:00 | 127.13 | 109.99
2017-09-15 08:30 | 124.12 | 105.96
2017-09-15 09:00 | 118.48 | 100.16
2017-09-15 09:30 | 116.16 | 96.92
2017-09-15 10:00 | 118.67 | 99.7
2017-09-15 10:30 | 111.98 | 93.03
2017-09-15 11:00 | 110.15 | 90.4
2017-09-15 11:30 | 108.15 | 88.48
2017-09-15 12:00 | 108.68 | 89.8
2017-09-15 12:30 | 116.63 | 97.72
2017-09-15 13:00 | 120.2 | 101.69
2017-09-15 13:30 | 115.38 | 97
2017-09-15 14:00 | 110.99 | 92.22
2017-09-15 14:30 | 115.82 | 97.28
2017-09-15 15:00 | 115.36 | 95.72
2017-09-15 15:30 | 115.63 | 95.51
2017-09-15 16:00 | 111.71 | 92.55
2017-09-15 16:30 | 121.68 | 104.84
2017-09-15 17:00 | 120.3 | 102.37
2017-09-15 17:30 | 115.3 | 97.02
2017-09-15 18:00 | 119.92 | 101.33
2017-09-15 18:30 | 114.83 | 94.63
2017-09-15 19:00 | 115.47 | 95.42
2017-09-15 19:30 | 119.27 | 99.44
2017-09-15 20:00 | 116.1 | 96.66
2017-09-15 20:30 | 119.05 | 100.3
2017-09-15 21:00 | 119.49 | 100.86
2017-09-15 21:30 | 118.47 | 101.25
2017-09-15 22:00 | 118.11 | 101.32
2017-09-15 22:30 | 120.16 | 102.61
2017-09-15 23:00 | 123.3 | 106.79
2017-09-15 23:30 | 120.18 | 105.03
2017-09-16 | 119.29 | 103.41
2017-09-16 00:30 | 122.34 | 106.37
2017-09-16 01:00 | 121.1 | 104.87
2017-09-16 01:30 | 116.74 | 100.86
2017-09-16 02:00 | 126.74 | 111.47
2017-09-16 02:30 | 113.55 | 98.52
2017-09-16 03:00 | 112.41 | 96.02
2017-09-16 03:30 | 114.25 | 98.66
2017-09-16 04:00 | 117.19 | 102.1
2017-09-16 04:30 | 120.08 | 104.41
2017-09-16 05:00 | 113.04 | 97.87
2017-09-16 05:30 | 117.59 | 102.75
2017-09-16 06:00 | 117.78 | 101.74
2017-09-16 06:30 | 100.24 | 82.41
2017-09-16 07:00 | 106 | 88.18
2017-09-16 07:30 | 108.9 | 91
2017-09-16 08:00 | 101.82 | 83.78
2017-09-16 08:30 | 102.33 | 83.26
2017-09-16 09:00 | 112.38 | 93.27
2017-09-16 09:30 | 122.38 | 105.26
2017-09-16 10:00 | 123.09 | 104.71
2017-09-16 10:30 | 120.26 | 101.34
2017-09-16 11:00 | 123.22 | 103.82
2017-09-16 11:30 | 113.94 | 94.24
2017-09-16 12:00 | 118.57 | 98.59
2017-09-16 12:30 | 116.82 | 97.01
2017-09-16 13:00 | 118 | 99.65
2017-09-16 13:30 | 120.21 | 101.92
2017-09-16 14:00 | 120.98 | 102.91
2017-09-16 14:30 | 121.99 | 102.51
2017-09-16 15:00 | 116.31 | 97.02
2017-09-16 15:30 | 121.74 | 104.11
2017-09-16 16:00 | 114.25 | 95.73
2017-09-16 16:30 | 119.24 | 101.54
2017-09-16 17:00 | 115.56 | 98.63
2017-09-16 17:30 | 111.86 | 94.86
2017-09-16 18:00 | 116.36 | 96.96
2017-09-16 18:30 | 121.38 | 100.03
2017-09-16 19:00 | 119.52 | 99.87
2017-09-16 19:30 | 119.96 | 101.28
2017-09-16 20:00 | 121.13 | 101.85
2017-09-16 20:30 | 115.7 | 98.29
2017-09-16 21:00 | 112.45 | 95.84
2017-09-16 21:30 | 110.69 | 94.41
2017-09-16 22:00 | 104.93 | 87.86
2017-09-16 22:30 | 107.6 | 90.94
2017-09-16 23:00 | 110.92 | 92.98
2017-09-16 23:30 | 113.05 | 94.26
2017-09-17 | 115.05 | 97.07
2017-09-17 00:30 | 114.33 | 97.31
2017-09-17 01:00 | 119.09 | 102.29
2017-09-17 01:30 | 115.75 | 98.92
2017-09-17 02:00 | 116.28 | 100.51
2017-09-17 02:30 | 119.73 | 102.91
2017-09-17 03:00 | 110.55 | 93.66
2017-09-17 03:30 | 103.77 | 88.46
2017-09-17 04:00 | 106.77 | 92.01
2017-09-17 04:30 | 105.75 | 90.51
2017-09-17 05:00 | 107.73 | 92.25
2017-09-17 05:30 | 109.33 | 94.57
2017-09-17 06:00 | 105.22 | 90.52
2017-09-17 06:30 | 107.4 | 93.06
2017-09-17 07:00 | 100.23 | 86.51
2017-09-17 07:30 | 107.01 | 92.65
2017-09-17 08:00 | 105.48 | 90.45
2017-09-17 08:30 | 102.36 | 87.16
2017-09-17 09:00 | 110.32 | 95.1
2017-09-17 09:30 | 102.98 | 87.35
2017-09-17 10:00 | 107.56 | 91.48
2017-09-17 10:30 | 112.22 | 95.01
2017-09-17 11:00 | 119.83 | 101.24
2017-09-17 11:30 | 112.98 | 93.2
2017-09-17 12:00 | 115.35 | 97.79
2017-09-17 12:30 | 124.17 | 107.29
2017-09-17 13:00 | 119.36 | 102.47
2017-09-17 13:30 | 113.01 | 95.3
2017-09-17 14:00 | 117.43 | 99.56
2017-09-17 14:30 | 114.21 | 95.68
2017-09-17 15:00 | 112.04 | 92.05
2017-09-17 15:30 | 119.96 | 99.03
2017-09-17 16:00 | 122.04 | 102.66
2017-09-17 16:30 | 120.83 | 105.75
2017-09-17 17:00 | 118.27 | 102.82
2017-09-17 17:30 | 122.73 | 106.29
2017-09-17 18:00 | 118.27 | 101.18
2017-09-17 18:30 | 120.96 | 101.71
2017-09-17 19:00 | 126.34 | 108.29
2017-09-17 19:30 | 122.82 | 103.85
2017-09-17 20:00 | 116.04 | 97.61
2017-09-17 20:30 | 121.16 | 102.26
2017-09-17 21:00 | 126.12 | 108.96
2017-09-17 21:30 | 120.05 | 101.89
2017-09-17 22:00 | 118.77 | 100.68
2017-09-17 22:30 | 115.87 | 98.36
2017-09-17 23:00 | 117.43 | 98.99
2017-09-17 23:30 | 110.6 | 93.91
2017-09-18 | 106.51 | 89.35
2017-09-18 00:30 | 110.88 | 93.24
2017-09-18 01:00 | 112.86 | 96.28
2017-09-18 01:30 | 105.11 | 88.28
2017-09-18 02:00 | 109.14 | 92.3
2017-09-18 02:30 | 108.21 | 91.36
2017-09-18 03:00 | 108.21 | 91.68
2017-09-18 03:30 | 108.3 | 90.9
2017-09-18 04:00 | 109.19 | 91.57
2017-09-18 04:30 | 97.55 | 90.51
2017-09-18 05:00 | 89.25 | 83.36
2017-09-18 05:30 | 93.4 | 86.81
2017-09-18 06:00 | 97.31 | 90.11
2017-09-18 06:30 | 92.47 | 84.84
2017-09-18 07:00 | 96.48 | 89.24
2017-09-18 07:30 | 100.4 | 93.11
2017-09-18 08:00 | 92.71 | 85.82
2017-09-18 08:30 | 90.2 | 82.99
2017-09-18 09:00 | 89.99 | 81.88
2017-09-18 09:30 | 89.82 | 81.22
2017-09-18 10:00 | 90.63 | 81.62
2017-09-18 10:30 | 89.32 | 81.27
2017-09-18 11:00 | 87.09 | 78.96
2017-09-18 11:30 | 83.02 | 75.18
2017-09-18 12:00 | 92.22 | 84.8
2017-09-18 12:30 | 94.53 | 87.32
2017-09-18 13:00 | 96.38 | 88.83
2017-09-18 13:30 | 100.26 | 92.36
2017-09-18 14:00 | 98.25 | 89.83
2017-09-18 14:30 | 93.5 | 84.67
2017-09-18 15:00 | 94.81 | 87.18
2017-09-18 15:30 | 88.17 | 80.11
2017-09-18 16:00 | 91.83 | 83.48
2017-09-18 16:30 | 92.1 | 85.15
2017-09-18 17:00 | 94.6 | 86.97
2017-09-18 17:30 | 102.86 | 94.54
2017-09-18 18:00 | 96.34 | 89.15
2017-09-18 18:30 | 89.5 | 81.04
2017-09-18 19:00 | 95.27 | 87.99
2017-09-18 19:30 | 92.86 | 86.79
2017-09-18 20:00 | 95.08 | 88.57
2017-09-18 20:30 | 95.19 | 88.09
2017-09-18 21:00 | 91.83 | 84.77
2017-09-18 21:30 | 97.73 | 90.11
2017-09-18 22:00 | 95.36 | 87.17
2017-09-18 22:30 | 97.36 | 89.1
2017-09-18 23:00 | 97.21 | 89.2
2017-09-18 23:30 | 95.98 | 88.59
2017-09-19 | 95.72 | 88.6
2017-09-19 00:30 | 96.3 | 88.83
2017-09-19 01:00 | 95.3 | 88.55
2017-09-19 01:30 | 95.36 | 87.79
2017-09-19 02:00 | 96.45 | 88.92
2017-09-19 02:30 | 100.27 | 93.23
2017-09-19 03:00 | 93.23 | 86.75
2017-09-19 03:30 | 93.62 | 86.57
2017-09-19 04:00 | 94.99 | 88.3
2017-09-19 04:30 | 91.13 | 84.44
2017-09-19 05:00 | 95.41 | 88.09
2017-09-19 05:30 | 99.2 | 91.21
2017-09-19 06:00 | 99.28 | 91.91
2017-09-19 06:30 | 88.85 | 80.72
2017-09-19 07:00 | 92.15 | 85.48
2017-09-19 07:30 | 95.15 | 87.93
2017-09-19 08:00 | 93.62 | 85.9
2017-09-19 08:30 | 94.61 | 86.43
2017-09-19 09:00 | 93.88 | 86.05
2017-09-19 09:30 | 90.19 | 82.12
2017-09-19 10:00 | 94.03 | 86.12
2017-09-19 10:30 | 95.15 | 87.55
2017-09-19 11:00 | 89.18 | 80.98
2017-09-19 11:30 | 87.73 | 80.72
2017-09-19 12:00 | 90.54 | 82.41
2017-09-19 12:30 | 95.62 | 87.62
2017-09-19 13:00 | 99.55 | 91.8
2017-09-19 13:30 | 99.39 | 90.99
2017-09-19 14:00 | 100.86 | 92.68
2017-09-19 14:30 | 98.57 | 90.56
2017-09-19 15:00 | 97.36 | 89.72
2017-09-19 15:30 | 95.58 | 87.98
2017-09-19 16:00 | 97.54 | 90.16
2017-09-19 16:30 | 93.34 | 86.03
2017-09-19 17:00 | 97.29 | 89.86
2017-09-19 17:30 | 100.32 | 92.45
2017-09-19 18:00 | 113.65 | 96.31
2017-09-19 18:30 | 106.72 | 86.12
2017-09-19 19:00 | 112.99 | 94.39
2017-09-19 19:30 | 118.49 | 101.73
2017-09-19 20:00 | 118.73 | 100.92
2017-09-19 20:30 | 114.96 | 97.41
2017-09-19 21:00 | 114.4 | 95.8
2017-09-19 21:30 | 117.41 | 97.38
2017-09-19 22:00 | 115.66 | 95.83
2017-09-19 22:30 | 116.53 | 96.73
2017-09-19 23:00 | 115.38 | 96.23
2017-09-19 23:30 | 109.41 | 90.57
2017-09-20 | 104.39 | 85.43
2017-09-20 00:30 | 107.22 | 87.49
2017-09-20 01:00 | 108.2 | 88.99
2017-09-20 01:30 | 110.79 | 92.93
2017-09-20 02:00 | 120.16 | 102.09
2017-09-20 02:30 | 111.74 | 93.44
2017-09-20 03:00 | 112.14 | 94.72
2017-09-20 03:30 | 113.95 | 96.52
2017-09-20 04:00 | 114.33 | 97.27
2017-09-20 04:30 | 118.05 | 102.02
2017-09-20 05:00 | 112.11 | 94.96
2017-09-20 05:30 | 113.41 | 95.88
2017-09-20 06:00 | 109.23 | 92.2
2017-09-20 06:30 | 103.32 | 85.18
2017-09-20 07:00 | 106.43 | 90.81
2017-09-20 07:30 | 97.22 | 83.2
2017-09-20 08:00 | 94.45 | 78.59
2017-09-20 08:30 | 103.97 | 86.29
2017-09-20 09:00 | 103.25 | 83.93
2017-09-20 09:30 | 107.37 | 86.43
2017-09-20 10:00 | 110.3 | 89.76
2017-09-20 10:30 | 122.78 | 103.06
2017-09-20 11:00 | 117.77 | 96.4
2017-09-20 11:30 | 110.69 | 92.56
2017-09-20 12:00 | 117.59 | 98.67
2017-09-20 12:30 | 111.46 | 91.46
2017-09-20 13:00 | 106.79 | 87.22
2017-09-20 13:30 | 103.17 | 85.81
2017-09-20 14:00 | 106.74 | 88.17
2017-09-20 14:30 | 112.23 | 93.18
2017-09-20 15:00 | 113.33 | 93.16
2017-09-20 15:30 | 112.69 | 90.09
2017-09-20 16:00 | 107.82 | 84.37
2017-09-20 16:30 | 112.77 | 88.64
2017-09-20 17:00 | 112.91 | 88.59
2017-09-20 17:30 | 121.95 | 98.9
2017-09-20 18:00 | 123.88 | 101.09
2017-09-20 18:30 | 113.34 | 90.87
2017-09-20 19:00 | 127.12 | 106.7
2017-09-20 19:30 | 132.8 | 113.71
2017-09-20 20:00 | 130.25 | 108.63
2017-09-20 20:30 | 130.7 | 108.95
2017-09-20 21:00 | 123.23 | 100.94
2017-09-20 21:30 | 126.72 | 104.57
2017-09-20 22:00 | 125.98 | 107.36
2017-09-20 22:30 | 120.34 | 102.33
2017-09-20 23:00 | 112.36 | 94.4
2017-09-20 23:30 | 108.7 | 90.84
2017-09-21 | 116.12 | 98.64
2017-09-21 00:30 | 110.3 | 92.52
2017-09-21 01:00 | 111.98 | 95.63
2017-09-21 01:30 | 113.16 | 97.11
2017-09-21 02:00 | 110.82 | 93.72
2017-09-21 02:30 | 117.92 | 101.93
2017-09-21 03:00 | 109.92 | 92.44
2017-09-21 03:30 | 107.96 | 92.56
2017-09-21 04:00 | 117.93 | 101.25
2017-09-21 04:30 | 109.03 | 91.18
2017-09-21 05:00 | 110.29 | 92.07
2017-09-21 05:30 | 110.85 | 92.08
2017-09-21 06:00 | 110.89 | 90.42
2017-09-21 06:30 | 101.76 | 80.35
2017-09-21 07:00 | 100.6 | 79.39
2017-09-21 07:30 | 97.46 | 78.6
2017-09-21 08:00 | 95.44 | 75.1
2017-09-21 08:30 | 96.33 | 76.35
2017-09-21 09:00 | 94.24 | 75.15
2017-09-21 09:30 | 92.21 | 73.69
2017-09-21 10:00 | 89.72 | 75.53
2017-09-21 10:30 | 93.36 | 78.35
2017-09-21 11:00 | 95.72 | 79.31
2017-09-21 11:30 | 94.3 | 77.6
2017-09-21 12:00 | 99.26 | 81.91
2017-09-21 12:30 | 99.46 | 84.03
2017-09-21 13:00 | 95.29 | 79.88
2017-09-21 13:30 | 107.59 | 91.71
2017-09-21 14:00 | 110.06 | 94.94
2017-09-21 14:30 | 105.7 | 89.25
2017-09-21 15:00 | 107.5 | 89.57
2017-09-21 15:30 | 103.74 | 86.6
2017-09-21 16:00 | 107.78 | 89.24
2017-09-21 16:30 | 102.87 | 82.42
2017-09-21 17:00 | 108.05 | 87.51
2017-09-21 17:30 | 102.42 | 83.74
2017-09-21 18:00 | 107.9 | 88.7
2017-09-21 18:30 | 100.06 | 79.78
2017-09-21 19:00 | 112.41 | 94.36
2017-09-21 19:30 | 110.69 | 91.79
2017-09-21 20:00 | 117.13 | 98.42
2017-09-21 20:30 | 115.97 | 96.88
2017-09-21 21:00 | 112.35 | 92.63
2017-09-21 21:30 | 109.73 | 90.52
2017-09-21 22:00 | 103.89 | 83.54
2017-09-21 22:30 | 109.99 | 91.49
2017-09-21 23:00 | 113.42 | 95.4
2017-09-21 23:30 | 111.9 | 91.63
2017-09-22 | 119.87 | 101.72
2017-09-22 00:30 | 126.53 | 108.96
2017-09-22 01:00 | 120.27 | 103.1
2017-09-22 01:30 | 122.52 | 105.4
2017-09-22 02:00 | 119.34 | 99.88
2017-09-22 02:30 | 120.07 | 103.34
2017-09-22 03:00 | 115.79 | 98.68
2017-09-22 03:30 | 124.18 | 104.33
2017-09-22 04:00 | 121.52 | 102.59
2017-09-22 04:30 | 125.03 | 106.28
2017-09-22 05:00 | 122.58 | 104.35
2017-09-22 05:30 | 115.97 | 97.54
2017-09-22 06:00 | 109.86 | 92.06
2017-09-22 06:30 | 106.93 | 85.8
2017-09-22 07:00 | 111.91 | 92.22
2017-09-22 07:30 | 114.12 | 95.29
2017-09-22 08:00 | 113.7 | 95.18
2017-09-22 08:30 | 119.4 | 99.14
2017-09-22 09:00 | 119.84 | 99.33
2017-09-22 09:30 | 123.19 | 101.94
2017-09-22 10:00 | 123.77 | 102.24
2017-09-22 10:30 | 125.01 | 103.62
2017-09-22 11:00 | 121.45 | 99.55
2017-09-22 11:30 | 117.88 | 95.47
2017-09-22 12:00 | 115.9 | 94.19
2017-09-22 12:30 | 114.57 | 92.35
2017-09-22 13:00 | 116.55 | 97.7
2017-09-22 13:30 | 126.6 | 106.76
2017-09-22 14:00 | 130.11 | 108.87
2017-09-22 14:30 | 123.77 | 101.76
2017-09-22 15:00 | 118.25 | 95.46
2017-09-22 15:30 | 122.81 | 99.73
2017-09-22 16:00 | 123.24 | 101.84
2017-09-22 16:30 | 123.71 | 102.33
2017-09-22 17:00 | 127.17 | 105.87
2017-09-22 17:30 | 129.02 | 108.64
2017-09-22 18:00 | 132.81 | 110.85
2017-09-22 18:30 | 120.95 | 97.59
2017-09-22 19:00 | 122.54 | 101.89
2017-09-22 19:30 | 129.33 | 109.79
2017-09-22 20:00 | 128.59 | 110.51
2017-09-22 20:30 | 133.59 | 115.21
2017-09-22 21:00 | 127.1 | 108.72
2017-09-22 21:30 | 129.06 | 110.53
2017-09-22 22:00 | 128.97 | 111.94
2017-09-22 22:30 | 124.9 | 106.43
2017-09-22 23:00 | 127.77 | 110.3
2017-09-22 23:30 | 124.75 | 107.72
2017-09-23 | 125.7 | 109.52
2017-09-23 00:30 | 123.92 | 107.41
2017-09-23 01:00 | 117.03 | 97.94
2017-09-23 01:30 | 122.95 | 105.51
2017-09-23 02:00 | 122.25 | 105.15
2017-09-23 02:30 | 118.11 | 101.19
2017-09-23 03:00 | 120.89 | 105.47
2017-09-23 03:30 | 112.39 | 96.04
2017-09-23 04:00 | 115.32 | 99.01
2017-09-23 04:30 | 110.7 | 93.34
2017-09-23 05:00 | 117.62 | 101.37
2017-09-23 05:30 | 121.14 | 104.34
2017-09-23 06:00 | 125.56 | 109.31
2017-09-23 06:30 | 113.05 | 96.7
2017-09-23 07:00 | 119.5 | 104.42
2017-09-23 07:30 | 116.85 | 101.32
2017-09-23 08:00 | 125.01 | 108.62
2017-09-23 08:30 | 123.07 | 106.97
2017-09-23 09:00 | 119.77 | 103.23
2017-09-23 09:30 | 123.56 | 106
2017-09-23 10:00 | 122.42 | 105.25
2017-09-23 10:30 | 129.55 | 111.33
2017-09-23 11:00 | 121.99 | 104.3
2017-09-23 11:30 | 121.92 | 103.62
2017-09-23 12:00 | 125.93 | 106.09
2017-09-23 12:30 | 126.23 | 108.24
2017-09-23 13:00 | 130.04 | 112.18
2017-09-23 13:30 | 127.89 | 110.55
2017-09-23 14:00 | 122.59 | 104.94
2017-09-23 14:30 | 132.98 | 114.72
2017-09-23 15:00 | 132.24 | 112.9
2017-09-23 15:30 | 134.62 | 115.82
2017-09-23 16:00 | 131.81 | 112.34
2017-09-23 16:30 | 136.25 | 117.4
2017-09-23 17:00 | 141.56 | 120.39
2017-09-23 17:30 | 141.09 | 122.16
2017-09-23 18:00 | 142.15 | 122.53
2017-09-23 18:30 | 126.47 | 105.85
2017-09-23 19:00 | 133.76 | 114.64
2017-09-23 19:30 | 136.13 | 116.79
2017-09-23 20:00 | 139.8 | 119.94
2017-09-23 20:30 | 135.17 | 114.71
2017-09-23 21:00 | 132.36 | 111.56
2017-09-23 21:30 | 124.87 | 104.29
2017-09-23 22:00 | 123.74 | 105.28
2017-09-23 22:30 | 119.02 | 101.32
2017-09-23 23:00 | 111.74 | 95.45
2017-09-23 23:30 | 114.58 | 99.49
2017-09-24 | 113.81 | 99.15
2017-09-24 00:30 | 106.16 | 90.62
2017-09-24 01:00 | 106.14 | 91.04
2017-09-24 01:30 | 101.21 | 86
2017-09-24 02:00 | 94.11 | 79.23
2017-09-24 02:30 | 99.64 | 84.96
2017-09-24 03:00 | 101.63 | 87.29
2017-09-24 03:30 | 109.11 | 93.92
2017-09-24 04:00 | 110.7 | 96.02
2017-09-24 04:30 | 115.87 | 100.65
2017-09-24 05:00 | 118.24 | 101.26
2017-09-24 05:30 | 115.02 | 99.78
2017-09-24 06:00 | 118.23 | 103.48
2017-09-24 06:30 | 107.55 | 92.3
2017-09-24 07:00 | 109.55 | 94.97
2017-09-24 07:30 | 110.39 | 95.53
2017-09-24 08:00 | 109.38 | 94.37
2017-09-24 08:30 | 116.29 | 100.78
2017-09-24 09:00 | 116.61 | 100.24
2017-09-24 09:30 | 122.3 | 106.05
2017-09-24 10:00 | 116.03 | 101.38
2017-09-24 10:30 | 115.27 | 100.3
2017-09-24 11:00 | 116.21 | 100.93
2017-09-24 11:30 | 116.49 | 98.95
2017-09-24 12:00 | 111.88 | 94.41
2017-09-24 12:30 | 115.66 | 97.97
2017-09-24 13:00 | 112.44 | 94.27
2017-09-24 13:30 | 116.27 | 97.7
2017-09-24 14:00 | 116.73 | 99.27
2017-09-24 14:30 | 117.76 | 99.33
2017-09-24 15:00 | 127.01 | 108.58
2017-09-24 15:30 | 128.82 | 110.29
2017-09-24 16:00 | 123.16 | 104.36
2017-09-24 16:30 | 118.35 | 100.52
2017-09-24 17:00 | 127.95 | 109.24
2017-09-24 17:30 | 135.18 | 117.69
2017-09-24 18:00 | 136.7 | 119.37
2017-09-24 18:30 | 124.57 | 106.09
2017-09-24 19:00 | 140.13 | 121.17
2017-09-24 19:30 | 145.15 | 126.36
2017-09-24 20:00 | 137.12 | 118.05
2017-09-24 20:30 | 126.71 | 107.42
2017-09-24 21:00 | 126.59 | 108.3
2017-09-24 21:30 | 123.88 | 105.67
2017-09-24 22:00 | 121.91 | 104.27
2017-09-24 22:30 | 134.31 | 117.01
2017-09-24 23:00 | 123.85 | 107.41
2017-09-24 23:30 | 116.2 | 100.47
2017-09-25 | 106.9 | 92.51
2017-09-25 00:30 | 107.59 | 92.8
2017-09-25 01:00 | 107.17 | 93.08
2017-09-25 01:30 | 112.71 | 100.06
2017-09-25 02:00 | 113.67 | 100.29
2017-09-25 02:30 | 110.42 | 96.81
2017-09-25 03:00 | 109.79 | 96.3
2017-09-25 03:30 | 110.83 | 97.92
2017-09-25 04:00 | 113.01 | 99.72
2017-09-25 04:30 | 109.95 | 96.29
2017-09-25 05:00 | 114.14 | 99.88
2017-09-25 05:30 | 111.07 | 96.62
2017-09-25 06:00 | 110.97 | 96.9
2017-09-25 06:30 | 102.36 | 86.43
2017-09-25 07:00 | 102.38 | 86.66
2017-09-25 07:30 | 111.94 | 97.19
2017-09-25 08:00 | 108.04 | 91.57
2017-09-25 08:30 | 115.47 | 98.89
2017-09-25 09:00 | 109.45 | 92.05
2017-09-25 09:30 | 109.98 | 92.79
2017-09-25 10:00 | 115.02 | 98.24
2017-09-25 10:30 | 116.93 | 100.11
2017-09-25 11:00 | 114.14 | 97.14
2017-09-25 11:30 | 120.16 | 102.26
2017-09-25 12:00 | 111.95 | 94.23
2017-09-25 12:30 | 108.93 | 91.56
2017-09-25 13:00 | 121.32 | 105.05
2017-09-25 13:30 | 122.46 | 107.33
2017-09-25 14:00 | 122.42 | 106.51
2017-09-25 14:30 | 122.63 | 104.69
2017-09-25 15:00 | 115.38 | 97.64
2017-09-25 15:30 | 114.95 | 98.28
2017-09-25 16:00 | 115.61 | 98.58
2017-09-25 16:30 | 117.13 | 99.24
2017-09-25 17:00 | 117.73 | 98.59
2017-09-25 17:30 | 112.4 | 93.22
2017-09-25 18:00 | 124.57 | 105.82
2017-09-25 18:30 | 122.45 | 103.14
2017-09-25 19:00 | 122.75 | 104.13
2017-09-25 19:30 | 126.54 | 107.67
2017-09-25 20:00 | 127.99 | 109.45
2017-09-25 20:30 | 121.79 | 102.92
2017-09-25 21:00 | 129.01 | 112.36
2017-09-25 21:30 | 127.66 | 109.54
2017-09-25 22:00 | 135.51 | 118.14
2017-09-25 22:30 | 126.83 | 109.16
2017-09-25 23:00 | 123.89 | 105.24
2017-09-25 23:30 | 124.96 | 106.79
2017-09-26 | 131.7 | 116.28
2017-09-26 00:30 | 120.45 | 103.94
2017-09-26 01:00 | 120.73 | 104.6
2017-09-26 01:30 | 126.01 | 109.36
2017-09-26 02:00 | 123.24 | 106.39
2017-09-26 02:30 | 126.19 | 108.59
2017-09-26 03:00 | 117.61 | 99.8
2017-09-26 03:30 | 128.28 | 111.55
2017-09-26 04:00 | 124.44 | 107.97
2017-09-26 04:30 | 122.87 | 106.77
2017-09-26 05:00 | 129.75 | 112.86
2017-09-26 05:30 | 128.66 | 112.05
2017-09-26 06:00 | 128.56 | 112
2017-09-26 06:30 | 127.42 | 109.15
2017-09-26 07:00 | 117.31 | 100.49
2017-09-26 07:30 | 127.53 | 110.01
2017-09-26 08:00 | 116.84 | 99.1
2017-09-26 08:30 | 121.21 | 103.85
2017-09-26 09:00 | 112.85 | 94.82
2017-09-26 09:30 | 107.45 | 90.22
2017-09-26 10:00 | 98.1 | 83.83
2017-09-26 10:30 | 97.48 | 82.21
2017-09-26 11:00 | 100.21 | 85.45
2017-09-26 11:30 | 97.07 | 81.96
2017-09-26 12:00 | 106.78 | 92.37
2017-09-26 12:30 | 113.12 | 96.93
2017-09-26 13:00 | 114.86 | 98.05
2017-09-26 13:30 | 107.13 | 91.62
2017-09-26 14:00 | 109.48 | 91.97
2017-09-26 14:30 | 112.95 | 96.35
2017-09-26 15:00 | 114.81 | 96.59
2017-09-26 15:30 | 114.94 | 95.97
2017-09-26 16:00 | 114.31 | 95.76
2017-09-26 16:30 | 120.78 | 102.8
2017-09-26 17:00 | 124.72 | 107.59
2017-09-26 17:30 | 123.12 | 105.47
2017-09-26 18:00 | 125.03 | 106.66
2017-09-26 18:30 | 115.54 | 97.36
2017-09-26 19:00 | 126.83 | 110.55
2017-09-26 19:30 | 118.63 | 105.85
2017-09-26 20:00 | 116.47 | 103.16
2017-09-26 20:30 | 128.3 | 112.17
2017-09-26 21:00 | 125.12 | 108.3
2017-09-26 21:30 | 124.2 | 107.9
2017-09-26 22:00 | 120.6 | 103.5
2017-09-26 22:30 | 128.21 | 110.6
2017-09-26 23:00 | 126.63 | 109
2017-09-26 23:30 | 124.84 | 106.22
2017-09-27 | 133.37 | 116.05
2017-09-27 00:30 | 132.95 | 115.74
2017-09-27 01:00 | 122.31 | 104.91
2017-09-27 01:30 | 129.35 | 111.33
2017-09-27 02:00 | 131.58 | 113.53
2017-09-27 02:30 | 127.97 | 108.76
2017-09-27 03:00 | 121.76 | 103.38
2017-09-27 03:30 | 127.22 | 108.56
2017-09-27 04:00 | 130.53 | 113.28
2017-09-27 04:30 | 124.01 | 107.81
2017-09-27 05:00 | 129.67 | 113.08
2017-09-27 05:30 | 123.4 | 106.18
2017-09-27 06:00 | 122.64 | 106.8
2017-09-27 06:30 | 112.72 | 96.12
2017-09-27 07:00 | 116.92 | 101.18
2017-09-27 07:30 | 122.98 | 108.47
2017-09-27 08:00 | 112.91 | 97.53
2017-09-27 08:30 | 111.02 | 94.04
2017-09-27 09:00 | 111.59 | 94.21
2017-09-27 09:30 | 112.82 | 96.66
2017-09-27 10:00 | 103.32 | 89.79
2017-09-27 10:30 | 108.35 | 95.5
2017-09-27 11:00 | 111.7 | 98.6
2017-09-27 11:30 | 108.14 | 93.69
2017-09-27 12:00 | 96.25 | 81.54
2017-09-27 12:30 | 99.18 | 84.21
2017-09-27 13:00 | 95.17 | 79.74
2017-09-27 13:30 | 100.38 | 85.77
2017-09-27 14:00 | 111.87 | 97.22
2017-09-27 14:30 | 108.13 | 92.56
2017-09-27 15:00 | 110.97 | 93.54
2017-09-27 15:30 | 117.82 | 100.81
2017-09-27 16:00 | 122.92 | 106.44
2017-09-27 16:30 | 121.9 | 103.86
2017-09-27 17:00 | 132.12 | 112.53
2017-09-27 17:30 | 129.15 | 109.26
2017-09-27 18:00 | 132.72 | 114.15
2017-09-27 18:30 | 123.63 | 104.53
2017-09-27 19:00 | 130.84 | 112.45
2017-09-27 19:30 | 128.72 | 110.48
2017-09-27 20:00 | 134.11 | 115.24
2017-09-27 20:30 | 127.59 | 106.55
2017-09-27 21:00 | 126.19 | 106.04
2017-09-27 21:30 | 123.26 | 104.08
2017-09-27 22:00 | 126.04 | 108.82
2017-09-27 22:30 | 123.38 | 106.85
2017-09-27 23:00 | 124.69 | 108.56
2017-09-27 23:30 | 118.24 | 102.23
2017-09-28 | 118.75 | 102.86
2017-09-28 00:30 | 127.21 | 112.48
2017-09-28 01:00 | 128.1 | 112.93
2017-09-28 01:30 | 126.54 | 112.5
2017-09-28 02:00 | 122.09 | 108.43
2017-09-28 02:30 | 119.9 | 105.92
2017-09-28 03:00 | 114.71 | 100.01
2017-09-28 03:30 | 119.74 | 104.82
2017-09-28 04:00 | 115.89 | 99.21
2017-09-28 04:30 | 117.35 | 101.45
2017-09-28 05:00 | 120.27 | 104.44
2017-09-28 05:30 | 126.74 | 110.31
2017-09-28 06:00 | 126.31 | 109.96
2017-09-28 06:30 | 115.28 | 97.05
2017-09-28 07:00 | 116.32 | 100.57
2017-09-28 07:30 | 118.57 | 101.67
2017-09-28 08:00 | 114.32 | 97.77
2017-09-28 08:30 | 120.24 | 103.56
2017-09-28 09:00 | 116.5 | 98.52
2017-09-28 09:30 | 111.74 | 92.8
2017-09-28 10:00 | 118.15 | 100.42
2017-09-28 10:30 | 122.22 | 104.91
2017-09-28 11:00 | 122.64 | 104.91
2017-09-28 11:30 | 123.67 | 105.43
2017-09-28 12:00 | 120.96 | 102.58
2017-09-28 12:30 | 131.27 | 111.99
2017-09-28 13:00 | 132.28 | 113.71
2017-09-28 13:30 | 124.91 | 106.48
2017-09-28 14:00 | 132.52 | 113.78
2017-09-28 14:30 | 126.52 | 107.16
2017-09-28 15:00 | 127.72 | 107.68
2017-09-28 15:30 | 129.63 | 110.71
2017-09-28 16:00 | 130.72 | 110.96
2017-09-28 16:30 | 128.05 | 108.55
2017-09-28 17:00 | 125.84 | 105.49
2017-09-28 17:30 | 130.39 | 108.45
2017-09-28 18:00 | 128.5 | 107.4
2017-09-28 18:30 | 126.16 | 103.19
2017-09-28 19:00 | 129.61 | 106.58
2017-09-28 19:30 | 128.22 | 108.58
2017-09-28 20:00 | 129.26 | 108.29
2017-09-28 20:30 | 131.9 | 110.58
2017-09-28 21:00 | 136.87 | 118.43
2017-09-28 21:30 | 122.78 | 104.23
2017-09-28 22:00 | 121.08 | 103.09
2017-09-28 22:30 | 124.96 | 107.2
2017-09-28 23:00 | 128.03 | 111.21
2017-09-28 23:30 | 125.87 | 108.63
2017-09-29 | 126.42 | 109.32
2017-09-29 00:30 | 130.01 | 112.89
2017-09-29 01:00 | 125.34 | 108.85
2017-09-29 01:30 | 123.68 | 106.26
2017-09-29 02:00 | 120.27 | 103.14
2017-09-29 02:30 | 118.73 | 101.99
2017-09-29 03:00 | 120.08 | 103.79
2017-09-29 03:30 | 117.4 | 100.41
2017-09-29 04:00 | 114.12 | 97
2017-09-29 04:30 | 122.84 | 107.19
2017-09-29 05:00 | 115.79 | 99.65
2017-09-29 05:30 | 118.51 | 102.54
2017-09-29 06:00 | 117.05 | 101.59
2017-09-29 06:30 | 115.34 | 99
2017-09-29 07:00 | 121.48 | 105.77
2017-09-29 07:30 | 124.55 | 107.02
2017-09-29 08:00 | 130.58 | 112.91
2017-09-29 08:30 | 121.29 | 104.96
2017-09-29 09:00 | 137.35 | 120.3
2017-09-29 09:30 | 127.69 | 109.78
2017-09-29 10:00 | 126.54 | 108.45
2017-09-29 10:30 | 123.77 | 104.54
2017-09-29 11:00 | 124.7 | 105.31
2017-09-29 11:30 | 115.95 | 96.11
2017-09-29 12:00 | 118.65 | 99.49
2017-09-29 12:30 | 118.89 | 99.98
2017-09-29 13:00 | 125.74 | 107.56
2017-09-29 13:30 | 122.42 | 103.93
2017-09-29 14:00 | 124.05 | 106.54
2017-09-29 14:30 | 122.03 | 103.4
2017-09-29 15:00 | 117.76 | 98.62
2017-09-29 15:30 | 116.53 | 96.99
2017-09-29 16:00 | 120.7 | 101.44
2017-09-29 16:30 | 122.98 | 105.38
2017-09-29 17:00 | 126.51 | 109.42
2017-09-29 17:30 | 131.07 | 113.97
2017-09-29 18:00 | 137.06 | 118.78
2017-09-29 18:30 | 125.4 | 105.24
2017-09-29 19:00 | 129.47 | 110.73
2017-09-29 19:30 | 137.52 | 118.96
2017-09-29 20:00 | 134.26 | 114.59
2017-09-29 20:30 | 141.18 | 123.02
2017-09-29 21:00 | 132.91 | 115.2
2017-09-29 21:30 | 132.22 | 113.11
2017-09-29 22:00 | 128.86 | 110.85
2017-09-29 22:30 | 124.14 | 107.16
2017-09-29 23:00 | 120.19 | 103.41
2017-09-29 23:30 | 122.48 | 105.52
2017-09-30 | 124.38 | 107.7
2017-09-30 00:30 | 122.9 | 106.01
2017-09-30 01:00 | 117.35 | 99.7
2017-09-30 01:30 | 121.35 | 104.04
2017-09-30 02:00 | 123.56 | 106.56
2017-09-30 02:30 | 125.28 | 108.59
2017-09-30 03:00 | 123.96 | 107.05
2017-09-30 03:30 | 129.63 | 113.58
2017-09-30 04:00 | 119.82 | 103.56
2017-09-30 04:30 | 120.64 | 103.83
2017-09-30 05:00 | 119.21 | 103.35
2017-09-30 05:30 | 118.83 | 102.57
2017-09-30 06:00 | 113.73 | 97.79
2017-09-30 06:30 | 108.04 | 92.05
2017-09-30 07:00 | 116.24 | 100.39
2017-09-30 07:30 | 118.52 | 100.28
2017-09-30 08:00 | 116.69 | 97.37
2017-09-30 08:30 | 116.69 | 98.5
2017-09-30 09:00 | 116.19 | 97.31
2017-09-30 09:30 | 124.95 | 105.68
2017-09-30 10:00 | 118.13 | 99.54
2017-09-30 10:30 | 119.56 | 99.29
2017-09-30 11:00 | 121.81 | 100.94
2017-09-30 11:30 | 114.43 | 96.07
2017-09-30 12:00 | 114.78 | 95.15
2017-09-30 12:30 | 121.48 | 101.31
2017-09-30 13:00 | 127.32 | 108.07
2017-09-30 13:30 | 123.13 | 102.28
2017-09-30 14:00 | 124.55 | 104.77
2017-09-30 14:30 | 123.07 | 102.36
2017-09-30 15:00 | 124.13 | 102.74
2017-09-30 15:30 | 127.6 | 106.49
2017-09-30 16:00 | 129.07 | 109.03
2017-09-30 16:30 | 130.54 | 111.86
2017-09-30 17:00 | 124.17 | 106.14
2017-09-30 17:30 | 136.2 | 117.03
2017-09-30 18:00 | 131.79 | 111.54
2017-09-30 18:30 | 124.07 | 103.54
2017-09-30 19:00 | 121.1 | 102.09
2017-09-30 19:30 | 122.86 | 103.93
2017-09-30 20:00 | 129.23 | 110.28
2017-09-30 20:30 | 125.25 | 105.7
2017-09-30 21:00 | 123.61 | 104.79
2017-09-30 21:30 | 114.75 | 97.13
2017-09-30 22:00 | 121.44 | 103.44
2017-09-30 22:30 | 122.45 | 101.98
2017-09-30 23:00 | 125.64 | 107.69
2017-09-30 23:30 | 120.41 | 103.7
2017-10-01 | 118.25 | 102.02
2017-10-01 00:30 | 121.16 | 105.04
2017-10-01 01:00 | 120.87 | 104.02
2017-10-01 01:30 | 125.33 | 108.88
2017-10-01 02:00 | 119.6 | 102.17
2017-10-01 02:30 | 120.63 | 102.61
2017-10-01 03:00 | 119.46 | 102.97
2017-10-01 03:30 | 111.54 | 93.66
2017-10-01 04:00 | 112.22 | 94.04
2017-10-01 04:30 | 108.36 | 90.64
2017-10-01 05:00 | 119.17 | 101.78
2017-10-01 05:30 | 120.34 | 102.69
2017-10-01 06:00 | 126.51 | 111.64
2017-10-01 06:30 | 119.74 | 104.11
2017-10-01 07:00 | 113.92 | 98.62
2017-10-01 07:30 | 122.87 | 108.34
2017-10-01 08:00 | 118.34 | 101.69
2017-10-01 08:30 | 120.74 | 102.92
2017-10-01 09:00 | 119.97 | 101.82
2017-10-01 09:30 | 118.87 | 100.27
2017-10-01 10:00 | 116.63 | 100.3
2017-10-01 10:30 | 108.71 | 93.16
2017-10-01 11:00 | 106.92 | 92.27
2017-10-01 11:30 | 114.69 | 100.97
2017-10-01 12:00 | 114.79 | 101.15
2017-10-01 12:30 | 117.2 | 102.65
2017-10-01 13:00 | 116.25 | 102.9
2017-10-01 13:30 | 112.22 | 97.51
2017-10-01 14:00 | 106.73 | 93.47
2017-10-01 14:30 | 100.81 | 86.71
2017-10-01 15:00 | 94.6 | 81.29
2017-10-01 15:30 | 96.41 | 82.82
2017-10-01 16:00 | 91.93 | 78.15
2017-10-01 16:30 | 96.05 | 83.66
2017-10-01 17:00 | 95.97 | 83.53
2017-10-01 17:30 | 91.98 | 77.35
2017-10-01 18:00 | 91.24 | 74.73
2017-10-01 18:30 | 85.02 | 68.7
2017-10-01 19:00 | 91.35 | 77.56
2017-10-01 19:30 | 95.83 | 82.43
2017-10-01 20:00 | 93.22 | 80.08
2017-10-01 20:30 | 90.89 | 78.61
2017-10-01 21:00 | 92.05 | 79.3
2017-10-01 21:30 | 100.34 | 88.35
2017-10-01 22:00 | 98.39 | 86.4
2017-10-01 22:30 | 104.01 | 92.87
2017-10-01 23:00 | 101.46 | 89.63
2017-10-01 23:30 | 95.64 | 82.22
2017-10-02 | 95.08 | 81.84
2017-10-02 00:30 | 92.3 | 78.85
2017-10-02 01:00 | 89.22 | 75.5
2017-10-02 01:30 | 94.41 | 81.05
2017-10-02 02:00 | 98.1 | 86.1
2017-10-02 02:30 | 99.01 | 86.17
2017-10-02 03:00 | 93.48 | 79.91
2017-10-02 03:30 | 99.14 | 87.04
2017-10-02 04:00 | 100.67 | 89.49
2017-10-02 04:30 | 98.63 | 86.11
2017-10-02 05:00 | 95.97 | 83.17
2017-10-02 05:30 | 88.18 | 74.54
2017-10-02 06:00 | 89.1 | 75.18
2017-10-02 06:30 | 84.3 | 68.07
2017-10-02 07:00 | 90.18 | 75.76
2017-10-02 07:30 | 92.3 | 78.78
2017-10-02 08:00 | 89.97 | 76.41
2017-10-02 08:30 | 96.31 | 83.58
2017-10-02 09:00 | 104.87 | 92.23
2017-10-02 09:30 | 97.59 | 84.56
2017-10-02 10:00 | 89.89 | 76.56
2017-10-02 10:30 | 83.28 | 69.66
2017-10-02 11:00 | 89.08 | 74.66
2017-10-02 11:30 | 95 | 81.19
2017-10-02 12:00 | 104.11 | 92.25
2017-10-02 12:30 | 96.56 | 83.29
2017-10-02 13:00 | 96.57 | 82.44
2017-10-02 13:30 | 92.09 | 76.26
2017-10-02 14:00 | 85.87 | 69.53
2017-10-02 14:30 | 86.79 | 71.35
2017-10-02 15:00 | 90.45 | 75.57
2017-10-02 15:30 | 84.65 | 69.77
2017-10-02 16:00 | 80.77 | 66.79
2017-10-02 16:30 | 86.3 | 74.16
2017-10-02 17:00 | 83.34 | 70.5
2017-10-02 17:30 | 82.72 | 68.97
2017-10-02 18:00 | 88.22 | 75.59
2017-10-02 18:30 | 85.91 | 71.95
2017-10-02 19:00 | 90.22 | 76.32
2017-10-02 19:30 | 86.91 | 73.16
2017-10-02 20:00 | 83.9 | 70.54
2017-10-02 20:30 | 77.2 | 63.06
2017-10-02 21:00 | 77.13 | 63.35
2017-10-02 21:30 | 80.71 | 65.21
2017-10-02 22:00 | 80.83 | 65.23
2017-10-02 22:30 | 80.43 | 63.66
2017-10-02 23:00 | 88.22 | 71.94
2017-10-02 23:30 | 91.65 | 74.7
2017-10-03 | 89.18 | 71.84
2017-10-03 00:30 | 88.02 | 72.14
2017-10-03 01:00 | 87.46 | 68.08
2017-10-03 01:30 | 87.91 | 69.12
2017-10-03 02:00 | 88.79 | 70.1
2017-10-03 02:30 | 82.22 | 60.74
2017-10-03 03:00 | 83.53 | 63.27
2017-10-03 03:30 | 86.94 | 68.79
2017-10-03 04:00 | 91.84 | 77.63
2017-10-03 04:30 | 85.28 | 69.99
2017-10-03 05:00 | 84.08 | 67.71
2017-10-03 05:30 | 81.94 | 64.88
2017-10-03 06:00 | 83.87 | 67.36
2017-10-03 06:30 | 80.52 | 63.05
2017-10-03 07:00 | 81.5 | 63.87
2017-10-03 07:30 | 85.41 | 69.76
2017-10-03 08:00 | 88.83 | 74.99
2017-10-03 08:30 | 79.93 | 63.35
2017-10-03 09:00 | 81.12 | 66.75
2017-10-03 09:30 | 81.8 | 65.17
2017-10-03 10:00 | 82.58 | 66.45
2017-10-03 10:30 | 86.47 | 69.84
2017-10-03 11:00 | 90.01 | 74.23
2017-10-03 11:30 | 94.85 | 80.18
2017-10-03 12:00 | 100.24 | 87
2017-10-03 12:30 | 95.98 | 82.21
2017-10-03 13:00 | 93.2 | 80.42
2017-10-03 13:30 | 92.33 | 79.94
2017-10-03 14:00 | 91.22 | 79.12
2017-10-03 14:30 | 92.72 | 80.91
2017-10-03 15:00 | 85.54 | 72.23
2017-10-03 15:30 | 90.59 | 79
2017-10-03 16:00 | 101.62 | 90.72
2017-10-03 16:30 | 100.82 | 89.56
2017-10-03 17:00 | 97.68 | 86.24
2017-10-03 17:30 | 103.77 | 92.36
2017-10-03 18:00 | 100.65 | 89.67
2017-10-03 18:30 | 96.99 | 85
2017-10-03 19:00 | 98 | 84.88
2017-10-03 19:30 | 105.9 | 92.81
2017-10-03 20:00 | 98.46 | 85.41
2017-10-03 20:30 | 101.55 | 88.5
2017-10-03 21:00 | 102.11 | 89.39
2017-10-03 21:30 | 104.9 | 92.67
2017-10-03 22:00 | 103.09 | 90.94
2017-10-03 22:30 | 96.06 | 83.48
2017-10-03 23:00 | 100.79 | 88.73
2017-10-03 23:30 | 99.22 | 87.11
2017-10-04 | 98.28 | 87.21
2017-10-04 00:30 | 98.24 | 86.75
2017-10-04 01:00 | 98.37 | 86.87
2017-10-04 01:30 | 102.18 | 91
2017-10-04 02:00 | 99.77 | 87.98
2017-10-04 02:30 | 104.75 | 92.89
2017-10-04 03:00 | 95.84 | 84.14
2017-10-04 03:30 | 88.72 | 77.32
2017-10-04 04:00 | 97.58 | 86.43
2017-10-04 04:30 | 94.39 | 82.96
2017-10-04 05:00 | 97.76 | 86.22
2017-10-04 05:30 | 98.85 | 87.17
2017-10-04 06:00 | 92.39 | 81.06
2017-10-04 06:30 | 85.66 | 74.26
2017-10-04 07:00 | 88.02 | 76.33
2017-10-04 07:30 | 91.91 | 79.91
2017-10-04 08:00 | 87.5 | 75.25
2017-10-04 08:30 | 91.46 | 78.21
2017-10-04 09:00 | 98 | 84.67
2017-10-04 09:30 | 101.63 | 87.79
2017-10-04 10:00 | 95.82 | 81.9
2017-10-04 10:30 | 100.43 | 80
2017-10-04 11:00 | 98.93 | 77.96
2017-10-04 11:30 | 96.48 | 75.55
2017-10-04 12:00 | 102.83 | 80.65
2017-10-04 12:30 | 107.45 | 84.85
2017-10-04 13:00 | 109.9 | 85.67
2017-10-04 13:30 | 113.71 | 88.85
2017-10-04 14:00 | 105.23 | 80.9
2017-10-04 14:30 | 105.64 | 80.17
2017-10-04 15:00 | 104.61 | 78.23
2017-10-04 15:30 | 112.16 | 88.17
2017-10-04 16:00 | 112.12 | 85.99
2017-10-04 16:30 | 107.6 | 82.6
2017-10-04 17:00 | 111.44 | 87.43
2017-10-04 17:30 | 115.03 | 92.87
2017-10-04 18:00 | 113.01 | 89.23
2017-10-04 18:30 | 115.34 | 92.17
2017-10-04 19:00 | 115.85 | 93.47
2017-10-04 19:30 | 124.11 | 101.61
2017-10-04 20:00 | 115.57 | 92.2
2017-10-04 20:30 | 114.3 | 92.55
2017-10-04 21:00 | 112.07 | 90.66
2017-10-04 21:30 | 112.46 | 89.71
2017-10-04 22:00 | 119.66 | 96.21
2017-10-04 22:30 | 119.24 | 95.19
2017-10-04 23:00 | 121.27 | 99.24
2017-10-04 23:30 | 121.52 | 100.57
2017-10-05 | 120.76 | 99.98
2017-10-05 00:30 | 116.47 | 96.22
2017-10-05 01:00 | 121.14 | 99.99
2017-10-05 01:30 | 119.07 | 97.77
2017-10-05 02:00 | 122.22 | 100.85
2017-10-05 02:30 | 115.82 | 93.16
2017-10-05 03:00 | 110.46 | 87.87
2017-10-05 03:30 | 108.62 | 85.56
2017-10-05 04:00 | 114.25 | 93.35
2017-10-05 04:30 | 116.27 | 93.24
2017-10-05 05:00 | 120.75 | 97.15
2017-10-05 05:30 | 125.23 | 103.67
2017-10-05 06:00 | 123.27 | 102.1
2017-10-05 06:30 | 106.55 | 82.05
2017-10-05 07:00 | 115.01 | 91.35
2017-10-05 07:30 | 117.91 | 93.32
2017-10-05 08:00 | 113.18 | 88.71
2017-10-05 08:30 | 119.1 | 94.46
2017-10-05 09:00 | 120.84 | 97.24
2017-10-05 09:30 | 118.15 | 95.12
2017-10-05 10:00 | 118.54 | 95.11
2017-10-05 10:30 | 118.11 | 95.06
2017-10-05 11:00 | 123.71 | 100.14
2017-10-05 11:30 | 115.64 | 91.13
2017-10-05 12:00 | 119.77 | 96.43
2017-10-05 12:30 | 123.66 | 100.1
2017-10-05 13:00 | 114.97 | 90.75
2017-10-05 13:30 | 114.93 | 90.65
2017-10-05 14:00 | 114.65 | 90.29
2017-10-05 14:30 | 121.14 | 98.91
2017-10-05 15:00 | 115.97 | 93.23
2017-10-05 15:30 | 115.72 | 92.46
2017-10-05 16:00 | 115.4 | 93.79
2017-10-05 16:30 | 104.87 | 84.01
2017-10-05 17:00 | 99.55 | 76.31
2017-10-05 17:30 | 108.56 | 87.41
2017-10-05 18:00 | 110.61 | 89.91
2017-10-05 18:30 | 109.43 | 87.3
2017-10-05 19:00 | 113.51 | 91.62
2017-10-05 19:30 | 119.97 | 97.93
2017-10-05 20:00 | 122.74 | 100.46
2017-10-05 20:30 | 120.4 | 99.92
2017-10-05 21:00 | 119.75 | 98.53
2017-10-05 21:30 | 117.59 | 96.84
2017-10-05 22:00 | 115.72 | 95.05
2017-10-05 22:30 | 119.37 | 97.86
2017-10-05 23:00 | 124.6 | 102.7
2017-10-05 23:30 | 117.79 | 95.33
2017-10-06 | 121.09 | 99.99
2017-10-06 00:30 | 123.26 | 101.76
2017-10-06 01:00 | 122.09 | 100.82
2017-10-06 01:30 | 118.78 | 96.9
2017-10-06 02:00 | 119.84 | 98.16
2017-10-06 02:30 | 119.73 | 97.85
2017-10-06 03:00 | 118.38 | 95.91
2017-10-06 03:30 | 118.58 | 95.66
2017-10-06 04:00 | 120.94 | 100.52
2017-10-06 04:30 | 118.53 | 97.96
2017-10-06 05:00 | 119.54 | 99.23
2017-10-06 05:30 | 117.33 | 96.87
2017-10-06 06:00 | 121.88 | 101.12
2017-10-06 06:30 | 114.51 | 92.45
2017-10-06 07:00 | 120.89 | 99.04
2017-10-06 07:30 | 119 | 97.46
2017-10-06 08:00 | 119.49 | 97.3
2017-10-06 08:30 | 121.46 | 99.58
2017-10-06 09:00 | 121.29 | 99.39
2017-10-06 09:30 | 124.84 | 103.18
2017-10-06 10:00 | 113.42 | 91.23
2017-10-06 10:30 | 119.4 | 97.99
2017-10-06 11:00 | 116.14 | 95.41
2017-10-06 11:30 | 110.45 | 88.92
2017-10-06 12:00 | 117.57 | 97.02
2017-10-06 12:30 | 121.28 | 101.51
2017-10-06 13:00 | 116.1 | 96.58
2017-10-06 13:30 | 108.02 | 89.1
2017-10-06 14:00 | 114.19 | 93.3
2017-10-06 14:30 | 111.26 | 89.53
2017-10-06 15:00 | 109.06 | 88.48
2017-10-06 15:30 | 107.49 | 86.67
2017-10-06 16:00 | 120.41 | 101.44
2017-10-06 16:30 | 112.33 | 93.28
2017-10-06 17:00 | 115.74 | 95.95
2017-10-06 17:30 | 121.67 | 101.44
2017-10-06 18:00 | 133.03 | 110.62
2017-10-06 18:30 | 120.7 | 95.53
2017-10-06 19:00 | 133.38 | 110.42
2017-10-06 19:30 | 132.87 | 111.16
2017-10-06 20:00 | 134.27 | 111.83
2017-10-06 20:30 | 128.52 | 106.05
2017-10-06 21:00 | 124.61 | 101.07
2017-10-06 21:30 | 125.17 | 101.84
2017-10-06 22:00 | 125.17 | 101.32
2017-10-06 22:30 | 123.45 | 99.45
2017-10-06 23:00 | 115.21 | 90.7
2017-10-06 23:30 | 112.76 | 88.96
2017-10-07 | 117.02 | 96.56
2017-10-07 00:30 | 120.53 | 99.2
2017-10-07 01:00 | 117.64 | 96.14
2017-10-07 01:30 | 121.37 | 100.43
2017-10-07 02:00 | 116.55 | 96.8
2017-10-07 02:30 | 107.67 | 86.81
2017-10-07 03:00 | 109.31 | 89.26
2017-10-07 03:30 | 110.58 | 88.96
2017-10-07 04:00 | 113.27 | 91.24
2017-10-07 04:30 | 119.63 | 97.49
2017-10-07 05:00 | 119.13 | 96.53
2017-10-07 05:30 | 121.05 | 99.39
2017-10-07 06:00 | 118.95 | 97.01
2017-10-07 06:30 | 107.76 | 84.67
2017-10-07 07:00 | 110.82 | 89.78
2017-10-07 07:30 | 114.74 | 92.73
2017-10-07 08:00 | 116.6 | 94.49
2017-10-07 08:30 | 115.3 | 93.81
2017-10-07 09:00 | 114.79 | 92.39
2017-10-07 09:30 | 117.69 | 95.96
2017-10-07 10:00 | 114.18 | 92.63
2017-10-07 10:30 | 111.77 | 90.25
2017-10-07 11:00 | 118.81 | 96.45
2017-10-07 11:30 | 112.78 | 91.18
2017-10-07 12:00 | 120.41 | 99.99
2017-10-07 12:30 | 126.8 | 103.23
2017-10-07 13:00 | 119.79 | 96.13
2017-10-07 13:30 | 122.5 | 99.35
2017-10-07 14:00 | 126.68 | 101.67
2017-10-07 14:30 | 129.41 | 105.28
2017-10-07 15:00 | 128.38 | 104.33
2017-10-07 15:30 | 121.75 | 95.98
2017-10-07 16:00 | 123.72 | 95.16
2017-10-07 16:30 | 123.17 | 94.27
2017-10-07 17:00 | 127.73 | 97.27
2017-10-07 17:30 | 129.46 | 100.31
2017-10-07 18:00 | 123.45 | 94.17
2017-10-07 18:30 | 121.18 | 91.58
2017-10-07 19:00 | 122.03 | 93.88
2017-10-07 19:30 | 122.39 | 95.19
2017-10-07 20:00 | 123.59 | 96.54
2017-10-07 20:30 | 128.23 | 102.36
2017-10-07 21:00 | 124.55 | 98.64
2017-10-07 21:30 | 123.27 | 98.6
2017-10-07 22:00 | 119.21 | 94.78
2017-10-07 22:30 | 120.74 | 96.99
2017-10-07 23:00 | 118.27 | 94.26
2017-10-07 23:30 | 105.43 | 78.84
2017-10-08 | 111.26 | 85.54
2017-10-08 00:30 | 114.2 | 90.22
2017-10-08 01:00 | 103.97 | 82.16
2017-10-08 01:30 | 109.61 | 90.19
2017-10-08 02:00 | 115.55 | 96.86
2017-10-08 02:30 | 103.64 | 84.01
2017-10-08 03:00 | 107.79 | 87.91
2017-10-08 03:30 | 109.76 | 90.55
2017-10-08 04:00 | 110.82 | 92.93
2017-10-08 04:30 | 114.19 | 96.61
2017-10-08 05:00 | 119.25 | 100.48
2017-10-08 05:30 | 109.45 | 90.54
2017-10-08 06:00 | 108.33 | 88.3
2017-10-08 06:30 | 96.36 | 73.69
2017-10-08 07:00 | 105.09 | 84.87
2017-10-08 07:30 | 112.01 | 90.9
2017-10-08 08:00 | 108.02 | 86.36
2017-10-08 08:30 | 105.34 | 83.83
2017-10-08 09:00 | 105.85 | 83.54
2017-10-08 09:30 | 111.19 | 89.93
2017-10-08 10:00 | 115.17 | 93.64
2017-10-08 10:30 | 110.44 | 88.99
2017-10-08 11:00 | 112.34 | 90.84
2017-10-08 11:30 | 115.23 | 93.18
2017-10-08 12:00 | 118.23 | 95.07
2017-10-08 12:30 | 128.51 | 105.94
2017-10-08 13:00 | 125.62 | 101.61
2017-10-08 13:30 | 123.93 | 98.22
2017-10-08 14:00 | 127.54 | 101.35
2017-10-08 14:30 | 127.02 | 99.75
2017-10-08 15:00 | 122.2 | 95.36
2017-10-08 15:30 | 127.01 | 100.38
2017-10-08 16:00 | 116.91 | 92.13
2017-10-08 16:30 | 120.25 | 94.47
2017-10-08 17:00 | 128.02 | 103.17
2017-10-08 17:30 | 127.37 | 102.22
2017-10-08 18:00 | 123.91 | 99.25
2017-10-08 18:30 | 116.7 | 87.89
2017-10-08 19:00 | 122.65 | 96.83
2017-10-08 19:30 | 132.32 | 105.97
2017-10-08 20:00 | 127.33 | 101.13
2017-10-08 20:30 | 126.52 | 100.68
2017-10-08 21:00 | 121.8 | 96.57
2017-10-08 21:30 | 121.34 | 97.48
2017-10-08 22:00 | 124.77 | 100.55
2017-10-08 22:30 | 121.42 | 97.42
2017-10-08 23:00 | 121.43 | 96.22
2017-10-08 23:30 | 115.36 | 92.1
2017-10-09 | 112.02 | 88.8
2017-10-09 00:30 | 116.21 | 92.25
2017-10-09 01:00 | 116.58 | 93.65
2017-10-09 01:30 | 118.93 | 95.67
2017-10-09 02:00 | 120.58 | 98.13
2017-10-09 02:30 | 122.37 | 99.84
2017-10-09 03:00 | 113.4 | 91.98
2017-10-09 03:30 | 109.43 | 87.29
2017-10-09 04:00 | 108.05 | 85.35
2017-10-09 04:30 | 118.61 | 98.13
2017-10-09 05:00 | 115.94 | 94.26
2017-10-09 05:30 | 111.58 | 89.69
2017-10-09 06:00 | 112.42 | 91.65
2017-10-09 06:30 | 101.71 | 78.19
2017-10-09 07:00 | 108.47 | 86.28
2017-10-09 07:30 | 109.06 | 87.13
2017-10-09 08:00 | 111.68 | 88.25
2017-10-09 08:30 | 111.21 | 87.85
2017-10-09 09:00 | 114.12 | 88.49
2017-10-09 09:30 | 116.21 | 91.92
2017-10-09 10:00 | 113.87 | 89.27
2017-10-09 10:30 | 107.15 | 80.97
2017-10-09 11:00 | 105.94 | 79.19
2017-10-09 11:30 | 109.12 | 84.92
2017-10-09 12:00 | 114.15 | 89.14
2017-10-09 12:30 | 120.12 | 94.16
2017-10-09 13:00 | 114.65 | 87.53
2017-10-09 13:30 | 116.58 | 90.52
2017-10-09 14:00 | 124.53 | 98.85
2017-10-09 14:30 | 129.5 | 103.6
2017-10-09 15:00 | 130.18 | 103.5
2017-10-09 15:30 | 124.08 | 95.88
2017-10-09 16:00 | 134.23 | 109.07
2017-10-09 16:30 | 131.25 | 104.58
2017-10-09 17:00 | 124.03 | 97.86
2017-10-09 17:30 | 131.59 | 106.27
2017-10-09 18:00 | 130.38 | 107.23
2017-10-09 18:30 | 120.2 | 92.7
2017-10-09 19:00 | 122.01 | 98.23
2017-10-09 19:30 | 125.52 | 102.14
2017-10-09 20:00 | 120.64 | 95.77
2017-10-09 20:30 | 118.87 | 94.32
2017-10-09 21:00 | 113.2 | 86.87
2017-10-09 21:30 | 120.89 | 95.47
2017-10-09 22:00 | 115.99 | 92.31
2017-10-09 22:30 | 112.88 | 89.12
2017-10-09 23:00 | 109.06 | 85.89
2017-10-09 23:30 | 113.89 | 91.42
2017-10-10 | 116.28 | 94.13
2017-10-10 00:30 | 115.8 | 95.19
2017-10-10 01:00 | 111.13 | 89.5
2017-10-10 01:30 | 108.82 | 89.47
2017-10-10 02:00 | 102.94 | 83.77
2017-10-10 02:30 | 107.39 | 88.27
2017-10-10 03:00 | 111.93 | 94.59
2017-10-10 03:30 | 102.79 | 83.35
2017-10-10 04:00 | 97.47 | 78.26
2017-10-10 04:30 | 106.92 | 89.39
2017-10-10 05:00 | 105.87 | 88.45
2017-10-10 05:30 | 94.33 | 75.82
2017-10-10 06:00 | 92.85 | 74.3
2017-10-10 06:30 | 84.31 | 63.98
2017-10-10 07:00 | 85.56 | 65.53
2017-10-10 07:30 | 88.72 | 69.49
2017-10-10 08:00 | 89.76 | 72.01
2017-10-10 08:30 | 83.34 | 64.43
2017-10-10 09:00 | 87.6 | 69.85
2017-10-10 09:30 | 94.91 | 77.52
2017-10-10 10:00 | 91.24 | 72.53
2017-10-10 10:30 | 88.93 | 69.48
2017-10-10 11:00 | 90.46 | 70.67
2017-10-10 11:30 | 98.58 | 79.86
2017-10-10 12:00 | 106.76 | 89.13
2017-10-10 12:30 | 106.2 | 87.69
2017-10-10 13:00 | 107.27 | 88.79
2017-10-10 13:30 | 106.99 | 87.6
2017-10-10 14:00 | 109.91 | 90.45
2017-10-10 14:30 | 103.19 | 83.29
2017-10-10 15:00 | 116.72 | 96.82
2017-10-10 15:30 | 117.75 | 97.27
2017-10-10 16:00 | 114.91 | 93.93
2017-10-10 16:30 | 112.83 | 91.55
2017-10-10 17:00 | 119.83 | 99.33
2017-10-10 17:30 | 117.89 | 98.41
2017-10-10 18:00 | 116.61 | 97.87
2017-10-10 18:30 | 110.36 | 89.55
2017-10-10 19:00 | 107.71 | 86.84
2017-10-10 19:30 | 112.87 | 93.4
2017-10-10 20:00 | 114.15 | 94.07
2017-10-10 20:30 | 111.44 | 90.97
2017-10-10 21:00 | 111.04 | 90.75
2017-10-10 21:30 | 113.15 | 92.73
2017-10-10 22:00 | 114.04 | 94.63
2017-10-10 22:30 | 109.58 | 89.89
2017-10-10 23:00 | 106.86 | 85.8
2017-10-10 23:30 | 103.08 | 83.18
2017-10-11 | 108.38 | 89.54
2017-10-11 00:30 | 108.38 | 89.17
2017-10-11 01:00 | 107.79 | 89.2
2017-10-11 01:30 | 108.1 | 89.22
2017-10-11 02:00 | 110.45 | 91.58
2017-10-11 02:30 | 106.39 | 87.11
2017-10-11 03:00 | 102.29 | 82.88
2017-10-11 03:30 | 96.35 | 77.78
2017-10-11 04:00 | 103.05 | 84.41
2017-10-11 04:30 | 96.88 | 77.34
2017-10-11 05:00 | 96.07 | 76.04
2017-10-11 05:30 | 93.19 | 73.37
2017-10-11 06:00 | 94.55 | 74.54
2017-10-11 06:30 | 78.96 | 58.62
2017-10-11 07:00 | 80.86 | 60.36
2017-10-11 07:30 | 86.19 | 65.26
2017-10-11 08:00 | 88.55 | 67.5
2017-10-11 08:30 | 90.79 | 69.87
2017-10-11 09:00 | 94.69 | 73.22
2017-10-11 09:30 | 94.3 | 73.85
2017-10-11 10:00 | 90.01 | 69.87
2017-10-11 10:30 | 93.06 | 74.26
2017-10-11 11:00 | 88.21 | 69.51
2017-10-11 11:30 | 85.27 | 64.53
2017-10-11 12:00 | 99.97 | 79.47
2017-10-11 12:30 | 103.69 | 82.44
2017-10-11 13:00 | 97.58 | 75.27
2017-10-11 13:30 | 99.56 | 77.35
2017-10-11 14:00 | 97.7 | 76
2017-10-11 14:30 | 102.43 | 81.08
2017-10-11 15:00 | 102.44 | 80.69
2017-10-11 15:30 | 100.64 | 77.61
2017-10-11 16:00 | 109.24 | 87.87
2017-10-11 16:30 | 102.42 | 80.23
2017-10-11 17:00 | 101.94 | 80.34
2017-10-11 17:30 | 107.38 | 87.29
2017-10-11 18:00 | 100.94 | 80.06
2017-10-11 18:30 | 95.57 | 73.25
2017-10-11 19:00 | 101.01 | 79.62
2017-10-11 19:30 | 100.63 | 78.39
2017-10-11 20:00 | 104.14 | 83.42
2017-10-11 20:30 | 107.31 | 85.35
2017-10-11 21:00 | 105.6 | 84.19
2017-10-11 21:30 | 103.17 | 82.47
2017-10-11 22:00 | 103.63 | 82.62
2017-10-11 22:30 | 102.83 | 83.89
2017-10-11 23:00 | 99.73 | 80.77
2017-10-11 23:30 | 97.08 | 76.84
2017-10-12 | 98.25 | 79.31
2017-10-12 00:30 | 96.71 | 78.24
2017-10-12 01:00 | 95.05 | 75.23
2017-10-12 01:30 | 101.66 | 81.04
2017-10-12 02:00 | 111.42 | 91.72
2017-10-12 02:30 | 109.29 | 88.32
2017-10-12 03:00 | 112.75 | 90.97
2017-10-12 03:30 | 105.8 | 85.67
2017-10-12 04:00 | 111.09 | 90.42
2017-10-12 04:30 | 105.14 | 83.02
2017-10-12 05:00 | 106.55 | 85.83
2017-10-12 05:30 | 109.23 | 88.46
2017-10-12 06:00 | 106.68 | 83.92
2017-10-12 06:30 | 98.2 | 73.73
2017-10-12 07:00 | 104.56 | 81.1
2017-10-12 07:30 | 108.37 | 87.26
2017-10-12 08:00 | 108.61 | 87.17
2017-10-12 08:30 | 102.22 | 79.51
2017-10-12 09:00 | 101.15 | 80.4
2017-10-12 09:30 | 99.17 | 78.44
2017-10-12 10:00 | 97.09 | 75.55
2017-10-12 10:30 | 101.11 | 80.73
2017-10-12 11:00 | 103.83 | 83.98
2017-10-12 11:30 | 103.87 | 82.75
2017-10-12 12:00 | 110.87 | 90.04
2017-10-12 12:30 | 106.46 | 83.3
2017-10-12 13:00 | 105.64 | 83.16
2017-10-12 13:30 | 114.61 | 92.67
2017-10-12 14:00 | 114 | 92.29
2017-10-12 14:30 | 114.5 | 92.11
2017-10-12 15:00 | 107.33 | 81.82
2017-10-12 15:30 | 116.16 | 91.02
2017-10-12 16:00 | 108.08 | 83.34
2017-10-12 16:30 | 113.91 | 87.52
2017-10-12 17:00 | 117.05 | 89.45
2017-10-12 17:30 | 119.43 | 95.07
2017-10-12 18:00 | 114.58 | 90.59
2017-10-12 18:30 | 104.16 | 80.39
2017-10-12 19:00 | 92.19 | 70.8
2017-10-12 19:30 | 98.83 | 77.24
2017-10-12 20:00 | 99.33 | 77.01
2017-10-12 20:30 | 95.57 | 74.07
2017-10-12 21:00 | 97.64 | 76.51
2017-10-12 21:30 | 100.98 | 80.98
2017-10-12 22:00 | 95.76 | 74.06
2017-10-12 22:30 | 97.36 | 76.64
2017-10-12 23:00 | 92.93 | 71.44
2017-10-12 23:30 | 88.69 | 65.9
2017-10-13 | 90.47 | 67.92
2017-10-13 00:30 | 96.22 | 76.81
2017-10-13 01:00 | 93.33 | 73.55
2017-10-13 01:30 | 93.9 | 74.28
2017-10-13 02:00 | 98.14 | 78.3
2017-10-13 02:30 | 104.43 | 84.69
2017-10-13 03:00 | 99.27 | 80.65
2017-10-13 03:30 | 101.33 | 82.19
2017-10-13 04:00 | 92.75 | 72.97
2017-10-13 04:30 | 98.77 | 79.67
2017-10-13 05:00 | 100.37 | 81.27
2017-10-13 05:30 | 96.3 | 76.17
2017-10-13 06:00 | 95.43 | 74.22
2017-10-13 06:30 | 91.95 | 70.11
2017-10-13 07:00 | 87.08 | 65.02
2017-10-13 07:30 | 91.85 | 69.99
2017-10-13 08:00 | 91.56 | 69.57
2017-10-13 08:30 | 89.13 | 67.24
2017-10-13 09:00 | 94.29 | 72.29
2017-10-13 09:30 | 97.04 | 76.05
2017-10-13 10:00 | 104.88 | 85.55
2017-10-13 10:30 | 109.04 | 88.63
2017-10-13 11:00 | 104.74 | 84.81
2017-10-13 11:30 | 98.01 | 76.07
2017-10-13 12:00 | 101.77 | 77.66
2017-10-13 12:30 | 107.54 | 84.45
2017-10-13 13:00 | 102 | 78.71
2017-10-13 13:30 | 112.58 | 87.98
2017-10-13 14:00 | 120.43 | 95.69
2017-10-13 14:30 | 120.44 | 95.33
2017-10-13 15:00 | 123.32 | 97.02
2017-10-13 15:30 | 127.42 | 101.21
2017-10-13 16:00 | 121.35 | 92.88
2017-10-13 16:30 | 126.52 | 99.16
2017-10-13 17:00 | 118.65 | 90.88
2017-10-13 17:30 | 130.06 | 102.23
2017-10-13 18:00 | 121.58 | 95.23
2017-10-13 18:30 | 112.28 | 86.5
2017-10-13 19:00 | 109.17 | 84.37
2017-10-13 19:30 | 105.94 | 80.17
2017-10-13 20:00 | 105.63 | 80.84
2017-10-13 20:30 | 105.98 | 83.37
2017-10-13 21:00 | 109.36 | 86.9
2017-10-13 21:30 | 109.01 | 86.46
2017-10-13 22:00 | 114.13 | 91.57
2017-10-13 22:30 | 109.03 | 85.23
2017-10-13 23:00 | 107.26 | 83.32
2017-10-13 23:30 | 105.05 | 82.03
2017-10-14 | 101.4 | 78.63
2017-10-14 00:30 | 111.4 | 90.61
2017-10-14 01:00 | 106.17 | 84.14
2017-10-14 01:30 | 107.16 | 82.99
2017-10-14 02:00 | 108.22 | 83.89
2017-10-14 02:30 | 103.36 | 80.66
2017-10-14 03:00 | 105.74 | 83.58
2017-10-14 03:30 | 103.17 | 81.09
2017-10-14 04:00 | 105 | 83.04
2017-10-14 04:30 | 103.7 | 81.44
2017-10-14 05:00 | 102.18 | 79.54
2017-10-14 05:30 | 108.01 | 85.36
2017-10-14 06:00 | 102.08 | 78.76
2017-10-14 06:30 | 99.73 | 75.65
2017-10-14 07:00 | 100.59 | 77.05
2017-10-14 07:30 | 99.46 | 75.14
2017-10-14 08:00 | 101.73 | 76.57
2017-10-14 08:30 | 104.76 | 79.66
2017-10-14 09:00 | 103.87 | 78.68
2017-10-14 09:30 | 101.49 | 74.74
2017-10-14 10:00 | 107.36 | 83.5
2017-10-14 10:30 | 110.08 | 87.02
2017-10-14 11:00 | 111.67 | 87.84
2017-10-14 11:30 | 112.24 | 88.86
2017-10-14 12:00 | 112.17 | 88.44
2017-10-14 12:30 | 115.06 | 91.2
2017-10-14 13:00 | 112.73 | 88.94
2017-10-14 13:30 | 113.11 | 89.98
2017-10-14 14:00 | 116.05 | 92.48
2017-10-14 14:30 | 118.61 | 95.51
2017-10-14 15:00 | 115.85 | 91.87
2017-10-14 15:30 | 117.42 | 93.87
2017-10-14 16:00 | 117.6 | 94.57
2017-10-14 16:30 | 121.29 | 99.05
2017-10-14 17:00 | 112.7 | 89.1
2017-10-14 17:30 | 113.62 | 90.74
2017-10-14 18:00 | 114.54 | 91.31
2017-10-14 18:30 | 111.12 | 86.29
2017-10-14 19:00 | 113.77 | 91.51
2017-10-14 19:30 | 118.99 | 96.82
2017-10-14 20:00 | 110.28 | 87.75
2017-10-14 20:30 | 113.71 | 91.81
2017-10-14 21:00 | 119.21 | 96.95
2017-10-14 21:30 | 109.75 | 87.97
2017-10-14 22:00 | 111.01 | 90.89
2017-10-14 22:30 | 105.45 | 83.99
2017-10-14 23:00 | 103.24 | 83.12
2017-10-14 23:30 | 101.67 | 81.91
2017-10-15 | 106.45 | 86.49
2017-10-15 00:30 | 107.71 | 86.93
2017-10-15 01:00 | 109.37 | 89.21
2017-10-15 01:30 | 111.64 | 91.63
2017-10-15 02:00 | 111.16 | 91.36
2017-10-15 02:30 | 110.7 | 90.48
2017-10-15 03:00 | 112.77 | 92.87
2017-10-15 03:30 | 114.52 | 95.82
2017-10-15 04:00 | 106.93 | 87.54
2017-10-15 04:30 | 108.54 | 88.14
2017-10-15 05:00 | 111.86 | 92.83
2017-10-15 05:30 | 117.63 | 99.45
2017-10-15 06:00 | 112.55 | 94.85
2017-10-15 06:30 | 105.34 | 84.7
2017-10-15 07:00 | 114.07 | 93.35
2017-10-15 07:30 | 111.51 | 90.66
2017-10-15 08:00 | 113.84 | 91.09
2017-10-15 08:30 | 114.31 | 90.26
2017-10-15 09:00 | 115.81 | 91.21
2017-10-15 09:30 | 117.14 | 92.78
2017-10-15 10:00 | 122.32 | 100.13
2017-10-15 10:30 | 117.41 | 94.28
2017-10-15 11:00 | 116.47 | 92.75
2017-10-15 11:30 | 110.54 | 86.81
2017-10-15 12:00 | 113.2 | 89.53
2017-10-15 12:30 | 119.78 | 95.24
2017-10-15 13:00 | 120.16 | 97.17
2017-10-15 13:30 | 120.09 | 96.21
2017-10-15 14:00 | 121.88 | 96.99
2017-10-15 14:30 | 124 | 100.26
2017-10-15 15:00 | 124.15 | 100.49
2017-10-15 15:30 | 121.69 | 94.86
2017-10-15 16:00 | 121.78 | 96.7
2017-10-15 16:30 | 121 | 96
2017-10-15 17:00 | 123.68 | 98.72
2017-10-15 17:30 | 117.59 | 91.07
2017-10-15 18:00 | 122.51 | 95.69
2017-10-15 18:30 | 118.13 | 89.88
2017-10-15 19:00 | 124.56 | 97.67
2017-10-15 19:30 | 129.97 | 103.65
2017-10-15 20:00 | 125.01 | 98.81
2017-10-15 20:30 | 121.18 | 94.26
2017-10-15 21:00 | 108.68 | 77.49
2017-10-15 21:30 | 112.96 | 85.69
2017-10-15 22:00 | 111.3 | 86.17
2017-10-15 22:30 | 106.32 | 81.08
2017-10-15 23:00 | 113.66 | 90.33
2017-10-15 23:30 | 108.6 | 85.7
2017-10-16 | 108.97 | 85.23
2017-10-16 00:30 | 103.99 | 79.8
2017-10-16 01:00 | 107.81 | 82.16
2017-10-16 01:30 | 104.74 | 77.74
2017-10-16 02:00 | 107.79 | 82.9
2017-10-16 02:30 | 112.07 | 89.45
2017-10-16 03:00 | 110.53 | 85.86
2017-10-16 03:30 | 105.28 | 80.13
2017-10-16 04:00 | 108.57 | 83.87
2017-10-16 04:30 | 108.59 | 83.15
2017-10-16 05:00 | 109 | 82.27
2017-10-16 05:30 | 108.66 | 82.11
2017-10-16 06:00 | 105.09 | 80.09
2017-10-16 06:30 | 100.49 | 73.39
2017-10-16 07:00 | 95.65 | 69.45
2017-10-16 07:30 | 102.31 | 77.62
2017-10-16 08:00 | 102.96 | 77.77
2017-10-16 08:30 | 102.32 | 77.07
2017-10-16 09:00 | 104.78 | 80.03
2017-10-16 09:30 | 105.48 | 79.89
2017-10-16 10:00 | 105.82 | 80.89
2017-10-16 10:30 | 107.53 | 82.67
2017-10-16 11:00 | 110.59 | 85.11
2017-10-16 11:30 | 108.04 | 82.17
2017-10-16 12:00 | 108.37 | 83.47
2017-10-16 12:30 | 111.15 | 87.62
2017-10-16 13:00 | 109.49 | 85.5
2017-10-16 13:30 | 109.45 | 83.77
2017-10-16 14:00 | 114.92 | 89.82
2017-10-16 14:30 | 113.36 | 87.48
2017-10-16 15:00 | 112.74 | 87.07
2017-10-16 15:30 | 113.56 | 86.21
2017-10-16 16:00 | 116.19 | 89.12
2017-10-16 16:30 | 119.1 | 93.72
2017-10-16 17:00 | 114.59 | 88.41
2017-10-16 17:30 | 120.18 | 94.83
2017-10-16 18:00 | 119.79 | 94
2017-10-16 18:30 | 116.23 | 89.16
2017-10-16 19:00 | 125.02 | 98.77
2017-10-16 19:30 | 129.58 | 103.38
2017-10-16 20:00 | 128.25 | 101.48
2017-10-16 20:30 | 123.15 | 96.23
2017-10-16 21:00 | 119.47 | 93.09
2017-10-16 21:30 | 119.3 | 93.09
2017-10-16 22:00 | 121.28 | 95.47
2017-10-16 22:30 | 118.35 | 92.76
2017-10-16 23:00 | 117.35 | 91.6
2017-10-16 23:30 | 113.94 | 88.61
2017-10-17 | 116.31 | 92.15
2017-10-17 00:30 | 120.57 | 96.76
2017-10-17 01:00 | 114.99 | 90.73
2017-10-17 01:30 | 114.99 | 90.24
2017-10-17 02:00 | 112.79 | 88.6
2017-10-17 02:30 | 120.28 | 96.95
2017-10-17 03:00 | 118.19 | 93.83
2017-10-17 03:30 | 115.12 | 90.35
2017-10-17 04:00 | 112.84 | 87.43
2017-10-17 04:30 | 123.7 | 99.49
2017-10-17 05:00 | 121.96 | 96.64
2017-10-17 05:30 | 121.28 | 96.44
2017-10-17 06:00 | 119.41 | 95.28
2017-10-17 06:30 | 113.98 | 88.25
2017-10-17 07:00 | 112.16 | 86.39
2017-10-17 07:30 | 119.01 | 94.73
2017-10-17 08:00 | 119.48 | 94.64
2017-10-17 08:30 | 114.7 | 89.62
2017-10-17 09:00 | 111.72 | 87.04
2017-10-17 09:30 | 110.15 | 85.94
2017-10-17 10:00 | 112.95 | 88.65
2017-10-17 10:30 | 110.08 | 86.33
2017-10-17 11:00 | 107.39 | 84.2
2017-10-17 11:30 | 101.1 | 80.41
2017-10-17 12:00 | 100.65 | 80.29
2017-10-17 12:30 | 112.28 | 93.2
2017-10-17 13:00 | 100.93 | 80.04
2017-10-17 13:30 | 104.22 | 83.72
2017-10-17 14:00 | 104.13 | 83.06
2017-10-17 14:30 | 114.14 | 91.54
2017-10-17 15:00 | 114.3 | 90.62
2017-10-17 15:30 | 119.07 | 96.63
2017-10-17 16:00 | 123.05 | 98.17
2017-10-17 16:30 | 129.79 | 104.37
2017-10-17 17:00 | 127.34 | 102.16
2017-10-17 17:30 | 127.06 | 100.82
2017-10-17 18:00 | 125.17 | 98.95
2017-10-17 18:30 | 121.79 | 93.6
2017-10-17 19:00 | 137.3 | 112.8
2017-10-17 19:30 | 129.9 | 104.41
2017-10-17 20:00 | 131.6 | 105.3
2017-10-17 20:30 | 125.76 | 98.39
2017-10-17 21:00 | 129.01 | 101.07
2017-10-17 21:30 | 126.91 | 99.21
2017-10-17 22:00 | 126.44 | 99.31
2017-10-17 22:30 | 124.33 | 97.89
2017-10-17 23:00 | 127.03 | 101.72
2017-10-17 23:30 | 127.25 | 101.38
2017-10-18 | 122.63 | 97.02
2017-10-18 00:30 | 119.07 | 92.16
2017-10-18 01:00 | 115.39 | 88.86
2017-10-18 01:30 | 119.89 | 93.79
2017-10-18 02:00 | 117.53 | 91.17
2017-10-18 02:30 | 113.61 | 87.33
2017-10-18 03:00 | 113.91 | 87.9
2017-10-18 03:30 | 110.67 | 84.36
2017-10-18 04:00 | 112.93 | 86.78
2017-10-18 04:30 | 99.67 | 76.74
2017-10-18 05:00 | 101.77 | 79.53
2017-10-18 05:30 | 103.6 | 80.1
2017-10-18 06:00 | 108.05 | 83.91
2017-10-18 06:30 | 113.49 | 84.76
2017-10-18 07:00 | 110.11 | 81.06
2017-10-18 07:30 | 113.71 | 85.7
2017-10-18 08:00 | 107.3 | 80.02
2017-10-18 08:30 | 112.69 | 84.9
2017-10-18 09:00 | 113.44 | 85.52
2017-10-18 09:30 | 117.39 | 85.59
2017-10-18 10:00 | 119.07 | 88.04
2017-10-18 10:30 | 113.08 | 80.1
2017-10-18 11:00 | 112.78 | 81.22
2017-10-18 11:30 | 115.28 | 82.33
2017-10-18 12:00 | 122.84 | 92.44
2017-10-18 12:30 | 120.67 | 89.37
2017-10-18 13:00 | 110.7 | 79.98
2017-10-18 13:30 | 117.21 | 86.12
2017-10-18 14:00 | 114.56 | 81.91
2017-10-18 14:30 | 107.28 | 75.98
2017-10-18 15:00 | 120.4 | 89.34
2017-10-18 15:30 | 114.98 | 86.59
2017-10-18 16:00 | 121.46 | 92.9
2017-10-18 16:30 | 112.82 | 83.85
2017-10-18 17:00 | 111.16 | 81.88
2017-10-18 17:30 | 108.19 | 81.01
2017-10-18 18:00 | 113.24 | 86.64
2017-10-18 18:30 | 105.37 | 76.8
2017-10-18 19:00 | 111.96 | 85.01
2017-10-18 19:30 | 118.33 | 91.11
2017-10-18 20:00 | 117.5 | 89.22
2017-10-18 20:30 | 114.97 | 86.6
2017-10-18 21:00 | 110.62 | 81.96
2017-10-18 21:30 | 110.8 | 82.8
2017-10-18 22:00 | 116.16 | 90.47
2017-10-18 22:30 | 119.71 | 94.3
2017-10-18 23:00 | 110.82 | 85.09
2017-10-18 23:30 | 107.98 | 83.22
2017-10-19 | 110.52 | 85.41
2017-10-19 00:30 | 106.34 | 81.66
2017-10-19 01:00 | 114.96 | 90.92
2017-10-19 01:30 | 113.21 | 88.42
2017-10-19 02:00 | 112.72 | 88.17
2017-10-19 02:30 | 105.72 | 82.29
2017-10-19 03:00 | 106.17 | 81.75
2017-10-19 03:30 | 103.09 | 78.42
2017-10-19 04:00 | 102.77 | 78
2017-10-19 04:30 | 110.42 | 86.42
2017-10-19 05:00 | 100.98 | 75.73
2017-10-19 05:30 | 97.58 | 72.45
2017-10-19 06:00 | 101.61 | 76.4
2017-10-19 06:30 | 96.02 | 69.53
2017-10-19 07:00 | 95.56 | 68.2
2017-10-19 07:30 | 104.1 | 77.9
2017-10-19 08:00 | 99.47 | 71.65
2017-10-19 08:30 | 93.94 | 65.76
2017-10-19 09:00 | 96.89 | 68.89
2017-10-19 09:30 | 95.3 | 67.38
2017-10-19 10:00 | 92.57 | 64.65
2017-10-19 10:30 | 93.82 | 67.28
2017-10-19 11:00 | 87.35 | 59.3
2017-10-19 11:30 | 91.29 | 62.21
2017-10-19 12:00 | 90.2 | 61.78
2017-10-19 12:30 | 93.9 | 68.05
2017-10-19 13:00 | 97.31 | 71.68
2017-10-19 13:30 | 89.62 | 63.16
2017-10-19 14:00 | 90.35 | 63.08
2017-10-19 14:30 | 89.35 | 61
2017-10-19 15:00 | 92.81 | 64.94
2017-10-19 15:30 | 95.09 | 69.09
2017-10-19 16:00 | 97.47 | 71.85
2017-10-19 16:30 | 94.91 | 70.36
2017-10-19 17:00 | 95.44 | 69.88
2017-10-19 17:30 | 94.43 | 68.07
2017-10-19 18:00 | 96.35 | 70.36
2017-10-19 18:30 | 94.76 | 66.63
2017-10-19 19:00 | 102.86 | 75.81
2017-10-19 19:30 | 103.24 | 75.2
2017-10-19 20:00 | 107.49 | 79.48
2017-10-19 20:30 | 102.06 | 73.89
2017-10-19 21:00 | 107.37 | 79.96
2017-10-19 21:30 | 106.59 | 79.01
2017-10-19 22:00 | 110.45 | 84.61
2017-10-19 22:30 | 106.73 | 81.69
2017-10-19 23:00 | 110.35 | 87.25
2017-10-19 23:30 | 113.66 | 91.85
2017-10-20 | 110.51 | 87.02
2017-10-20 00:30 | 103.58 | 78.78
2017-10-20 01:00 | 110.12 | 86.04
2017-10-20 01:30 | 108.12 | 84.63
2017-10-20 02:00 | 110.24 | 86.72
2017-10-20 02:30 | 110.18 | 85.98
2017-10-20 03:00 | 105.64 | 81.88
2017-10-20 03:30 | 104.54 | 79.52
2017-10-20 04:00 | 110.63 | 87.08
2017-10-20 04:30 | 111.73 | 88.77
2017-10-20 05:00 | 110.6 | 85.54
2017-10-20 05:30 | 113.14 | 88.32
2017-10-20 06:00 | 111.65 | 87.76
2017-10-20 06:30 | 100.98 | 75.21
2017-10-20 07:00 | 109.76 | 85.74
2017-10-20 07:30 | 118.05 | 93.79
2017-10-20 08:00 | 116.38 | 91.64
2017-10-20 08:30 | 117.96 | 92.71
2017-10-20 09:00 | 114.21 | 87.88
2017-10-20 09:30 | 114.88 | 89.58
2017-10-20 10:00 | 118.22 | 94.39
2017-10-20 10:30 | 113.7 | 88.65
2017-10-20 11:00 | 115.59 | 90.58
2017-10-20 11:30 | 118.82 | 93.23
2017-10-20 12:00 | 119.66 | 94.64
2017-10-20 12:30 | 115.26 | 90.29
2017-10-20 13:00 | 111.59 | 85.45
2017-10-20 13:30 | 110.15 | 83.23
2017-10-20 14:00 | 112.95 | 88.37
2017-10-20 14:30 | 116.71 | 94.06
2017-10-20 15:00 | 114.71 | 90.65
2017-10-20 15:30 | 111.09 | 86.48
2017-10-20 16:00 | 118.37 | 92.8
2017-10-20 16:30 | 121.65 | 93.95
2017-10-20 17:00 | 121.31 | 93.78
2017-10-20 17:30 | 123.48 | 96.57
2017-10-20 18:00 | 120.72 | 94.55
2017-10-20 18:30 | 114.7 | 86.11
2017-10-20 19:00 | 121.36 | 93.03
2017-10-20 19:30 | 124.27 | 95.32
2017-10-20 20:00 | 133.41 | 104.97
2017-10-20 20:30 | 134.15 | 105.53
2017-10-20 21:00 | 131.95 | 103.99
2017-10-20 21:30 | 126.96 | 97.4
2017-10-20 22:00 | 117.01 | 87.94
2017-10-20 22:30 | 115.88 | 87.91
2017-10-20 23:00 | 113.43 | 86.12
2017-10-20 23:30 | 118.38 | 93.37
2017-10-21 | 117.3 | 91.87
2017-10-21 00:30 | 119.82 | 93.21
2017-10-21 01:00 | 121.58 | 95.1
2017-10-21 01:30 | 118.59 | 91.58
2017-10-21 02:00 | 114.77 | 88.03
2017-10-21 02:30 | 116.86 | 89.41
2017-10-21 03:00 | 115.12 | 87.97
2017-10-21 03:30 | 119.13 | 92.5
2017-10-21 04:00 | 123.34 | 97.55
2017-10-21 04:30 | 116.99 | 91.72
2017-10-21 05:00 | 112.68 | 86.9
2017-10-21 05:30 | 118.59 | 91.86
2017-10-21 06:00 | 114.34 | 87.43
2017-10-21 06:30 | 105.39 | 76.75
2017-10-21 07:00 | 97.41 | 70.46
2017-10-21 07:30 | 105.06 | 77.51
2017-10-21 08:00 | 108.28 | 82.39
2017-10-21 08:30 | 109.09 | 81.54
2017-10-21 09:00 | 112.5 | 86.47
2017-10-21 09:30 | 105.26 | 78.67
2017-10-21 10:00 | 108.2 | 82.79
2017-10-21 10:30 | 106.2 | 80.21
2017-10-21 11:00 | 106.23 | 82.22
2017-10-21 11:30 | 113.23 | 88.6
2017-10-21 12:00 | 104.67 | 79.45
2017-10-21 12:30 | 103.13 | 79.22
2017-10-21 13:00 | 106.69 | 79.8
2017-10-21 13:30 | 102.78 | 76.34
2017-10-21 14:00 | 101.13 | 74.84
2017-10-21 14:30 | 105.74 | 78.94
2017-10-21 15:00 | 107.03 | 80.89
2017-10-21 15:30 | 107.69 | 80.96
2017-10-21 16:00 | 113.39 | 84.23
2017-10-21 16:30 | 109.11 | 79.35
2017-10-21 17:00 | 112 | 84.37
2017-10-21 17:30 | 118.06 | 89.78
2017-10-21 18:00 | 124.47 | 96.54
2017-10-21 18:30 | 115.9 | 86.53
2017-10-21 19:00 | 117.8 | 87.93
2017-10-21 19:30 | 125 | 96.84
2017-10-21 20:00 | 119.7 | 90.83
2017-10-21 20:30 | 115.74 | 86.78
2017-10-21 21:00 | 119.93 | 89.91
2017-10-21 21:30 | 125.75 | 94.75
2017-10-21 22:00 | 123.23 | 92.28
2017-10-21 22:30 | 124 | 95.19
2017-10-21 23:00 | 125.68 | 99.99
2017-10-21 23:30 | 118.39 | 92.54
2017-10-22 | 113.55 | 86.87
2017-10-22 00:30 | 116.52 | 91.01
2017-10-22 01:00 | 117.11 | 90.7
2017-10-22 01:30 | 117.57 | 91.04
2017-10-22 02:00 | 110.73 | 83.78
2017-10-22 02:30 | 111.58 | 85.42
2017-10-22 03:00 | 111.81 | 86.35
2017-10-22 03:30 | 108.42 | 82.9
2017-10-22 04:00 | 115.3 | 91.65
2017-10-22 04:30 | 116.91 | 93.98
2017-10-22 05:00 | 122.97 | 99.27
2017-10-22 05:30 | 108.97 | 85.08
2017-10-22 06:00 | 113.12 | 90.34
2017-10-22 06:30 | 104.07 | 79.69
2017-10-22 07:00 | 106.85 | 83.49
2017-10-22 07:30 | 109.3 | 85.25
2017-10-22 08:00 | 112.78 | 88.08
2017-10-22 08:30 | 109.47 | 84.39
2017-10-22 09:00 | 107.14 | 80.57
2017-10-22 09:30 | 109.63 | 84.16
2017-10-22 10:00 | 110.5 | 85.12
2017-10-22 10:30 | 108.36 | 82.09
2017-10-22 11:00 | 109.73 | 82.22
2017-10-22 11:30 | 119.19 | 90.33
2017-10-22 12:00 | 116.09 | 88.37
2017-10-22 12:30 | 123.18 | 95.43
2017-10-22 13:00 | 108.11 | 76.86
2017-10-22 13:30 | 116.44 | 86.45
2017-10-22 14:00 | 115.5 | 86.25
2017-10-22 14:30 | 112.28 | 83.52
2017-10-22 15:00 | 111.4 | 83.29
2017-10-22 15:30 | 109.69 | 82.63
2017-10-22 16:00 | 112.77 | 86.97
2017-10-22 16:30 | 112.5 | 86.37
2017-10-22 17:00 | 112.82 | 83.09
2017-10-22 17:30 | 123.77 | 95.09
2017-10-22 18:00 | 128.19 | 100.55
2017-10-22 18:30 | 117.93 | 86.81
2017-10-22 19:00 | 119.51 | 89.92
2017-10-22 19:30 | 129.79 | 101.99
2017-10-22 20:00 | 124.28 | 96.35
2017-10-22 20:30 | 125.36 | 95.9
2017-10-22 21:00 | 120.76 | 89.96
2017-10-22 21:30 | 122.05 | 89.5
2017-10-22 22:00 | 124.43 | 91.86
2017-10-22 22:30 | 126.75 | 94.09
2017-10-22 23:00 | 125.78 | 93.78
2017-10-22 23:30 | 122.55 | 90.42
2017-10-23 | 127.02 | 96.38
2017-10-23 00:30 | 126.7 | 95.27
2017-10-23 01:00 | 119.48 | 87.78
2017-10-23 01:30 | 118.94 | 89.03
2017-10-23 02:00 | 112.13 | 82.32
2017-10-23 02:30 | 116.01 | 85.57
2017-10-23 03:00 | 108.15 | 80.49
2017-10-23 03:30 | 100.21 | 73.46
2017-10-23 04:00 | 106.82 | 81.06
2017-10-23 04:30 | 109.3 | 82.87
2017-10-23 05:00 | 117.1 | 92.13
2017-10-23 05:30 | 111.54 | 84.2
2017-10-23 06:00 | 111.57 | 83.56
2017-10-23 06:30 | 102.04 | 72.26
2017-10-23 07:00 | 111.64 | 84.19
2017-10-23 07:30 | 112.94 | 85.92
2017-10-23 08:00 | 111.49 | 83.68
2017-10-23 08:30 | 109.3 | 81.23
2017-10-23 09:00 | 113.34 | 85.28
2017-10-23 09:30 | 115.02 | 88.02
2017-10-23 10:00 | 111.67 | 85.44
2017-10-23 10:30 | 111.06 | 82.33
2017-10-23 11:00 | 110.7 | 81.51
2017-10-23 11:30 | 108.02 | 79.82
2017-10-23 12:00 | 111.24 | 82.53
2017-10-23 12:30 | 106.73 | 78.3
2017-10-23 13:00 | 107.67 | 75.46
2017-10-23 13:30 | 110.85 | 79.58
2017-10-23 14:00 | 113.86 | 84.16
2017-10-23 14:30 | 121.09 | 92.46
2017-10-23 15:00 | 119.62 | 90.61
2017-10-23 15:30 | 116.91 | 88.94
2017-10-23 16:00 | 116.2 | 87.41
2017-10-23 16:30 | 117.47 | 89.61
2017-10-23 17:00 | 117.05 | 88.67
2017-10-23 17:30 | 115.6 | 86.66
2017-10-23 18:00 | 116.66 | 89.18
2017-10-23 18:30 | 114.05 | 84.64
2017-10-23 19:00 | 117.3 | 89.42
2017-10-23 19:30 | 125.09 | 98.7
2017-10-23 20:00 | 122.92 | 96.61
2017-10-23 20:30 | 123.44 | 96.73
2017-10-23 21:00 | 117.57 | 90.39
2017-10-23 21:30 | 114.84 | 88.69
2017-10-23 22:00 | 107.19 | 79.88
2017-10-23 22:30 | 105.99 | 80.11
2017-10-23 23:00 | 108.76 | 83.04
2017-10-23 23:30 | 107.78 | 81.81
2017-10-24 | 117.15 | 91.08
2017-10-24 00:30 | 111.29 | 85.32
2017-10-24 01:00 | 112.94 | 87.18
2017-10-24 01:30 | 114.21 | 88.07
2017-10-24 02:00 | 116.56 | 90.97
2017-10-24 02:30 | 111.79 | 86.05
2017-10-24 03:00 | 112.48 | 86.87
2017-10-24 03:30 | 111.48 | 85.87
2017-10-24 04:00 | 109.06 | 81.6
2017-10-24 04:30 | 106.82 | 81.19
2017-10-24 05:00 | 111.59 | 86.06
2017-10-24 05:30 | 110.38 | 83.15
2017-10-24 06:00 | 112.16 | 86.14
2017-10-24 06:30 | 109.85 | 81.32
2017-10-24 07:00 | 107.12 | 79.12
2017-10-24 07:30 | 103.32 | 72.64
2017-10-24 08:00 | 102.71 | 69.08
2017-10-24 08:30 | 102.92 | 68.12
2017-10-24 09:00 | 101.56 | 64.81
2017-10-24 09:30 | 103.59 | 66.92
2017-10-24 10:00 | 93.74 | 57.86
2017-10-24 10:30 | 98.74 | 64.08
2017-10-24 11:00 | 95.73 | 62.28
2017-10-24 11:30 | 102.92 | 72.01
2017-10-24 12:00 | 104.62 | 72.35
2017-10-24 12:30 | 107.9 | 74.86
2017-10-24 13:00 | 109.87 | 76.83
2017-10-24 13:30 | 110.19 | 78.98
2017-10-24 14:00 | 111.4 | 79.39
2017-10-24 14:30 | 100.37 | 69.86
2017-10-24 15:00 | 92.85 | 61.43
2017-10-24 15:30 | 94.64 | 66.02
2017-10-24 16:00 | 98.96 | 70.14
2017-10-24 16:30 | 99.61 | 70.97
2017-10-24 17:00 | 102.94 | 73.79
2017-10-24 17:30 | 104.83 | 77.2
2017-10-24 18:00 | 106.58 | 79.2
2017-10-24 18:30 | 109.28 | 82.32
2017-10-24 19:00 | 124.9 | 99.98
2017-10-24 19:30 | 117.06 | 91.96
2017-10-24 20:00 | 111.1 | 86.55
2017-10-24 20:30 | 122.25 | 97.28
2017-10-24 21:00 | 115.87 | 88.99
2017-10-24 21:30 | 118.28 | 92.37
2017-10-24 22:00 | 113.59 | 87.02
2017-10-24 22:30 | 116.95 | 92.81
2017-10-24 23:00 | 118.82 | 91.98
2017-10-24 23:30 | 114.2 | 87.49
2017-10-25 | 114.63 | 86.24
2017-10-25 00:30 | 117.77 | 90.6
2017-10-25 01:00 | 118.9 | 90.12
2017-10-25 01:30 | 121.14 | 92.38
2017-10-25 02:00 | 122.63 | 93.59
2017-10-25 02:30 | 125.95 | 97.14
2017-10-25 03:00 | 113.13 | 86.9
2017-10-25 03:30 | 115.95 | 90.19
2017-10-25 04:00 | 115.69 | 88.68
2017-10-25 04:30 | 112.91 | 85.31
2017-10-25 05:00 | 107.28 | 80
2017-10-25 05:30 | 110.25 | 84.89
2017-10-25 06:00 | 112.14 | 88.07
2017-10-25 06:30 | 101.94 | 74.42
2017-10-25 07:00 | 99.45 | 72.89
2017-10-25 07:30 | 100.79 | 75.52
2017-10-25 08:00 | 103.89 | 77.74
2017-10-25 08:30 | 106.96 | 81.93
2017-10-25 09:00 | 106.26 | 76.89
2017-10-25 09:30 | 110.19 | 81.77
2017-10-25 10:00 | 108.77 | 81.94
2017-10-25 10:30 | 113.83 | 85.63
2017-10-25 11:00 | 114.32 | 84.82
2017-10-25 11:30 | 119.35 | 91.45
2017-10-25 12:00 | 119.06 | 90.66
2017-10-25 12:30 | 112.98 | 83.42
2017-10-25 13:00 | 119.91 | 89.54
2017-10-25 13:30 | 119.64 | 88.88
2017-10-25 14:00 | 117.51 | 87.43
2017-10-25 14:30 | 125.03 | 95.22
2017-10-25 15:00 | 116.11 | 85.39
2017-10-25 15:30 | 121.01 | 92.13
2017-10-25 16:00 | 120.19 | 90.25
2017-10-25 16:30 | 125.34 | 96.91
2017-10-25 17:00 | 124.39 | 96.45
2017-10-25 17:30 | 127.41 | 99.27
2017-10-25 18:00 | 126.07 | 97.28
2017-10-25 18:30 | 120.21 | 88.73
2017-10-25 19:00 | 123.45 | 95.67
2017-10-25 19:30 | 127.16 | 100.34
2017-10-25 20:00 | 133.29 | 107.54
2017-10-25 20:30 | 132.95 | 106.92
2017-10-25 21:00 | 129.61 | 103.01
2017-10-25 21:30 | 122.7 | 94.58
2017-10-25 22:00 | 117.06 | 88.59
2017-10-25 22:30 | 123.34 | 97.14
2017-10-25 23:00 | 122.14 | 94.8
2017-10-25 23:30 | 117.78 | 91.78
2017-10-26 | 120.04 | 92.54
2017-10-26 00:30 | 113.06 | 85.53
2017-10-26 01:00 | 122.61 | 96.04
2017-10-26 01:30 | 117.98 | 90.51
2017-10-26 02:00 | 118.35 | 90.35
2017-10-26 02:30 | 112.89 | 83.83
2017-10-26 03:00 | 118.07 | 92.16
2017-10-26 03:30 | 116.47 | 92.26
2017-10-26 04:00 | 117.2 | 91.85
2017-10-26 04:30 | 118.62 | 93.35
2017-10-26 05:00 | 121.32 | 95.3
2017-10-26 05:30 | 124.49 | 100.01
2017-10-26 06:00 | 120.48 | 94.51
2017-10-26 06:30 | 113.54 | 84.69
2017-10-26 07:00 | 112.71 | 84.15
2017-10-26 07:30 | 121 | 91.97
2017-10-26 08:00 | 118.66 | 88.58
2017-10-26 08:30 | 117.92 | 88.13
2017-10-26 09:00 | 118.59 | 88.8
2017-10-26 09:30 | 113.92 | 84.27
2017-10-26 10:00 | 113.58 | 82.78
2017-10-26 10:30 | 118.32 | 87.27
2017-10-26 11:00 | 117.59 | 87.5
2017-10-26 11:30 | 114.18 | 84.37
2017-10-26 12:00 | 120.18 | 89.3
2017-10-26 12:30 | 121.02 | 88.58
2017-10-26 13:00 | 127.83 | 94.93
2017-10-26 13:30 | 121.6 | 88.67
2017-10-26 14:00 | 126.82 | 93.98
2017-10-26 14:30 | 126.59 | 94.53
2017-10-26 15:00 | 118.83 | 82.72
2017-10-26 15:30 | 115.56 | 79.51
2017-10-26 16:00 | 119.99 | 82.44
2017-10-26 16:30 | 116.22 | 78.93
2017-10-26 17:00 | 117.02 | 81.17
2017-10-26 17:30 | 117.78 | 84.55
2017-10-26 18:00 | 123.63 | 91.94
2017-10-26 18:30 | 122.04 | 87.53
2017-10-26 19:00 | 127.79 | 94.99
2017-10-26 19:30 | 127.14 | 93.09
2017-10-26 20:00 | 125.28 | 90.92
2017-10-26 20:30 | 118.03 | 86.79
2017-10-26 21:00 | 75.55 | 41.37
2017-10-26 21:30 | 85.05 | 54.53
2017-10-26 22:00 | 89.19 | 60.92
2017-10-26 22:30 | 97.18 | 70.32
2017-10-26 23:00 | 103.21 | 76.23
2017-10-26 23:30 | 105.7 | 80.2
2017-10-27 | 100.54 | 74.9
2017-10-27 00:30 | 114.51 | 88
2017-10-27 01:00 | 110.47 | 83.93
2017-10-27 01:30 | 115.64 | 89.43
2017-10-27 02:00 | 112.34 | 84.24
2017-10-27 02:30 | 112.29 | 81.59
2017-10-27 03:00 | 121.65 | 91.68
2017-10-27 03:30 | 121.94 | 93.7
2017-10-27 04:00 | 122.17 | 95.09
2017-10-27 04:30 | 119.15 | 92
2017-10-27 05:00 | 116.8 | 89.28
2017-10-27 05:30 | 124.96 | 96.42
2017-10-27 06:00 | 124.75 | 93.85
2017-10-27 06:30 | 116.05 | 81.4
2017-10-27 07:00 | 125.65 | 94.13
2017-10-27 07:30 | 132.72 | 102.48
2017-10-27 08:00 | 122.81 | 93.61
2017-10-27 08:30 | 123.28 | 93.84
2017-10-27 09:00 | 127.05 | 96.04
2017-10-27 09:30 | 121.33 | 88.19
2017-10-27 10:00 | 129.09 | 97.44
2017-10-27 10:30 | 129.37 | 94.88
2017-10-27 11:00 | 122.67 | 90.4
2017-10-27 11:30 | 126.97 | 96.49
2017-10-27 12:00 | 131.9 | 101.08
2017-10-27 12:30 | 136.2 | 105.17
2017-10-27 13:00 | 135.84 | 104.44
2017-10-27 13:30 | 136.2 | 104.16
2017-10-27 14:00 | 129.07 | 95.28
2017-10-27 14:30 | 125.17 | 90.7
2017-10-27 15:00 | 129.98 | 96.05
2017-10-27 15:30 | 128.21 | 94.18
2017-10-27 16:00 | 138.22 | 106.2
2017-10-27 16:30 | 135.94 | 105.8
2017-10-27 17:00 | 130.68 | 99.18
2017-10-27 17:30 | 141.05 | 110.89
2017-10-27 18:00 | 144.09 | 112.41
2017-10-27 18:30 | 135.45 | 102.16
2017-10-27 19:00 | 138.67 | 106.83
2017-10-27 19:30 | 141.71 | 108.81
2017-10-27 20:00 | 136.41 | 105.36
2017-10-27 20:30 | 135.26 | 104.98
2017-10-27 21:00 | 127.58 | 95.89
2017-10-27 21:30 | 128.53 | 96.92
2017-10-27 22:00 | 127.05 | 97.47
2017-10-27 22:30 | 123.94 | 94.36
2017-10-27 23:00 | 122.06 | 92.21
2017-10-27 23:30 | 116.22 | 85.49
2017-10-28 | 124.64 | 94.58
2017-10-28 00:30 | 133.18 | 102.97
2017-10-28 01:00 | 130.45 | 100.75
2017-10-28 01:30 | 123.44 | 94.85
2017-10-28 02:00 | 130.37 | 102.45
2017-10-28 02:30 | 132.03 | 103.54
2017-10-28 03:00 | 128.85 | 100.45
2017-10-28 03:30 | 124.71 | 95.75
2017-10-28 04:00 | 126.95 | 97.62
2017-10-28 04:30 | 127.07 | 98.13
2017-10-28 05:00 | 122.67 | 92.81
2017-10-28 05:30 | 120.36 | 92.15
2017-10-28 06:00 | 121.23 | 92.61
2017-10-28 06:30 | 121.69 | 91.05
2017-10-28 07:00 | 120.01 | 91.23
2017-10-28 07:30 | 119.22 | 90.64
2017-10-28 08:00 | 119.47 | 90.5
2017-10-28 08:30 | 118.16 | 87.1
2017-10-28 09:00 | 122.77 | 93.16
2017-10-28 09:30 | 125.09 | 98.76
2017-10-28 10:00 | 125.21 | 98.17
2017-10-28 10:30 | 120.12 | 92.27
2017-10-28 11:00 | 117.82 | 89.52
2017-10-28 11:30 | 127.38 | 99.21
2017-10-28 12:00 | 124.91 | 96.5
2017-10-28 12:30 | 129.65 | 100.63
2017-10-28 13:00 | 131.81 | 102.67
2017-10-28 13:30 | 131.04 | 99.5
2017-10-28 14:00 | 136.87 | 107.44
2017-10-28 14:30 | 129.83 | 98.48
2017-10-28 15:00 | 135.02 | 105.2
2017-10-28 15:30 | 130.68 | 100.96
2017-10-28 16:00 | 130.07 | 99.07
2017-10-28 16:30 | 137.82 | 109.84
2017-10-28 17:00 | 130.57 | 102.33
2017-10-28 17:30 | 134.47 | 105.08
2017-10-28 18:00 | 130.99 | 100.8
2017-10-28 18:30 | 124.12 | 91.8
2017-10-28 19:00 | 127.07 | 97.26
2017-10-28 19:30 | 125.67 | 94.21
2017-10-28 20:00 | 125.87 | 94.55
2017-10-28 20:30 | 125.54 | 94.44
2017-10-28 21:00 | 127.04 | 96.34
2017-10-28 21:30 | 127.91 | 98.83
2017-10-28 22:00 | 131.97 | 105.27
2017-10-28 22:30 | 136.34 | 109.28
2017-10-28 23:00 | 129.07 | 100.4
2017-10-28 23:30 | 119.15 | 89.84
2017-10-29 | 129.65 | 102.07
2017-10-29 00:30 | 132.16 | 104.05
2017-10-29 01:00 | 131.4 | 103.85
2017-10-29 01:30 | 126.65 | 98.33
2017-10-29 02:00 | 122.8 | 94.69
2017-10-29 02:30 | 123.83 | 96.43
2017-10-29 03:00 | 122.65 | 94.7
2017-10-29 03:30 | 126.61 | 97.43
2017-10-29 04:00 | 134.19 | 106.84
2017-10-29 04:30 | 136.03 | 108.12
2017-10-29 05:00 | 130.91 | 102.34
2017-10-29 05:30 | 132.9 | 104.73
2017-10-29 06:00 | 127.36 | 100.09
2017-10-29 06:30 | 111.44 | 80.33
2017-10-29 07:00 | 123.41 | 95.74
2017-10-29 07:30 | 125.61 | 97.03
2017-10-29 08:00 | 121.9 | 92.3
2017-10-29 08:30 | 120.92 | 90.24
2017-10-29 09:00 | 123.03 | 93.8
2017-10-29 09:30 | 133.37 | 103.5
2017-10-29 10:00 | 126.12 | 94.29
2017-10-29 10:30 | 129.76 | 98.62
2017-10-29 11:00 | 128.55 | 97.25
2017-10-29 11:30 | 131.16 | 99.47
2017-10-29 12:00 | 132.91 | 103.02
2017-10-29 12:30 | 137.17 | 106.37
2017-10-29 13:00 | 131.87 | 100.88
2017-10-29 13:30 | 134.91 | 104.45
2017-10-29 14:00 | 139.73 | 107.82
2017-10-29 14:30 | 137.21 | 104.91
2017-10-29 15:00 | 141.6 | 110.02
2017-10-29 15:30 | 137.38 | 104.74
2017-10-29 16:00 | 134.9 | 101.96
2017-10-29 16:30 | 140.34 | 108.35
2017-10-29 17:00 | 140.58 | 107.93
2017-10-29 17:30 | 138.51 | 106.3
2017-10-29 18:00 | 140.57 | 108.32
2017-10-29 18:30 | 133.04 | 100.43
2017-10-29 19:00 | 138.13 | 107.18
2017-10-29 19:30 | 140.88 | 110.04
2017-10-29 20:00 | 135.77 | 104.04
2017-10-29 20:30 | 129.12 | 99.21
2017-10-29 21:00 | 137.43 | 108.05
2017-10-29 21:30 | 136.39 | 106.53
2017-10-29 22:00 | 130.53 | 100.45
2017-10-29 22:30 | 134.17 | 105.3
2017-10-29 23:00 | 128.66 | 100.6
2017-10-29 23:30 | 129.42 | 100.67
2017-10-30 | 129.49 | 100.9
2017-10-30 00:30 | 124.74 | 97.96
2017-10-30 01:00 | 119.29 | 90.43
2017-10-30 01:30 | 132.73 | 103.4
2017-10-30 02:00 | 127.26 | 98.65
2017-10-30 02:30 | 129.61 | 100.62
2017-10-30 03:00 | 128.11 | 97.79
2017-10-30 03:30 | 129.86 | 100.02
2017-10-30 04:00 | 123.77 | 93.62
2017-10-30 04:30 | 119.01 | 88.98
2017-10-30 05:00 | 121.92 | 92.51
2017-10-30 05:30 | 127.45 | 99.4
2017-10-30 06:00 | 123.46 | 94.83
2017-10-30 06:30 | 118.83 | 88.69
2017-10-30 07:00 | 122.78 | 93.06
2017-10-30 07:30 | 126.57 | 96.65
2017-10-30 08:00 | 124.26 | 92.25
2017-10-30 08:30 | 126.06 | 93.96
2017-10-30 09:00 | 122.36 | 90.95
2017-10-30 09:30 | 122.35 | 90.77
2017-10-30 10:00 | 124.39 | 92.86
2017-10-30 10:30 | 131.96 | 100.49
2017-10-30 11:00 | 126.98 | 95.28
2017-10-30 11:30 | 128.97 | 96.99
2017-10-30 12:00 | 129.76 | 98.18
2017-10-30 12:30 | 128.34 | 95.74
2017-10-30 13:00 | 130.2 | 98.54
2017-10-30 13:30 | 128.53 | 98.03
2017-10-30 14:00 | 127.98 | 97.13
2017-10-30 14:30 | 132.8 | 100.77
2017-10-30 15:00 | 124.93 | 94.15
2017-10-30 15:30 | 121.57 | 92.24
2017-10-30 16:00 | 121.56 | 95.73
2017-10-30 16:30 | 118.95 | 96.78
2017-10-30 17:00 | 116.12 | 93.69
2017-10-30 17:30 | 125.02 | 102.87
2017-10-30 18:00 | 124.07 | 102.17
2017-10-30 18:30 | 113.66 | 90.51
2017-10-30 19:00 | 115.82 | 93.11
2017-10-30 19:30 | 117.54 | 94.87
2017-10-30 20:00 | 113.21 | 89.24
2017-10-30 20:30 | 118.78 | 95.3
2017-10-30 21:00 | 111.28 | 88.49
2017-10-30 21:30 | 114.12 | 91.62
2017-10-30 22:00 | 108.72 | 86.52
2017-10-30 22:30 | 106.16 | 83.35
2017-10-30 23:00 | 104.1 | 82.26
2017-10-30 23:30 | 103.4 | 83.44
2017-10-31 | 104.97 | 84.6
2017-10-31 00:30 | 100.52 | 77.83
2017-10-31 01:00 | 104.69 | 82.89
2017-10-31 01:30 | 110.84 | 90.51
2017-10-31 02:00 | 108.16 | 87.44
2017-10-31 02:30 | 108.3 | 88.88
2017-10-31 03:00 | 106.89 | 87.42
2017-10-31 03:30 | 98.02 | 78.16
2017-10-31 04:00 | 106.21 | 86.13
2017-10-31 04:30 | 107.94 | 89.37
2017-10-31 05:00 | 102.89 | 81.34
2017-10-31 05:30 | 109.46 | 86.74
2017-10-31 06:00 | 105.55 | 82.31
2017-10-31 06:30 | 104.1 | 80.73
2017-10-31 07:00 | 100.24 | 78.57
2017-10-31 07:30 | 102.12 | 80.04
2017-10-31 08:00 | 100.89 | 78.36
2017-10-31 08:30 | 100.42 | 78.62
2017-10-31 09:00 | 95.13 | 72.7
2017-10-31 09:30 | 100.28 | 78.1
2017-10-31 10:00 | 106.88 | 85.02
2017-10-31 10:30 | 102.71 | 80.52
2017-10-31 11:00 | 101.72 | 78.16
2017-10-31 11:30 | 105.45 | 82.57
2017-10-31 12:00 | 105.59 | 80.04
2017-10-31 12:30 | 105.61 | 81.36
2017-10-31 13:00 | 110.38 | 86.77
2017-10-31 13:30 | 114.54 | 93.04
2017-10-31 14:00 | 119.87 | 96.89
2017-10-31 14:30 | 115.33 | 91.52
2017-10-31 15:00 | 112.47 | 87.29
2017-10-31 15:30 | 113.47 | 87.96
2017-10-31 16:00 | 109.59 | 83.1
2017-10-31 16:30 | 113.98 | 86.4
2017-10-31 17:00 | 118.59 | 91.83
2017-10-31 17:30 | 120.87 | 95.6
2017-10-31 18:00 | 126.42 | 102.04
2017-10-31 18:30 | 111.21 | 83.58
2017-10-31 19:00 | 122.05 | 97.56
2017-10-31 19:30 | 132.56 | 107.96
2017-10-31 20:00 | 126.15 | 101.03
2017-10-31 20:30 | 123.9 | 99.07
2017-10-31 21:00 | 129.97 | 104.66
2017-10-31 21:30 | 118.57 | 94.88
2017-10-31 22:00 | 122.77 | 99.66
2017-10-31 22:30 | 121.97 | 96.86
2017-10-31 23:00 | 118.6 | 94.03
2017-10-31 23:30 | 116.01 | 93.19
2017-11-01 | 110.93 | 87.59
2017-11-01 00:30 | 108.34 | 87.32
2017-11-01 01:00 | 110.81 | 89.71
2017-11-01 01:30 | 107.71 | 85.32
2017-11-01 02:00 | 111.6 | 88.95
2017-11-01 02:30 | 110.55 | 87.98
2017-11-01 03:00 | 106.49 | 84.81
2017-11-01 03:30 | 102.09 | 81.88
2017-11-01 04:00 | 105.74 | 84.75
2017-11-01 04:30 | 113.94 | 94.15
2017-11-01 05:00 | 107.41 | 87.98
2017-11-01 05:30 | 89.39 | 72.12
2017-11-01 06:00 | 91.28 | 73.66
2017-11-01 06:30 | 82.1 | 61.96
2017-11-01 07:00 | 86.03 | 64.79
2017-11-01 07:30 | 89.66 | 69.46
2017-11-01 08:00 | 89.03 | 67.64
2017-11-01 08:30 | 81.81 | 58.58
2017-11-01 09:00 | 89.81 | 67.43
2017-11-01 09:30 | 91.5 | 68.3
2017-11-01 10:00 | 101.34 | 79.52
2017-11-01 10:30 | 107.04 | 82.92
2017-11-01 11:00 | 106.83 | 81.6
2017-11-01 11:30 | 103.54 | 78.48
2017-11-01 12:00 | 107.17 | 81.59
2017-11-01 12:30 | 106.45 | 81.65
2017-11-01 13:00 | 110.75 | 86.65
2017-11-01 13:30 | 111.77 | 86.91
2017-11-01 14:00 | 115.6 | 90.2
2017-11-01 14:30 | 118.26 | 92.09
2017-11-01 15:00 | 112.79 | 86.36
2017-11-01 15:30 | 113.89 | 87.79
2017-11-01 16:00 | 118.41 | 93.51
2017-11-01 16:30 | 118 | 92.64
2017-11-01 17:00 | 117.66 | 90.98
2017-11-01 17:30 | 120.47 | 96.16
2017-11-01 18:00 | 125.12 | 101.48
2017-11-01 18:30 | 109.61 | 83.43
2017-11-01 19:00 | 113.07 | 86.74
2017-11-01 19:30 | 114.57 | 86.73
2017-11-01 20:00 | 111.6 | 83.95
2017-11-01 20:30 | 112.83 | 84.22
2017-11-01 21:00 | 114.69 | 86.98
2017-11-01 21:30 | 104.73 | 78.03
2017-11-01 22:00 | 100.35 | 74.9
2017-11-01 22:30 | 107.36 | 82.45
2017-11-01 23:00 | 102.89 | 79.19
2017-11-01 23:30 | 101.24 | 77.2
2017-11-02 | 100.44 | 73.79
2017-11-02 00:30 | 100.67 | 73.66
2017-11-02 01:00 | 104.19 | 77.08
2017-11-02 01:30 | 105 | 78.79
2017-11-02 02:00 | 109.23 | 84.54
2017-11-02 02:30 | 103.26 | 79.51
2017-11-02 03:00 | 106.36 | 82.81
2017-11-02 03:30 | 99.07 | 73.59
2017-11-02 04:00 | 98.44 | 73.9
2017-11-02 04:30 | 105.02 | 81.49
2017-11-02 05:00 | 105.4 | 81.06
2017-11-02 05:30 | 112.65 | 90.08
2017-11-02 06:00 | 111.39 | 88.28
2017-11-02 06:30 | 96.4 | 69.92
2017-11-02 07:00 | 104.68 | 80.19
2017-11-02 07:30 | 114.06 | 88.88
2017-11-02 08:00 | 113.12 | 86.78
2017-11-02 08:30 | 117.33 | 91.49
2017-11-02 09:00 | 112 | 86.31
2017-11-02 09:30 | 116.5 | 90.95
2017-11-02 10:00 | 118.85 | 93.33
2017-11-02 10:30 | 118.92 | 94.54
2017-11-02 11:00 | 120.85 | 97.76
2017-11-02 11:30 | 115.05 | 91.04
2017-11-02 12:00 | 112.07 | 86.85
2017-11-02 12:30 | 123.09 | 98.28
2017-11-02 13:00 | 122.25 | 94.69
2017-11-02 13:30 | 115.23 | 89.96
2017-11-02 14:00 | 113.56 | 90.43
2017-11-02 14:30 | 125.68 | 101.09
2017-11-02 15:00 | 120.08 | 94.95
2017-11-02 15:30 | 124.63 | 99.37
2017-11-02 16:00 | 122.07 | 95.66
2017-11-02 16:30 | 117.89 | 92.14
2017-11-02 17:00 | 118.14 | 91.87
2017-11-02 17:30 | 118.63 | 92.01
2017-11-02 18:00 | 125.99 | 98.62
2017-11-02 18:30 | 120.22 | 91.83
2017-11-02 19:00 | 129.08 | 100.95
2017-11-02 19:30 | 126.79 | 97.68
2017-11-02 20:00 | 128.92 | 99.26
2017-11-02 20:30 | 131.77 | 103.46
2017-11-02 21:00 | 133.66 | 106.8
2017-11-02 21:30 | 129.42 | 101.38
2017-11-02 22:00 | 122.53 | 94.56
2017-11-02 22:30 | 122.16 | 94.22
2017-11-02 23:00 | 124.83 | 96.56
2017-11-02 23:30 | 119.9 | 91.65
2017-11-03 | 120.48 | 92.83
2017-11-03 00:30 | 121.4 | 92.94
2017-11-03 01:00 | 123.56 | 95.88
2017-11-03 01:30 | 115.61 | 85.62
2017-11-03 02:00 | 122.62 | 93.37
2017-11-03 02:30 | 120.31 | 91.06
2017-11-03 03:00 | 121.07 | 92.58
2017-11-03 03:30 | 118.63 | 90.45
2017-11-03 04:00 | 122.24 | 94.82
2017-11-03 04:30 | 116.62 | 87.82
2017-11-03 05:00 | 119.93 | 91.79
2017-11-03 05:30 | 118.78 | 91.12
2017-11-03 06:00 | 116.87 | 90.19
2017-11-03 06:30 | 110.1 | 79.7
2017-11-03 07:00 | 114.08 | 84.2
2017-11-03 07:30 | 123.31 | 93.18
2017-11-03 08:00 | 118.41 | 88.04
2017-11-03 08:30 | 121.34 | 91.56
2017-11-03 09:00 | 119.01 | 87.44
2017-11-03 09:30 | 120.36 | 87.67
2017-11-03 10:00 | 122.06 | 91.44
2017-11-03 10:30 | 117.96 | 86.58
2017-11-03 11:00 | 120.05 | 91.23
2017-11-03 11:30 | 115.24 | 85.07
2017-11-03 12:00 | 120.02 | 90.51
2017-11-03 12:30 | 124.05 | 93.44
2017-11-03 13:00 | 122.82 | 92.9
2017-11-03 13:30 | 128.52 | 96.75
2017-11-03 14:00 | 129.61 | 96.02
2017-11-03 14:30 | 134.17 | 100.51
2017-11-03 15:00 | 130.34 | 96.69
2017-11-03 15:30 | 130.53 | 98.02
2017-11-03 16:00 | 131.14 | 99.26
2017-11-03 16:30 | 125.81 | 92.45
2017-11-03 17:00 | 133.46 | 97.41
2017-11-03 17:30 | 127.53 | 91.49
2017-11-03 18:00 | 132.37 | 99.71
2017-11-03 18:30 | 131.09 | 96.12
2017-11-03 19:00 | 134.22 | 99.48
2017-11-03 19:30 | 132.94 | 97.7
2017-11-03 20:00 | 134.8 | 98.79
2017-11-03 20:30 | 131.05 | 96.19
2017-11-03 21:00 | 131.93 | 98.56
2017-11-03 21:30 | 127.57 | 93.74
2017-11-03 22:00 | 128.81 | 95.08
2017-11-03 22:30 | 136.5 | 105.01
2017-11-03 23:00 | 129.77 | 98.58
2017-11-03 23:30 | 130.76 | 101.65
2017-11-04 | 127.6 | 98.87
2017-11-04 00:30 | 125.02 | 97.29
2017-11-04 01:00 | 123.51 | 94.86
2017-11-04 01:30 | 123.4 | 94.99
2017-11-04 02:00 | 124.72 | 97.7
2017-11-04 02:30 | 122.5 | 94.05
2017-11-04 03:00 | 121.11 | 93.09
2017-11-04 03:30 | 129.63 | 101.51
2017-11-04 04:00 | 130.79 | 101.66
2017-11-04 04:30 | 141.59 | 113.83
2017-11-04 05:00 | 133.16 | 105.67
2017-11-04 05:30 | 130.53 | 104.79
2017-11-04 06:00 | 121.86 | 94.85
2017-11-04 06:30 | 112.52 | 84.23
2017-11-04 07:00 | 116.67 | 90.34
2017-11-04 07:30 | 127.2 | 101.25
2017-11-04 08:00 | 122.39 | 95.08
2017-11-04 08:30 | 124.42 | 98.06
2017-11-04 09:00 | 118.99 | 91.07
2017-11-04 09:30 | 123.02 | 94.56
2017-11-04 10:00 | 124.76 | 95.59
2017-11-04 10:30 | 123.51 | 92.99
2017-11-04 11:00 | 125.37 | 95.86
2017-11-04 11:30 | 129.34 | 100.84
2017-11-04 12:00 | 137.53 | 106.81
2017-11-04 12:30 | 134.41 | 105.45
2017-11-04 13:00 | 138.16 | 110.93
2017-11-04 13:30 | 139.74 | 113
2017-11-04 14:00 | 143.22 | 115.89
2017-11-04 14:30 | 143.25 | 114.96
2017-11-04 15:00 | 136.58 | 105.6
2017-11-04 15:30 | 139.59 | 107.11
2017-11-04 16:00 | 139.35 | 106.11
2017-11-04 16:30 | 136.49 | 103.78
2017-11-04 17:00 | 132.41 | 98.95
2017-11-04 17:30 | 140.66 | 109.42
2017-11-04 18:00 | 138.62 | 109.17
2017-11-04 18:30 | 126.18 | 94.44
2017-11-04 19:00 | 129.85 | 99.06
2017-11-04 19:30 | 125.16 | 94.09
2017-11-04 20:00 | 131.74 | 102.72
2017-11-04 20:30 | 133.55 | 103.57
2017-11-04 21:00 | 130.68 | 101.73
2017-11-04 21:30 | 126.53 | 99.89
2017-11-04 22:00 | 122.92 | 96.28
2017-11-04 22:30 | 123.21 | 96.53
2017-11-04 23:00 | 127.35 | 101.18
2017-11-04 23:30 | 121.39 | 94.72
2017-11-05 | 120.4 | 92.29
2017-11-05 00:30 | 125.39 | 99.22
2017-11-05 01:00 | 127.1 | 101.91
2017-11-05 01:30 | 118.63 | 93.14
2017-11-05 02:00 | 127.29 | 100
2017-11-05 02:30 | 131.14 | 105.05
2017-11-05 03:00 | 131.51 | 105.51
2017-11-05 03:30 | 127.83 | 99.74
2017-11-05 04:00 | 125.78 | 96.74
2017-11-05 04:30 | 126 | 98.84
2017-11-05 05:00 | 123.04 | 96.74
2017-11-05 05:30 | 118.59 | 92.53
2017-11-05 06:00 | 116.89 | 90.41
2017-11-05 06:30 | 111.51 | 84.13
2017-11-05 07:00 | 117.48 | 91
2017-11-05 07:30 | 122.65 | 96.21
2017-11-05 08:00 | 128.77 | 103.41
2017-11-05 08:30 | 120.47 | 92.59
2017-11-05 09:00 | 125.95 | 97.01
2017-11-05 09:30 | 121.21 | 93.99
2017-11-05 10:00 | 119.1 | 91.42
2017-11-05 10:30 | 118.66 | 92.01
2017-11-05 11:00 | 124.38 | 98.38
2017-11-05 11:30 | 126.85 | 102.1
2017-11-05 12:00 | 124.04 | 97.39
2017-11-05 12:30 | 118.95 | 91.32
2017-11-05 13:00 | 121.34 | 94.16
2017-11-05 13:30 | 127.85 | 102.17
2017-11-05 14:00 | 125.82 | 98.76
2017-11-05 14:30 | 124.01 | 95.82
2017-11-05 15:00 | 128.66 | 99.95
2017-11-05 15:30 | 134.29 | 106.41
2017-11-05 16:00 | 134.36 | 104.56
2017-11-05 16:30 | 133.33 | 104.6
2017-11-05 17:00 | 139.61 | 110.17
2017-11-05 17:30 | 140.68 | 111.5
2017-11-05 18:00 | 143.92 | 114.88
2017-11-05 18:30 | 134.07 | 102.23
2017-11-05 19:00 | 134.88 | 104.08
2017-11-05 19:30 | 135.26 | 104.37
2017-11-05 20:00 | 138.47 | 109.4
2017-11-05 20:30 | 126.58 | 96.44
2017-11-05 21:00 | 124.84 | 95.42
2017-11-05 21:30 | 125.73 | 96.39
2017-11-05 22:00 | 128.97 | 101
2017-11-05 22:30 | 129.17 | 103.94
2017-11-05 23:00 | 126.77 | 100.12
2017-11-05 23:30 | 132.4 | 105.3
2017-11-06 | 126.92 | 100.06
2017-11-06 00:30 | 124.12 | 95.06
2017-11-06 01:00 | 125.65 | 96.95
2017-11-06 01:30 | 130.33 | 103.2
2017-11-06 02:00 | 132.55 | 104.73
2017-11-06 02:30 | 128.61 | 100.26
2017-11-06 03:00 | 131.78 | 102.87
2017-11-06 03:30 | 127.16 | 98.44
2017-11-06 04:00 | 132.25 | 105.08
2017-11-06 04:30 | 135.6 | 107.74
2017-11-06 05:00 | 127.13 | 98.83
2017-11-06 05:30 | 130.83 | 101.77
2017-11-06 06:00 | 129.36 | 101.43
2017-11-06 06:30 | 114.87 | 83.42
2017-11-06 07:00 | 125.55 | 97.05
2017-11-06 07:30 | 134.42 | 105.95
2017-11-06 08:00 | 132.37 | 102.61
2017-11-06 08:30 | 133.33 | 102.4
2017-11-06 09:00 | 128.1 | 94.72
2017-11-06 09:30 | 128.82 | 94.94
2017-11-06 10:00 | 134.9 | 101.69
2017-11-06 10:30 | 128.41 | 93.16
2017-11-06 11:00 | 130.92 | 96.01
2017-11-06 11:30 | 133.79 | 99.36
2017-11-06 12:00 | 135.62 | 102.96
2017-11-06 12:30 | 130.8 | 98.2
2017-11-06 13:00 | 133.42 | 101.19
2017-11-06 13:30 | 133.88 | 101.14
2017-11-06 14:00 | 132.01 | 96.92
2017-11-06 14:30 | 137.04 | 101.7
2017-11-06 15:00 | 135.03 | 100.21
2017-11-06 15:30 | 141.91 | 108.13
2017-11-06 16:00 | 138.98 | 104.95
2017-11-06 16:30 | 140.95 | 107.22
2017-11-06 17:00 | 139.11 | 105.13
2017-11-06 17:30 | 137.77 | 104.88
2017-11-06 18:00 | 139.65 | 106.02
2017-11-06 18:30 | 138.66 | 105.09
2017-11-06 19:00 | 138.25 | 105.33
2017-11-06 19:30 | 139.63 | 106.88
2017-11-06 20:00 | 139.7 | 106.84
2017-11-06 20:30 | 146.81 | 116.93
2017-11-06 21:00 | 146.84 | 118.03
2017-11-06 21:30 | 137.74 | 109.21
2017-11-06 22:00 | 135.34 | 106.44
2017-11-06 22:30 | 129.66 | 100.6
2017-11-06 23:00 | 131.12 | 101.26
2017-11-06 23:30 | 131.12 | 103.23
2017-11-07 | 134.76 | 107.28
2017-11-07 00:30 | 132.06 | 105.09
2017-11-07 01:00 | 129.06 | 102.05
2017-11-07 01:30 | 137.12 | 109.55
2017-11-07 02:00 | 138.41 | 111.05
2017-11-07 02:30 | 134.4 | 107.07
2017-11-07 03:00 | 133.43 | 107.48
2017-11-07 03:30 | 127.33 | 100.21
2017-11-07 04:00 | 127.13 | 101.11
2017-11-07 04:30 | 129.42 | 105.19
2017-11-07 05:00 | 125.1 | 100.08
2017-11-07 05:30 | 124.66 | 99.55
2017-11-07 06:00 | 129.64 | 106.71
2017-11-07 06:30 | 107 | 82.03
2017-11-07 07:00 | 113.94 | 90.97
2017-11-07 07:30 | 114.9 | 91.83
2017-11-07 08:00 | 116.87 | 92.74
2017-11-07 08:30 | 117.09 | 93.48
2017-11-07 09:00 | 114.18 | 88.23
2017-11-07 09:30 | 110.81 | 85.82
2017-11-07 10:00 | 107.33 | 82.06
2017-11-07 10:30 | 110.93 | 85.76
2017-11-07 11:00 | 116.26 | 91.69
2017-11-07 11:30 | 112.7 | 86.69
2017-11-07 12:00 | 114.84 | 89.61
2017-11-07 12:30 | 116.2 | 90.6
2017-11-07 13:00 | 114.45 | 88.44
2017-11-07 13:30 | 123.43 | 98.97
2017-11-07 14:00 | 127.17 | 103.43
2017-11-07 14:30 | 121.48 | 97.56
2017-11-07 15:00 | 125.58 | 100.16
2017-11-07 15:30 | 121.13 | 94.6
2017-11-07 16:00 | 126.76 | 101.3
2017-11-07 16:30 | 125.65 | 100.55
2017-11-07 17:00 | 119.63 | 93.68
2017-11-07 17:30 | 122.98 | 98.39
2017-11-07 18:00 | 114.56 | 90.52
2017-11-07 18:30 | 107.57 | 82.81
2017-11-07 19:00 | 112.27 | 88.09
2017-11-07 19:30 | 117.4 | 94.37
2017-11-07 20:00 | 123.11 | 98.84
2017-11-07 20:30 | 121.75 | 98.07
2017-11-07 21:00 | 124.03 | 98.29
2017-11-07 21:30 | 114.92 | 87.63
2017-11-07 22:00 | 110.49 | 81.31
2017-11-07 22:30 | 112.09 | 84.18
2017-11-07 23:00 | 121.61 | 94.74
2017-11-07 23:30 | 117.58 | 89.11
2017-11-08 | 117.16 | 89.87
2017-11-08 00:30 | 120.81 | 93.43
2017-11-08 01:00 | 118 | 92.75
2017-11-08 01:30 | 113.95 | 89.55
2017-11-08 02:00 | 112.84 | 88.34
2017-11-08 02:30 | 123.99 | 101.19
2017-11-08 03:00 | 123.61 | 100.56
2017-11-08 03:30 | 122.63 | 100.42
2017-11-08 04:00 | 119.62 | 96.28
2017-11-08 04:30 | 126.7 | 102.58
2017-11-08 05:00 | 127.36 | 103.28
2017-11-08 05:30 | 123.43 | 100.53
2017-11-08 06:00 | 115.14 | 93.74
2017-11-08 06:30 | 105.94 | 80.78
2017-11-08 07:00 | 113.91 | 89.66
2017-11-08 07:30 | 107.77 | 83.65
2017-11-08 08:00 | 120.55 | 94.41
2017-11-08 08:30 | 116.62 | 89.22
2017-11-08 09:00 | 119.6 | 90.7
2017-11-08 09:30 | 120.69 | 90.43
2017-11-08 10:00 | 120.74 | 90.92
2017-11-08 10:30 | 122.4 | 92.36
2017-11-08 11:00 | 122.78 | 93.24
2017-11-08 11:30 | 124.86 | 96.52
2017-11-08 12:00 | 130.87 | 101.84
2017-11-08 12:30 | 138.5 | 109.38
2017-11-08 13:00 | 142.35 | 110.46
2017-11-08 13:30 | 143 | 111.3
2017-11-08 14:00 | 138.19 | 105
2017-11-08 14:30 | 140.7 | 109.5
2017-11-08 15:00 | 139.26 | 106.86
2017-11-08 15:30 | 143.12 | 110.46
2017-11-08 16:00 | 143.46 | 110.32
2017-11-08 16:30 | 138.53 | 105.94
2017-11-08 17:00 | 137.41 | 105.1
2017-11-08 17:30 | 137.18 | 106.15
2017-11-08 18:00 | 140.34 | 112.03
2017-11-08 18:30 | 135.22 | 104.74
2017-11-08 19:00 | 139.11 | 110.52
2017-11-08 19:30 | 144.39 | 116.81
2017-11-08 20:00 | 140.1 | 112.4
2017-11-08 20:30 | 136.76 | 107.56
2017-11-08 21:00 | 140.15 | 111.44
2017-11-08 21:30 | 144.93 | 116.78
2017-11-08 22:00 | 143.15 | 115.87
2017-11-08 22:30 | 138.37 | 111.77
2017-11-08 23:00 | 144.21 | 116.98
2017-11-08 23:30 | 133.17 | 105.6
2017-11-09 | 138.17 | 111.75
2017-11-09 00:30 | 136.28 | 108.46
2017-11-09 01:00 | 135.75 | 106.66
2017-11-09 01:30 | 130.4 | 102.13
2017-11-09 02:00 | 134.3 | 107.36
2017-11-09 02:30 | 134.97 | 107.78
2017-11-09 03:00 | 134.68 | 107.52
2017-11-09 03:30 | 133.02 | 107.38
2017-11-09 04:00 | 126.62 | 99.77
2017-11-09 04:30 | 126.96 | 100.54
2017-11-09 05:00 | 126.96 | 100
2017-11-09 05:30 | 128.82 | 102.26
2017-11-09 06:00 | 126.36 | 101.68
2017-11-09 06:30 | 116.58 | 89.6
2017-11-09 07:00 | 117.4 | 91.16
2017-11-09 07:30 | 121.26 | 94.89
2017-11-09 08:00 | 124.49 | 99.02
2017-11-09 08:30 | 121.35 | 95.13
2017-11-09 09:00 | 118.37 | 89.72
2017-11-09 09:30 | 115.63 | 86.77
2017-11-09 10:00 | 113.44 | 84.12
2017-11-09 10:30 | 116.83 | 86.67
2017-11-09 11:00 | 113.59 | 84.69
2017-11-09 11:30 | 115.44 | 84.77
2017-11-09 12:00 | 117.72 | 88.63
2017-11-09 12:30 | 117.38 | 86.59
2017-11-09 13:00 | 122.41 | 92.54
2017-11-09 13:30 | 120.94 | 90.9
2017-11-09 14:00 | 126.87 | 97.49
2017-11-09 14:30 | 120.45 | 90.41
2017-11-09 15:00 | 119.22 | 87
2017-11-09 15:30 | 121.35 | 89.05
2017-11-09 16:00 | 125.06 | 92.95
2017-11-09 16:30 | 119.82 | 87.79
2017-11-09 17:00 | 122.27 | 91.29
2017-11-09 17:30 | 123.25 | 92.56
2017-11-09 18:00 | 132.65 | 104.31
2017-11-09 18:30 | 127.81 | 96.43
2017-11-09 19:00 | 129.51 | 100.3
2017-11-09 19:30 | 136.77 | 106.6
2017-11-09 20:00 | 126.14 | 94.97
2017-11-09 20:30 | 125.76 | 92.52
2017-11-09 21:00 | 131.87 | 100.53
2017-11-09 21:30 | 127.93 | 97.82
2017-11-09 22:00 | 133.14 | 104.28
2017-11-09 22:30 | 130.77 | 103.01
2017-11-09 23:00 | 126.91 | 99.11
2017-11-09 23:30 | 124.54 | 95.69
2017-11-10 | 132.4 | 105.82
2017-11-10 00:30 | 132.56 | 105.35
2017-11-10 01:00 | 134.21 | 107.63
2017-11-10 01:30 | 129.64 | 102.98
2017-11-10 02:00 | 130.35 | 103.07
2017-11-10 02:30 | 119.13 | 90.35
2017-11-10 03:00 | 121.78 | 94.12
2017-11-10 03:30 | 125.09 | 97.66
2017-11-10 04:00 | 131.7 | 103.38
2017-11-10 04:30 | 127.84 | 100.77
2017-11-10 05:00 | 124.52 | 97.56
2017-11-10 05:30 | 124.21 | 98.41
2017-11-10 06:00 | 120.58 | 96.13
2017-11-10 06:30 | 120.82 | 95.11
2017-11-10 07:00 | 121.17 | 94.16
2017-11-10 07:30 | 127.79 | 100.75
2017-11-10 08:00 | 124.25 | 96.61
2017-11-10 08:30 | 121.12 | 93.25
2017-11-10 09:00 | 116.13 | 85.26
2017-11-10 09:30 | 116.18 | 85.15
2017-11-10 10:00 | 116.31 | 86.03
2017-11-10 10:30 | 118.03 | 90.56
2017-11-10 11:00 | 115.3 | 87.33
2017-11-10 11:30 | 126.09 | 98.52
2017-11-10 12:00 | 125.62 | 97.56
2017-11-10 12:30 | 123.63 | 95.14
2017-11-10 13:00 | 117.92 | 89.91
2017-11-10 13:30 | 119.78 | 91.71
2017-11-10 14:00 | 125.04 | 96.3
2017-11-10 14:30 | 121.69 | 94.2
2017-11-10 15:00 | 123.97 | 96.5
2017-11-10 15:30 | 121.06 | 93.68
2017-11-10 16:00 | 123.03 | 96.9
2017-11-10 16:30 | 120.92 | 94.95
2017-11-10 17:00 | 128.59 | 103.33
2017-11-10 17:30 | 124.25 | 97.41
2017-11-10 18:00 | 121.91 | 95.05
2017-11-10 18:30 | 118.45 | 89.84
2017-11-10 19:00 | 124.37 | 97.94
2017-11-10 19:30 | 126.95 | 101.37
2017-11-10 20:00 | 126.31 | 99.67
2017-11-10 20:30 | 124.47 | 97.61
2017-11-10 21:00 | 125.17 | 99.09
2017-11-10 21:30 | 125.15 | 100.42
2017-11-10 22:00 | 123.8 | 99.74
2017-11-10 22:30 | 121.51 | 97.94
2017-11-10 23:00 | 118.49 | 93.86
2017-11-10 23:30 | 117 | 91.14
2017-11-11 | 114.11 | 88.76
2017-11-11 00:30 | 119.69 | 93.87
2017-11-11 01:00 | 123.59 | 98.73
2017-11-11 01:30 | 119.62 | 94.12
2017-11-11 02:00 | 122.17 | 98.14
2017-11-11 02:30 | 120.64 | 96.33
2017-11-11 03:00 | 119.14 | 94.64
2017-11-11 03:30 | 122.47 | 98.64
2017-11-11 04:00 | 122.11 | 99.35
2017-11-11 04:30 | 123 | 101.14
2017-11-11 05:00 | 124.68 | 101.56
2017-11-11 05:30 | 124.3 | 101.83
2017-11-11 06:00 | 121.41 | 98.83
2017-11-11 06:30 | 116.67 | 93.45
2017-11-11 07:00 | 122.01 | 100.24
2017-11-11 07:30 | 121.79 | 100.63
2017-11-11 08:00 | 118.93 | 96.99
2017-11-11 08:30 | 113.44 | 89.28
2017-11-11 09:00 | 117.45 | 91.26
2017-11-11 09:30 | 120.6 | 96.46
2017-11-11 10:00 | 119.3 | 95.15
2017-11-11 10:30 | 113.34 | 86.26
2017-11-11 11:00 | 115.3 | 90.79
2017-11-11 11:30 | 120.63 | 96.85
2017-11-11 12:00 | 117.86 | 94.38
2017-11-11 12:30 | 118.78 | 94.21
2017-11-11 13:00 | 117.75 | 93.19
2017-11-11 13:30 | 115.68 | 90.34
2017-11-11 14:00 | 117.47 | 92.87
2017-11-11 14:30 | 125.76 | 102.99
2017-11-11 15:00 | 126.02 | 101.86
2017-11-11 15:30 | 125.34 | 101.21
2017-11-11 16:00 | 125.74 | 102.1
2017-11-11 16:30 | 133.94 | 111.13
2017-11-11 17:00 | 128.8 | 104.18
2017-11-11 17:30 | 117.83 | 91.62
2017-11-11 18:00 | 119.53 | 93.41
2017-11-11 18:30 | 113.22 | 85.4
2017-11-11 19:00 | 122.48 | 99.19
2017-11-11 19:30 | 112.95 | 87.96
2017-11-11 20:00 | 124.25 | 99.7
2017-11-11 20:30 | 122.83 | 97.93
2017-11-11 21:00 | 122.89 | 98.52
2017-11-11 21:30 | 120.9 | 94.89
2017-11-11 22:00 | 124.81 | 99.44
2017-11-11 22:30 | 116.73 | 90.84
2017-11-11 23:00 | 122.49 | 97.89
2017-11-11 23:30 | 121.94 | 96.63
2017-11-12 | 121.63 | 97.85
2017-11-12 00:30 | 118.16 | 94.29
2017-11-12 01:00 | 125.46 | 101.92
2017-11-12 01:30 | 123.03 | 99.54
2017-11-12 02:00 | 116.39 | 92.82
2017-11-12 02:30 | 106.99 | 83.29
2017-11-12 03:00 | 107.76 | 82.85
2017-11-12 03:30 | 114.75 | 90.17
2017-11-12 04:00 | 116.6 | 92.95
2017-11-12 04:30 | 117.84 | 95.37
2017-11-12 05:00 | 112.3 | 88.89
2017-11-12 05:30 | 116.8 | 89.96
2017-11-12 06:00 | 128.23 | 102.48
2017-11-12 06:30 | 116.01 | 85.91
2017-11-12 07:00 | 112.75 | 84.86
2017-11-12 07:30 | 121.41 | 94.35
2017-11-12 08:00 | 121.11 | 92.57
2017-11-12 08:30 | 120.2 | 90.51
2017-11-12 09:00 | 121.15 | 91.13
2017-11-12 09:30 | 119.36 | 90.41
2017-11-12 10:00 | 117.88 | 88.41
2017-11-12 10:30 | 118.33 | 89.32
2017-11-12 11:00 | 120.66 | 90.26
2017-11-12 11:30 | 116.6 | 86.52
2017-11-12 12:00 | 126.86 | 99.25
2017-11-12 12:30 | 127.18 | 99.74
2017-11-12 13:00 | 121.6 | 93.64
2017-11-12 13:30 | 122.08 | 94.5
2017-11-12 14:00 | 127.49 | 100.14
2017-11-12 14:30 | 120.36 | 92.25
2017-11-12 15:00 | 115.44 | 85.18
2017-11-12 15:30 | 119.78 | 91.66
2017-11-12 16:00 | 118.53 | 91.03
2017-11-12 16:30 | 119.8 | 92.63
2017-11-12 17:00 | 128 | 101.29
2017-11-12 17:30 | 120.05 | 91.99
2017-11-12 18:00 | 118.4 | 90.27
2017-11-12 18:30 | 122.12 | 93.39
2017-11-12 19:00 | 130.5 | 101.01
2017-11-12 19:30 | 127.24 | 96.75
2017-11-12 20:00 | 127.76 | 98.2
2017-11-12 20:30 | 126.2 | 96.22
2017-11-12 21:00 | 130.97 | 101.41
2017-11-12 21:30 | 119.74 | 90.38
2017-11-12 22:00 | 121.19 | 93.84
2017-11-12 22:30 | 119.18 | 89.01
2017-11-12 23:00 | 123.86 | 94.58
2017-11-12 23:30 | 119.98 | 91.21
2017-11-13 | 120.19 | 91.82
2017-11-13 00:30 | 125.17 | 97.93
2017-11-13 01:00 | 116.01 | 89.01
2017-11-13 01:30 | 120.06 | 93.34
2017-11-13 02:00 | 118 | 92.76
2017-11-13 02:30 | 114.17 | 87.65
2017-11-13 03:00 | 117.97 | 90.09
2017-11-13 03:30 | 109.21 | 80.91
2017-11-13 04:00 | 114.36 | 86.63
2017-11-13 04:30 | 126.31 | 100.32
2017-11-13 05:00 | 122.57 | 96.96
2017-11-13 05:30 | 116.79 | 89.65
2017-11-13 06:00 | 119.02 | 92.28
2017-11-13 06:30 | 116.19 | 86.61
2017-11-13 07:00 | 118.76 | 90.82
2017-11-13 07:30 | 118.5 | 90.48
2017-11-13 08:00 | 120.45 | 90.16
2017-11-13 08:30 | 120.2 | 90.71
2017-11-13 09:00 | 119.08 | 89.24
2017-11-13 09:30 | 124.77 | 97.14
2017-11-13 10:00 | 123.81 | 94.84
2017-11-13 10:30 | 130.65 | 102.42
2017-11-13 11:00 | 127.11 | 97.56
2017-11-13 11:30 | 123.16 | 93.12
2017-11-13 12:00 | 125.22 | 95.88
2017-11-13 12:30 | 120.9 | 92.88
2017-11-13 13:00 | 120.86 | 93.29
2017-11-13 13:30 | 124.78 | 96.9
2017-11-13 14:00 | 120.87 | 93.65
2017-11-13 14:30 | 128.7 | 100.86
2017-11-13 15:00 | 121.82 | 93.21
2017-11-13 15:30 | 121.41 | 91.75
2017-11-13 16:00 | 120.38 | 91.02
2017-11-13 16:30 | 122.17 | 92.25
2017-11-13 17:00 | 122.39 | 92.9
2017-11-13 17:30 | 124.18 | 95.79
2017-11-13 18:00 | 121.11 | 93.06
2017-11-13 18:30 | 122.16 | 93.11
2017-11-13 19:00 | 128.32 | 101.15
2017-11-13 19:30 | 121.42 | 92.12
2017-11-13 20:00 | 132.33 | 102.9
2017-11-13 20:30 | 124.19 | 94.87
2017-11-13 21:00 | 126.18 | 98.34
2017-11-13 21:30 | 117.76 | 88.79
2017-11-13 22:00 | 117.75 | 89.47
2017-11-13 22:30 | 123.71 | 95.65
2017-11-13 23:00 | 122.4 | 93.06
2017-11-13 23:30 | 115.57 | 84.78
2017-11-14 | 112.83 | 83.72
2017-11-14 00:30 | 115.99 | 85.05
2017-11-14 01:00 | 125.04 | 95.61
2017-11-14 01:30 | 121.87 | 91.79
2017-11-14 02:00 | 119.65 | 89.31
2017-11-14 02:30 | 116.78 | 86.2
2017-11-14 03:00 | 115.59 | 84.73
2017-11-14 03:30 | 120.3 | 89.8
2017-11-14 04:00 | 124.46 | 94.55
2017-11-14 04:30 | 124.34 | 93.54
2017-11-14 05:00 | 124.8 | 97.25
2017-11-14 05:30 | 119.37 | 92.32
2017-11-14 06:00 | 114.02 | 86.14
2017-11-14 06:30 | 112.29 | 80.92
2017-11-14 07:00 | 115.59 | 87.09
2017-11-14 07:30 | 112.2 | 85.38
2017-11-14 08:00 | 119.08 | 92.04
2017-11-14 08:30 | 111.71 | 82.43
2017-11-14 09:00 | 112.21 | 82.96
2017-11-14 09:30 | 117.01 | 85.85
2017-11-14 10:00 | 117.67 | 87.09
2017-11-14 10:30 | 116.11 | 82.95
2017-11-14 11:00 | 119.52 | 89.25
2017-11-14 11:30 | 119.6 | 91.03
2017-11-14 12:00 | 119.39 | 89.4
2017-11-14 12:30 | 120.28 | 91.17
2017-11-14 13:00 | 121.27 | 93.3
2017-11-14 13:30 | 122.06 | 93.32
2017-11-14 14:00 | 122.49 | 94.26
2017-11-14 14:30 | 118.03 | 89.83
2017-11-14 15:00 | 125.47 | 97.08
2017-11-14 15:30 | 128.83 | 100.71
2017-11-14 16:00 | 127.2 | 97.09
2017-11-14 16:30 | 120.67 | 88.42
2017-11-14 17:00 | 124.93 | 93.78
2017-11-14 17:30 | 128.17 | 98.91
2017-11-14 18:00 | 122.31 | 93.39
2017-11-14 18:30 | 123.23 | 93.76
2017-11-14 19:00 | 130.89 | 102.94
2017-11-14 19:30 | 130.82 | 101.03
2017-11-14 20:00 | 133.13 | 103.33
2017-11-14 20:30 | 130.11 | 99.46
2017-11-14 21:00 | 128.66 | 99.43
2017-11-14 21:30 | 130.71 | 101.1
2017-11-14 22:00 | 128.19 | 99.06
2017-11-14 22:30 | 121.5 | 91.56
2017-11-14 23:00 | 121.42 | 91.69
2017-11-14 23:30 | 121.92 | 93.39
2017-11-15 | 119.7 | 90.9
2017-11-15 00:30 | 127.41 | 99.31
2017-11-15 01:00 | 127.67 | 99.39
2017-11-15 01:30 | 125.02 | 97.43
2017-11-15 02:00 | 122.36 | 94.9
2017-11-15 02:30 | 125.11 | 97.6
2017-11-15 03:00 | 126.26 | 98.89
2017-11-15 03:30 | 119.68 | 95.49
2017-11-15 04:00 | 113.36 | 88.26
2017-11-15 04:30 | 106.9 | 81.36
2017-11-15 05:00 | 109.02 | 83.75
2017-11-15 05:30 | 105.36 | 79.69
2017-11-15 06:00 | 108.05 | 82.84
2017-11-15 06:30 | 105.95 | 80.83
2017-11-15 07:00 | 111.59 | 87.79
2017-11-15 07:30 | 113.28 | 89.89
2017-11-15 08:00 | 102.17 | 77.17
2017-11-15 08:30 | 98.22 | 72.06
2017-11-15 09:00 | 95.02 | 68.46
2017-11-15 09:30 | 91.03 | 63.61
2017-11-15 10:00 | 92.56 | 64.46
2017-11-15 10:30 | 95.18 | 64.71
2017-11-15 11:00 | 93.32 | 63.9
2017-11-15 11:30 | 95.82 | 70.13
2017-11-15 12:00 | 108.43 | 82.68
2017-11-15 12:30 | 111.73 | 85.04
2017-11-15 13:00 | 108.52 | 83.09
2017-11-15 13:30 | 104.14 | 79.08
2017-11-15 14:00 | 106.16 | 80.32
2017-11-15 14:30 | 112 | 86.6
2017-11-15 15:00 | 108.39 | 81.51
2017-11-15 15:30 | 100.68 | 73.53
2017-11-15 16:00 | 104.37 | 77.38
2017-11-15 16:30 | 106.71 | 80.08
2017-11-15 17:00 | 106.21 | 81.02
2017-11-15 17:30 | 109.06 | 83.33
2017-11-15 18:00 | 105.12 | 80.37
2017-11-15 18:30 | 102.97 | 76.08
2017-11-15 19:00 | 112.06 | 86.83
2017-11-15 19:30 | 115.13 | 89.76
2017-11-15 20:00 | 115.21 | 89.08
2017-11-15 20:30 | 120.9 | 93.95
2017-11-15 21:00 | 122.46 | 98.06
2017-11-15 21:30 | 116.18 | 90.02
2017-11-15 22:00 | 117.28 | 91.89
2017-11-15 22:30 | 117.29 | 93.18
2017-11-15 23:00 | 117.87 | 95.59
2017-11-15 23:30 | 115.78 | 92.77
2017-11-16 | 116.02 | 91.98
2017-11-16 00:30 | 118.99 | 96.11
2017-11-16 01:00 | 118.8 | 95.14
2017-11-16 01:30 | 115.29 | 91.79
2017-11-16 02:00 | 120.43 | 97
2017-11-16 02:30 | 121.6 | 97.69
2017-11-16 03:00 | 113.23 | 90.33
2017-11-16 03:30 | 111.95 | 87.12
2017-11-16 04:00 | 119.93 | 96.07
2017-11-16 04:30 | 114.21 | 90.87
2017-11-16 05:00 | 115.08 | 90.86
2017-11-16 05:30 | 112.95 | 88.68
2017-11-16 06:00 | 117.26 | 93.19
2017-11-16 06:30 | 110.16 | 84.07
2017-11-16 07:00 | 124.34 | 101.67
2017-11-16 07:30 | 119.2 | 94.78
2017-11-16 08:00 | 118.1 | 94.04
2017-11-16 08:30 | 109.43 | 84.01
2017-11-16 09:00 | 114.18 | 88.55
2017-11-16 09:30 | 115.39 | 90.51
2017-11-16 10:00 | 111.29 | 87.46
2017-11-16 10:30 | 111.93 | 88.11
2017-11-16 11:00 | 114.43 | 88.92
2017-11-16 11:30 | 108.08 | 83.05
2017-11-16 12:00 | 107.13 | 80.89
2017-11-16 12:30 | 112.35 | 86.97
2017-11-16 13:00 | 120.01 | 95.31
2017-11-16 13:30 | 116.51 | 90.38
2017-11-16 14:00 | 115.52 | 87.01
2017-11-16 14:30 | 120.32 | 89.95
2017-11-16 15:00 | 120.96 | 90.28
2017-11-16 15:30 | 122.07 | 94.54
2017-11-16 16:00 | 120.35 | 91.92
2017-11-16 16:30 | 116.91 | 87.55
2017-11-16 17:00 | 118.07 | 90.71
2017-11-16 17:30 | 121.36 | 92.97
2017-11-16 18:00 | 126.83 | 97.85
2017-11-16 18:30 | 116.2 | 86.33
2017-11-16 19:00 | 117.09 | 90.18
2017-11-16 19:30 | 126.83 | 105.72
2017-11-16 20:00 | 132.87 | 112.63
2017-11-16 20:30 | 126.02 | 104.46
2017-11-16 21:00 | 125.86 | 102.19
2017-11-16 21:30 | 117.45 | 94.12
2017-11-16 22:00 | 119.18 | 94.66
2017-11-16 22:30 | 125.27 | 101.67
2017-11-16 23:00 | 121.78 | 99.32
2017-11-16 23:30 | 119.92 | 97.08
2017-11-17 | 124.38 | 102.2
2017-11-17 00:30 | 130.28 | 107.08
2017-11-17 01:00 | 127.66 | 103.48
2017-11-17 01:30 | 130.96 | 106.73
2017-11-17 02:00 | 133.28 | 108.68
2017-11-17 02:30 | 124.73 | 100.85
2017-11-17 03:00 | 119.87 | 94.51
2017-11-17 03:30 | 119.15 | 94.42
2017-11-17 04:00 | 123.37 | 100.19
2017-11-17 04:30 | 122.17 | 100.03
2017-11-17 05:00 | 119.91 | 95.78
2017-11-17 05:30 | 125.28 | 103.32
2017-11-17 06:00 | 130.44 | 109.28
2017-11-17 06:30 | 121.09 | 97.11
2017-11-17 07:00 | 119.34 | 96.08
2017-11-17 07:30 | 125.98 | 102.42
2017-11-17 08:00 | 133.88 | 109.52
2017-11-17 08:30 | 136.47 | 113.08
2017-11-17 09:00 | 133.85 | 106.76
2017-11-17 09:30 | 123.64 | 96.24
2017-11-17 10:00 | 119.9 | 90.78
2017-11-17 10:30 | 123.52 | 95.89
2017-11-17 11:00 | 122.01 | 95.8
2017-11-17 11:30 | 121.36 | 96.75
2017-11-17 12:00 | 128.24 | 102.67
2017-11-17 12:30 | 128.59 | 100.95
2017-11-17 13:00 | 134.2 | 105.45
2017-11-17 13:30 | 135.55 | 105.96
2017-11-17 14:00 | 136.64 | 106.7
2017-11-17 14:30 | 143.09 | 114.95
2017-11-17 15:00 | 143.1 | 115.09
2017-11-17 15:30 | 133.17 | 105.3
2017-11-17 16:00 | 128.84 | 98.66
2017-11-17 16:30 | 132.26 | 102.63
2017-11-17 17:00 | 136.54 | 106.89
2017-11-17 17:30 | 135.93 | 107.11
2017-11-17 18:00 | 136.97 | 109.1
2017-11-17 18:30 | 128.53 | 97.86
2017-11-17 19:00 | 137.84 | 108.85
2017-11-17 19:30 | 141.38 | 111.66
2017-11-17 20:00 | 140.82 | 110.92
2017-11-17 20:30 | 141.45 | 113.28
2017-11-17 21:00 | 135.33 | 107.66
2017-11-17 21:30 | 135.66 | 107.6
2017-11-17 22:00 | 138.05 | 110.14
2017-11-17 22:30 | 134.01 | 106.22
2017-11-17 23:00 | 129.13 | 101.77
2017-11-17 23:30 | 129.8 | 105.3
2017-11-18 | 122.15 | 96.26
2017-11-18 00:30 | 125.08 | 97.98
2017-11-18 01:00 | 120.87 | 96.23
2017-11-18 01:30 | 119.03 | 94.64
2017-11-18 02:00 | 122.39 | 98.46
2017-11-18 02:30 | 106.67 | 85.93
2017-11-18 03:00 | 98.38 | 78.65
2017-11-18 03:30 | 103.57 | 83.34
2017-11-18 04:00 | 94.86 | 74.21
2017-11-18 04:30 | 101.68 | 82.97
2017-11-18 05:00 | 110.5 | 92.21
2017-11-18 05:30 | 95.06 | 77.04
2017-11-18 06:00 | 96.31 | 75.54
2017-11-18 06:30 | 91.61 | 68.35
2017-11-18 07:00 | 98.93 | 77.14
2017-11-18 07:30 | 99.57 | 78.36
2017-11-18 08:00 | 95.07 | 72.83
2017-11-18 08:30 | 89.83 | 69.33
2017-11-18 09:00 | 100.25 | 80.77
2017-11-18 09:30 | 100.81 | 80.63
2017-11-18 10:00 | 107.27 | 86.73
2017-11-18 10:30 | 102.28 | 80.1
2017-11-18 11:00 | 96.87 | 74.96
2017-11-18 11:30 | 108.8 | 87.8
2017-11-18 12:00 | 106.51 | 85.86
2017-11-18 12:30 | 110.3 | 89.46
2017-11-18 13:00 | 107.37 | 86.36
2017-11-18 13:30 | 111.46 | 89.37
2017-11-18 14:00 | 101.47 | 77.81
2017-11-18 14:30 | 107.05 | 84.65
2017-11-18 15:00 | 106.95 | 85.24
2017-11-18 15:30 | 112.56 | 91.02
2017-11-18 16:00 | 113.59 | 92.13
2017-11-18 16:30 | 118.04 | 96.53
2017-11-18 17:00 | 112.99 | 91.63
2017-11-18 17:30 | 115.4 | 94.91
2017-11-18 18:00 | 110.71 | 90.57
2017-11-18 18:30 | 98.88 | 76.5
2017-11-18 19:00 | 110.65 | 90.21
2017-11-18 19:30 | 109.37 | 87.8
2017-11-18 20:00 | 104.69 | 84.1
2017-11-18 20:30 | 107.42 | 87.75
2017-11-18 21:00 | 102.68 | 81.95
2017-11-18 21:30 | 100.48 | 79.43
2017-11-18 22:00 | 101.32 | 81.81
2017-11-18 22:30 | 99.67 | 79.14
2017-11-18 23:00 | 101.92 | 82.19
2017-11-18 23:30 | 97.06 | 76.74
2017-11-19 | 100.67 | 78.62
2017-11-19 00:30 | 107.12 | 85.26
2017-11-19 01:00 | 108.65 | 87.23
2017-11-19 01:30 | 105.62 | 85.46
2017-11-19 02:00 | 104.81 | 83.66
2017-11-19 02:30 | 112.22 | 92.52
2017-11-19 03:00 | 106.67 | 86.62
2017-11-19 03:30 | 107.05 | 86.72
2017-11-19 04:00 | 104.12 | 83.29
2017-11-19 04:30 | 100.47 | 79.55
2017-11-19 05:00 | 100.11 | 78.78
2017-11-19 05:30 | 102.22 | 81.84
2017-11-19 06:00 | 108.22 | 88.64
2017-11-19 06:30 | 96.66 | 76.75
2017-11-19 07:00 | 107.36 | 88.42
2017-11-19 07:30 | 99.57 | 78.48
2017-11-19 08:00 | 99.27 | 77.38
2017-11-19 08:30 | 107.55 | 85.54
2017-11-19 09:00 | 107.05 | 86.42
2017-11-19 09:30 | 109.18 | 88.99
2017-11-19 10:00 | 114.93 | 93.44
2017-11-19 10:30 | 108.8 | 87.42
2017-11-19 11:00 | 108.45 | 86.87
2017-11-19 11:30 | 108.53 | 85.58
2017-11-19 12:00 | 112.27 | 88.22
2017-11-19 12:30 | 113.62 | 90.47
2017-11-19 13:00 | 107.8 | 85.4
2017-11-19 13:30 | 118.9 | 96.6
2017-11-19 14:00 | 112.3 | 89.65
2017-11-19 14:30 | 115.97 | 94.49
2017-11-19 15:00 | 121.2 | 99.24
2017-11-19 15:30 | 112.55 | 89.42
2017-11-19 16:00 | 106.24 | 82.7
2017-11-19 16:30 | 109.39 | 84.75
2017-11-19 17:00 | 112.86 | 87.22
2017-11-19 17:30 | 124.03 | 100.2
2017-11-19 18:00 | 120.23 | 94.41
2017-11-19 18:30 | 115.98 | 85.67
2017-11-19 19:00 | 123.16 | 94.91
2017-11-19 19:30 | 120.69 | 93.37
2017-11-19 20:00 | 129.05 | 102.67
2017-11-19 20:30 | 140.5 | 115.13
2017-11-19 21:00 | 132.94 | 107.67
2017-11-19 21:30 | 124.82 | 97.05
2017-11-19 22:00 | 130.23 | 102.19
2017-11-19 22:30 | 128.68 | 101.53
2017-11-19 23:00 | 130.72 | 102.09
2017-11-19 23:30 | 121.71 | 93.62
2017-11-20 | 126.66 | 97.76
2017-11-20 00:30 | 122.76 | 95.46
2017-11-20 01:00 | 131.66 | 104.14
2017-11-20 01:30 | 126.01 | 99.69
2017-11-20 02:00 | 127.39 | 100.72
2017-11-20 02:30 | 119.84 | 94.79
2017-11-20 03:00 | 121.38 | 96.69
2017-11-20 03:30 | 116.31 | 89.65
2017-11-20 04:00 | 123.27 | 96.65
2017-11-20 04:30 | 118.37 | 94.25
2017-11-20 05:00 | 118.36 | 94.23
2017-11-20 05:30 | 115.7 | 88.9
2017-11-20 06:00 | 120.36 | 94.52
2017-11-20 06:30 | 108.21 | 80.84
2017-11-20 07:00 | 116.48 | 89.68
2017-11-20 07:30 | 125.62 | 98.7
2017-11-20 08:00 | 120.31 | 91.29
2017-11-20 08:30 | 121.48 | 91.69
2017-11-20 09:00 | 122.19 | 92.48
2017-11-20 09:30 | 125.75 | 98.14
2017-11-20 10:00 | 122.56 | 94.25
2017-11-20 10:30 | 119.02 | 92.06
2017-11-20 11:00 | 120.27 | 92.69
2017-11-20 11:30 | 121.05 | 91.94
2017-11-20 12:00 | 114.09 | 86.72
2017-11-20 12:30 | 115.11 | 87.22
2017-11-20 13:00 | 113.53 | 87.84
2017-11-20 13:30 | 113 | 88.9
2017-11-20 14:00 | 117.11 | 92.66
2017-11-20 14:30 | 119.41 | 94.58
2017-11-20 15:00 | 118.67 | 94.51
2017-11-20 15:30 | 118.45 | 93.08
2017-11-20 16:00 | 125.2 | 95.27
2017-11-20 16:30 | 131.02 | 102.64
2017-11-20 17:00 | 128.32 | 101.01
2017-11-20 17:30 | 129.33 | 101.12
2017-11-20 18:00 | 129.72 | 101
2017-11-20 18:30 | 129.88 | 99.12
2017-11-20 19:00 | 130.67 | 101.63
2017-11-20 19:30 | 126.83 | 98.47
2017-11-20 20:00 | 134.52 | 106.17
2017-11-20 20:30 | 133.83 | 107.11
2017-11-20 21:00 | 125.64 | 97.24
2017-11-20 21:30 | 126.49 | 99.55
2017-11-20 22:00 | 125.18 | 99.99
2017-11-20 22:30 | 122.14 | 99.27
2017-11-20 23:00 | 119.16 | 96.08
2017-11-20 23:30 | 116.92 | 93.35
2017-11-21 | 115.18 | 92.64
2017-11-21 00:30 | 115.89 | 93.06
2017-11-21 01:00 | 109.85 | 84.78
2017-11-21 01:30 | 109.58 | 84.24
2017-11-21 02:00 | 108.43 | 84.84
2017-11-21 02:30 | 116.26 | 92.42
2017-11-21 03:00 | 110.89 | 86.07
2017-11-21 03:30 | 117.46 | 93.13
2017-11-21 04:00 | 121.4 | 97.07
2017-11-21 04:30 | 116.95 | 93.59
2017-11-21 05:00 | 112.43 | 89.12
2017-11-21 05:30 | 121.64 | 97.37
2017-11-21 06:00 | 122.15 | 98.51
2017-11-21 06:30 | 117.01 | 92.6
2017-11-21 07:00 | 117.04 | 93.16
2017-11-21 07:30 | 115.59 | 90.91
2017-11-21 08:00 | 115.24 | 90.55
2017-11-21 08:30 | 119.29 | 93.77
2017-11-21 09:00 | 118.43 | 93.37
2017-11-21 09:30 | 116.45 | 91
2017-11-21 10:00 | 119.38 | 94.21
2017-11-21 10:30 | 119.66 | 92.68
2017-11-21 11:00 | 117.67 | 89.65
2017-11-21 11:30 | 117.19 | 90.38
2017-11-21 12:00 | 118.89 | 91.78
2017-11-21 12:30 | 123.02 | 95.83
2017-11-21 13:00 | 118.5 | 91.7
2017-11-21 13:30 | 121.12 | 93.24
2017-11-21 14:00 | 116.75 | 87.36
2017-11-21 14:30 | 124.74 | 97.57
2017-11-21 15:00 | 118.04 | 90.65
2017-11-21 15:30 | 117.19 | 90.07
2017-11-21 16:00 | 126.08 | 100.79
2017-11-21 16:30 | 118.65 | 90.86
2017-11-21 17:00 | 117.26 | 89.63
2017-11-21 17:30 | 123.71 | 98.55
2017-11-21 18:00 | 125.3 | 99.59
2017-11-21 18:30 | 120.04 | 91.32
2017-11-21 19:00 | 129 | 102.21
2017-11-21 19:30 | 137.43 | 110.3
2017-11-21 20:00 | 135.85 | 108.38
2017-11-21 20:30 | 132.7 | 106.78
2017-11-21 21:00 | 132.53 | 106.91
2017-11-21 21:30 | 122.82 | 96.06
2017-11-21 22:00 | 120.23 | 94.27
2017-11-21 22:30 | 125.19 | 98.89
2017-11-21 23:00 | 123.93 | 97.37
2017-11-21 23:30 | 125.94 | 100.77
2017-11-22 | 125.2 | 100.05
2017-11-22 00:30 | 129.34 | 106.07
2017-11-22 01:00 | 124.22 | 101.09
2017-11-22 01:30 | 123.39 | 97.97
2017-11-22 02:00 | 131.64 | 107.36
2017-11-22 02:30 | 133.25 | 109.05
2017-11-22 03:00 | 127.87 | 103.58
2017-11-22 03:30 | 134.22 | 110.59
2017-11-22 04:00 | 133.1 | 108.54
2017-11-22 04:30 | 124.23 | 98.83
2017-11-22 05:00 | 124.72 | 98.6
2017-11-22 05:30 | 120.8 | 93.92
2017-11-22 06:00 | 124.86 | 99.2
2017-11-22 06:30 | 113.95 | 85.54
2017-11-22 07:00 | 118.64 | 90.72
2017-11-22 07:30 | 124.42 | 96.93
2017-11-22 08:00 | 118.07 | 88.95
2017-11-22 08:30 | 118.19 | 88.79
2017-11-22 09:00 | 118.43 | 88.42
2017-11-22 09:30 | 120.79 | 88.31
2017-11-22 10:00 | 120.15 | 88.38
2017-11-22 10:30 | 119.21 | 89.72
2017-11-22 11:00 | 129.26 | 101.65
2017-11-22 11:30 | 125.79 | 96.77
2017-11-22 12:00 | 116.24 | 88.56
2017-11-22 12:30 | 121.66 | 94.33
2017-11-22 13:00 | 118.9 | 92.76
2017-11-22 13:30 | 118.11 | 92.57
2017-11-22 14:00 | 125.02 | 100.26
2017-11-22 14:30 | 128.46 | 101.4
2017-11-22 15:00 | 125.82 | 98.83
2017-11-22 15:30 | 126.29 | 99.59
2017-11-22 16:00 | 129.14 | 102.7
2017-11-22 16:30 | 126.52 | 99.58
2017-11-22 17:00 | 124.85 | 99.07
2017-11-22 17:30 | 126.85 | 101.34
2017-11-22 18:00 | 126.73 | 102.73
2017-11-22 18:30 | 123.35 | 98.26
2017-11-22 19:00 | 126.73 | 101.54
2017-11-22 19:30 | 131.63 | 105.02
2017-11-22 20:00 | 132.06 | 105.32
2017-11-22 20:30 | 129.66 | 103.56
2017-11-22 21:00 | 127.25 | 101.94
2017-11-22 21:30 | 124.05 | 96.85
2017-11-22 22:00 | 123.29 | 96.81
2017-11-22 22:30 | 124.04 | 96.64
2017-11-22 23:00 | 128.22 | 103.84
2017-11-22 23:30 | 120.84 | 95.51
2017-11-23 | 130.28 | 105.47
2017-11-23 00:30 | 128.61 | 103.53
2017-11-23 01:00 | 115.46 | 93.57
2017-11-23 01:30 | 117.93 | 94.95
2017-11-23 02:00 | 127.65 | 103.05
2017-11-23 02:30 | 130.6 | 106.1
2017-11-23 03:00 | 126.8 | 100.37
2017-11-23 03:30 | 123.66 | 97.03
2017-11-23 04:00 | 124.52 | 97.26
2017-11-23 04:30 | 122.33 | 96.39
2017-11-23 05:00 | 124.38 | 97.87
2017-11-23 05:30 | 125.98 | 99.76
2017-11-23 06:00 | 123.94 | 98.3
2017-11-23 06:30 | 119.21 | 91.87
2017-11-23 07:00 | 118.42 | 93.61
2017-11-23 07:30 | 120.76 | 94.36
2017-11-23 08:00 | 115.52 | 88.43
2017-11-23 08:30 | 120.66 | 93.26
2017-11-23 09:00 | 119.81 | 92.48
2017-11-23 09:30 | 119.38 | 91.27
2017-11-23 10:00 | 117.94 | 90.52
2017-11-23 10:30 | 114.36 | 85.77
2017-11-23 11:00 | 120.55 | 92.89
2017-11-23 11:30 | 131.87 | 106.45
2017-11-23 12:00 | 123.01 | 96.16
2017-11-23 12:30 | 122.9 | 96.5
2017-11-23 13:00 | 119.98 | 92.98
2017-11-23 13:30 | 121.61 | 94.88
2017-11-23 14:00 | 121.21 | 94.76
2017-11-23 14:30 | 116.84 | 92.86
2017-11-23 15:00 | 118.16 | 93.21
2017-11-23 15:30 | 126.12 | 100.38
2017-11-23 16:00 | 122.58 | 94.75
2017-11-23 16:30 | 128.19 | 100.69
2017-11-23 17:00 | 135.35 | 106.59
2017-11-23 17:30 | 133.27 | 105.61
2017-11-23 18:00 | 137.98 | 109.19
2017-11-23 18:30 | 121.03 | 91.09
2017-11-23 19:00 | 127.95 | 100.3
2017-11-23 19:30 | 132.09 | 103.06
2017-11-23 20:00 | 133.84 | 104.85
2017-11-23 20:30 | 128.74 | 101.32
2017-11-23 21:00 | 132.69 | 105.78
2017-11-23 21:30 | 122.67 | 95.46
2017-11-23 22:00 | 127.9 | 101.15
2017-11-23 22:30 | 125.44 | 98.51
2017-11-23 23:00 | 127.16 | 101.14
2017-11-23 23:30 | 126.27 | 101.13
2017-11-24 | 123.23 | 100.65
2017-11-24 00:30 | 114.94 | 91.1
2017-11-24 01:00 | 120.98 | 98.71
2017-11-24 01:30 | 122.14 | 99.69
2017-11-24 02:00 | 127.41 | 104.25
2017-11-24 02:30 | 123.78 | 100.69
2017-11-24 03:00 | 128.44 | 105.04
2017-11-24 03:30 | 125.87 | 103.46
2017-11-24 04:00 | 130.97 | 109.17
2017-11-24 04:30 | 128.95 | 106.47
2017-11-24 05:00 | 132.35 | 108.22
2017-11-24 05:30 | 125.1 | 98.65
2017-11-24 06:00 | 127.59 | 101.49
2017-11-24 06:30 | 124.48 | 95.47
2017-11-24 07:00 | 127.94 | 101.55
2017-11-24 07:30 | 129.81 | 103.33
2017-11-24 08:00 | 124.47 | 95.62
2017-11-24 08:30 | 127.11 | 99
2017-11-24 09:00 | 127.18 | 97.97
2017-11-24 09:30 | 135.39 | 105.49
2017-11-24 10:00 | 132.28 | 103.27
2017-11-24 10:30 | 133 | 104.72
2017-11-24 11:00 | 131.9 | 103.98
2017-11-24 11:30 | 127.52 | 100.11
2017-11-24 12:00 | 122.32 | 95.7
2017-11-24 12:30 | 119.83 | 93.77
2017-11-24 13:00 | 128.01 | 102.61
2017-11-24 13:30 | 126.87 | 100.17
2017-11-24 14:00 | 135.08 | 109.14
2017-11-24 14:30 | 129.21 | 103.05
2017-11-24 15:00 | 128.77 | 100.89
2017-11-24 15:30 | 127.21 | 100.92
2017-11-24 16:00 | 133.33 | 106.82
2017-11-24 16:30 | 122.87 | 94.44
2017-11-24 17:00 | 126.12 | 98.08
2017-11-24 17:30 | 131.92 | 105.97
2017-11-24 18:00 | 132.96 | 107.49
2017-11-24 18:30 | 125.97 | 99.8
2017-11-24 19:00 | 125.77 | 99.46
2017-11-24 19:30 | 131.34 | 104.49
2017-11-24 20:00 | 135.74 | 109.98
2017-11-24 20:30 | 133.54 | 108
2017-11-24 21:00 | 131.15 | 105.12
2017-11-24 21:30 | 129.81 | 103.99
2017-11-24 22:00 | 123.15 | 97.73
2017-11-24 22:30 | 129.62 | 105.5
2017-11-24 23:00 | 127.94 | 104.32
2017-11-24 23:30 | 123.18 | 99.53
2017-11-25 | 119.39 | 94.77
2017-11-25 00:30 | 123.16 | 99.11
2017-11-25 01:00 | 120.82 | 97.4
2017-11-25 01:30 | 116.43 | 93.02
2017-11-25 02:00 | 115.36 | 92.5
2017-11-25 02:30 | 114.36 | 91.32
2017-11-25 03:00 | 118.14 | 94.98
2017-11-25 03:30 | 116.89 | 94.06
2017-11-25 04:00 | 119.98 | 97.58
2017-11-25 04:30 | 124.15 | 100.76
2017-11-25 05:00 | 124.22 | 98.67
2017-11-25 05:30 | 117.83 | 93.55
2017-11-25 06:00 | 119.76 | 96.22
2017-11-25 06:30 | 111.86 | 85.73
2017-11-25 07:00 | 118.59 | 93.18
2017-11-25 07:30 | 121.43 | 95.23
2017-11-25 08:00 | 126.59 | 101
2017-11-25 08:30 | 119.98 | 94.23
2017-11-25 09:00 | 119.24 | 92.31
2017-11-25 09:30 | 125.42 | 98.52
2017-11-25 10:00 | 122.11 | 96.62
2017-11-25 10:30 | 125.72 | 100.84
2017-11-25 11:00 | 124.43 | 99.32
2017-11-25 11:30 | 123.9 | 97.04
2017-11-25 12:00 | 124.51 | 98.28
2017-11-25 12:30 | 128.42 | 103.71
2017-11-25 13:00 | 124.23 | 99.18
2017-11-25 13:30 | 124.27 | 99.93
2017-11-25 14:00 | 124.74 | 100.68
2017-11-25 14:30 | 128.35 | 103.75
2017-11-25 15:00 | 127.72 | 102.97
2017-11-25 15:30 | 128.02 | 103.6
2017-11-25 16:00 | 137.05 | 113.75
2017-11-25 16:30 | 128.19 | 104.74
2017-11-25 17:00 | 123.79 | 99.96
2017-11-25 17:30 | 125.95 | 101.74
2017-11-25 18:00 | 125.9 | 99.02
2017-11-25 18:30 | 121.05 | 91.99
2017-11-25 19:00 | 125.07 | 97.73
2017-11-25 19:30 | 129.91 | 103.22
2017-11-25 20:00 | 132.83 | 106.22
2017-11-25 20:30 | 124.66 | 97.24
2017-11-25 21:00 | 123.66 | 97.44
2017-11-25 21:30 | 123.61 | 98.08
2017-11-25 22:00 | 120.19 | 95.16
2017-11-25 22:30 | 120.5 | 95.65
2017-11-25 23:00 | 117.8 | 92.19
2017-11-25 23:30 | 119.39 | 94.09
2017-11-26 | 113.15 | 87.82
2017-11-26 00:30 | 116.52 | 91.77
2017-11-26 01:00 | 119.76 | 95.73
2017-11-26 01:30 | 117.69 | 93.64
2017-11-26 02:00 | 119.22 | 97.45
2017-11-26 02:30 | 116.76 | 93.13
2017-11-26 03:00 | 116.68 | 92.28
2017-11-26 03:30 | 115.51 | 91.83
2017-11-26 04:00 | 110.77 | 86.44
2017-11-26 04:30 | 115.75 | 92.08
2017-11-26 05:00 | 115.41 | 91.97
2017-11-26 05:30 | 112.52 | 88.26
2017-11-26 06:00 | 115.07 | 91.37
2017-11-26 06:30 | 107.77 | 82.33
2017-11-26 07:00 | 108.96 | 84.48
2017-11-26 07:30 | 114.03 | 88.8
2017-11-26 08:00 | 113.66 | 89.41
2017-11-26 08:30 | 116.73 | 88.83
2017-11-26 09:00 | 120.56 | 93.3
2017-11-26 09:30 | 117.42 | 90.33
2017-11-26 10:00 | 117.7 | 90.25
2017-11-26 10:30 | 124.67 | 97.19
2017-11-26 11:00 | 126.75 | 100.03
2017-11-26 11:30 | 125.32 | 96.93
2017-11-26 12:00 | 133.39 | 107.53
2017-11-26 12:30 | 131.71 | 108.23
2017-11-26 13:00 | 130.17 | 105.61
2017-11-26 13:30 | 127.38 | 100.96
2017-11-26 14:00 | 128.77 | 103.66
2017-11-26 14:30 | 129.09 | 102.01
2017-11-26 15:00 | 127.77 | 99.74
2017-11-26 15:30 | 124.4 | 96.71
2017-11-26 16:00 | 130.39 | 104.77
2017-11-26 16:30 | 128.37 | 101.47
2017-11-26 17:00 | 129.17 | 103.14
2017-11-26 17:30 | 114.93 | 90.7
2017-11-26 18:00 | 113.88 | 91.51
2017-11-26 18:30 | 105.16 | 81.61
2017-11-26 19:00 | 106.97 | 83.92
2017-11-26 19:30 | 112.55 | 87.85
2017-11-26 20:00 | 116.68 | 93.54
2017-11-26 20:30 | 109.52 | 85.91
2017-11-26 21:00 | 109.81 | 86.55
2017-11-26 21:30 | 111.21 | 89.1
2017-11-26 22:00 | 106.54 | 81.68
2017-11-26 22:30 | 107.81 | 82.45
2017-11-26 23:00 | 106.28 | 82.31
2017-11-26 23:30 | 102.22 | 79.09
2017-11-27 | 102.19 | 79.71
2017-11-27 00:30 | 110.61 | 87.69
2017-11-27 01:00 | 118.22 | 96.77
2017-11-27 01:30 | 112.84 | 91.77
2017-11-27 02:00 | 113.63 | 93.04
2017-11-27 02:30 | 110.4 | 88.53
2017-11-27 03:00 | 117.66 | 94.18
2017-11-27 03:30 | 109.7 | 86.06
2017-11-27 04:00 | 109.67 | 85.97
2017-11-27 04:30 | 110.83 | 87.3
2017-11-27 05:00 | 111.34 | 87.62
2017-11-27 05:30 | 110.67 | 87.17
2017-11-27 06:00 | 105.58 | 79.76
2017-11-27 06:30 | 102.68 | 74.92
2017-11-27 07:00 | 101.34 | 73.6
2017-11-27 07:30 | 96.21 | 70.53
2017-11-27 08:00 | 101.75 | 78.95
2017-11-27 08:30 | 105.19 | 82.18
2017-11-27 09:00 | 111.89 | 87.61
2017-11-27 09:30 | 107.17 | 81.16
2017-11-27 10:00 | 114.79 | 86.93
2017-11-27 10:30 | 114.8 | 86.81
2017-11-27 11:00 | 118.39 | 90.27
2017-11-27 11:30 | 117.17 | 88.82
2017-11-27 12:00 | 116.79 | 89.1
2017-11-27 12:30 | 117.15 | 88.8
2017-11-27 13:00 | 118.22 | 91.38
2017-11-27 13:30 | 120.5 | 93.65
2017-11-27 14:00 | 119.5 | 92.99
2017-11-27 14:30 | 120.35 | 94.18
2017-11-27 15:00 | 118.39 | 92.98
2017-11-27 15:30 | 111.95 | 88.44
2017-11-27 16:00 | 112.15 | 88.97
2017-11-27 16:30 | 112.83 | 89.07
2017-11-27 17:00 | 114.32 | 92.12
2017-11-27 17:30 | 113.47 | 90.52
2017-11-27 18:00 | 116.15 | 93.69
2017-11-27 18:30 | 109.96 | 85.69
2017-11-27 19:00 | 112.93 | 90.64
2017-11-27 19:30 | 118.73 | 97.41
2017-11-27 20:00 | 115.41 | 94.1
2017-11-27 20:30 | 117.61 | 96.42
2017-11-27 21:00 | 118.08 | 96.55
2017-11-27 21:30 | 116.57 | 95.35
2017-11-27 22:00 | 115.12 | 94.21
2017-11-27 22:30 | 112.69 | 90.78
2017-11-27 23:00 | 111.21 | 88.29
2017-11-27 23:30 | 106.52 | 83.59
2017-11-28 | 107.53 | 84.7
2017-11-28 00:30 | 106.39 | 83.09
2017-11-28 01:00 | 109.39 | 87.2
2017-11-28 01:30 | 114.69 | 93.39
2017-11-28 02:00 | 112.42 | 90.56
2017-11-28 02:30 | 111.85 | 89.69
2017-11-28 03:00 | 108.72 | 86.99
2017-11-28 03:30 | 108.12 | 85.33
2017-11-28 04:00 | 109.23 | 86.71
2017-11-28 04:30 | 111.54 | 89.46
2017-11-28 05:00 | 107.22 | 83.71
2017-11-28 05:30 | 106.09 | 82.99
2017-11-28 06:00 | 108.79 | 86.33
2017-11-28 06:30 | 104.95 | 81.47
2017-11-28 07:00 | 110.66 | 89.28
2017-11-28 07:30 | 110.74 | 88.26
2017-11-28 08:00 | 106 | 82.8
2017-11-28 08:30 | 111.52 | 90.02
2017-11-28 09:00 | 106.15 | 82.78
2017-11-28 09:30 | 108.05 | 86.14
2017-11-28 10:00 | 111.07 | 89.46
2017-11-28 10:30 | 106.67 | 86.1
2017-11-28 11:00 | 103.02 | 83.56
2017-11-28 11:30 | 108.48 | 88.16
2017-11-28 12:00 | 106.14 | 84.05
2017-11-28 12:30 | 108.97 | 87.77
2017-11-28 13:00 | 118.98 | 97.11
2017-11-28 13:30 | 125.37 | 101.47
2017-11-28 14:00 | 125.67 | 101.44
2017-11-28 14:30 | 134.48 | 110.05
2017-11-28 15:00 | 127.01 | 99.93
2017-11-28 15:30 | 127.83 | 100.73
2017-11-28 16:00 | 126.02 | 98.71
2017-11-28 16:30 | 122.6 | 95.96
2017-11-28 17:00 | 127.32 | 101.57
2017-11-28 17:30 | 134.08 | 109.02
2017-11-28 18:00 | 130.14 | 103.41
2017-11-28 18:30 | 129.31 | 101.6
2017-11-28 19:00 | 131.68 | 104.95
2017-11-28 19:30 | 130.98 | 105.28
2017-11-28 20:00 | 130.66 | 104.35
2017-11-28 20:30 | 127.45 | 101.27
2017-11-28 21:00 | 129.8 | 103.81
2017-11-28 21:30 | 127.16 | 101.92
2017-11-28 22:00 | 116.15 | 95.38
2017-11-28 22:30 | 122.47 | 99.57
2017-11-28 23:00 | 125.52 | 100.54
2017-11-28 23:30 | 120.27 | 95.02
2017-11-29 | 117.41 | 92.78
2017-11-29 00:30 | 120.92 | 96.01
2017-11-29 01:00 | 125.57 | 100.08
2017-11-29 01:30 | 129.55 | 103.3
2017-11-29 02:00 | 124.91 | 100.16
2017-11-29 02:30 | 118.24 | 93.18
2017-11-29 03:00 | 116.01 | 91.25
2017-11-29 03:30 | 114.47 | 89.7
2017-11-29 04:00 | 122.45 | 97.9
2017-11-29 04:30 | 120.02 | 95.2
2017-11-29 05:00 | 122.08 | 95.7
2017-11-29 05:30 | 121.02 | 95.17
2017-11-29 06:00 | 121.43 | 94.96
2017-11-29 06:30 | 116.61 | 89.25
2017-11-29 07:00 | 119.5 | 93.57
2017-11-29 07:30 | 123.4 | 97.4
2017-11-29 08:00 | 129.02 | 103.87
2017-11-29 08:30 | 119.13 | 92.47
2017-11-29 09:00 | 124.77 | 97.79
2017-11-29 09:30 | 125.28 | 99.43
2017-11-29 10:00 | 122.38 | 96.35
2017-11-29 10:30 | 117.09 | 90.48
2017-11-29 11:00 | 117.65 | 91.91
2017-11-29 11:30 | 117.43 | 90.92
2017-11-29 12:00 | 122.87 | 97.92
2017-11-29 12:30 | 119.06 | 94.84
2017-11-29 13:00 | 116.84 | 91.95
2017-11-29 13:30 | 126.65 | 101.48
2017-11-29 14:00 | 120.04 | 96.09
2017-11-29 14:30 | 121.96 | 98.29
2017-11-29 15:00 | 127.8 | 103.26
2017-11-29 15:30 | 119.38 | 95.61
2017-11-29 16:00 | 122.71 | 96.8
2017-11-29 16:30 | 116.71 | 92.92
2017-11-29 17:00 | 120.91 | 97.38
2017-11-29 17:30 | 119.69 | 95.74
2017-11-29 18:00 | 125.16 | 100.86
2017-11-29 18:30 | 127.02 | 102.93
2017-11-29 19:00 | 130.27 | 105.83
2017-11-29 19:30 | 129.58 | 104.91
2017-11-29 20:00 | 130.37 | 105.62
2017-11-29 20:30 | 128.11 | 104.83
2017-11-29 21:00 | 117.5 | 95.71
2017-11-29 21:30 | 116.19 | 93.27
2017-11-29 22:00 | 110.26 | 90.61
2017-11-29 22:30 | 111.85 | 93.03
2017-11-29 23:00 | 114.5 | 95.13
2017-11-29 23:30 | 110.43 | 89.3
2017-11-30 | 113.2 | 92.42
2017-11-30 00:30 | 118.53 | 97.15
2017-11-30 01:00 | 117.67 | 95.37
2017-11-30 01:30 | 113.01 | 92.37
2017-11-30 02:00 | 116.95 | 94.61
2017-11-30 02:30 | 117.39 | 94.85
2017-11-30 03:00 | 115.06 | 93.7
2017-11-30 03:30 | 113.72 | 92.32
2017-11-30 04:00 | 117.71 | 96.81
2017-11-30 04:30 | 113.27 | 90.95
2017-11-30 05:00 | 115.37 | 93.39
2017-11-30 05:30 | 114.46 | 92.62
2017-11-30 06:00 | 108 | 86.52
2017-11-30 06:30 | 107.24 | 87.98
2017-11-30 07:00 | 118.14 | 100.54
2017-11-30 07:30 | 122.24 | 103.11
2017-11-30 08:00 | 119.52 | 99.75
2017-11-30 08:30 | 112.61 | 91.75
2017-11-30 09:00 | 109.45 | 87.12
2017-11-30 09:30 | 108.38 | 86.21
2017-11-30 10:00 | 109.28 | 86.93
2017-11-30 10:30 | 108.67 | 84.9
2017-11-30 11:00 | 109.31 | 85.24
2017-11-30 11:30 | 118.36 | 92.82
2017-11-30 12:00 | 125.29 | 99.58
2017-11-30 12:30 | 136.68 | 111.97
2017-11-30 13:00 | 127.09 | 102.55
2017-11-30 13:30 | 124.97 | 99.35
2017-11-30 14:00 | 130.69 | 105.24
2017-11-30 14:30 | 132.51 | 107.92
2017-11-30 15:00 | 125.21 | 98.58
2017-11-30 15:30 | 130.33 | 102.23
2017-11-30 16:00 | 129.86 | 100.95
2017-11-30 16:30 | 127.3 | 100.31
2017-11-30 17:00 | 132.07 | 107.19
2017-11-30 17:30 | 123.32 | 96.74
2017-11-30 18:00 | 135.06 | 109.67
2017-11-30 18:30 | 127.43 | 100.11
2017-11-30 19:00 | 135.74 | 107.29
2017-11-30 19:30 | 132.68 | 103.3
2017-11-30 20:00 | 118.15 | 88.85
2017-11-30 20:30 | 126.13 | 96.01
2017-11-30 21:00 | 124.86 | 96.54
2017-11-30 21:30 | 123.98 | 96.11
2017-11-30 22:00 | 122.93 | 95.58
2017-11-30 22:30 | 125.83 | 100.14
2017-11-30 23:00 | 125.47 | 98.1
2017-11-30 23:30 | 121.16 | 94.18
2017-12-01 | 125.21 | 99.98
2017-12-01 00:30 | 126.42 | 102.75
2017-12-01 01:00 | 120.42 | 97.39
2017-12-01 01:30 | 124.63 | 101.22
2017-12-01 02:00 | 123.79 | 99.17
2017-12-01 02:30 | 129.2 | 104.33
2017-12-01 03:00 | 121.53 | 95.25
2017-12-01 03:30 | 126.59 | 100.2
2017-12-01 04:00 | 124.04 | 98.16
2017-12-01 04:30 | 123.34 | 97.32
2017-12-01 05:00 | 120.49 | 93.22
2017-12-01 05:30 | 119.31 | 92.31
2017-12-01 06:00 | 120.51 | 93.78
2017-12-01 06:30 | 114.14 | 86.26
2017-12-01 07:00 | 127.98 | 101.89
2017-12-01 07:30 | 132.5 | 105.73
2017-12-01 08:00 | 125.71 | 98.38
2017-12-01 08:30 | 119.55 | 90.79
2017-12-01 09:00 | 124.63 | 96.31
2017-12-01 09:30 | 120.77 | 90.83
2017-12-01 10:00 | 118.1 | 86.8
2017-12-01 10:30 | 119.42 | 87.78
2017-12-01 11:00 | 120.92 | 89.49
2017-12-01 11:30 | 118.05 | 89.5
2017-12-01 12:00 | 120.74 | 92.01
2017-12-01 12:30 | 124.86 | 95.04
2017-12-01 13:00 | 119.73 | 90.74
2017-12-01 13:30 | 121.02 | 92.18
2017-12-01 14:00 | 124.89 | 96.2
2017-12-01 14:30 | 127.52 | 99.64
2017-12-01 15:00 | 129.23 | 100.32
2017-12-01 15:30 | 128.91 | 100.08
2017-12-01 16:00 | 131.16 | 103.32
2017-12-01 16:30 | 128.61 | 99.44
2017-12-01 17:00 | 130.31 | 100.55
2017-12-01 17:30 | 132.44 | 102.64
2017-12-01 18:00 | 131.97 | 102.29
2017-12-01 18:30 | 126.1 | 97.7
2017-12-01 19:00 | 130.03 | 102.17
2017-12-01 19:30 | 134.38 | 105.72
2017-12-01 20:00 | 135.08 | 105
2017-12-01 20:30 | 129.81 | 100.54
2017-12-01 21:00 | 128.29 | 98.08
2017-12-01 21:30 | 133.92 | 105.79
2017-12-01 22:00 | 136.16 | 108.75
2017-12-01 22:30 | 120.98 | 93.17
2017-12-01 23:00 | 126.57 | 98.34
2017-12-01 23:30 | 128.62 | 102.72
2017-12-02 | 123.19 | 95.32
2017-12-02 00:30 | 124.79 | 96.85
2017-12-02 01:00 | 119.74 | 90.49
2017-12-02 01:30 | 123.28 | 93.91
2017-12-02 02:00 | 126.38 | 97.25
2017-12-02 02:30 | 126.28 | 98.41
2017-12-02 03:00 | 122.94 | 95.63
2017-12-02 03:30 | 123.94 | 96.66
2017-12-02 04:00 | 121 | 94.46
2017-12-02 04:30 | 122.45 | 95
2017-12-02 05:00 | 125.2 | 98.47
2017-12-02 05:30 | 122.77 | 96.15
2017-12-02 06:00 | 119 | 92.49
2017-12-02 06:30 | 111.39 | 83.62
2017-12-02 07:00 | 110.5 | 83.01
2017-12-02 07:30 | 116.29 | 90.66
2017-12-02 08:00 | 106.89 | 83.13
2017-12-02 08:30 | 100.06 | 76.78
2017-12-02 09:00 | 101.32 | 76
2017-12-02 09:30 | 99.35 | 74.31
2017-12-02 10:00 | 103.2 | 78.06
2017-12-02 10:30 | 108.46 | 83.89
2017-12-02 11:00 | 117.49 | 90.11
2017-12-02 11:30 | 120.92 | 93.52
2017-12-02 12:00 | 123.77 | 95.58
2017-12-02 12:30 | 122.44 | 93.42
2017-12-02 13:00 | 125.13 | 95.62
2017-12-02 13:30 | 128.5 | 102.02
2017-12-02 14:00 | 128.77 | 101.01
2017-12-02 14:30 | 128.02 | 97.21
2017-12-02 15:00 | 122.75 | 90.43
2017-12-02 15:30 | 125.56 | 94.69
2017-12-02 16:00 | 128.48 | 100.06
2017-12-02 16:30 | 128.03 | 97.37
2017-12-02 17:00 | 130.56 | 99.9
2017-12-02 17:30 | 127.66 | 95.21
2017-12-02 18:00 | 127.17 | 95.03
2017-12-02 18:30 | 127.71 | 96.53
2017-12-02 19:00 | 129.04 | 98.2
2017-12-02 19:30 | 135.53 | 104.83
2017-12-02 20:00 | 133.73 | 103.16
2017-12-02 20:30 | 131.08 | 102.6
2017-12-02 21:00 | 128.52 | 101.69
2017-12-02 21:30 | 134.61 | 108.27
2017-12-02 22:00 | 122.79 | 93.94
2017-12-02 22:30 | 126.91 | 100.14
2017-12-02 23:00 | 122.99 | 95.76
2017-12-02 23:30 | 122.5 | 95.39
2017-12-03 | 116.63 | 90.22
2017-12-03 00:30 | 118.35 | 93.13
2017-12-03 01:00 | 110.81 | 85.31
2017-12-03 01:30 | 107.62 | 82.23
2017-12-03 02:00 | 108.41 | 84.24
2017-12-03 02:30 | 108.13 | 84.11
2017-12-03 03:00 | 113.23 | 88.21
2017-12-03 03:30 | 111.59 | 86.37
2017-12-03 04:00 | 112.95 | 85.42
2017-12-03 04:30 | 109.25 | 81.15
2017-12-03 05:00 | 120.12 | 92.29
2017-12-03 05:30 | 117.31 | 91.24
2017-12-03 06:00 | 110.08 | 85.76
2017-12-03 06:30 | 109 | 81.85
2017-12-03 07:00 | 110.49 | 82.66
2017-12-03 07:30 | 100.73 | 73.59
2017-12-03 08:00 | 109.13 | 82.54
2017-12-03 08:30 | 102.77 | 75.19
2017-12-03 09:00 | 100.52 | 72.95
2017-12-03 09:30 | 102.34 | 74.74
2017-12-03 10:00 | 103.43 | 77.12
2017-12-03 10:30 | 99.3 | 72.85
2017-12-03 11:00 | 100.6 | 73.31
2017-12-03 11:30 | 102.53 | 74.22
2017-12-03 12:00 | 101.14 | 73.24
2017-12-03 12:30 | 104.68 | 74.7
2017-12-03 13:00 | 111.95 | 82.71
2017-12-03 13:30 | 120.35 | 91.32
2017-12-03 14:00 | 113.96 | 84.66
2017-12-03 14:30 | 111.84 | 81.5
2017-12-03 15:00 | 111.04 | 81.48
2017-12-03 15:30 | 108.21 | 79.77
2017-12-03 16:00 | 113.88 | 86.39
2017-12-03 16:30 | 109.79 | 82.84
2017-12-03 17:00 | 110.95 | 83.48
2017-12-03 17:30 | 121.62 | 94.58
2017-12-03 18:00 | 121.14 | 93.16
2017-12-03 18:30 | 120.4 | 90.04
2017-12-03 19:00 | 120.99 | 90.82
2017-12-03 19:30 | 123.08 | 94.08
2017-12-03 20:00 | 114.93 | 85.89
2017-12-03 20:30 | 121.39 | 90.41
2017-12-03 21:00 | 115.69 | 84.45
2017-12-03 21:30 | 116.35 | 87.6
2017-12-03 22:00 | 124.03 | 97.05
2017-12-03 22:30 | 116.97 | 89.03
2017-12-03 23:00 | 121.07 | 93.23
2017-12-03 23:30 | 115.93 | 87.43
2017-12-04 | 121.01 | 91.54
2017-12-04 00:30 | 121.77 | 93.69
2017-12-04 01:00 | 122.27 | 96.84
2017-12-04 01:30 | 111.82 | 85.88
2017-12-04 02:00 | 110.69 | 85.56
2017-12-04 02:30 | 115.13 | 90.43
2017-12-04 03:00 | 105.33 | 78.86
2017-12-04 03:30 | 100.14 | 72.16
2017-12-04 04:00 | 100.38 | 71.84
2017-12-04 04:30 | 104.68 | 77.86
2017-12-04 05:00 | 112.77 | 85.75
2017-12-04 05:30 | 102.66 | 74.28
2017-12-04 06:00 | 99.93 | 71.18
2017-12-04 06:30 | 101.42 | 72.48
2017-12-04 07:00 | 98.04 | 68.99
2017-12-04 07:30 | 101.98 | 74.46
2017-12-04 08:00 | 104.53 | 75.95
2017-12-04 08:30 | 106.59 | 76.52
2017-12-04 09:00 | 112.3 | 82.24
2017-12-04 09:30 | 116.22 | 85.9
2017-12-04 10:00 | 105.09 | 75.05
2017-12-04 10:30 | 106.24 | 75.93
2017-12-04 11:00 | 107.49 | 76.15
2017-12-04 11:30 | 106.79 | 76.67
2017-12-04 12:00 | 106.71 | 77.22
2017-12-04 12:30 | 103.57 | 73.83
2017-12-04 13:00 | 105.17 | 77.01
2017-12-04 13:30 | 107.99 | 78.68
2017-12-04 14:00 | 110.88 | 81.72
2017-12-04 14:30 | 108.56 | 79.51
2017-12-04 15:00 | 108.63 | 80.02
2017-12-04 15:30 | 110.97 | 84.64
2017-12-04 16:00 | 115.58 | 91.19
2017-12-04 16:30 | 115.79 | 90.64
2017-12-04 17:00 | 118.44 | 94.39
2017-12-04 17:30 | 119.59 | 95.27
2017-12-04 18:00 | 122.02 | 97.79
2017-12-04 18:30 | 118.71 | 92.14
2017-12-04 19:00 | 122.15 | 96.32
2017-12-04 19:30 | 122.78 | 96.67
2017-12-04 20:00 | 115.83 | 89.15
2017-12-04 20:30 | 115.1 | 88.99
2017-12-04 21:00 | 117.98 | 92.59
2017-12-04 21:30 | 115.61 | 89.38
2017-12-04 22:00 | 115.72 | 89.83
2017-12-04 22:30 | 112.33 | 86.41
2017-12-04 23:00 | 114.68 | 90.31
2017-12-04 23:30 | 116.41 | 93.68
2017-12-05 | 108.15 | 86.03
2017-12-05 00:30 | 111.44 | 88.54
2017-12-05 01:00 | 104.61 | 80.49
2017-12-05 01:30 | 104.65 | 81.12
2017-12-05 02:00 | 106.5 | 80.68
2017-12-05 02:30 | 110.59 | 85.26
2017-12-05 03:00 | 105.02 | 79.23
2017-12-05 03:30 | 109.13 | 82.67
2017-12-05 04:00 | 108.08 | 81.28
2017-12-05 04:30 | 115.66 | 91.01
2017-12-05 05:00 | 121.01 | 96.79
2017-12-05 05:30 | 115.28 | 90.73
2017-12-05 06:00 | 107.59 | 80.92
2017-12-05 06:30 | 103.31 | 76.08
2017-12-05 07:00 | 102.88 | 76.49
2017-12-05 07:30 | 105.03 | 77.17
2017-12-05 08:00 | 102.66 | 73.6
2017-12-05 08:30 | 110.38 | 82.88
2017-12-05 09:00 | 111.56 | 85.22
2017-12-05 09:30 | 116.38 | 87.88
2017-12-05 10:00 | 116.92 | 88.17
2017-12-05 10:30 | 117.99 | 88.54
2017-12-05 11:00 | 114.32 | 84.69
2017-12-05 11:30 | 111.59 | 80.82
2017-12-05 12:00 | 118.76 | 87.85
2017-12-05 12:30 | 118.78 | 87.38
2017-12-05 13:00 | 117.29 | 86.55
2017-12-05 13:30 | 115.72 | 86.46
2017-12-05 14:00 | 124.97 | 94.96
2017-12-05 14:30 | 125.57 | 95.37
2017-12-05 15:00 | 124.26 | 92.88
2017-12-05 15:30 | 125.2 | 93.14
2017-12-05 16:00 | 128.57 | 97.49
2017-12-05 16:30 | 129.21 | 96.56
2017-12-05 17:00 | 130.64 | 100.89
2017-12-05 17:30 | 130.48 | 100.75
2017-12-05 18:00 | 122.4 | 94.56
2017-12-05 18:30 | 121.75 | 93.25
2017-12-05 19:00 | 123.46 | 94.84
2017-12-05 19:30 | 132.43 | 105.49
2017-12-05 20:00 | 134.18 | 108.1
2017-12-05 20:30 | 134.58 | 106.15
2017-12-05 21:00 | 126.52 | 98.34
2017-12-05 21:30 | 117.31 | 90.95
2017-12-05 22:00 | 117.28 | 91.7
2017-12-05 22:30 | 115.99 | 89.98
2017-12-05 23:00 | 111.67 | 85.41
2017-12-05 23:30 | 111.77 | 84.48
2017-12-06 | 118.24 | 90.91
2017-12-06 00:30 | 119.77 | 94.89
2017-12-06 01:00 | 122.14 | 96.21
2017-12-06 01:30 | 123.35 | 96.52
2017-12-06 02:00 | 123.28 | 96.18
2017-12-06 02:30 | 119.83 | 92.64
2017-12-06 03:00 | 122.56 | 97.06
2017-12-06 03:30 | 113.12 | 86.5
2017-12-06 04:00 | 111.33 | 85.01
2017-12-06 04:30 | 113.67 | 87.24
2017-12-06 05:00 | 110.68 | 84.25
2017-12-06 05:30 | 111.35 | 84.78
2017-12-06 06:00 | 109.7 | 81.37
2017-12-06 06:30 | 105.08 | 77.61
2017-12-06 07:00 | 100.06 | 75.59
2017-12-06 07:30 | 102.09 | 81.41
2017-12-06 08:00 | 94.13 | 78.87
2017-12-06 08:30 | 98.08 | 80.95
2017-12-06 09:00 | 97.9 | 80.24
2017-12-06 09:30 | 99.83 | 82.7
2017-12-06 10:00 | 99.59 | 82.13
2017-12-06 10:30 | 101.38 | 84.01
2017-12-06 11:00 | 99.87 | 82.94
2017-12-06 11:30 | 94.38 | 75.76
2017-12-06 12:00 | 98.88 | 79.98
2017-12-06 12:30 | 100.82 | 82.34
2017-12-06 13:00 | 91.34 | 76.97
2017-12-06 13:30 | 91.5 | 76.88
2017-12-06 14:00 | 100.5 | 84.82
2017-12-06 14:30 | 97.05 | 82.25
2017-12-06 15:00 | 98.98 | 82.73
2017-12-06 15:30 | 103.49 | 83.36
2017-12-06 16:00 | 109.69 | 90.4
2017-12-06 16:30 | 108.94 | 90.29
2017-12-06 17:00 | 114.32 | 94.91
2017-12-06 17:30 | 113.95 | 93.76
2017-12-06 18:00 | 110.61 | 90.55
2017-12-06 18:30 | 107.15 | 88.32
2017-12-06 19:00 | 105.28 | 87.3
2017-12-06 19:30 | 106.33 | 86.76
2017-12-06 20:00 | 113.59 | 94.59
2017-12-06 20:30 | 116.67 | 98.55
2017-12-06 21:00 | 116.69 | 98.9
2017-12-06 21:30 | 110.95 | 92.59
2017-12-06 22:00 | 108.49 | 89.83
2017-12-06 22:30 | 113.84 | 94.32
2017-12-06 23:00 | 114.28 | 95.62
2017-12-06 23:30 | 106.79 | 87.21
2017-12-07 | 110.4 | 91.92
2017-12-07 00:30 | 112.17 | 95.88
2017-12-07 01:00 | 124.68 | 98.98
2017-12-07 01:30 | 120.31 | 93.8
2017-12-07 02:00 | 121.13 | 94.69
2017-12-07 02:30 | 123 | 96.95
2017-12-07 03:00 | 126.14 | 101.02
2017-12-07 03:30 | 117.22 | 91.82
2017-12-07 04:00 | 117.62 | 91.62
2017-12-07 04:30 | 113.91 | 87.7
2017-12-07 05:00 | 116.29 | 89.69
2017-12-07 05:30 | 116.98 | 90.29
2017-12-07 06:00 | 113.46 | 86.25
2017-12-07 06:30 | 108.66 | 81.65
2017-12-07 07:00 | 109.8 | 86.12
2017-12-07 07:30 | 110.91 | 87.85
2017-12-07 08:00 | 107.87 | 84.27
2017-12-07 08:30 | 112.4 | 88.34
2017-12-07 09:00 | 116.62 | 92.53
2017-12-07 09:30 | 112.77 | 89.63
2017-12-07 10:00 | 114.1 | 92.01
2017-12-07 10:30 | 118 | 95.22
2017-12-07 11:00 | 112.37 | 88.03
2017-12-07 11:30 | 109.45 | 83.26
2017-12-07 12:00 | 108.52 | 81.47
2017-12-07 12:30 | 108.22 | 82.19
2017-12-07 13:00 | 120.08 | 94.61
2017-12-07 13:30 | 120.35 | 94.74
2017-12-07 14:00 | 123.3 | 95.95
2017-12-07 14:30 | 123.21 | 94.42
2017-12-07 15:00 | 129.96 | 101.07
2017-12-07 15:30 | 123.97 | 94.8
2017-12-07 16:00 | 124.4 | 96.24
2017-12-07 16:30 | 112.92 | 88.38
2017-12-07 17:00 | 111.13 | 86.54
2017-12-07 17:30 | 102.24 | 78.06
2017-12-07 18:00 | 107.65 | 83.19
2017-12-07 18:30 | 113.11 | 87.78
2017-12-07 19:00 | 120.54 | 93.68
2017-12-07 19:30 | 131.71 | 103.37
2017-12-07 20:00 | 120.95 | 91.11
2017-12-07 20:30 | 124.69 | 95.68
2017-12-07 21:00 | 123.12 | 94
2017-12-07 21:30 | 125.01 | 95.36
2017-12-07 22:00 | 124.92 | 96.37
2017-12-07 22:30 | 123.65 | 94.06
2017-12-07 23:00 | 118.87 | 89.35
2017-12-07 23:30 | 118.91 | 91.71
2017-12-08 | 120.24 | 94.09
2017-12-08 00:30 | 121.67 | 92.12
2017-12-08 01:00 | 111.17 | 83.78
2017-12-08 01:30 | 114.38 | 88.54
2017-12-08 02:00 | 117.19 | 90.34
2017-12-08 02:30 | 120.6 | 95.22
2017-12-08 03:00 | 118.41 | 92.95
2017-12-08 03:30 | 115.11 | 89.32
2017-12-08 04:00 | 110.3 | 83.87
2017-12-08 04:30 | 122.4 | 98.54
2017-12-08 05:00 | 115.66 | 91.55
2017-12-08 05:30 | 112.87 | 89.94
2017-12-08 06:00 | 112.72 | 90.16
2017-12-08 06:30 | 105.11 | 84.03
2017-12-08 07:00 | 107.21 | 90.26
2017-12-08 07:30 | 108.98 | 90.48
2017-12-08 08:00 | 111.41 | 87.91
2017-12-08 08:30 | 110.6 | 83.76
2017-12-08 09:00 | 115.59 | 87.93
2017-12-08 09:30 | 118.39 | 90.7
2017-12-08 10:00 | 118.78 | 93.44
2017-12-08 10:30 | 115.71 | 91.55
2017-12-08 11:00 | 113.08 | 88.79
2017-12-08 11:30 | 116.06 | 93.69
2017-12-08 12:00 | 110.64 | 87.77
2017-12-08 12:30 | 110.51 | 87.21
2017-12-08 13:00 | 116.67 | 93.57
2017-12-08 13:30 | 119.41 | 95.63
2017-12-08 14:00 | 122.34 | 96.57
2017-12-08 14:30 | 117.33 | 93.79
2017-12-08 15:00 | 119.57 | 96.67
2017-12-08 15:30 | 119.59 | 95.62
2017-12-08 16:00 | 117.92 | 93.86
2017-12-08 16:30 | 125.89 | 102.21
2017-12-08 17:00 | 131.56 | 103.91
2017-12-08 17:30 | 130.24 | 102.72
2017-12-08 18:00 | 130.53 | 103.1
2017-12-08 18:30 | 125.94 | 97.98
2017-12-08 19:00 | 128.87 | 102.3
2017-12-08 19:30 | 125.96 | 100.15
2017-12-08 20:00 | 126.19 | 101.35
2017-12-08 20:30 | 118.62 | 93.96
2017-12-08 21:00 | 119.68 | 92.96
2017-12-08 21:30 | 119.57 | 93.41
2017-12-08 22:00 | 122.52 | 97.04
2017-12-08 22:30 | 124.79 | 100.89
2017-12-08 23:00 | 123.86 | 99.94
2017-12-08 23:30 | 116.67 | 92.86
2017-12-09 | 118.98 | 94.48
2017-12-09 00:30 | 119.81 | 94.87
2017-12-09 01:00 | 114.11 | 90.15
2017-12-09 01:30 | 115.63 | 90.22
2017-12-09 02:00 | 115.75 | 90.25
2017-12-09 02:30 | 116.87 | 90.5
2017-12-09 03:00 | 115.33 | 89.08
2017-12-09 03:30 | 120.25 | 96.51
2017-12-09 04:00 | 118.59 | 94.06
2017-12-09 04:30 | 115.87 | 90.56
2017-12-09 05:00 | 110.8 | 85.92
2017-12-09 05:30 | 108.99 | 84.22
2017-12-09 06:00 | 108.16 | 81.6
2017-12-09 06:30 | 107.08 | 79.82
2017-12-09 07:00 | 110.47 | 83.33
2017-12-09 07:30 | 118.68 | 90.93
2017-12-09 08:00 | 116.55 | 89.12
2017-12-09 08:30 | 121.23 | 93.48
2017-12-09 09:00 | 123.42 | 95.73
2017-12-09 09:30 | 125.78 | 98.38
2017-12-09 10:00 | 126.99 | 99.13
2017-12-09 10:30 | 121.85 | 94.29
2017-12-09 11:00 | 134.21 | 107.77
2017-12-09 11:30 | 123.85 | 96.83
2017-12-09 12:00 | 125.76 | 98.29
2017-12-09 12:30 | 132.78 | 106.36
2017-12-09 13:00 | 137.36 | 111.09
2017-12-09 13:30 | 130.31 | 103.21
2017-12-09 14:00 | 136.9 | 110.61
2017-12-09 14:30 | 132.34 | 105.5
2017-12-09 15:00 | 128.17 | 100.4
2017-12-09 15:30 | 129.53 | 100.04
2017-12-09 16:00 | 126.09 | 97.57
2017-12-09 16:30 | 130.58 | 103.58
2017-12-09 17:00 | 125.79 | 98.88
2017-12-09 17:30 | 129.65 | 103.04
2017-12-09 18:00 | 138.62 | 111.71
2017-12-09 18:30 | 130.93 | 103.28
2017-12-09 19:00 | 132.58 | 104.87
2017-12-09 19:30 | 132.57 | 104.38
2017-12-09 20:00 | 137.99 | 110.57
2017-12-09 20:30 | 124.32 | 100.5
2017-12-09 21:00 | 121.84 | 99.18
2017-12-09 21:30 | 125.14 | 103.27
2017-12-09 22:00 | 116.03 | 94.03
2017-12-09 22:30 | 115.86 | 93.63
2017-12-09 23:00 | 118.74 | 96.48
2017-12-09 23:30 | 114.81 | 92.04
2017-12-10 | 118.43 | 94.04
2017-12-10 00:30 | 117.31 | 93.94
2017-12-10 01:00 | 122.95 | 98.55
2017-12-10 01:30 | 121.22 | 96.46
2017-12-10 02:00 | 128.55 | 106.73
2017-12-10 02:30 | 123.08 | 100.73
2017-12-10 03:00 | 121.85 | 98.66
2017-12-10 03:30 | 123.27 | 101.32
2017-12-10 04:00 | 123.25 | 100.8
2017-12-10 04:30 | 123.02 | 99.45
2017-12-10 05:00 | 118.49 | 93.77
2017-12-10 05:30 | 117.69 | 93.5
2017-12-10 06:00 | 120.78 | 96.78
2017-12-10 06:30 | 118.51 | 94.07
2017-12-10 07:00 | 122.25 | 97.95
2017-12-10 07:30 | 126.24 | 102.15
2017-12-10 08:00 | 121.92 | 95.96
2017-12-10 08:30 | 126.13 | 99.44
2017-12-10 09:00 | 129.2 | 102.49
2017-12-10 09:30 | 133.24 | 107.7
2017-12-10 10:00 | 126.55 | 100
2017-12-10 10:30 | 131.09 | 103.9
2017-12-10 11:00 | 126.11 | 97.84
2017-12-10 11:30 | 130.89 | 101.59
2017-12-10 12:00 | 131.83 | 102.14
2017-12-10 12:30 | 132.43 | 102.94
2017-12-10 13:00 | 130.46 | 100.32
2017-12-10 13:30 | 133.93 | 104.18
2017-12-10 14:00 | 135.48 | 107.6
2017-12-10 14:30 | 140.48 | 113.52
2017-12-10 15:00 | 147.26 | 117.4
2017-12-10 15:30 | 139.62 | 111.78
2017-12-10 16:00 | 138.76 | 109.52
2017-12-10 16:30 | 147.15 | 119.03
2017-12-10 17:00 | 149.65 | 122.1
2017-12-10 17:30 | 143.72 | 114.36
2017-12-10 18:00 | 145.69 | 116.27
2017-12-10 18:30 | 137.15 | 108.1
2017-12-10 19:00 | 136.82 | 109.8
2017-12-10 19:30 | 142.46 | 113.77
2017-12-10 20:00 | 146.88 | 117.97
2017-12-10 20:30 | 145.54 | 117.52
2017-12-10 21:00 | 138.08 | 111.24
2017-12-10 21:30 | 134.84 | 108.77
2017-12-10 22:00 | 135.79 | 110.67
2017-12-10 22:30 | 133.97 | 107.7
2017-12-10 23:00 | 139.06 | 113.35
2017-12-10 23:30 | 130.39 | 104.21
2017-12-11 | 133.56 | 108.28
2017-12-11 00:30 | 139.03 | 114.35
2017-12-11 01:00 | 132.38 | 106.66
2017-12-11 01:30 | 133.73 | 108.42
2017-12-11 02:00 | 141.83 | 116.8
2017-12-11 02:30 | 128.86 | 104.12
2017-12-11 03:00 | 124.08 | 99.12
2017-12-11 03:30 | 125.14 | 99.87
2017-12-11 04:00 | 124.43 | 99.18
2017-12-11 04:30 | 120.26 | 94.15
2017-12-11 05:00 | 124.7 | 98.53
2017-12-11 05:30 | 119.07 | 94.28
2017-12-11 06:00 | 121.23 | 97.11
2017-12-11 06:30 | 115.22 | 89.9
2017-12-11 07:00 | 121.32 | 95.28
2017-12-11 07:30 | 118.53 | 90.78
2017-12-11 08:00 | 118.52 | 90.04
2017-12-11 08:30 | 134.38 | 108.42
2017-12-11 09:00 | 127.9 | 100.4
2017-12-11 09:30 | 130.12 | 102.64
2017-12-11 10:00 | 123.3 | 98
2017-12-11 10:30 | 131.51 | 105.97
2017-12-11 11:00 | 124.41 | 98.21
2017-12-11 11:30 | 124.82 | 99.58
2017-12-11 12:00 | 123.29 | 96.71
2017-12-11 12:30 | 122.32 | 96.01
2017-12-11 13:00 | 129.52 | 103.09
2017-12-11 13:30 | 136.81 | 111.52
2017-12-11 14:00 | 129.51 | 103.38
2017-12-11 14:30 | 131.79 | 106.22
2017-12-11 15:00 | 127.99 | 102.02
2017-12-11 15:30 | 129.5 | 101.76
2017-12-11 16:00 | 133.42 | 106.1
2017-12-11 16:30 | 129.11 | 101.49
2017-12-11 17:00 | 133.66 | 106.71
2017-12-11 17:30 | 136.37 | 110.92
2017-12-11 18:00 | 135.79 | 109.94
2017-12-11 18:30 | 129.57 | 101.41
2017-12-11 19:00 | 136.03 | 107.25
2017-12-11 19:30 | 146 | 117.81
2017-12-11 20:00 | 137.11 | 107.01
2017-12-11 20:30 | 135.9 | 106.81
2017-12-11 21:00 | 137.64 | 109.34
2017-12-11 21:30 | 140.22 | 114.21
2017-12-11 22:00 | 131.43 | 104.87
2017-12-11 22:30 | 128.42 | 101.64
2017-12-11 23:00 | 130 | 104.27
2017-12-11 23:30 | 131.1 | 106.42
2017-12-12 | 129.82 | 104.85
2017-12-12 00:30 | 133.92 | 107.92
2017-12-12 01:00 | 126.28 | 99.77
2017-12-12 01:30 | 125.67 | 100.06
2017-12-12 02:00 | 126.04 | 99.85
2017-12-12 02:30 | 122.42 | 96.05
2017-12-12 03:00 | 121.4 | 95.19
2017-12-12 03:30 | 115.15 | 89.62
2017-12-12 04:00 | 116.88 | 93.59
2017-12-12 04:30 | 119.66 | 96.91
2017-12-12 05:00 | 116.05 | 91.79
2017-12-12 05:30 | 126.5 | 103.42
2017-12-12 06:00 | 123.75 | 100.97
2017-12-12 06:30 | 112.18 | 87.19
2017-12-12 07:00 | 113.21 | 89.17
2017-12-12 07:30 | 107.98 | 82.9
2017-12-12 08:00 | 112.28 | 86.89
2017-12-12 08:30 | 109.02 | 81.93
2017-12-12 09:00 | 106.3 | 77.98
2017-12-12 09:30 | 111.32 | 84.19
2017-12-12 10:00 | 105.19 | 78.56
2017-12-12 10:30 | 104.78 | 79.13
2017-12-12 11:00 | 103.72 | 77.64
2017-12-12 11:30 | 104.7 | 77.77
2017-12-12 12:00 | 113.76 | 87.29
2017-12-12 12:30 | 108.86 | 82.62
2017-12-12 13:00 | 114.85 | 89.25
2017-12-12 13:30 | 113.77 | 89.59
2017-12-12 14:00 | 113.09 | 88.82
2017-12-12 14:30 | 118.83 | 93.64
2017-12-12 15:00 | 123.93 | 98.78
2017-12-12 15:30 | 120.44 | 95.13
2017-12-12 16:00 | 124.16 | 99.37
2017-12-12 16:30 | 125.69 | 99.88
2017-12-12 17:00 | 123.23 | 95.86
2017-12-12 17:30 | 126.3 | 99.42
2017-12-12 18:00 | 126.31 | 99.24
2017-12-12 18:30 | 117.39 | 88.51
2017-12-12 19:00 | 120.06 | 92.75
2017-12-12 19:30 | 137.96 | 111.71
2017-12-12 20:00 | 128.77 | 102.05
2017-12-12 20:30 | 134.55 | 108.28
2017-12-12 21:00 | 133.87 | 106.67
2017-12-12 21:30 | 137.3 | 110.31
2017-12-12 22:00 | 129.23 | 101.8
2017-12-12 22:30 | 133.17 | 106.61
2017-12-12 23:00 | 131.34 | 104.67
2017-12-12 23:30 | 125.58 | 100.29
2017-12-13 | 122.09 | 97.28
2017-12-13 00:30 | 127.14 | 102.79
2017-12-13 01:00 | 123.27 | 98.61
2017-12-13 01:30 | 117.99 | 94.92
2017-12-13 02:00 | 116.68 | 93.19
2017-12-13 02:30 | 110.55 | 87.88
2017-12-13 03:00 | 102.48 | 79.88
2017-12-13 03:30 | 104.91 | 82.74
2017-12-13 04:00 | 103.21 | 82.39
2017-12-13 04:30 | 107.28 | 87.14
2017-12-13 05:00 | 113.08 | 94.6
2017-12-13 05:30 | 108 | 89.84
2017-12-13 06:00 | 107.85 | 90.26
2017-12-13 06:30 | 94.04 | 76.16
2017-12-13 07:00 | 100.74 | 81.94
2017-12-13 07:30 | 99.77 | 82.75
2017-12-13 08:00 | 90.09 | 72.87
2017-12-13 08:30 | 93.15 | 75.18
2017-12-13 09:00 | 94.5 | 75.57
2017-12-13 09:30 | 94.5 | 75.55
2017-12-13 10:00 | 101.69 | 83.39
2017-12-13 10:30 | 93.51 | 75.27
2017-12-13 11:00 | 98.2 | 79.44
2017-12-13 11:30 | 97.38 | 78.69
2017-12-13 12:00 | 94.72 | 75.16
2017-12-13 12:30 | 94.97 | 75.8
2017-12-13 13:00 | 98.31 | 80.43
2017-12-13 13:30 | 99.35 | 80.89
2017-12-13 14:00 | 91.98 | 72.37
2017-12-13 14:30 | 100.41 | 80.96
2017-12-13 15:00 | 104.56 | 84.56
2017-12-13 15:30 | 100.61 | 80.54
2017-12-13 16:00 | 100.83 | 79.61
2017-12-13 16:30 | 101.65 | 81.62
2017-12-13 17:00 | 102.48 | 84.01
2017-12-13 17:30 | 111.15 | 94.58
2017-12-13 18:00 | 109.28 | 91.8
2017-12-13 18:30 | 105.86 | 87.81
2017-12-13 19:00 | 106.1 | 87.73
2017-12-13 19:30 | 116.93 | 97.8
2017-12-13 20:00 | 112.21 | 92.34
2017-12-13 20:30 | 114.3 | 94.94
2017-12-13 21:00 | 112.07 | 92.43
2017-12-13 21:30 | 113.33 | 94.43
2017-12-13 22:00 | 108.89 | 90.88
2017-12-13 22:30 | 104.48 | 86.72
2017-12-13 23:00 | 105 | 86.79
2017-12-13 23:30 | 103.45 | 85.64
2017-12-14 | 102.79 | 84.91
2017-12-14 00:30 | 99.01 | 80.69
2017-12-14 01:00 | 101.36 | 82.65
2017-12-14 01:30 | 103.46 | 85.88
2017-12-14 02:00 | 106.6 | 89.37
2017-12-14 02:30 | 108.74 | 91.51
2017-12-14 03:00 | 98.31 | 80.47
2017-12-14 03:30 | 98.4 | 81.46
2017-12-14 04:00 | 108.48 | 92.61
2017-12-14 04:30 | 97.54 | 81.6
2017-12-14 05:00 | 99.8 | 83
2017-12-14 05:30 | 96.07 | 79.6
2017-12-14 06:00 | 97.62 | 80.5
2017-12-14 06:30 | 86.26 | 68.23
2017-12-14 07:00 | 93.94 | 76.03
2017-12-14 07:30 | 94.26 | 76.81
2017-12-14 08:00 | 96.19 | 78.36
2017-12-14 08:30 | 100.95 | 83.51
2017-12-14 09:00 | 101.72 | 84.21
2017-12-14 09:30 | 95.02 | 75.79
2017-12-14 10:00 | 97.74 | 78.54
2017-12-14 10:30 | 93.39 | 73.99
2017-12-14 11:00 | 95.77 | 75.08
2017-12-14 11:30 | 106.88 | 86.51
2017-12-14 12:00 | 100.21 | 80.32
2017-12-14 12:30 | 102.26 | 82.28
2017-12-14 13:00 | 103.74 | 83.84
2017-12-14 13:30 | 110.91 | 92
2017-12-14 14:00 | 100.04 | 77.97
2017-12-14 14:30 | 103.54 | 82.3
2017-12-14 15:00 | 101.87 | 78.59
2017-12-14 15:30 | 99.95 | 77.53
2017-12-14 16:00 | 102.02 | 80.19
2017-12-14 16:30 | 108.61 | 87.02
2017-12-14 17:00 | 106.64 | 84.92
2017-12-14 17:30 | 105.96 | 83.93
2017-12-14 18:00 | 119.36 | 98.18
2017-12-14 18:30 | 101.26 | 80.69
2017-12-14 19:00 | 112.35 | 92.59
2017-12-14 19:30 | 115.44 | 95.76
2017-12-14 20:00 | 112.9 | 92.54
2017-12-14 20:30 | 111.43 | 91.01
2017-12-14 21:00 | 115.77 | 93.58
2017-12-14 21:30 | 110.68 | 88.6
2017-12-14 22:00 | 117.77 | 95.09
2017-12-14 22:30 | 115.15 | 90.65
2017-12-14 23:00 | 119.17 | 95.64
2017-12-14 23:30 | 117.81 | 94.65
2017-12-15 | 121.3 | 98.97
2017-12-15 00:30 | 114.28 | 92.13
2017-12-15 01:00 | 115.23 | 93.12
2017-12-15 01:30 | 115.8 | 93.23
2017-12-15 02:00 | 122.02 | 98.14
2017-12-15 02:30 | 113.66 | 88.9
2017-12-15 03:00 | 116.2 | 90.74
2017-12-15 03:30 | 114.73 | 89.4
2017-12-15 04:00 | 116.57 | 91.52
2017-12-15 04:30 | 114.19 | 89.69
2017-12-15 05:00 | 122.67 | 99.17
2017-12-15 05:30 | 114.93 | 91.82
2017-12-15 06:00 | 117.49 | 94.3
2017-12-15 06:30 | 108.47 | 83.39
2017-12-15 07:00 | 110.51 | 85.61
2017-12-15 07:30 | 113.7 | 90.13
2017-12-15 08:00 | 110.46 | 85.46
2017-12-15 08:30 | 111.8 | 86.81
2017-12-15 09:00 | 112.8 | 87.26
2017-12-15 09:30 | 115.32 | 90.36
2017-12-15 10:00 | 114.69 | 90.49
2017-12-15 10:30 | 120.7 | 97.59
2017-12-15 11:00 | 113.75 | 89.72
2017-12-15 11:30 | 115.41 | 90.42
2017-12-15 12:00 | 111.39 | 86.89
2017-12-15 12:30 | 114.9 | 89.17
2017-12-15 13:00 | 110.94 | 87.22
2017-12-15 13:30 | 114.45 | 89.42
2017-12-15 14:00 | 114.48 | 89.29
2017-12-15 14:30 | 108.25 | 81.25
2017-12-15 15:00 | 105.85 | 78.11
2017-12-15 15:30 | 112.77 | 86.25
2017-12-15 16:00 | 120.15 | 92.24
2017-12-15 16:30 | 128.13 | 99.23
2017-12-15 17:00 | 134.01 | 102.09
2017-12-15 17:30 | 137.75 | 107.35
2017-12-15 18:00 | 147.55 | 117.72
2017-12-15 18:30 | 137.37 | 107.89
2017-12-15 19:00 | 139.72 | 110.79
2017-12-15 19:30 | 136.51 | 107.1
2017-12-15 20:00 | 133.34 | 104.88
2017-12-15 20:30 | 136.82 | 108.85
2017-12-15 21:00 | 134.19 | 105.89
2017-12-15 21:30 | 132.39 | 104.53
2017-12-15 22:00 | 124.48 | 96.84
2017-12-15 22:30 | 119.1 | 91.56
2017-12-15 23:00 | 119.2 | 91.35
2017-12-15 23:30 | 114.02 | 87.2
2017-12-16 | 117.94 | 93.07
2017-12-16 00:30 | 122.67 | 96.6
2017-12-16 01:00 | 122.71 | 96.78
2017-12-16 01:30 | 116.26 | 90.23
2017-12-16 02:00 | 113.87 | 88.56
2017-12-16 02:30 | 124.18 | 99.88
2017-12-16 03:00 | 114.67 | 88.66
2017-12-16 03:30 | 119.69 | 94.73
2017-12-16 04:00 | 121.48 | 94.64
2017-12-16 04:30 | 123.55 | 97.52
2017-12-16 05:00 | 132.2 | 106.72
2017-12-16 05:30 | 126.49 | 100.63
2017-12-16 06:00 | 132.17 | 107.67
2017-12-16 06:30 | 124.29 | 97.67
2017-12-16 07:00 | 128.68 | 102.67
2017-12-16 07:30 | 129.67 | 102.46
2017-12-16 08:00 | 118.75 | 91.31
2017-12-16 08:30 | 115.25 | 84.78
2017-12-16 09:00 | 108.91 | 75.19
2017-12-16 09:30 | 112.87 | 80.61
2017-12-16 10:00 | 123.24 | 90.01
2017-12-16 10:30 | 126.03 | 94.59
2017-12-16 11:00 | 125.27 | 93.9
2017-12-16 11:30 | 128.95 | 98.97
2017-12-16 12:00 | 126.1 | 98.86
2017-12-16 12:30 | 129.27 | 102.58
2017-12-16 13:00 | 122.84 | 95.03
2017-12-16 13:30 | 125.87 | 97.68
2017-12-16 14:00 | 125.23 | 98.46
2017-12-16 14:30 | 130.29 | 102.6
2017-12-16 15:00 | 122.85 | 94.43
2017-12-16 15:30 | 122.55 | 94.63
2017-12-16 16:00 | 128.04 | 99.81
2017-12-16 16:30 | 133.12 | 103.49
2017-12-16 17:00 | 141.55 | 110.11
2017-12-16 17:30 | 137.44 | 107.1
2017-12-16 18:00 | 137.03 | 107.74
2017-12-16 18:30 | 127.81 | 98.97
2017-12-16 19:00 | 125.72 | 98.28
2017-12-16 19:30 | 137.36 | 108.42
2017-12-16 20:00 | 141.03 | 112.18
2017-12-16 20:30 | 134.38 | 105.43
2017-12-16 21:00 | 133.7 | 106.96
2017-12-16 21:30 | 129.3 | 102.03
2017-12-16 22:00 | 126.83 | 98.76
2017-12-16 22:30 | 125.99 | 98.18
2017-12-16 23:00 | 120.4 | 92.96
2017-12-16 23:30 | 124.41 | 97.81
2017-12-17 | 124.22 | 98.14
2017-12-17 00:30 | 118.77 | 91.65
2017-12-17 01:00 | 122.89 | 96.32
2017-12-17 01:30 | 126.19 | 99.34
2017-12-17 02:00 | 119.42 | 93.59
2017-12-17 02:30 | 121.33 | 95.77
2017-12-17 03:00 | 115.51 | 88.72
2017-12-17 03:30 | 115.32 | 89.31
2017-12-17 04:00 | 115.23 | 89.56
2017-12-17 04:30 | 122.49 | 97.52
2017-12-17 05:00 | 119.5 | 95.04
2017-12-17 05:30 | 117.34 | 93.04
2017-12-17 06:00 | 119.27 | 94.08
2017-12-17 06:30 | 112.77 | 86.93
2017-12-17 07:00 | 114.25 | 87.79
2017-12-17 07:30 | 117.73 | 91.74
2017-12-17 08:00 | 116.17 | 89.8
2017-12-17 08:30 | 122.35 | 96.76
2017-12-17 09:00 | 132.18 | 106.81
2017-12-17 09:30 | 128.69 | 102.94
2017-12-17 10:00 | 124.79 | 99.37
2017-12-17 10:30 | 121.78 | 95.91
2017-12-17 11:00 | 123.06 | 97.08
2017-12-17 11:30 | 127.85 | 101.48
2017-12-17 12:00 | 124.06 | 96.68
2017-12-17 12:30 | 137.6 | 110.44
2017-12-17 13:00 | 132.86 | 105.45
2017-12-17 13:30 | 134.46 | 106.35
2017-12-17 14:00 | 136.57 | 107.87
2017-12-17 14:30 | 135.26 | 105.84
2017-12-17 15:00 | 135.62 | 105.13
2017-12-17 15:30 | 133.22 | 102.89
2017-12-17 16:00 | 130.91 | 100.38
2017-12-17 16:30 | 139.05 | 109.31
2017-12-17 17:00 | 148.55 | 119.15
2017-12-17 17:30 | 144.7 | 114.14
2017-12-17 18:00 | 144.81 | 114.68
2017-12-17 18:30 | 125.3 | 92.94
2017-12-17 19:00 | 134 | 102.16
2017-12-17 19:30 | 137.93 | 106.34
2017-12-17 20:00 | 138.23 | 108.2
2017-12-17 20:30 | 142.9 | 113.44
2017-12-17 21:00 | 139.35 | 110.15
2017-12-17 21:30 | 135.59 | 106.18
2017-12-17 22:00 | 142.22 | 113.08
2017-12-17 22:30 | 132.85 | 102.99
2017-12-17 23:00 | 139.48 | 110
2017-12-17 23:30 | 134.06 | 106.04
2017-12-18 | 129.46 | 102.92
2017-12-18 00:30 | 130.67 | 103.81
2017-12-18 01:00 | 128.31 | 100.39
2017-12-18 01:30 | 130.86 | 102.6
2017-12-18 02:00 | 131.13 | 101.93
2017-12-18 02:30 | 131.3 | 103.14
2017-12-18 03:00 | 129.94 | 101.01
2017-12-18 03:30 | 128.21 | 100.42
2017-12-18 04:00 | 128.92 | 102.76
2017-12-18 04:30 | 129.74 | 103.27
2017-12-18 05:00 | 126.98 | 99.54
2017-12-18 05:30 | 119.98 | 93.18
2017-12-18 06:00 | 112.27 | 83.42
2017-12-18 06:30 | 111.23 | 80.96
2017-12-18 07:00 | 115.82 | 85.3
2017-12-18 07:30 | 117.32 | 86.96
2017-12-18 08:00 | 118.08 | 88.02
2017-12-18 08:30 | 120.36 | 90.81
2017-12-18 09:00 | 119.47 | 89.14
2017-12-18 09:30 | 113.08 | 82.13
2017-12-18 10:00 | 113.93 | 92.07
2017-12-18 10:30 | 112.03 | 83.86
2017-12-18 11:00 | 107 | 82.18
2017-12-18 11:30 | 101.2 | 85.74
2017-12-18 12:00 | 101.88 | 86.74
2017-12-18 12:30 | 101.24 | 86.19
2017-12-18 13:00 | 99.15 | 85.07
2017-12-18 13:30 | 104.31 | 90.22
2017-12-18 14:00 | 106.91 | 93.28
2017-12-18 14:30 | 101.12 | 86.49
2017-12-18 15:00 | 115.54 | 94.53
2017-12-18 15:30 | 115.12 | 88.4
2017-12-18 16:00 | 121.9 | 92.83
2017-12-18 16:30 | 119.47 | 90.4
2017-12-18 17:00 | 119.76 | 90.06
2017-12-18 17:30 | 123.73 | 95.61
2017-12-18 18:00 | 123.75 | 94.99
2017-12-18 18:30 | 118.89 | 89.96
2017-12-18 19:00 | 127.68 | 99.85
2017-12-18 19:30 | 125.77 | 96.76
2017-12-18 20:00 | 129.47 | 98.32
2017-12-18 20:30 | 131.13 | 98.93
2017-12-18 21:00 | 127.35 | 95.17
2017-12-18 21:30 | 122.44 | 90.96
2017-12-18 22:00 | 124.44 | 94.72
2017-12-18 22:30 | 126.48 | 97.74
2017-12-18 23:00 | 126.77 | 98.3
2017-12-18 23:30 | 126.99 | 97.66
2017-12-19 | 132.24 | 102.94
2017-12-19 00:30 | 130.28 | 101.74
2017-12-19 01:00 | 129.69 | 101.65
2017-12-19 01:30 | 127.35 | 98.62
2017-12-19 02:00 | 131.62 | 103.01
2017-12-19 02:30 | 123.26 | 96.69
2017-12-19 03:00 | 121.17 | 93.63
2017-12-19 03:30 | 123.66 | 96.14
2017-12-19 04:00 | 123.62 | 97.19
2017-12-19 04:30 | 123.67 | 96.9
2017-12-19 05:00 | 119.33 | 91.54
2017-12-19 05:30 | 119.56 | 93.33
2017-12-19 06:00 | 119.72 | 93.26
2017-12-19 06:30 | 113.39 | 84.47
2017-12-19 07:00 | 114.41 | 88.01
2017-12-19 07:30 | 113.85 | 86.52
2017-12-19 08:00 | 117.86 | 88.41
2017-12-19 08:30 | 114.84 | 85.21
2017-12-19 09:00 | 118.27 | 89.34
2017-12-19 09:30 | 127.46 | 98.5
2017-12-19 10:00 | 123.25 | 92.46
2017-12-19 10:30 | 124.85 | 94.35
2017-12-19 11:00 | 126.2 | 95.93
2017-12-19 11:30 | 126.97 | 95.23
2017-12-19 12:00 | 121.37 | 93.14
2017-12-19 12:30 | 123.2 | 96.11
2017-12-19 13:00 | 129.04 | 101.44
2017-12-19 13:30 | 131.67 | 101.08
2017-12-19 14:00 | 136.3 | 103.36
2017-12-19 14:30 | 132.69 | 100.58
2017-12-19 15:00 | 138.25 | 106.04
2017-12-19 15:30 | 130.24 | 98.39
2017-12-19 16:00 | 126.71 | 96.66
2017-12-19 16:30 | 130.82 | 101.2
2017-12-19 17:00 | 135.48 | 107.5
2017-12-19 17:30 | 139.59 | 110.36
2017-12-19 18:00 | 132.84 | 104.88
2017-12-19 18:30 | 124.81 | 96.43
2017-12-19 19:00 | 123.48 | 94.97
2017-12-19 19:30 | 130.02 | 102.45
2017-12-19 20:00 | 131.39 | 103.85
2017-12-19 20:30 | 130.08 | 103.35
2017-12-19 21:00 | 124.97 | 96.51
2017-12-19 21:30 | 129.82 | 102.45
2017-12-19 22:00 | 131.99 | 104.91
2017-12-19 22:30 | 129.84 | 103.61
2017-12-19 23:00 | 132.64 | 106.95
2017-12-19 23:30 | 131.52 | 105.86
2017-12-20 | 132.43 | 105.37
2017-12-20 00:30 | 131.52 | 104.46
2017-12-20 01:00 | 127.82 | 101.92
2017-12-20 01:30 | 123.39 | 97.08
2017-12-20 02:00 | 132.92 | 107.43
2017-12-20 02:30 | 124.76 | 98.7
2017-12-20 03:00 | 127.24 | 101.39
2017-12-20 03:30 | 125.82 | 99.5
2017-12-20 04:00 | 122.53 | 94.57
2017-12-20 04:30 | 122.09 | 95.06
2017-12-20 05:00 | 114.75 | 87.1
2017-12-20 05:30 | 122.7 | 97.18
2017-12-20 06:00 | 120.13 | 93.68
2017-12-20 06:30 | 115.69 | 88.5
2017-12-20 07:00 | 114.19 | 86.67
2017-12-20 07:30 | 120.11 | 92.74
2017-12-20 08:00 | 122.77 | 94.56
2017-12-20 08:30 | 118.49 | 89.07
2017-12-20 09:00 | 126.06 | 97.53
2017-12-20 09:30 | 129.17 | 99.25
2017-12-20 10:00 | 129.25 | 100.13
2017-12-20 10:30 | 122.62 | 94.53
2017-12-20 11:00 | 121.1 | 93.29
2017-12-20 11:30 | 123.01 | 95.61
2017-12-20 12:00 | 124.8 | 97.99
2017-12-20 12:30 | 128.18 | 102.49
2017-12-20 13:00 | 124.94 | 99.73
2017-12-20 13:30 | 128.65 | 102.69
2017-12-20 14:00 | 126.68 | 99.32
2017-12-20 14:30 | 130.99 | 101.97
2017-12-20 15:00 | 137.15 | 107.39
2017-12-20 15:30 | 137.19 | 106.4
2017-12-20 16:00 | 132.49 | 103.25
2017-12-20 16:30 | 131.45 | 103.06
2017-12-20 17:00 | 146.13 | 116.01
2017-12-20 17:30 | 140.29 | 108.26
2017-12-20 18:00 | 143.75 | 112.6
2017-12-20 18:30 | 136.39 | 105.9
2017-12-20 19:00 | 136.3 | 105.52
2017-12-20 19:30 | 138.74 | 108.83
2017-12-20 20:00 | 146.75 | 116.31
2017-12-20 20:30 | 147.09 | 116.13
2017-12-20 21:00 | 146.18 | 115.73
2017-12-20 21:30 | 150.38 | 122.04
2017-12-20 22:00 | 143.7 | 114.03
2017-12-20 22:30 | 138.64 | 109.01
2017-12-20 23:00 | 138.27 | 108.25
2017-12-20 23:30 | 131.29 | 102.49
2017-12-21 | 130.12 | 101.47
2017-12-21 00:30 | 135.27 | 105.84
2017-12-21 01:00 | 132.97 | 103.26
2017-12-21 01:30 | 126.53 | 95.27
2017-12-21 02:00 | 128.47 | 99.35
2017-12-21 02:30 | 130.41 | 102.29
2017-12-21 03:00 | 127.29 | 101.34
2017-12-21 03:30 | 129.75 | 102.9
2017-12-21 04:00 | 128.82 | 102.05
2017-12-21 04:30 | 129.06 | 100.86
2017-12-21 05:00 | 130.9 | 103.13
2017-12-21 05:30 | 135.81 | 108.75
2017-12-21 06:00 | 133.33 | 105.14
2017-12-21 06:30 | 125.51 | 94.25
2017-12-21 07:00 | 125.28 | 95.63
2017-12-21 07:30 | 122.75 | 92.93
2017-12-21 08:00 | 122.57 | 92.07
2017-12-21 08:30 | 125.13 | 92.95
2017-12-21 09:00 | 129.73 | 98.67
2017-12-21 09:30 | 125.38 | 93.41
2017-12-21 10:00 | 126.19 | 92.12
2017-12-21 10:30 | 129.95 | 95.16
2017-12-21 11:00 | 122.81 | 87.91
2017-12-21 11:30 | 123.38 | 88.37
2017-12-21 12:00 | 124.98 | 90.95
2017-12-21 12:30 | 126.23 | 91.91
2017-12-21 13:00 | 123.96 | 92.18
2017-12-21 13:30 | 129.74 | 97.66
2017-12-21 14:00 | 133.74 | 97.51
2017-12-21 14:30 | 135.31 | 98.98
2017-12-21 15:00 | 128.87 | 93.23
2017-12-21 15:30 | 133.96 | 100.13
2017-12-21 16:00 | 136.5 | 104.34
2017-12-21 16:30 | 135.87 | 103.5
2017-12-21 17:00 | 134.64 | 103.34
2017-12-21 17:30 | 138.21 | 106.36
2017-12-21 18:00 | 137.89 | 106.14
2017-12-21 18:30 | 132.48 | 100.79
2017-12-21 19:00 | 136.6 | 108.05
2017-12-21 19:30 | 142.2 | 113.41
2017-12-21 20:00 | 138.06 | 108.79
2017-12-21 20:30 | 139.24 | 109.27
2017-12-21 21:00 | 139.25 | 109.52
2017-12-21 21:30 | 130.49 | 101.42
2017-12-21 22:00 | 134.24 | 105.09
2017-12-21 22:30 | 128.44 | 99.22
2017-12-21 23:00 | 132.36 | 104.81
2017-12-21 23:30 | 125.68 | 97.75
2017-12-22 | 130.79 | 102.07
2017-12-22 00:30 | 133.96 | 107.07
2017-12-22 01:00 | 121.6 | 94.5
2017-12-22 01:30 | 128.29 | 99.91
2017-12-22 02:00 | 131.6 | 105.61
2017-12-22 02:30 | 134.55 | 108.68
2017-12-22 03:00 | 134.67 | 109.92
2017-12-22 03:30 | 135.34 | 110.32
2017-12-22 04:00 | 126.69 | 101.14
2017-12-22 04:30 | 125.46 | 99.25
2017-12-22 05:00 | 124.66 | 100.12
2017-12-22 05:30 | 135.37 | 110.11
2017-12-22 06:00 | 110.19 | 82.74
2017-12-22 06:30 | 102.3 | 70.92
2017-12-22 07:00 | 106.73 | 79.22
2017-12-22 07:30 | 109.27 | 80.28
2017-12-22 08:00 | 110.32 | 81.19
2017-12-22 08:30 | 116.26 | 87.75
2017-12-22 09:00 | 119.81 | 92.67
2017-12-22 09:30 | 114.72 | 86.41
2017-12-22 10:00 | 122.89 | 96.41
2017-12-22 10:30 | 131.98 | 105.63
2017-12-22 11:00 | 129.11 | 103
2017-12-22 11:30 | 117.38 | 92.2
2017-12-22 12:00 | 116.35 | 91.6
2017-12-22 12:30 | 122.64 | 96
2017-12-22 13:00 | 129.67 | 103.02
2017-12-22 13:30 | 127.02 | 100.91
2017-12-22 14:00 | 126.58 | 98.82
2017-12-22 14:30 | 121.48 | 93.32
2017-12-22 15:00 | 121.08 | 94.41
2017-12-22 15:30 | 122.49 | 94.9
2017-12-22 16:00 | 125.54 | 97.83
2017-12-22 16:30 | 124.67 | 97.96
2017-12-22 17:00 | 126.88 | 102.01
2017-12-22 17:30 | 134.13 | 109.31
2017-12-22 18:00 | 136.21 | 109.75
2017-12-22 18:30 | 131.67 | 104.41
2017-12-22 19:00 | 134.25 | 109.37
2017-12-22 19:30 | 136.78 | 111.5
2017-12-22 20:00 | 136.56 | 110.73
2017-12-22 20:30 | 136.26 | 110.95
2017-12-22 21:00 | 134.33 | 109.41
2017-12-22 21:30 | 132.47 | 107.83
2017-12-22 22:00 | 129.59 | 103.01
2017-12-22 22:30 | 122.85 | 96.41
2017-12-22 23:00 | 126.32 | 100.51
2017-12-22 23:30 | 116.63 | 93.29
2017-12-23 | 120.02 | 97.82
2017-12-23 00:30 | 113.15 | 91.44
2017-12-23 01:00 | 112.99 | 90.68
2017-12-23 01:30 | 109.33 | 86.16
2017-12-23 02:00 | 123.26 | 99.91
2017-12-23 02:30 | 126.59 | 101.62
2017-12-23 03:00 | 124.17 | 99.99
2017-12-23 03:30 | 119.13 | 94.29
2017-12-23 04:00 | 117.19 | 92.04
2017-12-23 04:30 | 122.19 | 97.48
2017-12-23 05:00 | 126.15 | 102.05
2017-12-23 05:30 | 127.67 | 103.17
2017-12-23 06:00 | 126.22 | 100.91
2017-12-23 06:30 | 118.51 | 92.15
2017-12-23 07:00 | 127.89 | 103.94
2017-12-23 07:30 | 130.21 | 105.84
2017-12-23 08:00 | 130.06 | 105
2017-12-23 08:30 | 123.96 | 96.68
2017-12-23 09:00 | 117.03 | 87.74
2017-12-23 09:30 | 121.22 | 94.83
2017-12-23 10:00 | 117.92 | 92.31
2017-12-23 10:30 | 121.7 | 95.77
2017-12-23 11:00 | 117.23 | 91.41
2017-12-23 11:30 | 113.69 | 88.8
2017-12-23 12:00 | 114.33 | 88.89
2017-12-23 12:30 | 115.3 | 89.26
2017-12-23 13:00 | 121.4 | 95.59
2017-12-23 13:30 | 120.02 | 94.16
2017-12-23 14:00 | 121.15 | 93.44
2017-12-23 14:30 | 119.4 | 91.52
2017-12-23 15:00 | 115.51 | 86.95
2017-12-23 15:30 | 125.46 | 97.05
2017-12-23 16:00 | 126.69 | 98.82
2017-12-23 16:30 | 123.82 | 97.14
2017-12-23 17:00 | 123.08 | 94.8
2017-12-23 17:30 | 117.84 | 89.25
2017-12-23 18:00 | 114.78 | 85.41
2017-12-23 18:30 | 117.72 | 88.14
2017-12-23 19:00 | 121.42 | 91.1
2017-12-23 19:30 | 125.26 | 95.72
2017-12-23 20:00 | 124.53 | 95.66
2017-12-23 20:30 | 125.25 | 100.08
2017-12-23 21:00 | 130.53 | 105.26
2017-12-23 21:30 | 125.68 | 101.36
2017-12-23 22:00 | 116.83 | 92.75
2017-12-23 22:30 | 116.16 | 91.86
2017-12-23 23:00 | 118.3 | 95.73
2017-12-23 23:30 | 113.93 | 90.21
2017-12-24 | 117.67 | 94.76
2017-12-24 00:30 | 119 | 95.83
2017-12-24 01:00 | 110.82 | 86.82
2017-12-24 01:30 | 116.73 | 92.35
2017-12-24 02:00 | 111.69 | 87.79
2017-12-24 02:30 | 107.23 | 83.22
2017-12-24 03:00 | 108.21 | 84.52
2017-12-24 03:30 | 110.51 | 86.4
2017-12-24 04:00 | 108.53 | 86.12
2017-12-24 04:30 | 109.91 | 88.13
2017-12-24 05:00 | 113.12 | 92.64
2017-12-24 05:30 | 110.08 | 89.74
2017-12-24 06:00 | 106.54 | 85.32
2017-12-24 06:30 | 105.42 | 83.72
2017-12-24 07:00 | 106.32 | 84.56
2017-12-24 07:30 | 103.45 | 82.08
2017-12-24 08:00 | 107.34 | 85.73
2017-12-24 08:30 | 112.64 | 91.78
2017-12-24 09:00 | 116.12 | 95.78
2017-12-24 09:30 | 105.13 | 83.05
2017-12-24 10:00 | 102.69 | 79.6
2017-12-24 10:30 | 111.72 | 89.63
2017-12-24 11:00 | 110.89 | 89.2
2017-12-24 11:30 | 112.85 | 91.85
2017-12-24 12:00 | 112.21 | 91.9
2017-12-24 12:30 | 109.54 | 88.34
2017-12-24 13:00 | 108.4 | 87.4
2017-12-24 13:30 | 86.88 | 70.11
2017-12-24 14:00 | 77.01 | 59.13
2017-12-24 14:30 | 74.97 | 56.03
2017-12-24 15:00 | 78.48 | 59.18
2017-12-24 15:30 | 80.26 | 61.31
2017-12-24 16:00 | 80.43 | 61.82
2017-12-24 16:30 | 75.66 | 52.8
2017-12-24 17:00 | 78.11 | 56.87
2017-12-24 17:30 | 73.23 | 51.64
2017-12-24 18:00 | 77.74 | 56.18
2017-12-24 18:30 | 69.86 | 48.73
2017-12-24 19:00 | 69.12 | 47.14
2017-12-24 19:30 | 73.27 | 51.29
2017-12-24 20:00 | 74.16 | 52.51
2017-12-24 20:30 | 74.15 | 54.77
2017-12-24 21:00 | 70.64 | 49.78
2017-12-24 21:30 | 65.63 | 44.62
2017-12-24 22:00 | 70.98 | 51.05
2017-12-24 22:30 | 62.75 | 40.98
2017-12-24 23:00 | 63.13 | 41.73
2017-12-24 23:30 | 63.48 | 42.97
2017-12-25 | 61.61 | 41.22
2017-12-25 00:30 | 59.34 | 39.39
2017-12-25 01:00 | 65.83 | 46.44
2017-12-25 01:30 | 59.1 | 38.68
2017-12-25 02:00 | 58.67 | 37.51
2017-12-25 02:30 | 61.81 | 38.24
2017-12-25 03:00 | 61.21 | 35.87
2017-12-25 03:30 | 62.56 | 37.48
2017-12-25 04:00 | 61.63 | 36.26
2017-12-25 04:30 | 65.46 | 40.69
2017-12-25 05:00 | 68.58 | 44.07
2017-12-25 05:30 | 65.31 | 40.28
2017-12-25 06:00 | 65.3 | 39.8
2017-12-25 06:30 | 65.53 | 39.82
2017-12-25 07:00 | 64.81 | 40.64
2017-12-25 07:30 | 65.66 | 40.84
2017-12-25 08:00 | 66.17 | 40.52
2017-12-25 08:30 | 68.12 | 43.66
2017-12-25 09:00 | 72.79 | 50.31
2017-12-25 09:30 | 72.8 | 49.76
2017-12-25 10:00 | 69.96 | 46.75
2017-12-25 10:30 | 70.08 | 48.16
2017-12-25 11:00 | 74.25 | 51.96
2017-12-25 11:30 | 72.7 | 51.29
2017-12-25 12:00 | 72.34 | 50.84
2017-12-25 12:30 | 72.92 | 51.77
2017-12-25 13:00 | 72.74 | 49.5
2017-12-25 13:30 | 75.44 | 53.24
2017-12-25 14:00 | 74.31 | 51.38
2017-12-25 14:30 | 76.25 | 54.08
2017-12-25 15:00 | 77.76 | 55.74
2017-12-25 15:30 | 76.18 | 53.87
2017-12-25 16:00 | 74.69 | 52.7
2017-12-25 16:30 | 73.77 | 51.94
2017-12-25 17:00 | 77.64 | 55.34
2017-12-25 17:30 | 78.53 | 56.01
2017-12-25 18:00 | 75.76 | 51.05
2017-12-25 18:30 | 70.98 | 43.87
2017-12-25 19:00 | 72.36 | 45.08
2017-12-25 19:30 | 70.77 | 42.05
2017-12-25 20:00 | 72.28 | 43.3
2017-12-25 20:30 | 75.48 | 48.89
2017-12-25 21:00 | 74.66 | 47.25
2017-12-25 21:30 | 76.74 | 51.58
2017-12-25 22:00 | 77.33 | 53.17
2017-12-25 22:30 | 75.16 | 49.49
2017-12-25 23:00 | 69.5 | 43.08
2017-12-25 23:30 | 68.24 | 41.14
2017-12-26 | 62.66 | 35.24
2017-12-26 00:30 | 61.07 | 33.85
2017-12-26 01:00 | 61.96 | 35.57
2017-12-26 01:30 | 64.23 | 39.23
2017-12-26 02:00 | 63.59 | 38.96
2017-12-26 02:30 | 61.11 | 35.62
2017-12-26 03:00 | 59.28 | 34.18
2017-12-26 03:30 | 61.18 | 35.64
2017-12-26 04:00 | 61.54 | 35.31
2017-12-26 04:30 | 62.13 | 35.4
2017-12-26 05:00 | 61.35 | 35.2
2017-12-26 05:30 | 60.68 | 33.82
2017-12-26 06:00 | 59.48 | 32.77
2017-12-26 06:30 | 62.9 | 37.57
2017-12-26 07:00 | 67.27 | 44.61
2017-12-26 07:30 | 67.24 | 45.36
2017-12-26 08:00 | 67.84 | 45.78
2017-12-26 08:30 | 71.16 | 49.3
2017-12-26 09:00 | 74.32 | 53.44
2017-12-26 09:30 | 74.63 | 53.92
2017-12-26 10:00 | 75.94 | 52.59
2017-12-26 10:30 | 76.33 | 52.58
2017-12-26 11:00 | 77.28 | 53.05
2017-12-26 11:30 | 75.66 | 51.62
2017-12-26 12:00 | 76.85 | 51.28
2017-12-26 12:30 | 76.51 | 50.41
2017-12-26 13:00 | 77.87 | 52.05
2017-12-26 13:30 | 79.34 | 54.83
2017-12-26 14:00 | 82.81 | 57.33
2017-12-26 14:30 | 85.52 | 60.82
2017-12-26 15:00 | 85.19 | 61.15
2017-12-26 15:30 | 82.06 | 57.32
2017-12-26 16:00 | 84.79 | 59.6
2017-12-26 16:30 | 86.12 | 60.48
2017-12-26 17:00 | 83.85 | 57.7
2017-12-26 17:30 | 83.03 | 56.87
2017-12-26 18:00 | 87.67 | 61.83
2017-12-26 18:30 | 92.25 | 64.14
2017-12-26 19:00 | 87.74 | 61.76
2017-12-26 19:30 | 105.57 | 77.94
2017-12-26 20:00 | 111.44 | 80.73
2017-12-26 20:30 | 115.64 | 83.91
2017-12-26 21:00 | 116.05 | 84.78
2017-12-26 21:30 | 117.51 | 88.82
2017-12-26 22:00 | 117.89 | 89.65
2017-12-26 22:30 | 114.38 | 87.85
2017-12-26 23:00 | 105.55 | 79.78
2017-12-26 23:30 | 111.82 | 88.18
2017-12-27 | 108.97 | 85.61
2017-12-27 00:30 | 109.43 | 83.47
2017-12-27 01:00 | 105.36 | 79.39
2017-12-27 01:30 | 96.92 | 73.08
2017-12-27 02:00 | 90.34 | 68.17
2017-12-27 02:30 | 104.07 | 80.5
2017-12-27 03:00 | 117.02 | 93.49
2017-12-27 03:30 | 112.66 | 88.08
2017-12-27 04:00 | 104.01 | 78.46
2017-12-27 04:30 | 108.06 | 82.74
2017-12-27 05:00 | 108.08 | 80.69
2017-12-27 05:30 | 111.2 | 84.16
2017-12-27 06:00 | 108.99 | 79.49
2017-12-27 06:30 | 108.7 | 78.4
2017-12-27 07:00 | 107.45 | 77.03
2017-12-27 07:30 | 111.44 | 84.31
2017-12-27 08:00 | 109.58 | 81.37
2017-12-27 08:30 | 112.46 | 83.47
2017-12-27 09:00 | 117.68 | 88.73
2017-12-27 09:30 | 123.91 | 95.01
2017-12-27 10:00 | 124.4 | 95.83
2017-12-27 10:30 | 120.33 | 92.81
2017-12-27 11:00 | 125.42 | 98.01
2017-12-27 11:30 | 123.34 | 96.72
2017-12-27 12:00 | 118.59 | 90.44
2017-12-27 12:30 | 121.28 | 93.7
2017-12-27 13:00 | 127.07 | 99.58
2017-12-27 13:30 | 125.38 | 98.46
2017-12-27 14:00 | 129.53 | 103.44
2017-12-27 14:30 | 121.88 | 95.32
2017-12-27 15:00 | 115.77 | 89.48
2017-12-27 15:30 | 118.6 | 94.3
2017-12-27 16:00 | 124.15 | 99.56
2017-12-27 16:30 | 114.64 | 88.79
2017-12-27 17:00 | 131.16 | 104.73
2017-12-27 17:30 | 135.05 | 107.03
2017-12-27 18:00 | 135.81 | 107.64
2017-12-27 18:30 | 127.85 | 98.64
2017-12-27 19:00 | 125.55 | 96.78
2017-12-27 19:30 | 130.32 | 100.29
2017-12-27 20:00 | 131.15 | 101.64
2017-12-27 20:30 | 125.06 | 95.94
2017-12-27 21:00 | 128.03 | 99.47
2017-12-27 21:30 | 135.74 | 108.63
2017-12-27 22:00 | 127.35 | 99.57
2017-12-27 22:30 | 133.85 | 108.51
2017-12-27 23:00 | 132.29 | 106.65
2017-12-27 23:30 | 128.25 | 102.24
2017-12-28 | 128.11 | 101.77
2017-12-28 00:30 | 129.62 | 104.23
2017-12-28 01:00 | 129 | 103.24
2017-12-28 01:30 | 124.29 | 97.09
2017-12-28 02:00 | 119.71 | 92.84
2017-12-28 02:30 | 117.67 | 91.34
2017-12-28 03:00 | 119.64 | 94.34
2017-12-28 03:30 | 127.25 | 102.88
2017-12-28 04:00 | 122.82 | 97.55
2017-12-28 04:30 | 120.96 | 94.2
2017-12-28 05:00 | 126.6 | 99.89
2017-12-28 05:30 | 123.6 | 96.76
2017-12-28 06:00 | 127.28 | 101.56
2017-12-28 06:30 | 116.26 | 87.37
2017-12-28 07:00 | 115.57 | 86.93
2017-12-28 07:30 | 119.79 | 89.7
2017-12-28 08:00 | 123.22 | 91.48
2017-12-28 08:30 | 124.94 | 94.16
2017-12-28 09:00 | 123.92 | 92.34
2017-12-28 09:30 | 121.82 | 91.09
2017-12-28 10:00 | 122.31 | 91.24
2017-12-28 10:30 | 128.03 | 99.36
2017-12-28 11:00 | 131.49 | 103.66
2017-12-28 11:30 | 130.74 | 103.9
2017-12-28 12:00 | 130.42 | 103.24
2017-12-28 12:30 | 124.44 | 96.8
2017-12-28 13:00 | 127.33 | 99.42
2017-12-28 13:30 | 125.31 | 97.55
2017-12-28 14:00 | 129.04 | 102.11
2017-12-28 14:30 | 125.06 | 99.03
2017-12-28 15:00 | 132.08 | 105.03
2017-12-28 15:30 | 124.79 | 98.75
2017-12-28 16:00 | 123.32 | 96.97
2017-12-28 16:30 | 126.23 | 99.62
2017-12-28 17:00 | 118.94 | 92.36
2017-12-28 17:30 | 126 | 100.26
2017-12-28 18:00 | 124.71 | 99.54
2017-12-28 18:30 | 120.5 | 92.57
2017-12-28 19:00 | 124.01 | 95.9
2017-12-28 19:30 | 129.77 | 99.56
2017-12-28 20:00 | 130.51 | 100.2
2017-12-28 20:30 | 132.4 | 103.44
2017-12-28 21:00 | 138.31 | 110.25
2017-12-28 21:30 | 132.28 | 103.11
2017-12-28 22:00 | 132.68 | 105.27
2017-12-28 22:30 | 133.27 | 104.84
2017-12-28 23:00 | 130.13 | 101.91
2017-12-28 23:30 | 128.31 | 101.11
2017-12-29 | 121.31 | 91.78
2017-12-29 00:30 | 124.35 | 93.63
2017-12-29 01:00 | 131.78 | 104.79
2017-12-29 01:30 | 121.02 | 95.15
2017-12-29 02:00 | 126.04 | 99.78
2017-12-29 02:30 | 123.04 | 97
2017-12-29 03:00 | 125.92 | 98.8
2017-12-29 03:30 | 119.41 | 91.7
2017-12-29 04:00 | 122.49 | 95.3
2017-12-29 04:30 | 122.26 | 95.06
2017-12-29 05:00 | 123.97 | 96.12
2017-12-29 05:30 | 124.3 | 96.17
2017-12-29 06:00 | 124.04 | 96.85
2017-12-29 06:30 | 113.64 | 86.31
2017-12-29 07:00 | 118.97 | 93.18
2017-12-29 07:30 | 122.44 | 97.02
2017-12-29 08:00 | 118.41 | 91.58
2017-12-29 08:30 | 115.74 | 89.26
2017-12-29 09:00 | 117.79 | 89.66
2017-12-29 09:30 | 119.24 | 91.25
2017-12-29 10:00 | 123.17 | 95.19
2017-12-29 10:30 | 130.35 | 100.99
2017-12-29 11:00 | 124.47 | 94.78
2017-12-29 11:30 | 117.2 | 87.55
2017-12-29 12:00 | 122.27 | 94.18
2017-12-29 12:30 | 121.27 | 96.44
2017-12-29 13:00 | 129.43 | 103.76
2017-12-29 13:30 | 128.6 | 102.18
2017-12-29 14:00 | 125.35 | 98.39
2017-12-29 14:30 | 123.14 | 95.87
2017-12-29 15:00 | 117.51 | 89.77
2017-12-29 15:30 | 117.72 | 91.43
2017-12-29 16:00 | 128.05 | 99.49
2017-12-29 16:30 | 117.11 | 90.51
2017-12-29 17:00 | 117.36 | 90.28
2017-12-29 17:30 | 119.4 | 91.93
2017-12-29 18:00 | 127.19 | 99.84
2017-12-29 18:30 | 121.89 | 92.62
2017-12-29 19:00 | 127.83 | 100.46
2017-12-29 19:30 | 127.25 | 98.61
2017-12-29 20:00 | 127.37 | 97.59
2017-12-29 20:30 | 127.73 | 95.91
2017-12-29 21:00 | 130.19 | 99.32
2017-12-29 21:30 | 133.36 | 102.68
2017-12-29 22:00 | 129.26 | 99.38
2017-12-29 22:30 | 128.53 | 99.11
2017-12-29 23:00 | 123.02 | 94.29
2017-12-29 23:30 | 124.04 | 96.25
2017-12-30 | 122.68 | 94.76
2017-12-30 00:30 | 120.26 | 92.7
2017-12-30 01:00 | 116.1 | 87.88
2017-12-30 01:30 | 113.77 | 85.47
2017-12-30 02:00 | 121.03 | 94.06
2017-12-30 02:30 | 120.33 | 93.12
2017-12-30 03:00 | 122.44 | 96.07
2017-12-30 03:30 | 121.68 | 95.39
2017-12-30 04:00 | 121.08 | 95.39
2017-12-30 04:30 | 123.76 | 98.98
2017-12-30 05:00 | 121.74 | 96.91
2017-12-30 05:30 | 124.61 | 99.41
2017-12-30 06:00 | 118.19 | 92.81
2017-12-30 06:30 | 116.66 | 90.04
2017-12-30 07:00 | 112.39 | 86.64
2017-12-30 07:30 | 121.18 | 95.43
2017-12-30 08:00 | 123.15 | 96.61
2017-12-30 08:30 | 113.02 | 85.98
2017-12-30 09:00 | 116.77 | 89.11
2017-12-30 09:30 | 114.66 | 87.66
2017-12-30 10:00 | 125.55 | 100.74
2017-12-30 10:30 | 124.93 | 100.22
2017-12-30 11:00 | 115.27 | 89.42
2017-12-30 11:30 | 121.95 | 95.64
2017-12-30 12:00 | 120.36 | 93.99
2017-12-30 12:30 | 125.3 | 99.11
2017-12-30 13:00 | 126.99 | 100.2
2017-12-30 13:30 | 130.74 | 104.13
2017-12-30 14:00 | 134.03 | 107.77
2017-12-30 14:30 | 130.58 | 103.36
2017-12-30 15:00 | 122.27 | 95.91
2017-12-30 15:30 | 122.9 | 96.01
2017-12-30 16:00 | 121.9 | 95.42
2017-12-30 16:30 | 126.3 | 99.28
2017-12-30 17:00 | 131.46 | 103.78
2017-12-30 17:30 | 131.03 | 103.64
2017-12-30 18:00 | 133.66 | 105.91
2017-12-30 18:30 | 127.91 | 100.13
2017-12-30 19:00 | 130.41 | 102.5
2017-12-30 19:30 | 134.27 | 106.34
2017-12-30 20:00 | 133.62 | 105.62
2017-12-30 20:30 | 125.61 | 96.46
2017-12-30 21:00 | 125.88 | 96.4
2017-12-30 21:30 | 127.2 | 98.92
2017-12-30 22:00 | 125.11 | 97.93
2017-12-30 22:30 | 125.98 | 98.66
2017-12-30 23:00 | 119.27 | 91.56
2017-12-30 23:30 | 112.9 | 85
2017-12-31 | 114.54 | 87.69
2017-12-31 00:30 | 115.67 | 89.79
2017-12-31 01:00 | 118.68 | 93.35
2017-12-31 01:30 | 122.15 | 97.12
2017-12-31 02:00 | 123.42 | 98.73
2017-12-31 02:30 | 119.37 | 94.33
2017-12-31 03:00 | 114.65 | 89.33
2017-12-31 03:30 | 119.17 | 94.06
2017-12-31 04:00 | 116.68 | 91.59
2017-12-31 04:30 | 122.02 | 97.09
2017-12-31 05:00 | 120.32 | 96.24
2017-12-31 05:30 | 115.75 | 91.4
2017-12-31 06:00 | 111.68 | 87.37
2017-12-31 06:30 | 112.19 | 86.02
2017-12-31 07:00 | 114.52 | 90.59
2017-12-31 07:30 | 127.16 | 103.73
2017-12-31 08:00 | 126.07 | 100.37
2017-12-31 08:30 | 114.4 | 91.23
2017-12-31 09:00 | 110.95 | 88.43
2017-12-31 09:30 | 111.78 | 88.31
2017-12-31 10:00 | 120.96 | 97.6
2017-12-31 10:30 | 123.57 | 100.67
2017-12-31 11:00 | 124.79 | 102.43
2017-12-31 11:30 | 116.24 | 93.39
2017-12-31 12:00 | 121.06 | 97.55
2017-12-31 12:30 | 124.32 | 100.09
2017-12-31 13:00 | 128.88 | 100.18
2017-12-31 13:30 | 137.97 | 108.83
2017-12-31 14:00 | 135.85 | 107.65
2017-12-31 14:30 | 126.39 | 97.77
2017-12-31 15:00 | 128.31 | 98.81
2017-12-31 15:30 | 130.95 | 100.58
2017-12-31 16:00 | 129.58 | 98.36
2017-12-31 16:30 | 132.66 | 102.49
2017-12-31 17:00 | 127.23 | 98.24
2017-12-31 17:30 | 127.86 | 96.97
2017-12-31 18:00 | 131.27 | 101.34
2017-12-31 18:30 | 126.99 | 96.83
2017-12-31 19:00 | 117.45 | 90.87
2017-12-31 19:30 | 102.6 | 79.19
2017-12-31 20:00 | 91.01 | 68.11
2017-12-31 20:30 | 96.06 | 73.73
2017-12-31 21:00 | 97.74 | 76.84
2017-12-31 21:30 | 92.23 | 70.73
2017-12-31 22:00 | 94.94 | 74.92
2017-12-31 22:30 | 91.29 | 72.94
2017-12-31 23:00 | 89.73 | 70.86
2017-12-31 23:30 | 95.56 | 77.1
2018-01-01 | 89.44 | 71.67
2018-01-01 00:30 | 85.88 | 68.24
2018-01-01 01:00 | 84.93 | 67.21
2018-01-01 01:30 | 83.32 | 65.72
2018-01-01 02:00 | 79.74 | 61.96
2018-01-01 02:30 | 81.65 | 64
2018-01-01 03:00 | 84.47 | 66.28
2018-01-01 03:30 | 84.73 | 67.56
2018-01-01 04:00 | 88.06 | 71.27
2018-01-01 04:30 | 89.74 | 72.76
2018-01-01 05:00 | 85.39 | 68.26
2018-01-01 05:30 | 99.03 | 83.05
2018-01-01 06:00 | 95.32 | 78.74
2018-01-01 06:30 | 87.85 | 68.67
2018-01-01 07:00 | 86.77 | 68.48
2018-01-01 07:30 | 90.91 | 72.73
2018-01-01 08:00 | 96.01 | 78.23
2018-01-01 08:30 | 95.44 | 75.69
2018-01-01 09:00 | 96.33 | 75.09
2018-01-01 09:30 | 108.16 | 88.43
2018-01-01 10:00 | 106.49 | 85.5
2018-01-01 10:30 | 111.72 | 90.37
2018-01-01 11:00 | 107.46 | 84.07
2018-01-01 11:30 | 106.72 | 84.73
2018-01-01 12:00 | 108.01 | 85.41
2018-01-01 12:30 | 110.29 | 88.28
2018-01-01 13:00 | 119.51 | 97.11
2018-01-01 13:30 | 120.11 | 97.82
2018-01-01 14:00 | 121.13 | 99.27
2018-01-01 14:30 | 121.64 | 100.07
2018-01-01 15:00 | 118.47 | 96.92
2018-01-01 15:30 | 118.01 | 97.32
2018-01-01 16:00 | 121.47 | 100.82
2018-01-01 16:30 | 127.73 | 107.25
2018-01-01 17:00 | 131.83 | 112.18
2018-01-01 17:30 | 123.44 | 103.1
2018-01-01 18:00 | 124.21 | 104.55
2018-01-01 18:30 | 118.95 | 98.66
2018-01-01 19:00 | 119.36 | 100.29
2018-01-01 19:30 | 118.69 | 98.85
2018-01-01 20:00 | 112.39 | 92.05
2018-01-01 20:30 | 113.34 | 93.44
2018-01-01 21:00 | 105.79 | 86.59
2018-01-01 21:30 | 111.53 | 91.16
2018-01-01 22:00 | 108.9 | 88.44
2018-01-01 22:30 | 107.52 | 86.46
2018-01-01 23:00 | 109.65 | 90.4
2018-01-01 23:30 | 107.48 | 88.81
2018-01-02 | 104.89 | 87.14
2018-01-02 00:30 | 104.46 | 86.56
2018-01-02 01:00 | 105.51 | 88.4
2018-01-02 01:30 | 107.37 | 89.2
2018-01-02 02:00 | 102.1 | 84.34
2018-01-02 02:30 | 99.77 | 83.06
2018-01-02 03:00 | 100.81 | 84.49
2018-01-02 03:30 | 100.54 | 85.43
2018-01-02 04:00 | 101.98 | 86.9
2018-01-02 04:30 | 104.17 | 86.86
2018-01-02 05:00 | 98.96 | 81.05
2018-01-02 05:30 | 101.69 | 83.84
2018-01-02 06:00 | 99.94 | 82.63
2018-01-02 06:30 | 93.73 | 71.87
2018-01-02 07:00 | 100.72 | 79.76
2018-01-02 07:30 | 103.28 | 82.41
2018-01-02 08:00 | 107.38 | 87.51
2018-01-02 08:30 | 107.8 | 88.28
2018-01-02 09:00 | 105.61 | 84.11
2018-01-02 09:30 | 110.04 | 89.41
2018-01-02 10:00 | 110.51 | 88.22
2018-01-02 10:30 | 113.96 | 91.54
2018-01-02 11:00 | 115.36 | 93.74
2018-01-02 11:30 | 117.24 | 96.25
2018-01-02 12:00 | 113.07 | 91.78
2018-01-02 12:30 | 114.53 | 94.57
2018-01-02 13:00 | 115.83 | 97.48
2018-01-02 13:30 | 110.81 | 89.99
2018-01-02 14:00 | 109.84 | 89
2018-01-02 14:30 | 118.76 | 98.82
2018-01-02 15:00 | 120.28 | 99.95
2018-01-02 15:30 | 120.41 | 98.79
2018-01-02 16:00 | 123.3 | 99.21
2018-01-02 16:30 | 117.09 | 92.32
2018-01-02 17:00 | 112.7 | 85.93
2018-01-02 17:30 | 101.68 | 76.14
2018-01-02 18:00 | 103.83 | 79.6
2018-01-02 18:30 | 98.01 | 73.88
2018-01-02 19:00 | 102.92 | 81.14
2018-01-02 19:30 | 109.53 | 86.62
2018-01-02 20:00 | 110 | 92.76
2018-01-02 20:30 | 109.48 | 90.99
2018-01-02 21:00 | 104.63 | 84.27
2018-01-02 21:30 | 111.25 | 91.14
2018-01-02 22:00 | 107.65 | 89.28
2018-01-02 22:30 | 103.38 | 85.04
2018-01-02 23:00 | 96.79 | 78.46
2018-01-02 23:30 | 97.27 | 79.43
2018-01-03 | 99.89 | 82.94
2018-01-03 00:30 | 108.71 | 91.01
2018-01-03 01:00 | 107.55 | 89.26
2018-01-03 01:30 | 103.54 | 85.13
2018-01-03 02:00 | 103.36 | 85.64
2018-01-03 02:30 | 107.89 | 91.06
2018-01-03 03:00 | 103.04 | 85.26
2018-01-03 03:30 | 107.6 | 87.73
2018-01-03 04:00 | 113.95 | 94.03
2018-01-03 04:30 | 116.48 | 98.39
2018-01-03 05:00 | 123.76 | 106.61
2018-01-03 05:30 | 123.73 | 106.82
2018-01-03 06:00 | 111.92 | 94.84
2018-01-03 06:30 | 105.67 | 86.82
2018-01-03 07:00 | 107.99 | 89.13
2018-01-03 07:30 | 111.06 | 92.2
2018-01-03 08:00 | 113.8 | 95.42
2018-01-03 08:30 | 118.28 | 97.81
2018-01-03 09:00 | 117.66 | 94.55
2018-01-03 09:30 | 116.55 | 94.1
2018-01-03 10:00 | 128.07 | 107.6
2018-01-03 10:30 | 129.24 | 108.91
2018-01-03 11:00 | 125.84 | 104.13
2018-01-03 11:30 | 120.15 | 97.54
2018-01-03 12:00 | 125.82 | 103.81
2018-01-03 12:30 | 120.86 | 98.29
2018-01-03 13:00 | 124.99 | 101.74
2018-01-03 13:30 | 124 | 102.69
2018-01-03 14:00 | 113.62 | 95.08
2018-01-03 14:30 | 110.59 | 89.85
2018-01-03 15:00 | 116.82 | 94.17
2018-01-03 15:30 | 122.8 | 99.75
2018-01-03 16:00 | 118.59 | 94.6
2018-01-03 16:30 | 121.06 | 97.04
2018-01-03 17:00 | 121.85 | 97.52
2018-01-03 17:30 | 106.52 | 88.19
2018-01-03 18:00 | 102.79 | 86.25
2018-01-03 18:30 | 100.31 | 83.18
2018-01-03 19:00 | 100.68 | 84.37
2018-01-03 19:30 | 109.15 | 92.51
2018-01-03 20:00 | 115.7 | 98.88
2018-01-03 20:30 | 111.08 | 93.78
2018-01-03 21:00 | 107.2 | 90.82
2018-01-03 21:30 | 98.34 | 82.6
2018-01-03 22:00 | 106.73 | 90.68
2018-01-03 22:30 | 118.41 | 99.99
2018-01-03 23:00 | 117.54 | 98.51
2018-01-03 23:30 | 119.3 | 100.59
2018-01-04 | 118.5 | 98.05
2018-01-04 00:30 | 119.15 | 98.38
2018-01-04 01:00 | 118.8 | 99.74
2018-01-04 01:30 | 124.42 | 106.06
2018-01-04 02:00 | 121.7 | 102.74
2018-01-04 02:30 | 117.69 | 99.09
2018-01-04 03:00 | 118.5 | 100.4
2018-01-04 03:30 | 114.74 | 96.74
2018-01-04 04:00 | 112.59 | 94.48
2018-01-04 04:30 | 117.29 | 99.45
2018-01-04 05:00 | 116.28 | 100.98
2018-01-04 05:30 | 116.59 | 99.61
2018-01-04 06:00 | 119.71 | 100.84
2018-01-04 06:30 | 109.8 | 89.56
2018-01-04 07:00 | 107.49 | 89.15
2018-01-04 07:30 | 97.93 | 79.87
2018-01-04 08:00 | 107.01 | 88.35
2018-01-04 08:30 | 103.45 | 82.72
2018-01-04 09:00 | 109.74 | 89.7
2018-01-04 09:30 | 113.58 | 94.29
2018-01-04 10:00 | 104.56 | 84.88
2018-01-04 10:30 | 101.52 | 81.07
2018-01-04 11:00 | 104.73 | 85.41
2018-01-04 11:30 | 106.62 | 88.68
2018-01-04 12:00 | 97.42 | 81.22
2018-01-04 12:30 | 97.92 | 82.67
2018-01-04 13:00 | 107.15 | 91.94
2018-01-04 13:30 | 103.56 | 87.65
2018-01-04 14:00 | 96.11 | 79.2
2018-01-04 14:30 | 95.88 | 77.54
2018-01-04 15:00 | 96.06 | 75.98
2018-01-04 15:30 | 95.18 | 74.65
2018-01-04 16:00 | 93.86 | 74.89
2018-01-04 16:30 | 104.66 | 87.39
2018-01-04 17:00 | 112.84 | 94.22
2018-01-04 17:30 | 115.09 | 96.55
2018-01-04 18:00 | 111.95 | 92.78
2018-01-04 18:30 | 103.75 | 84.42
2018-01-04 19:00 | 105.19 | 86.51
2018-01-04 19:30 | 101.32 | 82.96
2018-01-04 20:00 | 102.11 | 86.4
2018-01-04 20:30 | 97.93 | 82.93
2018-01-04 21:00 | 94.04 | 80.21
2018-01-04 21:30 | 95.51 | 82.13
2018-01-04 22:00 | 102.73 | 89.72
2018-01-04 22:30 | 104.3 | 90.96
2018-01-04 23:00 | 103.02 | 88.66
2018-01-04 23:30 | 106.39 | 91.26
2018-01-05 | 105.79 | 89.21
2018-01-05 00:30 | 115.73 | 99.47
2018-01-05 01:00 | 112.4 | 96.15
2018-01-05 01:30 | 119.36 | 103.74
2018-01-05 02:00 | 121.3 | 105.87
2018-01-05 02:30 | 126.43 | 110.46
2018-01-05 03:00 | 119.25 | 103.26
2018-01-05 03:30 | 111.84 | 95.26
2018-01-05 04:00 | 107.85 | 92.28
2018-01-05 04:30 | 115.26 | 100.45
2018-01-05 05:00 | 113.98 | 99.02
2018-01-05 05:30 | 102.69 | 88.42
2018-01-05 06:00 | 105.84 | 91.59
2018-01-05 06:30 | 97.69 | 80.98
2018-01-05 07:00 | 103.1 | 86.72
2018-01-05 07:30 | 101.42 | 85.89
2018-01-05 08:00 | 98.79 | 81.83
2018-01-05 08:30 | 104.93 | 87.04
2018-01-05 09:00 | 111.98 | 93.56
2018-01-05 09:30 | 115.98 | 98.56
2018-01-05 10:00 | 113.68 | 97.61
2018-01-05 10:30 | 116.01 | 99.36
2018-01-05 11:00 | 116.99 | 100.72
2018-01-05 11:30 | 114.4 | 95.78
2018-01-05 12:00 | 117.82 | 100.09
2018-01-05 12:30 | 113.09 | 95.84
2018-01-05 13:00 | 122.21 | 104.36
2018-01-05 13:30 | 120.74 | 102.06
2018-01-05 14:00 | 119.75 | 100.3
2018-01-05 14:30 | 115.39 | 95.42
2018-01-05 15:00 | 118.76 | 98.93
2018-01-05 15:30 | 111.73 | 92.17
2018-01-05 16:00 | 113.49 | 94.5
2018-01-05 16:30 | 114.11 | 95.57
2018-01-05 17:00 | 118.43 | 101.12
2018-01-05 17:30 | 120.27 | 104.18
2018-01-05 18:00 | 127.14 | 111.61
2018-01-05 18:30 | 109.24 | 92.73
2018-01-05 19:00 | 110.21 | 94.73
2018-01-05 19:30 | 101.92 | 86.49
2018-01-05 20:00 | 104.2 | 89.14
2018-01-05 20:30 | 103.67 | 89.35
2018-01-05 21:00 | 108.17 | 94.95
2018-01-05 21:30 | 104.46 | 90.98
2018-01-05 22:00 | 110.94 | 97.12
2018-01-05 22:30 | 106.4 | 92.21
2018-01-05 23:00 | 116.56 | 100.72
2018-01-05 23:30 | 104.12 | 89.88
2018-01-06 | 103.45 | 88.59
2018-01-06 00:30 | 108.26 | 92.8
2018-01-06 01:00 | 102.56 | 87.44
2018-01-06 01:30 | 105.16 | 91.1
2018-01-06 02:00 | 102.61 | 88.83
2018-01-06 02:30 | 105.65 | 90.4
2018-01-06 03:00 | 103.15 | 88.35
2018-01-06 03:30 | 106.38 | 92.71
2018-01-06 04:00 | 99.17 | 85.29
2018-01-06 04:30 | 108.21 | 94.15
2018-01-06 05:00 | 107.43 | 94.35
2018-01-06 05:30 | 105.33 | 92.83
2018-01-06 06:00 | 103.53 | 91.01
2018-01-06 06:30 | 101.62 | 88.08
2018-01-06 07:00 | 104.9 | 91.61
2018-01-06 07:30 | 108.27 | 94.31
2018-01-06 08:00 | 102.37 | 88.11
2018-01-06 08:30 | 104.53 | 89.15
2018-01-06 09:00 | 105.4 | 91.75
2018-01-06 09:30 | 100.38 | 86.51
2018-01-06 10:00 | 110.95 | 96.94
2018-01-06 10:30 | 98.97 | 85.37
2018-01-06 11:00 | 105.74 | 90.85
2018-01-06 11:30 | 108.54 | 93.91
2018-01-06 12:00 | 109.31 | 94.7
2018-01-06 12:30 | 106.57 | 92.15
2018-01-06 13:00 | 107.99 | 93.71
2018-01-06 13:30 | 105.46 | 90.07
2018-01-06 14:00 | 125.71 | 108.8
2018-01-06 14:30 | 117.76 | 100.93
2018-01-06 15:00 | 121.65 | 102.67
2018-01-06 15:30 | 121.84 | 102.16
2018-01-06 16:00 | 117.03 | 95.99
2018-01-06 16:30 | 119.56 | 98.73
2018-01-06 17:00 | 118.91 | 97.06
2018-01-06 17:30 | 124.2 | 105.28
2018-01-06 18:00 | 120.54 | 101.33
2018-01-06 18:30 | 121.05 | 100.59
2018-01-06 19:00 | 120.95 | 101.94
2018-01-06 19:30 | 123.22 | 104.34
2018-01-06 20:00 | 120.84 | 100.51
2018-01-06 20:30 | 127.47 | 107.05
2018-01-06 21:00 | 126.55 | 107.83
2018-01-06 21:30 | 125.53 | 107.07
2018-01-06 22:00 | 119.04 | 100.28
2018-01-06 22:30 | 114.8 | 96.34
2018-01-06 23:00 | 122.59 | 105.16
2018-01-06 23:30 | 121.61 | 104.71
2018-01-07 | 128.47 | 111.2
2018-01-07 00:30 | 121.23 | 103.78
2018-01-07 01:00 | 117.19 | 100.26
2018-01-07 01:30 | 124.68 | 108.17
2018-01-07 02:00 | 125.74 | 109.06
2018-01-07 02:30 | 123.52 | 107.18
2018-01-07 03:00 | 119.58 | 103.22
2018-01-07 03:30 | 122.81 | 105.74
2018-01-07 04:00 | 121.47 | 105.55
2018-01-07 04:30 | 120.15 | 104.96
2018-01-07 05:00 | 128.92 | 113.64
2018-01-07 05:30 | 129.5 | 114.56
2018-01-07 06:00 | 119.22 | 104.7
2018-01-07 06:30 | 106.63 | 90.42
2018-01-07 07:00 | 125.47 | 110.47
2018-01-07 07:30 | 119.01 | 104.05
2018-01-07 08:00 | 113.17 | 96.78
2018-01-07 08:30 | 124.78 | 109.19
2018-01-07 09:00 | 118.95 | 102.13
2018-01-07 09:30 | 105.89 | 88.28
2018-01-07 10:00 | 109.14 | 90.7
2018-01-07 10:30 | 118.26 | 100.36
2018-01-07 11:00 | 117.76 | 101.27
2018-01-07 11:30 | 118.06 | 100.36
2018-01-07 12:00 | 122.75 | 105.63
2018-01-07 12:30 | 116.66 | 98.61
2018-01-07 13:00 | 123.08 | 105.41
2018-01-07 13:30 | 124.54 | 105.98
2018-01-07 14:00 | 120.5 | 100.98
2018-01-07 14:30 | 131.33 | 112.42
2018-01-07 15:00 | 127.73 | 108.87
2018-01-07 15:30 | 123.23 | 103.63
2018-01-07 16:00 | 122.15 | 102
2018-01-07 16:30 | 121.26 | 100.44
2018-01-07 17:00 | 123.89 | 104.56
2018-01-07 17:30 | 130.23 | 110.59
2018-01-07 18:00 | 133.85 | 114.56
2018-01-07 18:30 | 130.72 | 109.2
2018-01-07 19:00 | 134.62 | 112.9
2018-01-07 19:30 | 132.23 | 109.09
2018-01-07 20:00 | 137.31 | 115.19
2018-01-07 20:30 | 130.07 | 108.74
2018-01-07 21:00 | 129.38 | 108.51
2018-01-07 21:30 | 138.34 | 118.68
2018-01-07 22:00 | 129.25 | 110.97
2018-01-07 22:30 | 133.26 | 115.91
2018-01-07 23:00 | 131.03 | 112.99
2018-01-07 23:30 | 125.62 | 108.02
2018-01-08 | 125.29 | 107.5
2018-01-08 00:30 | 122.25 | 103.95
2018-01-08 01:00 | 125.02 | 107.05
2018-01-08 01:30 | 122.18 | 104.59
2018-01-08 02:00 | 124.97 | 107.99
2018-01-08 02:30 | 124.44 | 107.93
2018-01-08 03:00 | 121.99 | 105.43
2018-01-08 03:30 | 119.99 | 101.92
2018-01-08 04:00 | 118.83 | 102.94
2018-01-08 04:30 | 120.15 | 103.59
2018-01-08 05:00 | 114.93 | 98.37
2018-01-08 05:30 | 123.44 | 107.36
2018-01-08 06:00 | 128.72 | 112.78
2018-01-08 06:30 | 112.43 | 94.85
2018-01-08 07:00 | 112.87 | 95.46
2018-01-08 07:30 | 118.9 | 100.98
2018-01-08 08:00 | 124.58 | 106.75
2018-01-08 08:30 | 121.14 | 102.41
2018-01-08 09:00 | 116.88 | 96.97
2018-01-08 09:30 | 117.32 | 97.84
2018-01-08 10:00 | 122.72 | 104.26
2018-01-08 10:30 | 127.28 | 108.62
2018-01-08 11:00 | 119.64 | 100.19
2018-01-08 11:30 | 120.08 | 101.35
2018-01-08 12:00 | 115.24 | 96.82
2018-01-08 12:30 | 121.74 | 102.98
2018-01-08 13:00 | 127.25 | 109.76
2018-01-08 13:30 | 127.56 | 109.89
2018-01-08 14:00 | 128.78 | 110.56
2018-01-08 14:30 | 122.95 | 104.57
2018-01-08 15:00 | 122.89 | 104.18
2018-01-08 15:30 | 113.11 | 98.19
2018-01-08 16:00 | 115.06 | 99.88
2018-01-08 16:30 | 114.76 | 99.75
2018-01-08 17:00 | 110.88 | 94.21
2018-01-08 17:30 | 113.31 | 96.87
2018-01-08 18:00 | 112.65 | 97.82
2018-01-08 18:30 | 110.16 | 92.69
2018-01-08 19:00 | 114.8 | 98.38
2018-01-08 19:30 | 119.36 | 103.21
2018-01-08 20:00 | 116.85 | 101.84
2018-01-08 20:30 | 124.5 | 109.18
2018-01-08 21:00 | 114.77 | 99.11
2018-01-08 21:30 | 126.76 | 112.12
2018-01-08 22:00 | 133.05 | 119.04
2018-01-08 22:30 | 121.97 | 107.46
2018-01-08 23:00 | 117.28 | 103.08
2018-01-08 23:30 | 112.34 | 97.58
2018-01-09 | 111.17 | 96.4
2018-01-09 00:30 | 112.83 | 98.72
2018-01-09 01:00 | 111.18 | 96.31
2018-01-09 01:30 | 114.44 | 100.61
2018-01-09 02:00 | 113.43 | 98.64
2018-01-09 02:30 | 127.72 | 113.36
2018-01-09 03:00 | 120.27 | 105.18
2018-01-09 03:30 | 112.16 | 95.37
2018-01-09 04:00 | 111.06 | 95.12
2018-01-09 04:30 | 117.93 | 102.79
2018-01-09 05:00 | 127.5 | 113.28
2018-01-09 05:30 | 114.76 | 100.02
2018-01-09 06:00 | 111.1 | 96.19
2018-01-09 06:30 | 112.39 | 95.99
2018-01-09 07:00 | 106.75 | 89.37
2018-01-09 07:30 | 109.43 | 92.44
2018-01-09 08:00 | 108.05 | 91.93
2018-01-09 08:30 | 103.61 | 86.51
2018-01-09 09:00 | 108.98 | 90.99
2018-01-09 09:30 | 106.11 | 87.13
2018-01-09 10:00 | 98.09 | 81.29
2018-01-09 10:30 | 96.35 | 77.73
2018-01-09 11:00 | 97.86 | 78.26
2018-01-09 11:30 | 102.1 | 81.09
2018-01-09 12:00 | 113.81 | 94.88
2018-01-09 12:30 | 118.62 | 99.32
2018-01-09 13:00 | 117.39 | 99.56
2018-01-09 13:30 | 111.06 | 92.95
2018-01-09 14:00 | 114.35 | 97.47
2018-01-09 14:30 | 115.04 | 98.76
2018-01-09 15:00 | 112.95 | 95.18
2018-01-09 15:30 | 107.29 | 89.99
2018-01-09 16:00 | 113.1 | 96.13
2018-01-09 16:30 | 118.74 | 101.32
2018-01-09 17:00 | 121.1 | 101.77
2018-01-09 17:30 | 118.84 | 99.19
2018-01-09 18:00 | 124.19 | 104.89
2018-01-09 18:30 | 116.61 | 96.2
2018-01-09 19:00 | 123.39 | 103.9
2018-01-09 19:30 | 125.17 | 105.68
2018-01-09 20:00 | 133.44 | 113.92
2018-01-09 20:30 | 128.79 | 110.29
2018-01-09 21:00 | 124.39 | 106.83
2018-01-09 21:30 | 127.8 | 109.82
2018-01-09 22:00 | 126.97 | 108.42
2018-01-09 22:30 | 123.84 | 104.98
2018-01-09 23:00 | 121.87 | 103.04
2018-01-09 23:30 | 125.58 | 108.56
2018-01-10 | 121.2 | 104.19
2018-01-10 00:30 | 122.97 | 105.77
2018-01-10 01:00 | 121.9 | 104.44
2018-01-10 01:30 | 121.46 | 104.17
2018-01-10 02:00 | 126.18 | 109.47
2018-01-10 02:30 | 129.52 | 113.02
2018-01-10 03:00 | 113.65 | 98.06
2018-01-10 03:30 | 105.5 | 90.02
2018-01-10 04:00 | 109.99 | 95.81
2018-01-10 04:30 | 105.33 | 91.18
2018-01-10 05:00 | 103.95 | 89.58
2018-01-10 05:30 | 110.61 | 97.02
2018-01-10 06:00 | 102.2 | 88.59
2018-01-10 06:30 | 95.95 | 80.77
2018-01-10 07:00 | 97.26 | 82.08
2018-01-10 07:30 | 109.41 | 95.31
2018-01-10 08:00 | 101.09 | 87.6
2018-01-10 08:30 | 101.92 | 89.08
2018-01-10 09:00 | 104.92 | 91.17
2018-01-10 09:30 | 93.94 | 79.51
2018-01-10 10:00 | 93.44 | 80.2
2018-01-10 10:30 | 99.67 | 86.7
2018-01-10 11:00 | 96.82 | 83.4
2018-01-10 11:30 | 87.71 | 74.57
2018-01-10 12:00 | 97.71 | 85.24
2018-01-10 12:30 | 102.15 | 88.6
2018-01-10 13:00 | 104.07 | 92.35
2018-01-10 13:30 | 110.96 | 99.38
2018-01-10 14:00 | 103.13 | 89.98
2018-01-10 14:30 | 109.69 | 96.59
2018-01-10 15:00 | 119.62 | 106.97
2018-01-10 15:30 | 119.96 | 106.65
2018-01-10 16:00 | 118.57 | 103.72
2018-01-10 16:30 | 111.04 | 97.44
2018-01-10 17:00 | 109.93 | 95.79
2018-01-10 17:30 | 116.77 | 102.59
2018-01-10 18:00 | 118.89 | 104.54
2018-01-10 18:30 | 111.44 | 96.57
2018-01-10 19:00 | 114.8 | 100.62
2018-01-10 19:30 | 121.23 | 105.82
2018-01-10 20:00 | 115.73 | 100.28
2018-01-10 20:30 | 121.68 | 106.65
2018-01-10 21:00 | 119.1 | 105.27
2018-01-10 21:30 | 115.3 | 101.47
2018-01-10 22:00 | 120.29 | 105.3
2018-01-10 22:30 | 116.28 | 102.3
2018-01-10 23:00 | 113.87 | 99.6
2018-01-10 23:30 | 114.56 | 101.12
2018-01-11 | 109.99 | 96.79
2018-01-11 00:30 | 112.72 | 99.03
2018-01-11 01:00 | 108.84 | 95.29
2018-01-11 01:30 | 106.51 | 92.9
2018-01-11 02:00 | 107.3 | 92.49
2018-01-11 02:30 | 108.69 | 93.47
2018-01-11 03:00 | 103.51 | 88.96
2018-01-11 03:30 | 103.45 | 90.15
2018-01-11 04:00 | 98.7 | 85.35
2018-01-11 04:30 | 98.2 | 85.32
2018-01-11 05:00 | 92.56 | 79.44
2018-01-11 05:30 | 91.6 | 78.38
2018-01-11 06:00 | 82.51 | 66.83
2018-01-11 06:30 | 82.95 | 66.21
2018-01-11 07:00 | 95.75 | 81.57
2018-01-11 07:30 | 98.13 | 83.48
2018-01-11 08:00 | 93.19 | 77.17
2018-01-11 08:30 | 88.56 | 72.24
2018-01-11 09:00 | 92.36 | 76.5
2018-01-11 09:30 | 99.77 | 85.56
2018-01-11 10:00 | 109.7 | 94.85
2018-01-11 10:30 | 113.35 | 97.73
2018-01-11 11:00 | 105.69 | 90.38
2018-01-11 11:30 | 107.37 | 90.61
2018-01-11 12:00 | 99.25 | 83.6
2018-01-11 12:30 | 116.84 | 100.98
2018-01-11 13:00 | 110.32 | 94.73
2018-01-11 13:30 | 111.24 | 94.78
2018-01-11 14:00 | 111.68 | 93.72
2018-01-11 14:30 | 111.66 | 91.33
2018-01-11 15:00 | 109.65 | 89.61
2018-01-11 15:30 | 111.32 | 91.26
2018-01-11 16:00 | 113.61 | 94.69
2018-01-11 16:30 | 116.52 | 97.8
2018-01-11 17:00 | 113.96 | 95.95
2018-01-11 17:30 | 115.59 | 98.26
2018-01-11 18:00 | 124.63 | 107.41
2018-01-11 18:30 | 117.75 | 101.96
2018-01-11 19:00 | 126.45 | 110.56
2018-01-11 19:30 | 128.85 | 112.99
2018-01-11 20:00 | 119.69 | 102.75
2018-01-11 20:30 | 114.95 | 97.08
2018-01-11 21:00 | 119.79 | 104.68
2018-01-11 21:30 | 115.91 | 100.69
2018-01-11 22:00 | 116.61 | 101.19
2018-01-11 22:30 | 115.87 | 101.35
2018-01-11 23:00 | 109.67 | 95.67
2018-01-11 23:30 | 109.31 | 95.33
2018-01-12 | 107.6 | 93.86
2018-01-12 00:30 | 101.78 | 88.14
2018-01-12 01:00 | 109.23 | 95.62
2018-01-12 01:30 | 110.82 | 98.19
2018-01-12 02:00 | 120.62 | 108.97
2018-01-12 02:30 | 115.8 | 104.45
2018-01-12 03:00 | 110.43 | 99.07
2018-01-12 03:30 | 112.93 | 101.76
2018-01-12 04:00 | 115.42 | 103.29
2018-01-12 04:30 | 118.78 | 107.13
2018-01-12 05:00 | 112.67 | 100.01
2018-01-12 05:30 | 116.74 | 104.82
2018-01-12 06:00 | 114.25 | 102.26
2018-01-12 06:30 | 104.14 | 91.97
2018-01-12 07:00 | 107.11 | 95.67
2018-01-12 07:30 | 112.8 | 100.5
2018-01-12 08:00 | 121.81 | 108.82
2018-01-12 08:30 | 115.11 | 101.9
2018-01-12 09:00 | 115.01 | 102.84
2018-01-12 09:30 | 111.2 | 99.34
2018-01-12 10:00 | 104.53 | 93.75
2018-01-12 10:30 | 106.83 | 95.4
2018-01-12 11:00 | 109.71 | 97.74
2018-01-12 11:30 | 119 | 104.87
2018-01-12 12:00 | 119.12 | 105.83
2018-01-12 12:30 | 123.84 | 111.39
2018-01-12 13:00 | 120.6 | 108.07
2018-01-12 13:30 | 114.29 | 101.71
2018-01-12 14:00 | 117.55 | 104.85
2018-01-12 14:30 | 120.42 | 107.61
2018-01-12 15:00 | 124.87 | 111.87
2018-01-12 15:30 | 121.32 | 109.02
2018-01-12 16:00 | 120.85 | 108.73
2018-01-12 16:30 | 125.17 | 112.64
2018-01-12 17:00 | 124.79 | 111.69
2018-01-12 17:30 | 117.97 | 105.16
2018-01-12 18:00 | 125.37 | 112.18
2018-01-12 18:30 | 122.45 | 108.57
2018-01-12 19:00 | 131.85 | 118.34
2018-01-12 19:30 | 129.3 | 115.53
2018-01-12 20:00 | 132.62 | 117.75
2018-01-12 20:30 | 125.49 | 110.85
2018-01-12 21:00 | 119.58 | 106.78
2018-01-12 21:30 | 121.47 | 108.68
2018-01-12 22:00 | 122.13 | 109.76
2018-01-12 22:30 | 122.6 | 110.28
2018-01-12 23:00 | 122.36 | 109.39
2018-01-12 23:30 | 111.97 | 99.94
2018-01-13 | 112.17 | 100.29
2018-01-13 00:30 | 111.13 | 99.95
2018-01-13 01:00 | 110.89 | 99.23
2018-01-13 01:30 | 109.61 | 98.13
2018-01-13 02:00 | 111.57 | 100.2
2018-01-13 02:30 | 115.55 | 104.44
2018-01-13 03:00 | 107.96 | 96.67
2018-01-13 03:30 | 109.38 | 98.19
2018-01-13 04:00 | 109.23 | 97.93
2018-01-13 04:30 | 109.63 | 97.76
2018-01-13 05:00 | 103.25 | 92.18
2018-01-13 05:30 | 106.41 | 95.5
2018-01-13 06:00 | 107.4 | 96.35
2018-01-13 06:30 | 99.74 | 87.97
2018-01-13 07:00 | 100.07 | 88.63
2018-01-13 07:30 | 116.2 | 106.27
2018-01-13 08:00 | 115.12 | 104.27
2018-01-13 08:30 | 118.72 | 106.51
2018-01-13 09:00 | 114.27 | 102.28
2018-01-13 09:30 | 110.11 | 97.61
2018-01-13 10:00 | 111.56 | 99.78
2018-01-13 10:30 | 112.19 | 99.47
2018-01-13 11:00 | 111.64 | 98.67
2018-01-13 11:30 | 122.69 | 109.55
2018-01-13 12:00 | 112.39 | 99.62
2018-01-13 12:30 | 115.99 | 102.41
2018-01-13 13:00 | 119.18 | 106.28
2018-01-13 13:30 | 120.22 | 107.4
2018-01-13 14:00 | 122.94 | 109.68
2018-01-13 14:30 | 113.07 | 100.33
2018-01-13 15:00 | 112.21 | 99.19
2018-01-13 15:30 | 109.66 | 95.83
2018-01-13 16:00 | 117.61 | 103.69
2018-01-13 16:30 | 123.46 | 110.2
2018-01-13 17:00 | 117.88 | 104.41
2018-01-13 17:30 | 123.48 | 110.96
2018-01-13 18:00 | 130.01 | 117.19
2018-01-13 18:30 | 120.31 | 107.91
2018-01-13 19:00 | 122.45 | 110.58
2018-01-13 19:30 | 122.21 | 108.36
2018-01-13 20:00 | 137.08 | 121.29
2018-01-13 20:30 | 137.62 | 122.48
2018-01-13 21:00 | 134.83 | 120.63
2018-01-13 21:30 | 127.25 | 112.32
2018-01-13 22:00 | 116.82 | 102.56
2018-01-13 22:30 | 116.39 | 102.99
2018-01-13 23:00 | 111.65 | 97.8
2018-01-13 23:30 | 111.13 | 97.59
2018-01-14 | 120.92 | 107.92
2018-01-14 00:30 | 115.5 | 102.34
2018-01-14 01:00 | 115.34 | 102.12
2018-01-14 01:30 | 117.93 | 105.27
2018-01-14 02:00 | 118.67 | 105.37
2018-01-14 02:30 | 120.09 | 106.5
2018-01-14 03:00 | 109.53 | 96.5
2018-01-14 03:30 | 114.79 | 101.97
2018-01-14 04:00 | 114.58 | 102.5
2018-01-14 04:30 | 113.76 | 102.14
2018-01-14 05:00 | 118.27 | 106.18
2018-01-14 05:30 | 116.65 | 105.69
2018-01-14 06:00 | 116.18 | 104.72
2018-01-14 06:30 | 102.62 | 90.72
2018-01-14 07:00 | 103.39 | 91.36
2018-01-14 07:30 | 116.8 | 104.85
2018-01-14 08:00 | 116.87 | 104.1
2018-01-14 08:30 | 117.14 | 103.63
2018-01-14 09:00 | 114.26 | 100.55
2018-01-14 09:30 | 113.94 | 102
2018-01-14 10:00 | 112.47 | 100.21
2018-01-14 10:30 | 112.4 | 100.07
2018-01-14 11:00 | 115.29 | 102.98
2018-01-14 11:30 | 123.91 | 112.16
2018-01-14 12:00 | 122.76 | 110.32
2018-01-14 12:30 | 122.75 | 108.07
2018-01-14 13:00 | 121.47 | 106.68
2018-01-14 13:30 | 122.29 | 107.53
2018-01-14 14:00 | 128.4 | 112.14
2018-01-14 14:30 | 120.52 | 106.88
2018-01-14 15:00 | 114.65 | 100.71
2018-01-14 15:30 | 117.66 | 103.87
2018-01-14 16:00 | 123.08 | 109.19
2018-01-14 16:30 | 116.16 | 103.81
2018-01-14 17:00 | 120.61 | 111.06
2018-01-14 17:30 | 114.53 | 105.4
2018-01-14 18:00 | 117.59 | 106.71
2018-01-14 18:30 | 110.42 | 98.42
2018-01-14 19:00 | 118.04 | 105.07
2018-01-14 19:30 | 124.2 | 112.02
2018-01-14 20:00 | 121.64 | 108.44
2018-01-14 20:30 | 127.21 | 114.79
2018-01-14 21:00 | 126.3 | 113.82
2018-01-14 21:30 | 121.76 | 109.9
2018-01-14 22:00 | 123.48 | 111.48
2018-01-14 22:30 | 126.14 | 113.31
2018-01-14 23:00 | 123.82 | 111.55
2018-01-14 23:30 | 114.18 | 102.35
2018-01-15 | 119.75 | 107.93
2018-01-15 00:30 | 114.39 | 101.21
2018-01-15 01:00 | 119.11 | 105.59
2018-01-15 01:30 | 118.55 | 105.39
2018-01-15 02:00 | 124.89 | 111.68
2018-01-15 02:30 | 123 | 110.39
2018-01-15 03:00 | 116.79 | 104.42
2018-01-15 03:30 | 118.48 | 106.59
2018-01-15 04:00 | 118.93 | 107.35
2018-01-15 04:30 | 116.37 | 104.85
2018-01-15 05:00 | 114.96 | 102.9
2018-01-15 05:30 | 116.42 | 104.64
2018-01-15 06:00 | 112.56 | 100.54
2018-01-15 06:30 | 102.52 | 89.74
2018-01-15 07:00 | 111.17 | 99.28
2018-01-15 07:30 | 115.03 | 103.89
2018-01-15 08:00 | 116.12 | 104.45
2018-01-15 08:30 | 117.76 | 105.16
2018-01-15 09:00 | 111.68 | 98.53
2018-01-15 09:30 | 119.72 | 106.22
2018-01-15 10:00 | 116.42 | 102.55
2018-01-15 10:30 | 114.41 | 100.35
2018-01-15 11:00 | 111.98 | 98.61
2018-01-15 11:30 | 123.68 | 108.93
2018-01-15 12:00 | 122.44 | 107.74
2018-01-15 12:30 | 123.69 | 108.16
2018-01-15 13:00 | 132.69 | 118.69
2018-01-15 13:30 | 126.4 | 111.9
2018-01-15 14:00 | 125.97 | 110.86
2018-01-15 14:30 | 127.78 | 113.07
2018-01-15 15:00 | 127.77 | 113.57
2018-01-15 15:30 | 120.88 | 107.59
2018-01-15 16:00 | 122.15 | 108.4
2018-01-15 16:30 | 126.41 | 113.3
2018-01-15 17:00 | 118.93 | 106.41
2018-01-15 17:30 | 119.15 | 106.66
2018-01-15 18:00 | 119.13 | 106.73
2018-01-15 18:30 | 118.57 | 104.2
2018-01-15 19:00 | 137.2 | 121.88
2018-01-15 19:30 | 141 | 125.64
2018-01-15 20:00 | 131.12 | 117.08
2018-01-15 20:30 | 131.61 | 117.98
2018-01-15 21:00 | 126.97 | 113.38
2018-01-15 21:30 | 121.01 | 107.85
2018-01-15 22:00 | 119.63 | 106.9
2018-01-15 22:30 | 116.79 | 104.55
2018-01-15 23:00 | 106.5 | 93.9
2018-01-15 23:30 | 115.69 | 102.58
2018-01-16 | 108.21 | 95.8
2018-01-16 00:30 | 113.2 | 101.99
2018-01-16 01:00 | 118.24 | 106.76
2018-01-16 01:30 | 113.74 | 102.96
2018-01-16 02:00 | 112.28 | 101.77
2018-01-16 02:30 | 111.62 | 100.93
2018-01-16 03:00 | 102.49 | 92.1
2018-01-16 03:30 | 101.87 | 90.99
2018-01-16 04:00 | 104.79 | 94.63
2018-01-16 04:30 | 101.12 | 91.73
2018-01-16 05:00 | 99.21 | 91.06
2018-01-16 05:30 | 90.91 | 82.79
2018-01-16 06:00 | 87.82 | 79.42
2018-01-16 06:30 | 84.42 | 75.65
2018-01-16 07:00 | 93.49 | 85.38
2018-01-16 07:30 | 97.74 | 89.51
2018-01-16 08:00 | 88.68 | 78.56
2018-01-16 08:30 | 102.02 | 93.05
2018-01-16 09:00 | 94.63 | 86.33
2018-01-16 09:30 | 88.77 | 80.28
2018-01-16 10:00 | 93.46 | 84.99
2018-01-16 10:30 | 95.32 | 86.48
2018-01-16 11:00 | 96.07 | 87.03
2018-01-16 11:30 | 101.79 | 91.26
2018-01-16 12:00 | 105.98 | 96.28
2018-01-16 12:30 | 108.34 | 98.65
2018-01-16 13:00 | 112.74 | 103.47
2018-01-16 13:30 | 100.18 | 91.15
2018-01-16 14:00 | 104.99 | 96.23
2018-01-16 14:30 | 108.59 | 99.98
2018-01-16 15:00 | 105.58 | 97.13
2018-01-16 15:30 | 110.28 | 102.07
2018-01-16 16:00 | 118.1 | 109.59
2018-01-16 16:30 | 109.46 | 98.35
2018-01-16 17:00 | 109.92 | 99.24
2018-01-16 17:30 | 118.08 | 108
2018-01-16 18:00 | 112.49 | 101.8
2018-01-16 18:30 | 110.27 | 99.04
2018-01-16 19:00 | 118.35 | 106.45
2018-01-16 19:30 | 121.62 | 108.78
2018-01-16 20:00 | 121.19 | 108.64
2018-01-16 20:30 | 117.57 | 106.13
2018-01-16 21:00 | 114.12 | 104.19
2018-01-16 21:30 | 104.26 | 94.25
2018-01-16 22:00 | 107.55 | 97.83
2018-01-16 22:30 | 102.85 | 93.05
2018-01-16 23:00 | 109.93 | 99.69
2018-01-16 23:30 | 108.04 | 98.39
2018-01-17 | 104.17 | 95.06
2018-01-17 00:30 | 106.7 | 97.68
2018-01-17 01:00 | 105.99 | 96.31
2018-01-17 01:30 | 106.02 | 97.09
2018-01-17 02:00 | 93.14 | 85.53
2018-01-17 02:30 | 93.23 | 85.52
2018-01-17 03:00 | 86.42 | 78.69
2018-01-17 03:30 | 86.14 | 78.42
2018-01-17 04:00 | 92.61 | 85.2
2018-01-17 04:30 | 87.22 | 79.68
2018-01-17 05:00 | 90.7 | 82.8
2018-01-17 05:30 | 90.73 | 82.34
2018-01-17 06:00 | 88.41 | 80.28
2018-01-17 06:30 | 81.48 | 72.52
2018-01-17 07:00 | 90.53 | 82.5
2018-01-17 07:30 | 92.54 | 85.03
2018-01-17 08:00 | 85.38 | 77.2
2018-01-17 08:30 | 89.03 | 80.9
2018-01-17 09:00 | 98.26 | 90.14
2018-01-17 09:30 | 90.73 | 83.42
2018-01-17 10:00 | 92.2 | 84.95
2018-01-17 10:30 | 92.02 | 84.26
2018-01-17 11:00 | 93.58 | 79.8
2018-01-17 11:30 | 89.95 | 73.84
2018-01-17 12:00 | 102.18 | 88.7
2018-01-17 12:30 | 105.41 | 91.65
2018-01-17 13:00 | 99.21 | 84.28
2018-01-17 13:30 | 97.46 | 86.16
2018-01-17 14:00 | 100.7 | 90.55
2018-01-17 14:30 | 105.97 | 92.61
2018-01-17 15:00 | 102.62 | 86.42
2018-01-17 15:30 | 102.35 | 89.62
2018-01-17 16:00 | 98.57 | 86.18
2018-01-17 16:30 | 99.47 | 87.31
2018-01-17 17:00 | 108.99 | 97.46
2018-01-17 17:30 | 101.09 | 90.35
2018-01-17 18:00 | 102.57 | 91.37
2018-01-17 18:30 | 92.33 | 80.71
2018-01-17 19:00 | 103.21 | 91.24
2018-01-17 19:30 | 105.78 | 93.48
2018-01-17 20:00 | 103.04 | 90.82
2018-01-17 20:30 | 109.51 | 97.37
2018-01-17 21:00 | 103.33 | 91.17
2018-01-17 21:30 | 96.89 | 85.39
2018-01-17 22:00 | 96.66 | 85.4
2018-01-17 22:30 | 96.93 | 85.31
2018-01-17 23:00 | 95.16 | 83.7
2018-01-17 23:30 | 92.76 | 81.71
2018-01-18 | 93.37 | 81.91
2018-01-18 00:30 | 94.42 | 83.8
2018-01-18 01:00 | 90.58 | 78.87
2018-01-18 01:30 | 100.74 | 89.89
2018-01-18 02:00 | 101.53 | 91.1
2018-01-18 02:30 | 95.87 | 84.71
2018-01-18 03:00 | 106.85 | 94.69
2018-01-18 03:30 | 113.78 | 102.56
2018-01-18 04:00 | 115.7 | 104.02
2018-01-18 04:30 | 102.76 | 92.75
2018-01-18 05:00 | 110.25 | 98.36
2018-01-18 05:30 | 113.28 | 101.83
2018-01-18 06:00 | 105.61 | 95.14
2018-01-18 06:30 | 103.66 | 92.04
2018-01-18 07:00 | 100.74 | 89.07
2018-01-18 07:30 | 102.48 | 91.47
2018-01-18 08:00 | 99.96 | 88.66
2018-01-18 08:30 | 101.28 | 89.73
2018-01-18 09:00 | 97.9 | 86.91
2018-01-18 09:30 | 100.81 | 88.34
2018-01-18 10:00 | 95.7 | 84.21
2018-01-18 10:30 | 103.51 | 92.41
2018-01-18 11:00 | 102.55 | 92.17
2018-01-18 11:30 | 101.26 | 89.52
2018-01-18 12:00 | 99.72 | 87.29
2018-01-18 12:30 | 105.77 | 94.26
2018-01-18 13:00 | 96.87 | 85.32
2018-01-18 13:30 | 101.63 | 90.04
2018-01-18 14:00 | 114.83 | 102.79
2018-01-18 14:30 | 110.34 | 97.32
2018-01-18 15:00 | 126.13 | 112.98
2018-01-18 15:30 | 121.33 | 108.8
2018-01-18 16:00 | 123.69 | 110.61
2018-01-18 16:30 | 120.13 | 108.11
2018-01-18 17:00 | 116.9 | 104.86
2018-01-18 17:30 | 121.48 | 108.22
2018-01-18 18:00 | 112.83 | 99.04
2018-01-18 18:30 | 103.87 | 89.33
2018-01-18 19:00 | 117 | 103.03
2018-01-18 19:30 | 113.29 | 98.58
2018-01-18 20:00 | 114.3 | 98.28
2018-01-18 20:30 | 115.01 | 99.56
2018-01-18 21:00 | 115.65 | 100.41
2018-01-18 21:30 | 112.2 | 96.94
2018-01-18 22:00 | 104.65 | 90.18
2018-01-18 22:30 | 100.14 | 86.47
2018-01-18 23:00 | 104.39 | 93.59
2018-01-18 23:30 | 102.58 | 91.69
2018-01-19 | 105.58 | 94.56
2018-01-19 00:30 | 113 | 101.24
2018-01-19 01:00 | 111.84 | 100.23
2018-01-19 01:30 | 108.25 | 96.25
2018-01-19 02:00 | 103.67 | 92.74
2018-01-19 02:30 | 107.29 | 96
2018-01-19 03:00 | 98.04 | 87.08
2018-01-19 03:30 | 100.53 | 88.56
2018-01-19 04:00 | 105.98 | 93.53
2018-01-19 04:30 | 100.39 | 87.81
2018-01-19 05:00 | 104.24 | 91.96
2018-01-19 05:30 | 112.08 | 100.19
2018-01-19 06:00 | 109.98 | 97.47
2018-01-19 06:30 | 105.89 | 93.06
2018-01-19 07:00 | 113.77 | 101.34
2018-01-19 07:30 | 109.6 | 97.52
2018-01-19 08:00 | 111.11 | 97.89
2018-01-19 08:30 | 108.43 | 95.59
2018-01-19 09:00 | 109.01 | 96.78
2018-01-19 09:30 | 102.55 | 89.08
2018-01-19 10:00 | 101 | 87.19
2018-01-19 10:30 | 105.64 | 91.17
2018-01-19 11:00 | 111.86 | 97.41
2018-01-19 11:30 | 103.02 | 88.57
2018-01-19 12:00 | 113.18 | 99.41
2018-01-19 12:30 | 117.58 | 103.66
2018-01-19 13:00 | 114.75 | 98.89
2018-01-19 13:30 | 111.03 | 94.64
2018-01-19 14:00 | 113.02 | 96.47
2018-01-19 14:30 | 115.69 | 100.91
2018-01-19 15:00 | 117.55 | 102.64
2018-01-19 15:30 | 124.19 | 109.09
2018-01-19 16:00 | 119.28 | 104.8
2018-01-19 16:30 | 111.72 | 97.34
2018-01-19 17:00 | 115.92 | 101.57
2018-01-19 17:30 | 113.01 | 99.02
2018-01-19 18:00 | 110.87 | 98.07
2018-01-19 18:30 | 108.07 | 94.73
2018-01-19 19:00 | 115.28 | 103.58
2018-01-19 19:30 | 117.6 | 105.63
2018-01-19 20:00 | 115.48 | 102.92
2018-01-19 20:30 | 114.16 | 100.65
2018-01-19 21:00 | 112.42 | 100.06
2018-01-19 21:30 | 115.95 | 103.25
2018-01-19 22:00 | 117.22 | 105.91
2018-01-19 22:30 | 110.75 | 99.14
2018-01-19 23:00 | 119.21 | 106.66
2018-01-19 23:30 | 118.21 | 106.59
2018-01-20 | 115.55 | 103.03
2018-01-20 00:30 | 104.94 | 92.45
2018-01-20 01:00 | 109.79 | 97.64
2018-01-20 01:30 | 108.85 | 96.82
2018-01-20 02:00 | 110.16 | 97.75
2018-01-20 02:30 | 111.33 | 99.94
2018-01-20 03:00 | 104.38 | 92.66
2018-01-20 03:30 | 104.22 | 92.93
2018-01-20 04:00 | 107.46 | 97.02
2018-01-20 04:30 | 101.87 | 90.31
2018-01-20 05:00 | 98.39 | 87.01
2018-01-20 05:30 | 100.06 | 89.33
2018-01-20 06:00 | 100.71 | 90.12
2018-01-20 06:30 | 99.66 | 86.66
2018-01-20 07:00 | 107.48 | 94.12
2018-01-20 07:30 | 116.41 | 103.19
2018-01-20 08:00 | 112.53 | 99.2
2018-01-20 08:30 | 118.29 | 104.34
2018-01-20 09:00 | 106.79 | 92.09
2018-01-20 09:30 | 111.63 | 96.57
2018-01-20 10:00 | 115.19 | 101.18
2018-01-20 10:30 | 112.62 | 98.28
2018-01-20 11:00 | 107.54 | 92.48
2018-01-20 11:30 | 119.67 | 104.61
2018-01-20 12:00 | 121.02 | 105.89
2018-01-20 12:30 | 120.97 | 105.87
2018-01-20 13:00 | 128.99 | 114.7
2018-01-20 13:30 | 126.78 | 111.54
2018-01-20 14:00 | 121.45 | 105.5
2018-01-20 14:30 | 120.49 | 104.76
2018-01-20 15:00 | 121.4 | 105.1
2018-01-20 15:30 | 116.15 | 100.37
2018-01-20 16:00 | 114 | 98.68
2018-01-20 16:30 | 122.77 | 106.97
2018-01-20 17:00 | 124.42 | 108.16
2018-01-20 17:30 | 125.23 | 109.63
2018-01-20 18:00 | 129.57 | 114.27
2018-01-20 18:30 | 120.35 | 105.25
2018-01-20 19:00 | 129.42 | 112.55
2018-01-20 19:30 | 133.78 | 116.09
2018-01-20 20:00 | 133.8 | 116.43
2018-01-20 20:30 | 131.3 | 113.43
2018-01-20 21:00 | 133.33 | 115.57
2018-01-20 21:30 | 123.65 | 106.84
2018-01-20 22:00 | 129.82 | 112.34
2018-01-20 22:30 | 128.02 | 110.1
2018-01-20 23:00 | 121.42 | 103.74
2018-01-20 23:30 | 124.6 | 107.75
2018-01-21 | 115.91 | 98.4
2018-01-21 00:30 | 124.75 | 106.93
2018-01-21 01:00 | 127.1 | 110.99
2018-01-21 01:30 | 130.75 | 113.65
2018-01-21 02:00 | 131.53 | 116.43
2018-01-21 02:30 | 129.43 | 114.54
2018-01-21 03:00 | 128.55 | 114.33
2018-01-21 03:30 | 126.95 | 113.39
2018-01-21 04:00 | 129.29 | 114.47
2018-01-21 04:30 | 129.9 | 114.54
2018-01-21 05:00 | 122.9 | 107.98
2018-01-21 05:30 | 123.58 | 109.33
2018-01-21 06:00 | 119.07 | 106.56
2018-01-21 06:30 | 104.95 | 91.22
2018-01-21 07:00 | 113.56 | 100.82
2018-01-21 07:30 | 109.97 | 97.37
2018-01-21 08:00 | 113.7 | 101.5
2018-01-21 08:30 | 112.15 | 98.64
2018-01-21 09:00 | 119.23 | 106.43
2018-01-21 09:30 | 117.24 | 103.02
2018-01-21 10:00 | 113.98 | 97.93
2018-01-21 10:30 | 108.98 | 91.69
2018-01-21 11:00 | 115.49 | 99.1
2018-01-21 11:30 | 118.16 | 101.82
2018-01-21 12:00 | 122.95 | 105.15
2018-01-21 12:30 | 130.11 | 112.91
2018-01-21 13:00 | 132.62 | 115.79
2018-01-21 13:30 | 131.51 | 114.37
2018-01-21 14:00 | 133.85 | 117.07
2018-01-21 14:30 | 122.97 | 106.22
2018-01-21 15:00 | 116.88 | 101.21
2018-01-21 15:30 | 122.32 | 107.54
2018-01-21 16:00 | 116.11 | 101.72
2018-01-21 16:30 | 117.06 | 102.14
2018-01-21 17:00 | 116.32 | 102.83
2018-01-21 17:30 | 116.38 | 102.41
2018-01-21 18:00 | 122.63 | 108
2018-01-21 18:30 | 105.59 | 90.3
2018-01-21 19:00 | 115.16 | 100.89
2018-01-21 19:30 | 120.04 | 105.25
2018-01-21 20:00 | 118.39 | 103.57
2018-01-21 20:30 | 117.76 | 103.03
2018-01-21 21:00 | 115.11 | 100.73
2018-01-21 21:30 | 112.71 | 98.62
2018-01-21 22:00 | 114.47 | 101.02
2018-01-21 22:30 | 112.51 | 98.95
2018-01-21 23:00 | 114.49 | 100.67
2018-01-21 23:30 | 104.92 | 91.93
2018-01-22 | 108.8 | 97.02
2018-01-22 00:30 | 103.24 | 91.48
2018-01-22 01:00 | 104.54 | 92.18
2018-01-22 01:30 | 104.4 | 91.47
2018-01-22 02:00 | 102.91 | 89.92
2018-01-22 02:30 | 98.49 | 85.4
2018-01-22 03:00 | 95.42 | 82.75
2018-01-22 03:30 | 92.19 | 79.67
2018-01-22 04:00 | 95.86 | 82.61
2018-01-22 04:30 | 94.68 | 81.87
2018-01-22 05:00 | 99.48 | 86.31
2018-01-22 05:30 | 94.25 | 81.14
2018-01-22 06:00 | 94.32 | 81.58
2018-01-22 06:30 | 89.82 | 76.01
2018-01-22 07:00 | 91.42 | 78.8
2018-01-22 07:30 | 100.79 | 86.36
2018-01-22 08:00 | 103.44 | 87.75
2018-01-22 08:30 | 108.6 | 91.92
2018-01-22 09:00 | 112.07 | 93.02
2018-01-22 09:30 | 115.83 | 94.38
2018-01-22 10:00 | 114.61 | 95.33
2018-01-22 10:30 | 118.64 | 98.57
2018-01-22 11:00 | 117.3 | 96.68
2018-01-22 11:30 | 118.65 | 97.47
2018-01-22 12:00 | 122.82 | 102.27
2018-01-22 12:30 | 121.89 | 100.48
2018-01-22 13:00 | 123.37 | 102.33
2018-01-22 13:30 | 124.99 | 103.99
2018-01-22 14:00 | 126.7 | 104.79
2018-01-22 14:30 | 128 | 106.69
2018-01-22 15:00 | 129.25 | 107.78
2018-01-22 15:30 | 127.18 | 106.21
2018-01-22 16:00 | 127.73 | 106.46
2018-01-22 16:30 | 121.96 | 100.68
2018-01-22 17:00 | 128.49 | 107.36
2018-01-22 17:30 | 125.53 | 104.61
2018-01-22 18:00 | 127.7 | 106.61
2018-01-22 18:30 | 119.6 | 97.19
2018-01-22 19:00 | 122.27 | 101.68
2018-01-22 19:30 | 127.55 | 107.26
2018-01-22 20:00 | 130.8 | 109.95
2018-01-22 20:30 | 136.54 | 117.07
2018-01-22 21:00 | 128.57 | 108.03
2018-01-22 21:30 | 123.95 | 103.59
2018-01-22 22:00 | 125.43 | 105.39
2018-01-22 22:30 | 124.68 | 104.81
2018-01-22 23:00 | 119.46 | 100.58
2018-01-22 23:30 | 111.61 | 94.25
2018-01-23 | 101.94 | 86.72
2018-01-23 00:30 | 105.31 | 90.47
2018-01-23 01:00 | 98.32 | 83.11
2018-01-23 01:30 | 102.55 | 88.63
2018-01-23 02:00 | 101.17 | 87.92
2018-01-23 02:30 | 97.67 | 84.99
2018-01-23 03:00 | 97.03 | 83.88
2018-01-23 03:30 | 87.79 | 73.89
2018-01-23 04:00 | 91.4 | 78.6
2018-01-23 04:30 | 96.06 | 83.86
2018-01-23 05:00 | 97.23 | 84.16
2018-01-23 05:30 | 99.57 | 86.77
2018-01-23 06:00 | 103.46 | 88.7
2018-01-23 06:30 | 103.4 | 85.42
2018-01-23 07:00 | 110.08 | 92.82
2018-01-23 07:30 | 113.27 | 95.64
2018-01-23 08:00 | 105.76 | 88.8
2018-01-23 08:30 | 105.15 | 88.31
2018-01-23 09:00 | 102.21 | 85.13
2018-01-23 09:30 | 112.14 | 91.72
2018-01-23 10:00 | 114.62 | 95.01
2018-01-23 10:30 | 113.01 | 93.56
2018-01-23 11:00 | 115.03 | 95.39
2018-01-23 11:30 | 116.74 | 96.06
2018-01-23 12:00 | 116.37 | 94.68
2018-01-23 12:30 | 133.14 | 111.05
2018-01-23 13:00 | 128.38 | 107.39
2018-01-23 13:30 | 123.18 | 101.75
2018-01-23 14:00 | 117.2 | 94.71
2018-01-23 14:30 | 118.52 | 96.89
2018-01-23 15:00 | 122.08 | 102
2018-01-23 15:30 | 128.72 | 108.82
2018-01-23 16:00 | 124.56 | 103.62
2018-01-23 16:30 | 128.06 | 107.82
2018-01-23 17:00 | 124.66 | 103.7
2018-01-23 17:30 | 123.56 | 103.93
2018-01-23 18:00 | 117.91 | 98.96
2018-01-23 18:30 | 112.74 | 92.83
2018-01-23 19:00 | 125.42 | 104.3
2018-01-23 19:30 | 130.85 | 108.76
2018-01-23 20:00 | 131.79 | 108.56
2018-01-23 20:30 | 128.89 | 103.57
2018-01-23 21:00 | 128.65 | 104.62
2018-01-23 21:30 | 129.76 | 103.83
2018-01-23 22:00 | 125.36 | 99.39
2018-01-23 22:30 | 120.2 | 96.68
2018-01-23 23:00 | 119.7 | 96.8
2018-01-23 23:30 | 121.46 | 100.27
2018-01-24 | 120.39 | 98.16
2018-01-24 00:30 | 124.78 | 103.34
2018-01-24 01:00 | 120.79 | 100.06
2018-01-24 01:30 | 117.36 | 97.61
2018-01-24 02:00 | 111.73 | 91.83
2018-01-24 02:30 | 118.67 | 98.52
2018-01-24 03:00 | 113.58 | 92.82
2018-01-24 03:30 | 115.65 | 95.39
2018-01-24 04:00 | 118.5 | 98.08
2018-01-24 04:30 | 117.19 | 97.28
2018-01-24 05:00 | 119.82 | 100.2
2018-01-24 05:30 | 119.19 | 99.9
2018-01-24 06:00 | 108.22 | 87.62
2018-01-24 06:30 | 108.96 | 87.42
2018-01-24 07:00 | 109.99 | 89.71
2018-01-24 07:30 | 114.19 | 93.65
2018-01-24 08:00 | 120.7 | 98.65
2018-01-24 08:30 | 119.72 | 97.14
2018-01-24 09:00 | 113.3 | 89.57
2018-01-24 09:30 | 114.45 | 91.84
2018-01-24 10:00 | 110.83 | 89.89
2018-01-24 10:30 | 115.02 | 93.85
2018-01-24 11:00 | 115.07 | 95.14
2018-01-24 11:30 | 112.58 | 91.83
2018-01-24 12:00 | 118.39 | 98.9
2018-01-24 12:30 | 116.9 | 95.24
2018-01-24 13:00 | 120.19 | 98.85
2018-01-24 13:30 | 123.54 | 102.45
2018-01-24 14:00 | 118.06 | 96.05
2018-01-24 14:30 | 119.13 | 96.9
2018-01-24 15:00 | 121.45 | 98.75
2018-01-24 15:30 | 119.78 | 97.39
2018-01-24 16:00 | 122.28 | 99.94
2018-01-24 16:30 | 123.92 | 103.05
2018-01-24 17:00 | 121.77 | 101.99
2018-01-24 17:30 | 123.29 | 103.99
2018-01-24 18:00 | 125.7 | 106.57
2018-01-24 18:30 | 114.35 | 93.09
2018-01-24 19:00 | 120.54 | 99.55
2018-01-24 19:30 | 124.21 | 102.2
2018-01-24 20:00 | 124.92 | 101.63
2018-01-24 20:30 | 121.4 | 99.07
2018-01-24 21:00 | 116.51 | 94.08
2018-01-24 21:30 | 116.55 | 94.83
2018-01-24 22:00 | 113.8 | 93.49
2018-01-24 22:30 | 112.21 | 91.91
2018-01-24 23:00 | 106.21 | 85
2018-01-24 23:30 | 105.56 | 83.33
2018-01-25 | 107.02 | 84.94
2018-01-25 00:30 | 106.54 | 83.47
2018-01-25 01:00 | 105.55 | 83.52
2018-01-25 01:30 | 105.48 | 83.92
2018-01-25 02:00 | 106.67 | 86.35
2018-01-25 02:30 | 106.44 | 86.7
2018-01-25 03:00 | 102.61 | 82.95
2018-01-25 03:30 | 104.5 | 84.55
2018-01-25 04:00 | 105.78 | 85.89
2018-01-25 04:30 | 108.12 | 88.47
2018-01-25 05:00 | 105.81 | 86.28
2018-01-25 05:30 | 106.38 | 85.57
2018-01-25 06:00 | 104.59 | 83.9
2018-01-25 06:30 | 97.06 | 74.93
2018-01-25 07:00 | 105.94 | 85.35
2018-01-25 07:30 | 112.46 | 92.62
2018-01-25 08:00 | 111.36 | 91.67
2018-01-25 08:30 | 110.03 | 91.2
2018-01-25 09:00 | 102.92 | 82.9
2018-01-25 09:30 | 103.89 | 83.17
2018-01-25 10:00 | 104.34 | 84.8
2018-01-25 10:30 | 106.26 | 86.56
2018-01-25 11:00 | 100.71 | 79.41
2018-01-25 11:30 | 104.47 | 81.96
2018-01-25 12:00 | 105.91 | 84.28
2018-01-25 12:30 | 101.98 | 80.92
2018-01-25 13:00 | 99.81 | 78.57
2018-01-25 13:30 | 99.57 | 76.92
2018-01-25 14:00 | 98.37 | 75.62
2018-01-25 14:30 | 96.82 | 74.66
2018-01-25 15:00 | 101.23 | 81.06
2018-01-25 15:30 | 104.8 | 84.64
2018-01-25 16:00 | 108.07 | 87.65
2018-01-25 16:30 | 113.58 | 93.5
2018-01-25 17:00 | 117.24 | 97.36
2018-01-25 17:30 | 114.53 | 93.23
2018-01-25 18:00 | 111.68 | 90.74
2018-01-25 18:30 | 110.59 | 89.12
2018-01-25 19:00 | 115.65 | 94.26
2018-01-25 19:30 | 118.14 | 95.3
2018-01-25 20:00 | 117.96 | 92.93
2018-01-25 20:30 | 115.81 | 91.74
2018-01-25 21:00 | 112.97 | 91.01
2018-01-25 21:30 | 115.61 | 94.14
2018-01-25 22:00 | 119.51 | 98.13
2018-01-25 22:30 | 117.75 | 96.86
2018-01-25 23:00 | 109.73 | 89.1
2018-01-25 23:30 | 111.85 | 91.56
2018-01-26 | 110.02 | 89.74
2018-01-26 00:30 | 110.6 | 89.47
2018-01-26 01:00 | 108.88 | 87.96
2018-01-26 01:30 | 108.32 | 87.19
2018-01-26 02:00 | 110.48 | 89.85
2018-01-26 02:30 | 108.09 | 89.05
2018-01-26 03:00 | 104.74 | 85.38
2018-01-26 03:30 | 106.6 | 87.01
2018-01-26 04:00 | 104.8 | 85.3
2018-01-26 04:30 | 103.88 | 85.05
2018-01-26 05:00 | 112.5 | 92.3
2018-01-26 05:30 | 114.68 | 93.45
2018-01-26 06:00 | 110.99 | 90.11
2018-01-26 06:30 | 105.86 | 83.12
2018-01-26 07:00 | 112.4 | 91.36
2018-01-26 07:30 | 116.24 | 95.04
2018-01-26 08:00 | 113.95 | 91.12
2018-01-26 08:30 | 114.53 | 91.91
2018-01-26 09:00 | 106.75 | 83.9
2018-01-26 09:30 | 106.58 | 83.68
2018-01-26 10:00 | 107.67 | 85.43
2018-01-26 10:30 | 110.35 | 86.23
2018-01-26 11:00 | 111.37 | 86.71
2018-01-26 11:30 | 108.02 | 84.56
2018-01-26 12:00 | 111.81 | 89.22
2018-01-26 12:30 | 117.37 | 95.34
2018-01-26 13:00 | 119.03 | 96.38
2018-01-26 13:30 | 116.38 | 93.06
2018-01-26 14:00 | 113.41 | 88.98
2018-01-26 14:30 | 115.33 | 91.94
2018-01-26 15:00 | 115.36 | 92.22
2018-01-26 15:30 | 119.61 | 96.79
2018-01-26 16:00 | 123.37 | 99.2
2018-01-26 16:30 | 124.69 | 101.34
2018-01-26 17:00 | 124.71 | 100.81
2018-01-26 17:30 | 119.29 | 94.51
2018-01-26 18:00 | 123.69 | 99.17
2018-01-26 18:30 | 122.47 | 96.34
2018-01-26 19:00 | 126.56 | 101.31
2018-01-26 19:30 | 135.6 | 110.13
2018-01-26 20:00 | 130.22 | 104.54
2018-01-26 20:30 | 128.85 | 103.3
2018-01-26 21:00 | 128.07 | 102.48
2018-01-26 21:30 | 127.55 | 101.75
2018-01-26 22:00 | 126.22 | 100.81
2018-01-26 22:30 | 123.26 | 98.3
2018-01-26 23:00 | 118.15 | 94
2018-01-26 23:30 | 121.48 | 97.65
2018-01-27 | 120.26 | 96.42
2018-01-27 00:30 | 119.49 | 95.8
2018-01-27 01:00 | 122.5 | 99.44
2018-01-27 01:30 | 121.47 | 98.19
2018-01-27 02:00 | 118.11 | 94.35
2018-01-27 02:30 | 110.03 | 86.05
2018-01-27 03:00 | 115.81 | 91.64
2018-01-27 03:30 | 115.65 | 91.71
2018-01-27 04:00 | 115.09 | 91.13
2018-01-27 04:30 | 117.41 | 94.67
2018-01-27 05:00 | 113.68 | 90.5
2018-01-27 05:30 | 110.13 | 88.31
2018-01-27 06:00 | 107.7 | 86.24
2018-01-27 06:30 | 100.73 | 77.66
2018-01-27 07:00 | 109.3 | 86.67
2018-01-27 07:30 | 112.99 | 90.58
2018-01-27 08:00 | 110.23 | 86.53
2018-01-27 08:30 | 106.2 | 81.87
2018-01-27 09:00 | 103.08 | 79.16
2018-01-27 09:30 | 103.6 | 79.05
2018-01-27 10:00 | 103.47 | 77.46
2018-01-27 10:30 | 104.58 | 77.95
2018-01-27 11:00 | 104.92 | 78.91
2018-01-27 11:30 | 106.65 | 80.45
2018-01-27 12:00 | 110.7 | 85.58
2018-01-27 12:30 | 113.13 | 87.71
2018-01-27 13:00 | 115.08 | 90.68
2018-01-27 13:30 | 116.18 | 91.46
2018-01-27 14:00 | 123.22 | 98.18
2018-01-27 14:30 | 124.7 | 100.55
2018-01-27 15:00 | 126.37 | 102.3
2018-01-27 15:30 | 127.16 | 102.41
2018-01-27 16:00 | 124.46 | 98.87
2018-01-27 16:30 | 121 | 96.35
2018-01-27 17:00 | 128.05 | 103.71
2018-01-27 17:30 | 131.72 | 107.11
2018-01-27 18:00 | 130.65 | 105.91
2018-01-27 18:30 | 123.29 | 96.8
2018-01-27 19:00 | 128.79 | 104.22
2018-01-27 19:30 | 129.79 | 105.25
2018-01-27 20:00 | 134.23 | 109.05
2018-01-27 20:30 | 132.15 | 106.75
2018-01-27 21:00 | 129.79 | 105.5
2018-01-27 21:30 | 125.36 | 99.98
2018-01-27 22:00 | 123.86 | 97.64
2018-01-27 22:30 | 126.24 | 100.45
2018-01-27 23:00 | 123.32 | 97.48
2018-01-27 23:30 | 122.28 | 97.56
2018-01-28 | 123.29 | 99.32
2018-01-28 00:30 | 116.6 | 92.18
2018-01-28 01:00 | 117.91 | 93.6
2018-01-28 01:30 | 116.22 | 92.34
2018-01-28 02:00 | 117.7 | 94.49
2018-01-28 02:30 | 115.68 | 92.81
2018-01-28 03:00 | 115.47 | 92.43
2018-01-28 03:30 | 114.43 | 91.33
2018-01-28 04:00 | 110.47 | 86.94
2018-01-28 04:30 | 111.28 | 88.33
2018-01-28 05:00 | 113.09 | 90.53
2018-01-28 05:30 | 106.9 | 83.25
2018-01-28 06:00 | 113.44 | 90.98
2018-01-28 06:30 | 101.78 | 77.3
2018-01-28 07:00 | 109.58 | 86.04
2018-01-28 07:30 | 108.8 | 85.91
2018-01-28 08:00 | 114.42 | 91.44
2018-01-28 08:30 | 110.98 | 87.11
2018-01-28 09:00 | 114.44 | 90.92
2018-01-28 09:30 | 113.17 | 89.3
2018-01-28 10:00 | 114.52 | 89.66
2018-01-28 10:30 | 115.03 | 90.86
2018-01-28 11:00 | 115.43 | 90.08
2018-01-28 11:30 | 115.62 | 89.1
2018-01-28 12:00 | 118.76 | 93.18
2018-01-28 12:30 | 124.22 | 99.28
2018-01-28 13:00 | 122.08 | 96.33
2018-01-28 13:30 | 114.76 | 89.3
2018-01-28 14:00 | 114.78 | 90.41
2018-01-28 14:30 | 119.59 | 95.29
2018-01-28 15:00 | 114.88 | 90.59
2018-01-28 15:30 | 115.85 | 92.05
2018-01-28 16:00 | 122.74 | 98.53
2018-01-28 16:30 | 121.58 | 97.95
2018-01-28 17:00 | 123.12 | 99.3
2018-01-28 17:30 | 126.94 | 101.62
2018-01-28 18:00 | 128.37 | 103.31
2018-01-28 18:30 | 120.45 | 94.99
2018-01-28 19:00 | 125.12 | 99.54
2018-01-28 19:30 | 131.93 | 104.89
2018-01-28 20:00 | 133.73 | 105.7
2018-01-28 20:30 | 130.58 | 103.29
2018-01-28 21:00 | 127.34 | 102.01
2018-01-28 21:30 | 125.79 | 100.88
2018-01-28 22:00 | 123.69 | 98.95
2018-01-28 22:30 | 122.78 | 98.27
2018-01-28 23:00 | 120.03 | 95.65
2018-01-28 23:30 | 116.12 | 93.23
2018-01-29 | 108.67 | 87.52
2018-01-29 00:30 | 111.9 | 91.05
2018-01-29 01:00 | 115.44 | 94.66
2018-01-29 01:30 | 105.92 | 84.46
2018-01-29 02:00 | 101.73 | 80.8
2018-01-29 02:30 | 101.45 | 80.92
2018-01-29 03:00 | 101.22 | 79.64
2018-01-29 03:30 | 104.31 | 82.74
2018-01-29 04:00 | 106.57 | 85.6
2018-01-29 04:30 | 102.2 | 80.01
2018-01-29 05:00 | 105.16 | 84.12
2018-01-29 05:30 | 104.61 | 83.23
2018-01-29 06:00 | 104.89 | 82.89
2018-01-29 06:30 | 99.16 | 76.17
2018-01-29 07:00 | 106.71 | 85.06
2018-01-29 07:30 | 113.22 | 92.41
2018-01-29 08:00 | 113.6 | 91.52
2018-01-29 08:30 | 110.13 | 86.74
2018-01-29 09:00 | 111.18 | 86.91
2018-01-29 09:30 | 112.99 | 89.69
2018-01-29 10:00 | 117.6 | 94.79
2018-01-29 10:30 | 114.94 | 90.97
2018-01-29 11:00 | 114.04 | 90.22
2018-01-29 11:30 | 111.86 | 87.39
2018-01-29 12:00 | 113.95 | 90.16
2018-01-29 12:30 | 118.79 | 94.29
2018-01-29 13:00 | 124.67 | 98.66
2018-01-29 13:30 | 126.45 | 99.95
2018-01-29 14:00 | 127.68 | 101.05
2018-01-29 14:30 | 122.87 | 96.13
2018-01-29 15:00 | 113.86 | 86.92
2018-01-29 15:30 | 113.93 | 86.71
2018-01-29 16:00 | 121.41 | 94.59
2018-01-29 16:30 | 127.71 | 100.42
2018-01-29 17:00 | 130.4 | 103.14
2018-01-29 17:30 | 120.82 | 94.31
2018-01-29 18:00 | 128.47 | 102.99
2018-01-29 18:30 | 128.77 | 101.27
2018-01-29 19:00 | 133.21 | 107.3
2018-01-29 19:30 | 139.86 | 112.1
2018-01-29 20:00 | 140.98 | 114.01
2018-01-29 20:30 | 134.43 | 107.28
2018-01-29 21:00 | 136.42 | 110.14
2018-01-29 21:30 | 133.49 | 108.34
2018-01-29 22:00 | 135.58 | 109.3
2018-01-29 22:30 | 134.83 | 108.62
2018-01-29 23:00 | 129.22 | 103.61
2018-01-29 23:30 | 121.49 | 96.65
2018-01-30 | 121.66 | 97.31
2018-01-30 00:30 | 125.53 | 101.13
2018-01-30 01:00 | 123.04 | 97.77
2018-01-30 01:30 | 123.18 | 98.9
2018-01-30 02:00 | 124.21 | 100.67
2018-01-30 02:30 | 125.31 | 100.88
2018-01-30 03:00 | 122.67 | 97.95
2018-01-30 03:30 | 129.34 | 105.32
2018-01-30 04:00 | 119.94 | 95.83
2018-01-30 04:30 | 118.98 | 93.45
2018-01-30 05:00 | 116.38 | 90.35
2018-01-30 05:30 | 119.37 | 93.21
2018-01-30 06:00 | 112.53 | 88.74
2018-01-30 06:30 | 112.73 | 87.67
2018-01-30 07:00 | 116.85 | 93.29
2018-01-30 07:30 | 119.67 | 96.36
2018-01-30 08:00 | 117.55 | 94.79
2018-01-30 08:30 | 125.99 | 103.33
2018-01-30 09:00 | 115.87 | 91.77
2018-01-30 09:30 | 120.47 | 97.03
2018-01-30 10:00 | 119.32 | 95.99
2018-01-30 10:30 | 119.64 | 98.2
2018-01-30 11:00 | 124.55 | 101.31
2018-01-30 11:30 | 118.76 | 95.7
2018-01-30 12:00 | 116.01 | 91.51
2018-01-30 12:30 | 122.86 | 99.58
2018-01-30 13:00 | 119.69 | 95.45
2018-01-30 13:30 | 121.01 | 96.88
2018-01-30 14:00 | 116.29 | 91.66
2018-01-30 14:30 | 115.15 | 91.08
2018-01-30 15:00 | 101.13 | 74.59
2018-01-30 15:30 | 103.07 | 77.72
2018-01-30 16:00 | 107.4 | 82.49
2018-01-30 16:30 | 107.66 | 84.88
2018-01-30 17:00 | 121.76 | 99.03
2018-01-30 17:30 | 125.44 | 102.04
2018-01-30 18:00 | 131.19 | 107.22
2018-01-30 18:30 | 125.12 | 99.27
2018-01-30 19:00 | 129.46 | 104.6
2018-01-30 19:30 | 125.88 | 98.48
2018-01-30 20:00 | 128.56 | 102.04
2018-01-30 20:30 | 135.45 | 110.81
2018-01-30 21:00 | 126.96 | 101.82
2018-01-30 21:30 | 114.81 | 90.34
2018-01-30 22:00 | 106.86 | 86.24
2018-01-30 22:30 | 108.31 | 88.13
2018-01-30 23:00 | 108.19 | 88.01
2018-01-30 23:30 | 107.96 | 87.4
2018-01-31 | 114.25 | 93.93
2018-01-31 00:30 | 116.82 | 96.63
2018-01-31 01:00 | 108.43 | 89.32
2018-01-31 01:30 | 113.18 | 94.36
2018-01-31 02:00 | 112.82 | 95.28
2018-01-31 02:30 | 115.27 | 97.75
2018-01-31 03:00 | 109 | 90.45
2018-01-31 03:30 | 110.96 | 92.53
2018-01-31 04:00 | 107.07 | 89.68
2018-01-31 04:30 | 103.4 | 86.65
2018-01-31 05:00 | 111.05 | 94.26
2018-01-31 05:30 | 109.32 | 92.77
2018-01-31 06:00 | 103.16 | 85.82
2018-01-31 06:30 | 95.55 | 77.33
2018-01-31 07:00 | 93.77 | 74.82
2018-01-31 07:30 | 91.22 | 70.63
2018-01-31 08:00 | 85.12 | 63.58
2018-01-31 08:30 | 86.39 | 63.69
2018-01-31 09:00 | 91.36 | 69.54
2018-01-31 09:30 | 94.44 | 73.04
2018-01-31 10:00 | 93.76 | 71.36
2018-01-31 10:30 | 102.67 | 78.84
2018-01-31 11:00 | 115.62 | 91.3
2018-01-31 11:30 | 114.4 | 87.03
2018-01-31 12:00 | 115.13 | 87.54
2018-01-31 12:30 | 113.41 | 87.18
2018-01-31 13:00 | 112.63 | 88.69
2018-01-31 13:30 | 105.34 | 80.8
2018-01-31 14:00 | 107.01 | 83
2018-01-31 14:30 | 104.64 | 81.81
2018-01-31 15:00 | 101.76 | 79.94
2018-01-31 15:30 | 103.78 | 80.15
2018-01-31 16:00 | 109.31 | 83.86
2018-01-31 16:30 | 114.17 | 86.33
2018-01-31 17:00 | 117.69 | 89.34
2018-01-31 17:30 | 125.4 | 99.03
2018-01-31 18:00 | 123.46 | 96.87
2018-01-31 18:30 | 123.82 | 97.54
2018-01-31 19:00 | 132.82 | 108.01
2018-01-31 19:30 | 143.25 | 117.87
2018-01-31 20:00 | 141.19 | 116.41
2018-01-31 20:30 | 134.44 | 110.32
2018-01-31 21:00 | 125.4 | 102.06
2018-01-31 21:30 | 120.7 | 97.81
2018-01-31 22:00 | 127.43 | 104.11
2018-01-31 22:30 | 120.5 | 98.29
2018-01-31 23:00 | 124.44 | 103.34
2018-01-31 23:30 | 130.41 | 108.36
2018-02-01 | 134.14 | 113.35
2018-02-01 00:30 | 130.33 | 108.54
2018-02-01 01:00 | 124.35 | 102.09
2018-02-01 01:30 | 123.08 | 102.35
2018-02-01 02:00 | 126.11 | 105.41
2018-02-01 02:30 | 129.03 | 107.77
2018-02-01 03:00 | 121.29 | 100.17
2018-02-01 03:30 | 123.67 | 102.14
2018-02-01 04:00 | 122.63 | 101.98
2018-02-01 04:30 | 124.62 | 103.47
2018-02-01 05:00 | 127.15 | 107.03
2018-02-01 05:30 | 109.64 | 88.17
2018-02-01 06:00 | 107.29 | 84.88
2018-02-01 06:30 | 112.16 | 90.09
2018-02-01 07:00 | 115.31 | 94.58
2018-02-01 07:30 | 117.33 | 95.08
2018-02-01 08:00 | 118.62 | 96.51
2018-02-01 08:30 | 115.82 | 92.12
2018-02-01 09:00 | 119.28 | 95.66
2018-02-01 09:30 | 124.37 | 101.34
2018-02-01 10:00 | 121.61 | 97.88
2018-02-01 10:30 | 125.28 | 102.66
2018-02-01 11:00 | 127.86 | 104.93
2018-02-01 11:30 | 132.76 | 108.79
2018-02-01 12:00 | 133.02 | 108.39
2018-02-01 12:30 | 129.29 | 104.87
2018-02-01 13:00 | 134.99 | 111.5
2018-02-01 13:30 | 130.49 | 106.72
2018-02-01 14:00 | 133.94 | 110.08
2018-02-01 14:30 | 130.12 | 105.58
2018-02-01 15:00 | 134.14 | 109.26
2018-02-01 15:30 | 135.81 | 110.4
2018-02-01 16:00 | 130.25 | 104.31
2018-02-01 16:30 | 129.59 | 102.87
2018-02-01 17:00 | 127.51 | 99.72
2018-02-01 17:30 | 127.91 | 99.44
2018-02-01 18:00 | 132.37 | 103.6
2018-02-01 18:30 | 132.19 | 103.84
2018-02-01 19:00 | 132.47 | 103.62
2018-02-01 19:30 | 141.6 | 114.97
2018-02-01 20:00 | 136.59 | 112.26
2018-02-01 20:30 | 136.67 | 114.52
2018-02-01 21:00 | 135.32 | 113.77
2018-02-01 21:30 | 132.53 | 111.92
2018-02-01 22:00 | 120.65 | 101.92
2018-02-01 22:30 | 123.7 | 106.1
2018-02-01 23:00 | 119.95 | 102.67
2018-02-01 23:30 | 113.02 | 97.07
2018-02-02 | 118.36 | 100.92
2018-02-02 00:30 | 123.82 | 105.88
2018-02-02 01:00 | 119.07 | 100.48
2018-02-02 01:30 | 125.38 | 105.7
2018-02-02 02:00 | 126.66 | 106.7
2018-02-02 02:30 | 127.45 | 107.31
2018-02-02 03:00 | 129.51 | 110.06
2018-02-02 03:30 | 119.31 | 100.57
2018-02-02 04:00 | 132.14 | 112.78
2018-02-02 04:30 | 127.12 | 107.78
2018-02-02 05:00 | 122.31 | 101.99
2018-02-02 05:30 | 125.07 | 104.84
2018-02-02 06:00 | 125.03 | 105.41
2018-02-02 06:30 | 113.62 | 91.43
2018-02-02 07:00 | 118.57 | 99.42
2018-02-02 07:30 | 128.2 | 108.37
2018-02-02 08:00 | 128.98 | 108.67
2018-02-02 08:30 | 126.5 | 104.79
2018-02-02 09:00 | 136.47 | 114.93
2018-02-02 09:30 | 136.76 | 115.63
2018-02-02 10:00 | 132.21 | 111.29
2018-02-02 10:30 | 130.07 | 108.55
2018-02-02 11:00 | 128.51 | 106.48
2018-02-02 11:30 | 126.3 | 104.29
2018-02-02 12:00 | 126.91 | 104.35
2018-02-02 12:30 | 128.2 | 105.72
2018-02-02 13:00 | 129.42 | 107.87
2018-02-02 13:30 | 128.53 | 104.57
2018-02-02 14:00 | 132.26 | 109.28
2018-02-02 14:30 | 135.05 | 113.66
2018-02-02 15:00 | 131.45 | 110.79
2018-02-02 15:30 | 130.8 | 109.93
2018-02-02 16:00 | 138.51 | 117.36
2018-02-02 16:30 | 135.4 | 114.73
2018-02-02 17:00 | 129.11 | 106.73
2018-02-02 17:30 | 128.11 | 106.14
2018-02-02 18:00 | 126.28 | 104.22
2018-02-02 18:30 | 130.95 | 107.11
2018-02-02 19:00 | 130.8 | 106.34
2018-02-02 19:30 | 132.85 | 107.81
2018-02-02 20:00 | 131.92 | 107.51
2018-02-02 20:30 | 134.09 | 108.55
2018-02-02 21:00 | 129.16 | 103.89
2018-02-02 21:30 | 128.8 | 104.49
2018-02-02 22:00 | 125.81 | 101.41
2018-02-02 22:30 | 123.56 | 98.89
2018-02-02 23:00 | 119.25 | 96.19
2018-02-02 23:30 | 112.46 | 90.48
2018-02-03 | 94.72 | 73.88
2018-02-03 00:30 | 99.81 | 77.86
2018-02-03 01:00 | 97.83 | 75.86
2018-02-03 01:30 | 100.1 | 77.83
2018-02-03 02:00 | 105.15 | 83.86
2018-02-03 02:30 | 107.2 | 85.81
2018-02-03 03:00 | 107.9 | 87.06
2018-02-03 03:30 | 115.64 | 95.24
2018-02-03 04:00 | 120.08 | 98.91
2018-02-03 04:30 | 114.12 | 93.18
2018-02-03 05:00 | 110.64 | 90.25
2018-02-03 05:30 | 109.89 | 90.08
2018-02-03 06:00 | 113.7 | 94.08
2018-02-03 06:30 | 100.88 | 82.25
2018-02-03 07:00 | 100.47 | 80.61
2018-02-03 07:30 | 108.37 | 89.29
2018-02-03 08:00 | 100.67 | 82.33
2018-02-03 08:30 | 101.12 | 83.73
2018-02-03 09:00 | 94.87 | 76.9
2018-02-03 09:30 | 103.83 | 85.6
2018-02-03 10:00 | 101.02 | 82.99
2018-02-03 10:30 | 101.56 | 83.06
2018-02-03 11:00 | 106.22 | 88.25
2018-02-03 11:30 | 100.26 | 81.89
2018-02-03 12:00 | 117.13 | 98.19
2018-02-03 12:30 | 118.47 | 98.14
2018-02-03 13:00 | 113.12 | 91.8
2018-02-03 13:30 | 114.98 | 94.48
2018-02-03 14:00 | 109.14 | 88.04
2018-02-03 14:30 | 114.24 | 92.39
2018-02-03 15:00 | 110.93 | 89.34
2018-02-03 15:30 | 108.39 | 87.57
2018-02-03 16:00 | 103.68 | 82.48
2018-02-03 16:30 | 102.33 | 82.11
2018-02-03 17:00 | 103.09 | 81.92
2018-02-03 17:30 | 107.81 | 86.53
2018-02-03 18:00 | 105.18 | 84.03
2018-02-03 18:30 | 104.58 | 83.76
2018-02-03 19:00 | 104.37 | 83.25
2018-02-03 19:30 | 99.38 | 77.87
2018-02-03 20:00 | 107.62 | 87.43
2018-02-03 20:30 | 114.33 | 94.95
2018-02-03 21:00 | 106.06 | 86.02
2018-02-03 21:30 | 97.89 | 77.34
2018-02-03 22:00 | 100.21 | 83.72
2018-02-03 22:30 | 105.56 | 89.19
2018-02-03 23:00 | 104.75 | 87.79
2018-02-03 23:30 | 102.78 | 86.06
2018-02-04 | 105.48 | 89.64
2018-02-04 00:30 | 102.92 | 86.08
2018-02-04 01:00 | 93.42 | 76.47
2018-02-04 01:30 | 94.08 | 77.61
2018-02-04 02:00 | 96.46 | 79.43
2018-02-04 02:30 | 94.93 | 78.64
2018-02-04 03:00 | 93.43 | 77.63
2018-02-04 03:30 | 88.69 | 73.65
2018-02-04 04:00 | 82.79 | 67.55
2018-02-04 04:30 | 87.09 | 70.18
2018-02-04 05:00 | 87.71 | 70.45
2018-02-04 05:30 | 91.46 | 74.14
2018-02-04 06:00 | 91.03 | 72.15
2018-02-04 06:30 | 90.37 | 71.64
2018-02-04 07:00 | 92.36 | 74.26
2018-02-04 07:30 | 94.73 | 77.34
2018-02-04 08:00 | 95.7 | 77.94
2018-02-04 08:30 | 91.9 | 74.33
2018-02-04 09:00 | 87.43 | 69.21
2018-02-04 09:30 | 87.8 | 68.94
2018-02-04 10:00 | 82.5 | 63.36
2018-02-04 10:30 | 75.59 | 55.15
2018-02-04 11:00 | 76.63 | 55.84
2018-02-04 11:30 | 82.58 | 61.95
2018-02-04 12:00 | 84.32 | 63.74
2018-02-04 12:30 | 79.23 | 58.33
2018-02-04 13:00 | 83.24 | 63.12
2018-02-04 13:30 | 86.26 | 66.54
2018-02-04 14:00 | 85.55 | 65.08
2018-02-04 14:30 | 82.51 | 61.93
2018-02-04 15:00 | 88.26 | 67.97
2018-02-04 15:30 | 97.36 | 78.04
2018-02-04 16:00 | 101.37 | 82.57
2018-02-04 16:30 | 108.22 | 88.98
2018-02-04 17:00 | 101.3 | 81.07
2018-02-04 17:30 | 110.24 | 90.63
2018-02-04 18:00 | 104.15 | 84.32
2018-02-04 18:30 | 95.77 | 75.34
2018-02-04 19:00 | 99.2 | 78.75
2018-02-04 19:30 | 102.11 | 81.02
2018-02-04 20:00 | 109.44 | 89.47
2018-02-04 20:30 | 104.41 | 84.75
2018-02-04 21:00 | 99.51 | 79.96
2018-02-04 21:30 | 99.12 | 79.9
2018-02-04 22:00 | 97.63 | 77.49
2018-02-04 22:30 | 101.99 | 81.93
2018-02-04 23:00 | 91.8 | 72.25
2018-02-04 23:30 | 103.39 | 84.64
2018-02-05 | 101.03 | 81.63
2018-02-05 00:30 | 106.83 | 88.1
2018-02-05 01:00 | 102.82 | 83.66
2018-02-05 01:30 | 98.5 | 79.47
2018-02-05 02:00 | 98.48 | 79.14
2018-02-05 02:30 | 100.84 | 81.55
2018-02-05 03:00 | 100.04 | 80.78
2018-02-05 03:30 | 97.09 | 77.37
2018-02-05 04:00 | 92.92 | 74.56
2018-02-05 04:30 | 98.02 | 80.58
2018-02-05 05:00 | 101.15 | 83.81
2018-02-05 05:30 | 101.72 | 83.63
2018-02-05 06:00 | 94.12 | 74.54
2018-02-05 06:30 | 101.22 | 81.69
2018-02-05 07:00 | 102.56 | 82.74
2018-02-05 07:30 | 105.8 | 85.68
2018-02-05 08:00 | 107.4 | 86.06
2018-02-05 08:30 | 100.31 | 78.56
2018-02-05 09:00 | 104.8 | 83.77
2018-02-05 09:30 | 111.26 | 91.18
2018-02-05 10:00 | 106.29 | 85.5
2018-02-05 10:30 | 105.18 | 83.62
2018-02-05 11:00 | 111.14 | 88.45
2018-02-05 11:30 | 105.75 | 83.56
2018-02-05 12:00 | 110.87 | 89.35
2018-02-05 12:30 | 112.62 | 89.58
2018-02-05 13:00 | 110.89 | 88.99
2018-02-05 13:30 | 114.23 | 92.43
2018-02-05 14:00 | 113.8 | 90.98
2018-02-05 14:30 | 111.78 | 88.85
2018-02-05 15:00 | 109.22 | 86.43
2018-02-05 15:30 | 107.16 | 82.87
2018-02-05 16:00 | 114.76 | 90.64
2018-02-05 16:30 | 112.02 | 89.17
2018-02-05 17:00 | 109.19 | 86.46
2018-02-05 17:30 | 119.25 | 94.61
2018-02-05 18:00 | 114.9 | 90.3
2018-02-05 18:30 | 118.59 | 91.83
2018-02-05 19:00 | 115.58 | 90.25
2018-02-05 19:30 | 125.32 | 101.73
2018-02-05 20:00 | 128.85 | 105.98
2018-02-05 20:30 | 121.3 | 96.92
2018-02-05 21:00 | 117.15 | 93.37
2018-02-05 21:30 | 112.73 | 90.5
2018-02-05 22:00 | 120.11 | 97.21
2018-02-05 22:30 | 115.68 | 94.32
2018-02-05 23:00 | 121.66 | 100.56
2018-02-05 23:30 | 122.83 | 100.75
2018-02-06 | 118.35 | 97.65
2018-02-06 00:30 | 116.4 | 94.43
2018-02-06 01:00 | 111.2 | 87.69
2018-02-06 01:30 | 120.67 | 98.54
2018-02-06 02:00 | 116.26 | 95.08
2018-02-06 02:30 | 114.56 | 91.75
2018-02-06 03:00 | 120.34 | 97.51
2018-02-06 03:30 | 115.19 | 90.69
2018-02-06 04:00 | 126.46 | 103.65
2018-02-06 04:30 | 122.54 | 100.25
2018-02-06 05:00 | 121.15 | 99.66
2018-02-06 05:30 | 122.79 | 103.04
2018-02-06 06:00 | 122.17 | 102.87
2018-02-06 06:30 | 115 | 93.76
2018-02-06 07:00 | 120.97 | 101.45
2018-02-06 07:30 | 120.22 | 101.55
2018-02-06 08:00 | 122.15 | 102.12
2018-02-06 08:30 | 111.75 | 92.17
2018-02-06 09:00 | 111.02 | 90.8
2018-02-06 09:30 | 116.06 | 93.55
2018-02-06 10:00 | 114.49 | 93.21
2018-02-06 10:30 | 120.19 | 99.37
2018-02-06 11:00 | 113.14 | 93.32
2018-02-06 11:30 | 113.15 | 92.75
2018-02-06 12:00 | 112.21 | 91.75
2018-02-06 12:30 | 112.24 | 91.19
2018-02-06 13:00 | 112.44 | 91.23
2018-02-06 13:30 | 114.84 | 93.67
2018-02-06 14:00 | 115.86 | 94.84
2018-02-06 14:30 | 117.32 | 97.26
2018-02-06 15:00 | 120.31 | 99.65
2018-02-06 15:30 | 115.19 | 93.98
2018-02-06 16:00 | 118.75 | 97.35
2018-02-06 16:30 | 115.69 | 94.23
2018-02-06 17:00 | 113.63 | 93
2018-02-06 17:30 | 114.06 | 92.45
2018-02-06 18:00 | 116.88 | 97.12
2018-02-06 18:30 | 104.86 | 83.61
2018-02-06 19:00 | 111.02 | 88.87
2018-02-06 19:30 | 114.33 | 92.12
2018-02-06 20:00 | 109.95 | 87.54
2018-02-06 20:30 | 109.16 | 87.03
2018-02-06 21:00 | 110.51 | 88.05
2018-02-06 21:30 | 107.22 | 85.42
2018-02-06 22:00 | 110.73 | 89.26
2018-02-06 22:30 | 111.87 | 90.65
2018-02-06 23:00 | 112.78 | 90.61
2018-02-06 23:30 | 111.23 | 89.08
2018-02-07 | 111.98 | 89.87
2018-02-07 00:30 | 109.9 | 87.49
2018-02-07 01:00 | 113.79 | 91.4
2018-02-07 01:30 | 116.6 | 94.48
2018-02-07 02:00 | 122.91 | 101.15
2018-02-07 02:30 | 116.68 | 93.62
2018-02-07 03:00 | 113.36 | 92.06
2018-02-07 03:30 | 109.14 | 87.04
2018-02-07 04:00 | 111.98 | 88.91
2018-02-07 04:30 | 114.34 | 92
2018-02-07 05:00 | 108.66 | 85.59
2018-02-07 05:30 | 112 | 90.82
2018-02-07 06:00 | 106.95 | 88.14
2018-02-07 06:30 | 99.4 | 81.77
2018-02-07 07:00 | 101.48 | 82.58
2018-02-07 07:30 | 107.82 | 87.45
2018-02-07 08:00 | 109.86 | 90.28
2018-02-07 08:30 | 98.16 | 78.58
2018-02-07 09:00 | 98.63 | 77.77
2018-02-07 09:30 | 101.39 | 80.19
2018-02-07 10:00 | 94.93 | 77.31
2018-02-07 10:30 | 84.07 | 66.04
2018-02-07 11:00 | 97.07 | 80.18
2018-02-07 11:30 | 93.06 | 76.19
2018-02-07 12:00 | 86.73 | 68.25
2018-02-07 12:30 | 88.24 | 71.43
2018-02-07 13:00 | 90.48 | 73.27
2018-02-07 13:30 | 92.39 | 77.09
2018-02-07 14:00 | 93.08 | 78.16
2018-02-07 14:30 | 93.1 | 78.41
2018-02-07 15:00 | 102.22 | 87.76
2018-02-07 15:30 | 97.86 | 82.65
2018-02-07 16:00 | 89.22 | 74.09
2018-02-07 16:30 | 97.58 | 82.95
2018-02-07 17:00 | 92.95 | 77.96
2018-02-07 17:30 | 99.72 | 84.95
2018-02-07 18:00 | 97.22 | 83.01
2018-02-07 18:30 | 83.24 | 68.23
2018-02-07 19:00 | 86.99 | 71.64
2018-02-07 19:30 | 92.2 | 76.36
2018-02-07 20:00 | 94.4 | 79.4
2018-02-07 20:30 | 97.34 | 82.33
2018-02-07 21:00 | 89.22 | 74.36
2018-02-07 21:30 | 88.69 | 74.22
2018-02-07 22:00 | 87.76 | 72.76
2018-02-07 22:30 | 95.54 | 81.54
2018-02-07 23:00 | 89.82 | 74.93
2018-02-07 23:30 | 100.97 | 86.8
2018-02-08 | 99.05 | 85.01
2018-02-08 00:30 | 100.16 | 86.6
2018-02-08 01:00 | 95.65 | 82.18
2018-02-08 01:30 | 95.67 | 81.15
2018-02-08 02:00 | 96.69 | 82.52
2018-02-08 02:30 | 95.16 | 81.3
2018-02-08 03:00 | 92.03 | 78.26
2018-02-08 03:30 | 95.39 | 81.22
2018-02-08 04:00 | 100.22 | 86.33
2018-02-08 04:30 | 96.03 | 81.95
2018-02-08 05:00 | 95.08 | 80.36
2018-02-08 05:30 | 90.76 | 74.84
2018-02-08 06:00 | 88.74 | 73.68
2018-02-08 06:30 | 78.94 | 62.02
2018-02-08 07:00 | 90.89 | 75.33
2018-02-08 07:30 | 92.29 | 75.68
2018-02-08 08:00 | 89.24 | 72.29
2018-02-08 08:30 | 89.03 | 73.05
2018-02-08 09:00 | 90.65 | 75.67
2018-02-08 09:30 | 81.74 | 68.83
2018-02-08 10:00 | 89.27 | 76.76
2018-02-08 10:30 | 88.86 | 73.79
2018-02-08 11:00 | 94.85 | 79.15
2018-02-08 11:30 | 97.25 | 82.01
2018-02-08 12:00 | 100.93 | 84.56
2018-02-08 12:30 | 97.43 | 80.99
2018-02-08 13:00 | 98.12 | 82.46
2018-02-08 13:30 | 100.98 | 84.9
2018-02-08 14:00 | 100.48 | 83.98
2018-02-08 14:30 | 104.8 | 88.7
2018-02-08 15:00 | 106.97 | 89.68
2018-02-08 15:30 | 101.41 | 85.56
2018-02-08 16:00 | 108.46 | 92.4
2018-02-08 16:30 | 107.61 | 92.01
2018-02-08 17:00 | 108.29 | 89.85
2018-02-08 17:30 | 109.8 | 90.66
2018-02-08 18:00 | 114.69 | 96.4
2018-02-08 18:30 | 103.32 | 85.48
2018-02-08 19:00 | 110.31 | 92.71
2018-02-08 19:30 | 113.79 | 92.96
2018-02-08 20:00 | 123.38 | 103.42
2018-02-08 20:30 | 116.24 | 97.85
2018-02-08 21:00 | 114.04 | 96.38
2018-02-08 21:30 | 119.1 | 102.02
2018-02-08 22:00 | 117.05 | 98.87
2018-02-08 22:30 | 113.03 | 94.82
2018-02-08 23:00 | 110.65 | 92.92
2018-02-08 23:30 | 112.25 | 95.46
2018-02-09 | 110.34 | 95.03
2018-02-09 00:30 | 113.42 | 97.36
2018-02-09 01:00 | 107.34 | 91.03
2018-02-09 01:30 | 107.58 | 91.47
2018-02-09 02:00 | 108.33 | 91.02
2018-02-09 02:30 | 111.04 | 93.51
2018-02-09 03:00 | 102.05 | 83.63
2018-02-09 03:30 | 98.97 | 80.49
2018-02-09 04:00 | 107.64 | 90.92
2018-02-09 04:30 | 108.78 | 92.8
2018-02-09 05:00 | 110.63 | 94.64
2018-02-09 05:30 | 111.55 | 94.79
2018-02-09 06:00 | 110.74 | 93.92
2018-02-09 06:30 | 111.6 | 93.94
2018-02-09 07:00 | 115.77 | 98.86
2018-02-09 07:30 | 125.24 | 109.1
2018-02-09 08:00 | 116.92 | 100.46
2018-02-09 08:30 | 115.76 | 98.92
2018-02-09 09:00 | 113.02 | 95.84
2018-02-09 09:30 | 117.2 | 99.14
2018-02-09 10:00 | 118.5 | 100.21
2018-02-09 10:30 | 112.62 | 93.78
2018-02-09 11:00 | 106.35 | 90.17
2018-02-09 11:30 | 117.33 | 98.25
2018-02-09 12:00 | 118.05 | 98.46
2018-02-09 12:30 | 126.78 | 107.63
2018-02-09 13:00 | 122.08 | 102.91
2018-02-09 13:30 | 115.82 | 96
2018-02-09 14:00 | 120.71 | 102.17
2018-02-09 14:30 | 127.05 | 108.69
2018-02-09 15:00 | 127.6 | 108.57
2018-02-09 15:30 | 122.73 | 103.62
2018-02-09 16:00 | 129.58 | 110.79
2018-02-09 16:30 | 130.57 | 112.46
2018-02-09 17:00 | 128.71 | 111.42
2018-02-09 17:30 | 129.94 | 113.28
2018-02-09 18:00 | 139.23 | 122.68
2018-02-09 18:30 | 118.74 | 101.26
2018-02-09 19:00 | 116.6 | 101.52
2018-02-09 19:30 | 114.94 | 99.38
2018-02-09 20:00 | 108.44 | 93.11
2018-02-09 20:30 | 102.87 | 85.96
2018-02-09 21:00 | 119.87 | 101.53
2018-02-09 21:30 | 124.31 | 105.53
2018-02-09 22:00 | 123.92 | 106.11
2018-02-09 22:30 | 121.71 | 104.27
2018-02-09 23:00 | 118.19 | 101.76
2018-02-09 23:30 | 112.58 | 96.08
2018-02-10 | 116.42 | 100.59
2018-02-10 00:30 | 122.94 | 106.7
2018-02-10 01:00 | 129.08 | 113
2018-02-10 01:30 | 115.93 | 99.58
2018-02-10 02:00 | 122.96 | 107.09
2018-02-10 02:30 | 120.07 | 104.6
2018-02-10 03:00 | 113.22 | 97
2018-02-10 03:30 | 108.17 | 90.18
2018-02-10 04:00 | 115.36 | 98.3
2018-02-10 04:30 | 117.57 | 101.63
2018-02-10 05:00 | 117.9 | 102.02
2018-02-10 05:30 | 119.14 | 103.48
2018-02-10 06:00 | 103.66 | 85.16
2018-02-10 06:30 | 102.83 | 83.78
2018-02-10 07:00 | 109.58 | 91.05
2018-02-10 07:30 | 109.86 | 92.13
2018-02-10 08:00 | 109.29 | 91.68
2018-02-10 08:30 | 106.9 | 89.17
2018-02-10 09:00 | 107.85 | 90.29
2018-02-10 09:30 | 107.78 | 91.4
2018-02-10 10:00 | 103.96 | 86.52
2018-02-10 10:30 | 106.92 | 88.66
2018-02-10 11:00 | 108.51 | 89.7
2018-02-10 11:30 | 105.83 | 87.84
2018-02-10 12:00 | 114.85 | 96.12
2018-02-10 12:30 | 116.08 | 94.87
2018-02-10 13:00 | 118.97 | 99.06
2018-02-10 13:30 | 126.52 | 104.69
2018-02-10 14:00 | 121.05 | 100.64
2018-02-10 14:30 | 127.21 | 106.32
2018-02-10 15:00 | 121.24 | 99.59
2018-02-10 15:30 | 121.05 | 98.48
2018-02-10 16:00 | 125.39 | 104.44
2018-02-10 16:30 | 128.81 | 109.03
2018-02-10 17:00 | 126.43 | 105.7
2018-02-10 17:30 | 128.84 | 108.65
2018-02-10 18:00 | 128.29 | 107.7
2018-02-10 18:30 | 121.91 | 101.49
2018-02-10 19:00 | 125.26 | 105.75
2018-02-10 19:30 | 125.85 | 104.55
2018-02-10 20:00 | 130.29 | 109.03
2018-02-10 20:30 | 127.49 | 106.42
2018-02-10 21:00 | 122.31 | 101.35
2018-02-10 21:30 | 123.5 | 103.19
2018-02-10 22:00 | 118.71 | 98.57
2018-02-10 22:30 | 119.87 | 99.6
2018-02-10 23:00 | 114.12 | 94.35
2018-02-10 23:30 | 117.66 | 98.81
2018-02-11 | 121.08 | 101.32
2018-02-11 00:30 | 119.74 | 101.18
2018-02-11 01:00 | 110.82 | 92.22
2018-02-11 01:30 | 115.01 | 96.82
2018-02-11 02:00 | 112.67 | 95.08
2018-02-11 02:30 | 114.4 | 96.14
2018-02-11 03:00 | 112.73 | 95.66
2018-02-11 03:30 | 112.18 | 94.37
2018-02-11 04:00 | 108.67 | 90.48
2018-02-11 04:30 | 108.57 | 90.06
2018-02-11 05:00 | 111.02 | 93.01
2018-02-11 05:30 | 114.35 | 97.09
2018-02-11 06:00 | 115.11 | 97.78
2018-02-11 06:30 | 103.9 | 85.42
2018-02-11 07:00 | 111.12 | 92.96
2018-02-11 07:30 | 108.55 | 90.46
2018-02-11 08:00 | 113.19 | 96.28
2018-02-11 08:30 | 112.21 | 93.83
2018-02-11 09:00 | 107.8 | 89.01
2018-02-11 09:30 | 106.16 | 88.46
2018-02-11 10:00 | 120.81 | 102.95
2018-02-11 10:30 | 118.04 | 99.7
2018-02-11 11:00 | 124.68 | 107.01
2018-02-11 11:30 | 122.48 | 103.93
2018-02-11 12:00 | 117.84 | 98.73
2018-02-11 12:30 | 116.37 | 97.23
2018-02-11 13:00 | 116.74 | 98.78
2018-02-11 13:30 | 112.78 | 97.45
2018-02-11 14:00 | 115.27 | 99.93
2018-02-11 14:30 | 125.28 | 108.26
2018-02-11 15:00 | 120.93 | 102.07
2018-02-11 15:30 | 111.83 | 91.48
2018-02-11 16:00 | 116.04 | 94.87
2018-02-11 16:30 | 117.8 | 94.46
2018-02-11 17:00 | 123.15 | 102.97
2018-02-11 17:30 | 126.67 | 107.64
2018-02-11 18:00 | 126.28 | 105.97
2018-02-11 18:30 | 118.18 | 96.73
2018-02-11 19:00 | 124.07 | 102.47
2018-02-11 19:30 | 132.09 | 110.49
2018-02-11 20:00 | 124.64 | 101.45
2018-02-11 20:30 | 130.14 | 108.65
2018-02-11 21:00 | 134.41 | 115.19
2018-02-11 21:30 | 132.05 | 113.47
2018-02-11 22:00 | 131.18 | 113.28
2018-02-11 22:30 | 120.75 | 101.62
2018-02-11 23:00 | 119.43 | 100.53
2018-02-11 23:30 | 118.62 | 101.14
2018-02-12 | 113.66 | 96.55
2018-02-12 00:30 | 114.96 | 96.99
2018-02-12 01:00 | 110.77 | 92.69
2018-02-12 01:30 | 111.81 | 94.31
2018-02-12 02:00 | 108.76 | 91.63
2018-02-12 02:30 | 109.99 | 93.67
2018-02-12 03:00 | 109.42 | 93.6
2018-02-12 03:30 | 100.29 | 83.65
2018-02-12 04:00 | 99.54 | 84.09
2018-02-12 04:30 | 91.11 | 76.34
2018-02-12 05:00 | 94.68 | 80.6
2018-02-12 05:30 | 93.55 | 78.42
2018-02-12 06:00 | 90.5 | 74.39
2018-02-12 06:30 | 85.58 | 67.85
2018-02-12 07:00 | 93.12 | 75.71
2018-02-12 07:30 | 102.48 | 85.39
2018-02-12 08:00 | 101.96 | 85.08
2018-02-12 08:30 | 101.13 | 84.1
2018-02-12 09:00 | 103.73 | 86.1
2018-02-12 09:30 | 102.66 | 85.41
2018-02-12 10:00 | 105.96 | 88.65
2018-02-12 10:30 | 105.09 | 86.77
2018-02-12 11:00 | 109.85 | 91.61
2018-02-12 11:30 | 110.27 | 90.76
2018-02-12 12:00 | 119.38 | 97.59
2018-02-12 12:30 | 122.04 | 100.2
2018-02-12 13:00 | 117.07 | 95.23
2018-02-12 13:30 | 122.48 | 99.17
2018-02-12 14:00 | 124.75 | 100.88
2018-02-12 14:30 | 126.77 | 103.94
2018-02-12 15:00 | 118.99 | 93.84
2018-02-12 15:30 | 116.55 | 92.89
2018-02-12 16:00 | 116.7 | 92.96
2018-02-12 16:30 | 115.69 | 92.55
2018-02-12 17:00 | 122.35 | 97.9
2018-02-12 17:30 | 120.49 | 95.38
2018-02-12 18:00 | 119.13 | 95.93
2018-02-12 18:30 | 114.75 | 91.93
2018-02-12 19:00 | 130.22 | 106.9
2018-02-12 19:30 | 131.36 | 107.72
2018-02-12 20:00 | 131.84 | 106.34
2018-02-12 20:30 | 132.29 | 107.77
2018-02-12 21:00 | 130.43 | 106.75
2018-02-12 21:30 | 118.98 | 94.86
2018-02-12 22:00 | 115.56 | 93.35
2018-02-12 22:30 | 103.72 | 80.1
2018-02-12 23:00 | 103.44 | 81.96
2018-02-12 23:30 | 107.38 | 87.06
2018-02-13 | 105.08 | 85.55
2018-02-13 00:30 | 100.98 | 81.02
2018-02-13 01:00 | 107.44 | 88.25
2018-02-13 01:30 | 102.63 | 81.84
2018-02-13 02:00 | 111.72 | 92.43
2018-02-13 02:30 | 108.84 | 89.2
2018-02-13 03:00 | 106.24 | 84.86
2018-02-13 03:30 | 106.04 | 84.57
2018-02-13 04:00 | 106.7 | 86.23
2018-02-13 04:30 | 111.07 | 90.98
2018-02-13 05:00 | 112.04 | 92.31
2018-02-13 05:30 | 114.37 | 94.8
2018-02-13 06:00 | 113.7 | 94.1
2018-02-13 06:30 | 108.69 | 87.73
2018-02-13 07:00 | 109.22 | 88.63
2018-02-13 07:30 | 114.2 | 92.66
2018-02-13 08:00 | 117.65 | 95.48
2018-02-13 08:30 | 119.55 | 98.74
2018-02-13 09:00 | 115.92 | 94.4
2018-02-13 09:30 | 114.66 | 91.47
2018-02-13 10:00 | 108.59 | 83.4
2018-02-13 10:30 | 108.95 | 82.8
2018-02-13 11:00 | 116.17 | 93.42
2018-02-13 11:30 | 114.56 | 92.1
2018-02-13 12:00 | 116.8 | 95.28
2018-02-13 12:30 | 121.81 | 99.21
2018-02-13 13:00 | 121.78 | 99.82
2018-02-13 13:30 | 120.83 | 99.94
2018-02-13 14:00 | 120.82 | 99.75
2018-02-13 14:30 | 126.04 | 102.87
2018-02-13 15:00 | 126.93 | 103.17
2018-02-13 15:30 | 118.83 | 96.71
2018-02-13 16:00 | 114.37 | 92.41
2018-02-13 16:30 | 114.79 | 94.34
2018-02-13 17:00 | 118.14 | 97.76
2018-02-13 17:30 | 120.28 | 101.26
2018-02-13 18:00 | 125.45 | 106.4
2018-02-13 18:30 | 120.27 | 99.63
2018-02-13 19:00 | 114.41 | 95.47
2018-02-13 19:30 | 125.53 | 106.82
2018-02-13 20:00 | 132.79 | 114.21
2018-02-13 20:30 | 125.38 | 105.73
2018-02-13 21:00 | 131.35 | 111.62
2018-02-13 21:30 | 123.01 | 103.46
2018-02-13 22:00 | 121.98 | 103.38
2018-02-13 22:30 | 122.03 | 104.29
2018-02-13 23:00 | 117.28 | 99.64
2018-02-13 23:30 | 115.51 | 97.49
2018-02-14 | 121.6 | 103.07
2018-02-14 00:30 | 115.79 | 97.45
2018-02-14 01:00 | 112.97 | 94.29
2018-02-14 01:30 | 113.39 | 94.63
2018-02-14 02:00 | 112 | 94.26
2018-02-14 02:30 | 112.98 | 96.48
2018-02-14 03:00 | 110.78 | 93.58
2018-02-14 03:30 | 107.65 | 89.48
2018-02-14 04:00 | 108.76 | 91.35
2018-02-14 04:30 | 111.98 | 94.99
2018-02-14 05:00 | 108.17 | 90.97
2018-02-14 05:30 | 107.92 | 90.33
2018-02-14 06:00 | 105.86 | 88
2018-02-14 06:30 | 97.99 | 79.47
2018-02-14 07:00 | 100.97 | 82.69
2018-02-14 07:30 | 105.85 | 88.03
2018-02-14 08:00 | 110.21 | 92.77
2018-02-14 08:30 | 106.03 | 88.06
2018-02-14 09:00 | 106.5 | 88.38
2018-02-14 09:30 | 104.11 | 85.34
2018-02-14 10:00 | 109.45 | 91.96
2018-02-14 10:30 | 112.98 | 94.02
2018-02-14 11:00 | 117.46 | 99.72
2018-02-14 11:30 | 117.63 | 99.54
2018-02-14 12:00 | 118.82 | 99.02
2018-02-14 12:30 | 119.09 | 100.5
2018-02-14 13:00 | 114.3 | 95.05
2018-02-14 13:30 | 115.17 | 95.26
2018-02-14 14:00 | 124.04 | 103.94
2018-02-14 14:30 | 120.47 | 100.31
2018-02-14 15:00 | 115.59 | 94.62
2018-02-14 15:30 | 114.01 | 93.87
2018-02-14 16:00 | 111.26 | 91.84
2018-02-14 16:30 | 107.36 | 87.23
2018-02-14 17:00 | 114.99 | 96.54
2018-02-14 17:30 | 115.73 | 97.19
2018-02-14 18:00 | 108.64 | 89.83
2018-02-14 18:30 | 105.66 | 86.21
2018-02-14 19:00 | 111.15 | 92.13
2018-02-14 19:30 | 112.53 | 92.71
2018-02-14 20:00 | 116.81 | 96.24
2018-02-14 20:30 | 117.2 | 95.8
2018-02-14 21:00 | 112.54 | 90.33
2018-02-14 21:30 | 116.54 | 95.67
2018-02-14 22:00 | 110.4 | 90.48
2018-02-14 22:30 | 110.56 | 91.55
2018-02-14 23:00 | 106.67 | 87.78
2018-02-14 23:30 | 104.75 | 85.59
2018-02-15 | 109.07 | 90.58
2018-02-15 00:30 | 105.7 | 86.79
2018-02-15 01:00 | 115.6 | 96.42
2018-02-15 01:30 | 104.81 | 86.23
2018-02-15 02:00 | 107.73 | 88.06
2018-02-15 02:30 | 106.8 | 87.98
2018-02-15 03:00 | 108.91 | 91.24
2018-02-15 03:30 | 105.65 | 86.64
2018-02-15 04:00 | 105.19 | 86.28
2018-02-15 04:30 | 109.79 | 91.29
2018-02-15 05:00 | 104.59 | 85.6
2018-02-15 05:30 | 105.93 | 88.05
2018-02-15 06:00 | 104.77 | 86.78
2018-02-15 06:30 | 108.46 | 88.47
2018-02-15 07:00 | 111.49 | 92.17
2018-02-15 07:30 | 103.08 | 83.49
2018-02-15 08:00 | 100.83 | 80.91
2018-02-15 08:30 | 106.47 | 85.97
2018-02-15 09:00 | 110.81 | 90.57
2018-02-15 09:30 | 114.68 | 94.55
2018-02-15 10:00 | 123.46 | 104.23
2018-02-15 10:30 | 121.59 | 102.18
2018-02-15 11:00 | 120.77 | 100.47
2018-02-15 11:30 | 119.75 | 99.31
2018-02-15 12:00 | 116.23 | 95.58
2018-02-15 12:30 | 114.04 | 93.79
2018-02-15 13:00 | 119.76 | 99.51
2018-02-15 13:30 | 130.01 | 108.83
2018-02-15 14:00 | 129.82 | 106.85
2018-02-15 14:30 | 127.87 | 104.23
2018-02-15 15:00 | 127.85 | 104.74
2018-02-15 15:30 | 115.06 | 92.15
2018-02-15 16:00 | 122.16 | 97.08
2018-02-15 16:30 | 122.46 | 99.14
2018-02-15 17:00 | 126.24 | 101.89
2018-02-15 17:30 | 126.79 | 101.08
2018-02-15 18:00 | 123.8 | 99.08
2018-02-15 18:30 | 124.13 | 99.78
2018-02-15 19:00 | 126.61 | 102.42
2018-02-15 19:30 | 128.79 | 102.98
2018-02-15 20:00 | 138.4 | 111
2018-02-15 20:30 | 125.66 | 96.53
2018-02-15 21:00 | 132.1 | 102.25
2018-02-15 21:30 | 126.5 | 99.55
2018-02-15 22:00 | 127.43 | 99.09
2018-02-15 22:30 | 117.92 | 89.49
2018-02-15 23:00 | 114.8 | 87.47
2018-02-15 23:30 | 117.34 | 90.97
2018-02-16 | 115.19 | 89.43
2018-02-16 00:30 | 118.41 | 93.21
2018-02-16 01:00 | 121.69 | 96.36
2018-02-16 01:30 | 119.75 | 93.85
2018-02-16 02:00 | 119.02 | 91.98
2018-02-16 02:30 | 121.13 | 94.86
2018-02-16 03:00 | 119.65 | 93.3
2018-02-16 03:30 | 115.82 | 87.35
2018-02-16 04:00 | 121.45 | 95.05
2018-02-16 04:30 | 115.86 | 92.01
2018-02-16 05:00 | 119.02 | 94.92
2018-02-16 05:30 | 126.16 | 103.22
2018-02-16 06:00 | 120.43 | 96.72
2018-02-16 06:30 | 119.73 | 94.41
2018-02-16 07:00 | 118.55 | 91.64
2018-02-16 07:30 | 116.93 | 92.56
2018-02-16 08:00 | 122.43 | 98.02
2018-02-16 08:30 | 133.62 | 107.42
2018-02-16 09:00 | 126.5 | 99.44
2018-02-16 09:30 | 124.58 | 96.95
2018-02-16 10:00 | 127.66 | 100.07
2018-02-16 10:30 | 128.04 | 101.48
2018-02-16 11:00 | 125.06 | 96.75
2018-02-16 11:30 | 130.42 | 101.44
2018-02-16 12:00 | 129.33 | 98.72
2018-02-16 12:30 | 125.97 | 95.56
2018-02-16 13:00 | 127.34 | 97.9
2018-02-16 13:30 | 122.67 | 94.66
2018-02-16 14:00 | 124.94 | 94.85
2018-02-16 14:30 | 127.02 | 96.01
2018-02-16 15:00 | 125.78 | 96.51
2018-02-16 15:30 | 126.61 | 96.5
2018-02-16 16:00 | 120.36 | 91.1
2018-02-16 16:30 | 119.88 | 92.02
2018-02-16 17:00 | 113.35 | 86.28
2018-02-16 17:30 | 106.68 | 82.5
2018-02-16 18:00 | 98.6 | 72.94
2018-02-16 18:30 | 97.96 | 74.04
2018-02-16 19:00 | 106.79 | 82.51
2018-02-16 19:30 | 111.91 | 88.67
2018-02-16 20:00 | 108.42 | 86.14
2018-02-16 20:30 | 109.97 | 88.75
2018-02-16 21:00 | 114.26 | 90.83
2018-02-16 21:30 | 119.99 | 98.06
2018-02-16 22:00 | 119.02 | 98.59
2018-02-16 22:30 | 126.59 | 106.1
2018-02-16 23:00 | 123.56 | 103.37
2018-02-16 23:30 | 120.6 | 101.34
2018-02-17 | 120.33 | 101.58
2018-02-17 00:30 | 122.3 | 105.01
2018-02-17 01:00 | 109.8 | 92.04
2018-02-17 01:30 | 110.68 | 92.15
2018-02-17 02:00 | 114.96 | 96.2
2018-02-17 02:30 | 115.26 | 96.65
2018-02-17 03:00 | 120.62 | 101.24
2018-02-17 03:30 | 122.75 | 103.2
2018-02-17 04:00 | 119.64 | 102.11
2018-02-17 04:30 | 122.28 | 106.47
2018-02-17 05:00 | 117.96 | 101.16
2018-02-17 05:30 | 115.22 | 96.57
2018-02-17 06:00 | 120.29 | 101.32
2018-02-17 06:30 | 114.07 | 94.03
2018-02-17 07:00 | 123.99 | 104.64
2018-02-17 07:30 | 117.58 | 98.35
2018-02-17 08:00 | 120.36 | 100.98
2018-02-17 08:30 | 129.23 | 108.43
2018-02-17 09:00 | 128.22 | 107.99
2018-02-17 09:30 | 122.34 | 102.18
2018-02-17 10:00 | 112.13 | 92.29
2018-02-17 10:30 | 113.92 | 92.8
2018-02-17 11:00 | 110.41 | 89.16
2018-02-17 11:30 | 118.25 | 96.87
2018-02-17 12:00 | 118.99 | 99.17
2018-02-17 12:30 | 118.61 | 99.23
2018-02-17 13:00 | 127.01 | 106.77
2018-02-17 13:30 | 119.11 | 100.01
2018-02-17 14:00 | 118.32 | 97.95
2018-02-17 14:30 | 117.43 | 97.83
2018-02-17 15:00 | 116.34 | 96.22
2018-02-17 15:30 | 118.08 | 97.77
2018-02-17 16:00 | 116.38 | 96.26
2018-02-17 16:30 | 88.32 | 66.2
2018-02-17 17:00 | 69.9 | 51.67
2018-02-17 17:30 | 64.36 | 46.8
2018-02-17 18:00 | 69 | 50.45
2018-02-17 18:30 | 73.44 | 55.36
2018-02-17 19:00 | 77.67 | 59.42
2018-02-17 19:30 | 85.06 | 64.95
2018-02-17 20:00 | 85.83 | 65.05
2018-02-17 20:30 | 93.57 | 66.93
2018-02-17 21:00 | 96.67 | 70.72
2018-02-17 21:30 | 97.84 | 73.58
2018-02-17 22:00 | 93.67 | 68.97
2018-02-17 22:30 | 97 | 73.42
2018-02-17 23:00 | 98 | 78.02
2018-02-17 23:30 | 90.88 | 71.39
2018-02-18 | 99.64 | 80.77
2018-02-18 00:30 | 98.83 | 78.64
2018-02-18 01:00 | 105.85 | 86.61
2018-02-18 01:30 | 96.19 | 75.55
2018-02-18 02:00 | 100.12 | 79.54
2018-02-18 02:30 | 102.13 | 81.19
2018-02-18 03:00 | 109.38 | 92.63
2018-02-18 03:30 | 111.85 | 95.15
2018-02-18 04:00 | 115.8 | 99.68
2018-02-18 04:30 | 112.28 | 95.2
2018-02-18 05:00 | 109.11 | 93.21
2018-02-18 05:30 | 118.67 | 102.75
2018-02-18 06:00 | 111.58 | 95.78
2018-02-18 06:30 | 103.37 | 86.43
2018-02-18 07:00 | 109.21 | 93.59
2018-02-18 07:30 | 113.48 | 97.98
2018-02-18 08:00 | 107.4 | 90.55
2018-02-18 08:30 | 115.26 | 98.37
2018-02-18 09:00 | 115.58 | 99.02
2018-02-18 09:30 | 109.02 | 92.95
2018-02-18 10:00 | 115.74 | 99.72
2018-02-18 10:30 | 120.67 | 102.99
2018-02-18 11:00 | 125.65 | 108.23
2018-02-18 11:30 | 121.5 | 103.71
2018-02-18 12:00 | 114.77 | 97.35
2018-02-18 12:30 | 112.93 | 93.45
2018-02-18 13:00 | 116.27 | 94.7
2018-02-18 13:30 | 120.62 | 96.99
2018-02-18 14:00 | 120.57 | 98.4
2018-02-18 14:30 | 124.05 | 102.96
2018-02-18 15:00 | 116.35 | 94.89
2018-02-18 15:30 | 114.62 | 92.94
2018-02-18 16:00 | 110.45 | 88.28
2018-02-18 16:30 | 117.1 | 95.01
2018-02-18 17:00 | 124.64 | 102.3
2018-02-18 17:30 | 129.35 | 106.54
2018-02-18 18:00 | 126.7 | 103.32
2018-02-18 18:30 | 119.39 | 91.72
2018-02-18 19:00 | 120.63 | 93.48
2018-02-18 19:30 | 128.23 | 101.71
2018-02-18 20:00 | 124.26 | 95.72
2018-02-18 20:30 | 121.71 | 95.51
2018-02-18 21:00 | 116.66 | 91.6
2018-02-18 21:30 | 115.4 | 91.7
2018-02-18 22:00 | 117.41 | 91.98
2018-02-18 22:30 | 115.27 | 89.56
2018-02-18 23:00 | 121.33 | 97.75
2018-02-18 23:30 | 118.11 | 93.23
2018-02-19 | 119.78 | 95.74
2018-02-19 00:30 | 113.4 | 90.25
2018-02-19 01:00 | 113.02 | 88.92
2018-02-19 01:30 | 111.93 | 89.26
2018-02-19 02:00 | 117.85 | 95.23
2018-02-19 02:30 | 117.14 | 94.38
2018-02-19 03:00 | 118.15 | 96.37
2018-02-19 03:30 | 120.23 | 98.77
2018-02-19 04:00 | 112.11 | 91.74
2018-02-19 04:30 | 113.95 | 93.8
2018-02-19 05:00 | 126.38 | 106.59
2018-02-19 05:30 | 115.38 | 95.21
2018-02-19 06:00 | 114.57 | 93.81
2018-02-19 06:30 | 104.99 | 83.2
2018-02-19 07:00 | 115.54 | 94.94
2018-02-19 07:30 | 118.3 | 97.6
2018-02-19 08:00 | 113.84 | 92.25
2018-02-19 08:30 | 119.03 | 96.89
2018-02-19 09:00 | 117.68 | 96.13
2018-02-19 09:30 | 119.25 | 98.35
2018-02-19 10:00 | 125.89 | 104.22
2018-02-19 10:30 | 124.25 | 101.74
2018-02-19 11:00 | 128.95 | 105.37
2018-02-19 11:30 | 125.07 | 102.88
2018-02-19 12:00 | 125.89 | 104.49
2018-02-19 12:30 | 132.75 | 111.61
2018-02-19 13:00 | 130.09 | 107.94
2018-02-19 13:30 | 123.01 | 105.49
2018-02-19 14:00 | 122.03 | 104.43
2018-02-19 14:30 | 120.87 | 103.86
2018-02-19 15:00 | 124.78 | 103.66
2018-02-19 15:30 | 125.69 | 105.28
2018-02-19 16:00 | 125.61 | 105.26
2018-02-19 16:30 | 113.09 | 92.08
2018-02-19 17:00 | 114.16 | 91.17
2018-02-19 17:30 | 115.82 | 92.62
2018-02-19 18:00 | 120.4 | 98.6
2018-02-19 18:30 | 119.4 | 96.5
2018-02-19 19:00 | 123.6 | 101.43
2018-02-19 19:30 | 121.6 | 99.67
2018-02-19 20:00 | 117.73 | 93.95
2018-02-19 20:30 | 116.88 | 93.58
2018-02-19 21:00 | 109.05 | 86.88
2018-02-19 21:30 | 110.3 | 88.36
2018-02-19 22:00 | 113.62 | 93.17
2018-02-19 22:30 | 112.22 | 91.82
2018-02-19 23:00 | 111.39 | 88.37
2018-02-19 23:30 | 112.26 | 90.23
2018-02-20 | 105.39 | 85.55
2018-02-20 00:30 | 107.27 | 87.02
2018-02-20 01:00 | 105.19 | 83.61
2018-02-20 01:30 | 112.07 | 91.16
2018-02-20 02:00 | 112.03 | 92.98
2018-02-20 02:30 | 103.75 | 84.09
2018-02-20 03:00 | 104.37 | 84.93
2018-02-20 03:30 | 108.23 | 90.15
2018-02-20 04:00 | 108.6 | 90.59
2018-02-20 04:30 | 116.46 | 98.37
2018-02-20 05:00 | 115.78 | 98.25
2018-02-20 05:30 | 109.79 | 94.24
2018-02-20 06:00 | 108.98 | 92.91
2018-02-20 06:30 | 112.54 | 94.94
2018-02-20 07:00 | 110.25 | 92.45
2018-02-20 07:30 | 118.37 | 98.52
2018-02-20 08:00 | 108.69 | 87.23
2018-02-20 08:30 | 111.05 | 89.57
2018-02-20 09:00 | 106.4 | 85.78
2018-02-20 09:30 | 107.63 | 85.93
2018-02-20 10:00 | 104.54 | 82.89
2018-02-20 10:30 | 107.33 | 85.08
2018-02-20 11:00 | 110.04 | 87.73
2018-02-20 11:30 | 107.32 | 84.68
2018-02-20 12:00 | 123.14 | 102.1
2018-02-20 12:30 | 117.78 | 96.85
2018-02-20 13:00 | 106.7 | 85.66
2018-02-20 13:30 | 107.18 | 84.97
2018-02-20 14:00 | 109.09 | 87.48
2018-02-20 14:30 | 112.11 | 90.1
2018-02-20 15:00 | 100.93 | 80.54
2018-02-20 15:30 | 87.75 | 68.48
2018-02-20 16:00 | 104.34 | 86.93
2018-02-20 16:30 | 87.3 | 65.1
2018-02-20 17:00 | 75.93 | 52
2018-02-20 17:30 | 72.23 | 50.8
2018-02-20 18:00 | 61.02 | 39.67
2018-02-20 18:30 | 63.65 | 42.77
2018-02-20 19:00 | 63.74 | 42.64
2018-02-20 19:30 | 64.91 | 46.02
2018-02-20 20:00 | 67.75 | 48.68
2018-02-20 20:30 | 63.78 | 45.14
2018-02-20 21:00 | 63.33 | 44.26
2018-02-20 21:30 | 64.81 | 47.1
2018-02-20 22:00 | 62.82 | 45.88
2018-02-20 22:30 | 66.29 | 48.95
2018-02-20 23:00 | 68.82 | 49.69
2018-02-20 23:30 | 68.91 | 46.78
2018-02-21 | 70.25 | 43.8
2018-02-21 00:30 | 72.76 | 45.11
2018-02-21 01:00 | 77.29 | 52.57
2018-02-21 01:30 | 73.57 | 49.99
2018-02-21 02:00 | 81.63 | 59.68
2018-02-21 02:30 | 86.24 | 63.47
2018-02-21 03:00 | 88.29 | 66.07
2018-02-21 03:30 | 81.6 | 60.14
2018-02-21 04:00 | 81.79 | 58.27
2018-02-21 04:30 | 87.25 | 63.36
2018-02-21 05:00 | 85.84 | 62.07
2018-02-21 05:30 | 89.91 | 67.01
2018-02-21 06:00 | 89.74 | 67.02
2018-02-21 06:30 | 84.19 | 58.88
2018-02-21 07:00 | 81.14 | 56.56
2018-02-21 07:30 | 82.14 | 58.15
2018-02-21 08:00 | 79.11 | 55.14
2018-02-21 08:30 | 71.51 | 46.3
2018-02-21 09:00 | 76.05 | 52.2
2018-02-21 09:30 | 75.19 | 55.14
2018-02-21 10:00 | 80.25 | 61.51
2018-02-21 10:30 | 80.46 | 60.73
2018-02-21 11:00 | 78.34 | 58.49
2018-02-21 11:30 | 83.48 | 66.03
2018-02-21 12:00 | 94.47 | 76.19
2018-02-21 12:30 | 84.26 | 67.96
2018-02-21 13:00 | 81.72 | 65.23
2018-02-21 13:30 | 86.54 | 68.97
2018-02-21 14:00 | 88.12 | 69.19
2018-02-21 14:30 | 89.05 | 70.41
2018-02-21 15:00 | 90.11 | 72.29
2018-02-21 15:30 | 96.25 | 77.71
2018-02-21 16:00 | 103.31 | 84.09
2018-02-21 16:30 | 105.07 | 84.96
2018-02-21 17:00 | 109.8 | 90.4
2018-02-21 17:30 | 102.13 | 84.7
2018-02-21 18:00 | 102.98 | 84.48
2018-02-21 18:30 | 108.58 | 89.04
2018-02-21 19:00 | 113.68 | 93.63
2018-02-21 19:30 | 116.4 | 96.61
2018-02-21 20:00 | 115.32 | 93.95
2018-02-21 20:30 | 117.54 | 95.89
2018-02-21 21:00 | 116.38 | 94.35
2018-02-21 21:30 | 115.17 | 94.17
2018-02-21 22:00 | 112.4 | 91.53
2018-02-21 22:30 | 107.83 | 87.48
2018-02-21 23:00 | 107.34 | 86.44
2018-02-21 23:30 | 107.17 | 86.86
2018-02-22 | 105.64 | 84.6
2018-02-22 00:30 | 111.97 | 92.54
2018-02-22 01:00 | 113.89 | 94.81
2018-02-22 01:30 | 107.46 | 86.59
2018-02-22 02:00 | 111.71 | 91
2018-02-22 02:30 | 106.76 | 87.08
2018-02-22 03:00 | 108.1 | 89.21
2018-02-22 03:30 | 106.2 | 87.42
2018-02-22 04:00 | 105.23 | 86.47
2018-02-22 04:30 | 104.66 | 87.54
2018-02-22 05:00 | 105.91 | 87.67
2018-02-22 05:30 | 106.59 | 88.25
2018-02-22 06:00 | 109.62 | 90.9
2018-02-22 06:30 | 98.98 | 78.29
2018-02-22 07:00 | 108.86 | 88.21
2018-02-22 07:30 | 109.92 | 88.81
2018-02-22 08:00 | 109.62 | 88.62
2018-02-22 08:30 | 108.16 | 87.74
2018-02-22 09:00 | 106.11 | 85.44
2018-02-22 09:30 | 108.49 | 88.26
2018-02-22 10:00 | 110.58 | 91.89
2018-02-22 10:30 | 114.31 | 95.39
2018-02-22 11:00 | 115.55 | 96.27
2018-02-22 11:30 | 114.83 | 96.49
2018-02-22 12:00 | 117.05 | 96.12
2018-02-22 12:30 | 118.7 | 96.99
2018-02-22 13:00 | 117.71 | 94.98
2018-02-22 13:30 | 114.89 | 93.32
2018-02-22 14:00 | 111.82 | 89.81
2018-02-22 14:30 | 112.89 | 91.88
2018-02-22 15:00 | 111.44 | 90.37
2018-02-22 15:30 | 110.43 | 88.19
2018-02-22 16:00 | 113.66 | 90.34
2018-02-22 16:30 | 120.14 | 96.43
2018-02-22 17:00 | 123.81 | 99.82
2018-02-22 17:30 | 117.06 | 93.96
2018-02-22 18:00 | 112.79 | 91.24
2018-02-22 18:30 | 108.41 | 87.06
2018-02-22 19:00 | 112.25 | 92.38
2018-02-22 19:30 | 111.55 | 89.12
2018-02-22 20:00 | 113.66 | 91.85
2018-02-22 20:30 | 117.27 | 95.68
2018-02-22 21:00 | 116.97 | 97.43
2018-02-22 21:30 | 114.61 | 95.17
2018-02-22 22:00 | 112.21 | 92.44
2018-02-22 22:30 | 108.84 | 89.65
2018-02-22 23:00 | 112.26 | 94.29
2018-02-22 23:30 | 112.42 | 94.58
2018-02-23 | 108.65 | 91.81
2018-02-23 00:30 | 105.27 | 88.06
2018-02-23 01:00 | 102.47 | 86.96
2018-02-23 01:30 | 113.11 | 96.22
2018-02-23 02:00 | 107.49 | 90.46
2018-02-23 02:30 | 107.89 | 90.71
2018-02-23 03:00 | 103.35 | 86.81
2018-02-23 03:30 | 100.64 | 83.82
2018-02-23 04:00 | 101.81 | 85.08
2018-02-23 04:30 | 99.84 | 82.93
2018-02-23 05:00 | 99.91 | 83.12
2018-02-23 05:30 | 103.89 | 87.34
2018-02-23 06:00 | 106.3 | 89.66
2018-02-23 06:30 | 98.52 | 81.1
2018-02-23 07:00 | 103.53 | 87.66
2018-02-23 07:30 | 111.92 | 93.92
2018-02-23 08:00 | 113.92 | 94.69
2018-02-23 08:30 | 116.03 | 96.17
2018-02-23 09:00 | 115.24 | 94.7
2018-02-23 09:30 | 116.07 | 94.33
2018-02-23 10:00 | 113.75 | 91.65
2018-02-23 10:30 | 114.26 | 92.86
2018-02-23 11:00 | 117.04 | 96.94
2018-02-23 11:30 | 110.88 | 91.23
2018-02-23 12:00 | 110.38 | 89.51
2018-02-23 12:30 | 107.17 | 86.8
2018-02-23 13:00 | 116.77 | 96.46
2018-02-23 13:30 | 111.97 | 93.21
2018-02-23 14:00 | 112.28 | 94.23
2018-02-23 14:30 | 105.79 | 85.86
2018-02-23 15:00 | 107.35 | 87.54
2018-02-23 15:30 | 116.49 | 98.53
2018-02-23 16:00 | 112.85 | 94.19
2018-02-23 16:30 | 109.68 | 89.96
2018-02-23 17:00 | 105.27 | 86.42
2018-02-23 17:30 | 109.06 | 89.16
2018-02-23 18:00 | 114.29 | 95.25
2018-02-23 18:30 | 104.04 | 84.07
2018-02-23 19:00 | 106.41 | 87.29
2018-02-23 19:30 | 110.22 | 90.21
2018-02-23 20:00 | 110.16 | 89.78
2018-02-23 20:30 | 107.34 | 87.58
2018-02-23 21:00 | 111.2 | 89.82
2018-02-23 21:30 | 116.08 | 94.76
2018-02-23 22:00 | 122.02 | 101.29
2018-02-23 22:30 | 115.98 | 95.38
2018-02-23 23:00 | 117.09 | 96.28
2018-02-23 23:30 | 119.25 | 98.27
2018-02-24 | 118.66 | 97.51
2018-02-24 00:30 | 120.91 | 100.3
2018-02-24 01:00 | 113.86 | 91.71
2018-02-24 01:30 | 118.48 | 96.25
2018-02-24 02:00 | 115.18 | 92.57
2018-02-24 02:30 | 118.93 | 97.54
2018-02-24 03:00 | 121.79 | 99.95
2018-02-24 03:30 | 114.67 | 93.88
2018-02-24 04:00 | 116.81 | 95.93
2018-02-24 04:30 | 115.74 | 94.08
2018-02-24 05:00 | 116.24 | 95.98
2018-02-24 05:30 | 118.29 | 97.2
2018-02-24 06:00 | 113.23 | 91.95
2018-02-24 06:30 | 105.79 | 84.12
2018-02-24 07:00 | 118.19 | 97.63
2018-02-24 07:30 | 120.6 | 99.28
2018-02-24 08:00 | 114.41 | 90.93
2018-02-24 08:30 | 116.88 | 95.09
2018-02-24 09:00 | 124.57 | 101.29
2018-02-24 09:30 | 117.33 | 91.79
2018-02-24 10:00 | 114.38 | 89.73
2018-02-24 10:30 | 124.31 | 99.33
2018-02-24 11:00 | 124.72 | 99.82
2018-02-24 11:30 | 128.05 | 104.5
2018-02-24 12:00 | 127.17 | 101.88
2018-02-24 12:30 | 127.72 | 103.3
2018-02-24 13:00 | 129.61 | 104.16
2018-02-24 13:30 | 123.13 | 97.88
2018-02-24 14:00 | 124.95 | 102.3
2018-02-24 14:30 | 126.93 | 103.01
2018-02-24 15:00 | 117.28 | 92.34
2018-02-24 15:30 | 121.03 | 96.17
2018-02-24 16:00 | 121.22 | 97.46
2018-02-24 16:30 | 113.17 | 89.95
2018-02-24 17:00 | 111.08 | 87.1
2018-02-24 17:30 | 107.07 | 83.55
2018-02-24 18:00 | 114.02 | 91.74
2018-02-24 18:30 | 107.21 | 83.68
2018-02-24 19:00 | 114.82 | 92.04
2018-02-24 19:30 | 109.87 | 88.07
2018-02-24 20:00 | 109.03 | 87.33
2018-02-24 20:30 | 112.42 | 90.93
2018-02-24 21:00 | 106.75 | 84.65
2018-02-24 21:30 | 112.08 | 90.05
2018-02-24 22:00 | 110.29 | 88.58
2018-02-24 22:30 | 114.58 | 93.41
2018-02-24 23:00 | 111.56 | 90.03
2018-02-24 23:30 | 113.76 | 93.13
2018-02-25 | 110.54 | 91.98
2018-02-25 00:30 | 112.29 | 92.99
2018-02-25 01:00 | 108.15 | 88.72
2018-02-25 01:30 | 106.08 | 85.85
2018-02-25 02:00 | 111.34 | 91.42
2018-02-25 02:30 | 113.52 | 92.58
2018-02-25 03:00 | 111.27 | 91.41
2018-02-25 03:30 | 108.63 | 89.93
2018-02-25 04:00 | 120.05 | 101.54
2018-02-25 04:30 | 120.08 | 101.01
2018-02-25 05:00 | 106.28 | 87.98
2018-02-25 05:30 | 109.09 | 90.92
2018-02-25 06:00 | 114.65 | 96.9
2018-02-25 06:30 | 100.2 | 81.22
2018-02-25 07:00 | 106.15 | 86.18
2018-02-25 07:30 | 106.22 | 86.67
2018-02-25 08:00 | 105.6 | 86.42
2018-02-25 08:30 | 109.53 | 90.94
2018-02-25 09:00 | 114.15 | 94.54
2018-02-25 09:30 | 108.87 | 89.84
2018-02-25 10:00 | 113.44 | 94.34
2018-02-25 10:30 | 112.62 | 91.63
2018-02-25 11:00 | 113.97 | 92.05
2018-02-25 11:30 | 116.68 | 94.41
2018-02-25 12:00 | 120.47 | 99.65
2018-02-25 12:30 | 125.04 | 104.29
2018-02-25 13:00 | 134.01 | 114.25
2018-02-25 13:30 | 124.86 | 105.11
2018-02-25 14:00 | 118.14 | 97.36
2018-02-25 14:30 | 112.56 | 92.27
2018-02-25 15:00 | 114.62 | 93.75
2018-02-25 15:30 | 110.34 | 89.36
2018-02-25 16:00 | 116.11 | 94.77
2018-02-25 16:30 | 116.15 | 93.26
2018-02-25 17:00 | 117.31 | 95.86
2018-02-25 17:30 | 118.79 | 96.52
2018-02-25 18:00 | 123.13 | 102.64
2018-02-25 18:30 | 119.06 | 97.52
2018-02-25 19:00 | 116.91 | 97.46
2018-02-25 19:30 | 115.63 | 95.63
2018-02-25 20:00 | 114.77 | 94.05
2018-02-25 20:30 | 114.07 | 91.08
2018-02-25 21:00 | 106.41 | 84.3
2018-02-25 21:30 | 103.02 | 83.35
2018-02-25 22:00 | 104.12 | 86.19
2018-02-25 22:30 | 106.32 | 87.88
2018-02-25 23:00 | 112.53 | 95.45
2018-02-25 23:30 | 109.09 | 92.49
2018-02-26 | 101.59 | 84.3
2018-02-26 00:30 | 109.9 | 92.49
2018-02-26 01:00 | 116.61 | 99.87
2018-02-26 01:30 | 114 | 97.57
2018-02-26 02:00 | 108.52 | 93.58
2018-02-26 02:30 | 112.07 | 97.21
2018-02-26 03:00 | 108.98 | 93.39
2018-02-26 03:30 | 103.5 | 87.23
2018-02-26 04:00 | 100.93 | 84.34
2018-02-26 04:30 | 107.36 | 91.24
2018-02-26 05:00 | 97.32 | 81.96
2018-02-26 05:30 | 102.48 | 85.89
2018-02-26 06:00 | 98.11 | 82.04
2018-02-26 06:30 | 91.56 | 74.05
2018-02-26 07:00 | 97.58 | 80.29
2018-02-26 07:30 | 109.86 | 92.65
2018-02-26 08:00 | 106.85 | 89.46
2018-02-26 08:30 | 110.57 | 91.04
2018-02-26 09:00 | 114.96 | 94.38
2018-02-26 09:30 | 111.65 | 89.44
2018-02-26 10:00 | 116.73 | 94.64
2018-02-26 10:30 | 123.56 | 101.3
2018-02-26 11:00 | 125.12 | 102.39
2018-02-26 11:30 | 119.52 | 96.72
2018-02-26 12:00 | 123.71 | 100.43
2018-02-26 12:30 | 127.05 | 104.37
2018-02-26 13:00 | 124.08 | 103.66
2018-02-26 13:30 | 131.39 | 111.27
2018-02-26 14:00 | 132.88 | 112.1
2018-02-26 14:30 | 131.35 | 110.36
2018-02-26 15:00 | 119.03 | 97.32
2018-02-26 15:30 | 130 | 107.41
2018-02-26 16:00 | 128.27 | 105.38
2018-02-26 16:30 | 133.65 | 111.14
2018-02-26 17:00 | 124.43 | 103.79
2018-02-26 17:30 | 131.46 | 112.06
2018-02-26 18:00 | 131.48 | 110.79
2018-02-26 18:30 | 122.35 | 100.91
2018-02-26 19:00 | 126.7 | 105.72
2018-02-26 19:30 | 135.34 | 113.98
2018-02-26 20:00 | 126.94 | 106.16
2018-02-26 20:30 | 123.68 | 102.8
2018-02-26 21:00 | 128.48 | 107.49
2018-02-26 21:30 | 122.81 | 102.18
2018-02-26 22:00 | 120.89 | 100.7
2018-02-26 22:30 | 120.51 | 101.45
2018-02-26 23:00 | 118.13 | 98.95
2018-02-26 23:30 | 122.93 | 103.63
2018-02-27 | 113.64 | 93.13
2018-02-27 00:30 | 114.7 | 94.82
2018-02-27 01:00 | 117.72 | 97.73
2018-02-27 01:30 | 109.22 | 89.21
2018-02-27 02:00 | 113.49 | 95.8
2018-02-27 02:30 | 121.83 | 102.93
2018-02-27 03:00 | 115.2 | 95.43
2018-02-27 03:30 | 123.58 | 103.48
2018-02-27 04:00 | 112.46 | 92.38
2018-02-27 04:30 | 116.03 | 96.69
2018-02-27 05:00 | 116.59 | 96.37
2018-02-27 05:30 | 113.23 | 92.56
2018-02-27 06:00 | 111.15 | 90.21
2018-02-27 06:30 | 106.76 | 84.16
2018-02-27 07:00 | 116.11 | 94.98
2018-02-27 07:30 | 111.9 | 89.94
2018-02-27 08:00 | 110.85 | 88.38
2018-02-27 08:30 | 118.94 | 97.5
2018-02-27 09:00 | 108.31 | 86.93
2018-02-27 09:30 | 105.88 | 87.34
2018-02-27 10:00 | 106.02 | 86.71
2018-02-27 10:30 | 112.78 | 88.03
2018-02-27 11:00 | 117.83 | 93.14
2018-02-27 11:30 | 111.14 | 86.66
2018-02-27 12:00 | 113.82 | 89
2018-02-27 12:30 | 119.47 | 95.52
2018-02-27 13:00 | 122.4 | 97.85
2018-02-27 13:30 | 119.63 | 94.52
2018-02-27 14:00 | 120.46 | 94.46
2018-02-27 14:30 | 123.91 | 96.67
2018-02-27 15:00 | 122.2 | 94.72
2018-02-27 15:30 | 122.47 | 96.41
2018-02-27 16:00 | 125.08 | 98.84
2018-02-27 16:30 | 130.47 | 103.53
2018-02-27 17:00 | 131.1 | 106.26
2018-02-27 17:30 | 116.26 | 91.5
2018-02-27 18:00 | 118.22 | 94.1
2018-02-27 18:30 | 113.38 | 90.05
2018-02-27 19:00 | 118.31 | 92.96
2018-02-27 19:30 | 122 | 96.61
2018-02-27 20:00 | 120.65 | 96.18
2018-02-27 20:30 | 126.05 | 103.05
2018-02-27 21:00 | 120.45 | 96.24
2018-02-27 21:30 | 116.14 | 90.62
2018-02-27 22:00 | 128.78 | 104.3
2018-02-27 22:30 | 122.79 | 99.97
2018-02-27 23:00 | 117.62 | 94.14
2018-02-27 23:30 | 115.02 | 91.44
2018-02-28 | 113.59 | 89.46
2018-02-28 00:30 | 114.21 | 91.75
2018-02-28 01:00 | 120.58 | 99.16
2018-02-28 01:30 | 119.41 | 99.82
2018-02-28 02:00 | 116.18 | 95.66
2018-02-28 02:30 | 117.79 | 97.57
2018-02-28 03:00 | 103.52 | 83.15
2018-02-28 03:30 | 102.77 | 84.05
2018-02-28 04:00 | 102.92 | 83.8
2018-02-28 04:30 | 102.14 | 82.4
2018-02-28 05:00 | 102.91 | 82.62
2018-02-28 05:30 | 100.14 | 79.67
2018-02-28 06:00 | 99.37 | 77.83
2018-02-28 06:30 | 95.89 | 74.95
2018-02-28 07:00 | 98.2 | 78.39
2018-02-28 07:30 | 90.56 | 69.56
2018-02-28 08:00 | 99.6 | 78.76
2018-02-28 08:30 | 100.85 | 80.35
2018-02-28 09:00 | 101.22 | 79.59
2018-02-28 09:30 | 97.53 | 74.96
2018-02-28 10:00 | 105.84 | 83.55
2018-02-28 10:30 | 103.37 | 80.93
2018-02-28 11:00 | 106.59 | 83.01
2018-02-28 11:30 | 103.8 | 80.93
2018-02-28 12:00 | 98.02 | 73.77
2018-02-28 12:30 | 96.41 | 73.38
2018-02-28 13:00 | 97.98 | 77.03
2018-02-28 13:30 | 97.08 | 73.66
2018-02-28 14:00 | 97.6 | 73.14
2018-02-28 14:30 | 104.93 | 78.51
2018-02-28 15:00 | 110.18 | 82.77
2018-02-28 15:30 | 109.91 | 83.86
2018-02-28 16:00 | 114.26 | 88.54
2018-02-28 16:30 | 110.2 | 85.16
2018-02-28 17:00 | 122.65 | 96.64
2018-02-28 17:30 | 117.15 | 92.13
2018-02-28 18:00 | 114.2 | 89.99
2018-02-28 18:30 | 109.98 | 84.71
2018-02-28 19:00 | 115.78 | 92.55
2018-02-28 19:30 | 114.92 | 92.76
2018-02-28 20:00 | 115.99 | 92.57
2018-02-28 20:30 | 116.2 | 92.64
2018-02-28 21:00 | 114.32 | 92.17
2018-02-28 21:30 | 108.39 | 85.88
2018-02-28 22:00 | 113.81 | 88.14
2018-02-28 22:30 | 111.94 | 86.7
2018-02-28 23:00 | 108.39 | 87.28
2018-02-28 23:30 | 115.81 | 90.66
2018-03-01 | 107.9 | 81.7
2018-03-01 00:30 | 109.62 | 85.08
2018-03-01 01:00 | 113.93 | 89.97
2018-03-01 01:30 | 110.83 | 89.5
2018-03-01 02:00 | 114.76 | 93.69
2018-03-01 02:30 | 115.9 | 95.22
2018-03-01 03:00 | 109.4 | 87.63
2018-03-01 03:30 | 106.9 | 83.52
2018-03-01 04:00 | 106.5 | 83.27
2018-03-01 04:30 | 107.92 | 85.32
2018-03-01 05:00 | 104.4 | 81.96
2018-03-01 05:30 | 114.55 | 92.57
2018-03-01 06:00 | 108.79 | 84.79
2018-03-01 06:30 | 107.26 | 81
2018-03-01 07:00 | 108.98 | 82.16
2018-03-01 07:30 | 115.3 | 90.01
2018-03-01 08:00 | 111.87 | 85.72
2018-03-01 08:30 | 110.67 | 85.49
2018-03-01 09:00 | 106.69 | 81.62
2018-03-01 09:30 | 108.85 | 83.65
2018-03-01 10:00 | 116.69 | 90.16
2018-03-01 10:30 | 122 | 96.59
2018-03-01 11:00 | 118.75 | 93.03
2018-03-01 11:30 | 113.43 | 86.19
2018-03-01 12:00 | 121.38 | 94.54
2018-03-01 12:30 | 124.56 | 95.01
2018-03-01 13:00 | 125.94 | 97.02
2018-03-01 13:30 | 131.1 | 103.13
2018-03-01 14:00 | 129.03 | 99.48
2018-03-01 14:30 | 123.42 | 92.83
2018-03-01 15:00 | 126.35 | 95.2
2018-03-01 15:30 | 123.86 | 93.52
2018-03-01 16:00 | 114.81 | 86.37
2018-03-01 16:30 | 122.31 | 94.1
2018-03-01 17:00 | 124.35 | 94.16
2018-03-01 17:30 | 122.13 | 90.94
2018-03-01 18:00 | 133.31 | 102.43
2018-03-01 18:30 | 124.16 | 92.72
2018-03-01 19:00 | 126.86 | 97.14
2018-03-01 19:30 | 137.74 | 107.94
2018-03-01 20:00 | 137.41 | 108.47
2018-03-01 20:30 | 131.41 | 102.32
2018-03-01 21:00 | 127.21 | 97.5
2018-03-01 21:30 | 114.73 | 86.62
2018-03-01 22:00 | 116.12 | 87.66
2018-03-01 22:30 | 123.57 | 93.1
2018-03-01 23:00 | 121.37 | 90.85
2018-03-01 23:30 | 118.67 | 88.91
2018-03-02 | 118.28 | 89.59
2018-03-02 00:30 | 118.2 | 90.03
2018-03-02 01:00 | 114.06 | 88.85
2018-03-02 01:30 | 111.95 | 85.89
2018-03-02 02:00 | 113.7 | 87.3
2018-03-02 02:30 | 116.21 | 89.43
2018-03-02 03:00 | 114.7 | 88.28
2018-03-02 03:30 | 112.21 | 87.06
2018-03-02 04:00 | 114.93 | 89.72
2018-03-02 04:30 | 116.06 | 90.73
2018-03-02 05:00 | 116.9 | 91.88
2018-03-02 05:30 | 122.42 | 98.47
2018-03-02 06:00 | 117.07 | 92.37
2018-03-02 06:30 | 111.99 | 86.01
2018-03-02 07:00 | 116.49 | 92.15
2018-03-02 07:30 | 120.17 | 96.07
2018-03-02 08:00 | 126.46 | 101.04
2018-03-02 08:30 | 126.34 | 100.94
2018-03-02 09:00 | 124.02 | 99.15
2018-03-02 09:30 | 121.72 | 96.73
2018-03-02 10:00 | 120.79 | 94.52
2018-03-02 10:30 | 123.05 | 96.06
2018-03-02 11:00 | 119.98 | 92.58
2018-03-02 11:30 | 129.87 | 103
2018-03-02 12:00 | 132.75 | 107.02
2018-03-02 12:30 | 133.69 | 109.45
2018-03-02 13:00 | 120.34 | 95.59
2018-03-02 13:30 | 123.3 | 98.2
2018-03-02 14:00 | 131.83 | 106.6
2018-03-02 14:30 | 120.27 | 94.67
2018-03-02 15:00 | 130.79 | 104.2
2018-03-02 15:30 | 120.01 | 94.3
2018-03-02 16:00 | 127.47 | 101.56
2018-03-02 16:30 | 133.91 | 105.98
2018-03-02 17:00 | 132.99 | 105.5
2018-03-02 17:30 | 132.93 | 105.32
2018-03-02 18:00 | 136.08 | 107.5
2018-03-02 18:30 | 135.49 | 107.53
2018-03-02 19:00 | 135.55 | 108.47
2018-03-02 19:30 | 134.23 | 105.82
2018-03-02 20:00 | 132.41 | 104.58
2018-03-02 20:30 | 129.55 | 99.93
2018-03-02 21:00 | 125.36 | 96.98
2018-03-02 21:30 | 128.65 | 101.02
2018-03-02 22:00 | 132.31 | 104.63
2018-03-02 22:30 | 129.19 | 100.7
2018-03-02 23:00 | 128.63 | 101.62
2018-03-02 23:30 | 126.11 | 100.35
2018-03-03 | 125.99 | 100.62
2018-03-03 00:30 | 130.5 | 105.36
2018-03-03 01:00 | 129.73 | 105.3
2018-03-03 01:30 | 128.45 | 103.76
2018-03-03 02:00 | 123.7 | 98.4
2018-03-03 02:30 | 128.06 | 103.64
2018-03-03 03:00 | 122.2 | 97.76
2018-03-03 03:30 | 127.62 | 103.24
2018-03-03 04:00 | 132.76 | 107.52
2018-03-03 04:30 | 128.15 | 102.19
2018-03-03 05:00 | 130.07 | 102.97
2018-03-03 05:30 | 124.17 | 98.13
2018-03-03 06:00 | 124.2 | 98.36
2018-03-03 06:30 | 124.81 | 99.14
2018-03-03 07:00 | 127.52 | 104.13
2018-03-03 07:30 | 129.73 | 107.04
2018-03-03 08:00 | 126.23 | 100.71
2018-03-03 08:30 | 128.6 | 102.05
2018-03-03 09:00 | 128.53 | 102.13
2018-03-03 09:30 | 124.7 | 98.6
2018-03-03 10:00 | 128.53 | 101.86
2018-03-03 10:30 | 129.98 | 103.91
2018-03-03 11:00 | 125.59 | 97.8
2018-03-03 11:30 | 124.98 | 99.02
2018-03-03 12:00 | 118.72 | 92.95
2018-03-03 12:30 | 135.32 | 110.22
2018-03-03 13:00 | 136.73 | 111.06
2018-03-03 13:30 | 137.27 | 111.26
2018-03-03 14:00 | 133.34 | 107.23
2018-03-03 14:30 | 134.92 | 108.88
2018-03-03 15:00 | 132.17 | 106.48
2018-03-03 15:30 | 134.68 | 108.46
2018-03-03 16:00 | 139.5 | 112.99
2018-03-03 16:30 | 128.65 | 102.35
2018-03-03 17:00 | 137.59 | 110.99
2018-03-03 17:30 | 126.14 | 99.87
2018-03-03 18:00 | 123.7 | 96.78
2018-03-03 18:30 | 119.91 | 92.96
2018-03-03 19:00 | 124.53 | 98.24
2018-03-03 19:30 | 127.28 | 100.01
2018-03-03 20:00 | 127.31 | 102.05
2018-03-03 20:30 | 123.65 | 99.05
2018-03-03 21:00 | 125.84 | 100.97
2018-03-03 21:30 | 115.05 | 89.55
2018-03-03 22:00 | 121.41 | 97.14
2018-03-03 22:30 | 113.76 | 91.45
2018-03-03 23:00 | 107.91 | 84.49
2018-03-03 23:30 | 110.57 | 87.66
2018-03-04 | 112.95 | 91.37
2018-03-04 00:30 | 113.15 | 90.75
2018-03-04 01:00 | 113.91 | 90.57
2018-03-04 01:30 | 113.26 | 90.73
2018-03-04 02:00 | 112.89 | 90.44
2018-03-04 02:30 | 112.68 | 90.17
2018-03-04 03:00 | 120.64 | 98.12
2018-03-04 03:30 | 118.76 | 95.18
2018-03-04 04:00 | 121.4 | 98.56
2018-03-04 04:30 | 121.75 | 98.77
2018-03-04 05:00 | 119.29 | 95.62
2018-03-04 05:30 | 116.7 | 93.62
2018-03-04 06:00 | 116.31 | 93.32
2018-03-04 06:30 | 108.31 | 84.14
2018-03-04 07:00 | 114.27 | 90.35
2018-03-04 07:30 | 116.2 | 92.78
2018-03-04 08:00 | 119.42 | 97.44
2018-03-04 08:30 | 119.84 | 96.86
2018-03-04 09:00 | 121.06 | 98.31
2018-03-04 09:30 | 114.86 | 91.5
2018-03-04 10:00 | 125.57 | 102.43
2018-03-04 10:30 | 122.11 | 99.19
2018-03-04 11:00 | 116.62 | 92.88
2018-03-04 11:30 | 123.06 | 97.65
2018-03-04 12:00 | 125.74 | 99.26
2018-03-04 12:30 | 128.61 | 101.43
2018-03-04 13:00 | 124.38 | 98.32
2018-03-04 13:30 | 124.4 | 99.69
2018-03-04 14:00 | 131.09 | 105.79
2018-03-04 14:30 | 124.5 | 101.45
2018-03-04 15:00 | 132.38 | 108.36
2018-03-04 15:30 | 122.16 | 97.08
2018-03-04 16:00 | 129.68 | 104.05
2018-03-04 16:30 | 127.89 | 102.77
2018-03-04 17:00 | 133.66 | 108.3
2018-03-04 17:30 | 127.98 | 102.36
2018-03-04 18:00 | 132.88 | 107.49
2018-03-04 18:30 | 126.22 | 99.87
2018-03-04 19:00 | 132.84 | 107.78
2018-03-04 19:30 | 139.82 | 113.79
2018-03-04 20:00 | 127.45 | 101.9
2018-03-04 20:30 | 123.37 | 97.93
2018-03-04 21:00 | 128.42 | 102.99
2018-03-04 21:30 | 122.85 | 98.58
2018-03-04 22:00 | 125.25 | 101.06
2018-03-04 22:30 | 124.81 | 102.54
2018-03-04 23:00 | 122.96 | 100.44
2018-03-04 23:30 | 118.85 | 94.38
2018-03-05 | 116.48 | 92.11
2018-03-05 00:30 | 119.47 | 94.42
2018-03-05 01:00 | 117.72 | 92.95
2018-03-05 01:30 | 117.82 | 94.18
2018-03-05 02:00 | 120.63 | 98.13
2018-03-05 02:30 | 120.99 | 99.34
2018-03-05 03:00 | 117.38 | 96.31
2018-03-05 03:30 | 118.62 | 96.92
2018-03-05 04:00 | 114.42 | 91.2
2018-03-05 04:30 | 115.02 | 93.21
2018-03-05 05:00 | 113.9 | 91.68
2018-03-05 05:30 | 112.81 | 89.54
2018-03-05 06:00 | 109.31 | 89.87
2018-03-05 06:30 | 102.49 | 83.06
2018-03-05 07:00 | 102.98 | 83.02
2018-03-05 07:30 | 110.77 | 91.2
2018-03-05 08:00 | 108.36 | 89.91
2018-03-05 08:30 | 110.39 | 91.69
2018-03-05 09:00 | 107.92 | 86.72
2018-03-05 09:30 | 107.82 | 87.28
2018-03-05 10:00 | 114.98 | 94.99
2018-03-05 10:30 | 112.4 | 92.94
2018-03-05 11:00 | 111.19 | 91.77
2018-03-05 11:30 | 110.51 | 91.44
2018-03-05 12:00 | 111.27 | 93.21
2018-03-05 12:30 | 110.65 | 93.39
2018-03-05 13:00 | 110.27 | 91.11
2018-03-05 13:30 | 108.78 | 89.56
2018-03-05 14:00 | 117.01 | 97.6
2018-03-05 14:30 | 115.47 | 95.97
2018-03-05 15:00 | 118.76 | 99.02
2018-03-05 15:30 | 119.66 | 99.17
2018-03-05 16:00 | 121.22 | 101.16
2018-03-05 16:30 | 124.05 | 104.17
2018-03-05 17:00 | 127.3 | 106.46
2018-03-05 17:30 | 124.08 | 104.26
2018-03-05 18:00 | 123.4 | 103.54
2018-03-05 18:30 | 117.4 | 96.74
2018-03-05 19:00 | 122.4 | 104.26
2018-03-05 19:30 | 124.69 | 106.72
2018-03-05 20:00 | 125.52 | 107.34
2018-03-05 20:30 | 126.57 | 107.65
2018-03-05 21:00 | 120.61 | 100.64
2018-03-05 21:30 | 119.95 | 100.68
2018-03-05 22:00 | 114.13 | 95.27
2018-03-05 22:30 | 108.4 | 89.56
2018-03-05 23:00 | 109.4 | 90.42
2018-03-05 23:30 | 102.06 | 82.46
2018-03-06 | 104.91 | 85.34
2018-03-06 00:30 | 113.35 | 94.43
2018-03-06 01:00 | 115.07 | 96.44
2018-03-06 01:30 | 109.44 | 90.73
2018-03-06 02:00 | 112.78 | 94.57
2018-03-06 02:30 | 103.51 | 86.06
2018-03-06 03:00 | 107.72 | 90.17
2018-03-06 03:30 | 102.45 | 84.07
2018-03-06 04:00 | 100.85 | 82.36
2018-03-06 04:30 | 106.84 | 88.85
2018-03-06 05:00 | 104.46 | 85.66
2018-03-06 05:30 | 99.89 | 81.65
2018-03-06 06:00 | 102.88 | 83.66
2018-03-06 06:30 | 96.03 | 76.44
2018-03-06 07:00 | 101.14 | 82.95
2018-03-06 07:30 | 104.36 | 86.41
2018-03-06 08:00 | 101.65 | 83.86
2018-03-06 08:30 | 97.48 | 80.34
2018-03-06 09:00 | 94.95 | 77.81
2018-03-06 09:30 | 94.98 | 78.2
2018-03-06 10:00 | 98.39 | 81.57
2018-03-06 10:30 | 100.87 | 84.22
2018-03-06 11:00 | 99.15 | 83.53
2018-03-06 11:30 | 96.38 | 79.93
2018-03-06 12:00 | 93.75 | 77.07
2018-03-06 12:30 | 90.98 | 74.98
2018-03-06 13:00 | 97.61 | 80.72
2018-03-06 13:30 | 101.21 | 83
2018-03-06 14:00 | 101.35 | 83.85
2018-03-06 14:30 | 97.14 | 79.93
2018-03-06 15:00 | 98.7 | 81.53
2018-03-06 15:30 | 96.35 | 78.86
2018-03-06 16:00 | 100.94 | 84.89
2018-03-06 16:30 | 96.27 | 80.09
2018-03-06 17:00 | 100.57 | 84.01
2018-03-06 17:30 | 101.91 | 86.18
2018-03-06 18:00 | 96.96 | 79.95
2018-03-06 18:30 | 92.88 | 74.39
2018-03-06 19:00 | 103.44 | 81.4
2018-03-06 19:30 | 103.12 | 80.11
2018-03-06 20:00 | 103.29 | 81.88
2018-03-06 20:30 | 105.53 | 85.14
2018-03-06 21:00 | 106.94 | 86.74
2018-03-06 21:30 | 113.73 | 92.97
2018-03-06 22:00 | 113.66 | 94.16
2018-03-06 22:30 | 109.08 | 87.94
2018-03-06 23:00 | 108.31 | 87.57
2018-03-06 23:30 | 104.54 | 83.9
2018-03-07 | 110.11 | 89.44
2018-03-07 00:30 | 105.5 | 85.56
2018-03-07 01:00 | 106.38 | 84.77
2018-03-07 01:30 | 109.81 | 87.85
2018-03-07 02:00 | 113.37 | 90.55
2018-03-07 02:30 | 110.85 | 87.82
2018-03-07 03:00 | 113.54 | 90.4
2018-03-07 03:30 | 110.15 | 86.84
2018-03-07 04:00 | 116.88 | 94.5
2018-03-07 04:30 | 117.72 | 96.19
2018-03-07 05:00 | 121.51 | 99.55
2018-03-07 05:30 | 111.44 | 89.29
2018-03-07 06:00 | 109.66 | 88.28
2018-03-07 06:30 | 94.4 | 72.61
2018-03-07 07:00 | 99.28 | 78.41
2018-03-07 07:30 | 104.27 | 83.02
2018-03-07 08:00 | 104.74 | 81.31
2018-03-07 08:30 | 107.4 | 83.35
2018-03-07 09:00 | 97.68 | 71.47
2018-03-07 09:30 | 102 | 77.98
2018-03-07 10:00 | 102.64 | 78.53
2018-03-07 10:30 | 106.58 | 82.55
2018-03-07 11:00 | 101.4 | 74.8
2018-03-07 11:30 | 104.83 | 77.83
2018-03-07 12:00 | 112.81 | 86.94
2018-03-07 12:30 | 103.8 | 78.67
2018-03-07 13:00 | 100.71 | 75.52
2018-03-07 13:30 | 106.28 | 80.77
2018-03-07 14:00 | 109.57 | 83.66
2018-03-07 14:30 | 106.37 | 82.32
2018-03-07 15:00 | 104 | 76.63
2018-03-07 15:30 | 107.07 | 80.78
2018-03-07 16:00 | 107.58 | 82
2018-03-07 16:30 | 108.67 | 83.5
2018-03-07 17:00 | 110.01 | 86.75
2018-03-07 17:30 | 107.63 | 84.93
2018-03-07 18:00 | 110.97 | 88.85
2018-03-07 18:30 | 99.75 | 76.61
2018-03-07 19:00 | 113.59 | 93.16
2018-03-07 19:30 | 113.85 | 93.34
2018-03-07 20:00 | 111.05 | 89.98
2018-03-07 20:30 | 120.45 | 98.38
2018-03-07 21:00 | 115.9 | 91.19
2018-03-07 21:30 | 120.73 | 95.39
2018-03-07 22:00 | 118.82 | 92.91
2018-03-07 22:30 | 115.94 | 92.06
2018-03-07 23:00 | 116.97 | 94.53
2018-03-07 23:30 | 116.77 | 94.07
2018-03-08 | 118.68 | 96.55
2018-03-08 00:30 | 122.51 | 100.36
2018-03-08 01:00 | 119.43 | 96.16
2018-03-08 01:30 | 119.73 | 97.33
2018-03-08 02:00 | 125.84 | 104.01
2018-03-08 02:30 | 129.03 | 108.09
2018-03-08 03:00 | 123.81 | 102.26
2018-03-08 03:30 | 110.78 | 87.6
2018-03-08 04:00 | 115.98 | 93.34
2018-03-08 04:30 | 119.36 | 96.8
2018-03-08 05:00 | 119.25 | 96.17
2018-03-08 05:30 | 117.55 | 96.86
2018-03-08 06:00 | 122.85 | 101.36
2018-03-08 06:30 | 106.3 | 82.13
2018-03-08 07:00 | 117.24 | 96.31
2018-03-08 07:30 | 120.6 | 97.24
2018-03-08 08:00 | 112.35 | 88.59
2018-03-08 08:30 | 105.47 | 81.78
2018-03-08 09:00 | 97.25 | 72.12
2018-03-08 09:30 | 102.32 | 77.32
2018-03-08 10:00 | 105.46 | 81.56
2018-03-08 10:30 | 101.31 | 76.96
2018-03-08 11:00 | 100.1 | 74.91
2018-03-08 11:30 | 98.5 | 74.78
2018-03-08 12:00 | 107.22 | 82.73
2018-03-08 12:30 | 108.01 | 82.38
2018-03-08 13:00 | 108.27 | 85.2
2018-03-08 13:30 | 103.8 | 80.41
2018-03-08 14:00 | 107 | 82.04
2018-03-08 14:30 | 113.31 | 89.61
2018-03-08 15:00 | 118.81 | 96.18
2018-03-08 15:30 | 116.18 | 93.49
2018-03-08 16:00 | 116.16 | 94.91
2018-03-08 16:30 | 121.63 | 101.46
2018-03-08 17:00 | 121.04 | 100.21
2018-03-08 17:30 | 119.8 | 98.04
2018-03-08 18:00 | 116.78 | 94.8
2018-03-08 18:30 | 111.04 | 89.3
2018-03-08 19:00 | 128.56 | 107.82
2018-03-08 19:30 | 128.95 | 106.05
2018-03-08 20:00 | 132.87 | 111.53
2018-03-08 20:30 | 131.92 | 110.97
2018-03-08 21:00 | 123.33 | 100.99
2018-03-08 21:30 | 123.66 | 101.96
2018-03-08 22:00 | 118.2 | 96.05
2018-03-08 22:30 | 119.07 | 96.33
2018-03-08 23:00 | 115.34 | 91.98
2018-03-08 23:30 | 120.08 | 98.71
2018-03-09 | 118.25 | 97.81
2018-03-09 00:30 | 121.49 | 99.99
2018-03-09 01:00 | 120.98 | 100.61
2018-03-09 01:30 | 122.78 | 102.99
2018-03-09 02:00 | 117.69 | 97.35
2018-03-09 02:30 | 118.63 | 98.89
2018-03-09 03:00 | 120.08 | 99.69
2018-03-09 03:30 | 116.62 | 96.95
2018-03-09 04:00 | 119.53 | 98.86
2018-03-09 04:30 | 114.33 | 92.51
2018-03-09 05:00 | 113.93 | 93.73
2018-03-09 05:30 | 115.66 | 95.41
2018-03-09 06:00 | 119 | 98.49
2018-03-09 06:30 | 114.09 | 93.73
2018-03-09 07:00 | 122.55 | 103.57
2018-03-09 07:30 | 125.73 | 106.71
2018-03-09 08:00 | 117.47 | 97.53
2018-03-09 08:30 | 118.93 | 97.59
2018-03-09 09:00 | 113.53 | 92.06
2018-03-09 09:30 | 113.92 | 92.87
2018-03-09 10:00 | 109.37 | 87.8
2018-03-09 10:30 | 112.94 | 91.67
2018-03-09 11:00 | 110.66 | 89.8
2018-03-09 11:30 | 114.1 | 96.5
2018-03-09 12:00 | 114.21 | 96.77
2018-03-09 12:30 | 114.47 | 95.81
2018-03-09 13:00 | 106.8 | 84.96
2018-03-09 13:30 | 113.31 | 91.91
2018-03-09 14:00 | 115.84 | 94.55
2018-03-09 14:30 | 112.5 | 92.26
2018-03-09 15:00 | 108.48 | 87.85
2018-03-09 15:30 | 108.31 | 87.71
2018-03-09 16:00 | 107.05 | 87.26
2018-03-09 16:30 | 106.93 | 87.82
2018-03-09 17:00 | 111.01 | 91.31
2018-03-09 17:30 | 110.12 | 90.38
2018-03-09 18:00 | 115.29 | 96.05
2018-03-09 18:30 | 101.42 | 80.09
2018-03-09 19:00 | 113.19 | 94.33
2018-03-09 19:30 | 124.28 | 102.74
2018-03-09 20:00 | 119.42 | 96.76
2018-03-09 20:30 | 120.78 | 98.39
2018-03-09 21:00 | 128.6 | 108.43
2018-03-09 21:30 | 126.2 | 105.19
2018-03-09 22:00 | 125.45 | 102.16
2018-03-09 22:30 | 127.12 | 103.09
2018-03-09 23:00 | 119.53 | 94.79
2018-03-09 23:30 | 124.06 | 100.01
2018-03-10 | 128.03 | 104.16
2018-03-10 00:30 | 128.58 | 104.67
2018-03-10 01:00 | 128.65 | 105.46
2018-03-10 01:30 | 126.03 | 103.01
2018-03-10 02:00 | 122.13 | 99.19
2018-03-10 02:30 | 122.87 | 99.68
2018-03-10 03:00 | 119.56 | 98.38
2018-03-10 03:30 | 118.73 | 96.84
2018-03-10 04:00 | 119.09 | 96.94
2018-03-10 04:30 | 122.31 | 99.48
2018-03-10 05:00 | 119.71 | 98.11
2018-03-10 05:30 | 122.28 | 99.73
2018-03-10 06:00 | 123.94 | 100.73
2018-03-10 06:30 | 118.82 | 95.7
2018-03-10 07:00 | 123.56 | 102.79
2018-03-10 07:30 | 119.05 | 97.77
2018-03-10 08:00 | 120.4 | 98.16
2018-03-10 08:30 | 121.67 | 98.18
2018-03-10 09:00 | 113.71 | 90.44
2018-03-10 09:30 | 114.26 | 91.02
2018-03-10 10:00 | 111.81 | 88.38
2018-03-10 10:30 | 115.73 | 92.35
2018-03-10 11:00 | 110.39 | 86.41
2018-03-10 11:30 | 115.09 | 90.89
2018-03-10 12:00 | 117.88 | 93.97
2018-03-10 12:30 | 113.26 | 89.94
2018-03-10 13:00 | 104.64 | 82
2018-03-10 13:30 | 114.78 | 91.69
2018-03-10 14:00 | 112.9 | 89.82
2018-03-10 14:30 | 115.28 | 93.15
2018-03-10 15:00 | 120.42 | 97.73
2018-03-10 15:30 | 119.54 | 96.81
2018-03-10 16:00 | 123.35 | 100.13
2018-03-10 16:30 | 124.67 | 101.81
2018-03-10 17:00 | 118.06 | 95
2018-03-10 17:30 | 116.25 | 92.49
2018-03-10 18:00 | 118.55 | 93.3
2018-03-10 18:30 | 115.91 | 88.27
2018-03-10 19:00 | 119.16 | 93.89
2018-03-10 19:30 | 122.49 | 97.71
2018-03-10 20:00 | 122.52 | 97.35
2018-03-10 20:30 | 124.59 | 100.28
2018-03-10 21:00 | 125.08 | 100.24
2018-03-10 21:30 | 124.16 | 97.48
2018-03-10 22:00 | 128.95 | 102.75
2018-03-10 22:30 | 120.98 | 95.31
2018-03-10 23:00 | 116.58 | 90.77
2018-03-10 23:30 | 118.15 | 93.32
2018-03-11 | 119.7 | 93.7
2018-03-11 00:30 | 121.1 | 96.28
2018-03-11 01:00 | 126.9 | 102.63
2018-03-11 01:30 | 120.33 | 96.19
2018-03-11 02:00 | 125.16 | 101
2018-03-11 02:30 | 127.05 | 103.65
2018-03-11 03:00 | 119.8 | 96.53
2018-03-11 03:30 | 121.07 | 97.72
2018-03-11 04:00 | 115.32 | 91.91
2018-03-11 04:30 | 118.24 | 94.92
2018-03-11 05:00 | 101.81 | 80.05
2018-03-11 05:30 | 108.22 | 86.35
2018-03-11 06:00 | 110.55 | 88.97
2018-03-11 06:30 | 100.8 | 78.39
2018-03-11 07:00 | 109.92 | 88.18
2018-03-11 07:30 | 116.31 | 94.08
2018-03-11 08:00 | 120.5 | 97.59
2018-03-11 08:30 | 126.1 | 103.49
2018-03-11 09:00 | 126.67 | 103.72
2018-03-11 09:30 | 124.59 | 102.51
2018-03-11 10:00 | 120.93 | 99.49
2018-03-11 10:30 | 116.09 | 94.35
2018-03-11 11:00 | 106.27 | 85.63
2018-03-11 11:30 | 107.64 | 87
2018-03-11 12:00 | 106.36 | 86.32
2018-03-11 12:30 | 116.3 | 97.82
2018-03-11 13:00 | 114.73 | 94.47
2018-03-11 13:30 | 118.21 | 95.11
2018-03-11 14:00 | 120.85 | 97.59
2018-03-11 14:30 | 111.88 | 86.59
2018-03-11 15:00 | 119.47 | 95.6
2018-03-11 15:30 | 121.17 | 96.86
2018-03-11 16:00 | 120.98 | 96.9
2018-03-11 16:30 | 124.05 | 100.08
2018-03-11 17:00 | 127.28 | 102.17
2018-03-11 17:30 | 130.75 | 104.9
2018-03-11 18:00 | 135.94 | 110.21
2018-03-11 18:30 | 128.77 | 101.46
2018-03-11 19:00 | 126.93 | 102.74
2018-03-11 19:30 | 129.58 | 104.18
2018-03-11 20:00 | 132.79 | 105.89
2018-03-11 20:30 | 130.9 | 104.03
2018-03-11 21:00 | 121.53 | 94.94
2018-03-11 21:30 | 119.46 | 92.26
2018-03-11 22:00 | 122.24 | 96.62
2018-03-11 22:30 | 123.54 | 97.99
2018-03-11 23:00 | 132.18 | 108.21
2018-03-11 23:30 | 128.59 | 105.03
2018-03-12 | 121.01 | 96.52
2018-03-12 00:30 | 123.44 | 99.37
2018-03-12 01:00 | 122.92 | 98.87
2018-03-12 01:30 | 122.1 | 99.59
2018-03-12 02:00 | 120.05 | 97.52
2018-03-12 02:30 | 114.63 | 91.94
2018-03-12 03:00 | 111.73 | 89.43
2018-03-12 03:30 | 111.87 | 89.46
2018-03-12 04:00 | 122.6 | 100.91
2018-03-12 04:30 | 118.71 | 97.15
2018-03-12 05:00 | 116.87 | 95
2018-03-12 05:30 | 110.81 | 87.94
2018-03-12 06:00 | 121.82 | 99.44
2018-03-12 06:30 | 112.68 | 88.29
2018-03-12 07:00 | 117.07 | 94.59
2018-03-12 07:30 | 128.35 | 105.47
2018-03-12 08:00 | 114.57 | 90.41
2018-03-12 08:30 | 119.98 | 95.96
2018-03-12 09:00 | 116.9 | 92.72
2018-03-12 09:30 | 122.23 | 98.5
2018-03-12 10:00 | 121.38 | 98.69
2018-03-12 10:30 | 121.05 | 97.91
2018-03-12 11:00 | 120.6 | 97.09
2018-03-12 11:30 | 121.77 | 97.03
2018-03-12 12:00 | 119.64 | 95.24
2018-03-12 12:30 | 123.31 | 98.06
2018-03-12 13:00 | 122.91 | 99.83
2018-03-12 13:30 | 117.6 | 94.47
2018-03-12 14:00 | 115.11 | 89.54
2018-03-12 14:30 | 114.56 | 88.6
2018-03-12 15:00 | 108.44 | 83.43
2018-03-12 15:30 | 110.95 | 87.93
2018-03-12 16:00 | 116.02 | 92.63
2018-03-12 16:30 | 117.46 | 94.7
2018-03-12 17:00 | 116.78 | 94.92
2018-03-12 17:30 | 116.84 | 94.65
2018-03-12 18:00 | 117.46 | 93.77
2018-03-12 18:30 | 117.31 | 92.89
2018-03-12 19:00 | 118.25 | 95.72
2018-03-12 19:30 | 124.05 | 100.54
2018-03-12 20:00 | 126.53 | 101.41
2018-03-12 20:30 | 123.94 | 99.42
2018-03-12 21:00 | 122.57 | 97.14
2018-03-12 21:30 | 122.22 | 98.2
2018-03-12 22:00 | 119.24 | 95.41
2018-03-12 22:30 | 121.1 | 97.52
2018-03-12 23:00 | 122.6 | 98.47
2018-03-12 23:30 | 120.35 | 97.62
2018-03-13 | 118.63 | 94.83
2018-03-13 00:30 | 122.76 | 100.46
2018-03-13 01:00 | 108.72 | 89.2
2018-03-13 01:30 | 109.77 | 90.45
2018-03-13 02:00 | 109.88 | 91.18
2018-03-13 02:30 | 106.54 | 88.54
2018-03-13 03:00 | 105.9 | 88.4
2018-03-13 03:30 | 100.55 | 81.37
2018-03-13 04:00 | 102.39 | 83.51
2018-03-13 04:30 | 93.5 | 76
2018-03-13 05:00 | 98.12 | 80.69
2018-03-13 05:30 | 95.2 | 78.54
2018-03-13 06:00 | 103.13 | 86.75
2018-03-13 06:30 | 96.79 | 77.45
2018-03-13 07:00 | 99.63 | 81.3
2018-03-13 07:30 | 99.95 | 81.14
2018-03-13 08:00 | 98.97 | 81.25
2018-03-13 08:30 | 96.56 | 77.86
2018-03-13 09:00 | 94.12 | 75.28
2018-03-13 09:30 | 90.14 | 71.35
2018-03-13 10:00 | 89.61 | 72.3
2018-03-13 10:30 | 84.77 | 66.62
2018-03-13 11:00 | 94.05 | 77.78
2018-03-13 11:30 | 96.03 | 81.22
2018-03-13 12:00 | 91.12 | 76.05
2018-03-13 12:30 | 96.54 | 80.6
2018-03-13 13:00 | 104.8 | 89.74
2018-03-13 13:30 | 103 | 88.76
2018-03-13 14:00 | 100.3 | 83.7
2018-03-13 14:30 | 103.21 | 87.16
2018-03-13 15:00 | 95.72 | 78.85
2018-03-13 15:30 | 99.18 | 81.2
2018-03-13 16:00 | 107.45 | 89.16
2018-03-13 16:30 | 104.94 | 87.05
2018-03-13 17:00 | 106.66 | 88.08
2018-03-13 17:30 | 101.76 | 82.67
2018-03-13 18:00 | 104.84 | 86.43
2018-03-13 18:30 | 99.41 | 79.69
2018-03-13 19:00 | 106.06 | 86.91
2018-03-13 19:30 | 114.01 | 95.64
2018-03-13 20:00 | 110.61 | 91.97
2018-03-13 20:30 | 109.18 | 90.95
2018-03-13 21:00 | 109.82 | 92.05
2018-03-13 21:30 | 112.89 | 95.16
2018-03-13 22:00 | 108.13 | 91.02
2018-03-13 22:30 | 106.34 | 89.01
2018-03-13 23:00 | 106.65 | 91.41
2018-03-13 23:30 | 109.7 | 94.38
2018-03-14 | 109.49 | 94.25
2018-03-14 00:30 | 106.88 | 90.86
2018-03-14 01:00 | 99.09 | 83.76
2018-03-14 01:30 | 103.75 | 88.14
2018-03-14 02:00 | 100.14 | 84.84
2018-03-14 02:30 | 99.15 | 83.72
2018-03-14 03:00 | 103.39 | 88.43
2018-03-14 03:30 | 94.63 | 78.77
2018-03-14 04:00 | 98.41 | 83.43
2018-03-14 04:30 | 98.2 | 83.49
2018-03-14 05:00 | 99.58 | 85.07
2018-03-14 05:30 | 99.28 | 84.48
2018-03-14 06:00 | 105.28 | 89.88
2018-03-14 06:30 | 90.35 | 74.63
2018-03-14 07:00 | 87.67 | 73.09
2018-03-14 07:30 | 84.21 | 71.08
2018-03-14 08:00 | 88.27 | 74.59
2018-03-14 08:30 | 88.93 | 74.18
2018-03-14 09:00 | 95.89 | 81.91
2018-03-14 09:30 | 97.25 | 84.18
2018-03-14 10:00 | 99.88 | 85.81
2018-03-14 10:30 | 97.4 | 83.45
2018-03-14 11:00 | 102.87 | 87.91
2018-03-14 11:30 | 101.5 | 86.55
2018-03-14 12:00 | 103.47 | 88.57
2018-03-14 12:30 | 102.82 | 87.76
2018-03-14 13:00 | 95.09 | 80.37
2018-03-14 13:30 | 100.48 | 83.99
2018-03-14 14:00 | 105.3 | 89.96
2018-03-14 14:30 | 97.28 | 80.32
2018-03-14 15:00 | 106 | 87.73
2018-03-14 15:30 | 99.34 | 80.88
2018-03-14 16:00 | 97.34 | 79.27
2018-03-14 16:30 | 97.27 | 78.3
2018-03-14 17:00 | 100.22 | 81.62
2018-03-14 17:30 | 101.44 | 83.98
2018-03-14 18:00 | 112.57 | 95.9
2018-03-14 18:30 | 100.07 | 82.36
2018-03-14 19:00 | 99.91 | 84.09
2018-03-14 19:30 | 112.05 | 95.65
2018-03-14 20:00 | 108.4 | 91.77
2018-03-14 20:30 | 106.29 | 89.65
2018-03-14 21:00 | 101.77 | 85.29
2018-03-14 21:30 | 102.37 | 84.99
2018-03-14 22:00 | 93.87 | 74.31
2018-03-14 22:30 | 95.8 | 75.31
2018-03-14 23:00 | 104.5 | 83.09
2018-03-14 23:30 | 101.37 | 79.96
2018-03-15 | 103.14 | 84.67
2018-03-15 00:30 | 104.78 | 85.98
2018-03-15 01:00 | 100.59 | 81.14
2018-03-15 01:30 | 104.13 | 84.6
2018-03-15 02:00 | 110.39 | 92.14
2018-03-15 02:30 | 112.55 | 94.11
2018-03-15 03:00 | 108.41 | 89.36
2018-03-15 03:30 | 111.22 | 90.75
2018-03-15 04:00 | 112.41 | 92.44
2018-03-15 04:30 | 118.9 | 99.36
2018-03-15 05:00 | 120.92 | 102.63
2018-03-15 05:30 | 104.57 | 86.66
2018-03-15 06:00 | 112.16 | 94.54
2018-03-15 06:30 | 105.96 | 87.39
2018-03-15 07:00 | 120.44 | 103.72
2018-03-15 07:30 | 116.26 | 99.25
2018-03-15 08:00 | 123.7 | 105.29
2018-03-15 08:30 | 124.78 | 105.79
2018-03-15 09:00 | 121.23 | 101.78
2018-03-15 09:30 | 104.68 | 84.32
2018-03-15 10:00 | 104.75 | 84.08
2018-03-15 10:30 | 103.7 | 82.53
2018-03-15 11:00 | 103.55 | 83.16
2018-03-15 11:30 | 105.91 | 85.05
2018-03-15 12:00 | 112.17 | 91.67
2018-03-15 12:30 | 107.89 | 87.54
2018-03-15 13:00 | 102.59 | 83.78
2018-03-15 13:30 | 103.6 | 83.79
2018-03-15 14:00 | 105.96 | 86.49
2018-03-15 14:30 | 108.46 | 88.79
2018-03-15 15:00 | 111.47 | 91.8
2018-03-15 15:30 | 112.85 | 93.65
2018-03-15 16:00 | 111.13 | 90.99
2018-03-15 16:30 | 109.04 | 88.54
2018-03-15 17:00 | 108.42 | 86.68
2018-03-15 17:30 | 110.95 | 89.79
2018-03-15 18:00 | 127.51 | 104.99
2018-03-15 18:30 | 109.91 | 88.67
2018-03-15 19:00 | 117.58 | 96.83
2018-03-15 19:30 | 115.72 | 93.11
2018-03-15 20:00 | 120.73 | 97.64
2018-03-15 20:30 | 125.99 | 104.51
2018-03-15 21:00 | 118.81 | 97.47
2018-03-15 21:30 | 114.19 | 93.75
2018-03-15 22:00 | 117.08 | 96.72
2018-03-15 22:30 | 118.45 | 98.66
2018-03-15 23:00 | 124.24 | 106.03
2018-03-15 23:30 | 123.56 | 105.1
2018-03-16 | 118.32 | 100.09
2018-03-16 00:30 | 122.3 | 104.47
2018-03-16 01:00 | 111.06 | 92.28
2018-03-16 01:30 | 109.82 | 90.4
2018-03-16 02:00 | 112.29 | 94.26
2018-03-16 02:30 | 114.83 | 96.39
2018-03-16 03:00 | 112.43 | 94.56
2018-03-16 03:30 | 108.62 | 91.17
2018-03-16 04:00 | 119.68 | 102.74
2018-03-16 04:30 | 119.64 | 103.36
2018-03-16 05:00 | 113.92 | 95.71
2018-03-16 05:30 | 120.73 | 102.3
2018-03-16 06:00 | 108.63 | 89.45
2018-03-16 06:30 | 104.67 | 85.41
2018-03-16 07:00 | 106.92 | 88.26
2018-03-16 07:30 | 123.28 | 104.24
2018-03-16 08:00 | 113.79 | 94.52
2018-03-16 08:30 | 115.02 | 95.1
2018-03-16 09:00 | 123.22 | 103.29
2018-03-16 09:30 | 113.08 | 93.94
2018-03-16 10:00 | 124.56 | 106.18
2018-03-16 10:30 | 123.36 | 104.28
2018-03-16 11:00 | 111.16 | 92.36
2018-03-16 11:30 | 116.74 | 97.89
2018-03-16 12:00 | 111.06 | 92.6
2018-03-16 12:30 | 118.98 | 98.15
2018-03-16 13:00 | 114.61 | 93.26
2018-03-16 13:30 | 109.69 | 86.74
2018-03-16 14:00 | 114.08 | 89.19
2018-03-16 14:30 | 115.05 | 90.87
2018-03-16 15:00 | 110.57 | 85.06
2018-03-16 15:30 | 113.4 | 87.76
2018-03-16 16:00 | 115.42 | 92.27
2018-03-16 16:30 | 119.5 | 97.79
2018-03-16 17:00 | 120.55 | 98.56
2018-03-16 17:30 | 120.46 | 99.7
2018-03-16 18:00 | 124.57 | 104.59
2018-03-16 18:30 | 118.77 | 98.3
2018-03-16 19:00 | 127.16 | 109.35
2018-03-16 19:30 | 127.53 | 108.64
2018-03-16 20:00 | 129.53 | 110.47
2018-03-16 20:30 | 126.45 | 107.81
2018-03-16 21:00 | 125.22 | 106.43
2018-03-16 21:30 | 128.4 | 108.85
2018-03-16 22:00 | 126.46 | 108.05
2018-03-16 22:30 | 125.68 | 106.78
2018-03-16 23:00 | 119.53 | 100.15
2018-03-16 23:30 | 111.3 | 92.87
2018-03-17 | 110.6 | 92.52
2018-03-17 00:30 | 114.09 | 95.37
2018-03-17 01:00 | 114.33 | 94.27
2018-03-17 01:30 | 110.99 | 91.92
2018-03-17 02:00 | 126.23 | 108
2018-03-17 02:30 | 120.94 | 104.12
2018-03-17 03:00 | 127.62 | 109.76
2018-03-17 03:30 | 114.8 | 97.52
2018-03-17 04:00 | 114.92 | 97.11
2018-03-17 04:30 | 125 | 106.56
2018-03-17 05:00 | 121.65 | 102.82
2018-03-17 05:30 | 124.37 | 106.82
2018-03-17 06:00 | 120.99 | 103.4
2018-03-17 06:30 | 109.35 | 89.32
2018-03-17 07:00 | 114.83 | 97.28
2018-03-17 07:30 | 119.61 | 101.32
2018-03-17 08:00 | 115.22 | 96.44
2018-03-17 08:30 | 124.49 | 106.8
2018-03-17 09:00 | 113.51 | 94.77
2018-03-17 09:30 | 125.75 | 106.78
2018-03-17 10:00 | 121.28 | 103.12
2018-03-17 10:30 | 124.64 | 105.42
2018-03-17 11:00 | 127.27 | 107.42
2018-03-17 11:30 | 116.68 | 95.15
2018-03-17 12:00 | 118.38 | 96.45
2018-03-17 12:30 | 123.96 | 101.87
2018-03-17 13:00 | 120.27 | 98.39
2018-03-17 13:30 | 111.25 | 89.65
2018-03-17 14:00 | 114.63 | 93.1
2018-03-17 14:30 | 114.18 | 92.63
2018-03-17 15:00 | 113.9 | 93.69
2018-03-17 15:30 | 113.44 | 93.28
2018-03-17 16:00 | 125.78 | 106.71
2018-03-17 16:30 | 127.67 | 108.38
2018-03-17 17:00 | 130.88 | 110
2018-03-17 17:30 | 121.18 | 101.21
2018-03-17 18:00 | 116.49 | 96
2018-03-17 18:30 | 115.69 | 95.06
2018-03-17 19:00 | 120.63 | 101.06
2018-03-17 19:30 | 125.87 | 106.03
2018-03-17 20:00 | 120.7 | 101.18
2018-03-17 20:30 | 112.06 | 93.6
2018-03-17 21:00 | 117.08 | 99.56
2018-03-17 21:30 | 119.59 | 101.63
2018-03-17 22:00 | 117.96 | 100.59
2018-03-17 22:30 | 119.35 | 101.71
2018-03-17 23:00 | 109.09 | 91.26
2018-03-17 23:30 | 111.35 | 93.97
2018-03-18 | 118.64 | 101.37
2018-03-18 00:30 | 109.9 | 91.66
2018-03-18 01:00 | 109.2 | 91.69
2018-03-18 01:30 | 112.56 | 95.49
2018-03-18 02:00 | 112.53 | 96.39
2018-03-18 02:30 | 108.99 | 93.14
2018-03-18 03:00 | 103.69 | 87.78
2018-03-18 03:30 | 103.45 | 87.19
2018-03-18 04:00 | 106.77 | 89.55
2018-03-18 04:30 | 107.56 | 91.43
2018-03-18 05:00 | 108.83 | 92.78
2018-03-18 05:30 | 112.48 | 95.68
2018-03-18 06:00 | 105.23 | 88.36
2018-03-18 06:30 | 91.99 | 73.77
2018-03-18 07:00 | 100.24 | 83.4
2018-03-18 07:30 | 112.65 | 95.46
2018-03-18 08:00 | 110.76 | 90.77
2018-03-18 08:30 | 118.18 | 98.03
2018-03-18 09:00 | 115.4 | 94.63
2018-03-18 09:30 | 114.48 | 92.89
2018-03-18 10:00 | 122.21 | 104.43
2018-03-18 10:30 | 116.87 | 98.33
2018-03-18 11:00 | 121.64 | 103.29
2018-03-18 11:30 | 115.38 | 94.46
2018-03-18 12:00 | 116.17 | 96.99
2018-03-18 12:30 | 120.97 | 101.99
2018-03-18 13:00 | 117.24 | 97.55
2018-03-18 13:30 | 110.7 | 90.75
2018-03-18 14:00 | 116.63 | 96.78
2018-03-18 14:30 | 114.24 | 93.99
2018-03-18 15:00 | 112.64 | 92.53
2018-03-18 15:30 | 114.92 | 94.56
2018-03-18 16:00 | 117.81 | 97.35
2018-03-18 16:30 | 127.34 | 106.51
2018-03-18 17:00 | 126.88 | 105.19
2018-03-18 17:30 | 122.9 | 101.2
2018-03-18 18:00 | 127.8 | 106
2018-03-18 18:30 | 118.59 | 95.68
2018-03-18 19:00 | 124.27 | 102.63
2018-03-18 19:30 | 128 | 105.54
2018-03-18 20:00 | 127.28 | 105.01
2018-03-18 20:30 | 129.11 | 107.29
2018-03-18 21:00 | 128.75 | 107.07
2018-03-18 21:30 | 122.04 | 100.2
2018-03-18 22:00 | 121.01 | 99.23
2018-03-18 22:30 | 119 | 98.02
2018-03-18 23:00 | 117.68 | 96.7
2018-03-18 23:30 | 121.33 | 100.59
2018-03-19 | 118.46 | 98.84
2018-03-19 00:30 | 108.62 | 88.04
2018-03-19 01:00 | 114.99 | 93.21
2018-03-19 01:30 | 114.12 | 93.24
2018-03-19 02:00 | 112.32 | 91.5
2018-03-19 02:30 | 112.07 | 91.59
2018-03-19 03:00 | 115.98 | 96.58
2018-03-19 03:30 | 108.74 | 88.07
2018-03-19 04:00 | 108.16 | 88.42
2018-03-19 04:30 | 118.29 | 98
2018-03-19 05:00 | 118.84 | 98.26
2018-03-19 05:30 | 115.55 | 93.97
2018-03-19 06:00 | 110.64 | 89.08
2018-03-19 06:30 | 108.41 | 83.67
2018-03-19 07:00 | 107.76 | 82.73
2018-03-19 07:30 | 108.42 | 81.98
2018-03-19 08:00 | 119.15 | 95.44
2018-03-19 08:30 | 113.38 | 90.31
2018-03-19 09:00 | 112.02 | 89.35
2018-03-19 09:30 | 119.37 | 98.52
2018-03-19 10:00 | 116.99 | 96.67
2018-03-19 10:30 | 112.92 | 90.34
2018-03-19 11:00 | 109.05 | 85.85
2018-03-19 11:30 | 112.84 | 90.35
2018-03-19 12:00 | 109.36 | 88.28
2018-03-19 12:30 | 110.91 | 90.09
2018-03-19 13:00 | 105.32 | 85.19
2018-03-19 13:30 | 103.32 | 79.6
2018-03-19 14:00 | 114.85 | 92.6
2018-03-19 14:30 | 115.74 | 93.15
2018-03-19 15:00 | 109.76 | 86.98
2018-03-19 15:30 | 105.67 | 82.07
2018-03-19 16:00 | 112.91 | 90.62
2018-03-19 16:30 | 115.67 | 93.61
2018-03-19 17:00 | 118.36 | 97.83
2018-03-19 17:30 | 123.15 | 101.87
2018-03-19 18:00 | 120.28 | 98.43
2018-03-19 18:30 | 120.61 | 98.53
2018-03-19 19:00 | 124.56 | 102.91
2018-03-19 19:30 | 128.27 | 108.27
2018-03-19 20:00 | 127.64 | 107.5
2018-03-19 20:30 | 122.57 | 101.44
2018-03-19 21:00 | 121.08 | 101.13
2018-03-19 21:30 | 119.39 | 99.69
2018-03-19 22:00 | 118.42 | 100.38
2018-03-19 22:30 | 114.22 | 96.64
2018-03-19 23:00 | 113.45 | 95.4
2018-03-19 23:30 | 113.71 | 95.2
2018-03-20 | 111.44 | 91.24
2018-03-20 00:30 | 113.59 | 92.68
2018-03-20 01:00 | 114.81 | 96.11
2018-03-20 01:30 | 108.3 | 89.63
2018-03-20 02:00 | 108.54 | 91.41
2018-03-20 02:30 | 110.54 | 93.91
2018-03-20 03:00 | 107.59 | 91
2018-03-20 03:30 | 106.49 | 88.55
2018-03-20 04:00 | 107.25 | 89.95
2018-03-20 04:30 | 106.26 | 87.94
2018-03-20 05:00 | 108.38 | 90.44
2018-03-20 05:30 | 110.15 | 92.74
2018-03-20 06:00 | 111.37 | 94.26
2018-03-20 06:30 | 105.06 | 88.15
2018-03-20 07:00 | 108 | 90.98
2018-03-20 07:30 | 106.97 | 89.96
2018-03-20 08:00 | 105.93 | 88.79
2018-03-20 08:30 | 103.75 | 83.43
2018-03-20 09:00 | 104 | 83.59
2018-03-20 09:30 | 105.18 | 86.36
2018-03-20 10:00 | 115.81 | 96.89
2018-03-20 10:30 | 119.66 | 100.84
2018-03-20 11:00 | 122.9 | 104.06
2018-03-20 11:30 | 116.04 | 96.92
2018-03-20 12:00 | 124.6 | 105.19
2018-03-20 12:30 | 115.62 | 95.71
2018-03-20 13:00 | 114.96 | 95.07
2018-03-20 13:30 | 118.1 | 98.17
2018-03-20 14:00 | 118.39 | 95.93
2018-03-20 14:30 | 115.52 | 92.29
2018-03-20 15:00 | 128.58 | 105.83
2018-03-20 15:30 | 123.26 | 100.55
2018-03-20 16:00 | 120.31 | 100.35
2018-03-20 16:30 | 118.8 | 99.05
2018-03-20 17:00 | 116.57 | 97.76
2018-03-20 17:30 | 113.69 | 94.18
2018-03-20 18:00 | 120.92 | 100.66
2018-03-20 18:30 | 112.38 | 89.55
2018-03-20 19:00 | 116.85 | 94.71
2018-03-20 19:30 | 125.53 | 103.34
2018-03-20 20:00 | 121.09 | 100.69
2018-03-20 20:30 | 120.72 | 101.81
2018-03-20 21:00 | 120.89 | 102.41
2018-03-20 21:30 | 107.37 | 88.9
2018-03-20 22:00 | 100.21 | 83.05
2018-03-20 22:30 | 105.33 | 88.05
2018-03-20 23:00 | 97.18 | 79.63
2018-03-20 23:30 | 103.34 | 83.54
2018-03-21 | 107.17 | 88.31
2018-03-21 00:30 | 103.08 | 84.44
2018-03-21 01:00 | 103 | 83.8
2018-03-21 01:30 | 110.57 | 93.23
2018-03-21 02:00 | 109.88 | 91.72
2018-03-21 02:30 | 111.22 | 92.81
2018-03-21 03:00 | 104.71 | 86.11
2018-03-21 03:30 | 103.32 | 84.39
2018-03-21 04:00 | 111.44 | 93.48
2018-03-21 04:30 | 109.28 | 92.05
2018-03-21 05:00 | 108.5 | 91.25
2018-03-21 05:30 | 108.09 | 91.02
2018-03-21 06:00 | 110.62 | 92.48
2018-03-21 06:30 | 101.55 | 80.76
2018-03-21 07:00 | 107.32 | 89.24
2018-03-21 07:30 | 117.91 | 100.82
2018-03-21 08:00 | 116.93 | 98.7
2018-03-21 08:30 | 116.18 | 97.09
2018-03-21 09:00 | 114.85 | 95.71
2018-03-21 09:30 | 111.85 | 91.37
2018-03-21 10:00 | 109.19 | 87.52
2018-03-21 10:30 | 114.82 | 92.91
2018-03-21 11:00 | 119.73 | 97.46
2018-03-21 11:30 | 112.13 | 91.61
2018-03-21 12:00 | 115.87 | 95.39
2018-03-21 12:30 | 111.22 | 91.4
2018-03-21 13:00 | 115.99 | 95.79
2018-03-21 13:30 | 119.06 | 97.54
2018-03-21 14:00 | 118.77 | 95.94
2018-03-21 14:30 | 115.87 | 92.97
2018-03-21 15:00 | 113.96 | 91.4
2018-03-21 15:30 | 115.92 | 93.56
2018-03-21 16:00 | 117.57 | 95.48
2018-03-21 16:30 | 117.34 | 95.2
2018-03-21 17:00 | 117.91 | 95.88
2018-03-21 17:30 | 118.25 | 95.58
2018-03-21 18:00 | 118.42 | 96.42
2018-03-21 18:30 | 119.01 | 96.32
2018-03-21 19:00 | 115.27 | 92.11
2018-03-21 19:30 | 120.47 | 97.44
2018-03-21 20:00 | 122.06 | 99.61
2018-03-21 20:30 | 118.47 | 96.16
2018-03-21 21:00 | 118.49 | 97.07
2018-03-21 21:30 | 119.29 | 98.27
2018-03-21 22:00 | 119.04 | 98.81
2018-03-21 22:30 | 105.41 | 84.94
2018-03-21 23:00 | 113.85 | 95.03
2018-03-21 23:30 | 103.61 | 84.13
2018-03-22 | 106.98 | 87.09
2018-03-22 00:30 | 106.6 | 87.64
2018-03-22 01:00 | 107.62 | 87.47
2018-03-22 01:30 | 110.84 | 91.91
2018-03-22 02:00 | 105.61 | 86.79
2018-03-22 02:30 | 113.22 | 93.94
2018-03-22 03:00 | 107.48 | 88.07
2018-03-22 03:30 | 107.88 | 89.31
2018-03-22 04:00 | 109.74 | 91.31
2018-03-22 04:30 | 117.54 | 98.96
2018-03-22 05:00 | 116.33 | 97.43
2018-03-22 05:30 | 112.43 | 92.99
2018-03-22 06:00 | 114.96 | 95.23
2018-03-22 06:30 | 113.78 | 94
2018-03-22 07:00 | 107.33 | 86.84
2018-03-22 07:30 | 100.96 | 79.22
2018-03-22 08:00 | 99.22 | 77.14
2018-03-22 08:30 | 98.73 | 78.14
2018-03-22 09:00 | 92.32 | 72.01
2018-03-22 09:30 | 97.53 | 78.74
2018-03-22 10:00 | 100.48 | 83.75
2018-03-22 10:30 | 108.72 | 90.63
2018-03-22 11:00 | 109.51 | 92.68
2018-03-22 11:30 | 104.35 | 87.51
2018-03-22 12:00 | 101.92 | 84.74
2018-03-22 12:30 | 101.93 | 83.43
2018-03-22 13:00 | 109.02 | 90.3
2018-03-22 13:30 | 101.53 | 82.03
2018-03-22 14:00 | 108.52 | 88.03
2018-03-22 14:30 | 115.5 | 95.79
2018-03-22 15:00 | 112.29 | 92.33
2018-03-22 15:30 | 108.91 | 88.85
2018-03-22 16:00 | 116.36 | 97.88
2018-03-22 16:30 | 118.44 | 97.87
2018-03-22 17:00 | 115.94 | 94.69
2018-03-22 17:30 | 112.33 | 90.31
2018-03-22 18:00 | 119.87 | 97.1
2018-03-22 18:30 | 116.68 | 94.31
2018-03-22 19:00 | 122.74 | 101.52
2018-03-22 19:30 | 122.14 | 101.38
2018-03-22 20:00 | 118.84 | 97.3
2018-03-22 20:30 | 121.98 | 101.71
2018-03-22 21:00 | 119.37 | 99.72
2018-03-22 21:30 | 119.23 | 98.53
2018-03-22 22:00 | 119.98 | 98.68
2018-03-22 22:30 | 111 | 89.92
2018-03-22 23:00 | 111.44 | 91.02
2018-03-22 23:30 | 105.69 | 85.17
2018-03-23 | 109.46 | 89.98
2018-03-23 00:30 | 113.12 | 93.17
2018-03-23 01:00 | 114.12 | 94.71
2018-03-23 01:30 | 122.07 | 104.4
2018-03-23 02:00 | 122.74 | 105.94
2018-03-23 02:30 | 121.85 | 104.72
2018-03-23 03:00 | 111.16 | 92.66
2018-03-23 03:30 | 112.31 | 93.31
2018-03-23 04:00 | 113.91 | 94.99
2018-03-23 04:30 | 116.29 | 96.75
2018-03-23 05:00 | 110.89 | 91.97
2018-03-23 05:30 | 108.67 | 91.05
2018-03-23 06:00 | 115.13 | 97.24
2018-03-23 06:30 | 99.82 | 80.94
2018-03-23 07:00 | 106.74 | 90.01
2018-03-23 07:30 | 110.29 | 93.36
2018-03-23 08:00 | 113.1 | 94.48
2018-03-23 08:30 | 113.5 | 94.4
2018-03-23 09:00 | 111.53 | 91.81
2018-03-23 09:30 | 108.64 | 90.41
2018-03-23 10:00 | 108.4 | 92.31
2018-03-23 10:30 | 108.89 | 91.93
2018-03-23 11:00 | 97.48 | 77.28
2018-03-23 11:30 | 96.47 | 77.5
2018-03-23 12:00 | 100.33 | 81.2
2018-03-23 12:30 | 101.13 | 83.1
2018-03-23 13:00 | 107.35 | 89.49
2018-03-23 13:30 | 107.04 | 88.15
2018-03-23 14:00 | 107.77 | 87.71
2018-03-23 14:30 | 111.16 | 90.27
2018-03-23 15:00 | 108.96 | 87.36
2018-03-23 15:30 | 105.99 | 83.41
2018-03-23 16:00 | 114.96 | 94.86
2018-03-23 16:30 | 114.05 | 95.82
2018-03-23 17:00 | 117.06 | 97.93
2018-03-23 17:30 | 120.7 | 102.65
2018-03-23 18:00 | 126.39 | 107.83
2018-03-23 18:30 | 119.74 | 100.27
2018-03-23 19:00 | 117.06 | 98.13
2018-03-23 19:30 | 125.71 | 105.55
2018-03-23 20:00 | 124.03 | 103.35
2018-03-23 20:30 | 127.19 | 106.73
2018-03-23 21:00 | 123.84 | 104.27
2018-03-23 21:30 | 121.59 | 101.9
2018-03-23 22:00 | 119.99 | 100.4
2018-03-23 22:30 | 121.19 | 101.17
2018-03-23 23:00 | 124.96 | 105.15
2018-03-23 23:30 | 119.43 | 100.72
2018-03-24 | 124.07 | 105.86
2018-03-24 00:30 | 123.03 | 104.95
2018-03-24 01:00 | 124.17 | 105.62
2018-03-24 01:30 | 116.82 | 98.53
2018-03-24 02:00 | 111.7 | 94.3
2018-03-24 02:30 | 110.9 | 92.05
2018-03-24 03:00 | 113.37 | 96.02
2018-03-24 03:30 | 109.2 | 92.25
2018-03-24 04:00 | 116.36 | 100.21
2018-03-24 04:30 | 117.77 | 101.58
2018-03-24 05:00 | 109.37 | 92.99
2018-03-24 05:30 | 120.05 | 103.1
2018-03-24 06:00 | 108.68 | 91.34
2018-03-24 06:30 | 107.08 | 86.75
2018-03-24 07:00 | 110.59 | 90.51
2018-03-24 07:30 | 104.68 | 83.75
2018-03-24 08:00 | 110.11 | 88.86
2018-03-24 08:30 | 117.69 | 96.37
2018-03-24 09:00 | 112.64 | 91.58
2018-03-24 09:30 | 106.4 | 85.74
2018-03-24 10:00 | 116.33 | 95.65
2018-03-24 10:30 | 111.9 | 90.37
2018-03-24 11:00 | 112.18 | 89.29
2018-03-24 11:30 | 110.29 | 90.43
2018-03-24 12:00 | 116.03 | 97.82
2018-03-24 12:30 | 116.73 | 98.2
2018-03-24 13:00 | 114.71 | 95.43
2018-03-24 13:30 | 116.29 | 97.2
2018-03-24 14:00 | 116.77 | 98.15
2018-03-24 14:30 | 117.99 | 98.53
2018-03-24 15:00 | 117.41 | 97.85
2018-03-24 15:30 | 107.52 | 88.36
2018-03-24 16:00 | 109.49 | 91.25
2018-03-24 16:30 | 114.13 | 94.53
2018-03-24 17:00 | 119.6 | 98.66
2018-03-24 17:30 | 121.76 | 102.57
2018-03-24 18:00 | 121.82 | 102.28
2018-03-24 18:30 | 112.94 | 93.64
2018-03-24 19:00 | 126.46 | 109.43
2018-03-24 19:30 | 125.85 | 108.34
2018-03-24 20:00 | 126.04 | 108.17
2018-03-24 20:30 | 120.14 | 101.33
2018-03-24 21:00 | 117.71 | 99.53
2018-03-24 21:30 | 116.5 | 98.14
2018-03-24 22:00 | 115.07 | 96.34
2018-03-24 22:30 | 112.85 | 94.48
2018-03-24 23:00 | 111.48 | 94.17
2018-03-24 23:30 | 110.79 | 93.78
2018-03-25 | 110.82 | 94.23
2018-03-25 00:30 | 109.4 | 91.84
2018-03-25 01:00 | 113.72 | 96.74
2018-03-25 01:30 | 125.23 | 108.18
2018-03-25 02:00 | 119.79 | 102.11
2018-03-25 02:30 | 120.35 | 102.56
2018-03-25 03:00 | 114.4 | 96.35
2018-03-25 03:30 | 116.33 | 100.03
2018-03-25 04:00 | 114.42 | 98.33
2018-03-25 04:30 | 113.73 | 97.39
2018-03-25 05:00 | 116.67 | 100.38
2018-03-25 05:30 | 110.77 | 93.7
2018-03-25 06:00 | 120.65 | 103.06
2018-03-25 06:30 | 111.17 | 94.78
2018-03-25 07:00 | 109.21 | 93.16
2018-03-25 07:30 | 118.83 | 103.76
2018-03-25 08:00 | 116.2 | 100.53
2018-03-25 08:30 | 116.74 | 100
2018-03-25 09:00 | 109.46 | 93.13
2018-03-25 09:30 | 109.26 | 92.84
2018-03-25 10:00 | 115.16 | 97.03
2018-03-25 10:30 | 116.42 | 99.35
2018-03-25 11:00 | 111.56 | 93.84
2018-03-25 11:30 | 120.93 | 103.57
2018-03-25 12:00 | 113.76 | 96.69
2018-03-25 12:30 | 120.41 | 103.99
2018-03-25 13:00 | 119.47 | 101.76
2018-03-25 13:30 | 116.27 | 98.56
2018-03-25 14:00 | 116.45 | 98.31
2018-03-25 14:30 | 121.58 | 102.81
2018-03-25 15:00 | 113.86 | 95.36
2018-03-25 15:30 | 109.37 | 91.08
2018-03-25 16:00 | 113.01 | 94.25
2018-03-25 16:30 | 117.68 | 100.42
2018-03-25 17:00 | 122.84 | 105.59
2018-03-25 17:30 | 120.84 | 104.42
2018-03-25 18:00 | 123.51 | 104.94
2018-03-25 18:30 | 116.33 | 95.39
2018-03-25 19:00 | 122.39 | 103.96
2018-03-25 19:30 | 122.84 | 103.84
2018-03-25 20:00 | 119.69 | 100.74
2018-03-25 20:30 | 120.22 | 100.92
2018-03-25 21:00 | 122.5 | 104.53
2018-03-25 21:30 | 120.34 | 101.81
2018-03-25 22:00 | 118.09 | 99.72
2018-03-25 22:30 | 117.87 | 99.81
2018-03-25 23:00 | 115 | 97.93
2018-03-25 23:30 | 111.81 | 94.86
2018-03-26 | 111.83 | 96.06
2018-03-26 00:30 | 115.46 | 100.94
2018-03-26 01:00 | 113.81 | 98.45
2018-03-26 01:30 | 109.61 | 93.51
2018-03-26 02:00 | 108.6 | 93.52
2018-03-26 02:30 | 105.42 | 89.63
2018-03-26 03:00 | 109.48 | 93.36
2018-03-26 03:30 | 109.69 | 93.73
2018-03-26 04:00 | 111 | 95.23
2018-03-26 04:30 | 114.18 | 97.68
2018-03-26 05:00 | 115.54 | 98.1
2018-03-26 05:30 | 119.39 | 102.88
2018-03-26 06:00 | 120.94 | 105.14
2018-03-26 06:30 | 107.21 | 89.04
2018-03-26 07:00 | 114.68 | 97.55
2018-03-26 07:30 | 113.85 | 96.24
2018-03-26 08:00 | 117.88 | 98.52
2018-03-26 08:30 | 115.47 | 95.84
2018-03-26 09:00 | 117.76 | 98.02
2018-03-26 09:30 | 121.65 | 101.45
2018-03-26 10:00 | 117.29 | 97.62
2018-03-26 10:30 | 112.64 | 91.02
2018-03-26 11:00 | 112.5 | 92.15
2018-03-26 11:30 | 123.88 | 105.11
2018-03-26 12:00 | 120.48 | 100.33
2018-03-26 12:30 | 129.31 | 109.45
2018-03-26 13:00 | 129.2 | 108.78
2018-03-26 13:30 | 136.77 | 117.02
2018-03-26 14:00 | 129.01 | 109.31
2018-03-26 14:30 | 119.82 | 100.11
2018-03-26 15:00 | 118.01 | 98.05
2018-03-26 15:30 | 116.92 | 96.63
2018-03-26 16:00 | 116.08 | 96.71
2018-03-26 16:30 | 125.28 | 106.6
2018-03-26 17:00 | 127.3 | 109.49
2018-03-26 17:30 | 121.2 | 103.73
2018-03-26 18:00 | 123.12 | 105.41
2018-03-26 18:30 | 115.38 | 95.73
2018-03-26 19:00 | 120.73 | 101.84
2018-03-26 19:30 | 119.95 | 100.54
2018-03-26 20:00 | 123.06 | 103.82
2018-03-26 20:30 | 119.09 | 99.68
2018-03-26 21:00 | 115.98 | 97.22
2018-03-26 21:30 | 117.82 | 100.37
2018-03-26 22:00 | 117.46 | 100.44
2018-03-26 22:30 | 117.65 | 101.42
2018-03-26 23:00 | 115.6 | 98.78
2018-03-26 23:30 | 111.99 | 95.14
2018-03-27 | 116.07 | 99.98
2018-03-27 00:30 | 109.97 | 93.56
2018-03-27 01:00 | 114.68 | 98.66
2018-03-27 01:30 | 116.92 | 100.54
2018-03-27 02:00 | 121.86 | 105.8
2018-03-27 02:30 | 120.67 | 104.51
2018-03-27 03:00 | 116.19 | 100.54
2018-03-27 03:30 | 116.29 | 100.48
2018-03-27 04:00 | 119.39 | 104.43
2018-03-27 04:30 | 119.36 | 103.99
2018-03-27 05:00 | 117.81 | 102.5
2018-03-27 05:30 | 117.91 | 102.56
2018-03-27 06:00 | 125.38 | 108.86
2018-03-27 06:30 | 108.99 | 90.4
2018-03-27 07:00 | 112.41 | 92.72
2018-03-27 07:30 | 113.61 | 92.81
2018-03-27 08:00 | 111.04 | 91.93
2018-03-27 08:30 | 106.93 | 89.17
2018-03-27 09:00 | 113.39 | 95.54
2018-03-27 09:30 | 119.95 | 100
2018-03-27 10:00 | 116.58 | 97
2018-03-27 10:30 | 118.38 | 98.81
2018-03-27 11:00 | 118.87 | 99.83
2018-03-27 11:30 | 125.18 | 105.26
2018-03-27 12:00 | 118.28 | 98.6
2018-03-27 12:30 | 112.21 | 94.01
2018-03-27 13:00 | 118.18 | 99.88
2018-03-27 13:30 | 119.12 | 101.14
2018-03-27 14:00 | 111.77 | 93.22
2018-03-27 14:30 | 118.03 | 100.35
2018-03-27 15:00 | 118.83 | 100.08
2018-03-27 15:30 | 112.63 | 92.26
2018-03-27 16:00 | 115.56 | 94.06
2018-03-27 16:30 | 114.51 | 94.67
2018-03-27 17:00 | 109.78 | 89.89
2018-03-27 17:30 | 111.88 | 92.07
2018-03-27 18:00 | 118.58 | 97.7
2018-03-27 18:30 | 114.93 | 91.4
2018-03-27 19:00 | 124.52 | 104.76
2018-03-27 19:30 | 129.71 | 109.75
2018-03-27 20:00 | 119.51 | 98.72
2018-03-27 20:30 | 126.13 | 106.51
2018-03-27 21:00 | 117.96 | 99.18
2018-03-27 21:30 | 125.58 | 107.82
2018-03-27 22:00 | 127.66 | 110.63
2018-03-27 22:30 | 126.95 | 110.67
2018-03-27 23:00 | 115.36 | 97.71
2018-03-27 23:30 | 118.72 | 101.74
2018-03-28 | 117.85 | 101.19
2018-03-28 00:30 | 124.25 | 106.26
2018-03-28 01:00 | 118.37 | 101.3
2018-03-28 01:30 | 115.26 | 97.74
2018-03-28 02:00 | 118.98 | 101.35
2018-03-28 02:30 | 119.66 | 102.12
2018-03-28 03:00 | 116.37 | 100.03
2018-03-28 03:30 | 114.44 | 96.8
2018-03-28 04:00 | 119 | 101.72
2018-03-28 04:30 | 120.29 | 104.02
2018-03-28 05:00 | 116.23 | 99.35
2018-03-28 05:30 | 112.16 | 94.72
2018-03-28 06:00 | 112.8 | 96.21
2018-03-28 06:30 | 99.43 | 82.96
2018-03-28 07:00 | 103.57 | 87.32
2018-03-28 07:30 | 109 | 93.2
2018-03-28 08:00 | 111.63 | 95.55
2018-03-28 08:30 | 107.97 | 91.44
2018-03-28 09:00 | 95.72 | 77.99
2018-03-28 09:30 | 101.97 | 84.99
2018-03-28 10:00 | 102.11 | 86.33
2018-03-28 10:30 | 100.43 | 84.11
2018-03-28 11:00 | 112 | 93.24
2018-03-28 11:30 | 109.74 | 90.12
2018-03-28 12:00 | 112.14 | 90.83
2018-03-28 12:30 | 115.28 | 95
2018-03-28 13:00 | 115.96 | 94.62
2018-03-28 13:30 | 114.29 | 91.45
2018-03-28 14:00 | 112.69 | 91.21
2018-03-28 14:30 | 109.86 | 89.74
2018-03-28 15:00 | 115.2 | 95.61
2018-03-28 15:30 | 115.35 | 95.2
2018-03-28 16:00 | 110.53 | 90.27
2018-03-28 16:30 | 109.14 | 88.84
2018-03-28 17:00 | 119.62 | 100.34
2018-03-28 17:30 | 116.18 | 96.12
2018-03-28 18:00 | 119.31 | 99.43
2018-03-28 18:30 | 114.62 | 94.11
2018-03-28 19:00 | 120.12 | 101.3
2018-03-28 19:30 | 123.91 | 106.16
2018-03-28 20:00 | 128.68 | 111.51
2018-03-28 20:30 | 126.33 | 107.96
2018-03-28 21:00 | 120.13 | 101.68
2018-03-28 21:30 | 114.72 | 96.34
2018-03-28 22:00 | 118 | 100.73
2018-03-28 22:30 | 113.59 | 97.87
2018-03-28 23:00 | 122.54 | 106.44
2018-03-28 23:30 | 122.75 | 106.42
2018-03-29 | 126.82 | 110.3
2018-03-29 00:30 | 119.91 | 102.81
2018-03-29 01:00 | 124.77 | 108.58
2018-03-29 01:30 | 122.85 | 106.49
2018-03-29 02:00 | 130.22 | 113.77
2018-03-29 02:30 | 125.96 | 109.49
2018-03-29 03:00 | 113.66 | 98.02
2018-03-29 03:30 | 108.66 | 92.55
2018-03-29 04:00 | 119.03 | 103.76
2018-03-29 04:30 | 117.02 | 101.68
2018-03-29 05:00 | 112.73 | 97.29
2018-03-29 05:30 | 109.2 | 94.51
2018-03-29 06:00 | 111.07 | 95.46
2018-03-29 06:30 | 102.43 | 84.86
2018-03-29 07:00 | 111.44 | 94.37
2018-03-29 07:30 | 108.57 | 90.02
2018-03-29 08:00 | 108.2 | 89.45
2018-03-29 08:30 | 109.07 | 91.91
2018-03-29 09:00 | 108.5 | 89.1
2018-03-29 09:30 | 111.15 | 91.04
2018-03-29 10:00 | 116.94 | 95.93
2018-03-29 10:30 | 115 | 92.89
2018-03-29 11:00 | 115.88 | 92.98
2018-03-29 11:30 | 120.64 | 98.79
2018-03-29 12:00 | 122.26 | 100.97
2018-03-29 12:30 | 121.18 | 101.28
2018-03-29 13:00 | 125.61 | 106.26
2018-03-29 13:30 | 127.11 | 106.93
2018-03-29 14:00 | 133.03 | 113.29
2018-03-29 14:30 | 134.12 | 113.83
2018-03-29 15:00 | 125.36 | 104.94
2018-03-29 15:30 | 125.93 | 104.27
2018-03-29 16:00 | 122.55 | 100.53
2018-03-29 16:30 | 123.91 | 102.53
2018-03-29 17:00 | 127.4 | 107.94
2018-03-29 17:30 | 131.32 | 112.29
2018-03-29 18:00 | 138.57 | 119.89
2018-03-29 18:30 | 126.91 | 107.85
2018-03-29 19:00 | 127.44 | 109.2
2018-03-29 19:30 | 134.98 | 115.93
2018-03-29 20:00 | 131.89 | 111.78
2018-03-29 20:30 | 129.61 | 109.65
2018-03-29 21:00 | 128.56 | 109.3
2018-03-29 21:30 | 125.87 | 106.37
2018-03-29 22:00 | 127.76 | 108.1
2018-03-29 22:30 | 124.73 | 105.92
2018-03-29 23:00 | 126.97 | 108.12
2018-03-29 23:30 | 125.81 | 106.69
2018-03-30 | 119.31 | 101.14
2018-03-30 00:30 | 129.42 | 112.24
2018-03-30 01:00 | 131.92 | 113.82
2018-03-30 01:30 | 134.01 | 114.69
2018-03-30 02:00 | 133.24 | 114.87
2018-03-30 02:30 | 129.04 | 111.51
2018-03-30 03:00 | 131.15 | 112.9
2018-03-30 03:30 | 125.29 | 106.71
2018-03-30 04:00 | 130.81 | 112.59
2018-03-30 04:30 | 120.61 | 102.98
2018-03-30 05:00 | 121.68 | 103.34
2018-03-30 05:30 | 123.82 | 106.46
2018-03-30 06:00 | 123.14 | 106.43
2018-03-30 06:30 | 115.67 | 98.52
2018-03-30 07:00 | 108.62 | 93.06
2018-03-30 07:30 | 118.28 | 102.42
2018-03-30 08:00 | 123.45 | 107.4
2018-03-30 08:30 | 127.36 | 110.44
2018-03-30 09:00 | 125.18 | 107.8
2018-03-30 09:30 | 116.96 | 98.1
2018-03-30 10:00 | 120.81 | 100.44
2018-03-30 10:30 | 122.71 | 102.78
2018-03-30 11:00 | 119.69 | 101.97
2018-03-30 11:30 | 116 | 97.76
2018-03-30 12:00 | 125.08 | 106.76
2018-03-30 12:30 | 126.45 | 108.87
2018-03-30 13:00 | 124.71 | 107.07
2018-03-30 13:30 | 127.41 | 109.11
2018-03-30 14:00 | 132.16 | 111.83
2018-03-30 14:30 | 131.67 | 111.14
2018-03-30 15:00 | 124.98 | 106.35
2018-03-30 15:30 | 116.92 | 97.92
2018-03-30 16:00 | 127.86 | 108.22
2018-03-30 16:30 | 121.76 | 101.57
2018-03-30 17:00 | 124.97 | 103.75
2018-03-30 17:30 | 127.34 | 106.73
2018-03-30 18:00 | 128.96 | 108.86
2018-03-30 18:30 | 117.65 | 96.2
2018-03-30 19:00 | 123.66 | 102.71
2018-03-30 19:30 | 124.25 | 103.7
2018-03-30 20:00 | 127.74 | 107.06
2018-03-30 20:30 | 126.28 | 107.05
2018-03-30 21:00 | 132.01 | 113.3
2018-03-30 21:30 | 123.73 | 105.38
2018-03-30 22:00 | 129.37 | 111.19
2018-03-30 22:30 | 129.27 | 111.39
2018-03-30 23:00 | 123.81 | 105.61
2018-03-30 23:30 | 118 | 100.09
2018-03-31 | 121.36 | 104.57
2018-03-31 00:30 | 118.16 | 100.86
2018-03-31 01:00 | 115.19 | 98.11
2018-03-31 01:30 | 118.08 | 101.41
2018-03-31 02:00 | 122.28 | 105.38
2018-03-31 02:30 | 122.14 | 105.54
2018-03-31 03:00 | 118.72 | 101.54
2018-03-31 03:30 | 111.23 | 94.06
2018-03-31 04:00 | 120.57 | 104.16
2018-03-31 04:30 | 116.51 | 99.59
2018-03-31 05:00 | 122.7 | 105.53
2018-03-31 05:30 | 122.83 | 106.04
2018-03-31 06:00 | 120.99 | 105.51
2018-03-31 06:30 | 118.94 | 102.74
2018-03-31 07:00 | 117.51 | 101.74
2018-03-31 07:30 | 121.99 | 105.62
2018-03-31 08:00 | 123.09 | 105.96
2018-03-31 08:30 | 113.61 | 95.1
2018-03-31 09:00 | 108.71 | 90.17
2018-03-31 09:30 | 108.02 | 89.84
2018-03-31 10:00 | 114.95 | 97.6
2018-03-31 10:30 | 114.3 | 96.7
2018-03-31 11:00 | 117.03 | 99.54
2018-03-31 11:30 | 113.39 | 95.54
2018-03-31 12:00 | 113.22 | 96.89
2018-03-31 12:30 | 122.37 | 105.2
2018-03-31 13:00 | 113.63 | 92.86
2018-03-31 13:30 | 119.03 | 98.74
2018-03-31 14:00 | 121.2 | 101.08
2018-03-31 14:30 | 118.25 | 98.18
2018-03-31 15:00 | 123.39 | 103.74
2018-03-31 15:30 | 120.83 | 102.04
2018-03-31 16:00 | 124.16 | 104.65
2018-03-31 16:30 | 126.76 | 107.64
2018-03-31 17:00 | 128.42 | 108.59
2018-03-31 17:30 | 128.79 | 108.45
2018-03-31 18:00 | 129.07 | 109.2
2018-03-31 18:30 | 125.65 | 104.51
2018-03-31 19:00 | 133.19 | 113.4
2018-03-31 19:30 | 130.2 | 110.68
2018-03-31 20:00 | 127.75 | 108.48
2018-03-31 20:30 | 124.06 | 104.9
2018-03-31 21:00 | 121.08 | 101.78
2018-03-31 21:30 | 121.71 | 103.41
2018-03-31 22:00 | 122.91 | 103.7
2018-03-31 22:30 | 124.26 | 106.97
2018-03-31 23:00 | 122.95 | 105.25
2018-03-31 23:30 | 118.96 | 100.95
2018-04-01 | 120.32 | 102.18
2018-04-01 00:30 | 117.13 | 98.86
2018-04-01 01:00 | 115.42 | 98.53
2018-04-01 01:30 | 115.46 | 97.68
2018-04-01 02:00 | 114.83 | 97.54
2018-04-01 02:30 | 116.79 | 98.54
2018-04-01 03:00 | 121.16 | 102.78
2018-04-01 03:30 | 118.37 | 99.63
2018-04-01 04:00 | 117.15 | 99.1
2018-04-01 04:30 | 113.7 | 94.95
2018-04-01 05:00 | 121.69 | 103.51
2018-04-01 05:30 | 121.49 | 102.58
2018-04-01 06:00 | 122.28 | 103.17
2018-04-01 06:30 | 113.66 | 94.3
2018-04-01 07:00 | 106.87 | 90.92
2018-04-01 07:30 | 111.23 | 94.89
2018-04-01 08:00 | 106.71 | 90.25
2018-04-01 08:30 | 110.97 | 93.88
2018-04-01 09:00 | 115.06 | 98.21
2018-04-01 09:30 | 110.42 | 94.82
2018-04-01 10:00 | 113.03 | 97.44
2018-04-01 10:30 | 116.3 | 99.72
2018-04-01 11:00 | 111.98 | 93.54
2018-04-01 11:30 | 119.65 | 100.17
2018-04-01 12:00 | 123.4 | 104.29
2018-04-01 12:30 | 123.19 | 104.37
2018-04-01 13:00 | 123.5 | 103.31
2018-04-01 13:30 | 127.07 | 106.67
2018-04-01 14:00 | 127.84 | 107.85
2018-04-01 14:30 | 122.61 | 102.4
2018-04-01 15:00 | 126.59 | 106
2018-04-01 15:30 | 120.14 | 99.18
2018-04-01 16:00 | 124.05 | 103.84
2018-04-01 16:30 | 124.8 | 105.01
2018-04-01 17:00 | 130.17 | 111.19
2018-04-01 17:30 | 121.66 | 101.55
2018-04-01 18:00 | 133.86 | 114.88
2018-04-01 18:30 | 126.98 | 107.52
2018-04-01 19:00 | 123.44 | 104.49
2018-04-01 19:30 | 128.05 | 108.5
2018-04-01 20:00 | 136.4 | 118.47
2018-04-01 20:30 | 129.06 | 112.29
2018-04-01 21:00 | 121.03 | 104.61
2018-04-01 21:30 | 127.97 | 110.61
2018-04-01 22:00 | 129.44 | 113.29
2018-04-01 22:30 | 126.76 | 110.65
2018-04-01 23:00 | 122.95 | 106.46
2018-04-01 23:30 | 118.35 | 101.9
2018-04-02 | 112.52 | 97.25
2018-04-02 00:30 | 104.52 | 89.55
2018-04-02 01:00 | 108.52 | 93.84
2018-04-02 01:30 | 110.67 | 96.14
2018-04-02 02:00 | 113 | 98.79
2018-04-02 02:30 | 118.25 | 103.17
2018-04-02 03:00 | 111.72 | 97.19
2018-04-02 03:30 | 117.02 | 103.06
2018-04-02 04:00 | 112.54 | 99.64
2018-04-02 04:30 | 115.26 | 100.74
2018-04-02 05:00 | 110.76 | 97.14
2018-04-02 05:30 | 120.21 | 104.85
2018-04-02 06:00 | 113.49 | 97.81
2018-04-02 06:30 | 110.74 | 94.05
2018-04-02 07:00 | 107.87 | 92.13
2018-04-02 07:30 | 118.84 | 102.72
2018-04-02 08:00 | 113.02 | 96.3
2018-04-02 08:30 | 111.02 | 92.47
2018-04-02 09:00 | 109.58 | 91.22
2018-04-02 09:30 | 111.6 | 93.78
2018-04-02 10:00 | 111.36 | 93.03
2018-04-02 10:30 | 114.27 | 95.8
2018-04-02 11:00 | 113.14 | 95.02
2018-04-02 11:30 | 120.36 | 103.59
2018-04-02 12:00 | 119.18 | 102.22
2018-04-02 12:30 | 120.92 | 103.81
2018-04-02 13:00 | 128 | 111.77
2018-04-02 13:30 | 122.89 | 106.45
2018-04-02 14:00 | 124.52 | 108.13
2018-04-02 14:30 | 124.25 | 107.68
2018-04-02 15:00 | 124.83 | 107.52
2018-04-02 15:30 | 122.49 | 105.04
2018-04-02 16:00 | 122.5 | 104.92
2018-04-02 16:30 | 121.91 | 104.03
2018-04-02 17:00 | 124.91 | 105.67
2018-04-02 17:30 | 133.22 | 114.74
2018-04-02 18:00 | 123.72 | 103.64
2018-04-02 18:30 | 116.46 | 94.74
2018-04-02 19:00 | 122.64 | 102.38
2018-04-02 19:30 | 129.44 | 110.26
2018-04-02 20:00 | 133.15 | 113.98
2018-04-02 20:30 | 134.05 | 115.06
2018-04-02 21:00 | 132.14 | 113.88
2018-04-02 21:30 | 126.16 | 109.85
2018-04-02 22:00 | 125.81 | 108.39
2018-04-02 22:30 | 120.72 | 103.75
2018-04-02 23:00 | 127.65 | 110.8
2018-04-02 23:30 | 116.81 | 99.85
2018-04-03 | 119.65 | 103.29
2018-04-03 00:30 | 120.65 | 104.29
2018-04-03 01:00 | 113.51 | 96.95
2018-04-03 01:30 | 111.24 | 94.38
2018-04-03 02:00 | 110.6 | 94.92
2018-04-03 02:30 | 118.21 | 103.1
2018-04-03 03:00 | 109.31 | 93.66
2018-04-03 03:30 | 108.01 | 91.34
2018-04-03 04:00 | 107.98 | 92.6
2018-04-03 04:30 | 110.86 | 95.3
2018-04-03 05:00 | 104.54 | 88.7
2018-04-03 05:30 | 108.31 | 92.47
2018-04-03 06:00 | 109.47 | 93.11
2018-04-03 06:30 | 96.84 | 78
2018-04-03 07:00 | 105 | 88.43
2018-04-03 07:30 | 114.36 | 97.89
2018-04-03 08:00 | 116.98 | 99.92
2018-04-03 08:30 | 121.99 | 104.44
2018-04-03 09:00 | 124.67 | 105.7
2018-04-03 09:30 | 120.9 | 100.59
2018-04-03 10:00 | 117.68 | 97.7
2018-04-03 10:30 | 120.73 | 100.42
2018-04-03 11:00 | 114.8 | 96.32
2018-04-03 11:30 | 111.81 | 92.18
2018-04-03 12:00 | 115.41 | 96.77
2018-04-03 12:30 | 111.92 | 93.33
2018-04-03 13:00 | 108.02 | 91.05
2018-04-03 13:30 | 112.05 | 95.62
2018-04-03 14:00 | 120.96 | 105.18
2018-04-03 14:30 | 123.45 | 106.29
2018-04-03 15:00 | 119.39 | 103.74
2018-04-03 15:30 | 122.5 | 106.59
2018-04-03 16:00 | 124.83 | 108.49
2018-04-03 16:30 | 131.15 | 114.69
2018-04-03 17:00 | 128.03 | 110.28
2018-04-03 17:30 | 129.08 | 111.69
2018-04-03 18:00 | 125.48 | 109.42
2018-04-03 18:30 | 120.79 | 103.35
2018-04-03 19:00 | 123.99 | 106.03
2018-04-03 19:30 | 128.81 | 112.04
2018-04-03 20:00 | 132.56 | 115.18
2018-04-03 20:30 | 129.59 | 112.8
2018-04-03 21:00 | 120.98 | 104.78
2018-04-03 21:30 | 121.24 | 104.24
2018-04-03 22:00 | 114.09 | 97.97
2018-04-03 22:30 | 111.37 | 95.06
2018-04-03 23:00 | 113.85 | 97.45
2018-04-03 23:30 | 114.43 | 98.41
2018-04-04 | 116.25 | 100.92
2018-04-04 00:30 | 116.14 | 100.54
2018-04-04 01:00 | 113.88 | 98.1
2018-04-04 01:30 | 110 | 94.48
2018-04-04 02:00 | 119.15 | 104.08
2018-04-04 02:30 | 116.86 | 100.4
2018-04-04 03:00 | 113.44 | 96.23
2018-04-04 03:30 | 115.67 | 99.03
2018-04-04 04:00 | 110.99 | 94.62
2018-04-04 04:30 | 105.7 | 89.41
2018-04-04 05:00 | 108.97 | 93.7
2018-04-04 05:30 | 104.31 | 89.08
2018-04-04 06:00 | 104.43 | 88.51
2018-04-04 06:30 | 95.86 | 78.9
2018-04-04 07:00 | 102.1 | 87.44
2018-04-04 07:30 | 97 | 82.28
2018-04-04 08:00 | 92.29 | 77.01
2018-04-04 08:30 | 90.34 | 74.61
2018-04-04 09:00 | 89.67 | 73.91
2018-04-04 09:30 | 93.91 | 77.79
2018-04-04 10:00 | 96.1 | 81.32
2018-04-04 10:30 | 98.52 | 83.64
2018-04-04 11:00 | 92.39 | 75.97
2018-04-04 11:30 | 92.5 | 74.74
2018-04-04 12:00 | 83.07 | 65.69
2018-04-04 12:30 | 89.39 | 72.09
2018-04-04 13:00 | 98.28 | 80.89
2018-04-04 13:30 | 98.93 | 82.02
2018-04-04 14:00 | 92.08 | 75.91
2018-04-04 14:30 | 96.18 | 80.03
2018-04-04 15:00 | 100.51 | 83.29
2018-04-04 15:30 | 103.48 | 86.6
2018-04-04 16:00 | 100.81 | 84.46
2018-04-04 16:30 | 99.91 | 84.04
2018-04-04 17:00 | 98.06 | 82.67
2018-04-04 17:30 | 96.6 | 81.7
2018-04-04 18:00 | 98.65 | 83.8
2018-04-04 18:30 | 99.44 | 83.58
2018-04-04 19:00 | 100.18 | 84.86
2018-04-04 19:30 | 104.94 | 89.91
2018-04-04 20:00 | 103.2 | 87.94
2018-04-04 20:30 | 105.63 | 89.85
2018-04-04 21:00 | 104.7 | 90.04
2018-04-04 21:30 | 111.06 | 93.74
2018-04-04 22:00 | 114.14 | 97.42
2018-04-04 22:30 | 111.91 | 95.57
2018-04-04 23:00 | 116.69 | 99.45
2018-04-04 23:30 | 114.84 | 98.24
2018-04-05 | 118.14 | 102.26
2018-04-05 00:30 | 120.88 | 105.53
2018-04-05 01:00 | 119.02 | 103.32
2018-04-05 01:30 | 119.95 | 103.67
2018-04-05 02:00 | 116.98 | 100.23
2018-04-05 02:30 | 113.15 | 96.28
2018-04-05 03:00 | 112.77 | 96.41
2018-04-05 03:30 | 115.87 | 100.32
2018-04-05 04:00 | 120.13 | 104.39
2018-04-05 04:30 | 114.21 | 98.74
2018-04-05 05:00 | 108.85 | 93.06
2018-04-05 05:30 | 111.62 | 96.68
2018-04-05 06:00 | 110.65 | 95.67
2018-04-05 06:30 | 102.79 | 83.47
2018-04-05 07:00 | 111.79 | 92.06
2018-04-05 07:30 | 112.46 | 92.05
2018-04-05 08:00 | 119.54 | 98.55
2018-04-05 08:30 | 114.48 | 94.71
2018-04-05 09:00 | 113.73 | 93.42
2018-04-05 09:30 | 115.52 | 94.41
2018-04-05 10:00 | 118.76 | 98
2018-04-05 10:30 | 109.96 | 88.89
2018-04-05 11:00 | 122.96 | 100.71
2018-04-05 11:30 | 120.81 | 99.06
2018-04-05 12:00 | 106.46 | 83.91
2018-04-05 12:30 | 116.46 | 94.28
2018-04-05 13:00 | 124.04 | 103.26
2018-04-05 13:30 | 122.92 | 102.97
2018-04-05 14:00 | 134.02 | 113.8
2018-04-05 14:30 | 132.69 | 111.19
2018-04-05 15:00 | 128.07 | 104.48
2018-04-05 15:30 | 123.02 | 100.8
2018-04-05 16:00 | 119.72 | 98.3
2018-04-05 16:30 | 117.67 | 96.99
2018-04-05 17:00 | 115.93 | 94.47
2018-04-05 17:30 | 111.87 | 89.39
2018-04-05 18:00 | 117.53 | 95.12
2018-04-05 18:30 | 111.61 | 89.46
2018-04-05 19:00 | 118.15 | 97.48
2018-04-05 19:30 | 126.06 | 105.67
2018-04-05 20:00 | 127.98 | 107.52
2018-04-05 20:30 | 128.64 | 108.39
2018-04-05 21:00 | 129.27 | 108.58
2018-04-05 21:30 | 131.98 | 111.75
2018-04-05 22:00 | 131.12 | 111.05
2018-04-05 22:30 | 125.3 | 105.56
2018-04-05 23:00 | 123.52 | 104.09
2018-04-05 23:30 | 119.94 | 100.74
2018-04-06 | 123.34 | 104.58
2018-04-06 00:30 | 130.03 | 109.83
2018-04-06 01:00 | 136.37 | 116.98
2018-04-06 01:30 | 126.28 | 107.15
2018-04-06 02:00 | 125.69 | 104.5
2018-04-06 02:30 | 123.81 | 103.33
2018-04-06 03:00 | 127.01 | 107.24
2018-04-06 03:30 | 127.78 | 106.71
2018-04-06 04:00 | 121.96 | 100.94
2018-04-06 04:30 | 126.61 | 106.7
2018-04-06 05:00 | 125.06 | 105.88
2018-04-06 05:30 | 125.18 | 107.32
2018-04-06 06:00 | 125.77 | 107.4
2018-04-06 06:30 | 121.34 | 100.62
2018-04-06 07:00 | 129.13 | 109.29
2018-04-06 07:30 | 132.28 | 111.71
2018-04-06 08:00 | 129.2 | 107.69
2018-04-06 08:30 | 122.7 | 99.51
2018-04-06 09:00 | 123.76 | 99.61
2018-04-06 09:30 | 120.62 | 95.9
2018-04-06 10:00 | 123.96 | 98.72
2018-04-06 10:30 | 136.91 | 113.63
2018-04-06 11:00 | 132.7 | 107.81
2018-04-06 11:30 | 124.42 | 97.82
2018-04-06 12:00 | 131.57 | 105.17
2018-04-06 12:30 | 127.06 | 100.53
2018-04-06 13:00 | 125.25 | 99.43
2018-04-06 13:30 | 125.36 | 99.58
2018-04-06 14:00 | 131.13 | 106.51
2018-04-06 14:30 | 131.72 | 104.99
2018-04-06 15:00 | 134.18 | 106.54
2018-04-06 15:30 | 140.78 | 114.52
2018-04-06 16:00 | 135.18 | 108.46
2018-04-06 16:30 | 135.77 | 110.45
2018-04-06 17:00 | 134.4 | 108.74
2018-04-06 17:30 | 134.36 | 109.11
2018-04-06 18:00 | 138.4 | 114.01
2018-04-06 18:30 | 125.44 | 101.28
2018-04-06 19:00 | 129.22 | 105.48
2018-04-06 19:30 | 135.22 | 112.04
2018-04-06 20:00 | 123.42 | 100.21
2018-04-06 20:30 | 128.37 | 106.4
2018-04-06 21:00 | 127.48 | 104.24
2018-04-06 21:30 | 126.26 | 102.34
2018-04-06 22:00 | 124.1 | 102.25
2018-04-06 22:30 | 118.92 | 98.17
2018-04-06 23:00 | 123.61 | 101.49
2018-04-06 23:30 | 123.35 | 101.28
2018-04-07 | 127.06 | 106.08
2018-04-07 00:30 | 123.73 | 101.44
2018-04-07 01:00 | 130.9 | 109.32
2018-04-07 01:30 | 129.69 | 108.42
2018-04-07 02:00 | 134.2 | 113.26
2018-04-07 02:30 | 128.85 | 106.77
2018-04-07 03:00 | 128.88 | 108.84
2018-04-07 03:30 | 129.45 | 108.31
2018-04-07 04:00 | 128.59 | 107.28
2018-04-07 04:30 | 128.17 | 107.41
2018-04-07 05:00 | 128.02 | 107.12
2018-04-07 05:30 | 132.77 | 112.25
2018-04-07 06:00 | 130.39 | 109.91
2018-04-07 06:30 | 121.99 | 101.12
2018-04-07 07:00 | 122.58 | 102.69
2018-04-07 07:30 | 119.46 | 99.43
2018-04-07 08:00 | 122.95 | 103.12
2018-04-07 08:30 | 135.73 | 116.29
2018-04-07 09:00 | 127.25 | 107.77
2018-04-07 09:30 | 134.87 | 115.92
2018-04-07 10:00 | 146.18 | 126.94
2018-04-07 10:30 | 140.99 | 120.6
2018-04-07 11:00 | 129.32 | 108.54
2018-04-07 11:30 | 133.13 | 112.46
2018-04-07 12:00 | 141.79 | 121.05
2018-04-07 12:30 | 130.41 | 108.77
2018-04-07 13:00 | 128.81 | 107.78
2018-04-07 13:30 | 131.3 | 110.15
2018-04-07 14:00 | 127.39 | 105.97
2018-04-07 14:30 | 134.79 | 113.82
2018-04-07 15:00 | 127.25 | 105.75
2018-04-07 15:30 | 125.53 | 103.95
2018-04-07 16:00 | 119.11 | 99.75
2018-04-07 16:30 | 112.02 | 93.28
2018-04-07 17:00 | 124.65 | 105.03
2018-04-07 17:30 | 133.3 | 113.21
2018-04-07 18:00 | 135.67 | 116.06
2018-04-07 18:30 | 127.51 | 106.24
2018-04-07 19:00 | 130.21 | 109.8
2018-04-07 19:30 | 132.66 | 113.28
2018-04-07 20:00 | 132.63 | 112.59
2018-04-07 20:30 | 131.14 | 114.1
2018-04-07 21:00 | 129.98 | 112.91
2018-04-07 21:30 | 119.65 | 100.88
2018-04-07 22:00 | 115.02 | 96.38
2018-04-07 22:30 | 123.7 | 106.21
2018-04-07 23:00 | 126.25 | 109.07
2018-04-07 23:30 | 124.92 | 107.79
2018-04-08 | 115.91 | 98.85
2018-04-08 00:30 | 121.21 | 104.91
2018-04-08 01:00 | 122.84 | 106.43
2018-04-08 01:30 | 122.99 | 107.67
2018-04-08 02:00 | 124.44 | 108.93
2018-04-08 02:30 | 112.3 | 95.71
2018-04-08 03:00 | 118.29 | 102.12
2018-04-08 03:30 | 111.87 | 95.06
2018-04-08 04:00 | 118.31 | 102
2018-04-08 04:30 | 115.19 | 97.49
2018-04-08 05:00 | 116.83 | 100.74
2018-04-08 05:30 | 120.46 | 105.54
2018-04-08 06:00 | 117.81 | 101.31
2018-04-08 06:30 | 109 | 92.39
2018-04-08 07:00 | 115.03 | 100.47
2018-04-08 07:30 | 115.59 | 99.53
2018-04-08 08:00 | 119.05 | 102.14
2018-04-08 08:30 | 125.52 | 108.22
2018-04-08 09:00 | 126.9 | 110.6
2018-04-08 09:30 | 127.1 | 111.46
2018-04-08 10:00 | 129.23 | 111.66
2018-04-08 10:30 | 124.44 | 107.18
2018-04-08 11:00 | 124.03 | 106.2
2018-04-08 11:30 | 118.05 | 101.12
2018-04-08 12:00 | 121.49 | 105.05
2018-04-08 12:30 | 118.86 | 101.28
2018-04-08 13:00 | 124.09 | 105.34
2018-04-08 13:30 | 114.94 | 94.62
2018-04-08 14:00 | 128.61 | 108.69
2018-04-08 14:30 | 121.13 | 101.45
2018-04-08 15:00 | 122.11 | 103.71
2018-04-08 15:30 | 122.84 | 104.75
2018-04-08 16:00 | 136.49 | 119.25
2018-04-08 16:30 | 135.21 | 117.83
2018-04-08 17:00 | 119.23 | 101.39
2018-04-08 17:30 | 123.19 | 106.71
2018-04-08 18:00 | 123.5 | 107.49
2018-04-08 18:30 | 112.83 | 95.61
2018-04-08 19:00 | 125.66 | 109.79
2018-04-08 19:30 | 128.91 | 112.65
2018-04-08 20:00 | 122.47 | 105.06
2018-04-08 20:30 | 121.81 | 103.23
2018-04-08 21:00 | 115.46 | 97.65
2018-04-08 21:30 | 118.38 | 101.23
2018-04-08 22:00 | 124.23 | 108.05
2018-04-08 22:30 | 121.94 | 105.01
2018-04-08 23:00 | 118.97 | 101.25
2018-04-08 23:30 | 126.52 | 110.58
2018-04-09 | 125.53 | 108.07
2018-04-09 00:30 | 128.02 | 111.01
2018-04-09 01:00 | 130.67 | 114.47
2018-04-09 01:30 | 117.72 | 101.7
2018-04-09 02:00 | 119.5 | 103.23
2018-04-09 02:30 | 116.22 | 99.18
2018-04-09 03:00 | 116.24 | 99.06
2018-04-09 03:30 | 111.81 | 93.88
2018-04-09 04:00 | 118.04 | 100.83
2018-04-09 04:30 | 116.48 | 98.86
2018-04-09 05:00 | 121.54 | 104.35
2018-04-09 05:30 | 113.02 | 96.19
2018-04-09 06:00 | 114.27 | 97.19
2018-04-09 06:30 | 104.54 | 85.62
2018-04-09 07:00 | 114.24 | 98.13
2018-04-09 07:30 | 123.24 | 106.82
2018-04-09 08:00 | 123.39 | 106.41
2018-04-09 08:30 | 123.46 | 105.14
2018-04-09 09:00 | 132.55 | 112.12
2018-04-09 09:30 | 122.86 | 102.2
2018-04-09 10:00 | 123.23 | 102.6
2018-04-09 10:30 | 123.35 | 102.68
2018-04-09 11:00 | 125.47 | 105.44
2018-04-09 11:30 | 123.14 | 102.7
2018-04-09 12:00 | 128.32 | 106.15
2018-04-09 12:30 | 129.53 | 107.46
2018-04-09 13:00 | 127.34 | 106.51
2018-04-09 13:30 | 127.34 | 106.46
2018-04-09 14:00 | 128.55 | 106.93
2018-04-09 14:30 | 133.63 | 112.27
2018-04-09 15:00 | 131.45 | 110.57
2018-04-09 15:30 | 134.36 | 112.77
2018-04-09 16:00 | 125.93 | 104.75
2018-04-09 16:30 | 132.27 | 111.42
2018-04-09 17:00 | 125.26 | 104.33
2018-04-09 17:30 | 119.7 | 98.89
2018-04-09 18:00 | 123.69 | 104.38
2018-04-09 18:30 | 118.84 | 97.92
2018-04-09 19:00 | 125.83 | 105
2018-04-09 19:30 | 131.87 | 113.06
2018-04-09 20:00 | 129.89 | 109.81
2018-04-09 20:30 | 135.88 | 116.42
2018-04-09 21:00 | 133.85 | 113.31
2018-04-09 21:30 | 129.03 | 110.56
2018-04-09 22:00 | 129.46 | 111.86
2018-04-09 22:30 | 119.12 | 101.56
2018-04-09 23:00 | 122.55 | 103.62
2018-04-09 23:30 | 124.68 | 106.07
2018-04-10 | 123.06 | 104.18
2018-04-10 00:30 | 124.23 | 104.82
2018-04-10 01:00 | 122.13 | 102.78
2018-04-10 01:30 | 116.47 | 97.76
2018-04-10 02:00 | 114.44 | 95.56
2018-04-10 02:30 | 112.47 | 95.39
2018-04-10 03:00 | 112.59 | 95.12
2018-04-10 03:30 | 112.82 | 95.62
2018-04-10 04:00 | 110.64 | 93.35
2018-04-10 04:30 | 111 | 94.62
2018-04-10 05:00 | 107.43 | 91.07
2018-04-10 05:30 | 102.76 | 85.18
2018-04-10 06:00 | 111.33 | 94.3
2018-04-10 06:30 | 109.39 | 90.57
2018-04-10 07:00 | 105.93 | 87.9
2018-04-10 07:30 | 105.86 | 88.85
2018-04-10 08:00 | 105.16 | 87.55
2018-04-10 08:30 | 104.98 | 87.5
2018-04-10 09:00 | 114.71 | 97.4
2018-04-10 09:30 | 111.42 | 93.31
2018-04-10 10:00 | 111.81 | 92.96
2018-04-10 10:30 | 117.61 | 99.62
2018-04-10 11:00 | 116.22 | 98.55
2018-04-10 11:30 | 110.46 | 92.75
2018-04-10 12:00 | 116.09 | 98.42
2018-04-10 12:30 | 125.57 | 109.43
2018-04-10 13:00 | 123.27 | 105.47
2018-04-10 13:30 | 115.28 | 97.96
2018-04-10 14:00 | 111.9 | 94.59
2018-04-10 14:30 | 114.94 | 96.92
2018-04-10 15:00 | 114.6 | 96.95
2018-04-10 15:30 | 115.75 | 97.24
2018-04-10 16:00 | 121.54 | 104.32
2018-04-10 16:30 | 125.31 | 107.1
2018-04-10 17:00 | 118.9 | 99.38
2018-04-10 17:30 | 123.9 | 103.98
2018-04-10 18:00 | 121.4 | 101.81
2018-04-10 18:30 | 117.67 | 98.04
2018-04-10 19:00 | 126.95 | 108.11
2018-04-10 19:30 | 126.51 | 107.78
2018-04-10 20:00 | 121.99 | 103.32
2018-04-10 20:30 | 119.77 | 102.05
2018-04-10 21:00 | 121.51 | 103.87
2018-04-10 21:30 | 126.3 | 108.66
2018-04-10 22:00 | 114.71 | 96.38
2018-04-10 22:30 | 116.02 | 98.22
2018-04-10 23:00 | 116.17 | 97.75
2018-04-10 23:30 | 109.67 | 90.19
2018-04-11 | 108.69 | 88.85
2018-04-11 00:30 | 109.77 | 91.62
2018-04-11 01:00 | 108.44 | 91.86
2018-04-11 01:30 | 102.19 | 86.53
2018-04-11 02:00 | 106.11 | 91.45
2018-04-11 02:30 | 116.53 | 101.77
2018-04-11 03:00 | 105.55 | 89.81
2018-04-11 03:30 | 114.34 | 97.73
2018-04-11 04:00 | 105.24 | 89.08
2018-04-11 04:30 | 98.89 | 83.16
2018-04-11 05:00 | 101.13 | 84.7
2018-04-11 05:30 | 104 | 87.61
2018-04-11 06:00 | 98.42 | 81.21
2018-04-11 06:30 | 90.51 | 73.06
2018-04-11 07:00 | 90.64 | 72.9
2018-04-11 07:30 | 99.3 | 81.91
2018-04-11 08:00 | 99.54 | 81.72
2018-04-11 08:30 | 98.33 | 80.68
2018-04-11 09:00 | 99.23 | 81.84
2018-04-11 09:30 | 99.02 | 81.66
2018-04-11 10:00 | 103.13 | 85.7
2018-04-11 10:30 | 100.23 | 82.55
2018-04-11 11:00 | 99.4 | 81.34
2018-04-11 11:30 | 100.48 | 82.45
2018-04-11 12:00 | 101.84 | 85.02
2018-04-11 12:30 | 103.91 | 87.82
2018-04-11 13:00 | 107.6 | 90.73
2018-04-11 13:30 | 104.19 | 86.78
2018-04-11 14:00 | 103.79 | 87.03
2018-04-11 14:30 | 109.27 | 92.12
2018-04-11 15:00 | 99.48 | 82.16
2018-04-11 15:30 | 105.39 | 87.71
2018-04-11 16:00 | 102.19 | 83.89
2018-04-11 16:30 | 98.3 | 80.7
2018-04-11 17:00 | 103.17 | 85.73
2018-04-11 17:30 | 107.23 | 90.31
2018-04-11 18:00 | 107.88 | 90.94
2018-04-11 18:30 | 97.79 | 81.17
2018-04-11 19:00 | 97.7 | 81.23
2018-04-11 19:30 | 112.46 | 96.44
2018-04-11 20:00 | 106.73 | 90.01
2018-04-11 20:30 | 108.95 | 92.27
2018-04-11 21:00 | 113.07 | 96.77
2018-04-11 21:30 | 116.19 | 99.21
2018-04-11 22:00 | 113.59 | 95.8
2018-04-11 22:30 | 108.41 | 91.63
2018-04-11 23:00 | 114.52 | 97.1
2018-04-11 23:30 | 108.3 | 91.14
2018-04-12 | 105.29 | 88.41
2018-04-12 00:30 | 112.53 | 97.28
2018-04-12 01:00 | 113.59 | 98.01
2018-04-12 01:30 | 104.8 | 88.21
2018-04-12 02:00 | 111.83 | 95.27
2018-04-12 02:30 | 102.95 | 85.25
2018-04-12 03:00 | 101.99 | 83.07
2018-04-12 03:30 | 105.96 | 86.52
2018-04-12 04:00 | 108.87 | 91.58
2018-04-12 04:30 | 109.67 | 93.53
2018-04-12 05:00 | 114.69 | 99.03
2018-04-12 05:30 | 110.98 | 96.75
2018-04-12 06:00 | 110.87 | 95.64
2018-04-12 06:30 | 103.6 | 88.65
2018-04-12 07:00 | 106.02 | 90.54
2018-04-12 07:30 | 102.52 | 86.59
2018-04-12 08:00 | 102 | 85.56
2018-04-12 08:30 | 100.5 | 82.68
2018-04-12 09:00 | 97.76 | 78.93
2018-04-12 09:30 | 96.82 | 78.75
2018-04-12 10:00 | 104.41 | 87.93
2018-04-12 10:30 | 101.57 | 86.36
2018-04-12 11:00 | 100.22 | 83.75
2018-04-12 11:30 | 94.57 | 77.59
2018-04-12 12:00 | 92.9 | 76.89
2018-04-12 12:30 | 92.96 | 77.25
2018-04-12 13:00 | 96.25 | 79.86
2018-04-12 13:30 | 99.75 | 83.36
2018-04-12 14:00 | 102.81 | 86.84
2018-04-12 14:30 | 104.81 | 88.84
2018-04-12 15:00 | 104.58 | 88.3
2018-04-12 15:30 | 104.74 | 88.6
2018-04-12 16:00 | 115.37 | 100.24
2018-04-12 16:30 | 107.82 | 92.32
2018-04-12 17:00 | 114.08 | 97.66
2018-04-12 17:30 | 112.32 | 96.84
2018-04-12 18:00 | 117.59 | 101.66
2018-04-12 18:30 | 109.39 | 93.36
2018-04-12 19:00 | 121.82 | 105.17
2018-04-12 19:30 | 117.1 | 99.95
2018-04-12 20:00 | 124.57 | 108.24
2018-04-12 20:30 | 120.18 | 103
2018-04-12 21:00 | 118.91 | 102.52
2018-04-12 21:30 | 121.25 | 103.2
2018-04-12 22:00 | 120.6 | 103.05
2018-04-12 22:30 | 116.7 | 99.58
2018-04-12 23:00 | 123.93 | 107.05
2018-04-12 23:30 | 119.58 | 103.03
2018-04-13 | 123.14 | 107.04
2018-04-13 00:30 | 118.41 | 102.53
2018-04-13 01:00 | 121.33 | 104.66
2018-04-13 01:30 | 119.47 | 103.78
2018-04-13 02:00 | 120.18 | 104.21
2018-04-13 02:30 | 121.47 | 105.12
2018-04-13 03:00 | 118.44 | 102
2018-04-13 03:30 | 114.2 | 97.27
2018-04-13 04:00 | 113.33 | 96.86
2018-04-13 04:30 | 119.72 | 103.69
2018-04-13 05:00 | 117.58 | 100.07
2018-04-13 05:30 | 117.61 | 100.56
2018-04-13 06:00 | 121.67 | 104.63
2018-04-13 06:30 | 110.89 | 93.03
2018-04-13 07:00 | 115.61 | 98.74
2018-04-13 07:30 | 117.89 | 100.49
2018-04-13 08:00 | 108.44 | 91.32
2018-04-13 08:30 | 112.65 | 95.28
2018-04-13 09:00 | 111.51 | 95.22
2018-04-13 09:30 | 111.65 | 94.64
2018-04-13 10:00 | 111.43 | 92.77
2018-04-13 10:30 | 116.67 | 97.59
2018-04-13 11:00 | 119.92 | 100.31
2018-04-13 11:30 | 113.96 | 94.51
2018-04-13 12:00 | 119.2 | 100.75
2018-04-13 12:30 | 117.32 | 99.61
2018-04-13 13:00 | 119.52 | 101.41
2018-04-13 13:30 | 116.64 | 98.95
2018-04-13 14:00 | 109.55 | 91.24
2018-04-13 14:30 | 107.18 | 88.41
2018-04-13 15:00 | 110.09 | 91.26
2018-04-13 15:30 | 108.84 | 90.9
2018-04-13 16:00 | 115.13 | 97.59
2018-04-13 16:30 | 118.98 | 100.68
2018-04-13 17:00 | 115.08 | 96.76
2018-04-13 17:30 | 114.69 | 96.37
2018-04-13 18:00 | 123.63 | 104.82
2018-04-13 18:30 | 117.01 | 98.57
2018-04-13 19:00 | 125.65 | 108.87
2018-04-13 19:30 | 119.07 | 100.84
2018-04-13 20:00 | 122.66 | 102.76
2018-04-13 20:30 | 113.94 | 93.25
2018-04-13 21:00 | 113.69 | 92.56
2018-04-13 21:30 | 114.89 | 93.78
2018-04-13 22:00 | 115.73 | 94.22
2018-04-13 22:30 | 117.36 | 98.16
2018-04-13 23:00 | 111.58 | 92.81
2018-04-13 23:30 | 112.53 | 91.75
2018-04-14 | 106.19 | 86.66
2018-04-14 00:30 | 111.49 | 93.02
2018-04-14 01:00 | 114.73 | 96.39
2018-04-14 01:30 | 112.19 | 94.88
2018-04-14 02:00 | 115.33 | 98.13
2018-04-14 02:30 | 112.65 | 96.21
2018-04-14 03:00 | 114.18 | 96.9
2018-04-14 03:30 | 115.39 | 98.56
2018-04-14 04:00 | 122.43 | 107.27
2018-04-14 04:30 | 117.59 | 102.17
2018-04-14 05:00 | 119.28 | 103.45
2018-04-14 05:30 | 112.77 | 95.51
2018-04-14 06:00 | 113.24 | 94.02
2018-04-14 06:30 | 110.46 | 91.61
2018-04-14 07:00 | 116.27 | 96.95
2018-04-14 07:30 | 119.62 | 101.35
2018-04-14 08:00 | 118.51 | 100.27
2018-04-14 08:30 | 116.35 | 97.44
2018-04-14 09:00 | 107.85 | 87.81
2018-04-14 09:30 | 107.33 | 88.3
2018-04-14 10:00 | 108.94 | 91.28
2018-04-14 10:30 | 117.16 | 99.51
2018-04-14 11:00 | 115.66 | 96.44
2018-04-14 11:30 | 105.75 | 86.86
2018-04-14 12:00 | 108.61 | 90.65
2018-04-14 12:30 | 104.69 | 85.47
2018-04-14 13:00 | 109.21 | 91.43
2018-04-14 13:30 | 107.77 | 89.46
2018-04-14 14:00 | 109.94 | 91.64
2018-04-14 14:30 | 115.7 | 97.05
2018-04-14 15:00 | 119.42 | 100.68
2018-04-14 15:30 | 117.4 | 97.86
2018-04-14 16:00 | 119.39 | 100.21
2018-04-14 16:30 | 114.38 | 95.48
2018-04-14 17:00 | 111.4 | 92.1
2018-04-14 17:30 | 113.69 | 93.9
2018-04-14 18:00 | 114.43 | 95.28
2018-04-14 18:30 | 107.42 | 84.66
2018-04-14 19:00 | 111.03 | 91.25
2018-04-14 19:30 | 117 | 96.43
2018-04-14 20:00 | 118.9 | 98.96
2018-04-14 20:30 | 119.9 | 103.05
2018-04-14 21:00 | 120.19 | 103.67
2018-04-14 21:30 | 116.87 | 100.81
2018-04-14 22:00 | 111.91 | 96.46
2018-04-14 22:30 | 105.99 | 90.18
2018-04-14 23:00 | 117.59 | 102.3
2018-04-14 23:30 | 113.63 | 97.15
2018-04-15 | 108.08 | 90.61
2018-04-15 00:30 | 115.55 | 97.51
2018-04-15 01:00 | 115.98 | 98.79
2018-04-15 01:30 | 114.07 | 97.01
2018-04-15 02:00 | 117.3 | 101.23
2018-04-15 02:30 | 113.56 | 98.37
2018-04-15 03:00 | 114.67 | 98.91
2018-04-15 03:30 | 102.65 | 85.88
2018-04-15 04:00 | 104.96 | 88.51
2018-04-15 04:30 | 110.52 | 95.01
2018-04-15 05:00 | 112.15 | 96.03
2018-04-15 05:30 | 112.9 | 96.37
2018-04-15 06:00 | 112.71 | 97.16
2018-04-15 06:30 | 103.18 | 87.94
2018-04-15 07:00 | 102.51 | 87.45
2018-04-15 07:30 | 104.58 | 88.87
2018-04-15 08:00 | 103.7 | 87.41
2018-04-15 08:30 | 106.2 | 90.13
2018-04-15 09:00 | 106.65 | 90.52
2018-04-15 09:30 | 102.34 | 86.93
2018-04-15 10:00 | 107.42 | 92.57
2018-04-15 10:30 | 101.19 | 85.03
2018-04-15 11:00 | 100.21 | 84.88
2018-04-15 11:30 | 101.83 | 86.09
2018-04-15 12:00 | 103.58 | 86.92
2018-04-15 12:30 | 104.67 | 87.9
2018-04-15 13:00 | 113.87 | 97.67
2018-04-15 13:30 | 118.74 | 100.98
2018-04-15 14:00 | 122.71 | 104.95
2018-04-15 14:30 | 114.87 | 98.46
2018-04-15 15:00 | 107.33 | 90.72
2018-04-15 15:30 | 103.12 | 85.32
2018-04-15 16:00 | 105.73 | 87.72
2018-04-15 16:30 | 113.43 | 95.7
2018-04-15 17:00 | 119 | 101.15
2018-04-15 17:30 | 122.49 | 103.66
2018-04-15 18:00 | 132.89 | 113.47
2018-04-15 18:30 | 124.24 | 102.75
2018-04-15 19:00 | 131.5 | 110.84
2018-04-15 19:30 | 133.01 | 112.95
2018-04-15 20:00 | 134.69 | 113.52
2018-04-15 20:30 | 135.73 | 115.45
2018-04-15 21:00 | 128.05 | 107.58
2018-04-15 21:30 | 132.37 | 112.75
2018-04-15 22:00 | 124.96 | 104.02
2018-04-15 22:30 | 123.86 | 103.22
2018-04-15 23:00 | 120.4 | 100.88
2018-04-15 23:30 | 115.69 | 96.8
2018-04-16 | 121.92 | 103.46
2018-04-16 00:30 | 120.21 | 101.93
2018-04-16 01:00 | 121.83 | 104.13
2018-04-16 01:30 | 116.36 | 96.87
2018-04-16 02:00 | 121.34 | 102.82
2018-04-16 02:30 | 124.25 | 106.25
2018-04-16 03:00 | 116.85 | 98.64
2018-04-16 03:30 | 111.3 | 92.96
2018-04-16 04:00 | 116.25 | 98.46
2018-04-16 04:30 | 115.68 | 98.22
2018-04-16 05:00 | 111.26 | 93.08
2018-04-16 05:30 | 115.31 | 96.7
2018-04-16 06:00 | 106.79 | 86.69
2018-04-16 06:30 | 104.87 | 82.18
2018-04-16 07:00 | 108.7 | 86.35
2018-04-16 07:30 | 111.89 | 91.28
2018-04-16 08:00 | 114.92 | 94.39
2018-04-16 08:30 | 122.5 | 101.63
2018-04-16 09:00 | 118.89 | 97.17
2018-04-16 09:30 | 122.69 | 101.15
2018-04-16 10:00 | 126.31 | 103.93
2018-04-16 10:30 | 128.43 | 107.42
2018-04-16 11:00 | 120.59 | 99.44
2018-04-16 11:30 | 121.61 | 99.99
2018-04-16 12:00 | 126.06 | 105.82
2018-04-16 12:30 | 123.76 | 102.62
2018-04-16 13:00 | 127.12 | 105.46
2018-04-16 13:30 | 123.38 | 102.83
2018-04-16 14:00 | 119.78 | 98.45
2018-04-16 14:30 | 124.23 | 104.61
2018-04-16 15:00 | 120.44 | 99.62
2018-04-16 15:30 | 121.34 | 100.24
2018-04-16 16:00 | 122.18 | 100.85
2018-04-16 16:30 | 114.09 | 94.08
2018-04-16 17:00 | 123.76 | 106.05
2018-04-16 17:30 | 137.61 | 118.64
2018-04-16 18:00 | 132.17 | 111.7
2018-04-16 18:30 | 133.58 | 113.02
2018-04-16 19:00 | 133.55 | 112.08
2018-04-16 19:30 | 132.92 | 111.38
2018-04-16 20:00 | 133.06 | 112.73
2018-04-16 20:30 | 132.97 | 112.5
2018-04-16 21:00 | 133.5 | 112.84
2018-04-16 21:30 | 130.92 | 110.43
2018-04-16 22:00 | 125.33 | 105.14
2018-04-16 22:30 | 129.34 | 109.67
2018-04-16 23:00 | 119.09 | 98.51
2018-04-16 23:30 | 116.84 | 96.79
2018-04-17 | 118.1 | 97.86
2018-04-17 00:30 | 118.87 | 98.24
2018-04-17 01:00 | 116.16 | 96.07
2018-04-17 01:30 | 119.55 | 101.27
2018-04-17 02:00 | 122.66 | 104.38
2018-04-17 02:30 | 115.83 | 96.37
2018-04-17 03:00 | 117.35 | 97.85
2018-04-17 03:30 | 119.86 | 101.76
2018-04-17 04:00 | 117.62 | 99.46
2018-04-17 04:30 | 120.95 | 103.77
2018-04-17 05:00 | 125.97 | 109.39
2018-04-17 05:30 | 115.71 | 99.41
2018-04-17 06:00 | 110.48 | 93.99
2018-04-17 06:30 | 112.03 | 94.3
2018-04-17 07:00 | 112.54 | 95.49
2018-04-17 07:30 | 109.64 | 92.59
2018-04-17 08:00 | 105.97 | 86.15
2018-04-17 08:30 | 109.51 | 88.82
2018-04-17 09:00 | 113.63 | 93.02
2018-04-17 09:30 | 117.19 | 96.68
2018-04-17 10:00 | 111.35 | 92
2018-04-17 10:30 | 109.49 | 88.7
2018-04-17 11:00 | 114.52 | 92.92
2018-04-17 11:30 | 119.59 | 99.1
2018-04-17 12:00 | 117.28 | 95.16
2018-04-17 12:30 | 128 | 107.48
2018-04-17 13:00 | 128.96 | 107.69
2018-04-17 13:30 | 127.48 | 105.43
2018-04-17 14:00 | 119.38 | 100.27
2018-04-17 14:30 | 123.66 | 103.47
2018-04-17 15:00 | 121.66 | 100.4
2018-04-17 15:30 | 119.25 | 96.77
2018-04-17 16:00 | 124.31 | 102.07
2018-04-17 16:30 | 133.91 | 113.56
2018-04-17 17:00 | 128.4 | 107.56
2018-04-17 17:30 | 128.51 | 109.27
2018-04-17 18:00 | 128.85 | 109.44
2018-04-17 18:30 | 116.24 | 96.2
2018-04-17 19:00 | 122.36 | 103.79
2018-04-17 19:30 | 128.38 | 108.28
2018-04-17 20:00 | 131.38 | 111.46
2018-04-17 20:30 | 132.38 | 112.82
2018-04-17 21:00 | 132.71 | 112.84
2018-04-17 21:30 | 121.6 | 102.63
2018-04-17 22:00 | 122.63 | 102.51
2018-04-17 22:30 | 122.28 | 103.4
2018-04-17 23:00 | 121.78 | 102.08
2018-04-17 23:30 | 122.17 | 104.15
2018-04-18 | 129.34 | 111.79
2018-04-18 00:30 | 124.87 | 107.31
2018-04-18 01:00 | 125.05 | 107.97
2018-04-18 01:30 | 125.11 | 108.87
2018-04-18 02:00 | 126.74 | 110.25
2018-04-18 02:30 | 124.34 | 107.55
2018-04-18 03:00 | 118.23 | 101.12
2018-04-18 03:30 | 121.7 | 104.87
2018-04-18 04:00 | 122.25 | 105.78
2018-04-18 04:30 | 119.93 | 103.24
2018-04-18 05:00 | 121.04 | 104.58
2018-04-18 05:30 | 124.71 | 109
2018-04-18 06:00 | 117.67 | 101.31
2018-04-18 06:30 | 108.31 | 90.33
2018-04-18 07:00 | 105.33 | 87.14
2018-04-18 07:30 | 118.08 | 99.13
2018-04-18 08:00 | 116.37 | 95.62
2018-04-18 08:30 | 123.48 | 102.73
2018-04-18 09:00 | 123.15 | 102.68
2018-04-18 09:30 | 119.94 | 98.8
2018-04-18 10:00 | 133.71 | 113.58
2018-04-18 10:30 | 123.36 | 101.48
2018-04-18 11:00 | 127.22 | 106.38
2018-04-18 11:30 | 125.15 | 104.68
2018-04-18 12:00 | 121.33 | 99.78
2018-04-18 12:30 | 124.29 | 103.4
2018-04-18 13:00 | 123.46 | 102.53
2018-04-18 13:30 | 124.35 | 102.65
2018-04-18 14:00 | 123.09 | 101.01
2018-04-18 14:30 | 127.73 | 108.2
2018-04-18 15:00 | 117.19 | 95.68
2018-04-18 15:30 | 119.35 | 97.09
2018-04-18 16:00 | 123.19 | 101.66
2018-04-18 16:30 | 132.48 | 110.29
2018-04-18 17:00 | 127.13 | 106.02
2018-04-18 17:30 | 130.21 | 110.89
2018-04-18 18:00 | 125.58 | 106.11
2018-04-18 18:30 | 118 | 97.45
2018-04-18 19:00 | 118.64 | 97.21
2018-04-18 19:30 | 119.73 | 97.47
2018-04-18 20:00 | 123.89 | 102.38
2018-04-18 20:30 | 135.18 | 114.76
2018-04-18 21:00 | 134.85 | 115.86
2018-04-18 21:30 | 124.59 | 104.66
2018-04-18 22:00 | 130.04 | 110.69
2018-04-18 22:30 | 125.66 | 106.33
2018-04-18 23:00 | 122.54 | 102.55
2018-04-18 23:30 | 124.23 | 104.73
2018-04-19 | 119.79 | 100.82
2018-04-19 00:30 | 121.17 | 102.43
2018-04-19 01:00 | 126.2 | 108.17
2018-04-19 01:30 | 125.9 | 108.5
2018-04-19 02:00 | 127.94 | 111.75
2018-04-19 02:30 | 122.01 | 105.72
2018-04-19 03:00 | 117.16 | 101.1
2018-04-19 03:30 | 112.59 | 95.54
2018-04-19 04:00 | 112.91 | 95.8
2018-04-19 04:30 | 117.32 | 100.82
2018-04-19 05:00 | 112.33 | 95.73
2018-04-19 05:30 | 107.87 | 92.96
2018-04-19 06:00 | 105.88 | 91.48
2018-04-19 06:30 | 102.22 | 87.17
2018-04-19 07:00 | 111.04 | 96.36
2018-04-19 07:30 | 112.63 | 97.88
2018-04-19 08:00 | 102.44 | 87.84
2018-04-19 08:30 | 110.1 | 93.6
2018-04-19 09:00 | 102.2 | 84.48
2018-04-19 09:30 | 107.24 | 92.37
2018-04-19 10:00 | 103.14 | 88.31
2018-04-19 10:30 | 104.32 | 88.59
2018-04-19 11:00 | 104.66 | 89.2
2018-04-19 11:30 | 102.92 | 86.99
2018-04-19 12:00 | 99.37 | 83.02
2018-04-19 12:30 | 106.31 | 92.23
2018-04-19 13:00 | 106.52 | 92.46
2018-04-19 13:30 | 108.55 | 92.6
2018-04-19 14:00 | 108.43 | 92.36
2018-04-19 14:30 | 112.23 | 95.16
2018-04-19 15:00 | 110.3 | 93.18
2018-04-19 15:30 | 105.28 | 89.18
2018-04-19 16:00 | 111.57 | 95.77
2018-04-19 16:30 | 110.91 | 94.38
2018-04-19 17:00 | 113.66 | 97.03
2018-04-19 17:30 | 114.17 | 99.57
2018-04-19 18:00 | 111.76 | 96.55
2018-04-19 18:30 | 106.97 | 90.52
2018-04-19 19:00 | 115.85 | 100.69
2018-04-19 19:30 | 118.91 | 102.85
2018-04-19 20:00 | 122.64 | 105.72
2018-04-19 20:30 | 121.73 | 104.61
2018-04-19 21:00 | 119.76 | 103.88
2018-04-19 21:30 | 120.03 | 105.17
2018-04-19 22:00 | 117.43 | 101.73
2018-04-19 22:30 | 116.49 | 100.76
2018-04-19 23:00 | 119.05 | 102.94
2018-04-19 23:30 | 118.43 | 102.53
2018-04-20 | 124.14 | 109.64
2018-04-20 00:30 | 120.42 | 105.31
2018-04-20 01:00 | 116.54 | 100.76
2018-04-20 01:30 | 117.4 | 102.39
2018-04-20 02:00 | 119.97 | 104.96
2018-04-20 02:30 | 116.31 | 100.84
2018-04-20 03:00 | 110.79 | 95.04
2018-04-20 03:30 | 114.18 | 97.99
2018-04-20 04:00 | 116.26 | 100.67
2018-04-20 04:30 | 118.2 | 102.87
2018-04-20 05:00 | 110.52 | 94.93
2018-04-20 05:30 | 111.26 | 96.72
2018-04-20 06:00 | 106.48 | 91.9
2018-04-20 06:30 | 100.16 | 86.43
2018-04-20 07:00 | 107.09 | 92.71
2018-04-20 07:30 | 112.2 | 97.58
2018-04-20 08:00 | 112.75 | 97.72
2018-04-20 08:30 | 109.7 | 92.13
2018-04-20 09:00 | 113.14 | 95.68
2018-04-20 09:30 | 113.77 | 98.19
2018-04-20 10:00 | 116.07 | 99.55
2018-04-20 10:30 | 114.96 | 98.14
2018-04-20 11:00 | 114.04 | 97.56
2018-04-20 11:30 | 115.66 | 99.88
2018-04-20 12:00 | 113.89 | 98.23
2018-04-20 12:30 | 120.32 | 104.51
2018-04-20 13:00 | 111.05 | 93.93
2018-04-20 13:30 | 115.76 | 97.57
2018-04-20 14:00 | 129.91 | 111.62
2018-04-20 14:30 | 124.23 | 104.81
2018-04-20 15:00 | 121.63 | 102.25
2018-04-20 15:30 | 121.63 | 102.64
2018-04-20 16:00 | 115.05 | 95.61
2018-04-20 16:30 | 120.08 | 101.42
2018-04-20 17:00 | 124.88 | 107.25
2018-04-20 17:30 | 127.01 | 109.96
2018-04-20 18:00 | 132.22 | 115.37
2018-04-20 18:30 | 121 | 103.3
2018-04-20 19:00 | 118.04 | 104.77
2018-04-20 19:30 | 123.12 | 110.79
2018-04-20 20:00 | 124.12 | 111.74
2018-04-20 20:30 | 120.44 | 109.01
2018-04-20 21:00 | 113.67 | 101.61
2018-04-20 21:30 | 118.29 | 106.3
2018-04-20 22:00 | 121.88 | 109.62
2018-04-20 22:30 | 111.48 | 98.95
2018-04-20 23:00 | 112.84 | 100.03
2018-04-20 23:30 | 112.34 | 99.44
2018-04-21 | 107.9 | 95.26
2018-04-21 00:30 | 112.53 | 99.47
2018-04-21 01:00 | 109.56 | 96.3
2018-04-21 01:30 | 112.39 | 100.51
2018-04-21 02:00 | 124.36 | 113.37
2018-04-21 02:30 | 129.37 | 117.65
2018-04-21 03:00 | 117.71 | 106.42
2018-04-21 03:30 | 112.56 | 101.51
2018-04-21 04:00 | 113.65 | 102.63
2018-04-21 04:30 | 113.64 | 102.99
2018-04-21 05:00 | 111.96 | 101.64
2018-04-21 05:30 | 105.82 | 95.23
2018-04-21 06:00 | 110.5 | 99.52
2018-04-21 06:30 | 100.52 | 89.69
2018-04-21 07:00 | 106.28 | 94.99
2018-04-21 07:30 | 109.69 | 98.6
2018-04-21 08:00 | 114.01 | 103.79
2018-04-21 08:30 | 104.32 | 92.93
2018-04-21 09:00 | 101.78 | 90.7
2018-04-21 09:30 | 101.79 | 90.98
2018-04-21 10:00 | 102.18 | 91.52
2018-04-21 10:30 | 106.07 | 94.67
2018-04-21 11:00 | 102.92 | 90.45
2018-04-21 11:30 | 107.15 | 94.94
2018-04-21 12:00 | 111.58 | 98.46
2018-04-21 12:30 | 119.18 | 106.09
2018-04-21 13:00 | 122.23 | 108.34
2018-04-21 13:30 | 115.9 | 100.3
2018-04-21 14:00 | 118.82 | 101.38
2018-04-21 14:30 | 126.23 | 108.93
2018-04-21 15:00 | 123.43 | 107.28
2018-04-21 15:30 | 122.21 | 104.98
2018-04-21 16:00 | 123.69 | 106.88
2018-04-21 16:30 | 121.17 | 104.72
2018-04-21 17:00 | 120.16 | 103.76
2018-04-21 17:30 | 124.29 | 107.11
2018-04-21 18:00 | 126.56 | 109.34
2018-04-21 18:30 | 121.09 | 103.36
2018-04-21 19:00 | 118.26 | 103.78
2018-04-21 19:30 | 120.79 | 105.15
2018-04-21 20:00 | 123.97 | 109.31
2018-04-21 20:30 | 122.95 | 107.8
2018-04-21 21:00 | 120.94 | 106.42
2018-04-21 21:30 | 126.08 | 111.62
2018-04-21 22:00 | 119.18 | 104.41
2018-04-21 22:30 | 123.82 | 109.21
2018-04-21 23:00 | 117.82 | 102.95
2018-04-21 23:30 | 118.96 | 103.83
2018-04-22 | 119.65 | 105.84
2018-04-22 00:30 | 115.63 | 102.13
2018-04-22 01:00 | 115.93 | 102.66
2018-04-22 01:30 | 113.45 | 99.69
2018-04-22 02:00 | 115.82 | 102.18
2018-04-22 02:30 | 109.45 | 95.2
2018-04-22 03:00 | 111.19 | 98.05
2018-04-22 03:30 | 112.62 | 99.03
2018-04-22 04:00 | 112.28 | 99.34
2018-04-22 04:30 | 112.63 | 100.03
2018-04-22 05:00 | 115.45 | 103.44
2018-04-22 05:30 | 112.76 | 100.12
2018-04-22 06:00 | 113.3 | 101.2
2018-04-22 06:30 | 105.58 | 93.56
2018-04-22 07:00 | 110.86 | 98.57
2018-04-22 07:30 | 113.26 | 100.87
2018-04-22 08:00 | 117.29 | 104.61
2018-04-22 08:30 | 111.79 | 98.61
2018-04-22 09:00 | 117.16 | 103.64
2018-04-22 09:30 | 109.68 | 96.14
2018-04-22 10:00 | 105.25 | 91.55
2018-04-22 10:30 | 106.73 | 92.67
2018-04-22 11:00 | 111.15 | 97.2
2018-04-22 11:30 | 110.16 | 95.27
2018-04-22 12:00 | 108.46 | 93.06
2018-04-22 12:30 | 113.68 | 99.14
2018-04-22 13:00 | 109.61 | 94.01
2018-04-22 13:30 | 114.96 | 98.99
2018-04-22 14:00 | 119.28 | 103.55
2018-04-22 14:30 | 115.36 | 99.89
2018-04-22 15:00 | 118.89 | 102.78
2018-04-22 15:30 | 116.29 | 101.25
2018-04-22 16:00 | 115.57 | 99.77
2018-04-22 16:30 | 117.74 | 102.43
2018-04-22 17:00 | 119.45 | 103.18
2018-04-22 17:30 | 121.01 | 105.13
2018-04-22 18:00 | 117.2 | 99.79
2018-04-22 18:30 | 113.8 | 95.13
2018-04-22 19:00 | 125.1 | 109.03
2018-04-22 19:30 | 123.31 | 108.58
2018-04-22 20:00 | 124.41 | 111
2018-04-22 20:30 | 125.23 | 112.45
2018-04-22 21:00 | 120.63 | 108.07
2018-04-22 21:30 | 124.43 | 111.83
2018-04-22 22:00 | 119.08 | 104.95
2018-04-22 22:30 | 126.86 | 113.45
2018-04-22 23:00 | 118.75 | 105.41
2018-04-22 23:30 | 123.12 | 110.4
2018-04-23 | 117.3 | 104.69
2018-04-23 00:30 | 110 | 96.74
2018-04-23 01:00 | 113.26 | 100.11
2018-04-23 01:30 | 117.36 | 104.53
2018-04-23 02:00 | 114.1 | 101.23
2018-04-23 02:30 | 113.63 | 100.11
2018-04-23 03:00 | 121.57 | 108.3
2018-04-23 03:30 | 117.09 | 103.16
2018-04-23 04:00 | 119.48 | 106.17
2018-04-23 04:30 | 123.78 | 110.71
2018-04-23 05:00 | 116.22 | 102.78
2018-04-23 05:30 | 118.92 | 105.5
2018-04-23 06:00 | 117.23 | 103.65
2018-04-23 06:30 | 106.28 | 92.03
2018-04-23 07:00 | 112.98 | 98.52
2018-04-23 07:30 | 115.07 | 99.66
2018-04-23 08:00 | 111.24 | 95.5
2018-04-23 08:30 | 108.91 | 91.64
2018-04-23 09:00 | 110.95 | 94.07
2018-04-23 09:30 | 106.98 | 91.31
2018-04-23 10:00 | 102.68 | 89.76
2018-04-23 10:30 | 119.73 | 102.98
2018-04-23 11:00 | 113.85 | 95.47
2018-04-23 11:30 | 106.98 | 89.02
2018-04-23 12:00 | 101.95 | 86.36
2018-04-23 12:30 | 106.26 | 90.77
2018-04-23 13:00 | 111.39 | 96.46
2018-04-23 13:30 | 119.89 | 105.29
2018-04-23 14:00 | 109.65 | 94.4
2018-04-23 14:30 | 114.84 | 99.33
2018-04-23 15:00 | 123.03 | 107.52
2018-04-23 15:30 | 115.97 | 100.7
2018-04-23 16:00 | 115.49 | 99.83
2018-04-23 16:30 | 119.86 | 104.87
2018-04-23 17:00 | 125.97 | 111.78
2018-04-23 17:30 | 121.6 | 107.32
2018-04-23 18:00 | 124.48 | 109.55
2018-04-23 18:30 | 116.26 | 99.7
2018-04-23 19:00 | 124.17 | 108.31
2018-04-23 19:30 | 125.76 | 110.93
2018-04-23 20:00 | 127.91 | 112.52
2018-04-23 20:30 | 127.1 | 113.17
2018-04-23 21:00 | 122.72 | 108.19
2018-04-23 21:30 | 124.54 | 108.85
2018-04-23 22:00 | 124.97 | 108.59
2018-04-23 22:30 | 120.09 | 103.97
2018-04-23 23:00 | 124.02 | 109.14
2018-04-23 23:30 | 112.13 | 97.55
2018-04-24 | 111.78 | 97.16
2018-04-24 00:30 | 111.16 | 97.18
2018-04-24 01:00 | 117.89 | 102.91
2018-04-24 01:30 | 110.67 | 95.78
2018-04-24 02:00 | 112.19 | 97.42
2018-04-24 02:30 | 120.22 | 104.67
2018-04-24 03:00 | 114.08 | 98.29
2018-04-24 03:30 | 122.74 | 108.14
2018-04-24 04:00 | 125.31 | 110.91
2018-04-24 04:30 | 121.34 | 106.15
2018-04-24 05:00 | 123.03 | 109.25
2018-04-24 05:30 | 120.54 | 107.67
2018-04-24 06:00 | 114.34 | 100.15
2018-04-24 06:30 | 110.08 | 95.5
2018-04-24 07:00 | 112.17 | 98
2018-04-24 07:30 | 113.42 | 98.47
2018-04-24 08:00 | 107.97 | 93.53
2018-04-24 08:30 | 106.84 | 91.18
2018-04-24 09:00 | 103.03 | 86.97
2018-04-24 09:30 | 97.18 | 79.96
2018-04-24 10:00 | 105.38 | 88.14
2018-04-24 10:30 | 103.81 | 85.96
2018-04-24 11:00 | 104.59 | 88.59
2018-04-24 11:30 | 108.52 | 93.92
2018-04-24 12:00 | 94.99 | 80.51
2018-04-24 12:30 | 102.13 | 87.87
2018-04-24 13:00 | 108.72 | 93.13
2018-04-24 13:30 | 103.2 | 87.95
2018-04-24 14:00 | 105.33 | 90.33
2018-04-24 14:30 | 103.86 | 88.34
2018-04-24 15:00 | 106.31 | 90.48
2018-04-24 15:30 | 107.67 | 91.68
2018-04-24 16:00 | 108.03 | 91.3
2018-04-24 16:30 | 106.24 | 90.37
2018-04-24 17:00 | 115.34 | 100.25
2018-04-24 17:30 | 107.64 | 91.81
2018-04-24 18:00 | 113.12 | 97.31
2018-04-24 18:30 | 107.88 | 91.17
2018-04-24 19:00 | 108.02 | 90.57
2018-04-24 19:30 | 122.01 | 106.13
2018-04-24 20:00 | 118.26 | 103.53
2018-04-24 20:30 | 109.73 | 95.35
2018-04-24 21:00 | 119.15 | 105.19
2018-04-24 21:30 | 121.79 | 108.41
2018-04-24 22:00 | 114.54 | 101.19
2018-04-24 22:30 | 115.5 | 102.67
2018-04-24 23:00 | 110.49 | 97.15
2018-04-24 23:30 | 108.23 | 95.72
2018-04-25 | 105.18 | 92.06
2018-04-25 00:30 | 114.3 | 101.94
2018-04-25 01:00 | 114.82 | 100.93
2018-04-25 01:30 | 107.25 | 92.25
2018-04-25 02:00 | 105.49 | 91.63
2018-04-25 02:30 | 104.65 | 90.03
2018-04-25 03:00 | 105.9 | 92.17
2018-04-25 03:30 | 109.72 | 95.45
2018-04-25 04:00 | 111.57 | 98.91
2018-04-25 04:30 | 105.49 | 93.04
2018-04-25 05:00 | 104.46 | 91.7
2018-04-25 05:30 | 106.22 | 94.45
2018-04-25 06:00 | 103.82 | 90.46
2018-04-25 06:30 | 104.78 | 91.42
2018-04-25 07:00 | 106.71 | 94.61
2018-04-25 07:30 | 106.29 | 94.14
2018-04-25 08:00 | 107.58 | 93.83
2018-04-25 08:30 | 107.34 | 93.3
2018-04-25 09:00 | 102.24 | 87.85
2018-04-25 09:30 | 101.89 | 88.32
2018-04-25 10:00 | 99.1 | 84.39
2018-04-25 10:30 | 102.95 | 88.03
2018-04-25 11:00 | 100.34 | 85.52
2018-04-25 11:30 | 102.53 | 87.46
2018-04-25 12:00 | 104.86 | 89.05
2018-04-25 12:30 | 103.7 | 86.12
2018-04-25 13:00 | 115.24 | 98.45
2018-04-25 13:30 | 112.66 | 96.46
2018-04-25 14:00 | 121.05 | 104.74
2018-04-25 14:30 | 120.57 | 103.67
2018-04-25 15:00 | 121.09 | 103.84
2018-04-25 15:30 | 116.31 | 99.5
2018-04-25 16:00 | 117.44 | 100.95
2018-04-25 16:30 | 121.95 | 105.27
2018-04-25 17:00 | 120.68 | 104.58
2018-04-25 17:30 | 129.18 | 112.62
2018-04-25 18:00 | 131.64 | 115.02
2018-04-25 18:30 | 125.63 | 107.6
2018-04-25 19:00 | 127.13 | 109.7
2018-04-25 19:30 | 131.75 | 115.82
2018-04-25 20:00 | 123.64 | 106.46
2018-04-25 20:30 | 118.37 | 102.37
2018-04-25 21:00 | 107.32 | 91.39
2018-04-25 21:30 | 116.18 | 100.83
2018-04-25 22:00 | 116.06 | 99.69
2018-04-25 22:30 | 121.21 | 106.24
2018-04-25 23:00 | 119.13 | 103.17
2018-04-25 23:30 | 111.66 | 95.53
2018-04-26 | 116.41 | 100.51
2018-04-26 00:30 | 112.16 | 95.93
2018-04-26 01:00 | 115.54 | 100
2018-04-26 01:30 | 110.81 | 95.5
2018-04-26 02:00 | 109.93 | 95.5
2018-04-26 02:30 | 114.99 | 101.59
2018-04-26 03:00 | 109.84 | 96.09
2018-04-26 03:30 | 114.41 | 100.14
2018-04-26 04:00 | 106.43 | 90.79
2018-04-26 04:30 | 104.28 | 88.22
2018-04-26 05:00 | 104.48 | 88.58
2018-04-26 05:30 | 105.41 | 89.17
2018-04-26 06:00 | 98.57 | 83.61
2018-04-26 06:30 | 103.79 | 89
2018-04-26 07:00 | 104.89 | 90.63
2018-04-26 07:30 | 107.94 | 93.35
2018-04-26 08:00 | 108.11 | 92.6
2018-04-26 08:30 | 102.25 | 86.9
2018-04-26 09:00 | 105.24 | 89.94
2018-04-26 09:30 | 103.02 | 87.79
2018-04-26 10:00 | 103.75 | 88.42
2018-04-26 10:30 | 104.83 | 88.64
2018-04-26 11:00 | 101.25 | 84.58
2018-04-26 11:30 | 100.39 | 84.43
2018-04-26 12:00 | 103.65 | 88.42
2018-04-26 12:30 | 100.75 | 86.45
2018-04-26 13:00 | 102.42 | 87.94
2018-04-26 13:30 | 106.42 | 90.26
2018-04-26 14:00 | 113.08 | 97.03
2018-04-26 14:30 | 118.79 | 103.74
2018-04-26 15:00 | 117.72 | 102.05
2018-04-26 15:30 | 111 | 94.25
2018-04-26 16:00 | 114.94 | 97.2
2018-04-26 16:30 | 114.79 | 98.68
2018-04-26 17:00 | 117.55 | 102.49
2018-04-26 17:30 | 113.41 | 96.94
2018-04-26 18:00 | 120.3 | 105.43
2018-04-26 18:30 | 112.49 | 96.7
2018-04-26 19:00 | 114.58 | 98.74
2018-04-26 19:30 | 120.58 | 105.11
2018-04-26 20:00 | 114.29 | 97.76
2018-04-26 20:30 | 113.96 | 98
2018-04-26 21:00 | 114.64 | 99.49
2018-04-26 21:30 | 113.33 | 98.13
2018-04-26 22:00 | 114.3 | 99.53
2018-04-26 22:30 | 114.62 | 99.37
2018-04-26 23:00 | 117.51 | 101.05
2018-04-26 23:30 | 111.1 | 94.94
2018-04-27 | 109.79 | 94.12
2018-04-27 00:30 | 110.06 | 95.3
2018-04-27 01:00 | 107.22 | 92.29
2018-04-27 01:30 | 106.55 | 91.2
2018-04-27 02:00 | 113.58 | 98.3
2018-04-27 02:30 | 111.92 | 96.05
2018-04-27 03:00 | 114.66 | 99.06
2018-04-27 03:30 | 114.09 | 97.69
2018-04-27 04:00 | 109.74 | 93.53
2018-04-27 04:30 | 110.47 | 95.23
2018-04-27 05:00 | 117.19 | 101.96
2018-04-27 05:30 | 114.32 | 99.16
2018-04-27 06:00 | 113.08 | 97.34
2018-04-27 06:30 | 113.15 | 97.33
2018-04-27 07:00 | 115.82 | 100.78
2018-04-27 07:30 | 117.42 | 102.25
2018-04-27 08:00 | 115.51 | 100.87
2018-04-27 08:30 | 118.05 | 102.93
2018-04-27 09:00 | 113.19 | 97.51
2018-04-27 09:30 | 107.36 | 89.34
2018-04-27 10:00 | 111.52 | 94.34
2018-04-27 10:30 | 107.3 | 90.66
2018-04-27 11:00 | 107.29 | 91.38
2018-04-27 11:30 | 108.49 | 91.81
2018-04-27 12:00 | 105.81 | 88.99
2018-04-27 12:30 | 113.47 | 98.18
2018-04-27 13:00 | 108.06 | 91.89
2018-04-27 13:30 | 106.64 | 90.89
2018-04-27 14:00 | 110.15 | 94.03
2018-04-27 14:30 | 112.47 | 96.97
2018-04-27 15:00 | 111.18 | 95.27
2018-04-27 15:30 | 109.55 | 93.48
2018-04-27 16:00 | 113.57 | 98.4
2018-04-27 16:30 | 113.05 | 98.02
2018-04-27 17:00 | 115.95 | 102.23
2018-04-27 17:30 | 110.88 | 96.28
2018-04-27 18:00 | 112.5 | 98.21
2018-04-27 18:30 | 105.02 | 89.1
2018-04-27 19:00 | 115.36 | 101.42
2018-04-27 19:30 | 116.24 | 102.42
2018-04-27 20:00 | 114.1 | 101.15
2018-04-27 20:30 | 109.66 | 95.44
2018-04-27 21:00 | 107.77 | 92.8
2018-04-27 21:30 | 106.62 | 91.44
2018-04-27 22:00 | 106.15 | 91.24
2018-04-27 22:30 | 104.68 | 89.43
2018-04-27 23:00 | 105.78 | 90.23
2018-04-27 23:30 | 102.86 | 87.14
2018-04-28 | 108.5 | 94.43
2018-04-28 00:30 | 111.73 | 97.35
2018-04-28 01:00 | 108.68 | 94.23
2018-04-28 01:30 | 105.21 | 89.01
2018-04-28 02:00 | 102.74 | 85.95
2018-04-28 02:30 | 104.71 | 87.68
2018-04-28 03:00 | 99.58 | 83.97
2018-04-28 03:30 | 107.13 | 91.73
2018-04-28 04:00 | 108.8 | 94.07
2018-04-28 04:30 | 107.27 | 93.11
2018-04-28 05:00 | 113.56 | 100.68
2018-04-28 05:30 | 110.97 | 97.59
2018-04-28 06:00 | 108.28 | 93.98
2018-04-28 06:30 | 104.46 | 89.62
2018-04-28 07:00 | 98.97 | 85.19
2018-04-28 07:30 | 104.22 | 90.45
2018-04-28 08:00 | 103.32 | 88.59
2018-04-28 08:30 | 105.82 | 92.97
2018-04-28 09:00 | 106.01 | 92.55
2018-04-28 09:30 | 102.58 | 89.85
2018-04-28 10:00 | 100.89 | 87.63
2018-04-28 10:30 | 102.51 | 87.39
2018-04-28 11:00 | 101.34 | 85.69
2018-04-28 11:30 | 108.3 | 94.58
2018-04-28 12:00 | 105.8 | 92.46
2018-04-28 12:30 | 110.25 | 96.99
2018-04-28 13:00 | 115.66 | 103.09
2018-04-28 13:30 | 109.84 | 96.31
2018-04-28 14:00 | 115.06 | 101.03
2018-04-28 14:30 | 113.63 | 98.69
2018-04-28 15:00 | 117.46 | 102.42
2018-04-28 15:30 | 112.82 | 96.88
2018-04-28 16:00 | 112.35 | 96.5
2018-04-28 16:30 | 118.13 | 103.34
2018-04-28 17:00 | 114.6 | 100.18
2018-04-28 17:30 | 120.2 | 106.11
2018-04-28 18:00 | 120.95 | 106.93
2018-04-28 18:30 | 111.82 | 96.67
2018-04-28 19:00 | 116.31 | 101.5
2018-04-28 19:30 | 115.06 | 100.6
2018-04-28 20:00 | 109.13 | 96.99
2018-04-28 20:30 | 115.71 | 104.59
2018-04-28 21:00 | 110.07 | 96.94
2018-04-28 21:30 | 106.88 | 91.86
2018-04-28 22:00 | 108.33 | 93.41
2018-04-28 22:30 | 114.19 | 99.92
2018-04-28 23:00 | 108.27 | 92.77
2018-04-28 23:30 | 106.66 | 90.48
2018-04-29 | 99.84 | 79.7
2018-04-29 00:30 | 106.85 | 89.09
2018-04-29 01:00 | 111.01 | 93.59
2018-04-29 01:30 | 115.7 | 100.4
2018-04-29 02:00 | 110.64 | 94.67
2018-04-29 02:30 | 115.78 | 100.61
2018-04-29 03:00 | 115.93 | 101.17
2018-04-29 03:30 | 114.44 | 97.8
2018-04-29 04:00 | 104.78 | 84.84
2018-04-29 04:30 | 107.65 | 88.62
2018-04-29 05:00 | 112.45 | 94.86
2018-04-29 05:30 | 117.86 | 101.28
2018-04-29 06:00 | 108.92 | 89.49
2018-04-29 06:30 | 107.1 | 87.07
2018-04-29 07:00 | 109.48 | 91.76
2018-04-29 07:30 | 112.87 | 95.9
2018-04-29 08:00 | 111.99 | 94.69
2018-04-29 08:30 | 116.54 | 100.8
2018-04-29 09:00 | 112.61 | 94.71
2018-04-29 09:30 | 111.87 | 95.62
2018-04-29 10:00 | 114.21 | 99.5
2018-04-29 10:30 | 110.8 | 94.16
2018-04-29 11:00 | 113.3 | 97.5
2018-04-29 11:30 | 110.63 | 92.63
2018-04-29 12:00 | 112.9 | 97.37
2018-04-29 12:30 | 110.21 | 94.56
2018-04-29 13:00 | 116.14 | 102.31
2018-04-29 13:30 | 116.4 | 102.88
2018-04-29 14:00 | 113.18 | 98.47
2018-04-29 14:30 | 103.96 | 87.84
2018-04-29 15:00 | 105.55 | 89.98
2018-04-29 15:30 | 112.25 | 96.75
2018-04-29 16:00 | 113.44 | 99.93
2018-04-29 16:30 | 112.4 | 99.26
2018-04-29 17:00 | 108.5 | 93.07
2018-04-29 17:30 | 107.84 | 92.38
2018-04-29 18:00 | 110.04 | 97.08
2018-04-29 18:30 | 108.15 | 92.9
2018-04-29 19:00 | 119.21 | 107.17
2018-04-29 19:30 | 118.73 | 106.75
2018-04-29 20:00 | 115.04 | 102.26
2018-04-29 20:30 | 114.7 | 102.4
2018-04-29 21:00 | 109.56 | 95.19
2018-04-29 21:30 | 107.85 | 92.8
2018-04-29 22:00 | 109.44 | 95.56
2018-04-29 22:30 | 104.44 | 89.92
2018-04-29 23:00 | 99.86 | 83.63
2018-04-29 23:30 | 95.81 | 76.46
2018-04-30 | 90.09 | 68.5
2018-04-30 00:30 | 92.16 | 72.5
2018-04-30 01:00 | 99.09 | 82.51
2018-04-30 01:30 | 98.99 | 83.12
2018-04-30 02:00 | 94.54 | 74.55
2018-04-30 02:30 | 99.89 | 84.23
2018-04-30 03:00 | 100.82 | 86.06
2018-04-30 03:30 | 95.04 | 77.13
2018-04-30 04:00 | 95.34 | 78.65
2018-04-30 04:30 | 95.77 | 78.45
2018-04-30 05:00 | 92.6 | 74.14
2018-04-30 05:30 | 81.82 | 70.79
2018-04-30 06:00 | 71.06 | 69.87
2018-04-30 06:30 | 70.32 | 68.94
2018-04-30 07:00 | 72.91 | 71.53
2018-04-30 07:30 | 77.37 | 75.84
2018-04-30 08:00 | 77.96 | 76.22
2018-04-30 08:30 | 78.93 | 76.91
2018-04-30 09:00 | 75.71 | 73.74
2018-04-30 09:30 | 73.34 | 71.57
2018-04-30 10:00 | 73.64 | 72.23
2018-04-30 10:30 | 76.94 | 75.57
2018-04-30 11:00 | 74.22 | 72.72
2018-04-30 11:30 | 72.71 | 71.3
2018-04-30 12:00 | 76.75 | 75.25
2018-04-30 12:30 | 76.07 | 74.56
2018-04-30 13:00 | 77.13 | 76.17
2018-04-30 13:30 | 79.36 | 78.35
2018-04-30 14:00 | 82.09 | 80.99
2018-04-30 14:30 | 78.99 | 77.97
2018-04-30 15:00 | 83.74 | 82.44
2018-04-30 15:30 | 88.51 | 86.88
2018-04-30 16:00 | 83.3 | 81.69
2018-04-30 16:30 | 85.58 | 84.11
2018-04-30 17:00 | 86.38 | 85.11
2018-04-30 17:30 | 86.84 | 85.55
2018-04-30 18:00 | 87.6 | 86.32
2018-04-30 18:30 | 85.68 | 84.12
2018-04-30 19:00 | 90.68 | 89.3
2018-04-30 19:30 | 89.51 | 88.01
2018-04-30 20:00 | 92.86 | 91.28
2018-04-30 20:30 | 90.72 | 89.29
2018-04-30 21:00 | 87.8 | 86.15
2018-04-30 21:30 | 90.5 | 88.6
2018-04-30 22:00 | 87.28 | 84.89
2018-04-30 22:30 | 85.06 | 82.34
2018-04-30 23:00 | 87.89 | 85.28
2018-04-30 23:30 | 86.04 | 83.25
2018-05-01 | 85.66 | 83.06
2018-05-01 00:30 | 85.15 | 82.72
2018-05-01 01:00 | 85.91 | 83.63
2018-05-01 01:30 | 87.03 | 84.71
2018-05-01 02:00 | 85.16 | 82.67
2018-05-01 02:30 | 86.69 | 84.3
2018-05-01 03:00 | 83.87 | 81.15
2018-05-01 03:30 | 83.64 | 80.46
2018-05-01 04:00 | 81.05 | 77.9
2018-05-01 04:30 | 81.19 | 78.12
2018-05-01 05:00 | 79.43 | 76.25
2018-05-01 05:30 | 84.38 | 81.61
2018-05-01 06:00 | 82.39 | 79.31
2018-05-01 06:30 | 79.58 | 76.18
2018-05-01 07:00 | 79.98 | 78.07
2018-05-01 07:30 | 79.05 | 77.85
2018-05-01 08:00 | 83.07 | 81.56
2018-05-01 08:30 | 82.91 | 81.16
2018-05-01 09:00 | 85.28 | 83.78
2018-05-01 09:30 | 82.23 | 80.55
2018-05-01 10:00 | 80.5 | 78.5
2018-05-01 10:30 | 83.52 | 81.57
2018-05-01 11:00 | 85.84 | 83.84
2018-05-01 11:30 | 75.79 | 73.46
2018-05-01 12:00 | 84.65 | 82.63
2018-05-01 12:30 | 82.77 | 80.84
2018-05-01 13:00 | 80.39 | 78.27
2018-05-01 13:30 | 83.9 | 81.92
2018-05-01 14:00 | 81.78 | 79.82
2018-05-01 14:30 | 83.31 | 81.26
2018-05-01 15:00 | 84.61 | 82.61
2018-05-01 15:30 | 81.62 | 79.6
2018-05-01 16:00 | 83.8 | 81.89
2018-05-01 16:30 | 88.82 | 86.99
2018-05-01 17:00 | 90.86 | 88.86
2018-05-01 17:30 | 86.1 | 84.66
2018-05-01 18:00 | 85.67 | 81.72
2018-05-01 18:30 | 94.47 | 76.69
2018-05-01 19:00 | 102.42 | 85.61
2018-05-01 19:30 | 102.3 | 84.8
2018-05-01 20:00 | 101.85 | 84.15
2018-05-01 20:30 | 101.1 | 82.27
2018-05-01 21:00 | 100.08 | 79.94
2018-05-01 21:30 | 104.34 | 84.59
2018-05-01 22:00 | 106.77 | 87.37
2018-05-01 22:30 | 106.51 | 86.71
2018-05-01 23:00 | 106.76 | 87.41
2018-05-01 23:30 | 104.56 | 84.8
2018-05-02 | 103.19 | 82.8
2018-05-02 00:30 | 105.83 | 85.83
2018-05-02 01:00 | 106.64 | 87.22
2018-05-02 01:30 | 104.96 | 84.83
2018-05-02 02:00 | 108.62 | 90.59
2018-05-02 02:30 | 110.27 | 92.39
2018-05-02 03:00 | 112.41 | 95.29
2018-05-02 03:30 | 110.17 | 91.91
2018-05-02 04:00 | 102.9 | 81.95
2018-05-02 04:30 | 107.37 | 89.12
2018-05-02 05:00 | 104.93 | 84.18
2018-05-02 05:30 | 108.32 | 91.05
2018-05-02 06:00 | 105.58 | 86.29
2018-05-02 06:30 | 99.52 | 77.29
2018-05-02 07:00 | 105.57 | 87.21
2018-05-02 07:30 | 99.03 | 79.35
2018-05-02 08:00 | 98.46 | 78.66
2018-05-02 08:30 | 97.93 | 77.76
2018-05-02 09:00 | 101.99 | 82.7
2018-05-02 09:30 | 101.77 | 82.01
2018-05-02 10:00 | 103.86 | 85.26
2018-05-02 10:30 | 100.78 | 81.67
2018-05-02 11:00 | 102.46 | 83.38
2018-05-02 11:30 | 100.7 | 80.42
2018-05-02 12:00 | 98.39 | 78.14
2018-05-02 12:30 | 102.01 | 82.39
2018-05-02 13:00 | 104.48 | 87.47
2018-05-02 13:30 | 103.03 | 85.9
2018-05-02 14:00 | 99.34 | 80.98
2018-05-02 14:30 | 95.59 | 76.38
2018-05-02 15:00 | 99.72 | 82.96
2018-05-02 15:30 | 101.84 | 84.27
2018-05-02 16:00 | 100.47 | 83.68
2018-05-02 16:30 | 98.48 | 81.44
2018-05-02 17:00 | 100.44 | 83.69
2018-05-02 17:30 | 103.77 | 88.05
2018-05-02 18:00 | 106.47 | 89.95
2018-05-02 18:30 | 103.7 | 88.85
2018-05-02 19:00 | 103.98 | 88.53
2018-05-02 19:30 | 107.4 | 92.5
2018-05-02 20:00 | 107.16 | 91.24
2018-05-02 20:30 | 109.66 | 94.84
2018-05-02 21:00 | 109.78 | 93.52
2018-05-02 21:30 | 111.79 | 94.48
2018-05-02 22:00 | 107.36 | 89.61
2018-05-02 22:30 | 112.09 | 96.65
2018-05-02 23:00 | 113.04 | 99.1
2018-05-02 23:30 | 107.88 | 90.51
2018-05-03 | 113.54 | 96.97
2018-05-03 00:30 | 106.1 | 87.24
2018-05-03 01:00 | 110.97 | 95.6
2018-05-03 01:30 | 113.29 | 98.27
2018-05-03 02:00 | 111.53 | 94.95
2018-05-03 02:30 | 112.88 | 97.86
2018-05-03 03:00 | 114.81 | 100.42
2018-05-03 03:30 | 114.69 | 98.8
2018-05-03 04:00 | 109.48 | 92.09
2018-05-03 04:30 | 112.17 | 94.78
2018-05-03 05:00 | 109.69 | 93.09
2018-05-03 05:30 | 108.03 | 89.74
2018-05-03 06:00 | 107.19 | 88.71
2018-05-03 06:30 | 101.41 | 78.51
2018-05-03 07:00 | 107.73 | 84.34
2018-05-03 07:30 | 108.04 | 84.54
2018-05-03 08:00 | 107.86 | 84.11
2018-05-03 08:30 | 107.23 | 83.59
2018-05-03 09:00 | 106.44 | 79.6
2018-05-03 09:30 | 104.07 | 75.57
2018-05-03 10:00 | 101.43 | 74.7
2018-05-03 10:30 | 99.51 | 70.62
2018-05-03 11:00 | 104.2 | 75.94
2018-05-03 11:30 | 105.21 | 76.76
2018-05-03 12:00 | 105.43 | 79.22
2018-05-03 12:30 | 108.02 | 82.56
2018-05-03 13:00 | 108.14 | 82.59
2018-05-03 13:30 | 107.47 | 81.75
2018-05-03 14:00 | 105.99 | 78.73
2018-05-03 14:30 | 109.21 | 83.19
2018-05-03 15:00 | 111.95 | 86.42
2018-05-03 15:30 | 108.69 | 83.81
2018-05-03 16:00 | 107.05 | 82.74
2018-05-03 16:30 | 108.26 | 84.86
2018-05-03 17:00 | 103.78 | 84.29
2018-05-03 17:30 | 104.46 | 86.85
2018-05-03 18:00 | 107.65 | 91.22
2018-05-03 18:30 | 102.56 | 84.79
2018-05-03 19:00 | 111.19 | 97.39
2018-05-03 19:30 | 111.78 | 98.11
2018-05-03 20:00 | 114.81 | 100.63
2018-05-03 20:30 | 115.9 | 102.75
2018-05-03 21:00 | 110.67 | 97.89
2018-05-03 21:30 | 111.67 | 98.37
2018-05-03 22:00 | 113.66 | 102.35
2018-05-03 22:30 | 119.76 | 108.85
2018-05-03 23:00 | 116.31 | 103.87
2018-05-03 23:30 | 111.51 | 97.36
2018-05-04 | 110.29 | 95.56
2018-05-04 00:30 | 110.19 | 95.23
2018-05-04 01:00 | 111.21 | 96.69
2018-05-04 01:30 | 105.47 | 88.92
2018-05-04 02:00 | 109.56 | 94.3
2018-05-04 02:30 | 112.42 | 97.34
2018-05-04 03:00 | 112.94 | 97.86
2018-05-04 03:30 | 107.57 | 92.07
2018-05-04 04:00 | 111.39 | 97.27
2018-05-04 04:30 | 109.56 | 94.71
2018-05-04 05:00 | 110.61 | 96.75
2018-05-04 05:30 | 113.17 | 99.86
2018-05-04 06:00 | 113.69 | 100.43
2018-05-04 06:30 | 105.51 | 89.84
2018-05-04 07:00 | 108.44 | 94.18
2018-05-04 07:30 | 108.45 | 94.06
2018-05-04 08:00 | 108.28 | 94.28
2018-05-04 08:30 | 109.4 | 95.38
2018-05-04 09:00 | 108.73 | 93.87
2018-05-04 09:30 | 114.29 | 101.44
2018-05-04 10:00 | 104.46 | 87.9
2018-05-04 10:30 | 105.75 | 89.93
2018-05-04 11:00 | 101.16 | 82.13
2018-05-04 11:30 | 110.3 | 94.74
2018-05-04 12:00 | 112.46 | 98.3
2018-05-04 12:30 | 110.71 | 96.63
2018-05-04 13:00 | 110.23 | 95.88
2018-05-04 13:30 | 106.86 | 92.11
2018-05-04 14:00 | 109.23 | 94.18
2018-05-04 14:30 | 111.79 | 97.12
2018-05-04 15:00 | 115.22 | 101.78
2018-05-04 15:30 | 102.55 | 85.04
2018-05-04 16:00 | 105.3 | 89.15
2018-05-04 16:30 | 111.29 | 97.34
2018-05-04 17:00 | 113.76 | 100.72
2018-05-04 17:30 | 105.42 | 90.59
2018-05-04 18:00 | 109.78 | 96.6
2018-05-04 18:30 | 105.8 | 91.31
2018-05-04 19:00 | 114.35 | 101.56
2018-05-04 19:30 | 117.75 | 106.18
2018-05-04 20:00 | 113.01 | 98.65
2018-05-04 20:30 | 114.16 | 100.35
2018-05-04 21:00 | 116.21 | 103.39
2018-05-04 21:30 | 108.17 | 93.41
2018-05-04 22:00 | 110.09 | 95.87
2018-05-04 22:30 | 108.18 | 91.85
2018-05-04 23:00 | 106.28 | 88.98
2018-05-04 23:30 | 106.54 | 89.39
2018-05-05 | 113.72 | 98.45
2018-05-05 00:30 | 110.86 | 96.52
2018-05-05 01:00 | 110.08 | 92.93
2018-05-05 01:30 | 107.1 | 89.57
2018-05-05 02:00 | 108.91 | 92.22
2018-05-05 02:30 | 110.57 | 92.96
2018-05-05 03:00 | 109.56 | 92.08
2018-05-05 03:30 | 112.27 | 96.05
2018-05-05 04:00 | 109.94 | 92.75
2018-05-05 04:30 | 107.22 | 88.72
2018-05-05 05:00 | 108.86 | 92.26
2018-05-05 05:30 | 103.09 | 83.43
2018-05-05 06:00 | 111.42 | 94.96
2018-05-05 06:30 | 105.7 | 86.78
2018-05-05 07:00 | 108.07 | 89.18
2018-05-05 07:30 | 108.13 | 90.17
2018-05-05 08:00 | 108.41 | 90.96
2018-05-05 08:30 | 107.32 | 89.74
2018-05-05 09:00 | 107.2 | 90.23
2018-05-05 09:30 | 104.48 | 85.46
2018-05-05 10:00 | 104.81 | 86.48
2018-05-05 10:30 | 105.08 | 85.36
2018-05-05 11:00 | 107.74 | 89.12
2018-05-05 11:30 | 106.31 | 89.58
2018-05-05 12:00 | 108.79 | 92.03
2018-05-05 12:30 | 114.68 | 100.91
2018-05-05 13:00 | 109.54 | 92.28
2018-05-05 13:30 | 108.13 | 90.99
2018-05-05 14:00 | 105.3 | 88.49
2018-05-05 14:30 | 107.89 | 91.53
2018-05-05 15:00 | 106.93 | 90.3
2018-05-05 15:30 | 105.19 | 87.02
2018-05-05 16:00 | 109.86 | 93.35
2018-05-05 16:30 | 114.63 | 98.98
2018-05-05 17:00 | 115.47 | 98.9
2018-05-05 17:30 | 107.49 | 91.76
2018-05-05 18:00 | 106.96 | 90.98
2018-05-05 18:30 | 106.14 | 89.43
2018-05-05 19:00 | 115.15 | 99.84
2018-05-05 19:30 | 114.97 | 100.58
2018-05-05 20:00 | 112.66 | 95.63
2018-05-05 20:30 | 107.68 | 89.62
2018-05-05 21:00 | 108.76 | 90.77
2018-05-05 21:30 | 113.89 | 97.49
2018-05-05 22:00 | 110.49 | 94.42
2018-05-05 22:30 | 111.86 | 95.59
2018-05-05 23:00 | 115.15 | 98.08
2018-05-05 23:30 | 111.5 | 94.25
2018-05-06 | 116.61 | 99.8
2018-05-06 00:30 | 114.11 | 98.23
2018-05-06 01:00 | 111.02 | 92.38
2018-05-06 01:30 | 114.09 | 97.56
2018-05-06 02:00 | 117.16 | 101.08
2018-05-06 02:30 | 116.5 | 101
2018-05-06 03:00 | 111.34 | 93.28
2018-05-06 03:30 | 109.63 | 91.83
2018-05-06 04:00 | 108.83 | 90.48
2018-05-06 04:30 | 115.07 | 100.45
2018-05-06 05:00 | 106.36 | 91.23
2018-05-06 05:30 | 104.4 | 93.56
2018-05-06 06:00 | 110.71 | 95.33
2018-05-06 06:30 | 106.02 | 89.09
2018-05-06 07:00 | 105.55 | 85.83
2018-05-06 07:30 | 107.6 | 88.61
2018-05-06 08:00 | 111 | 93.12
2018-05-06 08:30 | 101.55 | 82.15
2018-05-06 09:00 | 106.25 | 87.34
2018-05-06 09:30 | 100.04 | 82.08
2018-05-06 10:00 | 102.22 | 84.57
2018-05-06 10:30 | 105.33 | 88.93
2018-05-06 11:00 | 103.74 | 87.38
2018-05-06 11:30 | 98.97 | 79.44
2018-05-06 12:00 | 99.88 | 82.23
2018-05-06 12:30 | 99.82 | 79.82
2018-05-06 13:00 | 103.51 | 85.22
2018-05-06 13:30 | 114.55 | 98.03
2018-05-06 14:00 | 112.87 | 94.34
2018-05-06 14:30 | 111.46 | 93.23
2018-05-06 15:00 | 110.49 | 92.06
2018-05-06 15:30 | 111.54 | 92.63
2018-05-06 16:00 | 109.26 | 91.13
2018-05-06 16:30 | 114.87 | 99.6
2018-05-06 17:00 | 120.2 | 103.77
2018-05-06 17:30 | 114.94 | 97.74
2018-05-06 18:00 | 113.03 | 95.73
2018-05-06 18:30 | 105.69 | 85.83
2018-05-06 19:00 | 110.36 | 93.11
2018-05-06 19:30 | 114.4 | 97.56
2018-05-06 20:00 | 116.47 | 100.32
2018-05-06 20:30 | 116.71 | 99.59
2018-05-06 21:00 | 115.92 | 97.74
2018-05-06 21:30 | 120.48 | 105.12
2018-05-06 22:00 | 117.47 | 99.61
2018-05-06 22:30 | 116.12 | 98.21
2018-05-06 23:00 | 114.02 | 94.91
2018-05-06 23:30 | 116.3 | 98.48
2018-05-07 | 114.91 | 95.91
2018-05-07 00:30 | 114.06 | 94.65
2018-05-07 01:00 | 114.9 | 97.18
2018-05-07 01:30 | 114.13 | 94.64
2018-05-07 02:00 | 116.64 | 97.42
2018-05-07 02:30 | 114.52 | 94.93
2018-05-07 03:00 | 118.62 | 101.4
2018-05-07 03:30 | 115.3 | 96.64
2018-05-07 04:00 | 119.73 | 104.11
2018-05-07 04:30 | 110.45 | 89.7
2018-05-07 05:00 | 113.66 | 95.42
2018-05-07 05:30 | 120.28 | 105.4
2018-05-07 06:00 | 114.92 | 95.37
2018-05-07 06:30 | 115.1 | 95.4
2018-05-07 07:00 | 117.82 | 99.2
2018-05-07 07:30 | 113.72 | 95.33
2018-05-07 08:00 | 106.1 | 86.25
2018-05-07 08:30 | 104.4 | 83.83
2018-05-07 09:00 | 111.33 | 92.07
2018-05-07 09:30 | 114 | 94.45
2018-05-07 10:00 | 117.48 | 100.46
2018-05-07 10:30 | 118 | 102.35
2018-05-07 11:00 | 108.24 | 87.52
2018-05-07 11:30 | 112.29 | 92.78
2018-05-07 12:00 | 112.23 | 94.1
2018-05-07 12:30 | 117.65 | 101.62
2018-05-07 13:00 | 122.48 | 106.92
2018-05-07 13:30 | 121.68 | 104.53
2018-05-07 14:00 | 119.09 | 102.49
2018-05-07 14:30 | 121.28 | 104.78
2018-05-07 15:00 | 120.57 | 104.5
2018-05-07 15:30 | 114.31 | 96.15
2018-05-07 16:00 | 117.18 | 99.96
2018-05-07 16:30 | 115.67 | 98.2
2018-05-07 17:00 | 112.28 | 94.33
2018-05-07 17:30 | 120.62 | 104.01
2018-05-07 18:00 | 120.39 | 104.29
2018-05-07 18:30 | 109.61 | 91.75
2018-05-07 19:00 | 109.58 | 92.7
2018-05-07 19:30 | 115.06 | 98.65
2018-05-07 20:00 | 120.66 | 104.77
2018-05-07 20:30 | 122.63 | 107.03
2018-05-07 21:00 | 121.77 | 104.7
2018-05-07 21:30 | 118.99 | 99.88
2018-05-07 22:00 | 118.9 | 98.48
2018-05-07 22:30 | 117.77 | 98.26
2018-05-07 23:00 | 119.4 | 102.2
2018-05-07 23:30 | 119.24 | 101.17
2018-05-08 | 119.05 | 100.55
2018-05-08 00:30 | 116.56 | 96.23
2018-05-08 01:00 | 121.32 | 103.83
2018-05-08 01:30 | 111.56 | 91.04
2018-05-08 02:00 | 109.25 | 87.97
2018-05-08 02:30 | 116.71 | 97.51
2018-05-08 03:00 | 113.25 | 92.79
2018-05-08 03:30 | 113.61 | 93.86
2018-05-08 04:00 | 115.53 | 96.97
2018-05-08 04:30 | 112.76 | 92.05
2018-05-08 05:00 | 109.86 | 88.66
2018-05-08 05:30 | 112.02 | 91.38
2018-05-08 06:00 | 109.53 | 87.06
2018-05-08 06:30 | 108.33 | 85.21
2018-05-08 07:00 | 110.21 | 89.97
2018-05-08 07:30 | 110.38 | 91.14
2018-05-08 08:00 | 113.1 | 95.34
2018-05-08 08:30 | 109.42 | 88.45
2018-05-08 09:00 | 110.65 | 89.8
2018-05-08 09:30 | 109.42 | 88.6
2018-05-08 10:00 | 111.32 | 91.33
2018-05-08 10:30 | 114.72 | 97.12
2018-05-08 11:00 | 115.44 | 95.43
2018-05-08 11:30 | 114.5 | 93.88
2018-05-08 12:00 | 111.4 | 91.26
2018-05-08 12:30 | 113.06 | 94.38
2018-05-08 13:00 | 109.45 | 89.64
2018-05-08 13:30 | 105.85 | 86.6
2018-05-08 14:00 | 111.76 | 93.74
2018-05-08 14:30 | 114.32 | 94.79
2018-05-08 15:00 | 115.11 | 95.81
2018-05-08 15:30 | 114.88 | 96.41
2018-05-08 16:00 | 117.48 | 101.22
2018-05-08 16:30 | 120.22 | 104.94
2018-05-08 17:00 | 117.83 | 100.67
2018-05-08 17:30 | 121.62 | 106.29
2018-05-08 18:00 | 118.43 | 102.31
2018-05-08 18:30 | 115.84 | 100.23
2018-05-08 19:00 | 120.95 | 105.56
2018-05-08 19:30 | 127.26 | 114.46
2018-05-08 20:00 | 129.91 | 116.66
2018-05-08 20:30 | 123.37 | 106.84
2018-05-08 21:00 | 124.51 | 110.02
2018-05-08 21:30 | 122.89 | 107.08
2018-05-08 22:00 | 120.4 | 103.89
2018-05-08 22:30 | 119.52 | 103.77
2018-05-08 23:00 | 112.08 | 91.74
2018-05-08 23:30 | 115.67 | 94.12
2018-05-09 | 118.05 | 98.94
2018-05-09 00:30 | 117.33 | 97.86
2018-05-09 01:00 | 118.03 | 98.72
2018-05-09 01:30 | 115.14 | 95.03
2018-05-09 02:00 | 115.76 | 96.22
2018-05-09 02:30 | 116.51 | 96.39
2018-05-09 03:00 | 120.09 | 100.3
2018-05-09 03:30 | 115.47 | 94.33
2018-05-09 04:00 | 116.94 | 96.39
2018-05-09 04:30 | 119.94 | 99.38
2018-05-09 05:00 | 118.01 | 98.42
2018-05-09 05:30 | 117.47 | 96.87
2018-05-09 06:00 | 121.35 | 102.37
2018-05-09 06:30 | 112.58 | 90.65
2018-05-09 07:00 | 114.43 | 93.24
2018-05-09 07:30 | 114.62 | 95.49
2018-05-09 08:00 | 113.94 | 93.92
2018-05-09 08:30 | 112.38 | 93.11
2018-05-09 09:00 | 113.55 | 92
2018-05-09 09:30 | 113.75 | 92.33
2018-05-09 10:00 | 108.14 | 85.79
2018-05-09 10:30 | 110.13 | 88.01
2018-05-09 11:00 | 111.01 | 89.03
2018-05-09 11:30 | 114.18 | 91.39
2018-05-09 12:00 | 115.39 | 92.82
2018-05-09 12:30 | 115.64 | 93.97
2018-05-09 13:00 | 117.24 | 96.26
2018-05-09 13:30 | 114.75 | 94.63
2018-05-09 14:00 | 111.93 | 92.65
2018-05-09 14:30 | 114.2 | 95.13
2018-05-09 15:00 | 119.89 | 102.54
2018-05-09 15:30 | 114.28 | 94.23
2018-05-09 16:00 | 112.28 | 91.7
2018-05-09 16:30 | 111.53 | 91.93
2018-05-09 17:00 | 114.38 | 97.6
2018-05-09 17:30 | 117.59 | 102.45
2018-05-09 18:00 | 116.26 | 99.73
2018-05-09 18:30 | 116.11 | 100
2018-05-09 19:00 | 115.54 | 100.46
2018-05-09 19:30 | 114.31 | 98.21
2018-05-09 20:00 | 114.14 | 96.56
2018-05-09 20:30 | 113.81 | 96.2
2018-05-09 21:00 | 113.64 | 95.42
2018-05-09 21:30 | 111.95 | 92.53
2018-05-09 22:00 | 118.49 | 101.21
2018-05-09 22:30 | 118.84 | 100.07
2018-05-09 23:00 | 122.51 | 102.88
2018-05-09 23:30 | 114.8 | 92.42
2018-05-10 | 118.21 | 96.04
2018-05-10 00:30 | 116.5 | 94.81
2018-05-10 01:00 | 113.98 | 90.41
2018-05-10 01:30 | 113.31 | 91.51
2018-05-10 02:00 | 110.27 | 88.07
2018-05-10 02:30 | 110.78 | 91.47
2018-05-10 03:00 | 112.3 | 93.03
2018-05-10 03:30 | 112.79 | 90.83
2018-05-10 04:00 | 115.91 | 97.24
2018-05-10 04:30 | 123.37 | 107.48
2018-05-10 05:00 | 117.94 | 99.84
2018-05-10 05:30 | 119.06 | 101.09
2018-05-10 06:00 | 116.93 | 98.79
2018-05-10 06:30 | 112.26 | 89.99
2018-05-10 07:00 | 116.31 | 98.02
2018-05-10 07:30 | 113.57 | 95.79
2018-05-10 08:00 | 109.07 | 88.31
2018-05-10 08:30 | 106.47 | 85.66
2018-05-10 09:00 | 111.59 | 91.95
2018-05-10 09:30 | 114.92 | 96.4
2018-05-10 10:00 | 106.89 | 86.17
2018-05-10 10:30 | 116.77 | 96.43
2018-05-10 11:00 | 120.84 | 103.43
2018-05-10 11:30 | 111.36 | 88.02
2018-05-10 12:00 | 109.4 | 85.68
2018-05-10 12:30 | 107.39 | 82.98
2018-05-10 13:00 | 110.18 | 87.43
2018-05-10 13:30 | 109.82 | 89.46
2018-05-10 14:00 | 105.88 | 84.3
2018-05-10 14:30 | 111.16 | 91.06
2018-05-10 15:00 | 111.05 | 90.16
2018-05-10 15:30 | 108.6 | 86.97
2018-05-10 16:00 | 112.56 | 92.55
2018-05-10 16:30 | 111.49 | 93.01
2018-05-10 17:00 | 115.63 | 96.04
2018-05-10 17:30 | 119.8 | 102.09
2018-05-10 18:00 | 117.09 | 100.16
2018-05-10 18:30 | 111.2 | 92.03
2018-05-10 19:00 | 115.05 | 99.24
2018-05-10 19:30 | 116.68 | 99.68
2018-05-10 20:00 | 118.19 | 103
2018-05-10 20:30 | 115.6 | 97.03
2018-05-10 21:00 | 115.67 | 95.54
2018-05-10 21:30 | 111.28 | 90.12
2018-05-10 22:00 | 111.36 | 89.7
2018-05-10 22:30 | 113.56 | 93.32
2018-05-10 23:00 | 112.54 | 92.29
2018-05-10 23:30 | 110.46 | 88.77
2018-05-11 | 110.91 | 89.3
2018-05-11 00:30 | 110.45 | 89.04
2018-05-11 01:00 | 111.23 | 89.99
2018-05-11 01:30 | 112.13 | 92.03
2018-05-11 02:00 | 114.75 | 95.22
2018-05-11 02:30 | 112.9 | 91.78
2018-05-11 03:00 | 115.82 | 96.46
2018-05-11 03:30 | 106.5 | 83.84
2018-05-11 04:00 | 105.24 | 83.91
2018-05-11 04:30 | 109.51 | 89.84
2018-05-11 05:00 | 109.61 | 89.45
2018-05-11 05:30 | 115.2 | 97.79
2018-05-11 06:00 | 109.36 | 89.76
2018-05-11 06:30 | 108.83 | 87.09
2018-05-11 07:00 | 103.67 | 85.12
2018-05-11 07:30 | 102.55 | 82.54
2018-05-11 08:00 | 100.45 | 79.83
2018-05-11 08:30 | 107.39 | 87.5
2018-05-11 09:00 | 106.44 | 83.6
2018-05-11 09:30 | 105.23 | 83.53
2018-05-11 10:00 | 98.46 | 84.62
2018-05-11 10:30 | 109.35 | 91.54
2018-05-11 11:00 | 115.8 | 99.38
2018-05-11 11:30 | 109.29 | 89.25
2018-05-11 12:00 | 111.54 | 96.34
2018-05-11 12:30 | 108.88 | 90.43
2018-05-11 13:00 | 108.43 | 88.69
2018-05-11 13:30 | 112.25 | 95.49
2018-05-11 14:00 | 116.3 | 100.88
2018-05-11 14:30 | 112.54 | 95.08
2018-05-11 15:00 | 107.97 | 88.58
2018-05-11 15:30 | 105.5 | 88.37
2018-05-11 16:00 | 99.59 | 78.5
2018-05-11 16:30 | 97.07 | 77.48
2018-05-11 17:00 | 102.93 | 85.04
2018-05-11 17:30 | 106.9 | 88.08
2018-05-11 18:00 | 113.23 | 95.77
2018-05-11 18:30 | 105.54 | 86.21
2018-05-11 19:00 | 108.89 | 91.07
2018-05-11 19:30 | 110.65 | 93.85
2018-05-11 20:00 | 115.17 | 98.75
2018-05-11 20:30 | 110.67 | 91.62
2018-05-11 21:00 | 111.77 | 93.79
2018-05-11 21:30 | 112.2 | 93.14
2018-05-11 22:00 | 110.29 | 90.27
2018-05-11 22:30 | 109.26 | 88.04
2018-05-11 23:00 | 104.28 | 80.15
2018-05-11 23:30 | 107.26 | 84.97
2018-05-12 | 111.29 | 92.47
2018-05-12 00:30 | 108.6 | 95.25
2018-05-12 01:00 | 106.04 | 93.2
2018-05-12 01:30 | 105.41 | 91.54
2018-05-12 02:00 | 107.2 | 93.59
2018-05-12 02:30 | 101.21 | 87.42
2018-05-12 03:00 | 102.92 | 90.31
2018-05-12 03:30 | 98.12 | 84.74
2018-05-12 04:00 | 101.67 | 89.18
2018-05-12 04:30 | 106.18 | 94.24
2018-05-12 05:00 | 107.16 | 95.08
2018-05-12 05:30 | 101.12 | 87.33
2018-05-12 06:00 | 98.01 | 83.14
2018-05-12 06:30 | 92.88 | 76.07
2018-05-12 07:00 | 98.63 | 85.12
2018-05-12 07:30 | 96.94 | 81.93
2018-05-12 08:00 | 104.93 | 91.19
2018-05-12 08:30 | 103.53 | 89.64
2018-05-12 09:00 | 102.63 | 87.42
2018-05-12 09:30 | 101.79 | 85.17
2018-05-12 10:00 | 101.19 | 84.11
2018-05-12 10:30 | 99.94 | 83.12
2018-05-12 11:00 | 100.74 | 86.41
2018-05-12 11:30 | 101.31 | 86.6
2018-05-12 12:00 | 109.14 | 95.19
2018-05-12 12:30 | 107.26 | 92.63
2018-05-12 13:00 | 103.94 | 89.15
2018-05-12 13:30 | 109.46 | 97.09
2018-05-12 14:00 | 114.1 | 101.5
2018-05-12 14:30 | 111.95 | 98.4
2018-05-12 15:00 | 110.07 | 96.6
2018-05-12 15:30 | 109.36 | 96.61
2018-05-12 16:00 | 101.74 | 88.08
2018-05-12 16:30 | 103.97 | 91.19
2018-05-12 17:00 | 114.27 | 103.5
2018-05-12 17:30 | 101.26 | 88.24
2018-05-12 18:00 | 102.78 | 90.02
2018-05-12 18:30 | 108.57 | 95.27
2018-05-12 19:00 | 102.58 | 88.55
2018-05-12 19:30 | 105.65 | 93.2
2018-05-12 20:00 | 106.08 | 92.74
2018-05-12 20:30 | 108.21 | 95.86
2018-05-12 21:00 | 109.49 | 96.33
2018-05-12 21:30 | 105.67 | 91.75
2018-05-12 22:00 | 109.9 | 97.55
2018-05-12 22:30 | 105.44 | 91.72
2018-05-12 23:00 | 105.2 | 91.44
2018-05-12 23:30 | 108.05 | 94.04
2018-05-13 | 106.95 | 92.43
2018-05-13 00:30 | 105.25 | 91.77
2018-05-13 01:00 | 107.67 | 94.95
2018-05-13 01:30 | 102.85 | 89.85
2018-05-13 02:00 | 106.16 | 93.64
2018-05-13 02:30 | 103.5 | 90.21
2018-05-13 03:00 | 100.8 | 86.79
2018-05-13 03:30 | 102.9 | 88.4
2018-05-13 04:00 | 104.95 | 91.55
2018-05-13 04:30 | 104.17 | 91.23
2018-05-13 05:00 | 103.58 | 90.65
2018-05-13 05:30 | 109 | 97.2
2018-05-13 06:00 | 109.96 | 98.25
2018-05-13 06:30 | 103.96 | 91.5
2018-05-13 07:00 | 101.93 | 89.74
2018-05-13 07:30 | 107.74 | 95.67
2018-05-13 08:00 | 110.5 | 98.18
2018-05-13 08:30 | 108 | 95.41
2018-05-13 09:00 | 107.81 | 94.21
2018-05-13 09:30 | 102.16 | 89.74
2018-05-13 10:00 | 104.15 | 91.16
2018-05-13 10:30 | 99.83 | 83.66
2018-05-13 11:00 | 105.61 | 90.62
2018-05-13 11:30 | 97.72 | 81.5
2018-05-13 12:00 | 103.53 | 88.71
2018-05-13 12:30 | 98.02 | 82.74
2018-05-13 13:00 | 101.84 | 88.6
2018-05-13 13:30 | 102.24 | 88.59
2018-05-13 14:00 | 109.77 | 97.75
2018-05-13 14:30 | 106.36 | 94.36
2018-05-13 15:00 | 99.96 | 86.29
2018-05-13 15:30 | 99.4 | 86.17
2018-05-13 16:00 | 107.89 | 95.92
2018-05-13 16:30 | 96.54 | 82.4
2018-05-13 17:00 | 100.99 | 90.04
2018-05-13 17:30 | 104.49 | 93.72
2018-05-13 18:00 | 103.05 | 89.87
2018-05-13 18:30 | 104.57 | 91.41
2018-05-13 19:00 | 96.36 | 81.9
2018-05-13 19:30 | 104.23 | 92.71
2018-05-13 20:00 | 107.18 | 96.6
2018-05-13 20:30 | 108 | 96.83
2018-05-13 21:00 | 109.94 | 98.59
2018-05-13 21:30 | 112.28 | 99.79
2018-05-13 22:00 | 110.98 | 97.99
2018-05-13 22:30 | 112.89 | 101.18
2018-05-13 23:00 | 104 | 90.5
2018-05-13 23:30 | 106.12 | 92
2018-05-14 | 104.62 | 89.7
2018-05-14 00:30 | 104.74 | 90.12
2018-05-14 01:00 | 107.28 | 94.37
2018-05-14 01:30 | 103.44 | 88.75
2018-05-14 02:00 | 101.17 | 85.54
2018-05-14 02:30 | 105.25 | 90.49
2018-05-14 03:00 | 104.31 | 90.15
2018-05-14 03:30 | 97.25 | 81.03
2018-05-14 04:00 | 106.4 | 93.99
2018-05-14 04:30 | 104.25 | 91.45
2018-05-14 05:00 | 105.79 | 94.22
2018-05-14 05:30 | 103.98 | 91.08
2018-05-14 06:00 | 103.15 | 89.31
2018-05-14 06:30 | 99.88 | 85.87
2018-05-14 07:00 | 100.42 | 87.89
2018-05-14 07:30 | 101.57 | 89.05
2018-05-14 08:00 | 94.95 | 81.37
2018-05-14 08:30 | 101.74 | 88.95
2018-05-14 09:00 | 95.69 | 80
2018-05-14 09:30 | 97.96 | 82.31
2018-05-14 10:00 | 96.57 | 81.5
2018-05-14 10:30 | 93.22 | 77.48
2018-05-14 11:00 | 90.58 | 73.75
2018-05-14 11:30 | 95.6 | 79
2018-05-14 12:00 | 97.02 | 79.47
2018-05-14 12:30 | 103.34 | 87.98
2018-05-14 13:00 | 105.74 | 92.05
2018-05-14 13:30 | 109.94 | 96.38
2018-05-14 14:00 | 110.97 | 98.1
2018-05-14 14:30 | 110.26 | 97.03
2018-05-14 15:00 | 105.74 | 90.92
2018-05-14 15:30 | 105.36 | 91.3
2018-05-14 16:00 | 106.81 | 92.8
2018-05-14 16:30 | 108.46 | 95.95
2018-05-14 17:00 | 114.35 | 102.28
2018-05-14 17:30 | 107.51 | 94.96
2018-05-14 18:00 | 112.22 | 101.08
2018-05-14 18:30 | 112.71 | 100.94
2018-05-14 19:00 | 106.35 | 94.39
2018-05-14 19:30 | 108.93 | 97.71
2018-05-14 20:00 | 109.64 | 97.58
2018-05-14 20:30 | 116.48 | 104.87
2018-05-14 21:00 | 108.99 | 96.96
2018-05-14 21:30 | 102.77 | 90.54
2018-05-14 22:00 | 105.07 | 93.26
2018-05-14 22:30 | 104.89 | 93.01
2018-05-14 23:00 | 101.76 | 88.26
2018-05-14 23:30 | 108.02 | 95.54
2018-05-15 | 108.64 | 96.52
2018-05-15 00:30 | 107.99 | 95.43
2018-05-15 01:00 | 106.46 | 92.87
2018-05-15 01:30 | 105.49 | 92.16
2018-05-15 02:00 | 101.06 | 86.48
2018-05-15 02:30 | 101.54 | 86.67
2018-05-15 03:00 | 101.43 | 86.69
2018-05-15 03:30 | 97.72 | 81.08
2018-05-15 04:00 | 99.41 | 82.9
2018-05-15 04:30 | 97.85 | 80.63
2018-05-15 05:00 | 98.13 | 81.5
2018-05-15 05:30 | 100.04 | 84.55
2018-05-15 06:00 | 100.86 | 86.23
2018-05-15 06:30 | 94.04 | 76.93
2018-05-15 07:00 | 98.14 | 82.31
2018-05-15 07:30 | 98.78 | 82.26
2018-05-15 08:00 | 95.17 | 76.79
2018-05-15 08:30 | 99.82 | 82.58
2018-05-15 09:00 | 101.05 | 85.37
2018-05-15 09:30 | 96.43 | 78.33
2018-05-15 10:00 | 97.59 | 79.61
2018-05-15 10:30 | 96.58 | 78.55
2018-05-15 11:00 | 100.97 | 82.53
2018-05-15 11:30 | 98.68 | 79.21
2018-05-15 12:00 | 102.28 | 85.34
2018-05-15 12:30 | 98.42 | 79.72
2018-05-15 13:00 | 107.39 | 92.87
2018-05-15 13:30 | 105.07 | 88.7
2018-05-15 14:00 | 103.33 | 86.06
2018-05-15 14:30 | 100.51 | 84.06
2018-05-15 15:00 | 95.21 | 76.83
2018-05-15 15:30 | 91.28 | 71.66
2018-05-15 16:00 | 96.44 | 77.72
2018-05-15 16:30 | 96.58 | 77.58
2018-05-15 17:00 | 98.98 | 83.05
2018-05-15 17:30 | 101.54 | 86.53
2018-05-15 18:00 | 98.84 | 82.77
2018-05-15 18:30 | 99.25 | 84.61
2018-05-15 19:00 | 99.92 | 86.2
2018-05-15 19:30 | 98.42 | 85.79
2018-05-15 20:00 | 99.35 | 85.97
2018-05-15 20:30 | 99.21 | 85.74
2018-05-15 21:00 | 93.82 | 81.44
2018-05-15 21:30 | 95.46 | 82.37
2018-05-15 22:00 | 93.7 | 79.2
2018-05-15 22:30 | 95.57 | 81.06
2018-05-15 23:00 | 94.14 | 78.33
2018-05-15 23:30 | 101.1 | 87.04
2018-05-16 | 100.15 | 85.48
2018-05-16 00:30 | 101.04 | 85.92
2018-05-16 01:00 | 108.9 | 97.67
2018-05-16 01:30 | 103.82 | 89.84
2018-05-16 02:00 | 103.01 | 89.14
2018-05-16 02:30 | 98.35 | 84.16
2018-05-16 03:00 | 92.66 | 74.88
2018-05-16 03:30 | 95.63 | 79.77
2018-05-16 04:00 | 95.11 | 78.78
2018-05-16 04:30 | 94.95 | 77.93
2018-05-16 05:00 | 97.08 | 82.2
2018-05-16 05:30 | 91.74 | 74.43
2018-05-16 06:00 | 94.36 | 77.69
2018-05-16 06:30 | 82.51 | 62.58
2018-05-16 07:00 | 91.01 | 73.14
2018-05-16 07:30 | 86.57 | 68.38
2018-05-16 08:00 | 91.45 | 72.54
2018-05-16 08:30 | 91.31 | 72.7
2018-05-16 09:00 | 89.1 | 70.05
2018-05-16 09:30 | 87.89 | 68.04
2018-05-16 10:00 | 82.94 | 61.79
2018-05-16 10:30 | 87.5 | 68.33
2018-05-16 11:00 | 86.49 | 66.05
2018-05-16 11:30 | 81.93 | 56.78
2018-05-16 12:00 | 80.61 | 55.68
2018-05-16 12:30 | 79.6 | 54.37
2018-05-16 13:00 | 81.88 | 57.88
2018-05-16 13:30 | 80.84 | 57.89
2018-05-16 14:00 | 78.18 | 54.67
2018-05-16 14:30 | 79.32 | 56.6
2018-05-16 15:00 | 80.37 | 56.66
2018-05-16 15:30 | 78.64 | 55.52
2018-05-16 16:00 | 84.78 | 65.16
2018-05-16 16:30 | 89.17 | 72.87
2018-05-16 17:00 | 89.39 | 72.32
2018-05-16 17:30 | 94.17 | 79.75
2018-05-16 18:00 | 94.96 | 80.87
2018-05-16 18:30 | 89.32 | 73.54
2018-05-16 19:00 | 96.29 | 83.07
2018-05-16 19:30 | 100.05 | 86.7
2018-05-16 20:00 | 93.28 | 77.76
2018-05-16 20:30 | 98.94 | 84.56
2018-05-16 21:00 | 99.67 | 85.88
2018-05-16 21:30 | 96.83 | 80.59
2018-05-16 22:00 | 91.86 | 75.9
2018-05-16 22:30 | 93.77 | 78.78
2018-05-16 23:00 | 95.14 | 77.15
2018-05-16 23:30 | 92.79 | 76.01
2018-05-17 | 96.74 | 80.18
2018-05-17 00:30 | 102.68 | 89.06
2018-05-17 01:00 | 97.03 | 81.48
2018-05-17 01:30 | 97.89 | 81.62
2018-05-17 02:00 | 98.24 | 83.2
2018-05-17 02:30 | 97.26 | 81.12
2018-05-17 03:00 | 95.73 | 79.92
2018-05-17 03:30 | 92.51 | 76.88
2018-05-17 04:00 | 99.25 | 86.24
2018-05-17 04:30 | 97.55 | 83.63
2018-05-17 05:00 | 101.07 | 87.4
2018-05-17 05:30 | 104.98 | 91.76
2018-05-17 06:00 | 103.32 | 89.45
2018-05-17 06:30 | 99.5 | 85.69
2018-05-17 07:00 | 97.03 | 83.32
2018-05-17 07:30 | 99.19 | 85.36
2018-05-17 08:00 | 99.58 | 87.85
2018-05-17 08:30 | 103.87 | 92.44
2018-05-17 09:00 | 95.4 | 80.34
2018-05-17 09:30 | 93.36 | 77.1
2018-05-17 10:00 | 93.94 | 78.38
2018-05-17 10:30 | 87.78 | 69.29
2018-05-17 11:00 | 88.65 | 68.26
2018-05-17 11:30 | 92.06 | 73.27
2018-05-17 12:00 | 92.27 | 74.34
2018-05-17 12:30 | 94.15 | 76.87
2018-05-17 13:00 | 95.16 | 78.68
2018-05-17 13:30 | 92.07 | 74.33
2018-05-17 14:00 | 96.34 | 80.58
2018-05-17 14:30 | 96.87 | 83.16
2018-05-17 15:00 | 98.98 | 83.8
2018-05-17 15:30 | 93.82 | 77.28
2018-05-17 16:00 | 97.97 | 81.52
2018-05-17 16:30 | 91.85 | 76.22
2018-05-17 17:00 | 88.22 | 71.55
2018-05-17 17:30 | 93.08 | 78.85
2018-05-17 18:00 | 93.15 | 80.87
2018-05-17 18:30 | 84.79 | 68.45
2018-05-17 19:00 | 93.83 | 80.15
2018-05-17 19:30 | 87.78 | 75.34
2018-05-17 20:00 | 90.7 | 77.9
2018-05-17 20:30 | 94.01 | 81.58
2018-05-17 21:00 | 95.4 | 82.96
2018-05-17 21:30 | 89.36 | 71.59
2018-05-17 22:00 | 87.67 | 70.21
2018-05-17 22:30 | 85.15 | 68.12
2018-05-17 23:00 | 83.31 | 64.35
2018-05-17 23:30 | 81.51 | 61.06
2018-05-18 | 84.35 | 64.89
2018-05-18 00:30 | 83.35 | 67.43
2018-05-18 01:00 | 79.04 | 61.36
2018-05-18 01:30 | 78.97 | 60.9
2018-05-18 02:00 | 82.39 | 63.39
2018-05-18 02:30 | 85.83 | 69.3
2018-05-18 03:00 | 90.6 | 76.8
2018-05-18 03:30 | 93.49 | 80.04
2018-05-18 04:00 | 90.3 | 75.17
2018-05-18 04:30 | 89.25 | 73.71
2018-05-18 05:00 | 89.56 | 74.53
2018-05-18 05:30 | 87.97 | 74.89
2018-05-18 06:00 | 92.96 | 80.83
2018-05-18 06:30 | 90.11 | 78.22
2018-05-18 07:00 | 98.14 | 86.94
2018-05-18 07:30 | 94.52 | 81.74
2018-05-18 08:00 | 100.55 | 89.06
2018-05-18 08:30 | 97.71 | 85.44
2018-05-18 09:00 | 94.01 | 80.12
2018-05-18 09:30 | 91.88 | 78.5
2018-05-18 10:00 | 95.45 | 82.6
2018-05-18 10:30 | 87.15 | 72.57
2018-05-18 11:00 | 82.97 | 66.89
2018-05-18 11:30 | 88.2 | 74.52
2018-05-18 12:00 | 88.08 | 73.05
2018-05-18 12:30 | 92.47 | 76.98
2018-05-18 13:00 | 100.61 | 88.1
2018-05-18 13:30 | 90.38 | 73.98
2018-05-18 14:00 | 93.46 | 77.88
2018-05-18 14:30 | 98.73 | 84.52
2018-05-18 15:00 | 95.93 | 82.17
2018-05-18 15:30 | 99.17 | 85.71
2018-05-18 16:00 | 100.77 | 87.89
2018-05-18 16:30 | 94.32 | 81.24
2018-05-18 17:00 | 97.35 | 85.64
2018-05-18 17:30 | 96.64 | 83.09
2018-05-18 18:00 | 105.64 | 92.69
2018-05-18 18:30 | 92.14 | 77.12
2018-05-18 19:00 | 99.45 | 85.24
2018-05-18 19:30 | 98.77 | 85.21
2018-05-18 20:00 | 104.93 | 91.52
2018-05-18 20:30 | 94.45 | 81
2018-05-18 21:00 | 100.98 | 88.16
2018-05-18 21:30 | 96.18 | 82.22
2018-05-18 22:00 | 104.31 | 90.7
2018-05-18 22:30 | 109.03 | 95.66
2018-05-18 23:00 | 96.81 | 81.6
2018-05-18 23:30 | 102.35 | 88.45
2018-05-19 | 100.46 | 86.91
2018-05-19 00:30 | 98.86 | 84.77
2018-05-19 01:00 | 109.78 | 98.15
2018-05-19 01:30 | 101.12 | 88.57
2018-05-19 02:00 | 102.01 | 88.78
2018-05-19 02:30 | 98.63 | 83.94
2018-05-19 03:00 | 94.41 | 78.52
2018-05-19 03:30 | 94.61 | 78.79
2018-05-19 04:00 | 96.15 | 80.23
2018-05-19 04:30 | 98.06 | 84.25
2018-05-19 05:00 | 96.49 | 81.7
2018-05-19 05:30 | 101.22 | 88.83
2018-05-19 06:00 | 95.12 | 81.33
2018-05-19 06:30 | 88.86 | 72.5
2018-05-19 07:00 | 97.14 | 83.42
2018-05-19 07:30 | 96.13 | 81.78
2018-05-19 08:00 | 98.09 | 84.95
2018-05-19 08:30 | 94.07 | 78.13
2018-05-19 09:00 | 95.25 | 79.28
2018-05-19 09:30 | 98.1 | 84.29
2018-05-19 10:00 | 94.13 | 76.54
2018-05-19 10:30 | 96.34 | 82.53
2018-05-19 11:00 | 105.51 | 91.86
2018-05-19 11:30 | 105.82 | 91.35
2018-05-19 12:00 | 103.07 | 88.59
2018-05-19 12:30 | 94.84 | 80.8
2018-05-19 13:00 | 89.68 | 75.03
2018-05-19 13:30 | 93.3 | 78.6
2018-05-19 14:00 | 95.01 | 80.92
2018-05-19 14:30 | 103.78 | 90.49
2018-05-19 15:00 | 97.24 | 82.94
2018-05-19 15:30 | 99.19 | 85.54
2018-05-19 16:00 | 104.87 | 92.21
2018-05-19 16:30 | 101.75 | 88.44
2018-05-19 17:00 | 104.84 | 90.39
2018-05-19 17:30 | 107 | 93.95
2018-05-19 18:00 | 100.78 | 87.31
2018-05-19 18:30 | 98.77 | 84.56
2018-05-19 19:00 | 97.64 | 83.7
2018-05-19 19:30 | 103.61 | 89.13
2018-05-19 20:00 | 107.17 | 94.24
2018-05-19 20:30 | 104.06 | 90.56
2018-05-19 21:00 | 106.54 | 93.1
2018-05-19 21:30 | 104.86 | 91.6
2018-05-19 22:00 | 106.78 | 93.11
2018-05-19 22:30 | 108.61 | 95.91
2018-05-19 23:00 | 108.28 | 94.82
2018-05-19 23:30 | 112.59 | 99.24
2018-05-20 | 114.69 | 102.78
2018-05-20 00:30 | 112.55 | 100.04
2018-05-20 01:00 | 110.19 | 97.92
2018-05-20 01:30 | 100.28 | 86.78
2018-05-20 02:00 | 94.57 | 79.21
2018-05-20 02:30 | 97.45 | 83.48
2018-05-20 03:00 | 104.09 | 91.02
2018-05-20 03:30 | 107.17 | 94.64
2018-05-20 04:00 | 103.47 | 90.4
2018-05-20 04:30 | 108.04 | 96.01
2018-05-20 05:00 | 109.86 | 98.15
2018-05-20 05:30 | 99.75 | 85.41
2018-05-20 06:00 | 105.32 | 92.64
2018-05-20 06:30 | 95.14 | 79.79
2018-05-20 07:00 | 101.18 | 87.85
2018-05-20 07:30 | 101.35 | 88.09
2018-05-20 08:00 | 100.4 | 87.24
2018-05-20 08:30 | 110.65 | 97.69
2018-05-20 09:00 | 98.73 | 84.2
2018-05-20 09:30 | 104.52 | 90.91
2018-05-20 10:00 | 108.91 | 96.67
2018-05-20 10:30 | 104.27 | 90.23
2018-05-20 11:00 | 102.46 | 88.28
2018-05-20 11:30 | 106.79 | 92.8
2018-05-20 12:00 | 101.21 | 85.98
2018-05-20 12:30 | 97.7 | 82.73
2018-05-20 13:00 | 95.05 | 79.05
2018-05-20 13:30 | 93.78 | 78.9
2018-05-20 14:00 | 99.67 | 85.07
2018-05-20 14:30 | 105.91 | 94.04
2018-05-20 15:00 | 99.69 | 87.26
2018-05-20 15:30 | 100.06 | 86.26
2018-05-20 16:00 | 99.12 | 86.78
2018-05-20 16:30 | 93.62 | 81.3
2018-05-20 17:00 | 102.14 | 88.85
2018-05-20 17:30 | 106.53 | 93.67
2018-05-20 18:00 | 105.59 | 93.1
2018-05-20 18:30 | 99.21 | 85.61
2018-05-20 19:00 | 104.52 | 92.25
2018-05-20 19:30 | 105.73 | 93.08
2018-05-20 20:00 | 102.86 | 90.06
2018-05-20 20:30 | 103.45 | 90.71
2018-05-20 21:00 | 110.5 | 98.17
2018-05-20 21:30 | 110.83 | 98.26
2018-05-20 22:00 | 107.63 | 94.24
2018-05-20 22:30 | 102.42 | 88.78
2018-05-20 23:00 | 105.02 | 90.81
2018-05-20 23:30 | 105.35 | 91.25
2018-05-21 | 103.24 | 89.25
2018-05-21 00:30 | 108.29 | 94.27
2018-05-21 01:00 | 104.15 | 89.37
2018-05-21 01:30 | 102.94 | 88.12
2018-05-21 02:00 | 101.89 | 86.78
2018-05-21 02:30 | 109.26 | 95.16
2018-05-21 03:00 | 105.89 | 91.32
2018-05-21 03:30 | 101.17 | 86.8
2018-05-21 04:00 | 100.22 | 86.17
2018-05-21 04:30 | 97.54 | 83.46
2018-05-21 05:00 | 102.89 | 90.45
2018-05-21 05:30 | 104.25 | 91.98
2018-05-21 06:00 | 100.65 | 87.56
2018-05-21 06:30 | 94.87 | 81.37
2018-05-21 07:00 | 100.82 | 88.73
2018-05-21 07:30 | 103.07 | 91.22
2018-05-21 08:00 | 100.99 | 89.37
2018-05-21 08:30 | 99.61 | 87.64
2018-05-21 09:00 | 98.32 | 85.2
2018-05-21 09:30 | 101.02 | 88.27
2018-05-21 10:00 | 101.73 | 89
2018-05-21 10:30 | 95.07 | 80.23
2018-05-21 11:00 | 93.99 | 79.52
2018-05-21 11:30 | 94.11 | 80.2
2018-05-21 12:00 | 99.26 | 86.16
2018-05-21 12:30 | 105.28 | 91.89
2018-05-21 13:00 | 106.21 | 92.16
2018-05-21 13:30 | 113.13 | 99.82
2018-05-21 14:00 | 106.76 | 92.55
2018-05-21 14:30 | 105.84 | 91.67
2018-05-21 15:00 | 103.53 | 88.85
2018-05-21 15:30 | 104.73 | 90.81
2018-05-21 16:00 | 105.79 | 91.57
2018-05-21 16:30 | 106.77 | 93.62
2018-05-21 17:00 | 106.3 | 93.68
2018-05-21 17:30 | 105.38 | 93.33
2018-05-21 18:00 | 109.88 | 96.96
2018-05-21 18:30 | 103.87 | 87.97
2018-05-21 19:00 | 116.01 | 102.1
2018-05-21 19:30 | 114.35 | 99.67
2018-05-21 20:00 | 111.07 | 95.65
2018-05-21 20:30 | 115.62 | 99.81
2018-05-21 21:00 | 107.34 | 90.73
2018-05-21 21:30 | 109.82 | 92.69
2018-05-21 22:00 | 106.16 | 90.18
2018-05-21 22:30 | 107.54 | 92.02
2018-05-21 23:00 | 114.26 | 99.54
2018-05-21 23:30 | 106.54 | 90.61
2018-05-22 | 107.84 | 92.94
2018-05-22 00:30 | 112.21 | 97.47
2018-05-22 01:00 | 115.44 | 101.29
2018-05-22 01:30 | 100.39 | 85.65
2018-05-22 02:00 | 106.91 | 91.84
2018-05-22 02:30 | 109.57 | 96.1
2018-05-22 03:00 | 104.6 | 90
2018-05-22 03:30 | 97.24 | 82.31
2018-05-22 04:00 | 106.59 | 92.81
2018-05-22 04:30 | 98.38 | 84.26
2018-05-22 05:00 | 96.33 | 82.7
2018-05-22 05:30 | 90.26 | 75.9
2018-05-22 06:00 | 89.04 | 74.86
2018-05-22 06:30 | 87.2 | 72.32
2018-05-22 07:00 | 93.94 | 80.9
2018-05-22 07:30 | 90.82 | 77.66
2018-05-22 08:00 | 87.92 | 73.96
2018-05-22 08:30 | 89.47 | 74.15
2018-05-22 09:00 | 87.57 | 72.61
2018-05-22 09:30 | 89.4 | 75.24
2018-05-22 10:00 | 85.41 | 70.34
2018-05-22 10:30 | 85.07 | 69.74
2018-05-22 11:00 | 89.64 | 74.23
2018-05-22 11:30 | 90.97 | 74.57
2018-05-22 12:00 | 92.57 | 77.45
2018-05-22 12:30 | 95 | 79.56
2018-05-22 13:00 | 97.46 | 82.43
2018-05-22 13:30 | 96.24 | 80.67
2018-05-22 14:00 | 90.47 | 74.18
2018-05-22 14:30 | 94.58 | 81.42
2018-05-22 15:00 | 95.67 | 83.49
2018-05-22 15:30 | 98.82 | 86.91
2018-05-22 16:00 | 99.14 | 86.78
2018-05-22 16:30 | 106.27 | 94.14
2018-05-22 17:00 | 109.08 | 97
2018-05-22 17:30 | 107.43 | 95.05
2018-05-22 18:00 | 109.64 | 98.36
2018-05-22 18:30 | 103.78 | 91.3
2018-05-22 19:00 | 107.96 | 96.7
2018-05-22 19:30 | 107.26 | 96.09
2018-05-22 20:00 | 106.4 | 94.9
2018-05-22 20:30 | 111.02 | 99.73
2018-05-22 21:00 | 116.21 | 104.08
2018-05-22 21:30 | 118.36 | 106.74
2018-05-22 22:00 | 121.06 | 108.86
2018-05-22 22:30 | 115.62 | 103.14
2018-05-22 23:00 | 106.97 | 94.83
2018-05-22 23:30 | 101.73 | 89.65
2018-05-23 | 100.51 | 87.69
2018-05-23 00:30 | 105.74 | 93.96
2018-05-23 01:00 | 109.18 | 98.81
2018-05-23 01:30 | 111.41 | 100.76
2018-05-23 02:00 | 109.87 | 98.03
2018-05-23 02:30 | 109.42 | 97.97
2018-05-23 03:00 | 106.6 | 94.23
2018-05-23 03:30 | 109.49 | 97.36
2018-05-23 04:00 | 106.69 | 94.65
2018-05-23 04:30 | 107.74 | 96.14
2018-05-23 05:00 | 106.36 | 94.59
2018-05-23 05:30 | 106.49 | 93.82
2018-05-23 06:00 | 107.51 | 95.15
2018-05-23 06:30 | 102.01 | 87.7
2018-05-23 07:00 | 99.83 | 86.86
2018-05-23 07:30 | 97.94 | 85.47
2018-05-23 08:00 | 91.4 | 75.41
2018-05-23 08:30 | 97.35 | 81.82
2018-05-23 09:00 | 106.55 | 93.43
2018-05-23 09:30 | 109.27 | 96.15
2018-05-23 10:00 | 109.43 | 97.71
2018-05-23 10:30 | 106.61 | 94.51
2018-05-23 11:00 | 104.33 | 91.17
2018-05-23 11:30 | 102.44 | 88.67
2018-05-23 12:00 | 105.45 | 91.07
2018-05-23 12:30 | 106.78 | 91.88
2018-05-23 13:00 | 108.55 | 93.93
2018-05-23 13:30 | 106.21 | 91.4
2018-05-23 14:00 | 105.75 | 91.13
2018-05-23 14:30 | 99.71 | 85.41
2018-05-23 15:00 | 103.86 | 89.43
2018-05-23 15:30 | 96.82 | 82.22
2018-05-23 16:00 | 100.89 | 86.29
2018-05-23 16:30 | 107.76 | 93.19
2018-05-23 17:00 | 109.68 | 95.88
2018-05-23 17:30 | 109.94 | 96.75
2018-05-23 18:00 | 109.43 | 94.86
2018-05-23 18:30 | 106.27 | 91.57
2018-05-23 19:00 | 104.63 | 89.86
2018-05-23 19:30 | 105.27 | 91.91
2018-05-23 20:00 | 110.62 | 97.89
2018-05-23 20:30 | 111.7 | 98.87
2018-05-23 21:00 | 110 | 96.38
2018-05-23 21:30 | 109.11 | 94.94
2018-05-23 22:00 | 106 | 92.37
2018-05-23 22:30 | 102.11 | 88.33
2018-05-23 23:00 | 103.09 | 89.23
2018-05-23 23:30 | 99.88 | 86.57
2018-05-24 | 103.88 | 90.64
2018-05-24 00:30 | 101.18 | 87.76
2018-05-24 01:00 | 105.21 | 92.82
2018-05-24 01:30 | 103.91 | 91.05
2018-05-24 02:00 | 101.72 | 88.17
2018-05-24 02:30 | 102.85 | 89.34
2018-05-24 03:00 | 105.52 | 92.77
2018-05-24 03:30 | 97.88 | 83.26
2018-05-24 04:00 | 99.04 | 85.67
2018-05-24 04:30 | 96.51 | 81.25
2018-05-24 05:00 | 97.89 | 82.15
2018-05-24 05:30 | 99.43 | 84.89
2018-05-24 06:00 | 104.62 | 91.75
2018-05-24 06:30 | 97.68 | 83.01
2018-05-24 07:00 | 95.72 | 79.8
2018-05-24 07:30 | 99.86 | 86.07
2018-05-24 08:00 | 88.73 | 71.74
2018-05-24 08:30 | 90.48 | 73.91
2018-05-24 09:00 | 91.27 | 71.8
2018-05-24 09:30 | 88.8 | 67.09
2018-05-24 10:00 | 93.03 | 74.02
2018-05-24 10:30 | 98.51 | 81.25
2018-05-24 11:00 | 103.01 | 86.9
2018-05-24 11:30 | 103.35 | 87.27
2018-05-24 12:00 | 99.75 | 81.85
2018-05-24 12:30 | 97.52 | 78.79
2018-05-24 13:00 | 93.9 | 74.19
2018-05-24 13:30 | 94.97 | 75.59
2018-05-24 14:00 | 97.36 | 79.56
2018-05-24 14:30 | 102.73 | 87.23
2018-05-24 15:00 | 102.43 | 87.15
2018-05-24 15:30 | 103.79 | 88.35
2018-05-24 16:00 | 103.57 | 86.88
2018-05-24 16:30 | 107.51 | 91.53
2018-05-24 17:00 | 106.68 | 90.71
2018-05-24 17:30 | 106.5 | 90.8
2018-05-24 18:00 | 111.55 | 94.85
2018-05-24 18:30 | 107.02 | 90.37
2018-05-24 19:00 | 109.33 | 93.77
2018-05-24 19:30 | 111.58 | 95.93
2018-05-24 20:00 | 106.35 | 89.47
2018-05-24 20:30 | 118.4 | 102.93
2018-05-24 21:00 | 117.69 | 104.01
2018-05-24 21:30 | 117.55 | 103.66
2018-05-24 22:00 | 113.49 | 100.63
2018-05-24 22:30 | 111.72 | 98.81
2018-05-24 23:00 | 104.16 | 90.45
2018-05-24 23:30 | 106.96 | 93.59
2018-05-25 | 107.93 | 94.56
2018-05-25 00:30 | 104.27 | 91.15
2018-05-25 01:00 | 106.15 | 92.9
2018-05-25 01:30 | 114.67 | 101.17
2018-05-25 02:00 | 101.92 | 88.02
2018-05-25 02:30 | 96.79 | 82.47
2018-05-25 03:00 | 97.91 | 83.24
2018-05-25 03:30 | 100.96 | 86.77
2018-05-25 04:00 | 102.46 | 88.82
2018-05-25 04:30 | 102.18 | 88.23
2018-05-25 05:00 | 109.71 | 96.17
2018-05-25 05:30 | 98.14 | 83.73
2018-05-25 06:00 | 112.52 | 98.65
2018-05-25 06:30 | 101.21 | 85.55
2018-05-25 07:00 | 102.69 | 88.45
2018-05-25 07:30 | 103.52 | 89.76
2018-05-25 08:00 | 106.49 | 91.91
2018-05-25 08:30 | 109.68 | 95.67
2018-05-25 09:00 | 106.5 | 91.37
2018-05-25 09:30 | 103.37 | 89.36
2018-05-25 10:00 | 103.98 | 90.85
2018-05-25 10:30 | 92.38 | 77.98
2018-05-25 11:00 | 101.43 | 85.98
2018-05-25 11:30 | 99.08 | 83.69
2018-05-25 12:00 | 96.68 | 80.78
2018-05-25 12:30 | 102.33 | 87.63
2018-05-25 13:00 | 99.38 | 85.5
2018-05-25 13:30 | 105.9 | 93.08
2018-05-25 14:00 | 105.38 | 93.41
2018-05-25 14:30 | 97.62 | 84.22
2018-05-25 15:00 | 99.28 | 87.09
2018-05-25 15:30 | 101.77 | 88.58
2018-05-25 16:00 | 102.23 | 89.64
2018-05-25 16:30 | 112.9 | 101.58
2018-05-25 17:00 | 111.82 | 99.39
2018-05-25 17:30 | 115.08 | 102.46
2018-05-25 18:00 | 114.14 | 101.41
2018-05-25 18:30 | 103.74 | 89.11
2018-05-25 19:00 | 105.54 | 91.96
2018-05-25 19:30 | 107.02 | 94.28
2018-05-25 20:00 | 101.39 | 89.06
2018-05-25 20:30 | 101.18 | 88.29
2018-05-25 21:00 | 99.12 | 86.54
2018-05-25 21:30 | 108.34 | 96.84
2018-05-25 22:00 | 101.91 | 89.85
2018-05-25 22:30 | 100.5 | 87.2
2018-05-25 23:00 | 105.87 | 93.1
2018-05-25 23:30 | 111.81 | 99.16
2018-05-26 | 106.43 | 93.1
2018-05-26 00:30 | 110.76 | 98.42
2018-05-26 01:00 | 105.14 | 92.36
2018-05-26 01:30 | 112.06 | 99.22
2018-05-26 02:00 | 113.92 | 102.21
2018-05-26 02:30 | 118.11 | 106.27
2018-05-26 03:00 | 105.1 | 92.56
2018-05-26 03:30 | 105.59 | 92.49
2018-05-26 04:00 | 98.27 | 84.58
2018-05-26 04:30 | 105.78 | 92.37
2018-05-26 05:00 | 110.47 | 97.66
2018-05-26 05:30 | 110.96 | 98.41
2018-05-26 06:00 | 109.02 | 96.44
2018-05-26 06:30 | 98.76 | 84.75
2018-05-26 07:00 | 102.32 | 89.42
2018-05-26 07:30 | 102.85 | 89.21
2018-05-26 08:00 | 109.45 | 96.26
2018-05-26 08:30 | 104.69 | 91.22
2018-05-26 09:00 | 95.83 | 81.51
2018-05-26 09:30 | 94.47 | 80.23
2018-05-26 10:00 | 96.77 | 83.22
2018-05-26 10:30 | 92.68 | 78.03
2018-05-26 11:00 | 97.18 | 82.81
2018-05-26 11:30 | 92.74 | 78.29
2018-05-26 12:00 | 94.28 | 80.47
2018-05-26 12:30 | 98.02 | 84.96
2018-05-26 13:00 | 97.15 | 84.59
2018-05-26 13:30 | 90.81 | 77.21
2018-05-26 14:00 | 97.31 | 83.98
2018-05-26 14:30 | 99.6 | 86.49
2018-05-26 15:00 | 97.39 | 84.24
2018-05-26 15:30 | 101.14 | 88.35
2018-05-26 16:00 | 100.06 | 87.17
2018-05-26 16:30 | 103.51 | 91.22
2018-05-26 17:00 | 100.45 | 89.23
2018-05-26 17:30 | 101.2 | 88.77
2018-05-26 18:00 | 109.53 | 96.82
2018-05-26 18:30 | 108.77 | 94.97
2018-05-26 19:00 | 103.55 | 90.38
2018-05-26 19:30 | 111.83 | 98.96
2018-05-26 20:00 | 119.39 | 105.97
2018-05-26 20:30 | 115.06 | 101.36
2018-05-26 21:00 | 106.58 | 92.8
2018-05-26 21:30 | 103.98 | 89.88
2018-05-26 22:00 | 106.74 | 94.1
2018-05-26 22:30 | 109.87 | 97.42
2018-05-26 23:00 | 109.89 | 97.74
2018-05-26 23:30 | 105.06 | 92.47
2018-05-27 | 107.83 | 95.53
2018-05-27 00:30 | 105.6 | 92.81
2018-05-27 01:00 | 109.38 | 96.3
2018-05-27 01:30 | 109.08 | 96.55
2018-05-27 02:00 | 109.8 | 98.5
2018-05-27 02:30 | 115.72 | 104.44
2018-05-27 03:00 | 111.14 | 98.52
2018-05-27 03:30 | 111.53 | 100.31
2018-05-27 04:00 | 104.94 | 93.45
2018-05-27 04:30 | 99.96 | 87.5
2018-05-27 05:00 | 105.74 | 94.14
2018-05-27 05:30 | 105.44 | 93.44
2018-05-27 06:00 | 107.2 | 96.55
2018-05-27 06:30 | 97.62 | 84.82
2018-05-27 07:00 | 102.42 | 90.18
2018-05-27 07:30 | 109.35 | 97.75
2018-05-27 08:00 | 102.04 | 89.57
2018-05-27 08:30 | 106.72 | 94.95
2018-05-27 09:00 | 110.77 | 100.24
2018-05-27 09:30 | 109.23 | 98.51
2018-05-27 10:00 | 100.61 | 88.95
2018-05-27 10:30 | 94.53 | 82.33
2018-05-27 11:00 | 93.76 | 81.34
2018-05-27 11:30 | 91.5 | 77.29
2018-05-27 12:00 | 93.75 | 80.64
2018-05-27 12:30 | 98.75 | 87.05
2018-05-27 13:00 | 95.82 | 83.91
2018-05-27 13:30 | 101.15 | 90.05
2018-05-27 14:00 | 100.65 | 88.85
2018-05-27 14:30 | 100.48 | 88.67
2018-05-27 15:00 | 95.48 | 83.91
2018-05-27 15:30 | 96.49 | 85.18
2018-05-27 16:00 | 89.9 | 77.73
2018-05-27 16:30 | 91.63 | 79.62
2018-05-27 17:00 | 100.13 | 88.84
2018-05-27 17:30 | 102.11 | 90.32
2018-05-27 18:00 | 107.43 | 95.39
2018-05-27 18:30 | 96.99 | 84.72
2018-05-27 19:00 | 105.71 | 94.83
2018-05-27 19:30 | 109.19 | 98.46
2018-05-27 20:00 | 104.67 | 93.15
2018-05-27 20:30 | 105.77 | 93.91
2018-05-27 21:00 | 114.11 | 102.11
2018-05-27 21:30 | 108.11 | 94.42
2018-05-27 22:00 | 114.75 | 101.48
2018-05-27 22:30 | 111.74 | 98.24
2018-05-27 23:00 | 104.53 | 89.72
2018-05-27 23:30 | 105.66 | 93.14
2018-05-28 | 98.32 | 85.82
2018-05-28 00:30 | 105.47 | 93.53
2018-05-28 01:00 | 99.42 | 85.7
2018-05-28 01:30 | 107.25 | 94.94
2018-05-28 02:00 | 104.57 | 92.18
2018-05-28 02:30 | 104.97 | 92.97
2018-05-28 03:00 | 107.29 | 95.63
2018-05-28 03:30 | 102.32 | 89.96
2018-05-28 04:00 | 103.08 | 91.23
2018-05-28 04:30 | 102.06 | 90.51
2018-05-28 05:00 | 104.58 | 93.28
2018-05-28 05:30 | 104.02 | 92.42
2018-05-28 06:00 | 104.47 | 91.54
2018-05-28 06:30 | 98.69 | 85.11
2018-05-28 07:00 | 98.92 | 86.31
2018-05-28 07:30 | 104.35 | 91.92
2018-05-28 08:00 | 105.67 | 93.6
2018-05-28 08:30 | 98.09 | 85.22
2018-05-28 09:00 | 102.28 | 89.31
2018-05-28 09:30 | 98.14 | 83.98
2018-05-28 10:00 | 103.9 | 90.75
2018-05-28 10:30 | 100.58 | 87.17
2018-05-28 11:00 | 106.02 | 92.59
2018-05-28 11:30 | 104.78 | 90.74
2018-05-28 12:00 | 107.08 | 93.75
2018-05-28 12:30 | 111.7 | 98.99
2018-05-28 13:00 | 108.02 | 95.78
2018-05-28 13:30 | 103.54 | 90.48
2018-05-28 14:00 | 106.81 | 93.1
2018-05-28 14:30 | 102 | 87.45
2018-05-28 15:00 | 97.38 | 83.95
2018-05-28 15:30 | 92.25 | 77.74
2018-05-28 16:00 | 97.44 | 85.31
2018-05-28 16:30 | 111.11 | 100.06
2018-05-28 17:00 | 107.76 | 95.68
2018-05-28 17:30 | 110.9 | 99.52
2018-05-28 18:00 | 109.8 | 97.19
2018-05-28 18:30 | 111.89 | 99.28
2018-05-28 19:00 | 116.96 | 105.1
2018-05-28 19:30 | 118.96 | 107.01
2018-05-28 20:00 | 112.94 | 100.04
2018-05-28 20:30 | 115.57 | 102.93
2018-05-28 21:00 | 113.76 | 101.64
2018-05-28 21:30 | 114.61 | 102.87
2018-05-28 22:00 | 108.36 | 95.72
2018-05-28 22:30 | 111.3 | 99.13
2018-05-28 23:00 | 107.83 | 95.33
2018-05-28 23:30 | 109.44 | 98.02
2018-05-29 | 109.84 | 98.1
2018-05-29 00:30 | 108.78 | 96.25
2018-05-29 01:00 | 106.59 | 92.27
2018-05-29 01:30 | 109.64 | 96.09
2018-05-29 02:00 | 104.18 | 90.88
2018-05-29 02:30 | 104.27 | 90.44
2018-05-29 03:00 | 104.75 | 90.79
2018-05-29 03:30 | 104.98 | 91.31
2018-05-29 04:00 | 102.71 | 89.52
2018-05-29 04:30 | 103.81 | 91.36
2018-05-29 05:00 | 114.04 | 103.27
2018-05-29 05:30 | 113.06 | 102.23
2018-05-29 06:00 | 107.28 | 95.83
2018-05-29 06:30 | 111.78 | 99.87
2018-05-29 07:00 | 109.86 | 97.83
2018-05-29 07:30 | 105.79 | 93.51
2018-05-29 08:00 | 114.42 | 103.13
2018-05-29 08:30 | 106.47 | 92.8
2018-05-29 09:00 | 108.23 | 94.82
2018-05-29 09:30 | 104.2 | 90.82
2018-05-29 10:00 | 103.77 | 89.62
2018-05-29 10:30 | 109.17 | 95.97
2018-05-29 11:00 | 112.17 | 98.44
2018-05-29 11:30 | 105.36 | 91.02
2018-05-29 12:00 | 105.24 | 90.93
2018-05-29 12:30 | 107.56 | 94.37
2018-05-29 13:00 | 106.55 | 92.91
2018-05-29 13:30 | 104.26 | 90.49
2018-05-29 14:00 | 110.78 | 96.13
2018-05-29 14:30 | 102.55 | 86.91
2018-05-29 15:00 | 104.06 | 89.22
2018-05-29 15:30 | 105.9 | 90.72
2018-05-29 16:00 | 113.26 | 98.01
2018-05-29 16:30 | 110.35 | 95.27
2018-05-29 17:00 | 109.14 | 93.71
2018-05-29 17:30 | 114 | 97.2
2018-05-29 18:00 | 114.18 | 97.65
2018-05-29 18:30 | 96.28 | 81.07
2018-05-29 19:00 | 107.31 | 93.9
2018-05-29 19:30 | 107.98 | 95.05
2018-05-29 20:00 | 98.65 | 85.57
2018-05-29 20:30 | 110.83 | 95.57
2018-05-29 21:00 | 102.48 | 87.6
2018-05-29 21:30 | 111.13 | 97.26
2018-05-29 22:00 | 108.16 | 93.91
2018-05-29 22:30 | 102.93 | 88.75
2018-05-29 23:00 | 105.03 | 91.52
2018-05-29 23:30 | 105.67 | 91.86
2018-05-30 | 100.72 | 87.84
2018-05-30 00:30 | 105.83 | 92.85
2018-05-30 01:00 | 112.92 | 101.13
2018-05-30 01:30 | 110.46 | 98.46
2018-05-30 02:00 | 108.74 | 97.29
2018-05-30 02:30 | 115.63 | 104.33
2018-05-30 03:00 | 105.24 | 93.32
2018-05-30 03:30 | 99.9 | 88.36
2018-05-30 04:00 | 112.52 | 101.2
2018-05-30 04:30 | 104.54 | 92.45
2018-05-30 05:00 | 97.77 | 86.31
2018-05-30 05:30 | 95.83 | 83.46
2018-05-30 06:00 | 104.6 | 93.94
2018-05-30 06:30 | 98.93 | 87.22
2018-05-30 07:00 | 110.66 | 100.42
2018-05-30 07:30 | 105.53 | 95.04
2018-05-30 08:00 | 104.07 | 92.18
2018-05-30 08:30 | 97.37 | 85.25
2018-05-30 09:00 | 104.23 | 92.16
2018-05-30 09:30 | 101.51 | 88.36
2018-05-30 10:00 | 104.38 | 92.31
2018-05-30 10:30 | 110.98 | 99.45
2018-05-30 11:00 | 100.25 | 86.94
2018-05-30 11:30 | 105.29 | 92.44
2018-05-30 12:00 | 104.88 | 92.01
2018-05-30 12:30 | 106.18 | 92.99
2018-05-30 13:00 | 107.76 | 95.21
2018-05-30 13:30 | 108.85 | 96.02
2018-05-30 14:00 | 105.8 | 92.7
2018-05-30 14:30 | 102.93 | 89.71
2018-05-30 15:00 | 98.22 | 85.22
2018-05-30 15:30 | 106.65 | 93.49
2018-05-30 16:00 | 102.96 | 89.55
2018-05-30 16:30 | 99.55 | 85.52
2018-05-30 17:00 | 105.51 | 92.46
2018-05-30 17:30 | 115.04 | 102.02
2018-05-30 18:00 | 116.21 | 102.1
2018-05-30 18:30 | 110.05 | 95.96
2018-05-30 19:00 | 109.01 | 95.7
2018-05-30 19:30 | 120.09 | 106.93
2018-05-30 20:00 | 116.6 | 103.69
2018-05-30 20:30 | 110.45 | 96.18
2018-05-30 21:00 | 118.44 | 105.67
2018-05-30 21:30 | 117.68 | 104.78
2018-05-30 22:00 | 114.64 | 101.13
2018-05-30 22:30 | 113.1 | 99.7
2018-05-30 23:00 | 110.07 | 96.06
2018-05-30 23:30 | 98.08 | 83.85
2018-05-31 | 104.82 | 91.09
2018-05-31 00:30 | 100.31 | 87.31
2018-05-31 01:00 | 96.06 | 82.87
2018-05-31 01:30 | 96.78 | 84.22
2018-05-31 02:00 | 93.27 | 80.63
2018-05-31 02:30 | 89.85 | 77.06
2018-05-31 03:00 | 93.43 | 81
2018-05-31 03:30 | 97.76 | 84.87
2018-05-31 04:00 | 104.5 | 91.58
2018-05-31 04:30 | 104 | 91.51
2018-05-31 05:00 | 100.78 | 88.16
2018-05-31 05:30 | 100.71 | 88.25
2018-05-31 06:00 | 105.28 | 93.25
2018-05-31 06:30 | 97.16 | 83.53
2018-05-31 07:00 | 97.6 | 85.43
2018-05-31 07:30 | 96.35 | 84.05
2018-05-31 08:00 | 96.37 | 83.8
2018-05-31 08:30 | 93.68 | 81.2
2018-05-31 09:00 | 94.77 | 82.3
2018-05-31 09:30 | 94.36 | 81.16
2018-05-31 10:00 | 93.11 | 78.24
2018-05-31 10:30 | 97.16 | 83.38
2018-05-31 11:00 | 93.34 | 78.36
2018-05-31 11:30 | 91.97 | 75.35
2018-05-31 12:00 | 97.21 | 82.02
2018-05-31 12:30 | 99.21 | 83.97
2018-05-31 13:00 | 94.35 | 78.76
2018-05-31 13:30 | 96.18 | 80.93
2018-05-31 14:00 | 99.24 | 84.15
2018-05-31 14:30 | 101.4 | 86.01
2018-05-31 15:00 | 100.3 | 83.81
2018-05-31 15:30 | 96.91 | 80.71
2018-05-31 16:00 | 108.85 | 93.65
2018-05-31 16:30 | 105.87 | 91.33
2018-05-31 17:00 | 104.01 | 87.96
2018-05-31 17:30 | 112.99 | 98.05
2018-05-31 18:00 | 113.17 | 97.52
2018-05-31 18:30 | 99.82 | 83.05
2018-05-31 19:00 | 103.91 | 88.88
2018-05-31 19:30 | 107.33 | 93.89
2018-05-31 20:00 | 114.86 | 100.92
2018-05-31 20:30 | 114.37 | 99.69
2018-05-31 21:00 | 118.38 | 104.96
2018-05-31 21:30 | 112.3 | 98.6
2018-05-31 22:00 | 114.45 | 100.68
2018-05-31 22:30 | 110.22 | 97.17
2018-05-31 23:00 | 106.13 | 92.24
2018-05-31 23:30 | 107.45 | 94.62
2018-06-01 | 109.94 | 98.16
2018-06-01 00:30 | 110.94 | 98.45
2018-06-01 01:00 | 118.51 | 105.7
2018-06-01 01:30 | 121.1 | 107.62
2018-06-01 02:00 | 113.01 | 99.18
2018-06-01 02:30 | 112.18 | 98.78
2018-06-01 03:00 | 116.07 | 103.07
2018-06-01 03:30 | 111.79 | 98.81
2018-06-01 04:00 | 112.06 | 100.05
2018-06-01 04:30 | 108.39 | 97.01
2018-06-01 05:00 | 100.62 | 88.99
2018-06-01 05:30 | 95.82 | 83.15
2018-06-01 06:00 | 99.75 | 87.26
2018-06-01 06:30 | 96.88 | 84.74
2018-06-01 07:00 | 109.67 | 98.6
2018-06-01 07:30 | 110.82 | 99.92
2018-06-01 08:00 | 111.29 | 99.79
2018-06-01 08:30 | 102.9 | 90.84
2018-06-01 09:00 | 105.45 | 92.27
2018-06-01 09:30 | 107.25 | 93.88
2018-06-01 10:00 | 105.76 | 92.3
2018-06-01 10:30 | 101.26 | 88.04
2018-06-01 11:00 | 94.46 | 81.81
2018-06-01 11:30 | 99.34 | 86.89
2018-06-01 12:00 | 102.52 | 89.88
2018-06-01 12:30 | 103.18 | 90.48
2018-06-01 13:00 | 107.99 | 95.54
2018-06-01 13:30 | 111.13 | 98.46
2018-06-01 14:00 | 110.67 | 97.35
2018-06-01 14:30 | 110.3 | 96.65
2018-06-01 15:00 | 104.55 | 90.82
2018-06-01 15:30 | 99.46 | 85.15
2018-06-01 16:00 | 101.9 | 88.14
2018-06-01 16:30 | 100.91 | 87.68
2018-06-01 17:00 | 101.92 | 88.61
2018-06-01 17:30 | 109.98 | 97.02
2018-06-01 18:00 | 106.35 | 91.74
2018-06-01 18:30 | 103.01 | 88.6
2018-06-01 19:00 | 110.97 | 98.17
2018-06-01 19:30 | 111.48 | 98.64
2018-06-01 20:00 | 111.05 | 97.49
2018-06-01 20:30 | 107.34 | 93.78
2018-06-01 21:00 | 107.04 | 93.93
2018-06-01 21:30 | 106.82 | 93.91
2018-06-01 22:00 | 103.27 | 89.66
2018-06-01 22:30 | 104.25 | 91.35
2018-06-01 23:00 | 103.25 | 91.17
2018-06-01 23:30 | 101.53 | 89.44
2018-06-02 | 102.29 | 89.38
2018-06-02 00:30 | 108.44 | 96.41
2018-06-02 01:00 | 113.87 | 101.94
2018-06-02 01:30 | 109.99 | 98.17
2018-06-02 02:00 | 108.5 | 96.12
2018-06-02 02:30 | 107.3 | 94.83
2018-06-02 03:00 | 109.13 | 97.45
2018-06-02 03:30 | 109.98 | 98.08
2018-06-02 04:00 | 114.73 | 102.79
2018-06-02 04:30 | 110.18 | 98.08
2018-06-02 05:00 | 113.18 | 101.18
2018-06-02 05:30 | 115.93 | 103.75
2018-06-02 06:00 | 110.91 | 98.58
2018-06-02 06:30 | 103.97 | 90.18
2018-06-02 07:00 | 101.9 | 89.2
2018-06-02 07:30 | 101.89 | 90.16
2018-06-02 08:00 | 105.99 | 93.53
2018-06-02 08:30 | 105.71 | 93.04
2018-06-02 09:00 | 105.38 | 93.27
2018-06-02 09:30 | 114.14 | 101.89
2018-06-02 10:00 | 108.33 | 95.77
2018-06-02 10:30 | 108.6 | 96.28
2018-06-02 11:00 | 99.94 | 86.82
2018-06-02 11:30 | 102.69 | 90.02
2018-06-02 12:00 | 104 | 91.53
2018-06-02 12:30 | 105.2 | 92.85
2018-06-02 13:00 | 102.66 | 89.87
2018-06-02 13:30 | 103.11 | 90.33
2018-06-02 14:00 | 99.26 | 86.19
2018-06-02 14:30 | 104.62 | 92.41
2018-06-02 15:00 | 105.43 | 93.55
2018-06-02 15:30 | 95.32 | 82.19
2018-06-02 16:00 | 111.79 | 100.03
2018-06-02 16:30 | 109.41 | 97.01
2018-06-02 17:00 | 113.4 | 101.58
2018-06-02 17:30 | 107.68 | 95.53
2018-06-02 18:00 | 115.31 | 103.03
2018-06-02 18:30 | 104.09 | 91.76
2018-06-02 19:00 | 118.73 | 107.21
2018-06-02 19:30 | 120.39 | 108.98
2018-06-02 20:00 | 120.28 | 108.06
2018-06-02 20:30 | 109.87 | 97.5
2018-06-02 21:00 | 113.64 | 100.96
2018-06-02 21:30 | 113.46 | 101.21
2018-06-02 22:00 | 106.88 | 94.89
2018-06-02 22:30 | 114.93 | 102.79
2018-06-02 23:00 | 109.16 | 97.31
2018-06-02 23:30 | 102.88 | 90.39
2018-06-03 | 104.58 | 92.08
2018-06-03 00:30 | 108.91 | 97.21
2018-06-03 01:00 | 106.89 | 95.07
2018-06-03 01:30 | 110.48 | 99.22
2018-06-03 02:00 | 110.69 | 99.73
2018-06-03 02:30 | 109.08 | 98
2018-06-03 03:00 | 106.89 | 96.22
2018-06-03 03:30 | 103.87 | 92.77
2018-06-03 04:00 | 108.37 | 97.61
2018-06-03 04:30 | 106.95 | 95.89
2018-06-03 05:00 | 108.59 | 97.8
2018-06-03 05:30 | 106.25 | 95.16
2018-06-03 06:00 | 103.45 | 91.7
2018-06-03 06:30 | 101.28 | 88.96
2018-06-03 07:00 | 107.51 | 95.85
2018-06-03 07:30 | 104.38 | 92.1
2018-06-03 08:00 | 104.8 | 92.94
2018-06-03 08:30 | 106.32 | 94.32
2018-06-03 09:00 | 103.68 | 91.51
2018-06-03 09:30 | 109.48 | 97.83
2018-06-03 10:00 | 106.14 | 94.3
2018-06-03 10:30 | 102.51 | 90.3
2018-06-03 11:00 | 111.41 | 99.79
2018-06-03 11:30 | 103.27 | 90.66
2018-06-03 12:00 | 108.18 | 96.48
2018-06-03 12:30 | 105.35 | 92.96
2018-06-03 13:00 | 107.74 | 94.82
2018-06-03 13:30 | 106.7 | 94.09
2018-06-03 14:00 | 108.82 | 95.86
2018-06-03 14:30 | 102.02 | 87.92
2018-06-03 15:00 | 101.77 | 86.81
2018-06-03 15:30 | 108.73 | 93.21
2018-06-03 16:00 | 107.42 | 91.85
2018-06-03 16:30 | 105.58 | 90.94
2018-06-03 17:00 | 117.87 | 102.9
2018-06-03 17:30 | 115.86 | 101.91
2018-06-03 18:00 | 130.09 | 115.77
2018-06-03 18:30 | 120.93 | 105.33
2018-06-03 19:00 | 122.57 | 107.94
2018-06-03 19:30 | 127.68 | 111.75
2018-06-03 20:00 | 128.14 | 112.08
2018-06-03 20:30 | 122.42 | 107.03
2018-06-03 21:00 | 113.12 | 99.88
2018-06-03 21:30 | 110.17 | 97.95
2018-06-03 22:00 | 107.55 | 94.5
2018-06-03 22:30 | 122.48 | 108.4
2018-06-03 23:00 | 114.56 | 100.7
2018-06-03 23:30 | 111.39 | 99.61
2018-06-04 | 112.91 | 100.5
2018-06-04 00:30 | 110.69 | 97.23
2018-06-04 01:00 | 119.56 | 106.42
2018-06-04 01:30 | 112.07 | 98.96
2018-06-04 02:00 | 112.97 | 99.84
2018-06-04 02:30 | 115.97 | 103.92
2018-06-04 03:00 | 109.54 | 97.62
2018-06-04 03:30 | 110.13 | 98.86
2018-06-04 04:00 | 103.18 | 92.17
2018-06-04 04:30 | 110.19 | 99.72
2018-06-04 05:00 | 114.8 | 104.7
2018-06-04 05:30 | 112.6 | 102.34
2018-06-04 06:00 | 106.27 | 95.74
2018-06-04 06:30 | 101.5 | 90.25
2018-06-04 07:00 | 106.24 | 94.96
2018-06-04 07:30 | 108.98 | 95.31
2018-06-04 08:00 | 116.94 | 103.35
2018-06-04 08:30 | 109.11 | 96.17
2018-06-04 09:00 | 108.18 | 94.58
2018-06-04 09:30 | 108.73 | 94.95
2018-06-04 10:00 | 118.82 | 105.17
2018-06-04 10:30 | 116.28 | 103.4
2018-06-04 11:00 | 107.43 | 94.2
2018-06-04 11:30 | 104.39 | 91.19
2018-06-04 12:00 | 105.76 | 92.04
2018-06-04 12:30 | 112.25 | 99.63
2018-06-04 13:00 | 106.73 | 95.06
2018-06-04 13:30 | 104.43 | 92.11
2018-06-04 14:00 | 109.3 | 96.95
2018-06-04 14:30 | 108.08 | 94.83
2018-06-04 15:00 | 102.43 | 88.74
2018-06-04 15:30 | 102.29 | 89.41
2018-06-04 16:00 | 103.4 | 91.07
2018-06-04 16:30 | 106.44 | 95.09
2018-06-04 17:00 | 104.96 | 93.08
2018-06-04 17:30 | 106.13 | 94.53
2018-06-04 18:00 | 106.87 | 95.43
2018-06-04 18:30 | 98.85 | 86.41
2018-06-04 19:00 | 105.07 | 93.24
2018-06-04 19:30 | 103.56 | 91.74
2018-06-04 20:00 | 102.8 | 91.41
2018-06-04 20:30 | 104.78 | 94.08
2018-06-04 21:00 | 105.48 | 94.57
2018-06-04 21:30 | 102.33 | 91.15
2018-06-04 22:00 | 104.98 | 94.41
2018-06-04 22:30 | 100.87 | 89.95
2018-06-04 23:00 | 102.48 | 91.79
2018-06-04 23:30 | 97.73 | 86.11
2018-06-05 | 106.63 | 95.25
2018-06-05 00:30 | 96.61 | 85.38
2018-06-05 01:00 | 100.76 | 89.81
2018-06-05 01:30 | 108 | 97.57
2018-06-05 02:00 | 102.94 | 92.14
2018-06-05 02:30 | 111.23 | 100.12
2018-06-05 03:00 | 108.36 | 97.38
2018-06-05 03:30 | 110.28 | 99.44
2018-06-05 04:00 | 120.84 | 110
2018-06-05 04:30 | 110.51 | 99.56
2018-06-05 05:00 | 112.61 | 100.99
2018-06-05 05:30 | 111.36 | 100.79
2018-06-05 06:00 | 108.77 | 98.71
2018-06-05 06:30 | 106.07 | 95.78
2018-06-05 07:00 | 99.34 | 88.84
2018-06-05 07:30 | 95.42 | 84.32
2018-06-05 08:00 | 91.14 | 78.75
2018-06-05 08:30 | 86.15 | 70.35
2018-06-05 09:00 | 91.42 | 76.84
2018-06-05 09:30 | 87.42 | 71.66
2018-06-05 10:00 | 86.16 | 70.1
2018-06-05 10:30 | 93.37 | 79.92
2018-06-05 11:00 | 99.5 | 87.41
2018-06-05 11:30 | 91.76 | 78.79
2018-06-05 12:00 | 87.8 | 73.38
2018-06-05 12:30 | 92.72 | 80.52
2018-06-05 13:00 | 86.71 | 73.56
2018-06-05 13:30 | 86.15 | 72.97
2018-06-05 14:00 | 90.7 | 78.29
2018-06-05 14:30 | 94.15 | 82.59
2018-06-05 15:00 | 92.52 | 80.38
2018-06-05 15:30 | 89.99 | 77.19
2018-06-05 16:00 | 83.9 | 69.71
2018-06-05 16:30 | 89.32 | 76.85
2018-06-05 17:00 | 91.28 | 79.99
2018-06-05 17:30 | 92.26 | 80.47
2018-06-05 18:00 | 93.41 | 81.89
2018-06-05 18:30 | 83.57 | 70.87
2018-06-05 19:00 | 91.87 | 81.24
2018-06-05 19:30 | 95.84 | 85.24
2018-06-05 20:00 | 99.83 | 87.19
2018-06-05 20:30 | 99.08 | 87
2018-06-05 21:00 | 94.81 | 83.36
2018-06-05 21:30 | 97.08 | 86.03
2018-06-05 22:00 | 96.49 | 85.24
2018-06-05 22:30 | 98.4 | 87.55
2018-06-05 23:00 | 105.24 | 94.26
2018-06-05 23:30 | 103.16 | 92.24
2018-06-06 | 106.05 | 95.37
2018-06-06 00:30 | 106.04 | 94.76
2018-06-06 01:00 | 102.93 | 92.01
2018-06-06 01:30 | 99.83 | 88.77
2018-06-06 02:00 | 100.81 | 89.76
2018-06-06 02:30 | 97.64 | 85.89
2018-06-06 03:00 | 102.38 | 91.22
2018-06-06 03:30 | 106.39 | 95.75
2018-06-06 04:00 | 106.48 | 95.91
2018-06-06 04:30 | 108.68 | 98.39
2018-06-06 05:00 | 107.09 | 96.86
2018-06-06 05:30 | 108.16 | 97.69
2018-06-06 06:00 | 102.42 | 91.76
2018-06-06 06:30 | 89.95 | 77.01
2018-06-06 07:00 | 96.74 | 85.82
2018-06-06 07:30 | 105.15 | 94.66
2018-06-06 08:00 | 97.35 | 86.42
2018-06-06 08:30 | 92.68 | 80.55
2018-06-06 09:00 | 96.1 | 84.49
2018-06-06 09:30 | 98.37 | 86.11
2018-06-06 10:00 | 95.7 | 83.37
2018-06-06 10:30 | 101.94 | 90.2
2018-06-06 11:00 | 103.47 | 91.35
2018-06-06 11:30 | 101.41 | 89.22
2018-06-06 12:00 | 101.47 | 89.82
2018-06-06 12:30 | 104.08 | 91.75
2018-06-06 13:00 | 107.01 | 95.08
2018-06-06 13:30 | 105.92 | 93.11
2018-06-06 14:00 | 108.47 | 96.23
2018-06-06 14:30 | 105.9 | 93.43
2018-06-06 15:00 | 107.41 | 94.67
2018-06-06 15:30 | 108.86 | 96.13
2018-06-06 16:00 | 101.13 | 89.26
2018-06-06 16:30 | 112.34 | 100.65
2018-06-06 17:00 | 116.59 | 105.53
2018-06-06 17:30 | 113.75 | 102.21
2018-06-06 18:00 | 117.58 | 105.92
2018-06-06 18:30 | 113.6 | 100.64
2018-06-06 19:00 | 122.73 | 110.88
2018-06-06 19:30 | 118.91 | 107.66
2018-06-06 20:00 | 114.44 | 102.77
2018-06-06 20:30 | 123.89 | 112.9
2018-06-06 21:00 | 118.7 | 107.97
2018-06-06 21:30 | 114.81 | 103.69
2018-06-06 22:00 | 119.21 | 108.25
2018-06-06 22:30 | 113.03 | 101.89
2018-06-06 23:00 | 120.18 | 108.58
2018-06-06 23:30 | 119.57 | 108.21
2018-06-07 | 122.17 | 110.23
2018-06-07 00:30 | 111.8 | 100.96
2018-06-07 01:00 | 105.41 | 92.24
2018-06-07 01:30 | 108.65 | 96.03
2018-06-07 02:00 | 114.9 | 102.32
2018-06-07 02:30 | 108.58 | 97.54
2018-06-07 03:00 | 114.77 | 103.49
2018-06-07 03:30 | 109.33 | 97.41
2018-06-07 04:00 | 110.38 | 98.52
2018-06-07 04:30 | 110.48 | 98.94
2018-06-07 05:00 | 111.39 | 100.29
2018-06-07 05:30 | 114.78 | 103.33
2018-06-07 06:00 | 109.58 | 98.07
2018-06-07 06:30 | 103.98 | 91.98
2018-06-07 07:00 | 108.59 | 97.69
2018-06-07 07:30 | 112.6 | 101.96
2018-06-07 08:00 | 108 | 96.73
2018-06-07 08:30 | 103.42 | 92.25
2018-06-07 09:00 | 98.41 | 87.13
2018-06-07 09:30 | 95.96 | 84.24
2018-06-07 10:00 | 95.28 | 82.94
2018-06-07 10:30 | 91.93 | 77.85
2018-06-07 11:00 | 97.57 | 84.06
2018-06-07 11:30 | 99.79 | 86.65
2018-06-07 12:00 | 101.98 | 89.25
2018-06-07 12:30 | 99.76 | 86.23
2018-06-07 13:00 | 105.06 | 92.21
2018-06-07 13:30 | 104.58 | 91.92
2018-06-07 14:00 | 100.39 | 88.73
2018-06-07 14:30 | 105.7 | 94.93
2018-06-07 15:00 | 100.71 | 87.91
2018-06-07 15:30 | 96.29 | 82.79
2018-06-07 16:00 | 102.55 | 91.21
2018-06-07 16:30 | 113.46 | 102.25
2018-06-07 17:00 | 109.85 | 97.98
2018-06-07 17:30 | 114.21 | 102.67
2018-06-07 18:00 | 117.55 | 106.22
2018-06-07 18:30 | 113.61 | 101.4
2018-06-07 19:00 | 111.57 | 100.31
2018-06-07 19:30 | 121.18 | 108.97
2018-06-07 20:00 | 116.36 | 103.55
2018-06-07 20:30 | 121.73 | 108.75
2018-06-07 21:00 | 118.19 | 105.23
2018-06-07 21:30 | 118.34 | 105.6
2018-06-07 22:00 | 118.2 | 106.91
2018-06-07 22:30 | 118.98 | 107.27
2018-06-07 23:00 | 115.29 | 103.68
2018-06-07 23:30 | 116.07 | 104.02
2018-06-08 | 115.54 | 103.74
2018-06-08 00:30 | 114.88 | 103.45
2018-06-08 01:00 | 110.12 | 97.56
2018-06-08 01:30 | 109.69 | 96.47
2018-06-08 02:00 | 110.26 | 97.04
2018-06-08 02:30 | 112.27 | 98.94
2018-06-08 03:00 | 109.03 | 95.34
2018-06-08 03:30 | 109.02 | 96.51
2018-06-08 04:00 | 120.46 | 108.08
2018-06-08 04:30 | 113.69 | 101.55
2018-06-08 05:00 | 115.91 | 103.91
2018-06-08 05:30 | 115.89 | 104.11
2018-06-08 06:00 | 111.44 | 98.79
2018-06-08 06:30 | 99.87 | 86.43
2018-06-08 07:00 | 109.35 | 96.11
2018-06-08 07:30 | 111.12 | 98.58
2018-06-08 08:00 | 99.3 | 87.48
2018-06-08 08:30 | 110.24 | 97.09
2018-06-08 09:00 | 106.58 | 93.91
2018-06-08 09:30 | 107.39 | 94.82
2018-06-08 10:00 | 106.31 | 93.37
2018-06-08 10:30 | 104.96 | 91.67
2018-06-08 11:00 | 106.11 | 93.39
2018-06-08 11:30 | 98.36 | 85.19
2018-06-08 12:00 | 100.35 | 87.37
2018-06-08 12:30 | 107.85 | 95.24
2018-06-08 13:00 | 118.5 | 105.73
2018-06-08 13:30 | 111.32 | 98.45
2018-06-08 14:00 | 99.56 | 86.13
2018-06-08 14:30 | 105.23 | 91.47
2018-06-08 15:00 | 110.17 | 96.36
2018-06-08 15:30 | 112.17 | 98.28
2018-06-08 16:00 | 111.67 | 97.9
2018-06-08 16:30 | 112.01 | 99.05
2018-06-08 17:00 | 118.47 | 105.97
2018-06-08 17:30 | 120.51 | 108.33
2018-06-08 18:00 | 116.48 | 103.68
2018-06-08 18:30 | 112.76 | 99.77
2018-06-08 19:00 | 118.53 | 106.39
2018-06-08 19:30 | 115.46 | 102.71
2018-06-08 20:00 | 121.13 | 109.15
2018-06-08 20:30 | 123.54 | 112.26
2018-06-08 21:00 | 118.19 | 106.1
2018-06-08 21:30 | 118.63 | 105.25
2018-06-08 22:00 | 120.08 | 107.1
2018-06-08 22:30 | 117.94 | 104.66
2018-06-08 23:00 | 118.57 | 105.73
2018-06-08 23:30 | 112.93 | 101.52
2018-06-09 | 121.27 | 108.75
2018-06-09 00:30 | 123.75 | 109.94
2018-06-09 01:00 | 121.33 | 107.14
2018-06-09 01:30 | 115.72 | 100.95
2018-06-09 02:00 | 120.14 | 106.8
2018-06-09 02:30 | 115.12 | 101.3
2018-06-09 03:00 | 115.93 | 102.26
2018-06-09 03:30 | 112.5 | 98.31
2018-06-09 04:00 | 108.59 | 95.49
2018-06-09 04:30 | 104.24 | 90.85
2018-06-09 05:00 | 104.49 | 90.53
2018-06-09 05:30 | 110.08 | 97.84
2018-06-09 06:00 | 110.44 | 98.35
2018-06-09 06:30 | 111.38 | 98.78
2018-06-09 07:00 | 118.67 | 107.09
2018-06-09 07:30 | 111.59 | 100.03
2018-06-09 08:00 | 111.94 | 100.64
2018-06-09 08:30 | 101.79 | 90.48
2018-06-09 09:00 | 107.37 | 95.43
2018-06-09 09:30 | 112.3 | 101.06
2018-06-09 10:00 | 104.37 | 92.25
2018-06-09 10:30 | 105.87 | 93.78
2018-06-09 11:00 | 105.99 | 93.73
2018-06-09 11:30 | 104.31 | 91.67
2018-06-09 12:00 | 105.66 | 92.98
2018-06-09 12:30 | 112.28 | 100.83
2018-06-09 13:00 | 115.42 | 104.59
2018-06-09 13:30 | 108.46 | 97.07
2018-06-09 14:00 | 108.43 | 95.92
2018-06-09 14:30 | 105.55 | 91.76
2018-06-09 15:00 | 102.11 | 87.79
2018-06-09 15:30 | 102.98 | 89.67
2018-06-09 16:00 | 104.26 | 92.2
2018-06-09 16:30 | 108.31 | 95.98
2018-06-09 17:00 | 110.2 | 97.74
2018-06-09 17:30 | 116.5 | 104.03
2018-06-09 18:00 | 110.72 | 97.6
2018-06-09 18:30 | 101.29 | 87.2
2018-06-09 19:00 | 120.35 | 106.94
2018-06-09 19:30 | 118.3 | 105.13
2018-06-09 20:00 | 118.91 | 105.19
2018-06-09 20:30 | 115.18 | 101.77
2018-06-09 21:00 | 117.1 | 103.59
2018-06-09 21:30 | 114.9 | 102.36
2018-06-09 22:00 | 113.74 | 100.61
2018-06-09 22:30 | 122.5 | 110.92
2018-06-09 23:00 | 113.16 | 101.69
2018-06-09 23:30 | 111.3 | 98.97
2018-06-10 | 115.24 | 103.55
2018-06-10 00:30 | 115.55 | 104.36
2018-06-10 01:00 | 105.31 | 93.85
2018-06-10 01:30 | 97.93 | 85.88
2018-06-10 02:00 | 103.19 | 91.26
2018-06-10 02:30 | 103.6 | 91.86
2018-06-10 03:00 | 103.63 | 91.73
2018-06-10 03:30 | 102.96 | 91.02
2018-06-10 04:00 | 108.46 | 96.49
2018-06-10 04:30 | 107.46 | 95.66
2018-06-10 05:00 | 115.07 | 104.27
2018-06-10 05:30 | 109.3 | 98.24
2018-06-10 06:00 | 107.98 | 97.24
2018-06-10 06:30 | 104.71 | 92.8
2018-06-10 07:00 | 103.23 | 92.01
2018-06-10 07:30 | 100.29 | 88.9
2018-06-10 08:00 | 103.61 | 91.93
2018-06-10 08:30 | 106.96 | 95.34
2018-06-10 09:00 | 117.11 | 105.62
2018-06-10 09:30 | 105.91 | 93.73
2018-06-10 10:00 | 103.63 | 90.77
2018-06-10 10:30 | 108.39 | 96.37
2018-06-10 11:00 | 110.1 | 98.43
2018-06-10 11:30 | 98.26 | 85.7
2018-06-10 12:00 | 99.57 | 87.63
2018-06-10 12:30 | 101.72 | 88.96
2018-06-10 13:00 | 99.02 | 85.93
2018-06-10 13:30 | 101.78 | 88.12
2018-06-10 14:00 | 102.35 | 87.63
2018-06-10 14:30 | 107.15 | 92.91
2018-06-10 15:00 | 101.96 | 87.39
2018-06-10 15:30 | 107.62 | 93.61
2018-06-10 16:00 | 104.4 | 91.24
2018-06-10 16:30 | 104.85 | 91.71
2018-06-10 17:00 | 103.37 | 89.33
2018-06-10 17:30 | 112.5 | 99.1
2018-06-10 18:00 | 112.19 | 98.76
2018-06-10 18:30 | 109.27 | 94.81
2018-06-10 19:00 | 111.63 | 98.98
2018-06-10 19:30 | 112.4 | 98.79
2018-06-10 20:00 | 113.34 | 99.5
2018-06-10 20:30 | 116.67 | 102.97
2018-06-10 21:00 | 113.92 | 101.11
2018-06-10 21:30 | 121.07 | 108.74
2018-06-10 22:00 | 112.49 | 99.48
2018-06-10 22:30 | 115.79 | 103.26
2018-06-10 23:00 | 106.3 | 93.39
2018-06-10 23:30 | 111.82 | 99.39
2018-06-11 | 109.6 | 97.3
2018-06-11 00:30 | 108.28 | 94.92
2018-06-11 01:00 | 107.58 | 93.67
2018-06-11 01:30 | 107.61 | 96.13
2018-06-11 02:00 | 102.48 | 90.59
2018-06-11 02:30 | 108.51 | 97.93
2018-06-11 03:00 | 102.76 | 91.14
2018-06-11 03:30 | 93.64 | 79.76
2018-06-11 04:00 | 96.88 | 83.78
2018-06-11 04:30 | 99.69 | 87.87
2018-06-11 05:00 | 101.49 | 89.89
2018-06-11 05:30 | 106.26 | 95.46
2018-06-11 06:00 | 101.51 | 89.96
2018-06-11 06:30 | 103.88 | 92.57
2018-06-11 07:00 | 103.57 | 92.1
2018-06-11 07:30 | 107.73 | 97.03
2018-06-11 08:00 | 103.79 | 92.66
2018-06-11 08:30 | 101.75 | 90.33
2018-06-11 09:00 | 102.52 | 90.84
2018-06-11 09:30 | 93.37 | 79.84
2018-06-11 10:00 | 100.24 | 87.72
2018-06-11 10:30 | 93.35 | 78.72
2018-06-11 11:00 | 99.04 | 85.65
2018-06-11 11:30 | 102.91 | 89.36
2018-06-11 12:00 | 94.84 | 80.16
2018-06-11 12:30 | 95.63 | 81.64
2018-06-11 13:00 | 94.95 | 82.47
2018-06-11 13:30 | 95.95 | 83.07
2018-06-11 14:00 | 90.65 | 76.55
2018-06-11 14:30 | 90.03 | 75.33
2018-06-11 15:00 | 102.26 | 89.47
2018-06-11 15:30 | 100.81 | 88.5
2018-06-11 16:00 | 101.21 | 90.44
2018-06-11 16:30 | 92.82 | 79.68
2018-06-11 17:00 | 105.71 | 94.33
2018-06-11 17:30 | 106.67 | 96.35
2018-06-11 18:00 | 107.9 | 96.85
2018-06-11 18:30 | 95.32 | 82.23
2018-06-11 19:00 | 103.33 | 90.93
2018-06-11 19:30 | 104.24 | 92.07
2018-06-11 20:00 | 103.3 | 91.47
2018-06-11 20:30 | 102.26 | 90.63
2018-06-11 21:00 | 95.87 | 83.38
2018-06-11 21:30 | 97.6 | 86.05
2018-06-11 22:00 | 99.36 | 86.96
2018-06-11 22:30 | 100.7 | 89.26
2018-06-11 23:00 | 96.69 | 85.04
2018-06-11 23:30 | 100.01 | 88.62
2018-06-12 | 97.23 | 84.95
2018-06-12 00:30 | 106.48 | 95.3
2018-06-12 01:00 | 105.64 | 93.17
2018-06-12 01:30 | 107.73 | 96.09
2018-06-12 02:00 | 110.69 | 99.76
2018-06-12 02:30 | 106.2 | 93.77
2018-06-12 03:00 | 107.56 | 95.37
2018-06-12 03:30 | 101.02 | 89.17
2018-06-12 04:00 | 101.38 | 89.31
2018-06-12 04:30 | 106.58 | 94.43
2018-06-12 05:00 | 105.17 | 93.42
2018-06-12 05:30 | 107 | 95.53
2018-06-12 06:00 | 108.05 | 96.32
2018-06-12 06:30 | 102.16 | 89.43
2018-06-12 07:00 | 106.49 | 94.83
2018-06-12 07:30 | 110.8 | 100.09
2018-06-12 08:00 | 95.71 | 83.26
2018-06-12 08:30 | 102.83 | 90.5
2018-06-12 09:00 | 97.09 | 83.28
2018-06-12 09:30 | 106.72 | 94.14
2018-06-12 10:00 | 109 | 96.45
2018-06-12 10:30 | 108.58 | 97
2018-06-12 11:00 | 107.17 | 95.55
2018-06-12 11:30 | 117.57 | 106.02
2018-06-12 12:00 | 107.49 | 95.42
2018-06-12 12:30 | 111.19 | 99.45
2018-06-12 13:00 | 117.31 | 105.7
2018-06-12 13:30 | 109.89 | 97.62
2018-06-12 14:00 | 112.03 | 99.21
2018-06-12 14:30 | 110.11 | 97.64
2018-06-12 15:00 | 116.79 | 103.24
2018-06-12 15:30 | 117.82 | 103.72
2018-06-12 16:00 | 119.96 | 106.21
2018-06-12 16:30 | 112.74 | 100.11
2018-06-12 17:00 | 113.3 | 101.12
2018-06-12 17:30 | 104.06 | 92.97
2018-06-12 18:00 | 99.71 | 87.96
2018-06-12 18:30 | 96.08 | 84.02
2018-06-12 19:00 | 105.37 | 93.01
2018-06-12 19:30 | 109.26 | 97.08
2018-06-12 20:00 | 108.31 | 96.53
2018-06-12 20:30 | 108.89 | 97.31
2018-06-12 21:00 | 109.56 | 98.75
2018-06-12 21:30 | 104.61 | 93.87
2018-06-12 22:00 | 98.4 | 87.33
2018-06-12 22:30 | 103.61 | 92.28
2018-06-12 23:00 | 85.41 | 70.8
2018-06-12 23:30 | 87.46 | 72.72
2018-06-13 | 89.57 | 76.77
2018-06-13 00:30 | 94.02 | 81.49
2018-06-13 01:00 | 94.94 | 82.66
2018-06-13 01:30 | 92.74 | 80.15
2018-06-13 02:00 | 93.22 | 80.93
2018-06-13 02:30 | 98.81 | 87.19
2018-06-13 03:00 | 97.13 | 84.88
2018-06-13 03:30 | 90.15 | 77.71
2018-06-13 04:00 | 92.3 | 79.93
2018-06-13 04:30 | 92.77 | 80.32
2018-06-13 05:00 | 93.51 | 81.11
2018-06-13 05:30 | 96.14 | 83.84
2018-06-13 06:00 | 94.41 | 81.41
2018-06-13 06:30 | 81.7 | 65.42
2018-06-13 07:00 | 91.42 | 76.62
2018-06-13 07:30 | 94.36 | 79.59
2018-06-13 08:00 | 101.77 | 86.48
2018-06-13 08:30 | 95.21 | 78.71
2018-06-13 09:00 | 92.03 | 76.08
2018-06-13 09:30 | 89.68 | 74.35
2018-06-13 10:00 | 90.2 | 76.36
2018-06-13 10:30 | 94.47 | 82.4
2018-06-13 11:00 | 97.84 | 86.33
2018-06-13 11:30 | 103.58 | 92.95
2018-06-13 12:00 | 113.26 | 102.13
2018-06-13 12:30 | 108.02 | 97.12
2018-06-13 13:00 | 108.46 | 97.41
2018-06-13 13:30 | 109.2 | 98.42
2018-06-13 14:00 | 105.48 | 93.79
2018-06-13 14:30 | 93.82 | 81.22
2018-06-13 15:00 | 88.76 | 75.84
2018-06-13 15:30 | 84.49 | 71.41
2018-06-13 16:00 | 94.71 | 82.61
2018-06-13 16:30 | 100.31 | 88.32
2018-06-13 17:00 | 96.34 | 83.83
2018-06-13 17:30 | 93.55 | 81.55
2018-06-13 18:00 | 96.25 | 83.41
2018-06-13 18:30 | 85.49 | 71.79
2018-06-13 19:00 | 83.34 | 68.63
2018-06-13 19:30 | 83.15 | 68.47
2018-06-13 20:00 | 91.82 | 78.03
2018-06-13 20:30 | 97.53 | 84.42
2018-06-13 21:00 | 97.71 | 84.55
2018-06-13 21:30 | 100.19 | 87.14
2018-06-13 22:00 | 98.22 | 85.19
2018-06-13 22:30 | 99.93 | 87.14
2018-06-13 23:00 | 100.63 | 88.23
2018-06-13 23:30 | 94.82 | 83.09
2018-06-14 | 100.52 | 88.43
2018-06-14 00:30 | 94.35 | 82.33
2018-06-14 01:00 | 101.81 | 89.91
2018-06-14 01:30 | 104.58 | 92.73
2018-06-14 02:00 | 104.31 | 92.06
2018-06-14 02:30 | 91.6 | 78.88
2018-06-14 03:00 | 92.36 | 79.41
2018-06-14 03:30 | 93.27 | 80.68
2018-06-14 04:00 | 94.79 | 82.72
2018-06-14 04:30 | 96.52 | 85.16
2018-06-14 05:00 | 90.02 | 78
2018-06-14 05:30 | 95.2 | 83.31
2018-06-14 06:00 | 86.81 | 72.75
2018-06-14 06:30 | 82.7 | 67.78
2018-06-14 07:00 | 89.46 | 76.05
2018-06-14 07:30 | 85.76 | 71.3
2018-06-14 08:00 | 93.3 | 80.67
2018-06-14 08:30 | 93.8 | 80.78
2018-06-14 09:00 | 95.93 | 83.39
2018-06-14 09:30 | 94.84 | 81.77
2018-06-14 10:00 | 101.78 | 89.28
2018-06-14 10:30 | 91.86 | 77.98
2018-06-14 11:00 | 104.09 | 92.22
2018-06-14 11:30 | 102.42 | 90.12
2018-06-14 12:00 | 100.53 | 88.02
2018-06-14 12:30 | 85.47 | 70.43
2018-06-14 13:00 | 91.15 | 77.53
2018-06-14 13:30 | 94.22 | 81.56
2018-06-14 14:00 | 90.49 | 78
2018-06-14 14:30 | 91.65 | 79.6
2018-06-14 15:00 | 83.09 | 69.21
2018-06-14 15:30 | 89.55 | 77.07
2018-06-14 16:00 | 89 | 76.67
2018-06-14 16:30 | 91.75 | 80.3
2018-06-14 17:00 | 95.94 | 84.6
2018-06-14 17:30 | 92.8 | 81.04
2018-06-14 18:00 | 99.2 | 87.76
2018-06-14 18:30 | 101.16 | 89.54
2018-06-14 19:00 | 101.57 | 89.23
2018-06-14 19:30 | 97.39 | 84.08
2018-06-14 20:00 | 99.71 | 86.4
2018-06-14 20:30 | 105.14 | 91.94
2018-06-14 21:00 | 107.91 | 95.58
2018-06-14 21:30 | 104.73 | 92.28
2018-06-14 22:00 | 108.09 | 94.22
2018-06-14 22:30 | 110.65 | 95.89
2018-06-14 23:00 | 103.92 | 90.02
2018-06-14 23:30 | 98.72 | 86.06
2018-06-15 | 97.86 | 85.61
2018-06-15 00:30 | 104.91 | 92.78
2018-06-15 01:00 | 104.77 | 93.07
2018-06-15 01:30 | 105.85 | 94.36
2018-06-15 02:00 | 101.96 | 90.52
2018-06-15 02:30 | 110.62 | 98.68
2018-06-15 03:00 | 101.06 | 90.04
2018-06-15 03:30 | 109.11 | 95.9
2018-06-15 04:00 | 108.48 | 95.59
2018-06-15 04:30 | 107.96 | 95.36
2018-06-15 05:00 | 106.02 | 93.4
2018-06-15 05:30 | 104.15 | 91.83
2018-06-15 06:00 | 104.33 | 90.23
2018-06-15 06:30 | 99.07 | 83.15
2018-06-15 07:00 | 103.04 | 87.39
2018-06-15 07:30 | 104.51 | 88.71
2018-06-15 08:00 | 109.85 | 93.29
2018-06-15 08:30 | 114.01 | 97.69
2018-06-15 09:00 | 109.16 | 94.98
2018-06-15 09:30 | 107.87 | 93.45
2018-06-15 10:00 | 107.27 | 92.5
2018-06-15 10:30 | 105.65 | 89.88
2018-06-15 11:00 | 108.68 | 91.32
2018-06-15 11:30 | 109.91 | 92.03
2018-06-15 12:00 | 110.79 | 94.19
2018-06-15 12:30 | 113.74 | 99.04
2018-06-15 13:00 | 112.59 | 97.5
2018-06-15 13:30 | 110.69 | 94.93
2018-06-15 14:00 | 108.67 | 91.58
2018-06-15 14:30 | 106.46 | 88.95
2018-06-15 15:00 | 104.88 | 86.52
2018-06-15 15:30 | 106.48 | 88.36
2018-06-15 16:00 | 109.19 | 91.2
2018-06-15 16:30 | 103.76 | 85.45
2018-06-15 17:00 | 105.84 | 89.06
2018-06-15 17:30 | 109.27 | 93.24
2018-06-15 18:00 | 106.36 | 90.09
2018-06-15 18:30 | 112.61 | 96.91
2018-06-15 19:00 | 119.19 | 104.06
2018-06-15 19:30 | 118.69 | 103.5
2018-06-15 20:00 | 122.59 | 107.39
2018-06-15 20:30 | 124.69 | 110.17
2018-06-15 21:00 | 118.3 | 104.03
2018-06-15 21:30 | 110.37 | 96.69
2018-06-15 22:00 | 113.72 | 99.83
2018-06-15 22:30 | 108.87 | 95.56
2018-06-15 23:00 | 109.04 | 95.59
2018-06-15 23:30 | 114.55 | 100.46
2018-06-16 | 115.11 | 101.08
2018-06-16 00:30 | 115.03 | 101.16
2018-06-16 01:00 | 116.52 | 102.87
2018-06-16 01:30 | 117.02 | 103.35
2018-06-16 02:00 | 112.18 | 98.68
2018-06-16 02:30 | 115.62 | 101.67
2018-06-16 03:00 | 112.05 | 98.23
2018-06-16 03:30 | 108.7 | 95.27
2018-06-16 04:00 | 105.77 | 92.11
2018-06-16 04:30 | 112.53 | 99.76
2018-06-16 05:00 | 111.11 | 97.74
2018-06-16 05:30 | 111.55 | 98.57
2018-06-16 06:00 | 111.9 | 98.89
2018-06-16 06:30 | 104.43 | 90.39
2018-06-16 07:00 | 99.94 | 86.96
2018-06-16 07:30 | 108.92 | 97.29
2018-06-16 08:00 | 101.07 | 88.97
2018-06-16 08:30 | 98.48 | 85.2
2018-06-16 09:00 | 104.48 | 89.65
2018-06-16 09:30 | 102.18 | 87.66
2018-06-16 10:00 | 95.26 | 81.14
2018-06-16 10:30 | 98.97 | 85.21
2018-06-16 11:00 | 104.14 | 89.78
2018-06-16 11:30 | 107.62 | 92.88
2018-06-16 12:00 | 110.45 | 95.52
2018-06-16 12:30 | 113.19 | 98.05
2018-06-16 13:00 | 101.05 | 86.69
2018-06-16 13:30 | 112.55 | 97.74
2018-06-16 14:00 | 111.26 | 96.4
2018-06-16 14:30 | 106.43 | 91.94
2018-06-16 15:00 | 101.86 | 86.8
2018-06-16 15:30 | 106.89 | 92.27
2018-06-16 16:00 | 108.2 | 92.49
2018-06-16 16:30 | 111.33 | 95.29
2018-06-16 17:00 | 114.89 | 99.35
2018-06-16 17:30 | 119.28 | 104.38
2018-06-16 18:00 | 116.44 | 100.94
2018-06-16 18:30 | 125.03 | 109.48
2018-06-16 19:00 | 119.72 | 104.74
2018-06-16 19:30 | 124.24 | 109.51
2018-06-16 20:00 | 116.03 | 101.04
2018-06-16 20:30 | 116.94 | 103.25
2018-06-16 21:00 | 111.83 | 98.3
2018-06-16 21:30 | 118.55 | 103.68
2018-06-16 22:00 | 116.35 | 101.27
2018-06-16 22:30 | 119.55 | 103.7
2018-06-16 23:00 | 115.08 | 100.83
2018-06-16 23:30 | 111.97 | 98.26
2018-06-17 | 120.58 | 106.86
2018-06-17 00:30 | 115.24 | 100.47
2018-06-17 01:00 | 111.66 | 97.63
2018-06-17 01:30 | 113.26 | 98.77
2018-06-17 02:00 | 112.15 | 98.11
2018-06-17 02:30 | 111.01 | 98.06
2018-06-17 03:00 | 107.85 | 94.54
2018-06-17 03:30 | 105.95 | 93.29
2018-06-17 04:00 | 112.45 | 99.4
2018-06-17 04:30 | 116.06 | 103.27
2018-06-17 05:00 | 116.37 | 103.87
2018-06-17 05:30 | 119.04 | 106.92
2018-06-17 06:00 | 114.78 | 102.63
2018-06-17 06:30 | 103.78 | 90.36
2018-06-17 07:00 | 112.91 | 99.25
2018-06-17 07:30 | 116.79 | 104.27
2018-06-17 08:00 | 123.73 | 111.06
2018-06-17 08:30 | 114.19 | 101.23
2018-06-17 09:00 | 110.43 | 97.03
2018-06-17 09:30 | 112.66 | 98.75
2018-06-17 10:00 | 108.3 | 95
2018-06-17 10:30 | 112.22 | 98.06
2018-06-17 11:00 | 110.85 | 97.05
2018-06-17 11:30 | 108.17 | 94.09
2018-06-17 12:00 | 107.97 | 94.58
2018-06-17 12:30 | 104.07 | 90.37
2018-06-17 13:00 | 107.77 | 94.39
2018-06-17 13:30 | 112.63 | 98.61
2018-06-17 14:00 | 117.28 | 103.22
2018-06-17 14:30 | 107.16 | 93.42
2018-06-17 15:00 | 103.71 | 89.8
2018-06-17 15:30 | 110.6 | 96.56
2018-06-17 16:00 | 115.46 | 101.84
2018-06-17 16:30 | 111.47 | 97.61
2018-06-17 17:00 | 115.12 | 101.65
2018-06-17 17:30 | 118.16 | 104.49
2018-06-17 18:00 | 116.91 | 102.84
2018-06-17 18:30 | 120.23 | 104.8
2018-06-17 19:00 | 130.19 | 115.78
2018-06-17 19:30 | 118.69 | 104.33
2018-06-17 20:00 | 125.13 | 109.87
2018-06-17 20:30 | 119.86 | 105.08
2018-06-17 21:00 | 124.22 | 111.63
2018-06-17 21:30 | 112.84 | 99.65
2018-06-17 22:00 | 118.09 | 104.94
2018-06-17 22:30 | 129.86 | 116.37
2018-06-17 23:00 | 113.7 | 100.65
2018-06-17 23:30 | 108.77 | 95.09
2018-06-18 | 113.79 | 100.97
2018-06-18 00:30 | 115.18 | 102.68
2018-06-18 01:00 | 117.42 | 103.77
2018-06-18 01:30 | 117.77 | 103.66
2018-06-18 02:00 | 118 | 103.52
2018-06-18 02:30 | 109.64 | 95.11
2018-06-18 03:00 | 112.3 | 96.96
2018-06-18 03:30 | 114.02 | 99.11
2018-06-18 04:00 | 114.51 | 99.96
2018-06-18 04:30 | 107.39 | 93.28
2018-06-18 05:00 | 112.16 | 98.63
2018-06-18 05:30 | 109.4 | 96
2018-06-18 06:00 | 107.7 | 95.01
2018-06-18 06:30 | 103.75 | 90.35
2018-06-18 07:00 | 107.78 | 94.51
2018-06-18 07:30 | 115.77 | 102.84
2018-06-18 08:00 | 118.03 | 105.2
2018-06-18 08:30 | 107.77 | 93.54
2018-06-18 09:00 | 106.27 | 90.54
2018-06-18 09:30 | 104.58 | 89.31
2018-06-18 10:00 | 108.11 | 92.17
2018-06-18 10:30 | 111.59 | 95.97
2018-06-18 11:00 | 94.7 | 81.11
2018-06-18 11:30 | 93.8 | 80.76
2018-06-18 12:00 | 96.23 | 82.74
2018-06-18 12:30 | 100.51 | 87.62
2018-06-18 13:00 | 105.1 | 92.57
2018-06-18 13:30 | 86.85 | 74.53
2018-06-18 14:00 | 88.68 | 75.31
2018-06-18 14:30 | 89.93 | 76.79
2018-06-18 15:00 | 87.4 | 74.8
2018-06-18 15:30 | 92.49 | 79.87
2018-06-18 16:00 | 98.41 | 85.62
2018-06-18 16:30 | 92.41 | 79.61
2018-06-18 17:00 | 94.91 | 81.46
2018-06-18 17:30 | 88.23 | 73.95
2018-06-18 18:00 | 97.65 | 85.11
2018-06-18 18:30 | 95.96 | 83.35
2018-06-18 19:00 | 104.94 | 91.64
2018-06-18 19:30 | 105.7 | 92.93
2018-06-18 20:00 | 101.32 | 88.76
2018-06-18 20:30 | 103.18 | 90.79
2018-06-18 21:00 | 100.37 | 88.26
2018-06-18 21:30 | 92.68 | 80.61
2018-06-18 22:00 | 98.34 | 87.13
2018-06-18 22:30 | 105.83 | 94.29
2018-06-18 23:00 | 99.95 | 87.43
2018-06-18 23:30 | 100.41 | 87.22
2018-06-19 | 107.73 | 94.07
2018-06-19 00:30 | 113.29 | 99.98
2018-06-19 01:00 | 119.57 | 106.56
2018-06-19 01:30 | 119.72 | 106.96
2018-06-19 02:00 | 121.63 | 108.75
2018-06-19 02:30 | 110.86 | 97.95
2018-06-19 03:00 | 110 | 97.69
2018-06-19 03:30 | 108.52 | 95.62
2018-06-19 04:00 | 106.15 | 93.47
2018-06-19 04:30 | 114.38 | 102.68
2018-06-19 05:00 | 105.97 | 93.58
2018-06-19 05:30 | 114.55 | 101.89
2018-06-19 06:00 | 113.25 | 100.44
2018-06-19 06:30 | 112.3 | 97.86
2018-06-19 07:00 | 108.52 | 94.91
2018-06-19 07:30 | 105.92 | 92.22
2018-06-19 08:00 | 101.52 | 87.42
2018-06-19 08:30 | 106.41 | 93.86
2018-06-19 09:00 | 106.53 | 93.21
2018-06-19 09:30 | 102.27 | 89.21
2018-06-19 10:00 | 103.18 | 89.68
2018-06-19 10:30 | 105.27 | 91.29
2018-06-19 11:00 | 93.68 | 79.45
2018-06-19 11:30 | 93.87 | 79.93
2018-06-19 12:00 | 91.5 | 77.4
2018-06-19 12:30 | 92.51 | 78.54
2018-06-19 13:00 | 99.98 | 86.35
2018-06-19 13:30 | 101.61 | 88.17
2018-06-19 14:00 | 110.12 | 96.01
2018-06-19 14:30 | 111.64 | 97.73
2018-06-19 15:00 | 102.5 | 88.62
2018-06-19 15:30 | 112.89 | 99.06
2018-06-19 16:00 | 117.31 | 104.08
2018-06-19 16:30 | 119.81 | 105.57
2018-06-19 17:00 | 108.81 | 94.12
2018-06-19 17:30 | 109.17 | 95.83
2018-06-19 18:00 | 111.99 | 99.2
2018-06-19 18:30 | 110.66 | 96.41
2018-06-19 19:00 | 115.59 | 102.22
2018-06-19 19:30 | 115.61 | 102.67
2018-06-19 20:00 | 112.91 | 100.62
2018-06-19 20:30 | 115.43 | 102.08
2018-06-19 21:00 | 120.77 | 107.13
2018-06-19 21:30 | 123.81 | 109.85
2018-06-19 22:00 | 124.38 | 110.57
2018-06-19 22:30 | 124.77 | 111.11
2018-06-19 23:00 | 126.44 | 112.48
2018-06-19 23:30 | 120.1 | 105.34
2018-06-20 | 120.86 | 107.52
2018-06-20 00:30 | 112.39 | 99.08
2018-06-20 01:00 | 110.33 | 97.99
2018-06-20 01:30 | 114.9 | 101.11
2018-06-20 02:00 | 114.51 | 101.1
2018-06-20 02:30 | 120.22 | 107.94
2018-06-20 03:00 | 114.91 | 101.88
2018-06-20 03:30 | 119.28 | 105.86
2018-06-20 04:00 | 115.16 | 102.64
2018-06-20 04:30 | 117.01 | 104.01
2018-06-20 05:00 | 111.1 | 98.52
2018-06-20 05:30 | 115.8 | 102.5
2018-06-20 06:00 | 114.89 | 101.43
2018-06-20 06:30 | 112.75 | 97.73
2018-06-20 07:00 | 114.66 | 100.14
2018-06-20 07:30 | 121.95 | 107.64
2018-06-20 08:00 | 115.15 | 99.86
2018-06-20 08:30 | 118.77 | 103.88
2018-06-20 09:00 | 115.85 | 99.34
2018-06-20 09:30 | 120.8 | 104.04
2018-06-20 10:00 | 113.74 | 97.76
2018-06-20 10:30 | 115.17 | 99.38
2018-06-20 11:00 | 112.34 | 96.93
2018-06-20 11:30 | 109.9 | 93.68
2018-06-20 12:00 | 103.65 | 86.33
2018-06-20 12:30 | 109.15 | 91.95
2018-06-20 13:00 | 107.66 | 90.15
2018-06-20 13:30 | 108.66 | 90.07
2018-06-20 14:00 | 110.56 | 92.03
2018-06-20 14:30 | 112.51 | 94.75
2018-06-20 15:00 | 114 | 96.86
2018-06-20 15:30 | 121 | 102.89
2018-06-20 16:00 | 116.91 | 99.04
2018-06-20 16:30 | 114.51 | 97.22
2018-06-20 17:00 | 110.02 | 93.22
2018-06-20 17:30 | 115.32 | 99.21
2018-06-20 18:00 | 116.04 | 100.1
2018-06-20 18:30 | 116.97 | 99.85
2018-06-20 19:00 | 121.68 | 106.1
2018-06-20 19:30 | 119.68 | 103.65
2018-06-20 20:00 | 125.77 | 109.71
2018-06-20 20:30 | 128.35 | 112.42
2018-06-20 21:00 | 129.39 | 114.49
2018-06-20 21:30 | 121.72 | 106.31
2018-06-20 22:00 | 128.22 | 113.42
2018-06-20 22:30 | 121.51 | 106.9
2018-06-20 23:00 | 118.41 | 103.83
2018-06-20 23:30 | 117.27 | 102.34
2018-06-21 | 105.64 | 90.87
2018-06-21 00:30 | 113.54 | 98.98
2018-06-21 01:00 | 119.81 | 105.97
2018-06-21 01:30 | 114.15 | 100.65
2018-06-21 02:00 | 112.12 | 98.49
2018-06-21 02:30 | 125.34 | 111.12
2018-06-21 03:00 | 123.38 | 109.75
2018-06-21 03:30 | 126.41 | 112.49
2018-06-21 04:00 | 122.85 | 108.53
2018-06-21 04:30 | 124.21 | 108.99
2018-06-21 05:00 | 119.36 | 104.28
2018-06-21 05:30 | 124.37 | 109.67
2018-06-21 06:00 | 120.06 | 105.07
2018-06-21 06:30 | 115.06 | 100.08
2018-06-21 07:00 | 118.86 | 105.79
2018-06-21 07:30 | 119.83 | 106.16
2018-06-21 08:00 | 115.07 | 102.17
2018-06-21 08:30 | 116.59 | 101.44
2018-06-21 09:00 | 113.12 | 97.04
2018-06-21 09:30 | 110.92 | 95.03
2018-06-21 10:00 | 117.46 | 103.41
2018-06-21 10:30 | 114.87 | 100.34
2018-06-21 11:00 | 117.23 | 101.75
2018-06-21 11:30 | 114.45 | 98.04
2018-06-21 12:00 | 113.37 | 96.1
2018-06-21 12:30 | 105.67 | 86.61
2018-06-21 13:00 | 109.04 | 91.41
2018-06-21 13:30 | 108.1 | 91
2018-06-21 14:00 | 111.79 | 95.31
2018-06-21 14:30 | 103.58 | 88.25
2018-06-21 15:00 | 99.56 | 84.68
2018-06-21 15:30 | 108.63 | 92.61
2018-06-21 16:00 | 109.34 | 92.98
2018-06-21 16:30 | 110.14 | 93.85
2018-06-21 17:00 | 106.54 | 91.19
2018-06-21 17:30 | 114.62 | 99.2
2018-06-21 18:00 | 109.78 | 93.22
2018-06-21 18:30 | 115.97 | 99.78
2018-06-21 19:00 | 115.92 | 102.03
2018-06-21 19:30 | 122.78 | 110.14
2018-06-21 20:00 | 112.37 | 99.31
2018-06-21 20:30 | 108.15 | 94.74
2018-06-21 21:00 | 102.03 | 89.8
2018-06-21 21:30 | 99.86 | 87.11
2018-06-21 22:00 | 107.82 | 95.73
2018-06-21 22:30 | 98.36 | 87
2018-06-21 23:00 | 109.11 | 97.64
2018-06-21 23:30 | 111.88 | 98.82
2018-06-22 | 109.04 | 94.45
2018-06-22 00:30 | 106.38 | 92.31
2018-06-22 01:00 | 106.93 | 94.16
2018-06-22 01:30 | 110.1 | 96.45
2018-06-22 02:00 | 112.34 | 99.07
2018-06-22 02:30 | 117.44 | 105.07
2018-06-22 03:00 | 124.09 | 112.13
2018-06-22 03:30 | 110.78 | 98.09
2018-06-22 04:00 | 115.13 | 102.32
2018-06-22 04:30 | 112.15 | 99.03
2018-06-22 05:00 | 112.94 | 98.73
2018-06-22 05:30 | 122.48 | 108.97
2018-06-22 06:00 | 121.37 | 108.26
2018-06-22 06:30 | 111.39 | 96.84
2018-06-22 07:00 | 106.9 | 94.59
2018-06-22 07:30 | 116.56 | 105.63
2018-06-22 08:00 | 110.8 | 98.91
2018-06-22 08:30 | 102.05 | 89.96
2018-06-22 09:00 | 104.93 | 92.48
2018-06-22 09:30 | 115.97 | 102.18
2018-06-22 10:00 | 103.61 | 89.19
2018-06-22 10:30 | 104.8 | 90.5
2018-06-22 11:00 | 112.53 | 98.89
2018-06-22 11:30 | 108.11 | 93
2018-06-22 12:00 | 109.63 | 93.93
2018-06-22 12:30 | 108.97 | 94.79
2018-06-22 13:00 | 114.61 | 102.23
2018-06-22 13:30 | 114.54 | 101.65
2018-06-22 14:00 | 114.04 | 101.37
2018-06-22 14:30 | 113.47 | 99.96
2018-06-22 15:00 | 108.56 | 94.94
2018-06-22 15:30 | 105.15 | 91.62
2018-06-22 16:00 | 109.74 | 95.15
2018-06-22 16:30 | 113.57 | 98.84
2018-06-22 17:00 | 115.21 | 100.95
2018-06-22 17:30 | 125.68 | 111.36
2018-06-22 18:00 | 110.27 | 94.65
2018-06-22 18:30 | 117.53 | 101.63
2018-06-22 19:00 | 112.54 | 98.36
2018-06-22 19:30 | 112.53 | 98.02
2018-06-22 20:00 | 115.65 | 102.99
2018-06-22 20:30 | 114.52 | 101.61
2018-06-22 21:00 | 112.86 | 100.19
2018-06-22 21:30 | 114.6 | 102.48
2018-06-22 22:00 | 111.3 | 98.88
2018-06-22 22:30 | 116.4 | 104.27
2018-06-22 23:00 | 110 | 97.68
2018-06-22 23:30 | 97.97 | 84.77
2018-06-23 | 97.91 | 84.93
2018-06-23 00:30 | 106.91 | 95.1
2018-06-23 01:00 | 108.97 | 97.22
2018-06-23 01:30 | 103.1 | 90.88
2018-06-23 02:00 | 110.21 | 98
2018-06-23 02:30 | 108 | 95.88
2018-06-23 03:00 | 110 | 97.08
2018-06-23 03:30 | 104.23 | 91.86
2018-06-23 04:00 | 110.5 | 97.75
2018-06-23 04:30 | 116.31 | 103.33
2018-06-23 05:00 | 114.72 | 101.88
2018-06-23 05:30 | 117.06 | 104.25
2018-06-23 06:00 | 109.15 | 95.55
2018-06-23 06:30 | 111.48 | 96.45
2018-06-23 07:00 | 117.37 | 102.62
2018-06-23 07:30 | 118.52 | 103.09
2018-06-23 08:00 | 121.11 | 106.48
2018-06-23 08:30 | 118.14 | 104.28
2018-06-23 09:00 | 125.7 | 111.35
2018-06-23 09:30 | 118.59 | 104.19
2018-06-23 10:00 | 118.81 | 105.07
2018-06-23 10:30 | 115.73 | 100.29
2018-06-23 11:00 | 111.58 | 95.92
2018-06-23 11:30 | 107.89 | 91.37
2018-06-23 12:00 | 100.54 | 85.82
2018-06-23 12:30 | 105.78 | 92.07
2018-06-23 13:00 | 98.02 | 83.79
2018-06-23 13:30 | 95.1 | 81.76
2018-06-23 14:00 | 105.26 | 91.66
2018-06-23 14:30 | 110.01 | 95.1
2018-06-23 15:00 | 117.42 | 101.58
2018-06-23 15:30 | 116.72 | 99.95
2018-06-23 16:00 | 112.02 | 96.14
2018-06-23 16:30 | 116.08 | 97.94
2018-06-23 17:00 | 118.4 | 100.11
2018-06-23 17:30 | 119.05 | 102.77
2018-06-23 18:00 | 124.53 | 108.46
2018-06-23 18:30 | 110.52 | 95.38
2018-06-23 19:00 | 119.9 | 107.28
2018-06-23 19:30 | 130.5 | 117.44
2018-06-23 20:00 | 131.73 | 118.42
2018-06-23 20:30 | 121.41 | 107.6
2018-06-23 21:00 | 121.79 | 108.35
2018-06-23 21:30 | 124.86 | 111.67
2018-06-23 22:00 | 126.86 | 114.13
2018-06-23 22:30 | 111.44 | 99.19
2018-06-23 23:00 | 117.86 | 105.71
2018-06-23 23:30 | 112.61 | 100.49
2018-06-24 | 113.63 | 101.44
2018-06-24 00:30 | 109.97 | 98.07
2018-06-24 01:00 | 109.33 | 96.83
2018-06-24 01:30 | 111.47 | 99.28
2018-06-24 02:00 | 114.78 | 102.35
2018-06-24 02:30 | 110.27 | 97.68
2018-06-24 03:00 | 110.09 | 98.17
2018-06-24 03:30 | 106.62 | 94.65
2018-06-24 04:00 | 107.95 | 96.51
2018-06-24 04:30 | 110.42 | 99.43
2018-06-24 05:00 | 109.97 | 99.08
2018-06-24 05:30 | 107.72 | 96.9
2018-06-24 06:00 | 108.52 | 97.76
2018-06-24 06:30 | 107.4 | 95.78
2018-06-24 07:00 | 108.05 | 97.75
2018-06-24 07:30 | 104.67 | 93.8
2018-06-24 08:00 | 105.62 | 94.45
2018-06-24 08:30 | 102.26 | 90.64
2018-06-24 09:00 | 100.34 | 88.53
2018-06-24 09:30 | 101.23 | 89.89
2018-06-24 10:00 | 109.12 | 98.5
2018-06-24 10:30 | 106.47 | 94.71
2018-06-24 11:00 | 105.58 | 94.53
2018-06-24 11:30 | 106.6 | 95.52
2018-06-24 12:00 | 108.6 | 96.52
2018-06-24 12:30 | 110.78 | 99.49
2018-06-24 13:00 | 104.55 | 93.05
2018-06-24 13:30 | 111.32 | 99.9
2018-06-24 14:00 | 103.53 | 91.46
2018-06-24 14:30 | 106.7 | 94.33
2018-06-24 15:00 | 109.72 | 97.71
2018-06-24 15:30 | 111.87 | 99.71
2018-06-24 16:00 | 116.74 | 104.92
2018-06-24 16:30 | 116.51 | 105.48
2018-06-24 17:00 | 125.71 | 114.25
2018-06-24 17:30 | 122.79 | 109.62
2018-06-24 18:00 | 124.28 | 109.74
2018-06-24 18:30 | 122.97 | 109.01
2018-06-24 19:00 | 125.02 | 112.61
2018-06-24 19:30 | 124.53 | 111.99
2018-06-24 20:00 | 120.69 | 108.87
2018-06-24 20:30 | 126.3 | 114.79
2018-06-24 21:00 | 117.93 | 105.73
2018-06-24 21:30 | 119.91 | 107.5
2018-06-24 22:00 | 112.5 | 99.94
2018-06-24 22:30 | 114.82 | 102.62
2018-06-24 23:00 | 114.25 | 102.65
2018-06-24 23:30 | 110.85 | 99.49
2018-06-25 | 109.1 | 97.56
2018-06-25 00:30 | 112.66 | 100.98
2018-06-25 01:00 | 108.27 | 96.78
2018-06-25 01:30 | 103.51 | 91.66
2018-06-25 02:00 | 108.85 | 97.61
2018-06-25 02:30 | 103.21 | 91.59
2018-06-25 03:00 | 105.03 | 93.37
2018-06-25 03:30 | 100.96 | 89.44
2018-06-25 04:00 | 105.09 | 93.66
2018-06-25 04:30 | 106.64 | 95.61
2018-06-25 05:00 | 107.83 | 97.12
2018-06-25 05:30 | 109.13 | 98.49
2018-06-25 06:00 | 106.13 | 94.87
2018-06-25 06:30 | 110.74 | 98.65
2018-06-25 07:00 | 115.27 | 103.62
2018-06-25 07:30 | 112.39 | 100.55
2018-06-25 08:00 | 118.28 | 106
2018-06-25 08:30 | 113.77 | 101.43
2018-06-25 09:00 | 121.74 | 109.6
2018-06-25 09:30 | 115.01 | 103.35
2018-06-25 10:00 | 112.19 | 100.34
2018-06-25 10:30 | 111.82 | 99.44
2018-06-25 11:00 | 116.32 | 105.1
2018-06-25 11:30 | 114.97 | 103.53
2018-06-25 12:00 | 114.54 | 103.22
2018-06-25 12:30 | 116.82 | 104.94
2018-06-25 13:00 | 115.41 | 102.66
2018-06-25 13:30 | 118.37 | 105.48
2018-06-25 14:00 | 108.26 | 95.19
2018-06-25 14:30 | 113.92 | 101.08
2018-06-25 15:00 | 113.96 | 102.65
2018-06-25 15:30 | 107.5 | 94.26
2018-06-25 16:00 | 110.34 | 97.57
2018-06-25 16:30 | 115.36 | 102.11
2018-06-25 17:00 | 116.5 | 103.26
2018-06-25 17:30 | 114.71 | 100.25
2018-06-25 18:00 | 121.51 | 108.93
2018-06-25 18:30 | 115.28 | 103.07
2018-06-25 19:00 | 121.6 | 110.93
2018-06-25 19:30 | 121.47 | 110.52
2018-06-25 20:00 | 124.09 | 112.11
2018-06-25 20:30 | 131.01 | 116.52
2018-06-25 21:00 | 122.6 | 109.77
2018-06-25 21:30 | 124.6 | 112.04
2018-06-25 22:00 | 113.42 | 101.65
2018-06-25 22:30 | 111.33 | 98.91
2018-06-25 23:00 | 115.64 | 102.58
2018-06-25 23:30 | 111.69 | 98.99
2018-06-26 | 118.46 | 106.11
2018-06-26 00:30 | 117.56 | 104.97
2018-06-26 01:00 | 119.23 | 107.72
2018-06-26 01:30 | 122.6 | 111.17
2018-06-26 02:00 | 116.46 | 104.54
2018-06-26 02:30 | 125.44 | 112.98
2018-06-26 03:00 | 119.96 | 107.01
2018-06-26 03:30 | 122.65 | 109.9
2018-06-26 04:00 | 113.2 | 100.51
2018-06-26 04:30 | 113.01 | 101.07
2018-06-26 05:00 | 108.72 | 97.09
2018-06-26 05:30 | 108.8 | 96.25
2018-06-26 06:00 | 102.89 | 89.4
2018-06-26 06:30 | 102.02 | 89.34
2018-06-26 07:00 | 106.65 | 94.85
2018-06-26 07:30 | 116.38 | 104.91
2018-06-26 08:00 | 113.02 | 101.07
2018-06-26 08:30 | 100.93 | 88.83
2018-06-26 09:00 | 103.68 | 90.41
2018-06-26 09:30 | 109.82 | 96.93
2018-06-26 10:00 | 104.24 | 91.82
2018-06-26 10:30 | 102.25 | 89.5
2018-06-26 11:00 | 96.34 | 83.36
2018-06-26 11:30 | 93.01 | 79.48
2018-06-26 12:00 | 101.01 | 88
2018-06-26 12:30 | 103.16 | 90.35
2018-06-26 13:00 | 103.17 | 89.66
2018-06-26 13:30 | 102.08 | 90.26
2018-06-26 14:00 | 103.98 | 91.14
2018-06-26 14:30 | 105.51 | 92.28
2018-06-26 15:00 | 105.61 | 93.73
2018-06-26 15:30 | 104.03 | 91.57
2018-06-26 16:00 | 108.84 | 96.43
2018-06-26 16:30 | 106.36 | 93.68
2018-06-26 17:00 | 111.04 | 97.87
2018-06-26 17:30 | 112.73 | 99.49
2018-06-26 18:00 | 110.53 | 97.54
2018-06-26 18:30 | 106.24 | 92.64
2018-06-26 19:00 | 115.48 | 102.59
2018-06-26 19:30 | 107.18 | 94.5
2018-06-26 20:00 | 112.82 | 100.55
2018-06-26 20:30 | 107.61 | 95.44
2018-06-26 21:00 | 106.1 | 94.44
2018-06-26 21:30 | 104.13 | 92.13
2018-06-26 22:00 | 102.06 | 90.24
2018-06-26 22:30 | 99.61 | 88.13
2018-06-26 23:00 | 101.53 | 90.01
2018-06-26 23:30 | 96.98 | 85.36
2018-06-27 | 100.84 | 89.04
2018-06-27 00:30 | 99.19 | 86.94
2018-06-27 01:00 | 99.62 | 87.94
2018-06-27 01:30 | 96.47 | 83.59
2018-06-27 02:00 | 98.88 | 86.6
2018-06-27 02:30 | 100.93 | 88.85
2018-06-27 03:00 | 101.38 | 89.66
2018-06-27 03:30 | 95.63 | 83.34
2018-06-27 04:00 | 96.29 | 83.75
2018-06-27 04:30 | 89.02 | 76.76
2018-06-27 05:00 | 96.84 | 84.88
2018-06-27 05:30 | 106.31 | 94.4
2018-06-27 06:00 | 102.58 | 91.07
2018-06-27 06:30 | 97.25 | 85.41
2018-06-27 07:00 | 96.75 | 84.34
2018-06-27 07:30 | 102.99 | 91.54
2018-06-27 08:00 | 105.08 | 93.2
2018-06-27 08:30 | 101.33 | 89.89
2018-06-27 09:00 | 104.22 | 93.09
2018-06-27 09:30 | 92.13 | 80.2
2018-06-27 10:00 | 93.33 | 81.27
2018-06-27 10:30 | 92.21 | 79.6
2018-06-27 11:00 | 88.83 | 75.46
2018-06-27 11:30 | 98.32 | 85.92
2018-06-27 12:00 | 90.95 | 78.2
2018-06-27 12:30 | 89.05 | 76.18
2018-06-27 13:00 | 94.84 | 82.53
2018-06-27 13:30 | 96.03 | 84.09
2018-06-27 14:00 | 93.11 | 80.82
2018-06-27 14:30 | 97.87 | 85.61
2018-06-27 15:00 | 95.02 | 82.53
2018-06-27 15:30 | 94.59 | 81.82
2018-06-27 16:00 | 100.24 | 83.91
2018-06-27 16:30 | 93.19 | 75.56
2018-06-27 17:00 | 95.83 | 78.02
2018-06-27 17:30 | 96.53 | 79.74
2018-06-27 18:00 | 99.51 | 83.98
2018-06-27 18:30 | 95.29 | 78.98
2018-06-27 19:00 | 99.41 | 83.28
2018-06-27 19:30 | 104.56 | 87.98
2018-06-27 20:00 | 106.57 | 92.27
2018-06-27 20:30 | 100.03 | 84.77
2018-06-27 21:00 | 103.78 | 88.05
2018-06-27 21:30 | 108.75 | 94.1
2018-06-27 22:00 | 105.59 | 89.95
2018-06-27 22:30 | 103.62 | 88.51
2018-06-27 23:00 | 105.05 | 90.39
2018-06-27 23:30 | 100.35 | 87.52
2018-06-28 | 100.51 | 88.02
2018-06-28 00:30 | 100.99 | 89.14
2018-06-28 01:00 | 99.36 | 87.56
2018-06-28 01:30 | 101.87 | 90.45
2018-06-28 02:00 | 103.86 | 92.24
2018-06-28 02:30 | 99.76 | 88.23
2018-06-28 03:00 | 100.39 | 89.19
2018-06-28 03:30 | 103.75 | 92.63
2018-06-28 04:00 | 103.39 | 92.11
2018-06-28 04:30 | 107.96 | 97.3
2018-06-28 05:00 | 103.46 | 92.2
2018-06-28 05:30 | 96.62 | 85.2
2018-06-28 06:00 | 106.59 | 95.72
2018-06-28 06:30 | 103.16 | 91.22
2018-06-28 07:00 | 102.9 | 91.97
2018-06-28 07:30 | 111.67 | 100.9
2018-06-28 08:00 | 111.73 | 100.91
2018-06-28 08:30 | 106.68 | 95.52
2018-06-28 09:00 | 102.76 | 90.78
2018-06-28 09:30 | 116.79 | 105.68
2018-06-28 10:00 | 104.17 | 92.46
2018-06-28 10:30 | 102.21 | 89.86
2018-06-28 11:00 | 103.4 | 91.9
2018-06-28 11:30 | 95.89 | 87.11
2018-06-28 12:00 | 95.41 | 87.27
2018-06-28 12:30 | 98.36 | 90.68
2018-06-28 13:00 | 96.22 | 88.71
2018-06-28 13:30 | 95.2 | 87.49
2018-06-28 14:00 | 99.47 | 87.89
2018-06-28 14:30 | 97.37 | 84.13
2018-06-28 15:00 | 98.9 | 85.98
2018-06-28 15:30 | 95.39 | 82.15
2018-06-28 16:00 | 93.8 | 80.47
2018-06-28 16:30 | 95.08 | 83.1
2018-06-28 17:00 | 96.96 | 85.06
2018-06-28 17:30 | 97.79 | 86.19
2018-06-28 18:00 | 104.96 | 92.58
2018-06-28 18:30 | 95.54 | 82.3
2018-06-28 19:00 | 103.75 | 90.52
2018-06-28 19:30 | 106.33 | 93.18
2018-06-28 20:00 | 110.69 | 98.01
2018-06-28 20:30 | 120.73 | 108.22
2018-06-28 21:00 | 121.3 | 108.51
2018-06-28 21:30 | 112.88 | 100.78
2018-06-28 22:00 | 108.17 | 96.56
2018-06-28 22:30 | 110.71 | 99.41
2018-06-28 23:00 | 112.96 | 100.46
2018-06-28 23:30 | 107.19 | 94.33
2018-06-29 | 105.69 | 93.28
2018-06-29 00:30 | 106.93 | 94.76
2018-06-29 01:00 | 106.29 | 94.53
2018-06-29 01:30 | 110.22 | 98.2
2018-06-29 02:00 | 106.87 | 95
2018-06-29 02:30 | 110.51 | 96.92
2018-06-29 03:00 | 111.45 | 96.78
2018-06-29 03:30 | 108.43 | 94.95
2018-06-29 04:00 | 105.04 | 91.79
2018-06-29 04:30 | 110.48 | 96.72
2018-06-29 05:00 | 107.07 | 92.76
2018-06-29 05:30 | 108.33 | 95.36
2018-06-29 06:00 | 111.08 | 98.66
2018-06-29 06:30 | 100.36 | 87.91
2018-06-29 07:00 | 116.18 | 103.28
2018-06-29 07:30 | 117.44 | 105.62
2018-06-29 08:00 | 120.94 | 109.08
2018-06-29 08:30 | 130.77 | 119.67
2018-06-29 09:00 | 116.67 | 104.09
2018-06-29 09:30 | 111.7 | 97.35
2018-06-29 10:00 | 112.3 | 97.45
2018-06-29 10:30 | 115.6 | 100.96
2018-06-29 11:00 | 116.72 | 102.25
2018-06-29 11:30 | 115.05 | 100.78
2018-06-29 12:00 | 102.62 | 88.07
2018-06-29 12:30 | 106.38 | 92.38
2018-06-29 13:00 | 114.08 | 99.11
2018-06-29 13:30 | 108.82 | 94.22
2018-06-29 14:00 | 116.81 | 102.14
2018-06-29 14:30 | 115.22 | 101.66
2018-06-29 15:00 | 103.55 | 89.12
2018-06-29 15:30 | 104.34 | 89.65
2018-06-29 16:00 | 112.94 | 97.51
2018-06-29 16:30 | 108.94 | 93.36
2018-06-29 17:00 | 106.29 | 91.33
2018-06-29 17:30 | 112.85 | 98.1
2018-06-29 18:00 | 115.12 | 99.71
2018-06-29 18:30 | 98.73 | 83.1
2018-06-29 19:00 | 106.32 | 92.9
2018-06-29 19:30 | 105.48 | 93.09
2018-06-29 20:00 | 105.82 | 92.58
2018-06-29 20:30 | 102.61 | 88.45
2018-06-29 21:00 | 108.11 | 93.73
2018-06-29 21:30 | 106.44 | 92.75
2018-06-29 22:00 | 105.86 | 90.91
2018-06-29 22:30 | 104.64 | 90.1
2018-06-29 23:00 | 100.6 | 86.55
2018-06-29 23:30 | 102.88 | 89.44
2018-06-30 | 104.75 | 92.42
2018-06-30 00:30 | 102.38 | 90.37
2018-06-30 01:00 | 104.24 | 91.58
2018-06-30 01:30 | 106.07 | 92.65
2018-06-30 02:00 | 111.33 | 97.27
2018-06-30 02:30 | 107.48 | 93.86
2018-06-30 03:00 | 100.69 | 86.27
2018-06-30 03:30 | 108.26 | 94.15
2018-06-30 04:00 | 101.38 | 88.91
2018-06-30 04:30 | 102.46 | 90.21
2018-06-30 05:00 | 109.83 | 97.37
2018-06-30 05:30 | 112.87 | 100.02
2018-06-30 06:00 | 109.59 | 96.07
2018-06-30 06:30 | 104.02 | 88.91
2018-06-30 07:00 | 104.15 | 89.89
2018-06-30 07:30 | 114.8 | 101.42
2018-06-30 08:00 | 110.35 | 97.05
2018-06-30 08:30 | 100.47 | 87.46
2018-06-30 09:00 | 110.04 | 97.14
2018-06-30 09:30 | 100.41 | 87.07
2018-06-30 10:00 | 108.97 | 95.98
2018-06-30 10:30 | 114.91 | 102.19
2018-06-30 11:00 | 103.36 | 88.48
2018-06-30 11:30 | 107.91 | 93.19
2018-06-30 12:00 | 109.66 | 95.72
2018-06-30 12:30 | 112.59 | 98.19
2018-06-30 13:00 | 111.56 | 97.17
2018-06-30 13:30 | 112.24 | 97.29
2018-06-30 14:00 | 113.92 | 97.81
2018-06-30 14:30 | 110.08 | 94.3
2018-06-30 15:00 | 103.01 | 87.36
2018-06-30 15:30 | 117.54 | 101.24
2018-06-30 16:00 | 110.71 | 95.18
2018-06-30 16:30 | 104.87 | 91.15
2018-06-30 17:00 | 111.99 | 97.47
2018-06-30 17:30 | 111.84 | 95.95
2018-06-30 18:00 | 114.78 | 99.61
2018-06-30 18:30 | 109.92 | 93.3
2018-06-30 19:00 | 111.39 | 96.64
2018-06-30 19:30 | 117.43 | 102.42
2018-06-30 20:00 | 115.05 | 100.35
2018-06-30 20:30 | 115.53 | 101.7
2018-06-30 21:00 | 118.51 | 105.3
2018-06-30 21:30 | 110.63 | 96.95
2018-06-30 22:00 | 103.19 | 89.32
2018-06-30 22:30 | 110.03 | 95.38
2018-06-30 23:00 | 109.18 | 94.34
2018-06-30 23:30 | 111.52 | 96.26
2018-07-01 | 107.63 | 93.74
2018-07-01 00:30 | 112.6 | 98.88
2018-07-01 01:00 | 106.04 | 91.85
2018-07-01 01:30 | 103.49 | 88.48
2018-07-01 02:00 | 98.08 | 82.86
2018-07-01 02:30 | 96.04 | 81.06
2018-07-01 03:00 | 92.92 | 78.2
2018-07-01 03:30 | 98.75 | 84.53
2018-07-01 04:00 | 98.14 | 83.82
2018-07-01 04:30 | 101.07 | 87.59
2018-07-01 05:00 | 102.24 | 88.71
2018-07-01 05:30 | 104.69 | 91.6
2018-07-01 06:00 | 104.59 | 91.42
2018-07-01 06:30 | 96.95 | 82.65
2018-07-01 07:00 | 96.61 | 82.31
2018-07-01 07:30 | 102.47 | 89.52
2018-07-01 08:00 | 105.12 | 91.42
2018-07-01 08:30 | 106.31 | 92.42
2018-07-01 09:00 | 102.21 | 87.24
2018-07-01 09:30 | 102.21 | 87.7
2018-07-01 10:00 | 98.95 | 84.43
2018-07-01 10:30 | 98.08 | 84.13
2018-07-01 11:00 | 95.98 | 82.4
2018-07-01 11:30 | 95.52 | 81.29
2018-07-01 12:00 | 98.51 | 84.52
2018-07-01 12:30 | 117.72 | 104.27
2018-07-01 13:00 | 107.9 | 93.52
2018-07-01 13:30 | 111.46 | 96.6
2018-07-01 14:00 | 113.78 | 100.73
2018-07-01 14:30 | 111.24 | 98.2
2018-07-01 15:00 | 112.85 | 98.73
2018-07-01 15:30 | 108.88 | 94.96
2018-07-01 16:00 | 119.81 | 106.64
2018-07-01 16:30 | 110.08 | 96.99
2018-07-01 17:00 | 114.26 | 101.37
2018-07-01 17:30 | 108.48 | 95.79
2018-07-01 18:00 | 111.21 | 97.89
2018-07-01 18:30 | 108.23 | 95.03
2018-07-01 19:00 | 110.71 | 98.59
2018-07-01 19:30 | 117.15 | 104.82
2018-07-01 20:00 | 123.5 | 110.52
2018-07-01 20:30 | 115.73 | 101.4
2018-07-01 21:00 | 121.09 | 106.7
2018-07-01 21:30 | 105.09 | 91.59
2018-07-01 22:00 | 102.36 | 90.69
2018-07-01 22:30 | 109.09 | 97.78
2018-07-01 23:00 | 115.04 | 103.52
2018-07-01 23:30 | 118.82 | 106.75
2018-07-02 | 115.06 | 102.38
2018-07-02 00:30 | 112.92 | 98.88
2018-07-02 01:00 | 107.82 | 94.07
2018-07-02 01:30 | 101.61 | 88.04
2018-07-02 02:00 | 97.86 | 84.2
2018-07-02 02:30 | 98.92 | 85.55
2018-07-02 03:00 | 100.51 | 86.66
2018-07-02 03:30 | 98.86 | 84.92
2018-07-02 04:00 | 98.87 | 85.5
2018-07-02 04:30 | 92.31 | 79.18
2018-07-02 05:00 | 95.87 | 83.31
2018-07-02 05:30 | 95.38 | 82.48
2018-07-02 06:00 | 93.53 | 80.68
2018-07-02 06:30 | 87.83 | 73.99
2018-07-02 07:00 | 91.63 | 78.73
2018-07-02 07:30 | 97.52 | 84.47
2018-07-02 08:00 | 97 | 83.82
2018-07-02 08:30 | 99.65 | 85.55
2018-07-02 09:00 | 100.84 | 85.81
2018-07-02 09:30 | 101.65 | 86.42
2018-07-02 10:00 | 101.93 | 87.28
2018-07-02 10:30 | 109.79 | 95.18
2018-07-02 11:00 | 103.59 | 87.67
2018-07-02 11:30 | 100.64 | 84.32
2018-07-02 12:00 | 105.81 | 89.15
2018-07-02 12:30 | 107.64 | 91.75
2018-07-02 13:00 | 105.58 | 90.62
2018-07-02 13:30 | 94.96 | 80.66
2018-07-02 14:00 | 103.13 | 89.63
2018-07-02 14:30 | 98.82 | 84.35
2018-07-02 15:00 | 100.03 | 86.35
2018-07-02 15:30 | 99.01 | 85.79
2018-07-02 16:00 | 102.14 | 88.46
2018-07-02 16:30 | 97.02 | 84.12
2018-07-02 17:00 | 101.65 | 88.98
2018-07-02 17:30 | 100.74 | 87.16
2018-07-02 18:00 | 107.53 | 94.92
2018-07-02 18:30 | 102.89 | 88.52
2018-07-02 19:00 | 113.61 | 99.95
2018-07-02 19:30 | 110.02 | 96.63
2018-07-02 20:00 | 108.14 | 95.25
2018-07-02 20:30 | 105.6 | 92.36
2018-07-02 21:00 | 107.83 | 94.21
2018-07-02 21:30 | 102.16 | 87.93
2018-07-02 22:00 | 101.66 | 87.26
2018-07-02 22:30 | 101.84 | 87.57
2018-07-02 23:00 | 108.58 | 95.26
2018-07-02 23:30 | 113.13 | 100.06
2018-07-03 | 102.83 | 90.1
2018-07-03 00:30 | 106.34 | 93.18
2018-07-03 01:00 | 108.71 | 95.05
2018-07-03 01:30 | 107.21 | 94.44
2018-07-03 02:00 | 107.22 | 94.15
2018-07-03 02:30 | 103.66 | 90.45
2018-07-03 03:00 | 101.59 | 89.07
2018-07-03 03:30 | 97.33 | 83.98
2018-07-03 04:00 | 97.57 | 83.64
2018-07-03 04:30 | 93.6 | 79.18
2018-07-03 05:00 | 95.27 | 81.25
2018-07-03 05:30 | 107.45 | 93.98
2018-07-03 06:00 | 102.45 | 88.76
2018-07-03 06:30 | 103.57 | 89.33
2018-07-03 07:00 | 100.51 | 86.56
2018-07-03 07:30 | 96.01 | 81.58
2018-07-03 08:00 | 91.65 | 76.24
2018-07-03 08:30 | 89.24 | 73.77
2018-07-03 09:00 | 86.44 | 69.07
2018-07-03 09:30 | 87.79 | 70.8
2018-07-03 10:00 | 86.44 | 69.58
2018-07-03 10:30 | 94.59 | 79.7
2018-07-03 11:00 | 99.41 | 85.06
2018-07-03 11:30 | 90.39 | 74.27
2018-07-03 12:00 | 89.86 | 74.08
2018-07-03 12:30 | 88.45 | 71.87
2018-07-03 13:00 | 86.99 | 71.06
2018-07-03 13:30 | 84.31 | 66.96
2018-07-03 14:00 | 87.48 | 70.7
2018-07-03 14:30 | 90.24 | 73.9
2018-07-03 15:00 | 94.7 | 77.24
2018-07-03 15:30 | 95.74 | 79.05
2018-07-03 16:00 | 94.78 | 78.05
2018-07-03 16:30 | 101.26 | 85.87
2018-07-03 17:00 | 104.65 | 89.97
2018-07-03 17:30 | 104.93 | 90.86
2018-07-03 18:00 | 105.15 | 90.06
2018-07-03 18:30 | 93.24 | 77.15
2018-07-03 19:00 | 93.07 | 77.14
2018-07-03 19:30 | 92.55 | 76.8
2018-07-03 20:00 | 93.82 | 79.24
2018-07-03 20:30 | 98.29 | 85.07
2018-07-03 21:00 | 98.3 | 85.07
2018-07-03 21:30 | 107.4 | 93.12
2018-07-03 22:00 | 109.25 | 95.15
2018-07-03 22:30 | 107.34 | 93.29
2018-07-03 23:00 | 104.73 | 92.06
2018-07-03 23:30 | 100.12 | 86.59
2018-07-04 | 97.91 | 83.58
2018-07-04 00:30 | 103.02 | 88.81
2018-07-04 01:00 | 106.81 | 92.4
2018-07-04 01:30 | 106.96 | 93.3
2018-07-04 02:00 | 101.25 | 87.16
2018-07-04 02:30 | 111.87 | 98.45
2018-07-04 03:00 | 111.34 | 98.76
2018-07-04 03:30 | 108.43 | 95.63
2018-07-04 04:00 | 110.11 | 96.72
2018-07-04 04:30 | 111.24 | 98.18
2018-07-04 05:00 | 108.76 | 94.68
2018-07-04 05:30 | 106.35 | 91.85
2018-07-04 06:00 | 109.08 | 95.18
2018-07-04 06:30 | 106.59 | 91.13
2018-07-04 07:00 | 106.54 | 89.91
2018-07-04 07:30 | 109.98 | 93.44
2018-07-04 08:00 | 101.76 | 86.23
2018-07-04 08:30 | 99.54 | 85.29
2018-07-04 09:00 | 95.52 | 82.85
2018-07-04 09:30 | 93.47 | 81.25
2018-07-04 10:00 | 92.63 | 80.22
2018-07-04 10:30 | 89.38 | 75.42
2018-07-04 11:00 | 91.58 | 76.74
2018-07-04 11:30 | 96.62 | 83.26
2018-07-04 12:00 | 91.13 | 77.21
2018-07-04 12:30 | 101.41 | 89.19
2018-07-04 13:00 | 96.5 | 82.49
2018-07-04 13:30 | 98.31 | 85.1
2018-07-04 14:00 | 106.59 | 93.91
2018-07-04 14:30 | 100.15 | 85.43
2018-07-04 15:00 | 100.76 | 86
2018-07-04 15:30 | 105.15 | 91.47
2018-07-04 16:00 | 109.01 | 95.32
2018-07-04 16:30 | 109.82 | 97.06
2018-07-04 17:00 | 109.97 | 96.47
2018-07-04 17:30 | 110.23 | 96.71
2018-07-04 18:00 | 111.09 | 98.14
2018-07-04 18:30 | 112.78 | 97.81
2018-07-04 19:00 | 112.85 | 98.36
2018-07-04 19:30 | 113.95 | 100.33
2018-07-04 20:00 | 113.88 | 100.56
2018-07-04 20:30 | 110.7 | 97.43
2018-07-04 21:00 | 108.98 | 95.8
2018-07-04 21:30 | 104.86 | 92.25
2018-07-04 22:00 | 115.12 | 102.3
2018-07-04 22:30 | 118.48 | 106.46
2018-07-04 23:00 | 105.3 | 93.37
2018-07-04 23:30 | 106.89 | 94.52
2018-07-05 | 110.95 | 98.99
2018-07-05 00:30 | 104.79 | 91.63
2018-07-05 01:00 | 106.19 | 91.79
2018-07-05 01:30 | 107.91 | 94.2
2018-07-05 02:00 | 111.07 | 97.26
2018-07-05 02:30 | 103.79 | 90.04
2018-07-05 03:00 | 102.72 | 88.98
2018-07-05 03:30 | 107.28 | 93.13
2018-07-05 04:00 | 112.82 | 99.27
2018-07-05 04:30 | 104.15 | 90.36
2018-07-05 05:00 | 103.61 | 90.38
2018-07-05 05:30 | 115 | 102.2
2018-07-05 06:00 | 111.03 | 98.04
2018-07-05 06:30 | 104.23 | 89.86
2018-07-05 07:00 | 114.22 | 100.77
2018-07-05 07:30 | 113.41 | 99.9
2018-07-05 08:00 | 110.23 | 95.97
2018-07-05 08:30 | 108.75 | 93.91
2018-07-05 09:00 | 106.43 | 91.52
2018-07-05 09:30 | 105.37 | 92.01
2018-07-05 10:00 | 99.69 | 84.62
2018-07-05 10:30 | 100.72 | 85.12
2018-07-05 11:00 | 104.64 | 89.74
2018-07-05 11:30 | 100.08 | 82.57
2018-07-05 12:00 | 100.5 | 81.25
2018-07-05 12:30 | 102.5 | 84.34
2018-07-05 13:00 | 97.96 | 79.94
2018-07-05 13:30 | 101.19 | 84.69
2018-07-05 14:00 | 105.37 | 89.64
2018-07-05 14:30 | 105.52 | 89.33
2018-07-05 15:00 | 106.22 | 89.27
2018-07-05 15:30 | 105.29 | 87.94
2018-07-05 16:00 | 105.96 | 89.31
2018-07-05 16:30 | 108.61 | 93.01
2018-07-05 17:00 | 119.29 | 106.02
2018-07-05 17:30 | 114.98 | 100.67
2018-07-05 18:00 | 110.85 | 97.1
2018-07-05 18:30 | 106.17 | 92.3
2018-07-05 19:00 | 107.14 | 94.91
2018-07-05 19:30 | 108.06 | 96.35
2018-07-05 20:00 | 108.53 | 96.76
2018-07-05 20:30 | 111.67 | 99.18
2018-07-05 21:00 | 100.95 | 88.99
2018-07-05 21:30 | 104.69 | 93.11
2018-07-05 22:00 | 103.18 | 91.62
2018-07-05 22:30 | 99.67 | 87.59
2018-07-05 23:00 | 104.17 | 92.01
2018-07-05 23:30 | 97.32 | 82.68
2018-07-06 | 99.88 | 86.2
2018-07-06 00:30 | 106.38 | 93.73
2018-07-06 01:00 | 107.31 | 94.92
2018-07-06 01:30 | 100.65 | 87.24
2018-07-06 02:00 | 96.74 | 82.1
2018-07-06 02:30 | 100.86 | 86.86
2018-07-06 03:00 | 98.47 | 83.98
2018-07-06 03:30 | 95.1 | 78.65
2018-07-06 04:00 | 96.84 | 81.01
2018-07-06 04:30 | 103.94 | 89.3
2018-07-06 05:00 | 101.92 | 87.24
2018-07-06 05:30 | 105.69 | 92.1
2018-07-06 06:00 | 100.2 | 85.42
2018-07-06 06:30 | 95.34 | 78.91
2018-07-06 07:00 | 91.76 | 76.18
2018-07-06 07:30 | 94.93 | 80.09
2018-07-06 08:00 | 105.4 | 92
2018-07-06 08:30 | 98.25 | 82.91
2018-07-06 09:00 | 97.9 | 83.47
2018-07-06 09:30 | 103.27 | 87.89
2018-07-06 10:00 | 105.72 | 90.1
2018-07-06 10:30 | 108.78 | 95.21
2018-07-06 11:00 | 105.61 | 90.43
2018-07-06 11:30 | 99.69 | 85.19
2018-07-06 12:00 | 92.34 | 81.86
2018-07-06 12:30 | 100.25 | 91.68
2018-07-06 13:00 | 97.81 | 89.61
2018-07-06 13:30 | 97.24 | 88.91
2018-07-06 14:00 | 91.72 | 83.07
2018-07-06 14:30 | 100.37 | 86.45
2018-07-06 15:00 | 97.97 | 82.49
2018-07-06 15:30 | 91.2 | 74.58
2018-07-06 16:00 | 93.92 | 77.62
2018-07-06 16:30 | 95.78 | 80.42
2018-07-06 17:00 | 103.92 | 91.94
2018-07-06 17:30 | 102.8 | 91.7
2018-07-06 18:00 | 93.99 | 80.57
2018-07-06 18:30 | 93.98 | 80.31
2018-07-06 19:00 | 100.29 | 87.71
2018-07-06 19:30 | 101.22 | 89.06
2018-07-06 20:00 | 101.41 | 87.96
2018-07-06 20:30 | 97.71 | 84
2018-07-06 21:00 | 95.62 | 81.15
2018-07-06 21:30 | 96.31 | 83.14
2018-07-06 22:00 | 98.7 | 85.03
2018-07-06 22:30 | 102.6 | 89.02
2018-07-06 23:00 | 103.82 | 91.02
2018-07-06 23:30 | 101.54 | 88.38
2018-07-07 | 107.3 | 94.86
2018-07-07 00:30 | 101.35 | 88.38
2018-07-07 01:00 | 98.44 | 84.92
2018-07-07 01:30 | 97.84 | 83.66
2018-07-07 02:00 | 99.11 | 85.35
2018-07-07 02:30 | 101.93 | 89.13
2018-07-07 03:00 | 102.53 | 90.13
2018-07-07 03:30 | 103.43 | 91.4
2018-07-07 04:00 | 102.91 | 90.58
2018-07-07 04:30 | 99.76 | 86.69
2018-07-07 05:00 | 103.85 | 91.73
2018-07-07 05:30 | 97.52 | 85.57
2018-07-07 06:00 | 101.25 | 88.95
2018-07-07 06:30 | 96.73 | 82.44
2018-07-07 07:00 | 106.17 | 93.97
2018-07-07 07:30 | 100.01 | 85.59
2018-07-07 08:00 | 102.1 | 88.61
2018-07-07 08:30 | 103.64 | 90.91
2018-07-07 09:00 | 99.76 | 85.88
2018-07-07 09:30 | 101.59 | 88.21
2018-07-07 10:00 | 98.69 | 85.67
2018-07-07 10:30 | 99.55 | 85.47
2018-07-07 11:00 | 101.29 | 87.49
2018-07-07 11:30 | 97.5 | 83.59
2018-07-07 12:00 | 99.74 | 86.52
2018-07-07 12:30 | 98.8 | 85.16
2018-07-07 13:00 | 105.96 | 93.33
2018-07-07 13:30 | 103.17 | 90.26
2018-07-07 14:00 | 106.27 | 94.04
2018-07-07 14:30 | 105.23 | 93.75
2018-07-07 15:00 | 105.89 | 94.3
2018-07-07 15:30 | 106.37 | 94.14
2018-07-07 16:00 | 102.81 | 88.83
2018-07-07 16:30 | 96.42 | 82.24
2018-07-07 17:00 | 101.07 | 88.88
2018-07-07 17:30 | 104.46 | 92.93
2018-07-07 18:00 | 101.57 | 89.79
2018-07-07 18:30 | 102 | 89.01
2018-07-07 19:00 | 98.23 | 85.68
2018-07-07 19:30 | 101.1 | 88.93
2018-07-07 20:00 | 104.84 | 92.85
2018-07-07 20:30 | 108.13 | 95.69
2018-07-07 21:00 | 101.52 | 89.1
2018-07-07 21:30 | 98.23 | 85.46
2018-07-07 22:00 | 109.26 | 98.03
2018-07-07 22:30 | 107.46 | 95.93
2018-07-07 23:00 | 99.03 | 86.82
2018-07-07 23:30 | 99.08 | 86.54
2018-07-08 | 93.47 | 79.36
2018-07-08 00:30 | 96.39 | 82.92
2018-07-08 01:00 | 96.58 | 81.8
2018-07-08 01:30 | 102.24 | 87.87
2018-07-08 02:00 | 102.1 | 87.97
2018-07-08 02:30 | 99.53 | 84.96
2018-07-08 03:00 | 104.2 | 91.04
2018-07-08 03:30 | 106.48 | 93.2
2018-07-08 04:00 | 101.53 | 87.43
2018-07-08 04:30 | 105.01 | 91.99
2018-07-08 05:00 | 107.65 | 95.85
2018-07-08 05:30 | 105.58 | 92.64
2018-07-08 06:00 | 106.65 | 94.49
2018-07-08 06:30 | 102.42 | 88.16
2018-07-08 07:00 | 102.92 | 89.21
2018-07-08 07:30 | 105.22 | 91.65
2018-07-08 08:00 | 105.3 | 91.69
2018-07-08 08:30 | 105.84 | 92.35
2018-07-08 09:00 | 112.39 | 101.08
2018-07-08 09:30 | 100.35 | 86.04
2018-07-08 10:00 | 101.39 | 88.51
2018-07-08 10:30 | 106.99 | 94.4
2018-07-08 11:00 | 105.79 | 92.51
2018-07-08 11:30 | 101.48 | 86.32
2018-07-08 12:00 | 103.51 | 88.34
2018-07-08 12:30 | 100.88 | 86.07
2018-07-08 13:00 | 101.5 | 87.24
2018-07-08 13:30 | 95.19 | 80.41
2018-07-08 14:00 | 103.8 | 91.34
2018-07-08 14:30 | 105.6 | 92.5
2018-07-08 15:00 | 99.39 | 85.62
2018-07-08 15:30 | 101.88 | 88.75
2018-07-08 16:00 | 100.47 | 86.41
2018-07-08 16:30 | 99.59 | 86.34
2018-07-08 17:00 | 110.15 | 98.77
2018-07-08 17:30 | 108.5 | 97.03
2018-07-08 18:00 | 109.2 | 96.81
2018-07-08 18:30 | 103.92 | 90.51
2018-07-08 19:00 | 105.06 | 92.58
2018-07-08 19:30 | 116.3 | 103.45
2018-07-08 20:00 | 115.14 | 102.35
2018-07-08 20:30 | 108.74 | 96.49
2018-07-08 21:00 | 105.29 | 92.47
2018-07-08 21:30 | 111.5 | 99.58
2018-07-08 22:00 | 117.06 | 105.65
2018-07-08 22:30 | 113.16 | 102.57
2018-07-08 23:00 | 106.69 | 94.89
2018-07-08 23:30 | 103.92 | 91.16
2018-07-09 | 107.75 | 95.53
2018-07-09 00:30 | 103.25 | 91.35
2018-07-09 01:00 | 104.41 | 92.97
2018-07-09 01:30 | 104.81 | 93.25
2018-07-09 02:00 | 107.91 | 96.57
2018-07-09 02:30 | 102.87 | 91.64
2018-07-09 03:00 | 104.23 | 91.51
2018-07-09 03:30 | 95.64 | 81.32
2018-07-09 04:00 | 95.93 | 82.64
2018-07-09 04:30 | 96.54 | 83.34
2018-07-09 05:00 | 98.92 | 85.62
2018-07-09 05:30 | 98.78 | 85.9
2018-07-09 06:00 | 98.32 | 85.52
2018-07-09 06:30 | 90.55 | 74.73
2018-07-09 07:00 | 96.34 | 82.89
2018-07-09 07:30 | 102.48 | 90.62
2018-07-09 08:00 | 103.07 | 90.78
2018-07-09 08:30 | 94.34 | 80.04
2018-07-09 09:00 | 94.01 | 77.96
2018-07-09 09:30 | 90.28 | 71.12
2018-07-09 10:00 | 90.51 | 68.51
2018-07-09 10:30 | 88.1 | 67.07
2018-07-09 11:00 | 89.63 | 66.98
2018-07-09 11:30 | 93.93 | 70.34
2018-07-09 12:00 | 94.94 | 70.44
2018-07-09 12:30 | 96.71 | 73.04
2018-07-09 13:00 | 96.73 | 73.35
2018-07-09 13:30 | 95.56 | 74.37
2018-07-09 14:00 | 100.68 | 79.7
2018-07-09 14:30 | 101.77 | 81.73
2018-07-09 15:00 | 96.95 | 77.42
2018-07-09 15:30 | 97.41 | 79.7
2018-07-09 16:00 | 99.84 | 81.37
2018-07-09 16:30 | 100.32 | 81.5
2018-07-09 17:00 | 100.81 | 82.81
2018-07-09 17:30 | 104.1 | 88.14
2018-07-09 18:00 | 108.05 | 94.09
2018-07-09 18:30 | 100.94 | 86.22
2018-07-09 19:00 | 104.88 | 91.53
2018-07-09 19:30 | 106.75 | 93.03
2018-07-09 20:00 | 102.59 | 87.25
2018-07-09 20:30 | 101.91 | 86.9
2018-07-09 21:00 | 101.03 | 85.54
2018-07-09 21:30 | 100.92 | 85.14
2018-07-09 22:00 | 101.94 | 86.34
2018-07-09 22:30 | 103.13 | 87.8
2018-07-09 23:00 | 102.01 | 86.25
2018-07-09 23:30 | 99.66 | 82.74
2018-07-10 | 100.27 | 82.26
2018-07-10 00:30 | 105.07 | 88.44
2018-07-10 01:00 | 104.3 | 88.15
2018-07-10 01:30 | 103.27 | 87.2
2018-07-10 02:00 | 101.42 | 84.69
2018-07-10 02:30 | 103.05 | 87.74
2018-07-10 03:00 | 104.16 | 88.59
2018-07-10 03:30 | 98.5 | 80.9
2018-07-10 04:00 | 95.81 | 78.23
2018-07-10 04:30 | 96.78 | 80.03
2018-07-10 05:00 | 96.12 | 79.88
2018-07-10 05:30 | 96.67 | 80.87
2018-07-10 06:00 | 96.67 | 79.75
2018-07-10 06:30 | 93.07 | 75.21
2018-07-10 07:00 | 96.04 | 79.54
2018-07-10 07:30 | 96.01 | 78.73
2018-07-10 08:00 | 92.1 | 73.78
2018-07-10 08:30 | 96 | 77.67
2018-07-10 09:00 | 93.99 | 74.7
2018-07-10 09:30 | 95.43 | 77.59
2018-07-10 10:00 | 96.15 | 74.81
2018-07-10 10:30 | 98.7 | 78.09
2018-07-10 11:00 | 98.33 | 77.44
2018-07-10 11:30 | 97.22 | 75.88
2018-07-10 12:00 | 93.99 | 71.08
2018-07-10 12:30 | 96.78 | 74.74
2018-07-10 13:00 | 98.06 | 76.48
2018-07-10 13:30 | 97.7 | 75.23
2018-07-10 14:00 | 96.97 | 73.35
2018-07-10 14:30 | 94.16 | 71.59
2018-07-10 15:00 | 97 | 75.95
2018-07-10 15:30 | 94.74 | 72.47
2018-07-10 16:00 | 92.65 | 69.45
2018-07-10 16:30 | 94.46 | 73.44
2018-07-10 17:00 | 94.17 | 75.24
2018-07-10 17:30 | 98.29 | 82.01
2018-07-10 18:00 | 97.02 | 81.17
2018-07-10 18:30 | 97.5 | 81.74
2018-07-10 19:00 | 100.63 | 87.2
2018-07-10 19:30 | 97.3 | 81.32
2018-07-10 20:00 | 105.3 | 92.24
2018-07-10 20:30 | 103.98 | 90.91
2018-07-10 21:00 | 98.37 | 81.74
2018-07-10 21:30 | 106.05 | 90.61
2018-07-10 22:00 | 105.55 | 90.78
2018-07-10 22:30 | 100.76 | 84.12
2018-07-10 23:00 | 101.61 | 84.97
2018-07-10 23:30 | 99.55 | 83.11
2018-07-11 | 99.36 | 82.74
2018-07-11 00:30 | 105.8 | 89.92
2018-07-11 01:00 | 104.53 | 88.35
2018-07-11 01:30 | 103.18 | 86.09
2018-07-11 02:00 | 101.36 | 84.28
2018-07-11 02:30 | 100.5 | 81.89
2018-07-11 03:00 | 99.44 | 81.01
2018-07-11 03:30 | 98.57 | 79.22
2018-07-11 04:00 | 102.63 | 84.23
2018-07-11 04:30 | 99.81 | 80.22
2018-07-11 05:00 | 98.45 | 79.01
2018-07-11 05:30 | 97.56 | 78
2018-07-11 06:00 | 94.96 | 74.73
2018-07-11 06:30 | 89.51 | 68.58
2018-07-11 07:00 | 97.48 | 77.43
2018-07-11 07:30 | 102.84 | 85.33
2018-07-11 08:00 | 99.04 | 78.87
2018-07-11 08:30 | 102.2 | 82.75
2018-07-11 09:00 | 103.66 | 86.16
2018-07-11 09:30 | 93.58 | 70.51
2018-07-11 10:00 | 90.62 | 64.1
2018-07-11 10:30 | 91.75 | 63
2018-07-11 11:00 | 88.37 | 56.76
2018-07-11 11:30 | 90.01 | 57.52
2018-07-11 12:00 | 90.49 | 54.23
2018-07-11 12:30 | 88.75 | 53.44
2018-07-11 13:00 | 93.6 | 61.99
2018-07-11 13:30 | 96.23 | 65.89
2018-07-11 14:00 | 94.07 | 61.91
2018-07-11 14:30 | 95.5 | 67.09
2018-07-11 15:00 | 95.86 | 70.58
2018-07-11 15:30 | 96.64 | 71.59
2018-07-11 16:00 | 94 | 69.84
2018-07-11 16:30 | 97.32 | 76.64
2018-07-11 17:00 | 92.2 | 68.43
2018-07-11 17:30 | 95.68 | 73.24
2018-07-11 18:00 | 99.54 | 80.42
2018-07-11 18:30 | 93.25 | 73.61
2018-07-11 19:00 | 99.1 | 80.67
2018-07-11 19:30 | 101.85 | 83.41
2018-07-11 20:00 | 99.35 | 80.71
2018-07-11 20:30 | 97.94 | 77.98
2018-07-11 21:00 | 97.86 | 75.89
2018-07-11 21:30 | 96.13 | 75.5
2018-07-11 22:00 | 97.12 | 79.27
2018-07-11 22:30 | 102.11 | 84.95
2018-07-11 23:00 | 102.79 | 85.13
2018-07-11 23:30 | 96.18 | 75.17
2018-07-12 | 100.65 | 79.34
2018-07-12 00:30 | 95.04 | 73.96
2018-07-12 01:00 | 93.25 | 76.37
2018-07-12 01:30 | 88.93 | 68.35
2018-07-12 02:00 | 95.46 | 76.46
2018-07-12 02:30 | 95.56 | 77.65
2018-07-12 03:00 | 89.36 | 69.1
2018-07-12 03:30 | 94.33 | 75.71
2018-07-12 04:00 | 98.03 | 75.25
2018-07-12 04:30 | 99.33 | 74.2
2018-07-12 05:00 | 103.52 | 83.27
2018-07-12 05:30 | 103.51 | 84.59
2018-07-12 06:00 | 99.24 | 80.05
2018-07-12 06:30 | 95.55 | 75.22
2018-07-12 07:00 | 106.59 | 87.76
2018-07-12 07:30 | 101.78 | 82.35
2018-07-12 08:00 | 99.15 | 79.36
2018-07-12 08:30 | 97.77 | 75.16
2018-07-12 09:00 | 101.31 | 78.16
2018-07-12 09:30 | 100.12 | 75.09
2018-07-12 10:00 | 98.73 | 72.55
2018-07-12 10:30 | 96.26 | 72.06
2018-07-12 11:00 | 96.03 | 71.07
2018-07-12 11:30 | 95.21 | 69.6
2018-07-12 12:00 | 96.19 | 71.46
2018-07-12 12:30 | 100.82 | 77.97
2018-07-12 13:00 | 99.79 | 77.94
2018-07-12 13:30 | 97.86 | 73.51
2018-07-12 14:00 | 106.13 | 86.74
2018-07-12 14:30 | 102.66 | 80.31
2018-07-12 15:00 | 98.67 | 76.88
2018-07-12 15:30 | 102.13 | 80.39
2018-07-12 16:00 | 101.21 | 77.9
2018-07-12 16:30 | 96.41 | 74.91
2018-07-12 17:00 | 105.26 | 86.72
2018-07-12 17:30 | 105.53 | 87.52
2018-07-12 18:00 | 102.57 | 83.27
2018-07-12 18:30 | 97.25 | 76.42
2018-07-12 19:00 | 102.35 | 84.9
2018-07-12 19:30 | 105.59 | 88.92
2018-07-12 20:00 | 104.88 | 88.6
2018-07-12 20:30 | 107.92 | 93.16
2018-07-12 21:00 | 101.6 | 84.33
2018-07-12 21:30 | 100.34 | 81.37
2018-07-12 22:00 | 103.46 | 84.78
2018-07-12 22:30 | 101.49 | 82.26
2018-07-12 23:00 | 100.78 | 80.07
2018-07-12 23:30 | 100.51 | 79.74
2018-07-13 | 103.56 | 84.17
2018-07-13 00:30 | 98.09 | 77.28
2018-07-13 01:00 | 101.2 | 81.43
2018-07-13 01:30 | 100.15 | 80.05
2018-07-13 02:00 | 101.51 | 81.68
2018-07-13 02:30 | 103.35 | 83.56
2018-07-13 03:00 | 100.12 | 78.64
2018-07-13 03:30 | 104.43 | 85.01
2018-07-13 04:00 | 109.19 | 90.1
2018-07-13 04:30 | 106.02 | 86.91
2018-07-13 05:00 | 112.39 | 96.26
2018-07-13 05:30 | 120.52 | 107.53
2018-07-13 06:00 | 112.46 | 97.43
2018-07-13 06:30 | 108.03 | 91.24
2018-07-13 07:00 | 106.91 | 90.24
2018-07-13 07:30 | 115.43 | 101.72
2018-07-13 08:00 | 116.48 | 103.92
2018-07-13 08:30 | 111.95 | 96.94
2018-07-13 09:00 | 108.44 | 90.67
2018-07-13 09:30 | 109.6 | 92.79
2018-07-13 10:00 | 112.69 | 95.35
2018-07-13 10:30 | 111.88 | 94.9
2018-07-13 11:00 | 114.86 | 99.24
2018-07-13 11:30 | 111.65 | 93.77
2018-07-13 12:00 | 108.92 | 90.84
2018-07-13 12:30 | 112.08 | 94.91
2018-07-13 13:00 | 113.7 | 97.62
2018-07-13 13:30 | 104.85 | 85.79
2018-07-13 14:00 | 111.05 | 93.15
2018-07-13 14:30 | 110.67 | 92.62
2018-07-13 15:00 | 106.32 | 87.87
2018-07-13 15:30 | 100.02 | 80.87
2018-07-13 16:00 | 102.6 | 84.84
2018-07-13 16:30 | 103.06 | 85.94
2018-07-13 17:00 | 102.68 | 85.78
2018-07-13 17:30 | 106.91 | 90.23
2018-07-13 18:00 | 113.8 | 99.76
2018-07-13 18:30 | 110.64 | 95.75
2018-07-13 19:00 | 122.88 | 110.39
2018-07-13 19:30 | 119.16 | 106.47
2018-07-13 20:00 | 115.48 | 102.72
2018-07-13 20:30 | 116.93 | 103.86
2018-07-13 21:00 | 115.47 | 100.95
2018-07-13 21:30 | 108.12 | 92.11
2018-07-13 22:00 | 106.78 | 90.88
2018-07-13 22:30 | 112.02 | 95.24
2018-07-13 23:00 | 106.19 | 88.33
2018-07-13 23:30 | 99.1 | 79.93
2018-07-14 | 99.4 | 81.27
2018-07-14 00:30 | 97.59 | 79.4
2018-07-14 01:00 | 99.67 | 81
2018-07-14 01:30 | 109.24 | 93.51
2018-07-14 02:00 | 107.45 | 90.7
2018-07-14 02:30 | 108.27 | 91.65
2018-07-14 03:00 | 111.08 | 93.87
2018-07-14 03:30 | 102.69 | 84.61
2018-07-14 04:00 | 103.24 | 86.54
2018-07-14 04:30 | 105.26 | 88.18
2018-07-14 05:00 | 106.09 | 90.75
2018-07-14 05:30 | 102.16 | 85.74
2018-07-14 06:00 | 105.81 | 89.53
2018-07-14 06:30 | 102.07 | 84.74
2018-07-14 07:00 | 111.49 | 97.25
2018-07-14 07:30 | 108.23 | 94.16
2018-07-14 08:00 | 114.78 | 101.76
2018-07-14 08:30 | 104.33 | 86.41
2018-07-14 09:00 | 106.7 | 90.78
2018-07-14 09:30 | 108.66 | 91.86
2018-07-14 10:00 | 107.85 | 91.57
2018-07-14 10:30 | 97.07 | 76.56
2018-07-14 11:00 | 101.04 | 82.61
2018-07-14 11:30 | 112.3 | 95.69
2018-07-14 12:00 | 112.2 | 95.82
2018-07-14 12:30 | 109.95 | 93.75
2018-07-14 13:00 | 105.98 | 89.28
2018-07-14 13:30 | 102.25 | 82.41
2018-07-14 14:00 | 97.8 | 77.54
2018-07-14 14:30 | 103.08 | 84.09
2018-07-14 15:00 | 107.04 | 88.73
2018-07-14 15:30 | 110.8 | 93.24
2018-07-14 16:00 | 108.63 | 91.36
2018-07-14 16:30 | 109.24 | 94.64
2018-07-14 17:00 | 113.23 | 99.23
2018-07-14 17:30 | 114.59 | 102.2
2018-07-14 18:00 | 115.45 | 102.93
2018-07-14 18:30 | 117.09 | 104.51
2018-07-14 19:00 | 127.48 | 117.41
2018-07-14 19:30 | 119.71 | 108.19
2018-07-14 20:00 | 118.63 | 107.36
2018-07-14 20:30 | 119.49 | 107.33
2018-07-14 21:00 | 115.35 | 101.83
2018-07-14 21:30 | 113.45 | 99.28
2018-07-14 22:00 | 116.57 | 102.65
2018-07-14 22:30 | 115.66 | 101.74
2018-07-14 23:00 | 118.08 | 104.1
2018-07-14 23:30 | 115.88 | 102.3
2018-07-15 | 114.94 | 100.99
2018-07-15 00:30 | 124.29 | 112.04
2018-07-15 01:00 | 119.37 | 106.19
2018-07-15 01:30 | 116.33 | 101.82
2018-07-15 02:00 | 115.55 | 100.64
2018-07-15 02:30 | 119.32 | 105.25
2018-07-15 03:00 | 116.39 | 101.66
2018-07-15 03:30 | 114.43 | 99.7
2018-07-15 04:00 | 112.34 | 96.85
2018-07-15 04:30 | 111.68 | 96.44
2018-07-15 05:00 | 116.81 | 102.79
2018-07-15 05:30 | 117.88 | 103.32
2018-07-15 06:00 | 111.32 | 95.49
2018-07-15 06:30 | 106.31 | 88.94
2018-07-15 07:00 | 108.49 | 91.32
2018-07-15 07:30 | 110.55 | 95.72
2018-07-15 08:00 | 116.51 | 102.62
2018-07-15 08:30 | 117.51 | 103.96
2018-07-15 09:00 | 118.73 | 104.24
2018-07-15 09:30 | 116.78 | 101.76
2018-07-15 10:00 | 113.85 | 97.51
2018-07-15 10:30 | 112.8 | 95.8
2018-07-15 11:00 | 111.02 | 92.45
2018-07-15 11:30 | 113.36 | 95.99
2018-07-15 12:00 | 110.8 | 92.26
2018-07-15 12:30 | 106.49 | 87.09
2018-07-15 13:00 | 102.59 | 81.54
2018-07-15 13:30 | 101.2 | 79.49
2018-07-15 14:00 | 100.82 | 79
2018-07-15 14:30 | 101.51 | 81.47
2018-07-15 15:00 | 105.87 | 87
2018-07-15 15:30 | 110.39 | 93.55
2018-07-15 16:00 | 109.15 | 92.76
2018-07-15 16:30 | 111.94 | 96.55
2018-07-15 17:00 | 115.16 | 100.43
2018-07-15 17:30 | 110.17 | 96.15
2018-07-15 18:00 | 116.46 | 103.7
2018-07-15 18:30 | 110.19 | 95.58
2018-07-15 19:00 | 115.49 | 102.71
2018-07-15 19:30 | 116.34 | 104.95
2018-07-15 20:00 | 118.67 | 107.07
2018-07-15 20:30 | 118.1 | 105.81
2018-07-15 21:00 | 114.73 | 100.98
2018-07-15 21:30 | 113.29 | 98.07
2018-07-15 22:00 | 110.28 | 95.42
2018-07-15 22:30 | 113.67 | 97.87
2018-07-15 23:00 | 111.92 | 94.95
2018-07-15 23:30 | 116.3 | 101.09
2018-07-16 | 123.01 | 109.1
2018-07-16 00:30 | 112.53 | 96.94
2018-07-16 01:00 | 111.96 | 95.61
2018-07-16 01:30 | 112.16 | 95.2
2018-07-16 02:00 | 118.65 | 103.82
2018-07-16 02:30 | 116.72 | 101.57
2018-07-16 03:00 | 122.51 | 109.26
2018-07-16 03:30 | 113.83 | 98.98
2018-07-16 04:00 | 121.65 | 107.28
2018-07-16 04:30 | 117.53 | 102.99
2018-07-16 05:00 | 113.9 | 98.88
2018-07-16 05:30 | 115.64 | 101.53
2018-07-16 06:00 | 114.55 | 100.18
2018-07-16 06:30 | 112.27 | 97.29
2018-07-16 07:00 | 118.28 | 104.64
2018-07-16 07:30 | 121.91 | 111.07
2018-07-16 08:00 | 127.76 | 116.51
2018-07-16 08:30 | 125.43 | 113.04
2018-07-16 09:00 | 130.06 | 119.05
2018-07-16 09:30 | 129.21 | 117.03
2018-07-16 10:00 | 126.89 | 112.69
2018-07-16 10:30 | 126.6 | 111.92
2018-07-16 11:00 | 122.39 | 106.53
2018-07-16 11:30 | 117.22 | 102.25
2018-07-16 12:00 | 114.8 | 99.96
2018-07-16 12:30 | 113.16 | 98.24
2018-07-16 13:00 | 116.04 | 100.82
2018-07-16 13:30 | 115.37 | 100.44
2018-07-16 14:00 | 119.27 | 104.38
2018-07-16 14:30 | 117.1 | 102.76
2018-07-16 15:00 | 116.52 | 102.18
2018-07-16 15:30 | 117.94 | 103.02
2018-07-16 16:00 | 120.95 | 108.4
2018-07-16 16:30 | 116.36 | 103.27
2018-07-16 17:00 | 125.74 | 113.7
2018-07-16 17:30 | 126.54 | 114.4
2018-07-16 18:00 | 131.2 | 119.6
2018-07-16 18:30 | 125.96 | 113.88
2018-07-16 19:00 | 134.31 | 124.72
2018-07-16 19:30 | 131.91 | 121.93
2018-07-16 20:00 | 132.05 | 121.97
2018-07-16 20:30 | 132.74 | 122.5
2018-07-16 21:00 | 130.05 | 118.79
2018-07-16 21:30 | 125.41 | 113.97
2018-07-16 22:00 | 126.85 | 115.8
2018-07-16 22:30 | 125.56 | 113.33
2018-07-16 23:00 | 121.63 | 108.73
2018-07-16 23:30 | 113.57 | 99.03
2018-07-17 | 118.48 | 105.44
2018-07-17 00:30 | 123.15 | 110.26
2018-07-17 01:00 | 121.37 | 108.01
2018-07-17 01:30 | 120.09 | 107.08
2018-07-17 02:00 | 123.91 | 112.24
2018-07-17 02:30 | 123.96 | 111.88
2018-07-17 03:00 | 125.74 | 114.44
2018-07-17 03:30 | 113.75 | 99.72
2018-07-17 04:00 | 110.41 | 95.06
2018-07-17 04:30 | 111.46 | 95.94
2018-07-17 05:00 | 108.31 | 92.21
2018-07-17 05:30 | 109.64 | 94.85
2018-07-17 06:00 | 104.75 | 88.22
2018-07-17 06:30 | 108.93 | 94.83
2018-07-17 07:00 | 111.99 | 98.23
2018-07-17 07:30 | 115.23 | 102.51
2018-07-17 08:00 | 120.41 | 107.89
2018-07-17 08:30 | 116.01 | 102.02
2018-07-17 09:00 | 115.19 | 101.87
2018-07-17 09:30 | 112.08 | 97.09
2018-07-17 10:00 | 109.33 | 93.59
2018-07-17 10:30 | 112.49 | 97.37
2018-07-17 11:00 | 109.4 | 93.4
2018-07-17 11:30 | 112.41 | 97.35
2018-07-17 12:00 | 110.15 | 94.69
2018-07-17 12:30 | 110.2 | 92.84
2018-07-17 13:00 | 112.1 | 94.56
2018-07-17 13:30 | 109.38 | 92.37
2018-07-17 14:00 | 105.09 | 87.85
2018-07-17 14:30 | 108.64 | 93.19
2018-07-17 15:00 | 107.14 | 91.61
2018-07-17 15:30 | 106.62 | 90.17
2018-07-17 16:00 | 110.67 | 95.05
2018-07-17 16:30 | 115.37 | 101.59
2018-07-17 17:00 | 114.5 | 101.62
2018-07-17 17:30 | 123.2 | 112.69
2018-07-17 18:00 | 119.78 | 108.67
2018-07-17 18:30 | 116.21 | 104.33
2018-07-17 19:00 | 124.94 | 115.55
2018-07-17 19:30 | 124.26 | 114.9
2018-07-17 20:00 | 120.12 | 109.95
2018-07-17 20:30 | 124 | 114.17
2018-07-17 21:00 | 122.05 | 111.26
2018-07-17 21:30 | 128.12 | 118.39
2018-07-17 22:00 | 124.67 | 114.04
2018-07-17 22:30 | 121.83 | 111.03
2018-07-17 23:00 | 120.39 | 108.59
2018-07-17 23:30 | 118.25 | 105.26
2018-07-18 | 112.83 | 99.32
2018-07-18 00:30 | 114.45 | 101.43
2018-07-18 01:00 | 114.68 | 101.2
2018-07-18 01:30 | 116.82 | 103.67
2018-07-18 02:00 | 117.36 | 104.6
2018-07-18 02:30 | 116.51 | 103.13
2018-07-18 03:00 | 115.43 | 101.35
2018-07-18 03:30 | 111.34 | 96.82
2018-07-18 04:00 | 110.69 | 97.16
2018-07-18 04:30 | 117.9 | 106.56
2018-07-18 05:00 | 121.1 | 109.69
2018-07-18 05:30 | 118.79 | 106.22
2018-07-18 06:00 | 116.1 | 102.05
2018-07-18 06:30 | 110.38 | 95.21
2018-07-18 07:00 | 112.38 | 96.32
2018-07-18 07:30 | 121.69 | 107.48
2018-07-18 08:00 | 122.1 | 107.23
2018-07-18 08:30 | 120.3 | 105.33
2018-07-18 09:00 | 118.53 | 103.28
2018-07-18 09:30 | 114.36 | 97.98
2018-07-18 10:00 | 118.98 | 104.05
2018-07-18 10:30 | 121.56 | 105.93
2018-07-18 11:00 | 119.72 | 102.85
2018-07-18 11:30 | 114.33 | 96.2
2018-07-18 12:00 | 117.85 | 101.03
2018-07-18 12:30 | 114.01 | 97.15
2018-07-18 13:00 | 108.59 | 91.56
2018-07-18 13:30 | 108.02 | 89.69
2018-07-18 14:00 | 112.44 | 95.34
2018-07-18 14:30 | 116.65 | 101.65
2018-07-18 15:00 | 115.95 | 100.23
2018-07-18 15:30 | 112.93 | 96.16
2018-07-18 16:00 | 115.89 | 100.17
2018-07-18 16:30 | 118.75 | 102.79
2018-07-18 17:00 | 120.45 | 104.94
2018-07-18 17:30 | 124.58 | 110.26
2018-07-18 18:00 | 125.36 | 112.26
2018-07-18 18:30 | 122.42 | 108.21
2018-07-18 19:00 | 125.17 | 112.84
2018-07-18 19:30 | 130.76 | 120.64
2018-07-18 20:00 | 125.33 | 113.98
2018-07-18 20:30 | 125.66 | 114.46
2018-07-18 21:00 | 125.95 | 113.3
2018-07-18 21:30 | 127.66 | 114.83
2018-07-18 22:00 | 129.48 | 117.61
2018-07-18 22:30 | 127.43 | 115.49
2018-07-18 23:00 | 124.06 | 111.44
2018-07-18 23:30 | 125.21 | 113.83
2018-07-19 | 123.7 | 110.52
2018-07-19 00:30 | 125.46 | 114.07
2018-07-19 01:00 | 123.61 | 110.98
2018-07-19 01:30 | 122.28 | 109.47
2018-07-19 02:00 | 125.28 | 112.88
2018-07-19 02:30 | 123.94 | 111.32
2018-07-19 03:00 | 117.11 | 102.72
2018-07-19 03:30 | 116.35 | 101.96
2018-07-19 04:00 | 124.29 | 112.29
2018-07-19 04:30 | 126.41 | 115.19
2018-07-19 05:00 | 122.23 | 108.82
2018-07-19 05:30 | 126.48 | 114.7
2018-07-19 06:00 | 135.28 | 125.23
2018-07-19 06:30 | 128.28 | 116.9
2018-07-19 07:00 | 139.33 | 128.79
2018-07-19 07:30 | 139.59 | 128.85
2018-07-19 08:00 | 142.66 | 132.4
2018-07-19 08:30 | 135.82 | 123.47
2018-07-19 09:00 | 126.91 | 113.56
2018-07-19 09:30 | 128.09 | 114.83
2018-07-19 10:00 | 124.33 | 110.48
2018-07-19 10:30 | 128.79 | 115.06
2018-07-19 11:00 | 124.17 | 109.83
2018-07-19 11:30 | 112.96 | 96.16
2018-07-19 12:00 | 111.11 | 93.84
2018-07-19 12:30 | 115.12 | 100.87
2018-07-19 13:00 | 114.75 | 99.9
2018-07-19 13:30 | 118.61 | 105.05
2018-07-19 14:00 | 117.76 | 104.7
2018-07-19 14:30 | 116.21 | 103.2
2018-07-19 15:00 | 119.52 | 107.41
2018-07-19 15:30 | 126.93 | 115.2
2018-07-19 16:00 | 126.21 | 114.81
2018-07-19 16:30 | 130.18 | 119.42
2018-07-19 17:00 | 131.56 | 120.26
2018-07-19 17:30 | 132 | 120.04
2018-07-19 18:00 | 140.19 | 129.93
2018-07-19 18:30 | 128.99 | 116.51
2018-07-19 19:00 | 132.2 | 122.12
2018-07-19 19:30 | 128.4 | 118.47
2018-07-19 20:00 | 125.91 | 115.43
2018-07-19 20:30 | 123.68 | 111.55
2018-07-19 21:00 | 124.18 | 112.14
2018-07-19 21:30 | 129.85 | 118.52
2018-07-19 22:00 | 129.52 | 118.31
2018-07-19 22:30 | 136.61 | 127.05
2018-07-19 23:00 | 130.49 | 119.37
2018-07-19 23:30 | 127.89 | 116.16
2018-07-20 | 131.67 | 120.49
2018-07-20 00:30 | 122.06 | 109.49
2018-07-20 01:00 | 129.41 | 118.2
2018-07-20 01:30 | 131.96 | 121.6
2018-07-20 02:00 | 127.46 | 115.2
2018-07-20 02:30 | 125.64 | 113.7
2018-07-20 03:00 | 123.97 | 111.99
2018-07-20 03:30 | 123.65 | 111.85
2018-07-20 04:00 | 119.99 | 108
2018-07-20 04:30 | 123.33 | 111.5
2018-07-20 05:00 | 122.94 | 111.26
2018-07-20 05:30 | 118.74 | 105.32
2018-07-20 06:00 | 122.77 | 110.6
2018-07-20 06:30 | 115.62 | 102.19
2018-07-20 07:00 | 123.85 | 111.98
2018-07-20 07:30 | 134.1 | 123.8
2018-07-20 08:00 | 132.31 | 121.58
2018-07-20 08:30 | 129.05 | 118.18
2018-07-20 09:00 | 135.82 | 125.68
2018-07-20 09:30 | 129.74 | 118.42
2018-07-20 10:00 | 128.06 | 116.67
2018-07-20 10:30 | 132.68 | 120.68
2018-07-20 11:00 | 135.57 | 124.16
2018-07-20 11:30 | 135.47 | 123.68
2018-07-20 12:00 | 124.95 | 110.92
2018-07-20 12:30 | 128.53 | 115.51
2018-07-20 13:00 | 135.4 | 124.24
2018-07-20 13:30 | 134.83 | 123.1
2018-07-20 14:00 | 131.03 | 119.34
2018-07-20 14:30 | 122.25 | 109.25
2018-07-20 15:00 | 118.29 | 104.89
2018-07-20 15:30 | 116.42 | 102.73
2018-07-20 16:00 | 121.13 | 109.35
2018-07-20 16:30 | 117.08 | 104.27
2018-07-20 17:00 | 117.92 | 104.83
2018-07-20 17:30 | 117.26 | 102.62
2018-07-20 18:00 | 123.09 | 110.02
2018-07-20 18:30 | 113.71 | 98.66
2018-07-20 19:00 | 120.74 | 108.01
2018-07-20 19:30 | 116.9 | 103.63
2018-07-20 20:00 | 114.88 | 101.59
2018-07-20 20:30 | 112.98 | 99.54
2018-07-20 21:00 | 115.11 | 101.59
2018-07-20 21:30 | 120.1 | 108.51
2018-07-20 22:00 | 114.72 | 102.54
2018-07-20 22:30 | 114.18 | 102.1
2018-07-20 23:00 | 114.24 | 101.62
2018-07-20 23:30 | 113.11 | 99.98
2018-07-21 | 112 | 97
2018-07-21 00:30 | 112.74 | 98.14
2018-07-21 01:00 | 108.37 | 93.03
2018-07-21 01:30 | 111.55 | 97.58
2018-07-21 02:00 | 124.32 | 111.93
2018-07-21 02:30 | 119.65 | 106.38
2018-07-21 03:00 | 129.79 | 118.71
2018-07-21 03:30 | 119.06 | 106.55
2018-07-21 04:00 | 116.27 | 102.98
2018-07-21 04:30 | 114.47 | 100.32
2018-07-21 05:00 | 117.98 | 105.49
2018-07-21 05:30 | 118.78 | 106.72
2018-07-21 06:00 | 120.54 | 108.92
2018-07-21 06:30 | 112.97 | 99.74
2018-07-21 07:00 | 120.67 | 109.24
2018-07-21 07:30 | 118.85 | 106.39
2018-07-21 08:00 | 110.56 | 95.65
2018-07-21 08:30 | 110.75 | 95.87
2018-07-21 09:00 | 116.85 | 104.43
2018-07-21 09:30 | 112.36 | 97.98
2018-07-21 10:00 | 116.06 | 103.23
2018-07-21 10:30 | 113.57 | 99.9
2018-07-21 11:00 | 112.23 | 98.08
2018-07-21 11:30 | 106.41 | 89.84
2018-07-21 12:00 | 108.07 | 92.07
2018-07-21 12:30 | 113.38 | 100.13
2018-07-21 13:00 | 102.19 | 85.8
2018-07-21 13:30 | 110.83 | 96.19
2018-07-21 14:00 | 109.61 | 95.42
2018-07-21 14:30 | 110.25 | 95.74
2018-07-21 15:00 | 117.22 | 104.57
2018-07-21 15:30 | 113 | 98.69
2018-07-21 16:00 | 115.4 | 103.01
2018-07-21 16:30 | 118.83 | 107.32
2018-07-21 17:00 | 108.31 | 95.07
2018-07-21 17:30 | 115 | 102.44
2018-07-21 18:00 | 116.82 | 104.77
2018-07-21 18:30 | 119.87 | 107.52
2018-07-21 19:00 | 122.1 | 110.54
2018-07-21 19:30 | 116.53 | 103.69
2018-07-21 20:00 | 113.56 | 100.85
2018-07-21 20:30 | 114.55 | 101.24
2018-07-21 21:00 | 117.86 | 105.18
2018-07-21 21:30 | 115.48 | 102.14
2018-07-21 22:00 | 120.3 | 108.38
2018-07-21 22:30 | 119.33 | 106.97
2018-07-21 23:00 | 115.16 | 101.5
2018-07-21 23:30 | 115.01 | 101.08
2018-07-22 | 106.28 | 90.22
2018-07-22 00:30 | 109.65 | 95.47
2018-07-22 01:00 | 109.12 | 94.58
2018-07-22 01:30 | 114.68 | 100.93
2018-07-22 02:00 | 116.65 | 103.59
2018-07-22 02:30 | 118.49 | 105.67
2018-07-22 03:00 | 113.21 | 99.45
2018-07-22 03:30 | 115.27 | 100.5
2018-07-22 04:00 | 113.48 | 98.57
2018-07-22 04:30 | 110.64 | 95.24
2018-07-22 05:00 | 115.39 | 102.02
2018-07-22 05:30 | 110.51 | 96.89
2018-07-22 06:00 | 112.82 | 98.76
2018-07-22 06:30 | 107.5 | 91.35
2018-07-22 07:00 | 113.59 | 97.91
2018-07-22 07:30 | 120.89 | 107.76
2018-07-22 08:00 | 121.84 | 108.77
2018-07-22 08:30 | 121.69 | 108.56
2018-07-22 09:00 | 121.39 | 107.68
2018-07-22 09:30 | 115.43 | 100.85
2018-07-22 10:00 | 107.03 | 90.33
2018-07-22 10:30 | 108.4 | 92.33
2018-07-22 11:00 | 113.52 | 99.09
2018-07-22 11:30 | 114.03 | 98.23
2018-07-22 12:00 | 117.05 | 102.57
2018-07-22 12:30 | 112.07 | 96.19
2018-07-22 13:00 | 109.04 | 92.46
2018-07-22 13:30 | 108.33 | 91
2018-07-22 14:00 | 115.56 | 99.62
2018-07-22 14:30 | 110.96 | 94.62
2018-07-22 15:00 | 113.24 | 98.17
2018-07-22 15:30 | 115.08 | 100.38
2018-07-22 16:00 | 117.91 | 104.03
2018-07-22 16:30 | 118.66 | 104.57
2018-07-22 17:00 | 114.55 | 100.61
2018-07-22 17:30 | 115.61 | 101.64
2018-07-22 18:00 | 118.87 | 105.88
2018-07-22 18:30 | 114.62 | 101.43
2018-07-22 19:00 | 117.95 | 106.25
2018-07-22 19:30 | 122.26 | 111.46
2018-07-22 20:00 | 116.31 | 103.83
2018-07-22 20:30 | 118.98 | 106.88
2018-07-22 21:00 | 115.39 | 101.76
2018-07-22 21:30 | 120.93 | 108.73
2018-07-22 22:00 | 125.95 | 114.88
2018-07-22 22:30 | 122.71 | 110.52
2018-07-22 23:00 | 123.13 | 110.06
2018-07-22 23:30 | 120.01 | 106.97
2018-07-23 | 119.34 | 106.14
2018-07-23 00:30 | 120.73 | 106.64
2018-07-23 01:00 | 116.17 | 101.09
2018-07-23 01:30 | 118.11 | 104.21
2018-07-23 02:00 | 123.21 | 110.04
2018-07-23 02:30 | 117.1 | 102.74
2018-07-23 03:00 | 114.74 | 99.41
2018-07-23 03:30 | 119.5 | 105.85
2018-07-23 04:00 | 118.69 | 105.39
2018-07-23 04:30 | 121.15 | 106.93
2018-07-23 05:00 | 119.86 | 105.99
2018-07-23 05:30 | 126.72 | 114.85
2018-07-23 06:00 | 130.15 | 118.06
2018-07-23 06:30 | 117.49 | 100.93
2018-07-23 07:00 | 122.58 | 108.27
2018-07-23 07:30 | 124.2 | 111.21
2018-07-23 08:00 | 127.85 | 115.69
2018-07-23 08:30 | 120.97 | 106.81
2018-07-23 09:00 | 120.37 | 106.08
2018-07-23 09:30 | 121.7 | 107.01
2018-07-23 10:00 | 116.79 | 100.78
2018-07-23 10:30 | 118.44 | 103.58
2018-07-23 11:00 | 122.27 | 108.13
2018-07-23 11:30 | 122.27 | 107.84
2018-07-23 12:00 | 121.22 | 106.72
2018-07-23 12:30 | 121.06 | 106.84
2018-07-23 13:00 | 118.38 | 103.26
2018-07-23 13:30 | 122.52 | 109.28
2018-07-23 14:00 | 118.61 | 103.77
2018-07-23 14:30 | 121.52 | 106.92
2018-07-23 15:00 | 122.87 | 108.93
2018-07-23 15:30 | 123.17 | 109.53
2018-07-23 16:00 | 121.77 | 107.89
2018-07-23 16:30 | 123.52 | 110.86
2018-07-23 17:00 | 123.63 | 111.34
2018-07-23 17:30 | 121.68 | 109.85
2018-07-23 18:00 | 127.92 | 116.69
2018-07-23 18:30 | 118.87 | 107.31
2018-07-23 19:00 | 124.46 | 114.42
2018-07-23 19:30 | 127.21 | 117.39
2018-07-23 20:00 | 118.98 | 106.9
2018-07-23 20:30 | 117.59 | 104.92
2018-07-23 21:00 | 116.42 | 103.73
2018-07-23 21:30 | 115.63 | 101.87
2018-07-23 22:00 | 106.75 | 91.01
2018-07-23 22:30 | 111.35 | 96.41
2018-07-23 23:00 | 114.52 | 100.57
2018-07-23 23:30 | 115.44 | 100.12
2018-07-24 | 116.69 | 101.91
2018-07-24 00:30 | 112.53 | 96.05
2018-07-24 01:00 | 106.52 | 88.92
2018-07-24 01:30 | 110.04 | 93.64
2018-07-24 02:00 | 113.53 | 97.32
2018-07-24 02:30 | 111.4 | 94.68
2018-07-24 03:00 | 111.58 | 95.08
2018-07-24 03:30 | 113.47 | 97.55
2018-07-24 04:00 | 110.47 | 92.78
2018-07-24 04:30 | 115.44 | 99.34
2018-07-24 05:00 | 116.76 | 101.44
2018-07-24 05:30 | 116.13 | 101.2
2018-07-24 06:00 | 109.3 | 92.71
2018-07-24 06:30 | 107.18 | 88.77
2018-07-24 07:00 | 109.29 | 91.24
2018-07-24 07:30 | 103.71 | 84.05
2018-07-24 08:00 | 107.38 | 87.83
2018-07-24 08:30 | 109.89 | 91.51
2018-07-24 09:00 | 112.35 | 93.97
2018-07-24 09:30 | 114.28 | 95.7
2018-07-24 10:00 | 116.1 | 99.07
2018-07-24 10:30 | 115.38 | 98.07
2018-07-24 11:00 | 111.16 | 92.95
2018-07-24 11:30 | 112.12 | 94.85
2018-07-24 12:00 | 115.37 | 98.9
2018-07-24 12:30 | 117.48 | 101.73
2018-07-24 13:00 | 117.93 | 101.95
2018-07-24 13:30 | 115.47 | 99.34
2018-07-24 14:00 | 112.2 | 95.03
2018-07-24 14:30 | 112.67 | 95.43
2018-07-24 15:00 | 113.93 | 97.73
2018-07-24 15:30 | 111.04 | 91.99
2018-07-24 16:00 | 114.92 | 97.38
2018-07-24 16:30 | 112 | 95.09
2018-07-24 17:00 | 112.04 | 96.14
2018-07-24 17:30 | 121.41 | 107.82
2018-07-24 18:00 | 121.89 | 109.74
2018-07-24 18:30 | 117.14 | 104.97
2018-07-24 19:00 | 124.91 | 114.24
2018-07-24 19:30 | 122.76 | 110.99
2018-07-24 20:00 | 125.11 | 113.55
2018-07-24 20:30 | 122.16 | 110.65
2018-07-24 21:00 | 116.39 | 103.21
2018-07-24 21:30 | 117.81 | 105.24
2018-07-24 22:00 | 112.26 | 98.67
2018-07-24 22:30 | 111 | 97.44
2018-07-24 23:00 | 113.82 | 99.63
2018-07-24 23:30 | 115.11 | 100.6
2018-07-25 | 112.4 | 97.62
2018-07-25 00:30 | 116.21 | 101.88
2018-07-25 01:00 | 117.29 | 103.76
2018-07-25 01:30 | 118.3 | 104.15
2018-07-25 02:00 | 125.08 | 112.63
2018-07-25 02:30 | 126.47 | 114.93
2018-07-25 03:00 | 125.66 | 113.17
2018-07-25 03:30 | 121.22 | 107.25
2018-07-25 04:00 | 112.28 | 96.98
2018-07-25 04:30 | 118.7 | 103.83
2018-07-25 05:00 | 118.31 | 103.68
2018-07-25 05:30 | 125.72 | 112.89
2018-07-25 06:00 | 118.52 | 105.11
2018-07-25 06:30 | 108.07 | 91.03
2018-07-25 07:00 | 114.6 | 100.26
2018-07-25 07:30 | 119.05 | 105.68
2018-07-25 08:00 | 112.44 | 97.13
2018-07-25 08:30 | 109.99 | 93.37
2018-07-25 09:00 | 112.28 | 96.52
2018-07-25 09:30 | 108.93 | 92.03
2018-07-25 10:00 | 108.31 | 90.5
2018-07-25 10:30 | 104.61 | 84.93
2018-07-25 11:00 | 99.56 | 79.18
2018-07-25 11:30 | 104.8 | 86.4
2018-07-25 12:00 | 113.45 | 96.91
2018-07-25 12:30 | 109.99 | 92.34
2018-07-25 13:00 | 106.06 | 88.82
2018-07-25 13:30 | 105.26 | 86.37
2018-07-25 14:00 | 106.42 | 88.57
2018-07-25 14:30 | 101.02 | 81.23
2018-07-25 15:00 | 96.79 | 76.37
2018-07-25 15:30 | 97.87 | 77.18
2018-07-25 16:00 | 106.2 | 88.72
2018-07-25 16:30 | 106.93 | 89.57
2018-07-25 17:00 | 104.4 | 87.78
2018-07-25 17:30 | 103.75 | 85.33
2018-07-25 18:00 | 109.4 | 92.47
2018-07-25 18:30 | 101.55 | 84.15
2018-07-25 19:00 | 109.67 | 93.94
2018-07-25 19:30 | 110.54 | 95.82
2018-07-25 20:00 | 107.08 | 91.24
2018-07-25 20:30 | 112.93 | 98.72
2018-07-25 21:00 | 110.03 | 94.54
2018-07-25 21:30 | 104.31 | 87.36
2018-07-25 22:00 | 109.86 | 92.52
2018-07-25 22:30 | 114.63 | 98.4
2018-07-25 23:00 | 119.35 | 104.91
2018-07-25 23:30 | 112.9 | 96.9
2018-07-26 | 113.71 | 97.79
2018-07-26 00:30 | 110.99 | 94.36
2018-07-26 01:00 | 105.34 | 86.32
2018-07-26 01:30 | 110.07 | 92.03
2018-07-26 02:00 | 108.03 | 90.05
2018-07-26 02:30 | 109.9 | 90.33
2018-07-26 03:00 | 109.01 | 88.88
2018-07-26 03:30 | 111.6 | 92.85
2018-07-26 04:00 | 107.29 | 89
2018-07-26 04:30 | 112.54 | 93.82
2018-07-26 05:00 | 111.64 | 92.91
2018-07-26 05:30 | 113.83 | 96.11
2018-07-26 06:00 | 117.06 | 101.24
2018-07-26 06:30 | 105.49 | 85.7
2018-07-26 07:00 | 102.77 | 83.48
2018-07-26 07:30 | 99.32 | 78.12
2018-07-26 08:00 | 98.41 | 76.95
2018-07-26 08:30 | 106.74 | 86.72
2018-07-26 09:00 | 104.28 | 82.84
2018-07-26 09:30 | 104.02 | 81.34
2018-07-26 10:00 | 104.13 | 82.7
2018-07-26 10:30 | 97.91 | 73.04
2018-07-26 11:00 | 98.54 | 73.51
2018-07-26 11:30 | 107.16 | 83.62
2018-07-26 12:00 | 107.09 | 84.69
2018-07-26 12:30 | 102.3 | 79.46
2018-07-26 13:00 | 109.21 | 88.71
2018-07-26 13:30 | 101.2 | 78.73
2018-07-26 14:00 | 100.26 | 77.82
2018-07-26 14:30 | 104.86 | 84.59
2018-07-26 15:00 | 105.15 | 85.47
2018-07-26 15:30 | 111.56 | 93.06
2018-07-26 16:00 | 114.69 | 96.51
2018-07-26 16:30 | 109.79 | 91.8
2018-07-26 17:00 | 117.32 | 102.97
2018-07-26 17:30 | 106.59 | 88.53
2018-07-26 18:00 | 111.37 | 95.24
2018-07-26 18:30 | 108.79 | 92.91
2018-07-26 19:00 | 115.26 | 100.98
2018-07-26 19:30 | 114.84 | 100.72
2018-07-26 20:00 | 116.4 | 102.53
2018-07-26 20:30 | 116.46 | 102.36
2018-07-26 21:00 | 114.13 | 99.04
2018-07-26 21:30 | 112.76 | 96.63
2018-07-26 22:00 | 115.2 | 99.51
2018-07-26 22:30 | 110.67 | 93.11
2018-07-26 23:00 | 113.43 | 97.2
2018-07-26 23:30 | 111.67 | 95.35
2018-07-27 | 110.55 | 93.38
2018-07-27 00:30 | 113.48 | 97.77
2018-07-27 01:00 | 112.25 | 95.52
2018-07-27 01:30 | 114.16 | 99.28
2018-07-27 02:00 | 114.96 | 98.88
2018-07-27 02:30 | 115.68 | 99.61
2018-07-27 03:00 | 117.06 | 100.89
2018-07-27 03:30 | 115.75 | 97.89
2018-07-27 04:00 | 112.9 | 95
2018-07-27 04:30 | 112.09 | 95.57
2018-07-27 05:00 | 115.31 | 99.31
2018-07-27 05:30 | 117.05 | 101.85
2018-07-27 06:00 | 110.81 | 94.29
2018-07-27 06:30 | 98.55 | 77.34
2018-07-27 07:00 | 104.94 | 88
2018-07-27 07:30 | 106.25 | 88.49
2018-07-27 08:00 | 100.41 | 81.81
2018-07-27 08:30 | 98.85 | 78.89
2018-07-27 09:00 | 98.14 | 77.55
2018-07-27 09:30 | 97.88 | 78.03
2018-07-27 10:00 | 98.38 | 79.13
2018-07-27 10:30 | 104.63 | 87.74
2018-07-27 11:00 | 107.04 | 89.58
2018-07-27 11:30 | 105.43 | 87.25
2018-07-27 12:00 | 104.08 | 86.81
2018-07-27 12:30 | 102.77 | 84.53
2018-07-27 13:00 | 111.24 | 95.76
2018-07-27 13:30 | 109.36 | 93.36
2018-07-27 14:00 | 110.29 | 93.4
2018-07-27 14:30 | 109.06 | 90.93
2018-07-27 15:00 | 107.9 | 89.17
2018-07-27 15:30 | 107.49 | 88.55
2018-07-27 16:00 | 111.12 | 94.06
2018-07-27 16:30 | 107.88 | 91.4
2018-07-27 17:00 | 111.72 | 96.15
2018-07-27 17:30 | 112.72 | 99.01
2018-07-27 18:00 | 110.76 | 96.6
2018-07-27 18:30 | 107.13 | 92.12
2018-07-27 19:00 | 111.79 | 97.21
2018-07-27 19:30 | 112.38 | 97.89
2018-07-27 20:00 | 113.83 | 98.84
2018-07-27 20:30 | 113.25 | 99.08
2018-07-27 21:00 | 105.83 | 89.07
2018-07-27 21:30 | 101.77 | 84.57
2018-07-27 22:00 | 103.17 | 84.78
2018-07-27 22:30 | 104.21 | 86.89
2018-07-27 23:00 | 109.47 | 93.48
2018-07-27 23:30 | 110.29 | 94.1
2018-07-28 | 106.79 | 89.55
2018-07-28 00:30 | 106.79 | 90.3
2018-07-28 01:00 | 102.5 | 84.48
2018-07-28 01:30 | 104.01 | 87.21
2018-07-28 02:00 | 105.34 | 88.1
2018-07-28 02:30 | 101.27 | 82.38
2018-07-28 03:00 | 110.5 | 94.61
2018-07-28 03:30 | 110.6 | 95.2
2018-07-28 04:00 | 106.23 | 89.3
2018-07-28 04:30 | 115.5 | 101.89
2018-07-28 05:00 | 112.8 | 98.91
2018-07-28 05:30 | 113.58 | 98.33
2018-07-28 06:00 | 111.33 | 95.55
2018-07-28 06:30 | 104.83 | 86.94
2018-07-28 07:00 | 115.83 | 101.15
2018-07-28 07:30 | 115.15 | 101.15
2018-07-28 08:00 | 111.13 | 96.34
2018-07-28 08:30 | 109.38 | 94.16
2018-07-28 09:00 | 118.48 | 105.32
2018-07-28 09:30 | 114.32 | 100.2
2018-07-28 10:00 | 110.53 | 95.97
2018-07-28 10:30 | 107.82 | 92.07
2018-07-28 11:00 | 113.67 | 97.66
2018-07-28 11:30 | 113.97 | 98.25
2018-07-28 12:00 | 115.61 | 100.83
2018-07-28 12:30 | 114.37 | 99.28
2018-07-28 13:00 | 111.36 | 96.28
2018-07-28 13:30 | 110.6 | 94.77
2018-07-28 14:00 | 110.29 | 94.27
2018-07-28 14:30 | 110.78 | 94.21
2018-07-28 15:00 | 106.92 | 88.27
2018-07-28 15:30 | 112.58 | 95.8
2018-07-28 16:00 | 112.64 | 97.58
2018-07-28 16:30 | 114.87 | 100.09
2018-07-28 17:00 | 118.62 | 104.89
2018-07-28 17:30 | 114.02 | 99.84
2018-07-28 18:00 | 115.92 | 102.69
2018-07-28 18:30 | 110.73 | 96.19
2018-07-28 19:00 | 119.58 | 106.57
2018-07-28 19:30 | 119.11 | 106.06
2018-07-28 20:00 | 120.3 | 107.86
2018-07-28 20:30 | 113.93 | 98.73
2018-07-28 21:00 | 116.78 | 102.03
2018-07-28 21:30 | 117.64 | 102.77
2018-07-28 22:00 | 112.64 | 96.82
2018-07-28 22:30 | 115.5 | 100.23
2018-07-28 23:00 | 115.39 | 100.65
2018-07-28 23:30 | 112.32 | 97.88
2018-07-29 | 110.94 | 96.55
2018-07-29 00:30 | 109.88 | 94.93
2018-07-29 01:00 | 106.95 | 91.61
2018-07-29 01:30 | 106.72 | 90.66
2018-07-29 02:00 | 111.48 | 96.63
2018-07-29 02:30 | 110.16 | 95.55
2018-07-29 03:00 | 115.79 | 101.19
2018-07-29 03:30 | 116.42 | 101.03
2018-07-29 04:00 | 114.04 | 98.58
2018-07-29 04:30 | 115.91 | 99.82
2018-07-29 05:00 | 118.12 | 103.35
2018-07-29 05:30 | 114.55 | 97.74
2018-07-29 06:00 | 109.62 | 91.28
2018-07-29 06:30 | 107.31 | 88.74
2018-07-29 07:00 | 112.29 | 95.4
2018-07-29 07:30 | 116.42 | 101.27
2018-07-29 08:00 | 112.44 | 96.64
2018-07-29 08:30 | 109.47 | 94.63
2018-07-29 09:00 | 116.44 | 102.42
2018-07-29 09:30 | 115.12 | 99.41
2018-07-29 10:00 | 113.78 | 99.38
2018-07-29 10:30 | 113.43 | 98.2
2018-07-29 11:00 | 113.66 | 98.55
2018-07-29 11:30 | 111.79 | 97.12
2018-07-29 12:00 | 115.91 | 101.04
2018-07-29 12:30 | 115.15 | 101.73
2018-07-29 13:00 | 106.18 | 89.74
2018-07-29 13:30 | 106.53 | 88.94
2018-07-29 14:00 | 111.72 | 96.58
2018-07-29 14:30 | 114.23 | 99.6
2018-07-29 15:00 | 117.37 | 103.04
2018-07-29 15:30 | 120.45 | 106.34
2018-07-29 16:00 | 122.4 | 109.82
2018-07-29 16:30 | 122.67 | 110.96
2018-07-29 17:00 | 119.31 | 105.22
2018-07-29 17:30 | 115.59 | 103.03
2018-07-29 18:00 | 111.48 | 98.07
2018-07-29 18:30 | 107.84 | 93.01
2018-07-29 19:00 | 113.34 | 100.03
2018-07-29 19:30 | 117.29 | 104.03
2018-07-29 20:00 | 119.07 | 106.48
2018-07-29 20:30 | 117.67 | 104.34
2018-07-29 21:00 | 112.33 | 98.01
2018-07-29 21:30 | 120.49 | 106.6
2018-07-29 22:00 | 112.35 | 97.42
2018-07-29 22:30 | 113.28 | 98.2
2018-07-29 23:00 | 111.68 | 95.89
2018-07-29 23:30 | 115.11 | 100.05
2018-07-30 | 112.79 | 97.34
2018-07-30 00:30 | 116.23 | 101.79
2018-07-30 01:00 | 114.05 | 98.6
2018-07-30 01:30 | 121.38 | 107.46
2018-07-30 02:00 | 118.36 | 103.42
2018-07-30 02:30 | 119.52 | 105.1
2018-07-30 03:00 | 115.99 | 100.61
2018-07-30 03:30 | 112.66 | 96.79
2018-07-30 04:00 | 113.02 | 97.82
2018-07-30 04:30 | 114.46 | 99.45
2018-07-30 05:00 | 112.18 | 97.17
2018-07-30 05:30 | 115.48 | 101.59
2018-07-30 06:00 | 118.6 | 104.81
2018-07-30 06:30 | 105.26 | 87.06
2018-07-30 07:00 | 113.22 | 98.35
2018-07-30 07:30 | 117.35 | 102.94
2018-07-30 08:00 | 123.2 | 110.31
2018-07-30 08:30 | 127.53 | 114.69
2018-07-30 09:00 | 113.2 | 97.5
2018-07-30 09:30 | 118.6 | 102.58
2018-07-30 10:00 | 122.62 | 107.54
2018-07-30 10:30 | 119.11 | 102.84
2018-07-30 11:00 | 120.77 | 106.39
2018-07-30 11:30 | 118.92 | 102.78
2018-07-30 12:00 | 117.13 | 100.31
2018-07-30 12:30 | 113.48 | 95.92
2018-07-30 13:00 | 108.24 | 89.37
2018-07-30 13:30 | 110.1 | 90.87
2018-07-30 14:00 | 110.78 | 92.49
2018-07-30 14:30 | 113.4 | 96.71
2018-07-30 15:00 | 114.44 | 97.63
2018-07-30 15:30 | 117.81 | 101.4
2018-07-30 16:00 | 121.24 | 106.45
2018-07-30 16:30 | 117.15 | 101.64
2018-07-30 17:00 | 106.88 | 89.33
2018-07-30 17:30 | 111.83 | 97.47
2018-07-30 18:00 | 110.48 | 97.83
2018-07-30 18:30 | 101.84 | 86.66
2018-07-30 19:00 | 109.23 | 95.84
2018-07-30 19:30 | 113.66 | 100.23
2018-07-30 20:00 | 111.53 | 97.08
2018-07-30 20:30 | 109.99 | 94.85
2018-07-30 21:00 | 106.95 | 91.63
2018-07-30 21:30 | 107.35 | 92.16
2018-07-30 22:00 | 108.03 | 93.48
2018-07-30 22:30 | 115.13 | 101.76
2018-07-30 23:00 | 112.81 | 97.03
2018-07-30 23:30 | 111.74 | 94.94
2018-07-31 | 107.62 | 90.49
2018-07-31 00:30 | 111.99 | 96.17
2018-07-31 01:00 | 116.12 | 99.95
2018-07-31 01:30 | 114.63 | 97.76
2018-07-31 02:00 | 115.38 | 99.02
2018-07-31 02:30 | 111.94 | 94.99
2018-07-31 03:00 | 113.22 | 95.89
2018-07-31 03:30 | 114.95 | 98.15
2018-07-31 04:00 | 120.74 | 105.61
2018-07-31 04:30 | 113.3 | 96.38
2018-07-31 05:00 | 113.94 | 96.53
2018-07-31 05:30 | 114.01 | 97.8
2018-07-31 06:00 | 111.3 | 94.11
2018-07-31 06:30 | 102.63 | 81.98
2018-07-31 07:00 | 99.74 | 78.22
2018-07-31 07:30 | 100.58 | 81.11
2018-07-31 08:00 | 93.69 | 73.39
2018-07-31 08:30 | 97.59 | 76.93
2018-07-31 09:00 | 98.75 | 79.27
2018-07-31 09:30 | 108.16 | 92.61
2018-07-31 10:00 | 107.57 | 90.19
2018-07-31 10:30 | 107.08 | 89.66
2018-07-31 11:00 | 112.39 | 96.28
2018-07-31 11:30 | 106.17 | 87.33
2018-07-31 12:00 | 109.65 | 92.23
2018-07-31 12:30 | 111.54 | 94.12
2018-07-31 13:00 | 108.79 | 90.11
2018-07-31 13:30 | 111.03 | 94
2018-07-31 14:00 | 110.91 | 92.49
2018-07-31 14:30 | 108.87 | 89.79
2018-07-31 15:00 | 105.89 | 85.47
2018-07-31 15:30 | 112.43 | 94.74
2018-07-31 16:00 | 116.2 | 100.07
2018-07-31 16:30 | 115.23 | 98.93
2018-07-31 17:00 | 112.71 | 96.55
2018-07-31 17:30 | 113.86 | 98.99
2018-07-31 18:00 | 109.66 | 93.58
2018-07-31 18:30 | 108.85 | 94.27
2018-07-31 19:00 | 110.43 | 96.5
2018-07-31 19:30 | 113.99 | 100.39
2018-07-31 20:00 | 116.59 | 104.21
2018-07-31 20:30 | 119.63 | 107.71
2018-07-31 21:00 | 123.66 | 111.54
2018-07-31 21:30 | 119.6 | 105.76
2018-07-31 22:00 | 117.85 | 104.21
2018-07-31 22:30 | 115.95 | 102.57
2018-07-31 23:00 | 114.68 | 100.33
2018-07-31 23:30 | 115.79 | 101.44
2018-08-01 | 113.69 | 98.26
2018-08-01 00:30 | 115.64 | 99.71
2018-08-01 01:00 | 116.16 | 100.93
2018-08-01 01:30 | 110.96 | 94.35
2018-08-01 02:00 | 110.33 | 92.58
2018-08-01 02:30 | 114.07 | 96.79
2018-08-01 03:00 | 108.59 | 89.93
2018-08-01 03:30 | 109.58 | 91.02
2018-08-01 04:00 | 113.07 | 95.79
2018-08-01 04:30 | 115.26 | 100.04
2018-08-01 05:00 | 109.79 | 93.45
2018-08-01 05:30 | 117.23 | 103.21
2018-08-01 06:00 | 107.35 | 90.55
2018-08-01 06:30 | 107.12 | 89.21
2018-08-01 07:00 | 107.86 | 90.98
2018-08-01 07:30 | 116.68 | 102.63
2018-08-01 08:00 | 105.88 | 88.52
2018-08-01 08:30 | 112.24 | 95.44
2018-08-01 09:00 | 108.84 | 91.05
2018-08-01 09:30 | 108.23 | 89.95
2018-08-01 10:00 | 106.44 | 88.66
2018-08-01 10:30 | 111.64 | 93.55
2018-08-01 11:00 | 114.35 | 96.79
2018-08-01 11:30 | 113.57 | 95.45
2018-08-01 12:00 | 115.1 | 97.71
2018-08-01 12:30 | 116.52 | 99.22
2018-08-01 13:00 | 113.02 | 94.07
2018-08-01 13:30 | 112.09 | 94.19
2018-08-01 14:00 | 108.38 | 88.25
2018-08-01 14:30 | 110.54 | 91.22
2018-08-01 15:00 | 112.63 | 93.73
2018-08-01 15:30 | 112.11 | 93.44
2018-08-01 16:00 | 113.11 | 96.33
2018-08-01 16:30 | 115.4 | 100.58
2018-08-01 17:00 | 117.82 | 101.56
2018-08-01 17:30 | 114.91 | 98.01
2018-08-01 18:00 | 118.88 | 104.01
2018-08-01 18:30 | 114.76 | 99.06
2018-08-01 19:00 | 111.58 | 95.49
2018-08-01 19:30 | 121.43 | 108.08
2018-08-01 20:00 | 111.81 | 96.9
2018-08-01 20:30 | 113.51 | 99.73
2018-08-01 21:00 | 112.97 | 96.82
2018-08-01 21:30 | 113.05 | 97.44
2018-08-01 22:00 | 112.68 | 96.67
2018-08-01 22:30 | 115.99 | 100.13
2018-08-01 23:00 | 111.87 | 93.76
2018-08-01 23:30 | 116 | 98.75
2018-08-02 | 118.57 | 102.64
2018-08-02 00:30 | 110.49 | 92.7
2018-08-02 01:00 | 113.89 | 98.03
2018-08-02 01:30 | 112.23 | 95.39
2018-08-02 02:00 | 117.32 | 100.96
2018-08-02 02:30 | 122.84 | 107.67
2018-08-02 03:00 | 120.65 | 104.5
2018-08-02 03:30 | 110.26 | 90.96
2018-08-02 04:00 | 115.2 | 98.5
2018-08-02 04:30 | 115.3 | 98.97
2018-08-02 05:00 | 114.05 | 97.75
2018-08-02 05:30 | 115.86 | 100.84
2018-08-02 06:00 | 117.17 | 102.06
2018-08-02 06:30 | 114.89 | 98.84
2018-08-02 07:00 | 117.56 | 103.55
2018-08-02 07:30 | 107.33 | 90.35
2018-08-02 08:00 | 108.5 | 88.89
2018-08-02 08:30 | 108.11 | 88.71
2018-08-02 09:00 | 111.51 | 92.55
2018-08-02 09:30 | 114.91 | 95.47
2018-08-02 10:00 | 118.18 | 100.16
2018-08-02 10:30 | 123.11 | 105.88
2018-08-02 11:00 | 111.02 | 89.14
2018-08-02 11:30 | 116.89 | 96.44
2018-08-02 12:00 | 112.87 | 90.89
2018-08-02 12:30 | 110.01 | 86.2
2018-08-02 13:00 | 111.99 | 89.51
2018-08-02 13:30 | 115.88 | 95.26
2018-08-02 14:00 | 115.41 | 94.66
2018-08-02 14:30 | 119.14 | 99.86
2018-08-02 15:00 | 116.49 | 96.34
2018-08-02 15:30 | 118.76 | 99.86
2018-08-02 16:00 | 123.48 | 106.09
2018-08-02 16:30 | 123.91 | 106.91
2018-08-02 17:00 | 125.54 | 109.87
2018-08-02 17:30 | 116.66 | 98.79
2018-08-02 18:00 | 128 | 114.56
2018-08-02 18:30 | 119.24 | 104.65
2018-08-02 19:00 | 116.1 | 100.48
2018-08-02 19:30 | 122.74 | 109.57
2018-08-02 20:00 | 115.78 | 101.39
2018-08-02 20:30 | 108.78 | 91.57
2018-08-02 21:00 | 109.15 | 90.8
2018-08-02 21:30 | 111.14 | 93.3
2018-08-02 22:00 | 109.16 | 91.36
2018-08-02 22:30 | 112.39 | 96.7
2018-08-02 23:00 | 110.04 | 93.81
2018-08-02 23:30 | 113.07 | 96.76
2018-08-03 | 115.93 | 100.24
2018-08-03 00:30 | 120.36 | 107.28
2018-08-03 01:00 | 122.85 | 110.25
2018-08-03 01:30 | 115.09 | 98.59
2018-08-03 02:00 | 116.09 | 100.62
2018-08-03 02:30 | 116.25 | 101.3
2018-08-03 03:00 | 115.71 | 100.69
2018-08-03 03:30 | 113.94 | 98.12
2018-08-03 04:00 | 116.14 | 101.73
2018-08-03 04:30 | 114.97 | 100.2
2018-08-03 05:00 | 114.92 | 99.62
2018-08-03 05:30 | 111.42 | 95.03
2018-08-03 06:00 | 114.03 | 98.57
2018-08-03 06:30 | 117.77 | 103.18
2018-08-03 07:00 | 112.07 | 96.17
2018-08-03 07:30 | 120.65 | 106.44
2018-08-03 08:00 | 120.01 | 105.95
2018-08-03 08:30 | 112.06 | 94.66
2018-08-03 09:00 | 117.31 | 101.47
2018-08-03 09:30 | 116.62 | 99.99
2018-08-03 10:00 | 116.18 | 98.76
2018-08-03 10:30 | 113.44 | 97.02
2018-08-03 11:00 | 119.33 | 102.38
2018-08-03 11:30 | 113.36 | 93.04
2018-08-03 12:00 | 117.78 | 99.11
2018-08-03 12:30 | 113.58 | 94.42
2018-08-03 13:00 | 114.93 | 96.73
2018-08-03 13:30 | 106.48 | 86.45
2018-08-03 14:00 | 109.39 | 89.58
2018-08-03 14:30 | 110.69 | 91.6
2018-08-03 15:00 | 112.76 | 95.51
2018-08-03 15:30 | 113.46 | 95.83
2018-08-03 16:00 | 114.54 | 97.15
2018-08-03 16:30 | 120.21 | 104.98
2018-08-03 17:00 | 114.46 | 97.67
2018-08-03 17:30 | 116.36 | 102.17
2018-08-03 18:00 | 110.57 | 95.78
2018-08-03 18:30 | 107.97 | 92.1
2018-08-03 19:00 | 117.3 | 104.7
2018-08-03 19:30 | 117.21 | 105
2018-08-03 20:00 | 121.35 | 108.79
2018-08-03 20:30 | 122.15 | 109.1
2018-08-03 21:00 | 125.1 | 112.95
2018-08-03 21:30 | 119.47 | 105.89
2018-08-03 22:00 | 113.5 | 99.83
2018-08-03 22:30 | 113.08 | 99.71
2018-08-03 23:00 | 116.46 | 103.04
2018-08-03 23:30 | 111.93 | 97.44
2018-08-04 | 108.51 | 92.31
2018-08-04 00:30 | 111.7 | 96.73
2018-08-04 01:00 | 109.95 | 94.69
2018-08-04 01:30 | 107.71 | 90.66
2018-08-04 02:00 | 113.06 | 97.83
2018-08-04 02:30 | 112.99 | 97.6
2018-08-04 03:00 | 112.34 | 96.52
2018-08-04 03:30 | 103.95 | 85.97
2018-08-04 04:00 | 108.8 | 91.75
2018-08-04 04:30 | 112.32 | 95.91
2018-08-04 05:00 | 113.19 | 96.36
2018-08-04 05:30 | 112.1 | 95.1
2018-08-04 06:00 | 117.23 | 101.7
2018-08-04 06:30 | 103.74 | 82.83
2018-08-04 07:00 | 110.72 | 93.29
2018-08-04 07:30 | 105.81 | 87.34
2018-08-04 08:00 | 106.71 | 88.67
2018-08-04 08:30 | 112.81 | 95.81
2018-08-04 09:00 | 108.7 | 89.7
2018-08-04 09:30 | 108.99 | 89.39
2018-08-04 10:00 | 109.6 | 90.27
2018-08-04 10:30 | 103.38 | 81.42
2018-08-04 11:00 | 105.47 | 85.75
2018-08-04 11:30 | 104.7 | 84.8
2018-08-04 12:00 | 110.74 | 92.76
2018-08-04 12:30 | 112.34 | 92.86
2018-08-04 13:00 | 108.49 | 86.87
2018-08-04 13:30 | 115.17 | 97.4
2018-08-04 14:00 | 112.58 | 93.46
2018-08-04 14:30 | 108.52 | 89.94
2018-08-04 15:00 | 113.28 | 96.22
2018-08-04 15:30 | 116.16 | 100.6
2018-08-04 16:00 | 109.51 | 91.78
2018-08-04 16:30 | 112.53 | 94.83
2018-08-04 17:00 | 112.87 | 94.62
2018-08-04 17:30 | 115.46 | 100.09
2018-08-04 18:00 | 117.44 | 103.6
2018-08-04 18:30 | 117.81 | 104.18
2018-08-04 19:00 | 121.3 | 109.12
2018-08-04 19:30 | 117.84 | 105.42
2018-08-04 20:00 | 116.96 | 104.91
2018-08-04 20:30 | 118.39 | 105.53
2018-08-04 21:00 | 116.14 | 101.53
2018-08-04 21:30 | 118.44 | 104.27
2018-08-04 22:00 | 115.84 | 100.38
2018-08-04 22:30 | 121.98 | 107.24
2018-08-04 23:00 | 120.39 | 105.45
2018-08-04 23:30 | 121.12 | 106.1
2018-08-05 | 121.68 | 106.6
2018-08-05 00:30 | 113.95 | 98.02
2018-08-05 01:00 | 112.11 | 95.29
2018-08-05 01:30 | 120.33 | 105.88
2018-08-05 02:00 | 119.12 | 103.27
2018-08-05 02:30 | 119.39 | 104.73
2018-08-05 03:00 | 121.21 | 107.12
2018-08-05 03:30 | 119.52 | 103.63
2018-08-05 04:00 | 118.59 | 102.98
2018-08-05 04:30 | 124.69 | 110.06
2018-08-05 05:00 | 114.89 | 96.69
2018-08-05 05:30 | 118.7 | 102.42
2018-08-05 06:00 | 112.06 | 95.07
2018-08-05 06:30 | 105.19 | 86.3
2018-08-05 07:00 | 109.29 | 91.71
2018-08-05 07:30 | 120.01 | 103.66
2018-08-05 08:00 | 116.66 | 97.67
2018-08-05 08:30 | 117.95 | 99.73
2018-08-05 09:00 | 115 | 95.92
2018-08-05 09:30 | 117.15 | 98.58
2018-08-05 10:00 | 123.18 | 106.69
2018-08-05 10:30 | 120.42 | 103.12
2018-08-05 11:00 | 112.86 | 92.61
2018-08-05 11:30 | 117.68 | 99.55
2018-08-05 12:00 | 116.36 | 98.53
2018-08-05 12:30 | 116.94 | 98.34
2018-08-05 13:00 | 116.88 | 98.68
2018-08-05 13:30 | 112.03 | 91.92
2018-08-05 14:00 | 112.16 | 94.05
2018-08-05 14:30 | 110.33 | 93.59
2018-08-05 15:00 | 113.26 | 96.53
2018-08-05 15:30 | 112.96 | 94.77
2018-08-05 16:00 | 113.58 | 95.66
2018-08-05 16:30 | 112.93 | 95.44
2018-08-05 17:00 | 114.89 | 99.11
2018-08-05 17:30 | 117.53 | 103.07
2018-08-05 18:00 | 116.49 | 101.75
2018-08-05 18:30 | 98.69 | 80.05
2018-08-05 19:00 | 110.82 | 95.67
2018-08-05 19:30 | 116.43 | 102.43
2018-08-05 20:00 | 115.82 | 101.2
2018-08-05 20:30 | 111.97 | 96.06
2018-08-05 21:00 | 117.86 | 102.42
2018-08-05 21:30 | 119.31 | 103.85
2018-08-05 22:00 | 127.71 | 114.4
2018-08-05 22:30 | 123.12 | 108.41
2018-08-05 23:00 | 126.98 | 112.79
2018-08-05 23:30 | 122.92 | 107.13
2018-08-06 | 127.78 | 114.46
2018-08-06 00:30 | 123.64 | 108.67
2018-08-06 01:00 | 124 | 109.05
2018-08-06 01:30 | 121.06 | 104.61
2018-08-06 02:00 | 117.8 | 101.84
2018-08-06 02:30 | 120.22 | 103.49
2018-08-06 03:00 | 122.03 | 104.74
2018-08-06 03:30 | 121.29 | 103.3
2018-08-06 04:00 | 124.4 | 109.07
2018-08-06 04:30 | 125.02 | 110.71
2018-08-06 05:00 | 121.44 | 106.68
2018-08-06 05:30 | 118.68 | 102.53
2018-08-06 06:00 | 111.96 | 94.04
2018-08-06 06:30 | 112.25 | 94.52
2018-08-06 07:00 | 116.92 | 99.23
2018-08-06 07:30 | 124.54 | 109.71
2018-08-06 08:00 | 119.98 | 104.21
2018-08-06 08:30 | 119.55 | 103.46
2018-08-06 09:00 | 119.04 | 101.97
2018-08-06 09:30 | 113.54 | 95.57
2018-08-06 10:00 | 108.88 | 89.7
2018-08-06 10:30 | 112.67 | 94.8
2018-08-06 11:00 | 113.84 | 95.79
2018-08-06 11:30 | 108.78 | 88.13
2018-08-06 12:00 | 112.55 | 94.36
2018-08-06 12:30 | 112.05 | 93.79
2018-08-06 13:00 | 108.18 | 88.65
2018-08-06 13:30 | 101.63 | 81.46
2018-08-06 14:00 | 113.95 | 95.97
2018-08-06 14:30 | 113.58 | 96.63
2018-08-06 15:00 | 110.9 | 93.23
2018-08-06 15:30 | 117.47 | 102.49
2018-08-06 16:00 | 110.7 | 92.44
2018-08-06 16:30 | 111.6 | 95.32
2018-08-06 17:00 | 118.4 | 103.21
2018-08-06 17:30 | 117.97 | 102.7
2018-08-06 18:00 | 108.56 | 92.28
2018-08-06 18:30 | 107.55 | 89.57
2018-08-06 19:00 | 116.89 | 101.61
2018-08-06 19:30 | 118.9 | 104.42
2018-08-06 20:00 | 113.54 | 97.33
2018-08-06 20:30 | 113.99 | 97.39
2018-08-06 21:00 | 111.22 | 93.31
2018-08-06 21:30 | 112.67 | 95.74
2018-08-06 22:00 | 115.03 | 99.06
2018-08-06 22:30 | 117.28 | 101.18
2018-08-06 23:00 | 118.7 | 103.34
2018-08-06 23:30 | 121.61 | 107.07
2018-08-07 | 120.2 | 104.92
2018-08-07 00:30 | 120.69 | 105.32
2018-08-07 01:00 | 122.76 | 107.9
2018-08-07 01:30 | 118.79 | 102.14
2018-08-07 02:00 | 124.39 | 108.72
2018-08-07 02:30 | 120.66 | 103.86
2018-08-07 03:00 | 120.72 | 103.81
2018-08-07 03:30 | 119.07 | 101.9
2018-08-07 04:00 | 125.3 | 110.35
2018-08-07 04:30 | 125.74 | 110.92
2018-08-07 05:00 | 119.71 | 103.54
2018-08-07 05:30 | 119 | 103.29
2018-08-07 06:00 | 112.75 | 93.9
2018-08-07 06:30 | 111.74 | 92.15
2018-08-07 07:00 | 112.31 | 94.48
2018-08-07 07:30 | 118.22 | 99.99
2018-08-07 08:00 | 121.54 | 103.87
2018-08-07 08:30 | 121.23 | 102.17
2018-08-07 09:00 | 108.95 | 86.01
2018-08-07 09:30 | 108.75 | 86.02
2018-08-07 10:00 | 112.95 | 92.67
2018-08-07 10:30 | 121.91 | 105.25
2018-08-07 11:00 | 116.47 | 96.94
2018-08-07 11:30 | 113.17 | 94.38
2018-08-07 12:00 | 118.01 | 98.82
2018-08-07 12:30 | 113.03 | 92.79
2018-08-07 13:00 | 108.04 | 84.94
2018-08-07 13:30 | 118.09 | 97.78
2018-08-07 14:00 | 115.56 | 94.9
2018-08-07 14:30 | 123.13 | 104.91
2018-08-07 15:00 | 116.02 | 95.1
2018-08-07 15:30 | 111.51 | 90.71
2018-08-07 16:00 | 103.08 | 80.45
2018-08-07 16:30 | 108.14 | 86.14
2018-08-07 17:00 | 108.55 | 88.45
2018-08-07 17:30 | 108.58 | 88.26
2018-08-07 18:00 | 107.34 | 86.71
2018-08-07 18:30 | 98.17 | 75.59
2018-08-07 19:00 | 97.55 | 76.42
2018-08-07 19:30 | 98.53 | 77.16
2018-08-07 20:00 | 106.76 | 89.73
2018-08-07 20:30 | 100.12 | 79.4
2018-08-07 21:00 | 107.81 | 87.19
2018-08-07 21:30 | 112.72 | 93.47
2018-08-07 22:00 | 108.91 | 89.38
2018-08-07 22:30 | 107.84 | 87.52
2018-08-07 23:00 | 107.01 | 86.81
2018-08-07 23:30 | 106.57 | 86.7
2018-08-08 | 103.18 | 81.07
2018-08-08 00:30 | 105.86 | 84.6
2018-08-08 01:00 | 104.57 | 82.78
2018-08-08 01:30 | 102.54 | 79.68
2018-08-08 02:00 | 104.55 | 81.67
2018-08-08 02:30 | 108.37 | 87.86
2018-08-08 03:00 | 103.52 | 81.08
2018-08-08 03:30 | 110.32 | 89.3
2018-08-08 04:00 | 111.88 | 91.59
2018-08-08 04:30 | 113.8 | 95.17
2018-08-08 05:00 | 114.92 | 97.14
2018-08-08 05:30 | 116 | 99.03
2018-08-08 06:00 | 113.39 | 96.21
2018-08-08 06:30 | 99.08 | 77.57
2018-08-08 07:00 | 103.58 | 85.08
2018-08-08 07:30 | 102.27 | 84.91
2018-08-08 08:00 | 100.04 | 81.89
2018-08-08 08:30 | 104.07 | 86.5
2018-08-08 09:00 | 105.57 | 88.15
2018-08-08 09:30 | 116.15 | 98.66
2018-08-08 10:00 | 113.96 | 96.44
2018-08-08 10:30 | 113.61 | 95.54
2018-08-08 11:00 | 111.14 | 91.53
2018-08-08 11:30 | 110.57 | 90.57
2018-08-08 12:00 | 108.36 | 86.99
2018-08-08 12:30 | 108.22 | 87.85
2018-08-08 13:00 | 109.1 | 89.11
2018-08-08 13:30 | 111.04 | 91.76
2018-08-08 14:00 | 113.05 | 93.98
2018-08-08 14:30 | 106.34 | 85.62
2018-08-08 15:00 | 109.74 | 89.93
2018-08-08 15:30 | 112.08 | 93.54
2018-08-08 16:00 | 114.28 | 95.92
2018-08-08 16:30 | 114.93 | 96.86
2018-08-08 17:00 | 113.73 | 96.46
2018-08-08 17:30 | 120.12 | 103.48
2018-08-08 18:00 | 116.68 | 98.99
2018-08-08 18:30 | 118.45 | 101.81
2018-08-08 19:00 | 122.28 | 107.03
2018-08-08 19:30 | 117.41 | 101.33
2018-08-08 20:00 | 114.38 | 98.41
2018-08-08 20:30 | 119.81 | 104.81
2018-08-08 21:00 | 117.08 | 100.78
2018-08-08 21:30 | 116.7 | 101.51
2018-08-08 22:00 | 116.25 | 99.51
2018-08-08 22:30 | 115.08 | 97.2
2018-08-08 23:00 | 112.03 | 94.71
2018-08-08 23:30 | 121.44 | 106.69
2018-08-09 | 121.05 | 104.75
2018-08-09 00:30 | 116.11 | 98.03
2018-08-09 01:00 | 116.28 | 98.52
2018-08-09 01:30 | 113.26 | 93.21
2018-08-09 02:00 | 117.12 | 98.59
2018-08-09 02:30 | 118.93 | 100.9
2018-08-09 03:00 | 117.79 | 98.72
2018-08-09 03:30 | 121.18 | 103.09
2018-08-09 04:00 | 119.56 | 101.97
2018-08-09 04:30 | 114.16 | 97.36
2018-08-09 05:00 | 112.83 | 95.05
2018-08-09 05:30 | 117.26 | 100.28
2018-08-09 06:00 | 124.8 | 109.62
2018-08-09 06:30 | 113.38 | 95.17
2018-08-09 07:00 | 126.01 | 110.27
2018-08-09 07:30 | 123.75 | 106.87
2018-08-09 08:00 | 121.38 | 103.29
2018-08-09 08:30 | 118.23 | 98.44
2018-08-09 09:00 | 112.12 | 92.72
2018-08-09 09:30 | 115.5 | 96.7
2018-08-09 10:00 | 109.72 | 89.1
2018-08-09 10:30 | 107.02 | 85.12
2018-08-09 11:00 | 108.45 | 85.47
2018-08-09 11:30 | 112.45 | 92.24
2018-08-09 12:00 | 114.67 | 94.57
2018-08-09 12:30 | 122.81 | 103.9
2018-08-09 13:00 | 117.71 | 96.87
2018-08-09 13:30 | 117.39 | 95.67
2018-08-09 14:00 | 122.74 | 105.07
2018-08-09 14:30 | 122.86 | 105.3
2018-08-09 15:00 | 116.27 | 97.2
2018-08-09 15:30 | 117.28 | 98.9
2018-08-09 16:00 | 112.81 | 93.9
2018-08-09 16:30 | 113.12 | 94.24
2018-08-09 17:00 | 107.6 | 86.75
2018-08-09 17:30 | 110.65 | 91.44
2018-08-09 18:00 | 112.17 | 94.71
2018-08-09 18:30 | 107.22 | 88.47
2018-08-09 19:00 | 114.57 | 98.51
2018-08-09 19:30 | 113.7 | 97.25
2018-08-09 20:00 | 110.09 | 93.31
2018-08-09 20:30 | 108.46 | 91.69
2018-08-09 21:00 | 108.9 | 91.29
2018-08-09 21:30 | 106.2 | 88.25
2018-08-09 22:00 | 111.12 | 93.67
2018-08-09 22:30 | 117.56 | 101.68
2018-08-09 23:00 | 111.65 | 92.99
2018-08-09 23:30 | 115.38 | 97.46
2018-08-10 | 119.41 | 103.79
2018-08-10 00:30 | 118.2 | 102.14
2018-08-10 01:00 | 116.58 | 99.92
2018-08-10 01:30 | 115.62 | 98.01
2018-08-10 02:00 | 120.35 | 103.11
2018-08-10 02:30 | 120.51 | 104.1
2018-08-10 03:00 | 119.09 | 101.83
2018-08-10 03:30 | 116.79 | 98.86
2018-08-10 04:00 | 109.34 | 90.12
2018-08-10 04:30 | 108.96 | 90.53
2018-08-10 05:00 | 109.06 | 91.22
2018-08-10 05:30 | 116.57 | 100.74
2018-08-10 06:00 | 113.92 | 96.47
2018-08-10 06:30 | 115.39 | 98.72
2018-08-10 07:00 | 123.08 | 107.72
2018-08-10 07:30 | 116.32 | 101.21
2018-08-10 08:00 | 114.96 | 99.99
2018-08-10 08:30 | 119.01 | 106.49
2018-08-10 09:00 | 119.35 | 105.4
2018-08-10 09:30 | 111.15 | 95.09
2018-08-10 10:00 | 115.1 | 100.05
2018-08-10 10:30 | 119.92 | 105.68
2018-08-10 11:00 | 110.52 | 93.06
2018-08-10 11:30 | 113.55 | 98.25
2018-08-10 12:00 | 116.67 | 101.46
2018-08-10 12:30 | 116.07 | 98.87
2018-08-10 13:00 | 116.28 | 98.06
2018-08-10 13:30 | 115.48 | 97.25
2018-08-10 14:00 | 124.99 | 109.8
2018-08-10 14:30 | 123.68 | 107.63
2018-08-10 15:00 | 118.35 | 101.1
2018-08-10 15:30 | 117.68 | 100.03
2018-08-10 16:00 | 119.16 | 102.57
2018-08-10 16:30 | 118.8 | 104.05
2018-08-10 17:00 | 114.76 | 97.8
2018-08-10 17:30 | 120.66 | 106.79
2018-08-10 18:00 | 116.72 | 103.03
2018-08-10 18:30 | 112.39 | 97.75
2018-08-10 19:00 | 116.2 | 103.07
2018-08-10 19:30 | 113.78 | 99.1
2018-08-10 20:00 | 115.51 | 100.9
2018-08-10 20:30 | 112.49 | 97
2018-08-10 21:00 | 114.72 | 99.47
2018-08-10 21:30 | 118.7 | 105.35
2018-08-10 22:00 | 112.25 | 96.68
2018-08-10 22:30 | 107.47 | 91.21
2018-08-10 23:00 | 112.27 | 96.11
2018-08-10 23:30 | 112.73 | 96.33
2018-08-11 | 119.09 | 104.79
2018-08-11 00:30 | 122.01 | 108.1
2018-08-11 01:00 | 123.19 | 109.17
2018-08-11 01:30 | 127.6 | 114.86
2018-08-11 02:00 | 127.12 | 114.96
2018-08-11 02:30 | 120.72 | 107.97
2018-08-11 03:00 | 121.32 | 107.48
2018-08-11 03:30 | 114.71 | 98.35
2018-08-11 04:00 | 118.05 | 100.98
2018-08-11 04:30 | 117.33 | 101.83
2018-08-11 05:00 | 117.08 | 102.29
2018-08-11 05:30 | 121.74 | 107.42
2018-08-11 06:00 | 117.37 | 102.83
2018-08-11 06:30 | 119.14 | 104.28
2018-08-11 07:00 | 118.83 | 103.17
2018-08-11 07:30 | 115.69 | 100.21
2018-08-11 08:00 | 115.5 | 99.14
2018-08-11 08:30 | 113.43 | 98.24
2018-08-11 09:00 | 113.2 | 97.16
2018-08-11 09:30 | 114.77 | 98.25
2018-08-11 10:00 | 108.45 | 91.33
2018-08-11 10:30 | 111.94 | 95.37
2018-08-11 11:00 | 111.61 | 94.53
2018-08-11 11:30 | 114.09 | 96.28
2018-08-11 12:00 | 110.88 | 93.44
2018-08-11 12:30 | 112.72 | 95.73
2018-08-11 13:00 | 109.2 | 91.86
2018-08-11 13:30 | 113.24 | 96.75
2018-08-11 14:00 | 111.76 | 95.43
2018-08-11 14:30 | 122.88 | 110.14
2018-08-11 15:00 | 112.45 | 96.43
2018-08-11 15:30 | 117.12 | 102.44
2018-08-11 16:00 | 115.88 | 100.5
2018-08-11 16:30 | 114.84 | 100.94
2018-08-11 17:00 | 117.19 | 103.46
2018-08-11 17:30 | 110.89 | 96.56
2018-08-11 18:00 | 114.02 | 101.59
2018-08-11 18:30 | 105.41 | 91.53
2018-08-11 19:00 | 109.75 | 97.43
2018-08-11 19:30 | 113.56 | 101.74
2018-08-11 20:00 | 113.39 | 101.55
2018-08-11 20:30 | 112.27 | 99.31
2018-08-11 21:00 | 109.76 | 95.98
2018-08-11 21:30 | 113.12 | 101.11
2018-08-11 22:00 | 112.49 | 99.09
2018-08-11 22:30 | 116.24 | 101.75
2018-08-11 23:00 | 113.11 | 97.7
2018-08-11 23:30 | 109.5 | 92.6
2018-08-12 | 113.39 | 98.03
2018-08-12 00:30 | 115.6 | 101.06
2018-08-12 01:00 | 112.11 | 96.39
2018-08-12 01:30 | 110.34 | 95.82
2018-08-12 02:00 | 117.18 | 103.48
2018-08-12 02:30 | 111.55 | 95.19
2018-08-12 03:00 | 113.32 | 97.24
2018-08-12 03:30 | 110.2 | 93.83
2018-08-12 04:00 | 110.26 | 93.92
2018-08-12 04:30 | 110.31 | 94.07
2018-08-12 05:00 | 104.76 | 86.72
2018-08-12 05:30 | 112.48 | 97.16
2018-08-12 06:00 | 111.82 | 94.41
2018-08-12 06:30 | 111.87 | 95.38
2018-08-12 07:00 | 114.02 | 97.85
2018-08-12 07:30 | 114.37 | 98.86
2018-08-12 08:00 | 112.3 | 94.82
2018-08-12 08:30 | 115.51 | 99.73
2018-08-12 09:00 | 105.66 | 87.88
2018-08-12 09:30 | 109.32 | 93.61
2018-08-12 10:00 | 107.47 | 91.34
2018-08-12 10:30 | 112.55 | 97.83
2018-08-12 11:00 | 110.11 | 94.34
2018-08-12 11:30 | 114.09 | 99.21
2018-08-12 12:00 | 115.43 | 100.34
2018-08-12 12:30 | 110.9 | 93.61
2018-08-12 13:00 | 112.57 | 94.44
2018-08-12 13:30 | 114.97 | 98.57
2018-08-12 14:00 | 117.32 | 101.41
2018-08-12 14:30 | 115.98 | 100.11
2018-08-12 15:00 | 115.79 | 97.56
2018-08-12 15:30 | 116.24 | 100.71
2018-08-12 16:00 | 116.75 | 102.45
2018-08-12 16:30 | 115.16 | 99.92
2018-08-12 17:00 | 115.4 | 99.42
2018-08-12 17:30 | 115.67 | 99.55
2018-08-12 18:00 | 118.31 | 105.07
2018-08-12 18:30 | 116.54 | 103.44
2018-08-12 19:00 | 113.87 | 99.73
2018-08-12 19:30 | 110.32 | 96.32
2018-08-12 20:00 | 110.71 | 97.26
2018-08-12 20:30 | 108.36 | 94.1
2018-08-12 21:00 | 113.18 | 98.47
2018-08-12 21:30 | 113.31 | 98.42
2018-08-12 22:00 | 116.81 | 102.43
2018-08-12 22:30 | 116.98 | 102.3
2018-08-12 23:00 | 115.35 | 99.47
2018-08-12 23:30 | 118.7 | 103.79
2018-08-13 | 114.88 | 99.3
2018-08-13 00:30 | 110.2 | 94.12
2018-08-13 01:00 | 119.9 | 105.6
2018-08-13 01:30 | 118.6 | 103.53
2018-08-13 02:00 | 113.6 | 97.7
2018-08-13 02:30 | 115.35 | 99.96
2018-08-13 03:00 | 112.65 | 95.35
2018-08-13 03:30 | 109.2 | 91.43
2018-08-13 04:00 | 111.21 | 94.23
2018-08-13 04:30 | 110.29 | 93.12
2018-08-13 05:00 | 109.87 | 92.36
2018-08-13 05:30 | 111.75 | 95.02
2018-08-13 06:00 | 111.46 | 94.38
2018-08-13 06:30 | 102 | 82.75
2018-08-13 07:00 | 107.48 | 90.2
2018-08-13 07:30 | 111.98 | 95.84
2018-08-13 08:00 | 108.97 | 90.38
2018-08-13 08:30 | 110.57 | 91.69
2018-08-13 09:00 | 101.77 | 86.49
2018-08-13 09:30 | 97.94 | 82.77
2018-08-13 10:00 | 96.07 | 80.72
2018-08-13 10:30 | 94.3 | 78.68
2018-08-13 11:00 | 93.66 | 78.26
2018-08-13 11:30 | 88.34 | 72.96
2018-08-13 12:00 | 92.79 | 77.51
2018-08-13 12:30 | 92.18 | 76.36
2018-08-13 13:00 | 91.37 | 75.99
2018-08-13 13:30 | 93.29 | 78.34
2018-08-13 14:00 | 96.02 | 81.48
2018-08-13 14:30 | 97.8 | 83.39
2018-08-13 15:00 | 93.61 | 78.84
2018-08-13 15:30 | 91.37 | 79.14
2018-08-13 16:00 | 96.44 | 82.73
2018-08-13 16:30 | 95.65 | 81.31
2018-08-13 17:00 | 93.41 | 78.51
2018-08-13 17:30 | 96.47 | 81.08
2018-08-13 18:00 | 98.98 | 82.31
2018-08-13 18:30 | 95.17 | 77.72
2018-08-13 19:00 | 100.54 | 82.57
2018-08-13 19:30 | 107.56 | 90.55
2018-08-13 20:00 | 106.73 | 89.68
2018-08-13 20:30 | 106.94 | 91.1
2018-08-13 21:00 | 103.58 | 87.5
2018-08-13 21:30 | 103.8 | 87.52
2018-08-13 22:00 | 106.53 | 91.21
2018-08-13 22:30 | 103.59 | 88.25
2018-08-13 23:00 | 98.35 | 81.93
2018-08-13 23:30 | 97 | 80.43
2018-08-14 | 103.01 | 88.26
2018-08-14 00:30 | 100.86 | 86.77
2018-08-14 01:00 | 99.37 | 84.84
2018-08-14 01:30 | 98.97 | 85.15
2018-08-14 02:00 | 99.98 | 86.82
2018-08-14 02:30 | 103.09 | 90.31
2018-08-14 03:00 | 97.65 | 84.54
2018-08-14 03:30 | 98.5 | 85.77
2018-08-14 04:00 | 94.56 | 81.94
2018-08-14 04:30 | 90.51 | 76.38
2018-08-14 05:00 | 88.22 | 74.42
2018-08-14 05:30 | 90.45 | 77.04
2018-08-14 06:00 | 89.65 | 76.93
2018-08-14 06:30 | 87.11 | 73.45
2018-08-14 07:00 | 89.34 | 76.37
2018-08-14 07:30 | 95.59 | 83.39
2018-08-14 08:00 | 89.39 | 74.09
2018-08-14 08:30 | 89.08 | 69.42
2018-08-14 09:00 | 92.3 | 74.13
2018-08-14 09:30 | 88.04 | 68.11
2018-08-14 10:00 | 87.77 | 68.11
2018-08-14 10:30 | 96.48 | 80.17
2018-08-14 11:00 | 93.4 | 75.31
2018-08-14 11:30 | 94.53 | 76.98
2018-08-14 12:00 | 92.15 | 73.57
2018-08-14 12:30 | 94.03 | 76.28
2018-08-14 13:00 | 91.4 | 73.86
2018-08-14 13:30 | 94.97 | 78.28
2018-08-14 14:00 | 94.59 | 77.07
2018-08-14 14:30 | 93.65 | 75.44
2018-08-14 15:00 | 88.88 | 69.54
2018-08-14 15:30 | 91.8 | 72.98
2018-08-14 16:00 | 93.24 | 73.95
2018-08-14 16:30 | 94.48 | 74.4
2018-08-14 17:00 | 93.61 | 73.82
2018-08-14 17:30 | 100.3 | 80.39
2018-08-14 18:00 | 105.72 | 85.67
2018-08-14 18:30 | 101.3 | 78.89
2018-08-14 19:00 | 102.66 | 81.06
2018-08-14 19:30 | 112.94 | 92.9
2018-08-14 20:00 | 121 | 101.13
2018-08-14 20:30 | 113.53 | 92.37
2018-08-14 21:00 | 107.54 | 85.42
2018-08-14 21:30 | 109.56 | 88.16
2018-08-14 22:00 | 104.1 | 82.72
2018-08-14 22:30 | 102.67 | 81.43
2018-08-14 23:00 | 105.16 | 84.85
2018-08-14 23:30 | 116.23 | 97.19
2018-08-15 | 105.95 | 85.59
2018-08-15 00:30 | 106.46 | 86.2
2018-08-15 01:00 | 110.02 | 92.03
2018-08-15 01:30 | 106.1 | 88.43
2018-08-15 02:00 | 98.24 | 81.02
2018-08-15 02:30 | 100.82 | 83.85
2018-08-15 03:00 | 100.46 | 83.64
2018-08-15 03:30 | 100.37 | 83.23
2018-08-15 04:00 | 99.33 | 82.87
2018-08-15 04:30 | 102.58 | 86.06
2018-08-15 05:00 | 96.89 | 79.3
2018-08-15 05:30 | 98.45 | 80.75
2018-08-15 06:00 | 101.98 | 84.79
2018-08-15 06:30 | 93.41 | 75.95
2018-08-15 07:00 | 97.75 | 79.81
2018-08-15 07:30 | 98.43 | 80.27
2018-08-15 08:00 | 102.67 | 84.24
2018-08-15 08:30 | 94.1 | 75.03
2018-08-15 09:00 | 99.31 | 81.67
2018-08-15 09:30 | 94.05 | 76.14
2018-08-15 10:00 | 93.55 | 74.79
2018-08-15 10:30 | 89.05 | 70.51
2018-08-15 11:00 | 93.14 | 74.76
2018-08-15 11:30 | 88.4 | 69.39
2018-08-15 12:00 | 90.17 | 71.1
2018-08-15 12:30 | 98.44 | 79.63
2018-08-15 13:00 | 97.75 | 79.6
2018-08-15 13:30 | 91.37 | 72.73
2018-08-15 14:00 | 88.66 | 70.22
2018-08-15 14:30 | 86.72 | 66.14
2018-08-15 15:00 | 87.5 | 67.03
2018-08-15 15:30 | 86.54 | 66.19
2018-08-15 16:00 | 89.6 | 70.59
2018-08-15 16:30 | 94.34 | 74.82
2018-08-15 17:00 | 91.54 | 71.79
2018-08-15 17:30 | 91.58 | 70.7
2018-08-15 18:00 | 95.78 | 75.86
2018-08-15 18:30 | 92.23 | 72.05
2018-08-15 19:00 | 89.64 | 68.86
2018-08-15 19:30 | 91.26 | 71.19
2018-08-15 20:00 | 97.99 | 78.81
2018-08-15 20:30 | 97.57 | 79.02
2018-08-15 21:00 | 92.13 | 73.28
2018-08-15 21:30 | 100.64 | 83.33
2018-08-15 22:00 | 93.41 | 75.87
2018-08-15 22:30 | 98.18 | 80.34
2018-08-15 23:00 | 104.05 | 86.5
2018-08-15 23:30 | 98.84 | 81.62
2018-08-16 | 104.88 | 87.62
2018-08-16 00:30 | 103.56 | 86.17
2018-08-16 01:00 | 108.11 | 91.1
2018-08-16 01:30 | 103.15 | 86.17
2018-08-16 02:00 | 101.99 | 84.99
2018-08-16 02:30 | 99.41 | 82.66
2018-08-16 03:00 | 96.7 | 79.91
2018-08-16 03:30 | 111.44 | 94.71
2018-08-16 04:00 | 106.85 | 89.55
2018-08-16 04:30 | 105.86 | 88.06
2018-08-16 05:00 | 110.53 | 93.67
2018-08-16 05:30 | 102.43 | 84.6
2018-08-16 06:00 | 98.91 | 80.98
2018-08-16 06:30 | 98.94 | 80.27
2018-08-16 07:00 | 104.99 | 87.3
2018-08-16 07:30 | 103.05 | 84.78
2018-08-16 08:00 | 94.24 | 74.93
2018-08-16 08:30 | 97.93 | 77.79
2018-08-16 09:00 | 107.26 | 88.14
2018-08-16 09:30 | 105.33 | 86.85
2018-08-16 10:00 | 107.01 | 88.96
2018-08-16 10:30 | 107.58 | 89.58
2018-08-16 11:00 | 101.88 | 82.7
2018-08-16 11:30 | 94.38 | 75.05
2018-08-16 12:00 | 97.2 | 78.16
2018-08-16 12:30 | 99.51 | 79.67
2018-08-16 13:00 | 100.9 | 82.61
2018-08-16 13:30 | 102.76 | 83.47
2018-08-16 14:00 | 101.11 | 81.91
2018-08-16 14:30 | 96.65 | 78.15
2018-08-16 15:00 | 98.58 | 80.68
2018-08-16 15:30 | 100.51 | 81.81
2018-08-16 16:00 | 104.29 | 85.48
2018-08-16 16:30 | 106.07 | 85.96
2018-08-16 17:00 | 100.5 | 81.44
2018-08-16 17:30 | 108.07 | 89.32
2018-08-16 18:00 | 104.46 | 84.4
2018-08-16 18:30 | 107.69 | 89.13
2018-08-16 19:00 | 105.55 | 86.82
2018-08-16 19:30 | 107.41 | 87.84
2018-08-16 20:00 | 108.82 | 88.58
2018-08-16 20:30 | 114.68 | 92.33
2018-08-16 21:00 | 115.26 | 91.99
2018-08-16 21:30 | 116.43 | 94.17
2018-08-16 22:00 | 114.89 | 91.97
2018-08-16 22:30 | 116.91 | 93.97
2018-08-16 23:00 | 116.93 | 95.14
2018-08-16 23:30 | 112.4 | 91.52
2018-08-17 | 113.96 | 91.22
2018-08-17 00:30 | 114.08 | 89.91
2018-08-17 01:00 | 115.58 | 92.08
2018-08-17 01:30 | 115.3 | 92.02
2018-08-17 02:00 | 113.52 | 89.45
2018-08-17 02:30 | 112.15 | 88.14
2018-08-17 03:00 | 117.96 | 94.19
2018-08-17 03:30 | 116.13 | 93.1
2018-08-17 04:00 | 117 | 94.21
2018-08-17 04:30 | 117.61 | 95.28
2018-08-17 05:00 | 116.54 | 93.44
2018-08-17 05:30 | 114.42 | 91.81
2018-08-17 06:00 | 117.15 | 94.72
2018-08-17 06:30 | 109.34 | 86.32
2018-08-17 07:00 | 115.81 | 92.69
2018-08-17 07:30 | 111.06 | 86.76
2018-08-17 08:00 | 107.75 | 84.49
2018-08-17 08:30 | 104.57 | 81.49
2018-08-17 09:00 | 107.78 | 85.18
2018-08-17 09:30 | 107.6 | 84.46
2018-08-17 10:00 | 106.49 | 82.4
2018-08-17 10:30 | 110.2 | 88.15
2018-08-17 11:00 | 103.48 | 80.91
2018-08-17 11:30 | 101 | 77.4
2018-08-17 12:00 | 112.01 | 89.22
2018-08-17 12:30 | 113.39 | 90.9
2018-08-17 13:00 | 116.09 | 94.99
2018-08-17 13:30 | 117.85 | 96.72
2018-08-17 14:00 | 116.49 | 94.52
2018-08-17 14:30 | 107.77 | 85.02
2018-08-17 15:00 | 113.54 | 92.96
2018-08-17 15:30 | 113.82 | 92.63
2018-08-17 16:00 | 117.1 | 94.58
2018-08-17 16:30 | 106.63 | 81.71
2018-08-17 17:00 | 108.37 | 84.73
2018-08-17 17:30 | 109.21 | 84.72
2018-08-17 18:00 | 110.71 | 84.74
2018-08-17 18:30 | 113.54 | 88.6
2018-08-17 19:00 | 115.38 | 93.13
2018-08-17 19:30 | 117.82 | 96.06
2018-08-17 20:00 | 121.46 | 99.45
2018-08-17 20:30 | 117.9 | 96
2018-08-17 21:00 | 113.56 | 91.76
2018-08-17 21:30 | 111.63 | 88.96
2018-08-17 22:00 | 111.24 | 88.95
2018-08-17 22:30 | 111.07 | 89.13
2018-08-17 23:00 | 114.25 | 94.98
2018-08-17 23:30 | 116.35 | 98.72
2018-08-18 | 109.99 | 91.83
2018-08-18 00:30 | 106.29 | 87.36
2018-08-18 01:00 | 105.98 | 86.34
2018-08-18 01:30 | 107.78 | 86.82
2018-08-18 02:00 | 102.17 | 80.15
2018-08-18 02:30 | 107.4 | 87.23
2018-08-18 03:00 | 102.97 | 82.13
2018-08-18 03:30 | 105.55 | 85.39
2018-08-18 04:00 | 101.09 | 80.93
2018-08-18 04:30 | 109.71 | 89.54
2018-08-18 05:00 | 111.15 | 92.62
2018-08-18 05:30 | 112.22 | 92.88
2018-08-18 06:00 | 112.89 | 92.74
2018-08-18 06:30 | 108.35 | 88.27
2018-08-18 07:00 | 111.45 | 93.24
2018-08-18 07:30 | 112.77 | 94.68
2018-08-18 08:00 | 105.5 | 87.39
2018-08-18 08:30 | 102.57 | 84.22
2018-08-18 09:00 | 109.92 | 91.59
2018-08-18 09:30 | 99.84 | 80.3
2018-08-18 10:00 | 100.88 | 81.58
2018-08-18 10:30 | 102.05 | 83.48
2018-08-18 11:00 | 97.4 | 78.13
2018-08-18 11:30 | 103.86 | 84.75
2018-08-18 12:00 | 95.17 | 75.64
2018-08-18 12:30 | 98.39 | 78.87
2018-08-18 13:00 | 101.27 | 80.51
2018-08-18 13:30 | 108.62 | 88.86
2018-08-18 14:00 | 109.71 | 88.77
2018-08-18 14:30 | 108.83 | 87.34
2018-08-18 15:00 | 119.03 | 96.08
2018-08-18 15:30 | 120.48 | 98.71
2018-08-18 16:00 | 115.1 | 92.61
2018-08-18 16:30 | 119.21 | 96.73
2018-08-18 17:00 | 121.57 | 98.43
2018-08-18 17:30 | 122.15 | 99.32
2018-08-18 18:00 | 114.97 | 91.54
2018-08-18 18:30 | 112.39 | 88.65
2018-08-18 19:00 | 116.16 | 93.8
2018-08-18 19:30 | 122.79 | 101.42
2018-08-18 20:00 | 126.13 | 104.08
2018-08-18 20:30 | 128.62 | 107.23
2018-08-18 21:00 | 123.38 | 102.4
2018-08-18 21:30 | 121.66 | 101.46
2018-08-18 22:00 | 122.45 | 101.73
2018-08-18 22:30 | 123.83 | 103.6
2018-08-18 23:00 | 114.78 | 93.45
2018-08-18 23:30 | 107.32 | 85.15
2018-08-19 | 103.97 | 82.44
2018-08-19 00:30 | 110.34 | 89.14
2018-08-19 01:00 | 107.97 | 86.42
2018-08-19 01:30 | 108.72 | 87.43
2018-08-19 02:00 | 110.84 | 90.49
2018-08-19 02:30 | 118.94 | 99.96
2018-08-19 03:00 | 115.07 | 95.2
2018-08-19 03:30 | 121.75 | 102.65
2018-08-19 04:00 | 117.19 | 97.59
2018-08-19 04:30 | 108.53 | 89.76
2018-08-19 05:00 | 115.16 | 95.78
2018-08-19 05:30 | 113.43 | 94.25
2018-08-19 06:00 | 104.31 | 85.51
2018-08-19 06:30 | 96.58 | 76.98
2018-08-19 07:00 | 102.58 | 82.97
2018-08-19 07:30 | 106.97 | 88.1
2018-08-19 08:00 | 108.34 | 89.26
2018-08-19 08:30 | 106.79 | 87.09
2018-08-19 09:00 | 107.17 | 87.16
2018-08-19 09:30 | 106.97 | 88.63
2018-08-19 10:00 | 114.72 | 95.29
2018-08-19 10:30 | 115.04 | 94.48
2018-08-19 11:00 | 111.71 | 91.28
2018-08-19 11:30 | 108.16 | 87.13
2018-08-19 12:00 | 112.18 | 91.25
2018-08-19 12:30 | 116.13 | 94.06
2018-08-19 13:00 | 115.9 | 94.57
2018-08-19 13:30 | 111.09 | 90.85
2018-08-19 14:00 | 112.99 | 91.94
2018-08-19 14:30 | 112.39 | 92.36
2018-08-19 15:00 | 116.31 | 96.1
2018-08-19 15:30 | 114.13 | 93.92
2018-08-19 16:00 | 108.93 | 86.77
2018-08-19 16:30 | 112.58 | 90.21
2018-08-19 17:00 | 118.72 | 97.09
2018-08-19 17:30 | 124.33 | 102.88
2018-08-19 18:00 | 122.38 | 101.11
2018-08-19 18:30 | 111.15 | 88.37
2018-08-19 19:00 | 117.25 | 95.65
2018-08-19 19:30 | 116.66 | 95.32
2018-08-19 20:00 | 120.22 | 98.16
2018-08-19 20:30 | 119.19 | 95.15
2018-08-19 21:00 | 119.63 | 97.2
2018-08-19 21:30 | 114.39 | 94.88
2018-08-19 22:00 | 120.6 | 98.76
2018-08-19 22:30 | 120.78 | 99.93
2018-08-19 23:00 | 120.83 | 99.05
2018-08-19 23:30 | 116.97 | 95.91
2018-08-20 | 121.89 | 101.66
2018-08-20 00:30 | 122.36 | 103.01
2018-08-20 01:00 | 124.33 | 105.54
2018-08-20 01:30 | 120.74 | 101.74
2018-08-20 02:00 | 121.09 | 101.78
2018-08-20 02:30 | 119.49 | 99.12
2018-08-20 03:00 | 115.5 | 94.59
2018-08-20 03:30 | 118.4 | 97.88
2018-08-20 04:00 | 117.53 | 96.49
2018-08-20 04:30 | 118.22 | 96.49
2018-08-20 05:00 | 114.73 | 94.29
2018-08-20 05:30 | 122.25 | 101.99
2018-08-20 06:00 | 124.24 | 104.47
2018-08-20 06:30 | 112.23 | 92.61
2018-08-20 07:00 | 118.22 | 98.03
2018-08-20 07:30 | 118.36 | 98.6
2018-08-20 08:00 | 112.78 | 93.95
2018-08-20 08:30 | 116.45 | 95.86
2018-08-20 09:00 | 115.05 | 93.49
2018-08-20 09:30 | 111.65 | 89.27
2018-08-20 10:00 | 109.64 | 85.7
2018-08-20 10:30 | 110.19 | 87.64
2018-08-20 11:00 | 114.35 | 91.16
2018-08-20 11:30 | 113.83 | 90.68
2018-08-20 12:00 | 110.67 | 88.97
2018-08-20 12:30 | 109.55 | 85.4
2018-08-20 13:00 | 109.06 | 84.93
2018-08-20 13:30 | 110.81 | 86.98
2018-08-20 14:00 | 112.58 | 88.74
2018-08-20 14:30 | 111.46 | 86.8
2018-08-20 15:00 | 111.76 | 89.58
2018-08-20 15:30 | 106.8 | 85.93
2018-08-20 16:00 | 102.3 | 80.31
2018-08-20 16:30 | 104.88 | 83
2018-08-20 17:00 | 108.83 | 85.28
2018-08-20 17:30 | 116.63 | 93.55
2018-08-20 18:00 | 113.36 | 89.07
2018-08-20 18:30 | 115.39 | 92.92
2018-08-20 19:00 | 119.87 | 96.84
2018-08-20 19:30 | 118.96 | 97.01
2018-08-20 20:00 | 118.07 | 96.15
2018-08-20 20:30 | 129.02 | 106.6
2018-08-20 21:00 | 122.32 | 100.8
2018-08-20 21:30 | 113.45 | 89.94
2018-08-20 22:00 | 115.47 | 92.28
2018-08-20 22:30 | 117.26 | 95.86
2018-08-20 23:00 | 117 | 94.52
2018-08-20 23:30 | 118.84 | 97.27
2018-08-21 | 112.34 | 91.71
2018-08-21 00:30 | 120.36 | 99.32
2018-08-21 01:00 | 121.98 | 101.64
2018-08-21 01:30 | 114.12 | 92.98
2018-08-21 02:00 | 118.03 | 97.23
2018-08-21 02:30 | 117.7 | 96.58
2018-08-21 03:00 | 120.4 | 98.74
2018-08-21 03:30 | 118.31 | 97.19
2018-08-21 04:00 | 116.88 | 96.23
2018-08-21 04:30 | 118.39 | 98.03
2018-08-21 05:00 | 120.39 | 101.65
2018-08-21 05:30 | 116.7 | 97.49
2018-08-21 06:00 | 118.24 | 98.9
2018-08-21 06:30 | 109.96 | 89.75
2018-08-21 07:00 | 110.71 | 90.98
2018-08-21 07:30 | 114.63 | 95.43
2018-08-21 08:00 | 112.39 | 92.45
2018-08-21 08:30 | 103.58 | 83.78
2018-08-21 09:00 | 104.84 | 85.83
2018-08-21 09:30 | 98.52 | 80.17
2018-08-21 10:00 | 99.64 | 82.45
2018-08-21 10:30 | 100.56 | 83.18
2018-08-21 11:00 | 100.62 | 83.44
2018-08-21 11:30 | 100.85 | 83.45
2018-08-21 12:00 | 99.13 | 81.16
2018-08-21 12:30 | 102.06 | 84.26
2018-08-21 13:00 | 105.91 | 88.24
2018-08-21 13:30 | 106.58 | 88.87
2018-08-21 14:00 | 106.07 | 88.06
2018-08-21 14:30 | 114.14 | 96.3
2018-08-21 15:00 | 104.91 | 85.81
2018-08-21 15:30 | 104.87 | 85.26
2018-08-21 16:00 | 105.27 | 86.44
2018-08-21 16:30 | 105.03 | 85.59
2018-08-21 17:00 | 114.22 | 95.18
2018-08-21 17:30 | 108.6 | 86.26
2018-08-21 18:00 | 101 | 76.76
2018-08-21 18:30 | 111.35 | 87.94
2018-08-21 19:00 | 118.61 | 92.3
2018-08-21 19:30 | 120.63 | 95.4
2018-08-21 20:00 | 116.58 | 93.51
2018-08-21 20:30 | 130.24 | 106.99
2018-08-21 21:00 | 120.74 | 99.32
2018-08-21 21:30 | 118.28 | 96.07
2018-08-21 22:00 | 120.42 | 96.04
2018-08-21 22:30 | 121.89 | 96.85
2018-08-21 23:00 | 118.7 | 94.65
2018-08-21 23:30 | 119.04 | 96.08
2018-08-22 | 111.1 | 86.93
2018-08-22 00:30 | 106.57 | 82.06
2018-08-22 01:00 | 114.1 | 90.56
2018-08-22 01:30 | 108.4 | 84.74
2018-08-22 02:00 | 120.23 | 97.81
2018-08-22 02:30 | 119.93 | 97.61
2018-08-22 03:00 | 121.06 | 98.38
2018-08-22 03:30 | 125.41 | 101.38
2018-08-22 04:00 | 120.92 | 96.37
2018-08-22 04:30 | 121.84 | 96.67
2018-08-22 05:00 | 115.15 | 90.92
2018-08-22 05:30 | 115.43 | 90.99
2018-08-22 06:00 | 116.6 | 93.37
2018-08-22 06:30 | 110.13 | 87
2018-08-22 07:00 | 109.32 | 87.81
2018-08-22 07:30 | 107.94 | 87.1
2018-08-22 08:00 | 108.93 | 87.77
2018-08-22 08:30 | 110.73 | 89.42
2018-08-22 09:00 | 104.68 | 83.62
2018-08-22 09:30 | 100.22 | 78.65
2018-08-22 10:00 | 99.67 | 80.47
2018-08-22 10:30 | 97.99 | 78.22
2018-08-22 11:00 | 101.56 | 83.42
2018-08-22 11:30 | 105.25 | 85.72
2018-08-22 12:00 | 109.11 | 90.05
2018-08-22 12:30 | 103.54 | 83.46
2018-08-22 13:00 | 106.95 | 88.53
2018-08-22 13:30 | 102.23 | 82.67
2018-08-22 14:00 | 105.59 | 84.4
2018-08-22 14:30 | 101.09 | 80.78
2018-08-22 15:00 | 106.04 | 85.39
2018-08-22 15:30 | 100.15 | 78.62
2018-08-22 16:00 | 101.16 | 80.26
2018-08-22 16:30 | 106.12 | 84.9
2018-08-22 17:00 | 109.18 | 89.14
2018-08-22 17:30 | 107.92 | 88.85
2018-08-22 18:00 | 107.39 | 89.52
2018-08-22 18:30 | 97.72 | 77.54
2018-08-22 19:00 | 110.76 | 92.07
2018-08-22 19:30 | 116.7 | 98.48
2018-08-22 20:00 | 117.97 | 98.08
2018-08-22 20:30 | 117.01 | 96.63
2018-08-22 21:00 | 115.95 | 97.01
2018-08-22 21:30 | 113.32 | 94.86
2018-08-22 22:00 | 109.65 | 90.38
2018-08-22 22:30 | 119.55 | 97.95
2018-08-22 23:00 | 121.68 | 100.24
2018-08-22 23:30 | 114.14 | 91.36
2018-08-23 | 121.31 | 99.13
2018-08-23 00:30 | 123.49 | 101.06
2018-08-23 01:00 | 125.22 | 103.26
2018-08-23 01:30 | 118.73 | 94.89
2018-08-23 02:00 | 121.68 | 99.95
2018-08-23 02:30 | 119.24 | 97.76
2018-08-23 03:00 | 121.25 | 101.48
2018-08-23 03:30 | 112.94 | 94.15
2018-08-23 04:00 | 125.19 | 104.54
2018-08-23 04:30 | 119.28 | 100.05
2018-08-23 05:00 | 112.8 | 91.73
2018-08-23 05:30 | 112.48 | 90.3
2018-08-23 06:00 | 113.11 | 92.9
2018-08-23 06:30 | 108.09 | 87.92
2018-08-23 07:00 | 124.61 | 102.58
2018-08-23 07:30 | 127.8 | 105.77
2018-08-23 08:00 | 121.17 | 99.95
2018-08-23 08:30 | 118.67 | 98.76
2018-08-23 09:00 | 108.06 | 87.58
2018-08-23 09:30 | 115.42 | 95.27
2018-08-23 10:00 | 113.9 | 94.56
2018-08-23 10:30 | 113.84 | 95.32
2018-08-23 11:00 | 106.93 | 88.22
2018-08-23 11:30 | 113.16 | 95.35
2018-08-23 12:00 | 113.34 | 94.94
2018-08-23 12:30 | 121.13 | 101.06
2018-08-23 13:00 | 122 | 101.93
2018-08-23 13:30 | 122.25 | 103.1
2018-08-23 14:00 | 124.49 | 104.3
2018-08-23 14:30 | 118.36 | 98.79
2018-08-23 15:00 | 111.99 | 90.59
2018-08-23 15:30 | 113.67 | 92.55
2018-08-23 16:00 | 114.16 | 93.5
2018-08-23 16:30 | 117.73 | 96.71
2018-08-23 17:00 | 111.29 | 89.51
2018-08-23 17:30 | 116.73 | 96.44
2018-08-23 18:00 | 117.63 | 96.05
2018-08-23 18:30 | 107.43 | 86.69
2018-08-23 19:00 | 115.03 | 95.99
2018-08-23 19:30 | 112.75 | 93.29
2018-08-23 20:00 | 108.27 | 87.91
2018-08-23 20:30 | 111.03 | 91.62
2018-08-23 21:00 | 114.3 | 94.62
2018-08-23 21:30 | 119.65 | 100.62
2018-08-23 22:00 | 124.93 | 104.64
2018-08-23 22:30 | 121 | 100.19
2018-08-23 23:00 | 128.32 | 104.28
2018-08-23 23:30 | 126.96 | 105.6
2018-08-24 | 129.51 | 108.85
2018-08-24 00:30 | 130.65 | 110.7
2018-08-24 01:00 | 119.48 | 98.57
2018-08-24 01:30 | 121.81 | 101.73
2018-08-24 02:00 | 125.79 | 105.71
2018-08-24 02:30 | 127.53 | 108.7
2018-08-24 03:00 | 118.85 | 99.73
2018-08-24 03:30 | 120.68 | 100.04
2018-08-24 04:00 | 121.16 | 100.7
2018-08-24 04:30 | 118.69 | 100.29
2018-08-24 05:00 | 114.06 | 96.58
2018-08-24 05:30 | 110.64 | 93.3
2018-08-24 06:00 | 118 | 99.65
2018-08-24 06:30 | 121.21 | 101.02
2018-08-24 07:00 | 125.57 | 105.38
2018-08-24 07:30 | 127.77 | 108.94
2018-08-24 08:00 | 129.42 | 109.52
2018-08-24 08:30 | 132.1 | 111.87
2018-08-24 09:00 | 122.51 | 103.93
2018-08-24 09:30 | 120.81 | 101.75
2018-08-24 10:00 | 121.72 | 102.72
2018-08-24 10:30 | 127.77 | 106.16
2018-08-24 11:00 | 130.37 | 109.15
2018-08-24 11:30 | 129.15 | 107.87
2018-08-24 12:00 | 130.79 | 109.91
2018-08-24 12:30 | 137.27 | 116.08
2018-08-24 13:00 | 132.62 | 112.91
2018-08-24 13:30 | 135.86 | 116.99
2018-08-24 14:00 | 136.51 | 116.81
2018-08-24 14:30 | 136.06 | 116.32
2018-08-24 15:00 | 129.86 | 109.22
2018-08-24 15:30 | 130.71 | 111.66
2018-08-24 16:00 | 137.58 | 118.4
2018-08-24 16:30 | 134.61 | 113.82
2018-08-24 17:00 | 133.14 | 112.32
2018-08-24 17:30 | 143.92 | 122.75
2018-08-24 18:00 | 147.71 | 127.22
2018-08-24 18:30 | 136.82 | 114.72
2018-08-24 19:00 | 140.72 | 120.6
2018-08-24 19:30 | 135.42 | 114.8
2018-08-24 20:00 | 135.73 | 115.49
2018-08-24 20:30 | 135.55 | 115.5
2018-08-24 21:00 | 136.29 | 116.71
2018-08-24 21:30 | 139.16 | 119.91
2018-08-24 22:00 | 137.06 | 118.68
2018-08-24 22:30 | 137.46 | 118.99
2018-08-24 23:00 | 135.04 | 116.91
2018-08-24 23:30 | 126.25 | 108.24
2018-08-25 | 133.91 | 114.63
2018-08-25 00:30 | 133.85 | 115.93
2018-08-25 01:00 | 132.27 | 114.65
2018-08-25 01:30 | 130.79 | 113.63
2018-08-25 02:00 | 132.76 | 116.28
2018-08-25 02:30 | 124.85 | 108.25
2018-08-25 03:00 | 132.41 | 116.88
2018-08-25 03:30 | 132.74 | 116.77
2018-08-25 04:00 | 124.53 | 108.32
2018-08-25 04:30 | 130.73 | 114.42
2018-08-25 05:00 | 124.51 | 107.35
2018-08-25 05:30 | 125.29 | 107.88
2018-08-25 06:00 | 121.48 | 105.62
2018-08-25 06:30 | 120.66 | 104.71
2018-08-25 07:00 | 128.07 | 113.09
2018-08-25 07:30 | 138.65 | 124.48
2018-08-25 08:00 | 124.37 | 109.89
2018-08-25 08:30 | 119.86 | 103.64
2018-08-25 09:00 | 137.4 | 122
2018-08-25 09:30 | 123.37 | 105.62
2018-08-25 10:00 | 126.85 | 110.02
2018-08-25 10:30 | 126.05 | 109.4
2018-08-25 11:00 | 117.87 | 100.72
2018-08-25 11:30 | 123.45 | 106.2
2018-08-25 12:00 | 127.17 | 109.73
2018-08-25 12:30 | 122.22 | 104.68
2018-08-25 13:00 | 127.03 | 110.31
2018-08-25 13:30 | 116.8 | 100.03
2018-08-25 14:00 | 124.65 | 107.72
2018-08-25 14:30 | 124.38 | 106.58
2018-08-25 15:00 | 132.52 | 115.17
2018-08-25 15:30 | 135.38 | 118.2
2018-08-25 16:00 | 130.98 | 113.53
2018-08-25 16:30 | 135.81 | 117.48
2018-08-25 17:00 | 131.47 | 111.76
2018-08-25 17:30 | 134.55 | 115.72
2018-08-25 18:00 | 137.38 | 119.53
2018-08-25 18:30 | 121.7 | 103.43
2018-08-25 19:00 | 125.49 | 106.94
2018-08-25 19:30 | 125 | 106.66
2018-08-25 20:00 | 126.07 | 108.24
2018-08-25 20:30 | 127.96 | 109.23
2018-08-25 21:00 | 131.03 | 114.5
2018-08-25 21:30 | 119.92 | 102.38
2018-08-25 22:00 | 132.16 | 113.27
2018-08-25 22:30 | 129.46 | 111.76
2018-08-25 23:00 | 130.47 | 112.3
2018-08-25 23:30 | 141.55 | 125.01
2018-08-26 | 135.31 | 118.91
2018-08-26 00:30 | 127.98 | 111.09
2018-08-26 01:00 | 128.88 | 112.02
2018-08-26 01:30 | 124.27 | 108.04
2018-08-26 02:00 | 127.52 | 111.52
2018-08-26 02:30 | 123.79 | 107.87
2018-08-26 03:00 | 114.61 | 98.4
2018-08-26 03:30 | 123.17 | 107.69
2018-08-26 04:00 | 121.9 | 106.29
2018-08-26 04:30 | 125.9 | 110.17
2018-08-26 05:00 | 118.68 | 102.32
2018-08-26 05:30 | 125.32 | 109.13
2018-08-26 06:00 | 119.23 | 103.01
2018-08-26 06:30 | 120.5 | 104.73
2018-08-26 07:00 | 117.99 | 102.51
2018-08-26 07:30 | 127.59 | 112.47
2018-08-26 08:00 | 119.28 | 103.91
2018-08-26 08:30 | 126.04 | 110.1
2018-08-26 09:00 | 125.72 | 109.72
2018-08-26 09:30 | 125.58 | 108.03
2018-08-26 10:00 | 126.61 | 109.99
2018-08-26 10:30 | 120.28 | 103.3
2018-08-26 11:00 | 119.82 | 103.09
2018-08-26 11:30 | 122.83 | 106.24
2018-08-26 12:00 | 125.72 | 110.4
2018-08-26 12:30 | 126.09 | 110.19
2018-08-26 13:00 | 122.84 | 106.27
2018-08-26 13:30 | 127 | 110.42
2018-08-26 14:00 | 124.78 | 107.79
2018-08-26 14:30 | 124.76 | 108.18
2018-08-26 15:00 | 114.82 | 98.54
2018-08-26 15:30 | 120.94 | 104.38
2018-08-26 16:00 | 125.7 | 109.39
2018-08-26 16:30 | 121.2 | 104.71
2018-08-26 17:00 | 121.39 | 102.2
2018-08-26 17:30 | 121.82 | 101.25
2018-08-26 18:00 | 125.5 | 104.02
2018-08-26 18:30 | 122.26 | 100.41
2018-08-26 19:00 | 132.6 | 111.36
2018-08-26 19:30 | 139.69 | 119.09
2018-08-26 20:00 | 133.32 | 114.71
2018-08-26 20:30 | 136.83 | 118.59
2018-08-26 21:00 | 132.04 | 113.61
2018-08-26 21:30 | 131.6 | 114.52
2018-08-26 22:00 | 134.56 | 117.34
2018-08-26 22:30 | 129.5 | 112.66
2018-08-26 23:00 | 127.42 | 110.59
2018-08-26 23:30 | 130.08 | 113.25
2018-08-27 | 130.91 | 114.42
2018-08-27 00:30 | 134.2 | 117.27
2018-08-27 01:00 | 139.31 | 121.81
2018-08-27 01:30 | 137.48 | 120.42
2018-08-27 02:00 | 135.41 | 117.88
2018-08-27 02:30 | 131.29 | 113.62
2018-08-27 03:00 | 128.99 | 112.05
2018-08-27 03:30 | 129.66 | 113.41
2018-08-27 04:00 | 132.28 | 115.05
2018-08-27 04:30 | 136.66 | 119.58
2018-08-27 05:00 | 124.85 | 107.16
2018-08-27 05:30 | 126.73 | 109.52
2018-08-27 06:00 | 128 | 109.98
2018-08-27 06:30 | 129.83 | 110.36
2018-08-27 07:00 | 133.85 | 113.6
2018-08-27 07:30 | 128.41 | 108.34
2018-08-27 08:00 | 126.21 | 106.33
2018-08-27 08:30 | 127.2 | 106.2
2018-08-27 09:00 | 132.12 | 112.34
2018-08-27 09:30 | 127.66 | 108.45
2018-08-27 10:00 | 134.63 | 116.34
2018-08-27 10:30 | 124.13 | 106.83
2018-08-27 11:00 | 114.36 | 95.82
2018-08-27 11:30 | 120.65 | 99.89
2018-08-27 12:00 | 125.61 | 106.33
2018-08-27 12:30 | 130.57 | 111.78
2018-08-27 13:00 | 130.24 | 111.03
2018-08-27 13:30 | 128.33 | 107.9
2018-08-27 14:00 | 128.69 | 108.76
2018-08-27 14:30 | 126.39 | 107.54
2018-08-27 15:00 | 127.3 | 109.98
2018-08-27 15:30 | 127.88 | 110.04
2018-08-27 16:00 | 130.32 | 112.86
2018-08-27 16:30 | 133.85 | 115.1
2018-08-27 17:00 | 142.98 | 124.54
2018-08-27 17:30 | 134.11 | 113.76
2018-08-27 18:00 | 149.24 | 130.44
2018-08-27 18:30 | 146.49 | 126.21
2018-08-27 19:00 | 146.76 | 127.69
2018-08-27 19:30 | 148.05 | 129.77
2018-08-27 20:00 | 140.27 | 122.65
2018-08-27 20:30 | 139.26 | 121.89
2018-08-27 21:00 | 137.6 | 120.21
2018-08-27 21:30 | 145.19 | 127.09
2018-08-27 22:00 | 140.18 | 122.99
2018-08-27 22:30 | 139.08 | 121.78
2018-08-27 23:00 | 131.25 | 114.61
2018-08-27 23:30 | 133.12 | 117.03
2018-08-28 | 132.33 | 116.66
2018-08-28 00:30 | 130.54 | 113.9
2018-08-28 01:00 | 133.5 | 116.25
2018-08-28 01:30 | 130.15 | 114.1
2018-08-28 02:00 | 124.14 | 108.37
2018-08-28 02:30 | 125.04 | 109.21
2018-08-28 03:00 | 122.93 | 106.7
2018-08-28 03:30 | 121.44 | 105.65
2018-08-28 04:00 | 123.97 | 107.46
2018-08-28 04:30 | 116.86 | 99.92
2018-08-28 05:00 | 117.91 | 101.59
2018-08-28 05:30 | 123.26 | 106.76
2018-08-28 06:00 | 126.54 | 111.04
2018-08-28 06:30 | 119.93 | 104.29
2018-08-28 07:00 | 133 | 116.97
2018-08-28 07:30 | 126.06 | 108.76
2018-08-28 08:00 | 119.71 | 103.68
2018-08-28 08:30 | 122.48 | 107.46
2018-08-28 09:00 | 122.46 | 107.59
2018-08-28 09:30 | 124.62 | 109.91
2018-08-28 10:00 | 116.37 | 101.15
2018-08-28 10:30 | 122.61 | 107.24
2018-08-28 11:00 | 117.44 | 101.48
2018-08-28 11:30 | 112.12 | 96.77
2018-08-28 12:00 | 113.82 | 98.54
2018-08-28 12:30 | 116.79 | 100.63
2018-08-28 13:00 | 111.06 | 93.68
2018-08-28 13:30 | 113.16 | 96.06
2018-08-28 14:00 | 124.54 | 106.76
2018-08-28 14:30 | 131.24 | 113.08
2018-08-28 15:00 | 133.27 | 113.98
2018-08-28 15:30 | 129.57 | 111.84
2018-08-28 16:00 | 128.22 | 109.94
2018-08-28 16:30 | 131.94 | 115.01
2018-08-28 17:00 | 136.52 | 118.37
2018-08-28 17:30 | 140.1 | 122.61
2018-08-28 18:00 | 141.11 | 123.37
2018-08-28 18:30 | 134.74 | 115.56
2018-08-28 19:00 | 129.14 | 109.91
2018-08-28 19:30 | 127.76 | 108.85
2018-08-28 20:00 | 140.21 | 122.59
2018-08-28 20:30 | 147.07 | 130.22
2018-08-28 21:00 | 140.95 | 125.11
2018-08-28 21:30 | 141.13 | 125.13
2018-08-28 22:00 | 143.39 | 127.41
2018-08-28 22:30 | 139.02 | 122.33
2018-08-28 23:00 | 137.96 | 120.88
2018-08-28 23:30 | 133.44 | 116.24
2018-08-29 | 135.18 | 119.08
2018-08-29 00:30 | 141.23 | 125.51
2018-08-29 01:00 | 128.87 | 112.21
2018-08-29 01:30 | 126.39 | 109.72
2018-08-29 02:00 | 124.54 | 108.03
2018-08-29 02:30 | 117.73 | 100.73
2018-08-29 03:00 | 118.76 | 102.56
2018-08-29 03:30 | 125.94 | 110.77
2018-08-29 04:00 | 133.78 | 117.93
2018-08-29 04:30 | 124.52 | 108.41
2018-08-29 05:00 | 130.32 | 114.09
2018-08-29 05:30 | 134.84 | 117.93
2018-08-29 06:00 | 134.07 | 116.51
2018-08-29 06:30 | 124.69 | 105.83
2018-08-29 07:00 | 131.72 | 112.8
2018-08-29 07:30 | 136.51 | 119.14
2018-08-29 08:00 | 127.85 | 109.34
2018-08-29 08:30 | 122.9 | 102.85
2018-08-29 09:00 | 124.7 | 103.08
2018-08-29 09:30 | 121.01 | 99.99
2018-08-29 10:00 | 123.43 | 103.75
2018-08-29 10:30 | 124.05 | 105.73
2018-08-29 11:00 | 117.97 | 99.81
2018-08-29 11:30 | 132.45 | 114.25
2018-08-29 12:00 | 130.19 | 111.41
2018-08-29 12:30 | 129.57 | 109.87
2018-08-29 13:00 | 126.86 | 106.43
2018-08-29 13:30 | 122.17 | 100.62
2018-08-29 14:00 | 125.98 | 105.21
2018-08-29 14:30 | 126.96 | 106.63
2018-08-29 15:00 | 125.81 | 105.22
2018-08-29 15:30 | 127.53 | 106.64
2018-08-29 16:00 | 123.23 | 101.87
2018-08-29 16:30 | 116.88 | 93.89
2018-08-29 17:00 | 117.16 | 93.84
2018-08-29 17:30 | 116.46 | 96.52
2018-08-29 18:00 | 121.09 | 99.52
2018-08-29 18:30 | 122.9 | 99.55
2018-08-29 19:00 | 130.55 | 108.55
2018-08-29 19:30 | 136.53 | 115.06
2018-08-29 20:00 | 137.33 | 116.11
2018-08-29 20:30 | 137.8 | 117.91
2018-08-29 21:00 | 129.68 | 110.53
2018-08-29 21:30 | 131.56 | 112.11
2018-08-29 22:00 | 133.68 | 115.03
2018-08-29 22:30 | 134.64 | 115.48
2018-08-29 23:00 | 126.92 | 107.87
2018-08-29 23:30 | 123.04 | 103.97
2018-08-30 | 120.53 | 102.39
2018-08-30 00:30 | 129.35 | 111.42
2018-08-30 01:00 | 125.06 | 107.25
2018-08-30 01:30 | 117.88 | 99.09
2018-08-30 02:00 | 114.35 | 96.16
2018-08-30 02:30 | 123.84 | 106.2
2018-08-30 03:00 | 120.48 | 103.06
2018-08-30 03:30 | 122.78 | 105.13
2018-08-30 04:00 | 119.11 | 100.99
2018-08-30 04:30 | 119.73 | 102.6
2018-08-30 05:00 | 120.46 | 102.09
2018-08-30 05:30 | 117.31 | 98.47
2018-08-30 06:00 | 119.01 | 101.23
2018-08-30 06:30 | 122.63 | 104.29
2018-08-30 07:00 | 132.16 | 113.35
2018-08-30 07:30 | 126.52 | 107.79
2018-08-30 08:00 | 123.26 | 104.67
2018-08-30 08:30 | 126.35 | 108.08
2018-08-30 09:00 | 123.13 | 105.26
2018-08-30 09:30 | 120.13 | 102.31
2018-08-30 10:00 | 117.11 | 98.82
2018-08-30 10:30 | 124.62 | 106.92
2018-08-30 11:00 | 124.82 | 107.53
2018-08-30 11:30 | 119.39 | 101.42
2018-08-30 12:00 | 117.38 | 98.76
2018-08-30 12:30 | 118 | 98.96
2018-08-30 13:00 | 123.53 | 105.15
2018-08-30 13:30 | 128.37 | 110.83
2018-08-30 14:00 | 129.66 | 112
2018-08-30 14:30 | 127.12 | 107.77
2018-08-30 15:00 | 126.38 | 105.27
2018-08-30 15:30 | 122.24 | 100.64
2018-08-30 16:00 | 126.03 | 103.91
2018-08-30 16:30 | 131.42 | 110.01
2018-08-30 17:00 | 140.76 | 119.58
2018-08-30 17:30 | 144.7 | 123.1
2018-08-30 18:00 | 141.98 | 118.42
2018-08-30 18:30 | 143.15 | 119.85
2018-08-30 19:00 | 151.68 | 129.94
2018-08-30 19:30 | 142.13 | 119.79
2018-08-30 20:00 | 147.19 | 124.04
2018-08-30 20:30 | 145.58 | 124.37
2018-08-30 21:00 | 141.16 | 119.48
2018-08-30 21:30 | 143.51 | 122.62
2018-08-30 22:00 | 140.82 | 120.35
2018-08-30 22:30 | 144.74 | 124.37
2018-08-30 23:00 | 135.73 | 116.5
2018-08-30 23:30 | 135.69 | 116.58
2018-08-31 | 133.57 | 114.5
2018-08-31 00:30 | 125.81 | 106.5
2018-08-31 01:00 | 130 | 110.41
2018-08-31 01:30 | 131.02 | 111.15
2018-08-31 02:00 | 133.32 | 113.12
2018-08-31 02:30 | 131.05 | 110.41
2018-08-31 03:00 | 135.93 | 115.32
2018-08-31 03:30 | 129.49 | 110.11
2018-08-31 04:00 | 130.19 | 111.18
2018-08-31 04:30 | 130.96 | 111.86
2018-08-31 05:00 | 134.14 | 113.95
2018-08-31 05:30 | 135.48 | 115.82
2018-08-31 06:00 | 131.19 | 112.01
2018-08-31 06:30 | 124.84 | 105.11
2018-08-31 07:00 | 134.8 | 115.92
2018-08-31 07:30 | 144.87 | 126.02
2018-08-31 08:00 | 141.98 | 123.88
2018-08-31 08:30 | 130.45 | 110.96
2018-08-31 09:00 | 119.57 | 98.19
2018-08-31 09:30 | 112.83 | 92.1
2018-08-31 10:00 | 118.77 | 98.27
2018-08-31 10:30 | 120.66 | 100.39
2018-08-31 11:00 | 117.85 | 98.93
2018-08-31 11:30 | 120.53 | 101.04
2018-08-31 12:00 | 114.26 | 94.79
2018-08-31 12:30 | 101.91 | 82.47
2018-08-31 13:00 | 104.44 | 85.58
2018-08-31 13:30 | 111.37 | 92.13
2018-08-31 14:00 | 108.8 | 88.74
2018-08-31 14:30 | 121.57 | 102.76
2018-08-31 15:00 | 112.12 | 93.31
2018-08-31 15:30 | 110.15 | 90.54
2018-08-31 16:00 | 114.22 | 93.97
2018-08-31 16:30 | 110.88 | 90.28
2018-08-31 17:00 | 115.55 | 95.03
2018-08-31 17:30 | 113.33 | 93.21
2018-08-31 18:00 | 111.37 | 90.1
2018-08-31 18:30 | 117.63 | 96.72
2018-08-31 19:00 | 114.07 | 92.56
2018-08-31 19:30 | 119.98 | 98.95
2018-08-31 20:00 | 120.43 | 100.57
2018-08-31 20:30 | 116.92 | 97.65
2018-08-31 21:00 | 128.62 | 110.13
2018-08-31 21:30 | 128.59 | 109.14
2018-08-31 22:00 | 126.37 | 106.31
2018-08-31 22:30 | 128.97 | 108.24
2018-08-31 23:00 | 129.85 | 109.15
2018-08-31 23:30 | 131.88 | 112.47
2018-09-01 | 132.37 | 114.66
2018-09-01 00:30 | 133.03 | 115.46
2018-09-01 01:00 | 130.07 | 110.67
2018-09-01 01:30 | 129.45 | 109.85
2018-09-01 02:00 | 127.88 | 107.89
2018-09-01 02:30 | 127.39 | 107.36
2018-09-01 03:00 | 123.09 | 103.18
2018-09-01 03:30 | 126.96 | 108.99
2018-09-01 04:00 | 121.54 | 103.48
2018-09-01 04:30 | 122.58 | 103.68
2018-09-01 05:00 | 121.45 | 103.3
2018-09-01 05:30 | 125.69 | 107.82
2018-09-01 06:00 | 122.65 | 105.41
2018-09-01 06:30 | 117.35 | 100.06
2018-09-01 07:00 | 125.32 | 108.72
2018-09-01 07:30 | 121.75 | 105.31
2018-09-01 08:00 | 117.15 | 99.64
2018-09-01 08:30 | 112.21 | 94.2
2018-09-01 09:00 | 111.72 | 93.11
2018-09-01 09:30 | 114.58 | 96.49
2018-09-01 10:00 | 112.48 | 94.81
2018-09-01 10:30 | 117.02 | 98.41
2018-09-01 11:00 | 115.48 | 97.73
2018-09-01 11:30 | 120.99 | 103.51
2018-09-01 12:00 | 119.56 | 101.75
2018-09-01 12:30 | 120.88 | 102.26
2018-09-01 13:00 | 124.37 | 105.64
2018-09-01 13:30 | 130.3 | 112.56
2018-09-01 14:00 | 124.33 | 104.82
2018-09-01 14:30 | 128.45 | 107.84
2018-09-01 15:00 | 127.71 | 107.35
2018-09-01 15:30 | 122.52 | 101.6
2018-09-01 16:00 | 134.1 | 114.8
2018-09-01 16:30 | 129.48 | 110.55
2018-09-01 17:00 | 133.45 | 114.03
2018-09-01 17:30 | 129.4 | 109.32
2018-09-01 18:00 | 137.51 | 118.57
2018-09-01 18:30 | 131.08 | 110.88
2018-09-01 19:00 | 134.55 | 114.02
2018-09-01 19:30 | 132.61 | 111.65
2018-09-01 20:00 | 139.77 | 117.71
2018-09-01 20:30 | 134.19 | 112.8
2018-09-01 21:00 | 132.97 | 112.39
2018-09-01 21:30 | 125.23 | 105.26
2018-09-01 22:00 | 125.94 | 106.72
2018-09-01 22:30 | 133.4 | 114.52
2018-09-01 23:00 | 127.41 | 109.71
2018-09-01 23:30 | 121.43 | 104.77
2018-09-02 | 120.15 | 102.74
2018-09-02 00:30 | 121.35 | 103.78
2018-09-02 01:00 | 128.76 | 112
2018-09-02 01:30 | 127.97 | 110.85
2018-09-02 02:00 | 124.39 | 107.18
2018-09-02 02:30 | 125.39 | 108.39
2018-09-02 03:00 | 119.36 | 102.6
2018-09-02 03:30 | 116.42 | 99.13
2018-09-02 04:00 | 120.64 | 103.38
2018-09-02 04:30 | 121.31 | 105.16
2018-09-02 05:00 | 121.24 | 105.04
2018-09-02 05:30 | 128.92 | 112.44
2018-09-02 06:00 | 116.81 | 99.71
2018-09-02 06:30 | 113.29 | 95.99
2018-09-02 07:00 | 103.88 | 85.96
2018-09-02 07:30 | 120.17 | 103.39
2018-09-02 08:00 | 118.03 | 101.59
2018-09-02 08:30 | 117.76 | 100.96
2018-09-02 09:00 | 118.09 | 101.84
2018-09-02 09:30 | 122.32 | 105.92
2018-09-02 10:00 | 121.3 | 104.93
2018-09-02 10:30 | 121.56 | 105.15
2018-09-02 11:00 | 117.36 | 101.14
2018-09-02 11:30 | 114.22 | 96.68
2018-09-02 12:00 | 118.5 | 100.92
2018-09-02 12:30 | 120.41 | 101.81
2018-09-02 13:00 | 123.16 | 105.96
2018-09-02 13:30 | 127.7 | 110.08
2018-09-02 14:00 | 126.55 | 107.73
2018-09-02 14:30 | 131.45 | 113.72
2018-09-02 15:00 | 125.06 | 107.98
2018-09-02 15:30 | 127.28 | 110.01
2018-09-02 16:00 | 131.24 | 113.62
2018-09-02 16:30 | 135.19 | 116.98
2018-09-02 17:00 | 132.45 | 113.84
2018-09-02 17:30 | 133.71 | 114.99
2018-09-02 18:00 | 136.86 | 117.71
2018-09-02 18:30 | 122.64 | 102.8
2018-09-02 19:00 | 130.51 | 111.45
2018-09-02 19:30 | 134.11 | 115.08
2018-09-02 20:00 | 133.41 | 114.82
2018-09-02 20:30 | 134.71 | 117.05
2018-09-02 21:00 | 131.24 | 113.84
2018-09-02 21:30 | 126.66 | 108.94
2018-09-02 22:00 | 130.11 | 113.14
2018-09-02 22:30 | 124.38 | 107.07
2018-09-02 23:00 | 128.74 | 111.03
2018-09-02 23:30 | 126 | 107.98
2018-09-03 | 125.65 | 107.85
2018-09-03 00:30 | 131.96 | 114.16
2018-09-03 01:00 | 129.27 | 111.45
2018-09-03 01:30 | 124.89 | 107.47
2018-09-03 02:00 | 124.64 | 107.46
2018-09-03 02:30 | 127.87 | 110.39
2018-09-03 03:00 | 125.75 | 108.5
2018-09-03 03:30 | 121.78 | 104.33
2018-09-03 04:00 | 123.15 | 106.12
2018-09-03 04:30 | 127.1 | 110.74
2018-09-03 05:00 | 122.41 | 105.49
2018-09-03 05:30 | 126.92 | 109.49
2018-09-03 06:00 | 123.71 | 106.29
2018-09-03 06:30 | 108.35 | 89.75
2018-09-03 07:00 | 115.35 | 96.31
2018-09-03 07:30 | 122.17 | 104.2
2018-09-03 08:00 | 115.82 | 97.8
2018-09-03 08:30 | 116.77 | 99.71
2018-09-03 09:00 | 114.87 | 98.68
2018-09-03 09:30 | 115.72 | 98.98
2018-09-03 10:00 | 114.92 | 97.93
2018-09-03 10:30 | 111.58 | 94.55
2018-09-03 11:00 | 113.99 | 97.14
2018-09-03 11:30 | 115.6 | 97.78
2018-09-03 12:00 | 114.45 | 96.29
2018-09-03 12:30 | 118.71 | 100.44
2018-09-03 13:00 | 111.48 | 93.64
2018-09-03 13:30 | 108.33 | 90.06
2018-09-03 14:00 | 109.55 | 91.55
2018-09-03 14:30 | 113 | 93.72
2018-09-03 15:00 | 112.35 | 90.96
2018-09-03 15:30 | 115.39 | 96.05
2018-09-03 16:00 | 115.32 | 95.81
2018-09-03 16:30 | 121.67 | 101.93
2018-09-03 17:00 | 123.92 | 104.41
2018-09-03 17:30 | 127.87 | 109.23
2018-09-03 18:00 | 124.15 | 105.68
2018-09-03 18:30 | 121.93 | 102.76
2018-09-03 19:00 | 135.73 | 117.23
2018-09-03 19:30 | 129.41 | 110.97
2018-09-03 20:00 | 135.18 | 117.32
2018-09-03 20:30 | 130.08 | 110.99
2018-09-03 21:00 | 119.78 | 99.49
2018-09-03 21:30 | 123.43 | 104.28
2018-09-03 22:00 | 121.82 | 104.01
2018-09-03 22:30 | 115.59 | 97.4
2018-09-03 23:00 | 118.59 | 101.06
2018-09-03 23:30 | 117.2 | 99.65
2018-09-04 | 120.56 | 103.4
2018-09-04 00:30 | 130.01 | 113.04
2018-09-04 01:00 | 122.17 | 105.16
2018-09-04 01:30 | 113.95 | 97.23
2018-09-04 02:00 | 113.89 | 97.05
2018-09-04 02:30 | 115.06 | 98.35
2018-09-04 03:00 | 118.95 | 103.25
2018-09-04 03:30 | 105.46 | 90.54
2018-09-04 04:00 | 115.93 | 100.02
2018-09-04 04:30 | 125.44 | 110.67
2018-09-04 05:00 | 114.31 | 98.33
2018-09-04 05:30 | 122.78 | 107.16
2018-09-04 06:00 | 120.8 | 104.55
2018-09-04 06:30 | 113.9 | 97.44
2018-09-04 07:00 | 122.34 | 106.82
2018-09-04 07:30 | 131.22 | 115.17
2018-09-04 08:00 | 122.86 | 106.57
2018-09-04 08:30 | 122.19 | 104.38
2018-09-04 09:00 | 123.09 | 105.54
2018-09-04 09:30 | 119.62 | 102.4
2018-09-04 10:00 | 123.65 | 107.37
2018-09-04 10:30 | 122.07 | 105.73
2018-09-04 11:00 | 119.83 | 101.85
2018-09-04 11:30 | 119.32 | 101.89
2018-09-04 12:00 | 120.06 | 102.27
2018-09-04 12:30 | 122.13 | 103.97
2018-09-04 13:00 | 118.85 | 100.13
2018-09-04 13:30 | 115.36 | 96.25
2018-09-04 14:00 | 124.98 | 105.96
2018-09-04 14:30 | 117.79 | 98.01
2018-09-04 15:00 | 122.23 | 103.67
2018-09-04 15:30 | 127.68 | 109.17
2018-09-04 16:00 | 129.55 | 110.87
2018-09-04 16:30 | 130.29 | 110.67
2018-09-04 17:00 | 134.93 | 115.29
2018-09-04 17:30 | 130.55 | 111.24
2018-09-04 18:00 | 141.63 | 123.22
2018-09-04 18:30 | 132.61 | 112.67
2018-09-04 19:00 | 125.21 | 107.41
2018-09-04 19:30 | 121.62 | 105.11
2018-09-04 20:00 | 122.84 | 106.28
2018-09-04 20:30 | 117.71 | 100.18
2018-09-04 21:00 | 113.82 | 97.33
2018-09-04 21:30 | 116.12 | 100.47
2018-09-04 22:00 | 107.87 | 90.87
2018-09-04 22:30 | 106.08 | 88.8
2018-09-04 23:00 | 103.45 | 85.31
2018-09-04 23:30 | 105.85 | 88.56
2018-09-05 | 105.81 | 88.38
2018-09-05 00:30 | 110.55 | 93.14
2018-09-05 01:00 | 106.5 | 89.59
2018-09-05 01:30 | 104.44 | 87.49
2018-09-05 02:00 | 104.14 | 86.92
2018-09-05 02:30 | 107.19 | 90.51
2018-09-05 03:00 | 101.61 | 83.15
2018-09-05 03:30 | 99.82 | 81.36
2018-09-05 04:00 | 96.18 | 77.27
2018-09-05 04:30 | 101.92 | 83.63
2018-09-05 05:00 | 105.44 | 87.68
2018-09-05 05:30 | 105.84 | 88.65
2018-09-05 06:00 | 103.77 | 86.92
2018-09-05 06:30 | 94.04 | 76.87
2018-09-05 07:00 | 104.76 | 88.39
2018-09-05 07:30 | 105.88 | 89.08
2018-09-05 08:00 | 101.26 | 84.23
2018-09-05 08:30 | 100.6 | 84.19
2018-09-05 09:00 | 106.26 | 89.31
2018-09-05 09:30 | 100.72 | 83.42
2018-09-05 10:00 | 97.76 | 79.93
2018-09-05 10:30 | 102.96 | 86.22
2018-09-05 11:00 | 100.44 | 83.51
2018-09-05 11:30 | 100.57 | 83.78
2018-09-05 12:00 | 102.19 | 84.91
2018-09-05 12:30 | 104.62 | 88.36
2018-09-05 13:00 | 109.07 | 92.36
2018-09-05 13:30 | 100.35 | 82.42
2018-09-05 14:00 | 106.35 | 89.22
2018-09-05 14:30 | 103.52 | 85.41
2018-09-05 15:00 | 102.05 | 83.41
2018-09-05 15:30 | 102.35 | 83.25
2018-09-05 16:00 | 106.47 | 87.46
2018-09-05 16:30 | 112.89 | 94.93
2018-09-05 17:00 | 107.77 | 88.69
2018-09-05 17:30 | 114.57 | 96.85
2018-09-05 18:00 | 109.8 | 92.04
2018-09-05 18:30 | 112.01 | 94.7
2018-09-05 19:00 | 111.83 | 93.79
2018-09-05 19:30 | 116.08 | 99.07
2018-09-05 20:00 | 127.05 | 109.63
2018-09-05 20:30 | 122.01 | 104.35
2018-09-05 21:00 | 121.43 | 103.79
2018-09-05 21:30 | 117.23 | 98.88
2018-09-05 22:00 | 119.59 | 100.91
2018-09-05 22:30 | 115.23 | 96.25
2018-09-05 23:00 | 117.28 | 98.88
2018-09-05 23:30 | 113.56 | 96.55
2018-09-06 | 112.47 | 95.86
2018-09-06 00:30 | 118.8 | 102.99
2018-09-06 01:00 | 122.52 | 106.4
2018-09-06 01:30 | 123.82 | 107.3
2018-09-06 02:00 | 122.53 | 105.64
2018-09-06 02:30 | 124.74 | 107.44
2018-09-06 03:00 | 119.7 | 101.6
2018-09-06 03:30 | 120.54 | 103.19
2018-09-06 04:00 | 118.53 | 101.76
2018-09-06 04:30 | 119.05 | 102.09
2018-09-06 05:00 | 120.6 | 102.85
2018-09-06 05:30 | 123.5 | 105.89
2018-09-06 06:00 | 118.78 | 101.74
2018-09-06 06:30 | 117.58 | 100.58
2018-09-06 07:00 | 122.43 | 104.84
2018-09-06 07:30 | 122.99 | 104.72
2018-09-06 08:00 | 116.74 | 98.26
2018-09-06 08:30 | 113.03 | 93.75
2018-09-06 09:00 | 115.11 | 95.71
2018-09-06 09:30 | 113.43 | 92.55
2018-09-06 10:00 | 118.68 | 97.9
2018-09-06 10:30 | 114.28 | 93.39
2018-09-06 11:00 | 118.21 | 97
2018-09-06 11:30 | 118.34 | 97.23
2018-09-06 12:00 | 121.08 | 98.7
2018-09-06 12:30 | 127.2 | 104.99
2018-09-06 13:00 | 129.57 | 109.48
2018-09-06 13:30 | 125.62 | 106.08
2018-09-06 14:00 | 125.42 | 105.43
2018-09-06 14:30 | 120.68 | 100.71
2018-09-06 15:00 | 126.92 | 106.19
2018-09-06 15:30 | 128.72 | 108.25
2018-09-06 16:00 | 120.9 | 100.2
2018-09-06 16:30 | 125.42 | 106.94
2018-09-06 17:00 | 130.85 | 112.59
2018-09-06 17:30 | 129.69 | 110.55
2018-09-06 18:00 | 133.49 | 114.6
2018-09-06 18:30 | 136.48 | 115.91
2018-09-06 19:00 | 147.42 | 127.3
2018-09-06 19:30 | 144.34 | 123.79
2018-09-06 20:00 | 143.79 | 123.91
2018-09-06 20:30 | 142.56 | 123.09
2018-09-06 21:00 | 142.19 | 123.53
2018-09-06 21:30 | 136.96 | 117.9
2018-09-06 22:00 | 135.46 | 116.58
2018-09-06 22:30 | 130.69 | 111.27
2018-09-06 23:00 | 132.38 | 113.09
2018-09-06 23:30 | 133.65 | 115.56
2018-09-07 | 128.71 | 110.35
2018-09-07 00:30 | 130.23 | 113.05
2018-09-07 01:00 | 128.45 | 111.77
2018-09-07 01:30 | 125.04 | 107.69
2018-09-07 02:00 | 127.76 | 110.68
2018-09-07 02:30 | 136.56 | 119.38
2018-09-07 03:00 | 132.24 | 115.01
2018-09-07 03:30 | 127.81 | 111.22
2018-09-07 04:00 | 128.95 | 112.49
2018-09-07 04:30 | 129.5 | 112.93
2018-09-07 05:00 | 125.36 | 108.29
2018-09-07 05:30 | 127.59 | 111.4
2018-09-07 06:00 | 126.68 | 110.47
2018-09-07 06:30 | 119.95 | 103.28
2018-09-07 07:00 | 125.38 | 108.78
2018-09-07 07:30 | 133.19 | 117.62
2018-09-07 08:00 | 116.49 | 100.08
2018-09-07 08:30 | 123.34 | 106.53
2018-09-07 09:00 | 130.25 | 112.65
2018-09-07 09:30 | 134.3 | 114.9
2018-09-07 10:00 | 130.99 | 110.89
2018-09-07 10:30 | 133.71 | 114.03
2018-09-07 11:00 | 129.95 | 109.85
2018-09-07 11:30 | 131.25 | 112.37
2018-09-07 12:00 | 128.07 | 108.67
2018-09-07 12:30 | 126.86 | 107.55
2018-09-07 13:00 | 137.64 | 117.65
2018-09-07 13:30 | 143.63 | 123.21
2018-09-07 14:00 | 143.66 | 122.93
2018-09-07 14:30 | 140.24 | 118.83
2018-09-07 15:00 | 140.79 | 117.89
2018-09-07 15:30 | 130.57 | 108.49
2018-09-07 16:00 | 138.9 | 117.62
2018-09-07 16:30 | 136.75 | 115.31
2018-09-07 17:00 | 137.87 | 118.05
2018-09-07 17:30 | 144.12 | 124.28
2018-09-07 18:00 | 140.88 | 120.7
2018-09-07 18:30 | 138.77 | 116.8
2018-09-07 19:00 | 143.24 | 119.74
2018-09-07 19:30 | 150.58 | 127.76
2018-09-07 20:00 | 147.78 | 126.19
2018-09-07 20:30 | 143.09 | 120.8
2018-09-07 21:00 | 144.56 | 123.44
2018-09-07 21:30 | 133.4 | 113.54
2018-09-07 22:00 | 134.35 | 114.43
2018-09-07 22:30 | 128.33 | 108.73
2018-09-07 23:00 | 129.22 | 109.99
2018-09-07 23:30 | 124.62 | 106.67
2018-09-08 | 127.84 | 110.1
2018-09-08 00:30 | 136.01 | 118.05
2018-09-08 01:00 | 126.43 | 108.14
2018-09-08 01:30 | 125.76 | 107.68
2018-09-08 02:00 | 126.49 | 108.36
2018-09-08 02:30 | 126.87 | 108.77
2018-09-08 03:00 | 129.42 | 111.19
2018-09-08 03:30 | 132.81 | 114.73
2018-09-08 04:00 | 135.78 | 118.08
2018-09-08 04:30 | 134.08 | 115.78
2018-09-08 05:00 | 138.01 | 119.72
2018-09-08 05:30 | 135.76 | 117.48
2018-09-08 06:00 | 129.62 | 111.33
2018-09-08 06:30 | 121.33 | 103.56
2018-09-08 07:00 | 120.3 | 102.25
2018-09-08 07:30 | 120.85 | 104.09
2018-09-08 08:00 | 115.85 | 98.82
2018-09-08 08:30 | 111.6 | 94.38
2018-09-08 09:00 | 115.93 | 98.58
2018-09-08 09:30 | 121.51 | 103.64
2018-09-08 10:00 | 123.66 | 105.94
2018-09-08 10:30 | 127.61 | 109.37
2018-09-08 11:00 | 124.03 | 106.23
2018-09-08 11:30 | 124.37 | 106.34
2018-09-08 12:00 | 127.96 | 109.97
2018-09-08 12:30 | 123.75 | 105.81
2018-09-08 13:00 | 123.75 | 104.85
2018-09-08 13:30 | 121.79 | 102.55
2018-09-08 14:00 | 127.13 | 108.37
2018-09-08 14:30 | 127.47 | 109.1
2018-09-08 15:00 | 123.03 | 104.62
2018-09-08 15:30 | 125.61 | 107.04
2018-09-08 16:00 | 125.24 | 104.95
2018-09-08 16:30 | 126.64 | 105.52
2018-09-08 17:00 | 128.56 | 107.02
2018-09-08 17:30 | 133.03 | 110.97
2018-09-08 18:00 | 137.29 | 116.51
2018-09-08 18:30 | 131.01 | 109.09
2018-09-08 19:00 | 140.2 | 119.9
2018-09-08 19:30 | 143.83 | 123.82
2018-09-08 20:00 | 135.18 | 113.59
2018-09-08 20:30 | 140.87 | 120.04
2018-09-08 21:00 | 137.9 | 117.01
2018-09-08 21:30 | 133.91 | 115.18
2018-09-08 22:00 | 133.92 | 114.59
2018-09-08 22:30 | 131.53 | 111.84
2018-09-08 23:00 | 131.31 | 112.74
2018-09-08 23:30 | 123.15 | 104.88
2018-09-09 | 126.75 | 108.37
2018-09-09 00:30 | 128.57 | 110.46
2018-09-09 01:00 | 121.04 | 103.43
2018-09-09 01:30 | 116.9 | 99.87
2018-09-09 02:00 | 118.29 | 100.98
2018-09-09 02:30 | 121.89 | 103.84
2018-09-09 03:00 | 122.74 | 104.57
2018-09-09 03:30 | 120.25 | 101.7
2018-09-09 04:00 | 123.11 | 104.41
2018-09-09 04:30 | 119.57 | 100.47
2018-09-09 05:00 | 117.25 | 97.8
2018-09-09 05:30 | 126.52 | 107.76
2018-09-09 06:00 | 124.22 | 106.66
2018-09-09 06:30 | 118.67 | 100.02
2018-09-09 07:00 | 119.96 | 101.84
2018-09-09 07:30 | 122.04 | 103.84
2018-09-09 08:00 | 116.62 | 98.88
2018-09-09 08:30 | 119.42 | 103.01
2018-09-09 09:00 | 114.88 | 98.07
2018-09-09 09:30 | 113.93 | 96.54
2018-09-09 10:00 | 113.05 | 95.52
2018-09-09 10:30 | 111.57 | 93.76
2018-09-09 11:00 | 110.27 | 93.23
2018-09-09 11:30 | 113.43 | 95.44
2018-09-09 12:00 | 115.96 | 97.86
2018-09-09 12:30 | 114.95 | 96.01
2018-09-09 13:00 | 111.69 | 93.36
2018-09-09 13:30 | 109.25 | 90.54
2018-09-09 14:00 | 112.75 | 94.1
2018-09-09 14:30 | 120.87 | 102.4
2018-09-09 15:00 | 120.76 | 102.6
2018-09-09 15:30 | 116.08 | 98.04
2018-09-09 16:00 | 123.65 | 105.79
2018-09-09 16:30 | 118.97 | 101.44
2018-09-09 17:00 | 132.58 | 114.39
2018-09-09 17:30 | 129.56 | 111.17
2018-09-09 18:00 | 135.07 | 115.06
2018-09-09 18:30 | 132.85 | 112.62
2018-09-09 19:00 | 138.98 | 119.58
2018-09-09 19:30 | 136.45 | 116.48
2018-09-09 20:00 | 141.27 | 122.03
2018-09-09 20:30 | 140.88 | 121.61
2018-09-09 21:00 | 138.98 | 120.27
2018-09-09 21:30 | 130.97 | 112.24
2018-09-09 22:00 | 133.09 | 114.81
2018-09-09 22:30 | 133.51 | 115.67
2018-09-09 23:00 | 136.78 | 118.69
2018-09-09 23:30 | 128.98 | 111.08
2018-09-10 | 124.25 | 106.27
2018-09-10 00:30 | 121.33 | 103.19
2018-09-10 01:00 | 129.12 | 110.88
2018-09-10 01:30 | 128.44 | 110.32
2018-09-10 02:00 | 124.6 | 106.83
2018-09-10 02:30 | 125.61 | 107.84
2018-09-10 03:00 | 122.14 | 104.54
2018-09-10 03:30 | 124.68 | 107.06
2018-09-10 04:00 | 120.47 | 103.13
2018-09-10 04:30 | 121.12 | 102.95
2018-09-10 05:00 | 124.03 | 105.47
2018-09-10 05:30 | 119.35 | 100.08
2018-09-10 06:00 | 120.1 | 101.16
2018-09-10 06:30 | 117.55 | 97.33
2018-09-10 07:00 | 119.91 | 101.07
2018-09-10 07:30 | 122.28 | 104.76
2018-09-10 08:00 | 122.28 | 105.33
2018-09-10 08:30 | 114.68 | 97.36
2018-09-10 09:00 | 120.36 | 102.89
2018-09-10 09:30 | 115.21 | 97.22
2018-09-10 10:00 | 119.23 | 101.48
2018-09-10 10:30 | 116.42 | 98.66
2018-09-10 11:00 | 115.6 | 97.31
2018-09-10 11:30 | 116.29 | 97.6
2018-09-10 12:00 | 121.07 | 103
2018-09-10 12:30 | 117.61 | 99.62
2018-09-10 13:00 | 113.37 | 93.94
2018-09-10 13:30 | 114.09 | 95.55
2018-09-10 14:00 | 115.1 | 96.01
2018-09-10 14:30 | 117.87 | 100.01
2018-09-10 15:00 | 111.59 | 95.03
2018-09-10 15:30 | 106.7 | 89.45
2018-09-10 16:00 | 116.01 | 98.15
2018-09-10 16:30 | 115.19 | 97.1
2018-09-10 17:00 | 118.28 | 100.58
2018-09-10 17:30 | 124.55 | 105.61
2018-09-10 18:00 | 122.3 | 104.3
2018-09-10 18:30 | 124.37 | 105.91
2018-09-10 19:00 | 127.75 | 108.94
2018-09-10 19:30 | 135.66 | 116.47
2018-09-10 20:00 | 138.07 | 119.11
2018-09-10 20:30 | 130.74 | 112.73
2018-09-10 21:00 | 135.14 | 116.33
2018-09-10 21:30 | 127.44 | 109
2018-09-10 22:00 | 131.68 | 113.57
2018-09-10 22:30 | 128.55 | 112.07
2018-09-10 23:00 | 119.68 | 103.69
2018-09-10 23:30 | 128.03 | 112.77
2018-09-11 | 131.41 | 116.26
2018-09-11 00:30 | 124.41 | 109.21
2018-09-11 01:00 | 121.67 | 105.97
2018-09-11 01:30 | 120.95 | 105.78
2018-09-11 02:00 | 118.85 | 103.62
2018-09-11 02:30 | 122.54 | 107.61
2018-09-11 03:00 | 123.61 | 109.03
2018-09-11 03:30 | 124.47 | 109.78
2018-09-11 04:00 | 127.47 | 112.85
2018-09-11 04:30 | 117.73 | 102.16
2018-09-11 05:00 | 123.83 | 108.61
2018-09-11 05:30 | 125.56 | 110.02
2018-09-11 06:00 | 120.5 | 104.44
2018-09-11 06:30 | 121.68 | 106.05
2018-09-11 07:00 | 116.91 | 102.2
2018-09-11 07:30 | 119.94 | 105.87
2018-09-11 08:00 | 117.46 | 102.77
2018-09-11 08:30 | 106.85 | 92.11
2018-09-11 09:00 | 107.27 | 92.99
2018-09-11 09:30 | 98.86 | 84.74
2018-09-11 10:00 | 101.98 | 88.35
2018-09-11 10:30 | 108.11 | 93.91
2018-09-11 11:00 | 100.63 | 84.75
2018-09-11 11:30 | 109.59 | 95.32
2018-09-11 12:00 | 102.21 | 86.89
2018-09-11 12:30 | 104.41 | 88.6
2018-09-11 13:00 | 96.96 | 80.36
2018-09-11 13:30 | 97.51 | 81.25
2018-09-11 14:00 | 97.24 | 80.97
2018-09-11 14:30 | 98.1 | 81.64
2018-09-11 15:00 | 107.53 | 91.32
2018-09-11 15:30 | 108.7 | 92.61
2018-09-11 16:00 | 113.5 | 96.79
2018-09-11 16:30 | 115.1 | 97.96
2018-09-11 17:00 | 116.69 | 98.7
2018-09-11 17:30 | 115.67 | 98.89
2018-09-11 18:00 | 111.95 | 94.61
2018-09-11 18:30 | 112.07 | 94.7
2018-09-11 19:00 | 120.3 | 103.02
2018-09-11 19:30 | 124.59 | 107.21
2018-09-11 20:00 | 127.52 | 110.04
2018-09-11 20:30 | 131.22 | 113.94
2018-09-11 21:00 | 129.77 | 112.22
2018-09-11 21:30 | 123.96 | 105.72
2018-09-11 22:00 | 118.98 | 100.26
2018-09-11 22:30 | 113.48 | 94.75
2018-09-11 23:00 | 117.39 | 100.09
2018-09-11 23:30 | 114.74 | 97.48
2018-09-12 | 116.9 | 99.94
2018-09-12 00:30 | 116.81 | 100.12
2018-09-12 01:00 | 119.96 | 102.95
2018-09-12 01:30 | 119.13 | 101.85
2018-09-12 02:00 | 118.93 | 102.62
2018-09-12 02:30 | 115.29 | 99.16
2018-09-12 03:00 | 118.94 | 104.17
2018-09-12 03:30 | 115.11 | 99.5
2018-09-12 04:00 | 121.2 | 106.51
2018-09-12 04:30 | 119.92 | 105.05
2018-09-12 05:00 | 117.5 | 102.91
2018-09-12 05:30 | 120.24 | 105.59
2018-09-12 06:00 | 116.39 | 101.56
2018-09-12 06:30 | 111.07 | 95.2
2018-09-12 07:00 | 116.98 | 100.66
2018-09-12 07:30 | 114.8 | 98.06
2018-09-12 08:00 | 111.69 | 95.72
2018-09-12 08:30 | 110.34 | 93.1
2018-09-12 09:00 | 98.83 | 81.16
2018-09-12 09:30 | 103.85 | 87.58
2018-09-12 10:00 | 106.38 | 90.34
2018-09-12 10:30 | 106.71 | 89.75
2018-09-12 11:00 | 104.46 | 87.62
2018-09-12 11:30 | 97.28 | 80.5
2018-09-12 12:00 | 102.95 | 85.91
2018-09-12 12:30 | 107.39 | 89.82
2018-09-12 13:00 | 105.52 | 86.95
2018-09-12 13:30 | 104.92 | 87.16
2018-09-12 14:00 | 107.7 | 90.97
2018-09-12 14:30 | 109.45 | 92.94
2018-09-12 15:00 | 115.33 | 99.82
2018-09-12 15:30 | 109.78 | 93.4
2018-09-12 16:00 | 109.89 | 92.97
2018-09-12 16:30 | 112.97 | 96.22
2018-09-12 17:00 | 118.88 | 102.21
2018-09-12 17:30 | 114.79 | 97.8
2018-09-12 18:00 | 109.72 | 92.54
2018-09-12 18:30 | 120.95 | 104.23
2018-09-12 19:00 | 114.97 | 98.68
2018-09-12 19:30 | 112.24 | 96.1
2018-09-12 20:00 | 121.11 | 104.69
2018-09-12 20:30 | 119.02 | 102.78
2018-09-12 21:00 | 123.66 | 107.59
2018-09-12 21:30 | 120.22 | 103.73
2018-09-12 22:00 | 112.48 | 96.2
2018-09-12 22:30 | 119.04 | 102.58
2018-09-12 23:00 | 120.56 | 104.61
2018-09-12 23:30 | 112.87 | 96.4
2018-09-13 | 119.76 | 103.4
2018-09-13 00:30 | 114.01 | 97.64
2018-09-13 01:00 | 116.36 | 100.61
2018-09-13 01:30 | 109.4 | 93.7
2018-09-13 02:00 | 114.95 | 98.49
2018-09-13 02:30 | 119.49 | 103.74
2018-09-13 03:00 | 104.41 | 88.67
2018-09-13 03:30 | 111.11 | 94.92
2018-09-13 04:00 | 106.63 | 90.85
2018-09-13 04:30 | 103.72 | 87.6
2018-09-13 05:00 | 104.33 | 88.58
2018-09-13 05:30 | 106.25 | 90.35
2018-09-13 06:00 | 107.77 | 91.88
2018-09-13 06:30 | 106.89 | 90.3
2018-09-13 07:00 | 105.47 | 88.77
2018-09-13 07:30 | 108.88 | 93.1
2018-09-13 08:00 | 108.74 | 93.29
2018-09-13 08:30 | 105.49 | 90.06
2018-09-13 09:00 | 109.5 | 94.75
2018-09-13 09:30 | 113.39 | 97.82
2018-09-13 10:00 | 112.67 | 97.48
2018-09-13 10:30 | 113.3 | 97.69
2018-09-13 11:00 | 112.22 | 95.88
2018-09-13 11:30 | 110.39 | 93.14
2018-09-13 12:00 | 107.35 | 88.9
2018-09-13 12:30 | 108.33 | 89.07
2018-09-13 13:00 | 110.46 | 91.49
2018-09-13 13:30 | 114.03 | 95.22
2018-09-13 14:00 | 109.64 | 90.67
2018-09-13 14:30 | 115.94 | 98.71
2018-09-13 15:00 | 112.36 | 94.93
2018-09-13 15:30 | 97.01 | 78.28
2018-09-13 16:00 | 102.04 | 83.89
2018-09-13 16:30 | 113.27 | 96.04
2018-09-13 17:00 | 121.58 | 104.4
2018-09-13 17:30 | 117.34 | 99.04
2018-09-13 18:00 | 128.95 | 111.81
2018-09-13 18:30 | 123.29 | 105.36
2018-09-13 19:00 | 135.7 | 117.34
2018-09-13 19:30 | 134.34 | 117.03
2018-09-13 20:00 | 136.75 | 119.32
2018-09-13 20:30 | 125.58 | 107.26
2018-09-13 21:00 | 122.48 | 104.72
2018-09-13 21:30 | 118.84 | 100.45
2018-09-13 22:00 | 117.32 | 98.77
2018-09-13 22:30 | 119.71 | 101.8
2018-09-13 23:00 | 120.48 | 102.55
2018-09-13 23:30 | 120.5 | 102.9
2018-09-14 | 117.47 | 99.77
2018-09-14 00:30 | 112.15 | 94.72
2018-09-14 01:00 | 120.47 | 102.78
2018-09-14 01:30 | 120.15 | 102.13
2018-09-14 02:00 | 121.74 | 103.54
2018-09-14 02:30 | 119.69 | 101.17
2018-09-14 03:00 | 123.05 | 104.77
2018-09-14 03:30 | 120.37 | 101.82
2018-09-14 04:00 | 119.83 | 101.01
2018-09-14 04:30 | 116.4 | 97.08
2018-09-14 05:00 | 124.75 | 106.29
2018-09-14 05:30 | 113.71 | 95.68
2018-09-14 06:00 | 114.52 | 96.31
2018-09-14 06:30 | 109.09 | 91.18
2018-09-14 07:00 | 121.15 | 103.95
2018-09-14 07:30 | 123.9 | 107.03
2018-09-14 08:00 | 131.49 | 114.94
2018-09-14 08:30 | 116.95 | 99.19
2018-09-14 09:00 | 122.4 | 105.02
2018-09-14 09:30 | 115.16 | 97.38
2018-09-14 10:00 | 117.73 | 100.13
2018-09-14 10:30 | 119.28 | 101.93
2018-09-14 11:00 | 115.78 | 98.22
2018-09-14 11:30 | 120.61 | 103.19
2018-09-14 12:00 | 114.64 | 98.5
2018-09-14 12:30 | 107.26 | 89.86
2018-09-14 13:00 | 105.53 | 88.13
2018-09-14 13:30 | 108.52 | 91.38
2018-09-14 14:00 | 109.63 | 92.88
2018-09-14 14:30 | 110.43 | 93.36
2018-09-14 15:00 | 109.32 | 91.19
2018-09-14 15:30 | 107.63 | 89.04
2018-09-14 16:00 | 114.65 | 96.58
2018-09-14 16:30 | 120.6 | 102.71
2018-09-14 17:00 | 111.81 | 93.86
2018-09-14 17:30 | 122.33 | 105.54
2018-09-14 18:00 | 110.08 | 92.2
2018-09-14 18:30 | 113.93 | 95.37
2018-09-14 19:00 | 115.27 | 97.05
2018-09-14 19:30 | 120.14 | 101.38
2018-09-14 20:00 | 117.44 | 99.6
2018-09-14 20:30 | 114.2 | 96.29
2018-09-14 21:00 | 111.84 | 93.72
2018-09-14 21:30 | 111.69 | 93.74
2018-09-14 22:00 | 114.77 | 96.7
2018-09-14 22:30 | 114.02 | 96.27
2018-09-14 23:00 | 109.52 | 92.02
2018-09-14 23:30 | 105.22 | 87.04
2018-09-15 | 107.47 | 89.71
2018-09-15 00:30 | 104.38 | 86.38
2018-09-15 01:00 | 106.41 | 88.81
2018-09-15 01:30 | 107.04 | 88.86
2018-09-15 02:00 | 109.81 | 92.18
2018-09-15 02:30 | 111.72 | 94.19
2018-09-15 03:00 | 104.48 | 86.28
2018-09-15 03:30 | 108.36 | 90.1
2018-09-15 04:00 | 109.09 | 91.63
2018-09-15 04:30 | 108.45 | 90.94
2018-09-15 05:00 | 112.17 | 94.56
2018-09-15 05:30 | 108.29 | 90.6
2018-09-15 06:00 | 109.45 | 91.41
2018-09-15 06:30 | 102.48 | 84.01
2018-09-15 07:00 | 108.2 | 90.11
2018-09-15 07:30 | 105.2 | 88.9
2018-09-15 08:00 | 108.87 | 91.63
2018-09-15 08:30 | 109.29 | 91.67
2018-09-15 09:00 | 109.06 | 91.55
2018-09-15 09:30 | 100.61 | 81.89
2018-09-15 10:00 | 100.46 | 81.48
2018-09-15 10:30 | 108.61 | 90.72
2018-09-15 11:00 | 107.31 | 89.33
2018-09-15 11:30 | 106.22 | 88.71
2018-09-15 12:00 | 114.03 | 97.09
2018-09-15 12:30 | 114.67 | 96.76
2018-09-15 13:00 | 112.45 | 93.96
2018-09-15 13:30 | 119.68 | 101.33
2018-09-15 14:00 | 109.85 | 90.49
2018-09-15 14:30 | 111.29 | 91.99
2018-09-15 15:00 | 112.41 | 93.03
2018-09-15 15:30 | 112.82 | 92.81
2018-09-15 16:00 | 117.98 | 101.13
2018-09-15 16:30 | 116.87 | 99.71
2018-09-15 17:00 | 106.53 | 88.32
2018-09-15 17:30 | 114.22 | 96.39
2018-09-15 18:00 | 106.16 | 87.38
2018-09-15 18:30 | 112.83 | 94.2
2018-09-15 19:00 | 113.77 | 95.66
2018-09-15 19:30 | 115.24 | 96.85
2018-09-15 20:00 | 117.76 | 100.12
2018-09-15 20:30 | 114.1 | 95.82
2018-09-15 21:00 | 115.51 | 96.63
2018-09-15 21:30 | 109.92 | 91.66
2018-09-15 22:00 | 104.35 | 86.29
2018-09-15 22:30 | 110.87 | 92.68
2018-09-15 23:00 | 107.36 | 88.49
2018-09-15 23:30 | 101.14 | 82.35
2018-09-16 | 105.74 | 86.73
2018-09-16 00:30 | 102.49 | 83.98
2018-09-16 01:00 | 105.07 | 86.74
2018-09-16 01:30 | 103.87 | 85.67
2018-09-16 02:00 | 111.25 | 93.2
2018-09-16 02:30 | 108.38 | 89.95
2018-09-16 03:00 | 110.46 | 92.36
2018-09-16 03:30 | 109.22 | 91.89
2018-09-16 04:00 | 111.65 | 92.71
2018-09-16 04:30 | 111.43 | 91.9
2018-09-16 05:00 | 106.88 | 87.64
2018-09-16 05:30 | 104.94 | 85.79
2018-09-16 06:00 | 105.26 | 87.09
2018-09-16 06:30 | 93.65 | 74.74
2018-09-16 07:00 | 100.6 | 81.93
2018-09-16 07:30 | 100.35 | 81.76
2018-09-16 08:00 | 101.22 | 82.36
2018-09-16 08:30 | 104.39 | 87.29
2018-09-16 09:00 | 97.43 | 79.78
2018-09-16 09:30 | 102.78 | 84.7
2018-09-16 10:00 | 104.04 | 85.68
2018-09-16 10:30 | 108.55 | 91.31
2018-09-16 11:00 | 108.19 | 91.91
2018-09-16 11:30 | 105.65 | 89.91
2018-09-16 12:00 | 101.72 | 84.98
2018-09-16 12:30 | 103.43 | 86.13
2018-09-16 13:00 | 100.97 | 82.11
2018-09-16 13:30 | 110.42 | 92.12
2018-09-16 14:00 | 105.79 | 87.14
2018-09-16 14:30 | 109.19 | 90.34
2018-09-16 15:00 | 104.25 | 84.93
2018-09-16 15:30 | 105.46 | 81.85
2018-09-16 16:00 | 103.5 | 81.63
2018-09-16 16:30 | 103.38 | 81.5
2018-09-16 17:00 | 107.44 | 85.52
2018-09-16 17:30 | 107.53 | 85.9
2018-09-16 18:00 | 106.62 | 84.07
2018-09-16 18:30 | 109.03 | 85.42
2018-09-16 19:00 | 120.92 | 98.51
2018-09-16 19:30 | 111.83 | 89.26
2018-09-16 20:00 | 113.73 | 91.24
2018-09-16 20:30 | 117.93 | 95.92
2018-09-16 21:00 | 114.07 | 91.43
2018-09-16 21:30 | 112.36 | 90.1
2018-09-16 22:00 | 107.2 | 84.7
2018-09-16 22:30 | 114.02 | 92
2018-09-16 23:00 | 113.26 | 92.09
2018-09-16 23:30 | 112.85 | 91.48
2018-09-17 | 112.09 | 89.93
2018-09-17 00:30 | 110.25 | 86.7
2018-09-17 01:00 | 106.82 | 84.32
2018-09-17 01:30 | 105.03 | 82.14
2018-09-17 02:00 | 106.58 | 83.82
2018-09-17 02:30 | 107.64 | 84.77
2018-09-17 03:00 | 107.61 | 84.77
2018-09-17 03:30 | 105 | 82.18
2018-09-17 04:00 | 100.42 | 77.34
2018-09-17 04:30 | 100.74 | 78.55
2018-09-17 05:00 | 101.74 | 79.17
2018-09-17 05:30 | 92.36 | 72.33
2018-09-17 06:00 | 84.26 | 70.61
2018-09-17 06:30 | 81.46 | 67.5
2018-09-17 07:00 | 83.28 | 70.21
2018-09-17 07:30 | 83.73 | 71.32
2018-09-17 08:00 | 81.87 | 69.91
2018-09-17 08:30 | 79.55 | 67.9
2018-09-17 09:00 | 76.98 | 66.75
2018-09-17 09:30 | 74.62 | 64.49
2018-09-17 10:00 | 79.28 | 69.49
2018-09-17 10:30 | 78.05 | 69.11
2018-09-17 11:00 | 80.47 | 71.06
2018-09-17 11:30 | 77.41 | 67.45
2018-09-17 12:00 | 86.11 | 76.49
2018-09-17 12:30 | 89.38 | 80.16
2018-09-17 13:00 | 84.56 | 75.59
2018-09-17 13:30 | 82.74 | 73.57
2018-09-17 14:00 | 84.56 | 75.51
2018-09-17 14:30 | 82.6 | 73.48
2018-09-17 15:00 | 82.98 | 72.98
2018-09-17 15:30 | 85.58 | 75.34
2018-09-17 16:00 | 89.79 | 79.26
2018-09-17 16:30 | 85.99 | 75.2
2018-09-17 17:00 | 87.69 | 77.17
2018-09-17 17:30 | 86.07 | 74.71
2018-09-17 18:00 | 85.83 | 74.52
2018-09-17 18:30 | 81.27 | 69.66
2018-09-17 19:00 | 90.64 | 79.44
2018-09-17 19:30 | 88.67 | 77.77
2018-09-17 20:00 | 89.99 | 78.77
2018-09-17 20:30 | 92.57 | 81.86
2018-09-17 21:00 | 90.71 | 80.51
2018-09-17 21:30 | 90.68 | 80.95
2018-09-17 22:00 | 86.12 | 76.9
2018-09-17 22:30 | 88.49 | 79.49
2018-09-17 23:00 | 89.04 | 79.41
2018-09-17 23:30 | 84.95 | 75.61
2018-09-18 | 86.25 | 77.3
2018-09-18 00:30 | 89.41 | 80.18
2018-09-18 01:00 | 83.87 | 75.25
2018-09-18 01:30 | 84.44 | 75.79
2018-09-18 02:00 | 83.24 | 74.05
2018-09-18 02:30 | 85.08 | 75.87
2018-09-18 03:00 | 82.63 | 73.62
2018-09-18 03:30 | 81.23 | 72.2
2018-09-18 04:00 | 78.41 | 69.14
2018-09-18 04:30 | 74.94 | 65.72
2018-09-18 05:00 | 72.03 | 63.31
2018-09-18 05:30 | 72.39 | 63.52
2018-09-18 06:00 | 71.78 | 62.37
2018-09-18 06:30 | 67.33 | 57.74
2018-09-18 07:00 | 68.74 | 60.38
2018-09-18 07:30 | 61.65 | 53.1
2018-09-18 08:00 | 61.06 | 51.96
2018-09-18 08:30 | 51.79 | 41.64
2018-09-18 09:00 | 50.48 | 41.09
2018-09-18 09:30 | 54.8 | 46.03
2018-09-18 10:00 | 55.06 | 45.56
2018-09-18 10:30 | 57.32 | 48.09
2018-09-18 11:00 | 57.07 | 47.75
2018-09-18 11:30 | 54.36 | 45.13
2018-09-18 12:00 | 53.79 | 44.44
2018-09-18 12:30 | 57.69 | 48.61
2018-09-18 13:00 | 60.05 | 49.79
2018-09-18 13:30 | 57.65 | 47.48
2018-09-18 14:00 | 61.9 | 51.32
2018-09-18 14:30 | 61.86 | 51.23
2018-09-18 15:00 | 59.81 | 49.04
2018-09-18 15:30 | 60.23 | 48.68
2018-09-18 16:00 | 61.72 | 50.07
2018-09-18 16:30 | 63.42 | 51.68
2018-09-18 17:00 | 66.28 | 54.09
2018-09-18 17:30 | 71.72 | 59.3
2018-09-18 18:00 | 75.55 | 62.04
2018-09-18 18:30 | 75.13 | 61.13
2018-09-18 19:00 | 83.78 | 70.52
2018-09-18 19:30 | 85.41 | 72.64
2018-09-18 20:00 | 86.9 | 74.02
2018-09-18 20:30 | 90.46 | 77.19
2018-09-18 21:00 | 87.15 | 74.07
2018-09-18 21:30 | 85.02 | 72.03
2018-09-18 22:00 | 87.2 | 74.28
2018-09-18 22:30 | 84.63 | 72.3
2018-09-18 23:00 | 82.48 | 69.79
2018-09-18 23:30 | 83.96 | 71.79
2018-09-19 | 84.17 | 72.03
2018-09-19 00:30 | 82.35 | 70.53
2018-09-19 01:00 | 84.96 | 72.66
2018-09-19 01:30 | 81.91 | 69.95
2018-09-19 02:00 | 82.38 | 70.71
2018-09-19 02:30 | 85.06 | 73.05
2018-09-19 03:00 | 82.08 | 69.78
2018-09-19 03:30 | 81.32 | 68.97
2018-09-19 04:00 | 80.86 | 69.28
2018-09-19 04:30 | 78.34 | 66.68
2018-09-19 05:00 | 76.39 | 64.91
2018-09-19 05:30 | 75.84 | 64.06
2018-09-19 06:00 | 76.18 | 64.5
2018-09-19 06:30 | 69.87 | 57.55
2018-09-19 07:00 | 90.02 | 67.86
2018-09-19 07:30 | 95.93 | 74.21
2018-09-19 08:00 | 90.49 | 68.9
2018-09-19 08:30 | 86.63 | 64.65
2018-09-19 09:00 | 91.58 | 70.04
2018-09-19 09:30 | 84.06 | 60.1
2018-09-19 10:00 | 85.12 | 61.46
2018-09-19 10:30 | 83.4 | 60.83
2018-09-19 11:00 | 83.82 | 61.89
2018-09-19 11:30 | 83.19 | 61.96
2018-09-19 12:00 | 98.96 | 79.47
2018-09-19 12:30 | 88.6 | 68.26
2018-09-19 13:00 | 85.71 | 65.41
2018-09-19 13:30 | 89.45 | 68.8
2018-09-19 14:00 | 92.72 | 72.55
2018-09-19 14:30 | 92.79 | 72.57
2018-09-19 15:00 | 86.64 | 66.32
2018-09-19 15:30 | 85.9 | 65.73
2018-09-19 16:00 | 97.03 | 77.04
2018-09-19 16:30 | 94.8 | 74.99
2018-09-19 17:00 | 92.3 | 71.5
2018-09-19 17:30 | 91.41 | 70.14
2018-09-19 18:00 | 93.42 | 72.95
2018-09-19 18:30 | 88.94 | 67.36
2018-09-19 19:00 | 98.51 | 78.07
2018-09-19 19:30 | 102.32 | 81.77
2018-09-19 20:00 | 106.82 | 86.63
2018-09-19 20:30 | 105.63 | 84.93
2018-09-19 21:00 | 104.6 | 83.99
2018-09-19 21:30 | 99.52 | 78.14
2018-09-19 22:00 | 108.06 | 88.32
2018-09-19 22:30 | 104.83 | 85.16
2018-09-19 23:00 | 105.19 | 83.63
2018-09-19 23:30 | 106.75 | 86.52
2018-09-20 | 103.85 | 84.31
2018-09-20 00:30 | 105.82 | 86.48
2018-09-20 01:00 | 101.04 | 79.96
2018-09-20 01:30 | 100.53 | 79.33
2018-09-20 02:00 | 110.92 | 90.76
2018-09-20 02:30 | 113.79 | 93.4
2018-09-20 03:00 | 100.19 | 79.82
2018-09-20 03:30 | 101.71 | 82.21
2018-09-20 04:00 | 104 | 84.51
2018-09-20 04:30 | 99.14 | 78.55
2018-09-20 05:00 | 95.04 | 75.01
2018-09-20 05:30 | 92.57 | 71.66
2018-09-20 06:00 | 95.99 | 75.65
2018-09-20 06:30 | 87.08 | 65.24
2018-09-20 07:00 | 96.9 | 76.03
2018-09-20 07:30 | 91.68 | 70.89
2018-09-20 08:00 | 91.06 | 70.59
2018-09-20 08:30 | 96.38 | 77.95
2018-09-20 09:00 | 102.91 | 86.06
2018-09-20 09:30 | 99.02 | 81.4
2018-09-20 10:00 | 98.9 | 81.72
2018-09-20 10:30 | 97.63 | 80.05
2018-09-20 11:00 | 92.54 | 74.46
2018-09-20 11:30 | 93.92 | 75.46
2018-09-20 12:00 | 101.09 | 83.4
2018-09-20 12:30 | 103.59 | 85.67
2018-09-20 13:00 | 94.35 | 75.37
2018-09-20 13:30 | 99.2 | 80.76
2018-09-20 14:00 | 104.3 | 86.28
2018-09-20 14:30 | 103.06 | 85.22
2018-09-20 15:00 | 108.02 | 90.53
2018-09-20 15:30 | 107.99 | 89.54
2018-09-20 16:00 | 105.51 | 87.02
2018-09-20 16:30 | 111.75 | 92.58
2018-09-20 17:00 | 108.82 | 90.19
2018-09-20 17:30 | 103.48 | 83.56
2018-09-20 18:00 | 103.17 | 82.58
2018-09-20 18:30 | 98.66 | 77.39
2018-09-20 19:00 | 110.04 | 88.71
2018-09-20 19:30 | 112.37 | 91.01
2018-09-20 20:00 | 112.53 | 91.4
2018-09-20 20:30 | 109.33 | 88.03
2018-09-20 21:00 | 112.37 | 91.28
2018-09-20 21:30 | 107.87 | 86.75
2018-09-20 22:00 | 109.68 | 88.48
2018-09-20 22:30 | 107.76 | 86.85
2018-09-20 23:00 | 102.47 | 81.12
2018-09-20 23:30 | 105.82 | 82.51
2018-09-21 | 101.12 | 78.7
2018-09-21 00:30 | 103.15 | 81.94
2018-09-21 01:00 | 97.6 | 74.84
2018-09-21 01:30 | 96.72 | 73.75
2018-09-21 02:00 | 102.05 | 79.62
2018-09-21 02:30 | 102.68 | 80.15
2018-09-21 03:00 | 96.77 | 73.63
2018-09-21 03:30 | 100.27 | 78.06
2018-09-21 04:00 | 100.23 | 78.27
2018-09-21 04:30 | 104.63 | 82.83
2018-09-21 05:00 | 107.57 | 86.45
2018-09-21 05:30 | 103.84 | 82.37
2018-09-21 06:00 | 106.33 | 84.4
2018-09-21 06:30 | 95.83 | 71.99
2018-09-21 07:00 | 101.63 | 79.37
2018-09-21 07:30 | 108.6 | 87.33
2018-09-21 08:00 | 100.08 | 78.03
2018-09-21 08:30 | 94.52 | 72.48
2018-09-21 09:00 | 95.47 | 73.76
2018-09-21 09:30 | 101.6 | 79.88
2018-09-21 10:00 | 105.49 | 83.08
2018-09-21 10:30 | 104.59 | 83.49
2018-09-21 11:00 | 95.53 | 74.99
2018-09-21 11:30 | 96.74 | 76.33
2018-09-21 12:00 | 104.93 | 85.03
2018-09-21 12:30 | 106.34 | 87.26
2018-09-21 13:00 | 99.07 | 78.64
2018-09-21 13:30 | 97.47 | 75.81
2018-09-21 14:00 | 106.65 | 86.61
2018-09-21 14:30 | 99.52 | 77.84
2018-09-21 15:00 | 99.36 | 76.83
2018-09-21 15:30 | 102.17 | 79.6
2018-09-21 16:00 | 105.41 | 83.97
2018-09-21 16:30 | 108.39 | 87.4
2018-09-21 17:00 | 108.92 | 87.36
2018-09-21 17:30 | 107.76 | 86.93
2018-09-21 18:00 | 108.82 | 88.11
2018-09-21 18:30 | 101.11 | 80.22
2018-09-21 19:00 | 118.13 | 97.48
2018-09-21 19:30 | 115.98 | 95.53
2018-09-21 20:00 | 110.98 | 89.58
2018-09-21 20:30 | 111.83 | 90.7
2018-09-21 21:00 | 106.76 | 86.08
2018-09-21 21:30 | 103.8 | 82.15
2018-09-21 22:00 | 105.89 | 84.82
2018-09-21 22:30 | 104.21 | 83.77
2018-09-21 23:00 | 112.31 | 93
2018-09-21 23:30 | 105.16 | 84.65
2018-09-22 | 104.54 | 84.5
2018-09-22 00:30 | 112.46 | 92.77
2018-09-22 01:00 | 101.17 | 79.98
2018-09-22 01:30 | 100.29 | 79.79
2018-09-22 02:00 | 106.69 | 86.97
2018-09-22 02:30 | 99.69 | 78.97
2018-09-22 03:00 | 97.34 | 76.04
2018-09-22 03:30 | 101.19 | 79.72
2018-09-22 04:00 | 101.69 | 79.95
2018-09-22 04:30 | 97.19 | 75.59
2018-09-22 05:00 | 98.62 | 77.15
2018-09-22 05:30 | 99.26 | 78.06
2018-09-22 06:00 | 104.17 | 83.55
2018-09-22 06:30 | 100.87 | 79.44
2018-09-22 07:00 | 102.15 | 82.11
2018-09-22 07:30 | 101.63 | 81.7
2018-09-22 08:00 | 103.55 | 84.12
2018-09-22 08:30 | 97.12 | 77.46
2018-09-22 09:00 | 97.78 | 77.25
2018-09-22 09:30 | 101.41 | 80.13
2018-09-22 10:00 | 95.11 | 72.56
2018-09-22 10:30 | 102.73 | 82.36
2018-09-22 11:00 | 98.9 | 77.61
2018-09-22 11:30 | 96.34 | 74.59
2018-09-22 12:00 | 103.52 | 82.35
2018-09-22 12:30 | 96.59 | 75.1
2018-09-22 13:00 | 99.21 | 78.3
2018-09-22 13:30 | 105.08 | 84.03
2018-09-22 14:00 | 94.83 | 73.18
2018-09-22 14:30 | 99.05 | 78.75
2018-09-22 15:00 | 94.69 | 73.8
2018-09-22 15:30 | 88.43 | 66.19
2018-09-22 16:00 | 96.96 | 75.75
2018-09-22 16:30 | 101.86 | 79.23
2018-09-22 17:00 | 101.78 | 79.61
2018-09-22 17:30 | 102.18 | 80.22
2018-09-22 18:00 | 100.21 | 77.15
2018-09-22 18:30 | 101.85 | 79.02
2018-09-22 19:00 | 106.44 | 84.53
2018-09-22 19:30 | 109.85 | 87.49
2018-09-22 20:00 | 117.91 | 96.47
2018-09-22 20:30 | 119.87 | 95.47
2018-09-22 21:00 | 111.92 | 88.18
2018-09-22 21:30 | 108.92 | 85.51
2018-09-22 22:00 | 112.82 | 90.5
2018-09-22 22:30 | 112.53 | 89.88
2018-09-22 23:00 | 112.63 | 90.39
2018-09-22 23:30 | 109.89 | 87.99
2018-09-23 | 111.82 | 90.77
2018-09-23 00:30 | 100.45 | 77.23
2018-09-23 01:00 | 103.17 | 80.95
2018-09-23 01:30 | 102.41 | 80.96
2018-09-23 02:00 | 103.35 | 81.81
2018-09-23 02:30 | 106.29 | 84.51
2018-09-23 03:00 | 109.8 | 87.8
2018-09-23 03:30 | 101.65 | 79.1
2018-09-23 04:00 | 110.16 | 88.69
2018-09-23 04:30 | 109.91 | 88.4
2018-09-23 05:00 | 105.95 | 83.75
2018-09-23 05:30 | 101.91 | 78.96
2018-09-23 06:00 | 103.78 | 81.79
2018-09-23 06:30 | 103.37 | 81.29
2018-09-23 07:00 | 106.34 | 83.94
2018-09-23 07:30 | 103.45 | 81
2018-09-23 08:00 | 98.23 | 75.21
2018-09-23 08:30 | 101.6 | 77.48
2018-09-23 09:00 | 103.4 | 78.85
2018-09-23 09:30 | 105.14 | 81.05
2018-09-23 10:00 | 106.73 | 83.05
2018-09-23 10:30 | 98.02 | 73.66
2018-09-23 11:00 | 96.54 | 71.1
2018-09-23 11:30 | 103.3 | 80.15
2018-09-23 12:00 | 106.58 | 83.56
2018-09-23 12:30 | 104 | 80.15
2018-09-23 13:00 | 114.22 | 91.8
2018-09-23 13:30 | 111.93 | 88.06
2018-09-23 14:00 | 107.94 | 85.51
2018-09-23 14:30 | 104.78 | 82.74
2018-09-23 15:00 | 105.73 | 83.07
2018-09-23 15:30 | 95.58 | 72.58
2018-09-23 16:00 | 101.42 | 78.3
2018-09-23 16:30 | 101.97 | 78.55
2018-09-23 17:00 | 111.17 | 88.23
2018-09-23 17:30 | 124.36 | 102.19
2018-09-23 18:00 | 122.87 | 99.94
2018-09-23 18:30 | 115.11 | 91.42
2018-09-23 19:00 | 114.83 | 91.19
2018-09-23 19:30 | 118.8 | 94.72
2018-09-23 20:00 | 115.51 | 92.32
2018-09-23 20:30 | 117.31 | 93.48
2018-09-23 21:00 | 107.65 | 83.09
2018-09-23 21:30 | 103.52 | 82.04
2018-09-23 22:00 | 99.62 | 78.19
2018-09-23 22:30 | 100.92 | 78.91
2018-09-23 23:00 | 94.86 | 71.27
2018-09-23 23:30 | 100.08 | 77.1
2018-09-24 | 105.35 | 82.31
2018-09-24 00:30 | 100.03 | 77.06
2018-09-24 01:00 | 97.16 | 74.06
2018-09-24 01:30 | 97.49 | 73.91
2018-09-24 02:00 | 107.55 | 84.3
2018-09-24 02:30 | 116.28 | 93.2
2018-09-24 03:00 | 110.57 | 85.77
2018-09-24 03:30 | 115.98 | 92.9
2018-09-24 04:00 | 113.82 | 90.76
2018-09-24 04:30 | 112.13 | 89.43
2018-09-24 05:00 | 114.18 | 91.5
2018-09-24 05:30 | 115.95 | 93.33
2018-09-24 06:00 | 118.85 | 97.87
2018-09-24 06:30 | 115.46 | 91.32
2018-09-24 07:00 | 116 | 92.48
2018-09-24 07:30 | 121.15 | 98.32
2018-09-24 08:00 | 120.44 | 96.3
2018-09-24 08:30 | 118.33 | 93.06
2018-09-24 09:00 | 119.84 | 94.69
2018-09-24 09:30 | 131.35 | 105.9
2018-09-24 10:00 | 121.24 | 98.08
2018-09-24 10:30 | 110.89 | 87.69
2018-09-24 11:00 | 118.15 | 94.81
2018-09-24 11:30 | 115.27 | 93.16
2018-09-24 12:00 | 110.33 | 86.74
2018-09-24 12:30 | 113 | 89.76
2018-09-24 13:00 | 117.76 | 94.16
2018-09-24 13:30 | 108.46 | 85.78
2018-09-24 14:00 | 112.82 | 91.49
2018-09-24 14:30 | 114.38 | 92.8
2018-09-24 15:00 | 112.93 | 90.24
2018-09-24 15:30 | 106.31 | 81.47
2018-09-24 16:00 | 119.68 | 95.83
2018-09-24 16:30 | 129.13 | 104.36
2018-09-24 17:00 | 126.67 | 100.45
2018-09-24 17:30 | 120.83 | 94.45
2018-09-24 18:00 | 124.3 | 98.08
2018-09-24 18:30 | 124.64 | 98.4
2018-09-24 19:00 | 120.45 | 92.85
2018-09-24 19:30 | 127.53 | 101.05
2018-09-24 20:00 | 119.37 | 92.3
2018-09-24 20:30 | 123.25 | 95.78
2018-09-24 21:00 | 126.9 | 100.76
2018-09-24 21:30 | 128.53 | 103.12
2018-09-24 22:00 | 124.04 | 96.62
2018-09-24 22:30 | 129.83 | 100.92
2018-09-24 23:00 | 125.75 | 96.6
2018-09-24 23:30 | 120.37 | 92.26
2018-09-25 | 124.71 | 98.39
2018-09-25 00:30 | 127.32 | 99.99
2018-09-25 01:00 | 119.96 | 93.81
2018-09-25 01:30 | 118.68 | 92.64
2018-09-25 02:00 | 122.42 | 97.88
2018-09-25 02:30 | 110.14 | 86.49
2018-09-25 03:00 | 121.85 | 97.43
2018-09-25 03:30 | 116.31 | 90.32
2018-09-25 04:00 | 120.96 | 95.69
2018-09-25 04:30 | 115.87 | 90.3
2018-09-25 05:00 | 109.9 | 85.26
2018-09-25 05:30 | 108.92 | 86.28
2018-09-25 06:00 | 117.09 | 94.6
2018-09-25 06:30 | 118.15 | 95.35
2018-09-25 07:00 | 113.55 | 92.04
2018-09-25 07:30 | 111.05 | 88.78
2018-09-25 08:00 | 109.56 | 87.31
2018-09-25 08:30 | 112.15 | 88.27
2018-09-25 09:00 | 107.36 | 82.08
2018-09-25 09:30 | 110.41 | 86.05
2018-09-25 10:00 | 107.99 | 85.87
2018-09-25 10:30 | 102.56 | 80.64
2018-09-25 11:00 | 98.96 | 75.89
2018-09-25 11:30 | 111.94 | 89.74
2018-09-25 12:00 | 108.39 | 85.63
2018-09-25 12:30 | 100.57 | 78.73
2018-09-25 13:00 | 109.81 | 86.1
2018-09-25 13:30 | 107.17 | 84.55
2018-09-25 14:00 | 109.93 | 85.55
2018-09-25 14:30 | 112.67 | 87.81
2018-09-25 15:00 | 110.21 | 83.72
2018-09-25 15:30 | 108.62 | 85.46
2018-09-25 16:00 | 108.39 | 84.27
2018-09-25 16:30 | 109.53 | 85.7
2018-09-25 17:00 | 106.29 | 84.42
2018-09-25 17:30 | 109.53 | 88.51
2018-09-25 18:00 | 112.51 | 90.48
2018-09-25 18:30 | 105.07 | 82.98
2018-09-25 19:00 | 108.94 | 85.75
2018-09-25 19:30 | 115.67 | 94.12
2018-09-25 20:00 | 113.8 | 92.16
2018-09-25 20:30 | 119.12 | 96.3
2018-09-25 21:00 | 117.04 | 95.85
2018-09-25 21:30 | 107.41 | 86.87
2018-09-25 22:00 | 112.64 | 93.77
2018-09-25 22:30 | 111.51 | 92.54
2018-09-25 23:00 | 108.56 | 90.44
2018-09-25 23:30 | 115.57 | 96.8
2018-09-26 | 114.51 | 94.64
2018-09-26 00:30 | 119.69 | 100.48
2018-09-26 01:00 | 114.11 | 94.33
2018-09-26 01:30 | 115.64 | 94.51
2018-09-26 02:00 | 110.68 | 89.65
2018-09-26 02:30 | 114.62 | 93.29
2018-09-26 03:00 | 119.72 | 99.8
2018-09-26 03:30 | 117.2 | 96.31
2018-09-26 04:00 | 125.08 | 103.96
2018-09-26 04:30 | 119.5 | 98.75
2018-09-26 05:00 | 114.23 | 93.77
2018-09-26 05:30 | 115.36 | 94.72
2018-09-26 06:00 | 116.8 | 97.85
2018-09-26 06:30 | 109.84 | 90.21
2018-09-26 07:00 | 110.96 | 91.53
2018-09-26 07:30 | 114.24 | 94.8
2018-09-26 08:00 | 123.28 | 104.27
2018-09-26 08:30 | 115.3 | 92.4
2018-09-26 09:00 | 120.43 | 99.3
2018-09-26 09:30 | 105.86 | 83.16
2018-09-26 10:00 | 105.76 | 80.39
2018-09-26 10:30 | 99.34 | 73.77
2018-09-26 11:00 | 103.77 | 78.74
2018-09-26 11:30 | 104.68 | 78.89
2018-09-26 12:00 | 110.44 | 84.78
2018-09-26 12:30 | 113.57 | 89.24
2018-09-26 13:00 | 109.68 | 84.7
2018-09-26 13:30 | 113.58 | 88.35
2018-09-26 14:00 | 115.13 | 90.38
2018-09-26 14:30 | 118.14 | 93.24
2018-09-26 15:00 | 116.5 | 90.55
2018-09-26 15:30 | 129.81 | 105.37
2018-09-26 16:00 | 125.99 | 99.93
2018-09-26 16:30 | 122.35 | 97.05
2018-09-26 17:00 | 118.72 | 92.74
2018-09-26 17:30 | 125.74 | 101.37
2018-09-26 18:00 | 122.34 | 98.97
2018-09-26 18:30 | 112.96 | 88.21
2018-09-26 19:00 | 123.5 | 101.52
2018-09-26 19:30 | 126.23 | 104.53
2018-09-26 20:00 | 121.89 | 98.91
2018-09-26 20:30 | 128.15 | 106.17
2018-09-26 21:00 | 123.68 | 101.49
2018-09-26 21:30 | 127.84 | 106.74
2018-09-26 22:00 | 129.76 | 107.4
2018-09-26 22:30 | 116.97 | 93.65
2018-09-26 23:00 | 120.84 | 97.42
2018-09-26 23:30 | 117.74 | 94.77
2018-09-27 | 121.11 | 98.91
2018-09-27 00:30 | 117.71 | 95.72
2018-09-27 01:00 | 118.23 | 95.95
2018-09-27 01:30 | 118.9 | 97.28
2018-09-27 02:00 | 126 | 104.32
2018-09-27 02:30 | 125.65 | 104.48
2018-09-27 03:00 | 123.51 | 101.08
2018-09-27 03:30 | 123.52 | 101.24
2018-09-27 04:00 | 124.47 | 101.56
2018-09-27 04:30 | 117.42 | 95.35
2018-09-27 05:00 | 124.79 | 102.36
2018-09-27 05:30 | 116.06 | 93.2
2018-09-27 06:00 | 117.41 | 96.27
2018-09-27 06:30 | 111.07 | 90.67
2018-09-27 07:00 | 117.51 | 98.56
2018-09-27 07:30 | 118.31 | 97.47
2018-09-27 08:00 | 114.8 | 93.72
2018-09-27 08:30 | 116.7 | 96.93
2018-09-27 09:00 | 112.86 | 91.82
2018-09-27 09:30 | 106.51 | 87.06
2018-09-27 10:00 | 106.07 | 85.7
2018-09-27 10:30 | 111.18 | 91.93
2018-09-27 11:00 | 112.7 | 93.31
2018-09-27 11:30 | 102.61 | 82.05
2018-09-27 12:00 | 115.4 | 94.61
2018-09-27 12:30 | 119.78 | 98.85
2018-09-27 13:00 | 111.18 | 89.64
2018-09-27 13:30 | 110.15 | 88.2
2018-09-27 14:00 | 113.69 | 93.21
2018-09-27 14:30 | 114.31 | 94.46
2018-09-27 15:00 | 117.45 | 98.49
2018-09-27 15:30 | 115.54 | 96.76
2018-09-27 16:00 | 117.4 | 97.85
2018-09-27 16:30 | 124.74 | 105.15
2018-09-27 17:00 | 131.45 | 110.8
2018-09-27 17:30 | 123.03 | 102.38
2018-09-27 18:00 | 119.55 | 99.51
2018-09-27 18:30 | 110.72 | 89.86
2018-09-27 19:00 | 119.58 | 99.01
2018-09-27 19:30 | 121.24 | 100.9
2018-09-27 20:00 | 121.83 | 101.77
2018-09-27 20:30 | 134.74 | 115.7
2018-09-27 21:00 | 130.65 | 111.04
2018-09-27 21:30 | 126.3 | 105.96
2018-09-27 22:00 | 128.27 | 106.47
2018-09-27 22:30 | 122.72 | 102.44
2018-09-27 23:00 | 119.32 | 99.36
2018-09-27 23:30 | 122.42 | 102.08
2018-09-28 | 116.51 | 95.93
2018-09-28 00:30 | 110.78 | 89.21
2018-09-28 01:00 | 121.49 | 100.35
2018-09-28 01:30 | 116.08 | 94.85
2018-09-28 02:00 | 118.14 | 97.69
2018-09-28 02:30 | 120.76 | 101.1
2018-09-28 03:00 | 122.01 | 102.64
2018-09-28 03:30 | 113.56 | 93.71
2018-09-28 04:00 | 121.95 | 102.98
2018-09-28 04:30 | 121.3 | 101.46
2018-09-28 05:00 | 118.8 | 99.1
2018-09-28 05:30 | 117.33 | 97.34
2018-09-28 06:00 | 111.82 | 91.76
2018-09-28 06:30 | 110.21 | 89.3
2018-09-28 07:00 | 110.34 | 90.34
2018-09-28 07:30 | 117.12 | 98.18
2018-09-28 08:00 | 119.33 | 100.06
2018-09-28 08:30 | 120.27 | 101.02
2018-09-28 09:00 | 120.82 | 101.91
2018-09-28 09:30 | 109.52 | 87.77
2018-09-28 10:00 | 113.31 | 90.58
2018-09-28 10:30 | 109.36 | 87.43
2018-09-28 11:00 | 115.36 | 95.12
2018-09-28 11:30 | 115.11 | 93.59
2018-09-28 12:00 | 120.33 | 96.86
2018-09-28 12:30 | 118.35 | 93.86
2018-09-28 13:00 | 120.56 | 96.26
2018-09-28 13:30 | 116.28 | 92.21
2018-09-28 14:00 | 120.06 | 97.4
2018-09-28 14:30 | 122.15 | 100.87
2018-09-28 15:00 | 119.72 | 97.77
2018-09-28 15:30 | 127.82 | 104.68
2018-09-28 16:00 | 125.59 | 102.96
2018-09-28 16:30 | 122.47 | 98.3
2018-09-28 17:00 | 128.92 | 105.51
2018-09-28 17:30 | 128.42 | 104.48
2018-09-28 18:00 | 120.5 | 96.75
2018-09-28 18:30 | 120.13 | 97.13
2018-09-28 19:00 | 128.94 | 106.28
2018-09-28 19:30 | 128.02 | 103.85
2018-09-28 20:00 | 126.98 | 103.87
2018-09-28 20:30 | 125.9 | 103.83
2018-09-28 21:00 | 131.73 | 109.77
2018-09-28 21:30 | 116.99 | 94.02
2018-09-28 22:00 | 118.03 | 96.26
2018-09-28 22:30 | 119.74 | 100.06
2018-09-28 23:00 | 115.81 | 93.48
2018-09-28 23:30 | 116.66 | 94.22
2018-09-29 | 121.35 | 100.74
2018-09-29 00:30 | 124.63 | 103.29
2018-09-29 01:00 | 119.39 | 97.1
2018-09-29 01:30 | 123.06 | 99.86
2018-09-29 02:00 | 123.88 | 101.26
2018-09-29 02:30 | 118.86 | 96.56
2018-09-29 03:00 | 117.51 | 95.33
2018-09-29 03:30 | 119.07 | 96.58
2018-09-29 04:00 | 124.28 | 103.47
2018-09-29 04:30 | 122.32 | 101.84
2018-09-29 05:00 | 123.91 | 103.29
2018-09-29 05:30 | 120.74 | 100.75
2018-09-29 06:00 | 112.16 | 91.83
2018-09-29 06:30 | 114.35 | 92.87
2018-09-29 07:00 | 118.38 | 98.44
2018-09-29 07:30 | 119.62 | 99.93
2018-09-29 08:00 | 122.34 | 102.65
2018-09-29 08:30 | 112.2 | 91.26
2018-09-29 09:00 | 109.26 | 89.9
2018-09-29 09:30 | 99.84 | 81.82
2018-09-29 10:00 | 107.29 | 85.98
2018-09-29 10:30 | 111.9 | 91.23
2018-09-29 11:00 | 96.51 | 78.57
2018-09-29 11:30 | 96.32 | 76.45
2018-09-29 12:00 | 108.39 | 86.33
2018-09-29 12:30 | 121.41 | 97.69
2018-09-29 13:00 | 119 | 95.51
2018-09-29 13:30 | 119.05 | 94.6
2018-09-29 14:00 | 125 | 101.74
2018-09-29 14:30 | 120.47 | 96.76
2018-09-29 15:00 | 120.88 | 98.08
2018-09-29 15:30 | 121.8 | 99.92
2018-09-29 16:00 | 124.94 | 102.72
2018-09-29 16:30 | 122.92 | 100.34
2018-09-29 17:00 | 121.49 | 97.99
2018-09-29 17:30 | 123.29 | 98.93
2018-09-29 18:00 | 125.32 | 101.19
2018-09-29 18:30 | 116.34 | 91.39
2018-09-29 19:00 | 125.31 | 101.77
2018-09-29 19:30 | 124.78 | 101.13
2018-09-29 20:00 | 126.86 | 102.8
2018-09-29 20:30 | 123.6 | 99.22
2018-09-29 21:00 | 125.07 | 101.67
2018-09-29 21:30 | 114.85 | 90.63
2018-09-29 22:00 | 116.01 | 91.79
2018-09-29 22:30 | 117.08 | 93.31
2018-09-29 23:00 | 120.81 | 98.06
2018-09-29 23:30 | 117.03 | 93.98
2018-09-30 | 118.22 | 96.99
2018-09-30 00:30 | 114.41 | 92.24
2018-09-30 01:00 | 113.79 | 90.56
2018-09-30 01:30 | 120.3 | 96.38
2018-09-30 02:00 | 116.24 | 91.79
2018-09-30 02:30 | 118.45 | 93.96
2018-09-30 03:00 | 116.25 | 92.68
2018-09-30 03:30 | 113.91 | 90.8
2018-09-30 04:00 | 118.84 | 97.4
2018-09-30 04:30 | 117.28 | 95.45
2018-09-30 05:00 | 123.63 | 101.72
2018-09-30 05:30 | 113.92 | 92.09
2018-09-30 06:00 | 112.47 | 89.35
2018-09-30 06:30 | 107.11 | 83.04
2018-09-30 07:00 | 110.75 | 88.37
2018-09-30 07:30 | 118.79 | 95.26
2018-09-30 08:00 | 114.8 | 90.88
2018-09-30 08:30 | 119.03 | 95.53
2018-09-30 09:00 | 113.98 | 91.04
2018-09-30 09:30 | 110.29 | 85.4
2018-09-30 10:00 | 111.48 | 85.37
2018-09-30 10:30 | 119.12 | 94.6
2018-09-30 11:00 | 109.94 | 85.09
2018-09-30 11:30 | 110.33 | 86.43
2018-09-30 12:00 | 106.58 | 81.38
2018-09-30 12:30 | 122.42 | 99.23
2018-09-30 13:00 | 112.89 | 87.29
2018-09-30 13:30 | 117.28 | 92.11
2018-09-30 14:00 | 112.42 | 87.37
2018-09-30 14:30 | 113.47 | 87.49
2018-09-30 15:00 | 114.59 | 88.86
2018-09-30 15:30 | 113.15 | 87.54
2018-09-30 16:00 | 112.95 | 86.67
2018-09-30 16:30 | 118.67 | 91.75
2018-09-30 17:00 | 123.45 | 99.86
2018-09-30 17:30 | 127.98 | 104.17
2018-09-30 18:00 | 132.8 | 109.97
2018-09-30 18:30 | 121.35 | 98.81
2018-09-30 19:00 | 130.92 | 107.71
2018-09-30 19:30 | 128.82 | 107.19
2018-09-30 20:00 | 118.78 | 96.31
2018-09-30 20:30 | 122.82 | 100.41
2018-09-30 21:00 | 122.13 | 101.32
2018-09-30 21:30 | 126.24 | 105.59
2018-09-30 22:00 | 129.9 | 110
2018-09-30 22:30 | 123.72 | 104.11
2018-09-30 23:00 | 124.42 | 104.2
2018-09-30 23:30 | 123.32 | 103.05
2018-10-01 | 117.6 | 96.66
2018-10-01 00:30 | 116.43 | 95.1
2018-10-01 01:00 | 117.95 | 96.29
2018-10-01 01:30 | 116.69 | 95.02
2018-10-01 02:00 | 113.07 | 93.48
2018-10-01 02:30 | 114.38 | 95.18
2018-10-01 03:00 | 119.9 | 100.66
2018-10-01 03:30 | 117.41 | 96.12
2018-10-01 04:00 | 119.33 | 99.31
2018-10-01 04:30 | 116.9 | 97.09
2018-10-01 05:00 | 120.2 | 101.63
2018-10-01 05:30 | 112.85 | 93.04
2018-10-01 06:00 | 118.51 | 99.19
2018-10-01 06:30 | 110.36 | 91.03
2018-10-01 07:00 | 114.97 | 95.78
2018-10-01 07:30 | 111.69 | 92.35
2018-10-01 08:00 | 110.2 | 91.43
2018-10-01 08:30 | 117.49 | 99.26
2018-10-01 09:00 | 120.36 | 102.03
2018-10-01 09:30 | 117.56 | 97.64
2018-10-01 10:00 | 123.18 | 102.78
2018-10-01 10:30 | 120.25 | 100.08
2018-10-01 11:00 | 116.32 | 95.26
2018-10-01 11:30 | 111.07 | 88.7
2018-10-01 12:00 | 113.54 | 92.46
2018-10-01 12:30 | 108.76 | 86.09
2018-10-01 13:00 | 109.74 | 87.89
2018-10-01 13:30 | 110.59 | 91.12
2018-10-01 14:00 | 116.73 | 97.68
2018-10-01 14:30 | 113.73 | 93.42
2018-10-01 15:00 | 112.29 | 91.4
2018-10-01 15:30 | 117.83 | 97.71
2018-10-01 16:00 | 112.87 | 93.2
2018-10-01 16:30 | 119.12 | 98.47
2018-10-01 17:00 | 121.49 | 100.6
2018-10-01 17:30 | 122.02 | 100.73
2018-10-01 18:00 | 122.21 | 100.94
2018-10-01 18:30 | 118.31 | 95.55
2018-10-01 19:00 | 116.88 | 93.62
2018-10-01 19:30 | 123.97 | 100.32
2018-10-01 20:00 | 115.18 | 90.92
2018-10-01 20:30 | 119.14 | 95.98
2018-10-01 21:00 | 119.73 | 97.67
2018-10-01 21:30 | 115.63 | 93.48
2018-10-01 22:00 | 113.4 | 91.01
2018-10-01 22:30 | 124 | 101.54
2018-10-01 23:00 | 116.11 | 92.78
2018-10-01 23:30 | 113.58 | 90.32
2018-10-02 | 119.9 | 97.14
2018-10-02 00:30 | 118.59 | 95.52
2018-10-02 01:00 | 122.39 | 100.41
2018-10-02 01:30 | 122.14 | 101.35
2018-10-02 02:00 | 122.69 | 102.74
2018-10-02 02:30 | 120.25 | 99.11
2018-10-02 03:00 | 114.57 | 91.97
2018-10-02 03:30 | 113.83 | 90.58
2018-10-02 04:00 | 110.03 | 89.39
2018-10-02 04:30 | 108.86 | 89.04
2018-10-02 05:00 | 114.34 | 94.42
2018-10-02 05:30 | 118.88 | 99.48
2018-10-02 06:00 | 114.72 | 94.31
2018-10-02 06:30 | 112.24 | 91.52
2018-10-02 07:00 | 114.87 | 93.31
2018-10-02 07:30 | 122.79 | 102.28
2018-10-02 08:00 | 116.76 | 97.74
2018-10-02 08:30 | 109.27 | 91.81
2018-10-02 09:00 | 102.89 | 83.92
2018-10-02 09:30 | 111.39 | 91.44
2018-10-02 10:00 | 107.48 | 87.78
2018-10-02 10:30 | 106.42 | 86.87
2018-10-02 11:00 | 112.86 | 92.56
2018-10-02 11:30 | 111.86 | 91.69
2018-10-02 12:00 | 103.14 | 84.45
2018-10-02 12:30 | 101.94 | 83.46
2018-10-02 13:00 | 107.2 | 89.12
2018-10-02 13:30 | 109.4 | 91.56
2018-10-02 14:00 | 110.09 | 87.88
2018-10-02 14:30 | 106.24 | 84.29
2018-10-02 15:00 | 109.84 | 85.65
2018-10-02 15:30 | 111.65 | 86.71
2018-10-02 16:00 | 111.98 | 89.58
2018-10-02 16:30 | 114.09 | 92.33
2018-10-02 17:00 | 122.16 | 100.73
2018-10-02 17:30 | 120.53 | 99.54
2018-10-02 18:00 | 118.81 | 98.22
2018-10-02 18:30 | 112.04 | 89.17
2018-10-02 19:00 | 114.56 | 94.08
2018-10-02 19:30 | 117.07 | 96.26
2018-10-02 20:00 | 117.41 | 95.85
2018-10-02 20:30 | 120.95 | 100.15
2018-10-02 21:00 | 123.5 | 101.8
2018-10-02 21:30 | 125.83 | 102.1
2018-10-02 22:00 | 115.68 | 92.47
2018-10-02 22:30 | 125.94 | 102.77
2018-10-02 23:00 | 125.37 | 102.29
2018-10-02 23:30 | 121.16 | 97
2018-10-03 | 125.62 | 103.48
2018-10-03 00:30 | 118.5 | 94.54
2018-10-03 01:00 | 123.05 | 100.47
2018-10-03 01:30 | 118.91 | 95.27
2018-10-03 02:00 | 123.67 | 101.45
2018-10-03 02:30 | 122.28 | 99.07
2018-10-03 03:00 | 123.45 | 101.12
2018-10-03 03:30 | 120 | 98.51
2018-10-03 04:00 | 125.61 | 104.45
2018-10-03 04:30 | 126.3 | 105.38
2018-10-03 05:00 | 126.03 | 105.02
2018-10-03 05:30 | 120.43 | 99.25
2018-10-03 06:00 | 120.12 | 98.84
2018-10-03 06:30 | 116.17 | 94.03
2018-10-03 07:00 | 118.08 | 94.49
2018-10-03 07:30 | 126.58 | 103.95
2018-10-03 08:00 | 122.9 | 99.86
2018-10-03 08:30 | 119.79 | 96.35
2018-10-03 09:00 | 117.02 | 93.26
2018-10-03 09:30 | 121.83 | 98.89
2018-10-03 10:00 | 120.09 | 97.44
2018-10-03 10:30 | 118.28 | 97.42
2018-10-03 11:00 | 119.67 | 96.33
2018-10-03 11:30 | 114.42 | 89.64
2018-10-03 12:00 | 116.04 | 92.38
2018-10-03 12:30 | 114.48 | 90.51
2018-10-03 13:00 | 117.54 | 94.98
2018-10-03 13:30 | 120.77 | 98.09
2018-10-03 14:00 | 126.23 | 103.68
2018-10-03 14:30 | 123.96 | 101.44
2018-10-03 15:00 | 119.35 | 95.84
2018-10-03 15:30 | 122.08 | 98.47
2018-10-03 16:00 | 122.25 | 98.73
2018-10-03 16:30 | 123.12 | 100.08
2018-10-03 17:00 | 124.66 | 103.49
2018-10-03 17:30 | 119.42 | 99.26
2018-10-03 18:00 | 121.99 | 102.83
2018-10-03 18:30 | 123.42 | 103.81
2018-10-03 19:00 | 129.27 | 109
2018-10-03 19:30 | 135.08 | 113.14
2018-10-03 20:00 | 130.49 | 108.82
2018-10-03 20:30 | 129.62 | 108.09
2018-10-03 21:00 | 125.86 | 104.69
2018-10-03 21:30 | 124.73 | 103.47
2018-10-03 22:00 | 123.53 | 102.58
2018-10-03 22:30 | 118.63 | 97.48
2018-10-03 23:00 | 120.23 | 99.12
2018-10-03 23:30 | 122.18 | 102.52
2018-10-04 | 123.49 | 103.4
2018-10-04 00:30 | 126.59 | 107.12
2018-10-04 01:00 | 123.04 | 103.7
2018-10-04 01:30 | 122.72 | 102.53
2018-10-04 02:00 | 131.04 | 111.08
2018-10-04 02:30 | 131.47 | 110.89
2018-10-04 03:00 | 130.49 | 109.61
2018-10-04 03:30 | 120.19 | 98.32
2018-10-04 04:00 | 118.97 | 97.66
2018-10-04 04:30 | 115.01 | 94.55
2018-10-04 05:00 | 112.62 | 91.07
2018-10-04 05:30 | 117.32 | 95.72
2018-10-04 06:00 | 114.59 | 93.15
2018-10-04 06:30 | 114.82 | 91.96
2018-10-04 07:00 | 119.15 | 96.53
2018-10-04 07:30 | 114.11 | 93.13
2018-10-04 08:00 | 113.68 | 89.39
2018-10-04 08:30 | 120.64 | 96.96
2018-10-04 09:00 | 123.67 | 100.89
2018-10-04 09:30 | 110.26 | 86.86
2018-10-04 10:00 | 109.24 | 84.52
2018-10-04 10:30 | 108.65 | 84.84
2018-10-04 11:00 | 111.38 | 89.04
2018-10-04 11:30 | 114.52 | 90.2
2018-10-04 12:00 | 115.79 | 91.86
2018-10-04 12:30 | 116.75 | 92.52
2018-10-04 13:00 | 113.02 | 86.24
2018-10-04 13:30 | 116.56 | 89.9
2018-10-04 14:00 | 116.36 | 89.7
2018-10-04 14:30 | 125.86 | 99.73
2018-10-04 15:00 | 118.39 | 92.36
2018-10-04 15:30 | 118.12 | 94.37
2018-10-04 16:00 | 124.44 | 99.47
2018-10-04 16:30 | 125.37 | 101.07
2018-10-04 17:00 | 122.82 | 98.6
2018-10-04 17:30 | 123.83 | 99.59
2018-10-04 18:00 | 120.63 | 95.65
2018-10-04 18:30 | 119.93 | 96.43
2018-10-04 19:00 | 124.97 | 100.72
2018-10-04 19:30 | 125.77 | 102.22
2018-10-04 20:00 | 130.84 | 107.31
2018-10-04 20:30 | 135.33 | 111.48
2018-10-04 21:00 | 129.85 | 104.98
2018-10-04 21:30 | 126.9 | 100.61
2018-10-04 22:00 | 133.09 | 108.66
2018-10-04 22:30 | 132.79 | 109.5
2018-10-04 23:00 | 126.02 | 103.16
2018-10-04 23:30 | 119.26 | 97.01
2018-10-05 | 124.68 | 103.52
2018-10-05 00:30 | 127.28 | 103.82
2018-10-05 01:00 | 123.32 | 99.17
2018-10-05 01:30 | 118.43 | 93.02
2018-10-05 02:00 | 121.25 | 97.07
2018-10-05 02:30 | 122.9 | 98.7
2018-10-05 03:00 | 122.58 | 99.23
2018-10-05 03:30 | 123.13 | 100.36
2018-10-05 04:00 | 126.25 | 104.88
2018-10-05 04:30 | 132.04 | 112.28
2018-10-05 05:00 | 131.87 | 111.63
2018-10-05 05:30 | 125 | 103.32
2018-10-05 06:00 | 126.25 | 104.34
2018-10-05 06:30 | 116.75 | 93.54
2018-10-05 07:00 | 124.89 | 103.76
2018-10-05 07:30 | 123.05 | 103.11
2018-10-05 08:00 | 121.68 | 100.79
2018-10-05 08:30 | 129.87 | 112.44
2018-10-05 09:00 | 133.76 | 115.62
2018-10-05 09:30 | 135.24 | 115.3
2018-10-05 10:00 | 135.47 | 116.17
2018-10-05 10:30 | 130.24 | 109.86
2018-10-05 11:00 | 127.43 | 106.96
2018-10-05 11:30 | 132.92 | 112.87
2018-10-05 12:00 | 129.46 | 107.86
2018-10-05 12:30 | 134.79 | 114.01
2018-10-05 13:00 | 133.44 | 112.34
2018-10-05 13:30 | 131.72 | 109.49
2018-10-05 14:00 | 129.82 | 106.75
2018-10-05 14:30 | 137.37 | 114.99
2018-10-05 15:00 | 132.9 | 110.17
2018-10-05 15:30 | 137.25 | 116.3
2018-10-05 16:00 | 139.28 | 118.1
2018-10-05 16:30 | 147.28 | 125.41
2018-10-05 17:00 | 144.34 | 122.57
2018-10-05 17:30 | 151.13 | 130.79
2018-10-05 18:00 | 145.81 | 124.82
2018-10-05 18:30 | 139.28 | 117.53
2018-10-05 19:00 | 142.03 | 119.48
2018-10-05 19:30 | 144.34 | 121.12
2018-10-05 20:00 | 147.14 | 123.71
2018-10-05 20:30 | 146.9 | 124.35
2018-10-05 21:00 | 145.47 | 123.85
2018-10-05 21:30 | 144.73 | 122.63
2018-10-05 22:00 | 135.82 | 115.1
2018-10-05 22:30 | 134.36 | 114.83
2018-10-05 23:00 | 135.54 | 115.12
2018-10-05 23:30 | 135.65 | 116.94
2018-10-06 | 138.82 | 121.44
2018-10-06 00:30 | 135.36 | 117.45
2018-10-06 01:00 | 130.47 | 112.41
2018-10-06 01:30 | 129.46 | 111.09
2018-10-06 02:00 | 128.08 | 110.05
2018-10-06 02:30 | 125.64 | 106.4
2018-10-06 03:00 | 127.04 | 107.31
2018-10-06 03:30 | 129.89 | 110.29
2018-10-06 04:00 | 120.77 | 101.17
2018-10-06 04:30 | 121.34 | 102.83
2018-10-06 05:00 | 120.04 | 101.4
2018-10-06 05:30 | 127.04 | 108.61
2018-10-06 06:00 | 128.52 | 110.72
2018-10-06 06:30 | 120.11 | 102.15
2018-10-06 07:00 | 124.01 | 106.7
2018-10-06 07:30 | 125.76 | 108.42
2018-10-06 08:00 | 125.58 | 107.72
2018-10-06 08:30 | 125.24 | 106.18
2018-10-06 09:00 | 125.12 | 107.31
2018-10-06 09:30 | 123.25 | 104.45
2018-10-06 10:00 | 128.95 | 111.45
2018-10-06 10:30 | 131.82 | 114.59
2018-10-06 11:00 | 127.71 | 109.06
2018-10-06 11:30 | 124.85 | 105.25
2018-10-06 12:00 | 124.36 | 105.55
2018-10-06 12:30 | 127.03 | 106.94
2018-10-06 13:00 | 129.52 | 110.08
2018-10-06 13:30 | 130.62 | 110.38
2018-10-06 14:00 | 129.94 | 110.17
2018-10-06 14:30 | 130.96 | 112.14
2018-10-06 15:00 | 129.52 | 110.99
2018-10-06 15:30 | 128.02 | 109.83
2018-10-06 16:00 | 132.95 | 114.23
2018-10-06 16:30 | 138.26 | 118.3
2018-10-06 17:00 | 136.13 | 115.86
2018-10-06 17:30 | 142.19 | 122.14
2018-10-06 18:00 | 133.76 | 112.54
2018-10-06 18:30 | 134.13 | 112.41
2018-10-06 19:00 | 147.65 | 127.49
2018-10-06 19:30 | 136.18 | 115.86
2018-10-06 20:00 | 137.5 | 115.96
2018-10-06 20:30 | 140.6 | 120.36
2018-10-06 21:00 | 134.42 | 114.51
2018-10-06 21:30 | 133.74 | 114.49
2018-10-06 22:00 | 135.27 | 116.48
2018-10-06 22:30 | 129.46 | 111.54
2018-10-06 23:00 | 129.2 | 111.46
2018-10-06 23:30 | 129.75 | 112.85
2018-10-07 | 132.95 | 115.37
2018-10-07 00:30 | 124.04 | 106.29
2018-10-07 01:00 | 123.1 | 105.06
2018-10-07 01:30 | 126.84 | 109.57
2018-10-07 02:00 | 129.8 | 111.96
2018-10-07 02:30 | 125.1 | 107.59
2018-10-07 03:00 | 120.96 | 102.94
2018-10-07 03:30 | 118.9 | 99.42
2018-10-07 04:00 | 122.3 | 104.85
2018-10-07 04:30 | 124.64 | 107.05
2018-10-07 05:00 | 125.37 | 107.54
2018-10-07 05:30 | 131.8 | 114.46
2018-10-07 06:00 | 120 | 102.49
2018-10-07 06:30 | 114.19 | 96.78
2018-10-07 07:00 | 121.85 | 104.79
2018-10-07 07:30 | 132.92 | 116.42
2018-10-07 08:00 | 122.42 | 104.6
2018-10-07 08:30 | 126.62 | 108.77
2018-10-07 09:00 | 122.45 | 104.69
2018-10-07 09:30 | 123.39 | 105.15
2018-10-07 10:00 | 124.88 | 105.28
2018-10-07 10:30 | 126.44 | 105.82
2018-10-07 11:00 | 131.24 | 112.1
2018-10-07 11:30 | 136.6 | 117.51
2018-10-07 12:00 | 134.74 | 114.35
2018-10-07 12:30 | 142.12 | 121.53
2018-10-07 13:00 | 139.29 | 119.12
2018-10-07 13:30 | 138.41 | 118.4
2018-10-07 14:00 | 131.34 | 110.79
2018-10-07 14:30 | 135.44 | 114.04
2018-10-07 15:00 | 135.87 | 115.54
2018-10-07 15:30 | 129.99 | 109.29
2018-10-07 16:00 | 138.86 | 118.45
2018-10-07 16:30 | 143.07 | 123.98
2018-10-07 17:00 | 142.31 | 121.98
2018-10-07 17:30 | 143.91 | 123.22
2018-10-07 18:00 | 142.34 | 121.54
2018-10-07 18:30 | 135.74 | 111.73
2018-10-07 19:00 | 141.47 | 117.98
2018-10-07 19:30 | 142.86 | 118.81
2018-10-07 20:00 | 138.15 | 115.43
2018-10-07 20:30 | 144.47 | 122.26
2018-10-07 21:00 | 133.42 | 111.92
2018-10-07 21:30 | 134.07 | 114.29
2018-10-07 22:00 | 131.59 | 112.07
2018-10-07 22:30 | 122.26 | 102.44
2018-10-07 23:00 | 123.36 | 103.28
2018-10-07 23:30 | 116.73 | 96.9
2018-10-08 | 125.18 | 108.13
2018-10-08 00:30 | 122.92 | 105.38
2018-10-08 01:00 | 116.24 | 98.84
2018-10-08 01:30 | 120.67 | 103
2018-10-08 02:00 | 130.76 | 114.87
2018-10-08 02:30 | 124.34 | 109.39
2018-10-08 03:00 | 118.36 | 102.36
2018-10-08 03:30 | 115.31 | 98.87
2018-10-08 04:00 | 123.79 | 106.27
2018-10-08 04:30 | 122.11 | 104.79
2018-10-08 05:00 | 123.79 | 103.83
2018-10-08 05:30 | 125.62 | 106
2018-10-08 06:00 | 124.23 | 104.27
2018-10-08 06:30 | 125.13 | 106.02
2018-10-08 07:00 | 120.7 | 100.95
2018-10-08 07:30 | 122.91 | 103.45
2018-10-08 08:00 | 129.21 | 109.46
2018-10-08 08:30 | 129.74 | 108.92
2018-10-08 09:00 | 133.52 | 113.33
2018-10-08 09:30 | 122.31 | 102.04
2018-10-08 10:00 | 122.19 | 99.74
2018-10-08 10:30 | 129.02 | 108.77
2018-10-08 11:00 | 125.77 | 103.46
2018-10-08 11:30 | 123.97 | 101.37
2018-10-08 12:00 | 129.13 | 106.82
2018-10-08 12:30 | 133.12 | 111.56
2018-10-08 13:00 | 134.63 | 113.23
2018-10-08 13:30 | 126.93 | 102.87
2018-10-08 14:00 | 131.24 | 107.24
2018-10-08 14:30 | 132.99 | 107.51
2018-10-08 15:00 | 135.63 | 109.13
2018-10-08 15:30 | 136.99 | 111.1
2018-10-08 16:00 | 138.01 | 112.59
2018-10-08 16:30 | 140.17 | 115.45
2018-10-08 17:00 | 146.61 | 121.43
2018-10-08 17:30 | 143.23 | 118.51
2018-10-08 18:00 | 147 | 123
2018-10-08 18:30 | 140.42 | 114.1
2018-10-08 19:00 | 145.95 | 119.22
2018-10-08 19:30 | 147.05 | 120.28
2018-10-08 20:00 | 146.69 | 119.18
2018-10-08 20:30 | 143.32 | 118.4
2018-10-08 21:00 | 143.59 | 120.03
2018-10-08 21:30 | 137.34 | 112.48
2018-10-08 22:00 | 126.8 | 101.91
2018-10-08 22:30 | 133.45 | 110.03
2018-10-08 23:00 | 129.86 | 108.17
2018-10-08 23:30 | 129.86 | 108.74
2018-10-09 | 136.51 | 115.68
2018-10-09 00:30 | 134.66 | 114.61
2018-10-09 01:00 | 138.43 | 118.26
2018-10-09 01:30 | 137.78 | 117.16
2018-10-09 02:00 | 130.8 | 111.56
2018-10-09 02:30 | 129.32 | 107.98
2018-10-09 03:00 | 127.5 | 106.66
2018-10-09 03:30 | 131.43 | 111
2018-10-09 04:00 | 131.54 | 111.74
2018-10-09 04:30 | 126 | 105.25
2018-10-09 05:00 | 123.23 | 102.5
2018-10-09 05:30 | 127.28 | 107.07
2018-10-09 06:00 | 124.68 | 104.41
2018-10-09 06:30 | 123.41 | 103.01
2018-10-09 07:00 | 120.69 | 101.52
2018-10-09 07:30 | 130.79 | 112.68
2018-10-09 08:00 | 126.94 | 108.37
2018-10-09 08:30 | 130.61 | 110.56
2018-10-09 09:00 | 129.12 | 108.44
2018-10-09 09:30 | 114.14 | 94.34
2018-10-09 10:00 | 112.52 | 89.45
2018-10-09 10:30 | 118.23 | 95.65
2018-10-09 11:00 | 111.17 | 88.24
2018-10-09 11:30 | 113.71 | 89.61
2018-10-09 12:00 | 119.61 | 95.88
2018-10-09 12:30 | 104.93 | 77.73
2018-10-09 13:00 | 101.47 | 74.51
2018-10-09 13:30 | 111 | 86.87
2018-10-09 14:00 | 118.08 | 93.1
2018-10-09 14:30 | 116.21 | 90.43
2018-10-09 15:00 | 116.61 | 91.64
2018-10-09 15:30 | 116.66 | 90.85
2018-10-09 16:00 | 121.48 | 95.65
2018-10-09 16:30 | 122.53 | 96.47
2018-10-09 17:00 | 112.32 | 83.58
2018-10-09 17:30 | 123.18 | 92.53
2018-10-09 18:00 | 124.1 | 95.56
2018-10-09 18:30 | 116.86 | 86.91
2018-10-09 19:00 | 118.28 | 88.89
2018-10-09 19:30 | 126.79 | 97.87
2018-10-09 20:00 | 126.25 | 96.47
2018-10-09 20:30 | 124.05 | 94.49
2018-10-09 21:00 | 128.32 | 98.96
2018-10-09 21:30 | 128.93 | 99.83
2018-10-09 22:00 | 126.64 | 97.59
2018-10-09 22:30 | 128.75 | 99.82
2018-10-09 23:00 | 122.47 | 92.73
2018-10-09 23:30 | 123.79 | 93.78
2018-10-10 | 134.75 | 106.52
2018-10-10 00:30 | 131.98 | 102.9
2018-10-10 01:00 | 127.39 | 97.55
2018-10-10 01:30 | 121.57 | 91.44
2018-10-10 02:00 | 123.45 | 94.67
2018-10-10 02:30 | 122.91 | 94.33
2018-10-10 03:00 | 120.23 | 91.18
2018-10-10 03:30 | 121.3 | 92.93
2018-10-10 04:00 | 122.34 | 92.9
2018-10-10 04:30 | 120.69 | 90
2018-10-10 05:00 | 124.95 | 94.18
2018-10-10 05:30 | 126.02 | 94.5
2018-10-10 06:00 | 121.87 | 90.47
2018-10-10 06:30 | 122.81 | 90.53
2018-10-10 07:00 | 126.5 | 95.34
2018-10-10 07:30 | 127.58 | 96.45
2018-10-10 08:00 | 124.65 | 92.72
2018-10-10 08:30 | 120.4 | 86.88
2018-10-10 09:00 | 122.49 | 85.77
2018-10-10 09:30 | 120.52 | 83.72
2018-10-10 10:00 | 127.46 | 89.92
2018-10-10 10:30 | 126.6 | 86.79
2018-10-10 11:00 | 124.24 | 85.03
2018-10-10 11:30 | 122.99 | 85.39
2018-10-10 12:00 | 122.92 | 85.3
2018-10-10 12:30 | 114.98 | 80.61
2018-10-10 13:00 | 122.1 | 83.76
2018-10-10 13:30 | 120.94 | 82.37
2018-10-10 14:00 | 124.86 | 90.45
2018-10-10 14:30 | 127.13 | 90.72
2018-10-10 15:00 | 130.3 | 95.42
2018-10-10 15:30 | 133.23 | 101.81
2018-10-10 16:00 | 126.47 | 92.77
2018-10-10 16:30 | 128.58 | 96.2
2018-10-10 17:00 | 124.2 | 93.73
2018-10-10 17:30 | 114.28 | 80.11
2018-10-10 18:00 | 115.64 | 80.97
2018-10-10 18:30 | 118.92 | 84.02
2018-10-10 19:00 | 125.87 | 91.62
2018-10-10 19:30 | 129.37 | 95.6
2018-10-10 20:00 | 120.41 | 84.81
2018-10-10 20:30 | 116.28 | 83.2
2018-10-10 21:00 | 111.5 | 77.3
2018-10-10 21:30 | 108.44 | 74.64
2018-10-10 22:00 | 108.42 | 76.14
2018-10-10 22:30 | 113.64 | 81.05
2018-10-10 23:00 | 110.94 | 76.93
2018-10-10 23:30 | 109.61 | 75.28
2018-10-11 | 107.74 | 73.58
2018-10-11 00:30 | 107.35 | 71.88
2018-10-11 01:00 | 110.28 | 75.12
2018-10-11 01:30 | 106.63 | 74.3
2018-10-11 02:00 | 104.78 | 74.9
2018-10-11 02:30 | 110.15 | 80.79
2018-10-11 03:00 | 105.37 | 74.4
2018-10-11 03:30 | 104.03 | 72.2
2018-10-11 04:00 | 106.06 | 74.63
2018-10-11 04:30 | 105.4 | 73.6
2018-10-11 05:00 | 105.41 | 73.65
2018-10-11 05:30 | 107.02 | 75.36
2018-10-11 06:00 | 104.73 | 72.84
2018-10-11 06:30 | 100.07 | 69.27
2018-10-11 07:00 | 101.42 | 70.1
2018-10-11 07:30 | 102.79 | 71.91
2018-10-11 08:00 | 104.16 | 72.4
2018-10-11 08:30 | 97.09 | 64.43
2018-10-11 09:00 | 101.19 | 69.33
2018-10-11 09:30 | 92.82 | 61.59
2018-10-11 10:00 | 94.23 | 66.2
2018-10-11 10:30 | 94.7 | 67.9
2018-10-11 11:00 | 101.74 | 75.45
2018-10-11 11:30 | 98.75 | 72.35
2018-10-11 12:00 | 105.81 | 83.75
2018-10-11 12:30 | 110.92 | 89.6
2018-10-11 13:00 | 109.39 | 84.43
2018-10-11 13:30 | 95.99 | 66.36
2018-10-11 14:00 | 102.62 | 71.84
2018-10-11 14:30 | 110.33 | 81.84
2018-10-11 15:00 | 114.51 | 89.18
2018-10-11 15:30 | 123.27 | 98.91
2018-10-11 16:00 | 127.52 | 103.24
2018-10-11 16:30 | 132.27 | 109.14
2018-10-11 17:00 | 127.98 | 105.14
2018-10-11 17:30 | 119.45 | 95.21
2018-10-11 18:00 | 107.22 | 80.04
2018-10-11 18:30 | 87.01 | 60.98
2018-10-11 19:00 | 79.87 | 53.26
2018-10-11 19:30 | 82.74 | 54.47
2018-10-11 20:00 | 92.3 | 64.27
2018-10-11 20:30 | 94.74 | 65.14
2018-10-11 21:00 | 95.07 | 64.89
2018-10-11 21:30 | 99.05 | 70.35
2018-10-11 22:00 | 100.8 | 73.18
2018-10-11 22:30 | 102.3 | 72.25
2018-10-11 23:00 | 105.2 | 76.15
2018-10-11 23:30 | 102.55 | 75.84
2018-10-12 | 109.53 | 83.64
2018-10-12 00:30 | 107.66 | 82.79
2018-10-12 01:00 | 112.43 | 84.9
2018-10-12 01:30 | 113.73 | 87.09
2018-10-12 02:00 | 114.61 | 89.68
2018-10-12 02:30 | 117.43 | 92.99
2018-10-12 03:00 | 122.21 | 97.59
2018-10-12 03:30 | 111.48 | 84.85
2018-10-12 04:00 | 114 | 87.66
2018-10-12 04:30 | 113.49 | 88.56
2018-10-12 05:00 | 104.14 | 78.3
2018-10-12 05:30 | 109.74 | 83.34
2018-10-12 06:00 | 114.54 | 88.49
2018-10-12 06:30 | 115.65 | 88.25
2018-10-12 07:00 | 109.9 | 82.88
2018-10-12 07:30 | 114.55 | 88.82
2018-10-12 08:00 | 107.75 | 80.79
2018-10-12 08:30 | 111.86 | 86.08
2018-10-12 09:00 | 116.01 | 92.44
2018-10-12 09:30 | 116.15 | 92.81
2018-10-12 10:00 | 106.1 | 83.24
2018-10-12 10:30 | 105.26 | 84.27
2018-10-12 11:00 | 101.4 | 77.82
2018-10-12 11:30 | 113.13 | 91.1
2018-10-12 12:00 | 108.41 | 85.52
2018-10-12 12:30 | 105.72 | 87.03
2018-10-12 13:00 | 98.23 | 81.32
2018-10-12 13:30 | 101.88 | 85.35
2018-10-12 14:00 | 104.27 | 87.68
2018-10-12 14:30 | 98.55 | 81.96
2018-10-12 15:00 | 92.74 | 75.52
2018-10-12 15:30 | 101.04 | 84.63
2018-10-12 16:00 | 103.26 | 86.8
2018-10-12 16:30 | 95.95 | 78.02
2018-10-12 17:00 | 97.73 | 80.11
2018-10-12 17:30 | 99.73 | 82.75
2018-10-12 18:00 | 95.77 | 77.72
2018-10-12 18:30 | 90.96 | 72.36
2018-10-12 19:00 | 97.59 | 78.88
2018-10-12 19:30 | 99 | 80.23
2018-10-12 20:00 | 90.22 | 69.53
2018-10-12 20:30 | 98.51 | 78.53
2018-10-12 21:00 | 108.14 | 88.84
2018-10-12 21:30 | 106.43 | 86.31
2018-10-12 22:00 | 69.56 | 37.67
2018-10-12 22:30 | 68.45 | 37.36
2018-10-12 23:00 | 72.04 | 43.48
2018-10-12 23:30 | 75.18 | 47.9
2018-10-13 | 78.86 | 53.22
2018-10-13 00:30 | 81.03 | 56.43
2018-10-13 01:00 | 77.06 | 51.82
2018-10-13 01:30 | 75.03 | 48.9
2018-10-13 02:00 | 76.51 | 50.46
2018-10-13 02:30 | 78.46 | 53.1
2018-10-13 03:00 | 81.64 | 57.35
2018-10-13 03:30 | 86.26 | 62.82
2018-10-13 04:00 | 90.78 | 67.49
2018-10-13 04:30 | 87.12 | 63.01
2018-10-13 05:00 | 90.28 | 66.83
2018-10-13 05:30 | 97.15 | 73.67
2018-10-13 06:00 | 93.62 | 70.1
2018-10-13 06:30 | 90.26 | 65.44
2018-10-13 07:00 | 99.16 | 75.79
2018-10-13 07:30 | 98 | 74.36
2018-10-13 08:00 | 98.47 | 74.23
2018-10-13 08:30 | 106.46 | 84.3
2018-10-13 09:00 | 103.4 | 80.65
2018-10-13 09:30 | 106.06 | 83.59
2018-10-13 10:00 | 101.69 | 79.09
2018-10-13 10:30 | 95.6 | 70.87
2018-10-13 11:00 | 103.42 | 80.14
2018-10-13 11:30 | 97.26 | 72.71
2018-10-13 12:00 | 102.22 | 79.16
2018-10-13 12:30 | 102.36 | 78.5
2018-10-13 13:00 | 107.55 | 83.84
2018-10-13 13:30 | 106.25 | 83.34
2018-10-13 14:00 | 96.96 | 74.12
2018-10-13 14:30 | 97.74 | 74.6
2018-10-13 15:00 | 97.51 | 73.35
2018-10-13 15:30 | 94.27 | 70.09
2018-10-13 16:00 | 94.14 | 70.59
2018-10-13 16:30 | 100.43 | 78.2
2018-10-13 17:00 | 100.94 | 77.91
2018-10-13 17:30 | 105.75 | 83.46
2018-10-13 18:00 | 101.97 | 79.53
2018-10-13 18:30 | 100.5 | 78.13
2018-10-13 19:00 | 101.71 | 80.32
2018-10-13 19:30 | 100.29 | 78.66
2018-10-13 20:00 | 104.22 | 83.62
2018-10-13 20:30 | 101.02 | 79.13
2018-10-13 21:00 | 102.47 | 81.07
2018-10-13 21:30 | 95.26 | 73.28
2018-10-13 22:00 | 96.41 | 74.92
2018-10-13 22:30 | 101.99 | 81.55
2018-10-13 23:00 | 104.03 | 83.18
2018-10-13 23:30 | 103 | 82.38
2018-10-14 | 103.31 | 82.9
2018-10-14 00:30 | 97.97 | 76.69
2018-10-14 01:00 | 107.47 | 85.76
2018-10-14 01:30 | 107.2 | 85.93
2018-10-14 02:00 | 99.13 | 76.45
2018-10-14 02:30 | 96.33 | 73.16
2018-10-14 03:00 | 102.86 | 81.58
2018-10-14 03:30 | 104.49 | 83.91
2018-10-14 04:00 | 111.55 | 91.61
2018-10-14 04:30 | 110.65 | 90.7
2018-10-14 05:00 | 110.32 | 90.36
2018-10-14 05:30 | 105.39 | 85.58
2018-10-14 06:00 | 103.69 | 84.68
2018-10-14 06:30 | 101.24 | 81.39
2018-10-14 07:00 | 100.88 | 80.92
2018-10-14 07:30 | 105.26 | 85.28
2018-10-14 08:00 | 107.24 | 88.61
2018-10-14 08:30 | 109.35 | 89.59
2018-10-14 09:00 | 102.37 | 81.74
2018-10-14 09:30 | 100.02 | 79.46
2018-10-14 10:00 | 101.86 | 81.49
2018-10-14 10:30 | 102.44 | 82.33
2018-10-14 11:00 | 100.37 | 81.08
2018-10-14 11:30 | 100.28 | 80.21
2018-10-14 12:00 | 105.88 | 85.77
2018-10-14 12:30 | 100.02 | 79.33
2018-10-14 13:00 | 102.33 | 81.35
2018-10-14 13:30 | 99.84 | 78.53
2018-10-14 14:00 | 90.95 | 73.33
2018-10-14 14:30 | 88.78 | 71.52
2018-10-14 15:00 | 98.44 | 82.33
2018-10-14 15:30 | 95.1 | 77.71
2018-10-14 16:00 | 100.3 | 81.95
2018-10-14 16:30 | 97.84 | 79.79
2018-10-14 17:00 | 103.66 | 86.35
2018-10-14 17:30 | 101.44 | 83.97
2018-10-14 18:00 | 101.42 | 82.44
2018-10-14 18:30 | 105.96 | 85.9
2018-10-14 19:00 | 117.61 | 96.83
2018-10-14 19:30 | 117.13 | 96.79
2018-10-14 20:00 | 116.7 | 94.7
2018-10-14 20:30 | 110.34 | 89.33
2018-10-14 21:00 | 121.7 | 97.31
2018-10-14 21:30 | 134.98 | 110.85
2018-10-14 22:00 | 127.48 | 101.77
2018-10-14 22:30 | 129.47 | 103.28
2018-10-14 23:00 | 128.85 | 103.07
2018-10-14 23:30 | 120.94 | 95.83
2018-10-15 | 124.52 | 99.33
2018-10-15 00:30 | 123.01 | 98.25
2018-10-15 01:00 | 122.76 | 97.45
2018-10-15 01:30 | 129.12 | 104.62
2018-10-15 02:00 | 131.12 | 106.99
2018-10-15 02:30 | 133.26 | 108.66
2018-10-15 03:00 | 120.46 | 93.71
2018-10-15 03:30 | 124.5 | 98.52
2018-10-15 04:00 | 119.61 | 94.25
2018-10-15 04:30 | 123.53 | 98.12
2018-10-15 05:00 | 123.88 | 99.23
2018-10-15 05:30 | 128.17 | 105.33
2018-10-15 06:00 | 124.44 | 103.16
2018-10-15 06:30 | 111.76 | 90.01
2018-10-15 07:00 | 105.42 | 83.18
2018-10-15 07:30 | 112.51 | 90.4
2018-10-15 08:00 | 115.99 | 93.25
2018-10-15 08:30 | 118.94 | 94.87
2018-10-15 09:00 | 112.05 | 86.18
2018-10-15 09:30 | 120.75 | 95.13
2018-10-15 10:00 | 127.03 | 102.66
2018-10-15 10:30 | 122.53 | 97.38
2018-10-15 11:00 | 118.45 | 92.95
2018-10-15 11:30 | 121.02 | 95.35
2018-10-15 12:00 | 121.83 | 96.15
2018-10-15 12:30 | 121.25 | 95.48
2018-10-15 13:00 | 117.34 | 92.19
2018-10-15 13:30 | 122.53 | 98.43
2018-10-15 14:00 | 124.74 | 101.4
2018-10-15 14:30 | 124.61 | 101.09
2018-10-15 15:00 | 121.83 | 97.77
2018-10-15 15:30 | 135.29 | 112.48
2018-10-15 16:00 | 137.76 | 112.67
2018-10-15 16:30 | 127.61 | 102.62
2018-10-15 17:00 | 120.2 | 93.98
2018-10-15 17:30 | 126.02 | 98.81
2018-10-15 18:00 | 125.19 | 97.85
2018-10-15 18:30 | 130.48 | 103.18
2018-10-15 19:00 | 139.42 | 113.4
2018-10-15 19:30 | 123.15 | 98.63
2018-10-15 20:00 | 123.93 | 100.34
2018-10-15 20:30 | 129.21 | 105.36
2018-10-15 21:00 | 120.53 | 95.53
2018-10-15 21:30 | 122.1 | 96.88
2018-10-15 22:00 | 120.24 | 94.68
2018-10-15 22:30 | 126.6 | 100.68
2018-10-15 23:00 | 124.69 | 98.91
2018-10-15 23:30 | 127.96 | 101.39
2018-10-16 | 124.39 | 97.62
2018-10-16 00:30 | 126.57 | 99.25
2018-10-16 01:00 | 125.27 | 99.17
2018-10-16 01:30 | 128 | 103.15
2018-10-16 02:00 | 128.02 | 103.02
2018-10-16 02:30 | 126.6 | 102.54
2018-10-16 03:00 | 124.74 | 100.55
2018-10-16 03:30 | 127.78 | 104.15
2018-10-16 04:00 | 126.48 | 102.73
2018-10-16 04:30 | 120.26 | 96.69
2018-10-16 05:00 | 124.49 | 101.13
2018-10-16 05:30 | 132.38 | 108.03
2018-10-16 06:00 | 123.4 | 98.85
2018-10-16 06:30 | 121.08 | 96.7
2018-10-16 07:00 | 125.82 | 100.95
2018-10-16 07:30 | 120.94 | 92.5
2018-10-16 08:00 | 129.14 | 100.87
2018-10-16 08:30 | 121.13 | 96.12
2018-10-16 09:00 | 108.05 | 81.58
2018-10-16 09:30 | 113.74 | 83.79
2018-10-16 10:00 | 121.73 | 90.79
2018-10-16 10:30 | 117.24 | 87.67
2018-10-16 11:00 | 116.01 | 86.1
2018-10-16 11:30 | 118.14 | 90.11
2018-10-16 12:00 | 131.71 | 100.99
2018-10-16 12:30 | 135.64 | 105.82
2018-10-16 13:00 | 126.04 | 93.06
2018-10-16 13:30 | 134.71 | 106.24
2018-10-16 14:00 | 127.7 | 98.44
2018-10-16 14:30 | 128.63 | 99.46
2018-10-16 15:00 | 131.39 | 102.63
2018-10-16 15:30 | 126.98 | 95.83
2018-10-16 16:00 | 126.98 | 99.85
2018-10-16 16:30 | 133.1 | 103.85
2018-10-16 17:00 | 138.41 | 109.81
2018-10-16 17:30 | 136.95 | 109.55
2018-10-16 18:00 | 142.47 | 116.44
2018-10-16 18:30 | 136.16 | 107.45
2018-10-16 19:00 | 137.45 | 109.87
2018-10-16 19:30 | 141.64 | 114.12
2018-10-16 20:00 | 137.54 | 110.58
2018-10-16 20:30 | 142.05 | 116.12
2018-10-16 21:00 | 138.09 | 113.18
2018-10-16 21:30 | 138.94 | 113.16
2018-10-16 22:00 | 134.31 | 108.3
2018-10-16 22:30 | 133.49 | 107.06
2018-10-16 23:00 | 127.73 | 101.11
2018-10-16 23:30 | 127.28 | 102.76
2018-10-17 | 126.88 | 102.03
2018-10-17 00:30 | 133.71 | 109.4
2018-10-17 01:00 | 131.61 | 106.85
2018-10-17 01:30 | 137.35 | 113.68
2018-10-17 02:00 | 131.74 | 108.43
2018-10-17 02:30 | 131.24 | 106.75
2018-10-17 03:00 | 132.75 | 107.79
2018-10-17 03:30 | 134.15 | 108.5
2018-10-17 04:00 | 129.29 | 104.56
2018-10-17 04:30 | 133.06 | 109.14
2018-10-17 05:00 | 132.87 | 110.07
2018-10-17 05:30 | 131.47 | 106.35
2018-10-17 06:00 | 129.13 | 103.68
2018-10-17 06:30 | 111.84 | 86.51
2018-10-17 07:00 | 112.54 | 87.73
2018-10-17 07:30 | 124.28 | 99.55
2018-10-17 08:00 | 115.99 | 88.81
2018-10-17 08:30 | 113.23 | 87.07
2018-10-17 09:00 | 104.09 | 78.36
2018-10-17 09:30 | 100.9 | 73.28
2018-10-17 10:00 | 102.53 | 74.23
2018-10-17 10:30 | 99.9 | 71.74
2018-10-17 11:00 | 108.02 | 79.3
2018-10-17 11:30 | 103.57 | 74.31
2018-10-17 12:00 | 104.77 | 76.23
2018-10-17 12:30 | 110.29 | 81.95
2018-10-17 13:00 | 110.54 | 83.84
2018-10-17 13:30 | 109.4 | 82.15
2018-10-17 14:00 | 115.31 | 88.41
2018-10-17 14:30 | 114.59 | 87.64
2018-10-17 15:00 | 107.56 | 80.26
2018-10-17 15:30 | 114.06 | 86.94
2018-10-17 16:00 | 114.22 | 87.48
2018-10-17 16:30 | 108.02 | 79.64
2018-10-17 17:00 | 113.25 | 85.86
2018-10-17 17:30 | 117.41 | 93.7
2018-10-17 18:00 | 114.31 | 92.11
2018-10-17 18:30 | 112.59 | 89.45
2018-10-17 19:00 | 115.66 | 92.2
2018-10-17 19:30 | 118.11 | 95.47
2018-10-17 20:00 | 115.09 | 91.4
2018-10-17 20:30 | 119.22 | 94.63
2018-10-17 21:00 | 125.41 | 101.05
2018-10-17 21:30 | 126.19 | 101.2
2018-10-17 22:00 | 131.76 | 106.5
2018-10-17 22:30 | 132.4 | 107.74
2018-10-17 23:00 | 126.26 | 101.13
2018-10-17 23:30 | 116.87 | 92.05
2018-10-18 | 101.79 | 79.35
2018-10-18 00:30 | 106.92 | 85.69
2018-10-18 01:00 | 109.12 | 86.47
2018-10-18 01:30 | 107.36 | 85.54
2018-10-18 02:00 | 103.2 | 80.06
2018-10-18 02:30 | 106.16 | 83.78
2018-10-18 03:00 | 105.69 | 83.74
2018-10-18 03:30 | 102.24 | 79.76
2018-10-18 04:00 | 94.82 | 72.77
2018-10-18 04:30 | 102.01 | 81
2018-10-18 05:00 | 95.18 | 71.72
2018-10-18 05:30 | 107.77 | 81.82
2018-10-18 06:00 | 109.87 | 83.63
2018-10-18 06:30 | 113.54 | 85.19
2018-10-18 07:00 | 113.1 | 85.93
2018-10-18 07:30 | 114.78 | 88.02
2018-10-18 08:00 | 108.09 | 80.69
2018-10-18 08:30 | 107.59 | 81.12
2018-10-18 09:00 | 116.23 | 90.91
2018-10-18 09:30 | 115.15 | 87.78
2018-10-18 10:00 | 115.81 | 87.66
2018-10-18 10:30 | 119.25 | 92.77
2018-10-18 11:00 | 120.36 | 93.04
2018-10-18 11:30 | 122.4 | 93.13
2018-10-18 12:00 | 126.41 | 99.09
2018-10-18 12:30 | 127.56 | 102.02
2018-10-18 13:00 | 125.9 | 99.44
2018-10-18 13:30 | 129.64 | 102.03
2018-10-18 14:00 | 124.08 | 95.3
2018-10-18 14:30 | 127.52 | 99.44
2018-10-18 15:00 | 126.98 | 98.06
2018-10-18 15:30 | 127.19 | 98.94
2018-10-18 16:00 | 130.42 | 102.14
2018-10-18 16:30 | 130.09 | 101.87
2018-10-18 17:00 | 129.13 | 101.91
2018-10-18 17:30 | 133.1 | 107.05
2018-10-18 18:00 | 129.34 | 103.79
2018-10-18 18:30 | 128.91 | 102.82
2018-10-18 19:00 | 133.11 | 107.39
2018-10-18 19:30 | 137.24 | 111.35
2018-10-18 20:00 | 137.99 | 112.33
2018-10-18 20:30 | 132.17 | 104.77
2018-10-18 21:00 | 130.77 | 104.3
2018-10-18 21:30 | 135.03 | 110.14
2018-10-18 22:00 | 132.55 | 106.1
2018-10-18 22:30 | 134.12 | 107.11
2018-10-18 23:00 | 126.13 | 99.38
2018-10-18 23:30 | 129.31 | 102.88
2018-10-19 | 129.77 | 103.84
2018-10-19 00:30 | 135.26 | 108.67
2018-10-19 01:00 | 130.1 | 102.71
2018-10-19 01:30 | 131.52 | 104.55
2018-10-19 02:00 | 130.89 | 104.45
2018-10-19 02:30 | 130.27 | 102.61
2018-10-19 03:00 | 127.31 | 98.85
2018-10-19 03:30 | 127.16 | 98.42
2018-10-19 04:00 | 129.85 | 102.71
2018-10-19 04:30 | 127.65 | 100.34
2018-10-19 05:00 | 131.53 | 105.68
2018-10-19 05:30 | 131.23 | 105.77
2018-10-19 06:00 | 125.89 | 98.4
2018-10-19 06:30 | 114.65 | 85.02
2018-10-19 07:00 | 115.98 | 85.76
2018-10-19 07:30 | 111.57 | 80.46
2018-10-19 08:00 | 112.71 | 81.01
2018-10-19 08:30 | 120.65 | 88.33
2018-10-19 09:00 | 126.18 | 96.23
2018-10-19 09:30 | 127.38 | 98.74
2018-10-19 10:00 | 123.33 | 93.62
2018-10-19 10:30 | 127.36 | 99
2018-10-19 11:00 | 129.9 | 103.03
2018-10-19 11:30 | 122.44 | 95.27
2018-10-19 12:00 | 126.96 | 97.24
2018-10-19 12:30 | 126.05 | 95.07
2018-10-19 13:00 | 124.11 | 94.81
2018-10-19 13:30 | 122.26 | 92.83
2018-10-19 14:00 | 117.81 | 91.62
2018-10-19 14:30 | 122.82 | 97.53
2018-10-19 15:00 | 123.08 | 95.27
2018-10-19 15:30 | 128.17 | 99.68
2018-10-19 16:00 | 130.66 | 102.91
2018-10-19 16:30 | 131.63 | 106.19
2018-10-19 17:00 | 132.21 | 106.61
2018-10-19 17:30 | 136.92 | 111.68
2018-10-19 18:00 | 125.12 | 100.23
2018-10-19 18:30 | 125.12 | 101.25
2018-10-19 19:00 | 125.75 | 101.04
2018-10-19 19:30 | 132.33 | 109.68
2018-10-19 20:00 | 135.18 | 113.03
2018-10-19 20:30 | 138 | 116.4
2018-10-19 21:00 | 137.05 | 114.63
2018-10-19 21:30 | 136.7 | 114.4
2018-10-19 22:00 | 133.41 | 108.61
2018-10-19 22:30 | 132.36 | 108.7
2018-10-19 23:00 | 130.61 | 105.91
2018-10-19 23:30 | 127.49 | 105.24
2018-10-20 | 127.93 | 105.42
2018-10-20 00:30 | 131.24 | 108.59
2018-10-20 01:00 | 138.59 | 116.07
2018-10-20 01:30 | 144.14 | 120.36
2018-10-20 02:00 | 133.8 | 109.6
2018-10-20 02:30 | 135.63 | 109.96
2018-10-20 03:00 | 131.96 | 108.22
2018-10-20 03:30 | 130.33 | 109.26
2018-10-20 04:00 | 137.15 | 114.99
2018-10-20 04:30 | 130.3 | 107.22
2018-10-20 05:00 | 128.78 | 105.04
2018-10-20 05:30 | 131.61 | 108.28
2018-10-20 06:00 | 128.21 | 104.01
2018-10-20 06:30 | 121.26 | 94.92
2018-10-20 07:00 | 120.54 | 94.39
2018-10-20 07:30 | 119.21 | 93.28
2018-10-20 08:00 | 116.15 | 88.09
2018-10-20 08:30 | 113.39 | 86.95
2018-10-20 09:00 | 117.91 | 90.1
2018-10-20 09:30 | 120.74 | 93.04
2018-10-20 10:00 | 114.88 | 85.89
2018-10-20 10:30 | 119.93 | 91.86
2018-10-20 11:00 | 117.26 | 87.78
2018-10-20 11:30 | 121.08 | 92.15
2018-10-20 12:00 | 123.97 | 98.95
2018-10-20 12:30 | 122.68 | 99.94
2018-10-20 13:00 | 121.61 | 98.52
2018-10-20 13:30 | 124.32 | 100.6
2018-10-20 14:00 | 130.74 | 108.38
2018-10-20 14:30 | 129.77 | 107.76
2018-10-20 15:00 | 128.93 | 106.79
2018-10-20 15:30 | 123.8 | 100.86
2018-10-20 16:00 | 129.89 | 108.36
2018-10-20 16:30 | 129.67 | 103.64
2018-10-20 17:00 | 128.65 | 102.09
2018-10-20 17:30 | 137.02 | 111.89
2018-10-20 18:00 | 132.44 | 107.43
2018-10-20 18:30 | 133.66 | 108.85
2018-10-20 19:00 | 130.52 | 106.35
2018-10-20 19:30 | 140.53 | 115.32
2018-10-20 20:00 | 145.59 | 121.3
2018-10-20 20:30 | 146.65 | 123.53
2018-10-20 21:00 | 142.08 | 119.02
2018-10-20 21:30 | 135.55 | 111.48
2018-10-20 22:00 | 135.46 | 111.14
2018-10-20 22:30 | 131 | 107.11
2018-10-20 23:00 | 132.38 | 108.21
2018-10-20 23:30 | 132.47 | 106.91
2018-10-21 | 134.31 | 108.55
2018-10-21 00:30 | 128.7 | 103.36
2018-10-21 01:00 | 128.62 | 101.26
2018-10-21 01:30 | 126.22 | 98.85
2018-10-21 02:00 | 120.76 | 93.08
2018-10-21 02:30 | 119.4 | 92.28
2018-10-21 03:00 | 118.23 | 93.72
2018-10-21 03:30 | 125.86 | 101.07
2018-10-21 04:00 | 124.6 | 99.66
2018-10-21 04:30 | 126 | 101.08
2018-10-21 05:00 | 127 | 103.12
2018-10-21 05:30 | 119.82 | 94.48
2018-10-21 06:00 | 119.31 | 93.77
2018-10-21 06:30 | 111.71 | 84.14
2018-10-21 07:00 | 117.66 | 88.88
2018-10-21 07:30 | 121.28 | 92.07
2018-10-21 08:00 | 115.82 | 85.58
2018-10-21 08:30 | 120.48 | 91.84
2018-10-21 09:00 | 120.53 | 91.47
2018-10-21 09:30 | 124.09 | 95.05
2018-10-21 10:00 | 123.76 | 95.7
2018-10-21 10:30 | 120.19 | 92.08
2018-10-21 11:00 | 124.8 | 96.99
2018-10-21 11:30 | 127.39 | 101.27
2018-10-21 12:00 | 120.12 | 93.04
2018-10-21 12:30 | 111.65 | 83.19
2018-10-21 13:00 | 108.94 | 81.41
2018-10-21 13:30 | 114.8 | 88.46
2018-10-21 14:00 | 122.75 | 95.93
2018-10-21 14:30 | 122.82 | 96.02
2018-10-21 15:00 | 122.62 | 95.65
2018-10-21 15:30 | 126.53 | 101.35
2018-10-21 16:00 | 132 | 107.07
2018-10-21 16:30 | 126.73 | 100.89
2018-10-21 17:00 | 128.05 | 99.79
2018-10-21 17:30 | 126.75 | 102.05
2018-10-21 18:00 | 128.22 | 103.43
2018-10-21 18:30 | 121.09 | 94.29
2018-10-21 19:00 | 123.01 | 97.55
2018-10-21 19:30 | 123.26 | 100.47
2018-10-21 20:00 | 127.54 | 104.26
2018-10-21 20:30 | 130.44 | 109.04
2018-10-21 21:00 | 130.12 | 109.38
2018-10-21 21:30 | 127.21 | 105.57
2018-10-21 22:00 | 124.35 | 102.47
2018-10-21 22:30 | 126.38 | 105.66
2018-10-21 23:00 | 119.99 | 100.24
2018-10-21 23:30 | 115.46 | 93.69
2018-10-22 | 114.95 | 92.49
2018-10-22 00:30 | 117.24 | 95.71
2018-10-22 01:00 | 110.56 | 88.17
2018-10-22 01:30 | 111.6 | 89.82
2018-10-22 02:00 | 112.28 | 90.11
2018-10-22 02:30 | 112.32 | 90.34
2018-10-22 03:00 | 106.42 | 83.83
2018-10-22 03:30 | 108.17 | 85.64
2018-10-22 04:00 | 108.54 | 86.24
2018-10-22 04:30 | 106.91 | 84.23
2018-10-22 05:00 | 108.46 | 86.03
2018-10-22 05:30 | 101.95 | 79.14
2018-10-22 06:00 | 93.76 | 79.25
2018-10-22 06:30 | 81.99 | 70.58
2018-10-22 07:00 | 90.48 | 79.91
2018-10-22 07:30 | 94.37 | 83.45
2018-10-22 08:00 | 94.65 | 82.93
2018-10-22 08:30 | 97.46 | 85.81
2018-10-22 09:00 | 94.92 | 82.77
2018-10-22 09:30 | 91.21 | 76.19
2018-10-22 10:00 | 91.68 | 75.18
2018-10-22 10:30 | 90.91 | 75.38
2018-10-22 11:00 | 94.27 | 78.95
2018-10-22 11:30 | 98.49 | 82.74
2018-10-22 12:00 | 99.6 | 83.47
2018-10-22 12:30 | 100.13 | 83.72
2018-10-22 13:00 | 104.26 | 89.15
2018-10-22 13:30 | 104.58 | 89.66
2018-10-22 14:00 | 106.06 | 91.84
2018-10-22 14:30 | 107.78 | 92.94
2018-10-22 15:00 | 108.5 | 92.8
2018-10-22 15:30 | 112.23 | 96.93
2018-10-22 16:00 | 113.85 | 97.46
2018-10-22 16:30 | 117.6 | 102.36
2018-10-22 17:00 | 115.85 | 99.4
2018-10-22 17:30 | 114.33 | 99.39
2018-10-22 18:00 | 116.84 | 102.35
2018-10-22 18:30 | 112.06 | 97.79
2018-10-22 19:00 | 119.3 | 105.56
2018-10-22 19:30 | 118.32 | 104.61
2018-10-22 20:00 | 118.4 | 104.33
2018-10-22 20:30 | 116.94 | 102.42
2018-10-22 21:00 | 113.38 | 100.02
2018-10-22 21:30 | 107.8 | 94.4
2018-10-22 22:00 | 103.53 | 90.4
2018-10-22 22:30 | 103.29 | 90.38
2018-10-22 23:00 | 102.5 | 89.42
2018-10-22 23:30 | 106.19 | 92.47
2018-10-23 | 107.88 | 93.69
2018-10-23 00:30 | 107.37 | 92.98
2018-10-23 01:00 | 107.39 | 93.13
2018-10-23 01:30 | 104.77 | 89.46
2018-10-23 02:00 | 108.98 | 94.1
2018-10-23 02:30 | 111.41 | 97
2018-10-23 03:00 | 108.01 | 94.18
2018-10-23 03:30 | 107.15 | 92.5
2018-10-23 04:00 | 102.83 | 88.16
2018-10-23 04:30 | 103.11 | 88.9
2018-10-23 05:00 | 101.63 | 87.83
2018-10-23 05:30 | 101.11 | 87.46
2018-10-23 06:00 | 100.51 | 86.06
2018-10-23 06:30 | 94.42 | 78.5
2018-10-23 07:00 | 91.68 | 75.35
2018-10-23 07:30 | 89.01 | 74.97
2018-10-23 08:00 | 87.1 | 74.27
2018-10-23 08:30 | 82.49 | 69.57
2018-10-23 09:00 | 79.65 | 67.17
2018-10-23 09:30 | 80.34 | 67.61
2018-10-23 10:00 | 81.69 | 68.3
2018-10-23 10:30 | 81.12 | 67.57
2018-10-23 11:00 | 81.1 | 67.55
2018-10-23 11:30 | 77.57 | 64.74
2018-10-23 12:00 | 79.34 | 67.01
2018-10-23 12:30 | 78.94 | 66.1
2018-10-23 13:00 | 79.03 | 65.6
2018-10-23 13:30 | 79.9 | 67.96
2018-10-23 14:00 | 82.08 | 69.41
2018-10-23 14:30 | 88.58 | 75.66
2018-10-23 15:00 | 86.28 | 73.86
2018-10-23 15:30 | 82.22 | 69.34
2018-10-23 16:00 | 82.25 | 69.54
2018-10-23 16:30 | 85.93 | 70.38
2018-10-23 17:00 | 86.87 | 73.72
2018-10-23 17:30 | 91.15 | 79.02
2018-10-23 18:00 | 99.73 | 87.56
2018-10-23 18:30 | 96.22 | 82.4
2018-10-23 19:00 | 103.3 | 90.82
2018-10-23 19:30 | 108.17 | 95.83
2018-10-23 20:00 | 104.3 | 90.27
2018-10-23 20:30 | 103.34 | 88.01
2018-10-23 21:00 | 106.19 | 92.27
2018-10-23 21:30 | 105.89 | 91.35
2018-10-23 22:00 | 108.42 | 94.44
2018-10-23 22:30 | 108.35 | 94.14
2018-10-23 23:00 | 106.61 | 93.29
2018-10-23 23:30 | 101.98 | 88.17
2018-10-24 | 104.16 | 90.85
2018-10-24 00:30 | 105.57 | 91.72
2018-10-24 01:00 | 106.42 | 92.95
2018-10-24 01:30 | 102.93 | 89.71
2018-10-24 02:00 | 102.27 | 90.15
2018-10-24 02:30 | 98.5 | 87.47
2018-10-24 03:00 | 95.81 | 84.81
2018-10-24 03:30 | 95.09 | 83.7
2018-10-24 04:00 | 94.03 | 84.31
2018-10-24 04:30 | 88.6 | 79.9
2018-10-24 05:00 | 87.35 | 78.41
2018-10-24 05:30 | 85.92 | 77.73
2018-10-24 06:00 | 81.65 | 73.19
2018-10-24 06:30 | 74.41 | 65.35
2018-10-24 07:00 | 75.33 | 65.68
2018-10-24 07:30 | 76.57 | 66.93
2018-10-24 08:00 | 78.19 | 68.23
2018-10-24 08:30 | 80.91 | 70.77
2018-10-24 09:00 | 75.66 | 63.52
2018-10-24 09:30 | 80.79 | 68.23
2018-10-24 10:00 | 79.71 | 67.25
2018-10-24 10:30 | 80.19 | 67.02
2018-10-24 11:00 | 81.68 | 68.94
2018-10-24 11:30 | 86.51 | 74.64
2018-10-24 12:00 | 86.19 | 74.34
2018-10-24 12:30 | 90.16 | 78.17
2018-10-24 13:00 | 88.85 | 76.3
2018-10-24 13:30 | 92.93 | 80.6
2018-10-24 14:00 | 95.35 | 82.92
2018-10-24 14:30 | 88.05 | 74.43
2018-10-24 15:00 | 89.93 | 76.26
2018-10-24 15:30 | 88.37 | 75.08
2018-10-24 16:00 | 89.38 | 76.78
2018-10-24 16:30 | 86.75 | 73.4
2018-10-24 17:00 | 95.17 | 73.82
2018-10-24 17:30 | 96.69 | 76.13
2018-10-24 18:00 | 100.32 | 79.53
2018-10-24 18:30 | 99.29 | 76.83
2018-10-24 19:00 | 103.12 | 80.84
2018-10-24 19:30 | 103.63 | 81.05
2018-10-24 20:00 | 103.02 | 81.23
2018-10-24 20:30 | 104.47 | 82.84
2018-10-24 21:00 | 102.78 | 81.69
2018-10-24 21:30 | 101.91 | 80.97
2018-10-24 22:00 | 105.46 | 84.36
2018-10-24 22:30 | 105.98 | 85.47
2018-10-24 23:00 | 97.86 | 77.04
2018-10-24 23:30 | 96.87 | 74.54
2018-10-25 | 96.61 | 72.68
2018-10-25 00:30 | 96.99 | 74
2018-10-25 01:00 | 97.77 | 75.33
2018-10-25 01:30 | 100.84 | 78.86
2018-10-25 02:00 | 103.37 | 82.28
2018-10-25 02:30 | 102.57 | 81.15
2018-10-25 03:00 | 98.89 | 76.81
2018-10-25 03:30 | 100.59 | 78.85
2018-10-25 04:00 | 102.34 | 79.93
2018-10-25 04:30 | 108.36 | 87.6
2018-10-25 05:00 | 104.81 | 83.51
2018-10-25 05:30 | 106.59 | 85.84
2018-10-25 06:00 | 106.08 | 86.24
2018-10-25 06:30 | 101.18 | 79.58
2018-10-25 07:00 | 95.63 | 73.04
2018-10-25 07:30 | 101.29 | 79.12
2018-10-25 08:00 | 102.94 | 80.68
2018-10-25 08:30 | 106.91 | 85.64
2018-10-25 09:00 | 104.69 | 83.23
2018-10-25 09:30 | 102.66 | 80.08
2018-10-25 10:00 | 107.29 | 86.52
2018-10-25 10:30 | 104.09 | 82.65
2018-10-25 11:00 | 94.32 | 70.44
2018-10-25 11:30 | 89.86 | 65.34
2018-10-25 12:00 | 95.54 | 72.77
2018-10-25 12:30 | 101.49 | 79.71
2018-10-25 13:00 | 100.2 | 79.21
2018-10-25 13:30 | 99.41 | 78.32
2018-10-25 14:00 | 94.53 | 73.35
2018-10-25 14:30 | 100.98 | 79.4
2018-10-25 15:00 | 108.06 | 86.65
2018-10-25 15:30 | 106.98 | 85.44
2018-10-25 16:00 | 106.13 | 83.48
2018-10-25 16:30 | 105.58 | 82.82
2018-10-25 17:00 | 108.23 | 87.21
2018-10-25 17:30 | 106.05 | 85.68
2018-10-25 18:00 | 110.62 | 90.08
2018-10-25 18:30 | 105.23 | 82.53
2018-10-25 19:00 | 117.69 | 97.16
2018-10-25 19:30 | 120.4 | 101.14
2018-10-25 20:00 | 118.84 | 99.19
2018-10-25 20:30 | 120.79 | 101.06
2018-10-25 21:00 | 115.24 | 94.08
2018-10-25 21:30 | 111.84 | 91.84
2018-10-25 22:00 | 114.38 | 94.3
2018-10-25 22:30 | 112.37 | 92.12
2018-10-25 23:00 | 116.26 | 97.56
2018-10-25 23:30 | 114.46 | 94.77
2018-10-26 | 110.51 | 89.07
2018-10-26 00:30 | 104.21 | 81.84
2018-10-26 01:00 | 105.29 | 82.34
2018-10-26 01:30 | 105.14 | 82.47
2018-10-26 02:00 | 104.39 | 81.79
2018-10-26 02:30 | 115.92 | 94.22
2018-10-26 03:00 | 109.57 | 86.49
2018-10-26 03:30 | 104.17 | 81.5
2018-10-26 04:00 | 112.25 | 90.48
2018-10-26 04:30 | 105 | 82.81
2018-10-26 05:00 | 106.02 | 83.73
2018-10-26 05:30 | 104.53 | 82.39
2018-10-26 06:00 | 109.51 | 87.93
2018-10-26 06:30 | 102.62 | 79.18
2018-10-26 07:00 | 101.98 | 78.34
2018-10-26 07:30 | 104.81 | 81.16
2018-10-26 08:00 | 101.06 | 76.44
2018-10-26 08:30 | 102.23 | 77.34
2018-10-26 09:00 | 101.48 | 75.79
2018-10-26 09:30 | 100 | 73.18
2018-10-26 10:00 | 103.78 | 78.73
2018-10-26 10:30 | 106.46 | 83.45
2018-10-26 11:00 | 109.61 | 87.14
2018-10-26 11:30 | 108.3 | 83.73
2018-10-26 12:00 | 108.06 | 81.7
2018-10-26 12:30 | 104.78 | 79.04
2018-10-26 13:00 | 114.73 | 87.56
2018-10-26 13:30 | 121.31 | 92.28
2018-10-26 14:00 | 125.33 | 97.17
2018-10-26 14:30 | 122.02 | 95.16
2018-10-26 15:00 | 120.07 | 94.25
2018-10-26 15:30 | 114.4 | 89
2018-10-26 16:00 | 114.43 | 90.88
2018-10-26 16:30 | 120.57 | 98.18
2018-10-26 17:00 | 112.61 | 91.57
2018-10-26 17:30 | 114.74 | 95.23
2018-10-26 18:00 | 113.97 | 94.94
2018-10-26 18:30 | 113.81 | 93.96
2018-10-26 19:00 | 121.49 | 100.52
2018-10-26 19:30 | 122.29 | 100.74
2018-10-26 20:00 | 122.25 | 100.54
2018-10-26 20:30 | 130.67 | 110.95
2018-10-26 21:00 | 120.26 | 98.49
2018-10-26 21:30 | 128.04 | 107.99
2018-10-26 22:00 | 120.95 | 100.73
2018-10-26 22:30 | 122.97 | 104.42
2018-10-26 23:00 | 124.31 | 105.03
2018-10-26 23:30 | 117.03 | 97.41
2018-10-27 | 115.08 | 95.94
2018-10-27 00:30 | 109.08 | 89.95
2018-10-27 01:00 | 107.55 | 88.49
2018-10-27 01:30 | 106.89 | 88.29
2018-10-27 02:00 | 108.54 | 89.7
2018-10-27 02:30 | 106 | 86.71
2018-10-27 03:00 | 105.29 | 86.5
2018-10-27 03:30 | 117.81 | 100.2
2018-10-27 04:00 | 114.07 | 96.45
2018-10-27 04:30 | 110.39 | 92.59
2018-10-27 05:00 | 108.07 | 90.4
2018-10-27 05:30 | 99.67 | 82.99
2018-10-27 06:00 | 89.94 | 69.73
2018-10-27 06:30 | 93.26 | 69.58
2018-10-27 07:00 | 86.32 | 61.18
2018-10-27 07:30 | 92.44 | 68.41
2018-10-27 08:00 | 80.23 | 55.32
2018-10-27 08:30 | 88.38 | 65.76
2018-10-27 09:00 | 94.01 | 72.78
2018-10-27 09:30 | 95.43 | 72.74
2018-10-27 10:00 | 92.24 | 69.87
2018-10-27 10:30 | 98.21 | 76.35
2018-10-27 11:00 | 99.05 | 75.54
2018-10-27 11:30 | 98.46 | 76.28
2018-10-27 12:00 | 95.86 | 70.32
2018-10-27 12:30 | 106.89 | 84.3
2018-10-27 13:00 | 108.81 | 85.88
2018-10-27 13:30 | 113.78 | 90.84
2018-10-27 14:00 | 117.33 | 95.44
2018-10-27 14:30 | 113.09 | 90.58
2018-10-27 15:00 | 107.48 | 85.28
2018-10-27 15:30 | 112.41 | 90.04
2018-10-27 16:00 | 109.09 | 87.7
2018-10-27 16:30 | 111.43 | 90.39
2018-10-27 17:00 | 109.03 | 88.13
2018-10-27 17:30 | 108.63 | 87.25
2018-10-27 18:00 | 111.56 | 89.5
2018-10-27 18:30 | 105.71 | 84.15
2018-10-27 19:00 | 117.27 | 97.24
2018-10-27 19:30 | 127.39 | 107.12
2018-10-27 20:00 | 118.09 | 96.52
2018-10-27 20:30 | 119.75 | 96.33
2018-10-27 21:00 | 114.92 | 91.87
2018-10-27 21:30 | 124.54 | 102.96
2018-10-27 22:00 | 130.6 | 109.93
2018-10-27 22:30 | 123.13 | 102.73
2018-10-27 23:00 | 124.85 | 105.11
2018-10-27 23:30 | 119.9 | 99.16
2018-10-28 | 122.98 | 101.37
2018-10-28 00:30 | 120.79 | 98.96
2018-10-28 01:00 | 116.42 | 94.16
2018-10-28 01:30 | 120.63 | 99.38
2018-10-28 02:00 | 112.03 | 91.44
2018-10-28 02:30 | 103.77 | 84.35
2018-10-28 03:00 | 111.93 | 93.13
2018-10-28 03:30 | 107.97 | 88.39
2018-10-28 04:00 | 106.54 | 85.54
2018-10-28 04:30 | 108.68 | 86.45
2018-10-28 05:00 | 109.51 | 88.3
2018-10-28 05:30 | 113.77 | 92.85
2018-10-28 06:00 | 104.02 | 82.93
2018-10-28 06:30 | 99.44 | 75.13
2018-10-28 07:00 | 109.46 | 85.22
2018-10-28 07:30 | 113.4 | 88.93
2018-10-28 08:00 | 105.79 | 85.07
2018-10-28 08:30 | 99.5 | 78.42
2018-10-28 09:00 | 105.01 | 83.04
2018-10-28 09:30 | 106.41 | 83.34
2018-10-28 10:00 | 110.58 | 87.32
2018-10-28 10:30 | 107.15 | 83.82
2018-10-28 11:00 | 108.79 | 87.26
2018-10-28 11:30 | 108.11 | 88.65
2018-10-28 12:00 | 108.35 | 87.15
2018-10-28 12:30 | 111.46 | 86.29
2018-10-28 13:00 | 113.69 | 85.99
2018-10-28 13:30 | 115.55 | 88.02
2018-10-28 14:00 | 117.21 | 92.35
2018-10-28 14:30 | 125.23 | 100.79
2018-10-28 15:00 | 118.79 | 94.62
2018-10-28 15:30 | 114.84 | 91.83
2018-10-28 16:00 | 121.93 | 99.84
2018-10-28 16:30 | 120.37 | 97.85
2018-10-28 17:00 | 126.17 | 104.55
2018-10-28 17:30 | 127.74 | 107.18
2018-10-28 18:00 | 124.33 | 103.25
2018-10-28 18:30 | 111.34 | 86.89
2018-10-28 19:00 | 112.1 | 88
2018-10-28 19:30 | 114.44 | 92.37
2018-10-28 20:00 | 118.59 | 96.76
2018-10-28 20:30 | 119.81 | 98.34
2018-10-28 21:00 | 119.3 | 97.08
2018-10-28 21:30 | 123.58 | 101.18
2018-10-28 22:00 | 128.36 | 105.5
2018-10-28 22:30 | 123.43 | 99.37
2018-10-28 23:00 | 119.58 | 95.5
2018-10-28 23:30 | 116.27 | 93.07
2018-10-29 | 116.97 | 92.83
2018-10-29 00:30 | 112.44 | 87.6
2018-10-29 01:00 | 120.2 | 97.24
2018-10-29 01:30 | 116.1 | 94.4
2018-10-29 02:00 | 115.12 | 93.68
2018-10-29 02:30 | 122.86 | 98.95
2018-10-29 03:00 | 134.92 | 111.71
2018-10-29 03:30 | 131.31 | 108.62
2018-10-29 04:00 | 120.01 | 99.03
2018-10-29 04:30 | 116.42 | 95.23
2018-10-29 05:00 | 115.66 | 93.25
2018-10-29 05:30 | 113.6 | 90.84
2018-10-29 06:00 | 102.77 | 79.8
2018-10-29 06:30 | 108.05 | 85.24
2018-10-29 07:00 | 114.34 | 91.73
2018-10-29 07:30 | 120.33 | 98.06
2018-10-29 08:00 | 114.67 | 92.39
2018-10-29 08:30 | 111.65 | 87.03
2018-10-29 09:00 | 110.78 | 86.07
2018-10-29 09:30 | 111.49 | 88.18
2018-10-29 10:00 | 110.2 | 85.03
2018-10-29 10:30 | 112.99 | 86.84
2018-10-29 11:00 | 106.18 | 80.43
2018-10-29 11:30 | 103.77 | 77.94
2018-10-29 12:00 | 112.68 | 86.69
2018-10-29 12:30 | 111.77 | 85.35
2018-10-29 13:00 | 115.12 | 90.06
2018-10-29 13:30 | 117.13 | 90.59
2018-10-29 14:00 | 119.1 | 91.77
2018-10-29 14:30 | 114.15 | 87.5
2018-10-29 15:00 | 118.34 | 93.52
2018-10-29 15:30 | 125.44 | 102.65
2018-10-29 16:00 | 125.21 | 102.8
2018-10-29 16:30 | 120.45 | 92.01
2018-10-29 17:00 | 117.72 | 89.72
2018-10-29 17:30 | 124.28 | 100.82
2018-10-29 18:00 | 121.7 | 98.93
2018-10-29 18:30 | 112.31 | 87.64
2018-10-29 19:00 | 124.75 | 101.22
2018-10-29 19:30 | 124.64 | 102.44
2018-10-29 20:00 | 122.83 | 100.73
2018-10-29 20:30 | 114.68 | 92.76
2018-10-29 21:00 | 115.78 | 91.25
2018-10-29 21:30 | 122.65 | 99.62
2018-10-29 22:00 | 120.13 | 96.39
2018-10-29 22:30 | 119.04 | 94.71
2018-10-29 23:00 | 115.86 | 90.8
2018-10-29 23:30 | 115.86 | 89.99
2018-10-30 | 120.87 | 95.48
2018-10-30 00:30 | 124.77 | 100.18
2018-10-30 01:00 | 123.5 | 98.83
2018-10-30 01:30 | 123.72 | 100.03
2018-10-30 02:00 | 126.73 | 102.7
2018-10-30 02:30 | 132.46 | 110.15
2018-10-30 03:00 | 127.85 | 103.97
2018-10-30 03:30 | 119.14 | 95.05
2018-10-30 04:00 | 122.82 | 97.18
2018-10-30 04:30 | 120.17 | 96.29
2018-10-30 05:00 | 126.7 | 103.48
2018-10-30 05:30 | 129.22 | 105.04
2018-10-30 06:00 | 117.92 | 92.79
2018-10-30 06:30 | 115.66 | 89.41
2018-10-30 07:00 | 120.01 | 95.56
2018-10-30 07:30 | 115.51 | 90.05
2018-10-30 08:00 | 114.14 | 89.52
2018-10-30 08:30 | 118.01 | 92.75
2018-10-30 09:00 | 124.84 | 100.24
2018-10-30 09:30 | 120.14 | 92.23
2018-10-30 10:00 | 119.89 | 93.52
2018-10-30 10:30 | 118.32 | 91.62
2018-10-30 11:00 | 121.59 | 94.33
2018-10-30 11:30 | 116.72 | 89.51
2018-10-30 12:00 | 117.52 | 91.93
2018-10-30 12:30 | 118.18 | 93.66
2018-10-30 13:00 | 115.41 | 88.76
2018-10-30 13:30 | 118.43 | 91.16
2018-10-30 14:00 | 118.89 | 89.76
2018-10-30 14:30 | 114.27 | 86.07
2018-10-30 15:00 | 118.26 | 90.65
2018-10-30 15:30 | 117.61 | 91.16
2018-10-30 16:00 | 126.49 | 100.74
2018-10-30 16:30 | 120.5 | 94.7
2018-10-30 17:00 | 126.39 | 104.18
2018-10-30 17:30 | 124.69 | 101.94
2018-10-30 18:00 | 122.32 | 98.36
2018-10-30 18:30 | 116.09 | 93.88
2018-10-30 19:00 | 125.52 | 103.01
2018-10-30 19:30 | 113.45 | 89.79
2018-10-30 20:00 | 120.52 | 97.74
2018-10-30 20:30 | 122.33 | 99.24
2018-10-30 21:00 | 121.18 | 99.51
2018-10-30 21:30 | 108.76 | 87.12
2018-10-30 22:00 | 105.49 | 85.55
2018-10-30 22:30 | 96.66 | 78.37
2018-10-30 23:00 | 96.52 | 78.24
2018-10-30 23:30 | 104.93 | 87.2
2018-10-31 | 99.76 | 81.23
2018-10-31 00:30 | 101.14 | 82.98
2018-10-31 01:00 | 103.71 | 85.26
2018-10-31 01:30 | 102.62 | 83.78
2018-10-31 02:00 | 108.8 | 88.52
2018-10-31 02:30 | 106.23 | 86.05
2018-10-31 03:00 | 105.27 | 85.33
2018-10-31 03:30 | 103.52 | 83.38
2018-10-31 04:00 | 113.09 | 93.45
2018-10-31 04:30 | 111.16 | 91.9
2018-10-31 05:00 | 106.04 | 88.23
2018-10-31 05:30 | 102.75 | 83.75
2018-10-31 06:00 | 98.45 | 80.39
2018-10-31 06:30 | 98.93 | 77.54
2018-10-31 07:00 | 103.51 | 84.78
2018-10-31 07:30 | 107.07 | 87.73
2018-10-31 08:00 | 108.19 | 89.19
2018-10-31 08:30 | 99.02 | 79.16
2018-10-31 09:00 | 96.15 | 76.02
2018-10-31 09:30 | 95.28 | 73.88
2018-10-31 10:00 | 97.92 | 76.55
2018-10-31 10:30 | 103.92 | 80.38
2018-10-31 11:00 | 107.54 | 82.64
2018-10-31 11:30 | 107.28 | 83.58
2018-10-31 12:00 | 108.19 | 84.2
2018-10-31 12:30 | 106.38 | 80.88
2018-10-31 13:00 | 102.1 | 75.85
2018-10-31 13:30 | 97.53 | 68.84
2018-10-31 14:00 | 99.23 | 71.35
2018-10-31 14:30 | 111.88 | 88.39
2018-10-31 15:00 | 107.66 | 82.58
2018-10-31 15:30 | 110.75 | 85.05
2018-10-31 16:00 | 113.97 | 88.41
2018-10-31 16:30 | 113.39 | 88.48
2018-10-31 17:00 | 113.12 | 91.3
2018-10-31 17:30 | 113.69 | 91.58
2018-10-31 18:00 | 119.78 | 98.48
2018-10-31 18:30 | 116.1 | 96
2018-10-31 19:00 | 121.3 | 101.29
2018-10-31 19:30 | 123.58 | 104.65
2018-10-31 20:00 | 126.7 | 106.81
2018-10-31 20:30 | 116.84 | 96.91
2018-10-31 21:00 | 118.37 | 98.55
2018-10-31 21:30 | 104.6 | 84.43
2018-10-31 22:00 | 107.23 | 87.25
2018-10-31 22:30 | 107.79 | 86.25
2018-10-31 23:00 | 107.79 | 85.49
2018-10-31 23:30 | 107.78 | 86.54
2018-11-01 | 110.65 | 90.03
2018-11-01 00:30 | 114.14 | 92.31
2018-11-01 01:00 | 107.97 | 84.68
2018-11-01 01:30 | 113.34 | 90.39
2018-11-01 02:00 | 115.47 | 93.13
2018-11-01 02:30 | 108.96 | 86.08
2018-11-01 03:00 | 107.56 | 83.75
2018-11-01 03:30 | 110.37 | 88.18
2018-11-01 04:00 | 115.11 | 89.4
2018-11-01 04:30 | 109.77 | 84.65
2018-11-01 05:00 | 110.46 | 86.13
2018-11-01 05:30 | 117.02 | 94.59
2018-11-01 06:00 | 109.6 | 84.91
2018-11-01 06:30 | 105.13 | 79.85
2018-11-01 07:00 | 111.38 | 86.74
2018-11-01 07:30 | 110.18 | 84.74
2018-11-01 08:00 | 108.8 | 84.93
2018-11-01 08:30 | 110 | 85.42
2018-11-01 09:00 | 102.19 | 77.84
2018-11-01 09:30 | 105.86 | 82.75
2018-11-01 10:00 | 98.85 | 73.43
2018-11-01 10:30 | 97.68 | 73.6
2018-11-01 11:00 | 97.51 | 72.44
2018-11-01 11:30 | 101.43 | 75.02
2018-11-01 12:00 | 106.63 | 80.77
2018-11-01 12:30 | 106.63 | 78.94
2018-11-01 13:00 | 101.99 | 75.29
2018-11-01 13:30 | 99.82 | 72.63
2018-11-01 14:00 | 97.33 | 70.37
2018-11-01 14:30 | 99.09 | 69.53
2018-11-01 15:00 | 105 | 76.52
2018-11-01 15:30 | 109.5 | 84.69
2018-11-01 16:00 | 100.17 | 76.55
2018-11-01 16:30 | 101.9 | 78.94
2018-11-01 17:00 | 109.74 | 87.6
2018-11-01 17:30 | 110.6 | 88.25
2018-11-01 18:00 | 108.68 | 86.26
2018-11-01 18:30 | 104.64 | 82.86
2018-11-01 19:00 | 107.93 | 86.38
2018-11-01 19:30 | 110.54 | 88.85
2018-11-01 20:00 | 104.8 | 83.45
2018-11-01 20:30 | 105.6 | 84.61
2018-11-01 21:00 | 109.26 | 87.36
2018-11-01 21:30 | 116.75 | 94.61
2018-11-01 22:00 | 118.22 | 96.39
2018-11-01 22:30 | 121.01 | 99.54
2018-11-01 23:00 | 121.15 | 98.42
2018-11-01 23:30 | 119.93 | 95
2018-11-02 | 117.53 | 91.87
2018-11-02 00:30 | 119.96 | 94.3
2018-11-02 01:00 | 122.38 | 98
2018-11-02 01:30 | 116.35 | 90.93
2018-11-02 02:00 | 114.68 | 89.66
2018-11-02 02:30 | 119.17 | 94.02
2018-11-02 03:00 | 118.48 | 93.16
2018-11-02 03:30 | 112.91 | 86.2
2018-11-02 04:00 | 116.85 | 91.03
2018-11-02 04:30 | 121.6 | 96.89
2018-11-02 05:00 | 118.15 | 93.04
2018-11-02 05:30 | 113.8 | 90.09
2018-11-02 06:00 | 112.34 | 87.49
2018-11-02 06:30 | 96.72 | 67.19
2018-11-02 07:00 | 105.44 | 78.42
2018-11-02 07:30 | 102.92 | 75.34
2018-11-02 08:00 | 104.26 | 75.57
2018-11-02 08:30 | 105.02 | 76.28
2018-11-02 09:00 | 106.67 | 77.08
2018-11-02 09:30 | 105.85 | 77.3
2018-11-02 10:00 | 109.32 | 79.69
2018-11-02 10:30 | 110.45 | 82.3
2018-11-02 11:00 | 115.54 | 87.53
2018-11-02 11:30 | 111.5 | 83.45
2018-11-02 12:00 | 120.33 | 92.86
2018-11-02 12:30 | 113.57 | 85.73
2018-11-02 13:00 | 118.05 | 89.37
2018-11-02 13:30 | 117.78 | 89.24
2018-11-02 14:00 | 114.49 | 85.45
2018-11-02 14:30 | 112.53 | 83
2018-11-02 15:00 | 112.45 | 82.14
2018-11-02 15:30 | 110.1 | 80.49
2018-11-02 16:00 | 103.52 | 78.34
2018-11-02 16:30 | 106.89 | 84.19
2018-11-02 17:00 | 116.81 | 92.49
2018-11-02 17:30 | 121.46 | 96.05
2018-11-02 18:00 | 115.49 | 91.25
2018-11-02 18:30 | 113.44 | 87.09
2018-11-02 19:00 | 127.24 | 102.37
2018-11-02 19:30 | 119.81 | 96.55
2018-11-02 20:00 | 123.09 | 97.44
2018-11-02 20:30 | 120.15 | 95.77
2018-11-02 21:00 | 114.35 | 90.55
2018-11-02 21:30 | 120.68 | 97.12
2018-11-02 22:00 | 112.28 | 87.62
2018-11-02 22:30 | 108.82 | 83.05
2018-11-02 23:00 | 113.11 | 88.21
2018-11-02 23:30 | 115.44 | 89.16
2018-11-03 | 121.27 | 97.47
2018-11-03 00:30 | 120.09 | 94.04
2018-11-03 01:00 | 120.87 | 95.33
2018-11-03 01:30 | 121.47 | 96.8
2018-11-03 02:00 | 119.21 | 94.53
2018-11-03 02:30 | 119.01 | 92.89
2018-11-03 03:00 | 116.84 | 89.67
2018-11-03 03:30 | 114.28 | 87.31
2018-11-03 04:00 | 116.41 | 89.84
2018-11-03 04:30 | 117.37 | 91.9
2018-11-03 05:00 | 117.32 | 93.48
2018-11-03 05:30 | 118.43 | 94.06
2018-11-03 06:00 | 125.59 | 100.08
2018-11-03 06:30 | 115.29 | 87.26
2018-11-03 07:00 | 113.93 | 89.7
2018-11-03 07:30 | 113.79 | 89.35
2018-11-03 08:00 | 111.97 | 85.34
2018-11-03 08:30 | 109.11 | 79.96
2018-11-03 09:00 | 113.39 | 83.41
2018-11-03 09:30 | 115.49 | 86.21
2018-11-03 10:00 | 117.64 | 87.73
2018-11-03 10:30 | 119.21 | 90.23
2018-11-03 11:00 | 122.72 | 94.1
2018-11-03 11:30 | 116.8 | 88.66
2018-11-03 12:00 | 122.86 | 95.91
2018-11-03 12:30 | 124.92 | 97.96
2018-11-03 13:00 | 119.04 | 89.37
2018-11-03 13:30 | 112.2 | 83.02
2018-11-03 14:00 | 114.87 | 85.63
2018-11-03 14:30 | 126.4 | 97.69
2018-11-03 15:00 | 127.94 | 101.25
2018-11-03 15:30 | 128.82 | 100.89
2018-11-03 16:00 | 127.91 | 98.69
2018-11-03 16:30 | 128.2 | 98.54
2018-11-03 17:00 | 120.9 | 92.87
2018-11-03 17:30 | 116.98 | 90.74
2018-11-03 18:00 | 127.77 | 103.6
2018-11-03 18:30 | 122.52 | 97.67
2018-11-03 19:00 | 124.88 | 100.14
2018-11-03 19:30 | 123.45 | 99.98
2018-11-03 20:00 | 123.52 | 100.55
2018-11-03 20:30 | 122.06 | 98.79
2018-11-03 21:00 | 119.8 | 95.09
2018-11-03 21:30 | 121.4 | 96.5
2018-11-03 22:00 | 122.21 | 98.21
2018-11-03 22:30 | 116.75 | 93.37
2018-11-03 23:00 | 116.98 | 92.72
2018-11-03 23:30 | 114.35 | 89.79
2018-11-04 | 115.62 | 91.37
2018-11-04 00:30 | 114.11 | 89.32
2018-11-04 01:00 | 117.7 | 93.28
2018-11-04 01:30 | 118.65 | 92.45
2018-11-04 02:00 | 125.42 | 100.43
2018-11-04 02:30 | 131.96 | 107.36
2018-11-04 03:00 | 122.24 | 96.04
2018-11-04 03:30 | 120.46 | 94.84
2018-11-04 04:00 | 118.25 | 91.61
2018-11-04 04:30 | 117.69 | 91.42
2018-11-04 05:00 | 125.57 | 100.88
2018-11-04 05:30 | 120.66 | 95.53
2018-11-04 06:00 | 123.26 | 97.06
2018-11-04 06:30 | 112.89 | 85.9
2018-11-04 07:00 | 123.81 | 95.72
2018-11-04 07:30 | 124.75 | 95.69
2018-11-04 08:00 | 124.26 | 93.12
2018-11-04 08:30 | 121.53 | 90.16
2018-11-04 09:00 | 115.41 | 83.31
2018-11-04 09:30 | 115.88 | 83.27
2018-11-04 10:00 | 120.31 | 88.41
2018-11-04 10:30 | 123.98 | 92.85
2018-11-04 11:00 | 121.39 | 90.14
2018-11-04 11:30 | 125.16 | 94.37
2018-11-04 12:00 | 119.88 | 88.26
2018-11-04 12:30 | 122.1 | 91.07
2018-11-04 13:00 | 117.56 | 85.08
2018-11-04 13:30 | 121.11 | 90.25
2018-11-04 14:00 | 124.57 | 94.12
2018-11-04 14:30 | 129.11 | 97.24
2018-11-04 15:00 | 127.37 | 97
2018-11-04 15:30 | 122.6 | 92.87
2018-11-04 16:00 | 127.56 | 97.66
2018-11-04 16:30 | 121.88 | 93.91
2018-11-04 17:00 | 125.78 | 99.28
2018-11-04 17:30 | 116.55 | 89.22
2018-11-04 18:00 | 115.99 | 88.81
2018-11-04 18:30 | 121.64 | 95.01
2018-11-04 19:00 | 128.93 | 102.25
2018-11-04 19:30 | 128.57 | 102
2018-11-04 20:00 | 128.87 | 102.72
2018-11-04 20:30 | 129.15 | 103.53
2018-11-04 21:00 | 129.68 | 103.59
2018-11-04 21:30 | 134.06 | 108.42
2018-11-04 22:00 | 132.25 | 106.27
2018-11-04 22:30 | 131.22 | 104.58
2018-11-04 23:00 | 122.44 | 96.71
2018-11-04 23:30 | 125.11 | 101.38
2018-11-05 | 125.01 | 101.43
2018-11-05 00:30 | 124.94 | 99.62
2018-11-05 01:00 | 129.39 | 105.25
2018-11-05 01:30 | 119.33 | 93.42
2018-11-05 02:00 | 126.85 | 102.71
2018-11-05 02:30 | 124.09 | 99.61
2018-11-05 03:00 | 123.28 | 98.02
2018-11-05 03:30 | 119.86 | 94.74
2018-11-05 04:00 | 121.84 | 96.32
2018-11-05 04:30 | 116.67 | 91.81
2018-11-05 05:00 | 117.83 | 91.69
2018-11-05 05:30 | 117.95 | 91.89
2018-11-05 06:00 | 118.42 | 94.72
2018-11-05 06:30 | 109.84 | 84.71
2018-11-05 07:00 | 108.9 | 83
2018-11-05 07:30 | 107.41 | 82.5
2018-11-05 08:00 | 110.13 | 84.79
2018-11-05 08:30 | 115.17 | 88.16
2018-11-05 09:00 | 116.36 | 87.85
2018-11-05 09:30 | 118.6 | 90.34
2018-11-05 10:00 | 118.98 | 91.37
2018-11-05 10:30 | 119.93 | 92.3
2018-11-05 11:00 | 113.63 | 85.2
2018-11-05 11:30 | 113.62 | 85.28
2018-11-05 12:00 | 118.99 | 93.12
2018-11-05 12:30 | 120.64 | 94.85
2018-11-05 13:00 | 125.14 | 99.64
2018-11-05 13:30 | 125.05 | 99.16
2018-11-05 14:00 | 122.6 | 97.86
2018-11-05 14:30 | 118.36 | 92.56
2018-11-05 15:00 | 114.7 | 87.94
2018-11-05 15:30 | 117.98 | 89.39
2018-11-05 16:00 | 120.65 | 92.88
2018-11-05 16:30 | 125.87 | 97.24
2018-11-05 17:00 | 126.95 | 97.78
2018-11-05 17:30 | 128.28 | 100.74
2018-11-05 18:00 | 135.37 | 110.53
2018-11-05 18:30 | 130.38 | 104.96
2018-11-05 19:00 | 132.15 | 106.85
2018-11-05 19:30 | 140.76 | 116.43
2018-11-05 20:00 | 136.99 | 110.91
2018-11-05 20:30 | 138.07 | 111.99
2018-11-05 21:00 | 137.76 | 111.46
2018-11-05 21:30 | 134.17 | 107.35
2018-11-05 22:00 | 136.58 | 110.51
2018-11-05 22:30 | 130.47 | 103.99
2018-11-05 23:00 | 131.61 | 106.8
2018-11-05 23:30 | 128.39 | 102.87
2018-11-06 | 132.33 | 106.72
2018-11-06 00:30 | 124.66 | 98.85
2018-11-06 01:00 | 128.83 | 103.91
2018-11-06 01:30 | 130.2 | 105.79
2018-11-06 02:00 | 126.68 | 102.34
2018-11-06 02:30 | 128.8 | 103.76
2018-11-06 03:00 | 128.47 | 103.9
2018-11-06 03:30 | 127.48 | 103.73
2018-11-06 04:00 | 134.62 | 112.27
2018-11-06 04:30 | 139.36 | 117.65
2018-11-06 05:00 | 127.44 | 103.34
2018-11-06 05:30 | 126.06 | 101.42
2018-11-06 06:00 | 119.85 | 94.44
2018-11-06 06:30 | 117.15 | 88.84
2018-11-06 07:00 | 115.85 | 88.11
2018-11-06 07:30 | 118.92 | 94.26
2018-11-06 08:00 | 126.98 | 102.28
2018-11-06 08:30 | 120.69 | 92.98
2018-11-06 09:00 | 125.01 | 95.76
2018-11-06 09:30 | 126.91 | 97.68
2018-11-06 10:00 | 122.92 | 93.53
2018-11-06 10:30 | 130.79 | 103
2018-11-06 11:00 | 125.58 | 98.07
2018-11-06 11:30 | 127 | 99.24
2018-11-06 12:00 | 131.79 | 104.73
2018-11-06 12:30 | 128.49 | 100.88
2018-11-06 13:00 | 130.53 | 103.57
2018-11-06 13:30 | 124.34 | 96.24
2018-11-06 14:00 | 129.08 | 101.68
2018-11-06 14:30 | 135.6 | 108.54
2018-11-06 15:00 | 144.95 | 118.9
2018-11-06 15:30 | 138.44 | 109.68
2018-11-06 16:00 | 134.91 | 106.98
2018-11-06 16:30 | 138.13 | 110.46
2018-11-06 17:00 | 139.03 | 113.27
2018-11-06 17:30 | 137.55 | 113.14
2018-11-06 18:00 | 135.74 | 112.19
2018-11-06 18:30 | 130.09 | 106.91
2018-11-06 19:00 | 132.93 | 109.72
2018-11-06 19:30 | 146.1 | 122.82
2018-11-06 20:00 | 146.98 | 125.32
2018-11-06 20:30 | 142.01 | 119.32
2018-11-06 21:00 | 139.73 | 117.1
2018-11-06 21:30 | 135.44 | 112.53
2018-11-06 22:00 | 131.01 | 106.49
2018-11-06 22:30 | 132.39 | 108.68
2018-11-06 23:00 | 135.51 | 113.07
2018-11-06 23:30 | 133.79 | 110.8
2018-11-07 | 128.9 | 105.98
2018-11-07 00:30 | 132.53 | 109.41
2018-11-07 01:00 | 136.51 | 113.05
2018-11-07 01:30 | 133.9 | 110.35
2018-11-07 02:00 | 129.53 | 105.65
2018-11-07 02:30 | 126.28 | 102.68
2018-11-07 03:00 | 120.24 | 94.69
2018-11-07 03:30 | 119.73 | 93.56
2018-11-07 04:00 | 120.16 | 94.52
2018-11-07 04:30 | 120.37 | 96.93
2018-11-07 05:00 | 120.44 | 96.83
2018-11-07 05:30 | 124.87 | 100.9
2018-11-07 06:00 | 123.91 | 98.02
2018-11-07 06:30 | 113.82 | 83.96
2018-11-07 07:00 | 118.65 | 88.34
2018-11-07 07:30 | 125.47 | 95.87
2018-11-07 08:00 | 120.97 | 89.88
2018-11-07 08:30 | 122.61 | 87.99
2018-11-07 09:00 | 121.25 | 85.3
2018-11-07 09:30 | 119.03 | 80.94
2018-11-07 10:00 | 114.96 | 76.5
2018-11-07 10:30 | 119.01 | 81.4
2018-11-07 11:00 | 122.15 | 84.75
2018-11-07 11:30 | 124.84 | 90.79
2018-11-07 12:00 | 127.59 | 92.56
2018-11-07 12:30 | 133.14 | 98.92
2018-11-07 13:00 | 138.58 | 104.88
2018-11-07 13:30 | 135.93 | 102.46
2018-11-07 14:00 | 133.51 | 100.13
2018-11-07 14:30 | 129.74 | 95.57
2018-11-07 15:00 | 133.24 | 100.15
2018-11-07 15:30 | 137.3 | 105.92
2018-11-07 16:00 | 135.8 | 103.05
2018-11-07 16:30 | 128.36 | 96.95
2018-11-07 17:00 | 131.71 | 102.98
2018-11-07 17:30 | 135.9 | 107.58
2018-11-07 18:00 | 130.84 | 104.51
2018-11-07 18:30 | 135.39 | 110.9
2018-11-07 19:00 | 137.21 | 113.83
2018-11-07 19:30 | 139 | 116.03
2018-11-07 20:00 | 140.09 | 119.03
2018-11-07 20:30 | 136.93 | 114.99
2018-11-07 21:00 | 135.15 | 113.26
2018-11-07 21:30 | 135.76 | 112.76
2018-11-07 22:00 | 137.34 | 114.8
2018-11-07 22:30 | 130.08 | 106.84
2018-11-07 23:00 | 131.53 | 108.79
2018-11-07 23:30 | 128.06 | 105.74
2018-11-08 | 126.32 | 104.55
2018-11-08 00:30 | 132.05 | 109.61
2018-11-08 01:00 | 128.1 | 105.57
2018-11-08 01:30 | 127.41 | 105.28
2018-11-08 02:00 | 136.12 | 112.94
2018-11-08 02:30 | 126.86 | 103.66
2018-11-08 03:00 | 129.21 | 106.47
2018-11-08 03:30 | 124.05 | 101.32
2018-11-08 04:00 | 122.59 | 100.84
2018-11-08 04:30 | 122.5 | 101.54
2018-11-08 05:00 | 116.42 | 94.91
2018-11-08 05:30 | 115.73 | 95.54
2018-11-08 06:00 | 105.53 | 85.83
2018-11-08 06:30 | 104.64 | 85.72
2018-11-08 07:00 | 113.35 | 95.28
2018-11-08 07:30 | 114.94 | 95.94
2018-11-08 08:00 | 113.19 | 95.2
2018-11-08 08:30 | 107.07 | 85.43
2018-11-08 09:00 | 111.07 | 85.17
2018-11-08 09:30 | 105.78 | 76.4
2018-11-08 10:00 | 110.36 | 79.07
2018-11-08 10:30 | 105.56 | 70.43
2018-11-08 11:00 | 109.81 | 73.58
2018-11-08 11:30 | 104.02 | 69.32
2018-11-08 12:00 | 107.11 | 73.5
2018-11-08 12:30 | 111.34 | 78.72
2018-11-08 13:00 | 111.6 | 78.28
2018-11-08 13:30 | 112.94 | 78.7
2018-11-08 14:00 | 114.94 | 80.34
2018-11-08 14:30 | 116.29 | 82.96
2018-11-08 15:00 | 125.06 | 93.26
2018-11-08 15:30 | 110.93 | 83.04
2018-11-08 16:00 | 111.12 | 80.25
2018-11-08 16:30 | 125.08 | 82.77
2018-11-08 17:00 | 112.28 | 74.7
2018-11-08 17:30 | 111.06 | 78.2
2018-11-08 18:00 | 112.43 | 86.64
2018-11-08 18:30 | 115.39 | 91.62
2018-11-08 19:00 | 124.63 | 102.95
2018-11-08 19:30 | 124.26 | 102.2
2018-11-08 20:00 | 126.97 | 105.57
2018-11-08 20:30 | 121.52 | 98.87
2018-11-08 21:00 | 120.8 | 96.72
2018-11-08 21:30 | 109.81 | 85.31
2018-11-08 22:00 | 119.44 | 95.29
2018-11-08 22:30 | 117.44 | 93.48
2018-11-08 23:00 | 118.14 | 93.71
2018-11-08 23:30 | 117.14 | 92.84
2018-11-09 | 115.94 | 92.14
2018-11-09 00:30 | 122.28 | 100.08
2018-11-09 01:00 | 116.55 | 92.44
2018-11-09 01:30 | 120.79 | 96.97
2018-11-09 02:00 | 118.1 | 93.65
2018-11-09 02:30 | 125.03 | 101.08
2018-11-09 03:00 | 120.93 | 97.87
2018-11-09 03:30 | 120.24 | 97.54
2018-11-09 04:00 | 118.19 | 97.06
2018-11-09 04:30 | 125.39 | 102.34
2018-11-09 05:00 | 119.57 | 94.78
2018-11-09 05:30 | 118.27 | 92.12
2018-11-09 06:00 | 117.14 | 92.07
2018-11-09 06:30 | 108.07 | 72.59
2018-11-09 07:00 | 111.63 | 71.11
2018-11-09 07:30 | 121.96 | 83.14
2018-11-09 08:00 | 116.58 | 77.29
2018-11-09 08:30 | 119 | 78.8
2018-11-09 09:00 | 114.98 | 73.44
2018-11-09 09:30 | 122.52 | 83.66
2018-11-09 10:00 | 127.75 | 91.36
2018-11-09 10:30 | 121.63 | 82.19
2018-11-09 11:00 | 120.2 | 81.78
2018-11-09 11:30 | 112.69 | 72.83
2018-11-09 12:00 | 114.14 | 74.79
2018-11-09 12:30 | 116.64 | 77.34
2018-11-09 13:00 | 113.32 | 76.37
2018-11-09 13:30 | 118.32 | 82.9
2018-11-09 14:00 | 116.53 | 78.18
2018-11-09 14:30 | 116.27 | 78.57
2018-11-09 15:00 | 116.03 | 79.76
2018-11-09 15:30 | 114.82 | 80.89
2018-11-09 16:00 | 121.68 | 83.61
2018-11-09 16:30 | 128.62 | 90.5
2018-11-09 17:00 | 123.71 | 86.52
2018-11-09 17:30 | 131.73 | 100.88
2018-11-09 18:00 | 130.35 | 103.55
2018-11-09 18:30 | 120.67 | 95.35
2018-11-09 19:00 | 132.95 | 107.94
2018-11-09 19:30 | 129.81 | 104.83
2018-11-09 20:00 | 134.08 | 108.74
2018-11-09 20:30 | 134.64 | 109.51
2018-11-09 21:00 | 126.52 | 102.57
2018-11-09 21:30 | 132.32 | 107.59
2018-11-09 22:00 | 127.51 | 102.97
2018-11-09 22:30 | 129.03 | 104.79
2018-11-09 23:00 | 130.84 | 106.12
2018-11-09 23:30 | 122.29 | 98.42
2018-11-10 | 116.23 | 91.49
2018-11-10 00:30 | 122.77 | 97.19
2018-11-10 01:00 | 122.24 | 96.03
2018-11-10 01:30 | 126.46 | 101.42
2018-11-10 02:00 | 130.08 | 105.69
2018-11-10 02:30 | 123.26 | 97.93
2018-11-10 03:00 | 123.87 | 97.07
2018-11-10 03:30 | 121.4 | 94.74
2018-11-10 04:00 | 128.7 | 101.82
2018-11-10 04:30 | 126.51 | 100.05
2018-11-10 05:00 | 125.45 | 99.63
2018-11-10 05:30 | 127.09 | 100.84
2018-11-10 06:00 | 124.31 | 98.89
2018-11-10 06:30 | 120.26 | 92.56
2018-11-10 07:00 | 122.84 | 96.08
2018-11-10 07:30 | 125.43 | 97.8
2018-11-10 08:00 | 112.58 | 82.41
2018-11-10 08:30 | 113.38 | 72.87
2018-11-10 09:00 | 115.86 | 75.26
2018-11-10 09:30 | 117.04 | 82.3
2018-11-10 10:00 | 122.6 | 84.93
2018-11-10 10:30 | 117 | 77.68
2018-11-10 11:00 | 111.95 | 74.24
2018-11-10 11:30 | 114.41 | 76.9
2018-11-10 12:00 | 113.72 | 74.72
2018-11-10 12:30 | 117.34 | 79.75
2018-11-10 13:00 | 113.88 | 74.84
2018-11-10 13:30 | 121.74 | 89.95
2018-11-10 14:00 | 126.2 | 99.96
2018-11-10 14:30 | 121.12 | 83.65
2018-11-10 15:00 | 120.34 | 82.29
2018-11-10 15:30 | 115.46 | 82.26
2018-11-10 16:00 | 122.81 | 88.94
2018-11-10 16:30 | 124.97 | 91.43
2018-11-10 17:00 | 128.61 | 95.63
2018-11-10 17:30 | 129.58 | 101.81
2018-11-10 18:00 | 137.96 | 112.75
2018-11-10 18:30 | 129.7 | 103.84
2018-11-10 19:00 | 136.8 | 111.65
2018-11-10 19:30 | 133.87 | 111.11
2018-11-10 20:00 | 131.41 | 107.26
2018-11-10 20:30 | 121.78 | 98.84
2018-11-10 21:00 | 132.29 | 105.06
2018-11-10 21:30 | 127.69 | 100.97
2018-11-10 22:00 | 135.8 | 110.44
2018-11-10 22:30 | 129.86 | 104.12
2018-11-10 23:00 | 133.13 | 108.12
2018-11-10 23:30 | 131.77 | 107.52
2018-11-11 | 130.27 | 105.11
2018-11-11 00:30 | 134.18 | 109.79
2018-11-11 01:00 | 130.67 | 104.79
2018-11-11 01:30 | 132.27 | 105.98
2018-11-11 02:00 | 136.63 | 109.47
2018-11-11 02:30 | 129.54 | 101.83
2018-11-11 03:00 | 128.77 | 101.79
2018-11-11 03:30 | 130.6 | 103.84
2018-11-11 04:00 | 127.82 | 100.85
2018-11-11 04:30 | 126.57 | 100.06
2018-11-11 05:00 | 122.93 | 96.09
2018-11-11 05:30 | 121.19 | 94.28
2018-11-11 06:00 | 122.81 | 97.07
2018-11-11 06:30 | 113.66 | 82.2
2018-11-11 07:00 | 111.1 | 73.8
2018-11-11 07:30 | 113.78 | 76.34
2018-11-11 08:00 | 110.22 | 70.39
2018-11-11 08:30 | 110.24 | 71.67
2018-11-11 09:00 | 110.77 | 71.22
2018-11-11 09:30 | 114.68 | 76.4
2018-11-11 10:00 | 116.61 | 79.21
2018-11-11 10:30 | 118.63 | 82.02
2018-11-11 11:00 | 117.91 | 82.56
2018-11-11 11:30 | 115.42 | 76.68
2018-11-11 12:00 | 113.77 | 75.44
2018-11-11 12:30 | 123.8 | 89.49
2018-11-11 13:00 | 121.49 | 85.71
2018-11-11 13:30 | 123.74 | 88.12
2018-11-11 14:00 | 114.94 | 76.96
2018-11-11 14:30 | 112.44 | 73.55
2018-11-11 15:00 | 115.52 | 78.77
2018-11-11 15:30 | 116.78 | 79.6
2018-11-11 16:00 | 117.95 | 82.44
2018-11-11 16:30 | 123.9 | 91.21
2018-11-11 17:00 | 123.38 | 92.42
2018-11-11 17:30 | 124.22 | 97.58
2018-11-11 18:00 | 127.11 | 103.23
2018-11-11 18:30 | 125.14 | 101.69
2018-11-11 19:00 | 121.05 | 98.49
2018-11-11 19:30 | 122.27 | 99.78
2018-11-11 20:00 | 126.41 | 104.78
2018-11-11 20:30 | 127.22 | 106
2018-11-11 21:00 | 122.46 | 100.81
2018-11-11 21:30 | 123.89 | 101.47
2018-11-11 22:00 | 129.92 | 106.4
2018-11-11 22:30 | 125.93 | 103.4
2018-11-11 23:00 | 130.82 | 108.75
2018-11-11 23:30 | 127.16 | 105.04
2018-11-12 | 130.5 | 108.46
2018-11-12 00:30 | 127.21 | 106.38
2018-11-12 01:00 | 124.9 | 103.94
2018-11-12 01:30 | 114.33 | 91.53
2018-11-12 02:00 | 117.12 | 95.96
2018-11-12 02:30 | 120.18 | 98.05
2018-11-12 03:00 | 117.99 | 93.85
2018-11-12 03:30 | 116.64 | 91.57
2018-11-12 04:00 | 117.87 | 94.15
2018-11-12 04:30 | 126.86 | 103.34
2018-11-12 05:00 | 132.43 | 107.48
2018-11-12 05:30 | 124.23 | 97.77
2018-11-12 06:00 | 117.42 | 89.82
2018-11-12 06:30 | 119.5 | 91.74
2018-11-12 07:00 | 124.36 | 95.77
2018-11-12 07:30 | 125.65 | 95.36
2018-11-12 08:00 | 133.77 | 99.27
2018-11-12 08:30 | 125.83 | 88.54
2018-11-12 09:00 | 112.42 | 67.82
2018-11-12 09:30 | 109.57 | 65.79
2018-11-12 10:00 | 118.3 | 72.06
2018-11-12 10:30 | 118.88 | 77.35
2018-11-12 11:00 | 122.76 | 79.78
2018-11-12 11:30 | 122.96 | 77.26
2018-11-12 12:00 | 119.07 | 71.6
2018-11-12 12:30 | 119.52 | 73.59
2018-11-12 13:00 | 130.34 | 89.04
2018-11-12 13:30 | 132.13 | 86.41
2018-11-12 14:00 | 129.83 | 82.62
2018-11-12 14:30 | 126.08 | 79.8
2018-11-12 15:00 | 128.69 | 80.66
2018-11-12 15:30 | 115.16 | 70.24
2018-11-12 16:00 | 119.57 | 77.86
2018-11-12 16:30 | 121.98 | 83.88
2018-11-12 17:00 | 118.66 | 82.69
2018-11-12 17:30 | 121.69 | 88.04
2018-11-12 18:00 | 124.44 | 94.34
2018-11-12 18:30 | 122.24 | 93.53
2018-11-12 19:00 | 128.65 | 100.23
2018-11-12 19:30 | 127.16 | 97.72
2018-11-12 20:00 | 128.15 | 99.3
2018-11-12 20:30 | 124.7 | 94.85
2018-11-12 21:00 | 129.08 | 98.14
2018-11-12 21:30 | 138.63 | 109.58
2018-11-12 22:00 | 133.55 | 105.25
2018-11-12 22:30 | 136.09 | 108.96
2018-11-12 23:00 | 126.65 | 102.02
2018-11-12 23:30 | 129.63 | 102.84
2018-11-13 | 119.02 | 90.78
2018-11-13 00:30 | 122.73 | 95.17
2018-11-13 01:00 | 122.91 | 94.56
2018-11-13 01:30 | 127.51 | 100.15
2018-11-13 02:00 | 124.42 | 95.64
2018-11-13 02:30 | 127.06 | 98.83
2018-11-13 03:00 | 127.99 | 100.35
2018-11-13 03:30 | 131.91 | 104.3
2018-11-13 04:00 | 132.36 | 104.34
2018-11-13 04:30 | 124.73 | 96.48
2018-11-13 05:00 | 132.12 | 105.3
2018-11-13 05:30 | 124.96 | 96.17
2018-11-13 06:00 | 122.97 | 92.46
2018-11-13 06:30 | 118.15 | 82.17
2018-11-13 07:00 | 119.87 | 78.59
2018-11-13 07:30 | 119.32 | 76.3
2018-11-13 08:00 | 122.68 | 80.18
2018-11-13 08:30 | 116.9 | 70.41
2018-11-13 09:00 | 120.11 | 75.99
2018-11-13 09:30 | 121.46 | 77.22
2018-11-13 10:00 | 121.36 | 79.83
2018-11-13 10:30 | 120.48 | 77.84
2018-11-13 11:00 | 120.34 | 77.13
2018-11-13 11:30 | 122.38 | 79.41
2018-11-13 12:00 | 121.86 | 75.69
2018-11-13 12:30 | 122.48 | 77.07
2018-11-13 13:00 | 117.84 | 72.95
2018-11-13 13:30 | 125.26 | 81.12
2018-11-13 14:00 | 122.48 | 77.81
2018-11-13 14:30 | 118.8 | 72.96
2018-11-13 15:00 | 122.41 | 79.73
2018-11-13 15:30 | 124.27 | 83.2
2018-11-13 16:00 | 122.82 | 83.86
2018-11-13 16:30 | 126.69 | 83.58
2018-11-13 17:00 | 126.05 | 82.86
2018-11-13 17:30 | 131.04 | 93.34
2018-11-13 18:00 | 133.62 | 103.53
2018-11-13 18:30 | 127.3 | 98.09
2018-11-13 19:00 | 130.41 | 100.95
2018-11-13 19:30 | 139.04 | 110.31
2018-11-13 20:00 | 139.93 | 111.41
2018-11-13 20:30 | 137.15 | 107.77
2018-11-13 21:00 | 134.86 | 104.53
2018-11-13 21:30 | 137.89 | 107.46
2018-11-13 22:00 | 138.76 | 108.13
2018-11-13 22:30 | 131.36 | 100.65
2018-11-13 23:00 | 136.21 | 106.89
2018-11-13 23:30 | 129.04 | 101.65
2018-11-14 | 124.92 | 95.6
2018-11-14 00:30 | 127.96 | 98.1
2018-11-14 01:00 | 126.57 | 95.58
2018-11-14 01:30 | 133.89 | 103.63
2018-11-14 02:00 | 135.37 | 105.44
2018-11-14 02:30 | 131.29 | 100.7
2018-11-14 03:00 | 123.69 | 93.21
2018-11-14 03:30 | 120.1 | 92.22
2018-11-14 04:00 | 118.31 | 91.32
2018-11-14 04:30 | 108.34 | 83.49
2018-11-14 05:00 | 107.04 | 83.13
2018-11-14 05:30 | 108.43 | 84.98
2018-11-14 06:00 | 108.3 | 85.13
2018-11-14 06:30 | 93.05 | 64.14
2018-11-14 07:00 | 92.64 | 60.11
2018-11-14 07:30 | 95.74 | 61.75
2018-11-14 08:00 | 94.52 | 60.44
2018-11-14 08:30 | 93.97 | 61.47
2018-11-14 09:00 | 90.61 | 57.11
2018-11-14 09:30 | 90.69 | 55.53
2018-11-14 10:00 | 91.56 | 57.55
2018-11-14 10:30 | 96.31 | 64.57
2018-11-14 11:00 | 95.92 | 66.86
2018-11-14 11:30 | 92.34 | 60.69
2018-11-14 12:00 | 94.23 | 59.98
2018-11-14 12:30 | 98.81 | 67.54
2018-11-14 13:00 | 96.31 | 63.75
2018-11-14 13:30 | 97.61 | 64.65
2018-11-14 14:00 | 98.88 | 66.01
2018-11-14 14:30 | 98 | 67.19
2018-11-14 15:00 | 102.19 | 76.14
2018-11-14 15:30 | 103.73 | 78.15
2018-11-14 16:00 | 101.53 | 73.77
2018-11-14 16:30 | 97.43 | 70.14
2018-11-14 17:00 | 101.88 | 77.72
2018-11-14 17:30 | 99.09 | 80.79
2018-11-14 18:00 | 99.39 | 82.52
2018-11-14 18:30 | 99.99 | 83.6
2018-11-14 19:00 | 113.44 | 97
2018-11-14 19:30 | 119.1 | 103.22
2018-11-14 20:00 | 112.68 | 96.53
2018-11-14 20:30 | 109.25 | 92.08
2018-11-14 21:00 | 108.62 | 90.54
2018-11-14 21:30 | 109.74 | 90.53
2018-11-14 22:00 | 113.46 | 95.41
2018-11-14 22:30 | 124.15 | 106.52
2018-11-14 23:00 | 109.43 | 90.74
2018-11-14 23:30 | 108.78 | 89.58
2018-11-15 | 112.65 | 94.15
2018-11-15 00:30 | 109.89 | 92.84
2018-11-15 01:00 | 107.5 | 90.21
2018-11-15 01:30 | 101.59 | 84.01
2018-11-15 02:00 | 110.53 | 93.02
2018-11-15 02:30 | 102.82 | 84.85
2018-11-15 03:00 | 103.63 | 85.74
2018-11-15 03:30 | 100.15 | 81.71
2018-11-15 04:00 | 99.33 | 82.42
2018-11-15 04:30 | 103.28 | 85.41
2018-11-15 05:00 | 98.4 | 80.32
2018-11-15 05:30 | 100.23 | 81.29
2018-11-15 06:00 | 98.42 | 78.02
2018-11-15 06:30 | 91.84 | 66.58
2018-11-15 07:00 | 98.16 | 67.57
2018-11-15 07:30 | 93.26 | 61.48
2018-11-15 08:00 | 94.9 | 62.57
2018-11-15 08:30 | 97.93 | 64.4
2018-11-15 09:00 | 96.89 | 62.89
2018-11-15 09:30 | 96.94 | 63.64
2018-11-15 10:00 | 94.19 | 60.09
2018-11-15 10:30 | 93.23 | 60.26
2018-11-15 11:00 | 95.43 | 62.85
2018-11-15 11:30 | 99.64 | 67.7
2018-11-15 12:00 | 99.98 | 70
2018-11-15 12:30 | 95.71 | 66.23
2018-11-15 13:00 | 102.74 | 73.62
2018-11-15 13:30 | 95.53 | 67.4
2018-11-15 14:00 | 102.96 | 73.87
2018-11-15 14:30 | 105.24 | 75.62
2018-11-15 15:00 | 99.83 | 69.43
2018-11-15 15:30 | 103.61 | 74.7
2018-11-15 16:00 | 108.45 | 80.65
2018-11-15 16:30 | 108.03 | 87.81
2018-11-15 17:00 | 115.36 | 97.14
2018-11-15 17:30 | 114.64 | 95.79
2018-11-15 18:00 | 110.6 | 91.32
2018-11-15 18:30 | 106.75 | 88.13
2018-11-15 19:00 | 125.19 | 104.73
2018-11-15 19:30 | 123.95 | 103.3
2018-11-15 20:00 | 125.68 | 103.81
2018-11-15 20:30 | 126.53 | 104.85
2018-11-15 21:00 | 126.6 | 103.65
2018-11-15 21:30 | 122.05 | 98.67
2018-11-15 22:00 | 121.77 | 98.15
2018-11-15 22:30 | 122.7 | 100.98
2018-11-15 23:00 | 116.75 | 93.81
2018-11-15 23:30 | 115.5 | 93.56
2018-11-16 | 118.97 | 97.66
2018-11-16 00:30 | 117.84 | 96.39
2018-11-16 01:00 | 113.65 | 91.52
2018-11-16 01:30 | 111.59 | 89.37
2018-11-16 02:00 | 113.73 | 91.78
2018-11-16 02:30 | 113.14 | 90.14
2018-11-16 03:00 | 114.22 | 91.28
2018-11-16 03:30 | 110.33 | 86.99
2018-11-16 04:00 | 109.16 | 85.86
2018-11-16 04:30 | 109.39 | 87.67
2018-11-16 05:00 | 117.23 | 96.19
2018-11-16 05:30 | 117.53 | 95.9
2018-11-16 06:00 | 114.43 | 91.78
2018-11-16 06:30 | 113.74 | 86.17
2018-11-16 07:00 | 112.66 | 79.95
2018-11-16 07:30 | 114.45 | 79.65
2018-11-16 08:00 | 117.63 | 81.85
2018-11-16 08:30 | 116.62 | 80.9
2018-11-16 09:00 | 120.43 | 86.46
2018-11-16 09:30 | 117.31 | 84.89
2018-11-16 10:00 | 123.11 | 93.68
2018-11-16 10:30 | 113.65 | 82.21
2018-11-16 11:00 | 111.65 | 78.67
2018-11-16 11:30 | 121.21 | 82.46
2018-11-16 12:00 | 123.72 | 81.39
2018-11-16 12:30 | 120.23 | 77.66
2018-11-16 13:00 | 120.06 | 75.58
2018-11-16 13:30 | 125.51 | 81.74
2018-11-16 14:00 | 116.17 | 78.8
2018-11-16 14:30 | 114.55 | 84.1
2018-11-16 15:00 | 123.62 | 85.61
2018-11-16 15:30 | 128.62 | 86.25
2018-11-16 16:00 | 124.36 | 80.86
2018-11-16 16:30 | 125.72 | 84.59
2018-11-16 17:00 | 126.48 | 85.86
2018-11-16 17:30 | 131.22 | 99.5
2018-11-16 18:00 | 128.14 | 99.12
2018-11-16 18:30 | 133.44 | 107.44
2018-11-16 19:00 | 140.46 | 114.07
2018-11-16 19:30 | 129.68 | 100.58
2018-11-16 20:00 | 131.82 | 102.77
2018-11-16 20:30 | 135.42 | 106.16
2018-11-16 21:00 | 131.55 | 102.65
2018-11-16 21:30 | 129.16 | 98.88
2018-11-16 22:00 | 125.74 | 95.58
2018-11-16 22:30 | 125.34 | 98.09
2018-11-16 23:00 | 130.82 | 104.4
2018-11-16 23:30 | 123.63 | 96.35
2018-11-17 | 126.43 | 97.84
2018-11-17 00:30 | 130.27 | 104.24
2018-11-17 01:00 | 129.83 | 102.53
2018-11-17 01:30 | 128.57 | 101.64
2018-11-17 02:00 | 129.56 | 102.01
2018-11-17 02:30 | 125.1 | 98.24
2018-11-17 03:00 | 123.74 | 96.35
2018-11-17 03:30 | 122.32 | 94.78
2018-11-17 04:00 | 126.48 | 98.94
2018-11-17 04:30 | 129.99 | 102.91
2018-11-17 05:00 | 130.21 | 102.45
2018-11-17 05:30 | 128.52 | 103.03
2018-11-17 06:00 | 123.38 | 95.98
2018-11-17 06:30 | 119.65 | 88.88
2018-11-17 07:00 | 121.19 | 84.96
2018-11-17 07:30 | 114.05 | 70.16
2018-11-17 08:00 | 117.95 | 74.91
2018-11-17 08:30 | 125.55 | 81.51
2018-11-17 09:00 | 120.78 | 74.12
2018-11-17 09:30 | 116.95 | 72.19
2018-11-17 10:00 | 114.43 | 72.29
2018-11-17 10:30 | 119.56 | 81.21
2018-11-17 11:00 | 119.36 | 77.43
2018-11-17 11:30 | 128.77 | 85.72
2018-11-17 12:00 | 129.02 | 88.12
2018-11-17 12:30 | 132.57 | 88.18
2018-11-17 13:00 | 125.97 | 83.98
2018-11-17 13:30 | 130.98 | 85.94
2018-11-17 14:00 | 125.44 | 89.03
2018-11-17 14:30 | 130.68 | 84.96
2018-11-17 15:00 | 129.07 | 83.77
2018-11-17 15:30 | 131.66 | 89.63
2018-11-17 16:00 | 128.31 | 86.01
2018-11-17 16:30 | 126.31 | 89.04
2018-11-17 17:00 | 138.23 | 107.71
2018-11-17 17:30 | 138.54 | 108.82
2018-11-17 18:00 | 139.9 | 113.51
2018-11-17 18:30 | 133.52 | 106.54
2018-11-17 19:00 | 137.57 | 108.33
2018-11-17 19:30 | 134.97 | 106.8
2018-11-17 20:00 | 137.35 | 109.83
2018-11-17 20:30 | 135.97 | 108.03
2018-11-17 21:00 | 132.37 | 105.39
2018-11-17 21:30 | 135.62 | 110.08
2018-11-17 22:00 | 136.24 | 110.29
2018-11-17 22:30 | 125.8 | 98
2018-11-17 23:00 | 125.84 | 98.25
2018-11-17 23:30 | 129.64 | 103.25
2018-11-18 | 131.57 | 104.61
2018-11-18 00:30 | 133.53 | 106.9
2018-11-18 01:00 | 130.23 | 105.18
2018-11-18 01:30 | 133.04 | 105.44
2018-11-18 02:00 | 127.58 | 98.99
2018-11-18 02:30 | 124.69 | 95.19
2018-11-18 03:00 | 124.9 | 97.55
2018-11-18 03:30 | 131.54 | 105.77
2018-11-18 04:00 | 126.77 | 100.88
2018-11-18 04:30 | 134.72 | 107.84
2018-11-18 05:00 | 129.8 | 102.81
2018-11-18 05:30 | 130.89 | 104.31
2018-11-18 06:00 | 126.95 | 99.55
2018-11-18 06:30 | 120.4 | 91.66
2018-11-18 07:00 | 128.15 | 90.89
2018-11-18 07:30 | 132.46 | 97.06
2018-11-18 08:00 | 132.84 | 87.17
2018-11-18 08:30 | 134.1 | 91.48
2018-11-18 09:00 | 129.28 | 86.29
2018-11-18 09:30 | 127.45 | 77.05
2018-11-18 10:00 | 132.06 | 82.95
2018-11-18 10:30 | 130.94 | 85.43
2018-11-18 11:00 | 131.03 | 84.06
2018-11-18 11:30 | 129.51 | 83.58
2018-11-18 12:00 | 129.63 | 86.19
2018-11-18 12:30 | 129.33 | 95.13
2018-11-18 13:00 | 130.44 | 87.71
2018-11-18 13:30 | 130.32 | 83.77
2018-11-18 14:00 | 131.91 | 88.54
2018-11-18 14:30 | 132.66 | 92.93
2018-11-18 15:00 | 130.94 | 98.91
2018-11-18 15:30 | 136.61 | 105.01
2018-11-18 16:00 | 140.25 | 103.58
2018-11-18 16:30 | 131.26 | 91.7
2018-11-18 17:00 | 129.31 | 90.76
2018-11-18 17:30 | 132.86 | 100.26
2018-11-18 18:00 | 133.62 | 103.45
2018-11-18 18:30 | 130.2 | 103.69
2018-11-18 19:00 | 135.05 | 110.06
2018-11-18 19:30 | 138.58 | 115.26
2018-11-18 20:00 | 142.08 | 118.41
2018-11-18 20:30 | 128.02 | 103.12
2018-11-18 21:00 | 116.19 | 93.72
2018-11-18 21:30 | 104.35 | 84.65
2018-11-18 22:00 | 101.92 | 82.27
2018-11-18 22:30 | 106.5 | 86.95
2018-11-18 23:00 | 101.99 | 81.75
2018-11-18 23:30 | 99.94 | 77.54
2018-11-19 | 108.07 | 86.4
2018-11-19 00:30 | 110.07 | 88.19
2018-11-19 01:00 | 106.52 | 82.09
2018-11-19 01:30 | 112.18 | 87.58
2018-11-19 02:00 | 109.47 | 84.35
2018-11-19 02:30 | 118.72 | 96.02
2018-11-19 03:00 | 118.26 | 95.67
2018-11-19 03:30 | 115.85 | 91.54
2018-11-19 04:00 | 119.66 | 95.87
2018-11-19 04:30 | 121.86 | 99.5
2018-11-19 05:00 | 117.66 | 95.5
2018-11-19 05:30 | 118.83 | 97.65
2018-11-19 06:00 | 115.39 | 93.1
2018-11-19 06:30 | 110.95 | 85.31
2018-11-19 07:00 | 109.75 | 81.81
2018-11-19 07:30 | 115.18 | 89.71
2018-11-19 08:00 | 118.89 | 90.52
2018-11-19 08:30 | 112.82 | 91.82
2018-11-19 09:00 | 110.82 | 83.11
2018-11-19 09:30 | 108.43 | 82.68
2018-11-19 10:00 | 114.71 | 87.22
2018-11-19 10:30 | 124.08 | 93.09
2018-11-19 11:00 | 117.54 | 81.22
2018-11-19 11:30 | 115.93 | 79.62
2018-11-19 12:00 | 112.66 | 80.42
2018-11-19 12:30 | 112.99 | 74.22
2018-11-19 13:00 | 113.61 | 76.39
2018-11-19 13:30 | 110.76 | 76.06
2018-11-19 14:00 | 114.9 | 86.76
2018-11-19 14:30 | 114.36 | 88.27
2018-11-19 15:00 | 115.81 | 80.38
2018-11-19 15:30 | 106.62 | 74.01
2018-11-19 16:00 | 109.67 | 73.55
2018-11-19 16:30 | 117.23 | 82.83
2018-11-19 17:00 | 115.18 | 78.77
2018-11-19 17:30 | 118.3 | 86.51
2018-11-19 18:00 | 118.33 | 90.38
2018-11-19 18:30 | 115.84 | 88.95
2018-11-19 19:00 | 127.92 | 103.98
2018-11-19 19:30 | 125.38 | 101.63
2018-11-19 20:00 | 126.74 | 101.95
2018-11-19 20:30 | 129.21 | 107.4
2018-11-19 21:00 | 123.82 | 101.22
2018-11-19 21:30 | 128.15 | 106.56
2018-11-19 22:00 | 131.6 | 110.32
2018-11-19 22:30 | 122.6 | 101.3
2018-11-19 23:00 | 125.82 | 105.19
2018-11-19 23:30 | 128.53 | 106.51
2018-11-20 | 126.62 | 104.41
2018-11-20 00:30 | 132.44 | 109.52
2018-11-20 01:00 | 126.83 | 101.83
2018-11-20 01:30 | 127.7 | 103.37
2018-11-20 02:00 | 127.95 | 104.1
2018-11-20 02:30 | 129.04 | 104.67
2018-11-20 03:00 | 121.5 | 97.29
2018-11-20 03:30 | 121.57 | 96.44
2018-11-20 04:00 | 124.47 | 99.43
2018-11-20 04:30 | 116.42 | 90.16
2018-11-20 05:00 | 117.09 | 92.63
2018-11-20 05:30 | 124.6 | 101.7
2018-11-20 06:00 | 120.66 | 96.4
2018-11-20 06:30 | 112.18 | 79.93
2018-11-20 07:00 | 119.35 | 93.15
2018-11-20 07:30 | 120.62 | 93.58
2018-11-20 08:00 | 109.52 | 80.32
2018-11-20 08:30 | 116.83 | 88.1
2018-11-20 09:00 | 119.02 | 88.07
2018-11-20 09:30 | 118.44 | 85.99
2018-11-20 10:00 | 116.35 | 76.03
2018-11-20 10:30 | 120.79 | 81.14
2018-11-20 11:00 | 121.77 | 80.43
2018-11-20 11:30 | 116.85 | 76.35
2018-11-20 12:00 | 120.53 | 79.19
2018-11-20 12:30 | 117.78 | 78.99
2018-11-20 13:00 | 117.91 | 78.14
2018-11-20 13:30 | 120.36 | 79.44
2018-11-20 14:00 | 121.82 | 82.3
2018-11-20 14:30 | 115.4 | 75.58
2018-11-20 15:00 | 122 | 83.51
2018-11-20 15:30 | 120.78 | 76.48
2018-11-20 16:00 | 124.02 | 84.78
2018-11-20 16:30 | 130.8 | 91.48
2018-11-20 17:00 | 129.82 | 95.3
2018-11-20 17:30 | 128.44 | 95.2
2018-11-20 18:00 | 127.62 | 99.6
2018-11-20 18:30 | 134.22 | 107.34
2018-11-20 19:00 | 141.56 | 114.8
2018-11-20 19:30 | 132.49 | 107.58
2018-11-20 20:00 | 130.49 | 104.71
2018-11-20 20:30 | 130.44 | 104.46
2018-11-20 21:00 | 108.74 | 86.68
2018-11-20 21:30 | 109.77 | 88.57
2018-11-20 22:00 | 108.22 | 87.19
2018-11-20 22:30 | 108.27 | 86.35
2018-11-20 23:00 | 106.58 | 87.22
2018-11-20 23:30 | 112.98 | 95.38
2018-11-21 | 103.47 | 84.72
2018-11-21 00:30 | 106.85 | 87.53
2018-11-21 01:00 | 119.71 | 101
2018-11-21 01:30 | 127.88 | 108.61
2018-11-21 02:00 | 123.53 | 103.8
2018-11-21 02:30 | 120.35 | 99
2018-11-21 03:00 | 119.77 | 98.2
2018-11-21 03:30 | 113.59 | 92.37
2018-11-21 04:00 | 118.18 | 96.42
2018-11-21 04:30 | 117.73 | 96.23
2018-11-21 05:00 | 103.6 | 83.26
2018-11-21 05:30 | 98.94 | 78.95
2018-11-21 06:00 | 105.7 | 86.99
2018-11-21 06:30 | 94.15 | 74.87
2018-11-21 07:00 | 95.16 | 64.86
2018-11-21 07:30 | 99.43 | 59.21
2018-11-21 08:00 | 100.7 | 56.65
2018-11-21 08:30 | 101.48 | 56.32
2018-11-21 09:00 | 103.82 | 57.23
2018-11-21 09:30 | 106.24 | 67.33
2018-11-21 10:00 | 111.94 | 70.96
2018-11-21 10:30 | 112.57 | 71.05
2018-11-21 11:00 | 109.91 | 68
2018-11-21 11:30 | 111.76 | 69.18
2018-11-21 12:00 | 115.2 | 74.63
2018-11-21 12:30 | 108.35 | 71.32
2018-11-21 13:00 | 112.43 | 80.06
2018-11-21 13:30 | 115.14 | 85.24
2018-11-21 14:00 | 120.22 | 81.41
2018-11-21 14:30 | 119.94 | 91.48
2018-11-21 15:00 | 115.55 | 87.96
2018-11-21 15:30 | 110.95 | 83.74
2018-11-21 16:00 | 110.73 | 80.91
2018-11-21 16:30 | 113.05 | 86.29
2018-11-21 17:00 | 120.11 | 96.73
2018-11-21 17:30 | 121.77 | 100.49
2018-11-21 18:00 | 124.41 | 101.49
2018-11-21 18:30 | 120.27 | 96.25
2018-11-21 19:00 | 118.79 | 96
2018-11-21 19:30 | 126.07 | 104.29
2018-11-21 20:00 | 122.56 | 100.32
2018-11-21 20:30 | 122.27 | 99.38
2018-11-21 21:00 | 119.53 | 96.4
2018-11-21 21:30 | 121.75 | 99.05
2018-11-21 22:00 | 117.05 | 93.42
2018-11-21 22:30 | 127.9 | 106.67
2018-11-21 23:00 | 122.15 | 98.81
2018-11-21 23:30 | 113.52 | 89.29
2018-11-22 | 112.35 | 87.98
2018-11-22 00:30 | 105.17 | 79.25
2018-11-22 01:00 | 113.42 | 88.47
2018-11-22 01:30 | 116.17 | 91.01
2018-11-22 02:00 | 115.63 | 91.4
2018-11-22 02:30 | 115.78 | 92.01
2018-11-22 03:00 | 112.59 | 88.45
2018-11-22 03:30 | 111.2 | 88.31
2018-11-22 04:00 | 123.23 | 101.86
2018-11-22 04:30 | 116.42 | 94.51
2018-11-22 05:00 | 117.09 | 94.34
2018-11-22 05:30 | 113.24 | 89.91
2018-11-22 06:00 | 112.23 | 88.07
2018-11-22 06:30 | 109.81 | 82.92
2018-11-22 07:00 | 104.48 | 78.69
2018-11-22 07:30 | 104.77 | 80.25
2018-11-22 08:00 | 102.64 | 78.35
2018-11-22 08:30 | 101.03 | 78.11
2018-11-22 09:00 | 98.31 | 68.62
2018-11-22 09:30 | 95.11 | 66.95
2018-11-22 10:00 | 95.93 | 65.27
2018-11-22 10:30 | 104.09 | 69.92
2018-11-22 11:00 | 109.57 | 73.25
2018-11-22 11:30 | 104.62 | 71.78
2018-11-22 12:00 | 111.01 | 76.29
2018-11-22 12:30 | 113.84 | 80.63
2018-11-22 13:00 | 112.97 | 83.31
2018-11-22 13:30 | 109.05 | 73.79
2018-11-22 14:00 | 113.73 | 80.03
2018-11-22 14:30 | 113.72 | 78.83
2018-11-22 15:00 | 113.17 | 83.03
2018-11-22 15:30 | 117.1 | 81.25
2018-11-22 16:00 | 121.83 | 83.05
2018-11-22 16:30 | 141.06 | 84
2018-11-22 17:00 | 151.17 | 81.6
2018-11-22 17:30 | 147.28 | 87.4
2018-11-22 18:00 | 142.28 | 94.65
2018-11-22 18:30 | 137.78 | 99.11
2018-11-22 19:00 | 137.61 | 107.84
2018-11-22 19:30 | 143.01 | 112.46
2018-11-22 20:00 | 140.01 | 107.4
2018-11-22 20:30 | 137.31 | 103.29
2018-11-22 21:00 | 137.02 | 102.28
2018-11-22 21:30 | 135.39 | 101.02
2018-11-22 22:00 | 139.74 | 105.44
2018-11-22 22:30 | 143.79 | 109.21
2018-11-22 23:00 | 133.32 | 97.93
2018-11-22 23:30 | 135.9 | 101.9
2018-11-23 | 136.02 | 101.48
2018-11-23 00:30 | 136.47 | 103.29
2018-11-23 01:00 | 137.2 | 102.25
2018-11-23 01:30 | 134.11 | 98.43
2018-11-23 02:00 | 130.06 | 94.9
2018-11-23 02:30 | 128.74 | 93.23
2018-11-23 03:00 | 125.98 | 89.77
2018-11-23 03:30 | 126.6 | 90.98
2018-11-23 04:00 | 125.77 | 89.59
2018-11-23 04:30 | 127.78 | 91.79
2018-11-23 05:00 | 126.88 | 91.74
2018-11-23 05:30 | 135.67 | 101.63
2018-11-23 06:00 | 133.01 | 97.14
2018-11-23 06:30 | 125.98 | 80.26
2018-11-23 07:00 | 131.92 | 80.28
2018-11-23 07:30 | 135.48 | 78.38
2018-11-23 08:00 | 136.15 | 77.97
2018-11-23 08:30 | 134.41 | 75.1
2018-11-23 09:00 | 135.43 | 78.79
2018-11-23 09:30 | 133 | 73.54
2018-11-23 10:00 | 142.6 | 82.79
2018-11-23 10:30 | 140.5 | 78.87
2018-11-23 11:00 | 139.79 | 78.51
2018-11-23 11:30 | 139 | 77.47
2018-11-23 12:00 | 136.93 | 75.83
2018-11-23 12:30 | 139.56 | 79.73
2018-11-23 13:00 | 136.61 | 76.09
2018-11-23 13:30 | 133.83 | 70.37
2018-11-23 14:00 | 137.4 | 74.81
2018-11-23 14:30 | 137.68 | 74.18
2018-11-23 15:00 | 139.42 | 78.04
2018-11-23 15:30 | 147.07 | 87.58
2018-11-23 16:00 | 145.86 | 85.32
2018-11-23 16:30 | 146.89 | 88.54
2018-11-23 17:00 | 140.69 | 81.9
2018-11-23 17:30 | 139.14 | 89.95
2018-11-23 18:00 | 138.86 | 94.23
2018-11-23 18:30 | 142.5 | 102.24
2018-11-23 19:00 | 148.14 | 109.44
2018-11-23 19:30 | 152.61 | 115.33
2018-11-23 20:00 | 148.58 | 110.87
2018-11-23 20:30 | 148.76 | 110.53
2018-11-23 21:00 | 146.99 | 107.91
2018-11-23 21:30 | 146.52 | 108.29
2018-11-23 22:00 | 143.62 | 105
2018-11-23 22:30 | 147.39 | 107.53
2018-11-23 23:00 | 138.94 | 99.19
2018-11-23 23:30 | 137.26 | 96.43
2018-11-24 | 143.15 | 103.2
2018-11-24 00:30 | 147.8 | 109.38
2018-11-24 01:00 | 142.04 | 102.49
2018-11-24 01:30 | 141.19 | 101.62
2018-11-24 02:00 | 148.25 | 110.88
2018-11-24 02:30 | 146.45 | 107.98
2018-11-24 03:00 | 148.75 | 110.29
2018-11-24 03:30 | 144.36 | 105.59
2018-11-24 04:00 | 141.16 | 100.06
2018-11-24 04:30 | 141.35 | 101.54
2018-11-24 05:00 | 139.69 | 99.92
2018-11-24 05:30 | 145.63 | 106.64
2018-11-24 06:00 | 137.77 | 94.89
2018-11-24 06:30 | 134.66 | 84.12
2018-11-24 07:00 | 136.69 | 80.23
2018-11-24 07:30 | 140.74 | 79.83
2018-11-24 08:00 | 142.6 | 80.58
2018-11-24 08:30 | 142.89 | 81.71
2018-11-24 09:00 | 136.51 | 75.65
2018-11-24 09:30 | 145.81 | 86.91
2018-11-24 10:00 | 142.54 | 82.75
2018-11-24 10:30 | 141.67 | 83.23
2018-11-24 11:00 | 142.94 | 83.45
2018-11-24 11:30 | 134.73 | 76.29
2018-11-24 12:00 | 138.52 | 75.86
2018-11-24 12:30 | 144.25 | 82.11
2018-11-24 13:00 | 145.81 | 85.15
2018-11-24 13:30 | 143.26 | 84.1
2018-11-24 14:00 | 136.94 | 77.32
2018-11-24 14:30 | 141.78 | 85.59
2018-11-24 15:00 | 137.38 | 80.58
2018-11-24 15:30 | 138.16 | 80.3
2018-11-24 16:00 | 137.01 | 81.43
2018-11-24 16:30 | 138.65 | 84.99
2018-11-24 17:00 | 133.81 | 77.84
2018-11-24 17:30 | 137.85 | 90.4
2018-11-24 18:00 | 133.46 | 92.83
2018-11-24 18:30 | 133.81 | 96.18
2018-11-24 19:00 | 140.64 | 104.7
2018-11-24 19:30 | 138.46 | 102.33
2018-11-24 20:00 | 141.09 | 104.87
2018-11-24 20:30 | 137.36 | 102.38
2018-11-24 21:00 | 137.71 | 102.69
2018-11-24 21:30 | 134.64 | 100.82
2018-11-24 22:00 | 135.05 | 101.65
2018-11-24 22:30 | 137.12 | 102.61
2018-11-24 23:00 | 135.33 | 100.98
2018-11-24 23:30 | 134.3 | 100.48
2018-11-25 | 135.24 | 100.62
2018-11-25 00:30 | 132.27 | 96.57
2018-11-25 01:00 | 122.42 | 85.54
2018-11-25 01:30 | 132.84 | 97.31
2018-11-25 02:00 | 135.87 | 101.13
2018-11-25 02:30 | 133.57 | 98.2
2018-11-25 03:00 | 131.43 | 95.06
2018-11-25 03:30 | 131.52 | 94.67
2018-11-25 04:00 | 131.9 | 95.66
2018-11-25 04:30 | 135.23 | 99.9
2018-11-25 05:00 | 133.25 | 97.35
2018-11-25 05:30 | 126.55 | 92.97
2018-11-25 06:00 | 125.94 | 90.26
2018-11-25 06:30 | 124.58 | 84.15
2018-11-25 07:00 | 120.83 | 74.57
2018-11-25 07:30 | 124.58 | 85.5
2018-11-25 08:00 | 121.91 | 82.3
2018-11-25 08:30 | 123.77 | 86.38
2018-11-25 09:00 | 126.19 | 82.14
2018-11-25 09:30 | 125.42 | 81.02
2018-11-25 10:00 | 129.69 | 92.66
2018-11-25 10:30 | 126.39 | 81.65
2018-11-25 11:00 | 131.94 | 79.9
2018-11-25 11:30 | 125.96 | 74.7
2018-11-25 12:00 | 130.89 | 84.76
2018-11-25 12:30 | 126.66 | 78.51
2018-11-25 13:00 | 135.21 | 87.71
2018-11-25 13:30 | 136.36 | 90.41
2018-11-25 14:00 | 143.48 | 98.54
2018-11-25 14:30 | 138.47 | 94.36
2018-11-25 15:00 | 138.82 | 86.22
2018-11-25 15:30 | 128.06 | 78.81
2018-11-25 16:00 | 132.58 | 95.56
2018-11-25 16:30 | 134.25 | 94.2
2018-11-25 17:00 | 145.47 | 106.54
2018-11-25 17:30 | 145.74 | 105.17
2018-11-25 18:00 | 146.6 | 105.84
2018-11-25 18:30 | 141.36 | 106.24
2018-11-25 19:00 | 147.22 | 112.58
2018-11-25 19:30 | 148.18 | 114.4
2018-11-25 20:00 | 138.42 | 102.59
2018-11-25 20:30 | 144.14 | 107.56
2018-11-25 21:00 | 141.28 | 107.13
2018-11-25 21:30 | 134.6 | 102.59
2018-11-25 22:00 | 133.62 | 102.34
2018-11-25 22:30 | 135.74 | 104.74
2018-11-25 23:00 | 137.46 | 107.76
2018-11-25 23:30 | 131.18 | 100.91
2018-11-26 | 129 | 98.46
2018-11-26 00:30 | 132.62 | 103.13
2018-11-26 01:00 | 126.4 | 96.28
2018-11-26 01:30 | 129.81 | 100.82
2018-11-26 02:00 | 129.08 | 101.62
2018-11-26 02:30 | 122.86 | 95.15
2018-11-26 03:00 | 120.09 | 90.39
2018-11-26 03:30 | 121.53 | 91.66
2018-11-26 04:00 | 123.53 | 94.13
2018-11-26 04:30 | 121.6 | 92.07
2018-11-26 05:00 | 120.21 | 90.85
2018-11-26 05:30 | 123.24 | 94.62
2018-11-26 06:00 | 109.41 | 89.55
2018-11-26 06:30 | 103.3 | 79.72
2018-11-26 07:00 | 105.55 | 69.56
2018-11-26 07:30 | 113.88 | 73.7
2018-11-26 08:00 | 112.29 | 68.28
2018-11-26 08:30 | 117.02 | 72.33
2018-11-26 09:00 | 116.76 | 69.38
2018-11-26 09:30 | 110.81 | 65.25
2018-11-26 10:00 | 104.5 | 59.94
2018-11-26 10:30 | 108.48 | 64.16
2018-11-26 11:00 | 118.14 | 75.82
2018-11-26 11:30 | 118.65 | 73.24
2018-11-26 12:00 | 118.95 | 73.41
2018-11-26 12:30 | 120.01 | 74.75
2018-11-26 13:00 | 120.58 | 73.11
2018-11-26 13:30 | 118.55 | 71.62
2018-11-26 14:00 | 122.49 | 76.31
2018-11-26 14:30 | 124.52 | 78.56
2018-11-26 15:00 | 129.88 | 85.31
2018-11-26 15:30 | 127.99 | 83.78
2018-11-26 16:00 | 129.18 | 85.32
2018-11-26 16:30 | 121.02 | 78.46
2018-11-26 17:00 | 122.98 | 82.93
2018-11-26 17:30 | 130.44 | 97.67
2018-11-26 18:00 | 129.17 | 101.93
2018-11-26 18:30 | 125.87 | 100.37
2018-11-26 19:00 | 130.19 | 105.1
2018-11-26 19:30 | 132.99 | 107.31
2018-11-26 20:00 | 123.85 | 99.37
2018-11-26 20:30 | 125.52 | 100.21
2018-11-26 21:00 | 123.88 | 97.79
2018-11-26 21:30 | 122.33 | 96.28
2018-11-26 22:00 | 115.9 | 88.45
2018-11-26 22:30 | 113.28 | 87.01
2018-11-26 23:00 | 114.71 | 88.92
2018-11-26 23:30 | 111.69 | 85.61
2018-11-27 | 116.02 | 92.88
2018-11-27 00:30 | 113.92 | 90.44
2018-11-27 01:00 | 111.02 | 87.33
2018-11-27 01:30 | 110.3 | 86.29
2018-11-27 02:00 | 109.1 | 84.98
2018-11-27 02:30 | 107.87 | 83.94
2018-11-27 03:00 | 110.52 | 87.68
2018-11-27 03:30 | 106.54 | 82.12
2018-11-27 04:00 | 109.34 | 85.75
2018-11-27 04:30 | 109.66 | 86.35
2018-11-27 05:00 | 113.17 | 89.79
2018-11-27 05:30 | 112.55 | 89.08
2018-11-27 06:00 | 110.15 | 83.71
2018-11-27 06:30 | 96.94 | 64.58
2018-11-27 07:00 | 97.71 | 67.39
2018-11-27 07:30 | 104.22 | 77.49
2018-11-27 08:00 | 109.95 | 85.28
2018-11-27 08:30 | 110.85 | 83.24
2018-11-27 09:00 | 112.2 | 85.54
2018-11-27 09:30 | 111.89 | 82.45
2018-11-27 10:00 | 109.77 | 74.5
2018-11-27 10:30 | 113.13 | 79.1
2018-11-27 11:00 | 111.77 | 71.76
2018-11-27 11:30 | 110 | 68.71
2018-11-27 12:00 | 109.08 | 71.14
2018-11-27 12:30 | 108.88 | 79.06
2018-11-27 13:00 | 110.38 | 83.53
2018-11-27 13:30 | 110.74 | 87.69
2018-11-27 14:00 | 113.94 | 89.7
2018-11-27 14:30 | 114.88 | 90.25
2018-11-27 15:00 | 117.74 | 90.63
2018-11-27 15:30 | 120.39 | 89.77
2018-11-27 16:00 | 120.01 | 81.83
2018-11-27 16:30 | 118.53 | 84.22
2018-11-27 17:00 | 114.33 | 81.6
2018-11-27 17:30 | 118.08 | 88.27
2018-11-27 18:00 | 120.2 | 94.02
2018-11-27 18:30 | 124.09 | 99.51
2018-11-27 19:00 | 126.44 | 102.12
2018-11-27 19:30 | 131.49 | 107.66
2018-11-27 20:00 | 130.95 | 106.83
2018-11-27 20:30 | 131.46 | 107.47
2018-11-27 21:00 | 126.88 | 103.21
2018-11-27 21:30 | 127.05 | 102.47
2018-11-27 22:00 | 123.13 | 97.91
2018-11-27 22:30 | 119.86 | 94.59
2018-11-27 23:00 | 117.39 | 91.52
2018-11-27 23:30 | 114.29 | 88.01
2018-11-28 | 115.49 | 90.13
2018-11-28 00:30 | 116.13 | 90.89
2018-11-28 01:00 | 117.33 | 91.65
2018-11-28 01:30 | 114.04 | 88.49
2018-11-28 02:00 | 118.16 | 93.92
2018-11-28 02:30 | 119.71 | 97.23
2018-11-28 03:00 | 117.58 | 94.29
2018-11-28 03:30 | 116.59 | 93.44
2018-11-28 04:00 | 115.87 | 93.89
2018-11-28 04:30 | 113.4 | 92.07
2018-11-28 05:00 | 111.27 | 89.81
2018-11-28 05:30 | 113.81 | 92.15
2018-11-28 06:00 | 109.44 | 86.2
2018-11-28 06:30 | 106.16 | 76.03
2018-11-28 07:00 | 108.07 | 74.6
2018-11-28 07:30 | 118.25 | 74.63
2018-11-28 08:00 | 132.7 | 76.89
2018-11-28 08:30 | 129.29 | 72.46
2018-11-28 09:00 | 133.07 | 74.72
2018-11-28 09:30 | 138.62 | 82.13
2018-11-28 10:00 | 143.21 | 89.45
2018-11-28 10:30 | 144.98 | 90.51
2018-11-28 11:00 | 137.98 | 80.86
2018-11-28 11:30 | 137.69 | 81.51
2018-11-28 12:00 | 136.77 | 80.18
2018-11-28 12:30 | 139.54 | 84.03
2018-11-28 13:00 | 138.55 | 86.55
2018-11-28 13:30 | 139.54 | 86.22
2018-11-28 14:00 | 135.09 | 81.97
2018-11-28 14:30 | 135.55 | 84.25
2018-11-28 15:00 | 126.51 | 74.64
2018-11-28 15:30 | 117.95 | 67.63
2018-11-28 16:00 | 122.08 | 73.67
2018-11-28 16:30 | 121.3 | 78.03
2018-11-28 17:00 | 117.58 | 79.68
2018-11-28 17:30 | 124.19 | 91.54
2018-11-28 18:00 | 120.71 | 93.18
2018-11-28 18:30 | 126.16 | 99.46
2018-11-28 19:00 | 128.75 | 103.22
2018-11-28 19:30 | 129.09 | 103.92
2018-11-28 20:00 | 125.03 | 97.56
2018-11-28 20:30 | 130.75 | 104.11
2018-11-28 21:00 | 128.9 | 103.08
2018-11-28 21:30 | 131.16 | 104.99
2018-11-28 22:00 | 127.64 | 100.14
2018-11-28 22:30 | 124.62 | 96.38
2018-11-28 23:00 | 120.57 | 93.42
2018-11-28 23:30 | 121.08 | 94.41
2018-11-29 | 120.92 | 93.76
2018-11-29 00:30 | 119.62 | 91.41
2018-11-29 01:00 | 121.6 | 93.62
2018-11-29 01:30 | 121.44 | 95.27
2018-11-29 02:00 | 121.84 | 96.34
2018-11-29 02:30 | 120.37 | 92.83
2018-11-29 03:00 | 114.1 | 88.38
2018-11-29 03:30 | 113.2 | 86.75
2018-11-29 04:00 | 118.17 | 92.44
2018-11-29 04:30 | 116.37 | 91.1
2018-11-29 05:00 | 116.16 | 91.25
2018-11-29 05:30 | 114.32 | 91.09
2018-11-29 06:00 | 111.01 | 84.81
2018-11-29 06:30 | 103.15 | 71.13
2018-11-29 07:00 | 104.53 | 66.44
2018-11-29 07:30 | 109.69 | 66.25
2018-11-29 08:00 | 110.64 | 65.02
2018-11-29 08:30 | 110.68 | 63.44
2018-11-29 09:00 | 107.53 | 60.25
2018-11-29 09:30 | 108.33 | 60.91
2018-11-29 10:00 | 112.78 | 66.36
2018-11-29 10:30 | 114.23 | 66.73
2018-11-29 11:00 | 112.48 | 64.61
2018-11-29 11:30 | 109.84 | 61.28
2018-11-29 12:00 | 107.86 | 59.4
2018-11-29 12:30 | 108.92 | 61.89
2018-11-29 13:00 | 112.04 | 65.84
2018-11-29 13:30 | 111.06 | 65.75
2018-11-29 14:00 | 112.54 | 67.4
2018-11-29 14:30 | 112.43 | 68.7
2018-11-29 15:00 | 113.47 | 70.27
2018-11-29 15:30 | 109.97 | 65.03
2018-11-29 16:00 | 113 | 70.23
2018-11-29 16:30 | 114.45 | 74.11
2018-11-29 17:00 | 116.01 | 78.15
2018-11-29 17:30 | 119.59 | 85.51
2018-11-29 18:00 | 117.4 | 87.91
2018-11-29 18:30 | 112.94 | 86.63
2018-11-29 19:00 | 120.98 | 94.76
2018-11-29 19:30 | 128.78 | 102.4
2018-11-29 20:00 | 115.67 | 90.9
2018-11-29 20:30 | 114.69 | 88.98
2018-11-29 21:00 | 118.46 | 91.9
2018-11-29 21:30 | 118.19 | 90.17
2018-11-29 22:00 | 121.47 | 92.97
2018-11-29 22:30 | 119.64 | 91.78
2018-11-29 23:00 | 115.8 | 86.39
2018-11-29 23:30 | 119.22 | 90.71
2018-11-30 | 116.44 | 88.32
2018-11-30 00:30 | 120.1 | 92.43
2018-11-30 01:00 | 118.64 | 90.82
2018-11-30 01:30 | 120.27 | 92.93
2018-11-30 02:00 | 122.28 | 94.64
2018-11-30 02:30 | 119.23 | 90.55
2018-11-30 03:00 | 120.84 | 92.01
2018-11-30 03:30 | 116.83 | 88.36
2018-11-30 04:00 | 122.57 | 94.25
2018-11-30 04:30 | 117.08 | 89.48
2018-11-30 05:00 | 118.58 | 90.49
2018-11-30 05:30 | 110.61 | 82.08
2018-11-30 06:00 | 114.05 | 85.94
2018-11-30 06:30 | 104.65 | 71.62
2018-11-30 07:00 | 108.21 | 71.17
2018-11-30 07:30 | 109.49 | 68.73
2018-11-30 08:00 | 116.02 | 72.78
2018-11-30 08:30 | 117.54 | 72.06
2018-11-30 09:00 | 121.19 | 74.32
2018-11-30 09:30 | 118.07 | 68.59
2018-11-30 10:00 | 116.91 | 66.02
2018-11-30 10:30 | 122.39 | 73.14
2018-11-30 11:00 | 119.21 | 70.93
2018-11-30 11:30 | 117.99 | 70.71
2018-11-30 12:00 | 116.8 | 66.49
2018-11-30 12:30 | 116.9 | 70.35
2018-11-30 13:00 | 117.82 | 70.81
2018-11-30 13:30 | 118.44 | 73.51
2018-11-30 14:00 | 110.41 | 67.55
2018-11-30 14:30 | 112.86 | 69.14
2018-11-30 15:00 | 119.37 | 73.17
2018-11-30 15:30 | 119.25 | 69.3
2018-11-30 16:00 | 123.17 | 74.79
2018-11-30 16:30 | 123.63 | 75.33
2018-11-30 17:00 | 122.74 | 76.95
2018-11-30 17:30 | 125.69 | 87.44
2018-11-30 18:00 | 129.16 | 98.05
2018-11-30 18:30 | 126.85 | 96.5
2018-11-30 19:00 | 138.44 | 110.36
2018-11-30 19:30 | 135.55 | 106.16
2018-11-30 20:00 | 138.1 | 108.32
2018-11-30 20:30 | 131.29 | 101.48
2018-11-30 21:00 | 127.81 | 96.74
2018-11-30 21:30 | 129.29 | 98.51
2018-11-30 22:00 | 130.63 | 100.26
2018-11-30 22:30 | 136.83 | 107.01
2018-11-30 23:00 | 132.24 | 103.13
2018-11-30 23:30 | 122.36 | 92.24
2018-12-01 | 117.64 | 86.64
2018-12-01 00:30 | 125.03 | 93.31
2018-12-01 01:00 | 128.11 | 97.83
2018-12-01 01:30 | 126.57 | 97.3
2018-12-01 02:00 | 129.54 | 99.21
2018-12-01 02:30 | 123.86 | 94.72
2018-12-01 03:00 | 124.43 | 94.8
2018-12-01 03:30 | 123.67 | 95.42
2018-12-01 04:00 | 119.7 | 91.11
2018-12-01 04:30 | 120.66 | 92.43
2018-12-01 05:00 | 120.85 | 93.33
2018-12-01 05:30 | 122.76 | 94.15
2018-12-01 06:00 | 127.16 | 97.6
2018-12-01 06:30 | 120.09 | 85.59
2018-12-01 07:00 | 120.61 | 83.72
2018-12-01 07:30 | 126.14 | 87.32
2018-12-01 08:00 | 129.32 | 85.66
2018-12-01 08:30 | 125.27 | 80.56
2018-12-01 09:00 | 128.19 | 83.38
2018-12-01 09:30 | 127.09 | 82.33
2018-12-01 10:00 | 134.72 | 91.72
2018-12-01 10:30 | 133.63 | 86.58
2018-12-01 11:00 | 128.82 | 78.16
2018-12-01 11:30 | 133.29 | 83.8
2018-12-01 12:00 | 133.78 | 88.08
2018-12-01 12:30 | 136.09 | 91.62
2018-12-01 13:00 | 136.72 | 90.36
2018-12-01 13:30 | 129.31 | 83.6
2018-12-01 14:00 | 128.99 | 84.49
2018-12-01 14:30 | 133.58 | 88.62
2018-12-01 15:00 | 126.14 | 79.17
2018-12-01 15:30 | 129.19 | 84.52
2018-12-01 16:00 | 131.79 | 87.88
2018-12-01 16:30 | 126.65 | 82.5
2018-12-01 17:00 | 127.95 | 87.75
2018-12-01 17:30 | 132.1 | 98.16
2018-12-01 18:00 | 131.77 | 100.77
2018-12-01 18:30 | 126.09 | 96.23
2018-12-01 19:00 | 133.49 | 103.03
2018-12-01 19:30 | 136.53 | 104.67
2018-12-01 20:00 | 136.38 | 105.13
2018-12-01 20:30 | 137.04 | 106.23
2018-12-01 21:00 | 123.92 | 93.47
2018-12-01 21:30 | 131.97 | 99.64
2018-12-01 22:00 | 131.88 | 99.58
2018-12-01 22:30 | 134.24 | 101.67
2018-12-01 23:00 | 133.23 | 99.96
2018-12-01 23:30 | 135.51 | 102.11
2018-12-02 | 131.44 | 99.16
2018-12-02 00:30 | 139.46 | 106.78
2018-12-02 01:00 | 134.8 | 102.43
2018-12-02 01:30 | 136.29 | 106.41
2018-12-02 02:00 | 126.83 | 96.64
2018-12-02 02:30 | 131.25 | 100.16
2018-12-02 03:00 | 131.58 | 100.9
2018-12-02 03:30 | 124.94 | 94.78
2018-12-02 04:00 | 123.14 | 92.73
2018-12-02 04:30 | 121.39 | 89.91
2018-12-02 05:00 | 119.94 | 90.83
2018-12-02 05:30 | 115.51 | 89.15
2018-12-02 06:00 | 115 | 88.37
2018-12-02 06:30 | 109.3 | 79.85
2018-12-02 07:00 | 112.85 | 79.73
2018-12-02 07:30 | 105.09 | 65.71
2018-12-02 08:00 | 110.1 | 69.52
2018-12-02 08:30 | 112.74 | 71.55
2018-12-02 09:00 | 109.83 | 61.99
2018-12-02 09:30 | 110.93 | 65.72
2018-12-02 10:00 | 119.22 | 74.66
2018-12-02 10:30 | 121.58 | 74.77
2018-12-02 11:00 | 119.91 | 72.86
2018-12-02 11:30 | 125.31 | 75.25
2018-12-02 12:00 | 129.31 | 79.71
2018-12-02 12:30 | 131.39 | 83.98
2018-12-02 13:00 | 127.47 | 80.1
2018-12-02 13:30 | 133.01 | 84.91
2018-12-02 14:00 | 131.02 | 87.31
2018-12-02 14:30 | 131.84 | 85.92
2018-12-02 15:00 | 136.33 | 92.29
2018-12-02 15:30 | 132.24 | 92.51
2018-12-02 16:00 | 132.27 | 95.69
2018-12-02 16:30 | 134.64 | 96.83
2018-12-02 17:00 | 130.99 | 99.06
2018-12-02 17:30 | 126.63 | 91.04
2018-12-02 18:00 | 130.55 | 99.41
2018-12-02 18:30 | 135.17 | 106.18
2018-12-02 19:00 | 127.49 | 99.42
2018-12-02 19:30 | 137.4 | 110.27
2018-12-02 20:00 | 141.24 | 113.45
2018-12-02 20:30 | 135.3 | 107.71
2018-12-02 21:00 | 133.23 | 105.25
2018-12-02 21:30 | 138.83 | 110.42
2018-12-02 22:00 | 140.56 | 110.62
2018-12-02 22:30 | 136.28 | 105.42
2018-12-02 23:00 | 129.89 | 99.78
2018-12-02 23:30 | 125.21 | 93.67
2018-12-03 | 117.29 | 85.5
2018-12-03 00:30 | 116.13 | 85.7
2018-12-03 01:00 | 121.42 | 90.63
2018-12-03 01:30 | 117.11 | 87.1
2018-12-03 02:00 | 114.95 | 86.89
2018-12-03 02:30 | 130.51 | 101.54
2018-12-03 03:00 | 131.66 | 100.94
2018-12-03 03:30 | 130.25 | 99.74
2018-12-03 04:00 | 132.69 | 103.48
2018-12-03 04:30 | 138.47 | 107.96
2018-12-03 05:00 | 128.71 | 97.46
2018-12-03 05:30 | 135.3 | 106.41
2018-12-03 06:00 | 135.26 | 104.18
2018-12-03 06:30 | 117.74 | 78.43
2018-12-03 07:00 | 122.96 | 83.04
2018-12-03 07:30 | 124.9 | 80.34
2018-12-03 08:00 | 123.12 | 76.91
2018-12-03 08:30 | 121.51 | 72.48
2018-12-03 09:00 | 122.58 | 76.98
2018-12-03 09:30 | 116.75 | 69.47
2018-12-03 10:00 | 124.7 | 76.11
2018-12-03 10:30 | 136.4 | 89.92
2018-12-03 11:00 | 130.11 | 83.15
2018-12-03 11:30 | 134.09 | 86.36
2018-12-03 12:00 | 136.41 | 90.01
2018-12-03 12:30 | 143.51 | 97.02
2018-12-03 13:00 | 141.77 | 95.47
2018-12-03 13:30 | 140.33 | 95.08
2018-12-03 14:00 | 137.19 | 91.91
2018-12-03 14:30 | 129.99 | 83.37
2018-12-03 15:00 | 136.51 | 102.74
2018-12-03 15:30 | 136.4 | 103.77
2018-12-03 16:00 | 138.32 | 105.32
2018-12-03 16:30 | 133.69 | 95.26
2018-12-03 17:00 | 135.6 | 98.83
2018-12-03 17:30 | 139.44 | 107.16
2018-12-03 18:00 | 139.69 | 109.96
2018-12-03 18:30 | 135.95 | 108.15
2018-12-03 19:00 | 148.18 | 120.09
2018-12-03 19:30 | 156.06 | 126.74
2018-12-03 20:00 | 150.67 | 121.11
2018-12-03 20:30 | 141.68 | 113.07
2018-12-03 21:00 | 147.5 | 118.66
2018-12-03 21:30 | 140.63 | 111.25
2018-12-03 22:00 | 143.35 | 115.2
2018-12-03 22:30 | 139.65 | 111.25
2018-12-03 23:00 | 132.26 | 107.48
2018-12-03 23:30 | 131.8 | 104.25
2018-12-04 | 133.2 | 104.97
2018-12-04 00:30 | 130.57 | 102.35
2018-12-04 01:00 | 127.87 | 97.27
2018-12-04 01:30 | 135.01 | 103.96
2018-12-04 02:00 | 132.3 | 101.4
2018-12-04 02:30 | 139.99 | 108.48
2018-12-04 03:00 | 130.09 | 97.8
2018-12-04 03:30 | 134.24 | 101.86
2018-12-04 04:00 | 126.14 | 94.99
2018-12-04 04:30 | 137.24 | 104.62
2018-12-04 05:00 | 134.42 | 101.22
2018-12-04 05:30 | 132.51 | 99.43
2018-12-04 06:00 | 132.53 | 98.38
2018-12-04 06:30 | 120.38 | 82.34
2018-12-04 07:00 | 120.69 | 76.31
2018-12-04 07:30 | 125.95 | 79.05
2018-12-04 08:00 | 127.78 | 81.29
2018-12-04 08:30 | 129.03 | 82.53
2018-12-04 09:00 | 133.28 | 86.57
2018-12-04 09:30 | 133.24 | 86.66
2018-12-04 10:00 | 132.58 | 86.41
2018-12-04 10:30 | 137.02 | 87.62
2018-12-04 11:00 | 130.47 | 81.66
2018-12-04 11:30 | 136.02 | 89.9
2018-12-04 12:00 | 137.82 | 95.41
2018-12-04 12:30 | 137.24 | 93
2018-12-04 13:00 | 133.42 | 90.57
2018-12-04 13:30 | 136.35 | 95.78
2018-12-04 14:00 | 136.34 | 90.54
2018-12-04 14:30 | 125.85 | 87.53
2018-12-04 15:00 | 126.02 | 80.43
2018-12-04 15:30 | 121.44 | 77.65
2018-12-04 16:00 | 124.67 | 80.8
2018-12-04 16:30 | 125.84 | 82.5
2018-12-04 17:00 | 127.76 | 89.76
2018-12-04 17:30 | 131.19 | 96.66
2018-12-04 18:00 | 129.1 | 100.89
2018-12-04 18:30 | 126.75 | 99.11
2018-12-04 19:00 | 131.21 | 103.54
2018-12-04 19:30 | 127.54 | 99.65
2018-12-04 20:00 | 129.44 | 100.82
2018-12-04 20:30 | 134.74 | 107.2
2018-12-04 21:00 | 138.31 | 112.13
2018-12-04 21:30 | 140.44 | 114.76
2018-12-04 22:00 | 142.94 | 117.04
2018-12-04 22:30 | 141.82 | 116.47
2018-12-04 23:00 | 132.8 | 106.6
2018-12-04 23:30 | 128.03 | 100.33
2018-12-05 | 125.99 | 98.92
2018-12-05 00:30 | 129.26 | 101.58
2018-12-05 01:00 | 133.69 | 106.45
2018-12-05 01:30 | 119.71 | 93.56
2018-12-05 02:00 | 116.27 | 91.86
2018-12-05 02:30 | 117.81 | 91.63
2018-12-05 03:00 | 114.67 | 86.97
2018-12-05 03:30 | 117.24 | 89.16
2018-12-05 04:00 | 118.34 | 90.84
2018-12-05 04:30 | 117.59 | 91.01
2018-12-05 05:00 | 115.62 | 87.97
2018-12-05 05:30 | 116.69 | 89.71
2018-12-05 06:00 | 116.19 | 89.41
2018-12-05 06:30 | 110.52 | 83.12
2018-12-05 07:00 | 113.37 | 87.33
2018-12-05 07:30 | 117.49 | 91.68
2018-12-05 08:00 | 111.87 | 85.56
2018-12-05 08:30 | 106.36 | 78.84
2018-12-05 09:00 | 110.15 | 77.21
2018-12-05 09:30 | 107.98 | 67.69
2018-12-05 10:00 | 112.35 | 80.94
2018-12-05 10:30 | 112.2 | 81.85
2018-12-05 11:00 | 114.48 | 77.06
2018-12-05 11:30 | 116.43 | 75.31
2018-12-05 12:00 | 118.75 | 85.01
2018-12-05 12:30 | 118.73 | 81.05
2018-12-05 13:00 | 123.76 | 84.14
2018-12-05 13:30 | 128.17 | 88.03
2018-12-05 14:00 | 126.02 | 83.95
2018-12-05 14:30 | 130.8 | 89.35
2018-12-05 15:00 | 115.3 | 88.01
2018-12-05 15:30 | 109.63 | 82.35
2018-12-05 16:00 | 116.24 | 83.97
2018-12-05 16:30 | 115.42 | 84.51
2018-12-05 17:00 | 112.61 | 80.45
2018-12-05 17:30 | 117.04 | 87.48
2018-12-05 18:00 | 119.5 | 94.14
2018-12-05 18:30 | 115.31 | 93.3
2018-12-05 19:00 | 118.46 | 96.69
2018-12-05 19:30 | 127.45 | 104.85
2018-12-05 20:00 | 120.35 | 97.92
2018-12-05 20:30 | 119.55 | 98.35
2018-12-05 21:00 | 118.42 | 98.14
2018-12-05 21:30 | 129.31 | 109.54
2018-12-05 22:00 | 127.65 | 107.01
2018-12-05 22:30 | 127 | 106.5
2018-12-05 23:00 | 126.67 | 105.59
2018-12-05 23:30 | 124.69 | 103.27
2018-12-06 | 128.07 | 105.65
2018-12-06 00:30 | 127.14 | 103.29
2018-12-06 01:00 | 119.49 | 96.24
2018-12-06 01:30 | 122.4 | 99.69
2018-12-06 02:00 | 124.17 | 103.21
2018-12-06 02:30 | 119.89 | 99.55
2018-12-06 03:00 | 121.86 | 100.69
2018-12-06 03:30 | 119.96 | 98.54
2018-12-06 04:00 | 118.09 | 96.25
2018-12-06 04:30 | 112.54 | 92.45
2018-12-06 05:00 | 126.67 | 107.84
2018-12-06 05:30 | 122.81 | 104.31
2018-12-06 06:00 | 113.69 | 93.74
2018-12-06 06:30 | 104.29 | 81.3
2018-12-06 07:00 | 113.08 | 86.77
2018-12-06 07:30 | 109.33 | 75.83
2018-12-06 08:00 | 116.02 | 81.27
2018-12-06 08:30 | 106.4 | 73.8
2018-12-06 09:00 | 103.33 | 75.21
2018-12-06 09:30 | 107.88 | 76.11
2018-12-06 10:00 | 113.95 | 83.34
2018-12-06 10:30 | 114.85 | 88.52
2018-12-06 11:00 | 108.54 | 80.71
2018-12-06 11:30 | 106.57 | 77.86
2018-12-06 12:00 | 99.57 | 73.31
2018-12-06 12:30 | 104.41 | 78.94
2018-12-06 13:00 | 101.92 | 73.56
2018-12-06 13:30 | 103.6 | 80.47
2018-12-06 14:00 | 104.18 | 77.07
2018-12-06 14:30 | 102.58 | 73.78
2018-12-06 15:00 | 101.97 | 76.68
2018-12-06 15:30 | 107.01 | 83.83
2018-12-06 16:00 | 108.17 | 72.3
2018-12-06 16:30 | 114.18 | 84.32
2018-12-06 17:00 | 117.59 | 86.89
2018-12-06 17:30 | 116.94 | 90.71
2018-12-06 18:00 | 116.91 | 95.42
2018-12-06 18:30 | 123.39 | 100.47
2018-12-06 19:00 | 134.52 | 112.39
2018-12-06 19:30 | 137.55 | 114.62
2018-12-06 20:00 | 136.7 | 113.12
2018-12-06 20:30 | 141.62 | 118.23
2018-12-06 21:00 | 140.2 | 116.61
2018-12-06 21:30 | 130.74 | 107.08
2018-12-06 22:00 | 132.22 | 107.5
2018-12-06 22:30 | 124.45 | 100.03
2018-12-06 23:00 | 131.93 | 109.21
2018-12-06 23:30 | 126.85 | 102.63
2018-12-07 | 137.02 | 114
2018-12-07 00:30 | 124.9 | 101.9
2018-12-07 01:00 | 125.29 | 103.65
2018-12-07 01:30 | 127.91 | 105.46
2018-12-07 02:00 | 133.95 | 112.3
2018-12-07 02:30 | 121.47 | 99.38
2018-12-07 03:00 | 123.73 | 101.63
2018-12-07 03:30 | 135.5 | 113.54
2018-12-07 04:00 | 126.6 | 104.13
2018-12-07 04:30 | 129.57 | 106.75
2018-12-07 05:00 | 125.3 | 102.15
2018-12-07 05:30 | 131.46 | 108.15
2018-12-07 06:00 | 127.55 | 105.19
2018-12-07 06:30 | 111.81 | 85.44
2018-12-07 07:00 | 124.83 | 101.81
2018-12-07 07:30 | 120.78 | 91.36
2018-12-07 08:00 | 116.97 | 77.05
2018-12-07 08:30 | 115.16 | 82.45
2018-12-07 09:00 | 112.26 | 81.69
2018-12-07 09:30 | 119.09 | 83.36
2018-12-07 10:00 | 121.1 | 83.2
2018-12-07 10:30 | 127.3 | 89.51
2018-12-07 11:00 | 118.88 | 86.59
2018-12-07 11:30 | 117.95 | 75.69
2018-12-07 12:00 | 125.3 | 81.65
2018-12-07 12:30 | 125.25 | 83.98
2018-12-07 13:00 | 118.84 | 78.49
2018-12-07 13:30 | 120.05 | 88.23
2018-12-07 14:00 | 122.3 | 94.13
2018-12-07 14:30 | 121.54 | 88.49
2018-12-07 15:00 | 112.83 | 77.45
2018-12-07 15:30 | 116.15 | 82.25
2018-12-07 16:00 | 112.7 | 79.58
2018-12-07 16:30 | 116.09 | 85.46
2018-12-07 17:00 | 118.72 | 86.05
2018-12-07 17:30 | 116.97 | 88.07
2018-12-07 18:00 | 123.05 | 97.85
2018-12-07 18:30 | 120.84 | 94.88
2018-12-07 19:00 | 127.93 | 103.18
2018-12-07 19:30 | 142.3 | 118.33
2018-12-07 20:00 | 141.1 | 115.29
2018-12-07 20:30 | 141.24 | 115.58
2018-12-07 21:00 | 139.5 | 114.74
2018-12-07 21:30 | 135.39 | 110.15
2018-12-07 22:00 | 125.3 | 98.24
2018-12-07 22:30 | 129.79 | 102.76
2018-12-07 23:00 | 123.32 | 96.84
2018-12-07 23:30 | 124.6 | 96.72
2018-12-08 | 123.7 | 95.05
2018-12-08 00:30 | 119.65 | 91.95
2018-12-08 01:00 | 123.62 | 96.79
2018-12-08 01:30 | 130.33 | 102.52
2018-12-08 02:00 | 126.63 | 97.41
2018-12-08 02:30 | 125.45 | 99.74
2018-12-08 03:00 | 121.76 | 95.81
2018-12-08 03:30 | 119.37 | 94.08
2018-12-08 04:00 | 124.92 | 99.8
2018-12-08 04:30 | 119.64 | 93.13
2018-12-08 05:00 | 129.63 | 105.01
2018-12-08 05:30 | 124.2 | 100.23
2018-12-08 06:00 | 127.37 | 103.33
2018-12-08 06:30 | 113.31 | 87.25
2018-12-08 07:00 | 118.77 | 91.21
2018-12-08 07:30 | 125.16 | 96.62
2018-12-08 08:00 | 114.34 | 72.41
2018-12-08 08:30 | 126.16 | 78.58
2018-12-08 09:00 | 120.82 | 75.63
2018-12-08 09:30 | 119.52 | 80.68
2018-12-08 10:00 | 127.65 | 88.33
2018-12-08 10:30 | 120.09 | 77.32
2018-12-08 11:00 | 120.93 | 77.41
2018-12-08 11:30 | 119.66 | 82.82
2018-12-08 12:00 | 122.5 | 85.69
2018-12-08 12:30 | 125.63 | 86.07
2018-12-08 13:00 | 121.82 | 88.13
2018-12-08 13:30 | 122.37 | 89.71
2018-12-08 14:00 | 123.46 | 90.45
2018-12-08 14:30 | 128.93 | 97.22
2018-12-08 15:00 | 120.61 | 92.05
2018-12-08 15:30 | 122.09 | 90.37
2018-12-08 16:00 | 123.93 | 92.43
2018-12-08 16:30 | 125.02 | 96.4
2018-12-08 17:00 | 122.02 | 90.94
2018-12-08 17:30 | 127.77 | 98.24
2018-12-08 18:00 | 125.94 | 98.33
2018-12-08 18:30 | 120.3 | 94.05
2018-12-08 19:00 | 123.84 | 99.62
2018-12-08 19:30 | 134.85 | 111
2018-12-08 20:00 | 141.34 | 117.92
2018-12-08 20:30 | 140.76 | 117.14
2018-12-08 21:00 | 142.08 | 117.9
2018-12-08 21:30 | 132.47 | 108.52
2018-12-08 22:00 | 133.11 | 108.79
2018-12-08 22:30 | 136.92 | 113.79
2018-12-08 23:00 | 140.84 | 117.07
2018-12-08 23:30 | 141.56 | 117.53
2018-12-09 | 137.11 | 112.1
2018-12-09 00:30 | 137.1 | 112.59
2018-12-09 01:00 | 139.2 | 113.99
2018-12-09 01:30 | 130.43 | 104.41
2018-12-09 02:00 | 132.49 | 106.17
2018-12-09 02:30 | 132.36 | 105.73
2018-12-09 03:00 | 132.14 | 105.25
2018-12-09 03:30 | 130.45 | 103.85
2018-12-09 04:00 | 123.29 | 95.71
2018-12-09 04:30 | 130.05 | 102.21
2018-12-09 05:00 | 138.16 | 111.8
2018-12-09 05:30 | 126.98 | 102.03
2018-12-09 06:00 | 129.61 | 103.61
2018-12-09 06:30 | 129.52 | 101.05
2018-12-09 07:00 | 132.11 | 97.43
2018-12-09 07:30 | 132.67 | 90.82
2018-12-09 08:00 | 129.98 | 85.28
2018-12-09 08:30 | 128.15 | 86.17
2018-12-09 09:00 | 126.68 | 83.66
2018-12-09 09:30 | 125.03 | 87.27
2018-12-09 10:00 | 124.73 | 81.55
2018-12-09 10:30 | 124.52 | 84.45
2018-12-09 11:00 | 133.25 | 94.43
2018-12-09 11:30 | 127.06 | 89.08
2018-12-09 12:00 | 124.63 | 83.42
2018-12-09 12:30 | 135.58 | 94.9
2018-12-09 13:00 | 129.27 | 86.69
2018-12-09 13:30 | 129.39 | 90.9
2018-12-09 14:00 | 130.72 | 96.39
2018-12-09 14:30 | 129.79 | 95.47
2018-12-09 15:00 | 131.54 | 98.09
2018-12-09 15:30 | 131.97 | 97.36
2018-12-09 16:00 | 127.69 | 95.7
2018-12-09 16:30 | 130.57 | 102.22
2018-12-09 17:00 | 123.92 | 90.15
2018-12-09 17:30 | 130.36 | 96.52
2018-12-09 18:00 | 126.84 | 97.47
2018-12-09 18:30 | 131.92 | 106.04
2018-12-09 19:00 | 136.2 | 111.82
2018-12-09 19:30 | 136.33 | 110.9
2018-12-09 20:00 | 135.57 | 109.86
2018-12-09 20:30 | 139.75 | 114.45
2018-12-09 21:00 | 128.35 | 102.35
2018-12-09 21:30 | 126.8 | 101.95
2018-12-09 22:00 | 122.34 | 97.99
2018-12-09 22:30 | 120.25 | 95.56
2018-12-09 23:00 | 120.77 | 96.3
2018-12-09 23:30 | 124.02 | 99.51
2018-12-10 | 120.55 | 95.97
2018-12-10 00:30 | 116.91 | 92.74
2018-12-10 01:00 | 118.16 | 93.57
2018-12-10 01:30 | 121.25 | 96.89
2018-12-10 02:00 | 124.46 | 101.22
2018-12-10 02:30 | 122.98 | 98.56
2018-12-10 03:00 | 125.2 | 100.09
2018-12-10 03:30 | 125.16 | 99.99
2018-12-10 04:00 | 128.82 | 104.35
2018-12-10 04:30 | 133.13 | 108.6
2018-12-10 05:00 | 127.29 | 101.51
2018-12-10 05:30 | 130.05 | 104.18
2018-12-10 06:00 | 123.18 | 95.12
2018-12-10 06:30 | 112.23 | 78.72
2018-12-10 07:00 | 116.35 | 74.61
2018-12-10 07:30 | 116.09 | 68.11
2018-12-10 08:00 | 112.96 | 60.76
2018-12-10 08:30 | 118.15 | 67.97
2018-12-10 09:00 | 124.12 | 75.84
2018-12-10 09:30 | 122.16 | 72.73
2018-12-10 10:00 | 119.51 | 68.08
2018-12-10 10:30 | 119.88 | 69.92
2018-12-10 11:00 | 113.78 | 65.14
2018-12-10 11:30 | 114.91 | 68.06
2018-12-10 12:00 | 108.63 | 59.97
2018-12-10 12:30 | 119.75 | 71.51
2018-12-10 13:00 | 119.84 | 71.85
2018-12-10 13:30 | 116.58 | 70.7
2018-12-10 14:00 | 117.41 | 71.66
2018-12-10 14:30 | 114.88 | 75.5
2018-12-10 15:00 | 118.7 | 80.06
2018-12-10 15:30 | 114.15 | 74.33
2018-12-10 16:00 | 116.76 | 78.05
2018-12-10 16:30 | 116.74 | 85.7
2018-12-10 17:00 | 118.35 | 82.18
2018-12-10 17:30 | 120.07 | 87.2
2018-12-10 18:00 | 118.45 | 89.1
2018-12-10 18:30 | 119.14 | 93.99
2018-12-10 19:00 | 123.4 | 100.13
2018-12-10 19:30 | 127.02 | 103.5
2018-12-10 20:00 | 133.85 | 111.28
2018-12-10 20:30 | 135.36 | 112.44
2018-12-10 21:00 | 128.1 | 104.87
2018-12-10 21:30 | 128.4 | 105.81
2018-12-10 22:00 | 139.6 | 116.13
2018-12-10 22:30 | 138.55 | 114.45
2018-12-10 23:00 | 136.3 | 111.15
2018-12-10 23:30 | 125.38 | 101.19
2018-12-11 | 134.89 | 110.45
2018-12-11 00:30 | 133.5 | 107.13
2018-12-11 01:00 | 132.72 | 106.83
2018-12-11 01:30 | 134.17 | 108.49
2018-12-11 02:00 | 139.46 | 114.16
2018-12-11 02:30 | 140.53 | 114.23
2018-12-11 03:00 | 131.75 | 104.19
2018-12-11 03:30 | 128.21 | 100.11
2018-12-11 04:00 | 129.07 | 102.26
2018-12-11 04:30 | 127.41 | 101.95
2018-12-11 05:00 | 129.96 | 104.89
2018-12-11 05:30 | 124.58 | 99.3
2018-12-11 06:00 | 129.03 | 102.69
2018-12-11 06:30 | 126.66 | 95.91
2018-12-11 07:00 | 131.59 | 96.27
2018-12-11 07:30 | 124.46 | 85.13
2018-12-11 08:00 | 121.87 | 77.57
2018-12-11 08:30 | 118.67 | 75.19
2018-12-11 09:00 | 126.43 | 80.08
2018-12-11 09:30 | 124.61 | 81.75
2018-12-11 10:00 | 129.59 | 84.85
2018-12-11 10:30 | 130.94 | 86.05
2018-12-11 11:00 | 125.58 | 80.6
2018-12-11 11:30 | 124.51 | 80.37
2018-12-11 12:00 | 125.98 | 85.15
2018-12-11 12:30 | 132.47 | 95.14
2018-12-11 13:00 | 138.31 | 100.91
2018-12-11 13:30 | 127.93 | 87.22
2018-12-11 14:00 | 125.01 | 82.87
2018-12-11 14:30 | 122.56 | 79.94
2018-12-11 15:00 | 110.77 | 68.58
2018-12-11 15:30 | 112.66 | 70.07
2018-12-11 16:00 | 110.55 | 74.48
2018-12-11 16:30 | 127.73 | 93.55
2018-12-11 17:00 | 126.53 | 91.06
2018-12-11 17:30 | 121.94 | 91.95
2018-12-11 18:00 | 115.68 | 91.65
2018-12-11 18:30 | 121.84 | 103.84
2018-12-11 19:00 | 132.56 | 113.99
2018-12-11 19:30 | 128.88 | 110.44
2018-12-11 20:00 | 129.68 | 110.35
2018-12-11 20:30 | 130.02 | 109.54
2018-12-11 21:00 | 127.44 | 108.04
2018-12-11 21:30 | 117.34 | 97.5
2018-12-11 22:00 | 126.58 | 103.55
2018-12-11 22:30 | 127.32 | 103.17
2018-12-11 23:00 | 121.6 | 97.34
2018-12-11 23:30 | 126.74 | 103.25
2018-12-12 | 133.54 | 110.87
2018-12-12 00:30 | 121.39 | 99.62
2018-12-12 01:00 | 117.44 | 95.86
2018-12-12 01:30 | 128.43 | 108.69
2018-12-12 02:00 | 124.43 | 103.16
2018-12-12 02:30 | 117.3 | 97.53
2018-12-12 03:00 | 118.73 | 99.31
2018-12-12 03:30 | 115.25 | 99.27
2018-12-12 04:00 | 108.99 | 92.06
2018-12-12 04:30 | 104.66 | 87.45
2018-12-12 05:00 | 105.62 | 88.44
2018-12-12 05:30 | 107.26 | 90.89
2018-12-12 06:00 | 108.04 | 92.35
2018-12-12 06:30 | 90.63 | 72.79
2018-12-12 07:00 | 94.36 | 75.72
2018-12-12 07:30 | 95.92 | 76.8
2018-12-12 08:00 | 96.57 | 77.44
2018-12-12 08:30 | 96.23 | 76.86
2018-12-12 09:00 | 91.59 | 71.81
2018-12-12 09:30 | 92.69 | 73.87
2018-12-12 10:00 | 93.6 | 76.22
2018-12-12 10:30 | 91.53 | 73.67
2018-12-12 11:00 | 95.77 | 78.77
2018-12-12 11:30 | 87.87 | 70.21
2018-12-12 12:00 | 91.14 | 73.05
2018-12-12 12:30 | 95.01 | 75.53
2018-12-12 13:00 | 78.9 | 56.28
2018-12-12 13:30 | 82.26 | 58.42
2018-12-12 14:00 | 82.09 | 58.33
2018-12-12 14:30 | 83.7 | 55.2
2018-12-12 15:00 | 82.53 | 55.15
2018-12-12 15:30 | 85.55 | 57.5
2018-12-12 16:00 | 90.66 | 58.81
2018-12-12 16:30 | 94.75 | 68.01
2018-12-12 17:00 | 95.61 | 67.15
2018-12-12 17:30 | 99.32 | 79.52
2018-12-12 18:00 | 103.29 | 84.79
2018-12-12 18:30 | 105.3 | 86.69
2018-12-12 19:00 | 116.49 | 97.12
2018-12-12 19:30 | 113.12 | 93.43
2018-12-12 20:00 | 121.61 | 101.46
2018-12-12 20:30 | 114.91 | 94.92
2018-12-12 21:00 | 111.6 | 91.81
2018-12-12 21:30 | 115.5 | 96.37
2018-12-12 22:00 | 113.4 | 95.57
2018-12-12 22:30 | 122.3 | 105.13
2018-12-12 23:00 | 121.16 | 103.64
2018-12-12 23:30 | 114.88 | 97.1
2018-12-13 | 113.38 | 96.01
2018-12-13 00:30 | 117.66 | 100.86
2018-12-13 01:00 | 106.58 | 88.67
2018-12-13 01:30 | 105.94 | 88.83
2018-12-13 02:00 | 108.63 | 91.65
2018-12-13 02:30 | 113.22 | 96.39
2018-12-13 03:00 | 102.59 | 84.8
2018-12-13 03:30 | 106.45 | 88.76
2018-12-13 04:00 | 103.4 | 85.62
2018-12-13 04:30 | 106.7 | 88.88
2018-12-13 05:00 | 107.54 | 90.11
2018-12-13 05:30 | 98.97 | 80.77
2018-12-13 06:00 | 102.27 | 84.32
2018-12-13 06:30 | 93.62 | 75.65
2018-12-13 07:00 | 99.8 | 82.77
2018-12-13 07:30 | 97.21 | 79.98
2018-12-13 08:00 | 95.43 | 77.84
2018-12-13 08:30 | 94.93 | 76.01
2018-12-13 09:00 | 97.11 | 79.18
2018-12-13 09:30 | 92.63 | 74.29
2018-12-13 10:00 | 93.52 | 75.59
2018-12-13 10:30 | 94.22 | 76.14
2018-12-13 11:00 | 93.67 | 76.06
2018-12-13 11:30 | 96.48 | 78.51
2018-12-13 12:00 | 97.43 | 80.47
2018-12-13 12:30 | 101.18 | 82.94
2018-12-13 13:00 | 95 | 71.48
2018-12-13 13:30 | 96.07 | 71.21
2018-12-13 14:00 | 94.4 | 64.17
2018-12-13 14:30 | 97.18 | 65.1
2018-12-13 15:00 | 93.79 | 66.08
2018-12-13 15:30 | 92.57 | 66.52
2018-12-13 16:00 | 97.23 | 73.79
2018-12-13 16:30 | 104.51 | 84
2018-12-13 17:00 | 105.75 | 88.64
2018-12-13 17:30 | 100.24 | 83.52
2018-12-13 18:00 | 113.37 | 97.84
2018-12-13 18:30 | 105.7 | 89.06
2018-12-13 19:00 | 117.69 | 102.26
2018-12-13 19:30 | 115.31 | 99.27
2018-12-13 20:00 | 117.66 | 101.38
2018-12-13 20:30 | 111.66 | 94.5
2018-12-13 21:00 | 109.42 | 91.52
2018-12-13 21:30 | 111.02 | 94.14
2018-12-13 22:00 | 109.85 | 92.65
2018-12-13 22:30 | 109.13 | 92.24
2018-12-13 23:00 | 107.65 | 90.35
2018-12-13 23:30 | 110.46 | 93.73
2018-12-14 | 108.76 | 90.51
2018-12-14 00:30 | 114.86 | 95.42
2018-12-14 01:00 | 118.45 | 97.81
2018-12-14 01:30 | 117.89 | 98.04
2018-12-14 02:00 | 117.18 | 97.49
2018-12-14 02:30 | 115.9 | 96.08
2018-12-14 03:00 | 113.18 | 93.33
2018-12-14 03:30 | 120.05 | 101.13
2018-12-14 04:00 | 127.67 | 106.66
2018-12-14 04:30 | 124.08 | 103.24
2018-12-14 05:00 | 128.62 | 104.97
2018-12-14 05:30 | 115.67 | 92.12
2018-12-14 06:00 | 105.84 | 83.29
2018-12-14 06:30 | 104.21 | 80.38
2018-12-14 07:00 | 112.57 | 88.6
2018-12-14 07:30 | 109.96 | 82.7
2018-12-14 08:00 | 112.27 | 87.07
2018-12-14 08:30 | 112.89 | 88.62
2018-12-14 09:00 | 117.04 | 93.96
2018-12-14 09:30 | 116.83 | 91.92
2018-12-14 10:00 | 120.74 | 93.13
2018-12-14 10:30 | 120.94 | 79.63
2018-12-14 11:00 | 115.68 | 79.34
2018-12-14 11:30 | 116.01 | 74.97
2018-12-14 12:00 | 120.74 | 80.01
2018-12-14 12:30 | 117.35 | 80.02
2018-12-14 13:00 | 113.4 | 73.75
2018-12-14 13:30 | 113.42 | 73.26
2018-12-14 14:00 | 122.1 | 83.93
2018-12-14 14:30 | 125.73 | 82.8
2018-12-14 15:00 | 120.23 | 77.6
2018-12-14 15:30 | 116.16 | 77.57
2018-12-14 16:00 | 119.52 | 82.4
2018-12-14 16:30 | 111.7 | 76.42
2018-12-14 17:00 | 111.5 | 80.56
2018-12-14 17:30 | 116.1 | 90.28
2018-12-14 18:00 | 111.33 | 86.4
2018-12-14 18:30 | 107.99 | 82.17
2018-12-14 19:00 | 115 | 88.91
2018-12-14 19:30 | 120.73 | 95.47
2018-12-14 20:00 | 121.14 | 95.26
2018-12-14 20:30 | 120.23 | 94.94
2018-12-14 21:00 | 121.62 | 96.49
2018-12-14 21:30 | 117.3 | 92.49
2018-12-14 22:00 | 120.25 | 94.86
2018-12-14 22:30 | 120.4 | 94.24
2018-12-14 23:00 | 118.57 | 91.66
2018-12-14 23:30 | 116.8 | 89.5
2018-12-15 | 115.09 | 88.78
2018-12-15 00:30 | 115.46 | 87.57
2018-12-15 01:00 | 119.12 | 91.35
2018-12-15 01:30 | 124.11 | 96.92
2018-12-15 02:00 | 119.04 | 90.87
2018-12-15 02:30 | 115.87 | 88.79
2018-12-15 03:00 | 117.38 | 89.46
2018-12-15 03:30 | 119.48 | 91.34
2018-12-15 04:00 | 121.97 | 94.66
2018-12-15 04:30 | 118.5 | 91.23
2018-12-15 05:00 | 111.69 | 83.85
2018-12-15 05:30 | 116.52 | 89.04
2018-12-15 06:00 | 115.76 | 87.45
2018-12-15 06:30 | 111.12 | 80.37
2018-12-15 07:00 | 117.09 | 85.81
2018-12-15 07:30 | 117.9 | 86.93
2018-12-15 08:00 | 116.15 | 81.34
2018-12-15 08:30 | 112.78 | 75.13
2018-12-15 09:00 | 106.59 | 67.1
2018-12-15 09:30 | 108.89 | 68.37
2018-12-15 10:00 | 110.95 | 66.84
2018-12-15 10:30 | 112.43 | 69.42
2018-12-15 11:00 | 111 | 68.99
2018-12-15 11:30 | 115.65 | 83.02
2018-12-15 12:00 | 117.8 | 85.29
2018-12-15 12:30 | 115.3 | 83.35
2018-12-15 13:00 | 123.12 | 93.84
2018-12-15 13:30 | 122.9 | 93.51
2018-12-15 14:00 | 131.56 | 103.15
2018-12-15 14:30 | 132.7 | 101.28
2018-12-15 15:00 | 130.07 | 99.08
2018-12-15 15:30 | 125.37 | 93.25
2018-12-15 16:00 | 132.67 | 100.95
2018-12-15 16:30 | 135.93 | 104.23
2018-12-15 17:00 | 132.65 | 100.25
2018-12-15 17:30 | 138.31 | 107.28
2018-12-15 18:00 | 133.6 | 102.85
2018-12-15 18:30 | 128.64 | 97.03
2018-12-15 19:00 | 138.7 | 109.2
2018-12-15 19:30 | 142.61 | 113.5
2018-12-15 20:00 | 135.62 | 105.65
2018-12-15 20:30 | 131.17 | 99.67
2018-12-15 21:00 | 132.41 | 101.85
2018-12-15 21:30 | 145.25 | 117.38
2018-12-15 22:00 | 130.07 | 101.67
2018-12-15 22:30 | 136.1 | 108.61
2018-12-15 23:00 | 131.89 | 105.57
2018-12-15 23:30 | 125.83 | 98.91
2018-12-16 | 131.56 | 105.35
2018-12-16 00:30 | 128.53 | 102.36
2018-12-16 01:00 | 125.76 | 99.59
2018-12-16 01:30 | 127.37 | 102.35
2018-12-16 02:00 | 136.6 | 112.61
2018-12-16 02:30 | 125.1 | 100.01
2018-12-16 03:00 | 129.6 | 105.29
2018-12-16 03:30 | 122.49 | 98.92
2018-12-16 04:00 | 122.98 | 100.33
2018-12-16 04:30 | 121.46 | 96.76
2018-12-16 05:00 | 114.8 | 89.99
2018-12-16 05:30 | 111.79 | 88.76
2018-12-16 06:00 | 113.33 | 89.55
2018-12-16 06:30 | 109.18 | 83.76
2018-12-16 07:00 | 111.8 | 87.08
2018-12-16 07:30 | 115.02 | 91.28
2018-12-16 08:00 | 107.96 | 83.75
2018-12-16 08:30 | 107.85 | 83.48
2018-12-16 09:00 | 107.1 | 81.15
2018-12-16 09:30 | 110.9 | 85.91
2018-12-16 10:00 | 116.75 | 94.35
2018-12-16 10:30 | 113.74 | 95.27
2018-12-16 11:00 | 115.39 | 97.15
2018-12-16 11:30 | 118.77 | 94.8
2018-12-16 12:00 | 125.66 | 103.37
2018-12-16 12:30 | 122.55 | 100.06
2018-12-16 13:00 | 118.01 | 93.94
2018-12-16 13:30 | 120.69 | 96.63
2018-12-16 14:00 | 120.22 | 96.12
2018-12-16 14:30 | 118.28 | 91.49
2018-12-16 15:00 | 119.19 | 91.36
2018-12-16 15:30 | 119.37 | 92.28
2018-12-16 16:00 | 119.86 | 92.6
2018-12-16 16:30 | 126.07 | 99.26
2018-12-16 17:00 | 129.31 | 103.19
2018-12-16 17:30 | 130.26 | 106.2
2018-12-16 18:00 | 122.44 | 96.77
2018-12-16 18:30 | 118.58 | 91.27
2018-12-16 19:00 | 122.48 | 93.72
2018-12-16 19:30 | 131.18 | 102.68
2018-12-16 20:00 | 133.84 | 106.88
2018-12-16 20:30 | 136.68 | 109.2
2018-12-16 21:00 | 128.22 | 99.46
2018-12-16 21:30 | 127.4 | 98.61
2018-12-16 22:00 | 133.43 | 105.46
2018-12-16 22:30 | 126.76 | 98.47
2018-12-16 23:00 | 132.34 | 106.28
2018-12-16 23:30 | 126.47 | 100.33
2018-12-17 | 122.08 | 95.22
2018-12-17 00:30 | 128.37 | 101.76
2018-12-17 01:00 | 132.52 | 106.95
2018-12-17 01:30 | 123.67 | 97.13
2018-12-17 02:00 | 124.68 | 99.43
2018-12-17 02:30 | 126.59 | 100.48
2018-12-17 03:00 | 122.86 | 97.12
2018-12-17 03:30 | 117.53 | 93.45
2018-12-17 04:00 | 133.9 | 110.72
2018-12-17 04:30 | 119.31 | 94.52
2018-12-17 05:00 | 114.51 | 89.2
2018-12-17 05:30 | 109.27 | 83.46
2018-12-17 06:00 | 109.37 | 84.49
2018-12-17 06:30 | 111.74 | 85.57
2018-12-17 07:00 | 111.35 | 85.73
2018-12-17 07:30 | 127.52 | 103.45
2018-12-17 08:00 | 127.84 | 102.15
2018-12-17 08:30 | 124.8 | 96.66
2018-12-17 09:00 | 121.86 | 93.39
2018-12-17 09:30 | 114.35 | 73.32
2018-12-17 10:00 | 118.2 | 70.73
2018-12-17 10:30 | 123.09 | 79.46
2018-12-17 11:00 | 118.94 | 70.72
2018-12-17 11:30 | 115.91 | 69.16
2018-12-17 12:00 | 117.32 | 69.43
2018-12-17 12:30 | 111.18 | 65.13
2018-12-17 13:00 | 114.41 | 68
2018-12-17 13:30 | 119.03 | 81.71
2018-12-17 14:00 | 118.83 | 74.21
2018-12-17 14:30 | 118.73 | 77.33
2018-12-17 15:00 | 116.89 | 71.24
2018-12-17 15:30 | 121.91 | 79.15
2018-12-17 16:00 | 119.46 | 79.33
2018-12-17 16:30 | 117.98 | 78.2
2018-12-17 17:00 | 117.64 | 79.21
2018-12-17 17:30 | 112.8 | 77.05
2018-12-17 18:00 | 119.99 | 89.28
2018-12-17 18:30 | 116.98 | 89.56
2018-12-17 19:00 | 128.46 | 102.59
2018-12-17 19:30 | 143.66 | 119.01
2018-12-17 20:00 | 141.6 | 116.49
2018-12-17 20:30 | 151.6 | 125.96
2018-12-17 21:00 | 146.22 | 120.23
2018-12-17 21:30 | 144.98 | 117.04
2018-12-17 22:00 | 133.97 | 105.58
2018-12-17 22:30 | 130.9 | 100.46
2018-12-17 23:00 | 138.15 | 107.53
2018-12-17 23:30 | 139.79 | 111.25
2018-12-18 | 138.33 | 109.57
2018-12-18 00:30 | 139.27 | 110.17
2018-12-18 01:00 | 139.64 | 110.77
2018-12-18 01:30 | 137.43 | 108.92
2018-12-18 02:00 | 137.37 | 108.78
2018-12-18 02:30 | 135.14 | 106.45
2018-12-18 03:00 | 139.02 | 110.22
2018-12-18 03:30 | 133.63 | 105.76
2018-12-18 04:00 | 138.47 | 112.53
2018-12-18 04:30 | 133.17 | 106.02
2018-12-18 05:00 | 136.76 | 110.15
2018-12-18 05:30 | 134.61 | 107.95
2018-12-18 06:00 | 121.97 | 92.75
2018-12-18 06:30 | 116.61 | 80.72
2018-12-18 07:00 | 119.66 | 75.88
2018-12-18 07:30 | 118.15 | 69.78
2018-12-18 08:00 | 121.64 | 74.3
2018-12-18 08:30 | 116.68 | 64.73
2018-12-18 09:00 | 122.26 | 73.9
2018-12-18 09:30 | 122.66 | 76.33
2018-12-18 10:00 | 125.42 | 78.92
2018-12-18 10:30 | 133.96 | 87.55
2018-12-18 11:00 | 125.95 | 77.93
2018-12-18 11:30 | 119.57 | 82.81
2018-12-18 12:00 | 122.53 | 82.1
2018-12-18 12:30 | 110.73 | 70.03
2018-12-18 13:00 | 108 | 64.66
2018-12-18 13:30 | 114.31 | 71.23
2018-12-18 14:00 | 128.03 | 82.66
2018-12-18 14:30 | 125.87 | 80.98
2018-12-18 15:00 | 130.9 | 85.78
2018-12-18 15:30 | 131.85 | 86
2018-12-18 16:00 | 133.03 | 89.18
2018-12-18 16:30 | 132.52 | 89.21
2018-12-18 17:00 | 127.37 | 84.71
2018-12-18 17:30 | 134.93 | 96.47
2018-12-18 18:00 | 139.55 | 107.27
2018-12-18 18:30 | 141.08 | 111.91
2018-12-18 19:00 | 142.29 | 115.49
2018-12-18 19:30 | 148.14 | 121.12
2018-12-18 20:00 | 151.01 | 123.58
2018-12-18 20:30 | 155.47 | 127.71
2018-12-18 21:00 | 150.01 | 123.43
2018-12-18 21:30 | 142.03 | 115.06
2018-12-18 22:00 | 147.49 | 118.39
2018-12-18 22:30 | 135.43 | 105.54
2018-12-18 23:00 | 136.52 | 106.94
2018-12-18 23:30 | 132.3 | 101.51
2018-12-19 | 134.22 | 102.39
2018-12-19 00:30 | 133.28 | 103.27
2018-12-19 01:00 | 138.35 | 107.8
2018-12-19 01:30 | 133.23 | 102.96
2018-12-19 02:00 | 132.5 | 102.35
2018-12-19 02:30 | 136.05 | 106.3
2018-12-19 03:00 | 129.71 | 100.92
2018-12-19 03:30 | 133.93 | 105.81
2018-12-19 04:00 | 131.71 | 103.36
2018-12-19 04:30 | 131.02 | 101.78
2018-12-19 05:00 | 124.31 | 94.14
2018-12-19 05:30 | 128.63 | 99.58
2018-12-19 06:00 | 131.86 | 104.18
2018-12-19 06:30 | 123.08 | 90.86
2018-12-19 07:00 | 120.16 | 87.17
2018-12-19 07:30 | 117.1 | 83.32
2018-12-19 08:00 | 121.74 | 88.39
2018-12-19 08:30 | 125.93 | 95.68
2018-12-19 09:00 | 119.72 | 84.36
2018-12-19 09:30 | 127.21 | 90.19
2018-12-19 10:00 | 139.95 | 103
2018-12-19 10:30 | 138.81 | 98.94
2018-12-19 11:00 | 133.72 | 92.42
2018-12-19 11:30 | 133.74 | 91.42
2018-12-19 12:00 | 135.28 | 93.31
2018-12-19 12:30 | 137.82 | 92.67
2018-12-19 13:00 | 133.86 | 85.67
2018-12-19 13:30 | 133.92 | 86.95
2018-12-19 14:00 | 131.02 | 88.91
2018-12-19 14:30 | 123.5 | 80.14
2018-12-19 15:00 | 125.89 | 79.74
2018-12-19 15:30 | 130.76 | 85.1
2018-12-19 16:00 | 137.83 | 92.97
2018-12-19 16:30 | 137.42 | 93.49
2018-12-19 17:00 | 136.94 | 97.61
2018-12-19 17:30 | 138.89 | 102.39
2018-12-19 18:00 | 133.96 | 100.57
2018-12-19 18:30 | 137.1 | 108.02
2018-12-19 19:00 | 139.93 | 114.01
2018-12-19 19:30 | 145.86 | 120.64
2018-12-19 20:00 | 145.62 | 120.13
2018-12-19 20:30 | 139.23 | 113.13
2018-12-19 21:00 | 134.83 | 107.84
2018-12-19 21:30 | 130.15 | 102.3
2018-12-19 22:00 | 133.92 | 105.21
2018-12-19 22:30 | 130.49 | 101.85
2018-12-19 23:00 | 134.91 | 106.17
2018-12-19 23:30 | 132.89 | 102.85
2018-12-20 | 123.91 | 93.29
2018-12-20 00:30 | 127.56 | 96.73
2018-12-20 01:00 | 125.09 | 94
2018-12-20 01:30 | 128.44 | 98.34
2018-12-20 02:00 | 126.8 | 97.21
2018-12-20 02:30 | 130.53 | 101.8
2018-12-20 03:00 | 129.19 | 99.25
2018-12-20 03:30 | 129.3 | 101.02
2018-12-20 04:00 | 127.43 | 99.41
2018-12-20 04:30 | 126.66 | 99.69
2018-12-20 05:00 | 128.75 | 99.01
2018-12-20 05:30 | 126.17 | 96.25
2018-12-20 06:00 | 128.37 | 99.18
2018-12-20 06:30 | 123.37 | 91.37
2018-12-20 07:00 | 121.59 | 91.56
2018-12-20 07:30 | 123.76 | 93.46
2018-12-20 08:00 | 129.27 | 96.83
2018-12-20 08:30 | 123.91 | 87.66
2018-12-20 09:00 | 124.98 | 86.02
2018-12-20 09:30 | 128.09 | 91.36
2018-12-20 10:00 | 120.41 | 74.15
2018-12-20 10:30 | 118.66 | 70.91
2018-12-20 11:00 | 122.2 | 73.21
2018-12-20 11:30 | 124.29 | 78.67
2018-12-20 12:00 | 123.25 | 80.56
2018-12-20 12:30 | 119.32 | 75.22
2018-12-20 13:00 | 120.16 | 75.59
2018-12-20 13:30 | 118.25 | 71.46
2018-12-20 14:00 | 120.57 | 77.42
2018-12-20 14:30 | 123.33 | 79.06
2018-12-20 15:00 | 121.57 | 76.29
2018-12-20 15:30 | 119.95 | 75.13
2018-12-20 16:00 | 120.5 | 76.43
2018-12-20 16:30 | 124.18 | 79.74
2018-12-20 17:00 | 121.04 | 76.14
2018-12-20 17:30 | 124.75 | 84.26
2018-12-20 18:00 | 125.23 | 88.33
2018-12-20 18:30 | 131.18 | 99.81
2018-12-20 19:00 | 126.83 | 98.79
2018-12-20 19:30 | 130.56 | 102.2
2018-12-20 20:00 | 140.13 | 111.99
2018-12-20 20:30 | 142.14 | 113.97
2018-12-20 21:00 | 138.13 | 109.01
2018-12-20 21:30 | 136.03 | 106.6
2018-12-20 22:00 | 125.01 | 94.15
2018-12-20 22:30 | 128.19 | 97.3
2018-12-20 23:00 | 134.41 | 105.36
2018-12-20 23:30 | 128.99 | 99.88
2018-12-21 | 130.19 | 103.15
2018-12-21 00:30 | 132.15 | 104.9
2018-12-21 01:00 | 128.55 | 100.26
2018-12-21 01:30 | 120.32 | 92.01
2018-12-21 02:00 | 120.34 | 91.24
2018-12-21 02:30 | 120.48 | 90.21
2018-12-21 03:00 | 124.39 | 95.52
2018-12-21 03:30 | 129.46 | 100.19
2018-12-21 04:00 | 125.35 | 95.96
2018-12-21 04:30 | 124.79 | 95.84
2018-12-21 05:00 | 129.1 | 100.41
2018-12-21 05:30 | 123.6 | 95.04
2018-12-21 06:00 | 123.94 | 93.68
2018-12-21 06:30 | 122.2 | 85.87
2018-12-21 07:00 | 120.72 | 79.26
2018-12-21 07:30 | 122.8 | 75.85
2018-12-21 08:00 | 125.51 | 75.56
2018-12-21 08:30 | 124.09 | 72.78
2018-12-21 09:00 | 126.16 | 80.64
2018-12-21 09:30 | 131.94 | 87.16
2018-12-21 10:00 | 124.81 | 75.31
2018-12-21 10:30 | 129.38 | 82.05
2018-12-21 11:00 | 133.97 | 88.02
2018-12-21 11:30 | 137.85 | 91.69
2018-12-21 12:00 | 129.96 | 82.23
2018-12-21 12:30 | 134.36 | 88.92
2018-12-21 13:00 | 132.87 | 87.64
2018-12-21 13:30 | 129.72 | 82.33
2018-12-21 14:00 | 134.54 | 88.88
2018-12-21 14:30 | 135.47 | 90.82
2018-12-21 15:00 | 133.96 | 89.1
2018-12-21 15:30 | 133.57 | 89.48
2018-12-21 16:00 | 138.67 | 95.85
2018-12-21 16:30 | 135.4 | 91.89
2018-12-21 17:00 | 139.2 | 98.62
2018-12-21 17:30 | 139.3 | 102.08
2018-12-21 18:00 | 141.06 | 108.59
2018-12-21 18:30 | 139.71 | 110.64
2018-12-21 19:00 | 146.67 | 118.6
2018-12-21 19:30 | 147.34 | 119.06
2018-12-21 20:00 | 148.39 | 120.27
2018-12-21 20:30 | 149.31 | 120.58
2018-12-21 21:00 | 136.5 | 108.16
2018-12-21 21:30 | 137.57 | 108.76
2018-12-21 22:00 | 143.4 | 114.94
2018-12-21 22:30 | 145.68 | 118.13
2018-12-21 23:00 | 137.11 | 108.73
2018-12-21 23:30 | 140.72 | 111.1
2018-12-22 | 137.33 | 108.34
2018-12-22 00:30 | 135.16 | 107.16
2018-12-22 01:00 | 139.47 | 110.57
2018-12-22 01:30 | 135.49 | 106.98
2018-12-22 02:00 | 135.67 | 107.65
2018-12-22 02:30 | 136.09 | 107.61
2018-12-22 03:00 | 137.29 | 109.45
2018-12-22 03:30 | 134.7 | 106.02
2018-12-22 04:00 | 130.25 | 100.39
2018-12-22 04:30 | 135.39 | 106.3
2018-12-22 05:00 | 133.07 | 104.97
2018-12-22 05:30 | 133.16 | 105.6
2018-12-22 06:00 | 138.93 | 110.35
2018-12-22 06:30 | 135.55 | 104.98
2018-12-22 07:00 | 134.31 | 97.62
2018-12-22 07:30 | 136.9 | 100.06
2018-12-22 08:00 | 130.48 | 92.09
2018-12-22 08:30 | 129.51 | 94.35
2018-12-22 09:00 | 128.42 | 85.36
2018-12-22 09:30 | 131.51 | 89.35
2018-12-22 10:00 | 133.82 | 88.55
2018-12-22 10:30 | 130.89 | 86.09
2018-12-22 11:00 | 124.9 | 77.46
2018-12-22 11:30 | 129.86 | 82.51
2018-12-22 12:00 | 134.53 | 89.56
2018-12-22 12:30 | 134.65 | 85.93
2018-12-22 13:00 | 132.28 | 87.22
2018-12-22 13:30 | 136.42 | 90.37
2018-12-22 14:00 | 135.96 | 93.06
2018-12-22 14:30 | 129.1 | 83.67
2018-12-22 15:00 | 132.78 | 93.7
2018-12-22 15:30 | 135.32 | 103.44
2018-12-22 16:00 | 135.73 | 106.24
2018-12-22 16:30 | 142.21 | 113.44
2018-12-22 17:00 | 134.26 | 104.89
2018-12-22 17:30 | 112.7 | 82.43
2018-12-22 18:00 | 76.48 | 49.12
2018-12-22 18:30 | 68.92 | 41.3
2018-12-22 19:00 | 73.89 | 48.63
2018-12-22 19:30 | 73.33 | 48.64
2018-12-22 20:00 | 77.21 | 53.71
2018-12-22 20:30 | 81.88 | 61.11
2018-12-22 21:00 | 79.34 | 63.65
2018-12-22 21:30 | 85.02 | 69.2
2018-12-22 22:00 | 83.87 | 68.89
2018-12-22 22:30 | 86.13 | 72.19
2018-12-22 23:00 | 100.77 | 86.62
2018-12-22 23:30 | 91.69 | 77.31
2018-12-23 | 90.34 | 75.85
2018-12-23 00:30 | 95.23 | 80.34
2018-12-23 01:00 | 88.49 | 73.4
2018-12-23 01:30 | 89.85 | 74.85
2018-12-23 02:00 | 93.88 | 78.64
2018-12-23 02:30 | 92.25 | 76.25
2018-12-23 03:00 | 88.29 | 72.34
2018-12-23 03:30 | 89.78 | 72.1
2018-12-23 04:00 | 92.49 | 74.37
2018-12-23 04:30 | 90.28 | 62.31
2018-12-23 05:00 | 91.55 | 62.64
2018-12-23 05:30 | 94.66 | 68.56
2018-12-23 06:00 | 93.38 | 66.05
2018-12-23 06:30 | 94.38 | 58.04
2018-12-23 07:00 | 97.5 | 55.34
2018-12-23 07:30 | 106.45 | 59.68
2018-12-23 08:00 | 105.81 | 55.9
2018-12-23 08:30 | 105.8 | 51.93
2018-12-23 09:00 | 105.85 | 53.29
2018-12-23 09:30 | 107.02 | 53.73
2018-12-23 10:00 | 104.75 | 53.54
2018-12-23 10:30 | 105.49 | 52.95
2018-12-23 11:00 | 101.07 | 50.26
2018-12-23 11:30 | 101 | 50.88
2018-12-23 12:00 | 99.32 | 54.35
2018-12-23 12:30 | 100.59 | 57.4
2018-12-23 13:00 | 97.54 | 57.68
2018-12-23 13:30 | 97.56 | 62.53
2018-12-23 14:00 | 98.9 | 61.85
2018-12-23 14:30 | 94.79 | 58.89
2018-12-23 15:00 | 97.18 | 63.6
2018-12-23 15:30 | 99.79 | 67.01
2018-12-23 16:00 | 103.09 | 73.6
2018-12-23 16:30 | 100.71 | 64.01
2018-12-23 17:00 | 112.11 | 76.38
2018-12-23 17:30 | 122.32 | 81.11
2018-12-23 18:00 | 130.73 | 99.76
2018-12-23 18:30 | 132.21 | 103.38
2018-12-23 19:00 | 125.78 | 95.39
2018-12-23 19:30 | 133.83 | 104.68
2018-12-23 20:00 | 128.65 | 98.93
2018-12-23 20:30 | 129.8 | 101.68
2018-12-23 21:00 | 118.04 | 91.18
2018-12-23 21:30 | 126.96 | 98.89
2018-12-23 22:00 | 125.24 | 97.34
2018-12-23 22:30 | 129.35 | 101.02
2018-12-23 23:00 | 125 | 96.2
2018-12-23 23:30 | 119.41 | 91.31
2018-12-24 | 124.18 | 97.28
2018-12-24 00:30 | 130.3 | 102.98
2018-12-24 01:00 | 125.57 | 97.5
2018-12-24 01:30 | 125.26 | 95.61
2018-12-24 02:00 | 123.95 | 95.64
2018-12-24 02:30 | 119.78 | 91.91
2018-12-24 03:00 | 120.2 | 92.77
2018-12-24 03:30 | 121.15 | 93.14
2018-12-24 04:00 | 115.81 | 89.26
2018-12-24 04:30 | 111.2 | 85.1
2018-12-24 05:00 | 112.91 | 85.55
2018-12-24 05:30 | 118.06 | 91.78
2018-12-24 06:00 | 114.49 | 84.98
2018-12-24 06:30 | 112.18 | 77.24
2018-12-24 07:00 | 110.76 | 71.26
2018-12-24 07:30 | 112.48 | 69.71
2018-12-24 08:00 | 117.78 | 72.9
2018-12-24 08:30 | 111.95 | 64.26
2018-12-24 09:00 | 114.22 | 67.08
2018-12-24 09:30 | 117.91 | 69.84
2018-12-24 10:00 | 120.22 | 75.17
2018-12-24 10:30 | 112.97 | 70.54
2018-12-24 11:00 | 112.3 | 68.17
2018-12-24 11:30 | 102.57 | 57.25
2018-12-24 12:00 | 104.64 | 63.06
2018-12-24 12:30 | 100.81 | 57.72
2018-12-24 13:00 | 96.66 | 48.96
2018-12-24 13:30 | 100.73 | 57.74
2018-12-24 14:00 | 94.84 | 48.02
2018-12-24 14:30 | 92.5 | 44.73
2018-12-24 15:00 | 94.43 | 51.26
2018-12-24 15:30 | 83.68 | 43.55
2018-12-24 16:00 | 69.56 | 27.75
2018-12-24 16:30 | 67.44 | 17.42
2018-12-24 17:00 | 67.34 | 19.6
2018-12-24 17:30 | 63.28 | 21.14
2018-12-24 18:00 | 58.02 | 30.88
2018-12-24 18:30 | 56 | 33.49
2018-12-24 19:00 | 57.3 | 34.91
2018-12-24 19:30 | 56.75 | 32.2
2018-12-24 20:00 | 59.83 | 36.36
2018-12-24 20:30 | 57.37 | 31.19
2018-12-24 21:00 | 58.24 | 32.97
2018-12-24 21:30 | 61.58 | 40.72
2018-12-24 22:00 | 63.73 | 43.93
2018-12-24 22:30 | 61.75 | 38.29
2018-12-24 23:00 | 57.22 | 27.59
2018-12-24 23:30 | 57.8 | 28.73
2018-12-25 | 57.82 | 28.46
2018-12-25 00:30 | 57.23 | 28.16
2018-12-25 01:00 | 57.75 | 29.18
2018-12-25 01:30 | 57.94 | 28.53
2018-12-25 02:00 | 59.46 | 32.98
2018-12-25 02:30 | 58.66 | 31.39
2018-12-25 03:00 | 58.04 | 24.58
2018-12-25 03:30 | 57.94 | 28.42
2018-12-25 04:00 | 55.58 | 26.91
2018-12-25 04:30 | 55.76 | 28.39
2018-12-25 05:00 | 54.92 | 24.58
2018-12-25 05:30 | 56.03 | 27.02
2018-12-25 06:00 | 53.95 | 23.13
2018-12-25 06:30 | 51.49 | 17.54
2018-12-25 07:00 | 53.47 | 18.61
2018-12-25 07:30 | 55.37 | 16.13
2018-12-25 08:00 | 56.87 | 18.94
2018-12-25 08:30 | 58.73 | 23.85
2018-12-25 09:00 | 56.82 | 17.46
2018-12-25 09:30 | 55.69 | 16.43
2018-12-25 10:00 | 59.2 | 24.44
2018-12-25 10:30 | 57.98 | 19.15
2018-12-25 11:00 | 60.42 | 24.39
2018-12-25 11:30 | 56.9 | 21.65
2018-12-25 12:00 | 57.14 | 20.75
2018-12-25 12:30 | 58.95 | 26.04
2018-12-25 13:00 | 57.54 | 22.67
2018-12-25 13:30 | 60.02 | 26.96
2018-12-25 14:00 | 58.4 | 25.11
2018-12-25 14:30 | 60.45 | 25.08
2018-12-25 15:00 | 58.91 | 23.61
2018-12-25 15:30 | 59.46 | 26.78
2018-12-25 16:00 | 60.77 | 26.39
2018-12-25 16:30 | 59.6 | 24.37
2018-12-25 17:00 | 59.44 | 25.54
2018-12-25 17:30 | 54.77 | 22.23
2018-12-25 18:00 | 52.18 | 25.66
2018-12-25 18:30 | 54.83 | 31.46
2018-12-25 19:00 | 58.23 | 33.76
2018-12-25 19:30 | 59.49 | 37.12
2018-12-25 20:00 | 59.9 | 38.07
2018-12-25 20:30 | 58.11 | 34.6
2018-12-25 21:00 | 56.62 | 32.45
2018-12-25 21:30 | 57.49 | 32.82
2018-12-25 22:00 | 57.77 | 33.15
2018-12-25 22:30 | 57.97 | 34.87
2018-12-25 23:00 | 58.61 | 36.01
2018-12-25 23:30 | 55.98 | 31.1
2018-12-26 | 56.8 | 31.45
2018-12-26 00:30 | 58.62 | 37.01
2018-12-26 01:00 | 57.78 | 33.95
2018-12-26 01:30 | 57.55 | 33.25
2018-12-26 02:00 | 56.97 | 33.37
2018-12-26 02:30 | 55.41 | 28.39
2018-12-26 03:00 | 55.58 | 28.67
2018-12-26 03:30 | 55.14 | 27.27
2018-12-26 04:00 | 56.69 | 29.57
2018-12-26 04:30 | 55.97 | 28.04
2018-12-26 05:00 | 56.41 | 29.49
2018-12-26 05:30 | 57.52 | 31.39
2018-12-26 06:00 | 55.88 | 29.32
2018-12-26 06:30 | 53.04 | 19.39
2018-12-26 07:00 | 55.21 | 18.22
2018-12-26 07:30 | 56.96 | 16.41
2018-12-26 08:00 | 60.74 | 18.05
2018-12-26 08:30 | 60.23 | 16.26
2018-12-26 09:00 | 60.7 | 15.36
2018-12-26 09:30 | 63.19 | 17.84
2018-12-26 10:00 | 65.25 | 19.25
2018-12-26 10:30 | 65.42 | 18.08
2018-12-26 11:00 | 68.59 | 21.52
2018-12-26 11:30 | 76.01 | 28.58
2018-12-26 12:00 | 73.86 | 23.39
2018-12-26 12:30 | 74.48 | 24.53
2018-12-26 13:00 | 74.23 | 25.97
2018-12-26 13:30 | 76.17 | 31.21
2018-12-26 14:00 | 76.38 | 30.45
2018-12-26 14:30 | 76.32 | 29.23
2018-12-26 15:00 | 75.52 | 27.92
2018-12-26 15:30 | 82.13 | 37.12
2018-12-26 16:00 | 79.6 | 36.06
2018-12-26 16:30 | 75.03 | 29.28
2018-12-26 17:00 | 77.91 | 34.99
2018-12-26 17:30 | 78.39 | 40.81
2018-12-26 18:00 | 74.45 | 42.76
2018-12-26 18:30 | 74.45 | 52.04
2018-12-26 19:00 | 82.96 | 63.14
2018-12-26 19:30 | 83.46 | 64.46
2018-12-26 20:00 | 86.56 | 67.8
2018-12-26 20:30 | 100.92 | 82.93
2018-12-26 21:00 | 102.82 | 83.42
2018-12-26 21:30 | 98.98 | 80.61
2018-12-26 22:00 | 99.18 | 80.38
2018-12-26 22:30 | 104.25 | 86.18
2018-12-26 23:00 | 100.29 | 81.13
2018-12-26 23:30 | 99.85 | 81.36
2018-12-27 | 101.87 | 83.46
2018-12-27 00:30 | 106.8 | 88.93
2018-12-27 01:00 | 110.32 | 92.14
2018-12-27 01:30 | 103.95 | 84.83
2018-12-27 02:00 | 103.41 | 84.13
2018-12-27 02:30 | 103.1 | 83.81
2018-12-27 03:00 | 104.06 | 84.81
2018-12-27 03:30 | 103.79 | 85.15
2018-12-27 04:00 | 110.12 | 92.7
2018-12-27 04:30 | 106.84 | 91.33
2018-12-27 05:00 | 114.68 | 97.97
2018-12-27 05:30 | 110.42 | 92.69
2018-12-27 06:00 | 107.77 | 89.39
2018-12-27 06:30 | 103.04 | 79.43
2018-12-27 07:00 | 100.74 | 73.75
2018-12-27 07:30 | 99.84 | 65.78
2018-12-27 08:00 | 98.12 | 60.92
2018-12-27 08:30 | 100.57 | 62.33
2018-12-27 09:00 | 94 | 53.44
2018-12-27 09:30 | 99.91 | 59.81
2018-12-27 10:00 | 103.57 | 65.35
2018-12-27 10:30 | 97.37 | 56.19
2018-12-27 11:00 | 95.06 | 55.83
2018-12-27 11:30 | 103.84 | 69.31
2018-12-27 12:00 | 104.62 | 67.94
2018-12-27 12:30 | 98.19 | 57.92
2018-12-27 13:00 | 101.25 | 64.08
2018-12-27 13:30 | 102.85 | 65.67
2018-12-27 14:00 | 109.33 | 74.53
2018-12-27 14:30 | 105.48 | 70.04
2018-12-27 15:00 | 103.82 | 68.81
2018-12-27 15:30 | 105.12 | 71.35
2018-12-27 16:00 | 114.47 | 80.64
2018-12-27 16:30 | 115.04 | 80.89
2018-12-27 17:00 | 111.66 | 75.37
2018-12-27 17:30 | 112.98 | 81.59
2018-12-27 18:00 | 113.05 | 88.56
2018-12-27 18:30 | 113.97 | 91.67
2018-12-27 19:00 | 113.22 | 93.07
2018-12-27 19:30 | 114.51 | 94.84
2018-12-27 20:00 | 119.59 | 99.45
2018-12-27 20:30 | 121.41 | 101.89
2018-12-27 21:00 | 122.37 | 103.59
2018-12-27 21:30 | 124.4 | 105.86
2018-12-27 22:00 | 120.75 | 100.13
2018-12-27 22:30 | 115.58 | 94.45
2018-12-27 23:00 | 112.37 | 90.88
2018-12-27 23:30 | 114.02 | 92.74
2018-12-28 | 117.57 | 97.12
2018-12-28 00:30 | 117.32 | 96.89
2018-12-28 01:00 | 116.33 | 95.71
2018-12-28 01:30 | 117.57 | 97.86
2018-12-28 02:00 | 117.98 | 99.02
2018-12-28 02:30 | 123.18 | 103.59
2018-12-28 03:00 | 112.1 | 92.73
2018-12-28 03:30 | 113.22 | 93.77
2018-12-28 04:00 | 111.66 | 92.14
2018-12-28 04:30 | 111.36 | 91.92
2018-12-28 05:00 | 115.67 | 97.59
2018-12-28 05:30 | 110.77 | 92.73
2018-12-28 06:00 | 103.13 | 82.51
2018-12-28 06:30 | 99.65 | 74.86
2018-12-28 07:00 | 106.08 | 75.76
2018-12-28 07:30 | 109.23 | 73.4
2018-12-28 08:00 | 117.73 | 82.32
2018-12-28 08:30 | 109.76 | 71.65
2018-12-28 09:00 | 105.15 | 62.78
2018-12-28 09:30 | 115.44 | 73.31
2018-12-28 10:00 | 111.1 | 73.27
2018-12-28 10:30 | 117.48 | 80.52
2018-12-28 11:00 | 109.23 | 69.39
2018-12-28 11:30 | 113.55 | 75.13
2018-12-28 12:00 | 108.3 | 71.62
2018-12-28 12:30 | 111.45 | 75.19
2018-12-28 13:00 | 116.55 | 80.41
2018-12-28 13:30 | 118.24 | 82.44
2018-12-28 14:00 | 117.14 | 80.45
2018-12-28 14:30 | 118.83 | 82.76
2018-12-28 15:00 | 123.42 | 85.66
2018-12-28 15:30 | 116.28 | 79.6
2018-12-28 16:00 | 124.49 | 89.29
2018-12-28 16:30 | 118.74 | 82.92
2018-12-28 17:00 | 116.45 | 82.45
2018-12-28 17:30 | 122.13 | 92.92
2018-12-28 18:00 | 120.73 | 95.48
2018-12-28 18:30 | 112.42 | 90.88
2018-12-28 19:00 | 110.55 | 91.52
2018-12-28 19:30 | 122.14 | 102.79
2018-12-28 20:00 | 122.78 | 101.62
2018-12-28 20:30 | 130.49 | 109.38
2018-12-28 21:00 | 128.39 | 108.53
2018-12-28 21:30 | 120.18 | 98.91
2018-12-28 22:00 | 120.61 | 100.3
2018-12-28 22:30 | 125.87 | 105.57
2018-12-28 23:00 | 124.26 | 105.74
2018-12-28 23:30 | 123.6 | 105.35
2018-12-29 | 127.16 | 107.98
2018-12-29 00:30 | 122.03 | 101.58
2018-12-29 01:00 | 115.49 | 94.65
2018-12-29 01:30 | 117.94 | 97.8
2018-12-29 02:00 | 116.85 | 97.49
2018-12-29 02:30 | 120.23 | 100.38
2018-12-29 03:00 | 124.6 | 105.25
2018-12-29 03:30 | 116.2 | 96.91
2018-12-29 04:00 | 116.17 | 96.06
2018-12-29 04:30 | 117.71 | 97.73
2018-12-29 05:00 | 112.56 | 91.43
2018-12-29 05:30 | 112.76 | 92.52
2018-12-29 06:00 | 117.8 | 99.06
2018-12-29 06:30 | 110.8 | 87.75
2018-12-29 07:00 | 111.36 | 85.51
2018-12-29 07:30 | 114.49 | 81.96
2018-12-29 08:00 | 112.02 | 75.55
2018-12-29 08:30 | 115.07 | 80.18
2018-12-29 09:00 | 112.12 | 80.06
2018-12-29 09:30 | 110.41 | 76.55
2018-12-29 10:00 | 115.26 | 80.81
2018-12-29 10:30 | 110.83 | 80.16
2018-12-29 11:00 | 109.3 | 78.92
2018-12-29 11:30 | 114.78 | 80.84
2018-12-29 12:00 | 115.84 | 80.29
2018-12-29 12:30 | 114.38 | 79.04
2018-12-29 13:00 | 109.97 | 77.88
2018-12-29 13:30 | 112.91 | 85.64
2018-12-29 14:00 | 105.21 | 74.64
2018-12-29 14:30 | 106.28 | 78.17
2018-12-29 15:00 | 104.22 | 74.85
2018-12-29 15:30 | 107.02 | 78.66
2018-12-29 16:00 | 106.17 | 77.07
2018-12-29 16:30 | 114.33 | 81.83
2018-12-29 17:00 | 112.99 | 86.5
2018-12-29 17:30 | 115.47 | 90.31
2018-12-29 18:00 | 121.22 | 95.39
2018-12-29 18:30 | 116.99 | 93.99
2018-12-29 19:00 | 117.84 | 96.16
2018-12-29 19:30 | 124.89 | 103.89
2018-12-29 20:00 | 131.19 | 109.62
2018-12-29 20:30 | 131.35 | 109.39
2018-12-29 21:00 | 127.22 | 104.45
2018-12-29 21:30 | 121.2 | 99.19
2018-12-29 22:00 | 125.8 | 104.2
2018-12-29 22:30 | 121.27 | 99.91
2018-12-29 23:00 | 122.41 | 102.36
2018-12-29 23:30 | 119.25 | 100.18
2018-12-30 | 117.07 | 95.79
2018-12-30 00:30 | 113.7 | 92.23
2018-12-30 01:00 | 119.14 | 98.43
2018-12-30 01:30 | 121.87 | 100.94
2018-12-30 02:00 | 119.12 | 97.84
2018-12-30 02:30 | 123.59 | 102.57
2018-12-30 03:00 | 117.07 | 96.41
2018-12-30 03:30 | 119.86 | 100.84
2018-12-30 04:00 | 124.31 | 105.41
2018-12-30 04:30 | 118.22 | 99.37
2018-12-30 05:00 | 125.25 | 105.39
2018-12-30 05:30 | 121.8 | 101.03
2018-12-30 06:00 | 109.35 | 87.7
2018-12-30 06:30 | 108.62 | 83.51
2018-12-30 07:00 | 115.26 | 88.68
2018-12-30 07:30 | 114.28 | 79.17
2018-12-30 08:00 | 109.73 | 77.09
2018-12-30 08:30 | 109.25 | 73.76
2018-12-30 09:00 | 114.9 | 75.01
2018-12-30 09:30 | 111.4 | 68.21
2018-12-30 10:00 | 111.06 | 69.17
2018-12-30 10:30 | 120.56 | 84.01
2018-12-30 11:00 | 112.67 | 74.99
2018-12-30 11:30 | 116.68 | 79.69
2018-12-30 12:00 | 120.54 | 83
2018-12-30 12:30 | 116.19 | 77.1
2018-12-30 13:00 | 116.61 | 79.13
2018-12-30 13:30 | 113.85 | 77.21
2018-12-30 14:00 | 115.07 | 76.93
2018-12-30 14:30 | 118.64 | 81.97
2018-12-30 15:00 | 119.26 | 82.81
2018-12-30 15:30 | 119.98 | 82.19
2018-12-30 16:00 | 125.93 | 90.89
2018-12-30 16:30 | 123.63 | 86.27
2018-12-30 17:00 | 127.27 | 91.13
2018-12-30 17:30 | 128.01 | 95.87
2018-12-30 18:00 | 120.82 | 93.01
2018-12-30 18:30 | 123.88 | 101.18
2018-12-30 19:00 | 121.21 | 99.68
2018-12-30 19:30 | 125.06 | 103.29
2018-12-30 20:00 | 127.28 | 106.37
2018-12-30 20:30 | 124.31 | 103.07
2018-12-30 21:00 | 126.57 | 104.98
2018-12-30 21:30 | 127.26 | 105.9
2018-12-30 22:00 | 125.06 | 103.5
2018-12-30 22:30 | 133.74 | 112.86
2018-12-30 23:00 | 125.31 | 104.55
2018-12-30 23:30 | 127.28 | 104.8
2018-12-31 | 119.24 | 96.73
2018-12-31 00:30 | 120.6 | 98.18
2018-12-31 01:00 | 122.48 | 100.22
2018-12-31 01:30 | 122.4 | 101.2
2018-12-31 02:00 | 123.11 | 102.14
2018-12-31 02:30 | 116.55 | 97.65
2018-12-31 03:00 | 120.26 | 99.75
2018-12-31 03:30 | 125.57 | 105.56
2018-12-31 04:00 | 128.18 | 109.16
2018-12-31 04:30 | 120.98 | 100.09
2018-12-31 05:00 | 118.9 | 99.39
2018-12-31 05:30 | 108.82 | 89.04
2018-12-31 06:00 | 107.37 | 88.02
2018-12-31 06:30 | 98.31 | 74.85
2018-12-31 07:00 | 95.91 | 70.13
2018-12-31 07:30 | 101.07 | 69.92
2018-12-31 08:00 | 106.95 | 72
2018-12-31 08:30 | 108.68 | 75.39
2018-12-31 09:00 | 120.67 | 84.54
2018-12-31 09:30 | 119.15 | 80.58
2018-12-31 10:00 | 113.53 | 71.08
2018-12-31 10:30 | 115.88 | 73.3
2018-12-31 11:00 | 117.7 | 76
2018-12-31 11:30 | 119.09 | 80.15
2018-12-31 12:00 | 116.92 | 74.5
2018-12-31 12:30 | 117.01 | 76.78
2018-12-31 13:00 | 116.51 | 77.4
2018-12-31 13:30 | 120.14 | 83.26
2018-12-31 14:00 | 123.19 | 85.5
2018-12-31 14:30 | 122.09 | 84.28
2018-12-31 15:00 | 119.29 | 78.55
2018-12-31 15:30 | 118.18 | 76.66
2018-12-31 16:00 | 121.42 | 83.29
2018-12-31 16:30 | 125.12 | 86.64
2018-12-31 17:00 | 123.67 | 86.63
2018-12-31 17:30 | 129.36 | 98.13
2018-12-31 18:00 | 129.96 | 104.01
2018-12-31 18:30 | 116.16 | 93.38
2018-12-31 19:00 | 124.24 | 103.43
2018-12-31 19:30 | 123.81 | 103.85
2018-12-31 20:00 | 121.28 | 100.83
2018-12-31 20:30 | 118.19 | 96.22
2018-12-31 21:00 | 121.01 | 100.13
2018-12-31 21:30 | 127.58 | 106.97
2018-12-31 22:00 | 129.83 | 106.88
2018-12-31 22:30 | 138.41 | 117.03
2018-12-31 23:00 | 133.85 | 112.15
2018-12-31 23:30 | 130.65 | 108.14
2019-01-01 | 120.89 | 99.61
2019-01-01 00:30 | 120.58 | 99.29
2019-01-01 01:00 | 120.62 | 98.73
2019-01-01 01:30 | 118.6 | 97.24
2019-01-01 02:00 | 114.91 | 93.87
2019-01-01 02:30 | 117.94 | 97.25
2019-01-01 03:00 | 111.91 | 90.95
2019-01-01 03:30 | 114.66 | 93.69
2019-01-01 04:00 | 120.74 | 99.58
2019-01-01 04:30 | 123.49 | 102.32
2019-01-01 05:00 | 121.24 | 100.31
2019-01-01 05:30 | 119.53 | 98.82
2019-01-01 06:00 | 120.28 | 98.32
2019-01-01 06:30 | 115.68 | 90.96
2019-01-01 07:00 | 118.61 | 88.35
2019-01-01 07:30 | 121.75 | 85.73
2019-01-01 08:00 | 118.51 | 76.95
2019-01-01 08:30 | 119.52 | 77.33
2019-01-01 09:00 | 121.12 | 80.56
2019-01-01 09:30 | 120.43 | 81.57
2019-01-01 10:00 | 115.34 | 78.15
2019-01-01 10:30 | 121.13 | 83.91
2019-01-01 11:00 | 122.92 | 86.09
2019-01-01 11:30 | 114.1 | 72.8
2019-01-01 12:00 | 118.87 | 78.79
2019-01-01 12:30 | 119.95 | 78.05
2019-01-01 13:00 | 117.15 | 73.97
2019-01-01 13:30 | 122.77 | 80.83
2019-01-01 14:00 | 119.75 | 76.79
2019-01-01 14:30 | 123.91 | 83.57
2019-01-01 15:00 | 125.89 | 86.49
2019-01-01 15:30 | 122.61 | 82.27
2019-01-01 16:00 | 121.77 | 82.57
2019-01-01 16:30 | 118.36 | 79.16
2019-01-01 17:00 | 120.06 | 84.12
2019-01-01 17:30 | 124.13 | 94.06
2019-01-01 18:00 | 126.41 | 99.8
2019-01-01 18:30 | 118.71 | 95.72
2019-01-01 19:00 | 122.29 | 101.6
2019-01-01 19:30 | 128.35 | 106.07
2019-01-01 20:00 | 131.63 | 109.27
2019-01-01 20:30 | 127.3 | 105.37
2019-01-01 21:00 | 126.06 | 103.47
2019-01-01 21:30 | 120.65 | 98.13
2019-01-01 22:00 | 118.92 | 97.37
2019-01-01 22:30 | 124.88 | 103.69
2019-01-01 23:00 | 132.42 | 111.64
2019-01-01 23:30 | 121.56 | 98.43
2019-01-02 | 122.64 | 99.9
2019-01-02 00:30 | 121.58 | 99.28
2019-01-02 01:00 | 125.05 | 102.76
2019-01-02 01:30 | 126.41 | 104.19
2019-01-02 02:00 | 123.85 | 101.88
2019-01-02 02:30 | 115.08 | 91.52
2019-01-02 03:00 | 119.27 | 97.17
2019-01-02 03:30 | 112.46 | 90.58
2019-01-02 04:00 | 114.19 | 93.63
2019-01-02 04:30 | 114.1 | 93.85
2019-01-02 05:00 | 105.98 | 86.38
2019-01-02 05:30 | 108.07 | 88.31
2019-01-02 06:00 | 110.86 | 92.47
2019-01-02 06:30 | 100.15 | 77.18
2019-01-02 07:00 | 99.05 | 70.66
2019-01-02 07:30 | 94.99 | 60.75
2019-01-02 08:00 | 100.71 | 66.62
2019-01-02 08:30 | 98.49 | 65.73
2019-01-02 09:00 | 95.66 | 56.84
2019-01-02 09:30 | 99.6 | 60.91
2019-01-02 10:00 | 96.95 | 57.87
2019-01-02 10:30 | 99.2 | 61.46
2019-01-02 11:00 | 106.39 | 67.54
2019-01-02 11:30 | 106.6 | 70.81
2019-01-02 12:00 | 106.62 | 68.42
2019-01-02 12:30 | 106.89 | 68.1
2019-01-02 13:00 | 105.25 | 68.2
2019-01-02 13:30 | 97.74 | 57.99
2019-01-02 14:00 | 98.62 | 59.99
2019-01-02 14:30 | 100.79 | 64.4
2019-01-02 15:00 | 112.4 | 77.95
2019-01-02 15:30 | 109.39 | 73.42
2019-01-02 16:00 | 106.3 | 70.22
2019-01-02 16:30 | 110.18 | 78.54
2019-01-02 17:00 | 105.86 | 75.98
2019-01-02 17:30 | 107.91 | 81.81
2019-01-02 18:00 | 102.42 | 80.9
2019-01-02 18:30 | 97.82 | 79.7
2019-01-02 19:00 | 104.62 | 88.11
2019-01-02 19:30 | 107.77 | 90.81
2019-01-02 20:00 | 107.01 | 89.86
2019-01-02 20:30 | 111.07 | 94.49
2019-01-02 21:00 | 117.25 | 100.85
2019-01-02 21:30 | 109.23 | 92.07
2019-01-02 22:00 | 112.95 | 94.99
2019-01-02 22:30 | 111.42 | 93.73
2019-01-02 23:00 | 111.91 | 92.65
2019-01-02 23:30 | 110.31 | 90.49
2019-01-03 | 110.32 | 91.34
2019-01-03 00:30 | 110.6 | 92.6
2019-01-03 01:00 | 114.41 | 94.81
2019-01-03 01:30 | 117.79 | 97.32
2019-01-03 02:00 | 106.56 | 87.19
2019-01-03 02:30 | 112.31 | 94.88
2019-01-03 03:00 | 105.06 | 88.03
2019-01-03 03:30 | 108.94 | 90.02
2019-01-03 04:00 | 107.11 | 86.85
2019-01-03 04:30 | 105.55 | 86.77
2019-01-03 05:00 | 104.16 | 85.8
2019-01-03 05:30 | 104.78 | 86.17
2019-01-03 06:00 | 102.47 | 81.17
2019-01-03 06:30 | 105.83 | 81.29
2019-01-03 07:00 | 100.92 | 70.56
2019-01-03 07:30 | 103.07 | 66.45
2019-01-03 08:00 | 102.92 | 63.07
2019-01-03 08:30 | 105.55 | 67.84
2019-01-03 09:00 | 107.08 | 72.5
2019-01-03 09:30 | 107.71 | 75.11
2019-01-03 10:00 | 102.62 | 65.82
2019-01-03 10:30 | 106.75 | 67.57
2019-01-03 11:00 | 107.61 | 67.22
2019-01-03 11:30 | 115.03 | 77.01
2019-01-03 12:00 | 101.62 | 64.1
2019-01-03 12:30 | 114.25 | 76.74
2019-01-03 13:00 | 104.92 | 64.22
2019-01-03 13:30 | 101.84 | 60.81
2019-01-03 14:00 | 102.26 | 59.83
2019-01-03 14:30 | 105.42 | 63.47
2019-01-03 15:00 | 102.08 | 61.27
2019-01-03 15:30 | 101.39 | 65.81
2019-01-03 16:00 | 104.38 | 68.62
2019-01-03 16:30 | 114.99 | 77.91
2019-01-03 17:00 | 109.76 | 74.22
2019-01-03 17:30 | 116.86 | 87.81
2019-01-03 18:00 | 118.92 | 92.06
2019-01-03 18:30 | 122.69 | 101.19
2019-01-03 19:00 | 122.44 | 104.12
2019-01-03 19:30 | 131.88 | 114.54
2019-01-03 20:00 | 113.76 | 98.22
2019-01-03 20:30 | 113.69 | 99.21
2019-01-03 21:00 | 115.54 | 99.4
2019-01-03 21:30 | 111.03 | 94.41
2019-01-03 22:00 | 112.61 | 94.94
2019-01-03 22:30 | 104.06 | 86.58
2019-01-03 23:00 | 112.94 | 95.79
2019-01-03 23:30 | 118.47 | 101.73
2019-01-04 | 115.49 | 99.59
2019-01-04 00:30 | 117.47 | 101.73
2019-01-04 01:00 | 110.8 | 94.37
2019-01-04 01:30 | 113.77 | 96.74
2019-01-04 02:00 | 113.68 | 96.5
2019-01-04 02:30 | 113.83 | 96.83
2019-01-04 03:00 | 119.12 | 102.76
2019-01-04 03:30 | 115.19 | 98.87
2019-01-04 04:00 | 115.57 | 98.88
2019-01-04 04:30 | 113.32 | 96.96
2019-01-04 05:00 | 111.05 | 94.1
2019-01-04 05:30 | 117.07 | 100.22
2019-01-04 06:00 | 108.13 | 90.51
2019-01-04 06:30 | 94.96 | 73.56
2019-01-04 07:00 | 104.26 | 79.48
2019-01-04 07:30 | 109.64 | 82.54
2019-01-04 08:00 | 109.6 | 78.66
2019-01-04 08:30 | 107.35 | 72.08
2019-01-04 09:00 | 106.12 | 69.2
2019-01-04 09:30 | 113.6 | 77.27
2019-01-04 10:00 | 111.13 | 74.38
2019-01-04 10:30 | 106.24 | 70.06
2019-01-04 11:00 | 107.22 | 75.61
2019-01-04 11:30 | 105.55 | 71.63
2019-01-04 12:00 | 109.32 | 75.49
2019-01-04 12:30 | 113.05 | 76.96
2019-01-04 13:00 | 105.36 | 72.12
2019-01-04 13:30 | 107.38 | 71.85
2019-01-04 14:00 | 110.28 | 75.64
2019-01-04 14:30 | 110.84 | 75.84
2019-01-04 15:00 | 106.74 | 74.25
2019-01-04 15:30 | 102.18 | 71.33
2019-01-04 16:00 | 102.76 | 70.48
2019-01-04 16:30 | 110.3 | 86.39
2019-01-04 17:00 | 110.81 | 84.63
2019-01-04 17:30 | 110.89 | 87.93
2019-01-04 18:00 | 102.6 | 85.1
2019-01-04 18:30 | 100.23 | 84.79
2019-01-04 19:00 | 114.62 | 99.75
2019-01-04 19:30 | 115.87 | 100.48
2019-01-04 20:00 | 126.43 | 111.26
2019-01-04 20:30 | 122.58 | 104.98
2019-01-04 21:00 | 120.66 | 101.71
2019-01-04 21:30 | 122.66 | 103.72
2019-01-04 22:00 | 114.94 | 96.38
2019-01-04 22:30 | 120.6 | 102.52
2019-01-04 23:00 | 111.95 | 93.97
2019-01-04 23:30 | 112.64 | 94.3
2019-01-05 | 110.35 | 91.7
2019-01-05 00:30 | 116.42 | 98.56
2019-01-05 01:00 | 116.6 | 98.12
2019-01-05 01:30 | 119.15 | 102.62
2019-01-05 02:00 | 121.2 | 104.45
2019-01-05 02:30 | 119.14 | 102.62
2019-01-05 03:00 | 118.06 | 101.45
2019-01-05 03:30 | 118.96 | 101.69
2019-01-05 04:00 | 120.15 | 102.66
2019-01-05 04:30 | 124.08 | 106.37
2019-01-05 05:00 | 108.42 | 93.69
2019-01-05 05:30 | 107.23 | 92.02
2019-01-05 06:00 | 102.37 | 84.72
2019-01-05 06:30 | 106.35 | 86.04
2019-01-05 07:00 | 112.5 | 89.82
2019-01-05 07:30 | 106.28 | 76.86
2019-01-05 08:00 | 106.93 | 73.9
2019-01-05 08:30 | 110.59 | 81.72
2019-01-05 09:00 | 116.61 | 82.69
2019-01-05 09:30 | 116.21 | 86.73
2019-01-05 10:00 | 109.07 | 76.31
2019-01-05 10:30 | 109.27 | 78.09
2019-01-05 11:00 | 109.83 | 78.92
2019-01-05 11:30 | 114.04 | 80.05
2019-01-05 12:00 | 111.89 | 77.18
2019-01-05 12:30 | 107.27 | 75.24
2019-01-05 13:00 | 102.46 | 72.3
2019-01-05 13:30 | 106 | 69.64
2019-01-05 14:00 | 107.35 | 73.46
2019-01-05 14:30 | 99.99 | 65.55
2019-01-05 15:00 | 111.57 | 77.84
2019-01-05 15:30 | 113.01 | 80.57
2019-01-05 16:00 | 109.75 | 77.89
2019-01-05 16:30 | 110.79 | 80.71
2019-01-05 17:00 | 116.32 | 85.61
2019-01-05 17:30 | 123.58 | 95.54
2019-01-05 18:00 | 127.77 | 105.02
2019-01-05 18:30 | 125.3 | 106.95
2019-01-05 19:00 | 128.25 | 110.45
2019-01-05 19:30 | 127.49 | 109.29
2019-01-05 20:00 | 141.86 | 122.72
2019-01-05 20:30 | 133.83 | 115.17
2019-01-05 21:00 | 131.78 | 113.11
2019-01-05 21:30 | 124.56 | 106.32
2019-01-05 22:00 | 127.27 | 109.05
2019-01-05 22:30 | 124.97 | 107.55
2019-01-05 23:00 | 126.68 | 108.44
2019-01-05 23:30 | 118.07 | 100.44
2019-01-06 | 119.82 | 102.74
2019-01-06 00:30 | 117.41 | 100.78
2019-01-06 01:00 | 115.83 | 98.26
2019-01-06 01:30 | 120.89 | 103.3
2019-01-06 02:00 | 116.77 | 99
2019-01-06 02:30 | 119.19 | 100.75
2019-01-06 03:00 | 115.2 | 95.72
2019-01-06 03:30 | 117.41 | 97.49
2019-01-06 04:00 | 120.19 | 100.25
2019-01-06 04:30 | 121.38 | 102.89
2019-01-06 05:00 | 125.21 | 106.72
2019-01-06 05:30 | 119.54 | 103.62
2019-01-06 06:00 | 118.75 | 101.94
2019-01-06 06:30 | 110.49 | 90.63
2019-01-06 07:00 | 108 | 83.23
2019-01-06 07:30 | 111.64 | 82.49
2019-01-06 08:00 | 112.92 | 80.23
2019-01-06 08:30 | 110.72 | 78.26
2019-01-06 09:00 | 106.81 | 75.39
2019-01-06 09:30 | 109.53 | 79.43
2019-01-06 10:00 | 108.17 | 76.49
2019-01-06 10:30 | 114.47 | 81.64
2019-01-06 11:00 | 119.27 | 86.08
2019-01-06 11:30 | 113.69 | 79.48
2019-01-06 12:00 | 118.72 | 85.65
2019-01-06 12:30 | 113.69 | 77.32
2019-01-06 13:00 | 116.88 | 81.29
2019-01-06 13:30 | 112.12 | 75.38
2019-01-06 14:00 | 113.28 | 77.71
2019-01-06 14:30 | 120.15 | 87.34
2019-01-06 15:00 | 117.33 | 83.97
2019-01-06 15:30 | 121.28 | 90.14
2019-01-06 16:00 | 120.19 | 90.68
2019-01-06 16:30 | 123.57 | 94.09
2019-01-06 17:00 | 120.43 | 91.18
2019-01-06 17:30 | 114.27 | 88.1
2019-01-06 18:00 | 116.37 | 92.85
2019-01-06 18:30 | 114.84 | 95.03
2019-01-06 19:00 | 122.75 | 105.59
2019-01-06 19:30 | 120.07 | 102.75
2019-01-06 20:00 | 124.49 | 107.73
2019-01-06 20:30 | 131.01 | 113.87
2019-01-06 21:00 | 116.82 | 98.55
2019-01-06 21:30 | 120.08 | 101.64
2019-01-06 22:00 | 124.66 | 106.93
2019-01-06 22:30 | 131.06 | 113.8
2019-01-06 23:00 | 122.98 | 105.38
2019-01-06 23:30 | 123.8 | 104.94
2019-01-07 | 118.95 | 100.45
2019-01-07 00:30 | 120.99 | 101.98
2019-01-07 01:00 | 122.61 | 104.02
2019-01-07 01:30 | 128.43 | 110.03
2019-01-07 02:00 | 129.51 | 111.6
2019-01-07 02:30 | 116.92 | 97.73
2019-01-07 03:00 | 116.88 | 97.75
2019-01-07 03:30 | 106.7 | 88.37
2019-01-07 04:00 | 110.21 | 93.89
2019-01-07 04:30 | 112.74 | 95.73
2019-01-07 05:00 | 113.31 | 95.66
2019-01-07 05:30 | 113.59 | 95.57
2019-01-07 06:00 | 116.34 | 99.31
2019-01-07 06:30 | 107.32 | 87.33
2019-01-07 07:00 | 110.75 | 88.98
2019-01-07 07:30 | 107.05 | 80.73
2019-01-07 08:00 | 111.03 | 81.47
2019-01-07 08:30 | 104.46 | 72.74
2019-01-07 09:00 | 106.08 | 78.77
2019-01-07 09:30 | 106.58 | 75.34
2019-01-07 10:00 | 104.08 | 76.84
2019-01-07 10:30 | 103.26 | 71.25
2019-01-07 11:00 | 98.87 | 62.42
2019-01-07 11:30 | 102.69 | 68.43
2019-01-07 12:00 | 107.82 | 77.94
2019-01-07 12:30 | 104.6 | 74.95
2019-01-07 13:00 | 109.27 | 81.58
2019-01-07 13:30 | 106.24 | 70.26
2019-01-07 14:00 | 109.02 | 75.8
2019-01-07 14:30 | 109.34 | 77.2
2019-01-07 15:00 | 115.31 | 89.26
2019-01-07 15:30 | 109.6 | 77.42
2019-01-07 16:00 | 106.02 | 77.66
2019-01-07 16:30 | 118.31 | 96.16
2019-01-07 17:00 | 113.35 | 85.63
2019-01-07 17:30 | 121.54 | 98.51
2019-01-07 18:00 | 115.68 | 92.64
2019-01-07 18:30 | 109.53 | 90.11
2019-01-07 19:00 | 119.65 | 101.89
2019-01-07 19:30 | 120.24 | 102.21
2019-01-07 20:00 | 114.82 | 95.5
2019-01-07 20:30 | 115.04 | 94.63
2019-01-07 21:00 | 120.81 | 100.64
2019-01-07 21:30 | 121.42 | 100.07
2019-01-07 22:00 | 123.8 | 102.39
2019-01-07 22:30 | 115.17 | 94.44
2019-01-07 23:00 | 118.72 | 97.4
2019-01-07 23:30 | 112.79 | 93.34
2019-01-08 | 119.86 | 99.58
2019-01-08 00:30 | 115.19 | 95.02
2019-01-08 01:00 | 117.91 | 98.67
2019-01-08 01:30 | 113.41 | 93.89
2019-01-08 02:00 | 115.4 | 95.86
2019-01-08 02:30 | 110.01 | 90.62
2019-01-08 03:00 | 112.68 | 92.9
2019-01-08 03:30 | 119.17 | 100.73
2019-01-08 04:00 | 110.98 | 92.78
2019-01-08 04:30 | 111.93 | 94.37
2019-01-08 05:00 | 104.03 | 86.28
2019-01-08 05:30 | 110.88 | 92.28
2019-01-08 06:00 | 103.42 | 83.92
2019-01-08 06:30 | 101.19 | 81.78
2019-01-08 07:00 | 99.74 | 79.94
2019-01-08 07:30 | 103.27 | 82.43
2019-01-08 08:00 | 99.72 | 75.57
2019-01-08 08:30 | 104.85 | 84.69
2019-01-08 09:00 | 99.2 | 76.88
2019-01-08 09:30 | 97.96 | 73.16
2019-01-08 10:00 | 104.6 | 74.35
2019-01-08 10:30 | 99.1 | 72.97
2019-01-08 11:00 | 92.99 | 65.82
2019-01-08 11:30 | 92.35 | 62.16
2019-01-08 12:00 | 89.61 | 60.51
2019-01-08 12:30 | 92.18 | 69.06
2019-01-08 13:00 | 86.2 | 59.75
2019-01-08 13:30 | 82.73 | 56.36
2019-01-08 14:00 | 91.51 | 68.69
2019-01-08 14:30 | 93.06 | 72.66
2019-01-08 15:00 | 92.27 | 72.01
2019-01-08 15:30 | 92.52 | 71.64
2019-01-08 16:00 | 103.83 | 87.49
2019-01-08 16:30 | 103.56 | 87.02
2019-01-08 17:00 | 110.1 | 93.13
2019-01-08 17:30 | 108.01 | 91.96
2019-01-08 18:00 | 111.74 | 95.27
2019-01-08 18:30 | 112.6 | 96.31
2019-01-08 19:00 | 108.08 | 91.68
2019-01-08 19:30 | 112.82 | 96.35
2019-01-08 20:00 | 118.11 | 103.21
2019-01-08 20:30 | 114.86 | 98.96
2019-01-08 21:00 | 98.36 | 82.64
2019-01-08 21:30 | 102.11 | 87.52
2019-01-08 22:00 | 107.36 | 91.68
2019-01-08 22:30 | 103.4 | 87.91
2019-01-08 23:00 | 105.54 | 89.7
2019-01-08 23:30 | 104.66 | 89.57
2019-01-09 | 106.52 | 92.25
2019-01-09 00:30 | 103.32 | 88.68
2019-01-09 01:00 | 97.03 | 81.27
2019-01-09 01:30 | 98.45 | 82.96
2019-01-09 02:00 | 100.65 | 85.53
2019-01-09 02:30 | 102.06 | 86.72
2019-01-09 03:00 | 95.66 | 83.79
2019-01-09 03:30 | 93.12 | 77.93
2019-01-09 04:00 | 87.34 | 66.6
2019-01-09 04:30 | 90.82 | 70.73
2019-01-09 05:00 | 97.08 | 80.06
2019-01-09 05:30 | 97.5 | 80.85
2019-01-09 06:00 | 101.76 | 85.21
2019-01-09 06:30 | 95.89 | 78.43
2019-01-09 07:00 | 93.67 | 75.19
2019-01-09 07:30 | 88.84 | 71.44
2019-01-09 08:00 | 88.97 | 70.43
2019-01-09 08:30 | 92.69 | 74.51
2019-01-09 09:00 | 94.71 | 78.45
2019-01-09 09:30 | 100.46 | 85.98
2019-01-09 10:00 | 109.07 | 95.09
2019-01-09 10:30 | 102.89 | 87.59
2019-01-09 11:00 | 97.35 | 82.31
2019-01-09 11:30 | 99.39 | 84.76
2019-01-09 12:00 | 96.72 | 81.78
2019-01-09 12:30 | 95.84 | 80.77
2019-01-09 13:00 | 94.65 | 79.3
2019-01-09 13:30 | 95.67 | 80.31
2019-01-09 14:00 | 102.6 | 89.04
2019-01-09 14:30 | 101.47 | 87.68
2019-01-09 15:00 | 105.09 | 91.08
2019-01-09 15:30 | 110.23 | 96.08
2019-01-09 16:00 | 110.86 | 97.66
2019-01-09 16:30 | 102.48 | 89.53
2019-01-09 17:00 | 109.26 | 95.56
2019-01-09 17:30 | 100.07 | 85.1
2019-01-09 18:00 | 97.55 | 82.83
2019-01-09 18:30 | 101.12 | 85.5
2019-01-09 19:00 | 99.92 | 83.29
2019-01-09 19:30 | 100.24 | 84.83
2019-01-09 20:00 | 104.92 | 88.52
2019-01-09 20:30 | 110.52 | 94.2
2019-01-09 21:00 | 111.78 | 95.5
2019-01-09 21:30 | 111.37 | 96.39
2019-01-09 22:00 | 112.36 | 96.32
2019-01-09 22:30 | 109.25 | 93.49
2019-01-09 23:00 | 114.22 | 96.39
2019-01-09 23:30 | 114.76 | 97.83
2019-01-10 | 119.89 | 104.17
2019-01-10 00:30 | 120.43 | 105.64
2019-01-10 01:00 | 127.71 | 113.29
2019-01-10 01:30 | 123.97 | 109.6
2019-01-10 02:00 | 123.76 | 108.27
2019-01-10 02:30 | 116.36 | 100.73
2019-01-10 03:00 | 119.53 | 103.82
2019-01-10 03:30 | 124.31 | 109.06
2019-01-10 04:00 | 124.95 | 110.14
2019-01-10 04:30 | 126.27 | 111.04
2019-01-10 05:00 | 126.47 | 111.33
2019-01-10 05:30 | 118.8 | 103.34
2019-01-10 06:00 | 120.26 | 104.8
2019-01-10 06:30 | 109.11 | 93.85
2019-01-10 07:00 | 107.98 | 88.32
2019-01-10 07:30 | 100.88 | 81.11
2019-01-10 08:00 | 102.08 | 77.96
2019-01-10 08:30 | 105.58 | 79.52
2019-01-10 09:00 | 106.76 | 80.94
2019-01-10 09:30 | 101.95 | 77.89
2019-01-10 10:00 | 102.22 | 76.88
2019-01-10 10:30 | 107.53 | 81.31
2019-01-10 11:00 | 103.26 | 77.57
2019-01-10 11:30 | 100.31 | 76.64
2019-01-10 12:00 | 103.13 | 76.76
2019-01-10 12:30 | 104.28 | 77.46
2019-01-10 13:00 | 104.19 | 76.53
2019-01-10 13:30 | 101.81 | 67.61
2019-01-10 14:00 | 105.24 | 80.84
2019-01-10 14:30 | 104.91 | 81.31
2019-01-10 15:00 | 99.13 | 79.26
2019-01-10 15:30 | 104.98 | 87.74
2019-01-10 16:00 | 99.03 | 81.95
2019-01-10 16:30 | 94.65 | 77.11
2019-01-10 17:00 | 96.29 | 78.07
2019-01-10 17:30 | 97.87 | 80.05
2019-01-10 18:00 | 104.93 | 88.49
2019-01-10 18:30 | 101.7 | 85.98
2019-01-10 19:00 | 113.77 | 99.45
2019-01-10 19:30 | 120.23 | 105.41
2019-01-10 20:00 | 119.24 | 102.49
2019-01-10 20:30 | 120.79 | 103.57
2019-01-10 21:00 | 124.7 | 107.96
2019-01-10 21:30 | 122.09 | 104.7
2019-01-10 22:00 | 125.08 | 107.74
2019-01-10 22:30 | 120.43 | 102.77
2019-01-10 23:00 | 125.36 | 109.66
2019-01-10 23:30 | 122.71 | 106.99
2019-01-11 | 122.11 | 106.18
2019-01-11 00:30 | 122.36 | 105.11
2019-01-11 01:00 | 117.93 | 100.46
2019-01-11 01:30 | 124.1 | 106.32
2019-01-11 02:00 | 121.81 | 104.71
2019-01-11 02:30 | 115.11 | 97.95
2019-01-11 03:00 | 116.9 | 100.6
2019-01-11 03:30 | 123.86 | 107.35
2019-01-11 04:00 | 124.63 | 109.44
2019-01-11 04:30 | 127.15 | 111.09
2019-01-11 05:00 | 123 | 105.4
2019-01-11 05:30 | 125.71 | 107.05
2019-01-11 06:00 | 123.89 | 106.99
2019-01-11 06:30 | 119.46 | 102.28
2019-01-11 07:00 | 111.34 | 92.54
2019-01-11 07:30 | 110.55 | 88.13
2019-01-11 08:00 | 118.08 | 96.16
2019-01-11 08:30 | 114.2 | 91.29
2019-01-11 09:00 | 109.92 | 87.36
2019-01-11 09:30 | 105.53 | 83.7
2019-01-11 10:00 | 114.39 | 92.41
2019-01-11 10:30 | 108.86 | 85.28
2019-01-11 11:00 | 109.05 | 80.73
2019-01-11 11:30 | 107.53 | 74.68
2019-01-11 12:00 | 110.2 | 82.18
2019-01-11 12:30 | 110.15 | 86.55
2019-01-11 13:00 | 108.6 | 78.58
2019-01-11 13:30 | 111.1 | 89.1
2019-01-11 14:00 | 108.85 | 88.29
2019-01-11 14:30 | 117.19 | 98.33
2019-01-11 15:00 | 113.69 | 95.62
2019-01-11 15:30 | 111.82 | 91.79
2019-01-11 16:00 | 115.51 | 96.45
2019-01-11 16:30 | 116.4 | 97.18
2019-01-11 17:00 | 120.81 | 100.86
2019-01-11 17:30 | 124.03 | 104.44
2019-01-11 18:00 | 126.64 | 109.69
2019-01-11 18:30 | 114.81 | 98.09
2019-01-11 19:00 | 124.31 | 108.2
2019-01-11 19:30 | 122.09 | 105.74
2019-01-11 20:00 | 122.81 | 105.74
2019-01-11 20:30 | 125.71 | 108.55
2019-01-11 21:00 | 127.35 | 110.5
2019-01-11 21:30 | 123.61 | 107.94
2019-01-11 22:00 | 125.69 | 110.62
2019-01-11 22:30 | 130.4 | 114.02
2019-01-11 23:00 | 123.43 | 106.07
2019-01-11 23:30 | 118.51 | 100.66
2019-01-12 | 121.46 | 104
2019-01-12 00:30 | 124.41 | 107.4
2019-01-12 01:00 | 117.52 | 100.79
2019-01-12 01:30 | 121.81 | 105.92
2019-01-12 02:00 | 125.3 | 108.89
2019-01-12 02:30 | 116.44 | 97.71
2019-01-12 03:00 | 125.65 | 109.73
2019-01-12 03:30 | 119.26 | 102.3
2019-01-12 04:00 | 127.1 | 111.32
2019-01-12 04:30 | 122.9 | 106.28
2019-01-12 05:00 | 120.07 | 102.53
2019-01-12 05:30 | 119.2 | 101.51
2019-01-12 06:00 | 114.93 | 96.77
2019-01-12 06:30 | 114.52 | 93.66
2019-01-12 07:00 | 115.31 | 91.97
2019-01-12 07:30 | 107.41 | 80.17
2019-01-12 08:00 | 114.04 | 84.76
2019-01-12 08:30 | 114.63 | 86.58
2019-01-12 09:00 | 115.36 | 80.23
2019-01-12 09:30 | 122.15 | 90.59
2019-01-12 10:00 | 119.97 | 90.02
2019-01-12 10:30 | 122.45 | 90.62
2019-01-12 11:00 | 119.05 | 84.32
2019-01-12 11:30 | 121.59 | 86.19
2019-01-12 12:00 | 117.19 | 81.77
2019-01-12 12:30 | 116.09 | 79.35
2019-01-12 13:00 | 114.23 | 77.07
2019-01-12 13:30 | 119.57 | 83.48
2019-01-12 14:00 | 118.72 | 83.28
2019-01-12 14:30 | 117.22 | 81.39
2019-01-12 15:00 | 120.82 | 85.72
2019-01-12 15:30 | 125.06 | 90.25
2019-01-12 16:00 | 128.41 | 95.49
2019-01-12 16:30 | 120.53 | 88.76
2019-01-12 17:00 | 123.79 | 92.48
2019-01-12 17:30 | 129.34 | 101.9
2019-01-12 18:00 | 131.03 | 109.72
2019-01-12 18:30 | 123.86 | 104.19
2019-01-12 19:00 | 126.25 | 108.91
2019-01-12 19:30 | 122.22 | 104.57
2019-01-12 20:00 | 128.28 | 109.9
2019-01-12 20:30 | 130.7 | 113.94
2019-01-12 21:00 | 126.1 | 108.9
2019-01-12 21:30 | 117.22 | 100.32
2019-01-12 22:00 | 115.54 | 98.52
2019-01-12 22:30 | 120.65 | 103.52
2019-01-12 23:00 | 114.05 | 96.19
2019-01-12 23:30 | 113.94 | 96.24
2019-01-13 | 124.49 | 107.29
2019-01-13 00:30 | 124.05 | 106.49
2019-01-13 01:00 | 124.27 | 106.91
2019-01-13 01:30 | 126.67 | 108.4
2019-01-13 02:00 | 123.22 | 104.43
2019-01-13 02:30 | 121.01 | 101.75
2019-01-13 03:00 | 122.32 | 104.33
2019-01-13 03:30 | 122.15 | 102.88
2019-01-13 04:00 | 118.79 | 99.78
2019-01-13 04:30 | 120.18 | 100.96
2019-01-13 05:00 | 116.3 | 99.18
2019-01-13 05:30 | 116.28 | 98.94
2019-01-13 06:00 | 116.13 | 98.77
2019-01-13 06:30 | 110.34 | 90.3
2019-01-13 07:00 | 120.87 | 98.04
2019-01-13 07:30 | 115.23 | 87.46
2019-01-13 08:00 | 107.17 | 73.91
2019-01-13 08:30 | 107.15 | 72.26
2019-01-13 09:00 | 109.33 | 76.08
2019-01-13 09:30 | 117.23 | 83.25
2019-01-13 10:00 | 116.36 | 81.64
2019-01-13 10:30 | 112.87 | 77.85
2019-01-13 11:00 | 111.87 | 76.37
2019-01-13 11:30 | 106.95 | 71.7
2019-01-13 12:00 | 116.6 | 84.47
2019-01-13 12:30 | 119.41 | 87.02
2019-01-13 13:00 | 114.19 | 81.58
2019-01-13 13:30 | 110.16 | 77.93
2019-01-13 14:00 | 110.96 | 79.68
2019-01-13 14:30 | 116.9 | 86.68
2019-01-13 15:00 | 117.22 | 88.23
2019-01-13 15:30 | 126.51 | 94.34
2019-01-13 16:00 | 120.38 | 90.01
2019-01-13 16:30 | 116.67 | 84.93
2019-01-13 17:00 | 119.7 | 90.6
2019-01-13 17:30 | 126.65 | 101.14
2019-01-13 18:00 | 125.1 | 103.94
2019-01-13 18:30 | 129 | 110.99
2019-01-13 19:00 | 135.61 | 119.43
2019-01-13 19:30 | 131.83 | 114.96
2019-01-13 20:00 | 127.84 | 110.93
2019-01-13 20:30 | 124.9 | 107.27
2019-01-13 21:00 | 125.3 | 107.7
2019-01-13 21:30 | 129.26 | 112.33
2019-01-13 22:00 | 124.25 | 107.59
2019-01-13 22:30 | 127.89 | 110.92
2019-01-13 23:00 | 123.83 | 106.72
2019-01-13 23:30 | 132.09 | 115.29
2019-01-14 | 121.7 | 104.68
2019-01-14 00:30 | 122.96 | 105.95
2019-01-14 01:00 | 127.3 | 110.15
2019-01-14 01:30 | 121.78 | 104.68
2019-01-14 02:00 | 120.59 | 104.64
2019-01-14 02:30 | 115.79 | 100.08
2019-01-14 03:00 | 115.28 | 99.69
2019-01-14 03:30 | 108.45 | 92.3
2019-01-14 04:00 | 110.55 | 94.38
2019-01-14 04:30 | 106.87 | 90.43
2019-01-14 05:00 | 106.24 | 89.93
2019-01-14 05:30 | 103.76 | 87.12
2019-01-14 06:00 | 104.68 | 89.04
2019-01-14 06:30 | 98.76 | 79.4
2019-01-14 07:00 | 104.53 | 82.92
2019-01-14 07:30 | 102.11 | 75.4
2019-01-14 08:00 | 103.72 | 78.55
2019-01-14 08:30 | 93.75 | 68.52
2019-01-14 09:00 | 95.14 | 64.38
2019-01-14 09:30 | 106.36 | 80.66
2019-01-14 10:00 | 105.23 | 76.41
2019-01-14 10:30 | 104.76 | 72.64
2019-01-14 11:00 | 95.58 | 60.38
2019-01-14 11:30 | 113.69 | 80.37
2019-01-14 12:00 | 116.63 | 82.09
2019-01-14 12:30 | 116.47 | 81.02
2019-01-14 13:00 | 115.58 | 81.61
2019-01-14 13:30 | 116.68 | 81.62
2019-01-14 14:00 | 120.55 | 86.68
2019-01-14 14:30 | 125.29 | 92.34
2019-01-14 15:00 | 122.62 | 88.72
2019-01-14 15:30 | 116.25 | 80.17
2019-01-14 16:00 | 123.14 | 90.06
2019-01-14 16:30 | 114.09 | 81.68
2019-01-14 17:00 | 112.23 | 81.42
2019-01-14 17:30 | 122 | 95.62
2019-01-14 18:00 | 115.51 | 93.31
2019-01-14 18:30 | 109.15 | 91.43
2019-01-14 19:00 | 114.95 | 101.66
2019-01-14 19:30 | 126.85 | 112.17
2019-01-14 20:00 | 139.56 | 123.35
2019-01-14 20:30 | 124.32 | 107.98
2019-01-14 21:00 | 129.88 | 113.85
2019-01-14 21:30 | 129.19 | 112.87
2019-01-14 22:00 | 127.48 | 110.47
2019-01-14 22:30 | 129.48 | 113.09
2019-01-14 23:00 | 119.54 | 102.61
2019-01-14 23:30 | 128.97 | 111.26
2019-01-15 | 127.97 | 109.7
2019-01-15 00:30 | 124.1 | 106.28
2019-01-15 01:00 | 122.24 | 105.6
2019-01-15 01:30 | 117.45 | 100.3
2019-01-15 02:00 | 117.13 | 100.54
2019-01-15 02:30 | 120.64 | 104.34
2019-01-15 03:00 | 113.48 | 97.09
2019-01-15 03:30 | 110.12 | 93
2019-01-15 04:00 | 113.6 | 96.97
2019-01-15 04:30 | 114.78 | 97.72
2019-01-15 05:00 | 114.5 | 98.05
2019-01-15 05:30 | 113.98 | 97.22
2019-01-15 06:00 | 116.31 | 99.16
2019-01-15 06:30 | 113.65 | 94.66
2019-01-15 07:00 | 115.05 | 97.86
2019-01-15 07:30 | 110 | 88.37
2019-01-15 08:00 | 102.99 | 76.44
2019-01-15 08:30 | 101.13 | 65.33
2019-01-15 09:00 | 103.95 | 74.06
2019-01-15 09:30 | 110.47 | 82.66
2019-01-15 10:00 | 108.42 | 80.76
2019-01-15 10:30 | 105.01 | 73.52
2019-01-15 11:00 | 100.78 | 63.77
2019-01-15 11:30 | 102.89 | 67.99
2019-01-15 12:00 | 105.68 | 69.97
2019-01-15 12:30 | 112.56 | 78.32
2019-01-15 13:00 | 108.92 | 75.16
2019-01-15 13:30 | 110.5 | 77.32
2019-01-15 14:00 | 107.72 | 74.19
2019-01-15 14:30 | 117.69 | 82.9
2019-01-15 15:00 | 110.33 | 74.57
2019-01-15 15:30 | 106.47 | 71.36
2019-01-15 16:00 | 105.39 | 71.91
2019-01-15 16:30 | 105.74 | 73.87
2019-01-15 17:00 | 108.69 | 77.57
2019-01-15 17:30 | 110.55 | 84.08
2019-01-15 18:00 | 100.79 | 78.8
2019-01-15 18:30 | 108.62 | 89.79
2019-01-15 19:00 | 112.73 | 95.67
2019-01-15 19:30 | 124.56 | 107.91
2019-01-15 20:00 | 130.7 | 113.68
2019-01-15 20:30 | 125.44 | 108.79
2019-01-15 21:00 | 130.02 | 112.78
2019-01-15 21:30 | 118.5 | 101.04
2019-01-15 22:00 | 116.67 | 98.39
2019-01-15 22:30 | 124.34 | 105.6
2019-01-15 23:00 | 132.47 | 114.78
2019-01-15 23:30 | 129.56 | 113.01
2019-01-16 | 125.68 | 108.54
2019-01-16 00:30 | 132.58 | 115.37
2019-01-16 01:00 | 121.71 | 104.07
2019-01-16 01:30 | 115.25 | 97.75
2019-01-16 02:00 | 120.59 | 103.69
2019-01-16 02:30 | 118.37 | 101.68
2019-01-16 03:00 | 115.45 | 98.37
2019-01-16 03:30 | 118.13 | 102.27
2019-01-16 04:00 | 119.29 | 103.54
2019-01-16 04:30 | 115.55 | 99.98
2019-01-16 05:00 | 117.4 | 102.53
2019-01-16 05:30 | 112.55 | 97.87
2019-01-16 06:00 | 112.68 | 97.6
2019-01-16 06:30 | 97.98 | 78.55
2019-01-16 07:00 | 100.69 | 78.61
2019-01-16 07:30 | 99.69 | 74.76
2019-01-16 08:00 | 94.46 | 70.07
2019-01-16 08:30 | 96.42 | 71.33
2019-01-16 09:00 | 98.42 | 73.37
2019-01-16 09:30 | 102.52 | 76.72
2019-01-16 10:00 | 97.38 | 69.77
2019-01-16 10:30 | 98.16 | 69.98
2019-01-16 11:00 | 101.37 | 74.49
2019-01-16 11:30 | 101.24 | 74.53
2019-01-16 12:00 | 103.9 | 76.69
2019-01-16 12:30 | 108.79 | 83.33
2019-01-16 13:00 | 103.67 | 74.34
2019-01-16 13:30 | 109.77 | 81.22
2019-01-16 14:00 | 109.7 | 83.01
2019-01-16 14:30 | 110.16 | 82.92
2019-01-16 15:00 | 110.67 | 84.39
2019-01-16 15:30 | 107.26 | 81.36
2019-01-16 16:00 | 103.21 | 76.45
2019-01-16 16:30 | 103 | 75.98
2019-01-16 17:00 | 106.73 | 82.1
2019-01-16 17:30 | 113.52 | 95.05
2019-01-16 18:00 | 108.05 | 92.56
2019-01-16 18:30 | 106.41 | 94.54
2019-01-16 19:00 | 117.93 | 107.73
2019-01-16 19:30 | 114.53 | 104.12
2019-01-16 20:00 | 114.93 | 104.01
2019-01-16 20:30 | 119.46 | 107.97
2019-01-16 21:00 | 111.93 | 99.56
2019-01-16 21:30 | 105.95 | 93.67
2019-01-16 22:00 | 99.69 | 86.82
2019-01-16 22:30 | 107.21 | 94.45
2019-01-16 23:00 | 100.6 | 86.3
2019-01-16 23:30 | 105.38 | 91.74
2019-01-17 | 103.73 | 90.63
2019-01-17 00:30 | 102.72 | 89.67
2019-01-17 01:00 | 102.5 | 89.21
2019-01-17 01:30 | 104.22 | 90.05
2019-01-17 02:00 | 106.02 | 92.98
2019-01-17 02:30 | 103.85 | 89.74
2019-01-17 03:00 | 104.45 | 90.81
2019-01-17 03:30 | 107.15 | 93.48
2019-01-17 04:00 | 106.32 | 93.61
2019-01-17 04:30 | 111.93 | 98.65
2019-01-17 05:00 | 110.07 | 96.19
2019-01-17 05:30 | 109.08 | 95.98
2019-01-17 06:00 | 105.06 | 90.3
2019-01-17 06:30 | 96.91 | 80
2019-01-17 07:00 | 98.34 | 79.54
2019-01-17 07:30 | 95.9 | 72.71
2019-01-17 08:00 | 92.68 | 70.13
2019-01-17 08:30 | 87.77 | 63.91
2019-01-17 09:00 | 89.4 | 64.48
2019-01-17 09:30 | 97.71 | 74.8
2019-01-17 10:00 | 107.86 | 85.54
2019-01-17 10:30 | 100.37 | 76.04
2019-01-17 11:00 | 106.12 | 75.69
2019-01-17 11:30 | 102.76 | 71.94
2019-01-17 12:00 | 98.68 | 69.22
2019-01-17 12:30 | 103.94 | 72.51
2019-01-17 13:00 | 98.46 | 67.26
2019-01-17 13:30 | 98.68 | 68.66
2019-01-17 14:00 | 102.54 | 74.66
2019-01-17 14:30 | 99.65 | 69.66
2019-01-17 15:00 | 101.06 | 73.31
2019-01-17 15:30 | 106.25 | 76.67
2019-01-17 16:00 | 106.83 | 75.54
2019-01-17 16:30 | 108.59 | 78.98
2019-01-17 17:00 | 104.55 | 77.26
2019-01-17 17:30 | 103.38 | 80.86
2019-01-17 18:00 | 102.41 | 84.23
2019-01-17 18:30 | 105.85 | 91.48
2019-01-17 19:00 | 118.15 | 106.21
2019-01-17 19:30 | 117.1 | 105.6
2019-01-17 20:00 | 119.76 | 108.68
2019-01-17 20:30 | 112.76 | 100.77
2019-01-17 21:00 | 112.82 | 99.7
2019-01-17 21:30 | 113.12 | 99.77
2019-01-17 22:00 | 112.23 | 98.34
2019-01-17 22:30 | 117.78 | 103
2019-01-17 23:00 | 123.8 | 107.23
2019-01-17 23:30 | 122.31 | 104.49
2019-01-18 | 125 | 107.45
2019-01-18 00:30 | 122.42 | 104.2
2019-01-18 01:00 | 114.86 | 94.94
2019-01-18 01:30 | 116.32 | 97.06
2019-01-18 02:00 | 118.85 | 100.05
2019-01-18 02:30 | 119.87 | 101.38
2019-01-18 03:00 | 110.67 | 94.25
2019-01-18 03:30 | 112.7 | 96.91
2019-01-18 04:00 | 112.01 | 96.18
2019-01-18 04:30 | 114.97 | 99.21
2019-01-18 05:00 | 114.09 | 98.76
2019-01-18 05:30 | 108.41 | 92.17
2019-01-18 06:00 | 109.72 | 93.85
2019-01-18 06:30 | 100.97 | 82.95
2019-01-18 07:00 | 103.47 | 81.78
2019-01-18 07:30 | 108.99 | 86.49
2019-01-18 08:00 | 108.83 | 82.08
2019-01-18 08:30 | 115.24 | 91.95
2019-01-18 09:00 | 118.59 | 93.97
2019-01-18 09:30 | 114.8 | 92.02
2019-01-18 10:00 | 106.4 | 84
2019-01-18 10:30 | 107.45 | 83.98
2019-01-18 11:00 | 112.26 | 89.2
2019-01-18 11:30 | 107.3 | 77.88
2019-01-18 12:00 | 108.59 | 83.72
2019-01-18 12:30 | 109.1 | 80.31
2019-01-18 13:00 | 116.12 | 87
2019-01-18 13:30 | 120.96 | 96.98
2019-01-18 14:00 | 119.83 | 95.77
2019-01-18 14:30 | 123.83 | 100
2019-01-18 15:00 | 120.54 | 88.03
2019-01-18 15:30 | 121.92 | 91.88
2019-01-18 16:00 | 122.01 | 96
2019-01-18 16:30 | 121.46 | 93.29
2019-01-18 17:00 | 126.04 | 100.79
2019-01-18 17:30 | 121.33 | 96.2
2019-01-18 18:00 | 125.64 | 100.97
2019-01-18 18:30 | 119.63 | 95.73
2019-01-18 19:00 | 127.93 | 107.07
2019-01-18 19:30 | 138.72 | 118.39
2019-01-18 20:00 | 137.98 | 117.8
2019-01-18 20:30 | 132.41 | 111.26
2019-01-18 21:00 | 126.92 | 105.3
2019-01-18 21:30 | 131.43 | 110.64
2019-01-18 22:00 | 133.99 | 114.34
2019-01-18 22:30 | 134.56 | 114.73
2019-01-18 23:00 | 128.19 | 107.41
2019-01-18 23:30 | 126.1 | 105.91
2019-01-19 | 119.65 | 98.24
2019-01-19 00:30 | 122.6 | 102.9
2019-01-19 01:00 | 113.72 | 94.73
2019-01-19 01:30 | 113.4 | 95.33
2019-01-19 02:00 | 110.23 | 92.11
2019-01-19 02:30 | 117.73 | 101.21
2019-01-19 03:00 | 113.16 | 95.86
2019-01-19 03:30 | 115.54 | 98.42
2019-01-19 04:00 | 113.01 | 95.23
2019-01-19 04:30 | 115.44 | 97.29
2019-01-19 05:00 | 106.92 | 89.16
2019-01-19 05:30 | 110.21 | 93.51
2019-01-19 06:00 | 107.96 | 90.74
2019-01-19 06:30 | 103.4 | 83.53
2019-01-19 07:00 | 107.43 | 84.43
2019-01-19 07:30 | 113.38 | 85.9
2019-01-19 08:00 | 109.82 | 78.43
2019-01-19 08:30 | 108.78 | 75.72
2019-01-19 09:00 | 103.73 | 71.79
2019-01-19 09:30 | 110.89 | 83.71
2019-01-19 10:00 | 103.96 | 77.17
2019-01-19 10:30 | 109.3 | 81.46
2019-01-19 11:00 | 107.36 | 79.23
2019-01-19 11:30 | 106.75 | 79.68
2019-01-19 12:00 | 111.79 | 85.01
2019-01-19 12:30 | 108.38 | 78.08
2019-01-19 13:00 | 106.63 | 74.18
2019-01-19 13:30 | 107.72 | 73.62
2019-01-19 14:00 | 112.18 | 80.71
2019-01-19 14:30 | 112.28 | 79.28
2019-01-19 15:00 | 108.72 | 77.35
2019-01-19 15:30 | 112.55 | 79.21
2019-01-19 16:00 | 105.93 | 72.26
2019-01-19 16:30 | 112.83 | 82.68
2019-01-19 17:00 | 120.84 | 89.6
2019-01-19 17:30 | 127.52 | 98.75
2019-01-19 18:00 | 116.74 | 92.46
2019-01-19 18:30 | 121.86 | 100.6
2019-01-19 19:00 | 137.2 | 116.92
2019-01-19 19:30 | 131.38 | 111.32
2019-01-19 20:00 | 130.44 | 110.62
2019-01-19 20:30 | 132.16 | 113.11
2019-01-19 21:00 | 127.75 | 107.85
2019-01-19 21:30 | 122.24 | 101.57
2019-01-19 22:00 | 119.86 | 99.01
2019-01-19 22:30 | 123.79 | 104.01
2019-01-19 23:00 | 118.2 | 96.87
2019-01-19 23:30 | 119.58 | 97.99
2019-01-20 | 122.25 | 100.55
2019-01-20 00:30 | 116.33 | 94.51
2019-01-20 01:00 | 118.28 | 97.36
2019-01-20 01:30 | 127.5 | 107.26
2019-01-20 02:00 | 130.67 | 110.82
2019-01-20 02:30 | 125.54 | 104.19
2019-01-20 03:00 | 130.74 | 108.59
2019-01-20 03:30 | 119.2 | 96.6
2019-01-20 04:00 | 125.08 | 103.23
2019-01-20 04:30 | 124.45 | 103.18
2019-01-20 05:00 | 122 | 100.92
2019-01-20 05:30 | 123.1 | 102.61
2019-01-20 06:00 | 128.21 | 108.56
2019-01-20 06:30 | 121.45 | 100.97
2019-01-20 07:00 | 126.65 | 99.46
2019-01-20 07:30 | 120.87 | 87.11
2019-01-20 08:00 | 120.43 | 85.45
2019-01-20 08:30 | 115.14 | 71.67
2019-01-20 09:00 | 111.52 | 67.58
2019-01-20 09:30 | 112.08 | 68.31
2019-01-20 10:00 | 114.91 | 71.2
2019-01-20 10:30 | 113.05 | 71.14
2019-01-20 11:00 | 122.12 | 82.57
2019-01-20 11:30 | 119.36 | 78.66
2019-01-20 12:00 | 119.18 | 79.74
2019-01-20 12:30 | 121.24 | 84.36
2019-01-20 13:00 | 113.47 | 75.6
2019-01-20 13:30 | 119.67 | 82.11
2019-01-20 14:00 | 117 | 79.47
2019-01-20 14:30 | 119.99 | 82.85
2019-01-20 15:00 | 123.61 | 86.34
2019-01-20 15:30 | 120.01 | 82.37
2019-01-20 16:00 | 124.6 | 91.55
2019-01-20 16:30 | 121.23 | 88.87
2019-01-20 17:00 | 126.16 | 95.17
2019-01-20 17:30 | 130.67 | 102.93
2019-01-20 18:00 | 117.54 | 92.03
2019-01-20 18:30 | 117.14 | 94.94
2019-01-20 19:00 | 127.57 | 107.42
2019-01-20 19:30 | 134.88 | 115.05
2019-01-20 20:00 | 129.25 | 108.83
2019-01-20 20:30 | 134.07 | 114.32
2019-01-20 21:00 | 136.8 | 117.06
2019-01-20 21:30 | 138.22 | 118.81
2019-01-20 22:00 | 133.52 | 114.54
2019-01-20 22:30 | 122.27 | 102.92
2019-01-20 23:00 | 133.14 | 113.52
2019-01-20 23:30 | 124.56 | 104.43
2019-01-21 | 136.32 | 116.74
2019-01-21 00:30 | 126.45 | 105.74
2019-01-21 01:00 | 121.25 | 101
2019-01-21 01:30 | 120.66 | 100.29
2019-01-21 02:00 | 128.14 | 109.23
2019-01-21 02:30 | 126.03 | 105.94
2019-01-21 03:00 | 122.5 | 102.65
2019-01-21 03:30 | 126.58 | 105.94
2019-01-21 04:00 | 123.06 | 101.83
2019-01-21 04:30 | 124.93 | 103.84
2019-01-21 05:00 | 125.37 | 105.02
2019-01-21 05:30 | 129.1 | 109.3
2019-01-21 06:00 | 124.5 | 104.19
2019-01-21 06:30 | 117.3 | 93.88
2019-01-21 07:00 | 120.29 | 94.34
2019-01-21 07:30 | 120.37 | 92.22
2019-01-21 08:00 | 117.73 | 80.91
2019-01-21 08:30 | 113.46 | 85.2
2019-01-21 09:00 | 109.26 | 77.53
2019-01-21 09:30 | 111.22 | 78.97
2019-01-21 10:00 | 102.73 | 69.38
2019-01-21 10:30 | 115.55 | 79.56
2019-01-21 11:00 | 118.86 | 84.67
2019-01-21 11:30 | 121.71 | 87.29
2019-01-21 12:00 | 123.84 | 89.6
2019-01-21 12:30 | 120.44 | 84.19
2019-01-21 13:00 | 123.42 | 87.37
2019-01-21 13:30 | 119.66 | 82.65
2019-01-21 14:00 | 122.13 | 85.13
2019-01-21 14:30 | 121.77 | 82.75
2019-01-21 15:00 | 118.49 | 79.51
2019-01-21 15:30 | 119.52 | 80.68
2019-01-21 16:00 | 122.8 | 82.61
2019-01-21 16:30 | 118.88 | 79.98
2019-01-21 17:00 | 119.46 | 83.22
2019-01-21 17:30 | 122.16 | 90.32
2019-01-21 18:00 | 121.95 | 96.31
2019-01-21 18:30 | 125.81 | 104.33
2019-01-21 19:00 | 129.47 | 110.37
2019-01-21 19:30 | 136.63 | 116.84
2019-01-21 20:00 | 133.27 | 113.08
2019-01-21 20:30 | 131.65 | 111.96
2019-01-21 21:00 | 133.1 | 113.5
2019-01-21 21:30 | 136.09 | 116.76
2019-01-21 22:00 | 129.73 | 111.6
2019-01-21 22:30 | 136.68 | 118.38
2019-01-21 23:00 | 134.72 | 115.63
2019-01-21 23:30 | 124.67 | 104.78
2019-01-22 | 123.54 | 105.31
2019-01-22 00:30 | 125.28 | 106.23
2019-01-22 01:00 | 120.5 | 100.98
2019-01-22 01:30 | 120.53 | 101.81
2019-01-22 02:00 | 120.17 | 101.42
2019-01-22 02:30 | 115.67 | 97.33
2019-01-22 03:00 | 120.46 | 102
2019-01-22 03:30 | 116.65 | 98.1
2019-01-22 04:00 | 117.69 | 99.17
2019-01-22 04:30 | 127.39 | 109.42
2019-01-22 05:00 | 122.44 | 103.19
2019-01-22 05:30 | 119.08 | 99.37
2019-01-22 06:00 | 115.03 | 94.49
2019-01-22 06:30 | 113.34 | 90.46
2019-01-22 07:00 | 112.42 | 86.94
2019-01-22 07:30 | 110.09 | 80.15
2019-01-22 08:00 | 102.34 | 69.84
2019-01-22 08:30 | 110.66 | 77.83
2019-01-22 09:00 | 107.59 | 72.86
2019-01-22 09:30 | 109.32 | 73.69
2019-01-22 10:00 | 109.67 | 72.32
2019-01-22 10:30 | 111.18 | 77.09
2019-01-22 11:00 | 109.1 | 76.08
2019-01-22 11:30 | 112.42 | 77.14
2019-01-22 12:00 | 110.64 | 76.81
2019-01-22 12:30 | 108.38 | 75.82
2019-01-22 13:00 | 111.66 | 78.52
2019-01-22 13:30 | 116.26 | 83.76
2019-01-22 14:00 | 116.12 | 82.41
2019-01-22 14:30 | 119.49 | 85.78
2019-01-22 15:00 | 119.4 | 87.22
2019-01-22 15:30 | 121.99 | 87.04
2019-01-22 16:00 | 125.2 | 93.45
2019-01-22 16:30 | 127.72 | 104.27
2019-01-22 17:00 | 122.31 | 92.96
2019-01-22 17:30 | 119.94 | 93.54
2019-01-22 18:00 | 122.14 | 101.65
2019-01-22 18:30 | 120.6 | 104.02
2019-01-22 19:00 | 118.38 | 103.72
2019-01-22 19:30 | 123.97 | 109.66
2019-01-22 20:00 | 120.64 | 105.75
2019-01-22 20:30 | 122.67 | 107.1
2019-01-22 21:00 | 121.75 | 106.38
2019-01-22 21:30 | 114.48 | 99.21
2019-01-22 22:00 | 116.23 | 100.42
2019-01-22 22:30 | 115.18 | 98.63
2019-01-22 23:00 | 117.31 | 102.19
2019-01-22 23:30 | 120.57 | 105.02
2019-01-23 | 117.96 | 101.51
2019-01-23 00:30 | 113.74 | 97.41
2019-01-23 01:00 | 124.96 | 108.48
2019-01-23 01:30 | 117.92 | 100.43
2019-01-23 02:00 | 121.59 | 104.83
2019-01-23 02:30 | 119.03 | 101.28
2019-01-23 03:00 | 115.65 | 97.61
2019-01-23 03:30 | 107.64 | 89.68
2019-01-23 04:00 | 112.69 | 97.1
2019-01-23 04:30 | 109.98 | 93.24
2019-01-23 05:00 | 109.47 | 93.63
2019-01-23 05:30 | 106.9 | 91.19
2019-01-23 06:00 | 108.31 | 92.19
2019-01-23 06:30 | 97.89 | 80.62
2019-01-23 07:00 | 96.6 | 76
2019-01-23 07:30 | 98.81 | 75.16
2019-01-23 08:00 | 91.93 | 64.46
2019-01-23 08:30 | 91.07 | 62.21
2019-01-23 09:00 | 98.72 | 72.99
2019-01-23 09:30 | 101.8 | 73.21
2019-01-23 10:00 | 99.43 | 67.52
2019-01-23 10:30 | 105.89 | 72.09
2019-01-23 11:00 | 103.68 | 69.66
2019-01-23 11:30 | 108.39 | 76.05
2019-01-23 12:00 | 108.68 | 78.62
2019-01-23 12:30 | 110.76 | 82.23
2019-01-23 13:00 | 107.46 | 77.87
2019-01-23 13:30 | 101.15 | 68.65
2019-01-23 14:00 | 107.38 | 76.69
2019-01-23 14:30 | 101.82 | 69.66
2019-01-23 15:00 | 97.76 | 66.46
2019-01-23 15:30 | 104.16 | 72.93
2019-01-23 16:00 | 113.42 | 89.6
2019-01-23 16:30 | 107.24 | 82.46
2019-01-23 17:00 | 114.03 | 90.91
2019-01-23 17:30 | 112.06 | 89.56
2019-01-23 18:00 | 120.21 | 101.63
2019-01-23 18:30 | 114.79 | 100.74
2019-01-23 19:00 | 124.66 | 113
2019-01-23 19:30 | 128.55 | 117.16
2019-01-23 20:00 | 114.25 | 103.1
2019-01-23 20:30 | 120.57 | 109.45
2019-01-23 21:00 | 111.22 | 98.53
2019-01-23 21:30 | 114.9 | 102.16
2019-01-23 22:00 | 111.93 | 98.96
2019-01-23 22:30 | 116.95 | 103.09
2019-01-23 23:00 | 113.38 | 99.42
2019-01-23 23:30 | 118.88 | 104.91
2019-01-24 | 122.52 | 109.24
2019-01-24 00:30 | 117.63 | 105.01
2019-01-24 01:00 | 122.17 | 109.07
2019-01-24 01:30 | 122.61 | 109.66
2019-01-24 02:00 | 114.81 | 101
2019-01-24 02:30 | 110.89 | 96.66
2019-01-24 03:00 | 114.26 | 99.98
2019-01-24 03:30 | 110.27 | 95.52
2019-01-24 04:00 | 111.54 | 98.11
2019-01-24 04:30 | 111.14 | 96.24
2019-01-24 05:00 | 112.94 | 99.14
2019-01-24 05:30 | 110.22 | 95.7
2019-01-24 06:00 | 111.01 | 95.9
2019-01-24 06:30 | 100.73 | 82.91
2019-01-24 07:00 | 104.44 | 85.15
2019-01-24 07:30 | 102.18 | 81.77
2019-01-24 08:00 | 96.75 | 74.17
2019-01-24 08:30 | 98.77 | 78.01
2019-01-24 09:00 | 100.1 | 79.09
2019-01-24 09:30 | 108.86 | 88.35
2019-01-24 10:00 | 102.66 | 80.46
2019-01-24 10:30 | 98.7 | 70.35
2019-01-24 11:00 | 99.93 | 72.32
2019-01-24 11:30 | 98.11 | 69.89
2019-01-24 12:00 | 101.68 | 73.33
2019-01-24 12:30 | 104.05 | 76.77
2019-01-24 13:00 | 102.43 | 75.61
2019-01-24 13:30 | 100.16 | 72.49
2019-01-24 14:00 | 105.08 | 80.46
2019-01-24 14:30 | 104.86 | 80.07
2019-01-24 15:00 | 104.57 | 79.55
2019-01-24 15:30 | 110.18 | 85.72
2019-01-24 16:00 | 109.58 | 85.53
2019-01-24 16:30 | 103.55 | 79.7
2019-01-24 17:00 | 101.47 | 77.54
2019-01-24 17:30 | 98.67 | 78.24
2019-01-24 18:00 | 100.8 | 84.61
2019-01-24 18:30 | 104.02 | 91.47
2019-01-24 19:00 | 113.67 | 103
2019-01-24 19:30 | 118.38 | 107.08
2019-01-24 20:00 | 117.81 | 106.07
2019-01-24 20:30 | 114.47 | 103.42
2019-01-24 21:00 | 118.6 | 107.7
2019-01-24 21:30 | 107.87 | 97.12
2019-01-24 22:00 | 101.14 | 88.58
2019-01-24 22:30 | 113.67 | 100.68
2019-01-24 23:00 | 114.54 | 100.95
2019-01-24 23:30 | 117.83 | 105
2019-01-25 | 113.07 | 99.86
2019-01-25 00:30 | 120.86 | 107.99
2019-01-25 01:00 | 116.61 | 102.54
2019-01-25 01:30 | 109.05 | 95.19
2019-01-25 02:00 | 113.89 | 99.99
2019-01-25 02:30 | 108.46 | 94.2
2019-01-25 03:00 | 110.3 | 96.65
2019-01-25 03:30 | 115.73 | 102.59
2019-01-25 04:00 | 112.17 | 98.3
2019-01-25 04:30 | 113.49 | 99.32
2019-01-25 05:00 | 112.61 | 99.02
2019-01-25 05:30 | 115.92 | 102.08
2019-01-25 06:00 | 109.74 | 95.14
2019-01-25 06:30 | 102.89 | 87.78
2019-01-25 07:00 | 103.16 | 84.55
2019-01-25 07:30 | 106.46 | 84.83
2019-01-25 08:00 | 108.18 | 86.1
2019-01-25 08:30 | 110.36 | 85.41
2019-01-25 09:00 | 102.64 | 76.17
2019-01-25 09:30 | 106.14 | 75.97
2019-01-25 10:00 | 108.44 | 78.58
2019-01-25 10:30 | 109.96 | 83.17
2019-01-25 11:00 | 104.55 | 76.58
2019-01-25 11:30 | 101.35 | 72.3
2019-01-25 12:00 | 105.39 | 77.39
2019-01-25 12:30 | 108.96 | 78.94
2019-01-25 13:00 | 120.73 | 93.22
2019-01-25 13:30 | 117.94 | 92.46
2019-01-25 14:00 | 112.19 | 85.12
2019-01-25 14:30 | 116.43 | 90.61
2019-01-25 15:00 | 112.81 | 87.54
2019-01-25 15:30 | 113.74 | 87.25
2019-01-25 16:00 | 109.54 | 80.42
2019-01-25 16:30 | 108.14 | 82.29
2019-01-25 17:00 | 118.38 | 101.49
2019-01-25 17:30 | 118.13 | 101.42
2019-01-25 18:00 | 115.9 | 100.54
2019-01-25 18:30 | 109.84 | 95.43
2019-01-25 19:00 | 121.38 | 108.76
2019-01-25 19:30 | 121.51 | 108.99
2019-01-25 20:00 | 124.9 | 113.31
2019-01-25 20:30 | 125.37 | 113.23
2019-01-25 21:00 | 128.99 | 116.61
2019-01-25 21:30 | 126.86 | 113.88
2019-01-25 22:00 | 131.96 | 119.45
2019-01-25 22:30 | 125.43 | 111.7
2019-01-25 23:00 | 144.91 | 130.78
2019-01-25 23:30 | 122.16 | 108.13
2019-01-26 | 123.41 | 109.63
2019-01-26 00:30 | 122.82 | 108.74
2019-01-26 01:00 | 125.69 | 111.34
2019-01-26 01:30 | 123.38 | 110.33
2019-01-26 02:00 | 125.99 | 112.39
2019-01-26 02:30 | 116.19 | 102.22
2019-01-26 03:00 | 117.8 | 104.15
2019-01-26 03:30 | 128.65 | 115.13
2019-01-26 04:00 | 126.22 | 112.59
2019-01-26 04:30 | 126.39 | 111.89
2019-01-26 05:00 | 120.47 | 105.62
2019-01-26 05:30 | 122.37 | 108.63
2019-01-26 06:00 | 128.3 | 114.93
2019-01-26 06:30 | 119.08 | 104.91
2019-01-26 07:00 | 114.24 | 99.52
2019-01-26 07:30 | 125.68 | 111.8
2019-01-26 08:00 | 110.89 | 87.48
2019-01-26 08:30 | 113.98 | 96.2
2019-01-26 09:00 | 116.09 | 96.92
2019-01-26 09:30 | 108.77 | 85.8
2019-01-26 10:00 | 98.24 | 72.1
2019-01-26 10:30 | 94.43 | 66.93
2019-01-26 11:00 | 93.25 | 68.32
2019-01-26 11:30 | 95.86 | 71.62
2019-01-26 12:00 | 97.37 | 76.82
2019-01-26 12:30 | 98.48 | 76.04
2019-01-26 13:00 | 98.93 | 76.43
2019-01-26 13:30 | 101 | 79.5
2019-01-26 14:00 | 103.79 | 80.27
2019-01-26 14:30 | 100.23 | 78.3
2019-01-26 15:00 | 109.34 | 87.2
2019-01-26 15:30 | 112.42 | 89.08
2019-01-26 16:00 | 117.27 | 89.23
2019-01-26 16:30 | 117.6 | 93.51
2019-01-26 17:00 | 122.34 | 102.27
2019-01-26 17:30 | 116.98 | 95.33
2019-01-26 18:00 | 117.91 | 98.07
2019-01-26 18:30 | 118.31 | 102.62
2019-01-26 19:00 | 129.49 | 116.2
2019-01-26 19:30 | 135.94 | 122.98
2019-01-26 20:00 | 136.39 | 121.91
2019-01-26 20:30 | 131.92 | 116.6
2019-01-26 21:00 | 129.29 | 113.84
2019-01-26 21:30 | 124.34 | 110.13
2019-01-26 22:00 | 123.27 | 109.86
2019-01-26 22:30 | 119.9 | 105.55
2019-01-26 23:00 | 125.36 | 111.58
2019-01-26 23:30 | 132.67 | 118.96
2019-01-27 | 127.19 | 113.84
2019-01-27 00:30 | 128.91 | 114.62
2019-01-27 01:00 | 125.85 | 111.53
2019-01-27 01:30 | 112.72 | 98.93
2019-01-27 02:00 | 116.87 | 103.27
2019-01-27 02:30 | 116.4 | 102.09
2019-01-27 03:00 | 115.45 | 100.72
2019-01-27 03:30 | 121.1 | 107.2
2019-01-27 04:00 | 118.3 | 104.51
2019-01-27 04:30 | 117.38 | 103.89
2019-01-27 05:00 | 115.08 | 100.56
2019-01-27 05:30 | 116.87 | 101.88
2019-01-27 06:00 | 115.29 | 100.02
2019-01-27 06:30 | 107.2 | 91.2
2019-01-27 07:00 | 105.75 | 85.65
2019-01-27 07:30 | 107.64 | 83.9
2019-01-27 08:00 | 107.8 | 80.5
2019-01-27 08:30 | 106.9 | 77.25
2019-01-27 09:00 | 113.1 | 81.85
2019-01-27 09:30 | 120.57 | 89.78
2019-01-27 10:00 | 113.76 | 83.52
2019-01-27 10:30 | 113.46 | 82.53
2019-01-27 11:00 | 119.04 | 90.97
2019-01-27 11:30 | 114.94 | 85.62
2019-01-27 12:00 | 118.37 | 89.48
2019-01-27 12:30 | 121.82 | 94.48
2019-01-27 13:00 | 114.7 | 89.41
2019-01-27 13:30 | 112.98 | 84.25
2019-01-27 14:00 | 112.93 | 82.45
2019-01-27 14:30 | 116.5 | 86.98
2019-01-27 15:00 | 121.73 | 94.59
2019-01-27 15:30 | 116.72 | 89.06
2019-01-27 16:00 | 123.09 | 100.1
2019-01-27 16:30 | 127.58 | 101.1
2019-01-27 17:00 | 120.07 | 89.84
2019-01-27 17:30 | 124.75 | 98.5
2019-01-27 18:00 | 128.47 | 107.6
2019-01-27 18:30 | 126.45 | 109.8
2019-01-27 19:00 | 132.09 | 117.38
2019-01-27 19:30 | 137.16 | 121.43
2019-01-27 20:00 | 135.67 | 119.89
2019-01-27 20:30 | 132.34 | 116.57
2019-01-27 21:00 | 122.71 | 106.68
2019-01-27 21:30 | 118.47 | 102.1
2019-01-27 22:00 | 122.03 | 104.75
2019-01-27 22:30 | 130.33 | 114.16
2019-01-27 23:00 | 131.29 | 115.07
2019-01-27 23:30 | 126.91 | 110.92
2019-01-28 | 132.27 | 116.58
2019-01-28 00:30 | 125.31 | 107.98
2019-01-28 01:00 | 134.36 | 118.44
2019-01-28 01:30 | 129.79 | 114.71
2019-01-28 02:00 | 121.57 | 106.3
2019-01-28 02:30 | 127.67 | 112.25
2019-01-28 03:00 | 126.95 | 112.22
2019-01-28 03:30 | 124.07 | 109.62
2019-01-28 04:00 | 123.14 | 107.58
2019-01-28 04:30 | 124.41 | 109.49
2019-01-28 05:00 | 120.13 | 104.42
2019-01-28 05:30 | 114.34 | 98.84
2019-01-28 06:00 | 110.6 | 93.6
2019-01-28 06:30 | 105.38 | 86.87
2019-01-28 07:00 | 109.77 | 90.09
2019-01-28 07:30 | 110.73 | 90.75
2019-01-28 08:00 | 113.26 | 95.14
2019-01-28 08:30 | 115.85 | 97.56
2019-01-28 09:00 | 111.61 | 91.63
2019-01-28 09:30 | 110.97 | 90.99
2019-01-28 10:00 | 117.25 | 95.87
2019-01-28 10:30 | 119.34 | 99.91
2019-01-28 11:00 | 125.76 | 107.05
2019-01-28 11:30 | 122.65 | 101.15
2019-01-28 12:00 | 117.95 | 94.15
2019-01-28 12:30 | 120.2 | 93.5
2019-01-28 13:00 | 117.46 | 89.71
2019-01-28 13:30 | 116.03 | 92.25
2019-01-28 14:00 | 119.47 | 96.05
2019-01-28 14:30 | 117.36 | 94.16
2019-01-28 15:00 | 113.83 | 92.1
2019-01-28 15:30 | 113.53 | 94.52
2019-01-28 16:00 | 113.28 | 94.76
2019-01-28 16:30 | 114.86 | 95.82
2019-01-28 17:00 | 118.42 | 101.92
2019-01-28 17:30 | 114.89 | 97.68
2019-01-28 18:00 | 122.82 | 105.73
2019-01-28 18:30 | 117.59 | 101.34
2019-01-28 19:00 | 124.58 | 110
2019-01-28 19:30 | 132.36 | 117.33
2019-01-28 20:00 | 136.23 | 120.07
2019-01-28 20:30 | 127.27 | 110.82
2019-01-28 21:00 | 126.12 | 108.96
2019-01-28 21:30 | 128.11 | 110.6
2019-01-28 22:00 | 129.98 | 113.52
2019-01-28 22:30 | 133.49 | 116.79
2019-01-28 23:00 | 130.83 | 115.19
2019-01-28 23:30 | 125.15 | 109.57
2019-01-29 | 126.48 | 111.8
2019-01-29 00:30 | 123.24 | 108.07
2019-01-29 01:00 | 125.39 | 109
2019-01-29 01:30 | 127.93 | 111.33
2019-01-29 02:00 | 125.46 | 109.11
2019-01-29 02:30 | 120.2 | 103.38
2019-01-29 03:00 | 119.16 | 102.94
2019-01-29 03:30 | 124.39 | 107.97
2019-01-29 04:00 | 120.26 | 103.62
2019-01-29 04:30 | 120.7 | 104.28
2019-01-29 05:00 | 125.2 | 108.84
2019-01-29 05:30 | 127.07 | 111.49
2019-01-29 06:00 | 117.78 | 100.6
2019-01-29 06:30 | 116.77 | 100.6
2019-01-29 07:00 | 124.47 | 106.89
2019-01-29 07:30 | 119.56 | 101.24
2019-01-29 08:00 | 121.77 | 103.34
2019-01-29 08:30 | 116.17 | 93.84
2019-01-29 09:00 | 116.95 | 90.58
2019-01-29 09:30 | 111.91 | 82.12
2019-01-29 10:00 | 113.56 | 85.79
2019-01-29 10:30 | 112.45 | 85.54
2019-01-29 11:00 | 106.1 | 78.74
2019-01-29 11:30 | 112.22 | 90.77
2019-01-29 12:00 | 116.39 | 98.25
2019-01-29 12:30 | 121.38 | 101.07
2019-01-29 13:00 | 118.17 | 95.46
2019-01-29 13:30 | 119.56 | 98.24
2019-01-29 14:00 | 113.87 | 91.02
2019-01-29 14:30 | 120.31 | 97.28
2019-01-29 15:00 | 122.61 | 100.37
2019-01-29 15:30 | 115.32 | 93.14
2019-01-29 16:00 | 117.27 | 98.84
2019-01-29 16:30 | 115.15 | 96.73
2019-01-29 17:00 | 113.84 | 96.1
2019-01-29 17:30 | 117.17 | 99.76
2019-01-29 18:00 | 113.19 | 96.41
2019-01-29 18:30 | 113.43 | 98.64
2019-01-29 19:00 | 120.28 | 105.67
2019-01-29 19:30 | 126.22 | 112.68
2019-01-29 20:00 | 129.81 | 116.18
2019-01-29 20:30 | 123.52 | 109.45
2019-01-29 21:00 | 128.2 | 114.36
2019-01-29 21:30 | 120.47 | 106.11
2019-01-29 22:00 | 122.1 | 107.57
2019-01-29 22:30 | 127.36 | 112.48
2019-01-29 23:00 | 132.85 | 116.84
2019-01-29 23:30 | 128.91 | 112.44
2019-01-30 | 126.58 | 110.19
2019-01-30 00:30 | 129.7 | 113.71
2019-01-30 01:00 | 126.5 | 109.86
2019-01-30 01:30 | 130.86 | 114.97
2019-01-30 02:00 | 130.13 | 115.41
2019-01-30 02:30 | 124.54 | 108.76
2019-01-30 03:00 | 125.23 | 109.57
2019-01-30 03:30 | 114.64 | 97.74
2019-01-30 04:00 | 112.03 | 94.45
2019-01-30 04:30 | 118.88 | 103.95
2019-01-30 05:00 | 113.82 | 98.32
2019-01-30 05:30 | 122.16 | 107.05
2019-01-30 06:00 | 117.72 | 101.15
2019-01-30 06:30 | 114.77 | 97.92
2019-01-30 07:00 | 120.4 | 105.36
2019-01-30 07:30 | 122.08 | 105.61
2019-01-30 08:00 | 110.48 | 90.64
2019-01-30 08:30 | 114.16 | 94.27
2019-01-30 09:00 | 112.46 | 91.73
2019-01-30 09:30 | 111.2 | 88.92
2019-01-30 10:00 | 118.81 | 97.35
2019-01-30 10:30 | 118.23 | 93.79
2019-01-30 11:00 | 113.89 | 86.6
2019-01-30 11:30 | 110 | 84.54
2019-01-30 12:00 | 113.16 | 90.53
2019-01-30 12:30 | 111.82 | 88.3
2019-01-30 13:00 | 111.24 | 88.03
2019-01-30 13:30 | 105.52 | 82.24
2019-01-30 14:00 | 113.5 | 92.33
2019-01-30 14:30 | 114.12 | 92.82
2019-01-30 15:00 | 112.53 | 90.19
2019-01-30 15:30 | 117.06 | 96.04
2019-01-30 16:00 | 126.42 | 107.48
2019-01-30 16:30 | 128.26 | 110.9
2019-01-30 17:00 | 123.79 | 105.88
2019-01-30 17:30 | 118.95 | 102.08
2019-01-30 18:00 | 123.91 | 107.65
2019-01-30 18:30 | 114.41 | 98.04
2019-01-30 19:00 | 124.55 | 108.44
2019-01-30 19:30 | 121.94 | 106.81
2019-01-30 20:00 | 127.8 | 112.78
2019-01-30 20:30 | 125.45 | 108.73
2019-01-30 21:00 | 123.05 | 104.68
2019-01-30 21:30 | 119.72 | 101.34
2019-01-30 22:00 | 113.32 | 94.47
2019-01-30 22:30 | 111.36 | 94.57
2019-01-30 23:00 | 115.81 | 98.08
2019-01-30 23:30 | 120.1 | 101.7
2019-01-31 | 118.98 | 99.31
2019-01-31 00:30 | 116.4 | 96.33
2019-01-31 01:00 | 122.01 | 103.6
2019-01-31 01:30 | 128.93 | 111.17
2019-01-31 02:00 | 133.74 | 115.88
2019-01-31 02:30 | 121.63 | 103.09
2019-01-31 03:00 | 123.67 | 104.6
2019-01-31 03:30 | 120.65 | 102.31
2019-01-31 04:00 | 121.76 | 102.75
2019-01-31 04:30 | 119.23 | 99.99
2019-01-31 05:00 | 117.98 | 98.72
2019-01-31 05:30 | 114.62 | 93.98
2019-01-31 06:00 | 115.82 | 96.89
2019-01-31 06:30 | 113.26 | 95.25
2019-01-31 07:00 | 106.84 | 92.28
2019-01-31 07:30 | 112.87 | 100.61
2019-01-31 08:00 | 113.69 | 97.28
2019-01-31 08:30 | 111.86 | 93.58
2019-01-31 09:00 | 118.92 | 101
2019-01-31 09:30 | 119.82 | 101.2
2019-01-31 10:00 | 127.96 | 109.35
2019-01-31 10:30 | 130.3 | 111.26
2019-01-31 11:00 | 129.02 | 111.2
2019-01-31 11:30 | 126.64 | 109.53
2019-01-31 12:00 | 131.98 | 114.04
2019-01-31 12:30 | 133.49 | 116.06
2019-01-31 13:00 | 124.43 | 106.56
2019-01-31 13:30 | 125.83 | 108.18
2019-01-31 14:00 | 123.78 | 106.4
2019-01-31 14:30 | 125.8 | 108.69
2019-01-31 15:00 | 124.94 | 107.07
2019-01-31 15:30 | 127.56 | 109.58
2019-01-31 16:00 | 132.18 | 115.32
2019-01-31 16:30 | 139.61 | 122.01
2019-01-31 17:00 | 139.65 | 120.64
2019-01-31 17:30 | 144.31 | 127.26
2019-01-31 18:00 | 137.86 | 119.94
2019-01-31 18:30 | 137.78 | 119.94
2019-01-31 19:00 | 143.65 | 125.52
2019-01-31 19:30 | 145.28 | 126.05
2019-01-31 20:00 | 139.13 | 121.32
2019-01-31 20:30 | 134.87 | 115.4
2019-01-31 21:00 | 137.32 | 117.05
2019-01-31 21:30 | 131.78 | 110.79
2019-01-31 22:00 | 120.35 | 101.19
2019-01-31 22:30 | 129.21 | 110.99
2019-01-31 23:00 | 127.4 | 109.74
2019-01-31 23:30 | 123.61 | 105
2019-02-01 | 117.19 | 97.84
2019-02-01 00:30 | 117.73 | 99.11
2019-02-01 01:00 | 114.3 | 95.72
2019-02-01 01:30 | 120.59 | 101.91
2019-02-01 02:00 | 122.76 | 104.06
2019-02-01 02:30 | 121.33 | 102.65
2019-02-01 03:00 | 125.27 | 105.77
2019-02-01 03:30 | 131.11 | 112.28
2019-02-01 04:00 | 129.12 | 110.71
2019-02-01 04:30 | 128.94 | 110.65
2019-02-01 05:00 | 126.59 | 109.71
2019-02-01 05:30 | 126.99 | 109.36
2019-02-01 06:00 | 121.88 | 104.15
2019-02-01 06:30 | 116.7 | 97.96
2019-02-01 07:00 | 112.69 | 91.73
2019-02-01 07:30 | 106.89 | 81.34
2019-02-01 08:00 | 105.14 | 74.53
2019-02-01 08:30 | 107.41 | 75.65
2019-02-01 09:00 | 108 | 73.11
2019-02-01 09:30 | 112.73 | 78.33
2019-02-01 10:00 | 119.44 | 85.06
2019-02-01 10:30 | 119.61 | 83.32
2019-02-01 11:00 | 116.29 | 82.14
2019-02-01 11:30 | 123.09 | 87.27
2019-02-01 12:00 | 115.76 | 79.79
2019-02-01 12:30 | 116.33 | 80.79
2019-02-01 13:00 | 118.01 | 77.94
2019-02-01 13:30 | 121.64 | 80.87
2019-02-01 14:00 | 129.58 | 94.39
2019-02-01 14:30 | 129.69 | 100.03
2019-02-01 15:00 | 128.11 | 100.01
2019-02-01 15:30 | 125.56 | 99.04
2019-02-01 16:00 | 134.58 | 113.31
2019-02-01 16:30 | 125.45 | 103.39
2019-02-01 17:00 | 122.22 | 101.35
2019-02-01 17:30 | 124.65 | 102.72
2019-02-01 18:00 | 123.46 | 100.92
2019-02-01 18:30 | 129.1 | 108.74
2019-02-01 19:00 | 131.96 | 112.83
2019-02-01 19:30 | 135.78 | 117.79
2019-02-01 20:00 | 139.39 | 121.45
2019-02-01 20:30 | 130.22 | 111.98
2019-02-01 21:00 | 135.05 | 115.46
2019-02-01 21:30 | 134.15 | 115.07
2019-02-01 22:00 | 133.09 | 114
2019-02-01 22:30 | 132.07 | 113.17
2019-02-01 23:00 | 131.16 | 112.13
2019-02-01 23:30 | 127.58 | 110.09
2019-02-02 | 137.54 | 120.57
2019-02-02 00:30 | 128.2 | 110.36
2019-02-02 01:00 | 134.9 | 116.02
2019-02-02 01:30 | 123.95 | 106.41
2019-02-02 02:00 | 128.18 | 110.48
2019-02-02 02:30 | 137.52 | 119.49
2019-02-02 03:00 | 127.83 | 109.4
2019-02-02 03:30 | 124.1 | 105.36
2019-02-02 04:00 | 124.13 | 105.73
2019-02-02 04:30 | 126.53 | 108.48
2019-02-02 05:00 | 129.95 | 112.36
2019-02-02 05:30 | 127.94 | 110.8
2019-02-02 06:00 | 117.87 | 100.14
2019-02-02 06:30 | 106.72 | 88.38
2019-02-02 07:00 | 109.56 | 92.24
2019-02-02 07:30 | 107.62 | 90.74
2019-02-02 08:00 | 104.11 | 85.17
2019-02-02 08:30 | 104.34 | 80.68
2019-02-02 09:00 | 111.08 | 91.18
2019-02-02 09:30 | 110.63 | 82.67
2019-02-02 10:00 | 107.33 | 82.19
2019-02-02 10:30 | 98.16 | 70.86
2019-02-02 11:00 | 102.15 | 68.84
2019-02-02 11:30 | 101.12 | 69.75
2019-02-02 12:00 | 105.23 | 77.01
2019-02-02 12:30 | 100.79 | 72.07
2019-02-02 13:00 | 99.22 | 70.56
2019-02-02 13:30 | 103.29 | 70
2019-02-02 14:00 | 111.35 | 80.45
2019-02-02 14:30 | 109.77 | 83.87
2019-02-02 15:00 | 109.03 | 83.71
2019-02-02 15:30 | 116.41 | 92.04
2019-02-02 16:00 | 127.1 | 108.03
2019-02-02 16:30 | 128.43 | 109.25
2019-02-02 17:00 | 122.73 | 102.24
2019-02-02 17:30 | 123.12 | 101.8
2019-02-02 18:00 | 128.14 | 107.01
2019-02-02 18:30 | 123.08 | 103.09
2019-02-02 19:00 | 126.01 | 106.92
2019-02-02 19:30 | 131.89 | 113.23
2019-02-02 20:00 | 138.62 | 120.24
2019-02-02 20:30 | 142.07 | 124.22
2019-02-02 21:00 | 131.88 | 114.63
2019-02-02 21:30 | 133.52 | 116.38
2019-02-02 22:00 | 126.67 | 109.54
2019-02-02 22:30 | 118.96 | 100.89
2019-02-02 23:00 | 122.18 | 103.69
2019-02-02 23:30 | 120.99 | 102.76
2019-02-03 | 120.64 | 102.45
2019-02-03 00:30 | 123.91 | 106.21
2019-02-03 01:00 | 127.32 | 109.52
2019-02-03 01:30 | 124.27 | 106.05
2019-02-03 02:00 | 128.02 | 109.53
2019-02-03 02:30 | 117.82 | 99.6
2019-02-03 03:00 | 116.88 | 99.2
2019-02-03 03:30 | 118.26 | 102.92
2019-02-03 04:00 | 113.53 | 98.07
2019-02-03 04:30 | 113.93 | 98.44
2019-02-03 05:00 | 114.5 | 99.57
2019-02-03 05:30 | 106.63 | 90.14
2019-02-03 06:00 | 110.36 | 94.4
2019-02-03 06:30 | 107.27 | 90.33
2019-02-03 07:00 | 105.21 | 86.88
2019-02-03 07:30 | 105.5 | 87.25
2019-02-03 08:00 | 102.53 | 82.55
2019-02-03 08:30 | 107.77 | 89.01
2019-02-03 09:00 | 110.36 | 92.59
2019-02-03 09:30 | 104.08 | 84.44
2019-02-03 10:00 | 105.92 | 85.97
2019-02-03 10:30 | 101.87 | 81.21
2019-02-03 11:00 | 101.69 | 78.5
2019-02-03 11:30 | 93.17 | 64.01
2019-02-03 12:00 | 92.51 | 64.7
2019-02-03 12:30 | 92.79 | 66.42
2019-02-03 13:00 | 94.81 | 71.75
2019-02-03 13:30 | 92.24 | 65.02
2019-02-03 14:00 | 98.87 | 72.86
2019-02-03 14:30 | 91.07 | 68.37
2019-02-03 15:00 | 103.32 | 81
2019-02-03 15:30 | 103.99 | 84.12
2019-02-03 16:00 | 111.14 | 93.73
2019-02-03 16:30 | 106.95 | 89.77
2019-02-03 17:00 | 114.48 | 96.67
2019-02-03 17:30 | 118.49 | 101.62
2019-02-03 18:00 | 123.04 | 106.53
2019-02-03 18:30 | 125.55 | 107.75
2019-02-03 19:00 | 125.96 | 108.28
2019-02-03 19:30 | 130.98 | 113.91
2019-02-03 20:00 | 127.31 | 109.56
2019-02-03 20:30 | 125.12 | 107.03
2019-02-03 21:00 | 129.83 | 112.55
2019-02-03 21:30 | 133.66 | 116.13
2019-02-03 22:00 | 126.05 | 108.98
2019-02-03 22:30 | 122.71 | 105.74
2019-02-03 23:00 | 116.04 | 97.59
2019-02-03 23:30 | 117.12 | 97.78
2019-02-04 | 121.8 | 103.5
2019-02-04 00:30 | 130.36 | 112.88
2019-02-04 01:00 | 127.51 | 109.15
2019-02-04 01:30 | 132.4 | 114.61
2019-02-04 02:00 | 128.8 | 111.35
2019-02-04 02:30 | 121.05 | 103.89
2019-02-04 03:00 | 115.51 | 96.83
2019-02-04 03:30 | 109.31 | 89.96
2019-02-04 04:00 | 107.63 | 88.48
2019-02-04 04:30 | 108.25 | 89.16
2019-02-04 05:00 | 106.08 | 87.19
2019-02-04 05:30 | 107.49 | 89.39
2019-02-04 06:00 | 96.93 | 85.47
2019-02-04 06:30 | 87.23 | 82.33
2019-02-04 07:00 | 85.44 | 79.67
2019-02-04 07:30 | 87.06 | 80.39
2019-02-04 08:00 | 84.66 | 75.19
2019-02-04 08:30 | 84.32 | 72.9
2019-02-04 09:00 | 84.16 | 70.85
2019-02-04 09:30 | 78.25 | 70.3
2019-02-04 10:00 | 73.81 | 66.43
2019-02-04 10:30 | 71.89 | 64.45
2019-02-04 11:00 | 74.7 | 67.43
2019-02-04 11:30 | 70.24 | 61.71
2019-02-04 12:00 | 68.33 | 59.49
2019-02-04 12:30 | 66.94 | 60.69
2019-02-04 13:00 | 65.54 | 57.4
2019-02-04 13:30 | 70.31 | 60.27
2019-02-04 14:00 | 71.1 | 61.14
2019-02-04 14:30 | 67.94 | 57.94
2019-02-04 15:00 | 66.9 | 58.12
2019-02-04 15:30 | 71.65 | 64.7
2019-02-04 16:00 | 74.45 | 69.65
2019-02-04 16:30 | 72.06 | 68.41
2019-02-04 17:00 | 75.27 | 72.07
2019-02-04 17:30 | 85.6 | 81.36
2019-02-04 18:00 | 87.43 | 83.97
2019-02-04 18:30 | 89.31 | 86.35
2019-02-04 19:00 | 93.76 | 91.05
2019-02-04 19:30 | 96.34 | 93.57
2019-02-04 20:00 | 98.75 | 96.11
2019-02-04 20:30 | 94.12 | 91.97
2019-02-04 21:00 | 93.12 | 90.74
2019-02-04 21:30 | 84.51 | 81.28
2019-02-04 22:00 | 84.13 | 80.2
2019-02-04 22:30 | 82.99 | 78.72
2019-02-04 23:00 | 81.14 | 76.62
2019-02-04 23:30 | 76.62 | 72.28
2019-02-05 | 82.13 | 77.49
2019-02-05 00:30 | 84.79 | 80
2019-02-05 01:00 | 81.47 | 76.65
2019-02-05 01:30 | 83.51 | 78.65
2019-02-05 02:00 | 78.62 | 73.56
2019-02-05 02:30 | 83.04 | 78.2
2019-02-05 03:00 | 83.1 | 78.06
2019-02-05 03:30 | 81.25 | 76.06
2019-02-05 04:00 | 80.2 | 74.83
2019-02-05 04:30 | 80 | 75.05
2019-02-05 05:00 | 78.69 | 74.18
2019-02-05 05:30 | 81.19 | 76.46
2019-02-05 06:00 | 78.09 | 73.03
2019-02-05 06:30 | 79 | 73.88
2019-02-05 07:00 | 80.1 | 75.17
2019-02-05 07:30 | 81.6 | 76.49
2019-02-05 08:00 | 83.17 | 77.87
2019-02-05 08:30 | 81.84 | 76.69
2019-02-05 09:00 | 78.51 | 72.65
2019-02-05 09:30 | 80.38 | 74.88
2019-02-05 10:00 | 76.61 | 71.35
2019-02-05 10:30 | 64.13 | 57.3
2019-02-05 11:00 | 63.14 | 55.56
2019-02-05 11:30 | 67.43 | 58.47
2019-02-05 12:00 | 68.49 | 60.56
2019-02-05 12:30 | 64.81 | 56.97
2019-02-05 13:00 | 67.96 | 61.71
2019-02-05 13:30 | 71.64 | 65.6
2019-02-05 14:00 | 76.61 | 71.44
2019-02-05 14:30 | 79 | 72.97
2019-02-05 15:00 | 74.81 | 66.98
2019-02-05 15:30 | 80.79 | 74.19
2019-02-05 16:00 | 85.54 | 78.51
2019-02-05 16:30 | 92.16 | 85.65
2019-02-05 17:00 | 94.61 | 88.31
2019-02-05 17:30 | 99.7 | 92.34
2019-02-05 18:00 | 95.05 | 87.5
2019-02-05 18:30 | 90.68 | 84.2
2019-02-05 19:00 | 101.28 | 94.24
2019-02-05 19:30 | 101.57 | 94.61
2019-02-05 20:00 | 103.16 | 96.02
2019-02-05 20:30 | 107.2 | 99.48
2019-02-05 21:00 | 107.42 | 99.73
2019-02-05 21:30 | 102.07 | 93.97
2019-02-05 22:00 | 93.36 | 87.67
2019-02-05 22:30 | 93.6 | 87.58
2019-02-05 23:00 | 97.22 | 90.38
2019-02-05 23:30 | 95.86 | 88.72
2019-02-06 | 93.54 | 85.86
2019-02-06 00:30 | 94 | 86.12
2019-02-06 01:00 | 98.3 | 90.42
2019-02-06 01:30 | 94.14 | 87.11
2019-02-06 02:00 | 92.45 | 84.86
2019-02-06 02:30 | 98.08 | 90.04
2019-02-06 03:00 | 99.46 | 91.64
2019-02-06 03:30 | 97.49 | 89.53
2019-02-06 04:00 | 96.64 | 88.76
2019-02-06 04:30 | 95.15 | 87.76
2019-02-06 05:00 | 98.77 | 90.71
2019-02-06 05:30 | 99.73 | 91.87
2019-02-06 06:00 | 97.94 | 88.67
2019-02-06 06:30 | 110.61 | 82.01
2019-02-06 07:00 | 112.74 | 83.63
2019-02-06 07:30 | 114.57 | 85.23
2019-02-06 08:00 | 110.38 | 80.39
2019-02-06 08:30 | 110.99 | 82.21
2019-02-06 09:00 | 110.42 | 81.3
2019-02-06 09:30 | 109.64 | 79.93
2019-02-06 10:00 | 110.77 | 78.65
2019-02-06 10:30 | 110.91 | 76.09
2019-02-06 11:00 | 106.74 | 72.07
2019-02-06 11:30 | 104.8 | 70.34
2019-02-06 12:00 | 106.46 | 68.22
2019-02-06 12:30 | 107.05 | 68.49
2019-02-06 13:00 | 106.45 | 71.42
2019-02-06 13:30 | 110.51 | 81.91
2019-02-06 14:00 | 107.68 | 77.45
2019-02-06 14:30 | 106.89 | 74.94
2019-02-06 15:00 | 106.63 | 73.55
2019-02-06 15:30 | 106.66 | 76.94
2019-02-06 16:00 | 106.58 | 77.87
2019-02-06 16:30 | 105.01 | 76.41
2019-02-06 17:00 | 109.84 | 84.22
2019-02-06 17:30 | 113.59 | 88.49
2019-02-06 18:00 | 112.35 | 87.21
2019-02-06 18:30 | 108.84 | 85.68
2019-02-06 19:00 | 113.84 | 91.79
2019-02-06 19:30 | 116.92 | 97.1
2019-02-06 20:00 | 113.22 | 92.84
2019-02-06 20:30 | 111.87 | 90.07
2019-02-06 21:00 | 117.27 | 96.37
2019-02-06 21:30 | 114.53 | 93.37
2019-02-06 22:00 | 114.27 | 92.59
2019-02-06 22:30 | 110.4 | 88.28
2019-02-06 23:00 | 117.64 | 96.12
2019-02-06 23:30 | 117.31 | 96.12
2019-02-07 | 121.56 | 100.85
2019-02-07 00:30 | 117.46 | 95.81
2019-02-07 01:00 | 110.25 | 88.28
2019-02-07 01:30 | 108.81 | 84.78
2019-02-07 02:00 | 114.02 | 89.41
2019-02-07 02:30 | 112.95 | 89.21
2019-02-07 03:00 | 105.55 | 80.36
2019-02-07 03:30 | 107.21 | 82.38
2019-02-07 04:00 | 107.53 | 83.37
2019-02-07 04:30 | 108.25 | 85.67
2019-02-07 05:00 | 110.43 | 87.17
2019-02-07 05:30 | 108.78 | 82.18
2019-02-07 06:00 | 107.3 | 80.89
2019-02-07 06:30 | 101.62 | 71.96
2019-02-07 07:00 | 104.85 | 77.89
2019-02-07 07:30 | 105.61 | 79.48
2019-02-07 08:00 | 107.83 | 81.13
2019-02-07 08:30 | 107.31 | 79.64
2019-02-07 09:00 | 105.52 | 77.42
2019-02-07 09:30 | 105.7 | 77.82
2019-02-07 10:00 | 107.21 | 78.33
2019-02-07 10:30 | 106.18 | 75.83
2019-02-07 11:00 | 106.3 | 73.6
2019-02-07 11:30 | 103.95 | 69.33
2019-02-07 12:00 | 105.44 | 70.49
2019-02-07 12:30 | 106.44 | 70.76
2019-02-07 13:00 | 108.08 | 74.77
2019-02-07 13:30 | 109.13 | 78.41
2019-02-07 14:00 | 112.67 | 85.02
2019-02-07 14:30 | 112.82 | 83.7
2019-02-07 15:00 | 114.73 | 86.32
2019-02-07 15:30 | 113.44 | 86.59
2019-02-07 16:00 | 109.29 | 82.03
2019-02-07 16:30 | 107.25 | 82.37
2019-02-07 17:00 | 107.58 | 82.87
2019-02-07 17:30 | 110.39 | 87.68
2019-02-07 18:00 | 109.67 | 88.08
2019-02-07 18:30 | 110.26 | 91.36
2019-02-07 19:00 | 114.73 | 96.84
2019-02-07 19:30 | 117.47 | 100.75
2019-02-07 20:00 | 117.78 | 100.7
2019-02-07 20:30 | 116.03 | 98.06
2019-02-07 21:00 | 116.85 | 98.91
2019-02-07 21:30 | 117.74 | 99.71
2019-02-07 22:00 | 116.45 | 97.59
2019-02-07 22:30 | 113.14 | 92.97
2019-02-07 23:00 | 116.98 | 98.7
2019-02-07 23:30 | 119.17 | 101.06
2019-02-08 | 120.72 | 101.95
2019-02-08 00:30 | 112.76 | 93.99
2019-02-08 01:00 | 116.85 | 98.56
2019-02-08 01:30 | 122.11 | 104.58
2019-02-08 02:00 | 122.31 | 104.4
2019-02-08 02:30 | 126.53 | 107.73
2019-02-08 03:00 | 122.06 | 102.41
2019-02-08 03:30 | 120.07 | 100.67
2019-02-08 04:00 | 122.73 | 105.2
2019-02-08 04:30 | 115.39 | 98.62
2019-02-08 05:00 | 110.8 | 92.79
2019-02-08 05:30 | 117.63 | 100.81
2019-02-08 06:00 | 118.72 | 101.83
2019-02-08 06:30 | 110.03 | 91.79
2019-02-08 07:00 | 117.68 | 101
2019-02-08 07:30 | 112.15 | 93.02
2019-02-08 08:00 | 104.95 | 82.04
2019-02-08 08:30 | 98.49 | 72.49
2019-02-08 09:00 | 106.19 | 84.34
2019-02-08 09:30 | 102.15 | 76.89
2019-02-08 10:00 | 102.24 | 75.96
2019-02-08 10:30 | 99.07 | 65.18
2019-02-08 11:00 | 100.94 | 70.56
2019-02-08 11:30 | 101.76 | 70.32
2019-02-08 12:00 | 100.46 | 71.16
2019-02-08 12:30 | 106.11 | 79.94
2019-02-08 13:00 | 109.69 | 81.75
2019-02-08 13:30 | 109.75 | 82.86
2019-02-08 14:00 | 108.61 | 79.14
2019-02-08 14:30 | 107.05 | 79.58
2019-02-08 15:00 | 108.47 | 79.69
2019-02-08 15:30 | 109.06 | 82.2
2019-02-08 16:00 | 112.53 | 83.12
2019-02-08 16:30 | 111.93 | 87.58
2019-02-08 17:00 | 117.84 | 97.48
2019-02-08 17:30 | 120.27 | 94.47
2019-02-08 18:00 | 124.84 | 106.63
2019-02-08 18:30 | 123.48 | 106.09
2019-02-08 19:00 | 131.56 | 115.05
2019-02-08 19:30 | 133.69 | 117.49
2019-02-08 20:00 | 131.24 | 114.01
2019-02-08 20:30 | 128.99 | 113.41
2019-02-08 21:00 | 122.55 | 106.18
2019-02-08 21:30 | 120.36 | 104.31
2019-02-08 22:00 | 123.17 | 108.3
2019-02-08 22:30 | 130.22 | 116.08
2019-02-08 23:00 | 133.44 | 118.84
2019-02-08 23:30 | 122.72 | 106.2
2019-02-09 | 122.74 | 105.92
2019-02-09 00:30 | 126.39 | 109
2019-02-09 01:00 | 124.88 | 106.68
2019-02-09 01:30 | 131.16 | 114.12
2019-02-09 02:00 | 124.88 | 106.41
2019-02-09 02:30 | 118.36 | 98.75
2019-02-09 03:00 | 124.05 | 106
2019-02-09 03:30 | 122.5 | 104.15
2019-02-09 04:00 | 124.81 | 107.51
2019-02-09 04:30 | 123.85 | 106.69
2019-02-09 05:00 | 124.49 | 107.18
2019-02-09 05:30 | 119.2 | 100.7
2019-02-09 06:00 | 121.71 | 103.56
2019-02-09 06:30 | 116.47 | 96.75
2019-02-09 07:00 | 114.68 | 92.54
2019-02-09 07:30 | 108.97 | 82.06
2019-02-09 08:00 | 109.42 | 79.09
2019-02-09 08:30 | 111.94 | 81.82
2019-02-09 09:00 | 110.8 | 79.88
2019-02-09 09:30 | 116.86 | 88.85
2019-02-09 10:00 | 113.06 | 83.68
2019-02-09 10:30 | 111.23 | 80.87
2019-02-09 11:00 | 113.18 | 84.53
2019-02-09 11:30 | 114.51 | 85.45
2019-02-09 12:00 | 113.11 | 82.73
2019-02-09 12:30 | 110.96 | 82.68
2019-02-09 13:00 | 108.68 | 80.51
2019-02-09 13:30 | 114.13 | 84.61
2019-02-09 14:00 | 113.81 | 84.69
2019-02-09 14:30 | 114.02 | 85.62
2019-02-09 15:00 | 110.04 | 80.91
2019-02-09 15:30 | 106.08 | 77.96
2019-02-09 16:00 | 116.08 | 89.17
2019-02-09 16:30 | 112.87 | 90.12
2019-02-09 17:00 | 116.5 | 95.04
2019-02-09 17:30 | 118.3 | 97.44
2019-02-09 18:00 | 114.41 | 95.95
2019-02-09 18:30 | 113 | 96.3
2019-02-09 19:00 | 125.42 | 111.01
2019-02-09 19:30 | 123.34 | 108.82
2019-02-09 20:00 | 129.43 | 115.38
2019-02-09 20:30 | 135.97 | 122.13
2019-02-09 21:00 | 126.33 | 111.62
2019-02-09 21:30 | 129.36 | 115.46
2019-02-09 22:00 | 129.27 | 114.63
2019-02-09 22:30 | 134.03 | 119.56
2019-02-09 23:00 | 129.19 | 114.34
2019-02-09 23:30 | 116.5 | 100.15
2019-02-10 | 128.15 | 112.44
2019-02-10 00:30 | 130.2 | 115.93
2019-02-10 01:00 | 131.11 | 115.81
2019-02-10 01:30 | 134.54 | 118.72
2019-02-10 02:00 | 133.62 | 117.02
2019-02-10 02:30 | 126.27 | 107.4
2019-02-10 03:00 | 125.4 | 106.82
2019-02-10 03:30 | 122.44 | 103.27
2019-02-10 04:00 | 124.61 | 106.23
2019-02-10 04:30 | 122.95 | 105.21
2019-02-10 05:00 | 127.27 | 110.1
2019-02-10 05:30 | 128.2 | 111.67
2019-02-10 06:00 | 116.15 | 99.26
2019-02-10 06:30 | 115.69 | 97.58
2019-02-10 07:00 | 119.67 | 96.47
2019-02-10 07:30 | 111.24 | 83.06
2019-02-10 08:00 | 115.29 | 84.3
2019-02-10 08:30 | 107.42 | 76.33
2019-02-10 09:00 | 109.36 | 79.49
2019-02-10 09:30 | 103.74 | 71.82
2019-02-10 10:00 | 103.54 | 70.49
2019-02-10 10:30 | 103.96 | 72.11
2019-02-10 11:00 | 111.03 | 80.47
2019-02-10 11:30 | 112.97 | 83.72
2019-02-10 12:00 | 113.64 | 86.04
2019-02-10 12:30 | 115.52 | 88.04
2019-02-10 13:00 | 118.84 | 91.19
2019-02-10 13:30 | 117.43 | 90.46
2019-02-10 14:00 | 112.45 | 83.84
2019-02-10 14:30 | 112.43 | 84.05
2019-02-10 15:00 | 112.89 | 85.61
2019-02-10 15:30 | 112.63 | 87.59
2019-02-10 16:00 | 125.18 | 106.84
2019-02-10 16:30 | 120.9 | 103.2
2019-02-10 17:00 | 128.81 | 113.67
2019-02-10 17:30 | 129.02 | 115.33
2019-02-10 18:00 | 115.41 | 100.18
2019-02-10 18:30 | 110.94 | 92.62
2019-02-10 19:00 | 120.26 | 103.8
2019-02-10 19:30 | 118.52 | 101.97
2019-02-10 20:00 | 126.49 | 110.97
2019-02-10 20:30 | 130.76 | 114.57
2019-02-10 21:00 | 136.27 | 120.79
2019-02-10 21:30 | 139.87 | 124.3
2019-02-10 22:00 | 138.02 | 121.96
2019-02-10 22:30 | 132.6 | 115.3
2019-02-10 23:00 | 132.79 | 114.78
2019-02-10 23:30 | 130.94 | 112.62
2019-02-11 | 133.71 | 116.1
2019-02-11 00:30 | 129.38 | 110.66
2019-02-11 01:00 | 128.97 | 109.07
2019-02-11 01:30 | 128.93 | 111.14
2019-02-11 02:00 | 129.51 | 111.43
2019-02-11 02:30 | 125.28 | 104.91
2019-02-11 03:00 | 124.14 | 101.57
2019-02-11 03:30 | 120.7 | 98.33
2019-02-11 04:00 | 129.7 | 108.72
2019-02-11 04:30 | 129.77 | 108.18
2019-02-11 05:00 | 124.67 | 102.08
2019-02-11 05:30 | 123.81 | 100.55
2019-02-11 06:00 | 119.08 | 93.98
2019-02-11 06:30 | 117.69 | 91.16
2019-02-11 07:00 | 111.58 | 79.54
2019-02-11 07:30 | 112.59 | 76.64
2019-02-11 08:00 | 113.13 | 74.92
2019-02-11 08:30 | 122.28 | 89.07
2019-02-11 09:00 | 117.35 | 81.84
2019-02-11 09:30 | 119.1 | 84.09
2019-02-11 10:00 | 122.76 | 90.26
2019-02-11 10:30 | 125.76 | 95.08
2019-02-11 11:00 | 117.83 | 85.02
2019-02-11 11:30 | 116.15 | 82.32
2019-02-11 12:00 | 115.3 | 83.81
2019-02-11 12:30 | 111.09 | 79.07
2019-02-11 13:00 | 119.55 | 90.05
2019-02-11 13:30 | 122.58 | 95.83
2019-02-11 14:00 | 133.13 | 109.89
2019-02-11 14:30 | 128.89 | 100.87
2019-02-11 15:00 | 124.94 | 95.58
2019-02-11 15:30 | 123.13 | 92.85
2019-02-11 16:00 | 132.89 | 106.6
2019-02-11 16:30 | 127.34 | 103.07
2019-02-11 17:00 | 134.83 | 118.29
2019-02-11 17:30 | 137.75 | 122.12
2019-02-11 18:00 | 133.23 | 116.92
2019-02-11 18:30 | 125.06 | 109.95
2019-02-11 19:00 | 131.27 | 117.31
2019-02-11 19:30 | 143.33 | 129
2019-02-11 20:00 | 139.34 | 125.18
2019-02-11 20:30 | 134.46 | 119.81
2019-02-11 21:00 | 133.62 | 118.37
2019-02-11 21:30 | 135.21 | 119.63
2019-02-11 22:00 | 131.74 | 115.64
2019-02-11 22:30 | 135.39 | 119.44
2019-02-11 23:00 | 132.09 | 115.69
2019-02-11 23:30 | 127.15 | 109.68
2019-02-12 | 122.74 | 105.39
2019-02-12 00:30 | 121.86 | 104.89
2019-02-12 01:00 | 126.67 | 110.23
2019-02-12 01:30 | 127.84 | 112.88
2019-02-12 02:00 | 122.31 | 105.31
2019-02-12 02:30 | 124.58 | 105.89
2019-02-12 03:00 | 124.04 | 104.66
2019-02-12 03:30 | 124.99 | 105.56
2019-02-12 04:00 | 128.4 | 109.41
2019-02-12 04:30 | 129.85 | 111.61
2019-02-12 05:00 | 120.78 | 101.04
2019-02-12 05:30 | 120.72 | 100.81
2019-02-12 06:00 | 119.94 | 100.96
2019-02-12 06:30 | 114.5 | 94.29
2019-02-12 07:00 | 112.88 | 89.79
2019-02-12 07:30 | 108.12 | 80.48
2019-02-12 08:00 | 111.52 | 84.4
2019-02-12 08:30 | 111.27 | 79.82
2019-02-12 09:00 | 115.19 | 84.74
2019-02-12 09:30 | 112.34 | 79.44
2019-02-12 10:00 | 112.27 | 79.27
2019-02-12 10:30 | 112.8 | 77.83
2019-02-12 11:00 | 111.58 | 76.8
2019-02-12 11:30 | 119.12 | 87.87
2019-02-12 12:00 | 119.06 | 87.82
2019-02-12 12:30 | 122.94 | 92.71
2019-02-12 13:00 | 120.43 | 91.17
2019-02-12 13:30 | 123.09 | 94.75
2019-02-12 14:00 | 123.62 | 94.23
2019-02-12 14:30 | 126.06 | 96.28
2019-02-12 15:00 | 117.72 | 84.9
2019-02-12 15:30 | 111.61 | 80.91
2019-02-12 16:00 | 113.4 | 84.67
2019-02-12 16:30 | 120.76 | 93.04
2019-02-12 17:00 | 118.01 | 93.3
2019-02-12 17:30 | 118.44 | 94.56
2019-02-12 18:00 | 122.06 | 104.26
2019-02-12 18:30 | 127.67 | 112.16
2019-02-12 19:00 | 130.06 | 116.96
2019-02-12 19:30 | 124.48 | 110.91
2019-02-12 20:00 | 134.43 | 120.53
2019-02-12 20:30 | 135.84 | 121.67
2019-02-12 21:00 | 137.47 | 123.39
2019-02-12 21:30 | 133.12 | 118.67
2019-02-12 22:00 | 125.99 | 112.58
2019-02-12 22:30 | 132.16 | 118.85
2019-02-12 23:00 | 126.84 | 110.7
2019-02-12 23:30 | 126.11 | 110.42
2019-02-13 | 128.06 | 113.72
2019-02-13 00:30 | 126.16 | 110.16
2019-02-13 01:00 | 135.02 | 120.09
2019-02-13 01:30 | 125.58 | 108.84
2019-02-13 02:00 | 130.43 | 114.26
2019-02-13 02:30 | 128.19 | 111.24
2019-02-13 03:00 | 124.47 | 105.49
2019-02-13 03:30 | 125.42 | 106.22
2019-02-13 04:00 | 129.4 | 112.33
2019-02-13 04:30 | 124.65 | 107.64
2019-02-13 05:00 | 127.19 | 110.59
2019-02-13 05:30 | 125.04 | 106.63
2019-02-13 06:00 | 118.29 | 98.76
2019-02-13 06:30 | 112.87 | 91.95
2019-02-13 07:00 | 108.21 | 83.34
2019-02-13 07:30 | 104.67 | 76.96
2019-02-13 08:00 | 105.49 | 74.14
2019-02-13 08:30 | 111.68 | 80.32
2019-02-13 09:00 | 109.08 | 77.44
2019-02-13 09:30 | 106.82 | 74.79
2019-02-13 10:00 | 106.99 | 73.73
2019-02-13 10:30 | 107.93 | 78.94
2019-02-13 11:00 | 106.44 | 76.42
2019-02-13 11:30 | 104.15 | 73.93
2019-02-13 12:00 | 110.41 | 83.47
2019-02-13 12:30 | 114.69 | 88.66
2019-02-13 13:00 | 112.11 | 85.61
2019-02-13 13:30 | 115.14 | 89.28
2019-02-13 14:00 | 113.57 | 86.54
2019-02-13 14:30 | 112.35 | 86.1
2019-02-13 15:00 | 108.53 | 81.62
2019-02-13 15:30 | 112.97 | 87.9
2019-02-13 16:00 | 115.53 | 92.17
2019-02-13 16:30 | 115.03 | 92.62
2019-02-13 17:00 | 120.17 | 97.4
2019-02-13 17:30 | 115.15 | 95.01
2019-02-13 18:00 | 129.84 | 113.8
2019-02-13 18:30 | 122.4 | 109.18
2019-02-13 19:00 | 127.79 | 116.27
2019-02-13 19:30 | 130.11 | 118.01
2019-02-13 20:00 | 127.96 | 115.86
2019-02-13 20:30 | 126.78 | 114.7
2019-02-13 21:00 | 131.87 | 118.52
2019-02-13 21:30 | 123.77 | 108.66
2019-02-13 22:00 | 119.63 | 106.02
2019-02-13 22:30 | 128.06 | 113.69
2019-02-13 23:00 | 124.68 | 109.66
2019-02-13 23:30 | 120.09 | 105.59
2019-02-14 | 118.42 | 102.17
2019-02-14 00:30 | 119.76 | 103.09
2019-02-14 01:00 | 118.6 | 101.76
2019-02-14 01:30 | 124.64 | 109.51
2019-02-14 02:00 | 125.29 | 109.7
2019-02-14 02:30 | 120.19 | 103.13
2019-02-14 03:00 | 121.11 | 104.09
2019-02-14 03:30 | 113.28 | 95.02
2019-02-14 04:00 | 119.44 | 101.26
2019-02-14 04:30 | 119.38 | 101.72
2019-02-14 05:00 | 123.66 | 105.18
2019-02-14 05:30 | 124.78 | 106
2019-02-14 06:00 | 123.28 | 103.8
2019-02-14 06:30 | 118.99 | 98.62
2019-02-14 07:00 | 115.83 | 94.7
2019-02-14 07:30 | 111.69 | 87.08
2019-02-14 08:00 | 109.57 | 81.79
2019-02-14 08:30 | 108.96 | 77.8
2019-02-14 09:00 | 107.5 | 74.4
2019-02-14 09:30 | 110.71 | 77.92
2019-02-14 10:00 | 110.61 | 76.99
2019-02-14 10:30 | 113.48 | 82.83
2019-02-14 11:00 | 120.46 | 86.04
2019-02-14 11:30 | 126.59 | 86.66
2019-02-14 12:00 | 121.16 | 80
2019-02-14 12:30 | 119.84 | 78.4
2019-02-14 13:00 | 123.46 | 83.37
2019-02-14 13:30 | 119.66 | 78.15
2019-02-14 14:00 | 121.49 | 80.67
2019-02-14 14:30 | 121.81 | 81.91
2019-02-14 15:00 | 125.58 | 88.63
2019-02-14 15:30 | 128.72 | 91.15
2019-02-14 16:00 | 121.73 | 84.36
2019-02-14 16:30 | 119.93 | 85.23
2019-02-14 17:00 | 132.77 | 102.61
2019-02-14 17:30 | 137.12 | 110.27
2019-02-14 18:00 | 134.97 | 111.32
2019-02-14 18:30 | 134.63 | 112.2
2019-02-14 19:00 | 144.28 | 122.17
2019-02-14 19:30 | 146.5 | 123.59
2019-02-14 20:00 | 136.79 | 113.81
2019-02-14 20:30 | 138.34 | 112.22
2019-02-14 21:00 | 137.36 | 111.71
2019-02-14 21:30 | 137.66 | 111.74
2019-02-14 22:00 | 134.54 | 108.69
2019-02-14 22:30 | 133.37 | 109.18
2019-02-14 23:00 | 136.4 | 111.32
2019-02-14 23:30 | 130.17 | 104.76
2019-02-15 | 137.06 | 110.87
2019-02-15 00:30 | 137.32 | 111.03
2019-02-15 01:00 | 130.21 | 103.94
2019-02-15 01:30 | 135.7 | 108.83
2019-02-15 02:00 | 140.53 | 116.24
2019-02-15 02:30 | 138.02 | 113.58
2019-02-15 03:00 | 137.32 | 112.15
2019-02-15 03:30 | 132.5 | 106.17
2019-02-15 04:00 | 128.34 | 102.23
2019-02-15 04:30 | 133.72 | 111.44
2019-02-15 05:00 | 137.99 | 116.98
2019-02-15 05:30 | 137.99 | 117.15
2019-02-15 06:00 | 131.67 | 111.2
2019-02-15 06:30 | 118.95 | 97.4
2019-02-15 07:00 | 127.69 | 106.79
2019-02-15 07:30 | 123.92 | 99.75
2019-02-15 08:00 | 124.09 | 95.72
2019-02-15 08:30 | 115.44 | 85.01
2019-02-15 09:00 | 112.58 | 85.32
2019-02-15 09:30 | 111.06 | 74.8
2019-02-15 10:00 | 122.28 | 86.04
2019-02-15 10:30 | 120.05 | 88.46
2019-02-15 11:00 | 131.34 | 100.45
2019-02-15 11:30 | 127.12 | 98.63
2019-02-15 12:00 | 134.2 | 109.48
2019-02-15 12:30 | 134.35 | 107.29
2019-02-15 13:00 | 129.64 | 94.65
2019-02-15 13:30 | 128.13 | 93.76
2019-02-15 14:00 | 126.63 | 91.24
2019-02-15 14:30 | 124.32 | 85.51
2019-02-15 15:00 | 125.26 | 86.58
2019-02-15 15:30 | 126.3 | 92.51
2019-02-15 16:00 | 127.54 | 96.97
2019-02-15 16:30 | 136.37 | 108.81
2019-02-15 17:00 | 134.87 | 109.53
2019-02-15 17:30 | 144.67 | 114.99
2019-02-15 18:00 | 142.38 | 118.07
2019-02-15 18:30 | 139.59 | 115.97
2019-02-15 19:00 | 143.06 | 119.27
2019-02-15 19:30 | 144.59 | 120.93
2019-02-15 20:00 | 153.09 | 130.04
2019-02-15 20:30 | 149.02 | 126.05
2019-02-15 21:00 | 147.94 | 124.81
2019-02-15 21:30 | 150.9 | 127.4
2019-02-15 22:00 | 145.87 | 122.93
2019-02-15 22:30 | 144.53 | 121.73
2019-02-15 23:00 | 139.43 | 115.46
2019-02-15 23:30 | 132.92 | 107.7
2019-02-16 | 138.18 | 113.83
2019-02-16 00:30 | 133.74 | 108.53
2019-02-16 01:00 | 136.76 | 112.92
2019-02-16 01:30 | 140.47 | 117.05
2019-02-16 02:00 | 135.01 | 111.85
2019-02-16 02:30 | 133.01 | 110.38
2019-02-16 03:00 | 133.29 | 111.09
2019-02-16 03:30 | 129.45 | 106.79
2019-02-16 04:00 | 132.38 | 109.56
2019-02-16 04:30 | 132.06 | 108.71
2019-02-16 05:00 | 140.46 | 117.95
2019-02-16 05:30 | 135.92 | 112.85
2019-02-16 06:00 | 135.98 | 114.28
2019-02-16 06:30 | 122.4 | 99.33
2019-02-16 07:00 | 134.78 | 111.45
2019-02-16 07:30 | 129.77 | 102.38
2019-02-16 08:00 | 123.52 | 88.5
2019-02-16 08:30 | 127.63 | 88.11
2019-02-16 09:00 | 130.25 | 92.84
2019-02-16 09:30 | 129.23 | 88.78
2019-02-16 10:00 | 137.79 | 96.48
2019-02-16 10:30 | 147.2 | 106.31
2019-02-16 11:00 | 142.54 | 99.63
2019-02-16 11:30 | 139.69 | 97.23
2019-02-16 12:00 | 142.85 | 101.06
2019-02-16 12:30 | 146.04 | 107.47
2019-02-16 13:00 | 145.88 | 106.22
2019-02-16 13:30 | 141.68 | 101.33
2019-02-16 14:00 | 148.04 | 108.42
2019-02-16 14:30 | 142.72 | 100.17
2019-02-16 15:00 | 141.98 | 101.51
2019-02-16 15:30 | 146.89 | 109.1
2019-02-16 16:00 | 147.33 | 110.06
2019-02-16 16:30 | 147.22 | 109.76
2019-02-16 17:00 | 141.22 | 103.31
2019-02-16 17:30 | 141.85 | 107.05
2019-02-16 18:00 | 148.54 | 117.92
2019-02-16 18:30 | 139.38 | 112.11
2019-02-16 19:00 | 149.14 | 121.1
2019-02-16 19:30 | 151.9 | 125.27
2019-02-16 20:00 | 153.45 | 126.88
2019-02-16 20:30 | 149.83 | 123.94
2019-02-16 21:00 | 149.68 | 122.43
2019-02-16 21:30 | 150.5 | 123.4
2019-02-16 22:00 | 155.3 | 128.38
2019-02-16 22:30 | 151.21 | 125.79
2019-02-16 23:00 | 148.44 | 123.08
2019-02-16 23:30 | 138.63 | 113.29
2019-02-17 | 141.92 | 115.92
2019-02-17 00:30 | 130.12 | 103.88
2019-02-17 01:00 | 135.42 | 108.92
2019-02-17 01:30 | 141.97 | 116.88
2019-02-17 02:00 | 146.44 | 121.34
2019-02-17 02:30 | 140.71 | 114.47
2019-02-17 03:00 | 139.26 | 112.27
2019-02-17 03:30 | 141.57 | 115.58
2019-02-17 04:00 | 137.51 | 111.7
2019-02-17 04:30 | 141.68 | 117.6
2019-02-17 05:00 | 142.29 | 116.85
2019-02-17 05:30 | 132.11 | 108.36
2019-02-17 06:00 | 128.93 | 106.16
2019-02-17 06:30 | 120.62 | 96.58
2019-02-17 07:00 | 115.92 | 86.22
2019-02-17 07:30 | 118.78 | 85.88
2019-02-17 08:00 | 120.65 | 81.61
2019-02-17 08:30 | 123.52 | 79.19
2019-02-17 09:00 | 126.56 | 82.41
2019-02-17 09:30 | 132.19 | 89.27
2019-02-17 10:00 | 125.23 | 80.32
2019-02-17 10:30 | 125.99 | 78.96
2019-02-17 11:00 | 126.65 | 82.12
2019-02-17 11:30 | 128.35 | 83.34
2019-02-17 12:00 | 125.34 | 79.6
2019-02-17 12:30 | 133.88 | 91.48
2019-02-17 13:00 | 122.61 | 79.18
2019-02-17 13:30 | 123.84 | 80.73
2019-02-17 14:00 | 128.47 | 84.36
2019-02-17 14:30 | 129.7 | 86.83
2019-02-17 15:00 | 131.28 | 90.12
2019-02-17 15:30 | 140.73 | 101.67
2019-02-17 16:00 | 142.49 | 101.86
2019-02-17 16:30 | 132.23 | 99.39
2019-02-17 17:00 | 134.95 | 99.65
2019-02-17 17:30 | 145.2 | 111.06
2019-02-17 18:00 | 141.82 | 110.92
2019-02-17 18:30 | 143.93 | 117.69
2019-02-17 19:00 | 146.59 | 121.08
2019-02-17 19:30 | 147.98 | 122.71
2019-02-17 20:00 | 147.07 | 122.34
2019-02-17 20:30 | 145.55 | 121.14
2019-02-17 21:00 | 141.95 | 116.06
2019-02-17 21:30 | 138.44 | 113.43
2019-02-17 22:00 | 145.52 | 119.9
2019-02-17 22:30 | 152.35 | 126.71
2019-02-17 23:00 | 141.59 | 114.99
2019-02-17 23:30 | 137.07 | 111.53
2019-02-18 | 136.33 | 110.9
2019-02-18 00:30 | 137.19 | 110.96
2019-02-18 01:00 | 130.92 | 102.77
2019-02-18 01:30 | 137.73 | 111.49
2019-02-18 02:00 | 137.51 | 111.74
2019-02-18 02:30 | 135.22 | 110.58
2019-02-18 03:00 | 132.6 | 108.46
2019-02-18 03:30 | 133.86 | 108.8
2019-02-18 04:00 | 136.26 | 112.22
2019-02-18 04:30 | 138.5 | 113.84
2019-02-18 05:00 | 132.84 | 108.06
2019-02-18 05:30 | 133.98 | 106.97
2019-02-18 06:00 | 126.08 | 96.68
2019-02-18 06:30 | 120.12 | 91.16
2019-02-18 07:00 | 127.28 | 97.41
2019-02-18 07:30 | 128.33 | 94.16
2019-02-18 08:00 | 127.8 | 87.8
2019-02-18 08:30 | 130.89 | 90.26
2019-02-18 09:00 | 125.01 | 80.11
2019-02-18 09:30 | 125.2 | 81.87
2019-02-18 10:00 | 121.52 | 77.57
2019-02-18 10:30 | 119.6 | 77.28
2019-02-18 11:00 | 111.75 | 70.38
2019-02-18 11:30 | 112.11 | 69.39
2019-02-18 12:00 | 123 | 80.13
2019-02-18 12:30 | 129.78 | 86.97
2019-02-18 13:00 | 130.96 | 89.34
2019-02-18 13:30 | 134.17 | 92.83
2019-02-18 14:00 | 137.06 | 93.8
2019-02-18 14:30 | 133.65 | 91
2019-02-18 15:00 | 140.68 | 99.54
2019-02-18 15:30 | 141.48 | 99.94
2019-02-18 16:00 | 142.97 | 103.52
2019-02-18 16:30 | 140.96 | 103.51
2019-02-18 17:00 | 131.57 | 94.29
2019-02-18 17:30 | 129.99 | 97.55
2019-02-18 18:00 | 139.34 | 108.88
2019-02-18 18:30 | 139.03 | 111.89
2019-02-18 19:00 | 148.75 | 122.88
2019-02-18 19:30 | 145.68 | 118.82
2019-02-18 20:00 | 142.82 | 115.61
2019-02-18 20:30 | 146.05 | 118.96
2019-02-18 21:00 | 141.53 | 116.33
2019-02-18 21:30 | 128.23 | 102.64
2019-02-18 22:00 | 128.94 | 104.39
2019-02-18 22:30 | 135.44 | 110.02
2019-02-18 23:00 | 134.34 | 109.71
2019-02-18 23:30 | 129.59 | 106.71
2019-02-19 | 125.8 | 102.07
2019-02-19 00:30 | 134.91 | 111.29
2019-02-19 01:00 | 131.35 | 107.75
2019-02-19 01:30 | 131.17 | 107.09
2019-02-19 02:00 | 134.83 | 112.14
2019-02-19 02:30 | 130.84 | 107.64
2019-02-19 03:00 | 129.13 | 106.1
2019-02-19 03:30 | 127.52 | 103.45
2019-02-19 04:00 | 120.34 | 97.97
2019-02-19 04:30 | 117.97 | 95.97
2019-02-19 05:00 | 125.59 | 104.13
2019-02-19 05:30 | 131.05 | 108.34
2019-02-19 06:00 | 115.06 | 90.81
2019-02-19 06:30 | 119.01 | 96.76
2019-02-19 07:00 | 121.49 | 97.8
2019-02-19 07:30 | 116.43 | 86.59
2019-02-19 08:00 | 123.11 | 89.16
2019-02-19 08:30 | 113.58 | 78.15
2019-02-19 09:00 | 111.8 | 73.58
2019-02-19 09:30 | 125.13 | 88.61
2019-02-19 10:00 | 121.15 | 83.92
2019-02-19 10:30 | 120.86 | 82.11
2019-02-19 11:00 | 115.3 | 73.39
2019-02-19 11:30 | 114.45 | 71.44
2019-02-19 12:00 | 121.24 | 78.97
2019-02-19 12:30 | 125.55 | 86.95
2019-02-19 13:00 | 122.5 | 82.53
2019-02-19 13:30 | 124.58 | 83.88
2019-02-19 14:00 | 125.69 | 86.19
2019-02-19 14:30 | 122.1 | 83.86
2019-02-19 15:00 | 120.87 | 85.06
2019-02-19 15:30 | 115.74 | 82.43
2019-02-19 16:00 | 119.49 | 85.91
2019-02-19 16:30 | 114.87 | 79.91
2019-02-19 17:00 | 125.06 | 92.34
2019-02-19 17:30 | 131 | 104.12
2019-02-19 18:00 | 129.3 | 104.98
2019-02-19 18:30 | 131.7 | 108.03
2019-02-19 19:00 | 140.09 | 115.91
2019-02-19 19:30 | 139.7 | 115.58
2019-02-19 20:00 | 138.98 | 115.57
2019-02-19 20:30 | 140.17 | 116.27
2019-02-19 21:00 | 141.3 | 116.29
2019-02-19 21:30 | 146.32 | 121.35
2019-02-19 22:00 | 139.84 | 112.84
2019-02-19 22:30 | 149.08 | 124.54
2019-02-19 23:00 | 151.22 | 127.49
2019-02-19 23:30 | 148.44 | 126.02
2019-02-20 | 140.15 | 117.07
2019-02-20 00:30 | 141.28 | 115.5
2019-02-20 01:00 | 144 | 119.03
2019-02-20 01:30 | 143.63 | 118.82
2019-02-20 02:00 | 136.92 | 112.8
2019-02-20 02:30 | 136.76 | 112.2
2019-02-20 03:00 | 127.71 | 105.17
2019-02-20 03:30 | 127.66 | 106.71
2019-02-20 04:00 | 116.3 | 96.37
2019-02-20 04:30 | 119.84 | 99.78
2019-02-20 05:00 | 117.55 | 96.54
2019-02-20 05:30 | 116.35 | 95.58
2019-02-20 06:00 | 114.47 | 94.12
2019-02-20 06:30 | 109.11 | 90.55
2019-02-20 07:00 | 112.83 | 89.75
2019-02-20 07:30 | 113.33 | 87.85
2019-02-20 08:00 | 110.89 | 79.83
2019-02-20 08:30 | 119.15 | 87.5
2019-02-20 09:00 | 109.92 | 74.64
2019-02-20 09:30 | 116.56 | 81.48
2019-02-20 10:00 | 114.13 | 78.5
2019-02-20 10:30 | 108.48 | 72.78
2019-02-20 11:00 | 113.82 | 78.38
2019-02-20 11:30 | 114.31 | 79.72
2019-02-20 12:00 | 112.04 | 76.33
2019-02-20 12:30 | 123.34 | 89.4
2019-02-20 13:00 | 116.25 | 83.22
2019-02-20 13:30 | 117.86 | 86.23
2019-02-20 14:00 | 113.28 | 79.3
2019-02-20 14:30 | 113.26 | 87.82
2019-02-20 15:00 | 109.97 | 76.47
2019-02-20 15:30 | 112.3 | 80.8
2019-02-20 16:00 | 110.46 | 84.54
2019-02-20 16:30 | 108.85 | 78.86
2019-02-20 17:00 | 106.75 | 76.16
2019-02-20 17:30 | 106.38 | 81.15
2019-02-20 18:00 | 113.08 | 90.45
2019-02-20 18:30 | 115.87 | 95.91
2019-02-20 19:00 | 121.13 | 102.58
2019-02-20 19:30 | 122.99 | 104.67
2019-02-20 20:00 | 129.7 | 111.54
2019-02-20 20:30 | 127.89 | 109.64
2019-02-20 21:00 | 128 | 109.43
2019-02-20 21:30 | 125.08 | 106.49
2019-02-20 22:00 | 128.82 | 109.83
2019-02-20 22:30 | 119.72 | 100.62
2019-02-20 23:00 | 119.57 | 98.63
2019-02-20 23:30 | 118.54 | 97.04
2019-02-21 | 118.93 | 97.47
2019-02-21 00:30 | 119.76 | 98.22
2019-02-21 01:00 | 130.48 | 110.25
2019-02-21 01:30 | 123.47 | 104.16
2019-02-21 02:00 | 121.2 | 101.17
2019-02-21 02:30 | 129.75 | 109.06
2019-02-21 03:00 | 124.99 | 104.59
2019-02-21 03:30 | 122.57 | 102.62
2019-02-21 04:00 | 122.18 | 102.5
2019-02-21 04:30 | 121.85 | 103.36
2019-02-21 05:00 | 117.33 | 100.42
2019-02-21 05:30 | 121.54 | 103.83
2019-02-21 06:00 | 120.44 | 100.65
2019-02-21 06:30 | 112.67 | 93.66
2019-02-21 07:00 | 103.56 | 82.02
2019-02-21 07:30 | 109.69 | 83.83
2019-02-21 08:00 | 108.68 | 77.92
2019-02-21 08:30 | 101.07 | 67.07
2019-02-21 09:00 | 106.19 | 71.94
2019-02-21 09:30 | 106.34 | 73.68
2019-02-21 10:00 | 104.37 | 70.41
2019-02-21 10:30 | 107.88 | 73.8
2019-02-21 11:00 | 102.64 | 67.64
2019-02-21 11:30 | 111.25 | 77.32
2019-02-21 12:00 | 114.5 | 81.3
2019-02-21 12:30 | 109.17 | 75.51
2019-02-21 13:00 | 105.37 | 70.92
2019-02-21 13:30 | 104.94 | 71.18
2019-02-21 14:00 | 99.27 | 67.33
2019-02-21 14:30 | 113.6 | 83.17
2019-02-21 15:00 | 108.13 | 76.05
2019-02-21 15:30 | 102.56 | 73.64
2019-02-21 16:00 | 111.92 | 85.76
2019-02-21 16:30 | 112.42 | 84.6
2019-02-21 17:00 | 102.64 | 74.49
2019-02-21 17:30 | 110.15 | 86
2019-02-21 18:00 | 102.44 | 84.18
2019-02-21 18:30 | 109.19 | 93.2
2019-02-21 19:00 | 115.14 | 99.07
2019-02-21 19:30 | 118.57 | 102.9
2019-02-21 20:00 | 117.2 | 100.52
2019-02-21 20:30 | 125.35 | 107.79
2019-02-21 21:00 | 126.41 | 108.39
2019-02-21 21:30 | 113.29 | 95.55
2019-02-21 22:00 | 111.03 | 92.58
2019-02-21 22:30 | 108.04 | 88.54
2019-02-21 23:00 | 105.48 | 84.23
2019-02-21 23:30 | 114.07 | 92.69
2019-02-22 | 117.03 | 96.22
2019-02-22 00:30 | 120.77 | 98.72
2019-02-22 01:00 | 118.58 | 95.79
2019-02-22 01:30 | 122.13 | 100.04
2019-02-22 02:00 | 127.21 | 105.05
2019-02-22 02:30 | 134.47 | 114.11
2019-02-22 03:00 | 134.39 | 112.82
2019-02-22 03:30 | 137.95 | 116.68
2019-02-22 04:00 | 129.56 | 109.04
2019-02-22 04:30 | 137.57 | 117.73
2019-02-22 05:00 | 133.32 | 112.66
2019-02-22 05:30 | 130.74 | 109.42
2019-02-22 06:00 | 132.07 | 110.53
2019-02-22 06:30 | 123.92 | 103.96
2019-02-22 07:00 | 125.55 | 103
2019-02-22 07:30 | 131.99 | 105.83
2019-02-22 08:00 | 124.81 | 94.72
2019-02-22 08:30 | 122.52 | 88.58
2019-02-22 09:00 | 124.41 | 88.84
2019-02-22 09:30 | 129.84 | 97
2019-02-22 10:00 | 127.06 | 99.99
2019-02-22 10:30 | 125.24 | 92.77
2019-02-22 11:00 | 128.85 | 94.76
2019-02-22 11:30 | 127.73 | 90.54
2019-02-22 12:00 | 131.83 | 94.06
2019-02-22 12:30 | 128.73 | 93.62
2019-02-22 13:00 | 127.42 | 88.87
2019-02-22 13:30 | 130.9 | 92.49
2019-02-22 14:00 | 131.24 | 90.9
2019-02-22 14:30 | 137.93 | 97.74
2019-02-22 15:00 | 138.27 | 98.94
2019-02-22 15:30 | 132.91 | 93.91
2019-02-22 16:00 | 145.71 | 118.11
2019-02-22 16:30 | 141.74 | 112.25
2019-02-22 17:00 | 138.99 | 103.17
2019-02-22 17:30 | 135.53 | 108.04
2019-02-22 18:00 | 142 | 117.9
2019-02-22 18:30 | 133.76 | 110.1
2019-02-22 19:00 | 138.66 | 115.77
2019-02-22 19:30 | 148.23 | 124.63
2019-02-22 20:00 | 149.53 | 126.58
2019-02-22 20:30 | 146.53 | 122.61
2019-02-22 21:00 | 144.31 | 120.62
2019-02-22 21:30 | 137.99 | 114.04
2019-02-22 22:00 | 136.08 | 112.1
2019-02-22 22:30 | 131.15 | 107.22
2019-02-22 23:00 | 128.88 | 103.69
2019-02-22 23:30 | 129.08 | 104.25
2019-02-23 | 123.93 | 98.8
2019-02-23 00:30 | 124.69 | 100.85
2019-02-23 01:00 | 131.41 | 107.91
2019-02-23 01:30 | 136.16 | 111.65
2019-02-23 02:00 | 140.44 | 116.73
2019-02-23 02:30 | 146.03 | 123.55
2019-02-23 03:00 | 140.41 | 115.95
2019-02-23 03:30 | 138.93 | 113.01
2019-02-23 04:00 | 140.57 | 115.9
2019-02-23 04:30 | 139 | 115.27
2019-02-23 05:00 | 138.34 | 113.58
2019-02-23 05:30 | 126.94 | 102.7
2019-02-23 06:00 | 124.34 | 101.52
2019-02-23 06:30 | 113.8 | 90.29
2019-02-23 07:00 | 120.55 | 95
2019-02-23 07:30 | 126.97 | 97.05
2019-02-23 08:00 | 118.32 | 82.03
2019-02-23 08:30 | 125.12 | 85.65
2019-02-23 09:00 | 125.54 | 90.98
2019-02-23 09:30 | 122.65 | 91.4
2019-02-23 10:00 | 117.29 | 85.48
2019-02-23 10:30 | 108.04 | 75.47
2019-02-23 11:00 | 104.96 | 70.89
2019-02-23 11:30 | 110.81 | 75.3
2019-02-23 12:00 | 115.96 | 78.24
2019-02-23 12:30 | 119.26 | 76.72
2019-02-23 13:00 | 125.19 | 83.62
2019-02-23 13:30 | 128.89 | 91.53
2019-02-23 14:00 | 131.23 | 97.77
2019-02-23 14:30 | 135.66 | 96.75
2019-02-23 15:00 | 138.51 | 99.36
2019-02-23 15:30 | 133.9 | 93.91
2019-02-23 16:00 | 128.95 | 89.25
2019-02-23 16:30 | 127.47 | 88.6
2019-02-23 17:00 | 127.68 | 91.24
2019-02-23 17:30 | 140.18 | 109.96
2019-02-23 18:00 | 135.42 | 113.1
2019-02-23 18:30 | 136.29 | 112.15
2019-02-23 19:00 | 146.1 | 123.27
2019-02-23 19:30 | 143.17 | 120.72
2019-02-23 20:00 | 149.12 | 127.14
2019-02-23 20:30 | 145.58 | 123.81
2019-02-23 21:00 | 147.32 | 125.9
2019-02-23 21:30 | 137.59 | 115.27
2019-02-23 22:00 | 129.52 | 106.65
2019-02-23 22:30 | 133.61 | 112.23
2019-02-23 23:00 | 130.84 | 109.3
2019-02-23 23:30 | 130.3 | 108.34
2019-02-24 | 129.09 | 106.41
2019-02-24 00:30 | 125.61 | 102.21
2019-02-24 01:00 | 127.67 | 105
2019-02-24 01:30 | 128.44 | 106.37
2019-02-24 02:00 | 130.78 | 107.29
2019-02-24 02:30 | 127.29 | 104.09
2019-02-24 03:00 | 126.28 | 102.42
2019-02-24 03:30 | 127.88 | 103.48
2019-02-24 04:00 | 125.26 | 102.48
2019-02-24 04:30 | 129.83 | 107.93
2019-02-24 05:00 | 129.13 | 106.73
2019-02-24 05:30 | 127.91 | 104.85
2019-02-24 06:00 | 123.64 | 101.47
2019-02-24 06:30 | 110.78 | 87.42
2019-02-24 07:00 | 119.67 | 92.95
2019-02-24 07:30 | 118.63 | 85.11
2019-02-24 08:00 | 117.68 | 80.43
2019-02-24 08:30 | 119.61 | 75.84
2019-02-24 09:00 | 119.79 | 74.01
2019-02-24 09:30 | 119.6 | 74.73
2019-02-24 10:00 | 123.99 | 81.21
2019-02-24 10:30 | 128.23 | 86.09
2019-02-24 11:00 | 127.32 | 85.32
2019-02-24 11:30 | 125.24 | 84.67
2019-02-24 12:00 | 127.57 | 95.04
2019-02-24 12:30 | 123.48 | 83.5
2019-02-24 13:00 | 124.39 | 88.96
2019-02-24 13:30 | 121.53 | 84.11
2019-02-24 14:00 | 129.38 | 96.91
2019-02-24 14:30 | 130.75 | 95.86
2019-02-24 15:00 | 128.88 | 90.98
2019-02-24 15:30 | 119.48 | 79.96
2019-02-24 16:00 | 128.78 | 92.25
2019-02-24 16:30 | 130.11 | 100.4
2019-02-24 17:00 | 136.07 | 102.25
2019-02-24 17:30 | 133.27 | 105.75
2019-02-24 18:00 | 131.26 | 103.69
2019-02-24 18:30 | 127.93 | 104.48
2019-02-24 19:00 | 130.42 | 107.23
2019-02-24 19:30 | 136.03 | 113.17
2019-02-24 20:00 | 134.44 | 111.01
2019-02-24 20:30 | 134.31 | 110.15
2019-02-24 21:00 | 135.27 | 110.91
2019-02-24 21:30 | 134.06 | 108.99
2019-02-24 22:00 | 127.48 | 102.94
2019-02-24 22:30 | 124 | 98.97
2019-02-24 23:00 | 119.95 | 94.79
2019-02-24 23:30 | 133.43 | 109.79
2019-02-25 | 128.78 | 105.54
2019-02-25 00:30 | 131.18 | 107.02
2019-02-25 01:00 | 131.41 | 109.87
2019-02-25 01:30 | 126.28 | 103.65
2019-02-25 02:00 | 120.07 | 97.65
2019-02-25 02:30 | 118.32 | 96.41
2019-02-25 03:00 | 123.15 | 99.53
2019-02-25 03:30 | 123.77 | 100.1
2019-02-25 04:00 | 124.92 | 102.36
2019-02-25 04:30 | 125.45 | 102.45
2019-02-25 05:00 | 127.82 | 105.64
2019-02-25 05:30 | 122.74 | 99.86
2019-02-25 06:00 | 119.92 | 94.68
2019-02-25 06:30 | 119.75 | 96.35
2019-02-25 07:00 | 123.16 | 98.83
2019-02-25 07:30 | 126.17 | 95.21
2019-02-25 08:00 | 116.03 | 76.33
2019-02-25 08:30 | 116.56 | 71.98
2019-02-25 09:00 | 123.97 | 79.82
2019-02-25 09:30 | 124.02 | 77.77
2019-02-25 10:00 | 122.27 | 74.97
2019-02-25 10:30 | 122.12 | 75.91
2019-02-25 11:00 | 121.51 | 75.31
2019-02-25 11:30 | 119.86 | 77.85
2019-02-25 12:00 | 121.19 | 78.03
2019-02-25 12:30 | 119.11 | 76.53
2019-02-25 13:00 | 124.94 | 79.71
2019-02-25 13:30 | 124.49 | 79.37
2019-02-25 14:00 | 128.57 | 85.43
2019-02-25 14:30 | 137.33 | 95.75
2019-02-25 15:00 | 137 | 94.21
2019-02-25 15:30 | 123.87 | 78.98
2019-02-25 16:00 | 129.68 | 86.36
2019-02-25 16:30 | 134.62 | 92.2
2019-02-25 17:00 | 134.93 | 94.96
2019-02-25 17:30 | 131.68 | 98.09
2019-02-25 18:00 | 129.1 | 101.56
2019-02-25 18:30 | 129.17 | 103.84
2019-02-25 19:00 | 139.73 | 116.41
2019-02-25 19:30 | 149.91 | 125.39
2019-02-25 20:00 | 143.88 | 119.55
2019-02-25 20:30 | 142.14 | 117.65
2019-02-25 21:00 | 134.07 | 110.55
2019-02-25 21:30 | 131.14 | 106.63
2019-02-25 22:00 | 134.62 | 110.7
2019-02-25 22:30 | 130.57 | 107.27
2019-02-25 23:00 | 131.12 | 107.78
2019-02-25 23:30 | 131.61 | 108.74
2019-02-26 | 136.73 | 113.24
2019-02-26 00:30 | 136.5 | 113.59
2019-02-26 01:00 | 137.76 | 113.81
2019-02-26 01:30 | 136.08 | 113.46
2019-02-26 02:00 | 136.51 | 114.28
2019-02-26 02:30 | 140.79 | 118.27
2019-02-26 03:00 | 134.99 | 111.71
2019-02-26 03:30 | 130.63 | 106.93
2019-02-26 04:00 | 140.03 | 116.59
2019-02-26 04:30 | 138.17 | 115
2019-02-26 05:00 | 137.38 | 115.5
2019-02-26 05:30 | 140.92 | 119.99
2019-02-26 06:00 | 129.16 | 106.93
2019-02-26 06:30 | 127.77 | 106.86
2019-02-26 07:00 | 120.37 | 96.37
2019-02-26 07:30 | 124.12 | 95.67
2019-02-26 08:00 | 116.61 | 87.57
2019-02-26 08:30 | 111.74 | 77.88
2019-02-26 09:00 | 114.62 | 78.52
2019-02-26 09:30 | 111.41 | 75.37
2019-02-26 10:00 | 117.43 | 80.9
2019-02-26 10:30 | 116.95 | 83.5
2019-02-26 11:00 | 110.83 | 75.17
2019-02-26 11:30 | 113.62 | 76.75
2019-02-26 12:00 | 118.31 | 82.87
2019-02-26 12:30 | 123.33 | 87.19
2019-02-26 13:00 | 126.15 | 91.87
2019-02-26 13:30 | 123.84 | 87.68
2019-02-26 14:00 | 123.47 | 85.63
2019-02-26 14:30 | 125.94 | 87.67
2019-02-26 15:00 | 129.3 | 88.92
2019-02-26 15:30 | 127.84 | 87.57
2019-02-26 16:00 | 128.75 | 91.11
2019-02-26 16:30 | 125.33 | 87.73
2019-02-26 17:00 | 123.24 | 87.05
2019-02-26 17:30 | 127.01 | 96.52
2019-02-26 18:00 | 126.05 | 100.2
2019-02-26 18:30 | 128.38 | 106.03
2019-02-26 19:00 | 138.75 | 116.48
2019-02-26 19:30 | 146.05 | 123.97
2019-02-26 20:00 | 143.59 | 121.46
2019-02-26 20:30 | 142.12 | 118.54
2019-02-26 21:00 | 138.11 | 115.79
2019-02-26 21:30 | 136.44 | 113.62
2019-02-26 22:00 | 138.33 | 116.34
2019-02-26 22:30 | 141.1 | 117.44
2019-02-26 23:00 | 135.02 | 110.58
2019-02-26 23:30 | 130 | 106.58
2019-02-27 | 129.41 | 106.34
2019-02-27 00:30 | 130.27 | 108.35
2019-02-27 01:00 | 121.1 | 99.94
2019-02-27 01:30 | 125.81 | 104.9
2019-02-27 02:00 | 133.35 | 111.88
2019-02-27 02:30 | 130.31 | 108.01
2019-02-27 03:00 | 131.36 | 108.73
2019-02-27 03:30 | 124.32 | 101.43
2019-02-27 04:00 | 125.62 | 103.12
2019-02-27 04:30 | 131.39 | 109.52
2019-02-27 05:00 | 125.92 | 103.59
2019-02-27 05:30 | 127 | 104.28
2019-02-27 06:00 | 128.77 | 108.06
2019-02-27 06:30 | 115.99 | 95.12
2019-02-27 07:00 | 116.73 | 94.8
2019-02-27 07:30 | 120.53 | 90.86
2019-02-27 08:00 | 116.52 | 78.55
2019-02-27 08:30 | 119.3 | 74.97
2019-02-27 09:00 | 118.34 | 76.44
2019-02-27 09:30 | 117.61 | 79.26
2019-02-27 10:00 | 117.74 | 77.51
2019-02-27 10:30 | 120.62 | 77.75
2019-02-27 11:00 | 116.21 | 74.27
2019-02-27 11:30 | 113.89 | 73.31
2019-02-27 12:00 | 117.66 | 76.85
2019-02-27 12:30 | 119.63 | 81.69
2019-02-27 13:00 | 125.72 | 84.86
2019-02-27 13:30 | 123.99 | 84.3
2019-02-27 14:00 | 126.04 | 91.34
2019-02-27 14:30 | 125.21 | 85.67
2019-02-27 15:00 | 131.38 | 90.53
2019-02-27 15:30 | 128.5 | 89.53
2019-02-27 16:00 | 126.5 | 84.5
2019-02-27 16:30 | 132.43 | 92.5
2019-02-27 17:00 | 125.91 | 87.22
2019-02-27 17:30 | 130.75 | 95.54
2019-02-27 18:00 | 127.55 | 99.68
2019-02-27 18:30 | 124.95 | 100.66
2019-02-27 19:00 | 126.05 | 102.7
2019-02-27 19:30 | 128.12 | 104.47
2019-02-27 20:00 | 132.91 | 110.92
2019-02-27 20:30 | 127.97 | 104.99
2019-02-27 21:00 | 127.55 | 104.54
2019-02-27 21:30 | 128.24 | 103.73
2019-02-27 22:00 | 124.88 | 100.72
2019-02-27 22:30 | 125.81 | 100.73
2019-02-27 23:00 | 125.22 | 100.62
2019-02-27 23:30 | 127.98 | 105.79
2019-02-28 | 127.39 | 105.22
2019-02-28 00:30 | 134.66 | 112.25
2019-02-28 01:00 | 129.37 | 106.86
2019-02-28 01:30 | 128.46 | 104.5
2019-02-28 02:00 | 131.38 | 108.43
2019-02-28 02:30 | 128.63 | 104.12
2019-02-28 03:00 | 131.25 | 106.87
2019-02-28 03:30 | 124.98 | 100.3
2019-02-28 04:00 | 129.65 | 105.37
2019-02-28 04:30 | 133.57 | 108.47
2019-02-28 05:00 | 131.19 | 106.29
2019-02-28 05:30 | 125.1 | 99.83
2019-02-28 06:00 | 139.36 | 114.86
2019-02-28 06:30 | 130.04 | 104.73
2019-02-28 07:00 | 126.13 | 97.11
2019-02-28 07:30 | 129.3 | 99.08
2019-02-28 08:00 | 124.9 | 89.75
2019-02-28 08:30 | 128.04 | 94.03
2019-02-28 09:00 | 118.76 | 72.2
2019-02-28 09:30 | 123.96 | 80.51
2019-02-28 10:00 | 128.73 | 84.21
2019-02-28 10:30 | 137.51 | 91.89
2019-02-28 11:00 | 134.36 | 88.64
2019-02-28 11:30 | 120.53 | 74.37
2019-02-28 12:00 | 125 | 80.59
2019-02-28 12:30 | 123.12 | 84.07
2019-02-28 13:00 | 130.77 | 94.67
2019-02-28 13:30 | 142.43 | 103.18
2019-02-28 14:00 | 139.38 | 94.55
2019-02-28 14:30 | 127.87 | 81.36
2019-02-28 15:00 | 118.65 | 75.09
2019-02-28 15:30 | 127.77 | 78.87
2019-02-28 16:00 | 134.93 | 93.59
2019-02-28 16:30 | 129.93 | 90.26
2019-02-28 17:00 | 135.19 | 93.99
2019-02-28 17:30 | 138.57 | 103.55
2019-02-28 18:00 | 135.35 | 106.65
2019-02-28 18:30 | 127.24 | 99.53
2019-02-28 19:00 | 136.96 | 111.56
2019-02-28 19:30 | 139.78 | 113.64
2019-02-28 20:00 | 141.65 | 113.16
2019-02-28 20:30 | 139.35 | 110.32
2019-02-28 21:00 | 137.48 | 109.31
2019-02-28 21:30 | 134.7 | 105.46
2019-02-28 22:00 | 138.95 | 111.66
2019-02-28 22:30 | 144.8 | 117.25
2019-02-28 23:00 | 148.94 | 121.08
2019-02-28 23:30 | 145.25 | 117.15
2019-03-01 | 140.67 | 112.46
2019-03-01 00:30 | 143.06 | 114.55
2019-03-01 01:00 | 141.17 | 112.65
2019-03-01 01:30 | 134.37 | 107.15
2019-03-01 02:00 | 140.24 | 113.69
2019-03-01 02:30 | 135.7 | 106.64
2019-03-01 03:00 | 137.06 | 107.11
2019-03-01 03:30 | 135.95 | 105.94
2019-03-01 04:00 | 139.49 | 110.9
2019-03-01 04:30 | 139 | 110.42
2019-03-01 05:00 | 139.45 | 113.04
2019-03-01 05:30 | 139.19 | 112.43
2019-03-01 06:00 | 133.61 | 103.74
2019-03-01 06:30 | 122.93 | 92.61
2019-03-01 07:00 | 120.8 | 87.14
2019-03-01 07:30 | 122.89 | 84.18
2019-03-01 08:00 | 117.38 | 71.89
2019-03-01 08:30 | 116.44 | 72.44
2019-03-01 09:00 | 117.92 | 71.66
2019-03-01 09:30 | 129 | 82.62
2019-03-01 10:00 | 128.84 | 80.88
2019-03-01 10:30 | 121.35 | 74.22
2019-03-01 11:00 | 118.95 | 71.83
2019-03-01 11:30 | 121.58 | 77.53
2019-03-01 12:00 | 119.04 | 73.32
2019-03-01 12:30 | 121.45 | 79.64
2019-03-01 13:00 | 124.7 | 87.49
2019-03-01 13:30 | 121.58 | 81.77
2019-03-01 14:00 | 129.19 | 90.93
2019-03-01 14:30 | 131.24 | 95.6
2019-03-01 15:00 | 126.57 | 89.11
2019-03-01 15:30 | 132.04 | 92.64
2019-03-01 16:00 | 130.26 | 92.89
2019-03-01 16:30 | 127.67 | 87.46
2019-03-01 17:00 | 128.89 | 91.46
2019-03-01 17:30 | 142.59 | 112.24
2019-03-01 18:00 | 143.94 | 116.44
2019-03-01 18:30 | 138.98 | 111.91
2019-03-01 19:00 | 144.02 | 116.36
2019-03-01 19:30 | 145.17 | 117.35
2019-03-01 20:00 | 144.48 | 117.89
2019-03-01 20:30 | 151.99 | 125.2
2019-03-01 21:00 | 149.61 | 122.58
2019-03-01 21:30 | 148.74 | 121.35
2019-03-01 22:00 | 150 | 122.23
2019-03-01 22:30 | 140.01 | 111.57
2019-03-01 23:00 | 144.83 | 117.25
2019-03-01 23:30 | 146.13 | 118.75
2019-03-02 | 127.61 | 98.84
2019-03-02 00:30 | 136.82 | 109.51
2019-03-02 01:00 | 131.31 | 102.7
2019-03-02 01:30 | 137.82 | 109.2
2019-03-02 02:00 | 139.23 | 111.56
2019-03-02 02:30 | 139.91 | 111.63
2019-03-02 03:00 | 145.13 | 117.09
2019-03-02 03:30 | 140.05 | 111.37
2019-03-02 04:00 | 143.98 | 115.35
2019-03-02 04:30 | 146.86 | 118.08
2019-03-02 05:00 | 134.15 | 104.52
2019-03-02 05:30 | 139.47 | 111.55
2019-03-02 06:00 | 134.21 | 104.65
2019-03-02 06:30 | 128.86 | 99.52
2019-03-02 07:00 | 134.79 | 105.76
2019-03-02 07:30 | 125.9 | 93.74
2019-03-02 08:00 | 126.77 | 89.5
2019-03-02 08:30 | 125.13 | 81.84
2019-03-02 09:00 | 131.54 | 87.17
2019-03-02 09:30 | 131.43 | 88.03
2019-03-02 10:00 | 132.66 | 89.34
2019-03-02 10:30 | 136.68 | 95.77
2019-03-02 11:00 | 137.7 | 95.9
2019-03-02 11:30 | 129.72 | 87.09
2019-03-02 12:00 | 129.35 | 83.56
2019-03-02 12:30 | 134.69 | 96.4
2019-03-02 13:00 | 125.3 | 83.7
2019-03-02 13:30 | 126.4 | 87.18
2019-03-02 14:00 | 127.58 | 89.28
2019-03-02 14:30 | 126.6 | 85.03
2019-03-02 15:00 | 122.9 | 84.76
2019-03-02 15:30 | 122.17 | 76.76
2019-03-02 16:00 | 128.23 | 90.46
2019-03-02 16:30 | 134.78 | 99.54
2019-03-02 17:00 | 126.57 | 96.04
2019-03-02 17:30 | 129.97 | 98.38
2019-03-02 18:00 | 136.64 | 110.17
2019-03-02 18:30 | 131.9 | 105.03
2019-03-02 19:00 | 141.14 | 113.87
2019-03-02 19:30 | 146.72 | 119.44
2019-03-02 20:00 | 143.7 | 118.08
2019-03-02 20:30 | 138.57 | 112.93
2019-03-02 21:00 | 134.66 | 109.62
2019-03-02 21:30 | 128.7 | 104.56
2019-03-02 22:00 | 125.97 | 102.39
2019-03-02 22:30 | 123.46 | 99.77
2019-03-02 23:00 | 127.23 | 103.2
2019-03-02 23:30 | 123.22 | 99.35
2019-03-03 | 125.29 | 99.26
2019-03-03 00:30 | 129.81 | 102.78
2019-03-03 01:00 | 128.64 | 101.37
2019-03-03 01:30 | 128.44 | 101.64
2019-03-03 02:00 | 131.82 | 106.74
2019-03-03 02:30 | 129.17 | 103.22
2019-03-03 03:00 | 132.96 | 107.46
2019-03-03 03:30 | 137.01 | 111.95
2019-03-03 04:00 | 138 | 112.78
2019-03-03 04:30 | 139.96 | 115.11
2019-03-03 05:00 | 137.55 | 111.79
2019-03-03 05:30 | 133.59 | 108.22
2019-03-03 06:00 | 135.71 | 110.95
2019-03-03 06:30 | 127.04 | 103.16
2019-03-03 07:00 | 129.31 | 102.32
2019-03-03 07:30 | 128.44 | 94.01
2019-03-03 08:00 | 129.28 | 86.97
2019-03-03 08:30 | 123.56 | 75.4
2019-03-03 09:00 | 135.12 | 87.89
2019-03-03 09:30 | 132.45 | 84.96
2019-03-03 10:00 | 124.18 | 72.88
2019-03-03 10:30 | 129.58 | 83.1
2019-03-03 11:00 | 123.8 | 78.93
2019-03-03 11:30 | 135.23 | 94.07
2019-03-03 12:00 | 131.87 | 88.62
2019-03-03 12:30 | 134.89 | 92.53
2019-03-03 13:00 | 132.66 | 91.54
2019-03-03 13:30 | 120.37 | 80.52
2019-03-03 14:00 | 132.12 | 92.32
2019-03-03 14:30 | 129.03 | 94.47
2019-03-03 15:00 | 131.56 | 98.64
2019-03-03 15:30 | 126.91 | 94.12
2019-03-03 16:00 | 126.89 | 93.56
2019-03-03 16:30 | 127.8 | 96.3
2019-03-03 17:00 | 126.54 | 93.85
2019-03-03 17:30 | 130.49 | 100.7
2019-03-03 18:00 | 132.72 | 106.87
2019-03-03 18:30 | 132.23 | 108.38
2019-03-03 19:00 | 132.73 | 108.14
2019-03-03 19:30 | 138.36 | 114.53
2019-03-03 20:00 | 140.12 | 115.62
2019-03-03 20:30 | 138.61 | 115.29
2019-03-03 21:00 | 134.89 | 110.46
2019-03-03 21:30 | 137.75 | 114.96
2019-03-03 22:00 | 132.59 | 108.39
2019-03-03 22:30 | 130.28 | 105.78
2019-03-03 23:00 | 125.16 | 99.66
2019-03-03 23:30 | 128.97 | 104.71
2019-03-04 | 126.39 | 101.43
2019-03-04 00:30 | 127.18 | 102.6
2019-03-04 01:00 | 133.53 | 109.79
2019-03-04 01:30 | 138.08 | 114.68
2019-03-04 02:00 | 140.46 | 117.35
2019-03-04 02:30 | 135.24 | 112.46
2019-03-04 03:00 | 128.12 | 104.6
2019-03-04 03:30 | 128.72 | 104.84
2019-03-04 04:00 | 126.14 | 103.16
2019-03-04 04:30 | 127.68 | 106.3
2019-03-04 05:00 | 122.39 | 101
2019-03-04 05:30 | 129.11 | 106.57
2019-03-04 06:00 | 111.09 | 85.44
2019-03-04 06:30 | 103.72 | 78.86
2019-03-04 07:00 | 95.97 | 70.51
2019-03-04 07:30 | 92.68 | 62.93
2019-03-04 08:00 | 92.81 | 54.24
2019-03-04 08:30 | 99.84 | 55.75
2019-03-04 09:00 | 102.63 | 57.6
2019-03-04 09:30 | 107.68 | 65.49
2019-03-04 10:00 | 102.81 | 62.56
2019-03-04 10:30 | 108.55 | 64.9
2019-03-04 11:00 | 110.49 | 68.16
2019-03-04 11:30 | 113.1 | 75.69
2019-03-04 12:00 | 111.11 | 70.47
2019-03-04 12:30 | 110.32 | 69.32
2019-03-04 13:00 | 109.61 | 76.06
2019-03-04 13:30 | 112.42 | 77.01
2019-03-04 14:00 | 119.51 | 88.99
2019-03-04 14:30 | 120.08 | 85.03
2019-03-04 15:00 | 114.24 | 85.59
2019-03-04 15:30 | 115.42 | 86.66
2019-03-04 16:00 | 113.32 | 85.09
2019-03-04 16:30 | 113.73 | 88.38
2019-03-04 17:00 | 113.12 | 83.81
2019-03-04 17:30 | 122.21 | 100.08
2019-03-04 18:00 | 113.67 | 90.66
2019-03-04 18:30 | 112.82 | 94.05
2019-03-04 19:00 | 121.27 | 102.76
2019-03-04 19:30 | 132.69 | 112.87
2019-03-04 20:00 | 130.89 | 110.01
2019-03-04 20:30 | 130.14 | 108.2
2019-03-04 21:00 | 129.79 | 108.67
2019-03-04 21:30 | 128.41 | 107.54
2019-03-04 22:00 | 127.04 | 105.43
2019-03-04 22:30 | 120.65 | 99.43
2019-03-04 23:00 | 119.45 | 97.99
2019-03-04 23:30 | 117.07 | 96.13
2019-03-05 | 113.77 | 92.55
2019-03-05 00:30 | 119.32 | 98.98
2019-03-05 01:00 | 117.33 | 97.58
2019-03-05 01:30 | 116.91 | 96.83
2019-03-05 02:00 | 119.78 | 98.19
2019-03-05 02:30 | 110.71 | 87.54
2019-03-05 03:00 | 108.17 | 84.2
2019-03-05 03:30 | 110.02 | 86.31
2019-03-05 04:00 | 117.35 | 95.15
2019-03-05 04:30 | 116.17 | 93.24
2019-03-05 05:00 | 111.54 | 88.48
2019-03-05 05:30 | 121.12 | 97.99
2019-03-05 06:00 | 117.76 | 94.53
2019-03-05 06:30 | 118.48 | 96
2019-03-05 07:00 | 116.26 | 91.46
2019-03-05 07:30 | 116.12 | 87.37
2019-03-05 08:00 | 113.7 | 75.13
2019-03-05 08:30 | 114.4 | 70.26
2019-03-05 09:00 | 108.92 | 63.16
2019-03-05 09:30 | 107.04 | 57.52
2019-03-05 10:00 | 110.47 | 61.11
2019-03-05 10:30 | 112.41 | 64.82
2019-03-05 11:00 | 115.64 | 65.79
2019-03-05 11:30 | 116.43 | 68.38
2019-03-05 12:00 | 120.16 | 74.76
2019-03-05 12:30 | 119 | 74.22
2019-03-05 13:00 | 124.12 | 77.63
2019-03-05 13:30 | 125.81 | 81.8
2019-03-05 14:00 | 126.99 | 85.07
2019-03-05 14:30 | 128.4 | 94.55
2019-03-05 15:00 | 125.92 | 92.14
2019-03-05 15:30 | 117.58 | 86.23
2019-03-05 16:00 | 117.16 | 86.92
2019-03-05 16:30 | 126.18 | 92.67
2019-03-05 17:00 | 123.67 | 93.88
2019-03-05 17:30 | 120.74 | 89.73
2019-03-05 18:00 | 120.17 | 91.33
2019-03-05 18:30 | 113.28 | 86.54
2019-03-05 19:00 | 119.82 | 92.46
2019-03-05 19:30 | 126.46 | 101.43
2019-03-05 20:00 | 127.3 | 102.35
2019-03-05 20:30 | 132.51 | 108.91
2019-03-05 21:00 | 122.31 | 98.2
2019-03-05 21:30 | 118.7 | 94.28
2019-03-05 22:00 | 117.72 | 93.42
2019-03-05 22:30 | 119.41 | 93.07
2019-03-05 23:00 | 121.21 | 95.41
2019-03-05 23:30 | 116.55 | 89.4
2019-03-06 | 124.01 | 99.73
2019-03-06 00:30 | 122.87 | 97.26
2019-03-06 01:00 | 121.65 | 96.08
2019-03-06 01:30 | 113.48 | 87
2019-03-06 02:00 | 116.72 | 89.23
2019-03-06 02:30 | 119.17 | 92.84
2019-03-06 03:00 | 115.91 | 89.47
2019-03-06 03:30 | 118.38 | 91.65
2019-03-06 04:00 | 116.59 | 89.36
2019-03-06 04:30 | 119.31 | 91.88
2019-03-06 05:00 | 127.27 | 101.4
2019-03-06 05:30 | 121.08 | 93.59
2019-03-06 06:00 | 120.01 | 92.08
2019-03-06 06:30 | 113.12 | 85.55
2019-03-06 07:00 | 116.44 | 87.95
2019-03-06 07:30 | 114.84 | 85.01
2019-03-06 08:00 | 119.56 | 90.79
2019-03-06 08:30 | 120.3 | 90.38
2019-03-06 09:00 | 109.98 | 74.19
2019-03-06 09:30 | 118.68 | 87.81
2019-03-06 10:00 | 117.63 | 78.53
2019-03-06 10:30 | 121.82 | 77.18
2019-03-06 11:00 | 126.35 | 84.96
2019-03-06 11:30 | 117.82 | 76.16
2019-03-06 12:00 | 118.28 | 72.78
2019-03-06 12:30 | 114.79 | 77.85
2019-03-06 13:00 | 119.08 | 89.29
2019-03-06 13:30 | 118.12 | 84.94
2019-03-06 14:00 | 117.38 | 79.45
2019-03-06 14:30 | 119.66 | 82.84
2019-03-06 15:00 | 107.83 | 72.04
2019-03-06 15:30 | 105.87 | 67.67
2019-03-06 16:00 | 103.54 | 68.6
2019-03-06 16:30 | 113.66 | 84.31
2019-03-06 17:00 | 110.1 | 74.49
2019-03-06 17:30 | 111.83 | 84.02
2019-03-06 18:00 | 114.31 | 88.76
2019-03-06 18:30 | 111.32 | 89.7
2019-03-06 19:00 | 124.44 | 103.73
2019-03-06 19:30 | 122.17 | 101.23
2019-03-06 20:00 | 127.61 | 106.82
2019-03-06 20:30 | 122.4 | 99.41
2019-03-06 21:00 | 126.89 | 105
2019-03-06 21:30 | 127.53 | 104.94
2019-03-06 22:00 | 125.99 | 103.95
2019-03-06 22:30 | 124.39 | 101.89
2019-03-06 23:00 | 123.01 | 99.94
2019-03-06 23:30 | 130.08 | 108.19
2019-03-07 | 128.25 | 103.69
2019-03-07 00:30 | 124.47 | 99.12
2019-03-07 01:00 | 116.27 | 90.43
2019-03-07 01:30 | 128.19 | 104.91
2019-03-07 02:00 | 126.84 | 104.5
2019-03-07 02:30 | 123.45 | 99.9
2019-03-07 03:00 | 128.79 | 105.38
2019-03-07 03:30 | 118.11 | 93.95
2019-03-07 04:00 | 119.87 | 95.38
2019-03-07 04:30 | 117.97 | 94.35
2019-03-07 05:00 | 118.89 | 94.79
2019-03-07 05:30 | 120.56 | 97.67
2019-03-07 06:00 | 125.24 | 103.02
2019-03-07 06:30 | 112.63 | 89.54
2019-03-07 07:00 | 119.76 | 94.08
2019-03-07 07:30 | 109.3 | 84.37
2019-03-07 08:00 | 105.55 | 83.73
2019-03-07 08:30 | 100.63 | 78.29
2019-03-07 09:00 | 108.61 | 86.08
2019-03-07 09:30 | 118.13 | 97.87
2019-03-07 10:00 | 118.96 | 96.63
2019-03-07 10:30 | 119.53 | 96.6
2019-03-07 11:00 | 124.04 | 101.37
2019-03-07 11:30 | 117.58 | 96.98
2019-03-07 12:00 | 117.5 | 96.81
2019-03-07 12:30 | 121.95 | 100.6
2019-03-07 13:00 | 123.22 | 101.72
2019-03-07 13:30 | 109.95 | 82.69
2019-03-07 14:00 | 119.8 | 97.25
2019-03-07 14:30 | 117.77 | 95.72
2019-03-07 15:00 | 124.11 | 95.77
2019-03-07 15:30 | 114.73 | 74.41
2019-03-07 16:00 | 112.75 | 73.96
2019-03-07 16:30 | 113.64 | 78.12
2019-03-07 17:00 | 119.43 | 90.01
2019-03-07 17:30 | 119 | 88.46
2019-03-07 18:00 | 121.84 | 99.24
2019-03-07 18:30 | 123.98 | 105.67
2019-03-07 19:00 | 127.57 | 107.57
2019-03-07 19:30 | 135.37 | 115.1
2019-03-07 20:00 | 132.05 | 110.07
2019-03-07 20:30 | 132.61 | 111.35
2019-03-07 21:00 | 136.75 | 114.76
2019-03-07 21:30 | 130.83 | 108.93
2019-03-07 22:00 | 119.86 | 97.94
2019-03-07 22:30 | 128.21 | 104.04
2019-03-07 23:00 | 125.64 | 101.14
2019-03-07 23:30 | 114.97 | 94.24
2019-03-08 | 113.41 | 92.12
2019-03-08 00:30 | 118.38 | 94.04
2019-03-08 01:00 | 122.46 | 97.42
2019-03-08 01:30 | 125.36 | 100.33
2019-03-08 02:00 | 128.57 | 104.1
2019-03-08 02:30 | 128.7 | 104.2
2019-03-08 03:00 | 125.96 | 102.06
2019-03-08 03:30 | 120.08 | 94.99
2019-03-08 04:00 | 123.04 | 99.22
2019-03-08 04:30 | 126.81 | 103.57
2019-03-08 05:00 | 128.17 | 104.82
2019-03-08 05:30 | 121.57 | 97.04
2019-03-08 06:00 | 117.45 | 91.19
2019-03-08 06:30 | 111.23 | 83.81
2019-03-08 07:00 | 112.37 | 85.33
2019-03-08 07:30 | 123.29 | 95.93
2019-03-08 08:00 | 114.67 | 84.22
2019-03-08 08:30 | 117.5 | 88.22
2019-03-08 09:00 | 119.81 | 92.15
2019-03-08 09:30 | 124.39 | 94.16
2019-03-08 10:00 | 123.36 | 94.64
2019-03-08 10:30 | 121.27 | 89.06
2019-03-08 11:00 | 119.33 | 84.09
2019-03-08 11:30 | 114.95 | 82.29
2019-03-08 12:00 | 115.55 | 78.7
2019-03-08 12:30 | 119.65 | 82
2019-03-08 13:00 | 118.39 | 83.61
2019-03-08 13:30 | 117.54 | 86.48
2019-03-08 14:00 | 118.41 | 83.08
2019-03-08 14:30 | 118.23 | 83.21
2019-03-08 15:00 | 114.05 | 76.18
2019-03-08 15:30 | 114.68 | 84.26
2019-03-08 16:00 | 120.59 | 94.05
2019-03-08 16:30 | 115.9 | 89.66
2019-03-08 17:00 | 113.77 | 87.87
2019-03-08 17:30 | 101.05 | 79.87
2019-03-08 18:00 | 101.96 | 79.56
2019-03-08 18:30 | 98.43 | 77.11
2019-03-08 19:00 | 112.93 | 91.32
2019-03-08 19:30 | 124.59 | 103.79
2019-03-08 20:00 | 121.64 | 100.13
2019-03-08 20:30 | 128.96 | 106.66
2019-03-08 21:00 | 132.25 | 108.08
2019-03-08 21:30 | 131.4 | 106.64
2019-03-08 22:00 | 122.87 | 97.77
2019-03-08 22:30 | 124.8 | 101.99
2019-03-08 23:00 | 117.39 | 94.24
2019-03-08 23:30 | 113.91 | 89.05
2019-03-09 | 119.89 | 94.77
2019-03-09 00:30 | 118.91 | 93.24
2019-03-09 01:00 | 127.83 | 100.7
2019-03-09 01:30 | 133.79 | 105.81
2019-03-09 02:00 | 130.04 | 99.91
2019-03-09 02:30 | 121.08 | 91.6
2019-03-09 03:00 | 121.37 | 96.61
2019-03-09 03:30 | 126.39 | 100.69
2019-03-09 04:00 | 127.59 | 100.27
2019-03-09 04:30 | 138.15 | 110.73
2019-03-09 05:00 | 130.02 | 104.25
2019-03-09 05:30 | 132.94 | 106.51
2019-03-09 06:00 | 132.01 | 106.92
2019-03-09 06:30 | 132.41 | 107.52
2019-03-09 07:00 | 131.11 | 101.95
2019-03-09 07:30 | 126.83 | 93.69
2019-03-09 08:00 | 125.26 | 86.79
2019-03-09 08:30 | 121.64 | 89.84
2019-03-09 09:00 | 125.65 | 88.97
2019-03-09 09:30 | 125.98 | 89.11
2019-03-09 10:00 | 112.9 | 70.85
2019-03-09 10:30 | 120.99 | 87.74
2019-03-09 11:00 | 122.51 | 92.07
2019-03-09 11:30 | 116.24 | 86.61
2019-03-09 12:00 | 114.06 | 82.33
2019-03-09 12:30 | 107.99 | 73.2
2019-03-09 13:00 | 106.79 | 74.01
2019-03-09 13:30 | 101.55 | 68.75
2019-03-09 14:00 | 101.68 | 67.9
2019-03-09 14:30 | 106.62 | 74.84
2019-03-09 15:00 | 120.56 | 84.24
2019-03-09 15:30 | 116.75 | 73.93
2019-03-09 16:00 | 124.96 | 83.02
2019-03-09 16:30 | 121.75 | 79.35
2019-03-09 17:00 | 118.24 | 79.65
2019-03-09 17:30 | 128.65 | 101.03
2019-03-09 18:00 | 130.9 | 104.37
2019-03-09 18:30 | 128.05 | 103.23
2019-03-09 19:00 | 140.79 | 115.06
2019-03-09 19:30 | 139.96 | 112.93
2019-03-09 20:00 | 135.75 | 107.18
2019-03-09 20:30 | 133.7 | 105.21
2019-03-09 21:00 | 132.59 | 107.6
2019-03-09 21:30 | 123.97 | 99.52
2019-03-09 22:00 | 120.36 | 98.25
2019-03-09 22:30 | 118.52 | 95.56
2019-03-09 23:00 | 112.8 | 87.48
2019-03-09 23:30 | 122.1 | 93.94
2019-03-10 | 130.07 | 102.63
2019-03-10 00:30 | 131.76 | 104.42
2019-03-10 01:00 | 129.85 | 102.83
2019-03-10 01:30 | 130.04 | 103.75
2019-03-10 02:00 | 127.87 | 101.59
2019-03-10 02:30 | 124.62 | 97.28
2019-03-10 03:00 | 123.22 | 95.61
2019-03-10 03:30 | 114.68 | 86.12
2019-03-10 04:00 | 119.62 | 93.03
2019-03-10 04:30 | 122.78 | 97.61
2019-03-10 05:00 | 121.72 | 96.36
2019-03-10 05:30 | 122.32 | 96.59
2019-03-10 06:00 | 119.45 | 93.21
2019-03-10 06:30 | 124.29 | 97.92
2019-03-10 07:00 | 117.56 | 87.03
2019-03-10 07:30 | 121.04 | 85.09
2019-03-10 08:00 | 130.26 | 88.56
2019-03-10 08:30 | 127.43 | 81.24
2019-03-10 09:00 | 131.37 | 84.66
2019-03-10 09:30 | 123.1 | 73.29
2019-03-10 10:00 | 127.29 | 78.07
2019-03-10 10:30 | 126.44 | 79.89
2019-03-10 11:00 | 127.32 | 77.19
2019-03-10 11:30 | 127.13 | 76.4
2019-03-10 12:00 | 136 | 88.26
2019-03-10 12:30 | 133.29 | 86.31
2019-03-10 13:00 | 137.29 | 90.22
2019-03-10 13:30 | 138.14 | 90.87
2019-03-10 14:00 | 136.08 | 90.78
2019-03-10 14:30 | 140.76 | 95.25
2019-03-10 15:00 | 140.14 | 93.8
2019-03-10 15:30 | 136.8 | 88.84
2019-03-10 16:00 | 134.46 | 85.19
2019-03-10 16:30 | 140.23 | 93.73
2019-03-10 17:00 | 139.13 | 96.67
2019-03-10 17:30 | 143.99 | 107.02
2019-03-10 18:00 | 138.41 | 105.95
2019-03-10 18:30 | 141.84 | 112.69
2019-03-10 19:00 | 155.29 | 125.89
2019-03-10 19:30 | 154.58 | 125.75
2019-03-10 20:00 | 150.56 | 120.79
2019-03-10 20:30 | 142.32 | 112.63
2019-03-10 21:00 | 142.89 | 113.49
2019-03-10 21:30 | 140.49 | 111.41
2019-03-10 22:00 | 135.68 | 105.98
2019-03-10 22:30 | 143.82 | 114.06
2019-03-10 23:00 | 142.69 | 111.62
2019-03-10 23:30 | 126.39 | 94.16
2019-03-11 | 131.62 | 100.32
2019-03-11 00:30 | 134.18 | 104.27
2019-03-11 01:00 | 130.68 | 99.72
2019-03-11 01:30 | 133.51 | 102.31
2019-03-11 02:00 | 130.55 | 99.78
2019-03-11 02:30 | 132.05 | 102.31
2019-03-11 03:00 | 129.68 | 100.31
2019-03-11 03:30 | 124.3 | 94.65
2019-03-11 04:00 | 125.93 | 95.22
2019-03-11 04:30 | 124.61 | 94.48
2019-03-11 05:00 | 123.23 | 93.13
2019-03-11 05:30 | 126.33 | 96.66
2019-03-11 06:00 | 124.02 | 92.95
2019-03-11 06:30 | 118 | 86.41
2019-03-11 07:00 | 122.44 | 88.94
2019-03-11 07:30 | 124.13 | 86.57
2019-03-11 08:00 | 121.16 | 83.65
2019-03-11 08:30 | 121.06 | 72.84
2019-03-11 09:00 | 121.6 | 67.94
2019-03-11 09:30 | 119.02 | 67.93
2019-03-11 10:00 | 122.56 | 70.83
2019-03-11 10:30 | 122.73 | 70.21
2019-03-11 11:00 | 125.47 | 71.97
2019-03-11 11:30 | 126.09 | 72.94
2019-03-11 12:00 | 126.44 | 73.45
2019-03-11 12:30 | 125.78 | 72.69
2019-03-11 13:00 | 127.72 | 75.77
2019-03-11 13:30 | 125.05 | 75.62
2019-03-11 14:00 | 117.91 | 68.57
2019-03-11 14:30 | 118.65 | 67.46
2019-03-11 15:00 | 121.02 | 83.41
2019-03-11 15:30 | 124.11 | 81.43
2019-03-11 16:00 | 126.4 | 82.33
2019-03-11 16:30 | 125.44 | 86.19
2019-03-11 17:00 | 124.51 | 90.46
2019-03-11 17:30 | 125.79 | 93.36
2019-03-11 18:00 | 117.56 | 94.14
2019-03-11 18:30 | 115.67 | 92.22
2019-03-11 19:00 | 123.12 | 101.24
2019-03-11 19:30 | 118.48 | 96.91
2019-03-11 20:00 | 115.76 | 94.44
2019-03-11 20:30 | 111.98 | 90.49
2019-03-11 21:00 | 109.69 | 88.38
2019-03-11 21:30 | 120.72 | 97.18
2019-03-11 22:00 | 120.85 | 95.94
2019-03-11 22:30 | 120.33 | 94.95
2019-03-11 23:00 | 113.09 | 89.83
2019-03-11 23:30 | 120.22 | 95.38
2019-03-12 | 122.16 | 97.15
2019-03-12 00:30 | 123.16 | 97.74
2019-03-12 01:00 | 123.07 | 97.95
2019-03-12 01:30 | 119.94 | 93.51
2019-03-12 02:00 | 120.34 | 93.96
2019-03-12 02:30 | 111.47 | 89.36
2019-03-12 03:00 | 108 | 86.58
2019-03-12 03:30 | 103.13 | 81.52
2019-03-12 04:00 | 103.83 | 81.9
2019-03-12 04:30 | 102.69 | 81.16
2019-03-12 05:00 | 102.91 | 81.93
2019-03-12 05:30 | 103.98 | 83.85
2019-03-12 06:00 | 104.91 | 84.87
2019-03-12 06:30 | 102.15 | 83.23
2019-03-12 07:00 | 101.39 | 81.03
2019-03-12 07:30 | 95.35 | 72.39
2019-03-12 08:00 | 96.95 | 70.33
2019-03-12 08:30 | 89.46 | 57.84
2019-03-12 09:00 | 92.67 | 55.38
2019-03-12 09:30 | 94.73 | 55.39
2019-03-12 10:00 | 98.66 | 60.7
2019-03-12 10:30 | 98.72 | 61.68
2019-03-12 11:00 | 99 | 74.43
2019-03-12 11:30 | 99.5 | 66.3
2019-03-12 12:00 | 100.14 | 63.57
2019-03-12 12:30 | 103.28 | 69.54
2019-03-12 13:00 | 99.92 | 68.16
2019-03-12 13:30 | 102.51 | 71.34
2019-03-12 14:00 | 113.41 | 92.5
2019-03-12 14:30 | 112.68 | 94.05
2019-03-12 15:00 | 104.91 | 83.86
2019-03-12 15:30 | 100.68 | 77.7
2019-03-12 16:00 | 102.1 | 69.12
2019-03-12 16:30 | 104.57 | 82.55
2019-03-12 17:00 | 98.02 | 80.51
2019-03-12 17:30 | 94.34 | 79.05
2019-03-12 18:00 | 92.44 | 77.4
2019-03-12 18:30 | 89.55 | 73.44
2019-03-12 19:00 | 99.27 | 83.06
2019-03-12 19:30 | 105.32 | 89.57
2019-03-12 20:00 | 103.27 | 87.2
2019-03-12 20:30 | 102.34 | 85.67
2019-03-12 21:00 | 103.26 | 87.18
2019-03-12 21:30 | 99.2 | 83.21
2019-03-12 22:00 | 104.59 | 87.66
2019-03-12 22:30 | 103.57 | 87.28
2019-03-12 23:00 | 104.13 | 86.99
2019-03-12 23:30 | 105.01 | 86.75
2019-03-13 | 106.39 | 88.31
2019-03-13 00:30 | 107.16 | 88.77
2019-03-13 01:00 | 105.88 | 87.17
2019-03-13 01:30 | 102.57 | 84.21
2019-03-13 02:00 | 99.8 | 82.01
2019-03-13 02:30 | 101.22 | 83.42
2019-03-13 03:00 | 93.93 | 75.49
2019-03-13 03:30 | 91.85 | 72.73
2019-03-13 04:00 | 95.77 | 77.81
2019-03-13 04:30 | 96.24 | 77.64
2019-03-13 05:00 | 98.54 | 79.49
2019-03-13 05:30 | 96.98 | 78.61
2019-03-13 06:00 | 94.86 | 76.38
2019-03-13 06:30 | 86.91 | 68.08
2019-03-13 07:00 | 86.47 | 63.81
2019-03-13 07:30 | 85.79 | 59.42
2019-03-13 08:00 | 83.91 | 52.64
2019-03-13 08:30 | 88.66 | 56.48
2019-03-13 09:00 | 82.57 | 46.05
2019-03-13 09:30 | 86.65 | 51.62
2019-03-13 10:00 | 93.12 | 58.57
2019-03-13 10:30 | 90.17 | 52.3
2019-03-13 11:00 | 81.66 | 42.62
2019-03-13 11:30 | 83.15 | 44.32
2019-03-13 12:00 | 87.68 | 50.5
2019-03-13 12:30 | 87.48 | 51.09
2019-03-13 13:00 | 84.2 | 45.85
2019-03-13 13:30 | 79.25 | 42.06
2019-03-13 14:00 | 81.21 | 45.46
2019-03-13 14:30 | 82.06 | 48.52
2019-03-13 15:00 | 80.69 | 44.44
2019-03-13 15:30 | 80.23 | 54.25
2019-03-13 16:00 | 79.55 | 53.3
2019-03-13 16:30 | 83.95 | 55.44
2019-03-13 17:00 | 87.82 | 71.47
2019-03-13 17:30 | 80.86 | 64.95
2019-03-13 18:00 | 80.84 | 64.35
2019-03-13 18:30 | 86.01 | 69.97
2019-03-13 19:00 | 96.4 | 81.46
2019-03-13 19:30 | 105.23 | 90.98
2019-03-13 20:00 | 103.79 | 89.56
2019-03-13 20:30 | 107.44 | 91.88
2019-03-13 21:00 | 103.87 | 87.37
2019-03-13 21:30 | 110.12 | 91.44
2019-03-13 22:00 | 120.69 | 99.11
2019-03-13 22:30 | 124.24 | 100.77
2019-03-13 23:00 | 130.58 | 105.73
2019-03-13 23:30 | 127.9 | 105.55
2019-03-14 | 121.73 | 99.8
2019-03-14 00:30 | 125.6 | 103.39
2019-03-14 01:00 | 128.26 | 106.2
2019-03-14 01:30 | 115.86 | 92.24
2019-03-14 02:00 | 112.36 | 88.25
2019-03-14 02:30 | 118.64 | 95.99
2019-03-14 03:00 | 119.48 | 96.71
2019-03-14 03:30 | 115.71 | 92.08
2019-03-14 04:00 | 120.85 | 98.08
2019-03-14 04:30 | 122.69 | 100.6
2019-03-14 05:00 | 132.18 | 110.64
2019-03-14 05:30 | 125.28 | 104.6
2019-03-14 06:00 | 121.39 | 98.84
2019-03-14 06:30 | 110.68 | 88.45
2019-03-14 07:00 | 114.19 | 90.73
2019-03-14 07:30 | 114.42 | 86.24
2019-03-14 08:00 | 114.14 | 75.97
2019-03-14 08:30 | 118.92 | 79.06
2019-03-14 09:00 | 115.15 | 76.57
2019-03-14 09:30 | 117.98 | 76.5
2019-03-14 10:00 | 113.78 | 69.44
2019-03-14 10:30 | 114.28 | 69.63
2019-03-14 11:00 | 122.94 | 80.66
2019-03-14 11:30 | 117.04 | 72.37
2019-03-14 12:00 | 112.75 | 68.66
2019-03-14 12:30 | 110.97 | 68.92
2019-03-14 13:00 | 112.87 | 72.93
2019-03-14 13:30 | 106.51 | 74.99
2019-03-14 14:00 | 104.09 | 74.52
2019-03-14 14:30 | 100.1 | 75.1
2019-03-14 15:00 | 101.12 | 79.13
2019-03-14 15:30 | 98.07 | 77.27
2019-03-14 16:00 | 96.4 | 76.48
2019-03-14 16:30 | 101.72 | 78.72
2019-03-14 17:00 | 110.98 | 77.32
2019-03-14 17:30 | 114.76 | 86.18
2019-03-14 18:00 | 119.98 | 95.47
2019-03-14 18:30 | 122.44 | 99.69
2019-03-14 19:00 | 131.32 | 108.68
2019-03-14 19:30 | 132.53 | 110.51
2019-03-14 20:00 | 126.81 | 104.29
2019-03-14 20:30 | 112.9 | 90.6
2019-03-14 21:00 | 118.68 | 95.14
2019-03-14 21:30 | 122.6 | 99.49
2019-03-14 22:00 | 128.37 | 103.67
2019-03-14 22:30 | 126.11 | 99
2019-03-14 23:00 | 121.89 | 95.46
2019-03-14 23:30 | 125.5 | 100.1
2019-03-15 | 132.96 | 107.95
2019-03-15 00:30 | 125.5 | 98.88
2019-03-15 01:00 | 131.25 | 105.23
2019-03-15 01:30 | 136.31 | 111.23
2019-03-15 02:00 | 124.9 | 98.27
2019-03-15 02:30 | 123.77 | 98.57
2019-03-15 03:00 | 132.25 | 107.01
2019-03-15 03:30 | 122.84 | 97.01
2019-03-15 04:00 | 131.56 | 107.45
2019-03-15 04:30 | 128.43 | 105.59
2019-03-15 05:00 | 136.5 | 113.21
2019-03-15 05:30 | 124.5 | 102.84
2019-03-15 06:00 | 108.44 | 88.32
2019-03-15 06:30 | 118.09 | 98.35
2019-03-15 07:00 | 122.84 | 101.43
2019-03-15 07:30 | 123.38 | 99.03
2019-03-15 08:00 | 123.37 | 93.62
2019-03-15 08:30 | 120.72 | 83.09
2019-03-15 09:00 | 119.57 | 77.56
2019-03-15 09:30 | 122.43 | 84.02
2019-03-15 10:00 | 123.27 | 93.17
2019-03-15 10:30 | 116.72 | 80.82
2019-03-15 11:00 | 121.95 | 87.89
2019-03-15 11:30 | 119.74 | 80.67
2019-03-15 12:00 | 121.85 | 87.11
2019-03-15 12:30 | 118.97 | 82.52
2019-03-15 13:00 | 121.51 | 86.7
2019-03-15 13:30 | 123.83 | 95.96
2019-03-15 14:00 | 122.27 | 96.24
2019-03-15 14:30 | 116.43 | 90.61
2019-03-15 15:00 | 110.18 | 81.09
2019-03-15 15:30 | 120.48 | 91.38
2019-03-15 16:00 | 125.05 | 81.53
2019-03-15 16:30 | 122.83 | 91.07
2019-03-15 17:00 | 119.12 | 93.27
2019-03-15 17:30 | 120.79 | 95.94
2019-03-15 18:00 | 119.89 | 95.94
2019-03-15 18:30 | 118.94 | 94.98
2019-03-15 19:00 | 126.31 | 103.51
2019-03-15 19:30 | 132.36 | 110.11
2019-03-15 20:00 | 129.42 | 106.38
2019-03-15 20:30 | 119.47 | 95.72
2019-03-15 21:00 | 112.98 | 88.85
2019-03-15 21:30 | 74.48 | 38.78
2019-03-15 22:00 | 65.7 | 20.66
2019-03-15 22:30 | 56.9 | 23.8
2019-03-15 23:00 | 58.13 | 25.77
2019-03-15 23:30 | 57.14 | 21.62
2019-03-16 | 60.77 | 26.14
2019-03-16 00:30 | 68.36 | 41.64
2019-03-16 01:00 | 69.28 | 41.4
2019-03-16 01:30 | 71.39 | 45.23
2019-03-16 02:00 | 70.12 | 45.73
2019-03-16 02:30 | 73.91 | 54.08
2019-03-16 03:00 | 71.72 | 50.24
2019-03-16 03:30 | 73.23 | 53.36
2019-03-16 04:00 | 74.86 | 55.13
2019-03-16 04:30 | 76.41 | 56.91
2019-03-16 05:00 | 73.63 | 54.16
2019-03-16 05:30 | 76.68 | 57.57
2019-03-16 06:00 | 84.67 | 66.96
2019-03-16 06:30 | 79.71 | 60.63
2019-03-16 07:00 | 78.66 | 58.33
2019-03-16 07:30 | 84.93 | 65.97
2019-03-16 08:00 | 78.29 | 57.38
2019-03-16 08:30 | 75.28 | 52.93
2019-03-16 09:00 | 81.95 | 61.92
2019-03-16 09:30 | 84.16 | 64.18
2019-03-16 10:00 | 88.18 | 69.04
2019-03-16 10:30 | 80.73 | 59.76
2019-03-16 11:00 | 79.99 | 58.86
2019-03-16 11:30 | 76.44 | 53.57
2019-03-16 12:00 | 83.6 | 51.05
2019-03-16 12:30 | 99.23 | 71.08
2019-03-16 13:00 | 84.31 | 53.77
2019-03-16 13:30 | 85.57 | 56.14
2019-03-16 14:00 | 84.43 | 47.84
2019-03-16 14:30 | 96.51 | 54.85
2019-03-16 15:00 | 94.26 | 55.78
2019-03-16 15:30 | 93.92 | 65.81
2019-03-16 16:00 | 84.28 | 61.11
2019-03-16 16:30 | 87.46 | 65.64
2019-03-16 17:00 | 88.51 | 63.97
2019-03-16 17:30 | 92.34 | 67.59
2019-03-16 18:00 | 91.93 | 67.83
2019-03-16 18:30 | 94.46 | 72.11
2019-03-16 19:00 | 94.69 | 71.26
2019-03-16 19:30 | 98.21 | 76.37
2019-03-16 20:00 | 102.54 | 81.17
2019-03-16 20:30 | 97.47 | 76.36
2019-03-16 21:00 | 102.29 | 80.48
2019-03-16 21:30 | 98.15 | 76.76
2019-03-16 22:00 | 103.44 | 82.54
2019-03-16 22:30 | 96.63 | 76.02
2019-03-16 23:00 | 100.04 | 79.08
2019-03-16 23:30 | 108.61 | 88.02
2019-03-17 | 103.43 | 82.74
2019-03-17 00:30 | 102.07 | 79.82
2019-03-17 01:00 | 105.75 | 85.5
2019-03-17 01:30 | 103.9 | 82.75
2019-03-17 02:00 | 112.05 | 90.31
2019-03-17 02:30 | 109.93 | 88.37
2019-03-17 03:00 | 110.34 | 88.84
2019-03-17 03:30 | 104.23 | 82.09
2019-03-17 04:00 | 110.32 | 89.07
2019-03-17 04:30 | 106.84 | 87.74
2019-03-17 05:00 | 98.38 | 79.73
2019-03-17 05:30 | 101.47 | 82.62
2019-03-17 06:00 | 101.17 | 82.07
2019-03-17 06:30 | 96.63 | 78.59
2019-03-17 07:00 | 96.42 | 77.03
2019-03-17 07:30 | 104.7 | 81.72
2019-03-17 08:00 | 102.1 | 77.75
2019-03-17 08:30 | 110.61 | 84.17
2019-03-17 09:00 | 107.79 | 76.3
2019-03-17 09:30 | 113.99 | 82.49
2019-03-17 10:00 | 116.95 | 85.66
2019-03-17 10:30 | 123.02 | 93.2
2019-03-17 11:00 | 116.14 | 74.88
2019-03-17 11:30 | 120.63 | 76.51
2019-03-17 12:00 | 120.75 | 76.97
2019-03-17 12:30 | 125.8 | 87.53
2019-03-17 13:00 | 124.91 | 85.64
2019-03-17 13:30 | 124.56 | 85.79
2019-03-17 14:00 | 134.65 | 102.3
2019-03-17 14:30 | 132.38 | 98.6
2019-03-17 15:00 | 137.95 | 97.26
2019-03-17 15:30 | 134.57 | 96.96
2019-03-17 16:00 | 129.4 | 87.08
2019-03-17 16:30 | 130.41 | 88.99
2019-03-17 17:00 | 122.28 | 84.5
2019-03-17 17:30 | 133.23 | 106.51
2019-03-17 18:00 | 140.99 | 116.99
2019-03-17 18:30 | 135.7 | 110.82
2019-03-17 19:00 | 135.2 | 109.37
2019-03-17 19:30 | 135.22 | 110.54
2019-03-17 20:00 | 133.89 | 108.39
2019-03-17 20:30 | 127.62 | 101.28
2019-03-17 21:00 | 130.56 | 104.81
2019-03-17 21:30 | 129 | 102.65
2019-03-17 22:00 | 124.08 | 99.34
2019-03-17 22:30 | 129.75 | 104.37
2019-03-17 23:00 | 134.62 | 109.95
2019-03-17 23:30 | 125.68 | 103.15
2019-03-18 | 121.08 | 97.5
2019-03-18 00:30 | 123.08 | 98.45
2019-03-18 01:00 | 127.79 | 103.81
2019-03-18 01:30 | 128.47 | 105.02
2019-03-18 02:00 | 122.22 | 101.4
2019-03-18 02:30 | 135.44 | 114.25
2019-03-18 03:00 | 127.47 | 106.31
2019-03-18 03:30 | 127 | 105.76
2019-03-18 04:00 | 122.88 | 99.97
2019-03-18 04:30 | 123.82 | 100.51
2019-03-18 05:00 | 113.87 | 88.7
2019-03-18 05:30 | 119.43 | 95.84
2019-03-18 06:00 | 121.03 | 98.47
2019-03-18 06:30 | 120.45 | 97.49
2019-03-18 07:00 | 116.96 | 90.88
2019-03-18 07:30 | 119.24 | 88.69
2019-03-18 08:00 | 124 | 86.28
2019-03-18 08:30 | 123.68 | 81.98
2019-03-18 09:00 | 124.05 | 78.78
2019-03-18 09:30 | 115.18 | 68.32
2019-03-18 10:00 | 118.38 | 72.64
2019-03-18 10:30 | 120.75 | 77.32
2019-03-18 11:00 | 121.14 | 75.66
2019-03-18 11:30 | 116.38 | 72.85
2019-03-18 12:00 | 109.68 | 65.98
2019-03-18 12:30 | 100.7 | 61.86
2019-03-18 13:00 | 105.37 | 64.86
2019-03-18 13:30 | 113.85 | 69.32
2019-03-18 14:00 | 116.72 | 81.78
2019-03-18 14:30 | 123.19 | 80.82
2019-03-18 15:00 | 118.78 | 77.07
2019-03-18 15:30 | 122.37 | 79.84
2019-03-18 16:00 | 131.48 | 94.47
2019-03-18 16:30 | 123.43 | 88.57
2019-03-18 17:00 | 133.09 | 106.41
2019-03-18 17:30 | 135.63 | 112.07
2019-03-18 18:00 | 134.41 | 110.95
2019-03-18 18:30 | 130.13 | 106.34
2019-03-18 19:00 | 133.73 | 108.39
2019-03-18 19:30 | 139.35 | 114.77
2019-03-18 20:00 | 139.62 | 114.56
2019-03-18 20:30 | 137.03 | 111.57
2019-03-18 21:00 | 117.47 | 99.06
2019-03-18 21:30 | 111.12 | 93.24
2019-03-18 22:00 | 111.63 | 93.66
2019-03-18 22:30 | 109.96 | 93.63
2019-03-18 23:00 | 118.5 | 102.31
2019-03-18 23:30 | 112.47 | 94.15
2019-03-19 | 119.16 | 99.68
2019-03-19 00:30 | 124.04 | 104.3
2019-03-19 01:00 | 120.45 | 99.17
2019-03-19 01:30 | 121.19 | 100.6
2019-03-19 02:00 | 123.99 | 102.7
2019-03-19 02:30 | 123.22 | 101.24
2019-03-19 03:00 | 116.91 | 94.73
2019-03-19 03:30 | 118.45 | 97.1
2019-03-19 04:00 | 123.15 | 101.54
2019-03-19 04:30 | 122.84 | 101.73
2019-03-19 05:00 | 118.63 | 97.46
2019-03-19 05:30 | 118.48 | 96.35
2019-03-19 06:00 | 116.17 | 93.35
2019-03-19 06:30 | 120.92 | 98.57
2019-03-19 07:00 | 114.18 | 90.28
2019-03-19 07:30 | 114.97 | 87.09
2019-03-19 08:00 | 114.11 | 86.06
2019-03-19 08:30 | 108.31 | 83.9
2019-03-19 09:00 | 106.85 | 82.55
2019-03-19 09:30 | 109.76 | 83.85
2019-03-19 10:00 | 113.49 | 88.12
2019-03-19 10:30 | 101.65 | 78.94
2019-03-19 11:00 | 90.71 | 73.83
2019-03-19 11:30 | 100.17 | 81.14
2019-03-19 12:00 | 103.62 | 81.56
2019-03-19 12:30 | 108.75 | 80.71
2019-03-19 13:00 | 106.28 | 69.44
2019-03-19 13:30 | 115.27 | 79.77
2019-03-19 14:00 | 112.64 | 69.69
2019-03-19 14:30 | 114.41 | 71.78
2019-03-19 15:00 | 117.95 | 77.32
2019-03-19 15:30 | 125.37 | 84.3
2019-03-19 16:00 | 121.6 | 77.86
2019-03-19 16:30 | 122.56 | 83.22
2019-03-19 17:00 | 115.3 | 84.78
2019-03-19 17:30 | 96.53 | 74.02
2019-03-19 18:00 | 103.92 | 82.9
2019-03-19 18:30 | 105.48 | 82.34
2019-03-19 19:00 | 116.4 | 91.96
2019-03-19 19:30 | 123.44 | 101.39
2019-03-19 20:00 | 129.62 | 106.23
2019-03-19 20:30 | 122.75 | 100.32
2019-03-19 21:00 | 125.19 | 103.19
2019-03-19 21:30 | 117.85 | 95.67
2019-03-19 22:00 | 116.27 | 94.58
2019-03-19 22:30 | 116.71 | 94.37
2019-03-19 23:00 | 119.63 | 97.2
2019-03-19 23:30 | 124.94 | 103.55
2019-03-20 | 120.16 | 98.49
2019-03-20 00:30 | 126.05 | 104.77
2019-03-20 01:00 | 128.56 | 108.62
2019-03-20 01:30 | 130.42 | 109.82
2019-03-20 02:00 | 107.91 | 91.15
2019-03-20 02:30 | 105.72 | 89.88
2019-03-20 03:00 | 106.52 | 87.38
2019-03-20 03:30 | 112.74 | 92.45
2019-03-20 04:00 | 104.65 | 87
2019-03-20 04:30 | 112.38 | 94.57
2019-03-20 05:00 | 115.12 | 95.64
2019-03-20 05:30 | 110.52 | 90.14
2019-03-20 06:00 | 106.69 | 85.75
2019-03-20 06:30 | 102.57 | 81.35
2019-03-20 07:00 | 102.94 | 78.04
2019-03-20 07:30 | 113.72 | 86.43
2019-03-20 08:00 | 113.7 | 79.69
2019-03-20 08:30 | 118.1 | 80.49
2019-03-20 09:00 | 109.57 | 67.15
2019-03-20 09:30 | 117.27 | 74.58
2019-03-20 10:00 | 118.3 | 76.6
2019-03-20 10:30 | 117.16 | 73.44
2019-03-20 11:00 | 117.88 | 77.68
2019-03-20 11:30 | 116.09 | 73.49
2019-03-20 12:00 | 119.07 | 80.51
2019-03-20 12:30 | 110.08 | 76.61
2019-03-20 13:00 | 111.39 | 88.8
2019-03-20 13:30 | 108.87 | 88.46
2019-03-20 14:00 | 107.3 | 85.87
2019-03-20 14:30 | 113.44 | 91.67
2019-03-20 15:00 | 113.59 | 84.95
2019-03-20 15:30 | 113.46 | 80.29
2019-03-20 16:00 | 115.2 | 85.37
2019-03-20 16:30 | 111.82 | 85.25
2019-03-20 17:00 | 108.44 | 88.3
2019-03-20 17:30 | 110.82 | 87.44
2019-03-20 18:00 | 106.29 | 86.67
2019-03-20 18:30 | 107.34 | 88.16
2019-03-20 19:00 | 114.78 | 97.14
2019-03-20 19:30 | 106.33 | 89.19
2019-03-20 20:00 | 104.64 | 88.44
2019-03-20 20:30 | 109.02 | 91.57
2019-03-20 21:00 | 114.72 | 96.26
2019-03-20 21:30 | 113.28 | 95.19
2019-03-20 22:00 | 108.05 | 89.97
2019-03-20 22:30 | 114 | 95.22
2019-03-20 23:00 | 111.33 | 92.02
2019-03-20 23:30 | 105.86 | 85.24
2019-03-21 | 104.72 | 84.38
2019-03-21 00:30 | 111.83 | 91.53
2019-03-21 01:00 | 112.3 | 93.54
2019-03-21 01:30 | 113.77 | 95.28
2019-03-21 02:00 | 119.42 | 101.19
2019-03-21 02:30 | 119.57 | 102.09
2019-03-21 03:00 | 117.46 | 99.59
2019-03-21 03:30 | 111.82 | 94.4
2019-03-21 04:00 | 113.67 | 96.27
2019-03-21 04:30 | 116.66 | 98.87
2019-03-21 05:00 | 114.56 | 97.02
2019-03-21 05:30 | 116.84 | 97.35
2019-03-21 06:00 | 119.87 | 99.06
2019-03-21 06:30 | 108.47 | 88.11
2019-03-21 07:00 | 111.74 | 90.04
2019-03-21 07:30 | 112.14 | 87.84
2019-03-21 08:00 | 116.78 | 85.76
2019-03-21 08:30 | 113.05 | 71.83
2019-03-21 09:00 | 109.72 | 66.89
2019-03-21 09:30 | 108.34 | 63.78
2019-03-21 10:00 | 107.22 | 61.5
2019-03-21 10:30 | 106.53 | 59.73
2019-03-21 11:00 | 111.15 | 63.75
2019-03-21 11:30 | 107.88 | 59.4
2019-03-21 12:00 | 107 | 62.54
2019-03-21 12:30 | 117.01 | 73.29
2019-03-21 13:00 | 118.55 | 79.5
2019-03-21 13:30 | 113.69 | 70.49
2019-03-21 14:00 | 115.83 | 74.45
2019-03-21 14:30 | 121.54 | 80.89
2019-03-21 15:00 | 116.96 | 76.85
2019-03-21 15:30 | 114.7 | 75.18
2019-03-21 16:00 | 113.37 | 77.38
2019-03-21 16:30 | 112.92 | 76.11
2019-03-21 17:00 | 121.05 | 90.41
2019-03-21 17:30 | 126.07 | 100.25
2019-03-21 18:00 | 123.58 | 102.33
2019-03-21 18:30 | 122.48 | 100.46
2019-03-21 19:00 | 141.39 | 121.16
2019-03-21 19:30 | 134.01 | 112.53
2019-03-21 20:00 | 134.59 | 112.19
2019-03-21 20:30 | 123.43 | 99.76
2019-03-21 21:00 | 126.64 | 102.95
2019-03-21 21:30 | 117.45 | 94.78
2019-03-21 22:00 | 117.37 | 95.58
2019-03-21 22:30 | 118.23 | 95.5
2019-03-21 23:00 | 119.78 | 98
2019-03-21 23:30 | 120.36 | 98.9
2019-03-22 | 128.96 | 108.85
2019-03-22 00:30 | 123.26 | 102.26
2019-03-22 01:00 | 121.76 | 100.95
2019-03-22 01:30 | 122.82 | 102.27
2019-03-22 02:00 | 123.25 | 102.3
2019-03-22 02:30 | 122.46 | 101.93
2019-03-22 03:00 | 126.61 | 106.16
2019-03-22 03:30 | 130.26 | 109.2
2019-03-22 04:00 | 133.71 | 112.48
2019-03-22 04:30 | 136.77 | 115.03
2019-03-22 05:00 | 129.52 | 108.18
2019-03-22 05:30 | 127.73 | 104.82
2019-03-22 06:00 | 129.19 | 104.98
2019-03-22 06:30 | 117.75 | 93.36
2019-03-22 07:00 | 126.42 | 100
2019-03-22 07:30 | 131.85 | 103.56
2019-03-22 08:00 | 130.72 | 95.71
2019-03-22 08:30 | 136.12 | 98.29
2019-03-22 09:00 | 133.49 | 93.98
2019-03-22 09:30 | 132.15 | 84.62
2019-03-22 10:00 | 143.74 | 100.91
2019-03-22 10:30 | 138.55 | 91.56
2019-03-22 11:00 | 136.23 | 88.71
2019-03-22 11:30 | 135.71 | 89.35
2019-03-22 12:00 | 132.64 | 84.04
2019-03-22 12:30 | 136.16 | 90.34
2019-03-22 13:00 | 136.29 | 91.13
2019-03-22 13:30 | 149.74 | 105.86
2019-03-22 14:00 | 140.67 | 98.37
2019-03-22 14:30 | 137.19 | 90.67
2019-03-22 15:00 | 139.06 | 94.17
2019-03-22 15:30 | 139.71 | 98.13
2019-03-22 16:00 | 138.82 | 99.55
2019-03-22 16:30 | 139.29 | 106.64
2019-03-22 17:00 | 141.93 | 110.87
2019-03-22 17:30 | 140.8 | 112.44
2019-03-22 18:00 | 146.96 | 119.93
2019-03-22 18:30 | 132.74 | 107.75
2019-03-22 19:00 | 147.74 | 123.06
2019-03-22 19:30 | 146.53 | 121.79
2019-03-22 20:00 | 146.44 | 122.16
2019-03-22 20:30 | 148 | 123.22
2019-03-22 21:00 | 143.59 | 118.36
2019-03-22 21:30 | 142.37 | 118.24
2019-03-22 22:00 | 141.08 | 118.1
2019-03-22 22:30 | 141.9 | 118.49
2019-03-22 23:00 | 137.75 | 113.9
2019-03-22 23:30 | 130.87 | 106.84
2019-03-23 | 128.92 | 104.71
2019-03-23 00:30 | 129.61 | 106.18
2019-03-23 01:00 | 135.46 | 112.14
2019-03-23 01:30 | 129.7 | 105.67
2019-03-23 02:00 | 130.83 | 107.11
2019-03-23 02:30 | 133.48 | 110.43
2019-03-23 03:00 | 140.5 | 117.86
2019-03-23 03:30 | 134.14 | 110.52
2019-03-23 04:00 | 137.39 | 113.43
2019-03-23 04:30 | 131.74 | 107.02
2019-03-23 05:00 | 128.7 | 104.33
2019-03-23 05:30 | 133.51 | 109.2
2019-03-23 06:00 | 132.27 | 108.32
2019-03-23 06:30 | 122.45 | 99
2019-03-23 07:00 | 130.35 | 105.76
2019-03-23 07:30 | 132.22 | 104.85
2019-03-23 08:00 | 123.57 | 87.92
2019-03-23 08:30 | 124.31 | 81.89
2019-03-23 09:00 | 125.49 | 86.17
2019-03-23 09:30 | 131.67 | 98.28
2019-03-23 10:00 | 131.63 | 90.43
2019-03-23 10:30 | 122.93 | 82.56
2019-03-23 11:00 | 116.14 | 76.8
2019-03-23 11:30 | 111.44 | 74.98
2019-03-23 12:00 | 116.65 | 78.07
2019-03-23 12:30 | 113.3 | 73.31
2019-03-23 13:00 | 122.69 | 82.58
2019-03-23 13:30 | 123.57 | 83.85
2019-03-23 14:00 | 126.19 | 85.63
2019-03-23 14:30 | 130.77 | 90.06
2019-03-23 15:00 | 130.66 | 91.22
2019-03-23 15:30 | 128.96 | 85.98
2019-03-23 16:00 | 135.09 | 94.03
2019-03-23 16:30 | 133.15 | 95.28
2019-03-23 17:00 | 129.29 | 96.26
2019-03-23 17:30 | 134.96 | 107.5
2019-03-23 18:00 | 138.6 | 115.34
2019-03-23 18:30 | 137.33 | 115.84
2019-03-23 19:00 | 135.51 | 113.65
2019-03-23 19:30 | 146.89 | 124.67
2019-03-23 20:00 | 140.41 | 117.82
2019-03-23 20:30 | 136.79 | 113.59
2019-03-23 21:00 | 133.2 | 109.58
2019-03-23 21:30 | 136.83 | 113.45
2019-03-23 22:00 | 124.28 | 100.9
2019-03-23 22:30 | 130.64 | 108.69
2019-03-23 23:00 | 125.08 | 103.02
2019-03-23 23:30 | 127.59 | 104.83
2019-03-24 | 122.2 | 101.86
2019-03-24 00:30 | 120.6 | 101.43
2019-03-24 01:00 | 122.05 | 102.54
2019-03-24 01:30 | 133.64 | 114.94
2019-03-24 02:00 | 123.28 | 103.29
2019-03-24 02:30 | 128.26 | 108.06
2019-03-24 03:00 | 117.89 | 97.77
2019-03-24 03:30 | 121.99 | 103.28
2019-03-24 04:00 | 123.51 | 104.55
2019-03-24 04:30 | 124.18 | 105.92
2019-03-24 05:00 | 124.97 | 107.53
2019-03-24 05:30 | 130.08 | 112.24
2019-03-24 06:00 | 122.16 | 103.48
2019-03-24 06:30 | 113.73 | 95.28
2019-03-24 07:00 | 118.94 | 98.3
2019-03-24 07:30 | 113.01 | 87.62
2019-03-24 08:00 | 116.31 | 83.66
2019-03-24 08:30 | 111.78 | 72.25
2019-03-24 09:00 | 114.09 | 75.18
2019-03-24 09:30 | 110.24 | 71.23
2019-03-24 10:00 | 117.28 | 79.86
2019-03-24 10:30 | 122.85 | 83.86
2019-03-24 11:00 | 122.69 | 83.43
2019-03-24 11:30 | 121.4 | 86.03
2019-03-24 12:00 | 129.63 | 94.7
2019-03-24 12:30 | 121.92 | 84.97
2019-03-24 13:00 | 131.26 | 98.53
2019-03-24 13:30 | 132.37 | 99.32
2019-03-24 14:00 | 126.58 | 93.97
2019-03-24 14:30 | 134.8 | 104.02
2019-03-24 15:00 | 127.4 | 94.87
2019-03-24 15:30 | 128.94 | 102.2
2019-03-24 16:00 | 122.51 | 96.03
2019-03-24 16:30 | 127.76 | 98.03
2019-03-24 17:00 | 128.86 | 108.95
2019-03-24 17:30 | 132.13 | 114.95
2019-03-24 18:00 | 133.86 | 118.05
2019-03-24 18:30 | 126.88 | 111.81
2019-03-24 19:00 | 139.28 | 123.17
2019-03-24 19:30 | 135.74 | 119.82
2019-03-24 20:00 | 130.57 | 114.59
2019-03-24 20:30 | 136.78 | 119.97
2019-03-24 21:00 | 129.22 | 113.29
2019-03-24 21:30 | 130.75 | 114.44
2019-03-24 22:00 | 126.02 | 109.8
2019-03-24 22:30 | 120.25 | 102.84
2019-03-24 23:00 | 128.31 | 111.26
2019-03-24 23:30 | 128.32 | 111.82
2019-03-25 | 118.02 | 100.04
2019-03-25 00:30 | 123.83 | 105.54
2019-03-25 01:00 | 127.11 | 109.7
2019-03-25 01:30 | 122.18 | 104.37
2019-03-25 02:00 | 131.52 | 113.41
2019-03-25 02:30 | 127.03 | 108.53
2019-03-25 03:00 | 127.12 | 107.83
2019-03-25 03:30 | 130.24 | 111.18
2019-03-25 04:00 | 125.1 | 105.25
2019-03-25 04:30 | 127.29 | 107.1
2019-03-25 05:00 | 128.29 | 108.26
2019-03-25 05:30 | 127.65 | 107.52
2019-03-25 06:00 | 128.88 | 108.5
2019-03-25 06:30 | 118.51 | 97.54
2019-03-25 07:00 | 119.53 | 95.97
2019-03-25 07:30 | 114.24 | 85.56
2019-03-25 08:00 | 117.37 | 84.61
2019-03-25 08:30 | 117.74 | 80.19
2019-03-25 09:00 | 116.58 | 76.64
2019-03-25 09:30 | 115.77 | 79.24
2019-03-25 10:00 | 112.22 | 77.43
2019-03-25 10:30 | 126.52 | 90.66
2019-03-25 11:00 | 132.18 | 96.39
2019-03-25 11:30 | 127.81 | 92.09
2019-03-25 12:00 | 127.37 | 91.98
2019-03-25 12:30 | 131.94 | 90.52
2019-03-25 13:00 | 134.56 | 89.61
2019-03-25 13:30 | 128.69 | 85.62
2019-03-25 14:00 | 127.06 | 86.77
2019-03-25 14:30 | 124.9 | 84.23
2019-03-25 15:00 | 125.12 | 89.01
2019-03-25 15:30 | 126.08 | 93.76
2019-03-25 16:00 | 120.54 | 90.37
2019-03-25 16:30 | 128.19 | 99.6
2019-03-25 17:00 | 127.74 | 103.62
2019-03-25 17:30 | 132.97 | 109.24
2019-03-25 18:00 | 140.77 | 119.32
2019-03-25 18:30 | 137.98 | 116.63
2019-03-25 19:00 | 142.15 | 121.47
2019-03-25 19:30 | 140.6 | 121.26
2019-03-25 20:00 | 134.87 | 116.91
2019-03-25 20:30 | 134.04 | 117.52
2019-03-25 21:00 | 133.93 | 117.04
2019-03-25 21:30 | 122.54 | 105
2019-03-25 22:00 | 121.93 | 103.5
2019-03-25 22:30 | 129.78 | 112.73
2019-03-25 23:00 | 120.92 | 102.85
2019-03-25 23:30 | 125.02 | 107.79
2019-03-26 | 120 | 101.97
2019-03-26 00:30 | 121.2 | 103.4
2019-03-26 01:00 | 129.83 | 113.15
2019-03-26 01:30 | 129.83 | 112.58
2019-03-26 02:00 | 128.01 | 110.01
2019-03-26 02:30 | 124.98 | 107.34
2019-03-26 03:00 | 139.86 | 120.76
2019-03-26 03:30 | 129.55 | 110.37
2019-03-26 04:00 | 128.65 | 109.02
2019-03-26 04:30 | 128.98 | 109.65
2019-03-26 05:00 | 125.25 | 105.73
2019-03-26 05:30 | 125.79 | 108.33
2019-03-26 06:00 | 119.76 | 101.19
2019-03-26 06:30 | 112.33 | 94.05
2019-03-26 07:00 | 101.46 | 81.65
2019-03-26 07:30 | 98.9 | 75.35
2019-03-26 08:00 | 102.72 | 79.6
2019-03-26 08:30 | 110.24 | 89.72
2019-03-26 09:00 | 112.77 | 87.89
2019-03-26 09:30 | 112.53 | 86.8
2019-03-26 10:00 | 111.05 | 86.36
2019-03-26 10:30 | 113.04 | 86.39
2019-03-26 11:00 | 107.13 | 79.4
2019-03-26 11:30 | 110.95 | 85.72
2019-03-26 12:00 | 111.8 | 87.42
2019-03-26 12:30 | 110.25 | 83.79
2019-03-26 13:00 | 109.78 | 86.97
2019-03-26 13:30 | 111.12 | 89.99
2019-03-26 14:00 | 113.99 | 93.22
2019-03-26 14:30 | 113.91 | 93.98
2019-03-26 15:00 | 113.31 | 93.44
2019-03-26 15:30 | 114.71 | 91.03
2019-03-26 16:00 | 123.77 | 106.24
2019-03-26 16:30 | 124.2 | 106.1
2019-03-26 17:00 | 122.76 | 104.94
2019-03-26 17:30 | 125.37 | 110.31
2019-03-26 18:00 | 127.53 | 113.29
2019-03-26 18:30 | 126.77 | 111.91
2019-03-26 19:00 | 130.42 | 115.38
2019-03-26 19:30 | 129.93 | 115.28
2019-03-26 20:00 | 124.05 | 108.31
2019-03-26 20:30 | 121.38 | 106.14
2019-03-26 21:00 | 120.61 | 105.25
2019-03-26 21:30 | 127.37 | 111.83
2019-03-26 22:00 | 123.8 | 108.85
2019-03-26 22:30 | 126.84 | 111.58
2019-03-26 23:00 | 131.56 | 114.4
2019-03-26 23:30 | 120.99 | 104.27
2019-03-27 | 119.7 | 103.29
2019-03-27 00:30 | 118.68 | 101.86
2019-03-27 01:00 | 118.78 | 102.04
2019-03-27 01:30 | 118.44 | 100.97
2019-03-27 02:00 | 119.21 | 101.96
2019-03-27 02:30 | 116.45 | 97.3
2019-03-27 03:00 | 116.8 | 98.18
2019-03-27 03:30 | 124.25 | 106.42
2019-03-27 04:00 | 117.45 | 99.49
2019-03-27 04:30 | 126.48 | 108.44
2019-03-27 05:00 | 124.46 | 106.95
2019-03-27 05:30 | 118.35 | 100.24
2019-03-27 06:00 | 114.95 | 95.42
2019-03-27 06:30 | 110.52 | 90.52
2019-03-27 07:00 | 112.95 | 91.31
2019-03-27 07:30 | 115.98 | 93.57
2019-03-27 08:00 | 115.29 | 92.46
2019-03-27 08:30 | 114.49 | 86.79
2019-03-27 09:00 | 125.91 | 93.15
2019-03-27 09:30 | 118 | 87.28
2019-03-27 10:00 | 115.56 | 87.65
2019-03-27 10:30 | 116.92 | 91.07
2019-03-27 11:00 | 109.2 | 82.26
2019-03-27 11:30 | 102.69 | 76.9
2019-03-27 12:00 | 109.81 | 85.06
2019-03-27 12:30 | 120.47 | 92.27
2019-03-27 13:00 | 115.36 | 87.03
2019-03-27 13:30 | 119.73 | 91.59
2019-03-27 14:00 | 122.96 | 96.28
2019-03-27 14:30 | 113.64 | 89.98
2019-03-27 15:00 | 109.97 | 90.02
2019-03-27 15:30 | 109.14 | 88.96
2019-03-27 16:00 | 122.86 | 105.3
2019-03-27 16:30 | 114.03 | 94.41
2019-03-27 17:00 | 116.83 | 98.03
2019-03-27 17:30 | 110.16 | 92.05
2019-03-27 18:00 | 115.74 | 98.44
2019-03-27 18:30 | 111.35 | 93.24
2019-03-27 19:00 | 110.01 | 93.37
2019-03-27 19:30 | 112.11 | 97.15
2019-03-27 20:00 | 106.97 | 91.72
2019-03-27 20:30 | 107.74 | 91.75
2019-03-27 21:00 | 110.29 | 94.41
2019-03-27 21:30 | 105.03 | 87.78
2019-03-27 22:00 | 103.56 | 85.75
2019-03-27 22:30 | 102.44 | 84.34
2019-03-27 23:00 | 99.42 | 78.01
2019-03-27 23:30 | 98.71 | 77.28
2019-03-28 | 101.33 | 80.09
2019-03-28 00:30 | 102.55 | 80.32
2019-03-28 01:00 | 94.22 | 71.41
2019-03-28 01:30 | 99.4 | 76.54
2019-03-28 02:00 | 100.39 | 77.81
2019-03-28 02:30 | 102.37 | 80.84
2019-03-28 03:00 | 108.4 | 87.58
2019-03-28 03:30 | 107.85 | 84.7
2019-03-28 04:00 | 108.96 | 87.21
2019-03-28 04:30 | 107.09 | 85.16
2019-03-28 05:00 | 102.23 | 79.37
2019-03-28 05:30 | 113.02 | 90.06
2019-03-28 06:00 | 115.41 | 93.35
2019-03-28 06:30 | 111.4 | 89.88
2019-03-28 07:00 | 104.79 | 85.97
2019-03-28 07:30 | 104.91 | 84.5
2019-03-28 08:00 | 103.62 | 84.26
2019-03-28 08:30 | 102.55 | 82.07
2019-03-28 09:00 | 97.61 | 76.62
2019-03-28 09:30 | 102.49 | 79.2
2019-03-28 10:00 | 112.89 | 89.19
2019-03-28 10:30 | 106.04 | 78.93
2019-03-28 11:00 | 109.43 | 84.57
2019-03-28 11:30 | 108.33 | 82.14
2019-03-28 12:00 | 117.42 | 93.07
2019-03-28 12:30 | 118.15 | 91.44
2019-03-28 13:00 | 106.01 | 79.41
2019-03-28 13:30 | 107.02 | 82.13
2019-03-28 14:00 | 111.8 | 85.45
2019-03-28 14:30 | 114.6 | 91.02
2019-03-28 15:00 | 110.65 | 87.17
2019-03-28 15:30 | 108.42 | 85.6
2019-03-28 16:00 | 111.4 | 87.12
2019-03-28 16:30 | 108.68 | 85.89
2019-03-28 17:00 | 111.95 | 89.49
2019-03-28 17:30 | 120.36 | 98.74
2019-03-28 18:00 | 124.5 | 102.81
2019-03-28 18:30 | 121.59 | 99.76
2019-03-28 19:00 | 112.71 | 90.69
2019-03-28 19:30 | 115.6 | 94.72
2019-03-28 20:00 | 112.35 | 91.21
2019-03-28 20:30 | 115.33 | 92.75
2019-03-28 21:00 | 114.19 | 93.18
2019-03-28 21:30 | 119.24 | 96.55
2019-03-28 22:00 | 114.37 | 91.74
2019-03-28 22:30 | 117.25 | 94.69
2019-03-28 23:00 | 116.55 | 93.43
2019-03-28 23:30 | 116.43 | 94.06
2019-03-29 | 117.43 | 95.2
2019-03-29 00:30 | 117.12 | 96.3
2019-03-29 01:00 | 113.95 | 94.2
2019-03-29 01:30 | 123.6 | 102.17
2019-03-29 02:00 | 121.77 | 99.45
2019-03-29 02:30 | 112.58 | 90.26
2019-03-29 03:00 | 118.87 | 96.62
2019-03-29 03:30 | 120.88 | 98.62
2019-03-29 04:00 | 120.05 | 96.74
2019-03-29 04:30 | 111.68 | 89.06
2019-03-29 05:00 | 121.91 | 100.95
2019-03-29 05:30 | 118.65 | 97.45
2019-03-29 06:00 | 123.44 | 101.72
2019-03-29 06:30 | 118.71 | 96.65
2019-03-29 07:00 | 117.92 | 95.04
2019-03-29 07:30 | 108.34 | 83.07
2019-03-29 08:00 | 115.87 | 91.72
2019-03-29 08:30 | 117.05 | 92.76
2019-03-29 09:00 | 119.78 | 95.3
2019-03-29 09:30 | 115.34 | 90.65
2019-03-29 10:00 | 114.92 | 91.04
2019-03-29 10:30 | 119.41 | 92.27
2019-03-29 11:00 | 110.03 | 79.16
2019-03-29 11:30 | 106.06 | 71.78
2019-03-29 12:00 | 114.05 | 81.41
2019-03-29 12:30 | 109.07 | 77.12
2019-03-29 13:00 | 116.1 | 80.49
2019-03-29 13:30 | 111.75 | 76.54
2019-03-29 14:00 | 107.84 | 71.63
2019-03-29 14:30 | 113.44 | 78.24
2019-03-29 15:00 | 113.18 | 77.2
2019-03-29 15:30 | 119.59 | 89.33
2019-03-29 16:00 | 121.71 | 92.18
2019-03-29 16:30 | 121.47 | 93.98
2019-03-29 17:00 | 119.12 | 92.25
2019-03-29 17:30 | 125.15 | 98.85
2019-03-29 18:00 | 132.92 | 108.99
2019-03-29 18:30 | 129.55 | 105.4
2019-03-29 19:00 | 128.15 | 102.86
2019-03-29 19:30 | 127.48 | 104.12
2019-03-29 20:00 | 130.08 | 107.06
2019-03-29 20:30 | 131.84 | 107.41
2019-03-29 21:00 | 123.76 | 98.01
2019-03-29 21:30 | 127.81 | 103.01
2019-03-29 22:00 | 134.3 | 111.12
2019-03-29 22:30 | 125.92 | 101.58
2019-03-29 23:00 | 125.38 | 100.97
2019-03-29 23:30 | 122.48 | 98.31
2019-03-30 | 131.34 | 106.29
2019-03-30 00:30 | 126.98 | 101.89
2019-03-30 01:00 | 127.07 | 102.94
2019-03-30 01:30 | 120.01 | 95.65
2019-03-30 02:00 | 119.83 | 95.16
2019-03-30 02:30 | 123.05 | 97.09
2019-03-30 03:00 | 119.14 | 93.88
2019-03-30 03:30 | 118.06 | 91.72
2019-03-30 04:00 | 117.85 | 92.33
2019-03-30 04:30 | 112.59 | 88.47
2019-03-30 05:00 | 116.88 | 92.63
2019-03-30 05:30 | 118.92 | 94.28
2019-03-30 06:00 | 119.85 | 94.21
2019-03-30 06:30 | 116.88 | 91.49
2019-03-30 07:00 | 119.86 | 94.61
2019-03-30 07:30 | 120.66 | 95.24
2019-03-30 08:00 | 124.74 | 96.68
2019-03-30 08:30 | 118.76 | 91.23
2019-03-30 09:00 | 109.75 | 82.28
2019-03-30 09:30 | 122.39 | 93.06
2019-03-30 10:00 | 117.78 | 87.8
2019-03-30 10:30 | 122.95 | 94.55
2019-03-30 11:00 | 120.92 | 91.85
2019-03-30 11:30 | 118.08 | 88.03
2019-03-30 12:00 | 124.48 | 96.8
2019-03-30 12:30 | 122.68 | 93.54
2019-03-30 13:00 | 122.38 | 91.54
2019-03-30 13:30 | 120.42 | 91.4
2019-03-30 14:00 | 120.01 | 91.46
2019-03-30 14:30 | 116.87 | 87.07
2019-03-30 15:00 | 117.01 | 87.09
2019-03-30 15:30 | 121.34 | 90.67
2019-03-30 16:00 | 124.17 | 88.97
2019-03-30 16:30 | 128.63 | 90.88
2019-03-30 17:00 | 129.5 | 96.98
2019-03-30 17:30 | 124.36 | 94.29
2019-03-30 18:00 | 126.28 | 100.73
2019-03-30 18:30 | 128.9 | 105.79
2019-03-30 19:00 | 127.09 | 104.15
2019-03-30 19:30 | 132.52 | 109.87
2019-03-30 20:00 | 131.68 | 108.91
2019-03-30 20:30 | 125.9 | 103.2
2019-03-30 21:00 | 125.64 | 104.27
2019-03-30 21:30 | 118.88 | 97.07
2019-03-30 22:00 | 118.79 | 96.15
2019-03-30 22:30 | 116.98 | 96.8
2019-03-30 23:00 | 120.25 | 97.61
2019-03-30 23:30 | 120.23 | 97.41
2019-03-31 | 129.96 | 104.42
2019-03-31 00:30 | 127.39 | 97.93
2019-03-31 01:00 | 125.38 | 95.2
2019-03-31 01:30 | 129.06 | 101.59
2019-03-31 02:00 | 133.95 | 108.95
2019-03-31 02:30 | 129.37 | 106.23
2019-03-31 03:00 | 125.67 | 101.38
2019-03-31 03:30 | 123.46 | 99.1
2019-03-31 04:00 | 114.59 | 91.04
2019-03-31 04:30 | 126.04 | 103.62
2019-03-31 05:00 | 121.68 | 97
2019-03-31 05:30 | 121.14 | 95.94
2019-03-31 06:00 | 112.34 | 85.03
2019-03-31 06:30 | 112.63 | 85.12
2019-03-31 07:00 | 111.65 | 83.47
2019-03-31 07:30 | 110.44 | 80.54
2019-03-31 08:00 | 106.87 | 65.97
2019-03-31 08:30 | 105.08 | 65.3
2019-03-31 09:00 | 112.07 | 79.94
2019-03-31 09:30 | 114.14 | 78.89
2019-03-31 10:00 | 113.55 | 68.47
2019-03-31 10:30 | 117.55 | 70.76
2019-03-31 11:00 | 116.21 | 71.1
2019-03-31 11:30 | 117.79 | 70.68
2019-03-31 12:00 | 121.97 | 72.7
2019-03-31 12:30 | 121.97 | 74.19
2019-03-31 13:00 | 120.26 | 70.39
2019-03-31 13:30 | 121.9 | 71.28
2019-03-31 14:00 | 124.89 | 77.51
2019-03-31 14:30 | 121.45 | 74.02
2019-03-31 15:00 | 124.5 | 78.1
2019-03-31 15:30 | 120.24 | 75.08
2019-03-31 16:00 | 128.92 | 84.03
2019-03-31 16:30 | 113.08 | 69.39
2019-03-31 17:00 | 115.6 | 78.98
2019-03-31 17:30 | 110.04 | 79.83
2019-03-31 18:00 | 123.61 | 98.5
2019-03-31 18:30 | 121.09 | 96.4
2019-03-31 19:00 | 126.36 | 103.5
2019-03-31 19:30 | 122.28 | 98.7
2019-03-31 20:00 | 123.4 | 102.16
2019-03-31 20:30 | 120.96 | 100.38
2019-03-31 21:00 | 128.62 | 108.63
2019-03-31 21:30 | 128.38 | 108.18
2019-03-31 22:00 | 117.4 | 97.81
2019-03-31 22:30 | 122.89 | 102.05
2019-03-31 23:00 | 124.97 | 104.48
2019-03-31 23:30 | 110.69 | 90.05
2019-04-01 | 110.18 | 88.91
2019-04-01 00:30 | 117.89 | 97.02
2019-04-01 01:00 | 117.26 | 96.88
2019-04-01 01:30 | 113.07 | 91.92
2019-04-01 02:00 | 110.14 | 89.71
2019-04-01 02:30 | 108.94 | 87.53
2019-04-01 03:00 | 104.97 | 85.25
2019-04-01 03:30 | 107.31 | 87.07
2019-04-01 04:00 | 111.94 | 92.45
2019-04-01 04:30 | 115.23 | 96.47
2019-04-01 05:00 | 108.9 | 89.03
2019-04-01 05:30 | 117.81 | 97.33
2019-04-01 06:00 | 105.64 | 84.81
2019-04-01 06:30 | 110.65 | 90.88
2019-04-01 07:00 | 107.12 | 82.87
2019-04-01 07:30 | 109.94 | 80.56
2019-04-01 08:00 | 105.33 | 67.65
2019-04-01 08:30 | 109.26 | 65.43
2019-04-01 09:00 | 108.32 | 63
2019-04-01 09:30 | 106.02 | 57.54
2019-04-01 10:00 | 110.24 | 60.36
2019-04-01 10:30 | 114.49 | 65.46
2019-04-01 11:00 | 115.7 | 66.9
2019-04-01 11:30 | 115.54 | 68.7
2019-04-01 12:00 | 113.53 | 68.8
2019-04-01 12:30 | 109.35 | 61.42
2019-04-01 13:00 | 109.92 | 61.36
2019-04-01 13:30 | 113.8 | 66.87
2019-04-01 14:00 | 115.65 | 69.57
2019-04-01 14:30 | 119.3 | 74.11
2019-04-01 15:00 | 116.66 | 72.38
2019-04-01 15:30 | 119.9 | 73.73
2019-04-01 16:00 | 117.32 | 70.38
2019-04-01 16:30 | 116.44 | 74.9
2019-04-01 17:00 | 106.72 | 71.73
2019-04-01 17:30 | 115.46 | 87.53
2019-04-01 18:00 | 122.91 | 98.25
2019-04-01 18:30 | 123.17 | 99.52
2019-04-01 19:00 | 125.53 | 102.06
2019-04-01 19:30 | 123.12 | 100.64
2019-04-01 20:00 | 119.4 | 99.27
2019-04-01 20:30 | 119.93 | 100.95
2019-04-01 21:00 | 121.47 | 99.5
2019-04-01 21:30 | 124.67 | 101.77
2019-04-01 22:00 | 124.17 | 102.65
2019-04-01 22:30 | 128.9 | 107.06
2019-04-01 23:00 | 123.41 | 101.68
2019-04-01 23:30 | 118.03 | 95.12
2019-04-02 | 122.02 | 99.55
2019-04-02 00:30 | 123.25 | 100.39
2019-04-02 01:00 | 122.25 | 98.53
2019-04-02 01:30 | 124.54 | 102.05
2019-04-02 02:00 | 122.01 | 99.01
2019-04-02 02:30 | 120.05 | 97.34
2019-04-02 03:00 | 124.13 | 102.32
2019-04-02 03:30 | 116.05 | 93.48
2019-04-02 04:00 | 120.02 | 98.06
2019-04-02 04:30 | 119.51 | 96.37
2019-04-02 05:00 | 127.39 | 104.28
2019-04-02 05:30 | 127 | 102.86
2019-04-02 06:00 | 118.6 | 93.22
2019-04-02 06:30 | 122.87 | 101.71
2019-04-02 07:00 | 119.51 | 94.6
2019-04-02 07:30 | 101.14 | 69.64
2019-04-02 08:00 | 102.17 | 63.81
2019-04-02 08:30 | 111.84 | 69.05
2019-04-02 09:00 | 117.05 | 72.01
2019-04-02 09:30 | 112.83 | 66.45
2019-04-02 10:00 | 111.95 | 64.91
2019-04-02 10:30 | 109.76 | 69.34
2019-04-02 11:00 | 114.33 | 73.95
2019-04-02 11:30 | 112.19 | 70.52
2019-04-02 12:00 | 119.5 | 83
2019-04-02 12:30 | 114.38 | 76.55
2019-04-02 13:00 | 119.41 | 80.72
2019-04-02 13:30 | 120.95 | 82.53
2019-04-02 14:00 | 125.18 | 87.27
2019-04-02 14:30 | 127.69 | 84.49
2019-04-02 15:00 | 123.72 | 80.39
2019-04-02 15:30 | 121.06 | 73.25
2019-04-02 16:00 | 124.84 | 78.83
2019-04-02 16:30 | 124.06 | 83.22
2019-04-02 17:00 | 130.11 | 98.13
2019-04-02 17:30 | 125.16 | 98.94
2019-04-02 18:00 | 128.84 | 105.29
2019-04-02 18:30 | 125.62 | 103.79
2019-04-02 19:00 | 132.99 | 110.95
2019-04-02 19:30 | 136.21 | 112.86
2019-04-02 20:00 | 134.1 | 109.11
2019-04-02 20:30 | 129.69 | 104.15
2019-04-02 21:00 | 136.91 | 111.22
2019-04-02 21:30 | 137.26 | 112.95
2019-04-02 22:00 | 124.94 | 98.5
2019-04-02 22:30 | 126.69 | 101.04
2019-04-02 23:00 | 129.06 | 104.4
2019-04-02 23:30 | 127.91 | 102.72
2019-04-03 | 127.49 | 104.47
2019-04-03 00:30 | 134.98 | 112.81
2019-04-03 01:00 | 134.87 | 110.97
2019-04-03 01:30 | 139.41 | 114.77
2019-04-03 02:00 | 140.26 | 115.46
2019-04-03 02:30 | 135.92 | 109.6
2019-04-03 03:00 | 129.39 | 102.46
2019-04-03 03:30 | 128.33 | 101.67
2019-04-03 04:00 | 131.91 | 106.05
2019-04-03 04:30 | 130.23 | 104.64
2019-04-03 05:00 | 129.99 | 103.29
2019-04-03 05:30 | 128.54 | 100.91
2019-04-03 06:00 | 130.08 | 102.03
2019-04-03 06:30 | 116.67 | 91.98
2019-04-03 07:00 | 112.38 | 89.65
2019-04-03 07:30 | 117.12 | 90.17
2019-04-03 08:00 | 102.37 | 70.31
2019-04-03 08:30 | 104.73 | 65.86
2019-04-03 09:00 | 104.76 | 61.44
2019-04-03 09:30 | 98.37 | 56.57
2019-04-03 10:00 | 108.88 | 69.55
2019-04-03 10:30 | 113.85 | 74.85
2019-04-03 11:00 | 114.58 | 74.51
2019-04-03 11:30 | 110.3 | 69.11
2019-04-03 12:00 | 116.3 | 74.23
2019-04-03 12:30 | 112.95 | 73.78
2019-04-03 13:00 | 112.62 | 73.09
2019-04-03 13:30 | 109.29 | 74.4
2019-04-03 14:00 | 115.81 | 79.23
2019-04-03 14:30 | 116.18 | 76.89
2019-04-03 15:00 | 114.44 | 73.42
2019-04-03 15:30 | 109.82 | 72.55
2019-04-03 16:00 | 107.06 | 73.16
2019-04-03 16:30 | 114.99 | 82.64
2019-04-03 17:00 | 112.2 | 83.87
2019-04-03 17:30 | 117.09 | 94.13
2019-04-03 18:00 | 116.82 | 97.75
2019-04-03 18:30 | 117.66 | 98.54
2019-04-03 19:00 | 113.96 | 94.53
2019-04-03 19:30 | 115 | 94.81
2019-04-03 20:00 | 115.2 | 94.45
2019-04-03 20:30 | 121.1 | 99.73
2019-04-03 21:00 | 120.34 | 99.27
2019-04-03 21:30 | 122.48 | 102.77
2019-04-03 22:00 | 127.14 | 106.57
2019-04-03 22:30 | 128.39 | 107.43
2019-04-03 23:00 | 136.55 | 116.36
2019-04-03 23:30 | 138.09 | 116.57
2019-04-04 | 130.05 | 108
2019-04-04 00:30 | 128.85 | 105.72
2019-04-04 01:00 | 127.69 | 104.47
2019-04-04 01:30 | 116.75 | 98.16
2019-04-04 02:00 | 116.99 | 97.3
2019-04-04 02:30 | 120.87 | 97.04
2019-04-04 03:00 | 127.34 | 104.82
2019-04-04 03:30 | 129.81 | 107.94
2019-04-04 04:00 | 126.44 | 102.86
2019-04-04 04:30 | 129.12 | 107.55
2019-04-04 05:00 | 123.43 | 101.29
2019-04-04 05:30 | 117.22 | 93.97
2019-04-04 06:00 | 119.12 | 95.82
2019-04-04 06:30 | 124.59 | 103.51
2019-04-04 07:00 | 121.19 | 98.56
2019-04-04 07:30 | 123.68 | 96.43
2019-04-04 08:00 | 128.13 | 96.77
2019-04-04 08:30 | 125.9 | 86.72
2019-04-04 09:00 | 119.24 | 76.21
2019-04-04 09:30 | 125.59 | 83.76
2019-04-04 10:00 | 119.97 | 77.09
2019-04-04 10:30 | 116.39 | 67.73
2019-04-04 11:00 | 116.4 | 69.37
2019-04-04 11:30 | 115.18 | 70.42
2019-04-04 12:00 | 119.2 | 74.06
2019-04-04 12:30 | 117.71 | 73.12
2019-04-04 13:00 | 115.81 | 72.69
2019-04-04 13:30 | 115.58 | 71.92
2019-04-04 14:00 | 128.29 | 83.18
2019-04-04 14:30 | 125.74 | 82.19
2019-04-04 15:00 | 124.04 | 80.83
2019-04-04 15:30 | 131.54 | 90.81
2019-04-04 16:00 | 123.81 | 87.55
2019-04-04 16:30 | 114.83 | 85.04
2019-04-04 17:00 | 106.56 | 79.07
2019-04-04 17:30 | 102.43 | 82.01
2019-04-04 18:00 | 105.91 | 87.23
2019-04-04 18:30 | 110.33 | 88.35
2019-04-04 19:00 | 123.63 | 100.46
2019-04-04 19:30 | 128.32 | 105.3
2019-04-04 20:00 | 135.15 | 112.6
2019-04-04 20:30 | 123.67 | 101.31
2019-04-04 21:00 | 125.74 | 103.93
2019-04-04 21:30 | 132.86 | 110.71
2019-04-04 22:00 | 127.91 | 106.54
2019-04-04 22:30 | 130.93 | 110.56
2019-04-04 23:00 | 127.02 | 106.88
2019-04-04 23:30 | 122.01 | 101.72
2019-04-05 | 122.74 | 103.37
2019-04-05 00:30 | 125.55 | 106.54
2019-04-05 01:00 | 128.57 | 111.57
2019-04-05 01:30 | 126.39 | 113.19
2019-04-05 02:00 | 128.11 | 114.81
2019-04-05 02:30 | 127.37 | 114.72
2019-04-05 03:00 | 126.75 | 112.42
2019-04-05 03:30 | 120.25 | 105.54
2019-04-05 04:00 | 115.61 | 98.94
2019-04-05 04:30 | 122.13 | 108.09
2019-04-05 05:00 | 120.12 | 105.43
2019-04-05 05:30 | 115.63 | 100.27
2019-04-05 06:00 | 118.42 | 103.3
2019-04-05 06:30 | 119.51 | 104.94
2019-04-05 07:00 | 118.29 | 103.93
2019-04-05 07:30 | 123.72 | 108.79
2019-04-05 08:00 | 121.29 | 105.95
2019-04-05 08:30 | 120.98 | 106.45
2019-04-05 09:00 | 122.89 | 108.45
2019-04-05 09:30 | 121.28 | 98.33
2019-04-05 10:00 | 122.56 | 92.47
2019-04-05 10:30 | 115.06 | 85.16
2019-04-05 11:00 | 115.36 | 84.73
2019-04-05 11:30 | 112.33 | 82.19
2019-04-05 12:00 | 110.16 | 80.1
2019-04-05 12:30 | 112.06 | 82.96
2019-04-05 13:00 | 109.41 | 80.01
2019-04-05 13:30 | 111.76 | 86.58
2019-04-05 14:00 | 118.13 | 95.12
2019-04-05 14:30 | 116.42 | 88.67
2019-04-05 15:00 | 114.26 | 88.35
2019-04-05 15:30 | 118.15 | 94.02
2019-04-05 16:00 | 123.56 | 99.64
2019-04-05 16:30 | 119.92 | 99.24
2019-04-05 17:00 | 125.24 | 105.52
2019-04-05 17:30 | 126 | 110.19
2019-04-05 18:00 | 123.36 | 109.14
2019-04-05 18:30 | 116.07 | 102.46
2019-04-05 19:00 | 122.95 | 108.98
2019-04-05 19:30 | 121.84 | 107.33
2019-04-05 20:00 | 121.45 | 106.15
2019-04-05 20:30 | 124.01 | 110
2019-04-05 21:00 | 118.15 | 103.13
2019-04-05 21:30 | 117.03 | 102.35
2019-04-05 22:00 | 133.49 | 119.92
2019-04-05 22:30 | 128.75 | 114.35
2019-04-05 23:00 | 120.4 | 106.18
2019-04-05 23:30 | 111.79 | 94.65
2019-04-06 | 110.37 | 92.03
2019-04-06 00:30 | 116.22 | 99.79
2019-04-06 01:00 | 121.59 | 105.82
2019-04-06 01:30 | 122.61 | 107.47
2019-04-06 02:00 | 122.11 | 106.12
2019-04-06 02:30 | 126.59 | 111.9
2019-04-06 03:00 | 129.62 | 115.53
2019-04-06 03:30 | 125.49 | 110.09
2019-04-06 04:00 | 121.57 | 104.91
2019-04-06 04:30 | 120.34 | 104.24
2019-04-06 05:00 | 120.19 | 104.01
2019-04-06 05:30 | 124.87 | 109.79
2019-04-06 06:00 | 115.48 | 97.05
2019-04-06 06:30 | 118.04 | 101.87
2019-04-06 07:00 | 122.58 | 105.76
2019-04-06 07:30 | 111.65 | 89.38
2019-04-06 08:00 | 107.59 | 77.2
2019-04-06 08:30 | 112.62 | 82.75
2019-04-06 09:00 | 109.31 | 79.49
2019-04-06 09:30 | 115.6 | 91.3
2019-04-06 10:00 | 111.8 | 83.63
2019-04-06 10:30 | 109.58 | 78.21
2019-04-06 11:00 | 109.17 | 77.53
2019-04-06 11:30 | 106.22 | 74.16
2019-04-06 12:00 | 105.39 | 76.48
2019-04-06 12:30 | 103.17 | 73.77
2019-04-06 13:00 | 107.54 | 77.74
2019-04-06 13:30 | 104.61 | 74.56
2019-04-06 14:00 | 105.71 | 75.59
2019-04-06 14:30 | 104.92 | 76.68
2019-04-06 15:00 | 105.01 | 77.34
2019-04-06 15:30 | 104.6 | 74.36
2019-04-06 16:00 | 106.04 | 77.27
2019-04-06 16:30 | 100.37 | 70.96
2019-04-06 17:00 | 100.73 | 75.89
2019-04-06 17:30 | 108.86 | 90.46
2019-04-06 18:00 | 106.66 | 90.75
2019-04-06 18:30 | 103.95 | 89.25
2019-04-06 19:00 | 108.47 | 93.66
2019-04-06 19:30 | 100.83 | 85.09
2019-04-06 20:00 | 99.6 | 82.6
2019-04-06 20:30 | 105.6 | 88.95
2019-04-06 21:00 | 108.76 | 91.74
2019-04-06 21:30 | 107.21 | 90.41
2019-04-06 22:00 | 109.44 | 94.02
2019-04-06 22:30 | 107.54 | 91.49
2019-04-06 23:00 | 109.93 | 93.44
2019-04-06 23:30 | 103.46 | 84.96
2019-04-07 | 106.54 | 87.05
2019-04-07 00:30 | 106.71 | 87.89
2019-04-07 01:00 | 107.18 | 87.78
2019-04-07 01:30 | 107.5 | 88.17
2019-04-07 02:00 | 112.47 | 95.15
2019-04-07 02:30 | 111.56 | 94.13
2019-04-07 03:00 | 115.33 | 100.21
2019-04-07 03:30 | 103.23 | 86.33
2019-04-07 04:00 | 101.68 | 83.99
2019-04-07 04:30 | 105.84 | 88.05
2019-04-07 05:00 | 108.69 | 92.44
2019-04-07 05:30 | 106.84 | 89.56
2019-04-07 06:00 | 109.07 | 91.03
2019-04-07 06:30 | 107.48 | 91.07
2019-04-07 07:00 | 108.21 | 89.54
2019-04-07 07:30 | 103.9 | 81.67
2019-04-07 08:00 | 100.96 | 75.03
2019-04-07 08:30 | 99.08 | 68.77
2019-04-07 09:00 | 102.75 | 73.2
2019-04-07 09:30 | 104.15 | 75.66
2019-04-07 10:00 | 101.78 | 69.79
2019-04-07 10:30 | 103.37 | 74.74
2019-04-07 11:00 | 103.4 | 73.35
2019-04-07 11:30 | 100.16 | 70.89
2019-04-07 12:00 | 99.3 | 71
2019-04-07 12:30 | 105.75 | 82.04
2019-04-07 13:00 | 104.81 | 78.38
2019-04-07 13:30 | 104.43 | 79.96
2019-04-07 14:00 | 105.77 | 77.93
2019-04-07 14:30 | 105.73 | 79.04
2019-04-07 15:00 | 109.16 | 86.49
2019-04-07 15:30 | 108.3 | 85.6
2019-04-07 16:00 | 115.77 | 99.01
2019-04-07 16:30 | 113.58 | 92.29
2019-04-07 17:00 | 121.71 | 108.37
2019-04-07 17:30 | 119.44 | 105.46
2019-04-07 18:00 | 118.52 | 104.96
2019-04-07 18:30 | 112.1 | 99.02
2019-04-07 19:00 | 121.8 | 109.13
2019-04-07 19:30 | 119.61 | 107.06
2019-04-07 20:00 | 119.79 | 106.69
2019-04-07 20:30 | 116.19 | 102.58
2019-04-07 21:00 | 120.78 | 107.27
2019-04-07 21:30 | 117.46 | 103.27
2019-04-07 22:00 | 121.26 | 107.78
2019-04-07 22:30 | 113.12 | 98.14
2019-04-07 23:00 | 112.67 | 96.99
2019-04-07 23:30 | 121.49 | 107.87
2019-04-08 | 119.27 | 104.88
2019-04-08 00:30 | 121.05 | 106.53
2019-04-08 01:00 | 115.75 | 100.39
2019-04-08 01:30 | 110.15 | 94.91
2019-04-08 02:00 | 111.88 | 96.54
2019-04-08 02:30 | 112.09 | 96.96
2019-04-08 03:00 | 109.67 | 92.82
2019-04-08 03:30 | 112.56 | 96.95
2019-04-08 04:00 | 110.46 | 94.33
2019-04-08 04:30 | 108.98 | 92.34
2019-04-08 05:00 | 106.87 | 89.21
2019-04-08 05:30 | 106.34 | 89.24
2019-04-08 06:00 | 97 | 75.56
2019-04-08 06:30 | 101.77 | 83.11
2019-04-08 07:00 | 102.77 | 82.59
2019-04-08 07:30 | 98.44 | 75.51
2019-04-08 08:00 | 96.09 | 70.8
2019-04-08 08:30 | 98.37 | 71.43
2019-04-08 09:00 | 95.81 | 66.1
2019-04-08 09:30 | 96.16 | 66.63
2019-04-08 10:00 | 93.79 | 60.74
2019-04-08 10:30 | 102.22 | 72.42
2019-04-08 11:00 | 100.65 | 70.8
2019-04-08 11:30 | 102.99 | 72.74
2019-04-08 12:00 | 106.81 | 78.41
2019-04-08 12:30 | 103.44 | 75.26
2019-04-08 13:00 | 109.54 | 80.49
2019-04-08 13:30 | 105.12 | 74.66
2019-04-08 14:00 | 101.03 | 71.99
2019-04-08 14:30 | 102.27 | 79.45
2019-04-08 15:00 | 106.47 | 81.86
2019-04-08 15:30 | 103.46 | 76.68
2019-04-08 16:00 | 103.71 | 79.58
2019-04-08 16:30 | 107.35 | 81.44
2019-04-08 17:00 | 108.22 | 87.71
2019-04-08 17:30 | 111.97 | 95.5
2019-04-08 18:00 | 115.45 | 101.94
2019-04-08 18:30 | 110.65 | 96.33
2019-04-08 19:00 | 117.83 | 104.82
2019-04-08 19:30 | 111.82 | 98.89
2019-04-08 20:00 | 116.53 | 104.05
2019-04-08 20:30 | 116.3 | 103.55
2019-04-08 21:00 | 114.37 | 100.97
2019-04-08 21:30 | 109.99 | 94.81
2019-04-08 22:00 | 112.39 | 98.1
2019-04-08 22:30 | 113.15 | 99
2019-04-08 23:00 | 107.06 | 91.5
2019-04-08 23:30 | 116.66 | 103.35
2019-04-09 | 118.85 | 105.44
2019-04-09 00:30 | 117.96 | 104.84
2019-04-09 01:00 | 116.8 | 102.47
2019-04-09 01:30 | 114.31 | 100.41
2019-04-09 02:00 | 115.26 | 101.55
2019-04-09 02:30 | 112.17 | 96.9
2019-04-09 03:00 | 115.96 | 101.12
2019-04-09 03:30 | 115.51 | 101.83
2019-04-09 04:00 | 116.55 | 103.35
2019-04-09 04:30 | 112.4 | 96.93
2019-04-09 05:00 | 107.27 | 90.51
2019-04-09 05:30 | 111.79 | 97.08
2019-04-09 06:00 | 111.8 | 96.16
2019-04-09 06:30 | 111.47 | 97.21
2019-04-09 07:00 | 111.91 | 97.22
2019-04-09 07:30 | 105.27 | 85.66
2019-04-09 08:00 | 103.72 | 79.69
2019-04-09 08:30 | 97.28 | 70.29
2019-04-09 09:00 | 98.08 | 70.76
2019-04-09 09:30 | 95.79 | 65.97
2019-04-09 10:00 | 95.19 | 62.34
2019-04-09 10:30 | 98.93 | 68.42
2019-04-09 11:00 | 98.26 | 67.37
2019-04-09 11:30 | 101.17 | 75.11
2019-04-09 12:00 | 104.51 | 79.84
2019-04-09 12:30 | 100.64 | 74.05
2019-04-09 13:00 | 99.94 | 72.22
2019-04-09 13:30 | 99.95 | 72.11
2019-04-09 14:00 | 103.72 | 79.03
2019-04-09 14:30 | 98.43 | 69.12
2019-04-09 15:00 | 93.17 | 61.56
2019-04-09 15:30 | 94.73 | 64.72
2019-04-09 16:00 | 101.96 | 76.65
2019-04-09 16:30 | 101.74 | 78.35
2019-04-09 17:00 | 105.73 | 86.86
2019-04-09 17:30 | 106.25 | 90.39
2019-04-09 18:00 | 107.51 | 93.32
2019-04-09 18:30 | 107.56 | 93.68
2019-04-09 19:00 | 103.58 | 88.17
2019-04-09 19:30 | 111.9 | 99.54
2019-04-09 20:00 | 115.91 | 105.57
2019-04-09 20:30 | 117.76 | 107.37
2019-04-09 21:00 | 118.02 | 107.26
2019-04-09 21:30 | 114.51 | 102.34
2019-04-09 22:00 | 114.39 | 101.99
2019-04-09 22:30 | 112.66 | 98.91
2019-04-09 23:00 | 111.7 | 98.56
2019-04-09 23:30 | 106.69 | 92.26
2019-04-10 | 108.7 | 94.37
2019-04-10 00:30 | 109.79 | 96.64
2019-04-10 01:00 | 109.78 | 96.35
2019-04-10 01:30 | 108.95 | 94.87
2019-04-10 02:00 | 109.3 | 94.91
2019-04-10 02:30 | 110.53 | 97.31
2019-04-10 03:00 | 109.79 | 95.87
2019-04-10 03:30 | 105.39 | 90.59
2019-04-10 04:00 | 107.9 | 93.99
2019-04-10 04:30 | 112.07 | 98.94
2019-04-10 05:00 | 104.48 | 90.82
2019-04-10 05:30 | 102.89 | 88.26
2019-04-10 06:00 | 97.47 | 81.91
2019-04-10 06:30 | 97.85 | 82.27
2019-04-10 07:00 | 100.01 | 84.8
2019-04-10 07:30 | 88.27 | 66.82
2019-04-10 08:00 | 87.91 | 61.28
2019-04-10 08:30 | 92.85 | 68.24
2019-04-10 09:00 | 89.74 | 68.22
2019-04-10 09:30 | 86.1 | 63.87
2019-04-10 10:00 | 84.4 | 55.61
2019-04-10 10:30 | 83.19 | 51.34
2019-04-10 11:00 | 88.65 | 62.24
2019-04-10 11:30 | 88.63 | 58.79
2019-04-10 12:00 | 81.29 | 54.53
2019-04-10 12:30 | 86.23 | 60.33
2019-04-10 13:00 | 88.72 | 59.86
2019-04-10 13:30 | 88.58 | 59.29
2019-04-10 14:00 | 90.1 | 59.48
2019-04-10 14:30 | 91.82 | 61.29
2019-04-10 15:00 | 94.06 | 69.51
2019-04-10 15:30 | 95.73 | 72.23
2019-04-10 16:00 | 99.45 | 81.5
2019-04-10 16:30 | 92.78 | 75.82
2019-04-10 17:00 | 100.55 | 85.27
2019-04-10 17:30 | 101.07 | 86.1
2019-04-10 18:00 | 100.26 | 86.4
2019-04-10 18:30 | 98.22 | 84.36
2019-04-10 19:00 | 111.86 | 100.13
2019-04-10 19:30 | 106.77 | 95.23
2019-04-10 20:00 | 105.32 | 93.87
2019-04-10 20:30 | 106.7 | 94.79
2019-04-10 21:00 | 106.16 | 93.99
2019-04-10 21:30 | 113.06 | 101.2
2019-04-10 22:00 | 109.52 | 96.6
2019-04-10 22:30 | 108.18 | 95.15
2019-04-10 23:00 | 110.82 | 97.67
2019-04-10 23:30 | 104.7 | 89.01
2019-04-11 | 107.72 | 93.39
2019-04-11 00:30 | 120.05 | 106.42
2019-04-11 01:00 | 116.24 | 101.73
2019-04-11 01:30 | 116.63 | 102.1
2019-04-11 02:00 | 109.77 | 94.38
2019-04-11 02:30 | 113.5 | 99.19
2019-04-11 03:00 | 110.32 | 95.24
2019-04-11 03:30 | 108.1 | 90.42
2019-04-11 04:00 | 109.33 | 93.34
2019-04-11 04:30 | 107.96 | 91.51
2019-04-11 05:00 | 114.51 | 99.73
2019-04-11 05:30 | 114.46 | 99.61
2019-04-11 06:00 | 109.15 | 93.86
2019-04-11 06:30 | 105.54 | 89
2019-04-11 07:00 | 111.03 | 96.1
2019-04-11 07:30 | 100.42 | 78.7
2019-04-11 08:00 | 98.29 | 72.2
2019-04-11 08:30 | 100.32 | 72.85
2019-04-11 09:00 | 98.87 | 69.47
2019-04-11 09:30 | 102.44 | 73.66
2019-04-11 10:00 | 96.82 | 68.16
2019-04-11 10:30 | 102.38 | 72.83
2019-04-11 11:00 | 101.12 | 74.56
2019-04-11 11:30 | 95.37 | 63.15
2019-04-11 12:00 | 96.7 | 65.62
2019-04-11 12:30 | 96.6 | 67.07
2019-04-11 13:00 | 93.2 | 62.22
2019-04-11 13:30 | 92.45 | 66.24
2019-04-11 14:00 | 97.03 | 73.91
2019-04-11 14:30 | 99.21 | 77.57
2019-04-11 15:00 | 96.45 | 72.89
2019-04-11 15:30 | 95.94 | 72.99
2019-04-11 16:00 | 100.27 | 80.36
2019-04-11 16:30 | 103.75 | 85.89
2019-04-11 17:00 | 107.99 | 93.04
2019-04-11 17:30 | 106.14 | 91.13
2019-04-11 18:00 | 109.28 | 95.99
2019-04-11 18:30 | 107.13 | 94.26
2019-04-11 19:00 | 116.8 | 105.34
2019-04-11 19:30 | 118.2 | 106.41
2019-04-11 20:00 | 121.25 | 110.5
2019-04-11 20:30 | 116.02 | 104.45
2019-04-11 21:00 | 113.08 | 101.28
2019-04-11 21:30 | 108.13 | 95.11
2019-04-11 22:00 | 111.49 | 98.92
2019-04-11 22:30 | 106.71 | 92.99
2019-04-11 23:00 | 109.18 | 95.95
2019-04-11 23:30 | 109.28 | 94.12
2019-04-12 | 106.47 | 92.88
2019-04-12 00:30 | 109.53 | 96.91
2019-04-12 01:00 | 106.52 | 94.58
2019-04-12 01:30 | 100.37 | 87.29
2019-04-12 02:00 | 110.3 | 98.79
2019-04-12 02:30 | 103.73 | 90.92
2019-04-12 03:00 | 100.95 | 86.84
2019-04-12 03:30 | 97.09 | 81.61
2019-04-12 04:00 | 97.33 | 82.76
2019-04-12 04:30 | 98.3 | 84.42
2019-04-12 05:00 | 97.52 | 83.49
2019-04-12 05:30 | 104.02 | 92
2019-04-12 06:00 | 108.03 | 96.29
2019-04-12 06:30 | 107.39 | 95.02
2019-04-12 07:00 | 98.23 | 83.28
2019-04-12 07:30 | 98.01 | 81.93
2019-04-12 08:00 | 106.33 | 90.44
2019-04-12 08:30 | 106.42 | 87.8
2019-04-12 09:00 | 104.33 | 83.64
2019-04-12 09:30 | 104.18 | 81.98
2019-04-12 10:00 | 101.82 | 75.94
2019-04-12 10:30 | 104.02 | 79.38
2019-04-12 11:00 | 107.12 | 84.39
2019-04-12 11:30 | 106.78 | 82.2
2019-04-12 12:00 | 109.15 | 83.04
2019-04-12 12:30 | 117.05 | 96.21
2019-04-12 13:00 | 107.41 | 81.07
2019-04-12 13:30 | 113.52 | 89.75
2019-04-12 14:00 | 114.74 | 91.22
2019-04-12 14:30 | 116.53 | 95.3
2019-04-12 15:00 | 119.16 | 98.42
2019-04-12 15:30 | 120.58 | 100.2
2019-04-12 16:00 | 120.21 | 100.84
2019-04-12 16:30 | 117.12 | 100.08
2019-04-12 17:00 | 118.69 | 101.89
2019-04-12 17:30 | 128.52 | 114.57
2019-04-12 18:00 | 125.83 | 111.01
2019-04-12 18:30 | 117.04 | 99.92
2019-04-12 19:00 | 126.59 | 111.67
2019-04-12 19:30 | 129.45 | 115.62
2019-04-12 20:00 | 127.63 | 113.05
2019-04-12 20:30 | 132.6 | 118.57
2019-04-12 21:00 | 126.86 | 111.27
2019-04-12 21:30 | 129.87 | 114.91
2019-04-12 22:00 | 126.55 | 110.63
2019-04-12 22:30 | 122.94 | 105.95
2019-04-12 23:00 | 122.33 | 103.71
2019-04-12 23:30 | 120.61 | 103.43
2019-04-13 | 118.32 | 102.83
2019-04-13 00:30 | 115.2 | 99.22
2019-04-13 01:00 | 118.31 | 103.23
2019-04-13 01:30 | 124.77 | 110.17
2019-04-13 02:00 | 126.17 | 112.55
2019-04-13 02:30 | 118.32 | 102.41
2019-04-13 03:00 | 115.57 | 99.18
2019-04-13 03:30 | 115.83 | 99.39
2019-04-13 04:00 | 111.12 | 94.7
2019-04-13 04:30 | 117.05 | 102.72
2019-04-13 05:00 | 119.08 | 105.84
2019-04-13 05:30 | 124.34 | 110.5
2019-04-13 06:00 | 115.32 | 99.58
2019-04-13 06:30 | 109.14 | 91.48
2019-04-13 07:00 | 112.28 | 95.59
2019-04-13 07:30 | 108.59 | 88.5
2019-04-13 08:00 | 106.63 | 80.48
2019-04-13 08:30 | 112.51 | 84.93
2019-04-13 09:00 | 110.2 | 80.49
2019-04-13 09:30 | 113.05 | 83.24
2019-04-13 10:00 | 115.55 | 86.09
2019-04-13 10:30 | 113.02 | 81.44
2019-04-13 11:00 | 112.72 | 82.29
2019-04-13 11:30 | 112.62 | 82.88
2019-04-13 12:00 | 108.32 | 79.32
2019-04-13 12:30 | 104.72 | 76.68
2019-04-13 13:00 | 104.06 | 74.53
2019-04-13 13:30 | 108.28 | 79.12
2019-04-13 14:00 | 108.06 | 81.91
2019-04-13 14:30 | 109.17 | 86.16
2019-04-13 15:00 | 107.37 | 84.5
2019-04-13 15:30 | 106.94 | 81.44
2019-04-13 16:00 | 104.19 | 81.54
2019-04-13 16:30 | 103.79 | 78.34
2019-04-13 17:00 | 107.91 | 84.29
2019-04-13 17:30 | 112.21 | 94.35
2019-04-13 18:00 | 115.22 | 98.56
2019-04-13 18:30 | 118.4 | 102.98
2019-04-13 19:00 | 119.51 | 104.47
2019-04-13 19:30 | 116.83 | 100.76
2019-04-13 20:00 | 112.88 | 96.33
2019-04-13 20:30 | 120.4 | 105.32
2019-04-13 21:00 | 126.86 | 110.85
2019-04-13 21:30 | 125.48 | 108.87
2019-04-13 22:00 | 122.69 | 105.6
2019-04-13 22:30 | 116.79 | 101.14
2019-04-13 23:00 | 123.14 | 109.23
2019-04-13 23:30 | 118.85 | 100.74
2019-04-14 | 115.35 | 96.22
2019-04-14 00:30 | 125.86 | 110.31
2019-04-14 01:00 | 123.99 | 108.94
2019-04-14 01:30 | 114.89 | 98.96
2019-04-14 02:00 | 115.51 | 97.9
2019-04-14 02:30 | 117.64 | 102.29
2019-04-14 03:00 | 117.6 | 102.75
2019-04-14 03:30 | 114.61 | 100.06
2019-04-14 04:00 | 117.76 | 103.86
2019-04-14 04:30 | 121.64 | 107.62
2019-04-14 05:00 | 118.88 | 103.86
2019-04-14 05:30 | 121.13 | 107.11
2019-04-14 06:00 | 114.58 | 99.51
2019-04-14 06:30 | 113.95 | 98.5
2019-04-14 07:00 | 117.15 | 101.91
2019-04-14 07:30 | 114.9 | 96.03
2019-04-14 08:00 | 107.36 | 82.12
2019-04-14 08:30 | 107.45 | 79.53
2019-04-14 09:00 | 106.93 | 78.38
2019-04-14 09:30 | 109.47 | 81.98
2019-04-14 10:00 | 105.87 | 74.82
2019-04-14 10:30 | 113.15 | 85.54
2019-04-14 11:00 | 117.08 | 90.67
2019-04-14 11:30 | 116.13 | 88.84
2019-04-14 12:00 | 116.56 | 90.04
2019-04-14 12:30 | 109.11 | 81.28
2019-04-14 13:00 | 119.02 | 92.26
2019-04-14 13:30 | 121.1 | 94.52
2019-04-14 14:00 | 113.89 | 86.94
2019-04-14 14:30 | 118.88 | 93.27
2019-04-14 15:00 | 109.85 | 83.99
2019-04-14 15:30 | 116.07 | 88.68
2019-04-14 16:00 | 105.54 | 77.53
2019-04-14 16:30 | 107.12 | 82.92
2019-04-14 17:00 | 114.48 | 96.2
2019-04-14 17:30 | 113.76 | 98.04
2019-04-14 18:00 | 119.23 | 107.17
2019-04-14 18:30 | 125.33 | 112.36
2019-04-14 19:00 | 130.13 | 117.65
2019-04-14 19:30 | 133.76 | 122.28
2019-04-14 20:00 | 128.27 | 115.85
2019-04-14 20:30 | 120.6 | 107.61
2019-04-14 21:00 | 117.09 | 102.45
2019-04-14 21:30 | 113.31 | 97.51
2019-04-14 22:00 | 106.01 | 90.57
2019-04-14 22:30 | 105.61 | 88.96
2019-04-14 23:00 | 110.58 | 93.62
2019-04-14 23:30 | 108.91 | 91.61
2019-04-15 | 109.56 | 93.15
2019-04-15 00:30 | 111.3 | 94.66
2019-04-15 01:00 | 111.08 | 93.01
2019-04-15 01:30 | 106.13 | 86.97
2019-04-15 02:00 | 106.03 | 85.16
2019-04-15 02:30 | 113.57 | 96.45
2019-04-15 03:00 | 119.91 | 104.21
2019-04-15 03:30 | 116.3 | 100.16
2019-04-15 04:00 | 114.75 | 99.19
2019-04-15 04:30 | 117.09 | 102.11
2019-04-15 05:00 | 113.26 | 97.56
2019-04-15 05:30 | 92.64 | 89.17
2019-04-15 06:00 | 91.85 | 89
2019-04-15 06:30 | 87.21 | 84.67
2019-04-15 07:00 | 88 | 85
2019-04-15 07:30 | 86.98 | 82.31
2019-04-15 08:00 | 79.56 | 72.58
2019-04-15 08:30 | 77.31 | 67.16
2019-04-15 09:00 | 79.49 | 67.78
2019-04-15 09:30 | 81.05 | 67.99
2019-04-15 10:00 | 80.65 | 66.34
2019-04-15 10:30 | 85.3 | 68.65
2019-04-15 11:00 | 88.66 | 73.07
2019-04-15 11:30 | 85.57 | 70.8
2019-04-15 12:00 | 87.91 | 70.82
2019-04-15 12:30 | 88.8 | 72.74
2019-04-15 13:00 | 93.74 | 79.98
2019-04-15 13:30 | 94.07 | 80.74
2019-04-15 14:00 | 89.08 | 75.16
2019-04-15 14:30 | 83.32 | 67.38
2019-04-15 15:00 | 80.53 | 63.93
2019-04-15 15:30 | 78.91 | 64.16
2019-04-15 16:00 | 84.28 | 75.79
2019-04-15 16:30 | 85.85 | 73.29
2019-04-15 17:00 | 85.31 | 76.87
2019-04-15 17:30 | 92.89 | 87.99
2019-04-15 18:00 | 101.05 | 97.18
2019-04-15 18:30 | 93.92 | 89.5
2019-04-15 19:00 | 112.05 | 98.13
2019-04-15 19:30 | 113.27 | 100
2019-04-15 20:00 | 116.22 | 102.41
2019-04-15 20:30 | 111.13 | 96.52
2019-04-15 21:00 | 110.35 | 95.27
2019-04-15 21:30 | 109.68 | 94.26
2019-04-15 22:00 | 111.28 | 96.04
2019-04-15 22:30 | 108.77 | 92.49
2019-04-15 23:00 | 110.61 | 94.75
2019-04-15 23:30 | 107.7 | 91.88
2019-04-16 | 103.28 | 86.36
2019-04-16 00:30 | 104.38 | 87.64
2019-04-16 01:00 | 102.45 | 84.96
2019-04-16 01:30 | 107.4 | 91.88
2019-04-16 02:00 | 110.39 | 95.03
2019-04-16 02:30 | 109.56 | 93.75
2019-04-16 03:00 | 110.46 | 95.29
2019-04-16 03:30 | 105.04 | 87.35
2019-04-16 04:00 | 105.35 | 88.23
2019-04-16 04:30 | 105.03 | 88.64
2019-04-16 05:00 | 106.11 | 89.45
2019-04-16 05:30 | 106.72 | 90.83
2019-04-16 06:00 | 106.74 | 90.34
2019-04-16 06:30 | 103.44 | 85.53
2019-04-16 07:00 | 101.92 | 83.56
2019-04-16 07:30 | 103.75 | 82.76
2019-04-16 08:00 | 105.54 | 81.06
2019-04-16 08:30 | 100.97 | 71.75
2019-04-16 09:00 | 102.38 | 73.28
2019-04-16 09:30 | 98.87 | 68.05
2019-04-16 10:00 | 103.3 | 74.1
2019-04-16 10:30 | 101.3 | 71.53
2019-04-16 11:00 | 103.31 | 72.81
2019-04-16 11:30 | 106.48 | 75.92
2019-04-16 12:00 | 99.24 | 66.31
2019-04-16 12:30 | 99.44 | 71.97
2019-04-16 13:00 | 100.74 | 68.54
2019-04-16 13:30 | 110.84 | 82.63
2019-04-16 14:00 | 107.19 | 77.69
2019-04-16 14:30 | 109.61 | 83.83
2019-04-16 15:00 | 117.2 | 90.67
2019-04-16 15:30 | 112.22 | 86.84
2019-04-16 16:00 | 114.49 | 90.38
2019-04-16 16:30 | 114.17 | 90
2019-04-16 17:00 | 121.19 | 102.14
2019-04-16 17:30 | 124.86 | 108.6
2019-04-16 18:00 | 119.95 | 105.03
2019-04-16 18:30 | 122.04 | 107.57
2019-04-16 19:00 | 124.72 | 110.35
2019-04-16 19:30 | 123.59 | 110.07
2019-04-16 20:00 | 124.32 | 110.75
2019-04-16 20:30 | 124.92 | 109.94
2019-04-16 21:00 | 119.97 | 104.78
2019-04-16 21:30 | 120.42 | 105.99
2019-04-16 22:00 | 120.93 | 106.84
2019-04-16 22:30 | 118.65 | 104.75
2019-04-16 23:00 | 127.31 | 113.86
2019-04-16 23:30 | 124.03 | 109.42
2019-04-17 | 126.09 | 112.59
2019-04-17 00:30 | 126.34 | 113.01
2019-04-17 01:00 | 125.41 | 111.06
2019-04-17 01:30 | 122.59 | 107.14
2019-04-17 02:00 | 118.21 | 101.72
2019-04-17 02:30 | 117.35 | 101.44
2019-04-17 03:00 | 115.83 | 99.98
2019-04-17 03:30 | 107.73 | 90.48
2019-04-17 04:00 | 109.35 | 93.58
2019-04-17 04:30 | 107.98 | 93.53
2019-04-17 05:00 | 108.88 | 95.88
2019-04-17 05:30 | 107.56 | 95.21
2019-04-17 06:00 | 95.16 | 80.33
2019-04-17 06:30 | 98.27 | 83.59
2019-04-17 07:00 | 104.16 | 88.03
2019-04-17 07:30 | 104.69 | 86.72
2019-04-17 08:00 | 97.69 | 74.63
2019-04-17 08:30 | 89.95 | 62.08
2019-04-17 09:00 | 101.09 | 73.62
2019-04-17 09:30 | 103.37 | 77.68
2019-04-17 10:00 | 97.01 | 71.04
2019-04-17 10:30 | 98.84 | 71.35
2019-04-17 11:00 | 103.17 | 77.23
2019-04-17 11:30 | 99.73 | 74.38
2019-04-17 12:00 | 102.06 | 77.59
2019-04-17 12:30 | 100.27 | 74.13
2019-04-17 13:00 | 96.52 | 70.09
2019-04-17 13:30 | 98.76 | 72.03
2019-04-17 14:00 | 98.3 | 73.91
2019-04-17 14:30 | 98.25 | 73.62
2019-04-17 15:00 | 96.48 | 69.25
2019-04-17 15:30 | 90.89 | 62.94
2019-04-17 16:00 | 93.73 | 70.22
2019-04-17 16:30 | 100.29 | 80.77
2019-04-17 17:00 | 98.7 | 79.22
2019-04-17 17:30 | 103.87 | 88.55
2019-04-17 18:00 | 112.77 | 99.56
2019-04-17 18:30 | 104.39 | 90.58
2019-04-17 19:00 | 111.73 | 99.71
2019-04-17 19:30 | 116.07 | 105.22
2019-04-17 20:00 | 119.18 | 107.21
2019-04-17 20:30 | 117.58 | 105.48
2019-04-17 21:00 | 110.79 | 96.39
2019-04-17 21:30 | 117.16 | 103.93
2019-04-17 22:00 | 111.43 | 97.39
2019-04-17 22:30 | 111.12 | 96.24
2019-04-17 23:00 | 110.09 | 96.27
2019-04-17 23:30 | 110.78 | 96.04
2019-04-18 | 108.39 | 91.9
2019-04-18 00:30 | 112.83 | 98.35
2019-04-18 01:00 | 113.16 | 98.7
2019-04-18 01:30 | 109.32 | 95.04
2019-04-18 02:00 | 107.3 | 90.24
2019-04-18 02:30 | 108.01 | 91.97
2019-04-18 03:00 | 108.38 | 91.7
2019-04-18 03:30 | 105.07 | 87.4
2019-04-18 04:00 | 106.17 | 89.11
2019-04-18 04:30 | 113.3 | 99.15
2019-04-18 05:00 | 109.37 | 92.75
2019-04-18 05:30 | 111.66 | 95.99
2019-04-18 06:00 | 112.05 | 96
2019-04-18 06:30 | 104.51 | 86.82
2019-04-18 07:00 | 110.78 | 94.11
2019-04-18 07:30 | 104.27 | 83.42
2019-04-18 08:00 | 101.99 | 76.45
2019-04-18 08:30 | 97.72 | 68.36
2019-04-18 09:00 | 103.51 | 76.39
2019-04-18 09:30 | 103.83 | 74.05
2019-04-18 10:00 | 96.13 | 60.27
2019-04-18 10:30 | 95.44 | 58.99
2019-04-18 11:00 | 97.77 | 62.14
2019-04-18 11:30 | 98.26 | 64.97
2019-04-18 12:00 | 99.11 | 66.85
2019-04-18 12:30 | 105.78 | 76.32
2019-04-18 13:00 | 103.6 | 74.69
2019-04-18 13:30 | 107.3 | 78.61
2019-04-18 14:00 | 108.72 | 82.53
2019-04-18 14:30 | 110.68 | 84.87
2019-04-18 15:00 | 107.46 | 79.81
2019-04-18 15:30 | 104.85 | 75.63
2019-04-18 16:00 | 109.44 | 83.69
2019-04-18 16:30 | 104.33 | 79.79
2019-04-18 17:00 | 104.34 | 83.85
2019-04-18 17:30 | 113 | 98.37
2019-04-18 18:00 | 110.68 | 96.14
2019-04-18 18:30 | 115.53 | 102.01
2019-04-18 19:00 | 121.66 | 111.24
2019-04-18 19:30 | 118.44 | 107.64
2019-04-18 20:00 | 113.18 | 101.29
2019-04-18 20:30 | 111.6 | 99.33
2019-04-18 21:00 | 113.93 | 102.47
2019-04-18 21:30 | 108.53 | 95.86
2019-04-18 22:00 | 110.55 | 99
2019-04-18 22:30 | 113.7 | 102.38
2019-04-18 23:00 | 119.08 | 108.61
2019-04-18 23:30 | 118.1 | 107.16
2019-04-19 | 120.6 | 108.38
2019-04-19 00:30 | 112.56 | 99.34
2019-04-19 01:00 | 110.28 | 96.78
2019-04-19 01:30 | 117.9 | 105.56
2019-04-19 02:00 | 109.72 | 95.37
2019-04-19 02:30 | 110.42 | 95.26
2019-04-19 03:00 | 112.49 | 97.66
2019-04-19 03:30 | 109.91 | 94.87
2019-04-19 04:00 | 111.81 | 97.09
2019-04-19 04:30 | 116.47 | 102.91
2019-04-19 05:00 | 113.96 | 100.83
2019-04-19 05:30 | 113.22 | 100.05
2019-04-19 06:00 | 105.04 | 89.92
2019-04-19 06:30 | 108.71 | 94.57
2019-04-19 07:00 | 103.96 | 88.21
2019-04-19 07:30 | 106 | 86.03
2019-04-19 08:00 | 107.43 | 84.78
2019-04-19 08:30 | 110.16 | 85.35
2019-04-19 09:00 | 102.32 | 74.14
2019-04-19 09:30 | 103.52 | 74.13
2019-04-19 10:00 | 98.27 | 66.58
2019-04-19 10:30 | 99.49 | 67.43
2019-04-19 11:00 | 96.22 | 63.31
2019-04-19 11:30 | 98.78 | 69.1
2019-04-19 12:00 | 95.87 | 63.63
2019-04-19 12:30 | 101.85 | 75.6
2019-04-19 13:00 | 104.66 | 76.95
2019-04-19 13:30 | 105.34 | 79.96
2019-04-19 14:00 | 102.05 | 74.89
2019-04-19 14:30 | 109.65 | 83.41
2019-04-19 15:00 | 106.77 | 81.28
2019-04-19 15:30 | 103.68 | 77.74
2019-04-19 16:00 | 99.42 | 75.43
2019-04-19 16:30 | 97.47 | 75.34
2019-04-19 17:00 | 100.84 | 83.12
2019-04-19 17:30 | 108.98 | 94.52
2019-04-19 18:00 | 101.93 | 89.52
2019-04-19 18:30 | 99.8 | 87.13
2019-04-19 19:00 | 99.5 | 87.8
2019-04-19 19:30 | 109.2 | 97.81
2019-04-19 20:00 | 111.9 | 99.46
2019-04-19 20:30 | 103.84 | 91.5
2019-04-19 21:00 | 109.22 | 97.49
2019-04-19 21:30 | 109.34 | 97.17
2019-04-19 22:00 | 106.91 | 94.71
2019-04-19 22:30 | 111.86 | 99.64
2019-04-19 23:00 | 115.14 | 102.88
2019-04-19 23:30 | 109.87 | 97.11
2019-04-20 | 110.1 | 97.94
2019-04-20 00:30 | 108.98 | 97.03
2019-04-20 01:00 | 105.06 | 92.08
2019-04-20 01:30 | 103.73 | 90.87
2019-04-20 02:00 | 103.47 | 89.68
2019-04-20 02:30 | 101.02 | 86.3
2019-04-20 03:00 | 101.27 | 87.05
2019-04-20 03:30 | 100.34 | 86.46
2019-04-20 04:00 | 101.58 | 87.77
2019-04-20 04:30 | 96.21 | 82.77
2019-04-20 05:00 | 94.94 | 79.83
2019-04-20 05:30 | 101.09 | 88.5
2019-04-20 06:00 | 90.39 | 74.35
2019-04-20 06:30 | 88.5 | 72.56
2019-04-20 07:00 | 88.2 | 72.02
2019-04-20 07:30 | 90.04 | 71.32
2019-04-20 08:00 | 94.5 | 73.43
2019-04-20 08:30 | 96.63 | 71.68
2019-04-20 09:00 | 95.79 | 69.05
2019-04-20 09:30 | 93.87 | 65.85
2019-04-20 10:00 | 91.15 | 62.12
2019-04-20 10:30 | 91.87 | 63.59
2019-04-20 11:00 | 88.32 | 59.43
2019-04-20 11:30 | 92.58 | 67.8
2019-04-20 12:00 | 92.95 | 62.12
2019-04-20 12:30 | 93.13 | 65.27
2019-04-20 13:00 | 96.51 | 68.38
2019-04-20 13:30 | 101.61 | 75.62
2019-04-20 14:00 | 104.28 | 70.36
2019-04-20 14:30 | 97.07 | 72.13
2019-04-20 15:00 | 101.81 | 72.12
2019-04-20 15:30 | 97.5 | 65.01
2019-04-20 16:00 | 100.39 | 76.17
2019-04-20 16:30 | 101.65 | 75.55
2019-04-20 17:00 | 100.78 | 80.84
2019-04-20 17:30 | 109.47 | 95
2019-04-20 18:00 | 108.68 | 94.57
2019-04-20 18:30 | 102.43 | 87.23
2019-04-20 19:00 | 109.95 | 94.8
2019-04-20 19:30 | 108.78 | 94
2019-04-20 20:00 | 108.59 | 94.39
2019-04-20 20:30 | 109.29 | 93.98
2019-04-20 21:00 | 108.66 | 93.38
2019-04-20 21:30 | 104.18 | 89.51
2019-04-20 22:00 | 101.38 | 86.2
2019-04-20 22:30 | 98.1 | 83.19
2019-04-20 23:00 | 99.02 | 84.15
2019-04-20 23:30 | 107.72 | 93.11
2019-04-21 | 103.32 | 87.46
2019-04-21 00:30 | 104.14 | 89.08
2019-04-21 01:00 | 111.54 | 97.64
2019-04-21 01:30 | 103.46 | 88.07
2019-04-21 02:00 | 101.29 | 85.03
2019-04-21 02:30 | 101.17 | 84.78
2019-04-21 03:00 | 103.1 | 86.73
2019-04-21 03:30 | 103.72 | 87.3
2019-04-21 04:00 | 100.04 | 83.55
2019-04-21 04:30 | 101.53 | 85.37
2019-04-21 05:00 | 104.5 | 88.82
2019-04-21 05:30 | 106.6 | 90.98
2019-04-21 06:00 | 96.5 | 78.53
2019-04-21 06:30 | 96.02 | 78.91
2019-04-21 07:00 | 99.07 | 82.9
2019-04-21 07:30 | 97.79 | 78.37
2019-04-21 08:00 | 90 | 64.19
2019-04-21 08:30 | 88.97 | 58.2
2019-04-21 09:00 | 95.62 | 65.26
2019-04-21 09:30 | 94.35 | 66.25
2019-04-21 10:00 | 100.86 | 80.1
2019-04-21 10:30 | 106.62 | 86.85
2019-04-21 11:00 | 100.59 | 78.41
2019-04-21 11:30 | 100.26 | 78.64
2019-04-21 12:00 | 95.9 | 73.01
2019-04-21 12:30 | 98.27 | 75.75
2019-04-21 13:00 | 96.44 | 73.52
2019-04-21 13:30 | 93.9 | 71.94
2019-04-21 14:00 | 100.54 | 77.21
2019-04-21 14:30 | 92.36 | 66.72
2019-04-21 15:00 | 93.46 | 65.1
2019-04-21 15:30 | 93.99 | 65.89
2019-04-21 16:00 | 101.6 | 76.2
2019-04-21 16:30 | 96.93 | 74.51
2019-04-21 17:00 | 98.18 | 80.4
2019-04-21 17:30 | 106.49 | 92.95
2019-04-21 18:00 | 98.9 | 84.75
2019-04-21 18:30 | 104.08 | 90.55
2019-04-21 19:00 | 103.45 | 91.1
2019-04-21 19:30 | 101.62 | 88.1
2019-04-21 20:00 | 101.74 | 88.46
2019-04-21 20:30 | 105.57 | 91.61
2019-04-21 21:00 | 106.71 | 93.17
2019-04-21 21:30 | 103.27 | 89.29
2019-04-21 22:00 | 91.47 | 78.43
2019-04-21 22:30 | 89.64 | 75.92
2019-04-21 23:00 | 89.13 | 74.83
2019-04-21 23:30 | 88.54 | 72.92
2019-04-22 | 91.37 | 76.47
2019-04-22 00:30 | 93.81 | 79.94
2019-04-22 01:00 | 93.15 | 79.32
2019-04-22 01:30 | 91.44 | 76.84
2019-04-22 02:00 | 94.33 | 81.78
2019-04-22 02:30 | 91.27 | 77
2019-04-22 03:00 | 89.31 | 74.36
2019-04-22 03:30 | 88.63 | 73.19
2019-04-22 04:00 | 86.33 | 70.05
2019-04-22 04:30 | 86.3 | 70.69
2019-04-22 05:00 | 86.01 | 70.16
2019-04-22 05:30 | 89.06 | 73.19
2019-04-22 06:00 | 85.74 | 66.67
2019-04-22 06:30 | 85.98 | 67.8
2019-04-22 07:00 | 88.3 | 71.59
2019-04-22 07:30 | 87.65 | 69.41
2019-04-22 08:00 | 87.67 | 67.83
2019-04-22 08:30 | 82.79 | 59.97
2019-04-22 09:00 | 81.44 | 58.07
2019-04-22 09:30 | 78.38 | 48.76
2019-04-22 10:00 | 82.96 | 56.19
2019-04-22 10:30 | 82.7 | 56.87
2019-04-22 11:00 | 81.58 | 51.67
2019-04-22 11:30 | 84.74 | 58.7
2019-04-22 12:00 | 87.59 | 59.36
2019-04-22 12:30 | 86.72 | 55.89
2019-04-22 13:00 | 89.71 | 60.44
2019-04-22 13:30 | 85.04 | 53.04
2019-04-22 14:00 | 88.85 | 62.03
2019-04-22 14:30 | 93.01 | 66.08
2019-04-22 15:00 | 92.04 | 66.66
2019-04-22 15:30 | 91.32 | 64.03
2019-04-22 16:00 | 89.67 | 65.82
2019-04-22 16:30 | 94.35 | 75.52
2019-04-22 17:00 | 106.81 | 92.55
2019-04-22 17:30 | 108.67 | 95.27
2019-04-22 18:00 | 108.34 | 95.89
2019-04-22 18:30 | 108.93 | 95.49
2019-04-22 19:00 | 110.93 | 97.99
2019-04-22 19:30 | 112.23 | 99.39
2019-04-22 20:00 | 115.46 | 103.04
2019-04-22 20:30 | 106.9 | 94.43
2019-04-22 21:00 | 107.01 | 94.42
2019-04-22 21:30 | 101.38 | 88.07
2019-04-22 22:00 | 104.73 | 91.62
2019-04-22 22:30 | 108.67 | 95.95
2019-04-22 23:00 | 107 | 94.15
2019-04-22 23:30 | 114.55 | 102.44
2019-04-23 | 105.71 | 92.59
2019-04-23 00:30 | 106.81 | 93
2019-04-23 01:00 | 103.82 | 90.31
2019-04-23 01:30 | 108.29 | 94.26
2019-04-23 02:00 | 106.16 | 92.8
2019-04-23 02:30 | 102.35 | 88.55
2019-04-23 03:00 | 100.04 | 85.66
2019-04-23 03:30 | 96.62 | 82.52
2019-04-23 04:00 | 93.49 | 78.21
2019-04-23 04:30 | 95.75 | 80.28
2019-04-23 05:00 | 102.86 | 88.78
2019-04-23 05:30 | 105.83 | 91.16
2019-04-23 06:00 | 98.85 | 82.32
2019-04-23 06:30 | 93.26 | 76.08
2019-04-23 07:00 | 95 | 79.04
2019-04-23 07:30 | 94.07 | 78.26
2019-04-23 08:00 | 97.43 | 81.47
2019-04-23 08:30 | 92.74 | 75.23
2019-04-23 09:00 | 92.38 | 73.45
2019-04-23 09:30 | 98.85 | 78.58
2019-04-23 10:00 | 89.82 | 65.78
2019-04-23 10:30 | 94.8 | 73.24
2019-04-23 11:00 | 92.3 | 70.36
2019-04-23 11:30 | 95.22 | 75.66
2019-04-23 12:00 | 96.88 | 77.12
2019-04-23 12:30 | 94.24 | 66.41
2019-04-23 13:00 | 97.67 | 74.65
2019-04-23 13:30 | 90.83 | 67
2019-04-23 14:00 | 91.43 | 70.5
2019-04-23 14:30 | 94.05 | 75.51
2019-04-23 15:00 | 98.91 | 83.55
2019-04-23 15:30 | 100.11 | 83.72
2019-04-23 16:00 | 95.11 | 76.53
2019-04-23 16:30 | 94.52 | 77.97
2019-04-23 17:00 | 96.35 | 80.42
2019-04-23 17:30 | 96.79 | 82.42
2019-04-23 18:00 | 94.95 | 79.46
2019-04-23 18:30 | 100.67 | 85.87
2019-04-23 19:00 | 101.99 | 87.88
2019-04-23 19:30 | 102.08 | 89.1
2019-04-23 20:00 | 107.94 | 95.62
2019-04-23 20:30 | 103.47 | 90.75
2019-04-23 21:00 | 99.02 | 86.85
2019-04-23 21:30 | 102.24 | 90.94
2019-04-23 22:00 | 95.27 | 80.73
2019-04-23 22:30 | 97.88 | 84.74
2019-04-23 23:00 | 101.48 | 89.26
2019-04-23 23:30 | 100.4 | 87.75
2019-04-24 | 96.3 | 81.85
2019-04-24 00:30 | 97.79 | 84.17
2019-04-24 01:00 | 95.95 | 82.08
2019-04-24 01:30 | 103.69 | 90.84
2019-04-24 02:00 | 108.1 | 95.41
2019-04-24 02:30 | 100.3 | 85.39
2019-04-24 03:00 | 110.59 | 97.06
2019-04-24 03:30 | 105.65 | 91.78
2019-04-24 04:00 | 107.24 | 93.93
2019-04-24 04:30 | 110.15 | 96.79
2019-04-24 05:00 | 109.02 | 95.47
2019-04-24 05:30 | 101.03 | 85.88
2019-04-24 06:00 | 100.42 | 85.74
2019-04-24 06:30 | 96.59 | 83.17
2019-04-24 07:00 | 97.65 | 84.85
2019-04-24 07:30 | 101.45 | 88.71
2019-04-24 08:00 | 93.43 | 77.39
2019-04-24 08:30 | 97.13 | 80.91
2019-04-24 09:00 | 94.92 | 76.78
2019-04-24 09:30 | 97.73 | 80.39
2019-04-24 10:00 | 92.63 | 73.16
2019-04-24 10:30 | 95.04 | 74.35
2019-04-24 11:00 | 98.15 | 78.52
2019-04-24 11:30 | 97.59 | 75.95
2019-04-24 12:00 | 98.83 | 79.56
2019-04-24 12:30 | 93.96 | 73.99
2019-04-24 13:00 | 97.18 | 79.49
2019-04-24 13:30 | 96.65 | 77.12
2019-04-24 14:00 | 94.31 | 75.39
2019-04-24 14:30 | 102.4 | 86
2019-04-24 15:00 | 99.86 | 81.41
2019-04-24 15:30 | 103.46 | 87.72
2019-04-24 16:00 | 101.61 | 86.33
2019-04-24 16:30 | 100.37 | 86.11
2019-04-24 17:00 | 112.5 | 101.16
2019-04-24 17:30 | 102.01 | 88.89
2019-04-24 18:00 | 103.93 | 90.91
2019-04-24 18:30 | 103.46 | 90.84
2019-04-24 19:00 | 108.68 | 96.96
2019-04-24 19:30 | 110.46 | 99.44
2019-04-24 20:00 | 110.64 | 99
2019-04-24 20:30 | 102.79 | 90.34
2019-04-24 21:00 | 102.86 | 89.52
2019-04-24 21:30 | 103.47 | 89.79
2019-04-24 22:00 | 104.92 | 91.34
2019-04-24 22:30 | 97.98 | 82.28
2019-04-24 23:00 | 104.9 | 91.27
2019-04-24 23:30 | 103.84 | 89.41
2019-04-25 | 103.22 | 88.43
2019-04-25 00:30 | 102.2 | 88.12
2019-04-25 01:00 | 104.91 | 92.4
2019-04-25 01:30 | 106.33 | 93.05
2019-04-25 02:00 | 99.82 | 84.33
2019-04-25 02:30 | 101.4 | 85.74
2019-04-25 03:00 | 103.25 | 88.47
2019-04-25 03:30 | 103.35 | 89.48
2019-04-25 04:00 | 109.28 | 96.35
2019-04-25 04:30 | 103.16 | 88.27
2019-04-25 05:00 | 104.62 | 89.99
2019-04-25 05:30 | 97.57 | 81.15
2019-04-25 06:00 | 99.04 | 83.53
2019-04-25 06:30 | 94.53 | 77.12
2019-04-25 07:00 | 92.61 | 75.36
2019-04-25 07:30 | 92.01 | 73.75
2019-04-25 08:00 | 93.59 | 73.51
2019-04-25 08:30 | 95.81 | 77.83
2019-04-25 09:00 | 88.71 | 68.21
2019-04-25 09:30 | 90.94 | 70.69
2019-04-25 10:00 | 92.76 | 71.96
2019-04-25 10:30 | 94.17 | 73.32
2019-04-25 11:00 | 92.5 | 70.3
2019-04-25 11:30 | 89.6 | 66.51
2019-04-25 12:00 | 94.36 | 74.31
2019-04-25 12:30 | 89.3 | 67.8
2019-04-25 13:00 | 87.79 | 67.45
2019-04-25 13:30 | 89.13 | 67.23
2019-04-25 14:00 | 90.62 | 70.12
2019-04-25 14:30 | 94.04 | 75.04
2019-04-25 15:00 | 98.37 | 82.64
2019-04-25 15:30 | 101.15 | 86.91
2019-04-25 16:00 | 101.31 | 87.48
2019-04-25 16:30 | 95.29 | 80.47
2019-04-25 17:00 | 95.8 | 81.38
2019-04-25 17:30 | 96.2 | 82.35
2019-04-25 18:00 | 94.14 | 80.43
2019-04-25 18:30 | 98.7 | 87.22
2019-04-25 19:00 | 93.76 | 81.69
2019-04-25 19:30 | 98.71 | 87.94
2019-04-25 20:00 | 100.27 | 89.64
2019-04-25 20:30 | 97.35 | 85.43
2019-04-25 21:00 | 99.63 | 87.62
2019-04-25 21:30 | 100.16 | 88.39
2019-04-25 22:00 | 98.9 | 86.2
2019-04-25 22:30 | 99.26 | 87.02
2019-04-25 23:00 | 100.2 | 88.38
2019-04-25 23:30 | 95.69 | 82.36
2019-04-26 | 98.01 | 85.71
2019-04-26 00:30 | 94.55 | 80.48
2019-04-26 01:00 | 94.35 | 79.98
2019-04-26 01:30 | 105.87 | 93.85
2019-04-26 02:00 | 103.81 | 91.56
2019-04-26 02:30 | 92.05 | 76.58
2019-04-26 03:00 | 96.79 | 81.99
2019-04-26 03:30 | 91.23 | 74.09
2019-04-26 04:00 | 95.62 | 80.22
2019-04-26 04:30 | 94.73 | 79.64
2019-04-26 05:00 | 97.24 | 83.92
2019-04-26 05:30 | 102.14 | 90.47
2019-04-26 06:00 | 99.66 | 87.22
2019-04-26 06:30 | 89.29 | 74.76
2019-04-26 07:00 | 92.39 | 79.09
2019-04-26 07:30 | 101.4 | 90.02
2019-04-26 08:00 | 97.28 | 83.59
2019-04-26 08:30 | 95.59 | 81.5
2019-04-26 09:00 | 93.08 | 78.3
2019-04-26 09:30 | 94.21 | 79.09
2019-04-26 10:00 | 91.9 | 74.15
2019-04-26 10:30 | 88.84 | 68.6
2019-04-26 11:00 | 86.89 | 65.42
2019-04-26 11:30 | 87.34 | 67.56
2019-04-26 12:00 | 86.63 | 65.94
2019-04-26 12:30 | 89.2 | 71.09
2019-04-26 13:00 | 91.46 | 75.77
2019-04-26 13:30 | 89.81 | 72.43
2019-04-26 14:00 | 95.52 | 79.5
2019-04-26 14:30 | 94.49 | 78.66
2019-04-26 15:00 | 92.58 | 75.93
2019-04-26 15:30 | 92.41 | 76.57
2019-04-26 16:00 | 101.55 | 89.29
2019-04-26 16:30 | 96.83 | 84.09
2019-04-26 17:00 | 103.47 | 91.98
2019-04-26 17:30 | 97.51 | 85.21
2019-04-26 18:00 | 96.84 | 84.41
2019-04-26 18:30 | 96.84 | 84.31
2019-04-26 19:00 | 107.04 | 96.8
2019-04-26 19:30 | 107.8 | 97.57
2019-04-26 20:00 | 102.54 | 90.98
2019-04-26 20:30 | 105.11 | 94.24
2019-04-26 21:00 | 107.3 | 96.33
2019-04-26 21:30 | 107.27 | 96.47
2019-04-26 22:00 | 99.1 | 86.08
2019-04-26 22:30 | 102.54 | 90.16
2019-04-26 23:00 | 95.42 | 81.08
2019-04-26 23:30 | 100.88 | 87.68
2019-04-27 | 94.87 | 81.21
2019-04-27 00:30 | 93.58 | 80.01
2019-04-27 01:00 | 95.62 | 83.19
2019-04-27 01:30 | 96.76 | 83.9
2019-04-27 02:00 | 100.81 | 88.61
2019-04-27 02:30 | 98.28 | 84.87
2019-04-27 03:00 | 100.33 | 86.74
2019-04-27 03:30 | 99.62 | 85.01
2019-04-27 04:00 | 99.66 | 85.07
2019-04-27 04:30 | 95.45 | 80.19
2019-04-27 05:00 | 95.26 | 78.57
2019-04-27 05:30 | 104.68 | 90.35
2019-04-27 06:00 | 105.49 | 89.83
2019-04-27 06:30 | 95.89 | 78.53
2019-04-27 07:00 | 102.07 | 87.48
2019-04-27 07:30 | 105.09 | 91.79
2019-04-27 08:00 | 103.29 | 86.41
2019-04-27 08:30 | 101.22 | 78.61
2019-04-27 09:00 | 98.29 | 76.75
2019-04-27 09:30 | 96.24 | 68.48
2019-04-27 10:00 | 94.49 | 66.61
2019-04-27 10:30 | 99.35 | 69.53
2019-04-27 11:00 | 97.26 | 63.79
2019-04-27 11:30 | 100.39 | 70.03
2019-04-27 12:00 | 99.56 | 73.77
2019-04-27 12:30 | 103.16 | 76.3
2019-04-27 13:00 | 101.99 | 72.45
2019-04-27 13:30 | 103.89 | 74.17
2019-04-27 14:00 | 104.11 | 76.02
2019-04-27 14:30 | 102.52 | 80.58
2019-04-27 15:00 | 105.87 | 80.5
2019-04-27 15:30 | 98.62 | 66.37
2019-04-27 16:00 | 106.2 | 76.93
2019-04-27 16:30 | 102.01 | 82.31
2019-04-27 17:00 | 106.12 | 86.95
2019-04-27 17:30 | 112.62 | 97.61
2019-04-27 18:00 | 110.01 | 95.67
2019-04-27 18:30 | 118.78 | 104.74
2019-04-27 19:00 | 125.7 | 110.56
2019-04-27 19:30 | 120.97 | 106.14
2019-04-27 20:00 | 129.64 | 113.44
2019-04-27 20:30 | 122.95 | 106.26
2019-04-27 21:00 | 128.57 | 113
2019-04-27 21:30 | 121.04 | 104.89
2019-04-27 22:00 | 115.33 | 99.79
2019-04-27 22:30 | 121.58 | 106.66
2019-04-27 23:00 | 111.42 | 95.19
2019-04-27 23:30 | 113.76 | 97.83
2019-04-28 | 120.94 | 105.27
2019-04-28 00:30 | 119.96 | 104.85
2019-04-28 01:00 | 113.37 | 97.86
2019-04-28 01:30 | 119.05 | 103.28
2019-04-28 02:00 | 114.92 | 99.23
2019-04-28 02:30 | 119.31 | 102.63
2019-04-28 03:00 | 114.93 | 98.77
2019-04-28 03:30 | 115.14 | 99.25
2019-04-28 04:00 | 115.26 | 98.81
2019-04-28 04:30 | 109.1 | 92.89
2019-04-28 05:00 | 112.54 | 97.59
2019-04-28 05:30 | 109.03 | 94.07
2019-04-28 06:00 | 105.38 | 89.26
2019-04-28 06:30 | 103.45 | 87.37
2019-04-28 07:00 | 101.38 | 84.45
2019-04-28 07:30 | 99.37 | 80.34
2019-04-28 08:00 | 91.71 | 66.53
2019-04-28 08:30 | 94.08 | 64.9
2019-04-28 09:00 | 101.33 | 70.24
2019-04-28 09:30 | 104.88 | 74.57
2019-04-28 10:00 | 104.07 | 73.05
2019-04-28 10:30 | 107.72 | 77.6
2019-04-28 11:00 | 107.12 | 76.52
2019-04-28 11:30 | 102.34 | 73.48
2019-04-28 12:00 | 112.91 | 83.39
2019-04-28 12:30 | 105.65 | 73.71
2019-04-28 13:00 | 101.94 | 69.77
2019-04-28 13:30 | 102.08 | 70.47
2019-04-28 14:00 | 104.97 | 74.36
2019-04-28 14:30 | 105.59 | 74.96
2019-04-28 15:00 | 105.16 | 73.89
2019-04-28 15:30 | 99.65 | 68.65
2019-04-28 16:00 | 103.27 | 73.08
2019-04-28 16:30 | 102.45 | 77.67
2019-04-28 17:00 | 112.72 | 93.12
2019-04-28 17:30 | 113.46 | 96.55
2019-04-28 18:00 | 109.68 | 93.56
2019-04-28 18:30 | 114.51 | 99.36
2019-04-28 19:00 | 112.61 | 97.94
2019-04-28 19:30 | 118.8 | 105.3
2019-04-28 20:00 | 124.19 | 109.61
2019-04-28 20:30 | 123.28 | 109.55
2019-04-28 21:00 | 120.6 | 106.69
2019-04-28 21:30 | 119.61 | 105.57
2019-04-28 22:00 | 114.75 | 100.84
2019-04-28 22:30 | 120.91 | 107.89
2019-04-28 23:00 | 116.61 | 102.4
2019-04-28 23:30 | 112.13 | 97.5
2019-04-29 | 118.14 | 104.17
2019-04-29 00:30 | 117.71 | 102.52
2019-04-29 01:00 | 117.69 | 103.11
2019-04-29 01:30 | 111.29 | 95.98
2019-04-29 02:00 | 114.99 | 100.21
2019-04-29 02:30 | 119.59 | 105.89
2019-04-29 03:00 | 119.22 | 105.02
2019-04-29 03:30 | 120.72 | 105.57
2019-04-29 04:00 | 117.62 | 102.84
2019-04-29 04:30 | 118.07 | 104.11
2019-04-29 05:00 | 116.92 | 102.64
2019-04-29 05:30 | 118.49 | 103.69
2019-04-29 06:00 | 115.87 | 100.29
2019-04-29 06:30 | 111.42 | 95.47
2019-04-29 07:00 | 113.09 | 97.71
2019-04-29 07:30 | 111.96 | 95.7
2019-04-29 08:00 | 111.9 | 93.57
2019-04-29 08:30 | 108.12 | 82.27
2019-04-29 09:00 | 103.6 | 74.37
2019-04-29 09:30 | 108.08 | 76.69
2019-04-29 10:00 | 103.15 | 70.74
2019-04-29 10:30 | 105.84 | 74.36
2019-04-29 11:00 | 101.69 | 69.97
2019-04-29 11:30 | 103.79 | 73.74
2019-04-29 12:00 | 103.95 | 73.58
2019-04-29 12:30 | 101.72 | 69.94
2019-04-29 13:00 | 100.09 | 68.59
2019-04-29 13:30 | 105.6 | 74.69
2019-04-29 14:00 | 106.44 | 75.67
2019-04-29 14:30 | 110.81 | 79.35
2019-04-29 15:00 | 101.91 | 73.23
2019-04-29 15:30 | 104.02 | 74.66
2019-04-29 16:00 | 107.89 | 79.14
2019-04-29 16:30 | 109.63 | 84.8
2019-04-29 17:00 | 111.64 | 91.28
2019-04-29 17:30 | 125.67 | 108.96
2019-04-29 18:00 | 116.19 | 99.93
2019-04-29 18:30 | 114.35 | 98.67
2019-04-29 19:00 | 119.07 | 104.07
2019-04-29 19:30 | 125.06 | 110.16
2019-04-29 20:00 | 118.42 | 104.19
2019-04-29 20:30 | 122.13 | 107.3
2019-04-29 21:00 | 120.06 | 104.96
2019-04-29 21:30 | 117.56 | 101.66
2019-04-29 22:00 | 116.92 | 101.04
2019-04-29 22:30 | 119.37 | 102.93
2019-04-29 23:00 | 116.3 | 98.34
2019-04-29 23:30 | 115.86 | 97.76
2019-04-30 | 122.05 | 105.85
2019-04-30 00:30 | 125.19 | 108.95
2019-04-30 01:00 | 120.3 | 104.44
2019-04-30 01:30 | 122.1 | 106.35
2019-04-30 02:00 | 120.43 | 103.95
2019-04-30 02:30 | 122.08 | 105.46
2019-04-30 03:00 | 126.18 | 110
2019-04-30 03:30 | 123.87 | 107.79
2019-04-30 04:00 | 119.81 | 103.9
2019-04-30 04:30 | 122.72 | 106.84
2019-04-30 05:00 | 121.06 | 104.78
2019-04-30 05:30 | 121.83 | 104.51
2019-04-30 06:00 | 122.41 | 106.09
2019-04-30 06:30 | 115.33 | 97.79
2019-04-30 07:00 | 114.86 | 97.18
2019-04-30 07:30 | 120.08 | 102.78
2019-04-30 08:00 | 120.81 | 103.69
2019-04-30 08:30 | 122.54 | 105.57
2019-04-30 09:00 | 116.89 | 97.94
2019-04-30 09:30 | 109.71 | 80.37
2019-04-30 10:00 | 107.61 | 75.87
2019-04-30 10:30 | 108.81 | 79.94
2019-04-30 11:00 | 110.11 | 87.45
2019-04-30 11:30 | 109.6 | 81.28
2019-04-30 12:00 | 105.25 | 75.53
2019-04-30 12:30 | 103.97 | 78.68
2019-04-30 13:00 | 106.34 | 81.82
2019-04-30 13:30 | 118.05 | 97.53
2019-04-30 14:00 | 113.58 | 93.05
2019-04-30 14:30 | 119.16 | 101.23
2019-04-30 15:00 | 106.95 | 88.18
2019-04-30 15:30 | 102.49 | 82.48
2019-04-30 16:00 | 108.3 | 88.99
2019-04-30 16:30 | 108.95 | 88.17
2019-04-30 17:00 | 109.91 | 93.32
2019-04-30 17:30 | 113.82 | 97.86
2019-04-30 18:00 | 116.22 | 100.07
2019-04-30 18:30 | 112.29 | 97.02
2019-04-30 19:00 | 117.85 | 102.07
2019-04-30 19:30 | 127.42 | 113.47
2019-04-30 20:00 | 120.6 | 107.3
2019-04-30 20:30 | 115.1 | 100.32
2019-04-30 21:00 | 124.8 | 110.71
2019-04-30 21:30 | 118.21 | 102.56
2019-04-30 22:00 | 114.31 | 97.53
2019-04-30 22:30 | 104.92 | 87.45
2019-04-30 23:00 | 108.51 | 91.28
2019-04-30 23:30 | 113.29 | 97.8
2019-05-01 | 110.05 | 92.9
2019-05-01 00:30 | 113.18 | 96.43
2019-05-01 01:00 | 114.1 | 97.18
2019-05-01 01:30 | 113.05 | 96.94
2019-05-01 02:00 | 113.22 | 96.61
2019-05-01 02:30 | 112.72 | 96.06
2019-05-01 03:00 | 115.69 | 98.68
2019-05-01 03:30 | 109.9 | 92.78
2019-05-01 04:00 | 114.53 | 99.55
2019-05-01 04:30 | 113.48 | 98.19
2019-05-01 05:00 | 113.09 | 96.28
2019-05-01 05:30 | 114.15 | 98.97
2019-05-01 06:00 | 109.98 | 92.92
2019-05-01 06:30 | 103.15 | 86.18
2019-05-01 07:00 | 106.39 | 90.29
2019-05-01 07:30 | 107.22 | 90.14
2019-05-01 08:00 | 103.7 | 86.17
2019-05-01 08:30 | 100.3 | 74.23
2019-05-01 09:00 | 105.58 | 79.43
2019-05-01 09:30 | 103.47 | 75.98
2019-05-01 10:00 | 100.7 | 75.88
2019-05-01 10:30 | 95.27 | 66.81
2019-05-01 11:00 | 97.08 | 70.85
2019-05-01 11:30 | 96.38 | 69.88
2019-05-01 12:00 | 103.87 | 79.88
2019-05-01 12:30 | 99.33 | 72.84
2019-05-01 13:00 | 95.94 | 63.22
2019-05-01 13:30 | 94.66 | 60.96
2019-05-01 14:00 | 92.18 | 61.72
2019-05-01 14:30 | 95.57 | 69.44
2019-05-01 15:00 | 99.63 | 72.49
2019-05-01 15:30 | 102.51 | 78.04
2019-05-01 16:00 | 105.89 | 82.44
2019-05-01 16:30 | 105.38 | 84.12
2019-05-01 17:00 | 105.19 | 86.01
2019-05-01 17:30 | 116.76 | 101.21
2019-05-01 18:00 | 117.01 | 101.67
2019-05-01 18:30 | 109.02 | 93.51
2019-05-01 19:00 | 116.45 | 102.34
2019-05-01 19:30 | 117.03 | 102.25
2019-05-01 20:00 | 121.23 | 105.91
2019-05-01 20:30 | 115.87 | 98.42
2019-05-01 21:00 | 116.03 | 98.35
2019-05-01 21:30 | 114.71 | 95.46
2019-05-01 22:00 | 107.96 | 86.58
2019-05-01 22:30 | 113.23 | 93.84
2019-05-01 23:00 | 109.48 | 89.35
2019-05-01 23:30 | 114.4 | 94.38
2019-05-02 | 116 | 95.47
2019-05-02 00:30 | 113.28 | 92.4
2019-05-02 01:00 | 113.7 | 91.88
2019-05-02 01:30 | 116.89 | 97.95
2019-05-02 02:00 | 123.35 | 105.97
2019-05-02 02:30 | 119.59 | 100.65
2019-05-02 03:00 | 118.35 | 99.02
2019-05-02 03:30 | 113.74 | 94.65
2019-05-02 04:00 | 117.15 | 98.82
2019-05-02 04:30 | 114.12 | 94.45
2019-05-02 05:00 | 112.26 | 92.83
2019-05-02 05:30 | 118.49 | 99.4
2019-05-02 06:00 | 114.59 | 92.92
2019-05-02 06:30 | 112 | 89.47
2019-05-02 07:00 | 121.75 | 102.65
2019-05-02 07:30 | 116.19 | 95.16
2019-05-02 08:00 | 117.94 | 98.14
2019-05-02 08:30 | 117.02 | 96.72
2019-05-02 09:00 | 108.3 | 84.02
2019-05-02 09:30 | 114.98 | 93.36
2019-05-02 10:00 | 111.17 | 87.06
2019-05-02 10:30 | 116.49 | 94.64
2019-05-02 11:00 | 110.96 | 85.55
2019-05-02 11:30 | 106.07 | 80.34
2019-05-02 12:00 | 105.45 | 74.49
2019-05-02 12:30 | 110.6 | 85.88
2019-05-02 13:00 | 111.01 | 86.58
2019-05-02 13:30 | 108.98 | 85.25
2019-05-02 14:00 | 109.59 | 84.53
2019-05-02 14:30 | 109.56 | 84.58
2019-05-02 15:00 | 112.99 | 90.75
2019-05-02 15:30 | 113.38 | 92.17
2019-05-02 16:00 | 113.74 | 92.72
2019-05-02 16:30 | 119.81 | 101.35
2019-05-02 17:00 | 124.63 | 108.66
2019-05-02 17:30 | 108.48 | 90.38
2019-05-02 18:00 | 122.62 | 106.23
2019-05-02 18:30 | 118.79 | 102.91
2019-05-02 19:00 | 125.71 | 109.53
2019-05-02 19:30 | 123.74 | 106.92
2019-05-02 20:00 | 123.55 | 106.84
2019-05-02 20:30 | 127.84 | 109.05
2019-05-02 21:00 | 127.48 | 106.45
2019-05-02 21:30 | 123.07 | 100.12
2019-05-02 22:00 | 127.69 | 107.6
2019-05-02 22:30 | 128.37 | 107.25
2019-05-02 23:00 | 125.02 | 101.49
2019-05-02 23:30 | 120.88 | 97.44
2019-05-03 | 125.39 | 102.55
2019-05-03 00:30 | 127.11 | 105.08
2019-05-03 01:00 | 123.85 | 101.84
2019-05-03 01:30 | 125.07 | 101.11
2019-05-03 02:00 | 128.93 | 109.2
2019-05-03 02:30 | 128.84 | 109.96
2019-05-03 03:00 | 130.63 | 111.51
2019-05-03 03:30 | 124.86 | 102.88
2019-05-03 04:00 | 130.8 | 110.69
2019-05-03 04:30 | 118.96 | 95.91
2019-05-03 05:00 | 118.92 | 95.1
2019-05-03 05:30 | 124.69 | 103.08
2019-05-03 06:00 | 118.35 | 94.92
2019-05-03 06:30 | 114.37 | 89.53
2019-05-03 07:00 | 119.44 | 99.58
2019-05-03 07:30 | 123.68 | 106.63
2019-05-03 08:00 | 118.14 | 97.19
2019-05-03 08:30 | 117.14 | 92.52
2019-05-03 09:00 | 116.33 | 89.99
2019-05-03 09:30 | 120.41 | 97.84
2019-05-03 10:00 | 121.64 | 98.13
2019-05-03 10:30 | 118.03 | 93.06
2019-05-03 11:00 | 118.21 | 93.48
2019-05-03 11:30 | 119.18 | 96.48
2019-05-03 12:00 | 122.22 | 99.18
2019-05-03 12:30 | 117.18 | 89.95
2019-05-03 13:00 | 114.58 | 86.42
2019-05-03 13:30 | 115.98 | 91.13
2019-05-03 14:00 | 117.9 | 94.62
2019-05-03 14:30 | 110.41 | 85.1
2019-05-03 15:00 | 115.29 | 90.76
2019-05-03 15:30 | 120.45 | 98.12
2019-05-03 16:00 | 119.6 | 99
2019-05-03 16:30 | 113.1 | 93.09
2019-05-03 17:00 | 122.01 | 103.42
2019-05-03 17:30 | 115.53 | 93.66
2019-05-03 18:00 | 120.16 | 99.33
2019-05-03 18:30 | 110.78 | 87.33
2019-05-03 19:00 | 118.12 | 98.2
2019-05-03 19:30 | 120.69 | 101.69
2019-05-03 20:00 | 126.06 | 107.06
2019-05-03 20:30 | 126.03 | 107.69
2019-05-03 21:00 | 117.85 | 96.51
2019-05-03 21:30 | 119.76 | 96.74
2019-05-03 22:00 | 131.32 | 111.78
2019-05-03 22:30 | 118.03 | 94.39
2019-05-03 23:00 | 117.48 | 93.42
2019-05-03 23:30 | 119.83 | 97.06
2019-05-04 | 128.86 | 109.67
2019-05-04 00:30 | 129.41 | 110.43
2019-05-04 01:00 | 126.57 | 107.41
2019-05-04 01:30 | 123.57 | 103.63
2019-05-04 02:00 | 120.35 | 98.1
2019-05-04 02:30 | 119.5 | 99.16
2019-05-04 03:00 | 119.94 | 101.24
2019-05-04 03:30 | 124.16 | 102.38
2019-05-04 04:00 | 123.35 | 101.08
2019-05-04 04:30 | 122.96 | 102.46
2019-05-04 05:00 | 127.55 | 108.99
2019-05-04 05:30 | 127.04 | 109.19
2019-05-04 06:00 | 126.27 | 108.49
2019-05-04 06:30 | 123.41 | 105.43
2019-05-04 07:00 | 128.16 | 109.37
2019-05-04 07:30 | 129.52 | 112.5
2019-05-04 08:00 | 123.95 | 103.31
2019-05-04 08:30 | 118.74 | 97.69
2019-05-04 09:00 | 124.89 | 106.28
2019-05-04 09:30 | 121.22 | 101.02
2019-05-04 10:00 | 116.15 | 93.96
2019-05-04 10:30 | 114.01 | 91.01
2019-05-04 11:00 | 109.34 | 84.65
2019-05-04 11:30 | 119.06 | 95.09
2019-05-04 12:00 | 116.02 | 92.62
2019-05-04 12:30 | 120.31 | 98.16
2019-05-04 13:00 | 118.89 | 95.98
2019-05-04 13:30 | 120.68 | 99.74
2019-05-04 14:00 | 120.75 | 101.71
2019-05-04 14:30 | 127.86 | 112.35
2019-05-04 15:00 | 129.91 | 113.08
2019-05-04 15:30 | 122.58 | 102.3
2019-05-04 16:00 | 126.77 | 109.05
2019-05-04 16:30 | 122.56 | 104.02
2019-05-04 17:00 | 127.08 | 109.44
2019-05-04 17:30 | 124.12 | 105.58
2019-05-04 18:00 | 122.79 | 102.65
2019-05-04 18:30 | 118.93 | 98.18
2019-05-04 19:00 | 121.79 | 100.22
2019-05-04 19:30 | 118.81 | 97.25
2019-05-04 20:00 | 118.77 | 97.11
2019-05-04 20:30 | 118.93 | 95.6
2019-05-04 21:00 | 123.41 | 102.45
2019-05-04 21:30 | 123.76 | 103.74
2019-05-04 22:00 | 124.61 | 105.29
2019-05-04 22:30 | 121.17 | 100.74
2019-05-04 23:00 | 122.01 | 99.63
2019-05-04 23:30 | 116.02 | 91.35
2019-05-05 | 115.99 | 92.92
2019-05-05 00:30 | 118.76 | 96.28
2019-05-05 01:00 | 120.42 | 97.67
2019-05-05 01:30 | 119.64 | 97.02
2019-05-05 02:00 | 119.07 | 95.7
2019-05-05 02:30 | 124.39 | 103.33
2019-05-05 03:00 | 124.71 | 103.41
2019-05-05 03:30 | 117.89 | 94.4
2019-05-05 04:00 | 122.41 | 101.19
2019-05-05 04:30 | 120.4 | 101.75
2019-05-05 05:00 | 122.45 | 101.44
2019-05-05 05:30 | 122.28 | 102.02
2019-05-05 06:00 | 118.71 | 95.42
2019-05-05 06:30 | 119.55 | 98.23
2019-05-05 07:00 | 122.96 | 102.31
2019-05-05 07:30 | 119.61 | 94.99
2019-05-05 08:00 | 116.58 | 85.93
2019-05-05 08:30 | 115.85 | 83.42
2019-05-05 09:00 | 119.06 | 87.9
2019-05-05 09:30 | 117.01 | 87.32
2019-05-05 10:00 | 114.64 | 77.46
2019-05-05 10:30 | 117.68 | 80.56
2019-05-05 11:00 | 114.92 | 80.69
2019-05-05 11:30 | 113.72 | 82.53
2019-05-05 12:00 | 118.52 | 89.21
2019-05-05 12:30 | 118.17 | 85.71
2019-05-05 13:00 | 115.44 | 82.5
2019-05-05 13:30 | 111.33 | 79.02
2019-05-05 14:00 | 106.66 | 74.14
2019-05-05 14:30 | 111.69 | 80.22
2019-05-05 15:00 | 106.77 | 71.58
2019-05-05 15:30 | 103.54 | 65.99
2019-05-05 16:00 | 108.48 | 73.8
2019-05-05 16:30 | 112.49 | 82.67
2019-05-05 17:00 | 124.49 | 101.93
2019-05-05 17:30 | 123.98 | 103.66
2019-05-05 18:00 | 127.07 | 107.06
2019-05-05 18:30 | 125.55 | 105.46
2019-05-05 19:00 | 125.64 | 106.21
2019-05-05 19:30 | 119.91 | 97.47
2019-05-05 20:00 | 115.91 | 90.9
2019-05-05 20:30 | 121.89 | 99.88
2019-05-05 21:00 | 121.12 | 99.52
2019-05-05 21:30 | 121.83 | 98.48
2019-05-05 22:00 | 126.64 | 106.02
2019-05-05 22:30 | 122.91 | 101.56
2019-05-05 23:00 | 119.31 | 95.53
2019-05-05 23:30 | 116.35 | 92.65
2019-05-06 | 124.52 | 103.54
2019-05-06 00:30 | 123.38 | 102.05
2019-05-06 01:00 | 126.1 | 104.08
2019-05-06 01:30 | 126.83 | 104.96
2019-05-06 02:00 | 126.35 | 103.53
2019-05-06 02:30 | 128.37 | 107.61
2019-05-06 03:00 | 126.24 | 103.6
2019-05-06 03:30 | 126.24 | 103.83
2019-05-06 04:00 | 133.39 | 114.8
2019-05-06 04:30 | 125.68 | 102.39
2019-05-06 05:00 | 122.08 | 100
2019-05-06 05:30 | 125.55 | 104.53
2019-05-06 06:00 | 122.27 | 100.39
2019-05-06 06:30 | 121.64 | 99.51
2019-05-06 07:00 | 117.81 | 94.42
2019-05-06 07:30 | 109.95 | 81.73
2019-05-06 08:00 | 113.92 | 85.67
2019-05-06 08:30 | 113.58 | 84.21
2019-05-06 09:00 | 108.41 | 75.14
2019-05-06 09:30 | 112.47 | 80.07
2019-05-06 10:00 | 116.67 | 85.12
2019-05-06 10:30 | 114.02 | 81.98
2019-05-06 11:00 | 108.31 | 71.98
2019-05-06 11:30 | 110.14 | 76.22
2019-05-06 12:00 | 113.7 | 79.81
2019-05-06 12:30 | 110.63 | 75.78
2019-05-06 13:00 | 113.45 | 79.91
2019-05-06 13:30 | 115.8 | 81.93
2019-05-06 14:00 | 111.94 | 76.34
2019-05-06 14:30 | 111.62 | 73.72
2019-05-06 15:00 | 115.3 | 81.81
2019-05-06 15:30 | 114.17 | 80.67
2019-05-06 16:00 | 114.56 | 81.68
2019-05-06 16:30 | 115.93 | 86.74
2019-05-06 17:00 | 117.36 | 92.48
2019-05-06 17:30 | 122.39 | 99.48
2019-05-06 18:00 | 122.49 | 104.08
2019-05-06 18:30 | 116 | 96.14
2019-05-06 19:00 | 122.26 | 104.16
2019-05-06 19:30 | 131.87 | 116.71
2019-05-06 20:00 | 129.67 | 113.92
2019-05-06 20:30 | 124.4 | 106.14
2019-05-06 21:00 | 130.93 | 113.48
2019-05-06 21:30 | 126.22 | 106.58
2019-05-06 22:00 | 124.63 | 105.6
2019-05-06 22:30 | 125.34 | 105.83
2019-05-06 23:00 | 127.63 | 109.23
2019-05-06 23:30 | 128.57 | 109.98
2019-05-07 | 125.77 | 107.63
2019-05-07 00:30 | 122.69 | 102.08
2019-05-07 01:00 | 123.26 | 104.91
2019-05-07 01:30 | 125.82 | 107.81
2019-05-07 02:00 | 120.32 | 98.15
2019-05-07 02:30 | 120.55 | 99.16
2019-05-07 03:00 | 119.67 | 96.82
2019-05-07 03:30 | 115.95 | 93.55
2019-05-07 04:00 | 118.6 | 97.95
2019-05-07 04:30 | 119.74 | 99.13
2019-05-07 05:00 | 118.15 | 98.17
2019-05-07 05:30 | 114.31 | 93.51
2019-05-07 06:00 | 117.42 | 95.5
2019-05-07 06:30 | 112.96 | 88.22
2019-05-07 07:00 | 112 | 86.12
2019-05-07 07:30 | 111.77 | 86.07
2019-05-07 08:00 | 109.23 | 77.07
2019-05-07 08:30 | 109 | 71.25
2019-05-07 09:00 | 110.33 | 73.58
2019-05-07 09:30 | 117.72 | 84.9
2019-05-07 10:00 | 114.62 | 80.89
2019-05-07 10:30 | 122.25 | 90.33
2019-05-07 11:00 | 111.47 | 74.9
2019-05-07 11:30 | 113.49 | 78.27
2019-05-07 12:00 | 112.9 | 68.87
2019-05-07 12:30 | 111.42 | 73.48
2019-05-07 13:00 | 106.26 | 71.31
2019-05-07 13:30 | 110.16 | 76.65
2019-05-07 14:00 | 106.51 | 67.93
2019-05-07 14:30 | 108.39 | 67.65
2019-05-07 15:00 | 105.95 | 65.99
2019-05-07 15:30 | 108.52 | 69.98
2019-05-07 16:00 | 110 | 72.23
2019-05-07 16:30 | 109.88 | 75.16
2019-05-07 17:00 | 115.62 | 89.6
2019-05-07 17:30 | 121.86 | 101.62
2019-05-07 18:00 | 119.95 | 98.66
2019-05-07 18:30 | 116.73 | 96.24
2019-05-07 19:00 | 121.57 | 103.55
2019-05-07 19:30 | 126.68 | 110
2019-05-07 20:00 | 123.31 | 104.51
2019-05-07 20:30 | 119.13 | 97.89
2019-05-07 21:00 | 129.14 | 111.55
2019-05-07 21:30 | 129.86 | 113.27
2019-05-07 22:00 | 124.2 | 104.69
2019-05-07 22:30 | 127.26 | 107.24
2019-05-07 23:00 | 126.32 | 107.02
2019-05-07 23:30 | 122.21 | 103.65
2019-05-08 | 119.78 | 101.87
2019-05-08 00:30 | 124.86 | 104.88
2019-05-08 01:00 | 121.96 | 101.44
2019-05-08 01:30 | 128.24 | 110
2019-05-08 02:00 | 133 | 115.42
2019-05-08 02:30 | 129.7 | 110.67
2019-05-08 03:00 | 130.45 | 111.63
2019-05-08 03:30 | 120.71 | 100.28
2019-05-08 04:00 | 120.87 | 103.3
2019-05-08 04:30 | 130.87 | 113.92
2019-05-08 05:00 | 123.99 | 106.47
2019-05-08 05:30 | 124.63 | 106.51
2019-05-08 06:00 | 125.84 | 107.24
2019-05-08 06:30 | 118.56 | 96.35
2019-05-08 07:00 | 117.16 | 95.64
2019-05-08 07:30 | 108.74 | 84.13
2019-05-08 08:00 | 107.98 | 80.07
2019-05-08 08:30 | 102.17 | 68.52
2019-05-08 09:00 | 101.73 | 68.42
2019-05-08 09:30 | 103.87 | 69.76
2019-05-08 10:00 | 104.49 | 69.94
2019-05-08 10:30 | 102.17 | 65.38
2019-05-08 11:00 | 98.62 | 61.22
2019-05-08 11:30 | 98.91 | 61.26
2019-05-08 12:00 | 105.42 | 73.53
2019-05-08 12:30 | 105.19 | 74.71
2019-05-08 13:00 | 104.18 | 74.42
2019-05-08 13:30 | 102.36 | 70.07
2019-05-08 14:00 | 106.18 | 75.71
2019-05-08 14:30 | 101.02 | 69.42
2019-05-08 15:00 | 99.06 | 66.92
2019-05-08 15:30 | 104.4 | 73.04
2019-05-08 16:00 | 104.53 | 73.68
2019-05-08 16:30 | 105.8 | 78.2
2019-05-08 17:00 | 109.5 | 86.01
2019-05-08 17:30 | 112.68 | 92.1
2019-05-08 18:00 | 110.62 | 90.64
2019-05-08 18:30 | 113.25 | 94.01
2019-05-08 19:00 | 111.65 | 91.96
2019-05-08 19:30 | 115.05 | 95.85
2019-05-08 20:00 | 116.61 | 98.96
2019-05-08 20:30 | 110.69 | 91.19
2019-05-08 21:00 | 107.54 | 87.07
2019-05-08 21:30 | 114.09 | 92.3
2019-05-08 22:00 | 116.24 | 95.46
2019-05-08 22:30 | 120.38 | 101.08
2019-05-08 23:00 | 117.66 | 97.46
2019-05-08 23:30 | 114.75 | 93.33
2019-05-09 | 113.6 | 88.82
2019-05-09 00:30 | 114.79 | 91.91
2019-05-09 01:00 | 117.43 | 95.93
2019-05-09 01:30 | 111.46 | 87.68
2019-05-09 02:00 | 109.77 | 85.51
2019-05-09 02:30 | 111.24 | 86.85
2019-05-09 03:00 | 114.35 | 91.77
2019-05-09 03:30 | 107.7 | 83.25
2019-05-09 04:00 | 108.65 | 84.6
2019-05-09 04:30 | 113.41 | 90.24
2019-05-09 05:00 | 106.6 | 80.55
2019-05-09 05:30 | 112.38 | 89.24
2019-05-09 06:00 | 110.23 | 87.29
2019-05-09 06:30 | 108.3 | 82.54
2019-05-09 07:00 | 112.93 | 88.03
2019-05-09 07:30 | 109.96 | 83.72
2019-05-09 08:00 | 110.29 | 82.12
2019-05-09 08:30 | 100.46 | 65.14
2019-05-09 09:00 | 102.64 | 64.82
2019-05-09 09:30 | 106.7 | 69.06
2019-05-09 10:00 | 104.51 | 64.1
2019-05-09 10:30 | 105.62 | 70.55
2019-05-09 11:00 | 107.17 | 70.38
2019-05-09 11:30 | 102.48 | 64.7
2019-05-09 12:00 | 103.94 | 66.11
2019-05-09 12:30 | 110.2 | 79.95
2019-05-09 13:00 | 106.12 | 75.26
2019-05-09 13:30 | 105.35 | 70.81
2019-05-09 14:00 | 107.44 | 72.58
2019-05-09 14:30 | 106.88 | 70.25
2019-05-09 15:00 | 107.46 | 75.65
2019-05-09 15:30 | 106.53 | 74.27
2019-05-09 16:00 | 111.93 | 87.67
2019-05-09 16:30 | 117.35 | 97.12
2019-05-09 17:00 | 113.1 | 91.95
2019-05-09 17:30 | 114.53 | 95.05
2019-05-09 18:00 | 113.39 | 93.86
2019-05-09 18:30 | 113.64 | 94.79
2019-05-09 19:00 | 124.04 | 108.87
2019-05-09 19:30 | 126.85 | 112.45
2019-05-09 20:00 | 117.41 | 99.87
2019-05-09 20:30 | 113.36 | 95.28
2019-05-09 21:00 | 120.54 | 104.62
2019-05-09 21:30 | 111.97 | 92.06
2019-05-09 22:00 | 118.77 | 100.79
2019-05-09 22:30 | 116.41 | 96.59
2019-05-09 23:00 | 119.85 | 102.84
2019-05-09 23:30 | 113.74 | 94.47
2019-05-10 | 111.76 | 91.38
2019-05-10 00:30 | 114.48 | 94.83
2019-05-10 01:00 | 117.91 | 98.66
2019-05-10 01:30 | 118.85 | 100.32
2019-05-10 02:00 | 118.3 | 99.82
2019-05-10 02:30 | 115.53 | 97.4
2019-05-10 03:00 | 119.88 | 102.92
2019-05-10 03:30 | 110.47 | 89.83
2019-05-10 04:00 | 118.77 | 101.28
2019-05-10 04:30 | 114.53 | 95.5
2019-05-10 05:00 | 107.36 | 86.01
2019-05-10 05:30 | 113.97 | 94.77
2019-05-10 06:00 | 107.53 | 85.73
2019-05-10 06:30 | 107.46 | 86.12
2019-05-10 07:00 | 111.07 | 90.13
2019-05-10 07:30 | 113.48 | 93.69
2019-05-10 08:00 | 118.25 | 100.98
2019-05-10 08:30 | 116.65 | 95.53
2019-05-10 09:00 | 111.13 | 85.68
2019-05-10 09:30 | 111.71 | 84.78
2019-05-10 10:00 | 110.74 | 82.05
2019-05-10 10:30 | 109.2 | 78.71
2019-05-10 11:00 | 113.18 | 86.3
2019-05-10 11:30 | 111.76 | 81.81
2019-05-10 12:00 | 111.04 | 80.69
2019-05-10 12:30 | 114.35 | 87.1
2019-05-10 13:00 | 115.6 | 89.28
2019-05-10 13:30 | 115.88 | 89.86
2019-05-10 14:00 | 112.09 | 82.28
2019-05-10 14:30 | 110.57 | 79.09
2019-05-10 15:00 | 117 | 88.87
2019-05-10 15:30 | 121.01 | 95.97
2019-05-10 16:00 | 116.94 | 90.96
2019-05-10 16:30 | 116 | 92.7
2019-05-10 17:00 | 119.64 | 100.75
2019-05-10 17:30 | 129.07 | 114.42
2019-05-10 18:00 | 130.5 | 115.65
2019-05-10 18:30 | 125.34 | 108.7
2019-05-10 19:00 | 123.58 | 105.58
2019-05-10 19:30 | 126.65 | 111.09
2019-05-10 20:00 | 131.93 | 117.05
2019-05-10 20:30 | 130.64 | 115.05
2019-05-10 21:00 | 127.62 | 111.33
2019-05-10 21:30 | 125.36 | 107.37
2019-05-10 22:00 | 126.06 | 108.36
2019-05-10 22:30 | 134.47 | 119.02
2019-05-10 23:00 | 128.02 | 110.54
2019-05-10 23:30 | 124.79 | 106.06
2019-05-11 | 125.72 | 106.08
2019-05-11 00:30 | 123.79 | 103.05
2019-05-11 01:00 | 125.07 | 104.68
2019-05-11 01:30 | 126.28 | 108.44
2019-05-11 02:00 | 123.25 | 100.95
2019-05-11 02:30 | 126.68 | 108.73
2019-05-11 03:00 | 124.03 | 103.25
2019-05-11 03:30 | 120.58 | 99.19
2019-05-11 04:00 | 119.81 | 96.83
2019-05-11 04:30 | 124.33 | 102.35
2019-05-11 05:00 | 123.21 | 102.44
2019-05-11 05:30 | 125.48 | 104.46
2019-05-11 06:00 | 118.44 | 94.17
2019-05-11 06:30 | 120.8 | 98.61
2019-05-11 07:00 | 120.96 | 99.94
2019-05-11 07:30 | 117.32 | 93.11
2019-05-11 08:00 | 111.92 | 82.78
2019-05-11 08:30 | 108.36 | 73.74
2019-05-11 09:00 | 112.74 | 77.4
2019-05-11 09:30 | 109.2 | 75.19
2019-05-11 10:00 | 113.8 | 83.28
2019-05-11 10:30 | 115.37 | 83.02
2019-05-11 11:00 | 112.8 | 77.93
2019-05-11 11:30 | 116.69 | 86.67
2019-05-11 12:00 | 117.26 | 84.91
2019-05-11 12:30 | 116.19 | 84.85
2019-05-11 13:00 | 113.76 | 78.41
2019-05-11 13:30 | 111.83 | 76.16
2019-05-11 14:00 | 114.14 | 79.85
2019-05-11 14:30 | 113.45 | 80.02
2019-05-11 15:00 | 118.09 | 86.13
2019-05-11 15:30 | 115.22 | 80.7
2019-05-11 16:00 | 107.29 | 69.27
2019-05-11 16:30 | 118.7 | 91.91
2019-05-11 17:00 | 119.9 | 96.8
2019-05-11 17:30 | 125.1 | 107.69
2019-05-11 18:00 | 121.81 | 102.89
2019-05-11 18:30 | 117.12 | 95.26
2019-05-11 19:00 | 123.82 | 104.87
2019-05-11 19:30 | 130.89 | 115.36
2019-05-11 20:00 | 128.4 | 112.86
2019-05-11 20:30 | 129.02 | 111.95
2019-05-11 21:00 | 126.89 | 107.89
2019-05-11 21:30 | 132.58 | 115.36
2019-05-11 22:00 | 128.4 | 109.69
2019-05-11 22:30 | 128.88 | 110.69
2019-05-11 23:00 | 128.84 | 110.47
2019-05-11 23:30 | 115.63 | 92.3
2019-05-12 | 114.99 | 93.77
2019-05-12 00:30 | 123.71 | 104.03
2019-05-12 01:00 | 120.93 | 99.62
2019-05-12 01:30 | 121.15 | 98.53
2019-05-12 02:00 | 129.42 | 108.83
2019-05-12 02:30 | 132.15 | 112.75
2019-05-12 03:00 | 126.54 | 104.74
2019-05-12 03:30 | 121.17 | 98.65
2019-05-12 04:00 | 129.22 | 107.23
2019-05-12 04:30 | 127.78 | 107
2019-05-12 05:00 | 120.37 | 95.47
2019-05-12 05:30 | 123.41 | 101.02
2019-05-12 06:00 | 117.51 | 92.9
2019-05-12 06:30 | 113.15 | 86.67
2019-05-12 07:00 | 117.33 | 92.8
2019-05-12 07:30 | 119.84 | 95.94
2019-05-12 08:00 | 115.33 | 87.29
2019-05-12 08:30 | 112.36 | 82.17
2019-05-12 09:00 | 113.25 | 82.23
2019-05-12 09:30 | 115.36 | 85.37
2019-05-12 10:00 | 113.65 | 81.28
2019-05-12 10:30 | 110.52 | 75.99
2019-05-12 11:00 | 110.61 | 76.47
2019-05-12 11:30 | 105.05 | 70.43
2019-05-12 12:00 | 107.01 | 72.28
2019-05-12 12:30 | 106.37 | 71.67
2019-05-12 13:00 | 105.34 | 71.03
2019-05-12 13:30 | 107.25 | 74.44
2019-05-12 14:00 | 111.46 | 81.5
2019-05-12 14:30 | 114.66 | 86.39
2019-05-12 15:00 | 114.66 | 88.33
2019-05-12 15:30 | 119.64 | 95.97
2019-05-12 16:00 | 118 | 94.35
2019-05-12 16:30 | 110.54 | 86.01
2019-05-12 17:00 | 117.37 | 98.86
2019-05-12 17:30 | 120.31 | 105.44
2019-05-12 18:00 | 114.01 | 98.05
2019-05-12 18:30 | 110.25 | 92.62
2019-05-12 19:00 | 111.48 | 94.2
2019-05-12 19:30 | 110.47 | 93.81
2019-05-12 20:00 | 110.91 | 94.03
2019-05-12 20:30 | 116.54 | 102.09
2019-05-12 21:00 | 117.33 | 101.34
2019-05-12 21:30 | 113.92 | 98.33
2019-05-12 22:00 | 117.27 | 101.78
2019-05-12 22:30 | 120.99 | 105.53
2019-05-12 23:00 | 119.2 | 103.07
2019-05-12 23:30 | 112.37 | 92.76
2019-05-13 | 114.71 | 95.11
2019-05-13 00:30 | 116.57 | 96.74
2019-05-13 01:00 | 120.42 | 102.34
2019-05-13 01:30 | 119.81 | 101.33
2019-05-13 02:00 | 120.95 | 101.76
2019-05-13 02:30 | 120.29 | 102.49
2019-05-13 03:00 | 125.75 | 107.27
2019-05-13 03:30 | 124.76 | 107.7
2019-05-13 04:00 | 118.03 | 98.83
2019-05-13 04:30 | 120.41 | 102.62
2019-05-13 05:00 | 116.08 | 96.35
2019-05-13 05:30 | 114.58 | 92.46
2019-05-13 06:00 | 114.61 | 92.97
2019-05-13 06:30 | 113.87 | 92.48
2019-05-13 07:00 | 118.6 | 99.8
2019-05-13 07:30 | 117.74 | 100.53
2019-05-13 08:00 | 124.61 | 106.09
2019-05-13 08:30 | 121.44 | 101.57
2019-05-13 09:00 | 119.37 | 96.04
2019-05-13 09:30 | 115.22 | 88.97
2019-05-13 10:00 | 114.6 | 89.28
2019-05-13 10:30 | 116.24 | 93.52
2019-05-13 11:00 | 111.04 | 86.71
2019-05-13 11:30 | 109.79 | 85.44
2019-05-13 12:00 | 108.36 | 80.16
2019-05-13 12:30 | 111.88 | 88.3
2019-05-13 13:00 | 112.54 | 87.9
2019-05-13 13:30 | 114.39 | 93.1
2019-05-13 14:00 | 114.09 | 95.46
2019-05-13 14:30 | 122.38 | 106.38
2019-05-13 15:00 | 119.64 | 99.07
2019-05-13 15:30 | 121.56 | 101.39
2019-05-13 16:00 | 117.88 | 99.87
2019-05-13 16:30 | 116.63 | 97.48
2019-05-13 17:00 | 123.07 | 106.11
2019-05-13 17:30 | 127.15 | 110.9
2019-05-13 18:00 | 123.03 | 106.74
2019-05-13 18:30 | 118.37 | 101.38
2019-05-13 19:00 | 118.11 | 102.5
2019-05-13 19:30 | 120.57 | 106.13
2019-05-13 20:00 | 128.97 | 113.77
2019-05-13 20:30 | 130.73 | 115.75
2019-05-13 21:00 | 123.51 | 107.45
2019-05-13 21:30 | 121.35 | 105.96
2019-05-13 22:00 | 124.48 | 109.78
2019-05-13 22:30 | 122.03 | 106.94
2019-05-13 23:00 | 123.98 | 109
2019-05-13 23:30 | 109.08 | 92.14
2019-05-14 | 114.9 | 98.03
2019-05-14 00:30 | 119 | 102.92
2019-05-14 01:00 | 118.98 | 103.49
2019-05-14 01:30 | 121.28 | 106.14
2019-05-14 02:00 | 118.05 | 102.23
2019-05-14 02:30 | 125.17 | 109.36
2019-05-14 03:00 | 123.56 | 108.18
2019-05-14 03:30 | 119.52 | 102.87
2019-05-14 04:00 | 118.35 | 101.7
2019-05-14 04:30 | 118.54 | 101.94
2019-05-14 05:00 | 113.72 | 99.4
2019-05-14 05:30 | 110.17 | 98.19
2019-05-14 06:00 | 97.48 | 84.08
2019-05-14 06:30 | 87.32 | 73.49
2019-05-14 07:00 | 87.64 | 73.94
2019-05-14 07:30 | 84.62 | 69.8
2019-05-14 08:00 | 83.67 | 64.24
2019-05-14 08:30 | 82.2 | 59.16
2019-05-14 09:00 | 87.59 | 62.61
2019-05-14 09:30 | 79.53 | 55.69
2019-05-14 10:00 | 74.82 | 48.07
2019-05-14 10:30 | 76.65 | 50.73
2019-05-14 11:00 | 80.06 | 59.57
2019-05-14 11:30 | 78.93 | 54.76
2019-05-14 12:00 | 80.84 | 59.67
2019-05-14 12:30 | 83.66 | 64.39
2019-05-14 13:00 | 81.41 | 64.37
2019-05-14 13:30 | 84.77 | 66.46
2019-05-14 14:00 | 89.44 | 69.4
2019-05-14 14:30 | 87.19 | 70.58
2019-05-14 15:00 | 86.58 | 68.42
2019-05-14 15:30 | 86.52 | 73.06
2019-05-14 16:00 | 84.33 | 70.12
2019-05-14 16:30 | 78.76 | 65.8
2019-05-14 17:00 | 83.96 | 71.03
2019-05-14 17:30 | 88.24 | 76.14
2019-05-14 18:00 | 86.91 | 75.06
2019-05-14 18:30 | 82.69 | 70.96
2019-05-14 19:00 | 88.92 | 77.44
2019-05-14 19:30 | 90.95 | 79.79
2019-05-14 20:00 | 95.57 | 83.97
2019-05-14 20:30 | 105.36 | 95.61
2019-05-14 21:00 | 101.8 | 91.44
2019-05-14 21:30 | 104.77 | 93.72
2019-05-14 22:00 | 105.24 | 94.38
2019-05-14 22:30 | 109.11 | 97.19
2019-05-14 23:00 | 115.44 | 95.33
2019-05-14 23:30 | 107.87 | 86.86
2019-05-15 | 108.47 | 87.15
2019-05-15 00:30 | 112.01 | 92.33
2019-05-15 01:00 | 115.09 | 94.7
2019-05-15 01:30 | 118.01 | 97.11
2019-05-15 02:00 | 115.16 | 95.39
2019-05-15 02:30 | 119.91 | 100.62
2019-05-15 03:00 | 121.4 | 101.54
2019-05-15 03:30 | 114.69 | 94.68
2019-05-15 04:00 | 115.46 | 96.27
2019-05-15 04:30 | 118.14 | 101.31
2019-05-15 05:00 | 116.85 | 100.21
2019-05-15 05:30 | 114.52 | 98.38
2019-05-15 06:00 | 106.89 | 88.02
2019-05-15 06:30 | 98.22 | 78.53
2019-05-15 07:00 | 107.41 | 90.57
2019-05-15 07:30 | 106.18 | 89.43
2019-05-15 08:00 | 99.73 | 76.14
2019-05-15 08:30 | 98.04 | 71.55
2019-05-15 09:00 | 101.98 | 70.5
2019-05-15 09:30 | 106.65 | 75.67
2019-05-15 10:00 | 113.07 | 78.72
2019-05-15 10:30 | 104.97 | 67.47
2019-05-15 11:00 | 103.08 | 71.65
2019-05-15 11:30 | 104.72 | 73.05
2019-05-15 12:00 | 107.84 | 74.47
2019-05-15 12:30 | 100.97 | 66.75
2019-05-15 13:00 | 102.41 | 73.71
2019-05-15 13:30 | 102.34 | 76.54
2019-05-15 14:00 | 106.13 | 79.23
2019-05-15 14:30 | 118.28 | 83.65
2019-05-15 15:00 | 116.83 | 91.83
2019-05-15 15:30 | 114.22 | 90.69
2019-05-15 16:00 | 111.87 | 89.25
2019-05-15 16:30 | 111.01 | 87.35
2019-05-15 17:00 | 124.08 | 104.89
2019-05-15 17:30 | 131.63 | 113
2019-05-15 18:00 | 119.96 | 100.7
2019-05-15 18:30 | 113.84 | 94.88
2019-05-15 19:00 | 128.39 | 110.06
2019-05-15 19:30 | 126.85 | 107.24
2019-05-15 20:00 | 129.27 | 110.98
2019-05-15 20:30 | 124.28 | 104.56
2019-05-15 21:00 | 121.76 | 102.04
2019-05-15 21:30 | 122.94 | 103.57
2019-05-15 22:00 | 120.94 | 102.59
2019-05-15 22:30 | 116.06 | 96.12
2019-05-15 23:00 | 119.81 | 100.98
2019-05-15 23:30 | 105.02 | 86.61
2019-05-16 | 115.4 | 95.8
2019-05-16 00:30 | 109.09 | 90.15
2019-05-16 01:00 | 114.67 | 95.27
2019-05-16 01:30 | 121.43 | 101.11
2019-05-16 02:00 | 123.19 | 103.41
2019-05-16 02:30 | 118.54 | 99.27
2019-05-16 03:00 | 119.83 | 100.73
2019-05-16 03:30 | 115.79 | 96.9
2019-05-16 04:00 | 118.76 | 99.61
2019-05-16 04:30 | 115.68 | 96.97
2019-05-16 05:00 | 115.09 | 98.07
2019-05-16 05:30 | 113.17 | 95.81
2019-05-16 06:00 | 104.17 | 85.41
2019-05-16 06:30 | 106.52 | 90.83
2019-05-16 07:00 | 107.81 | 92.69
2019-05-16 07:30 | 100.12 | 84.37
2019-05-16 08:00 | 109.74 | 92.82
2019-05-16 08:30 | 97.07 | 76.68
2019-05-16 09:00 | 100.44 | 74.56
2019-05-16 09:30 | 94.9 | 65.43
2019-05-16 10:00 | 95.93 | 68.27
2019-05-16 10:30 | 89.52 | 67.46
2019-05-16 11:00 | 85.57 | 67.05
2019-05-16 11:30 | 94.88 | 74.77
2019-05-16 12:00 | 92.91 | 75.75
2019-05-16 12:30 | 100.01 | 82.94
2019-05-16 13:00 | 94.6 | 75.13
2019-05-16 13:30 | 91.88 | 72.92
2019-05-16 14:00 | 93.54 | 75.1
2019-05-16 14:30 | 101.28 | 84.02
2019-05-16 15:00 | 99.41 | 84.51
2019-05-16 15:30 | 96.15 | 77.6
2019-05-16 16:00 | 97.66 | 80.83
2019-05-16 16:30 | 100.04 | 85.41
2019-05-16 17:00 | 106.5 | 91.76
2019-05-16 17:30 | 114.06 | 99.51
2019-05-16 18:00 | 105.81 | 91.64
2019-05-16 18:30 | 113.23 | 98.89
2019-05-16 19:00 | 118.29 | 100.94
2019-05-16 19:30 | 125.47 | 106.51
2019-05-16 20:00 | 125.43 | 106.08
2019-05-16 20:30 | 124.39 | 105.33
2019-05-16 21:00 | 128.28 | 109.04
2019-05-16 21:30 | 125.9 | 106.08
2019-05-16 22:00 | 124.96 | 104.25
2019-05-16 22:30 | 131.79 | 111.75
2019-05-16 23:00 | 120.31 | 99.93
2019-05-16 23:30 | 118.75 | 96.88
2019-05-17 | 119.5 | 99.6
2019-05-17 00:30 | 112.72 | 93.11
2019-05-17 01:00 | 115.18 | 94.51
2019-05-17 01:30 | 117.43 | 97.37
2019-05-17 02:00 | 121.52 | 101.92
2019-05-17 02:30 | 118.51 | 98.09
2019-05-17 03:00 | 122.76 | 101.46
2019-05-17 03:30 | 116.47 | 93.2
2019-05-17 04:00 | 126.42 | 105.98
2019-05-17 04:30 | 128.52 | 107.73
2019-05-17 05:00 | 122.75 | 101.78
2019-05-17 05:30 | 124.14 | 104.3
2019-05-17 06:00 | 119.09 | 98.07
2019-05-17 06:30 | 121.49 | 102.51
2019-05-17 07:00 | 122.9 | 103.04
2019-05-17 07:30 | 115.55 | 93.84
2019-05-17 08:00 | 118.63 | 92.78
2019-05-17 08:30 | 115.17 | 83.09
2019-05-17 09:00 | 114.8 | 78.96
2019-05-17 09:30 | 116.82 | 80.23
2019-05-17 10:00 | 110.24 | 72.83
2019-05-17 10:30 | 116.57 | 79.55
2019-05-17 11:00 | 112.48 | 72.42
2019-05-17 11:30 | 107.53 | 71.47
2019-05-17 12:00 | 103.15 | 72.62
2019-05-17 12:30 | 103.91 | 73.73
2019-05-17 13:00 | 107.3 | 79.11
2019-05-17 13:30 | 117.94 | 92.56
2019-05-17 14:00 | 115.08 | 88.39
2019-05-17 14:30 | 110.34 | 79.17
2019-05-17 15:00 | 111.99 | 75.1
2019-05-17 15:30 | 108.95 | 69.44
2019-05-17 16:00 | 115.91 | 79.01
2019-05-17 16:30 | 113.03 | 80.67
2019-05-17 17:00 | 107.76 | 81.44
2019-05-17 17:30 | 114.49 | 92.32
2019-05-17 18:00 | 117.39 | 93.13
2019-05-17 18:30 | 113.13 | 89.92
2019-05-17 19:00 | 126.17 | 103.28
2019-05-17 19:30 | 126.24 | 105.06
2019-05-17 20:00 | 134.85 | 112.64
2019-05-17 20:30 | 130.87 | 107.78
2019-05-17 21:00 | 120.59 | 98.75
2019-05-17 21:30 | 125.1 | 102.19
2019-05-17 22:00 | 123.88 | 102.41
2019-05-17 22:30 | 124.46 | 103.54
2019-05-17 23:00 | 115.37 | 92.66
2019-05-17 23:30 | 110.62 | 87.22
2019-05-18 | 118.04 | 95.85
2019-05-18 00:30 | 115.49 | 93.29
2019-05-18 01:00 | 128.32 | 106.31
2019-05-18 01:30 | 123.23 | 100.18
2019-05-18 02:00 | 124.12 | 101.67
2019-05-18 02:30 | 119.27 | 98.02
2019-05-18 03:00 | 117.97 | 97.46
2019-05-18 03:30 | 122.9 | 101.9
2019-05-18 04:00 | 122.43 | 101.6
2019-05-18 04:30 | 116.84 | 97.29
2019-05-18 05:00 | 117.75 | 97.01
2019-05-18 05:30 | 116.63 | 96.46
2019-05-18 06:00 | 117.96 | 97.66
2019-05-18 06:30 | 103.02 | 83.98
2019-05-18 07:00 | 108.28 | 88.76
2019-05-18 07:30 | 106.64 | 84.94
2019-05-18 08:00 | 103.2 | 76.23
2019-05-18 08:30 | 100.9 | 66.93
2019-05-18 09:00 | 107.6 | 74.17
2019-05-18 09:30 | 110.8 | 76.77
2019-05-18 10:00 | 106.65 | 72.01
2019-05-18 10:30 | 108.23 | 72.31
2019-05-18 11:00 | 104.17 | 62.47
2019-05-18 11:30 | 102.54 | 62.08
2019-05-18 12:00 | 109.32 | 69.12
2019-05-18 12:30 | 104.41 | 65.83
2019-05-18 13:00 | 109.25 | 69.62
2019-05-18 13:30 | 111.24 | 72.89
2019-05-18 14:00 | 112.08 | 78.45
2019-05-18 14:30 | 120.26 | 88.22
2019-05-18 15:00 | 116.05 | 83.74
2019-05-18 15:30 | 112.84 | 85.17
2019-05-18 16:00 | 111.43 | 77.82
2019-05-18 16:30 | 114.26 | 85.8
2019-05-18 17:00 | 111.89 | 87.75
2019-05-18 17:30 | 118.38 | 95.93
2019-05-18 18:00 | 113.47 | 90.65
2019-05-18 18:30 | 115.69 | 91.4
2019-05-18 19:00 | 116.92 | 93.75
2019-05-18 19:30 | 112.29 | 91.47
2019-05-18 20:00 | 112.78 | 91.05
2019-05-18 20:30 | 115.81 | 94.54
2019-05-18 21:00 | 113 | 91.62
2019-05-18 21:30 | 116.57 | 94.66
2019-05-18 22:00 | 112.62 | 91.26
2019-05-18 22:30 | 116.66 | 96.17
2019-05-18 23:00 | 108.32 | 87.55
2019-05-18 23:30 | 111.58 | 91.23
2019-05-19 | 114.49 | 95.51
2019-05-19 00:30 | 108.58 | 89.13
2019-05-19 01:00 | 103.98 | 82.48
2019-05-19 01:30 | 109.76 | 89.03
2019-05-19 02:00 | 113.54 | 93.39
2019-05-19 02:30 | 110.11 | 89.29
2019-05-19 03:00 | 113.27 | 92.72
2019-05-19 03:30 | 113.35 | 92.98
2019-05-19 04:00 | 117.19 | 98.78
2019-05-19 04:30 | 122.98 | 103.49
2019-05-19 05:00 | 115.96 | 97.63
2019-05-19 05:30 | 118.52 | 100.14
2019-05-19 06:00 | 116 | 97.83
2019-05-19 06:30 | 108.98 | 89.6
2019-05-19 07:00 | 114.79 | 95.86
2019-05-19 07:30 | 112.3 | 90.58
2019-05-19 08:00 | 107.87 | 80.32
2019-05-19 08:30 | 107.19 | 73.5
2019-05-19 09:00 | 115.34 | 79.3
2019-05-19 09:30 | 117.61 | 81.4
2019-05-19 10:00 | 115.7 | 79.64
2019-05-19 10:30 | 111.3 | 74.29
2019-05-19 11:00 | 113.57 | 78.29
2019-05-19 11:30 | 109.78 | 74.71
2019-05-19 12:00 | 110.64 | 80.74
2019-05-19 12:30 | 107.52 | 68.1
2019-05-19 13:00 | 112.06 | 73.72
2019-05-19 13:30 | 108.97 | 72.62
2019-05-19 14:00 | 111.42 | 83.68
2019-05-19 14:30 | 107.76 | 78.7
2019-05-19 15:00 | 106.96 | 79.52
2019-05-19 15:30 | 109.61 | 77.99
2019-05-19 16:00 | 111.53 | 86.18
2019-05-19 16:30 | 111.12 | 88.4
2019-05-19 17:00 | 110.91 | 87.57
2019-05-19 17:30 | 113.13 | 90.62
2019-05-19 18:00 | 113.3 | 89.81
2019-05-19 18:30 | 119.35 | 96.12
2019-05-19 19:00 | 123.17 | 101
2019-05-19 19:30 | 126.95 | 104.51
2019-05-19 20:00 | 125.49 | 100.74
2019-05-19 20:30 | 117.76 | 92.06
2019-05-19 21:00 | 114.93 | 90.15
2019-05-19 21:30 | 114.26 | 89.81
2019-05-19 22:00 | 113.21 | 88.54
2019-05-19 22:30 | 112.26 | 89.42
2019-05-19 23:00 | 115.75 | 94
2019-05-19 23:30 | 111.13 | 89.1
2019-05-20 | 120.42 | 99.27
2019-05-20 00:30 | 117.5 | 95.29
2019-05-20 01:00 | 119.49 | 98.23
2019-05-20 01:30 | 113.29 | 92.15
2019-05-20 02:00 | 114.37 | 95.11
2019-05-20 02:30 | 113.71 | 92.47
2019-05-20 03:00 | 109.44 | 87
2019-05-20 03:30 | 103.89 | 81.35
2019-05-20 04:00 | 103.48 | 82.35
2019-05-20 04:30 | 104.63 | 84.57
2019-05-20 05:00 | 100.13 | 83.71
2019-05-20 05:30 | 93.41 | 83.02
2019-05-20 06:00 | 90.22 | 80.65
2019-05-20 06:30 | 81.53 | 71.78
2019-05-20 07:00 | 92.38 | 83.07
2019-05-20 07:30 | 90.03 | 78.73
2019-05-20 08:00 | 82.43 | 66.45
2019-05-20 08:30 | 84 | 62.8
2019-05-20 09:00 | 87.39 | 60.75
2019-05-20 09:30 | 89.03 | 60.69
2019-05-20 10:00 | 88.79 | 60.38
2019-05-20 10:30 | 88.37 | 61.74
2019-05-20 11:00 | 86.74 | 59.52
2019-05-20 11:30 | 86.95 | 59.7
2019-05-20 12:00 | 86.36 | 61.36
2019-05-20 12:30 | 84.46 | 60.24
2019-05-20 13:00 | 83.27 | 54.71
2019-05-20 13:30 | 82.85 | 55.83
2019-05-20 14:00 | 86.97 | 61.87
2019-05-20 14:30 | 90.09 | 68.16
2019-05-20 15:00 | 88.42 | 65.01
2019-05-20 15:30 | 84.63 | 60.44
2019-05-20 16:00 | 86.24 | 70.73
2019-05-20 16:30 | 85.66 | 71.89
2019-05-20 17:00 | 90.61 | 75.65
2019-05-20 17:30 | 103.32 | 80.55
2019-05-20 18:00 | 103.79 | 80.36
2019-05-20 18:30 | 105.05 | 82.46
2019-05-20 19:00 | 111.75 | 89.34
2019-05-20 19:30 | 113.15 | 90.39
2019-05-20 20:00 | 116.64 | 92.5
2019-05-20 20:30 | 115.77 | 91.89
2019-05-20 21:00 | 118.09 | 91.86
2019-05-20 21:30 | 114.53 | 87.01
2019-05-20 22:00 | 116.32 | 88.28
2019-05-20 22:30 | 119.57 | 91.46
2019-05-20 23:00 | 117.1 | 89.57
2019-05-20 23:30 | 115.89 | 88.86
2019-05-21 | 116.44 | 89.39
2019-05-21 00:30 | 118.21 | 92.82
2019-05-21 01:00 | 114.46 | 88.33
2019-05-21 01:30 | 115.43 | 88.26
2019-05-21 02:00 | 119.76 | 92.58
2019-05-21 02:30 | 117.9 | 90.06
2019-05-21 03:00 | 116.53 | 88.34
2019-05-21 03:30 | 118.52 | 92.37
2019-05-21 04:00 | 119.29 | 92.89
2019-05-21 04:30 | 119.38 | 91.43
2019-05-21 05:00 | 114.93 | 85.46
2019-05-21 05:30 | 115.46 | 86.58
2019-05-21 06:00 | 116.08 | 88.94
2019-05-21 06:30 | 113.82 | 87.3
2019-05-21 07:00 | 120.16 | 97.57
2019-05-21 07:30 | 103.18 | 84.9
2019-05-21 08:00 | 105.35 | 83.79
2019-05-21 08:30 | 101.63 | 75.91
2019-05-21 09:00 | 105.33 | 76.03
2019-05-21 09:30 | 104.92 | 74.4
2019-05-21 10:00 | 109.81 | 81.97
2019-05-21 10:30 | 111.36 | 81.58
2019-05-21 11:00 | 109.73 | 78.2
2019-05-21 11:30 | 104.09 | 73.34
2019-05-21 12:00 | 105.19 | 75.69
2019-05-21 12:30 | 104.72 | 75.6
2019-05-21 13:00 | 107 | 77.83
2019-05-21 13:30 | 110.25 | 81.05
2019-05-21 14:00 | 110.5 | 81.91
2019-05-21 14:30 | 106.79 | 76.7
2019-05-21 15:00 | 106.86 | 77
2019-05-21 15:30 | 106.73 | 77.67
2019-05-21 16:00 | 105.37 | 77.21
2019-05-21 16:30 | 101.89 | 82.23
2019-05-21 17:00 | 112.34 | 94.9
2019-05-21 17:30 | 111.15 | 96
2019-05-21 18:00 | 122.95 | 106.21
2019-05-21 18:30 | 123.78 | 106.14
2019-05-21 19:00 | 128.23 | 111.56
2019-05-21 19:30 | 121.14 | 104.31
2019-05-21 20:00 | 128.26 | 112.16
2019-05-21 20:30 | 116.65 | 99.53
2019-05-21 21:00 | 109.6 | 91.52
2019-05-21 21:30 | 111.67 | 94.39
2019-05-21 22:00 | 114.02 | 97
2019-05-21 22:30 | 107.2 | 89.67
2019-05-21 23:00 | 117.02 | 100.62
2019-05-21 23:30 | 105.66 | 91.67
2019-05-22 | 103.74 | 89.65
2019-05-22 00:30 | 107.13 | 92.55
2019-05-22 01:00 | 108.57 | 92.03
2019-05-22 01:30 | 111.29 | 94.48
2019-05-22 02:00 | 109.19 | 92.85
2019-05-22 02:30 | 110.1 | 93.58
2019-05-22 03:00 | 105.79 | 89.82
2019-05-22 03:30 | 97.16 | 80.36
2019-05-22 04:00 | 99.07 | 82.7
2019-05-22 04:30 | 103.82 | 89.4
2019-05-22 05:00 | 103.26 | 90
2019-05-22 05:30 | 98.79 | 84.24
2019-05-22 06:00 | 95.06 | 79.9
2019-05-22 06:30 | 90.9 | 73.65
2019-05-22 07:00 | 100.56 | 85.46
2019-05-22 07:30 | 101.47 | 84.48
2019-05-22 08:00 | 95.2 | 72.04
2019-05-22 08:30 | 96.02 | 70.5
2019-05-22 09:00 | 95.29 | 65.15
2019-05-22 09:30 | 92.3 | 58.28
2019-05-22 10:00 | 95.34 | 65.21
2019-05-22 10:30 | 94.96 | 62.37
2019-05-22 11:00 | 93.96 | 60.75
2019-05-22 11:30 | 91.6 | 60.43
2019-05-22 12:00 | 90.8 | 56.88
2019-05-22 12:30 | 95.62 | 63.68
2019-05-22 13:00 | 100.28 | 75.22
2019-05-22 13:30 | 98.41 | 77.01
2019-05-22 14:00 | 101.31 | 80.17
2019-05-22 14:30 | 98.07 | 75.41
2019-05-22 15:00 | 93.49 | 68.84
2019-05-22 15:30 | 100.44 | 79.18
2019-05-22 16:00 | 97.44 | 75.83
2019-05-22 16:30 | 103.45 | 85.65
2019-05-22 17:00 | 104.68 | 87.62
2019-05-22 17:30 | 106.47 | 89.26
2019-05-22 18:00 | 108.66 | 92.19
2019-05-22 18:30 | 110.85 | 94.9
2019-05-22 19:00 | 110.72 | 94.97
2019-05-22 19:30 | 109.66 | 94.01
2019-05-22 20:00 | 109.37 | 93.66
2019-05-22 20:30 | 113.2 | 98.3
2019-05-22 21:00 | 118.86 | 103.86
2019-05-22 21:30 | 113.35 | 96.04
2019-05-22 22:00 | 112.01 | 93.98
2019-05-22 22:30 | 114.56 | 97.77
2019-05-22 23:00 | 113.62 | 96.21
2019-05-22 23:30 | 111.85 | 94.54
2019-05-23 | 111.46 | 91.92
2019-05-23 00:30 | 106.95 | 85.97
2019-05-23 01:00 | 110.14 | 89.53
2019-05-23 01:30 | 113.01 | 94.41
2019-05-23 02:00 | 104.19 | 86.03
2019-05-23 02:30 | 108.03 | 89.36
2019-05-23 03:00 | 111.28 | 93
2019-05-23 03:30 | 109.65 | 89.85
2019-05-23 04:00 | 113.12 | 93.95
2019-05-23 04:30 | 117.19 | 99.66
2019-05-23 05:00 | 116.4 | 99.36
2019-05-23 05:30 | 111.2 | 92.7
2019-05-23 06:00 | 111.06 | 91.3
2019-05-23 06:30 | 108.61 | 88.09
2019-05-23 07:00 | 112.86 | 94.21
2019-05-23 07:30 | 117.31 | 99.74
2019-05-23 08:00 | 105.55 | 82.7
2019-05-23 08:30 | 104.87 | 78.79
2019-05-23 09:00 | 102.94 | 70.43
2019-05-23 09:30 | 105.28 | 71.69
2019-05-23 10:00 | 99.42 | 62.69
2019-05-23 10:30 | 103.44 | 70.07
2019-05-23 11:00 | 105.32 | 73.07
2019-05-23 11:30 | 100.74 | 64.93
2019-05-23 12:00 | 96.44 | 58.35
2019-05-23 12:30 | 98.76 | 62.85
2019-05-23 13:00 | 101.74 | 69.62
2019-05-23 13:30 | 96.38 | 60.3
2019-05-23 14:00 | 102.17 | 69.32
2019-05-23 14:30 | 105.82 | 81.23
2019-05-23 15:00 | 101.65 | 72.35
2019-05-23 15:30 | 101.89 | 71.52
2019-05-23 16:00 | 102.72 | 70.38
2019-05-23 16:30 | 106.31 | 82.53
2019-05-23 17:00 | 107.21 | 86.37
2019-05-23 17:30 | 116.54 | 100.38
2019-05-23 18:00 | 116.11 | 99.29
2019-05-23 18:30 | 107.15 | 86.4
2019-05-23 19:00 | 105.4 | 85.1
2019-05-23 19:30 | 115.88 | 98.7
2019-05-23 20:00 | 115.95 | 98.1
2019-05-23 20:30 | 112.78 | 93.69
2019-05-23 21:00 | 111.76 | 92.47
2019-05-23 21:30 | 107.92 | 88.21
2019-05-23 22:00 | 111.76 | 91.58
2019-05-23 22:30 | 114.93 | 95.1
2019-05-23 23:00 | 120.65 | 102.23
2019-05-23 23:30 | 115.87 | 95.44
2019-05-24 | 116.03 | 95.79
2019-05-24 00:30 | 119.78 | 101.22
2019-05-24 01:00 | 113.5 | 93.87
2019-05-24 01:30 | 112.86 | 92.78
2019-05-24 02:00 | 115.69 | 96.41
2019-05-24 02:30 | 112.48 | 90.39
2019-05-24 03:00 | 113.62 | 92.96
2019-05-24 03:30 | 115.04 | 95.34
2019-05-24 04:00 | 116.3 | 98.52
2019-05-24 04:30 | 115.72 | 99.35
2019-05-24 05:00 | 112.77 | 96.17
2019-05-24 05:30 | 109.92 | 92.01
2019-05-24 06:00 | 113.24 | 95.94
2019-05-24 06:30 | 108.76 | 90.06
2019-05-24 07:00 | 109.69 | 91.64
2019-05-24 07:30 | 113.36 | 95.72
2019-05-24 08:00 | 113.68 | 94.81
2019-05-24 08:30 | 119.22 | 98.16
2019-05-24 09:00 | 117.36 | 92.59
2019-05-24 09:30 | 110.94 | 84.09
2019-05-24 10:00 | 115.57 | 89.12
2019-05-24 10:30 | 117.9 | 92.36
2019-05-24 11:00 | 114.35 | 88.3
2019-05-24 11:30 | 115.03 | 91.24
2019-05-24 12:00 | 112.97 | 95.41
2019-05-24 12:30 | 119.66 | 102.91
2019-05-24 13:00 | 115.46 | 97.09
2019-05-24 13:30 | 109.87 | 89.05
2019-05-24 14:00 | 114.86 | 96.19
2019-05-24 14:30 | 122.46 | 105.34
2019-05-24 15:00 | 123.81 | 105.35
2019-05-24 15:30 | 123.08 | 105.36
2019-05-24 16:00 | 119.74 | 99.51
2019-05-24 16:30 | 115.53 | 95.58
2019-05-24 17:00 | 116.13 | 100.64
2019-05-24 17:30 | 115.18 | 99.37
2019-05-24 18:00 | 115.69 | 98.77
2019-05-24 18:30 | 112.91 | 94.72
2019-05-24 19:00 | 114.71 | 97.94
2019-05-24 19:30 | 120.23 | 104.25
2019-05-24 20:00 | 118.14 | 100.15
2019-05-24 20:30 | 117.42 | 100.83
2019-05-24 21:00 | 115.16 | 98.72
2019-05-24 21:30 | 117.3 | 100.73
2019-05-24 22:00 | 111.37 | 93.12
2019-05-24 22:30 | 118.06 | 101.71
2019-05-24 23:00 | 118.74 | 101.68
2019-05-24 23:30 | 121.82 | 104.72
2019-05-25 | 119.87 | 102.4
2019-05-25 00:30 | 122.42 | 105.95
2019-05-25 01:00 | 121.49 | 103.49
2019-05-25 01:30 | 120.27 | 100.99
2019-05-25 02:00 | 121.52 | 102.44
2019-05-25 02:30 | 123.31 | 105.39
2019-05-25 03:00 | 122.13 | 103.65
2019-05-25 03:30 | 120.69 | 102.86
2019-05-25 04:00 | 119.71 | 101.86
2019-05-25 04:30 | 123.79 | 106.18
2019-05-25 05:00 | 122.32 | 103.89
2019-05-25 05:30 | 118.12 | 99.38
2019-05-25 06:00 | 111.24 | 91.31
2019-05-25 06:30 | 106.6 | 85.71
2019-05-25 07:00 | 115.24 | 98.44
2019-05-25 07:30 | 114.29 | 97.25
2019-05-25 08:00 | 103.65 | 83.89
2019-05-25 08:30 | 107.44 | 87.72
2019-05-25 09:00 | 107.44 | 88.68
2019-05-25 09:30 | 107.72 | 88.12
2019-05-25 10:00 | 114.74 | 98.83
2019-05-25 10:30 | 113.51 | 95.58
2019-05-25 11:00 | 109.44 | 91.81
2019-05-25 11:30 | 105.16 | 85.97
2019-05-25 12:00 | 114.26 | 95.12
2019-05-25 12:30 | 111.97 | 95.05
2019-05-25 13:00 | 109.41 | 91.58
2019-05-25 13:30 | 112.49 | 95.53
2019-05-25 14:00 | 118.11 | 102.84
2019-05-25 14:30 | 114.5 | 97.21
2019-05-25 15:00 | 105.18 | 81.76
2019-05-25 15:30 | 104.63 | 82.51
2019-05-25 16:00 | 106.23 | 83.96
2019-05-25 16:30 | 108.59 | 89.71
2019-05-25 17:00 | 113.1 | 96.14
2019-05-25 17:30 | 111.59 | 95.93
2019-05-25 18:00 | 110.57 | 93.57
2019-05-25 18:30 | 111.34 | 95.71
2019-05-25 19:00 | 113.28 | 98.43
2019-05-25 19:30 | 117.49 | 103.17
2019-05-25 20:00 | 120.22 | 106.25
2019-05-25 20:30 | 121.43 | 107.93
2019-05-25 21:00 | 123.34 | 109.82
2019-05-25 21:30 | 123.25 | 109.78
2019-05-25 22:00 | 116.61 | 100.79
2019-05-25 22:30 | 119.95 | 104.8
2019-05-25 23:00 | 119.97 | 103.35
2019-05-25 23:30 | 118.15 | 101.06
2019-05-26 | 114.64 | 96.69
2019-05-26 00:30 | 118.77 | 102.69
2019-05-26 01:00 | 119.54 | 103.2
2019-05-26 01:30 | 119.43 | 101.25
2019-05-26 02:00 | 118.94 | 99.94
2019-05-26 02:30 | 117.19 | 98.54
2019-05-26 03:00 | 121.18 | 102.73
2019-05-26 03:30 | 120.28 | 101.63
2019-05-26 04:00 | 119.08 | 100.64
2019-05-26 04:30 | 116.39 | 97.92
2019-05-26 05:00 | 118.87 | 101.14
2019-05-26 05:30 | 121.94 | 105.87
2019-05-26 06:00 | 111.33 | 94.55
2019-05-26 06:30 | 111.45 | 93.32
2019-05-26 07:00 | 117.81 | 100.74
2019-05-26 07:30 | 113.23 | 94.61
2019-05-26 08:00 | 105.26 | 81.88
2019-05-26 08:30 | 108.1 | 84.25
2019-05-26 09:00 | 110.56 | 85.9
2019-05-26 09:30 | 105.46 | 80.83
2019-05-26 10:00 | 102.7 | 74.06
2019-05-26 10:30 | 105.06 | 76.65
2019-05-26 11:00 | 105.02 | 76.08
2019-05-26 11:30 | 105.4 | 75.79
2019-05-26 12:00 | 107.47 | 80.9
2019-05-26 12:30 | 114.7 | 91.78
2019-05-26 13:00 | 114.48 | 89.97
2019-05-26 13:30 | 111.13 | 84.84
2019-05-26 14:00 | 115.83 | 93.92
2019-05-26 14:30 | 113.02 | 93.24
2019-05-26 15:00 | 116.71 | 96.68
2019-05-26 15:30 | 114.72 | 95.47
2019-05-26 16:00 | 116.47 | 97.48
2019-05-26 16:30 | 118.06 | 98.06
2019-05-26 17:00 | 116.87 | 99.88
2019-05-26 17:30 | 123.41 | 108.15
2019-05-26 18:00 | 116.74 | 100.56
2019-05-26 18:30 | 122.67 | 107.79
2019-05-26 19:00 | 123.21 | 107.88
2019-05-26 19:30 | 121.19 | 104.5
2019-05-26 20:00 | 120.66 | 103.31
2019-05-26 20:30 | 119.66 | 102.93
2019-05-26 21:00 | 119.93 | 102.28
2019-05-26 21:30 | 119.79 | 103.4
2019-05-26 22:00 | 120.86 | 104.85
2019-05-26 22:30 | 124.3 | 107.58
2019-05-26 23:00 | 124.52 | 108.43
2019-05-26 23:30 | 121.2 | 104.36
2019-05-27 | 121.35 | 102.11
2019-05-27 00:30 | 129.21 | 110.43
2019-05-27 01:00 | 123.49 | 102.4
2019-05-27 01:30 | 126.11 | 104.56
2019-05-27 02:00 | 128.29 | 107.25
2019-05-27 02:30 | 123.47 | 101.07
2019-05-27 03:00 | 126.83 | 104.81
2019-05-27 03:30 | 121.11 | 99.66
2019-05-27 04:00 | 116.89 | 97.35
2019-05-27 04:30 | 131.78 | 111.93
2019-05-27 05:00 | 131.68 | 111.66
2019-05-27 05:30 | 128.23 | 107.12
2019-05-27 06:00 | 128.59 | 106.95
2019-05-27 06:30 | 120.09 | 98.31
2019-05-27 07:00 | 123.69 | 102.07
2019-05-27 07:30 | 114.64 | 94.26
2019-05-27 08:00 | 106.69 | 86.63
2019-05-27 08:30 | 108.58 | 86.92
2019-05-27 09:00 | 101.89 | 72.18
2019-05-27 09:30 | 101.46 | 72.2
2019-05-27 10:00 | 107.95 | 73.52
2019-05-27 10:30 | 111.48 | 73.21
2019-05-27 11:00 | 109.51 | 70.22
2019-05-27 11:30 | 110.31 | 69.74
2019-05-27 12:00 | 109.06 | 70.52
2019-05-27 12:30 | 110.15 | 71.17
2019-05-27 13:00 | 115.54 | 77.66
2019-05-27 13:30 | 116.34 | 83.29
2019-05-27 14:00 | 118.01 | 77.35
2019-05-27 14:30 | 123.43 | 84.08
2019-05-27 15:00 | 126.22 | 90.37
2019-05-27 15:30 | 122.35 | 92.75
2019-05-27 16:00 | 116.37 | 78.6
2019-05-27 16:30 | 115.03 | 88.47
2019-05-27 17:00 | 116.58 | 93.45
2019-05-27 17:30 | 119.49 | 96.22
2019-05-27 18:00 | 117.17 | 94.6
2019-05-27 18:30 | 123.99 | 101.76
2019-05-27 19:00 | 128.85 | 105.04
2019-05-27 19:30 | 126.13 | 103.09
2019-05-27 20:00 | 130.99 | 107.76
2019-05-27 20:30 | 129.22 | 106.07
2019-05-27 21:00 | 126.56 | 102.57
2019-05-27 21:30 | 126.76 | 102.09
2019-05-27 22:00 | 131.83 | 106.43
2019-05-27 22:30 | 128.86 | 103.79
2019-05-27 23:00 | 132.17 | 108.78
2019-05-27 23:30 | 126.8 | 102.51
2019-05-28 | 125.93 | 100.76
2019-05-28 00:30 | 131.98 | 106.21
2019-05-28 01:00 | 128.52 | 101.71
2019-05-28 01:30 | 124.64 | 99.56
2019-05-28 02:00 | 131.62 | 105.91
2019-05-28 02:30 | 129.3 | 103.86
2019-05-28 03:00 | 135.1 | 111.4
2019-05-28 03:30 | 129.97 | 105.41
2019-05-28 04:00 | 123.1 | 100.39
2019-05-28 04:30 | 119.95 | 97.84
2019-05-28 05:00 | 124.89 | 103.51
2019-05-28 05:30 | 122.82 | 101.61
2019-05-28 06:00 | 125.13 | 101.95
2019-05-28 06:30 | 125.9 | 103.6
2019-05-28 07:00 | 124 | 101.44
2019-05-28 07:30 | 127.34 | 102.17
2019-05-28 08:00 | 119.18 | 87.85
2019-05-28 08:30 | 116.32 | 82.09
2019-05-28 09:00 | 122.95 | 85.62
2019-05-28 09:30 | 127.06 | 91.02
2019-05-28 10:00 | 125.45 | 89.23
2019-05-28 10:30 | 122.34 | 81.58
2019-05-28 11:00 | 120.33 | 80.48
2019-05-28 11:30 | 122.69 | 84.31
2019-05-28 12:00 | 121.3 | 81.4
2019-05-28 12:30 | 125.94 | 87.68
2019-05-28 13:00 | 125.68 | 89.12
2019-05-28 13:30 | 122.93 | 87.31
2019-05-28 14:00 | 122.41 | 87.44
2019-05-28 14:30 | 128.23 | 90.41
2019-05-28 15:00 | 121.19 | 83.98
2019-05-28 15:30 | 118.22 | 80.94
2019-05-28 16:00 | 113.51 | 75.47
2019-05-28 16:30 | 111.06 | 80.56
2019-05-28 17:00 | 124.77 | 99.66
2019-05-28 17:30 | 130.96 | 108.88
2019-05-28 18:00 | 124.61 | 101.94
2019-05-28 18:30 | 114.11 | 90.08
2019-05-28 19:00 | 123.68 | 101.44
2019-05-28 19:30 | 131.88 | 110.15
2019-05-28 20:00 | 127.45 | 103.89
2019-05-28 20:30 | 130.71 | 106.23
2019-05-28 21:00 | 131.38 | 106.75
2019-05-28 21:30 | 122.28 | 98.22
2019-05-28 22:00 | 122.56 | 99.56
2019-05-28 22:30 | 123.17 | 101.37
2019-05-28 23:00 | 122.39 | 98.72
2019-05-28 23:30 | 121.82 | 99.04
2019-05-29 | 131.07 | 109.42
2019-05-29 00:30 | 121.03 | 99.14
2019-05-29 01:00 | 124.1 | 102.33
2019-05-29 01:30 | 122.82 | 100.13
2019-05-29 02:00 | 126.28 | 103.04
2019-05-29 02:30 | 130.77 | 107.94
2019-05-29 03:00 | 124.53 | 103.9
2019-05-29 03:30 | 115.72 | 93.84
2019-05-29 04:00 | 119.01 | 98.43
2019-05-29 04:30 | 123.97 | 103.22
2019-05-29 05:00 | 119.88 | 98.35
2019-05-29 05:30 | 120.64 | 99.47
2019-05-29 06:00 | 120.95 | 97.43
2019-05-29 06:30 | 112.57 | 93.07
2019-05-29 07:00 | 113.51 | 96.69
2019-05-29 07:30 | 108.66 | 90.39
2019-05-29 08:00 | 103.44 | 84.33
2019-05-29 08:30 | 111.92 | 93.37
2019-05-29 09:00 | 100.73 | 82.97
2019-05-29 09:30 | 94.1 | 78.87
2019-05-29 10:00 | 92.37 | 70.87
2019-05-29 10:30 | 89.47 | 60.11
2019-05-29 11:00 | 91.13 | 61.94
2019-05-29 11:30 | 83.67 | 53.86
2019-05-29 12:00 | 93.34 | 64.26
2019-05-29 12:30 | 92.34 | 62.69
2019-05-29 13:00 | 91.8 | 61.09
2019-05-29 13:30 | 96.27 | 66.14
2019-05-29 14:00 | 96.76 | 65.11
2019-05-29 14:30 | 98.16 | 66.92
2019-05-29 15:00 | 93.87 | 63.29
2019-05-29 15:30 | 97.4 | 68.35
2019-05-29 16:00 | 96.82 | 70.39
2019-05-29 16:30 | 100.18 | 78.95
2019-05-29 17:00 | 106.23 | 87.8
2019-05-29 17:30 | 102.15 | 85.68
2019-05-29 18:00 | 110.99 | 94.53
2019-05-29 18:30 | 104.87 | 89.43
2019-05-29 19:00 | 105.96 | 89.09
2019-05-29 19:30 | 113.29 | 96.27
2019-05-29 20:00 | 124.48 | 107.33
2019-05-29 20:30 | 115.84 | 98.57
2019-05-29 21:00 | 118.03 | 98.79
2019-05-29 21:30 | 115.78 | 94.85
2019-05-29 22:00 | 121.69 | 100.36
2019-05-29 22:30 | 128.08 | 109.15
2019-05-29 23:00 | 119.72 | 100.41
2019-05-29 23:30 | 114.95 | 96.09
2019-05-30 | 123.55 | 104.97
2019-05-30 00:30 | 117.44 | 97.38
2019-05-30 01:00 | 110.59 | 89.84
2019-05-30 01:30 | 116.29 | 96.06
2019-05-30 02:00 | 114.34 | 94.75
2019-05-30 02:30 | 119.96 | 100.62
2019-05-30 03:00 | 124.74 | 104.52
2019-05-30 03:30 | 113.25 | 92.51
2019-05-30 04:00 | 118.07 | 99.3
2019-05-30 04:30 | 113.43 | 95.05
2019-05-30 05:00 | 119.03 | 101.1
2019-05-30 05:30 | 115.14 | 97.61
2019-05-30 06:00 | 111.52 | 91.57
2019-05-30 06:30 | 112.4 | 93.84
2019-05-30 07:00 | 120.43 | 102.22
2019-05-30 07:30 | 119.27 | 98.48
2019-05-30 08:00 | 111.11 | 89.73
2019-05-30 08:30 | 105.6 | 83.07
2019-05-30 09:00 | 102.35 | 73.9
2019-05-30 09:30 | 104.87 | 73.19
2019-05-30 10:00 | 100.97 | 68.35
2019-05-30 10:30 | 107.84 | 76.55
2019-05-30 11:00 | 113.41 | 81.11
2019-05-30 11:30 | 106.63 | 73.63
2019-05-30 12:00 | 109.25 | 77.03
2019-05-30 12:30 | 109.67 | 76.2
2019-05-30 13:00 | 111.54 | 77.93
2019-05-30 13:30 | 111.81 | 77.85
2019-05-30 14:00 | 110 | 76.98
2019-05-30 14:30 | 101.57 | 66.64
2019-05-30 15:00 | 106.7 | 77.84
2019-05-30 15:30 | 109.59 | 80.03
2019-05-30 16:00 | 110.61 | 81.07
2019-05-30 16:30 | 112.86 | 88.26
2019-05-30 17:00 | 110.36 | 90.49
2019-05-30 17:30 | 119.95 | 101.65
2019-05-30 18:00 | 114.39 | 96.22
2019-05-30 18:30 | 112.05 | 92.92
2019-05-30 19:00 | 117.99 | 98.29
2019-05-30 19:30 | 116 | 96.59
2019-05-30 20:00 | 126.51 | 106.65
2019-05-30 20:30 | 120.01 | 101.71
2019-05-30 21:00 | 117.21 | 95.75
2019-05-30 21:30 | 111.08 | 87.84
2019-05-30 22:00 | 110.57 | 87.88
2019-05-30 22:30 | 109.17 | 86.79
2019-05-30 23:00 | 114.47 | 93.02
2019-05-30 23:30 | 119.08 | 97.03
2019-05-31 | 112.24 | 89.94
2019-05-31 00:30 | 114.78 | 91.73
2019-05-31 01:00 | 116.37 | 93.63
2019-05-31 01:30 | 112.76 | 89.49
2019-05-31 02:00 | 118.54 | 95.37
2019-05-31 02:30 | 117.47 | 95.9
2019-05-31 03:00 | 115.9 | 93.42
2019-05-31 03:30 | 118.92 | 96.19
2019-05-31 04:00 | 113.76 | 90.76
2019-05-31 04:30 | 113.04 | 91.3
2019-05-31 05:00 | 122.94 | 101.37
2019-05-31 05:30 | 118.07 | 95.65
2019-05-31 06:00 | 112.96 | 91.93
2019-05-31 06:30 | 116.41 | 95.54
2019-05-31 07:00 | 115.12 | 93.53
2019-05-31 07:30 | 115.56 | 95.49
2019-05-31 08:00 | 112.71 | 88.76
2019-05-31 08:30 | 110.67 | 81.8
2019-05-31 09:00 | 120.82 | 90.95
2019-05-31 09:30 | 127.07 | 96.71
2019-05-31 10:00 | 118.28 | 87.02
2019-05-31 10:30 | 118.92 | 87.67
2019-05-31 11:00 | 115.89 | 81.33
2019-05-31 11:30 | 114.86 | 79.33
2019-05-31 12:00 | 122.78 | 92.59
2019-05-31 12:30 | 114.32 | 81.23
2019-05-31 13:00 | 121.26 | 91.94
2019-05-31 13:30 | 123.64 | 95.92
2019-05-31 14:00 | 119.51 | 91.82
2019-05-31 14:30 | 120.26 | 92.04
2019-05-31 15:00 | 119.8 | 94.19
2019-05-31 15:30 | 119.89 | 93.13
2019-05-31 16:00 | 126.29 | 102.34
2019-05-31 16:30 | 127.4 | 103.69
2019-05-31 17:00 | 130.2 | 105.99
2019-05-31 17:30 | 126.62 | 103.65
2019-05-31 18:00 | 128.94 | 106.42
2019-05-31 18:30 | 128.42 | 106.8
2019-05-31 19:00 | 132.42 | 110.48
2019-05-31 19:30 | 134.18 | 111.69
2019-05-31 20:00 | 139.58 | 116.95
2019-05-31 20:30 | 129.45 | 106.78
2019-05-31 21:00 | 133 | 109.14
2019-05-31 21:30 | 133.98 | 112.22
2019-05-31 22:00 | 133.42 | 111.37
2019-05-31 22:30 | 133.31 | 111.05
2019-05-31 23:00 | 130.56 | 108.66
2019-05-31 23:30 | 125.88 | 103.59
2019-06-01 | 121.99 | 99.44
2019-06-01 00:30 | 129.13 | 107.39
2019-06-01 01:00 | 125.82 | 101.57
2019-06-01 01:30 | 120.53 | 98.2
2019-06-01 02:00 | 125.28 | 102.92
2019-06-01 02:30 | 127.58 | 105.44
2019-06-01 03:00 | 122.43 | 100.1
2019-06-01 03:30 | 116.8 | 96.13
2019-06-01 04:00 | 120.24 | 100.59
2019-06-01 04:30 | 123.35 | 103.25
2019-06-01 05:00 | 120.62 | 100.9
2019-06-01 05:30 | 124.74 | 104.45
2019-06-01 06:00 | 119.52 | 97.6
2019-06-01 06:30 | 114.69 | 94.06
2019-06-01 07:00 | 123.54 | 103.61
2019-06-01 07:30 | 117.73 | 98.35
2019-06-01 08:00 | 125.18 | 104.42
2019-06-01 08:30 | 125.68 | 105.55
2019-06-01 09:00 | 122.76 | 101.95
2019-06-01 09:30 | 122.46 | 101.65
2019-06-01 10:00 | 124.44 | 101.42
2019-06-01 10:30 | 115.17 | 87.21
2019-06-01 11:00 | 117.35 | 88.19
2019-06-01 11:30 | 118.13 | 91.35
2019-06-01 12:00 | 124.75 | 98.28
2019-06-01 12:30 | 128.64 | 104.94
2019-06-01 13:00 | 119.75 | 95.37
2019-06-01 13:30 | 111.87 | 87.95
2019-06-01 14:00 | 105.96 | 81.01
2019-06-01 14:30 | 115.53 | 93.47
2019-06-01 15:00 | 120.21 | 98.31
2019-06-01 15:30 | 117.52 | 94.85
2019-06-01 16:00 | 118.82 | 97.42
2019-06-01 16:30 | 120.28 | 99.02
2019-06-01 17:00 | 122.9 | 103.3
2019-06-01 17:30 | 122.64 | 102.93
2019-06-01 18:00 | 121.91 | 102.48
2019-06-01 18:30 | 118.09 | 100.7
2019-06-01 19:00 | 116.85 | 100.03
2019-06-01 19:30 | 121.57 | 104.76
2019-06-01 20:00 | 121.23 | 103.68
2019-06-01 20:30 | 126.26 | 109.96
2019-06-01 21:00 | 122.24 | 104.31
2019-06-01 21:30 | 123.15 | 103.83
2019-06-01 22:00 | 120.12 | 101.7
2019-06-01 22:30 | 121.71 | 105.51
2019-06-01 23:00 | 117.61 | 100.34
2019-06-01 23:30 | 124.04 | 103.9
2019-06-02 | 124.69 | 104.99
2019-06-02 00:30 | 126.88 | 106.66
2019-06-02 01:00 | 126.6 | 106.34
2019-06-02 01:30 | 119.43 | 100.22
2019-06-02 02:00 | 119.34 | 100.03
2019-06-02 02:30 | 110.23 | 92.95
2019-06-02 03:00 | 109.89 | 91.15
2019-06-02 03:30 | 112.97 | 92.37
2019-06-02 04:00 | 112.17 | 92.87
2019-06-02 04:30 | 114.47 | 94.89
2019-06-02 05:00 | 115.79 | 97.33
2019-06-02 05:30 | 111.14 | 91.75
2019-06-02 06:00 | 108.93 | 87.6
2019-06-02 06:30 | 103.62 | 82.62
2019-06-02 07:00 | 115.96 | 95.47
2019-06-02 07:30 | 121.9 | 102.91
2019-06-02 08:00 | 115.9 | 95.82
2019-06-02 08:30 | 109.41 | 88.4
2019-06-02 09:00 | 116.41 | 98.64
2019-06-02 09:30 | 118.81 | 100.01
2019-06-02 10:00 | 117.39 | 97.1
2019-06-02 10:30 | 114.3 | 90.37
2019-06-02 11:00 | 112.44 | 85.61
2019-06-02 11:30 | 110.88 | 83.18
2019-06-02 12:00 | 115.05 | 89.89
2019-06-02 12:30 | 113.11 | 87.99
2019-06-02 13:00 | 115.39 | 89.08
2019-06-02 13:30 | 118.73 | 88.02
2019-06-02 14:00 | 107.65 | 74.72
2019-06-02 14:30 | 108.52 | 74.24
2019-06-02 15:00 | 105.31 | 73.24
2019-06-02 15:30 | 101.75 | 71.88
2019-06-02 16:00 | 99.45 | 71.28
2019-06-02 16:30 | 107.21 | 84.29
2019-06-02 17:00 | 111.36 | 85.82
2019-06-02 17:30 | 115.17 | 90.17
2019-06-02 18:00 | 114.32 | 89.62
2019-06-02 18:30 | 118.39 | 95.13
2019-06-02 19:00 | 114.87 | 93.56
2019-06-02 19:30 | 120.46 | 100.96
2019-06-02 20:00 | 121.41 | 102.78
2019-06-02 20:30 | 120.65 | 100.88
2019-06-02 21:00 | 128.71 | 107.48
2019-06-02 21:30 | 118.86 | 98.4
2019-06-02 22:00 | 110.87 | 89.55
2019-06-02 22:30 | 120.02 | 101.25
2019-06-02 23:00 | 121.3 | 104.06
2019-06-02 23:30 | 125.12 | 106.04
2019-06-03 | 123.17 | 103.02
2019-06-03 00:30 | 119.56 | 99.02
2019-06-03 01:00 | 129.71 | 109.55
2019-06-03 01:30 | 120.71 | 102.49
2019-06-03 02:00 | 118.22 | 99.64
2019-06-03 02:30 | 124.77 | 106.08
2019-06-03 03:00 | 122.29 | 101.51
2019-06-03 03:30 | 120.1 | 100.16
2019-06-03 04:00 | 122.17 | 102.41
2019-06-03 04:30 | 125.06 | 106.08
2019-06-03 05:00 | 119.25 | 101.31
2019-06-03 05:30 | 115.09 | 97.92
2019-06-03 06:00 | 109.31 | 91.1
2019-06-03 06:30 | 104.41 | 87.61
2019-06-03 07:00 | 114.52 | 96.88
2019-06-03 07:30 | 105.99 | 87.61
2019-06-03 08:00 | 94.62 | 72.93
2019-06-03 08:30 | 95.48 | 69.53
2019-06-03 09:00 | 101.81 | 71.09
2019-06-03 09:30 | 101.7 | 67.37
2019-06-03 10:00 | 105.97 | 70.85
2019-06-03 10:30 | 101.25 | 65.33
2019-06-03 11:00 | 96.65 | 60.59
2019-06-03 11:30 | 103.56 | 68.47
2019-06-03 12:00 | 104.11 | 71.52
2019-06-03 12:30 | 102.02 | 69.2
2019-06-03 13:00 | 102.47 | 65.74
2019-06-03 13:30 | 98.46 | 62.99
2019-06-03 14:00 | 101.42 | 69.17
2019-06-03 14:30 | 100.37 | 70.79
2019-06-03 15:00 | 92.9 | 63.23
2019-06-03 15:30 | 98.8 | 65.72
2019-06-03 16:00 | 107.37 | 75.47
2019-06-03 16:30 | 103.43 | 76.92
2019-06-03 17:00 | 102.06 | 82.68
2019-06-03 17:30 | 109.15 | 93.78
2019-06-03 18:00 | 98.41 | 82.24
2019-06-03 18:30 | 98.3 | 82.95
2019-06-03 19:00 | 115.15 | 98.35
2019-06-03 19:30 | 111.93 | 96.17
2019-06-03 20:00 | 127.44 | 110.15
2019-06-03 20:30 | 118.47 | 101.48
2019-06-03 21:00 | 114.17 | 95.56
2019-06-03 21:30 | 110.55 | 91.45
2019-06-03 22:00 | 106.23 | 87.4
2019-06-03 22:30 | 106.66 | 87.59
2019-06-03 23:00 | 109.57 | 88.91
2019-06-03 23:30 | 117.05 | 96.19
2019-06-04 | 111.27 | 91.34
2019-06-04 00:30 | 120.16 | 100.33
2019-06-04 01:00 | 114.29 | 94.31
2019-06-04 01:30 | 119.07 | 100.5
2019-06-04 02:00 | 112.75 | 94.62
2019-06-04 02:30 | 114.05 | 95.23
2019-06-04 03:00 | 118.46 | 99.74
2019-06-04 03:30 | 123.24 | 104.22
2019-06-04 04:00 | 125.84 | 106.34
2019-06-04 04:30 | 122.71 | 104.05
2019-06-04 05:00 | 119.77 | 101.3
2019-06-04 05:30 | 117.47 | 97.75
2019-06-04 06:00 | 121.05 | 100.41
2019-06-04 06:30 | 115.06 | 96.33
2019-06-04 07:00 | 110.14 | 92.11
2019-06-04 07:30 | 114.87 | 96.38
2019-06-04 08:00 | 106.14 | 84.06
2019-06-04 08:30 | 86.45 | 60.38
2019-06-04 09:00 | 103.76 | 75.18
2019-06-04 09:30 | 101.62 | 69.05
2019-06-04 10:00 | 106.9 | 75.06
2019-06-04 10:30 | 104.53 | 74.69
2019-06-04 11:00 | 105.39 | 74.65
2019-06-04 11:30 | 102.63 | 71.72
2019-06-04 12:00 | 100.69 | 68.87
2019-06-04 12:30 | 101.74 | 69.43
2019-06-04 13:00 | 104.55 | 72.22
2019-06-04 13:30 | 101.33 | 68.56
2019-06-04 14:00 | 105.09 | 72.3
2019-06-04 14:30 | 106.55 | 73.68
2019-06-04 15:00 | 99.98 | 63.59
2019-06-04 15:30 | 100.56 | 65.92
2019-06-04 16:00 | 104.51 | 75.05
2019-06-04 16:30 | 115.55 | 91.44
2019-06-04 17:00 | 117.04 | 96.67
2019-06-04 17:30 | 128.95 | 110.02
2019-06-04 18:00 | 120.83 | 102.05
2019-06-04 18:30 | 119.02 | 101.92
2019-06-04 19:00 | 133.56 | 116.9
2019-06-04 19:30 | 122.09 | 106.01
2019-06-04 20:00 | 129.66 | 112.82
2019-06-04 20:30 | 122.29 | 103.98
2019-06-04 21:00 | 126.83 | 106.35
2019-06-04 21:30 | 126.94 | 106.71
2019-06-04 22:00 | 115.33 | 97.45
2019-06-04 22:30 | 117.91 | 99.96
2019-06-04 23:00 | 120.06 | 101.11
2019-06-04 23:30 | 119.71 | 100.92
2019-06-05 | 126.53 | 106.65
2019-06-05 00:30 | 123.36 | 104.27
2019-06-05 01:00 | 119.41 | 101.83
2019-06-05 01:30 | 121.5 | 103.15
2019-06-05 02:00 | 115.07 | 99.43
2019-06-05 02:30 | 121.73 | 105.93
2019-06-05 03:00 | 119.92 | 103.28
2019-06-05 03:30 | 124.1 | 107.91
2019-06-05 04:00 | 124.04 | 108.21
2019-06-05 04:30 | 124.5 | 108.77
2019-06-05 05:00 | 120.62 | 106.15
2019-06-05 05:30 | 123.83 | 109.19
2019-06-05 06:00 | 119.81 | 104.83
2019-06-05 06:30 | 111.82 | 94.49
2019-06-05 07:00 | 107.95 | 88.71
2019-06-05 07:30 | 120.44 | 104.09
2019-06-05 08:00 | 117.9 | 99.35
2019-06-05 08:30 | 117.6 | 97.65
2019-06-05 09:00 | 115.68 | 91.4
2019-06-05 09:30 | 107.34 | 77.28
2019-06-05 10:00 | 107.31 | 78.02
2019-06-05 10:30 | 115.37 | 89.93
2019-06-05 11:00 | 118.74 | 92.33
2019-06-05 11:30 | 110.71 | 80.21
2019-06-05 12:00 | 115.5 | 87.57
2019-06-05 12:30 | 115.28 | 88.43
2019-06-05 13:00 | 113.46 | 86.43
2019-06-05 13:30 | 112.36 | 85.78
2019-06-05 14:00 | 113.46 | 87.08
2019-06-05 14:30 | 109.13 | 80.08
2019-06-05 15:00 | 108.55 | 80.81
2019-06-05 15:30 | 114.81 | 88.17
2019-06-05 16:00 | 114.23 | 86.69
2019-06-05 16:30 | 122.2 | 99.76
2019-06-05 17:00 | 121.8 | 101.7
2019-06-05 17:30 | 119.14 | 103.05
2019-06-05 18:00 | 116.79 | 99.74
2019-06-05 18:30 | 120.22 | 104.8
2019-06-05 19:00 | 118.45 | 102.09
2019-06-05 19:30 | 118.66 | 103.19
2019-06-05 20:00 | 117.24 | 100.53
2019-06-05 20:30 | 124.6 | 109.38
2019-06-05 21:00 | 126.11 | 110.96
2019-06-05 21:30 | 127.02 | 108.64
2019-06-05 22:00 | 138.88 | 119.26
2019-06-05 22:30 | 134.81 | 116.11
2019-06-05 23:00 | 130.69 | 108.26
2019-06-05 23:30 | 127.45 | 99.2
2019-06-06 | 131.24 | 105.27
2019-06-06 00:30 | 137.97 | 115.65
2019-06-06 01:00 | 127.66 | 101.72
2019-06-06 01:30 | 135.16 | 112.93
2019-06-06 02:00 | 130.86 | 107.51
2019-06-06 02:30 | 130.45 | 107.55
2019-06-06 03:00 | 129.96 | 105.26
2019-06-06 03:30 | 122.87 | 95.97
2019-06-06 04:00 | 126.16 | 100.52
2019-06-06 04:30 | 128.25 | 103.84
2019-06-06 05:00 | 123.58 | 97.75
2019-06-06 05:30 | 126.24 | 101.75
2019-06-06 06:00 | 120.63 | 94.85
2019-06-06 06:30 | 123.78 | 99.46
2019-06-06 07:00 | 129.8 | 106.98
2019-06-06 07:30 | 118.41 | 92.25
2019-06-06 08:00 | 113.69 | 88.7
2019-06-06 08:30 | 113.04 | 86.43
2019-06-06 09:00 | 110.25 | 88.27
2019-06-06 09:30 | 98.36 | 71.77
2019-06-06 10:00 | 99 | 70.82
2019-06-06 10:30 | 104.37 | 71.57
2019-06-06 11:00 | 105.88 | 70.01
2019-06-06 11:30 | 103.23 | 68.57
2019-06-06 12:00 | 99.93 | 67.01
2019-06-06 12:30 | 101.25 | 71.39
2019-06-06 13:00 | 100.61 | 71.29
2019-06-06 13:30 | 101.05 | 74.28
2019-06-06 14:00 | 102.8 | 76.48
2019-06-06 14:30 | 105.93 | 77.49
2019-06-06 15:00 | 118.21 | 90.57
2019-06-06 15:30 | 121.3 | 99.66
2019-06-06 16:00 | 100.62 | 79.06
2019-06-06 16:30 | 109.94 | 87.1
2019-06-06 17:00 | 115 | 92.88
2019-06-06 17:30 | 119.81 | 99.36
2019-06-06 18:00 | 129.88 | 111.45
2019-06-06 18:30 | 127.17 | 109.15
2019-06-06 19:00 | 121.28 | 102.86
2019-06-06 19:30 | 133.47 | 116.04
2019-06-06 20:00 | 134.33 | 116.94
2019-06-06 20:30 | 137.3 | 118.49
2019-06-06 21:00 | 128.34 | 110.55
2019-06-06 21:30 | 121.22 | 102.16
2019-06-06 22:00 | 126.47 | 107.82
2019-06-06 22:30 | 127.88 | 109.6
2019-06-06 23:00 | 122.77 | 104.6
2019-06-06 23:30 | 126.62 | 107.34
2019-06-07 | 140.36 | 122.28
2019-06-07 00:30 | 134.91 | 116.12
2019-06-07 01:00 | 127.9 | 109.41
2019-06-07 01:30 | 130.47 | 111.89
2019-06-07 02:00 | 131.31 | 114.94
2019-06-07 02:30 | 126.6 | 109.76
2019-06-07 03:00 | 126.91 | 109.57
2019-06-07 03:30 | 119.53 | 99.94
2019-06-07 04:00 | 114.32 | 95.12
2019-06-07 04:30 | 122.35 | 104.25
2019-06-07 05:00 | 124.39 | 105.68
2019-06-07 05:30 | 132.31 | 113.48
2019-06-07 06:00 | 121 | 102.79
2019-06-07 06:30 | 126.89 | 109.94
2019-06-07 07:00 | 128.77 | 111.72
2019-06-07 07:30 | 128.3 | 110.51
2019-06-07 08:00 | 122.06 | 102.35
2019-06-07 08:30 | 111.64 | 90.84
2019-06-07 09:00 | 115.07 | 92.24
2019-06-07 09:30 | 107.61 | 79.73
2019-06-07 10:00 | 110.25 | 79.42
2019-06-07 10:30 | 107.42 | 80.72
2019-06-07 11:00 | 112.1 | 90.37
2019-06-07 11:30 | 111.38 | 88.35
2019-06-07 12:00 | 102.59 | 77.04
2019-06-07 12:30 | 104.21 | 81.11
2019-06-07 13:00 | 107.02 | 86.16
2019-06-07 13:30 | 106.51 | 88.49
2019-06-07 14:00 | 101.82 | 83.72
2019-06-07 14:30 | 109.85 | 91.86
2019-06-07 15:00 | 108.25 | 90.06
2019-06-07 15:30 | 107.67 | 88.73
2019-06-07 16:00 | 111.3 | 93.41
2019-06-07 16:30 | 106.9 | 89.69
2019-06-07 17:00 | 111.75 | 93.94
2019-06-07 17:30 | 122.13 | 105.49
2019-06-07 18:00 | 119.43 | 101.03
2019-06-07 18:30 | 125.98 | 106.8
2019-06-07 19:00 | 121.97 | 103.54
2019-06-07 19:30 | 123.67 | 106.57
2019-06-07 20:00 | 124.05 | 106.64
2019-06-07 20:30 | 125.62 | 107.79
2019-06-07 21:00 | 123.55 | 106.14
2019-06-07 21:30 | 130.15 | 113.84
2019-06-07 22:00 | 119.61 | 104.51
2019-06-07 22:30 | 126.65 | 111.66
2019-06-07 23:00 | 127.82 | 112.52
2019-06-07 23:30 | 119.87 | 103.37
2019-06-08 | 126.15 | 109.5
2019-06-08 00:30 | 123.57 | 107.59
2019-06-08 01:00 | 118.77 | 102.79
2019-06-08 01:30 | 113.82 | 97.09
2019-06-08 02:00 | 120.09 | 103.99
2019-06-08 02:30 | 121.08 | 104.97
2019-06-08 03:00 | 121.77 | 106.15
2019-06-08 03:30 | 112.28 | 94.84
2019-06-08 04:00 | 108.79 | 91.45
2019-06-08 04:30 | 112.12 | 95.12
2019-06-08 05:00 | 112.58 | 95.85
2019-06-08 05:30 | 111.73 | 95.34
2019-06-08 06:00 | 110.13 | 93.71
2019-06-08 06:30 | 110.21 | 94.32
2019-06-08 07:00 | 116.48 | 101.75
2019-06-08 07:30 | 118.84 | 104.06
2019-06-08 08:00 | 121.76 | 107.25
2019-06-08 08:30 | 127.14 | 112.97
2019-06-08 09:00 | 120.53 | 104.54
2019-06-08 09:30 | 114.91 | 98.42
2019-06-08 10:00 | 112.1 | 95.32
2019-06-08 10:30 | 118.11 | 101.76
2019-06-08 11:00 | 111.48 | 95.37
2019-06-08 11:30 | 114.31 | 98.16
2019-06-08 12:00 | 110.03 | 93.18
2019-06-08 12:30 | 119.27 | 101.47
2019-06-08 13:00 | 110.66 | 91.45
2019-06-08 13:30 | 119.5 | 100.69
2019-06-08 14:00 | 124.85 | 106.31
2019-06-08 14:30 | 116.76 | 97.15
2019-06-08 15:00 | 114.11 | 95.31
2019-06-08 15:30 | 111.06 | 90.43
2019-06-08 16:00 | 116.07 | 96.23
2019-06-08 16:30 | 115.96 | 97.41
2019-06-08 17:00 | 122.6 | 105.24
2019-06-08 17:30 | 121.05 | 104.07
2019-06-08 18:00 | 118.11 | 100.78
2019-06-08 18:30 | 122.78 | 106.25
2019-06-08 19:00 | 121.52 | 104.53
2019-06-08 19:30 | 126.88 | 110.36
2019-06-08 20:00 | 120.12 | 103.93
2019-06-08 20:30 | 116.87 | 100.58
2019-06-08 21:00 | 114.78 | 97.84
2019-06-08 21:30 | 116.66 | 99.68
2019-06-08 22:00 | 115.58 | 98.91
2019-06-08 22:30 | 118.17 | 101.34
2019-06-08 23:00 | 120.03 | 103.92
2019-06-08 23:30 | 115.85 | 98.73
2019-06-09 | 112.2 | 94.91
2019-06-09 00:30 | 114.11 | 97.38
2019-06-09 01:00 | 112.77 | 94.66
2019-06-09 01:30 | 110.45 | 92.84
2019-06-09 02:00 | 114.68 | 97.49
2019-06-09 02:30 | 119.47 | 102.57
2019-06-09 03:00 | 116.59 | 99.46
2019-06-09 03:30 | 119.82 | 103.33
2019-06-09 04:00 | 123.04 | 106.41
2019-06-09 04:30 | 117.71 | 99.68
2019-06-09 05:00 | 121.37 | 103.88
2019-06-09 05:30 | 110.39 | 92.84
2019-06-09 06:00 | 110.06 | 92.32
2019-06-09 06:30 | 115.61 | 98.74
2019-06-09 07:00 | 107.12 | 89.35
2019-06-09 07:30 | 104.56 | 88.23
2019-06-09 08:00 | 100.61 | 85.29
2019-06-09 08:30 | 101.47 | 87.6
2019-06-09 09:00 | 105.61 | 88.67
2019-06-09 09:30 | 103.58 | 86.28
2019-06-09 10:00 | 109.45 | 90.87
2019-06-09 10:30 | 106.41 | 88.14
2019-06-09 11:00 | 98.16 | 78.7
2019-06-09 11:30 | 94.95 | 76.4
2019-06-09 12:00 | 94.16 | 76.79
2019-06-09 12:30 | 97.16 | 79.83
2019-06-09 13:00 | 110.09 | 90.02
2019-06-09 13:30 | 112.1 | 89.94
2019-06-09 14:00 | 115.33 | 93.48
2019-06-09 14:30 | 114.57 | 92.44
2019-06-09 15:00 | 112.79 | 92.65
2019-06-09 15:30 | 113.75 | 96.29
2019-06-09 16:00 | 114.93 | 97.13
2019-06-09 16:30 | 114.39 | 96.59
2019-06-09 17:00 | 116.26 | 98.34
2019-06-09 17:30 | 125.89 | 109.07
2019-06-09 18:00 | 119.19 | 102.81
2019-06-09 18:30 | 120.27 | 103.66
2019-06-09 19:00 | 119.14 | 103.11
2019-06-09 19:30 | 128.33 | 113.11
2019-06-09 20:00 | 125.64 | 108.76
2019-06-09 20:30 | 123.63 | 107.36
2019-06-09 21:00 | 115.82 | 99.21
2019-06-09 21:30 | 119.64 | 103.67
2019-06-09 22:00 | 113.67 | 97.2
2019-06-09 22:30 | 117.66 | 102.05
2019-06-09 23:00 | 116.78 | 101.52
2019-06-09 23:30 | 106.81 | 91.15
2019-06-10 | 107.02 | 91.17
2019-06-10 00:30 | 106.14 | 90.44
2019-06-10 01:00 | 107.38 | 91.74
2019-06-10 01:30 | 109.01 | 94.2
2019-06-10 02:00 | 113.62 | 99.6
2019-06-10 02:30 | 110.18 | 95.07
2019-06-10 03:00 | 101.83 | 86.16
2019-06-10 03:30 | 100.47 | 83.76
2019-06-10 04:00 | 105.02 | 87.36
2019-06-10 04:30 | 102.2 | 84.48
2019-06-10 05:00 | 104.45 | 86.66
2019-06-10 05:30 | 107.03 | 89.45
2019-06-10 06:00 | 106.83 | 91.46
2019-06-10 06:30 | 104.88 | 88.02
2019-06-10 07:00 | 104.84 | 88.14
2019-06-10 07:30 | 108.55 | 91.17
2019-06-10 08:00 | 101.39 | 79.96
2019-06-10 08:30 | 97.77 | 71.91
2019-06-10 09:00 | 98.85 | 70.27
2019-06-10 09:30 | 94.14 | 62.11
2019-06-10 10:00 | 85.85 | 62.28
2019-06-10 10:30 | 86.59 | 60.85
2019-06-10 11:00 | 85.99 | 58.68
2019-06-10 11:30 | 90.56 | 62.57
2019-06-10 12:00 | 89.92 | 64.6
2019-06-10 12:30 | 90.39 | 63.05
2019-06-10 13:00 | 93.72 | 67.64
2019-06-10 13:30 | 93.94 | 69.88
2019-06-10 14:00 | 101.04 | 75.69
2019-06-10 14:30 | 96.59 | 66.81
2019-06-10 15:00 | 95.07 | 66.82
2019-06-10 15:30 | 100.29 | 71.17
2019-06-10 16:00 | 104.06 | 77.57
2019-06-10 16:30 | 101.77 | 79.62
2019-06-10 17:00 | 105.24 | 85.74
2019-06-10 17:30 | 114.62 | 98.22
2019-06-10 18:00 | 112.3 | 96.64
2019-06-10 18:30 | 111.17 | 95
2019-06-10 19:00 | 112.27 | 96.19
2019-06-10 19:30 | 114.53 | 98.57
2019-06-10 20:00 | 114.16 | 97.94
2019-06-10 20:30 | 113.48 | 95.63
2019-06-10 21:00 | 116.54 | 99.07
2019-06-10 21:30 | 114.13 | 96.73
2019-06-10 22:00 | 118.79 | 101.35
2019-06-10 22:30 | 117.37 | 100.08
2019-06-10 23:00 | 112.79 | 96.21
2019-06-10 23:30 | 116.1 | 98.88
2019-06-11 | 113.2 | 96.17
2019-06-11 00:30 | 111.51 | 92.67
2019-06-11 01:00 | 125.41 | 107.44
2019-06-11 01:30 | 121.27 | 102.87
2019-06-11 02:00 | 116.26 | 98.37
2019-06-11 02:30 | 115.97 | 97.53
2019-06-11 03:00 | 112.15 | 93.82
2019-06-11 03:30 | 108.36 | 89.9
2019-06-11 04:00 | 110.49 | 95.92
2019-06-11 04:30 | 107.8 | 94.03
2019-06-11 05:00 | 104.63 | 90.4
2019-06-11 05:30 | 104.4 | 89.74
2019-06-11 06:00 | 97.5 | 83.71
2019-06-11 06:30 | 91.63 | 77.6
2019-06-11 07:00 | 92.14 | 78.15
2019-06-11 07:30 | 89.38 | 74.66
2019-06-11 08:00 | 83.84 | 67.52
2019-06-11 08:30 | 83.07 | 63.49
2019-06-11 09:00 | 85.6 | 63.76
2019-06-11 09:30 | 93.04 | 70.61
2019-06-11 10:00 | 96.32 | 69.71
2019-06-11 10:30 | 95.57 | 66.83
2019-06-11 11:00 | 97.61 | 71.47
2019-06-11 11:30 | 93.96 | 67.66
2019-06-11 12:00 | 99.12 | 72.77
2019-06-11 12:30 | 102.79 | 83.31
2019-06-11 13:00 | 98.2 | 79.64
2019-06-11 13:30 | 99.76 | 76.92
2019-06-11 14:00 | 95.53 | 71.93
2019-06-11 14:30 | 101.55 | 72.9
2019-06-11 15:00 | 101.91 | 73.47
2019-06-11 15:30 | 97.84 | 70.33
2019-06-11 16:00 | 100.9 | 75.14
2019-06-11 16:30 | 94.54 | 71.58
2019-06-11 17:00 | 101.38 | 81.01
2019-06-11 17:30 | 106.66 | 89.95
2019-06-11 18:00 | 110.6 | 94.47
2019-06-11 18:30 | 106.07 | 90.32
2019-06-11 19:00 | 107.72 | 91.97
2019-06-11 19:30 | 108.07 | 91.14
2019-06-11 20:00 | 108.16 | 91.36
2019-06-11 20:30 | 115.3 | 97.28
2019-06-11 21:00 | 116.01 | 96.74
2019-06-11 21:30 | 109.3 | 89.47
2019-06-11 22:00 | 112.03 | 92.54
2019-06-11 22:30 | 117.05 | 98.61
2019-06-11 23:00 | 113.63 | 96.62
2019-06-11 23:30 | 124.51 | 107.59
2019-06-12 | 125.45 | 107.83
2019-06-12 00:30 | 117.52 | 101.27
2019-06-12 01:00 | 120.77 | 104.17
2019-06-12 01:30 | 122.04 | 105.68
2019-06-12 02:00 | 114.52 | 96.28
2019-06-12 02:30 | 119.98 | 102.67
2019-06-12 03:00 | 116.42 | 99.83
2019-06-12 03:30 | 114.06 | 97.02
2019-06-12 04:00 | 111.2 | 93.86
2019-06-12 04:30 | 116.4 | 101.38
2019-06-12 05:00 | 116.28 | 101.24
2019-06-12 05:30 | 116.36 | 101.93
2019-06-12 06:00 | 111.51 | 95.78
2019-06-12 06:30 | 110.78 | 96.12
2019-06-12 07:00 | 107.46 | 93.48
2019-06-12 07:30 | 105.49 | 89.75
2019-06-12 08:00 | 99.8 | 81.26
2019-06-12 08:30 | 94.36 | 69.28
2019-06-12 09:00 | 105.76 | 77.2
2019-06-12 09:30 | 104.53 | 75.86
2019-06-12 10:00 | 105.03 | 76.01
2019-06-12 10:30 | 106.4 | 76.8
2019-06-12 11:00 | 103.9 | 76.07
2019-06-12 11:30 | 97.94 | 69.37
2019-06-12 12:00 | 107.74 | 79.38
2019-06-12 12:30 | 110.75 | 83.39
2019-06-12 13:00 | 105.95 | 84.8
2019-06-12 13:30 | 102.42 | 80.67
2019-06-12 14:00 | 108.36 | 82.78
2019-06-12 14:30 | 106.45 | 81.95
2019-06-12 15:00 | 108.43 | 84.18
2019-06-12 15:30 | 107.98 | 82.9
2019-06-12 16:00 | 106.22 | 87.21
2019-06-12 16:30 | 115.57 | 97.51
2019-06-12 17:00 | 114.31 | 97.83
2019-06-12 17:30 | 116.9 | 100.02
2019-06-12 18:00 | 119.48 | 103.69
2019-06-12 18:30 | 114.51 | 98.13
2019-06-12 19:00 | 120.57 | 105.31
2019-06-12 19:30 | 122.12 | 107.17
2019-06-12 20:00 | 121.05 | 106.03
2019-06-12 20:30 | 118.35 | 103.09
2019-06-12 21:00 | 123.11 | 103.1
2019-06-12 21:30 | 122.63 | 101.54
2019-06-12 22:00 | 120.17 | 99.17
2019-06-12 22:30 | 126.22 | 104.36
2019-06-12 23:00 | 127.98 | 106.36
2019-06-12 23:30 | 130.17 | 109.13
2019-06-13 | 130.81 | 110.19
2019-06-13 00:30 | 123.59 | 102.33
2019-06-13 01:00 | 126.16 | 106.21
2019-06-13 01:30 | 123.52 | 103.67
2019-06-13 02:00 | 124.11 | 103.62
2019-06-13 02:30 | 127.43 | 106.16
2019-06-13 03:00 | 126.84 | 106.03
2019-06-13 03:30 | 123.01 | 102.26
2019-06-13 04:00 | 117.56 | 97.43
2019-06-13 04:30 | 117.9 | 98.91
2019-06-13 05:00 | 122.55 | 103.4
2019-06-13 05:30 | 115.96 | 96.91
2019-06-13 06:00 | 115.89 | 96.11
2019-06-13 06:30 | 110.13 | 91.82
2019-06-13 07:00 | 109.55 | 89.68
2019-06-13 07:30 | 109.81 | 89.77
2019-06-13 08:00 | 106.79 | 88.09
2019-06-13 08:30 | 113.36 | 93.59
2019-06-13 09:00 | 105.72 | 79.28
2019-06-13 09:30 | 108.47 | 77.31
2019-06-13 10:00 | 99.88 | 68.63
2019-06-13 10:30 | 94.42 | 63.56
2019-06-13 11:00 | 90.37 | 64.7
2019-06-13 11:30 | 98.51 | 70.61
2019-06-13 12:00 | 95.13 | 65.67
2019-06-13 12:30 | 97.75 | 70.54
2019-06-13 13:00 | 96.15 | 69.58
2019-06-13 13:30 | 98.1 | 73.3
2019-06-13 14:00 | 100.93 | 79.86
2019-06-13 14:30 | 99.59 | 78.93
2019-06-13 15:00 | 95.8 | 72.95
2019-06-13 15:30 | 95.79 | 64.08
2019-06-13 16:00 | 101.82 | 74.2
2019-06-13 16:30 | 102.23 | 75.75
2019-06-13 17:00 | 99.87 | 78.89
2019-06-13 17:30 | 108.05 | 90.33
2019-06-13 18:00 | 111.54 | 92.76
2019-06-13 18:30 | 114.28 | 95.08
2019-06-13 19:00 | 118.1 | 98.29
2019-06-13 19:30 | 116.54 | 97.81
2019-06-13 20:00 | 118.25 | 99.46
2019-06-13 20:30 | 122.69 | 103.3
2019-06-13 21:00 | 124.9 | 105.56
2019-06-13 21:30 | 120.79 | 103.32
2019-06-13 22:00 | 116.23 | 98.84
2019-06-13 22:30 | 111.87 | 94.54
2019-06-13 23:00 | 115.19 | 97.46
2019-06-13 23:30 | 112.95 | 94.94
2019-06-14 | 113.08 | 95.86
2019-06-14 00:30 | 111.92 | 93.27
2019-06-14 01:00 | 114.16 | 96.1
2019-06-14 01:30 | 112.1 | 94.04
2019-06-14 02:00 | 118.28 | 100.13
2019-06-14 02:30 | 114.97 | 95.76
2019-06-14 03:00 | 112.52 | 91.67
2019-06-14 03:30 | 112.82 | 90.94
2019-06-14 04:00 | 126.11 | 106.5
2019-06-14 04:30 | 124.29 | 105.17
2019-06-14 05:00 | 124.08 | 104.32
2019-06-14 05:30 | 123.2 | 105.02
2019-06-14 06:00 | 127.5 | 108.72
2019-06-14 06:30 | 119.54 | 101.78
2019-06-14 07:00 | 115.9 | 98.54
2019-06-14 07:30 | 115.14 | 97.82
2019-06-14 08:00 | 111.5 | 90.35
2019-06-14 08:30 | 104.9 | 78.15
2019-06-14 09:00 | 104.62 | 76.9
2019-06-14 09:30 | 106.42 | 78.55
2019-06-14 10:00 | 106.42 | 77.65
2019-06-14 10:30 | 104.83 | 74.98
2019-06-14 11:00 | 101.95 | 71.5
2019-06-14 11:30 | 102.08 | 71.79
2019-06-14 12:00 | 113.51 | 85.26
2019-06-14 12:30 | 107.34 | 82.06
2019-06-14 13:00 | 109.11 | 81.21
2019-06-14 13:30 | 114.04 | 84.38
2019-06-14 14:00 | 112.61 | 82.43
2019-06-14 14:30 | 112.41 | 81.52
2019-06-14 15:00 | 105.44 | 72.53
2019-06-14 15:30 | 106.55 | 75.25
2019-06-14 16:00 | 103.03 | 72.87
2019-06-14 16:30 | 114.4 | 88.84
2019-06-14 17:00 | 121.76 | 100.65
2019-06-14 17:30 | 124.32 | 104.86
2019-06-14 18:00 | 123.03 | 103.84
2019-06-14 18:30 | 116.43 | 96.43
2019-06-14 19:00 | 123.36 | 103.28
2019-06-14 19:30 | 115.66 | 94.93
2019-06-14 20:00 | 118.03 | 96.45
2019-06-14 20:30 | 117.4 | 95.79
2019-06-14 21:00 | 122.94 | 101.75
2019-06-14 21:30 | 117.5 | 96.1
2019-06-14 22:00 | 118.48 | 96.58
2019-06-14 22:30 | 119.87 | 99.34
2019-06-14 23:00 | 118.96 | 98.69
2019-06-14 23:30 | 121.15 | 100.82
2019-06-15 | 118.85 | 98.2
2019-06-15 00:30 | 115.28 | 94.66
2019-06-15 01:00 | 114.33 | 93.59
2019-06-15 01:30 | 116.15 | 95.76
2019-06-15 02:00 | 113.01 | 92.62
2019-06-15 02:30 | 121.94 | 103.17
2019-06-15 03:00 | 117.63 | 97.16
2019-06-15 03:30 | 112.52 | 92.73
2019-06-15 04:00 | 121.85 | 101.89
2019-06-15 04:30 | 120.68 | 100.24
2019-06-15 05:00 | 122.1 | 104.45
2019-06-15 05:30 | 114.48 | 94.74
2019-06-15 06:00 | 116.09 | 96
2019-06-15 06:30 | 108.7 | 89.32
2019-06-15 07:00 | 113.83 | 95.02
2019-06-15 07:30 | 119.08 | 99.6
2019-06-15 08:00 | 109.05 | 84.97
2019-06-15 08:30 | 109.98 | 79.27
2019-06-15 09:00 | 110.09 | 77.05
2019-06-15 09:30 | 113.33 | 79.57
2019-06-15 10:00 | 107.96 | 72.07
2019-06-15 10:30 | 108.6 | 72.17
2019-06-15 11:00 | 115.6 | 79.02
2019-06-15 11:30 | 116.78 | 81.77
2019-06-15 12:00 | 119.67 | 86.91
2019-06-15 12:30 | 116.75 | 80.81
2019-06-15 13:00 | 113.55 | 76.04
2019-06-15 13:30 | 115.15 | 79.2
2019-06-15 14:00 | 112.02 | 75.32
2019-06-15 14:30 | 121.57 | 85.28
2019-06-15 15:00 | 112.28 | 76.13
2019-06-15 15:30 | 110.9 | 73.57
2019-06-15 16:00 | 114.1 | 80.53
2019-06-15 16:30 | 122.34 | 94.07
2019-06-15 17:00 | 117.75 | 93.83
2019-06-15 17:30 | 123.01 | 99.9
2019-06-15 18:00 | 123.79 | 102.36
2019-06-15 18:30 | 120.71 | 97.76
2019-06-15 19:00 | 127.71 | 104.75
2019-06-15 19:30 | 126.32 | 103.9
2019-06-15 20:00 | 126.57 | 103.31
2019-06-15 20:30 | 119.18 | 96.52
2019-06-15 21:00 | 122.13 | 97.79
2019-06-15 21:30 | 121.04 | 96.56
2019-06-15 22:00 | 119.81 | 96.23
2019-06-15 22:30 | 120.38 | 96.5
2019-06-15 23:00 | 126.23 | 101.71
2019-06-15 23:30 | 124.58 | 101.34
2019-06-16 | 118.68 | 95.85
2019-06-16 00:30 | 118.07 | 95.02
2019-06-16 01:00 | 119.91 | 96.24
2019-06-16 01:30 | 120 | 96.69
2019-06-16 02:00 | 123.03 | 100.51
2019-06-16 02:30 | 123.12 | 100.17
2019-06-16 03:00 | 121.66 | 99.35
2019-06-16 03:30 | 121.83 | 99.2
2019-06-16 04:00 | 118.66 | 96.73
2019-06-16 04:30 | 128.05 | 105.54
2019-06-16 05:00 | 126.78 | 104.56
2019-06-16 05:30 | 120.79 | 98.34
2019-06-16 06:00 | 119.21 | 97.16
2019-06-16 06:30 | 114.89 | 92.07
2019-06-16 07:00 | 113.34 | 90.19
2019-06-16 07:30 | 118.04 | 96.41
2019-06-16 08:00 | 119.33 | 95.83
2019-06-16 08:30 | 112.21 | 83.25
2019-06-16 09:00 | 111.74 | 77.31
2019-06-16 09:30 | 106.61 | 70.16
2019-06-16 10:00 | 108.67 | 73.22
2019-06-16 10:30 | 115.43 | 79.23
2019-06-16 11:00 | 110.56 | 75.6
2019-06-16 11:30 | 112.22 | 78.18
2019-06-16 12:00 | 113.77 | 79.32
2019-06-16 12:30 | 112.22 | 78.19
2019-06-16 13:00 | 110.87 | 77.74
2019-06-16 13:30 | 112.12 | 80.2
2019-06-16 14:00 | 111.18 | 75.98
2019-06-16 14:30 | 116.63 | 82.09
2019-06-16 15:00 | 126.38 | 100.71
2019-06-16 15:30 | 132.12 | 110.25
2019-06-16 16:00 | 118.02 | 90.38
2019-06-16 16:30 | 125.33 | 96.86
2019-06-16 17:00 | 130.75 | 107.34
2019-06-16 17:30 | 124.22 | 101.72
2019-06-16 18:00 | 123.19 | 102.12
2019-06-16 18:30 | 122.78 | 101.24
2019-06-16 19:00 | 130.18 | 108.83
2019-06-16 19:30 | 121.71 | 100.72
2019-06-16 20:00 | 121.04 | 99.28
2019-06-16 20:30 | 122.35 | 101.21
2019-06-16 21:00 | 119.91 | 98.16
2019-06-16 21:30 | 120.75 | 99.87
2019-06-16 22:00 | 123.28 | 102.63
2019-06-16 22:30 | 129.13 | 108.98
2019-06-16 23:00 | 126.34 | 106.14
2019-06-16 23:30 | 117.44 | 96.37
2019-06-17 | 125.49 | 105.02
2019-06-17 00:30 | 115.4 | 94.48
2019-06-17 01:00 | 116.66 | 95.92
2019-06-17 01:30 | 117.05 | 97.07
2019-06-17 02:00 | 115.09 | 95.72
2019-06-17 02:30 | 117.51 | 94.76
2019-06-17 03:00 | 115.4 | 92.28
2019-06-17 03:30 | 113.59 | 89.54
2019-06-17 04:00 | 117.32 | 95.29
2019-06-17 04:30 | 118.38 | 95.4
2019-06-17 05:00 | 118.58 | 95.64
2019-06-17 05:30 | 117.03 | 94.37
2019-06-17 06:00 | 118.48 | 95.94
2019-06-17 06:30 | 117.29 | 95.11
2019-06-17 07:00 | 115.07 | 92.67
2019-06-17 07:30 | 127.38 | 105.85
2019-06-17 08:00 | 120.31 | 94.15
2019-06-17 08:30 | 115.71 | 82.52
2019-06-17 09:00 | 113.01 | 74.39
2019-06-17 09:30 | 113.9 | 73.74
2019-06-17 10:00 | 112.46 | 70.08
2019-06-17 10:30 | 109.8 | 69.42
2019-06-17 11:00 | 107.19 | 67.01
2019-06-17 11:30 | 110.07 | 71.04
2019-06-17 12:00 | 105.63 | 66.61
2019-06-17 12:30 | 106.88 | 67.66
2019-06-17 13:00 | 106.7 | 69.31
2019-06-17 13:30 | 111.07 | 70.03
2019-06-17 14:00 | 105.92 | 65.04
2019-06-17 14:30 | 112 | 75.98
2019-06-17 15:00 | 115.32 | 76.73
2019-06-17 15:30 | 105.56 | 64.48
2019-06-17 16:00 | 107.39 | 71.49
2019-06-17 16:30 | 109.28 | 79.38
2019-06-17 17:00 | 116.21 | 93.46
2019-06-17 17:30 | 118.91 | 97.6
2019-06-17 18:00 | 118.39 | 97.07
2019-06-17 18:30 | 119.68 | 98.81
2019-06-17 19:00 | 125.98 | 104.7
2019-06-17 19:30 | 123.58 | 102.37
2019-06-17 20:00 | 131.11 | 110.55
2019-06-17 20:30 | 133.16 | 114.2
2019-06-17 21:00 | 124.45 | 103.5
2019-06-17 21:30 | 110.41 | 87.92
2019-06-17 22:00 | 119.16 | 97.66
2019-06-17 22:30 | 123.57 | 103.13
2019-06-17 23:00 | 124.99 | 104.17
2019-06-17 23:30 | 119.75 | 98.77
2019-06-18 | 126.84 | 106.75
2019-06-18 00:30 | 119.16 | 97.94
2019-06-18 01:00 | 121.69 | 100.37
2019-06-18 01:30 | 125 | 104.4
2019-06-18 02:00 | 121.16 | 99.89
2019-06-18 02:30 | 122.14 | 100.95
2019-06-18 03:00 | 118.88 | 98.19
2019-06-18 03:30 | 114.03 | 92.62
2019-06-18 04:00 | 114.42 | 93.52
2019-06-18 04:30 | 109.86 | 88.53
2019-06-18 05:00 | 125.15 | 104.89
2019-06-18 05:30 | 121.35 | 100.25
2019-06-18 06:00 | 119.74 | 98.52
2019-06-18 06:30 | 128.61 | 107.9
2019-06-18 07:00 | 125.08 | 105.2
2019-06-18 07:30 | 118.33 | 97.03
2019-06-18 08:00 | 116.82 | 90.83
2019-06-18 08:30 | 113.6 | 80.68
2019-06-18 09:00 | 113.96 | 76.98
2019-06-18 09:30 | 113.17 | 76.02
2019-06-18 10:00 | 108.33 | 70.46
2019-06-18 10:30 | 106.2 | 64.33
2019-06-18 11:00 | 110.96 | 71.69
2019-06-18 11:30 | 112.48 | 75.05
2019-06-18 12:00 | 113.96 | 77.45
2019-06-18 12:30 | 114.02 | 77.35
2019-06-18 13:00 | 111.62 | 75.87
2019-06-18 13:30 | 110.65 | 73.75
2019-06-18 14:00 | 105.6 | 67.24
2019-06-18 14:30 | 105.44 | 65.85
2019-06-18 15:00 | 113.18 | 77.33
2019-06-18 15:30 | 104.77 | 68.68
2019-06-18 16:00 | 110.07 | 76.57
2019-06-18 16:30 | 112.53 | 82.77
2019-06-18 17:00 | 114.15 | 90.42
2019-06-18 17:30 | 119.56 | 98.55
2019-06-18 18:00 | 124 | 102.03
2019-06-18 18:30 | 129.2 | 107.97
2019-06-18 19:00 | 130.57 | 108.84
2019-06-18 19:30 | 129.41 | 108.17
2019-06-18 20:00 | 137.82 | 118.17
2019-06-18 20:30 | 128.94 | 108.78
2019-06-18 21:00 | 131.29 | 110.67
2019-06-18 21:30 | 135.68 | 114.43
2019-06-18 22:00 | 131.13 | 110.27
2019-06-18 22:30 | 127.84 | 107.1
2019-06-18 23:00 | 125.78 | 104.35
2019-06-18 23:30 | 129.08 | 108.33
2019-06-19 | 128.21 | 106.86
2019-06-19 00:30 | 119.66 | 97.54
2019-06-19 01:00 | 115.95 | 96.59
2019-06-19 01:30 | 106.08 | 91.21
2019-06-19 02:00 | 110.07 | 96.54
2019-06-19 02:30 | 111.84 | 98.03
2019-06-19 03:00 | 111.21 | 97.94
2019-06-19 03:30 | 103.06 | 89.58
2019-06-19 04:00 | 100 | 86.7
2019-06-19 04:30 | 94.99 | 79.3
2019-06-19 05:00 | 99.65 | 85.37
2019-06-19 05:30 | 96.7 | 82
2019-06-19 06:00 | 101.99 | 88.35
2019-06-19 06:30 | 96.78 | 83.52
2019-06-19 07:00 | 95.12 | 81.51
2019-06-19 07:30 | 92.47 | 78.9
2019-06-19 08:00 | 89.14 | 71.81
2019-06-19 08:30 | 86.41 | 63.34
2019-06-19 09:00 | 81.76 | 59.17
2019-06-19 09:30 | 87.61 | 73.01
2019-06-19 10:00 | 90.5 | 74.09
2019-06-19 10:30 | 82.93 | 56.02
2019-06-19 11:00 | 82.63 | 52.38
2019-06-19 11:30 | 84.6 | 55.07
2019-06-19 12:00 | 85.41 | 55.52
2019-06-19 12:30 | 87.37 | 57.52
2019-06-19 13:00 | 85.92 | 54.57
2019-06-19 13:30 | 83.1 | 54.41
2019-06-19 14:00 | 84.77 | 57.12
2019-06-19 14:30 | 82.06 | 52.68
2019-06-19 15:00 | 84.05 | 56.52
2019-06-19 15:30 | 85.04 | 58.87
2019-06-19 16:00 | 85.5 | 64.13
2019-06-19 16:30 | 87.04 | 66.28
2019-06-19 17:00 | 99.22 | 84.8
2019-06-19 17:30 | 102.81 | 90.22
2019-06-19 18:00 | 99.53 | 86.41
2019-06-19 18:30 | 99.07 | 86.06
2019-06-19 19:00 | 100.62 | 87.51
2019-06-19 19:30 | 103.86 | 92.23
2019-06-19 20:00 | 109.46 | 98.45
2019-06-19 20:30 | 107.07 | 94.74
2019-06-19 21:00 | 103.25 | 89.99
2019-06-19 21:30 | 106.62 | 94.62
2019-06-19 22:00 | 101.13 | 87.81
2019-06-19 22:30 | 100.28 | 87.32
2019-06-19 23:00 | 104.49 | 92.12
2019-06-19 23:30 | 100.54 | 85.98
2019-06-20 | 103.7 | 89.99
2019-06-20 00:30 | 104.5 | 91.91
2019-06-20 01:00 | 106.79 | 95.19
2019-06-20 01:30 | 107.97 | 96.52
2019-06-20 02:00 | 105.52 | 92.53
2019-06-20 02:30 | 103.26 | 89.86
2019-06-20 03:00 | 101.24 | 87.42
2019-06-20 03:30 | 108.55 | 96.63
2019-06-20 04:00 | 95.99 | 81.56
2019-06-20 04:30 | 100.72 | 87.35
2019-06-20 05:00 | 101.69 | 87.49
2019-06-20 05:30 | 96.49 | 79.19
2019-06-20 06:00 | 99.9 | 83.84
2019-06-20 06:30 | 96.45 | 81.59
2019-06-20 07:00 | 98.23 | 83.9
2019-06-20 07:30 | 102.81 | 88.6
2019-06-20 08:00 | 100.29 | 83.03
2019-06-20 08:30 | 93.4 | 69.98
2019-06-20 09:00 | 89.69 | 63.71
2019-06-20 09:30 | 90.6 | 63.1
2019-06-20 10:00 | 89.47 | 60.09
2019-06-20 10:30 | 88.16 | 57.86
2019-06-20 11:00 | 87.14 | 56.07
2019-06-20 11:30 | 87.98 | 59.13
2019-06-20 12:00 | 90.84 | 63.02
2019-06-20 12:30 | 88.56 | 59.47
2019-06-20 13:00 | 84.62 | 51.78
2019-06-20 13:30 | 85.53 | 55.88
2019-06-20 14:00 | 87.85 | 58.18
2019-06-20 14:30 | 90.58 | 62.25
2019-06-20 15:00 | 88.11 | 57.02
2019-06-20 15:30 | 89.71 | 59.82
2019-06-20 16:00 | 93.42 | 68.4
2019-06-20 16:30 | 95.46 | 75.29
2019-06-20 17:00 | 97.92 | 81.01
2019-06-20 17:30 | 98.11 | 82.75
2019-06-20 18:00 | 101.7 | 87.94
2019-06-20 18:30 | 108.24 | 96.32
2019-06-20 19:00 | 104.64 | 91.65
2019-06-20 19:30 | 104.56 | 92.66
2019-06-20 20:00 | 112.05 | 101.48
2019-06-20 20:30 | 116.01 | 105.8
2019-06-20 21:00 | 107.46 | 95.91
2019-06-20 21:30 | 106.48 | 95.15
2019-06-20 22:00 | 102.18 | 88.42
2019-06-20 22:30 | 104.54 | 91.65
2019-06-20 23:00 | 101.66 | 87.33
2019-06-20 23:30 | 96.7 | 81.8
2019-06-21 | 96.32 | 82.47
2019-06-21 00:30 | 99.49 | 86.19
2019-06-21 01:00 | 103.97 | 91
2019-06-21 01:30 | 103.04 | 90.34
2019-06-21 02:00 | 105.81 | 91.54
2019-06-21 02:30 | 111.68 | 98.01
2019-06-21 03:00 | 108.75 | 94.57
2019-06-21 03:30 | 106.62 | 91.46
2019-06-21 04:00 | 107.9 | 92.57
2019-06-21 04:30 | 104.89 | 90.45
2019-06-21 05:00 | 112 | 98.42
2019-06-21 05:30 | 110.45 | 97.04
2019-06-21 06:00 | 106.88 | 92.76
2019-06-21 06:30 | 113.68 | 100.94
2019-06-21 07:00 | 106.71 | 93.14
2019-06-21 07:30 | 108.59 | 94.82
2019-06-21 08:00 | 104.92 | 87.69
2019-06-21 08:30 | 99.7 | 75.85
2019-06-21 09:00 | 99.9 | 72.57
2019-06-21 09:30 | 98.31 | 69.67
2019-06-21 10:00 | 94.87 | 63.42
2019-06-21 10:30 | 96.13 | 67.59
2019-06-21 11:00 | 101.38 | 77.02
2019-06-21 11:30 | 97.02 | 71.59
2019-06-21 12:00 | 97.05 | 69.82
2019-06-21 12:30 | 98.69 | 70.91
2019-06-21 13:00 | 94.97 | 67.78
2019-06-21 13:30 | 97.2 | 67.51
2019-06-21 14:00 | 95.24 | 64.78
2019-06-21 14:30 | 97.92 | 70.19
2019-06-21 15:00 | 100.24 | 73.99
2019-06-21 15:30 | 93.3 | 62.61
2019-06-21 16:00 | 96.34 | 69.46
2019-06-21 16:30 | 100.75 | 81.51
2019-06-21 17:00 | 101.45 | 86.15
2019-06-21 17:30 | 99.51 | 85.51
2019-06-21 18:00 | 108.27 | 94.36
2019-06-21 18:30 | 114.45 | 99.6
2019-06-21 19:00 | 117.05 | 100.86
2019-06-21 19:30 | 120.62 | 104.09
2019-06-21 20:00 | 115.2 | 98.88
2019-06-21 20:30 | 114.85 | 98.5
2019-06-21 21:00 | 109.33 | 92.79
2019-06-21 21:30 | 108.32 | 92.19
2019-06-21 22:00 | 114.56 | 98.59
2019-06-21 22:30 | 122.99 | 107.82
2019-06-21 23:00 | 111.65 | 95.61
2019-06-21 23:30 | 107.58 | 90.79
2019-06-22 | 109.61 | 92.97
2019-06-22 00:30 | 107.16 | 90.62
2019-06-22 01:00 | 100.94 | 82.64
2019-06-22 01:30 | 105.79 | 88.57
2019-06-22 02:00 | 106.85 | 89.48
2019-06-22 02:30 | 101.9 | 85.11
2019-06-22 03:00 | 102.1 | 86.13
2019-06-22 03:30 | 104.23 | 88.86
2019-06-22 04:00 | 100.24 | 85.07
2019-06-22 04:30 | 99.74 | 84.71
2019-06-22 05:00 | 107.46 | 91.88
2019-06-22 05:30 | 105.44 | 90.3
2019-06-22 06:00 | 101.39 | 86.12
2019-06-22 06:30 | 101.77 | 87.71
2019-06-22 07:00 | 105.84 | 92.09
2019-06-22 07:30 | 103.68 | 87.68
2019-06-22 08:00 | 100.85 | 81.58
2019-06-22 08:30 | 100.89 | 77.42
2019-06-22 09:00 | 97.83 | 72.11
2019-06-22 09:30 | 97.39 | 73.01
2019-06-22 10:00 | 103.22 | 77.31
2019-06-22 10:30 | 102.83 | 73.5
2019-06-22 11:00 | 101.48 | 73.16
2019-06-22 11:30 | 93.77 | 64.13
2019-06-22 12:00 | 88.69 | 57
2019-06-22 12:30 | 95.01 | 66.24
2019-06-22 13:00 | 91.78 | 60.92
2019-06-22 13:30 | 96.18 | 66.91
2019-06-22 14:00 | 96.67 | 66.96
2019-06-22 14:30 | 95.72 | 66.1
2019-06-22 15:00 | 94.08 | 62.73
2019-06-22 15:30 | 96.58 | 68.55
2019-06-22 16:00 | 92.89 | 64.67
2019-06-22 16:30 | 96.88 | 74.99
2019-06-22 17:00 | 97.81 | 81.4
2019-06-22 17:30 | 103.92 | 89.27
2019-06-22 18:00 | 110.07 | 96.84
2019-06-22 18:30 | 105.76 | 91.82
2019-06-22 19:00 | 106.68 | 93.09
2019-06-22 19:30 | 109.26 | 95.38
2019-06-22 20:00 | 113.95 | 99.78
2019-06-22 20:30 | 116.26 | 102.35
2019-06-22 21:00 | 116.44 | 102.17
2019-06-22 21:30 | 119.46 | 106.37
2019-06-22 22:00 | 111.21 | 97.35
2019-06-22 22:30 | 122.07 | 109.63
2019-06-22 23:00 | 117.44 | 104.03
2019-06-22 23:30 | 110.49 | 96.14
2019-06-23 | 109.35 | 95.33
2019-06-23 00:30 | 111.88 | 97.84
2019-06-23 01:00 | 110.38 | 96.37
2019-06-23 01:30 | 109.58 | 95.72
2019-06-23 02:00 | 109.52 | 95.38
2019-06-23 02:30 | 108.82 | 93.86
2019-06-23 03:00 | 106.2 | 91.52
2019-06-23 03:30 | 108.83 | 93.38
2019-06-23 04:00 | 107.9 | 93.5
2019-06-23 04:30 | 108.71 | 94.6
2019-06-23 05:00 | 115.38 | 101.4
2019-06-23 05:30 | 115.52 | 101.43
2019-06-23 06:00 | 112.76 | 98.42
2019-06-23 06:30 | 102.68 | 87.91
2019-06-23 07:00 | 108.87 | 94.92
2019-06-23 07:30 | 112.06 | 97.9
2019-06-23 08:00 | 110.24 | 92.64
2019-06-23 08:30 | 107.43 | 85.79
2019-06-23 09:00 | 106.8 | 83.44
2019-06-23 09:30 | 113.06 | 90.2
2019-06-23 10:00 | 117.19 | 93.14
2019-06-23 10:30 | 109.31 | 82.43
2019-06-23 11:00 | 115.56 | 90.55
2019-06-23 11:30 | 103.1 | 76.22
2019-06-23 12:00 | 109.2 | 82.15
2019-06-23 12:30 | 106.93 | 79.62
2019-06-23 13:00 | 101.24 | 70.23
2019-06-23 13:30 | 106.4 | 80.2
2019-06-23 14:00 | 107.43 | 78.86
2019-06-23 14:30 | 108.72 | 80.88
2019-06-23 15:00 | 105.19 | 77.57
2019-06-23 15:30 | 100.94 | 76.05
2019-06-23 16:00 | 108.67 | 88.82
2019-06-23 16:30 | 109.34 | 90.65
2019-06-23 17:00 | 113.07 | 96.84
2019-06-23 17:30 | 120.32 | 105.44
2019-06-23 18:00 | 119.38 | 105.21
2019-06-23 18:30 | 117.9 | 104.49
2019-06-23 19:00 | 118.1 | 102.58
2019-06-23 19:30 | 128.61 | 114.38
2019-06-23 20:00 | 126.09 | 112.22
2019-06-23 20:30 | 124.97 | 110.86
2019-06-23 21:00 | 119.57 | 104.37
2019-06-23 21:30 | 126.9 | 111.27
2019-06-23 22:00 | 116.52 | 100.73
2019-06-23 22:30 | 119.96 | 104.09
2019-06-23 23:00 | 123.14 | 107.79
2019-06-23 23:30 | 113.13 | 96.42
2019-06-24 | 116.94 | 99.47
2019-06-24 00:30 | 119.25 | 102.58
2019-06-24 01:00 | 121.13 | 104.69
2019-06-24 01:30 | 121.4 | 104.53
2019-06-24 02:00 | 116.45 | 98.94
2019-06-24 02:30 | 116.2 | 98.39
2019-06-24 03:00 | 121.57 | 105.13
2019-06-24 03:30 | 117.6 | 102.1
2019-06-24 04:00 | 112.53 | 96.14
2019-06-24 04:30 | 116.36 | 99.49
2019-06-24 05:00 | 118.1 | 100.79
2019-06-24 05:30 | 116.12 | 99.4
2019-06-24 06:00 | 107.55 | 90.95
2019-06-24 06:30 | 113.72 | 97.58
2019-06-24 07:00 | 113.93 | 98.28
2019-06-24 07:30 | 109.28 | 93.73
2019-06-24 08:00 | 104.72 | 85.02
2019-06-24 08:30 | 99.39 | 74.8
2019-06-24 09:00 | 96.87 | 68.22
2019-06-24 09:30 | 95.19 | 64.11
2019-06-24 10:00 | 98.71 | 68.02
2019-06-24 10:30 | 102.58 | 73.22
2019-06-24 11:00 | 99.69 | 69.3
2019-06-24 11:30 | 101.38 | 72.92
2019-06-24 12:00 | 106.01 | 78.67
2019-06-24 12:30 | 96.36 | 67.96
2019-06-24 13:00 | 104.89 | 76.47
2019-06-24 13:30 | 102.39 | 75.24
2019-06-24 14:00 | 99.14 | 70.65
2019-06-24 14:30 | 100.64 | 72.43
2019-06-24 15:00 | 102.99 | 72.7
2019-06-24 15:30 | 102.59 | 73.42
2019-06-24 16:00 | 99.04 | 70.83
2019-06-24 16:30 | 104.2 | 80.37
2019-06-24 17:00 | 109.01 | 90.22
2019-06-24 17:30 | 106.27 | 90.28
2019-06-24 18:00 | 103.58 | 88.76
2019-06-24 18:30 | 107.3 | 94.02
2019-06-24 19:00 | 117.02 | 103.67
2019-06-24 19:30 | 119.36 | 105.83
2019-06-24 20:00 | 118.07 | 103.63
2019-06-24 20:30 | 117.15 | 101.16
2019-06-24 21:00 | 125.42 | 110.18
2019-06-24 21:30 | 122.87 | 108.12
2019-06-24 22:00 | 126.08 | 112.31
2019-06-24 22:30 | 121.94 | 108.01
2019-06-24 23:00 | 118.53 | 103.5
2019-06-24 23:30 | 115.88 | 101.48
2019-06-25 | 105.39 | 91.82
2019-06-25 00:30 | 115.99 | 102.36
2019-06-25 01:00 | 116.79 | 102.61
2019-06-25 01:30 | 116.06 | 100.6
2019-06-25 02:00 | 117.18 | 100.91
2019-06-25 02:30 | 120.98 | 105.38
2019-06-25 03:00 | 110.04 | 93.02
2019-06-25 03:30 | 108.01 | 91.42
2019-06-25 04:00 | 109.29 | 94.13
2019-06-25 04:30 | 112.25 | 97.83
2019-06-25 05:00 | 116.85 | 101.69
2019-06-25 05:30 | 122.46 | 107.78
2019-06-25 06:00 | 116 | 99.3
2019-06-25 06:30 | 110.79 | 94.85
2019-06-25 07:00 | 112.22 | 95.44
2019-06-25 07:30 | 115.91 | 99.54
2019-06-25 08:00 | 107.9 | 88.49
2019-06-25 08:30 | 104.72 | 81.11
2019-06-25 09:00 | 113 | 86.71
2019-06-25 09:30 | 104.59 | 76.77
2019-06-25 10:00 | 102.48 | 74.64
2019-06-25 10:30 | 104.68 | 75.24
2019-06-25 11:00 | 109.41 | 79.72
2019-06-25 11:30 | 102.4 | 70.87
2019-06-25 12:00 | 103.58 | 73.36
2019-06-25 12:30 | 105.73 | 75.1
2019-06-25 13:00 | 103.58 | 74.57
2019-06-25 13:30 | 102.65 | 73.26
2019-06-25 14:00 | 102.76 | 71.49
2019-06-25 14:30 | 101.63 | 72.06
2019-06-25 15:00 | 100.14 | 67.69
2019-06-25 15:30 | 95.03 | 62.13
2019-06-25 16:00 | 97.82 | 68.01
2019-06-25 16:30 | 101.29 | 78.47
2019-06-25 17:00 | 110.81 | 92.78
2019-06-25 17:30 | 114.3 | 99.37
2019-06-25 18:00 | 118.21 | 103.28
2019-06-25 18:30 | 103.56 | 88.68
2019-06-25 19:00 | 112.01 | 97.94
2019-06-25 19:30 | 114.78 | 100.29
2019-06-25 20:00 | 115.81 | 101.92
2019-06-25 20:30 | 117.77 | 103.67
2019-06-25 21:00 | 120.18 | 105.34
2019-06-25 21:30 | 121.26 | 105.69
2019-06-25 22:00 | 120.7 | 105.93
2019-06-25 22:30 | 123.26 | 109.09
2019-06-25 23:00 | 117.11 | 101.58
2019-06-25 23:30 | 111.29 | 96.1
2019-06-26 | 112.44 | 97.18
2019-06-26 00:30 | 118.21 | 103.25
2019-06-26 01:00 | 121.63 | 107.21
2019-06-26 01:30 | 124.43 | 111.05
2019-06-26 02:00 | 118.19 | 105.15
2019-06-26 02:30 | 120.39 | 106.32
2019-06-26 03:00 | 106.68 | 92.31
2019-06-26 03:30 | 102.05 | 87.92
2019-06-26 04:00 | 101.07 | 87.1
2019-06-26 04:30 | 107.1 | 94.07
2019-06-26 05:00 | 112.64 | 100.99
2019-06-26 05:30 | 116.98 | 104.63
2019-06-26 06:00 | 108.59 | 95.23
2019-06-26 06:30 | 103.62 | 90.37
2019-06-26 07:00 | 103.17 | 89.54
2019-06-26 07:30 | 110.18 | 97.85
2019-06-26 08:00 | 109.51 | 95.32
2019-06-26 08:30 | 105.96 | 85.33
2019-06-26 09:00 | 101.35 | 79.12
2019-06-26 09:30 | 102.57 | 80.98
2019-06-26 10:00 | 104.34 | 82.52
2019-06-26 10:30 | 101.75 | 77.21
2019-06-26 11:00 | 100.8 | 74.2
2019-06-26 11:30 | 97.01 | 69.43
2019-06-26 12:00 | 100.14 | 76.73
2019-06-26 12:30 | 95.73 | 70.43
2019-06-26 13:00 | 98.43 | 72.26
2019-06-26 13:30 | 94.01 | 63.94
2019-06-26 14:00 | 98.35 | 72.84
2019-06-26 14:30 | 98.1 | 69.61
2019-06-26 15:00 | 97.97 | 68.9
2019-06-26 15:30 | 96.28 | 68.55
2019-06-26 16:00 | 100.13 | 73.39
2019-06-26 16:30 | 103.37 | 82.47
2019-06-26 17:00 | 118.67 | 105.17
2019-06-26 17:30 | 120.7 | 108.73
2019-06-26 18:00 | 119.16 | 106.46
2019-06-26 18:30 | 111.18 | 98.22
2019-06-26 19:00 | 119.17 | 106.18
2019-06-26 19:30 | 126 | 113.28
2019-06-26 20:00 | 127.62 | 115.37
2019-06-26 20:30 | 124.57 | 111.62
2019-06-26 21:00 | 114.14 | 100.7
2019-06-26 21:30 | 116.78 | 103.01
2019-06-26 22:00 | 117.25 | 102.94
2019-06-26 22:30 | 111.68 | 97.77
2019-06-26 23:00 | 115.5 | 100.89
2019-06-26 23:30 | 115.92 | 102.25
2019-06-27 | 113.43 | 99.49
2019-06-27 00:30 | 117.18 | 103.88
2019-06-27 01:00 | 119.29 | 105.49
2019-06-27 01:30 | 114.51 | 100.54
2019-06-27 02:00 | 116.31 | 101.64
2019-06-27 02:30 | 111.76 | 96.56
2019-06-27 03:00 | 113.11 | 98.08
2019-06-27 03:30 | 119.18 | 104.67
2019-06-27 04:00 | 122.76 | 109.34
2019-06-27 04:30 | 120.91 | 107.92
2019-06-27 05:00 | 112.71 | 98.63
2019-06-27 05:30 | 111.38 | 97.64
2019-06-27 06:00 | 112.82 | 98.95
2019-06-27 06:30 | 105.11 | 90.66
2019-06-27 07:00 | 105.47 | 91.68
2019-06-27 07:30 | 107.56 | 93.15
2019-06-27 08:00 | 102.3 | 82.79
2019-06-27 08:30 | 104.35 | 81.4
2019-06-27 09:00 | 100.36 | 75.4
2019-06-27 09:30 | 103.89 | 77.49
2019-06-27 10:00 | 103.44 | 77.92
2019-06-27 10:30 | 92.66 | 60.08
2019-06-27 11:00 | 97.65 | 70.18
2019-06-27 11:30 | 99.55 | 72.28
2019-06-27 12:00 | 101.65 | 79.63
2019-06-27 12:30 | 98 | 75.8
2019-06-27 13:00 | 95.81 | 70.92
2019-06-27 13:30 | 96.25 | 73.8
2019-06-27 14:00 | 88.11 | 68.3
2019-06-27 14:30 | 91.41 | 73.95
2019-06-27 15:00 | 94.4 | 78.14
2019-06-27 15:30 | 96.47 | 80.05
2019-06-27 16:00 | 93.52 | 78.01
2019-06-27 16:30 | 91.85 | 77.59
2019-06-27 17:00 | 95.74 | 81.87
2019-06-27 17:30 | 101.05 | 88.01
2019-06-27 18:00 | 98.78 | 85.82
2019-06-27 18:30 | 94.18 | 81.18
2019-06-27 19:00 | 105.83 | 94.58
2019-06-27 19:30 | 103.21 | 91.19
2019-06-27 20:00 | 100.52 | 88.19
2019-06-27 20:30 | 98.22 | 85.34
2019-06-27 21:00 | 100.28 | 86.17
2019-06-27 21:30 | 107.25 | 93.36
2019-06-27 22:00 | 108.05 | 93.92
2019-06-27 22:30 | 110.07 | 97.04
2019-06-27 23:00 | 110.87 | 97.88
2019-06-27 23:30 | 110.69 | 97.57
2019-06-28 | 108.95 | 96.28
2019-06-28 00:30 | 110.72 | 97.35
2019-06-28 01:00 | 112.7 | 98.77
2019-06-28 01:30 | 110.14 | 95.6
2019-06-28 02:00 | 111.15 | 97.57
2019-06-28 02:30 | 116.9 | 103.28
2019-06-28 03:00 | 117.27 | 103.62
2019-06-28 03:30 | 112.52 | 98.54
2019-06-28 04:00 | 115.14 | 100.58
2019-06-28 04:30 | 110.05 | 95.98
2019-06-28 05:00 | 112.56 | 98.31
2019-06-28 05:30 | 113.24 | 100.1
2019-06-28 06:00 | 108.02 | 94.27
2019-06-28 06:30 | 104.09 | 89.83
2019-06-28 07:00 | 105 | 91.06
2019-06-28 07:30 | 102.8 | 88.19
2019-06-28 08:00 | 111.63 | 95.62
2019-06-28 08:30 | 105.5 | 85.77
2019-06-28 09:00 | 116.33 | 101.03
2019-06-28 09:30 | 108.81 | 88.74
2019-06-28 10:00 | 100.14 | 73.62
2019-06-28 10:30 | 95.64 | 68.18
2019-06-28 11:00 | 96 | 68.05
2019-06-28 11:30 | 97.63 | 73.78
2019-06-28 12:00 | 96.51 | 70.88
2019-06-28 12:30 | 99.61 | 77.43
2019-06-28 13:00 | 96.5 | 71.84
2019-06-28 13:30 | 99.35 | 76.35
2019-06-28 14:00 | 107.5 | 87.35
2019-06-28 14:30 | 101.46 | 83.76
2019-06-28 15:00 | 103.05 | 82.29
2019-06-28 15:30 | 104.83 | 87.35
2019-06-28 16:00 | 103.82 | 85.92
2019-06-28 16:30 | 102.36 | 81.97
2019-06-28 17:00 | 104.04 | 87.87
2019-06-28 17:30 | 115.71 | 102.59
2019-06-28 18:00 | 117.48 | 103.62
2019-06-28 18:30 | 117.43 | 104.01
2019-06-28 19:00 | 117.58 | 103.95
2019-06-28 19:30 | 111.56 | 98.12
2019-06-28 20:00 | 111.06 | 98.22
2019-06-28 20:30 | 107.4 | 93.82
2019-06-28 21:00 | 105.68 | 93.06
2019-06-28 21:30 | 110.32 | 98.26
2019-06-28 22:00 | 104.52 | 92.3
2019-06-28 22:30 | 107.68 | 96.11
2019-06-28 23:00 | 101.4 | 89.48
2019-06-28 23:30 | 99.32 | 86.45
2019-06-29 | 100.67 | 87.64
2019-06-29 00:30 | 107.95 | 95.26
2019-06-29 01:00 | 114.88 | 102.38
2019-06-29 01:30 | 110.53 | 97.9
2019-06-29 02:00 | 105.89 | 91.79
2019-06-29 02:30 | 102.07 | 88.21
2019-06-29 03:00 | 107.6 | 94.11
2019-06-29 03:30 | 113.29 | 100.33
2019-06-29 04:00 | 109.14 | 95.61
2019-06-29 04:30 | 107.75 | 94.08
2019-06-29 05:00 | 110.22 | 97.23
2019-06-29 05:30 | 109.23 | 96.35
2019-06-29 06:00 | 115.22 | 102.21
2019-06-29 06:30 | 113.45 | 100.04
2019-06-29 07:00 | 117.75 | 103.73
2019-06-29 07:30 | 115.75 | 101.14
2019-06-29 08:00 | 107.14 | 90.12
2019-06-29 08:30 | 100.55 | 79.6
2019-06-29 09:00 | 99.28 | 75.8
2019-06-29 09:30 | 98.07 | 73.72
2019-06-29 10:00 | 103.67 | 79.22
2019-06-29 10:30 | 99.45 | 73.75
2019-06-29 11:00 | 103.24 | 77.94
2019-06-29 11:30 | 101.65 | 76.22
2019-06-29 12:00 | 100.35 | 74.84
2019-06-29 12:30 | 103.96 | 77.96
2019-06-29 13:00 | 108.83 | 84.63
2019-06-29 13:30 | 102.79 | 76.95
2019-06-29 14:00 | 102.19 | 76.8
2019-06-29 14:30 | 109.49 | 85.9
2019-06-29 15:00 | 99.89 | 73.38
2019-06-29 15:30 | 106.99 | 83.05
2019-06-29 16:00 | 101.65 | 79.37
2019-06-29 16:30 | 102.5 | 83.34
2019-06-29 17:00 | 106.33 | 90.8
2019-06-29 17:30 | 110.3 | 97.28
2019-06-29 18:00 | 113.56 | 100.54
2019-06-29 18:30 | 119.48 | 106.83
2019-06-29 19:00 | 126.4 | 113.53
2019-06-29 19:30 | 120.83 | 109.36
2019-06-29 20:00 | 120.03 | 107.6
2019-06-29 20:30 | 115.88 | 103
2019-06-29 21:00 | 115.32 | 101.49
2019-06-29 21:30 | 112.41 | 100.15
2019-06-29 22:00 | 108.8 | 96.69
2019-06-29 22:30 | 115.68 | 102.85
2019-06-29 23:00 | 116.23 | 103.15
2019-06-29 23:30 | 111.66 | 97.83
2019-06-30 | 110.71 | 97.85
2019-06-30 00:30 | 116.95 | 103.63
2019-06-30 01:00 | 117.63 | 104.2
2019-06-30 01:30 | 108.93 | 94.83
2019-06-30 02:00 | 108.62 | 95.27
2019-06-30 02:30 | 115.85 | 103.42
2019-06-30 03:00 | 111.74 | 99.04
2019-06-30 03:30 | 113.24 | 100.76
2019-06-30 04:00 | 117.69 | 105.67
2019-06-30 04:30 | 125.35 | 113.91
2019-06-30 05:00 | 114.61 | 102.2
2019-06-30 05:30 | 113.33 | 99.98
2019-06-30 06:00 | 106.7 | 93.32
2019-06-30 06:30 | 104.06 | 91.54
2019-06-30 07:00 | 104.09 | 91.33
2019-06-30 07:30 | 111.79 | 98.39
2019-06-30 08:00 | 109.44 | 94.35
2019-06-30 08:30 | 99.01 | 79.99
2019-06-30 09:00 | 101.29 | 79.23
2019-06-30 09:30 | 94.22 | 70.32
2019-06-30 10:00 | 101.44 | 79.94
2019-06-30 10:30 | 99.67 | 76.99
2019-06-30 11:00 | 98.61 | 74.68
2019-06-30 11:30 | 98.75 | 74.59
2019-06-30 12:00 | 102.56 | 78.88
2019-06-30 12:30 | 100.96 | 75.17
2019-06-30 13:00 | 100.77 | 75.79
2019-06-30 13:30 | 108.2 | 83.92
2019-06-30 14:00 | 99.11 | 71.5
2019-06-30 14:30 | 96.85 | 69.07
2019-06-30 15:00 | 99.58 | 72.15
2019-06-30 15:30 | 100.5 | 75.07
2019-06-30 16:00 | 100.16 | 75.69
2019-06-30 16:30 | 105.53 | 86.14
2019-06-30 17:00 | 110.43 | 95.62
2019-06-30 17:30 | 109.76 | 96.91
2019-06-30 18:00 | 114.42 | 100.98
2019-06-30 18:30 | 107.46 | 94.13
2019-06-30 19:00 | 116.87 | 103.01
2019-06-30 19:30 | 112.36 | 99.43
2019-06-30 20:00 | 108.44 | 96.05
2019-06-30 20:30 | 116.87 | 105.07
2019-06-30 21:00 | 115.96 | 104.17
2019-06-30 21:30 | 116.61 | 104.59
2019-06-30 22:00 | 109.88 | 98.36
2019-06-30 22:30 | 113.72 | 101.72
2019-06-30 23:00 | 104.27 | 90.61
2019-06-30 23:30 | 105.81 | 92.68
2019-07-01 | 111.64 | 99.35
2019-07-01 00:30 | 108.4 | 95.48
2019-07-01 01:00 | 105.68 | 91.92
2019-07-01 01:30 | 109.23 | 95.94
2019-07-01 02:00 | 112.11 | 99.23
2019-07-01 02:30 | 105.93 | 92.55
2019-07-01 03:00 | 99.78 | 84.65
2019-07-01 03:30 | 96.94 | 81.2
2019-07-01 04:00 | 101.99 | 88.77
2019-07-01 04:30 | 103.19 | 90.72
2019-07-01 05:00 | 105.65 | 92.73
2019-07-01 05:30 | 108.35 | 95.79
2019-07-01 06:00 | 110.07 | 98.34
2019-07-01 06:30 | 110.15 | 97.97
2019-07-01 07:00 | 114.1 | 102
2019-07-01 07:30 | 108.27 | 94.67
2019-07-01 08:00 | 110.75 | 95.24
2019-07-01 08:30 | 103.03 | 83.16
2019-07-01 09:00 | 98.53 | 73.85
2019-07-01 09:30 | 99.32 | 73.59
2019-07-01 10:00 | 98.9 | 74.47
2019-07-01 10:30 | 104.73 | 81.31
2019-07-01 11:00 | 102.91 | 78.13
2019-07-01 11:30 | 96.78 | 70.33
2019-07-01 12:00 | 91.25 | 61.27
2019-07-01 12:30 | 95.58 | 71.03
2019-07-01 13:00 | 90.42 | 60.87
2019-07-01 13:30 | 98.1 | 73.91
2019-07-01 14:00 | 98.32 | 74.89
2019-07-01 14:30 | 100.65 | 75.66
2019-07-01 15:00 | 100.45 | 78.29
2019-07-01 15:30 | 92.95 | 64.87
2019-07-01 16:00 | 95.94 | 69.04
2019-07-01 16:30 | 105.52 | 85.55
2019-07-01 17:00 | 105.47 | 90.05
2019-07-01 17:30 | 109.37 | 95.9
2019-07-01 18:00 | 110.8 | 99.04
2019-07-01 18:30 | 105.11 | 94.04
2019-07-01 19:00 | 116.9 | 106.28
2019-07-01 19:30 | 113.89 | 103.2
2019-07-01 20:00 | 116.47 | 105.43
2019-07-01 20:30 | 121.04 | 110.66
2019-07-01 21:00 | 117.77 | 106.19
2019-07-01 21:30 | 110.31 | 98.34
2019-07-01 22:00 | 116.95 | 104.87
2019-07-01 22:30 | 113.21 | 100.91
2019-07-01 23:00 | 109.66 | 97.6
2019-07-01 23:30 | 117.84 | 106.88
2019-07-02 | 113.46 | 101.68
2019-07-02 00:30 | 117.86 | 104.8
2019-07-02 01:00 | 115.34 | 102.39
2019-07-02 01:30 | 108.85 | 95.79
2019-07-02 02:00 | 115.78 | 104.05
2019-07-02 02:30 | 108.49 | 95.7
2019-07-02 03:00 | 106.15 | 92.37
2019-07-02 03:30 | 106.35 | 92.42
2019-07-02 04:00 | 103.1 | 89.61
2019-07-02 04:30 | 112.92 | 100.82
2019-07-02 05:00 | 117.45 | 103.68
2019-07-02 05:30 | 108.73 | 94.57
2019-07-02 06:00 | 106.63 | 93.05
2019-07-02 06:30 | 101.84 | 87.35
2019-07-02 07:00 | 97.07 | 81.6
2019-07-02 07:30 | 96.01 | 79.53
2019-07-02 08:00 | 100.49 | 82.98
2019-07-02 08:30 | 101.94 | 80.61
2019-07-02 09:00 | 97.67 | 73.37
2019-07-02 09:30 | 102.12 | 79.45
2019-07-02 10:00 | 100.17 | 73.9
2019-07-02 10:30 | 96.22 | 66.43
2019-07-02 11:00 | 93.32 | 65.15
2019-07-02 11:30 | 91.86 | 60.82
2019-07-02 12:00 | 94.62 | 64.55
2019-07-02 12:30 | 98.46 | 75.56
2019-07-02 13:00 | 99.41 | 79.42
2019-07-02 13:30 | 105.07 | 86.59
2019-07-02 14:00 | 94.66 | 66.75
2019-07-02 14:30 | 96.9 | 65.63
2019-07-02 15:00 | 99.44 | 70.14
2019-07-02 15:30 | 95.3 | 65.05
2019-07-02 16:00 | 98.16 | 70.65
2019-07-02 16:30 | 103.38 | 81.06
2019-07-02 17:00 | 102.85 | 84.3
2019-07-02 17:30 | 115.03 | 101.11
2019-07-02 18:00 | 113.3 | 98.73
2019-07-02 18:30 | 114.16 | 100.71
2019-07-02 19:00 | 116.56 | 103.41
2019-07-02 19:30 | 116.03 | 103.17
2019-07-02 20:00 | 112.01 | 99.33
2019-07-02 20:30 | 111.77 | 99.62
2019-07-02 21:00 | 111.51 | 98.15
2019-07-02 21:30 | 110.91 | 97.41
2019-07-02 22:00 | 115.38 | 102.86
2019-07-02 22:30 | 113.69 | 100.83
2019-07-02 23:00 | 114.26 | 101.19
2019-07-02 23:30 | 112.68 | 98.92
2019-07-03 | 111.77 | 97.87
2019-07-03 00:30 | 119.21 | 107.09
2019-07-03 01:00 | 117.62 | 104.63
2019-07-03 01:30 | 117.19 | 105.43
2019-07-03 02:00 | 114.57 | 101.62
2019-07-03 02:30 | 119.39 | 107.1
2019-07-03 03:00 | 116.94 | 104.83
2019-07-03 03:30 | 109.95 | 96.06
2019-07-03 04:00 | 113.36 | 100.27
2019-07-03 04:30 | 108.58 | 95.17
2019-07-03 05:00 | 109.02 | 96.35
2019-07-03 05:30 | 108.63 | 96.85
2019-07-03 06:00 | 112.26 | 100.82
2019-07-03 06:30 | 106.83 | 94.45
2019-07-03 07:00 | 107.17 | 94.26
2019-07-03 07:30 | 103.67 | 90.04
2019-07-03 08:00 | 105.45 | 90.65
2019-07-03 08:30 | 102.93 | 86.62
2019-07-03 09:00 | 105.07 | 83.65
2019-07-03 09:30 | 102.5 | 75.11
2019-07-03 10:00 | 97.71 | 68.32
2019-07-03 10:30 | 95.62 | 68.33
2019-07-03 11:00 | 93.5 | 66.63
2019-07-03 11:30 | 97.77 | 73.31
2019-07-03 12:00 | 90.87 | 63.02
2019-07-03 12:30 | 97.26 | 72.73
2019-07-03 13:00 | 101.9 | 78.15
2019-07-03 13:30 | 103.44 | 80.94
2019-07-03 14:00 | 105.24 | 84.91
2019-07-03 14:30 | 101.58 | 80.8
2019-07-03 15:00 | 102.94 | 85.28
2019-07-03 15:30 | 100.29 | 81.73
2019-07-03 16:00 | 106.04 | 89.98
2019-07-03 16:30 | 110.2 | 95.27
2019-07-03 17:00 | 109.9 | 95.93
2019-07-03 17:30 | 114.7 | 102.86
2019-07-03 18:00 | 110.24 | 98.48
2019-07-03 18:30 | 107.76 | 95.76
2019-07-03 19:00 | 117.87 | 107.35
2019-07-03 19:30 | 118.18 | 107.96
2019-07-03 20:00 | 123.56 | 113.68
2019-07-03 20:30 | 119.02 | 108.43
2019-07-03 21:00 | 119.23 | 108.3
2019-07-03 21:30 | 117.91 | 106.69
2019-07-03 22:00 | 117.51 | 105.57
2019-07-03 22:30 | 116.17 | 103.92
2019-07-03 23:00 | 118.14 | 105.68
2019-07-03 23:30 | 111.77 | 98.93
2019-07-04 | 104.75 | 92.29
2019-07-04 00:30 | 109.54 | 97.04
2019-07-04 01:00 | 115.2 | 103
2019-07-04 01:30 | 107.45 | 94.07
2019-07-04 02:00 | 105.24 | 91.11
2019-07-04 02:30 | 106.72 | 93.18
2019-07-04 03:00 | 111.78 | 99.37
2019-07-04 03:30 | 107.31 | 93.74
2019-07-04 04:00 | 105.95 | 92.06
2019-07-04 04:30 | 109.29 | 96.25
2019-07-04 05:00 | 106.84 | 93.42
2019-07-04 05:30 | 109.96 | 97.7
2019-07-04 06:00 | 109.25 | 96.95
2019-07-04 06:30 | 109.29 | 97.75
2019-07-04 07:00 | 107.87 | 96.28
2019-07-04 07:30 | 101.82 | 86.42
2019-07-04 08:00 | 99.56 | 81.93
2019-07-04 08:30 | 94.59 | 72.4
2019-07-04 09:00 | 95.18 | 77.35
2019-07-04 09:30 | 100.31 | 82.29
2019-07-04 10:00 | 97.49 | 71.53
2019-07-04 10:30 | 102.76 | 81.8
2019-07-04 11:00 | 98.42 | 74.63
2019-07-04 11:30 | 95.97 | 70.24
2019-07-04 12:00 | 95.22 | 69.77
2019-07-04 12:30 | 104.81 | 84.66
2019-07-04 13:00 | 102.02 | 80.44
2019-07-04 13:30 | 102.31 | 82.17
2019-07-04 14:00 | 100.61 | 81
2019-07-04 14:30 | 103.92 | 85.32
2019-07-04 15:00 | 113.07 | 98.88
2019-07-04 15:30 | 108.64 | 91.29
2019-07-04 16:00 | 111.95 | 96.92
2019-07-04 16:30 | 111.09 | 96.72
2019-07-04 17:00 | 104.73 | 91.6
2019-07-04 17:30 | 103.49 | 89.77
2019-07-04 18:00 | 99.39 | 85.23
2019-07-04 18:30 | 111.61 | 98.93
2019-07-04 19:00 | 107.5 | 95.01
2019-07-04 19:30 | 115.06 | 103.1
2019-07-04 20:00 | 108.61 | 96.72
2019-07-04 20:30 | 108.82 | 96.27
2019-07-04 21:00 | 108.58 | 96.56
2019-07-04 21:30 | 104.62 | 90.7
2019-07-04 22:00 | 101.07 | 86.23
2019-07-04 22:30 | 96.77 | 78.59
2019-07-04 23:00 | 98.54 | 80.93
2019-07-04 23:30 | 93.68 | 75.67
2019-07-05 | 98.16 | 81.68
2019-07-05 00:30 | 97.46 | 79.63
2019-07-05 01:00 | 102.87 | 87.52
2019-07-05 01:30 | 105.62 | 92.01
2019-07-05 02:00 | 109.08 | 96.16
2019-07-05 02:30 | 100.39 | 84.85
2019-07-05 03:00 | 101.09 | 85.99
2019-07-05 03:30 | 98.85 | 82.33
2019-07-05 04:00 | 101.82 | 87.24
2019-07-05 04:30 | 98.15 | 82.55
2019-07-05 05:00 | 100.81 | 86.25
2019-07-05 05:30 | 96.74 | 82.45
2019-07-05 06:00 | 93.99 | 77.96
2019-07-05 06:30 | 92.69 | 76.95
2019-07-05 07:00 | 99.92 | 86.47
2019-07-05 07:30 | 96.84 | 82.03
2019-07-05 08:00 | 97.76 | 82.42
2019-07-05 08:30 | 96.68 | 80.72
2019-07-05 09:00 | 88.18 | 68.08
2019-07-05 09:30 | 92.15 | 72.92
2019-07-05 10:00 | 99.71 | 82.68
2019-07-05 10:30 | 98.82 | 79.98
2019-07-05 11:00 | 95.37 | 71.79
2019-07-05 11:30 | 97.48 | 74.11
2019-07-05 12:00 | 99.51 | 77.74
2019-07-05 12:30 | 99.48 | 81.43
2019-07-05 13:00 | 97.62 | 78.97
2019-07-05 13:30 | 101.4 | 84.95
2019-07-05 14:00 | 101.51 | 85.13
2019-07-05 14:30 | 97.19 | 78.97
2019-07-05 15:00 | 96.59 | 75.54
2019-07-05 15:30 | 101.14 | 83.85
2019-07-05 16:00 | 103.96 | 86.89
2019-07-05 16:30 | 104.06 | 87.21
2019-07-05 17:00 | 108.19 | 93.89
2019-07-05 17:30 | 111.44 | 98.14
2019-07-05 18:00 | 115.94 | 104.05
2019-07-05 18:30 | 117.81 | 106.18
2019-07-05 19:00 | 116.28 | 103.24
2019-07-05 19:30 | 122.83 | 111.51
2019-07-05 20:00 | 109.52 | 95.73
2019-07-05 20:30 | 118.54 | 106.68
2019-07-05 21:00 | 115.34 | 101.76
2019-07-05 21:30 | 115.93 | 102.39
2019-07-05 22:00 | 118.74 | 105.87
2019-07-05 22:30 | 113.34 | 100.4
2019-07-05 23:00 | 115.62 | 103.34
2019-07-05 23:30 | 117.84 | 105.97
2019-07-06 | 115.37 | 102.23
2019-07-06 00:30 | 118.71 | 106.24
2019-07-06 01:00 | 111.81 | 97.97
2019-07-06 01:30 | 111.84 | 98.89
2019-07-06 02:00 | 116.03 | 103.62
2019-07-06 02:30 | 114.84 | 100.9
2019-07-06 03:00 | 109.79 | 95.87
2019-07-06 03:30 | 106.04 | 91.93
2019-07-06 04:00 | 113.55 | 99.87
2019-07-06 04:30 | 114.68 | 101.32
2019-07-06 05:00 | 117.23 | 104.03
2019-07-06 05:30 | 119.14 | 106.82
2019-07-06 06:00 | 114.04 | 100.84
2019-07-06 06:30 | 114.46 | 101.22
2019-07-06 07:00 | 120.48 | 109.4
2019-07-06 07:30 | 121.19 | 110.52
2019-07-06 08:00 | 121.8 | 109.47
2019-07-06 08:30 | 113.09 | 99.88
2019-07-06 09:00 | 109.45 | 93.41
2019-07-06 09:30 | 110.31 | 93.61
2019-07-06 10:00 | 111.09 | 94.98
2019-07-06 10:30 | 111.73 | 94.09
2019-07-06 11:00 | 110.27 | 90.79
2019-07-06 11:30 | 104.65 | 82.08
2019-07-06 12:00 | 104.43 | 84.42
2019-07-06 12:30 | 106 | 86.36
2019-07-06 13:00 | 105.34 | 82.01
2019-07-06 13:30 | 108.29 | 87.6
2019-07-06 14:00 | 107.14 | 85.44
2019-07-06 14:30 | 108.99 | 90.01
2019-07-06 15:00 | 107.2 | 86.86
2019-07-06 15:30 | 107.3 | 88.01
2019-07-06 16:00 | 109.71 | 91.1
2019-07-06 16:30 | 105.38 | 87.32
2019-07-06 17:00 | 110 | 94.16
2019-07-06 17:30 | 112.26 | 97.71
2019-07-06 18:00 | 112.96 | 99.69
2019-07-06 18:30 | 112.16 | 98.47
2019-07-06 19:00 | 114.55 | 101.18
2019-07-06 19:30 | 120.34 | 108.27
2019-07-06 20:00 | 116.12 | 103.36
2019-07-06 20:30 | 115.18 | 101.31
2019-07-06 21:00 | 114.53 | 100.17
2019-07-06 21:30 | 113.26 | 98.47
2019-07-06 22:00 | 110.72 | 95.62
2019-07-06 22:30 | 107.59 | 91.48
2019-07-06 23:00 | 109.57 | 94.02
2019-07-06 23:30 | 112.76 | 98.02
2019-07-07 | 116.98 | 102.89
2019-07-07 00:30 | 115.75 | 101.21
2019-07-07 01:00 | 119.83 | 106.26
2019-07-07 01:30 | 122.48 | 109.26
2019-07-07 02:00 | 119.24 | 104.96
2019-07-07 02:30 | 124.68 | 110.86
2019-07-07 03:00 | 115 | 99.83
2019-07-07 03:30 | 111.43 | 96.54
2019-07-07 04:00 | 118.33 | 104.38
2019-07-07 04:30 | 114.48 | 99.69
2019-07-07 05:00 | 120.45 | 106.04
2019-07-07 05:30 | 109.87 | 93.79
2019-07-07 06:00 | 111.73 | 97.01
2019-07-07 06:30 | 116.42 | 102.65
2019-07-07 07:00 | 119.25 | 105.94
2019-07-07 07:30 | 129.81 | 117.1
2019-07-07 08:00 | 113.99 | 97.37
2019-07-07 08:30 | 108.94 | 88.53
2019-07-07 09:00 | 109.94 | 91.09
2019-07-07 09:30 | 107.42 | 88.93
2019-07-07 10:00 | 100.65 | 75.54
2019-07-07 10:30 | 103 | 82.12
2019-07-07 11:00 | 107.41 | 87.05
2019-07-07 11:30 | 107.61 | 85.97
2019-07-07 12:00 | 108.1 | 87.09
2019-07-07 12:30 | 108.65 | 86.22
2019-07-07 13:00 | 107.73 | 88.03
2019-07-07 13:30 | 111.32 | 91.87
2019-07-07 14:00 | 105.04 | 84.57
2019-07-07 14:30 | 112.88 | 94.96
2019-07-07 15:00 | 106.57 | 85.78
2019-07-07 15:30 | 112.31 | 94.35
2019-07-07 16:00 | 111.5 | 95.16
2019-07-07 16:30 | 108.89 | 92.22
2019-07-07 17:00 | 114.66 | 99.48
2019-07-07 17:30 | 119.77 | 105.53
2019-07-07 18:00 | 119.31 | 104.51
2019-07-07 18:30 | 105.31 | 90.15
2019-07-07 19:00 | 114.02 | 100.52
2019-07-07 19:30 | 104.35 | 88.74
2019-07-07 20:00 | 106.37 | 91.71
2019-07-07 20:30 | 111.07 | 96.52
2019-07-07 21:00 | 107.95 | 93.2
2019-07-07 21:30 | 105.53 | 89.61
2019-07-07 22:00 | 103.76 | 87.9
2019-07-07 22:30 | 104.25 | 88.92
2019-07-07 23:00 | 101.23 | 84.6
2019-07-07 23:30 | 100.09 | 82.33
2019-07-08 | 105.7 | 88.53
2019-07-08 00:30 | 106.55 | 90.28
2019-07-08 01:00 | 107.39 | 90.92
2019-07-08 01:30 | 104.15 | 86.1
2019-07-08 02:00 | 104.97 | 85.85
2019-07-08 02:30 | 103.57 | 84.32
2019-07-08 03:00 | 103.25 | 84.03
2019-07-08 03:30 | 103.3 | 83.45
2019-07-08 04:00 | 99.54 | 79.9
2019-07-08 04:30 | 101.29 | 82.53
2019-07-08 05:00 | 102.56 | 85.34
2019-07-08 05:30 | 97.78 | 78.33
2019-07-08 06:00 | 87.01 | 77.34
2019-07-08 06:30 | 80.77 | 78.24
2019-07-08 07:00 | 83.36 | 80.56
2019-07-08 07:30 | 84.27 | 81.16
2019-07-08 08:00 | 81.81 | 78.14
2019-07-08 08:30 | 78.58 | 74.41
2019-07-08 09:00 | 79.07 | 75.06
2019-07-08 09:30 | 76.48 | 72.13
2019-07-08 10:00 | 75.42 | 71.62
2019-07-08 10:30 | 73.33 | 69.05
2019-07-08 11:00 | 73.03 | 67.8
2019-07-08 11:30 | 68.1 | 61.55
2019-07-08 12:00 | 70.07 | 64.59
2019-07-08 12:30 | 75.49 | 72.2
2019-07-08 13:00 | 76.29 | 72.07
2019-07-08 13:30 | 76.9 | 72.67
2019-07-08 14:00 | 75.17 | 69.95
2019-07-08 14:30 | 74.88 | 69.78
2019-07-08 15:00 | 82.58 | 78.27
2019-07-08 15:30 | 84.9 | 79.98
2019-07-08 16:00 | 86.3 | 82.78
2019-07-08 16:30 | 85.58 | 82.35
2019-07-08 17:00 | 83.56 | 79.71
2019-07-08 17:30 | 88.98 | 84.86
2019-07-08 18:00 | 93.88 | 90.11
2019-07-08 18:30 | 94.89 | 92.14
2019-07-08 19:00 | 98.43 | 96.02
2019-07-08 19:30 | 92.07 | 89.53
2019-07-08 20:00 | 82.35 | 80.3
2019-07-08 20:30 | 82.1 | 80.63
2019-07-08 21:00 | 88.38 | 86.14
2019-07-08 21:30 | 92.26 | 89.75
2019-07-08 22:00 | 98.89 | 95.94
2019-07-08 22:30 | 98.6 | 95.5
2019-07-08 23:00 | 98.75 | 95.13
2019-07-08 23:30 | 102.02 | 98.2
2019-07-09 | 94.4 | 91.74
2019-07-09 00:30 | 93.15 | 90.67
2019-07-09 01:00 | 100.82 | 97.77
2019-07-09 01:30 | 95 | 91.4
2019-07-09 02:00 | 98.71 | 94.99
2019-07-09 02:30 | 102.37 | 98.52
2019-07-09 03:00 | 94.96 | 92.02
2019-07-09 03:30 | 88.83 | 85.8
2019-07-09 04:00 | 92.01 | 88.29
2019-07-09 04:30 | 94.48 | 90.63
2019-07-09 05:00 | 96.03 | 91.93
2019-07-09 05:30 | 95.29 | 91.34
2019-07-09 06:00 | 84.45 | 80.51
2019-07-09 06:30 | 81.38 | 78.49
2019-07-09 07:00 | 79.9 | 76.58
2019-07-09 07:30 | 75.7 | 72.34
2019-07-09 08:00 | 69.23 | 63.84
2019-07-09 08:30 | 65.17 | 57.26
2019-07-09 09:00 | 62.28 | 53.71
2019-07-09 09:30 | 62.63 | 53.03
2019-07-09 10:00 | 67.62 | 56.74
2019-07-09 10:30 | 70.45 | 59.95
2019-07-09 11:00 | 65.52 | 54.49
2019-07-09 11:30 | 67.19 | 56.5
2019-07-09 12:00 | 59.21 | 49.2
2019-07-09 12:30 | 61.06 | 50.29
2019-07-09 13:00 | 67.78 | 58.24
2019-07-09 13:30 | 67.27 | 55.97
2019-07-09 14:00 | 66.15 | 54.49
2019-07-09 14:30 | 68.84 | 58.15
2019-07-09 15:00 | 71.99 | 63.78
2019-07-09 15:30 | 69.23 | 61.01
2019-07-09 16:00 | 66.57 | 56.69
2019-07-09 16:30 | 67.87 | 59.71
2019-07-09 17:00 | 89.19 | 65.59
2019-07-09 17:30 | 99.35 | 70.01
2019-07-09 18:00 | 102.52 | 74.86
2019-07-09 18:30 | 104.14 | 81.81
2019-07-09 19:00 | 105.73 | 83.59
2019-07-09 19:30 | 109 | 89.15
2019-07-09 20:00 | 109.78 | 89.57
2019-07-09 20:30 | 112.02 | 91.54
2019-07-09 21:00 | 110.24 | 89.4
2019-07-09 21:30 | 117.68 | 99.95
2019-07-09 22:00 | 116.01 | 97.8
2019-07-09 22:30 | 116.42 | 97.77
2019-07-09 23:00 | 117.04 | 98.03
2019-07-09 23:30 | 119.56 | 100.17
2019-07-10 | 121.5 | 102.51
2019-07-10 00:30 | 117.93 | 97.59
2019-07-10 01:00 | 118.21 | 97.47
2019-07-10 01:30 | 121.49 | 102.65
2019-07-10 02:00 | 112.56 | 90.91
2019-07-10 02:30 | 118.88 | 99.91
2019-07-10 03:00 | 115.04 | 96.2
2019-07-10 03:30 | 110.67 | 91.29
2019-07-10 04:00 | 108.87 | 89.3
2019-07-10 04:30 | 107.43 | 87.34
2019-07-10 05:00 | 108.52 | 89.89
2019-07-10 05:30 | 106.35 | 87.35
2019-07-10 06:00 | 103.16 | 83.53
2019-07-10 06:30 | 103.56 | 86.32
2019-07-10 07:00 | 107.99 | 91.57
2019-07-10 07:30 | 107.87 | 90.98
2019-07-10 08:00 | 105.02 | 86.76
2019-07-10 08:30 | 102.77 | 83.31
2019-07-10 09:00 | 100.15 | 80.38
2019-07-10 09:30 | 105.66 | 87.25
2019-07-10 10:00 | 94.89 | 70.4
2019-07-10 10:30 | 93.82 | 68.13
2019-07-10 11:00 | 93.33 | 64.56
2019-07-10 11:30 | 90.39 | 61.5
2019-07-10 12:00 | 95.51 | 69.22
2019-07-10 12:30 | 92.14 | 64.14
2019-07-10 13:00 | 86.68 | 51.36
2019-07-10 13:30 | 89.06 | 56.11
2019-07-10 14:00 | 90.92 | 65.45
2019-07-10 14:30 | 92.54 | 69.32
2019-07-10 15:00 | 93.7 | 71.05
2019-07-10 15:30 | 89.62 | 64.72
2019-07-10 16:00 | 94.08 | 71.13
2019-07-10 16:30 | 97.23 | 78.74
2019-07-10 17:00 | 100.49 | 82.46
2019-07-10 17:30 | 106.99 | 91.97
2019-07-10 18:00 | 107.22 | 91.88
2019-07-10 18:30 | 105.47 | 88.69
2019-07-10 19:00 | 106.84 | 89.63
2019-07-10 19:30 | 107.18 | 90.26
2019-07-10 20:00 | 105.26 | 86.46
2019-07-10 20:30 | 104.35 | 85.57
2019-07-10 21:00 | 104.67 | 84.38
2019-07-10 21:30 | 108.31 | 88.15
2019-07-10 22:00 | 107.67 | 88.64
2019-07-10 22:30 | 108.44 | 89.72
2019-07-10 23:00 | 103.89 | 84.25
2019-07-10 23:30 | 110.94 | 93.28
2019-07-11 | 113.11 | 95.23
2019-07-11 00:30 | 112.28 | 94.35
2019-07-11 01:00 | 112.45 | 94.56
2019-07-11 01:30 | 108.57 | 89.46
2019-07-11 02:00 | 104.32 | 84.02
2019-07-11 02:30 | 106.41 | 88.54
2019-07-11 03:00 | 105.79 | 86.48
2019-07-11 03:30 | 103.39 | 83.46
2019-07-11 04:00 | 103.57 | 84.56
2019-07-11 04:30 | 104.2 | 86.2
2019-07-11 05:00 | 106.62 | 88.74
2019-07-11 05:30 | 109.66 | 93.07
2019-07-11 06:00 | 109.28 | 92.21
2019-07-11 06:30 | 108.4 | 91.27
2019-07-11 07:00 | 113.6 | 98.46
2019-07-11 07:30 | 109.97 | 94.15
2019-07-11 08:00 | 107.23 | 88.16
2019-07-11 08:30 | 98.6 | 74.3
2019-07-11 09:00 | 94.99 | 68.73
2019-07-11 09:30 | 92.98 | 60.22
2019-07-11 10:00 | 101.01 | 75.19
2019-07-11 10:30 | 100.3 | 73.1
2019-07-11 11:00 | 97.77 | 66.61
2019-07-11 11:30 | 99.02 | 67.51
2019-07-11 12:00 | 100 | 66.72
2019-07-11 12:30 | 103.67 | 72.44
2019-07-11 13:00 | 101.04 | 67.27
2019-07-11 13:30 | 101.46 | 68.47
2019-07-11 14:00 | 98.52 | 63.72
2019-07-11 14:30 | 96.58 | 58.42
2019-07-11 15:00 | 100.24 | 66.6
2019-07-11 15:30 | 90.55 | 54.29
2019-07-11 16:00 | 104.19 | 75.43
2019-07-11 16:30 | 111.34 | 88.44
2019-07-11 17:00 | 109.07 | 87.73
2019-07-11 17:30 | 112.07 | 95.02
2019-07-11 18:00 | 105.86 | 88.97
2019-07-11 18:30 | 99.48 | 82
2019-07-11 19:00 | 105.57 | 89.29
2019-07-11 19:30 | 100.9 | 83.41
2019-07-11 20:00 | 104.45 | 87.16
2019-07-11 20:30 | 111.49 | 96.11
2019-07-11 21:00 | 108.45 | 91.41
2019-07-11 21:30 | 111.49 | 94.73
2019-07-11 22:00 | 117.31 | 100.48
2019-07-11 22:30 | 110.44 | 92.11
2019-07-11 23:00 | 108.94 | 92.6
2019-07-11 23:30 | 106.84 | 90.47
2019-07-12 | 111 | 94.97
2019-07-12 00:30 | 113.74 | 98.73
2019-07-12 01:00 | 117.82 | 101.6
2019-07-12 01:30 | 116.51 | 100.15
2019-07-12 02:00 | 120.59 | 105.65
2019-07-12 02:30 | 116.8 | 100.18
2019-07-12 03:00 | 117.77 | 100.76
2019-07-12 03:30 | 113.53 | 95.53
2019-07-12 04:00 | 113.05 | 94.69
2019-07-12 04:30 | 109.6 | 91.44
2019-07-12 05:00 | 113.75 | 96.97
2019-07-12 05:30 | 113.86 | 97.06
2019-07-12 06:00 | 113.87 | 97.52
2019-07-12 06:30 | 110.24 | 94.54
2019-07-12 07:00 | 107.79 | 90.5
2019-07-12 07:30 | 103.87 | 84.92
2019-07-12 08:00 | 109.44 | 88.96
2019-07-12 08:30 | 113.05 | 90.63
2019-07-12 09:00 | 115.04 | 92.43
2019-07-12 09:30 | 106.81 | 80.05
2019-07-12 10:00 | 111.53 | 86.62
2019-07-12 10:30 | 117.38 | 93.08
2019-07-12 11:00 | 114.78 | 88.27
2019-07-12 11:30 | 113.65 | 87.42
2019-07-12 12:00 | 105.26 | 74.47
2019-07-12 12:30 | 108.58 | 78.02
2019-07-12 13:00 | 109.82 | 78.8
2019-07-12 13:30 | 113.82 | 86.17
2019-07-12 14:00 | 112.27 | 84.42
2019-07-12 14:30 | 111.45 | 83.03
2019-07-12 15:00 | 109.42 | 81.28
2019-07-12 15:30 | 112.77 | 85.11
2019-07-12 16:00 | 117.13 | 92.45
2019-07-12 16:30 | 114.43 | 90.48
2019-07-12 17:00 | 118.82 | 98.96
2019-07-12 17:30 | 117.72 | 100.63
2019-07-12 18:00 | 117.35 | 100.27
2019-07-12 18:30 | 118.58 | 103.44
2019-07-12 19:00 | 122.68 | 109.24
2019-07-12 19:30 | 122.72 | 109.91
2019-07-12 20:00 | 120.3 | 106.89
2019-07-12 20:30 | 121.57 | 106.73
2019-07-12 21:00 | 117.15 | 100.6
2019-07-12 21:30 | 114.62 | 98.18
2019-07-12 22:00 | 119.38 | 104.2
2019-07-12 22:30 | 122.35 | 106.66
2019-07-12 23:00 | 121.75 | 105.27
2019-07-12 23:30 | 111.95 | 91.59
2019-07-13 | 115.13 | 95.83
2019-07-13 00:30 | 112.82 | 91.63
2019-07-13 01:00 | 118.54 | 97.84
2019-07-13 01:30 | 120.88 | 101.01
2019-07-13 02:00 | 119.65 | 98.52
2019-07-13 02:30 | 123.63 | 104.81
2019-07-13 03:00 | 122.66 | 103.15
2019-07-13 03:30 | 118.65 | 98.64
2019-07-13 04:00 | 114.88 | 93.89
2019-07-13 04:30 | 119.04 | 99.98
2019-07-13 05:00 | 116.72 | 97.98
2019-07-13 05:30 | 120.81 | 102.39
2019-07-13 06:00 | 118.92 | 100.05
2019-07-13 06:30 | 112.42 | 92.74
2019-07-13 07:00 | 116.52 | 96.96
2019-07-13 07:30 | 116.13 | 97.74
2019-07-13 08:00 | 113.21 | 90.68
2019-07-13 08:30 | 103.69 | 73.98
2019-07-13 09:00 | 103.58 | 71.59
2019-07-13 09:30 | 112.01 | 81.63
2019-07-13 10:00 | 105.28 | 70.73
2019-07-13 10:30 | 113.53 | 82.49
2019-07-13 11:00 | 114.09 | 82.72
2019-07-13 11:30 | 105.76 | 72.66
2019-07-13 12:00 | 107.87 | 75.27
2019-07-13 12:30 | 109.49 | 78.2
2019-07-13 13:00 | 102.6 | 69.71
2019-07-13 13:30 | 105.36 | 75.72
2019-07-13 14:00 | 107.12 | 74.65
2019-07-13 14:30 | 108.33 | 75.81
2019-07-13 15:00 | 109.71 | 78.6
2019-07-13 15:30 | 107.38 | 75.38
2019-07-13 16:00 | 112.43 | 84.92
2019-07-13 16:30 | 114.5 | 89.35
2019-07-13 17:00 | 110.27 | 86.08
2019-07-13 17:30 | 115.56 | 97.23
2019-07-13 18:00 | 119.41 | 102.46
2019-07-13 18:30 | 120.89 | 103.93
2019-07-13 19:00 | 127.53 | 112.16
2019-07-13 19:30 | 125.61 | 109
2019-07-13 20:00 | 124.63 | 107.75
2019-07-13 20:30 | 120.9 | 103.81
2019-07-13 21:00 | 126.58 | 110.91
2019-07-13 21:30 | 124.52 | 108.07
2019-07-13 22:00 | 127.57 | 111.4
2019-07-13 22:30 | 126.91 | 109.96
2019-07-13 23:00 | 127.95 | 111.34
2019-07-13 23:30 | 125.35 | 108.42
2019-07-14 | 123.82 | 106.46
2019-07-14 00:30 | 121.58 | 104.55
2019-07-14 01:00 | 124.07 | 106.38
2019-07-14 01:30 | 125.44 | 107.62
2019-07-14 02:00 | 120.24 | 102.23
2019-07-14 02:30 | 119.88 | 102.08
2019-07-14 03:00 | 119.99 | 101.37
2019-07-14 03:30 | 117.98 | 98.75
2019-07-14 04:00 | 122.34 | 104.43
2019-07-14 04:30 | 123.01 | 105.73
2019-07-14 05:00 | 124.11 | 106.16
2019-07-14 05:30 | 124.88 | 107.88
2019-07-14 06:00 | 114.47 | 93.66
2019-07-14 06:30 | 116.01 | 98.69
2019-07-14 07:00 | 120.69 | 103.59
2019-07-14 07:30 | 118.35 | 100.17
2019-07-14 08:00 | 117.16 | 94.71
2019-07-14 08:30 | 109.91 | 81.68
2019-07-14 09:00 | 109.22 | 77.8
2019-07-14 09:30 | 107.3 | 75.18
2019-07-14 10:00 | 104.26 | 69.92
2019-07-14 10:30 | 106.12 | 73.2
2019-07-14 11:00 | 106.12 | 73.63
2019-07-14 11:30 | 110.18 | 78.76
2019-07-14 12:00 | 113.96 | 84.95
2019-07-14 12:30 | 117.57 | 89.93
2019-07-14 13:00 | 112.88 | 81.71
2019-07-14 13:30 | 107.53 | 73.5
2019-07-14 14:00 | 107.22 | 72.44
2019-07-14 14:30 | 109.17 | 74.83
2019-07-14 15:00 | 110.03 | 73.82
2019-07-14 15:30 | 112.47 | 79.69
2019-07-14 16:00 | 115.59 | 86.62
2019-07-14 16:30 | 114.19 | 87.19
2019-07-14 17:00 | 118.75 | 96.52
2019-07-14 17:30 | 120.34 | 101.72
2019-07-14 18:00 | 122.71 | 106.33
2019-07-14 18:30 | 123.83 | 109.08
2019-07-14 19:00 | 126.38 | 111.51
2019-07-14 19:30 | 121.89 | 105.63
2019-07-14 20:00 | 120.18 | 103.93
2019-07-14 20:30 | 118.46 | 101.44
2019-07-14 21:00 | 121.8 | 106.49
2019-07-14 21:30 | 122.61 | 107.26
2019-07-14 22:00 | 117.63 | 101.14
2019-07-14 22:30 | 119.97 | 102.77
2019-07-14 23:00 | 124.23 | 107.08
2019-07-14 23:30 | 125.79 | 110.05
2019-07-15 | 118.55 | 102.24
2019-07-15 00:30 | 123.32 | 107.15
2019-07-15 01:00 | 116.38 | 97.39
2019-07-15 01:30 | 121.65 | 104.28
2019-07-15 02:00 | 108.02 | 88.7
2019-07-15 02:30 | 111.36 | 92.68
2019-07-15 03:00 | 118.23 | 101.77
2019-07-15 03:30 | 117.56 | 100.21
2019-07-15 04:00 | 121.52 | 105.8
2019-07-15 04:30 | 118.23 | 102.05
2019-07-15 05:00 | 113.6 | 95.04
2019-07-15 05:30 | 113.5 | 95.75
2019-07-15 06:00 | 110.83 | 91.23
2019-07-15 06:30 | 110.39 | 92.41
2019-07-15 07:00 | 113.94 | 97.37
2019-07-15 07:30 | 121.39 | 105.95
2019-07-15 08:00 | 123.71 | 104.72
2019-07-15 08:30 | 113.67 | 86.82
2019-07-15 09:00 | 118.36 | 97.44
2019-07-15 09:30 | 109.55 | 86.65
2019-07-15 10:00 | 107.03 | 83.3
2019-07-15 10:30 | 102.66 | 79.49
2019-07-15 11:00 | 107.54 | 82.67
2019-07-15 11:30 | 106.84 | 83.44
2019-07-15 12:00 | 108.85 | 85.28
2019-07-15 12:30 | 107.41 | 85.31
2019-07-15 13:00 | 111.88 | 90.42
2019-07-15 13:30 | 111.75 | 88.72
2019-07-15 14:00 | 118.94 | 99.06
2019-07-15 14:30 | 116.85 | 96.99
2019-07-15 15:00 | 111.4 | 80.67
2019-07-15 15:30 | 105.01 | 68.34
2019-07-15 16:00 | 107.44 | 72.96
2019-07-15 16:30 | 105.83 | 76.37
2019-07-15 17:00 | 111.4 | 86.73
2019-07-15 17:30 | 118.78 | 99.63
2019-07-15 18:00 | 126.29 | 109.39
2019-07-15 18:30 | 127.19 | 111.08
2019-07-15 19:00 | 130.28 | 115.05
2019-07-15 19:30 | 127.89 | 111.55
2019-07-15 20:00 | 127.16 | 109.64
2019-07-15 20:30 | 126.48 | 110.18
2019-07-15 21:00 | 128.32 | 109.74
2019-07-15 21:30 | 128.65 | 112.35
2019-07-15 22:00 | 127.81 | 111.57
2019-07-15 22:30 | 129.2 | 112.74
2019-07-15 23:00 | 133.24 | 116.26
2019-07-15 23:30 | 126.36 | 108.6
2019-07-16 | 129.99 | 112.1
2019-07-16 00:30 | 129.01 | 111.12
2019-07-16 01:00 | 125.96 | 105.97
2019-07-16 01:30 | 126.64 | 106.96
2019-07-16 02:00 | 122.78 | 101.66
2019-07-16 02:30 | 122.15 | 100.56
2019-07-16 03:00 | 118.8 | 97.86
2019-07-16 03:30 | 118.41 | 96.11
2019-07-16 04:00 | 118.3 | 95.32
2019-07-16 04:30 | 119.19 | 96.23
2019-07-16 05:00 | 114.91 | 92.64
2019-07-16 05:30 | 115.14 | 93.99
2019-07-16 06:00 | 110.77 | 91.71
2019-07-16 06:30 | 113.11 | 93.51
2019-07-16 07:00 | 115.86 | 98.87
2019-07-16 07:30 | 117.04 | 99.1
2019-07-16 08:00 | 109.15 | 89.02
2019-07-16 08:30 | 109.26 | 76.69
2019-07-16 09:00 | 107.42 | 74.13
2019-07-16 09:30 | 107.66 | 69.59
2019-07-16 10:00 | 108.47 | 66.43
2019-07-16 10:30 | 109.5 | 71.62
2019-07-16 11:00 | 109.63 | 68.77
2019-07-16 11:30 | 109.67 | 66.75
2019-07-16 12:00 | 106.85 | 67.83
2019-07-16 12:30 | 106.21 | 67.48
2019-07-16 13:00 | 112.4 | 75.55
2019-07-16 13:30 | 109.72 | 72.84
2019-07-16 14:00 | 107.74 | 71.24
2019-07-16 14:30 | 110.99 | 74.38
2019-07-16 15:00 | 116.31 | 77.04
2019-07-16 15:30 | 114.76 | 77.62
2019-07-16 16:00 | 111.51 | 75
2019-07-16 16:30 | 107.29 | 70.77
2019-07-16 17:00 | 118.43 | 93.08
2019-07-16 17:30 | 125.33 | 104.5
2019-07-16 18:00 | 124.44 | 102.93
2019-07-16 18:30 | 119.15 | 97.89
2019-07-16 19:00 | 127.53 | 107.76
2019-07-16 19:30 | 129.56 | 110.06
2019-07-16 20:00 | 129.01 | 110.86
2019-07-16 20:30 | 127.85 | 108.51
2019-07-16 21:00 | 125.01 | 103.57
2019-07-16 21:30 | 118.43 | 95.73
2019-07-16 22:00 | 124.81 | 103
2019-07-16 22:30 | 127.72 | 106.17
2019-07-16 23:00 | 129.3 | 108.9
2019-07-16 23:30 | 126.33 | 106.5
2019-07-17 | 117.5 | 96.26
2019-07-17 00:30 | 117.16 | 94.79
2019-07-17 01:00 | 119.74 | 100.76
2019-07-17 01:30 | 120.24 | 101.41
2019-07-17 02:00 | 119.85 | 100.18
2019-07-17 02:30 | 121.04 | 100.74
2019-07-17 03:00 | 115.27 | 94.22
2019-07-17 03:30 | 114.16 | 91.58
2019-07-17 04:00 | 115.41 | 95.21
2019-07-17 04:30 | 107.87 | 85.38
2019-07-17 05:00 | 114.4 | 94.12
2019-07-17 05:30 | 113.06 | 92.53
2019-07-17 06:00 | 110.09 | 89.24
2019-07-17 06:30 | 108.78 | 88.45
2019-07-17 07:00 | 114.1 | 94.72
2019-07-17 07:30 | 111.52 | 90.41
2019-07-17 08:00 | 104.03 | 80.25
2019-07-17 08:30 | 112.9 | 87.78
2019-07-17 09:00 | 105.85 | 74.42
2019-07-17 09:30 | 104.83 | 72.82
2019-07-17 10:00 | 101.86 | 65.96
2019-07-17 10:30 | 106.02 | 72.34
2019-07-17 11:00 | 105.14 | 72.33
2019-07-17 11:30 | 107.8 | 75.91
2019-07-17 12:00 | 104.45 | 71.2
2019-07-17 12:30 | 102.73 | 74.06
2019-07-17 13:00 | 104.4 | 67.59
2019-07-17 13:30 | 102.08 | 64.78
2019-07-17 14:00 | 100.97 | 64.05
2019-07-17 14:30 | 101.86 | 66.51
2019-07-17 15:00 | 100.06 | 61.86
2019-07-17 15:30 | 98.47 | 59.73
2019-07-17 16:00 | 100.68 | 66.4
2019-07-17 16:30 | 102.96 | 73.44
2019-07-17 17:00 | 103.81 | 77.79
2019-07-17 17:30 | 105.09 | 82.38
2019-07-17 18:00 | 115.83 | 97.86
2019-07-17 18:30 | 115.4 | 96.93
2019-07-17 19:00 | 117.23 | 100.09
2019-07-17 19:30 | 118.06 | 101.14
2019-07-17 20:00 | 114.08 | 96.65
2019-07-17 20:30 | 117.61 | 100.95
2019-07-17 21:00 | 113.56 | 94.69
2019-07-17 21:30 | 114.81 | 95.33
2019-07-17 22:00 | 115.12 | 96.69
2019-07-17 22:30 | 112.03 | 92.22
2019-07-17 23:00 | 110.88 | 90.88
2019-07-17 23:30 | 109.6 | 88.53
2019-07-18 | 113.35 | 92.79
2019-07-18 00:30 | 111.73 | 90.24
2019-07-18 01:00 | 115.75 | 96.61
2019-07-18 01:30 | 113.64 | 93.09
2019-07-18 02:00 | 111.03 | 90.86
2019-07-18 02:30 | 120 | 102.59
2019-07-18 03:00 | 120.61 | 103.32
2019-07-18 03:30 | 113 | 93.78
2019-07-18 04:00 | 118.88 | 101.41
2019-07-18 04:30 | 116.96 | 96.73
2019-07-18 05:00 | 124.05 | 106.62
2019-07-18 05:30 | 114.13 | 94.59
2019-07-18 06:00 | 112.37 | 94.33
2019-07-18 06:30 | 105.9 | 85.15
2019-07-18 07:00 | 106.46 | 83.44
2019-07-18 07:30 | 107.43 | 83.77
2019-07-18 08:00 | 103.2 | 75.21
2019-07-18 08:30 | 106.71 | 78.65
2019-07-18 09:00 | 102.6 | 68.84
2019-07-18 09:30 | 102.81 | 70.64
2019-07-18 10:00 | 104.85 | 72.16
2019-07-18 10:30 | 103.6 | 66.7
2019-07-18 11:00 | 108.14 | 77.04
2019-07-18 11:30 | 102.09 | 65.87
2019-07-18 12:00 | 100.12 | 62.78
2019-07-18 12:30 | 99.75 | 62.31
2019-07-18 13:00 | 96.51 | 56.76
2019-07-18 13:30 | 103.18 | 67.17
2019-07-18 14:00 | 103.81 | 69
2019-07-18 14:30 | 101.12 | 63.62
2019-07-18 15:00 | 105.81 | 71.62
2019-07-18 15:30 | 105.86 | 69.41
2019-07-18 16:00 | 103.57 | 67
2019-07-18 16:30 | 103.15 | 68.92
2019-07-18 17:00 | 112.05 | 87.3
2019-07-18 17:30 | 107.62 | 85.38
2019-07-18 18:00 | 109.51 | 88.62
2019-07-18 18:30 | 113.2 | 93.53
2019-07-18 19:00 | 115.14 | 98.39
2019-07-18 19:30 | 114.05 | 96.53
2019-07-18 20:00 | 117.72 | 102.35
2019-07-18 20:30 | 118.39 | 104.1
2019-07-18 21:00 | 115.1 | 98.86
2019-07-18 21:30 | 112.65 | 95.89
2019-07-18 22:00 | 113.77 | 96.72
2019-07-18 22:30 | 119.71 | 104.12
2019-07-18 23:00 | 115.72 | 97.99
2019-07-18 23:30 | 115.22 | 96.8
2019-07-19 | 118.09 | 101.22
2019-07-19 00:30 | 115.07 | 96.2
2019-07-19 01:00 | 114.46 | 95.92
2019-07-19 01:30 | 118.02 | 100.72
2019-07-19 02:00 | 129.36 | 115.31
2019-07-19 02:30 | 128.08 | 112.69
2019-07-19 03:00 | 128.63 | 112.38
2019-07-19 03:30 | 123.6 | 106.3
2019-07-19 04:00 | 122.93 | 105.88
2019-07-19 04:30 | 127.42 | 112.35
2019-07-19 05:00 | 125.59 | 108.46
2019-07-19 05:30 | 121.94 | 104.59
2019-07-19 06:00 | 118.44 | 100.38
2019-07-19 06:30 | 112.38 | 93.26
2019-07-19 07:00 | 119.54 | 101.66
2019-07-19 07:30 | 117.78 | 99.41
2019-07-19 08:00 | 105.83 | 79.32
2019-07-19 08:30 | 110.22 | 82.8
2019-07-19 09:00 | 110.29 | 83.53
2019-07-19 09:30 | 108.98 | 79.29
2019-07-19 10:00 | 101.95 | 69.9
2019-07-19 10:30 | 99.54 | 64.84
2019-07-19 11:00 | 100.55 | 65.99
2019-07-19 11:30 | 104.4 | 71.29
2019-07-19 12:00 | 104.57 | 71.66
2019-07-19 12:30 | 107.25 | 73.21
2019-07-19 13:00 | 108.99 | 77.81
2019-07-19 13:30 | 99.15 | 66.07
2019-07-19 14:00 | 102.53 | 70.05
2019-07-19 14:30 | 102.94 | 67.05
2019-07-19 15:00 | 99.45 | 62.34
2019-07-19 15:30 | 97.49 | 60.74
2019-07-19 16:00 | 101.88 | 69.11
2019-07-19 16:30 | 108.02 | 79.72
2019-07-19 17:00 | 109.01 | 84.13
2019-07-19 17:30 | 115.63 | 96.29
2019-07-19 18:00 | 120.73 | 101.52
2019-07-19 18:30 | 122.08 | 104.66
2019-07-19 19:00 | 121.03 | 102.99
2019-07-19 19:30 | 120 | 101.6
2019-07-19 20:00 | 120.97 | 103.6
2019-07-19 20:30 | 120.78 | 103.96
2019-07-19 21:00 | 122 | 104.84
2019-07-19 21:30 | 122.46 | 103.96
2019-07-19 22:00 | 120.03 | 100.08
2019-07-19 22:30 | 122.2 | 103.21
2019-07-19 23:00 | 121.76 | 102.87
2019-07-19 23:30 | 120.72 | 102.3
2019-07-20 | 124.92 | 106.7
2019-07-20 00:30 | 120.69 | 101.84
2019-07-20 01:00 | 121.56 | 102.42
2019-07-20 01:30 | 122.31 | 103.71
2019-07-20 02:00 | 117.93 | 97.49
2019-07-20 02:30 | 112.09 | 92.62
2019-07-20 03:00 | 110.07 | 90.82
2019-07-20 03:30 | 109.96 | 91.3
2019-07-20 04:00 | 108.45 | 90.71
2019-07-20 04:30 | 108.42 | 90.02
2019-07-20 05:00 | 113.47 | 96.86
2019-07-20 05:30 | 114.96 | 99.55
2019-07-20 06:00 | 107.38 | 89.48
2019-07-20 06:30 | 113.77 | 97.96
2019-07-20 07:00 | 125.31 | 112.24
2019-07-20 07:30 | 116.91 | 101.96
2019-07-20 08:00 | 114.21 | 94.03
2019-07-20 08:30 | 108.09 | 80.91
2019-07-20 09:00 | 106.64 | 78.47
2019-07-20 09:30 | 117.21 | 96.97
2019-07-20 10:00 | 116.03 | 96.55
2019-07-20 10:30 | 116.04 | 95.21
2019-07-20 11:00 | 111.63 | 82.76
2019-07-20 11:30 | 103.83 | 68.97
2019-07-20 12:00 | 110.17 | 80.48
2019-07-20 12:30 | 98.67 | 63.46
2019-07-20 13:00 | 98.75 | 63.65
2019-07-20 13:30 | 101.31 | 66.14
2019-07-20 14:00 | 102.41 | 70.78
2019-07-20 14:30 | 98.46 | 64.48
2019-07-20 15:00 | 102.83 | 70.67
2019-07-20 15:30 | 92.92 | 55.02
2019-07-20 16:00 | 97.89 | 63.92
2019-07-20 16:30 | 105.13 | 77.78
2019-07-20 17:00 | 108.93 | 85.95
2019-07-20 17:30 | 110.29 | 90.6
2019-07-20 18:00 | 111.58 | 92.92
2019-07-20 18:30 | 112.05 | 93.36
2019-07-20 19:00 | 114.63 | 97.27
2019-07-20 19:30 | 118.14 | 100.61
2019-07-20 20:00 | 120.84 | 103.94
2019-07-20 20:30 | 118.37 | 99.04
2019-07-20 21:00 | 114.54 | 95.08
2019-07-20 21:30 | 112.52 | 91.89
2019-07-20 22:00 | 112.99 | 92.6
2019-07-20 22:30 | 117.46 | 99.69
2019-07-20 23:00 | 116.5 | 97.88
2019-07-20 23:30 | 111.02 | 89.88
2019-07-21 | 116.8 | 99.59
2019-07-21 00:30 | 110.18 | 90.14
2019-07-21 01:00 | 113.62 | 92.75
2019-07-21 01:30 | 108.53 | 86.08
2019-07-21 02:00 | 110.44 | 88.67
2019-07-21 02:30 | 115.8 | 96.28
2019-07-21 03:00 | 114.48 | 94.08
2019-07-21 03:30 | 112.93 | 92.82
2019-07-21 04:00 | 113.3 | 91.94
2019-07-21 04:30 | 116.91 | 96.75
2019-07-21 05:00 | 113.36 | 93.45
2019-07-21 05:30 | 114.21 | 95.6
2019-07-21 06:00 | 107.74 | 86.18
2019-07-21 06:30 | 98.49 | 75.49
2019-07-21 07:00 | 98.6 | 77.23
2019-07-21 07:30 | 97.06 | 73.98
2019-07-21 08:00 | 96.27 | 69.21
2019-07-21 08:30 | 88.99 | 52.46
2019-07-21 09:00 | 91.51 | 54.99
2019-07-21 09:30 | 91.83 | 52.01
2019-07-21 10:00 | 95.85 | 59.49
2019-07-21 10:30 | 97.6 | 61.07
2019-07-21 11:00 | 94.39 | 53.96
2019-07-21 11:30 | 94.92 | 55
2019-07-21 12:00 | 95.36 | 59.15
2019-07-21 12:30 | 90.21 | 53.61
2019-07-21 13:00 | 93.52 | 55.86
2019-07-21 13:30 | 103.12 | 73.25
2019-07-21 14:00 | 103.04 | 74.52
2019-07-21 14:30 | 105.82 | 78.72
2019-07-21 15:00 | 103.12 | 73.23
2019-07-21 15:30 | 108.19 | 81.04
2019-07-21 16:00 | 103.22 | 73.11
2019-07-21 16:30 | 103.57 | 76.21
2019-07-21 17:00 | 108.55 | 86.25
2019-07-21 17:30 | 113.92 | 95.45
2019-07-21 18:00 | 114.86 | 96.52
2019-07-21 18:30 | 120.06 | 101.76
2019-07-21 19:00 | 125.85 | 109.19
2019-07-21 19:30 | 118.12 | 97.71
2019-07-21 20:00 | 125.27 | 107.97
2019-07-21 20:30 | 120.68 | 102.46
2019-07-21 21:00 | 122.64 | 104.32
2019-07-21 21:30 | 120.7 | 100.1
2019-07-21 22:00 | 117.93 | 97.2
2019-07-21 22:30 | 124.89 | 106.13
2019-07-21 23:00 | 130.05 | 112.43
2019-07-21 23:30 | 120.77 | 99.13
2019-07-22 | 123.11 | 103.55
2019-07-22 00:30 | 121.84 | 100.12
2019-07-22 01:00 | 125.9 | 106.61
2019-07-22 01:30 | 121.98 | 99.82
2019-07-22 02:00 | 118.22 | 97.06
2019-07-22 02:30 | 117.7 | 95.38
2019-07-22 03:00 | 118.95 | 97.61
2019-07-22 03:30 | 120.13 | 99.15
2019-07-22 04:00 | 120.52 | 99.4
2019-07-22 04:30 | 115.92 | 95.43
2019-07-22 05:00 | 119.62 | 98.49
2019-07-22 05:30 | 119.99 | 98.61
2019-07-22 06:00 | 116.91 | 95.56
2019-07-22 06:30 | 96.39 | 68.23
2019-07-22 07:00 | 98.61 | 74.18
2019-07-22 07:30 | 91.64 | 66.11
2019-07-22 08:00 | 91.25 | 63.25
2019-07-22 08:30 | 95.34 | 66.34
2019-07-22 09:00 | 98.42 | 69.21
2019-07-22 09:30 | 94.71 | 57.5
2019-07-22 10:00 | 94.62 | 56.49
2019-07-22 10:30 | 101.41 | 68.26
2019-07-22 11:00 | 102 | 69.2
2019-07-22 11:30 | 100.71 | 67.12
2019-07-22 12:00 | 101.89 | 69.52
2019-07-22 12:30 | 101.7 | 68.84
2019-07-22 13:00 | 105.37 | 71.29
2019-07-22 13:30 | 104.4 | 69.22
2019-07-22 14:00 | 104.42 | 68.04
2019-07-22 14:30 | 105.59 | 73.64
2019-07-22 15:00 | 105.63 | 73.15
2019-07-22 15:30 | 101.23 | 65.77
2019-07-22 16:00 | 99.55 | 63.81
2019-07-22 16:30 | 103.74 | 77.51
2019-07-22 17:00 | 105.76 | 80.57
2019-07-22 17:30 | 109.42 | 88.01
2019-07-22 18:00 | 111.46 | 90.32
2019-07-22 18:30 | 109.24 | 87.17
2019-07-22 19:00 | 114.6 | 95
2019-07-22 19:30 | 111.49 | 91.15
2019-07-22 20:00 | 113.04 | 92.41
2019-07-22 20:30 | 125.01 | 108.51
2019-07-22 21:00 | 121.58 | 101.58
2019-07-22 21:30 | 116.41 | 96.58
2019-07-22 22:00 | 115.54 | 94.77
2019-07-22 22:30 | 117.45 | 96.52
2019-07-22 23:00 | 119.16 | 98.41
2019-07-22 23:30 | 110.61 | 85.76
2019-07-23 | 107.3 | 83.41
2019-07-23 00:30 | 104.16 | 80.79
2019-07-23 01:00 | 102.6 | 79.35
2019-07-23 01:30 | 108.65 | 88.05
2019-07-23 02:00 | 112.19 | 90.75
2019-07-23 02:30 | 107.77 | 86.34
2019-07-23 03:00 | 109.08 | 85.14
2019-07-23 03:30 | 111.31 | 88.19
2019-07-23 04:00 | 105.42 | 80.36
2019-07-23 04:30 | 107.51 | 82.41
2019-07-23 05:00 | 106.87 | 82.6
2019-07-23 05:30 | 105.88 | 77.85
2019-07-23 06:00 | 107.45 | 82.04
2019-07-23 06:30 | 105.57 | 78.61
2019-07-23 07:00 | 108.36 | 83.76
2019-07-23 07:30 | 111.59 | 88.61
2019-07-23 08:00 | 109.66 | 82.41
2019-07-23 08:30 | 109.87 | 77.06
2019-07-23 09:00 | 106.63 | 72.25
2019-07-23 09:30 | 106.22 | 71.84
2019-07-23 10:00 | 104.38 | 67.97
2019-07-23 10:30 | 104.82 | 69.39
2019-07-23 11:00 | 100.64 | 64.01
2019-07-23 11:30 | 99.25 | 61.18
2019-07-23 12:00 | 99.75 | 61.24
2019-07-23 12:30 | 104.31 | 66.9
2019-07-23 13:00 | 108.62 | 77.2
2019-07-23 13:30 | 102.45 | 63.96
2019-07-23 14:00 | 107.18 | 76
2019-07-23 14:30 | 104.07 | 70.52
2019-07-23 15:00 | 105.68 | 73.72
2019-07-23 15:30 | 98.65 | 61.87
2019-07-23 16:00 | 99.96 | 67.1
2019-07-23 16:30 | 101.28 | 71.59
2019-07-23 17:00 | 106.08 | 79.57
2019-07-23 17:30 | 109.54 | 89.44
2019-07-23 18:00 | 107.86 | 86.75
2019-07-23 18:30 | 104.79 | 83.92
2019-07-23 19:00 | 114.15 | 96.65
2019-07-23 19:30 | 110.32 | 90.71
2019-07-23 20:00 | 115.9 | 97.2
2019-07-23 20:30 | 112.47 | 91.87
2019-07-23 21:00 | 111.4 | 90.93
2019-07-23 21:30 | 109.1 | 88.97
2019-07-23 22:00 | 109.3 | 89.7
2019-07-23 22:30 | 110.48 | 91.58
2019-07-23 23:00 | 108.33 | 87.22
2019-07-23 23:30 | 102.13 | 78.47
2019-07-24 | 108.45 | 86.63
2019-07-24 00:30 | 109.65 | 88.55
2019-07-24 01:00 | 108.85 | 88.99
2019-07-24 01:30 | 108.25 | 86.25
2019-07-24 02:00 | 107.71 | 83.5
2019-07-24 02:30 | 113.64 | 92.56
2019-07-24 03:00 | 110.51 | 86.61
2019-07-24 03:30 | 113.2 | 92.58
2019-07-24 04:00 | 116.24 | 96.74
2019-07-24 04:30 | 109.24 | 86.57
2019-07-24 05:00 | 111.42 | 91.07
2019-07-24 05:30 | 107.53 | 87.47
2019-07-24 06:00 | 105.51 | 83.64
2019-07-24 06:30 | 110.64 | 91.74
2019-07-24 07:00 | 112.76 | 92.77
2019-07-24 07:30 | 112.06 | 91.78
2019-07-24 08:00 | 109.05 | 83.44
2019-07-24 08:30 | 104.04 | 73.11
2019-07-24 09:00 | 99.27 | 62.32
2019-07-24 09:30 | 104.1 | 67.92
2019-07-24 10:00 | 101.58 | 61.5
2019-07-24 10:30 | 101.3 | 61.7
2019-07-24 11:00 | 100.6 | 59.26
2019-07-24 11:30 | 100.71 | 59.73
2019-07-24 12:00 | 98.9 | 55.25
2019-07-24 12:30 | 102.21 | 62.17
2019-07-24 13:00 | 101.81 | 64.75
2019-07-24 13:30 | 100.57 | 62.65
2019-07-24 14:00 | 102.26 | 65.14
2019-07-24 14:30 | 101.81 | 64.94
2019-07-24 15:00 | 100.33 | 60.9
2019-07-24 15:30 | 104.83 | 68.08
2019-07-24 16:00 | 106.35 | 71.98
2019-07-24 16:30 | 105.15 | 74.09
2019-07-24 17:00 | 104.79 | 78.2
2019-07-24 17:30 | 107.23 | 85.12
2019-07-24 18:00 | 110.13 | 87.93
2019-07-24 18:30 | 111.56 | 91.29
2019-07-24 19:00 | 101.31 | 88.91
2019-07-24 19:30 | 95.83 | 82.71
2019-07-24 20:00 | 106.2 | 92.1
2019-07-24 20:30 | 111.09 | 95.77
2019-07-24 21:00 | 107.5 | 88.93
2019-07-24 21:30 | 107.81 | 90.4
2019-07-24 22:00 | 115.88 | 97.74
2019-07-24 22:30 | 117.37 | 99.12
2019-07-24 23:00 | 108.56 | 85.09
2019-07-24 23:30 | 108.64 | 85.48
2019-07-25 | 110.79 | 90.78
2019-07-25 00:30 | 107.69 | 86.86
2019-07-25 01:00 | 111.26 | 91.84
2019-07-25 01:30 | 114.3 | 95.69
2019-07-25 02:00 | 109.83 | 88.16
2019-07-25 02:30 | 109.99 | 89.75
2019-07-25 03:00 | 102.59 | 76.03
2019-07-25 03:30 | 105.99 | 82.59
2019-07-25 04:00 | 107.73 | 85.31
2019-07-25 04:30 | 108.39 | 86.67
2019-07-25 05:00 | 114.19 | 94.48
2019-07-25 05:30 | 114.3 | 95.18
2019-07-25 06:00 | 104.41 | 82.4
2019-07-25 06:30 | 100.56 | 77.85
2019-07-25 07:00 | 109.58 | 87
2019-07-25 07:30 | 107.11 | 82.3
2019-07-25 08:00 | 99.25 | 69.35
2019-07-25 08:30 | 92.81 | 56.83
2019-07-25 09:00 | 96.35 | 60.27
2019-07-25 09:30 | 93.39 | 54.96
2019-07-25 10:00 | 95.13 | 57.4
2019-07-25 10:30 | 94.35 | 55.5
2019-07-25 11:00 | 87.63 | 44.28
2019-07-25 11:30 | 88.7 | 42.87
2019-07-25 12:00 | 90.47 | 45.77
2019-07-25 12:30 | 96.45 | 59.6
2019-07-25 13:00 | 96.57 | 58.56
2019-07-25 13:30 | 94.17 | 52.78
2019-07-25 14:00 | 96.27 | 57.16
2019-07-25 14:30 | 98.3 | 61.07
2019-07-25 15:00 | 99 | 62.68
2019-07-25 15:30 | 96.14 | 55.12
2019-07-25 16:00 | 98.94 | 64.5
2019-07-25 16:30 | 98.37 | 66.85
2019-07-25 17:00 | 102.39 | 75.61
2019-07-25 17:30 | 108.24 | 85.99
2019-07-25 18:00 | 110.52 | 90.84
2019-07-25 18:30 | 105.58 | 83.61
2019-07-25 19:00 | 111.4 | 91.04
2019-07-25 19:30 | 113.8 | 95.05
2019-07-25 20:00 | 118.06 | 100.96
2019-07-25 20:30 | 113.79 | 93.85
2019-07-25 21:00 | 112.88 | 92.05
2019-07-25 21:30 | 110.27 | 88.56
2019-07-25 22:00 | 111.96 | 89.81
2019-07-25 22:30 | 114.61 | 92.2
2019-07-25 23:00 | 107.11 | 82.92
2019-07-25 23:30 | 113.97 | 91.91
2019-07-26 | 108.76 | 83.51
2019-07-26 00:30 | 108.03 | 85.54
2019-07-26 01:00 | 110.23 | 88
2019-07-26 01:30 | 116.93 | 95.27
2019-07-26 02:00 | 122.15 | 104.03
2019-07-26 02:30 | 121 | 101.54
2019-07-26 03:00 | 118.34 | 98.39
2019-07-26 03:30 | 112.71 | 91.71
2019-07-26 04:00 | 115.32 | 95.42
2019-07-26 04:30 | 114.89 | 93.69
2019-07-26 05:00 | 115.36 | 94.9
2019-07-26 05:30 | 111.7 | 90.69
2019-07-26 06:00 | 108.19 | 86.7
2019-07-26 06:30 | 102.58 | 81.84
2019-07-26 07:00 | 105.33 | 83.77
2019-07-26 07:30 | 106.16 | 86.25
2019-07-26 08:00 | 105.11 | 82
2019-07-26 08:30 | 101.26 | 72.37
2019-07-26 09:00 | 98.37 | 68.4
2019-07-26 09:30 | 97.26 | 66.36
2019-07-26 10:00 | 94.64 | 60.25
2019-07-26 10:30 | 95.71 | 59.17
2019-07-26 11:00 | 96.97 | 59.6
2019-07-26 11:30 | 98.09 | 63.55
2019-07-26 12:00 | 101.59 | 72.07
2019-07-26 12:30 | 97.68 | 71.38
2019-07-26 13:00 | 96.62 | 64.72
2019-07-26 13:30 | 99.53 | 74.9
2019-07-26 14:00 | 100.85 | 80.32
2019-07-26 14:30 | 107.14 | 85.48
2019-07-26 15:00 | 109.99 | 82.19
2019-07-26 15:30 | 106.89 | 78.73
2019-07-26 16:00 | 114.95 | 95.77
2019-07-26 16:30 | 115.47 | 98.21
2019-07-26 17:00 | 105.33 | 82.06
2019-07-26 17:30 | 112.56 | 93.61
2019-07-26 18:00 | 117.96 | 98.56
2019-07-26 18:30 | 108.41 | 89.05
2019-07-26 19:00 | 112.29 | 94.07
2019-07-26 19:30 | 114.62 | 96.56
2019-07-26 20:00 | 113.67 | 96.99
2019-07-26 20:30 | 115.52 | 96.96
2019-07-26 21:00 | 112.19 | 93.76
2019-07-26 21:30 | 105.42 | 82.98
2019-07-26 22:00 | 117.03 | 98.5
2019-07-26 22:30 | 119.95 | 103.26
2019-07-26 23:00 | 112.7 | 94.44
2019-07-26 23:30 | 106.15 | 83.87
2019-07-27 | 110.88 | 89.72
2019-07-27 00:30 | 113.95 | 94.98
2019-07-27 01:00 | 113.73 | 95.49
2019-07-27 01:30 | 114.73 | 94.48
2019-07-27 02:00 | 115.33 | 96.94
2019-07-27 02:30 | 111.45 | 91.65
2019-07-27 03:00 | 113.36 | 93.22
2019-07-27 03:30 | 112.68 | 92.49
2019-07-27 04:00 | 111.74 | 91.39
2019-07-27 04:30 | 112.6 | 92.69
2019-07-27 05:00 | 116.86 | 99.02
2019-07-27 05:30 | 109.21 | 89.78
2019-07-27 06:00 | 112.97 | 93.67
2019-07-27 06:30 | 111.17 | 92.4
2019-07-27 07:00 | 120.18 | 103.82
2019-07-27 07:30 | 116.02 | 98.02
2019-07-27 08:00 | 111.32 | 91.03
2019-07-27 08:30 | 109.27 | 85.37
2019-07-27 09:00 | 111.25 | 85.45
2019-07-27 09:30 | 109.06 | 83.94
2019-07-27 10:00 | 101.4 | 70.62
2019-07-27 10:30 | 99.83 | 69.36
2019-07-27 11:00 | 101.13 | 71.53
2019-07-27 11:30 | 100.65 | 68.71
2019-07-27 12:00 | 102.87 | 74.82
2019-07-27 12:30 | 102.35 | 74.56
2019-07-27 13:00 | 100.93 | 67.67
2019-07-27 13:30 | 103.08 | 75.31
2019-07-27 14:00 | 101.66 | 71.84
2019-07-27 14:30 | 103.93 | 76.45
2019-07-27 15:00 | 104.64 | 76.71
2019-07-27 15:30 | 101.45 | 71.02
2019-07-27 16:00 | 104.11 | 74.75
2019-07-27 16:30 | 103.3 | 76
2019-07-27 17:00 | 111.17 | 90.03
2019-07-27 17:30 | 110.6 | 92.96
2019-07-27 18:00 | 113.58 | 97.43
2019-07-27 18:30 | 111.93 | 95.61
2019-07-27 19:00 | 122.55 | 108.63
2019-07-27 19:30 | 120.15 | 105.38
2019-07-27 20:00 | 124.53 | 110.29
2019-07-27 20:30 | 118.38 | 102.92
2019-07-27 21:00 | 116.78 | 100.84
2019-07-27 21:30 | 116.94 | 101.35
2019-07-27 22:00 | 110.81 | 93.22
2019-07-27 22:30 | 112.48 | 95.31
2019-07-27 23:00 | 108.58 | 90.86
2019-07-27 23:30 | 106.22 | 87.41
2019-07-28 | 110.17 | 92.51
2019-07-28 00:30 | 110.77 | 92.48
2019-07-28 01:00 | 106.61 | 87.01
2019-07-28 01:30 | 105.79 | 87.69
2019-07-28 02:00 | 104.41 | 84.79
2019-07-28 02:30 | 103 | 84.38
2019-07-28 03:00 | 104.09 | 85.82
2019-07-28 03:30 | 100.32 | 80.69
2019-07-28 04:00 | 110.39 | 93.96
2019-07-28 04:30 | 109.36 | 91.81
2019-07-28 05:00 | 109.6 | 92.83
2019-07-28 05:30 | 105.19 | 86.38
2019-07-28 06:00 | 104.14 | 84.96
2019-07-28 06:30 | 103.57 | 84.77
2019-07-28 07:00 | 106.46 | 87.19
2019-07-28 07:30 | 105.79 | 89.37
2019-07-28 08:00 | 100.38 | 79.53
2019-07-28 08:30 | 92.75 | 63.99
2019-07-28 09:00 | 94.79 | 66.65
2019-07-28 09:30 | 97.35 | 66.7
2019-07-28 10:00 | 102.22 | 75.05
2019-07-28 10:30 | 102.56 | 73.05
2019-07-28 11:00 | 101.94 | 70.75
2019-07-28 11:30 | 95.86 | 61.6
2019-07-28 12:00 | 96.86 | 63.54
2019-07-28 12:30 | 98.11 | 66.55
2019-07-28 13:00 | 95.77 | 61.64
2019-07-28 13:30 | 95.53 | 61.35
2019-07-28 14:00 | 97.3 | 65.65
2019-07-28 14:30 | 96.71 | 64.79
2019-07-28 15:00 | 97.05 | 63.37
2019-07-28 15:30 | 100.55 | 70.49
2019-07-28 16:00 | 103.34 | 75.35
2019-07-28 16:30 | 97.38 | 70.55
2019-07-28 17:00 | 103.68 | 83.25
2019-07-28 17:30 | 103.8 | 84.9
2019-07-28 18:00 | 105.55 | 87.6
2019-07-28 18:30 | 107.15 | 90.57
2019-07-28 19:00 | 111.96 | 95.46
2019-07-28 19:30 | 113 | 96.89
2019-07-28 20:00 | 114.1 | 98.02
2019-07-28 20:30 | 109.22 | 91.73
2019-07-28 21:00 | 105.42 | 87.16
2019-07-28 21:30 | 103.97 | 83.85
2019-07-28 22:00 | 107.67 | 90.24
2019-07-28 22:30 | 116.42 | 99.55
2019-07-28 23:00 | 110.54 | 91.02
2019-07-28 23:30 | 110.5 | 92.82
2019-07-29 | 112.88 | 93.72
2019-07-29 00:30 | 116.16 | 98.93
2019-07-29 01:00 | 114.72 | 96.64
2019-07-29 01:30 | 115.22 | 96.8
2019-07-29 02:00 | 113.41 | 93.66
2019-07-29 02:30 | 111.23 | 91.52
2019-07-29 03:00 | 110.81 | 91.32
2019-07-29 03:30 | 108.58 | 88.52
2019-07-29 04:00 | 109.25 | 89.72
2019-07-29 04:30 | 111.32 | 93.14
2019-07-29 05:00 | 109.15 | 91.66
2019-07-29 05:30 | 103.6 | 84.46
2019-07-29 06:00 | 95.89 | 71.94
2019-07-29 06:30 | 94.12 | 68.8
2019-07-29 07:00 | 98.91 | 76.48
2019-07-29 07:30 | 96.27 | 75.01
2019-07-29 08:00 | 95.77 | 70.59
2019-07-29 08:30 | 88.31 | 56.5
2019-07-29 09:00 | 87.35 | 53.91
2019-07-29 09:30 | 90.09 | 56.34
2019-07-29 10:00 | 91.41 | 57.01
2019-07-29 10:30 | 89.78 | 56.61
2019-07-29 11:00 | 90.81 | 59.23
2019-07-29 11:30 | 87.36 | 56.71
2019-07-29 12:00 | 87.97 | 55.29
2019-07-29 12:30 | 87.83 | 52.94
2019-07-29 13:00 | 84.66 | 50.54
2019-07-29 13:30 | 84.76 | 48.27
2019-07-29 14:00 | 87.66 | 52.6
2019-07-29 14:30 | 85.33 | 47.81
2019-07-29 15:00 | 84.6 | 46.85
2019-07-29 15:30 | 88.04 | 53.68
2019-07-29 16:00 | 94.55 | 66.75
2019-07-29 16:30 | 98.28 | 72.53
2019-07-29 17:00 | 98.24 | 76.85
2019-07-29 17:30 | 99.58 | 81.06
2019-07-29 18:00 | 106.17 | 89.67
2019-07-29 18:30 | 112.22 | 95.48
2019-07-29 19:00 | 112.64 | 95.04
2019-07-29 19:30 | 108.6 | 91.92
2019-07-29 20:00 | 111.05 | 92.73
2019-07-29 20:30 | 116.01 | 98.77
2019-07-29 21:00 | 112.5 | 94.9
2019-07-29 21:30 | 108.69 | 89.2
2019-07-29 22:00 | 105.84 | 86.32
2019-07-29 22:30 | 110.99 | 90.83
2019-07-29 23:00 | 109.84 | 89.27
2019-07-29 23:30 | 105.78 | 85.25
2019-07-30 | 106.57 | 85.33
2019-07-30 00:30 | 107.2 | 86.6
2019-07-30 01:00 | 106.81 | 86.54
2019-07-30 01:30 | 108.05 | 88.67
2019-07-30 02:00 | 104.74 | 84.61
2019-07-30 02:30 | 111.35 | 92.29
2019-07-30 03:00 | 112.15 | 92.01
2019-07-30 03:30 | 113.03 | 93.37
2019-07-30 04:00 | 109.08 | 88.61
2019-07-30 04:30 | 112.91 | 94.58
2019-07-30 05:00 | 110.03 | 90.9
2019-07-30 05:30 | 113.59 | 98.25
2019-07-30 06:00 | 110.42 | 92.28
2019-07-30 06:30 | 106.79 | 87.65
2019-07-30 07:00 | 112.18 | 94.47
2019-07-30 07:30 | 110.85 | 92.58
2019-07-30 08:00 | 97.37 | 74.35
2019-07-30 08:30 | 93.74 | 68.32
2019-07-30 09:00 | 87.08 | 57.33
2019-07-30 09:30 | 82.83 | 45.37
2019-07-30 10:00 | 85.67 | 50.94
2019-07-30 10:30 | 86.26 | 47.28
2019-07-30 11:00 | 86.96 | 50.88
2019-07-30 11:30 | 90.78 | 56.4
2019-07-30 12:00 | 93.35 | 54.19
2019-07-30 12:30 | 94.73 | 53.53
2019-07-30 13:00 | 94.25 | 51.31
2019-07-30 13:30 | 92.92 | 49.63
2019-07-30 14:00 | 94.41 | 51.98
2019-07-30 14:30 | 97.07 | 59.25
2019-07-30 15:00 | 97.21 | 56.65
2019-07-30 15:30 | 97.67 | 58.46
2019-07-30 16:00 | 94.15 | 56
2019-07-30 16:30 | 98.1 | 63.09
2019-07-30 17:00 | 103.72 | 76.42
2019-07-30 17:30 | 103.52 | 78.07
2019-07-30 18:00 | 104.45 | 82.27
2019-07-30 18:30 | 105.94 | 86.07
2019-07-30 19:00 | 110.91 | 90.01
2019-07-30 19:30 | 113.46 | 93.91
2019-07-30 20:00 | 111.14 | 89.97
2019-07-30 20:30 | 109.34 | 86.47
2019-07-30 21:00 | 112.84 | 90.43
2019-07-30 21:30 | 117.42 | 95.94
2019-07-30 22:00 | 117.71 | 95.99
2019-07-30 22:30 | 117.26 | 96.51
2019-07-30 23:00 | 112.46 | 89.63
2019-07-30 23:30 | 112.3 | 90.17
2019-07-31 | 116.2 | 94.49
2019-07-31 00:30 | 113.24 | 90.8
2019-07-31 01:00 | 109.79 | 84.88
2019-07-31 01:30 | 106.55 | 82.15
2019-07-31 02:00 | 111.15 | 88.34
2019-07-31 02:30 | 109.53 | 84.76
2019-07-31 03:00 | 109.07 | 84.58
2019-07-31 03:30 | 110.3 | 85.28
2019-07-31 04:00 | 106.29 | 79.38
2019-07-31 04:30 | 108.28 | 82.85
2019-07-31 05:00 | 115.19 | 93.39
2019-07-31 05:30 | 114.88 | 93.51
2019-07-31 06:00 | 110.93 | 86.97
2019-07-31 06:30 | 107.36 | 82.22
2019-07-31 07:00 | 101.77 | 77.31
2019-07-31 07:30 | 102.08 | 77.89
2019-07-31 08:00 | 105.67 | 78.1
2019-07-31 08:30 | 104.31 | 70.8
2019-07-31 09:00 | 98.69 | 66.87
2019-07-31 09:30 | 96.91 | 56.62
2019-07-31 10:00 | 98.65 | 60.86
2019-07-31 10:30 | 97.56 | 56.7
2019-07-31 11:00 | 97.07 | 56.62
2019-07-31 11:30 | 96.53 | 55.4
2019-07-31 12:00 | 91.85 | 46.03
2019-07-31 12:30 | 89.27 | 37.98
2019-07-31 13:00 | 94.02 | 47.74
2019-07-31 13:30 | 97.27 | 60.62
2019-07-31 14:00 | 97.29 | 56.56
2019-07-31 14:30 | 96.79 | 58.72
2019-07-31 15:00 | 95.82 | 54.6
2019-07-31 15:30 | 102.14 | 66.7
2019-07-31 16:00 | 101.85 | 68.74
2019-07-31 16:30 | 100.34 | 65.08
2019-07-31 17:00 | 103.34 | 75.36
2019-07-31 17:30 | 105.19 | 81.11
2019-07-31 18:00 | 108.47 | 84.14
2019-07-31 18:30 | 110.91 | 86.59
2019-07-31 19:00 | 115.35 | 93.91
2019-07-31 19:30 | 118.09 | 97.34
2019-07-31 20:00 | 121.03 | 98.72
2019-07-31 20:30 | 122.42 | 99.45
2019-07-31 21:00 | 118.12 | 92.82
2019-07-31 21:30 | 115.22 | 88.94
2019-07-31 22:00 | 116.68 | 90
2019-07-31 22:30 | 120.46 | 94.3
2019-07-31 23:00 | 122.43 | 97.4
2019-07-31 23:30 | 112.79 | 88.2
2019-08-01 | 114.65 | 89.69
2019-08-01 00:30 | 115.3 | 88.54
2019-08-01 01:00 | 116.38 | 89.87
2019-08-01 01:30 | 114.9 | 90.34
2019-08-01 02:00 | 116.76 | 91.06
2019-08-01 02:30 | 117.75 | 92.82
2019-08-01 03:00 | 119.45 | 93.19
2019-08-01 03:30 | 117.36 | 91.15
2019-08-01 04:00 | 118.05 | 93.29
2019-08-01 04:30 | 112 | 86.13
2019-08-01 05:00 | 109.54 | 82.47
2019-08-01 05:30 | 113.85 | 89.09
2019-08-01 06:00 | 106.15 | 78
2019-08-01 06:30 | 106.26 | 79.29
2019-08-01 07:00 | 108.69 | 80.54
2019-08-01 07:30 | 111.34 | 84.14
2019-08-01 08:00 | 111.85 | 85.82
2019-08-01 08:30 | 108.54 | 88.81
2019-08-01 09:00 | 110.31 | 90.7
2019-08-01 09:30 | 115.18 | 95.51
2019-08-01 10:00 | 111.08 | 88.45
2019-08-01 10:30 | 111.11 | 87.06
2019-08-01 11:00 | 113.21 | 90.5
2019-08-01 11:30 | 110.25 | 85.38
2019-08-01 12:00 | 111.93 | 88.09
2019-08-01 12:30 | 112.97 | 89.42
2019-08-01 13:00 | 108.07 | 80.85
2019-08-01 13:30 | 113.47 | 88.96
2019-08-01 14:00 | 115.1 | 91.18
2019-08-01 14:30 | 113.04 | 90.26
2019-08-01 15:00 | 112.23 | 88.74
2019-08-01 15:30 | 109.93 | 87.4
2019-08-01 16:00 | 116 | 94.33
2019-08-01 16:30 | 118.6 | 99.97
2019-08-01 17:00 | 112.86 | 91.08
2019-08-01 17:30 | 120.25 | 101.71
2019-08-01 18:00 | 114.86 | 92.65
2019-08-01 18:30 | 125.05 | 108.39
2019-08-01 19:00 | 118.4 | 100.37
2019-08-01 19:30 | 124.89 | 108.05
2019-08-01 20:00 | 117.3 | 99.25
2019-08-01 20:30 | 114.51 | 94.84
2019-08-01 21:00 | 113.41 | 93.18
2019-08-01 21:30 | 113.36 | 92.1
2019-08-01 22:00 | 114.06 | 92.43
2019-08-01 22:30 | 116.83 | 95.82
2019-08-01 23:00 | 113.89 | 89.58
2019-08-01 23:30 | 118.19 | 96.86
2019-08-02 | 121.27 | 99.69
2019-08-02 00:30 | 122.34 | 101.98
2019-08-02 01:00 | 120.9 | 100.31
2019-08-02 01:30 | 120.25 | 98.68
2019-08-02 02:00 | 120.83 | 100.32
2019-08-02 02:30 | 121.98 | 101.36
2019-08-02 03:00 | 120.78 | 100.56
2019-08-02 03:30 | 116.35 | 94.37
2019-08-02 04:00 | 118.24 | 97.59
2019-08-02 04:30 | 120.53 | 99.42
2019-08-02 05:00 | 122.67 | 103.3
2019-08-02 05:30 | 120.75 | 100.07
2019-08-02 06:00 | 110.39 | 86.09
2019-08-02 06:30 | 103.13 | 76.74
2019-08-02 07:00 | 105.62 | 82.73
2019-08-02 07:30 | 99.19 | 73.69
2019-08-02 08:00 | 99.93 | 71.32
2019-08-02 08:30 | 96.9 | 61.89
2019-08-02 09:00 | 99.67 | 67.57
2019-08-02 09:30 | 101.65 | 66.19
2019-08-02 10:00 | 98.13 | 57.24
2019-08-02 10:30 | 98.74 | 60.93
2019-08-02 11:00 | 96.44 | 57.34
2019-08-02 11:30 | 101.55 | 67.33
2019-08-02 12:00 | 97.89 | 61.79
2019-08-02 12:30 | 99.93 | 60.46
2019-08-02 13:00 | 104.69 | 70.27
2019-08-02 13:30 | 104.98 | 70.15
2019-08-02 14:00 | 106.13 | 74.71
2019-08-02 14:30 | 107.49 | 77.77
2019-08-02 15:00 | 102.08 | 71.99
2019-08-02 15:30 | 101.21 | 67.93
2019-08-02 16:00 | 105.02 | 74.48
2019-08-02 16:30 | 108.67 | 83.32
2019-08-02 17:00 | 114.07 | 92.2
2019-08-02 17:30 | 113.83 | 93.07
2019-08-02 18:00 | 112.17 | 88.6
2019-08-02 18:30 | 115.19 | 93.57
2019-08-02 19:00 | 116.97 | 93.92
2019-08-02 19:30 | 116.79 | 93.84
2019-08-02 20:00 | 117.31 | 96.59
2019-08-02 20:30 | 117.75 | 98.43
2019-08-02 21:00 | 116.07 | 94.61
2019-08-02 21:30 | 116.81 | 95.41
2019-08-02 22:00 | 113.79 | 89.83
2019-08-02 22:30 | 119.85 | 98.22
2019-08-02 23:00 | 114.96 | 89.78
2019-08-02 23:30 | 118.45 | 95.26
2019-08-03 | 118.16 | 95.41
2019-08-03 00:30 | 115.2 | 90.26
2019-08-03 01:00 | 116.82 | 92.6
2019-08-03 01:30 | 113.3 | 86.41
2019-08-03 02:00 | 111.96 | 84.34
2019-08-03 02:30 | 112.78 | 86.34
2019-08-03 03:00 | 111.04 | 84.63
2019-08-03 03:30 | 109.9 | 83.33
2019-08-03 04:00 | 114.89 | 90.24
2019-08-03 04:30 | 111.05 | 83.4
2019-08-03 05:00 | 107.83 | 79.03
2019-08-03 05:30 | 116.65 | 92.24
2019-08-03 06:00 | 108.26 | 79.85
2019-08-03 06:30 | 110.79 | 85.29
2019-08-03 07:00 | 112.38 | 88.13
2019-08-03 07:30 | 106.93 | 83.55
2019-08-03 08:00 | 103.95 | 76.05
2019-08-03 08:30 | 101.33 | 69.4
2019-08-03 09:00 | 104.17 | 73.56
2019-08-03 09:30 | 102.35 | 69.51
2019-08-03 10:00 | 98.7 | 61.52
2019-08-03 10:30 | 99.64 | 61.44
2019-08-03 11:00 | 99.5 | 64.46
2019-08-03 11:30 | 97.69 | 59.9
2019-08-03 12:00 | 93.86 | 53.27
2019-08-03 12:30 | 96.2 | 57.64
2019-08-03 13:00 | 99.64 | 62.35
2019-08-03 13:30 | 100.84 | 64.83
2019-08-03 14:00 | 101.49 | 69.07
2019-08-03 14:30 | 100.66 | 65.69
2019-08-03 15:00 | 103.83 | 72.95
2019-08-03 15:30 | 103.09 | 71.47
2019-08-03 16:00 | 99.79 | 64.21
2019-08-03 16:30 | 102.27 | 70.71
2019-08-03 17:00 | 106.76 | 82.36
2019-08-03 17:30 | 106.5 | 85.21
2019-08-03 18:00 | 111.07 | 88.83
2019-08-03 18:30 | 112.64 | 89.37
2019-08-03 19:00 | 114.57 | 93.15
2019-08-03 19:30 | 111.05 | 86.59
2019-08-03 20:00 | 115.9 | 94.16
2019-08-03 20:30 | 117.19 | 95.98
2019-08-03 21:00 | 116.84 | 93.41
2019-08-03 21:30 | 117.87 | 95.75
2019-08-03 22:00 | 119.76 | 97.02
2019-08-03 22:30 | 114.89 | 90.18
2019-08-03 23:00 | 120.5 | 97.53
2019-08-03 23:30 | 117.11 | 91.98
2019-08-04 | 117.22 | 91.84
2019-08-04 00:30 | 117.76 | 91.4
2019-08-04 01:00 | 115.76 | 89.34
2019-08-04 01:30 | 117.17 | 91.33
2019-08-04 02:00 | 113.79 | 86.34
2019-08-04 02:30 | 114.99 | 89.17
2019-08-04 03:00 | 114.09 | 88.15
2019-08-04 03:30 | 106.4 | 77.47
2019-08-04 04:00 | 109.33 | 83.31
2019-08-04 04:30 | 108.11 | 81.01
2019-08-04 05:00 | 108.24 | 79.27
2019-08-04 05:30 | 112.7 | 85.03
2019-08-04 06:00 | 107.68 | 76.55
2019-08-04 06:30 | 103.14 | 70.84
2019-08-04 07:00 | 107.15 | 78.42
2019-08-04 07:30 | 106.14 | 81.51
2019-08-04 08:00 | 105.4 | 74.21
2019-08-04 08:30 | 100.23 | 64.48
2019-08-04 09:00 | 100.02 | 60.68
2019-08-04 09:30 | 100.02 | 56.79
2019-08-04 10:00 | 96.37 | 50.6
2019-08-04 10:30 | 97.08 | 52.49
2019-08-04 11:00 | 100.3 | 53.43
2019-08-04 11:30 | 97.43 | 50.1
2019-08-04 12:00 | 99.46 | 52.11
2019-08-04 12:30 | 99.86 | 51.99
2019-08-04 13:00 | 98.98 | 56.4
2019-08-04 13:30 | 101.03 | 59.93
2019-08-04 14:00 | 94.74 | 53.03
2019-08-04 14:30 | 99.68 | 56.78
2019-08-04 15:00 | 99.25 | 55.37
2019-08-04 15:30 | 100.61 | 62.17
2019-08-04 16:00 | 102.32 | 66.3
2019-08-04 16:30 | 110.65 | 86.59
2019-08-04 17:00 | 115.95 | 93.59
2019-08-04 17:30 | 116.44 | 95.74
2019-08-04 18:00 | 111.84 | 86.95
2019-08-04 18:30 | 106.69 | 77.85
2019-08-04 19:00 | 110.35 | 84.76
2019-08-04 19:30 | 107.54 | 78.98
2019-08-04 20:00 | 111.04 | 85.55
2019-08-04 20:30 | 112.77 | 87.08
2019-08-04 21:00 | 110.51 | 82.66
2019-08-04 21:30 | 114.42 | 88.61
2019-08-04 22:00 | 114.4 | 88.1
2019-08-04 22:30 | 119.22 | 95.48
2019-08-04 23:00 | 120.3 | 94.84
2019-08-04 23:30 | 120.46 | 93.49
2019-08-05 | 122.88 | 96.92
2019-08-05 00:30 | 115.53 | 85.65
2019-08-05 01:00 | 114.84 | 83.4
2019-08-05 01:30 | 115.48 | 86.63
2019-08-05 02:00 | 118.97 | 92.85
2019-08-05 02:30 | 118.56 | 92.6
2019-08-05 03:00 | 116.43 | 88.49
2019-08-05 03:30 | 113.45 | 83.57
2019-08-05 04:00 | 111.09 | 82.26
2019-08-05 04:30 | 106.41 | 79.31
2019-08-05 05:00 | 107.6 | 82.34
2019-08-05 05:30 | 105.83 | 77.59
2019-08-05 06:00 | 105.39 | 78.36
2019-08-05 06:30 | 104.93 | 78.89
2019-08-05 07:00 | 102.5 | 73.9
2019-08-05 07:30 | 98.39 | 69.7
2019-08-05 08:00 | 100.73 | 70.7
2019-08-05 08:30 | 103.22 | 72.79
2019-08-05 09:00 | 100.33 | 69.3
2019-08-05 09:30 | 98.88 | 64.7
2019-08-05 10:00 | 94.83 | 57.98
2019-08-05 10:30 | 94.51 | 55.45
2019-08-05 11:00 | 95.14 | 54.63
2019-08-05 11:30 | 92.94 | 55.55
2019-08-05 12:00 | 92.72 | 57.33
2019-08-05 12:30 | 99.88 | 67.64
2019-08-05 13:00 | 102.88 | 71.82
2019-08-05 13:30 | 105.75 | 75.74
2019-08-05 14:00 | 106.29 | 79.54
2019-08-05 14:30 | 106.84 | 79.68
2019-08-05 15:00 | 104.37 | 78.18
2019-08-05 15:30 | 100.08 | 64.55
2019-08-05 16:00 | 104.03 | 75.59
2019-08-05 16:30 | 102.6 | 71.43
2019-08-05 17:00 | 109.78 | 83.66
2019-08-05 17:30 | 108.01 | 85.29
2019-08-05 18:00 | 107.35 | 84.04
2019-08-05 18:30 | 107.91 | 85.54
2019-08-05 19:00 | 115.94 | 95.11
2019-08-05 19:30 | 116.14 | 93.01
2019-08-05 20:00 | 118.39 | 96.77
2019-08-05 20:30 | 114.62 | 93.37
2019-08-05 21:00 | 116.16 | 94.45
2019-08-05 21:30 | 118.64 | 94.88
2019-08-05 22:00 | 114.83 | 89.14
2019-08-05 22:30 | 119.76 | 95.5
2019-08-05 23:00 | 117.45 | 92.21
2019-08-05 23:30 | 120.06 | 96.42
2019-08-06 | 119.13 | 94.89
2019-08-06 00:30 | 124.46 | 100.88
2019-08-06 01:00 | 124.48 | 101.49
2019-08-06 01:30 | 122.05 | 97.85
2019-08-06 02:00 | 121.52 | 96.8
2019-08-06 02:30 | 115.68 | 89.09
2019-08-06 03:00 | 122.09 | 99.93
2019-08-06 03:30 | 118.91 | 95.12
2019-08-06 04:00 | 118.3 | 95.26
2019-08-06 04:30 | 114.79 | 90.1
2019-08-06 05:00 | 116.84 | 94.24
2019-08-06 05:30 | 115.73 | 92.31
2019-08-06 06:00 | 117.14 | 93.95
2019-08-06 06:30 | 115.31 | 92.05
2019-08-06 07:00 | 115.61 | 91.76
2019-08-06 07:30 | 106.75 | 82.4
2019-08-06 08:00 | 106.5 | 80.31
2019-08-06 08:30 | 106.73 | 76.63
2019-08-06 09:00 | 104.74 | 73.64
2019-08-06 09:30 | 101.24 | 64.88
2019-08-06 10:00 | 105.04 | 70.55
2019-08-06 10:30 | 104.4 | 68.86
2019-08-06 11:00 | 103.15 | 66.59
2019-08-06 11:30 | 102.51 | 69.31
2019-08-06 12:00 | 103.59 | 70.45
2019-08-06 12:30 | 99.02 | 67.96
2019-08-06 13:00 | 100.28 | 74.05
2019-08-06 13:30 | 105.5 | 76.75
2019-08-06 14:00 | 106.69 | 78.65
2019-08-06 14:30 | 106.36 | 78.02
2019-08-06 15:00 | 107.28 | 80.77
2019-08-06 15:30 | 110.71 | 86.56
2019-08-06 16:00 | 105.42 | 76.44
2019-08-06 16:30 | 113.13 | 91.43
2019-08-06 17:00 | 116.05 | 95.46
2019-08-06 17:30 | 101.71 | 77.02
2019-08-06 18:00 | 107.17 | 83.73
2019-08-06 18:30 | 106.12 | 83.29
2019-08-06 19:00 | 109.68 | 86.33
2019-08-06 19:30 | 113.89 | 93.34
2019-08-06 20:00 | 114.59 | 95.42
2019-08-06 20:30 | 121.22 | 103.45
2019-08-06 21:00 | 122.64 | 104.95
2019-08-06 21:30 | 118.01 | 97.09
2019-08-06 22:00 | 112.24 | 87.93
2019-08-06 22:30 | 116.82 | 94.56
2019-08-06 23:00 | 115.15 | 90.99
2019-08-06 23:30 | 112.11 | 87.84
2019-08-07 | 119.79 | 96.91
2019-08-07 00:30 | 112.52 | 87.66
2019-08-07 01:00 | 113.16 | 91.31
2019-08-07 01:30 | 119.79 | 100.47
2019-08-07 02:00 | 113.18 | 90.57
2019-08-07 02:30 | 112.9 | 91.2
2019-08-07 03:00 | 116.17 | 95.18
2019-08-07 03:30 | 110.95 | 88.06
2019-08-07 04:00 | 114.63 | 92.33
2019-08-07 04:30 | 119.61 | 97.61
2019-08-07 05:00 | 124.93 | 105.44
2019-08-07 05:30 | 116.59 | 93.81
2019-08-07 06:00 | 116.47 | 93.63
2019-08-07 06:30 | 116.28 | 95.96
2019-08-07 07:00 | 111.81 | 87.74
2019-08-07 07:30 | 112.04 | 90.84
2019-08-07 08:00 | 108.63 | 87.37
2019-08-07 08:30 | 106.39 | 82.49
2019-08-07 09:00 | 100.37 | 71.56
2019-08-07 09:30 | 102.35 | 71.95
2019-08-07 10:00 | 100.25 | 70.42
2019-08-07 10:30 | 100.24 | 68.04
2019-08-07 11:00 | 103.53 | 72.5
2019-08-07 11:30 | 95.99 | 57.71
2019-08-07 12:00 | 99.53 | 61.88
2019-08-07 12:30 | 97.62 | 60.09
2019-08-07 13:00 | 97.97 | 58.42
2019-08-07 13:30 | 100.79 | 62.43
2019-08-07 14:00 | 103.28 | 68.38
2019-08-07 14:30 | 104.37 | 67.45
2019-08-07 15:00 | 101.51 | 64.25
2019-08-07 15:30 | 101.96 | 70.77
2019-08-07 16:00 | 99.24 | 65.64
2019-08-07 16:30 | 108.09 | 83.87
2019-08-07 17:00 | 108.35 | 86.04
2019-08-07 17:30 | 107.7 | 85.52
2019-08-07 18:00 | 112.23 | 90.15
2019-08-07 18:30 | 115.4 | 95.33
2019-08-07 19:00 | 117.89 | 100.32
2019-08-07 19:30 | 118.67 | 98.95
2019-08-07 20:00 | 121.84 | 103.68
2019-08-07 20:30 | 124.09 | 105.33
2019-08-07 21:00 | 126.52 | 106.94
2019-08-07 21:30 | 125.09 | 105.79
2019-08-07 22:00 | 128.56 | 111.3
2019-08-07 22:30 | 123.47 | 103.71
2019-08-07 23:00 | 124.05 | 101.94
2019-08-07 23:30 | 119.34 | 95.37
2019-08-08 | 120.03 | 97.63
2019-08-08 00:30 | 117.37 | 95.17
2019-08-08 01:00 | 116.65 | 93.09
2019-08-08 01:30 | 116.54 | 92.46
2019-08-08 02:00 | 113.67 | 88.89
2019-08-08 02:30 | 116.74 | 91.72
2019-08-08 03:00 | 116.65 | 90.75
2019-08-08 03:30 | 114.84 | 87.86
2019-08-08 04:00 | 111.79 | 83.4
2019-08-08 04:30 | 111.6 | 85.07
2019-08-08 05:00 | 121.21 | 99
2019-08-08 05:30 | 118.37 | 94.11
2019-08-08 06:00 | 116.07 | 90.77
2019-08-08 06:30 | 113.65 | 88.65
2019-08-08 07:00 | 117.79 | 94.34
2019-08-08 07:30 | 116.31 | 94.26
2019-08-08 08:00 | 111.93 | 87.45
2019-08-08 08:30 | 105.56 | 76.16
2019-08-08 09:00 | 102.61 | 66.35
2019-08-08 09:30 | 105.67 | 71.65
2019-08-08 10:00 | 108.26 | 70.57
2019-08-08 10:30 | 107.41 | 66.64
2019-08-08 11:00 | 105.53 | 66.06
2019-08-08 11:30 | 105.65 | 65.69
2019-08-08 12:00 | 102.81 | 58.59
2019-08-08 12:30 | 103.97 | 60.9
2019-08-08 13:00 | 106.03 | 63.77
2019-08-08 13:30 | 101 | 60.4
2019-08-08 14:00 | 102.52 | 62.78
2019-08-08 14:30 | 104.74 | 67.22
2019-08-08 15:00 | 107.73 | 69.76
2019-08-08 15:30 | 104.23 | 64.62
2019-08-08 16:00 | 107.8 | 72.25
2019-08-08 16:30 | 109.41 | 75.41
2019-08-08 17:00 | 109.96 | 81.3
2019-08-08 17:30 | 111.58 | 89.02
2019-08-08 18:00 | 114.73 | 92.71
2019-08-08 18:30 | 116.33 | 94.74
2019-08-08 19:00 | 117.43 | 96.55
2019-08-08 19:30 | 118.29 | 97.23
2019-08-08 20:00 | 116.65 | 95.02
2019-08-08 20:30 | 121.36 | 101.67
2019-08-08 21:00 | 124.1 | 104.35
2019-08-08 21:30 | 115.44 | 93.33
2019-08-08 22:00 | 118.79 | 96.25
2019-08-08 22:30 | 122.12 | 100.5
2019-08-08 23:00 | 125.56 | 106.52
2019-08-08 23:30 | 117.28 | 95.42
2019-08-09 | 116.09 | 93.28
2019-08-09 00:30 | 125.49 | 104.17
2019-08-09 01:00 | 116.21 | 94.18
2019-08-09 01:30 | 115.88 | 94.36
2019-08-09 02:00 | 120.31 | 99.42
2019-08-09 02:30 | 120.16 | 99.02
2019-08-09 03:00 | 121.13 | 99.9
2019-08-09 03:30 | 112.97 | 89.61
2019-08-09 04:00 | 114.5 | 93.79
2019-08-09 04:30 | 117.7 | 97.54
2019-08-09 05:00 | 117.93 | 95.88
2019-08-09 05:30 | 119.05 | 97.48
2019-08-09 06:00 | 112.39 | 88.17
2019-08-09 06:30 | 108.83 | 83.7
2019-08-09 07:00 | 109.47 | 84.82
2019-08-09 07:30 | 106.94 | 81.89
2019-08-09 08:00 | 100.82 | 68.6
2019-08-09 08:30 | 99.46 | 64.46
2019-08-09 09:00 | 103.14 | 70.01
2019-08-09 09:30 | 97.77 | 58.67
2019-08-09 10:00 | 100.04 | 61.21
2019-08-09 10:30 | 100.95 | 64.04
2019-08-09 11:00 | 100.22 | 59.34
2019-08-09 11:30 | 95.9 | 50.07
2019-08-09 12:00 | 95.86 | 52.57
2019-08-09 12:30 | 98.64 | 59.16
2019-08-09 13:00 | 100.51 | 60.72
2019-08-09 13:30 | 101.44 | 65.03
2019-08-09 14:00 | 102.21 | 63.61
2019-08-09 14:30 | 107.73 | 72.78
2019-08-09 15:00 | 105.99 | 69.18
2019-08-09 15:30 | 103.46 | 63.93
2019-08-09 16:00 | 109.69 | 77.87
2019-08-09 16:30 | 106.64 | 74.71
2019-08-09 17:00 | 113.11 | 87.72
2019-08-09 17:30 | 116.72 | 94.9
2019-08-09 18:00 | 120.2 | 100.14
2019-08-09 18:30 | 117 | 95.47
2019-08-09 19:00 | 118.17 | 98.13
2019-08-09 19:30 | 117.26 | 96.39
2019-08-09 20:00 | 122.51 | 103.9
2019-08-09 20:30 | 122.26 | 102.66
2019-08-09 21:00 | 121.8 | 101.08
2019-08-09 21:30 | 126.42 | 106.45
2019-08-09 22:00 | 123.46 | 103.3
2019-08-09 22:30 | 119.79 | 98.9
2019-08-09 23:00 | 118.4 | 95.91
2019-08-09 23:30 | 121.75 | 99.92
2019-08-10 | 117.71 | 97.01
2019-08-10 00:30 | 115.32 | 91.17
2019-08-10 01:00 | 125.06 | 103.42
2019-08-10 01:30 | 121.85 | 100.17
2019-08-10 02:00 | 120.4 | 97.05
2019-08-10 02:30 | 123.08 | 101.7
2019-08-10 03:00 | 119.48 | 96.55
2019-08-10 03:30 | 112.04 | 85.45
2019-08-10 04:00 | 116.29 | 92.59
2019-08-10 04:30 | 112.52 | 87.63
2019-08-10 05:00 | 112.52 | 88.67
2019-08-10 05:30 | 108.71 | 83.45
2019-08-10 06:00 | 109.16 | 83.23
2019-08-10 06:30 | 108.85 | 83.79
2019-08-10 07:00 | 112.21 | 88.14
2019-08-10 07:30 | 107.18 | 82
2019-08-10 08:00 | 102.57 | 75.47
2019-08-10 08:30 | 97.13 | 67.14
2019-08-10 09:00 | 99.16 | 68.54
2019-08-10 09:30 | 98.94 | 69.76
2019-08-10 10:00 | 105.52 | 77.53
2019-08-10 10:30 | 102.35 | 74.01
2019-08-10 11:00 | 104.72 | 74.66
2019-08-10 11:30 | 97.36 | 61.91
2019-08-10 12:00 | 102.34 | 68.96
2019-08-10 12:30 | 100 | 66.83
2019-08-10 13:00 | 107 | 75.49
2019-08-10 13:30 | 97.48 | 59.9
2019-08-10 14:00 | 99.19 | 65.74
2019-08-10 14:30 | 103.58 | 70.32
2019-08-10 15:00 | 103.19 | 66.64
2019-08-10 15:30 | 102.28 | 68.72
2019-08-10 16:00 | 100.78 | 69.96
2019-08-10 16:30 | 104.47 | 75.61
2019-08-10 17:00 | 110.69 | 84.91
2019-08-10 17:30 | 111.81 | 90.49
2019-08-10 18:00 | 109.71 | 88.96
2019-08-10 18:30 | 115.64 | 96.49
2019-08-10 19:00 | 119.2 | 101.42
2019-08-10 19:30 | 122.07 | 103.67
2019-08-10 20:00 | 122.88 | 105.15
2019-08-10 20:30 | 117.23 | 99.13
2019-08-10 21:00 | 117.42 | 99.62
2019-08-10 21:30 | 116.49 | 97.16
2019-08-10 22:00 | 121.47 | 102.21
2019-08-10 22:30 | 122.05 | 103.22
2019-08-10 23:00 | 117.3 | 97.39
2019-08-10 23:30 | 118.5 | 97.79
2019-08-11 | 113.89 | 91.83
2019-08-11 00:30 | 114.25 | 91.06
2019-08-11 01:00 | 120.33 | 100.24
2019-08-11 01:30 | 113.45 | 91.13
2019-08-11 02:00 | 109.13 | 86.78
2019-08-11 02:30 | 114.71 | 94.59
2019-08-11 03:00 | 108.18 | 85.25
2019-08-11 03:30 | 108.05 | 84.73
2019-08-11 04:00 | 114.9 | 94.42
2019-08-11 04:30 | 116.76 | 96.88
2019-08-11 05:00 | 115.23 | 94.17
2019-08-11 05:30 | 117.98 | 97.92
2019-08-11 06:00 | 110.14 | 88.37
2019-08-11 06:30 | 107.14 | 86.09
2019-08-11 07:00 | 111.87 | 91.94
2019-08-11 07:30 | 109.76 | 90.22
2019-08-11 08:00 | 102.48 | 75.69
2019-08-11 08:30 | 103.26 | 72.08
2019-08-11 09:00 | 108.35 | 79.01
2019-08-11 09:30 | 106.56 | 75.89
2019-08-11 10:00 | 104.85 | 72.66
2019-08-11 10:30 | 101.01 | 69.03
2019-08-11 11:00 | 100.73 | 71.27
2019-08-11 11:30 | 101.06 | 66.12
2019-08-11 12:00 | 104.73 | 66.29
2019-08-11 12:30 | 107.75 | 73.2
2019-08-11 13:00 | 110.11 | 78.43
2019-08-11 13:30 | 105.51 | 71.85
2019-08-11 14:00 | 108.59 | 75.99
2019-08-11 14:30 | 113.71 | 83.77
2019-08-11 15:00 | 111.12 | 79.13
2019-08-11 15:30 | 106.85 | 74.93
2019-08-11 16:00 | 106.66 | 75.11
2019-08-11 16:30 | 112.33 | 84.94
2019-08-11 17:00 | 114.73 | 91.2
2019-08-11 17:30 | 116.57 | 97.13
2019-08-11 18:00 | 119.79 | 102.11
2019-08-11 18:30 | 116.54 | 99.39
2019-08-11 19:00 | 123.21 | 107.65
2019-08-11 19:30 | 113.96 | 97.12
2019-08-11 20:00 | 112.79 | 95.4
2019-08-11 20:30 | 113.58 | 96.6
2019-08-11 21:00 | 117.23 | 99.75
2019-08-11 21:30 | 127.31 | 111.66
2019-08-11 22:00 | 128.66 | 112.48
2019-08-11 22:30 | 127.14 | 109.74
2019-08-11 23:00 | 129.29 | 112.45
2019-08-11 23:30 | 122.13 | 103.86
2019-08-12 | 118.92 | 98.94
2019-08-12 00:30 | 116.8 | 96.34
2019-08-12 01:00 | 118.27 | 97.63
2019-08-12 01:30 | 125.03 | 106.42
2019-08-12 02:00 | 121.4 | 102.75
2019-08-12 02:30 | 124.2 | 106.68
2019-08-12 03:00 | 124.55 | 108.08
2019-08-12 03:30 | 121.59 | 104.46
2019-08-12 04:00 | 120.67 | 102.88
2019-08-12 04:30 | 118.61 | 98.73
2019-08-12 05:00 | 116.91 | 97.74
2019-08-12 05:30 | 114.95 | 98.22
2019-08-12 06:00 | 114.5 | 97.67
2019-08-12 06:30 | 110.59 | 92.42
2019-08-12 07:00 | 114.68 | 97.94
2019-08-12 07:30 | 111.03 | 92.58
2019-08-12 08:00 | 104.22 | 81.68
2019-08-12 08:30 | 98.1 | 69.66
2019-08-12 09:00 | 93.85 | 61.24
2019-08-12 09:30 | 96.64 | 66.61
2019-08-12 10:00 | 96.9 | 66.62
2019-08-12 10:30 | 100.15 | 68.27
2019-08-12 11:00 | 101.29 | 69.07
2019-08-12 11:30 | 99.82 | 66.61
2019-08-12 12:00 | 97.99 | 62.68
2019-08-12 12:30 | 99.35 | 66.63
2019-08-12 13:00 | 98.35 | 62.89
2019-08-12 13:30 | 102.02 | 69.35
2019-08-12 14:00 | 102.15 | 72.98
2019-08-12 14:30 | 104.87 | 75.96
2019-08-12 15:00 | 99.43 | 67.78
2019-08-12 15:30 | 99.93 | 68.11
2019-08-12 16:00 | 107.19 | 80.09
2019-08-12 16:30 | 108.61 | 83.09
2019-08-12 17:00 | 112.92 | 94.14
2019-08-12 17:30 | 114.01 | 97.84
2019-08-12 18:00 | 109.37 | 90.56
2019-08-12 18:30 | 113.53 | 95.12
2019-08-12 19:00 | 113.59 | 96.25
2019-08-12 19:30 | 116.19 | 100.08
2019-08-12 20:00 | 118.01 | 101.37
2019-08-12 20:30 | 123.48 | 107.89
2019-08-12 21:00 | 117.13 | 99.75
2019-08-12 21:30 | 112.9 | 95.83
2019-08-12 22:00 | 116.45 | 98.46
2019-08-12 22:30 | 121.12 | 104.89
2019-08-12 23:00 | 112.39 | 91.81
2019-08-12 23:30 | 111.9 | 91.31
2019-08-13 | 119.05 | 101.25
2019-08-13 00:30 | 115.98 | 96.72
2019-08-13 01:00 | 113.78 | 94.35
2019-08-13 01:30 | 112.78 | 94.03
2019-08-13 02:00 | 104.4 | 84.54
2019-08-13 02:30 | 109.99 | 91.4
2019-08-13 03:00 | 110.32 | 92.47
2019-08-13 03:30 | 108.81 | 89.4
2019-08-13 04:00 | 108.45 | 88.43
2019-08-13 04:30 | 111.14 | 92.21
2019-08-13 05:00 | 108.5 | 89.6
2019-08-13 05:30 | 110.36 | 92.03
2019-08-13 06:00 | 104.03 | 83.27
2019-08-13 06:30 | 113.16 | 98.05
2019-08-13 07:00 | 106.75 | 88.89
2019-08-13 07:30 | 102.35 | 81.84
2019-08-13 08:00 | 93.41 | 67.11
2019-08-13 08:30 | 91.11 | 61.29
2019-08-13 09:00 | 96.17 | 68.64
2019-08-13 09:30 | 94.34 | 63.88
2019-08-13 10:00 | 97.29 | 66.83
2019-08-13 10:30 | 97.71 | 68.18
2019-08-13 11:00 | 103.41 | 70.41
2019-08-13 11:30 | 103.63 | 70.79
2019-08-13 12:00 | 97.44 | 63.3
2019-08-13 12:30 | 102.5 | 68.76
2019-08-13 13:00 | 101.01 | 67.28
2019-08-13 13:30 | 97.62 | 61.66
2019-08-13 14:00 | 97.31 | 63.67
2019-08-13 14:30 | 98.7 | 66.32
2019-08-13 15:00 | 101.02 | 67.56
2019-08-13 15:30 | 95.98 | 60.82
2019-08-13 16:00 | 96.68 | 64.52
2019-08-13 16:30 | 98.34 | 64.74
2019-08-13 17:00 | 110.07 | 87.39
2019-08-13 17:30 | 116.31 | 99.16
2019-08-13 18:00 | 118.3 | 98.87
2019-08-13 18:30 | 117.54 | 96.17
2019-08-13 19:00 | 122.03 | 104.15
2019-08-13 19:30 | 123.61 | 104.84
2019-08-13 20:00 | 120.52 | 101.94
2019-08-13 20:30 | 123.36 | 105
2019-08-13 21:00 | 123.79 | 107.12
2019-08-13 21:30 | 118.49 | 98.62
2019-08-13 22:00 | 112.63 | 90.79
2019-08-13 22:30 | 119.9 | 99.28
2019-08-13 23:00 | 116.23 | 94.07
2019-08-13 23:30 | 115.74 | 93.23
2019-08-14 | 114.44 | 92.22
2019-08-14 00:30 | 113.69 | 90.41
2019-08-14 01:00 | 111.56 | 88.61
2019-08-14 01:30 | 114.84 | 93.5
2019-08-14 02:00 | 112.54 | 89.73
2019-08-14 02:30 | 116.39 | 94.71
2019-08-14 03:00 | 111.46 | 88.5
2019-08-14 03:30 | 101.75 | 75.15
2019-08-14 04:00 | 99.53 | 72.55
2019-08-14 04:30 | 98.4 | 72.11
2019-08-14 05:00 | 104.03 | 82.07
2019-08-14 05:30 | 108.22 | 87.95
2019-08-14 06:00 | 102.6 | 79.38
2019-08-14 06:30 | 104.35 | 80.93
2019-08-14 07:00 | 110.04 | 92.05
2019-08-14 07:30 | 104.1 | 83.9
2019-08-14 08:00 | 101.85 | 76.31
2019-08-14 08:30 | 98.8 | 67.76
2019-08-14 09:00 | 101.41 | 71.77
2019-08-14 09:30 | 94.46 | 61.36
2019-08-14 10:00 | 96.72 | 63.47
2019-08-14 10:30 | 96.45 | 64.11
2019-08-14 11:00 | 90.58 | 54.31
2019-08-14 11:30 | 94.46 | 60.2
2019-08-14 12:00 | 91.41 | 55.55
2019-08-14 12:30 | 94.14 | 61.98
2019-08-14 13:00 | 91.66 | 58.33
2019-08-14 13:30 | 95.13 | 64.24
2019-08-14 14:00 | 90.31 | 56.96
2019-08-14 14:30 | 90.27 | 57.45
2019-08-14 15:00 | 95.78 | 67.57
2019-08-14 15:30 | 97.05 | 64.28
2019-08-14 16:00 | 91.36 | 53.99
2019-08-14 16:30 | 90.84 | 60.68
2019-08-14 17:00 | 101.15 | 76.11
2019-08-14 17:30 | 99.2 | 76.59
2019-08-14 18:00 | 107.16 | 86.35
2019-08-14 18:30 | 104.43 | 81.14
2019-08-14 19:00 | 106.41 | 87.02
2019-08-14 19:30 | 103.68 | 81.71
2019-08-14 20:00 | 101.64 | 80.47
2019-08-14 20:30 | 107.58 | 87.55
2019-08-14 21:00 | 112.37 | 92.46
2019-08-14 21:30 | 110.12 | 90.06
2019-08-14 22:00 | 108.77 | 89.25
2019-08-14 22:30 | 115.91 | 97.95
2019-08-14 23:00 | 112.15 | 92.86
2019-08-14 23:30 | 110.28 | 90.26
2019-08-15 | 110.23 | 89.11
2019-08-15 00:30 | 110.59 | 89.36
2019-08-15 01:00 | 105.83 | 83.05
2019-08-15 01:30 | 103.87 | 85.45
2019-08-15 02:00 | 98.5 | 79.95
2019-08-15 02:30 | 100.66 | 82.24
2019-08-15 03:00 | 103.62 | 85.05
2019-08-15 03:30 | 103.18 | 84.39
2019-08-15 04:00 | 103.32 | 85.03
2019-08-15 04:30 | 103.61 | 85.37
2019-08-15 05:00 | 108.28 | 91.37
2019-08-15 05:30 | 106.53 | 88.78
2019-08-15 06:00 | 102 | 82.17
2019-08-15 06:30 | 102.01 | 83.76
2019-08-15 07:00 | 101.58 | 83.14
2019-08-15 07:30 | 99.86 | 79.03
2019-08-15 08:00 | 99.39 | 76.81
2019-08-15 08:30 | 98.15 | 71.98
2019-08-15 09:00 | 85.56 | 50.91
2019-08-15 09:30 | 83.48 | 45.88
2019-08-15 10:00 | 85.17 | 50.07
2019-08-15 10:30 | 86.33 | 56.47
2019-08-15 11:00 | 83.08 | 47.52
2019-08-15 11:30 | 83.97 | 50.87
2019-08-15 12:00 | 83.25 | 45.82
2019-08-15 12:30 | 82.65 | 43.41
2019-08-15 13:00 | 83.55 | 48.22
2019-08-15 13:30 | 86.15 | 51.23
2019-08-15 14:00 | 89.7 | 56.28
2019-08-15 14:30 | 92.28 | 63.96
2019-08-15 15:00 | 88.86 | 54.08
2019-08-15 15:30 | 91.47 | 59.09
2019-08-15 16:00 | 90.7 | 62.7
2019-08-15 16:30 | 90.78 | 66.64
2019-08-15 17:00 | 93.32 | 72.03
2019-08-15 17:30 | 96.72 | 79.75
2019-08-15 18:00 | 99.78 | 84.69
2019-08-15 18:30 | 96.22 | 80.97
2019-08-15 19:00 | 98.22 | 82.81
2019-08-15 19:30 | 112.95 | 99.62
2019-08-15 20:00 | 115.49 | 101.6
2019-08-15 20:30 | 114.97 | 101.3
2019-08-15 21:00 | 111.71 | 98.21
2019-08-15 21:30 | 104.51 | 90.35
2019-08-15 22:00 | 108.16 | 93.59
2019-08-15 22:30 | 122.31 | 108.9
2019-08-15 23:00 | 120.05 | 105.81
2019-08-15 23:30 | 110.69 | 95.76
2019-08-16 | 104.29 | 87.18
2019-08-16 00:30 | 106.71 | 91.53
2019-08-16 01:00 | 101.82 | 86.38
2019-08-16 01:30 | 97.56 | 79.68
2019-08-16 02:00 | 104.66 | 90.06
2019-08-16 02:30 | 103.76 | 90.26
2019-08-16 03:00 | 101.67 | 86.48
2019-08-16 03:30 | 99.47 | 83.55
2019-08-16 04:00 | 100.25 | 84.9
2019-08-16 04:30 | 103.07 | 88.47
2019-08-16 05:00 | 102.56 | 88.35
2019-08-16 05:30 | 103.24 | 91.05
2019-08-16 06:00 | 88.88 | 74.32
2019-08-16 06:30 | 83.77 | 67.37
2019-08-16 07:00 | 84.66 | 68.65
2019-08-16 07:30 | 88.76 | 75.11
2019-08-16 08:00 | 81.92 | 65.26
2019-08-16 08:30 | 78.47 | 57.62
2019-08-16 09:00 | 80.81 | 56.39
2019-08-16 09:30 | 88.17 | 64.72
2019-08-16 10:00 | 84.83 | 57.59
2019-08-16 10:30 | 79.77 | 50.39
2019-08-16 11:00 | 76.12 | 45.59
2019-08-16 11:30 | 84.78 | 56.74
2019-08-16 12:00 | 85.49 | 57.11
2019-08-16 12:30 | 90.79 | 64.33
2019-08-16 13:00 | 96.09 | 73.03
2019-08-16 13:30 | 98.67 | 71.84
2019-08-16 14:00 | 101.75 | 73.6
2019-08-16 14:30 | 109.09 | 84.39
2019-08-16 15:00 | 104.27 | 76.98
2019-08-16 15:30 | 101.06 | 78.16
2019-08-16 16:00 | 101.59 | 81.81
2019-08-16 16:30 | 105.45 | 88.98
2019-08-16 17:00 | 109.13 | 91.2
2019-08-16 17:30 | 103.23 | 87.24
2019-08-16 18:00 | 107.85 | 93.11
2019-08-16 18:30 | 107.94 | 93.75
2019-08-16 19:00 | 110.71 | 97
2019-08-16 19:30 | 108.85 | 96.05
2019-08-16 20:00 | 114.95 | 100.45
2019-08-16 20:30 | 115.25 | 99.79
2019-08-16 21:00 | 109.71 | 93.99
2019-08-16 21:30 | 111.03 | 96.33
2019-08-16 22:00 | 107.73 | 92.66
2019-08-16 22:30 | 106.57 | 92.1
2019-08-16 23:00 | 111 | 97.4
2019-08-16 23:30 | 108.49 | 94.26
2019-08-17 | 104.19 | 89.22
2019-08-17 00:30 | 103.69 | 88.3
2019-08-17 01:00 | 106.1 | 91.4
2019-08-17 01:30 | 110.02 | 96.61
2019-08-17 02:00 | 102.65 | 88.24
2019-08-17 02:30 | 108.15 | 93.65
2019-08-17 03:00 | 103.64 | 87.99
2019-08-17 03:30 | 106.9 | 92.18
2019-08-17 04:00 | 103.88 | 89.78
2019-08-17 04:30 | 101.59 | 86.42
2019-08-17 05:00 | 104.69 | 89.54
2019-08-17 05:30 | 110.03 | 96
2019-08-17 06:00 | 104.52 | 89.08
2019-08-17 06:30 | 106.51 | 91.87
2019-08-17 07:00 | 106.32 | 91.55
2019-08-17 07:30 | 102.19 | 85.06
2019-08-17 08:00 | 101.38 | 80.47
2019-08-17 08:30 | 101.59 | 77.09
2019-08-17 09:00 | 104.91 | 78.01
2019-08-17 09:30 | 108.44 | 83.8
2019-08-17 10:00 | 106.48 | 78.32
2019-08-17 10:30 | 109.82 | 78.63
2019-08-17 11:00 | 112.28 | 76.96
2019-08-17 11:30 | 106.76 | 67.68
2019-08-17 12:00 | 108.46 | 70.59
2019-08-17 12:30 | 111.29 | 74.78
2019-08-17 13:00 | 102.11 | 63.14
2019-08-17 13:30 | 108.65 | 73.07
2019-08-17 14:00 | 112.72 | 79.29
2019-08-17 14:30 | 108.31 | 74.94
2019-08-17 15:00 | 108.63 | 73.37
2019-08-17 15:30 | 103.09 | 67.64
2019-08-17 16:00 | 108.57 | 77.38
2019-08-17 16:30 | 105.93 | 77.24
2019-08-17 17:00 | 108.48 | 85.71
2019-08-17 17:30 | 111.32 | 92.35
2019-08-17 18:00 | 111.43 | 95.46
2019-08-17 18:30 | 108.38 | 93.53
2019-08-17 19:00 | 117.53 | 101.3
2019-08-17 19:30 | 104.75 | 88.46
2019-08-17 20:00 | 114.48 | 96.26
2019-08-17 20:30 | 122.55 | 103.45
2019-08-17 21:00 | 127.82 | 110.09
2019-08-17 21:30 | 127.25 | 109.15
2019-08-17 22:00 | 120.27 | 103.01
2019-08-17 22:30 | 128.34 | 113.04
2019-08-17 23:00 | 117.59 | 102.65
2019-08-17 23:30 | 116.53 | 100.52
2019-08-18 | 115.39 | 98.56
2019-08-18 00:30 | 119.26 | 101.66
2019-08-18 01:00 | 125.56 | 108
2019-08-18 01:30 | 116.51 | 98.91
2019-08-18 02:00 | 118.84 | 100.82
2019-08-18 02:30 | 126.08 | 107.86
2019-08-18 03:00 | 124.74 | 106.92
2019-08-18 03:30 | 117.58 | 99.3
2019-08-18 04:00 | 115.66 | 97.01
2019-08-18 04:30 | 120.18 | 102.08
2019-08-18 05:00 | 116.87 | 97.46
2019-08-18 05:30 | 115.29 | 95.89
2019-08-18 06:00 | 112.76 | 93.71
2019-08-18 06:30 | 109.86 | 92.73
2019-08-18 07:00 | 108.13 | 92.92
2019-08-18 07:30 | 106.16 | 90
2019-08-18 08:00 | 111.85 | 96.5
2019-08-18 08:30 | 109.89 | 93.1
2019-08-18 09:00 | 107.73 | 86.93
2019-08-18 09:30 | 103.51 | 83.5
2019-08-18 10:00 | 108.55 | 86.58
2019-08-18 10:30 | 116.74 | 97.97
2019-08-18 11:00 | 108.48 | 76.34
2019-08-18 11:30 | 104.62 | 68.96
2019-08-18 12:00 | 109.73 | 76.13
2019-08-18 12:30 | 109.2 | 73.97
2019-08-18 13:00 | 106.6 | 70.28
2019-08-18 13:30 | 100.56 | 62.97
2019-08-18 14:00 | 99.61 | 63.83
2019-08-18 14:30 | 100.86 | 62.62
2019-08-18 15:00 | 108.71 | 72.45
2019-08-18 15:30 | 111.56 | 75.61
2019-08-18 16:00 | 116.14 | 83.13
2019-08-18 16:30 | 120.06 | 92.03
2019-08-18 17:00 | 114.86 | 89.12
2019-08-18 17:30 | 121.25 | 101.27
2019-08-18 18:00 | 120.72 | 103.79
2019-08-18 18:30 | 120.47 | 101.19
2019-08-18 19:00 | 120.72 | 102.02
2019-08-18 19:30 | 120.56 | 101.61
2019-08-18 20:00 | 121.64 | 101.3
2019-08-18 20:30 | 128.84 | 109.24
2019-08-18 21:00 | 135.81 | 116.78
2019-08-18 21:30 | 133.98 | 115.2
2019-08-18 22:00 | 133.44 | 114.7
2019-08-18 22:30 | 123.63 | 104.05
2019-08-18 23:00 | 133.2 | 115.09
2019-08-18 23:30 | 132.94 | 113.8
2019-08-19 | 126.85 | 107.79
2019-08-19 00:30 | 133.55 | 114.13
2019-08-19 01:00 | 118.92 | 101.18
2019-08-19 01:30 | 119.44 | 101.15
2019-08-19 02:00 | 126.49 | 107.9
2019-08-19 02:30 | 122.45 | 102.97
2019-08-19 03:00 | 124.4 | 104.84
2019-08-19 03:30 | 124.84 | 103.57
2019-08-19 04:00 | 122.69 | 101.87
2019-08-19 04:30 | 127.8 | 106.82
2019-08-19 05:00 | 124.25 | 104.43
2019-08-19 05:30 | 132.13 | 113.33
2019-08-19 06:00 | 118.59 | 100.41
2019-08-19 06:30 | 115.17 | 96.13
2019-08-19 07:00 | 121.74 | 103.06
2019-08-19 07:30 | 110.85 | 90.26
2019-08-19 08:00 | 108.37 | 82.24
2019-08-19 08:30 | 102.41 | 69.87
2019-08-19 09:00 | 106.67 | 70.73
2019-08-19 09:30 | 109.02 | 72.66
2019-08-19 10:00 | 106.55 | 67.77
2019-08-19 10:30 | 108.92 | 72.92
2019-08-19 11:00 | 118.14 | 81.04
2019-08-19 11:30 | 116.36 | 76.36
2019-08-19 12:00 | 111.66 | 69.88
2019-08-19 12:30 | 112.51 | 74.27
2019-08-19 13:00 | 115.67 | 78.91
2019-08-19 13:30 | 106.3 | 70.91
2019-08-19 14:00 | 113.88 | 78.17
2019-08-19 14:30 | 108.15 | 70.2
2019-08-19 15:00 | 102.05 | 62.87
2019-08-19 15:30 | 103.5 | 63.56
2019-08-19 16:00 | 103.84 | 67.63
2019-08-19 16:30 | 99.12 | 66.73
2019-08-19 17:00 | 91.84 | 65.58
2019-08-19 17:30 | 91.62 | 73.28
2019-08-19 18:00 | 96.9 | 80.48
2019-08-19 18:30 | 104.98 | 87.66
2019-08-19 19:00 | 105.59 | 89
2019-08-19 19:30 | 101.22 | 84.67
2019-08-19 20:00 | 110.83 | 94.09
2019-08-19 20:30 | 104.61 | 87.47
2019-08-19 21:00 | 110.38 | 92.91
2019-08-19 21:30 | 105.54 | 87.63
2019-08-19 22:00 | 110.59 | 92.24
2019-08-19 22:30 | 108.79 | 91
2019-08-19 23:00 | 111.32 | 94.62
2019-08-19 23:30 | 115.12 | 95.68
2019-08-20 | 111.98 | 91.48
2019-08-20 00:30 | 118.36 | 98.31
2019-08-20 01:00 | 111.37 | 91.51
2019-08-20 01:30 | 106.65 | 86.26
2019-08-20 02:00 | 106.7 | 85.73
2019-08-20 02:30 | 109.99 | 87.07
2019-08-20 03:00 | 113.69 | 91.72
2019-08-20 03:30 | 111.74 | 88.35
2019-08-20 04:00 | 112.46 | 90.54
2019-08-20 04:30 | 118.47 | 96.39
2019-08-20 05:00 | 126.92 | 106.22
2019-08-20 05:30 | 121.97 | 102.54
2019-08-20 06:00 | 109.31 | 89.32
2019-08-20 06:30 | 111.86 | 92.74
2019-08-20 07:00 | 110.17 | 90.62
2019-08-20 07:30 | 117.3 | 95.13
2019-08-20 08:00 | 113.76 | 85.36
2019-08-20 08:30 | 111.68 | 81.1
2019-08-20 09:00 | 114.28 | 82.11
2019-08-20 09:30 | 105.15 | 69.69
2019-08-20 10:00 | 106.61 | 66.34
2019-08-20 10:30 | 113.28 | 73.31
2019-08-20 11:00 | 115.84 | 75.49
2019-08-20 11:30 | 111.34 | 73.04
2019-08-20 12:00 | 112.83 | 74.49
2019-08-20 12:30 | 113.33 | 75.32
2019-08-20 13:00 | 115.9 | 76.6
2019-08-20 13:30 | 120.76 | 82.01
2019-08-20 14:00 | 115.13 | 75.36
2019-08-20 14:30 | 109.62 | 70.57
2019-08-20 15:00 | 115.16 | 77.07
2019-08-20 15:30 | 115.48 | 79.98
2019-08-20 16:00 | 113.16 | 76.95
2019-08-20 16:30 | 118.83 | 87.4
2019-08-20 17:00 | 119.65 | 95.53
2019-08-20 17:30 | 125.32 | 105.19
2019-08-20 18:00 | 128.66 | 110.27
2019-08-20 18:30 | 123.01 | 103.63
2019-08-20 19:00 | 131.83 | 112.9
2019-08-20 19:30 | 136.76 | 119.5
2019-08-20 20:00 | 133.58 | 114.42
2019-08-20 20:30 | 131.87 | 112.06
2019-08-20 21:00 | 129.35 | 110.52
2019-08-20 21:30 | 128.17 | 109.2
2019-08-20 22:00 | 127.24 | 108.73
2019-08-20 22:30 | 131.12 | 113.69
2019-08-20 23:00 | 110.58 | 93.76
2019-08-20 23:30 | 116.95 | 100.43
2019-08-21 | 119.03 | 101.8
2019-08-21 00:30 | 117.2 | 99.01
2019-08-21 01:00 | 119.12 | 100.87
2019-08-21 01:30 | 113.17 | 94.93
2019-08-21 02:00 | 113.11 | 96.61
2019-08-21 02:30 | 108.48 | 92.9
2019-08-21 03:00 | 107.21 | 91.83
2019-08-21 03:30 | 110.11 | 94.6
2019-08-21 04:00 | 111.91 | 96.58
2019-08-21 04:30 | 108.65 | 93.93
2019-08-21 05:00 | 104.29 | 89.5
2019-08-21 05:30 | 104.23 | 88.99
2019-08-21 06:00 | 98.31 | 82.99
2019-08-21 06:30 | 93.98 | 80.11
2019-08-21 07:00 | 96.14 | 83.3
2019-08-21 07:30 | 81.3 | 64.72
2019-08-21 08:00 | 79.82 | 60.22
2019-08-21 08:30 | 77.98 | 55.39
2019-08-21 09:00 | 78.39 | 51.19
2019-08-21 09:30 | 78.36 | 54.14
2019-08-21 10:00 | 81.57 | 55.47
2019-08-21 10:30 | 79.33 | 52.67
2019-08-21 11:00 | 79.73 | 51.63
2019-08-21 11:30 | 79.57 | 51.08
2019-08-21 12:00 | 79.09 | 51.02
2019-08-21 12:30 | 72.44 | 45.88
2019-08-21 13:00 | 73.35 | 46.16
2019-08-21 13:30 | 75.94 | 48.06
2019-08-21 14:00 | 78.38 | 49.71
2019-08-21 14:30 | 86.03 | 57.51
2019-08-21 15:00 | 83.04 | 54.08
2019-08-21 15:30 | 85.93 | 58.24
2019-08-21 16:00 | 87.94 | 62.18
2019-08-21 16:30 | 94.23 | 73.5
2019-08-21 17:00 | 93.33 | 76.85
2019-08-21 17:30 | 98.88 | 86.09
2019-08-21 18:00 | 96.31 | 84.39
2019-08-21 18:30 | 98.02 | 86.63
2019-08-21 19:00 | 105.06 | 94.17
2019-08-21 19:30 | 114.61 | 104.01
2019-08-21 20:00 | 111.69 | 100.32
2019-08-21 20:30 | 99.54 | 87.4
2019-08-21 21:00 | 102.18 | 88.95
2019-08-21 21:30 | 105.37 | 93.11
2019-08-21 22:00 | 107.65 | 95.44
2019-08-21 22:30 | 102.19 | 90.4
2019-08-21 23:00 | 105.15 | 93.04
2019-08-21 23:30 | 101.41 | 88.9
2019-08-22 | 104.85 | 92.38
2019-08-22 00:30 | 98.29 | 85.55
2019-08-22 01:00 | 104.8 | 93.03
2019-08-22 01:30 | 103.08 | 91.21
2019-08-22 02:00 | 102.32 | 90.02
2019-08-22 02:30 | 101.02 | 88.78
2019-08-22 03:00 | 97.67 | 85.07
2019-08-22 03:30 | 96.75 | 83.72
2019-08-22 04:00 | 99.93 | 87.59
2019-08-22 04:30 | 100.73 | 88.71
2019-08-22 05:00 | 103.42 | 91.56
2019-08-22 05:30 | 100.92 | 88.85
2019-08-22 06:00 | 98.1 | 85.53
2019-08-22 06:30 | 92.28 | 77.02
2019-08-22 07:00 | 95.46 | 79.3
2019-08-22 07:30 | 98.91 | 82.18
2019-08-22 08:00 | 96.39 | 73.8
2019-08-22 08:30 | 92.94 | 66.32
2019-08-22 09:00 | 92.43 | 63.72
2019-08-22 09:30 | 88.58 | 59.99
2019-08-22 10:00 | 92.62 | 63.9
2019-08-22 10:30 | 88.47 | 53.83
2019-08-22 11:00 | 87.41 | 51.16
2019-08-22 11:30 | 88.15 | 53.04
2019-08-22 12:00 | 92.06 | 60.21
2019-08-22 12:30 | 92.97 | 60.92
2019-08-22 13:00 | 91.48 | 61.43
2019-08-22 13:30 | 89.8 | 62.47
2019-08-22 14:00 | 95.87 | 69.17
2019-08-22 14:30 | 98.64 | 71.27
2019-08-22 15:00 | 93.83 | 66.12
2019-08-22 15:30 | 89.03 | 61.59
2019-08-22 16:00 | 97.55 | 72.89
2019-08-22 16:30 | 99.3 | 76.59
2019-08-22 17:00 | 101.17 | 82.05
2019-08-22 17:30 | 104.95 | 90.64
2019-08-22 18:00 | 105.52 | 92.85
2019-08-22 18:30 | 106.84 | 95.16
2019-08-22 19:00 | 112.74 | 100.21
2019-08-22 19:30 | 111.79 | 98
2019-08-22 20:00 | 112.02 | 98.63
2019-08-22 20:30 | 117.08 | 103.44
2019-08-22 21:00 | 113.51 | 98.81
2019-08-22 21:30 | 115.99 | 101.07
2019-08-22 22:00 | 113.18 | 96.75
2019-08-22 22:30 | 117.89 | 102.13
2019-08-22 23:00 | 121.5 | 105.58
2019-08-22 23:30 | 117.56 | 101.31
2019-08-23 | 116.74 | 100.66
2019-08-23 00:30 | 122.87 | 104.19
2019-08-23 01:00 | 123.76 | 105.47
2019-08-23 01:30 | 125.39 | 107.01
2019-08-23 02:00 | 134.54 | 114.98
2019-08-23 02:30 | 122.69 | 103.18
2019-08-23 03:00 | 130.25 | 109.66
2019-08-23 03:30 | 109.14 | 89.96
2019-08-23 04:00 | 116.36 | 98.93
2019-08-23 04:30 | 114.06 | 97.28
2019-08-23 05:00 | 111.64 | 94.61
2019-08-23 05:30 | 114.72 | 97.67
2019-08-23 06:00 | 117.32 | 101.19
2019-08-23 06:30 | 113.84 | 98.47
2019-08-23 07:00 | 121.14 | 106.72
2019-08-23 07:30 | 118.13 | 101.88
2019-08-23 08:00 | 111.89 | 90.88
2019-08-23 08:30 | 109.2 | 82.97
2019-08-23 09:00 | 105.52 | 78.24
2019-08-23 09:30 | 106.74 | 75.29
2019-08-23 10:00 | 103.99 | 72.04
2019-08-23 10:30 | 101.37 | 71.11
2019-08-23 11:00 | 102.43 | 75.7
2019-08-23 11:30 | 95.73 | 67.23
2019-08-23 12:00 | 102.46 | 70.6
2019-08-23 12:30 | 110 | 79.86
2019-08-23 13:00 | 104.9 | 71.57
2019-08-23 13:30 | 103.6 | 68.16
2019-08-23 14:00 | 108.13 | 76.53
2019-08-23 14:30 | 107.26 | 74.64
2019-08-23 15:00 | 109.54 | 75.06
2019-08-23 15:30 | 103.17 | 69.85
2019-08-23 16:00 | 102.75 | 72.49
2019-08-23 16:30 | 107.42 | 80.12
2019-08-23 17:00 | 115.76 | 94.96
2019-08-23 17:30 | 113.13 | 96.78
2019-08-23 18:00 | 113.4 | 97.86
2019-08-23 18:30 | 110.84 | 95.96
2019-08-23 19:00 | 115.96 | 100.05
2019-08-23 19:30 | 115.74 | 100.55
2019-08-23 20:00 | 115.97 | 101.1
2019-08-23 20:30 | 116.25 | 101.06
2019-08-23 21:00 | 109.89 | 94.42
2019-08-23 21:30 | 111.89 | 95.94
2019-08-23 22:00 | 113.35 | 97.52
2019-08-23 22:30 | 110.17 | 94.99
2019-08-23 23:00 | 103.63 | 88.78
2019-08-23 23:30 | 108.9 | 92.09
2019-08-24 | 106.62 | 89.98
2019-08-24 00:30 | 112.42 | 94.86
2019-08-24 01:00 | 108.72 | 91.01
2019-08-24 01:30 | 109.14 | 91.95
2019-08-24 02:00 | 118.4 | 102.09
2019-08-24 02:30 | 121.42 | 106.15
2019-08-24 03:00 | 114.02 | 97.64
2019-08-24 03:30 | 105.94 | 90.51
2019-08-24 04:00 | 111.09 | 95.59
2019-08-24 04:30 | 107.5 | 92.41
2019-08-24 05:00 | 109.12 | 93.19
2019-08-24 05:30 | 111.04 | 95.47
2019-08-24 06:00 | 121.1 | 103.51
2019-08-24 06:30 | 120.68 | 103.94
2019-08-24 07:00 | 119.59 | 102.71
2019-08-24 07:30 | 110.37 | 90.08
2019-08-24 08:00 | 107.98 | 83.34
2019-08-24 08:30 | 111.92 | 82.39
2019-08-24 09:00 | 115.5 | 86.02
2019-08-24 09:30 | 120.04 | 87.4
2019-08-24 10:00 | 116.33 | 82.38
2019-08-24 10:30 | 123.93 | 90.41
2019-08-24 11:00 | 121.39 | 89.51
2019-08-24 11:30 | 118.39 | 88.41
2019-08-24 12:00 | 117.21 | 85.81
2019-08-24 12:30 | 118.47 | 87.98
2019-08-24 13:00 | 123.87 | 89.54
2019-08-24 13:30 | 133.77 | 102.23
2019-08-24 14:00 | 122.46 | 95.22
2019-08-24 14:30 | 124.11 | 95.31
2019-08-24 15:00 | 123.91 | 95.31
2019-08-24 15:30 | 121.45 | 94.62
2019-08-24 16:00 | 119.03 | 92.33
2019-08-24 16:30 | 118.87 | 94.49
2019-08-24 17:00 | 107.25 | 86.32
2019-08-24 17:30 | 113.68 | 94.05
2019-08-24 18:00 | 112.72 | 92.21
2019-08-24 18:30 | 106.94 | 90.28
2019-08-24 19:00 | 111.18 | 95
2019-08-24 19:30 | 117.63 | 101.16
2019-08-24 20:00 | 113.46 | 96.61
2019-08-24 20:30 | 115.32 | 97.41
2019-08-24 21:00 | 125.52 | 107.31
2019-08-24 21:30 | 112.48 | 94.78
2019-08-24 22:00 | 112.68 | 97.14
2019-08-24 22:30 | 109.2 | 93.06
2019-08-24 23:00 | 103.31 | 85.55
2019-08-24 23:30 | 104.97 | 87.95
2019-08-25 | 105.58 | 88.51
2019-08-25 00:30 | 106.83 | 90.04
2019-08-25 01:00 | 107.81 | 91.53
2019-08-25 01:30 | 109.81 | 91.64
2019-08-25 02:00 | 102.09 | 84.65
2019-08-25 02:30 | 99.32 | 82.79
2019-08-25 03:00 | 101.11 | 84.62
2019-08-25 03:30 | 100.04 | 83.47
2019-08-25 04:00 | 102.33 | 85.89
2019-08-25 04:30 | 104.16 | 87.74
2019-08-25 05:00 | 99.84 | 82.9
2019-08-25 05:30 | 98.85 | 83.12
2019-08-25 06:00 | 90.24 | 78.62
2019-08-25 06:30 | 86.52 | 77.11
2019-08-25 07:00 | 85.85 | 76.57
2019-08-25 07:30 | 84.42 | 74.9
2019-08-25 08:00 | 82.69 | 71.59
2019-08-25 08:30 | 84.79 | 74.31
2019-08-25 09:00 | 83.55 | 70.31
2019-08-25 09:30 | 79.08 | 60.52
2019-08-25 10:00 | 67.86 | 55.01
2019-08-25 10:30 | 65.79 | 48.77
2019-08-25 11:00 | 62.26 | 41.68
2019-08-25 11:30 | 62.62 | 43.19
2019-08-25 12:00 | 76.23 | 66.86
2019-08-25 12:30 | 81.3 | 73.67
2019-08-25 13:00 | 81.06 | 72.27
2019-08-25 13:30 | 88.42 | 77.76
2019-08-25 14:00 | 87.03 | 69.61
2019-08-25 14:30 | 88.98 | 77.16
2019-08-25 15:00 | 84.66 | 64.19
2019-08-25 15:30 | 77.9 | 58.21
2019-08-25 16:00 | 90.07 | 74.42
2019-08-25 16:30 | 96.12 | 81.94
2019-08-25 17:00 | 99.8 | 87.48
2019-08-25 17:30 | 101.53 | 91.07
2019-08-25 18:00 | 100.77 | 89.1
2019-08-25 18:30 | 98.52 | 87.15
2019-08-25 19:00 | 103.92 | 91.67
2019-08-25 19:30 | 102.48 | 89.88
2019-08-25 20:00 | 108.49 | 95.46
2019-08-25 20:30 | 107.66 | 94.04
2019-08-25 21:00 | 100.91 | 87.45
2019-08-25 21:30 | 104.2 | 91.18
2019-08-25 22:00 | 100.68 | 87.25
2019-08-25 22:30 | 103.47 | 89.23
2019-08-25 23:00 | 99.35 | 85.09
2019-08-25 23:30 | 96.91 | 83.02
2019-08-26 | 101.33 | 87.96
2019-08-26 00:30 | 102.02 | 89.09
2019-08-26 01:00 | 102.4 | 89.14
2019-08-26 01:30 | 102.37 | 89.54
2019-08-26 02:00 | 98.12 | 86.48
2019-08-26 02:30 | 100.09 | 88.19
2019-08-26 03:00 | 102.05 | 90.09
2019-08-26 03:30 | 96.6 | 83.95
2019-08-26 04:00 | 95.75 | 83.88
2019-08-26 04:30 | 98.88 | 86.27
2019-08-26 05:00 | 98.27 | 84.76
2019-08-26 05:30 | 97.17 | 85.04
2019-08-26 06:00 | 95.37 | 82.77
2019-08-26 06:30 | 95.6 | 83.45
2019-08-26 07:00 | 102.29 | 90.09
2019-08-26 07:30 | 92.66 | 79.62
2019-08-26 08:00 | 94.39 | 75.72
2019-08-26 08:30 | 93.06 | 70.3
2019-08-26 09:00 | 92.4 | 67.06
2019-08-26 09:30 | 86.52 | 59.76
2019-08-26 10:00 | 87.47 | 58.44
2019-08-26 10:30 | 85.53 | 55.24
2019-08-26 11:00 | 87.99 | 56.98
2019-08-26 11:30 | 83.34 | 50.26
2019-08-26 12:00 | 84.88 | 59.02
2019-08-26 12:30 | 83.77 | 54.22
2019-08-26 13:00 | 86.73 | 55.28
2019-08-26 13:30 | 87.99 | 59.08
2019-08-26 14:00 | 91.41 | 59.49
2019-08-26 14:30 | 92.76 | 63.13
2019-08-26 15:00 | 97.24 | 67.34
2019-08-26 15:30 | 97.19 | 67.98
2019-08-26 16:00 | 95.76 | 67.63
2019-08-26 16:30 | 94.84 | 70.89
2019-08-26 17:00 | 94.65 | 75.07
2019-08-26 17:30 | 93.04 | 79.27
2019-08-26 18:00 | 96.19 | 84.27
2019-08-26 18:30 | 96.63 | 83.49
2019-08-26 19:00 | 100.43 | 85.18
2019-08-26 19:30 | 103.24 | 86.88
2019-08-26 20:00 | 105.92 | 88.84
2019-08-26 20:30 | 108.72 | 91.46
2019-08-26 21:00 | 107.81 | 89.63
2019-08-26 21:30 | 109.14 | 90.65
2019-08-26 22:00 | 104.69 | 84.3
2019-08-26 22:30 | 104.96 | 84.1
2019-08-26 23:00 | 109.77 | 88.69
2019-08-26 23:30 | 110.05 | 88.68
2019-08-27 | 106.68 | 86.31
2019-08-27 00:30 | 111.46 | 91.51
2019-08-27 01:00 | 111.21 | 91.06
2019-08-27 01:30 | 108.7 | 88.54
2019-08-27 02:00 | 108.19 | 88.72
2019-08-27 02:30 | 111.37 | 93.16
2019-08-27 03:00 | 114.22 | 96.3
2019-08-27 03:30 | 108.05 | 88.76
2019-08-27 04:00 | 109.33 | 90.6
2019-08-27 04:30 | 108.51 | 89.76
2019-08-27 05:00 | 110.44 | 91.92
2019-08-27 05:30 | 112.78 | 95.25
2019-08-27 06:00 | 105.79 | 87.46
2019-08-27 06:30 | 104.11 | 87.13
2019-08-27 07:00 | 108.71 | 91.8
2019-08-27 07:30 | 96.18 | 74.53
2019-08-27 08:00 | 94.98 | 67.16
2019-08-27 08:30 | 98.74 | 68.11
2019-08-27 09:00 | 99.82 | 71.83
2019-08-27 09:30 | 94.76 | 65.17
2019-08-27 10:00 | 101.54 | 70.76
2019-08-27 10:30 | 99.83 | 68.92
2019-08-27 11:00 | 100.95 | 68.88
2019-08-27 11:30 | 101.1 | 69.4
2019-08-27 12:00 | 102.95 | 72.77
2019-08-27 12:30 | 101.67 | 72.39
2019-08-27 13:00 | 98.55 | 68.81
2019-08-27 13:30 | 94.35 | 63.11
2019-08-27 14:00 | 91.57 | 56.12
2019-08-27 14:30 | 98.35 | 73.28
2019-08-27 15:00 | 104.24 | 85.66
2019-08-27 15:30 | 105.1 | 75.71
2019-08-27 16:00 | 100.69 | 71.31
2019-08-27 16:30 | 102.53 | 76.22
2019-08-27 17:00 | 101.15 | 81.03
2019-08-27 17:30 | 103.06 | 89.27
2019-08-27 18:00 | 99.11 | 87.74
2019-08-27 18:30 | 98.13 | 85.67
2019-08-27 19:00 | 106.28 | 93.89
2019-08-27 19:30 | 96.7 | 84.1
2019-08-27 20:00 | 98.79 | 86.78
2019-08-27 20:30 | 95.86 | 83.6
2019-08-27 21:00 | 95.51 | 82.81
2019-08-27 21:30 | 101.17 | 88.97
2019-08-27 22:00 | 102.11 | 89.79
2019-08-27 22:30 | 104.38 | 91.46
2019-08-27 23:00 | 102.95 | 89.33
2019-08-27 23:30 | 96.62 | 82.97
2019-08-28 | 101.81 | 89.15
2019-08-28 00:30 | 97.6 | 84.67
2019-08-28 01:00 | 99.56 | 86.96
2019-08-28 01:30 | 97.9 | 85.1
2019-08-28 02:00 | 99.05 | 86.43
2019-08-28 02:30 | 97.68 | 85.82
2019-08-28 03:00 | 103.44 | 91.4
2019-08-28 03:30 | 104.97 | 92.64
2019-08-28 04:00 | 92.72 | 78.69
2019-08-28 04:30 | 100.93 | 87.45
2019-08-28 05:00 | 107.5 | 93.64
2019-08-28 05:30 | 100.84 | 87.16
2019-08-28 06:00 | 97.36 | 83.44
2019-08-28 06:30 | 98.15 | 83.68
2019-08-28 07:00 | 94.75 | 79.69
2019-08-28 07:30 | 93.31 | 78.63
2019-08-28 08:00 | 95.02 | 78.63
2019-08-28 08:30 | 93.78 | 74.18
2019-08-28 09:00 | 97.22 | 71.46
2019-08-28 09:30 | 86.55 | 60.03
2019-08-28 10:00 | 90.05 | 57.17
2019-08-28 10:30 | 98.93 | 65.64
2019-08-28 11:00 | 98.25 | 65.24
2019-08-28 11:30 | 93.31 | 57.75
2019-08-28 12:00 | 93.16 | 56.74
2019-08-28 12:30 | 95.66 | 57.54
2019-08-28 13:00 | 92.18 | 54.04
2019-08-28 13:30 | 97.56 | 60.41
2019-08-28 14:00 | 92.82 | 58.79
2019-08-28 14:30 | 90.3 | 57.06
2019-08-28 15:00 | 95.24 | 63.86
2019-08-28 15:30 | 98.33 | 67.1
2019-08-28 16:00 | 102.57 | 74.75
2019-08-28 16:30 | 102.71 | 79.82
2019-08-28 17:00 | 99.66 | 82.06
2019-08-28 17:30 | 110.95 | 94.85
2019-08-28 18:00 | 106.71 | 91.17
2019-08-28 18:30 | 103.79 | 87.91
2019-08-28 19:00 | 102.39 | 87.33
2019-08-28 19:30 | 108.86 | 92.71
2019-08-28 20:00 | 105.9 | 90.74
2019-08-28 20:30 | 108.53 | 93.81
2019-08-28 21:00 | 108.67 | 92.33
2019-08-28 21:30 | 101.23 | 84.8
2019-08-28 22:00 | 105.15 | 88.99
2019-08-28 22:30 | 107.53 | 90.56
2019-08-28 23:00 | 108.72 | 92.32
2019-08-28 23:30 | 109.72 | 93.68
2019-08-29 | 110.51 | 94.41
2019-08-29 00:30 | 114.47 | 98.21
2019-08-29 01:00 | 117.98 | 102.01
2019-08-29 01:30 | 117.92 | 103.34
2019-08-29 02:00 | 119.54 | 104.26
2019-08-29 02:30 | 113.98 | 98.52
2019-08-29 03:00 | 116.01 | 100.38
2019-08-29 03:30 | 104.33 | 86.83
2019-08-29 04:00 | 107 | 91.12
2019-08-29 04:30 | 111.86 | 95.97
2019-08-29 05:00 | 107.37 | 91.68
2019-08-29 05:30 | 119.87 | 105.15
2019-08-29 06:00 | 111.07 | 94.92
2019-08-29 06:30 | 101.9 | 86.06
2019-08-29 07:00 | 109.08 | 93.39
2019-08-29 07:30 | 108.47 | 92.13
2019-08-29 08:00 | 105.07 | 85.11
2019-08-29 08:30 | 104.25 | 75.15
2019-08-29 09:00 | 105.96 | 72.69
2019-08-29 09:30 | 105.76 | 71.39
2019-08-29 10:00 | 98.26 | 70.48
2019-08-29 10:30 | 98.71 | 67.47
2019-08-29 11:00 | 101.09 | 73.05
2019-08-29 11:30 | 96.44 | 66.4
2019-08-29 12:00 | 97.84 | 66.22
2019-08-29 12:30 | 103.08 | 77.99
2019-08-29 13:00 | 94.77 | 64.72
2019-08-29 13:30 | 98.41 | 68.84
2019-08-29 14:00 | 105.4 | 72.91
2019-08-29 14:30 | 95.14 | 61.82
2019-08-29 15:00 | 99.1 | 70.5
2019-08-29 15:30 | 100.03 | 75.01
2019-08-29 16:00 | 103.75 | 83.3
2019-08-29 16:30 | 103.92 | 86.41
2019-08-29 17:00 | 99.06 | 77.85
2019-08-29 17:30 | 105.83 | 91.66
2019-08-29 18:00 | 98.1 | 84.03
2019-08-29 18:30 | 102.57 | 89.33
2019-08-29 19:00 | 108.57 | 94.79
2019-08-29 19:30 | 105.32 | 91.42
2019-08-29 20:00 | 111.07 | 96.23
2019-08-29 20:30 | 118.45 | 103.4
2019-08-29 21:00 | 118.17 | 102.32
2019-08-29 21:30 | 111.77 | 95.42
2019-08-29 22:00 | 116.94 | 100.39
2019-08-29 22:30 | 112.93 | 95.52
2019-08-29 23:00 | 116.38 | 98.11
2019-08-29 23:30 | 110.29 | 92.42
2019-08-30 | 112.1 | 95.22
2019-08-30 00:30 | 111.87 | 95.37
2019-08-30 01:00 | 111.06 | 93.6
2019-08-30 01:30 | 112.84 | 95.15
2019-08-30 02:00 | 115.19 | 97.88
2019-08-30 02:30 | 115.81 | 99.05
2019-08-30 03:00 | 119.04 | 102.9
2019-08-30 03:30 | 114.8 | 99.28
2019-08-30 04:00 | 123.35 | 108.65
2019-08-30 04:30 | 113.19 | 97.26
2019-08-30 05:00 | 102.06 | 84.32
2019-08-30 05:30 | 106.99 | 91.19
2019-08-30 06:00 | 108.09 | 92.58
2019-08-30 06:30 | 109.34 | 96.18
2019-08-30 07:00 | 103.26 | 89.55
2019-08-30 07:30 | 104.69 | 87.53
2019-08-30 08:00 | 100.64 | 75.91
2019-08-30 08:30 | 105 | 76.04
2019-08-30 09:00 | 112.05 | 82.59
2019-08-30 09:30 | 102.36 | 67.3
2019-08-30 10:00 | 112.06 | 75.65
2019-08-30 10:30 | 108.53 | 74.08
2019-08-30 11:00 | 107.99 | 70.79
2019-08-30 11:30 | 108.18 | 71.44
2019-08-30 12:00 | 104.91 | 70.08
2019-08-30 12:30 | 100.58 | 81.22
2019-08-30 13:00 | 105.46 | 74.43
2019-08-30 13:30 | 105.95 | 76.98
2019-08-30 14:00 | 109.21 | 78.01
2019-08-30 14:30 | 107.57 | 82.72
2019-08-30 15:00 | 106.36 | 88
2019-08-30 15:30 | 104.03 | 78.18
2019-08-30 16:00 | 104.45 | 72.99
2019-08-30 16:30 | 107.79 | 81.77
2019-08-30 17:00 | 125.98 | 107.64
2019-08-30 17:30 | 114.58 | 97.19
2019-08-30 18:00 | 105.78 | 93.2
2019-08-30 18:30 | 104.91 | 93.37
2019-08-30 19:00 | 108.77 | 96.28
2019-08-30 19:30 | 112.69 | 99.32
2019-08-30 20:00 | 113.2 | 99.93
2019-08-30 20:30 | 118.58 | 105.05
2019-08-30 21:00 | 120.05 | 105.44
2019-08-30 21:30 | 120.23 | 105.38
2019-08-30 22:00 | 109.41 | 95.38
2019-08-30 22:30 | 112.65 | 98.04
2019-08-30 23:00 | 113 | 97.9
2019-08-30 23:30 | 109.64 | 94.27
2019-08-31 | 112.31 | 96.47
2019-08-31 00:30 | 112.28 | 97.21
2019-08-31 01:00 | 107.28 | 92.38
2019-08-31 01:30 | 110.07 | 94.71
2019-08-31 02:00 | 112.77 | 99.26
2019-08-31 02:30 | 119.56 | 106.42
2019-08-31 03:00 | 114.58 | 100.7
2019-08-31 03:30 | 109.35 | 95.41
2019-08-31 04:00 | 112.02 | 98.06
2019-08-31 04:30 | 112.85 | 98
2019-08-31 05:00 | 106.32 | 89.95
2019-08-31 05:30 | 108.58 | 93.51
2019-08-31 06:00 | 108.08 | 92.85
2019-08-31 06:30 | 102.31 | 87.54
2019-08-31 07:00 | 100.96 | 85.73
2019-08-31 07:30 | 102.12 | 82.74
2019-08-31 08:00 | 104.9 | 81.67
2019-08-31 08:30 | 108.86 | 80.42
2019-08-31 09:00 | 110.5 | 77.85
2019-08-31 09:30 | 110.68 | 76.09
2019-08-31 10:00 | 110.95 | 75.2
2019-08-31 10:30 | 102 | 63.14
2019-08-31 11:00 | 106.16 | 71.07
2019-08-31 11:30 | 106.31 | 70.69
2019-08-31 12:00 | 113.45 | 93.25
2019-08-31 12:30 | 109.52 | 88.56
2019-08-31 13:00 | 117.76 | 97.32
2019-08-31 13:30 | 123.14 | 99.84
2019-08-31 14:00 | 113.35 | 90.24
2019-08-31 14:30 | 110.84 | 86.35
2019-08-31 15:00 | 111.99 | 79.26
2019-08-31 15:30 | 114.92 | 80.9
2019-08-31 16:00 | 109.03 | 76.72
2019-08-31 16:30 | 111.38 | 77.89
2019-08-31 17:00 | 111.48 | 82.82
2019-08-31 17:30 | 117.95 | 95.32
2019-08-31 18:00 | 120.72 | 102.23
2019-08-31 18:30 | 124.07 | 106.37
2019-08-31 19:00 | 128.26 | 110.55
2019-08-31 19:30 | 128.27 | 110.28
2019-08-31 20:00 | 135.38 | 117.69
2019-08-31 20:30 | 132.96 | 113.48
2019-08-31 21:00 | 130.74 | 112.08
2019-08-31 21:30 | 126.08 | 106.57
2019-08-31 22:00 | 119.88 | 100.84
2019-08-31 22:30 | 130.26 | 110.97
2019-08-31 23:00 | 129.64 | 111.61
2019-08-31 23:30 | 126.27 | 107.09
2019-09-01 | 131.39 | 112.97
2019-09-01 00:30 | 121.41 | 102.92
2019-09-01 01:00 | 124.54 | 105.55
2019-09-01 01:30 | 129.2 | 110.33
2019-09-01 02:00 | 118.87 | 100.52
2019-09-01 02:30 | 124.67 | 105.35
2019-09-01 03:00 | 101.11 | 83.2
2019-09-01 03:30 | 122.38 | 103.14
2019-09-01 04:00 | 118.65 | 98.25
2019-09-01 04:30 | 127.38 | 110.11
2019-09-01 05:00 | 121.96 | 104.59
2019-09-01 05:30 | 119.37 | 101.3
2019-09-01 06:00 | 117.51 | 99.7
2019-09-01 06:30 | 109.11 | 90.8
2019-09-01 07:00 | 110.59 | 91.33
2019-09-01 07:30 | 107.36 | 84.54
2019-09-01 08:00 | 107.56 | 84.64
2019-09-01 08:30 | 112.22 | 87.76
2019-09-01 09:00 | 113.3 | 80.19
2019-09-01 09:30 | 112.59 | 84.23
2019-09-01 10:00 | 112.99 | 79.85
2019-09-01 10:30 | 106.95 | 72.65
2019-09-01 11:00 | 98.73 | 64.96
2019-09-01 11:30 | 102.01 | 66.71
2019-09-01 12:00 | 102.25 | 79.61
2019-09-01 12:30 | 99.47 | 81.2
2019-09-01 13:00 | 107.59 | 87.19
2019-09-01 13:30 | 111.14 | 87.68
2019-09-01 14:00 | 109.77 | 87.8
2019-09-01 14:30 | 113.43 | 91.94
2019-09-01 15:00 | 116.18 | 92.52
2019-09-01 15:30 | 115.24 | 79.91
2019-09-01 16:00 | 114.07 | 80.09
2019-09-01 16:30 | 115.37 | 84.55
2019-09-01 17:00 | 113.4 | 86.93
2019-09-01 17:30 | 117.46 | 97.55
2019-09-01 18:00 | 120.77 | 102.65
2019-09-01 18:30 | 108.22 | 88.96
2019-09-01 19:00 | 122.2 | 104.95
2019-09-01 19:30 | 120.93 | 102.51
2019-09-01 20:00 | 121.92 | 102.65
2019-09-01 20:30 | 122.77 | 103
2019-09-01 21:00 | 124.1 | 104.97
2019-09-01 21:30 | 121.65 | 102.19
2019-09-01 22:00 | 113.24 | 95.82
2019-09-01 22:30 | 113.95 | 95.34
2019-09-01 23:00 | 113.78 | 94.88
2019-09-01 23:30 | 113.93 | 95.49
2019-09-02 | 117.55 | 99.51
2019-09-02 00:30 | 115.58 | 98.44
2019-09-02 01:00 | 113.88 | 94.41
2019-09-02 01:30 | 119.49 | 99.96
2019-09-02 02:00 | 118.22 | 99.67
2019-09-02 02:30 | 114.69 | 96.52
2019-09-02 03:00 | 110.8 | 91.01
2019-09-02 03:30 | 108.41 | 90.25
2019-09-02 04:00 | 111.41 | 95.43
2019-09-02 04:30 | 114.1 | 98.59
2019-09-02 05:00 | 110.97 | 94.55
2019-09-02 05:30 | 111.05 | 94.52
2019-09-02 06:00 | 104.57 | 87.43
2019-09-02 06:30 | 104.75 | 89.7
2019-09-02 07:00 | 106.1 | 91.17
2019-09-02 07:30 | 105.41 | 86.55
2019-09-02 08:00 | 104.5 | 80.43
2019-09-02 08:30 | 107.3 | 78.07
2019-09-02 09:00 | 98.29 | 63.07
2019-09-02 09:30 | 101.88 | 63.73
2019-09-02 10:00 | 107.35 | 71.19
2019-09-02 10:30 | 101.69 | 63.65
2019-09-02 11:00 | 110.71 | 70.85
2019-09-02 11:30 | 99.51 | 59.06
2019-09-02 12:00 | 100.18 | 78.46
2019-09-02 12:30 | 108.79 | 88.46
2019-09-02 13:00 | 112.87 | 87.19
2019-09-02 13:30 | 104.03 | 64.86
2019-09-02 14:00 | 114.42 | 76.75
2019-09-02 14:30 | 112.56 | 70.88
2019-09-02 15:00 | 107.74 | 64.86
2019-09-02 15:30 | 105.91 | 65.54
2019-09-02 16:00 | 112.19 | 76.61
2019-09-02 16:30 | 115.41 | 83.03
2019-09-02 17:00 | 108.34 | 80.6
2019-09-02 17:30 | 111.93 | 89.88
2019-09-02 18:00 | 105.42 | 87.25
2019-09-02 18:30 | 108.32 | 91.06
2019-09-02 19:00 | 115.73 | 99.31
2019-09-02 19:30 | 116.74 | 98.7
2019-09-02 20:00 | 113.6 | 96.62
2019-09-02 20:30 | 120.14 | 102.24
2019-09-02 21:00 | 116.38 | 99.12
2019-09-02 21:30 | 113.64 | 95.62
2019-09-02 22:00 | 122.93 | 104.25
2019-09-02 22:30 | 110.69 | 91.58
2019-09-02 23:00 | 111.79 | 92.65
2019-09-02 23:30 | 117.23 | 98.23
2019-09-03 | 112.87 | 93.94
2019-09-03 00:30 | 115.09 | 97.08
2019-09-03 01:00 | 120.14 | 103.24
2019-09-03 01:30 | 116.69 | 97.74
2019-09-03 02:00 | 110.93 | 92.31
2019-09-03 02:30 | 118.36 | 99.39
2019-09-03 03:00 | 115.89 | 97
2019-09-03 03:30 | 113.68 | 94.54
2019-09-03 04:00 | 116.52 | 98.51
2019-09-03 04:30 | 114.07 | 94.17
2019-09-03 05:00 | 113.86 | 93.13
2019-09-03 05:30 | 112.32 | 93.68
2019-09-03 06:00 | 112.88 | 95.37
2019-09-03 06:30 | 113.27 | 96.72
2019-09-03 07:00 | 112.48 | 94.98
2019-09-03 07:30 | 100.35 | 82.01
2019-09-03 08:00 | 96.56 | 71.71
2019-09-03 08:30 | 100.71 | 71.67
2019-09-03 09:00 | 102.82 | 71.17
2019-09-03 09:30 | 96.95 | 62.19
2019-09-03 10:00 | 101.83 | 67.32
2019-09-03 10:30 | 100.96 | 64.5
2019-09-03 11:00 | 105.85 | 64.87
2019-09-03 11:30 | 98.78 | 55.27
2019-09-03 12:00 | 91.2 | 60.4
2019-09-03 12:30 | 97.38 | 72.66
2019-09-03 13:00 | 92.51 | 65.02
2019-09-03 13:30 | 105.24 | 67.93
2019-09-03 14:00 | 107.29 | 67.04
2019-09-03 14:30 | 108.1 | 68.36
2019-09-03 15:00 | 105.74 | 64.29
2019-09-03 15:30 | 107.16 | 68.78
2019-09-03 16:00 | 106.75 | 69.23
2019-09-03 16:30 | 109.58 | 73.64
2019-09-03 17:00 | 111.37 | 81.21
2019-09-03 17:30 | 115.09 | 91.81
2019-09-03 18:00 | 114.56 | 94.06
2019-09-03 18:30 | 112.99 | 91.84
2019-09-03 19:00 | 117.69 | 96.49
2019-09-03 19:30 | 124.09 | 104.3
2019-09-03 20:00 | 130.64 | 110.66
2019-09-03 20:30 | 121.16 | 100.24
2019-09-03 21:00 | 120.5 | 98.39
2019-09-03 21:30 | 110.94 | 89.82
2019-09-03 22:00 | 119.69 | 98.03
2019-09-03 22:30 | 119.17 | 96.97
2019-09-03 23:00 | 119.23 | 96.83
2019-09-03 23:30 | 119.26 | 97.16
2019-09-04 | 120.71 | 99.53
2019-09-04 00:30 | 124.22 | 102.33
2019-09-04 01:00 | 117.18 | 95.15
2019-09-04 01:30 | 120.55 | 97.92
2019-09-04 02:00 | 121.43 | 100.06
2019-09-04 02:30 | 116.2 | 95.27
2019-09-04 03:00 | 118.36 | 99.61
2019-09-04 03:30 | 114.29 | 94.17
2019-09-04 04:00 | 116.83 | 96.92
2019-09-04 04:30 | 118.95 | 99.7
2019-09-04 05:00 | 120.6 | 101.1
2019-09-04 05:30 | 121.24 | 102.43
2019-09-04 06:00 | 112.65 | 93.69
2019-09-04 06:30 | 113.53 | 95.07
2019-09-04 07:00 | 111.9 | 91.87
2019-09-04 07:30 | 101.95 | 76.53
2019-09-04 08:00 | 106.14 | 75.97
2019-09-04 08:30 | 102.85 | 68.05
2019-09-04 09:00 | 99.71 | 64.12
2019-09-04 09:30 | 99.99 | 65.11
2019-09-04 10:00 | 98.91 | 63.26
2019-09-04 10:30 | 99.34 | 63.89
2019-09-04 11:00 | 100.91 | 67.65
2019-09-04 11:30 | 98.84 | 65.92
2019-09-04 12:00 | 100.44 | 80.26
2019-09-04 12:30 | 105.65 | 86.85
2019-09-04 13:00 | 108.7 | 89.44
2019-09-04 13:30 | 108.78 | 88.31
2019-09-04 14:00 | 106.2 | 85.03
2019-09-04 14:30 | 112.11 | 93.56
2019-09-04 15:00 | 109.4 | 87.92
2019-09-04 15:30 | 105.52 | 79.87
2019-09-04 16:00 | 111.43 | 80.18
2019-09-04 16:30 | 111.19 | 85.29
2019-09-04 17:00 | 111.34 | 87.4
2019-09-04 17:30 | 110.62 | 91.3
2019-09-04 18:00 | 113.19 | 95.63
2019-09-04 18:30 | 113.02 | 94.84
2019-09-04 19:00 | 118.67 | 101.89
2019-09-04 19:30 | 119.99 | 104.31
2019-09-04 20:00 | 114.51 | 97.07
2019-09-04 20:30 | 118.35 | 101.99
2019-09-04 21:00 | 117.98 | 100.84
2019-09-04 21:30 | 114.94 | 96.92
2019-09-04 22:00 | 114.97 | 96.76
2019-09-04 22:30 | 119.53 | 102.4
2019-09-04 23:00 | 118.86 | 101.45
2019-09-04 23:30 | 118.62 | 100.86
2019-09-05 | 111.09 | 92.75
2019-09-05 00:30 | 114.82 | 96.12
2019-09-05 01:00 | 112.77 | 94.27
2019-09-05 01:30 | 111.76 | 92.91
2019-09-05 02:00 | 116.04 | 95.91
2019-09-05 02:30 | 119.72 | 100.13
2019-09-05 03:00 | 116.99 | 97.78
2019-09-05 03:30 | 112.07 | 92.05
2019-09-05 04:00 | 117.18 | 96.21
2019-09-05 04:30 | 115.86 | 96.12
2019-09-05 05:00 | 118.36 | 98.81
2019-09-05 05:30 | 113.48 | 94.17
2019-09-05 06:00 | 107.4 | 87.77
2019-09-05 06:30 | 104.72 | 85.94
2019-09-05 07:00 | 117.79 | 101.05
2019-09-05 07:30 | 111.28 | 89.46
2019-09-05 08:00 | 107.69 | 86.16
2019-09-05 08:30 | 102.19 | 82.25
2019-09-05 09:00 | 104.49 | 84.41
2019-09-05 09:30 | 108.47 | 88.42
2019-09-05 10:00 | 106.33 | 84.5
2019-09-05 10:30 | 105.72 | 84.28
2019-09-05 11:00 | 97.59 | 75.96
2019-09-05 11:30 | 97.7 | 77.34
2019-09-05 12:00 | 100.39 | 82.47
2019-09-05 12:30 | 105.66 | 84.51
2019-09-05 13:00 | 113.4 | 93.77
2019-09-05 13:30 | 102.7 | 82.19
2019-09-05 14:00 | 104.15 | 83.3
2019-09-05 14:30 | 104.62 | 73.74
2019-09-05 15:00 | 107.21 | 72.32
2019-09-05 15:30 | 107.81 | 75.84
2019-09-05 16:00 | 105.26 | 67.65
2019-09-05 16:30 | 105.05 | 71.94
2019-09-05 17:00 | 113.59 | 86.45
2019-09-05 17:30 | 115.84 | 96.43
2019-09-05 18:00 | 112.73 | 94.73
2019-09-05 18:30 | 106.43 | 87.7
2019-09-05 19:00 | 112 | 94.25
2019-09-05 19:30 | 112.93 | 95.4
2019-09-05 20:00 | 117.13 | 100.03
2019-09-05 20:30 | 111.28 | 94.98
2019-09-05 21:00 | 105.54 | 88.17
2019-09-05 21:30 | 112.5 | 96.58
2019-09-05 22:00 | 120.46 | 104.18
2019-09-05 22:30 | 124.49 | 108.97
2019-09-05 23:00 | 115.34 | 99.99
2019-09-05 23:30 | 118.49 | 100.81
2019-09-06 | 119.73 | 102.13
2019-09-06 00:30 | 117.59 | 99.63
2019-09-06 01:00 | 120.23 | 101.67
2019-09-06 01:30 | 116.81 | 97.67
2019-09-06 02:00 | 117.02 | 99.42
2019-09-06 02:30 | 119.33 | 101.54
2019-09-06 03:00 | 124.27 | 107.74
2019-09-06 03:30 | 122.92 | 106.2
2019-09-06 04:00 | 122.72 | 106.14
2019-09-06 04:30 | 120.02 | 102.36
2019-09-06 05:00 | 114.25 | 96.09
2019-09-06 05:30 | 113.76 | 96.76
2019-09-06 06:00 | 110.33 | 91.96
2019-09-06 06:30 | 109.55 | 92.14
2019-09-06 07:00 | 112.77 | 94.59
2019-09-06 07:30 | 105.62 | 82.79
2019-09-06 08:00 | 100.83 | 71.3
2019-09-06 08:30 | 109.36 | 75.3
2019-09-06 09:00 | 112.44 | 76.87
2019-09-06 09:30 | 109 | 71.2
2019-09-06 10:00 | 113.61 | 73.89
2019-09-06 10:30 | 117.03 | 77.59
2019-09-06 11:00 | 108.93 | 67.35
2019-09-06 11:30 | 110.82 | 66.26
2019-09-06 12:00 | 113.72 | 70.79
2019-09-06 12:30 | 115.83 | 76.77
2019-09-06 13:00 | 113.04 | 78.31
2019-09-06 13:30 | 117.72 | 83.56
2019-09-06 14:00 | 116.26 | 83.36
2019-09-06 14:30 | 119.79 | 88.88
2019-09-06 15:00 | 118.14 | 85.36
2019-09-06 15:30 | 117.21 | 89.72
2019-09-06 16:00 | 114.53 | 85.19
2019-09-06 16:30 | 121.84 | 94.14
2019-09-06 17:00 | 117.91 | 94.44
2019-09-06 17:30 | 118.2 | 100.05
2019-09-06 18:00 | 117.94 | 100.58
2019-09-06 18:30 | 124.82 | 110.52
2019-09-06 19:00 | 125.48 | 111.65
2019-09-06 19:30 | 123.32 | 108.91
2019-09-06 20:00 | 111.16 | 98.89
2019-09-06 20:30 | 124.76 | 111.56
2019-09-06 21:00 | 119.75 | 105.65
2019-09-06 21:30 | 129.79 | 116.05
2019-09-06 22:00 | 126.46 | 112.39
2019-09-06 22:30 | 124.28 | 110.16
2019-09-06 23:00 | 129.51 | 114.61
2019-09-06 23:30 | 123.68 | 108.73
2019-09-07 | 119.12 | 102.91
2019-09-07 00:30 | 117.64 | 101.58
2019-09-07 01:00 | 118.72 | 102.92
2019-09-07 01:30 | 115.91 | 100.16
2019-09-07 02:00 | 115.75 | 99.29
2019-09-07 02:30 | 118.91 | 102.54
2019-09-07 03:00 | 111.65 | 95.17
2019-09-07 03:30 | 103.65 | 85.32
2019-09-07 04:00 | 109.43 | 92.47
2019-09-07 04:30 | 113.3 | 96.7
2019-09-07 05:00 | 112.32 | 95.52
2019-09-07 05:30 | 123.81 | 108.71
2019-09-07 06:00 | 111.75 | 95.33
2019-09-07 06:30 | 104.48 | 87.88
2019-09-07 07:00 | 114.36 | 97.29
2019-09-07 07:30 | 106.74 | 86.33
2019-09-07 08:00 | 111.23 | 87.73
2019-09-07 08:30 | 109.43 | 85.39
2019-09-07 09:00 | 112.95 | 85.96
2019-09-07 09:30 | 114.97 | 84.22
2019-09-07 10:00 | 110.53 | 81.8
2019-09-07 10:30 | 103.3 | 71.95
2019-09-07 11:00 | 107.9 | 78.22
2019-09-07 11:30 | 112.43 | 81.13
2019-09-07 12:00 | 109.84 | 77.92
2019-09-07 12:30 | 115.88 | 94.02
2019-09-07 13:00 | 108.13 | 87.9
2019-09-07 13:30 | 110.22 | 82.13
2019-09-07 14:00 | 110.39 | 75.48
2019-09-07 14:30 | 110.87 | 78.2
2019-09-07 15:00 | 111.81 | 78.96
2019-09-07 15:30 | 118.1 | 87.07
2019-09-07 16:00 | 106.68 | 75.61
2019-09-07 16:30 | 113.84 | 88.18
2019-09-07 17:00 | 119.75 | 102.86
2019-09-07 17:30 | 110.5 | 92.74
2019-09-07 18:00 | 107.59 | 90.73
2019-09-07 18:30 | 106.83 | 90.93
2019-09-07 19:00 | 109.07 | 94.29
2019-09-07 19:30 | 115.85 | 100.82
2019-09-07 20:00 | 112.11 | 95.27
2019-09-07 20:30 | 114.13 | 98.63
2019-09-07 21:00 | 121.08 | 105.84
2019-09-07 21:30 | 125.87 | 111.12
2019-09-07 22:00 | 118.59 | 104.03
2019-09-07 22:30 | 112.45 | 96.26
2019-09-07 23:00 | 121.11 | 105.12
2019-09-07 23:30 | 116.88 | 100.15
2019-09-08 | 123.31 | 107.41
2019-09-08 00:30 | 116.43 | 99.53
2019-09-08 01:00 | 116.47 | 99.99
2019-09-08 01:30 | 119.4 | 103.12
2019-09-08 02:00 | 115.79 | 99.99
2019-09-08 02:30 | 118.45 | 102.94
2019-09-08 03:00 | 114.46 | 98.63
2019-09-08 03:30 | 112.24 | 95.14
2019-09-08 04:00 | 104.64 | 86.94
2019-09-08 04:30 | 115.38 | 97.21
2019-09-08 05:00 | 108.59 | 89.71
2019-09-08 05:30 | 105.55 | 86.51
2019-09-08 06:00 | 106.22 | 87.67
2019-09-08 06:30 | 102.1 | 83.62
2019-09-08 07:00 | 106.66 | 86.23
2019-09-08 07:30 | 112.82 | 90.1
2019-09-08 08:00 | 111.24 | 81.76
2019-09-08 08:30 | 104.87 | 78.49
2019-09-08 09:00 | 105.88 | 85.71
2019-09-08 09:30 | 103.97 | 65.54
2019-09-08 10:00 | 107.22 | 64.96
2019-09-08 10:30 | 110.95 | 74.84
2019-09-08 11:00 | 95.29 | 68.73
2019-09-08 11:30 | 99.46 | 81.32
2019-09-08 12:00 | 110.05 | 91.98
2019-09-08 12:30 | 117.73 | 97.76
2019-09-08 13:00 | 118.93 | 97.49
2019-09-08 13:30 | 123.73 | 100.93
2019-09-08 14:00 | 115.69 | 92.96
2019-09-08 14:30 | 114.38 | 92.59
2019-09-08 15:00 | 111.89 | 86.65
2019-09-08 15:30 | 116.52 | 84.99
2019-09-08 16:00 | 116.41 | 78.29
2019-09-08 16:30 | 115.29 | 78.75
2019-09-08 17:00 | 107.93 | 81.11
2019-09-08 17:30 | 111.91 | 90.16
2019-09-08 18:00 | 114.45 | 94.29
2019-09-08 18:30 | 109.59 | 89.83
2019-09-08 19:00 | 120.35 | 101.42
2019-09-08 19:30 | 114.61 | 95.02
2019-09-08 20:00 | 115.14 | 95.93
2019-09-08 20:30 | 121.81 | 103.38
2019-09-08 21:00 | 127.23 | 108.8
2019-09-08 21:30 | 122.55 | 103.39
2019-09-08 22:00 | 126.7 | 107.54
2019-09-08 22:30 | 125.75 | 106.54
2019-09-08 23:00 | 125.92 | 106.94
2019-09-08 23:30 | 122.52 | 103.32
2019-09-09 | 112.38 | 93.5
2019-09-09 00:30 | 114.4 | 95.32
2019-09-09 01:00 | 122.59 | 104.45
2019-09-09 01:30 | 117 | 98.37
2019-09-09 02:00 | 122.81 | 104.69
2019-09-09 02:30 | 126.4 | 107.89
2019-09-09 03:00 | 122.77 | 103.23
2019-09-09 03:30 | 120.11 | 101.12
2019-09-09 04:00 | 121.29 | 102.95
2019-09-09 04:30 | 127.65 | 109.35
2019-09-09 05:00 | 121.25 | 100.02
2019-09-09 05:30 | 114.98 | 94.29
2019-09-09 06:00 | 114.75 | 92.5
2019-09-09 06:30 | 119.65 | 99.92
2019-09-09 07:00 | 118.63 | 98.34
2019-09-09 07:30 | 120.46 | 99.97
2019-09-09 08:00 | 118.89 | 98.75
2019-09-09 08:30 | 114.74 | 97.19
2019-09-09 09:00 | 103.86 | 74.73
2019-09-09 09:30 | 116.1 | 86.23
2019-09-09 10:00 | 103.24 | 82.14
2019-09-09 10:30 | 107.29 | 91.03
2019-09-09 11:00 | 107.38 | 90.65
2019-09-09 11:30 | 99.34 | 81.8
2019-09-09 12:00 | 101.74 | 83.19
2019-09-09 12:30 | 97.12 | 77.32
2019-09-09 13:00 | 105.03 | 85.46
2019-09-09 13:30 | 111.47 | 92.82
2019-09-09 14:00 | 110.48 | 84.54
2019-09-09 14:30 | 114.03 | 88.48
2019-09-09 15:00 | 117.81 | 82.67
2019-09-09 15:30 | 107.84 | 66.01
2019-09-09 16:00 | 110.17 | 72.84
2019-09-09 16:30 | 114 | 86.92
2019-09-09 17:00 | 105.56 | 77.92
2019-09-09 17:30 | 114.13 | 94.73
2019-09-09 18:00 | 118.08 | 101.18
2019-09-09 18:30 | 112.13 | 93.93
2019-09-09 19:00 | 113.85 | 97.07
2019-09-09 19:30 | 116.59 | 98.93
2019-09-09 20:00 | 106.46 | 88.17
2019-09-09 20:30 | 110.8 | 92.57
2019-09-09 21:00 | 115.9 | 96.25
2019-09-09 21:30 | 119.84 | 99.75
2019-09-09 22:00 | 117.81 | 97.41
2019-09-09 22:30 | 120.25 | 100.85
2019-09-09 23:00 | 124.38 | 105.52
2019-09-09 23:30 | 123.21 | 102.9
2019-09-10 | 116.93 | 96.29
2019-09-10 00:30 | 126.4 | 104.66
2019-09-10 01:00 | 120.23 | 98.39
2019-09-10 01:30 | 123.85 | 102.02
2019-09-10 02:00 | 119.31 | 98.71
2019-09-10 02:30 | 122.77 | 102.46
2019-09-10 03:00 | 121.25 | 99.58
2019-09-10 03:30 | 124.44 | 103.57
2019-09-10 04:00 | 127.14 | 107.85
2019-09-10 04:30 | 120.4 | 101.08
2019-09-10 05:00 | 122.29 | 102.1
2019-09-10 05:30 | 116.85 | 96.18
2019-09-10 06:00 | 116.27 | 96.81
2019-09-10 06:30 | 117.84 | 97.9
2019-09-10 07:00 | 121.9 | 102.28
2019-09-10 07:30 | 113.04 | 95.24
2019-09-10 08:00 | 112.23 | 93.88
2019-09-10 08:30 | 104.6 | 81.75
2019-09-10 09:00 | 101.63 | 68.26
2019-09-10 09:30 | 110.81 | 83.34
2019-09-10 10:00 | 108.36 | 79.84
2019-09-10 10:30 | 113.57 | 85.51
2019-09-10 11:00 | 110.93 | 85.42
2019-09-10 11:30 | 105.11 | 76.72
2019-09-10 12:00 | 112.63 | 88.68
2019-09-10 12:30 | 107.89 | 79.76
2019-09-10 13:00 | 107.12 | 74.24
2019-09-10 13:30 | 107.11 | 71.02
2019-09-10 14:00 | 101.51 | 63.67
2019-09-10 14:30 | 102.28 | 63.86
2019-09-10 15:00 | 105.01 | 71.88
2019-09-10 15:30 | 114.83 | 90.92
2019-09-10 16:00 | 111.5 | 83.53
2019-09-10 16:30 | 110.77 | 83.56
2019-09-10 17:00 | 114.42 | 90.52
2019-09-10 17:30 | 118.77 | 97.77
2019-09-10 18:00 | 120.99 | 103.34
2019-09-10 18:30 | 120.58 | 102.56
2019-09-10 19:00 | 117.77 | 99.73
2019-09-10 19:30 | 127.83 | 111.43
2019-09-10 20:00 | 125.4 | 108.44
2019-09-10 20:30 | 127.18 | 110.82
2019-09-10 21:00 | 130.61 | 113.59
2019-09-10 21:30 | 134.99 | 118.17
2019-09-10 22:00 | 129.68 | 113.58
2019-09-10 22:30 | 126.89 | 110.04
2019-09-10 23:00 | 122.81 | 103.75
2019-09-10 23:30 | 131.55 | 116.04
2019-09-11 | 129.7 | 112.49
2019-09-11 00:30 | 122.07 | 104.95
2019-09-11 01:00 | 117.88 | 101.59
2019-09-11 01:30 | 125.21 | 107.56
2019-09-11 02:00 | 126.17 | 108.93
2019-09-11 02:30 | 122.59 | 105.4
2019-09-11 03:00 | 119.81 | 101.12
2019-09-11 03:30 | 125.45 | 106.85
2019-09-11 04:00 | 127.69 | 110.25
2019-09-11 04:30 | 126.94 | 108.6
2019-09-11 05:00 | 122.64 | 105.08
2019-09-11 05:30 | 117.15 | 98.73
2019-09-11 06:00 | 118.48 | 100.2
2019-09-11 06:30 | 122.32 | 106.28
2019-09-11 07:00 | 117.7 | 99.4
2019-09-11 07:30 | 108.99 | 84.96
2019-09-11 08:00 | 111.14 | 82.58
2019-09-11 08:30 | 107.09 | 75.45
2019-09-11 09:00 | 108.95 | 77.51
2019-09-11 09:30 | 110.75 | 80.91
2019-09-11 10:00 | 105.28 | 74.66
2019-09-11 10:30 | 104.21 | 71.64
2019-09-11 11:00 | 107.74 | 74.52
2019-09-11 11:30 | 104 | 69.39
2019-09-11 12:00 | 102.3 | 69.5
2019-09-11 12:30 | 104.3 | 73
2019-09-11 13:00 | 105.61 | 75.21
2019-09-11 13:30 | 103.34 | 70.67
2019-09-11 14:00 | 106.46 | 74.15
2019-09-11 14:30 | 109.8 | 80
2019-09-11 15:00 | 113.15 | 84.13
2019-09-11 15:30 | 107.23 | 76.27
2019-09-11 16:00 | 107.89 | 78.39
2019-09-11 16:30 | 115.95 | 89.64
2019-09-11 17:00 | 114.03 | 90.86
2019-09-11 17:30 | 120.8 | 103.39
2019-09-11 18:00 | 122.13 | 106.46
2019-09-11 18:30 | 125.47 | 110.22
2019-09-11 19:00 | 125.92 | 110.43
2019-09-11 19:30 | 126.79 | 112.92
2019-09-11 20:00 | 127.5 | 113.72
2019-09-11 20:30 | 123.07 | 106.7
2019-09-11 21:00 | 126.82 | 110.97
2019-09-11 21:30 | 121.66 | 104.26
2019-09-11 22:00 | 122.52 | 105.8
2019-09-11 22:30 | 122.5 | 105.67
2019-09-11 23:00 | 122.9 | 106.6
2019-09-11 23:30 | 127.68 | 113.07
2019-09-12 | 119.71 | 102.38
2019-09-12 00:30 | 117.08 | 98.71
2019-09-12 01:00 | 119.72 | 103.95
2019-09-12 01:30 | 116.94 | 100.62
2019-09-12 02:00 | 123.03 | 106.27
2019-09-12 02:30 | 120.05 | 103.53
2019-09-12 03:00 | 123.51 | 107.67
2019-09-12 03:30 | 121.91 | 104.56
2019-09-12 04:00 | 122.21 | 104.93
2019-09-12 04:30 | 122.47 | 104.64
2019-09-12 05:00 | 119.72 | 101.09
2019-09-12 05:30 | 125.51 | 110.08
2019-09-12 06:00 | 122.93 | 107.92
2019-09-12 06:30 | 114.37 | 95.85
2019-09-12 07:00 | 117.64 | 95.05
2019-09-12 07:30 | 118.45 | 97.24
2019-09-12 08:00 | 113.98 | 92.29
2019-09-12 08:30 | 117.23 | 96.86
2019-09-12 09:00 | 109.28 | 79.46
2019-09-12 09:30 | 111.87 | 80.96
2019-09-12 10:00 | 110.9 | 80.52
2019-09-12 10:30 | 110.07 | 79.54
2019-09-12 11:00 | 108.72 | 79.23
2019-09-12 11:30 | 109.02 | 77.34
2019-09-12 12:00 | 115.84 | 87.64
2019-09-12 12:30 | 114.37 | 81.92
2019-09-12 13:00 | 111.28 | 80.17
2019-09-12 13:30 | 104.43 | 68.93
2019-09-12 14:00 | 103.8 | 69.08
2019-09-12 14:30 | 109.04 | 78.87
2019-09-12 15:00 | 104.21 | 68.86
2019-09-12 15:30 | 103.49 | 70.07
2019-09-12 16:00 | 104.38 | 72.04
2019-09-12 16:30 | 104.47 | 74.34
2019-09-12 17:00 | 109.03 | 85.05
2019-09-12 17:30 | 110.03 | 89.73
2019-09-12 18:00 | 113.14 | 96.11
2019-09-12 18:30 | 107.28 | 89.37
2019-09-12 19:00 | 119.67 | 106.62
2019-09-12 19:30 | 118.92 | 105
2019-09-12 20:00 | 123.1 | 108.02
2019-09-12 20:30 | 121.8 | 105.95
2019-09-12 21:00 | 119.61 | 101.35
2019-09-12 21:30 | 120.96 | 103.09
2019-09-12 22:00 | 121.5 | 102.19
2019-09-12 22:30 | 126.94 | 110.05
2019-09-12 23:00 | 128.42 | 111.45
2019-09-12 23:30 | 123.7 | 105.41
2019-09-13 | 118.09 | 101.72
2019-09-13 00:30 | 120.66 | 105.4
2019-09-13 01:00 | 119.53 | 103.77
2019-09-13 01:30 | 116.12 | 98.71
2019-09-13 02:00 | 122.52 | 107.24
2019-09-13 02:30 | 117 | 99.87
2019-09-13 03:00 | 112.6 | 94
2019-09-13 03:30 | 114.31 | 94.95
2019-09-13 04:00 | 117.56 | 98.85
2019-09-13 04:30 | 119.77 | 100.71
2019-09-13 05:00 | 122.29 | 104.48
2019-09-13 05:30 | 124.12 | 107.35
2019-09-13 06:00 | 117.63 | 99.57
2019-09-13 06:30 | 115.89 | 96.77
2019-09-13 07:00 | 109.62 | 88.52
2019-09-13 07:30 | 109.37 | 86.97
2019-09-13 08:00 | 105.79 | 79.44
2019-09-13 08:30 | 104.79 | 73.58
2019-09-13 09:00 | 102.78 | 70.03
2019-09-13 09:30 | 105.69 | 74.3
2019-09-13 10:00 | 109.5 | 80.67
2019-09-13 10:30 | 103.6 | 71.85
2019-09-13 11:00 | 101.05 | 68.06
2019-09-13 11:30 | 98.79 | 65.57
2019-09-13 12:00 | 100.85 | 68.34
2019-09-13 12:30 | 108.29 | 79.01
2019-09-13 13:00 | 103.61 | 73.76
2019-09-13 13:30 | 102.33 | 71.55
2019-09-13 14:00 | 101.58 | 73.2
2019-09-13 14:30 | 95.79 | 67.21
2019-09-13 15:00 | 104.1 | 76.32
2019-09-13 15:30 | 104.41 | 76.28
2019-09-13 16:00 | 108.33 | 83.19
2019-09-13 16:30 | 107.16 | 82.86
2019-09-13 17:00 | 110.49 | 90.96
2019-09-13 17:30 | 123.76 | 109.21
2019-09-13 18:00 | 125.11 | 111.37
2019-09-13 18:30 | 107.69 | 91.1
2019-09-13 19:00 | 114.13 | 99.78
2019-09-13 19:30 | 115.47 | 99.49
2019-09-13 20:00 | 116.27 | 101
2019-09-13 20:30 | 114.78 | 99.77
2019-09-13 21:00 | 122.04 | 108.04
2019-09-13 21:30 | 118.04 | 102.91
2019-09-13 22:00 | 120.71 | 105.34
2019-09-13 22:30 | 115.95 | 100.41
2019-09-13 23:00 | 117.04 | 102.59
2019-09-13 23:30 | 116.37 | 100.62
2019-09-14 | 114.16 | 98.69
2019-09-14 00:30 | 126.68 | 112.98
2019-09-14 01:00 | 130.31 | 116.67
2019-09-14 01:30 | 118.75 | 103.16
2019-09-14 02:00 | 122.21 | 107.61
2019-09-14 02:30 | 125.38 | 111.3
2019-09-14 03:00 | 119.34 | 104.79
2019-09-14 03:30 | 121.75 | 107.25
2019-09-14 04:00 | 116.66 | 100.28
2019-09-14 04:30 | 118.57 | 102.17
2019-09-14 05:00 | 123.24 | 107.62
2019-09-14 05:30 | 125.05 | 110.96
2019-09-14 06:00 | 117.75 | 102.96
2019-09-14 06:30 | 108.33 | 91.72
2019-09-14 07:00 | 114.28 | 97.94
2019-09-14 07:30 | 115.41 | 95.41
2019-09-14 08:00 | 110.59 | 85.75
2019-09-14 08:30 | 106.04 | 79.54
2019-09-14 09:00 | 105.62 | 79.17
2019-09-14 09:30 | 106.23 | 76.48
2019-09-14 10:00 | 103.61 | 74.34
2019-09-14 10:30 | 108.06 | 80.77
2019-09-14 11:00 | 107.24 | 85.39
2019-09-14 11:30 | 107.56 | 87.78
2019-09-14 12:00 | 109.23 | 88.6
2019-09-14 12:30 | 111.71 | 91.52
2019-09-14 13:00 | 110.8 | 89.86
2019-09-14 13:30 | 114.29 | 94.6
2019-09-14 14:00 | 108.78 | 84.81
2019-09-14 14:30 | 109.03 | 82.6
2019-09-14 15:00 | 107.97 | 77.8
2019-09-14 15:30 | 97.62 | 64.39
2019-09-14 16:00 | 98.61 | 62.49
2019-09-14 16:30 | 106.41 | 79.66
2019-09-14 17:00 | 109.55 | 88.33
2019-09-14 17:30 | 112 | 91.4
2019-09-14 18:00 | 122.49 | 106.35
2019-09-14 18:30 | 115.59 | 92.76
2019-09-14 19:00 | 118.83 | 98.14
2019-09-14 19:30 | 116.44 | 93.72
2019-09-14 20:00 | 119.02 | 98.52
2019-09-14 20:30 | 120.99 | 101.93
2019-09-14 21:00 | 123.13 | 105.12
2019-09-14 21:30 | 120.06 | 98.83
2019-09-14 22:00 | 124.5 | 107.29
2019-09-14 22:30 | 122.48 | 102.26
2019-09-14 23:00 | 122.15 | 98.08
2019-09-14 23:30 | 117.43 | 92.27
2019-09-15 | 119.34 | 100.12
2019-09-15 00:30 | 115.91 | 94.77
2019-09-15 01:00 | 117.71 | 96.73
2019-09-15 01:30 | 115.66 | 96.29
2019-09-15 02:00 | 114.52 | 100.8
2019-09-15 02:30 | 114.39 | 100.12
2019-09-15 03:00 | 115.84 | 101.06
2019-09-15 03:30 | 113.91 | 98.29
2019-09-15 04:00 | 113.82 | 98.97
2019-09-15 04:30 | 113.65 | 97
2019-09-15 05:00 | 118.02 | 100.72
2019-09-15 05:30 | 126.41 | 111.59
2019-09-15 06:00 | 124.22 | 108.28
2019-09-15 06:30 | 115.36 | 96.96
2019-09-15 07:00 | 115.39 | 97.35
2019-09-15 07:30 | 105.88 | 84.62
2019-09-15 08:00 | 99.59 | 76.6
2019-09-15 08:30 | 96.15 | 70.61
2019-09-15 09:00 | 94.93 | 69.87
2019-09-15 09:30 | 106.37 | 85.48
2019-09-15 10:00 | 105.56 | 82.4
2019-09-15 10:30 | 111.05 | 90.67
2019-09-15 11:00 | 109.44 | 90.19
2019-09-15 11:30 | 111.16 | 92.9
2019-09-15 12:00 | 113.18 | 95.8
2019-09-15 12:30 | 104.62 | 82.63
2019-09-15 13:00 | 103.15 | 82.46
2019-09-15 13:30 | 107.3 | 90.29
2019-09-15 14:00 | 96.61 | 76.8
2019-09-15 14:30 | 94.41 | 66.08
2019-09-15 15:00 | 94.54 | 61.74
2019-09-15 15:30 | 101.71 | 69.35
2019-09-15 16:00 | 97.93 | 67.83
2019-09-15 16:30 | 103.09 | 77.67
2019-09-15 17:00 | 99.55 | 76.34
2019-09-15 17:30 | 105.76 | 86.88
2019-09-15 18:00 | 108.76 | 91.32
2019-09-15 18:30 | 108.4 | 90.49
2019-09-15 19:00 | 115.8 | 97.8
2019-09-15 19:30 | 114.28 | 96.39
2019-09-15 20:00 | 113.9 | 94.87
2019-09-15 20:30 | 112.47 | 93.91
2019-09-15 21:00 | 113.79 | 95.07
2019-09-15 21:30 | 116.74 | 96.64
2019-09-15 22:00 | 118.2 | 99.64
2019-09-15 22:30 | 115.62 | 96.99
2019-09-15 23:00 | 116.22 | 97.66
2019-09-15 23:30 | 115.34 | 96.52
2019-09-16 | 111.93 | 91.79
2019-09-16 00:30 | 111.75 | 93.24
2019-09-16 01:00 | 110.82 | 91.35
2019-09-16 01:30 | 110.82 | 92.5
2019-09-16 02:00 | 112.89 | 95.02
2019-09-16 02:30 | 113.34 | 95.05
2019-09-16 03:00 | 109.87 | 90.22
2019-09-16 03:30 | 113.86 | 95.71
2019-09-16 04:00 | 105.84 | 89.07
2019-09-16 04:30 | 106.55 | 90.23
2019-09-16 05:00 | 111.02 | 96.46
2019-09-16 05:30 | 101.54 | 84.48
2019-09-16 06:00 | 104.18 | 87.44
2019-09-16 06:30 | 102.75 | 84.69
2019-09-16 07:00 | 95.55 | 77.74
2019-09-16 07:30 | 101.97 | 84.83
2019-09-16 08:00 | 99.77 | 83.63
2019-09-16 08:30 | 98.56 | 72.54
2019-09-16 09:00 | 97.29 | 66.17
2019-09-16 09:30 | 91.85 | 59.34
2019-09-16 10:00 | 98.01 | 67.03
2019-09-16 10:30 | 98.73 | 67.86
2019-09-16 11:00 | 94.11 | 61.98
2019-09-16 11:30 | 93.9 | 61.53
2019-09-16 12:00 | 94.27 | 65.64
2019-09-16 12:30 | 94.02 | 65
2019-09-16 13:00 | 95.3 | 64.12
2019-09-16 13:30 | 100.61 | 68.94
2019-09-16 14:00 | 100.09 | 68.44
2019-09-16 14:30 | 99.84 | 66.84
2019-09-16 15:00 | 101.94 | 67.98
2019-09-16 15:30 | 101.89 | 68.01
2019-09-16 16:00 | 100.68 | 68.33
2019-09-16 16:30 | 110.61 | 86.15
2019-09-16 17:00 | 113 | 93.36
2019-09-16 17:30 | 120.2 | 105.42
2019-09-16 18:00 | 120.42 | 106.42
2019-09-16 18:30 | 107.08 | 88.9
2019-09-16 19:00 | 114.98 | 98.74
2019-09-16 19:30 | 110.49 | 92.78
2019-09-16 20:00 | 116.32 | 100.81
2019-09-16 20:30 | 117.75 | 101.25
2019-09-16 21:00 | 119.47 | 102.66
2019-09-16 21:30 | 117.79 | 101.25
2019-09-16 22:00 | 117.21 | 99.76
2019-09-16 22:30 | 118.24 | 101.06
2019-09-16 23:00 | 109.61 | 89.17
2019-09-16 23:30 | 107.59 | 88.35
2019-09-17 | 107.11 | 86.43
2019-09-17 00:30 | 110.31 | 91.11
2019-09-17 01:00 | 111.78 | 94.64
2019-09-17 01:30 | 104.52 | 86
2019-09-17 02:00 | 104.56 | 86.35
2019-09-17 02:30 | 104.15 | 85.16
2019-09-17 03:00 | 101.26 | 80.09
2019-09-17 03:30 | 100.15 | 78.64
2019-09-17 04:00 | 102.26 | 82.6
2019-09-17 04:30 | 103.58 | 83.11
2019-09-17 05:00 | 103.25 | 82.19
2019-09-17 05:30 | 94.09 | 84.76
2019-09-17 06:00 | 81.56 | 80
2019-09-17 06:30 | 68.35 | 66.39
2019-09-17 07:00 | 70.79 | 68.9
2019-09-17 07:30 | 64.03 | 62.03
2019-09-17 08:00 | 67.48 | 65.3
2019-09-17 08:30 | 69.38 | 67
2019-09-17 09:00 | 56.48 | 53.47
2019-09-17 09:30 | 48.87 | 42.1
2019-09-17 10:00 | 53.77 | 44.8
2019-09-17 10:30 | 54.03 | 43.05
2019-09-17 11:00 | 53.41 | 42.16
2019-09-17 11:30 | 52.91 | 41.44
2019-09-17 12:00 | 53.11 | 42.76
2019-09-17 12:30 | 53.94 | 45.38
2019-09-17 13:00 | 56.18 | 48.09
2019-09-17 13:30 | 51.63 | 42.18
2019-09-17 14:00 | 61.47 | 57.85
2019-09-17 14:30 | 70.7 | 67.44
2019-09-17 15:00 | 67.2 | 65.29
2019-09-17 15:30 | 64.05 | 62.26
2019-09-17 16:00 | 70.84 | 69.02
2019-09-17 16:30 | 70.64 | 69.03
2019-09-17 17:00 | 74.68 | 72.91
2019-09-17 17:30 | 77.42 | 75.76
2019-09-17 18:00 | 77.53 | 75.8
2019-09-17 18:30 | 66.34 | 64.22
2019-09-17 19:00 | 73.65 | 71.13
2019-09-17 19:30 | 74.36 | 72.04
2019-09-17 20:00 | 71.28 | 69.65
2019-09-17 20:30 | 72.62 | 71.25
2019-09-17 21:00 | 76.15 | 74.78
2019-09-17 21:30 | 75.21 | 73.74
2019-09-17 22:00 | 74.11 | 72.68
2019-09-17 22:30 | 73.4 | 72.06
2019-09-17 23:00 | 71.89 | 70.29
2019-09-17 23:30 | 70.65 | 68.89
2019-09-18 | 70.81 | 68.97
2019-09-18 00:30 | 72.31 | 70.63
2019-09-18 01:00 | 71.63 | 69.74
2019-09-18 01:30 | 71.38 | 69.24
2019-09-18 02:00 | 67.56 | 65.48
2019-09-18 02:30 | 60.65 | 58.62
2019-09-18 03:00 | 64.95 | 62.72
2019-09-18 03:30 | 61.89 | 59.74
2019-09-18 04:00 | 60.49 | 58.49
2019-09-18 04:30 | 57.15 | 55.3
2019-09-18 05:00 | 59.67 | 57.35
2019-09-18 05:30 | 57.35 | 55.03
2019-09-18 06:00 | 56.28 | 53.57
2019-09-18 06:30 | 46.48 | 43.43
2019-09-18 07:00 | 51.42 | 48.98
2019-09-18 07:30 | 52.18 | 49.77
2019-09-18 08:00 | 58.5 | 55.55
2019-09-18 08:30 | 52.41 | 49.69
2019-09-18 09:00 | 37.17 | 27.3
2019-09-18 09:30 | 38.64 | 26.88
2019-09-18 10:00 | 40.35 | 29.98
2019-09-18 10:30 | 43.88 | 39.98
2019-09-18 11:00 | 40.86 | 37.36
2019-09-18 11:30 | 37.72 | 27.27
2019-09-18 12:00 | 38.04 | 30.48
2019-09-18 12:30 | 38.05 | 32.58
2019-09-18 13:00 | 39.46 | 30.67
2019-09-18 13:30 | 39.63 | 30.52
2019-09-18 14:00 | 40.74 | 31.22
2019-09-18 14:30 | 40.88 | 36.15
2019-09-18 15:00 | 55.82 | 53.15
2019-09-18 15:30 | 58.6 | 55.84
2019-09-18 16:00 | 56.14 | 53.12
2019-09-18 16:30 | 55.44 | 52.14
2019-09-18 17:00 | 59.02 | 55.83
2019-09-18 17:30 | 63.3 | 60.33
2019-09-18 18:00 | 66.06 | 63.24
2019-09-18 18:30 | 59.85 | 57.26
2019-09-18 19:00 | 69.07 | 66.6
2019-09-18 19:30 | 70.31 | 67.84
2019-09-18 20:00 | 77.62 | 74.83
2019-09-18 20:30 | 77.82 | 75.43
2019-09-18 21:00 | 74.57 | 72.38
2019-09-18 21:30 | 71.48 | 69.56
2019-09-18 22:00 | 69.74 | 67.87
2019-09-18 22:30 | 69.69 | 67.79
2019-09-18 23:00 | 70.14 | 68.18
2019-09-18 23:30 | 67.35 | 65.21
2019-09-19 | 67.04 | 64.95
2019-09-19 00:30 | 70.24 | 68.24
2019-09-19 01:00 | 68.27 | 65.98
2019-09-19 01:30 | 70.82 | 68.51
2019-09-19 02:00 | 75.97 | 73.46
2019-09-19 02:30 | 66.47 | 64.08
2019-09-19 03:00 | 71.85 | 69.26
2019-09-19 03:30 | 68.73 | 66.41
2019-09-19 04:00 | 67.65 | 65.5
2019-09-19 04:30 | 69.44 | 67.14
2019-09-19 05:00 | 68.11 | 65.86
2019-09-19 05:30 | 68.59 | 66.82
2019-09-19 06:00 | 73.4 | 71.56
2019-09-19 06:30 | 57.08 | 55.54
2019-09-19 07:00 | 74.05 | 72.4
2019-09-19 07:30 | 67.87 | 66.27
2019-09-19 08:00 | 68.4 | 66.81
2019-09-19 08:30 | 69.13 | 67.26
2019-09-19 09:00 | 67.48 | 65.69
2019-09-19 09:30 | 70.84 | 68.76
2019-09-19 10:00 | 71.06 | 69.01
2019-09-19 10:30 | 70.53 | 68.18
2019-09-19 11:00 | 78.74 | 75.83
2019-09-19 11:30 | 75.12 | 72.43
2019-09-19 12:00 | 66.02 | 57.81
2019-09-19 12:30 | 58.07 | 49.42
2019-09-19 13:00 | 64.38 | 53.76
2019-09-19 13:30 | 63.23 | 50.7
2019-09-19 14:00 | 63.43 | 50.98
2019-09-19 14:30 | 61.79 | 50.68
2019-09-19 15:00 | 74.58 | 70.49
2019-09-19 15:30 | 75.6 | 73.1
2019-09-19 16:00 | 81.27 | 77.3
2019-09-19 16:30 | 89.34 | 85.54
2019-09-19 17:00 | 84.1 | 78.13
2019-09-19 17:30 | 88.1 | 81.89
2019-09-19 18:00 | 89.29 | 84.27
2019-09-19 18:30 | 85.65 | 79.87
2019-09-19 19:00 | 97.11 | 91.41
2019-09-19 19:30 | 104.34 | 98.41
2019-09-19 20:00 | 107.2 | 101.04
2019-09-19 20:30 | 96.17 | 89.94
2019-09-19 21:00 | 94.32 | 88.98
2019-09-19 21:30 | 101.34 | 96.04
2019-09-19 22:00 | 96.54 | 91.23
2019-09-19 22:30 | 98.04 | 91.64
2019-09-19 23:00 | 98.2 | 91.94
2019-09-19 23:30 | 96.46 | 90.18
2019-09-20 | 102.08 | 96.57
2019-09-20 00:30 | 98.44 | 90.94
2019-09-20 01:00 | 107.19 | 98.75
2019-09-20 01:30 | 109.57 | 100.94
2019-09-20 02:00 | 108.44 | 99.71
2019-09-20 02:30 | 94.76 | 85.25
2019-09-20 03:00 | 97.01 | 87.25
2019-09-20 03:30 | 90.28 | 80.29
2019-09-20 04:00 | 94.3 | 84.56
2019-09-20 04:30 | 100.93 | 91.54
2019-09-20 05:00 | 97.35 | 87.76
2019-09-20 05:30 | 99.93 | 90.22
2019-09-20 06:00 | 96.84 | 87.92
2019-09-20 06:30 | 92.98 | 83.68
2019-09-20 07:00 | 90.75 | 81.91
2019-09-20 07:30 | 101.3 | 92.31
2019-09-20 08:00 | 107.56 | 98.44
2019-09-20 08:30 | 113.19 | 103.08
2019-09-20 09:00 | 89.28 | 81.15
2019-09-20 09:30 | 89.27 | 76.84
2019-09-20 10:00 | 89.32 | 76.12
2019-09-20 10:30 | 94.81 | 76.35
2019-09-20 11:00 | 90.27 | 65.62
2019-09-20 11:30 | 89.35 | 63.26
2019-09-20 12:00 | 93.84 | 71.04
2019-09-20 12:30 | 95.67 | 73.49
2019-09-20 13:00 | 98.75 | 77.62
2019-09-20 13:30 | 91.56 | 69.89
2019-09-20 14:00 | 96.45 | 79.66
2019-09-20 14:30 | 94.43 | 79.86
2019-09-20 15:00 | 91.87 | 72.95
2019-09-20 15:30 | 91.32 | 72.97
2019-09-20 16:00 | 99.14 | 88.3
2019-09-20 16:30 | 104.11 | 96.89
2019-09-20 17:00 | 104.46 | 97.19
2019-09-20 17:30 | 105.03 | 97.93
2019-09-20 18:00 | 110.91 | 103.92
2019-09-20 18:30 | 105.24 | 97.78
2019-09-20 19:00 | 106.54 | 99.08
2019-09-20 19:30 | 107.43 | 99.92
2019-09-20 20:00 | 112.86 | 106.39
2019-09-20 20:30 | 108.67 | 101.13
2019-09-20 21:00 | 106.78 | 99.11
2019-09-20 21:30 | 104.57 | 97.11
2019-09-20 22:00 | 96.1 | 89.11
2019-09-20 22:30 | 95.75 | 88.48
2019-09-20 23:00 | 98.28 | 91.47
2019-09-20 23:30 | 103.96 | 96.94
2019-09-21 | 100.22 | 92.98
2019-09-21 00:30 | 95.36 | 86.45
2019-09-21 01:00 | 99.65 | 90.66
2019-09-21 01:30 | 99.66 | 91.03
2019-09-21 02:00 | 103.16 | 94.79
2019-09-21 02:30 | 105.81 | 97.88
2019-09-21 03:00 | 96.08 | 86.94
2019-09-21 03:30 | 95.58 | 86.95
2019-09-21 04:00 | 99.24 | 90.89
2019-09-21 04:30 | 102.79 | 94.37
2019-09-21 05:00 | 112.43 | 103.64
2019-09-21 05:30 | 108.22 | 98.35
2019-09-21 06:00 | 100.73 | 91.44
2019-09-21 06:30 | 96.44 | 86.49
2019-09-21 07:00 | 99.06 | 86.72
2019-09-21 07:30 | 97.76 | 80.34
2019-09-21 08:00 | 93.18 | 71.09
2019-09-21 08:30 | 95.2 | 72.32
2019-09-21 09:00 | 95.38 | 72.14
2019-09-21 09:30 | 93.85 | 71.11
2019-09-21 10:00 | 89.24 | 67.18
2019-09-21 10:30 | 94.73 | 73.19
2019-09-21 11:00 | 96.73 | 76.71
2019-09-21 11:30 | 93.12 | 66.42
2019-09-21 12:00 | 96.03 | 74.3
2019-09-21 12:30 | 100.09 | 85.19
2019-09-21 13:00 | 100.44 | 83.21
2019-09-21 13:30 | 94.6 | 74.76
2019-09-21 14:00 | 101.73 | 83.21
2019-09-21 14:30 | 100.8 | 79.36
2019-09-21 15:00 | 94.29 | 70.76
2019-09-21 15:30 | 89.86 | 65.19
2019-09-21 16:00 | 90.63 | 66.95
2019-09-21 16:30 | 95.06 | 75.47
2019-09-21 17:00 | 96.01 | 80.79
2019-09-21 17:30 | 99.88 | 90.09
2019-09-21 18:00 | 101.58 | 94.9
2019-09-21 18:30 | 95.83 | 89.72
2019-09-21 19:00 | 105.48 | 98.69
2019-09-21 19:30 | 102.38 | 94.27
2019-09-21 20:00 | 103.43 | 95.99
2019-09-21 20:30 | 106.52 | 99.49
2019-09-21 21:00 | 106.38 | 99.57
2019-09-21 21:30 | 104.04 | 97.22
2019-09-21 22:00 | 103.42 | 97.03
2019-09-21 22:30 | 105.44 | 99.4
2019-09-21 23:00 | 102.48 | 97.17
2019-09-21 23:30 | 103.28 | 97.57
2019-09-22 | 106.81 | 101.54
2019-09-22 00:30 | 105.25 | 100.1
2019-09-22 01:00 | 91.39 | 85.92
2019-09-22 01:30 | 88.62 | 82.72
2019-09-22 02:00 | 97.32 | 91.48
2019-09-22 02:30 | 100.14 | 94.79
2019-09-22 03:00 | 100.77 | 94.08
2019-09-22 03:30 | 104.97 | 98.8
2019-09-22 04:00 | 99.83 | 92.71
2019-09-22 04:30 | 103.22 | 96.42
2019-09-22 05:00 | 101.59 | 94.76
2019-09-22 05:30 | 96.07 | 88.87
2019-09-22 06:00 | 98.07 | 90.96
2019-09-22 06:30 | 93.83 | 86.09
2019-09-22 07:00 | 94.26 | 84.72
2019-09-22 07:30 | 88.2 | 74.08
2019-09-22 08:00 | 91.95 | 75.01
2019-09-22 08:30 | 89.55 | 68.88
2019-09-22 09:00 | 84.35 | 63.89
2019-09-22 09:30 | 92.19 | 73.39
2019-09-22 10:00 | 92.2 | 74.05
2019-09-22 10:30 | 80.34 | 63.78
2019-09-22 11:00 | 89.08 | 71.16
2019-09-22 11:30 | 85.21 | 70.47
2019-09-22 12:00 | 83.56 | 69.09
2019-09-22 12:30 | 83.33 | 70.08
2019-09-22 13:00 | 90.65 | 73.21
2019-09-22 13:30 | 94.48 | 75.02
2019-09-22 14:00 | 96.69 | 81.22
2019-09-22 14:30 | 93.74 | 74.65
2019-09-22 15:00 | 88.26 | 68.99
2019-09-22 15:30 | 94.3 | 74.45
2019-09-22 16:00 | 105.08 | 86.4
2019-09-22 16:30 | 105.1 | 97.61
2019-09-22 17:00 | 100.62 | 88.36
2019-09-22 17:30 | 108.7 | 99.45
2019-09-22 18:00 | 113.24 | 105.78
2019-09-22 18:30 | 104.93 | 98.39
2019-09-22 19:00 | 108.85 | 103.01
2019-09-22 19:30 | 112.51 | 105.44
2019-09-22 20:00 | 105.12 | 98.55
2019-09-22 20:30 | 105.48 | 98.35
2019-09-22 21:00 | 109.41 | 101.52
2019-09-22 21:30 | 113.1 | 105.66
2019-09-22 22:00 | 115.51 | 108.63
2019-09-22 22:30 | 118.84 | 112.54
2019-09-22 23:00 | 112.39 | 105.82
2019-09-22 23:30 | 111.56 | 104.51
2019-09-23 | 107.28 | 100.99
2019-09-23 00:30 | 95.52 | 89.48
2019-09-23 01:00 | 100.41 | 93.73
2019-09-23 01:30 | 96.75 | 90.56
2019-09-23 02:00 | 98.54 | 92.88
2019-09-23 02:30 | 101.48 | 96.02
2019-09-23 03:00 | 101.02 | 95.38
2019-09-23 03:30 | 108.71 | 102.93
2019-09-23 04:00 | 98.1 | 92.09
2019-09-23 04:30 | 99.88 | 93.78
2019-09-23 05:00 | 101.96 | 96.44
2019-09-23 05:30 | 110.44 | 104.98
2019-09-23 06:00 | 106.99 | 102.43
2019-09-23 06:30 | 89.33 | 83.08
2019-09-23 07:00 | 100.99 | 94.14
2019-09-23 07:30 | 99.62 | 92.17
2019-09-23 08:00 | 92.51 | 84.85
2019-09-23 08:30 | 93.14 | 83.67
2019-09-23 09:00 | 96.86 | 79.86
2019-09-23 09:30 | 89.31 | 71.42
2019-09-23 10:00 | 90.67 | 68.33
2019-09-23 10:30 | 89.59 | 66.8
2019-09-23 11:00 | 87.01 | 63.03
2019-09-23 11:30 | 90.04 | 63.55
2019-09-23 12:00 | 96.98 | 74.5
2019-09-23 12:30 | 90.26 | 64.74
2019-09-23 13:00 | 99.64 | 73.94
2019-09-23 13:30 | 99.76 | 74.3
2019-09-23 14:00 | 100.92 | 76.68
2019-09-23 14:30 | 93.81 | 72.49
2019-09-23 15:00 | 95.28 | 83.54
2019-09-23 15:30 | 98.81 | 89.82
2019-09-23 16:00 | 105.49 | 97.34
2019-09-23 16:30 | 113.82 | 105.11
2019-09-23 17:00 | 114.15 | 105.76
2019-09-23 17:30 | 108.94 | 101.25
2019-09-23 18:00 | 104.82 | 97.68
2019-09-23 18:30 | 94.62 | 86.01
2019-09-23 19:00 | 104.07 | 95.97
2019-09-23 19:30 | 114.92 | 107.54
2019-09-23 20:00 | 105.86 | 98.92
2019-09-23 20:30 | 111.38 | 104.48
2019-09-23 21:00 | 113.27 | 105.78
2019-09-23 21:30 | 105.57 | 98.21
2019-09-23 22:00 | 108.6 | 101.63
2019-09-23 22:30 | 114.11 | 106.9
2019-09-23 23:00 | 109.56 | 102.45
2019-09-23 23:30 | 111.59 | 105.08
2019-09-24 | 116.18 | 107.05
2019-09-24 00:30 | 120.46 | 109.52
2019-09-24 01:00 | 113.7 | 102.68
2019-09-24 01:30 | 119.88 | 108.67
2019-09-24 02:00 | 115.36 | 104.1
2019-09-24 02:30 | 110.15 | 98.73
2019-09-24 03:00 | 113.88 | 102.38
2019-09-24 03:30 | 110.87 | 99.05
2019-09-24 04:00 | 111.7 | 99.65
2019-09-24 04:30 | 110.16 | 98.91
2019-09-24 05:00 | 115.02 | 103.81
2019-09-24 05:30 | 117.88 | 106.42
2019-09-24 06:00 | 111.22 | 99.91
2019-09-24 06:30 | 99.62 | 87.52
2019-09-24 07:00 | 105.08 | 92.94
2019-09-24 07:30 | 106.57 | 90.65
2019-09-24 08:00 | 94.65 | 84.73
2019-09-24 08:30 | 86.08 | 77.11
2019-09-24 09:00 | 93.4 | 86.12
2019-09-24 09:30 | 95.83 | 87.69
2019-09-24 10:00 | 93.82 | 85.38
2019-09-24 10:30 | 92.91 | 84.04
2019-09-24 11:00 | 98.97 | 88.27
2019-09-24 11:30 | 94.71 | 74.24
2019-09-24 12:00 | 87.98 | 73.16
2019-09-24 12:30 | 91.39 | 71.67
2019-09-24 13:00 | 103.94 | 82.62
2019-09-24 13:30 | 104.79 | 80.7
2019-09-24 14:00 | 107.87 | 83.47
2019-09-24 14:30 | 99.3 | 76.59
2019-09-24 15:00 | 99.34 | 85.11
2019-09-24 15:30 | 112.11 | 102.17
2019-09-24 16:00 | 111.17 | 102.19
2019-09-24 16:30 | 108.93 | 99.69
2019-09-24 17:00 | 106.26 | 98.51
2019-09-24 17:30 | 102.93 | 95.86
2019-09-24 18:00 | 114.95 | 106.54
2019-09-24 18:30 | 109.16 | 100.77
2019-09-24 19:00 | 115.17 | 107.91
2019-09-24 19:30 | 118.92 | 111.33
2019-09-24 20:00 | 112.93 | 105.61
2019-09-24 20:30 | 122.58 | 114.2
2019-09-24 21:00 | 112.67 | 104.81
2019-09-24 21:30 | 119.8 | 112.2
2019-09-24 22:00 | 120.41 | 112.42
2019-09-24 22:30 | 111.26 | 102.42
2019-09-24 23:00 | 111.53 | 102.65
2019-09-24 23:30 | 109.34 | 100.67
2019-09-25 | 113.51 | 104.24
2019-09-25 00:30 | 119.19 | 108.12
2019-09-25 01:00 | 114.78 | 103.84
2019-09-25 01:30 | 116.71 | 106.08
2019-09-25 02:00 | 116.38 | 107.58
2019-09-25 02:30 | 106.55 | 99.24
2019-09-25 03:00 | 107.83 | 99.93
2019-09-25 03:30 | 108.8 | 101.67
2019-09-25 04:00 | 109.76 | 102.31
2019-09-25 04:30 | 105.2 | 96.7
2019-09-25 05:00 | 99.67 | 90.73
2019-09-25 05:30 | 103.59 | 96.04
2019-09-25 06:00 | 104.49 | 97.76
2019-09-25 06:30 | 101.37 | 93.23
2019-09-25 07:00 | 96.25 | 89.07
2019-09-25 07:30 | 95.48 | 88.72
2019-09-25 08:00 | 102.58 | 95.18
2019-09-25 08:30 | 96.66 | 89.14
2019-09-25 09:00 | 95.25 | 86.7
2019-09-25 09:30 | 95.85 | 88.24
2019-09-25 10:00 | 86.27 | 79.65
2019-09-25 10:30 | 87.59 | 80.27
2019-09-25 11:00 | 91.45 | 84.41
2019-09-25 11:30 | 101.64 | 93.93
2019-09-25 12:00 | 95.65 | 84.2
2019-09-25 12:30 | 102.87 | 95.1
2019-09-25 13:00 | 93.33 | 87.36
2019-09-25 13:30 | 96.57 | 90.77
2019-09-25 14:00 | 95.63 | 88.92
2019-09-25 14:30 | 100.97 | 95.06
2019-09-25 15:00 | 103.43 | 97.79
2019-09-25 15:30 | 103.94 | 97.86
2019-09-25 16:00 | 106.37 | 100.11
2019-09-25 16:30 | 104.45 | 98.58
2019-09-25 17:00 | 102.65 | 96.96
2019-09-25 17:30 | 109.12 | 103.93
2019-09-25 18:00 | 113.28 | 107.95
2019-09-25 18:30 | 98.39 | 93.98
2019-09-25 19:00 | 117.95 | 113.84
2019-09-25 19:30 | 118.28 | 113.81
2019-09-25 20:00 | 114.72 | 110.41
2019-09-25 20:30 | 115.2 | 110.98
2019-09-25 21:00 | 117.64 | 113.43
2019-09-25 21:30 | 107.97 | 103.51
2019-09-25 22:00 | 112.49 | 108.17
2019-09-25 22:30 | 111.82 | 107.86
2019-09-25 23:00 | 111.83 | 107.35
2019-09-25 23:30 | 93.12 | 88.58
2019-09-26 | 92.76 | 87.81
2019-09-26 00:30 | 108.05 | 103.51
2019-09-26 01:00 | 104.48 | 100.01
2019-09-26 01:30 | 104.85 | 100.12
2019-09-26 02:00 | 102.79 | 97.95
2019-09-26 02:30 | 101.96 | 96.99
2019-09-26 03:00 | 91.99 | 86.76
2019-09-26 03:30 | 98.51 | 91.75
2019-09-26 04:00 | 109.37 | 101.81
2019-09-26 04:30 | 112.05 | 104.42
2019-09-26 05:00 | 111.13 | 103.29
2019-09-26 05:30 | 105.52 | 97.93
2019-09-26 06:00 | 102.83 | 95.37
2019-09-26 06:30 | 93.77 | 86.15
2019-09-26 07:00 | 97.66 | 89.7
2019-09-26 07:30 | 100.96 | 93.27
2019-09-26 08:00 | 104.96 | 97.29
2019-09-26 08:30 | 104.2 | 96.7
2019-09-26 09:00 | 99.96 | 92.7
2019-09-26 09:30 | 102.54 | 95.42
2019-09-26 10:00 | 109.84 | 102.79
2019-09-26 10:30 | 101.78 | 94.48
2019-09-26 11:00 | 88.98 | 81.81
2019-09-26 11:30 | 94.33 | 87.2
2019-09-26 12:00 | 92.07 | 84.84
2019-09-26 12:30 | 94.41 | 86.92
2019-09-26 13:00 | 104.49 | 94.14
2019-09-26 13:30 | 93.28 | 80.21
2019-09-26 14:00 | 102.55 | 89.43
2019-09-26 14:30 | 111.13 | 101.55
2019-09-26 15:00 | 111.65 | 103.61
2019-09-26 15:30 | 111.57 | 102.16
2019-09-26 16:00 | 101.08 | 91.71
2019-09-26 16:30 | 113.15 | 103.83
2019-09-26 17:00 | 110.29 | 100.13
2019-09-26 17:30 | 104.96 | 95.36
2019-09-26 18:00 | 116.02 | 106.03
2019-09-26 18:30 | 105.37 | 94.65
2019-09-26 19:00 | 105.27 | 95.54
2019-09-26 19:30 | 114.74 | 105.35
2019-09-26 20:00 | 115.81 | 106.13
2019-09-26 20:30 | 104.32 | 95.83
2019-09-26 21:00 | 104.74 | 96.48
2019-09-26 21:30 | 104.19 | 96.87
2019-09-26 22:00 | 106.71 | 99.14
2019-09-26 22:30 | 108.45 | 100.78
2019-09-26 23:00 | 102.71 | 93.89
2019-09-26 23:30 | 108.51 | 100.38
2019-09-27 | 107.71 | 99.83
2019-09-27 00:30 | 115.74 | 107.49
2019-09-27 01:00 | 110.26 | 101.74
2019-09-27 01:30 | 113.05 | 105.12
2019-09-27 02:00 | 102.2 | 94.23
2019-09-27 02:30 | 104.99 | 96.54
2019-09-27 03:00 | 104.85 | 95.87
2019-09-27 03:30 | 103.68 | 95.43
2019-09-27 04:00 | 109.6 | 101.45
2019-09-27 04:30 | 112.8 | 104.34
2019-09-27 05:00 | 114.73 | 105.6
2019-09-27 05:30 | 113.12 | 104.58
2019-09-27 06:00 | 114.8 | 106.37
2019-09-27 06:30 | 103.75 | 94.21
2019-09-27 07:00 | 111.61 | 103.34
2019-09-27 07:30 | 107.4 | 98.83
2019-09-27 08:00 | 108.91 | 98.76
2019-09-27 08:30 | 108.42 | 97.64
2019-09-27 09:00 | 99.33 | 88.37
2019-09-27 09:30 | 98.48 | 81.26
2019-09-27 10:00 | 96.2 | 72.78
2019-09-27 10:30 | 99.81 | 74.44
2019-09-27 11:00 | 99.09 | 75.12
2019-09-27 11:30 | 98.17 | 77.69
2019-09-27 12:00 | 100.41 | 74.7
2019-09-27 12:30 | 92.77 | 73.67
2019-09-27 13:00 | 91.44 | 73.75
2019-09-27 13:30 | 88.42 | 78.18
2019-09-27 14:00 | 88.72 | 79.33
2019-09-27 14:30 | 90.08 | 82.17
2019-09-27 15:00 | 88.69 | 80.39
2019-09-27 15:30 | 90.7 | 82.61
2019-09-27 16:00 | 97.74 | 90.29
2019-09-27 16:30 | 103.02 | 95.32
2019-09-27 17:00 | 108.51 | 100.91
2019-09-27 17:30 | 116.63 | 108.92
2019-09-27 18:00 | 99.77 | 91.14
2019-09-27 18:30 | 95.58 | 85.93
2019-09-27 19:00 | 104.23 | 94.48
2019-09-27 19:30 | 103.14 | 92.36
2019-09-27 20:00 | 116.56 | 106.14
2019-09-27 20:30 | 109.23 | 99.87
2019-09-27 21:00 | 111.21 | 100.88
2019-09-27 21:30 | 104.37 | 94.78
2019-09-27 22:00 | 117.34 | 108.13
2019-09-27 22:30 | 113.02 | 103.78
2019-09-27 23:00 | 116.13 | 106.71
2019-09-27 23:30 | 104.48 | 93.99
2019-09-28 | 107.97 | 97.74
2019-09-28 00:30 | 111.59 | 100.35
2019-09-28 01:00 | 104.32 | 92.83
2019-09-28 01:30 | 109.63 | 98.92
2019-09-28 02:00 | 110.55 | 98.97
2019-09-28 02:30 | 114.59 | 104.14
2019-09-28 03:00 | 108.03 | 96.71
2019-09-28 03:30 | 113.51 | 102.65
2019-09-28 04:00 | 121.36 | 111.67
2019-09-28 04:30 | 106.74 | 97.26
2019-09-28 05:00 | 109.75 | 100.63
2019-09-28 05:30 | 102.24 | 93.42
2019-09-28 06:00 | 99.77 | 92
2019-09-28 06:30 | 95.42 | 87.3
2019-09-28 07:00 | 87.11 | 78.72
2019-09-28 07:30 | 87.83 | 76.25
2019-09-28 08:00 | 89 | 72.69
2019-09-28 08:30 | 100.08 | 84.6
2019-09-28 09:00 | 101.8 | 83.76
2019-09-28 09:30 | 88.1 | 68.66
2019-09-28 10:00 | 98.73 | 77.5
2019-09-28 10:30 | 97.51 | 79.71
2019-09-28 11:00 | 88.63 | 70.47
2019-09-28 11:30 | 104.89 | 85.59
2019-09-28 12:00 | 105.26 | 82.61
2019-09-28 12:30 | 106.11 | 86.61
2019-09-28 13:00 | 98.45 | 73.19
2019-09-28 13:30 | 97.86 | 73.55
2019-09-28 14:00 | 103.07 | 79.49
2019-09-28 14:30 | 89.81 | 61.8
2019-09-28 15:00 | 84.5 | 62.43
2019-09-28 15:30 | 103.07 | 93.09
2019-09-28 16:00 | 105.29 | 96.41
2019-09-28 16:30 | 102.89 | 93.36
2019-09-28 17:00 | 106.65 | 96.97
2019-09-28 17:30 | 103.12 | 92.42
2019-09-28 18:00 | 106.61 | 98.44
2019-09-28 18:30 | 103.13 | 94.01
2019-09-28 19:00 | 111.95 | 103.38
2019-09-28 19:30 | 110.46 | 101.11
2019-09-28 20:00 | 113.68 | 103.71
2019-09-28 20:30 | 112.1 | 100.57
2019-09-28 21:00 | 108.68 | 97.75
2019-09-28 21:30 | 112.4 | 102.44
2019-09-28 22:00 | 122.51 | 112.91
2019-09-28 22:30 | 112.86 | 103.5
2019-09-28 23:00 | 109.11 | 100.55
2019-09-28 23:30 | 112.63 | 103.91
2019-09-29 | 108.41 | 99.44
2019-09-29 00:30 | 108.71 | 100.04
2019-09-29 01:00 | 108.24 | 99.24
2019-09-29 01:30 | 105.81 | 96.53
2019-09-29 02:00 | 112.19 | 103.87
2019-09-29 02:30 | 108.98 | 104.23
2019-09-29 03:00 | 105.34 | 100.29
2019-09-29 03:30 | 97.71 | 92.93
2019-09-29 04:00 | 99.86 | 95.29
2019-09-29 04:30 | 93.92 | 90.06
2019-09-29 05:00 | 95.37 | 91.41
2019-09-29 05:30 | 101.28 | 97.58
2019-09-29 06:00 | 99.71 | 96.38
2019-09-29 06:30 | 86.51 | 82.44
2019-09-29 07:00 | 90.02 | 84.87
2019-09-29 07:30 | 96.86 | 90.7
2019-09-29 08:00 | 91.3 | 84.88
2019-09-29 08:30 | 82.19 | 73.02
2019-09-29 09:00 | 88.95 | 84.08
2019-09-29 09:30 | 81.84 | 72.86
2019-09-29 10:00 | 77.11 | 63.22
2019-09-29 10:30 | 87.72 | 77.5
2019-09-29 11:00 | 97.9 | 93.85
2019-09-29 11:30 | 101.75 | 98.28
2019-09-29 12:00 | 95.85 | 91.69
2019-09-29 12:30 | 99.78 | 95.59
2019-09-29 13:00 | 104.84 | 100.4
2019-09-29 13:30 | 100.22 | 96.02
2019-09-29 14:00 | 108.64 | 104.8
2019-09-29 14:30 | 96.41 | 91.49
2019-09-29 15:00 | 98.51 | 92.02
2019-09-29 15:30 | 98.3 | 89.03
2019-09-29 16:00 | 87.27 | 75.49
2019-09-29 16:30 | 104.92 | 100.82
2019-09-29 17:00 | 113.81 | 110.57
2019-09-29 17:30 | 103.29 | 100.05
2019-09-29 18:00 | 110.22 | 106.74
2019-09-29 18:30 | 101.56 | 98.09
2019-09-29 19:00 | 110.17 | 106.34
2019-09-29 19:30 | 100.93 | 97.56
2019-09-29 20:00 | 102.48 | 99.35
2019-09-29 20:30 | 105.01 | 101.97
2019-09-29 21:00 | 100.19 | 96.87
2019-09-29 21:30 | 97.62 | 94.26
2019-09-29 22:00 | 111.66 | 108.37
2019-09-29 22:30 | 104.21 | 100.82
2019-09-29 23:00 | 108.11 | 104
2019-09-29 23:30 | 100.45 | 96.79
2019-09-30 | 95.51 | 91.62
2019-09-30 00:30 | 101.78 | 97.83
2019-09-30 01:00 | 98.97 | 95.03
2019-09-30 01:30 | 96.26 | 92.02
2019-09-30 02:00 | 108.25 | 104.19
2019-09-30 02:30 | 102.09 | 98.11
2019-09-30 03:00 | 101.89 | 97.8
2019-09-30 03:30 | 101.34 | 97.58
2019-09-30 04:00 | 97.31 | 93.34
2019-09-30 04:30 | 109.91 | 106.09
2019-09-30 05:00 | 103.45 | 99.35
2019-09-30 05:30 | 104.56 | 100.57
2019-09-30 06:00 | 95.28 | 91.69
2019-09-30 06:30 | 88.4 | 83.87
2019-09-30 07:00 | 85.95 | 80.72
2019-09-30 07:30 | 94.62 | 88.98
2019-09-30 08:00 | 94.87 | 90.72
2019-09-30 08:30 | 95.72 | 91.23
2019-09-30 09:00 | 98.82 | 93.73
2019-09-30 09:30 | 93.89 | 88.17
2019-09-30 10:00 | 99.45 | 93.66
2019-09-30 10:30 | 98.84 | 92.71
2019-09-30 11:00 | 100.83 | 94.75
2019-09-30 11:30 | 102.88 | 95.13
2019-09-30 12:00 | 97.77 | 88.5
2019-09-30 12:30 | 95.02 | 86.24
2019-09-30 13:00 | 95.96 | 87.86
2019-09-30 13:30 | 102.45 | 93.84
2019-09-30 14:00 | 109.05 | 99.77
2019-09-30 14:30 | 111.38 | 101.84
2019-09-30 15:00 | 112.13 | 102.79
2019-09-30 15:30 | 115.94 | 106.06
2019-09-30 16:00 | 115.64 | 106.73
2019-09-30 16:30 | 113.9 | 106.1
2019-09-30 17:00 | 112.52 | 106.35
2019-09-30 17:30 | 110.57 | 105.61
2019-09-30 18:00 | 104.95 | 99.95
2019-09-30 18:30 | 106.94 | 101.37
2019-09-30 19:00 | 111.65 | 106.92
2019-09-30 19:30 | 110.29 | 105.8
2019-09-30 20:00 | 116.52 | 110.82
2019-09-30 20:30 | 117.06 | 110.82
2019-09-30 21:00 | 108.89 | 102.42
2019-09-30 21:30 | 113.84 | 106.6
2019-09-30 22:00 | 117.92 | 111.02
2019-09-30 22:30 | 120.41 | 113.57
2019-09-30 23:00 | 117.46 | 110.91
2019-09-30 23:30 | 113.94 | 106.93
2019-10-01 | 112.69 | 105.87
2019-10-01 00:30 | 105.85 | 97.75
2019-10-01 01:00 | 118.23 | 110
2019-10-01 01:30 | 109.15 | 101.38
2019-10-01 02:00 | 111.89 | 104.26
2019-10-01 02:30 | 111.56 | 104.59
2019-10-01 03:00 | 102.4 | 97.16
2019-10-01 03:30 | 102.01 | 97.32
2019-10-01 04:00 | 96.31 | 91.8
2019-10-01 04:30 | 99.65 | 94.45
2019-10-01 05:00 | 91.42 | 86.91
2019-10-01 05:30 | 96.98 | 92.05
2019-10-01 06:00 | 94.86 | 89.68
2019-10-01 06:30 | 85.4 | 79.72
2019-10-01 07:00 | 84.5 | 77.03
2019-10-01 07:30 | 82.33 | 75.74
2019-10-01 08:00 | 90.23 | 85.28
2019-10-01 08:30 | 94.17 | 89.51
2019-10-01 09:00 | 89.81 | 84.24
2019-10-01 09:30 | 90.18 | 83.61
2019-10-01 10:00 | 93.88 | 88.16
2019-10-01 10:30 | 95.59 | 90.48
2019-10-01 11:00 | 89.94 | 84.56
2019-10-01 11:30 | 94.97 | 89.87
2019-10-01 12:00 | 84.33 | 77.99
2019-10-01 12:30 | 85.65 | 78.14
2019-10-01 13:00 | 96.55 | 90.7
2019-10-01 13:30 | 108.56 | 103.14
2019-10-01 14:00 | 107.02 | 101.38
2019-10-01 14:30 | 106.46 | 99.95
2019-10-01 15:00 | 102.52 | 95.15
2019-10-01 15:30 | 112.56 | 106.6
2019-10-01 16:00 | 110.02 | 103.62
2019-10-01 16:30 | 112.85 | 106.77
2019-10-01 17:00 | 118.83 | 112.67
2019-10-01 17:30 | 124.1 | 117.88
2019-10-01 18:00 | 118.53 | 112.11
2019-10-01 18:30 | 104.56 | 98.79
2019-10-01 19:00 | 111.01 | 104.87
2019-10-01 19:30 | 114.4 | 108.35
2019-10-01 20:00 | 117.7 | 111.31
2019-10-01 20:30 | 110.7 | 104.12
2019-10-01 21:00 | 116.99 | 110.95
2019-10-01 21:30 | 112.55 | 106.61
2019-10-01 22:00 | 111.92 | 106.61
2019-10-01 22:30 | 113.96 | 108.32
2019-10-01 23:00 | 120.05 | 114.31
2019-10-01 23:30 | 105.79 | 99.98
2019-10-02 | 99.24 | 94.25
2019-10-02 00:30 | 107.77 | 103.52
2019-10-02 01:00 | 110.49 | 106.13
2019-10-02 01:30 | 101.87 | 97.4
2019-10-02 02:00 | 95.75 | 91.26
2019-10-02 02:30 | 97.95 | 93.27
2019-10-02 03:00 | 91.58 | 86.17
2019-10-02 03:30 | 96.37 | 91.55
2019-10-02 04:00 | 98.86 | 93.91
2019-10-02 04:30 | 95.67 | 89.78
2019-10-02 05:00 | 100.1 | 94.84
2019-10-02 05:30 | 96.91 | 91.7
2019-10-02 06:00 | 101.94 | 96.72
2019-10-02 06:30 | 95.55 | 90.16
2019-10-02 07:00 | 101.98 | 97.31
2019-10-02 07:30 | 95.3 | 89.89
2019-10-02 08:00 | 95.72 | 90.91
2019-10-02 08:30 | 89.99 | 84.6
2019-10-02 09:00 | 87.45 | 82.06
2019-10-02 09:30 | 90.58 | 85.21
2019-10-02 10:00 | 91.43 | 85.63
2019-10-02 10:30 | 87.9 | 78.95
2019-10-02 11:00 | 82.09 | 72.77
2019-10-02 11:30 | 84.23 | 75.8
2019-10-02 12:00 | 88.36 | 78.37
2019-10-02 12:30 | 87.65 | 80.13
2019-10-02 13:00 | 90.32 | 83.95
2019-10-02 13:30 | 88.21 | 80.7
2019-10-02 14:00 | 91.71 | 79.11
2019-10-02 14:30 | 86.09 | 76.09
2019-10-02 15:00 | 100.06 | 94.43
2019-10-02 15:30 | 98.23 | 92.69
2019-10-02 16:00 | 99.33 | 93.18
2019-10-02 16:30 | 104.51 | 98.03
2019-10-02 17:00 | 103.87 | 98.67
2019-10-02 17:30 | 106.51 | 101.69
2019-10-02 18:00 | 105.97 | 101.16
2019-10-02 18:30 | 100.22 | 95.19
2019-10-02 19:00 | 108.45 | 103.84
2019-10-02 19:30 | 97.24 | 92.95
2019-10-02 20:00 | 98.91 | 94.69
2019-10-02 20:30 | 105.19 | 101.07
2019-10-02 21:00 | 109.24 | 104.89
2019-10-02 21:30 | 104.42 | 99.91
2019-10-02 22:00 | 108.79 | 103.95
2019-10-02 22:30 | 104.87 | 99.8
2019-10-02 23:00 | 104.97 | 99.73
2019-10-02 23:30 | 104.21 | 99.26
2019-10-03 | 102.46 | 97.73
2019-10-03 00:30 | 101.4 | 95.48
2019-10-03 01:00 | 101.16 | 95.56
2019-10-03 01:30 | 106.05 | 100.48
2019-10-03 02:00 | 111.93 | 106.66
2019-10-03 02:30 | 113.87 | 108.5
2019-10-03 03:00 | 104.82 | 98.99
2019-10-03 03:30 | 104.77 | 98.68
2019-10-03 04:00 | 101.43 | 95.52
2019-10-03 04:30 | 103.07 | 97.92
2019-10-03 05:00 | 101.92 | 96.81
2019-10-03 05:30 | 93.89 | 88.77
2019-10-03 06:00 | 96.29 | 91.12
2019-10-03 06:30 | 87.33 | 81
2019-10-03 07:00 | 99.07 | 93.31
2019-10-03 07:30 | 98.91 | 92.97
2019-10-03 08:00 | 96.77 | 91.31
2019-10-03 08:30 | 93.99 | 87.65
2019-10-03 09:00 | 94.61 | 88.52
2019-10-03 09:30 | 98.23 | 92.29
2019-10-03 10:00 | 95.94 | 89.97
2019-10-03 10:30 | 103.7 | 97.54
2019-10-03 11:00 | 100.69 | 93.96
2019-10-03 11:30 | 95.94 | 87.83
2019-10-03 12:00 | 98.57 | 92.44
2019-10-03 12:30 | 96.64 | 90.01
2019-10-03 13:00 | 92.6 | 85.06
2019-10-03 13:30 | 88.99 | 80.92
2019-10-03 14:00 | 97.41 | 82.28
2019-10-03 14:30 | 96.22 | 82.18
2019-10-03 15:00 | 95.96 | 89.55
2019-10-03 15:30 | 101.26 | 94.86
2019-10-03 16:00 | 103.04 | 97.1
2019-10-03 16:30 | 98.01 | 92.41
2019-10-03 17:00 | 101.15 | 95.37
2019-10-03 17:30 | 104.92 | 98.58
2019-10-03 18:00 | 107.27 | 101.67
2019-10-03 18:30 | 104.39 | 98.63
2019-10-03 19:00 | 115.22 | 109.24
2019-10-03 19:30 | 112.9 | 106.84
2019-10-03 20:00 | 116.92 | 111.3
2019-10-03 20:30 | 123.25 | 117.16
2019-10-03 21:00 | 117.18 | 111.46
2019-10-03 21:30 | 104.91 | 99.81
2019-10-03 22:00 | 102.56 | 98.09
2019-10-03 22:30 | 104.36 | 99.37
2019-10-03 23:00 | 108.93 | 103.8
2019-10-03 23:30 | 104.69 | 99.4
2019-10-04 | 103.1 | 97.74
2019-10-04 00:30 | 105.12 | 99.98
2019-10-04 01:00 | 100.46 | 95.25
2019-10-04 01:30 | 101.09 | 95.69
2019-10-04 02:00 | 103.66 | 98.35
2019-10-04 02:30 | 97.97 | 92.66
2019-10-04 03:00 | 110.78 | 105.82
2019-10-04 03:30 | 107.81 | 103.31
2019-10-04 04:00 | 101.56 | 97.12
2019-10-04 04:30 | 104.91 | 100.47
2019-10-04 05:00 | 107.68 | 103.28
2019-10-04 05:30 | 104.27 | 98.85
2019-10-04 06:00 | 104.95 | 100.38
2019-10-04 06:30 | 93.28 | 88.13
2019-10-04 07:00 | 104.63 | 100.63
2019-10-04 07:30 | 102.78 | 98.64
2019-10-04 08:00 | 99.98 | 95.84
2019-10-04 08:30 | 96.39 | 91.83
2019-10-04 09:00 | 106.9 | 101.87
2019-10-04 09:30 | 103.77 | 97.8
2019-10-04 10:00 | 97.17 | 90.4
2019-10-04 10:30 | 98.2 | 92.81
2019-10-04 11:00 | 96.99 | 91.17
2019-10-04 11:30 | 92.83 | 87.14
2019-10-04 12:00 | 98.15 | 92.11
2019-10-04 12:30 | 104.83 | 98.18
2019-10-04 13:00 | 101.58 | 94.54
2019-10-04 13:30 | 103.1 | 96.7
2019-10-04 14:00 | 109.5 | 103.07
2019-10-04 14:30 | 106.61 | 100.25
2019-10-04 15:00 | 100.01 | 93.22
2019-10-04 15:30 | 98.73 | 91.58
2019-10-04 16:00 | 107.78 | 101.04
2019-10-04 16:30 | 98.62 | 92.04
2019-10-04 17:00 | 103.76 | 97.05
2019-10-04 17:30 | 106.33 | 99.34
2019-10-04 18:00 | 106.57 | 101.28
2019-10-04 18:30 | 103.18 | 97.36
2019-10-04 19:00 | 116.43 | 111.06
2019-10-04 19:30 | 111.52 | 105.58
2019-10-04 20:00 | 114.63 | 109.22
2019-10-04 20:30 | 109.17 | 103.64
2019-10-04 21:00 | 111.78 | 106.47
2019-10-04 21:30 | 106.99 | 101.48
2019-10-04 22:00 | 116.42 | 111.06
2019-10-04 22:30 | 119.91 | 114.06
2019-10-04 23:00 | 113.36 | 107.2
2019-10-04 23:30 | 101.3 | 94.88
2019-10-05 | 103.83 | 97.37
2019-10-05 00:30 | 104.42 | 97.52
2019-10-05 01:00 | 108.89 | 102.58
2019-10-05 01:30 | 112.18 | 105.85
2019-10-05 02:00 | 105.97 | 99.12
2019-10-05 02:30 | 112.87 | 106.4
2019-10-05 03:00 | 111.49 | 104.94
2019-10-05 03:30 | 106.66 | 100.32
2019-10-05 04:00 | 128.4 | 122.9
2019-10-05 04:30 | 112.15 | 106.48
2019-10-05 05:00 | 110.49 | 104.22
2019-10-05 05:30 | 100.99 | 94.78
2019-10-05 06:00 | 96.9 | 90.74
2019-10-05 06:30 | 91.01 | 83.79
2019-10-05 07:00 | 96.49 | 87.99
2019-10-05 07:30 | 100.63 | 93.74
2019-10-05 08:00 | 106.17 | 100.21
2019-10-05 08:30 | 105.27 | 97.44
2019-10-05 09:00 | 95.17 | 84.61
2019-10-05 09:30 | 97.89 | 87.32
2019-10-05 10:00 | 99.64 | 86.42
2019-10-05 10:30 | 105.57 | 98.85
2019-10-05 11:00 | 104.77 | 97.57
2019-10-05 11:30 | 97.46 | 88.93
2019-10-05 12:00 | 102.05 | 95.47
2019-10-05 12:30 | 92.77 | 83
2019-10-05 13:00 | 91.72 | 80.11
2019-10-05 13:30 | 97.06 | 87.96
2019-10-05 14:00 | 106.57 | 100.32
2019-10-05 14:30 | 100.8 | 93.05
2019-10-05 15:00 | 99.54 | 93.37
2019-10-05 15:30 | 105.63 | 94.57
2019-10-05 16:00 | 94.17 | 76.25
2019-10-05 16:30 | 93.06 | 76.69
2019-10-05 17:00 | 88.45 | 76.55
2019-10-05 17:30 | 94.53 | 87.57
2019-10-05 18:00 | 103.18 | 97.48
2019-10-05 18:30 | 96.63 | 90.27
2019-10-05 19:00 | 104.3 | 98.89
2019-10-05 19:30 | 104.72 | 98.59
2019-10-05 20:00 | 103.71 | 97.35
2019-10-05 20:30 | 113.74 | 107.43
2019-10-05 21:00 | 107.91 | 101.5
2019-10-05 21:30 | 103.7 | 97.23
2019-10-05 22:00 | 109.6 | 102.99
2019-10-05 22:30 | 111.02 | 105.11
2019-10-05 23:00 | 114.6 | 109.11
2019-10-05 23:30 | 114.84 | 109.52
2019-10-06 | 117.44 | 111.57
2019-10-06 00:30 | 116.82 | 111.05
2019-10-06 01:00 | 109.07 | 103.06
2019-10-06 01:30 | 104.62 | 98.51
2019-10-06 02:00 | 96.81 | 90.38
2019-10-06 02:30 | 104.89 | 99.26
2019-10-06 03:00 | 104.11 | 98.23
2019-10-06 03:30 | 99.93 | 93.49
2019-10-06 04:00 | 99.11 | 93.18
2019-10-06 04:30 | 101.67 | 95.71
2019-10-06 05:00 | 101.81 | 95.78
2019-10-06 05:30 | 103.6 | 97.48
2019-10-06 06:00 | 104.09 | 98.18
2019-10-06 06:30 | 90.45 | 82.85
2019-10-06 07:00 | 98.3 | 89.93
2019-10-06 07:30 | 98.28 | 89.08
2019-10-06 08:00 | 102.89 | 95.12
2019-10-06 08:30 | 102.28 | 94.24
2019-10-06 09:00 | 94.98 | 76.8
2019-10-06 09:30 | 99.84 | 81.3
2019-10-06 10:00 | 92.07 | 73.67
2019-10-06 10:30 | 84.22 | 65.48
2019-10-06 11:00 | 87.71 | 74.58
2019-10-06 11:30 | 86.04 | 74.57
2019-10-06 12:00 | 87.61 | 78.44
2019-10-06 12:30 | 95.98 | 87.5
2019-10-06 13:00 | 97.02 | 86.06
2019-10-06 13:30 | 93.74 | 76.74
2019-10-06 14:00 | 101.99 | 83.74
2019-10-06 14:30 | 104.52 | 85.13
2019-10-06 15:00 | 104.48 | 85.71
2019-10-06 15:30 | 100.16 | 83.32
2019-10-06 16:00 | 90.07 | 75.51
2019-10-06 16:30 | 88.48 | 77.9
2019-10-06 17:00 | 100.96 | 92.88
2019-10-06 17:30 | 106.2 | 99.64
2019-10-06 18:00 | 109.46 | 104.4
2019-10-06 18:30 | 110.6 | 105.45
2019-10-06 19:00 | 110.16 | 105.58
2019-10-06 19:30 | 116.94 | 111.37
2019-10-06 20:00 | 104.6 | 99.29
2019-10-06 20:30 | 109.48 | 104.68
2019-10-06 21:00 | 106.74 | 101.34
2019-10-06 21:30 | 111.9 | 106.63
2019-10-06 22:00 | 115.32 | 109.81
2019-10-06 22:30 | 106.96 | 100.96
2019-10-06 23:00 | 113.97 | 108
2019-10-06 23:30 | 106.87 | 101.17
2019-10-07 | 112.93 | 107
2019-10-07 00:30 | 113.75 | 107.3
2019-10-07 01:00 | 107.63 | 101.08
2019-10-07 01:30 | 108.92 | 102.64
2019-10-07 02:00 | 108.01 | 102.25
2019-10-07 02:30 | 107.6 | 101.5
2019-10-07 03:00 | 99.35 | 92.26
2019-10-07 03:30 | 99.13 | 92.23
2019-10-07 04:00 | 103.48 | 97.11
2019-10-07 04:30 | 106.7 | 101.2
2019-10-07 05:00 | 96.61 | 90.74
2019-10-07 05:30 | 93.75 | 87.64
2019-10-07 06:00 | 99.75 | 94.63
2019-10-07 06:30 | 88.06 | 81.78
2019-10-07 07:00 | 96.95 | 89.49
2019-10-07 07:30 | 95.97 | 88.45
2019-10-07 08:00 | 100.87 | 95.76
2019-10-07 08:30 | 92.65 | 87.12
2019-10-07 09:00 | 102.94 | 96.56
2019-10-07 09:30 | 98.39 | 88.25
2019-10-07 10:00 | 92.39 | 81.5
2019-10-07 10:30 | 102.12 | 85.62
2019-10-07 11:00 | 93.8 | 75.28
2019-10-07 11:30 | 91.04 | 75.75
2019-10-07 12:00 | 99.47 | 86.49
2019-10-07 12:30 | 103.41 | 94.02
2019-10-07 13:00 | 96.68 | 81.15
2019-10-07 13:30 | 92.73 | 75.76
2019-10-07 14:00 | 95.69 | 79.78
2019-10-07 14:30 | 101.11 | 84.9
2019-10-07 15:00 | 108.99 | 93.21
2019-10-07 15:30 | 100.95 | 87.02
2019-10-07 16:00 | 103.79 | 92.16
2019-10-07 16:30 | 105.7 | 93.92
2019-10-07 17:00 | 104.96 | 96.02
2019-10-07 17:30 | 117.98 | 111.49
2019-10-07 18:00 | 121.51 | 116.71
2019-10-07 18:30 | 114.65 | 109.43
2019-10-07 19:00 | 117.3 | 112.66
2019-10-07 19:30 | 112.89 | 108.41
2019-10-07 20:00 | 112.11 | 107.15
2019-10-07 20:30 | 111.55 | 106.88
2019-10-07 21:00 | 115.58 | 110.67
2019-10-07 21:30 | 119.65 | 114.84
2019-10-07 22:00 | 117.83 | 112.22
2019-10-07 22:30 | 119.22 | 113.46
2019-10-07 23:00 | 115.22 | 109.45
2019-10-07 23:30 | 108.22 | 101.43
2019-10-08 | 116.58 | 111.24
2019-10-08 00:30 | 109.05 | 102.71
2019-10-08 01:00 | 118.08 | 112.58
2019-10-08 01:30 | 123.78 | 117.98
2019-10-08 02:00 | 117.14 | 111.15
2019-10-08 02:30 | 119.1 | 113.06
2019-10-08 03:00 | 115.57 | 108.85
2019-10-08 03:30 | 106.64 | 100.01
2019-10-08 04:00 | 108.83 | 102.52
2019-10-08 04:30 | 107.63 | 100.88
2019-10-08 05:00 | 110.92 | 104.79
2019-10-08 05:30 | 112.64 | 106.78
2019-10-08 06:00 | 117.38 | 112.41
2019-10-08 06:30 | 106.35 | 100.37
2019-10-08 07:00 | 102.92 | 94.9
2019-10-08 07:30 | 94.46 | 83.28
2019-10-08 08:00 | 94.15 | 81.3
2019-10-08 08:30 | 92.59 | 77.6
2019-10-08 09:00 | 98.9 | 82.79
2019-10-08 09:30 | 95.62 | 80.65
2019-10-08 10:00 | 94.73 | 79.81
2019-10-08 10:30 | 108.98 | 103.54
2019-10-08 11:00 | 116.55 | 111.32
2019-10-08 11:30 | 110.99 | 105.58
2019-10-08 12:00 | 109.79 | 104.73
2019-10-08 12:30 | 116.32 | 110.44
2019-10-08 13:00 | 117.7 | 112.36
2019-10-08 13:30 | 112.1 | 106.77
2019-10-08 14:00 | 115.2 | 110.04
2019-10-08 14:30 | 120.82 | 115.79
2019-10-08 15:00 | 107.2 | 100.38
2019-10-08 15:30 | 111.87 | 105.45
2019-10-08 16:00 | 107.29 | 100.92
2019-10-08 16:30 | 116.88 | 110.6
2019-10-08 17:00 | 127.72 | 121.19
2019-10-08 17:30 | 132.77 | 127.18
2019-10-08 18:00 | 132 | 126.02
2019-10-08 18:30 | 118.86 | 112.54
2019-10-08 19:00 | 125.18 | 119.4
2019-10-08 19:30 | 129.71 | 123.7
2019-10-08 20:00 | 125.48 | 119.9
2019-10-08 20:30 | 131.3 | 126.48
2019-10-08 21:00 | 125.26 | 120.18
2019-10-08 21:30 | 122.3 | 116.82
2019-10-08 22:00 | 121.97 | 116.27
2019-10-08 22:30 | 118.72 | 112.44
2019-10-08 23:00 | 119.94 | 113.81
2019-10-08 23:30 | 112.4 | 106.21
2019-10-09 | 112.86 | 107.09
2019-10-09 00:30 | 117.26 | 110.87
2019-10-09 01:00 | 122.02 | 116.2
2019-10-09 01:30 | 124.05 | 118.02
2019-10-09 02:00 | 116.14 | 110.84
2019-10-09 02:30 | 110.35 | 104.79
2019-10-09 03:00 | 104.16 | 98.77
2019-10-09 03:30 | 104.94 | 99.26
2019-10-09 04:00 | 109.37 | 103.7
2019-10-09 04:30 | 111.11 | 105.31
2019-10-09 05:00 | 108.16 | 101.52
2019-10-09 05:30 | 111.78 | 106.4
2019-10-09 06:00 | 101.1 | 94.66
2019-10-09 06:30 | 104.17 | 98.5
2019-10-09 07:00 | 104.21 | 97.4
2019-10-09 07:30 | 96.9 | 89.56
2019-10-09 08:00 | 99.57 | 93.07
2019-10-09 08:30 | 94.04 | 86.46
2019-10-09 09:00 | 94.6 | 86.33
2019-10-09 09:30 | 97.88 | 90.57
2019-10-09 10:00 | 95.13 | 87.24
2019-10-09 10:30 | 95.3 | 87.5
2019-10-09 11:00 | 92.75 | 84.71
2019-10-09 11:30 | 86.9 | 77.81
2019-10-09 12:00 | 96.33 | 88.04
2019-10-09 12:30 | 103.7 | 96.82
2019-10-09 13:00 | 95.39 | 87.6
2019-10-09 13:30 | 98.25 | 90.57
2019-10-09 14:00 | 98.78 | 90.58
2019-10-09 14:30 | 101.01 | 93.4
2019-10-09 15:00 | 97.59 | 89.59
2019-10-09 15:30 | 93.13 | 84.12
2019-10-09 16:00 | 100.3 | 92.39
2019-10-09 16:30 | 101.55 | 94.25
2019-10-09 17:00 | 97.64 | 90.27
2019-10-09 17:30 | 97.99 | 90.48
2019-10-09 18:00 | 102.65 | 95.66
2019-10-09 18:30 | 101.73 | 93.94
2019-10-09 19:00 | 103.47 | 97.07
2019-10-09 19:30 | 101.73 | 96.4
2019-10-09 20:00 | 104.67 | 100.46
2019-10-09 20:30 | 108.62 | 103.72
2019-10-09 21:00 | 112.44 | 107.04
2019-10-09 21:30 | 113.5 | 108.92
2019-10-09 22:00 | 117.73 | 113.25
2019-10-09 22:30 | 123.24 | 118.57
2019-10-09 23:00 | 112.69 | 107.31
2019-10-09 23:30 | 114.97 | 109.37
2019-10-10 | 104.82 | 98.3
2019-10-10 00:30 | 104.32 | 97.38
2019-10-10 01:00 | 109.69 | 103.03
2019-10-10 01:30 | 101.27 | 93.97
2019-10-10 02:00 | 103.27 | 95.92
2019-10-10 02:30 | 105.16 | 98.71
2019-10-10 03:00 | 100.09 | 92.09
2019-10-10 03:30 | 112.41 | 105.67
2019-10-10 04:00 | 106.96 | 100.44
2019-10-10 04:30 | 105.81 | 99.36
2019-10-10 05:00 | 109.76 | 103.36
2019-10-10 05:30 | 100.48 | 91.9
2019-10-10 06:00 | 107.11 | 100.11
2019-10-10 06:30 | 97.52 | 89.69
2019-10-10 07:00 | 107.39 | 100.84
2019-10-10 07:30 | 105.58 | 99.16
2019-10-10 08:00 | 97.73 | 89.09
2019-10-10 08:30 | 96.67 | 88.64
2019-10-10 09:00 | 97.06 | 89.12
2019-10-10 09:30 | 97.44 | 90.09
2019-10-10 10:00 | 97.9 | 90.69
2019-10-10 10:30 | 104.24 | 98.19
2019-10-10 11:00 | 91.21 | 82.49
2019-10-10 11:30 | 93.45 | 84.97
2019-10-10 12:00 | 94.23 | 85.29
2019-10-10 12:30 | 99.11 | 91.47
2019-10-10 13:00 | 94.22 | 85.48
2019-10-10 13:30 | 101.9 | 95.06
2019-10-10 14:00 | 97.25 | 89.36
2019-10-10 14:30 | 102.62 | 96.07
2019-10-10 15:00 | 99.18 | 92.66
2019-10-10 15:30 | 91.93 | 84.51
2019-10-10 16:00 | 93.48 | 87.39
2019-10-10 16:30 | 89.71 | 85.74
2019-10-10 17:00 | 95.22 | 91.52
2019-10-10 17:30 | 104.59 | 101.44
2019-10-10 18:00 | 96.74 | 93.12
2019-10-10 18:30 | 99.79 | 95.68
2019-10-10 19:00 | 104.55 | 100.61
2019-10-10 19:30 | 103.62 | 99.71
2019-10-10 20:00 | 104.13 | 100.3
2019-10-10 20:30 | 99.02 | 95.29
2019-10-10 21:00 | 103.46 | 99.36
2019-10-10 21:30 | 103.03 | 98.89
2019-10-10 22:00 | 102.26 | 97.49
2019-10-10 22:30 | 111.84 | 106.67
2019-10-10 23:00 | 108.4 | 103.62
2019-10-10 23:30 | 105.84 | 101.46
2019-10-11 | 102.75 | 98.08
2019-10-11 00:30 | 105.3 | 100.84
2019-10-11 01:00 | 102.44 | 97.74
2019-10-11 01:30 | 102.49 | 97.38
2019-10-11 02:00 | 109.83 | 105.11
2019-10-11 02:30 | 106.78 | 102
2019-10-11 03:00 | 103.07 | 98.75
2019-10-11 03:30 | 106.22 | 101.73
2019-10-11 04:00 | 107.57 | 103.37
2019-10-11 04:30 | 103.73 | 99.19
2019-10-11 05:00 | 107.87 | 103.59
2019-10-11 05:30 | 108.1 | 104.03
2019-10-11 06:00 | 102.52 | 98.62
2019-10-11 06:30 | 89.57 | 83.77
2019-10-11 07:00 | 95.06 | 89.59
2019-10-11 07:30 | 94.47 | 90.09
2019-10-11 08:00 | 99.46 | 95.31
2019-10-11 08:30 | 95.73 | 91.56
2019-10-11 09:00 | 94.35 | 89.61
2019-10-11 09:30 | 97.69 | 93.05
2019-10-11 10:00 | 91.3 | 86.77
2019-10-11 10:30 | 86.62 | 81.02
2019-10-11 11:00 | 90.84 | 85.16
2019-10-11 11:30 | 97.01 | 92.22
2019-10-11 12:00 | 100.09 | 95.85
2019-10-11 12:30 | 94.8 | 89.18
2019-10-11 13:00 | 104.04 | 99.48
2019-10-11 13:30 | 102.4 | 97.65
2019-10-11 14:00 | 95.15 | 89.72
2019-10-11 14:30 | 101.72 | 96.57
2019-10-11 15:00 | 99.62 | 93.46
2019-10-11 15:30 | 94.67 | 88.43
2019-10-11 16:00 | 93.01 | 85.1
2019-10-11 16:30 | 97.59 | 91.14
2019-10-11 17:00 | 102.84 | 97.34
2019-10-11 17:30 | 104.24 | 99.57
2019-10-11 18:00 | 103.29 | 98.92
2019-10-11 18:30 | 95.27 | 89.44
2019-10-11 19:00 | 103.95 | 99.28
2019-10-11 19:30 | 112.22 | 107.55
2019-10-11 20:00 | 107.6 | 103.3
2019-10-11 20:30 | 103.9 | 99.42
2019-10-11 21:00 | 98.81 | 93.59
2019-10-11 21:30 | 105.46 | 99.56
2019-10-11 22:00 | 101.91 | 96.18
2019-10-11 22:30 | 107.69 | 102.6
2019-10-11 23:00 | 111.96 | 107.02
2019-10-11 23:30 | 104.33 | 99.26
2019-10-12 | 102.92 | 97.81
2019-10-12 00:30 | 105.14 | 100.08
2019-10-12 01:00 | 109.24 | 104.45
2019-10-12 01:30 | 111.66 | 106.29
2019-10-12 02:00 | 109.27 | 104.03
2019-10-12 02:30 | 111.61 | 106.56
2019-10-12 03:00 | 111.2 | 106.1
2019-10-12 03:30 | 108.51 | 103.46
2019-10-12 04:00 | 109.4 | 104.15
2019-10-12 04:30 | 107.96 | 102.94
2019-10-12 05:00 | 104.65 | 98.65
2019-10-12 05:30 | 103.65 | 98.28
2019-10-12 06:00 | 99.2 | 93.71
2019-10-12 06:30 | 94.67 | 88.36
2019-10-12 07:00 | 98.88 | 93.11
2019-10-12 07:30 | 100.35 | 94.97
2019-10-12 08:00 | 107.05 | 101.96
2019-10-12 08:30 | 101.82 | 96.53
2019-10-12 09:00 | 102.95 | 97.84
2019-10-12 09:30 | 102.79 | 96.54
2019-10-12 10:00 | 104.06 | 98.09
2019-10-12 10:30 | 103.33 | 96.89
2019-10-12 11:00 | 103.56 | 96.54
2019-10-12 11:30 | 109.12 | 101.95
2019-10-12 12:00 | 95.33 | 89.51
2019-10-12 12:30 | 97.18 | 90.93
2019-10-12 13:00 | 98.11 | 92.32
2019-10-12 13:30 | 105.47 | 99.54
2019-10-12 14:00 | 110.24 | 104.2
2019-10-12 14:30 | 102.86 | 97.01
2019-10-12 15:00 | 97.85 | 91.45
2019-10-12 15:30 | 92.91 | 86.66
2019-10-12 16:00 | 100.87 | 95.11
2019-10-12 16:30 | 106.83 | 101.34
2019-10-12 17:00 | 100.29 | 94.81
2019-10-12 17:30 | 102.54 | 96.61
2019-10-12 18:00 | 104.14 | 98.63
2019-10-12 18:30 | 103.35 | 97.25
2019-10-12 19:00 | 115.3 | 109.56
2019-10-12 19:30 | 116.22 | 110.46
2019-10-12 20:00 | 116.68 | 110.97
2019-10-12 20:30 | 117.76 | 111.84
2019-10-12 21:00 | 103.03 | 98.04
2019-10-12 21:30 | 98.46 | 93.84
2019-10-12 22:00 | 97.28 | 92.01
2019-10-12 22:30 | 107.07 | 101.13
2019-10-12 23:00 | 104.76 | 99.46
2019-10-12 23:30 | 105.46 | 100.35
2019-10-13 | 107.15 | 101.75
2019-10-13 00:30 | 101.1 | 95.86
2019-10-13 01:00 | 101.83 | 96.52
2019-10-13 01:30 | 108.45 | 102.9
2019-10-13 02:00 | 107.52 | 102.38
2019-10-13 02:30 | 106.32 | 101.05
2019-10-13 03:00 | 101.36 | 96.47
2019-10-13 03:30 | 107.15 | 101.13
2019-10-13 04:00 | 99.86 | 94.23
2019-10-13 04:30 | 102.43 | 96.63
2019-10-13 05:00 | 100.87 | 95.36
2019-10-13 05:30 | 96.26 | 90.9
2019-10-13 06:00 | 102.86 | 97.07
2019-10-13 06:30 | 84.99 | 79.24
2019-10-13 07:00 | 97.54 | 93.34
2019-10-13 07:30 | 96.07 | 90.8
2019-10-13 08:00 | 98.59 | 92.6
2019-10-13 08:30 | 98.6 | 92.01
2019-10-13 09:00 | 102.94 | 95.65
2019-10-13 09:30 | 108.02 | 100.75
2019-10-13 10:00 | 106.82 | 99.81
2019-10-13 10:30 | 113.2 | 106.43
2019-10-13 11:00 | 109.11 | 102.37
2019-10-13 11:30 | 109.29 | 101.32
2019-10-13 12:00 | 106.67 | 99.06
2019-10-13 12:30 | 105.51 | 97.48
2019-10-13 13:00 | 101.96 | 94.36
2019-10-13 13:30 | 99.49 | 92.3
2019-10-13 14:00 | 105.4 | 98.4
2019-10-13 14:30 | 107.02 | 99.3
2019-10-13 15:00 | 115.74 | 107.88
2019-10-13 15:30 | 113.05 | 105.37
2019-10-13 16:00 | 112.51 | 104.69
2019-10-13 16:30 | 117.21 | 109.24
2019-10-13 17:00 | 113.9 | 105.89
2019-10-13 17:30 | 107.36 | 100.47
2019-10-13 18:00 | 123.15 | 115.89
2019-10-13 18:30 | 111.53 | 102.69
2019-10-13 19:00 | 116.71 | 107.61
2019-10-13 19:30 | 117.18 | 108.09
2019-10-13 20:00 | 115.82 | 106.91
2019-10-13 20:30 | 111.74 | 101.27
2019-10-13 21:00 | 110.38 | 100.78
2019-10-13 21:30 | 117.9 | 109.71
2019-10-13 22:00 | 121.15 | 112.97
2019-10-13 22:30 | 110.9 | 103.14
2019-10-13 23:00 | 114.78 | 108.05
2019-10-13 23:30 | 109.88 | 103.28
2019-10-14 | 119.5 | 112
2019-10-14 00:30 | 112.68 | 105.47
2019-10-14 01:00 | 114.83 | 107.04
2019-10-14 01:30 | 116.71 | 109.32
2019-10-14 02:00 | 111.51 | 103.62
2019-10-14 02:30 | 113.22 | 106.07
2019-10-14 03:00 | 115.86 | 108.18
2019-10-14 03:30 | 113.8 | 106.72
2019-10-14 04:00 | 114.33 | 107.76
2019-10-14 04:30 | 107.46 | 101.3
2019-10-14 05:00 | 115.53 | 108.41
2019-10-14 05:30 | 110.05 | 102.93
2019-10-14 06:00 | 114.59 | 107.92
2019-10-14 06:30 | 92.25 | 86.6
2019-10-14 07:00 | 94.89 | 90.84
2019-10-14 07:30 | 102.18 | 98.07
2019-10-14 08:00 | 97.54 | 92.86
2019-10-14 08:30 | 95.15 | 89.86
2019-10-14 09:00 | 97.72 | 91.38
2019-10-14 09:30 | 101.19 | 94.57
2019-10-14 10:00 | 104.33 | 97.57
2019-10-14 10:30 | 95.07 | 87.51
2019-10-14 11:00 | 95.97 | 88.33
2019-10-14 11:30 | 98.09 | 90.75
2019-10-14 12:00 | 101.13 | 92.79
2019-10-14 12:30 | 105.02 | 97.76
2019-10-14 13:00 | 110.94 | 103.09
2019-10-14 13:30 | 123.07 | 114.65
2019-10-14 14:00 | 118.82 | 110.57
2019-10-14 14:30 | 104.94 | 97.2
2019-10-14 15:00 | 112.15 | 103.34
2019-10-14 15:30 | 111.58 | 103.29
2019-10-14 16:00 | 112.42 | 104.11
2019-10-14 16:30 | 117.74 | 109.96
2019-10-14 17:00 | 118.34 | 111.6
2019-10-14 17:30 | 121.21 | 113.88
2019-10-14 18:00 | 121.5 | 113.66
2019-10-14 18:30 | 112.93 | 104.14
2019-10-14 19:00 | 118.25 | 109.95
2019-10-14 19:30 | 109.4 | 101.65
2019-10-14 20:00 | 118.15 | 110.77
2019-10-14 20:30 | 121.53 | 114
2019-10-14 21:00 | 118.87 | 111.82
2019-10-14 21:30 | 112.87 | 106.58
2019-10-14 22:00 | 114.74 | 109.28
2019-10-14 22:30 | 117.36 | 111.93
2019-10-14 23:00 | 115.67 | 110.24
2019-10-14 23:30 | 103.56 | 98.67
2019-10-15 | 105.66 | 100.42
2019-10-15 00:30 | 114.79 | 108.44
2019-10-15 01:00 | 109.19 | 102.94
2019-10-15 01:30 | 116.87 | 110.72
2019-10-15 02:00 | 118.48 | 113.17
2019-10-15 02:30 | 111.71 | 106.1
2019-10-15 03:00 | 104.43 | 98.76
2019-10-15 03:30 | 107.23 | 101.77
2019-10-15 04:00 | 97.86 | 92.47
2019-10-15 04:30 | 105.56 | 100.98
2019-10-15 05:00 | 101.16 | 96.48
2019-10-15 05:30 | 97.66 | 93.25
2019-10-15 06:00 | 94.64 | 90.12
2019-10-15 06:30 | 87.69 | 81.76
2019-10-15 07:00 | 96.12 | 91.04
2019-10-15 07:30 | 94.14 | 88.27
2019-10-15 08:00 | 96.41 | 90.88
2019-10-15 08:30 | 107.79 | 101.9
2019-10-15 09:00 | 106.21 | 99.76
2019-10-15 09:30 | 99.01 | 93.38
2019-10-15 10:00 | 109.62 | 104.26
2019-10-15 10:30 | 106.59 | 100.74
2019-10-15 11:00 | 107.84 | 102.39
2019-10-15 11:30 | 106.05 | 99.91
2019-10-15 12:00 | 99.99 | 86.95
2019-10-15 12:30 | 92.33 | 79.96
2019-10-15 13:00 | 103 | 97.39
2019-10-15 13:30 | 102.77 | 92.64
2019-10-15 14:00 | 95.61 | 82.14
2019-10-15 14:30 | 98.07 | 83.93
2019-10-15 15:00 | 97.27 | 87.04
2019-10-15 15:30 | 86.19 | 73.4
2019-10-15 16:00 | 92.28 | 80.03
2019-10-15 16:30 | 87.61 | 78.09
2019-10-15 17:00 | 89.11 | 81.81
2019-10-15 17:30 | 104.61 | 100.44
2019-10-15 18:00 | 107.36 | 103.36
2019-10-15 18:30 | 95.81 | 90.86
2019-10-15 19:00 | 109.95 | 105.51
2019-10-15 19:30 | 105.81 | 100.42
2019-10-15 20:00 | 114.09 | 108.27
2019-10-15 20:30 | 115.42 | 109.72
2019-10-15 21:00 | 116.54 | 110.23
2019-10-15 21:30 | 112.88 | 106.41
2019-10-15 22:00 | 119.38 | 113.44
2019-10-15 22:30 | 113.06 | 107.13
2019-10-15 23:00 | 113.57 | 107.72
2019-10-15 23:30 | 106.35 | 100.11
2019-10-16 | 105.25 | 99.04
2019-10-16 00:30 | 105 | 98.73
2019-10-16 01:00 | 96.43 | 89.48
2019-10-16 01:30 | 101.94 | 95.68
2019-10-16 02:00 | 104.08 | 98.12
2019-10-16 02:30 | 98.95 | 93.73
2019-10-16 03:00 | 98.52 | 94
2019-10-16 03:30 | 98.99 | 94.74
2019-10-16 04:00 | 103.69 | 100.06
2019-10-16 04:30 | 98.71 | 94.38
2019-10-16 05:00 | 98.27 | 93.64
2019-10-16 05:30 | 102.04 | 97.73
2019-10-16 06:00 | 95.36 | 90.94
2019-10-16 06:30 | 84.17 | 79.16
2019-10-16 07:00 | 73.58 | 65.82
2019-10-16 07:30 | 77.18 | 68.02
2019-10-16 08:00 | 70.57 | 59.79
2019-10-16 08:30 | 72.35 | 61.48
2019-10-16 09:00 | 77.39 | 66.01
2019-10-16 09:30 | 71.23 | 58.77
2019-10-16 10:00 | 72.4 | 61.04
2019-10-16 10:30 | 76.92 | 65.35
2019-10-16 11:00 | 78.42 | 67.26
2019-10-16 11:30 | 69.13 | 56.91
2019-10-16 12:00 | 73.26 | 62.59
2019-10-16 12:30 | 83.01 | 73.01
2019-10-16 13:00 | 84 | 73.81
2019-10-16 13:30 | 74.07 | 62.93
2019-10-16 14:00 | 72.53 | 61.99
2019-10-16 14:30 | 65.23 | 54.95
2019-10-16 15:00 | 64.83 | 55.96
2019-10-16 15:30 | 71.87 | 65.45
2019-10-16 16:00 | 71.95 | 63.8
2019-10-16 16:30 | 74.06 | 66.7
2019-10-16 17:00 | 88.28 | 83.92
2019-10-16 17:30 | 89.29 | 85.67
2019-10-16 18:00 | 90.32 | 87.31
2019-10-16 18:30 | 87.72 | 84.79
2019-10-16 19:00 | 94 | 91.13
2019-10-16 19:30 | 100.13 | 97.36
2019-10-16 20:00 | 100.15 | 97.37
2019-10-16 20:30 | 96.49 | 93.44
2019-10-16 21:00 | 96.53 | 92.95
2019-10-16 21:30 | 98.52 | 94.79
2019-10-16 22:00 | 90.85 | 86.58
2019-10-16 22:30 | 101.69 | 97.77
2019-10-16 23:00 | 105.6 | 101.63
2019-10-16 23:30 | 100.4 | 96.17
2019-10-17 | 99.32 | 95
2019-10-17 00:30 | 93.9 | 89.63
2019-10-17 01:00 | 93.63 | 89.39
2019-10-17 01:30 | 97.58 | 93.51
2019-10-17 02:00 | 97.73 | 93.24
2019-10-17 02:30 | 104.79 | 100.13
2019-10-17 03:00 | 91.89 | 86.41
2019-10-17 03:30 | 91.6 | 86.57
2019-10-17 04:00 | 96.11 | 90.93
2019-10-17 04:30 | 95.44 | 90.36
2019-10-17 05:00 | 98.36 | 92.87
2019-10-17 05:30 | 93.56 | 88.22
2019-10-17 06:00 | 96 | 91.95
2019-10-17 06:30 | 92.92 | 88.83
2019-10-17 07:00 | 86.91 | 81
2019-10-17 07:30 | 72.38 | 62.16
2019-10-17 08:00 | 76.23 | 65.26
2019-10-17 08:30 | 78.38 | 66.34
2019-10-17 09:00 | 80.72 | 68.44
2019-10-17 09:30 | 86.15 | 73.45
2019-10-17 10:00 | 86.06 | 72.39
2019-10-17 10:30 | 87.91 | 72.8
2019-10-17 11:00 | 84.47 | 69.59
2019-10-17 11:30 | 88.82 | 75.46
2019-10-17 12:00 | 90.32 | 77.49
2019-10-17 12:30 | 89.61 | 75.13
2019-10-17 13:00 | 93.7 | 79.42
2019-10-17 13:30 | 93.29 | 79.04
2019-10-17 14:00 | 88.53 | 75.33
2019-10-17 14:30 | 94.37 | 80.71
2019-10-17 15:00 | 100.64 | 86.93
2019-10-17 15:30 | 100.92 | 88.02
2019-10-17 16:00 | 91.22 | 80.56
2019-10-17 16:30 | 92.61 | 82.91
2019-10-17 17:00 | 105.64 | 99.44
2019-10-17 17:30 | 116.89 | 112.07
2019-10-17 18:00 | 100.11 | 93.36
2019-10-17 18:30 | 100.5 | 93.47
2019-10-17 19:00 | 107.05 | 100.98
2019-10-17 19:30 | 104.13 | 98.35
2019-10-17 20:00 | 110.06 | 104.11
2019-10-17 20:30 | 108.58 | 102.52
2019-10-17 21:00 | 104.17 | 97.45
2019-10-17 21:30 | 106.12 | 100.13
2019-10-17 22:00 | 109.86 | 104
2019-10-17 22:30 | 109.36 | 103.04
2019-10-17 23:00 | 106.38 | 99.3
2019-10-17 23:30 | 103.85 | 96.06
2019-10-18 | 102.79 | 94.22
2019-10-18 00:30 | 103.48 | 94.48
2019-10-18 01:00 | 104.49 | 96.08
2019-10-18 01:30 | 107.76 | 99.65
2019-10-18 02:00 | 105.19 | 96.54
2019-10-18 02:30 | 104.71 | 96
2019-10-18 03:00 | 111.36 | 103.11
2019-10-18 03:30 | 114.08 | 106.99
2019-10-18 04:00 | 106.26 | 98.77
2019-10-18 04:30 | 110.85 | 104.4
2019-10-18 05:00 | 108.87 | 102.18
2019-10-18 05:30 | 106.82 | 99.31
2019-10-18 06:00 | 108.82 | 102.72
2019-10-18 06:30 | 102.16 | 94.91
2019-10-18 07:00 | 99.76 | 90.98
2019-10-18 07:30 | 98.23 | 87.09
2019-10-18 08:00 | 101.72 | 88.85
2019-10-18 08:30 | 95.15 | 80.76
2019-10-18 09:00 | 86.94 | 77.01
2019-10-18 09:30 | 102 | 96.06
2019-10-18 10:00 | 107.5 | 101.72
2019-10-18 10:30 | 114.64 | 108.82
2019-10-18 11:00 | 117.78 | 111.49
2019-10-18 11:30 | 112.33 | 104.93
2019-10-18 12:00 | 107.93 | 101.04
2019-10-18 12:30 | 108.93 | 101.35
2019-10-18 13:00 | 106.85 | 98.62
2019-10-18 13:30 | 113.38 | 106.36
2019-10-18 14:00 | 103.19 | 94.02
2019-10-18 14:30 | 98.16 | 83.03
2019-10-18 15:00 | 103.64 | 88.94
2019-10-18 15:30 | 102.89 | 88.33
2019-10-18 16:00 | 112.05 | 101.79
2019-10-18 16:30 | 105.93 | 93.09
2019-10-18 17:00 | 94.43 | 76.31
2019-10-18 17:30 | 97.65 | 84.78
2019-10-18 18:00 | 91.67 | 78.85
2019-10-18 18:30 | 94.84 | 83.2
2019-10-18 19:00 | 102.29 | 91.89
2019-10-18 19:30 | 107.25 | 98.61
2019-10-18 20:00 | 110.63 | 102.27
2019-10-18 20:30 | 117.8 | 109.57
2019-10-18 21:00 | 115.81 | 107.1
2019-10-18 21:30 | 114.22 | 105.87
2019-10-18 22:00 | 108.74 | 100.67
2019-10-18 22:30 | 109 | 101.14
2019-10-18 23:00 | 110.82 | 102.28
2019-10-18 23:30 | 109.73 | 102.01
2019-10-19 | 105.94 | 99.94
2019-10-19 00:30 | 102.45 | 95.87
2019-10-19 01:00 | 107.5 | 100.27
2019-10-19 01:30 | 108.84 | 101.18
2019-10-19 02:00 | 109.33 | 101.47
2019-10-19 02:30 | 111.45 | 103.92
2019-10-19 03:00 | 107.11 | 99.54
2019-10-19 03:30 | 105.3 | 97.88
2019-10-19 04:00 | 110.41 | 102.75
2019-10-19 04:30 | 111.32 | 104.22
2019-10-19 05:00 | 112.8 | 105.65
2019-10-19 05:30 | 106.35 | 99.75
2019-10-19 06:00 | 97.58 | 90.89
2019-10-19 06:30 | 97.35 | 87.19
2019-10-19 07:00 | 99.6 | 86.44
2019-10-19 07:30 | 89.05 | 72.17
2019-10-19 08:00 | 98.22 | 82.56
2019-10-19 08:30 | 94.77 | 77.79
2019-10-19 09:00 | 98.68 | 83.66
2019-10-19 09:30 | 100.72 | 85
2019-10-19 10:00 | 104.87 | 89.63
2019-10-19 10:30 | 92.99 | 79.92
2019-10-19 11:00 | 90.85 | 75.13
2019-10-19 11:30 | 85.42 | 70.44
2019-10-19 12:00 | 95.49 | 81.12
2019-10-19 12:30 | 99.12 | 83.41
2019-10-19 13:00 | 99.68 | 84.06
2019-10-19 13:30 | 103.96 | 89.37
2019-10-19 14:00 | 104.85 | 93.23
2019-10-19 14:30 | 93.49 | 79.06
2019-10-19 15:00 | 112.16 | 96.33
2019-10-19 15:30 | 103.47 | 85.4
2019-10-19 16:00 | 117.72 | 103.59
2019-10-19 16:30 | 105.93 | 92.11
2019-10-19 17:00 | 102.05 | 89.98
2019-10-19 17:30 | 120.62 | 112.21
2019-10-19 18:00 | 120.05 | 112.93
2019-10-19 18:30 | 110.23 | 103
2019-10-19 19:00 | 123.09 | 116.09
2019-10-19 19:30 | 114.58 | 108.03
2019-10-19 20:00 | 122.62 | 116.1
2019-10-19 20:30 | 115.51 | 108.38
2019-10-19 21:00 | 110.81 | 104.2
2019-10-19 21:30 | 101.96 | 95.64
2019-10-19 22:00 | 107.63 | 101.51
2019-10-19 22:30 | 110.25 | 103.63
2019-10-19 23:00 | 114.17 | 106.69
2019-10-19 23:30 | 108.69 | 101.51
2019-10-20 | 110.06 | 102.38
2019-10-20 00:30 | 113.87 | 105.73
2019-10-20 01:00 | 115.93 | 108.08
2019-10-20 01:30 | 113.06 | 105.5
2019-10-20 02:00 | 112.18 | 105.11
2019-10-20 02:30 | 109.6 | 102.14
2019-10-20 03:00 | 115.51 | 107.6
2019-10-20 03:30 | 100.14 | 91.62
2019-10-20 04:00 | 102.05 | 93.45
2019-10-20 04:30 | 103.49 | 95.15
2019-10-20 05:00 | 105.8 | 98.19
2019-10-20 05:30 | 109.05 | 101.68
2019-10-20 06:00 | 102.09 | 93.84
2019-10-20 06:30 | 102 | 91.48
2019-10-20 07:00 | 101.1 | 85.94
2019-10-20 07:30 | 99.85 | 81.3
2019-10-20 08:00 | 102.52 | 83.07
2019-10-20 08:30 | 103.92 | 83.48
2019-10-20 09:00 | 103.02 | 82.52
2019-10-20 09:30 | 108.05 | 89.76
2019-10-20 10:00 | 104.17 | 83.95
2019-10-20 10:30 | 96.91 | 77.14
2019-10-20 11:00 | 88.95 | 71.19
2019-10-20 11:30 | 89.39 | 74.62
2019-10-20 12:00 | 88.29 | 73.1
2019-10-20 12:30 | 87.5 | 72.19
2019-10-20 13:00 | 91.95 | 81.36
2019-10-20 13:30 | 87.59 | 73.95
2019-10-20 14:00 | 89.29 | 73.53
2019-10-20 14:30 | 93.28 | 77.01
2019-10-20 15:00 | 99.78 | 83.79
2019-10-20 15:30 | 99.62 | 83.04
2019-10-20 16:00 | 96.98 | 78.78
2019-10-20 16:30 | 95.67 | 79.43
2019-10-20 17:00 | 93.09 | 77.69
2019-10-20 17:30 | 99.85 | 89
2019-10-20 18:00 | 109.36 | 101.69
2019-10-20 18:30 | 103.14 | 95.65
2019-10-20 19:00 | 117.32 | 109.67
2019-10-20 19:30 | 116.99 | 109.29
2019-10-20 20:00 | 116.84 | 109.06
2019-10-20 20:30 | 108.58 | 101.18
2019-10-20 21:00 | 108.78 | 101.17
2019-10-20 21:30 | 106.66 | 99.41
2019-10-20 22:00 | 107.76 | 100.3
2019-10-20 22:30 | 111.87 | 104.7
2019-10-20 23:00 | 114.8 | 107.04
2019-10-20 23:30 | 103.8 | 96.36
2019-10-21 | 108.37 | 100.83
2019-10-21 00:30 | 117.73 | 109.84
2019-10-21 01:00 | 121.3 | 112.74
2019-10-21 01:30 | 107.33 | 99.26
2019-10-21 02:00 | 111.39 | 103.01
2019-10-21 02:30 | 108.81 | 100.84
2019-10-21 03:00 | 111.93 | 103.47
2019-10-21 03:30 | 107.86 | 99.9
2019-10-21 04:00 | 107.1 | 99.02
2019-10-21 04:30 | 98 | 89.4
2019-10-21 05:00 | 106.53 | 99.13
2019-10-21 05:30 | 113.53 | 106.87
2019-10-21 06:00 | 114.12 | 107.39
2019-10-21 06:30 | 102.98 | 93.78
2019-10-21 07:00 | 106.07 | 95.52
2019-10-21 07:30 | 97.45 | 81.84
2019-10-21 08:00 | 96.98 | 79.37
2019-10-21 08:30 | 96.14 | 76.84
2019-10-21 09:00 | 96.09 | 76.56
2019-10-21 09:30 | 94.26 | 74.4
2019-10-21 10:00 | 90.04 | 73.34
2019-10-21 10:30 | 95.12 | 77.76
2019-10-21 11:00 | 99.69 | 81.31
2019-10-21 11:30 | 93.93 | 74.99
2019-10-21 12:00 | 90.44 | 70.19
2019-10-21 12:30 | 100.6 | 81.26
2019-10-21 13:00 | 92.7 | 74.24
2019-10-21 13:30 | 97.67 | 80.35
2019-10-21 14:00 | 96.8 | 80.19
2019-10-21 14:30 | 101.56 | 87.46
2019-10-21 15:00 | 105.04 | 89.42
2019-10-21 15:30 | 106.65 | 94.31
2019-10-21 16:00 | 106.88 | 91.33
2019-10-21 16:30 | 101.14 | 89.5
2019-10-21 17:00 | 101.75 | 93.47
2019-10-21 17:30 | 112.49 | 104.32
2019-10-21 18:00 | 109.73 | 102.27
2019-10-21 18:30 | 102.97 | 96.61
2019-10-21 19:00 | 118.71 | 111.09
2019-10-21 19:30 | 118.24 | 111.03
2019-10-21 20:00 | 121.33 | 114.47
2019-10-21 20:30 | 117.92 | 111.48
2019-10-21 21:00 | 114.04 | 107.19
2019-10-21 21:30 | 113 | 106.06
2019-10-21 22:00 | 109.99 | 103.5
2019-10-21 22:30 | 117.68 | 110.58
2019-10-21 23:00 | 116.42 | 109.14
2019-10-21 23:30 | 110.92 | 104.39
2019-10-22 | 117.64 | 110.72
2019-10-22 00:30 | 123.56 | 116.55
2019-10-22 01:00 | 117.95 | 110.87
2019-10-22 01:30 | 127.8 | 120.78
2019-10-22 02:00 | 117.11 | 109.81
2019-10-22 02:30 | 108.76 | 101.65
2019-10-22 03:00 | 107.38 | 99.18
2019-10-22 03:30 | 103.08 | 94.99
2019-10-22 04:00 | 103.52 | 95.94
2019-10-22 04:30 | 103.51 | 95.78
2019-10-22 05:00 | 106.94 | 98.78
2019-10-22 05:30 | 109.5 | 102.25
2019-10-22 06:00 | 106.55 | 99.79
2019-10-22 06:30 | 105.32 | 95.23
2019-10-22 07:00 | 105.62 | 95.15
2019-10-22 07:30 | 97.07 | 81.48
2019-10-22 08:00 | 96.36 | 79.1
2019-10-22 08:30 | 82.33 | 63.12
2019-10-22 09:00 | 88.58 | 67.27
2019-10-22 09:30 | 91.11 | 69.52
2019-10-22 10:00 | 93.88 | 74.08
2019-10-22 10:30 | 98.62 | 83.25
2019-10-22 11:00 | 99.92 | 89.12
2019-10-22 11:30 | 103.23 | 91.19
2019-10-22 12:00 | 103.02 | 81.96
2019-10-22 12:30 | 97.26 | 76.91
2019-10-22 13:00 | 104.81 | 85.07
2019-10-22 13:30 | 100.05 | 79.59
2019-10-22 14:00 | 96.86 | 77.76
2019-10-22 14:30 | 95.98 | 74.31
2019-10-22 15:00 | 101.46 | 79.48
2019-10-22 15:30 | 97.54 | 77.25
2019-10-22 16:00 | 97.68 | 78.73
2019-10-22 16:30 | 99.18 | 81.64
2019-10-22 17:00 | 96.75 | 82.1
2019-10-22 17:30 | 100.25 | 90.5
2019-10-22 18:00 | 102.65 | 96.33
2019-10-22 18:30 | 100.09 | 94.48
2019-10-22 19:00 | 107.1 | 101.82
2019-10-22 19:30 | 109.14 | 103.73
2019-10-22 20:00 | 107.91 | 101.9
2019-10-22 20:30 | 110.31 | 104.36
2019-10-22 21:00 | 104.15 | 98.3
2019-10-22 21:30 | 119.44 | 113.63
2019-10-22 22:00 | 106.63 | 101.12
2019-10-22 22:30 | 109.23 | 103.79
2019-10-22 23:00 | 103.58 | 98.61
2019-10-22 23:30 | 101.42 | 96.54
2019-10-23 | 103.55 | 98.52
2019-10-23 00:30 | 102.47 | 97.81
2019-10-23 01:00 | 104.21 | 99.61
2019-10-23 01:30 | 106.35 | 101.93
2019-10-23 02:00 | 95.77 | 91.02
2019-10-23 02:30 | 96.49 | 92.11
2019-10-23 03:00 | 96.5 | 92.01
2019-10-23 03:30 | 92.09 | 87.64
2019-10-23 04:00 | 96.07 | 91.42
2019-10-23 04:30 | 100.4 | 96.04
2019-10-23 05:00 | 101.83 | 96.47
2019-10-23 05:30 | 94.79 | 89.87
2019-10-23 06:00 | 100.85 | 95.26
2019-10-23 06:30 | 81.94 | 74.12
2019-10-23 07:00 | 83.63 | 73.2
2019-10-23 07:30 | 89.66 | 77.11
2019-10-23 08:00 | 87.05 | 74.85
2019-10-23 08:30 | 84.37 | 70.89
2019-10-23 09:00 | 89.69 | 76.57
2019-10-23 09:30 | 99.66 | 85.52
2019-10-23 10:00 | 88.52 | 74.81
2019-10-23 10:30 | 92.43 | 78.86
2019-10-23 11:00 | 89.88 | 77.11
2019-10-23 11:30 | 79.67 | 64.21
2019-10-23 12:00 | 77.44 | 62.87
2019-10-23 12:30 | 89.34 | 74.1
2019-10-23 13:00 | 90.49 | 75.09
2019-10-23 13:30 | 86.78 | 71.71
2019-10-23 14:00 | 87.7 | 73.31
2019-10-23 14:30 | 91.09 | 76.15
2019-10-23 15:00 | 88 | 72.38
2019-10-23 15:30 | 81.55 | 65.69
2019-10-23 16:00 | 80.04 | 64.99
2019-10-23 16:30 | 84.84 | 72.23
2019-10-23 17:00 | 90.78 | 79.84
2019-10-23 17:30 | 88.73 | 80.91
2019-10-23 18:00 | 90.69 | 84.29
2019-10-23 18:30 | 95.23 | 89.91
2019-10-23 19:00 | 107.73 | 103.38
2019-10-23 19:30 | 103.96 | 99.98
2019-10-23 20:00 | 98.35 | 94.17
2019-10-23 20:30 | 111.2 | 107.27
2019-10-23 21:00 | 109.97 | 105.11
2019-10-23 21:30 | 101.88 | 96.01
2019-10-23 22:00 | 97.98 | 91.52
2019-10-23 22:30 | 98.96 | 91.86
2019-10-23 23:00 | 99.58 | 92.25
2019-10-23 23:30 | 97.09 | 89.18
2019-10-24 | 98.7 | 92.96
2019-10-24 00:30 | 106.18 | 101.04
2019-10-24 01:00 | 106.2 | 100.78
2019-10-24 01:30 | 112.86 | 107.45
2019-10-24 02:00 | 109.75 | 104.46
2019-10-24 02:30 | 103.94 | 98.05
2019-10-24 03:00 | 99.39 | 93.19
2019-10-24 03:30 | 99.99 | 93.96
2019-10-24 04:00 | 99.31 | 93.14
2019-10-24 04:30 | 101.86 | 96.3
2019-10-24 05:00 | 101.43 | 95.93
2019-10-24 05:30 | 102.04 | 96.63
2019-10-24 06:00 | 96.07 | 90.67
2019-10-24 06:30 | 87.58 | 78.83
2019-10-24 07:00 | 90.9 | 79.37
2019-10-24 07:30 | 83.75 | 67.98
2019-10-24 08:00 | 87.13 | 70.78
2019-10-24 08:30 | 91.35 | 75.63
2019-10-24 09:00 | 95.46 | 79.54
2019-10-24 09:30 | 87.62 | 70.64
2019-10-24 10:00 | 81.3 | 62.96
2019-10-24 10:30 | 88.34 | 71.19
2019-10-24 11:00 | 93.88 | 75.85
2019-10-24 11:30 | 92.37 | 73.14
2019-10-24 12:00 | 88.71 | 69.47
2019-10-24 12:30 | 90.99 | 73.17
2019-10-24 13:00 | 83.32 | 65.64
2019-10-24 13:30 | 95.24 | 80
2019-10-24 14:00 | 96.29 | 79.94
2019-10-24 14:30 | 106.47 | 91.22
2019-10-24 15:00 | 104.43 | 91.36
2019-10-24 15:30 | 103.4 | 89.47
2019-10-24 16:00 | 93.2 | 75.22
2019-10-24 16:30 | 91.63 | 73.45
2019-10-24 17:00 | 102.52 | 89.58
2019-10-24 17:30 | 98.13 | 89.67
2019-10-24 18:00 | 102.63 | 96
2019-10-24 18:30 | 98.6 | 91.67
2019-10-24 19:00 | 112.11 | 105.78
2019-10-24 19:30 | 108.75 | 102.79
2019-10-24 20:00 | 112.63 | 106.59
2019-10-24 20:30 | 107.23 | 100.86
2019-10-24 21:00 | 96.36 | 89.38
2019-10-24 21:30 | 103.19 | 97.03
2019-10-24 22:00 | 104.82 | 98.1
2019-10-24 22:30 | 109.57 | 102.69
2019-10-24 23:00 | 106.82 | 99.31
2019-10-24 23:30 | 99.86 | 92.52
2019-10-25 | 97.79 | 90.38
2019-10-25 00:30 | 103.64 | 96.18
2019-10-25 01:00 | 106.15 | 98.9
2019-10-25 01:30 | 118.15 | 110.32
2019-10-25 02:00 | 115.14 | 107.79
2019-10-25 02:30 | 107.3 | 100.22
2019-10-25 03:00 | 107.62 | 100.91
2019-10-25 03:30 | 112.91 | 105.82
2019-10-25 04:00 | 102.78 | 95.87
2019-10-25 04:30 | 110.36 | 103.14
2019-10-25 05:00 | 116.49 | 108.46
2019-10-25 05:30 | 111.83 | 103.58
2019-10-25 06:00 | 109.16 | 100.66
2019-10-25 06:30 | 102.86 | 91.12
2019-10-25 07:00 | 106.53 | 92.04
2019-10-25 07:30 | 100.69 | 82.46
2019-10-25 08:00 | 96.93 | 77.82
2019-10-25 08:30 | 100.81 | 80.05
2019-10-25 09:00 | 103.68 | 80.39
2019-10-25 09:30 | 108.7 | 85.15
2019-10-25 10:00 | 107.28 | 85.72
2019-10-25 10:30 | 104.21 | 83.2
2019-10-25 11:00 | 102.2 | 80.21
2019-10-25 11:30 | 97.05 | 75.32
2019-10-25 12:00 | 102.21 | 81.45
2019-10-25 12:30 | 101.05 | 80.14
2019-10-25 13:00 | 95.73 | 75.74
2019-10-25 13:30 | 103.09 | 83.77
2019-10-25 14:00 | 100.89 | 81.19
2019-10-25 14:30 | 109.19 | 88.89
2019-10-25 15:00 | 101.74 | 82.93
2019-10-25 15:30 | 96.92 | 78.34
2019-10-25 16:00 | 97.16 | 80.82
2019-10-25 16:30 | 101.13 | 85.79
2019-10-25 17:00 | 115.81 | 102.48
2019-10-25 17:30 | 117.22 | 107.09
2019-10-25 18:00 | 115.22 | 107.46
2019-10-25 18:30 | 108.7 | 101.29
2019-10-25 19:00 | 108.12 | 101.02
2019-10-25 19:30 | 113.9 | 106.91
2019-10-25 20:00 | 117 | 109.79
2019-10-25 20:30 | 123.79 | 116.42
2019-10-25 21:00 | 120.4 | 113.34
2019-10-25 21:30 | 114.81 | 106.93
2019-10-25 22:00 | 111.82 | 103.6
2019-10-25 22:30 | 112.73 | 105.24
2019-10-25 23:00 | 110.24 | 102.38
2019-10-25 23:30 | 115.67 | 108.41
2019-10-26 | 113.33 | 105.71
2019-10-26 00:30 | 111.07 | 103.88
2019-10-26 01:00 | 113.21 | 105.41
2019-10-26 01:30 | 106.95 | 99.97
2019-10-26 02:00 | 113.23 | 106.53
2019-10-26 02:30 | 113.99 | 107.3
2019-10-26 03:00 | 109.18 | 102.65
2019-10-26 03:30 | 107.31 | 100.53
2019-10-26 04:00 | 109.49 | 99.98
2019-10-26 04:30 | 112.23 | 98.75
2019-10-26 05:00 | 115.27 | 101.03
2019-10-26 05:30 | 113.24 | 99.54
2019-10-26 06:00 | 107.63 | 95.25
2019-10-26 06:30 | 98.27 | 82.15
2019-10-26 07:00 | 97.24 | 79.49
2019-10-26 07:30 | 100.72 | 86.25
2019-10-26 08:00 | 104.4 | 93.31
2019-10-26 08:30 | 102.95 | 90.52
2019-10-26 09:00 | 98.47 | 83.31
2019-10-26 09:30 | 99.75 | 88.44
2019-10-26 10:00 | 106.19 | 97.12
2019-10-26 10:30 | 101.68 | 90.85
2019-10-26 11:00 | 102.54 | 87.02
2019-10-26 11:30 | 106.7 | 86.18
2019-10-26 12:00 | 112.89 | 97.2
2019-10-26 12:30 | 113.09 | 103.87
2019-10-26 13:00 | 108.43 | 98.48
2019-10-26 13:30 | 110.5 | 100.29
2019-10-26 14:00 | 109.29 | 98.93
2019-10-26 14:30 | 115.45 | 105.14
2019-10-26 15:00 | 117.49 | 106.73
2019-10-26 15:30 | 115.52 | 104.76
2019-10-26 16:00 | 115.86 | 105.57
2019-10-26 16:30 | 112.5 | 102.18
2019-10-26 17:00 | 110.84 | 100.24
2019-10-26 17:30 | 122.95 | 112.23
2019-10-26 18:00 | 117.72 | 107.51
2019-10-26 18:30 | 108.52 | 97.67
2019-10-26 19:00 | 113.56 | 102.96
2019-10-26 19:30 | 114.07 | 103.34
2019-10-26 20:00 | 122.44 | 111.57
2019-10-26 20:30 | 120.26 | 109.63
2019-10-26 21:00 | 119.38 | 108.65
2019-10-26 21:30 | 119.11 | 107.84
2019-10-26 22:00 | 115.9 | 106.42
2019-10-26 22:30 | 102.15 | 93.14
2019-10-26 23:00 | 100.02 | 90.67
2019-10-26 23:30 | 114.42 | 105.11
2019-10-27 | 102.65 | 92.87
2019-10-27 00:30 | 109.54 | 99.29
2019-10-27 01:00 | 109.77 | 98.56
2019-10-27 01:30 | 98.47 | 86.19
2019-10-27 02:00 | 100.07 | 88.27
2019-10-27 02:30 | 98.8 | 87.18
2019-10-27 03:00 | 102.04 | 90.91
2019-10-27 03:30 | 103.59 | 92.39
2019-10-27 04:00 | 101.98 | 91.27
2019-10-27 04:30 | 105.54 | 93.88
2019-10-27 05:00 | 110.61 | 99.56
2019-10-27 05:30 | 119.14 | 106.36
2019-10-27 06:00 | 112.73 | 100.2
2019-10-27 06:30 | 112.69 | 98.91
2019-10-27 07:00 | 111.74 | 100.21
2019-10-27 07:30 | 117.85 | 106.03
2019-10-27 08:00 | 112.8 | 100.51
2019-10-27 08:30 | 120.66 | 106.99
2019-10-27 09:00 | 118.75 | 105.61
2019-10-27 09:30 | 113.19 | 99.18
2019-10-27 10:00 | 120.13 | 106.35
2019-10-27 10:30 | 110.44 | 97.73
2019-10-27 11:00 | 111.72 | 99.12
2019-10-27 11:30 | 103.47 | 91.62
2019-10-27 12:00 | 102.67 | 90.3
2019-10-27 12:30 | 113.75 | 99.33
2019-10-27 13:00 | 109.87 | 96.57
2019-10-27 13:30 | 113.71 | 100.33
2019-10-27 14:00 | 122.04 | 107.85
2019-10-27 14:30 | 120.63 | 106
2019-10-27 15:00 | 118.43 | 105.94
2019-10-27 15:30 | 116.97 | 104.36
2019-10-27 16:00 | 120.94 | 107.82
2019-10-27 16:30 | 121.48 | 108.05
2019-10-27 17:00 | 128.67 | 113.92
2019-10-27 17:30 | 127.3 | 113.97
2019-10-27 18:00 | 133.12 | 119.25
2019-10-27 18:30 | 119.29 | 103.64
2019-10-27 19:00 | 125.43 | 111.21
2019-10-27 19:30 | 124.56 | 110.32
2019-10-27 20:00 | 124.2 | 110.61
2019-10-27 20:30 | 116.19 | 102.58
2019-10-27 21:00 | 116.48 | 102.62
2019-10-27 21:30 | 116.91 | 105.04
2019-10-27 22:00 | 117.19 | 105.05
2019-10-27 22:30 | 115.43 | 105.4
2019-10-27 23:00 | 106.57 | 97.66
2019-10-27 23:30 | 102.93 | 93.94
2019-10-28 | 108.62 | 99.91
2019-10-28 00:30 | 113.47 | 103.8
2019-10-28 01:00 | 107.78 | 96.94
2019-10-28 01:30 | 104.07 | 94.31
2019-10-28 02:00 | 104.22 | 94.58
2019-10-28 02:30 | 111.34 | 102.35
2019-10-28 03:00 | 110.08 | 100.84
2019-10-28 03:30 | 108.05 | 99.44
2019-10-28 04:00 | 109.49 | 99.9
2019-10-28 04:30 | 112.32 | 102.99
2019-10-28 05:00 | 116.94 | 107.03
2019-10-28 05:30 | 117.74 | 108.56
2019-10-28 06:00 | 110.84 | 101.93
2019-10-28 06:30 | 105.29 | 96.38
2019-10-28 07:00 | 112.34 | 103.06
2019-10-28 07:30 | 119.55 | 109.02
2019-10-28 08:00 | 112.16 | 102.39
2019-10-28 08:30 | 114.53 | 103.93
2019-10-28 09:00 | 121.1 | 109.59
2019-10-28 09:30 | 115.94 | 104.24
2019-10-28 10:00 | 111.73 | 100.33
2019-10-28 10:30 | 115.89 | 103.81
2019-10-28 11:00 | 117.4 | 105.88
2019-10-28 11:30 | 120.38 | 108.22
2019-10-28 12:00 | 114.6 | 101.48
2019-10-28 12:30 | 117.68 | 105.39
2019-10-28 13:00 | 114.82 | 103.25
2019-10-28 13:30 | 114.84 | 103.7
2019-10-28 14:00 | 105.69 | 87.49
2019-10-28 14:30 | 97.64 | 73.6
2019-10-28 15:00 | 112.14 | 91.09
2019-10-28 15:30 | 110.87 | 89.59
2019-10-28 16:00 | 113.85 | 94.51
2019-10-28 16:30 | 104.72 | 85.58
2019-10-28 17:00 | 107.02 | 92.17
2019-10-28 17:30 | 115.08 | 104.52
2019-10-28 18:00 | 116.28 | 108
2019-10-28 18:30 | 110.25 | 101.84
2019-10-28 19:00 | 119.61 | 111.19
2019-10-28 19:30 | 118.06 | 109.63
2019-10-28 20:00 | 113.88 | 105.24
2019-10-28 20:30 | 113.13 | 104.15
2019-10-28 21:00 | 112.31 | 103.97
2019-10-28 21:30 | 108.06 | 99.83
2019-10-28 22:00 | 105.67 | 97.17
2019-10-28 22:30 | 94.34 | 85.16
2019-10-28 23:00 | 91.31 | 82.28
2019-10-28 23:30 | 89.17 | 80.78
2019-10-29 | 98.85 | 89.3
2019-10-29 00:30 | 106.63 | 96.3
2019-10-29 01:00 | 120.29 | 109.7
2019-10-29 01:30 | 117.08 | 107.03
2019-10-29 02:00 | 113.78 | 103.75
2019-10-29 02:30 | 121.45 | 110.63
2019-10-29 03:00 | 110.75 | 101.15
2019-10-29 03:30 | 106.6 | 97.64
2019-10-29 04:00 | 118.34 | 109.41
2019-10-29 04:30 | 112.44 | 103.83
2019-10-29 05:00 | 106.66 | 97.24
2019-10-29 05:30 | 103.55 | 94.89
2019-10-29 06:00 | 107.32 | 99.03
2019-10-29 06:30 | 100.16 | 88.61
2019-10-29 07:00 | 104.73 | 94.14
2019-10-29 07:30 | 100.28 | 88.63
2019-10-29 08:00 | 100.52 | 88.75
2019-10-29 08:30 | 101.08 | 82.67
2019-10-29 09:00 | 101.71 | 83.3
2019-10-29 09:30 | 107.85 | 89.06
2019-10-29 10:00 | 100.93 | 82.21
2019-10-29 10:30 | 100.94 | 82.12
2019-10-29 11:00 | 104.17 | 85.82
2019-10-29 11:30 | 107.81 | 92.29
2019-10-29 12:00 | 101.34 | 84.65
2019-10-29 12:30 | 103.37 | 89.84
2019-10-29 13:00 | 108.26 | 93.37
2019-10-29 13:30 | 110.52 | 95.79
2019-10-29 14:00 | 115 | 97.23
2019-10-29 14:30 | 106.18 | 90.89
2019-10-29 15:00 | 105.45 | 93.22
2019-10-29 15:30 | 97.45 | 85.77
2019-10-29 16:00 | 107.46 | 98.18
2019-10-29 16:30 | 106.37 | 97.1
2019-10-29 17:00 | 111.57 | 102.98
2019-10-29 17:30 | 115.95 | 107.51
2019-10-29 18:00 | 118.08 | 110.08
2019-10-29 18:30 | 118.85 | 110.5
2019-10-29 19:00 | 118.06 | 110.33
2019-10-29 19:30 | 125.09 | 116.23
2019-10-29 20:00 | 121.07 | 112.59
2019-10-29 20:30 | 118.01 | 109.93
2019-10-29 21:00 | 117.43 | 108.49
2019-10-29 21:30 | 120.7 | 111.9
2019-10-29 22:00 | 115.68 | 106.61
2019-10-29 22:30 | 115.64 | 106.25
2019-10-29 23:00 | 121.02 | 112.32
2019-10-29 23:30 | 119.94 | 110.89
2019-10-30 | 111.23 | 103.63
2019-10-30 00:30 | 104.27 | 95.77
2019-10-30 01:00 | 109.04 | 100.84
2019-10-30 01:30 | 100.2 | 92.32
2019-10-30 02:00 | 104.24 | 96.06
2019-10-30 02:30 | 104.61 | 96.86
2019-10-30 03:00 | 107.38 | 99.42
2019-10-30 03:30 | 104.73 | 97.06
2019-10-30 04:00 | 112.62 | 104.94
2019-10-30 04:30 | 112 | 104.36
2019-10-30 05:00 | 110.64 | 102.93
2019-10-30 05:30 | 107.85 | 99.86
2019-10-30 06:00 | 107.25 | 99.01
2019-10-30 06:30 | 105.02 | 96.34
2019-10-30 07:00 | 100.85 | 91.64
2019-10-30 07:30 | 95.65 | 84.54
2019-10-30 08:00 | 93.12 | 84.52
2019-10-30 08:30 | 95.61 | 86.69
2019-10-30 09:00 | 105.69 | 96.71
2019-10-30 09:30 | 96.72 | 84.93
2019-10-30 10:00 | 89.01 | 76.98
2019-10-30 10:30 | 95.4 | 82.77
2019-10-30 11:00 | 95.4 | 82.5
2019-10-30 11:30 | 87.19 | 72.66
2019-10-30 12:00 | 91.85 | 76.28
2019-10-30 12:30 | 98.86 | 84.91
2019-10-30 13:00 | 96.35 | 86.2
2019-10-30 13:30 | 100.44 | 89.78
2019-10-30 14:00 | 99.4 | 87.99
2019-10-30 14:30 | 99.91 | 86.92
2019-10-30 15:00 | 96.54 | 85.98
2019-10-30 15:30 | 99.84 | 89.99
2019-10-30 16:00 | 95.34 | 87.29
2019-10-30 16:30 | 108.43 | 101.28
2019-10-30 17:00 | 98.85 | 89.87
2019-10-30 17:30 | 114.03 | 107.5
2019-10-30 18:00 | 119.35 | 112.87
2019-10-30 18:30 | 111.79 | 105.14
2019-10-30 19:00 | 114.9 | 107.49
2019-10-30 19:30 | 113.62 | 105.83
2019-10-30 20:00 | 110.21 | 103.02
2019-10-30 20:30 | 116.38 | 109.19
2019-10-30 21:00 | 115.91 | 108.85
2019-10-30 21:30 | 114.7 | 107.26
2019-10-30 22:00 | 107.57 | 100.67
2019-10-30 22:30 | 113.06 | 105.82
2019-10-30 23:00 | 109.71 | 101.8
2019-10-30 23:30 | 109.93 | 101.98
2019-10-31 | 113.92 | 105.63
2019-10-31 00:30 | 106.9 | 98.21
2019-10-31 01:00 | 108.62 | 100.03
2019-10-31 01:30 | 105.94 | 98.73
2019-10-31 02:00 | 114.86 | 108.13
2019-10-31 02:30 | 121.31 | 113.66
2019-10-31 03:00 | 117.13 | 109.35
2019-10-31 03:30 | 113.85 | 106.03
2019-10-31 04:00 | 107.35 | 99.89
2019-10-31 04:30 | 110.56 | 102.57
2019-10-31 05:00 | 108.04 | 100.42
2019-10-31 05:30 | 103.72 | 96.01
2019-10-31 06:00 | 106.51 | 99.14
2019-10-31 06:30 | 96.51 | 88.18
2019-10-31 07:00 | 100.16 | 90.28
2019-10-31 07:30 | 98.55 | 88.62
2019-10-31 08:00 | 97.79 | 85.62
2019-10-31 08:30 | 105.89 | 94.18
2019-10-31 09:00 | 98.22 | 85.36
2019-10-31 09:30 | 91.9 | 78.34
2019-10-31 10:00 | 84.69 | 64.56
2019-10-31 10:30 | 92.17 | 69.75
2019-10-31 11:00 | 95.94 | 74.32
2019-10-31 11:30 | 94.05 | 73.16
2019-10-31 12:00 | 89.47 | 70.07
2019-10-31 12:30 | 107.85 | 88.32
2019-10-31 13:00 | 101.82 | 83.51
2019-10-31 13:30 | 96.51 | 78.83
2019-10-31 14:00 | 95.58 | 80.03
2019-10-31 14:30 | 97.32 | 82.39
2019-10-31 15:00 | 93.8 | 79.83
2019-10-31 15:30 | 97.71 | 85.15
2019-10-31 16:00 | 98.48 | 78.35
2019-10-31 16:30 | 96.74 | 82.5
2019-10-31 17:00 | 100.33 | 91.58
2019-10-31 17:30 | 109.37 | 100.45
2019-10-31 18:00 | 97.64 | 88.96
2019-10-31 18:30 | 102.62 | 95.35
2019-10-31 19:00 | 100.75 | 93.86
2019-10-31 19:30 | 110.31 | 102.6
2019-10-31 20:00 | 110.94 | 103.9
2019-10-31 20:30 | 119.02 | 112.2
2019-10-31 21:00 | 115.15 | 107.96
2019-10-31 21:30 | 101.58 | 94.21
2019-10-31 22:00 | 109.93 | 103.02
2019-10-31 22:30 | 108.61 | 101.39
2019-10-31 23:00 | 118.47 | 111.13
2019-10-31 23:30 | 115.31 | 108.88
2019-11-01 | 109.99 | 103.18
2019-11-01 00:30 | 120.34 | 112.9
2019-11-01 01:00 | 110.16 | 103.19
2019-11-01 01:30 | 116.18 | 108.41
2019-11-01 02:00 | 115.8 | 108.89
2019-11-01 02:30 | 109.32 | 102.62
2019-11-01 03:00 | 112.93 | 105.66
2019-11-01 03:30 | 105.8 | 98.78
2019-11-01 04:00 | 112.12 | 104.53
2019-11-01 04:30 | 105.85 | 98.7
2019-11-01 05:00 | 109.92 | 102.52
2019-11-01 05:30 | 112.78 | 105.09
2019-11-01 06:00 | 108.05 | 101.58
2019-11-01 06:30 | 97.54 | 90.09
2019-11-01 07:00 | 109.41 | 97.72
2019-11-01 07:30 | 107.14 | 89.15
2019-11-01 08:00 | 98.38 | 78.09
2019-11-01 08:30 | 105.37 | 86.24
2019-11-01 09:00 | 104.34 | 88.27
2019-11-01 09:30 | 107.18 | 91.06
2019-11-01 10:00 | 98.56 | 84.35
2019-11-01 10:30 | 99.8 | 82.35
2019-11-01 11:00 | 106.77 | 92.66
2019-11-01 11:30 | 102.62 | 87.13
2019-11-01 12:00 | 101.89 | 87.16
2019-11-01 12:30 | 98.78 | 79.03
2019-11-01 13:00 | 109.37 | 91.28
2019-11-01 13:30 | 106.99 | 91.47
2019-11-01 14:00 | 101.54 | 83.41
2019-11-01 14:30 | 104.98 | 88.52
2019-11-01 15:00 | 102.8 | 83.08
2019-11-01 15:30 | 92.64 | 77.56
2019-11-01 16:00 | 103.33 | 89.75
2019-11-01 16:30 | 88.93 | 76.23
2019-11-01 17:00 | 93.74 | 81.56
2019-11-01 17:30 | 104.1 | 94.73
2019-11-01 18:00 | 105.81 | 98.73
2019-11-01 18:30 | 96.6 | 90.11
2019-11-01 19:00 | 109.87 | 103.94
2019-11-01 19:30 | 115.31 | 109.57
2019-11-01 20:00 | 117.57 | 111.13
2019-11-01 20:30 | 120.76 | 114.48
2019-11-01 21:00 | 109.42 | 102.68
2019-11-01 21:30 | 108.87 | 101.5
2019-11-01 22:00 | 104.72 | 98.5
2019-11-01 22:30 | 102.73 | 96.43
2019-11-01 23:00 | 98.48 | 91.63
2019-11-01 23:30 | 100.19 | 93.64
2019-11-02 | 104.38 | 98.29
2019-11-02 00:30 | 101.32 | 94.8
2019-11-02 01:00 | 105.98 | 99.36
2019-11-02 01:30 | 102.61 | 95.74
2019-11-02 02:00 | 99.76 | 92.3
2019-11-02 02:30 | 109.39 | 102.21
2019-11-02 03:00 | 104.69 | 97.79
2019-11-02 03:30 | 93.54 | 86.37
2019-11-02 04:00 | 102.86 | 96.48
2019-11-02 04:30 | 98.17 | 92.44
2019-11-02 05:00 | 93.08 | 86.72
2019-11-02 05:30 | 102.61 | 96.05
2019-11-02 06:00 | 98.38 | 92
2019-11-02 06:30 | 86.41 | 77.02
2019-11-02 07:00 | 93.54 | 80.98
2019-11-02 07:30 | 99.26 | 83.64
2019-11-02 08:00 | 97.42 | 83.82
2019-11-02 08:30 | 98.28 | 85.06
2019-11-02 09:00 | 98.2 | 81.58
2019-11-02 09:30 | 98.05 | 79.17
2019-11-02 10:00 | 99.18 | 80.17
2019-11-02 10:30 | 103.88 | 86.39
2019-11-02 11:00 | 100.64 | 82.3
2019-11-02 11:30 | 101.97 | 82.57
2019-11-02 12:00 | 102.19 | 85.25
2019-11-02 12:30 | 103.16 | 85.88
2019-11-02 13:00 | 95.67 | 76.95
2019-11-02 13:30 | 106.02 | 89.23
2019-11-02 14:00 | 105.05 | 88.25
2019-11-02 14:30 | 102.89 | 86.64
2019-11-02 15:00 | 96.56 | 81.17
2019-11-02 15:30 | 102.26 | 87.47
2019-11-02 16:00 | 99.21 | 82.98
2019-11-02 16:30 | 102.6 | 87.63
2019-11-02 17:00 | 93.88 | 80.56
2019-11-02 17:30 | 105.78 | 95.67
2019-11-02 18:00 | 111.56 | 104.35
2019-11-02 18:30 | 103.04 | 95.5
2019-11-02 19:00 | 114.06 | 106.64
2019-11-02 19:30 | 107.84 | 100.64
2019-11-02 20:00 | 112.1 | 104.85
2019-11-02 20:30 | 112.98 | 105.59
2019-11-02 21:00 | 115.34 | 107.39
2019-11-02 21:30 | 108.07 | 100.58
2019-11-02 22:00 | 112.35 | 105.18
2019-11-02 22:30 | 109.91 | 103.15
2019-11-02 23:00 | 112.73 | 105.27
2019-11-02 23:30 | 114.3 | 106.56
2019-11-03 | 114.38 | 107.19
2019-11-03 00:30 | 120.52 | 113.21
2019-11-03 01:00 | 109.12 | 102.72
2019-11-03 01:30 | 98.68 | 91.61
2019-11-03 02:00 | 100.42 | 93.59
2019-11-03 02:30 | 103.07 | 95.87
2019-11-03 03:00 | 98.37 | 90.63
2019-11-03 03:30 | 96.99 | 89.91
2019-11-03 04:00 | 100.85 | 93.84
2019-11-03 04:30 | 98.13 | 91.05
2019-11-03 05:00 | 104.54 | 98.4
2019-11-03 05:30 | 98.64 | 92.57
2019-11-03 06:00 | 103.54 | 97.81
2019-11-03 06:30 | 94.38 | 84.13
2019-11-03 07:00 | 95.33 | 82.35
2019-11-03 07:30 | 96.25 | 81.42
2019-11-03 08:00 | 89.14 | 72.91
2019-11-03 08:30 | 92.84 | 73.91
2019-11-03 09:00 | 95.8 | 78.08
2019-11-03 09:30 | 96.39 | 79.9
2019-11-03 10:00 | 94.39 | 78.48
2019-11-03 10:30 | 91.58 | 76.56
2019-11-03 11:00 | 91.53 | 74.41
2019-11-03 11:30 | 92.26 | 76.51
2019-11-03 12:00 | 100.73 | 82.76
2019-11-03 12:30 | 100.38 | 83.24
2019-11-03 13:00 | 99.13 | 82.28
2019-11-03 13:30 | 104.78 | 85.73
2019-11-03 14:00 | 102.14 | 84.19
2019-11-03 14:30 | 102.46 | 83.92
2019-11-03 15:00 | 101.73 | 86.04
2019-11-03 15:30 | 110.99 | 96.27
2019-11-03 16:00 | 105.79 | 89.1
2019-11-03 16:30 | 110.42 | 93.45
2019-11-03 17:00 | 102.87 | 87.71
2019-11-03 17:30 | 112.27 | 101.3
2019-11-03 18:00 | 117.31 | 109.09
2019-11-03 18:30 | 106.47 | 98.78
2019-11-03 19:00 | 117.26 | 110.15
2019-11-03 19:30 | 116.77 | 109.21
2019-11-03 20:00 | 116.59 | 108.93
2019-11-03 20:30 | 123.47 | 115.67
2019-11-03 21:00 | 115.84 | 107.53
2019-11-03 21:30 | 116.82 | 108.56
2019-11-03 22:00 | 110.97 | 102.39
2019-11-03 22:30 | 103.92 | 95.67
2019-11-03 23:00 | 98.05 | 89.7
2019-11-03 23:30 | 101.16 | 93.41
2019-11-04 | 98.76 | 90.71
2019-11-04 00:30 | 102.76 | 94.25
2019-11-04 01:00 | 102.14 | 93.56
2019-11-04 01:30 | 108.32 | 99.73
2019-11-04 02:00 | 108.58 | 99.99
2019-11-04 02:30 | 106.2 | 98.64
2019-11-04 03:00 | 110.8 | 102.25
2019-11-04 03:30 | 104.42 | 96.82
2019-11-04 04:00 | 102.03 | 94.53
2019-11-04 04:30 | 103.66 | 96.3
2019-11-04 05:00 | 109.99 | 102.13
2019-11-04 05:30 | 105.07 | 97.23
2019-11-04 06:00 | 109.2 | 101.79
2019-11-04 06:30 | 97.03 | 88.39
2019-11-04 07:00 | 111.21 | 102.39
2019-11-04 07:30 | 112.47 | 102.38
2019-11-04 08:00 | 106.74 | 95.22
2019-11-04 08:30 | 105.17 | 90.73
2019-11-04 09:00 | 104.23 | 89.11
2019-11-04 09:30 | 114.64 | 100.08
2019-11-04 10:00 | 111.11 | 93.75
2019-11-04 10:30 | 95.64 | 75.03
2019-11-04 11:00 | 101.35 | 79.72
2019-11-04 11:30 | 102.08 | 83.31
2019-11-04 12:00 | 89.98 | 74.61
2019-11-04 12:30 | 93.15 | 81.18
2019-11-04 13:00 | 99.76 | 88.25
2019-11-04 13:30 | 89.3 | 73.68
2019-11-04 14:00 | 102.43 | 90.06
2019-11-04 14:30 | 110.24 | 93.92
2019-11-04 15:00 | 106.83 | 88.25
2019-11-04 15:30 | 115.62 | 104.91
2019-11-04 16:00 | 110.14 | 99.69
2019-11-04 16:30 | 109.27 | 99.93
2019-11-04 17:00 | 114.23 | 105.83
2019-11-04 17:30 | 119.99 | 112.99
2019-11-04 18:00 | 118.87 | 112.08
2019-11-04 18:30 | 115.73 | 108.02
2019-11-04 19:00 | 115.32 | 107.5
2019-11-04 19:30 | 118.66 | 110.78
2019-11-04 20:00 | 124.6 | 117.16
2019-11-04 20:30 | 126 | 118.48
2019-11-04 21:00 | 111.52 | 104
2019-11-04 21:30 | 119.06 | 111.63
2019-11-04 22:00 | 118.6 | 110.89
2019-11-04 22:30 | 116.42 | 108.7
2019-11-04 23:00 | 108.87 | 101.77
2019-11-04 23:30 | 101.04 | 93.96
2019-11-05 | 100.19 | 91.66
2019-11-05 00:30 | 99.05 | 91.28
2019-11-05 01:00 | 101.61 | 94.6
2019-11-05 01:30 | 102.16 | 94.49
2019-11-05 02:00 | 100.62 | 93.27
2019-11-05 02:30 | 98.83 | 92.53
2019-11-05 03:00 | 93.2 | 86.15
2019-11-05 03:30 | 97.17 | 90.51
2019-11-05 04:00 | 97.58 | 91.07
2019-11-05 04:30 | 97.49 | 90.72
2019-11-05 05:00 | 99.16 | 92.15
2019-11-05 05:30 | 100.27 | 93.4
2019-11-05 06:00 | 97.42 | 90.34
2019-11-05 06:30 | 82.38 | 71.01
2019-11-05 07:00 | 83.83 | 70.95
2019-11-05 07:30 | 89.23 | 73.2
2019-11-05 08:00 | 82.67 | 65.37
2019-11-05 08:30 | 91.83 | 74.9
2019-11-05 09:00 | 91.85 | 74.75
2019-11-05 09:30 | 95.95 | 78.17
2019-11-05 10:00 | 89.55 | 70.22
2019-11-05 10:30 | 93.45 | 74.28
2019-11-05 11:00 | 95.36 | 77.83
2019-11-05 11:30 | 93.08 | 73.68
2019-11-05 12:00 | 90.54 | 71.99
2019-11-05 12:30 | 96.11 | 78.9
2019-11-05 13:00 | 90.9 | 74.28
2019-11-05 13:30 | 96.9 | 79.92
2019-11-05 14:00 | 98.09 | 79.4
2019-11-05 14:30 | 97.78 | 79.59
2019-11-05 15:00 | 93.05 | 73.09
2019-11-05 15:30 | 93.96 | 75
2019-11-05 16:00 | 102.41 | 83.58
2019-11-05 16:30 | 97.75 | 78.17
2019-11-05 17:00 | 100.08 | 83.26
2019-11-05 17:30 | 111.43 | 101.15
2019-11-05 18:00 | 113.59 | 105.42
2019-11-05 18:30 | 113.08 | 105.35
2019-11-05 19:00 | 120.9 | 114.08
2019-11-05 19:30 | 111.26 | 104.03
2019-11-05 20:00 | 119.36 | 112.04
2019-11-05 20:30 | 116.12 | 108.49
2019-11-05 21:00 | 120.38 | 113.09
2019-11-05 21:30 | 123.86 | 116.17
2019-11-05 22:00 | 114.2 | 107.07
2019-11-05 22:30 | 116.04 | 108.14
2019-11-05 23:00 | 103.73 | 95.69
2019-11-05 23:30 | 111.86 | 103.08
2019-11-06 | 120.2 | 111.25
2019-11-06 00:30 | 115.67 | 106.53
2019-11-06 01:00 | 112.63 | 104.5
2019-11-06 01:30 | 117.72 | 108.85
2019-11-06 02:00 | 112.08 | 103
2019-11-06 02:30 | 111.45 | 103.16
2019-11-06 03:00 | 106.84 | 98.22
2019-11-06 03:30 | 108.82 | 100.95
2019-11-06 04:00 | 108.45 | 100.79
2019-11-06 04:30 | 111.98 | 104.4
2019-11-06 05:00 | 112.15 | 104.68
2019-11-06 05:30 | 104.01 | 96.94
2019-11-06 06:00 | 107.07 | 99.6
2019-11-06 06:30 | 94.3 | 83.62
2019-11-06 07:00 | 93.38 | 78.44
2019-11-06 07:30 | 86.88 | 68.07
2019-11-06 08:00 | 85.92 | 64.2
2019-11-06 08:30 | 88.24 | 66.73
2019-11-06 09:00 | 91.54 | 71.05
2019-11-06 09:30 | 89.63 | 68.64
2019-11-06 10:00 | 87.48 | 67.75
2019-11-06 10:30 | 85.32 | 65.18
2019-11-06 11:00 | 88.37 | 69.01
2019-11-06 11:30 | 102.95 | 82.48
2019-11-06 12:00 | 101.83 | 80.24
2019-11-06 12:30 | 101.27 | 79.76
2019-11-06 13:00 | 100.79 | 77.81
2019-11-06 13:30 | 103.8 | 81.25
2019-11-06 14:00 | 106.19 | 82.72
2019-11-06 14:30 | 94.41 | 71.05
2019-11-06 15:00 | 93.1 | 70.27
2019-11-06 15:30 | 93.9 | 70.61
2019-11-06 16:00 | 95.17 | 74.74
2019-11-06 16:30 | 99.66 | 81.05
2019-11-06 17:00 | 102.62 | 85.89
2019-11-06 17:30 | 105.7 | 94.25
2019-11-06 18:00 | 111.93 | 104.67
2019-11-06 18:30 | 95.88 | 88.83
2019-11-06 19:00 | 102.09 | 94.24
2019-11-06 19:30 | 107.66 | 100.02
2019-11-06 20:00 | 112.86 | 105.88
2019-11-06 20:30 | 116.32 | 109.76
2019-11-06 21:00 | 113.27 | 106.49
2019-11-06 21:30 | 108.05 | 101.79
2019-11-06 22:00 | 107.75 | 101.12
2019-11-06 22:30 | 106.56 | 99.24
2019-11-06 23:00 | 110.68 | 104.11
2019-11-06 23:30 | 92.95 | 86.09
2019-11-07 | 97.19 | 90.28
2019-11-07 00:30 | 110.41 | 103.7
2019-11-07 01:00 | 106.43 | 100.33
2019-11-07 01:30 | 111.78 | 105.3
2019-11-07 02:00 | 106.77 | 100.45
2019-11-07 02:30 | 107.92 | 100.6
2019-11-07 03:00 | 104.26 | 96.92
2019-11-07 03:30 | 91.37 | 83.75
2019-11-07 04:00 | 94.66 | 87.43
2019-11-07 04:30 | 96.44 | 89.48
2019-11-07 05:00 | 101.98 | 94.81
2019-11-07 05:30 | 102.04 | 94.99
2019-11-07 06:00 | 101.37 | 93.41
2019-11-07 06:30 | 95.05 | 83.78
2019-11-07 07:00 | 95.46 | 80.69
2019-11-07 07:30 | 90.96 | 71.4
2019-11-07 08:00 | 96.64 | 76.72
2019-11-07 08:30 | 94.05 | 73.95
2019-11-07 09:00 | 89.57 | 68.83
2019-11-07 09:30 | 94.74 | 74.39
2019-11-07 10:00 | 99.85 | 80.2
2019-11-07 10:30 | 95.6 | 75.84
2019-11-07 11:00 | 103.69 | 84.13
2019-11-07 11:30 | 99.07 | 79.39
2019-11-07 12:00 | 104.31 | 86.22
2019-11-07 12:30 | 94.53 | 78.51
2019-11-07 13:00 | 99.84 | 83.37
2019-11-07 13:30 | 89.94 | 74.6
2019-11-07 14:00 | 94.35 | 77.84
2019-11-07 14:30 | 91.7 | 74.66
2019-11-07 15:00 | 95.71 | 78.74
2019-11-07 15:30 | 97.28 | 78.7
2019-11-07 16:00 | 103.94 | 86.77
2019-11-07 16:30 | 110.01 | 93.97
2019-11-07 17:00 | 109.59 | 95.8
2019-11-07 17:30 | 112.81 | 102.72
2019-11-07 18:00 | 118.34 | 111.28
2019-11-07 18:30 | 107.92 | 101.18
2019-11-07 19:00 | 117.21 | 110.98
2019-11-07 19:30 | 117.42 | 111.33
2019-11-07 20:00 | 113.43 | 108.44
2019-11-07 20:30 | 115.11 | 110.01
2019-11-07 21:00 | 110.84 | 105.5
2019-11-07 21:30 | 112.1 | 105.46
2019-11-07 22:00 | 108.5 | 103.29
2019-11-07 22:30 | 113.52 | 107.31
2019-11-07 23:00 | 124.69 | 117.92
2019-11-07 23:30 | 125.48 | 117.82
2019-11-08 | 124.1 | 115.8
2019-11-08 00:30 | 114.61 | 106.9
2019-11-08 01:00 | 117.56 | 110.43
2019-11-08 01:30 | 118.11 | 111.05
2019-11-08 02:00 | 120.11 | 112.67
2019-11-08 02:30 | 121.83 | 114.86
2019-11-08 03:00 | 118.04 | 110.84
2019-11-08 03:30 | 115.93 | 108.65
2019-11-08 04:00 | 94.65 | 89.15
2019-11-08 04:30 | 95.21 | 90.15
2019-11-08 05:00 | 98.82 | 94.18
2019-11-08 05:30 | 102.28 | 97.59
2019-11-08 06:00 | 105.04 | 99.85
2019-11-08 06:30 | 93.85 | 85.65
2019-11-08 07:00 | 91.48 | 81.21
2019-11-08 07:30 | 96.56 | 84.33
2019-11-08 08:00 | 92.44 | 78.62
2019-11-08 08:30 | 86.5 | 72.16
2019-11-08 09:00 | 88.26 | 73.64
2019-11-08 09:30 | 97.59 | 84.54
2019-11-08 10:00 | 95.64 | 80.92
2019-11-08 10:30 | 94.65 | 78.06
2019-11-08 11:00 | 102.46 | 86.2
2019-11-08 11:30 | 101 | 84.18
2019-11-08 12:00 | 106.56 | 87.83
2019-11-08 12:30 | 105.38 | 85.94
2019-11-08 13:00 | 99.1 | 79.81
2019-11-08 13:30 | 100.24 | 80.77
2019-11-08 14:00 | 105.19 | 88.6
2019-11-08 14:30 | 104.52 | 86.83
2019-11-08 15:00 | 101.14 | 83.4
2019-11-08 15:30 | 102.23 | 85.4
2019-11-08 16:00 | 109.83 | 93.33
2019-11-08 16:30 | 101.99 | 86.35
2019-11-08 17:00 | 109.44 | 96.53
2019-11-08 17:30 | 114.24 | 104.47
2019-11-08 18:00 | 126.01 | 119.57
2019-11-08 18:30 | 118.39 | 112.58
2019-11-08 19:00 | 115.66 | 110.05
2019-11-08 19:30 | 114.66 | 109.89
2019-11-08 20:00 | 120.33 | 115.23
2019-11-08 20:30 | 120.77 | 114.98
2019-11-08 21:00 | 114.77 | 109.5
2019-11-08 21:30 | 120.1 | 114.82
2019-11-08 22:00 | 112.61 | 107.45
2019-11-08 22:30 | 113.99 | 108.73
2019-11-08 23:00 | 118.53 | 112.32
2019-11-08 23:30 | 114.29 | 107.61
2019-11-09 | 112.11 | 105.5
2019-11-09 00:30 | 121.11 | 113.96
2019-11-09 01:00 | 108.84 | 102.02
2019-11-09 01:30 | 105.57 | 98.97
2019-11-09 02:00 | 106.17 | 99.57
2019-11-09 02:30 | 109.59 | 103.39
2019-11-09 03:00 | 112.7 | 106.23
2019-11-09 03:30 | 99.55 | 93.49
2019-11-09 04:00 | 104.84 | 99.53
2019-11-09 04:30 | 103.77 | 98.66
2019-11-09 05:00 | 102.59 | 97.4
2019-11-09 05:30 | 101.18 | 95.87
2019-11-09 06:00 | 107.51 | 102.42
2019-11-09 06:30 | 94.87 | 86.59
2019-11-09 07:00 | 104.81 | 99.96
2019-11-09 07:30 | 95.16 | 89.77
2019-11-09 08:00 | 94.17 | 88.09
2019-11-09 08:30 | 102.67 | 97.89
2019-11-09 09:00 | 110.72 | 105.91
2019-11-09 09:30 | 118.21 | 113.02
2019-11-09 10:00 | 109.91 | 104.5
2019-11-09 10:30 | 109.49 | 103.95
2019-11-09 11:00 | 111.98 | 106.9
2019-11-09 11:30 | 110.53 | 105.31
2019-11-09 12:00 | 113.55 | 108.5
2019-11-09 12:30 | 111.99 | 107.03
2019-11-09 13:00 | 106.2 | 100.88
2019-11-09 13:30 | 111.7 | 105.56
2019-11-09 14:00 | 105.9 | 100.46
2019-11-09 14:30 | 107.28 | 101.47
2019-11-09 15:00 | 105.99 | 100.86
2019-11-09 15:30 | 97.82 | 92.76
2019-11-09 16:00 | 99.9 | 95.11
2019-11-09 16:30 | 105.75 | 100.72
2019-11-09 17:00 | 108.07 | 102.4
2019-11-09 17:30 | 124.92 | 119.57
2019-11-09 18:00 | 122.58 | 117
2019-11-09 18:30 | 107.29 | 101.46
2019-11-09 19:00 | 112.71 | 107.25
2019-11-09 19:30 | 116.42 | 111.39
2019-11-09 20:00 | 116.42 | 111.67
2019-11-09 20:30 | 110.31 | 105.57
2019-11-09 21:00 | 108.26 | 103.38
2019-11-09 21:30 | 109.3 | 104.39
2019-11-09 22:00 | 110.16 | 105.16
2019-11-09 22:30 | 104.01 | 98.65
2019-11-09 23:00 | 104.84 | 99.5
2019-11-09 23:30 | 111.77 | 106.05
2019-11-10 | 103.3 | 97.32
2019-11-10 00:30 | 106.17 | 100.01
2019-11-10 01:00 | 104.59 | 98.13
2019-11-10 01:30 | 104.67 | 98.67
2019-11-10 02:00 | 97.88 | 91.86
2019-11-10 02:30 | 99.76 | 93.89
2019-11-10 03:00 | 93.74 | 87.71
2019-11-10 03:30 | 99.39 | 92.98
2019-11-10 04:00 | 100.79 | 94.88
2019-11-10 04:30 | 101.55 | 96.18
2019-11-10 05:00 | 101.19 | 96.06
2019-11-10 05:30 | 98.02 | 93.08
2019-11-10 06:00 | 102.68 | 97.47
2019-11-10 06:30 | 93.82 | 88.49
2019-11-10 07:00 | 103.54 | 98.28
2019-11-10 07:30 | 100.75 | 95.44
2019-11-10 08:00 | 96.29 | 91.32
2019-11-10 08:30 | 93.99 | 88.42
2019-11-10 09:00 | 106.65 | 100.79
2019-11-10 09:30 | 108.83 | 102.31
2019-11-10 10:00 | 118.45 | 111.75
2019-11-10 10:30 | 110.1 | 102.56
2019-11-10 11:00 | 106.49 | 100
2019-11-10 11:30 | 99.64 | 92.1
2019-11-10 12:00 | 97.89 | 91.7
2019-11-10 12:30 | 112.65 | 106.43
2019-11-10 13:00 | 95.23 | 90.47
2019-11-10 13:30 | 100.26 | 95.67
2019-11-10 14:00 | 107.85 | 97.13
2019-11-10 14:30 | 101.61 | 94.42
2019-11-10 15:00 | 92.53 | 78.06
2019-11-10 15:30 | 90.63 | 78.78
2019-11-10 16:00 | 101 | 84.57
2019-11-10 16:30 | 108.33 | 91.55
2019-11-10 17:00 | 100.56 | 84.99
2019-11-10 17:30 | 115.5 | 103.58
2019-11-10 18:00 | 123.19 | 113.49
2019-11-10 18:30 | 111.02 | 102.66
2019-11-10 19:00 | 125.88 | 117.42
2019-11-10 19:30 | 124.35 | 115.26
2019-11-10 20:00 | 122.76 | 114.13
2019-11-10 20:30 | 129.3 | 120.15
2019-11-10 21:00 | 126.65 | 117.18
2019-11-10 21:30 | 122.43 | 112.89
2019-11-10 22:00 | 118.96 | 109.38
2019-11-10 22:30 | 115.46 | 106.28
2019-11-10 23:00 | 111.18 | 101.75
2019-11-10 23:30 | 109.05 | 99.86
2019-11-11 | 110.33 | 101.87
2019-11-11 00:30 | 108.75 | 100.05
2019-11-11 01:00 | 106.84 | 98.08
2019-11-11 01:30 | 105.45 | 97.35
2019-11-11 02:00 | 100.29 | 93.29
2019-11-11 02:30 | 99.27 | 92.16
2019-11-11 03:00 | 95.69 | 88.64
2019-11-11 03:30 | 96.72 | 89.8
2019-11-11 04:00 | 95.65 | 88.62
2019-11-11 04:30 | 98.78 | 91.26
2019-11-11 05:00 | 99.44 | 91.31
2019-11-11 05:30 | 100.59 | 93.31
2019-11-11 06:00 | 93.23 | 87.38
2019-11-11 06:30 | 86.7 | 76.96
2019-11-11 07:00 | 83.03 | 69.42
2019-11-11 07:30 | 86.58 | 69.8
2019-11-11 08:00 | 88.53 | 70.82
2019-11-11 08:30 | 84.87 | 68.93
2019-11-11 09:00 | 78.58 | 64.09
2019-11-11 09:30 | 70.76 | 55.02
2019-11-11 10:00 | 75.1 | 59.18
2019-11-11 10:30 | 75.06 | 58.33
2019-11-11 11:00 | 77.87 | 60.75
2019-11-11 11:30 | 76.26 | 58.25
2019-11-11 12:00 | 75.12 | 62.42
2019-11-11 12:30 | 74.36 | 57.88
2019-11-11 13:00 | 75.3 | 65.82
2019-11-11 13:30 | 74.84 | 63.94
2019-11-11 14:00 | 73.32 | 57.46
2019-11-11 14:30 | 70.4 | 54.76
2019-11-11 15:00 | 72.36 | 57.18
2019-11-11 15:30 | 70.27 | 56.09
2019-11-11 16:00 | 71.05 | 56.28
2019-11-11 16:30 | 75.07 | 60.26
2019-11-11 17:00 | 84.34 | 74.05
2019-11-11 17:30 | 81.4 | 75.08
2019-11-11 18:00 | 88.5 | 84.58
2019-11-11 18:30 | 89.48 | 86.14
2019-11-11 19:00 | 98.66 | 95.31
2019-11-11 19:30 | 97.62 | 94.53
2019-11-11 20:00 | 95.98 | 92.88
2019-11-11 20:30 | 91.58 | 88.13
2019-11-11 21:00 | 83.67 | 80.46
2019-11-11 21:30 | 85.66 | 82.4
2019-11-11 22:00 | 89.4 | 86.11
2019-11-11 22:30 | 94.51 | 91.22
2019-11-11 23:00 | 90.72 | 87.5
2019-11-11 23:30 | 90.47 | 87.21
2019-11-12 | 91.08 | 87.83
2019-11-12 00:30 | 91.66 | 88.46
2019-11-12 01:00 | 94.46 | 91.26
2019-11-12 01:30 | 95.75 | 91.7
2019-11-12 02:00 | 96.51 | 92.2
2019-11-12 02:30 | 97.87 | 92.68
2019-11-12 03:00 | 97.3 | 92.33
2019-11-12 03:30 | 98.46 | 93.3
2019-11-12 04:00 | 101.96 | 96.86
2019-11-12 04:30 | 102.32 | 97.46
2019-11-12 05:00 | 97.76 | 93.49
2019-11-12 05:30 | 98.23 | 94.37
2019-11-12 06:00 | 95.47 | 91.97
2019-11-12 06:30 | 77.07 | 70.39
2019-11-12 07:00 | 85.07 | 77.75
2019-11-12 07:30 | 81.31 | 67.85
2019-11-12 08:00 | 87.7 | 73.02
2019-11-12 08:30 | 92.91 | 80.01
2019-11-12 09:00 | 94.1 | 85.32
2019-11-12 09:30 | 88.49 | 73.05
2019-11-12 10:00 | 87.02 | 70.17
2019-11-12 10:30 | 92.65 | 77.28
2019-11-12 11:00 | 88.6 | 71.85
2019-11-12 11:30 | 80.55 | 64.3
2019-11-12 12:00 | 82.33 | 74.6
2019-11-12 12:30 | 83.54 | 66.79
2019-11-12 13:00 | 82.48 | 64.8
2019-11-12 13:30 | 86.58 | 69.61
2019-11-12 14:00 | 89.61 | 71.96
2019-11-12 14:30 | 91.6 | 74.69
2019-11-12 15:00 | 94.54 | 81.26
2019-11-12 15:30 | 102.93 | 97.11
2019-11-12 16:00 | 103.56 | 98.47
2019-11-12 16:30 | 99.71 | 94.79
2019-11-12 17:00 | 102.74 | 98.21
2019-11-12 17:30 | 103.75 | 98.53
2019-11-12 18:00 | 104.96 | 97.64
2019-11-12 18:30 | 98.61 | 91.87
2019-11-12 19:00 | 109.22 | 102.67
2019-11-12 19:30 | 109.4 | 102.57
2019-11-12 20:00 | 110.49 | 103.93
2019-11-12 20:30 | 113.26 | 106.82
2019-11-12 21:00 | 114.66 | 107.75
2019-11-12 21:30 | 114.43 | 108.1
2019-11-12 22:00 | 106.8 | 100.02
2019-11-12 22:30 | 109.82 | 102.98
2019-11-12 23:00 | 108.81 | 102.08
2019-11-12 23:30 | 106.6 | 100.29
2019-11-13 | 107.46 | 100.77
2019-11-13 00:30 | 105.61 | 98.28
2019-11-13 01:00 | 109.78 | 102.3
2019-11-13 01:30 | 106.52 | 99.13
2019-11-13 02:00 | 106.91 | 100.53
2019-11-13 02:30 | 103.04 | 95.96
2019-11-13 03:00 | 96.07 | 89.34
2019-11-13 03:30 | 98.96 | 91.87
2019-11-13 04:00 | 97.72 | 91.75
2019-11-13 04:30 | 96.69 | 91.66
2019-11-13 05:00 | 94.94 | 89.93
2019-11-13 05:30 | 95.53 | 91.13
2019-11-13 06:00 | 91.76 | 87.4
2019-11-13 06:30 | 82.47 | 76.7
2019-11-13 07:00 | 72.38 | 65.16
2019-11-13 07:30 | 76.88 | 68.59
2019-11-13 08:00 | 77.94 | 68
2019-11-13 08:30 | 75.74 | 64.06
2019-11-13 09:00 | 78.63 | 66.78
2019-11-13 09:30 | 76.64 | 65.66
2019-11-13 10:00 | 79.43 | 68.8
2019-11-13 10:30 | 81.62 | 69.47
2019-11-13 11:00 | 84.19 | 71.44
2019-11-13 11:30 | 87.28 | 74.74
2019-11-13 12:00 | 85.02 | 74.06
2019-11-13 12:30 | 89.79 | 78.69
2019-11-13 13:00 | 88.09 | 77.55
2019-11-13 13:30 | 86.17 | 72.82
2019-11-13 14:00 | 92.21 | 78.75
2019-11-13 14:30 | 91.68 | 77.69
2019-11-13 15:00 | 86.32 | 72.21
2019-11-13 15:30 | 86.76 | 74.07
2019-11-13 16:00 | 89.82 | 79.51
2019-11-13 16:30 | 91.26 | 83.76
2019-11-13 17:00 | 90.19 | 80.71
2019-11-13 17:30 | 95.94 | 88.97
2019-11-13 18:00 | 101.15 | 96.68
2019-11-13 18:30 | 96.44 | 92.67
2019-11-13 19:00 | 98.82 | 94.91
2019-11-13 19:30 | 108.75 | 104.79
2019-11-13 20:00 | 111.39 | 107.17
2019-11-13 20:30 | 114.41 | 109.5
2019-11-13 21:00 | 107.2 | 102.18
2019-11-13 21:30 | 99.29 | 94.24
2019-11-13 22:00 | 98.05 | 92.55
2019-11-13 22:30 | 102.76 | 97.4
2019-11-13 23:00 | 93.08 | 87.33
2019-11-13 23:30 | 90.32 | 85.04
2019-11-14 | 91.08 | 86.35
2019-11-14 00:30 | 98.01 | 93.89
2019-11-14 01:00 | 96.05 | 91.59
2019-11-14 01:30 | 100.96 | 96.08
2019-11-14 02:00 | 100.09 | 95.29
2019-11-14 02:30 | 98.68 | 93.1
2019-11-14 03:00 | 92.66 | 86.39
2019-11-14 03:30 | 89.1 | 83.14
2019-11-14 04:00 | 86.92 | 81.92
2019-11-14 04:30 | 94.87 | 89.79
2019-11-14 05:00 | 95.32 | 89.42
2019-11-14 05:30 | 97.12 | 91.59
2019-11-14 06:00 | 101.05 | 94.82
2019-11-14 06:30 | 84.13 | 75.39
2019-11-14 07:00 | 83.93 | 73.68
2019-11-14 07:30 | 85.78 | 72.63
2019-11-14 08:00 | 77.15 | 63.19
2019-11-14 08:30 | 79.58 | 65.87
2019-11-14 09:00 | 82 | 68.32
2019-11-14 09:30 | 75.81 | 59.2
2019-11-14 10:00 | 80.04 | 63.27
2019-11-14 10:30 | 72.7 | 55.25
2019-11-14 11:00 | 71.69 | 52.89
2019-11-14 11:30 | 83.83 | 67.82
2019-11-14 12:00 | 72.97 | 57.99
2019-11-14 12:30 | 79.17 | 63.73
2019-11-14 13:00 | 77.81 | 63.41
2019-11-14 13:30 | 78.56 | 64.29
2019-11-14 14:00 | 81.31 | 66.54
2019-11-14 14:30 | 82.65 | 68.12
2019-11-14 15:00 | 87.41 | 71.57
2019-11-14 15:30 | 80.77 | 65.28
2019-11-14 16:00 | 79.56 | 65.67
2019-11-14 16:30 | 89.18 | 77.07
2019-11-14 17:00 | 89.94 | 80.1
2019-11-14 17:30 | 96.03 | 89.01
2019-11-14 18:00 | 99.44 | 94.59
2019-11-14 18:30 | 93.72 | 88.89
2019-11-14 19:00 | 103.72 | 98.9
2019-11-14 19:30 | 104.87 | 99.53
2019-11-14 20:00 | 112.1 | 105.98
2019-11-14 20:30 | 107.98 | 101.92
2019-11-14 21:00 | 107.53 | 100.78
2019-11-14 21:30 | 105.48 | 98.27
2019-11-14 22:00 | 106.45 | 99.69
2019-11-14 22:30 | 106.98 | 99.58
2019-11-14 23:00 | 109.75 | 101.64
2019-11-14 23:30 | 106.9 | 99.13
2019-11-15 | 97.27 | 89.56
2019-11-15 00:30 | 103.76 | 96.81
2019-11-15 01:00 | 99.09 | 92
2019-11-15 01:30 | 99.77 | 92.49
2019-11-15 02:00 | 106.37 | 98.66
2019-11-15 02:30 | 102.77 | 95.39
2019-11-15 03:00 | 107.58 | 100.1
2019-11-15 03:30 | 96.02 | 88.41
2019-11-15 04:00 | 96.99 | 89.77
2019-11-15 04:30 | 100.3 | 93.04
2019-11-15 05:00 | 105.67 | 97.86
2019-11-15 05:30 | 93.78 | 86.08
2019-11-15 06:00 | 99.46 | 92.02
2019-11-15 06:30 | 83.85 | 72.63
2019-11-15 07:00 | 85.92 | 72.21
2019-11-15 07:30 | 86.78 | 68.89
2019-11-15 08:00 | 89.83 | 71.08
2019-11-15 08:30 | 90.11 | 69.17
2019-11-15 09:00 | 87.93 | 65.18
2019-11-15 09:30 | 84.49 | 65.01
2019-11-15 10:00 | 84.58 | 66.4
2019-11-15 10:30 | 94.73 | 72.99
2019-11-15 11:00 | 90.99 | 68.09
2019-11-15 11:30 | 97.51 | 74.45
2019-11-15 12:00 | 102 | 80.56
2019-11-15 12:30 | 104.18 | 82.59
2019-11-15 13:00 | 95.02 | 74.31
2019-11-15 13:30 | 102.54 | 83.97
2019-11-15 14:00 | 100.75 | 81.6
2019-11-15 14:30 | 89.38 | 69.74
2019-11-15 15:00 | 87.88 | 69.4
2019-11-15 15:30 | 95.36 | 84.2
2019-11-15 16:00 | 93.78 | 83.05
2019-11-15 16:30 | 102.78 | 91.05
2019-11-15 17:00 | 101.93 | 89.78
2019-11-15 17:30 | 103.96 | 95.38
2019-11-15 18:00 | 107.8 | 100.96
2019-11-15 18:30 | 100.63 | 93.94
2019-11-15 19:00 | 98.96 | 91.9
2019-11-15 19:30 | 102.52 | 95.42
2019-11-15 20:00 | 105.17 | 98.6
2019-11-15 20:30 | 108.36 | 101.15
2019-11-15 21:00 | 105.54 | 97.9
2019-11-15 21:30 | 107.63 | 100.14
2019-11-15 22:00 | 98.5 | 91.35
2019-11-15 22:30 | 104.19 | 97.1
2019-11-15 23:00 | 104.78 | 97.38
2019-11-15 23:30 | 100.86 | 94.09
2019-11-16 | 99.92 | 92.57
2019-11-16 00:30 | 100.4 | 93.9
2019-11-16 01:00 | 97.53 | 91.42
2019-11-16 01:30 | 101.41 | 95.15
2019-11-16 02:00 | 104.84 | 98.74
2019-11-16 02:30 | 105.88 | 99.87
2019-11-16 03:00 | 109.51 | 102.68
2019-11-16 03:30 | 100.66 | 93.96
2019-11-16 04:00 | 108.74 | 102
2019-11-16 04:30 | 109.58 | 102.86
2019-11-16 05:00 | 106.58 | 99.98
2019-11-16 05:30 | 104.84 | 98
2019-11-16 06:00 | 99.27 | 92.61
2019-11-16 06:30 | 100.53 | 93.05
2019-11-16 07:00 | 111.64 | 104.34
2019-11-16 07:30 | 106.61 | 99.04
2019-11-16 08:00 | 103.25 | 92.22
2019-11-16 08:30 | 100.75 | 84.52
2019-11-16 09:00 | 103.54 | 85.89
2019-11-16 09:30 | 108.2 | 90.34
2019-11-16 10:00 | 105.81 | 87.32
2019-11-16 10:30 | 102.22 | 82.67
2019-11-16 11:00 | 100.14 | 82.25
2019-11-16 11:30 | 98.53 | 80.13
2019-11-16 12:00 | 98.93 | 81.61
2019-11-16 12:30 | 100.67 | 83.2
2019-11-16 13:00 | 98.2 | 81.08
2019-11-16 13:30 | 107.12 | 90.33
2019-11-16 14:00 | 104.6 | 87.99
2019-11-16 14:30 | 105.55 | 92.23
2019-11-16 15:00 | 104.51 | 88.89
2019-11-16 15:30 | 99.16 | 86.18
2019-11-16 16:00 | 105.98 | 94.72
2019-11-16 16:30 | 113.79 | 105.92
2019-11-16 17:00 | 112.41 | 105.13
2019-11-16 17:30 | 114.58 | 105.42
2019-11-16 18:00 | 114.51 | 106.78
2019-11-16 18:30 | 105.12 | 98.3
2019-11-16 19:00 | 114.01 | 107.8
2019-11-16 19:30 | 124.74 | 117.97
2019-11-16 20:00 | 115.15 | 108.23
2019-11-16 20:30 | 117.72 | 110.16
2019-11-16 21:00 | 113.68 | 106.72
2019-11-16 21:30 | 111.7 | 104.35
2019-11-16 22:00 | 112.01 | 104.75
2019-11-16 22:30 | 113.89 | 107.21
2019-11-16 23:00 | 117.26 | 111.05
2019-11-16 23:30 | 104.69 | 98.37
2019-11-17 | 111.43 | 105.27
2019-11-17 00:30 | 103.79 | 97.5
2019-11-17 01:00 | 107.34 | 101.17
2019-11-17 01:30 | 104.45 | 98.28
2019-11-17 02:00 | 111.06 | 104.16
2019-11-17 02:30 | 108.2 | 101.67
2019-11-17 03:00 | 107.94 | 100.84
2019-11-17 03:30 | 111.51 | 104.91
2019-11-17 04:00 | 112.54 | 105.72
2019-11-17 04:30 | 109.04 | 102.25
2019-11-17 05:00 | 102.31 | 95.99
2019-11-17 05:30 | 94.43 | 88.18
2019-11-17 06:00 | 95.58 | 89.63
2019-11-17 06:30 | 92.65 | 84.36
2019-11-17 07:00 | 99.12 | 88.01
2019-11-17 07:30 | 92.67 | 79.16
2019-11-17 08:00 | 90.62 | 73.78
2019-11-17 08:30 | 84.34 | 68.78
2019-11-17 09:00 | 92.53 | 75.26
2019-11-17 09:30 | 84.57 | 67.14
2019-11-17 10:00 | 87.37 | 70.8
2019-11-17 10:30 | 85.91 | 68.31
2019-11-17 11:00 | 93.05 | 75.46
2019-11-17 11:30 | 91.96 | 74.43
2019-11-17 12:00 | 97.88 | 80.93
2019-11-17 12:30 | 100.35 | 83.62
2019-11-17 13:00 | 103.71 | 88.65
2019-11-17 13:30 | 100.08 | 86.02
2019-11-17 14:00 | 98.46 | 84.83
2019-11-17 14:30 | 98.47 | 87.37
2019-11-17 15:00 | 102.22 | 93.89
2019-11-17 15:30 | 103.04 | 96.53
2019-11-17 16:00 | 104.59 | 95.09
2019-11-17 16:30 | 97.18 | 82.15
2019-11-17 17:00 | 100.32 | 87.67
2019-11-17 17:30 | 104.01 | 93.66
2019-11-17 18:00 | 110.12 | 104.18
2019-11-17 18:30 | 106.36 | 101.11
2019-11-17 19:00 | 116.03 | 111.76
2019-11-17 19:30 | 126.28 | 121.5
2019-11-17 20:00 | 123.72 | 118.95
2019-11-17 20:30 | 122.6 | 117.92
2019-11-17 21:00 | 117.02 | 112.51
2019-11-17 21:30 | 116.23 | 111.51
2019-11-17 22:00 | 108.27 | 103.84
2019-11-17 22:30 | 107.33 | 103.02
2019-11-17 23:00 | 109.12 | 104.54
2019-11-17 23:30 | 107.71 | 102.67
2019-11-18 | 96.02 | 90.92
2019-11-18 00:30 | 106.91 | 101.11
2019-11-18 01:00 | 109.3 | 103
2019-11-18 01:30 | 106.38 | 100.34
2019-11-18 02:00 | 111.57 | 104.93
2019-11-18 02:30 | 124.68 | 117.62
2019-11-18 03:00 | 111.28 | 104.4
2019-11-18 03:30 | 109.32 | 102.7
2019-11-18 04:00 | 112.91 | 106.33
2019-11-18 04:30 | 102.24 | 96.75
2019-11-18 05:00 | 96.65 | 90.45
2019-11-18 05:30 | 100.63 | 94.68
2019-11-18 06:00 | 101.62 | 94.96
2019-11-18 06:30 | 89.85 | 79.4
2019-11-18 07:00 | 91.16 | 78.73
2019-11-18 07:30 | 98.12 | 81.74
2019-11-18 08:00 | 100.2 | 81.47
2019-11-18 08:30 | 105.63 | 87.03
2019-11-18 09:00 | 107.61 | 88.49
2019-11-18 09:30 | 105.11 | 86.3
2019-11-18 10:00 | 103.54 | 85.29
2019-11-18 10:30 | 104.82 | 87.16
2019-11-18 11:00 | 106.2 | 87.35
2019-11-18 11:30 | 102.14 | 84.67
2019-11-18 12:00 | 100.29 | 83.33
2019-11-18 12:30 | 102.27 | 85.42
2019-11-18 13:00 | 103.98 | 86.96
2019-11-18 13:30 | 106.77 | 91
2019-11-18 14:00 | 102.77 | 86.43
2019-11-18 14:30 | 112.59 | 99.92
2019-11-18 15:00 | 94.79 | 82.69
2019-11-18 15:30 | 93.84 | 80.87
2019-11-18 16:00 | 100.31 | 87.1
2019-11-18 16:30 | 97.46 | 84.29
2019-11-18 17:00 | 103.12 | 92
2019-11-18 17:30 | 111.51 | 103.25
2019-11-18 18:00 | 115.35 | 108.22
2019-11-18 18:30 | 113.87 | 108.24
2019-11-18 19:00 | 124.22 | 117.99
2019-11-18 19:30 | 125.37 | 117.83
2019-11-18 20:00 | 127.09 | 119.63
2019-11-18 20:30 | 118.18 | 110.74
2019-11-18 21:00 | 116.38 | 108.53
2019-11-18 21:30 | 119.9 | 112.74
2019-11-18 22:00 | 120.2 | 113.33
2019-11-18 22:30 | 123.22 | 115.63
2019-11-18 23:00 | 124.57 | 116.91
2019-11-18 23:30 | 117.86 | 110.57
2019-11-19 | 112.51 | 105.63
2019-11-19 00:30 | 110.49 | 103.72
2019-11-19 01:00 | 112.04 | 105.73
2019-11-19 01:30 | 120.14 | 113.77
2019-11-19 02:00 | 119.99 | 113.44
2019-11-19 02:30 | 113.63 | 107.33
2019-11-19 03:00 | 113.57 | 107
2019-11-19 03:30 | 105.21 | 98.95
2019-11-19 04:00 | 102.35 | 96.59
2019-11-19 04:30 | 108.52 | 103.01
2019-11-19 05:00 | 106.01 | 100.63
2019-11-19 05:30 | 102.95 | 97.79
2019-11-19 06:00 | 100.22 | 95.36
2019-11-19 06:30 | 94.21 | 87.16
2019-11-19 07:00 | 93.88 | 84.62
2019-11-19 07:30 | 84.21 | 72.46
2019-11-19 08:00 | 88.43 | 74.51
2019-11-19 08:30 | 90.24 | 79.15
2019-11-19 09:00 | 94.58 | 83.06
2019-11-19 09:30 | 95.53 | 80.36
2019-11-19 10:00 | 90.98 | 75.38
2019-11-19 10:30 | 88.84 | 71.13
2019-11-19 11:00 | 95.55 | 79.28
2019-11-19 11:30 | 94.51 | 77.8
2019-11-19 12:00 | 94.86 | 78.03
2019-11-19 12:30 | 96.73 | 80.68
2019-11-19 13:00 | 92.57 | 79.18
2019-11-19 13:30 | 93.36 | 78.96
2019-11-19 14:00 | 96.95 | 83.12
2019-11-19 14:30 | 97.71 | 83.42
2019-11-19 15:00 | 103.73 | 90.63
2019-11-19 15:30 | 93.66 | 81.88
2019-11-19 16:00 | 94.27 | 82.29
2019-11-19 16:30 | 110.1 | 99.42
2019-11-19 17:00 | 104.87 | 93.06
2019-11-19 17:30 | 110.18 | 100.76
2019-11-19 18:00 | 118.23 | 112.11
2019-11-19 18:30 | 109.84 | 104.48
2019-11-19 19:00 | 117.17 | 111.74
2019-11-19 19:30 | 116.99 | 111.12
2019-11-19 20:00 | 112.96 | 107.56
2019-11-19 20:30 | 115.34 | 109.87
2019-11-19 21:00 | 122.18 | 117.12
2019-11-19 21:30 | 117.11 | 111.6
2019-11-19 22:00 | 109.39 | 103.78
2019-11-19 22:30 | 117.79 | 112.41
2019-11-19 23:00 | 116.95 | 111.3
2019-11-19 23:30 | 114.83 | 109.52
2019-11-20 | 108.37 | 102.79
2019-11-20 00:30 | 112.62 | 107.05
2019-11-20 01:00 | 117.5 | 112.16
2019-11-20 01:30 | 107.01 | 101.51
2019-11-20 02:00 | 114.15 | 108.8
2019-11-20 02:30 | 113.27 | 107.79
2019-11-20 03:00 | 111.74 | 106.49
2019-11-20 03:30 | 104.52 | 99.56
2019-11-20 04:00 | 100.86 | 95.63
2019-11-20 04:30 | 99.1 | 94.21
2019-11-20 05:00 | 94.18 | 89.05
2019-11-20 05:30 | 93.8 | 88.56
2019-11-20 06:00 | 95.96 | 91.72
2019-11-20 06:30 | 90.01 | 83.92
2019-11-20 07:00 | 83.76 | 75.31
2019-11-20 07:30 | 87.17 | 77.57
2019-11-20 08:00 | 85.49 | 74.98
2019-11-20 08:30 | 89.58 | 78.68
2019-11-20 09:00 | 85.93 | 73.55
2019-11-20 09:30 | 86.18 | 73.2
2019-11-20 10:00 | 83.6 | 70.68
2019-11-20 10:30 | 86.15 | 72.63
2019-11-20 11:00 | 89.85 | 78.24
2019-11-20 11:30 | 90.77 | 78.67
2019-11-20 12:00 | 94.34 | 81.97
2019-11-20 12:30 | 89.83 | 77.68
2019-11-20 13:00 | 99.92 | 88.48
2019-11-20 13:30 | 100.66 | 88.46
2019-11-20 14:00 | 96.13 | 84.74
2019-11-20 14:30 | 93.73 | 81.34
2019-11-20 15:00 | 102.38 | 90.01
2019-11-20 15:30 | 108.55 | 96.67
2019-11-20 16:00 | 110.19 | 99.55
2019-11-20 16:30 | 104.01 | 93.38
2019-11-20 17:00 | 98.52 | 89.58
2019-11-20 17:30 | 107.86 | 102
2019-11-20 18:00 | 114.53 | 110.47
2019-11-20 18:30 | 108.25 | 103.9
2019-11-20 19:00 | 115.3 | 111.46
2019-11-20 19:30 | 115.67 | 111.64
2019-11-20 20:00 | 117.01 | 113.04
2019-11-20 20:30 | 120.67 | 116.28
2019-11-20 21:00 | 114.53 | 110.29
2019-11-20 21:30 | 117.35 | 112.91
2019-11-20 22:00 | 106.78 | 102.19
2019-11-20 22:30 | 106.94 | 102.34
2019-11-20 23:00 | 108.46 | 103.35
2019-11-20 23:30 | 105.15 | 100.04
2019-11-21 | 104.26 | 99.06
2019-11-21 00:30 | 107.33 | 102.71
2019-11-21 01:00 | 106.03 | 101.01
2019-11-21 01:30 | 106.59 | 101
2019-11-21 02:00 | 109.35 | 104.29
2019-11-21 02:30 | 109.66 | 104.41
2019-11-21 03:00 | 104.67 | 99.17
2019-11-21 03:30 | 100.94 | 94.95
2019-11-21 04:00 | 101.02 | 95.06
2019-11-21 04:30 | 98.68 | 93.4
2019-11-21 05:00 | 99.34 | 93.69
2019-11-21 05:30 | 106.71 | 101.54
2019-11-21 06:00 | 114.51 | 110.03
2019-11-21 06:30 | 98.79 | 92.15
2019-11-21 07:00 | 94.87 | 86.53
2019-11-21 07:30 | 88.48 | 77.81
2019-11-21 08:00 | 95.45 | 84.62
2019-11-21 08:30 | 94.88 | 83.32
2019-11-21 09:00 | 101.23 | 88.44
2019-11-21 09:30 | 96.03 | 83.28
2019-11-21 10:00 | 88.12 | 75.96
2019-11-21 10:30 | 93.49 | 79.99
2019-11-21 11:00 | 90.08 | 77.92
2019-11-21 11:30 | 94.17 | 81.65
2019-11-21 12:00 | 90.14 | 76.52
2019-11-21 12:30 | 93.46 | 81.03
2019-11-21 13:00 | 91.36 | 79.4
2019-11-21 13:30 | 89.3 | 77.97
2019-11-21 14:00 | 99.28 | 88.22
2019-11-21 14:30 | 95.2 | 84.46
2019-11-21 15:00 | 89.12 | 78.97
2019-11-21 15:30 | 86.62 | 75.17
2019-11-21 16:00 | 92.25 | 82.13
2019-11-21 16:30 | 99.49 | 90.56
2019-11-21 17:00 | 100.47 | 93.33
2019-11-21 17:30 | 107.35 | 102.25
2019-11-21 18:00 | 103.71 | 99.97
2019-11-21 18:30 | 102.02 | 97.8
2019-11-21 19:00 | 106.52 | 102.72
2019-11-21 19:30 | 106.35 | 103.28
2019-11-21 20:00 | 119.04 | 115.72
2019-11-21 20:30 | 112.23 | 108.64
2019-11-21 21:00 | 108.1 | 104.01
2019-11-21 21:30 | 104.69 | 99.94
2019-11-21 22:00 | 107.17 | 102.24
2019-11-21 22:30 | 105.93 | 100.53
2019-11-21 23:00 | 106.26 | 100.78
2019-11-21 23:30 | 99.61 | 93.38
2019-11-22 | 91.21 | 84.76
2019-11-22 00:30 | 97.06 | 91.45
2019-11-22 01:00 | 91.43 | 85.59
2019-11-22 01:30 | 96.89 | 91.08
2019-11-22 02:00 | 97.93 | 91.97
2019-11-22 02:30 | 106.94 | 101.32
2019-11-22 03:00 | 109.38 | 103.73
2019-11-22 03:30 | 106.4 | 100.44
2019-11-22 04:00 | 104.14 | 97.96
2019-11-22 04:30 | 107.48 | 101.77
2019-11-22 05:00 | 107.42 | 101.94
2019-11-22 05:30 | 99.56 | 93.47
2019-11-22 06:00 | 99.79 | 93.97
2019-11-22 06:30 | 89.36 | 80.41
2019-11-22 07:00 | 98.43 | 88.52
2019-11-22 07:30 | 98.69 | 86.15
2019-11-22 08:00 | 99.15 | 85.46
2019-11-22 08:30 | 95.62 | 82.27
2019-11-22 09:00 | 92.14 | 77.54
2019-11-22 09:30 | 92.36 | 78.12
2019-11-22 10:00 | 100.05 | 87.48
2019-11-22 10:30 | 94.38 | 81.76
2019-11-22 11:00 | 98.22 | 84.29
2019-11-22 11:30 | 107.67 | 91.92
2019-11-22 12:00 | 107.81 | 92.41
2019-11-22 12:30 | 109.08 | 93.44
2019-11-22 13:00 | 109.22 | 91.71
2019-11-22 13:30 | 107.97 | 89.38
2019-11-22 14:00 | 105.07 | 86.95
2019-11-22 14:30 | 104.11 | 86.46
2019-11-22 15:00 | 111.9 | 95.32
2019-11-22 15:30 | 107.74 | 91.61
2019-11-22 16:00 | 105.45 | 90.56
2019-11-22 16:30 | 106.8 | 93.94
2019-11-22 17:00 | 107.26 | 95.1
2019-11-22 17:30 | 111.25 | 101.68
2019-11-22 18:00 | 122.01 | 115.39
2019-11-22 18:30 | 122.07 | 115.25
2019-11-22 19:00 | 130.37 | 124.4
2019-11-22 19:30 | 134.67 | 128.78
2019-11-22 20:00 | 125.26 | 119.02
2019-11-22 20:30 | 116.26 | 110.35
2019-11-22 21:00 | 118.86 | 112.18
2019-11-22 21:30 | 111.02 | 104.32
2019-11-22 22:00 | 110.81 | 103.67
2019-11-22 22:30 | 118.1 | 111.35
2019-11-22 23:00 | 114.32 | 107.59
2019-11-22 23:30 | 111.56 | 104.89
2019-11-23 | 114.67 | 108
2019-11-23 00:30 | 114.69 | 107.91
2019-11-23 01:00 | 116.7 | 108.96
2019-11-23 01:30 | 117.43 | 109.48
2019-11-23 02:00 | 116.25 | 108.82
2019-11-23 02:30 | 107.19 | 99.28
2019-11-23 03:00 | 102.61 | 96.96
2019-11-23 03:30 | 87.4 | 81.46
2019-11-23 04:00 | 91.31 | 84.98
2019-11-23 04:30 | 97.37 | 91.15
2019-11-23 05:00 | 104.7 | 97.93
2019-11-23 05:30 | 106.35 | 99.36
2019-11-23 06:00 | 106.15 | 98.17
2019-11-23 06:30 | 93.17 | 82.13
2019-11-23 07:00 | 92.66 | 80.51
2019-11-23 07:30 | 101.2 | 86.62
2019-11-23 08:00 | 99.54 | 83.01
2019-11-23 08:30 | 101.6 | 82.8
2019-11-23 09:00 | 103.99 | 85.42
2019-11-23 09:30 | 102.26 | 81.69
2019-11-23 10:00 | 103.49 | 82.19
2019-11-23 10:30 | 96.3 | 74.29
2019-11-23 11:00 | 93.52 | 72.88
2019-11-23 11:30 | 96.52 | 75.92
2019-11-23 12:00 | 98.31 | 78.05
2019-11-23 12:30 | 101.54 | 82.74
2019-11-23 13:00 | 95.85 | 77.55
2019-11-23 13:30 | 101.28 | 82.78
2019-11-23 14:00 | 101.62 | 83.03
2019-11-23 14:30 | 102.3 | 85.5
2019-11-23 15:00 | 95.42 | 82.6
2019-11-23 15:30 | 91.65 | 79.07
2019-11-23 16:00 | 91.25 | 79.14
2019-11-23 16:30 | 89.65 | 78.71
2019-11-23 17:00 | 102.67 | 91.77
2019-11-23 17:30 | 105.96 | 98.21
2019-11-23 18:00 | 104.63 | 99.03
2019-11-23 18:30 | 102.22 | 96.81
2019-11-23 19:00 | 92.89 | 87.46
2019-11-23 19:30 | 100.65 | 94.97
2019-11-23 20:00 | 101.82 | 97.34
2019-11-23 20:30 | 101.44 | 96.79
2019-11-23 21:00 | 97.15 | 92.45
2019-11-23 21:30 | 107.68 | 102.3
2019-11-23 22:00 | 107.97 | 102.36
2019-11-23 22:30 | 100.65 | 94.62
2019-11-23 23:00 | 109.18 | 103.87
2019-11-23 23:30 | 101.46 | 95.68
2019-11-24 | 97.48 | 92
2019-11-24 00:30 | 106.19 | 101.01
2019-11-24 01:00 | 103.51 | 98.01
2019-11-24 01:30 | 103.5 | 98.07
2019-11-24 02:00 | 101.05 | 95.34
2019-11-24 02:30 | 103.13 | 97.23
2019-11-24 03:00 | 103.25 | 97.61
2019-11-24 03:30 | 100.3 | 94.5
2019-11-24 04:00 | 102.16 | 96.5
2019-11-24 04:30 | 99.67 | 94.25
2019-11-24 05:00 | 96.07 | 90.14
2019-11-24 05:30 | 94.03 | 88.04
2019-11-24 06:00 | 96.72 | 91.41
2019-11-24 06:30 | 82.85 | 75.16
2019-11-24 07:00 | 89.94 | 78.94
2019-11-24 07:30 | 93.56 | 79.6
2019-11-24 08:00 | 90.61 | 79
2019-11-24 08:30 | 83.83 | 72.6
2019-11-24 09:00 | 75.69 | 62.85
2019-11-24 09:30 | 79.42 | 62.1
2019-11-24 10:00 | 87.4 | 72.91
2019-11-24 10:30 | 87 | 70.85
2019-11-24 11:00 | 95.93 | 80.59
2019-11-24 11:30 | 89.91 | 74.73
2019-11-24 12:00 | 90.03 | 74.51
2019-11-24 12:30 | 107.83 | 91.63
2019-11-24 13:00 | 107.82 | 93.71
2019-11-24 13:30 | 110.28 | 96
2019-11-24 14:00 | 113.17 | 97.79
2019-11-24 14:30 | 108.78 | 93.08
2019-11-24 15:00 | 107.63 | 90.23
2019-11-24 15:30 | 110.11 | 93.19
2019-11-24 16:00 | 112.16 | 99.76
2019-11-24 16:30 | 101.98 | 88.14
2019-11-24 17:00 | 102.39 | 89.78
2019-11-24 17:30 | 111.7 | 100.5
2019-11-24 18:00 | 113.32 | 105.9
2019-11-24 18:30 | 112.74 | 104.59
2019-11-24 19:00 | 120.14 | 112.08
2019-11-24 19:30 | 117.69 | 109.27
2019-11-24 20:00 | 121.68 | 112.56
2019-11-24 20:30 | 121.06 | 112.58
2019-11-24 21:00 | 124.76 | 116.13
2019-11-24 21:30 | 116.76 | 107.72
2019-11-24 22:00 | 109.98 | 101.36
2019-11-24 22:30 | 107.34 | 99.46
2019-11-24 23:00 | 106.33 | 98.76
2019-11-24 23:30 | 102.31 | 95.08
2019-11-25 | 106 | 98.85
2019-11-25 00:30 | 111.67 | 103.43
2019-11-25 01:00 | 101.14 | 95.15
2019-11-25 01:30 | 106.36 | 100.09
2019-11-25 02:00 | 107.63 | 102.55
2019-11-25 02:30 | 98.4 | 93.45
2019-11-25 03:00 | 99.14 | 93.49
2019-11-25 03:30 | 104.45 | 98.84
2019-11-25 04:00 | 104.22 | 98.76
2019-11-25 04:30 | 106.4 | 100.22
2019-11-25 05:00 | 95.26 | 88.82
2019-11-25 05:30 | 91.78 | 84.95
2019-11-25 06:00 | 96.99 | 90.89
2019-11-25 06:30 | 84.62 | 77.07
2019-11-25 07:00 | 88.45 | 81.83
2019-11-25 07:30 | 89.26 | 82.19
2019-11-25 08:00 | 83.78 | 75.74
2019-11-25 08:30 | 85.38 | 77.39
2019-11-25 09:00 | 87.72 | 79.53
2019-11-25 09:30 | 87.61 | 76.17
2019-11-25 10:00 | 92.87 | 82.49
2019-11-25 10:30 | 97.29 | 87.6
2019-11-25 11:00 | 87.18 | 75.87
2019-11-25 11:30 | 81.47 | 67.17
2019-11-25 12:00 | 80.15 | 69.9
2019-11-25 12:30 | 86.61 | 73.48
2019-11-25 13:00 | 84.07 | 71.84
2019-11-25 13:30 | 82.21 | 69.53
2019-11-25 14:00 | 96.85 | 80.16
2019-11-25 14:30 | 97.1 | 79.93
2019-11-25 15:00 | 98.79 | 82.25
2019-11-25 15:30 | 100.43 | 81.05
2019-11-25 16:00 | 95.8 | 76.88
2019-11-25 16:30 | 103.47 | 87.85
2019-11-25 17:00 | 103.28 | 88.84
2019-11-25 17:30 | 104.99 | 94.53
2019-11-25 18:00 | 117.95 | 110.34
2019-11-25 18:30 | 101.96 | 95.45
2019-11-25 19:00 | 114.5 | 108.13
2019-11-25 19:30 | 119.29 | 113.13
2019-11-25 20:00 | 120.98 | 114.12
2019-11-25 20:30 | 120.15 | 113.3
2019-11-25 21:00 | 107.39 | 101.84
2019-11-25 21:30 | 99.86 | 94.28
2019-11-25 22:00 | 101.45 | 96.07
2019-11-25 22:30 | 106.36 | 101.04
2019-11-25 23:00 | 106.39 | 100.55
2019-11-25 23:30 | 103.31 | 97.23
2019-11-26 | 99.74 | 92.8
2019-11-26 00:30 | 102.92 | 95.64
2019-11-26 01:00 | 102.95 | 95.35
2019-11-26 01:30 | 96.66 | 89.64
2019-11-26 02:00 | 98.8 | 92.31
2019-11-26 02:30 | 100.57 | 94.23
2019-11-26 03:00 | 103.2 | 96.81
2019-11-26 03:30 | 100.42 | 94.3
2019-11-26 04:00 | 109.25 | 103.31
2019-11-26 04:30 | 104.92 | 98.77
2019-11-26 05:00 | 100.15 | 93.36
2019-11-26 05:30 | 107.88 | 101.34
2019-11-26 06:00 | 116.89 | 109.77
2019-11-26 06:30 | 104.78 | 95.25
2019-11-26 07:00 | 103.32 | 92.27
2019-11-26 07:30 | 96.08 | 81.54
2019-11-26 08:00 | 101.41 | 86.02
2019-11-26 08:30 | 93.15 | 78.09
2019-11-26 09:00 | 82.49 | 67.86
2019-11-26 09:30 | 84.58 | 71.33
2019-11-26 10:00 | 92.79 | 76.57
2019-11-26 10:30 | 87.03 | 71.29
2019-11-26 11:00 | 97.93 | 82.13
2019-11-26 11:30 | 92.78 | 77.47
2019-11-26 12:00 | 101.9 | 85.44
2019-11-26 12:30 | 109.2 | 92.8
2019-11-26 13:00 | 98.6 | 81.57
2019-11-26 13:30 | 98.35 | 80.18
2019-11-26 14:00 | 105.53 | 88.26
2019-11-26 14:30 | 105.07 | 88.97
2019-11-26 15:00 | 106.88 | 92.15
2019-11-26 15:30 | 104.69 | 88.99
2019-11-26 16:00 | 104.97 | 87.83
2019-11-26 16:30 | 107.27 | 92.41
2019-11-26 17:00 | 113.65 | 99.32
2019-11-26 17:30 | 114.75 | 103.91
2019-11-26 18:00 | 125.58 | 118.5
2019-11-26 18:30 | 110.93 | 104.29
2019-11-26 19:00 | 121.66 | 115.12
2019-11-26 19:30 | 114.99 | 109.19
2019-11-26 20:00 | 120.41 | 114.65
2019-11-26 20:30 | 116.19 | 109.49
2019-11-26 21:00 | 115.24 | 108.64
2019-11-26 21:30 | 125.78 | 119.78
2019-11-26 22:00 | 120.49 | 114.48
2019-11-26 22:30 | 120.41 | 113.95
2019-11-26 23:00 | 129.19 | 123.07
2019-11-26 23:30 | 123.49 | 116.93
2019-11-27 | 109.46 | 103.26
2019-11-27 00:30 | 119.43 | 112.45
2019-11-27 01:00 | 112.84 | 105.9
2019-11-27 01:30 | 118.93 | 111.71
2019-11-27 02:00 | 114.57 | 107.52
2019-11-27 02:30 | 121.09 | 114.27
2019-11-27 03:00 | 123.36 | 116.8
2019-11-27 03:30 | 118.16 | 111.95
2019-11-27 04:00 | 98.96 | 93.28
2019-11-27 04:30 | 111.72 | 106.35
2019-11-27 05:00 | 115.24 | 109.77
2019-11-27 05:30 | 117.6 | 111.82
2019-11-27 06:00 | 106.24 | 100.42
2019-11-27 06:30 | 84.68 | 76.46
2019-11-27 07:00 | 97.14 | 87.76
2019-11-27 07:30 | 96.18 | 83.01
2019-11-27 08:00 | 105.5 | 90.43
2019-11-27 08:30 | 91.9 | 76.25
2019-11-27 09:00 | 92.35 | 74.94
2019-11-27 09:30 | 93.63 | 76.58
2019-11-27 10:00 | 94.06 | 77.55
2019-11-27 10:30 | 102.41 | 85.44
2019-11-27 11:00 | 87.27 | 69.16
2019-11-27 11:30 | 94.5 | 73.32
2019-11-27 12:00 | 91.41 | 69.45
2019-11-27 12:30 | 96.53 | 75.68
2019-11-27 13:00 | 94.98 | 74.33
2019-11-27 13:30 | 98.37 | 78.73
2019-11-27 14:00 | 90.22 | 73.04
2019-11-27 14:30 | 95.52 | 76.62
2019-11-27 15:00 | 95.36 | 81.78
2019-11-27 15:30 | 114.86 | 104.91
2019-11-27 16:00 | 118.97 | 110.57
2019-11-27 16:30 | 111.08 | 99.28
2019-11-27 17:00 | 107.19 | 96.76
2019-11-27 17:30 | 110.15 | 99.84
2019-11-27 18:00 | 117.2 | 111.52
2019-11-27 18:30 | 112.08 | 106.6
2019-11-27 19:00 | 119.74 | 113.81
2019-11-27 19:30 | 106.79 | 101.21
2019-11-27 20:00 | 111.12 | 105.46
2019-11-27 20:30 | 112.39 | 106.06
2019-11-27 21:00 | 106.67 | 101.14
2019-11-27 21:30 | 106.12 | 100.76
2019-11-27 22:00 | 108.01 | 102.91
2019-11-27 22:30 | 108.21 | 103.44
2019-11-27 23:00 | 105.07 | 100.5
2019-11-27 23:30 | 109.43 | 104.5
2019-11-28 | 103.25 | 98.11
2019-11-28 00:30 | 107.56 | 102.25
2019-11-28 01:00 | 103.61 | 98.46
2019-11-28 01:30 | 108.07 | 103.21
2019-11-28 02:00 | 105.87 | 101.11
2019-11-28 02:30 | 101.6 | 96.28
2019-11-28 03:00 | 101.18 | 95.52
2019-11-28 03:30 | 103.41 | 97.02
2019-11-28 04:00 | 103.75 | 97.45
2019-11-28 04:30 | 101.36 | 94.73
2019-11-28 05:00 | 100.94 | 94.44
2019-11-28 05:30 | 104.74 | 99.4
2019-11-28 06:00 | 97.39 | 92.03
2019-11-28 06:30 | 82.84 | 72.9
2019-11-28 07:00 | 92.22 | 81.59
2019-11-28 07:30 | 88.85 | 75.72
2019-11-28 08:00 | 96.54 | 82.52
2019-11-28 08:30 | 85.51 | 70.4
2019-11-28 09:00 | 92.96 | 77.8
2019-11-28 09:30 | 91.56 | 76.15
2019-11-28 10:00 | 89.12 | 74.01
2019-11-28 10:30 | 97.26 | 83.29
2019-11-28 11:00 | 101.8 | 88.36
2019-11-28 11:30 | 96.19 | 82.15
2019-11-28 12:00 | 93.98 | 79.53
2019-11-28 12:30 | 97.14 | 83.96
2019-11-28 13:00 | 99.77 | 85.4
2019-11-28 13:30 | 111.4 | 97.83
2019-11-28 14:00 | 110.42 | 96.93
2019-11-28 14:30 | 110.67 | 96.76
2019-11-28 15:00 | 115.27 | 103.88
2019-11-28 15:30 | 112.38 | 99.53
2019-11-28 16:00 | 111.59 | 102.92
2019-11-28 16:30 | 110.98 | 99.49
2019-11-28 17:00 | 112.25 | 102.09
2019-11-28 17:30 | 110.68 | 102.71
2019-11-28 18:00 | 125 | 118.55
2019-11-28 18:30 | 125.11 | 119.36
2019-11-28 19:00 | 121.5 | 116.11
2019-11-28 19:30 | 127.63 | 122.11
2019-11-28 20:00 | 125.97 | 120.57
2019-11-28 20:30 | 133.43 | 127.08
2019-11-28 21:00 | 122.79 | 117.13
2019-11-28 21:30 | 114.71 | 109.96
2019-11-28 22:00 | 111.05 | 106.83
2019-11-28 22:30 | 118.36 | 113.6
2019-11-28 23:00 | 121.51 | 116.42
2019-11-28 23:30 | 124.49 | 118.85
2019-11-29 | 120.05 | 113.89
2019-11-29 00:30 | 118.86 | 112.41
2019-11-29 01:00 | 121.49 | 114.45
2019-11-29 01:30 | 120.94 | 113.83
2019-11-29 02:00 | 124.46 | 118
2019-11-29 02:30 | 114.82 | 108.8
2019-11-29 03:00 | 115.13 | 109.46
2019-11-29 03:30 | 104.24 | 98.38
2019-11-29 04:00 | 111.24 | 105.07
2019-11-29 04:30 | 108.34 | 102.26
2019-11-29 05:00 | 113.45 | 107.52
2019-11-29 05:30 | 104.14 | 97.89
2019-11-29 06:00 | 117.21 | 110.42
2019-11-29 06:30 | 102.11 | 92.79
2019-11-29 07:00 | 104.34 | 93.18
2019-11-29 07:30 | 107.45 | 93.9
2019-11-29 08:00 | 104.16 | 90.19
2019-11-29 08:30 | 102.24 | 87.48
2019-11-29 09:00 | 107.75 | 89.54
2019-11-29 09:30 | 109.56 | 90.12
2019-11-29 10:00 | 109.43 | 89.68
2019-11-29 10:30 | 107.15 | 87.22
2019-11-29 11:00 | 106.61 | 86.68
2019-11-29 11:30 | 104.37 | 83.68
2019-11-29 12:00 | 111.29 | 89.32
2019-11-29 12:30 | 117.24 | 96.38
2019-11-29 13:00 | 112.17 | 91.3
2019-11-29 13:30 | 114.58 | 94.19
2019-11-29 14:00 | 123.83 | 103.96
2019-11-29 14:30 | 115.56 | 96.51
2019-11-29 15:00 | 102.71 | 86.34
2019-11-29 15:30 | 95.7 | 81.99
2019-11-29 16:00 | 108.58 | 96.49
2019-11-29 16:30 | 117.41 | 103.39
2019-11-29 17:00 | 123.07 | 109.72
2019-11-29 17:30 | 119.72 | 107.93
2019-11-29 18:00 | 126.15 | 117.91
2019-11-29 18:30 | 117.85 | 110.12
2019-11-29 19:00 | 130.58 | 124.56
2019-11-29 19:30 | 126.77 | 120.14
2019-11-29 20:00 | 122.46 | 116.57
2019-11-29 20:30 | 131.26 | 125.15
2019-11-29 21:00 | 124.9 | 118.07
2019-11-29 21:30 | 116.38 | 109.73
2019-11-29 22:00 | 120.47 | 114.28
2019-11-29 22:30 | 114.77 | 109.3
2019-11-29 23:00 | 118.82 | 112.86
2019-11-29 23:30 | 107.12 | 101.15
2019-11-30 | 119.04 | 112.96
2019-11-30 00:30 | 114.43 | 108.1
2019-11-30 01:00 | 101.8 | 95.76
2019-11-30 01:30 | 105.87 | 99.33
2019-11-30 02:00 | 112.37 | 106.84
2019-11-30 02:30 | 109.58 | 104.24
2019-11-30 03:00 | 110.59 | 105.32
2019-11-30 03:30 | 101.81 | 96.06
2019-11-30 04:00 | 110.3 | 104.66
2019-11-30 04:30 | 119 | 113.43
2019-11-30 05:00 | 113.6 | 107.94
2019-11-30 05:30 | 105.1 | 99.57
2019-11-30 06:00 | 113.89 | 107.43
2019-11-30 06:30 | 96.48 | 86.72
2019-11-30 07:00 | 106.05 | 94.42
2019-11-30 07:30 | 102.75 | 88.79
2019-11-30 08:00 | 97.75 | 81.97
2019-11-30 08:30 | 99.14 | 82.22
2019-11-30 09:00 | 92.97 | 73.56
2019-11-30 09:30 | 99.02 | 80.39
2019-11-30 10:00 | 99.03 | 80.09
2019-11-30 10:30 | 94.56 | 75.34
2019-11-30 11:00 | 100.05 | 80.87
2019-11-30 11:30 | 98.82 | 79.71
2019-11-30 12:00 | 99.21 | 79.22
2019-11-30 12:30 | 105.65 | 86.47
2019-11-30 13:00 | 112.15 | 94.08
2019-11-30 13:30 | 104.64 | 86.69
2019-11-30 14:00 | 108.02 | 91.91
2019-11-30 14:30 | 116.31 | 100.85
2019-11-30 15:00 | 113.79 | 98.73
2019-11-30 15:30 | 95.72 | 80.77
2019-11-30 16:00 | 107.88 | 91.36
2019-11-30 16:30 | 103.93 | 88.48
2019-11-30 17:00 | 104.14 | 90.48
2019-11-30 17:30 | 107.56 | 97.41
2019-11-30 18:00 | 111.41 | 104.35
2019-11-30 18:30 | 110.35 | 103.89
2019-11-30 19:00 | 119.29 | 113.25
2019-11-30 19:30 | 117.51 | 110.89
2019-11-30 20:00 | 126.83 | 120.63
2019-11-30 20:30 | 123.35 | 117.66
2019-11-30 21:00 | 120.85 | 115.5
2019-11-30 21:30 | 125.3 | 119.36
2019-11-30 22:00 | 119.22 | 113.4
2019-11-30 22:30 | 121.2 | 114.21
2019-11-30 23:00 | 120.58 | 114.42
2019-11-30 23:30 | 122.73 | 115.91
2019-12-01 | 121.4 | 114.98
2019-12-01 00:30 | 103.1 | 95.73
2019-12-01 01:00 | 116.76 | 109.9
2019-12-01 01:30 | 110.78 | 103.89
2019-12-01 02:00 | 111.83 | 105.17
2019-12-01 02:30 | 119.29 | 112.6
2019-12-01 03:00 | 108.82 | 101.55
2019-12-01 03:30 | 111.77 | 104.95
2019-12-01 04:00 | 120.75 | 113.87
2019-12-01 04:30 | 117.26 | 110.64
2019-12-01 05:00 | 116.44 | 109.63
2019-12-01 05:30 | 104.91 | 97.75
2019-12-01 06:00 | 114.1 | 106.73
2019-12-01 06:30 | 94.61 | 84
2019-12-01 07:00 | 95.55 | 82.9
2019-12-01 07:30 | 104.04 | 88.62
2019-12-01 08:00 | 94.92 | 77.87
2019-12-01 08:30 | 95.44 | 77.47
2019-12-01 09:00 | 102.06 | 83.22
2019-12-01 09:30 | 102.83 | 84.92
2019-12-01 10:00 | 106.96 | 88.65
2019-12-01 10:30 | 95.84 | 77.52
2019-12-01 11:00 | 106.07 | 85.64
2019-12-01 11:30 | 92.92 | 72.6
2019-12-01 12:00 | 95.4 | 76.66
2019-12-01 12:30 | 97.3 | 79.15
2019-12-01 13:00 | 106.48 | 89.58
2019-12-01 13:30 | 107.54 | 93.26
2019-12-01 14:00 | 110.75 | 96.6
2019-12-01 14:30 | 107.64 | 96.14
2019-12-01 15:00 | 112.04 | 103.56
2019-12-01 15:30 | 115.16 | 107.88
2019-12-01 16:00 | 118.73 | 111.09
2019-12-01 16:30 | 115.01 | 107.44
2019-12-01 17:00 | 120.73 | 113.51
2019-12-01 17:30 | 127.12 | 119.24
2019-12-01 18:00 | 126.47 | 120.14
2019-12-01 18:30 | 118.75 | 112.72
2019-12-01 19:00 | 125.55 | 120.28
2019-12-01 19:30 | 127.67 | 121.23
2019-12-01 20:00 | 127.48 | 120.38
2019-12-01 20:30 | 126.53 | 119.74
2019-12-01 21:00 | 129.16 | 122.49
2019-12-01 21:30 | 116.79 | 110.46
2019-12-01 22:00 | 118.91 | 112.89
2019-12-01 22:30 | 122.74 | 116.23
2019-12-01 23:00 | 127.9 | 121.91
2019-12-01 23:30 | 114.03 | 107.83
2019-12-02 | 117.8 | 112.01
2019-12-02 00:30 | 112.22 | 106.29
2019-12-02 01:00 | 109.53 | 103.27
2019-12-02 01:30 | 105.11 | 99.19
2019-12-02 02:00 | 111.46 | 105.54
2019-12-02 02:30 | 120.76 | 114.59
2019-12-02 03:00 | 107.53 | 101.19
2019-12-02 03:30 | 105.01 | 98.23
2019-12-02 04:00 | 114.06 | 107.29
2019-12-02 04:30 | 105.14 | 98.76
2019-12-02 05:00 | 111.29 | 103.53
2019-12-02 05:30 | 104.61 | 98.02
2019-12-02 06:00 | 104.51 | 98.26
2019-12-02 06:30 | 95.56 | 85.96
2019-12-02 07:00 | 101.64 | 88.65
2019-12-02 07:30 | 107.05 | 88.9
2019-12-02 08:00 | 108.03 | 87.58
2019-12-02 08:30 | 105.08 | 84.58
2019-12-02 09:00 | 109.76 | 90.33
2019-12-02 09:30 | 106.44 | 85.18
2019-12-02 10:00 | 105.34 | 84.16
2019-12-02 10:30 | 103.03 | 82.72
2019-12-02 11:00 | 101.47 | 80.18
2019-12-02 11:30 | 101.93 | 79.58
2019-12-02 12:00 | 109.13 | 88
2019-12-02 12:30 | 108.41 | 87.51
2019-12-02 13:00 | 111.4 | 91.62
2019-12-02 13:30 | 111.55 | 92.02
2019-12-02 14:00 | 113.19 | 94.97
2019-12-02 14:30 | 109.19 | 90.66
2019-12-02 15:00 | 114.2 | 95.96
2019-12-02 15:30 | 107.02 | 86.97
2019-12-02 16:00 | 118.08 | 98.79
2019-12-02 16:30 | 115.69 | 98.01
2019-12-02 17:00 | 121.1 | 106.42
2019-12-02 17:30 | 121.38 | 108.45
2019-12-02 18:00 | 121.1 | 111.64
2019-12-02 18:30 | 109.78 | 102.41
2019-12-02 19:00 | 118.74 | 112.89
2019-12-02 19:30 | 123.23 | 117.26
2019-12-02 20:00 | 124.11 | 118.68
2019-12-02 20:30 | 130.12 | 123.38
2019-12-02 21:00 | 117.2 | 111.05
2019-12-02 21:30 | 116.02 | 109.9
2019-12-02 22:00 | 117.78 | 111.1
2019-12-02 22:30 | 118.16 | 111.63
2019-12-02 23:00 | 115.43 | 108.55
2019-12-02 23:30 | 115.08 | 108.49
2019-12-03 | 109.68 | 103.04
2019-12-03 00:30 | 111.79 | 104.43
2019-12-03 01:00 | 112.22 | 104.76
2019-12-03 01:30 | 118.26 | 111.35
2019-12-03 02:00 | 118.18 | 111.61
2019-12-03 02:30 | 110.83 | 104.52
2019-12-03 03:00 | 113.99 | 107.73
2019-12-03 03:30 | 112.96 | 105.81
2019-12-03 04:00 | 117.97 | 110.42
2019-12-03 04:30 | 117.96 | 110.69
2019-12-03 05:00 | 114.95 | 107.71
2019-12-03 05:30 | 107.21 | 99.74
2019-12-03 06:00 | 105.03 | 97.38
2019-12-03 06:30 | 98.29 | 86.84
2019-12-03 07:00 | 104.78 | 90.74
2019-12-03 07:30 | 107 | 90.59
2019-12-03 08:00 | 107.5 | 86.69
2019-12-03 08:30 | 105.02 | 84.46
2019-12-03 09:00 | 100.53 | 77.97
2019-12-03 09:30 | 107.59 | 84.78
2019-12-03 10:00 | 117.1 | 97.25
2019-12-03 10:30 | 109.56 | 86.78
2019-12-03 11:00 | 110.43 | 87.45
2019-12-03 11:30 | 114.05 | 92.74
2019-12-03 12:00 | 115.97 | 94.19
2019-12-03 12:30 | 110.23 | 88.09
2019-12-03 13:00 | 112.99 | 91.53
2019-12-03 13:30 | 114.59 | 94.53
2019-12-03 14:00 | 114.17 | 94.22
2019-12-03 14:30 | 105.9 | 85.67
2019-12-03 15:00 | 106.44 | 87.73
2019-12-03 15:30 | 113.71 | 94.5
2019-12-03 16:00 | 121.26 | 102.81
2019-12-03 16:30 | 116.74 | 100.06
2019-12-03 17:00 | 120.42 | 107.09
2019-12-03 17:30 | 118.54 | 108.21
2019-12-03 18:00 | 125.76 | 118.65
2019-12-03 18:30 | 124.32 | 118.78
2019-12-03 19:00 | 128.22 | 122.18
2019-12-03 19:30 | 126.68 | 120.02
2019-12-03 20:00 | 134.84 | 127.08
2019-12-03 20:30 | 127.44 | 120.71
2019-12-03 21:00 | 126.27 | 118.76
2019-12-03 21:30 | 119.92 | 112.78
2019-12-03 22:00 | 120.97 | 114.81
2019-12-03 22:30 | 124.01 | 116.73
2019-12-03 23:00 | 125.45 | 118.11
2019-12-03 23:30 | 112.35 | 105.1
2019-12-04 | 117.94 | 110.05
2019-12-04 00:30 | 110.69 | 103.43
2019-12-04 01:00 | 114.72 | 107.6
2019-12-04 01:30 | 115.51 | 108.76
2019-12-04 02:00 | 117.01 | 109.84
2019-12-04 02:30 | 111.06 | 104.34
2019-12-04 03:00 | 114.33 | 107.01
2019-12-04 03:30 | 112.29 | 105.34
2019-12-04 04:00 | 108.29 | 101.37
2019-12-04 04:30 | 109.89 | 102.91
2019-12-04 05:00 | 106.61 | 100.33
2019-12-04 05:30 | 111.23 | 104.74
2019-12-04 06:00 | 106.21 | 98.92
2019-12-04 06:30 | 96.4 | 86.61
2019-12-04 07:00 | 99.02 | 87.42
2019-12-04 07:30 | 88.27 | 72.86
2019-12-04 08:00 | 89.8 | 72.19
2019-12-04 08:30 | 97.41 | 78.02
2019-12-04 09:00 | 98.62 | 80.07
2019-12-04 09:30 | 104.76 | 86.16
2019-12-04 10:00 | 109.34 | 89.9
2019-12-04 10:30 | 101.96 | 81.4
2019-12-04 11:00 | 108 | 88.43
2019-12-04 11:30 | 107.27 | 87.22
2019-12-04 12:00 | 106.16 | 87.21
2019-12-04 12:30 | 114.9 | 96.78
2019-12-04 13:00 | 108.1 | 90.42
2019-12-04 13:30 | 110.84 | 92.66
2019-12-04 14:00 | 105.26 | 88.13
2019-12-04 14:30 | 106.44 | 89.55
2019-12-04 15:00 | 110.75 | 93.94
2019-12-04 15:30 | 111 | 94.31
2019-12-04 16:00 | 108.43 | 92.99
2019-12-04 16:30 | 110.47 | 96.02
2019-12-04 17:00 | 112.04 | 99.35
2019-12-04 17:30 | 109.17 | 98.68
2019-12-04 18:00 | 121.95 | 113.41
2019-12-04 18:30 | 124.01 | 116.58
2019-12-04 19:00 | 125.63 | 119.73
2019-12-04 19:30 | 123.23 | 117.73
2019-12-04 20:00 | 127.75 | 121.39
2019-12-04 20:30 | 123.25 | 116.42
2019-12-04 21:00 | 109.15 | 102.63
2019-12-04 21:30 | 113.9 | 107.57
2019-12-04 22:00 | 116.95 | 110.9
2019-12-04 22:30 | 112.62 | 106.4
2019-12-04 23:00 | 115.43 | 110.04
2019-12-04 23:30 | 115.04 | 108.99
2019-12-05 | 106.1 | 98.74
2019-12-05 00:30 | 114.29 | 106.97
2019-12-05 01:00 | 118.32 | 111.06
2019-12-05 01:30 | 114.91 | 107.89
2019-12-05 02:00 | 115.56 | 108.87
2019-12-05 02:30 | 108.73 | 102.27
2019-12-05 03:00 | 118.84 | 111.81
2019-12-05 03:30 | 112.66 | 106.04
2019-12-05 04:00 | 105.9 | 98.91
2019-12-05 04:30 | 107.37 | 99.73
2019-12-05 05:00 | 106.41 | 98.69
2019-12-05 05:30 | 104.72 | 97.85
2019-12-05 06:00 | 106.36 | 99.09
2019-12-05 06:30 | 96.98 | 87.06
2019-12-05 07:00 | 91.33 | 77.24
2019-12-05 07:30 | 98.49 | 83.11
2019-12-05 08:00 | 101.88 | 85.12
2019-12-05 08:30 | 87.09 | 72.27
2019-12-05 09:00 | 82.17 | 69.74
2019-12-05 09:30 | 93.57 | 82.1
2019-12-05 10:00 | 92.35 | 80.74
2019-12-05 10:30 | 81.88 | 68.71
2019-12-05 11:00 | 85.91 | 73.13
2019-12-05 11:30 | 92.28 | 73.24
2019-12-05 12:00 | 90.73 | 69.49
2019-12-05 12:30 | 92.54 | 73.81
2019-12-05 13:00 | 83.59 | 73.24
2019-12-05 13:30 | 88.64 | 78.88
2019-12-05 14:00 | 92.3 | 79.99
2019-12-05 14:30 | 82.07 | 68.67
2019-12-05 15:00 | 84.24 | 71.15
2019-12-05 15:30 | 87.11 | 74.37
2019-12-05 16:00 | 93.38 | 82.14
2019-12-05 16:30 | 89.79 | 79.16
2019-12-05 17:00 | 92.59 | 83.34
2019-12-05 17:30 | 94.97 | 86.35
2019-12-05 18:00 | 108.64 | 102.35
2019-12-05 18:30 | 100.93 | 94.95
2019-12-05 19:00 | 104.38 | 98.33
2019-12-05 19:30 | 110.38 | 105.81
2019-12-05 20:00 | 110.6 | 105.59
2019-12-05 20:30 | 114.95 | 110.07
2019-12-05 21:00 | 111.43 | 105.84
2019-12-05 21:30 | 123.06 | 117.11
2019-12-05 22:00 | 119.24 | 113.56
2019-12-05 22:30 | 116.65 | 110.67
2019-12-05 23:00 | 114.15 | 107.93
2019-12-05 23:30 | 109 | 102.61
2019-12-06 | 111.29 | 104.23
2019-12-06 00:30 | 116.67 | 109.3
2019-12-06 01:00 | 117.64 | 110.41
2019-12-06 01:30 | 115.34 | 108.16
2019-12-06 02:00 | 115.38 | 108.89
2019-12-06 02:30 | 115.03 | 108.58
2019-12-06 03:00 | 123.61 | 117.24
2019-12-06 03:30 | 121.9 | 115.73
2019-12-06 04:00 | 104.45 | 98.06
2019-12-06 04:30 | 118.38 | 112.42
2019-12-06 05:00 | 116.93 | 110.96
2019-12-06 05:30 | 115.93 | 110.02
2019-12-06 06:00 | 126.94 | 121.09
2019-12-06 06:30 | 103.72 | 94.31
2019-12-06 07:00 | 105.68 | 94.73
2019-12-06 07:30 | 100.65 | 87.17
2019-12-06 08:00 | 107.44 | 94.17
2019-12-06 08:30 | 103.5 | 90.77
2019-12-06 09:00 | 99.85 | 85.82
2019-12-06 09:30 | 103.37 | 88.37
2019-12-06 10:00 | 110.85 | 96.24
2019-12-06 10:30 | 102.9 | 86.79
2019-12-06 11:00 | 106.89 | 92.28
2019-12-06 11:30 | 107.39 | 92.97
2019-12-06 12:00 | 114.47 | 99.94
2019-12-06 12:30 | 118.66 | 107.86
2019-12-06 13:00 | 111.93 | 99.63
2019-12-06 13:30 | 115.11 | 100.73
2019-12-06 14:00 | 113.87 | 102.38
2019-12-06 14:30 | 115.78 | 103.23
2019-12-06 15:00 | 115.94 | 102.76
2019-12-06 15:30 | 121.98 | 113.25
2019-12-06 16:00 | 123.52 | 117.78
2019-12-06 16:30 | 112.7 | 105.39
2019-12-06 17:00 | 108.97 | 99.28
2019-12-06 17:30 | 121.28 | 115.65
2019-12-06 18:00 | 111.66 | 106.6
2019-12-06 18:30 | 113.52 | 107.86
2019-12-06 19:00 | 120 | 115.01
2019-12-06 19:30 | 120.95 | 115.98
2019-12-06 20:00 | 122.58 | 117.48
2019-12-06 20:30 | 119.23 | 113.86
2019-12-06 21:00 | 121.47 | 116.39
2019-12-06 21:30 | 113.8 | 108.3
2019-12-06 22:00 | 114.57 | 108.72
2019-12-06 22:30 | 123.44 | 117.5
2019-12-06 23:00 | 123.04 | 117.06
2019-12-06 23:30 | 126.18 | 120.14
2019-12-07 | 122.7 | 116.34
2019-12-07 00:30 | 117.89 | 111.81
2019-12-07 01:00 | 119.78 | 113.63
2019-12-07 01:30 | 127.81 | 121.56
2019-12-07 02:00 | 122.28 | 116.12
2019-12-07 02:30 | 112.19 | 105.24
2019-12-07 03:00 | 109.97 | 103.17
2019-12-07 03:30 | 110.02 | 103.55
2019-12-07 04:00 | 113.16 | 107.26
2019-12-07 04:30 | 118.04 | 112.43
2019-12-07 05:00 | 108.73 | 103.1
2019-12-07 05:30 | 110.46 | 104.86
2019-12-07 06:00 | 114.49 | 108.88
2019-12-07 06:30 | 103.17 | 93.02
2019-12-07 07:00 | 103.67 | 93.76
2019-12-07 07:30 | 97.8 | 85.96
2019-12-07 08:00 | 92.36 | 80.4
2019-12-07 08:30 | 89.55 | 76.47
2019-12-07 09:00 | 89.04 | 77.3
2019-12-07 09:30 | 92.28 | 80.68
2019-12-07 10:00 | 89.83 | 76.84
2019-12-07 10:30 | 87.8 | 73.7
2019-12-07 11:00 | 93.56 | 80.89
2019-12-07 11:30 | 97.09 | 85.28
2019-12-07 12:00 | 98.3 | 87.11
2019-12-07 12:30 | 98.24 | 87.52
2019-12-07 13:00 | 101.64 | 89.75
2019-12-07 13:30 | 99.64 | 89.71
2019-12-07 14:00 | 102.52 | 92.56
2019-12-07 14:30 | 112.01 | 101.96
2019-12-07 15:00 | 110.91 | 100.23
2019-12-07 15:30 | 110.03 | 99.07
2019-12-07 16:00 | 102 | 91.73
2019-12-07 16:30 | 106.4 | 96.03
2019-12-07 17:00 | 108.31 | 99.34
2019-12-07 17:30 | 108.64 | 100.81
2019-12-07 18:00 | 109.16 | 103.37
2019-12-07 18:30 | 109.59 | 104.38
2019-12-07 19:00 | 112.86 | 108.13
2019-12-07 19:30 | 113.52 | 109.46
2019-12-07 20:00 | 110.53 | 105.93
2019-12-07 20:30 | 117.92 | 113.04
2019-12-07 21:00 | 116.92 | 111.89
2019-12-07 21:30 | 118.11 | 112.93
2019-12-07 22:00 | 112.91 | 107.74
2019-12-07 22:30 | 114.76 | 109.98
2019-12-07 23:00 | 113.5 | 108.56
2019-12-07 23:30 | 113.4 | 108.12
2019-12-08 | 114.29 | 109.13
2019-12-08 00:30 | 111.47 | 106.15
2019-12-08 01:00 | 117.75 | 112.41
2019-12-08 01:30 | 115.1 | 109.61
2019-12-08 02:00 | 110.86 | 105.55
2019-12-08 02:30 | 122.44 | 117.12
2019-12-08 03:00 | 124.43 | 119.01
2019-12-08 03:30 | 118.88 | 113.19
2019-12-08 04:00 | 118.49 | 111.99
2019-12-08 04:30 | 125.85 | 119.93
2019-12-08 05:00 | 119.58 | 113.97
2019-12-08 05:30 | 120.59 | 114.72
2019-12-08 06:00 | 111.53 | 105.2
2019-12-08 06:30 | 98.17 | 88.73
2019-12-08 07:00 | 98.12 | 86.38
2019-12-08 07:30 | 101.07 | 90.7
2019-12-08 08:00 | 102.71 | 91.35
2019-12-08 08:30 | 94.04 | 81.16
2019-12-08 09:00 | 97.91 | 85.06
2019-12-08 09:30 | 94.78 | 82.39
2019-12-08 10:00 | 99.4 | 86.96
2019-12-08 10:30 | 103.5 | 91.44
2019-12-08 11:00 | 98.88 | 84.75
2019-12-08 11:30 | 92.11 | 78.41
2019-12-08 12:00 | 102.42 | 90.29
2019-12-08 12:30 | 107.35 | 94.67
2019-12-08 13:00 | 104.05 | 91.34
2019-12-08 13:30 | 106.2 | 93.96
2019-12-08 14:00 | 107.43 | 95.1
2019-12-08 14:30 | 107.61 | 95.02
2019-12-08 15:00 | 103.87 | 91.9
2019-12-08 15:30 | 102.91 | 92.23
2019-12-08 16:00 | 103.06 | 93.22
2019-12-08 16:30 | 105.31 | 95.27
2019-12-08 17:00 | 104.24 | 95.02
2019-12-08 17:30 | 105.32 | 97.35
2019-12-08 18:00 | 111.16 | 105.01
2019-12-08 18:30 | 124 | 119.73
2019-12-08 19:00 | 132.59 | 128.69
2019-12-08 19:30 | 119.35 | 115.16
2019-12-08 20:00 | 132.5 | 127.43
2019-12-08 20:30 | 134.9 | 129.61
2019-12-08 21:00 | 136.4 | 130.79
2019-12-08 21:30 | 122.89 | 118.31
2019-12-08 22:00 | 119.24 | 114.62
2019-12-08 22:30 | 123.05 | 117.97
2019-12-08 23:00 | 120.45 | 115.14
2019-12-08 23:30 | 113.22 | 106.95
2019-12-09 | 110.75 | 103.73
2019-12-09 00:30 | 120.73 | 114.41
2019-12-09 01:00 | 115.86 | 108.95
2019-12-09 01:30 | 124.76 | 118.75
2019-12-09 02:00 | 120.76 | 114.38
2019-12-09 02:30 | 121.78 | 115.77
2019-12-09 03:00 | 123.64 | 118.31
2019-12-09 03:30 | 113.89 | 108.25
2019-12-09 04:00 | 114.52 | 109.34
2019-12-09 04:30 | 114.35 | 108.79
2019-12-09 05:00 | 110.66 | 103.9
2019-12-09 05:30 | 105.24 | 98.28
2019-12-09 06:00 | 107.61 | 101.6
2019-12-09 06:30 | 98.72 | 91.81
2019-12-09 07:00 | 99.42 | 91.45
2019-12-09 07:30 | 107.14 | 99.84
2019-12-09 08:00 | 102.7 | 93.17
2019-12-09 08:30 | 104.99 | 95.32
2019-12-09 09:00 | 98.28 | 84.19
2019-12-09 09:30 | 90.9 | 77.01
2019-12-09 10:00 | 85.63 | 72.02
2019-12-09 10:30 | 88.85 | 75.06
2019-12-09 11:00 | 83.82 | 69.82
2019-12-09 11:30 | 82.42 | 67.84
2019-12-09 12:00 | 86.44 | 72.78
2019-12-09 12:30 | 92.01 | 79.49
2019-12-09 13:00 | 93.34 | 81.71
2019-12-09 13:30 | 91.66 | 79.54
2019-12-09 14:00 | 93.89 | 83.14
2019-12-09 14:30 | 99.23 | 88.25
2019-12-09 15:00 | 95.66 | 84.42
2019-12-09 15:30 | 101.1 | 91.06
2019-12-09 16:00 | 104.06 | 94.71
2019-12-09 16:30 | 103.18 | 94.46
2019-12-09 17:00 | 100.58 | 91.22
2019-12-09 17:30 | 104.12 | 97.25
2019-12-09 18:00 | 112 | 107.68
2019-12-09 18:30 | 112.6 | 108.24
2019-12-09 19:00 | 117.23 | 113.41
2019-12-09 19:30 | 121.17 | 117.11
2019-12-09 20:00 | 122.86 | 118.87
2019-12-09 20:30 | 119.83 | 115.75
2019-12-09 21:00 | 121.07 | 117.04
2019-12-09 21:30 | 118.66 | 113.39
2019-12-09 22:00 | 115.67 | 110.49
2019-12-09 22:30 | 119.05 | 114.17
2019-12-09 23:00 | 117.53 | 112.7
2019-12-09 23:30 | 114.05 | 108.67
2019-12-10 | 113.58 | 108.13
2019-12-10 00:30 | 117.74 | 112.2
2019-12-10 01:00 | 117.37 | 111.83
2019-12-10 01:30 | 113.21 | 107.3
2019-12-10 02:00 | 121.26 | 115.43
2019-12-10 02:30 | 118.63 | 112.45
2019-12-10 03:00 | 115.77 | 109.32
2019-12-10 03:30 | 124.62 | 118.44
2019-12-10 04:00 | 117.26 | 110.41
2019-12-10 04:30 | 109.48 | 101.71
2019-12-10 05:00 | 110.5 | 102.6
2019-12-10 05:30 | 109.55 | 100.93
2019-12-10 06:00 | 111.32 | 104.22
2019-12-10 06:30 | 100.02 | 89.26
2019-12-10 07:00 | 99.86 | 88
2019-12-10 07:30 | 96.53 | 82.63
2019-12-10 08:00 | 101 | 88.55
2019-12-10 08:30 | 103.38 | 89.63
2019-12-10 09:00 | 98.47 | 83.84
2019-12-10 09:30 | 103.76 | 90.39
2019-12-10 10:00 | 98.56 | 83.97
2019-12-10 10:30 | 101.98 | 88.69
2019-12-10 11:00 | 102.12 | 87.95
2019-12-10 11:30 | 99.46 | 83.19
2019-12-10 12:00 | 98.65 | 82.78
2019-12-10 12:30 | 97.93 | 81.93
2019-12-10 13:00 | 95.98 | 80.65
2019-12-10 13:30 | 104.43 | 90.59
2019-12-10 14:00 | 99.72 | 85.8
2019-12-10 14:30 | 103.14 | 88.56
2019-12-10 15:00 | 99.82 | 86.71
2019-12-10 15:30 | 101.74 | 88.9
2019-12-10 16:00 | 108.59 | 97.06
2019-12-10 16:30 | 113.91 | 103.52
2019-12-10 17:00 | 106.67 | 95.32
2019-12-10 17:30 | 108.76 | 100.14
2019-12-10 18:00 | 112.27 | 106.12
2019-12-10 18:30 | 114.47 | 108.52
2019-12-10 19:00 | 129.83 | 125.26
2019-12-10 19:30 | 127.45 | 122.66
2019-12-10 20:00 | 127.84 | 122.98
2019-12-10 20:30 | 118.16 | 111.32
2019-12-10 21:00 | 119.16 | 112.4
2019-12-10 21:30 | 118.45 | 111.31
2019-12-10 22:00 | 120.27 | 113.57
2019-12-10 22:30 | 126.95 | 120.86
2019-12-10 23:00 | 118.37 | 111.17
2019-12-10 23:30 | 117.31 | 110.63
2019-12-11 | 112.57 | 105.7
2019-12-11 00:30 | 107.8 | 100.43
2019-12-11 01:00 | 108.79 | 101.32
2019-12-11 01:30 | 108.85 | 102.12
2019-12-11 02:00 | 105.39 | 98.22
2019-12-11 02:30 | 109.9 | 103.06
2019-12-11 03:00 | 101.59 | 94.42
2019-12-11 03:30 | 99.56 | 92.57
2019-12-11 04:00 | 104.39 | 98.35
2019-12-11 04:30 | 101.49 | 94.53
2019-12-11 05:00 | 104.55 | 98.47
2019-12-11 05:30 | 101.57 | 95.13
2019-12-11 06:00 | 100.65 | 95.39
2019-12-11 06:30 | 73.02 | 61.65
2019-12-11 07:00 | 71.24 | 60.02
2019-12-11 07:30 | 70.48 | 59.44
2019-12-11 08:00 | 70.21 | 59.08
2019-12-11 08:30 | 63.01 | 49.47
2019-12-11 09:00 | 73.06 | 62.75
2019-12-11 09:30 | 76.46 | 65.89
2019-12-11 10:00 | 77.89 | 68.01
2019-12-11 10:30 | 75.49 | 65.58
2019-12-11 11:00 | 72.61 | 60.51
2019-12-11 11:30 | 78.7 | 68.8
2019-12-11 12:00 | 76 | 65.08
2019-12-11 12:30 | 72.73 | 63.6
2019-12-11 13:00 | 75.39 | 65.05
2019-12-11 13:30 | 76.49 | 65.81
2019-12-11 14:00 | 79.18 | 69.58
2019-12-11 14:30 | 74.58 | 63.89
2019-12-11 15:00 | 76.55 | 66.63
2019-12-11 15:30 | 77.85 | 68.98
2019-12-11 16:00 | 80.88 | 71.99
2019-12-11 16:30 | 86.84 | 78.65
2019-12-11 17:00 | 90.14 | 82.88
2019-12-11 17:30 | 88.38 | 82.01
2019-12-11 18:00 | 95.73 | 90.05
2019-12-11 18:30 | 98.04 | 91.37
2019-12-11 19:00 | 101.31 | 94.94
2019-12-11 19:30 | 97.74 | 91
2019-12-11 20:00 | 109.4 | 104.31
2019-12-11 20:30 | 109.04 | 104.33
2019-12-11 21:00 | 111.12 | 106.41
2019-12-11 21:30 | 106.4 | 100.82
2019-12-11 22:00 | 108.59 | 103
2019-12-11 22:30 | 103.22 | 96.47
2019-12-11 23:00 | 98.94 | 91.94
2019-12-11 23:30 | 100.08 | 93.03
2019-12-12 | 98.4 | 90.41
2019-12-12 00:30 | 101.68 | 95.33
2019-12-12 01:00 | 103.12 | 96.65
2019-12-12 01:30 | 100.72 | 93
2019-12-12 02:00 | 101.86 | 93.89
2019-12-12 02:30 | 105.43 | 99.72
2019-12-12 03:00 | 101.13 | 99.19
2019-12-12 03:30 | 91.73 | 89.6
2019-12-12 04:00 | 96.29 | 94.04
2019-12-12 04:30 | 99.8 | 97.96
2019-12-12 05:00 | 93.46 | 91.55
2019-12-12 05:30 | 87.88 | 85.74
2019-12-12 06:00 | 93.04 | 91.25
2019-12-12 06:30 | 74.11 | 70.69
2019-12-12 07:00 | 72.69 | 68.27
2019-12-12 07:30 | 71.41 | 65.43
2019-12-12 08:00 | 71.41 | 65.43
2019-12-12 08:30 | 66.15 | 59.33
2019-12-12 09:00 | 69.65 | 62.5
2019-12-12 09:30 | 72.77 | 66.36
2019-12-12 10:00 | 71.95 | 65.94
2019-12-12 10:30 | 72.23 | 63.75
2019-12-12 11:00 | 83.05 | 71.04
2019-12-12 11:30 | 82.79 | 70.48
2019-12-12 12:00 | 83.65 | 72.17
2019-12-12 12:30 | 90.72 | 81.84
2019-12-12 13:00 | 81.59 | 70.36
2019-12-12 13:30 | 88.24 | 78.68
2019-12-12 14:00 | 87.05 | 76.66
2019-12-12 14:30 | 82.6 | 72.04
2019-12-12 15:00 | 82.04 | 72.15
2019-12-12 15:30 | 88.58 | 79.11
2019-12-12 16:00 | 94.66 | 86.12
2019-12-12 16:30 | 91.32 | 82.74
2019-12-12 17:00 | 92.39 | 84.56
2019-12-12 17:30 | 105.02 | 100.86
2019-12-12 18:00 | 109.6 | 106.03
2019-12-12 18:30 | 103.73 | 98.68
2019-12-12 19:00 | 115.47 | 111.36
2019-12-12 19:30 | 119.4 | 115.15
2019-12-12 20:00 | 114.56 | 109.71
2019-12-12 20:30 | 116.86 | 112.61
2019-12-12 21:00 | 105.53 | 100.5
2019-12-12 21:30 | 104.01 | 98.42
2019-12-12 22:00 | 111.84 | 105.9
2019-12-12 22:30 | 114.77 | 108.54
2019-12-12 23:00 | 111.46 | 105.83
2019-12-12 23:30 | 108.19 | 100.39
2019-12-13 | 112.32 | 105.3
2019-12-13 00:30 | 111.86 | 105.45
2019-12-13 01:00 | 111.71 | 105.15
2019-12-13 01:30 | 109.34 | 102.76
2019-12-13 02:00 | 108.46 | 101.62
2019-12-13 02:30 | 107.21 | 99.48
2019-12-13 03:00 | 106.22 | 97.52
2019-12-13 03:30 | 104.78 | 96.65
2019-12-13 04:00 | 110.32 | 102.91
2019-12-13 04:30 | 107.4 | 99.31
2019-12-13 05:00 | 105.99 | 97.2
2019-12-13 05:30 | 108.55 | 100.44
2019-12-13 06:00 | 105.98 | 98.08
2019-12-13 06:30 | 98.31 | 86.07
2019-12-13 07:00 | 98.48 | 85.3
2019-12-13 07:30 | 91.8 | 77.33
2019-12-13 08:00 | 88.11 | 74.08
2019-12-13 08:30 | 84.58 | 70.84
2019-12-13 09:00 | 89.32 | 76.13
2019-12-13 09:30 | 87.14 | 72.3
2019-12-13 10:00 | 90.37 | 77.37
2019-12-13 10:30 | 85.95 | 73.25
2019-12-13 11:00 | 91.48 | 77.88
2019-12-13 11:30 | 93.67 | 79.93
2019-12-13 12:00 | 97.68 | 86.31
2019-12-13 12:30 | 106.26 | 94.61
2019-12-13 13:00 | 103.08 | 91.39
2019-12-13 13:30 | 98.44 | 87.72
2019-12-13 14:00 | 106.66 | 95.89
2019-12-13 14:30 | 103.86 | 92.63
2019-12-13 15:00 | 98.81 | 87.07
2019-12-13 15:30 | 97.01 | 84.35
2019-12-13 16:00 | 98.19 | 85.57
2019-12-13 16:30 | 100.35 | 89.56
2019-12-13 17:00 | 111.24 | 104.41
2019-12-13 17:30 | 116.43 | 111.22
2019-12-13 18:00 | 119.13 | 113.62
2019-12-13 18:30 | 110.79 | 105.86
2019-12-13 19:00 | 121.93 | 118.45
2019-12-13 19:30 | 134.35 | 130.11
2019-12-13 20:00 | 134.13 | 128.97
2019-12-13 20:30 | 133.2 | 128.22
2019-12-13 21:00 | 132.81 | 127.69
2019-12-13 21:30 | 135.91 | 131.53
2019-12-13 22:00 | 128.73 | 123.74
2019-12-13 22:30 | 126.43 | 121.01
2019-12-13 23:00 | 128.1 | 122.45
2019-12-13 23:30 | 126.75 | 120.78
2019-12-14 | 125.37 | 119.31
2019-12-14 00:30 | 116.9 | 110.2
2019-12-14 01:00 | 120.87 | 114.37
2019-12-14 01:30 | 125.61 | 119.32
2019-12-14 02:00 | 121.63 | 115.01
2019-12-14 02:30 | 129.11 | 123.84
2019-12-14 03:00 | 126.09 | 119.96
2019-12-14 03:30 | 116.34 | 109.6
2019-12-14 04:00 | 111.98 | 104.81
2019-12-14 04:30 | 113.93 | 107.43
2019-12-14 05:00 | 111.7 | 104.91
2019-12-14 05:30 | 104.32 | 95.9
2019-12-14 06:00 | 106.46 | 98.9
2019-12-14 06:30 | 100.44 | 90.8
2019-12-14 07:00 | 105.94 | 95.78
2019-12-14 07:30 | 107.4 | 98.78
2019-12-14 08:00 | 104.13 | 96.19
2019-12-14 08:30 | 101.54 | 92.15
2019-12-14 09:00 | 98 | 86.88
2019-12-14 09:30 | 98.97 | 87.03
2019-12-14 10:00 | 94.83 | 81.29
2019-12-14 10:30 | 100.43 | 86.65
2019-12-14 11:00 | 95.02 | 81.69
2019-12-14 11:30 | 96.26 | 83.16
2019-12-14 12:00 | 95.73 | 84.85
2019-12-14 12:30 | 97.52 | 87.29
2019-12-14 13:00 | 102.35 | 93.1
2019-12-14 13:30 | 102.97 | 92.74
2019-12-14 14:00 | 94.71 | 84.22
2019-12-14 14:30 | 98.94 | 90.97
2019-12-14 15:00 | 113.32 | 108.09
2019-12-14 15:30 | 112.19 | 104.43
2019-12-14 16:00 | 109.33 | 102.46
2019-12-14 16:30 | 119.98 | 115.11
2019-12-14 17:00 | 113.81 | 108.4
2019-12-14 17:30 | 110.19 | 104.91
2019-12-14 18:00 | 111.42 | 106.99
2019-12-14 18:30 | 97.96 | 92.03
2019-12-14 19:00 | 110.05 | 104.87
2019-12-14 19:30 | 113.95 | 108.71
2019-12-14 20:00 | 116.05 | 111.62
2019-12-14 20:30 | 113.81 | 109.54
2019-12-14 21:00 | 124.22 | 119.12
2019-12-14 21:30 | 123.33 | 117.73
2019-12-14 22:00 | 130.47 | 124.92
2019-12-14 22:30 | 128.13 | 122.59
2019-12-14 23:00 | 123.89 | 118.16
2019-12-14 23:30 | 115.71 | 109.68
2019-12-15 | 115.85 | 109.32
2019-12-15 00:30 | 101.19 | 94.31
2019-12-15 01:00 | 112.99 | 106.9
2019-12-15 01:30 | 117.14 | 110.81
2019-12-15 02:00 | 109.05 | 101.83
2019-12-15 02:30 | 108.61 | 101.13
2019-12-15 03:00 | 108.88 | 101.44
2019-12-15 03:30 | 118.73 | 111.84
2019-12-15 04:00 | 109.92 | 102.99
2019-12-15 04:30 | 116.15 | 109.17
2019-12-15 05:00 | 113.28 | 106.46
2019-12-15 05:30 | 104.84 | 96.65
2019-12-15 06:00 | 111.01 | 104.12
2019-12-15 06:30 | 99.07 | 88.5
2019-12-15 07:00 | 96.34 | 85.75
2019-12-15 07:30 | 98.27 | 86.54
2019-12-15 08:00 | 97.83 | 85.54
2019-12-15 08:30 | 95.04 | 81.82
2019-12-15 09:00 | 94.62 | 79.75
2019-12-15 09:30 | 93.5 | 77.77
2019-12-15 10:00 | 103.42 | 88.78
2019-12-15 10:30 | 97.08 | 83.07
2019-12-15 11:00 | 103.46 | 89.91
2019-12-15 11:30 | 109.13 | 95.01
2019-12-15 12:00 | 100.71 | 86.97
2019-12-15 12:30 | 100.91 | 86.88
2019-12-15 13:00 | 101.67 | 88.65
2019-12-15 13:30 | 102.22 | 89.72
2019-12-15 14:00 | 108.61 | 96.9
2019-12-15 14:30 | 108.15 | 97.08
2019-12-15 15:00 | 98.12 | 87.23
2019-12-15 15:30 | 100.11 | 89.98
2019-12-15 16:00 | 103 | 91.14
2019-12-15 16:30 | 115.61 | 105.56
2019-12-15 17:00 | 106.31 | 96.66
2019-12-15 17:30 | 113.85 | 105.28
2019-12-15 18:00 | 118.04 | 112.24
2019-12-15 18:30 | 108.92 | 103.77
2019-12-15 19:00 | 127.19 | 123.25
2019-12-15 19:30 | 127.76 | 123.4
2019-12-15 20:00 | 130.32 | 124.81
2019-12-15 20:30 | 130.31 | 123.8
2019-12-15 21:00 | 130.92 | 125.02
2019-12-15 21:30 | 125.74 | 119.72
2019-12-15 22:00 | 129.5 | 123.82
2019-12-15 22:30 | 124.51 | 118.46
2019-12-15 23:00 | 118.1 | 111.69
2019-12-15 23:30 | 124.99 | 118.98
2019-12-16 | 119.71 | 113.36
2019-12-16 00:30 | 114.39 | 108.17
2019-12-16 01:00 | 117.2 | 109.63
2019-12-16 01:30 | 112.1 | 103.74
2019-12-16 02:00 | 116.43 | 108.76
2019-12-16 02:30 | 122.13 | 115.05
2019-12-16 03:00 | 116.06 | 108.61
2019-12-16 03:30 | 110.44 | 102.73
2019-12-16 04:00 | 106.6 | 98.12
2019-12-16 04:30 | 111.83 | 104.47
2019-12-16 05:00 | 108.27 | 100.06
2019-12-16 05:30 | 111.69 | 104.59
2019-12-16 06:00 | 106.24 | 98.46
2019-12-16 06:30 | 102.7 | 92.13
2019-12-16 07:00 | 103.69 | 91.34
2019-12-16 07:30 | 109.53 | 97.38
2019-12-16 08:00 | 103.14 | 88.23
2019-12-16 08:30 | 100.02 | 84.64
2019-12-16 09:00 | 97.82 | 81.39
2019-12-16 09:30 | 89.73 | 75.1
2019-12-16 10:00 | 100.54 | 85.95
2019-12-16 10:30 | 101.05 | 86.3
2019-12-16 11:00 | 96.16 | 81.27
2019-12-16 11:30 | 93.25 | 77.22
2019-12-16 12:00 | 97.68 | 82.9
2019-12-16 12:30 | 102.76 | 88.27
2019-12-16 13:00 | 96.51 | 82.25
2019-12-16 13:30 | 94.48 | 80.46
2019-12-16 14:00 | 99.11 | 85.95
2019-12-16 14:30 | 98.3 | 85.3
2019-12-16 15:00 | 99.94 | 87.79
2019-12-16 15:30 | 108.81 | 97.49
2019-12-16 16:00 | 103.77 | 92.6
2019-12-16 16:30 | 104.95 | 94.52
2019-12-16 17:00 | 108.78 | 97.96
2019-12-16 17:30 | 108.63 | 100.38
2019-12-16 18:00 | 109.33 | 103.59
2019-12-16 18:30 | 108.08 | 103.38
2019-12-16 19:00 | 118.01 | 113.96
2019-12-16 19:30 | 123.15 | 118.21
2019-12-16 20:00 | 122.01 | 117.12
2019-12-16 20:30 | 123.79 | 119.35
2019-12-16 21:00 | 120.01 | 114.4
2019-12-16 21:30 | 120.35 | 113.94
2019-12-16 22:00 | 114.9 | 108.31
2019-12-16 22:30 | 119.03 | 112.56
2019-12-16 23:00 | 123.24 | 116.37
2019-12-16 23:30 | 121.89 | 114.6
2019-12-17 | 121.6 | 114.17
2019-12-17 00:30 | 119.19 | 111.58
2019-12-17 01:00 | 120.05 | 113.26
2019-12-17 01:30 | 123.46 | 116.9
2019-12-17 02:00 | 124.93 | 119.08
2019-12-17 02:30 | 116.3 | 108.99
2019-12-17 03:00 | 115.04 | 106.83
2019-12-17 03:30 | 107.28 | 97.56
2019-12-17 04:00 | 105.52 | 95.57
2019-12-17 04:30 | 102.48 | 93.21
2019-12-17 05:00 | 107.09 | 97.41
2019-12-17 05:30 | 110.35 | 101.53
2019-12-17 06:00 | 113.98 | 105.73
2019-12-17 06:30 | 101.08 | 88.71
2019-12-17 07:00 | 107.17 | 94.95
2019-12-17 07:30 | 104.21 | 91.18
2019-12-17 08:00 | 99.19 | 82.93
2019-12-17 08:30 | 101.91 | 86.02
2019-12-17 09:00 | 104.01 | 88.42
2019-12-17 09:30 | 105.47 | 89.62
2019-12-17 10:00 | 109.54 | 93.34
2019-12-17 10:30 | 105.24 | 88.71
2019-12-17 11:00 | 107.47 | 91.52
2019-12-17 11:30 | 100.09 | 83.81
2019-12-17 12:00 | 100.6 | 85.42
2019-12-17 12:30 | 106.41 | 91.17
2019-12-17 13:00 | 97.35 | 81.5
2019-12-17 13:30 | 100.87 | 85.42
2019-12-17 14:00 | 101.9 | 87.26
2019-12-17 14:30 | 100.19 | 85.55
2019-12-17 15:00 | 101.5 | 88.53
2019-12-17 15:30 | 105.38 | 91.61
2019-12-17 16:00 | 107.86 | 94.34
2019-12-17 16:30 | 103.67 | 91.23
2019-12-17 17:00 | 110.11 | 99.98
2019-12-17 17:30 | 113.16 | 105.14
2019-12-17 18:00 | 120.5 | 114.14
2019-12-17 18:30 | 115.46 | 110.43
2019-12-17 19:00 | 123.15 | 119.32
2019-12-17 19:30 | 133.26 | 129.26
2019-12-17 20:00 | 131.02 | 127.17
2019-12-17 20:30 | 130.94 | 127.25
2019-12-17 21:00 | 121.22 | 116.49
2019-12-17 21:30 | 123.29 | 118.3
2019-12-17 22:00 | 120.66 | 115.85
2019-12-17 22:30 | 121.17 | 115.74
2019-12-17 23:00 | 116.87 | 111.23
2019-12-17 23:30 | 111.02 | 105.13
2019-12-18 | 113.22 | 106.78
2019-12-18 00:30 | 112.5 | 105.97
2019-12-18 01:00 | 111.29 | 104.24
2019-12-18 01:30 | 109.12 | 101.5
2019-12-18 02:00 | 118.55 | 112.37
2019-12-18 02:30 | 114.96 | 108.09
2019-12-18 03:00 | 111.04 | 103.29
2019-12-18 03:30 | 112.35 | 105.25
2019-12-18 04:00 | 113.17 | 105.42
2019-12-18 04:30 | 110.99 | 103.6
2019-12-18 05:00 | 113.16 | 105.72
2019-12-18 05:30 | 103.92 | 94.12
2019-12-18 06:00 | 105.04 | 96.56
2019-12-18 06:30 | 96.31 | 85.21
2019-12-18 07:00 | 91.26 | 77.51
2019-12-18 07:30 | 95.5 | 81.04
2019-12-18 08:00 | 94.96 | 79.14
2019-12-18 08:30 | 95.63 | 78
2019-12-18 09:00 | 94.61 | 78.07
2019-12-18 09:30 | 90.29 | 73.42
2019-12-18 10:00 | 89 | 72.49
2019-12-18 10:30 | 96.16 | 80.92
2019-12-18 11:00 | 92.77 | 78
2019-12-18 11:30 | 94.65 | 79.45
2019-12-18 12:00 | 93.9 | 78.71
2019-12-18 12:30 | 95.13 | 80.47
2019-12-18 13:00 | 97.2 | 82.81
2019-12-18 13:30 | 91.65 | 75.88
2019-12-18 14:00 | 92.72 | 77.75
2019-12-18 14:30 | 96.35 | 81.89
2019-12-18 15:00 | 97.11 | 83.85
2019-12-18 15:30 | 98.59 | 85.78
2019-12-18 16:00 | 101.46 | 88.26
2019-12-18 16:30 | 104.47 | 92.13
2019-12-18 17:00 | 97.13 | 84.32
2019-12-18 17:30 | 103.67 | 92.2
2019-12-18 18:00 | 116.95 | 110.24
2019-12-18 18:30 | 111.62 | 105.74
2019-12-18 19:00 | 115.88 | 112.17
2019-12-18 19:30 | 115.15 | 111.24
2019-12-18 20:00 | 117.04 | 113.13
2019-12-18 20:30 | 123.28 | 119.06
2019-12-18 21:00 | 119.19 | 112.34
2019-12-18 21:30 | 114.27 | 103.51
2019-12-18 22:00 | 113.66 | 102.61
2019-12-18 22:30 | 103.83 | 94.12
2019-12-18 23:00 | 112.18 | 101.67
2019-12-18 23:30 | 113.95 | 101.74
2019-12-19 | 121.3 | 110.2
2019-12-19 00:30 | 119.6 | 107.89
2019-12-19 01:00 | 121.98 | 110.54
2019-12-19 01:30 | 116.39 | 104.29
2019-12-19 02:00 | 113.16 | 101.21
2019-12-19 02:30 | 111.3 | 99.81
2019-12-19 03:00 | 114.79 | 103.14
2019-12-19 03:30 | 110.96 | 98.95
2019-12-19 04:00 | 112.23 | 100.1
2019-12-19 04:30 | 119.98 | 109.74
2019-12-19 05:00 | 118.01 | 107.17
2019-12-19 05:30 | 109.89 | 96.51
2019-12-19 06:00 | 107.94 | 93.94
2019-12-19 06:30 | 93.76 | 74.7
2019-12-19 07:00 | 100.59 | 81.11
2019-12-19 07:30 | 101.49 | 80.26
2019-12-19 08:00 | 96.25 | 72.09
2019-12-19 08:30 | 99.92 | 76.49
2019-12-19 09:00 | 100.38 | 73.45
2019-12-19 09:30 | 100.9 | 75.46
2019-12-19 10:00 | 100.66 | 75.55
2019-12-19 10:30 | 95.92 | 69.86
2019-12-19 11:00 | 99.87 | 75.56
2019-12-19 11:30 | 94.01 | 69.26
2019-12-19 12:00 | 94.82 | 69.45
2019-12-19 12:30 | 97.84 | 71.68
2019-12-19 13:00 | 95.57 | 69.44
2019-12-19 13:30 | 93.37 | 67.09
2019-12-19 14:00 | 98.55 | 73.06
2019-12-19 14:30 | 98.76 | 74.36
2019-12-19 15:00 | 104.92 | 82.96
2019-12-19 15:30 | 94.49 | 75.54
2019-12-19 16:00 | 95.2 | 78.27
2019-12-19 16:30 | 101.54 | 84.54
2019-12-19 17:00 | 103 | 88.47
2019-12-19 17:30 | 103.95 | 92.9
2019-12-19 18:00 | 106.93 | 99.2
2019-12-19 18:30 | 101.85 | 94.6
2019-12-19 19:00 | 113.51 | 108.76
2019-12-19 19:30 | 120.53 | 115.65
2019-12-19 20:00 | 109.77 | 104.72
2019-12-19 20:30 | 124.56 | 118.73
2019-12-19 21:00 | 124.57 | 119.35
2019-12-19 21:30 | 121.63 | 116.18
2019-12-19 22:00 | 118.99 | 113.24
2019-12-19 22:30 | 113.08 | 107.43
2019-12-19 23:00 | 118.68 | 113.14
2019-12-19 23:30 | 100.46 | 95.15
2019-12-20 | 106.48 | 101.1
2019-12-20 00:30 | 103.99 | 98
2019-12-20 01:00 | 104.75 | 98.96
2019-12-20 01:30 | 102.75 | 97.32
2019-12-20 02:00 | 101.18 | 95.52
2019-12-20 02:30 | 102.32 | 96.74
2019-12-20 03:00 | 98.76 | 93.11
2019-12-20 03:30 | 100.27 | 93.87
2019-12-20 04:00 | 95.73 | 89.47
2019-12-20 04:30 | 101.55 | 96.62
2019-12-20 05:00 | 97.49 | 92.1
2019-12-20 05:30 | 94.01 | 88.21
2019-12-20 06:00 | 98.48 | 93.07
2019-12-20 06:30 | 94.99 | 87.8
2019-12-20 07:00 | 94.56 | 85.83
2019-12-20 07:30 | 91.59 | 80.36
2019-12-20 08:00 | 94.67 | 81.18
2019-12-20 08:30 | 93.51 | 78.11
2019-12-20 09:00 | 87.57 | 71.09
2019-12-20 09:30 | 90.25 | 73.11
2019-12-20 10:00 | 89.1 | 72.14
2019-12-20 10:30 | 91.18 | 73.66
2019-12-20 11:00 | 92.14 | 74.66
2019-12-20 11:30 | 90.71 | 72.45
2019-12-20 12:00 | 90.58 | 73.2
2019-12-20 12:30 | 86.66 | 70.05
2019-12-20 13:00 | 97.38 | 82.32
2019-12-20 13:30 | 97.29 | 80.99
2019-12-20 14:00 | 95.6 | 79.8
2019-12-20 14:30 | 88.59 | 72.72
2019-12-20 15:00 | 92.65 | 77.17
2019-12-20 15:30 | 94.13 | 78.16
2019-12-20 16:00 | 99.12 | 84.7
2019-12-20 16:30 | 96.74 | 84.22
2019-12-20 17:00 | 100.3 | 88.59
2019-12-20 17:30 | 101.02 | 92.02
2019-12-20 18:00 | 99.76 | 93.63
2019-12-20 18:30 | 98.39 | 93.49
2019-12-20 19:00 | 116.11 | 111.76
2019-12-20 19:30 | 118.34 | 114.05
2019-12-20 20:00 | 120.32 | 116.19
2019-12-20 20:30 | 110.3 | 106.39
2019-12-20 21:00 | 104.75 | 100.14
2019-12-20 21:30 | 112.52 | 107.72
2019-12-20 22:00 | 119.25 | 114.43
2019-12-20 22:30 | 109.89 | 104.54
2019-12-20 23:00 | 111.91 | 106.44
2019-12-20 23:30 | 109.61 | 104.25
2019-12-21 | 105.52 | 100.51
2019-12-21 00:30 | 103.42 | 98.62
2019-12-21 01:00 | 105.88 | 100.69
2019-12-21 01:30 | 113.63 | 108.27
2019-12-21 02:00 | 103.78 | 98.29
2019-12-21 02:30 | 105.69 | 100.12
2019-12-21 03:00 | 102.55 | 97.15
2019-12-21 03:30 | 101.95 | 96.18
2019-12-21 04:00 | 106.49 | 101.5
2019-12-21 04:30 | 107.69 | 102.92
2019-12-21 05:00 | 100.04 | 94.26
2019-12-21 05:30 | 107.75 | 102.71
2019-12-21 06:00 | 109.97 | 104.52
2019-12-21 06:30 | 92.94 | 84.92
2019-12-21 07:00 | 93.66 | 83.9
2019-12-21 07:30 | 90.41 | 79.46
2019-12-21 08:00 | 90 | 76.57
2019-12-21 08:30 | 95.13 | 81.25
2019-12-21 09:00 | 89.38 | 74.03
2019-12-21 09:30 | 89.12 | 72.98
2019-12-21 10:00 | 80.37 | 64.79
2019-12-21 10:30 | 81.83 | 65.55
2019-12-21 11:00 | 94.51 | 78.91
2019-12-21 11:30 | 93.66 | 77.09
2019-12-21 12:00 | 92.49 | 77.29
2019-12-21 12:30 | 95.88 | 80.25
2019-12-21 13:00 | 98.61 | 81.24
2019-12-21 13:30 | 106.8 | 90.05
2019-12-21 14:00 | 100.72 | 84.2
2019-12-21 14:30 | 110.18 | 93.96
2019-12-21 15:00 | 100.25 | 83.36
2019-12-21 15:30 | 100.44 | 86.14
2019-12-21 16:00 | 104.92 | 91.47
2019-12-21 16:30 | 100.43 | 88.22
2019-12-21 17:00 | 96.37 | 84.88
2019-12-21 17:30 | 104.46 | 95.56
2019-12-21 18:00 | 115.82 | 109.19
2019-12-21 18:30 | 108.77 | 102.59
2019-12-21 19:00 | 111.22 | 105.87
2019-12-21 19:30 | 112.59 | 106.91
2019-12-21 20:00 | 111.07 | 106.44
2019-12-21 20:30 | 113.48 | 107.6
2019-12-21 21:00 | 105.82 | 100.41
2019-12-21 21:30 | 110.29 | 104.73
2019-12-21 22:00 | 112 | 105.95
2019-12-21 22:30 | 118.57 | 112.79
2019-12-21 23:00 | 114.52 | 108.88
2019-12-21 23:30 | 109.47 | 103.93
2019-12-22 | 112.99 | 107.3
2019-12-22 00:30 | 110.92 | 105.31
2019-12-22 01:00 | 120.06 | 114.45
2019-12-22 01:30 | 114.4 | 108.78
2019-12-22 02:00 | 111.89 | 106.17
2019-12-22 02:30 | 111.79 | 105.86
2019-12-22 03:00 | 110.59 | 104.74
2019-12-22 03:30 | 101.07 | 95.06
2019-12-22 04:00 | 108.18 | 102.5
2019-12-22 04:30 | 105.67 | 100.42
2019-12-22 05:00 | 102.58 | 96.33
2019-12-22 05:30 | 100.8 | 94.87
2019-12-22 06:00 | 99.55 | 93.17
2019-12-22 06:30 | 93.36 | 84.97
2019-12-22 07:00 | 102.78 | 93.57
2019-12-22 07:30 | 108.24 | 97.29
2019-12-22 08:00 | 107.32 | 94.54
2019-12-22 08:30 | 87.24 | 75.71
2019-12-22 09:00 | 84.57 | 72.27
2019-12-22 09:30 | 86.09 | 73.54
2019-12-22 10:00 | 97.51 | 83.12
2019-12-22 10:30 | 96.24 | 81.52
2019-12-22 11:00 | 90.68 | 74.35
2019-12-22 11:30 | 89.86 | 74.16
2019-12-22 12:00 | 92.13 | 78.85
2019-12-22 12:30 | 91.68 | 80.35
2019-12-22 13:00 | 99.9 | 86.4
2019-12-22 13:30 | 104.35 | 90.01
2019-12-22 14:00 | 102.15 | 87.57
2019-12-22 14:30 | 100.54 | 87.8
2019-12-22 15:00 | 108.5 | 96.2
2019-12-22 15:30 | 103.61 | 92.57
2019-12-22 16:00 | 105.45 | 94.41
2019-12-22 16:30 | 98.93 | 89.2
2019-12-22 17:00 | 106.42 | 96.99
2019-12-22 17:30 | 110.38 | 102.12
2019-12-22 18:00 | 114.94 | 108.67
2019-12-22 18:30 | 118.16 | 113.01
2019-12-22 19:00 | 108.67 | 104.1
2019-12-22 19:30 | 114.6 | 110.09
2019-12-22 20:00 | 109.43 | 105.34
2019-12-22 20:30 | 120.88 | 115.89
2019-12-22 21:00 | 114.03 | 108.8
2019-12-22 21:30 | 120.56 | 115.49
2019-12-22 22:00 | 118.03 | 113.52
2019-12-22 22:30 | 118.32 | 113.85
2019-12-22 23:00 | 115.34 | 111.14
2019-12-22 23:30 | 113.84 | 108.82
2019-12-23 | 113.99 | 108.68
2019-12-23 00:30 | 117.76 | 112.59
2019-12-23 01:00 | 118.53 | 113.02
2019-12-23 01:30 | 125.51 | 120.22
2019-12-23 02:00 | 121.68 | 116.8
2019-12-23 02:30 | 116.12 | 111.32
2019-12-23 03:00 | 120.03 | 114.99
2019-12-23 03:30 | 108.56 | 103.36
2019-12-23 04:00 | 105.54 | 100.61
2019-12-23 04:30 | 109.27 | 104.47
2019-12-23 05:00 | 107.86 | 102.34
2019-12-23 05:30 | 100.96 | 95.1
2019-12-23 06:00 | 103.87 | 98.95
2019-12-23 06:30 | 87.57 | 80.6
2019-12-23 07:00 | 93.38 | 86.32
2019-12-23 07:30 | 97.81 | 89.44
2019-12-23 08:00 | 91.45 | 81.42
2019-12-23 08:30 | 90.72 | 80.35
2019-12-23 09:00 | 92.93 | 80.76
2019-12-23 09:30 | 91.67 | 78.49
2019-12-23 10:00 | 94.42 | 82.59
2019-12-23 10:30 | 88.93 | 77.28
2019-12-23 11:00 | 89.61 | 76.51
2019-12-23 11:30 | 88.63 | 76.06
2019-12-23 12:00 | 93.5 | 79.91
2019-12-23 12:30 | 92.22 | 77.47
2019-12-23 13:00 | 94.33 | 79.75
2019-12-23 13:30 | 94.47 | 79.82
2019-12-23 14:00 | 95.73 | 82.58
2019-12-23 14:30 | 92.26 | 79.9
2019-12-23 15:00 | 92.4 | 80.62
2019-12-23 15:30 | 96.79 | 85.54
2019-12-23 16:00 | 93.96 | 83.05
2019-12-23 16:30 | 104.93 | 96.04
2019-12-23 17:00 | 103.98 | 96.4
2019-12-23 17:30 | 117.09 | 111.16
2019-12-23 18:00 | 120.25 | 114.88
2019-12-23 18:30 | 110.21 | 104.48
2019-12-23 19:00 | 125.92 | 121.47
2019-12-23 19:30 | 129.52 | 124.82
2019-12-23 20:00 | 124.54 | 118.93
2019-12-23 20:30 | 118.72 | 112.99
2019-12-23 21:00 | 115.36 | 109.83
2019-12-23 21:30 | 114.74 | 109.36
2019-12-23 22:00 | 112.57 | 107.78
2019-12-23 22:30 | 119.05 | 114.05
2019-12-23 23:00 | 112.23 | 108
2019-12-23 23:30 | 105.47 | 100.32
2019-12-24 | 104.89 | 99.45
2019-12-24 00:30 | 101.04 | 95.61
2019-12-24 01:00 | 104.98 | 99.85
2019-12-24 01:30 | 103.14 | 97.94
2019-12-24 02:00 | 111.58 | 107.14
2019-12-24 02:30 | 109.66 | 105.11
2019-12-24 03:00 | 111.28 | 106.18
2019-12-24 03:30 | 110.74 | 105.82
2019-12-24 04:00 | 97.55 | 91.59
2019-12-24 04:30 | 111.77 | 106.99
2019-12-24 05:00 | 107.38 | 102.45
2019-12-24 05:30 | 100.49 | 95.23
2019-12-24 06:00 | 100.99 | 95.83
2019-12-24 06:30 | 93.99 | 86.54
2019-12-24 07:00 | 94.88 | 86.79
2019-12-24 07:30 | 96.59 | 86.77
2019-12-24 08:00 | 92.86 | 80.95
2019-12-24 08:30 | 97.89 | 83.86
2019-12-24 09:00 | 92.35 | 77.39
2019-12-24 09:30 | 98.39 | 84.44
2019-12-24 10:00 | 95.61 | 81.88
2019-12-24 10:30 | 85.19 | 69.79
2019-12-24 11:00 | 89.41 | 74.52
2019-12-24 11:30 | 83.87 | 69.72
2019-12-24 12:00 | 85.47 | 72.62
2019-12-24 12:30 | 85 | 73.12
2019-12-24 13:00 | 86.58 | 74.31
2019-12-24 13:30 | 82.42 | 70.14
2019-12-24 14:00 | 87.15 | 75.26
2019-12-24 14:30 | 78.56 | 65.1
2019-12-24 15:00 | 73.83 | 59.61
2019-12-24 15:30 | 74.7 | 58.93
2019-12-24 16:00 | 78.14 | 62.88
2019-12-24 16:30 | 71.24 | 58.23
2019-12-24 17:00 | 66.94 | 55.53
2019-12-24 17:30 | 62.08 | 50.37
2019-12-24 18:00 | 61.55 | 51.07
2019-12-24 18:30 | 67.64 | 60.08
2019-12-24 19:00 | 73.55 | 66.12
2019-12-24 19:30 | 64.97 | 55.65
2019-12-24 20:00 | 66 | 57.25
2019-12-24 20:30 | 64.08 | 55.53
2019-12-24 21:00 | 62.67 | 53.91
2019-12-24 21:30 | 59.49 | 49.42
2019-12-24 22:00 | 59.37 | 48.46
2019-12-24 22:30 | 60.33 | 49.82
2019-12-24 23:00 | 55.28 | 42.09
2019-12-24 23:30 | 57.02 | 44.54
2019-12-25 | 57.16 | 44.93
2019-12-25 00:30 | 59 | 46.27
2019-12-25 01:00 | 54.43 | 39.19
2019-12-25 01:30 | 56.73 | 42.24
2019-12-25 02:00 | 58.23 | 44.66
2019-12-25 02:30 | 60.42 | 48.35
2019-12-25 03:00 | 56.89 | 44.98
2019-12-25 03:30 | 52.65 | 38.43
2019-12-25 04:00 | 55.46 | 41.72
2019-12-25 04:30 | 55.43 | 41.46
2019-12-25 05:00 | 54.42 | 39.84
2019-12-25 05:30 | 54.88 | 40.09
2019-12-25 06:00 | 52.47 | 40.19
2019-12-25 06:30 | 51.99 | 38.34
2019-12-25 07:00 | 56.63 | 45.13
2019-12-25 07:30 | 51.91 | 32.75
2019-12-25 08:00 | 50.34 | 28.66
2019-12-25 08:30 | 51.06 | 28.31
2019-12-25 09:00 | 53.28 | 31.95
2019-12-25 09:30 | 52.7 | 31.87
2019-12-25 10:00 | 56.48 | 37.66
2019-12-25 10:30 | 52.77 | 32.05
2019-12-25 11:00 | 57.27 | 36.88
2019-12-25 11:30 | 56.36 | 36.23
2019-12-25 12:00 | 58.21 | 41.06
2019-12-25 12:30 | 57.58 | 41.12
2019-12-25 13:00 | 55.36 | 35.57
2019-12-25 13:30 | 56.41 | 37.09
2019-12-25 14:00 | 55.24 | 36.14
2019-12-25 14:30 | 55.42 | 35.02
2019-12-25 15:00 | 55.14 | 34.41
2019-12-25 15:30 | 65.61 | 55.76
2019-12-25 16:00 | 60.53 | 50.26
2019-12-25 16:30 | 62.35 | 52.87
2019-12-25 17:00 | 57.36 | 45.51
2019-12-25 17:30 | 52.29 | 36.32
2019-12-25 18:00 | 56.27 | 45.26
2019-12-25 18:30 | 58.93 | 50.4
2019-12-25 19:00 | 59.45 | 47.81
2019-12-25 19:30 | 58.82 | 48.72
2019-12-25 20:00 | 60.18 | 49.7
2019-12-25 20:30 | 59.85 | 50.39
2019-12-25 21:00 | 59.97 | 49.81
2019-12-25 21:30 | 56.78 | 45.47
2019-12-25 22:00 | 58.03 | 46.89
2019-12-25 22:30 | 57.88 | 45.93
2019-12-25 23:00 | 54.74 | 41.43
2019-12-25 23:30 | 54.13 | 40.39
2019-12-26 | 53.12 | 38.76
2019-12-26 00:30 | 53.65 | 39.49
2019-12-26 01:00 | 53.3 | 38.94
2019-12-26 01:30 | 54.54 | 40.9
2019-12-26 02:00 | 52.73 | 38.53
2019-12-26 02:30 | 49.48 | 33.24
2019-12-26 03:00 | 50.33 | 33.37
2019-12-26 03:30 | 49.11 | 31.64
2019-12-26 04:00 | 51.18 | 34.35
2019-12-26 04:30 | 49.22 | 32.23
2019-12-26 05:00 | 48.18 | 30.42
2019-12-26 05:30 | 54.33 | 41.13
2019-12-26 06:00 | 52.52 | 37.97
2019-12-26 06:30 | 51.25 | 33.94
2019-12-26 07:00 | 49.54 | 29.84
2019-12-26 07:30 | 50.91 | 32.56
2019-12-26 08:00 | 48.48 | 25.59
2019-12-26 08:30 | 48.05 | 17.68
2019-12-26 09:00 | 48.92 | 25.3
2019-12-26 09:30 | 46.96 | 14.52
2019-12-26 10:00 | 49.29 | 17.23
2019-12-26 10:30 | 49.42 | 17.24
2019-12-26 11:00 | 47.64 | 18.42
2019-12-26 11:30 | 49.26 | 22.1
2019-12-26 12:00 | 50.25 | 22.35
2019-12-26 12:30 | 49.99 | 28.45
2019-12-26 13:00 | 50.06 | 30.17
2019-12-26 13:30 | 49.78 | 26.21
2019-12-26 14:00 | 52.35 | 33.1
2019-12-26 14:30 | 52.27 | 33.27
2019-12-26 15:00 | 52.63 | 35.15
2019-12-26 15:30 | 50.67 | 29.9
2019-12-26 16:00 | 52.75 | 32.22
2019-12-26 16:30 | 57.18 | 44.97
2019-12-26 17:00 | 60.32 | 47.58
2019-12-26 17:30 | 66.18 | 56.63
2019-12-26 18:00 | 60.41 | 46.95
2019-12-26 18:30 | 64.68 | 54.47
2019-12-26 19:00 | 75.02 | 65.91
2019-12-26 19:30 | 82.26 | 73.83
2019-12-26 20:00 | 84.05 | 74.96
2019-12-26 20:30 | 86.47 | 78.93
2019-12-26 21:00 | 88.21 | 81.12
2019-12-26 21:30 | 91.99 | 84.21
2019-12-26 22:00 | 93.02 | 85.19
2019-12-26 22:30 | 90.29 | 81.55
2019-12-26 23:00 | 97.11 | 89.11
2019-12-26 23:30 | 97.05 | 88.79
2019-12-27 | 97.51 | 88.98
2019-12-27 00:30 | 101.6 | 94.03
2019-12-27 01:00 | 97.13 | 88.85
2019-12-27 01:30 | 97.07 | 89.17
2019-12-27 02:00 | 96.55 | 88.18
2019-12-27 02:30 | 96.76 | 88.58
2019-12-27 03:00 | 94.01 | 85.51
2019-12-27 03:30 | 97.96 | 90.49
2019-12-27 04:00 | 96.77 | 88.87
2019-12-27 04:30 | 94.56 | 86.86
2019-12-27 05:00 | 93.1 | 83.75
2019-12-27 05:30 | 91.52 | 81.48
2019-12-27 06:00 | 88.2 | 79.67
2019-12-27 06:30 | 79.44 | 67.54
2019-12-27 07:00 | 80.65 | 68.2
2019-12-27 07:30 | 77.66 | 62.08
2019-12-27 08:00 | 81.63 | 68.9
2019-12-27 08:30 | 81.47 | 66.8
2019-12-27 09:00 | 89.55 | 75.28
2019-12-27 09:30 | 92.47 | 77.78
2019-12-27 10:00 | 91.03 | 74.94
2019-12-27 10:30 | 90.6 | 75.38
2019-12-27 11:00 | 89.4 | 71.55
2019-12-27 11:30 | 85.32 | 69.31
2019-12-27 12:00 | 85.77 | 71.52
2019-12-27 12:30 | 83.61 | 65.83
2019-12-27 13:00 | 90.47 | 74.56
2019-12-27 13:30 | 90.83 | 74
2019-12-27 14:00 | 83.82 | 67.59
2019-12-27 14:30 | 94.32 | 79.02
2019-12-27 15:00 | 98.49 | 83.9
2019-12-27 15:30 | 96.05 | 82.59
2019-12-27 16:00 | 94.83 | 81.79
2019-12-27 16:30 | 102.33 | 90.05
2019-12-27 17:00 | 100.54 | 86.41
2019-12-27 17:30 | 98.21 | 84.39
2019-12-27 18:00 | 102.93 | 94.44
2019-12-27 18:30 | 100.34 | 93.67
2019-12-27 19:00 | 114.33 | 109.54
2019-12-27 19:30 | 119.87 | 115.02
2019-12-27 20:00 | 115.03 | 110.08
2019-12-27 20:30 | 113.79 | 109.24
2019-12-27 21:00 | 111.37 | 106.97
2019-12-27 21:30 | 116.53 | 111.81
2019-12-27 22:00 | 106.85 | 101.84
2019-12-27 22:30 | 106.43 | 101.01
2019-12-27 23:00 | 113.33 | 107.84
2019-12-27 23:30 | 121.18 | 116.06
2019-12-28 | 113.47 | 108.25
2019-12-28 00:30 | 112.07 | 107.6
2019-12-28 01:00 | 112.65 | 108.01
2019-12-28 01:30 | 116.03 | 110.93
2019-12-28 02:00 | 113.5 | 108.73
2019-12-28 02:30 | 114.26 | 108.88
2019-12-28 03:00 | 112.18 | 106.67
2019-12-28 03:30 | 108.12 | 102.54
2019-12-28 04:00 | 99.03 | 93.89
2019-12-28 04:30 | 100.1 | 94.93
2019-12-28 05:00 | 96.42 | 91.18
2019-12-28 05:30 | 105.64 | 100.78
2019-12-28 06:00 | 112.41 | 107.35
2019-12-28 06:30 | 98.36 | 89.88
2019-12-28 07:00 | 107.89 | 100.02
2019-12-28 07:30 | 107.52 | 97.94
2019-12-28 08:00 | 103.84 | 94.48
2019-12-28 08:30 | 102.47 | 91.79
2019-12-28 09:00 | 101.83 | 88.47
2019-12-28 09:30 | 91.62 | 76.87
2019-12-28 10:00 | 84.04 | 69.59
2019-12-28 10:30 | 86.07 | 71.02
2019-12-28 11:00 | 98.17 | 82.01
2019-12-28 11:30 | 105.04 | 90.96
2019-12-28 12:00 | 106.61 | 91.57
2019-12-28 12:30 | 110.99 | 97.19
2019-12-28 13:00 | 106.63 | 89.68
2019-12-28 13:30 | 109.78 | 93.96
2019-12-28 14:00 | 100.87 | 88.44
2019-12-28 14:30 | 99.97 | 88.92
2019-12-28 15:00 | 105.47 | 97.11
2019-12-28 15:30 | 109.14 | 101.15
2019-12-28 16:00 | 105.08 | 96.8
2019-12-28 16:30 | 106.3 | 97.9
2019-12-28 17:00 | 108.13 | 100.59
2019-12-28 17:30 | 113.64 | 106.64
2019-12-28 18:00 | 119.55 | 113.29
2019-12-28 18:30 | 109.68 | 103.06
2019-12-28 19:00 | 119.3 | 114.13
2019-12-28 19:30 | 124.72 | 118.91
2019-12-28 20:00 | 120.44 | 115.38
2019-12-28 20:30 | 120.7 | 115.69
2019-12-28 21:00 | 114.11 | 108.44
2019-12-28 21:30 | 117.72 | 111.82
2019-12-28 22:00 | 109.83 | 103.7
2019-12-28 22:30 | 113.74 | 108.03
2019-12-28 23:00 | 118.84 | 113.2
2019-12-28 23:30 | 121.46 | 115.09
2019-12-29 | 115.79 | 109.81
2019-12-29 00:30 | 112.51 | 106.1
2019-12-29 01:00 | 106.95 | 101.22
2019-12-29 01:30 | 108.13 | 102.01
2019-12-29 02:00 | 110.35 | 104.76
2019-12-29 02:30 | 107.38 | 101.71
2019-12-29 03:00 | 110.15 | 104.65
2019-12-29 03:30 | 105.54 | 99.21
2019-12-29 04:00 | 118.24 | 112.05
2019-12-29 04:30 | 114.01 | 107.84
2019-12-29 05:00 | 116.75 | 110.86
2019-12-29 05:30 | 110.12 | 103.73
2019-12-29 06:00 | 110.9 | 105.8
2019-12-29 06:30 | 95.8 | 88.77
2019-12-29 07:00 | 106.56 | 100.51
2019-12-29 07:30 | 97.83 | 91.21
2019-12-29 08:00 | 99.21 | 93.02
2019-12-29 08:30 | 101.42 | 96.21
2019-12-29 09:00 | 95.35 | 89.52
2019-12-29 09:30 | 97.87 | 89.13
2019-12-29 10:00 | 104.98 | 94.74
2019-12-29 10:30 | 101.26 | 87.51
2019-12-29 11:00 | 103.83 | 94.05
2019-12-29 11:30 | 104.56 | 90.72
2019-12-29 12:00 | 99.87 | 87.74
2019-12-29 12:30 | 111.7 | 98.14
2019-12-29 13:00 | 102.86 | 92.16
2019-12-29 13:30 | 114.09 | 104.02
2019-12-29 14:00 | 117.42 | 107.59
2019-12-29 14:30 | 108.52 | 94.03
2019-12-29 15:00 | 113.4 | 98.84
2019-12-29 15:30 | 96.52 | 80.98
2019-12-29 16:00 | 95.36 | 79.43
2019-12-29 16:30 | 103.96 | 88.98
2019-12-29 17:00 | 111.12 | 99.19
2019-12-29 17:30 | 114.26 | 104.49
2019-12-29 18:00 | 109.36 | 101.46
2019-12-29 18:30 | 102.32 | 95.47
2019-12-29 19:00 | 118.61 | 114.03
2019-12-29 19:30 | 116.46 | 111.41
2019-12-29 20:00 | 109.41 | 103.52
2019-12-29 20:30 | 111.23 | 105.4
2019-12-29 21:00 | 114.98 | 109.19
2019-12-29 21:30 | 112.76 | 107.09
2019-12-29 22:00 | 112.57 | 106.55
2019-12-29 22:30 | 109.42 | 103.23
2019-12-29 23:00 | 106.9 | 100.97
2019-12-29 23:30 | 108.71 | 102.46
2019-12-30 | 109.96 | 104.53
2019-12-30 00:30 | 107.51 | 101.99
2019-12-30 01:00 | 118.78 | 113.2
2019-12-30 01:30 | 116.16 | 110.66
2019-12-30 02:00 | 112.39 | 106.04
2019-12-30 02:30 | 115.14 | 109.2
2019-12-30 03:00 | 110.43 | 103.67
2019-12-30 03:30 | 110.31 | 103.89
2019-12-30 04:00 | 110.74 | 104.23
2019-12-30 04:30 | 102.99 | 96.47
2019-12-30 05:00 | 103.13 | 97.07
2019-12-30 05:30 | 104.6 | 97.97
2019-12-30 06:00 | 97.1 | 90.84
2019-12-30 06:30 | 90.97 | 81.93
2019-12-30 07:00 | 95.58 | 85.34
2019-12-30 07:30 | 92.45 | 79.2
2019-12-30 08:00 | 95.83 | 81.32
2019-12-30 08:30 | 93.57 | 77.8
2019-12-30 09:00 | 85.84 | 69.58
2019-12-30 09:30 | 90.31 | 73.71
2019-12-30 10:00 | 92.43 | 76.34
2019-12-30 10:30 | 91.25 | 76.28
2019-12-30 11:00 | 95.68 | 79.71
2019-12-30 11:30 | 87.32 | 71.93
2019-12-30 12:00 | 99.21 | 85.16
2019-12-30 12:30 | 100.53 | 87.04
2019-12-30 13:00 | 90.67 | 76.83
2019-12-30 13:30 | 99.18 | 84.15
2019-12-30 14:00 | 100.61 | 87.86
2019-12-30 14:30 | 100.97 | 87.53
2019-12-30 15:00 | 97.95 | 85.82
2019-12-30 15:30 | 93.71 | 82.03
2019-12-30 16:00 | 96.67 | 86.61
2019-12-30 16:30 | 99.13 | 86.89
2019-12-30 17:00 | 96.64 | 85.55
2019-12-30 17:30 | 95.74 | 85.7
2019-12-30 18:00 | 101.41 | 94.29
2019-12-30 18:30 | 91.8 | 85.19
2019-12-30 19:00 | 112.28 | 107.39
2019-12-30 19:30 | 113.37 | 108.83
2019-12-30 20:00 | 116.26 | 112.19
2019-12-30 20:30 | 113.27 | 108.36
2019-12-30 21:00 | 112.92 | 108.31
2019-12-30 21:30 | 113.49 | 107.67
2019-12-30 22:00 | 113.69 | 107.78
2019-12-30 22:30 | 111.75 | 105.32
2019-12-30 23:00 | 112.67 | 106.05
2019-12-30 23:30 | 106.36 | 99.26
2019-12-31 | 104.42 | 97.49
2019-12-31 00:30 | 107.89 | 102.12
2019-12-31 01:00 | 107.27 | 100.87
2019-12-31 01:30 | 112.93 | 107.24
2019-12-31 02:00 | 115.16 | 109.52
2019-12-31 02:30 | 110.03 | 103.45
2019-12-31 03:00 | 107.13 | 100.61
2019-12-31 03:30 | 104.33 | 97.2
2019-12-31 04:00 | 107.49 | 100.66
2019-12-31 04:30 | 110.27 | 103.61
2019-12-31 05:00 | 107.92 | 100.19
2019-12-31 05:30 | 111.28 | 104.82
2019-12-31 06:00 | 103.42 | 98.08
2019-12-31 06:30 | 89.2 | 80.56
2019-12-31 07:00 | 95.88 | 84.83
2019-12-31 07:30 | 86.77 | 72.54
2019-12-31 08:00 | 85.92 | 70
2019-12-31 08:30 | 94.8 | 80.35
2019-12-31 09:00 | 92.58 | 77.78
2019-12-31 09:30 | 91.09 | 74.62
2019-12-31 10:00 | 92.7 | 75.98
2019-12-31 10:30 | 96.58 | 79.47
2019-12-31 11:00 | 102.26 | 85.84
2019-12-31 11:30 | 94.67 | 78.69
2019-12-31 12:00 | 100.49 | 86.3
2019-12-31 12:30 | 97.23 | 82.34
2019-12-31 13:00 | 102.61 | 87.37
2019-12-31 13:30 | 104.85 | 89.98
2019-12-31 14:00 | 104.58 | 92.79
2019-12-31 14:30 | 103.44 | 90.19
2019-12-31 15:00 | 100.89 | 86.74
2019-12-31 15:30 | 108.68 | 95.1
2019-12-31 16:00 | 103.05 | 89.12
2019-12-31 16:30 | 111.88 | 100.69
2019-12-31 17:00 | 116.4 | 105.4
2019-12-31 17:30 | 113.86 | 105.2
2019-12-31 18:00 | 115.86 | 109.91
2019-12-31 18:30 | 113.1 | 107.44
2019-12-31 19:00 | 112.71 | 107.88
2019-12-31 19:30 | 118.4 | 113.94
2019-12-31 20:00 | 118.54 | 113.59
2019-12-31 20:30 | 122.1 | 117.22
2019-12-31 21:00 | 114.48 | 109.95
2019-12-31 21:30 | 114.31 | 109.15
2019-12-31 22:00 | 113.44 | 108.38
2019-12-31 22:30 | 112.86 | 108
2019-12-31 23:00 | 109.64 | 103.99
2019-12-31 23:30 | 110.17 | 104.39
2020-01-01 | 109.2 | 103.01
2020-01-01 00:30 | 108.06 | 101.74
2020-01-01 01:00 | 109.01 | 103.37
2020-01-01 01:30 | 112.88 | 106.78
2020-01-01 02:00 | 111.15 | 105.53
2020-01-01 02:30 | 112.63 | 106.88
2020-01-01 03:00 | 115.33 | 109.74
2020-01-01 03:30 | 111.25 | 104.96
2020-01-01 04:00 | 118.53 | 111.75
2020-01-01 04:30 | 118.28 | 111.98
2020-01-01 05:00 | 112.87 | 106.52
2020-01-01 05:30 | 106.89 | 99.51
2020-01-01 06:00 | 107 | 100.73
2020-01-01 06:30 | 94.82 | 84.7
2020-01-01 07:00 | 95.4 | 84.76
2020-01-01 07:30 | 93.61 | 81.27
2020-01-01 08:00 | 90.5 | 78.01
2020-01-01 08:30 | 84.67 | 72.24
2020-01-01 09:00 | 82.55 | 70.52
2020-01-01 09:30 | 80.73 | 69.47
2020-01-01 10:00 | 79.87 | 69.62
2020-01-01 10:30 | 78.73 | 67.69
2020-01-01 11:00 | 78.96 | 67.05
2020-01-01 11:30 | 79.48 | 66.5
2020-01-01 12:00 | 78.8 | 66.62
2020-01-01 12:30 | 76.76 | 63.84
2020-01-01 13:00 | 79.12 | 68.75
2020-01-01 13:30 | 82.43 | 72.96
2020-01-01 14:00 | 84.2 | 75
2020-01-01 14:30 | 95.07 | 86.1
2020-01-01 15:00 | 96.95 | 86.4
2020-01-01 15:30 | 93.05 | 81.58
2020-01-01 16:00 | 91.29 | 79.69
2020-01-01 16:30 | 93.88 | 84.13
2020-01-01 17:00 | 93.34 | 83.81
2020-01-01 17:30 | 93.12 | 84.52
2020-01-01 18:00 | 119.05 | 113.11
2020-01-01 18:30 | 114.42 | 108.85
2020-01-01 19:00 | 124.86 | 120.45
2020-01-01 19:30 | 121.38 | 117.26
2020-01-01 20:00 | 118.08 | 114.08
2020-01-01 20:30 | 117.79 | 113.37
2020-01-01 21:00 | 115.96 | 111.54
2020-01-01 21:30 | 122.39 | 118.28
2020-01-01 22:00 | 124.45 | 119.63
2020-01-01 22:30 | 123.44 | 118.36
2020-01-01 23:00 | 121.12 | 115.6
2020-01-01 23:30 | 121.18 | 116.24
2020-01-02 | 122.14 | 116.51
2020-01-02 00:30 | 117.68 | 111.55
2020-01-02 01:00 | 110.75 | 104.91
2020-01-02 01:30 | 113.65 | 107.52
2020-01-02 02:00 | 110.6 | 104.14
2020-01-02 02:30 | 108.66 | 101.72
2020-01-02 03:00 | 106.59 | 100.24
2020-01-02 03:30 | 104.63 | 97.19
2020-01-02 04:00 | 112.93 | 106.28
2020-01-02 04:30 | 111.74 | 105.69
2020-01-02 05:00 | 108.06 | 101.52
2020-01-02 05:30 | 113.61 | 107.44
2020-01-02 06:00 | 116.29 | 110.91
2020-01-02 06:30 | 103.6 | 94.32
2020-01-02 07:00 | 105.2 | 95.79
2020-01-02 07:30 | 111.12 | 101.29
2020-01-02 08:00 | 104 | 93.01
2020-01-02 08:30 | 98.52 | 85.38
2020-01-02 09:00 | 93.88 | 78.88
2020-01-02 09:30 | 99 | 85.04
2020-01-02 10:00 | 93.06 | 77.71
2020-01-02 10:30 | 101.51 | 87.37
2020-01-02 11:00 | 100.59 | 86.55
2020-01-02 11:30 | 99.85 | 85.81
2020-01-02 12:00 | 98.19 | 84.71
2020-01-02 12:30 | 107.71 | 95.35
2020-01-02 13:00 | 102.25 | 89.41
2020-01-02 13:30 | 98.09 | 84.69
2020-01-02 14:00 | 101.81 | 88.78
2020-01-02 14:30 | 99.11 | 86.03
2020-01-02 15:00 | 99.18 | 86.75
2020-01-02 15:30 | 106.12 | 93.8
2020-01-02 16:00 | 108.53 | 96.73
2020-01-02 16:30 | 106.55 | 95.71
2020-01-02 17:00 | 109.95 | 100.01
2020-01-02 17:30 | 113.88 | 106.15
2020-01-02 18:00 | 115.96 | 110.14
2020-01-02 18:30 | 108.23 | 102.8
2020-01-02 19:00 | 120.56 | 116.24
2020-01-02 19:30 | 129.17 | 125.16
2020-01-02 20:00 | 132.01 | 127.27
2020-01-02 20:30 | 127.35 | 122.76
2020-01-02 21:00 | 122.88 | 118.29
2020-01-02 21:30 | 112.8 | 107.92
2020-01-02 22:00 | 116.59 | 111.56
2020-01-02 22:30 | 118.29 | 113.08
2020-01-02 23:00 | 116.52 | 110.7
2020-01-02 23:30 | 118.98 | 113.42
2020-01-03 | 109.82 | 103.1
2020-01-03 00:30 | 109.68 | 102.99
2020-01-03 01:00 | 114.65 | 108.73
2020-01-03 01:30 | 118.85 | 113.28
2020-01-03 02:00 | 116.51 | 111.25
2020-01-03 02:30 | 119.16 | 113.78
2020-01-03 03:00 | 114.11 | 108.6
2020-01-03 03:30 | 112.98 | 107.47
2020-01-03 04:00 | 110.81 | 104.92
2020-01-03 04:30 | 110.12 | 104.85
2020-01-03 05:00 | 111.74 | 106.39
2020-01-03 05:30 | 115.61 | 110.32
2020-01-03 06:00 | 113.02 | 107.81
2020-01-03 06:30 | 107.19 | 100.12
2020-01-03 07:00 | 112.43 | 105.48
2020-01-03 07:30 | 119.1 | 112.59
2020-01-03 08:00 | 105.1 | 97.91
2020-01-03 08:30 | 94.01 | 84.4
2020-01-03 09:00 | 94.36 | 84.53
2020-01-03 09:30 | 93.37 | 84.31
2020-01-03 10:00 | 97.21 | 87.19
2020-01-03 10:30 | 94.25 | 82.85
2020-01-03 11:00 | 89.55 | 78
2020-01-03 11:30 | 91.66 | 80.38
2020-01-03 12:00 | 95.46 | 84.02
2020-01-03 12:30 | 95.88 | 85.12
2020-01-03 13:00 | 96.93 | 85.37
2020-01-03 13:30 | 93.76 | 81.76
2020-01-03 14:00 | 96.83 | 84.87
2020-01-03 14:30 | 92.47 | 80.49
2020-01-03 15:00 | 96.63 | 84.76
2020-01-03 15:30 | 95.02 | 83.11
2020-01-03 16:00 | 101.96 | 90.32
2020-01-03 16:30 | 99.29 | 87.85
2020-01-03 17:00 | 97.05 | 87.57
2020-01-03 17:30 | 96.22 | 87.88
2020-01-03 18:00 | 106.15 | 99.7
2020-01-03 18:30 | 107.72 | 102.56
2020-01-03 19:00 | 114.19 | 110.4
2020-01-03 19:30 | 117.64 | 113.47
2020-01-03 20:00 | 116.04 | 111.69
2020-01-03 20:30 | 122.9 | 118.09
2020-01-03 21:00 | 117.16 | 112.68
2020-01-03 21:30 | 113.72 | 109.21
2020-01-03 22:00 | 111.64 | 106.81
2020-01-03 22:30 | 114.45 | 109.32
2020-01-03 23:00 | 116.89 | 112.21
2020-01-03 23:30 | 119.35 | 114.86
2020-01-04 | 121.49 | 116.25
2020-01-04 00:30 | 118.16 | 113.15
2020-01-04 01:00 | 109.37 | 103.85
2020-01-04 01:30 | 111.14 | 105.56
2020-01-04 02:00 | 114.16 | 109.04
2020-01-04 02:30 | 114.48 | 109.33
2020-01-04 03:00 | 111.89 | 106.33
2020-01-04 03:30 | 111.96 | 106.09
2020-01-04 04:00 | 109.54 | 103.68
2020-01-04 04:30 | 114.42 | 108.81
2020-01-04 05:00 | 108.2 | 101.89
2020-01-04 05:30 | 105.71 | 98.92
2020-01-04 06:00 | 106.5 | 100.47
2020-01-04 06:30 | 96.3 | 87.44
2020-01-04 07:00 | 100.45 | 91.46
2020-01-04 07:30 | 98.64 | 86.94
2020-01-04 08:00 | 98.9 | 86.61
2020-01-04 08:30 | 90.87 | 77.47
2020-01-04 09:00 | 89.44 | 74.98
2020-01-04 09:30 | 88.56 | 73.35
2020-01-04 10:00 | 89.97 | 73.65
2020-01-04 10:30 | 94.86 | 79.66
2020-01-04 11:00 | 94.12 | 79.68
2020-01-04 11:30 | 89.26 | 74.1
2020-01-04 12:00 | 88.66 | 73.52
2020-01-04 12:30 | 96.88 | 83.51
2020-01-04 13:00 | 95.89 | 82.69
2020-01-04 13:30 | 94.72 | 81.83
2020-01-04 14:00 | 93.66 | 80.76
2020-01-04 14:30 | 97.74 | 84.82
2020-01-04 15:00 | 97.89 | 83.55
2020-01-04 15:30 | 99.46 | 84.67
2020-01-04 16:00 | 92.73 | 77.92
2020-01-04 16:30 | 101.72 | 88.19
2020-01-04 17:00 | 107.24 | 94.84
2020-01-04 17:30 | 103.92 | 93.75
2020-01-04 18:00 | 107.81 | 100.01
2020-01-04 18:30 | 108.72 | 102.33
2020-01-04 19:00 | 113.04 | 108.11
2020-01-04 19:30 | 108.77 | 103.41
2020-01-04 20:00 | 110.82 | 105.64
2020-01-04 20:30 | 119.44 | 115.12
2020-01-04 21:00 | 118.76 | 113.7
2020-01-04 21:30 | 121.08 | 115.96
2020-01-04 22:00 | 117.56 | 112.27
2020-01-04 22:30 | 112.79 | 106.98
2020-01-04 23:00 | 109.5 | 102.59
2020-01-04 23:30 | 114.67 | 108.49
2020-01-05 | 118.67 | 113.27
2020-01-05 00:30 | 108.76 | 101.6
2020-01-05 01:00 | 106.58 | 100.09
2020-01-05 01:30 | 107.62 | 101.44
2020-01-05 02:00 | 107.47 | 100.79
2020-01-05 02:30 | 114.06 | 108.34
2020-01-05 03:00 | 110.21 | 103.85
2020-01-05 03:30 | 108.85 | 101.74
2020-01-05 04:00 | 109.36 | 101.85
2020-01-05 04:30 | 106.79 | 98.21
2020-01-05 05:00 | 113.69 | 106.55
2020-01-05 05:30 | 104.31 | 95.8
2020-01-05 06:00 | 101.45 | 92.76
2020-01-05 06:30 | 89.42 | 78.34
2020-01-05 07:00 | 93.81 | 82.86
2020-01-05 07:30 | 99.77 | 87.96
2020-01-05 08:00 | 92.37 | 77.8
2020-01-05 08:30 | 92.37 | 77.43
2020-01-05 09:00 | 101.79 | 87.74
2020-01-05 09:30 | 97.69 | 83.64
2020-01-05 10:00 | 97.97 | 84.19
2020-01-05 10:30 | 93.27 | 79.06
2020-01-05 11:00 | 102.55 | 88.69
2020-01-05 11:30 | 89.85 | 74.67
2020-01-05 12:00 | 93.71 | 78.5
2020-01-05 12:30 | 100.22 | 87.31
2020-01-05 13:00 | 105.8 | 92.15
2020-01-05 13:30 | 100.54 | 87.45
2020-01-05 14:00 | 105.3 | 92.53
2020-01-05 14:30 | 98.19 | 84.95
2020-01-05 15:00 | 99.57 | 85.91
2020-01-05 15:30 | 93.18 | 79.24
2020-01-05 16:00 | 100.54 | 87.86
2020-01-05 16:30 | 102.34 | 90.13
2020-01-05 17:00 | 102.29 | 90.72
2020-01-05 17:30 | 99.49 | 90.12
2020-01-05 18:00 | 111.57 | 106.42
2020-01-05 18:30 | 108.34 | 103.22
2020-01-05 19:00 | 110.49 | 105.92
2020-01-05 19:30 | 119.19 | 114.39
2020-01-05 20:00 | 118.29 | 113.24
2020-01-05 20:30 | 129.75 | 125.67
2020-01-05 21:00 | 127.17 | 122.86
2020-01-05 21:30 | 120.79 | 115.63
2020-01-05 22:00 | 120.22 | 115.14
2020-01-05 22:30 | 116.14 | 110.81
2020-01-05 23:00 | 119.58 | 114.34
2020-01-05 23:30 | 120.78 | 115.67
2020-01-06 | 127.55 | 122.67
2020-01-06 00:30 | 117.96 | 111.67
2020-01-06 01:00 | 116.54 | 110.25
2020-01-06 01:30 | 123.91 | 118.14
2020-01-06 02:00 | 117.14 | 110.73
2020-01-06 02:30 | 119.44 | 113.61
2020-01-06 03:00 | 114.67 | 108.59
2020-01-06 03:30 | 107.68 | 100.67
2020-01-06 04:00 | 102.68 | 95.61
2020-01-06 04:30 | 109.1 | 102.51
2020-01-06 05:00 | 109.72 | 103.25
2020-01-06 05:30 | 106.09 | 99.44
2020-01-06 06:00 | 106.61 | 100.53
2020-01-06 06:30 | 99.67 | 91.47
2020-01-06 07:00 | 101.67 | 93.77
2020-01-06 07:30 | 100.12 | 89.92
2020-01-06 08:00 | 100.02 | 88.27
2020-01-06 08:30 | 91.79 | 78.33
2020-01-06 09:00 | 91.97 | 78.61
2020-01-06 09:30 | 93.91 | 83.08
2020-01-06 10:00 | 83.88 | 71.41
2020-01-06 10:30 | 79.15 | 66.67
2020-01-06 11:00 | 77.03 | 63.65
2020-01-06 11:30 | 81.53 | 68.71
2020-01-06 12:00 | 84.24 | 72.33
2020-01-06 12:30 | 90.05 | 81.6
2020-01-06 13:00 | 87.49 | 78.27
2020-01-06 13:30 | 80.72 | 68.59
2020-01-06 14:00 | 79.42 | 65.25
2020-01-06 14:30 | 88.38 | 78.19
2020-01-06 15:00 | 90.48 | 81.55
2020-01-06 15:30 | 89.32 | 80.25
2020-01-06 16:00 | 88.32 | 81.96
2020-01-06 16:30 | 87.13 | 78.15
2020-01-06 17:00 | 90.08 | 81.1
2020-01-06 17:30 | 88.59 | 80.07
2020-01-06 18:00 | 94.86 | 89.27
2020-01-06 18:30 | 94.25 | 88.85
2020-01-06 19:00 | 110.54 | 106.14
2020-01-06 19:30 | 111.01 | 106.45
2020-01-06 20:00 | 103.17 | 98.18
2020-01-06 20:30 | 110.11 | 105.91
2020-01-06 21:00 | 113.33 | 109.22
2020-01-06 21:30 | 112.97 | 108.17
2020-01-06 22:00 | 111.9 | 106.55
2020-01-06 22:30 | 112.86 | 107.72
2020-01-06 23:00 | 108.04 | 102.37
2020-01-06 23:30 | 111.7 | 105.45
2020-01-07 | 114.03 | 109.02
2020-01-07 00:30 | 113.24 | 107.77
2020-01-07 01:00 | 116.66 | 111.06
2020-01-07 01:30 | 117.01 | 112.04
2020-01-07 02:00 | 118.5 | 113.95
2020-01-07 02:30 | 109.77 | 104.09
2020-01-07 03:00 | 115.79 | 110.57
2020-01-07 03:30 | 118.58 | 112.1
2020-01-07 04:00 | 118.51 | 111.98
2020-01-07 04:30 | 105.96 | 98.42
2020-01-07 05:00 | 111.49 | 103.93
2020-01-07 05:30 | 104.65 | 96.9
2020-01-07 06:00 | 103.22 | 96.02
2020-01-07 06:30 | 101.01 | 93.24
2020-01-07 07:00 | 85.94 | 72.34
2020-01-07 07:30 | 97.27 | 85.77
2020-01-07 08:00 | 96.65 | 86.23
2020-01-07 08:30 | 94.26 | 81.61
2020-01-07 09:00 | 92.7 | 81.16
2020-01-07 09:30 | 99.55 | 89.77
2020-01-07 10:00 | 97.02 | 86.24
2020-01-07 10:30 | 93.94 | 79.27
2020-01-07 11:00 | 86.43 | 68.25
2020-01-07 11:30 | 90.12 | 72.85
2020-01-07 12:00 | 95.99 | 82.84
2020-01-07 12:30 | 98.82 | 87.97
2020-01-07 13:00 | 99.3 | 88.24
2020-01-07 13:30 | 96.14 | 81.31
2020-01-07 14:00 | 95.65 | 81.21
2020-01-07 14:30 | 101.07 | 89.81
2020-01-07 15:00 | 103.78 | 94.48
2020-01-07 15:30 | 96.91 | 83.13
2020-01-07 16:00 | 97.81 | 86.31
2020-01-07 16:30 | 103.29 | 92.03
2020-01-07 17:00 | 97.15 | 88.29
2020-01-07 17:30 | 99.39 | 91.04
2020-01-07 18:00 | 103.16 | 95.44
2020-01-07 18:30 | 99.72 | 92.46
2020-01-07 19:00 | 107.88 | 101.69
2020-01-07 19:30 | 114.97 | 109.83
2020-01-07 20:00 | 116.72 | 111.26
2020-01-07 20:30 | 117.47 | 111.79
2020-01-07 21:00 | 116.43 | 109.87
2020-01-07 21:30 | 115.67 | 108.98
2020-01-07 22:00 | 107.4 | 100.43
2020-01-07 22:30 | 110.77 | 104.22
2020-01-07 23:00 | 115.34 | 108.43
2020-01-07 23:30 | 116.67 | 109.99
2020-01-08 | 118.83 | 112.19
2020-01-08 00:30 | 114.55 | 107.41
2020-01-08 01:00 | 109.65 | 101.71
2020-01-08 01:30 | 111.77 | 104.59
2020-01-08 02:00 | 109.69 | 102.16
2020-01-08 02:30 | 111.36 | 104.66
2020-01-08 03:00 | 109.73 | 102.88
2020-01-08 03:30 | 104.53 | 96.43
2020-01-08 04:00 | 110.3 | 104.77
2020-01-08 04:30 | 113.5 | 107.82
2020-01-08 05:00 | 107.91 | 101.68
2020-01-08 05:30 | 105.03 | 98.1
2020-01-08 06:00 | 102.83 | 96.44
2020-01-08 06:30 | 82.57 | 71.44
2020-01-08 07:00 | 87.02 | 76
2020-01-08 07:30 | 84.68 | 72.68
2020-01-08 08:00 | 84.52 | 71.07
2020-01-08 08:30 | 84.83 | 73.28
2020-01-08 09:00 | 84.48 | 73.58
2020-01-08 09:30 | 87.69 | 76.58
2020-01-08 10:00 | 87.14 | 75.07
2020-01-08 10:30 | 78.52 | 63.41
2020-01-08 11:00 | 84.31 | 71.05
2020-01-08 11:30 | 87.69 | 73.88
2020-01-08 12:00 | 86.5 | 74.66
2020-01-08 12:30 | 94.27 | 82.05
2020-01-08 13:00 | 93.57 | 81.23
2020-01-08 13:30 | 94.41 | 82.63
2020-01-08 14:00 | 95.92 | 85.64
2020-01-08 14:30 | 83.64 | 70.94
2020-01-08 15:00 | 81.5 | 67.39
2020-01-08 15:30 | 84.35 | 70.48
2020-01-08 16:00 | 88.65 | 75.84
2020-01-08 16:30 | 88.88 | 76.91
2020-01-08 17:00 | 94.11 | 84.7
2020-01-08 17:30 | 108.82 | 101.43
2020-01-08 18:00 | 98.47 | 91.29
2020-01-08 18:30 | 97.32 | 91.45
2020-01-08 19:00 | 110.18 | 105.17
2020-01-08 19:30 | 109.19 | 103.19
2020-01-08 20:00 | 110.8 | 104.21
2020-01-08 20:30 | 107.34 | 100.57
2020-01-08 21:00 | 111.83 | 105.52
2020-01-08 21:30 | 115.5 | 108.92
2020-01-08 22:00 | 114.81 | 107.6
2020-01-08 22:30 | 116.51 | 110.15
2020-01-08 23:00 | 114.07 | 107.08
2020-01-08 23:30 | 101.61 | 92.4
2020-01-09 | 103.44 | 95.24
2020-01-09 00:30 | 107.22 | 99.86
2020-01-09 01:00 | 101.32 | 92.41
2020-01-09 01:30 | 109.69 | 101.98
2020-01-09 02:00 | 105.53 | 97.59
2020-01-09 02:30 | 103.43 | 94.57
2020-01-09 03:00 | 106.72 | 98.16
2020-01-09 03:30 | 107.86 | 98.84
2020-01-09 04:00 | 100.94 | 90.45
2020-01-09 04:30 | 105.15 | 96.2
2020-01-09 05:00 | 100.75 | 90.44
2020-01-09 05:30 | 104.25 | 94.62
2020-01-09 06:00 | 97.94 | 88.27
2020-01-09 06:30 | 88.45 | 76.92
2020-01-09 07:00 | 87.76 | 74.05
2020-01-09 07:30 | 88.86 | 75.05
2020-01-09 08:00 | 88.9 | 74.87
2020-01-09 08:30 | 91.84 | 78.55
2020-01-09 09:00 | 87.08 | 73.42
2020-01-09 09:30 | 91.33 | 74.83
2020-01-09 10:00 | 92.46 | 76.8
2020-01-09 10:30 | 91.83 | 75.71
2020-01-09 11:00 | 88.87 | 71.27
2020-01-09 11:30 | 88.78 | 70.16
2020-01-09 12:00 | 87.7 | 69.94
2020-01-09 12:30 | 97.71 | 82.36
2020-01-09 13:00 | 95.49 | 80.02
2020-01-09 13:30 | 93.35 | 77.64
2020-01-09 14:00 | 97.28 | 82.42
2020-01-09 14:30 | 98.95 | 84.84
2020-01-09 15:00 | 98.8 | 85.28
2020-01-09 15:30 | 94.2 | 80.13
2020-01-09 16:00 | 93.68 | 81.58
2020-01-09 16:30 | 85.14 | 72.41
2020-01-09 17:00 | 95.39 | 84.21
2020-01-09 17:30 | 101.3 | 92.04
2020-01-09 18:00 | 102.54 | 95.08
2020-01-09 18:30 | 104.65 | 99.26
2020-01-09 19:00 | 109.61 | 104.66
2020-01-09 19:30 | 117.58 | 112.83
2020-01-09 20:00 | 109.24 | 104.03
2020-01-09 20:30 | 111.84 | 107.59
2020-01-09 21:00 | 106.84 | 101.6
2020-01-09 21:30 | 105.33 | 99.19
2020-01-09 22:00 | 113.65 | 107.83
2020-01-09 22:30 | 113.64 | 107.81
2020-01-09 23:00 | 112.67 | 106.6
2020-01-09 23:30 | 107.43 | 99.88
2020-01-10 | 105.59 | 98.41
2020-01-10 00:30 | 108.98 | 102.72
2020-01-10 01:00 | 104.21 | 97.08
2020-01-10 01:30 | 111.1 | 104.53
2020-01-10 02:00 | 109.96 | 103.19
2020-01-10 02:30 | 111.83 | 104.1
2020-01-10 03:00 | 114.29 | 106.95
2020-01-10 03:30 | 101.96 | 92.51
2020-01-10 04:00 | 112.06 | 104.27
2020-01-10 04:30 | 111.85 | 105.46
2020-01-10 05:00 | 114.96 | 108.74
2020-01-10 05:30 | 110.8 | 103.41
2020-01-10 06:00 | 109.81 | 102.63
2020-01-10 06:30 | 98.91 | 90.14
2020-01-10 07:00 | 101.44 | 92.53
2020-01-10 07:30 | 100.88 | 88.75
2020-01-10 08:00 | 100.04 | 86.23
2020-01-10 08:30 | 97.19 | 81.74
2020-01-10 09:00 | 100.65 | 88.05
2020-01-10 09:30 | 90.67 | 76.51
2020-01-10 10:00 | 104.43 | 91.98
2020-01-10 10:30 | 101.49 | 87.85
2020-01-10 11:00 | 98.32 | 83.13
2020-01-10 11:30 | 95.03 | 78.38
2020-01-10 12:00 | 91.33 | 75.28
2020-01-10 12:30 | 95.52 | 79.71
2020-01-10 13:00 | 100.03 | 83.74
2020-01-10 13:30 | 99.32 | 84.48
2020-01-10 14:00 | 96.6 | 81.61
2020-01-10 14:30 | 104.87 | 89.58
2020-01-10 15:00 | 106.65 | 91.88
2020-01-10 15:30 | 110.41 | 94.85
2020-01-10 16:00 | 102.52 | 87.92
2020-01-10 16:30 | 110.52 | 97.95
2020-01-10 17:00 | 112.24 | 102.16
2020-01-10 17:30 | 116.4 | 107.52
2020-01-10 18:00 | 123.6 | 116.46
2020-01-10 18:30 | 108.73 | 102.15
2020-01-10 19:00 | 120.3 | 115.87
2020-01-10 19:30 | 119.78 | 115.21
2020-01-10 20:00 | 118.52 | 113.24
2020-01-10 20:30 | 120.8 | 115.66
2020-01-10 21:00 | 113.51 | 107.92
2020-01-10 21:30 | 120.16 | 114.48
2020-01-10 22:00 | 114.31 | 108.25
2020-01-10 22:30 | 117.88 | 112.37
2020-01-10 23:00 | 128.68 | 123.36
2020-01-10 23:30 | 124.11 | 118.37
2020-01-11 | 116.31 | 110.11
2020-01-11 00:30 | 120.76 | 115.33
2020-01-11 01:00 | 115.87 | 110.41
2020-01-11 01:30 | 106.43 | 100.5
2020-01-11 02:00 | 109.37 | 103.79
2020-01-11 02:30 | 114.13 | 107.49
2020-01-11 03:00 | 115.34 | 109.14
2020-01-11 03:30 | 111.45 | 104.32
2020-01-11 04:00 | 110 | 102.92
2020-01-11 04:30 | 118.88 | 112.43
2020-01-11 05:00 | 112.79 | 105.29
2020-01-11 05:30 | 117.83 | 110.9
2020-01-11 06:00 | 120.76 | 114.74
2020-01-11 06:30 | 103.42 | 95.46
2020-01-11 07:00 | 109.48 | 100.57
2020-01-11 07:30 | 104.64 | 93.27
2020-01-11 08:00 | 104.81 | 92.19
2020-01-11 08:30 | 102.23 | 89.55
2020-01-11 09:00 | 104.23 | 89.23
2020-01-11 09:30 | 95.32 | 78.99
2020-01-11 10:00 | 98.94 | 82.81
2020-01-11 10:30 | 103.43 | 86.64
2020-01-11 11:00 | 97 | 82.33
2020-01-11 11:30 | 105.34 | 93.82
2020-01-11 12:00 | 109.15 | 92.66
2020-01-11 12:30 | 111.92 | 96.02
2020-01-11 13:00 | 107.38 | 91.52
2020-01-11 13:30 | 108.65 | 94.41
2020-01-11 14:00 | 112.07 | 98.72
2020-01-11 14:30 | 100.95 | 85.92
2020-01-11 15:00 | 110.26 | 95.52
2020-01-11 15:30 | 109.47 | 94.22
2020-01-11 16:00 | 107.64 | 92.33
2020-01-11 16:30 | 108.49 | 96.12
2020-01-11 17:00 | 109.79 | 98.14
2020-01-11 17:30 | 114.5 | 108.24
2020-01-11 18:00 | 119.31 | 113.73
2020-01-11 18:30 | 112.3 | 105.92
2020-01-11 19:00 | 116.09 | 110.73
2020-01-11 19:30 | 115.87 | 110.72
2020-01-11 20:00 | 128.84 | 123.33
2020-01-11 20:30 | 127.07 | 121.38
2020-01-11 21:00 | 117.29 | 110.8
2020-01-11 21:30 | 120.23 | 114.03
2020-01-11 22:00 | 114.95 | 108.75
2020-01-11 22:30 | 115.71 | 110.05
2020-01-11 23:00 | 113.92 | 107.81
2020-01-11 23:30 | 105.09 | 98.33
2020-01-12 | 110.86 | 104.46
2020-01-12 00:30 | 112.92 | 107.04
2020-01-12 01:00 | 109.54 | 103
2020-01-12 01:30 | 120.72 | 115.39
2020-01-12 02:00 | 124.8 | 119.87
2020-01-12 02:30 | 116.15 | 110.67
2020-01-12 03:00 | 107.01 | 101.22
2020-01-12 03:30 | 115.92 | 110.54
2020-01-12 04:00 | 110.62 | 104.81
2020-01-12 04:30 | 120.98 | 115.77
2020-01-12 05:00 | 109.41 | 103.74
2020-01-12 05:30 | 111.71 | 105.67
2020-01-12 06:00 | 105.63 | 99.94
2020-01-12 06:30 | 94.93 | 87.56
2020-01-12 07:00 | 104.37 | 98.56
2020-01-12 07:30 | 106.53 | 99.98
2020-01-12 08:00 | 105.16 | 97.7
2020-01-12 08:30 | 92.69 | 82.7
2020-01-12 09:00 | 98.44 | 86.06
2020-01-12 09:30 | 96.53 | 84.17
2020-01-12 10:00 | 104.59 | 96.41
2020-01-12 10:30 | 90.8 | 81.32
2020-01-12 11:00 | 82.56 | 71.72
2020-01-12 11:30 | 87.48 | 77.61
2020-01-12 12:00 | 90.54 | 80.56
2020-01-12 12:30 | 98.79 | 90.4
2020-01-12 13:00 | 109.45 | 102.73
2020-01-12 13:30 | 109.68 | 103.25
2020-01-12 14:00 | 103.36 | 95.92
2020-01-12 14:30 | 97.75 | 88.79
2020-01-12 15:00 | 111.1 | 105.71
2020-01-12 15:30 | 116.35 | 111.54
2020-01-12 16:00 | 112.37 | 106.99
2020-01-12 16:30 | 119.06 | 112.51
2020-01-12 17:00 | 106.4 | 99.41
2020-01-12 17:30 | 102.28 | 96.7
2020-01-12 18:00 | 92.34 | 87.99
2020-01-12 18:30 | 83.8 | 78.7
2020-01-12 19:00 | 87 | 82.17
2020-01-12 19:30 | 94.03 | 89.51
2020-01-12 20:00 | 88.29 | 83.18
2020-01-12 20:30 | 96.21 | 92.01
2020-01-12 21:00 | 91.59 | 86.11
2020-01-12 21:30 | 85.06 | 77.69
2020-01-12 22:00 | 89.15 | 81.72
2020-01-12 22:30 | 84.48 | 75.57
2020-01-12 23:00 | 90.16 | 82.9
2020-01-12 23:30 | 84.84 | 77.07
2020-01-13 | 83.98 | 75.4
2020-01-13 00:30 | 77.97 | 70.11
2020-01-13 01:00 | 80.94 | 73.22
2020-01-13 01:30 | 85.14 | 77.84
2020-01-13 02:00 | 88.8 | 81.94
2020-01-13 02:30 | 87.24 | 79.94
2020-01-13 03:00 | 86.67 | 78.03
2020-01-13 03:30 | 86.52 | 77.74
2020-01-13 04:00 | 87.79 | 78.81
2020-01-13 04:30 | 83.1 | 74.44
2020-01-13 05:00 | 86.1 | 78.6
2020-01-13 05:30 | 80.63 | 71.53
2020-01-13 06:00 | 77.1 | 67.15
2020-01-13 06:30 | 70.19 | 59.33
2020-01-13 07:00 | 77.82 | 67.05
2020-01-13 07:30 | 74.5 | 64.14
2020-01-13 08:00 | 75.28 | 65.74
2020-01-13 08:30 | 67.94 | 55.14
2020-01-13 09:00 | 73.21 | 60.47
2020-01-13 09:30 | 68.24 | 52.37
2020-01-13 10:00 | 70.32 | 54.26
2020-01-13 10:30 | 69.91 | 55.69
2020-01-13 11:00 | 69.49 | 56.5
2020-01-13 11:30 | 69.6 | 56.62
2020-01-13 12:00 | 67.86 | 56.79
2020-01-13 12:30 | 70.36 | 60.33
2020-01-13 13:00 | 77.28 | 67.2
2020-01-13 13:30 | 83.38 | 73
2020-01-13 14:00 | 79.95 | 68.24
2020-01-13 14:30 | 81.52 | 70.38
2020-01-13 15:00 | 80.29 | 69.97
2020-01-13 15:30 | 70.34 | 60.71
2020-01-13 16:00 | 80.8 | 70.21
2020-01-13 16:30 | 81.97 | 71.82
2020-01-13 17:00 | 80.2 | 69
2020-01-13 17:30 | 80.2 | 70.51
2020-01-13 18:00 | 85.2 | 78.94
2020-01-13 18:30 | 78.37 | 71.46
2020-01-13 19:00 | 98.6 | 93.99
2020-01-13 19:30 | 93.63 | 88.24
2020-01-13 20:00 | 93.85 | 88.83
2020-01-13 20:30 | 92.76 | 87.48
2020-01-13 21:00 | 90.3 | 85.61
2020-01-13 21:30 | 88.57 | 82.83
2020-01-13 22:00 | 94.73 | 89.74
2020-01-13 22:30 | 93.88 | 88.71
2020-01-13 23:00 | 90.35 | 84.13
2020-01-13 23:30 | 87.68 | 80.22
2020-01-14 | 89.3 | 82.12
2020-01-14 00:30 | 86.86 | 80.04
2020-01-14 01:00 | 93.05 | 85.46
2020-01-14 01:30 | 92.91 | 85.03
2020-01-14 02:00 | 88.25 | 80.45
2020-01-14 02:30 | 93.15 | 86.21
2020-01-14 03:00 | 91.45 | 83.83
2020-01-14 03:30 | 90.03 | 81.81
2020-01-14 04:00 | 88.67 | 80.92
2020-01-14 04:30 | 84.83 | 77.06
2020-01-14 05:00 | 83.93 | 75.52
2020-01-14 05:30 | 84.94 | 77.24
2020-01-14 06:00 | 78.3 | 69.86
2020-01-14 06:30 | 78.59 | 70.25
2020-01-14 07:00 | 82.05 | 74.03
2020-01-14 07:30 | 84.26 | 76.02
2020-01-14 08:00 | 90.26 | 83.25
2020-01-14 08:30 | 88.02 | 80.63
2020-01-14 09:00 | 84.27 | 76.8
2020-01-14 09:30 | 85.53 | 78.75
2020-01-14 10:00 | 83.32 | 76.05
2020-01-14 10:30 | 83.83 | 76.14
2020-01-14 11:00 | 82.35 | 75.56
2020-01-14 11:30 | 80.58 | 73.9
2020-01-14 12:00 | 87.41 | 80.44
2020-01-14 12:30 | 86.98 | 80.12
2020-01-14 13:00 | 81.64 | 74.07
2020-01-14 13:30 | 78.77 | 71.77
2020-01-14 14:00 | 77.58 | 69.03
2020-01-14 14:30 | 72.3 | 59.51
2020-01-14 15:00 | 70.92 | 60.97
2020-01-14 15:30 | 77.93 | 69.38
2020-01-14 16:00 | 80.25 | 70.65
2020-01-14 16:30 | 75.92 | 65.97
2020-01-14 17:00 | 68.35 | 57.43
2020-01-14 17:30 | 74 | 66.09
2020-01-14 18:00 | 80.55 | 74.22
2020-01-14 18:30 | 89.9 | 84.39
2020-01-14 19:00 | 101.05 | 97.24
2020-01-14 19:30 | 97.78 | 94.01
2020-01-14 20:00 | 91.56 | 88.15
2020-01-14 20:30 | 95.29 | 90.74
2020-01-14 21:00 | 84.63 | 78.98
2020-01-14 21:30 | 85.72 | 80.01
2020-01-14 22:00 | 84.58 | 79.43
2020-01-14 22:30 | 73.36 | 67.3
2020-01-14 23:00 | 85.37 | 78.86
2020-01-14 23:30 | 79.37 | 72.32
2020-01-15 | 79.96 | 73.13
2020-01-15 00:30 | 80 | 73.58
2020-01-15 01:00 | 83.35 | 75.36
2020-01-15 01:30 | 88.71 | 81.86
2020-01-15 02:00 | 82.17 | 73.83
2020-01-15 02:30 | 84.21 | 76.7
2020-01-15 03:00 | 82.44 | 74.42
2020-01-15 03:30 | 77.92 | 69.35
2020-01-15 04:00 | 77.74 | 71.25
2020-01-15 04:30 | 75.19 | 67.51
2020-01-15 05:00 | 73.78 | 65.4
2020-01-15 05:30 | 76.45 | 67.9
2020-01-15 06:00 | 73.47 | 66.74
2020-01-15 06:30 | 66.36 | 56.02
2020-01-15 07:00 | 67.75 | 56.34
2020-01-15 07:30 | 73.63 | 64.02
2020-01-15 08:00 | 78.74 | 71.77
2020-01-15 08:30 | 68.18 | 59.92
2020-01-15 09:00 | 66.05 | 58.41
2020-01-15 09:30 | 67.58 | 59.79
2020-01-15 10:00 | 69.74 | 62.61
2020-01-15 10:30 | 67.78 | 59.48
2020-01-15 11:00 | 71.47 | 63.91
2020-01-15 11:30 | 65.18 | 58.07
2020-01-15 12:00 | 70.28 | 62.64
2020-01-15 12:30 | 74.63 | 67.92
2020-01-15 13:00 | 71.01 | 65.45
2020-01-15 13:30 | 71.22 | 66.38
2020-01-15 14:00 | 73.05 | 66.34
2020-01-15 14:30 | 81.03 | 75.84
2020-01-15 15:00 | 74.28 | 66.6
2020-01-15 15:30 | 75.34 | 67.89
2020-01-15 16:00 | 79.71 | 72.36
2020-01-15 16:30 | 87.18 | 81.53
2020-01-15 17:00 | 84.07 | 77.86
2020-01-15 17:30 | 87.63 | 82.29
2020-01-15 18:00 | 79.81 | 73.41
2020-01-15 18:30 | 74.43 | 65.88
2020-01-15 19:00 | 80.74 | 73.2
2020-01-15 19:30 | 76.63 | 68.29
2020-01-15 20:00 | 80.41 | 73.28
2020-01-15 20:30 | 64.09 | 50.93
2020-01-15 21:00 | 61.47 | 44.66
2020-01-15 21:30 | 62.68 | 47.71
2020-01-15 22:00 | 63.36 | 48.91
2020-01-15 22:30 | 82.43 | 71.15
2020-01-15 23:00 | 77.65 | 66.63
2020-01-15 23:30 | 73.64 | 60.89
2020-01-16 | 73.93 | 61.25
2020-01-16 00:30 | 69.71 | 57.19
2020-01-16 01:00 | 72.69 | 59.26
2020-01-16 01:30 | 70.83 | 56.91
2020-01-16 02:00 | 70.51 | 56.13
2020-01-16 02:30 | 70.72 | 56.67
2020-01-16 03:00 | 77.46 | 65.14
2020-01-16 03:30 | 69.9 | 54.7
2020-01-16 04:00 | 76.74 | 64.13
2020-01-16 04:30 | 80.54 | 68.5
2020-01-16 05:00 | 79.51 | 67.79
2020-01-16 05:30 | 82.71 | 71.69
2020-01-16 06:00 | 77.04 | 65.25
2020-01-16 06:30 | 73.67 | 60.63
2020-01-16 07:00 | 75.01 | 61.18
2020-01-16 07:30 | 78.31 | 65.92
2020-01-16 08:00 | 79.63 | 67.87
2020-01-16 08:30 | 78.05 | 65.8
2020-01-16 09:00 | 74.87 | 61.86
2020-01-16 09:30 | 70.58 | 55.29
2020-01-16 10:00 | 78.39 | 65.49
2020-01-16 10:30 | 75.2 | 61.67
2020-01-16 11:00 | 74.67 | 61.64
2020-01-16 11:30 | 77.52 | 64.62
2020-01-16 12:00 | 76.61 | 64.22
2020-01-16 12:30 | 74.83 | 63.07
2020-01-16 13:00 | 75.11 | 64.65
2020-01-16 13:30 | 70.89 | 61.12
2020-01-16 14:00 | 75.56 | 66.37
2020-01-16 14:30 | 78.11 | 67.38
2020-01-16 15:00 | 74.68 | 58.43
2020-01-16 15:30 | 73.16 | 58.62
2020-01-16 16:00 | 72.43 | 56.08
2020-01-16 16:30 | 70 | 51.68
2020-01-16 17:00 | 74.58 | 63.84
2020-01-16 17:30 | 70.77 | 51.73
2020-01-16 18:00 | 74.54 | 61.11
2020-01-16 18:30 | 71.76 | 61.34
2020-01-16 19:00 | 80.68 | 72.68
2020-01-16 19:30 | 81.44 | 73.58
2020-01-16 20:00 | 77.1 | 68.41
2020-01-16 20:30 | 77.55 | 68.81
2020-01-16 21:00 | 75.16 | 66.46
2020-01-16 21:30 | 75.97 | 67.02
2020-01-16 22:00 | 75.72 | 66.51
2020-01-16 22:30 | 74.97 | 65.57
2020-01-16 23:00 | 71.79 | 63.12
2020-01-16 23:30 | 75.18 | 67.06
2020-01-17 | 75.1 | 66.98
2020-01-17 00:30 | 78.22 | 70
2020-01-17 01:00 | 70.9 | 61.64
2020-01-17 01:30 | 72.73 | 62.61
2020-01-17 02:00 | 71.09 | 61.53
2020-01-17 02:30 | 67.21 | 58.31
2020-01-17 03:00 | 68.21 | 59.34
2020-01-17 03:30 | 67.01 | 57.14
2020-01-17 04:00 | 64.6 | 54.61
2020-01-17 04:30 | 64.45 | 55.46
2020-01-17 05:00 | 54.94 | 46.09
2020-01-17 05:30 | 57.37 | 49
2020-01-17 06:00 | 58.36 | 50.38
2020-01-17 06:30 | 49.56 | 41.05
2020-01-17 07:00 | 47.48 | 39.2
2020-01-17 07:30 | 52.09 | 44.18
2020-01-17 08:00 | 52.59 | 44.85
2020-01-17 08:30 | 54.51 | 46.6
2020-01-17 09:00 | 56.03 | 47.48
2020-01-17 09:30 | 64.15 | 55.01
2020-01-17 10:00 | 58.89 | 49.58
2020-01-17 10:30 | 63.11 | 54.24
2020-01-17 11:00 | 59.09 | 49.6
2020-01-17 11:30 | 53.76 | 43.65
2020-01-17 12:00 | 55.99 | 45.57
2020-01-17 12:30 | 58.59 | 40.45
2020-01-17 13:00 | 64.31 | 34.73
2020-01-17 13:30 | 67.73 | 37.65
2020-01-17 14:00 | 61.71 | 29.33
2020-01-17 14:30 | 63.88 | 34.06
2020-01-17 15:00 | 62.38 | 30.91
2020-01-17 15:30 | 61.87 | 28.46
2020-01-17 16:00 | 63.1 | 31.41
2020-01-17 16:30 | 61.07 | 28.55
2020-01-17 17:00 | 58.07 | 37.28
2020-01-17 17:30 | 69.89 | 59.7
2020-01-17 18:00 | 61.98 | 51.72
2020-01-17 18:30 | 68.65 | 58.08
2020-01-17 19:00 | 66.54 | 57.33
2020-01-17 19:30 | 67.5 | 57.79
2020-01-17 20:00 | 70.46 | 61.22
2020-01-17 20:30 | 78.85 | 69.79
2020-01-17 21:00 | 74.76 | 65.55
2020-01-17 21:30 | 73.38 | 64.08
2020-01-17 22:00 | 68.25 | 59.34
2020-01-17 22:30 | 71.75 | 61.72
2020-01-17 23:00 | 73.54 | 64.37
2020-01-17 23:30 | 65.05 | 56.31
2020-01-18 | 70.83 | 61.53
2020-01-18 00:30 | 66.22 | 57.25
2020-01-18 01:00 | 62.4 | 53.4
2020-01-18 01:30 | 69.26 | 59.22
2020-01-18 02:00 | 75.52 | 65.21
2020-01-18 02:30 | 76.83 | 66.3
2020-01-18 03:00 | 71.02 | 60.83
2020-01-18 03:30 | 70.36 | 60.12
2020-01-18 04:00 | 74.29 | 64.23
2020-01-18 04:30 | 63.15 | 51.57
2020-01-18 05:00 | 69.05 | 57.85
2020-01-18 05:30 | 66.75 | 56.43
2020-01-18 06:00 | 62.1 | 51.77
2020-01-18 06:30 | 62.01 | 47.39
2020-01-18 07:00 | 69.11 | 48.59
2020-01-18 07:30 | 69.36 | 42.02
2020-01-18 08:00 | 72.28 | 40.49
2020-01-18 08:30 | 80.99 | 49.19
2020-01-18 09:00 | 76.07 | 41.5
2020-01-18 09:30 | 76.61 | 41.69
2020-01-18 10:00 | 78.96 | 45.38
2020-01-18 10:30 | 80.91 | 49.37
2020-01-18 11:00 | 76.43 | 43.02
2020-01-18 11:30 | 74.22 | 40.12
2020-01-18 12:00 | 75.19 | 43.6
2020-01-18 12:30 | 77.31 | 48.81
2020-01-18 13:00 | 81.18 | 57.77
2020-01-18 13:30 | 80.66 | 55.44
2020-01-18 14:00 | 77.61 | 49.99
2020-01-18 14:30 | 76.86 | 45.45
2020-01-18 15:00 | 76.4 | 45.97
2020-01-18 15:30 | 75.9 | 46.14
2020-01-18 16:00 | 82.69 | 54.79
2020-01-18 16:30 | 79.01 | 51.86
2020-01-18 17:00 | 76.59 | 51.61
2020-01-18 17:30 | 74.34 | 52.91
2020-01-18 18:00 | 77.57 | 61.91
2020-01-18 18:30 | 75.04 | 62.45
2020-01-18 19:00 | 80.41 | 70.99
2020-01-18 19:30 | 86.93 | 76.95
2020-01-18 20:00 | 83.11 | 72.68
2020-01-18 20:30 | 87.29 | 76.54
2020-01-18 21:00 | 91.61 | 80.36
2020-01-18 21:30 | 91.73 | 80.8
2020-01-18 22:00 | 81.21 | 69.78
2020-01-18 22:30 | 83.89 | 72.37
2020-01-18 23:00 | 88.76 | 76.7
2020-01-18 23:30 | 80.77 | 69.37
2020-01-19 | 81.95 | 70.05
2020-01-19 00:30 | 82.34 | 70.7
2020-01-19 01:00 | 81.33 | 69.94
2020-01-19 01:30 | 80.03 | 68.93
2020-01-19 02:00 | 81.16 | 70.3
2020-01-19 02:30 | 79.58 | 69.72
2020-01-19 03:00 | 83.83 | 73.08
2020-01-19 03:30 | 89.71 | 79.89
2020-01-19 04:00 | 94.33 | 83.99
2020-01-19 04:30 | 88.8 | 77.92
2020-01-19 05:00 | 86.83 | 76.1
2020-01-19 05:30 | 88.32 | 77.63
2020-01-19 06:00 | 85.17 | 74.37
2020-01-19 06:30 | 78.63 | 63.68
2020-01-19 07:00 | 85.63 | 67.36
2020-01-19 07:30 | 82.36 | 57.72
2020-01-19 08:00 | 83.88 | 56.48
2020-01-19 08:30 | 81.15 | 52.83
2020-01-19 09:00 | 79.71 | 52.58
2020-01-19 09:30 | 92.84 | 60.89
2020-01-19 10:00 | 88.45 | 52.88
2020-01-19 10:30 | 90.98 | 58.21
2020-01-19 11:00 | 89.83 | 58.37
2020-01-19 11:30 | 95.92 | 60.06
2020-01-19 12:00 | 95.42 | 60.93
2020-01-19 12:30 | 97.17 | 64.52
2020-01-19 13:00 | 95.46 | 64.59
2020-01-19 13:30 | 98.96 | 69.93
2020-01-19 14:00 | 95.45 | 70.97
2020-01-19 14:30 | 95.12 | 71.61
2020-01-19 15:00 | 96.83 | 70.63
2020-01-19 15:30 | 103.94 | 88.77
2020-01-19 16:00 | 99.45 | 83.2
2020-01-19 16:30 | 99.4 | 82.26
2020-01-19 17:00 | 102.17 | 87.51
2020-01-19 17:30 | 97.14 | 83.92
2020-01-19 18:00 | 104.14 | 91.08
2020-01-19 18:30 | 98.06 | 84.24
2020-01-19 19:00 | 108.2 | 96.85
2020-01-19 19:30 | 110.59 | 98.33
2020-01-19 20:00 | 103.68 | 90.96
2020-01-19 20:30 | 99.45 | 87.22
2020-01-19 21:00 | 91.74 | 79.95
2020-01-19 21:30 | 95.58 | 83.62
2020-01-19 22:00 | 96.74 | 84.52
2020-01-19 22:30 | 93.14 | 81.8
2020-01-19 23:00 | 90.75 | 79.01
2020-01-19 23:30 | 91.49 | 79.44
2020-01-20 | 96.39 | 85.69
2020-01-20 00:30 | 88.65 | 77.22
2020-01-20 01:00 | 89.34 | 78.99
2020-01-20 01:30 | 89.18 | 79.19
2020-01-20 02:00 | 93.49 | 81.87
2020-01-20 02:30 | 93.12 | 79.92
2020-01-20 03:00 | 104.93 | 91.86
2020-01-20 03:30 | 104.65 | 90.27
2020-01-20 04:00 | 97.84 | 84.52
2020-01-20 04:30 | 104.1 | 91.38
2020-01-20 05:00 | 97.18 | 84
2020-01-20 05:30 | 93.84 | 81.85
2020-01-20 06:00 | 94.42 | 82.63
2020-01-20 06:30 | 86.6 | 72.17
2020-01-20 07:00 | 89.69 | 76.54
2020-01-20 07:30 | 82.75 | 69.56
2020-01-20 08:00 | 83.77 | 71.21
2020-01-20 08:30 | 79.88 | 60.63
2020-01-20 09:00 | 89.08 | 72.73
2020-01-20 09:30 | 93.47 | 76.98
2020-01-20 10:00 | 91.55 | 70.58
2020-01-20 10:30 | 85.89 | 53.34
2020-01-20 11:00 | 84.46 | 55.89
2020-01-20 11:30 | 85.46 | 54.19
2020-01-20 12:00 | 81.89 | 57.09
2020-01-20 12:30 | 95.27 | 71.19
2020-01-20 13:00 | 86.14 | 63.93
2020-01-20 13:30 | 89.86 | 71.67
2020-01-20 14:00 | 94.99 | 76.83
2020-01-20 14:30 | 87.11 | 60.57
2020-01-20 15:00 | 86.48 | 64.05
2020-01-20 15:30 | 88.28 | 64.64
2020-01-20 16:00 | 90.87 | 70.99
2020-01-20 16:30 | 96.57 | 82.11
2020-01-20 17:00 | 97.63 | 85.96
2020-01-20 17:30 | 98.37 | 87.19
2020-01-20 18:00 | 98.56 | 87.69
2020-01-20 18:30 | 96.54 | 82.63
2020-01-20 19:00 | 105.26 | 92.48
2020-01-20 19:30 | 102.34 | 89.49
2020-01-20 20:00 | 102.07 | 89.43
2020-01-20 20:30 | 104.45 | 90.72
2020-01-20 21:00 | 100.73 | 86.07
2020-01-20 21:30 | 96.2 | 82.05
2020-01-20 22:00 | 101.62 | 87.77
2020-01-20 22:30 | 107.57 | 93.79
2020-01-20 23:00 | 100.51 | 87.58
2020-01-20 23:30 | 105.47 | 92.23
2020-01-21 | 97.59 | 84.4
2020-01-21 00:30 | 94.2 | 81
2020-01-21 01:00 | 102.06 | 89.41
2020-01-21 01:30 | 96.91 | 84.24
2020-01-21 02:00 | 89.21 | 79.76
2020-01-21 02:30 | 90.76 | 81.25
2020-01-21 03:00 | 93.07 | 82.62
2020-01-21 03:30 | 92.34 | 80.7
2020-01-21 04:00 | 93.87 | 83.14
2020-01-21 04:30 | 92.77 | 82.62
2020-01-21 05:00 | 89.54 | 80.44
2020-01-21 05:30 | 83 | 75.75
2020-01-21 06:00 | 78.5 | 72.39
2020-01-21 06:30 | 66.79 | 57.38
2020-01-21 07:00 | 75.89 | 67.52
2020-01-21 07:30 | 67.87 | 56.6
2020-01-21 08:00 | 67.01 | 55.65
2020-01-21 08:30 | 70.7 | 59.15
2020-01-21 09:00 | 72.84 | 61.03
2020-01-21 09:30 | 73.38 | 60.9
2020-01-21 10:00 | 68.92 | 53.11
2020-01-21 10:30 | 70.61 | 53.56
2020-01-21 11:00 | 75.83 | 57.33
2020-01-21 11:30 | 78.94 | 62.99
2020-01-21 12:00 | 77.54 | 61.08
2020-01-21 12:30 | 76.72 | 59.38
2020-01-21 13:00 | 81.44 | 63.26
2020-01-21 13:30 | 76.55 | 61.19
2020-01-21 14:00 | 90.62 | 78.31
2020-01-21 14:30 | 87.25 | 74.97
2020-01-21 15:00 | 91.97 | 80.16
2020-01-21 15:30 | 96.07 | 82.21
2020-01-21 16:00 | 90.35 | 73.66
2020-01-21 16:30 | 98.19 | 83.1
2020-01-21 17:00 | 106.36 | 92.59
2020-01-21 17:30 | 100.01 | 87.58
2020-01-21 18:00 | 103.96 | 91.89
2020-01-21 18:30 | 95.34 | 82.58
2020-01-21 19:00 | 106.16 | 94.69
2020-01-21 19:30 | 108.25 | 95.97
2020-01-21 20:00 | 106.42 | 92.74
2020-01-21 20:30 | 110.94 | 97.47
2020-01-21 21:00 | 105.6 | 92.58
2020-01-21 21:30 | 108.65 | 94.37
2020-01-21 22:00 | 104.64 | 89.74
2020-01-21 22:30 | 105.29 | 91.24
2020-01-21 23:00 | 117.3 | 103.37
2020-01-21 23:30 | 106.82 | 93.29
2020-01-22 | 106.99 | 92.92
2020-01-22 00:30 | 107.59 | 91.48
2020-01-22 01:00 | 106.28 | 91.51
2020-01-22 01:30 | 103.31 | 89.72
2020-01-22 02:00 | 102.32 | 89.91
2020-01-22 02:30 | 103.6 | 90.07
2020-01-22 03:00 | 98.54 | 84.53
2020-01-22 03:30 | 100.27 | 85.55
2020-01-22 04:00 | 101.45 | 86.59
2020-01-22 04:30 | 104.81 | 90.03
2020-01-22 05:00 | 102.98 | 89.34
2020-01-22 05:30 | 93.04 | 81.19
2020-01-22 06:00 | 90.21 | 79.37
2020-01-22 06:30 | 78.14 | 64
2020-01-22 07:00 | 85.56 | 70.75
2020-01-22 07:30 | 81.19 | 62.1
2020-01-22 08:00 | 84.67 | 66.54
2020-01-22 08:30 | 86.38 | 69.21
2020-01-22 09:00 | 81.87 | 60.48
2020-01-22 09:30 | 74.25 | 50.69
2020-01-22 10:00 | 80.15 | 58.73
2020-01-22 10:30 | 87.22 | 66.83
2020-01-22 11:00 | 86.57 | 65.03
2020-01-22 11:30 | 82.66 | 59.17
2020-01-22 12:00 | 88.22 | 61.83
2020-01-22 12:30 | 88.56 | 64.93
2020-01-22 13:00 | 82.42 | 56.6
2020-01-22 13:30 | 89.91 | 62.89
2020-01-22 14:00 | 95.86 | 69.76
2020-01-22 14:30 | 102.39 | 80.96
2020-01-22 15:00 | 100.79 | 83.75
2020-01-22 15:30 | 91.53 | 75.1
2020-01-22 16:00 | 91.05 | 64.92
2020-01-22 16:30 | 102.64 | 81.34
2020-01-22 17:00 | 98.94 | 79.14
2020-01-22 17:30 | 104.68 | 90.83
2020-01-22 18:00 | 111.67 | 99.97
2020-01-22 18:30 | 93.19 | 81.05
2020-01-22 19:00 | 99.1 | 87.39
2020-01-22 19:30 | 114.79 | 102.01
2020-01-22 20:00 | 113.21 | 100.68
2020-01-22 20:30 | 121.51 | 108.82
2020-01-22 21:00 | 115.48 | 102.73
2020-01-22 21:30 | 110.27 | 97.64
2020-01-22 22:00 | 114.52 | 101
2020-01-22 22:30 | 122.36 | 108.93
2020-01-22 23:00 | 112.21 | 98.77
2020-01-22 23:30 | 118.9 | 105.16
2020-01-23 | 108.02 | 94.28
2020-01-23 00:30 | 113.61 | 98.36
2020-01-23 01:00 | 119.94 | 105.96
2020-01-23 01:30 | 111.99 | 99.67
2020-01-23 02:00 | 119.61 | 105.51
2020-01-23 02:30 | 116.04 | 101.47
2020-01-23 03:00 | 113.37 | 98.83
2020-01-23 03:30 | 108.72 | 94.04
2020-01-23 04:00 | 106.52 | 91.72
2020-01-23 04:30 | 104.01 | 89.08
2020-01-23 05:00 | 107.24 | 91.69
2020-01-23 05:30 | 107.81 | 92.5
2020-01-23 06:00 | 108.22 | 94.55
2020-01-23 06:30 | 107.36 | 93.25
2020-01-23 07:00 | 99.92 | 88.05
2020-01-23 07:30 | 105.78 | 91.97
2020-01-23 08:00 | 103.02 | 85.77
2020-01-23 08:30 | 99.3 | 82.28
2020-01-23 09:00 | 93 | 77.76
2020-01-23 09:30 | 94.26 | 75.7
2020-01-23 10:00 | 104.03 | 83.35
2020-01-23 10:30 | 103.69 | 82.67
2020-01-23 11:00 | 101.44 | 79.34
2020-01-23 11:30 | 107.12 | 83.32
2020-01-23 12:00 | 102.02 | 78.18
2020-01-23 12:30 | 102.45 | 80.11
2020-01-23 13:00 | 101.2 | 77.2
2020-01-23 13:30 | 102.71 | 79.32
2020-01-23 14:00 | 101.62 | 71.3
2020-01-23 14:30 | 97.3 | 66.06
2020-01-23 15:00 | 99.24 | 71.95
2020-01-23 15:30 | 104.66 | 67.88
2020-01-23 16:00 | 108.53 | 78.97
2020-01-23 16:30 | 114.33 | 92.6
2020-01-23 17:00 | 117.65 | 98.12
2020-01-23 17:30 | 118.09 | 98.58
2020-01-23 18:00 | 124.97 | 108.68
2020-01-23 18:30 | 113.57 | 94.86
2020-01-23 19:00 | 118.39 | 101.2
2020-01-23 19:30 | 119.14 | 102.65
2020-01-23 20:00 | 117.87 | 100.93
2020-01-23 20:30 | 122.03 | 105.74
2020-01-23 21:00 | 121.88 | 105.12
2020-01-23 21:30 | 120.23 | 103.86
2020-01-23 22:00 | 115.63 | 99.37
2020-01-23 22:30 | 125.69 | 109.86
2020-01-23 23:00 | 116.56 | 101.36
2020-01-23 23:30 | 115.42 | 100.18
2020-01-24 | 114.91 | 100.26
2020-01-24 00:30 | 116.86 | 100.45
2020-01-24 01:00 | 112.14 | 95.43
2020-01-24 01:30 | 112.47 | 96.15
2020-01-24 02:00 | 114.01 | 97.92
2020-01-24 02:30 | 107.79 | 90.81
2020-01-24 03:00 | 113.56 | 97.67
2020-01-24 03:30 | 109.19 | 93.16
2020-01-24 04:00 | 111.9 | 96.37
2020-01-24 04:30 | 114.81 | 98.32
2020-01-24 05:00 | 118.73 | 101.79
2020-01-24 05:30 | 108.62 | 90.94
2020-01-24 06:00 | 108.83 | 91.82
2020-01-24 06:30 | 104.83 | 86.99
2020-01-24 07:00 | 105.68 | 87.91
2020-01-24 07:30 | 106.06 | 88.62
2020-01-24 08:00 | 104.48 | 86.6
2020-01-24 08:30 | 107.26 | 89.04
2020-01-24 09:00 | 108.6 | 89.17
2020-01-24 09:30 | 103.91 | 78.15
2020-01-24 10:00 | 100.94 | 72.86
2020-01-24 10:30 | 103.66 | 79.69
2020-01-24 11:00 | 95.13 | 70.86
2020-01-24 11:30 | 98.19 | 75.05
2020-01-24 12:00 | 103.48 | 77.89
2020-01-24 12:30 | 102.14 | 76.38
2020-01-24 13:00 | 106.47 | 77.52
2020-01-24 13:30 | 105.8 | 83.04
2020-01-24 14:00 | 101.87 | 83.58
2020-01-24 14:30 | 93.11 | 72.47
2020-01-24 15:00 | 94.3 | 73.9
2020-01-24 15:30 | 84.49 | 76.43
2020-01-24 16:00 | 83.66 | 77.85
2020-01-24 16:30 | 80.72 | 75.19
2020-01-24 17:00 | 77.16 | 71.13
2020-01-24 17:30 | 88.47 | 82.38
2020-01-24 18:00 | 93.25 | 87.68
2020-01-24 18:30 | 81.2 | 76.11
2020-01-24 19:00 | 84.63 | 79.85
2020-01-24 19:30 | 81.25 | 76.91
2020-01-24 20:00 | 83.97 | 79.37
2020-01-24 20:30 | 83.88 | 79.59
2020-01-24 21:00 | 79.39 | 75.04
2020-01-24 21:30 | 82.26 | 77.98
2020-01-24 22:00 | 86.57 | 82.3
2020-01-24 22:30 | 88.25 | 84.23
2020-01-24 23:00 | 90.24 | 85.93
2020-01-24 23:30 | 80.89 | 76.41
2020-01-25 | 78.06 | 73.98
2020-01-25 00:30 | 84 | 79.79
2020-01-25 01:00 | 77.06 | 73.18
2020-01-25 01:30 | 69.96 | 65.93
2020-01-25 02:00 | 75.28 | 71.05
2020-01-25 02:30 | 75.66 | 71.49
2020-01-25 03:00 | 72.65 | 68.37
2020-01-25 03:30 | 68.52 | 64.51
2020-01-25 04:00 | 75.92 | 71.97
2020-01-25 04:30 | 75.17 | 71.21
2020-01-25 05:00 | 75.14 | 71.43
2020-01-25 05:30 | 80.64 | 77.02
2020-01-25 06:00 | 81.72 | 78.25
2020-01-25 06:30 | 73.79 | 69.88
2020-01-25 07:00 | 85.21 | 81.27
2020-01-25 07:30 | 80.19 | 76.03
2020-01-25 08:00 | 73.51 | 69.34
2020-01-25 08:30 | 67.88 | 63.61
2020-01-25 09:00 | 68.04 | 61.48
2020-01-25 09:30 | 65.54 | 54.55
2020-01-25 10:00 | 75.63 | 66.42
2020-01-25 10:30 | 75.81 | 66.2
2020-01-25 11:00 | 73.19 | 64.84
2020-01-25 11:30 | 73.97 | 68.51
2020-01-25 12:00 | 71.91 | 64.32
2020-01-25 12:30 | 82.51 | 72.16
2020-01-25 13:00 | 75.99 | 61.66
2020-01-25 13:30 | 77.84 | 69.82
2020-01-25 14:00 | 80.84 | 70.86
2020-01-25 14:30 | 81.24 | 68.15
2020-01-25 15:00 | 77.83 | 65.07
2020-01-25 15:30 | 86.35 | 78.9
2020-01-25 16:00 | 91.2 | 84.76
2020-01-25 16:30 | 79.78 | 70.45
2020-01-25 17:00 | 77.95 | 65.61
2020-01-25 17:30 | 76.46 | 68.45
2020-01-25 18:00 | 86.31 | 79.62
2020-01-25 18:30 | 81.29 | 75.01
2020-01-25 19:00 | 85.07 | 78.27
2020-01-25 19:30 | 80.28 | 73.1
2020-01-25 20:00 | 81.42 | 74.23
2020-01-25 20:30 | 83.36 | 76.5
2020-01-25 21:00 | 83.7 | 77.61
2020-01-25 21:30 | 77.55 | 71.57
2020-01-25 22:00 | 83.85 | 77.35
2020-01-25 22:30 | 78.45 | 72.18
2020-01-25 23:00 | 84.31 | 79.21
2020-01-25 23:30 | 82.9 | 77.78
2020-01-26 | 84.41 | 78.81
2020-01-26 00:30 | 74.84 | 68.77
2020-01-26 01:00 | 72.31 | 66.01
2020-01-26 01:30 | 78.93 | 73.21
2020-01-26 02:00 | 74.12 | 67.8
2020-01-26 02:30 | 80.92 | 74.52
2020-01-26 03:00 | 78.67 | 72.47
2020-01-26 03:30 | 70.51 | 64.18
2020-01-26 04:00 | 74.2 | 68.46
2020-01-26 04:30 | 73.44 | 68.04
2020-01-26 05:00 | 88.11 | 82.3
2020-01-26 05:30 | 78.01 | 72.08
2020-01-26 06:00 | 80.84 | 74.92
2020-01-26 06:30 | 75.05 | 68.72
2020-01-26 07:00 | 80.35 | 72.72
2020-01-26 07:30 | 75.23 | 68.34
2020-01-26 08:00 | 66.11 | 58.83
2020-01-26 08:30 | 69.67 | 60.78
2020-01-26 09:00 | 68 | 58.23
2020-01-26 09:30 | 72.68 | 64.91
2020-01-26 10:00 | 73.78 | 62.13
2020-01-26 10:30 | 67.92 | 56.9
2020-01-26 11:00 | 66.02 | 49.95
2020-01-26 11:30 | 69.8 | 51.73
2020-01-26 12:00 | 65.86 | 48.06
2020-01-26 12:30 | 71.41 | 54.69
2020-01-26 13:00 | 68.28 | 53.2
2020-01-26 13:30 | 74.81 | 63.59
2020-01-26 14:00 | 79.21 | 64.44
2020-01-26 14:30 | 81.38 | 72.45
2020-01-26 15:00 | 78.29 | 65.91
2020-01-26 15:30 | 72.48 | 62.02
2020-01-26 16:00 | 74.91 | 66.56
2020-01-26 16:30 | 76.09 | 68
2020-01-26 17:00 | 77.46 | 68.84
2020-01-26 17:30 | 79.08 | 71.37
2020-01-26 18:00 | 79.16 | 72
2020-01-26 18:30 | 80.77 | 73.81
2020-01-26 19:00 | 89.57 | 83.35
2020-01-26 19:30 | 84.81 | 78.44
2020-01-26 20:00 | 82.39 | 76.69
2020-01-26 20:30 | 82.69 | 76.63
2020-01-26 21:00 | 84.14 | 78.43
2020-01-26 21:30 | 87.37 | 81.85
2020-01-26 22:00 | 81.67 | 76.68
2020-01-26 22:30 | 79.64 | 75.06
2020-01-26 23:00 | 81.22 | 76.87
2020-01-26 23:30 | 84.21 | 80.05
2020-01-27 | 88.67 | 84.29
2020-01-27 00:30 | 91.94 | 87.5
2020-01-27 01:00 | 96.99 | 92.45
2020-01-27 01:30 | 88.64 | 84.28
2020-01-27 02:00 | 102.23 | 97.25
2020-01-27 02:30 | 96.13 | 92.08
2020-01-27 03:00 | 93.11 | 88.8
2020-01-27 03:30 | 89.9 | 85.26
2020-01-27 04:00 | 89.35 | 85.14
2020-01-27 04:30 | 88.3 | 83.61
2020-01-27 05:00 | 89.46 | 84.3
2020-01-27 05:30 | 87.87 | 82.58
2020-01-27 06:00 | 84.95 | 80.42
2020-01-27 06:30 | 79.17 | 73.93
2020-01-27 07:00 | 88.77 | 83.04
2020-01-27 07:30 | 96.47 | 91.23
2020-01-27 08:00 | 91.35 | 85.44
2020-01-27 08:30 | 84.18 | 78.44
2020-01-27 09:00 | 84.9 | 75.96
2020-01-27 09:30 | 90.97 | 80.35
2020-01-27 10:00 | 86.17 | 74.4
2020-01-27 10:30 | 87.17 | 72.79
2020-01-27 11:00 | 83.52 | 69.94
2020-01-27 11:30 | 83.62 | 73.38
2020-01-27 12:00 | 85.8 | 76.73
2020-01-27 12:30 | 94.38 | 84.77
2020-01-27 13:00 | 90.54 | 78.52
2020-01-27 13:30 | 88.57 | 78.36
2020-01-27 14:00 | 93.31 | 84.19
2020-01-27 14:30 | 97.65 | 90.28
2020-01-27 15:00 | 101.94 | 94.59
2020-01-27 15:30 | 89.07 | 82.53
2020-01-27 16:00 | 83.18 | 75.29
2020-01-27 16:30 | 88.54 | 81.24
2020-01-27 17:00 | 91.59 | 85.13
2020-01-27 17:30 | 91.54 | 86.48
2020-01-27 18:00 | 99.02 | 94.11
2020-01-27 18:30 | 98.69 | 92.77
2020-01-27 19:00 | 96.69 | 91.84
2020-01-27 19:30 | 96.99 | 92.24
2020-01-27 20:00 | 96.34 | 91.25
2020-01-27 20:30 | 98.15 | 93.06
2020-01-27 21:00 | 101.75 | 96.8
2020-01-27 21:30 | 101.01 | 96.39
2020-01-27 22:00 | 106.95 | 101.93
2020-01-27 22:30 | 106.82 | 101.29
2020-01-27 23:00 | 99.95 | 93.59
2020-01-27 23:30 | 107.31 | 101.41
2020-01-28 | 92 | 86.65
2020-01-28 00:30 | 95.23 | 89.84
2020-01-28 01:00 | 100.71 | 94.56
2020-01-28 01:30 | 94.39 | 87.6
2020-01-28 02:00 | 98.64 | 91.42
2020-01-28 02:30 | 108.07 | 100.99
2020-01-28 03:00 | 106.45 | 99.09
2020-01-28 03:30 | 97.34 | 89.27
2020-01-28 04:00 | 102.1 | 94.26
2020-01-28 04:30 | 103.16 | 95.76
2020-01-28 05:00 | 106.6 | 99.74
2020-01-28 05:30 | 102.07 | 94.51
2020-01-28 06:00 | 99.29 | 92.41
2020-01-28 06:30 | 97.59 | 89.23
2020-01-28 07:00 | 94.71 | 86.12
2020-01-28 07:30 | 107.76 | 99.44
2020-01-28 08:00 | 104.66 | 96.04
2020-01-28 08:30 | 99.95 | 88.21
2020-01-28 09:00 | 103.47 | 86.92
2020-01-28 09:30 | 101.83 | 83.01
2020-01-28 10:00 | 104.71 | 88.72
2020-01-28 10:30 | 99.23 | 84.78
2020-01-28 11:00 | 92.1 | 77
2020-01-28 11:30 | 87.26 | 69.04
2020-01-28 12:00 | 91.74 | 71.78
2020-01-28 12:30 | 90.79 | 68.65
2020-01-28 13:00 | 89.84 | 69.38
2020-01-28 13:30 | 98.77 | 80.12
2020-01-28 14:00 | 99.47 | 82.26
2020-01-28 14:30 | 91.7 | 72.23
2020-01-28 15:00 | 90.88 | 74.16
2020-01-28 15:30 | 92.46 | 79.59
2020-01-28 16:00 | 92.74 | 79
2020-01-28 16:30 | 91.47 | 74.45
2020-01-28 17:00 | 99.22 | 81.1
2020-01-28 17:30 | 99.82 | 88.22
2020-01-28 18:00 | 108.18 | 98.84
2020-01-28 18:30 | 97.17 | 87.63
2020-01-28 19:00 | 99.69 | 91.63
2020-01-28 19:30 | 107.54 | 98.98
2020-01-28 20:00 | 112.25 | 104.55
2020-01-28 20:30 | 114.29 | 106.03
2020-01-28 21:00 | 110.03 | 102.18
2020-01-28 21:30 | 104.52 | 96.82
2020-01-28 22:00 | 110.61 | 102.66
2020-01-28 22:30 | 101.29 | 93.29
2020-01-28 23:00 | 108.52 | 98.5
2020-01-28 23:30 | 108.84 | 97.9
2020-01-29 | 104.73 | 94.01
2020-01-29 00:30 | 109.66 | 99.51
2020-01-29 01:00 | 112.24 | 102.41
2020-01-29 01:30 | 113.12 | 102.61
2020-01-29 02:00 | 116.07 | 105.64
2020-01-29 02:30 | 109.45 | 99.29
2020-01-29 03:00 | 102.37 | 92.25
2020-01-29 03:30 | 112.75 | 101.47
2020-01-29 04:00 | 102.71 | 92.5
2020-01-29 04:30 | 109.44 | 98.31
2020-01-29 05:00 | 105.25 | 94.69
2020-01-29 05:30 | 105.3 | 94.26
2020-01-29 06:00 | 103 | 93.18
2020-01-29 06:30 | 96.98 | 85.09
2020-01-29 07:00 | 92.94 | 80.35
2020-01-29 07:30 | 96.11 | 82.97
2020-01-29 08:00 | 95.29 | 78.29
2020-01-29 08:30 | 94.88 | 78.17
2020-01-29 09:00 | 92.12 | 73.28
2020-01-29 09:30 | 91.75 | 68.06
2020-01-29 10:00 | 91.74 | 70.47
2020-01-29 10:30 | 95.6 | 73.94
2020-01-29 11:00 | 100.87 | 71.48
2020-01-29 11:30 | 102.8 | 73.74
2020-01-29 12:00 | 103.58 | 73.37
2020-01-29 12:30 | 105.12 | 80.22
2020-01-29 13:00 | 101.55 | 75.04
2020-01-29 13:30 | 100.27 | 72.85
2020-01-29 14:00 | 102.55 | 76.23
2020-01-29 14:30 | 105.9 | 84.63
2020-01-29 15:00 | 105.11 | 85.08
2020-01-29 15:30 | 106.01 | 83.81
2020-01-29 16:00 | 107 | 86.92
2020-01-29 16:30 | 109.8 | 94.48
2020-01-29 17:00 | 105.43 | 90.03
2020-01-29 17:30 | 102.59 | 88.22
2020-01-29 18:00 | 110.87 | 99.63
2020-01-29 18:30 | 101.87 | 91.08
2020-01-29 19:00 | 101.06 | 93.96
2020-01-29 19:30 | 102.37 | 95.15
2020-01-29 20:00 | 111.2 | 103.28
2020-01-29 20:30 | 111.93 | 103.75
2020-01-29 21:00 | 114.97 | 106.88
2020-01-29 21:30 | 112.18 | 103.95
2020-01-29 22:00 | 112.63 | 104.46
2020-01-29 22:30 | 109.64 | 100.76
2020-01-29 23:00 | 118.74 | 110.33
2020-01-29 23:30 | 110.24 | 101.6
2020-01-30 | 114.25 | 105.35
2020-01-30 00:30 | 105.13 | 96.1
2020-01-30 01:00 | 106.91 | 98.24
2020-01-30 01:30 | 100.95 | 92.21
2020-01-30 02:00 | 99.23 | 90.08
2020-01-30 02:30 | 93.11 | 84.42
2020-01-30 03:00 | 88.92 | 80.72
2020-01-30 03:30 | 94.04 | 85.48
2020-01-30 04:00 | 87.38 | 79.29
2020-01-30 04:30 | 81.05 | 72.85
2020-01-30 05:00 | 89.83 | 82.53
2020-01-30 05:30 | 91.23 | 84.4
2020-01-30 06:00 | 93.85 | 87.08
2020-01-30 06:30 | 86.46 | 78.12
2020-01-30 07:00 | 76.04 | 66.71
2020-01-30 07:30 | 79.37 | 69.06
2020-01-30 08:00 | 91.3 | 81.77
2020-01-30 08:30 | 85.7 | 74.95
2020-01-30 09:00 | 93.65 | 82.9
2020-01-30 09:30 | 91.63 | 76.42
2020-01-30 10:00 | 80.56 | 63.59
2020-01-30 10:30 | 95.84 | 76.5
2020-01-30 11:00 | 84.17 | 65.61
2020-01-30 11:30 | 78.49 | 56.38
2020-01-30 12:00 | 87.01 | 65.09
2020-01-30 12:30 | 81.54 | 59.44
2020-01-30 13:00 | 85.06 | 65.57
2020-01-30 13:30 | 90.62 | 68.72
2020-01-30 14:00 | 85.47 | 63.22
2020-01-30 14:30 | 89.95 | 70.3
2020-01-30 15:00 | 88.24 | 66.69
2020-01-30 15:30 | 83.43 | 63.15
2020-01-30 16:00 | 89.14 | 67.17
2020-01-30 16:30 | 85.18 | 64.93
2020-01-30 17:00 | 81.38 | 65
2020-01-30 17:30 | 94.59 | 85.24
2020-01-30 18:00 | 97.06 | 89.96
2020-01-30 18:30 | 100.84 | 94
2020-01-30 19:00 | 96.01 | 89.85
2020-01-30 19:30 | 112.04 | 104.71
2020-01-30 20:00 | 102.52 | 95.46
2020-01-30 20:30 | 98.11 | 90.6
2020-01-30 21:00 | 96.82 | 89.24
2020-01-30 21:30 | 92.82 | 85.42
2020-01-30 22:00 | 99.78 | 93.26
2020-01-30 22:30 | 102.72 | 95.88
2020-01-30 23:00 | 98.96 | 91.8
2020-01-30 23:30 | 104.18 | 97.52
2020-01-31 | 104.41 | 97.91
2020-01-31 00:30 | 101.56 | 95.91
2020-01-31 01:00 | 105.49 | 99.93
2020-01-31 01:30 | 102.29 | 96.61
2020-01-31 02:00 | 103.4 | 97.62
2020-01-31 02:30 | 104.62 | 98.81
2020-01-31 03:00 | 93.1 | 87.01
2020-01-31 03:30 | 106.98 | 100.21
2020-01-31 04:00 | 102.53 | 94.77
2020-01-31 04:30 | 103.3 | 95.27
2020-01-31 05:00 | 111.29 | 102.68
2020-01-31 05:30 | 107.43 | 98.25
2020-01-31 06:00 | 111.65 | 102.37
2020-01-31 06:30 | 103.25 | 92.18
2020-01-31 07:00 | 95.55 | 81.31
2020-01-31 07:30 | 97.1 | 77.17
2020-01-31 08:00 | 96.01 | 74.65
2020-01-31 08:30 | 101.93 | 78.78
2020-01-31 09:00 | 104.33 | 80.1
2020-01-31 09:30 | 106.63 | 83.77
2020-01-31 10:00 | 113.85 | 89.71
2020-01-31 10:30 | 108.57 | 87.42
2020-01-31 11:00 | 113.28 | 91.94
2020-01-31 11:30 | 107.8 | 88.49
2020-01-31 12:00 | 107.58 | 84.05
2020-01-31 12:30 | 116.26 | 94.19
2020-01-31 13:00 | 116.19 | 94.32
2020-01-31 13:30 | 103.27 | 80.73
2020-01-31 14:00 | 107.16 | 87.87
2020-01-31 14:30 | 109.14 | 97.44
2020-01-31 15:00 | 101.16 | 77.4
2020-01-31 15:30 | 107.63 | 82.6
2020-01-31 16:00 | 107.07 | 86.91
2020-01-31 16:30 | 118.71 | 105.98
2020-01-31 17:00 | 103.93 | 84.56
2020-01-31 17:30 | 106.38 | 91.07
2020-01-31 18:00 | 103.39 | 91.5
2020-01-31 18:30 | 97.79 | 86.12
2020-01-31 19:00 | 109.64 | 99.03
2020-01-31 19:30 | 112.12 | 101.44
2020-01-31 20:00 | 110.72 | 101.76
2020-01-31 20:30 | 115.09 | 106.22
2020-01-31 21:00 | 115.76 | 106.92
2020-01-31 21:30 | 117.51 | 108
2020-01-31 22:00 | 112.81 | 102.09
2020-01-31 22:30 | 110.66 | 100.82
2020-01-31 23:00 | 119.55 | 109.7
2020-01-31 23:30 | 117.68 | 107.22
2020-02-01 | 116.01 | 106.02
2020-02-01 00:30 | 118.22 | 107.48
2020-02-01 01:00 | 112.15 | 102.01
2020-02-01 01:30 | 117.75 | 106.28
2020-02-01 02:00 | 113.54 | 102.19
2020-02-01 02:30 | 104 | 93.64
2020-02-01 03:00 | 101.9 | 91.18
2020-02-01 03:30 | 97.92 | 87.42
2020-02-01 04:00 | 102.2 | 91.85
2020-02-01 04:30 | 107.86 | 97.85
2020-02-01 05:00 | 96.48 | 87.47
2020-02-01 05:30 | 98.83 | 92.15
2020-02-01 06:00 | 106.31 | 100.49
2020-02-01 06:30 | 94.97 | 86.24
2020-02-01 07:00 | 97.94 | 88.74
2020-02-01 07:30 | 91.73 | 79.52
2020-02-01 08:00 | 92.01 | 78.29
2020-02-01 08:30 | 88.12 | 72.62
2020-02-01 09:00 | 85.97 | 72.42
2020-02-01 09:30 | 93.29 | 76.4
2020-02-01 10:00 | 93.39 | 78.5
2020-02-01 10:30 | 89.21 | 74.52
2020-02-01 11:00 | 94.91 | 77.49
2020-02-01 11:30 | 97.15 | 80.46
2020-02-01 12:00 | 108.59 | 96.59
2020-02-01 12:30 | 106.83 | 94.88
2020-02-01 13:00 | 104.62 | 89.27
2020-02-01 13:30 | 102.97 | 87.51
2020-02-01 14:00 | 103 | 91.73
2020-02-01 14:30 | 104.91 | 93.58
2020-02-01 15:00 | 96.01 | 80.69
2020-02-01 15:30 | 104.38 | 90.34
2020-02-01 16:00 | 103.35 | 93.77
2020-02-01 16:30 | 108.67 | 99.2
2020-02-01 17:00 | 108.26 | 100.6
2020-02-01 17:30 | 112.37 | 105.69
2020-02-01 18:00 | 102.29 | 95.12
2020-02-01 18:30 | 105.29 | 99.62
2020-02-01 19:00 | 110.24 | 106.16
2020-02-01 19:30 | 113.52 | 109.65
2020-02-01 20:00 | 117.75 | 113.64
2020-02-01 20:30 | 113.82 | 109.47
2020-02-01 21:00 | 114.14 | 109.98
2020-02-01 21:30 | 110.89 | 106.27
2020-02-01 22:00 | 106.61 | 101.99
2020-02-01 22:30 | 110.75 | 106.56
2020-02-01 23:00 | 113.1 | 108.28
2020-02-01 23:30 | 113.49 | 108.36
2020-02-02 | 108.27 | 102.8
2020-02-02 00:30 | 112.78 | 106.98
2020-02-02 01:00 | 103.75 | 98.83
2020-02-02 01:30 | 102.82 | 98.54
2020-02-02 02:00 | 99.23 | 95.02
2020-02-02 02:30 | 103.07 | 98.98
2020-02-02 03:00 | 108.2 | 103.75
2020-02-02 03:30 | 109.71 | 104.94
2020-02-02 04:00 | 104.82 | 99.96
2020-02-02 04:30 | 100.34 | 95.65
2020-02-02 05:00 | 105.22 | 100.28
2020-02-02 05:30 | 100.16 | 95.76
2020-02-02 06:00 | 95.75 | 91.85
2020-02-02 06:30 | 87.28 | 81.79
2020-02-02 07:00 | 94.36 | 87.61
2020-02-02 07:30 | 88.73 | 81.14
2020-02-02 08:00 | 83.24 | 71.12
2020-02-02 08:30 | 93.68 | 86.81
2020-02-02 09:00 | 86.08 | 80.39
2020-02-02 09:30 | 90.43 | 86.42
2020-02-02 10:00 | 86.11 | 79.66
2020-02-02 10:30 | 89.37 | 81.19
2020-02-02 11:00 | 88.15 | 79.14
2020-02-02 11:30 | 90.11 | 82.15
2020-02-02 12:00 | 90.11 | 80.71
2020-02-02 12:30 | 93.34 | 84.57
2020-02-02 13:00 | 97.78 | 88.46
2020-02-02 13:30 | 104.44 | 95.02
2020-02-02 14:00 | 97.83 | 87.34
2020-02-02 14:30 | 93.43 | 85.45
2020-02-02 15:00 | 94.32 | 84.4
2020-02-02 15:30 | 93.06 | 82.83
2020-02-02 16:00 | 98.16 | 88.84
2020-02-02 16:30 | 94.37 | 85.34
2020-02-02 17:00 | 89.58 | 81.05
2020-02-02 17:30 | 96.82 | 91.02
2020-02-02 18:00 | 109.99 | 106.27
2020-02-02 18:30 | 101.81 | 98.88
2020-02-02 19:00 | 113.87 | 111.45
2020-02-02 19:30 | 106.45 | 104.08
2020-02-02 20:00 | 107.29 | 105.13
2020-02-02 20:30 | 118.84 | 116.88
2020-02-02 21:00 | 109.89 | 107.86
2020-02-02 21:30 | 109.82 | 107.89
2020-02-02 22:00 | 115.75 | 113.65
2020-02-02 22:30 | 114.91 | 112.96
2020-02-02 23:00 | 105.1 | 103.02
2020-02-02 23:30 | 102.64 | 100.06
2020-02-03 | 97.7 | 94.75
2020-02-03 00:30 | 93.4 | 90.03
2020-02-03 01:00 | 94.55 | 92.14
2020-02-03 01:30 | 92.07 | 89.55
2020-02-03 02:00 | 95.38 | 92.77
2020-02-03 02:30 | 97.55 | 95.22
2020-02-03 03:00 | 96.97 | 95.09
2020-02-03 03:30 | 96.61 | 94.89
2020-02-03 04:00 | 91.67 | 89.46
2020-02-03 04:30 | 87.5 | 85
2020-02-03 05:00 | 88.01 | 85.77
2020-02-03 05:30 | 88.53 | 86.01
2020-02-03 06:00 | 90.61 | 87.91
2020-02-03 06:30 | 82.97 | 79.16
2020-02-03 07:00 | 79.3 | 72.87
2020-02-03 07:30 | 78.02 | 70.42
2020-02-03 08:00 | 74.61 | 65.42
2020-02-03 08:30 | 77.69 | 68.7
2020-02-03 09:00 | 79.77 | 70.41
2020-02-03 09:30 | 78.39 | 68.44
2020-02-03 10:00 | 80.88 | 72.26
2020-02-03 10:30 | 76.94 | 68.07
2020-02-03 11:00 | 77.19 | 68.33
2020-02-03 11:30 | 78.24 | 68.98
2020-02-03 12:00 | 74.52 | 65.16
2020-02-03 12:30 | 75.14 | 67.55
2020-02-03 13:00 | 77.49 | 69.26
2020-02-03 13:30 | 78.64 | 68.85
2020-02-03 14:00 | 84.04 | 69.9
2020-02-03 14:30 | 89.19 | 75.76
2020-02-03 15:00 | 87.7 | 72.9
2020-02-03 15:30 | 85.95 | 72.34
2020-02-03 16:00 | 82.82 | 70.33
2020-02-03 16:30 | 90.94 | 81.14
2020-02-03 17:00 | 93.43 | 84.53
2020-02-03 17:30 | 96.41 | 87.16
2020-02-03 18:00 | 99.93 | 92.63
2020-02-03 18:30 | 101.26 | 94.34
2020-02-03 19:00 | 113.38 | 108.64
2020-02-03 19:30 | 115.97 | 111.64
2020-02-03 20:00 | 113.67 | 108.65
2020-02-03 20:30 | 120.03 | 115.33
2020-02-03 21:00 | 117.51 | 112.54
2020-02-03 21:30 | 95.11 | 88.53
2020-02-03 22:00 | 99.24 | 93.48
2020-02-03 22:30 | 98.72 | 92.83
2020-02-03 23:00 | 92.47 | 86.23
2020-02-03 23:30 | 90.67 | 83.25
2020-02-04 | 99.44 | 91.95
2020-02-04 00:30 | 99.14 | 92.07
2020-02-04 01:00 | 103.68 | 97.25
2020-02-04 01:30 | 97.2 | 90.1
2020-02-04 02:00 | 101.27 | 93.96
2020-02-04 02:30 | 102.07 | 95.16
2020-02-04 03:00 | 103.22 | 95.54
2020-02-04 03:30 | 103.6 | 95.71
2020-02-04 04:00 | 107.52 | 100.41
2020-02-04 04:30 | 109.75 | 102.81
2020-02-04 05:00 | 107.23 | 100.36
2020-02-04 05:30 | 107.04 | 100.62
2020-02-04 06:00 | 108.31 | 101.28
2020-02-04 06:30 | 107.46 | 99.21
2020-02-04 07:00 | 99.06 | 90.37
2020-02-04 07:30 | 97.8 | 85.69
2020-02-04 08:00 | 93.18 | 78.28
2020-02-04 08:30 | 95.04 | 81.55
2020-02-04 09:00 | 98.99 | 84.04
2020-02-04 09:30 | 89.73 | 71.69
2020-02-04 10:00 | 95.01 | 80.5
2020-02-04 10:30 | 98.25 | 85.82
2020-02-04 11:00 | 91.73 | 76.85
2020-02-04 11:30 | 92.86 | 77.85
2020-02-04 12:00 | 89.16 | 73.61
2020-02-04 12:30 | 88.05 | 74.21
2020-02-04 13:00 | 91.95 | 81.02
2020-02-04 13:30 | 93.7 | 83.86
2020-02-04 14:00 | 80.73 | 63.44
2020-02-04 14:30 | 95.93 | 86.79
2020-02-04 15:00 | 100.42 | 90.23
2020-02-04 15:30 | 101.31 | 93.68
2020-02-04 16:00 | 97.04 | 88.64
2020-02-04 16:30 | 101.26 | 94.84
2020-02-04 17:00 | 110.39 | 105.63
2020-02-04 17:30 | 103.25 | 97.69
2020-02-04 18:00 | 101.22 | 96.31
2020-02-04 18:30 | 92.95 | 88.23
2020-02-04 19:00 | 99.12 | 94.92
2020-02-04 19:30 | 102.58 | 98.74
2020-02-04 20:00 | 103.68 | 99.85
2020-02-04 20:30 | 103.09 | 98.6
2020-02-04 21:00 | 100.17 | 94.88
2020-02-04 21:30 | 93.07 | 86.72
2020-02-04 22:00 | 91.58 | 84.42
2020-02-04 22:30 | 92.05 | 84.48
2020-02-04 23:00 | 88.66 | 80.24
2020-02-04 23:30 | 91.74 | 83.76
2020-02-05 | 87.33 | 79.58
2020-02-05 00:30 | 96.46 | 87.96
2020-02-05 01:00 | 100.49 | 92.05
2020-02-05 01:30 | 101.13 | 93.21
2020-02-05 02:00 | 106.87 | 99.02
2020-02-05 02:30 | 102.4 | 94.27
2020-02-05 03:00 | 95.62 | 86.62
2020-02-05 03:30 | 97.59 | 89.26
2020-02-05 04:00 | 101.21 | 94.25
2020-02-05 04:30 | 107.11 | 100.72
2020-02-05 05:00 | 109.53 | 103.48
2020-02-05 05:30 | 107.91 | 101.52
2020-02-05 06:00 | 104.69 | 98.15
2020-02-05 06:30 | 109.06 | 103.97
2020-02-05 07:00 | 93.21 | 86.14
2020-02-05 07:30 | 97.4 | 89.25
2020-02-05 08:00 | 94.74 | 86.7
2020-02-05 08:30 | 95.31 | 87.77
2020-02-05 09:00 | 100.98 | 93
2020-02-05 09:30 | 101.3 | 94.51
2020-02-05 10:00 | 93.93 | 85.4
2020-02-05 10:30 | 88.07 | 77.55
2020-02-05 11:00 | 84.89 | 73.85
2020-02-05 11:30 | 90.88 | 79.66
2020-02-05 12:00 | 102.16 | 94.12
2020-02-05 12:30 | 97.13 | 87.57
2020-02-05 13:00 | 88.82 | 74.85
2020-02-05 13:30 | 85.85 | 71.2
2020-02-05 14:00 | 90.4 | 80.62
2020-02-05 14:30 | 95.46 | 87.97
2020-02-05 15:00 | 87.88 | 78.65
2020-02-05 15:30 | 90.9 | 80.75
2020-02-05 16:00 | 86.82 | 75.98
2020-02-05 16:30 | 87.27 | 79.06
2020-02-05 17:00 | 77.52 | 67.92
2020-02-05 17:30 | 80.34 | 71.7
2020-02-05 18:00 | 91.13 | 83
2020-02-05 18:30 | 94.88 | 88.07
2020-02-05 19:00 | 94.46 | 88.54
2020-02-05 19:30 | 92.02 | 85.13
2020-02-05 20:00 | 89.59 | 82.4
2020-02-05 20:30 | 90.38 | 82.14
2020-02-05 21:00 | 95.39 | 87.51
2020-02-05 21:30 | 95.66 | 85.84
2020-02-05 22:00 | 99.45 | 91.06
2020-02-05 22:30 | 95.17 | 86.55
2020-02-05 23:00 | 97.81 | 89.45
2020-02-05 23:30 | 92.51 | 82.51
2020-02-06 | 100.32 | 91.65
2020-02-06 00:30 | 96.23 | 87.33
2020-02-06 01:00 | 86.64 | 75.58
2020-02-06 01:30 | 84 | 71.72
2020-02-06 02:00 | 84.59 | 72.35
2020-02-06 02:30 | 90.07 | 79.72
2020-02-06 03:00 | 99.98 | 90.97
2020-02-06 03:30 | 97.8 | 88.07
2020-02-06 04:00 | 90.12 | 79.05
2020-02-06 04:30 | 95.36 | 84.58
2020-02-06 05:00 | 92.26 | 80.76
2020-02-06 05:30 | 88.67 | 76.99
2020-02-06 06:00 | 86.91 | 74.67
2020-02-06 06:30 | 83.32 | 69.72
2020-02-06 07:00 | 79.86 | 67.28
2020-02-06 07:30 | 76.79 | 63.49
2020-02-06 08:00 | 81.93 | 67.58
2020-02-06 08:30 | 82.3 | 67.2
2020-02-06 09:00 | 79.49 | 61.11
2020-02-06 09:30 | 80.02 | 59.38
2020-02-06 10:00 | 80.01 | 59.26
2020-02-06 10:30 | 80.16 | 62.08
2020-02-06 11:00 | 80.77 | 63.61
2020-02-06 11:30 | 79.45 | 60.81
2020-02-06 12:00 | 79.83 | 61.67
2020-02-06 12:30 | 81.71 | 60.88
2020-02-06 13:00 | 80.53 | 60.29
2020-02-06 13:30 | 90.23 | 74.18
2020-02-06 14:00 | 97.17 | 82.51
2020-02-06 14:30 | 90.09 | 74.78
2020-02-06 15:00 | 90.75 | 76.93
2020-02-06 15:30 | 91.33 | 76.57
2020-02-06 16:00 | 93.12 | 79.3
2020-02-06 16:30 | 92.06 | 79.75
2020-02-06 17:00 | 89.23 | 76.26
2020-02-06 17:30 | 88.83 | 77.67
2020-02-06 18:00 | 92 | 84.17
2020-02-06 18:30 | 88.87 | 82.46
2020-02-06 19:00 | 94.71 | 89.91
2020-02-06 19:30 | 97.8 | 93.97
2020-02-06 20:00 | 104.12 | 100.56
2020-02-06 20:30 | 110.74 | 107.32
2020-02-06 21:00 | 99.42 | 94.8
2020-02-06 21:30 | 94.41 | 90.08
2020-02-06 22:00 | 100.38 | 96.15
2020-02-06 22:30 | 107 | 102.46
2020-02-06 23:00 | 101.91 | 96.46
2020-02-06 23:30 | 107.94 | 102.96
2020-02-07 | 89.68 | 81.76
2020-02-07 00:30 | 91.68 | 84.77
2020-02-07 01:00 | 90.96 | 82.62
2020-02-07 01:30 | 94.95 | 86.04
2020-02-07 02:00 | 98.54 | 90.37
2020-02-07 02:30 | 99.14 | 91.55
2020-02-07 03:00 | 97.51 | 88.95
2020-02-07 03:30 | 100.32 | 91.83
2020-02-07 04:00 | 99.93 | 91.85
2020-02-07 04:30 | 101.43 | 93.78
2020-02-07 05:00 | 98.83 | 89.9
2020-02-07 05:30 | 100.6 | 92.96
2020-02-07 06:00 | 104.95 | 98.28
2020-02-07 06:30 | 97.34 | 89.51
2020-02-07 07:00 | 100.47 | 93.31
2020-02-07 07:30 | 97.21 | 88.64
2020-02-07 08:00 | 94.95 | 82.21
2020-02-07 08:30 | 94.44 | 83.3
2020-02-07 09:00 | 101.1 | 90.77
2020-02-07 09:30 | 100.57 | 90.14
2020-02-07 10:00 | 103.06 | 92.78
2020-02-07 10:30 | 97.33 | 84.89
2020-02-07 11:00 | 98.93 | 88.77
2020-02-07 11:30 | 99.11 | 88.38
2020-02-07 12:00 | 100.8 | 89.39
2020-02-07 12:30 | 108.49 | 100.38
2020-02-07 13:00 | 99.64 | 90.8
2020-02-07 13:30 | 101.8 | 95.04
2020-02-07 14:00 | 110.26 | 102.94
2020-02-07 14:30 | 103.07 | 93.77
2020-02-07 15:00 | 108.99 | 102.26
2020-02-07 15:30 | 102.48 | 93.95
2020-02-07 16:00 | 105.21 | 95.94
2020-02-07 16:30 | 104.37 | 94.14
2020-02-07 17:00 | 101.05 | 90.16
2020-02-07 17:30 | 101.66 | 93.02
2020-02-07 18:00 | 117.13 | 112.39
2020-02-07 18:30 | 111.27 | 106.55
2020-02-07 19:00 | 110.36 | 105.99
2020-02-07 19:30 | 108.09 | 103.78
2020-02-07 20:00 | 110.43 | 105.49
2020-02-07 20:30 | 111.01 | 106.46
2020-02-07 21:00 | 106.88 | 102.65
2020-02-07 21:30 | 106.77 | 101.82
2020-02-07 22:00 | 107.62 | 102.58
2020-02-07 22:30 | 109.35 | 103.61
2020-02-07 23:00 | 97.72 | 90.62
2020-02-07 23:30 | 101.72 | 95.05
2020-02-08 | 103.51 | 97.25
2020-02-08 00:30 | 104.39 | 97.88
2020-02-08 01:00 | 100.72 | 94.03
2020-02-08 01:30 | 103.68 | 96.98
2020-02-08 02:00 | 102.33 | 95.88
2020-02-08 02:30 | 99.85 | 92.91
2020-02-08 03:00 | 96.85 | 89.23
2020-02-08 03:30 | 98.2 | 91.73
2020-02-08 04:00 | 94.19 | 85.8
2020-02-08 04:30 | 93.25 | 84.89
2020-02-08 05:00 | 95.82 | 88.15
2020-02-08 05:30 | 91.79 | 83.85
2020-02-08 06:00 | 93.37 | 85.92
2020-02-08 06:30 | 97.89 | 91.34
2020-02-08 07:00 | 95.04 | 86.74
2020-02-08 07:30 | 97.63 | 88.08
2020-02-08 08:00 | 97.9 | 89.41
2020-02-08 08:30 | 95.1 | 86.39
2020-02-08 09:00 | 89.95 | 79.43
2020-02-08 09:30 | 96.88 | 88.66
2020-02-08 10:00 | 94.94 | 84.39
2020-02-08 10:30 | 92.51 | 82.77
2020-02-08 11:00 | 90.74 | 78.68
2020-02-08 11:30 | 89.96 | 77.33
2020-02-08 12:00 | 91.24 | 79.39
2020-02-08 12:30 | 90.7 | 78.12
2020-02-08 13:00 | 96.72 | 85.14
2020-02-08 13:30 | 99.98 | 90.01
2020-02-08 14:00 | 108.51 | 101.16
2020-02-08 14:30 | 115.29 | 110.6
2020-02-08 15:00 | 119.13 | 115.22
2020-02-08 15:30 | 103.27 | 93.69
2020-02-08 16:00 | 101.03 | 91.16
2020-02-08 16:30 | 103.05 | 95.86
2020-02-08 17:00 | 103.93 | 96.02
2020-02-08 17:30 | 105.71 | 99.69
2020-02-08 18:00 | 105.34 | 99.79
2020-02-08 18:30 | 105.82 | 101.97
2020-02-08 19:00 | 101.1 | 97.44
2020-02-08 19:30 | 102.43 | 98.93
2020-02-08 20:00 | 105.46 | 101.34
2020-02-08 20:30 | 112.97 | 108.84
2020-02-08 21:00 | 121.72 | 117.76
2020-02-08 21:30 | 109.77 | 105.84
2020-02-08 22:00 | 107.04 | 102.93
2020-02-08 22:30 | 104.27 | 100.09
2020-02-08 23:00 | 100.96 | 95.9
2020-02-08 23:30 | 102.37 | 97.75
2020-02-09 | 103.21 | 98.12
2020-02-09 00:30 | 106.87 | 102.49
2020-02-09 01:00 | 109.48 | 105.67
2020-02-09 01:30 | 111.98 | 107.94
2020-02-09 02:00 | 111.84 | 108.01
2020-02-09 02:30 | 105.17 | 101.7
2020-02-09 03:00 | 105.06 | 101.58
2020-02-09 03:30 | 107.82 | 103.31
2020-02-09 04:00 | 107.5 | 102.72
2020-02-09 04:30 | 103.62 | 98.62
2020-02-09 05:00 | 109.29 | 104.05
2020-02-09 05:30 | 107.71 | 102.54
2020-02-09 06:00 | 103.98 | 98.63
2020-02-09 06:30 | 100.86 | 94.78
2020-02-09 07:00 | 108.68 | 102.96
2020-02-09 07:30 | 89.23 | 80.47
2020-02-09 08:00 | 94.26 | 82
2020-02-09 08:30 | 91.69 | 76.78
2020-02-09 09:00 | 85.12 | 69.34
2020-02-09 09:30 | 98.01 | 83.67
2020-02-09 10:00 | 90.94 | 77.42
2020-02-09 10:30 | 98.84 | 83.57
2020-02-09 11:00 | 102.88 | 88.15
2020-02-09 11:30 | 87.17 | 71.8
2020-02-09 12:00 | 95.03 | 81.15
2020-02-09 12:30 | 90.62 | 77.33
2020-02-09 13:00 | 94.11 | 84.64
2020-02-09 13:30 | 97.11 | 87.54
2020-02-09 14:00 | 105.27 | 99.16
2020-02-09 14:30 | 108.76 | 103.47
2020-02-09 15:00 | 100.78 | 89.35
2020-02-09 15:30 | 97.11 | 84.25
2020-02-09 16:00 | 107.04 | 100.08
2020-02-09 16:30 | 105.29 | 95.77
2020-02-09 17:00 | 101.47 | 92.12
2020-02-09 17:30 | 101.89 | 92.94
2020-02-09 18:00 | 96.53 | 89.02
2020-02-09 18:30 | 99.05 | 93.2
2020-02-09 19:00 | 118.78 | 114.3
2020-02-09 19:30 | 121.48 | 116.63
2020-02-09 20:00 | 118.17 | 113.94
2020-02-09 20:30 | 119.98 | 116.21
2020-02-09 21:00 | 120.33 | 115.74
2020-02-09 21:30 | 120.1 | 115.02
2020-02-09 22:00 | 121.63 | 116.53
2020-02-09 22:30 | 115.53 | 110.78
2020-02-09 23:00 | 114.04 | 108.68
2020-02-09 23:30 | 111.69 | 106.93
2020-02-10 | 98.9 | 93.72
2020-02-10 00:30 | 106.47 | 101.46
2020-02-10 01:00 | 108.58 | 103.7
2020-02-10 01:30 | 107.43 | 102.95
2020-02-10 02:00 | 118.05 | 113.47
2020-02-10 02:30 | 111.35 | 106.46
2020-02-10 03:00 | 116.36 | 111.48
2020-02-10 03:30 | 116.62 | 111.83
2020-02-10 04:00 | 116.92 | 112.2
2020-02-10 04:30 | 117.19 | 112.85
2020-02-10 05:00 | 108.04 | 103.01
2020-02-10 05:30 | 109.97 | 105.62
2020-02-10 06:00 | 101.68 | 96.67
2020-02-10 06:30 | 96.24 | 90.45
2020-02-10 07:00 | 97.1 | 90.35
2020-02-10 07:30 | 91.61 | 81.84
2020-02-10 08:00 | 99.01 | 90.35
2020-02-10 08:30 | 99.03 | 90.05
2020-02-10 09:00 | 98.67 | 85.13
2020-02-10 09:30 | 93.72 | 79.59
2020-02-10 10:00 | 104.22 | 91.59
2020-02-10 10:30 | 108.08 | 96.06
2020-02-10 11:00 | 108.33 | 95.25
2020-02-10 11:30 | 98.55 | 86.45
2020-02-10 12:00 | 95.76 | 83.81
2020-02-10 12:30 | 91.28 | 77.19
2020-02-10 13:00 | 91.38 | 78.29
2020-02-10 13:30 | 89.44 | 72.42
2020-02-10 14:00 | 84.15 | 69.31
2020-02-10 14:30 | 90.08 | 74.88
2020-02-10 15:00 | 103.05 | 87.26
2020-02-10 15:30 | 106.5 | 90.12
2020-02-10 16:00 | 106.54 | 96.14
2020-02-10 16:30 | 90.88 | 79.66
2020-02-10 17:00 | 58.42 | 41.55
2020-02-10 17:30 | 70.79 | 62.28
2020-02-10 18:00 | 80.86 | 74.33
2020-02-10 18:30 | 79.35 | 73.29
2020-02-10 19:00 | 86.1 | 81.49
2020-02-10 19:30 | 91.27 | 87.12
2020-02-10 20:00 | 88.31 | 84.75
2020-02-10 20:30 | 86.71 | 82.75
2020-02-10 21:00 | 87.35 | 83.44
2020-02-10 21:30 | 87.23 | 83.07
2020-02-10 22:00 | 79.18 | 72.8
2020-02-10 22:30 | 84.21 | 77.11
2020-02-10 23:00 | 83.1 | 73.08
2020-02-10 23:30 | 84.51 | 74.64
2020-02-11 | 86.62 | 77.36
2020-02-11 00:30 | 90.26 | 82.17
2020-02-11 01:00 | 91.37 | 82.2
2020-02-11 01:30 | 85.11 | 75.92
2020-02-11 02:00 | 74.22 | 65
2020-02-11 02:30 | 74.93 | 63.49
2020-02-11 03:00 | 86.97 | 78.25
2020-02-11 03:30 | 86.81 | 78.65
2020-02-11 04:00 | 91.54 | 83.62
2020-02-11 04:30 | 86.58 | 77.88
2020-02-11 05:00 | 87.37 | 79.15
2020-02-11 05:30 | 86.6 | 78.83
2020-02-11 06:00 | 83.45 | 73.22
2020-02-11 06:30 | 84.05 | 74.76
2020-02-11 07:00 | 87.39 | 78.53
2020-02-11 07:30 | 85.88 | 75.08
2020-02-11 08:00 | 76.07 | 60.1
2020-02-11 08:30 | 69.33 | 46.75
2020-02-11 09:00 | 67.68 | 43.81
2020-02-11 09:30 | 70.19 | 45.12
2020-02-11 10:00 | 69.73 | 46.12
2020-02-11 10:30 | 65.25 | 38.22
2020-02-11 11:00 | 70.11 | 48.72
2020-02-11 11:30 | 73.85 | 55.47
2020-02-11 12:00 | 72.83 | 51.27
2020-02-11 12:30 | 76.27 | 54.67
2020-02-11 13:00 | 77.46 | 57.41
2020-02-11 13:30 | 64.67 | 38.09
2020-02-11 14:00 | 65.47 | 39.96
2020-02-11 14:30 | 73.14 | 52.8
2020-02-11 15:00 | 78.11 | 60.81
2020-02-11 15:30 | 75.6 | 54.38
2020-02-11 16:00 | 84.25 | 68
2020-02-11 16:30 | 85.86 | 72.84
2020-02-11 17:00 | 99.24 | 89.99
2020-02-11 17:30 | 97.34 | 89.29
2020-02-11 18:00 | 95.77 | 87.88
2020-02-11 18:30 | 99.58 | 92.97
2020-02-11 19:00 | 102.03 | 96.24
2020-02-11 19:30 | 100.25 | 94.72
2020-02-11 20:00 | 106.9 | 101.08
2020-02-11 20:30 | 97.32 | 90.9
2020-02-11 21:00 | 93.54 | 86.58
2020-02-11 21:30 | 94.93 | 87.66
2020-02-11 22:00 | 103.13 | 96.69
2020-02-11 22:30 | 100.81 | 93.92
2020-02-11 23:00 | 102.84 | 96.7
2020-02-11 23:30 | 109.37 | 103.3
2020-02-12 | 105.76 | 100.24
2020-02-12 00:30 | 106.19 | 100.68
2020-02-12 01:00 | 105.25 | 99.52
2020-02-12 01:30 | 99.56 | 93.7
2020-02-12 02:00 | 97.68 | 91.15
2020-02-12 02:30 | 98.56 | 91.69
2020-02-12 03:00 | 95.88 | 88.64
2020-02-12 03:30 | 93.56 | 86.17
2020-02-12 04:00 | 93.13 | 86.43
2020-02-12 04:30 | 95.19 | 88.48
2020-02-12 05:00 | 93.07 | 85.99
2020-02-12 05:30 | 95.59 | 89.32
2020-02-12 06:00 | 96.99 | 90.33
2020-02-12 06:30 | 84.02 | 75.38
2020-02-12 07:00 | 79.62 | 67.72
2020-02-12 07:30 | 74.9 | 60.7
2020-02-12 08:00 | 75.52 | 60.79
2020-02-12 08:30 | 79.13 | 64.56
2020-02-12 09:00 | 79.99 | 66.68
2020-02-12 09:30 | 82.73 | 69.67
2020-02-12 10:00 | 84.66 | 73.16
2020-02-12 10:30 | 77.78 | 63.6
2020-02-12 11:00 | 88.91 | 75.33
2020-02-12 11:30 | 83.57 | 68.22
2020-02-12 12:00 | 89.8 | 75.73
2020-02-12 12:30 | 95.21 | 86.05
2020-02-12 13:00 | 88.63 | 75.94
2020-02-12 13:30 | 87.38 | 74.45
2020-02-12 14:00 | 87.61 | 73.99
2020-02-12 14:30 | 101.18 | 90.3
2020-02-12 15:00 | 96.14 | 88.67
2020-02-12 15:30 | 99.38 | 91.61
2020-02-12 16:00 | 92.92 | 80.62
2020-02-12 16:30 | 92.44 | 79.67
2020-02-12 17:00 | 96.25 | 85.04
2020-02-12 17:30 | 102.95 | 93.49
2020-02-12 18:00 | 109.27 | 101.55
2020-02-12 18:30 | 113.09 | 105.65
2020-02-12 19:00 | 104.27 | 98.76
2020-02-12 19:30 | 108.11 | 102.78
2020-02-12 20:00 | 103.97 | 98.46
2020-02-12 20:30 | 104 | 98.77
2020-02-12 21:00 | 119.15 | 112.66
2020-02-12 21:30 | 116.71 | 110.34
2020-02-12 22:00 | 110.17 | 104.44
2020-02-12 22:30 | 118.65 | 113.06
2020-02-12 23:00 | 119.43 | 114.05
2020-02-12 23:30 | 115.6 | 109.7
2020-02-13 | 113.95 | 107.76
2020-02-13 00:30 | 110.01 | 103.44
2020-02-13 01:00 | 110.61 | 104.64
2020-02-13 01:30 | 115.75 | 110.33
2020-02-13 02:00 | 112.51 | 106.73
2020-02-13 02:30 | 107.73 | 102.18
2020-02-13 03:00 | 107.33 | 101.9
2020-02-13 03:30 | 108.47 | 102.36
2020-02-13 04:00 | 105.8 | 99.58
2020-02-13 04:30 | 104.62 | 98.21
2020-02-13 05:00 | 99.67 | 93.95
2020-02-13 05:30 | 103.97 | 98.06
2020-02-13 06:00 | 100.79 | 94.96
2020-02-13 06:30 | 93.74 | 86.72
2020-02-13 07:00 | 92.06 | 83.27
2020-02-13 07:30 | 94.17 | 84.34
2020-02-13 08:00 | 92.09 | 79.29
2020-02-13 08:30 | 89 | 73.07
2020-02-13 09:00 | 82.23 | 64.85
2020-02-13 09:30 | 92.11 | 75.76
2020-02-13 10:00 | 92.54 | 75.88
2020-02-13 10:30 | 96.36 | 86.86
2020-02-13 11:00 | 101.4 | 95.68
2020-02-13 11:30 | 104.41 | 96.21
2020-02-13 12:00 | 122.76 | 116.42
2020-02-13 12:30 | 125.33 | 118.82
2020-02-13 13:00 | 127.34 | 120.28
2020-02-13 13:30 | 133.63 | 126.76
2020-02-13 14:00 | 139.27 | 132.2
2020-02-13 14:30 | 135.02 | 127.74
2020-02-13 15:00 | 133.59 | 126.4
2020-02-13 15:30 | 122.61 | 115.84
2020-02-13 16:00 | 116.63 | 109.86
2020-02-13 16:30 | 113.28 | 106.88
2020-02-13 17:00 | 105.3 | 96.63
2020-02-13 17:30 | 104.51 | 96.64
2020-02-13 18:00 | 107.78 | 101.94
2020-02-13 18:30 | 101.11 | 94.73
2020-02-13 19:00 | 113.85 | 109.55
2020-02-13 19:30 | 107.35 | 102.52
2020-02-13 20:00 | 100.5 | 95.13
2020-02-13 20:30 | 102.73 | 96.64
2020-02-13 21:00 | 105.6 | 100.33
2020-02-13 21:30 | 98.83 | 92.38
2020-02-13 22:00 | 105.31 | 98.66
2020-02-13 22:30 | 101.87 | 94.02
2020-02-13 23:00 | 111.23 | 105.01
2020-02-13 23:30 | 107.46 | 100.51
2020-02-14 | 103.24 | 95.91
2020-02-14 00:30 | 100.09 | 92.97
2020-02-14 01:00 | 100.8 | 93.69
2020-02-14 01:30 | 102.87 | 95.77
2020-02-14 02:00 | 103.18 | 95.72
2020-02-14 02:30 | 103.07 | 95.16
2020-02-14 03:00 | 101.24 | 93.11
2020-02-14 03:30 | 102.31 | 93.97
2020-02-14 04:00 | 99.51 | 90.75
2020-02-14 04:30 | 104.26 | 96.94
2020-02-14 05:00 | 108.58 | 101.93
2020-02-14 05:30 | 99.79 | 92.22
2020-02-14 06:00 | 106.83 | 100.1
2020-02-14 06:30 | 101.25 | 93.23
2020-02-14 07:00 | 102.84 | 93.94
2020-02-14 07:30 | 95.32 | 83.52
2020-02-14 08:00 | 90.76 | 77.2
2020-02-14 08:30 | 93.25 | 77.65
2020-02-14 09:00 | 97.15 | 81.72
2020-02-14 09:30 | 92.75 | 77.94
2020-02-14 10:00 | 91.45 | 76.21
2020-02-14 10:30 | 94.36 | 79.73
2020-02-14 11:00 | 88.37 | 73.03
2020-02-14 11:30 | 93.04 | 75.91
2020-02-14 12:00 | 99.52 | 82.95
2020-02-14 12:30 | 105.99 | 93.43
2020-02-14 13:00 | 104.34 | 91.52
2020-02-14 13:30 | 104.96 | 91.29
2020-02-14 14:00 | 99.95 | 84.74
2020-02-14 14:30 | 103.93 | 92.08
2020-02-14 15:00 | 108.28 | 99.74
2020-02-14 15:30 | 113.86 | 99.83
2020-02-14 16:00 | 116.42 | 101.02
2020-02-14 16:30 | 114.22 | 97.64
2020-02-14 17:00 | 103.1 | 75.58
2020-02-14 17:30 | 96.73 | 69.13
2020-02-14 18:00 | 99.56 | 79.84
2020-02-14 18:30 | 97.37 | 80.37
2020-02-14 19:00 | 100.68 | 83.85
2020-02-14 19:30 | 106.75 | 91.31
2020-02-14 20:00 | 111.35 | 96.34
2020-02-14 20:30 | 114.51 | 100.22
2020-02-14 21:00 | 109.52 | 93.99
2020-02-14 21:30 | 114.69 | 100.46
2020-02-14 22:00 | 118.68 | 104.55
2020-02-14 22:30 | 113.72 | 97.4
2020-02-14 23:00 | 112.62 | 95.37
2020-02-14 23:30 | 114.99 | 97.31
2020-02-15 | 115.34 | 98.28
2020-02-15 00:30 | 114.51 | 98.8
2020-02-15 01:00 | 117.54 | 102.11
2020-02-15 01:30 | 118.06 | 102.16
2020-02-15 02:00 | 114.97 | 98.48
2020-02-15 02:30 | 116.38 | 99.87
2020-02-15 03:00 | 120.97 | 105.23
2020-02-15 03:30 | 116.4 | 98.97
2020-02-15 04:00 | 121.75 | 107
2020-02-15 04:30 | 111.08 | 91
2020-02-15 05:00 | 110.81 | 89.77
2020-02-15 05:30 | 108.03 | 86.73
2020-02-15 06:00 | 107.99 | 86.55
2020-02-15 06:30 | 110.02 | 89.47
2020-02-15 07:00 | 105.6 | 80.43
2020-02-15 07:30 | 106.4 | 78.19
2020-02-15 08:00 | 100.31 | 66.99
2020-02-15 08:30 | 97.81 | 63.46
2020-02-15 09:00 | 99.52 | 63.5
2020-02-15 09:30 | 94.83 | 59.42
2020-02-15 10:00 | 94.49 | 57.6
2020-02-15 10:30 | 95.19 | 61.89
2020-02-15 11:00 | 95.54 | 60.4
2020-02-15 11:30 | 92.34 | 54.3
2020-02-15 12:00 | 92.01 | 53.6
2020-02-15 12:30 | 93.7 | 56.24
2020-02-15 13:00 | 96.16 | 64.58
2020-02-15 13:30 | 100.4 | 67.98
2020-02-15 14:00 | 101.44 | 71.59
2020-02-15 14:30 | 101.07 | 70.48
2020-02-15 15:00 | 100.96 | 71.82
2020-02-15 15:30 | 105.85 | 77.94
2020-02-15 16:00 | 104.84 | 80.52
2020-02-15 16:30 | 105 | 81.88
2020-02-15 17:00 | 101.94 | 75.16
2020-02-15 17:30 | 111.39 | 91.26
2020-02-15 18:00 | 112.93 | 97.12
2020-02-15 18:30 | 108.81 | 95.17
2020-02-15 19:00 | 121.69 | 110.6
2020-02-15 19:30 | 119.38 | 108.87
2020-02-15 20:00 | 121.67 | 111.17
2020-02-15 20:30 | 127.46 | 117.67
2020-02-15 21:00 | 126.09 | 115.08
2020-02-15 21:30 | 118.7 | 105.67
2020-02-15 22:00 | 116.59 | 102.34
2020-02-15 22:30 | 122.21 | 107.84
2020-02-15 23:00 | 124.3 | 110.15
2020-02-15 23:30 | 117.26 | 100.11
2020-02-16 | 118.22 | 101.03
2020-02-16 00:30 | 113.37 | 96.31
2020-02-16 01:00 | 118.33 | 103.78
2020-02-16 01:30 | 124.25 | 108.99
2020-02-16 02:00 | 131.03 | 117.28
2020-02-16 02:30 | 124.89 | 110.05
2020-02-16 03:00 | 119.15 | 103.6
2020-02-16 03:30 | 114.74 | 96.81
2020-02-16 04:00 | 125.94 | 110.63
2020-02-16 04:30 | 122.45 | 107.23
2020-02-16 05:00 | 126.45 | 110.86
2020-02-16 05:30 | 132.33 | 118.77
2020-02-16 06:00 | 127.99 | 113.48
2020-02-16 06:30 | 113.31 | 94.34
2020-02-16 07:00 | 112.42 | 92.57
2020-02-16 07:30 | 113.25 | 91.98
2020-02-16 08:00 | 114.61 | 93.35
2020-02-16 08:30 | 107.4 | 82.68
2020-02-16 09:00 | 97.2 | 68.94
2020-02-16 09:30 | 98.43 | 70.73
2020-02-16 10:00 | 97.2 | 69.1
2020-02-16 10:30 | 97.52 | 68.73
2020-02-16 11:00 | 98.62 | 69.89
2020-02-16 11:30 | 102.39 | 75.09
2020-02-16 12:00 | 106.02 | 80.01
2020-02-16 12:30 | 101.65 | 74.18
2020-02-16 13:00 | 98.3 | 70.8
2020-02-16 13:30 | 100.61 | 73.36
2020-02-16 14:00 | 104.09 | 78.53
2020-02-16 14:30 | 107.87 | 83.23
2020-02-16 15:00 | 108.45 | 83.36
2020-02-16 15:30 | 111.62 | 86.01
2020-02-16 16:00 | 104.34 | 78.32
2020-02-16 16:30 | 104.69 | 79.1
2020-02-16 17:00 | 108.81 | 86.42
2020-02-16 17:30 | 116.05 | 97.82
2020-02-16 18:00 | 119.36 | 104.97
2020-02-16 18:30 | 115.74 | 101.4
2020-02-16 19:00 | 121.47 | 108.81
2020-02-16 19:30 | 123.94 | 112.09
2020-02-16 20:00 | 118.45 | 105.12
2020-02-16 20:30 | 113.93 | 99.49
2020-02-16 21:00 | 113.93 | 99.13
2020-02-16 21:30 | 113.66 | 97.95
2020-02-16 22:00 | 113.76 | 96.56
2020-02-16 22:30 | 122.33 | 107.03
2020-02-16 23:00 | 116.56 | 101.32
2020-02-16 23:30 | 112.36 | 94.23
2020-02-17 | 119.68 | 104.74
2020-02-17 00:30 | 119.89 | 106.04
2020-02-17 01:00 | 117.89 | 102.8
2020-02-17 01:30 | 113.65 | 96.23
2020-02-17 02:00 | 112.56 | 94.36
2020-02-17 02:30 | 112.18 | 94.42
2020-02-17 03:00 | 112.52 | 95.45
2020-02-17 03:30 | 108 | 88.63
2020-02-17 04:00 | 110.55 | 92.16
2020-02-17 04:30 | 117.08 | 101.68
2020-02-17 05:00 | 112.87 | 95.71
2020-02-17 05:30 | 109.82 | 91.16
2020-02-17 06:00 | 109.9 | 90.71
2020-02-17 06:30 | 104.25 | 81.82
2020-02-17 07:00 | 106.57 | 86.68
2020-02-17 07:30 | 108.32 | 87.1
2020-02-17 08:00 | 111.87 | 90.74
2020-02-17 08:30 | 116.9 | 97.52
2020-02-17 09:00 | 110.02 | 85.55
2020-02-17 09:30 | 110 | 85.41
2020-02-17 10:00 | 114.57 | 92.21
2020-02-17 10:30 | 112.24 | 86.47
2020-02-17 11:00 | 110.37 | 81.5
2020-02-17 11:30 | 112.31 | 83.91
2020-02-17 12:00 | 108.5 | 80.88
2020-02-17 12:30 | 110.67 | 88.66
2020-02-17 13:00 | 111.59 | 88.4
2020-02-17 13:30 | 112.72 | 87.83
2020-02-17 14:00 | 112.55 | 88.03
2020-02-17 14:30 | 112.68 | 87.43
2020-02-17 15:00 | 119.45 | 99.83
2020-02-17 15:30 | 113.33 | 90.28
2020-02-17 16:00 | 112.71 | 88.25
2020-02-17 16:30 | 116.13 | 95.78
2020-02-17 17:00 | 116.57 | 97.17
2020-02-17 17:30 | 119.56 | 102.18
2020-02-17 18:00 | 123.88 | 110.82
2020-02-17 18:30 | 117.46 | 104.53
2020-02-17 19:00 | 134.66 | 125.67
2020-02-17 19:30 | 131 | 121.78
2020-02-17 20:00 | 131.67 | 122.8
2020-02-17 20:30 | 126.31 | 116.09
2020-02-17 21:00 | 121.04 | 108.51
2020-02-17 21:30 | 124.06 | 112.67
2020-02-17 22:00 | 123.94 | 110.32
2020-02-17 22:30 | 125.28 | 111.22
2020-02-17 23:00 | 123.78 | 111.12
2020-02-17 23:30 | 121.82 | 109.01
2020-02-18 | 119.79 | 106.71
2020-02-18 00:30 | 125.37 | 112.94
2020-02-18 01:00 | 122.36 | 110.1
2020-02-18 01:30 | 118.6 | 106.26
2020-02-18 02:00 | 114.65 | 100.28
2020-02-18 02:30 | 115.84 | 101.25
2020-02-18 03:00 | 114.02 | 99.03
2020-02-18 03:30 | 117.47 | 101.26
2020-02-18 04:00 | 118.05 | 103.58
2020-02-18 04:30 | 111.01 | 95.03
2020-02-18 05:00 | 114.66 | 99.48
2020-02-18 05:30 | 113.12 | 98.32
2020-02-18 06:00 | 116.05 | 101.46
2020-02-18 06:30 | 109.59 | 93.39
2020-02-18 07:00 | 114.73 | 99.82
2020-02-18 07:30 | 113.53 | 94.7
2020-02-18 08:00 | 108.11 | 84.93
2020-02-18 08:30 | 113.93 | 96.12
2020-02-18 09:00 | 113.68 | 95.17
2020-02-18 09:30 | 111.04 | 92.42
2020-02-18 10:00 | 113.63 | 92.74
2020-02-18 10:30 | 113.15 | 90.55
2020-02-18 11:00 | 113.25 | 91.65
2020-02-18 11:30 | 109.07 | 84.13
2020-02-18 12:00 | 109.6 | 86.38
2020-02-18 12:30 | 109.34 | 87.06
2020-02-18 13:00 | 109.66 | 88.11
2020-02-18 13:30 | 102.34 | 77.68
2020-02-18 14:00 | 107.01 | 83.39
2020-02-18 14:30 | 106.19 | 82.47
2020-02-18 15:00 | 104.29 | 81.33
2020-02-18 15:30 | 103.15 | 78.52
2020-02-18 16:00 | 102.8 | 77.18
2020-02-18 16:30 | 105.03 | 84.92
2020-02-18 17:00 | 99.77 | 77.42
2020-02-18 17:30 | 109.82 | 92.05
2020-02-18 18:00 | 117.2 | 104.51
2020-02-18 18:30 | 113.98 | 103.19
2020-02-18 19:00 | 118.25 | 107.88
2020-02-18 19:30 | 120.55 | 111.99
2020-02-18 20:00 | 122.53 | 112.39
2020-02-18 20:30 | 122.95 | 113.37
2020-02-18 21:00 | 126.86 | 116.56
2020-02-18 21:30 | 124.13 | 113.28
2020-02-18 22:00 | 117.67 | 104.07
2020-02-18 22:30 | 117.78 | 104.45
2020-02-18 23:00 | 117.15 | 101.53
2020-02-18 23:30 | 116.33 | 100.73
2020-02-19 | 121.04 | 107.95
2020-02-19 00:30 | 114.21 | 101.04
2020-02-19 01:00 | 114.74 | 100.95
2020-02-19 01:30 | 115.47 | 102.62
2020-02-19 02:00 | 108.84 | 93.79
2020-02-19 02:30 | 113.46 | 99.78
2020-02-19 03:00 | 114.19 | 99.86
2020-02-19 03:30 | 109.73 | 93.29
2020-02-19 04:00 | 107.41 | 92.43
2020-02-19 04:30 | 111.48 | 98.18
2020-02-19 05:00 | 114.36 | 100.61
2020-02-19 05:30 | 116.83 | 103.79
2020-02-19 06:00 | 112.44 | 97.76
2020-02-19 06:30 | 103.46 | 86.92
2020-02-19 07:00 | 103.78 | 86.76
2020-02-19 07:30 | 105.31 | 87.48
2020-02-19 08:00 | 108.45 | 92.44
2020-02-19 08:30 | 98.61 | 78.79
2020-02-19 09:00 | 93.98 | 70.89
2020-02-19 09:30 | 90.64 | 66.77
2020-02-19 10:00 | 92.78 | 65.23
2020-02-19 10:30 | 100.94 | 77.56
2020-02-19 11:00 | 96.24 | 70.66
2020-02-19 11:30 | 95.11 | 68.7
2020-02-19 12:00 | 98.88 | 72.68
2020-02-19 12:30 | 97.94 | 69.33
2020-02-19 13:00 | 94.5 | 63.2
2020-02-19 13:30 | 96.54 | 69.71
2020-02-19 14:00 | 98.06 | 70.15
2020-02-19 14:30 | 96.45 | 73.27
2020-02-19 15:00 | 102.22 | 84.13
2020-02-19 15:30 | 105.39 | 87.84
2020-02-19 16:00 | 102.69 | 83.95
2020-02-19 16:30 | 93.62 | 63.68
2020-02-19 17:00 | 97.42 | 72.01
2020-02-19 17:30 | 99.74 | 78.43
2020-02-19 18:00 | 106.84 | 90.29
2020-02-19 18:30 | 104.27 | 88.52
2020-02-19 19:00 | 113.75 | 99.53
2020-02-19 19:30 | 111.11 | 94.96
2020-02-19 20:00 | 106.96 | 90.57
2020-02-19 20:30 | 106.46 | 89.1
2020-02-19 21:00 | 103.21 | 84.27
2020-02-19 21:30 | 105.03 | 85.8
2020-02-19 22:00 | 106.65 | 87.68
2020-02-19 22:30 | 107.06 | 86.18
2020-02-19 23:00 | 106.7 | 86.46
2020-02-19 23:30 | 105.25 | 87.01
2020-02-20 | 106.48 | 88.8
2020-02-20 00:30 | 100.41 | 82.84
2020-02-20 01:00 | 102.93 | 84.56
2020-02-20 01:30 | 100.57 | 83.35
2020-02-20 02:00 | 102.02 | 84.34
2020-02-20 02:30 | 100.03 | 82.69
2020-02-20 03:00 | 102.94 | 86.46
2020-02-20 03:30 | 104.91 | 85.47
2020-02-20 04:00 | 105.54 | 87.67
2020-02-20 04:30 | 103.32 | 85.31
2020-02-20 05:00 | 107.3 | 89.86
2020-02-20 05:30 | 105.41 | 87.68
2020-02-20 06:00 | 101.63 | 81.88
2020-02-20 06:30 | 92.96 | 71.51
2020-02-20 07:00 | 96.74 | 75.87
2020-02-20 07:30 | 100.71 | 77.57
2020-02-20 08:00 | 96.81 | 68.97
2020-02-20 08:30 | 92.32 | 57.61
2020-02-20 09:00 | 94.53 | 60.62
2020-02-20 09:30 | 97.54 | 63.51
2020-02-20 10:00 | 101.37 | 68.1
2020-02-20 10:30 | 103.65 | 70.24
2020-02-20 11:00 | 97.41 | 59.27
2020-02-20 11:30 | 97.14 | 65.69
2020-02-20 12:00 | 102.02 | 69.48
2020-02-20 12:30 | 96.85 | 60.17
2020-02-20 13:00 | 102 | 68.71
2020-02-20 13:30 | 98.88 | 64.54
2020-02-20 14:00 | 96.07 | 59.22
2020-02-20 14:30 | 100.11 | 64.76
2020-02-20 15:00 | 107 | 77.64
2020-02-20 15:30 | 106.08 | 76.14
2020-02-20 16:00 | 106.38 | 80.27
2020-02-20 16:30 | 110.42 | 86.85
2020-02-20 17:00 | 113.65 | 96.71
2020-02-20 17:30 | 121.36 | 108.41
2020-02-20 18:00 | 116.41 | 104.57
2020-02-20 18:30 | 115.36 | 103.94
2020-02-20 19:00 | 120.39 | 110.37
2020-02-20 19:30 | 122.44 | 113.15
2020-02-20 20:00 | 121.7 | 113.24
2020-02-20 20:30 | 126.96 | 117.6
2020-02-20 21:00 | 122.4 | 112.04
2020-02-20 21:30 | 132.39 | 124.39
2020-02-20 22:00 | 129.7 | 120.09
2020-02-20 22:30 | 113.83 | 105.51
2020-02-20 23:00 | 113.43 | 108.84
2020-02-20 23:30 | 108.18 | 102.79
2020-02-21 | 110.02 | 104.19
2020-02-21 00:30 | 107.9 | 102.28
2020-02-21 01:00 | 103.61 | 96.45
2020-02-21 01:30 | 105.1 | 98.09
2020-02-21 02:00 | 109.69 | 102.61
2020-02-21 02:30 | 112.36 | 105.56
2020-02-21 03:00 | 107.09 | 99.23
2020-02-21 03:30 | 112.58 | 105.14
2020-02-21 04:00 | 108.97 | 101.78
2020-02-21 04:30 | 108.14 | 100.74
2020-02-21 05:00 | 112.16 | 105.2
2020-02-21 05:30 | 111.12 | 104.4
2020-02-21 06:00 | 110.64 | 103.48
2020-02-21 06:30 | 100.8 | 92.67
2020-02-21 07:00 | 106.07 | 98.23
2020-02-21 07:30 | 107.19 | 98.93
2020-02-21 08:00 | 99.82 | 89.82
2020-02-21 08:30 | 97.88 | 86.78
2020-02-21 09:00 | 97.43 | 84.06
2020-02-21 09:30 | 88.22 | 70.15
2020-02-21 10:00 | 95.26 | 78
2020-02-21 10:30 | 97.84 | 83.5
2020-02-21 11:00 | 90.1 | 75.06
2020-02-21 11:30 | 92.43 | 77.4
2020-02-21 12:00 | 96.01 | 82.87
2020-02-21 12:30 | 97.19 | 84.26
2020-02-21 13:00 | 97.71 | 83.2
2020-02-21 13:30 | 92.12 | 78.29
2020-02-21 14:00 | 98.05 | 86.18
2020-02-21 14:30 | 102.12 | 89.07
2020-02-21 15:00 | 95.76 | 82.08
2020-02-21 15:30 | 100.16 | 86.74
2020-02-21 16:00 | 102.86 | 92.8
2020-02-21 16:30 | 95.87 | 85.34
2020-02-21 17:00 | 110.05 | 102.82
2020-02-21 17:30 | 105.13 | 96.81
2020-02-21 18:00 | 115.61 | 109.33
2020-02-21 18:30 | 106.56 | 98.34
2020-02-21 19:00 | 112.27 | 106.12
2020-02-21 19:30 | 112.32 | 106.63
2020-02-21 20:00 | 110.33 | 104.54
2020-02-21 20:30 | 109.96 | 103.59
2020-02-21 21:00 | 105.01 | 98.41
2020-02-21 21:30 | 105.27 | 98.37
2020-02-21 22:00 | 102.34 | 93.51
2020-02-21 22:30 | 98.67 | 90.08
2020-02-21 23:00 | 102.24 | 93.52
2020-02-21 23:30 | 106.23 | 96.52
2020-02-22 | 106.32 | 95.95
2020-02-22 00:30 | 106.84 | 96.29
2020-02-22 01:00 | 105.42 | 93.77
2020-02-22 01:30 | 104.97 | 93.49
2020-02-22 02:00 | 105.89 | 94.47
2020-02-22 02:30 | 111.33 | 101.17
2020-02-22 03:00 | 108.9 | 98.97
2020-02-22 03:30 | 105.91 | 95.1
2020-02-22 04:00 | 101.4 | 91.18
2020-02-22 04:30 | 106.56 | 95.73
2020-02-22 05:00 | 107.47 | 96.02
2020-02-22 05:30 | 110.24 | 100.03
2020-02-22 06:00 | 109.85 | 100.37
2020-02-22 06:30 | 103.91 | 92.71
2020-02-22 07:00 | 102.3 | 90.74
2020-02-22 07:30 | 102.04 | 89.56
2020-02-22 08:00 | 99.44 | 86.42
2020-02-22 08:30 | 97.63 | 83.86
2020-02-22 09:00 | 94.74 | 81.3
2020-02-22 09:30 | 92.86 | 74.22
2020-02-22 10:00 | 93.61 | 78.87
2020-02-22 10:30 | 96.68 | 83.27
2020-02-22 11:00 | 97.58 | 84.21
2020-02-22 11:30 | 98.09 | 85.4
2020-02-22 12:00 | 98.9 | 85.91
2020-02-22 12:30 | 100.67 | 87.08
2020-02-22 13:00 | 103.54 | 89.05
2020-02-22 13:30 | 102.82 | 90.37
2020-02-22 14:00 | 94.26 | 77.67
2020-02-22 14:30 | 98.97 | 83.04
2020-02-22 15:00 | 99.41 | 84.64
2020-02-22 15:30 | 95.51 | 79.49
2020-02-22 16:00 | 99.95 | 87.6
2020-02-22 16:30 | 93.16 | 81.3
2020-02-22 17:00 | 97.15 | 86.95
2020-02-22 17:30 | 99.82 | 88.77
2020-02-22 18:00 | 98.04 | 88.11
2020-02-22 18:30 | 96.45 | 84.93
2020-02-22 19:00 | 99.17 | 89.63
2020-02-22 19:30 | 98.79 | 89.8
2020-02-22 20:00 | 92.89 | 83.35
2020-02-22 20:30 | 98.16 | 88.76
2020-02-22 21:00 | 91.82 | 81
2020-02-22 21:30 | 97.61 | 86.16
2020-02-22 22:00 | 97.62 | 86.68
2020-02-22 22:30 | 104.5 | 94.45
2020-02-22 23:00 | 98 | 87.97
2020-02-22 23:30 | 91.83 | 79.46
2020-02-23 | 91.61 | 79.65
2020-02-23 00:30 | 91.78 | 81.13
2020-02-23 01:00 | 95.05 | 85.76
2020-02-23 01:30 | 90.52 | 79.36
2020-02-23 02:00 | 93.78 | 82.41
2020-02-23 02:30 | 91.34 | 78.36
2020-02-23 03:00 | 93.61 | 81.46
2020-02-23 03:30 | 94.94 | 83.49
2020-02-23 04:00 | 99.53 | 88.48
2020-02-23 04:30 | 102.17 | 91.52
2020-02-23 05:00 | 92.84 | 80.35
2020-02-23 05:30 | 87.28 | 72.28
2020-02-23 06:00 | 92.2 | 79.67
2020-02-23 06:30 | 85.24 | 71.27
2020-02-23 07:00 | 89.34 | 76.63
2020-02-23 07:30 | 86.55 | 74.96
2020-02-23 08:00 | 85.49 | 75.24
2020-02-23 08:30 | 87.95 | 76.9
2020-02-23 09:00 | 88.24 | 78.27
2020-02-23 09:30 | 87.92 | 77.32
2020-02-23 10:00 | 85.86 | 72.43
2020-02-23 10:30 | 88.01 | 74.5
2020-02-23 11:00 | 84.67 | 69.11
2020-02-23 11:30 | 78.73 | 61.38
2020-02-23 12:00 | 83.44 | 69.45
2020-02-23 12:30 | 80.92 | 65.04
2020-02-23 13:00 | 83.27 | 68.52
2020-02-23 13:30 | 85.72 | 73.82
2020-02-23 14:00 | 89.66 | 80.19
2020-02-23 14:30 | 92.14 | 83.21
2020-02-23 15:00 | 96.13 | 87.53
2020-02-23 15:30 | 96.11 | 86.69
2020-02-23 16:00 | 88.23 | 77.04
2020-02-23 16:30 | 98.99 | 89.82
2020-02-23 17:00 | 97.62 | 88.73
2020-02-23 17:30 | 102.61 | 94.75
2020-02-23 18:00 | 102.37 | 94.68
2020-02-23 18:30 | 103.22 | 93.75
2020-02-23 19:00 | 110.86 | 102.52
2020-02-23 19:30 | 99.11 | 89.27
2020-02-23 20:00 | 102.19 | 92.42
2020-02-23 20:30 | 107.5 | 99
2020-02-23 21:00 | 103.47 | 94.06
2020-02-23 21:30 | 107.87 | 98.37
2020-02-23 22:00 | 109.89 | 100.32
2020-02-23 22:30 | 106.69 | 96.21
2020-02-23 23:00 | 112.14 | 102.11
2020-02-23 23:30 | 110.32 | 99.96
2020-02-24 | 115.24 | 106.96
2020-02-24 00:30 | 102.18 | 92.02
2020-02-24 01:00 | 109.34 | 99.43
2020-02-24 01:30 | 100.53 | 88.51
2020-02-24 02:00 | 103 | 91.74
2020-02-24 02:30 | 112.82 | 104.27
2020-02-24 03:00 | 106.75 | 97.34
2020-02-24 03:30 | 107.42 | 96.94
2020-02-24 04:00 | 108.58 | 96.94
2020-02-24 04:30 | 111.4 | 100.36
2020-02-24 05:00 | 114.24 | 103.87
2020-02-24 05:30 | 113.75 | 102.55
2020-02-24 06:00 | 108.86 | 98.72
2020-02-24 06:30 | 112.53 | 102.61
2020-02-24 07:00 | 102.4 | 91.04
2020-02-24 07:30 | 108 | 99.52
2020-02-24 08:00 | 107.88 | 98.7
2020-02-24 08:30 | 103.3 | 92.23
2020-02-24 09:00 | 105.15 | 93.66
2020-02-24 09:30 | 102.8 | 90.56
2020-02-24 10:00 | 103.67 | 90.05
2020-02-24 10:30 | 97.33 | 82.98
2020-02-24 11:00 | 99.14 | 81.74
2020-02-24 11:30 | 105.07 | 90.43
2020-02-24 12:00 | 102.96 | 88.05
2020-02-24 12:30 | 101.71 | 86.37
2020-02-24 13:00 | 103.86 | 89.46
2020-02-24 13:30 | 102.62 | 88.85
2020-02-24 14:00 | 103 | 86.37
2020-02-24 14:30 | 108.04 | 91.63
2020-02-24 15:00 | 115.98 | 103.7
2020-02-24 15:30 | 113.95 | 101.7
2020-02-24 16:00 | 109.12 | 95.98
2020-02-24 16:30 | 115.3 | 105.21
2020-02-24 17:00 | 118.93 | 109.72
2020-02-24 17:30 | 106.14 | 96.56
2020-02-24 18:00 | 106.15 | 97.01
2020-02-24 18:30 | 109.05 | 99.94
2020-02-24 19:00 | 115.52 | 107.05
2020-02-24 19:30 | 118.06 | 110.28
2020-02-24 20:00 | 122.31 | 114.61
2020-02-24 20:30 | 125.24 | 117.45
2020-02-24 21:00 | 121.28 | 112.46
2020-02-24 21:30 | 118.61 | 109.25
2020-02-24 22:00 | 123.28 | 115.27
2020-02-24 22:30 | 124.1 | 116.71
2020-02-24 23:00 | 119.77 | 111.87
2020-02-24 23:30 | 118.51 | 109.22
2020-02-25 | 116.43 | 107.83
2020-02-25 00:30 | 120.39 | 112.19
2020-02-25 01:00 | 116.37 | 107.24
2020-02-25 01:30 | 114.58 | 105.01
2020-02-25 02:00 | 109.3 | 98.02
2020-02-25 02:30 | 111.89 | 100.84
2020-02-25 03:00 | 115.05 | 104.08
2020-02-25 03:30 | 109.87 | 98.82
2020-02-25 04:00 | 105.21 | 93.51
2020-02-25 04:30 | 110.05 | 97.56
2020-02-25 05:00 | 111.57 | 100.17
2020-02-25 05:30 | 110.05 | 97.43
2020-02-25 06:00 | 105.32 | 92.47
2020-02-25 06:30 | 99.45 | 85.7
2020-02-25 07:00 | 97.05 | 83.3
2020-02-25 07:30 | 98.42 | 85.77
2020-02-25 08:00 | 98.85 | 86.73
2020-02-25 08:30 | 99.96 | 84.39
2020-02-25 09:00 | 99.96 | 83.5
2020-02-25 09:30 | 99.34 | 85.05
2020-02-25 10:00 | 99.16 | 87.23
2020-02-25 10:30 | 93.9 | 80.25
2020-02-25 11:00 | 98.95 | 86.69
2020-02-25 11:30 | 104.86 | 92.53
2020-02-25 12:00 | 103.99 | 92.08
2020-02-25 12:30 | 103.42 | 91.63
2020-02-25 13:00 | 97.22 | 85.34
2020-02-25 13:30 | 94.84 | 83.63
2020-02-25 14:00 | 99.71 | 87
2020-02-25 14:30 | 97.54 | 81.23
2020-02-25 15:00 | 97.3 | 80.89
2020-02-25 15:30 | 97.98 | 80.92
2020-02-25 16:00 | 103.48 | 89.77
2020-02-25 16:30 | 102.83 | 90.48
2020-02-25 17:00 | 107.29 | 96.31
2020-02-25 17:30 | 113.27 | 105.37
2020-02-25 18:00 | 111.28 | 104.05
2020-02-25 18:30 | 114.39 | 105.93
2020-02-25 19:00 | 114.57 | 105.21
2020-02-25 19:30 | 120.45 | 111.53
2020-02-25 20:00 | 127.98 | 119.84
2020-02-25 20:30 | 119.99 | 110.26
2020-02-25 21:00 | 120.27 | 110.79
2020-02-25 21:30 | 116.11 | 106.45
2020-02-25 22:00 | 109.99 | 98.44
2020-02-25 22:30 | 110.73 | 99.37
2020-02-25 23:00 | 114.7 | 103.98
2020-02-25 23:30 | 106.99 | 95.5
2020-02-26 | 108.16 | 96.78
2020-02-26 00:30 | 110.92 | 99.27
2020-02-26 01:00 | 107.85 | 96.32
2020-02-26 01:30 | 107.4 | 95.92
2020-02-26 02:00 | 107.97 | 95.97
2020-02-26 02:30 | 106.05 | 94.1
2020-02-26 03:00 | 109.14 | 98.17
2020-02-26 03:30 | 104.66 | 91.66
2020-02-26 04:00 | 109.07 | 96.41
2020-02-26 04:30 | 111.35 | 99.64
2020-02-26 05:00 | 110.19 | 99.6
2020-02-26 05:30 | 107.62 | 97.12
2020-02-26 06:00 | 112.33 | 102.19
2020-02-26 06:30 | 111.14 | 101.16
2020-02-26 07:00 | 99.55 | 88.06
2020-02-26 07:30 | 89.76 | 75.62
2020-02-26 08:00 | 89.91 | 76.51
2020-02-26 08:30 | 98.78 | 86.21
2020-02-26 09:00 | 103.43 | 94.27
2020-02-26 09:30 | 96.22 | 85.98
2020-02-26 10:00 | 94.75 | 84.63
2020-02-26 10:30 | 87.98 | 75.97
2020-02-26 11:00 | 101.6 | 91.29
2020-02-26 11:30 | 104.66 | 94.12
2020-02-26 12:00 | 106.18 | 95.58
2020-02-26 12:30 | 105.61 | 96.59
2020-02-26 13:00 | 113.95 | 105.54
2020-02-26 13:30 | 112.69 | 104.31
2020-02-26 14:00 | 108.97 | 99.42
2020-02-26 14:30 | 114.78 | 106.41
2020-02-26 15:00 | 111.55 | 102.56
2020-02-26 15:30 | 111.68 | 101.24
2020-02-26 16:00 | 122.61 | 114.88
2020-02-26 16:30 | 120.85 | 112.34
2020-02-26 17:00 | 123.8 | 116.11
2020-02-26 17:30 | 113.19 | 104.04
2020-02-26 18:00 | 118.51 | 111.59
2020-02-26 18:30 | 117.23 | 109.9
2020-02-26 19:00 | 118.26 | 111.37
2020-02-26 19:30 | 112.05 | 105.28
2020-02-26 20:00 | 116.54 | 110.54
2020-02-26 20:30 | 110.52 | 103.13
2020-02-26 21:00 | 117.41 | 109.81
2020-02-26 21:30 | 106.25 | 96.22
2020-02-26 22:00 | 107.21 | 97.63
2020-02-26 22:30 | 103.05 | 91.22
2020-02-26 23:00 | 101.32 | 89.11
2020-02-26 23:30 | 106.73 | 96.05
2020-02-27 | 104.52 | 93.31
2020-02-27 00:30 | 102.48 | 90.4
2020-02-27 01:00 | 101.68 | 89.54
2020-02-27 01:30 | 99.62 | 88.08
2020-02-27 02:00 | 109.3 | 100
2020-02-27 02:30 | 107.72 | 97.65
2020-02-27 03:00 | 106.45 | 97.03
2020-02-27 03:30 | 107.14 | 96.22
2020-02-27 04:00 | 110.35 | 99.83
2020-02-27 04:30 | 109.12 | 99.3
2020-02-27 05:00 | 104.03 | 93.08
2020-02-27 05:30 | 108.1 | 99.15
2020-02-27 06:00 | 104.77 | 95.12
2020-02-27 06:30 | 94.95 | 80.81
2020-02-27 07:00 | 101.13 | 89.3
2020-02-27 07:30 | 91.98 | 76.19
2020-02-27 08:00 | 83.86 | 63.59
2020-02-27 08:30 | 83.54 | 62.88
2020-02-27 09:00 | 83.57 | 60.68
2020-02-27 09:30 | 82.93 | 58.71
2020-02-27 10:00 | 84.27 | 60.03
2020-02-27 10:30 | 91.54 | 69.11
2020-02-27 11:00 | 91.36 | 68.99
2020-02-27 11:30 | 86.12 | 61.6
2020-02-27 12:00 | 86.57 | 64.04
2020-02-27 12:30 | 86.95 | 65.2
2020-02-27 13:00 | 93.39 | 75.57
2020-02-27 13:30 | 87.71 | 67.74
2020-02-27 14:00 | 87.69 | 65.6
2020-02-27 14:30 | 83.34 | 62.68
2020-02-27 15:00 | 83.58 | 60.99
2020-02-27 15:30 | 85.49 | 60.92
2020-02-27 16:00 | 88.16 | 65.72
2020-02-27 16:30 | 88.14 | 67.55
2020-02-27 17:00 | 87.93 | 69.58
2020-02-27 17:30 | 88.79 | 74.32
2020-02-27 18:00 | 91.04 | 80.63
2020-02-27 18:30 | 91.19 | 81.6
2020-02-27 19:00 | 102.11 | 94.8
2020-02-27 19:30 | 104.8 | 97.39
2020-02-27 20:00 | 101.69 | 93.85
2020-02-27 20:30 | 104.18 | 95.52
2020-02-27 21:00 | 100.78 | 90.91
2020-02-27 21:30 | 96.12 | 85.99
2020-02-27 22:00 | 95.4 | 85.9
2020-02-27 22:30 | 94.17 | 84.33
2020-02-27 23:00 | 89.65 | 78.57
2020-02-27 23:30 | 97.85 | 87.21
2020-02-28 | 98.98 | 87.08
2020-02-28 00:30 | 96.53 | 84.23
2020-02-28 01:00 | 92.82 | 79.3
2020-02-28 01:30 | 94.28 | 82.15
2020-02-28 02:00 | 98.76 | 85.94
2020-02-28 02:30 | 94.2 | 79.66
2020-02-28 03:00 | 97.52 | 83.64
2020-02-28 03:30 | 97.65 | 83.36
2020-02-28 04:00 | 100.08 | 86.08
2020-02-28 04:30 | 100.15 | 86.74
2020-02-28 05:00 | 99.4 | 86.83
2020-02-28 05:30 | 98.42 | 84.87
2020-02-28 06:00 | 101.65 | 89.22
2020-02-28 06:30 | 91.93 | 77.16
2020-02-28 07:00 | 91.54 | 75.91
2020-02-28 07:30 | 87.24 | 68.39
2020-02-28 08:00 | 81.98 | 60.73
2020-02-28 08:30 | 82.37 | 59.45
2020-02-28 09:00 | 84.33 | 62.8
2020-02-28 09:30 | 83.16 | 63.82
2020-02-28 10:00 | 82.44 | 58.21
2020-02-28 10:30 | 88.77 | 67.46
2020-02-28 11:00 | 86.82 | 64.14
2020-02-28 11:30 | 85.6 | 62.05
2020-02-28 12:00 | 83.94 | 61.68
2020-02-28 12:30 | 88.12 | 69.5
2020-02-28 13:00 | 86.66 | 71.08
2020-02-28 13:30 | 94.29 | 80.5
2020-02-28 14:00 | 96.15 | 82.16
2020-02-28 14:30 | 93.3 | 78.32
2020-02-28 15:00 | 95.41 | 81.09
2020-02-28 15:30 | 103.29 | 91.5
2020-02-28 16:00 | 91.13 | 75.84
2020-02-28 16:30 | 88.34 | 71.58
2020-02-28 17:00 | 91.69 | 76.26
2020-02-28 17:30 | 86.94 | 74.31
2020-02-28 18:00 | 97.34 | 89.43
2020-02-28 18:30 | 98.99 | 92.4
2020-02-28 19:00 | 105.01 | 98.98
2020-02-28 19:30 | 109.27 | 103.46
2020-02-28 20:00 | 105.94 | 99.92
2020-02-28 20:30 | 105.7 | 99.03
2020-02-28 21:00 | 102.55 | 95.23
2020-02-28 21:30 | 101.66 | 94.09
2020-02-28 22:00 | 106.56 | 99.21
2020-02-28 22:30 | 98.01 | 88.78
2020-02-28 23:00 | 105.21 | 97.23
2020-02-28 23:30 | 100.86 | 92.24
2020-02-29 | 101.11 | 92.93
2020-02-29 00:30 | 96.9 | 88.44
2020-02-29 01:00 | 97.96 | 88.82
2020-02-29 01:30 | 90.08 | 79.32
2020-02-29 02:00 | 91.6 | 81
2020-02-29 02:30 | 94.45 | 84.61
2020-02-29 03:00 | 97.24 | 88.01
2020-02-29 03:30 | 96.26 | 86.67
2020-02-29 04:00 | 97.13 | 87.77
2020-02-29 04:30 | 99.28 | 90.7
2020-02-29 05:00 | 102.2 | 93.94
2020-02-29 05:30 | 100.53 | 91.66
2020-02-29 06:00 | 105.61 | 97.92
2020-02-29 06:30 | 98.36 | 88.68
2020-02-29 07:00 | 99.08 | 88.79
2020-02-29 07:30 | 94.56 | 81.56
2020-02-29 08:00 | 87.63 | 71.54
2020-02-29 08:30 | 87.76 | 70.59
2020-02-29 09:00 | 92.29 | 76.65
2020-02-29 09:30 | 88.74 | 72.15
2020-02-29 10:00 | 98.18 | 87.32
2020-02-29 10:30 | 91.63 | 76.97
2020-02-29 11:00 | 94.41 | 80.8
2020-02-29 11:30 | 93.92 | 76.79
2020-02-29 12:00 | 96.47 | 82.23
2020-02-29 12:30 | 90.3 | 74.49
2020-02-29 13:00 | 88.45 | 73.11
2020-02-29 13:30 | 90.08 | 76.63
2020-02-29 14:00 | 86.06 | 69.92
2020-02-29 14:30 | 84.84 | 68.12
2020-02-29 15:00 | 84.76 | 68.61
2020-02-29 15:30 | 90.03 | 77.07
2020-02-29 16:00 | 93.17 | 85.03
2020-02-29 16:30 | 95.55 | 84.62
2020-02-29 17:00 | 99.11 | 88.03
2020-02-29 17:30 | 98.87 | 90.13
2020-02-29 18:00 | 104.74 | 99.01
2020-02-29 18:30 | 100.62 | 94.32
2020-02-29 19:00 | 104.82 | 99.06
2020-02-29 19:30 | 106.65 | 100.92
2020-02-29 20:00 | 101.64 | 95.48
2020-02-29 20:30 | 108.09 | 102.15
2020-02-29 21:00 | 107.42 | 100.79
2020-02-29 21:30 | 104.23 | 96.77
2020-02-29 22:00 | 110.79 | 104.31
2020-02-29 22:30 | 110.31 | 103.61
2020-02-29 23:00 | 106.78 | 99.33
2020-02-29 23:30 | 111.83 | 105.04
2020-03-01 | 103.9 | 95.91

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 332 | 332 | 332 | 332 | 332 | 332
Transformers | T032T01 | 86 | 86 | 86 | 86 | 86 | 86
| T032T02 | 86 | 86 | 86 | 86 | 86 | 86
| T032T07 | 160 | 160 | 160 | 160 | 160 | 160

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2017-01-13 19:14 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | Storm | 0.18333 | 0.18 | 0 | 0
2017-01-13 20:27 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | Storm | 0.2 | 0.2 | 0 | 0
2017-03-14 17:58 | 7114/2 - 7114 Tee to T032 Blackwater | FEEDER | Storm | 0.18333
2017-04-01 20:16 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | HV Equipment malfunction or failure | 0.16667 | 0.17 | 0 | 0
2017-09-12 17:43 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | Transient Feeder Fault of Unknown Origin | 0.2
2017-10-06 04:24 | T032 132KV 1 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 2072.2667
2017-12-14 06:49 | T032 132KV 1 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 450.7333
2018-01-18 08:45 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | Secondary system malfunction or failure | 0.15 | 0.17 | 0 | 0
2018-02-16 17:23 | 0789 - H015 Lilyvale to T032 Blackwater | FEEDER | Storm | 0.083333
2018-04-18 15:53 | 7114/2 - 7114 Tee to T032 Blackwater | FEEDER | Secondary system malfunction or failure | 372.7333
2018-04-19 08:22 | 7113/2 - T210 Duaringa Tee to T032 Blackwater | FEEDER | Natural Hazard | 25.35 | 15 | 1 | 15
2018-09-27 21:30 | 7114/2 - 7114 Tee to T032 Blackwater | FEEDER | Storm | 1.6167
2018-12-22 18:00 | T032 132KV 2 TRANSFORMER | TRANSFORMER | HV Equipment malfunction or failure | 1310.75
2019-03-04 03:42 | 7113 - T031 Baralaba to T032 Blackwater | FEEDER | Secondary system malfunction or failure | 692.0167
2019-03-05 12:53 | 7113 - T031 Baralaba to T032 Blackwater | FEEDER | Human Error | 7.6167