## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Columboola
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -26.649
| Constrained connection point longitude (decimal degrees) | 150.279
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 296.2827 | 296.8137 | 270.3749 | 269.7387 | 260.4311 | 260.4942 | 260.5636 | 260.612 | 260.6867 | 260.9475 | 260.9979
| 50% PoE | 281.75 | 282.255 | 257.113 | 256.508 | 247.657 | 247.717 | 247.783 | 247.829 | 247.9 | 248.148 | 248.196
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 170.629 | 154.488 | 154.546 | 150.324 | 150.432 | 150.542 | 150.628 | 150.734 | 150.846 | 151.102 | 151.15
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 240.4616 | 240.3996 | 219.7644 | 219.2628 | 212.0069 | 212.0816 | 212.1699 | 212.2793 | 212.395 | 212.6558 | 212.7062
| 50% PoE | 228.667 | 228.608 | 208.985 | 208.508 | 201.608 | 201.679 | 201.763 | 201.867 | 201.977 | 202.225 | 202.273
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | 80.041 | 80.887 | 80.893 | 80.899 | 80.911 | 80.925 | 80.933 | 80.945 | 80.955 | 80.987 | 80.987
12 | Voltage Level (kV) | 132
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.8
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.5
14 | Load duration curve
15 | Preferred investment | Columboola 132kV secondary systems replacement
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) | [10 empty] | 15
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) | [10 empty] | 0.3
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2031-06-30
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Secondary systems
26 | Unplanned outages
27 | Maximum fault level (kA) | 21.2
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.5374
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112.6

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 241.617 | 201.773 | 176.939 | 176.59 | 167.689 | 167.631 | 167.575 | 167.523 | 223.981 | 224.023 | 224.023
1:00 | 255.714 | 201.193 | 176.374 | 176.04 | 167.134 | 167.074 | 167.016 | 166.962 | 223.056 | 223.096 | 223.096
1:30 | 255.096 | 200.969 | 176.102 | 175.723 | 166.817 | 166.759 | 166.699 | 166.647 | 222.3 | 222.324 | 222.324
2:00 | 255.16 | 200.999 | 175.95 | 175.412 | 166.5 | 166.44 | 166.38 | 166.328 | 222.072 | 222.096 | 222.094
2:30 | 254.474 | 201.555 | 176.211 | 175.417 | 166.488 | 166.428 | 166.37 | 166.316 | 221.706 | 221.734 | 221.732
3:00 | 254.65 | 201.91 | 176.422 | 175.425 | 166.505 | 166.477 | 166.449 | 166.417 | 221.612 | 221.64 | 221.638
3:30 | 253.603 | 202.044 | 176.528 | 175.351 | 166.409 | 166.349 | 166.289 | 166.237 | 221.77 | 221.798 | 221.796
4:00 | 253.904 | 202.225 | 176.728 | 175.779 | 166.843 | 166.783 | 166.725 | 166.671 | 221.589 | 221.607 | 221.607
4:30 | 254.192 | 203.64 | 178.242 | 177.403 | 168.489 | 168.461 | 168.433 | 168.401 | 221.966 | 221.964 | 221.962
5:00 | 254.349 | 204.772 | 179.595 | 178.95 | 170.047 | 170.019 | 169.993 | 169.961 | 222.641 | 222.653 | 222.655
5:30 | 255.184 | 207.21 | 181.819 | 180.991 | 172.077 | 172.051 | 172.025 | 171.997 | 223.582 | 223.596 | 223.602
6:00 | 255.856 | 209.747 | 184.572 | 183.929 | 175.028 | 175.002 | 174.98 | 174.954 | 225.151 | 225.137 | 225.145
6:30 | 258.756 | 214.294 | 188.837 | 187.949 | 179.036 | 179.014 | 178.994 | 178.974 | 227 | 226.92 | 226.886
7:00 | 259.031 | 219.414 | 194.193 | 193.509 | 184.607 | 184.585 | 184.567 | 184.549 | 226.872 | 226.598 | 226.492
7:30 | 258.976 | 219.105 | 193.753 | 192.94 | 184.019 | 183.959 | 183.907 | 183.873 | 226.6 | 226.182 | 225.988
8:00 | 257.588 | 220.083 | 194.647 | 193.507 | 184.585 | 184.549 | 184.523 | 184.509 | 224.648 | 224.176 | 223.934
8:30 | 255.674 | 228.456 | 202.604 | 200.253 | 191.153 | 190.933 | 190.725 | 190.563 | 221.388 | 220.656 | 220.332
9:00 | 253.339 | 222.65 | 196.454 | 193.321 | 184.072 | 183.71 | 183.364 | 183.076 | 218.126 | 217.218 | 216.828
9:30 | 251.381 | 207.384 | 181.085 | 177.731 | 168.4 | 167.966 | 167.55 | 167.19 | 215.835 | 214.919 | 214.441
10:00 | 253.055 | 201.333 | 174.703 | 171.542 | 162.106 | 161.558 | 161.032 | 160.564 | 214.056 | 213.046 | 212.468
10:30 | 254.811 | 196.317 | 169.72 | 167.65 | 158.171 | 157.577 | 157.005 | 156.475 | 214.056 | 213.082 | 212.47
11:00 | 256.419 | 193.509 | 167.226 | 165.584 | 156.038 | 155.344 | 154.674 | 154.06 | 218.606 | 217.692 | 217.094
11:30 | 256.914 | 191.187 | 165.142 | 163.675 | 154.172 | 153.546 | 152.94 | 152.366 | 219.515 | 218.581 | 217.957
12:00 | 258.106 | 190.272 | 164.222 | 162.723 | 153.197 | 152.545 | 151.915 | 151.321 | 219.783 | 218.821 | 218.175
12:30 | 260.093 | 190.362 | 164.273 | 162.706 | 153.201 | 152.575 | 151.971 | 151.403 | 221.049 | 220.099 | 219.477
13:00 | 261.688 | 189.928 | 163.79 | 162.148 | 152.643 | 152.019 | 151.413 | 150.847 | 221.771 | 220.949 | 220.337
13:30 | 263.079 | 190.419 | 164.188 | 162.447 | 152.957 | 152.351 | 151.765 | 151.215 | 221.726 | 221.01 | 220.424
14:00 | 265.275 | 191.855 | 165.48 | 163.489 | 153.976 | 153.356 | 152.758 | 152.194 | 224.099 | 223.429 | 222.885
14:30 | 267.442 | 193.275 | 166.996 | 164.747 | 155.306 | 154.782 | 154.274 | 153.788 | 226.645 | 226.067 | 225.603
15:00 | 269.301 | 194.461 | 168.293 | 166.383 | 157.023 | 156.583 | 156.161 | 155.753 | 228.727 | 228.281 | 227.869
15:30 | 270.891 | 196.889 | 170.744 | 168.057 | 158.777 | 158.439 | 158.115 | 157.803 | 230.669 | 230.311 | 229.979
16:00 | 273.872 | 238.162 | 212.069 | 209.61 | 200.449 | 200.215 | 199.997 | 199.787 | 233.769 | 233.491 | 233.241
16:30 | 277.142 | 273.103 | 247.291 | 245.17 | 236.138 | 236.042 | 235.958 | 235.87 | 237.745 | 237.589 | 237.449
17:00 | 279.517 | 274.216 | 248.644 | 247.175 | 238.246 | 238.25 | 238.262 | 238.26 | 240.862 | 240.988 | 240.928
17:30 | 280.219 | 275.612 | 250.205 | 248.77 | 239.919 | 240.007 | 240.103 | 240.179 | 242.469 | 242.703 | 242.735
18:00 | 281.573 | 277.214 | 252.107 | 251.513 | 242.703 | 242.801 | 242.907 | 242.997 | 243.749 | 244.017 | 244.087
18:30 | 281.75 | 282.255 | 257.113 | 256.508 | 247.657 | 247.717 | 247.783 | 247.829 | 245.538 | 245.8 | 245.866
19:00 | 278.333 | 280.364 | 255.283 | 254.731 | 245.881 | 245.933 | 245.991 | 246.027 | 247.9 | 248.148 | 248.196
19:30 | 253.908 | 251.654 | 226.525 | 225.925 | 217.054 | 217.076 | 217.098 | 217.108 | 247.136 | 247.36 | 247.388
20:00 | 233.406 | 229.3 | 204.167 | 203.566 | 194.693 | 194.713 | 194.735 | 194.741 | 244.345 | 244.559 | 244.579
20:30 | 230.753 | 227.364 | 202.302 | 201.765 | 192.894 | 192.914 | 192.934 | 192.94 | 242.334 | 242.542 | 242.56
21:00 | 226.457 | 225.889 | 200.919 | 200.46 | 191.592 | 191.612 | 191.632 | 191.636 | 241.215 | 241.423 | 241.439
21:30 | 223.826 | 224.597 | 199.645 | 199.198 | 190.319 | 190.315 | 190.313 | 190.299 | 239.018 | 239.152 | 239.164
22:00 | 222.402 | 222.666 | 198.231 | 198.175 | 189.382 | 189.378 | 189.374 | 189.36 | 237.717 | 237.793 | 237.801
22:30 | 219.615 | 220.936 | 196.228 | 195.992 | 187.115 | 187.091 | 187.071 | 187.045 | 235.462 | 235.514 | 235.524
23:00 | 217.707 | 219.171 | 194.767 | 194.699 | 185.933 | 185.909 | 185.887 | 185.859 | 233.553 | 233.603 | 233.611
23:30 | 244.331 | 218.463 | 194.052 | 193.982 | 185.212 | 185.188 | 185.164 | 185.136 | 232.958 | 232.986 | 232.99
0:00 | 212.137 | 202.214 | 177.48 | 177.223 | 168.342 | 168.316 | 168.29 | 168.262 | 224.387 | 224.431 | 224.433

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 96.649 | 97.73 | 97.736 | 97.742 | 97.754 | 97.768 | 97.776 | 97.788 | 97.798 | 97.83 | 97.83
1:00 | 97.32 | 98.172 | 98.17 | 98.17 | 98.172 | 98.172 | 98.172 | 98.174 | 98.174 | 98.178 | 98.178
1:30 | 104.878 | 105.014 | 105.012 | 105.012 | 105.012 | 105.012 | 105.014 | 105.014 | 105.014 | 105.018 | 105.018
2:00 | 123.906 | 124.038 | 124.034 | 124.032 | 124.03 | 124.028 | 124.026 | 124.024 | 124.022 | 124.018 | 124.018
2:30 | 131.047 | 131.191 | 131.187 | 131.181 | 131.177 | 131.171 | 131.167 | 131.161 | 131.157 | 131.145 | 131.143
3:00 | 136.87 | 137.02 | 137.014 | 137.01 | 137.006 | 137 | 136.996 | 136.99 | 136.984 | 136.974 | 136.972
3:30 | 136.864 | 137.022 | 137.016 | 137.012 | 137.006 | 137.002 | 136.998 | 136.992 | 136.986 | 136.976 | 136.974
4:00 | 136.699 | 136.857 | 136.851 | 136.847 | 136.841 | 136.837 | 136.831 | 136.827 | 136.821 | 136.811 | 136.809
4:30 | 137.131 | 137.257 | 137.251 | 137.245 | 137.239 | 137.231 | 137.227 | 137.221 | 137.215 | 137.201 | 137.199
5:00 | 137.844 | 137.914 | 137.908 | 137.904 | 137.896 | 137.89 | 137.886 | 137.88 | 137.876 | 137.864 | 137.864
5:30 | 139.539 | 139.531 | 139.523 | 139.519 | 139.513 | 139.505 | 139.503 | 139.499 | 139.495 | 139.487 | 139.491
6:00 | 140.402 | 140.4 | 140.396 | 140.394 | 140.39 | 140.388 | 140.39 | 140.392 | 140.4 | 140.404 | 140.422
6:30 | 135.468 | 135.268 | 135.124 | 135.032 | 134.93 | 134.834 | 134.754 | 134.672 | 134.58 | 134.452 | 134.418
7:00 | 133.707 | 133.293 | 133.005 | 132.823 | 132.633 | 132.453 | 132.293 | 132.131 | 131.939 | 131.703 | 131.601
7:30 | 133.199 | 132.535 | 132.073 | 131.789 | 131.505 | 131.235 | 130.987 | 130.737 | 130.435 | 130.101 | 129.917
8:00 | 131.742 | 130.95 | 130.3 | 129.896 | 129.49 | 129.098 | 128.746 | 128.386 | 127.952 | 127.466 | 127.202
8:30 | 129.089 | 128.183 | 127.317 | 126.775 | 126.219 | 125.685 | 125.205 | 124.709 | 124.117 | 123.421 | 123.067
9:00 | 132.614 | 131.61 | 130.606 | 129.972 | 129.322 | 128.692 | 128.126 | 127.54 | 126.836 | 125.998 | 125.57
9:30 | 136.422 | 135.292 | 134.16 | 133.442 | 132.694 | 131.974 | 131.324 | 130.642 | 129.818 | 128.814 | 128.304
10:00 | 139.763 | 138.521 | 137.297 | 136.537 | 135.775 | 135.039 | 134.357 | 133.649 | 132.777 | 131.799 | 131.211
10:30 | 144.607 | 141.188 | 139.886 | 139.072 | 138.252 | 137.458 | 136.722 | 135.952 | 135.01 | 134.198 | 134.838
11:00 | 161.516 | 153.339 | 152.031 | 151.223 | 150.427 | 149.655 | 148.931 | 148.181 | 147.253 | 147.437 | 148.089
11:30 | 174.262 | 163.863 | 162.459 | 161.607 | 160.799 | 160.017 | 159.265 | 158.495 | 157.529 | 157.383 | 158.101
12:00 | 177.128 | 164.524 | 163.052 | 162.16 | 161.316 | 160.498 | 159.71 | 158.904 | 157.892 | 158.09 | 158.844
12:30 | 178.56 | 164.183 | 162.721 | 161.825 | 160.963 | 160.129 | 159.335 | 158.521 | 157.879 | 158.923 | 159.657
13:00 | 181.971 | 165.675 | 164.185 | 163.273 | 162.397 | 161.545 | 160.737 | 159.905 | 159.845 | 160.907 | 161.665
13:30 | 191.168 | 170.343 | 168.913 | 163.927 | 163.117 | 162.329 | 161.569 | 160.791 | 159.811 | 158.869 | 159.367
14:00 | 197.092 | 174.101 | 172.743 | 165.73 | 164.972 | 164.238 | 163.522 | 162.794 | 161.872 | 161.012 | 160.308
14:30 | 198.126 | 175.119 | 173.917 | 166.851 | 166.193 | 165.551 | 164.925 | 164.289 | 163.479 | 162.755 | 162.125
15:00 | 198.415 | 176.228 | 175.206 | 168.853 | 168.305 | 167.773 | 167.247 | 166.717 | 166.041 | 165.455 | 164.921
15:30 | 196.937 | 176.725 | 175.881 | 171.314 | 170.866 | 170.432 | 170.006 | 169.578 | 169.03 | 168.564 | 168.138
16:00 | 201.99 | 180.428 | 179.716 | 173.991 | 173.617 | 173.259 | 172.905 | 172.553 | 172.101 | 171.723 | 171.373
16:30 | 204.139 | 182.578 | 182.054 | 176.253 | 175.995 | 175.753 | 175.511 | 175.273 | 174.963 | 174.745 | 174.501
17:00 | 205.335 | 183.905 | 183.607 | 177.794 | 177.71 | 177.634 | 177.538 | 177.462 | 177.34 | 177.392 | 177.26
17:30 | 206.526 | 185.198 | 185.026 | 179.195 | 179.161 | 179.139 | 179.105 | 179.089 | 179.049 | 179.135 | 179.093
18:00 | 207.685 | 186.447 | 186.393 | 180.556 | 180.588 | 180.634 | 180.666 | 180.716 | 180.764 | 180.93 | 180.958
18:30 | 207.488 | 186.872 | 186.928 | 181.586 | 181.694 | 181.806 | 181.898 | 182.012 | 182.136 | 182.4 | 182.466
19:00 | 209.391 | 188.683 | 188.741 | 183.311 | 183.419 | 183.529 | 183.615 | 183.721 | 183.833 | 184.089 | 184.137
19:30 | 208.165 | 187.955 | 188.007 | 183.029 | 183.121 | 183.215 | 183.285 | 183.371 | 183.461 | 183.677 | 183.705
20:00 | 205.574 | 186.102 | 186.152 | 181.847 | 181.939 | 182.031 | 182.097 | 182.177 | 182.263 | 182.471 | 182.493
20:30 | 205.021 | 185.259 | 185.311 | 180.719 | 180.815 | 180.907 | 180.973 | 181.055 | 181.141 | 181.355 | 181.371
21:00 | 205.126 | 184.368 | 184.418 | 178.937 | 179.029 | 179.117 | 179.181 | 179.259 | 179.341 | 179.547 | 179.561
21:30 | 206.733 | 184.838 | 184.874 | 178.301 | 178.363 | 178.425 | 178.469 | 178.523 | 178.579 | 178.719 | 178.731
22:00 | 204.893 | 183.541 | 183.569 | 177.53 | 177.582 | 177.634 | 177.672 | 177.718 | 177.764 | 177.884 | 177.894
22:30 | 201.722 | 180.881 | 180.893 | 175.274 | 175.296 | 175.32 | 175.336 | 175.358 | 175.382 | 175.436 | 175.444
23:00 | 198.711 | 178.416 | 178.43 | 173.295 | 173.317 | 173.339 | 173.355 | 173.375 | 173.397 | 173.449 | 173.455
23:30 | 197.462 | 177.407 | 177.419 | 172.507 | 172.527 | 172.545 | 172.559 | 172.577 | 172.595 | 172.639 | 172.643
0:00 | 97.415 | 98.477 | 98.481 | 98.487 | 98.501 | 98.515 | 98.525 | 98.537 | 98.549 | 98.581 | 98.583

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 193.587 | 163.949 | 144.552 | 144.26 | 137.305 | 179.153 | 179.165 | 179.181 | 179.197 | 179.239 | 179.239
1:00 | 204.196 | 163.376 | 143.989 | 143.709 | 136.751 | 178.225 | 178.237 | 178.251 | 178.267 | 178.307 | 178.307
1:30 | 203.632 | 163.135 | 143.711 | 143.395 | 136.436 | 177.531 | 177.537 | 177.547 | 177.553 | 177.577 | 177.577
2:00 | 203.712 | 163.094 | 143.528 | 143.088 | 136.124 | 177.289 | 177.295 | 177.303 | 177.311 | 177.335 | 177.333
2:30 | 203.098 | 163.535 | 143.739 | 143.099 | 136.122 | 176.937 | 176.945 | 176.953 | 176.963 | 176.991 | 176.989
3:00 | 203.156 | 163.811 | 143.905 | 143.112 | 136.145 | 176.837 | 176.845 | 176.853 | 176.863 | 176.891 | 176.889
3:30 | 202.271 | 163.909 | 143.977 | 143.039 | 136.052 | 176.971 | 176.977 | 176.987 | 176.997 | 177.025 | 177.023
4:00 | 202.534 | 164.141 | 144.225 | 143.465 | 136.482 | 176.832 | 176.836 | 176.842 | 176.848 | 176.866 | 176.866
4:30 | 202.817 | 165.589 | 145.753 | 145.083 | 138.121 | 177.259 | 177.257 | 177.255 | 177.253 | 177.251 | 177.249
5:00 | 203.011 | 166.806 | 147.143 | 146.624 | 139.671 | 177.935 | 177.939 | 177.941 | 177.945 | 177.957 | 177.959
5:30 | 203.905 | 169.158 | 149.329 | 148.667 | 141.706 | 178.873 | 178.877 | 178.881 | 178.889 | 178.903 | 178.909
6:00 | 204.567 | 171.774 | 152.114 | 151.597 | 144.646 | 180.411 | 180.401 | 180.393 | 180.385 | 180.371 | 180.379
6:30 | 207.175 | 176.207 | 156.328 | 155.62 | 148.66 | 182.415 | 182.349 | 182.285 | 182.211 | 182.131 | 182.097
7:00 | 207.479 | 181.412 | 161.717 | 161.168 | 154.216 | 182.67 | 182.5 | 182.32 | 182.112 | 181.838 | 181.732
7:30 | 207.361 | 181.047 | 161.251 | 160.601 | 153.632 | 182.707 | 182.431 | 182.143 | 181.803 | 181.385 | 181.191
8:00 | 206.052 | 181.811 | 161.948 | 161.044 | 154.077 | 180.957 | 180.619 | 180.275 | 179.863 | 179.391 | 179.149
8:30 | 204.176 | 187.216 | 166.965 | 165.068 | 157.928 | 178.124 | 177.65 | 177.158 | 176.576 | 175.844 | 175.52
9:00 | 201.969 | 181.682 | 161.097 | 158.546 | 151.26 | 175.16 | 174.6 | 174.01 | 173.314 | 172.406 | 172.016
9:30 | 200.058 | 168.638 | 147.931 | 145.179 | 137.813 | 173.025 | 172.421 | 171.787 | 171.023 | 170.107 | 169.629
10:00 | 201.474 | 162.914 | 141.89 | 139.247 | 131.775 | 171.516 | 170.834 | 170.12 | 169.25 | 168.24 | 167.664
10:30 | 202.839 | 158.18 | 137.169 | 135.345 | 127.821 | 171.415 | 170.727 | 170.013 | 169.131 | 168.159 | 167.547
11:00 | 204.468 | 155.563 | 134.79 | 133.27 | 125.675 | 175.099 | 174.437 | 173.751 | 172.901 | 171.987 | 171.389
11:30 | 204.94 | 153.306 | 132.737 | 131.36 | 123.805 | 175.927 | 175.243 | 174.535 | 173.655 | 172.721 | 172.097
12:00 | 206.024 | 152.393 | 131.818 | 130.408 | 122.83 | 176.346 | 175.64 | 174.91 | 174.002 | 173.04 | 172.394
12:30 | 207.859 | 152.434 | 131.845 | 130.393 | 122.837 | 177.664 | 176.974 | 176.258 | 175.37 | 174.42 | 173.798
13:00 | 209.473 | 151.963 | 131.346 | 129.836 | 122.281 | 178.3 | 177.654 | 176.992 | 176.162 | 175.342 | 174.73
13:30 | 210.888 | 152.393 | 131.717 | 130.137 | 122.599 | 178.13 | 177.534 | 176.926 | 176.156 | 175.442 | 174.856
14:00 | 212.952 | 153.752 | 132.962 | 131.183 | 123.624 | 180.353 | 179.797 | 179.231 | 178.517 | 177.847 | 177.303
14:30 | 215.03 | 155.088 | 134.398 | 132.446 | 124.961 | 182.631 | 182.157 | 181.671 | 181.059 | 180.481 | 180.017
15:00 | 216.752 | 156.322 | 135.74 | 134.077 | 126.672 | 184.458 | 184.05 | 183.64 | 183.116 | 182.67 | 182.258
15:30 | 218.142 | 158.537 | 137.993 | 135.762 | 128.443 | 186.069 | 185.735 | 185.403 | 184.975 | 184.617 | 184.285
16:00 | 221.025 | 191.109 | 170.619 | 168.607 | 161.406 | 188.789 | 188.529 | 188.271 | 187.939 | 187.661 | 187.411
16:30 | 223.949 | 218.749 | 198.536 | 196.829 | 189.757 | 192.324 | 192.166 | 192.014 | 191.816 | 191.66 | 191.52
17:00 | 226.145 | 219.934 | 199.951 | 198.785 | 191.813 | 195.007 | 194.979 | 194.971 | 194.939 | 195.065 | 195.005
17:30 | 226.827 | 221.425 | 201.609 | 200.496 | 193.602 | 196.342 | 196.398 | 196.478 | 196.556 | 196.79 | 196.822
18:00 | 228.289 | 223.363 | 203.79 | 203.338 | 196.479 | 197.498 | 197.586 | 197.7 | 197.82 | 198.088 | 198.158
18:30 | 228.667 | 228.608 | 208.985 | 208.508 | 201.608 | 199.302 | 199.394 | 199.506 | 199.63 | 199.892 | 199.958
19:00 | 226.033 | 227.131 | 207.555 | 207.12 | 200.22 | 201.679 | 201.763 | 201.867 | 201.977 | 202.225 | 202.273
19:30 | 207.128 | 204.459 | 184.842 | 184.366 | 177.445 | 200.985 | 201.055 | 201.145 | 201.237 | 201.461 | 201.489
20:00 | 190.441 | 186.787 | 167.167 | 166.69 | 159.767 | 198.216 | 198.282 | 198.366 | 198.452 | 198.666 | 198.686
20:30 | 188.637 | 185.234 | 165.668 | 165.24 | 158.319 | 196.258 | 196.322 | 196.402 | 196.484 | 196.692 | 196.71
21:00 | 184.366 | 183.735 | 164.241 | 163.874 | 156.955 | 195.15 | 195.214 | 195.296 | 195.378 | 195.586 | 195.602
21:30 | 181.887 | 182.531 | 163.048 | 162.688 | 155.757 | 193.059 | 193.101 | 193.153 | 193.205 | 193.339 | 193.351
22:00 | 180.32 | 180.926 | 161.846 | 161.79 | 154.926 | 191.823 | 191.847 | 191.877 | 191.909 | 191.985 | 191.993
22:30 | 177.593 | 179.132 | 159.837 | 159.638 | 152.707 | 189.604 | 189.62 | 189.642 | 189.664 | 189.716 | 189.726
23:00 | 175.73 | 177.492 | 158.434 | 158.366 | 151.52 | 187.68 | 187.696 | 187.716 | 187.738 | 187.788 | 187.796
23:30 | 196.219 | 176.78 | 157.716 | 157.646 | 150.798 | 187.111 | 187.121 | 187.131 | 187.143 | 187.171 | 187.175
0:00 | 170.568 | 164.422 | 145.106 | 144.89 | 137.954 | 179.552 | 179.564 | 179.58 | 179.596 | 179.64 | 179.642

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 80.041 | 80.887 | 80.893 | 80.899 | 80.911 | 80.925 | 80.933 | 80.945 | 80.955 | 80.987 | 80.987
1:00 | 80.537 | 81.218 | 81.216 | 81.216 | 81.218 | 81.218 | 81.218 | 81.22 | 81.22 | 81.224 | 81.224
1:30 | 86.299 | 86.435 | 86.433 | 86.433 | 86.433 | 86.433 | 86.435 | 86.435 | 86.435 | 86.439 | 86.439
2:00 | 100.893 | 101.025 | 101.021 | 101.019 | 101.017 | 101.015 | 101.013 | 101.011 | 101.009 | 101.005 | 101.005
2:30 | 106.404 | 106.548 | 106.544 | 106.538 | 106.534 | 106.528 | 106.524 | 106.518 | 106.514 | 106.502 | 106.5
3:00 | 110.933 | 111.083 | 111.077 | 111.073 | 111.069 | 111.063 | 111.059 | 111.053 | 111.047 | 111.037 | 111.035
3:30 | 110.918 | 111.076 | 111.07 | 111.066 | 111.06 | 111.056 | 111.052 | 111.046 | 111.04 | 111.03 | 111.028
4:00 | 110.799 | 110.957 | 110.951 | 110.947 | 110.941 | 110.937 | 110.931 | 110.927 | 110.921 | 110.911 | 110.909
4:30 | 111.236 | 111.362 | 111.356 | 111.35 | 111.344 | 111.336 | 111.332 | 111.326 | 111.32 | 111.306 | 111.304
5:00 | 111.929 | 111.999 | 111.993 | 111.989 | 111.981 | 111.975 | 111.971 | 111.965 | 111.961 | 111.949 | 111.949
5:30 | 113.62 | 113.612 | 113.604 | 113.6 | 113.594 | 113.586 | 113.584 | 113.58 | 113.576 | 113.568 | 113.572
6:00 | 114.504 | 114.502 | 114.498 | 114.496 | 114.492 | 114.49 | 114.492 | 114.494 | 114.502 | 114.506 | 114.524
6:30 | 111.01 | 110.81 | 110.668 | 110.576 | 110.474 | 110.378 | 110.298 | 110.216 | 110.124 | 109.996 | 109.962
7:00 | 109.587 | 109.173 | 108.885 | 108.703 | 108.513 | 108.333 | 108.173 | 108.011 | 107.819 | 107.583 | 107.481
7:30 | 109.047 | 108.383 | 107.921 | 107.637 | 107.353 | 107.083 | 106.835 | 106.585 | 106.283 | 105.949 | 105.765
8:00 | 107.546 | 106.754 | 106.104 | 105.7 | 105.294 | 104.904 | 104.552 | 104.192 | 103.758 | 103.272 | 103.008
8:30 | 104.979 | 104.075 | 103.209 | 102.667 | 102.111 | 101.577 | 101.097 | 100.601 | 100.009 | 99.315 | 98.961
9:00 | 107.338 | 106.334 | 105.33 | 104.696 | 104.046 | 103.418 | 102.852 | 102.266 | 101.562 | 100.724 | 100.296
9:30 | 109.839 | 108.709 | 107.579 | 106.861 | 106.113 | 105.393 | 104.743 | 104.061 | 103.239 | 102.235 | 101.725
10:00 | 112.518 | 111.276 | 110.054 | 109.294 | 108.532 | 107.796 | 107.114 | 106.406 | 105.536 | 104.558 | 103.97
10:30 | 116.167 | 113.205 | 111.903 | 111.089 | 110.269 | 109.475 | 108.739 | 107.971 | 107.029 | 105.957 | 105.317
11:00 | 129.212 | 122.534 | 121.226 | 120.418 | 119.622 | 118.85 | 118.128 | 117.378 | 116.45 | 115.446 | 114.794
11:30 | 139.261 | 130.817 | 129.413 | 128.561 | 127.753 | 126.971 | 126.221 | 125.451 | 124.485 | 123.535 | 122.817
12:00 | 141.636 | 131.452 | 129.98 | 129.088 | 128.244 | 127.426 | 126.64 | 125.834 | 124.822 | 123.832 | 123.078
12:30 | 142.501 | 130.935 | 129.473 | 128.577 | 127.715 | 126.881 | 126.089 | 125.275 | 124.257 | 123.213 | 122.479
13:00 | 145.231 | 132.157 | 130.667 | 129.755 | 128.879 | 128.029 | 127.221 | 126.389 | 125.349 | 124.287 | 123.529
13:30 | 152.574 | 135.987 | 134.559 | 130.479 | 129.669 | 128.881 | 128.121 | 127.345 | 126.365 | 125.423 | 124.685
14:00 | 157.557 | 139.302 | 137.944 | 132.296 | 131.538 | 130.804 | 130.088 | 129.36 | 128.438 | 127.58 | 126.876
14:30 | 158.556 | 140.322 | 139.12 | 133.45 | 132.792 | 132.152 | 131.526 | 130.89 | 130.08 | 129.356 | 128.726
15:00 | 159.078 | 141.521 | 140.499 | 135.41 | 134.862 | 134.33 | 133.804 | 133.274 | 132.598 | 132.014 | 131.48
15:30 | 158.294 | 142.305 | 141.461 | 137.79 | 137.342 | 136.908 | 136.482 | 136.054 | 135.506 | 135.04 | 134.614
16:00 | 162.735 | 145.695 | 144.983 | 140.425 | 140.051 | 139.693 | 139.339 | 138.987 | 138.535 | 138.159 | 137.809
16:30 | 164.946 | 147.954 | 147.43 | 142.839 | 142.583 | 142.341 | 142.099 | 141.861 | 141.551 | 141.333 | 141.089
17:00 | 166.457 | 149.636 | 149.338 | 144.77 | 144.686 | 144.61 | 144.514 | 144.438 | 144.316 | 144.368 | 144.236
17:30 | 167.652 | 150.954 | 150.782 | 146.216 | 146.182 | 146.16 | 146.126 | 146.11 | 146.07 | 146.156 | 146.114
18:00 | 168.788 | 152.199 | 152.145 | 147.591 | 147.623 | 147.669 | 147.701 | 147.751 | 147.799 | 147.965 | 147.993
18:30 | 168.737 | 152.668 | 152.724 | 148.571 | 148.679 | 148.791 | 148.883 | 148.997 | 149.121 | 149.385 | 149.451
19:00 | 170.629 | 154.488 | 154.546 | 150.324 | 150.432 | 150.542 | 150.628 | 150.734 | 150.846 | 151.102 | 151.15
19:30 | 169.547 | 153.794 | 153.846 | 149.975 | 150.067 | 150.161 | 150.231 | 150.317 | 150.407 | 150.623 | 150.651
20:00 | 167.278 | 152.1 | 152.15 | 148.804 | 148.896 | 148.988 | 149.054 | 149.134 | 149.22 | 149.428 | 149.45
20:30 | 166.763 | 151.359 | 151.411 | 147.84 | 147.936 | 148.028 | 148.094 | 148.176 | 148.262 | 148.476 | 148.492
21:00 | 166.42 | 150.239 | 150.289 | 146.025 | 146.117 | 146.205 | 146.269 | 146.347 | 146.429 | 146.635 | 146.649
21:30 | 167.702 | 150.63 | 150.666 | 145.547 | 145.609 | 145.671 | 145.715 | 145.769 | 145.825 | 145.965 | 145.977
22:00 | 165.993 | 149.344 | 149.372 | 144.668 | 144.72 | 144.772 | 144.81 | 144.856 | 144.902 | 145.022 | 145.032
22:30 | 163.144 | 146.892 | 146.904 | 142.524 | 142.546 | 142.57 | 142.586 | 142.608 | 142.632 | 142.686 | 142.694
23:00 | 160.386 | 144.558 | 144.572 | 140.57 | 140.592 | 140.614 | 140.63 | 140.65 | 140.672 | 140.724 | 140.73
23:30 | 159.222 | 143.581 | 143.593 | 139.764 | 139.784 | 139.802 | 139.816 | 139.834 | 139.852 | 139.896 | 139.9
0:00 | 80.802 | 81.631 | 81.635 | 81.641 | 81.655 | 81.669 | 81.679 | 81.691 | 81.703 | 81.735 | 81.737

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 179.17 | 172.85
2017-03-01 01:00 | 178.32 | 172.18
2017-03-01 01:30 | 177.67 | 171.52
2017-03-01 02:00 | 177.45 | 171.27
2017-03-01 02:30 | 176.84 | 170.7
2017-03-01 03:00 | 176.57 | 170.33
2017-03-01 03:30 | 176.29 | 170.06
2017-03-01 04:00 | 175.89 | 169.81
2017-03-01 04:30 | 176.77 | 170.67
2017-03-01 05:00 | 177.69 | 171.63
2017-03-01 05:30 | 179.43 | 173.26
2017-03-01 06:00 | 181.13 | 174.95
2017-03-01 06:30 | 199.56 | 193.37
2017-03-01 07:00 | 205.69 | 199.48
2017-03-01 07:30 | 206.93 | 201.04
2017-03-01 08:00 | 207.23 | 201.67
2017-03-01 08:30 | 207.31 | 201.81
2017-03-01 09:00 | 207.57 | 201.67
2017-03-01 09:30 | 208.08 | 201.57
2017-03-01 10:00 | 209.19 | 202.82
2017-03-01 10:30 | 209.35 | 202.81
2017-03-01 11:00 | 210.48 | 204.05
2017-03-01 11:30 | 211.56 | 205.44
2017-03-01 12:00 | 212.59 | 206.54
2017-03-01 12:30 | 214.32 | 207.92
2017-03-01 13:00 | 215.75 | 209.42
2017-03-01 13:30 | 216.83 | 210.79
2017-03-01 14:00 | 217.12 | 211.33
2017-03-01 14:30 | 218.29 | 212.03
2017-03-01 15:00 | 219.48 | 213.03
2017-03-01 15:30 | 219.8 | 213.24
2017-03-01 16:00 | 221.15 | 214.39
2017-03-01 16:30 | 220.78 | 213.99
2017-03-01 17:00 | 221.54 | 214.69
2017-03-01 17:30 | 221.52 | 214.52
2017-03-01 18:00 | 222.59 | 215.44
2017-03-01 18:30 | 223.07 | 215.91
2017-03-01 19:00 | 224.38 | 217.51
2017-03-01 19:30 | 225.72 | 218.89
2017-03-01 20:00 | 224.19 | 217.18
2017-03-01 20:30 | 221.78 | 214.32
2017-03-01 21:00 | 218.88 | 210.86
2017-03-01 21:30 | 217.11 | 209.17
2017-03-01 22:00 | 215.25 | 207.57
2017-03-01 22:30 | 196.28 | 188.2
2017-03-01 23:00 | 188.32 | 179.78
2017-03-01 23:30 | 187.08 | 178.28
2017-03-02 | 185.11 | 176.86
2017-03-02 00:30 | 183.79 | 175.89
2017-03-02 01:00 | 183.17 | 175.07
2017-03-02 01:30 | 182.33 | 174.18
2017-03-02 02:00 | 181.91 | 173.75
2017-03-02 02:30 | 181.42 | 173.22
2017-03-02 03:00 | 181.32 | 173.15
2017-03-02 03:30 | 180.78 | 172.63
2017-03-02 04:00 | 180.68 | 172.5
2017-03-02 04:30 | 180.88 | 172.81
2017-03-02 05:00 | 181.41 | 173.71
2017-03-02 05:30 | 182.64 | 175.22
2017-03-02 06:00 | 184.35 | 176.55
2017-03-02 06:30 | 201.9 | 193.96
2017-03-02 07:00 | 208.82 | 200.74
2017-03-02 07:30 | 210.04 | 202.32
2017-03-02 08:00 | 211.04 | 203.68
2017-03-02 08:30 | 210.98 | 203.75
2017-03-02 09:00 | 210.3 | 202.94
2017-03-02 09:30 | 211.85 | 204.48
2017-03-02 10:00 | 213.65 | 206.34
2017-03-02 10:30 | 214.27 | 206.86
2017-03-02 11:00 | 216.28 | 209.07
2017-03-02 11:30 | 217.3 | 210.27
2017-03-02 12:00 | 217.19 | 209.98
2017-03-02 12:30 | 218.55 | 211.38
2017-03-02 13:00 | 219.93 | 212.76
2017-03-02 13:30 | 221.12 | 214.01
2017-03-02 14:00 | 222.65 | 215.59
2017-03-02 14:30 | 222.88 | 215.73
2017-03-02 15:00 | 224.41 | 217.18
2017-03-02 15:30 | 224.92 | 217.77
2017-03-02 16:00 | 224.2 | 217.1
2017-03-02 16:30 | 221.38 | 214.1
2017-03-02 17:00 | 222.38 | 214.89
2017-03-02 17:30 | 222.48 | 215.01
2017-03-02 18:00 | 223.71 | 216.33
2017-03-02 18:30 | 224.66 | 217.29
2017-03-02 19:00 | 226.18 | 218.88
2017-03-02 19:30 | 226.73 | 219.2
2017-03-02 20:00 | 224.57 | 216.83
2017-03-02 20:30 | 222.11 | 214.08
2017-03-02 21:00 | 219.7 | 211.27
2017-03-02 21:30 | 217.47 | 209.59
2017-03-02 22:00 | 213.93 | 206.15
2017-03-02 22:30 | 195.77 | 187.66
2017-03-02 23:00 | 189.27 | 180.85
2017-03-02 23:30 | 188.53 | 179.7
2017-03-03 | 187.03 | 178.31
2017-03-03 00:30 | 185.24 | 176.91
2017-03-03 01:00 | 184.2 | 175.71
2017-03-03 01:30 | 183.47 | 174.98
2017-03-03 02:00 | 182.87 | 174.3
2017-03-03 02:30 | 182.78 | 174.12
2017-03-03 03:00 | 182.36 | 173.59
2017-03-03 03:30 | 182.24 | 173.45
2017-03-03 04:00 | 182.27 | 173.5
2017-03-03 04:30 | 182.23 | 173.73
2017-03-03 05:00 | 182.88 | 174.59
2017-03-03 05:30 | 184.21 | 175.89
2017-03-03 06:00 | 186.86 | 178.11
2017-03-03 06:30 | 204.23 | 195.74
2017-03-03 07:00 | 210.19 | 202
2017-03-03 07:30 | 211.46 | 203.32
2017-03-03 08:00 | 212.18 | 203.98
2017-03-03 08:30 | 211.82 | 203.94
2017-03-03 09:00 | 213.8 | 205.91
2017-03-03 09:30 | 215.37 | 207.49
2017-03-03 10:00 | 215.82 | 207.98
2017-03-03 10:30 | 216.22 | 208.34
2017-03-03 11:00 | 217.31 | 209.93
2017-03-03 11:30 | 216.75 | 209.38
2017-03-03 12:00 | 219.19 | 211.92
2017-03-03 12:30 | 220.46 | 213.04
2017-03-03 13:00 | 221.56 | 214.1
2017-03-03 13:30 | 221.75 | 214.27
2017-03-03 14:00 | 222.27 | 214.74
2017-03-03 14:30 | 224.64 | 217.03
2017-03-03 15:00 | 223.48 | 215.56
2017-03-03 15:30 | 223.2 | 215.22
2017-03-03 16:00 | 223.18 | 215.34
2017-03-03 16:30 | 223.25 | 215.35
2017-03-03 17:00 | 222.9 | 214.93
2017-03-03 17:30 | 222.31 | 214.21
2017-03-03 18:00 | 221.33 | 212.92
2017-03-03 18:30 | 221.3 | 212.74
2017-03-03 19:00 | 221.74 | 213.32
2017-03-03 19:30 | 221.83 | 213.29
2017-03-03 20:00 | 220.11 | 211.32
2017-03-03 20:30 | 218.47 | 209.36
2017-03-03 21:00 | 216.98 | 207.32
2017-03-03 21:30 | 215.2 | 206.23
2017-03-03 22:00 | 213.11 | 204.41
2017-03-03 22:30 | 194.58 | 186.51
2017-03-03 23:00 | 186.53 | 178.39
2017-03-03 23:30 | 185.49 | 177.36
2017-03-04 | 183.98 | 175.64
2017-03-04 00:30 | 183.34 | 175.14
2017-03-04 01:00 | 182.38 | 174.31
2017-03-04 01:30 | 181.26 | 173.89
2017-03-04 02:00 | 180.96 | 173.7
2017-03-04 02:30 | 180.42 | 173.09
2017-03-04 03:00 | 180.23 | 172.82
2017-03-04 03:30 | 180.01 | 172.6
2017-03-04 04:00 | 179.47 | 172.07
2017-03-04 04:30 | 179.56 | 172.13
2017-03-04 05:00 | 180.18 | 172.78
2017-03-04 05:30 | 180.4 | 173.08
2017-03-04 06:00 | 180.88 | 173.56
2017-03-04 06:30 | 181.42 | 174.1
2017-03-04 07:00 | 181.81 | 174.35
2017-03-04 07:30 | 182.98 | 175.33
2017-03-04 08:00 | 183.16 | 175.58
2017-03-04 08:30 | 183.35 | 175.7
2017-03-04 09:00 | 184.52 | 176.42
2017-03-04 09:30 | 202.13 | 194.01
2017-03-04 10:00 | 207.1 | 198.41
2017-03-04 10:30 | 207 | 198.36
2017-03-04 11:00 | 206.47 | 198.3
2017-03-04 11:30 | 207.68 | 199.41
2017-03-04 12:00 | 208.32 | 200.04
2017-03-04 12:30 | 209.02 | 200.71
2017-03-04 13:00 | 210.26 | 201.98
2017-03-04 13:30 | 210.23 | 201.47
2017-03-04 14:00 | 210.24 | 201.36
2017-03-04 14:30 | 210.46 | 202.16
2017-03-04 15:00 | 209.58 | 201.33
2017-03-04 15:30 | 209.77 | 201.67
2017-03-04 16:00 | 210.12 | 201.8
2017-03-04 16:30 | 210.21 | 201.71
2017-03-04 17:00 | 210.24 | 201.71
2017-03-04 17:30 | 210.77 | 202.06
2017-03-04 18:00 | 211.74 | 203.18
2017-03-04 18:30 | 214.1 | 205.46
2017-03-04 19:00 | 215.64 | 207.17
2017-03-04 19:30 | 215.73 | 207.26
2017-03-04 20:00 | 214.07 | 205.51
2017-03-04 20:30 | 212.57 | 203.89
2017-03-04 21:00 | 210.61 | 201.69
2017-03-04 21:30 | 209.15 | 200.57
2017-03-04 22:00 | 207.3 | 198.91
2017-03-04 22:30 | 190.35 | 181.73
2017-03-04 23:00 | 182.8 | 174.09
2017-03-04 23:30 | 182.95 | 173.95
2017-03-05 | 181.52 | 172.28
2017-03-05 00:30 | 180.31 | 171.25
2017-03-05 01:00 | 179.5 | 170.64
2017-03-05 01:30 | 179.05 | 170.2
2017-03-05 02:00 | 178.05 | 169.9
2017-03-05 02:30 | 178.03 | 169.82
2017-03-05 03:00 | 177.71 | 169.42
2017-03-05 03:30 | 177.6 | 169.45
2017-03-05 04:00 | 177.44 | 169.26
2017-03-05 04:30 | 177.36 | 169.19
2017-03-05 05:00 | 177.79 | 169.63
2017-03-05 05:30 | 178.07 | 170.02
2017-03-05 06:00 | 178.1 | 169.83
2017-03-05 06:30 | 177.99 | 169.98
2017-03-05 07:00 | 178.08 | 170.19
2017-03-05 07:30 | 178.62 | 170.82
2017-03-05 08:00 | 179.29 | 171.06
2017-03-05 08:30 | 179.89 | 171.42
2017-03-05 09:00 | 180.24 | 171.8
2017-03-05 09:30 | 180.86 | 172.32
2017-03-05 10:00 | 181.38 | 172.77
2017-03-05 10:30 | 182.56 | 173.81
2017-03-05 11:00 | 184.16 | 175.67
2017-03-05 11:30 | 185.67 | 177.42
2017-03-05 12:00 | 187.02 | 179.19
2017-03-05 12:30 | 205.68 | 197.93
2017-03-05 13:00 | 211.47 | 203.63
2017-03-05 13:30 | 212.12 | 204.22
2017-03-05 14:00 | 212.42 | 204.68
2017-03-05 14:30 | 213.29 | 205.62
2017-03-05 15:00 | 215.03 | 207.32
2017-03-05 15:30 | 208.57 | 204.26
2017-03-05 16:00 | 206.25 | 203.55
2017-03-05 16:30 | 204.77 | 201.7
2017-03-05 17:00 | 204.89 | 201.81
2017-03-05 17:30 | 203.52 | 200.38
2017-03-05 18:00 | 202.13 | 199
2017-03-05 18:30 | 199.4 | 196.45
2017-03-05 19:00 | 197.91 | 194.84
2017-03-05 19:30 | 197.46 | 194.1
2017-03-05 20:00 | 200.71 | 197.23
2017-03-05 20:30 | 206.25 | 202.53
2017-03-05 21:00 | 207.97 | 204.14
2017-03-05 21:30 | 209.98 | 202.43
2017-03-05 22:00 | 211.16 | 202.22
2017-03-05 22:30 | 193 | 183.84
2017-03-05 23:00 | 184.9 | 175.16
2017-03-05 23:30 | 183.44 | 173.84
2017-03-06 | 186.14 | 176.85
2017-03-06 00:30 | 200.68 | 191.65
2017-03-06 01:00 | 200.06 | 192.2
2017-03-06 01:30 | 199.64 | 191.81
2017-03-06 02:00 | 198.71 | 191.45
2017-03-06 02:30 | 198.52 | 191.3
2017-03-06 03:00 | 198.83 | 191.46
2017-03-06 03:30 | 198.07 | 190.77
2017-03-06 04:00 | 198.82 | 191.68
2017-03-06 04:30 | 183.91 | 177.28
2017-03-06 05:00 | 179.18 | 172.68
2017-03-06 05:30 | 180.26 | 173.6
2017-03-06 06:00 | 181.41 | 174.48
2017-03-06 06:30 | 198.92 | 191.93
2017-03-06 07:00 | 204.27 | 197.38
2017-03-06 07:30 | 204.26 | 197.28
2017-03-06 08:00 | 205.84 | 198.79
2017-03-06 08:30 | 205.86 | 199.11
2017-03-06 09:00 | 206.31 | 199.58
2017-03-06 09:30 | 207.59 | 200.56
2017-03-06 10:00 | 209.5 | 201.11
2017-03-06 10:30 | 210.56 | 201.56
2017-03-06 11:00 | 211.48 | 203.05
2017-03-06 11:30 | 211.01 | 202.84
2017-03-06 12:00 | 210.77 | 203.23
2017-03-06 12:30 | 212.41 | 204.78
2017-03-06 13:00 | 214.75 | 207.34
2017-03-06 13:30 | 216.36 | 209.04
2017-03-06 14:00 | 220.4 | 211.01
2017-03-06 14:30 | 223.09 | 213.89
2017-03-06 15:00 | 224.33 | 214.66
2017-03-06 15:30 | 224.27 | 214.64
2017-03-06 16:00 | 206.86 | 200.64
2017-03-06 16:30 | 206.48 | 200.02
2017-03-06 17:00 | 207.02 | 200.11
2017-03-06 17:30 | 208.62 | 200.79
2017-03-06 18:00 | 208.47 | 200.2
2017-03-06 18:30 | 208.37 | 200.19
2017-03-06 19:00 | 208.23 | 200.32
2017-03-06 19:30 | 207.81 | 199.9
2017-03-06 20:00 | 209.77 | 201.65
2017-03-06 20:30 | 219.32 | 208.08
2017-03-06 21:00 | 221.72 | 208.93
2017-03-06 21:30 | 218.66 | 207.43
2017-03-06 22:00 | 216.56 | 205.29
2017-03-06 22:30 | 214.41 | 202.84
2017-03-06 23:00 | 212.43 | 200.87
2017-03-06 23:30 | 211.29 | 199.81
2017-03-07 | 209.16 | 198.42
2017-03-07 00:30 | 208.06 | 197.65
2017-03-07 01:00 | 206.1 | 197
2017-03-07 01:30 | 205.72 | 196.51
2017-03-07 02:00 | 205.25 | 196.22
2017-03-07 02:30 | 204.8 | 195.73
2017-03-07 03:00 | 204.47 | 195.36
2017-03-07 03:30 | 206.74 | 195.24
2017-03-07 04:00 | 206.96 | 195.22
2017-03-07 04:30 | 206.79 | 195.27
2017-03-07 05:00 | 206.63 | 194.7
2017-03-07 05:30 | 207.19 | 195.19
2017-03-07 06:00 | 208.41 | 196.19
2017-03-07 06:30 | 209.99 | 197.37
2017-03-07 07:00 | 211.2 | 198.56
2017-03-07 07:30 | 212.15 | 199.34
2017-03-07 08:00 | 212.77 | 200.23
2017-03-07 08:30 | 212.61 | 200.22
2017-03-07 09:00 | 212.7 | 200.46
2017-03-07 09:30 | 213.17 | 201.24
2017-03-07 10:00 | 215.03 | 203.54
2017-03-07 10:30 | 215.72 | 204.34
2017-03-07 11:00 | 216.42 | 204.87
2017-03-07 11:30 | 218.17 | 206.74
2017-03-07 12:00 | 219.34 | 207.49
2017-03-07 12:30 | 220.75 | 208.95
2017-03-07 13:00 | 222.41 | 210.75
2017-03-07 13:30 | 225.03 | 213.61
2017-03-07 14:00 | 226.57 | 215.69
2017-03-07 14:30 | 227.93 | 217.36
2017-03-07 15:00 | 228.68 | 217.95
2017-03-07 15:30 | 224.22 | 214.36
2017-03-07 16:00 | 208.1 | 201.22
2017-03-07 16:30 | 206.86 | 200.2
2017-03-07 17:00 | 205.87 | 199.27
2017-03-07 17:30 | 206.48 | 199.92
2017-03-07 18:00 | 206.43 | 199.72
2017-03-07 18:30 | 206.93 | 200.17
2017-03-07 19:00 | 225.93 | 216.18
2017-03-07 19:30 | 234.87 | 223.87
2017-03-07 20:00 | 255.29 | 245.04
2017-03-07 20:30 | 262.05 | 251.45
2017-03-07 21:00 | 259.58 | 248.65
2017-03-07 21:30 | 254.83 | 245.34
2017-03-07 22:00 | 251.51 | 243.49
2017-03-07 22:30 | 223.08 | 211.57
2017-03-07 23:00 | 208.24 | 198.18
2017-03-07 23:30 | 215.69 | 204.77
2017-03-08 | 214.1 | 202.51
2017-03-08 00:30 | 209.99 | 198.27
2017-03-08 01:00 | 206.34 | 196.25
2017-03-08 01:30 | 204.71 | 194.48
2017-03-08 02:00 | 201.23 | 190.46
2017-03-08 02:30 | 199.84 | 188.94
2017-03-08 03:00 | 199.01 | 188.2
2017-03-08 03:30 | 197.83 | 186.84
2017-03-08 04:00 | 197.28 | 186.25
2017-03-08 04:30 | 197.57 | 186.6
2017-03-08 05:00 | 198.61 | 187.85
2017-03-08 05:30 | 200.34 | 189.69
2017-03-08 06:00 | 202.55 | 191.46
2017-03-08 06:30 | 220.92 | 209.73
2017-03-08 07:00 | 226.8 | 215.27
2017-03-08 07:30 | 228.57 | 216.91
2017-03-08 08:00 | 229.1 | 217.59
2017-03-08 08:30 | 228.83 | 217.64
2017-03-08 09:00 | 228.17 | 217.19
2017-03-08 09:30 | 227.69 | 216.4
2017-03-08 10:00 | 227.55 | 216.27
2017-03-08 10:30 | 227.23 | 215.62
2017-03-08 11:00 | 226.03 | 214.51
2017-03-08 11:30 | 223.84 | 212.48
2017-03-08 12:00 | 220.38 | 208.61
2017-03-08 12:30 | 220.52 | 208.52
2017-03-08 13:00 | 221.34 | 208.97
2017-03-08 13:30 | 221.88 | 209.38
2017-03-08 14:00 | 221.9 | 209.34
2017-03-08 14:30 | 220.88 | 208.26
2017-03-08 15:00 | 220.83 | 207.62
2017-03-08 15:30 | 221.09 | 207.51
2017-03-08 16:00 | 221.73 | 207.6
2017-03-08 16:30 | 222 | 207.77
2017-03-08 17:00 | 221.42 | 207.2
2017-03-08 17:30 | 221.86 | 207.53
2017-03-08 18:00 | 222.81 | 208.36
2017-03-08 18:30 | 224.23 | 209.65
2017-03-08 19:00 | 223.29 | 210.38
2017-03-08 19:30 | 222.59 | 210.34
2017-03-08 20:00 | 220.52 | 207.92
2017-03-08 20:30 | 219.7 | 206.68
2017-03-08 21:00 | 218.4 | 204.9
2017-03-08 21:30 | 217.27 | 204.1
2017-03-08 22:00 | 215.86 | 203.24
2017-03-08 22:30 | 197.33 | 185.4
2017-03-08 23:00 | 190.68 | 178.42
2017-03-08 23:30 | 190.48 | 178.03
2017-03-09 | 188.85 | 177.15
2017-03-09 00:30 | 188.24 | 176.42
2017-03-09 01:00 | 187.9 | 175.84
2017-03-09 01:30 | 187.28 | 175.37
2017-03-09 02:00 | 186.45 | 175.19
2017-03-09 02:30 | 186.22 | 174.83
2017-03-09 03:00 | 186.21 | 174.88
2017-03-09 03:30 | 186.51 | 174.99
2017-03-09 04:00 | 186.6 | 174.95
2017-03-09 04:30 | 186.79 | 175.34
2017-03-09 05:00 | 186.83 | 175.8
2017-03-09 05:30 | 188.37 | 177.07
2017-03-09 06:00 | 190.2 | 178.35
2017-03-09 06:30 | 206.18 | 194.37
2017-03-09 07:00 | 215.34 | 203.49
2017-03-09 07:30 | 216.49 | 204.8
2017-03-09 08:00 | 216.53 | 204.98
2017-03-09 08:30 | 215.99 | 204.55
2017-03-09 09:00 | 215.53 | 204.14
2017-03-09 09:30 | 215.42 | 203.84
2017-03-09 10:00 | 215.22 | 203.49
2017-03-09 10:30 | 210.09 | 198.24
2017-03-09 11:00 | 215.89 | 204.24
2017-03-09 11:30 | 217.11 | 205.87
2017-03-09 12:00 | 218.89 | 207.94
2017-03-09 12:30 | 218.96 | 207.89
2017-03-09 13:00 | 220.03 | 209.12
2017-03-09 13:30 | 220.89 | 210.32
2017-03-09 14:00 | 221.26 | 210.93
2017-03-09 14:30 | 222.21 | 211.36
2017-03-09 15:00 | 222.89 | 211.87
2017-03-09 15:30 | 222.98 | 211.82
2017-03-09 16:00 | 223.79 | 212.76
2017-03-09 16:30 | 223.82 | 212.94
2017-03-09 17:00 | 224.25 | 213.23
2017-03-09 17:30 | 224.77 | 213.45
2017-03-09 18:00 | 225.94 | 214.6
2017-03-09 18:30 | 226.12 | 214.71
2017-03-09 19:00 | 227.87 | 216.39
2017-03-09 19:30 | 229.06 | 217.12
2017-03-09 20:00 | 227.24 | 214.89
2017-03-09 20:30 | 225.49 | 213.01
2017-03-09 21:00 | 223.67 | 210.46
2017-03-09 21:30 | 221.56 | 209.19
2017-03-09 22:00 | 219.03 | 206.88
2017-03-09 22:30 | 201.1 | 188.41
2017-03-09 23:00 | 194.07 | 180.81
2017-03-09 23:30 | 192.8 | 180.11
2017-03-10 | 190.49 | 178.7
2017-03-10 00:30 | 189.26 | 177.97
2017-03-10 01:00 | 159.47 | 147.44
2017-03-10 01:30 | 145.68 | 133.05
2017-03-10 02:00 | 145.19 | 132.51
2017-03-10 02:30 | 145.12 | 132.09
2017-03-10 03:00 | 144.62 | 131.84
2017-03-10 03:30 | 144.53 | 131.69
2017-03-10 04:00 | 144.25 | 131.53
2017-03-10 04:30 | 143.61 | 130.72
2017-03-10 05:00 | 144.15 | 131.07
2017-03-10 05:30 | 145.59 | 132.67
2017-03-10 06:00 | 177.03 | 164.53
2017-03-10 06:30 | 205.96 | 194.29
2017-03-10 07:00 | 211.22 | 199.72
2017-03-10 07:30 | 211.88 | 200.62
2017-03-10 08:00 | 213.45 | 200.84
2017-03-10 08:30 | 213.94 | 201.08
2017-03-10 09:00 | 213.61 | 200.73
2017-03-10 09:30 | 215.05 | 202.09
2017-03-10 10:00 | 215.12 | 202.25
2017-03-10 10:30 | 215.01 | 201.84
2017-03-10 11:00 | 216.48 | 203.49
2017-03-10 11:30 | 217.84 | 204.97
2017-03-10 12:00 | 218.37 | 205.7
2017-03-10 12:30 | 220.88 | 207.76
2017-03-10 13:00 | 222.37 | 209.14
2017-03-10 13:30 | 223.56 | 210.18
2017-03-10 14:00 | 223.97 | 210.68
2017-03-10 14:30 | 224.69 | 211.61
2017-03-10 15:00 | 224.17 | 211.4
2017-03-10 15:30 | 223.02 | 210.1
2017-03-10 16:00 | 223.91 | 210.9
2017-03-10 16:30 | 224.55 | 211.52
2017-03-10 17:00 | 226.17 | 213.2
2017-03-10 17:30 | 226.78 | 213.58
2017-03-10 18:00 | 227.71 | 214.49
2017-03-10 18:30 | 228.4 | 215.15
2017-03-10 19:00 | 229.92 | 216.39
2017-03-10 19:30 | 230.63 | 216.7
2017-03-10 20:00 | 229.06 | 214.63
2017-03-10 20:30 | 226.96 | 212.35
2017-03-10 21:00 | 224.5 | 210.08
2017-03-10 21:30 | 222.14 | 209.37
2017-03-10 22:00 | 220.07 | 208.05
2017-03-10 22:30 | 202.56 | 189.76
2017-03-10 23:00 | 195.69 | 182.48
2017-03-10 23:30 | 194.74 | 181.47
2017-03-11 | 192.86 | 180.35
2017-03-11 00:30 | 191.93 | 179.49
2017-03-11 01:00 | 162.56 | 149.4
2017-03-11 01:30 | 148.2 | 134.07
2017-03-11 02:00 | 147.58 | 133.52
2017-03-11 02:30 | 146.76 | 132.82
2017-03-11 03:00 | 147.06 | 132.62
2017-03-11 03:30 | 146.26 | 132.1
2017-03-11 04:00 | 145.7 | 132.04
2017-03-11 04:30 | 145.56 | 131.67
2017-03-11 05:00 | 146.27 | 132.32
2017-03-11 05:30 | 147.01 | 133.1
2017-03-11 06:00 | 146.82 | 132.21
2017-03-11 06:30 | 147.08 | 132.57
2017-03-11 07:00 | 148.16 | 134.05
2017-03-11 07:30 | 148.44 | 134.51
2017-03-11 08:00 | 150.8 | 136.87
2017-03-11 08:30 | 152.03 | 138.41
2017-03-11 09:00 | 153.24 | 139.54
2017-03-11 09:30 | 153.11 | 139.47
2017-03-11 10:00 | 153.43 | 139.84
2017-03-11 10:30 | 153.47 | 139.69
2017-03-11 11:00 | 158.03 | 144.18
2017-03-11 11:30 | 161.67 | 148.43
2017-03-11 12:00 | 166.25 | 153.22
2017-03-11 12:30 | 164.56 | 151.12
2017-03-11 13:00 | 187.65 | 175.2
2017-03-11 13:30 | 196.78 | 183.91
2017-03-11 14:00 | 201.01 | 185.93
2017-03-11 14:30 | 216.36 | 201.59
2017-03-11 15:00 | 224.48 | 209.87
2017-03-11 15:30 | 226.17 | 211.62
2017-03-11 16:00 | 227.15 | 212.76
2017-03-11 16:30 | 228.17 | 214.08
2017-03-11 17:00 | 229.52 | 215.61
2017-03-11 17:30 | 230.47 | 216.66
2017-03-11 18:00 | 231.13 | 217.23
2017-03-11 18:30 | 231.09 | 217.28
2017-03-11 19:00 | 231.57 | 217.81
2017-03-11 19:30 | 231.53 | 217.4
2017-03-11 20:00 | 229.72 | 214.82
2017-03-11 20:30 | 225.54 | 212.02
2017-03-11 21:00 | 222.62 | 209.77
2017-03-11 21:30 | 220.76 | 208.18
2017-03-11 22:00 | 218.86 | 206.31
2017-03-11 22:30 | 200.93 | 188.29
2017-03-11 23:00 | 166.03 | 152.25
2017-03-11 23:30 | 153 | 138.1
2017-03-12 | 150.92 | 136.62
2017-03-12 00:30 | 149.74 | 135.86
2017-03-12 01:00 | 148.49 | 134.28
2017-03-12 01:30 | 147.82 | 133.97
2017-03-12 02:00 | 147.95 | 134.25
2017-03-12 02:30 | 147.02 | 133.26
2017-03-12 03:00 | 146.17 | 132.57
2017-03-12 03:30 | 146.08 | 132.51
2017-03-12 04:00 | 145.52 | 131.85
2017-03-12 04:30 | 145.42 | 131.82
2017-03-12 05:00 | 146.14 | 132.73
2017-03-12 05:30 | 145.71 | 132.55
2017-03-12 06:00 | 146.29 | 133.16
2017-03-12 06:30 | 147.31 | 134.35
2017-03-12 07:00 | 157.46 | 144.98
2017-03-12 07:30 | 185.31 | 173.99
2017-03-12 08:00 | 187.79 | 176.03
2017-03-12 08:30 | 206.34 | 194.61
2017-03-12 09:00 | 207.85 | 195.49
2017-03-12 09:30 | 207.71 | 195.12
2017-03-12 10:00 | 208.42 | 195.85
2017-03-12 10:30 | 209.61 | 196.95
2017-03-12 11:00 | 211.02 | 198.07
2017-03-12 11:30 | 212.84 | 200.25
2017-03-12 12:00 | 214.67 | 202.42
2017-03-12 12:30 | 216.8 | 204.55
2017-03-12 13:00 | 219.76 | 207.86
2017-03-12 13:30 | 221.12 | 209.47
2017-03-12 14:00 | 221.07 | 209.88
2017-03-12 14:30 | 223.21 | 211.98
2017-03-12 15:00 | 223.69 | 212.22
2017-03-12 15:30 | 224.74 | 213.37
2017-03-12 16:00 | 224.75 | 213.66
2017-03-12 16:30 | 197.89 | 186.89
2017-03-12 17:00 | 198.51 | 187.61
2017-03-12 17:30 | 199.66 | 188.83
2017-03-12 18:00 | 200.64 | 189.81
2017-03-12 18:30 | 200.87 | 190.15
2017-03-12 19:00 | 201.49 | 190.68
2017-03-12 19:30 | 201.33 | 189.88
2017-03-12 20:00 | 199.01 | 187.35
2017-03-12 20:30 | 221.52 | 209.41
2017-03-12 21:00 | 224.75 | 212.02
2017-03-12 21:30 | 222.22 | 209.97
2017-03-12 22:00 | 219.45 | 207.19
2017-03-12 22:30 | 217.18 | 204.72
2017-03-12 23:00 | 215.25 | 202.46
2017-03-12 23:30 | 214.1 | 201
2017-03-13 | 212.86 | 199.49
2017-03-13 00:30 | 211.47 | 198.63
2017-03-13 01:00 | 210.02 | 197.7
2017-03-13 01:30 | 209.2 | 196.45
2017-03-13 02:00 | 208.54 | 195.76
2017-03-13 02:30 | 208 | 195.2
2017-03-13 03:00 | 207.87 | 195.05
2017-03-13 03:30 | 207.78 | 194.93
2017-03-13 04:00 | 207.53 | 194.54
2017-03-13 04:30 | 207.15 | 194.38
2017-03-13 05:00 | 207.47 | 194.93
2017-03-13 05:30 | 208.44 | 196.13
2017-03-13 06:00 | 209.14 | 197
2017-03-13 06:30 | 211.4 | 200.14
2017-03-13 07:00 | 213.28 | 201.61
2017-03-13 07:30 | 215.13 | 203.19
2017-03-13 08:00 | 215.27 | 203.55
2017-03-13 08:30 | 215.45 | 203.61
2017-03-13 09:00 | 215.62 | 203.65
2017-03-13 09:30 | 215.18 | 202.89
2017-03-13 10:00 | 215.73 | 203.31
2017-03-13 10:30 | 215.51 | 202.86
2017-03-13 11:00 | 216.92 | 204.43
2017-03-13 11:30 | 220.37 | 208.28
2017-03-13 12:00 | 223.31 | 211.88
2017-03-13 12:30 | 228.89 | 217.27
2017-03-13 13:00 | 230.26 | 218.41
2017-03-13 13:30 | 230.48 | 218.94
2017-03-13 14:00 | 231.47 | 220.2
2017-03-13 14:30 | 233.37 | 222.08
2017-03-13 15:00 | 234.61 | 223.32
2017-03-13 15:30 | 234.67 | 223.3
2017-03-13 16:00 | 235.66 | 224.45
2017-03-13 16:30 | 234.73 | 223.23
2017-03-13 17:00 | 234.43 | 222.69
2017-03-13 17:30 | 234.14 | 221.76
2017-03-13 18:00 | 234.34 | 221.7
2017-03-13 18:30 | 235.49 | 223.04
2017-03-13 19:00 | 236.53 | 224.5
2017-03-13 19:30 | 236.81 | 224.48
2017-03-13 20:00 | 219.22 | 206.66
2017-03-13 20:30 | 223.52 | 213.19
2017-03-13 21:00 | 225.54 | 215.43
2017-03-13 21:30 | 223.27 | 213.4
2017-03-13 22:00 | 220.96 | 211.17
2017-03-13 22:30 | 209.47 | 199.85
2017-03-13 23:00 | 208.82 | 199.46
2017-03-13 23:30 | 208.17 | 198.48
2017-03-14 | 207.15 | 197.44
2017-03-14 00:30 | 205.1 | 196.47
2017-03-14 01:00 | 203.98 | 195
2017-03-14 01:30 | 204.36 | 193.75
2017-03-14 02:00 | 203.88 | 193.16
2017-03-14 02:30 | 202.98 | 192.42
2017-03-14 03:00 | 202.47 | 192.05
2017-03-14 03:30 | 202.22 | 191.93
2017-03-14 04:00 | 202.26 | 192.06
2017-03-14 04:30 | 202.83 | 192.73
2017-03-14 05:00 | 203.13 | 193.09
2017-03-14 05:30 | 204.8 | 194.9
2017-03-14 06:00 | 206.21 | 196.35
2017-03-14 06:30 | 208.22 | 198.33
2017-03-14 07:00 | 210.9 | 199.73
2017-03-14 07:30 | 212.42 | 201.32
2017-03-14 08:00 | 213.08 | 201.87
2017-03-14 08:30 | 212.44 | 201.28
2017-03-14 09:00 | 212.9 | 201.57
2017-03-14 09:30 | 213.31 | 201.25
2017-03-14 10:00 | 214.43 | 202.29
2017-03-14 10:30 | 214.67 | 202.69
2017-03-14 11:00 | 214.79 | 202.93
2017-03-14 11:30 | 215.61 | 204.19
2017-03-14 12:00 | 217.34 | 205.65
2017-03-14 12:30 | 218.67 | 206.79
2017-03-14 13:00 | 220.24 | 208.28
2017-03-14 13:30 | 219.66 | 207.43
2017-03-14 14:00 | 219.86 | 207.45
2017-03-14 14:30 | 219.95 | 207.38
2017-03-14 15:00 | 220.21 | 207.53
2017-03-14 15:30 | 219.24 | 206.53
2017-03-14 16:00 | 220.96 | 208.64
2017-03-14 16:30 | 219.6 | 206.99
2017-03-14 17:00 | 221.24 | 208.94
2017-03-14 17:30 | 220.94 | 208.4
2017-03-14 18:00 | 221.23 | 208.57
2017-03-14 18:30 | 222.84 | 210.23
2017-03-14 19:00 | 225.19 | 212.89
2017-03-14 19:30 | 225.13 | 212.66
2017-03-14 20:00 | 222.44 | 209.62
2017-03-14 20:30 | 219.51 | 206.52
2017-03-14 21:00 | 217.16 | 203.34
2017-03-14 21:30 | 215.33 | 201.95
2017-03-14 22:00 | 212.34 | 200.1
2017-03-14 22:30 | 210.26 | 198.2
2017-03-14 23:00 | 208.22 | 195.88
2017-03-14 23:30 | 206.88 | 194.7
2017-03-15 | 205.63 | 192.91
2017-03-15 00:30 | 209.52 | 197.78
2017-03-15 01:00 | 210.06 | 199.4
2017-03-15 01:30 | 207.31 | 195.88
2017-03-15 02:00 | 206.66 | 195.03
2017-03-15 02:30 | 206.38 | 195.06
2017-03-15 03:00 | 206.57 | 195.41
2017-03-15 03:30 | 206.7 | 195.44
2017-03-15 04:00 | 206.55 | 195.25
2017-03-15 04:30 | 206.55 | 195.44
2017-03-15 05:00 | 206.83 | 196.15
2017-03-15 05:30 | 207.9 | 197.46
2017-03-15 06:00 | 209.18 | 199.12
2017-03-15 06:30 | 210.54 | 200.99
2017-03-15 07:00 | 213.79 | 202.28
2017-03-15 07:30 | 214.57 | 203.42
2017-03-15 08:00 | 214.65 | 203.97
2017-03-15 08:30 | 214.12 | 203.47
2017-03-15 09:00 | 213.81 | 203.16
2017-03-15 09:30 | 213.67 | 202.5
2017-03-15 10:00 | 215.37 | 203.77
2017-03-15 10:30 | 216.71 | 204.2
2017-03-15 11:00 | 218.69 | 206.23
2017-03-15 11:30 | 219.81 | 207.53
2017-03-15 12:00 | 220.85 | 208.3
2017-03-15 12:30 | 223.17 | 210.54
2017-03-15 13:00 | 222.76 | 209.81
2017-03-15 13:30 | 222.01 | 209.48
2017-03-15 14:00 | 216.39 | 204.23
2017-03-15 14:30 | 218.79 | 206.55
2017-03-15 15:00 | 222.84 | 210.42
2017-03-15 15:30 | 223.75 | 210.88
2017-03-15 16:00 | 222.84 | 209.81
2017-03-15 16:30 | 221.57 | 208.08
2017-03-15 17:00 | 220.65 | 206.73
2017-03-15 17:30 | 221.14 | 206.79
2017-03-15 18:00 | 221.64 | 207.32
2017-03-15 18:30 | 223.18 | 209.1
2017-03-15 19:00 | 224.18 | 209.97
2017-03-15 19:30 | 224.02 | 209.3
2017-03-15 20:00 | 222.46 | 207.49
2017-03-15 20:30 | 220.62 | 205.78
2017-03-15 21:00 | 218.72 | 203.34
2017-03-15 21:30 | 216.17 | 201.4
2017-03-15 22:00 | 212.4 | 199.19
2017-03-15 22:30 | 210.27 | 197.13
2017-03-15 23:00 | 208.41 | 195.17
2017-03-15 23:30 | 208.05 | 194.37
2017-03-16 | 207.16 | 193.35
2017-03-16 00:30 | 206.5 | 192.49
2017-03-16 01:00 | 205.14 | 191.97
2017-03-16 01:30 | 204.35 | 191.69
2017-03-16 02:00 | 203.97 | 191.3
2017-03-16 02:30 | 203.45 | 191.11
2017-03-16 03:00 | 202.64 | 190.44
2017-03-16 03:30 | 201.98 | 189.94
2017-03-16 04:00 | 201.57 | 189.75
2017-03-16 04:30 | 201.38 | 189.48
2017-03-16 05:00 | 201.32 | 189.45
2017-03-16 05:30 | 202.83 | 190.96
2017-03-16 06:00 | 204.54 | 192.44
2017-03-16 06:30 | 206.31 | 194.39
2017-03-16 07:00 | 208.75 | 196.17
2017-03-16 07:30 | 209.33 | 197.31
2017-03-16 08:00 | 209.49 | 197.7
2017-03-16 08:30 | 209.25 | 197.73
2017-03-16 09:00 | 209.2 | 197.81
2017-03-16 09:30 | 209.61 | 197.95
2017-03-16 10:00 | 210.76 | 198.94
2017-03-16 10:30 | 211.31 | 198.98
2017-03-16 11:00 | 212.21 | 199.89
2017-03-16 11:30 | 212.57 | 200.36
2017-03-16 12:00 | 213.26 | 201.48
2017-03-16 12:30 | 214.59 | 202.65
2017-03-16 13:00 | 216.62 | 204.59
2017-03-16 13:30 | 217.57 | 205.77
2017-03-16 14:00 | 218.23 | 206.64
2017-03-16 14:30 | 219.6 | 207.8
2017-03-16 15:00 | 220.07 | 208.34
2017-03-16 15:30 | 219.72 | 208.05
2017-03-16 16:00 | 220.63 | 209.07
2017-03-16 16:30 | 220.45 | 208.66
2017-03-16 17:00 | 221.51 | 209.61
2017-03-16 17:30 | 222.01 | 209.78
2017-03-16 18:00 | 222.31 | 209.96
2017-03-16 18:30 | 222.64 | 210.27
2017-03-16 19:00 | 224.16 | 211.85
2017-03-16 19:30 | 224.03 | 211.63
2017-03-16 20:00 | 221.04 | 208.55
2017-03-16 20:30 | 218.93 | 206.26
2017-03-16 21:00 | 217.61 | 204.24
2017-03-16 21:30 | 216.09 | 202.48
2017-03-16 22:00 | 212.89 | 199.97
2017-03-16 22:30 | 209.88 | 197.14
2017-03-16 23:00 | 207.25 | 194.88
2017-03-16 23:30 | 206.12 | 194.04
2017-03-17 | 204.11 | 193.2
2017-03-17 00:30 | 203.17 | 192.46
2017-03-17 01:00 | 202.23 | 191.67
2017-03-17 01:30 | 201.71 | 191.08
2017-03-17 02:00 | 201.23 | 190.44
2017-03-17 02:30 | 200.82 | 190.17
2017-03-17 03:00 | 200.24 | 189.85
2017-03-17 03:30 | 199.7 | 189.4
2017-03-17 04:00 | 199.37 | 189.3
2017-03-17 04:30 | 199.51 | 189.51
2017-03-17 05:00 | 195.14 | 185.33
2017-03-17 05:30 | 185.19 | 174.82
2017-03-17 06:00 | 187.83 | 176.15
2017-03-17 06:30 | 189.38 | 177.9
2017-03-17 07:00 | 191.7 | 179.26
2017-03-17 07:30 | 193.11 | 181.06
2017-03-17 08:00 | 193.32 | 181.36
2017-03-17 08:30 | 195.2 | 183.21
2017-03-17 09:00 | 196.59 | 184.62
2017-03-17 09:30 | 196.03 | 183.04
2017-03-17 10:00 | 195.06 | 181.83
2017-03-17 10:30 | 195.53 | 182.13
2017-03-17 11:00 | 196.5 | 183.32
2017-03-17 11:30 | 197.89 | 185.2
2017-03-17 12:00 | 198.77 | 186.63
2017-03-17 12:30 | 200.38 | 188.12
2017-03-17 13:00 | 201.47 | 189.11
2017-03-17 13:30 | 201.68 | 189.4
2017-03-17 14:00 | 202.06 | 189.88
2017-03-17 14:30 | 202.47 | 189.84
2017-03-17 15:00 | 203.53 | 191.09
2017-03-17 15:30 | 202.75 | 190.77
2017-03-17 16:00 | 205.06 | 193.43
2017-03-17 16:30 | 204.54 | 192.76
2017-03-17 17:00 | 204.94 | 193.04
2017-03-17 17:30 | 204.82 | 192.8
2017-03-17 18:00 | 205.23 | 193
2017-03-17 18:30 | 204.6 | 192.43
2017-03-17 19:00 | 206 | 194.31
2017-03-17 19:30 | 206.42 | 194.56
2017-03-17 20:00 | 204.68 | 192.56
2017-03-17 20:30 | 203.46 | 190.93
2017-03-17 21:00 | 201.47 | 188.6
2017-03-17 21:30 | 199.52 | 187.01
2017-03-17 22:00 | 196.8 | 184.75
2017-03-17 22:30 | 193.93 | 182.24
2017-03-17 23:00 | 191.77 | 180.49
2017-03-17 23:30 | 191.04 | 179.47
2017-03-18 | 189.69 | 177.88
2017-03-18 00:30 | 188.36 | 177
2017-03-18 01:00 | 187.21 | 176.24
2017-03-18 01:30 | 186.37 | 175.13
2017-03-18 02:00 | 185.99 | 174.7
2017-03-18 02:30 | 185.43 | 174.17
2017-03-18 03:00 | 184.84 | 173.64
2017-03-18 03:30 | 184.56 | 173.31
2017-03-18 04:00 | 184.19 | 172.79
2017-03-18 04:30 | 183.87 | 172.48
2017-03-18 05:00 | 183.9 | 172.46
2017-03-18 05:30 | 184.68 | 173.46
2017-03-18 06:00 | 184.71 | 173.85
2017-03-18 06:30 | 185.02 | 174.27
2017-03-18 07:00 | 186.46 | 174.54
2017-03-18 07:30 | 187.2 | 175.2
2017-03-18 08:00 | 187.71 | 175.62
2017-03-18 08:30 | 187.91 | 176.05
2017-03-18 09:00 | 188.45 | 176.49
2017-03-18 09:30 | 197.4 | 186.2
2017-03-18 10:00 | 197.96 | 186.49
2017-03-18 10:30 | 197.89 | 186.2
2017-03-18 11:00 | 191.5 | 177.98
2017-03-18 11:30 | 192.42 | 178.7
2017-03-18 12:00 | 193.21 | 179.52
2017-03-18 12:30 | 195.49 | 181.88
2017-03-18 13:00 | 196.73 | 183.47
2017-03-18 13:30 | 197.09 | 184.16
2017-03-18 14:00 | 196.7 | 183.11
2017-03-18 14:30 | 195.09 | 182.96
2017-03-18 15:00 | 186.06 | 174.71
2017-03-18 15:30 | 185.43 | 174.32
2017-03-18 16:00 | 192.21 | 180.94
2017-03-18 16:30 | 197.47 | 186.02
2017-03-18 17:00 | 198.64 | 187.43
2017-03-18 17:30 | 204.01 | 192.8
2017-03-18 18:00 | 211.15 | 199.91
2017-03-18 18:30 | 212.49 | 201.29
2017-03-18 19:00 | 214.61 | 203.52
2017-03-18 19:30 | 214.43 | 203.16
2017-03-18 20:00 | 213.41 | 201.91
2017-03-18 20:30 | 211.28 | 199.99
2017-03-18 21:00 | 211.28 | 199.52
2017-03-18 21:30 | 208.17 | 196.6
2017-03-18 22:00 | 208.26 | 197.18
2017-03-18 22:30 | 208.85 | 197.83
2017-03-18 23:00 | 208.55 | 197.67
2017-03-18 23:30 | 209.31 | 198.25
2017-03-19 | 209.08 | 197.75
2017-03-19 00:30 | 207.42 | 196.88
2017-03-19 01:00 | 207.06 | 196.28
2017-03-19 01:30 | 206.12 | 195.71
2017-03-19 02:00 | 205.12 | 195.09
2017-03-19 02:30 | 204.27 | 194.43
2017-03-19 03:00 | 203.59 | 193.91
2017-03-19 03:30 | 203.42 | 193.74
2017-03-19 04:00 | 202.97 | 193.59
2017-03-19 04:30 | 202.94 | 193.49
2017-03-19 05:00 | 203.12 | 193.74
2017-03-19 05:30 | 202.7 | 193.45
2017-03-19 06:00 | 202.52 | 193.3
2017-03-19 06:30 | 202.91 | 193.54
2017-03-19 07:00 | 202.54 | 193.63
2017-03-19 07:30 | 204.54 | 193.72
2017-03-19 08:00 | 207.01 | 194.99
2017-03-19 08:30 | 209.12 | 197.91
2017-03-19 09:00 | 209.68 | 198.45
2017-03-19 09:30 | 209.82 | 198.64
2017-03-19 10:00 | 211.15 | 199.43
2017-03-19 10:30 | 212.33 | 200.37
2017-03-19 11:00 | 211.87 | 199.88
2017-03-19 11:30 | 212.21 | 200.8
2017-03-19 12:00 | 213.52 | 202.68
2017-03-19 12:30 | 214.56 | 203.38
2017-03-19 13:00 | 214.48 | 202.57
2017-03-19 13:30 | 207.42 | 195.1
2017-03-19 14:00 | 204.56 | 192.93
2017-03-19 14:30 | 206.39 | 194.76
2017-03-19 15:00 | 206.61 | 195.44
2017-03-19 15:30 | 206.2 | 195.21
2017-03-19 16:00 | 206.49 | 195.41
2017-03-19 16:30 | 212.09 | 204.18
2017-03-19 17:00 | 220.15 | 214.37
2017-03-19 17:30 | 218.68 | 212.73
2017-03-19 18:00 | 218.2 | 212.24
2017-03-19 18:30 | 219.05 | 212.93
2017-03-19 19:00 | 212.15 | 205.72
2017-03-19 19:30 | 210.7 | 204.09
2017-03-19 20:00 | 212.49 | 205.89
2017-03-19 20:30 | 213.81 | 207.03
2017-03-19 21:00 | 214.75 | 208.23
2017-03-19 21:30 | 214.93 | 208.67
2017-03-19 22:00 | 209.28 | 198.55
2017-03-19 22:30 | 209.85 | 197.2
2017-03-19 23:00 | 208.47 | 195.86
2017-03-19 23:30 | 207.69 | 195.08
2017-03-20 | 205.99 | 193.83
2017-03-20 00:30 | 204.59 | 193.09
2017-03-20 01:00 | 203.85 | 192.32
2017-03-20 01:30 | 203.64 | 192.13
2017-03-20 02:00 | 203.45 | 192.01
2017-03-20 02:30 | 202.9 | 191.8
2017-03-20 03:00 | 202.08 | 191.61
2017-03-20 03:30 | 201.99 | 191.34
2017-03-20 04:00 | 201.76 | 190.97
2017-03-20 04:30 | 201.95 | 190.96
2017-03-20 05:00 | 202.55 | 191.63
2017-03-20 05:30 | 203.81 | 192.95
2017-03-20 06:00 | 205.42 | 194.1
2017-03-20 06:30 | 207.98 | 196.84
2017-03-20 07:00 | 210.54 | 198.71
2017-03-20 07:30 | 211.73 | 200.46
2017-03-20 08:00 | 211.29 | 200.88
2017-03-20 08:30 | 210.57 | 200.54
2017-03-20 09:00 | 211.23 | 201.03
2017-03-20 09:30 | 200 | 191.61
2017-03-20 10:00 | 213.36 | 208.59
2017-03-20 10:30 | 213.64 | 208.8
2017-03-20 11:00 | 212.71 | 207.65
2017-03-20 11:30 | 212.75 | 207.77
2017-03-20 12:00 | 211.43 | 206.52
2017-03-20 12:30 | 209.65 | 204.75
2017-03-20 13:00 | 207.9 | 202.73
2017-03-20 13:30 | 207.11 | 201.76
2017-03-20 14:00 | 206.89 | 201.4
2017-03-20 14:30 | 206.18 | 200.62
2017-03-20 15:00 | 205.02 | 199.31
2017-03-20 15:30 | 204.29 | 198.69
2017-03-20 16:00 | 203.67 | 198.16
2017-03-20 16:30 | 203.74 | 198.12
2017-03-20 17:00 | 203.75 | 197.94
2017-03-20 17:30 | 204.95 | 199.06
2017-03-20 18:00 | 205.02 | 199.18
2017-03-20 18:30 | 205.2 | 199.44
2017-03-20 19:00 | 204.28 | 198.63
2017-03-20 19:30 | 204.81 | 199.34
2017-03-20 20:00 | 205.54 | 200.17
2017-03-20 20:30 | 215.39 | 205.5
2017-03-20 21:00 | 218.2 | 206.69
2017-03-20 21:30 | 216.78 | 205.56
2017-03-20 22:00 | 215 | 203.41
2017-03-20 22:30 | 211.99 | 200.99
2017-03-20 23:00 | 210.47 | 199.64
2017-03-20 23:30 | 209.22 | 198.82
2017-03-21 | 206.83 | 197.48
2017-03-21 00:30 | 205.14 | 195.8
2017-03-21 01:00 | 203.8 | 194.54
2017-03-21 01:30 | 203.67 | 194.84
2017-03-21 02:00 | 205.39 | 194.85
2017-03-21 02:30 | 206.36 | 194.53
2017-03-21 03:00 | 205.98 | 194
2017-03-21 03:30 | 205.92 | 193.61
2017-03-21 04:00 | 205.95 | 193.58
2017-03-21 04:30 | 206.26 | 194.1
2017-03-21 05:00 | 207.49 | 195.23
2017-03-21 05:30 | 209.27 | 196.76
2017-03-21 06:00 | 211.06 | 198.15
2017-03-21 06:30 | 213.28 | 199.89
2017-03-21 07:00 | 215.63 | 201.63
2017-03-21 07:30 | 218.01 | 204.53
2017-03-21 08:00 | 218.23 | 205.4
2017-03-21 08:30 | 219.01 | 206.43
2017-03-21 09:00 | 219.42 | 206.8
2017-03-21 09:30 | 219.87 | 207.03
2017-03-21 10:00 | 220.3 | 207.83
2017-03-21 10:30 | 219.64 | 207.17
2017-03-21 11:00 | 220.28 | 207.9
2017-03-21 11:30 | 221.12 | 209.05
2017-03-21 12:00 | 221.93 | 210.04
2017-03-21 12:30 | 222.11 | 210.08
2017-03-21 13:00 | 222.1 | 210.08
2017-03-21 13:30 | 223.09 | 210.95
2017-03-21 14:00 | 223.22 | 211.39
2017-03-21 14:30 | 222.44 | 210.77
2017-03-21 15:00 | 222.74 | 210.87
2017-03-21 15:30 | 222.77 | 211.05
2017-03-21 16:00 | 223.11 | 211.43
2017-03-21 16:30 | 223.18 | 210.98
2017-03-21 17:00 | 223.59 | 210.62
2017-03-21 17:30 | 223.13 | 209.83
2017-03-21 18:00 | 223.91 | 210.68
2017-03-21 18:30 | 225.48 | 212.36
2017-03-21 19:00 | 226.83 | 213.99
2017-03-21 19:30 | 225.23 | 212.21
2017-03-21 20:00 | 223.7 | 210.36
2017-03-21 20:30 | 222.23 | 208.45
2017-03-21 21:00 | 220.42 | 206.1
2017-03-21 21:30 | 220.14 | 205.18
2017-03-21 22:00 | 217.97 | 203.23
2017-03-21 22:30 | 215.92 | 200.93
2017-03-21 23:00 | 214.35 | 199.44
2017-03-21 23:30 | 213.14 | 198.42
2017-03-22 | 211.38 | 197.25
2017-03-22 00:30 | 210.03 | 196.08
2017-03-22 01:00 | 208.1 | 194.67
2017-03-22 01:30 | 207.45 | 194.22
2017-03-22 02:00 | 206.31 | 193.79
2017-03-22 02:30 | 206.2 | 193.76
2017-03-22 03:00 | 205.81 | 193.46
2017-03-22 03:30 | 205.28 | 193.07
2017-03-22 04:00 | 205.38 | 193.08
2017-03-22 04:30 | 205.83 | 192.89
2017-03-22 05:00 | 206.7 | 193.59
2017-03-22 05:30 | 207.63 | 195.15
2017-03-22 06:00 | 209.48 | 196.66
2017-03-22 06:30 | 212.09 | 198.51
2017-03-22 07:00 | 214.6 | 200.79
2017-03-22 07:30 | 216.59 | 203.71
2017-03-22 08:00 | 217.08 | 204.19
2017-03-22 08:30 | 217.41 | 204.43
2017-03-22 09:00 | 216.59 | 203.69
2017-03-22 09:30 | 216.81 | 203.42
2017-03-22 10:00 | 217.22 | 203.96
2017-03-22 10:30 | 217.19 | 204.19
2017-03-22 11:00 | 217.35 | 204.62
2017-03-22 11:30 | 218.6 | 205.85
2017-03-22 12:00 | 219.66 | 206.93
2017-03-22 12:30 | 219.78 | 207.07
2017-03-22 13:00 | 220.66 | 207.96
2017-03-22 13:30 | 221.92 | 209
2017-03-22 14:00 | 223.22 | 210.82
2017-03-22 14:30 | 221.74 | 209.66
2017-03-22 15:00 | 221.19 | 208.65
2017-03-22 15:30 | 221.73 | 209.21
2017-03-22 16:00 | 221.65 | 209.38
2017-03-22 16:30 | 222.1 | 209.73
2017-03-22 17:00 | 222.47 | 209.97
2017-03-22 17:30 | 222.42 | 209.89
2017-03-22 18:00 | 224.12 | 211.84
2017-03-22 18:30 | 225.08 | 212.67
2017-03-22 19:00 | 225.19 | 212.72
2017-03-22 19:30 | 224.17 | 211.44
2017-03-22 20:00 | 221.81 | 208.97
2017-03-22 20:30 | 220.3 | 207.19
2017-03-22 21:00 | 219.88 | 206.45
2017-03-22 21:30 | 218.92 | 205.5
2017-03-22 22:00 | 216.54 | 203.29
2017-03-22 22:30 | 214.27 | 200.36
2017-03-22 23:00 | 213.21 | 198.67
2017-03-22 23:30 | 212.62 | 197.89
2017-03-23 | 210.9 | 196.57
2017-03-23 00:30 | 209.53 | 195.6
2017-03-23 01:00 | 207.65 | 194.69
2017-03-23 01:30 | 205.16 | 193.98
2017-03-23 02:00 | 204.7 | 193.56
2017-03-23 02:30 | 204.7 | 193.7
2017-03-23 03:00 | 204.23 | 193.17
2017-03-23 03:30 | 204.34 | 192.79
2017-03-23 04:00 | 204.12 | 192.52
2017-03-23 04:30 | 204.67 | 193.01
2017-03-23 05:00 | 205.86 | 193.96
2017-03-23 05:30 | 207.39 | 195.68
2017-03-23 06:00 | 209.09 | 197.25
2017-03-23 06:30 | 210.91 | 199.28
2017-03-23 07:00 | 212.66 | 200.73
2017-03-23 07:30 | 202.87 | 191.84
2017-03-23 08:00 | 195.46 | 184.74
2017-03-23 08:30 | 194.78 | 184.51
2017-03-23 09:00 | 194.93 | 184.49
2017-03-23 09:30 | 194.13 | 183.52
2017-03-23 10:00 | 194.51 | 184.04
2017-03-23 10:30 | 194.67 | 184.44
2017-03-23 11:00 | 195.25 | 185.28
2017-03-23 11:30 | 196.33 | 186.62
2017-03-23 12:00 | 197.25 | 187.61
2017-03-23 12:30 | 198.01 | 188.3
2017-03-23 13:00 | 198.45 | 188.91
2017-03-23 13:30 | 198.93 | 189.45
2017-03-23 14:00 | 198.46 | 189.04
2017-03-23 14:30 | 200.3 | 190.95
2017-03-23 15:00 | 199.95 | 190.73
2017-03-23 15:30 | 199.62 | 190.02
2017-03-23 16:00 | 199.08 | 189.57
2017-03-23 16:30 | 200.84 | 191.26
2017-03-23 17:00 | 202.09 | 192.51
2017-03-23 17:30 | 201.23 | 191.4
2017-03-23 18:00 | 203.1 | 193.31
2017-03-23 18:30 | 205.66 | 194.94
2017-03-23 19:00 | 207.01 | 196.4
2017-03-23 19:30 | 205.28 | 194.49
2017-03-23 20:00 | 203.45 | 192.03
2017-03-23 20:30 | 202.25 | 190.12
2017-03-23 21:00 | 200.33 | 187.87
2017-03-23 21:30 | 198.12 | 185.97
2017-03-23 22:00 | 195.54 | 183.24
2017-03-23 22:30 | 193.4 | 180.39
2017-03-23 23:00 | 192.12 | 179.04
2017-03-23 23:30 | 191.95 | 178.66
2017-03-24 | 190.11 | 177.27
2017-03-24 00:30 | 189.01 | 176.08
2017-03-24 01:00 | 187.97 | 174.94
2017-03-24 01:30 | 187.4 | 174.34
2017-03-24 02:00 | 186.95 | 174.06
2017-03-24 02:30 | 186.87 | 173.84
2017-03-24 03:00 | 186.73 | 173.55
2017-03-24 03:30 | 186.35 | 173.33
2017-03-24 04:00 | 185.5 | 172.18
2017-03-24 04:30 | 185.85 | 172.56
2017-03-24 05:00 | 187 | 173.22
2017-03-24 05:30 | 187.54 | 174.63
2017-03-24 06:00 | 189.32 | 176.25
2017-03-24 06:30 | 190.64 | 177.88
2017-03-24 07:00 | 192.98 | 180.68
2017-03-24 07:30 | 195.54 | 183.2
2017-03-24 08:00 | 196.34 | 184.09
2017-03-24 08:30 | 196.56 | 184.71
2017-03-24 09:00 | 196.9 | 185.29
2017-03-24 09:30 | 197.24 | 185.13
2017-03-24 10:00 | 197.54 | 185.49
2017-03-24 10:30 | 197.75 | 185.76
2017-03-24 11:00 | 197.09 | 186.28
2017-03-24 11:30 | 198.46 | 189.59
2017-03-24 12:00 | 199.06 | 190.37
2017-03-24 12:30 | 200.99 | 192.14
2017-03-24 13:00 | 200.32 | 191.44
2017-03-24 13:30 | 201.96 | 192.72
2017-03-24 14:00 | 203.37 | 194.13
2017-03-24 14:30 | 205.12 | 196.26
2017-03-24 15:00 | 205.56 | 196.6
2017-03-24 15:30 | 204.18 | 195.2
2017-03-24 16:00 | 204.22 | 195.32
2017-03-24 16:30 | 205.1 | 196.56
2017-03-24 17:00 | 205.92 | 197.56
2017-03-24 17:30 | 206.24 | 197.69
2017-03-24 18:00 | 206.48 | 198.01
2017-03-24 18:30 | 206.58 | 198.29
2017-03-24 19:00 | 205.93 | 198.16
2017-03-24 19:30 | 205.75 | 197.74
2017-03-24 20:00 | 203.88 | 195.39
2017-03-24 20:30 | 202.61 | 193.47
2017-03-24 21:00 | 200.21 | 190.97
2017-03-24 21:30 | 198.65 | 189.21
2017-03-24 22:00 | 196.99 | 187.38
2017-03-24 22:30 | 195.42 | 184.77
2017-03-24 23:00 | 193.84 | 182.92
2017-03-24 23:30 | 192.34 | 181.6
2017-03-25 | 190.66 | 180.17
2017-03-25 00:30 | 173.73 | 163.11
2017-03-25 01:00 | 166.81 | 156.29
2017-03-25 01:30 | 165.95 | 155.76
2017-03-25 02:00 | 164.43 | 155.58
2017-03-25 02:30 | 165.18 | 154.89
2017-03-25 03:00 | 164.88 | 154.75
2017-03-25 03:30 | 164.94 | 154.59
2017-03-25 04:00 | 164.45 | 154.08
2017-03-25 04:30 | 164.75 | 154.16
2017-03-25 05:00 | 164.75 | 154.28
2017-03-25 05:30 | 164.89 | 154.73
2017-03-25 06:00 | 165.31 | 155.32
2017-03-25 06:30 | 167.32 | 156.18
2017-03-25 07:00 | 168 | 156.85
2017-03-25 07:30 | 168.65 | 157.81
2017-03-25 08:00 | 169.38 | 158.15
2017-03-25 08:30 | 170.51 | 158.99
2017-03-25 09:00 | 171.28 | 159.57
2017-03-25 09:30 | 172.59 | 161
2017-03-25 10:00 | 173.22 | 161.21
2017-03-25 10:30 | 174.41 | 161.58
2017-03-25 11:00 | 174.41 | 161.86
2017-03-25 11:30 | 174.9 | 162.81
2017-03-25 12:00 | 176.27 | 164.36
2017-03-25 12:30 | 177.09 | 164.92
2017-03-25 13:00 | 176.27 | 164.17
2017-03-25 13:30 | 179.06 | 167.3
2017-03-25 14:00 | 179.56 | 168.01
2017-03-25 14:30 | 180.69 | 168.33
2017-03-25 15:00 | 182 | 168.42
2017-03-25 15:30 | 183.61 | 170.02
2017-03-25 16:00 | 199.72 | 186.1
2017-03-25 16:30 | 206.12 | 192.75
2017-03-25 17:00 | 206.63 | 193.36
2017-03-25 17:30 | 207.18 | 194.22
2017-03-25 18:00 | 207.18 | 194.51
2017-03-25 18:30 | 207.85 | 195.34
2017-03-25 19:00 | 208.85 | 196.38
2017-03-25 19:30 | 208.14 | 195.19
2017-03-25 20:00 | 206.54 | 193.34
2017-03-25 20:30 | 205.86 | 192.22
2017-03-25 21:00 | 204.6 | 190.4
2017-03-25 21:30 | 203.33 | 188.72
2017-03-25 22:00 | 201.37 | 186.85
2017-03-25 22:30 | 199 | 185.14
2017-03-25 23:00 | 197.34 | 183.29
2017-03-25 23:30 | 195.8 | 182.22
2017-03-26 | 193.96 | 180.7
2017-03-26 00:30 | 192.79 | 179.74
2017-03-26 01:00 | 190.97 | 178.97
2017-03-26 01:30 | 189.98 | 178.18
2017-03-26 02:00 | 188.98 | 177.56
2017-03-26 02:30 | 172.63 | 161.22
2017-03-26 03:00 | 166.34 | 155.31
2017-03-26 03:30 | 166.12 | 154.82
2017-03-26 04:00 | 166.04 | 154
2017-03-26 04:30 | 165.98 | 154.3
2017-03-26 05:00 | 166.38 | 154.71
2017-03-26 05:30 | 167.08 | 155.47
2017-03-26 06:00 | 174.3 | 162.95
2017-03-26 06:30 | 189.7 | 178.14
2017-03-26 07:00 | 189.84 | 178.28
2017-03-26 07:30 | 189.73 | 178.91
2017-03-26 08:00 | 191.2 | 179.42
2017-03-26 08:30 | 190.59 | 178.87
2017-03-26 09:00 | 194.4 | 182.25
2017-03-26 09:30 | 197.04 | 183.49
2017-03-26 10:00 | 197.75 | 184.12
2017-03-26 10:30 | 197.3 | 183.68
2017-03-26 11:00 | 198.16 | 184.78
2017-03-26 11:30 | 199.1 | 186.45
2017-03-26 12:00 | 199.75 | 187.33
2017-03-26 12:30 | 199.28 | 186.54
2017-03-26 13:00 | 199.34 | 186.6
2017-03-26 13:30 | 199.66 | 187.28
2017-03-26 14:00 | 201.01 | 188.71
2017-03-26 14:30 | 202.12 | 189.94
2017-03-26 15:00 | 203.54 | 191.53
2017-03-26 15:30 | 206.32 | 194.87
2017-03-26 16:00 | 207.68 | 196.06
2017-03-26 16:30 | 209.41 | 197.32
2017-03-26 17:00 | 209.44 | 197.62
2017-03-26 17:30 | 210.74 | 199.19
2017-03-26 18:00 | 210.97 | 199.66
2017-03-26 18:30 | 211.5 | 200.23
2017-03-26 19:00 | 213.62 | 201.93
2017-03-26 19:30 | 212.86 | 200.76
2017-03-26 20:00 | 211.06 | 198.38
2017-03-26 20:30 | 207.65 | 196.21
2017-03-26 21:00 | 205.01 | 193.28
2017-03-26 21:30 | 202.77 | 191.06
2017-03-26 22:00 | 200.38 | 188.13
2017-03-26 22:30 | 197.31 | 185.11
2017-03-26 23:00 | 195.07 | 182.63
2017-03-26 23:30 | 193.32 | 181.53
2017-03-27 | 192.02 | 180.17
2017-03-27 00:30 | 190.52 | 178.96
2017-03-27 01:00 | 188.79 | 177.85
2017-03-27 01:30 | 188.18 | 177.08
2017-03-27 02:00 | 187.67 | 176.79
2017-03-27 02:30 | 187.08 | 176.32
2017-03-27 03:00 | 186.54 | 176.08
2017-03-27 03:30 | 185.85 | 175.78
2017-03-27 04:00 | 185.69 | 175.63
2017-03-27 04:30 | 186.94 | 176.46
2017-03-27 05:00 | 187.75 | 177.08
2017-03-27 05:30 | 188.68 | 178.29
2017-03-27 06:00 | 190.24 | 179.92
2017-03-27 06:30 | 193.34 | 182.1
2017-03-27 07:00 | 196.71 | 184.88
2017-03-27 07:30 | 198.27 | 187.16
2017-03-27 08:00 | 199.02 | 187.89
2017-03-27 08:30 | 198.44 | 187.71
2017-03-27 09:00 | 199.09 | 188.42
2017-03-27 09:30 | 200.05 | 189.08
2017-03-27 10:00 | 200.01 | 189.16
2017-03-27 10:30 | 200.34 | 189.48
2017-03-27 11:00 | 201 | 190.17
2017-03-27 11:30 | 201.54 | 191.22
2017-03-27 12:00 | 201.1 | 190.96
2017-03-27 12:30 | 201.24 | 190.99
2017-03-27 13:00 | 202.29 | 192.17
2017-03-27 13:30 | 203.44 | 193.29
2017-03-27 14:00 | 204.2 | 194.23
2017-03-27 14:30 | 205.47 | 195.84
2017-03-27 15:00 | 205.01 | 195.6
2017-03-27 15:30 | 203.8 | 194.39
2017-03-27 16:00 | 204.06 | 194.72
2017-03-27 16:30 | 204.1 | 195.04
2017-03-27 17:00 | 205.19 | 196.23
2017-03-27 17:30 | 205.82 | 196.4
2017-03-27 18:00 | 207.2 | 197.83
2017-03-27 18:30 | 208.31 | 199.11
2017-03-27 19:00 | 210.65 | 201.98
2017-03-27 19:30 | 209.78 | 200.9
2017-03-27 20:00 | 207.34 | 198.2
2017-03-27 20:30 | 205.18 | 195.18
2017-03-27 21:00 | 202.22 | 191.84
2017-03-27 21:30 | 200.65 | 189.76
2017-03-27 22:00 | 197.57 | 186.75
2017-03-27 22:30 | 194.88 | 183.63
2017-03-27 23:00 | 192.96 | 181.46
2017-03-27 23:30 | 191.02 | 180.48
2017-03-28 | 187.8 | 178.2
2017-03-28 00:30 | 186.7 | 177.92
2017-03-28 01:00 | 186.2 | 176.92
2017-03-28 01:30 | 186.91 | 177.56
2017-03-28 02:00 | 186.6 | 177.21
2017-03-28 02:30 | 186.21 | 176.84
2017-03-28 03:00 | 185.45 | 176.54
2017-03-28 03:30 | 185.02 | 175.92
2017-03-28 04:00 | 186.7 | 175.8
2017-03-28 04:30 | 186.59 | 176.11
2017-03-28 05:00 | 187.26 | 176.88
2017-03-28 05:30 | 188.89 | 178.23
2017-03-28 06:00 | 191.16 | 179.63
2017-03-28 06:30 | 193.88 | 181.13
2017-03-28 07:00 | 196.92 | 182.54
2017-03-28 07:30 | 197.95 | 184.1
2017-03-28 08:00 | 198.97 | 185.03
2017-03-28 08:30 | 200.08 | 186.52
2017-03-28 09:00 | 200.89 | 187.48
2017-03-28 09:30 | 200.75 | 187.4
2017-03-28 10:00 | 200.52 | 186.78
2017-03-28 10:30 | 200.18 | 186.44
2017-03-28 11:00 | 199.9 | 186.51
2017-03-28 11:30 | 200.41 | 187.39
2017-03-28 12:00 | 200.04 | 187.29
2017-03-28 12:30 | 200.55 | 188.51
2017-03-28 13:00 | 202.14 | 190.48
2017-03-28 13:30 | 205.24 | 193.74
2017-03-28 14:00 | 206.87 | 195.74
2017-03-28 14:30 | 208.43 | 197.64
2017-03-28 15:00 | 208.04 | 197.39
2017-03-28 15:30 | 208.46 | 197.8
2017-03-28 16:00 | 209.06 | 198.33
2017-03-28 16:30 | 209.27 | 198.18
2017-03-28 17:00 | 208.88 | 197.55
2017-03-28 17:30 | 209.28 | 197.96
2017-03-28 18:00 | 210.58 | 199.28
2017-03-28 18:30 | 211.94 | 200.77
2017-03-28 19:00 | 213.71 | 202.93
2017-03-28 19:30 | 213.23 | 202.43
2017-03-28 20:00 | 210.43 | 199.07
2017-03-28 20:30 | 208.43 | 196.17
2017-03-28 21:00 | 206.1 | 192.75
2017-03-28 21:30 | 203.65 | 190.45
2017-03-28 22:00 | 200.37 | 187.18
2017-03-28 22:30 | 198.9 | 184.48
2017-03-28 23:00 | 196.58 | 182.12
2017-03-28 23:30 | 195.13 | 181.4
2017-03-29 | 193.53 | 179.56
2017-03-29 00:30 | 192.24 | 178.6
2017-03-29 01:00 | 191.27 | 177.77
2017-03-29 01:30 | 190.72 | 177.23
2017-03-29 02:00 | 190.02 | 176.73
2017-03-29 02:30 | 188.91 | 176.22
2017-03-29 03:00 | 188.68 | 175.64
2017-03-29 03:30 | 188.43 | 175.66
2017-03-29 04:00 | 188 | 175.06
2017-03-29 04:30 | 188.53 | 175.59
2017-03-29 05:00 | 189.99 | 176.46
2017-03-29 05:30 | 191.05 | 177.47
2017-03-29 06:00 | 192.65 | 179.3
2017-03-29 06:30 | 195.83 | 181.8
2017-03-29 07:00 | 197.64 | 183.54
2017-03-29 07:30 | 198.98 | 184.96
2017-03-29 08:00 | 199.9 | 185.78
2017-03-29 08:30 | 200.23 | 186.3
2017-03-29 09:00 | 201.01 | 186.89
2017-03-29 09:30 | 201.11 | 187.04
2017-03-29 10:00 | 200.63 | 186.84
2017-03-29 10:30 | 201.24 | 188.12
2017-03-29 11:00 | 200.28 | 187.1
2017-03-29 11:30 | 202.99 | 190.03
2017-03-29 12:00 | 203.63 | 190.59
2017-03-29 12:30 | 205.53 | 192.7
2017-03-29 13:00 | 206.74 | 194.3
2017-03-29 13:30 | 208.3 | 196.17
2017-03-29 14:00 | 208.12 | 196.57
2017-03-29 14:30 | 207.64 | 196.29
2017-03-29 15:00 | 207.54 | 196.19
2017-03-29 15:30 | 207.22 | 195.78
2017-03-29 16:00 | 205.77 | 194.4
2017-03-29 16:30 | 204.65 | 192.97
2017-03-29 17:00 | 204.86 | 192.54
2017-03-29 17:30 | 204.75 | 191.7
2017-03-29 18:00 | 206.16 | 193.06
2017-03-29 18:30 | 207.77 | 194.68
2017-03-29 19:00 | 209.5 | 196.64
2017-03-29 19:30 | 208.33 | 195.05
2017-03-29 20:00 | 206.41 | 192.97
2017-03-29 20:30 | 204.92 | 191.13
2017-03-29 21:00 | 203.56 | 189.37
2017-03-29 21:30 | 201.71 | 187.84
2017-03-29 22:00 | 199.34 | 185.21
2017-03-29 22:30 | 197.78 | 182.91
2017-03-29 23:00 | 196.2 | 181.39
2017-03-29 23:30 | 195.83 | 181.46
2017-03-30 | 194.66 | 180.53
2017-03-30 00:30 | 192.92 | 178.98
2017-03-30 01:00 | 190.86 | 176.84
2017-03-30 01:30 | 189.86 | 175.9
2017-03-30 02:00 | 190.07 | 176.01
2017-03-30 02:30 | 189.54 | 175.61
2017-03-30 03:00 | 188.88 | 175.18
2017-03-30 03:30 | 188.21 | 174.57
2017-03-30 04:00 | 187.75 | 174.49
2017-03-30 04:30 | 188.15 | 175.08
2017-03-30 05:00 | 189.48 | 176.18
2017-03-30 05:30 | 190.2 | 177.23
2017-03-30 06:00 | 192.03 | 179.18
2017-03-30 06:30 | 194.44 | 181.26
2017-03-30 07:00 | 196.67 | 182.25
2017-03-30 07:30 | 196.73 | 182.55
2017-03-30 08:00 | 195.81 | 181.75
2017-03-30 08:30 | 195.35 | 181.27
2017-03-30 09:00 | 195.6 | 181.37
2017-03-30 09:30 | 196.47 | 181.25
2017-03-30 10:00 | 196.26 | 181.2
2017-03-30 10:30 | 195.95 | 180.8
2017-03-30 11:00 | 195.09 | 179.75
2017-03-30 11:30 | 195.21 | 179.63
2017-03-30 12:00 | 195.05 | 179.74
2017-03-30 12:30 | 194.66 | 179.47
2017-03-30 13:00 | 195 | 179.57
2017-03-30 13:30 | 194.89 | 179.26
2017-03-30 14:00 | 194.52 | 178.91
2017-03-30 14:30 | 194.32 | 178.55
2017-03-30 15:00 | 194.97 | 179.06
2017-03-30 15:30 | 195.2 | 179.27
2017-03-30 16:00 | 194.89 | 179.33
2017-03-30 16:30 | 194.98 | 179.56
2017-03-30 17:00 | 192.84 | 177.56
2017-03-30 17:30 | 195.96 | 182.32
2017-03-30 18:00 | 196.7 | 183.86
2017-03-30 18:30 | 196.71 | 184.17
2017-03-30 19:00 | 197.79 | 185.27
2017-03-30 19:30 | 197.27 | 184.1
2017-03-30 20:00 | 195.31 | 181.6
2017-03-30 20:30 | 195.4 | 181.26
2017-03-30 21:00 | 196.06 | 181.65
2017-03-30 21:30 | 194.72 | 181.12
2017-03-30 22:00 | 192.95 | 180.31
2017-03-30 22:30 | 192.3 | 179.98
2017-03-30 23:00 | 192.08 | 179.53
2017-03-30 23:30 | 191.47 | 178.83
2017-03-31 | 190.29 | 178.29
2017-03-31 00:30 | 190.51 | 178.25
2017-03-31 01:00 | 189.93 | 177.75
2017-03-31 01:30 | 189.06 | 178.01
2017-03-31 02:00 | 188.94 | 177.98
2017-03-31 02:30 | 188.64 | 177.61
2017-03-31 03:00 | 186.83 | 175.82
2017-03-31 03:30 | 186.78 | 175.73
2017-03-31 04:00 | 186.86 | 175.87
2017-03-31 04:30 | 187.09 | 176.35
2017-03-31 05:00 | 189.85 | 177.58
2017-03-31 05:30 | 191.59 | 178.99
2017-03-31 06:00 | 192.4 | 180.46
2017-03-31 06:30 | 194.59 | 182.43
2017-03-31 07:00 | 195.75 | 183.55
2017-03-31 07:30 | 198.69 | 185.21
2017-03-31 08:00 | 199.02 | 185.4
2017-03-31 08:30 | 197.31 | 183.62
2017-03-31 09:00 | 195.83 | 181.74
2017-03-31 09:30 | 195.04 | 180.45
2017-03-31 10:00 | 195.64 | 180.77
2017-03-31 10:30 | 195.92 | 180.89
2017-03-31 11:00 | 194.23 | 179.14
2017-03-31 11:30 | 192.56 | 177.94
2017-03-31 12:00 | 192.48 | 178.28
2017-03-31 12:30 | 192.73 | 178.28
2017-03-31 13:00 | 192.67 | 177.61
2017-03-31 13:30 | 192.87 | 178.02
2017-03-31 14:00 | 192.83 | 178.11
2017-03-31 14:30 | 193.68 | 178.97
2017-03-31 15:00 | 193.71 | 179.1
2017-03-31 15:30 | 192.69 | 178.11
2017-03-31 16:00 | 193.02 | 178.35
2017-03-31 16:30 | 193.84 | 178.85
2017-03-31 17:00 | 194.6 | 179.91
2017-03-31 17:30 | 195.25 | 180.49
2017-03-31 18:00 | 197.06 | 182.32
2017-03-31 18:30 | 198.32 | 183.82
2017-03-31 19:00 | 200.89 | 186.71
2017-03-31 19:30 | 200.82 | 186.21
2017-03-31 20:00 | 199.23 | 184.31
2017-03-31 20:30 | 198.72 | 183.7
2017-03-31 21:00 | 197.69 | 182.54
2017-03-31 21:30 | 196.69 | 182.18
2017-03-31 22:00 | 195.78 | 181.4
2017-03-31 22:30 | 194.7 | 179.87
2017-03-31 23:00 | 193.67 | 178.51
2017-03-31 23:30 | 192.71 | 178.32
2017-04-01 | 190.33 | 177.27
2017-04-01 00:30 | 188.17 | 176.03
2017-04-01 01:00 | 185.72 | 174.4
2017-04-01 01:30 | 184.89 | 174.28
2017-04-01 02:00 | 184.34 | 173.72
2017-04-01 02:30 | 184.56 | 173.54
2017-04-01 03:00 | 184.35 | 173.37
2017-04-01 03:30 | 184.32 | 173.47
2017-04-01 04:00 | 185.08 | 174.35
2017-04-01 04:30 | 185.75 | 175.14
2017-04-01 05:00 | 186.55 | 176.17
2017-04-01 05:30 | 186.83 | 176.7
2017-04-01 06:00 | 187.39 | 177.51
2017-04-01 06:30 | 188.14 | 178.21
2017-04-01 07:00 | 187.71 | 177.36
2017-04-01 07:30 | 188.12 | 177.79
2017-04-01 08:00 | 189.96 | 178.99
2017-04-01 08:30 | 189.84 | 179
2017-04-01 09:00 | 189.65 | 178.84
2017-04-01 09:30 | 189.12 | 178.21
2017-04-01 10:00 | 188.73 | 177.93
2017-04-01 10:30 | 188.86 | 177.66
2017-04-01 11:00 | 190.04 | 177.02
2017-04-01 11:30 | 189.52 | 176.48
2017-04-01 12:00 | 189.66 | 176.81
2017-04-01 12:30 | 187.61 | 175.05
2017-04-01 13:00 | 187.78 | 175.19
2017-04-01 13:30 | 187.37 | 174.89
2017-04-01 14:00 | 187.15 | 175
2017-04-01 14:30 | 187.02 | 174.91
2017-04-01 15:00 | 187.31 | 175.25
2017-04-01 15:30 | 188.45 | 176.2
2017-04-01 16:00 | 189.37 | 177.07
2017-04-01 16:30 | 190.01 | 177.7
2017-04-01 17:00 | 192.43 | 180.55
2017-04-01 17:30 | 194.3 | 182.09
2017-04-01 18:00 | 196.34 | 184.23
2017-04-01 18:30 | 197.24 | 185.62
2017-04-01 19:00 | 199.11 | 187.37
2017-04-01 19:30 | 198.78 | 186.65
2017-04-01 20:00 | 197.34 | 184.76
2017-04-01 20:30 | 196.05 | 183.44
2017-04-01 21:00 | 195.42 | 182.65
2017-04-01 21:30 | 195.43 | 182.33
2017-04-01 22:00 | 194.5 | 181.06
2017-04-01 22:30 | 193.48 | 178.93
2017-04-01 23:00 | 191.76 | 177.83
2017-04-01 23:30 | 191.91 | 178.24
2017-04-02 | 191.15 | 177.48
2017-04-02 00:30 | 190.63 | 176.93
2017-04-02 01:00 | 189.52 | 176.76
2017-04-02 01:30 | 187.8 | 176.02
2017-04-02 02:00 | 186.65 | 175.64
2017-04-02 02:30 | 185.98 | 175.18
2017-04-02 03:00 | 185.55 | 174.85
2017-04-02 03:30 | 185.45 | 174.83
2017-04-02 04:00 | 185.64 | 175.04
2017-04-02 04:30 | 185.73 | 175.19
2017-04-02 05:00 | 186.59 | 175.36
2017-04-02 05:30 | 185.68 | 174.56
2017-04-02 06:00 | 185.48 | 174.59
2017-04-02 06:30 | 185.34 | 174.43
2017-04-02 07:00 | 185.4 | 174.86
2017-04-02 07:30 | 184.88 | 174.67
2017-04-02 08:00 | 186.82 | 174.63
2017-04-02 08:30 | 188.53 | 176.09
2017-04-02 09:00 | 189.22 | 175.69
2017-04-02 09:30 | 189.92 | 175.38
2017-04-02 10:00 | 189.41 | 174.64
2017-04-02 10:30 | 189.17 | 174.14
2017-04-02 11:00 | 187.99 | 172.71
2017-04-02 11:30 | 188.37 | 172.47
2017-04-02 12:00 | 188.71 | 172.89
2017-04-02 12:30 | 189.08 | 173.3
2017-04-02 13:00 | 189.68 | 173.89
2017-04-02 13:30 | 189.6 | 173.91
2017-04-02 14:00 | 189.63 | 173.6
2017-04-02 14:30 | 190.07 | 173.99
2017-04-02 15:00 | 191.28 | 175.36
2017-04-02 15:30 | 193.6 | 177.83
2017-04-02 16:00 | 194.62 | 178.81
2017-04-02 16:30 | 195.58 | 179.56
2017-04-02 17:00 | 197.18 | 181.08
2017-04-02 17:30 | 198.77 | 182.85
2017-04-02 18:00 | 200.24 | 183.43
2017-04-02 18:30 | 200.61 | 185.95
2017-04-02 19:00 | 201.82 | 187.4
2017-04-02 19:30 | 201.71 | 186.78
2017-04-02 20:00 | 200.37 | 185.05
2017-04-02 20:30 | 199.09 | 183.74
2017-04-02 21:00 | 198.66 | 182.86
2017-04-02 21:30 | 197.77 | 181.68
2017-04-02 22:00 | 194.09 | 179.51
2017-04-02 22:30 | 193.05 | 178.17
2017-04-02 23:00 | 190.99 | 176.58
2017-04-02 23:30 | 190 | 175.88
2017-04-03 | 188.72 | 175.24
2017-04-03 00:30 | 187.38 | 174.6
2017-04-03 01:00 | 186.74 | 174.35
2017-04-03 01:30 | 186.76 | 174.2
2017-04-03 02:00 | 186.63 | 173.76
2017-04-03 02:30 | 185.89 | 173.83
2017-04-03 03:00 | 186.25 | 174.04
2017-04-03 03:30 | 186.32 | 174.34
2017-04-03 04:00 | 186.55 | 174.19
2017-04-03 04:30 | 186.89 | 174.62
2017-04-03 05:00 | 187.34 | 175.37
2017-04-03 05:30 | 187.66 | 176.42
2017-04-03 06:00 | 189.45 | 178.49
2017-04-03 06:30 | 191.04 | 180.58
2017-04-03 07:00 | 192.71 | 182.55
2017-04-03 07:30 | 193.68 | 183.98
2017-04-03 08:00 | 195.07 | 185.65
2017-04-03 08:30 | 195.19 | 185.63
2017-04-03 09:00 | 198.19 | 188.94
2017-04-03 09:30 | 196.99 | 187.36
2017-04-03 10:00 | 196.08 | 186.45
2017-04-03 10:30 | 195.08 | 185.4
2017-04-03 11:00 | 193.74 | 184.61
2017-04-03 11:30 | 192.4 | 183.04
2017-04-03 12:00 | 193.14 | 183.46
2017-04-03 12:30 | 194.16 | 184.05
2017-04-03 13:00 | 192.69 | 181.98
2017-04-03 13:30 | 193.4 | 182.58
2017-04-03 14:00 | 194.03 | 183.41
2017-04-03 14:30 | 195.15 | 184.43
2017-04-03 15:00 | 194.85 | 184.43
2017-04-03 15:30 | 195.8 | 185.48
2017-04-03 16:00 | 196.08 | 185.58
2017-04-03 16:30 | 196.34 | 185.7
2017-04-03 17:00 | 196.92 | 186.6
2017-04-03 17:30 | 197.33 | 186.68
2017-04-03 18:00 | 199.26 | 188.44
2017-04-03 18:30 | 201.17 | 190.74
2017-04-03 19:00 | 203.83 | 193.02
2017-04-03 19:30 | 201.85 | 190.84
2017-04-03 20:00 | 201.34 | 189.84
2017-04-03 20:30 | 200.76 | 188.81
2017-04-03 21:00 | 199.01 | 186.75
2017-04-03 21:30 | 198.46 | 186.07
2017-04-03 22:00 | 196.71 | 185.03
2017-04-03 22:30 | 196.37 | 183.51
2017-04-03 23:00 | 196.52 | 182.47
2017-04-03 23:30 | 193.8 | 181.51
2017-04-04 | 191.52 | 180.12
2017-04-04 00:30 | 190.76 | 179.68
2017-04-04 01:00 | 189.79 | 179.47
2017-04-04 01:30 | 189.14 | 178.79
2017-04-04 02:00 | 188.33 | 178.51
2017-04-04 02:30 | 188.86 | 178.72
2017-04-04 03:00 | 189.06 | 178.47
2017-04-04 03:30 | 189.69 | 178.21
2017-04-04 04:00 | 190.17 | 178.58
2017-04-04 04:30 | 190.54 | 178.84
2017-04-04 05:00 | 191.17 | 179.53
2017-04-04 05:30 | 191.3 | 180.38
2017-04-04 06:00 | 193.88 | 182.58
2017-04-04 06:30 | 196.04 | 184.5
2017-04-04 07:00 | 198.02 | 184.91
2017-04-04 07:30 | 197.98 | 185.19
2017-04-04 08:00 | 197.16 | 184.08
2017-04-04 08:30 | 196.34 | 182.44
2017-04-04 09:00 | 196.13 | 182.77
2017-04-04 09:30 | 196.38 | 181.8
2017-04-04 10:00 | 197.39 | 183.88
2017-04-04 10:30 | 196.88 | 183.06
2017-04-04 11:00 | 197.93 | 183.9
2017-04-04 11:30 | 198.08 | 184.44
2017-04-04 12:00 | 197.12 | 183.17
2017-04-04 12:30 | 197.01 | 183.31
2017-04-04 13:00 | 197.58 | 183.88
2017-04-04 13:30 | 198.79 | 184.92
2017-04-04 14:00 | 201.52 | 186.85
2017-04-04 14:30 | 201.68 | 187
2017-04-04 15:00 | 202.01 | 187.56
2017-04-04 15:30 | 202.45 | 188.03
2017-04-04 16:00 | 203.6 | 189.39
2017-04-04 16:30 | 205.13 | 190.44
2017-04-04 17:00 | 205.89 | 190.89
2017-04-04 17:30 | 204.83 | 192.12
2017-04-04 18:00 | 209.09 | 196.32
2017-04-04 18:30 | 212.87 | 200.31
2017-04-04 19:00 | 216.01 | 203.37
2017-04-04 19:30 | 215.3 | 202.03
2017-04-04 20:00 | 213.47 | 200.31
2017-04-04 20:30 | 211.99 | 198.98
2017-04-04 21:00 | 210.5 | 197.69
2017-04-04 21:30 | 209.15 | 197.07
2017-04-04 22:00 | 210.51 | 198.27
2017-04-04 22:30 | 212.44 | 199.04
2017-04-04 23:00 | 211.15 | 197.57
2017-04-04 23:30 | 209.21 | 197
2017-04-05 | 207.4 | 195.95
2017-04-05 00:30 | 206.86 | 195.15
2017-04-05 01:00 | 207.39 | 195.09
2017-04-05 01:30 | 206.71 | 195.12
2017-04-05 02:00 | 205.61 | 194.44
2017-04-05 02:30 | 204.31 | 193.11
2017-04-05 03:00 | 204.65 | 193.56
2017-04-05 03:30 | 206.74 | 195.01
2017-04-05 04:00 | 207.66 | 195.21
2017-04-05 04:30 | 208.29 | 195.84
2017-04-05 05:00 | 209.43 | 196.89
2017-04-05 05:30 | 210.42 | 198.37
2017-04-05 06:00 | 213.25 | 200.24
2017-04-05 06:30 | 214.82 | 202.32
2017-04-05 07:00 | 217.65 | 204.67
2017-04-05 07:30 | 218.57 | 205.31
2017-04-05 08:00 | 217.84 | 204.91
2017-04-05 08:30 | 217.03 | 204.27
2017-04-05 09:00 | 216.53 | 203.9
2017-04-05 09:30 | 216.25 | 203.32
2017-04-05 10:00 | 216.11 | 203.23
2017-04-05 10:30 | 216.03 | 202.86
2017-04-05 11:00 | 215.49 | 201.82
2017-04-05 11:30 | 216.26 | 202.73
2017-04-05 12:00 | 214.87 | 202.44
2017-04-05 12:30 | 215.87 | 202.99
2017-04-05 13:00 | 216.8 | 204.07
2017-04-05 13:30 | 218.24 | 205.92
2017-04-05 14:00 | 219.88 | 207.36
2017-04-05 14:30 | 219.79 | 206.69
2017-04-05 15:00 | 219.67 | 206.21
2017-04-05 15:30 | 221.77 | 208.03
2017-04-05 16:00 | 221.67 | 207.12
2017-04-05 16:30 | 221.66 | 206.71
2017-04-05 17:00 | 222.45 | 207.41
2017-04-05 17:30 | 223.16 | 207.74
2017-04-05 18:00 | 225.85 | 210.05
2017-04-05 18:30 | 228 | 212.52
2017-04-05 19:00 | 227.68 | 212.35
2017-04-05 19:30 | 226.63 | 211.12
2017-04-05 20:00 | 225.75 | 210.55
2017-04-05 20:30 | 224.84 | 210.04
2017-04-05 21:00 | 223.15 | 208.22
2017-04-05 21:30 | 222.81 | 207.57
2017-04-05 22:00 | 219.36 | 204.09
2017-04-05 22:30 | 216.5 | 201.32
2017-04-05 23:00 | 214.39 | 199.08
2017-04-05 23:30 | 212.88 | 198.09
2017-04-06 | 212.69 | 197.06
2017-04-06 00:30 | 211.83 | 196.26
2017-04-06 01:00 | 209.94 | 195.02
2017-04-06 01:30 | 209.57 | 195.15
2017-04-06 02:00 | 208.46 | 194.69
2017-04-06 02:30 | 206.92 | 192.95
2017-04-06 03:00 | 206.88 | 193.16
2017-04-06 03:30 | 207.58 | 194.2
2017-04-06 04:00 | 207.94 | 194.59
2017-04-06 04:30 | 208.42 | 195.05
2017-04-06 05:00 | 208.87 | 195.78
2017-04-06 05:30 | 208.75 | 196.49
2017-04-06 06:00 | 212.58 | 197.97
2017-04-06 06:30 | 215.18 | 200.44
2017-04-06 07:00 | 217.63 | 203.91
2017-04-06 07:30 | 218.81 | 205.59
2017-04-06 08:00 | 219.41 | 206.1
2017-04-06 08:30 | 220.92 | 207.02
2017-04-06 09:00 | 221.27 | 205.76
2017-04-06 09:30 | 220.86 | 204.78
2017-04-06 10:00 | 221.51 | 205.78
2017-04-06 10:30 | 221.9 | 205.74
2017-04-06 11:00 | 222.83 | 206.73
2017-04-06 11:30 | 223.66 | 207.7
2017-04-06 12:00 | 222.89 | 208.12
2017-04-06 12:30 | 222.67 | 207.72
2017-04-06 13:00 | 222.94 | 207.68
2017-04-06 13:30 | 223.42 | 207.84
2017-04-06 14:00 | 223.6 | 208.21
2017-04-06 14:30 | 224.23 | 208.68
2017-04-06 15:00 | 224.91 | 209.26
2017-04-06 15:30 | 222.6 | 207.37
2017-04-06 16:00 | 223.27 | 208.19
2017-04-06 16:30 | 224.35 | 209.29
2017-04-06 17:00 | 224.73 | 209.42
2017-04-06 17:30 | 225.77 | 209.71
2017-04-06 18:00 | 227.26 | 211.39
2017-04-06 18:30 | 229.44 | 214.01
2017-04-06 19:00 | 231.81 | 216.49
2017-04-06 19:30 | 230.68 | 215.25
2017-04-06 20:00 | 228.85 | 213.54
2017-04-06 20:30 | 228.4 | 213.08
2017-04-06 21:00 | 226.92 | 211.57
2017-04-06 21:30 | 226.36 | 211.15
2017-04-06 22:00 | 225.57 | 209.94
2017-04-06 22:30 | 224.54 | 207.86
2017-04-06 23:00 | 223.15 | 206.28
2017-04-06 23:30 | 221.99 | 205.34
2017-04-07 | 221.58 | 204.52
2017-04-07 00:30 | 220.6 | 203.85
2017-04-07 01:00 | 218.8 | 202.84
2017-04-07 01:30 | 218.43 | 202.14
2017-04-07 02:00 | 217.23 | 201.31
2017-04-07 02:30 | 217.37 | 201.19
2017-04-07 03:00 | 217.75 | 200.91
2017-04-07 03:30 | 218.25 | 200.82
2017-04-07 04:00 | 218.71 | 201.16
2017-04-07 04:30 | 218.92 | 201.41
2017-04-07 05:00 | 218.48 | 202.23
2017-04-07 05:30 | 218.47 | 202.85
2017-04-07 06:00 | 220.34 | 204.72
2017-04-07 06:30 | 222.52 | 207.37
2017-04-07 07:00 | 223.09 | 208.05
2017-04-07 07:30 | 222.87 | 209.16
2017-04-07 08:00 | 221.83 | 208.56
2017-04-07 08:30 | 220.88 | 207.03
2017-04-07 09:00 | 219.72 | 205.74
2017-04-07 09:30 | 220.47 | 205.89
2017-04-07 10:00 | 221.1 | 206.43
2017-04-07 10:30 | 221.09 | 206.22
2017-04-07 11:00 | 221.02 | 206.02
2017-04-07 11:30 | 221.02 | 206.49
2017-04-07 12:00 | 221.48 | 206.73
2017-04-07 12:30 | 221.56 | 206.58
2017-04-07 13:00 | 220.89 | 205.92
2017-04-07 13:30 | 221.17 | 205.64
2017-04-07 14:00 | 222.65 | 206.97
2017-04-07 14:30 | 222.38 | 206.56
2017-04-07 15:00 | 222.9 | 206.74
2017-04-07 15:30 | 223.58 | 207.32
2017-04-07 16:00 | 224.46 | 208.04
2017-04-07 16:30 | 223.9 | 208.03
2017-04-07 17:00 | 224.71 | 209.19
2017-04-07 17:30 | 224.99 | 209.83
2017-04-07 18:00 | 223.9 | 209.24
2017-04-07 18:30 | 226.19 | 211.68
2017-04-07 19:00 | 229.7 | 215.34
2017-04-07 19:30 | 229.56 | 215
2017-04-07 20:00 | 227.52 | 212.83
2017-04-07 20:30 | 225.02 | 210.33
2017-04-07 21:00 | 223.98 | 209.03
2017-04-07 21:30 | 223.44 | 208.11
2017-04-07 22:00 | 222.56 | 207.05
2017-04-07 22:30 | 222.77 | 205.78
2017-04-07 23:00 | 220.39 | 203.71
2017-04-07 23:30 | 219.06 | 203.32
2017-04-08 | 218 | 202.01
2017-04-08 00:30 | 218.94 | 202.85
2017-04-08 01:00 | 219.28 | 203.16
2017-04-08 01:30 | 218.69 | 202.66
2017-04-08 02:00 | 217.07 | 202.01
2017-04-08 02:30 | 216.26 | 201.2
2017-04-08 03:00 | 215.46 | 200.31
2017-04-08 03:30 | 215.21 | 199.71
2017-04-08 04:00 | 215.51 | 199.37
2017-04-08 04:30 | 216.47 | 200.11
2017-04-08 05:00 | 217 | 200.64
2017-04-08 05:30 | 217.52 | 201.65
2017-04-08 06:00 | 217.82 | 202.23
2017-04-08 06:30 | 218.59 | 202.42
2017-04-08 07:00 | 218.61 | 202.36
2017-04-08 07:30 | 218.01 | 202.46
2017-04-08 08:00 | 217.09 | 201.47
2017-04-08 08:30 | 215.45 | 200.46
2017-04-08 09:00 | 214.22 | 199.12
2017-04-08 09:30 | 214.56 | 199.64
2017-04-08 10:00 | 214.19 | 199.03
2017-04-08 10:30 | 214.08 | 198.34
2017-04-08 11:00 | 212.27 | 196.11
2017-04-08 11:30 | 212.97 | 197.08
2017-04-08 12:00 | 213.17 | 197.37
2017-04-08 12:30 | 214.7 | 198.4
2017-04-08 13:00 | 213.61 | 197.41
2017-04-08 13:30 | 214.16 | 198.46
2017-04-08 14:00 | 214.31 | 198.69
2017-04-08 14:30 | 216.48 | 200.7
2017-04-08 15:00 | 217.5 | 201.65
2017-04-08 15:30 | 218.05 | 202.26
2017-04-08 16:00 | 219.68 | 204.11
2017-04-08 16:30 | 220.49 | 204.82
2017-04-08 17:00 | 222.23 | 206.78
2017-04-08 17:30 | 223.1 | 207.89
2017-04-08 18:00 | 224.32 | 209.03
2017-04-08 18:30 | 225.82 | 210.72
2017-04-08 19:00 | 227.28 | 212.23
2017-04-08 19:30 | 225.94 | 210.9
2017-04-08 20:00 | 222.16 | 207
2017-04-08 20:30 | 221.64 | 206.36
2017-04-08 21:00 | 221.06 | 205.33
2017-04-08 21:30 | 220.82 | 204.64
2017-04-08 22:00 | 219.82 | 203.37
2017-04-08 22:30 | 218.83 | 201.83
2017-04-08 23:00 | 220.24 | 202.65
2017-04-08 23:30 | 219.44 | 202.89
2017-04-09 | 217.83 | 202.15
2017-04-09 00:30 | 216.62 | 201.01
2017-04-09 01:00 | 215.65 | 200.25
2017-04-09 01:30 | 215.02 | 199.67
2017-04-09 02:00 | 213.54 | 199
2017-04-09 02:30 | 213.98 | 198.99
2017-04-09 03:00 | 213.27 | 198.39
2017-04-09 03:30 | 213.74 | 198.99
2017-04-09 04:00 | 213.56 | 198.91
2017-04-09 04:30 | 213.64 | 198.89
2017-04-09 05:00 | 214.38 | 199.56
2017-04-09 05:30 | 213.83 | 199.11
2017-04-09 06:00 | 215.22 | 200.46
2017-04-09 06:30 | 216.29 | 201.25
2017-04-09 07:00 | 216.31 | 201.64
2017-04-09 07:30 | 216.26 | 201.52
2017-04-09 08:00 | 214.65 | 200.26
2017-04-09 08:30 | 212.26 | 198.73
2017-04-09 09:00 | 212.79 | 199.22
2017-04-09 09:30 | 208.28 | 194.12
2017-04-09 10:00 | 194.67 | 180.2
2017-04-09 10:30 | 196.54 | 181.87
2017-04-09 11:00 | 195.82 | 181.08
2017-04-09 11:30 | 195.31 | 180.36
2017-04-09 12:00 | 195.97 | 181.38
2017-04-09 12:30 | 196.84 | 182.15
2017-04-09 13:00 | 197.96 | 183.23
2017-04-09 13:30 | 196.28 | 181.38
2017-04-09 14:00 | 199.38 | 184.82
2017-04-09 14:30 | 201.61 | 187
2017-04-09 15:00 | 215.13 | 200.3
2017-04-09 15:30 | 222.2 | 206.84
2017-04-09 16:00 | 224.94 | 209.87
2017-04-09 16:30 | 226.47 | 211.87
2017-04-09 17:00 | 227.91 | 212.67
2017-04-09 17:30 | 230.01 | 213.8
2017-04-09 18:00 | 229.87 | 213.39
2017-04-09 18:30 | 230.08 | 214.23
2017-04-09 19:00 | 231.72 | 216.76
2017-04-09 19:30 | 230.42 | 214.9
2017-04-09 20:00 | 228.11 | 212.26
2017-04-09 20:30 | 227.41 | 211.4
2017-04-09 21:00 | 224.78 | 208.32
2017-04-09 21:30 | 223.91 | 208.54
2017-04-09 22:00 | 222.76 | 207.42
2017-04-09 22:30 | 220.62 | 204.52
2017-04-09 23:00 | 218.78 | 201.89
2017-04-09 23:30 | 218.15 | 202.44
2017-04-10 | 216.41 | 201.21
2017-04-10 00:30 | 215.14 | 199.92
2017-04-10 01:00 | 209.45 | 194.05
2017-04-10 01:30 | 208.89 | 193.47
2017-04-10 02:00 | 209.06 | 193.42
2017-04-10 02:30 | 208.75 | 193.09
2017-04-10 03:00 | 208.62 | 192.98
2017-04-10 03:30 | 204.56 | 188.75
2017-04-10 04:00 | 181.64 | 165
2017-04-10 04:30 | 181.92 | 165.52
2017-04-10 05:00 | 183.26 | 167.38
2017-04-10 05:30 | 184.48 | 169.14
2017-04-10 06:00 | 185.67 | 171.14
2017-04-10 06:30 | 188.03 | 173.63
2017-04-10 07:00 | 190.12 | 175.67
2017-04-10 07:30 | 193.04 | 179.32
2017-04-10 08:00 | 193.93 | 180.33
2017-04-10 08:30 | 192.76 | 179.62
2017-04-10 09:00 | 191.47 | 178.14
2017-04-10 09:30 | 192.55 | 178.98
2017-04-10 10:00 | 192.76 | 179.07
2017-04-10 10:30 | 192.62 | 178.5
2017-04-10 11:00 | 193.42 | 179.8
2017-04-10 11:30 | 178.14 | 163.95
2017-04-10 12:00 | 154.77 | 138.69
2017-04-10 12:30 | 155.02 | 138
2017-04-10 13:00 | 172.87 | 157
2017-04-10 13:30 | 204.82 | 190.38
2017-04-10 14:00 | 216.87 | 203.08
2017-04-10 14:30 | 220.56 | 206.85
2017-04-10 15:00 | 219.57 | 205.42
2017-04-10 15:30 | 219.76 | 205.56
2017-04-10 16:00 | 220.11 | 205.87
2017-04-10 16:30 | 221.76 | 207.32
2017-04-10 17:00 | 223.98 | 209.64
2017-04-10 17:30 | 225.9 | 211.52
2017-04-10 18:00 | 228.85 | 214.82
2017-04-10 18:30 | 231.42 | 217.71
2017-04-10 19:00 | 233.23 | 219.62
2017-04-10 19:30 | 231.68 | 217.78
2017-04-10 20:00 | 229.59 | 215.58
2017-04-10 20:30 | 225.58 | 211.36
2017-04-10 21:00 | 222.29 | 208.19
2017-04-10 21:30 | 221.75 | 207.76
2017-04-10 22:00 | 220.53 | 206.66
2017-04-10 22:30 | 218.76 | 204.19
2017-04-10 23:00 | 216.09 | 201.02
2017-04-10 23:30 | 216 | 201.42
2017-04-11 | 214.38 | 200.48
2017-04-11 00:30 | 213.65 | 199.72
2017-04-11 01:00 | 213.17 | 199.01
2017-04-11 01:30 | 211.98 | 197.96
2017-04-11 02:00 | 212.27 | 198.35
2017-04-11 02:30 | 212.36 | 198.87
2017-04-11 03:00 | 212.69 | 199.43
2017-04-11 03:30 | 212.68 | 199.11
2017-04-11 04:00 | 213.16 | 199.23
2017-04-11 04:30 | 213.94 | 200.41
2017-04-11 05:00 | 214.63 | 201.22
2017-04-11 05:30 | 216.08 | 202.42
2017-04-11 06:00 | 218.15 | 204.46
2017-04-11 06:30 | 221.81 | 207.92
2017-04-11 07:00 | 222.93 | 209.45
2017-04-11 07:30 | 222.36 | 208.79
2017-04-11 08:00 | 221.71 | 207.64
2017-04-11 08:30 | 218.15 | 203.69
2017-04-11 09:00 | 218.46 | 203.55
2017-04-11 09:30 | 219.54 | 204.09
2017-04-11 10:00 | 219.88 | 203.88
2017-04-11 10:30 | 218.79 | 202.42
2017-04-11 11:00 | 218.19 | 201.74
2017-04-11 11:30 | 216.92 | 200.82
2017-04-11 12:00 | 218.55 | 203.15
2017-04-11 12:30 | 219.52 | 204.1
2017-04-11 13:00 | 219.33 | 203.88
2017-04-11 13:30 | 219.29 | 203.98
2017-04-11 14:00 | 222.84 | 208.08
2017-04-11 14:30 | 227.17 | 213.05
2017-04-11 15:00 | 224.82 | 210.05
2017-04-11 15:30 | 225.66 | 210.8
2017-04-11 16:00 | 226.92 | 211.97
2017-04-11 16:30 | 228.41 | 212.93
2017-04-11 17:00 | 228.78 | 213.58
2017-04-11 17:30 | 229.45 | 214.27
2017-04-11 18:00 | 231.97 | 216.68
2017-04-11 18:30 | 236.64 | 221.55
2017-04-11 19:00 | 239.03 | 224.19
2017-04-11 19:30 | 233 | 218.24
2017-04-11 20:00 | 229.19 | 214.85
2017-04-11 20:30 | 229.02 | 214.69
2017-04-11 21:00 | 228.06 | 213.88
2017-04-11 21:30 | 227.15 | 212.96
2017-04-11 22:00 | 225.43 | 211.14
2017-04-11 22:30 | 225.1 | 210.02
2017-04-11 23:00 | 224.11 | 208.78
2017-04-11 23:30 | 223.43 | 208.15
2017-04-12 | 221.56 | 206.24
2017-04-12 00:30 | 220.14 | 205
2017-04-12 01:00 | 218.55 | 204.04
2017-04-12 01:30 | 218.44 | 204.44
2017-04-12 02:00 | 216.89 | 202.87
2017-04-12 02:30 | 215.42 | 201.71
2017-04-12 03:00 | 215.72 | 202.01
2017-04-12 03:30 | 215.9 | 202.07
2017-04-12 04:00 | 216.68 | 202.56
2017-04-12 04:30 | 217.06 | 203.09
2017-04-12 05:00 | 217.19 | 203.76
2017-04-12 05:30 | 218.74 | 205.57
2017-04-12 06:00 | 220.77 | 207.7
2017-04-12 06:30 | 222.32 | 209.52
2017-04-12 07:00 | 223.76 | 211.39
2017-04-12 07:30 | 225.71 | 212.01
2017-04-12 08:00 | 224.94 | 211.58
2017-04-12 08:30 | 222.75 | 209.86
2017-04-12 09:00 | 222.28 | 209.13
2017-04-12 09:30 | 221.34 | 207.71
2017-04-12 10:00 | 220.68 | 206.88
2017-04-12 10:30 | 219.48 | 205.76
2017-04-12 11:00 | 219.75 | 206.03
2017-04-12 11:30 | 220.01 | 205.88
2017-04-12 12:00 | 219.92 | 205.85
2017-04-12 12:30 | 220.36 | 206.22
2017-04-12 13:00 | 220.49 | 206.4
2017-04-12 13:30 | 220.39 | 206.44
2017-04-12 14:00 | 221.55 | 207.81
2017-04-12 14:30 | 221.9 | 208.37
2017-04-12 15:00 | 221.69 | 207.71
2017-04-12 15:30 | 223.04 | 208.55
2017-04-12 16:00 | 224.63 | 209.98
2017-04-12 16:30 | 226.06 | 211.27
2017-04-12 17:00 | 227.13 | 212.14
2017-04-12 17:30 | 227.72 | 212.66
2017-04-12 18:00 | 229.79 | 215.03
2017-04-12 18:30 | 232.86 | 218.42
2017-04-12 19:00 | 234.56 | 220.41
2017-04-12 19:30 | 233.56 | 219.3
2017-04-12 20:00 | 231.71 | 217.25
2017-04-12 20:30 | 230.04 | 215.38
2017-04-12 21:00 | 228.38 | 213.82
2017-04-12 21:30 | 228.08 | 213.53
2017-04-12 22:00 | 226.84 | 212.17
2017-04-12 22:30 | 225.37 | 210.29
2017-04-12 23:00 | 223.38 | 208.12
2017-04-12 23:30 | 222.18 | 207.49
2017-04-13 | 220.59 | 205.89
2017-04-13 00:30 | 218.99 | 204.52
2017-04-13 01:00 | 217.4 | 202.9
2017-04-13 01:30 | 218.02 | 202.79
2017-04-13 02:00 | 216.37 | 203.24
2017-04-13 02:30 | 215.23 | 202.96
2017-04-13 03:00 | 215.15 | 202.78
2017-04-13 03:30 | 215.27 | 202.8
2017-04-13 04:00 | 215.09 | 202.57
2017-04-13 04:30 | 215.7 | 203.06
2017-04-13 05:00 | 216.21 | 203.81
2017-04-13 05:30 | 216.75 | 204.81
2017-04-13 06:00 | 218.75 | 206.31
2017-04-13 06:30 | 221.43 | 208.04
2017-04-13 07:00 | 224.09 | 210.55
2017-04-13 07:30 | 224.67 | 211.16
2017-04-13 08:00 | 224.1 | 211.22
2017-04-13 08:30 | 223.59 | 210.65
2017-04-13 09:00 | 221.67 | 208.73
2017-04-13 09:30 | 222.49 | 209.21
2017-04-13 10:00 | 221.19 | 207.98
2017-04-13 10:30 | 220.45 | 207.35
2017-04-13 11:00 | 220.23 | 207.38
2017-04-13 11:30 | 221.58 | 207.83
2017-04-13 12:00 | 222.53 | 208.9
2017-04-13 12:30 | 222.88 | 209.2
2017-04-13 13:00 | 224.13 | 210.32
2017-04-13 13:30 | 224.88 | 211.09
2017-04-13 14:00 | 224.75 | 210.99
2017-04-13 14:30 | 227.12 | 213.48
2017-04-13 15:00 | 227.07 | 213.17
2017-04-13 15:30 | 228.23 | 214.45
2017-04-13 16:00 | 229.11 | 215.22
2017-04-13 16:30 | 227.3 | 212.76
2017-04-13 17:00 | 227.8 | 213.48
2017-04-13 17:30 | 226.41 | 212.11
2017-04-13 18:00 | 227.62 | 213.4
2017-04-13 18:30 | 231.39 | 217.18
2017-04-13 19:00 | 232.99 | 218.99
2017-04-13 19:30 | 233.83 | 219.71
2017-04-13 20:00 | 232.25 | 218.09
2017-04-13 20:30 | 230.91 | 216.71
2017-04-13 21:00 | 229.47 | 215.22
2017-04-13 21:30 | 227.92 | 214.71
2017-04-13 22:00 | 224.97 | 212.66
2017-04-13 22:30 | 224.85 | 211.12
2017-04-13 23:00 | 225.25 | 211.17
2017-04-13 23:30 | 224.24 | 210.21
2017-04-14 | 222.48 | 208.08
2017-04-14 00:30 | 220.3 | 206.02
2017-04-14 01:00 | 217.54 | 204.2
2017-04-14 01:30 | 215.14 | 203.52
2017-04-14 02:00 | 214.89 | 203.48
2017-04-14 02:30 | 214.92 | 203.65
2017-04-14 03:00 | 216.38 | 202.8
2017-04-14 03:30 | 216.17 | 202.43
2017-04-14 04:00 | 216.95 | 203.01
2017-04-14 04:30 | 217.14 | 203.02
2017-04-14 05:00 | 215.45 | 201.17
2017-04-14 05:30 | 210.28 | 196.11
2017-04-14 06:00 | 205.62 | 191.97
2017-04-14 06:30 | 205.65 | 192.71
2017-04-14 07:00 | 204.91 | 192.13
2017-04-14 07:30 | 204.43 | 191.81
2017-04-14 08:00 | 204.59 | 191.12
2017-04-14 08:30 | 205.88 | 191.01
2017-04-14 09:00 | 205.6 | 190.52
2017-04-14 09:30 | 204.28 | 189.42
2017-04-14 10:00 | 203.68 | 188.17
2017-04-14 10:30 | 203.71 | 187.83
2017-04-14 11:00 | 203.24 | 187.47
2017-04-14 11:30 | 203.04 | 187.55
2017-04-14 12:00 | 204.38 | 188.87
2017-04-14 12:30 | 205.28 | 189.46
2017-04-14 13:00 | 205.83 | 189.96
2017-04-14 13:30 | 204.88 | 189.75
2017-04-14 14:00 | 206.59 | 190.49
2017-04-14 14:30 | 206.74 | 191.1
2017-04-14 15:00 | 206.26 | 191.45
2017-04-14 15:30 | 206.96 | 192.12
2017-04-14 16:00 | 208.15 | 193.61
2017-04-14 16:30 | 208.76 | 194.8
2017-04-14 17:00 | 210.05 | 196.26
2017-04-14 17:30 | 210.44 | 195.91
2017-04-14 18:00 | 213.04 | 198.55
2017-04-14 18:30 | 216.02 | 200.78
2017-04-14 19:00 | 216.87 | 201.57
2017-04-14 19:30 | 215.82 | 200.48
2017-04-14 20:00 | 213.57 | 198.41
2017-04-14 20:30 | 212.41 | 197.04
2017-04-14 21:00 | 211.88 | 195.92
2017-04-14 21:30 | 210.81 | 195.33
2017-04-14 22:00 | 208.83 | 193.63
2017-04-14 22:30 | 208.23 | 192.17
2017-04-14 23:00 | 207.4 | 190.48
2017-04-14 23:30 | 207.12 | 190.67
2017-04-15 | 205.75 | 189.66
2017-04-15 00:30 | 204.72 | 190.12
2017-04-15 01:00 | 203.2 | 188.79
2017-04-15 01:30 | 202.77 | 188
2017-04-15 02:00 | 201.65 | 186.97
2017-04-15 02:30 | 200.43 | 185.92
2017-04-15 03:00 | 199.86 | 185.69
2017-04-15 03:30 | 200.97 | 185.46
2017-04-15 04:00 | 201.28 | 185.54
2017-04-15 04:30 | 202.24 | 185.8
2017-04-15 05:00 | 202.64 | 185.78
2017-04-15 05:30 | 204.15 | 186.85
2017-04-15 06:00 | 205.37 | 187.88
2017-04-15 06:30 | 206.18 | 189.26
2017-04-15 07:00 | 204.29 | 190.86
2017-04-15 07:30 | 204.08 | 191.92
2017-04-15 08:00 | 203.43 | 191.62
2017-04-15 08:30 | 202.98 | 191.07
2017-04-15 09:00 | 202.29 | 190
2017-04-15 09:30 | 200.5 | 187.92
2017-04-15 10:00 | 200.56 | 187.81
2017-04-15 10:30 | 198.92 | 186.28
2017-04-15 11:00 | 197.85 | 185.29
2017-04-15 11:30 | 197.43 | 184.55
2017-04-15 12:00 | 198.04 | 185.17
2017-04-15 12:30 | 206.67 | 193.82
2017-04-15 13:00 | 208.41 | 195.7
2017-04-15 13:30 | 209.1 | 196.8
2017-04-15 14:00 | 210.04 | 198.17
2017-04-15 14:30 | 211.22 | 198.79
2017-04-15 15:00 | 212.86 | 200.3
2017-04-15 15:30 | 212.67 | 199.99
2017-04-15 16:00 | 214.44 | 201.68
2017-04-15 16:30 | 216.51 | 203.68
2017-04-15 17:00 | 217.81 | 204.62
2017-04-15 17:30 | 219.07 | 205.68
2017-04-15 18:00 | 218.5 | 205.37
2017-04-15 18:30 | 219.63 | 206.3
2017-04-15 19:00 | 213.09 | 199.69
2017-04-15 19:30 | 211 | 197.65
2017-04-15 20:00 | 209.78 | 196.25
2017-04-15 20:30 | 209.32 | 195.77
2017-04-15 21:00 | 207.7 | 193.92
2017-04-15 21:30 | 206.96 | 193.43
2017-04-15 22:00 | 206.47 | 193.12
2017-04-15 22:30 | 206.37 | 192.47
2017-04-15 23:00 | 206.79 | 191.96
2017-04-15 23:30 | 205.35 | 191.24
2017-04-16 | 203.73 | 190.05
2017-04-16 00:30 | 202.4 | 188.74
2017-04-16 01:00 | 200.3 | 186.75
2017-04-16 01:30 | 200.5 | 186.85
2017-04-16 02:00 | 200.38 | 186.4
2017-04-16 02:30 | 200.13 | 186.19
2017-04-16 03:00 | 199.32 | 185.35
2017-04-16 03:30 | 199.87 | 185.29
2017-04-16 04:00 | 199.7 | 185.47
2017-04-16 04:30 | 200.07 | 186.22
2017-04-16 05:00 | 200.59 | 186.46
2017-04-16 05:30 | 201.23 | 187.18
2017-04-16 06:00 | 201.93 | 187.61
2017-04-16 06:30 | 202.77 | 188.18
2017-04-16 07:00 | 202.77 | 188.61
2017-04-16 07:30 | 203.13 | 190.09
2017-04-16 08:00 | 203.24 | 190.77
2017-04-16 08:30 | 202.52 | 190.33
2017-04-16 09:00 | 201.79 | 189.7
2017-04-16 09:30 | 202.07 | 189.54
2017-04-16 10:00 | 201.23 | 188.78
2017-04-16 10:30 | 200.88 | 187.68
2017-04-16 11:00 | 200.84 | 187.29
2017-04-16 11:30 | 201.57 | 187.65
2017-04-16 12:00 | 201.85 | 188.01
2017-04-16 12:30 | 200.7 | 186.72
2017-04-16 13:00 | 201.25 | 187.68
2017-04-16 13:30 | 202.53 | 189.15
2017-04-16 14:00 | 203.7 | 190.6
2017-04-16 14:30 | 204.07 | 191.54
2017-04-16 15:00 | 205.23 | 191.87
2017-04-16 15:30 | 205.18 | 191.54
2017-04-16 16:00 | 205.93 | 192.52
2017-04-16 16:30 | 213.41 | 200.29
2017-04-16 17:00 | 220.66 | 207.56
2017-04-16 17:30 | 220.91 | 208.12
2017-04-16 18:00 | 219.46 | 206.79
2017-04-16 18:30 | 222.08 | 208.79
2017-04-16 19:00 | 223.15 | 209.54
2017-04-16 19:30 | 221.69 | 207.84
2017-04-16 20:00 | 220.6 | 206.69
2017-04-16 20:30 | 221.56 | 207.43
2017-04-16 21:00 | 220.64 | 206.37
2017-04-16 21:30 | 219.61 | 205.52
2017-04-16 22:00 | 217.82 | 203.72
2017-04-16 22:30 | 215.56 | 201.37
2017-04-16 23:00 | 214.59 | 199.77
2017-04-16 23:30 | 214.41 | 199.76
2017-04-17 | 212.97 | 199.16
2017-04-17 00:30 | 212.61 | 198.6
2017-04-17 01:00 | 211.98 | 197.83
2017-04-17 01:30 | 211.13 | 197.05
2017-04-17 02:00 | 210.99 | 196.36
2017-04-17 02:30 | 209.68 | 196.17
2017-04-17 03:00 | 209.31 | 196.13
2017-04-17 03:30 | 208.94 | 195.81
2017-04-17 04:00 | 208.91 | 195.73
2017-04-17 04:30 | 209.06 | 195.8
2017-04-17 05:00 | 209.54 | 196.39
2017-04-17 05:30 | 204.22 | 191.12
2017-04-17 06:00 | 199.62 | 186.27
2017-04-17 06:30 | 200.59 | 187.3
2017-04-17 07:00 | 202.5 | 190.65
2017-04-17 07:30 | 202.23 | 191.1
2017-04-17 08:00 | 202.49 | 191.07
2017-04-17 08:30 | 200.87 | 189.84
2017-04-17 09:00 | 201.86 | 189.98
2017-04-17 09:30 | 204.19 | 190.79
2017-04-17 10:00 | 204.02 | 190.55
2017-04-17 10:30 | 202.73 | 189.64
2017-04-17 11:00 | 206.47 | 194
2017-04-17 11:30 | 213.49 | 202.73
2017-04-17 12:00 | 214.53 | 203.72
2017-04-17 12:30 | 215.65 | 204.62
2017-04-17 13:00 | 215.92 | 205.15
2017-04-17 13:30 | 216.38 | 205.89
2017-04-17 14:00 | 217.17 | 206.54
2017-04-17 14:30 | 218.08 | 207.44
2017-04-17 15:00 | 218.71 | 208.1
2017-04-17 15:30 | 219.87 | 209.04
2017-04-17 16:00 | 220.19 | 209.71
2017-04-17 16:30 | 220.41 | 209.81
2017-04-17 17:00 | 218.35 | 207.06
2017-04-17 17:30 | 217.13 | 204.67
2017-04-17 18:00 | 217.31 | 204.27
2017-04-17 18:30 | 226.8 | 215.42
2017-04-17 19:00 | 221.49 | 208.44
2017-04-17 19:30 | 219.04 | 205.78
2017-04-17 20:00 | 217.48 | 204
2017-04-17 20:30 | 216.46 | 202.97
2017-04-17 21:00 | 214.7 | 200.89
2017-04-17 21:30 | 213.94 | 200.02
2017-04-17 22:00 | 212.73 | 198.72
2017-04-17 22:30 | 211.63 | 196.76
2017-04-17 23:00 | 210.62 | 195.22
2017-04-17 23:30 | 209.49 | 194.42
2017-04-18 | 208.33 | 193.61
2017-04-18 00:30 | 206.66 | 192.91
2017-04-18 01:00 | 205.39 | 192.78
2017-04-18 01:30 | 205.08 | 192.35
2017-04-18 02:00 | 204.82 | 192.04
2017-04-18 02:30 | 204.82 | 191.93
2017-04-18 03:00 | 204.58 | 191.83
2017-04-18 03:30 | 204.71 | 191.8
2017-04-18 04:00 | 204.9 | 191.95
2017-04-18 04:30 | 205.18 | 192.1
2017-04-18 05:00 | 206.28 | 193.52
2017-04-18 05:30 | 207.24 | 194.93
2017-04-18 06:00 | 208.68 | 196.14
2017-04-18 06:30 | 211.19 | 198.83
2017-04-18 07:00 | 204.46 | 192.21
2017-04-18 07:30 | 191.58 | 179.87
2017-04-18 08:00 | 191.3 | 179.6
2017-04-18 08:30 | 189.64 | 177.91
2017-04-18 09:00 | 188.83 | 176.89
2017-04-18 09:30 | 189.24 | 176.66
2017-04-18 10:00 | 188.88 | 176.1
2017-04-18 10:30 | 188.83 | 175.41
2017-04-18 11:00 | 188.12 | 174.64
2017-04-18 11:30 | 187.94 | 174.52
2017-04-18 12:00 | 188.02 | 174.88
2017-04-18 12:30 | 186.93 | 173.29
2017-04-18 13:00 | 187.34 | 174.04
2017-04-18 13:30 | 187.87 | 174.75
2017-04-18 14:00 | 189.01 | 176.14
2017-04-18 14:30 | 188.62 | 175.96
2017-04-18 15:00 | 188.71 | 175.79
2017-04-18 15:30 | 189.67 | 176.92
2017-04-18 16:00 | 190.75 | 178.12
2017-04-18 16:30 | 191.19 | 178.51
2017-04-18 17:00 | 190.44 | 177.45
2017-04-18 17:30 | 198.73 | 185.83
2017-04-18 18:00 | 212.19 | 199.39
2017-04-18 18:30 | 218.84 | 205.98
2017-04-18 19:00 | 220.32 | 207.39
2017-04-18 19:30 | 218.59 | 205.64
2017-04-18 20:00 | 213.65 | 200.82
2017-04-18 20:30 | 219.45 | 206.33
2017-04-18 21:00 | 222.21 | 208.94
2017-04-18 21:30 | 221.73 | 207.98
2017-04-18 22:00 | 218.93 | 204.86
2017-04-18 22:30 | 218.36 | 203.23
2017-04-18 23:00 | 218.12 | 202.73
2017-04-18 23:30 | 217.76 | 202.71
2017-04-19 | 216.02 | 201.71
2017-04-19 00:30 | 214.72 | 200.93
2017-04-19 01:00 | 213.68 | 200.54
2017-04-19 01:30 | 212.89 | 199.86
2017-04-19 02:00 | 212.13 | 199.58
2017-04-19 02:30 | 212.24 | 199.57
2017-04-19 03:00 | 212.17 | 199.1
2017-04-19 03:30 | 212.06 | 199.06
2017-04-19 04:00 | 212.52 | 199.36
2017-04-19 04:30 | 213.09 | 200.04
2017-04-19 05:00 | 212.8 | 200.14
2017-04-19 05:30 | 214.16 | 201.53
2017-04-19 06:00 | 215.59 | 202.54
2017-04-19 06:30 | 218.43 | 204.91
2017-04-19 07:00 | 221.04 | 206.88
2017-04-19 07:30 | 220.81 | 207.25
2017-04-19 08:00 | 219.92 | 206.31
2017-04-19 08:30 | 218.74 | 205.26
2017-04-19 09:00 | 218.14 | 204.81
2017-04-19 09:30 | 218.56 | 204.85
2017-04-19 10:00 | 217.64 | 204.06
2017-04-19 10:30 | 217.47 | 203.78
2017-04-19 11:00 | 218.98 | 205.42
2017-04-19 11:30 | 219.52 | 206.35
2017-04-19 12:00 | 219.84 | 206.8
2017-04-19 12:30 | 220.59 | 207.33
2017-04-19 13:00 | 222.09 | 208.75
2017-04-19 13:30 | 223.63 | 210.43
2017-04-19 14:00 | 223.76 | 210.78
2017-04-19 14:30 | 223.95 | 211.21
2017-04-19 15:00 | 224.41 | 211.53
2017-04-19 15:30 | 225.31 | 212.17
2017-04-19 16:00 | 226.9 | 213.53
2017-04-19 16:30 | 227.35 | 213.79
2017-04-19 17:00 | 228.28 | 214.62
2017-04-19 17:30 | 228.08 | 214.56
2017-04-19 18:00 | 231.53 | 218.19
2017-04-19 18:30 | 234.69 | 221.24
2017-04-19 19:00 | 235.55 | 222.08
2017-04-19 19:30 | 233.84 | 220.04
2017-04-19 20:00 | 232.06 | 218.05
2017-04-19 20:30 | 230.72 | 216.53
2017-04-19 21:00 | 229.4 | 215.27
2017-04-19 21:30 | 228.45 | 214.11
2017-04-19 22:00 | 226.68 | 212.06
2017-04-19 22:30 | 225.87 | 210.15
2017-04-19 23:00 | 223.67 | 208.25
2017-04-19 23:30 | 223 | 207.76
2017-04-20 | 221.38 | 206.73
2017-04-20 00:30 | 219.84 | 205.5
2017-04-20 01:00 | 218.85 | 205.58
2017-04-20 01:30 | 218.37 | 204.9
2017-04-20 02:00 | 217.97 | 204.49
2017-04-20 02:30 | 217.28 | 203.57
2017-04-20 03:00 | 217.08 | 203.36
2017-04-20 03:30 | 216.81 | 203.12
2017-04-20 04:00 | 216.69 | 203.18
2017-04-20 04:30 | 217.26 | 203.8
2017-04-20 05:00 | 217.31 | 204
2017-04-20 05:30 | 218.12 | 204.94
2017-04-20 06:00 | 220.47 | 207.11
2017-04-20 06:30 | 222.64 | 209.26
2017-04-20 07:00 | 224.58 | 210.99
2017-04-20 07:30 | 225.18 | 211.94
2017-04-20 08:00 | 223.59 | 210.73
2017-04-20 08:30 | 221.26 | 208.58
2017-04-20 09:00 | 220.67 | 207.99
2017-04-20 09:30 | 221.15 | 208.17
2017-04-20 10:00 | 220.69 | 207.46
2017-04-20 10:30 | 220.15 | 206.5
2017-04-20 11:00 | 216.92 | 202.86
2017-04-20 11:30 | 217.85 | 204.55
2017-04-20 12:00 | 219.43 | 206
2017-04-20 12:30 | 220.46 | 206.74
2017-04-20 13:00 | 220.32 | 206.62
2017-04-20 13:30 | 219.99 | 206.67
2017-04-20 14:00 | 220.66 | 207.42
2017-04-20 14:30 | 221.65 | 207.47
2017-04-20 15:00 | 223.19 | 208.41
2017-04-20 15:30 | 223.96 | 208.95
2017-04-20 16:00 | 225.29 | 210.55
2017-04-20 16:30 | 225.8 | 210.72
2017-04-20 17:00 | 227 | 211.66
2017-04-20 17:30 | 227.62 | 212.29
2017-04-20 18:00 | 229.44 | 214.29
2017-04-20 18:30 | 232.55 | 217.46
2017-04-20 19:00 | 234.25 | 219.15
2017-04-20 19:30 | 233.09 | 217.91
2017-04-20 20:00 | 231.41 | 216.15
2017-04-20 20:30 | 230.68 | 215.07
2017-04-20 21:00 | 229.14 | 213.37
2017-04-20 21:30 | 228.11 | 212.56
2017-04-20 22:00 | 226.27 | 210.8
2017-04-20 22:30 | 224.33 | 208.52
2017-04-20 23:00 | 223.02 | 206.47
2017-04-20 23:30 | 221.32 | 205.83
2017-04-21 | 218.73 | 203.74
2017-04-21 00:30 | 218.19 | 203.7
2017-04-21 01:00 | 217.39 | 202.74
2017-04-21 01:30 | 216.8 | 202.44
2017-04-21 02:00 | 215.98 | 202.08
2017-04-21 02:30 | 215.5 | 201.76
2017-04-21 03:00 | 215.35 | 201.7
2017-04-21 03:30 | 215.45 | 201.5
2017-04-21 04:00 | 214.48 | 200.65
2017-04-21 04:30 | 214.55 | 200.61
2017-04-21 05:00 | 215.79 | 201.47
2017-04-21 05:30 | 218.16 | 203.38
2017-04-21 06:00 | 220.48 | 205.53
2017-04-21 06:30 | 223 | 207.89
2017-04-21 07:00 | 224.31 | 209.14
2017-04-21 07:30 | 224.93 | 210.19
2017-04-21 08:00 | 224.39 | 210.03
2017-04-21 08:30 | 220.59 | 206.27
2017-04-21 09:00 | 220.33 | 205.77
2017-04-21 09:30 | 222.03 | 207.31
2017-04-21 10:00 | 221.27 | 206.72
2017-04-21 10:30 | 220.74 | 205.91
2017-04-21 11:00 | 219.81 | 205
2017-04-21 11:30 | 219.25 | 204.35
2017-04-21 12:00 | 219.73 | 204.43
2017-04-21 12:30 | 219 | 203.72
2017-04-21 13:00 | 219.18 | 203.77
2017-04-21 13:30 | 221.98 | 207.18
2017-04-21 14:00 | 223.02 | 208.33
2017-04-21 14:30 | 223.75 | 209.03
2017-04-21 15:00 | 223.34 | 208.82
2017-04-21 15:30 | 225.78 | 211.48
2017-04-21 16:00 | 227.66 | 213.2
2017-04-21 16:30 | 228.64 | 213.53
2017-04-21 17:00 | 228.66 | 213.56
2017-04-21 17:30 | 228 | 213.27
2017-04-21 18:00 | 230.01 | 215.7
2017-04-21 18:30 | 232.77 | 218.59
2017-04-21 19:00 | 233.29 | 219.06
2017-04-21 19:30 | 231.99 | 217.54
2017-04-21 20:00 | 231.05 | 216.58
2017-04-21 20:30 | 229.81 | 215.18
2017-04-21 21:00 | 228.9 | 213.99
2017-04-21 21:30 | 227.72 | 213.4
2017-04-21 22:00 | 226.46 | 211.82
2017-04-21 22:30 | 223.77 | 210.24
2017-04-21 23:00 | 221.86 | 208.45
2017-04-21 23:30 | 221.45 | 208.19
2017-04-22 | 220.26 | 207.08
2017-04-22 00:30 | 219.01 | 205.91
2017-04-22 01:00 | 218.43 | 205.03
2017-04-22 01:30 | 217.99 | 204.47
2017-04-22 02:00 | 217.33 | 204.06
2017-04-22 02:30 | 216.92 | 203.57
2017-04-22 03:00 | 216.6 | 203.35
2017-04-22 03:30 | 216.34 | 203.1
2017-04-22 04:00 | 216.21 | 203.04
2017-04-22 04:30 | 216.64 | 203.44
2017-04-22 05:00 | 217.01 | 203.74
2017-04-22 05:30 | 217.35 | 204.47
2017-04-22 06:00 | 214.9 | 201.96
2017-04-22 06:30 | 200.28 | 187.98
2017-04-22 07:00 | 201.97 | 188.53
2017-04-22 07:30 | 202.56 | 188.18
2017-04-22 08:00 | 202.27 | 187.36
2017-04-22 08:30 | 201.84 | 186.71
2017-04-22 09:00 | 200.36 | 185.13
2017-04-22 09:30 | 201.3 | 186.3
2017-04-22 10:00 | 200.28 | 185.26
2017-04-22 10:30 | 200.04 | 185.03
2017-04-22 11:00 | 200.85 | 185.86
2017-04-22 11:30 | 200.65 | 185.52
2017-04-22 12:00 | 200.81 | 185.32
2017-04-22 12:30 | 201.6 | 185.94
2017-04-22 13:00 | 209.19 | 193.4
2017-04-22 13:30 | 218.38 | 202.89
2017-04-22 14:00 | 219.98 | 204.41
2017-04-22 14:30 | 220.96 | 205.26
2017-04-22 15:00 | 222.2 | 206.63
2017-04-22 15:30 | 221.96 | 206.94
2017-04-22 16:00 | 222.63 | 207.81
2017-04-22 16:30 | 222.83 | 208.01
2017-04-22 17:00 | 223.78 | 208.81
2017-04-22 17:30 | 207.66 | 192.86
2017-04-22 18:00 | 204.16 | 190.07
2017-04-22 18:30 | 209.93 | 195.27
2017-04-22 19:00 | 213.05 | 198.24
2017-04-22 19:30 | 212.07 | 197.11
2017-04-22 20:00 | 210.53 | 195.5
2017-04-22 20:30 | 209.58 | 194.73
2017-04-22 21:00 | 208.01 | 192.83
2017-04-22 21:30 | 206.57 | 192.04
2017-04-22 22:00 | 205.93 | 191.46
2017-04-22 22:30 | 221.31 | 207.76
2017-04-22 23:00 | 242.87 | 229.69
2017-04-22 23:30 | 243.07 | 229.98
2017-04-23 | 242.17 | 229.92
2017-04-23 00:30 | 238.33 | 229.07
2017-04-23 01:00 | 228.5 | 217.14
2017-04-23 01:30 | 220.91 | 210.58
2017-04-23 02:00 | 217.84 | 207.68
2017-04-23 02:30 | 216.27 | 205.01
2017-04-23 03:00 | 208.95 | 196.67
2017-04-23 03:30 | 209.29 | 196.79
2017-04-23 04:00 | 209.86 | 197.5
2017-04-23 04:30 | 209.73 | 197.54
2017-04-23 05:00 | 209.9 | 197.56
2017-04-23 05:30 | 209.85 | 197.68
2017-04-23 06:00 | 210.08 | 198.21
2017-04-23 06:30 | 210.81 | 198.83
2017-04-23 07:00 | 210.95 | 198.74
2017-04-23 07:30 | 210.62 | 198.65
2017-04-23 08:00 | 207.79 | 195.95
2017-04-23 08:30 | 207.45 | 195.52
2017-04-23 09:00 | 208.67 | 196.01
2017-04-23 09:30 | 208.73 | 195.44
2017-04-23 10:00 | 191.38 | 178.08
2017-04-23 10:30 | 189.5 | 176.32
2017-04-23 11:00 | 188.51 | 175.27
2017-04-23 11:30 | 188.57 | 174.86
2017-04-23 12:00 | 188.51 | 174.78
2017-04-23 12:30 | 187.82 | 174.05
2017-04-23 13:00 | 189.27 | 175.59
2017-04-23 13:30 | 190.64 | 176.22
2017-04-23 14:00 | 203.55 | 189.7
2017-04-23 14:30 | 212.05 | 198.4
2017-04-23 15:00 | 210.64 | 196.54
2017-04-23 15:30 | 212.76 | 199.25
2017-04-23 16:00 | 213.99 | 200.63
2017-04-23 16:30 | 214.3 | 200.72
2017-04-23 17:00 | 215.04 | 201.4
2017-04-23 17:30 | 215.67 | 202.14
2017-04-23 18:00 | 217.16 | 203.33
2017-04-23 18:30 | 217.91 | 202.96
2017-04-23 19:00 | 218.14 | 202.01
2017-04-23 19:30 | 216.85 | 200.15
2017-04-23 20:00 | 214.85 | 197.77
2017-04-23 20:30 | 214.21 | 197.03
2017-04-23 21:00 | 214.11 | 196.79
2017-04-23 21:30 | 212.54 | 195.94
2017-04-23 22:00 | 210.77 | 194.62
2017-04-23 22:30 | 209.88 | 193.15
2017-04-23 23:00 | 208.81 | 191.71
2017-04-23 23:30 | 206.81 | 190.33
2017-04-24 | 204.62 | 188.92
2017-04-24 00:30 | 203.79 | 188.38
2017-04-24 01:00 | 202.56 | 187.4
2017-04-24 01:30 | 201.85 | 186.93
2017-04-24 02:00 | 201.35 | 186.33
2017-04-24 02:30 | 202.05 | 187.11
2017-04-24 03:00 | 203.4 | 188.91
2017-04-24 03:30 | 203.28 | 188.9
2017-04-24 04:00 | 204.99 | 190.45
2017-04-24 04:30 | 204.26 | 190.52
2017-04-24 05:00 | 196.52 | 182.84
2017-04-24 05:30 | 198.85 | 184.97
2017-04-24 06:00 | 207.66 | 193.59
2017-04-24 06:30 | 211.97 | 198.01
2017-04-24 07:00 | 215.25 | 201.58
2017-04-24 07:30 | 216.43 | 203.16
2017-04-24 08:00 | 217.22 | 203.78
2017-04-24 08:30 | 215.89 | 202.66
2017-04-24 09:00 | 214.91 | 201.51
2017-04-24 09:30 | 213.87 | 200.18
2017-04-24 10:00 | 214.04 | 200.17
2017-04-24 10:30 | 214.98 | 200.95
2017-04-24 11:00 | 214.51 | 200.6
2017-04-24 11:30 | 215.5 | 201.77
2017-04-24 12:00 | 215.78 | 202
2017-04-24 12:30 | 216.02 | 201.85
2017-04-24 13:00 | 216.19 | 202.23
2017-04-24 13:30 | 216.69 | 203
2017-04-24 14:00 | 216.99 | 203.79
2017-04-24 14:30 | 218.59 | 205.42
2017-04-24 15:00 | 219.19 | 205.93
2017-04-24 15:30 | 220.73 | 207.5
2017-04-24 16:00 | 220.87 | 207.64
2017-04-24 16:30 | 221.1 | 207.67
2017-04-24 17:00 | 221.07 | 207.28
2017-04-24 17:30 | 221.75 | 207.9
2017-04-24 18:00 | 223.22 | 209.68
2017-04-24 18:30 | 226.14 | 212.42
2017-04-24 19:00 | 227.07 | 213.12
2017-04-24 19:30 | 225.22 | 211
2017-04-24 20:00 | 223.46 | 209.15
2017-04-24 20:30 | 221.75 | 207.15
2017-04-24 21:00 | 219.44 | 204.84
2017-04-24 21:30 | 217.94 | 203.52
2017-04-24 22:00 | 216.17 | 201.89
2017-04-24 22:30 | 215.02 | 199.63
2017-04-24 23:00 | 214.51 | 198.79
2017-04-24 23:30 | 213.41 | 198.25
2017-04-25 | 211.95 | 197.2
2017-04-25 00:30 | 210.2 | 196.27
2017-04-25 01:00 | 208.43 | 195.14
2017-04-25 01:30 | 207.9 | 194.79
2017-04-25 02:00 | 208.02 | 194.62
2017-04-25 02:30 | 207.07 | 193.73
2017-04-25 03:00 | 204.37 | 192.46
2017-04-25 03:30 | 205.46 | 193.64
2017-04-25 04:00 | 205.76 | 193.67
2017-04-25 04:30 | 206.32 | 193.68
2017-04-25 05:00 | 207.01 | 194.78
2017-04-25 05:30 | 208.38 | 196.36
2017-04-25 06:00 | 209.41 | 197.5
2017-04-25 06:30 | 211.16 | 199.27
2017-04-25 07:00 | 212.18 | 200.79
2017-04-25 07:30 | 213.58 | 202
2017-04-25 08:00 | 211.33 | 199.52
2017-04-25 08:30 | 210.35 | 198.5
2017-04-25 09:00 | 211.22 | 199.46
2017-04-25 09:30 | 210.89 | 199.04
2017-04-25 10:00 | 211.86 | 200.05
2017-04-25 10:30 | 211.25 | 199.52
2017-04-25 11:00 | 209.98 | 198.52
2017-04-25 11:30 | 209.9 | 198.72
2017-04-25 12:00 | 210.78 | 199.08
2017-04-25 12:30 | 211.5 | 199.81
2017-04-25 13:00 | 213.46 | 201.91
2017-04-25 13:30 | 213.9 | 202.31
2017-04-25 14:00 | 215.19 | 203.4
2017-04-25 14:30 | 215.29 | 203.74
2017-04-25 15:00 | 215.73 | 203.78
2017-04-25 15:30 | 216.37 | 203.67
2017-04-25 16:00 | 217.77 | 205.01
2017-04-25 16:30 | 218.63 | 205.64
2017-04-25 17:00 | 218.45 | 205.42
2017-04-25 17:30 | 220.26 | 206.4
2017-04-25 18:00 | 222.1 | 208.29
2017-04-25 18:30 | 224.18 | 210.8
2017-04-25 19:00 | 224.35 | 210.84
2017-04-25 19:30 | 222.77 | 208.94
2017-04-25 20:00 | 221.74 | 207.66
2017-04-25 20:30 | 220.7 | 206.56
2017-04-25 21:00 | 218.3 | 204.26
2017-04-25 21:30 | 218.12 | 204.53
2017-04-25 22:00 | 216.27 | 202.71
2017-04-25 22:30 | 215.32 | 200.85
2017-04-25 23:00 | 213.63 | 198.8
2017-04-25 23:30 | 212.06 | 196.97
2017-04-26 | 204.81 | 195.95
2017-04-26 00:30 | 203.79 | 195.07
2017-04-26 01:00 | 202.64 | 194.09
2017-04-26 01:30 | 202.43 | 193.77
2017-04-26 02:00 | 202.47 | 194.06
2017-04-26 02:30 | 202.13 | 194.68
2017-04-26 03:00 | 202.14 | 194.86
2017-04-26 03:30 | 201.77 | 194.58
2017-04-26 04:00 | 202.16 | 194.85
2017-04-26 04:30 | 201.8 | 194.48
2017-04-26 05:00 | 202.07 | 194.77
2017-04-26 05:30 | 203.01 | 195.88
2017-04-26 06:00 | 205.2 | 197.81
2017-04-26 06:30 | 207.65 | 200.38
2017-04-26 07:00 | 210.43 | 202.05
2017-04-26 07:30 | 211.73 | 203.85
2017-04-26 08:00 | 212.6 | 204.63
2017-04-26 08:30 | 211.23 | 203.57
2017-04-26 09:00 | 210.94 | 203.09
2017-04-26 09:30 | 211.24 | 202.72
2017-04-26 10:00 | 211.57 | 203.08
2017-04-26 10:30 | 215.62 | 206.72
2017-04-26 11:00 | 211.17 | 202.71
2017-04-26 11:30 | 211.63 | 202.85
2017-04-26 12:00 | 212.62 | 203.04
2017-04-26 12:30 | 214.59 | 204.74
2017-04-26 13:00 | 215.59 | 205.49
2017-04-26 13:30 | 215.67 | 205.64
2017-04-26 14:00 | 215.43 | 205.37
2017-04-26 14:30 | 214.75 | 204.81
2017-04-26 15:00 | 214.91 | 204.9
2017-04-26 15:30 | 215.57 | 205.42
2017-04-26 16:00 | 216.38 | 206.15
2017-04-26 16:30 | 217.47 | 207.43
2017-04-26 17:00 | 217.84 | 207.88
2017-04-26 17:30 | 215.83 | 205.79
2017-04-26 18:00 | 220.42 | 210.25
2017-04-26 18:30 | 223.66 | 213.7
2017-04-26 19:00 | 224.55 | 214.55
2017-04-26 19:30 | 223.04 | 212.73
2017-04-26 20:00 | 222.47 | 212.02
2017-04-26 20:30 | 222.06 | 211.42
2017-04-26 21:00 | 220.12 | 209.24
2017-04-26 21:30 | 220.24 | 209.8
2017-04-26 22:00 | 218.64 | 209
2017-04-26 22:30 | 216.57 | 206.88
2017-04-26 23:00 | 214.26 | 205.43
2017-04-26 23:30 | 212.9 | 204.94
2017-04-27 | 211.4 | 203.51
2017-04-27 00:30 | 210.77 | 203.16
2017-04-27 01:00 | 211.1 | 203.57
2017-04-27 01:30 | 209.23 | 201.49
2017-04-27 02:00 | 208.8 | 201.16
2017-04-27 02:30 | 209.35 | 200.53
2017-04-27 03:00 | 210.74 | 201.17
2017-04-27 03:30 | 210.9 | 200.99
2017-04-27 04:00 | 211.56 | 201.66
2017-04-27 04:30 | 211.64 | 201.73
2017-04-27 05:00 | 211.59 | 201.72
2017-04-27 05:30 | 213.07 | 203.53
2017-04-27 06:00 | 217.03 | 207
2017-04-27 06:30 | 221.7 | 210.51
2017-04-27 07:00 | 224.13 | 213.68
2017-04-27 07:30 | 224.31 | 215.96
2017-04-27 08:00 | 224.59 | 216.25
2017-04-27 08:30 | 224.16 | 215.7
2017-04-27 09:00 | 223.58 | 214.95
2017-04-27 09:30 | 219.24 | 210.56
2017-04-27 10:00 | 217.52 | 208.98
2017-04-27 10:30 | 215.69 | 207.03
2017-04-27 11:00 | 214.7 | 205.97
2017-04-27 11:30 | 214.02 | 204.9
2017-04-27 12:00 | 215.38 | 206.71
2017-04-27 12:30 | 216.86 | 207.92
2017-04-27 13:00 | 219.44 | 210.11
2017-04-27 13:30 | 220.35 | 211.11
2017-04-27 14:00 | 221.15 | 212.08
2017-04-27 14:30 | 221.13 | 212.1
2017-04-27 15:00 | 221.84 | 212.7
2017-04-27 15:30 | 223.36 | 214.03
2017-04-27 16:00 | 225.17 | 215.52
2017-04-27 16:30 | 226.71 | 216.86
2017-04-27 17:00 | 228.13 | 218.19
2017-04-27 17:30 | 229.25 | 218.88
2017-04-27 18:00 | 232.05 | 221.72
2017-04-27 18:30 | 232.8 | 223.17
2017-04-27 19:00 | 235.18 | 225.31
2017-04-27 19:30 | 235.2 | 224.9
2017-04-27 20:00 | 233.57 | 223.34
2017-04-27 20:30 | 234.78 | 224.57
2017-04-27 21:00 | 234.44 | 224.28
2017-04-27 21:30 | 232.56 | 223.21
2017-04-27 22:00 | 230.34 | 221.15
2017-04-27 22:30 | 227.75 | 218.61
2017-04-27 23:00 | 225.13 | 215.99
2017-04-27 23:30 | 224.49 | 215.45
2017-04-28 | 224.35 | 215.34
2017-04-28 00:30 | 223.49 | 214.73
2017-04-28 01:00 | 221.97 | 214.11
2017-04-28 01:30 | 220.35 | 213.02
2017-04-28 02:00 | 219.87 | 212.76
2017-04-28 02:30 | 220.58 | 212.88
2017-04-28 03:00 | 220.28 | 212.49
2017-04-28 03:30 | 220.46 | 212.57
2017-04-28 04:00 | 221.32 | 213.48
2017-04-28 04:30 | 221.6 | 213.95
2017-04-28 05:00 | 223.78 | 215.73
2017-04-28 05:30 | 226.17 | 217.63
2017-04-28 06:00 | 228.75 | 219.79
2017-04-28 06:30 | 233.73 | 223.7
2017-04-28 07:00 | 237.67 | 227.5
2017-04-28 07:30 | 237.07 | 229.44
2017-04-28 08:00 | 235.09 | 227.7
2017-04-28 08:30 | 234.37 | 227
2017-04-28 09:00 | 231.66 | 224.03
2017-04-28 09:30 | 228.52 | 220.57
2017-04-28 10:00 | 226.64 | 218.32
2017-04-28 10:30 | 224.52 | 216.08
2017-04-28 11:00 | 222.32 | 213.64
2017-04-28 11:30 | 221.39 | 212.31
2017-04-28 12:00 | 223.32 | 214.35
2017-04-28 12:30 | 223.82 | 214.63
2017-04-28 13:00 | 223.89 | 214.15
2017-04-28 13:30 | 224.37 | 214.74
2017-04-28 14:00 | 224.84 | 215.27
2017-04-28 14:30 | 225.04 | 215.45
2017-04-28 15:00 | 224.68 | 214.87
2017-04-28 15:30 | 225.32 | 215.62
2017-04-28 16:00 | 226.77 | 217.72
2017-04-28 16:30 | 229.02 | 219.97
2017-04-28 17:00 | 230.8 | 221.66
2017-04-28 17:30 | 233.26 | 224.28
2017-04-28 18:00 | 236.75 | 228.03
2017-04-28 18:30 | 239.93 | 231.4
2017-04-28 19:00 | 241.3 | 232.68
2017-04-28 19:30 | 240.4 | 231.65
2017-04-28 20:00 | 239.37 | 230.5
2017-04-28 20:30 | 237.7 | 228.84
2017-04-28 21:00 | 235.27 | 226.44
2017-04-28 21:30 | 233.79 | 225.43
2017-04-28 22:00 | 232.18 | 224.39
2017-04-28 22:30 | 230.43 | 222.29
2017-04-28 23:00 | 229.07 | 220.28
2017-04-28 23:30 | 228.08 | 219.33
2017-04-29 | 226.05 | 218.14
2017-04-29 00:30 | 224.38 | 216.87
2017-04-29 01:00 | 224.1 | 215.19
2017-04-29 01:30 | 223.82 | 214.61
2017-04-29 02:00 | 223.01 | 213.74
2017-04-29 02:30 | 223.73 | 214.36
2017-04-29 03:00 | 224.62 | 214.82
2017-04-29 03:30 | 224.98 | 214.93
2017-04-29 04:00 | 224.94 | 215.01
2017-04-29 04:30 | 225.3 | 215.45
2017-04-29 05:00 | 225.87 | 216
2017-04-29 05:30 | 225.98 | 215.99
2017-04-29 06:00 | 226.85 | 216.91
2017-04-29 06:30 | 228.53 | 219.07
2017-04-29 07:00 | 229.81 | 220.65
2017-04-29 07:30 | 231.4 | 221.81
2017-04-29 08:00 | 229.92 | 220.12
2017-04-29 08:30 | 227.42 | 218.01
2017-04-29 09:00 | 225.72 | 215.51
2017-04-29 09:30 | 224.97 | 214.51
2017-04-29 10:00 | 224.67 | 214.3
2017-04-29 10:30 | 222.79 | 212.36
2017-04-29 11:00 | 221.63 | 210.75
2017-04-29 11:30 | 220.38 | 209.53
2017-04-29 12:00 | 221.11 | 209.92
2017-04-29 12:30 | 220.78 | 209.62
2017-04-29 13:00 | 220.97 | 209.62
2017-04-29 13:30 | 222.8 | 211.03
2017-04-29 14:00 | 223.32 | 211.53
2017-04-29 14:30 | 222.75 | 211.07
2017-04-29 15:00 | 222.4 | 210.59
2017-04-29 15:30 | 224.25 | 212.41
2017-04-29 16:00 | 225.92 | 214.04
2017-04-29 16:30 | 227.49 | 215.92
2017-04-29 17:00 | 229.2 | 217.91
2017-04-29 17:30 | 230.34 | 218.89
2017-04-29 18:00 | 233.37 | 222.04
2017-04-29 18:30 | 236.22 | 225.06
2017-04-29 19:00 | 236.95 | 225.8
2017-04-29 19:30 | 235.84 | 224.55
2017-04-29 20:00 | 234.41 | 223.07
2017-04-29 20:30 | 233.97 | 222.55
2017-04-29 21:00 | 233.21 | 221.58
2017-04-29 21:30 | 232.61 | 221.21
2017-04-29 22:00 | 231.21 | 220.19
2017-04-29 22:30 | 230.13 | 219.21
2017-04-29 23:00 | 228.89 | 217.65
2017-04-29 23:30 | 227.83 | 216.63
2017-04-30 | 224.83 | 214.66
2017-04-30 00:30 | 224.34 | 214.22
2017-04-30 01:00 | 221.99 | 211.88
2017-04-30 01:30 | 221.24 | 211.19
2017-04-30 02:00 | 220.86 | 210.77
2017-04-30 02:30 | 221.31 | 210.93
2017-04-30 03:00 | 220.79 | 211.07
2017-04-30 03:30 | 220.38 | 211.13
2017-04-30 04:00 | 220.96 | 211.79
2017-04-30 04:30 | 221.66 | 212.33
2017-04-30 05:00 | 221.94 | 212.69
2017-04-30 05:30 | 222.36 | 213.11
2017-04-30 06:00 | 223.51 | 214.44
2017-04-30 06:30 | 223.51 | 214.78
2017-04-30 07:00 | 225.23 | 216.57
2017-04-30 07:30 | 226.7 | 217.66
2017-04-30 08:00 | 224.69 | 215.5
2017-04-30 08:30 | 222.71 | 213.46
2017-04-30 09:00 | 220.26 | 210.89
2017-04-30 09:30 | 221.35 | 212.07
2017-04-30 10:00 | 222.86 | 213.68
2017-04-30 10:30 | 221.93 | 212.62
2017-04-30 11:00 | 220.75 | 211.36
2017-04-30 11:30 | 220.28 | 210.96
2017-04-30 12:00 | 220.89 | 211.6
2017-04-30 12:30 | 220.18 | 210.64
2017-04-30 13:00 | 220.45 | 210.72
2017-04-30 13:30 | 220.84 | 211.12
2017-04-30 14:00 | 220.74 | 210.94
2017-04-30 14:30 | 221.96 | 212.18
2017-04-30 15:00 | 222.23 | 212.39
2017-04-30 15:30 | 223.47 | 213.65
2017-04-30 16:00 | 224.87 | 214.94
2017-04-30 16:30 | 226.56 | 216.82
2017-04-30 17:00 | 228.44 | 218.56
2017-04-30 17:30 | 228.71 | 218.56
2017-04-30 18:00 | 232.67 | 221.84
2017-04-30 18:30 | 235.96 | 225.06
2017-04-30 19:00 | 235.99 | 224.97
2017-04-30 19:30 | 234.21 | 223.02
2017-04-30 20:00 | 231.83 | 220.49
2017-04-30 20:30 | 230.76 | 219.27
2017-04-30 21:00 | 229.68 | 218.15
2017-04-30 21:30 | 229.04 | 217.95
2017-04-30 22:00 | 228.16 | 216.9
2017-04-30 22:30 | 226.72 | 215.21
2017-04-30 23:00 | 225.51 | 213.87
2017-04-30 23:30 | 225.25 | 213.78
2017-05-01 | 223.39 | 212.87
2017-05-01 00:30 | 222.06 | 211.87
2017-05-01 01:00 | 221.27 | 211.13
2017-05-01 01:30 | 220.23 | 210.22
2017-05-01 02:00 | 219.47 | 209.55
2017-05-01 02:30 | 218.84 | 208.88
2017-05-01 03:00 | 219.54 | 209.49
2017-05-01 03:30 | 219.18 | 209.22
2017-05-01 04:00 | 218.93 | 208.83
2017-05-01 04:30 | 217.25 | 207.06
2017-05-01 05:00 | 219.05 | 208.88
2017-05-01 05:30 | 220.37 | 210.42
2017-05-01 06:00 | 221.22 | 211.43
2017-05-01 06:30 | 222.11 | 212.93
2017-05-01 07:00 | 223.57 | 214.58
2017-05-01 07:30 | 223.77 | 215.02
2017-05-01 08:00 | 223.13 | 214.2
2017-05-01 08:30 | 223.99 | 214.51
2017-05-01 09:00 | 223.59 | 214.04
2017-05-01 09:30 | 223.07 | 213.44
2017-05-01 10:00 | 223.9 | 214.41
2017-05-01 10:30 | 223.26 | 213.6
2017-05-01 11:00 | 222.1 | 212.45
2017-05-01 11:30 | 222.71 | 213.04
2017-05-01 12:00 | 222.64 | 212.94
2017-05-01 12:30 | 222.37 | 212.67
2017-05-01 13:00 | 222.87 | 213.27
2017-05-01 13:30 | 223.03 | 213.38
2017-05-01 14:00 | 224.02 | 214.6
2017-05-01 14:30 | 224.06 | 214.68
2017-05-01 15:00 | 228.72 | 219.13
2017-05-01 15:30 | 235.48 | 225.42
2017-05-01 16:00 | 235.89 | 225.91
2017-05-01 16:30 | 237.68 | 227.12
2017-05-01 17:00 | 239.34 | 228.47
2017-05-01 17:30 | 240.38 | 229.52
2017-05-01 18:00 | 245.16 | 233.24
2017-05-01 18:30 | 246.05 | 233.98
2017-05-01 19:00 | 246.42 | 234.24
2017-05-01 19:30 | 247.66 | 235.17
2017-05-01 20:00 | 245.18 | 232.59
2017-05-01 20:30 | 242.76 | 229.85
2017-05-01 21:00 | 236.84 | 223.26
2017-05-01 21:30 | 232.23 | 219.82
2017-05-01 22:00 | 230.46 | 218.2
2017-05-01 22:30 | 229.31 | 216.78
2017-05-01 23:00 | 227.7 | 215.17
2017-05-01 23:30 | 227.18 | 214.57
2017-05-02 | 225.45 | 213.53
2017-05-02 00:30 | 224.72 | 213.19
2017-05-02 01:00 | 223.84 | 212.35
2017-05-02 01:30 | 223.08 | 211.68
2017-05-02 02:00 | 222.49 | 211.19
2017-05-02 02:30 | 221.06 | 209.76
2017-05-02 03:00 | 220.25 | 208.95
2017-05-02 03:30 | 220.5 | 209.27
2017-05-02 04:00 | 221.25 | 210.13
2017-05-02 04:30 | 222.01 | 211.03
2017-05-02 05:00 | 222.8 | 211.85
2017-05-02 05:30 | 224.04 | 213.46
2017-05-02 06:00 | 226.08 | 215.82
2017-05-02 06:30 | 228.65 | 218.98
2017-05-02 07:00 | 231.05 | 220.89
2017-05-02 07:30 | 233.34 | 223.32
2017-05-02 08:00 | 233.43 | 223.49
2017-05-02 08:30 | 232.66 | 222.62
2017-05-02 09:00 | 231.39 | 221.11
2017-05-02 09:30 | 229.93 | 219.55
2017-05-02 10:00 | 229.27 | 218.94
2017-05-02 10:30 | 227.97 | 217.52
2017-05-02 11:00 | 228.11 | 217.72
2017-05-02 11:30 | 229.07 | 218.82
2017-05-02 12:00 | 229.77 | 219.3
2017-05-02 12:30 | 229.41 | 218.84
2017-05-02 13:00 | 229.69 | 219.1
2017-05-02 13:30 | 230.93 | 220.38
2017-05-02 14:00 | 231.91 | 221.11
2017-05-02 14:30 | 234.58 | 222.78
2017-05-02 15:00 | 235.07 | 223.39
2017-05-02 15:30 | 234.56 | 222.85
2017-05-02 16:00 | 235.02 | 223.22
2017-05-02 16:30 | 236.24 | 223.66
2017-05-02 17:00 | 236.73 | 224
2017-05-02 17:30 | 238.02 | 225.2
2017-05-02 18:00 | 241 | 228.3
2017-05-02 18:30 | 243.9 | 231.46
2017-05-02 19:00 | 243.58 | 231.04
2017-05-02 19:30 | 241.5 | 228.49
2017-05-02 20:00 | 239.56 | 226.16
2017-05-02 20:30 | 237.97 | 224.25
2017-05-02 21:00 | 234.42 | 223.04
2017-05-02 21:30 | 233.28 | 222.84
2017-05-02 22:00 | 230.81 | 220.93
2017-05-02 22:30 | 229.29 | 218.88
2017-05-02 23:00 | 227.33 | 217.1
2017-05-02 23:30 | 226.26 | 216.35
2017-05-03 | 225.1 | 214.96
2017-05-03 00:30 | 223.88 | 213.9
2017-05-03 01:00 | 222.38 | 213.09
2017-05-03 01:30 | 221.4 | 212.4
2017-05-03 02:00 | 221.13 | 212.02
2017-05-03 02:30 | 220.68 | 211.74
2017-05-03 03:00 | 220.31 | 211.43
2017-05-03 03:30 | 220.12 | 211.18
2017-05-03 04:00 | 220.13 | 211.19
2017-05-03 04:30 | 220.75 | 211.78
2017-05-03 05:00 | 221.01 | 212.07
2017-05-03 05:30 | 222.82 | 214.03
2017-05-03 06:00 | 223.8 | 215.19
2017-05-03 06:30 | 227.63 | 218.29
2017-05-03 07:00 | 229.6 | 219.62
2017-05-03 07:30 | 233.25 | 223.11
2017-05-03 08:00 | 232.96 | 222.99
2017-05-03 08:30 | 231.84 | 221.53
2017-05-03 09:00 | 230.37 | 219.72
2017-05-03 09:30 | 228.54 | 217.79
2017-05-03 10:00 | 226.93 | 215.79
2017-05-03 10:30 | 228.47 | 217.22
2017-05-03 11:00 | 227.89 | 216.75
2017-05-03 11:30 | 228.2 | 217.31
2017-05-03 12:00 | 228.99 | 218.04
2017-05-03 12:30 | 229.51 | 218.51
2017-05-03 13:00 | 229.97 | 219.05
2017-05-03 13:30 | 230.43 | 219.6
2017-05-03 14:00 | 231.44 | 220.86
2017-05-03 14:30 | 231.87 | 221.44
2017-05-03 15:00 | 232.18 | 221.75
2017-05-03 15:30 | 232.11 | 221.66
2017-05-03 16:00 | 232.81 | 222.45
2017-05-03 16:30 | 233.1 | 222.84
2017-05-03 17:00 | 233.96 | 223.71
2017-05-03 17:30 | 233.46 | 222.9
2017-05-03 18:00 | 237.67 | 227.43
2017-05-03 18:30 | 240.47 | 230.27
2017-05-03 19:00 | 240.35 | 230.03
2017-05-03 19:30 | 238.81 | 228.2
2017-05-03 20:00 | 237.33 | 226.47
2017-05-03 20:30 | 236.43 | 225.5
2017-05-03 21:00 | 234.71 | 223.8
2017-05-03 21:30 | 232.81 | 222.73
2017-05-03 22:00 | 231.26 | 221.18
2017-05-03 22:30 | 228.95 | 218.84
2017-05-03 23:00 | 227.06 | 216.61
2017-05-03 23:30 | 226.11 | 215.52
2017-05-04 | 225.41 | 214.78
2017-05-04 00:30 | 225.06 | 214.59
2017-05-04 01:00 | 223.92 | 213.97
2017-05-04 01:30 | 222.39 | 213.27
2017-05-04 02:00 | 221.56 | 212.92
2017-05-04 02:30 | 221.48 | 212.61
2017-05-04 03:00 | 221.2 | 212.12
2017-05-04 03:30 | 222.32 | 212.3
2017-05-04 04:00 | 222.6 | 212.71
2017-05-04 04:30 | 223.56 | 213.27
2017-05-04 05:00 | 224.16 | 213.92
2017-05-04 05:30 | 225.42 | 215.34
2017-05-04 06:00 | 227.79 | 217.62
2017-05-04 06:30 | 230.29 | 220.29
2017-05-04 07:00 | 233.51 | 222.71
2017-05-04 07:30 | 236.37 | 225.32
2017-05-04 08:00 | 237.34 | 225.48
2017-05-04 08:30 | 232.46 | 220.68
2017-05-04 09:00 | 217.84 | 206.18
2017-05-04 09:30 | 216.32 | 204.43
2017-05-04 10:00 | 215.85 | 203.63
2017-05-04 10:30 | 214.34 | 202.12
2017-05-04 11:00 | 212.97 | 200.82
2017-05-04 11:30 | 212.41 | 200.29
2017-05-04 12:00 | 212.59 | 200.41
2017-05-04 12:30 | 217.64 | 205.37
2017-05-04 13:00 | 222.11 | 209.62
2017-05-04 13:30 | 227.68 | 214.97
2017-05-04 14:00 | 229.98 | 217.49
2017-05-04 14:30 | 229.73 | 217.48
2017-05-04 15:00 | 230.58 | 218.23
2017-05-04 15:30 | 230.34 | 217.88
2017-05-04 16:00 | 230.54 | 218.26
2017-05-04 16:30 | 230.21 | 217.74
2017-05-04 17:00 | 231.64 | 219.06
2017-05-04 17:30 | 232.75 | 220
2017-05-04 18:00 | 235.81 | 223.43
2017-05-04 18:30 | 239.42 | 226.82
2017-05-04 19:00 | 239.9 | 227.04
2017-05-04 19:30 | 238.88 | 225.65
2017-05-04 20:00 | 236.86 | 223.55
2017-05-04 20:30 | 235.43 | 222.21
2017-05-04 21:00 | 233.53 | 219.87
2017-05-04 21:30 | 232.68 | 219.74
2017-05-04 22:00 | 230.33 | 218.1
2017-05-04 22:30 | 228.78 | 216.25
2017-05-04 23:00 | 228.51 | 215.83
2017-05-04 23:30 | 228.18 | 215.58
2017-05-05 | 225.92 | 213.2
2017-05-05 00:30 | 225.65 | 212.92
2017-05-05 01:00 | 224.32 | 212.37
2017-05-05 01:30 | 223.86 | 211.84
2017-05-05 02:00 | 223.3 | 211.31
2017-05-05 02:30 | 223.11 | 211.07
2017-05-05 03:00 | 222.1 | 210.04
2017-05-05 03:30 | 221.77 | 209.62
2017-05-05 04:00 | 221.37 | 209.3
2017-05-05 04:30 | 221.91 | 210.03
2017-05-05 05:00 | 223.13 | 211.17
2017-05-05 05:30 | 224.25 | 212.79
2017-05-05 06:00 | 226.38 | 214.93
2017-05-05 06:30 | 228.46 | 217.51
2017-05-05 07:00 | 231.22 | 220.25
2017-05-05 07:30 | 233 | 221.52
2017-05-05 08:00 | 231.88 | 219.83
2017-05-05 08:30 | 229.01 | 216.6
2017-05-05 09:00 | 226.28 | 213.39
2017-05-05 09:30 | 225.35 | 212.46
2017-05-05 10:00 | 227.97 | 215.28
2017-05-05 10:30 | 228.39 | 215.72
2017-05-05 11:00 | 234.27 | 222.09
2017-05-05 11:30 | 237.92 | 226.28
2017-05-05 12:00 | 238.07 | 226.22
2017-05-05 12:30 | 237.69 | 225.44
2017-05-05 13:00 | 236.78 | 223.79
2017-05-05 13:30 | 235.6 | 222.32
2017-05-05 14:00 | 233.74 | 220.02
2017-05-05 14:30 | 233.37 | 219.59
2017-05-05 15:00 | 235.88 | 222.18
2017-05-05 15:30 | 232.79 | 219.25
2017-05-05 16:00 | 237.14 | 223.94
2017-05-05 16:30 | 238.02 | 224.94
2017-05-05 17:00 | 237.95 | 225
2017-05-05 17:30 | 237.88 | 225.11
2017-05-05 18:00 | 240.26 | 227.8
2017-05-05 18:30 | 242.24 | 229.9
2017-05-05 19:00 | 243.45 | 230.93
2017-05-05 19:30 | 242.77 | 229.79
2017-05-05 20:00 | 241.02 | 228
2017-05-05 20:30 | 239.74 | 226.46
2017-05-05 21:00 | 238.86 | 225.4
2017-05-05 21:30 | 237.88 | 225.21
2017-05-05 22:00 | 236.91 | 224.64
2017-05-05 22:30 | 236.12 | 223.39
2017-05-05 23:00 | 233.93 | 221.27
2017-05-05 23:30 | 232.99 | 220.67
2017-05-06 | 230.64 | 218.66
2017-05-06 00:30 | 229.43 | 218.21
2017-05-06 01:00 | 222.36 | 212.46
2017-05-06 01:30 | 218.05 | 208.55
2017-05-06 02:00 | 217.32 | 207.92
2017-05-06 02:30 | 217.46 | 207.98
2017-05-06 03:00 | 218.34 | 208.93
2017-05-06 03:30 | 218.41 | 208.85
2017-05-06 04:00 | 218.23 | 208.76
2017-05-06 04:30 | 218.55 | 208.88
2017-05-06 05:00 | 219.46 | 209.81
2017-05-06 05:30 | 219.85 | 210.35
2017-05-06 06:00 | 220.25 | 210.62
2017-05-06 06:30 | 222.39 | 212.81
2017-05-06 07:00 | 223.52 | 213.93
2017-05-06 07:30 | 222.99 | 214.03
2017-05-06 08:00 | 222.63 | 213.35
2017-05-06 08:30 | 221.11 | 211.72
2017-05-06 09:00 | 219.97 | 210.36
2017-05-06 09:30 | 218.98 | 209.05
2017-05-06 10:00 | 220.41 | 210.58
2017-05-06 10:30 | 219.71 | 209.74
2017-05-06 11:00 | 219.55 | 209.3
2017-05-06 11:30 | 220 | 209.96
2017-05-06 12:00 | 219.74 | 209.7
2017-05-06 12:30 | 219.38 | 209.36
2017-05-06 13:00 | 218.86 | 209.15
2017-05-06 13:30 | 219.46 | 209.74
2017-05-06 14:00 | 219.59 | 209.74
2017-05-06 14:30 | 219.78 | 210.06
2017-05-06 15:00 | 220.54 | 210.52
2017-05-06 15:30 | 221.9 | 211.77
2017-05-06 16:00 | 225 | 215.22
2017-05-06 16:30 | 226.67 | 217.23
2017-05-06 17:00 | 228.6 | 218.91
2017-05-06 17:30 | 230.18 | 220.65
2017-05-06 18:00 | 232.78 | 223.36
2017-05-06 18:30 | 235.16 | 225.76
2017-05-06 19:00 | 235.34 | 225.85
2017-05-06 19:30 | 233.17 | 223.31
2017-05-06 20:00 | 231.43 | 221.5
2017-05-06 20:30 | 231.1 | 221.1
2017-05-06 21:00 | 230.73 | 220.53
2017-05-06 21:30 | 230.97 | 221.22
2017-05-06 22:00 | 229.45 | 219.64
2017-05-06 22:30 | 227.27 | 217.55
2017-05-06 23:00 | 225.23 | 215.34
2017-05-06 23:30 | 223.89 | 214.29
2017-05-07 | 221.77 | 212.42
2017-05-07 00:30 | 221.08 | 212.73
2017-05-07 01:00 | 220.61 | 212.48
2017-05-07 01:30 | 220.19 | 211.91
2017-05-07 02:00 | 220.64 | 211.57
2017-05-07 02:30 | 221.12 | 211.98
2017-05-07 03:00 | 220.88 | 212.13
2017-05-07 03:30 | 221.11 | 212.82
2017-05-07 04:00 | 220.83 | 212.33
2017-05-07 04:30 | 220.8 | 212.64
2017-05-07 05:00 | 221.01 | 212.87
2017-05-07 05:30 | 221.21 | 212.94
2017-05-07 06:00 | 223.19 | 215.01
2017-05-07 06:30 | 223.92 | 215.77
2017-05-07 07:00 | 224.87 | 216.82
2017-05-07 07:30 | 221.76 | 214.18
2017-05-07 08:00 | 220.9 | 213.2
2017-05-07 08:30 | 219.45 | 211.69
2017-05-07 09:00 | 217.91 | 210.03
2017-05-07 09:30 | 216.14 | 208.1
2017-05-07 10:00 | 218.33 | 209.61
2017-05-07 10:30 | 218.31 | 209.39
2017-05-07 11:00 | 217.94 | 208.79
2017-05-07 11:30 | 217.32 | 208.03
2017-05-07 12:00 | 216.7 | 207.61
2017-05-07 12:30 | 216.6 | 207.63
2017-05-07 13:00 | 217.7 | 208.75
2017-05-07 13:30 | 217.39 | 208.46
2017-05-07 14:00 | 218.35 | 209.26
2017-05-07 14:30 | 219.2 | 209.71
2017-05-07 15:00 | 220.2 | 210.59
2017-05-07 15:30 | 221.95 | 212.59
2017-05-07 16:00 | 222.38 | 212.65
2017-05-07 16:30 | 224.97 | 213.66
2017-05-07 17:00 | 226.65 | 215.67
2017-05-07 17:30 | 228.7 | 217.87
2017-05-07 18:00 | 232.43 | 221.05
2017-05-07 18:30 | 234.43 | 222.59
2017-05-07 19:00 | 235.69 | 223.73
2017-05-07 19:30 | 234.61 | 222.39
2017-05-07 20:00 | 233.66 | 221.03
2017-05-07 20:30 | 232.29 | 219.62
2017-05-07 21:00 | 232.05 | 219.09
2017-05-07 21:30 | 231.32 | 218.71
2017-05-07 22:00 | 230.17 | 217.8
2017-05-07 22:30 | 229.62 | 216.78
2017-05-07 23:00 | 227.9 | 215.17
2017-05-07 23:30 | 227.29 | 214.77
2017-05-08 | 226.1 | 214.04
2017-05-08 00:30 | 223.79 | 211.95
2017-05-08 01:00 | 222.36 | 210.95
2017-05-08 01:30 | 220.94 | 209.71
2017-05-08 02:00 | 220 | 208.83
2017-05-08 02:30 | 219.96 | 208.89
2017-05-08 03:00 | 220.64 | 209.62
2017-05-08 03:30 | 220.78 | 209.66
2017-05-08 04:00 | 220.84 | 209.53
2017-05-08 04:30 | 222.03 | 210.9
2017-05-08 05:00 | 222.81 | 211.61
2017-05-08 05:30 | 224.45 | 213.56
2017-05-08 06:00 | 227.02 | 216.18
2017-05-08 06:30 | 231.77 | 219.82
2017-05-08 07:00 | 235.78 | 223.09
2017-05-08 07:30 | 236.54 | 223.89
2017-05-08 08:00 | 234.72 | 222.3
2017-05-08 08:30 | 232.51 | 219.89
2017-05-08 09:00 | 231.33 | 218.34
2017-05-08 09:30 | 229.63 | 215.84
2017-05-08 10:00 | 231.12 | 217.4
2017-05-08 10:30 | 231.49 | 217.6
2017-05-08 11:00 | 228.74 | 214.93
2017-05-08 11:30 | 227.47 | 213.8
2017-05-08 12:00 | 226.44 | 212.67
2017-05-08 12:30 | 227.11 | 213.35
2017-05-08 13:00 | 228.26 | 214.33
2017-05-08 13:30 | 230.31 | 216.41
2017-05-08 14:00 | 230.79 | 217.12
2017-05-08 14:30 | 231.13 | 217.61
2017-05-08 15:00 | 230.84 | 216.8
2017-05-08 15:30 | 230.42 | 216.2
2017-05-08 16:00 | 232.49 | 218.39
2017-05-08 16:30 | 233.76 | 219.52
2017-05-08 17:00 | 234.85 | 220.81
2017-05-08 17:30 | 236.6 | 222.7
2017-05-08 18:00 | 239.45 | 225.83
2017-05-08 18:30 | 242.47 | 229.05
2017-05-08 19:00 | 242.88 | 229.37
2017-05-08 19:30 | 241.5 | 227.55
2017-05-08 20:00 | 240.04 | 225.91
2017-05-08 20:30 | 238.46 | 224.71
2017-05-08 21:00 | 235.01 | 223.11
2017-05-08 21:30 | 234.7 | 223.32
2017-05-08 22:00 | 232.55 | 221.5
2017-05-08 22:30 | 229.89 | 219.4
2017-05-08 23:00 | 227.57 | 217.57
2017-05-08 23:30 | 227.48 | 217.17
2017-05-09 | 225.1 | 215
2017-05-09 00:30 | 224.09 | 214.14
2017-05-09 01:00 | 222.96 | 213.07
2017-05-09 01:30 | 222.58 | 212.54
2017-05-09 02:00 | 222.41 | 212.18
2017-05-09 02:30 | 221.81 | 211.52
2017-05-09 03:00 | 221.89 | 211.73
2017-05-09 03:30 | 221.92 | 211.78
2017-05-09 04:00 | 222.33 | 212.01
2017-05-09 04:30 | 223.24 | 212.88
2017-05-09 05:00 | 223.73 | 213.34
2017-05-09 05:30 | 224.9 | 214.95
2017-05-09 06:00 | 227.46 | 218.06
2017-05-09 06:30 | 230.74 | 221.31
2017-05-09 07:00 | 232.76 | 223.25
2017-05-09 07:30 | 235.81 | 226.54
2017-05-09 08:00 | 236.26 | 226.96
2017-05-09 08:30 | 233.64 | 224.01
2017-05-09 09:00 | 231.51 | 221.29
2017-05-09 09:30 | 229.56 | 218.95
2017-05-09 10:00 | 229.08 | 218.51
2017-05-09 10:30 | 227.93 | 217.33
2017-05-09 11:00 | 227.75 | 217.19
2017-05-09 11:30 | 227.07 | 216.53
2017-05-09 12:00 | 228.06 | 217.17
2017-05-09 12:30 | 227.68 | 216.73
2017-05-09 13:00 | 228.15 | 216.87
2017-05-09 13:30 | 227.83 | 216.41
2017-05-09 14:00 | 227.68 | 216.57
2017-05-09 14:30 | 226.71 | 215.81
2017-05-09 15:00 | 227.27 | 216.41
2017-05-09 15:30 | 226.99 | 215.94
2017-05-09 16:00 | 227.89 | 216.42
2017-05-09 16:30 | 229.11 | 217.53
2017-05-09 17:00 | 229.73 | 218.12
2017-05-09 17:30 | 230.94 | 219.59
2017-05-09 18:00 | 233.8 | 222.16
2017-05-09 18:30 | 238.37 | 226.79
2017-05-09 19:00 | 238.8 | 227.28
2017-05-09 19:30 | 237.59 | 225.68
2017-05-09 20:00 | 236.27 | 223.97
2017-05-09 20:30 | 235.71 | 223.21
2017-05-09 21:00 | 234.43 | 221.57
2017-05-09 21:30 | 232.24 | 220.07
2017-05-09 22:00 | 229.85 | 218.3
2017-05-09 22:30 | 227.23 | 215.86
2017-05-09 23:00 | 225.92 | 214.31
2017-05-09 23:30 | 224.65 | 213.08
2017-05-10 | 222.85 | 211.33
2017-05-10 00:30 | 220.68 | 209.24
2017-05-10 01:00 | 220.15 | 208.97
2017-05-10 01:30 | 219.02 | 207.97
2017-05-10 02:00 | 218.37 | 207.74
2017-05-10 02:30 | 217.89 | 207.31
2017-05-10 03:00 | 218.58 | 208.07
2017-05-10 03:30 | 218.88 | 208.33
2017-05-10 04:00 | 218.91 | 208.43
2017-05-10 04:30 | 218.86 | 208.22
2017-05-10 05:00 | 219.53 | 208.95
2017-05-10 05:30 | 221.03 | 210.78
2017-05-10 06:00 | 224.07 | 213.77
2017-05-10 06:30 | 227.85 | 217.6
2017-05-10 07:00 | 231.35 | 220.88
2017-05-10 07:30 | 233.48 | 223.4
2017-05-10 08:00 | 232.6 | 222.41
2017-05-10 08:30 | 229.11 | 218.87
2017-05-10 09:00 | 225.99 | 215.68
2017-05-10 09:30 | 226.38 | 215.71
2017-05-10 10:00 | 226.12 | 215.41
2017-05-10 10:30 | 226.08 | 215.31
2017-05-10 11:00 | 224.59 | 213.84
2017-05-10 11:30 | 225.17 | 214.42
2017-05-10 12:00 | 224.35 | 213.62
2017-05-10 12:30 | 223.72 | 212.59
2017-05-10 13:00 | 224.88 | 213.73
2017-05-10 13:30 | 225.55 | 214.42
2017-05-10 14:00 | 225.98 | 215.03
2017-05-10 14:30 | 226.72 | 215.88
2017-05-10 15:00 | 228.32 | 217.21
2017-05-10 15:30 | 228.87 | 217.93
2017-05-10 16:00 | 229.41 | 218.47
2017-05-10 16:30 | 229.66 | 218.68
2017-05-10 17:00 | 230.62 | 219.8
2017-05-10 17:30 | 232.1 | 221.35
2017-05-10 18:00 | 235.04 | 224.73
2017-05-10 18:30 | 237.79 | 227.62
2017-05-10 19:00 | 238.64 | 228.39
2017-05-10 19:30 | 238.23 | 227.62
2017-05-10 20:00 | 237.42 | 226.49
2017-05-10 20:30 | 236.84 | 225.77
2017-05-10 21:00 | 234.89 | 223.48
2017-05-10 21:30 | 231.93 | 221.43
2017-05-10 22:00 | 230.47 | 219.92
2017-05-10 22:30 | 228.43 | 217.7
2017-05-10 23:00 | 226.94 | 215.83
2017-05-10 23:30 | 225.77 | 215.27
2017-05-11 | 224.58 | 214.07
2017-05-11 00:30 | 224.21 | 213.75
2017-05-11 01:00 | 222.71 | 212.79
2017-05-11 01:30 | 222.12 | 212.33
2017-05-11 02:00 | 221.62 | 211.91
2017-05-11 02:30 | 222.05 | 212.34
2017-05-11 03:00 | 222.68 | 213.05
2017-05-11 03:30 | 223.02 | 213.4
2017-05-11 04:00 | 223.6 | 214
2017-05-11 04:30 | 224.41 | 214.63
2017-05-11 05:00 | 226.21 | 216.49
2017-05-11 05:30 | 227.7 | 218.07
2017-05-11 06:00 | 230.99 | 221.18
2017-05-11 06:30 | 234.48 | 224.46
2017-05-11 07:00 | 237.33 | 227.48
2017-05-11 07:30 | 238.64 | 229.02
2017-05-11 08:00 | 237.87 | 227.38
2017-05-11 08:30 | 234.4 | 223.71
2017-05-11 09:00 | 221.42 | 210.17
2017-05-11 09:30 | 170.86 | 158.46
2017-05-11 10:00 | 167.25 | 154.63
2017-05-11 10:30 | 166.45 | 153.65
2017-05-11 11:00 | 164.63 | 151.85
2017-05-11 11:30 | 164.24 | 151.41
2017-05-11 12:00 | 164.25 | 151.66
2017-05-11 12:30 | 163.84 | 150.87
2017-05-11 13:00 | 165.02 | 151.52
2017-05-11 13:30 | 165.9 | 152.33
2017-05-11 14:00 | 164.71 | 152.16
2017-05-11 14:30 | 199.89 | 188.53
2017-05-11 15:00 | 227.14 | 215.56
2017-05-11 15:30 | 227.88 | 215.87
2017-05-11 16:00 | 228.51 | 216.48
2017-05-11 16:30 | 230.95 | 218.81
2017-05-11 17:00 | 232.3 | 219.66
2017-05-11 17:30 | 233.45 | 221.16
2017-05-11 18:00 | 236.83 | 224.97
2017-05-11 18:30 | 240.77 | 228.91
2017-05-11 19:00 | 241.92 | 229.94
2017-05-11 19:30 | 240.63 | 228.45
2017-05-11 20:00 | 239.13 | 226.57
2017-05-11 20:30 | 238.52 | 225.87
2017-05-11 21:00 | 238.42 | 225.68
2017-05-11 21:30 | 234.04 | 222.03
2017-05-11 22:00 | 232.19 | 220.31
2017-05-11 22:30 | 230.71 | 218.62
2017-05-11 23:00 | 228.39 | 215.61
2017-05-11 23:30 | 225.98 | 213.86
2017-05-12 | 225.45 | 213.34
2017-05-12 00:30 | 224.08 | 212.99
2017-05-12 01:00 | 222.42 | 211.85
2017-05-12 01:30 | 221.95 | 211.28
2017-05-12 02:00 | 221.56 | 211.06
2017-05-12 02:30 | 221.82 | 211.35
2017-05-12 03:00 | 221.9 | 211.52
2017-05-12 03:30 | 221.82 | 211.66
2017-05-12 04:00 | 221.84 | 211.84
2017-05-12 04:30 | 222.85 | 212.92
2017-05-12 05:00 | 224.53 | 214.46
2017-05-12 05:30 | 225.85 | 216.08
2017-05-12 06:00 | 228.65 | 218.39
2017-05-12 06:30 | 231.9 | 221.44
2017-05-12 07:00 | 233.32 | 223
2017-05-12 07:30 | 234.4 | 223.83
2017-05-12 08:00 | 234.58 | 224.1
2017-05-12 08:30 | 232.86 | 222.02
2017-05-12 09:00 | 230.67 | 219.43
2017-05-12 09:30 | 227.84 | 216.35
2017-05-12 10:00 | 227.6 | 215.83
2017-05-12 10:30 | 226.86 | 214.83
2017-05-12 11:00 | 225.21 | 212.91
2017-05-12 11:30 | 224.51 | 212.11
2017-05-12 12:00 | 222.91 | 210.23
2017-05-12 12:30 | 223.52 | 210.81
2017-05-12 13:00 | 224.03 | 211.04
2017-05-12 13:30 | 222.93 | 210.04
2017-05-12 14:00 | 222.68 | 209.94
2017-05-12 14:30 | 222.95 | 210.25
2017-05-12 15:00 | 224.28 | 211.19
2017-05-12 15:30 | 224.99 | 211.77
2017-05-12 16:00 | 226.23 | 212.83
2017-05-12 16:30 | 225.94 | 212.62
2017-05-12 17:00 | 225.43 | 212.42
2017-05-12 17:30 | 228.29 | 215.78
2017-05-12 18:00 | 230.9 | 218.85
2017-05-12 18:30 | 233.63 | 221.73
2017-05-12 19:00 | 234.33 | 222.47
2017-05-12 19:30 | 233.68 | 221.66
2017-05-12 20:00 | 232.87 | 220.83
2017-05-12 20:30 | 232.17 | 220.17
2017-05-12 21:00 | 231.52 | 219.26
2017-05-12 21:30 | 230.5 | 218.77
2017-05-12 22:00 | 229.25 | 217.66
2017-05-12 22:30 | 228.09 | 216.59
2017-05-12 23:00 | 227.02 | 215.26
2017-05-12 23:30 | 226.39 | 214.38
2017-05-13 | 224.41 | 212.21
2017-05-13 00:30 | 222.01 | 211.03
2017-05-13 01:00 | 220.5 | 209.65
2017-05-13 01:30 | 218.07 | 207.64
2017-05-13 02:00 | 218.04 | 208.07
2017-05-13 02:30 | 218.09 | 208.23
2017-05-13 03:00 | 219.1 | 209.14
2017-05-13 03:30 | 219.35 | 209.67
2017-05-13 04:00 | 219.28 | 209.63
2017-05-13 04:30 | 219.86 | 210.33
2017-05-13 05:00 | 221.41 | 211.86
2017-05-13 05:30 | 222.18 | 212.85
2017-05-13 06:00 | 223.66 | 214.36
2017-05-13 06:30 | 225.23 | 216.17
2017-05-13 07:00 | 226.59 | 217.71
2017-05-13 07:30 | 227.02 | 218.19
2017-05-13 08:00 | 226.93 | 218.15
2017-05-13 08:30 | 227.06 | 217.87
2017-05-13 09:00 | 226.04 | 216.79
2017-05-13 09:30 | 223.52 | 214.37
2017-05-13 10:00 | 224.21 | 214.99
2017-05-13 10:30 | 223.31 | 214.11
2017-05-13 11:00 | 222.56 | 213.08
2017-05-13 11:30 | 220.21 | 210.61
2017-05-13 12:00 | 220.4 | 210.61
2017-05-13 12:30 | 219.76 | 209.81
2017-05-13 13:00 | 220.33 | 210.36
2017-05-13 13:30 | 221.4 | 211.5
2017-05-13 14:00 | 222.92 | 212.97
2017-05-13 14:30 | 223.35 | 213.4
2017-05-13 15:00 | 223.88 | 214.2
2017-05-13 15:30 | 224.06 | 214.21
2017-05-13 16:00 | 224.37 | 214.41
2017-05-13 16:30 | 225.83 | 216.12
2017-05-13 17:00 | 227.15 | 217.53
2017-05-13 17:30 | 229.78 | 220.19
2017-05-13 18:00 | 232.17 | 222.83
2017-05-13 18:30 | 233.47 | 224.08
2017-05-13 19:00 | 232.28 | 222.64
2017-05-13 19:30 | 231.57 | 221.8
2017-05-13 20:00 | 230.56 | 220.61
2017-05-13 20:30 | 229.85 | 219.77
2017-05-13 21:00 | 229.66 | 219.39
2017-05-13 21:30 | 228.74 | 218.67
2017-05-13 22:00 | 228.72 | 218.23
2017-05-13 22:30 | 228.11 | 217.47
2017-05-13 23:00 | 226.58 | 215.71
2017-05-13 23:30 | 225.61 | 214.81
2017-05-14 | 223.72 | 213.63
2017-05-14 00:30 | 222.41 | 212.7
2017-05-14 01:00 | 220.51 | 211.3
2017-05-14 01:30 | 219.45 | 210.57
2017-05-14 02:00 | 217.68 | 209.75
2017-05-14 02:30 | 217.24 | 209.36
2017-05-14 03:00 | 218.22 | 210.4
2017-05-14 03:30 | 218.53 | 210.72
2017-05-14 04:00 | 218.53 | 211
2017-05-14 04:30 | 219.12 | 211.42
2017-05-14 05:00 | 219.27 | 211.48
2017-05-14 05:30 | 219.45 | 211.59
2017-05-14 06:00 | 220.39 | 212.43
2017-05-14 06:30 | 221.55 | 213.75
2017-05-14 07:00 | 222.53 | 214.71
2017-05-14 07:30 | 222.88 | 215.2
2017-05-14 08:00 | 222.78 | 214.37
2017-05-14 08:30 | 222.94 | 214.36
2017-05-14 09:00 | 222.46 | 213.89
2017-05-14 09:30 | 220.87 | 212.24
2017-05-14 10:00 | 221.5 | 212.77
2017-05-14 10:30 | 223.5 | 213.79
2017-05-14 11:00 | 223.25 | 213.27
2017-05-14 11:30 | 220.25 | 210
2017-05-14 12:00 | 222.44 | 212.41
2017-05-14 12:30 | 223.72 | 213.77
2017-05-14 13:00 | 223.61 | 213.61
2017-05-14 13:30 | 223.02 | 213.04
2017-05-14 14:00 | 221.36 | 211.16
2017-05-14 14:30 | 221.24 | 210.97
2017-05-14 15:00 | 221.8 | 211.12
2017-05-14 15:30 | 221.99 | 211.26
2017-05-14 16:00 | 223.02 | 212.39
2017-05-14 16:30 | 223.84 | 212.9
2017-05-14 17:00 | 225.21 | 213.51
2017-05-14 17:30 | 228.2 | 216.82
2017-05-14 18:00 | 231.26 | 220.29
2017-05-14 18:30 | 232.1 | 221.08
2017-05-14 19:00 | 231.94 | 220.43
2017-05-14 19:30 | 230.27 | 218.72
2017-05-14 20:00 | 228.29 | 216.8
2017-05-14 20:30 | 228.01 | 216.71
2017-05-14 21:00 | 227.32 | 215.75
2017-05-14 21:30 | 226.32 | 214.82
2017-05-14 22:00 | 224.37 | 213.08
2017-05-14 22:30 | 222.74 | 211.92
2017-05-14 23:00 | 221.46 | 210.68
2017-05-14 23:30 | 220.21 | 209.38
2017-05-15 | 219.3 | 208.75
2017-05-15 00:30 | 218.16 | 208.25
2017-05-15 01:00 | 217.23 | 207.53
2017-05-15 01:30 | 215.2 | 206.04
2017-05-15 02:00 | 214.68 | 205.89
2017-05-15 02:30 | 215.01 | 206.17
2017-05-15 03:00 | 215.15 | 206.3
2017-05-15 03:30 | 215.66 | 206.66
2017-05-15 04:00 | 215.94 | 206.87
2017-05-15 04:30 | 217.91 | 208.85
2017-05-15 05:00 | 218.32 | 209.27
2017-05-15 05:30 | 220.41 | 211.66
2017-05-15 06:00 | 223.71 | 214.61
2017-05-15 06:30 | 227.62 | 218.43
2017-05-15 07:00 | 231.3 | 222.27
2017-05-15 07:30 | 235.82 | 224.85
2017-05-15 08:00 | 235.45 | 222.95
2017-05-15 08:30 | 230.6 | 219.46
2017-05-15 09:00 | 228.33 | 217.27
2017-05-15 09:30 | 225.07 | 213.55
2017-05-15 10:00 | 224.28 | 212.84
2017-05-15 10:30 | 222.99 | 211.38
2017-05-15 11:00 | 223.59 | 211.95
2017-05-15 11:30 | 223.49 | 211.93
2017-05-15 12:00 | 223 | 211.36
2017-05-15 12:30 | 222.65 | 210.89
2017-05-15 13:00 | 223.29 | 211.39
2017-05-15 13:30 | 223.02 | 211.18
2017-05-15 14:00 | 223.79 | 212.03
2017-05-15 14:30 | 224.29 | 212.63
2017-05-15 15:00 | 224.23 | 212.55
2017-05-15 15:30 | 225.08 | 213.4
2017-05-15 16:00 | 225.56 | 213.9
2017-05-15 16:30 | 227.34 | 215.7
2017-05-15 17:00 | 229.43 | 217.24
2017-05-15 17:30 | 230.69 | 218.11
2017-05-15 18:00 | 235.14 | 223.3
2017-05-15 18:30 | 238.07 | 226.62
2017-05-15 19:00 | 238.1 | 226.76
2017-05-15 19:30 | 236.1 | 224.21
2017-05-15 20:00 | 234.7 | 222.4
2017-05-15 20:30 | 233.95 | 221.58
2017-05-15 21:00 | 232.91 | 220.14
2017-05-15 21:30 | 231.05 | 218.74
2017-05-15 22:00 | 227.1 | 216.79
2017-05-15 22:30 | 224.58 | 214.92
2017-05-15 23:00 | 222.12 | 212.09
2017-05-15 23:30 | 221.16 | 210.91
2017-05-16 | 220.93 | 211.23
2017-05-16 00:30 | 219.18 | 210.03
2017-05-16 01:00 | 216.81 | 208.98
2017-05-16 01:30 | 217.35 | 208.13
2017-05-16 02:00 | 218.11 | 208.26
2017-05-16 02:30 | 217.97 | 208.08
2017-05-16 03:00 | 218.12 | 208.14
2017-05-16 03:30 | 218.18 | 208.18
2017-05-16 04:00 | 218.87 | 208.75
2017-05-16 04:30 | 219.53 | 209.7
2017-05-16 05:00 | 220.57 | 210.94
2017-05-16 05:30 | 222.39 | 212.71
2017-05-16 06:00 | 226.89 | 216.01
2017-05-16 06:30 | 231.08 | 219.43
2017-05-16 07:00 | 235.04 | 222.56
2017-05-16 07:30 | 236.19 | 224.71
2017-05-16 08:00 | 235.73 | 224.44
2017-05-16 08:30 | 235.02 | 223.06
2017-05-16 09:00 | 229.19 | 218.92
2017-05-16 09:30 | 224.83 | 214.2
2017-05-16 10:00 | 226.74 | 215.81
2017-05-16 10:30 | 226.14 | 214.81
2017-05-16 11:00 | 225.47 | 214.26
2017-05-16 11:30 | 224.48 | 212.89
2017-05-16 12:00 | 226.71 | 215.33
2017-05-16 12:30 | 225.51 | 214.17
2017-05-16 13:00 | 225.26 | 213.27
2017-05-16 13:30 | 226.07 | 214.02
2017-05-16 14:00 | 226.95 | 215.1
2017-05-16 14:30 | 226.08 | 214.27
2017-05-16 15:00 | 225.4 | 213.54
2017-05-16 15:30 | 224.95 | 213.45
2017-05-16 16:00 | 224.89 | 214.08
2017-05-16 16:30 | 226.03 | 215.35
2017-05-16 17:00 | 226.81 | 216.33
2017-05-16 17:30 | 228.7 | 218.72
2017-05-16 18:00 | 235.89 | 226.38
2017-05-16 18:30 | 239.63 | 230.01
2017-05-16 19:00 | 240.24 | 230.66
2017-05-16 19:30 | 238.59 | 228.77
2017-05-16 20:00 | 237.36 | 227.55
2017-05-16 20:30 | 235.69 | 225.74
2017-05-16 21:00 | 233.15 | 223.1
2017-05-16 21:30 | 229.26 | 219.86
2017-05-16 22:00 | 227.04 | 218.84
2017-05-16 22:30 | 225 | 217.36
2017-05-16 23:00 | 223.25 | 215.61
2017-05-16 23:30 | 223.09 | 214.67
2017-05-17 | 222.36 | 213.31
2017-05-17 00:30 | 221.9 | 212.89
2017-05-17 01:00 | 221.77 | 211.8
2017-05-17 01:30 | 221.2 | 211.3
2017-05-17 02:00 | 220.58 | 210.73
2017-05-17 02:30 | 220.45 | 210.74
2017-05-17 03:00 | 220.97 | 211.26
2017-05-17 03:30 | 221.16 | 211.55
2017-05-17 04:00 | 221.35 | 211.87
2017-05-17 04:30 | 221.8 | 212.54
2017-05-17 05:00 | 223.06 | 213.6
2017-05-17 05:30 | 224.58 | 215.47
2017-05-17 06:00 | 227.47 | 217.68
2017-05-17 06:30 | 231.09 | 221.48
2017-05-17 07:00 | 234.49 | 224.6
2017-05-17 07:30 | 237.63 | 226.75
2017-05-17 08:00 | 236.29 | 226.53
2017-05-17 08:30 | 233.63 | 223.62
2017-05-17 09:00 | 231.37 | 221.06
2017-05-17 09:30 | 226.96 | 216.36
2017-05-17 10:00 | 225.31 | 214.74
2017-05-17 10:30 | 224.41 | 213.39
2017-05-17 11:00 | 224.51 | 213.22
2017-05-17 11:30 | 224.27 | 213.1
2017-05-17 12:00 | 224.49 | 213.32
2017-05-17 12:30 | 223.76 | 212.38
2017-05-17 13:00 | 224.47 | 212.79
2017-05-17 13:30 | 225.1 | 213.25
2017-05-17 14:00 | 225.19 | 213.86
2017-05-17 14:30 | 225.89 | 214.84
2017-05-17 15:00 | 226.52 | 215.55
2017-05-17 15:30 | 226.93 | 216.12
2017-05-17 16:00 | 227.84 | 217.18
2017-05-17 16:30 | 227.84 | 216.86
2017-05-17 17:00 | 228.86 | 218.27
2017-05-17 17:30 | 230.43 | 219.99
2017-05-17 18:00 | 233.23 | 223.13
2017-05-17 18:30 | 235.86 | 225.7
2017-05-17 19:00 | 236.53 | 225.97
2017-05-17 19:30 | 234.84 | 223.78
2017-05-17 20:00 | 233.88 | 222.76
2017-05-17 20:30 | 233.46 | 222.3
2017-05-17 21:00 | 232.17 | 220.74
2017-05-17 21:30 | 229.97 | 219.69
2017-05-17 22:00 | 228.16 | 218.2
2017-05-17 22:30 | 226.66 | 216.59
2017-05-17 23:00 | 225.07 | 214.69
2017-05-17 23:30 | 224.07 | 213.75
2017-05-18 | 222.81 | 212.58
2017-05-18 00:30 | 220.36 | 210.54
2017-05-18 01:00 | 218.99 | 209.57
2017-05-18 01:30 | 217.69 | 208.57
2017-05-18 02:00 | 217.62 | 207.71
2017-05-18 02:30 | 217.52 | 207.64
2017-05-18 03:00 | 217.39 | 207.64
2017-05-18 03:30 | 217.61 | 207.62
2017-05-18 04:00 | 217.64 | 208.29
2017-05-18 04:30 | 215.06 | 209.07
2017-05-18 05:00 | 215.02 | 209.26
2017-05-18 05:30 | 217.65 | 212.02
2017-05-18 06:00 | 221.08 | 215.17
2017-05-18 06:30 | 225.12 | 218.29
2017-05-18 07:00 | 229.52 | 220.96
2017-05-18 07:30 | 231.61 | 223.13
2017-05-18 08:00 | 230.79 | 222.38
2017-05-18 08:30 | 228.63 | 220.11
2017-05-18 09:00 | 226.67 | 217.87
2017-05-18 09:30 | 225.05 | 215.76
2017-05-18 10:00 | 223.42 | 213.28
2017-05-18 10:30 | 223.29 | 213.21
2017-05-18 11:00 | 222.88 | 213.47
2017-05-18 11:30 | 223.33 | 214.04
2017-05-18 12:00 | 224.64 | 215.44
2017-05-18 12:30 | 224.89 | 215.63
2017-05-18 13:00 | 226.01 | 216.74
2017-05-18 13:30 | 226.09 | 216.86
2017-05-18 14:00 | 225.97 | 217.11
2017-05-18 14:30 | 226.17 | 217.49
2017-05-18 15:00 | 226.1 | 217.32
2017-05-18 15:30 | 226.05 | 217.2
2017-05-18 16:00 | 226.32 | 217.66
2017-05-18 16:30 | 227.2 | 218.56
2017-05-18 17:00 | 228.85 | 219.94
2017-05-18 17:30 | 230.03 | 220.72
2017-05-18 18:00 | 233.74 | 224.59
2017-05-18 18:30 | 234.95 | 225.65
2017-05-18 19:00 | 235.32 | 226
2017-05-18 19:30 | 233.93 | 224.35
2017-05-18 20:00 | 232.26 | 222.49
2017-05-18 20:30 | 231.92 | 221.96
2017-05-18 21:00 | 231.19 | 221.11
2017-05-18 21:30 | 229.23 | 219.95
2017-05-18 22:00 | 228.25 | 218.98
2017-05-18 22:30 | 226.4 | 217.25
2017-05-18 23:00 | 224.17 | 214.95
2017-05-18 23:30 | 223.62 | 214.2
2017-05-19 | 221.16 | 212.27
2017-05-19 00:30 | 220.41 | 211.44
2017-05-19 01:00 | 217.58 | 209.1
2017-05-19 01:30 | 216.29 | 207.88
2017-05-19 02:00 | 215.7 | 207.38
2017-05-19 02:30 | 215.83 | 207.33
2017-05-19 03:00 | 216.31 | 207.75
2017-05-19 03:30 | 216.42 | 207.99
2017-05-19 04:00 | 216.2 | 208.03
2017-05-19 04:30 | 216.99 | 208.39
2017-05-19 05:00 | 217.52 | 208.99
2017-05-19 05:30 | 216.46 | 208.06
2017-05-19 06:00 | 218.18 | 209.75
2017-05-19 06:30 | 220.71 | 212.21
2017-05-19 07:00 | 223.49 | 215.1
2017-05-19 07:30 | 227.13 | 218.95
2017-05-19 08:00 | 228.44 | 219.88
2017-05-19 08:30 | 228.64 | 220.05
2017-05-19 09:00 | 228.09 | 219.51
2017-05-19 09:30 | 225.77 | 217.26
2017-05-19 10:00 | 224.78 | 216.23
2017-05-19 10:30 | 224.33 | 215.42
2017-05-19 11:00 | 224.2 | 215.18
2017-05-19 11:30 | 223.27 | 214.25
2017-05-19 12:00 | 222.3 | 213.33
2017-05-19 12:30 | 222.31 | 213.1
2017-05-19 13:00 | 222.9 | 213.4
2017-05-19 13:30 | 223.05 | 213.38
2017-05-19 14:00 | 221.17 | 211.47
2017-05-19 14:30 | 222.33 | 212.54
2017-05-19 15:00 | 222.99 | 213.15
2017-05-19 15:30 | 223.03 | 213.14
2017-05-19 16:00 | 223.27 | 213.52
2017-05-19 16:30 | 223.99 | 214.31
2017-05-19 17:00 | 224.73 | 215.07
2017-05-19 17:30 | 226.48 | 216.49
2017-05-19 18:00 | 229.04 | 219.34
2017-05-19 18:30 | 231.03 | 221.34
2017-05-19 19:00 | 230.39 | 220.69
2017-05-19 19:30 | 230.4 | 220.63
2017-05-19 20:00 | 228.93 | 218.87
2017-05-19 20:30 | 228.67 | 218.52
2017-05-19 21:00 | 227.33 | 217.36
2017-05-19 21:30 | 224.43 | 215.4
2017-05-19 22:00 | 222.88 | 214.02
2017-05-19 22:30 | 222.14 | 213.21
2017-05-19 23:00 | 221.52 | 212.53
2017-05-19 23:30 | 221.63 | 212.26
2017-05-20 | 220.36 | 211.15
2017-05-20 00:30 | 219.53 | 210.53
2017-05-20 01:00 | 218.57 | 209.77
2017-05-20 01:30 | 217.97 | 209.24
2017-05-20 02:00 | 217.01 | 208.44
2017-05-20 02:30 | 217.14 | 208.49
2017-05-20 03:00 | 216.93 | 208.28
2017-05-20 03:30 | 217.28 | 208.71
2017-05-20 04:00 | 217.21 | 208.6
2017-05-20 04:30 | 217.89 | 209.43
2017-05-20 05:00 | 218.11 | 209.74
2017-05-20 05:30 | 218.59 | 210.3
2017-05-20 06:00 | 218.62 | 210.36
2017-05-20 06:30 | 220.53 | 212.15
2017-05-20 07:00 | 221.66 | 213.47
2017-05-20 07:30 | 222.49 | 214.44
2017-05-20 08:00 | 224.16 | 216.24
2017-05-20 08:30 | 223.89 | 216.01
2017-05-20 09:00 | 223.37 | 215.48
2017-05-20 09:30 | 222.99 | 214.21
2017-05-20 10:00 | 221.2 | 212.15
2017-05-20 10:30 | 221.09 | 212.09
2017-05-20 11:00 | 220.34 | 211.42
2017-05-20 11:30 | 220.61 | 211.63
2017-05-20 12:00 | 219.92 | 210.9
2017-05-20 12:30 | 219.71 | 210.6
2017-05-20 13:00 | 219.59 | 210.32
2017-05-20 13:30 | 219.59 | 210.18
2017-05-20 14:00 | 218.96 | 209.48
2017-05-20 14:30 | 218.96 | 209.5
2017-05-20 15:00 | 219.12 | 209.7
2017-05-20 15:30 | 218.29 | 208.84
2017-05-20 16:00 | 219.34 | 210
2017-05-20 16:30 | 221.12 | 211.97
2017-05-20 17:00 | 222.63 | 213.49
2017-05-20 17:30 | 225.21 | 215.89
2017-05-20 18:00 | 228.44 | 219.11
2017-05-20 18:30 | 229.31 | 219.97
2017-05-20 19:00 | 228.95 | 219.6
2017-05-20 19:30 | 227.71 | 218.21
2017-05-20 20:00 | 226.37 | 216.61
2017-05-20 20:30 | 225.15 | 215.28
2017-05-20 21:00 | 223.91 | 214.11
2017-05-20 21:30 | 223.43 | 214.73
2017-05-20 22:00 | 222.56 | 214.11
2017-05-20 22:30 | 221.25 | 212.7
2017-05-20 23:00 | 220.3 | 211.75
2017-05-20 23:30 | 220.2 | 211.87
2017-05-21 | 219.21 | 211.17
2017-05-21 00:30 | 218.82 | 210.74
2017-05-21 01:00 | 218.12 | 209.93
2017-05-21 01:30 | 217.65 | 209.3
2017-05-21 02:00 | 217.39 | 209.01
2017-05-21 02:30 | 216.91 | 208.58
2017-05-21 03:00 | 216.53 | 208.24
2017-05-21 03:30 | 216.57 | 208.21
2017-05-21 04:00 | 216.42 | 208.11
2017-05-21 04:30 | 216.4 | 208.4
2017-05-21 05:00 | 216.71 | 209.05
2017-05-21 05:30 | 216.4 | 208.98
2017-05-21 06:00 | 218.08 | 210.92
2017-05-21 06:30 | 218.94 | 211.59
2017-05-21 07:00 | 220.43 | 212.76
2017-05-21 07:30 | 220.92 | 213.48
2017-05-21 08:00 | 220.65 | 213.27
2017-05-21 08:30 | 220.48 | 212.95
2017-05-21 09:00 | 220.05 | 212.36
2017-05-21 09:30 | 219.74 | 212.21
2017-05-21 10:00 | 208.76 | 201.26
2017-05-21 10:30 | 189.83 | 182.13
2017-05-21 11:00 | 191.84 | 183.87
2017-05-21 11:30 | 198.77 | 190.57
2017-05-21 12:00 | 198.63 | 190.05
2017-05-21 12:30 | 198.7 | 190.21
2017-05-21 13:00 | 197.47 | 188.79
2017-05-21 13:30 | 198.61 | 190.48
2017-05-21 14:00 | 197.22 | 188.97
2017-05-21 14:30 | 209.21 | 201.08
2017-05-21 15:00 | 219.22 | 210.96
2017-05-21 15:30 | 220.33 | 211.99
2017-05-21 16:00 | 221.3 | 212.95
2017-05-21 16:30 | 222.97 | 214.63
2017-05-21 17:00 | 224.68 | 215.75
2017-05-21 17:30 | 226.89 | 217.77
2017-05-21 18:00 | 231.23 | 222.1
2017-05-21 18:30 | 233.09 | 224.08
2017-05-21 19:00 | 233.04 | 223.84
2017-05-21 19:30 | 231.86 | 222.34
2017-05-21 20:00 | 229.46 | 219.72
2017-05-21 20:30 | 228.28 | 218.46
2017-05-21 21:00 | 227.08 | 217.06
2017-05-21 21:30 | 226.67 | 217.12
2017-05-21 22:00 | 225.16 | 215.99
2017-05-21 22:30 | 223.63 | 214.46
2017-05-21 23:00 | 221.8 | 212.26
2017-05-21 23:30 | 221.89 | 212.31
2017-05-22 | 220.54 | 211.1
2017-05-22 00:30 | 219.09 | 210.94
2017-05-22 01:00 | 217.89 | 209.61
2017-05-22 01:30 | 217.32 | 209.17
2017-05-22 02:00 | 216.67 | 208.87
2017-05-22 02:30 | 216.36 | 208.74
2017-05-22 03:00 | 215.93 | 208.31
2017-05-22 03:30 | 216.26 | 208.62
2017-05-22 04:00 | 216.4 | 208.56
2017-05-22 04:30 | 216.84 | 208.92
2017-05-22 05:00 | 218.04 | 210.29
2017-05-22 05:30 | 219.35 | 211.68
2017-05-22 06:00 | 222.16 | 214.68
2017-05-22 06:30 | 225.69 | 218.15
2017-05-22 07:00 | 229.15 | 221.36
2017-05-22 07:30 | 230.75 | 222.93
2017-05-22 08:00 | 229.49 | 221.96
2017-05-22 08:30 | 227.7 | 220.18
2017-05-22 09:00 | 226.09 | 218.31
2017-05-22 09:30 | 224.67 | 216.81
2017-05-22 10:00 | 225.3 | 217.29
2017-05-22 10:30 | 224.55 | 216.18
2017-05-22 11:00 | 223.82 | 215.54
2017-05-22 11:30 | 223.38 | 215.25
2017-05-22 12:00 | 223.12 | 215.07
2017-05-22 12:30 | 222.91 | 214.66
2017-05-22 13:00 | 223.92 | 215.41
2017-05-22 13:30 | 225.15 | 216.7
2017-05-22 14:00 | 226.38 | 218.32
2017-05-22 14:30 | 225.18 | 217.34
2017-05-22 15:00 | 226.98 | 219.1
2017-05-22 15:30 | 227.65 | 219.77
2017-05-22 16:00 | 228.03 | 220.35
2017-05-22 16:30 | 227.9 | 219.99
2017-05-22 17:00 | 229.23 | 221.43
2017-05-22 17:30 | 230.01 | 222.15
2017-05-22 18:00 | 233.72 | 226.2
2017-05-22 18:30 | 236.83 | 229.31
2017-05-22 19:00 | 235.91 | 228.34
2017-05-22 19:30 | 234.56 | 226.97
2017-05-22 20:00 | 233 | 225.28
2017-05-22 20:30 | 232.21 | 224.46
2017-05-22 21:00 | 230.83 | 222.98
2017-05-22 21:30 | 229.55 | 222.07
2017-05-22 22:00 | 227.88 | 220.49
2017-05-22 22:30 | 225.56 | 218.15
2017-05-22 23:00 | 223.18 | 216.04
2017-05-22 23:30 | 222.57 | 215.44
2017-05-23 | 220.45 | 213.47
2017-05-23 00:30 | 219.53 | 212.77
2017-05-23 01:00 | 218.44 | 211.41
2017-05-23 01:30 | 217.85 | 210.8
2017-05-23 02:00 | 217.18 | 210.11
2017-05-23 02:30 | 217.18 | 209.83
2017-05-23 03:00 | 216.46 | 209.3
2017-05-23 03:30 | 216.59 | 209.42
2017-05-23 04:00 | 216.48 | 209.5
2017-05-23 04:30 | 217.08 | 210.11
2017-05-23 05:00 | 217.95 | 211.05
2017-05-23 05:30 | 219.31 | 212.53
2017-05-23 06:00 | 222.49 | 215.31
2017-05-23 06:30 | 226.46 | 218.62
2017-05-23 07:00 | 229.3 | 220.91
2017-05-23 07:30 | 230.71 | 222.72
2017-05-23 08:00 | 229.95 | 222.03
2017-05-23 08:30 | 228.3 | 220.04
2017-05-23 09:00 | 226.67 | 217.5
2017-05-23 09:30 | 228.35 | 216.05
2017-05-23 10:00 | 228.49 | 216.26
2017-05-23 10:30 | 230.07 | 218.02
2017-05-23 11:00 | 229.78 | 217.94
2017-05-23 11:30 | 228.47 | 216.47
2017-05-23 12:00 | 226.82 | 214.43
2017-05-23 12:30 | 227.24 | 214.85
2017-05-23 13:00 | 228.36 | 215.71
2017-05-23 13:30 | 228.19 | 215.78
2017-05-23 14:00 | 230.04 | 217.74
2017-05-23 14:30 | 230.4 | 218.3
2017-05-23 15:00 | 230.71 | 218.95
2017-05-23 15:30 | 231.79 | 219.73
2017-05-23 16:00 | 232.78 | 220.08
2017-05-23 16:30 | 232.36 | 219.53
2017-05-23 17:00 | 232.94 | 220.5
2017-05-23 17:30 | 234.44 | 222.26
2017-05-23 18:00 | 237.59 | 225.61
2017-05-23 18:30 | 239.82 | 227.86
2017-05-23 19:00 | 238.94 | 226.85
2017-05-23 19:30 | 238.34 | 225.63
2017-05-23 20:00 | 237.47 | 224.62
2017-05-23 20:30 | 236.67 | 223.58
2017-05-23 21:00 | 235.29 | 222.37
2017-05-23 21:30 | 233.47 | 221.51
2017-05-23 22:00 | 231.35 | 220.04
2017-05-23 22:30 | 230.21 | 217.92
2017-05-23 23:00 | 229.21 | 216.66
2017-05-23 23:30 | 228.44 | 215.96
2017-05-24 | 226.9 | 214.88
2017-05-24 00:30 | 226.09 | 213.98
2017-05-24 01:00 | 224.12 | 213
2017-05-24 01:30 | 223.39 | 212.82
2017-05-24 02:00 | 222.96 | 212.09
2017-05-24 02:30 | 221.65 | 210.38
2017-05-24 03:00 | 221.63 | 210.45
2017-05-24 03:30 | 221.71 | 210.57
2017-05-24 04:00 | 221.21 | 210.19
2017-05-24 04:30 | 221.83 | 210.84
2017-05-24 05:00 | 221.8 | 210.87
2017-05-24 05:30 | 223.42 | 211.96
2017-05-24 06:00 | 228.43 | 214.91
2017-05-24 06:30 | 230.81 | 217.39
2017-05-24 07:00 | 232.66 | 219.26
2017-05-24 07:30 | 234.12 | 221.36
2017-05-24 08:00 | 233.93 | 221.13
2017-05-24 08:30 | 231.69 | 218.75
2017-05-24 09:00 | 230.69 | 217.35
2017-05-24 09:30 | 232.71 | 218.94
2017-05-24 10:00 | 231.86 | 218.14
2017-05-24 10:30 | 230.7 | 217.03
2017-05-24 11:00 | 229.77 | 216.15
2017-05-24 11:30 | 229.13 | 215.67
2017-05-24 12:00 | 229.34 | 215.8
2017-05-24 12:30 | 229.02 | 215.23
2017-05-24 13:00 | 229.03 | 215.3
2017-05-24 13:30 | 228.64 | 214.82
2017-05-24 14:00 | 228.4 | 215.04
2017-05-24 14:30 | 229.08 | 215.67
2017-05-24 15:00 | 230.12 | 216.33
2017-05-24 15:30 | 230.57 | 216.64
2017-05-24 16:00 | 232.14 | 218.4
2017-05-24 16:30 | 232.48 | 218.62
2017-05-24 17:00 | 235.61 | 221.04
2017-05-24 17:30 | 236.99 | 222.15
2017-05-24 18:00 | 241.03 | 226.11
2017-05-24 18:30 | 242.66 | 227.59
2017-05-24 19:00 | 242.82 | 227.71
2017-05-24 19:30 | 242.11 | 226.38
2017-05-24 20:00 | 240.17 | 224.13
2017-05-24 20:30 | 239.19 | 222.97
2017-05-24 21:00 | 237.58 | 221.71
2017-05-24 21:30 | 233.59 | 221.3
2017-05-24 22:00 | 231.42 | 219.51
2017-05-24 22:30 | 230.26 | 218.22
2017-05-24 23:00 | 228.63 | 216.53
2017-05-24 23:30 | 227.95 | 215.94
2017-05-25 | 226.09 | 214.29
2017-05-25 00:30 | 224.54 | 213.1
2017-05-25 01:00 | 223.27 | 211.72
2017-05-25 01:30 | 223.18 | 211.84
2017-05-25 02:00 | 222.92 | 211.73
2017-05-25 02:30 | 222.06 | 210.69
2017-05-25 03:00 | 220.23 | 208.86
2017-05-25 03:30 | 219.85 | 208.85
2017-05-25 04:00 | 220.94 | 210.01
2017-05-25 04:30 | 221.85 | 210.53
2017-05-25 05:00 | 222.81 | 211.75
2017-05-25 05:30 | 224.86 | 213.98
2017-05-25 06:00 | 227.8 | 216.74
2017-05-25 06:30 | 230.56 | 220.09
2017-05-25 07:00 | 233.79 | 222.9
2017-05-25 07:30 | 236.42 | 225.8
2017-05-25 08:00 | 235.42 | 224.99
2017-05-25 08:30 | 232.28 | 221.6
2017-05-25 09:00 | 229.59 | 218.43
2017-05-25 09:30 | 226.98 | 215.52
2017-05-25 10:00 | 225.9 | 214.29
2017-05-25 10:30 | 227.71 | 215.74
2017-05-25 11:00 | 226.11 | 214.01
2017-05-25 11:30 | 225.7 | 213.63
2017-05-25 12:00 | 225.17 | 213.07
2017-05-25 12:30 | 221.69 | 209.49
2017-05-25 13:00 | 221.32 | 208.94
2017-05-25 13:30 | 226.5 | 214.16
2017-05-25 14:00 | 226.83 | 214.72
2017-05-25 14:30 | 226.82 | 214.97
2017-05-25 15:00 | 227.57 | 215.55
2017-05-25 15:30 | 227.83 | 215.78
2017-05-25 16:00 | 228.75 | 216.61
2017-05-25 16:30 | 231.3 | 218.26
2017-05-25 17:00 | 233.05 | 219.77
2017-05-25 17:30 | 234.47 | 221.47
2017-05-25 18:00 | 238.45 | 225.67
2017-05-25 18:30 | 241.53 | 228.96
2017-05-25 19:00 | 242.18 | 229.6
2017-05-25 19:30 | 241 | 228.26
2017-05-25 20:00 | 237.88 | 225.09
2017-05-25 20:30 | 237.02 | 224.01
2017-05-25 21:00 | 235.29 | 222.18
2017-05-25 21:30 | 233.95 | 221.75
2017-05-25 22:00 | 231.63 | 219.7
2017-05-25 22:30 | 229.99 | 217.72
2017-05-25 23:00 | 228.5 | 216.09
2017-05-25 23:30 | 226.91 | 214.54
2017-05-26 | 225.36 | 213.13
2017-05-26 00:30 | 225.41 | 213.15
2017-05-26 01:00 | 224.05 | 212.31
2017-05-26 01:30 | 223.5 | 211.81
2017-05-26 02:00 | 223.08 | 211.31
2017-05-26 02:30 | 223.06 | 211.15
2017-05-26 03:00 | 223.26 | 211.38
2017-05-26 03:30 | 223.1 | 211.32
2017-05-26 04:00 | 223.51 | 212.18
2017-05-26 04:30 | 225.51 | 214.35
2017-05-26 05:00 | 228.46 | 217.59
2017-05-26 05:30 | 229.78 | 219.2
2017-05-26 06:00 | 233.75 | 222.46
2017-05-26 06:30 | 236.91 | 225.53
2017-05-26 07:00 | 239.97 | 228.85
2017-05-26 07:30 | 242.57 | 231.86
2017-05-26 08:00 | 242.07 | 231.16
2017-05-26 08:30 | 239.02 | 227.75
2017-05-26 09:00 | 236.1 | 224.13
2017-05-26 09:30 | 232.89 | 220.57
2017-05-26 10:00 | 230.79 | 218.43
2017-05-26 10:30 | 230.32 | 217.18
2017-05-26 11:00 | 227.88 | 214.29
2017-05-26 11:30 | 227.66 | 213.99
2017-05-26 12:00 | 227.26 | 213.66
2017-05-26 12:30 | 228.59 | 215.4
2017-05-26 13:00 | 226.97 | 212.98
2017-05-26 13:30 | 226.11 | 211.73
2017-05-26 14:00 | 226.44 | 212.25
2017-05-26 14:30 | 226.59 | 212.37
2017-05-26 15:00 | 226.48 | 212.39
2017-05-26 15:30 | 225.81 | 211.95
2017-05-26 16:00 | 227.33 | 213.38
2017-05-26 16:30 | 229.97 | 215.97
2017-05-26 17:00 | 232.1 | 218.25
2017-05-26 17:30 | 233.78 | 220.38
2017-05-26 18:00 | 237.62 | 224.59
2017-05-26 18:30 | 240.49 | 227.57
2017-05-26 19:00 | 240.46 | 227.57
2017-05-26 19:30 | 239.92 | 226.81
2017-05-26 20:00 | 238.66 | 225.41
2017-05-26 20:30 | 237.86 | 224.54
2017-05-26 21:00 | 237.36 | 223.78
2017-05-26 21:30 | 233.7 | 220.95
2017-05-26 22:00 | 231.95 | 219.49
2017-05-26 22:30 | 229.96 | 217.69
2017-05-26 23:00 | 228.28 | 215.69
2017-05-26 23:30 | 226.63 | 214.72
2017-05-27 | 225.13 | 213.17
2017-05-27 00:30 | 223.36 | 211.58
2017-05-27 01:00 | 222.67 | 210.96
2017-05-27 01:30 | 222.65 | 210.96
2017-05-27 02:00 | 222.84 | 210.9
2017-05-27 02:30 | 222.73 | 210.74
2017-05-27 03:00 | 222.86 | 210.91
2017-05-27 03:30 | 206.78 | 194.73
2017-05-27 04:00 | 201.17 | 189.01
2017-05-27 04:30 | 201.38 | 189.67
2017-05-27 05:00 | 202.58 | 190.94
2017-05-27 05:30 | 203.18 | 191.58
2017-05-27 06:00 | 204.77 | 193.21
2017-05-27 06:30 | 206.75 | 195.1
2017-05-27 07:00 | 219.43 | 208.17
2017-05-27 07:30 | 230.3 | 219.39
2017-05-27 08:00 | 229.94 | 218.93
2017-05-27 08:30 | 228.34 | 217.16
2017-05-27 09:00 | 227.11 | 215.28
2017-05-27 09:30 | 226.28 | 213.65
2017-05-27 10:00 | 226.12 | 212.94
2017-05-27 10:30 | 226.17 | 212.65
2017-05-27 11:00 | 226.1 | 212.48
2017-05-27 11:30 | 224.8 | 211.22
2017-05-27 12:00 | 224.47 | 210.79
2017-05-27 12:30 | 224.58 | 210.81
2017-05-27 13:00 | 222.42 | 208.21
2017-05-27 13:30 | 222.25 | 207.95
2017-05-27 14:00 | 223.47 | 209.45
2017-05-27 14:30 | 223.83 | 209.87
2017-05-27 15:00 | 223.47 | 209.65
2017-05-27 15:30 | 223.83 | 210.39
2017-05-27 16:00 | 224.67 | 211.17
2017-05-27 16:30 | 226.85 | 213.4
2017-05-27 17:00 | 228.62 | 215.42
2017-05-27 17:30 | 230.54 | 217.6
2017-05-27 18:00 | 233.13 | 220.67
2017-05-27 18:30 | 235.22 | 222.86
2017-05-27 19:00 | 234.68 | 222.21
2017-05-27 19:30 | 233.82 | 221.34
2017-05-27 20:00 | 232.78 | 220.07
2017-05-27 20:30 | 232.53 | 219.74
2017-05-27 21:00 | 231.01 | 218.53
2017-05-27 21:30 | 230.21 | 218.26
2017-05-27 22:00 | 228.86 | 217.08
2017-05-27 22:30 | 227.97 | 216.05
2017-05-27 23:00 | 226.75 | 214.55
2017-05-27 23:30 | 225.89 | 214.12
2017-05-28 | 224.33 | 212.68
2017-05-28 00:30 | 223.27 | 211.46
2017-05-28 01:00 | 222.43 | 210.57
2017-05-28 01:30 | 221.9 | 210.02
2017-05-28 02:00 | 205 | 193.15
2017-05-28 02:30 | 173.65 | 161.13
2017-05-28 03:00 | 161.83 | 148.98
2017-05-28 03:30 | 161.97 | 149.3
2017-05-28 04:00 | 162.2 | 149.58
2017-05-28 04:30 | 162.17 | 149.7
2017-05-28 05:00 | 162.02 | 149.6
2017-05-28 05:30 | 162.68 | 150.28
2017-05-28 06:00 | 163.84 | 151.43
2017-05-28 06:30 | 164.49 | 151.98
2017-05-28 07:00 | 195.46 | 183.42
2017-05-28 07:30 | 212.49 | 201.25
2017-05-28 08:00 | 223.48 | 212.45
2017-05-28 08:30 | 224.69 | 214.26
2017-05-28 09:00 | 224.15 | 213.32
2017-05-28 09:30 | 221.9 | 210.64
2017-05-28 10:00 | 219.44 | 207.91
2017-05-28 10:30 | 221.21 | 209.26
2017-05-28 11:00 | 221.9 | 210.01
2017-05-28 11:30 | 221.25 | 209.22
2017-05-28 12:00 | 220.69 | 208.69
2017-05-28 12:30 | 220.83 | 208.79
2017-05-28 13:00 | 221.51 | 209.36
2017-05-28 13:30 | 221.7 | 209.17
2017-05-28 14:00 | 221.64 | 208.95
2017-05-28 14:30 | 221.26 | 209.32
2017-05-28 15:00 | 222.01 | 210.43
2017-05-28 15:30 | 222.92 | 210.61
2017-05-28 16:00 | 223.57 | 211.24
2017-05-28 16:30 | 226.34 | 212.7
2017-05-28 17:00 | 227.8 | 214.06
2017-05-28 17:30 | 228.96 | 215.81
2017-05-28 18:00 | 234.65 | 220.66
2017-05-28 18:30 | 237.19 | 223.06
2017-05-28 19:00 | 236.33 | 221.97
2017-05-28 19:30 | 234.97 | 220.25
2017-05-28 20:00 | 234.4 | 219.56
2017-05-28 20:30 | 233.51 | 219
2017-05-28 21:00 | 232.57 | 218.26
2017-05-28 21:30 | 232.24 | 218.48
2017-05-28 22:00 | 230.27 | 217.01
2017-05-28 22:30 | 227.94 | 215.07
2017-05-28 23:00 | 226.37 | 213.25
2017-05-28 23:30 | 226.04 | 212.76
2017-05-29 | 224.2 | 210.7
2017-05-29 00:30 | 223.27 | 210.04
2017-05-29 01:00 | 222.15 | 209.17
2017-05-29 01:30 | 221.62 | 208.63
2017-05-29 02:00 | 221.01 | 208.04
2017-05-29 02:30 | 217.95 | 205.86
2017-05-29 03:00 | 218.01 | 206.22
2017-05-29 03:30 | 218.52 | 206.87
2017-05-29 04:00 | 218.91 | 207.72
2017-05-29 04:30 | 219.8 | 208.46
2017-05-29 05:00 | 221.09 | 209.27
2017-05-29 05:30 | 223.01 | 210.85
2017-05-29 06:00 | 226.7 | 213.77
2017-05-29 06:30 | 230.28 | 217.23
2017-05-29 07:00 | 234.68 | 221.62
2017-05-29 07:30 | 237.26 | 224.12
2017-05-29 08:00 | 237.6 | 224.53
2017-05-29 08:30 | 234.56 | 221.29
2017-05-29 09:00 | 229.69 | 216.04
2017-05-29 09:30 | 226.03 | 212.18
2017-05-29 10:00 | 227.34 | 213.33
2017-05-29 10:30 | 226.14 | 211.97
2017-05-29 11:00 | 225.48 | 211.36
2017-05-29 11:30 | 224.67 | 210.35
2017-05-29 12:00 | 224.57 | 210.53
2017-05-29 12:30 | 224.79 | 210.9
2017-05-29 13:00 | 225.25 | 211.44
2017-05-29 13:30 | 225.66 | 211.8
2017-05-29 14:00 | 225.58 | 211.92
2017-05-29 14:30 | 225.61 | 212.22
2017-05-29 15:00 | 226.77 | 212.88
2017-05-29 15:30 | 227.61 | 213.68
2017-05-29 16:00 | 227.98 | 214.15
2017-05-29 16:30 | 229.48 | 215.36
2017-05-29 17:00 | 231.21 | 217.02
2017-05-29 17:30 | 233.58 | 219.72
2017-05-29 18:00 | 238.21 | 224.89
2017-05-29 18:30 | 243.64 | 230.76
2017-05-29 19:00 | 243.99 | 230.97
2017-05-29 19:30 | 243.95 | 230.52
2017-05-29 20:00 | 242.79 | 229.03
2017-05-29 20:30 | 241.23 | 227.2
2017-05-29 21:00 | 240.6 | 226.22
2017-05-29 21:30 | 236.75 | 223.47
2017-05-29 22:00 | 234.54 | 221.52
2017-05-29 22:30 | 231.93 | 218.32
2017-05-29 23:00 | 229.45 | 215.73
2017-05-29 23:30 | 229.38 | 215.64
2017-05-30 | 228.3 | 214.57
2017-05-30 00:30 | 227.26 | 213.89
2017-05-30 01:00 | 225.52 | 212.91
2017-05-30 01:30 | 225.03 | 212.54
2017-05-30 02:00 | 225.14 | 212.68
2017-05-30 02:30 | 225.38 | 212.96
2017-05-30 03:00 | 225.79 | 213.38
2017-05-30 03:30 | 225.35 | 213.05
2017-05-30 04:00 | 224.75 | 212.77
2017-05-30 04:30 | 226.33 | 213.97
2017-05-30 05:00 | 227.84 | 215.69
2017-05-30 05:30 | 229.39 | 217.89
2017-05-30 06:00 | 232.7 | 221.5
2017-05-30 06:30 | 236.82 | 225.36
2017-05-30 07:00 | 241.95 | 229.58
2017-05-30 07:30 | 244.28 | 231.94
2017-05-30 08:00 | 243.85 | 231.11
2017-05-30 08:30 | 240.66 | 227.67
2017-05-30 09:00 | 233.69 | 220.67
2017-05-30 09:30 | 237.08 | 231.02
2017-05-30 10:00 | 238.38 | 232.08
2017-05-30 10:30 | 241.13 | 234.27
2017-05-30 11:00 | 243.16 | 236.36
2017-05-30 11:30 | 243.8 | 237.1
2017-05-30 12:00 | 243.67 | 236.84
2017-05-30 12:30 | 244.05 | 237.1
2017-05-30 13:00 | 244.61 | 237.47
2017-05-30 13:30 | 240.86 | 233.15
2017-05-30 14:00 | 231.24 | 216.12
2017-05-30 14:30 | 230.6 | 215.74
2017-05-30 15:00 | 231.18 | 216.39
2017-05-30 15:30 | 234.3 | 219.94
2017-05-30 16:00 | 235.55 | 221.29
2017-05-30 16:30 | 234.91 | 219.88
2017-05-30 17:00 | 235.68 | 221
2017-05-30 17:30 | 239.1 | 224.61
2017-05-30 18:00 | 245.16 | 231.34
2017-05-30 18:30 | 247.98 | 234.19
2017-05-30 19:00 | 245.87 | 231.91
2017-05-30 19:30 | 243.68 | 229.41
2017-05-30 20:00 | 242.64 | 228.53
2017-05-30 20:30 | 242.25 | 228.4
2017-05-30 21:00 | 241.01 | 226.59
2017-05-30 21:30 | 240.27 | 226.19
2017-05-30 22:00 | 237.98 | 223.97
2017-05-30 22:30 | 236.26 | 221.87
2017-05-30 23:00 | 234.5 | 219.59
2017-05-30 23:30 | 233.81 | 218.82
2017-05-31 | 232.58 | 217.74
2017-05-31 00:30 | 232.23 | 217.37
2017-05-31 01:00 | 230.41 | 215.72
2017-05-31 01:30 | 229.03 | 215.15
2017-05-31 02:00 | 228.87 | 215.21
2017-05-31 02:30 | 228.34 | 214.98
2017-05-31 03:00 | 228.34 | 214.9
2017-05-31 03:30 | 228.31 | 215.19
2017-05-31 04:00 | 228.19 | 215.2
2017-05-31 04:30 | 228.7 | 216.05
2017-05-31 05:00 | 230.57 | 217.98
2017-05-31 05:30 | 231.8 | 219.61
2017-05-31 06:00 | 237.43 | 224.15
2017-05-31 06:30 | 241.65 | 229.17
2017-05-31 07:00 | 245.56 | 233.11
2017-05-31 07:30 | 249.13 | 236.81
2017-05-31 08:00 | 247.97 | 235.2
2017-05-31 08:30 | 243.88 | 230.52
2017-05-31 09:00 | 241.72 | 227.5
2017-05-31 09:30 | 239.35 | 224.42
2017-05-31 10:00 | 236.82 | 221.73
2017-05-31 10:30 | 234.41 | 218.76
2017-05-31 11:00 | 230.59 | 216.25
2017-05-31 11:30 | 229.78 | 215.47
2017-05-31 12:00 | 228.76 | 214.15
2017-05-31 12:30 | 230.11 | 214.77
2017-05-31 13:00 | 230.88 | 215.15
2017-05-31 13:30 | 232.75 | 216.77
2017-05-31 14:00 | 232.3 | 217.02
2017-05-31 14:30 | 231.47 | 216.6
2017-05-31 15:00 | 231.4 | 216.77
2017-05-31 15:30 | 233.31 | 218.22
2017-05-31 16:00 | 235.95 | 221.69
2017-05-31 16:30 | 238.41 | 224.22
2017-05-31 17:00 | 240.72 | 226.69
2017-05-31 17:30 | 243.34 | 229.88
2017-05-31 18:00 | 248.44 | 235.69
2017-05-31 18:30 | 252.36 | 239.98
2017-05-31 19:00 | 252.91 | 240.39
2017-05-31 19:30 | 250.92 | 238.09
2017-05-31 20:00 | 250.12 | 237.3
2017-05-31 20:30 | 249.57 | 237.08
2017-05-31 21:00 | 247.01 | 234.18
2017-05-31 21:30 | 246.11 | 233.93
2017-05-31 22:00 | 245.15 | 233.04
2017-05-31 22:30 | 243.15 | 230.25
2017-05-31 23:00 | 239.69 | 226.56
2017-05-31 23:30 | 238.68 | 225.37
2017-06-01 | 236.15 | 223.44
2017-06-01 00:30 | 235.95 | 223.48
2017-06-01 01:00 | 234.18 | 221.64
2017-06-01 01:30 | 232.6 | 220.91
2017-06-01 02:00 | 231.73 | 220.28
2017-06-01 02:30 | 231.4 | 220.02
2017-06-01 03:00 | 231.84 | 220.51
2017-06-01 03:30 | 231.77 | 220.41
2017-06-01 04:00 | 231.98 | 220.52
2017-06-01 04:30 | 233.15 | 221.77
2017-06-01 05:00 | 234.6 | 223.46
2017-06-01 05:30 | 236.29 | 225.5
2017-06-01 06:00 | 240.27 | 229.13
2017-06-01 06:30 | 239.04 | 228.46
2017-06-01 07:00 | 236.09 | 226.43
2017-06-01 07:30 | 241.84 | 232.67
2017-06-01 08:00 | 244.13 | 234.65
2017-06-01 08:30 | 243.33 | 233.21
2017-06-01 09:00 | 246.65 | 235.22
2017-06-01 09:30 | 242.29 | 230.66
2017-06-01 10:00 | 239.9 | 228.01
2017-06-01 10:30 | 237.06 | 224.68
2017-06-01 11:00 | 234.59 | 221.76
2017-06-01 11:30 | 233.26 | 219.78
2017-06-01 12:00 | 232.87 | 218.93
2017-06-01 12:30 | 231.04 | 216.54
2017-06-01 13:00 | 231.1 | 216.66
2017-06-01 13:30 | 233.64 | 218.92
2017-06-01 14:00 | 235.14 | 220.46
2017-06-01 14:30 | 234.5 | 220.03
2017-06-01 15:00 | 234.79 | 220.3
2017-06-01 15:30 | 235.27 | 220.95
2017-06-01 16:00 | 236.09 | 221.99
2017-06-01 16:30 | 237.48 | 223.47
2017-06-01 17:00 | 239.16 | 225.7
2017-06-01 17:30 | 243.21 | 229.89
2017-06-01 18:00 | 250.06 | 237.49
2017-06-01 18:30 | 252.88 | 240.87
2017-06-01 19:00 | 254.73 | 242.87
2017-06-01 19:30 | 253.81 | 241.94
2017-06-01 20:00 | 252.86 | 240.73
2017-06-01 20:30 | 251.58 | 239.47
2017-06-01 21:00 | 249.1 | 237.17
2017-06-01 21:30 | 247.28 | 235.43
2017-06-01 22:00 | 244.88 | 232.65
2017-06-01 22:30 | 242.75 | 230.02
2017-06-01 23:00 | 240.83 | 227.43
2017-06-01 23:30 | 239.62 | 226.17
2017-06-02 | 237.9 | 224.74
2017-06-02 00:30 | 237.69 | 224.51
2017-06-02 01:00 | 236.05 | 222.7
2017-06-02 01:30 | 232.77 | 219.96
2017-06-02 02:00 | 231.58 | 218.89
2017-06-02 02:30 | 232.05 | 219.61
2017-06-02 03:00 | 230.63 | 218.81
2017-06-02 03:30 | 231.73 | 220.13
2017-06-02 04:00 | 231.67 | 220.88
2017-06-02 04:30 | 232.45 | 221.81
2017-06-02 05:00 | 234.36 | 223.53
2017-06-02 05:30 | 236.92 | 226.1
2017-06-02 06:00 | 242.04 | 230.37
2017-06-02 06:30 | 245.57 | 234.28
2017-06-02 07:00 | 249.65 | 238.57
2017-06-02 07:30 | 250.82 | 240.11
2017-06-02 08:00 | 250.29 | 239.77
2017-06-02 08:30 | 248.18 | 237.42
2017-06-02 09:00 | 242.55 | 231.3
2017-06-02 09:30 | 238.63 | 226.78
2017-06-02 10:00 | 236.47 | 224.27
2017-06-02 10:30 | 234.2 | 221.23
2017-06-02 11:00 | 236.05 | 223.13
2017-06-02 11:30 | 235.7 | 222.11
2017-06-02 12:00 | 234.86 | 220.62
2017-06-02 12:30 | 231.99 | 217.51
2017-06-02 13:00 | 233.32 | 218.51
2017-06-02 13:30 | 232.51 | 217.47
2017-06-02 14:00 | 231.31 | 216.52
2017-06-02 14:30 | 231.36 | 216.93
2017-06-02 15:00 | 232.37 | 217.68
2017-06-02 15:30 | 232.62 | 217.73
2017-06-02 16:00 | 232.88 | 218.22
2017-06-02 16:30 | 234.9 | 220.63
2017-06-02 17:00 | 237.58 | 223.75
2017-06-02 17:30 | 241.07 | 226.92
2017-06-02 18:00 | 246.96 | 233.36
2017-06-02 18:30 | 248.83 | 235.52
2017-06-02 19:00 | 246.96 | 233.6
2017-06-02 19:30 | 246.24 | 232.76
2017-06-02 20:00 | 245.54 | 232.09
2017-06-02 20:30 | 245.29 | 232.12
2017-06-02 21:00 | 244.93 | 231.54
2017-06-02 21:30 | 243.57 | 230.91
2017-06-02 22:00 | 242.33 | 229.66
2017-06-02 22:30 | 240.02 | 227.43
2017-06-02 23:00 | 238.43 | 225.29
2017-06-02 23:30 | 237.34 | 224.53
2017-06-03 | 236.02 | 223.16
2017-06-03 00:30 | 234.03 | 221.8
2017-06-03 01:00 | 233.03 | 221.11
2017-06-03 01:30 | 232.21 | 221.25
2017-06-03 02:00 | 231.32 | 220.57
2017-06-03 02:30 | 230.21 | 220.38
2017-06-03 03:00 | 231.74 | 220.06
2017-06-03 03:30 | 232.69 | 220.32
2017-06-03 04:00 | 233.42 | 221.29
2017-06-03 04:30 | 233.72 | 221.74
2017-06-03 05:00 | 234.35 | 222.6
2017-06-03 05:30 | 235.49 | 224.16
2017-06-03 06:00 | 237.69 | 225.85
2017-06-03 06:30 | 241.24 | 228.08
2017-06-03 07:00 | 244.82 | 230.87
2017-06-03 07:30 | 247.62 | 233.58
2017-06-03 08:00 | 248.6 | 234.68
2017-06-03 08:30 | 248.77 | 233.85
2017-06-03 09:00 | 246.32 | 230.53
2017-06-03 09:30 | 238.89 | 225.61
2017-06-03 10:00 | 236.93 | 223.28
2017-06-03 10:30 | 233.39 | 219.71
2017-06-03 11:00 | 231.41 | 217.37
2017-06-03 11:30 | 233.19 | 219.1
2017-06-03 12:00 | 231.51 | 217.64
2017-06-03 12:30 | 231.14 | 217.08
2017-06-03 13:00 | 231.01 | 216.85
2017-06-03 13:30 | 230.98 | 216.75
2017-06-03 14:00 | 230.79 | 216.37
2017-06-03 14:30 | 229.95 | 215.59
2017-06-03 15:00 | 230.77 | 216.45
2017-06-03 15:30 | 231.13 | 217.01
2017-06-03 16:00 | 232.59 | 218.61
2017-06-03 16:30 | 234.45 | 220.46
2017-06-03 17:00 | 236.83 | 222.56
2017-06-03 17:30 | 240.2 | 227
2017-06-03 18:00 | 245.95 | 233.56
2017-06-03 18:30 | 249.42 | 236.7
2017-06-03 19:00 | 247.8 | 234.91
2017-06-03 19:30 | 246.01 | 232.97
2017-06-03 20:00 | 244.63 | 231.49
2017-06-03 20:30 | 245.26 | 232.34
2017-06-03 21:00 | 244.52 | 231.28
2017-06-03 21:30 | 244 | 231.16
2017-06-03 22:00 | 243.08 | 230.41
2017-06-03 22:30 | 242.26 | 229.11
2017-06-03 23:00 | 239.32 | 226.25
2017-06-03 23:30 | 239.03 | 226.18
2017-06-04 | 238.4 | 225.33
2017-06-04 00:30 | 237.45 | 224.7
2017-06-04 01:00 | 235.79 | 223.55
2017-06-04 01:30 | 234.74 | 222.62
2017-06-04 02:00 | 234.21 | 221.83
2017-06-04 02:30 | 234.38 | 222.14
2017-06-04 03:00 | 234.43 | 222.13
2017-06-04 03:30 | 217.45 | 206
2017-06-04 04:00 | 213.3 | 202.05
2017-06-04 04:30 | 213.29 | 202
2017-06-04 05:00 | 214.49 | 203.41
2017-06-04 05:30 | 216.24 | 205.23
2017-06-04 06:00 | 231.06 | 220.63
2017-06-04 06:30 | 238.59 | 228.44
2017-06-04 07:00 | 240.57 | 230.86
2017-06-04 07:30 | 242.59 | 233.12
2017-06-04 08:00 | 241.77 | 232.52
2017-06-04 08:30 | 241.45 | 231.91
2017-06-04 09:00 | 239.73 | 229.63
2017-06-04 09:30 | 237.58 | 226.95
2017-06-04 10:00 | 217.13 | 205.55
2017-06-04 10:30 | 176.69 | 161.12
2017-06-04 11:00 | 174.95 | 159.18
2017-06-04 11:30 | 172.81 | 157.67
2017-06-04 12:00 | 172.21 | 156.82
2017-06-04 12:30 | 171.36 | 156.67
2017-06-04 13:00 | 171.29 | 155.71
2017-06-04 13:30 | 170.61 | 155.74
2017-06-04 14:00 | 188.18 | 174.29
2017-06-04 14:30 | 228.82 | 215.81
2017-06-04 15:00 | 232.2 | 218.98
2017-06-04 15:30 | 232.18 | 218.79
2017-06-04 16:00 | 235.3 | 221.93
2017-06-04 16:30 | 237.44 | 223.93
2017-06-04 17:00 | 239.11 | 225.61
2017-06-04 17:30 | 241.74 | 228.89
2017-06-04 18:00 | 247.76 | 235.26
2017-06-04 18:30 | 251.44 | 239.07
2017-06-04 19:00 | 251.71 | 239.22
2017-06-04 19:30 | 249.63 | 236.94
2017-06-04 20:00 | 247.86 | 235.12
2017-06-04 20:30 | 246.52 | 233.9
2017-06-04 21:00 | 245.74 | 233.01
2017-06-04 21:30 | 245.46 | 232.76
2017-06-04 22:00 | 243.85 | 231.06
2017-06-04 22:30 | 241.69 | 228.44
2017-06-04 23:00 | 240.76 | 227.11
2017-06-04 23:30 | 238.69 | 225.18
2017-06-05 | 237.01 | 223.89
2017-06-05 00:30 | 236.58 | 223.91
2017-06-05 01:00 | 234.59 | 222.91
2017-06-05 01:30 | 234.14 | 222.61
2017-06-05 02:00 | 233.68 | 221.11
2017-06-05 02:30 | 234.06 | 220.13
2017-06-05 03:00 | 234.27 | 220.51
2017-06-05 03:30 | 235.17 | 221.02
2017-06-05 04:00 | 235.9 | 221.39
2017-06-05 04:30 | 236.31 | 222.29
2017-06-05 05:00 | 237.99 | 224.49
2017-06-05 05:30 | 240.49 | 227.19
2017-06-05 06:00 | 243.57 | 230.5
2017-06-05 06:30 | 249.41 | 236.22
2017-06-05 07:00 | 254.2 | 241.02
2017-06-05 07:30 | 256.16 | 243.44
2017-06-05 08:00 | 254.83 | 241.95
2017-06-05 08:30 | 250.27 | 237.07
2017-06-05 09:00 | 246.37 | 232.79
2017-06-05 09:30 | 243.29 | 229.32
2017-06-05 10:00 | 241.83 | 227.05
2017-06-05 10:30 | 240.63 | 224.85
2017-06-05 11:00 | 240.99 | 225.33
2017-06-05 11:30 | 240.84 | 224.35
2017-06-05 12:00 | 239.95 | 223.26
2017-06-05 12:30 | 239.17 | 222.47
2017-06-05 13:00 | 239 | 222.22
2017-06-05 13:30 | 239.24 | 222.35
2017-06-05 14:00 | 239.5 | 222.65
2017-06-05 14:30 | 239.99 | 222.65
2017-06-05 15:00 | 241.26 | 223.53
2017-06-05 15:30 | 242.74 | 224.73
2017-06-05 16:00 | 243.13 | 225.18
2017-06-05 16:30 | 243.41 | 225.52
2017-06-05 17:00 | 245.76 | 228.35
2017-06-05 17:30 | 248.6 | 231.81
2017-06-05 18:00 | 254.89 | 238.79
2017-06-05 18:30 | 259.16 | 243.3
2017-06-05 19:00 | 259.95 | 244.11
2017-06-05 19:30 | 257.45 | 241.27
2017-06-05 20:00 | 255.01 | 238.67
2017-06-05 20:30 | 253.27 | 236.77
2017-06-05 21:00 | 250.24 | 233.04
2017-06-05 21:30 | 248.37 | 231.21
2017-06-05 22:00 | 247.26 | 230.09
2017-06-05 22:30 | 245.29 | 227.46
2017-06-05 23:00 | 243.69 | 225.53
2017-06-05 23:30 | 243.93 | 225.7
2017-06-06 | 242.46 | 224.91
2017-06-06 00:30 | 240.84 | 223.94
2017-06-06 01:00 | 239.3 | 222.46
2017-06-06 01:30 | 237.67 | 221.49
2017-06-06 02:00 | 237.56 | 221.79
2017-06-06 02:30 | 237.93 | 222.15
2017-06-06 03:00 | 238.02 | 222.11
2017-06-06 03:30 | 238.89 | 223.01
2017-06-06 04:00 | 239.1 | 223.55
2017-06-06 04:30 | 239.69 | 224.59
2017-06-06 05:00 | 241.63 | 226.28
2017-06-06 05:30 | 244.47 | 229.62
2017-06-06 06:00 | 248.06 | 233.04
2017-06-06 06:30 | 252.42 | 237.98
2017-06-06 07:00 | 255.88 | 241.84
2017-06-06 07:30 | 259.86 | 244.83
2017-06-06 08:00 | 258.62 | 243.49
2017-06-06 08:30 | 256.03 | 240.56
2017-06-06 09:00 | 252.63 | 236.61
2017-06-06 09:30 | 247.16 | 230.58
2017-06-06 10:00 | 244.9 | 227.84
2017-06-06 10:30 | 241.52 | 224.21
2017-06-06 11:00 | 239.13 | 221.6
2017-06-06 11:30 | 240.52 | 223.03
2017-06-06 12:00 | 241.13 | 223.72
2017-06-06 12:30 | 240.24 | 222.7
2017-06-06 13:00 | 241.47 | 224.32
2017-06-06 13:30 | 245.02 | 227.67
2017-06-06 14:00 | 245.19 | 227.79
2017-06-06 14:30 | 245.38 | 228
2017-06-06 15:00 | 245.43 | 228.18
2017-06-06 15:30 | 243.11 | 225.98
2017-06-06 16:00 | 243.44 | 226.97
2017-06-06 16:30 | 245.11 | 228.35
2017-06-06 17:00 | 247.34 | 231.34
2017-06-06 17:30 | 251.65 | 236.07
2017-06-06 18:00 | 255.06 | 240.03
2017-06-06 18:30 | 258.98 | 244.38
2017-06-06 19:00 | 259.53 | 244.95
2017-06-06 19:30 | 259.42 | 244.65
2017-06-06 20:00 | 258.99 | 244.21
2017-06-06 20:30 | 258.09 | 243.38
2017-06-06 21:00 | 257.46 | 241.83
2017-06-06 21:30 | 256.08 | 240.68
2017-06-06 22:00 | 254.34 | 238.28
2017-06-06 22:30 | 251.89 | 235.08
2017-06-06 23:00 | 246.64 | 232.46
2017-06-06 23:30 | 245.32 | 231
2017-06-07 | 243.58 | 229
2017-06-07 00:30 | 241.97 | 227.81
2017-06-07 01:00 | 239.81 | 226.53
2017-06-07 01:30 | 238.41 | 225.48
2017-06-07 02:00 | 237.72 | 225.21
2017-06-07 02:30 | 237.16 | 224.48
2017-06-07 03:00 | 237.13 | 224.58
2017-06-07 03:30 | 237.63 | 225.05
2017-06-07 04:00 | 236.94 | 225.29
2017-06-07 04:30 | 237.46 | 226.08
2017-06-07 05:00 | 238.96 | 227.73
2017-06-07 05:30 | 241.06 | 230.4
2017-06-07 06:00 | 246.31 | 234.85
2017-06-07 06:30 | 250.9 | 240.08
2017-06-07 07:00 | 254.9 | 243.87
2017-06-07 07:30 | 256.79 | 245.17
2017-06-07 08:00 | 254.95 | 243.37
2017-06-07 08:30 | 252.88 | 240.92
2017-06-07 09:00 | 249.05 | 236.73
2017-06-07 09:30 | 244.78 | 232.59
2017-06-07 10:00 | 243.05 | 230.24
2017-06-07 10:30 | 241.12 | 227.59
2017-06-07 11:00 | 239.15 | 225.19
2017-06-07 11:30 | 237.6 | 223.33
2017-06-07 12:00 | 236.38 | 221.99
2017-06-07 12:30 | 235.41 | 220.57
2017-06-07 13:00 | 235.39 | 220.71
2017-06-07 13:30 | 235.21 | 220.42
2017-06-07 14:00 | 234.85 | 220.14
2017-06-07 14:30 | 235.92 | 221.26
2017-06-07 15:00 | 236.86 | 222.06
2017-06-07 15:30 | 238.3 | 222.95
2017-06-07 16:00 | 239.48 | 224.19
2017-06-07 16:30 | 239.44 | 224.48
2017-06-07 17:00 | 242.49 | 228.26
2017-06-07 17:30 | 247.22 | 233.6
2017-06-07 18:00 | 252.9 | 240.43
2017-06-07 18:30 | 256.9 | 244.86
2017-06-07 19:00 | 258.2 | 246.34
2017-06-07 19:30 | 256.45 | 244.22
2017-06-07 20:00 | 255.66 | 243.56
2017-06-07 20:30 | 253.72 | 241.65
2017-06-07 21:00 | 252.27 | 239.87
2017-06-07 21:30 | 250.22 | 238.18
2017-06-07 22:00 | 248.09 | 235.78
2017-06-07 22:30 | 245.45 | 232.7
2017-06-07 23:00 | 243.33 | 230.22
2017-06-07 23:30 | 241.7 | 228.52
2017-06-08 | 239.92 | 226.7
2017-06-08 00:30 | 237.82 | 225.48
2017-06-08 01:00 | 236.54 | 224.14
2017-06-08 01:30 | 235.17 | 222.95
2017-06-08 02:00 | 234.79 | 222.79
2017-06-08 02:30 | 234.83 | 222.65
2017-06-08 03:00 | 233.85 | 221.7
2017-06-08 03:30 | 234.12 | 222
2017-06-08 04:00 | 236.39 | 224.38
2017-06-08 04:30 | 237.51 | 225.64
2017-06-08 05:00 | 239.14 | 227.43
2017-06-08 05:30 | 242.03 | 230.5
2017-06-08 06:00 | 247.26 | 235.14
2017-06-08 06:30 | 252.71 | 240.74
2017-06-08 07:00 | 255.04 | 243.75
2017-06-08 07:30 | 258.5 | 247.87
2017-06-08 08:00 | 257.28 | 246.66
2017-06-08 08:30 | 255.29 | 244.38
2017-06-08 09:00 | 251.23 | 240.17
2017-06-08 09:30 | 247.38 | 235.82
2017-06-08 10:00 | 245.06 | 233.18
2017-06-08 10:30 | 241.78 | 229.42
2017-06-08 11:00 | 240.44 | 227.53
2017-06-08 11:30 | 238.83 | 225.28
2017-06-08 12:00 | 238.43 | 225.53
2017-06-08 12:30 | 238.07 | 225.29
2017-06-08 13:00 | 240.21 | 226.82
2017-06-08 13:30 | 240.46 | 226.58
2017-06-08 14:00 | 240.47 | 226.29
2017-06-08 14:30 | 239.66 | 225.52
2017-06-08 15:00 | 239.93 | 225.65
2017-06-08 15:30 | 239.93 | 225.62
2017-06-08 16:00 | 241.22 | 226.24
2017-06-08 16:30 | 242.28 | 227.56
2017-06-08 17:00 | 244.36 | 230.07
2017-06-08 17:30 | 247.47 | 233.68
2017-06-08 18:00 | 252.32 | 239.38
2017-06-08 18:30 | 254.7 | 242.23
2017-06-08 19:00 | 255.66 | 243.29
2017-06-08 19:30 | 255.13 | 242.55
2017-06-08 20:00 | 254.17 | 241.46
2017-06-08 20:30 | 253.4 | 240.56
2017-06-08 21:00 | 251.55 | 238.41
2017-06-08 21:30 | 249.22 | 236.6
2017-06-08 22:00 | 247.54 | 234.68
2017-06-08 22:30 | 245.66 | 232.36
2017-06-08 23:00 | 243.21 | 229.71
2017-06-08 23:30 | 242.46 | 228.54
2017-06-09 | 240.94 | 226.96
2017-06-09 00:30 | 240.09 | 226.27
2017-06-09 01:00 | 237.98 | 224.15
2017-06-09 01:30 | 235.85 | 223.36
2017-06-09 02:00 | 234.15 | 222.04
2017-06-09 02:30 | 234.35 | 222.39
2017-06-09 03:00 | 233.95 | 222.23
2017-06-09 03:30 | 233.25 | 221.82
2017-06-09 04:00 | 233.49 | 222.43
2017-06-09 04:30 | 234.12 | 223.11
2017-06-09 05:00 | 235.82 | 224.93
2017-06-09 05:30 | 238.2 | 227.52
2017-06-09 06:00 | 242.7 | 231.76
2017-06-09 06:30 | 247.23 | 236.22
2017-06-09 07:00 | 250.61 | 239.94
2017-06-09 07:30 | 254.38 | 243.85
2017-06-09 08:00 | 253.47 | 242.79
2017-06-09 08:30 | 250.36 | 239.21
2017-06-09 09:00 | 245.28 | 233.17
2017-06-09 09:30 | 233.54 | 221.07
2017-06-09 10:00 | 224.76 | 211.74
2017-06-09 10:30 | 233.73 | 219.89
2017-06-09 11:00 | 233.25 | 219.58
2017-06-09 11:30 | 233.55 | 220.12
2017-06-09 12:00 | 232.75 | 219.1
2017-06-09 12:30 | 232.05 | 217.89
2017-06-09 13:00 | 231.97 | 217.67
2017-06-09 13:30 | 231.07 | 216.65
2017-06-09 14:00 | 230.52 | 216
2017-06-09 14:30 | 230.31 | 215.41
2017-06-09 15:00 | 231.58 | 216.71
2017-06-09 15:30 | 232.46 | 217.61
2017-06-09 16:00 | 234.03 | 218.99
2017-06-09 16:30 | 235.51 | 220.67
2017-06-09 17:00 | 237.2 | 222.86
2017-06-09 17:30 | 240.36 | 225.83
2017-06-09 18:00 | 244.99 | 230.9
2017-06-09 18:30 | 247.9 | 234.14
2017-06-09 19:00 | 248.76 | 234.93
2017-06-09 19:30 | 247.53 | 233.48
2017-06-09 20:00 | 246.67 | 232.74
2017-06-09 20:30 | 246.73 | 233.05
2017-06-09 21:00 | 245.94 | 232.35
2017-06-09 21:30 | 244.04 | 231.63
2017-06-09 22:00 | 242.11 | 229.97
2017-06-09 22:30 | 240.24 | 227.82
2017-06-09 23:00 | 239.39 | 226.35
2017-06-09 23:30 | 237.56 | 224.77
2017-06-10 | 236.42 | 223.33
2017-06-10 00:30 | 235.44 | 222.75
2017-06-10 01:00 | 234.03 | 221.44
2017-06-10 01:30 | 233.93 | 221.22
2017-06-10 02:00 | 233.96 | 221.69
2017-06-10 02:30 | 233.35 | 221.01
2017-06-10 03:00 | 232.96 | 220.85
2017-06-10 03:30 | 232.46 | 220.89
2017-06-10 04:00 | 232.58 | 221.26
2017-06-10 04:30 | 233.54 | 222.36
2017-06-10 05:00 | 234.74 | 223.47
2017-06-10 05:30 | 235.85 | 224.58
2017-06-10 06:00 | 238.14 | 226.72
2017-06-10 06:30 | 240.16 | 229.11
2017-06-10 07:00 | 242.34 | 231.09
2017-06-10 07:30 | 243.25 | 231.82
2017-06-10 08:00 | 241.69 | 230.27
2017-06-10 08:30 | 239.39 | 228.25
2017-06-10 09:00 | 237.56 | 226.08
2017-06-10 09:30 | 236.57 | 225.23
2017-06-10 10:00 | 234.33 | 222.67
2017-06-10 10:30 | 231.38 | 219.46
2017-06-10 11:00 | 230.65 | 218.43
2017-06-10 11:30 | 233.32 | 217.14
2017-06-10 12:00 | 232.19 | 216.29
2017-06-10 12:30 | 232.39 | 216.56
2017-06-10 13:00 | 231.67 | 215.73
2017-06-10 13:30 | 231.23 | 215.22
2017-06-10 14:00 | 231.75 | 215.81
2017-06-10 14:30 | 231.9 | 215.98
2017-06-10 15:00 | 234.19 | 215.79
2017-06-10 15:30 | 234.74 | 215.77
2017-06-10 16:00 | 236.1 | 216.88
2017-06-10 16:30 | 237.98 | 219.19
2017-06-10 17:00 | 239.21 | 221.03
2017-06-10 17:30 | 242.93 | 225.39
2017-06-10 18:00 | 247.85 | 231.11
2017-06-10 18:30 | 250 | 233.54
2017-06-10 19:00 | 250.23 | 233.64
2017-06-10 19:30 | 247.13 | 230.79
2017-06-10 20:00 | 246.04 | 229.67
2017-06-10 20:30 | 246.11 | 229.73
2017-06-10 21:00 | 245.04 | 228.35
2017-06-10 21:30 | 243.96 | 227.51
2017-06-10 22:00 | 242.82 | 225.82
2017-06-10 22:30 | 226.76 | 208.71
2017-06-10 23:00 | 219.27 | 201.05
2017-06-10 23:30 | 218.1 | 199.85
2017-06-11 | 216.54 | 198.79
2017-06-11 00:30 | 215.27 | 197.94
2017-06-11 01:00 | 212.96 | 197.49
2017-06-11 01:30 | 213.19 | 197.79
2017-06-11 02:00 | 212.64 | 197.16
2017-06-11 02:30 | 212.62 | 196.62
2017-06-11 03:00 | 211.17 | 195.17
2017-06-11 03:30 | 211.23 | 195.2
2017-06-11 04:00 | 211.18 | 195.39
2017-06-11 04:30 | 211.41 | 195.57
2017-06-11 05:00 | 211.87 | 196.19
2017-06-11 05:30 | 212.7 | 197.12
2017-06-11 06:00 | 214 | 198.4
2017-06-11 06:30 | 215.24 | 199.98
2017-06-11 07:00 | 216.45 | 201.41
2017-06-11 07:30 | 218.01 | 203.57
2017-06-11 08:00 | 218.53 | 204.23
2017-06-11 08:30 | 217.71 | 203.53
2017-06-11 09:00 | 217.02 | 201.13
2017-06-11 09:30 | 214.84 | 198.95
2017-06-11 10:00 | 212.4 | 196.29
2017-06-11 10:30 | 209.53 | 193.21
2017-06-11 11:00 | 207.91 | 191.35
2017-06-11 11:30 | 209.29 | 192.64
2017-06-11 12:00 | 208.79 | 192.23
2017-06-11 12:30 | 208.95 | 192.4
2017-06-11 13:00 | 208.91 | 192.09
2017-06-11 13:30 | 209.26 | 192.17
2017-06-11 14:00 | 208.31 | 191.35
2017-06-11 14:30 | 208.03 | 190.77
2017-06-11 15:00 | 208.77 | 191.51
2017-06-11 15:30 | 209.1 | 191.72
2017-06-11 16:00 | 210.26 | 192.74
2017-06-11 16:30 | 212.69 | 194.92
2017-06-11 17:00 | 215.21 | 196.92
2017-06-11 17:30 | 217.76 | 200.29
2017-06-11 18:00 | 222.91 | 206.06
2017-06-11 18:30 | 226.41 | 209.18
2017-06-11 19:00 | 228.24 | 210.98
2017-06-11 19:30 | 226.37 | 208.64
2017-06-11 20:00 | 223.66 | 205.44
2017-06-11 20:30 | 223.07 | 204.76
2017-06-11 21:00 | 219.84 | 204.48
2017-06-11 21:30 | 216.34 | 202.66
2017-06-11 22:00 | 215.25 | 201.6
2017-06-11 22:30 | 213.81 | 200.21
2017-06-11 23:00 | 211.98 | 198.02
2017-06-11 23:30 | 210.99 | 196.86
2017-06-12 | 209.97 | 195.85
2017-06-12 00:30 | 209.84 | 196.7
2017-06-12 01:00 | 208.81 | 196.05
2017-06-12 01:30 | 208.73 | 196.13
2017-06-12 02:00 | 207.65 | 195.43
2017-06-12 02:30 | 207.29 | 195.25
2017-06-12 03:00 | 207.09 | 195.37
2017-06-12 03:30 | 206.82 | 195.09
2017-06-12 04:00 | 206.95 | 195.27
2017-06-12 04:30 | 208.07 | 196.28
2017-06-12 05:00 | 209.66 | 197.93
2017-06-12 05:30 | 211.34 | 199.6
2017-06-12 06:00 | 215.07 | 203.34
2017-06-12 06:30 | 218.51 | 206.97
2017-06-12 07:00 | 222.35 | 211.23
2017-06-12 07:30 | 225.94 | 214.67
2017-06-12 08:00 | 226.06 | 215.01
2017-06-12 08:30 | 224.55 | 213.56
2017-06-12 09:00 | 221.81 | 210.88
2017-06-12 09:30 | 219.05 | 207.81
2017-06-12 10:00 | 217.47 | 206.08
2017-06-12 10:30 | 215.9 | 204.02
2017-06-12 11:00 | 215.11 | 202.88
2017-06-12 11:30 | 213.96 | 201.58
2017-06-12 12:00 | 212.39 | 199.87
2017-06-12 12:30 | 211.46 | 198.38
2017-06-12 13:00 | 209.83 | 196.57
2017-06-12 13:30 | 211.04 | 197.81
2017-06-12 14:00 | 211.3 | 198.28
2017-06-12 14:30 | 211.43 | 198.59
2017-06-12 15:00 | 212.38 | 199.41
2017-06-12 15:30 | 212.31 | 199.12
2017-06-12 16:00 | 213.16 | 200
2017-06-12 16:30 | 214.27 | 201.13
2017-06-12 17:00 | 216.37 | 203.43
2017-06-12 17:30 | 220.01 | 206.18
2017-06-12 18:00 | 226.04 | 212.66
2017-06-12 18:30 | 229.45 | 216.32
2017-06-12 19:00 | 230.47 | 217.23
2017-06-12 19:30 | 229.03 | 215.34
2017-06-12 20:00 | 226.36 | 212.52
2017-06-12 20:30 | 225.99 | 212.08
2017-06-12 21:00 | 224.54 | 210.15
2017-06-12 21:30 | 221.92 | 208.7
2017-06-12 22:00 | 219.3 | 206.51
2017-06-12 22:30 | 219.52 | 206.24
2017-06-12 23:00 | 217.82 | 204.27
2017-06-12 23:30 | 216.5 | 202.59
2017-06-13 | 215.68 | 201.04
2017-06-13 00:30 | 214.06 | 200.29
2017-06-13 01:00 | 213.04 | 199.46
2017-06-13 01:30 | 211.63 | 198.42
2017-06-13 02:00 | 211.48 | 198.52
2017-06-13 02:30 | 211.1 | 198.04
2017-06-13 03:00 | 210.82 | 197.63
2017-06-13 03:30 | 210.61 | 197.64
2017-06-13 04:00 | 210.6 | 197.9
2017-06-13 04:30 | 211.26 | 198.86
2017-06-13 05:00 | 212.22 | 200.18
2017-06-13 05:30 | 214.53 | 201.82
2017-06-13 06:00 | 218.68 | 205.87
2017-06-13 06:30 | 223.46 | 210.47
2017-06-13 07:00 | 228.18 | 214.27
2017-06-13 07:30 | 230.94 | 216.91
2017-06-13 08:00 | 230.18 | 216.58
2017-06-13 08:30 | 227.22 | 213.68
2017-06-13 09:00 | 224.04 | 210.08
2017-06-13 09:30 | 219.55 | 205.38
2017-06-13 10:00 | 217.49 | 202.76
2017-06-13 10:30 | 216.8 | 201.44
2017-06-13 11:00 | 215.9 | 200.44
2017-06-13 11:30 | 216.45 | 200.91
2017-06-13 12:00 | 213.93 | 198.2
2017-06-13 12:30 | 213.15 | 196.96
2017-06-13 13:00 | 214.02 | 197.91
2017-06-13 13:30 | 214.02 | 197.73
2017-06-13 14:00 | 213.8 | 197.75
2017-06-13 14:30 | 214.01 | 198.07
2017-06-13 15:00 | 215.04 | 198.69
2017-06-13 15:30 | 214.47 | 198.28
2017-06-13 16:00 | 215.48 | 199.59
2017-06-13 16:30 | 217.37 | 201.37
2017-06-13 17:00 | 220.08 | 203.74
2017-06-13 17:30 | 222.33 | 206.64
2017-06-13 18:00 | 216.82 | 206.29
2017-06-13 18:30 | 214.63 | 207.15
2017-06-13 19:00 | 214.52 | 206.93
2017-06-13 19:30 | 215.4 | 207.88
2017-06-13 20:00 | 216.63 | 209.38
2017-06-13 20:30 | 216.42 | 209.48
2017-06-13 21:00 | 221.56 | 207.85
2017-06-13 21:30 | 224.15 | 209.61
2017-06-13 22:00 | 220.51 | 205.99
2017-06-13 22:30 | 217.86 | 203.36
2017-06-13 23:00 | 215.98 | 201.46
2017-06-13 23:30 | 215.48 | 200.4
2017-06-14 | 215.19 | 198.95
2017-06-14 00:30 | 213.43 | 198.17
2017-06-14 01:00 | 212.25 | 196.8
2017-06-14 01:30 | 211.58 | 196.3
2017-06-14 02:00 | 211.31 | 195.67
2017-06-14 02:30 | 210.49 | 194.83
2017-06-14 03:00 | 210.28 | 194.61
2017-06-14 03:30 | 210.85 | 195.1
2017-06-14 04:00 | 211.27 | 195.86
2017-06-14 04:30 | 212.16 | 196.84
2017-06-14 05:00 | 213.62 | 198.94
2017-06-14 05:30 | 215.61 | 201.37
2017-06-14 06:00 | 220.37 | 205.87
2017-06-14 06:30 | 224 | 210.75
2017-06-14 07:00 | 227.52 | 214.53
2017-06-14 07:30 | 229.55 | 216.58
2017-06-14 08:00 | 228.95 | 215.79
2017-06-14 08:30 | 225.62 | 211.96
2017-06-14 09:00 | 221.45 | 207.6
2017-06-14 09:30 | 217.91 | 203.31
2017-06-14 10:00 | 217.07 | 202.48
2017-06-14 10:30 | 215.43 | 200.25
2017-06-14 11:00 | 214.21 | 198.87
2017-06-14 11:30 | 210.78 | 195.35
2017-06-14 12:00 | 209.5 | 194.19
2017-06-14 12:30 | 208.57 | 193.29
2017-06-14 13:00 | 208.79 | 193.15
2017-06-14 13:30 | 208.69 | 193.17
2017-06-14 14:00 | 208.65 | 193.42
2017-06-14 14:30 | 208.54 | 193.77
2017-06-14 15:00 | 208.8 | 194.21
2017-06-14 15:30 | 210.23 | 195.87
2017-06-14 16:00 | 211.21 | 196.71
2017-06-14 16:30 | 212.9 | 198.05
2017-06-14 17:00 | 214.88 | 199.46
2017-06-14 17:30 | 215.96 | 200.2
2017-06-14 18:00 | 222.27 | 207.18
2017-06-14 18:30 | 225.58 | 210.49
2017-06-14 19:00 | 226.59 | 211.47
2017-06-14 19:30 | 226.02 | 210.38
2017-06-14 20:00 | 223.97 | 208.5
2017-06-14 20:30 | 223.45 | 207.99
2017-06-14 21:00 | 221.1 | 205.58
2017-06-14 21:30 | 218.67 | 204.45
2017-06-14 22:00 | 217.69 | 203.17
2017-06-14 22:30 | 216.22 | 201.43
2017-06-14 23:00 | 214.02 | 199.09
2017-06-14 23:30 | 212.24 | 197.78
2017-06-15 | 210.78 | 196.03
2017-06-15 00:30 | 210.46 | 195.49
2017-06-15 01:00 | 210.1 | 194.86
2017-06-15 01:30 | 209.64 | 194.68
2017-06-15 02:00 | 209.12 | 194.77
2017-06-15 02:30 | 209.37 | 195.07
2017-06-15 03:00 | 209.74 | 195.26
2017-06-15 03:30 | 209.93 | 195.26
2017-06-15 04:00 | 210.04 | 195.65
2017-06-15 04:30 | 210.62 | 196.44
2017-06-15 05:00 | 212.22 | 198.25
2017-06-15 05:30 | 214.78 | 200.88
2017-06-15 06:00 | 218.14 | 204.17
2017-06-15 06:30 | 222.13 | 208.83
2017-06-15 07:00 | 225.09 | 211.97
2017-06-15 07:30 | 227.62 | 214.72
2017-06-15 08:00 | 226.12 | 213.31
2017-06-15 08:30 | 221.33 | 208.18
2017-06-15 09:00 | 217.91 | 204.35
2017-06-15 09:30 | 215.06 | 200.94
2017-06-15 10:00 | 213.67 | 199.14
2017-06-15 10:30 | 211.48 | 196.25
2017-06-15 11:00 | 208.74 | 193.69
2017-06-15 11:30 | 207.37 | 192.54
2017-06-15 12:00 | 207.57 | 192.83
2017-06-15 12:30 | 207.28 | 192.38
2017-06-15 13:00 | 206.03 | 190.73
2017-06-15 13:30 | 205.92 | 190.52
2017-06-15 14:00 | 205.88 | 190.72
2017-06-15 14:30 | 207.55 | 193.11
2017-06-15 15:00 | 207.83 | 193.36
2017-06-15 15:30 | 208.68 | 194.45
2017-06-15 16:00 | 208.48 | 194.74
2017-06-15 16:30 | 210.33 | 196.51
2017-06-15 17:00 | 212.23 | 197.96
2017-06-15 17:30 | 214.7 | 200.34
2017-06-15 18:00 | 220.88 | 206.86
2017-06-15 18:30 | 223.63 | 210.13
2017-06-15 19:00 | 223.8 | 210.48
2017-06-15 19:30 | 221.43 | 207.52
2017-06-15 20:00 | 220.54 | 206.77
2017-06-15 20:30 | 221.2 | 207.28
2017-06-15 21:00 | 220.71 | 206.48
2017-06-15 21:30 | 219.81 | 206.35
2017-06-15 22:00 | 219.58 | 205.91
2017-06-15 22:30 | 217.29 | 203.22
2017-06-15 23:00 | 215.85 | 201.53
2017-06-15 23:30 | 215.57 | 201.15
2017-06-16 | 214.25 | 200.47
2017-06-16 00:30 | 213.65 | 200
2017-06-16 01:00 | 211.69 | 197.98
2017-06-16 01:30 | 210.34 | 196.59
2017-06-16 02:00 | 210.85 | 196.91
2017-06-16 02:30 | 210.97 | 197.01
2017-06-16 03:00 | 211.18 | 196.92
2017-06-16 03:30 | 211.03 | 197.01
2017-06-16 04:00 | 211.87 | 197.95
2017-06-16 04:30 | 212.83 | 198.38
2017-06-16 05:00 | 214.09 | 199.67
2017-06-16 05:30 | 215.97 | 201.84
2017-06-16 06:00 | 219.26 | 205.29
2017-06-16 06:30 | 222.53 | 209.11
2017-06-16 07:00 | 225.65 | 212.21
2017-06-16 07:30 | 227.41 | 214.54
2017-06-16 08:00 | 226.62 | 214.22
2017-06-16 08:30 | 223.88 | 211.24
2017-06-16 09:00 | 220.56 | 206.91
2017-06-16 09:30 | 217.27 | 203.06
2017-06-16 10:00 | 214.21 | 199.9
2017-06-16 10:30 | 212.59 | 197.42
2017-06-16 11:00 | 210.94 | 195.58
2017-06-16 11:30 | 209.59 | 193.73
2017-06-16 12:00 | 209.69 | 193.65
2017-06-16 12:30 | 209.11 | 192.74
2017-06-16 13:00 | 209.06 | 192.59
2017-06-16 13:30 | 208.75 | 191.56
2017-06-16 14:00 | 208.99 | 191.81
2017-06-16 14:30 | 208.95 | 191.88
2017-06-16 15:00 | 209.39 | 192.13
2017-06-16 15:30 | 210.14 | 192.75
2017-06-16 16:00 | 211.75 | 194.55
2017-06-16 16:30 | 212.32 | 195.62
2017-06-16 17:00 | 214.59 | 198.35
2017-06-16 17:30 | 214.53 | 198.31
2017-06-16 18:00 | 219.48 | 203.47
2017-06-16 18:30 | 223.38 | 206.92
2017-06-16 19:00 | 223.46 | 206.93
2017-06-16 19:30 | 222.18 | 205.26
2017-06-16 20:00 | 221.95 | 205.04
2017-06-16 20:30 | 221.36 | 204.84
2017-06-16 21:00 | 220.47 | 203.56
2017-06-16 21:30 | 218.9 | 203.18
2017-06-16 22:00 | 218.23 | 202.95
2017-06-16 22:30 | 216 | 200.71
2017-06-16 23:00 | 214.34 | 198.62
2017-06-16 23:30 | 213.71 | 198.23
2017-06-17 | 213.82 | 197.61
2017-06-17 00:30 | 212.9 | 197.12
2017-06-17 01:00 | 210.98 | 196.17
2017-06-17 01:30 | 209.38 | 195.53
2017-06-17 02:00 | 207.78 | 194.97
2017-06-17 02:30 | 207.17 | 194.38
2017-06-17 03:00 | 207.08 | 194.5
2017-06-17 03:30 | 206.79 | 194.73
2017-06-17 04:00 | 206.75 | 194.47
2017-06-17 04:30 | 207.82 | 195.51
2017-06-17 05:00 | 208.64 | 196.4
2017-06-17 05:30 | 209.01 | 196.96
2017-06-17 06:00 | 210.47 | 198.43
2017-06-17 06:30 | 212.46 | 199.51
2017-06-17 07:00 | 214.44 | 201.53
2017-06-17 07:30 | 216.59 | 203.33
2017-06-17 08:00 | 218.05 | 203.44
2017-06-17 08:30 | 216.71 | 201.98
2017-06-17 09:00 | 217.3 | 201.69
2017-06-17 09:30 | 215.83 | 200.25
2017-06-17 10:00 | 213.27 | 197.83
2017-06-17 10:30 | 211.15 | 195.49
2017-06-17 11:00 | 210.34 | 194.6
2017-06-17 11:30 | 209.65 | 193.95
2017-06-17 12:00 | 207.65 | 191.91
2017-06-17 12:30 | 207.14 | 192.03
2017-06-17 13:00 | 206.33 | 190.89
2017-06-17 13:30 | 206.69 | 190.94
2017-06-17 14:00 | 205.19 | 189.35
2017-06-17 14:30 | 204.64 | 188.98
2017-06-17 15:00 | 205.25 | 189.26
2017-06-17 15:30 | 204.34 | 188.4
2017-06-17 16:00 | 205 | 189.15
2017-06-17 16:30 | 207.49 | 191.39
2017-06-17 17:00 | 208.96 | 193.06
2017-06-17 17:30 | 211.3 | 195.7
2017-06-17 18:00 | 216.23 | 200.43
2017-06-17 18:30 | 219.05 | 203.16
2017-06-17 19:00 | 219.3 | 203.15
2017-06-17 19:30 | 218.99 | 202.63
2017-06-17 20:00 | 218.34 | 201.97
2017-06-17 20:30 | 218.34 | 201.76
2017-06-17 21:00 | 216.64 | 200.35
2017-06-17 21:30 | 215.55 | 200.29
2017-06-17 22:00 | 214.5 | 199.85
2017-06-17 22:30 | 213.57 | 198.95
2017-06-17 23:00 | 212.91 | 198.02
2017-06-17 23:30 | 212.03 | 197.21
2017-06-18 | 212 | 197.13
2017-06-18 00:30 | 213.67 | 200.03
2017-06-18 01:00 | 211.57 | 198.46
2017-06-18 01:30 | 210.65 | 198.06
2017-06-18 02:00 | 209.9 | 197.79
2017-06-18 02:30 | 210.46 | 197.93
2017-06-18 03:00 | 210.15 | 197.69
2017-06-18 03:30 | 210.18 | 197.75
2017-06-18 04:00 | 209.47 | 198.27
2017-06-18 04:30 | 209.71 | 199.14
2017-06-18 05:00 | 210.17 | 199.72
2017-06-18 05:30 | 210.9 | 200.39
2017-06-18 06:00 | 213.42 | 201.66
2017-06-18 06:30 | 215.21 | 203.59
2017-06-18 07:00 | 217.28 | 205.66
2017-06-18 07:30 | 218.86 | 207.79
2017-06-18 08:00 | 219.78 | 208.45
2017-06-18 08:30 | 218.97 | 207.4
2017-06-18 09:00 | 217.96 | 206.25
2017-06-18 09:30 | 214.68 | 202.63
2017-06-18 10:00 | 211.54 | 199.2
2017-06-18 10:30 | 208.72 | 195.82
2017-06-18 11:00 | 207.16 | 194.29
2017-06-18 11:30 | 205.9 | 193.31
2017-06-18 12:00 | 204.64 | 191.8
2017-06-18 12:30 | 203.89 | 190.91
2017-06-18 13:00 | 203.53 | 190.65
2017-06-18 13:30 | 203.4 | 190.64
2017-06-18 14:00 | 202.73 | 189.71
2017-06-18 14:30 | 202.52 | 189.72
2017-06-18 15:00 | 202.94 | 189.98
2017-06-18 15:30 | 204.18 | 190.8
2017-06-18 16:00 | 205.54 | 191.77
2017-06-18 16:30 | 207.88 | 193.45
2017-06-18 17:00 | 210.2 | 196.18
2017-06-18 17:30 | 212.8 | 199.11
2017-06-18 18:00 | 219.31 | 205.69
2017-06-18 18:30 | 222.62 | 209
2017-06-18 19:00 | 223.38 | 209.54
2017-06-18 19:30 | 222.69 | 208.54
2017-06-18 20:00 | 221.33 | 206.77
2017-06-18 20:30 | 220.7 | 205.92
2017-06-18 21:00 | 219.73 | 204.48
2017-06-18 21:30 | 218.42 | 203.97
2017-06-18 22:00 | 216.7 | 202.94
2017-06-18 22:30 | 214.75 | 200.61
2017-06-18 23:00 | 213.37 | 198.88
2017-06-18 23:30 | 212.86 | 198.28
2017-06-19 | 211.88 | 197.38
2017-06-19 00:30 | 210.13 | 197.09
2017-06-19 01:00 | 209.54 | 196.84
2017-06-19 01:30 | 209.21 | 197.07
2017-06-19 02:00 | 209.18 | 197.14
2017-06-19 02:30 | 209.26 | 197.12
2017-06-19 03:00 | 208.97 | 196.69
2017-06-19 03:30 | 209.71 | 197.7
2017-06-19 04:00 | 210.24 | 198.48
2017-06-19 04:30 | 211.27 | 199.72
2017-06-19 05:00 | 212.2 | 200.9
2017-06-19 05:30 | 214.95 | 203.76
2017-06-19 06:00 | 219.48 | 206.76
2017-06-19 06:30 | 224.33 | 211.56
2017-06-19 07:00 | 228.9 | 216.4
2017-06-19 07:30 | 232.02 | 219.65
2017-06-19 08:00 | 232.79 | 218.8
2017-06-19 08:30 | 226.15 | 214.08
2017-06-19 09:00 | 222.51 | 209.59
2017-06-19 09:30 | 219.36 | 206
2017-06-19 10:00 | 217.32 | 203.59
2017-06-19 10:30 | 214.52 | 199.98
2017-06-19 11:00 | 214.82 | 200.81
2017-06-19 11:30 | 213.19 | 199.45
2017-06-19 12:00 | 212.12 | 198.53
2017-06-19 12:30 | 211.25 | 197.15
2017-06-19 13:00 | 211.57 | 197.03
2017-06-19 13:30 | 210.34 | 196.2
2017-06-19 14:00 | 209.36 | 195.7
2017-06-19 14:30 | 208.64 | 195.41
2017-06-19 15:00 | 209.67 | 195.9
2017-06-19 15:30 | 210.33 | 196.61
2017-06-19 16:00 | 212.03 | 199.02
2017-06-19 16:30 | 213.43 | 200.46
2017-06-19 17:00 | 215.8 | 202.19
2017-06-19 17:30 | 218.82 | 205.05
2017-06-19 18:00 | 223.66 | 209.86
2017-06-19 18:30 | 228.28 | 214.54
2017-06-19 19:00 | 229.57 | 215.84
2017-06-19 19:30 | 229.05 | 215.19
2017-06-19 20:00 | 227.29 | 213.37
2017-06-19 20:30 | 226.96 | 213.08
2017-06-19 21:00 | 225.21 | 211.16
2017-06-19 21:30 | 222.53 | 209.84
2017-06-19 22:00 | 220.62 | 208.67
2017-06-19 22:30 | 218.14 | 206.86
2017-06-19 23:00 | 216.67 | 205.58
2017-06-19 23:30 | 215.52 | 204.25
2017-06-20 | 213.7 | 202.41
2017-06-20 00:30 | 211.28 | 200.07
2017-06-20 01:00 | 210.22 | 199
2017-06-20 01:30 | 209.63 | 198.94
2017-06-20 02:00 | 209.64 | 199.32
2017-06-20 02:30 | 209.34 | 198.64
2017-06-20 03:00 | 208.84 | 196.1
2017-06-20 03:30 | 208.45 | 194.78
2017-06-20 04:00 | 207.92 | 194.74
2017-06-20 04:30 | 208.76 | 195.52
2017-06-20 05:00 | 210.36 | 197.12
2017-06-20 05:30 | 213.03 | 199.91
2017-06-20 06:00 | 217.13 | 204.06
2017-06-20 06:30 | 221.64 | 208.98
2017-06-20 07:00 | 225.81 | 213.15
2017-06-20 07:30 | 228.44 | 216.12
2017-06-20 08:00 | 228.65 | 215.68
2017-06-20 08:30 | 224.02 | 210.86
2017-06-20 09:00 | 221.96 | 208.65
2017-06-20 09:30 | 219.24 | 205.65
2017-06-20 10:00 | 217.53 | 203.45
2017-06-20 10:30 | 215.13 | 200.3
2017-06-20 11:00 | 216.01 | 201.28
2017-06-20 11:30 | 214.74 | 199.48
2017-06-20 12:00 | 213.5 | 197.77
2017-06-20 12:30 | 214.79 | 198.51
2017-06-20 13:00 | 213.89 | 197.51
2017-06-20 13:30 | 212.31 | 195.58
2017-06-20 14:00 | 211.19 | 194.92
2017-06-20 14:30 | 210.89 | 195.2
2017-06-20 15:00 | 210.71 | 194.83
2017-06-20 15:30 | 211.35 | 195.43
2017-06-20 16:00 | 212.17 | 196.88
2017-06-20 16:30 | 210.72 | 194.89
2017-06-20 17:00 | 209.83 | 193.7
2017-06-20 17:30 | 212.34 | 196.59
2017-06-20 18:00 | 218.56 | 203.33
2017-06-20 18:30 | 222.54 | 207.81
2017-06-20 19:00 | 223.12 | 208.44
2017-06-20 19:30 | 222.47 | 207.79
2017-06-20 20:00 | 220.48 | 205.8
2017-06-20 20:30 | 219.88 | 204.92
2017-06-20 21:00 | 219.5 | 204.12
2017-06-20 21:30 | 219.05 | 204.23
2017-06-20 22:00 | 218.11 | 203.76
2017-06-20 22:30 | 216.24 | 201.75
2017-06-20 23:00 | 216.04 | 200.81
2017-06-20 23:30 | 214.93 | 199.82
2017-06-21 | 213.13 | 199.11
2017-06-21 00:30 | 212.85 | 199.63
2017-06-21 01:00 | 210.64 | 197.85
2017-06-21 01:30 | 209.17 | 197.09
2017-06-21 02:00 | 208.15 | 196.59
2017-06-21 02:30 | 208 | 196.29
2017-06-21 03:00 | 207.65 | 195.98
2017-06-21 03:30 | 208.11 | 196.59
2017-06-21 04:00 | 208.49 | 196.92
2017-06-21 04:30 | 209.24 | 198.12
2017-06-21 05:00 | 211.2 | 200.29
2017-06-21 05:30 | 214.36 | 203.18
2017-06-21 06:00 | 219.01 | 207.67
2017-06-21 06:30 | 224.99 | 213.79
2017-06-21 07:00 | 229.13 | 217.66
2017-06-21 07:30 | 232.95 | 221.19
2017-06-21 08:00 | 232.65 | 220.76
2017-06-21 08:30 | 229.38 | 217.24
2017-06-21 09:00 | 221.26 | 208.26
2017-06-21 09:30 | 215.98 | 202.68
2017-06-21 10:00 | 215.72 | 202.33
2017-06-21 10:30 | 213.61 | 199.93
2017-06-21 11:00 | 211.88 | 198.4
2017-06-21 11:30 | 211.38 | 197.86
2017-06-21 12:00 | 212.05 | 198.58
2017-06-21 12:30 | 211.86 | 197.7
2017-06-21 13:00 | 210.67 | 196.19
2017-06-21 13:30 | 211.25 | 196.6
2017-06-21 14:00 | 211.15 | 196.75
2017-06-21 14:30 | 211.27 | 198.41
2017-06-21 15:00 | 209.2 | 196.14
2017-06-21 15:30 | 208.56 | 194.99
2017-06-21 16:00 | 210.23 | 196.64
2017-06-21 16:30 | 211.94 | 198.39
2017-06-21 17:00 | 213.6 | 199.77
2017-06-21 17:30 | 227.21 | 213.69
2017-06-21 18:00 | 243.46 | 230.49
2017-06-21 18:30 | 247.13 | 234.76
2017-06-21 19:00 | 244.91 | 234.08
2017-06-21 19:30 | 241.97 | 230.98
2017-06-21 20:00 | 239.2 | 228.29
2017-06-21 20:30 | 239.9 | 228.66
2017-06-21 21:00 | 239.1 | 227.3
2017-06-21 21:30 | 239.22 | 228.5
2017-06-21 22:00 | 238.69 | 227.81
2017-06-21 22:30 | 236.62 | 225.46
2017-06-21 23:00 | 234.67 | 222.92
2017-06-21 23:30 | 233.24 | 221.31
2017-06-22 | 231.69 | 219.81
2017-06-22 00:30 | 230.05 | 218.65
2017-06-22 01:00 | 228.45 | 217.82
2017-06-22 01:30 | 227.82 | 216.78
2017-06-22 02:00 | 214.23 | 202.98
2017-06-22 02:30 | 206.15 | 194.43
2017-06-22 03:00 | 205.98 | 194.1
2017-06-22 03:30 | 206.06 | 194.67
2017-06-22 04:00 | 206.84 | 195.78
2017-06-22 04:30 | 207.92 | 196.95
2017-06-22 05:00 | 210.26 | 199.33
2017-06-22 05:30 | 213.2 | 202.41
2017-06-22 06:00 | 217.46 | 206.97
2017-06-22 06:30 | 236.83 | 227.03
2017-06-22 07:00 | 244.43 | 235.36
2017-06-22 07:30 | 248.22 | 239.1
2017-06-22 08:00 | 246.38 | 237.5
2017-06-22 08:30 | 243.77 | 233.97
2017-06-22 09:00 | 241.64 | 230.46
2017-06-22 09:30 | 238.46 | 226.47
2017-06-22 10:00 | 236.21 | 223.69
2017-06-22 10:30 | 233.22 | 220.24
2017-06-22 11:00 | 229 | 215.84
2017-06-22 11:30 | 230.85 | 217.28
2017-06-22 12:00 | 233.33 | 219.21
2017-06-22 12:30 | 231.67 | 217.2
2017-06-22 13:00 | 232.15 | 217.41
2017-06-22 13:30 | 231.68 | 216.86
2017-06-22 14:00 | 231.43 | 216.83
2017-06-22 14:30 | 231.44 | 217.05
2017-06-22 15:00 | 232.16 | 217.87
2017-06-22 15:30 | 232.75 | 218.43
2017-06-22 16:00 | 233.05 | 218.84
2017-06-22 16:30 | 234.39 | 220.17
2017-06-22 17:00 | 235.95 | 221.71
2017-06-22 17:30 | 239.59 | 225.43
2017-06-22 18:00 | 245.07 | 231.71
2017-06-22 18:30 | 248.3 | 235.42
2017-06-22 19:00 | 247.61 | 234.87
2017-06-22 19:30 | 245.52 | 232.49
2017-06-22 20:00 | 245.42 | 232.28
2017-06-22 20:30 | 245.41 | 232.26
2017-06-22 21:00 | 243.48 | 230.34
2017-06-22 21:30 | 242.61 | 230.08
2017-06-22 22:00 | 240.7 | 228.07
2017-06-22 22:30 | 237.23 | 224.69
2017-06-22 23:00 | 235.04 | 222.17
2017-06-22 23:30 | 233.64 | 220.84
2017-06-23 | 233.25 | 220.34
2017-06-23 00:30 | 232.45 | 219.86
2017-06-23 01:00 | 230.83 | 218.22
2017-06-23 01:30 | 230.46 | 217.6
2017-06-23 02:00 | 230.25 | 217.51
2017-06-23 02:30 | 230.39 | 217.81
2017-06-23 03:00 | 230.89 | 218.23
2017-06-23 03:30 | 229.93 | 217.92
2017-06-23 04:00 | 230.14 | 218.12
2017-06-23 04:30 | 230.21 | 218.51
2017-06-23 05:00 | 231.68 | 220.19
2017-06-23 05:30 | 234.01 | 222.52
2017-06-23 06:00 | 237.42 | 226.5
2017-06-23 06:30 | 241.45 | 230.97
2017-06-23 07:00 | 246.04 | 234.94
2017-06-23 07:30 | 248.82 | 238.2
2017-06-23 08:00 | 248.1 | 237.52
2017-06-23 08:30 | 244.15 | 233.18
2017-06-23 09:00 | 238.65 | 227.1
2017-06-23 09:30 | 233.86 | 221.66
2017-06-23 10:00 | 230.14 | 217.34
2017-06-23 10:30 | 228.52 | 215.04
2017-06-23 11:00 | 228.23 | 214
2017-06-23 11:30 | 231.26 | 216.77
2017-06-23 12:00 | 230.85 | 216.04
2017-06-23 12:30 | 229.96 | 214.51
2017-06-23 13:00 | 230.48 | 214.33
2017-06-23 13:30 | 230.47 | 214.32
2017-06-23 14:00 | 229.66 | 213.66
2017-06-23 14:30 | 229.55 | 213.78
2017-06-23 15:00 | 229.68 | 213.71
2017-06-23 15:30 | 230.19 | 214.15
2017-06-23 16:00 | 230.78 | 214.84
2017-06-23 16:30 | 231.7 | 215.83
2017-06-23 17:00 | 233.03 | 217.46
2017-06-23 17:30 | 234.78 | 219.61
2017-06-23 18:00 | 239.75 | 225.2
2017-06-23 18:30 | 243.18 | 228.76
2017-06-23 19:00 | 244.04 | 229.76
2017-06-23 19:30 | 243.85 | 229.45
2017-06-23 20:00 | 243.78 | 229.28
2017-06-23 20:30 | 240.63 | 226.64
2017-06-23 21:00 | 239.18 | 224.97
2017-06-23 21:30 | 237.6 | 223.89
2017-06-23 22:00 | 236.6 | 222.65
2017-06-23 22:30 | 234.49 | 220.16
2017-06-23 23:00 | 233.23 | 218.75
2017-06-23 23:30 | 232.94 | 218.28
2017-06-24 | 214.75 | 201.02
2017-06-24 00:30 | 207.45 | 194.08
2017-06-24 01:00 | 206.21 | 193.42
2017-06-24 01:30 | 205.39 | 192.76
2017-06-24 02:00 | 195.76 | 183.42
2017-06-24 02:30 | 163.37 | 151.59
2017-06-24 03:00 | 163.07 | 151.25
2017-06-24 03:30 | 162.78 | 151.17
2017-06-24 04:00 | 166.06 | 154.65
2017-06-24 04:30 | 184.85 | 173.37
2017-06-24 05:00 | 197.11 | 185.45
2017-06-24 05:30 | 205.3 | 193.47
2017-06-24 06:00 | 220.9 | 209.4
2017-06-24 06:30 | 232.23 | 220.37
2017-06-24 07:00 | 234.77 | 222.74
2017-06-24 07:30 | 237.27 | 225.01
2017-06-24 08:00 | 239.13 | 226.3
2017-06-24 08:30 | 237.64 | 224.68
2017-06-24 09:00 | 235.09 | 221.68
2017-06-24 09:30 | 231.26 | 217.67
2017-06-24 10:00 | 229.52 | 215.48
2017-06-24 10:30 | 230.81 | 216.54
2017-06-24 11:00 | 230.62 | 216.03
2017-06-24 11:30 | 231.12 | 216.75
2017-06-24 12:00 | 231.36 | 216.85
2017-06-24 12:30 | 230.94 | 216.16
2017-06-24 13:00 | 231.24 | 216.5
2017-06-24 13:30 | 230.96 | 216.14
2017-06-24 14:00 | 230.31 | 215.94
2017-06-24 14:30 | 230.04 | 215.77
2017-06-24 15:00 | 230.44 | 216.05
2017-06-24 15:30 | 224.29 | 209.71
2017-06-24 16:00 | 231.74 | 217.19
2017-06-24 16:30 | 233.09 | 218.66
2017-06-24 17:00 | 234.3 | 219.76
2017-06-24 17:30 | 237.36 | 222.75
2017-06-24 18:00 | 241.82 | 227.86
2017-06-24 18:30 | 244.79 | 231.04
2017-06-24 19:00 | 245.13 | 231.28
2017-06-24 19:30 | 244.98 | 230.85
2017-06-24 20:00 | 244.73 | 230.49
2017-06-24 20:30 | 242.67 | 228.67
2017-06-24 21:00 | 239.77 | 225.42
2017-06-24 21:30 | 238.81 | 224.59
2017-06-24 22:00 | 237.6 | 223.44
2017-06-24 22:30 | 236.38 | 221.94
2017-06-24 23:00 | 234.35 | 219.57
2017-06-24 23:30 | 234.63 | 220.31
2017-06-25 | 232.86 | 219.14
2017-06-25 00:30 | 231.27 | 218.17
2017-06-25 01:00 | 229.99 | 217.35
2017-06-25 01:30 | 213.07 | 200.51
2017-06-25 02:00 | 207.03 | 194.42
2017-06-25 02:30 | 208.41 | 196.03
2017-06-25 03:00 | 209.07 | 196.67
2017-06-25 03:30 | 208.91 | 196.7
2017-06-25 04:00 | 210.41 | 196.88
2017-06-25 04:30 | 212.9 | 197.94
2017-06-25 05:00 | 212.57 | 196.92
2017-06-25 05:30 | 213.58 | 198.16
2017-06-25 06:00 | 215.45 | 200.18
2017-06-25 06:30 | 217.24 | 202.28
2017-06-25 07:00 | 219.45 | 204.79
2017-06-25 07:30 | 218.98 | 204.36
2017-06-25 08:00 | 218.36 | 203.3
2017-06-25 08:30 | 217.73 | 202.84
2017-06-25 09:00 | 216.21 | 200.93
2017-06-25 09:30 | 213.17 | 197.43
2017-06-25 10:00 | 212.28 | 196.16
2017-06-25 10:30 | 212.21 | 195.9
2017-06-25 11:00 | 211.27 | 195.05
2017-06-25 11:30 | 210.06 | 194.1
2017-06-25 12:00 | 209.99 | 193.23
2017-06-25 12:30 | 209.98 | 192.9
2017-06-25 13:00 | 209.47 | 192.18
2017-06-25 13:30 | 208.92 | 191.53
2017-06-25 14:00 | 208.53 | 191.32
2017-06-25 14:30 | 209.02 | 191.85
2017-06-25 15:00 | 209.61 | 192.62
2017-06-25 15:30 | 211.1 | 193.85
2017-06-25 16:00 | 211.74 | 194.4
2017-06-25 16:30 | 230.06 | 213.33
2017-06-25 17:00 | 235.5 | 219
2017-06-25 17:30 | 238.39 | 222.17
2017-06-25 18:00 | 243.18 | 227.18
2017-06-25 18:30 | 246.29 | 230.38
2017-06-25 19:00 | 246.83 | 231.04
2017-06-25 19:30 | 248.55 | 233.11
2017-06-25 20:00 | 248.81 | 233.11
2017-06-25 20:30 | 248.13 | 231.96
2017-06-25 21:00 | 247.56 | 231.14
2017-06-25 21:30 | 246.88 | 230.82
2017-06-25 22:00 | 245.74 | 229.33
2017-06-25 22:30 | 243.88 | 227.1
2017-06-25 23:00 | 241.14 | 224.55
2017-06-25 23:30 | 240.07 | 223.55
2017-06-26 | 237.26 | 219.82
2017-06-26 00:30 | 234.52 | 218.77
2017-06-26 01:00 | 231.8 | 217.14
2017-06-26 01:30 | 215.35 | 200.23
2017-06-26 02:00 | 209.83 | 194.39
2017-06-26 02:30 | 211.18 | 195.77
2017-06-26 03:00 | 210.72 | 195.24
2017-06-26 03:30 | 210.25 | 194.92
2017-06-26 04:00 | 210.46 | 195.51
2017-06-26 04:30 | 211 | 195.93
2017-06-26 05:00 | 212.76 | 197.86
2017-06-26 05:30 | 215.61 | 200.97
2017-06-26 06:00 | 218.39 | 204.1
2017-06-26 06:30 | 236.58 | 223.61
2017-06-26 07:00 | 243.47 | 231.09
2017-06-26 07:30 | 246.13 | 233.46
2017-06-26 08:00 | 245.37 | 231.91
2017-06-26 08:30 | 243.19 | 229.46
2017-06-26 09:00 | 240.61 | 226.39
2017-06-26 09:30 | 235.43 | 220.66
2017-06-26 10:00 | 232.53 | 216.77
2017-06-26 10:30 | 233.96 | 218.03
2017-06-26 11:00 | 233.09 | 217.34
2017-06-26 11:30 | 231.72 | 216.63
2017-06-26 12:00 | 231.53 | 216.68
2017-06-26 12:30 | 231.93 | 216.39
2017-06-26 13:00 | 232.45 | 215.72
2017-06-26 13:30 | 233.16 | 215.8
2017-06-26 14:00 | 232.94 | 215.26
2017-06-26 14:30 | 232.62 | 215.36
2017-06-26 15:00 | 233.5 | 216.04
2017-06-26 15:30 | 234.92 | 217.22
2017-06-26 16:00 | 234.54 | 217.14
2017-06-26 16:30 | 236.2 | 218.51
2017-06-26 17:00 | 238.19 | 220.45
2017-06-26 17:30 | 241.26 | 223.25
2017-06-26 18:00 | 246.83 | 229.66
2017-06-26 18:30 | 250.79 | 233.95
2017-06-26 19:00 | 251.56 | 234.73
2017-06-26 19:30 | 250.82 | 233.77
2017-06-26 20:00 | 249.94 | 232.44
2017-06-26 20:30 | 249.01 | 231.5
2017-06-26 21:00 | 247.58 | 229.9
2017-06-26 21:30 | 245.61 | 229.15
2017-06-26 22:00 | 243.95 | 227.4
2017-06-26 22:30 | 241.91 | 225.68
2017-06-26 23:00 | 239.2 | 222.77
2017-06-26 23:30 | 238.4 | 221.83
2017-06-27 | 235.56 | 220.06
2017-06-27 00:30 | 234.55 | 220.04
2017-06-27 01:00 | 231.42 | 216.96
2017-06-27 01:30 | 230.25 | 215.56
2017-06-27 02:00 | 230.45 | 215.67
2017-06-27 02:30 | 213.86 | 198.63
2017-06-27 03:00 | 209.01 | 193.43
2017-06-27 03:30 | 208.38 | 192.95
2017-06-27 04:00 | 208.38 | 193.12
2017-06-27 04:30 | 208.12 | 192.77
2017-06-27 05:00 | 209.29 | 194.12
2017-06-27 05:30 | 210.94 | 196.13
2017-06-27 06:00 | 214.9 | 199.34
2017-06-27 06:30 | 233.2 | 218.78
2017-06-27 07:00 | 239.81 | 225.67
2017-06-27 07:30 | 242.67 | 228.57
2017-06-27 08:00 | 243.17 | 229.25
2017-06-27 08:30 | 240.92 | 227.25
2017-06-27 09:00 | 238.46 | 224.49
2017-06-27 09:30 | 235.85 | 221.49
2017-06-27 10:00 | 234.14 | 219.21
2017-06-27 10:30 | 235.72 | 220.73
2017-06-27 11:00 | 235.69 | 220.34
2017-06-27 11:30 | 235.16 | 219.42
2017-06-27 12:00 | 233.96 | 218.28
2017-06-27 12:30 | 233.69 | 217.72
2017-06-27 13:00 | 234.46 | 218.01
2017-06-27 13:30 | 233.53 | 216.89
2017-06-27 14:00 | 232.51 | 216.3
2017-06-27 14:30 | 232.12 | 216.48
2017-06-27 15:00 | 232.32 | 216.81
2017-06-27 15:30 | 233.22 | 217.91
2017-06-27 16:00 | 233.57 | 218.36
2017-06-27 16:30 | 234.08 | 218.65
2017-06-27 17:00 | 235.77 | 220.13
2017-06-27 17:30 | 238.93 | 222.62
2017-06-27 18:00 | 243.1 | 227.02
2017-06-27 18:30 | 246.18 | 230.15
2017-06-27 19:00 | 246.83 | 230.68
2017-06-27 19:30 | 245.58 | 229.15
2017-06-27 20:00 | 245.17 | 228.38
2017-06-27 20:30 | 244.75 | 227.69
2017-06-27 21:00 | 243.53 | 226.07
2017-06-27 21:30 | 241.74 | 225.06
2017-06-27 22:00 | 240.29 | 223.4
2017-06-27 22:30 | 236.88 | 219.52
2017-06-27 23:00 | 234.91 | 217.49
2017-06-27 23:30 | 235.46 | 217.64
2017-06-28 | 235.16 | 217.16
2017-06-28 00:30 | 233.15 | 215.94
2017-06-28 01:00 | 231.25 | 214.81
2017-06-28 01:30 | 229.39 | 213.98
2017-06-28 02:00 | 213.8 | 197.88
2017-06-28 02:30 | 208.25 | 191.32
2017-06-28 03:00 | 207.28 | 190.41
2017-06-28 03:30 | 206.6 | 190.41
2017-06-28 04:00 | 206.2 | 190.13
2017-06-28 04:30 | 206.75 | 190.66
2017-06-28 05:00 | 208.12 | 192.15
2017-06-28 05:30 | 209.91 | 194.26
2017-06-28 06:00 | 213.25 | 197.2
2017-06-28 06:30 | 231.08 | 216.02
2017-06-28 07:00 | 238.78 | 224.28
2017-06-28 07:30 | 239.63 | 225.66
2017-06-28 08:00 | 239.53 | 225.8
2017-06-28 08:30 | 237.46 | 223.89
2017-06-28 09:00 | 237.56 | 223.51
2017-06-28 09:30 | 238.24 | 224.75
2017-06-28 10:00 | 241.07 | 227.87
2017-06-28 10:30 | 234.68 | 220.18
2017-06-28 11:00 | 233.89 | 219.14
2017-06-28 11:30 | 233.92 | 218.92
2017-06-28 12:00 | 233.75 | 218.36
2017-06-28 12:30 | 233.31 | 217.7
2017-06-28 13:00 | 233.17 | 217.37
2017-06-28 13:30 | 233.5 | 217.48
2017-06-28 14:00 | 233.54 | 217.99
2017-06-28 14:30 | 232.84 | 217.4
2017-06-28 15:00 | 233.83 | 218.45
2017-06-28 15:30 | 233.99 | 218.34
2017-06-28 16:00 | 233.57 | 218.38
2017-06-28 16:30 | 234.35 | 219.46
2017-06-28 17:00 | 236.11 | 220.79
2017-06-28 17:30 | 236.73 | 221.74
2017-06-28 18:00 | 241.13 | 226.3
2017-06-28 18:30 | 244.28 | 229.24
2017-06-28 19:00 | 244.46 | 229.23
2017-06-28 19:30 | 239.29 | 224.4
2017-06-28 20:00 | 241.88 | 226.3
2017-06-28 20:30 | 241.55 | 225.7
2017-06-28 21:00 | 240.39 | 224.2
2017-06-28 21:30 | 238.46 | 222.33
2017-06-28 22:00 | 238.24 | 221.63
2017-06-28 22:30 | 236.16 | 219.27
2017-06-28 23:00 | 234.64 | 217.67
2017-06-28 23:30 | 234.29 | 217.32
2017-06-29 | 232.2 | 215.71
2017-06-29 00:30 | 230.4 | 214.59
2017-06-29 01:00 | 229.8 | 214.22
2017-06-29 01:30 | 229.77 | 214.05
2017-06-29 02:00 | 229.34 | 213.52
2017-06-29 02:30 | 228.01 | 212.12
2017-06-29 03:00 | 228.21 | 212.46
2017-06-29 03:30 | 228.02 | 212.5
2017-06-29 04:00 | 228.23 | 212.8
2017-06-29 04:30 | 228.58 | 213.68
2017-06-29 05:00 | 229.35 | 214.43
2017-06-29 05:30 | 229.45 | 215.01
2017-06-29 06:00 | 231.44 | 216.45
2017-06-29 06:30 | 234.54 | 219.83
2017-06-29 07:00 | 237.16 | 222.09
2017-06-29 07:30 | 240.15 | 225.08
2017-06-29 08:00 | 240.17 | 225.62
2017-06-29 08:30 | 238.87 | 224.46
2017-06-29 09:00 | 238.67 | 224.33
2017-06-29 09:30 | 237.41 | 222.96
2017-06-29 10:00 | 236.26 | 221.14
2017-06-29 10:30 | 235.18 | 219.84
2017-06-29 11:00 | 235.05 | 219.39
2017-06-29 11:30 | 234.51 | 218.58
2017-06-29 12:00 | 236.34 | 220.48
2017-06-29 12:30 | 237.17 | 221.41
2017-06-29 13:00 | 237.39 | 220.96
2017-06-29 13:30 | 237.73 | 221.22
2017-06-29 14:00 | 237.24 | 220.71
2017-06-29 14:30 | 237.5 | 221.28
2017-06-29 15:00 | 237.81 | 221.63
2017-06-29 15:30 | 238.42 | 222.41
2017-06-29 16:00 | 238.31 | 222.25
2017-06-29 16:30 | 238.55 | 222.61
2017-06-29 17:00 | 240.08 | 223.83
2017-06-29 17:30 | 243.66 | 228.26
2017-06-29 18:00 | 248.53 | 233.78
2017-06-29 18:30 | 250.37 | 235.69
2017-06-29 19:00 | 250.29 | 235.41
2017-06-29 19:30 | 248.41 | 233.07
2017-06-29 20:00 | 247.55 | 231.98
2017-06-29 20:30 | 245.87 | 230.71
2017-06-29 21:00 | 245.41 | 229.93
2017-06-29 21:30 | 244.27 | 229.11
2017-06-29 22:00 | 242.16 | 226.89
2017-06-29 22:30 | 240 | 224.44
2017-06-29 23:00 | 238.67 | 222.8
2017-06-29 23:30 | 237.54 | 221.72
2017-06-30 | 235.62 | 220.45
2017-06-30 00:30 | 234.49 | 219.35
2017-06-30 01:00 | 234.1 | 218.58
2017-06-30 01:30 | 233.19 | 218.13
2017-06-30 02:00 | 232.2 | 217.49
2017-06-30 02:30 | 232.41 | 217.75
2017-06-30 03:00 | 233.08 | 218
2017-06-30 03:30 | 232.82 | 217.73
2017-06-30 04:00 | 233.27 | 218.48
2017-06-30 04:30 | 233.87 | 219.23
2017-06-30 05:00 | 234.69 | 220.38
2017-06-30 05:30 | 236.57 | 222.55
2017-06-30 06:00 | 240.5 | 226.22
2017-06-30 06:30 | 241.27 | 227.47
2017-06-30 07:00 | 231.79 | 217.96
2017-06-30 07:30 | 228.99 | 215.92
2017-06-30 08:00 | 230.61 | 217.29
2017-06-30 08:30 | 228.93 | 215.64
2017-06-30 09:00 | 227.55 | 214.17
2017-06-30 09:30 | 224.64 | 210.83
2017-06-30 10:00 | 222.91 | 208.24
2017-06-30 10:30 | 219.29 | 203.41
2017-06-30 11:00 | 216.53 | 200.39
2017-06-30 11:30 | 218.02 | 202.45
2017-06-30 12:00 | 216.48 | 200.72
2017-06-30 12:30 | 215.18 | 199.43
2017-06-30 13:00 | 215.03 | 199.12
2017-06-30 13:30 | 214.13 | 198.21
2017-06-30 14:00 | 214.52 | 198.83
2017-06-30 14:30 | 215.08 | 199.54
2017-06-30 15:00 | 216.17 | 200.82
2017-06-30 15:30 | 216.64 | 201.36
2017-06-30 16:00 | 218.21 | 202.85
2017-06-30 16:30 | 224.24 | 209.04
2017-06-30 17:00 | 237.19 | 222.14
2017-06-30 17:30 | 244.24 | 229.43
2017-06-30 18:00 | 246.86 | 233.1
2017-06-30 18:30 | 250.63 | 237.13
2017-06-30 19:00 | 251.84 | 238.21
2017-06-30 19:30 | 251.79 | 237.82
2017-06-30 20:00 | 250.44 | 235.94
2017-06-30 20:30 | 249.03 | 234.71
2017-06-30 21:00 | 250.49 | 235.95
2017-06-30 21:30 | 250 | 235.66
2017-06-30 22:00 | 247.84 | 233.38
2017-06-30 22:30 | 245.47 | 230.67
2017-06-30 23:00 | 243.44 | 228.36
2017-06-30 23:30 | 241.39 | 226.03
2017-07-01 | 239.61 | 224.14
2017-07-01 00:30 | 238.85 | 223.46
2017-07-01 01:00 | 236.97 | 222.62
2017-07-01 01:30 | 235.69 | 221.45
2017-07-01 02:00 | 233.84 | 219.27
2017-07-01 02:30 | 234.04 | 218.82
2017-07-01 03:00 | 234.15 | 219.5
2017-07-01 03:30 | 234.68 | 220.51
2017-07-01 04:00 | 234.06 | 220.17
2017-07-01 04:30 | 202.87 | 189.16
2017-07-01 05:00 | 182.67 | 169.78
2017-07-01 05:30 | 182.59 | 169.72
2017-07-01 06:00 | 181.12 | 168.89
2017-07-01 06:30 | 199.3 | 191.83
2017-07-01 07:00 | 210.15 | 204.59
2017-07-01 07:30 | 212.01 | 206.61
2017-07-01 08:00 | 213.03 | 207.64
2017-07-01 08:30 | 211.67 | 206.27
2017-07-01 09:00 | 208.89 | 203.53
2017-07-01 09:30 | 207.96 | 202.35
2017-07-01 10:00 | 206.3 | 199.59
2017-07-01 10:30 | 199.01 | 190.83
2017-07-01 11:00 | 172.61 | 161.92
2017-07-01 11:30 | 170.07 | 159.73
2017-07-01 12:00 | 169.43 | 159.65
2017-07-01 12:30 | 168.15 | 158.17
2017-07-01 13:00 | 168.55 | 158.51
2017-07-01 13:30 | 172.54 | 162.83
2017-07-01 14:00 | 174.09 | 164.45
2017-07-01 14:30 | 174.92 | 165.38
2017-07-01 15:00 | 175.91 | 166.16
2017-07-01 15:30 | 176.81 | 166.98
2017-07-01 16:00 | 178.93 | 168.74
2017-07-01 16:30 | 179.85 | 170.04
2017-07-01 17:00 | 181.64 | 172.51
2017-07-01 17:30 | 188.99 | 180.43
2017-07-01 18:00 | 194.81 | 186.79
2017-07-01 18:30 | 198.25 | 190.33
2017-07-01 19:00 | 199.47 | 191.23
2017-07-01 19:30 | 199.05 | 190.39
2017-07-01 20:00 | 197.84 | 189.17
2017-07-01 20:30 | 196.73 | 188.34
2017-07-01 21:00 | 196.13 | 187.62
2017-07-01 21:30 | 195.31 | 187.39
2017-07-01 22:00 | 193.95 | 186.22
2017-07-01 22:30 | 191.97 | 183.76
2017-07-01 23:00 | 190.47 | 181.84
2017-07-01 23:30 | 188.84 | 180.39
2017-07-02 | 187.56 | 178.91
2017-07-02 00:30 | 186.93 | 178.34
2017-07-02 01:00 | 185.75 | 177.3
2017-07-02 01:30 | 184.79 | 176.21
2017-07-02 02:00 | 184 | 175.93
2017-07-02 02:30 | 183.15 | 175.57
2017-07-02 03:00 | 182.72 | 175.12
2017-07-02 03:30 | 182.5 | 175.03
2017-07-02 04:00 | 182.06 | 174.92
2017-07-02 04:30 | 182.41 | 175.42
2017-07-02 05:00 | 182.8 | 175.99
2017-07-02 05:30 | 184.5 | 176.99
2017-07-02 06:00 | 185.32 | 177.56
2017-07-02 06:30 | 187.08 | 179.95
2017-07-02 07:00 | 189.52 | 182.23
2017-07-02 07:30 | 191.42 | 184.06
2017-07-02 08:00 | 193.14 | 185.37
2017-07-02 08:30 | 191.59 | 183.64
2017-07-02 09:00 | 189.67 | 181.19
2017-07-02 09:30 | 187.87 | 178.87
2017-07-02 10:00 | 185.64 | 176.54
2017-07-02 10:30 | 183.45 | 173.98
2017-07-02 11:00 | 181.91 | 171.92
2017-07-02 11:30 | 181.92 | 171.44
2017-07-02 12:00 | 181.14 | 170.46
2017-07-02 12:30 | 180.5 | 169.92
2017-07-02 13:00 | 179.63 | 169.21
2017-07-02 13:30 | 179.85 | 170.1
2017-07-02 14:00 | 179.61 | 169.96
2017-07-02 14:30 | 179.93 | 170.36
2017-07-02 15:00 | 179.93 | 170.48
2017-07-02 15:30 | 180.28 | 170.79
2017-07-02 16:00 | 181.97 | 172.13
2017-07-02 16:30 | 183.73 | 173.87
2017-07-02 17:00 | 184.47 | 174.68
2017-07-02 17:30 | 187.16 | 177.64
2017-07-02 18:00 | 192.98 | 183.94
2017-07-02 18:30 | 196.19 | 186.76
2017-07-02 19:00 | 196.63 | 187.27
2017-07-02 19:30 | 195.89 | 186.32
2017-07-02 20:00 | 194.55 | 184.88
2017-07-02 20:30 | 193.71 | 184.17
2017-07-02 21:00 | 192.31 | 182.94
2017-07-02 21:30 | 191.34 | 181.92
2017-07-02 22:00 | 190.11 | 180.35
2017-07-02 22:30 | 187.91 | 177.71
2017-07-02 23:00 | 185.53 | 175.3
2017-07-02 23:30 | 185.22 | 174.58
2017-07-03 | 183.8 | 173.38
2017-07-03 00:30 | 182.66 | 172.61
2017-07-03 01:00 | 181.23 | 172.02
2017-07-03 01:30 | 179.97 | 171.34
2017-07-03 02:00 | 179.07 | 170.66
2017-07-03 02:30 | 179.35 | 170.37
2017-07-03 03:00 | 180.75 | 170.74
2017-07-03 03:30 | 180.43 | 170.39
2017-07-03 04:00 | 180.65 | 170.58
2017-07-03 04:30 | 180.91 | 170.68
2017-07-03 05:00 | 181.68 | 171.4
2017-07-03 05:30 | 183.15 | 173
2017-07-03 06:00 | 185.98 | 175.35
2017-07-03 06:30 | 188.21 | 178.05
2017-07-03 07:00 | 189.93 | 180.63
2017-07-03 07:30 | 192.8 | 183.02
2017-07-03 08:00 | 194.51 | 184.63
2017-07-03 08:30 | 193.86 | 183.96
2017-07-03 09:00 | 193.35 | 183.33
2017-07-03 09:30 | 191.77 | 181.57
2017-07-03 10:00 | 188.55 | 179.12
2017-07-03 10:30 | 185.52 | 176.83
2017-07-03 11:00 | 185.29 | 176.42
2017-07-03 11:30 | 185.33 | 175.5
2017-07-03 12:00 | 184.71 | 175.01
2017-07-03 12:30 | 184.14 | 174.86
2017-07-03 13:00 | 182.74 | 173.34
2017-07-03 13:30 | 182.62 | 173.09
2017-07-03 14:00 | 182.28 | 173.02
2017-07-03 14:30 | 183.85 | 174.09
2017-07-03 15:00 | 184.18 | 174.47
2017-07-03 15:30 | 184.3 | 174.59
2017-07-03 16:00 | 185.39 | 175.18
2017-07-03 16:30 | 190.62 | 177.92
2017-07-03 17:00 | 204.44 | 192.01
2017-07-03 17:30 | 205.91 | 193.26
2017-07-03 18:00 | 211.16 | 198.5
2017-07-03 18:30 | 214.81 | 202.7
2017-07-03 19:00 | 215.81 | 203.55
2017-07-03 19:30 | 214.94 | 202.37
2017-07-03 20:00 | 213.25 | 200.68
2017-07-03 20:30 | 211.85 | 199.69
2017-07-03 21:00 | 211.22 | 198.74
2017-07-03 21:30 | 210.74 | 198.25
2017-07-03 22:00 | 209.49 | 196.46
2017-07-03 22:30 | 207.96 | 194.33
2017-07-03 23:00 | 206.7 | 192.2
2017-07-03 23:30 | 205.51 | 191.07
2017-07-04 | 204.68 | 189.85
2017-07-04 00:30 | 203.22 | 188.7
2017-07-04 01:00 | 201.79 | 187.3
2017-07-04 01:30 | 199.6 | 186.63
2017-07-04 02:00 | 198.5 | 186.12
2017-07-04 02:30 | 198.61 | 186.14
2017-07-04 03:00 | 198.21 | 185.9
2017-07-04 03:30 | 197.86 | 185.89
2017-07-04 04:00 | 197.92 | 186.08
2017-07-04 04:30 | 198.37 | 186.91
2017-07-04 05:00 | 199.03 | 187.93
2017-07-04 05:30 | 200.81 | 189.78
2017-07-04 06:00 | 203.95 | 192.45
2017-07-04 06:30 | 206.81 | 195.76
2017-07-04 07:00 | 208.6 | 198
2017-07-04 07:30 | 210.21 | 199.87
2017-07-04 08:00 | 210.36 | 199.8
2017-07-04 08:30 | 208.9 | 198.36
2017-07-04 09:00 | 207.35 | 195.94
2017-07-04 09:30 | 204.47 | 192.65
2017-07-04 10:00 | 203.4 | 191
2017-07-04 10:30 | 195.63 | 182.41
2017-07-04 11:00 | 184.24 | 170.66
2017-07-04 11:30 | 184.01 | 170.46
2017-07-04 12:00 | 183.36 | 169.81
2017-07-04 12:30 | 183.55 | 170.01
2017-07-04 13:00 | 185.02 | 171.19
2017-07-04 13:30 | 185.95 | 171.98
2017-07-04 14:00 | 206.3 | 192.76
2017-07-04 14:30 | 226.59 | 213.73
2017-07-04 15:00 | 229.12 | 216.39
2017-07-04 15:30 | 230.77 | 218.38
2017-07-04 16:00 | 231.3 | 218.78
2017-07-04 16:30 | 232.86 | 220.56
2017-07-04 17:00 | 234.55 | 222.32
2017-07-04 17:30 | 235.53 | 223.25
2017-07-04 18:00 | 240.07 | 228.77
2017-07-04 18:30 | 244.3 | 233.35
2017-07-04 19:00 | 245.91 | 234.6
2017-07-04 19:30 | 244.87 | 233.38
2017-07-04 20:00 | 243.98 | 232.19
2017-07-04 20:30 | 244.14 | 231.73
2017-07-04 21:00 | 243.2 | 230.66
2017-07-04 21:30 | 242.49 | 229.9
2017-07-04 22:00 | 241.55 | 228.67
2017-07-04 22:30 | 239.58 | 226.49
2017-07-04 23:00 | 237.71 | 224.23
2017-07-04 23:30 | 235.9 | 222.82
2017-07-05 | 232.29 | 218.83
2017-07-05 00:30 | 230.9 | 218.15
2017-07-05 01:00 | 229.22 | 217.4
2017-07-05 01:30 | 229.17 | 217.05
2017-07-05 02:00 | 228.53 | 216.61
2017-07-05 02:30 | 227.55 | 216.08
2017-07-05 03:00 | 227.54 | 216.5
2017-07-05 03:30 | 227.41 | 216.5
2017-07-05 04:00 | 227.43 | 216.45
2017-07-05 04:30 | 228.29 | 217.33
2017-07-05 05:00 | 229.72 | 218.7
2017-07-05 05:30 | 231.9 | 221.07
2017-07-05 06:00 | 234.12 | 223.55
2017-07-05 06:30 | 236.25 | 225.43
2017-07-05 07:00 | 240.56 | 228.75
2017-07-05 07:30 | 242.57 | 230.77
2017-07-05 08:00 | 242.92 | 230.91
2017-07-05 08:30 | 242.12 | 230.12
2017-07-05 09:00 | 240.33 | 227.68
2017-07-05 09:30 | 237.27 | 224.56
2017-07-05 10:00 | 235.74 | 222.95
2017-07-05 10:30 | 235.68 | 222.62
2017-07-05 11:00 | 233.95 | 221.06
2017-07-05 11:30 | 232.94 | 219.82
2017-07-05 12:00 | 235.63 | 222.41
2017-07-05 12:30 | 235.23 | 222.8
2017-07-05 13:00 | 232.69 | 220.08
2017-07-05 13:30 | 232.74 | 220.17
2017-07-05 14:00 | 232.22 | 219.5
2017-07-05 14:30 | 236.45 | 224.71
2017-07-05 15:00 | 237.42 | 225.9
2017-07-05 15:30 | 238.92 | 226.55
2017-07-05 16:00 | 239.32 | 226.84
2017-07-05 16:30 | 239.76 | 227.33
2017-07-05 17:00 | 241.44 | 228.65
2017-07-05 17:30 | 242.36 | 229.27
2017-07-05 18:00 | 248.68 | 235.19
2017-07-05 18:30 | 252.28 | 238.92
2017-07-05 19:00 | 249.57 | 239.67
2017-07-05 19:30 | 246.47 | 237.44
2017-07-05 20:00 | 245.98 | 236.75
2017-07-05 20:30 | 245.47 | 235.92
2017-07-05 21:00 | 243.8 | 234.02
2017-07-05 21:30 | 240.84 | 232.26
2017-07-05 22:00 | 239.5 | 230.88
2017-07-05 22:30 | 237.31 | 228.4
2017-07-05 23:00 | 235.83 | 226.81
2017-07-05 23:30 | 234.94 | 225.96
2017-07-06 | 233.37 | 224.44
2017-07-06 00:30 | 232.19 | 223.53
2017-07-06 01:00 | 231.18 | 222.81
2017-07-06 01:30 | 229.45 | 221.8
2017-07-06 02:00 | 228.18 | 221.14
2017-07-06 02:30 | 227.88 | 220.89
2017-07-06 03:00 | 228.03 | 221.05
2017-07-06 03:30 | 228.01 | 220.95
2017-07-06 04:00 | 227.82 | 220.5
2017-07-06 04:30 | 228.21 | 220.66
2017-07-06 05:00 | 229.32 | 221.66
2017-07-06 05:30 | 231.63 | 224.08
2017-07-06 06:00 | 233.92 | 226.8
2017-07-06 06:30 | 237.43 | 229.75
2017-07-06 07:00 | 239.45 | 231.99
2017-07-06 07:30 | 243.17 | 234.55
2017-07-06 08:00 | 245.71 | 235.88
2017-07-06 08:30 | 244.27 | 234.42
2017-07-06 09:00 | 241.5 | 231.55
2017-07-06 09:30 | 238.22 | 227.78
2017-07-06 10:00 | 236.66 | 225.73
2017-07-06 10:30 | 218.81 | 207.69
2017-07-06 11:00 | 210.75 | 199.51
2017-07-06 11:30 | 210.46 | 199.27
2017-07-06 12:00 | 209.9 | 198.65
2017-07-06 12:30 | 210.82 | 199.42
2017-07-06 13:00 | 210.87 | 199.1
2017-07-06 13:30 | 210.05 | 198.41
2017-07-06 14:00 | 209.55 | 197.81
2017-07-06 14:30 | 227.75 | 216.56
2017-07-06 15:00 | 229.62 | 216.53
2017-07-06 15:30 | 233.22 | 220.67
2017-07-06 16:00 | 232.04 | 219.14
2017-07-06 16:30 | 232.85 | 219.79
2017-07-06 17:00 | 235.1 | 222.21
2017-07-06 17:30 | 239.84 | 227.42
2017-07-06 18:00 | 244.22 | 231.39
2017-07-06 18:30 | 247.61 | 235.02
2017-07-06 19:00 | 249.98 | 237.37
2017-07-06 19:30 | 248.32 | 235.1
2017-07-06 20:00 | 245.34 | 231.45
2017-07-06 20:30 | 245.06 | 231.1
2017-07-06 21:00 | 243.65 | 229.67
2017-07-06 21:30 | 242 | 228.48
2017-07-06 22:00 | 240.8 | 226.81
2017-07-06 22:30 | 239.03 | 224.78
2017-07-06 23:00 | 237.12 | 222.73
2017-07-06 23:30 | 234.32 | 221.82
2017-07-07 | 231.56 | 220.11
2017-07-07 00:30 | 229.8 | 219.02
2017-07-07 01:00 | 228.66 | 218.27
2017-07-07 01:30 | 229.16 | 217.2
2017-07-07 02:00 | 228.7 | 216.6
2017-07-07 02:30 | 228.28 | 215.41
2017-07-07 03:00 | 228.03 | 215.52
2017-07-07 03:30 | 227.68 | 215.05
2017-07-07 04:00 | 227.79 | 215.11
2017-07-07 04:30 | 228.52 | 216.1
2017-07-07 05:00 | 229.57 | 217.02
2017-07-07 05:30 | 231.22 | 218.41
2017-07-07 06:00 | 232.84 | 219.61
2017-07-07 06:30 | 235.99 | 222.04
2017-07-07 07:00 | 237.81 | 224.21
2017-07-07 07:30 | 240.81 | 227.58
2017-07-07 08:00 | 242.38 | 229.69
2017-07-07 08:30 | 242.33 | 229.55
2017-07-07 09:00 | 241.54 | 228.51
2017-07-07 09:30 | 239.41 | 226.43
2017-07-07 10:00 | 238.45 | 224.68
2017-07-07 10:30 | 237.58 | 223.44
2017-07-07 11:00 | 236.81 | 222.82
2017-07-07 11:30 | 235.48 | 221.39
2017-07-07 12:00 | 233.1 | 218.76
2017-07-07 12:30 | 232.94 | 218.63
2017-07-07 13:00 | 232.35 | 217.86
2017-07-07 13:30 | 232.47 | 218.21
2017-07-07 14:00 | 234.6 | 221.21
2017-07-07 14:30 | 233.41 | 220.21
2017-07-07 15:00 | 231.04 | 217.32
2017-07-07 15:30 | 230.36 | 216.34
2017-07-07 16:00 | 232.06 | 218.12
2017-07-07 16:30 | 234.56 | 220.87
2017-07-07 17:00 | 234.24 | 221.75
2017-07-07 17:30 | 238.24 | 225.23
2017-07-07 18:00 | 242.01 | 229.06
2017-07-07 18:30 | 244.83 | 231.91
2017-07-07 19:00 | 245.34 | 232.25
2017-07-07 19:30 | 244.86 | 231.73
2017-07-07 20:00 | 243.98 | 230.9
2017-07-07 20:30 | 243.47 | 230.63
2017-07-07 21:00 | 242.85 | 229.99
2017-07-07 21:30 | 242.27 | 228.98
2017-07-07 22:00 | 241.36 | 228.16
2017-07-07 22:30 | 241.07 | 227.22
2017-07-07 23:00 | 239.22 | 225.35
2017-07-07 23:30 | 238.19 | 224.64
2017-07-08 | 236.69 | 223.47
2017-07-08 00:30 | 234.77 | 222.9
2017-07-08 01:00 | 234.37 | 222.19
2017-07-08 01:30 | 232.55 | 221.7
2017-07-08 02:00 | 232.24 | 221.4
2017-07-08 02:30 | 231.87 | 221.16
2017-07-08 03:00 | 232.2 | 221.6
2017-07-08 03:30 | 232.7 | 222.07
2017-07-08 04:00 | 233.05 | 221.98
2017-07-08 04:30 | 233.09 | 222.16
2017-07-08 05:00 | 233.49 | 223.18
2017-07-08 05:30 | 234.23 | 223.77
2017-07-08 06:00 | 236.49 | 226.09
2017-07-08 06:30 | 238.61 | 228.69
2017-07-08 07:00 | 238.76 | 229.03
2017-07-08 07:30 | 242.22 | 232.24
2017-07-08 08:00 | 243.92 | 233.58
2017-07-08 08:30 | 244.67 | 234.76
2017-07-08 09:00 | 242.65 | 232.76
2017-07-08 09:30 | 240.48 | 230.28
2017-07-08 10:00 | 239.26 | 228.6
2017-07-08 10:30 | 236.75 | 226
2017-07-08 11:00 | 234.84 | 223.64
2017-07-08 11:30 | 235.83 | 224.01
2017-07-08 12:00 | 235.23 | 223.1
2017-07-08 12:30 | 233.87 | 222.11
2017-07-08 13:00 | 233.07 | 221.23
2017-07-08 13:30 | 231.85 | 220.23
2017-07-08 14:00 | 232.24 | 220.77
2017-07-08 14:30 | 231.29 | 219.83
2017-07-08 15:00 | 231.04 | 219.01
2017-07-08 15:30 | 231.77 | 219.55
2017-07-08 16:00 | 233.14 | 220.6
2017-07-08 16:30 | 234.38 | 222.28
2017-07-08 17:00 | 236.34 | 224.48
2017-07-08 17:30 | 240.35 | 228.63
2017-07-08 18:00 | 244.53 | 233.05
2017-07-08 18:30 | 248.02 | 236.59
2017-07-08 19:00 | 248.87 | 237.37
2017-07-08 19:30 | 247.24 | 235.7
2017-07-08 20:00 | 247.34 | 235.68
2017-07-08 20:30 | 247.96 | 236.14
2017-07-08 21:00 | 246.69 | 234.94
2017-07-08 21:30 | 245.09 | 233.15
2017-07-08 22:00 | 244.18 | 231.86
2017-07-08 22:30 | 243.01 | 231.13
2017-07-08 23:00 | 240.87 | 228.48
2017-07-08 23:30 | 239.2 | 227.47
2017-07-09 | 236.51 | 224.65
2017-07-09 00:30 | 234.48 | 222.49
2017-07-09 01:00 | 232.48 | 221.93
2017-07-09 01:30 | 230.91 | 220.56
2017-07-09 02:00 | 229.75 | 219.89
2017-07-09 02:30 | 229.41 | 219.71
2017-07-09 03:00 | 229.6 | 219.86
2017-07-09 03:30 | 229.37 | 219.39
2017-07-09 04:00 | 229.21 | 219.24
2017-07-09 04:30 | 228.4 | 218.65
2017-07-09 05:00 | 229.58 | 219.55
2017-07-09 05:30 | 237.75 | 221.21
2017-07-09 06:00 | 238.96 | 222.42
2017-07-09 06:30 | 240.31 | 224.03
2017-07-09 07:00 | 241.68 | 225.57
2017-07-09 07:30 | 243.4 | 227.51
2017-07-09 08:00 | 246.45 | 228.83
2017-07-09 08:30 | 247.29 | 229.62
2017-07-09 09:00 | 246.15 | 229.16
2017-07-09 09:30 | 244.16 | 227.26
2017-07-09 10:00 | 242.47 | 225.12
2017-07-09 10:30 | 239.79 | 222.28
2017-07-09 11:00 | 237.96 | 220.11
2017-07-09 11:30 | 236.07 | 218.03
2017-07-09 12:00 | 235.32 | 217.76
2017-07-09 12:30 | 237.59 | 220.2
2017-07-09 13:00 | 237.44 | 219.75
2017-07-09 13:30 | 236.27 | 219
2017-07-09 14:00 | 236.48 | 219.82
2017-07-09 14:30 | 235.6 | 218.98
2017-07-09 15:00 | 236.84 | 220.11
2017-07-09 15:30 | 236.63 | 220.16
2017-07-09 16:00 | 237.99 | 221.1
2017-07-09 16:30 | 240.7 | 223.81
2017-07-09 17:00 | 243.22 | 226.56
2017-07-09 17:30 | 246.67 | 231.18
2017-07-09 18:00 | 250.71 | 235.24
2017-07-09 18:30 | 252.16 | 237.22
2017-07-09 19:00 | 251.58 | 236.67
2017-07-09 19:30 | 250.49 | 235.3
2017-07-09 20:00 | 249.25 | 233.91
2017-07-09 20:30 | 247.97 | 232.6
2017-07-09 21:00 | 247.2 | 231.33
2017-07-09 21:30 | 246.49 | 230.53
2017-07-09 22:00 | 244.14 | 227.82
2017-07-09 22:30 | 242.48 | 225.47
2017-07-09 23:00 | 240.44 | 222.65
2017-07-09 23:30 | 238.94 | 221.27
2017-07-10 | 236.99 | 219.43
2017-07-10 00:30 | 235.72 | 218.49
2017-07-10 01:00 | 234.36 | 217.26
2017-07-10 01:30 | 234.12 | 216.98
2017-07-10 02:00 | 233.38 | 216.87
2017-07-10 02:30 | 233.54 | 216.8
2017-07-10 03:00 | 233.82 | 217.05
2017-07-10 03:30 | 233.34 | 216.66
2017-07-10 04:00 | 233.9 | 217.14
2017-07-10 04:30 | 234.27 | 217.84
2017-07-10 05:00 | 235.27 | 219.12
2017-07-10 05:30 | 237.7 | 221.48
2017-07-10 06:00 | 239.96 | 223.58
2017-07-10 06:30 | 244.25 | 228.15
2017-07-10 07:00 | 247.87 | 231.94
2017-07-10 07:30 | 249.53 | 234.2
2017-07-10 08:00 | 251.3 | 236.67
2017-07-10 08:30 | 250.2 | 235.65
2017-07-10 09:00 | 248.47 | 234.22
2017-07-10 09:30 | 246.39 | 232.06
2017-07-10 10:00 | 245.55 | 231.21
2017-07-10 10:30 | 244.83 | 229.63
2017-07-10 11:00 | 243.92 | 228.8
2017-07-10 11:30 | 241.91 | 226.99
2017-07-10 12:00 | 243.16 | 228.35
2017-07-10 12:30 | 243.26 | 228.43
2017-07-10 13:00 | 244.02 | 228.93
2017-07-10 13:30 | 243.96 | 228.7
2017-07-10 14:00 | 243.1 | 227.92
2017-07-10 14:30 | 242.77 | 227.43
2017-07-10 15:00 | 243.84 | 228.4
2017-07-10 15:30 | 243.95 | 228.5
2017-07-10 16:00 | 244.51 | 229.4
2017-07-10 16:30 | 245.65 | 230.55
2017-07-10 17:00 | 247.28 | 232.23
2017-07-10 17:30 | 251.28 | 236.17
2017-07-10 18:00 | 257.07 | 242.81
2017-07-10 18:30 | 261.04 | 247.21
2017-07-10 19:00 | 261.07 | 246.55
2017-07-10 19:30 | 260.1 | 245.14
2017-07-10 20:00 | 258.04 | 242.93
2017-07-10 20:30 | 256.15 | 240.77
2017-07-10 21:00 | 254.09 | 238.39
2017-07-10 21:30 | 252.13 | 236.43
2017-07-10 22:00 | 249.72 | 233.37
2017-07-10 22:30 | 247.46 | 230.13
2017-07-10 23:00 | 245.56 | 227.03
2017-07-10 23:30 | 244.2 | 225.82
2017-07-11 | 242.09 | 223.94
2017-07-11 00:30 | 240.93 | 223.55
2017-07-11 01:00 | 238.36 | 221.33
2017-07-11 01:30 | 237.99 | 221.1
2017-07-11 02:00 | 237.68 | 221.13
2017-07-11 02:30 | 237.17 | 220.65
2017-07-11 03:00 | 237 | 220.45
2017-07-11 03:30 | 237.21 | 220.24
2017-07-11 04:00 | 237.52 | 220.73
2017-07-11 04:30 | 238.03 | 221.42
2017-07-11 05:00 | 238.96 | 222.84
2017-07-11 05:30 | 240.89 | 225.05
2017-07-11 06:00 | 243.11 | 226.95
2017-07-11 06:30 | 246.47 | 231.08
2017-07-11 07:00 | 249.91 | 235.11
2017-07-11 07:30 | 253.23 | 239.16
2017-07-11 08:00 | 252.31 | 238.57
2017-07-11 08:30 | 249.5 | 234.77
2017-07-11 09:00 | 249.84 | 233.94
2017-07-11 09:30 | 246.91 | 230.06
2017-07-11 10:00 | 245.59 | 228.23
2017-07-11 10:30 | 243.02 | 224.97
2017-07-11 11:00 | 241.23 | 223.22
2017-07-11 11:30 | 240.88 | 222.76
2017-07-11 12:00 | 240.23 | 222.02
2017-07-11 12:30 | 239.18 | 220.83
2017-07-11 13:00 | 240.35 | 221.69
2017-07-11 13:30 | 239.41 | 220.8
2017-07-11 14:00 | 238.99 | 220.6
2017-07-11 14:30 | 238.83 | 220.83
2017-07-11 15:00 | 238.26 | 220.27
2017-07-11 15:30 | 239.27 | 220.69
2017-07-11 16:00 | 240.63 | 221.8
2017-07-11 16:30 | 239.95 | 221
2017-07-11 17:00 | 241.94 | 223.19
2017-07-11 17:30 | 244.11 | 226.26
2017-07-11 18:00 | 250.36 | 233.34
2017-07-11 18:30 | 254.89 | 238.55
2017-07-11 19:00 | 257.8 | 240.68
2017-07-11 19:30 | 256.95 | 239.63
2017-07-11 20:00 | 256.18 | 239.16
2017-07-11 20:30 | 255.14 | 238.15
2017-07-11 21:00 | 253.57 | 236.44
2017-07-11 21:30 | 251.58 | 234.3
2017-07-11 22:00 | 250.25 | 232.6
2017-07-11 22:30 | 247.93 | 229.29
2017-07-11 23:00 | 245.36 | 225.84
2017-07-11 23:30 | 244.06 | 224.86
2017-07-12 | 242.08 | 222.93
2017-07-12 00:30 | 239.74 | 222.29
2017-07-12 01:00 | 238.71 | 221.01
2017-07-12 01:30 | 238.37 | 220.32
2017-07-12 02:00 | 222.15 | 203.9
2017-07-12 02:30 | 219.05 | 200.73
2017-07-12 03:00 | 219.82 | 201.65
2017-07-12 03:30 | 219.63 | 201.63
2017-07-12 04:00 | 220.05 | 201.53
2017-07-12 04:30 | 221.27 | 203.02
2017-07-12 05:00 | 222.53 | 205.08
2017-07-12 05:30 | 225.27 | 208.52
2017-07-12 06:00 | 230.57 | 212.6
2017-07-12 06:30 | 235.18 | 218.2
2017-07-12 07:00 | 239.25 | 223.22
2017-07-12 07:30 | 256.12 | 241.61
2017-07-12 08:00 | 260.34 | 246.12
2017-07-12 08:30 | 257.1 | 242.64
2017-07-12 09:00 | 252.85 | 237.27
2017-07-12 09:30 | 247.87 | 231.48
2017-07-12 10:00 | 245.32 | 228.65
2017-07-12 10:30 | 242.38 | 225.11
2017-07-12 11:00 | 239.63 | 221.81
2017-07-12 11:30 | 238.06 | 220
2017-07-12 12:00 | 237.63 | 219.2
2017-07-12 12:30 | 237.02 | 218.32
2017-07-12 13:00 | 237.58 | 218.53
2017-07-12 13:30 | 237.94 | 218.88
2017-07-12 14:00 | 236.85 | 218.23
2017-07-12 14:30 | 237.71 | 219.38
2017-07-12 15:00 | 238.92 | 220.92
2017-07-12 15:30 | 239.93 | 221.93
2017-07-12 16:00 | 239.95 | 222.04
2017-07-12 16:30 | 241.49 | 223.04
2017-07-12 17:00 | 243.34 | 225.2
2017-07-12 17:30 | 245.04 | 227.15
2017-07-12 18:00 | 251.56 | 234.31
2017-07-12 18:30 | 257.42 | 240.33
2017-07-12 19:00 | 259.32 | 242.89
2017-07-12 19:30 | 258.64 | 242.22
2017-07-12 20:00 | 257.87 | 240.92
2017-07-12 20:30 | 256.91 | 239.74
2017-07-12 21:00 | 254.99 | 237.36
2017-07-12 21:30 | 254.03 | 236.79
2017-07-12 22:00 | 252.24 | 235.15
2017-07-12 22:30 | 250.56 | 232.45
2017-07-12 23:00 | 247.97 | 230.05
2017-07-12 23:30 | 245.82 | 227.97
2017-07-13 | 243.35 | 225.44
2017-07-13 00:30 | 242.3 | 224.57
2017-07-13 01:00 | 240.9 | 223.16
2017-07-13 01:30 | 239.76 | 222.45
2017-07-13 02:00 | 238.38 | 221.12
2017-07-13 02:30 | 238.15 | 220.74
2017-07-13 03:00 | 238.83 | 221.28
2017-07-13 03:30 | 235.91 | 218.44
2017-07-13 04:00 | 237.97 | 220.3
2017-07-13 04:30 | 239.59 | 222.16
2017-07-13 05:00 | 240.08 | 223.23
2017-07-13 05:30 | 242.38 | 226.13
2017-07-13 06:00 | 246 | 229.39
2017-07-13 06:30 | 250.41 | 234.42
2017-07-13 07:00 | 254.81 | 238.99
2017-07-13 07:30 | 257.39 | 242.44
2017-07-13 08:00 | 256.93 | 242.51
2017-07-13 08:30 | 253.23 | 238.43
2017-07-13 09:00 | 249.63 | 234.34
2017-07-13 09:30 | 245.37 | 229.6
2017-07-13 10:00 | 242.88 | 226.32
2017-07-13 10:30 | 240.16 | 223.04
2017-07-13 11:00 | 238.04 | 220.63
2017-07-13 11:30 | 236.72 | 219.1
2017-07-13 12:00 | 235.87 | 217.82
2017-07-13 12:30 | 234.78 | 216.48
2017-07-13 13:00 | 235.39 | 217.17
2017-07-13 13:30 | 235.12 | 217.16
2017-07-13 14:00 | 234.86 | 216.95
2017-07-13 14:30 | 236.63 | 218.71
2017-07-13 15:00 | 237.39 | 219.13
2017-07-13 15:30 | 237.76 | 219.85
2017-07-13 16:00 | 238.58 | 220.46
2017-07-13 16:30 | 238.82 | 220.84
2017-07-13 17:00 | 241.15 | 222.37
2017-07-13 17:30 | 241.84 | 223.06
2017-07-13 18:00 | 248.26 | 230.04
2017-07-13 18:30 | 253.68 | 235.64
2017-07-13 19:00 | 255.02 | 237.19
2017-07-13 19:30 | 253.13 | 235.01
2017-07-13 20:00 | 252.17 | 233.91
2017-07-13 20:30 | 251.14 | 232.82
2017-07-13 21:00 | 250.28 | 231.83
2017-07-13 21:30 | 248.11 | 230.5
2017-07-13 22:00 | 246.32 | 228.9
2017-07-13 22:30 | 244.71 | 226.5
2017-07-13 23:00 | 243.16 | 224.4
2017-07-13 23:30 | 241.2 | 222.67
2017-07-14 | 240.72 | 221.46
2017-07-14 00:30 | 240.82 | 220.94
2017-07-14 01:00 | 238.94 | 220.41
2017-07-14 01:30 | 237.72 | 219.52
2017-07-14 02:00 | 236.54 | 219.21
2017-07-14 02:30 | 237.17 | 219.21
2017-07-14 03:00 | 236.15 | 218.95
2017-07-14 03:30 | 236.39 | 219.34
2017-07-14 04:00 | 236.02 | 219.03
2017-07-14 04:30 | 236.54 | 220.23
2017-07-14 05:00 | 237.43 | 220.92
2017-07-14 05:30 | 239.76 | 224.14
2017-07-14 06:00 | 242.26 | 226.33
2017-07-14 06:30 | 246.77 | 230.45
2017-07-14 07:00 | 250.67 | 234.07
2017-07-14 07:30 | 252.9 | 237.4
2017-07-14 08:00 | 251.68 | 236.47
2017-07-14 08:30 | 249.25 | 233.97
2017-07-14 09:00 | 246.62 | 231.64
2017-07-14 09:30 | 243.77 | 228.78
2017-07-14 10:00 | 240.84 | 225.83
2017-07-14 10:30 | 237.8 | 221.91
2017-07-14 11:00 | 235.52 | 219.39
2017-07-14 11:30 | 233.9 | 217.61
2017-07-14 12:00 | 234.82 | 218.1
2017-07-14 12:30 | 235.06 | 218.42
2017-07-14 13:00 | 235.39 | 218.38
2017-07-14 13:30 | 236.51 | 219.12
2017-07-14 14:00 | 236.31 | 219.49
2017-07-14 14:30 | 236.15 | 219.04
2017-07-14 15:00 | 235.93 | 218.74
2017-07-14 15:30 | 235.96 | 218.88
2017-07-14 16:00 | 236.86 | 219.41
2017-07-14 16:30 | 238.97 | 220.74
2017-07-14 17:00 | 239.04 | 220.42
2017-07-14 17:30 | 240.38 | 221.19
2017-07-14 18:00 | 243.76 | 224.74
2017-07-14 18:30 | 247.51 | 228.82
2017-07-14 19:00 | 248.87 | 230.22
2017-07-14 19:30 | 248.88 | 230.19
2017-07-14 20:00 | 249.37 | 230.52
2017-07-14 20:30 | 249.32 | 230.11
2017-07-14 21:00 | 248.46 | 228.96
2017-07-14 21:30 | 246.4 | 228.34
2017-07-14 22:00 | 244.78 | 227.02
2017-07-14 22:30 | 243.99 | 225.23
2017-07-14 23:00 | 241.11 | 221.98
2017-07-14 23:30 | 240.09 | 221.31
2017-07-15 | 238.9 | 219.96
2017-07-15 00:30 | 237.47 | 219.35
2017-07-15 01:00 | 235.85 | 218.23
2017-07-15 01:30 | 233.8 | 217.87
2017-07-15 02:00 | 233.48 | 217.5
2017-07-15 02:30 | 233.36 | 217.06
2017-07-15 03:00 | 233.55 | 217.12
2017-07-15 03:30 | 233.61 | 217.09
2017-07-15 04:00 | 233.57 | 216.7
2017-07-15 04:30 | 233.71 | 216.87
2017-07-15 05:00 | 234.47 | 217.82
2017-07-15 05:30 | 235.73 | 219.4
2017-07-15 06:00 | 236.76 | 220.54
2017-07-15 06:30 | 238.55 | 222.71
2017-07-15 07:00 | 242.39 | 225.83
2017-07-15 07:30 | 244.83 | 228.42
2017-07-15 08:00 | 245.19 | 228.74
2017-07-15 08:30 | 244.66 | 228.03
2017-07-15 09:00 | 243.85 | 227.29
2017-07-15 09:30 | 233 | 216.62
2017-07-15 10:00 | 219.11 | 202.54
2017-07-15 10:30 | 216.21 | 199.92
2017-07-15 11:00 | 215.11 | 197.88
2017-07-15 11:30 | 214.4 | 196.55
2017-07-15 12:00 | 214.23 | 196.29
2017-07-15 12:30 | 214.51 | 196.62
2017-07-15 13:00 | 214.66 | 196.63
2017-07-15 13:30 | 224.54 | 207.14
2017-07-15 14:00 | 237.39 | 220.04
2017-07-15 14:30 | 236.89 | 219.25
2017-07-15 15:00 | 235.35 | 217.21
2017-07-15 15:30 | 234.67 | 216.09
2017-07-15 16:00 | 235.15 | 216.66
2017-07-15 16:30 | 236.42 | 218.6
2017-07-15 17:00 | 240.05 | 222.79
2017-07-15 17:30 | 243.49 | 226.88
2017-07-15 18:00 | 246.93 | 230.24
2017-07-15 18:30 | 248.87 | 231.67
2017-07-15 19:00 | 249.59 | 232.45
2017-07-15 19:30 | 248.63 | 231.65
2017-07-15 20:00 | 247.5 | 230.16
2017-07-15 20:30 | 246.26 | 229.3
2017-07-15 21:00 | 245.2 | 228.12
2017-07-15 21:30 | 244.59 | 227.49
2017-07-15 22:00 | 243.65 | 226.44
2017-07-15 22:30 | 243.03 | 224.91
2017-07-15 23:00 | 241.16 | 222.59
2017-07-15 23:30 | 239.67 | 221.58
2017-07-16 | 237.68 | 220.13
2017-07-16 00:30 | 220.25 | 203.13
2017-07-16 01:00 | 214.01 | 196.44
2017-07-16 01:30 | 212.87 | 195.76
2017-07-16 02:00 | 211.13 | 195.12
2017-07-16 02:30 | 211.4 | 195.46
2017-07-16 03:00 | 212.07 | 195.73
2017-07-16 03:30 | 212.09 | 195.66
2017-07-16 04:00 | 211.63 | 195.69
2017-07-16 04:30 | 210.79 | 195.56
2017-07-16 05:00 | 211.8 | 196.26
2017-07-16 05:30 | 212.4 | 196.72
2017-07-16 06:00 | 213.22 | 197.44
2017-07-16 06:30 | 216.07 | 199.6
2017-07-16 07:00 | 217.98 | 201.56
2017-07-16 07:30 | 218.87 | 203.16
2017-07-16 08:00 | 219.91 | 204.3
2017-07-16 08:30 | 220.24 | 205.04
2017-07-16 09:00 | 218.81 | 204.51
2017-07-16 09:30 | 218.73 | 203.6
2017-07-16 10:00 | 218.17 | 202.29
2017-07-16 10:30 | 217.72 | 201.52
2017-07-16 11:00 | 215.8 | 199.61
2017-07-16 11:30 | 212.91 | 197.13
2017-07-16 12:00 | 211.83 | 195.11
2017-07-16 12:30 | 211.45 | 194.55
2017-07-16 13:00 | 211.75 | 194.72
2017-07-16 13:30 | 211.59 | 194.24
2017-07-16 14:00 | 211.47 | 193.82
2017-07-16 14:30 | 210.06 | 192.66
2017-07-16 15:00 | 211.38 | 193.31
2017-07-16 15:30 | 211.11 | 192.99
2017-07-16 16:00 | 211.09 | 193.19
2017-07-16 16:30 | 212.99 | 195.23
2017-07-16 17:00 | 232.47 | 215.56
2017-07-16 17:30 | 238.99 | 223.22
2017-07-16 18:00 | 244.09 | 228.1
2017-07-16 18:30 | 248.18 | 232.26
2017-07-16 19:00 | 249.24 | 233.23
2017-07-16 19:30 | 248.56 | 232.65
2017-07-16 20:00 | 246.43 | 230.48
2017-07-16 20:30 | 245.91 | 230.05
2017-07-16 21:00 | 244.76 | 228.74
2017-07-16 21:30 | 244.03 | 227.64
2017-07-16 22:00 | 242.12 | 225.97
2017-07-16 22:30 | 240.34 | 223.38
2017-07-16 23:00 | 238.47 | 221.02
2017-07-16 23:30 | 237.22 | 219.78
2017-07-17 | 220.74 | 202.54
2017-07-17 00:30 | 214.46 | 196.12
2017-07-17 01:00 | 212.05 | 194.79
2017-07-17 01:30 | 210.17 | 194.1
2017-07-17 02:00 | 208.9 | 193.95
2017-07-17 02:30 | 210.01 | 193.96
2017-07-17 03:00 | 211.54 | 194.07
2017-07-17 03:30 | 211.9 | 194.23
2017-07-17 04:00 | 212.32 | 194.53
2017-07-17 04:30 | 213.67 | 195.73
2017-07-17 05:00 | 213.85 | 196.32
2017-07-17 05:30 | 218.32 | 198.82
2017-07-17 06:00 | 222.9 | 201.94
2017-07-17 06:30 | 228.83 | 209.44
2017-07-17 07:00 | 249.54 | 231.84
2017-07-17 07:30 | 252.05 | 236.4
2017-07-17 08:00 | 249.76 | 237.01
2017-07-17 08:30 | 246.17 | 233.39
2017-07-17 09:00 | 242.28 | 229.47
2017-07-17 09:30 | 238.28 | 225.77
2017-07-17 10:00 | 235.3 | 223.09
2017-07-17 10:30 | 233.29 | 220.99
2017-07-17 11:00 | 231.28 | 218.86
2017-07-17 11:30 | 230.31 | 217.28
2017-07-17 12:00 | 230.4 | 217.49
2017-07-17 12:30 | 230.01 | 217.19
2017-07-17 13:00 | 228.02 | 214.55
2017-07-17 13:30 | 227 | 213.34
2017-07-17 14:00 | 227.03 | 213.14
2017-07-17 14:30 | 227.96 | 214.06
2017-07-17 15:00 | 228.76 | 214.39
2017-07-17 15:30 | 229.8 | 216.18
2017-07-17 16:00 | 229.34 | 216.12
2017-07-17 16:30 | 234.29 | 221.61
2017-07-17 17:00 | 234.99 | 222.51
2017-07-17 17:30 | 234.06 | 220.67
2017-07-17 18:00 | 236.82 | 223.05
2017-07-17 18:30 | 239.56 | 225.48
2017-07-17 19:00 | 242.7 | 228.86
2017-07-17 19:30 | 241.86 | 228.25
2017-07-17 20:00 | 240.32 | 226.79
2017-07-17 20:30 | 239.88 | 226.26
2017-07-17 21:00 | 238.63 | 224.69
2017-07-17 21:30 | 237.84 | 224.33
2017-07-17 22:00 | 235.85 | 222.53
2017-07-17 22:30 | 233.66 | 220.49
2017-07-17 23:00 | 230.78 | 218.3
2017-07-17 23:30 | 229.4 | 217.57
2017-07-18 | 227.85 | 216.49
2017-07-18 00:30 | 226.68 | 215.68
2017-07-18 01:00 | 225.99 | 214.98
2017-07-18 01:30 | 226.37 | 215.05
2017-07-18 02:00 | 225.67 | 214.85
2017-07-18 02:30 | 224.76 | 213.73
2017-07-18 03:00 | 225.54 | 213.29
2017-07-18 03:30 | 226.19 | 213.44
2017-07-18 04:00 | 225.95 | 213.47
2017-07-18 04:30 | 226.32 | 214.27
2017-07-18 05:00 | 227.69 | 215.81
2017-07-18 05:30 | 227.6 | 215.48
2017-07-18 06:00 | 231.43 | 217.62
2017-07-18 06:30 | 234.13 | 219.87
2017-07-18 07:00 | 237.79 | 223.53
2017-07-18 07:30 | 240.53 | 226.27
2017-07-18 08:00 | 241.64 | 227.1
2017-07-18 08:30 | 239.01 | 224.05
2017-07-18 09:00 | 237.58 | 222.95
2017-07-18 09:30 | 233.31 | 219.21
2017-07-18 10:00 | 231.21 | 216.72
2017-07-18 10:30 | 232.04 | 217.26
2017-07-18 11:00 | 231.68 | 217.09
2017-07-18 11:30 | 231.56 | 216.91
2017-07-18 12:00 | 230.1 | 215.86
2017-07-18 12:30 | 230.75 | 215.05
2017-07-18 13:00 | 231.32 | 214.89
2017-07-18 13:30 | 230.81 | 214.34
2017-07-18 14:00 | 229.08 | 215.13
2017-07-18 14:30 | 229.52 | 215.67
2017-07-18 15:00 | 228.63 | 214.58
2017-07-18 15:30 | 227.88 | 213.75
2017-07-18 16:00 | 228.57 | 214.87
2017-07-18 16:30 | 229.31 | 215.57
2017-07-18 17:00 | 230.57 | 217.09
2017-07-18 17:30 | 233.17 | 219.19
2017-07-18 18:00 | 238.57 | 225.03
2017-07-18 18:30 | 243.09 | 229.38
2017-07-18 19:00 | 244.96 | 231.21
2017-07-18 19:30 | 243.96 | 230.3
2017-07-18 20:00 | 241.88 | 228.32
2017-07-18 20:30 | 241.59 | 227.87
2017-07-18 21:00 | 240.39 | 226.32
2017-07-18 21:30 | 238.83 | 225.84
2017-07-18 22:00 | 238.35 | 225.44
2017-07-18 22:30 | 236.92 | 223.99
2017-07-18 23:00 | 234.45 | 221.52
2017-07-18 23:30 | 233.02 | 220.85
2017-07-19 | 229.78 | 218.21
2017-07-19 00:30 | 226.73 | 215.41
2017-07-19 01:00 | 226.77 | 214.75
2017-07-19 01:30 | 228.81 | 216.91
2017-07-19 02:00 | 228.41 | 215.99
2017-07-19 02:30 | 227.81 | 215.42
2017-07-19 03:00 | 229.31 | 216.88
2017-07-19 03:30 | 231.92 | 218.65
2017-07-19 04:00 | 232.95 | 219.58
2017-07-19 04:30 | 234.46 | 221.05
2017-07-19 05:00 | 235.72 | 222.62
2017-07-19 05:30 | 236.51 | 225.29
2017-07-19 06:00 | 240.78 | 229.03
2017-07-19 06:30 | 244.91 | 232.79
2017-07-19 07:00 | 250.12 | 237.13
2017-07-19 07:30 | 251.43 | 240.08
2017-07-19 08:00 | 251.86 | 240.31
2017-07-19 08:30 | 249.78 | 238.07
2017-07-19 09:00 | 246.71 | 234.94
2017-07-19 09:30 | 242.48 | 230.44
2017-07-19 10:00 | 237.69 | 225.34
2017-07-19 10:30 | 234.86 | 222.54
2017-07-19 11:00 | 232.95 | 220.26
2017-07-19 11:30 | 230.89 | 218.23
2017-07-19 12:00 | 231.18 | 218.48
2017-07-19 12:30 | 231.59 | 218.36
2017-07-19 13:00 | 230.53 | 217.4
2017-07-19 13:30 | 229.9 | 216.95
2017-07-19 14:00 | 232.31 | 219.03
2017-07-19 14:30 | 233.34 | 219.53
2017-07-19 15:00 | 233.46 | 219.35
2017-07-19 15:30 | 234.34 | 220.1
2017-07-19 16:00 | 234.41 | 220.53
2017-07-19 16:30 | 236.25 | 222.52
2017-07-19 17:00 | 238.93 | 225.37
2017-07-19 17:30 | 242.9 | 229.69
2017-07-19 18:00 | 246.37 | 233.3
2017-07-19 18:30 | 252.32 | 239.95
2017-07-19 19:00 | 254.15 | 241.91
2017-07-19 19:30 | 253.99 | 241.49
2017-07-19 20:00 | 253.4 | 240.7
2017-07-19 20:30 | 252.82 | 239.81
2017-07-19 21:00 | 252.06 | 238.37
2017-07-19 21:30 | 249.27 | 236.4
2017-07-19 22:00 | 246.69 | 233.5
2017-07-19 22:30 | 244.27 | 231.08
2017-07-19 23:00 | 241.63 | 228.28
2017-07-19 23:30 | 240.13 | 226.55
2017-07-20 | 239.61 | 225.71
2017-07-20 00:30 | 237.26 | 224.59
2017-07-20 01:00 | 235.73 | 223.73
2017-07-20 01:30 | 235.09 | 223.19
2017-07-20 02:00 | 234.76 | 222.65
2017-07-20 02:30 | 234.06 | 222.14
2017-07-20 03:00 | 233.69 | 222.02
2017-07-20 03:30 | 234.2 | 222.4
2017-07-20 04:00 | 234.58 | 222.85
2017-07-20 04:30 | 235.7 | 223.69
2017-07-20 05:00 | 236.51 | 224.87
2017-07-20 05:30 | 238.7 | 227.63
2017-07-20 06:00 | 242.6 | 231.33
2017-07-20 06:30 | 246.2 | 235.18
2017-07-20 07:00 | 250.51 | 239.39
2017-07-20 07:30 | 254.67 | 243.51
2017-07-20 08:00 | 254.45 | 242.37
2017-07-20 08:30 | 250.32 | 238.11
2017-07-20 09:00 | 247.09 | 234.85
2017-07-20 09:30 | 243.14 | 230.52
2017-07-20 10:00 | 240.87 | 227.76
2017-07-20 10:30 | 237.62 | 224.76
2017-07-20 11:00 | 235.88 | 222.89
2017-07-20 11:30 | 234.45 | 221.27
2017-07-20 12:00 | 233.2 | 219.87
2017-07-20 12:30 | 232.41 | 218.8
2017-07-20 13:00 | 232.66 | 218.36
2017-07-20 13:30 | 232.46 | 218.27
2017-07-20 14:00 | 233.97 | 219.44
2017-07-20 14:30 | 234.04 | 219.66
2017-07-20 15:00 | 234.15 | 220.07
2017-07-20 15:30 | 234.74 | 220.8
2017-07-20 16:00 | 234.72 | 221.94
2017-07-20 16:30 | 237.14 | 223.22
2017-07-20 17:00 | 239.27 | 225.64
2017-07-20 17:30 | 242.61 | 229.11
2017-07-20 18:00 | 247.51 | 234.34
2017-07-20 18:30 | 252.78 | 239.5
2017-07-20 19:00 | 255.56 | 242.53
2017-07-20 19:30 | 255.07 | 242.07
2017-07-20 20:00 | 254.56 | 241.56
2017-07-20 20:30 | 253.74 | 240.64
2017-07-20 21:00 | 252.96 | 239.46
2017-07-20 21:30 | 252.07 | 238.71
2017-07-20 22:00 | 249.63 | 236.04
2017-07-20 22:30 | 247.12 | 233.01
2017-07-20 23:00 | 242.24 | 230
2017-07-20 23:30 | 239.84 | 227.95
2017-07-21 | 238.29 | 226.79
2017-07-21 00:30 | 236.17 | 225.59
2017-07-21 01:00 | 235.23 | 224.6
2017-07-21 01:30 | 234.65 | 223.97
2017-07-21 02:00 | 232.23 | 223.12
2017-07-21 02:30 | 232.78 | 223.24
2017-07-21 03:00 | 233.73 | 223.19
2017-07-21 03:30 | 233.96 | 223.6
2017-07-21 04:00 | 235.4 | 224.3
2017-07-21 04:30 | 235.96 | 224.35
2017-07-21 05:00 | 239.19 | 227.3
2017-07-21 05:30 | 241.29 | 229.56
2017-07-21 06:00 | 244.97 | 234.16
2017-07-21 06:30 | 249.4 | 238.84
2017-07-21 07:00 | 253.73 | 243.48
2017-07-21 07:30 | 257.37 | 247.5
2017-07-21 08:00 | 257.72 | 248
2017-07-21 08:30 | 251.78 | 241.9
2017-07-21 09:00 | 248.1 | 237.97
2017-07-21 09:30 | 244.15 | 233.36
2017-07-21 10:00 | 241.58 | 230.53
2017-07-21 10:30 | 238.94 | 228.1
2017-07-21 11:00 | 237.08 | 225.91
2017-07-21 11:30 | 235.98 | 224.15
2017-07-21 12:00 | 234.75 | 222.46
2017-07-21 12:30 | 233.61 | 220.91
2017-07-21 13:00 | 232.34 | 219.38
2017-07-21 13:30 | 234.29 | 221.6
2017-07-21 14:00 | 233.48 | 221.22
2017-07-21 14:30 | 233.75 | 221.38
2017-07-21 15:00 | 234.36 | 221.4
2017-07-21 15:30 | 235.1 | 221.47
2017-07-21 16:00 | 236.96 | 223.53
2017-07-21 16:30 | 238.64 | 225.23
2017-07-21 17:00 | 240.25 | 226.94
2017-07-21 17:30 | 242.76 | 229.61
2017-07-21 18:00 | 247.57 | 234.81
2017-07-21 18:30 | 252.02 | 239.49
2017-07-21 19:00 | 254.12 | 241.94
2017-07-21 19:30 | 253.74 | 241.52
2017-07-21 20:00 | 254.01 | 241.78
2017-07-21 20:30 | 254.14 | 241.99
2017-07-21 21:00 | 251.97 | 239.65
2017-07-21 21:30 | 251.15 | 239.18
2017-07-21 22:00 | 249.85 | 237.77
2017-07-21 22:30 | 247.32 | 235.06
2017-07-21 23:00 | 244.82 | 232.22
2017-07-21 23:30 | 243.08 | 230.21
2017-07-22 | 241.69 | 229.18
2017-07-22 00:30 | 240.02 | 228.65
2017-07-22 01:00 | 238.02 | 227.71
2017-07-22 01:30 | 236.49 | 225.85
2017-07-22 02:00 | 236.57 | 226.12
2017-07-22 02:30 | 236.1 | 225.65
2017-07-22 03:00 | 235.03 | 224.94
2017-07-22 03:30 | 235.09 | 225.47
2017-07-22 04:00 | 235.21 | 225.73
2017-07-22 04:30 | 236.47 | 226.86
2017-07-22 05:00 | 238.02 | 228.29
2017-07-22 05:30 | 239.9 | 230.22
2017-07-22 06:00 | 241.67 | 232.17
2017-07-22 06:30 | 244.27 | 234.65
2017-07-22 07:00 | 247.62 | 237.85
2017-07-22 07:30 | 250.55 | 241.3
2017-07-22 08:00 | 251.95 | 242.9
2017-07-22 08:30 | 251.72 | 242.66
2017-07-22 09:00 | 256.73 | 248.4
2017-07-22 09:30 | 256.42 | 248.45
2017-07-22 10:00 | 253.47 | 245.18
2017-07-22 10:30 | 248.7 | 240.01
2017-07-22 11:00 | 241.8 | 231.8
2017-07-22 11:30 | 237.88 | 226.94
2017-07-22 12:00 | 235.6 | 224.23
2017-07-22 12:30 | 233.93 | 222.24
2017-07-22 13:00 | 235.67 | 223.81
2017-07-22 13:30 | 235.55 | 223.38
2017-07-22 14:00 | 234.78 | 223.23
2017-07-22 14:30 | 233.98 | 222.02
2017-07-22 15:00 | 233.86 | 221.66
2017-07-22 15:30 | 234.29 | 222.28
2017-07-22 16:00 | 237.41 | 226.02
2017-07-22 16:30 | 244.23 | 233.59
2017-07-22 17:00 | 245.51 | 233.82
2017-07-22 17:30 | 247.27 | 235.39
2017-07-22 18:00 | 247.91 | 236.09
2017-07-22 18:30 | 250.45 | 239.34
2017-07-22 19:00 | 251.04 | 240.16
2017-07-22 19:30 | 250.68 | 239.65
2017-07-22 20:00 | 250 | 238.55
2017-07-22 20:30 | 249.08 | 237.77
2017-07-22 21:00 | 248.59 | 237.18
2017-07-22 21:30 | 247.72 | 236.33
2017-07-22 22:00 | 245.91 | 234.17
2017-07-22 22:30 | 244.3 | 232.76
2017-07-22 23:00 | 242.01 | 230.32
2017-07-22 23:30 | 240.89 | 229.38
2017-07-23 | 239.41 | 228.08
2017-07-23 00:30 | 222.86 | 211.35
2017-07-23 01:00 | 216.21 | 205.82
2017-07-23 01:30 | 215.44 | 205.1
2017-07-23 02:00 | 214.83 | 204.86
2017-07-23 02:30 | 213.85 | 203.87
2017-07-23 03:00 | 214.27 | 203.83
2017-07-23 03:30 | 215.11 | 204.72
2017-07-23 04:00 | 214.76 | 204.18
2017-07-23 04:30 | 214.79 | 204.32
2017-07-23 05:00 | 216.1 | 205.82
2017-07-23 05:30 | 216.35 | 206.72
2017-07-23 06:00 | 218.08 | 208.19
2017-07-23 06:30 | 219.38 | 210.51
2017-07-23 07:00 | 222.17 | 212.95
2017-07-23 07:30 | 225.14 | 215.92
2017-07-23 08:00 | 226.41 | 216.56
2017-07-23 08:30 | 225.82 | 215.75
2017-07-23 09:00 | 223.41 | 213.08
2017-07-23 09:30 | 219.74 | 209.01
2017-07-23 10:00 | 216.93 | 206.04
2017-07-23 10:30 | 212.96 | 201.64
2017-07-23 11:00 | 211.58 | 199.59
2017-07-23 11:30 | 208.75 | 196.78
2017-07-23 12:00 | 209.03 | 196.92
2017-07-23 12:30 | 210.17 | 198.33
2017-07-23 13:00 | 210.09 | 198.11
2017-07-23 13:30 | 208.9 | 197.41
2017-07-23 14:00 | 207.71 | 195.96
2017-07-23 14:30 | 207.28 | 195.45
2017-07-23 15:00 | 206.33 | 195.12
2017-07-23 15:30 | 207.97 | 196
2017-07-23 16:00 | 209.02 | 197.26
2017-07-23 16:30 | 211.01 | 199.52
2017-07-23 17:00 | 227.91 | 214.98
2017-07-23 17:30 | 237.43 | 224.54
2017-07-23 18:00 | 242.18 | 229.64
2017-07-23 18:30 | 245.79 | 233.86
2017-07-23 19:00 | 247.09 | 235.33
2017-07-23 19:30 | 245.32 | 233.36
2017-07-23 20:00 | 244.83 | 232.66
2017-07-23 20:30 | 244.82 | 232.54
2017-07-23 21:00 | 244.39 | 231.65
2017-07-23 21:30 | 243.79 | 231.58
2017-07-23 22:00 | 242.54 | 230.37
2017-07-23 22:30 | 224.26 | 211.62
2017-07-23 23:00 | 217.48 | 204.37
2017-07-23 23:30 | 216.61 | 203.66
2017-07-24 | 215.3 | 202.47
2017-07-24 00:30 | 214.61 | 202.23
2017-07-24 01:00 | 213.26 | 201.39
2017-07-24 01:30 | 213.18 | 201.31
2017-07-24 02:00 | 211.87 | 200.48
2017-07-24 02:30 | 211.24 | 199.84
2017-07-24 03:00 | 210.79 | 199.19
2017-07-24 03:30 | 210.43 | 199.28
2017-07-24 04:00 | 211.44 | 200.14
2017-07-24 04:30 | 213.14 | 201.59
2017-07-24 05:00 | 214.31 | 203.19
2017-07-24 05:30 | 216.82 | 206.16
2017-07-24 06:00 | 220.93 | 210
2017-07-24 06:30 | 226.08 | 215.48
2017-07-24 07:00 | 245.77 | 235.4
2017-07-24 07:30 | 255.04 | 243.78
2017-07-24 08:00 | 256.5 | 244.89
2017-07-24 08:30 | 252.87 | 240.53
2017-07-24 09:00 | 248.11 | 235.51
2017-07-24 09:30 | 241.73 | 228.21
2017-07-24 10:00 | 240.82 | 226.41
2017-07-24 10:30 | 238.83 | 223.94
2017-07-24 11:00 | 237.6 | 222.66
2017-07-24 11:30 | 236.03 | 220.76
2017-07-24 12:00 | 233.57 | 218.57
2017-07-24 12:30 | 232.89 | 218.28
2017-07-24 13:00 | 233.82 | 219.37
2017-07-24 13:30 | 232.74 | 217.93
2017-07-24 14:00 | 234.58 | 220.37
2017-07-24 14:30 | 235.09 | 218.95
2017-07-24 15:00 | 235.22 | 217.94
2017-07-24 15:30 | 235.49 | 217.89
2017-07-24 16:00 | 233.05 | 218.08
2017-07-24 16:30 | 232.69 | 217.77
2017-07-24 17:00 | 232.72 | 217.8
2017-07-24 17:30 | 235.39 | 220.62
2017-07-24 18:00 | 240.37 | 226
2017-07-24 18:30 | 244.94 | 231.48
2017-07-24 19:00 | 247.15 | 234.21
2017-07-24 19:30 | 246.29 | 233.43
2017-07-24 20:00 | 246.49 | 233.78
2017-07-24 20:30 | 247.8 | 235.14
2017-07-24 21:00 | 247.28 | 234.46
2017-07-24 21:30 | 245.68 | 233.23
2017-07-24 22:00 | 243.92 | 231.89
2017-07-24 22:30 | 241.51 | 229.15
2017-07-24 23:00 | 239.07 | 226.78
2017-07-24 23:30 | 236.99 | 225.11
2017-07-25 | 235.21 | 223.62
2017-07-25 00:30 | 234.92 | 223.33
2017-07-25 01:00 | 232.88 | 222.08
2017-07-25 01:30 | 232.58 | 221.17
2017-07-25 02:00 | 231.4 | 220.55
2017-07-25 02:30 | 231.92 | 220.55
2017-07-25 03:00 | 231.94 | 220.67
2017-07-25 03:30 | 232.67 | 221.46
2017-07-25 04:00 | 233.03 | 221.81
2017-07-25 04:30 | 233.7 | 222.85
2017-07-25 05:00 | 234.6 | 224.31
2017-07-25 05:30 | 237.33 | 227.21
2017-07-25 06:00 | 242.04 | 231.38
2017-07-25 06:30 | 246.43 | 235.77
2017-07-25 07:00 | 251.89 | 241.23
2017-07-25 07:30 | 254.15 | 243.37
2017-07-25 08:00 | 253.87 | 243.22
2017-07-25 08:30 | 250.21 | 239.1
2017-07-25 09:00 | 246.06 | 234.57
2017-07-25 09:30 | 241 | 228.72
2017-07-25 10:00 | 237.74 | 225.12
2017-07-25 10:30 | 237.12 | 224.17
2017-07-25 11:00 | 235.69 | 222.44
2017-07-25 11:30 | 234.31 | 221.04
2017-07-25 12:00 | 233.65 | 219.98
2017-07-25 12:30 | 233.05 | 219.04
2017-07-25 13:00 | 231.57 | 217.43
2017-07-25 13:30 | 231.05 | 216.93
2017-07-25 14:00 | 231.24 | 217.5
2017-07-25 14:30 | 231.64 | 217.77
2017-07-25 15:00 | 232.78 | 218.81
2017-07-25 15:30 | 233.66 | 219.63
2017-07-25 16:00 | 234.5 | 220.46
2017-07-25 16:30 | 235.51 | 221.37
2017-07-25 17:00 | 235.89 | 222.03
2017-07-25 17:30 | 239.44 | 225.87
2017-07-25 18:00 | 244.23 | 231.07
2017-07-25 18:30 | 249.41 | 236.65
2017-07-25 19:00 | 251.17 | 238.48
2017-07-25 19:30 | 250.11 | 237.53
2017-07-25 20:00 | 249.6 | 237.16
2017-07-25 20:30 | 248.77 | 236.27
2017-07-25 21:00 | 247.88 | 235.12
2017-07-25 21:30 | 246.11 | 234.15
2017-07-25 22:00 | 244.46 | 232.95
2017-07-25 22:30 | 242.28 | 230.22
2017-07-25 23:00 | 239.84 | 227.71
2017-07-25 23:30 | 238.14 | 225.97
2017-07-26 | 236.19 | 224.03
2017-07-26 00:30 | 235.82 | 223.78
2017-07-26 01:00 | 233.2 | 221.26
2017-07-26 01:30 | 232.87 | 220.54
2017-07-26 02:00 | 232.92 | 220.97
2017-07-26 02:30 | 232.64 | 220.97
2017-07-26 03:00 | 232.78 | 221.18
2017-07-26 03:30 | 233.1 | 221.31
2017-07-26 04:00 | 233.02 | 220.87
2017-07-26 04:30 | 234.96 | 222.93
2017-07-26 05:00 | 235.88 | 224.21
2017-07-26 05:30 | 238.7 | 227.55
2017-07-26 06:00 | 243 | 230.94
2017-07-26 06:30 | 247.55 | 236.14
2017-07-26 07:00 | 251.68 | 240.24
2017-07-26 07:30 | 254.97 | 243.55
2017-07-26 08:00 | 254.41 | 242.95
2017-07-26 08:30 | 251.33 | 239.46
2017-07-26 09:00 | 246.66 | 234.19
2017-07-26 09:30 | 241.76 | 228.66
2017-07-26 10:00 | 239.83 | 226.21
2017-07-26 10:30 | 237.96 | 224.13
2017-07-26 11:00 | 236.68 | 222.81
2017-07-26 11:30 | 235.47 | 221.41
2017-07-26 12:00 | 234.6 | 220.19
2017-07-26 12:30 | 232.84 | 218.31
2017-07-26 13:00 | 232.9 | 218.09
2017-07-26 13:30 | 233.28 | 218.15
2017-07-26 14:00 | 232.8 | 217.95
2017-07-26 14:30 | 232 | 217.29
2017-07-26 15:00 | 232.73 | 217.72
2017-07-26 15:30 | 233.32 | 218.25
2017-07-26 16:00 | 233.81 | 219.01
2017-07-26 16:30 | 234.71 | 219.89
2017-07-26 17:00 | 235.56 | 221.36
2017-07-26 17:30 | 237.12 | 223.79
2017-07-26 18:00 | 241.78 | 228.39
2017-07-26 18:30 | 246.64 | 233.38
2017-07-26 19:00 | 248.29 | 235.34
2017-07-26 19:30 | 247.33 | 234.37
2017-07-26 20:00 | 246.71 | 233.31
2017-07-26 20:30 | 246.35 | 233
2017-07-26 21:00 | 244.05 | 230.43
2017-07-26 21:30 | 241.56 | 228.74
2017-07-26 22:00 | 240.5 | 227.84
2017-07-26 22:30 | 238.63 | 225.88
2017-07-26 23:00 | 236.41 | 223.6
2017-07-26 23:30 | 234.54 | 222.03
2017-07-27 | 217.84 | 204.9
2017-07-27 00:30 | 211.38 | 198.87
2017-07-27 01:00 | 210.48 | 198.05
2017-07-27 01:30 | 209.87 | 197.3
2017-07-27 02:00 | 209.63 | 196.91
2017-07-27 02:30 | 210.12 | 197.29
2017-07-27 03:00 | 210.84 | 198.11
2017-07-27 03:30 | 210.94 | 198.02
2017-07-27 04:00 | 211.8 | 198.88
2017-07-27 04:30 | 212.48 | 199.84
2017-07-27 05:00 | 213.56 | 201.46
2017-07-27 05:30 | 215.91 | 204.32
2017-07-27 06:00 | 220.95 | 208.73
2017-07-27 06:30 | 225.6 | 214.32
2017-07-27 07:00 | 247.08 | 236.02
2017-07-27 07:30 | 252.54 | 242.11
2017-07-27 08:00 | 250.87 | 241.31
2017-07-27 08:30 | 246.18 | 236.01
2017-07-27 09:00 | 241.29 | 230.54
2017-07-27 09:30 | 237.28 | 226.04
2017-07-27 10:00 | 218.54 | 208.56
2017-07-27 10:30 | 211.83 | 201.03
2017-07-27 11:00 | 210.44 | 199.12
2017-07-27 11:30 | 209.5 | 197.66
2017-07-27 12:00 | 207.76 | 195.78
2017-07-27 12:30 | 206.66 | 193.94
2017-07-27 13:00 | 207.12 | 194.07
2017-07-27 13:30 | 206.3 | 193.14
2017-07-27 14:00 | 207.48 | 194.62
2017-07-27 14:30 | 207.24 | 194.56
2017-07-27 15:00 | 224.62 | 211.89
2017-07-27 15:30 | 229.06 | 216.21
2017-07-27 16:00 | 229.5 | 216.94
2017-07-27 16:30 | 231.37 | 218.32
2017-07-27 17:00 | 233.23 | 219.92
2017-07-27 17:30 | 234.57 | 221.45
2017-07-27 18:00 | 237.79 | 224.86
2017-07-27 18:30 | 242.56 | 229.91
2017-07-27 19:00 | 245.57 | 233.06
2017-07-27 19:30 | 244.82 | 232.3
2017-07-27 20:00 | 244.32 | 231.86
2017-07-27 20:30 | 243.54 | 231.16
2017-07-27 21:00 | 242.05 | 229.49
2017-07-27 21:30 | 239.31 | 227.73
2017-07-27 22:00 | 238.67 | 227.05
2017-07-27 22:30 | 237.33 | 225.38
2017-07-27 23:00 | 235.7 | 223.84
2017-07-27 23:30 | 233.78 | 221.89
2017-07-28 | 231.56 | 219.72
2017-07-28 00:30 | 230.49 | 219.45
2017-07-28 01:00 | 229.14 | 218.86
2017-07-28 01:30 | 229.02 | 218.61
2017-07-28 02:00 | 212.66 | 202.03
2017-07-28 02:30 | 207.57 | 196.36
2017-07-28 03:00 | 207.83 | 196.15
2017-07-28 03:30 | 208.46 | 196.44
2017-07-28 04:00 | 208.4 | 196.65
2017-07-28 04:30 | 209.43 | 198.14
2017-07-28 05:00 | 210.94 | 200.42
2017-07-28 05:30 | 213.07 | 202.27
2017-07-28 06:00 | 216.78 | 206.02
2017-07-28 06:30 | 236.54 | 226.09
2017-07-28 07:00 | 246.51 | 236.72
2017-07-28 07:30 | 249.72 | 239.81
2017-07-28 08:00 | 248.86 | 238.67
2017-07-28 08:30 | 244.09 | 233.84
2017-07-28 09:00 | 239.07 | 228.57
2017-07-28 09:30 | 234.36 | 222.68
2017-07-28 10:00 | 231.78 | 219.8
2017-07-28 10:30 | 231.12 | 218.97
2017-07-28 11:00 | 230.67 | 218.89
2017-07-28 11:30 | 229.66 | 217.37
2017-07-28 12:00 | 229.54 | 216.78
2017-07-28 12:30 | 228.03 | 215.35
2017-07-28 13:00 | 226.76 | 213.4
2017-07-28 13:30 | 225.51 | 212.08
2017-07-28 14:00 | 225.31 | 211.94
2017-07-28 14:30 | 226.42 | 213.33
2017-07-28 15:00 | 227.65 | 214.54
2017-07-28 15:30 | 227.98 | 214.7
2017-07-28 16:00 | 229.76 | 216.38
2017-07-28 16:30 | 230.76 | 217.22
2017-07-28 17:00 | 231.57 | 218.29
2017-07-28 17:30 | 232.97 | 219.72
2017-07-28 18:00 | 233.13 | 219.46
2017-07-28 18:30 | 236.99 | 223.55
2017-07-28 19:00 | 237.9 | 224.56
2017-07-28 19:30 | 238.11 | 224.65
2017-07-28 20:00 | 238.59 | 225.27
2017-07-28 20:30 | 239.71 | 226.89
2017-07-28 21:00 | 239.21 | 226.08
2017-07-28 21:30 | 238.12 | 225.82
2017-07-28 22:00 | 236.68 | 224.86
2017-07-28 22:30 | 236.08 | 224.12
2017-07-28 23:00 | 234.39 | 222.75
2017-07-28 23:30 | 233.57 | 221.77
2017-07-29 | 232.43 | 220.53
2017-07-29 00:30 | 231.79 | 220.34
2017-07-29 01:00 | 231.12 | 219.87
2017-07-29 01:30 | 228.44 | 218.42
2017-07-29 02:00 | 211.36 | 201.58
2017-07-29 02:30 | 205.95 | 196.26
2017-07-29 03:00 | 205.91 | 196.27
2017-07-29 03:30 | 206.78 | 197.28
2017-07-29 04:00 | 207.39 | 197.63
2017-07-29 04:30 | 207.9 | 198.46
2017-07-29 05:00 | 208.29 | 199.18
2017-07-29 05:30 | 208.46 | 199.86
2017-07-29 06:00 | 210.39 | 201.99
2017-07-29 06:30 | 222.83 | 213.4
2017-07-29 07:00 | 227.12 | 217.38
2017-07-29 07:30 | 229.61 | 218.75
2017-07-29 08:00 | 229.99 | 218.44
2017-07-29 08:30 | 232.55 | 221.45
2017-07-29 09:00 | 235.35 | 224.01
2017-07-29 09:30 | 233.31 | 221.84
2017-07-29 10:00 | 233.34 | 221.5
2017-07-29 10:30 | 226.37 | 213.93
2017-07-29 11:00 | 208.3 | 195.66
2017-07-29 11:30 | 207.41 | 194.74
2017-07-29 12:00 | 206.13 | 193.87
2017-07-29 12:30 | 205.36 | 193.18
2017-07-29 13:00 | 203.76 | 192.3
2017-07-29 13:30 | 203.01 | 191.74
2017-07-29 14:00 | 201.83 | 190.18
2017-07-29 14:30 | 200.57 | 188.86
2017-07-29 15:00 | 200.36 | 189.07
2017-07-29 15:30 | 201.04 | 189.75
2017-07-29 16:00 | 202.24 | 190.95
2017-07-29 16:30 | 220.22 | 208.84
2017-07-29 17:00 | 226.2 | 215.04
2017-07-29 17:30 | 229.58 | 217.6
2017-07-29 18:00 | 232.43 | 220.54
2017-07-29 18:30 | 236.34 | 224.15
2017-07-29 19:00 | 237.55 | 225.37
2017-07-29 19:30 | 236.75 | 224.56
2017-07-29 20:00 | 235.4 | 223.27
2017-07-29 20:30 | 235.33 | 223.19
2017-07-29 21:00 | 233.97 | 221.43
2017-07-29 21:30 | 232.54 | 220.86
2017-07-29 22:00 | 231.59 | 220.81
2017-07-29 22:30 | 230.53 | 219.66
2017-07-29 23:00 | 228.06 | 216.97
2017-07-29 23:30 | 226.69 | 215.77
2017-07-30 | 225.37 | 214.81
2017-07-30 00:30 | 225.58 | 215.37
2017-07-30 01:00 | 224.67 | 214.95
2017-07-30 01:30 | 224.35 | 214.36
2017-07-30 02:00 | 209.3 | 198.35
2017-07-30 02:30 | 203.96 | 192.7
2017-07-30 03:00 | 203.85 | 192.04
2017-07-30 03:30 | 203.57 | 191.49
2017-07-30 04:00 | 202.58 | 191.24
2017-07-30 04:30 | 202.99 | 192.41
2017-07-30 05:00 | 203.49 | 193.01
2017-07-30 05:30 | 204.15 | 193.91
2017-07-30 06:00 | 205.39 | 195.47
2017-07-30 06:30 | 206.07 | 197.09
2017-07-30 07:00 | 207.93 | 199.11
2017-07-30 07:30 | 209.7 | 200.58
2017-07-30 08:00 | 211.05 | 201.06
2017-07-30 08:30 | 209.85 | 199.6
2017-07-30 09:00 | 207.76 | 197.89
2017-07-30 09:30 | 205.26 | 195.51
2017-07-30 10:00 | 205.91 | 193.32
2017-07-30 10:30 | 170.42 | 156.74
2017-07-30 11:00 | 162.8 | 148.98
2017-07-30 11:30 | 163.43 | 150.71
2017-07-30 12:00 | 162.84 | 150.81
2017-07-30 12:30 | 162.6 | 150.6
2017-07-30 13:00 | 186.33 | 174.73
2017-07-30 13:30 | 201.82 | 190.74
2017-07-30 14:00 | 200.69 | 189.69
2017-07-30 14:30 | 199.35 | 188.4
2017-07-30 15:00 | 200.46 | 188.61
2017-07-30 15:30 | 202.44 | 189.93
2017-07-30 16:00 | 219.53 | 207.93
2017-07-30 16:30 | 225.52 | 213.35
2017-07-30 17:00 | 227.47 | 215.29
2017-07-30 17:30 | 230.23 | 217.67
2017-07-30 18:00 | 233.35 | 220.63
2017-07-30 18:30 | 237.3 | 224.55
2017-07-30 19:00 | 238.29 | 225.12
2017-07-30 19:30 | 237.54 | 224.05
2017-07-30 20:00 | 235.94 | 222.34
2017-07-30 20:30 | 235.16 | 221.46
2017-07-30 21:00 | 234.32 | 220.47
2017-07-30 21:30 | 233.54 | 220.42
2017-07-30 22:00 | 232.29 | 219.45
2017-07-30 22:30 | 230.43 | 217.83
2017-07-30 23:00 | 228.8 | 216.08
2017-07-30 23:30 | 228.41 | 215.58
2017-07-31 | 228 | 214.89
2017-07-31 00:30 | 226.95 | 214.58
2017-07-31 01:00 | 225.54 | 213.73
2017-07-31 01:30 | 224.83 | 213.43
2017-07-31 02:00 | 222.7 | 211.36
2017-07-31 02:30 | 220.37 | 208.91
2017-07-31 03:00 | 220.08 | 208.6
2017-07-31 03:30 | 220 | 208.61
2017-07-31 04:00 | 220.04 | 208.84
2017-07-31 04:30 | 221.51 | 209.75
2017-07-31 05:00 | 223.47 | 211.3
2017-07-31 05:30 | 224.29 | 212.52
2017-07-31 06:00 | 227.47 | 215.87
2017-07-31 06:30 | 230.67 | 219.07
2017-07-31 07:00 | 234.93 | 223
2017-07-31 07:30 | 238.74 | 225.36
2017-07-31 08:00 | 239.37 | 225.61
2017-07-31 08:30 | 236.74 | 222.9
2017-07-31 09:00 | 234.12 | 220.09
2017-07-31 09:30 | 229.23 | 215.18
2017-07-31 10:00 | 227.69 | 213.42
2017-07-31 10:30 | 226.46 | 212.29
2017-07-31 11:00 | 226.29 | 211.29
2017-07-31 11:30 | 225.91 | 210.66
2017-07-31 12:00 | 226.7 | 211.14
2017-07-31 12:30 | 227.45 | 211.6
2017-07-31 13:00 | 228.09 | 212.32
2017-07-31 13:30 | 227.21 | 211.37
2017-07-31 14:00 | 226.63 | 211.69
2017-07-31 14:30 | 226.51 | 211.33
2017-07-31 15:00 | 226.6 | 211.25
2017-07-31 15:30 | 226.78 | 211.37
2017-07-31 16:00 | 227.46 | 212.02
2017-07-31 16:30 | 228.27 | 212.65
2017-07-31 17:00 | 229.45 | 213.55
2017-07-31 17:30 | 230.63 | 214.93
2017-07-31 18:00 | 226.25 | 210.95
2017-07-31 18:30 | 226.71 | 215.63
2017-07-31 19:00 | 239.26 | 230.42
2017-07-31 19:30 | 240.16 | 231.54
2017-07-31 20:00 | 241.44 | 233.17
2017-07-31 20:30 | 236.6 | 221.48
2017-07-31 21:00 | 236.51 | 219.96
2017-07-31 21:30 | 234.49 | 218.74
2017-07-31 22:00 | 232.94 | 217.59
2017-07-31 22:30 | 230.59 | 216.17
2017-07-31 23:00 | 228.91 | 214.54
2017-07-31 23:30 | 228.06 | 213.72
2017-08-01 | 227.72 | 212.42
2017-08-01 00:30 | 226.6 | 211.87
2017-08-01 01:00 | 224.73 | 210.7
2017-08-01 01:30 | 224.8 | 210.68
2017-08-01 02:00 | 224.8 | 210.58
2017-08-01 02:30 | 224.97 | 210.64
2017-08-01 03:00 | 225.78 | 211.08
2017-08-01 03:30 | 225.46 | 211.31
2017-08-01 04:00 | 224.75 | 210.9
2017-08-01 04:30 | 226.61 | 212.71
2017-08-01 05:00 | 227.4 | 214.06
2017-08-01 05:30 | 229.43 | 215.97
2017-08-01 06:00 | 234.22 | 219.69
2017-08-01 06:30 | 238.16 | 223.5
2017-08-01 07:00 | 241.5 | 227.38
2017-08-01 07:30 | 243.01 | 230.04
2017-08-01 08:00 | 244.03 | 232.81
2017-08-01 08:30 | 246.68 | 235
2017-08-01 09:00 | 245.77 | 233.71
2017-08-01 09:30 | 239.44 | 226.47
2017-08-01 10:00 | 229.69 | 217.28
2017-08-01 10:30 | 228.58 | 216.21
2017-08-01 11:00 | 225.95 | 213.6
2017-08-01 11:30 | 222.35 | 209.89
2017-08-01 12:00 | 219.21 | 206.63
2017-08-01 12:30 | 219.91 | 206.74
2017-08-01 13:00 | 219.97 | 206.48
2017-08-01 13:30 | 219.97 | 206.4
2017-08-01 14:00 | 220.15 | 206.71
2017-08-01 14:30 | 220.08 | 206.85
2017-08-01 15:00 | 220.14 | 206.82
2017-08-01 15:30 | 220.58 | 207.31
2017-08-01 16:00 | 222.43 | 208.86
2017-08-01 16:30 | 224.02 | 209.91
2017-08-01 17:00 | 225.99 | 211.58
2017-08-01 17:30 | 230.78 | 221.45
2017-08-01 18:00 | 237.63 | 231.24
2017-08-01 18:30 | 236.06 | 229.45
2017-08-01 19:00 | 234.6 | 227.9
2017-08-01 19:30 | 235.48 | 228.95
2017-08-01 20:00 | 236.45 | 230.17
2017-08-01 20:30 | 237.01 | 230.65
2017-08-01 21:00 | 214.59 | 204.01
2017-08-01 21:30 | 226.4 | 213.27
2017-08-01 22:00 | 230.92 | 217.82
2017-08-01 22:30 | 229.34 | 216.2
2017-08-01 23:00 | 226.96 | 213.58
2017-08-01 23:30 | 225.24 | 212.4
2017-08-02 | 223.08 | 210.36
2017-08-02 00:30 | 205.55 | 192.89
2017-08-02 01:00 | 200.52 | 188.89
2017-08-02 01:30 | 198.17 | 187.78
2017-08-02 02:00 | 197.31 | 187.25
2017-08-02 02:30 | 197.17 | 187.1
2017-08-02 03:00 | 197.48 | 187.3
2017-08-02 03:30 | 197.97 | 187.38
2017-08-02 04:00 | 197.9 | 187.22
2017-08-02 04:30 | 198.71 | 188.24
2017-08-02 05:00 | 199.66 | 189.69
2017-08-02 05:30 | 201.62 | 192.18
2017-08-02 06:00 | 205.78 | 195.72
2017-08-02 06:30 | 223.18 | 212.77
2017-08-02 07:00 | 234.84 | 224.01
2017-08-02 07:30 | 238.07 | 227.2
2017-08-02 08:00 | 237.27 | 226.61
2017-08-02 08:30 | 233.31 | 222.42
2017-08-02 09:00 | 228.65 | 217.58
2017-08-02 09:30 | 225.22 | 213.69
2017-08-02 10:00 | 222.78 | 210.86
2017-08-02 10:30 | 220.62 | 208.36
2017-08-02 11:00 | 217.71 | 205.19
2017-08-02 11:30 | 217.32 | 204.65
2017-08-02 12:00 | 217.35 | 204.35
2017-08-02 12:30 | 216.52 | 203.5
2017-08-02 13:00 | 215.31 | 202.41
2017-08-02 13:30 | 215.33 | 202.16
2017-08-02 14:00 | 216.37 | 203.48
2017-08-02 14:30 | 215.93 | 202.86
2017-08-02 15:00 | 218.63 | 205.57
2017-08-02 15:30 | 220.08 | 206.81
2017-08-02 16:00 | 221.42 | 208.1
2017-08-02 16:30 | 222.26 | 208.76
2017-08-02 17:00 | 223.47 | 209.78
2017-08-02 17:30 | 224.82 | 211.32
2017-08-02 18:00 | 228.36 | 214.84
2017-08-02 18:30 | 233.21 | 219.15
2017-08-02 19:00 | 235.19 | 221.23
2017-08-02 19:30 | 234.23 | 220.39
2017-08-02 20:00 | 232.89 | 219.11
2017-08-02 20:30 | 231.67 | 218.05
2017-08-02 21:00 | 230.01 | 216.3
2017-08-02 21:30 | 228.29 | 215.3
2017-08-02 22:00 | 225.28 | 213.45
2017-08-02 22:30 | 224.61 | 211.6
2017-08-02 23:00 | 222.65 | 209.5
2017-08-02 23:30 | 220.6 | 208.43
2017-08-03 | 218.23 | 206.19
2017-08-03 00:30 | 216.09 | 204.73
2017-08-03 01:00 | 214.84 | 203.74
2017-08-03 01:30 | 213.67 | 203.15
2017-08-03 02:00 | 213.03 | 203.07
2017-08-03 02:30 | 212.59 | 202.76
2017-08-03 03:00 | 212.38 | 202.58
2017-08-03 03:30 | 212.38 | 202.62
2017-08-03 04:00 | 212.76 | 203.03
2017-08-03 04:30 | 213.01 | 203.37
2017-08-03 05:00 | 213.97 | 204.24
2017-08-03 05:30 | 215.94 | 205.92
2017-08-03 06:00 | 218.65 | 207.86
2017-08-03 06:30 | 222.76 | 212.11
2017-08-03 07:00 | 225.05 | 214.79
2017-08-03 07:30 | 225.07 | 214.89
2017-08-03 08:00 | 220.31 | 210.08
2017-08-03 08:30 | 216.98 | 207.07
2017-08-03 09:00 | 214.56 | 204.38
2017-08-03 09:30 | 211.29 | 201.04
2017-08-03 10:00 | 209.37 | 199.52
2017-08-03 10:30 | 208.03 | 198.2
2017-08-03 11:00 | 207.39 | 197.06
2017-08-03 11:30 | 208.94 | 198.65
2017-08-03 12:00 | 208.9 | 198.33
2017-08-03 12:30 | 209.61 | 198.42
2017-08-03 13:00 | 209.5 | 198.21
2017-08-03 13:30 | 209.44 | 198.09
2017-08-03 14:00 | 209.6 | 198.5
2017-08-03 14:30 | 210.11 | 198.98
2017-08-03 15:00 | 211.35 | 200.23
2017-08-03 15:30 | 213.97 | 202.86
2017-08-03 16:00 | 215.23 | 204.53
2017-08-03 16:30 | 214.68 | 203.78
2017-08-03 17:00 | 217.46 | 206.76
2017-08-03 17:30 | 221.35 | 210.34
2017-08-03 18:00 | 225.53 | 214.45
2017-08-03 18:30 | 229.57 | 218.66
2017-08-03 19:00 | 231.31 | 219.89
2017-08-03 19:30 | 230.68 | 218.96
2017-08-03 20:00 | 231.49 | 219.8
2017-08-03 20:30 | 232.42 | 220.76
2017-08-03 21:00 | 232.38 | 220.44
2017-08-03 21:30 | 230.13 | 218.59
2017-08-03 22:00 | 227.97 | 216.66
2017-08-03 22:30 | 225.6 | 214.53
2017-08-03 23:00 | 221.26 | 209.74
2017-08-03 23:30 | 219.19 | 207.55
2017-08-04 | 218.54 | 206.27
2017-08-04 00:30 | 217.2 | 205.5
2017-08-04 01:00 | 215.63 | 204.37
2017-08-04 01:30 | 213.88 | 202.84
2017-08-04 02:00 | 213.31 | 202.42
2017-08-04 02:30 | 213.32 | 202.28
2017-08-04 03:00 | 213.32 | 202.28
2017-08-04 03:30 | 213.11 | 202.09
2017-08-04 04:00 | 213.3 | 202.2
2017-08-04 04:30 | 213.53 | 202.54
2017-08-04 05:00 | 214.96 | 204.27
2017-08-04 05:30 | 216.77 | 206.02
2017-08-04 06:00 | 221.46 | 209.76
2017-08-04 06:30 | 225.77 | 213.95
2017-08-04 07:00 | 231.54 | 219.81
2017-08-04 07:30 | 236.76 | 225.49
2017-08-04 08:00 | 234.44 | 225.63
2017-08-04 08:30 | 229.36 | 220.49
2017-08-04 09:00 | 226.95 | 217.45
2017-08-04 09:30 | 222.56 | 213.06
2017-08-04 10:00 | 220.3 | 210.74
2017-08-04 10:30 | 218.83 | 208.88
2017-08-04 11:00 | 217.53 | 207.51
2017-08-04 11:30 | 216.01 | 205.7
2017-08-04 12:00 | 215.3 | 203.87
2017-08-04 12:30 | 215.11 | 203.52
2017-08-04 13:00 | 215.5 | 203.74
2017-08-04 13:30 | 214.8 | 202.86
2017-08-04 14:00 | 215.68 | 203.41
2017-08-04 14:30 | 216.07 | 203.45
2017-08-04 15:00 | 216.76 | 204.07
2017-08-04 15:30 | 217.64 | 205.26
2017-08-04 16:00 | 216.4 | 204.39
2017-08-04 16:30 | 217.27 | 205.47
2017-08-04 17:00 | 218.73 | 207.07
2017-08-04 17:30 | 219.46 | 206.77
2017-08-04 18:00 | 222.71 | 209.97
2017-08-04 18:30 | 226.6 | 213.72
2017-08-04 19:00 | 225.17 | 212.08
2017-08-04 19:30 | 222.86 | 209.54
2017-08-04 20:00 | 222.63 | 209.51
2017-08-04 20:30 | 224.82 | 211.74
2017-08-04 21:00 | 223.69 | 210.52
2017-08-04 21:30 | 222.03 | 210
2017-08-04 22:00 | 219.58 | 207.51
2017-08-04 22:30 | 218.19 | 205.43
2017-08-04 23:00 | 216.12 | 202.79
2017-08-04 23:30 | 214.61 | 201.69
2017-08-05 | 214.25 | 201.5
2017-08-05 00:30 | 214.03 | 201.08
2017-08-05 01:00 | 214.05 | 200.62
2017-08-05 01:30 | 211.34 | 200.31
2017-08-05 02:00 | 208.71 | 199.11
2017-08-05 02:30 | 206.77 | 197.58
2017-08-05 03:00 | 205.98 | 197.14
2017-08-05 03:30 | 205.89 | 197.43
2017-08-05 04:00 | 205.98 | 197.53
2017-08-05 04:30 | 206.18 | 196.5
2017-08-05 05:00 | 208.2 | 197.34
2017-08-05 05:30 | 208.99 | 198.75
2017-08-05 06:00 | 210.31 | 200.87
2017-08-05 06:30 | 211.82 | 202.95
2017-08-05 07:00 | 214.91 | 206.28
2017-08-05 07:30 | 218.51 | 208.65
2017-08-05 08:00 | 218.68 | 208.15
2017-08-05 08:30 | 216.65 | 206.25
2017-08-05 09:00 | 214.94 | 202.53
2017-08-05 09:30 | 211.4 | 199.62
2017-08-05 10:00 | 208.06 | 196.32
2017-08-05 10:30 | 204.2 | 191.45
2017-08-05 11:00 | 187.06 | 173.55
2017-08-05 11:30 | 181.65 | 169.63
2017-08-05 12:00 | 181.25 | 169.36
2017-08-05 12:30 | 180.04 | 168.66
2017-08-05 13:00 | 179.23 | 168.2
2017-08-05 13:30 | 178.31 | 167.12
2017-08-05 14:00 | 178.52 | 167.05
2017-08-05 14:30 | 177.9 | 166.56
2017-08-05 15:00 | 176.69 | 164.08
2017-08-05 15:30 | 180.41 | 167.52
2017-08-05 16:00 | 181.81 | 169.2
2017-08-05 16:30 | 198.8 | 186.59
2017-08-05 17:00 | 205.4 | 193.63
2017-08-05 17:30 | 208.24 | 196.77
2017-08-05 18:00 | 212.71 | 201.1
2017-08-05 18:30 | 216.46 | 205
2017-08-05 19:00 | 215.97 | 204.57
2017-08-05 19:30 | 216.72 | 204.42
2017-08-05 20:00 | 216.2 | 203.94
2017-08-05 20:30 | 215.76 | 203.81
2017-08-05 21:00 | 215.25 | 203.01
2017-08-05 21:30 | 215.4 | 203.19
2017-08-05 22:00 | 214.52 | 201.85
2017-08-05 22:30 | 213 | 200.02
2017-08-05 23:00 | 210.85 | 198.36
2017-08-05 23:30 | 210.49 | 198.03
2017-08-06 | 209.27 | 197.39
2017-08-06 00:30 | 208.19 | 196.85
2017-08-06 01:00 | 187.36 | 176.5
2017-08-06 01:30 | 184.56 | 174.05
2017-08-06 02:00 | 184.22 | 173.57
2017-08-06 02:30 | 184.09 | 173.32
2017-08-06 03:00 | 183.74 | 172.89
2017-08-06 03:30 | 184.29 | 173.27
2017-08-06 04:00 | 185.4 | 174.66
2017-08-06 04:30 | 185.67 | 174.94
2017-08-06 05:00 | 187.49 | 177.2
2017-08-06 05:30 | 188.48 | 178.32
2017-08-06 06:00 | 189.32 | 179.15
2017-08-06 06:30 | 190.86 | 181.06
2017-08-06 07:00 | 192.83 | 183.42
2017-08-06 07:30 | 194.74 | 185.63
2017-08-06 08:00 | 194.71 | 185.25
2017-08-06 08:30 | 192.6 | 183.08
2017-08-06 09:00 | 190.19 | 180.27
2017-08-06 09:30 | 188.13 | 177.91
2017-08-06 10:00 | 185.57 | 174.72
2017-08-06 10:30 | 178.56 | 166.99
2017-08-06 11:00 | 174.98 | 163.11
2017-08-06 11:30 | 176.11 | 164.5
2017-08-06 12:00 | 175.09 | 163.51
2017-08-06 12:30 | 173.76 | 162.07
2017-08-06 13:00 | 172.7 | 161.38
2017-08-06 13:30 | 173.53 | 162.26
2017-08-06 14:00 | 173.54 | 162.08
2017-08-06 14:30 | 172.65 | 161.17
2017-08-06 15:00 | 173.57 | 162.24
2017-08-06 15:30 | 174.55 | 163.43
2017-08-06 16:00 | 175.17 | 164.46
2017-08-06 16:30 | 181.71 | 171.19
2017-08-06 17:00 | 200.43 | 187.28
2017-08-06 17:30 | 208.18 | 195.29
2017-08-06 18:00 | 211.87 | 203.78
2017-08-06 18:30 | 221.56 | 215.7
2017-08-06 19:00 | 218.75 | 212.91
2017-08-06 19:30 | 217.83 | 212.07
2017-08-06 20:00 | 214.48 | 203.69
2017-08-06 20:30 | 216.43 | 204.19
2017-08-06 21:00 | 215.6 | 203.14
2017-08-06 21:30 | 215.14 | 202.59
2017-08-06 22:00 | 213.89 | 201.04
2017-08-06 22:30 | 212.35 | 198.95
2017-08-06 23:00 | 210.55 | 196.95
2017-08-06 23:30 | 209.25 | 196.11
2017-08-07 | 206.98 | 195.06
2017-08-07 00:30 | 151.18 | 139.54
2017-08-07 01:00 | 150.13 | 138.35
2017-08-07 01:30 | 150.06 | 138.18
2017-08-07 02:00 | 150.77 | 138.38
2017-08-07 02:30 | 150.74 | 138.21
2017-08-07 03:00 | 150.93 | 138.35
2017-08-07 03:30 | 151.18 | 138.61
2017-08-07 04:00 | 151.48 | 139.11
2017-08-07 04:30 | 151.37 | 139
2017-08-07 05:00 | 151.77 | 139.81
2017-08-07 05:30 | 153.97 | 142.54
2017-08-07 06:00 | 156.48 | 145.64
2017-08-07 06:30 | 160.46 | 150.72
2017-08-07 07:00 | 165.42 | 155.85
2017-08-07 07:30 | 168.77 | 159.41
2017-08-07 08:00 | 168.7 | 159.21
2017-08-07 08:30 | 164.64 | 154.97
2017-08-07 09:00 | 155.08 | 145.28
2017-08-07 09:30 | 158.12 | 151.03
2017-08-07 10:00 | 182.03 | 175.98
2017-08-07 10:30 | 177.61 | 171.3
2017-08-07 11:00 | 179.27 | 173.21
2017-08-07 11:30 | 177.85 | 171.32
2017-08-07 12:00 | 150.74 | 140.77
2017-08-07 12:30 | 137.57 | 125.93
2017-08-07 13:00 | 143.21 | 130.49
2017-08-07 13:30 | 158.09 | 146.46
2017-08-07 14:00 | 180.95 | 170.8
2017-08-07 14:30 | 196.88 | 187.3
2017-08-07 15:00 | 203.06 | 193.43
2017-08-07 15:30 | 204.83 | 194.71
2017-08-07 16:00 | 206.54 | 195.97
2017-08-07 16:30 | 208.18 | 197.36
2017-08-07 17:00 | 209.85 | 199.1
2017-08-07 17:30 | 212.36 | 201.67
2017-08-07 18:00 | 217.24 | 207.01
2017-08-07 18:30 | 224.08 | 214.29
2017-08-07 19:00 | 225.84 | 216
2017-08-07 19:30 | 225.23 | 215.42
2017-08-07 20:00 | 224.6 | 214.98
2017-08-07 20:30 | 223.2 | 213.58
2017-08-07 21:00 | 218.67 | 208.45
2017-08-07 21:30 | 216.44 | 206.71
2017-08-07 22:00 | 214.93 | 205.08
2017-08-07 22:30 | 213.67 | 203.16
2017-08-07 23:00 | 211.76 | 201.26
2017-08-07 23:30 | 210.76 | 200.54
2017-08-08 | 209.32 | 199.64
2017-08-08 00:30 | 209.05 | 199.47
2017-08-08 01:00 | 208.37 | 198.95
2017-08-08 01:30 | 207.85 | 198.8
2017-08-08 02:00 | 206.78 | 198.75
2017-08-08 02:30 | 206.44 | 198.37
2017-08-08 03:00 | 206.75 | 198.51
2017-08-08 03:30 | 207.08 | 198.61
2017-08-08 04:00 | 207.56 | 198.95
2017-08-08 04:30 | 207.73 | 199.55
2017-08-08 05:00 | 208.38 | 200.87
2017-08-08 05:30 | 211.69 | 204.36
2017-08-08 06:00 | 216.04 | 208.49
2017-08-08 06:30 | 222.17 | 214.1
2017-08-08 07:00 | 225.25 | 217.56
2017-08-08 07:30 | 226.92 | 218.67
2017-08-08 08:00 | 225.72 | 217.83
2017-08-08 08:30 | 221.35 | 213.14
2017-08-08 09:00 | 217.86 | 209.19
2017-08-08 09:30 | 213.88 | 204.83
2017-08-08 10:00 | 211.89 | 202.71
2017-08-08 10:30 | 208.39 | 198.78
2017-08-08 11:00 | 206.6 | 196.99
2017-08-08 11:30 | 205.05 | 195.29
2017-08-08 12:00 | 205.54 | 195.74
2017-08-08 12:30 | 204.3 | 194.47
2017-08-08 13:00 | 204.99 | 194.87
2017-08-08 13:30 | 204.75 | 194.59
2017-08-08 14:00 | 205.08 | 194.72
2017-08-08 14:30 | 205.38 | 195.12
2017-08-08 15:00 | 204.83 | 194.54
2017-08-08 15:30 | 206.01 | 195.59
2017-08-08 16:00 | 206.54 | 196.03
2017-08-08 16:30 | 208.93 | 197.68
2017-08-08 17:00 | 211.53 | 199.75
2017-08-08 17:30 | 214.64 | 203.33
2017-08-08 18:00 | 219.66 | 208.35
2017-08-08 18:30 | 223.49 | 212.52
2017-08-08 19:00 | 226.13 | 215.25
2017-08-08 19:30 | 226.58 | 215.75
2017-08-08 20:00 | 225.84 | 215.13
2017-08-08 20:30 | 225.22 | 214.6
2017-08-08 21:00 | 224.85 | 214.24
2017-08-08 21:30 | 222.49 | 212.97
2017-08-08 22:00 | 219.87 | 210.49
2017-08-08 22:30 | 217.51 | 207.85
2017-08-08 23:00 | 215.85 | 205.62
2017-08-08 23:30 | 213.79 | 203.58
2017-08-09 | 212.34 | 202.19
2017-08-09 00:30 | 211.52 | 202
2017-08-09 01:00 | 209.97 | 200.57
2017-08-09 01:30 | 208.61 | 200.62
2017-08-09 02:00 | 207.64 | 199.76
2017-08-09 02:30 | 208.21 | 200.23
2017-08-09 03:00 | 208.22 | 200.17
2017-08-09 03:30 | 209.14 | 200.9
2017-08-09 04:00 | 210.02 | 202.16
2017-08-09 04:30 | 209.7 | 202.12
2017-08-09 05:00 | 212.06 | 204.57
2017-08-09 05:30 | 215.57 | 208.27
2017-08-09 06:00 | 220.23 | 211.96
2017-08-09 06:30 | 224.69 | 217.41
2017-08-09 07:00 | 229.24 | 221.66
2017-08-09 07:30 | 232.23 | 224.84
2017-08-09 08:00 | 231.1 | 223.76
2017-08-09 08:30 | 226.44 | 219.09
2017-08-09 09:00 | 222.56 | 214.52
2017-08-09 09:30 | 217.54 | 209.22
2017-08-09 10:00 | 214.31 | 205.55
2017-08-09 10:30 | 211.3 | 201.67
2017-08-09 11:00 | 209.95 | 200.15
2017-08-09 11:30 | 208.25 | 198.48
2017-08-09 12:00 | 207.65 | 197.7
2017-08-09 12:30 | 209.26 | 199.2
2017-08-09 13:00 | 211.93 | 201.84
2017-08-09 13:30 | 211.56 | 201.52
2017-08-09 14:00 | 205.12 | 195.01
2017-08-09 14:30 | 205.36 | 194.67
2017-08-09 15:00 | 205.75 | 194.63
2017-08-09 15:30 | 206.33 | 195.11
2017-08-09 16:00 | 207.19 | 196.11
2017-08-09 16:30 | 208.26 | 196.8
2017-08-09 17:00 | 210.22 | 198.66
2017-08-09 17:30 | 212.56 | 201.15
2017-08-09 18:00 | 217.05 | 206.09
2017-08-09 18:30 | 221.76 | 211.09
2017-08-09 19:00 | 222 | 211.63
2017-08-09 19:30 | 221.51 | 211.01
2017-08-09 20:00 | 220.92 | 210.38
2017-08-09 20:30 | 220.33 | 209.79
2017-08-09 21:00 | 219.44 | 208.93
2017-08-09 21:30 | 216.8 | 207.7
2017-08-09 22:00 | 214.66 | 205.92
2017-08-09 22:30 | 212.79 | 203.41
2017-08-09 23:00 | 210.97 | 201.46
2017-08-09 23:30 | 209.71 | 200.4
2017-08-10 | 208.02 | 198.86
2017-08-10 00:30 | 206.83 | 198.9
2017-08-10 01:00 | 204.93 | 197.59
2017-08-10 01:30 | 187.41 | 180.68
2017-08-10 02:00 | 181.51 | 174.79
2017-08-10 02:30 | 180.75 | 173.96
2017-08-10 03:00 | 181.27 | 174.46
2017-08-10 03:30 | 181.68 | 174.41
2017-08-10 04:00 | 181.87 | 174.55
2017-08-10 04:30 | 183.98 | 176.41
2017-08-10 05:00 | 186.14 | 179.01
2017-08-10 05:30 | 189.76 | 182.18
2017-08-10 06:00 | 194.62 | 186.14
2017-08-10 06:30 | 214.48 | 206.57
2017-08-10 07:00 | 224.26 | 216.41
2017-08-10 07:30 | 226.78 | 218.8
2017-08-10 08:00 | 225.61 | 217.62
2017-08-10 08:30 | 220.31 | 212.28
2017-08-10 09:00 | 215.6 | 207.19
2017-08-10 09:30 | 211.3 | 201.94
2017-08-10 10:00 | 208.17 | 198.66
2017-08-10 10:30 | 207.85 | 198.41
2017-08-10 11:00 | 208.43 | 199.3
2017-08-10 11:30 | 206.64 | 197.26
2017-08-10 12:00 | 205.49 | 196.07
2017-08-10 12:30 | 204.87 | 194.9
2017-08-10 13:00 | 204.92 | 194.46
2017-08-10 13:30 | 204.99 | 194.15
2017-08-10 14:00 | 205.55 | 194.53
2017-08-10 14:30 | 204.4 | 193.9
2017-08-10 15:00 | 204.5 | 194.17
2017-08-10 15:30 | 205.96 | 195.39
2017-08-10 16:00 | 206.65 | 196.4
2017-08-10 16:30 | 208.05 | 197.27
2017-08-10 17:00 | 209.42 | 198.55
2017-08-10 17:30 | 211.46 | 200.38
2017-08-10 18:00 | 214.89 | 203.87
2017-08-10 18:30 | 219.02 | 207.95
2017-08-10 19:00 | 221.08 | 210.09
2017-08-10 19:30 | 220.46 | 209.17
2017-08-10 20:00 | 219.76 | 208.53
2017-08-10 20:30 | 219.08 | 207.98
2017-08-10 21:00 | 217.98 | 206.77
2017-08-10 21:30 | 215.11 | 205.84
2017-08-10 22:00 | 213.31 | 204.49
2017-08-10 22:30 | 211.93 | 202.23
2017-08-10 23:00 | 210.38 | 200.42
2017-08-10 23:30 | 208.65 | 199.09
2017-08-11 | 207.5 | 198.05
2017-08-11 00:30 | 206.39 | 197.4
2017-08-11 01:00 | 204.71 | 196.62
2017-08-11 01:30 | 187.47 | 179.31
2017-08-11 02:00 | 180.01 | 172.15
2017-08-11 02:30 | 179.01 | 171.25
2017-08-11 03:00 | 178.97 | 171.24
2017-08-11 03:30 | 179.64 | 171.39
2017-08-11 04:00 | 180.53 | 171.85
2017-08-11 04:30 | 181.5 | 172.71
2017-08-11 05:00 | 182.84 | 174.18
2017-08-11 05:30 | 184.17 | 176.42
2017-08-11 06:00 | 187.26 | 179.38
2017-08-11 06:30 | 207.99 | 199.83
2017-08-11 07:00 | 216.23 | 208.49
2017-08-11 07:30 | 218.56 | 210.4
2017-08-11 08:00 | 217.23 | 208.82
2017-08-11 08:30 | 213.43 | 205.15
2017-08-11 09:00 | 208.84 | 200.81
2017-08-11 09:30 | 205.22 | 196.7
2017-08-11 10:00 | 203.61 | 194.83
2017-08-11 10:30 | 204.11 | 195.16
2017-08-11 11:00 | 186.98 | 177.63
2017-08-11 11:30 | 180.99 | 171.35
2017-08-11 12:00 | 180.31 | 170.51
2017-08-11 12:30 | 179.32 | 169.39
2017-08-11 13:00 | 179.69 | 169.26
2017-08-11 13:30 | 180.11 | 169.64
2017-08-11 14:00 | 181.03 | 170.18
2017-08-11 14:30 | 181.4 | 170.66
2017-08-11 15:00 | 181.27 | 170.7
2017-08-11 15:30 | 181.35 | 171.04
2017-08-11 16:00 | 182.23 | 172.01
2017-08-11 16:30 | 199.82 | 189.24
2017-08-11 17:00 | 206.73 | 196.05
2017-08-11 17:30 | 207.91 | 197.23
2017-08-11 18:00 | 210.05 | 199.43
2017-08-11 18:30 | 212.68 | 202.1
2017-08-11 19:00 | 213.68 | 203.02
2017-08-11 19:30 | 213.17 | 202.56
2017-08-11 20:00 | 212.12 | 201.42
2017-08-11 20:30 | 211.61 | 201.07
2017-08-11 21:00 | 210.76 | 200.29
2017-08-11 21:30 | 209.67 | 200.09
2017-08-11 22:00 | 207.81 | 198.58
2017-08-11 22:30 | 207.85 | 197.71
2017-08-11 23:00 | 206.43 | 196.15
2017-08-11 23:30 | 206.02 | 195.66
2017-08-12 | 204.77 | 194.53
2017-08-12 00:30 | 202.42 | 193.27
2017-08-12 01:00 | 202.24 | 193.11
2017-08-12 01:30 | 200.5 | 192.6
2017-08-12 02:00 | 200.68 | 192.27
2017-08-12 02:30 | 200.54 | 192.14
2017-08-12 03:00 | 199.64 | 192.09
2017-08-12 03:30 | 199.73 | 192.12
2017-08-12 04:00 | 199.85 | 192.19
2017-08-12 04:30 | 199.85 | 192.25
2017-08-12 05:00 | 200.45 | 193.06
2017-08-12 05:30 | 201.46 | 194.55
2017-08-12 06:00 | 201.92 | 195.51
2017-08-12 06:30 | 201.82 | 195.44
2017-08-12 07:00 | 203.24 | 196.33
2017-08-12 07:30 | 203.97 | 197.6
2017-08-12 08:00 | 204.56 | 197.78
2017-08-12 08:30 | 204.8 | 196.94
2017-08-12 09:00 | 208.29 | 200.35
2017-08-12 09:30 | 192.29 | 184.33
2017-08-12 10:00 | 185.83 | 177.56
2017-08-12 10:30 | 185.25 | 176.88
2017-08-12 11:00 | 183.4 | 175.28
2017-08-12 11:30 | 182.44 | 174.37
2017-08-12 12:00 | 182.35 | 174.01
2017-08-12 12:30 | 182.62 | 173.95
2017-08-12 13:00 | 182.07 | 173.46
2017-08-12 13:30 | 181.28 | 172.37
2017-08-12 14:00 | 180.77 | 171.48
2017-08-12 14:30 | 180.87 | 171.61
2017-08-12 15:00 | 181.95 | 172.9
2017-08-12 15:30 | 182.65 | 173.65
2017-08-12 16:00 | 184.24 | 175.78
2017-08-12 16:30 | 202.16 | 193.94
2017-08-12 17:00 | 207.85 | 199.47
2017-08-12 17:30 | 209.93 | 201.39
2017-08-12 18:00 | 212.11 | 203.57
2017-08-12 18:30 | 215.12 | 206.3
2017-08-12 19:00 | 215.97 | 207.22
2017-08-12 19:30 | 215.29 | 206.58
2017-08-12 20:00 | 214.16 | 205.41
2017-08-12 20:30 | 213.98 | 205.41
2017-08-12 21:00 | 213.22 | 204.43
2017-08-12 21:30 | 212.13 | 204.24
2017-08-12 22:00 | 210.85 | 203.23
2017-08-12 22:30 | 193.5 | 185.27
2017-08-12 23:00 | 187.85 | 179.29
2017-08-12 23:30 | 187.25 | 178.79
2017-08-13 | 185.9 | 178.48
2017-08-13 00:30 | 184.99 | 178.1
2017-08-13 01:00 | 183.06 | 176.72
2017-08-13 01:30 | 181.4 | 174.31
2017-08-13 02:00 | 181.05 | 173.7
2017-08-13 02:30 | 180.53 | 173.91
2017-08-13 03:00 | 180.51 | 173.79
2017-08-13 03:30 | 180.08 | 173.38
2017-08-13 04:00 | 180.66 | 174.09
2017-08-13 04:30 | 181.49 | 175.23
2017-08-13 05:00 | 182.88 | 176.56
2017-08-13 05:30 | 183.39 | 177.32
2017-08-13 06:00 | 184.89 | 179.07
2017-08-13 06:30 | 186.71 | 180.77
2017-08-13 07:00 | 189.05 | 182.87
2017-08-13 07:30 | 191.26 | 183.13
2017-08-13 08:00 | 190.46 | 182.48
2017-08-13 08:30 | 188.35 | 180.47
2017-08-13 09:00 | 186.46 | 178.5
2017-08-13 09:30 | 183.92 | 175.84
2017-08-13 10:00 | 185.07 | 176.75
2017-08-13 10:30 | 152.71 | 143.84
2017-08-13 11:00 | 139.43 | 130.11
2017-08-13 11:30 | 139.09 | 129.59
2017-08-13 12:00 | 138.19 | 128.8
2017-08-13 12:30 | 136.6 | 128.41
2017-08-13 13:00 | 139.05 | 128.41
2017-08-13 13:30 | 139.32 | 128.41
2017-08-13 14:00 | 139.77 | 128.54
2017-08-13 14:30 | 140.49 | 129.22
2017-08-13 15:00 | 140.66 | 129.39
2017-08-13 15:30 | 150.35 | 139.66
2017-08-13 16:00 | 185.59 | 176.08
2017-08-13 16:30 | 215.75 | 205.7
2017-08-13 17:00 | 223.73 | 213.44
2017-08-13 17:30 | 225.21 | 214.79
2017-08-13 18:00 | 225.93 | 215
2017-08-13 18:30 | 228.32 | 217.53
2017-08-13 19:00 | 230.02 | 219.08
2017-08-13 19:30 | 230.31 | 219.18
2017-08-13 20:00 | 229.71 | 218.66
2017-08-13 20:30 | 230.45 | 219.3
2017-08-13 21:00 | 228.66 | 218.1
2017-08-13 21:30 | 226.55 | 217.47
2017-08-13 22:00 | 225.61 | 216.47
2017-08-13 22:30 | 224.13 | 214.54
2017-08-13 23:00 | 222.47 | 213.06
2017-08-13 23:30 | 219.35 | 210.36
2017-08-14 | 216.15 | 207.37
2017-08-14 00:30 | 199.85 | 191.44
2017-08-14 01:00 | 193.11 | 184.95
2017-08-14 01:30 | 192.26 | 183.93
2017-08-14 02:00 | 190.48 | 182.23
2017-08-14 02:30 | 190.98 | 182.84
2017-08-14 03:00 | 190.99 | 182.89
2017-08-14 03:30 | 191.89 | 183.65
2017-08-14 04:00 | 193.06 | 184.94
2017-08-14 04:30 | 193.93 | 185.95
2017-08-14 05:00 | 194.85 | 187.05
2017-08-14 05:30 | 196.57 | 189.38
2017-08-14 06:00 | 199.58 | 192.08
2017-08-14 06:30 | 204.27 | 196.2
2017-08-14 07:00 | 225.02 | 216.65
2017-08-14 07:30 | 233.49 | 224.62
2017-08-14 08:00 | 231.73 | 222.6
2017-08-14 08:30 | 228.13 | 219.09
2017-08-14 09:00 | 224.41 | 215.07
2017-08-14 09:30 | 226.8 | 217.01
2017-08-14 10:00 | 226.09 | 215.96
2017-08-14 10:30 | 225.51 | 215.26
2017-08-14 11:00 | 225.16 | 215.05
2017-08-14 11:30 | 225.8 | 215.47
2017-08-14 12:00 | 226.69 | 216.3
2017-08-14 12:30 | 226.85 | 216.43
2017-08-14 13:00 | 226.93 | 216.51
2017-08-14 13:30 | 226.88 | 216.44
2017-08-14 14:00 | 226.81 | 216.58
2017-08-14 14:30 | 227.88 | 217.5
2017-08-14 15:00 | 229.51 | 219.04
2017-08-14 15:30 | 230.23 | 220.05
2017-08-14 16:00 | 230.78 | 220.78
2017-08-14 16:30 | 231.5 | 221.29
2017-08-14 17:00 | 233.17 | 222.79
2017-08-14 17:30 | 234.41 | 223.63
2017-08-14 18:00 | 236.63 | 225.86
2017-08-14 18:30 | 239.24 | 228.36
2017-08-14 19:00 | 241.63 | 230.7
2017-08-14 19:30 | 240.5 | 229.45
2017-08-14 20:00 | 238.44 | 227.54
2017-08-14 20:30 | 237.64 | 226.86
2017-08-14 21:00 | 236.43 | 225.72
2017-08-14 21:30 | 233.93 | 224.19
2017-08-14 22:00 | 232.35 | 222.77
2017-08-14 22:30 | 230.96 | 221.02
2017-08-14 23:00 | 226.91 | 217.05
2017-08-14 23:30 | 223.63 | 213.91
2017-08-15 | 222.65 | 212.88
2017-08-15 00:30 | 221.79 | 212.35
2017-08-15 01:00 | 221.27 | 212.17
2017-08-15 01:30 | 219.77 | 211.42
2017-08-15 02:00 | 219.58 | 211.41
2017-08-15 02:30 | 219.44 | 211.16
2017-08-15 03:00 | 218.74 | 210.39
2017-08-15 03:30 | 220.23 | 211.78
2017-08-15 04:00 | 220.02 | 211.65
2017-08-15 04:30 | 219.94 | 211.62
2017-08-15 05:00 | 220.99 | 212.81
2017-08-15 05:30 | 223.47 | 214.98
2017-08-15 06:00 | 227.76 | 218.13
2017-08-15 06:30 | 231.54 | 221.65
2017-08-15 07:00 | 235.73 | 224.99
2017-08-15 07:30 | 237.43 | 226.53
2017-08-15 08:00 | 234.95 | 224.26
2017-08-15 08:30 | 231.35 | 220.87
2017-08-15 09:00 | 231.11 | 220.86
2017-08-15 09:30 | 231.62 | 220.79
2017-08-15 10:00 | 229.28 | 218.29
2017-08-15 10:30 | 229.42 | 218.54
2017-08-15 11:00 | 228.72 | 217.93
2017-08-15 11:30 | 227.98 | 217.16
2017-08-15 12:00 | 228.88 | 218.15
2017-08-15 12:30 | 228.83 | 217.69
2017-08-15 13:00 | 229.95 | 218.49
2017-08-15 13:30 | 230.38 | 218.76
2017-08-15 14:00 | 231 | 219.3
2017-08-15 14:30 | 231.45 | 219.7
2017-08-15 15:00 | 231.54 | 219.73
2017-08-15 15:30 | 232.72 | 220.93
2017-08-15 16:00 | 233.27 | 222.13
2017-08-15 16:30 | 239.12 | 233.96
2017-08-15 17:00 | 240.02 | 234.81
2017-08-15 17:30 | 239.8 | 234.62
2017-08-15 18:00 | 239.87 | 234.55
2017-08-15 18:30 | 239.59 | 233.83
2017-08-15 19:00 | 239.3 | 233.64
2017-08-15 19:30 | 240.37 | 234.78
2017-08-15 20:00 | 241.7 | 236.22
2017-08-15 20:30 | 242.4 | 236.96
2017-08-15 21:00 | 236.78 | 225.39
2017-08-15 21:30 | 235.72 | 224.3
2017-08-15 22:00 | 233.49 | 222.5
2017-08-15 22:30 | 231.88 | 220.56
2017-08-15 23:00 | 230.27 | 218.81
2017-08-15 23:30 | 229.46 | 218.47
2017-08-16 | 228.5 | 217.76
2017-08-16 00:30 | 226.43 | 216.78
2017-08-16 01:00 | 224.9 | 215.03
2017-08-16 01:30 | 223.61 | 214.36
2017-08-16 02:00 | 223.4 | 214.01
2017-08-16 02:30 | 222.75 | 213.23
2017-08-16 03:00 | 222.38 | 213.42
2017-08-16 03:30 | 222.26 | 213.22
2017-08-16 04:00 | 222.2 | 213.17
2017-08-16 04:30 | 222.55 | 213.54
2017-08-16 05:00 | 223.29 | 214.33
2017-08-16 05:30 | 224.44 | 215.91
2017-08-16 06:00 | 226.78 | 218.2
2017-08-16 06:30 | 229.44 | 221.07
2017-08-16 07:00 | 231.37 | 223.22
2017-08-16 07:30 | 233.28 | 225.17
2017-08-16 08:00 | 232.76 | 224.61
2017-08-16 08:30 | 231.43 | 222.9
2017-08-16 09:00 | 228.73 | 220.38
2017-08-16 09:30 | 226.67 | 218.3
2017-08-16 10:00 | 226.41 | 217.97
2017-08-16 10:30 | 226.04 | 217.23
2017-08-16 11:00 | 225.81 | 217.18
2017-08-16 11:30 | 225.74 | 217.29
2017-08-16 12:00 | 226.18 | 217.47
2017-08-16 12:30 | 226.11 | 216.86
2017-08-16 13:00 | 227.04 | 217.8
2017-08-16 13:30 | 227.28 | 218.01
2017-08-16 14:00 | 209.38 | 200.81
2017-08-16 14:30 | 207.24 | 198.65
2017-08-16 15:00 | 207.98 | 199.24
2017-08-16 15:30 | 208.85 | 200.05
2017-08-16 16:00 | 211.19 | 202.56
2017-08-16 16:30 | 222.88 | 213.41
2017-08-16 17:00 | 227.47 | 217.92
2017-08-16 17:30 | 234.33 | 224.49
2017-08-16 18:00 | 237.72 | 227.92
2017-08-16 18:30 | 240.2 | 230.55
2017-08-16 19:00 | 241.23 | 231.64
2017-08-16 19:30 | 239.68 | 229.86
2017-08-16 20:00 | 238.17 | 228.26
2017-08-16 20:30 | 237.14 | 227.06
2017-08-16 21:00 | 235.68 | 225.27
2017-08-16 21:30 | 234.28 | 224.22
2017-08-16 22:00 | 232.67 | 222.62
2017-08-16 22:30 | 230.8 | 220.85
2017-08-16 23:00 | 228.87 | 219.05
2017-08-16 23:30 | 227.42 | 217.5
2017-08-17 | 225.42 | 215.93
2017-08-17 00:30 | 224.1 | 215.75
2017-08-17 01:00 | 222.8 | 215.04
2017-08-17 01:30 | 222.72 | 214.41
2017-08-17 02:00 | 222.44 | 214.08
2017-08-17 02:30 | 222.28 | 213.72
2017-08-17 03:00 | 221.47 | 212.93
2017-08-17 03:30 | 222.58 | 213.4
2017-08-17 04:00 | 222.4 | 213.61
2017-08-17 04:30 | 222.39 | 213.71
2017-08-17 05:00 | 223.04 | 214.54
2017-08-17 05:30 | 224.04 | 216.06
2017-08-17 06:00 | 226.54 | 218.73
2017-08-17 06:30 | 229.45 | 221.33
2017-08-17 07:00 | 233.22 | 224.45
2017-08-17 07:30 | 235.56 | 226.05
2017-08-17 08:00 | 234.71 | 225.02
2017-08-17 08:30 | 231.73 | 222.25
2017-08-17 09:00 | 229.59 | 220.11
2017-08-17 09:30 | 229.3 | 219.48
2017-08-17 10:00 | 228.81 | 219.39
2017-08-17 10:30 | 227.68 | 218.04
2017-08-17 11:00 | 228.21 | 217.79
2017-08-17 11:30 | 228.71 | 217.55
2017-08-17 12:00 | 228.16 | 216.72
2017-08-17 12:30 | 229.63 | 218.29
2017-08-17 13:00 | 230.15 | 218.69
2017-08-17 13:30 | 230.12 | 218.62
2017-08-17 14:00 | 230.52 | 219.03
2017-08-17 14:30 | 230.78 | 219.28
2017-08-17 15:00 | 231.38 | 219.82
2017-08-17 15:30 | 230.3 | 218.21
2017-08-17 16:00 | 231.43 | 219.73
2017-08-17 16:30 | 232.13 | 220.19
2017-08-17 17:00 | 232.94 | 220.88
2017-08-17 17:30 | 234.17 | 221.94
2017-08-17 18:00 | 235.78 | 223.7
2017-08-17 18:30 | 238.91 | 226.96
2017-08-17 19:00 | 240.51 | 228.78
2017-08-17 19:30 | 239.79 | 227.95
2017-08-17 20:00 | 237.83 | 226.04
2017-08-17 20:30 | 237.23 | 225.49
2017-08-17 21:00 | 236.06 | 224.31
2017-08-17 21:30 | 234.83 | 223.98
2017-08-17 22:00 | 232.57 | 222.34
2017-08-17 22:30 | 231.69 | 220.25
2017-08-17 23:00 | 230.35 | 218.74
2017-08-17 23:30 | 229.12 | 218.07
2017-08-18 | 227.73 | 216.9
2017-08-18 00:30 | 227.26 | 216.21
2017-08-18 01:00 | 225.97 | 215.51
2017-08-18 01:30 | 224.87 | 215.05
2017-08-18 02:00 | 224.47 | 214.22
2017-08-18 02:30 | 224.54 | 213.94
2017-08-18 03:00 | 224.48 | 213.85
2017-08-18 03:30 | 224.91 | 214.71
2017-08-18 04:00 | 224.92 | 214.91
2017-08-18 04:30 | 223.37 | 213.49
2017-08-18 05:00 | 221.96 | 212.22
2017-08-18 05:30 | 221.81 | 212.75
2017-08-18 06:00 | 224.95 | 215.28
2017-08-18 06:30 | 229.2 | 218.69
2017-08-18 07:00 | 232.92 | 221.91
2017-08-18 07:30 | 234.29 | 223.68
2017-08-18 08:00 | 235.31 | 224.6
2017-08-18 08:30 | 232.31 | 221.02
2017-08-18 09:00 | 232.42 | 220.97
2017-08-18 09:30 | 233.36 | 221.57
2017-08-18 10:00 | 233.36 | 221.52
2017-08-18 10:30 | 231.9 | 219.68
2017-08-18 11:00 | 230.61 | 218.4
2017-08-18 11:30 | 229.91 | 217.29
2017-08-18 12:00 | 228.28 | 215.58
2017-08-18 12:30 | 226.72 | 213.61
2017-08-18 13:00 | 226.62 | 213.49
2017-08-18 13:30 | 226.16 | 213.21
2017-08-18 14:00 | 226.49 | 213.3
2017-08-18 14:30 | 226.97 | 213.84
2017-08-18 15:00 | 226.53 | 213.79
2017-08-18 15:30 | 227.37 | 214.57
2017-08-18 16:00 | 228.33 | 215.7
2017-08-18 16:30 | 229.75 | 217.34
2017-08-18 17:00 | 231.52 | 219.05
2017-08-18 17:30 | 233.19 | 220.5
2017-08-18 18:00 | 235.49 | 223.47
2017-08-18 18:30 | 237.32 | 225.43
2017-08-18 19:00 | 239.98 | 228.36
2017-08-18 19:30 | 237.65 | 226.03
2017-08-18 20:00 | 236.17 | 224.68
2017-08-18 20:30 | 236.54 | 225.09
2017-08-18 21:00 | 235.11 | 223.41
2017-08-18 21:30 | 231.05 | 220.27
2017-08-18 22:00 | 229.53 | 218.66
2017-08-18 22:30 | 228.64 | 217.58
2017-08-18 23:00 | 227.35 | 216.18
2017-08-18 23:30 | 226.52 | 215.82
2017-08-19 | 226.14 | 215.08
2017-08-19 00:30 | 224.52 | 214.51
2017-08-19 01:00 | 224.07 | 214.03
2017-08-19 01:30 | 221.88 | 212.78
2017-08-19 02:00 | 221.2 | 212.76
2017-08-19 02:30 | 221.07 | 212.63
2017-08-19 03:00 | 221.42 | 212.83
2017-08-19 03:30 | 221.3 | 212.69
2017-08-19 04:00 | 221.53 | 212.81
2017-08-19 04:30 | 221.11 | 212.43
2017-08-19 05:00 | 222.68 | 214.15
2017-08-19 05:30 | 223.38 | 215.23
2017-08-19 06:00 | 225.22 | 216.81
2017-08-19 06:30 | 226.63 | 217.94
2017-08-19 07:00 | 229.1 | 220.61
2017-08-19 07:30 | 230.31 | 221.73
2017-08-19 08:00 | 231.31 | 222.56
2017-08-19 08:30 | 231.42 | 222.5
2017-08-19 09:00 | 230.43 | 221.29
2017-08-19 09:30 | 228.64 | 219.29
2017-08-19 10:00 | 210.34 | 200.71
2017-08-19 10:30 | 203.5 | 193.62
2017-08-19 11:00 | 201.67 | 191.7
2017-08-19 11:30 | 200.92 | 190.76
2017-08-19 12:00 | 200.06 | 189.76
2017-08-19 12:30 | 198.67 | 188.55
2017-08-19 13:00 | 197.65 | 187.64
2017-08-19 13:30 | 196.62 | 186.59
2017-08-19 14:00 | 196.31 | 186.31
2017-08-19 14:30 | 196.5 | 186.57
2017-08-19 15:00 | 196.92 | 186.95
2017-08-19 15:30 | 197.07 | 187.32
2017-08-19 16:00 | 198.28 | 188.77
2017-08-19 16:30 | 200.28 | 191.1
2017-08-19 17:00 | 203.52 | 194.15
2017-08-19 17:30 | 207.39 | 197.89
2017-08-19 18:00 | 227.69 | 218.57
2017-08-19 18:30 | 236.98 | 228.42
2017-08-19 19:00 | 237.86 | 229.61
2017-08-19 19:30 | 237.26 | 228.88
2017-08-19 20:00 | 236.94 | 228.57
2017-08-19 20:30 | 236.86 | 228.4
2017-08-19 21:00 | 236.48 | 227.8
2017-08-19 21:30 | 235.43 | 226.97
2017-08-19 22:00 | 234.21 | 225.59
2017-08-19 22:30 | 231.82 | 222.66
2017-08-19 23:00 | 229.91 | 220.93
2017-08-19 23:30 | 228.65 | 219.82
2017-08-20 | 228.12 | 219.02
2017-08-20 00:30 | 227.47 | 218.48
2017-08-20 01:00 | 225.91 | 217.13
2017-08-20 01:30 | 224.97 | 216.72
2017-08-20 02:00 | 224.33 | 216.02
2017-08-20 02:30 | 224.34 | 216.02
2017-08-20 03:00 | 223.89 | 215.62
2017-08-20 03:30 | 224.17 | 215.79
2017-08-20 04:00 | 224.72 | 216.31
2017-08-20 04:30 | 208.96 | 200.59
2017-08-20 05:00 | 205.85 | 197.6
2017-08-20 05:30 | 206.45 | 198.47
2017-08-20 06:00 | 207.53 | 199.87
2017-08-20 06:30 | 208.94 | 201.54
2017-08-20 07:00 | 187.07 | 179.48
2017-08-20 07:30 | 169.37 | 160.5
2017-08-20 08:00 | 171.03 | 160.74
2017-08-20 08:30 | 168.84 | 158.43
2017-08-20 09:00 | 167.88 | 157.33
2017-08-20 09:30 | 166.23 | 155.79
2017-08-20 10:00 | 163.46 | 153.82
2017-08-20 10:30 | 160.92 | 151.07
2017-08-20 11:00 | 159.63 | 149.53
2017-08-20 11:30 | 158.47 | 148.77
2017-08-20 12:00 | 157.63 | 147.72
2017-08-20 12:30 | 157.05 | 147.2
2017-08-20 13:00 | 156.4 | 146.29
2017-08-20 13:30 | 155.96 | 145.78
2017-08-20 14:00 | 188.54 | 179.23
2017-08-20 14:30 | 215.48 | 206.24
2017-08-20 15:00 | 221.85 | 212.71
2017-08-20 15:30 | 223.35 | 214.23
2017-08-20 16:00 | 224.31 | 215.12
2017-08-20 16:30 | 226.42 | 217.62
2017-08-20 17:00 | 228.98 | 219.71
2017-08-20 17:30 | 232.57 | 223.15
2017-08-20 18:00 | 236.42 | 227.01
2017-08-20 18:30 | 240.17 | 230.59
2017-08-20 19:00 | 242.76 | 233.3
2017-08-20 19:30 | 242.58 | 233.06
2017-08-20 20:00 | 242.36 | 232.93
2017-08-20 20:30 | 242.39 | 233.25
2017-08-20 21:00 | 241.5 | 232.02
2017-08-20 21:30 | 240.05 | 230.54
2017-08-20 22:00 | 237.89 | 228.17
2017-08-20 22:30 | 236.2 | 225.51
2017-08-20 23:00 | 233.98 | 223.13
2017-08-20 23:30 | 231.97 | 221.53
2017-08-21 | 230.66 | 220.75
2017-08-21 00:30 | 229.72 | 220.66
2017-08-21 01:00 | 227.54 | 219.36
2017-08-21 01:30 | 227.02 | 218.68
2017-08-21 02:00 | 226.96 | 218.19
2017-08-21 02:30 | 226.81 | 218.11
2017-08-21 03:00 | 227.38 | 218.57
2017-08-21 03:30 | 227.37 | 218.46
2017-08-21 04:00 | 227.88 | 218.99
2017-08-21 04:30 | 227.72 | 219.27
2017-08-21 05:00 | 229.53 | 221.53
2017-08-21 05:30 | 231.59 | 223.99
2017-08-21 06:00 | 234.75 | 227.49
2017-08-21 06:30 | 239.42 | 231.9
2017-08-21 07:00 | 245.11 | 236.63
2017-08-21 07:30 | 247.31 | 238.86
2017-08-21 08:00 | 248.13 | 239.52
2017-08-21 08:30 | 245.63 | 236.79
2017-08-21 09:00 | 242.3 | 233.39
2017-08-21 09:30 | 238.69 | 229.96
2017-08-21 10:00 | 236.44 | 227.23
2017-08-21 10:30 | 233.5 | 224
2017-08-21 11:00 | 232.3 | 222.77
2017-08-21 11:30 | 230.5 | 220.7
2017-08-21 12:00 | 228.36 | 218.24
2017-08-21 12:30 | 227.42 | 217.32
2017-08-21 13:00 | 226.12 | 215.73
2017-08-21 13:30 | 225.02 | 214.97
2017-08-21 14:00 | 229.82 | 219.92
2017-08-21 14:30 | 229.21 | 218.86
2017-08-21 15:00 | 228.84 | 218.39
2017-08-21 15:30 | 229.34 | 218.87
2017-08-21 16:00 | 229.75 | 219.54
2017-08-21 16:30 | 230.06 | 219.56
2017-08-21 17:00 | 231.23 | 220.51
2017-08-21 17:30 | 233.66 | 222.95
2017-08-21 18:00 | 235.1 | 226.5
2017-08-21 18:30 | 241.14 | 237.1
2017-08-21 19:00 | 239.4 | 235.15
2017-08-21 19:30 | 239.98 | 235.71
2017-08-21 20:00 | 240.72 | 236.56
2017-08-21 20:30 | 241.26 | 237.24
2017-08-21 21:00 | 242.97 | 238.33
2017-08-21 21:30 | 242.84 | 238.75
2017-08-21 22:00 | 234.62 | 225.01
2017-08-21 22:30 | 234.33 | 222.28
2017-08-21 23:00 | 232.08 | 219.97
2017-08-21 23:30 | 230.76 | 218.83
2017-08-22 | 229.35 | 217.36
2017-08-22 00:30 | 226.05 | 214.31
2017-08-22 01:00 | 224.21 | 212.71
2017-08-22 01:30 | 223.53 | 212.2
2017-08-22 02:00 | 223.07 | 211.93
2017-08-22 02:30 | 222.95 | 211.58
2017-08-22 03:00 | 222.19 | 211.42
2017-08-22 03:30 | 221.42 | 211.78
2017-08-22 04:00 | 221.75 | 212.02
2017-08-22 04:30 | 222.28 | 212.42
2017-08-22 05:00 | 223.77 | 214.32
2017-08-22 05:30 | 225.41 | 216.58
2017-08-22 06:00 | 229.75 | 219.6
2017-08-22 06:30 | 233.71 | 223.63
2017-08-22 07:00 | 237.4 | 227.22
2017-08-22 07:30 | 237.5 | 229.21
2017-08-22 08:00 | 235.92 | 227.61
2017-08-22 08:30 | 231.71 | 223.65
2017-08-22 09:00 | 228.48 | 219.81
2017-08-22 09:30 | 224.43 | 215.72
2017-08-22 10:00 | 221.8 | 213.17
2017-08-22 10:30 | 219.98 | 211.67
2017-08-22 11:00 | 220.67 | 212.14
2017-08-22 11:30 | 220.76 | 211.93
2017-08-22 12:00 | 220.15 | 211.43
2017-08-22 12:30 | 219.95 | 210.97
2017-08-22 13:00 | 220.73 | 211.45
2017-08-22 13:30 | 220.66 | 211.08
2017-08-22 14:00 | 222.11 | 212.3
2017-08-22 14:30 | 223.07 | 213.37
2017-08-22 15:00 | 223.83 | 213.87
2017-08-22 15:30 | 224.15 | 214.38
2017-08-22 16:00 | 223.68 | 214.02
2017-08-22 16:30 | 224.99 | 215.16
2017-08-22 17:00 | 226.36 | 216.47
2017-08-22 17:30 | 228.42 | 218.33
2017-08-22 18:00 | 231.6 | 221.83
2017-08-22 18:30 | 235.54 | 225.92
2017-08-22 19:00 | 238.06 | 228.61
2017-08-22 19:30 | 237.49 | 227.92
2017-08-22 20:00 | 235.64 | 226.16
2017-08-22 20:30 | 234.81 | 225.44
2017-08-22 21:00 | 233.28 | 223.88
2017-08-22 21:30 | 231.83 | 223.16
2017-08-22 22:00 | 227.39 | 219.19
2017-08-22 22:30 | 225.57 | 216.84
2017-08-22 23:00 | 223.02 | 214.49
2017-08-22 23:30 | 222.39 | 214.03
2017-08-23 | 221.46 | 213.19
2017-08-23 00:30 | 220.37 | 212.41
2017-08-23 01:00 | 219.43 | 211.62
2017-08-23 01:30 | 219.01 | 210.44
2017-08-23 02:00 | 218.67 | 210.6
2017-08-23 02:30 | 219.44 | 210.88
2017-08-23 03:00 | 219.06 | 210.87
2017-08-23 03:30 | 219.99 | 211.74
2017-08-23 04:00 | 219.89 | 211.68
2017-08-23 04:30 | 221.43 | 213.44
2017-08-23 05:00 | 223.11 | 215.39
2017-08-23 05:30 | 225.01 | 217.47
2017-08-23 06:00 | 229.97 | 221.38
2017-08-23 06:30 | 233.76 | 224.97
2017-08-23 07:00 | 236.77 | 227.4
2017-08-23 07:30 | 238.44 | 228.85
2017-08-23 08:00 | 236.46 | 226.97
2017-08-23 08:30 | 232.61 | 222.94
2017-08-23 09:00 | 227.14 | 217.43
2017-08-23 09:30 | 221.73 | 212.05
2017-08-23 10:00 | 218.62 | 209.02
2017-08-23 10:30 | 217.67 | 207.94
2017-08-23 11:00 | 215.81 | 206.32
2017-08-23 11:30 | 216.64 | 205.93
2017-08-23 12:00 | 217.2 | 206.06
2017-08-23 12:30 | 217.58 | 205.91
2017-08-23 13:00 | 218.33 | 206.23
2017-08-23 13:30 | 218.53 | 206.06
2017-08-23 14:00 | 218.95 | 206.76
2017-08-23 14:30 | 218.98 | 206.98
2017-08-23 15:00 | 219.78 | 207.59
2017-08-23 15:30 | 221.15 | 209.03
2017-08-23 16:00 | 221.83 | 209.83
2017-08-23 16:30 | 222.44 | 210.06
2017-08-23 17:00 | 223.84 | 211.42
2017-08-23 17:30 | 225.98 | 213.42
2017-08-23 18:00 | 227.38 | 216.43
2017-08-23 18:30 | 229.99 | 219.8
2017-08-23 19:00 | 232.32 | 222.23
2017-08-23 19:30 | 231.42 | 220.93
2017-08-23 20:00 | 229.72 | 219.25
2017-08-23 20:30 | 227.77 | 217.32
2017-08-23 21:00 | 225.76 | 215.03
2017-08-23 21:30 | 224.17 | 214.56
2017-08-23 22:00 | 223 | 213.56
2017-08-23 22:30 | 221.15 | 211.29
2017-08-23 23:00 | 219.21 | 209.01
2017-08-23 23:30 | 217.87 | 207.71
2017-08-24 | 216.66 | 206.43
2017-08-24 00:30 | 215.57 | 205.76
2017-08-24 01:00 | 214.48 | 205.23
2017-08-24 01:30 | 213.17 | 204.5
2017-08-24 02:00 | 212.39 | 203.97
2017-08-24 02:30 | 211.87 | 204.06
2017-08-24 03:00 | 211.31 | 204.1
2017-08-24 03:30 | 212.09 | 204.4
2017-08-24 04:00 | 212.01 | 204.35
2017-08-24 04:30 | 212.75 | 205.09
2017-08-24 05:00 | 213.49 | 206.39
2017-08-24 05:30 | 210.83 | 204.28
2017-08-24 06:00 | 212.69 | 206.33
2017-08-24 06:30 | 217.53 | 210.76
2017-08-24 07:00 | 220.35 | 213.4
2017-08-24 07:30 | 206.57 | 199.86
2017-08-24 08:00 | 191.41 | 185.25
2017-08-24 08:30 | 192.63 | 186.62
2017-08-24 09:00 | 194.42 | 188.59
2017-08-24 09:30 | 196.34 | 190.68
2017-08-24 10:00 | 197.32 | 191.66
2017-08-24 10:30 | 197.94 | 192.25
2017-08-24 11:00 | 199 | 193.29
2017-08-24 11:30 | 199.75 | 194.01
2017-08-24 12:00 | 202.67 | 194.87
2017-08-24 12:30 | 204.51 | 196.09
2017-08-24 13:00 | 204.37 | 195.93
2017-08-24 13:30 | 204.52 | 196.08
2017-08-24 14:00 | 204.44 | 195.87
2017-08-24 14:30 | 204.68 | 195.92
2017-08-24 15:00 | 204.59 | 195.84
2017-08-24 15:30 | 204.75 | 196.1
2017-08-24 16:00 | 205.89 | 197.19
2017-08-24 16:30 | 206.81 | 197.97
2017-08-24 17:00 | 208.7 | 199.79
2017-08-24 17:30 | 210.61 | 201.67
2017-08-24 18:00 | 213.32 | 204.81
2017-08-24 18:30 | 218.13 | 209.45
2017-08-24 19:00 | 220.59 | 212.26
2017-08-24 19:30 | 220.43 | 212.07
2017-08-24 20:00 | 219.47 | 211.08
2017-08-24 20:30 | 218.52 | 210.06
2017-08-24 21:00 | 217.26 | 208.95
2017-08-24 21:30 | 216.49 | 207.91
2017-08-24 22:00 | 212.05 | 203.57
2017-08-24 22:30 | 209.65 | 201.35
2017-08-24 23:00 | 207.64 | 199.46
2017-08-24 23:30 | 207.03 | 199.18
2017-08-25 | 205.68 | 197.91
2017-08-25 00:30 | 204.94 | 197.39
2017-08-25 01:00 | 204.23 | 197.1
2017-08-25 01:30 | 204.02 | 196.73
2017-08-25 02:00 | 203.58 | 196.79
2017-08-25 02:30 | 203.51 | 196.68
2017-08-25 03:00 | 203.48 | 196.77
2017-08-25 03:30 | 203.43 | 196.54
2017-08-25 04:00 | 204.01 | 197.17
2017-08-25 04:30 | 204.09 | 197.28
2017-08-25 05:00 | 205.23 | 198.6
2017-08-25 05:30 | 207.42 | 201.07
2017-08-25 06:00 | 210.81 | 204.52
2017-08-25 06:30 | 214.77 | 208.47
2017-08-25 07:00 | 219.05 | 212.83
2017-08-25 07:30 | 219.95 | 213.87
2017-08-25 08:00 | 218.83 | 212.7
2017-08-25 08:30 | 217.09 | 210.83
2017-08-25 09:00 | 213.9 | 207.33
2017-08-25 09:30 | 210.77 | 203.68
2017-08-25 10:00 | 209.42 | 201.79
2017-08-25 10:30 | 206.76 | 198.96
2017-08-25 11:00 | 205.28 | 197.45
2017-08-25 11:30 | 204.08 | 196.34
2017-08-25 12:00 | 203.27 | 195.6
2017-08-25 12:30 | 201.85 | 193.83
2017-08-25 13:00 | 203.15 | 194.59
2017-08-25 13:30 | 205.87 | 197.2
2017-08-25 14:00 | 205.13 | 196.27
2017-08-25 14:30 | 204.49 | 195.76
2017-08-25 15:00 | 203.77 | 195.16
2017-08-25 15:30 | 204.49 | 195.63
2017-08-25 16:00 | 206.17 | 197.29
2017-08-25 16:30 | 207.75 | 198.74
2017-08-25 17:00 | 209.82 | 201.23
2017-08-25 17:30 | 196.41 | 189.49
2017-08-25 18:00 | 194.35 | 187.33
2017-08-25 18:30 | 192.25 | 184.69
2017-08-25 19:00 | 188.92 | 180.94
2017-08-25 19:30 | 188.67 | 180.76
2017-08-25 20:00 | 189.96 | 182.13
2017-08-25 20:30 | 190.62 | 182.86
2017-08-25 21:00 | 190.67 | 183.05
2017-08-25 21:30 | 190.45 | 183.33
2017-08-25 22:00 | 209.75 | 201.98
2017-08-25 22:30 | 213.37 | 205.42
2017-08-25 23:00 | 212.22 | 203.77
2017-08-25 23:30 | 211.3 | 203.1
2017-08-26 | 208.99 | 201.53
2017-08-26 00:30 | 207.49 | 200.75
2017-08-26 01:00 | 207 | 199.97
2017-08-26 01:30 | 205.65 | 198.98
2017-08-26 02:00 | 205.93 | 199.15
2017-08-26 02:30 | 205.59 | 198.92
2017-08-26 03:00 | 205.25 | 198.6
2017-08-26 03:30 | 204.6 | 198.04
2017-08-26 04:00 | 204.53 | 198.79
2017-08-26 04:30 | 204.98 | 198.98
2017-08-26 05:00 | 205.79 | 200.05
2017-08-26 05:30 | 206.79 | 201.14
2017-08-26 06:00 | 208.02 | 202.49
2017-08-26 06:30 | 210.13 | 205.09
2017-08-26 07:00 | 213.97 | 207.84
2017-08-26 07:30 | 214.61 | 208.6
2017-08-26 08:00 | 213.78 | 207.44
2017-08-26 08:30 | 211.59 | 205.19
2017-08-26 09:00 | 207.03 | 200.62
2017-08-26 09:30 | 157.85 | 150.87
2017-08-26 10:00 | 164.64 | 157.37
2017-08-26 10:30 | 183.28 | 176.19
2017-08-26 11:00 | 182.11 | 174.71
2017-08-26 11:30 | 181.37 | 173.7
2017-08-26 12:00 | 181.07 | 173.3
2017-08-26 12:30 | 179.87 | 172.11
2017-08-26 13:00 | 179.03 | 171.05
2017-08-26 13:30 | 178.75 | 170.8
2017-08-26 14:00 | 178.19 | 170.3
2017-08-26 14:30 | 178.17 | 170.33
2017-08-26 15:00 | 177.89 | 170.16
2017-08-26 15:30 | 177.65 | 169.85
2017-08-26 16:00 | 179.11 | 171.7
2017-08-26 16:30 | 181.71 | 174.06
2017-08-26 17:00 | 183.65 | 175.74
2017-08-26 17:30 | 186.03 | 178.22
2017-08-26 18:00 | 197.64 | 189.94
2017-08-26 18:30 | 213.69 | 206.21
2017-08-26 19:00 | 214.95 | 207.49
2017-08-26 19:30 | 214.33 | 206.92
2017-08-26 20:00 | 213.38 | 206.07
2017-08-26 20:30 | 212.74 | 205.55
2017-08-26 21:00 | 209.02 | 202.06
2017-08-26 21:30 | 207.77 | 201.08
2017-08-26 22:00 | 207.52 | 200.43
2017-08-26 22:30 | 206.94 | 199.09
2017-08-26 23:00 | 205.69 | 197.61
2017-08-26 23:30 | 204.97 | 197.26
2017-08-27 | 203.82 | 196.42
2017-08-27 00:30 | 202.91 | 196.32
2017-08-27 01:00 | 202.5 | 196.16
2017-08-27 01:30 | 201.48 | 195.32
2017-08-27 02:00 | 201.09 | 194.7
2017-08-27 02:30 | 201.81 | 194.49
2017-08-27 03:00 | 202.17 | 194.75
2017-08-27 03:30 | 201.51 | 195.31
2017-08-27 04:00 | 201.69 | 195.49
2017-08-27 04:30 | 201.93 | 195.45
2017-08-27 05:00 | 202.36 | 195.59
2017-08-27 05:30 | 203.67 | 197.13
2017-08-27 06:00 | 204.5 | 198.32
2017-08-27 06:30 | 205.55 | 199.74
2017-08-27 07:00 | 207.61 | 201.56
2017-08-27 07:30 | 208.11 | 201.78
2017-08-27 08:00 | 207.56 | 201.3
2017-08-27 08:30 | 206.27 | 200.13
2017-08-27 09:00 | 204.58 | 198.14
2017-08-27 09:30 | 201.77 | 195.27
2017-08-27 10:00 | 182.41 | 175.72
2017-08-27 10:30 | 173.58 | 166.67
2017-08-27 11:00 | 174.36 | 167.32
2017-08-27 11:30 | 175.47 | 168.4
2017-08-27 12:00 | 174.67 | 167.69
2017-08-27 12:30 | 174.95 | 167.81
2017-08-27 13:00 | 174.64 | 167.24
2017-08-27 13:30 | 174.25 | 167.36
2017-08-27 14:00 | 173.3 | 166.18
2017-08-27 14:30 | 173.23 | 165.99
2017-08-27 15:00 | 174.27 | 167.16
2017-08-27 15:30 | 174.6 | 167.61
2017-08-27 16:00 | 192.29 | 185.17
2017-08-27 16:30 | 200.12 | 192.72
2017-08-27 17:00 | 201.86 | 194.32
2017-08-27 17:30 | 205.08 | 198.89
2017-08-27 18:00 | 217.96 | 215.35
2017-08-27 18:30 | 216.36 | 213.51
2017-08-27 19:00 | 215.55 | 212.64
2017-08-27 19:30 | 216.8 | 213.96
2017-08-27 20:00 | 218.19 | 215.44
2017-08-27 20:30 | 219.74 | 217.14
2017-08-27 21:00 | 220.98 | 218.44
2017-08-27 21:30 | 218.28 | 215.87
2017-08-27 22:00 | 218.74 | 216.4
2017-08-27 22:30 | 220.37 | 218.1
2017-08-27 23:00 | 205.17 | 197.46
2017-08-27 23:30 | 203.97 | 195.08
2017-08-28 | 202.71 | 194.67
2017-08-28 00:30 | 202.24 | 194.64
2017-08-28 01:00 | 201.36 | 194.29
2017-08-28 01:30 | 200.64 | 193.95
2017-08-28 02:00 | 200.39 | 193.78
2017-08-28 02:30 | 200.98 | 193.92
2017-08-28 03:00 | 200.72 | 193.92
2017-08-28 03:30 | 201.29 | 194.24
2017-08-28 04:00 | 201.64 | 194.76
2017-08-28 04:30 | 202.07 | 195.48
2017-08-28 05:00 | 204.1 | 197.41
2017-08-28 05:30 | 206.28 | 199.74
2017-08-28 06:00 | 210.01 | 203.41
2017-08-28 06:30 | 214.11 | 207.52
2017-08-28 07:00 | 219.31 | 212.57
2017-08-28 07:30 | 190.5 | 183.81
2017-08-28 08:00 | 190.09 | 183.76
2017-08-28 08:30 | 192.28 | 186
2017-08-28 09:00 | 208.74 | 201.16
2017-08-28 09:30 | 211.33 | 203.26
2017-08-28 10:00 | 209.24 | 200.96
2017-08-28 10:30 | 207.1 | 198.5
2017-08-28 11:00 | 205.66 | 196.98
2017-08-28 11:30 | 204.09 | 195.42
2017-08-28 12:00 | 203.4 | 194.34
2017-08-28 12:30 | 203.84 | 194.09
2017-08-28 13:00 | 206.26 | 196.53
2017-08-28 13:30 | 205.77 | 196.15
2017-08-28 14:00 | 204.57 | 194.67
2017-08-28 14:30 | 205.37 | 195.71
2017-08-28 15:00 | 205.6 | 195.85
2017-08-28 15:30 | 206.01 | 196.36
2017-08-28 16:00 | 206.75 | 197.03
2017-08-28 16:30 | 207.59 | 197.47
2017-08-28 17:00 | 209.8 | 199.73
2017-08-28 17:30 | 213.13 | 203.37
2017-08-28 18:00 | 217.42 | 208.1
2017-08-28 18:30 | 220.81 | 211.98
2017-08-28 19:00 | 222.62 | 214
2017-08-28 19:30 | 222.61 | 214.05
2017-08-28 20:00 | 222.12 | 213.7
2017-08-28 20:30 | 221.98 | 213.39
2017-08-28 21:00 | 220.54 | 211.8
2017-08-28 21:30 | 219.3 | 210.71
2017-08-28 22:00 | 217.69 | 209.21
2017-08-28 22:30 | 215.24 | 206.63
2017-08-28 23:00 | 212.92 | 203.98
2017-08-28 23:30 | 211.12 | 202.4
2017-08-29 | 209.88 | 200.99
2017-08-29 00:30 | 209.23 | 200.54
2017-08-29 01:00 | 207.9 | 199.51
2017-08-29 01:30 | 206.53 | 198.94
2017-08-29 02:00 | 205.75 | 198.24
2017-08-29 02:30 | 206.21 | 198.37
2017-08-29 03:00 | 206.22 | 198.45
2017-08-29 03:30 | 206.57 | 198.9
2017-08-29 04:00 | 207.17 | 199.69
2017-08-29 04:30 | 207.57 | 200.22
2017-08-29 05:00 | 209.46 | 202.52
2017-08-29 05:30 | 212.77 | 205.73
2017-08-29 06:00 | 217.59 | 210.38
2017-08-29 06:30 | 222.05 | 215.21
2017-08-29 07:00 | 226.88 | 220.37
2017-08-29 07:30 | 229.38 | 222.39
2017-08-29 08:00 | 227.8 | 220.67
2017-08-29 08:30 | 222.78 | 215.79
2017-08-29 09:00 | 219.12 | 211.51
2017-08-29 09:30 | 214.8 | 206.89
2017-08-29 10:00 | 212.9 | 203.83
2017-08-29 10:30 | 209.07 | 200.72
2017-08-29 11:00 | 206.53 | 198.63
2017-08-29 11:30 | 206.14 | 198.05
2017-08-29 12:00 | 207.35 | 199.15
2017-08-29 12:30 | 207.49 | 199.08
2017-08-29 13:00 | 208.39 | 199.58
2017-08-29 13:30 | 208.73 | 200.1
2017-08-29 14:00 | 207.7 | 198.77
2017-08-29 14:30 | 206.42 | 197.29
2017-08-29 15:00 | 205.71 | 196.65
2017-08-29 15:30 | 206.32 | 197.04
2017-08-29 16:00 | 207.23 | 197.72
2017-08-29 16:30 | 208.8 | 199.06
2017-08-29 17:00 | 210.75 | 201.13
2017-08-29 17:30 | 212.18 | 203.14
2017-08-29 18:00 | 215.97 | 207.23
2017-08-29 18:30 | 221.36 | 213.19
2017-08-29 19:00 | 225.2 | 216.95
2017-08-29 19:30 | 222.26 | 213.84
2017-08-29 20:00 | 222.02 | 213.63
2017-08-29 20:30 | 222.03 | 213.71
2017-08-29 21:00 | 220.84 | 212.59
2017-08-29 21:30 | 220 | 211.84
2017-08-29 22:00 | 218.37 | 210.24
2017-08-29 22:30 | 215.69 | 207.67
2017-08-29 23:00 | 214.13 | 205.76
2017-08-29 23:30 | 212.72 | 204.77
2017-08-30 | 210.92 | 203.28
2017-08-30 00:30 | 210.06 | 202.96
2017-08-30 01:00 | 208.96 | 202.22
2017-08-30 01:30 | 207.67 | 201.31
2017-08-30 02:00 | 207.15 | 200.97
2017-08-30 02:30 | 206.69 | 200.47
2017-08-30 03:00 | 207.04 | 200.81
2017-08-30 03:30 | 207.85 | 201.45
2017-08-30 04:00 | 207.83 | 201.62
2017-08-30 04:30 | 208.96 | 202.91
2017-08-30 05:00 | 211.11 | 204.84
2017-08-30 05:30 | 214.18 | 208.12
2017-08-30 06:00 | 217.84 | 211.9
2017-08-30 06:30 | 223.11 | 216.76
2017-08-30 07:00 | 226.76 | 220.44
2017-08-30 07:30 | 229.73 | 222.66
2017-08-30 08:00 | 227.89 | 220.13
2017-08-30 08:30 | 222.64 | 214.82
2017-08-30 09:00 | 217.91 | 210.08
2017-08-30 09:30 | 213.72 | 205.22
2017-08-30 10:00 | 212.21 | 203.24
2017-08-30 10:30 | 212.1 | 203.14
2017-08-30 11:00 | 210.44 | 201.54
2017-08-30 11:30 | 209.93 | 200.83
2017-08-30 12:00 | 207.89 | 198.59
2017-08-30 12:30 | 206.76 | 197.41
2017-08-30 13:00 | 206.35 | 196.6
2017-08-30 13:30 | 206.62 | 196.44
2017-08-30 14:00 | 206.18 | 195.83
2017-08-30 14:30 | 206.26 | 196.56
2017-08-30 15:00 | 206.89 | 197.15
2017-08-30 15:30 | 204 | 194.89
2017-08-30 16:00 | 199.04 | 191.07
2017-08-30 16:30 | 198.23 | 189.83
2017-08-30 17:00 | 198.26 | 189.62
2017-08-30 17:30 | 196.89 | 188.34
2017-08-30 18:00 | 195.65 | 186.8
2017-08-30 18:30 | 194.11 | 184.69
2017-08-30 19:00 | 192.46 | 182.68
2017-08-30 19:30 | 192.83 | 183.11
2017-08-30 20:00 | 192.24 | 182.69
2017-08-30 20:30 | 191.78 | 182.41
2017-08-30 21:00 | 215.51 | 205.45
2017-08-30 21:30 | 219.33 | 211.03
2017-08-30 22:00 | 216.11 | 208.75
2017-08-30 22:30 | 214.15 | 206.39
2017-08-30 23:00 | 212.5 | 204.23
2017-08-30 23:30 | 210.5 | 203.12
2017-08-31 | 209.18 | 202.04
2017-08-31 00:30 | 208.56 | 201.3
2017-08-31 01:00 | 207.24 | 200.73
2017-08-31 01:30 | 205.88 | 199.53
2017-08-31 02:00 | 206.1 | 199.46
2017-08-31 02:30 | 205.34 | 198.93
2017-08-31 03:00 | 205.31 | 199.24
2017-08-31 03:30 | 205.64 | 199.71
2017-08-31 04:00 | 206.87 | 200.22
2017-08-31 04:30 | 207.15 | 200.96
2017-08-31 05:00 | 209.39 | 202.84
2017-08-31 05:30 | 211.64 | 205.13
2017-08-31 06:00 | 216.18 | 209.77
2017-08-31 06:30 | 220.36 | 214.49
2017-08-31 07:00 | 224.55 | 218.45
2017-08-31 07:30 | 226.72 | 220.43
2017-08-31 08:00 | 225.24 | 217.84
2017-08-31 08:30 | 220.88 | 213.38
2017-08-31 09:00 | 216.19 | 208.47
2017-08-31 09:30 | 211.73 | 203.83
2017-08-31 10:00 | 210.17 | 201.86
2017-08-31 10:30 | 209.56 | 201.2
2017-08-31 11:00 | 210.88 | 201.05
2017-08-31 11:30 | 210.29 | 199.77
2017-08-31 12:00 | 209.35 | 198.7
2017-08-31 12:30 | 207.85 | 196.93
2017-08-31 13:00 | 197.91 | 187.37
2017-08-31 13:30 | 184.43 | 174.44
2017-08-31 14:00 | 200.2 | 190.84
2017-08-31 14:30 | 205.26 | 196.13
2017-08-31 15:00 | 205.28 | 196.33
2017-08-31 15:30 | 206.19 | 196.5
2017-08-31 16:00 | 206.91 | 196.88
2017-08-31 16:30 | 207.96 | 197.76
2017-08-31 17:00 | 209.52 | 198.98
2017-08-31 17:30 | 212.47 | 201.37
2017-08-31 18:00 | 214.84 | 204
2017-08-31 18:30 | 219.37 | 208.92
2017-08-31 19:00 | 222.87 | 212.63
2017-08-31 19:30 | 222.66 | 212.28
2017-08-31 20:00 | 222.83 | 212.46
2017-08-31 20:30 | 221.39 | 211.14
2017-08-31 21:00 | 216.68 | 206.66
2017-08-31 21:30 | 214.81 | 205.92
2017-08-31 22:00 | 214.02 | 205.01
2017-08-31 22:30 | 212.49 | 203.23
2017-08-31 23:00 | 211.28 | 201.81
2017-08-31 23:30 | 210.3 | 200.85
2017-09-01 | 209.25 | 199.8
2017-09-01 00:30 | 207.89 | 199.32
2017-09-01 01:00 | 205.79 | 197.56
2017-09-01 01:30 | 205.72 | 198.12
2017-09-01 02:00 | 205.99 | 198.41
2017-09-01 02:30 | 205.95 | 198.41
2017-09-01 03:00 | 206.72 | 199.08
2017-09-01 03:30 | 206.79 | 199.25
2017-09-01 04:00 | 206.25 | 199.19
2017-09-01 04:30 | 207.57 | 200.48
2017-09-01 05:00 | 208.83 | 201.66
2017-09-01 05:30 | 211.24 | 204.64
2017-09-01 06:00 | 215.43 | 208.26
2017-09-01 06:30 | 219.62 | 212.41
2017-09-01 07:00 | 224.02 | 216.73
2017-09-01 07:30 | 225.59 | 217.91
2017-09-01 08:00 | 223.4 | 215.39
2017-09-01 08:30 | 218.35 | 210.15
2017-09-01 09:00 | 214.67 | 206.02
2017-09-01 09:30 | 211.81 | 202.32
2017-09-01 10:00 | 211.02 | 201.57
2017-09-01 10:30 | 208.24 | 199.25
2017-09-01 11:00 | 208.69 | 200.04
2017-09-01 11:30 | 208.32 | 199.38
2017-09-01 12:00 | 207.9 | 198.26
2017-09-01 12:30 | 205.92 | 196.14
2017-09-01 13:00 | 206.59 | 196.06
2017-09-01 13:30 | 206.44 | 196.21
2017-09-01 14:00 | 206.42 | 196.01
2017-09-01 14:30 | 206.44 | 196.42
2017-09-01 15:00 | 205.58 | 195.92
2017-09-01 15:30 | 206.64 | 196.28
2017-09-01 16:00 | 207.79 | 196.95
2017-09-01 16:30 | 209.64 | 198.18
2017-09-01 17:00 | 211.98 | 200.23
2017-09-01 17:30 | 213.11 | 201.72
2017-09-01 18:00 | 214.55 | 204
2017-09-01 18:30 | 217.37 | 207.16
2017-09-01 19:00 | 219.88 | 209.41
2017-09-01 19:30 | 220.31 | 209.48
2017-09-01 20:00 | 219.32 | 208.65
2017-09-01 20:30 | 218.5 | 207.98
2017-09-01 21:00 | 216.34 | 205.82
2017-09-01 21:30 | 211.13 | 201.6
2017-09-01 22:00 | 208.74 | 199.65
2017-09-01 22:30 | 207.52 | 198.22
2017-09-01 23:00 | 206.75 | 197.34
2017-09-01 23:30 | 206.06 | 196.88
2017-09-02 | 205.55 | 196.52
2017-09-02 00:30 | 204.41 | 195.67
2017-09-02 01:00 | 201.99 | 193.79
2017-09-02 01:30 | 201.43 | 193.42
2017-09-02 02:00 | 201.84 | 193.86
2017-09-02 02:30 | 202.43 | 194.26
2017-09-02 03:00 | 202.94 | 194.94
2017-09-02 03:30 | 202.78 | 194.69
2017-09-02 04:00 | 202.56 | 194.63
2017-09-02 04:30 | 202.5 | 194.55
2017-09-02 05:00 | 203.66 | 195.95
2017-09-02 05:30 | 205.69 | 197.74
2017-09-02 06:00 | 207.07 | 199.34
2017-09-02 06:30 | 207.11 | 200.17
2017-09-02 07:00 | 209.09 | 202.49
2017-09-02 07:30 | 208.05 | 200.94
2017-09-02 08:00 | 206.01 | 198.33
2017-09-02 08:30 | 203.83 | 196.26
2017-09-02 09:00 | 202.49 | 193.78
2017-09-02 09:30 | 200.6 | 191.04
2017-09-02 10:00 | 199.64 | 190.34
2017-09-02 10:30 | 202.57 | 190.77
2017-09-02 11:00 | 200.75 | 189.48
2017-09-02 11:30 | 200.03 | 188.65
2017-09-02 12:00 | 199.28 | 188.2
2017-09-02 12:30 | 198.79 | 187.77
2017-09-02 13:00 | 198.53 | 187.43
2017-09-02 13:30 | 199.48 | 189.58
2017-09-02 14:00 | 203.51 | 194.44
2017-09-02 14:30 | 205.7 | 197.07
2017-09-02 15:00 | 206.58 | 198.26
2017-09-02 15:30 | 207.36 | 198.68
2017-09-02 16:00 | 205.92 | 197.37
2017-09-02 16:30 | 202.21 | 193.33
2017-09-02 17:00 | 191.63 | 183.45
2017-09-02 17:30 | 190.97 | 182.27
2017-09-02 18:00 | 190.94 | 181.76
2017-09-02 18:30 | 191.32 | 181.6
2017-09-02 19:00 | 192.05 | 182.47
2017-09-02 19:30 | 192.98 | 183.24
2017-09-02 20:00 | 194.74 | 185.38
2017-09-02 20:30 | 193.01 | 182.81
2017-09-02 21:00 | 192.79 | 182.67
2017-09-02 21:30 | 192.94 | 183.96
2017-09-02 22:00 | 204.47 | 193.89
2017-09-02 22:30 | 208.38 | 197.39
2017-09-02 23:00 | 208.03 | 196.92
2017-09-02 23:30 | 207.41 | 196.51
2017-09-03 | 205.64 | 195.26
2017-09-03 00:30 | 204.41 | 194.66
2017-09-03 01:00 | 201.91 | 193.41
2017-09-03 01:30 | 200.61 | 192.26
2017-09-03 02:00 | 196.45 | 189.15
2017-09-03 02:30 | 196.35 | 189.21
2017-09-03 03:00 | 195.63 | 189.27
2017-09-03 03:30 | 196 | 189.39
2017-09-03 04:00 | 196.2 | 189.62
2017-09-03 04:30 | 196.54 | 189.89
2017-09-03 05:00 | 197.39 | 190.75
2017-09-03 05:30 | 198 | 191.61
2017-09-03 06:00 | 198.97 | 192.76
2017-09-03 06:30 | 200.69 | 193.48
2017-09-03 07:00 | 201.75 | 193.78
2017-09-03 07:30 | 200.58 | 192.83
2017-09-03 08:00 | 199.88 | 192.12
2017-09-03 08:30 | 198.64 | 190.52
2017-09-03 09:00 | 199.78 | 188.54
2017-09-03 09:30 | 200.67 | 189.14
2017-09-03 10:00 | 200 | 188.46
2017-09-03 10:30 | 199.13 | 187.53
2017-09-03 11:00 | 198.91 | 186.62
2017-09-03 11:30 | 198.72 | 186.27
2017-09-03 12:00 | 198.92 | 185.93
2017-09-03 12:30 | 198.45 | 186.03
2017-09-03 13:00 | 198.72 | 186.51
2017-09-03 13:30 | 198.49 | 186.52
2017-09-03 14:00 | 199.45 | 186.95
2017-09-03 14:30 | 199.31 | 187.18
2017-09-03 15:00 | 199.81 | 188.17
2017-09-03 15:30 | 200.61 | 189.14
2017-09-03 16:00 | 202.57 | 191.02
2017-09-03 16:30 | 203.4 | 191.82
2017-09-03 17:00 | 205.16 | 193.56
2017-09-03 17:30 | 207.36 | 195.65
2017-09-03 18:00 | 209.41 | 196.56
2017-09-03 18:30 | 210.8 | 199.49
2017-09-03 19:00 | 210.81 | 200.91
2017-09-03 19:30 | 209.9 | 199.67
2017-09-03 20:00 | 208.1 | 197.79
2017-09-03 20:30 | 207.02 | 196.53
2017-09-03 21:00 | 205.83 | 195.19
2017-09-03 21:30 | 204.03 | 194.03
2017-09-03 22:00 | 202.15 | 192.57
2017-09-03 22:30 | 200.79 | 190.23
2017-09-03 23:00 | 199.56 | 189.26
2017-09-03 23:30 | 197.86 | 188.14
2017-09-04 | 197.06 | 187.26
2017-09-04 00:30 | 196.03 | 186.7
2017-09-04 01:00 | 195.14 | 185.95
2017-09-04 01:30 | 194.44 | 185.29
2017-09-04 02:00 | 194.02 | 184.71
2017-09-04 02:30 | 192.92 | 184.03
2017-09-04 03:00 | 193.04 | 183.8
2017-09-04 03:30 | 192.56 | 183.62
2017-09-04 04:00 | 192.7 | 183.87
2017-09-04 04:30 | 192.99 | 184.39
2017-09-04 05:00 | 194.04 | 185.66
2017-09-04 05:30 | 195.42 | 187.44
2017-09-04 06:00 | 197.83 | 190.06
2017-09-04 06:30 | 201.02 | 193.33
2017-09-04 07:00 | 205.51 | 196.37
2017-09-04 07:30 | 206.88 | 197.51
2017-09-04 08:00 | 205.69 | 196.57
2017-09-04 08:30 | 203.62 | 194.55
2017-09-04 09:00 | 201.29 | 192.44
2017-09-04 09:30 | 199.45 | 190.69
2017-09-04 10:00 | 199.39 | 190.42
2017-09-04 10:30 | 197.93 | 188.9
2017-09-04 11:00 | 196.78 | 188.24
2017-09-04 11:30 | 196.26 | 187.52
2017-09-04 12:00 | 205.28 | 196.31
2017-09-04 12:30 | 202.5 | 192.87
2017-09-04 13:00 | 203.7 | 193.64
2017-09-04 13:30 | 204.45 | 194.61
2017-09-04 14:00 | 204.88 | 195.11
2017-09-04 14:30 | 205.11 | 195.37
2017-09-04 15:00 | 205.13 | 195.53
2017-09-04 15:30 | 206.19 | 196.34
2017-09-04 16:00 | 206.81 | 197.08
2017-09-04 16:30 | 207.79 | 198.17
2017-09-04 17:00 | 211.35 | 201.89
2017-09-04 17:30 | 208.92 | 199.04
2017-09-04 18:00 | 210.25 | 200.52
2017-09-04 18:30 | 213.66 | 204.19
2017-09-04 19:00 | 216.21 | 206.63
2017-09-04 19:30 | 215.76 | 205.72
2017-09-04 20:00 | 214.79 | 204.45
2017-09-04 20:30 | 214.2 | 203.86
2017-09-04 21:00 | 212.39 | 202.06
2017-09-04 21:30 | 210.36 | 201.12
2017-09-04 22:00 | 208.4 | 199.49
2017-09-04 22:30 | 207.31 | 197.71
2017-09-04 23:00 | 205.58 | 195.95
2017-09-04 23:30 | 204.92 | 195.54
2017-09-05 | 203.26 | 194.15
2017-09-05 00:30 | 202.46 | 193.81
2017-09-05 01:00 | 197.81 | 189.56
2017-09-05 01:30 | 197.25 | 189.22
2017-09-05 02:00 | 197.74 | 189.94
2017-09-05 02:30 | 198.36 | 189.96
2017-09-05 03:00 | 198.75 | 190.08
2017-09-05 03:30 | 198.34 | 190.1
2017-09-05 04:00 | 199.02 | 191.03
2017-09-05 04:30 | 200.91 | 192.79
2017-09-05 05:00 | 201.31 | 193.79
2017-09-05 05:30 | 202.67 | 195.94
2017-09-05 06:00 | 207.13 | 199.47
2017-09-05 06:30 | 211 | 202.84
2017-09-05 07:00 | 213.78 | 205.52
2017-09-05 07:30 | 216.03 | 207.48
2017-09-05 08:00 | 214.13 | 205.1
2017-09-05 08:30 | 210.92 | 201.95
2017-09-05 09:00 | 207.82 | 199.38
2017-09-05 09:30 | 207.96 | 198.94
2017-09-05 10:00 | 218.66 | 209
2017-09-05 10:30 | 219.67 | 210.03
2017-09-05 11:00 | 218.68 | 208.9
2017-09-05 11:30 | 217.96 | 207.87
2017-09-05 12:00 | 217.39 | 207.54
2017-09-05 12:30 | 216.99 | 206.65
2017-09-05 13:00 | 216.71 | 205.94
2017-09-05 13:30 | 211.89 | 201.93
2017-09-05 14:00 | 218.05 | 207.38
2017-09-05 14:30 | 219.71 | 209.01
2017-09-05 15:00 | 219.86 | 209.09
2017-09-05 15:30 | 221.4 | 210.23
2017-09-05 16:00 | 222.56 | 211.69
2017-09-05 16:30 | 224.28 | 212.79
2017-09-05 17:00 | 227.53 | 216.3
2017-09-05 17:30 | 231.81 | 220.52
2017-09-05 18:00 | 234.78 | 223.68
2017-09-05 18:30 | 237.99 | 227.18
2017-09-05 19:00 | 239.85 | 229.14
2017-09-05 19:30 | 238.87 | 228.1
2017-09-05 20:00 | 237.85 | 227.29
2017-09-05 20:30 | 237.04 | 226.35
2017-09-05 21:00 | 235.88 | 225.27
2017-09-05 21:30 | 233.87 | 225.03
2017-09-05 22:00 | 228.61 | 220.2
2017-09-05 22:30 | 227.45 | 218.34
2017-09-05 23:00 | 225.66 | 216.56
2017-09-05 23:30 | 224.6 | 215.95
2017-09-06 | 223.64 | 215.26
2017-09-06 00:30 | 223.05 | 214.94
2017-09-06 01:00 | 221.38 | 213.72
2017-09-06 01:30 | 220.51 | 213.27
2017-09-06 02:00 | 220.33 | 213.11
2017-09-06 02:30 | 220.91 | 213.08
2017-09-06 03:00 | 222.28 | 214.27
2017-09-06 03:30 | 223.6 | 215.68
2017-09-06 04:00 | 225.83 | 217.96
2017-09-06 04:30 | 227.64 | 219.92
2017-09-06 05:00 | 228.35 | 220.98
2017-09-06 05:30 | 229.92 | 222.87
2017-09-06 06:00 | 235.21 | 227.19
2017-09-06 06:30 | 239.4 | 231.44
2017-09-06 07:00 | 243.59 | 234.95
2017-09-06 07:30 | 243.93 | 235.45
2017-09-06 08:00 | 215.47 | 208.03
2017-09-06 08:30 | 217.05 | 209.75
2017-09-06 09:00 | 219.08 | 211.98
2017-09-06 09:30 | 219.45 | 212.75
2017-09-06 10:00 | 229.38 | 221.02
2017-09-06 10:30 | 231.79 | 223.14
2017-09-06 11:00 | 230.45 | 220.98
2017-09-06 11:30 | 230.77 | 220.87
2017-09-06 12:00 | 230.62 | 220.48
2017-09-06 12:30 | 229.94 | 219.67
2017-09-06 13:00 | 230.49 | 219.82
2017-09-06 13:30 | 230.91 | 220.14
2017-09-06 14:00 | 228.97 | 218.11
2017-09-06 14:30 | 223.51 | 212.97
2017-09-06 15:00 | 223.8 | 213.31
2017-09-06 15:30 | 224.43 | 213.82
2017-09-06 16:00 | 224.94 | 214.32
2017-09-06 16:30 | 226.56 | 215.45
2017-09-06 17:00 | 227.88 | 216.76
2017-09-06 17:30 | 228.93 | 218.05
2017-09-06 18:00 | 212.97 | 203.62
2017-09-06 18:30 | 212.28 | 202.25
2017-09-06 19:00 | 211.79 | 201.41
2017-09-06 19:30 | 211.53 | 201.05
2017-09-06 20:00 | 212.62 | 202.41
2017-09-06 20:30 | 232.75 | 221.51
2017-09-06 21:00 | 236.2 | 224.74
2017-09-06 21:30 | 232.27 | 221.61
2017-09-06 22:00 | 229.35 | 219.09
2017-09-06 22:30 | 228.79 | 217.97
2017-09-06 23:00 | 227.41 | 216.46
2017-09-06 23:30 | 226.43 | 215.68
2017-09-07 | 225.05 | 214.74
2017-09-07 00:30 | 225.46 | 214.75
2017-09-07 01:00 | 223.57 | 213.62
2017-09-07 01:30 | 223.16 | 213.94
2017-09-07 02:00 | 223.7 | 214.47
2017-09-07 02:30 | 223.67 | 214.41
2017-09-07 03:00 | 222.64 | 213.49
2017-09-07 03:30 | 222.52 | 213.29
2017-09-07 04:00 | 222.87 | 213.72
2017-09-07 04:30 | 223.4 | 214.47
2017-09-07 05:00 | 224.88 | 215.87
2017-09-07 05:30 | 227.84 | 218.73
2017-09-07 06:00 | 231.15 | 222.15
2017-09-07 06:30 | 235.87 | 226.47
2017-09-07 07:00 | 239.32 | 229.6
2017-09-07 07:30 | 239.35 | 229.39
2017-09-07 08:00 | 234.83 | 224.31
2017-09-07 08:30 | 230.78 | 220.4
2017-09-07 09:00 | 226.74 | 216.16
2017-09-07 09:30 | 224.45 | 213.89
2017-09-07 10:00 | 224.21 | 213.33
2017-09-07 10:30 | 222.53 | 212.57
2017-09-07 11:00 | 222.32 | 212.49
2017-09-07 11:30 | 222.17 | 212.07
2017-09-07 12:00 | 222.33 | 212.31
2017-09-07 12:30 | 221.54 | 211.28
2017-09-07 13:00 | 221.37 | 210.87
2017-09-07 13:30 | 220.79 | 210.51
2017-09-07 14:00 | 219.41 | 208.99
2017-09-07 14:30 | 219.94 | 209.66
2017-09-07 15:00 | 220.58 | 210.02
2017-09-07 15:30 | 221.54 | 210.16
2017-09-07 16:00 | 221.64 | 210.05
2017-09-07 16:30 | 222.18 | 210.38
2017-09-07 17:00 | 224.75 | 212.48
2017-09-07 17:30 | 226.4 | 214.04
2017-09-07 18:00 | 229.69 | 217.42
2017-09-07 18:30 | 233.13 | 220.56
2017-09-07 19:00 | 236.67 | 224.04
2017-09-07 19:30 | 236.37 | 223.56
2017-09-07 20:00 | 235.89 | 223.1
2017-09-07 20:30 | 235.53 | 223.01
2017-09-07 21:00 | 234.31 | 222.16
2017-09-07 21:30 | 231.25 | 219
2017-09-07 22:00 | 228.17 | 216.69
2017-09-07 22:30 | 226.99 | 215.12
2017-09-07 23:00 | 225.63 | 213.59
2017-09-07 23:30 | 224.55 | 212.76
2017-09-08 | 223.69 | 212.04
2017-09-08 00:30 | 221.4 | 210.15
2017-09-08 01:00 | 221.39 | 210.96
2017-09-08 01:30 | 220.53 | 211.07
2017-09-08 02:00 | 220.02 | 210.61
2017-09-08 02:30 | 220.48 | 210.81
2017-09-08 03:00 | 220.33 | 210.64
2017-09-08 03:30 | 220.56 | 210.81
2017-09-08 04:00 | 220.1 | 211.26
2017-09-08 04:30 | 202.48 | 193.97
2017-09-08 05:00 | 200.33 | 192.11
2017-09-08 05:30 | 202.51 | 194.52
2017-09-08 06:00 | 206.14 | 197.03
2017-09-08 06:30 | 209.83 | 201.32
2017-09-08 07:00 | 212.48 | 203.37
2017-09-08 07:30 | 211.41 | 202.22
2017-09-08 08:00 | 207.55 | 198.51
2017-09-08 08:30 | 176.77 | 165.33
2017-09-08 09:00 | 170.58 | 158.93
2017-09-08 09:30 | 169.27 | 157.67
2017-09-08 10:00 | 169.98 | 158.46
2017-09-08 10:30 | 167.69 | 155.87
2017-09-08 11:00 | 166.28 | 154.38
2017-09-08 11:30 | 165.83 | 154.03
2017-09-08 12:00 | 165.21 | 153.21
2017-09-08 12:30 | 164.68 | 152.44
2017-09-08 13:00 | 164.6 | 152.1
2017-09-08 13:30 | 164.09 | 151.59
2017-09-08 14:00 | 164.57 | 151.94
2017-09-08 14:30 | 164.75 | 152.22
2017-09-08 15:00 | 165.87 | 153.45
2017-09-08 15:30 | 165.55 | 152.96
2017-09-08 16:00 | 166.76 | 154.24
2017-09-08 16:30 | 168.59 | 155.95
2017-09-08 17:00 | 171.26 | 158.79
2017-09-08 17:30 | 172.3 | 159.77
2017-09-08 18:00 | 174.77 | 162.53
2017-09-08 18:30 | 177.92 | 165.7
2017-09-08 19:00 | 179.86 | 168.04
2017-09-08 19:30 | 179.56 | 167.84
2017-09-08 20:00 | 178.71 | 166.95
2017-09-08 20:30 | 177.41 | 165.65
2017-09-08 21:00 | 173.3 | 161.58
2017-09-08 21:30 | 172.56 | 161.12
2017-09-08 22:00 | 171.15 | 159.85
2017-09-08 22:30 | 170.3 | 158.62
2017-09-08 23:00 | 169.24 | 157.02
2017-09-08 23:30 | 168.31 | 156.64
2017-09-09 | 167.62 | 155.86
2017-09-09 00:30 | 166.83 | 155.7
2017-09-09 01:00 | 166.31 | 155.27
2017-09-09 01:30 | 167.25 | 155.02
2017-09-09 02:00 | 167 | 154.59
2017-09-09 02:30 | 167.25 | 154.57
2017-09-09 03:00 | 166.83 | 154.6
2017-09-09 03:30 | 166.53 | 154.17
2017-09-09 04:00 | 166.73 | 154.82
2017-09-09 04:30 | 166.66 | 154.89
2017-09-09 05:00 | 168.52 | 156.63
2017-09-09 05:30 | 169.46 | 157.69
2017-09-09 06:00 | 171.27 | 159.07
2017-09-09 06:30 | 173.63 | 161.61
2017-09-09 07:00 | 175.35 | 163.33
2017-09-09 07:30 | 176.24 | 164.23
2017-09-09 08:00 | 174.49 | 162.74
2017-09-09 08:30 | 173.1 | 160.91
2017-09-09 09:00 | 170.8 | 158.49
2017-09-09 09:30 | 170.82 | 158.58
2017-09-09 10:00 | 169.91 | 157.21
2017-09-09 10:30 | 169.01 | 156.08
2017-09-09 11:00 | 170.52 | 157.65
2017-09-09 11:30 | 170.51 | 157.27
2017-09-09 12:00 | 169.04 | 155.6
2017-09-09 12:30 | 168.77 | 155.54
2017-09-09 13:00 | 168.46 | 155.84
2017-09-09 13:30 | 168.86 | 155.98
2017-09-09 14:00 | 168.97 | 156.24
2017-09-09 14:30 | 169.11 | 156.45
2017-09-09 15:00 | 169.54 | 157.03
2017-09-09 15:30 | 170.63 | 158.12
2017-09-09 16:00 | 171.32 | 158.64
2017-09-09 16:30 | 171.89 | 158.63
2017-09-09 17:00 | 172.91 | 159.31
2017-09-09 17:30 | 175.4 | 161.72
2017-09-09 18:00 | 177.28 | 163.67
2017-09-09 18:30 | 181.06 | 167.51
2017-09-09 19:00 | 183 | 169.53
2017-09-09 19:30 | 182.99 | 169.47
2017-09-09 20:00 | 180.98 | 167.29
2017-09-09 20:30 | 178.32 | 164.47
2017-09-09 21:00 | 176.84 | 162.91
2017-09-09 21:30 | 176.22 | 162.43
2017-09-09 22:00 | 175.9 | 161.72
2017-09-09 22:30 | 174.66 | 160.37
2017-09-09 23:00 | 173.7 | 159.04
2017-09-09 23:30 | 173.28 | 158.92
2017-09-10 | 171.55 | 157.93
2017-09-10 00:30 | 170.81 | 157.42
2017-09-10 01:00 | 168.93 | 156.8
2017-09-10 01:30 | 168.1 | 156.65
2017-09-10 02:00 | 168.15 | 156.69
2017-09-10 02:30 | 167.91 | 156.27
2017-09-10 03:00 | 168.43 | 156.86
2017-09-10 03:30 | 168.93 | 157.49
2017-09-10 04:00 | 168.31 | 157.18
2017-09-10 04:30 | 167.79 | 157.13
2017-09-10 05:00 | 168.9 | 158.12
2017-09-10 05:30 | 170.37 | 159.44
2017-09-10 06:00 | 171.33 | 160.32
2017-09-10 06:30 | 172.68 | 162.02
2017-09-10 07:00 | 173.08 | 162.53
2017-09-10 07:30 | 171.75 | 161.64
2017-09-10 08:00 | 171.46 | 161.01
2017-09-10 08:30 | 169.94 | 159.28
2017-09-10 09:00 | 167.91 | 156.52
2017-09-10 09:30 | 165.89 | 154.41
2017-09-10 10:00 | 166.98 | 155.41
2017-09-10 10:30 | 168.28 | 156.4
2017-09-10 11:00 | 166.22 | 154.22
2017-09-10 11:30 | 165.05 | 152.92
2017-09-10 12:00 | 164.95 | 152.88
2017-09-10 12:30 | 164.75 | 152.54
2017-09-10 13:00 | 164.21 | 151.83
2017-09-10 13:30 | 163.78 | 151.58
2017-09-10 14:00 | 163.83 | 151.66
2017-09-10 14:30 | 163.47 | 151.42
2017-09-10 15:00 | 164.37 | 152.32
2017-09-10 15:30 | 164.89 | 153.06
2017-09-10 16:00 | 166.12 | 154.41
2017-09-10 16:30 | 168.93 | 156.91
2017-09-10 17:00 | 171.65 | 158.91
2017-09-10 17:30 | 174.21 | 161.71
2017-09-10 18:00 | 176.11 | 163.37
2017-09-10 18:30 | 178.56 | 166.03
2017-09-10 19:00 | 181.39 | 169.14
2017-09-10 19:30 | 182.09 | 169.8
2017-09-10 20:00 | 180.4 | 167.87
2017-09-10 20:30 | 162.34 | 149.46
2017-09-10 21:00 | 159.17 | 147.07
2017-09-10 21:30 | 176.72 | 167.9
2017-09-10 22:00 | 191.52 | 184.82
2017-09-10 22:30 | 196.68 | 190.81
2017-09-10 23:00 | 194.93 | 188.88
2017-09-10 23:30 | 193.44 | 187.46
2017-09-11 | 192.13 | 185.89
2017-09-11 00:30 | 191.88 | 185.59
2017-09-11 01:00 | 191.05 | 184.67
2017-09-11 01:30 | 190.73 | 184.35
2017-09-11 02:00 | 190.52 | 184.19
2017-09-11 02:30 | 190.31 | 183.96
2017-09-11 03:00 | 189.96 | 183.64
2017-09-11 03:30 | 190.08 | 183.78
2017-09-11 04:00 | 190.3 | 184
2017-09-11 04:30 | 190.87 | 184.59
2017-09-11 05:00 | 191.74 | 185.5
2017-09-11 05:30 | 194.19 | 188.18
2017-09-11 06:00 | 197.01 | 191.41
2017-09-11 06:30 | 200.33 | 195.04
2017-09-11 07:00 | 203.62 | 198.55
2017-09-11 07:30 | 205.98 | 200.86
2017-09-11 08:00 | 205 | 199.75
2017-09-11 08:30 | 202.43 | 197.18
2017-09-11 09:00 | 199.57 | 194.18
2017-09-11 09:30 | 196.64 | 191.05
2017-09-11 10:00 | 196.41 | 190.69
2017-09-11 10:30 | 195.97 | 190.07
2017-09-11 11:00 | 195.53 | 189.67
2017-09-11 11:30 | 195.66 | 189.71
2017-09-11 12:00 | 195.77 | 189.73
2017-09-11 12:30 | 195.72 | 189.7
2017-09-11 13:00 | 196.53 | 190.46
2017-09-11 13:30 | 197.7 | 191.54
2017-09-11 14:00 | 198.61 | 192.49
2017-09-11 14:30 | 199.23 | 193.19
2017-09-11 15:00 | 199.94 | 193.84
2017-09-11 15:30 | 200.03 | 194.05
2017-09-11 16:00 | 200.39 | 194.65
2017-09-11 16:30 | 201.03 | 195.32
2017-09-11 17:00 | 202.17 | 196.51
2017-09-11 17:30 | 186.09 | 181.16
2017-09-11 18:00 | 183.04 | 178.19
2017-09-11 18:30 | 181.83 | 177.04
2017-09-11 19:00 | 180.82 | 175.98
2017-09-11 19:30 | 181.76 | 177.12
2017-09-11 20:00 | 182.76 | 178.21
2017-09-11 20:30 | 183.13 | 178.64
2017-09-11 21:00 | 197.73 | 192.28
2017-09-11 21:30 | 201.99 | 196.24
2017-09-11 22:00 | 200.55 | 194.69
2017-09-11 22:30 | 198.59 | 192.7
2017-09-11 23:00 | 196.75 | 190.73
2017-09-11 23:30 | 196.14 | 189.97
2017-09-12 | 195.08 | 188.73
2017-09-12 00:30 | 194.7 | 188.21
2017-09-12 01:00 | 193.98 | 187.45
2017-09-12 01:30 | 193.42 | 186.87
2017-09-12 02:00 | 192.95 | 186.39
2017-09-12 02:30 | 192.63 | 186.08
2017-09-12 03:00 | 192.61 | 186.05
2017-09-12 03:30 | 192.56 | 186
2017-09-12 04:00 | 192.79 | 186.22
2017-09-12 04:30 | 193.17 | 186.61
2017-09-12 05:00 | 194.13 | 187.62
2017-09-12 05:30 | 196.17 | 189.85
2017-09-12 06:00 | 198.67 | 192.5
2017-09-12 06:30 | 201.89 | 196.11
2017-09-12 07:00 | 203.74 | 198.13
2017-09-12 07:30 | 204.42 | 198.96
2017-09-12 08:00 | 202.45 | 197.04
2017-09-12 08:30 | 200.57 | 195.05
2017-09-12 09:00 | 198.8 | 193.09
2017-09-12 09:30 | 196.92 | 191.04
2017-09-12 10:00 | 196.55 | 190.71
2017-09-12 10:30 | 195.85 | 190.08
2017-09-12 11:00 | 195.89 | 190.15
2017-09-12 11:30 | 195.67 | 189.87
2017-09-12 12:00 | 196.44 | 190.62
2017-09-12 12:30 | 196.97 | 191.21
2017-09-12 13:00 | 197.78 | 192.03
2017-09-12 13:30 | 198.45 | 192.65
2017-09-12 14:00 | 199.95 | 194.27
2017-09-12 14:30 | 200.61 | 195.01
2017-09-12 15:00 | 201.37 | 195.74
2017-09-12 15:30 | 202.06 | 196.44
2017-09-12 16:00 | 202.85 | 197.4
2017-09-12 16:30 | 203.19 | 197.72
2017-09-12 17:00 | 182.73 | 177.87
2017-09-12 17:30 | 181.69 | 176.76
2017-09-12 18:00 | 181.4 | 176.4
2017-09-12 18:30 | 180.81 | 175.8
2017-09-12 19:00 | 179.36 | 174.45
2017-09-12 19:30 | 180.56 | 175.9
2017-09-12 20:00 | 182.45 | 177.97
2017-09-12 20:30 | 183.3 | 178.98
2017-09-12 21:00 | 184.19 | 179.9
2017-09-12 21:30 | 185.56 | 180.94
2017-09-12 22:00 | 186.36 | 181.7
2017-09-12 22:30 | 187.1 | 182.66
2017-09-12 23:00 | 187.63 | 183.3
2017-09-12 23:30 | 194.47 | 188.62
2017-09-13 | 195.99 | 189.75
2017-09-13 00:30 | 195.17 | 188.89
2017-09-13 01:00 | 193.91 | 187.95
2017-09-13 01:30 | 193.39 | 187.32
2017-09-13 02:00 | 192.75 | 186.79
2017-09-13 02:30 | 192.29 | 186.2
2017-09-13 03:00 | 192.62 | 186.41
2017-09-13 03:30 | 192.75 | 186.56
2017-09-13 04:00 | 192.82 | 186.59
2017-09-13 04:30 | 192.92 | 186.8
2017-09-13 05:00 | 193.5 | 187.42
2017-09-13 05:30 | 194.82 | 188.83
2017-09-13 06:00 | 196.69 | 190.76
2017-09-13 06:30 | 198.7 | 192.96
2017-09-13 07:00 | 200.24 | 194.52
2017-09-13 07:30 | 201.78 | 196.11
2017-09-13 08:00 | 198.98 | 195.96
2017-09-13 08:30 | 216.53 | 212.88
2017-09-13 09:00 | 217.04 | 213.34
2017-09-13 09:30 | 216.46 | 212.75
2017-09-13 10:00 | 216.24 | 212.23
2017-09-13 10:30 | 216.79 | 212.77
2017-09-13 11:00 | 215.85 | 211.89
2017-09-13 11:30 | 214.58 | 210.67
2017-09-13 12:00 | 214.67 | 210.75
2017-09-13 12:30 | 219.02 | 215.13
2017-09-13 13:00 | 219.57 | 215.62
2017-09-13 13:30 | 219.86 | 215.94
2017-09-13 14:00 | 221.3 | 217.34
2017-09-13 14:30 | 219.91 | 216.08
2017-09-13 15:00 | 219.7 | 215.9
2017-09-13 15:30 | 215.16 | 211.6
2017-09-13 16:00 | 212.69 | 209.35
2017-09-13 16:30 | 210.8 | 207.61
2017-09-13 17:00 | 209.11 | 206.07
2017-09-13 17:30 | 208.92 | 205.93
2017-09-13 18:00 | 207.67 | 205.47
2017-09-13 18:30 | 206.72 | 205
2017-09-13 19:00 | 205.66 | 203.85
2017-09-13 19:30 | 206.73 | 205.09
2017-09-13 20:00 | 208.94 | 207.39
2017-09-13 20:30 | 209.34 | 207.88
2017-09-13 21:00 | 210.57 | 209.15
2017-09-13 21:30 | 210.88 | 209.29
2017-09-13 22:00 | 211.76 | 210.15
2017-09-13 22:30 | 213.44 | 211.9
2017-09-13 23:00 | 214.4 | 212.95
2017-09-13 23:30 | 198.59 | 193.98
2017-09-14 | 196.26 | 190.5
2017-09-14 00:30 | 194.96 | 189.09
2017-09-14 01:00 | 193.79 | 187.95
2017-09-14 01:30 | 192.77 | 187
2017-09-14 02:00 | 192.38 | 186.55
2017-09-14 02:30 | 191.88 | 185.95
2017-09-14 03:00 | 191.66 | 185.75
2017-09-14 03:30 | 190.93 | 185.05
2017-09-14 04:00 | 190.72 | 184.78
2017-09-14 04:30 | 191.03 | 185.12
2017-09-14 05:00 | 191.13 | 185.25
2017-09-14 05:30 | 190.97 | 185.29
2017-09-14 06:00 | 185.68 | 181.39
2017-09-14 06:30 | 210.47 | 209.3
2017-09-14 07:00 | 208.15 | 206.99
2017-09-14 07:30 | 197.75 | 196.86
2017-09-14 08:00 | 199.27 | 198.36
2017-09-14 08:30 | 202.48 | 201.34
2017-09-14 09:00 | 199.71 | 198.73
2017-09-14 09:30 | 200.11 | 199.21
2017-09-14 10:00 | 200.14 | 199.16
2017-09-14 10:30 | 200.99 | 199.95
2017-09-14 11:00 | 201.49 | 200.47
2017-09-14 11:30 | 201.57 | 200.52
2017-09-14 12:00 | 202.16 | 201.17
2017-09-14 12:30 | 201.88 | 200.89
2017-09-14 13:00 | 202.35 | 201.24
2017-09-14 13:30 | 201.96 | 200.87
2017-09-14 14:00 | 201.76 | 200.67
2017-09-14 14:30 | 201.3 | 200.33
2017-09-14 15:00 | 201.46 | 200.52
2017-09-14 15:30 | 201.75 | 200.77
2017-09-14 16:00 | 200.95 | 199.99
2017-09-14 16:30 | 200.25 | 199.27
2017-09-14 17:00 | 199.47 | 198.43
2017-09-14 17:30 | 197.5 | 196.33
2017-09-14 18:00 | 196.17 | 194.88
2017-09-14 18:30 | 194.32 | 192.92
2017-09-14 19:00 | 192.87 | 191.38
2017-09-14 19:30 | 193.63 | 192.23
2017-09-14 20:00 | 194.55 | 193.22
2017-09-14 20:30 | 195.09 | 193.75
2017-09-14 21:00 | 183.92 | 180.33
2017-09-14 21:30 | 183.18 | 178.83
2017-09-14 22:00 | 182.01 | 177.62
2017-09-14 22:30 | 179.62 | 175.16
2017-09-14 23:00 | 177.95 | 173.38
2017-09-14 23:30 | 176.97 | 172.26
2017-09-15 | 175.3 | 170.47
2017-09-15 00:30 | 175.24 | 170.35
2017-09-15 01:00 | 174.14 | 169.27
2017-09-15 01:30 | 173.71 | 168.75
2017-09-15 02:00 | 173.45 | 168.6
2017-09-15 02:30 | 173.01 | 168.22
2017-09-15 03:00 | 172.76 | 167.99
2017-09-15 03:30 | 172.92 | 168.19
2017-09-15 04:00 | 172.93 | 168.2
2017-09-15 04:30 | 173.63 | 168.93
2017-09-15 05:00 | 174.83 | 170.19
2017-09-15 05:30 | 177.02 | 172.55
2017-09-15 06:00 | 179.73 | 175.37
2017-09-15 06:30 | 183.4 | 179.4
2017-09-15 07:00 | 185.48 | 181.63
2017-09-15 07:30 | 185.38 | 181.62
2017-09-15 08:00 | 183.04 | 179.8
2017-09-15 08:30 | 179.5 | 177.17
2017-09-15 09:00 | 176.4 | 174
2017-09-15 09:30 | 173.9 | 171.42
2017-09-15 10:00 | 172.77 | 170.25
2017-09-15 10:30 | 171.36 | 168.79
2017-09-15 11:00 | 170.52 | 167.92
2017-09-15 11:30 | 170.27 | 167.6
2017-09-15 12:00 | 169.55 | 166.92
2017-09-15 12:30 | 168.85 | 166.21
2017-09-15 13:00 | 168.32 | 165.51
2017-09-15 13:30 | 167.78 | 165
2017-09-15 14:00 | 168.13 | 165.35
2017-09-15 14:30 | 169.19 | 166.29
2017-09-15 15:00 | 170.29 | 167.35
2017-09-15 15:30 | 171.13 | 168.22
2017-09-15 16:00 | 172.05 | 169.19
2017-09-15 16:30 | 173.88 | 171
2017-09-15 17:00 | 176.79 | 172.28
2017-09-15 17:30 | 167.96 | 162.62
2017-09-15 18:00 | 143.74 | 136.71
2017-09-15 18:30 | 144.07 | 136.84
2017-09-15 19:00 | 146.78 | 139.68
2017-09-15 19:30 | 146.02 | 138.98
2017-09-15 20:00 | 144.58 | 137.54
2017-09-15 20:30 | 143.71 | 136.64
2017-09-15 21:00 | 142.95 | 135.79
2017-09-15 21:30 | 143.05 | 136.05
2017-09-15 22:00 | 141.72 | 134.67
2017-09-15 22:30 | 140.02 | 132.66
2017-09-15 23:00 | 138.21 | 130.69
2017-09-15 23:30 | 136.92 | 129.48
2017-09-16 | 135.02 | 127.79
2017-09-16 00:30 | 134.08 | 126.96
2017-09-16 01:00 | 132.31 | 125.94
2017-09-16 01:30 | 131.89 | 125.44
2017-09-16 02:00 | 131.66 | 125.2
2017-09-16 02:30 | 131.24 | 124.92
2017-09-16 03:00 | 131.2 | 124.82
2017-09-16 03:30 | 131.24 | 124.85
2017-09-16 04:00 | 131.08 | 124.74
2017-09-16 04:30 | 132.23 | 126.05
2017-09-16 05:00 | 133.21 | 126.97
2017-09-16 05:30 | 134.23 | 128.07
2017-09-16 06:00 | 135.12 | 128.62
2017-09-16 06:30 | 138.51 | 132.05
2017-09-16 07:00 | 140.01 | 133.77
2017-09-16 07:30 | 138.74 | 132.79
2017-09-16 08:00 | 137.86 | 132.05
2017-09-16 08:30 | 136.56 | 130.79
2017-09-16 09:00 | 135.27 | 129.4
2017-09-16 09:30 | 133.2 | 127.24
2017-09-16 10:00 | 128.59 | 122.93
2017-09-16 10:30 | 130.45 | 123.71
2017-09-16 11:00 | 129.8 | 123.03
2017-09-16 11:30 | 128.24 | 121.52
2017-09-16 12:00 | 130.89 | 124.06
2017-09-16 12:30 | 129.48 | 122.82
2017-09-16 13:00 | 127.28 | 120.69
2017-09-16 13:30 | 128.19 | 121.21
2017-09-16 14:00 | 127.32 | 120.43
2017-09-16 14:30 | 130.19 | 122.99
2017-09-16 15:00 | 131.66 | 124.33
2017-09-16 15:30 | 132.9 | 125.55
2017-09-16 16:00 | 133.83 | 126.56
2017-09-16 16:30 | 135.3 | 127.99
2017-09-16 17:00 | 136.73 | 129.37
2017-09-16 17:30 | 138.2 | 130.99
2017-09-16 18:00 | 140.01 | 132.92
2017-09-16 18:30 | 142.11 | 134.93
2017-09-16 19:00 | 143.26 | 135.93
2017-09-16 19:30 | 142.32 | 134.77
2017-09-16 20:00 | 140.9 | 133.14
2017-09-16 20:30 | 140.43 | 132.35
2017-09-16 21:00 | 139.51 | 131.35
2017-09-16 21:30 | 138.59 | 130.52
2017-09-16 22:00 | 137.8 | 129.67
2017-09-16 22:30 | 136.86 | 128.65
2017-09-16 23:00 | 135.82 | 127.65
2017-09-16 23:30 | 134.78 | 126.8
2017-09-17 | 133.53 | 125.91
2017-09-17 00:30 | 132.59 | 125.27
2017-09-17 01:00 | 131.5 | 124.34
2017-09-17 01:30 | 132.11 | 124.98
2017-09-17 02:00 | 132.2 | 124.76
2017-09-17 02:30 | 131.93 | 124.3
2017-09-17 03:00 | 131.47 | 123.82
2017-09-17 03:30 | 131.45 | 123.79
2017-09-17 04:00 | 131.14 | 123.54
2017-09-17 04:30 | 131.54 | 124.02
2017-09-17 05:00 | 132.29 | 124.82
2017-09-17 05:30 | 132.32 | 124.79
2017-09-17 06:00 | 133.07 | 125.7
2017-09-17 06:30 | 133.76 | 126.58
2017-09-17 07:00 | 135.44 | 128.13
2017-09-17 07:30 | 137.05 | 129.68
2017-09-17 08:00 | 136.76 | 128.91
2017-09-17 08:30 | 135.07 | 127.18
2017-09-17 09:00 | 133.55 | 126.02
2017-09-17 09:30 | 132.29 | 124.81
2017-09-17 10:00 | 131.42 | 123.92
2017-09-17 10:30 | 131.15 | 123.47
2017-09-17 11:00 | 130.73 | 122.98
2017-09-17 11:30 | 129.9 | 122.1
2017-09-17 12:00 | 130.33 | 122.58
2017-09-17 12:30 | 131.1 | 123.27
2017-09-17 13:00 | 131.27 | 123.35
2017-09-17 13:30 | 131.64 | 123.66
2017-09-17 14:00 | 131.95 | 124.19
2017-09-17 14:30 | 132.02 | 124.23
2017-09-17 15:00 | 132.53 | 124.74
2017-09-17 15:30 | 133.45 | 125.76
2017-09-17 16:00 | 134.4 | 126.84
2017-09-17 16:30 | 135.77 | 128.28
2017-09-17 17:00 | 137.13 | 129.45
2017-09-17 17:30 | 139.26 | 131.47
2017-09-17 18:00 | 141.22 | 133.43
2017-09-17 18:30 | 143.02 | 135.46
2017-09-17 19:00 | 145.02 | 137.55
2017-09-17 19:30 | 143.79 | 136.18
2017-09-17 20:00 | 142 | 134.15
2017-09-17 20:30 | 141.07 | 132.98
2017-09-17 21:00 | 139.84 | 131.58
2017-09-17 21:30 | 139.13 | 131.08
2017-09-17 22:00 | 137.73 | 129.61
2017-09-17 22:30 | 136.54 | 128.13
2017-09-17 23:00 | 135.33 | 126.84
2017-09-17 23:30 | 134.51 | 126.05
2017-09-18 | 133.3 | 125.11
2017-09-18 00:30 | 132.39 | 124.58
2017-09-18 01:00 | 131.58 | 123.84
2017-09-18 01:30 | 131.02 | 123.4
2017-09-18 02:00 | 130.41 | 122.74
2017-09-18 02:30 | 130.39 | 122.63
2017-09-18 03:00 | 130.28 | 122.48
2017-09-18 03:30 | 130.3 | 122.43
2017-09-18 04:00 | 130.31 | 122.46
2017-09-18 04:30 | 130.64 | 122.86
2017-09-18 05:00 | 131.39 | 123.69
2017-09-18 05:30 | 132.94 | 125.35
2017-09-18 06:00 | 134.82 | 127.54
2017-09-18 06:30 | 136.8 | 129.61
2017-09-18 07:00 | 138.61 | 131.36
2017-09-18 07:30 | 139.54 | 132.43
2017-09-18 08:00 | 139.34 | 132.16
2017-09-18 08:30 | 138.52 | 131.37
2017-09-18 09:00 | 137.48 | 130.21
2017-09-18 09:30 | 135.99 | 128.57
2017-09-18 10:00 | 136.38 | 128.6
2017-09-18 10:30 | 135.8 | 128.06
2017-09-18 11:00 | 135.8 | 128.19
2017-09-18 11:30 | 135.81 | 128.38
2017-09-18 12:00 | 136.18 | 128.63
2017-09-18 12:30 | 136.24 | 128.3
2017-09-18 13:00 | 136.85 | 129.29
2017-09-18 13:30 | 137.12 | 129.51
2017-09-18 14:00 | 137.87 | 130.46
2017-09-18 14:30 | 138.57 | 131.63
2017-09-18 15:00 | 139.36 | 132.35
2017-09-18 15:30 | 141.14 | 134.14
2017-09-18 16:00 | 141.9 | 134.88
2017-09-18 16:30 | 142.44 | 135.36
2017-09-18 17:00 | 143.59 | 136.46
2017-09-18 17:30 | 139.61 | 132.51
2017-09-18 18:00 | 124.38 | 118.12
2017-09-18 18:30 | 123.12 | 116.71
2017-09-18 19:00 | 121.46 | 114.92
2017-09-18 19:30 | 122.07 | 115.67
2017-09-18 20:00 | 123.72 | 117.55
2017-09-18 20:30 | 124.35 | 118.29
2017-09-18 21:00 | 136.57 | 129.32
2017-09-18 21:30 | 142.18 | 134.85
2017-09-18 22:00 | 140.22 | 132.88
2017-09-18 22:30 | 138.38 | 130.75
2017-09-18 23:00 | 136.79 | 129.04
2017-09-18 23:30 | 136.07 | 128.23
2017-09-19 | 134.74 | 127.14
2017-09-19 00:30 | 133.73 | 126.44
2017-09-19 01:00 | 132.91 | 125.9
2017-09-19 01:30 | 131.79 | 124.74
2017-09-19 02:00 | 131.72 | 124.09
2017-09-19 02:30 | 131.6 | 123.71
2017-09-19 03:00 | 131.11 | 123.27
2017-09-19 03:30 | 131.36 | 123.52
2017-09-19 04:00 | 131.23 | 123.4
2017-09-19 04:30 | 131.89 | 124.19
2017-09-19 05:00 | 132.4 | 124.77
2017-09-19 05:30 | 133.96 | 126.26
2017-09-19 06:00 | 136.04 | 128
2017-09-19 06:30 | 138.19 | 130.49
2017-09-19 07:00 | 138.04 | 130.7
2017-09-19 07:30 | 138.09 | 131.12
2017-09-19 08:00 | 137.66 | 131.17
2017-09-19 08:30 | 137.12 | 130.66
2017-09-19 09:00 | 136.39 | 129.84
2017-09-19 09:30 | 135.37 | 128.62
2017-09-19 10:00 | 135.28 | 128.58
2017-09-19 10:30 | 135.19 | 128.39
2017-09-19 11:00 | 135.43 | 128.7
2017-09-19 11:30 | 136.11 | 129.27
2017-09-19 12:00 | 158.43 | 153.31
2017-09-19 12:30 | 175.13 | 170.75
2017-09-19 13:00 | 176.05 | 171.5
2017-09-19 13:30 | 174.67 | 170.11
2017-09-19 14:00 | 177.94 | 173.57
2017-09-19 14:30 | 179.53 | 175.24
2017-09-19 15:00 | 181.56 | 177.01
2017-09-19 15:30 | 184.86 | 180.07
2017-09-19 16:00 | 179.92 | 175.61
2017-09-19 16:30 | 163.63 | 160.17
2017-09-19 17:00 | 163.37 | 159.71
2017-09-19 17:30 | 146.51 | 142.1
2017-09-19 18:00 | 124.66 | 118.73
2017-09-19 18:30 | 123.73 | 117.59
2017-09-19 19:00 | 122.81 | 116.44
2017-09-19 19:30 | 124.12 | 117.69
2017-09-19 20:00 | 127.87 | 119.01
2017-09-19 20:30 | 128.23 | 119.53
2017-09-19 21:00 | 129.6 | 121.12
2017-09-19 21:30 | 129.8 | 121.51
2017-09-19 22:00 | 142.25 | 132.24
2017-09-19 22:30 | 144.54 | 134.02
2017-09-19 23:00 | 142.75 | 132.11
2017-09-19 23:30 | 141.72 | 130.97
2017-09-20 | 140.13 | 129.32
2017-09-20 00:30 | 139.18 | 128.51
2017-09-20 01:00 | 138.02 | 127.36
2017-09-20 01:30 | 137.52 | 126.74
2017-09-20 02:00 | 137.23 | 126.34
2017-09-20 02:30 | 136.51 | 125.49
2017-09-20 03:00 | 136.46 | 125.27
2017-09-20 03:30 | 137.47 | 126.2
2017-09-20 04:00 | 137.8 | 126.25
2017-09-20 04:30 | 137.69 | 126.33
2017-09-20 05:00 | 138.56 | 127.17
2017-09-20 05:30 | 139.94 | 128.88
2017-09-20 06:00 | 141.6 | 130.76
2017-09-20 06:30 | 144.08 | 133.35
2017-09-20 07:00 | 146.16 | 135.34
2017-09-20 07:30 | 177.5 | 169.74
2017-09-20 08:00 | 184.38 | 176.9
2017-09-20 08:30 | 184.63 | 177.21
2017-09-20 09:00 | 182.73 | 175.18
2017-09-20 09:30 | 168.99 | 160.7
2017-09-20 10:00 | 142.93 | 132.28
2017-09-20 10:30 | 142.97 | 131.97
2017-09-20 11:00 | 143.45 | 132.55
2017-09-20 11:30 | 144.25 | 133.27
2017-09-20 12:00 | 144.48 | 133.45
2017-09-20 12:30 | 139.94 | 130.48
2017-09-20 13:00 | 139.25 | 130.48
2017-09-20 13:30 | 137.42 | 128.5
2017-09-20 14:00 | 136.54 | 127.7
2017-09-20 14:30 | 140.91 | 133.29
2017-09-20 15:00 | 128.14 | 120.12
2017-09-20 15:30 | 126.88 | 120.23
2017-09-20 16:00 | 127.64 | 121.15
2017-09-20 16:30 | 137.63 | 131.64
2017-09-20 17:00 | 158.34 | 152.85
2017-09-20 17:30 | 159.39 | 153
2017-09-20 18:00 | 175.49 | 169.08
2017-09-20 18:30 | 183.73 | 177.39
2017-09-20 19:00 | 186.79 | 180.5
2017-09-20 19:30 | 187.53 | 180.99
2017-09-20 20:00 | 186.13 | 179.4
2017-09-20 20:30 | 185.07 | 178.25
2017-09-20 21:00 | 184.03 | 177.2
2017-09-20 21:30 | 181.74 | 175.54
2017-09-20 22:00 | 180.75 | 174.54
2017-09-20 22:30 | 178.97 | 172.57
2017-09-20 23:00 | 177.72 | 171.68
2017-09-20 23:30 | 175.77 | 170.2
2017-09-21 | 172.05 | 166.56
2017-09-21 00:30 | 171.26 | 166.39
2017-09-21 01:00 | 170.4 | 165.59
2017-09-21 01:30 | 169.49 | 164.8
2017-09-21 02:00 | 168.91 | 164.52
2017-09-21 02:30 | 168.63 | 164.24
2017-09-21 03:00 | 169.26 | 164.77
2017-09-21 03:30 | 169.39 | 164.91
2017-09-21 04:00 | 168.8 | 164.29
2017-09-21 04:30 | 169.31 | 164.81
2017-09-21 05:00 | 170.2 | 165.78
2017-09-21 05:30 | 171.93 | 167.59
2017-09-21 06:00 | 174.07 | 169.82
2017-09-21 06:30 | 176.84 | 172.79
2017-09-21 07:00 | 177.92 | 173.6
2017-09-21 07:30 | 178.19 | 173.5
2017-09-21 08:00 | 176.81 | 172.05
2017-09-21 08:30 | 174.83 | 170.24
2017-09-21 09:00 | 177.37 | 173.09
2017-09-21 09:30 | 180.79 | 176.34
2017-09-21 10:00 | 182.63 | 178.49
2017-09-21 10:30 | 181.7 | 177.8
2017-09-21 11:00 | 179.33 | 175.3
2017-09-21 11:30 | 175.01 | 170.35
2017-09-21 12:00 | 174.15 | 169.31
2017-09-21 12:30 | 173.18 | 168.1
2017-09-21 13:00 | 173.78 | 168.48
2017-09-21 13:30 | 175.56 | 170.25
2017-09-21 14:00 | 175.73 | 170.37
2017-09-21 14:30 | 176.22 | 171.1
2017-09-21 15:00 | 176.67 | 171.91
2017-09-21 15:30 | 183.53 | 178.65
2017-09-21 16:00 | 202.34 | 197.43
2017-09-21 16:30 | 210.2 | 205.12
2017-09-21 17:00 | 211.9 | 206.7
2017-09-21 17:30 | 212.81 | 207.35
2017-09-21 18:00 | 202.83 | 197.62
2017-09-21 18:30 | 188.36 | 183.26
2017-09-21 19:00 | 187.85 | 182.38
2017-09-21 19:30 | 188.35 | 182.85
2017-09-21 20:00 | 189.54 | 184.15
2017-09-21 20:30 | 189.7 | 184.42
2017-09-21 21:00 | 190.9 | 185.94
2017-09-21 21:30 | 190.78 | 186.64
2017-09-21 22:00 | 192.54 | 188.58
2017-09-21 22:30 | 194.05 | 190.05
2017-09-21 23:00 | 193.97 | 190.24
2017-09-21 23:30 | 194 | 190.54
2017-09-22 | 195.21 | 191.91
2017-09-22 00:30 | 195.58 | 192.5
2017-09-22 01:00 | 197.44 | 193.17
2017-09-22 01:30 | 198.4 | 193.99
2017-09-22 02:00 | 197.9 | 193.7
2017-09-22 02:30 | 197.77 | 193.18
2017-09-22 03:00 | 197.89 | 193.32
2017-09-22 03:30 | 197.92 | 193.2
2017-09-22 04:00 | 197.57 | 193
2017-09-22 04:30 | 199.68 | 193.25
2017-09-22 05:00 | 202.81 | 194.05
2017-09-22 05:30 | 204.15 | 195.45
2017-09-22 06:00 | 206.58 | 197.15
2017-09-22 06:30 | 208.52 | 199.33
2017-09-22 07:00 | 210.81 | 200.71
2017-09-22 07:30 | 211.68 | 201.41
2017-09-22 08:00 | 210.75 | 200.74
2017-09-22 08:30 | 209.93 | 199.7
2017-09-22 09:00 | 208.91 | 198.66
2017-09-22 09:30 | 207.21 | 196.79
2017-09-22 10:00 | 207.41 | 197.25
2017-09-22 10:30 | 206.33 | 196.24
2017-09-22 11:00 | 207.35 | 197
2017-09-22 11:30 | 208.17 | 197.47
2017-09-22 12:00 | 208.91 | 198.48
2017-09-22 12:30 | 209.73 | 199.19
2017-09-22 13:00 | 210.55 | 199.64
2017-09-22 13:30 | 211.51 | 200.78
2017-09-22 14:00 | 212.22 | 201.03
2017-09-22 14:30 | 213.09 | 202.04
2017-09-22 15:00 | 215.94 | 204.78
2017-09-22 15:30 | 215.47 | 204.49
2017-09-22 16:00 | 217.57 | 206.61
2017-09-22 16:30 | 219.17 | 208.19
2017-09-22 17:00 | 220.53 | 209.64
2017-09-22 17:30 | 221.03 | 210.05
2017-09-22 18:00 | 221.8 | 210.89
2017-09-22 18:30 | 222.05 | 211.28
2017-09-22 19:00 | 222.38 | 211.79
2017-09-22 19:30 | 221.06 | 209.96
2017-09-22 20:00 | 219.83 | 208.59
2017-09-22 20:30 | 217.82 | 206.53
2017-09-22 21:00 | 216.25 | 204.97
2017-09-22 21:30 | 214.61 | 204.43
2017-09-22 22:00 | 212.77 | 203.05
2017-09-22 22:30 | 211.75 | 201.79
2017-09-22 23:00 | 210.53 | 200.51
2017-09-22 23:30 | 208.95 | 199.71
2017-09-23 | 207.03 | 198.54
2017-09-23 00:30 | 205.41 | 197.55
2017-09-23 01:00 | 204.53 | 196.63
2017-09-23 01:30 | 203.74 | 195.86
2017-09-23 02:00 | 203.17 | 195.28
2017-09-23 02:30 | 203.48 | 195.16
2017-09-23 03:00 | 202.5 | 194.55
2017-09-23 03:30 | 202.42 | 194.46
2017-09-23 04:00 | 202.3 | 194.53
2017-09-23 04:30 | 202.73 | 194.64
2017-09-23 05:00 | 203.39 | 195.08
2017-09-23 05:30 | 203.6 | 195.7
2017-09-23 06:00 | 204.59 | 196.37
2017-09-23 06:30 | 205.43 | 197.25
2017-09-23 07:00 | 207.06 | 198.4
2017-09-23 07:30 | 207.11 | 198.23
2017-09-23 08:00 | 207.6 | 198.4
2017-09-23 08:30 | 207.65 | 198.16
2017-09-23 09:00 | 207.02 | 198.05
2017-09-23 09:30 | 206.71 | 197.81
2017-09-23 10:00 | 191.26 | 182.33
2017-09-23 10:30 | 185.53 | 176.79
2017-09-23 11:00 | 185.34 | 176.97
2017-09-23 11:30 | 185.68 | 177.66
2017-09-23 12:00 | 186.77 | 178.89
2017-09-23 12:30 | 186.61 | 178.73
2017-09-23 13:00 | 187.9 | 179.33
2017-09-23 13:30 | 189.89 | 181.18
2017-09-23 14:00 | 192.29 | 184.07
2017-09-23 14:30 | 205.89 | 197.43
2017-09-23 15:00 | 216 | 208.24
2017-09-23 15:30 | 217.33 | 210.19
2017-09-23 16:00 | 219.13 | 211.39
2017-09-23 16:30 | 221.8 | 211.87
2017-09-23 17:00 | 210.96 | 201.82
2017-09-23 17:30 | 193.06 | 183.87
2017-09-23 18:00 | 193.03 | 183.99
2017-09-23 18:30 | 193.68 | 184.62
2017-09-23 19:00 | 195.09 | 185.77
2017-09-23 19:30 | 193.77 | 184.21
2017-09-23 20:00 | 191.57 | 181.99
2017-09-23 20:30 | 190.76 | 181.16
2017-09-23 21:00 | 191.86 | 182.56
2017-09-23 21:30 | 213.03 | 204.21
2017-09-23 22:00 | 215.94 | 207.14
2017-09-23 22:30 | 214.59 | 205.33
2017-09-23 23:00 | 212.88 | 203.34
2017-09-23 23:30 | 210.91 | 201.94
2017-09-24 | 208.55 | 200.25
2017-09-24 00:30 | 206.65 | 199.16
2017-09-24 01:00 | 204.28 | 198.05
2017-09-24 01:30 | 204.29 | 197.62
2017-09-24 02:00 | 203.24 | 197.17
2017-09-24 02:30 | 204.02 | 197.01
2017-09-24 03:00 | 204.29 | 197.17
2017-09-24 03:30 | 204.55 | 196.89
2017-09-24 04:00 | 204.78 | 196.69
2017-09-24 04:30 | 204.4 | 196.48
2017-09-24 05:00 | 205.03 | 197.21
2017-09-24 05:30 | 204.68 | 197.37
2017-09-24 06:00 | 205 | 197.77
2017-09-24 06:30 | 205.18 | 198.07
2017-09-24 07:00 | 205.88 | 198.46
2017-09-24 07:30 | 205.84 | 198.47
2017-09-24 08:00 | 204.76 | 197.76
2017-09-24 08:30 | 203.89 | 197.18
2017-09-24 09:00 | 204.23 | 196.49
2017-09-24 09:30 | 204.6 | 196.79
2017-09-24 10:00 | 204.92 | 197.77
2017-09-24 10:30 | 205.79 | 198.29
2017-09-24 11:00 | 207.15 | 199.6
2017-09-24 11:30 | 209 | 201.09
2017-09-24 12:00 | 210.21 | 202.55
2017-09-24 12:30 | 211.1 | 203.34
2017-09-24 13:00 | 211.43 | 203.01
2017-09-24 13:30 | 214.44 | 205.92
2017-09-24 14:00 | 215.85 | 207.19
2017-09-24 14:30 | 216.85 | 208.43
2017-09-24 15:00 | 218.11 | 210.07
2017-09-24 15:30 | 219.6 | 211.49
2017-09-24 16:00 | 221.08 | 212.98
2017-09-24 16:30 | 223.07 | 214.95
2017-09-24 17:00 | 224.24 | 215.86
2017-09-24 17:30 | 226.23 | 217.39
2017-09-24 18:00 | 227.22 | 218.59
2017-09-24 18:30 | 228.87 | 219.98
2017-09-24 19:00 | 230.59 | 221.7
2017-09-24 19:30 | 229.22 | 219.81
2017-09-24 20:00 | 225.16 | 215
2017-09-24 20:30 | 224.22 | 214.13
2017-09-24 21:00 | 222.68 | 212.07
2017-09-24 21:30 | 219.62 | 210
2017-09-24 22:00 | 217 | 207.53
2017-09-24 22:30 | 214.33 | 204.8
2017-09-24 23:00 | 212.62 | 202.84
2017-09-24 23:30 | 211.38 | 201.88
2017-09-25 | 209.41 | 200.41
2017-09-25 00:30 | 207.39 | 199.45
2017-09-25 01:00 | 205.57 | 198.58
2017-09-25 01:30 | 205.35 | 198.02
2017-09-25 02:00 | 205.68 | 197.8
2017-09-25 02:30 | 205.37 | 197.56
2017-09-25 03:00 | 205.5 | 197.41
2017-09-25 03:30 | 205.24 | 197.15
2017-09-25 04:00 | 205.1 | 196.95
2017-09-25 04:30 | 204.67 | 196.86
2017-09-25 05:00 | 204.86 | 197.7
2017-09-25 05:30 | 205.35 | 198.78
2017-09-25 06:00 | 207.33 | 200.09
2017-09-25 06:30 | 209.7 | 201.47
2017-09-25 07:00 | 212.13 | 202.59
2017-09-25 07:30 | 213.41 | 203.59
2017-09-25 08:00 | 213.33 | 204.31
2017-09-25 08:30 | 212.74 | 203.7
2017-09-25 09:00 | 211.99 | 202.8
2017-09-25 09:30 | 211.62 | 202.2
2017-09-25 10:00 | 212.5 | 202.53
2017-09-25 10:30 | 212.13 | 201.99
2017-09-25 11:00 | 212.44 | 202.73
2017-09-25 11:30 | 213.54 | 203.59
2017-09-25 12:00 | 214.65 | 204.91
2017-09-25 12:30 | 215.9 | 206.3
2017-09-25 13:00 | 216.27 | 206.48
2017-09-25 13:30 | 217.11 | 207.23
2017-09-25 14:00 | 216.17 | 207.5
2017-09-25 14:30 | 207.21 | 202.76
2017-09-25 15:00 | 204.44 | 200.17
2017-09-25 15:30 | 203.5 | 199.32
2017-09-25 16:00 | 202.66 | 198.64
2017-09-25 16:30 | 201.97 | 197.8
2017-09-25 17:00 | 203.12 | 198.73
2017-09-25 17:30 | 203.98 | 199.25
2017-09-25 18:00 | 204.58 | 199.51
2017-09-25 18:30 | 205.8 | 200.85
2017-09-25 19:00 | 205.91 | 200.69
2017-09-25 19:30 | 207.87 | 202.88
2017-09-25 20:00 | 210.13 | 205.2
2017-09-25 20:30 | 212.48 | 207.32
2017-09-25 21:00 | 214.94 | 209.76
2017-09-25 21:30 | 214.31 | 210.39
2017-09-25 22:00 | 216.94 | 213.44
2017-09-25 22:30 | 219.39 | 215.78
2017-09-25 23:00 | 220.97 | 217.24
2017-09-25 23:30 | 221.87 | 218.27
2017-09-26 | 223.41 | 220.13
2017-09-26 00:30 | 224.37 | 221.16
2017-09-26 01:00 | 207.53 | 199.81
2017-09-26 01:30 | 206.55 | 198.32
2017-09-26 02:00 | 205.9 | 197.61
2017-09-26 02:30 | 206.17 | 197.35
2017-09-26 03:00 | 206.22 | 197.2
2017-09-26 03:30 | 206.28 | 197.11
2017-09-26 04:00 | 206.29 | 197.16
2017-09-26 04:30 | 206.36 | 197.29
2017-09-26 05:00 | 207.06 | 198.01
2017-09-26 05:30 | 207.89 | 199.01
2017-09-26 06:00 | 208.9 | 200.24
2017-09-26 06:30 | 211.68 | 202.01
2017-09-26 07:00 | 213.14 | 203.09
2017-09-26 07:30 | 213.02 | 204.47
2017-09-26 08:00 | 212.43 | 203.96
2017-09-26 08:30 | 222.31 | 219.02
2017-09-26 09:00 | 224.57 | 221.6
2017-09-26 09:30 | 222.75 | 219.72
2017-09-26 10:00 | 221.68 | 218.69
2017-09-26 10:30 | 220.69 | 217.68
2017-09-26 11:00 | 218.25 | 214.98
2017-09-26 11:30 | 217.08 | 213.56
2017-09-26 12:00 | 213.53 | 209.8
2017-09-26 12:30 | 213.43 | 209.54
2017-09-26 13:00 | 211.45 | 207.49
2017-09-26 13:30 | 211.06 | 207.07
2017-09-26 14:00 | 210.48 | 206.59
2017-09-26 14:30 | 209.75 | 205.84
2017-09-26 15:00 | 208.73 | 204.81
2017-09-26 15:30 | 207.52 | 203.61
2017-09-26 16:00 | 206.48 | 202.49
2017-09-26 16:30 | 205.6 | 201.27
2017-09-26 17:00 | 205.07 | 200.37
2017-09-26 17:30 | 205.81 | 201.18
2017-09-26 18:00 | 205.78 | 201.06
2017-09-26 18:30 | 205.77 | 200.89
2017-09-26 19:00 | 206.19 | 200.92
2017-09-26 19:30 | 209.54 | 202.45
2017-09-26 20:00 | 216.33 | 205.63
2017-09-26 20:30 | 218.34 | 208.06
2017-09-26 21:00 | 220.5 | 210.41
2017-09-26 21:30 | 221.72 | 212.5
2017-09-26 22:00 | 222.77 | 213.72
2017-09-26 22:30 | 223.86 | 215.22
2017-09-26 23:00 | 225.48 | 217.29
2017-09-26 23:30 | 226.26 | 217.95
2017-09-27 | 216.03 | 201.01
2017-09-27 00:30 | 215.24 | 200.13
2017-09-27 01:00 | 214.57 | 198.64
2017-09-27 01:30 | 213.81 | 197.42
2017-09-27 02:00 | 213.22 | 196.5
2017-09-27 02:30 | 212.39 | 195.71
2017-09-27 03:00 | 212.66 | 195.68
2017-09-27 03:30 | 212.74 | 195.63
2017-09-27 04:00 | 212.76 | 195.61
2017-09-27 04:30 | 213.13 | 196.1
2017-09-27 05:00 | 213.25 | 196.76
2017-09-27 05:30 | 213.65 | 198.11
2017-09-27 06:00 | 215.29 | 199.44
2017-09-27 06:30 | 208.69 | 192.15
2017-09-27 07:00 | 209.15 | 199.19
2017-09-27 07:30 | 224.15 | 217.6
2017-09-27 08:00 | 222.77 | 216.31
2017-09-27 08:30 | 221.95 | 215.65
2017-09-27 09:00 | 221.39 | 215.08
2017-09-27 09:30 | 221.06 | 214.44
2017-09-27 10:00 | 219.11 | 212.25
2017-09-27 10:30 | 218.22 | 210.96
2017-09-27 11:00 | 216.2 | 208.63
2017-09-27 11:30 | 214.71 | 206.96
2017-09-27 12:00 | 212.8 | 204.82
2017-09-27 12:30 | 210.71 | 202.71
2017-09-27 13:00 | 208.32 | 200.05
2017-09-27 13:30 | 207.21 | 198.66
2017-09-27 14:00 | 205.88 | 197.01
2017-09-27 14:30 | 206.04 | 197.14
2017-09-27 15:00 | 207.3 | 198.18
2017-09-27 15:30 | 206.8 | 197.73
2017-09-27 16:00 | 206.59 | 197.02
2017-09-27 16:30 | 206.49 | 196.6
2017-09-27 17:00 | 204.82 | 194.66
2017-09-27 17:30 | 204.49 | 194.33
2017-09-27 18:00 | 205.36 | 195.29
2017-09-27 18:30 | 206.41 | 196.5
2017-09-27 19:00 | 206.15 | 196.24
2017-09-27 19:30 | 208.66 | 198.98
2017-09-27 20:00 | 211.48 | 202.21
2017-09-27 20:30 | 227.85 | 215.99
2017-09-27 21:00 | 230.26 | 217.61
2017-09-27 21:30 | 225.65 | 215.31
2017-09-27 22:00 | 222.09 | 212.4
2017-09-27 22:30 | 219.85 | 209.7
2017-09-27 23:00 | 218.37 | 207.77
2017-09-27 23:30 | 217.65 | 206.66
2017-09-28 | 216.24 | 205.06
2017-09-28 00:30 | 214.62 | 203.62
2017-09-28 01:00 | 211.22 | 201.99
2017-09-28 01:30 | 210.44 | 201.39
2017-09-28 02:00 | 210.32 | 201.06
2017-09-28 02:30 | 210.47 | 200.83
2017-09-28 03:00 | 209.64 | 200.81
2017-09-28 03:30 | 209.82 | 200.87
2017-09-28 04:00 | 210.8 | 201.28
2017-09-28 04:30 | 210.76 | 201.29
2017-09-28 05:00 | 211.39 | 202.22
2017-09-28 05:30 | 212.79 | 203.22
2017-09-28 06:00 | 214.33 | 204.49
2017-09-28 06:30 | 216.72 | 206.17
2017-09-28 07:00 | 219.42 | 207.3
2017-09-28 07:30 | 221.18 | 208.95
2017-09-28 08:00 | 222.4 | 209.09
2017-09-28 08:30 | 221.18 | 207.63
2017-09-28 09:00 | 221.82 | 208.54
2017-09-28 09:30 | 221.74 | 208.66
2017-09-28 10:00 | 222.57 | 210.01
2017-09-28 10:30 | 222.45 | 209.65
2017-09-28 11:00 | 223.13 | 210.42
2017-09-28 11:30 | 223.81 | 211.51
2017-09-28 12:00 | 216.41 | 206.33
2017-09-28 12:30 | 214.2 | 207.01
2017-09-28 13:00 | 212.2 | 204.82
2017-09-28 13:30 | 211.37 | 203.7
2017-09-28 14:00 | 209.97 | 202.39
2017-09-28 14:30 | 209.05 | 201.15
2017-09-28 15:00 | 208.56 | 200.34
2017-09-28 15:30 | 207.99 | 199.77
2017-09-28 16:00 | 207.52 | 199.4
2017-09-28 16:30 | 207.56 | 199.33
2017-09-28 17:00 | 208.01 | 199.67
2017-09-28 17:30 | 208.56 | 200.04
2017-09-28 18:00 | 208.83 | 200.33
2017-09-28 18:30 | 209.41 | 201
2017-09-28 19:00 | 209.61 | 201.26
2017-09-28 19:30 | 210.7 | 202.57
2017-09-28 20:00 | 212.68 | 204.94
2017-09-28 20:30 | 214.86 | 207.41
2017-09-28 21:00 | 216.44 | 209.73
2017-09-28 21:30 | 217.28 | 211.13
2017-09-28 22:00 | 218.98 | 213.37
2017-09-28 22:30 | 222.14 | 216.73
2017-09-28 23:00 | 223.92 | 218.5
2017-09-28 23:30 | 225.37 | 219.67
2017-09-29 | 227.06 | 221.64
2017-09-29 00:30 | 228.85 | 223.08
2017-09-29 01:00 | 215.14 | 202.27
2017-09-29 01:30 | 213.92 | 200.47
2017-09-29 02:00 | 213.05 | 199.75
2017-09-29 02:30 | 212.53 | 198.87
2017-09-29 03:00 | 211.86 | 198.15
2017-09-29 03:30 | 211.92 | 198.24
2017-09-29 04:00 | 211.28 | 197.9
2017-09-29 04:30 | 211.21 | 197.88
2017-09-29 05:00 | 211.96 | 198.99
2017-09-29 05:30 | 213.05 | 199.68
2017-09-29 06:00 | 216.85 | 200.64
2017-09-29 06:30 | 218.49 | 202.06
2017-09-29 07:00 | 215.07 | 202.82
2017-09-29 07:30 | 213.17 | 203.28
2017-09-29 08:00 | 212.63 | 202.72
2017-09-29 08:30 | 212.74 | 202.72
2017-09-29 09:00 | 213.16 | 202.98
2017-09-29 09:30 | 213.15 | 202.59
2017-09-29 10:00 | 216.48 | 206.15
2017-09-29 10:30 | 212.95 | 202.58
2017-09-29 11:00 | 212.96 | 202.94
2017-09-29 11:30 | 213.51 | 203.54
2017-09-29 12:00 | 214.19 | 204.43
2017-09-29 12:30 | 214.67 | 204.95
2017-09-29 13:00 | 215.6 | 205.75
2017-09-29 13:30 | 206.34 | 198.71
2017-09-29 14:00 | 215.06 | 210.47
2017-09-29 14:30 | 213.96 | 208.92
2017-09-29 15:00 | 213.18 | 207.93
2017-09-29 15:30 | 212.18 | 206.94
2017-09-29 16:00 | 211.54 | 206.15
2017-09-29 16:30 | 210.91 | 205.52
2017-09-29 17:00 | 210.64 | 205.18
2017-09-29 17:30 | 211.29 | 205.52
2017-09-29 18:00 | 212.58 | 206.68
2017-09-29 18:30 | 213.29 | 207.52
2017-09-29 19:00 | 213.08 | 207.4
2017-09-29 19:30 | 214.92 | 209.33
2017-09-29 20:00 | 216.69 | 211.29
2017-09-29 20:30 | 217.48 | 212.25
2017-09-29 21:00 | 218.79 | 213.78
2017-09-29 21:30 | 218.23 | 214.34
2017-09-29 22:00 | 219.58 | 216.09
2017-09-29 22:30 | 220.7 | 217.42
2017-09-29 23:00 | 222.07 | 218.81
2017-09-29 23:30 | 210.14 | 201.37
2017-09-30 | 209.31 | 199.19
2017-09-30 00:30 | 208.56 | 198.54
2017-09-30 01:00 | 206.42 | 197.52
2017-09-30 01:30 | 205.29 | 197.04
2017-09-30 02:00 | 205.07 | 196.5
2017-09-30 02:30 | 204.8 | 195.55
2017-09-30 03:00 | 204.83 | 195.35
2017-09-30 03:30 | 204.46 | 194.9
2017-09-30 04:00 | 204.66 | 194.92
2017-09-30 04:30 | 204.95 | 194.69
2017-09-30 05:00 | 205.63 | 195.12
2017-09-30 05:30 | 206.17 | 195.91
2017-09-30 06:00 | 206.72 | 196.48
2017-09-30 06:30 | 207.48 | 197.39
2017-09-30 07:00 | 213.24 | 203.69
2017-09-30 07:30 | 218.68 | 209.91
2017-09-30 08:00 | 218.97 | 211.2
2017-09-30 08:30 | 218.28 | 210.3
2017-09-30 09:00 | 218.6 | 210.97
2017-09-30 09:30 | 216.89 | 209.22
2017-09-30 10:00 | 214.31 | 206.13
2017-09-30 10:30 | 211.91 | 203.75
2017-09-30 11:00 | 214.72 | 206.31
2017-09-30 11:30 | 216.37 | 207.44
2017-09-30 12:00 | 217.9 | 208.27
2017-09-30 12:30 | 219.51 | 209.72
2017-09-30 13:00 | 221.07 | 211.14
2017-09-30 13:30 | 224.34 | 214.36
2017-09-30 14:00 | 224.47 | 214.62
2017-09-30 14:30 | 225.91 | 215.95
2017-09-30 15:00 | 226.87 | 217.06
2017-09-30 15:30 | 230.06 | 223.64
2017-09-30 16:00 | 238.12 | 234.58
2017-09-30 16:30 | 237.78 | 234
2017-09-30 17:00 | 237.79 | 233.71
2017-09-30 17:30 | 238.79 | 234.45
2017-09-30 18:00 | 237.97 | 233.55
2017-09-30 18:30 | 238.29 | 233.92
2017-09-30 19:00 | 239.05 | 234.22
2017-09-30 19:30 | 240.4 | 235.93
2017-09-30 20:00 | 242.05 | 237.58
2017-09-30 20:30 | 232.5 | 221.92
2017-09-30 21:00 | 232.89 | 221.01
2017-09-30 21:30 | 232.59 | 221.02
2017-09-30 22:00 | 231.37 | 219.65
2017-09-30 22:30 | 230.4 | 218.69
2017-09-30 23:00 | 228.83 | 216.96
2017-09-30 23:30 | 227.44 | 216.01
2017-10-01 | 226.15 | 215.78
2017-10-01 00:30 | 225.54 | 216.12
2017-10-01 01:00 | 223.85 | 215.72
2017-10-01 01:30 | 223.32 | 215.12
2017-10-01 02:00 | 223.23 | 214.39
2017-10-01 02:30 | 222.53 | 213.66
2017-10-01 03:00 | 222.49 | 213.83
2017-10-01 03:30 | 221.8 | 212.78
2017-10-01 04:00 | 221.15 | 212.15
2017-10-01 04:30 | 222.06 | 213.26
2017-10-01 05:00 | 222.47 | 213.78
2017-10-01 05:30 | 222.57 | 214.1
2017-10-01 06:00 | 221.99 | 213.36
2017-10-01 06:30 | 220.47 | 212.2
2017-10-01 07:00 | 220.51 | 212.3
2017-10-01 07:30 | 221.27 | 213.56
2017-10-01 08:00 | 221.82 | 214.3
2017-10-01 08:30 | 224.04 | 216.1
2017-10-01 09:00 | 226.55 | 218.47
2017-10-01 09:30 | 227.32 | 218.57
2017-10-01 10:00 | 230.22 | 221.78
2017-10-01 10:30 | 230.68 | 222.23
2017-10-01 11:00 | 231.33 | 223.24
2017-10-01 11:30 | 232.17 | 224.06
2017-10-01 12:00 | 232.53 | 224.32
2017-10-01 12:30 | 233.12 | 224.75
2017-10-01 13:00 | 231.87 | 222.95
2017-10-01 13:30 | 232.27 | 223.25
2017-10-01 14:00 | 231.78 | 222.82
2017-10-01 14:30 | 232.18 | 223.29
2017-10-01 15:00 | 232.46 | 223.68
2017-10-01 15:30 | 233.71 | 224.91
2017-10-01 16:00 | 239.37 | 232.87
2017-10-01 16:30 | 251.55 | 248.15
2017-10-01 17:00 | 250.07 | 246.58
2017-10-01 17:30 | 249.29 | 245.69
2017-10-01 18:00 | 247.95 | 243.76
2017-10-01 18:30 | 247.65 | 243.19
2017-10-01 19:00 | 247.97 | 243.5
2017-10-01 19:30 | 249.13 | 244.68
2017-10-01 20:00 | 249.13 | 244.69
2017-10-01 20:30 | 249.07 | 244.59
2017-10-01 21:00 | 249.98 | 245.6
2017-10-01 21:30 | 235.43 | 225.61
2017-10-01 22:00 | 234.76 | 223.94
2017-10-01 22:30 | 232.56 | 221.84
2017-10-01 23:00 | 231.76 | 220.02
2017-10-01 23:30 | 230.03 | 219.07
2017-10-02 | 229.23 | 218.18
2017-10-02 00:30 | 228.77 | 217.57
2017-10-02 01:00 | 227.54 | 216.58
2017-10-02 01:30 | 227.17 | 216.42
2017-10-02 02:00 | 227.54 | 216.31
2017-10-02 02:30 | 227 | 215.63
2017-10-02 03:00 | 227.14 | 215.65
2017-10-02 03:30 | 228.26 | 217.87
2017-10-02 04:00 | 229.28 | 219.06
2017-10-02 04:30 | 228.41 | 218.86
2017-10-02 05:00 | 228.7 | 219.35
2017-10-02 05:30 | 228.96 | 220.03
2017-10-02 06:00 | 230.36 | 221
2017-10-02 06:30 | 231.08 | 221.91
2017-10-02 07:00 | 231.71 | 222.96
2017-10-02 07:30 | 232.48 | 224.86
2017-10-02 08:00 | 233.12 | 225.27
2017-10-02 08:30 | 234.18 | 225.66
2017-10-02 09:00 | 234.56 | 226
2017-10-02 09:30 | 235.54 | 226.28
2017-10-02 10:00 | 224.96 | 215.69
2017-10-02 10:30 | 226.72 | 216.79
2017-10-02 11:00 | 227.52 | 217.84
2017-10-02 11:30 | 228.06 | 218.67
2017-10-02 12:00 | 228.27 | 218.95
2017-10-02 12:30 | 228.52 | 218.92
2017-10-02 13:00 | 226.94 | 217.56
2017-10-02 13:30 | 226.82 | 217.22
2017-10-02 14:00 | 227.24 | 217.8
2017-10-02 14:30 | 229.42 | 219.74
2017-10-02 15:00 | 228.61 | 219.03
2017-10-02 15:30 | 227.31 | 217.5
2017-10-02 16:00 | 226.49 | 216.7
2017-10-02 16:30 | 228.08 | 218.2
2017-10-02 17:00 | 234.05 | 227.38
2017-10-02 17:30 | 246.35 | 242.48
2017-10-02 18:00 | 243.57 | 239.76
2017-10-02 18:30 | 239.59 | 235.34
2017-10-02 19:00 | 239.36 | 234.89
2017-10-02 19:30 | 239.94 | 235.59
2017-10-02 20:00 | 240.95 | 236.65
2017-10-02 20:30 | 240.97 | 236.83
2017-10-02 21:00 | 241.69 | 237.44
2017-10-02 21:30 | 240.97 | 237.2
2017-10-02 22:00 | 242.74 | 238.82
2017-10-02 22:30 | 243.92 | 240.31
2017-10-02 23:00 | 245.15 | 241.55
2017-10-02 23:30 | 224.68 | 214.69
2017-10-03 | 222.52 | 210.96
2017-10-03 00:30 | 221.18 | 210.05
2017-10-03 01:00 | 220.3 | 208.93
2017-10-03 01:30 | 219.04 | 207.82
2017-10-03 02:00 | 218.67 | 207.44
2017-10-03 02:30 | 218.36 | 206.99
2017-10-03 03:00 | 218.42 | 207.46
2017-10-03 03:30 | 218.73 | 208.02
2017-10-03 04:00 | 218.92 | 208.38
2017-10-03 04:30 | 219.06 | 208.68
2017-10-03 05:00 | 219.73 | 209.41
2017-10-03 05:30 | 221.18 | 211.2
2017-10-03 06:00 | 222.79 | 212.93
2017-10-03 06:30 | 224.86 | 215.53
2017-10-03 07:00 | 216.99 | 207.83
2017-10-03 07:30 | 215.15 | 205.76
2017-10-03 08:00 | 241.58 | 236.92
2017-10-03 08:30 | 242.31 | 237.83
2017-10-03 09:00 | 242.07 | 237.69
2017-10-03 09:30 | 242.07 | 237.59
2017-10-03 10:00 | 242.44 | 238.03
2017-10-03 10:30 | 243.73 | 239.29
2017-10-03 11:00 | 244.11 | 239.6
2017-10-03 11:30 | 242.67 | 237.7
2017-10-03 12:00 | 242.31 | 237.27
2017-10-03 12:30 | 242.25 | 237.38
2017-10-03 13:00 | 241.9 | 237.26
2017-10-03 13:30 | 240.32 | 235.75
2017-10-03 14:00 | 239.08 | 234.51
2017-10-03 14:30 | 240.26 | 235.78
2017-10-03 15:00 | 239.68 | 235.27
2017-10-03 15:30 | 238.68 | 234.17
2017-10-03 16:00 | 237.33 | 232.83
2017-10-03 16:30 | 236.65 | 232.23
2017-10-03 17:00 | 235.67 | 230.95
2017-10-03 17:30 | 235.04 | 230.1
2017-10-03 18:00 | 235.18 | 229.83
2017-10-03 18:30 | 235.09 | 229.38
2017-10-03 19:00 | 233.41 | 228.17
2017-10-03 19:30 | 234.33 | 228.96
2017-10-03 20:00 | 235.95 | 230.59
2017-10-03 20:30 | 237.01 | 232.02
2017-10-03 21:00 | 238.32 | 233.34
2017-10-03 21:30 | 238.29 | 233.58
2017-10-03 22:00 | 238.86 | 234.17
2017-10-03 22:30 | 240.02 | 235.58
2017-10-03 23:00 | 241.05 | 236.93
2017-10-03 23:30 | 221.59 | 210.81
2017-10-04 | 219.75 | 208.3
2017-10-04 00:30 | 218.67 | 207.87
2017-10-04 01:00 | 217.83 | 207.07
2017-10-04 01:30 | 217.02 | 206.12
2017-10-04 02:00 | 216.62 | 205.57
2017-10-04 02:30 | 216.57 | 205.32
2017-10-04 03:00 | 216.43 | 205.1
2017-10-04 03:30 | 216.4 | 205.11
2017-10-04 04:00 | 216.51 | 205.35
2017-10-04 04:30 | 216.69 | 205.75
2017-10-04 05:00 | 217.17 | 206.53
2017-10-04 05:30 | 218.45 | 208.21
2017-10-04 06:00 | 220.36 | 210.39
2017-10-04 06:30 | 216.24 | 207.3
2017-10-04 07:00 | 234.91 | 229.96
2017-10-04 07:30 | 239.73 | 235
2017-10-04 08:00 | 240.03 | 235.17
2017-10-04 08:30 | 240.88 | 236.12
2017-10-04 09:00 | 240.86 | 236.23
2017-10-04 09:30 | 240.22 | 235.76
2017-10-04 10:00 | 239.59 | 235.04
2017-10-04 10:30 | 238.5 | 233.96
2017-10-04 11:00 | 238.54 | 233.89
2017-10-04 11:30 | 237.2 | 232.29
2017-10-04 12:00 | 235.26 | 230.06
2017-10-04 12:30 | 234.58 | 229.41
2017-10-04 13:00 | 232.78 | 227.15
2017-10-04 13:30 | 231.32 | 225.55
2017-10-04 14:00 | 229.47 | 223.55
2017-10-04 14:30 | 230.37 | 224.57
2017-10-04 15:00 | 230.77 | 224.86
2017-10-04 15:30 | 230.58 | 224.69
2017-10-04 16:00 | 230.03 | 224.38
2017-10-04 16:30 | 231.39 | 225.75
2017-10-04 17:00 | 231.44 | 225.64
2017-10-04 17:30 | 230.14 | 224
2017-10-04 18:00 | 229.84 | 223.47
2017-10-04 18:30 | 229.22 | 222.92
2017-10-04 19:00 | 228.48 | 222.11
2017-10-04 19:30 | 230.23 | 223.78
2017-10-04 20:00 | 232.04 | 225.69
2017-10-04 20:30 | 232.45 | 226.47
2017-10-04 21:00 | 228.21 | 216.67
2017-10-04 21:30 | 228.68 | 215.89
2017-10-04 22:00 | 225.87 | 214.11
2017-10-04 22:30 | 224.75 | 212.83
2017-10-04 23:00 | 222.93 | 210.72
2017-10-04 23:30 | 222.5 | 209.99
2017-10-05 | 220.89 | 208.44
2017-10-05 00:30 | 218.9 | 207.28
2017-10-05 01:00 | 216.64 | 206.54
2017-10-05 01:30 | 215.15 | 206.17
2017-10-05 02:00 | 214.81 | 205.48
2017-10-05 02:30 | 214.18 | 204.88
2017-10-05 03:00 | 213.57 | 204.03
2017-10-05 03:30 | 213.43 | 204.14
2017-10-05 04:00 | 213.13 | 203.86
2017-10-05 04:30 | 213.37 | 203.72
2017-10-05 05:00 | 214.63 | 204.73
2017-10-05 05:30 | 216.16 | 206.12
2017-10-05 06:00 | 218.32 | 208.47
2017-10-05 06:30 | 220.9 | 210.52
2017-10-05 07:00 | 226.41 | 220.47
2017-10-05 07:30 | 235.57 | 230.62
2017-10-05 08:00 | 236.12 | 230.62
2017-10-05 08:30 | 237.9 | 232.55
2017-10-05 09:00 | 238.25 | 232.83
2017-10-05 09:30 | 238.63 | 233.41
2017-10-05 10:00 | 238.3 | 233.04
2017-10-05 10:30 | 237.79 | 232.42
2017-10-05 11:00 | 236.78 | 231.28
2017-10-05 11:30 | 236.56 | 231.02
2017-10-05 12:00 | 235.9 | 230.34
2017-10-05 12:30 | 234.18 | 228.78
2017-10-05 13:00 | 232.92 | 227.3
2017-10-05 13:30 | 232.2 | 226.25
2017-10-05 14:00 | 230.78 | 224.81
2017-10-05 14:30 | 231.02 | 224.98
2017-10-05 15:00 | 230.74 | 224.69
2017-10-05 15:30 | 230.33 | 223.98
2017-10-05 16:00 | 229.81 | 223.37
2017-10-05 16:30 | 228.49 | 222.12
2017-10-05 17:00 | 228.33 | 222.04
2017-10-05 17:30 | 228.82 | 222.38
2017-10-05 18:00 | 229.09 | 222.7
2017-10-05 18:30 | 228.89 | 222.39
2017-10-05 19:00 | 229.03 | 221.88
2017-10-05 19:30 | 231.24 | 223.83
2017-10-05 20:00 | 232.99 | 225.85
2017-10-05 20:30 | 234.13 | 227.31
2017-10-05 21:00 | 233.37 | 222.37
2017-10-05 21:30 | 232.79 | 222.68
2017-10-05 22:00 | 229.87 | 220.48
2017-10-05 22:30 | 227.67 | 218.26
2017-10-05 23:00 | 226.39 | 216.34
2017-10-05 23:30 | 225.58 | 215.29
2017-10-06 | 223.72 | 214.1
2017-10-06 00:30 | 223.19 | 213.47
2017-10-06 01:00 | 222.03 | 212.28
2017-10-06 01:30 | 220.45 | 211.54
2017-10-06 02:00 | 220.07 | 210.98
2017-10-06 02:30 | 220.09 | 210.66
2017-10-06 03:00 | 219.77 | 210.24
2017-10-06 03:30 | 220.07 | 210.18
2017-10-06 04:00 | 219.56 | 209.98
2017-10-06 04:30 | 219.36 | 209.72
2017-10-06 05:00 | 219.79 | 210.52
2017-10-06 05:30 | 220.79 | 211.77
2017-10-06 06:00 | 222.68 | 213.83
2017-10-06 06:30 | 219.73 | 211.59
2017-10-06 07:00 | 239.3 | 234.79
2017-10-06 07:30 | 238.28 | 233.49
2017-10-06 08:00 | 238.41 | 233.46
2017-10-06 08:30 | 238.2 | 233.09
2017-10-06 09:00 | 237.66 | 232.4
2017-10-06 09:30 | 237.23 | 231.89
2017-10-06 10:00 | 236.11 | 230.81
2017-10-06 10:30 | 236.37 | 231.04
2017-10-06 11:00 | 235.34 | 229.8
2017-10-06 11:30 | 233.73 | 228.14
2017-10-06 12:00 | 232.29 | 226.58
2017-10-06 12:30 | 230.53 | 224.76
2017-10-06 13:00 | 229.49 | 223.43
2017-10-06 13:30 | 230.77 | 224.58
2017-10-06 14:00 | 229.16 | 222.8
2017-10-06 14:30 | 229 | 222.64
2017-10-06 15:00 | 229.25 | 223.04
2017-10-06 15:30 | 225.75 | 218.6
2017-10-06 16:00 | 226.19 | 219.1
2017-10-06 16:30 | 227.93 | 221.02
2017-10-06 17:00 | 230.25 | 223.75
2017-10-06 17:30 | 233.53 | 227.29
2017-10-06 18:00 | 234.33 | 227.98
2017-10-06 18:30 | 234.59 | 228.27
2017-10-06 19:00 | 234.43 | 228.06
2017-10-06 19:30 | 235.23 | 228.77
2017-10-06 20:00 | 236.52 | 230.12
2017-10-06 20:30 | 236.61 | 230.18
2017-10-06 21:00 | 237.1 | 231.66
2017-10-06 21:30 | 236.49 | 232.14
2017-10-06 22:00 | 226.55 | 217.98
2017-10-06 22:30 | 225.93 | 215.53
2017-10-06 23:00 | 223.94 | 214.26
2017-10-06 23:30 | 224.02 | 213.65
2017-10-07 | 222.68 | 212.59
2017-10-07 00:30 | 222.13 | 211.76
2017-10-07 01:00 | 220.66 | 210.36
2017-10-07 01:30 | 220.46 | 209.99
2017-10-07 02:00 | 220.04 | 209.52
2017-10-07 02:30 | 220.11 | 209.54
2017-10-07 03:00 | 219.73 | 209.38
2017-10-07 03:30 | 219.09 | 208.95
2017-10-07 04:00 | 218.52 | 208.65
2017-10-07 04:30 | 218.24 | 208.74
2017-10-07 05:00 | 218.93 | 209.65
2017-10-07 05:30 | 219.45 | 210.24
2017-10-07 06:00 | 219.95 | 210.71
2017-10-07 06:30 | 220.75 | 211.77
2017-10-07 07:00 | 221.36 | 212.83
2017-10-07 07:30 | 222.56 | 213.97
2017-10-07 08:00 | 223.01 | 214.22
2017-10-07 08:30 | 225.05 | 214.94
2017-10-07 09:00 | 225.31 | 214.49
2017-10-07 09:30 | 213.73 | 201.93
2017-10-07 10:00 | 204.98 | 193.02
2017-10-07 10:30 | 204.42 | 192.4
2017-10-07 11:00 | 204.3 | 192.36
2017-10-07 11:30 | 204.46 | 192.32
2017-10-07 12:00 | 206.39 | 194.21
2017-10-07 12:30 | 224.8 | 213.06
2017-10-07 13:00 | 224.65 | 213.27
2017-10-07 13:30 | 223.38 | 211.64
2017-10-07 14:00 | 224.42 | 212.3
2017-10-07 14:30 | 224.6 | 212.62
2017-10-07 15:00 | 225.57 | 213.58
2017-10-07 15:30 | 226.73 | 214.86
2017-10-07 16:00 | 222.43 | 210.96
2017-10-07 16:30 | 208.33 | 197.1
2017-10-07 17:00 | 207.46 | 196.62
2017-10-07 17:30 | 206.84 | 195.86
2017-10-07 18:00 | 207.02 | 196.03
2017-10-07 18:30 | 206.49 | 195.71
2017-10-07 19:00 | 206.12 | 195.08
2017-10-07 19:30 | 207.28 | 196.25
2017-10-07 20:00 | 209.52 | 198.69
2017-10-07 20:30 | 210.26 | 199.67
2017-10-07 21:00 | 227.74 | 216.37
2017-10-07 21:30 | 229.71 | 219.38
2017-10-07 22:00 | 227.82 | 217.94
2017-10-07 22:30 | 226.77 | 216.42
2017-10-07 23:00 | 226.06 | 215.49
2017-10-07 23:30 | 225.1 | 214.81
2017-10-08 | 223.95 | 213.91
2017-10-08 00:30 | 223.22 | 213.13
2017-10-08 01:00 | 222.46 | 212.32
2017-10-08 01:30 | 222.34 | 211.62
2017-10-08 02:00 | 222.46 | 211.2
2017-10-08 02:30 | 222.12 | 210.95
2017-10-08 03:00 | 222.43 | 210.96
2017-10-08 03:30 | 222.23 | 210.91
2017-10-08 04:00 | 222.15 | 210.85
2017-10-08 04:30 | 222.4 | 211.18
2017-10-08 05:00 | 222.74 | 211.69
2017-10-08 05:30 | 223.01 | 212.16
2017-10-08 06:00 | 222.82 | 212.5
2017-10-08 06:30 | 222.45 | 212.86
2017-10-08 07:00 | 222.25 | 213.29
2017-10-08 07:30 | 222.26 | 213.93
2017-10-08 08:00 | 223.26 | 214.15
2017-10-08 08:30 | 224.07 | 213.73
2017-10-08 09:00 | 224.19 | 213.96
2017-10-08 09:30 | 224.8 | 213.81
2017-10-08 10:00 | 226.93 | 213.57
2017-10-08 10:30 | 226.58 | 213.41
2017-10-08 11:00 | 226.61 | 213.27
2017-10-08 11:30 | 226.56 | 213.04
2017-10-08 12:00 | 227.17 | 213.7
2017-10-08 12:30 | 226.57 | 214.6
2017-10-08 13:00 | 226.06 | 214.9
2017-10-08 13:30 | 226.41 | 215.72
2017-10-08 14:00 | 225.6 | 215.22
2017-10-08 14:30 | 225.36 | 215.58
2017-10-08 15:00 | 226.8 | 216.42
2017-10-08 15:30 | 227.72 | 217.41
2017-10-08 16:00 | 227.36 | 217.15
2017-10-08 16:30 | 227.78 | 217.45
2017-10-08 17:00 | 228.41 | 218.06
2017-10-08 17:30 | 225.65 | 217.41
2017-10-08 18:00 | 225.59 | 220.18
2017-10-08 18:30 | 226.03 | 220.45
2017-10-08 19:00 | 227.17 | 221.34
2017-10-08 19:30 | 228.26 | 222.52
2017-10-08 20:00 | 229.32 | 223.65
2017-10-08 20:30 | 230.9 | 225.56
2017-10-08 21:00 | 232.02 | 226.77
2017-10-08 21:30 | 228.05 | 216.72
2017-10-08 22:00 | 229 | 216.3
2017-10-08 22:30 | 227.57 | 214.54
2017-10-08 23:00 | 226.5 | 212.87
2017-10-08 23:30 | 224.97 | 211.87
2017-10-09 | 222.45 | 210.83
2017-10-09 00:30 | 220.53 | 210.02
2017-10-09 01:00 | 219.93 | 209.31
2017-10-09 01:30 | 219.82 | 208.8
2017-10-09 02:00 | 219.98 | 208.32
2017-10-09 02:30 | 219.8 | 208.07
2017-10-09 03:00 | 219.48 | 207.84
2017-10-09 03:30 | 219.04 | 207.67
2017-10-09 04:00 | 218.55 | 207.49
2017-10-09 04:30 | 219.2 | 208.18
2017-10-09 05:00 | 219.87 | 209.13
2017-10-09 05:30 | 220.58 | 210.59
2017-10-09 06:00 | 220.71 | 211.92
2017-10-09 06:30 | 223.14 | 213.84
2017-10-09 07:00 | 227.07 | 215.73
2017-10-09 07:30 | 226.61 | 219.44
2017-10-09 08:00 | 236 | 231.14
2017-10-09 08:30 | 234.11 | 228.84
2017-10-09 09:00 | 233.4 | 227.8
2017-10-09 09:30 | 232.35 | 226.68
2017-10-09 10:00 | 232.34 | 226.87
2017-10-09 10:30 | 232.84 | 227.19
2017-10-09 11:00 | 231.25 | 225.11
2017-10-09 11:30 | 230.74 | 224.41
2017-10-09 12:00 | 230.31 | 224.02
2017-10-09 12:30 | 228.57 | 222.28
2017-10-09 13:00 | 227.58 | 221.02
2017-10-09 13:30 | 227.39 | 220.56
2017-10-09 14:00 | 227.41 | 220.58
2017-10-09 14:30 | 226.49 | 219.88
2017-10-09 15:00 | 226.51 | 219.67
2017-10-09 15:30 | 226.25 | 219
2017-10-09 16:00 | 225.81 | 218.67
2017-10-09 16:30 | 225.38 | 218.07
2017-10-09 17:00 | 225.75 | 218.39
2017-10-09 17:30 | 227.06 | 219.81
2017-10-09 18:00 | 227.33 | 220.63
2017-10-09 18:30 | 233.4 | 227.87
2017-10-09 19:00 | 233.14 | 227.51
2017-10-09 19:30 | 233.94 | 228.35
2017-10-09 20:00 | 233.59 | 229.35
2017-10-09 20:30 | 231.56 | 226.74
2017-10-09 21:00 | 230.2 | 224.93
2017-10-09 21:30 | 227.03 | 215.8
2017-10-09 22:00 | 226.81 | 214.46
2017-10-09 22:30 | 223.82 | 211.67
2017-10-09 23:00 | 221.73 | 209.7
2017-10-09 23:30 | 221.28 | 208.91
2017-10-10 | 219.79 | 207.58
2017-10-10 00:30 | 219.17 | 207.42
2017-10-10 01:00 | 218.33 | 206.29
2017-10-10 01:30 | 217.57 | 205.76
2017-10-10 02:00 | 217.14 | 205.37
2017-10-10 02:30 | 216.69 | 204.8
2017-10-10 03:00 | 216.79 | 204.55
2017-10-10 03:30 | 216.65 | 204.25
2017-10-10 04:00 | 216.24 | 203.85
2017-10-10 04:30 | 216.42 | 204.13
2017-10-10 05:00 | 217.01 | 205.21
2017-10-10 05:30 | 217.56 | 206.39
2017-10-10 06:00 | 216.18 | 206.26
2017-10-10 06:30 | 229.02 | 224.67
2017-10-10 07:00 | 232.58 | 228.1
2017-10-10 07:30 | 231.72 | 226.98
2017-10-10 08:00 | 231.44 | 226.41
2017-10-10 08:30 | 231 | 225.73
2017-10-10 09:00 | 230.69 | 225.11
2017-10-10 09:30 | 229.94 | 224.31
2017-10-10 10:00 | 228.55 | 222.92
2017-10-10 10:30 | 226.9 | 221.11
2017-10-10 11:00 | 226.56 | 220.49
2017-10-10 11:30 | 226.09 | 220.22
2017-10-10 12:00 | 226.33 | 220.31
2017-10-10 12:30 | 225.1 | 218.96
2017-10-10 13:00 | 224.25 | 218.37
2017-10-10 13:30 | 224.02 | 217.46
2017-10-10 14:00 | 222.52 | 215.77
2017-10-10 14:30 | 221.79 | 215.09
2017-10-10 15:00 | 221.8 | 215.06
2017-10-10 15:30 | 221.7 | 215.16
2017-10-10 16:00 | 220.72 | 214.19
2017-10-10 16:30 | 219.53 | 212.86
2017-10-10 17:00 | 219.5 | 212.62
2017-10-10 17:30 | 220.7 | 213.51
2017-10-10 18:00 | 220.94 | 213.95
2017-10-10 18:30 | 220.76 | 214.26
2017-10-10 19:00 | 220.16 | 213.42
2017-10-10 19:30 | 222.44 | 215.19
2017-10-10 20:00 | 224.48 | 217.74
2017-10-10 20:30 | 225.45 | 219.07
2017-10-10 21:00 | 228.09 | 221.91
2017-10-10 21:30 | 229.25 | 223.44
2017-10-10 22:00 | 231.07 | 225.23
2017-10-10 22:30 | 232.92 | 227.33
2017-10-10 23:00 | 234.33 | 229
2017-10-10 23:30 | 224.6 | 213.21
2017-10-11 | 223.9 | 211.3
2017-10-11 00:30 | 222.49 | 210.17
2017-10-11 01:00 | 221.17 | 209.18
2017-10-11 01:30 | 220.95 | 208.46
2017-10-11 02:00 | 219.46 | 207.8
2017-10-11 02:30 | 219.13 | 207.49
2017-10-11 03:00 | 219.08 | 207.19
2017-10-11 03:30 | 218.75 | 206.78
2017-10-11 04:00 | 218.41 | 206.56
2017-10-11 04:30 | 218.84 | 206.92
2017-10-11 05:00 | 218.99 | 207.51
2017-10-11 05:30 | 220.32 | 209
2017-10-11 06:00 | 216.83 | 206.53
2017-10-11 06:30 | 230.34 | 224.54
2017-10-11 07:00 | 236.82 | 231.57
2017-10-11 07:30 | 236.26 | 230.71
2017-10-11 08:00 | 235.26 | 229.14
2017-10-11 08:30 | 234.13 | 228.29
2017-10-11 09:00 | 233.54 | 227.77
2017-10-11 09:30 | 232.6 | 226.93
2017-10-11 10:00 | 231.31 | 225.35
2017-10-11 10:30 | 230.59 | 224.47
2017-10-11 11:00 | 229.15 | 222.93
2017-10-11 11:30 | 227.52 | 220.74
2017-10-11 12:00 | 225.77 | 219.04
2017-10-11 12:30 | 223.5 | 216.55
2017-10-11 13:00 | 222.16 | 215.12
2017-10-11 13:30 | 221.23 | 213.9
2017-10-11 14:00 | 219.85 | 211.94
2017-10-11 14:30 | 219.16 | 210.99
2017-10-11 15:00 | 219.16 | 210.9
2017-10-11 15:30 | 218.06 | 209.4
2017-10-11 16:00 | 217.12 | 208.6
2017-10-11 16:30 | 219.9 | 211.51
2017-10-11 17:00 | 220.83 | 212.35
2017-10-11 17:30 | 222.54 | 213.96
2017-10-11 18:00 | 222.07 | 213.41
2017-10-11 18:30 | 222.34 | 213.93
2017-10-11 19:00 | 222.74 | 214.19
2017-10-11 19:30 | 224.18 | 215.78
2017-10-11 20:00 | 226.59 | 218.68
2017-10-11 20:30 | 228.41 | 221.07
2017-10-11 21:00 | 230.39 | 223.23
2017-10-11 21:30 | 232.17 | 225.29
2017-10-11 22:00 | 232.75 | 225.63
2017-10-11 22:30 | 228.81 | 215.39
2017-10-11 23:00 | 228.55 | 214.35
2017-10-11 23:30 | 224.5 | 213.79
2017-10-12 | 222.63 | 212.33
2017-10-12 00:30 | 222.3 | 211.33
2017-10-12 01:00 | 220.23 | 210.68
2017-10-12 01:30 | 219.51 | 210.33
2017-10-12 02:00 | 218.85 | 210.18
2017-10-12 02:30 | 218.29 | 209.78
2017-10-12 03:00 | 218.05 | 209.47
2017-10-12 03:30 | 218.14 | 209.41
2017-10-12 04:00 | 217.91 | 209.09
2017-10-12 04:30 | 218 | 209.31
2017-10-12 05:00 | 218.53 | 210.4
2017-10-12 05:30 | 215.8 | 208.38
2017-10-12 06:00 | 235.6 | 231.6
2017-10-12 06:30 | 236.2 | 231.78
2017-10-12 07:00 | 235.3 | 230.59
2017-10-12 07:30 | 234.66 | 229.73
2017-10-12 08:00 | 234.04 | 229.26
2017-10-12 08:30 | 234.02 | 229.34
2017-10-12 09:00 | 234.92 | 229.91
2017-10-12 09:30 | 234.48 | 229.56
2017-10-12 10:00 | 234.19 | 228.88
2017-10-12 10:30 | 234.06 | 228.67
2017-10-12 11:00 | 233.65 | 228.26
2017-10-12 11:30 | 233.23 | 227.69
2017-10-12 12:00 | 232.96 | 227.5
2017-10-12 12:30 | 232.58 | 227.17
2017-10-12 13:00 | 232.24 | 226.7
2017-10-12 13:30 | 231.12 | 225.91
2017-10-12 14:00 | 229.94 | 224.76
2017-10-12 14:30 | 230.51 | 225.33
2017-10-12 15:00 | 232.28 | 226.89
2017-10-12 15:30 | 232.29 | 226.97
2017-10-12 16:00 | 231.64 | 226.47
2017-10-12 16:30 | 231.49 | 226.2
2017-10-12 17:00 | 230.77 | 225.4
2017-10-12 17:30 | 232.51 | 227.17
2017-10-12 18:00 | 232.64 | 227.25
2017-10-12 18:30 | 232.13 | 226.86
2017-10-12 19:00 | 231.12 | 225.74
2017-10-12 19:30 | 232.09 | 226.53
2017-10-12 20:00 | 233.5 | 228.33
2017-10-12 20:30 | 234.87 | 229.72
2017-10-12 21:00 | 236.3 | 231.28
2017-10-12 21:30 | 231.21 | 220.7
2017-10-12 22:00 | 231.81 | 220.05
2017-10-12 22:30 | 229.94 | 218
2017-10-12 23:00 | 228.29 | 216.55
2017-10-12 23:30 | 227.46 | 215.74
2017-10-13 | 226.11 | 214.42
2017-10-13 00:30 | 223.86 | 213.03
2017-10-13 01:00 | 222.76 | 212.28
2017-10-13 01:30 | 222.31 | 211.51
2017-10-13 02:00 | 222.45 | 211.49
2017-10-13 02:30 | 221.84 | 210.74
2017-10-13 03:00 | 222.04 | 210.91
2017-10-13 03:30 | 221.91 | 210.55
2017-10-13 04:00 | 221.26 | 209.86
2017-10-13 04:30 | 221.61 | 210.18
2017-10-13 05:00 | 222.93 | 211.26
2017-10-13 05:30 | 223.44 | 212.46
2017-10-13 06:00 | 223.19 | 214.4
2017-10-13 06:30 | 243.4 | 239.29
2017-10-13 07:00 | 241.78 | 237.5
2017-10-13 07:30 | 241.29 | 236.84
2017-10-13 08:00 | 241.32 | 236.79
2017-10-13 08:30 | 241.33 | 237.01
2017-10-13 09:00 | 241.63 | 237.03
2017-10-13 09:30 | 241.32 | 236.39
2017-10-13 10:00 | 239.88 | 234.93
2017-10-13 10:30 | 238.62 | 234.06
2017-10-13 11:00 | 237.79 | 233.35
2017-10-13 11:30 | 237.39 | 232.91
2017-10-13 12:00 | 236.27 | 231.77
2017-10-13 12:30 | 235.83 | 231.18
2017-10-13 13:00 | 236.37 | 231.13
2017-10-13 13:30 | 235.56 | 230.17
2017-10-13 14:00 | 235.49 | 230.16
2017-10-13 14:30 | 235.03 | 229.55
2017-10-13 15:00 | 234.67 | 229.1
2017-10-13 15:30 | 234.42 | 228.89
2017-10-13 16:00 | 233.85 | 227.76
2017-10-13 16:30 | 237.17 | 231.49
2017-10-13 17:00 | 238.32 | 232.71
2017-10-13 17:30 | 238.74 | 232.52
2017-10-13 18:00 | 237.07 | 230.2
2017-10-13 18:30 | 237.97 | 231.3
2017-10-13 19:00 | 237.91 | 231.17
2017-10-13 19:30 | 238.07 | 231.35
2017-10-13 20:00 | 239.65 | 233.16
2017-10-13 20:30 | 240.6 | 234.13
2017-10-13 21:00 | 241.4 | 235.07
2017-10-13 21:30 | 239.21 | 234.18
2017-10-13 22:00 | 239.42 | 234.6
2017-10-13 22:30 | 240.72 | 236.34
2017-10-13 23:00 | 242.5 | 238.44
2017-10-13 23:30 | 243.37 | 239.05
2017-10-14 | 244.03 | 239.69
2017-10-14 00:30 | 244.17 | 240.21
2017-10-14 01:00 | 244.65 | 240.77
2017-10-14 01:30 | 221.98 | 212.91
2017-10-14 02:00 | 220.4 | 210.07
2017-10-14 02:30 | 220.13 | 209.42
2017-10-14 03:00 | 220.26 | 209.29
2017-10-14 03:30 | 220.3 | 209.21
2017-10-14 04:00 | 219.95 | 208.8
2017-10-14 04:30 | 220.68 | 209.3
2017-10-14 05:00 | 221.32 | 209.41
2017-10-14 05:30 | 221.8 | 209.91
2017-10-14 06:00 | 221.88 | 210.01
2017-10-14 06:30 | 222.63 | 210.98
2017-10-14 07:00 | 223.4 | 211.84
2017-10-14 07:30 | 222.33 | 211.07
2017-10-14 08:00 | 220.5 | 208.49
2017-10-14 08:30 | 220.5 | 207.89
2017-10-14 09:00 | 222.06 | 208.05
2017-10-14 09:30 | 221.64 | 207.55
2017-10-14 10:00 | 221.32 | 207.28
2017-10-14 10:30 | 209.24 | 195.66
2017-10-14 11:00 | 213.73 | 200.27
2017-10-14 11:30 | 220.5 | 206.69
2017-10-14 12:00 | 221.19 | 207.33
2017-10-14 12:30 | 222.35 | 208.48
2017-10-14 13:00 | 223.35 | 209.63
2017-10-14 13:30 | 223.43 | 209.82
2017-10-14 14:00 | 223.73 | 210.3
2017-10-14 14:30 | 223.62 | 210.33
2017-10-14 15:00 | 224.09 | 210.95
2017-10-14 15:30 | 225.06 | 212.12
2017-10-14 16:00 | 226.8 | 213.94
2017-10-14 16:30 | 228.63 | 214.97
2017-10-14 17:00 | 229.05 | 215.69
2017-10-14 17:30 | 215.61 | 203.18
2017-10-14 18:00 | 208.33 | 196.37
2017-10-14 18:30 | 208.96 | 196.68
2017-10-14 19:00 | 209.75 | 197
2017-10-14 19:30 | 210.48 | 197.64
2017-10-14 20:00 | 211.58 | 198.96
2017-10-14 20:30 | 227.94 | 214.06
2017-10-14 21:00 | 229.21 | 215.58
2017-10-14 21:30 | 228.32 | 215.33
2017-10-14 22:00 | 226.9 | 214.47
2017-10-14 22:30 | 224.94 | 212.77
2017-10-14 23:00 | 223.95 | 211.79
2017-10-14 23:30 | 223.1 | 210.95
2017-10-15 | 222.2 | 209.98
2017-10-15 00:30 | 221.31 | 209.42
2017-10-15 01:00 | 220.86 | 208.8
2017-10-15 01:30 | 220.5 | 208.3
2017-10-15 02:00 | 220.25 | 207.92
2017-10-15 02:30 | 219.5 | 207.28
2017-10-15 03:00 | 219.47 | 207.2
2017-10-15 03:30 | 218.91 | 207.11
2017-10-15 04:00 | 218.84 | 207.02
2017-10-15 04:30 | 218.84 | 207.07
2017-10-15 05:00 | 218.78 | 207.44
2017-10-15 05:30 | 219.21 | 208.03
2017-10-15 06:00 | 220.82 | 208.76
2017-10-15 06:30 | 221.2 | 209.17
2017-10-15 07:00 | 220.91 | 209.48
2017-10-15 07:30 | 221.26 | 210.3
2017-10-15 08:00 | 221.03 | 210.65
2017-10-15 08:30 | 221.57 | 210.53
2017-10-15 09:00 | 221.5 | 210.08
2017-10-15 09:30 | 221.91 | 210.45
2017-10-15 10:00 | 221.89 | 210.4
2017-10-15 10:30 | 222.01 | 209.78
2017-10-15 11:00 | 221.73 | 209.31
2017-10-15 11:30 | 221.91 | 209.45
2017-10-15 12:00 | 222.79 | 210.17
2017-10-15 12:30 | 223.32 | 210.74
2017-10-15 13:00 | 223.84 | 211.22
2017-10-15 13:30 | 223.29 | 210.52
2017-10-15 14:00 | 222.78 | 209.93
2017-10-15 14:30 | 223.07 | 210.33
2017-10-15 15:00 | 223.96 | 211.09
2017-10-15 15:30 | 224.28 | 211.31
2017-10-15 16:00 | 225.6 | 212.72
2017-10-15 16:30 | 226.75 | 213.99
2017-10-15 17:00 | 227.45 | 214.6
2017-10-15 17:30 | 229.04 | 215.8
2017-10-15 18:00 | 230.94 | 217.72
2017-10-15 18:30 | 232.36 | 219.31
2017-10-15 19:00 | 233.54 | 220.52
2017-10-15 19:30 | 233.06 | 219.77
2017-10-15 20:00 | 231.4 | 217.94
2017-10-15 20:30 | 230.14 | 216.94
2017-10-15 21:00 | 228.61 | 215.73
2017-10-15 21:30 | 228.42 | 215.12
2017-10-15 22:00 | 227.41 | 213.92
2017-10-15 22:30 | 225.96 | 211.9
2017-10-15 23:00 | 224.73 | 210.29
2017-10-15 23:30 | 223.28 | 209.59
2017-10-16 | 222.53 | 209.09
2017-10-16 00:30 | 222.52 | 209.07
2017-10-16 01:00 | 221.68 | 207.95
2017-10-16 01:30 | 221.17 | 207.56
2017-10-16 02:00 | 220.22 | 206.77
2017-10-16 02:30 | 220.12 | 206.43
2017-10-16 03:00 | 220.07 | 206.14
2017-10-16 03:30 | 219.63 | 205.81
2017-10-16 04:00 | 219.66 | 205.91
2017-10-16 04:30 | 219.94 | 206.29
2017-10-16 05:00 | 220.63 | 207.13
2017-10-16 05:30 | 222.07 | 208.68
2017-10-16 06:00 | 224.31 | 210.45
2017-10-16 06:30 | 226.8 | 212.35
2017-10-16 07:00 | 229.89 | 213.88
2017-10-16 07:30 | 230.76 | 215.08
2017-10-16 08:00 | 230.33 | 214.91
2017-10-16 08:30 | 229.62 | 214.71
2017-10-16 09:00 | 229.32 | 214.94
2017-10-16 09:30 | 229.4 | 214.77
2017-10-16 10:00 | 229.76 | 215.25
2017-10-16 10:30 | 229.1 | 214.54
2017-10-16 11:00 | 229.22 | 214.73
2017-10-16 11:30 | 229.12 | 214.86
2017-10-16 12:00 | 229.65 | 215.08
2017-10-16 12:30 | 228.69 | 214.08
2017-10-16 13:00 | 229.31 | 214.87
2017-10-16 13:30 | 229.05 | 214.81
2017-10-16 14:00 | 228.73 | 214.29
2017-10-16 14:30 | 229.09 | 214.67
2017-10-16 15:00 | 229.08 | 214.48
2017-10-16 15:30 | 229.12 | 214.74
2017-10-16 16:00 | 229.04 | 214.69
2017-10-16 16:30 | 229.51 | 214.95
2017-10-16 17:00 | 230.66 | 216.04
2017-10-16 17:30 | 232.67 | 218.38
2017-10-16 18:00 | 235.1 | 220.67
2017-10-16 18:30 | 237.47 | 222.42
2017-10-16 19:00 | 239.39 | 224.53
2017-10-16 19:30 | 238.58 | 223.37
2017-10-16 20:00 | 236.94 | 221.7
2017-10-16 20:30 | 235.41 | 220.18
2017-10-16 21:00 | 233.41 | 218.58
2017-10-16 21:30 | 231.95 | 217.92
2017-10-16 22:00 | 230.76 | 216.47
2017-10-16 22:30 | 229.72 | 215.11
2017-10-16 23:00 | 227.61 | 213.27
2017-10-16 23:30 | 226.41 | 212.32
2017-10-17 | 225.44 | 211.37
2017-10-17 00:30 | 224.73 | 210.79
2017-10-17 01:00 | 223.66 | 209.97
2017-10-17 01:30 | 223.03 | 209.67
2017-10-17 02:00 | 223.19 | 209.59
2017-10-17 02:30 | 222.73 | 209.05
2017-10-17 03:00 | 222.27 | 208.84
2017-10-17 03:30 | 222 | 208.69
2017-10-17 04:00 | 221.93 | 208.75
2017-10-17 04:30 | 222.58 | 209.14
2017-10-17 05:00 | 223.34 | 210.03
2017-10-17 05:30 | 224.52 | 211.51
2017-10-17 06:00 | 226.4 | 213.59
2017-10-17 06:30 | 228.29 | 215.45
2017-10-17 07:00 | 231.05 | 217.44
2017-10-17 07:30 | 232.34 | 218.62
2017-10-17 08:00 | 232.98 | 219.43
2017-10-17 08:30 | 232.03 | 218.47
2017-10-17 09:00 | 231.45 | 217.54
2017-10-17 09:30 | 233.23 | 218.38
2017-10-17 10:00 | 237.79 | 223.26
2017-10-17 10:30 | 236.23 | 221.45
2017-10-17 11:00 | 236.61 | 222.04
2017-10-17 11:30 | 236.99 | 222.46
2017-10-17 12:00 | 241.83 | 227.41
2017-10-17 12:30 | 242.49 | 228.06
2017-10-17 13:00 | 236.53 | 222.14
2017-10-17 13:30 | 236.82 | 222.14
2017-10-17 14:00 | 236.05 | 220.99
2017-10-17 14:30 | 234.09 | 218.87
2017-10-17 15:00 | 227.9 | 212.35
2017-10-17 15:30 | 227.93 | 212.63
2017-10-17 16:00 | 229.03 | 214.17
2017-10-17 16:30 | 229.64 | 215.01
2017-10-17 17:00 | 230.6 | 216.14
2017-10-17 17:30 | 231.76 | 217.46
2017-10-17 18:00 | 234.33 | 220.43
2017-10-17 18:30 | 236.95 | 222.78
2017-10-17 19:00 | 238.99 | 224.81
2017-10-17 19:30 | 238.16 | 223.6
2017-10-17 20:00 | 236.51 | 221.8
2017-10-17 20:30 | 235.81 | 220.72
2017-10-17 21:00 | 234.46 | 218.77
2017-10-17 21:30 | 233.38 | 217.96
2017-10-17 22:00 | 231.07 | 216.18
2017-10-17 22:30 | 229.42 | 214.48
2017-10-17 23:00 | 227.83 | 212.71
2017-10-17 23:30 | 226.81 | 211.72
2017-10-18 | 224.78 | 210.64
2017-10-18 00:30 | 221.97 | 210.3
2017-10-18 01:00 | 221.19 | 209.52
2017-10-18 01:30 | 221 | 209.05
2017-10-18 02:00 | 220.69 | 208.79
2017-10-18 02:30 | 220.92 | 208.53
2017-10-18 03:00 | 220.62 | 208.17
2017-10-18 03:30 | 220.77 | 208.31
2017-10-18 04:00 | 220.69 | 208.3
2017-10-18 04:30 | 220.77 | 208.37
2017-10-18 05:00 | 221.6 | 209.54
2017-10-18 05:30 | 222.11 | 209.99
2017-10-18 06:00 | 223.96 | 211.33
2017-10-18 06:30 | 226.15 | 213.83
2017-10-18 07:00 | 228.7 | 215.38
2017-10-18 07:30 | 231.22 | 216.66
2017-10-18 08:00 | 231.04 | 216.2
2017-10-18 08:30 | 230.47 | 215.01
2017-10-18 09:00 | 229.32 | 214
2017-10-18 09:30 | 228.26 | 213.02
2017-10-18 10:00 | 227.22 | 212.11
2017-10-18 10:30 | 226.16 | 211.29
2017-10-18 11:00 | 226.36 | 211.5
2017-10-18 11:30 | 227.12 | 211.69
2017-10-18 12:00 | 227.26 | 211.36
2017-10-18 12:30 | 227.3 | 211.09
2017-10-18 13:00 | 227.54 | 211.43
2017-10-18 13:30 | 227.89 | 212.29
2017-10-18 14:00 | 228.48 | 212.57
2017-10-18 14:30 | 228.67 | 213.09
2017-10-18 15:00 | 228.12 | 212.62
2017-10-18 15:30 | 228.31 | 212.93
2017-10-18 16:00 | 229.07 | 213.37
2017-10-18 16:30 | 230.09 | 213.99
2017-10-18 17:00 | 231.07 | 214.86
2017-10-18 17:30 | 231.89 | 215.55
2017-10-18 18:00 | 233.64 | 217.6
2017-10-18 18:30 | 235 | 219.48
2017-10-18 19:00 | 237.07 | 221.99
2017-10-18 19:30 | 236.91 | 221.66
2017-10-18 20:00 | 236.07 | 220.49
2017-10-18 20:30 | 234.79 | 218.5
2017-10-18 21:00 | 233.08 | 216.65
2017-10-18 21:30 | 232.9 | 216.43
2017-10-18 22:00 | 231.22 | 215.07
2017-10-18 22:30 | 230.58 | 213.92
2017-10-18 23:00 | 227.9 | 212.07
2017-10-18 23:30 | 226.81 | 211.45
2017-10-19 | 225.7 | 210.59
2017-10-19 00:30 | 224.77 | 210.01
2017-10-19 01:00 | 222.83 | 209.34
2017-10-19 01:30 | 221.9 | 208.99
2017-10-19 02:00 | 221.56 | 208.63
2017-10-19 02:30 | 221.22 | 208.3
2017-10-19 03:00 | 221.25 | 208.11
2017-10-19 03:30 | 221.2 | 208.02
2017-10-19 04:00 | 221.27 | 208.11
2017-10-19 04:30 | 221.55 | 208.42
2017-10-19 05:00 | 222.41 | 209.6
2017-10-19 05:30 | 223.52 | 210.71
2017-10-19 06:00 | 225.11 | 212.3
2017-10-19 06:30 | 227.67 | 214.88
2017-10-19 07:00 | 229.27 | 216.69
2017-10-19 07:30 | 231.56 | 218.12
2017-10-19 08:00 | 231.18 | 217.87
2017-10-19 08:30 | 230.08 | 216.86
2017-10-19 09:00 | 228.11 | 215.01
2017-10-19 09:30 | 227.44 | 213.89
2017-10-19 10:00 | 226.98 | 214.29
2017-10-19 10:30 | 226.84 | 213.88
2017-10-19 11:00 | 226.49 | 213.45
2017-10-19 11:30 | 225.84 | 213.06
2017-10-19 12:00 | 225.86 | 213.43
2017-10-19 12:30 | 227 | 213.85
2017-10-19 13:00 | 226.84 | 214.33
2017-10-19 13:30 | 227.33 | 214.45
2017-10-19 14:00 | 227.6 | 214.81
2017-10-19 14:30 | 228.33 | 216.01
2017-10-19 15:00 | 228.58 | 215.82
2017-10-19 15:30 | 228.64 | 215.71
2017-10-19 16:00 | 229.3 | 216.41
2017-10-19 16:30 | 230.09 | 216.79
2017-10-19 17:00 | 231.03 | 217.73
2017-10-19 17:30 | 232.01 | 218.32
2017-10-19 18:00 | 233.32 | 219.86
2017-10-19 18:30 | 234.97 | 221.6
2017-10-19 19:00 | 237.63 | 224.44
2017-10-19 19:30 | 237.45 | 224.32
2017-10-19 20:00 | 236.13 | 222.7
2017-10-19 20:30 | 235.77 | 221.69
2017-10-19 21:00 | 234.83 | 220.42
2017-10-19 21:30 | 233.3 | 219.74
2017-10-19 22:00 | 231.58 | 218.21
2017-10-19 22:30 | 229.81 | 216.09
2017-10-19 23:00 | 228.69 | 214.6
2017-10-19 23:30 | 227.38 | 213.98
2017-10-20 | 226.49 | 213.25
2017-10-20 00:30 | 225.71 | 212.59
2017-10-20 01:00 | 224.16 | 211.43
2017-10-20 01:30 | 223.57 | 211.18
2017-10-20 02:00 | 223.11 | 210.96
2017-10-20 02:30 | 222.93 | 210.78
2017-10-20 03:00 | 223.88 | 211.45
2017-10-20 03:30 | 223.59 | 211.17
2017-10-20 04:00 | 222.76 | 210.67
2017-10-20 04:30 | 222.89 | 210.48
2017-10-20 05:00 | 223.82 | 211.17
2017-10-20 05:30 | 224.48 | 211.75
2017-10-20 06:00 | 226.11 | 212.53
2017-10-20 06:30 | 227.85 | 214.84
2017-10-20 07:00 | 228.6 | 215.94
2017-10-20 07:30 | 231.53 | 218.26
2017-10-20 08:00 | 232.84 | 217.98
2017-10-20 08:30 | 234.28 | 219.15
2017-10-20 09:00 | 234.24 | 218.93
2017-10-20 09:30 | 233.46 | 217.67
2017-10-20 10:00 | 232.78 | 217
2017-10-20 10:30 | 232.5 | 216.75
2017-10-20 11:00 | 230.26 | 216.74
2017-10-20 11:30 | 230.06 | 217.13
2017-10-20 12:00 | 229.22 | 216.29
2017-10-20 12:30 | 228.91 | 216.02
2017-10-20 13:00 | 228.54 | 215.51
2017-10-20 13:30 | 228.75 | 215.85
2017-10-20 14:00 | 229.07 | 215.93
2017-10-20 14:30 | 229.5 | 216.37
2017-10-20 15:00 | 230.42 | 216.23
2017-10-20 15:30 | 230.95 | 216.4
2017-10-20 16:00 | 231.15 | 216.73
2017-10-20 16:30 | 231.12 | 216.75
2017-10-20 17:00 | 232.23 | 217.12
2017-10-20 17:30 | 232.51 | 217.62
2017-10-20 18:00 | 232.82 | 218.7
2017-10-20 18:30 | 233.21 | 219.82
2017-10-20 19:00 | 233.67 | 220.53
2017-10-20 19:30 | 233.58 | 220.16
2017-10-20 20:00 | 232.07 | 218.66
2017-10-20 20:30 | 231.56 | 218.08
2017-10-20 21:00 | 230.25 | 216.76
2017-10-20 21:30 | 228.31 | 216.22
2017-10-20 22:00 | 227.39 | 215.55
2017-10-20 22:30 | 225.3 | 213.24
2017-10-20 23:00 | 224.17 | 211.89
2017-10-20 23:30 | 223.28 | 211.36
2017-10-21 | 222.35 | 210.68
2017-10-21 00:30 | 221.7 | 210.29
2017-10-21 01:00 | 220.49 | 209.55
2017-10-21 01:30 | 219.98 | 209.26
2017-10-21 02:00 | 219.49 | 208.88
2017-10-21 02:30 | 220.51 | 208.81
2017-10-21 03:00 | 220.62 | 208.8
2017-10-21 03:30 | 220.38 | 208.8
2017-10-21 04:00 | 219.59 | 208.32
2017-10-21 04:30 | 218.92 | 207.91
2017-10-21 05:00 | 219.09 | 208.33
2017-10-21 05:30 | 219.7 | 208.77
2017-10-21 06:00 | 221.08 | 210.09
2017-10-21 06:30 | 221.97 | 211.11
2017-10-21 07:00 | 221.92 | 211.15
2017-10-21 07:30 | 222.21 | 211.43
2017-10-21 08:00 | 224.69 | 211.48
2017-10-21 08:30 | 225.53 | 211.69
2017-10-21 09:00 | 225.9 | 211.62
2017-10-21 09:30 | 225.72 | 211.25
2017-10-21 10:00 | 227.45 | 212.69
2017-10-21 10:30 | 228.58 | 214.04
2017-10-21 11:00 | 228.15 | 213.61
2017-10-21 11:30 | 227.52 | 213.02
2017-10-21 12:00 | 227.72 | 213.36
2017-10-21 12:30 | 228.48 | 214.48
2017-10-21 13:00 | 228.06 | 213.63
2017-10-21 13:30 | 228.35 | 213.86
2017-10-21 14:00 | 228.62 | 214.12
2017-10-21 14:30 | 229.71 | 215.56
2017-10-21 15:00 | 229.82 | 215.8
2017-10-21 15:30 | 229.44 | 214.99
2017-10-21 16:00 | 229.21 | 214.56
2017-10-21 16:30 | 230.11 | 215.21
2017-10-21 17:00 | 231.23 | 216.64
2017-10-21 17:30 | 230.99 | 216.21
2017-10-21 18:00 | 231.23 | 216.29
2017-10-21 18:30 | 200.72 | 185.42
2017-10-21 19:00 | 171.36 | 155.32
2017-10-21 19:30 | 171.57 | 155.62
2017-10-21 20:00 | 171.56 | 155.13
2017-10-21 20:30 | 171.21 | 154.25
2017-10-21 21:00 | 169.02 | 151.53
2017-10-21 21:30 | 168.45 | 151.24
2017-10-21 22:00 | 167.84 | 150.75
2017-10-21 22:30 | 166.92 | 149.48
2017-10-21 23:00 | 165.32 | 147.48
2017-10-21 23:30 | 163.93 | 145.97
2017-10-22 | 163.67 | 146.75
2017-10-22 00:30 | 163 | 146.72
2017-10-22 01:00 | 162.5 | 146.63
2017-10-22 01:30 | 161.42 | 146.05
2017-10-22 02:00 | 160.46 | 145.99
2017-10-22 02:30 | 160.19 | 145.74
2017-10-22 03:00 | 160.31 | 145.46
2017-10-22 03:30 | 160.77 | 146.46
2017-10-22 04:00 | 159.85 | 145.32
2017-10-22 04:30 | 159.87 | 145.95
2017-10-22 05:00 | 159.75 | 145.85
2017-10-22 05:30 | 160.07 | 146.24
2017-10-22 06:00 | 159.94 | 145.84
2017-10-22 06:30 | 160.36 | 146.41
2017-10-22 07:00 | 162.1 | 146.55
2017-10-22 07:30 | 162.52 | 147.39
2017-10-22 08:00 | 163.42 | 147.43
2017-10-22 08:30 | 165.8 | 149.87
2017-10-22 09:00 | 164.13 | 148.42
2017-10-22 09:30 | 164.32 | 148.16
2017-10-22 10:00 | 164.17 | 148.5
2017-10-22 10:30 | 164.43 | 148.88
2017-10-22 11:00 | 164.23 | 148.51
2017-10-22 11:30 | 163.73 | 147.73
2017-10-22 12:00 | 162.14 | 145.97
2017-10-22 12:30 | 161.98 | 145.81
2017-10-22 13:00 | 162.82 | 146.46
2017-10-22 13:30 | 163.68 | 147.04
2017-10-22 14:00 | 163.51 | 146.7
2017-10-22 14:30 | 163.81 | 146.92
2017-10-22 15:00 | 164.43 | 147.69
2017-10-22 15:30 | 165.68 | 148.34
2017-10-22 16:00 | 165.91 | 148.71
2017-10-22 16:30 | 167.73 | 150.29
2017-10-22 17:00 | 167.51 | 150.48
2017-10-22 17:30 | 166.53 | 149.34
2017-10-22 18:00 | 169.3 | 151.08
2017-10-22 18:30 | 170.67 | 153.11
2017-10-22 19:00 | 172.34 | 155.24
2017-10-22 19:30 | 171.6 | 154.42
2017-10-22 20:00 | 169.77 | 152.01
2017-10-22 20:30 | 170.02 | 152.47
2017-10-22 21:00 | 168.94 | 151.03
2017-10-22 21:30 | 168.31 | 149.97
2017-10-22 22:00 | 182.22 | 165.36
2017-10-22 22:30 | 211.12 | 195.34
2017-10-22 23:00 | 224.61 | 209.16
2017-10-22 23:30 | 224.84 | 209.6
2017-10-23 | 223.65 | 208.63
2017-10-23 00:30 | 223.01 | 208.32
2017-10-23 01:00 | 221.69 | 207.47
2017-10-23 01:30 | 221.42 | 207.27
2017-10-23 02:00 | 221.5 | 207.46
2017-10-23 02:30 | 221.73 | 207.62
2017-10-23 03:00 | 221.61 | 207.49
2017-10-23 03:30 | 221.05 | 207.03
2017-10-23 04:00 | 221.4 | 206.79
2017-10-23 04:30 | 221.54 | 207.36
2017-10-23 05:00 | 221.79 | 207.64
2017-10-23 05:30 | 221.39 | 206.87
2017-10-23 06:00 | 206.77 | 190.14
2017-10-23 06:30 | 206.77 | 190.84
2017-10-23 07:00 | 204.7 | 191.65
2017-10-23 07:30 | 205.62 | 192.59
2017-10-23 08:00 | 204.6 | 191.45
2017-10-23 08:30 | 203.89 | 190.68
2017-10-23 09:00 | 202.59 | 189.22
2017-10-23 09:30 | 200.98 | 187.7
2017-10-23 10:00 | 173.16 | 158.82
2017-10-23 10:30 | 160.54 | 145.69
2017-10-23 11:00 | 160.65 | 145.95
2017-10-23 11:30 | 160.58 | 145.91
2017-10-23 12:00 | 161.61 | 147.27
2017-10-23 12:30 | 160.92 | 146.71
2017-10-23 13:00 | 161.55 | 146.74
2017-10-23 13:30 | 162.48 | 147.82
2017-10-23 14:00 | 162.04 | 147.74
2017-10-23 14:30 | 162.44 | 148.09
2017-10-23 15:00 | 162.59 | 147.95
2017-10-23 15:30 | 163.4 | 148.92
2017-10-23 16:00 | 163.2 | 148.94
2017-10-23 16:30 | 163.79 | 149.45
2017-10-23 17:00 | 164.52 | 150.29
2017-10-23 17:30 | 164.52 | 150.43
2017-10-23 18:00 | 164.8 | 151.59
2017-10-23 18:30 | 165.95 | 153.39
2017-10-23 19:00 | 169.03 | 156.91
2017-10-23 19:30 | 168.61 | 156.48
2017-10-23 20:00 | 166.14 | 154.16
2017-10-23 20:30 | 165.28 | 153.4
2017-10-23 21:00 | 163.84 | 151.08
2017-10-23 21:30 | 162.02 | 149.94
2017-10-23 22:00 | 160.4 | 148.26
2017-10-23 22:30 | 158.97 | 145.06
2017-10-23 23:00 | 157.35 | 142.84
2017-10-23 23:30 | 156.47 | 142.48
2017-10-24 | 154.23 | 141.29
2017-10-24 00:30 | 152.74 | 140.31
2017-10-24 01:00 | 151.03 | 139.34
2017-10-24 01:30 | 153.83 | 138.99
2017-10-24 02:00 | 154 | 138.9
2017-10-24 02:30 | 152.11 | 138.13
2017-10-24 03:00 | 152.03 | 138.47
2017-10-24 03:30 | 151.96 | 138.38
2017-10-24 04:00 | 152.73 | 139.19
2017-10-24 04:30 | 152.63 | 139.13
2017-10-24 05:00 | 154.25 | 140.38
2017-10-24 05:30 | 156.52 | 142.69
2017-10-24 06:00 | 159.65 | 143.06
2017-10-24 06:30 | 160.79 | 144.95
2017-10-24 07:00 | 162.67 | 146.24
2017-10-24 07:30 | 162.49 | 147.22
2017-10-24 08:00 | 163.34 | 147.52
2017-10-24 08:30 | 162.68 | 146.79
2017-10-24 09:00 | 161.91 | 146.18
2017-10-24 09:30 | 160.84 | 145.27
2017-10-24 10:00 | 164.24 | 149.92
2017-10-24 10:30 | 164.1 | 149.8
2017-10-24 11:00 | 163.78 | 149.54
2017-10-24 11:30 | 164.84 | 150.62
2017-10-24 12:00 | 165.82 | 151.75
2017-10-24 12:30 | 165.99 | 151.95
2017-10-24 13:00 | 165.55 | 150.96
2017-10-24 13:30 | 165.14 | 150.46
2017-10-24 14:00 | 164.61 | 150.58
2017-10-24 14:30 | 168.43 | 155.57
2017-10-24 15:00 | 168.3 | 155.13
2017-10-24 15:30 | 166.72 | 153
2017-10-24 16:00 | 168.15 | 154.61
2017-10-24 16:30 | 169.16 | 154.56
2017-10-24 17:00 | 168.69 | 153.61
2017-10-24 17:30 | 169.12 | 154.08
2017-10-24 18:00 | 170.63 | 155.52
2017-10-24 18:30 | 171.65 | 156.68
2017-10-24 19:00 | 173.43 | 158.63
2017-10-24 19:30 | 172.74 | 158.15
2017-10-24 20:00 | 170.31 | 155.99
2017-10-24 20:30 | 169.21 | 154.94
2017-10-24 21:00 | 167.25 | 152.7
2017-10-24 21:30 | 164.58 | 151.37
2017-10-24 22:00 | 163.56 | 150.37
2017-10-24 22:30 | 162.02 | 147.68
2017-10-24 23:00 | 157.69 | 145.85
2017-10-24 23:30 | 156.27 | 145.34
2017-10-25 | 155.21 | 144.2
2017-10-25 00:30 | 157.05 | 143.52
2017-10-25 01:00 | 156.12 | 143.21
2017-10-25 01:30 | 154.62 | 141.72
2017-10-25 02:00 | 154.63 | 141.62
2017-10-25 02:30 | 154.87 | 141.51
2017-10-25 03:00 | 154.57 | 141.57
2017-10-25 03:30 | 154.49 | 141.55
2017-10-25 04:00 | 154.92 | 142.26
2017-10-25 04:30 | 155.99 | 143.37
2017-10-25 05:00 | 158.47 | 145.78
2017-10-25 05:30 | 160.11 | 146.84
2017-10-25 06:00 | 163 | 149.98
2017-10-25 06:30 | 164.58 | 151.72
2017-10-25 07:00 | 165.69 | 152.62
2017-10-25 07:30 | 167.33 | 154.3
2017-10-25 08:00 | 165.7 | 152.37
2017-10-25 08:30 | 163.68 | 150.1
2017-10-25 09:00 | 167.3 | 153.85
2017-10-25 09:30 | 212.41 | 200.18
2017-10-25 10:00 | 224.07 | 212.15
2017-10-25 10:30 | 224.33 | 212.42
2017-10-25 11:00 | 224.3 | 212.49
2017-10-25 11:30 | 224.64 | 212.95
2017-10-25 12:00 | 225.94 | 214.26
2017-10-25 12:30 | 226.23 | 214.65
2017-10-25 13:00 | 227.38 | 215.98
2017-10-25 13:30 | 228.31 | 217.06
2017-10-25 14:00 | 229.2 | 218.05
2017-10-25 14:30 | 230.42 | 219.39
2017-10-25 15:00 | 231.56 | 220.01
2017-10-25 15:30 | 232.99 | 221.3
2017-10-25 16:00 | 234.59 | 223.12
2017-10-25 16:30 | 235.83 | 223.84
2017-10-25 17:00 | 237.38 | 225.63
2017-10-25 17:30 | 238.02 | 226.03
2017-10-25 18:00 | 238.56 | 226.32
2017-10-25 18:30 | 239.21 | 226.96
2017-10-25 19:00 | 241.04 | 229.18
2017-10-25 19:30 | 241.12 | 229.15
2017-10-25 20:00 | 238.23 | 226.41
2017-10-25 20:30 | 235.62 | 224.06
2017-10-25 21:00 | 233.99 | 221.95
2017-10-25 21:30 | 232.1 | 220.34
2017-10-25 22:00 | 230.7 | 218.45
2017-10-25 22:30 | 229.37 | 216.19
2017-10-25 23:00 | 227.19 | 214.5
2017-10-25 23:30 | 225.83 | 213.84
2017-10-26 | 224.35 | 212.4
2017-10-26 00:30 | 223.15 | 211.54
2017-10-26 01:00 | 222.05 | 210.73
2017-10-26 01:30 | 220.94 | 209.82
2017-10-26 02:00 | 219.85 | 209.58
2017-10-26 02:30 | 219.78 | 209.39
2017-10-26 03:00 | 219.44 | 209.07
2017-10-26 03:30 | 219.36 | 208.98
2017-10-26 04:00 | 219.7 | 209.08
2017-10-26 04:30 | 220.09 | 209.68
2017-10-26 05:00 | 220.97 | 210.45
2017-10-26 05:30 | 222.13 | 212
2017-10-26 06:00 | 223.32 | 213.08
2017-10-26 06:30 | 225.49 | 214.66
2017-10-26 07:00 | 228.09 | 215.29
2017-10-26 07:30 | 228.55 | 216.23
2017-10-26 08:00 | 228.43 | 215.69
2017-10-26 08:30 | 228.56 | 215.71
2017-10-26 09:00 | 227.49 | 215.02
2017-10-26 09:30 | 226.91 | 214.08
2017-10-26 10:00 | 227.03 | 214.36
2017-10-26 10:30 | 212.21 | 198.7
2017-10-26 11:00 | 207.45 | 193.9
2017-10-26 11:30 | 208.55 | 194.71
2017-10-26 12:00 | 209.49 | 195.73
2017-10-26 12:30 | 209.9 | 196.3
2017-10-26 13:00 | 210.62 | 197.16
2017-10-26 13:30 | 212.53 | 198.85
2017-10-26 14:00 | 209.65 | 196.67
2017-10-26 14:30 | 214.47 | 201.4
2017-10-26 15:00 | 214.35 | 200.7
2017-10-26 15:30 | 215.03 | 201.63
2017-10-26 16:00 | 210.43 | 197.43
2017-10-26 16:30 | 233.17 | 219.91
2017-10-26 17:00 | 239.53 | 226.03
2017-10-26 17:30 | 239.4 | 225.51
2017-10-26 18:00 | 235.21 | 221.48
2017-10-26 18:30 | 241.32 | 226.98
2017-10-26 19:00 | 243.51 | 229.63
2017-10-26 19:30 | 243.23 | 229.2
2017-10-26 20:00 | 240.56 | 226.47
2017-10-26 20:30 | 238.57 | 224.22
2017-10-26 21:00 | 236.83 | 222.19
2017-10-26 21:30 | 234.02 | 220.9
2017-10-26 22:00 | 232.45 | 218.8
2017-10-26 22:30 | 216.36 | 201.19
2017-10-26 23:00 | 183.04 | 166.96
2017-10-26 23:30 | 170.35 | 153.38
2017-10-27 | 166.44 | 151.79
2017-10-27 00:30 | 164.14 | 151.21
2017-10-27 01:00 | 162.32 | 149.96
2017-10-27 01:30 | 162.55 | 149.43
2017-10-27 02:00 | 162.02 | 148.51
2017-10-27 02:30 | 161.28 | 147.83
2017-10-27 03:00 | 161.27 | 147.81
2017-10-27 03:30 | 161.26 | 147.81
2017-10-27 04:00 | 160.58 | 147.01
2017-10-27 04:30 | 160.94 | 147.47
2017-10-27 05:00 | 161.93 | 148.28
2017-10-27 05:30 | 162.4 | 149.35
2017-10-27 06:00 | 164.46 | 151.23
2017-10-27 06:30 | 166.45 | 152.56
2017-10-27 07:00 | 166.35 | 153.05
2017-10-27 07:30 | 168.2 | 154.33
2017-10-27 08:00 | 168.56 | 154.27
2017-10-27 08:30 | 167.66 | 153.35
2017-10-27 09:00 | 166.83 | 152.39
2017-10-27 09:30 | 166.15 | 151.6
2017-10-27 10:00 | 166.05 | 151.72
2017-10-27 10:30 | 166.96 | 152.8
2017-10-27 11:00 | 166.53 | 152.19
2017-10-27 11:30 | 167.24 | 153.26
2017-10-27 12:00 | 168.31 | 154.49
2017-10-27 12:30 | 168.52 | 154.53
2017-10-27 13:00 | 169.94 | 155.94
2017-10-27 13:30 | 170.24 | 156.35
2017-10-27 14:00 | 170.87 | 156.96
2017-10-27 14:30 | 172.4 | 158.61
2017-10-27 15:00 | 171.76 | 157.99
2017-10-27 15:30 | 172.14 | 158.4
2017-10-27 16:00 | 173.15 | 159.14
2017-10-27 16:30 | 175.71 | 161.33
2017-10-27 17:00 | 176.68 | 162.21
2017-10-27 17:30 | 176.78 | 161.66
2017-10-27 18:00 | 207.6 | 193.31
2017-10-27 18:30 | 234.58 | 220.94
2017-10-27 19:00 | 240.06 | 226.56
2017-10-27 19:30 | 240.41 | 226.58
2017-10-27 20:00 | 239.31 | 225.11
2017-10-27 20:30 | 238.06 | 223.49
2017-10-27 21:00 | 236.31 | 221.69
2017-10-27 21:30 | 235.2 | 221.64
2017-10-27 22:00 | 234.18 | 220.33
2017-10-27 22:30 | 233.09 | 218.65
2017-10-27 23:00 | 231.31 | 216.78
2017-10-27 23:30 | 230.07 | 215.89
2017-10-28 | 229.02 | 215.28
2017-10-28 00:30 | 228.27 | 214.09
2017-10-28 01:00 | 226.92 | 213.88
2017-10-28 01:30 | 226.28 | 213.36
2017-10-28 02:00 | 226.46 | 213.22
2017-10-28 02:30 | 226.02 | 212.6
2017-10-28 03:00 | 225.79 | 212.27
2017-10-28 03:30 | 226.16 | 212.6
2017-10-28 04:00 | 226.66 | 212.98
2017-10-28 04:30 | 224.43 | 211.07
2017-10-28 05:00 | 224.83 | 211.09
2017-10-28 05:30 | 224.66 | 211.41
2017-10-28 06:00 | 225.27 | 211.18
2017-10-28 06:30 | 224.65 | 210.35
2017-10-28 07:00 | 226.89 | 213.14
2017-10-28 07:30 | 226.92 | 213.56
2017-10-28 08:00 | 227.36 | 213.83
2017-10-28 08:30 | 227.94 | 213.69
2017-10-28 09:00 | 228.75 | 213.84
2017-10-28 09:30 | 228.57 | 213.71
2017-10-28 10:00 | 229.19 | 214.56
2017-10-28 10:30 | 229.89 | 215.2
2017-10-28 11:00 | 230.05 | 215.39
2017-10-28 11:30 | 230.7 | 216.12
2017-10-28 12:00 | 230.73 | 216.09
2017-10-28 12:30 | 230.39 | 215.29
2017-10-28 13:00 | 232.74 | 218.18
2017-10-28 13:30 | 233.91 | 219.57
2017-10-28 14:00 | 232.8 | 218.34
2017-10-28 14:30 | 232.29 | 217.85
2017-10-28 15:00 | 231.23 | 216.97
2017-10-28 15:30 | 232.96 | 218.81
2017-10-28 16:00 | 234.49 | 220.4
2017-10-28 16:30 | 234.47 | 220.65
2017-10-28 17:00 | 236.66 | 221.61
2017-10-28 17:30 | 237.74 | 222.75
2017-10-28 18:00 | 239.23 | 224.39
2017-10-28 18:30 | 239.91 | 225.29
2017-10-28 19:00 | 241.56 | 226.84
2017-10-28 19:30 | 241.6 | 226.92
2017-10-28 20:00 | 240.54 | 225.66
2017-10-28 20:30 | 239.51 | 224.52
2017-10-28 21:00 | 238.38 | 223.29
2017-10-28 21:30 | 237.53 | 222.84
2017-10-28 22:00 | 236.19 | 221.71
2017-10-28 22:30 | 235.13 | 220.2
2017-10-28 23:00 | 233.73 | 218.82
2017-10-28 23:30 | 232.28 | 217.97
2017-10-29 | 231.59 | 217.22
2017-10-29 00:30 | 230.67 | 216.4
2017-10-29 01:00 | 229.34 | 215.65
2017-10-29 01:30 | 228.97 | 215.19
2017-10-29 02:00 | 229.48 | 215.06
2017-10-29 02:30 | 228.57 | 214.08
2017-10-29 03:00 | 227.57 | 213.08
2017-10-29 03:30 | 226.45 | 212.37
2017-10-29 04:00 | 225.58 | 211.7
2017-10-29 04:30 | 225.71 | 211.15
2017-10-29 05:00 | 226.07 | 211.48
2017-10-29 05:30 | 226.04 | 212.1
2017-10-29 06:00 | 226.04 | 211.86
2017-10-29 06:30 | 225.53 | 211.26
2017-10-29 07:00 | 225.09 | 211.11
2017-10-29 07:30 | 226.35 | 212.66
2017-10-29 08:00 | 226.62 | 213.07
2017-10-29 08:30 | 226.26 | 212.91
2017-10-29 09:00 | 225.99 | 212.99
2017-10-29 09:30 | 225.95 | 213.03
2017-10-29 10:00 | 227.02 | 213.7
2017-10-29 10:30 | 227.18 | 214.01
2017-10-29 11:00 | 228.92 | 215.53
2017-10-29 11:30 | 230.27 | 217.3
2017-10-29 12:00 | 233.59 | 219.41
2017-10-29 12:30 | 235.55 | 220.49
2017-10-29 13:00 | 236.19 | 221.4
2017-10-29 13:30 | 236.87 | 222.57
2017-10-29 14:00 | 236.83 | 222.51
2017-10-29 14:30 | 225.77 | 211.08
2017-10-29 15:00 | 234.94 | 220.31
2017-10-29 15:30 | 242.7 | 228.14
2017-10-29 16:00 | 244.01 | 229.65
2017-10-29 16:30 | 244.9 | 230.25
2017-10-29 17:00 | 246.29 | 231.26
2017-10-29 17:30 | 247.27 | 232.55
2017-10-29 18:00 | 248.1 | 233.23
2017-10-29 18:30 | 248.42 | 233.64
2017-10-29 19:00 | 247.11 | 235.05
2017-10-29 19:30 | 246.96 | 234.38
2017-10-29 20:00 | 244.63 | 231.58
2017-10-29 20:30 | 242.7 | 229.12
2017-10-29 21:00 | 239.46 | 225.78
2017-10-29 21:30 | 235.34 | 224.29
2017-10-29 22:00 | 232.74 | 221.73
2017-10-29 22:30 | 230.92 | 219.51
2017-10-29 23:00 | 229.07 | 217.3
2017-10-29 23:30 | 227.94 | 216.26
2017-10-30 | 225.8 | 213.8
2017-10-30 00:30 | 223.32 | 210.51
2017-10-30 01:00 | 221.25 | 209.38
2017-10-30 01:30 | 219.91 | 208.75
2017-10-30 02:00 | 219.29 | 208.43
2017-10-30 02:30 | 219.08 | 208.1
2017-10-30 03:00 | 218.69 | 207.82
2017-10-30 03:30 | 218.64 | 207.79
2017-10-30 04:00 | 218.54 | 207.51
2017-10-30 04:30 | 221.1 | 207.64
2017-10-30 05:00 | 221.89 | 208.61
2017-10-30 05:30 | 223.02 | 209.97
2017-10-30 06:00 | 224.35 | 211.66
2017-10-30 06:30 | 228.07 | 213.41
2017-10-30 07:00 | 231.9 | 216.34
2017-10-30 07:30 | 233.04 | 218.21
2017-10-30 08:00 | 234.14 | 219.56
2017-10-30 08:30 | 233.29 | 219.04
2017-10-30 09:00 | 233.71 | 218.99
2017-10-30 09:30 | 235.03 | 219.78
2017-10-30 10:00 | 235.52 | 220.1
2017-10-30 10:30 | 235.5 | 220.05
2017-10-30 11:00 | 235.88 | 220.3
2017-10-30 11:30 | 235.85 | 220.7
2017-10-30 12:00 | 236.1 | 221.19
2017-10-30 12:30 | 237.01 | 221.86
2017-10-30 13:00 | 239.27 | 223.85
2017-10-30 13:30 | 239.85 | 224.45
2017-10-30 14:00 | 239.69 | 224.51
2017-10-30 14:30 | 239.88 | 224.54
2017-10-30 15:00 | 239.81 | 224.41
2017-10-30 15:30 | 239.66 | 223.97
2017-10-30 16:00 | 241.02 | 225.15
2017-10-30 16:30 | 242.51 | 226.42
2017-10-30 17:00 | 242.65 | 226.55
2017-10-30 17:30 | 244 | 228.85
2017-10-30 18:00 | 243.35 | 230.16
2017-10-30 18:30 | 243.99 | 231
2017-10-30 19:00 | 245.27 | 232.6
2017-10-30 19:30 | 245.14 | 232.1
2017-10-30 20:00 | 242.93 | 229.56
2017-10-30 20:30 | 241.56 | 227.93
2017-10-30 21:00 | 239.02 | 225.58
2017-10-30 21:30 | 235.44 | 224.27
2017-10-30 22:00 | 233.57 | 222.07
2017-10-30 22:30 | 231.62 | 219.2
2017-10-30 23:00 | 229.48 | 217.05
2017-10-30 23:30 | 228.25 | 215.9
2017-10-31 | 225.64 | 213.99
2017-10-31 00:30 | 224.13 | 212.98
2017-10-31 01:00 | 224.47 | 212.72
2017-10-31 01:30 | 227.94 | 214.79
2017-10-31 02:00 | 229.64 | 216.16
2017-10-31 02:30 | 230.8 | 216.91
2017-10-31 03:00 | 229.98 | 216.29
2017-10-31 03:30 | 229.99 | 216.51
2017-10-31 04:00 | 230.12 | 216.74
2017-10-31 04:30 | 229.93 | 216.65
2017-10-31 05:00 | 232.25 | 218.28
2017-10-31 05:30 | 233.1 | 219.53
2017-10-31 06:00 | 233.11 | 220.18
2017-10-31 06:30 | 232.86 | 219.09
2017-10-31 07:00 | 235 | 219.66
2017-10-31 07:30 | 235.02 | 220.01
2017-10-31 08:00 | 234.86 | 219.84
2017-10-31 08:30 | 235.38 | 220.12
2017-10-31 09:00 | 233.33 | 217.7
2017-10-31 09:30 | 233.85 | 217.82
2017-10-31 10:00 | 234.24 | 217.9
2017-10-31 10:30 | 232.51 | 216.07
2017-10-31 11:00 | 230.05 | 213.93
2017-10-31 11:30 | 230.33 | 214.2
2017-10-31 12:00 | 232.82 | 216.73
2017-10-31 12:30 | 236.9 | 220.78
2017-10-31 13:00 | 238.18 | 222.11
2017-10-31 13:30 | 239.58 | 223.54
2017-10-31 14:00 | 242.7 | 227.09
2017-10-31 14:30 | 243.91 | 228.57
2017-10-31 15:00 | 244.43 | 229.1
2017-10-31 15:30 | 245.76 | 230.86
2017-10-31 16:00 | 247.7 | 232.43
2017-10-31 16:30 | 251.13 | 234.52
2017-10-31 17:00 | 252.11 | 235.2
2017-10-31 17:30 | 248.75 | 231.96
2017-10-31 18:00 | 247.51 | 230.94
2017-10-31 18:30 | 248.62 | 232.12
2017-10-31 19:00 | 250.83 | 234.77
2017-10-31 19:30 | 251.32 | 235.17
2017-10-31 20:00 | 249.29 | 233.51
2017-10-31 20:30 | 246.36 | 232.78
2017-10-31 21:00 | 244.44 | 230.88
2017-10-31 21:30 | 242.21 | 230.67
2017-10-31 22:00 | 222.67 | 211.2
2017-10-31 22:30 | 184.3 | 171.26
2017-10-31 23:00 | 173.08 | 158.5
2017-10-31 23:30 | 171.33 | 157.42
2017-11-01 | 169.42 | 156.95
2017-11-01 00:30 | 167.97 | 155.65
2017-11-01 01:00 | 167.4 | 155.21
2017-11-01 01:30 | 166.36 | 154.52
2017-11-01 02:00 | 165.08 | 153.83
2017-11-01 02:30 | 165.06 | 153.75
2017-11-01 03:00 | 167.24 | 154.91
2017-11-01 03:30 | 167.22 | 154.98
2017-11-01 04:00 | 166.06 | 154.51
2017-11-01 04:30 | 167.06 | 155.23
2017-11-01 05:00 | 168.43 | 155.88
2017-11-01 05:30 | 169.71 | 157.16
2017-11-01 06:00 | 171.34 | 158.67
2017-11-01 06:30 | 172.69 | 160.32
2017-11-01 07:00 | 209.67 | 196.87
2017-11-01 07:30 | 238.17 | 225.23
2017-11-01 08:00 | 240.13 | 227.09
2017-11-01 08:30 | 239.83 | 226.79
2017-11-01 09:00 | 238.51 | 225.05
2017-11-01 09:30 | 237.24 | 223.41
2017-11-01 10:00 | 237.82 | 223.98
2017-11-01 10:30 | 237.44 | 223.8
2017-11-01 11:00 | 236.19 | 223.19
2017-11-01 11:30 | 236.33 | 223.51
2017-11-01 12:00 | 237.85 | 224.81
2017-11-01 12:30 | 238.21 | 224.67
2017-11-01 13:00 | 239.03 | 225.27
2017-11-01 13:30 | 238.85 | 225.03
2017-11-01 14:00 | 239.39 | 225.68
2017-11-01 14:30 | 239.59 | 226.15
2017-11-01 15:00 | 239.98 | 226.62
2017-11-01 15:30 | 240.67 | 227.37
2017-11-01 16:00 | 241.18 | 228.12
2017-11-01 16:30 | 241.99 | 228.73
2017-11-01 17:00 | 243.46 | 230.02
2017-11-01 17:30 | 244.95 | 231.48
2017-11-01 18:00 | 218.11 | 205.04
2017-11-01 18:30 | 189.48 | 174.96
2017-11-01 19:00 | 189.17 | 177.65
2017-11-01 19:30 | 198.93 | 189.19
2017-11-01 20:00 | 205.55 | 195.25
2017-11-01 20:30 | 225.85 | 215.85
2017-11-01 21:00 | 239.26 | 228.93
2017-11-01 21:30 | 244.52 | 233.35
2017-11-01 22:00 | 225.29 | 213.97
2017-11-01 22:30 | 185.29 | 172.26
2017-11-01 23:00 | 172.23 | 158.78
2017-11-01 23:30 | 171 | 157.7
2017-11-02 | 169.45 | 156.38
2017-11-02 00:30 | 168.95 | 155.94
2017-11-02 01:00 | 167.04 | 155.36
2017-11-02 01:30 | 166.03 | 154.51
2017-11-02 02:00 | 165.86 | 153.87
2017-11-02 02:30 | 166.42 | 154.6
2017-11-02 03:00 | 165.5 | 153.39
2017-11-02 03:30 | 164.71 | 152.1
2017-11-02 04:00 | 165.94 | 153.06
2017-11-02 04:30 | 166.7 | 153.36
2017-11-02 05:00 | 168.3 | 154.49
2017-11-02 05:30 | 168.87 | 155.79
2017-11-02 06:00 | 169.45 | 157.15
2017-11-02 06:30 | 170.55 | 158.75
2017-11-02 07:00 | 201.6 | 190.51
2017-11-02 07:30 | 227.83 | 216.77
2017-11-02 08:00 | 236.76 | 225.38
2017-11-02 08:30 | 236.33 | 224.69
2017-11-02 09:00 | 234.58 | 223.18
2017-11-02 09:30 | 233.89 | 222.4
2017-11-02 10:00 | 234.01 | 222.45
2017-11-02 10:30 | 234.03 | 222.5
2017-11-02 11:00 | 233.2 | 221.68
2017-11-02 11:30 | 233.79 | 222.4
2017-11-02 12:00 | 234.02 | 222.64
2017-11-02 12:30 | 233.75 | 222.25
2017-11-02 13:00 | 234.56 | 222.77
2017-11-02 13:30 | 235 | 223.3
2017-11-02 14:00 | 234.92 | 223.58
2017-11-02 14:30 | 238.19 | 227.4
2017-11-02 15:00 | 237.45 | 226.66
2017-11-02 15:30 | 238.59 | 227.83
2017-11-02 16:00 | 239.57 | 228.69
2017-11-02 16:30 | 240.96 | 229.68
2017-11-02 17:00 | 241.05 | 228.99
2017-11-02 17:30 | 241.19 | 228.79
2017-11-02 18:00 | 242.5 | 229.88
2017-11-02 18:30 | 243.6 | 231.19
2017-11-02 19:00 | 246.22 | 233.98
2017-11-02 19:30 | 246.5 | 234.14
2017-11-02 20:00 | 244.57 | 232.14
2017-11-02 20:30 | 243.85 | 231.19
2017-11-02 21:00 | 243.16 | 230.14
2017-11-02 21:30 | 224.22 | 212.75
2017-11-02 22:00 | 184.69 | 172.45
2017-11-02 22:30 | 172.71 | 159.53
2017-11-02 23:00 | 170.93 | 157.45
2017-11-02 23:30 | 170.39 | 156.41
2017-11-03 | 169.12 | 155.7
2017-11-03 00:30 | 167.86 | 154.76
2017-11-03 01:00 | 165.81 | 153.77
2017-11-03 01:30 | 165.66 | 153.79
2017-11-03 02:00 | 165.1 | 153.27
2017-11-03 02:30 | 164.61 | 152.85
2017-11-03 03:00 | 164.82 | 153.12
2017-11-03 03:30 | 163.4 | 151.38
2017-11-03 04:00 | 164.43 | 152.91
2017-11-03 04:30 | 164.53 | 152.74
2017-11-03 05:00 | 166.73 | 153.65
2017-11-03 05:30 | 167.65 | 154.74
2017-11-03 06:00 | 169.3 | 156.94
2017-11-03 06:30 | 169.87 | 157.57
2017-11-03 07:00 | 171.39 | 158.84
2017-11-03 07:30 | 171.15 | 159.05
2017-11-03 08:00 | 171.4 | 159.11
2017-11-03 08:30 | 170.32 | 157.83
2017-11-03 09:00 | 169.27 | 156.75
2017-11-03 09:30 | 169.08 | 156.43
2017-11-03 10:00 | 170.27 | 157.24
2017-11-03 10:30 | 169.3 | 156.57
2017-11-03 11:00 | 169.51 | 156.37
2017-11-03 11:30 | 170.47 | 156.97
2017-11-03 12:00 | 171.37 | 157.64
2017-11-03 12:30 | 171.83 | 157.56
2017-11-03 13:00 | 172.18 | 157.47
2017-11-03 13:30 | 173.13 | 158.02
2017-11-03 14:00 | 175 | 160.03
2017-11-03 14:30 | 175.91 | 161.11
2017-11-03 15:00 | 176 | 161.49
2017-11-03 15:30 | 176.78 | 162.63
2017-11-03 16:00 | 177.84 | 164.27
2017-11-03 16:30 | 178.53 | 165.11
2017-11-03 17:00 | 179.85 | 166.15
2017-11-03 17:30 | 180.81 | 166.52
2017-11-03 18:00 | 180.61 | 166.25
2017-11-03 18:30 | 181.18 | 166.87
2017-11-03 19:00 | 181.14 | 166.85
2017-11-03 19:30 | 180.95 | 166.43
2017-11-03 20:00 | 179.07 | 164.27
2017-11-03 20:30 | 177.71 | 162.9
2017-11-03 21:00 | 176.66 | 162.35
2017-11-03 21:30 | 175.79 | 162.33
2017-11-03 22:00 | 173.87 | 160.34
2017-11-03 22:30 | 172.55 | 158.36
2017-11-03 23:00 | 171.02 | 156.5
2017-11-03 23:30 | 170.54 | 155.82
2017-11-04 | 168.76 | 154.62
2017-11-04 00:30 | 166.54 | 153.44
2017-11-04 01:00 | 166.02 | 153.14
2017-11-04 01:30 | 165.12 | 152.1
2017-11-04 02:00 | 164.79 | 151.5
2017-11-04 02:30 | 164.93 | 151.55
2017-11-04 03:00 | 164.64 | 151.35
2017-11-04 03:30 | 164.51 | 151.42
2017-11-04 04:00 | 164.03 | 151.11
2017-11-04 04:30 | 164.6 | 151.57
2017-11-04 05:00 | 163.96 | 151.03
2017-11-04 05:30 | 164.94 | 152.04
2017-11-04 06:00 | 165.46 | 152.45
2017-11-04 06:30 | 165.96 | 153.02
2017-11-04 07:00 | 167.42 | 153.39
2017-11-04 07:30 | 168.73 | 154.6
2017-11-04 08:00 | 169.21 | 154.65
2017-11-04 08:30 | 169.98 | 155.63
2017-11-04 09:00 | 170.36 | 155.79
2017-11-04 09:30 | 170.93 | 156.52
2017-11-04 10:00 | 171.83 | 157.22
2017-11-04 10:30 | 172.54 | 157.24
2017-11-04 11:00 | 173.84 | 158.38
2017-11-04 11:30 | 176.21 | 160.35
2017-11-04 12:00 | 177.37 | 161.38
2017-11-04 12:30 | 180.63 | 165.27
2017-11-04 13:00 | 183.54 | 168.02
2017-11-04 13:30 | 184.81 | 169.34
2017-11-04 14:00 | 185.92 | 170.42
2017-11-04 14:30 | 186.24 | 170.67
2017-11-04 15:00 | 186.39 | 170.9
2017-11-04 15:30 | 187.41 | 172.09
2017-11-04 16:00 | 187.6 | 172.6
2017-11-04 16:30 | 189.94 | 175.3
2017-11-04 17:00 | 193.1 | 178.88
2017-11-04 17:30 | 195.97 | 181.75
2017-11-04 18:00 | 190.1 | 176.01
2017-11-04 18:30 | 187.76 | 173.78
2017-11-04 19:00 | 187.15 | 173.47
2017-11-04 19:30 | 186.2 | 172.36
2017-11-04 20:00 | 184.78 | 170.53
2017-11-04 20:30 | 182.91 | 168.13
2017-11-04 21:00 | 181.35 | 166.1
2017-11-04 21:30 | 179.57 | 164.76
2017-11-04 22:00 | 177.36 | 163.06
2017-11-04 22:30 | 177.27 | 162.53
2017-11-04 23:00 | 174.95 | 159.74
2017-11-04 23:30 | 174.06 | 159.3
2017-11-05 | 172.32 | 158.26
2017-11-05 00:30 | 170.8 | 157.78
2017-11-05 01:00 | 169.14 | 156.63
2017-11-05 01:30 | 168.26 | 155.74
2017-11-05 02:00 | 167.08 | 155.16
2017-11-05 02:30 | 166.27 | 154.68
2017-11-05 03:00 | 165.81 | 154.36
2017-11-05 03:30 | 165.45 | 154
2017-11-05 04:00 | 165.05 | 153.83
2017-11-05 04:30 | 164.86 | 153.63
2017-11-05 05:00 | 164.92 | 153.66
2017-11-05 05:30 | 167.43 | 153.85
2017-11-05 06:00 | 168.39 | 154.63
2017-11-05 06:30 | 168.59 | 154.66
2017-11-05 07:00 | 169.72 | 155.59
2017-11-05 07:30 | 171.34 | 157.49
2017-11-05 08:00 | 176.42 | 161.99
2017-11-05 08:30 | 176.88 | 162.48
2017-11-05 09:00 | 178.52 | 162.88
2017-11-05 09:30 | 179.12 | 163.32
2017-11-05 10:00 | 179.24 | 163.54
2017-11-05 10:30 | 180.19 | 164.39
2017-11-05 11:00 | 185.23 | 169.39
2017-11-05 11:30 | 187.23 | 171.53
2017-11-05 12:00 | 188.79 | 173.2
2017-11-05 12:30 | 185.73 | 170.64
2017-11-05 13:00 | 183.18 | 168.54
2017-11-05 13:30 | 183.98 | 169.53
2017-11-05 14:00 | 184.99 | 170.84
2017-11-05 14:30 | 186.88 | 172.17
2017-11-05 15:00 | 188.06 | 173.42
2017-11-05 15:30 | 189.53 | 175.19
2017-11-05 16:00 | 191.45 | 176.44
2017-11-05 16:30 | 190.74 | 175.26
2017-11-05 17:00 | 219.38 | 204.37
2017-11-05 17:30 | 227.36 | 212.4
2017-11-05 18:00 | 227.35 | 212.43
2017-11-05 18:30 | 227.48 | 212.82
2017-11-05 19:00 | 226.93 | 213.45
2017-11-05 19:30 | 227.01 | 213.1
2017-11-05 20:00 | 225.36 | 211.03
2017-11-05 20:30 | 195.54 | 180.06
2017-11-05 21:00 | 183.71 | 167.54
2017-11-05 21:30 | 179.76 | 165.52
2017-11-05 22:00 | 177.65 | 163.32
2017-11-05 22:30 | 176.2 | 161.69
2017-11-05 23:00 | 174.2 | 159.43
2017-11-05 23:30 | 174.27 | 159.15
2017-11-06 | 172.08 | 157.32
2017-11-06 00:30 | 170.48 | 157.09
2017-11-06 01:00 | 169.19 | 156.14
2017-11-06 01:30 | 168.88 | 155.71
2017-11-06 02:00 | 168.56 | 154.95
2017-11-06 02:30 | 169.52 | 155.01
2017-11-06 03:00 | 169.4 | 154.35
2017-11-06 03:30 | 168.09 | 154.1
2017-11-06 04:00 | 167.51 | 154.03
2017-11-06 04:30 | 168.51 | 155.43
2017-11-06 05:00 | 168.32 | 155.28
2017-11-06 05:30 | 168.98 | 156.43
2017-11-06 06:00 | 169.84 | 157.86
2017-11-06 06:30 | 170.07 | 157.61
2017-11-06 07:00 | 191 | 179.32
2017-11-06 07:30 | 192.99 | 181.31
2017-11-06 08:00 | 194.12 | 181.58
2017-11-06 08:30 | 192.8 | 180.33
2017-11-06 09:00 | 190.63 | 178.35
2017-11-06 09:30 | 181.84 | 169.41
2017-11-06 10:00 | 186.79 | 174.31
2017-11-06 10:30 | 197.29 | 185.79
2017-11-06 11:00 | 201.63 | 190.52
2017-11-06 11:30 | 176.32 | 165.35
2017-11-06 12:00 | 164.5 | 153.3
2017-11-06 12:30 | 165.97 | 154.87
2017-11-06 13:00 | 168.75 | 157.83
2017-11-06 13:30 | 173.41 | 161.73
2017-11-06 14:00 | 177.17 | 165.1
2017-11-06 14:30 | 172.53 | 162.1
2017-11-06 15:00 | 169.64 | 159.29
2017-11-06 15:30 | 168.59 | 156.96
2017-11-06 16:00 | 171.1 | 158.89
2017-11-06 16:30 | 167.81 | 155.43
2017-11-06 17:00 | 177.03 | 162.57
2017-11-06 17:30 | 183.18 | 167.91
2017-11-06 18:00 | 184.63 | 169.18
2017-11-06 18:30 | 182.95 | 167.11
2017-11-06 19:00 | 180.68 | 165.26
2017-11-06 19:30 | 175.91 | 159.61
2017-11-06 20:00 | 159.81 | 144.62
2017-11-06 20:30 | 163 | 149.87
2017-11-06 21:00 | 162.4 | 147.39
2017-11-06 21:30 | 158.83 | 144.29
2017-11-06 22:00 | 156.64 | 141.54
2017-11-06 22:30 | 154.02 | 139.2
2017-11-06 23:00 | 153.23 | 138.26
2017-11-06 23:30 | 152.52 | 137.52
2017-11-07 | 151.69 | 136.91
2017-11-07 00:30 | 151.8 | 137.68
2017-11-07 01:00 | 151.61 | 138.15
2017-11-07 01:30 | 152.21 | 138.59
2017-11-07 02:00 | 151.59 | 137.8
2017-11-07 02:30 | 151.62 | 137.81
2017-11-07 03:00 | 150.98 | 137.17
2017-11-07 03:30 | 150.77 | 136.98
2017-11-07 04:00 | 150.76 | 137.05
2017-11-07 04:30 | 156.44 | 142.79
2017-11-07 05:00 | 151.38 | 137.67
2017-11-07 05:30 | 152.4 | 139.03
2017-11-07 06:00 | 153.78 | 140.58
2017-11-07 06:30 | 155.26 | 141.8
2017-11-07 07:00 | 156.48 | 142.37
2017-11-07 07:30 | 158.07 | 144.01
2017-11-07 08:00 | 158.79 | 144.49
2017-11-07 08:30 | 157.84 | 143.15
2017-11-07 09:00 | 157.61 | 142.61
2017-11-07 09:30 | 156.5 | 141.45
2017-11-07 10:00 | 156.55 | 141.48
2017-11-07 10:30 | 155.54 | 140.31
2017-11-07 11:00 | 156.21 | 141.24
2017-11-07 11:30 | 156.44 | 141.31
2017-11-07 12:00 | 157.55 | 142.18
2017-11-07 12:30 | 159.07 | 142.42
2017-11-07 13:00 | 159.31 | 142.93
2017-11-07 13:30 | 160.1 | 143.61
2017-11-07 14:00 | 160.44 | 144.09
2017-11-07 14:30 | 160.83 | 144.44
2017-11-07 15:00 | 161.56 | 145.46
2017-11-07 15:30 | 161.91 | 146.59
2017-11-07 16:00 | 162.29 | 147.1
2017-11-07 16:30 | 164.2 | 148.67
2017-11-07 17:00 | 163.46 | 148.48
2017-11-07 17:30 | 164.4 | 149.17
2017-11-07 18:00 | 194.92 | 179.89
2017-11-07 18:30 | 207.07 | 192.09
2017-11-07 19:00 | 208.78 | 194.13
2017-11-07 19:30 | 208.86 | 194.25
2017-11-07 20:00 | 178.62 | 164
2017-11-07 20:30 | 164.16 | 149.09
2017-11-07 21:00 | 163.34 | 147.86
2017-11-07 21:30 | 159.96 | 145.8
2017-11-07 22:00 | 159.18 | 144.76
2017-11-07 22:30 | 157.68 | 142.5
2017-11-07 23:00 | 156.01 | 140.75
2017-11-07 23:30 | 153.2 | 139.55
2017-11-08 | 151.32 | 138.19
2017-11-08 00:30 | 150.77 | 138.22
2017-11-08 01:00 | 150.38 | 136.85
2017-11-08 01:30 | 150.27 | 136.85
2017-11-08 02:00 | 148.94 | 136.2
2017-11-08 02:30 | 148.71 | 135.9
2017-11-08 03:00 | 148.3 | 135.33
2017-11-08 03:30 | 148.69 | 135.51
2017-11-08 04:00 | 148.5 | 135.29
2017-11-08 04:30 | 148.98 | 135.77
2017-11-08 05:00 | 150.36 | 136.8
2017-11-08 05:30 | 151.51 | 137.5
2017-11-08 06:00 | 153.53 | 139.47
2017-11-08 06:30 | 155.77 | 141.09
2017-11-08 07:00 | 156.94 | 141.92
2017-11-08 07:30 | 157.74 | 142.68
2017-11-08 08:00 | 158.93 | 142.96
2017-11-08 08:30 | 157.82 | 141.95
2017-11-08 09:00 | 156.63 | 140.62
2017-11-08 09:30 | 156.21 | 140.31
2017-11-08 10:00 | 156.33 | 140.28
2017-11-08 10:30 | 156 | 140.07
2017-11-08 11:00 | 156.67 | 140.67
2017-11-08 11:30 | 157.27 | 141.38
2017-11-08 12:00 | 158.03 | 142.34
2017-11-08 12:30 | 158.46 | 142.71
2017-11-08 13:00 | 160.27 | 144.11
2017-11-08 13:30 | 161.32 | 145.1
2017-11-08 14:00 | 162.44 | 146.47
2017-11-08 14:30 | 163.05 | 147.2
2017-11-08 15:00 | 163.83 | 147.94
2017-11-08 15:30 | 164.96 | 149.01
2017-11-08 16:00 | 165.6 | 149.88
2017-11-08 16:30 | 172.11 | 156.41
2017-11-08 17:00 | 173.97 | 158.29
2017-11-08 17:30 | 176.71 | 160.82
2017-11-08 18:00 | 177.36 | 161.56
2017-11-08 18:30 | 177.63 | 161.9
2017-11-08 19:00 | 180.28 | 164.85
2017-11-08 19:30 | 177.82 | 162.56
2017-11-08 20:00 | 177.48 | 162.06
2017-11-08 20:30 | 176.2 | 160.45
2017-11-08 21:00 | 175.36 | 159.27
2017-11-08 21:30 | 173.81 | 158.26
2017-11-08 22:00 | 173.07 | 157.16
2017-11-08 22:30 | 172.05 | 155.68
2017-11-08 23:00 | 171.01 | 153.89
2017-11-08 23:30 | 170.51 | 153.7
2017-11-09 | 169.8 | 153.65
2017-11-09 00:30 | 170.16 | 153.87
2017-11-09 01:00 | 168.9 | 152.6
2017-11-09 01:30 | 168.96 | 152.53
2017-11-09 02:00 | 169.18 | 152.57
2017-11-09 02:30 | 168.35 | 151.71
2017-11-09 03:00 | 168.13 | 151.35
2017-11-09 03:30 | 167.62 | 150.99
2017-11-09 04:00 | 167.86 | 151.3
2017-11-09 04:30 | 166.92 | 150.84
2017-11-09 05:00 | 168.02 | 151.67
2017-11-09 05:30 | 169.29 | 152.99
2017-11-09 06:00 | 169.48 | 153.8
2017-11-09 06:30 | 170.07 | 154.68
2017-11-09 07:00 | 203.08 | 188.11
2017-11-09 07:30 | 214.94 | 200.29
2017-11-09 08:00 | 214.68 | 199.54
2017-11-09 08:30 | 213.44 | 198.07
2017-11-09 09:00 | 214 | 198.4
2017-11-09 09:30 | 186.92 | 170.85
2017-11-09 10:00 | 173.76 | 157.91
2017-11-09 10:30 | 174.05 | 158.29
2017-11-09 11:00 | 172.86 | 157.38
2017-11-09 11:30 | 173.89 | 158.8
2017-11-09 12:00 | 172.91 | 158.08
2017-11-09 12:30 | 173.41 | 158.57
2017-11-09 13:00 | 173.9 | 159.29
2017-11-09 13:30 | 173.99 | 159.25
2017-11-09 14:00 | 174.62 | 160.13
2017-11-09 14:30 | 176.46 | 162.2
2017-11-09 15:00 | 177.01 | 162.59
2017-11-09 15:30 | 177.24 | 162.51
2017-11-09 16:00 | 177.95 | 163.63
2017-11-09 16:30 | 209.66 | 194.99
2017-11-09 17:00 | 222.45 | 207.75
2017-11-09 17:30 | 223.21 | 208.26
2017-11-09 18:00 | 224.66 | 209.43
2017-11-09 18:30 | 226.14 | 211.07
2017-11-09 19:00 | 228.67 | 213.53
2017-11-09 19:30 | 229.27 | 214.14
2017-11-09 20:00 | 196.49 | 181.13
2017-11-09 20:30 | 182.81 | 167.07
2017-11-09 21:00 | 181.01 | 164.93
2017-11-09 21:30 | 180.72 | 164.57
2017-11-09 22:00 | 178.75 | 162.49
2017-11-09 22:30 | 177.13 | 160.43
2017-11-09 23:00 | 176.33 | 158.95
2017-11-09 23:30 | 175.41 | 157.87
2017-11-10 | 173.68 | 156.33
2017-11-10 00:30 | 172.67 | 155.56
2017-11-10 01:00 | 171.28 | 154.24
2017-11-10 01:30 | 171.49 | 154.78
2017-11-10 02:00 | 170.53 | 153.76
2017-11-10 02:30 | 169.62 | 153.21
2017-11-10 03:00 | 168.51 | 152.87
2017-11-10 03:30 | 168.41 | 152.87
2017-11-10 04:00 | 168.14 | 152.79
2017-11-10 04:30 | 168.4 | 153.18
2017-11-10 05:00 | 169.75 | 154.54
2017-11-10 05:30 | 170.35 | 155.23
2017-11-10 06:00 | 171 | 156.08
2017-11-10 06:30 | 171.76 | 157.39
2017-11-10 07:00 | 174.81 | 160.1
2017-11-10 07:30 | 176.51 | 160.92
2017-11-10 08:00 | 176.83 | 160.63
2017-11-10 08:30 | 175.19 | 158.46
2017-11-10 09:00 | 174.77 | 157.9
2017-11-10 09:30 | 173.96 | 156.9
2017-11-10 10:00 | 173.64 | 156.62
2017-11-10 10:30 | 172.88 | 155.98
2017-11-10 11:00 | 173.46 | 156.79
2017-11-10 11:30 | 174.67 | 158.26
2017-11-10 12:00 | 174.84 | 158.3
2017-11-10 12:30 | 174.82 | 158.46
2017-11-10 13:00 | 175.76 | 159.09
2017-11-10 13:30 | 176.76 | 159.89
2017-11-10 14:00 | 177.07 | 160.41
2017-11-10 14:30 | 177.7 | 160.73
2017-11-10 15:00 | 180.54 | 160.97
2017-11-10 15:30 | 178.71 | 161.56
2017-11-10 16:00 | 178.79 | 162.09
2017-11-10 16:30 | 180.58 | 163.7
2017-11-10 17:00 | 180.64 | 163.6
2017-11-10 17:30 | 182.09 | 164.91
2017-11-10 18:00 | 182.03 | 164.9
2017-11-10 18:30 | 183.03 | 166.15
2017-11-10 19:00 | 183.65 | 167.26
2017-11-10 19:30 | 185.02 | 168.58
2017-11-10 20:00 | 184.36 | 167.71
2017-11-10 20:30 | 183.3 | 166.35
2017-11-10 21:00 | 182.35 | 165.01
2017-11-10 21:30 | 180.97 | 164.07
2017-11-10 22:00 | 180.23 | 163.19
2017-11-10 22:30 | 178.49 | 161.19
2017-11-10 23:00 | 177.72 | 159.93
2017-11-10 23:30 | 175.76 | 159.16
2017-11-11 | 173.1 | 157.51
2017-11-11 00:30 | 172.66 | 157.41
2017-11-11 01:00 | 171.25 | 157.06
2017-11-11 01:30 | 170.14 | 155.95
2017-11-11 02:00 | 169.3 | 154.93
2017-11-11 02:30 | 169.43 | 155.31
2017-11-11 03:00 | 168.74 | 154.47
2017-11-11 03:30 | 168.39 | 154.3
2017-11-11 04:00 | 168.04 | 154.19
2017-11-11 04:30 | 167.95 | 154.15
2017-11-11 05:00 | 168.61 | 154.94
2017-11-11 05:30 | 170.14 | 155.37
2017-11-11 06:00 | 170.65 | 155.64
2017-11-11 06:30 | 171.17 | 156.15
2017-11-11 07:00 | 173.07 | 157.04
2017-11-11 07:30 | 172.24 | 156.74
2017-11-11 08:00 | 172.29 | 157.19
2017-11-11 08:30 | 171.33 | 156.24
2017-11-11 09:00 | 172.12 | 157.05
2017-11-11 09:30 | 170.93 | 155.9
2017-11-11 10:00 | 171.44 | 156.14
2017-11-11 10:30 | 170.79 | 155.29
2017-11-11 11:00 | 171.3 | 155.53
2017-11-11 11:30 | 172.33 | 156.6
2017-11-11 12:00 | 173.18 | 157.66
2017-11-11 12:30 | 175 | 157.16
2017-11-11 13:00 | 175.92 | 157.77
2017-11-11 13:30 | 176.85 | 158.27
2017-11-11 14:00 | 173.96 | 158.44
2017-11-11 14:30 | 173.52 | 158.14
2017-11-11 15:00 | 175.13 | 159.82
2017-11-11 15:30 | 176.36 | 160.97
2017-11-11 16:00 | 176.75 | 161.73
2017-11-11 16:30 | 178.91 | 163.78
2017-11-11 17:00 | 178.85 | 164.01
2017-11-11 17:30 | 179.88 | 165.11
2017-11-11 18:00 | 180.48 | 165.89
2017-11-11 18:30 | 180.45 | 166.12
2017-11-11 19:00 | 182 | 167.05
2017-11-11 19:30 | 182.39 | 167.38
2017-11-11 20:00 | 181.44 | 166.14
2017-11-11 20:30 | 180.3 | 164.72
2017-11-11 21:00 | 178.68 | 162.61
2017-11-11 21:30 | 177.59 | 161.4
2017-11-11 22:00 | 175.76 | 159.73
2017-11-11 22:30 | 175 | 158.6
2017-11-11 23:00 | 174.25 | 157.34
2017-11-11 23:30 | 172.82 | 156.51
2017-11-12 | 171.29 | 155.31
2017-11-12 00:30 | 169.84 | 155.2
2017-11-12 01:00 | 168.74 | 154.55
2017-11-12 01:30 | 166.9 | 153.13
2017-11-12 02:00 | 166.6 | 153.15
2017-11-12 02:30 | 166.39 | 152.87
2017-11-12 03:00 | 165.9 | 152.39
2017-11-12 03:30 | 166.04 | 152.17
2017-11-12 04:00 | 166.94 | 151.96
2017-11-12 04:30 | 166.78 | 151.66
2017-11-12 05:00 | 167.05 | 151.62
2017-11-12 05:30 | 167.2 | 151.66
2017-11-12 06:00 | 168.03 | 152.6
2017-11-12 06:30 | 169.71 | 154.25
2017-11-12 07:00 | 168.76 | 153.75
2017-11-12 07:30 | 169 | 154.15
2017-11-12 08:00 | 168.78 | 153.68
2017-11-12 08:30 | 169.16 | 154.11
2017-11-12 09:00 | 170.47 | 153.88
2017-11-12 09:30 | 170.5 | 155.07
2017-11-12 10:00 | 173.32 | 156.87
2017-11-12 10:30 | 174.86 | 157.09
2017-11-12 11:00 | 174.67 | 157
2017-11-12 11:30 | 175.75 | 158.18
2017-11-12 12:00 | 177.21 | 159.74
2017-11-12 12:30 | 178.75 | 161.49
2017-11-12 13:00 | 179.4 | 162.17
2017-11-12 13:30 | 178.74 | 161.72
2017-11-12 14:00 | 176.38 | 161.39
2017-11-12 14:30 | 176.03 | 161.85
2017-11-12 15:00 | 178.07 | 163.97
2017-11-12 15:30 | 177.01 | 162.27
2017-11-12 16:00 | 176.61 | 161.52
2017-11-12 16:30 | 177.13 | 161.75
2017-11-12 17:00 | 178.86 | 163.45
2017-11-12 17:30 | 179.88 | 164.95
2017-11-12 18:00 | 180.37 | 165.17
2017-11-12 18:30 | 181.1 | 166.01
2017-11-12 19:00 | 181.98 | 167.16
2017-11-12 19:30 | 182.23 | 167.51
2017-11-12 20:00 | 181.03 | 165.79
2017-11-12 20:30 | 179.51 | 163.73
2017-11-12 21:00 | 178.85 | 162.67
2017-11-12 21:30 | 177.75 | 161.47
2017-11-12 22:00 | 176.1 | 159.57
2017-11-12 22:30 | 175.46 | 158.58
2017-11-12 23:00 | 173.52 | 156.05
2017-11-12 23:30 | 172.73 | 155.4
2017-11-13 | 171.71 | 154.67
2017-11-13 00:30 | 170.23 | 153.84
2017-11-13 01:00 | 168.91 | 153
2017-11-13 01:30 | 168.55 | 152.63
2017-11-13 02:00 | 167.94 | 152.05
2017-11-13 02:30 | 167.52 | 151.81
2017-11-13 03:00 | 167.39 | 151.71
2017-11-13 03:30 | 166.86 | 151.28
2017-11-13 04:00 | 167.71 | 152.06
2017-11-13 04:30 | 168.04 | 152.13
2017-11-13 05:00 | 168.32 | 152.57
2017-11-13 05:30 | 169.87 | 154.47
2017-11-13 06:00 | 170.49 | 155.4
2017-11-13 06:30 | 172.71 | 156.93
2017-11-13 07:00 | 173.6 | 157.93
2017-11-13 07:30 | 175.56 | 159.43
2017-11-13 08:00 | 176.86 | 160.63
2017-11-13 08:30 | 176.09 | 159.74
2017-11-13 09:00 | 175.49 | 159.05
2017-11-13 09:30 | 174.63 | 158.37
2017-11-13 10:00 | 174.96 | 158.85
2017-11-13 10:30 | 174.32 | 158.45
2017-11-13 11:00 | 173.93 | 158.47
2017-11-13 11:30 | 175.66 | 159.67
2017-11-13 12:00 | 177.44 | 161.82
2017-11-13 12:30 | 177.34 | 162.04
2017-11-13 13:00 | 178.11 | 162.13
2017-11-13 13:30 | 180.09 | 163.35
2017-11-13 14:00 | 182 | 165.37
2017-11-13 14:30 | 182.4 | 165.91
2017-11-13 15:00 | 181.75 | 165.72
2017-11-13 15:30 | 180.66 | 165.13
2017-11-13 16:00 | 180.68 | 165.2
2017-11-13 16:30 | 182.02 | 166.37
2017-11-13 17:00 | 181.92 | 165.49
2017-11-13 17:30 | 182.23 | 166.22
2017-11-13 18:00 | 182.91 | 167.15
2017-11-13 18:30 | 183.85 | 168.04
2017-11-13 19:00 | 185.9 | 170.42
2017-11-13 19:30 | 186.47 | 171.02
2017-11-13 20:00 | 184.12 | 168.76
2017-11-13 20:30 | 184.36 | 168.22
2017-11-13 21:00 | 182.11 | 165.18
2017-11-13 21:30 | 179.14 | 163.15
2017-11-13 22:00 | 176.89 | 161.23
2017-11-13 22:30 | 174.99 | 158.64
2017-11-13 23:00 | 173.19 | 155.76
2017-11-13 23:30 | 172.07 | 154.5
2017-11-14 | 170.42 | 153.09
2017-11-14 00:30 | 170.68 | 153.66
2017-11-14 01:00 | 169.69 | 152.81
2017-11-14 01:30 | 169.73 | 153.47
2017-11-14 02:00 | 168.27 | 151.73
2017-11-14 02:30 | 168.14 | 151.58
2017-11-14 03:00 | 167.68 | 150.97
2017-11-14 03:30 | 168.24 | 151.63
2017-11-14 04:00 | 168.13 | 151.62
2017-11-14 04:30 | 169.83 | 153.9
2017-11-14 05:00 | 170.68 | 154.84
2017-11-14 05:30 | 172.16 | 156.58
2017-11-14 06:00 | 172.47 | 157.29
2017-11-14 06:30 | 174.06 | 159.32
2017-11-14 07:00 | 176.83 | 161.73
2017-11-14 07:30 | 176.37 | 162.41
2017-11-14 08:00 | 175.85 | 161.55
2017-11-14 08:30 | 176.57 | 161.93
2017-11-14 09:00 | 175.02 | 160.56
2017-11-14 09:30 | 174.94 | 161.09
2017-11-14 10:00 | 174.1 | 160.28
2017-11-14 10:30 | 173.69 | 160.08
2017-11-14 11:00 | 175.45 | 161.79
2017-11-14 11:30 | 177.21 | 163.23
2017-11-14 12:00 | 177.32 | 163.95
2017-11-14 12:30 | 178.25 | 165.46
2017-11-14 13:00 | 180.08 | 166.93
2017-11-14 13:30 | 180.19 | 167.66
2017-11-14 14:00 | 180.68 | 168.39
2017-11-14 14:30 | 182.1 | 169.49
2017-11-14 15:00 | 181.59 | 169.36
2017-11-14 15:30 | 183.45 | 170.28
2017-11-14 16:00 | 182.77 | 169.58
2017-11-14 16:30 | 184.3 | 170.58
2017-11-14 17:00 | 185.51 | 171.47
2017-11-14 17:30 | 186.05 | 171.64
2017-11-14 18:00 | 188.18 | 173.2
2017-11-14 18:30 | 188.54 | 173.63
2017-11-14 19:00 | 189.87 | 175.04
2017-11-14 19:30 | 190.53 | 175.95
2017-11-14 20:00 | 189.06 | 174.07
2017-11-14 20:30 | 187.91 | 172.59
2017-11-14 21:00 | 186.04 | 170.25
2017-11-14 21:30 | 183.99 | 169.11
2017-11-14 22:00 | 183.42 | 168.67
2017-11-14 22:30 | 180.24 | 164.79
2017-11-14 23:00 | 179.94 | 163.3
2017-11-14 23:30 | 178.27 | 162.26
2017-11-15 | 175.75 | 160.19
2017-11-15 00:30 | 174.81 | 159.51
2017-11-15 01:00 | 173.24 | 158.87
2017-11-15 01:30 | 172.36 | 158.15
2017-11-15 02:00 | 172.27 | 157.89
2017-11-15 02:30 | 172.05 | 157.7
2017-11-15 03:00 | 171.4 | 156.89
2017-11-15 03:30 | 171.6 | 157.19
2017-11-15 04:00 | 171.23 | 156.59
2017-11-15 04:30 | 172.1 | 157.83
2017-11-15 05:00 | 172.22 | 158.13
2017-11-15 05:30 | 173.76 | 160.04
2017-11-15 06:00 | 175.28 | 161.3
2017-11-15 06:30 | 176.93 | 162.89
2017-11-15 07:00 | 179.45 | 163.96
2017-11-15 07:30 | 180.49 | 165.55
2017-11-15 08:00 | 179.14 | 164.56
2017-11-15 08:30 | 177.9 | 163.27
2017-11-15 09:00 | 177.15 | 163.46
2017-11-15 09:30 | 175.88 | 162.3
2017-11-15 10:00 | 176.33 | 162.35
2017-11-15 10:30 | 176.84 | 162.78
2017-11-15 11:00 | 177.76 | 163.36
2017-11-15 11:30 | 179.57 | 164.84
2017-11-15 12:00 | 180.92 | 165.67
2017-11-15 12:30 | 182.2 | 165.98
2017-11-15 13:00 | 183.78 | 167.16
2017-11-15 13:30 | 183.11 | 167.29
2017-11-15 14:00 | 182.84 | 167.19
2017-11-15 14:30 | 183.52 | 167.83
2017-11-15 15:00 | 182.72 | 167.4
2017-11-15 15:30 | 183.83 | 168.75
2017-11-15 16:00 | 184.47 | 169.03
2017-11-15 16:30 | 184.48 | 168.59
2017-11-15 17:00 | 184.23 | 168.54
2017-11-15 17:30 | 184.7 | 168.82
2017-11-15 18:00 | 185.35 | 169.41
2017-11-15 18:30 | 186.74 | 170.45
2017-11-15 19:00 | 187.7 | 171.83
2017-11-15 19:30 | 187.56 | 171.66
2017-11-15 20:00 | 186.38 | 170.26
2017-11-15 20:30 | 184.96 | 168.22
2017-11-15 21:00 | 183.56 | 166.92
2017-11-15 21:30 | 181.51 | 165.97
2017-11-15 22:00 | 180.06 | 164.35
2017-11-15 22:30 | 178.97 | 162.78
2017-11-15 23:00 | 177.19 | 160.75
2017-11-15 23:30 | 175.43 | 160
2017-11-16 | 172.82 | 158.57
2017-11-16 00:30 | 171.62 | 157.6
2017-11-16 01:00 | 171.38 | 156.99
2017-11-16 01:30 | 171.42 | 156.29
2017-11-16 02:00 | 171.36 | 156.05
2017-11-16 02:30 | 170.9 | 155.5
2017-11-16 03:00 | 170.46 | 155.2
2017-11-16 03:30 | 169.93 | 155.38
2017-11-16 04:00 | 170.1 | 155.64
2017-11-16 04:30 | 170.25 | 155.8
2017-11-16 05:00 | 170.97 | 156.44
2017-11-16 05:30 | 172.28 | 157.83
2017-11-16 06:00 | 173.16 | 158.44
2017-11-16 06:30 | 175.96 | 161.18
2017-11-16 07:00 | 177.23 | 162.19
2017-11-16 07:30 | 177.27 | 162.17
2017-11-16 08:00 | 177.1 | 161.98
2017-11-16 08:30 | 176.08 | 161.07
2017-11-16 09:00 | 176.74 | 161.57
2017-11-16 09:30 | 175.35 | 160.09
2017-11-16 10:00 | 176.17 | 160.13
2017-11-16 10:30 | 176.45 | 160.62
2017-11-16 11:00 | 179.03 | 163.73
2017-11-16 11:30 | 179.12 | 163.53
2017-11-16 12:00 | 181.11 | 165.58
2017-11-16 12:30 | 181.49 | 166.04
2017-11-16 13:00 | 183.53 | 167.64
2017-11-16 13:30 | 184.03 | 168.3
2017-11-16 14:00 | 184.8 | 169.25
2017-11-16 14:30 | 185.33 | 170
2017-11-16 15:00 | 185.03 | 169.69
2017-11-16 15:30 | 185 | 169.51
2017-11-16 16:00 | 185.1 | 169.34
2017-11-16 16:30 | 186.73 | 170.89
2017-11-16 17:00 | 186.91 | 171.12
2017-11-16 17:30 | 187.52 | 171.32
2017-11-16 18:00 | 187.84 | 171.53
2017-11-16 18:30 | 188.39 | 172.11
2017-11-16 19:00 | 189.77 | 173.51
2017-11-16 19:30 | 189.35 | 172.8
2017-11-16 20:00 | 187.75 | 170.5
2017-11-16 20:30 | 184.5 | 168.64
2017-11-16 21:00 | 182.79 | 167.07
2017-11-16 21:30 | 180.29 | 166.07
2017-11-16 22:00 | 178.38 | 164.24
2017-11-16 22:30 | 177.3 | 162.65
2017-11-16 23:00 | 175.94 | 160.85
2017-11-16 23:30 | 175.02 | 159.83
2017-11-17 | 173.12 | 158.08
2017-11-17 00:30 | 171.95 | 157.14
2017-11-17 01:00 | 169.88 | 155.98
2017-11-17 01:30 | 169.56 | 155.8
2017-11-17 02:00 | 169.41 | 155.46
2017-11-17 02:30 | 168.88 | 154.88
2017-11-17 03:00 | 169.12 | 155.1
2017-11-17 03:30 | 168.28 | 154.26
2017-11-17 04:00 | 168.46 | 154.39
2017-11-17 04:30 | 169.14 | 155.13
2017-11-17 05:00 | 169.26 | 154.9
2017-11-17 05:30 | 169.91 | 155.69
2017-11-17 06:00 | 170.49 | 156.73
2017-11-17 06:30 | 173.02 | 159.08
2017-11-17 07:00 | 174.32 | 159.75
2017-11-17 07:30 | 175.79 | 161.13
2017-11-17 08:00 | 176.35 | 161.71
2017-11-17 08:30 | 174.66 | 160.4
2017-11-17 09:00 | 174.73 | 160.45
2017-11-17 09:30 | 173.68 | 159.39
2017-11-17 10:00 | 174.32 | 159.97
2017-11-17 10:30 | 174.4 | 160.12
2017-11-17 11:00 | 175.58 | 161.11
2017-11-17 11:30 | 176.44 | 162.01
2017-11-17 12:00 | 178.04 | 163.86
2017-11-17 12:30 | 179.8 | 165.21
2017-11-17 13:00 | 180.6 | 166.02
2017-11-17 13:30 | 181.45 | 167.32
2017-11-17 14:00 | 183.14 | 169.36
2017-11-17 14:30 | 183.13 | 169.79
2017-11-17 15:00 | 183.2 | 169.74
2017-11-17 15:30 | 182.83 | 168.73
2017-11-17 16:00 | 184.31 | 170.04
2017-11-17 16:30 | 184.3 | 170.14
2017-11-17 17:00 | 182.4 | 168.11
2017-11-17 17:30 | 180.42 | 165.88
2017-11-17 18:00 | 181.79 | 167.07
2017-11-17 18:30 | 182.32 | 167.67
2017-11-17 19:00 | 182.02 | 167.36
2017-11-17 19:30 | 182.14 | 166.72
2017-11-17 20:00 | 181.31 | 165.54
2017-11-17 20:30 | 179.98 | 164.21
2017-11-17 21:00 | 179.54 | 163.39
2017-11-17 21:30 | 176.93 | 162.54
2017-11-17 22:00 | 176.7 | 162.19
2017-11-17 22:30 | 174.4 | 159.93
2017-11-17 23:00 | 173.6 | 158.73
2017-11-17 23:30 | 173.03 | 157.67
2017-11-18 | 170.6 | 155.78
2017-11-18 00:30 | 168.49 | 155.92
2017-11-18 01:00 | 167.33 | 155.17
2017-11-18 01:30 | 166.53 | 154.96
2017-11-18 02:00 | 161.07 | 148.96
2017-11-18 02:30 | 158.38 | 146.7
2017-11-18 03:00 | 157.62 | 146.15
2017-11-18 03:30 | 158.32 | 146.88
2017-11-18 04:00 | 158.07 | 146.66
2017-11-18 04:30 | 156.71 | 144.8
2017-11-18 05:00 | 158.47 | 146.96
2017-11-18 05:30 | 158.54 | 147.08
2017-11-18 06:00 | 159.11 | 147.72
2017-11-18 06:30 | 159.43 | 148.03
2017-11-18 07:00 | 160.51 | 148.47
2017-11-18 07:30 | 161.19 | 149.02
2017-11-18 08:00 | 161.84 | 148.96
2017-11-18 08:30 | 161.01 | 147.04
2017-11-18 09:00 | 160.5 | 144.12
2017-11-18 09:30 | 160.23 | 144.07
2017-11-18 10:00 | 160.37 | 144.47
2017-11-18 10:30 | 159.86 | 143.73
2017-11-18 11:00 | 160.68 | 143.84
2017-11-18 11:30 | 160.68 | 144.48
2017-11-18 12:00 | 161.86 | 145.71
2017-11-18 12:30 | 163.28 | 146.33
2017-11-18 13:00 | 170.22 | 153.29
2017-11-18 13:30 | 167.24 | 150.17
2017-11-18 14:00 | 165.71 | 149.05
2017-11-18 14:30 | 166.32 | 149.91
2017-11-18 15:00 | 176.54 | 158.65
2017-11-18 15:30 | 177.79 | 160.11
2017-11-18 16:00 | 179.2 | 161.88
2017-11-18 16:30 | 180.53 | 163.62
2017-11-18 17:00 | 180.82 | 164.24
2017-11-18 17:30 | 182.05 | 165.26
2017-11-18 18:00 | 183.37 | 166.48
2017-11-18 18:30 | 183.31 | 166.32
2017-11-18 19:00 | 183.83 | 167.11
2017-11-18 19:30 | 183.23 | 166.32
2017-11-18 20:00 | 182.39 | 165.33
2017-11-18 20:30 | 181.66 | 164.62
2017-11-18 21:00 | 180.53 | 163.81
2017-11-18 21:30 | 178.95 | 163.53
2017-11-18 22:00 | 177.77 | 162.4
2017-11-18 22:30 | 176.43 | 160.81
2017-11-18 23:00 | 175.62 | 159.5
2017-11-18 23:30 | 174.05 | 158.47
2017-11-19 | 173.15 | 158.39
2017-11-19 00:30 | 171.24 | 156.64
2017-11-19 01:00 | 169.97 | 156.07
2017-11-19 01:30 | 169.41 | 155.4
2017-11-19 02:00 | 169.43 | 155.49
2017-11-19 02:30 | 168.93 | 154.69
2017-11-19 03:00 | 168.89 | 154.82
2017-11-19 03:30 | 168.43 | 154.16
2017-11-19 04:00 | 168.4 | 154.21
2017-11-19 04:30 | 169.09 | 155.03
2017-11-19 05:00 | 168.28 | 154.15
2017-11-19 05:30 | 168.3 | 154.27
2017-11-19 06:00 | 167.73 | 153.61
2017-11-19 06:30 | 168.16 | 154.13
2017-11-19 07:00 | 169.37 | 154.59
2017-11-19 07:30 | 170.2 | 155.22
2017-11-19 08:00 | 170.69 | 155.28
2017-11-19 08:30 | 170.67 | 155.34
2017-11-19 09:00 | 170.23 | 154.7
2017-11-19 09:30 | 170.42 | 154.73
2017-11-19 10:00 | 170.47 | 154.9
2017-11-19 10:30 | 169.54 | 154.08
2017-11-19 11:00 | 169.64 | 154.27
2017-11-19 11:30 | 170.16 | 154.88
2017-11-19 12:00 | 170.37 | 155.11
2017-11-19 12:30 | 171.23 | 155.93
2017-11-19 13:00 | 172.4 | 156.42
2017-11-19 13:30 | 173.87 | 157.46
2017-11-19 14:00 | 173.68 | 157.47
2017-11-19 14:30 | 174.13 | 157.82
2017-11-19 15:00 | 174.82 | 158.65
2017-11-19 15:30 | 175.19 | 158.83
2017-11-19 16:00 | 176.13 | 159.88
2017-11-19 16:30 | 177.11 | 160.52
2017-11-19 17:00 | 177.63 | 160.94
2017-11-19 17:30 | 178.16 | 161.05
2017-11-19 18:00 | 179.21 | 162.22
2017-11-19 18:30 | 179.7 | 163.19
2017-11-19 19:00 | 180.67 | 163.96
2017-11-19 19:30 | 181.33 | 164.51
2017-11-19 20:00 | 180.43 | 163.35
2017-11-19 20:30 | 179.91 | 162.2
2017-11-19 21:00 | 178.65 | 160.6
2017-11-19 21:30 | 177.34 | 160.34
2017-11-19 22:00 | 176.13 | 158.9
2017-11-19 22:30 | 173.82 | 156.48
2017-11-19 23:00 | 172.54 | 154.78
2017-11-19 23:30 | 171.84 | 154.23
2017-11-20 | 170.57 | 153.74
2017-11-20 00:30 | 169.73 | 153.4
2017-11-20 01:00 | 169.07 | 152.51
2017-11-20 01:30 | 168.71 | 152.21
2017-11-20 02:00 | 168.04 | 151.62
2017-11-20 02:30 | 167.23 | 151.27
2017-11-20 03:00 | 167.66 | 151.4
2017-11-20 03:30 | 167.73 | 151.49
2017-11-20 04:00 | 167.85 | 151.65
2017-11-20 04:30 | 167.61 | 151.57
2017-11-20 05:00 | 168.57 | 152.51
2017-11-20 05:30 | 170.12 | 154.22
2017-11-20 06:00 | 170.47 | 154.95
2017-11-20 06:30 | 172.77 | 157.8
2017-11-20 07:00 | 173.67 | 158.42
2017-11-20 07:30 | 174.87 | 159.44
2017-11-20 08:00 | 174.74 | 159.15
2017-11-20 08:30 | 173.42 | 158.26
2017-11-20 09:00 | 173.14 | 158.11
2017-11-20 09:30 | 172.21 | 156.93
2017-11-20 10:00 | 173.33 | 157.87
2017-11-20 10:30 | 172.64 | 156.87
2017-11-20 11:00 | 173.25 | 157.71
2017-11-20 11:30 | 174.03 | 158.73
2017-11-20 12:00 | 173.86 | 158.68
2017-11-20 12:30 | 174.76 | 159.4
2017-11-20 13:00 | 177.1 | 161.49
2017-11-20 13:30 | 178.12 | 162.3
2017-11-20 14:00 | 177.67 | 162.11
2017-11-20 14:30 | 178.45 | 162.8
2017-11-20 15:00 | 178.69 | 163.03
2017-11-20 15:30 | 176.91 | 161.9
2017-11-20 16:00 | 177.66 | 162.72
2017-11-20 16:30 | 178.08 | 163.42
2017-11-20 17:00 | 177.91 | 163.35
2017-11-20 17:30 | 179.06 | 164.42
2017-11-20 18:00 | 180.34 | 165.64
2017-11-20 18:30 | 180.93 | 166.08
2017-11-20 19:00 | 182.94 | 168.44
2017-11-20 19:30 | 183.26 | 168.87
2017-11-20 20:00 | 182.04 | 167.74
2017-11-20 20:30 | 180.65 | 166.06
2017-11-20 21:00 | 179.25 | 164.06
2017-11-20 21:30 | 178.06 | 162.9
2017-11-20 22:00 | 177.1 | 161.42
2017-11-20 22:30 | 173.9 | 159.08
2017-11-20 23:00 | 172.52 | 157.68
2017-11-20 23:30 | 172.18 | 157.02
2017-11-21 | 171.43 | 156.25
2017-11-21 00:30 | 170.8 | 156
2017-11-21 01:00 | 169.2 | 154.77
2017-11-21 01:30 | 168.99 | 154.7
2017-11-21 02:00 | 167.78 | 154.32
2017-11-21 02:30 | 167.5 | 153.82
2017-11-21 03:00 | 167.05 | 153.48
2017-11-21 03:30 | 166.88 | 153.17
2017-11-21 04:00 | 167.23 | 153.52
2017-11-21 04:30 | 167.51 | 153.75
2017-11-21 05:00 | 168.73 | 154.93
2017-11-21 05:30 | 169.44 | 155.75
2017-11-21 06:00 | 170.86 | 157.39
2017-11-21 06:30 | 171.88 | 158.62
2017-11-21 07:00 | 174.55 | 160.66
2017-11-21 07:30 | 175.34 | 161.48
2017-11-21 08:00 | 176.12 | 161.76
2017-11-21 08:30 | 174.48 | 160.08
2017-11-21 09:00 | 173.57 | 159.11
2017-11-21 09:30 | 172.14 | 157.92
2017-11-21 10:00 | 174.06 | 158.58
2017-11-21 10:30 | 173.27 | 157.9
2017-11-21 11:00 | 173.75 | 158.62
2017-11-21 11:30 | 174.39 | 159.1
2017-11-21 12:00 | 175.22 | 160.19
2017-11-21 12:30 | 175.77 | 159.97
2017-11-21 13:00 | 177.68 | 161.72
2017-11-21 13:30 | 177.77 | 161.96
2017-11-21 14:00 | 177.67 | 162.07
2017-11-21 14:30 | 176.96 | 162.21
2017-11-21 15:00 | 177.36 | 162.6
2017-11-21 15:30 | 176.93 | 162.24
2017-11-21 16:00 | 205.02 | 191.88
2017-11-21 16:30 | 214.33 | 201.49
2017-11-21 17:00 | 216.15 | 202.9
2017-11-21 17:30 | 216.46 | 203.04
2017-11-21 18:00 | 217.95 | 204.43
2017-11-21 18:30 | 219.34 | 205.88
2017-11-21 19:00 | 221.48 | 209.09
2017-11-21 19:30 | 222.66 | 210.23
2017-11-21 20:00 | 221.7 | 208.98
2017-11-21 20:30 | 220.34 | 207.25
2017-11-21 21:00 | 220.04 | 206.26
2017-11-21 21:30 | 187.86 | 173.56
2017-11-21 22:00 | 178.16 | 163.04
2017-11-21 22:30 | 176.69 | 161.24
2017-11-21 23:00 | 174.92 | 158.74
2017-11-21 23:30 | 174.41 | 158.46
2017-11-22 | 172.92 | 157.61
2017-11-22 00:30 | 171.28 | 156.44
2017-11-22 01:00 | 170.7 | 156.01
2017-11-22 01:30 | 170.33 | 155.59
2017-11-22 02:00 | 169.5 | 154.92
2017-11-22 02:30 | 169.05 | 154.43
2017-11-22 03:00 | 168.64 | 154.15
2017-11-22 03:30 | 168.79 | 154.27
2017-11-22 04:00 | 168.49 | 153.88
2017-11-22 04:30 | 168.91 | 154.39
2017-11-22 05:00 | 169.77 | 155.16
2017-11-22 05:30 | 171.31 | 156.76
2017-11-22 06:00 | 171.82 | 157.69
2017-11-22 06:30 | 173.17 | 159.43
2017-11-22 07:00 | 175.09 | 160.85
2017-11-22 07:30 | 176.23 | 161.26
2017-11-22 08:00 | 176.18 | 161.52
2017-11-22 08:30 | 174.45 | 159.53
2017-11-22 09:00 | 173.54 | 158.8
2017-11-22 09:30 | 172.42 | 157.72
2017-11-22 10:00 | 173.6 | 158.9
2017-11-22 10:30 | 173.56 | 159.01
2017-11-22 11:00 | 177.56 | 163.61
2017-11-22 11:30 | 211.08 | 199.41
2017-11-22 12:00 | 213.44 | 201.8
2017-11-22 12:30 | 214.34 | 202.72
2017-11-22 13:00 | 215.31 | 203.46
2017-11-22 13:30 | 215.1 | 203.21
2017-11-22 14:00 | 215 | 203.28
2017-11-22 14:30 | 215.63 | 203.9
2017-11-22 15:00 | 215.46 | 203.91
2017-11-22 15:30 | 215.65 | 203.65
2017-11-22 16:00 | 217.55 | 205.78
2017-11-22 16:30 | 217.44 | 205.3
2017-11-22 17:00 | 218.14 | 205.75
2017-11-22 17:30 | 218.63 | 206.01
2017-11-22 18:00 | 219.4 | 206.71
2017-11-22 18:30 | 220.45 | 207.53
2017-11-22 19:00 | 221.69 | 209.12
2017-11-22 19:30 | 222.56 | 210.3
2017-11-22 20:00 | 221.62 | 209.26
2017-11-22 20:30 | 220.64 | 207.96
2017-11-22 21:00 | 219.52 | 206.28
2017-11-22 21:30 | 187.53 | 172.85
2017-11-22 22:00 | 177.59 | 162.07
2017-11-22 22:30 | 176.05 | 160.02
2017-11-22 23:00 | 173.84 | 157.53
2017-11-22 23:30 | 173.32 | 156.92
2017-11-23 | 171.46 | 155.12
2017-11-23 00:30 | 170.06 | 155.08
2017-11-23 01:00 | 169.43 | 155.23
2017-11-23 01:30 | 168.57 | 154.32
2017-11-23 02:00 | 167.3 | 153.68
2017-11-23 02:30 | 166.73 | 153.13
2017-11-23 03:00 | 166.15 | 152.56
2017-11-23 03:30 | 166.56 | 152.86
2017-11-23 04:00 | 166.07 | 152.2
2017-11-23 04:30 | 166.36 | 152.74
2017-11-23 05:00 | 167.47 | 153.71
2017-11-23 05:30 | 169.32 | 155.7
2017-11-23 06:00 | 169.6 | 155.98
2017-11-23 06:30 | 172.17 | 158.45
2017-11-23 07:00 | 173.64 | 159.43
2017-11-23 07:30 | 174.06 | 160.03
2017-11-23 08:00 | 175.38 | 159.94
2017-11-23 08:30 | 174.26 | 158.21
2017-11-23 09:00 | 173.86 | 157.8
2017-11-23 09:30 | 173.07 | 156.87
2017-11-23 10:00 | 172.95 | 156.76
2017-11-23 10:30 | 173.74 | 157.87
2017-11-23 11:00 | 173.55 | 158.25
2017-11-23 11:30 | 175.1 | 159.03
2017-11-23 12:00 | 177 | 161.34
2017-11-23 12:30 | 168.52 | 152.51
2017-11-23 13:00 | 158.79 | 142.85
2017-11-23 13:30 | 161.41 | 146.39
2017-11-23 14:00 | 161.31 | 145.67
2017-11-23 14:30 | 190.18 | 177.03
2017-11-23 15:00 | 207.35 | 197.74
2017-11-23 15:30 | 220.19 | 209.63
2017-11-23 16:00 | 228.44 | 217.78
2017-11-23 16:30 | 228.71 | 217.77
2017-11-23 17:00 | 231.71 | 221.21
2017-11-23 17:30 | 239.82 | 230.27
2017-11-23 18:00 | 241.3 | 231.43
2017-11-23 18:30 | 242.22 | 232.29
2017-11-23 19:00 | 243.42 | 233.58
2017-11-23 19:30 | 244.52 | 234.71
2017-11-23 20:00 | 243.21 | 233.15
2017-11-23 20:30 | 241.44 | 231.56
2017-11-23 21:00 | 238.98 | 230.08
2017-11-23 21:30 | 223.67 | 213.37
2017-11-23 22:00 | 190.44 | 177.92
2017-11-23 22:30 | 178.79 | 163.08
2017-11-23 23:00 | 176.36 | 160.07
2017-11-23 23:30 | 176.65 | 160.4
2017-11-24 | 173.23 | 158.72
2017-11-24 00:30 | 172.12 | 158.14
2017-11-24 01:00 | 171.84 | 157.64
2017-11-24 01:30 | 171.7 | 156.49
2017-11-24 02:00 | 171.41 | 155.92
2017-11-24 02:30 | 170.74 | 155.09
2017-11-24 03:00 | 170.87 | 155.29
2017-11-24 03:30 | 171.05 | 155.26
2017-11-24 04:00 | 170.74 | 154.8
2017-11-24 04:30 | 171.08 | 155.11
2017-11-24 05:00 | 171.82 | 156.01
2017-11-24 05:30 | 173.08 | 157.61
2017-11-24 06:00 | 175.13 | 159.2
2017-11-24 06:30 | 176.55 | 160.7
2017-11-24 07:00 | 178.26 | 161.52
2017-11-24 07:30 | 178.65 | 162.04
2017-11-24 08:00 | 180.63 | 163.4
2017-11-24 08:30 | 179.28 | 162.22
2017-11-24 09:00 | 179.37 | 162.55
2017-11-24 09:30 | 178.43 | 161.37
2017-11-24 10:00 | 178.89 | 162.05
2017-11-24 10:30 | 179.74 | 162.37
2017-11-24 11:00 | 181.96 | 164.26
2017-11-24 11:30 | 184.27 | 166.57
2017-11-24 12:00 | 184.86 | 166.87
2017-11-24 12:30 | 212.73 | 197.97
2017-11-24 13:00 | 235.38 | 224.74
2017-11-24 13:30 | 239.39 | 229.08
2017-11-24 14:00 | 241.02 | 230.61
2017-11-24 14:30 | 242.08 | 231.35
2017-11-24 15:00 | 241.99 | 231.28
2017-11-24 15:30 | 242.22 | 231.52
2017-11-24 16:00 | 242.16 | 231.75
2017-11-24 16:30 | 242.94 | 232.74
2017-11-24 17:00 | 241.95 | 233.68
2017-11-24 17:30 | 242.48 | 233.9
2017-11-24 18:00 | 242.54 | 233.96
2017-11-24 18:30 | 242.1 | 233.51
2017-11-24 19:00 | 242.76 | 234.32
2017-11-24 19:30 | 243.59 | 235.29
2017-11-24 20:00 | 242.75 | 234.34
2017-11-24 20:30 | 241.19 | 232.5
2017-11-24 21:00 | 239.11 | 230.25
2017-11-24 21:30 | 236.73 | 229.04
2017-11-24 22:00 | 235.07 | 227.26
2017-11-24 22:30 | 233.54 | 225.57
2017-11-24 23:00 | 232.3 | 224.31
2017-11-24 23:30 | 231.19 | 223.13
2017-11-25 | 229.83 | 221.58
2017-11-25 00:30 | 214.58 | 204.14
2017-11-25 01:00 | 210.12 | 197.46
2017-11-25 01:30 | 209.06 | 196.51
2017-11-25 02:00 | 208.58 | 196.14
2017-11-25 02:30 | 207.94 | 195.71
2017-11-25 03:00 | 207.36 | 195.3
2017-11-25 03:30 | 207.09 | 194.93
2017-11-25 04:00 | 206.97 | 194.7
2017-11-25 04:30 | 207.13 | 194.67
2017-11-25 05:00 | 207.51 | 195.09
2017-11-25 05:30 | 208.11 | 195.62
2017-11-25 06:00 | 208.43 | 196.07
2017-11-25 06:30 | 211.36 | 196.87
2017-11-25 07:00 | 212.21 | 197.78
2017-11-25 07:30 | 212.53 | 198.35
2017-11-25 08:00 | 212.63 | 198.25
2017-11-25 08:30 | 186.64 | 170.77
2017-11-25 09:00 | 174.84 | 158.18
2017-11-25 09:30 | 174.45 | 158
2017-11-25 10:00 | 175.32 | 158.53
2017-11-25 10:30 | 176 | 159.7
2017-11-25 11:00 | 176.96 | 160.47
2017-11-25 11:30 | 177.01 | 160.46
2017-11-25 12:00 | 178.84 | 162.56
2017-11-25 12:30 | 181.79 | 164.57
2017-11-25 13:00 | 183.34 | 166.09
2017-11-25 13:30 | 183.79 | 166.68
2017-11-25 14:00 | 186.43 | 167.43
2017-11-25 14:30 | 189.34 | 167.75
2017-11-25 15:00 | 189.46 | 168.55
2017-11-25 15:30 | 190.62 | 170.38
2017-11-25 16:00 | 217.55 | 199.35
2017-11-25 16:30 | 227.76 | 209.55
2017-11-25 17:00 | 228.96 | 211.09
2017-11-25 17:30 | 230.71 | 212.31
2017-11-25 18:00 | 231.26 | 213.17
2017-11-25 18:30 | 231.12 | 212.66
2017-11-25 19:00 | 231.81 | 213.37
2017-11-25 19:30 | 232.11 | 213.55
2017-11-25 20:00 | 230.75 | 212.27
2017-11-25 20:30 | 229.2 | 210.04
2017-11-25 21:00 | 227.36 | 207.43
2017-11-25 21:30 | 224.04 | 205.31
2017-11-25 22:00 | 221.41 | 203.01
2017-11-25 22:30 | 219.74 | 201.29
2017-11-25 23:00 | 219.05 | 199.83
2017-11-25 23:30 | 218.63 | 199.04
2017-11-26 | 216.63 | 197.28
2017-11-26 00:30 | 215.03 | 196.76
2017-11-26 01:00 | 186.27 | 166.54
2017-11-26 01:30 | 175.54 | 155.72
2017-11-26 02:00 | 175.14 | 154.94
2017-11-26 02:30 | 174.21 | 154.17
2017-11-26 03:00 | 174.07 | 154.03
2017-11-26 03:30 | 173.3 | 153.67
2017-11-26 04:00 | 172.85 | 153.56
2017-11-26 04:30 | 172.64 | 153.47
2017-11-26 05:00 | 172.65 | 153.77
2017-11-26 05:30 | 172.58 | 153.28
2017-11-26 06:00 | 173.1 | 154.04
2017-11-26 06:30 | 173.1 | 154.61
2017-11-26 07:00 | 173.32 | 155.16
2017-11-26 07:30 | 174.79 | 156
2017-11-26 08:00 | 176.99 | 156.15
2017-11-26 08:30 | 177.58 | 156.34
2017-11-26 09:00 | 181.05 | 156.16
2017-11-26 09:30 | 181.65 | 156.8
2017-11-26 10:00 | 182.76 | 158.03
2017-11-26 10:30 | 183.7 | 158.67
2017-11-26 11:00 | 183.91 | 158.99
2017-11-26 11:30 | 184.9 | 160.33
2017-11-26 12:00 | 185.38 | 161.32
2017-11-26 12:30 | 188.1 | 164.02
2017-11-26 13:00 | 189.89 | 166.46
2017-11-26 13:30 | 191.12 | 167.85
2017-11-26 14:00 | 191.74 | 168.7
2017-11-26 14:30 | 192.24 | 169.65
2017-11-26 15:00 | 193.73 | 170.92
2017-11-26 15:30 | 193.35 | 170.77
2017-11-26 16:00 | 195.53 | 173.33
2017-11-26 16:30 | 224.21 | 203.38
2017-11-26 17:00 | 233.45 | 213.18
2017-11-26 17:30 | 235.41 | 214.68
2017-11-26 18:00 | 236.74 | 215.82
2017-11-26 18:30 | 236.5 | 216.65
2017-11-26 19:00 | 231.8 | 217.73
2017-11-26 19:30 | 205.59 | 191.05
2017-11-26 20:00 | 196.55 | 176.84
2017-11-26 20:30 | 197.13 | 174.2
2017-11-26 21:00 | 195.01 | 171.53
2017-11-26 21:30 | 192.14 | 169.5
2017-11-26 22:00 | 189.84 | 166.94
2017-11-26 22:30 | 187.66 | 164.22
2017-11-26 23:00 | 186.82 | 162.29
2017-11-26 23:30 | 185.83 | 161.16
2017-11-27 | 182.78 | 159.39
2017-11-27 00:30 | 180.36 | 158.58
2017-11-27 01:00 | 179.91 | 157.83
2017-11-27 01:30 | 179.07 | 157.01
2017-11-27 02:00 | 178.99 | 156.54
2017-11-27 02:30 | 178.53 | 156.19
2017-11-27 03:00 | 177.98 | 155.76
2017-11-27 03:30 | 177.59 | 155.21
2017-11-27 04:00 | 177.77 | 155.2
2017-11-27 04:30 | 177.64 | 155.4
2017-11-27 05:00 | 178.23 | 155.73
2017-11-27 05:30 | 182.73 | 157.39
2017-11-27 06:00 | 187.39 | 158.09
2017-11-27 06:30 | 190.22 | 160.88
2017-11-27 07:00 | 193.05 | 162.36
2017-11-27 07:30 | 194.41 | 162.96
2017-11-27 08:00 | 195.87 | 164.01
2017-11-27 08:30 | 195.86 | 163.68
2017-11-27 09:00 | 197.09 | 163.84
2017-11-27 09:30 | 197.66 | 164.07
2017-11-27 10:00 | 197 | 165.27
2017-11-27 10:30 | 196.6 | 165.7
2017-11-27 11:00 | 215.13 | 190.5
2017-11-27 11:30 | 239.39 | 223.51
2017-11-27 12:00 | 244.26 | 230.18
2017-11-27 12:30 | 246.01 | 232.07
2017-11-27 13:00 | 247.37 | 233.78
2017-11-27 13:30 | 248.58 | 235.36
2017-11-27 14:00 | 249.82 | 236.88
2017-11-27 14:30 | 251.23 | 237.85
2017-11-27 15:00 | 250.19 | 236.71
2017-11-27 15:30 | 251.12 | 237.63
2017-11-27 16:00 | 252.16 | 238.72
2017-11-27 16:30 | 252.77 | 239.38
2017-11-27 17:00 | 252.62 | 239.3
2017-11-27 17:30 | 252.47 | 239
2017-11-27 18:00 | 252.21 | 239.24
2017-11-27 18:30 | 253.03 | 239.7
2017-11-27 19:00 | 254.86 | 242.05
2017-11-27 19:30 | 255.28 | 242.65
2017-11-27 20:00 | 253.49 | 240.71
2017-11-27 20:30 | 251.64 | 238.21
2017-11-27 21:00 | 247.81 | 234.43
2017-11-27 21:30 | 230.59 | 218.92
2017-11-27 22:00 | 183.37 | 170.27
2017-11-27 22:30 | 180.02 | 166.5
2017-11-27 23:00 | 177.7 | 163.33
2017-11-27 23:30 | 176.4 | 162.85
2017-11-28 | 173.84 | 161.17
2017-11-28 00:30 | 172.92 | 160.12
2017-11-28 01:00 | 172.2 | 159.14
2017-11-28 01:30 | 172.82 | 158.64
2017-11-28 02:00 | 173.16 | 158.65
2017-11-28 02:30 | 172.64 | 157.73
2017-11-28 03:00 | 172.32 | 157.37
2017-11-28 03:30 | 172.54 | 157.39
2017-11-28 04:00 | 172.05 | 156.44
2017-11-28 04:30 | 172.97 | 157.65
2017-11-28 05:00 | 173.2 | 157.94
2017-11-28 05:30 | 174.03 | 158.89
2017-11-28 06:00 | 174.2 | 159.37
2017-11-28 06:30 | 176.84 | 161.57
2017-11-28 07:00 | 180.02 | 162.89
2017-11-28 07:30 | 183.15 | 164.59
2017-11-28 08:00 | 183.36 | 165.3
2017-11-28 08:30 | 181.26 | 165.11
2017-11-28 09:00 | 181.66 | 165.38
2017-11-28 09:30 | 181.3 | 164.97
2017-11-28 10:00 | 181.72 | 165.4
2017-11-28 10:30 | 182.64 | 166.14
2017-11-28 11:00 | 183.27 | 166.36
2017-11-28 11:30 | 184.53 | 167.97
2017-11-28 12:00 | 217.52 | 203.43
2017-11-28 12:30 | 244.36 | 230.63
2017-11-28 13:00 | 244.45 | 230.66
2017-11-28 13:30 | 246.03 | 232.11
2017-11-28 14:00 | 246.66 | 232.07
2017-11-28 14:30 | 246.3 | 232.7
2017-11-28 15:00 | 246.43 | 233.07
2017-11-28 15:30 | 246.52 | 233.32
2017-11-28 16:00 | 247.53 | 234.51
2017-11-28 16:30 | 247.76 | 234.74
2017-11-28 17:00 | 247.8 | 234.54
2017-11-28 17:30 | 247.53 | 234.11
2017-11-28 18:00 | 248.39 | 234.95
2017-11-28 18:30 | 249.38 | 236
2017-11-28 19:00 | 250.69 | 237.76
2017-11-28 19:30 | 250.56 | 237.99
2017-11-28 20:00 | 248.98 | 236.5
2017-11-28 20:30 | 247.59 | 234.92
2017-11-28 21:00 | 245.28 | 232.33
2017-11-28 21:30 | 211.52 | 199.33
2017-11-28 22:00 | 182.06 | 168.56
2017-11-28 22:30 | 180.27 | 166.57
2017-11-28 23:00 | 177.7 | 163.95
2017-11-28 23:30 | 177.38 | 163.36
2017-11-29 | 176.93 | 162.45
2017-11-29 00:30 | 174.92 | 160.87
2017-11-29 01:00 | 173.54 | 159.47
2017-11-29 01:30 | 173.21 | 159.43
2017-11-29 02:00 | 172.42 | 158.75
2017-11-29 02:30 | 172.07 | 158.5
2017-11-29 03:00 | 171.78 | 158.1
2017-11-29 03:30 | 171.86 | 157.87
2017-11-29 04:00 | 169.98 | 156.01
2017-11-29 04:30 | 169.7 | 155.89
2017-11-29 05:00 | 170.31 | 156.26
2017-11-29 05:30 | 171.51 | 157.21
2017-11-29 06:00 | 173.07 | 159.06
2017-11-29 06:30 | 174.91 | 159.91
2017-11-29 07:00 | 176.57 | 161.47
2017-11-29 07:30 | 178.16 | 162.69
2017-11-29 08:00 | 178.82 | 163.48
2017-11-29 08:30 | 209.4 | 196.08
2017-11-29 09:00 | 227.02 | 214.12
2017-11-29 09:30 | 227.84 | 214.95
2017-11-29 10:00 | 228.71 | 215.92
2017-11-29 10:30 | 229.88 | 216.65
2017-11-29 11:00 | 246.94 | 231.59
2017-11-29 11:30 | 231.33 | 218.19
2017-11-29 12:00 | 232.1 | 219.06
2017-11-29 12:30 | 233.29 | 220.23
2017-11-29 13:00 | 234.37 | 221.39
2017-11-29 13:30 | 234.15 | 221.66
2017-11-29 14:00 | 235.46 | 221.96
2017-11-29 14:30 | 235.59 | 221.65
2017-11-29 15:00 | 241.35 | 227.49
2017-11-29 15:30 | 245.59 | 231.66
2017-11-29 16:00 | 247.6 | 233.33
2017-11-29 16:30 | 248.34 | 234.27
2017-11-29 17:00 | 248.32 | 234.25
2017-11-29 17:30 | 249.7 | 235.34
2017-11-29 18:00 | 250.63 | 236.56
2017-11-29 18:30 | 251.62 | 237.88
2017-11-29 19:00 | 252.05 | 238.29
2017-11-29 19:30 | 252.19 | 238.52
2017-11-29 20:00 | 250.95 | 237.06
2017-11-29 20:30 | 249.62 | 235.28
2017-11-29 21:00 | 248.06 | 233.08
2017-11-29 21:30 | 244 | 230.63
2017-11-29 22:00 | 209.77 | 196.07
2017-11-29 22:30 | 181.65 | 166.98
2017-11-29 23:00 | 179.53 | 164.11
2017-11-29 23:30 | 178.48 | 162.9
2017-11-30 | 177.23 | 161.39
2017-11-30 00:30 | 176.35 | 161.01
2017-11-30 01:00 | 174.88 | 159.97
2017-11-30 01:30 | 174.19 | 159.1
2017-11-30 02:00 | 173.93 | 158.55
2017-11-30 02:30 | 173.67 | 158.09
2017-11-30 03:00 | 173.21 | 157.65
2017-11-30 03:30 | 173.28 | 157.48
2017-11-30 04:00 | 174.14 | 156.46
2017-11-30 04:30 | 175.35 | 157.86
2017-11-30 05:00 | 176.31 | 159.11
2017-11-30 05:30 | 176.53 | 159.39
2017-11-30 06:00 | 178.9 | 161.47
2017-11-30 06:30 | 180.51 | 163.25
2017-11-30 07:00 | 181.93 | 163.95
2017-11-30 07:30 | 183.51 | 165.21
2017-11-30 08:00 | 184.16 | 165.6
2017-11-30 08:30 | 184.18 | 166.08
2017-11-30 09:00 | 184.39 | 165.95
2017-11-30 09:30 | 183.35 | 164.76
2017-11-30 10:00 | 185.13 | 166.92
2017-11-30 10:30 | 185.07 | 166.58
2017-11-30 11:00 | 185.43 | 166.87
2017-11-30 11:30 | 186.51 | 168.24
2017-11-30 12:00 | 187.49 | 169.49
2017-11-30 12:30 | 188.34 | 170.73
2017-11-30 13:00 | 209.5 | 194
2017-11-30 13:30 | 242.86 | 228.22
2017-11-30 14:00 | 247.5 | 233.67
2017-11-30 14:30 | 248.14 | 234.72
2017-11-30 15:00 | 247.2 | 233.39
2017-11-30 15:30 | 248.3 | 233.88
2017-11-30 16:00 | 249.69 | 235.26
2017-11-30 16:30 | 251.14 | 236.34
2017-11-30 17:00 | 251.29 | 236.31
2017-11-30 17:30 | 252.14 | 236.69
2017-11-30 18:00 | 253.82 | 238.56
2017-11-30 18:30 | 254.44 | 239.02
2017-11-30 19:00 | 255.77 | 240.63
2017-11-30 19:30 | 255.09 | 239.88
2017-11-30 20:00 | 253.89 | 238.56
2017-11-30 20:30 | 252.3 | 236.56
2017-11-30 21:00 | 250 | 234.06
2017-11-30 21:30 | 246.39 | 232.33
2017-11-30 22:00 | 243.81 | 229.9
2017-11-30 22:30 | 241.89 | 227.74
2017-11-30 23:00 | 224.77 | 209.79
2017-11-30 23:30 | 190.53 | 175.11
2017-12-01 | 176.98 | 162.36
2017-12-01 00:30 | 176.68 | 161.73
2017-12-01 01:00 | 175.71 | 161.14
2017-12-01 01:30 | 174.56 | 159.76
2017-12-01 02:00 | 174.13 | 159.25
2017-12-01 02:30 | 173.22 | 158.65
2017-12-01 03:00 | 173.38 | 158.69
2017-12-01 03:30 | 173.26 | 158.25
2017-12-01 04:00 | 173.27 | 158.43
2017-12-01 04:30 | 173.2 | 158.84
2017-12-01 05:00 | 174.07 | 159.6
2017-12-01 05:30 | 175.7 | 161.76
2017-12-01 06:00 | 176.69 | 162.55
2017-12-01 06:30 | 177.94 | 163.72
2017-12-01 07:00 | 207.47 | 194.29
2017-12-01 07:30 | 203.19 | 192.16
2017-12-01 08:00 | 187.65 | 178.76
2017-12-01 08:30 | 176.86 | 168.45
2017-12-01 09:00 | 167.07 | 158.83
2017-12-01 09:30 | 169.04 | 161.17
2017-12-01 10:00 | 168.53 | 161.02
2017-12-01 10:30 | 172.52 | 164.29
2017-12-01 11:00 | 201.58 | 194.04
2017-12-01 11:30 | 173.62 | 165.39
2017-12-01 12:00 | 188.02 | 179.25
2017-12-01 12:30 | 210.62 | 201.85
2017-12-01 13:00 | 226.94 | 218.17
2017-12-01 13:30 | 224.66 | 216.05
2017-12-01 14:00 | 229.78 | 221.22
2017-12-01 14:30 | 235.77 | 227.5
2017-12-01 15:00 | 242.52 | 234.7
2017-12-01 15:30 | 244.15 | 236.38
2017-12-01 16:00 | 245.25 | 237.37
2017-12-01 16:30 | 246.13 | 238.24
2017-12-01 17:00 | 246.46 | 238.41
2017-12-01 17:30 | 246.03 | 237.39
2017-12-01 18:00 | 246.13 | 237.49
2017-12-01 18:30 | 245.55 | 236.82
2017-12-01 19:00 | 245.91 | 237.4
2017-12-01 19:30 | 246.01 | 237.68
2017-12-01 20:00 | 245.08 | 236.57
2017-12-01 20:30 | 243.54 | 234.46
2017-12-01 21:00 | 242.05 | 232.85
2017-12-01 21:30 | 222.61 | 214.39
2017-12-01 22:00 | 188 | 179.57
2017-12-01 22:30 | 174.15 | 165.31
2017-12-01 23:00 | 173.69 | 164.61
2017-12-01 23:30 | 171.66 | 162.93
2017-12-02 | 170.55 | 162.56
2017-12-02 00:30 | 171.62 | 161.05
2017-12-02 01:00 | 171.5 | 160.45
2017-12-02 01:30 | 170.15 | 159.68
2017-12-02 02:00 | 170.2 | 159.28
2017-12-02 02:30 | 170.27 | 159.47
2017-12-02 03:00 | 169.28 | 158.14
2017-12-02 03:30 | 169.74 | 158.33
2017-12-02 04:00 | 169.89 | 158.66
2017-12-02 04:30 | 169.67 | 158.54
2017-12-02 05:00 | 169.87 | 158.75
2017-12-02 05:30 | 169.57 | 158.81
2017-12-02 06:00 | 170.19 | 159.78
2017-12-02 06:30 | 171.14 | 160.22
2017-12-02 07:00 | 171.59 | 160.99
2017-12-02 07:30 | 172.93 | 161.87
2017-12-02 08:00 | 174.25 | 162.94
2017-12-02 08:30 | 174.49 | 163.06
2017-12-02 09:00 | 174.98 | 162.98
2017-12-02 09:30 | 175.55 | 162.73
2017-12-02 10:00 | 176.02 | 162.53
2017-12-02 10:30 | 175.68 | 161.22
2017-12-02 11:00 | 177.76 | 162.59
2017-12-02 11:30 | 177.86 | 163.45
2017-12-02 12:00 | 175.53 | 163.72
2017-12-02 12:30 | 175.63 | 164.03
2017-12-02 13:00 | 175.89 | 164.68
2017-12-02 13:30 | 174.94 | 164.04
2017-12-02 14:00 | 175.56 | 164.53
2017-12-02 14:30 | 175.43 | 164.39
2017-12-02 15:00 | 175.68 | 164.64
2017-12-02 15:30 | 175.55 | 164.07
2017-12-02 16:00 | 176.03 | 164.44
2017-12-02 16:30 | 176.86 | 165.02
2017-12-02 17:00 | 176.8 | 165.23
2017-12-02 17:30 | 177.62 | 166.18
2017-12-02 18:00 | 177.52 | 165.88
2017-12-02 18:30 | 176.79 | 164.68
2017-12-02 19:00 | 176.96 | 164.85
2017-12-02 19:30 | 176.99 | 164.98
2017-12-02 20:00 | 176.05 | 164.09
2017-12-02 20:30 | 175.95 | 164.22
2017-12-02 21:00 | 176.23 | 164.48
2017-12-02 21:30 | 174.8 | 164.09
2017-12-02 22:00 | 173.75 | 163.06
2017-12-02 22:30 | 171.84 | 161.46
2017-12-02 23:00 | 170.54 | 160.18
2017-12-02 23:30 | 170.26 | 159.75
2017-12-03 | 168.72 | 158.02
2017-12-03 00:30 | 166.93 | 157.26
2017-12-03 01:00 | 166.1 | 156.96
2017-12-03 01:30 | 165.69 | 156.61
2017-12-03 02:00 | 165.37 | 155.99
2017-12-03 02:30 | 165.14 | 155.44
2017-12-03 03:00 | 165.02 | 155.2
2017-12-03 03:30 | 164.1 | 155.02
2017-12-03 04:00 | 163.62 | 154.89
2017-12-03 04:30 | 164.96 | 154.96
2017-12-03 05:00 | 165.91 | 155.88
2017-12-03 05:30 | 165.42 | 155.42
2017-12-03 06:00 | 165.3 | 155.48
2017-12-03 06:30 | 165.51 | 156.13
2017-12-03 07:00 | 165 | 155.99
2017-12-03 07:30 | 165.07 | 155.95
2017-12-03 08:00 | 165.16 | 156.08
2017-12-03 08:30 | 165.08 | 156.14
2017-12-03 09:00 | 165.49 | 156.25
2017-12-03 09:30 | 168.89 | 159.79
2017-12-03 10:00 | 170.1 | 159.73
2017-12-03 10:30 | 170.02 | 159.62
2017-12-03 11:00 | 170.04 | 159.44
2017-12-03 11:30 | 169.9 | 158.93
2017-12-03 12:00 | 171.51 | 160.51
2017-12-03 12:30 | 172.2 | 161.14
2017-12-03 13:00 | 172.74 | 161.59
2017-12-03 13:30 | 173.9 | 162.82
2017-12-03 14:00 | 174.5 | 163.08
2017-12-03 14:30 | 175.49 | 164.24
2017-12-03 15:00 | 175.59 | 164.67
2017-12-03 15:30 | 175.51 | 164.23
2017-12-03 16:00 | 177.92 | 166.88
2017-12-03 16:30 | 178.6 | 167.76
2017-12-03 17:00 | 180.44 | 168.79
2017-12-03 17:30 | 182.07 | 170.35
2017-12-03 18:00 | 183.35 | 171.38
2017-12-03 18:30 | 183.83 | 171.88
2017-12-03 19:00 | 184.37 | 172.73
2017-12-03 19:30 | 184.44 | 172.83
2017-12-03 20:00 | 183.69 | 171.97
2017-12-03 20:30 | 182.66 | 170.52
2017-12-03 21:00 | 181.29 | 168.53
2017-12-03 21:30 | 179.13 | 167.35
2017-12-03 22:00 | 177.11 | 165.27
2017-12-03 22:30 | 176.04 | 163.7
2017-12-03 23:00 | 175.13 | 162.24
2017-12-03 23:30 | 174.43 | 161.48
2017-12-04 | 173.59 | 160.42
2017-12-04 00:30 | 172.06 | 159.52
2017-12-04 01:00 | 170.13 | 158.18
2017-12-04 01:30 | 169.8 | 158.7
2017-12-04 02:00 | 171.99 | 161.05
2017-12-04 02:30 | 171.94 | 161.53
2017-12-04 03:00 | 172.01 | 161.77
2017-12-04 03:30 | 172.04 | 161.74
2017-12-04 04:00 | 172.34 | 162.02
2017-12-04 04:30 | 173.13 | 162.66
2017-12-04 05:00 | 173.95 | 163.11
2017-12-04 05:30 | 174.38 | 164.02
2017-12-04 06:00 | 174.69 | 164.92
2017-12-04 06:30 | 175.58 | 166.2
2017-12-04 07:00 | 179.83 | 168.1
2017-12-04 07:30 | 179.96 | 168.09
2017-12-04 08:00 | 180.37 | 168.51
2017-12-04 08:30 | 179.73 | 168.03
2017-12-04 09:00 | 179.46 | 167.48
2017-12-04 09:30 | 179.34 | 166.94
2017-12-04 10:00 | 179.71 | 167.45
2017-12-04 10:30 | 177.99 | 166.8
2017-12-04 11:00 | 174.9 | 164.46
2017-12-04 11:30 | 200.87 | 191.6
2017-12-04 12:00 | 212.21 | 203
2017-12-04 12:30 | 229.02 | 220.26
2017-12-04 13:00 | 232.76 | 224.76
2017-12-04 13:30 | 231.84 | 223.65
2017-12-04 14:00 | 232.07 | 224.06
2017-12-04 14:30 | 232.23 | 224.21
2017-12-04 15:00 | 231.89 | 223.89
2017-12-04 15:30 | 232.24 | 224.12
2017-12-04 16:00 | 233.3 | 225.09
2017-12-04 16:30 | 234.27 | 225.97
2017-12-04 17:00 | 234.83 | 226.45
2017-12-04 17:30 | 235.64 | 227.11
2017-12-04 18:00 | 236.49 | 228.25
2017-12-04 18:30 | 238.18 | 229.94
2017-12-04 19:00 | 239.47 | 231.36
2017-12-04 19:30 | 239.82 | 231.74
2017-12-04 20:00 | 222.12 | 213.91
2017-12-04 20:30 | 215.85 | 207.45
2017-12-04 21:00 | 214.71 | 206.2
2017-12-04 21:30 | 184.55 | 176.91
2017-12-04 22:00 | 169.79 | 162.19
2017-12-04 22:30 | 167.89 | 160.14
2017-12-04 23:00 | 166.63 | 158.58
2017-12-04 23:30 | 166.1 | 158.4
2017-12-05 | 167.61 | 157.51
2017-12-05 00:30 | 165.69 | 156.58
2017-12-05 01:00 | 164.32 | 155.69
2017-12-05 01:30 | 164.48 | 155.71
2017-12-05 02:00 | 164.4 | 155.05
2017-12-05 02:30 | 164.51 | 154.62
2017-12-05 03:00 | 164.19 | 154.34
2017-12-05 03:30 | 163.73 | 154.15
2017-12-05 04:00 | 162.43 | 152.79
2017-12-05 04:30 | 163.09 | 153.41
2017-12-05 05:00 | 163.96 | 154.33
2017-12-05 05:30 | 165.07 | 155.73
2017-12-05 06:00 | 164.79 | 156.08
2017-12-05 06:30 | 167.6 | 157.99
2017-12-05 07:00 | 170.27 | 157.62
2017-12-05 07:30 | 170.28 | 157.9
2017-12-05 08:00 | 170.83 | 158.4
2017-12-05 08:30 | 170.9 | 157.65
2017-12-05 09:00 | 170.02 | 156.5
2017-12-05 09:30 | 170.13 | 156.83
2017-12-05 10:00 | 169.33 | 156.47
2017-12-05 10:30 | 169.26 | 156.3
2017-12-05 11:00 | 168.88 | 156.09
2017-12-05 11:30 | 169.81 | 156.87
2017-12-05 12:00 | 173.64 | 158.03
2017-12-05 12:30 | 173.52 | 157.69
2017-12-05 13:00 | 174.62 | 158.39
2017-12-05 13:30 | 176.09 | 159.94
2017-12-05 14:00 | 208.28 | 193.96
2017-12-05 14:30 | 234.65 | 220.96
2017-12-05 15:00 | 239.3 | 225.47
2017-12-05 15:30 | 238.58 | 224.23
2017-12-05 16:00 | 238.53 | 224.06
2017-12-05 16:30 | 240.01 | 225.5
2017-12-05 17:00 | 241.13 | 226.8
2017-12-05 17:30 | 242.59 | 227.82
2017-12-05 18:00 | 244.29 | 229.3
2017-12-05 18:30 | 245.48 | 230.53
2017-12-05 19:00 | 246.16 | 231.6
2017-12-05 19:30 | 247.22 | 232.77
2017-12-05 20:00 | 247.16 | 232.71
2017-12-05 20:30 | 245.73 | 231.04
2017-12-05 21:00 | 244.56 | 229.62
2017-12-05 21:30 | 241.67 | 227.91
2017-12-05 22:00 | 240.41 | 226.63
2017-12-05 22:30 | 238.97 | 224.79
2017-12-05 23:00 | 237.89 | 223.08
2017-12-05 23:30 | 219.98 | 205.19
2017-12-06 | 186.46 | 170.24
2017-12-06 00:30 | 168.44 | 154.86
2017-12-06 01:00 | 166.71 | 153.72
2017-12-06 01:30 | 183.26 | 171.42
2017-12-06 02:00 | 196.16 | 185.06
2017-12-06 02:30 | 196.87 | 186.01
2017-12-06 03:00 | 195.32 | 186.47
2017-12-06 03:30 | 193.38 | 185.82
2017-12-06 04:00 | 192.12 | 183.89
2017-12-06 04:30 | 194.71 | 183.98
2017-12-06 05:00 | 197.04 | 185.17
2017-12-06 05:30 | 195.56 | 187
2017-12-06 06:00 | 195.55 | 187.9
2017-12-06 06:30 | 194.9 | 187.51
2017-12-06 07:00 | 192 | 183.05
2017-12-06 07:30 | 187.49 | 174.79
2017-12-06 08:00 | 188.09 | 171.68
2017-12-06 08:30 | 186.23 | 169.22
2017-12-06 09:00 | 179.91 | 161.49
2017-12-06 09:30 | 174.61 | 158.45
2017-12-06 10:00 | 173.16 | 156.57
2017-12-06 10:30 | 175.46 | 157.46
2017-12-06 11:00 | 175.53 | 157.48
2017-12-06 11:30 | 175.38 | 157.49
2017-12-06 12:00 | 176.13 | 158.4
2017-12-06 12:30 | 177.21 | 158.82
2017-12-06 13:00 | 177.82 | 158.85
2017-12-06 13:30 | 178.44 | 159.8
2017-12-06 14:00 | 178.92 | 160.45
2017-12-06 14:30 | 181.32 | 162.66
2017-12-06 15:00 | 181.79 | 163
2017-12-06 15:30 | 208.84 | 191.44
2017-12-06 16:00 | 220.48 | 203.27
2017-12-06 16:30 | 222.5 | 205.07
2017-12-06 17:00 | 223.77 | 206.4
2017-12-06 17:30 | 224.81 | 207.19
2017-12-06 18:00 | 226.35 | 209.56
2017-12-06 18:30 | 226.53 | 209.9
2017-12-06 19:00 | 226.84 | 210.43
2017-12-06 19:30 | 227 | 210.62
2017-12-06 20:00 | 225.86 | 209.39
2017-12-06 20:30 | 225.35 | 208.43
2017-12-06 21:00 | 224.43 | 207.1
2017-12-06 21:30 | 193.37 | 175.84
2017-12-06 22:00 | 181.23 | 163.06
2017-12-06 22:30 | 179.82 | 160.97
2017-12-06 23:00 | 178.69 | 159.29
2017-12-06 23:30 | 178.66 | 158.34
2017-12-07 | 177.55 | 157.21
2017-12-07 00:30 | 175.54 | 156.37
2017-12-07 01:00 | 173.42 | 155.45
2017-12-07 01:30 | 161.1 | 143.68
2017-12-07 02:00 | 151.32 | 133.98
2017-12-07 02:30 | 150.48 | 133.32
2017-12-07 03:00 | 149.77 | 132.67
2017-12-07 03:30 | 151.97 | 134.64
2017-12-07 04:00 | 161.55 | 144.2
2017-12-07 04:30 | 162.26 | 144.96
2017-12-07 05:00 | 160.96 | 143.46
2017-12-07 05:30 | 161.98 | 144.69
2017-12-07 06:00 | 162.67 | 145.82
2017-12-07 06:30 | 163.9 | 146.86
2017-12-07 07:00 | 164.74 | 147.28
2017-12-07 07:30 | 167.49 | 148.92
2017-12-07 08:00 | 169.5 | 150.48
2017-12-07 08:30 | 168.79 | 150.89
2017-12-07 09:00 | 165.72 | 149.89
2017-12-07 09:30 | 165.22 | 149.47
2017-12-07 10:00 | 165.86 | 150.29
2017-12-07 10:30 | 167.77 | 151.91
2017-12-07 11:00 | 167.77 | 152.23
2017-12-07 11:30 | 168.45 | 153.2
2017-12-07 12:00 | 163.61 | 148.35
2017-12-07 12:30 | 160.82 | 145.23
2017-12-07 13:00 | 162.59 | 146.94
2017-12-07 13:30 | 191.05 | 176.82
2017-12-07 14:00 | 224.93 | 211.73
2017-12-07 14:30 | 241.21 | 227.78
2017-12-07 15:00 | 246.58 | 232.45
2017-12-07 15:30 | 248.2 | 234.18
2017-12-07 16:00 | 250.46 | 236.69
2017-12-07 16:30 | 253.24 | 239.63
2017-12-07 17:00 | 253.34 | 239.51
2017-12-07 17:30 | 252.26 | 238.48
2017-12-07 18:00 | 253.1 | 239.27
2017-12-07 18:30 | 253.52 | 239.55
2017-12-07 19:00 | 255.71 | 241.76
2017-12-07 19:30 | 254.98 | 240.93
2017-12-07 20:00 | 253.69 | 239.46
2017-12-07 20:30 | 235.77 | 220.9
2017-12-07 21:00 | 198.62 | 182.24
2017-12-07 21:30 | 186.6 | 171.71
2017-12-07 22:00 | 183.76 | 168.85
2017-12-07 22:30 | 182.39 | 166.84
2017-12-07 23:00 | 180.91 | 165.26
2017-12-07 23:30 | 180.28 | 165.05
2017-12-08 | 178.78 | 163.35
2017-12-08 00:30 | 178.5 | 163.03
2017-12-08 01:00 | 177.19 | 162.25
2017-12-08 01:30 | 175.83 | 160.79
2017-12-08 02:00 | 175.53 | 160.61
2017-12-08 02:30 | 175.11 | 159.84
2017-12-08 03:00 | 174.26 | 159.43
2017-12-08 03:30 | 174.36 | 159.78
2017-12-08 04:00 | 174.01 | 159.06
2017-12-08 04:30 | 174.75 | 159.53
2017-12-08 05:00 | 175.78 | 160.54
2017-12-08 05:30 | 176.41 | 161.52
2017-12-08 06:00 | 177.06 | 162.52
2017-12-08 06:30 | 178.66 | 163.96
2017-12-08 07:00 | 179.13 | 165.13
2017-12-08 07:30 | 180.48 | 165.71
2017-12-08 08:00 | 181.67 | 166.62
2017-12-08 08:30 | 178.52 | 166.83
2017-12-08 09:00 | 177.96 | 167.24
2017-12-08 09:30 | 179.16 | 167.89
2017-12-08 10:00 | 209.66 | 198.84
2017-12-08 10:30 | 235.99 | 225.3
2017-12-08 11:00 | 240.29 | 229.69
2017-12-08 11:30 | 241.86 | 231.25
2017-12-08 12:00 | 243.39 | 232.67
2017-12-08 12:30 | 245.13 | 233.79
2017-12-08 13:00 | 245.91 | 234.35
2017-12-08 13:30 | 247.74 | 236.29
2017-12-08 14:00 | 250.95 | 239.84
2017-12-08 14:30 | 249.54 | 238.33
2017-12-08 15:00 | 250 | 238.85
2017-12-08 15:30 | 250.94 | 239.93
2017-12-08 16:00 | 249.69 | 239.01
2017-12-08 16:30 | 250.96 | 240.27
2017-12-08 17:00 | 251.62 | 240.97
2017-12-08 17:30 | 251.09 | 240.34
2017-12-08 18:00 | 251.74 | 241.06
2017-12-08 18:30 | 252.19 | 241.71
2017-12-08 19:00 | 252.87 | 242.5
2017-12-08 19:30 | 252.7 | 242.49
2017-12-08 20:00 | 251.1 | 241.07
2017-12-08 20:30 | 249.46 | 238.86
2017-12-08 21:00 | 247.93 | 237.13
2017-12-08 21:30 | 245.1 | 235.37
2017-12-08 22:00 | 226.31 | 216.72
2017-12-08 22:30 | 191.09 | 180.61
2017-12-08 23:00 | 178.47 | 167
2017-12-08 23:30 | 177.71 | 165.91
2017-12-09 | 176.66 | 164.8
2017-12-09 00:30 | 174.68 | 163.43
2017-12-09 01:00 | 174.07 | 163.16
2017-12-09 01:30 | 172.93 | 161.87
2017-12-09 02:00 | 172.9 | 161.79
2017-12-09 02:30 | 172.26 | 161.33
2017-12-09 03:00 | 170.6 | 160.96
2017-12-09 03:30 | 169.83 | 160.5
2017-12-09 04:00 | 169.38 | 160.3
2017-12-09 04:30 | 169.62 | 160.41
2017-12-09 05:00 | 169.62 | 160.43
2017-12-09 05:30 | 170.22 | 160.87
2017-12-09 06:00 | 170.15 | 160.91
2017-12-09 06:30 | 170.55 | 161.6
2017-12-09 07:00 | 170.76 | 161.72
2017-12-09 07:30 | 171.19 | 162.2
2017-12-09 08:00 | 171.59 | 161.6
2017-12-09 08:30 | 172.92 | 162.8
2017-12-09 09:00 | 174.17 | 163.61
2017-12-09 09:30 | 174.13 | 163.65
2017-12-09 10:00 | 175.66 | 164.9
2017-12-09 10:30 | 175.91 | 164.87
2017-12-09 11:00 | 176.58 | 165.59
2017-12-09 11:30 | 178.14 | 166.99
2017-12-09 12:00 | 208.85 | 198.34
2017-12-09 12:30 | 218.38 | 208.01
2017-12-09 13:00 | 235.98 | 225.78
2017-12-09 13:30 | 242.47 | 232.34
2017-12-09 14:00 | 243.83 | 233.81
2017-12-09 14:30 | 244.82 | 234.9
2017-12-09 15:00 | 244.72 | 234.7
2017-12-09 15:30 | 245.17 | 235.11
2017-12-09 16:00 | 246.47 | 236.02
2017-12-09 16:30 | 248.2 | 237.8
2017-12-09 17:00 | 248.89 | 238.63
2017-12-09 17:30 | 250.15 | 239.98
2017-12-09 18:00 | 251.15 | 241.01
2017-12-09 18:30 | 249.86 | 239.56
2017-12-09 19:00 | 249.69 | 239.32
2017-12-09 19:30 | 249.97 | 239.68
2017-12-09 20:00 | 248.86 | 238.52
2017-12-09 20:30 | 247.34 | 236.75
2017-12-09 21:00 | 245.9 | 235.3
2017-12-09 21:30 | 243.44 | 233.82
2017-12-09 22:00 | 241.13 | 232
2017-12-09 22:30 | 239.21 | 229.89
2017-12-09 23:00 | 237.17 | 227.46
2017-12-09 23:30 | 219.62 | 209.82
2017-12-10 | 185.3 | 175.68
2017-12-10 00:30 | 171.63 | 162.36
2017-12-10 01:00 | 170.75 | 161.76
2017-12-10 01:30 | 169.98 | 160.81
2017-12-10 02:00 | 168.93 | 160.39
2017-12-10 02:30 | 167.78 | 159.63
2017-12-10 03:00 | 167.77 | 159.49
2017-12-10 03:30 | 167.46 | 159.12
2017-12-10 04:00 | 167.26 | 159.02
2017-12-10 04:30 | 167.6 | 159.19
2017-12-10 05:00 | 167.59 | 158.89
2017-12-10 05:30 | 167.08 | 159.11
2017-12-10 06:00 | 168.05 | 159.71
2017-12-10 06:30 | 169.37 | 160.3
2017-12-10 07:00 | 170.02 | 161.02
2017-12-10 07:30 | 171.04 | 161.93
2017-12-10 08:00 | 171.81 | 162.53
2017-12-10 08:30 | 172.58 | 162.72
2017-12-10 09:00 | 173.22 | 163.42
2017-12-10 09:30 | 173.64 | 163.8
2017-12-10 10:00 | 175.12 | 165.33
2017-12-10 10:30 | 176.4 | 166.62
2017-12-10 11:00 | 176.75 | 167.37
2017-12-10 11:30 | 178.93 | 169.53
2017-12-10 12:00 | 180.08 | 170.66
2017-12-10 12:30 | 182.08 | 172.92
2017-12-10 13:00 | 182.84 | 173.94
2017-12-10 13:30 | 184.25 | 175.09
2017-12-10 14:00 | 213.91 | 205.09
2017-12-10 14:30 | 240.51 | 231.65
2017-12-10 15:00 | 246.88 | 238.09
2017-12-10 15:30 | 248.25 | 239.55
2017-12-10 16:00 | 243 | 233.69
2017-12-10 16:30 | 243.62 | 234.72
2017-12-10 17:00 | 246.33 | 237.7
2017-12-10 17:30 | 251.3 | 243.2
2017-12-10 18:00 | 251.93 | 243.99
2017-12-10 18:30 | 251.83 | 244.04
2017-12-10 19:00 | 251.89 | 244.15
2017-12-10 19:30 | 252.08 | 244.45
2017-12-10 20:00 | 250.87 | 242.89
2017-12-10 20:30 | 249.31 | 240.65
2017-12-10 21:00 | 247.37 | 238.08
2017-12-10 21:30 | 244.97 | 235.67
2017-12-10 22:00 | 242.77 | 233.03
2017-12-10 22:30 | 241.11 | 230.98
2017-12-10 23:00 | 240.14 | 229.66
2017-12-10 23:30 | 239.11 | 228.8
2017-12-11 | 220.75 | 211.21
2017-12-11 00:30 | 183.7 | 174.15
2017-12-11 01:00 | 172.1 | 162.8
2017-12-11 01:30 | 171.35 | 162.26
2017-12-11 02:00 | 171.35 | 161.96
2017-12-11 02:30 | 170.31 | 160.36
2017-12-11 03:00 | 169.95 | 160.09
2017-12-11 03:30 | 170.22 | 160.42
2017-12-11 04:00 | 169.85 | 159.98
2017-12-11 04:30 | 202.13 | 192.89
2017-12-11 05:00 | 213.01 | 203.72
2017-12-11 05:30 | 214.15 | 205.26
2017-12-11 06:00 | 215.22 | 206.16
2017-12-11 06:30 | 217.37 | 208.13
2017-12-11 07:00 | 236.17 | 225.31
2017-12-11 07:30 | 241.22 | 231.47
2017-12-11 08:00 | 241.3 | 230.91
2017-12-11 08:30 | 240.89 | 230.69
2017-12-11 09:00 | 241.07 | 231.05
2017-12-11 09:30 | 241.37 | 231.27
2017-12-11 10:00 | 242.25 | 232
2017-12-11 10:30 | 242.31 | 232.28
2017-12-11 11:00 | 243.08 | 233.47
2017-12-11 11:30 | 243.86 | 234.83
2017-12-11 12:00 | 244.52 | 235.6
2017-12-11 12:30 | 244.43 | 235.86
2017-12-11 13:00 | 246.28 | 237.72
2017-12-11 13:30 | 248.51 | 239.86
2017-12-11 14:00 | 248.89 | 240.67
2017-12-11 14:30 | 249.02 | 241.16
2017-12-11 15:00 | 249.58 | 241.41
2017-12-11 15:30 | 249.8 | 241.7
2017-12-11 16:00 | 251.69 | 243.49
2017-12-11 16:30 | 253.04 | 244.82
2017-12-11 17:00 | 253.41 | 245.14
2017-12-11 17:30 | 254.16 | 246.09
2017-12-11 18:00 | 254.31 | 246.7
2017-12-11 18:30 | 254.92 | 247.16
2017-12-11 19:00 | 255.42 | 247.84
2017-12-11 19:30 | 255.48 | 247.96
2017-12-11 20:00 | 254.45 | 246.78
2017-12-11 20:30 | 252.18 | 244.01
2017-12-11 21:00 | 250.47 | 241.6
2017-12-11 21:30 | 230.69 | 221.99
2017-12-11 22:00 | 195.61 | 186.17
2017-12-11 22:30 | 179.96 | 169.86
2017-12-11 23:00 | 178.55 | 168.2
2017-12-11 23:30 | 176.95 | 166.58
2017-12-12 | 175.28 | 164.73
2017-12-12 00:30 | 174.41 | 163.96
2017-12-12 01:00 | 172.99 | 163.23
2017-12-12 01:30 | 172.24 | 162.27
2017-12-12 02:00 | 172.01 | 162.16
2017-12-12 02:30 | 170.54 | 161.16
2017-12-12 03:00 | 170.55 | 161.43
2017-12-12 03:30 | 170.5 | 161.16
2017-12-12 04:00 | 170.16 | 160.87
2017-12-12 04:30 | 170.7 | 161.28
2017-12-12 05:00 | 171.4 | 162.09
2017-12-12 05:30 | 172.69 | 163.55
2017-12-12 06:00 | 172.84 | 164.2
2017-12-12 06:30 | 175.1 | 165.55
2017-12-12 07:00 | 176.11 | 166.54
2017-12-12 07:30 | 207.03 | 197.89
2017-12-12 08:00 | 234.96 | 225.57
2017-12-12 08:30 | 240.95 | 231
2017-12-12 09:00 | 241.03 | 231.23
2017-12-12 09:30 | 241.26 | 231.39
2017-12-12 10:00 | 242.12 | 232.16
2017-12-12 10:30 | 242.74 | 232.96
2017-12-12 11:00 | 243.87 | 234.46
2017-12-12 11:30 | 244.6 | 235.58
2017-12-12 12:00 | 245.11 | 236.47
2017-12-12 12:30 | 247.01 | 238.48
2017-12-12 13:00 | 246.85 | 238.62
2017-12-12 13:30 | 248.24 | 239.7
2017-12-12 14:00 | 248.69 | 240.22
2017-12-12 14:30 | 249.5 | 241.32
2017-12-12 15:00 | 250.47 | 241.89
2017-12-12 15:30 | 251.58 | 243.42
2017-12-12 16:00 | 253.04 | 244.28
2017-12-12 16:30 | 255.04 | 245.44
2017-12-12 17:00 | 256.03 | 246.56
2017-12-12 17:30 | 257.27 | 247.64
2017-12-12 18:00 | 257.52 | 248.02
2017-12-12 18:30 | 256.32 | 248.76
2017-12-12 19:00 | 256.29 | 248.77
2017-12-12 19:30 | 256.22 | 248.48
2017-12-12 20:00 | 254.91 | 247.21
2017-12-12 20:30 | 252.55 | 244.47
2017-12-12 21:00 | 250.35 | 241.78
2017-12-12 21:30 | 230.64 | 223.31
2017-12-12 22:00 | 194.99 | 187.09
2017-12-12 22:30 | 181.06 | 171.96
2017-12-12 23:00 | 179.05 | 169.6
2017-12-12 23:30 | 177.84 | 168.29
2017-12-13 | 174.85 | 166.03
2017-12-13 00:30 | 173.82 | 165.2
2017-12-13 01:00 | 173.03 | 164.25
2017-12-13 01:30 | 172.23 | 163.6
2017-12-13 02:00 | 171.61 | 163.11
2017-12-13 02:30 | 171.8 | 162.46
2017-12-13 03:00 | 171.49 | 162.22
2017-12-13 03:30 | 170.46 | 161.85
2017-12-13 04:00 | 170.29 | 161.89
2017-12-13 04:30 | 170.81 | 162.16
2017-12-13 05:00 | 170.74 | 162.8
2017-12-13 05:30 | 170.8 | 163.35
2017-12-13 06:00 | 171.82 | 164.93
2017-12-13 06:30 | 174.09 | 166.74
2017-12-13 07:00 | 175.07 | 167.84
2017-12-13 07:30 | 205.31 | 198.42
2017-12-13 08:00 | 233.17 | 225.91
2017-12-13 08:30 | 239.05 | 231.85
2017-12-13 09:00 | 238.91 | 231.53
2017-12-13 09:30 | 239.08 | 231.87
2017-12-13 10:00 | 239.52 | 232.51
2017-12-13 10:30 | 239.26 | 232.64
2017-12-13 11:00 | 239.63 | 233.37
2017-12-13 11:30 | 240.4 | 233.84
2017-12-13 12:00 | 241.53 | 235.16
2017-12-13 12:30 | 242.7 | 236.83
2017-12-13 13:00 | 243.05 | 237.44
2017-12-13 13:30 | 244.93 | 239.24
2017-12-13 14:00 | 246.1 | 240.49
2017-12-13 14:30 | 246.35 | 241.24
2017-12-13 15:00 | 245.9 | 240.93
2017-12-13 15:30 | 247.81 | 242.3
2017-12-13 16:00 | 249.53 | 244.01
2017-12-13 16:30 | 250.59 | 244.89
2017-12-13 17:00 | 251.86 | 245.75
2017-12-13 17:30 | 253.54 | 247.31
2017-12-13 18:00 | 254.81 | 248.67
2017-12-13 18:30 | 255.42 | 249.07
2017-12-13 19:00 | 255.59 | 249.29
2017-12-13 19:30 | 255.71 | 249.34
2017-12-13 20:00 | 254.08 | 247.68
2017-12-13 20:30 | 251.61 | 244.77
2017-12-13 21:00 | 250.13 | 242.66
2017-12-13 21:30 | 231.66 | 224.27
2017-12-13 22:00 | 195.88 | 188.24
2017-12-13 22:30 | 180.69 | 172.44
2017-12-13 23:00 | 179.31 | 170.85
2017-12-13 23:30 | 177.44 | 168.81
2017-12-14 | 175.29 | 166.86
2017-12-14 00:30 | 173.18 | 165.54
2017-12-14 01:00 | 172.17 | 164.85
2017-12-14 01:30 | 171.15 | 163.71
2017-12-14 02:00 | 171.58 | 164.17
2017-12-14 02:30 | 174.08 | 166.43
2017-12-14 03:00 | 173.58 | 166.1
2017-12-14 03:30 | 173.06 | 165.6
2017-12-14 04:00 | 172.9 | 165.35
2017-12-14 04:30 | 172.98 | 165.49
2017-12-14 05:00 | 174.19 | 166.65
2017-12-14 05:30 | 174.98 | 167.37
2017-12-14 06:00 | 175.87 | 168.5
2017-12-14 06:30 | 176.62 | 169.63
2017-12-14 07:00 | 177.5 | 171.11
2017-12-14 07:30 | 179.12 | 172.37
2017-12-14 08:00 | 180.41 | 173.39
2017-12-14 08:30 | 182.05 | 175.02
2017-12-14 09:00 | 181.62 | 174.81
2017-12-14 09:30 | 181.04 | 174.38
2017-12-14 10:00 | 183.54 | 177.36
2017-12-14 10:30 | 188.88 | 183.35
2017-12-14 11:00 | 189.44 | 183.93
2017-12-14 11:30 | 217.55 | 211.23
2017-12-14 12:00 | 244.68 | 238.34
2017-12-14 12:30 | 249.89 | 243.23
2017-12-14 13:00 | 251.62 | 244.79
2017-12-14 13:30 | 252.52 | 245.85
2017-12-14 14:00 | 254 | 247.53
2017-12-14 14:30 | 238.5 | 232.46
2017-12-14 15:00 | 223.21 | 217.29
2017-12-14 15:30 | 224.05 | 218.15
2017-12-14 16:00 | 226.23 | 220.26
2017-12-14 16:30 | 228.12 | 222
2017-12-14 17:00 | 229.25 | 223.05
2017-12-14 17:30 | 229.53 | 223.3
2017-12-14 18:00 | 230.48 | 224.18
2017-12-14 18:30 | 230.53 | 224.17
2017-12-14 19:00 | 229.94 | 223.6
2017-12-14 19:30 | 229.29 | 223.02
2017-12-14 20:00 | 227 | 220.86
2017-12-14 20:30 | 224.19 | 217.98
2017-12-14 21:00 | 221.36 | 215.02
2017-12-14 21:30 | 211.04 | 204.99
2017-12-14 22:00 | 199.51 | 192.42
2017-12-14 22:30 | 184.42 | 177.21
2017-12-14 23:00 | 183.13 | 175.38
2017-12-14 23:30 | 181.31 | 173.85
2017-12-15 | 178.65 | 171.67
2017-12-15 00:30 | 177.36 | 171.03
2017-12-15 01:00 | 176.41 | 170.24
2017-12-15 01:30 | 177.44 | 169.31
2017-12-15 02:00 | 176.9 | 168.4
2017-12-15 02:30 | 176.1 | 167.58
2017-12-15 03:00 | 175.45 | 166.89
2017-12-15 03:30 | 174.93 | 166.5
2017-12-15 04:00 | 174.96 | 166.53
2017-12-15 04:30 | 175.82 | 167.22
2017-12-15 05:00 | 176.22 | 167.44
2017-12-15 05:30 | 176.74 | 167.88
2017-12-15 06:00 | 178.03 | 169.1
2017-12-15 06:30 | 180 | 170.68
2017-12-15 07:00 | 181.89 | 171.35
2017-12-15 07:30 | 212.62 | 202.62
2017-12-15 08:00 | 240.17 | 230.2
2017-12-15 08:30 | 244.95 | 235.24
2017-12-15 09:00 | 245.13 | 235.63
2017-12-15 09:30 | 246.13 | 236.33
2017-12-15 10:00 | 246.61 | 236.85
2017-12-15 10:30 | 247.32 | 237.72
2017-12-15 11:00 | 248.71 | 239.13
2017-12-15 11:30 | 249.71 | 240.2
2017-12-15 12:00 | 251.13 | 241.82
2017-12-15 12:30 | 253.37 | 243.46
2017-12-15 13:00 | 254.74 | 244.74
2017-12-15 13:30 | 256.25 | 246.77
2017-12-15 14:00 | 256.72 | 247.54
2017-12-15 14:30 | 255.99 | 247.15
2017-12-15 15:00 | 256.34 | 247.62
2017-12-15 15:30 | 258.42 | 249.45
2017-12-15 16:00 | 259.5 | 250.35
2017-12-15 16:30 | 261.33 | 252.15
2017-12-15 17:00 | 262.09 | 252.84
2017-12-15 17:30 | 262.75 | 253.91
2017-12-15 18:00 | 262.41 | 253.97
2017-12-15 18:30 | 261.49 | 253.19
2017-12-15 19:00 | 261.05 | 252.83
2017-12-15 19:30 | 260.46 | 252.4
2017-12-15 20:00 | 259.12 | 250.87
2017-12-15 20:30 | 257.16 | 248.64
2017-12-15 21:00 | 255.25 | 246.4
2017-12-15 21:30 | 236.26 | 228.29
2017-12-15 22:00 | 200.28 | 191.96
2017-12-15 22:30 | 187.01 | 178.21
2017-12-15 23:00 | 185.64 | 176.11
2017-12-15 23:30 | 184 | 174.23
2017-12-16 | 182.46 | 172.67
2017-12-16 00:30 | 181.41 | 171.74
2017-12-16 01:00 | 179.75 | 170.35
2017-12-16 01:30 | 178.59 | 169.41
2017-12-16 02:00 | 177.86 | 168.82
2017-12-16 02:30 | 177.29 | 168.11
2017-12-16 03:00 | 176.89 | 167.76
2017-12-16 03:30 | 177.38 | 167.56
2017-12-16 04:00 | 176.8 | 167.15
2017-12-16 04:30 | 176.72 | 167.26
2017-12-16 05:00 | 177.12 | 167.2
2017-12-16 05:30 | 176.75 | 167.01
2017-12-16 06:00 | 177.58 | 168.13
2017-12-16 06:30 | 178.11 | 168.65
2017-12-16 07:00 | 179.12 | 169.73
2017-12-16 07:30 | 180.12 | 170
2017-12-16 08:00 | 180.87 | 170.5
2017-12-16 08:30 | 182.32 | 171.7
2017-12-16 09:00 | 183.26 | 172.68
2017-12-16 09:30 | 183.36 | 173.38
2017-12-16 10:00 | 186.47 | 176.27
2017-12-16 10:30 | 186.84 | 176.4
2017-12-16 11:00 | 188.67 | 178.39
2017-12-16 11:30 | 190.1 | 179.98
2017-12-16 12:00 | 191.33 | 181.44
2017-12-16 12:30 | 192.99 | 182.84
2017-12-16 13:00 | 194.16 | 183.52
2017-12-16 13:30 | 195.55 | 185.45
2017-12-16 14:00 | 217.83 | 208.28
2017-12-16 14:30 | 250.9 | 241.68
2017-12-16 15:00 | 255.61 | 246.46
2017-12-16 15:30 | 257.07 | 248.22
2017-12-16 16:00 | 258.31 | 249.65
2017-12-16 16:30 | 259.83 | 251.12
2017-12-16 17:00 | 261.29 | 252.48
2017-12-16 17:30 | 263.07 | 254.06
2017-12-16 18:00 | 263.69 | 254.57
2017-12-16 18:30 | 263.33 | 254.02
2017-12-16 19:00 | 262.87 | 253.56
2017-12-16 19:30 | 262.64 | 253.33
2017-12-16 20:00 | 260.99 | 251.48
2017-12-16 20:30 | 258.89 | 248.93
2017-12-16 21:00 | 256.38 | 246.16
2017-12-16 21:30 | 253.18 | 243.94
2017-12-16 22:00 | 251.08 | 241.39
2017-12-16 22:30 | 249.44 | 239.14
2017-12-16 23:00 | 247.54 | 237.29
2017-12-16 23:30 | 230.15 | 220.1
2017-12-17 | 194.84 | 184.67
2017-12-17 00:30 | 182.49 | 172.27
2017-12-17 01:00 | 180.89 | 171.22
2017-12-17 01:30 | 179.3 | 170.58
2017-12-17 02:00 | 178.7 | 169.94
2017-12-17 02:30 | 178.28 | 169.44
2017-12-17 03:00 | 177.33 | 168.52
2017-12-17 03:30 | 177.12 | 168.08
2017-12-17 04:00 | 176.55 | 167.64
2017-12-17 04:30 | 176.63 | 167.76
2017-12-17 05:00 | 176.66 | 167.72
2017-12-17 05:30 | 176.49 | 167.61
2017-12-17 06:00 | 176.14 | 167.61
2017-12-17 06:30 | 176.96 | 168.59
2017-12-17 07:00 | 177.73 | 169.44
2017-12-17 07:30 | 178.73 | 170
2017-12-17 08:00 | 180.1 | 171.12
2017-12-17 08:30 | 180.39 | 171.59
2017-12-17 09:00 | 179.97 | 171.4
2017-12-17 09:30 | 180.98 | 172.42
2017-12-17 10:00 | 184.18 | 174.41
2017-12-17 10:30 | 185.83 | 175.78
2017-12-17 11:00 | 187.01 | 177.12
2017-12-17 11:30 | 188.65 | 179.02
2017-12-17 12:00 | 190.07 | 180.74
2017-12-17 12:30 | 191.79 | 182.2
2017-12-17 13:00 | 223.85 | 214.7
2017-12-17 13:30 | 248.11 | 239.34
2017-12-17 14:00 | 253.2 | 244.97
2017-12-17 14:30 | 255.15 | 246.6
2017-12-17 15:00 | 257.49 | 248.55
2017-12-17 15:30 | 257.6 | 248.41
2017-12-17 16:00 | 257.05 | 247.78
2017-12-17 16:30 | 258.85 | 249.46
2017-12-17 17:00 | 260.56 | 251.34
2017-12-17 17:30 | 260.83 | 251.83
2017-12-17 18:00 | 259.97 | 251.22
2017-12-17 18:30 | 259.92 | 251.22
2017-12-17 19:00 | 260.18 | 251.44
2017-12-17 19:30 | 260.19 | 251.4
2017-12-17 20:00 | 258.74 | 249.75
2017-12-17 20:30 | 239.66 | 230.5
2017-12-17 21:00 | 205.41 | 195.51
2017-12-17 21:30 | 188.85 | 179.56
2017-12-17 22:00 | 185.74 | 175.89
2017-12-17 22:30 | 183.21 | 173.2
2017-12-17 23:00 | 181.09 | 170.79
2017-12-17 23:30 | 180.1 | 169.54
2017-12-18 | 178.37 | 167.58
2017-12-18 00:30 | 177.64 | 166.56
2017-12-18 01:00 | 176.32 | 165.61
2017-12-18 01:30 | 175.25 | 165.08
2017-12-18 02:00 | 173.86 | 164.22
2017-12-18 02:30 | 173.02 | 163.39
2017-12-18 03:00 | 172.81 | 163.2
2017-12-18 03:30 | 172.62 | 162.94
2017-12-18 04:00 | 172.37 | 162.72
2017-12-18 04:30 | 172.61 | 162.95
2017-12-18 05:00 | 173.48 | 163.97
2017-12-18 05:30 | 173.31 | 164
2017-12-18 06:00 | 176.52 | 165.6
2017-12-18 06:30 | 178.62 | 167.8
2017-12-18 07:00 | 209.78 | 199.78
2017-12-18 07:30 | 236.8 | 226.95
2017-12-18 08:00 | 241.12 | 231.74
2017-12-18 08:30 | 240.96 | 232.06
2017-12-18 09:00 | 240.77 | 232.05
2017-12-18 09:30 | 241.25 | 232.25
2017-12-18 10:00 | 241.92 | 232.81
2017-12-18 10:30 | 241.89 | 232.78
2017-12-18 11:00 | 243.09 | 234.16
2017-12-18 11:30 | 245.7 | 236.7
2017-12-18 12:00 | 247.17 | 238.52
2017-12-18 12:30 | 247.74 | 239.12
2017-12-18 13:00 | 248.85 | 239.88
2017-12-18 13:30 | 250.66 | 241.88
2017-12-18 14:00 | 251.45 | 243.13
2017-12-18 14:30 | 252.5 | 244.37
2017-12-18 15:00 | 253.61 | 245.17
2017-12-18 15:30 | 255.33 | 246.93
2017-12-18 16:00 | 256.57 | 248.15
2017-12-18 16:30 | 258.13 | 250.44
2017-12-18 17:00 | 258.62 | 250.96
2017-12-18 17:30 | 259.91 | 251.94
2017-12-18 18:00 | 260.99 | 253.55
2017-12-18 18:30 | 262.72 | 254.73
2017-12-18 19:00 | 262.33 | 254.43
2017-12-18 19:30 | 262.02 | 254.05
2017-12-18 20:00 | 260.1 | 251.99
2017-12-18 20:30 | 256.24 | 248.02
2017-12-18 21:00 | 253.91 | 244.83
2017-12-18 21:30 | 250.78 | 242.28
2017-12-18 22:00 | 247.25 | 238.56
2017-12-18 22:30 | 228.9 | 219.43
2017-12-18 23:00 | 222.03 | 211.8
2017-12-18 23:30 | 193.08 | 182.62
2017-12-19 | 179.04 | 168.27
2017-12-19 00:30 | 178.01 | 167.11
2017-12-19 01:00 | 176.22 | 165.99
2017-12-19 01:30 | 175.7 | 165.41
2017-12-19 02:00 | 175.5 | 165.01
2017-12-19 02:30 | 174.9 | 163.89
2017-12-19 03:00 | 174.09 | 162.97
2017-12-19 03:30 | 173.43 | 162.29
2017-12-19 04:00 | 173.46 | 162.29
2017-12-19 04:30 | 174.28 | 163.32
2017-12-19 05:00 | 174.19 | 163.88
2017-12-19 05:30 | 175.22 | 165.59
2017-12-19 06:00 | 176.09 | 165.95
2017-12-19 06:30 | 178.78 | 168.95
2017-12-19 07:00 | 179.16 | 168.86
2017-12-19 07:30 | 179.3 | 169.6
2017-12-19 08:00 | 209.38 | 200.55
2017-12-19 08:30 | 236.45 | 227.84
2017-12-19 09:00 | 241.41 | 232.92
2017-12-19 09:30 | 241.14 | 232.7
2017-12-19 10:00 | 241.69 | 233.32
2017-12-19 10:30 | 240.61 | 232.14
2017-12-19 11:00 | 238.98 | 230.34
2017-12-19 11:30 | 240.38 | 231.97
2017-12-19 12:00 | 243.32 | 235.53
2017-12-19 12:30 | 247.25 | 239.27
2017-12-19 13:00 | 250.14 | 242.24
2017-12-19 13:30 | 251.4 | 244.31
2017-12-19 14:00 | 252.16 | 245.48
2017-12-19 14:30 | 252.44 | 245.92
2017-12-19 15:00 | 254.16 | 247.48
2017-12-19 15:30 | 242.5 | 236.65
2017-12-19 16:00 | 218.15 | 213.84
2017-12-19 16:30 | 217.35 | 212.66
2017-12-19 17:00 | 216.92 | 212.01
2017-12-19 17:30 | 226.05 | 220.44
2017-12-19 18:00 | 263.64 | 256.72
2017-12-19 18:30 | 264.23 | 257.4
2017-12-19 19:00 | 264.11 | 257.52
2017-12-19 19:30 | 264.42 | 257.76
2017-12-19 20:00 | 262.98 | 256.1
2017-12-19 20:30 | 258.9 | 251.58
2017-12-19 21:00 | 255.95 | 247.75
2017-12-19 21:30 | 253.11 | 244.84
2017-12-19 22:00 | 249.41 | 241.09
2017-12-19 22:30 | 246.81 | 237.7
2017-12-19 23:00 | 245.57 | 235.87
2017-12-19 23:30 | 244.11 | 234.04
2017-12-20 | 226.56 | 216.42
2017-12-20 00:30 | 192.29 | 181.98
2017-12-20 01:00 | 179.29 | 169.18
2017-12-20 01:30 | 178.47 | 168.51
2017-12-20 02:00 | 177.55 | 167.41
2017-12-20 02:30 | 177.41 | 167.23
2017-12-20 03:00 | 176.69 | 166.62
2017-12-20 03:30 | 176.27 | 166.14
2017-12-20 04:00 | 175.93 | 165.85
2017-12-20 04:30 | 176.08 | 165.94
2017-12-20 05:00 | 176.86 | 166.56
2017-12-20 05:30 | 177.63 | 167.14
2017-12-20 06:00 | 179.66 | 169.45
2017-12-20 06:30 | 180.16 | 169.85
2017-12-20 07:00 | 180.79 | 171.01
2017-12-20 07:30 | 210.04 | 201.36
2017-12-20 08:00 | 238.45 | 229.92
2017-12-20 08:30 | 243.53 | 234.48
2017-12-20 09:00 | 244.6 | 235.29
2017-12-20 09:30 | 244.68 | 235.67
2017-12-20 10:00 | 246.22 | 237.21
2017-12-20 10:30 | 247.24 | 238.07
2017-12-20 11:00 | 248.32 | 239.78
2017-12-20 11:30 | 250.69 | 242.04
2017-12-20 12:00 | 253.13 | 244.25
2017-12-20 12:30 | 254.73 | 245.87
2017-12-20 13:00 | 256.52 | 247.56
2017-12-20 13:30 | 256.69 | 248.27
2017-12-20 14:00 | 258.47 | 250.16
2017-12-20 14:30 | 259.54 | 251.29
2017-12-20 15:00 | 259.99 | 251.32
2017-12-20 15:30 | 261.2 | 252.59
2017-12-20 16:00 | 262.12 | 253.65
2017-12-20 16:30 | 263.98 | 255.64
2017-12-20 17:00 | 264.91 | 256.62
2017-12-20 17:30 | 265.85 | 257.35
2017-12-20 18:00 | 266.29 | 257.67
2017-12-20 18:30 | 266.53 | 257.89
2017-12-20 19:00 | 266.5 | 257.99
2017-12-20 19:30 | 266.37 | 258.06
2017-12-20 20:00 | 265.2 | 256.55
2017-12-20 20:30 | 262.68 | 253.51
2017-12-20 21:00 | 259.06 | 249.6
2017-12-20 21:30 | 239.95 | 231.62
2017-12-20 22:00 | 203.49 | 194.56
2017-12-20 22:30 | 189.33 | 179.71
2017-12-20 23:00 | 186.26 | 176.43
2017-12-20 23:30 | 185.87 | 175.44
2017-12-21 | 183.87 | 173.5
2017-12-21 00:30 | 182.21 | 171.98
2017-12-21 01:00 | 180.82 | 170.64
2017-12-21 01:30 | 179.95 | 169.68
2017-12-21 02:00 | 179.15 | 168.96
2017-12-21 02:30 | 178.03 | 168
2017-12-21 03:00 | 176.42 | 166.66
2017-12-21 03:30 | 175.6 | 165.92
2017-12-21 04:00 | 175.73 | 165.81
2017-12-21 04:30 | 176.19 | 166.4
2017-12-21 05:00 | 176.88 | 166.75
2017-12-21 05:30 | 177.98 | 167.75
2017-12-21 06:00 | 178.74 | 169.13
2017-12-21 06:30 | 179.66 | 170.15
2017-12-21 07:00 | 181.52 | 171.5
2017-12-21 07:30 | 210.41 | 201.29
2017-12-21 08:00 | 237.57 | 228.58
2017-12-21 08:30 | 242.27 | 233.21
2017-12-21 09:00 | 243.36 | 234.09
2017-12-21 09:30 | 243.08 | 233.57
2017-12-21 10:00 | 244.03 | 234.69
2017-12-21 10:30 | 244.4 | 235.26
2017-12-21 11:00 | 245 | 236.01
2017-12-21 11:30 | 245.54 | 236.42
2017-12-21 12:00 | 248.05 | 239.09
2017-12-21 12:30 | 249.8 | 240.81
2017-12-21 13:00 | 250.51 | 241.57
2017-12-21 13:30 | 250.89 | 241.78
2017-12-21 14:00 | 250.44 | 241.17
2017-12-21 14:30 | 249.71 | 240.28
2017-12-21 15:00 | 249.24 | 239.64
2017-12-21 15:30 | 251.78 | 242.51
2017-12-21 16:00 | 243.69 | 235.73
2017-12-21 16:30 | 230.15 | 224.76
2017-12-21 17:00 | 230.57 | 225.2
2017-12-21 17:30 | 232.11 | 226.61
2017-12-21 18:00 | 233.72 | 227.42
2017-12-21 18:30 | 244.05 | 234.81
2017-12-21 19:00 | 244.2 | 234.97
2017-12-21 19:30 | 241.84 | 232.71
2017-12-21 20:00 | 240.17 | 231.07
2017-12-21 20:30 | 237.46 | 228.37
2017-12-21 21:00 | 238.5 | 228.69
2017-12-21 21:30 | 241.88 | 230.99
2017-12-21 22:00 | 239.31 | 228.97
2017-12-21 22:30 | 236.99 | 227.19
2017-12-21 23:00 | 234.81 | 224.97
2017-12-21 23:30 | 234.51 | 224.45
2017-12-22 | 235.55 | 225.28
2017-12-22 00:30 | 234.96 | 224.78
2017-12-22 01:00 | 234.34 | 224.26
2017-12-22 01:30 | 233.67 | 223.55
2017-12-22 02:00 | 232.95 | 222.85
2017-12-22 02:30 | 231.23 | 222.04
2017-12-22 03:00 | 230.74 | 221.51
2017-12-22 03:30 | 230.84 | 221.66
2017-12-22 04:00 | 230.48 | 221.61
2017-12-22 04:30 | 230.66 | 221.7
2017-12-22 05:00 | 231.63 | 222.76
2017-12-22 05:30 | 231.9 | 223
2017-12-22 06:00 | 233.08 | 223.81
2017-12-22 06:30 | 234.97 | 225.1
2017-12-22 07:00 | 235.35 | 225.43
2017-12-22 07:30 | 235.74 | 225.58
2017-12-22 08:00 | 235.65 | 225.45
2017-12-22 08:30 | 236.06 | 225.74
2017-12-22 09:00 | 235.7 | 225.34
2017-12-22 09:30 | 236.01 | 225.06
2017-12-22 10:00 | 235.27 | 224.81
2017-12-22 10:30 | 236.06 | 225.86
2017-12-22 11:00 | 236.23 | 226.16
2017-12-22 11:30 | 236.63 | 226.57
2017-12-22 12:00 | 237.16 | 226.92
2017-12-22 12:30 | 237.69 | 227.58
2017-12-22 13:00 | 238.6 | 229.03
2017-12-22 13:30 | 238.65 | 229.7
2017-12-22 14:00 | 239.36 | 230.5
2017-12-22 14:30 | 239.92 | 230.72
2017-12-22 15:00 | 241.34 | 231.56
2017-12-22 15:30 | 241.86 | 232.18
2017-12-22 16:00 | 242.7 | 233.09
2017-12-22 16:30 | 243.79 | 234.28
2017-12-22 17:00 | 243.99 | 234.37
2017-12-22 17:30 | 244.68 | 234.87
2017-12-22 18:00 | 245 | 235.11
2017-12-22 18:30 | 245.26 | 235.24
2017-12-22 19:00 | 245.45 | 235.52
2017-12-22 19:30 | 245.67 | 235.93
2017-12-22 20:00 | 245.01 | 235.21
2017-12-22 20:30 | 243.38 | 233.5
2017-12-22 21:00 | 241.81 | 231.94
2017-12-22 21:30 | 239.92 | 231.07
2017-12-22 22:00 | 237.65 | 228.6
2017-12-22 22:30 | 235.47 | 226.36
2017-12-22 23:00 | 234.62 | 225.51
2017-12-22 23:30 | 233.84 | 224.56
2017-12-23 | 232.55 | 223.19
2017-12-23 00:30 | 231.54 | 222.37
2017-12-23 01:00 | 214.56 | 205.54
2017-12-23 01:30 | 182.46 | 172.91
2017-12-23 02:00 | 169.73 | 159.73
2017-12-23 02:30 | 168.63 | 158.54
2017-12-23 03:00 | 168.92 | 158.94
2017-12-23 03:30 | 168.81 | 158.97
2017-12-23 04:00 | 168.36 | 158.49
2017-12-23 04:30 | 168.46 | 158.58
2017-12-23 05:00 | 168.66 | 158.79
2017-12-23 05:30 | 168.45 | 158.74
2017-12-23 06:00 | 169.02 | 159.53
2017-12-23 06:30 | 169.1 | 159.83
2017-12-23 07:00 | 170.05 | 160.71
2017-12-23 07:30 | 170.86 | 161.29
2017-12-23 08:00 | 172.01 | 161.77
2017-12-23 08:30 | 172.34 | 161.88
2017-12-23 09:00 | 173.76 | 162.99
2017-12-23 09:30 | 203.75 | 193.46
2017-12-23 10:00 | 230.68 | 220.47
2017-12-23 10:30 | 235.58 | 225.5
2017-12-23 11:00 | 236.44 | 226.59
2017-12-23 11:30 | 237.81 | 228.15
2017-12-23 12:00 | 238.17 | 228.67
2017-12-23 12:30 | 239.36 | 229.92
2017-12-23 13:00 | 239.97 | 230.72
2017-12-23 13:30 | 241.32 | 231.79
2017-12-23 14:00 | 240.57 | 231.05
2017-12-23 14:30 | 241.3 | 231.96
2017-12-23 15:00 | 243.08 | 233.74
2017-12-23 15:30 | 243.9 | 235.02
2017-12-23 16:00 | 245.84 | 236.88
2017-12-23 16:30 | 247.16 | 238.17
2017-12-23 17:00 | 248.42 | 239.56
2017-12-23 17:30 | 250.58 | 241.56
2017-12-23 18:00 | 252.29 | 242.25
2017-12-23 18:30 | 252.43 | 242.19
2017-12-23 19:00 | 252.17 | 241.89
2017-12-23 19:30 | 252.23 | 242.13
2017-12-23 20:00 | 251.05 | 240.77
2017-12-23 20:30 | 248.99 | 238.35
2017-12-23 21:00 | 247.36 | 236.34
2017-12-23 21:30 | 243.55 | 233.77
2017-12-23 22:00 | 240.89 | 231.22
2017-12-23 22:30 | 238.4 | 228.74
2017-12-23 23:00 | 236.69 | 226.76
2017-12-23 23:30 | 235.95 | 225.6
2017-12-24 | 220.06 | 210.09
2017-12-24 00:30 | 185.96 | 175.75
2017-12-24 01:00 | 173.24 | 162.8
2017-12-24 01:30 | 172.49 | 162.37
2017-12-24 02:00 | 171.88 | 161.48
2017-12-24 02:30 | 171.22 | 160.71
2017-12-24 03:00 | 171.26 | 160.65
2017-12-24 03:30 | 171.33 | 160.71
2017-12-24 04:00 | 170.94 | 160.3
2017-12-24 04:30 | 170.38 | 160.01
2017-12-24 05:00 | 170.53 | 160.28
2017-12-24 05:30 | 169.82 | 159.97
2017-12-24 06:00 | 170.3 | 160.7
2017-12-24 06:30 | 171.15 | 161.65
2017-12-24 07:00 | 172.19 | 162.61
2017-12-24 07:30 | 172.18 | 162.48
2017-12-24 08:00 | 174.66 | 163.97
2017-12-24 08:30 | 175.1 | 164.49
2017-12-24 09:00 | 176.37 | 165.3
2017-12-24 09:30 | 205.31 | 194.66
2017-12-24 10:00 | 233.9 | 222.99
2017-12-24 10:30 | 238.27 | 227.57
2017-12-24 11:00 | 239.48 | 228.95
2017-12-24 11:30 | 240.73 | 230.3
2017-12-24 12:00 | 241.98 | 231.69
2017-12-24 12:30 | 243.79 | 233.16
2017-12-24 13:00 | 245.22 | 234.58
2017-12-24 13:30 | 245.16 | 235.01
2017-12-24 14:00 | 244.95 | 235.68
2017-12-24 14:30 | 244.94 | 235.6
2017-12-24 15:00 | 246.07 | 236.54
2017-12-24 15:30 | 245.93 | 236.63
2017-12-24 16:00 | 247.57 | 238.58
2017-12-24 16:30 | 237.9 | 230.2
2017-12-24 17:00 | 221.65 | 216.3
2017-12-24 17:30 | 220.3 | 214.56
2017-12-24 18:00 | 220.15 | 214.27
2017-12-24 18:30 | 221.37 | 215.22
2017-12-24 19:00 | 222.73 | 216.52
2017-12-24 19:30 | 224.09 | 217.93
2017-12-24 20:00 | 225.46 | 219.3
2017-12-24 20:30 | 227.4 | 220.97
2017-12-24 21:00 | 228.35 | 222.39
2017-12-24 21:30 | 230.57 | 225.01
2017-12-24 22:00 | 241.11 | 231.46
2017-12-24 22:30 | 239.02 | 228.92
2017-12-24 23:00 | 238.8 | 228.88
2017-12-24 23:30 | 238.44 | 227.64
2017-12-25 | 223.79 | 212.22
2017-12-25 00:30 | 188.89 | 176.67
2017-12-25 01:00 | 175.33 | 163.84
2017-12-25 01:30 | 175.05 | 163.1
2017-12-25 02:00 | 173.5 | 162.23
2017-12-25 02:30 | 172.38 | 161.91
2017-12-25 03:00 | 171.84 | 161.44
2017-12-25 03:30 | 171.93 | 161.21
2017-12-25 04:00 | 172.05 | 160.91
2017-12-25 04:30 | 171.27 | 160.66
2017-12-25 05:00 | 170.61 | 160.14
2017-12-25 05:30 | 170.24 | 160.17
2017-12-25 06:00 | 170.18 | 160.59
2017-12-25 06:30 | 170.98 | 161.26
2017-12-25 07:00 | 171.49 | 162.12
2017-12-25 07:30 | 172.32 | 163.46
2017-12-25 08:00 | 173.3 | 164.38
2017-12-25 08:30 | 174.4 | 164.64
2017-12-25 09:00 | 203.69 | 194.32
2017-12-25 09:30 | 231.81 | 221.67
2017-12-25 10:00 | 237.01 | 226.52
2017-12-25 10:30 | 238.08 | 227.67
2017-12-25 11:00 | 238.63 | 228.35
2017-12-25 11:30 | 239.22 | 229.2
2017-12-25 12:00 | 239.51 | 229.77
2017-12-25 12:30 | 238.41 | 228.6
2017-12-25 13:00 | 239.99 | 229.98
2017-12-25 13:30 | 239.15 | 229.27
2017-12-25 14:00 | 239.97 | 229.91
2017-12-25 14:30 | 240.59 | 229.91
2017-12-25 15:00 | 235.27 | 225.73
2017-12-25 15:30 | 237.16 | 228.14
2017-12-25 16:00 | 239.36 | 231.03
2017-12-25 16:30 | 239.31 | 230.43
2017-12-25 17:00 | 239.43 | 230.31
2017-12-25 17:30 | 242.44 | 233.06
2017-12-25 18:00 | 242.36 | 232.96
2017-12-25 18:30 | 242.52 | 232.56
2017-12-25 19:00 | 242.48 | 232.41
2017-12-25 19:30 | 243.49 | 233.05
2017-12-25 20:00 | 243.3 | 232.52
2017-12-25 20:30 | 242.71 | 231.69
2017-12-25 21:00 | 241.84 | 231.28
2017-12-25 21:30 | 238.2 | 230.22
2017-12-25 22:00 | 235.96 | 228.23
2017-12-25 22:30 | 235.04 | 226.85
2017-12-25 23:00 | 233.78 | 225.36
2017-12-25 23:30 | 231.33 | 224.18
2017-12-26 | 214.56 | 207.6
2017-12-26 00:30 | 180.73 | 173.45
2017-12-26 01:00 | 168.94 | 161.47
2017-12-26 01:30 | 168.66 | 161.07
2017-12-26 02:00 | 168.48 | 160.27
2017-12-26 02:30 | 168.18 | 159.9
2017-12-26 03:00 | 167.94 | 159.87
2017-12-26 03:30 | 167.26 | 159.48
2017-12-26 04:00 | 166.96 | 159.22
2017-12-26 04:30 | 166.74 | 158.81
2017-12-26 05:00 | 167.12 | 159.2
2017-12-26 05:30 | 166.86 | 158.92
2017-12-26 06:00 | 166.52 | 159.01
2017-12-26 06:30 | 167.75 | 159.47
2017-12-26 07:00 | 169.44 | 160
2017-12-26 07:30 | 169.83 | 160.51
2017-12-26 08:00 | 171.25 | 160.93
2017-12-26 08:30 | 171.16 | 160.71
2017-12-26 09:00 | 171.61 | 161.8
2017-12-26 09:30 | 171.71 | 161.53
2017-12-26 10:00 | 173.48 | 162.81
2017-12-26 10:30 | 174.75 | 164.15
2017-12-26 11:00 | 175.38 | 164.65
2017-12-26 11:30 | 176.47 | 165.77
2017-12-26 12:00 | 204.85 | 194.66
2017-12-26 12:30 | 231.08 | 221.35
2017-12-26 13:00 | 236.05 | 226.66
2017-12-26 13:30 | 237.35 | 228.32
2017-12-26 14:00 | 238.8 | 230.07
2017-12-26 14:30 | 238.38 | 229.29
2017-12-26 15:00 | 239.45 | 229.1
2017-12-26 15:30 | 239.19 | 229.02
2017-12-26 16:00 | 239.44 | 229.1
2017-12-26 16:30 | 237.46 | 226.75
2017-12-26 17:00 | 236.02 | 226.54
2017-12-26 17:30 | 236.26 | 227
2017-12-26 18:00 | 236.73 | 226.79
2017-12-26 18:30 | 195.15 | 186.42
2017-12-26 19:00 | 205.62 | 197.06
2017-12-26 19:30 | 219.25 | 210.3
2017-12-26 20:00 | 231.47 | 223.2
2017-12-26 20:30 | 234.75 | 225.84
2017-12-26 21:00 | 235.41 | 225.83
2017-12-26 21:30 | 234.16 | 225.51
2017-12-26 22:00 | 218.36 | 209.37
2017-12-26 22:30 | 184.08 | 174.93
2017-12-26 23:00 | 169.8 | 160.19
2017-12-26 23:30 | 168.27 | 159.02
2017-12-27 | 164.05 | 156.54
2017-12-27 00:30 | 163.42 | 155.83
2017-12-27 01:00 | 162.81 | 155.26
2017-12-27 01:30 | 162.73 | 154.83
2017-12-27 02:00 | 162.78 | 154.56
2017-12-27 02:30 | 162.28 | 153.78
2017-12-27 03:00 | 162.11 | 153.52
2017-12-27 03:30 | 161.66 | 152.93
2017-12-27 04:00 | 161.34 | 152.61
2017-12-27 04:30 | 161.41 | 152.76
2017-12-27 05:00 | 161.68 | 153.05
2017-12-27 05:30 | 161.4 | 152.65
2017-12-27 06:00 | 161.42 | 153.41
2017-12-27 06:30 | 161.7 | 154
2017-12-27 07:00 | 162.94 | 155.31
2017-12-27 07:30 | 164.19 | 155.89
2017-12-27 08:00 | 164.32 | 156.29
2017-12-27 08:30 | 164.68 | 155.77
2017-12-27 09:00 | 165 | 156.25
2017-12-27 09:30 | 165.73 | 157.65
2017-12-27 10:00 | 166 | 157.38
2017-12-27 10:30 | 167.87 | 159.02
2017-12-27 11:00 | 168.12 | 159.46
2017-12-27 11:30 | 169.77 | 161.02
2017-12-27 12:00 | 167.75 | 157.59
2017-12-27 12:30 | 170.75 | 160.69
2017-12-27 13:00 | 175.5 | 166.27
2017-12-27 13:30 | 176.62 | 168.32
2017-12-27 14:00 | 178.33 | 170.29
2017-12-27 14:30 | 179.99 | 171.64
2017-12-27 15:00 | 211.63 | 203.16
2017-12-27 15:30 | 236.56 | 227.55
2017-12-27 16:00 | 242.67 | 233.91
2017-12-27 16:30 | 241.97 | 233.7
2017-12-27 17:00 | 225.72 | 221.21
2017-12-27 17:30 | 225.99 | 221.62
2017-12-27 18:00 | 226.9 | 222.46
2017-12-27 18:30 | 227.93 | 223.26
2017-12-27 19:00 | 229.51 | 225.18
2017-12-27 19:30 | 230.02 | 225.96
2017-12-27 20:00 | 231.86 | 227.85
2017-12-27 20:30 | 226.79 | 222.05
2017-12-27 21:00 | 219.54 | 210.85
2017-12-27 21:30 | 239.96 | 232.06
2017-12-27 22:00 | 222.22 | 214.14
2017-12-27 22:30 | 188.54 | 179.74
2017-12-27 23:00 | 175.41 | 166.11
2017-12-27 23:30 | 174.35 | 164.7
2017-12-28 | 173.3 | 163.56
2017-12-28 00:30 | 172.47 | 162.9
2017-12-28 01:00 | 170.06 | 161.86
2017-12-28 01:30 | 169.9 | 161.34
2017-12-28 02:00 | 169 | 161.17
2017-12-28 02:30 | 168.18 | 160.42
2017-12-28 03:00 | 167.63 | 160.07
2017-12-28 03:30 | 166.38 | 158.89
2017-12-28 04:00 | 168.57 | 159.79
2017-12-28 04:30 | 169.24 | 159.71
2017-12-28 05:00 | 169.97 | 159.84
2017-12-28 05:30 | 169.81 | 159.63
2017-12-28 06:00 | 170.04 | 159.93
2017-12-28 06:30 | 170.82 | 160.64
2017-12-28 07:00 | 173.42 | 161.79
2017-12-28 07:30 | 173.74 | 161.9
2017-12-28 08:00 | 175.68 | 162.25
2017-12-28 08:30 | 175.5 | 162.13
2017-12-28 09:00 | 175.8 | 162.83
2017-12-28 09:30 | 175.8 | 163.05
2017-12-28 10:00 | 175.79 | 163.2
2017-12-28 10:30 | 176.56 | 163.9
2017-12-28 11:00 | 177.61 | 164.63
2017-12-28 11:30 | 178.9 | 166.46
2017-12-28 12:00 | 210.72 | 199.49
2017-12-28 12:30 | 234.99 | 223.99
2017-12-28 13:00 | 241.52 | 231.31
2017-12-28 13:30 | 243.89 | 234.76
2017-12-28 14:00 | 244.83 | 235.72
2017-12-28 14:30 | 244.49 | 234.47
2017-12-28 15:00 | 244.88 | 234.85
2017-12-28 15:30 | 246.82 | 236.5
2017-12-28 16:00 | 247.18 | 237.24
2017-12-28 16:30 | 247.96 | 237.76
2017-12-28 17:00 | 249.3 | 239.36
2017-12-28 17:30 | 251.44 | 240.91
2017-12-28 18:00 | 252.38 | 241.66
2017-12-28 18:30 | 252.27 | 241.59
2017-12-28 19:00 | 253.09 | 242.43
2017-12-28 19:30 | 253.45 | 242.95
2017-12-28 20:00 | 252.97 | 242.48
2017-12-28 20:30 | 248.89 | 239.4
2017-12-28 21:00 | 247.05 | 238.08
2017-12-28 21:30 | 241.93 | 234.32
2017-12-28 22:00 | 238.85 | 231.38
2017-12-28 22:30 | 236.93 | 229.42
2017-12-28 23:00 | 220.35 | 212.54
2017-12-28 23:30 | 186.63 | 178.45
2017-12-29 | 174.51 | 165.82
2017-12-29 00:30 | 173.84 | 165.3
2017-12-29 01:00 | 171.86 | 164.23
2017-12-29 01:30 | 171.11 | 163.51
2017-12-29 02:00 | 171.27 | 163.41
2017-12-29 02:30 | 170.9 | 162.89
2017-12-29 03:00 | 170.71 | 162.75
2017-12-29 03:30 | 170.29 | 162.26
2017-12-29 04:00 | 169.91 | 161.79
2017-12-29 04:30 | 168.73 | 161.5
2017-12-29 05:00 | 169.41 | 161.92
2017-12-29 05:30 | 169.01 | 161.35
2017-12-29 06:00 | 170.16 | 162.24
2017-12-29 06:30 | 170.81 | 163.33
2017-12-29 07:00 | 172.2 | 164.09
2017-12-29 07:30 | 172.87 | 164.14
2017-12-29 08:00 | 203.71 | 195.56
2017-12-29 08:30 | 228.92 | 220.4
2017-12-29 09:00 | 233.77 | 225.13
2017-12-29 09:30 | 234.03 | 225.56
2017-12-29 10:00 | 234.62 | 226.23
2017-12-29 10:30 | 235.46 | 226.91
2017-12-29 11:00 | 236.79 | 228.35
2017-12-29 11:30 | 237.35 | 228.67
2017-12-29 12:00 | 238.78 | 230.56
2017-12-29 12:30 | 240.73 | 232.98
2017-12-29 13:00 | 241.92 | 234.38
2017-12-29 13:30 | 243.76 | 235.43
2017-12-29 14:00 | 244.62 | 236.16
2017-12-29 14:30 | 221.85 | 215.16
2017-12-29 15:00 | 245.22 | 237.29
2017-12-29 15:30 | 246.27 | 238.48
2017-12-29 16:00 | 247.69 | 239.89
2017-12-29 16:30 | 248.89 | 240.9
2017-12-29 17:00 | 250.18 | 242.38
2017-12-29 17:30 | 251.12 | 243.45
2017-12-29 18:00 | 252.14 | 244.16
2017-12-29 18:30 | 253.06 | 244.59
2017-12-29 19:00 | 253.56 | 245.09
2017-12-29 19:30 | 254.16 | 245.72
2017-12-29 20:00 | 254.32 | 245.67
2017-12-29 20:30 | 253.87 | 244.8
2017-12-29 21:00 | 251.11 | 241.99
2017-12-29 21:30 | 247.3 | 240.61
2017-12-29 22:00 | 244.99 | 237.92
2017-12-29 22:30 | 242.39 | 235.02
2017-12-29 23:00 | 224.86 | 217.13
2017-12-29 23:30 | 190.44 | 182.49
2017-12-30 | 178.12 | 169.93
2017-12-30 00:30 | 176.37 | 168.41
2017-12-30 01:00 | 175.01 | 167.52
2017-12-30 01:30 | 173.96 | 166.39
2017-12-30 02:00 | 173.32 | 165.88
2017-12-30 02:30 | 172.88 | 165.31
2017-12-30 03:00 | 172.56 | 164.95
2017-12-30 03:30 | 171.93 | 164.18
2017-12-30 04:00 | 171.89 | 164.03
2017-12-30 04:30 | 171.79 | 163.78
2017-12-30 05:00 | 171.05 | 162.86
2017-12-30 05:30 | 171.19 | 163.34
2017-12-30 06:00 | 170.96 | 163.34
2017-12-30 06:30 | 171.32 | 163.26
2017-12-30 07:00 | 171.97 | 164.13
2017-12-30 07:30 | 173.12 | 165.11
2017-12-30 08:00 | 174.07 | 165.75
2017-12-30 08:30 | 174.08 | 166
2017-12-30 09:00 | 175.9 | 166.53
2017-12-30 09:30 | 177.16 | 167.85
2017-12-30 10:00 | 180.8 | 172.41
2017-12-30 10:30 | 181.45 | 173.56
2017-12-30 11:00 | 183.11 | 174.54
2017-12-30 11:30 | 185.35 | 176.84
2017-12-30 12:00 | 186.32 | 178.27
2017-12-30 12:30 | 186.85 | 179.2
2017-12-30 13:00 | 186.02 | 178.44
2017-12-30 13:30 | 185.42 | 177.54
2017-12-30 14:00 | 219.51 | 211.54
2017-12-30 14:30 | 242.99 | 234.96
2017-12-30 15:00 | 245.66 | 237.77
2017-12-30 15:30 | 247.6 | 239.05
2017-12-30 16:00 | 248.23 | 239.06
2017-12-30 16:30 | 248.84 | 239.36
2017-12-30 17:00 | 247.4 | 237.57
2017-12-30 17:30 | 247.73 | 238.31
2017-12-30 18:00 | 248.42 | 238.86
2017-12-30 18:30 | 248.23 | 238.51
2017-12-30 19:00 | 247.24 | 237.62
2017-12-30 19:30 | 246.67 | 237.04
2017-12-30 20:00 | 246.88 | 237.13
2017-12-30 20:30 | 245.89 | 235.43
2017-12-30 21:00 | 244.63 | 233.72
2017-12-30 21:30 | 240.47 | 231.9
2017-12-30 22:00 | 237.72 | 229.17
2017-12-30 22:30 | 235.64 | 226.9
2017-12-30 23:00 | 234.93 | 226.1
2017-12-30 23:30 | 218.8 | 209.67
2017-12-31 | 187.33 | 177.58
2017-12-31 00:30 | 175.27 | 164.79
2017-12-31 01:00 | 173.87 | 163.26
2017-12-31 01:30 | 172.96 | 162.37
2017-12-31 02:00 | 172.77 | 162.03
2017-12-31 02:30 | 172.5 | 161.82
2017-12-31 03:00 | 171.74 | 160.97
2017-12-31 03:30 | 171.78 | 161.02
2017-12-31 04:00 | 171.04 | 160.42
2017-12-31 04:30 | 170.54 | 159.54
2017-12-31 05:00 | 170.74 | 159.66
2017-12-31 05:30 | 170.61 | 159.74
2017-12-31 06:00 | 170.28 | 160.11
2017-12-31 06:30 | 169.82 | 160.08
2017-12-31 07:00 | 170.31 | 160.77
2017-12-31 07:30 | 171.74 | 162.02
2017-12-31 08:00 | 172.52 | 162.71
2017-12-31 08:30 | 203.41 | 194.07
2017-12-31 09:00 | 227.62 | 218.03
2017-12-31 09:30 | 232.63 | 223.53
2017-12-31 10:00 | 233.77 | 224.99
2017-12-31 10:30 | 234.31 | 225.72
2017-12-31 11:00 | 235.86 | 227.21
2017-12-31 11:30 | 237.04 | 228.9
2017-12-31 12:00 | 238.54 | 230.43
2017-12-31 12:30 | 239.73 | 231.18
2017-12-31 13:00 | 240.9 | 232.4
2017-12-31 13:30 | 237.27 | 229.99
2017-12-31 14:00 | 227.07 | 222.96
2017-12-31 14:30 | 222.49 | 218.32
2017-12-31 15:00 | 205.51 | 201.6
2017-12-31 15:30 | 203.24 | 198.92
2017-12-31 16:00 | 220.7 | 215.99
2017-12-31 16:30 | 224.28 | 219.33
2017-12-31 17:00 | 222.93 | 218
2017-12-31 17:30 | 220.76 | 215.78
2017-12-31 18:00 | 219.35 | 214.39
2017-12-31 18:30 | 219.9 | 214.98
2017-12-31 19:00 | 220 | 215.1
2017-12-31 19:30 | 221.54 | 216.75
2017-12-31 20:00 | 238.21 | 230.05
2017-12-31 20:30 | 243.31 | 233.75
2017-12-31 21:00 | 241.85 | 232.09
2017-12-31 21:30 | 238.78 | 231.08
2017-12-31 22:00 | 236.81 | 229.2
2017-12-31 22:30 | 234.06 | 226
2017-12-31 23:00 | 232.93 | 224.76
2017-12-31 23:30 | 232.66 | 224.52
2018-01-01 | 231.79 | 223.44
2018-01-01 00:30 | 214.53 | 206.41
2018-01-01 01:00 | 180.43 | 171.93
2018-01-01 01:30 | 170.73 | 162.32
2018-01-01 02:00 | 171.1 | 162.05
2018-01-01 02:30 | 171.02 | 161.28
2018-01-01 03:00 | 170.96 | 161.04
2018-01-01 03:30 | 169.92 | 160.4
2018-01-01 04:00 | 169.04 | 159.63
2018-01-01 04:30 | 168.46 | 159.62
2018-01-01 05:00 | 168.19 | 159.44
2018-01-01 05:30 | 167.71 | 158.97
2018-01-01 06:00 | 167.48 | 159.08
2018-01-01 06:30 | 168.34 | 159.46
2018-01-01 07:00 | 170.14 | 160.47
2018-01-01 07:30 | 170.52 | 161.09
2018-01-01 08:00 | 171.12 | 161.52
2018-01-01 08:30 | 199.68 | 190.83
2018-01-01 09:00 | 225 | 215.63
2018-01-01 09:30 | 229.79 | 220.77
2018-01-01 10:00 | 231.74 | 223.36
2018-01-01 10:30 | 233.61 | 224.8
2018-01-01 11:00 | 234.99 | 225.51
2018-01-01 11:30 | 236.61 | 227.23
2018-01-01 12:00 | 238.62 | 229.53
2018-01-01 12:30 | 239.48 | 230.11
2018-01-01 13:00 | 240.78 | 230.34
2018-01-01 13:30 | 241.7 | 231.1
2018-01-01 14:00 | 242.42 | 231.73
2018-01-01 14:30 | 243.39 | 232.42
2018-01-01 15:00 | 243.53 | 232.46
2018-01-01 15:30 | 243.37 | 232.36
2018-01-01 16:00 | 244.78 | 233.98
2018-01-01 16:30 | 245.91 | 235.24
2018-01-01 17:00 | 246.7 | 236.26
2018-01-01 17:30 | 248.63 | 238.63
2018-01-01 18:00 | 249.58 | 239.75
2018-01-01 18:30 | 250.81 | 240.86
2018-01-01 19:00 | 251 | 241.07
2018-01-01 19:30 | 251.21 | 241.33
2018-01-01 20:00 | 251.34 | 241.41
2018-01-01 20:30 | 250.04 | 239.8
2018-01-01 21:00 | 246 | 236.85
2018-01-01 21:30 | 242.37 | 235.21
2018-01-01 22:00 | 239.19 | 232.46
2018-01-01 22:30 | 235.94 | 229.48
2018-01-01 23:00 | 234.05 | 227.33
2018-01-01 23:30 | 233.07 | 225.95
2018-01-02 | 232.1 | 224.77
2018-01-02 00:30 | 231.28 | 223.75
2018-01-02 01:00 | 230.48 | 222.81
2018-01-02 01:30 | 229.94 | 222.22
2018-01-02 02:00 | 229.52 | 221.69
2018-01-02 02:30 | 229.2 | 221.22
2018-01-02 03:00 | 228.68 | 220.74
2018-01-02 03:30 | 228.48 | 220.59
2018-01-02 04:00 | 228.2 | 220.32
2018-01-02 04:30 | 228.15 | 220.16
2018-01-02 05:00 | 228.49 | 220.47
2018-01-02 05:30 | 228.92 | 220.98
2018-01-02 06:00 | 229.25 | 221.39
2018-01-02 06:30 | 230.01 | 222.08
2018-01-02 07:00 | 230.85 | 222.52
2018-01-02 07:30 | 231.71 | 223.49
2018-01-02 08:00 | 232.5 | 224.35
2018-01-02 08:30 | 232.75 | 224.75
2018-01-02 09:00 | 233.47 | 225.74
2018-01-02 09:30 | 234.06 | 226.53
2018-01-02 10:00 | 234.87 | 227.48
2018-01-02 10:30 | 236.17 | 229.06
2018-01-02 11:00 | 236.48 | 229.4
2018-01-02 11:30 | 237.35 | 229.94
2018-01-02 12:00 | 238.52 | 231.03
2018-01-02 12:30 | 240.46 | 233.26
2018-01-02 13:00 | 241.12 | 233.97
2018-01-02 13:30 | 240.59 | 233.57
2018-01-02 14:00 | 240.16 | 232.97
2018-01-02 14:30 | 241.47 | 233.95
2018-01-02 15:00 | 242.42 | 234.63
2018-01-02 15:30 | 235.28 | 228.25
2018-01-02 16:00 | 234.52 | 227.34
2018-01-02 16:30 | 234.95 | 227.81
2018-01-02 17:00 | 235.93 | 228.78
2018-01-02 17:30 | 236.28 | 229.13
2018-01-02 18:00 | 238.67 | 231.42
2018-01-02 18:30 | 250.19 | 242.48
2018-01-02 19:00 | 251.83 | 244.15
2018-01-02 19:30 | 251.18 | 243.42
2018-01-02 20:00 | 251.19 | 243.36
2018-01-02 20:30 | 249.23 | 240.91
2018-01-02 21:00 | 246.14 | 237.74
2018-01-02 21:30 | 242.02 | 235.2
2018-01-02 22:00 | 239.77 | 232.54
2018-01-02 22:30 | 236.41 | 229.27
2018-01-02 23:00 | 234.65 | 227.27
2018-01-02 23:30 | 218.34 | 210.58
2018-01-03 | 184.44 | 176.11
2018-01-03 00:30 | 174.88 | 166.27
2018-01-03 01:00 | 172.81 | 164.24
2018-01-03 01:30 | 172.27 | 163.85
2018-01-03 02:00 | 171.94 | 163.62
2018-01-03 02:30 | 171.17 | 162.74
2018-01-03 03:00 | 170.52 | 162.08
2018-01-03 03:30 | 170.25 | 161.77
2018-01-03 04:00 | 169.75 | 161.22
2018-01-03 04:30 | 168.95 | 160.69
2018-01-03 05:00 | 168.61 | 161.05
2018-01-03 05:30 | 168.66 | 161.2
2018-01-03 06:00 | 168.71 | 161.51
2018-01-03 06:30 | 173.01 | 163.1
2018-01-03 07:00 | 174.84 | 163.76
2018-01-03 07:30 | 175.76 | 164.03
2018-01-03 08:00 | 177.75 | 165.83
2018-01-03 08:30 | 177.43 | 165.58
2018-01-03 09:00 | 180.9 | 169.6
2018-01-03 09:30 | 180.82 | 169.26
2018-01-03 10:00 | 207.47 | 196.76
2018-01-03 10:30 | 231.48 | 221.13
2018-01-03 11:00 | 238.46 | 228.02
2018-01-03 11:30 | 239.85 | 229.22
2018-01-03 12:00 | 241.28 | 230.58
2018-01-03 12:30 | 242.71 | 232.14
2018-01-03 13:00 | 244.39 | 234.18
2018-01-03 13:30 | 246.31 | 236.4
2018-01-03 14:00 | 246.8 | 237.2
2018-01-03 14:30 | 245.59 | 235.92
2018-01-03 15:00 | 244.99 | 235.56
2018-01-03 15:30 | 246.73 | 237.71
2018-01-03 16:00 | 247.9 | 239.31
2018-01-03 16:30 | 250.35 | 241.77
2018-01-03 17:00 | 252.63 | 243.94
2018-01-03 17:30 | 255.29 | 246.39
2018-01-03 18:00 | 256.53 | 247.63
2018-01-03 18:30 | 256.96 | 248.07
2018-01-03 19:00 | 257.58 | 248.81
2018-01-03 19:30 | 257.77 | 248.97
2018-01-03 20:00 | 257.06 | 248.07
2018-01-03 20:30 | 238.34 | 228.7
2018-01-03 21:00 | 200.26 | 189.8
2018-01-03 21:30 | 187.37 | 178.78
2018-01-03 22:00 | 183.5 | 174.69
2018-01-03 22:30 | 181.76 | 172.57
2018-01-03 23:00 | 179.39 | 169.77
2018-01-03 23:30 | 178.15 | 168.06
2018-01-04 | 176.22 | 166.46
2018-01-04 00:30 | 175.36 | 165.5
2018-01-04 01:00 | 174.08 | 164.55
2018-01-04 01:30 | 173.43 | 163.69
2018-01-04 02:00 | 172.73 | 162.89
2018-01-04 02:30 | 172.77 | 162.71
2018-01-04 03:00 | 172.24 | 162.07
2018-01-04 03:30 | 172.16 | 162.09
2018-01-04 04:00 | 171.41 | 161.48
2018-01-04 04:30 | 171.59 | 161.7
2018-01-04 05:00 | 171.82 | 162.04
2018-01-04 05:30 | 172.02 | 162.31
2018-01-04 06:00 | 172.58 | 163.13
2018-01-04 06:30 | 174.27 | 164.16
2018-01-04 07:00 | 176.65 | 165.01
2018-01-04 07:30 | 177.11 | 165.5
2018-01-04 08:00 | 177.81 | 166.18
2018-01-04 08:30 | 178.17 | 167.05
2018-01-04 09:00 | 179.06 | 168.04
2018-01-04 09:30 | 183.92 | 173.22
2018-01-04 10:00 | 225.78 | 216.11
2018-01-04 10:30 | 237.27 | 227.81
2018-01-04 11:00 | 238.05 | 228.91
2018-01-04 11:30 | 239.66 | 230.2
2018-01-04 12:00 | 239.7 | 230.68
2018-01-04 12:30 | 241.6 | 233.08
2018-01-04 13:00 | 242.89 | 234.62
2018-01-04 13:30 | 243.45 | 235.28
2018-01-04 14:00 | 244.53 | 236.38
2018-01-04 14:30 | 244.92 | 236.67
2018-01-04 15:00 | 246.36 | 238.29
2018-01-04 15:30 | 247.24 | 239.7
2018-01-04 16:00 | 247.74 | 240.63
2018-01-04 16:30 | 250.06 | 242.78
2018-01-04 17:00 | 250.2 | 243.12
2018-01-04 17:30 | 250.79 | 243.03
2018-01-04 18:00 | 249.88 | 242.17
2018-01-04 18:30 | 250.48 | 242.92
2018-01-04 19:00 | 251.91 | 244.51
2018-01-04 19:30 | 252.53 | 245.31
2018-01-04 20:00 | 252.19 | 244.74
2018-01-04 20:30 | 250.09 | 242.09
2018-01-04 21:00 | 247.79 | 238.96
2018-01-04 21:30 | 246.3 | 237.81
2018-01-04 22:00 | 243.82 | 235.04
2018-01-04 22:30 | 240.93 | 231.79
2018-01-04 23:00 | 238.57 | 229.04
2018-01-04 23:30 | 221.47 | 211.62
2018-01-05 | 188.87 | 178
2018-01-05 00:30 | 175.24 | 165.1
2018-01-05 01:00 | 173.44 | 163.62
2018-01-05 01:30 | 172.79 | 162.95
2018-01-05 02:00 | 172.35 | 162.32
2018-01-05 02:30 | 172.1 | 162.01
2018-01-05 03:00 | 171.81 | 161.58
2018-01-05 03:30 | 171.74 | 161.65
2018-01-05 04:00 | 171.51 | 161.37
2018-01-05 04:30 | 171.01 | 160.84
2018-01-05 05:00 | 171.4 | 161.42
2018-01-05 05:30 | 172.01 | 162.26
2018-01-05 06:00 | 172.06 | 162.43
2018-01-05 06:30 | 173.6 | 163.53
2018-01-05 07:00 | 176.81 | 164.31
2018-01-05 07:30 | 177.23 | 164.7
2018-01-05 08:00 | 177.99 | 165.5
2018-01-05 08:30 | 178.99 | 166.49
2018-01-05 09:00 | 179.26 | 166.72
2018-01-05 09:30 | 179.45 | 167.35
2018-01-05 10:00 | 180.53 | 168.74
2018-01-05 10:30 | 180.77 | 169.37
2018-01-05 11:00 | 209.09 | 198.39
2018-01-05 11:30 | 235.45 | 225.14
2018-01-05 12:00 | 242.14 | 232.25
2018-01-05 12:30 | 243.19 | 233.67
2018-01-05 13:00 | 244.16 | 235.07
2018-01-05 13:30 | 245.5 | 236.65
2018-01-05 14:00 | 245.28 | 236.56
2018-01-05 14:30 | 246.08 | 237.48
2018-01-05 15:00 | 247.77 | 239.4
2018-01-05 15:30 | 249.87 | 241.85
2018-01-05 16:00 | 249.88 | 242.11
2018-01-05 16:30 | 251.11 | 243.34
2018-01-05 17:00 | 252.6 | 244.76
2018-01-05 17:30 | 252.61 | 244.48
2018-01-05 18:00 | 252.88 | 244.52
2018-01-05 18:30 | 253.44 | 245.36
2018-01-05 19:00 | 253.75 | 245.54
2018-01-05 19:30 | 254.3 | 246.17
2018-01-05 20:00 | 254.13 | 245.8
2018-01-05 20:30 | 252.7 | 244.11
2018-01-05 21:00 | 249.9 | 241.8
2018-01-05 21:30 | 231.78 | 224.38
2018-01-05 22:00 | 198.09 | 190.04
2018-01-05 22:30 | 185.44 | 177.07
2018-01-05 23:00 | 183.22 | 174.48
2018-01-05 23:30 | 181.83 | 172.79
2018-01-06 | 180.31 | 170.82
2018-01-06 00:30 | 179.61 | 169.97
2018-01-06 01:00 | 177.78 | 168.3
2018-01-06 01:30 | 177.05 | 167.58
2018-01-06 02:00 | 176.36 | 166.98
2018-01-06 02:30 | 176.04 | 166.43
2018-01-06 03:00 | 175.5 | 165.8
2018-01-06 03:30 | 175.09 | 165.42
2018-01-06 04:00 | 175.08 | 165.35
2018-01-06 04:30 | 174.51 | 164.7
2018-01-06 05:00 | 174.62 | 164.68
2018-01-06 05:30 | 173.99 | 164.1
2018-01-06 06:00 | 173.3 | 163.96
2018-01-06 06:30 | 174.03 | 164.84
2018-01-06 07:00 | 175.25 | 166.05
2018-01-06 07:30 | 176.05 | 166.95
2018-01-06 08:00 | 177.23 | 167.29
2018-01-06 08:30 | 178.47 | 167.63
2018-01-06 09:00 | 179.24 | 168.41
2018-01-06 09:30 | 179.92 | 169.25
2018-01-06 10:00 | 180.17 | 170.57
2018-01-06 10:30 | 181.14 | 171.68
2018-01-06 11:00 | 204.68 | 195.01
2018-01-06 11:30 | 236.97 | 227.7
2018-01-06 12:00 | 243.42 | 234.35
2018-01-06 12:30 | 244.46 | 235.92
2018-01-06 13:00 | 244.69 | 236.69
2018-01-06 13:30 | 245.8 | 237.76
2018-01-06 14:00 | 245.59 | 237.62
2018-01-06 14:30 | 246.26 | 237.74
2018-01-06 15:00 | 246.72 | 238.28
2018-01-06 15:30 | 247.31 | 239.42
2018-01-06 16:00 | 248.1 | 240.64
2018-01-06 16:30 | 250.4 | 242.79
2018-01-06 17:00 | 252.09 | 244.21
2018-01-06 17:30 | 253.84 | 245.87
2018-01-06 18:00 | 255.26 | 247.43
2018-01-06 18:30 | 256.47 | 248.8
2018-01-06 19:00 | 256.45 | 248.66
2018-01-06 19:30 | 256.25 | 248.54
2018-01-06 20:00 | 255.92 | 248.33
2018-01-06 20:30 | 254.29 | 246.27
2018-01-06 21:00 | 251.86 | 243.41
2018-01-06 21:30 | 249.14 | 241.13
2018-01-06 22:00 | 229.76 | 222.2
2018-01-06 22:30 | 196.2 | 188
2018-01-06 23:00 | 181.05 | 172.26
2018-01-06 23:30 | 179.78 | 170.59
2018-01-07 | 176.62 | 168.74
2018-01-07 00:30 | 175.71 | 167.79
2018-01-07 01:00 | 174.48 | 166.49
2018-01-07 01:30 | 173.19 | 165.03
2018-01-07 02:00 | 172.84 | 164.76
2018-01-07 02:30 | 171.85 | 163.73
2018-01-07 03:00 | 171.14 | 162.92
2018-01-07 03:30 | 170.69 | 162.39
2018-01-07 04:00 | 170.7 | 162.44
2018-01-07 04:30 | 170.25 | 161.95
2018-01-07 05:00 | 170.62 | 162.02
2018-01-07 05:30 | 169.29 | 161.36
2018-01-07 06:00 | 168.36 | 161.25
2018-01-07 06:30 | 170.7 | 162.51
2018-01-07 07:00 | 167.51 | 158.98
2018-01-07 07:30 | 171.02 | 163.01
2018-01-07 08:00 | 173.48 | 164.67
2018-01-07 08:30 | 173.25 | 163.91
2018-01-07 09:00 | 174.06 | 164.7
2018-01-07 09:30 | 175.21 | 166.04
2018-01-07 10:00 | 176.74 | 168.57
2018-01-07 10:30 | 177.32 | 168.95
2018-01-07 11:00 | 178.45 | 170.06
2018-01-07 11:30 | 181.12 | 172.13
2018-01-07 12:00 | 211.77 | 204.23
2018-01-07 12:30 | 236.98 | 229.19
2018-01-07 13:00 | 244.23 | 236.65
2018-01-07 13:30 | 245 | 237.45
2018-01-07 14:00 | 245.84 | 238.6
2018-01-07 14:30 | 246.63 | 239.22
2018-01-07 15:00 | 247.33 | 240.2
2018-01-07 15:30 | 249.37 | 242.41
2018-01-07 16:00 | 250.56 | 243.13
2018-01-07 16:30 | 252.13 | 245.06
2018-01-07 17:00 | 253.44 | 246.18
2018-01-07 17:30 | 255.64 | 248.4
2018-01-07 18:00 | 256.99 | 250.14
2018-01-07 18:30 | 257.93 | 251.19
2018-01-07 19:00 | 258.08 | 251.35
2018-01-07 19:30 | 257.65 | 250.88
2018-01-07 20:00 | 257.05 | 250.06
2018-01-07 20:30 | 255.57 | 247.87
2018-01-07 21:00 | 252.81 | 244.13
2018-01-07 21:30 | 249.5 | 241.03
2018-01-07 22:00 | 246.79 | 237.66
2018-01-07 22:30 | 244.45 | 234.82
2018-01-07 23:00 | 242.36 | 231.94
2018-01-07 23:30 | 224.51 | 213.83
2018-01-08 | 191.75 | 180.69
2018-01-08 00:30 | 177.22 | 166.41
2018-01-08 01:00 | 176.22 | 165.65
2018-01-08 01:30 | 175.47 | 164.32
2018-01-08 02:00 | 176.1 | 164.85
2018-01-08 02:30 | 174.86 | 163.63
2018-01-08 03:00 | 174.32 | 162.99
2018-01-08 03:30 | 173.68 | 162.1
2018-01-08 04:00 | 173.74 | 161.92
2018-01-08 04:30 | 174.05 | 162.35
2018-01-08 05:00 | 174.16 | 162.46
2018-01-08 05:30 | 174.6 | 162.47
2018-01-08 06:00 | 174.61 | 162.85
2018-01-08 06:30 | 176.81 | 165.34
2018-01-08 07:00 | 206.09 | 195.25
2018-01-08 07:30 | 229.92 | 220.06
2018-01-08 08:00 | 238.1 | 228.53
2018-01-08 08:30 | 238.54 | 228.78
2018-01-08 09:00 | 239.91 | 230.35
2018-01-08 09:30 | 240.07 | 230.54
2018-01-08 10:00 | 241.12 | 232.01
2018-01-08 10:30 | 243.72 | 234.46
2018-01-08 11:00 | 244.01 | 235.22
2018-01-08 11:30 | 245.19 | 236.42
2018-01-08 12:00 | 246.23 | 237.77
2018-01-08 12:30 | 247.01 | 239.03
2018-01-08 13:00 | 248.13 | 240.54
2018-01-08 13:30 | 249.24 | 241.57
2018-01-08 14:00 | 250.63 | 243.05
2018-01-08 14:30 | 252.03 | 244.34
2018-01-08 15:00 | 253.79 | 246.1
2018-01-08 15:30 | 255.1 | 247.45
2018-01-08 16:00 | 256.19 | 248.74
2018-01-08 16:30 | 257.88 | 250.42
2018-01-08 17:00 | 258.47 | 251.06
2018-01-08 17:30 | 257.92 | 250.09
2018-01-08 18:00 | 257.48 | 249.62
2018-01-08 18:30 | 258.37 | 250.31
2018-01-08 19:00 | 258.31 | 250.37
2018-01-08 19:30 | 258.55 | 250.58
2018-01-08 20:00 | 257.09 | 248.96
2018-01-08 20:30 | 255 | 246.16
2018-01-08 21:00 | 252.03 | 242.64
2018-01-08 21:30 | 247.98 | 239.37
2018-01-08 22:00 | 245.44 | 236.65
2018-01-08 22:30 | 242.57 | 233.15
2018-01-08 23:00 | 240.01 | 230.75
2018-01-08 23:30 | 220.71 | 211.39
2018-01-09 | 184.09 | 174.54
2018-01-09 00:30 | 174.71 | 164.88
2018-01-09 01:00 | 173.21 | 163.68
2018-01-09 01:30 | 172.03 | 162.88
2018-01-09 02:00 | 171.71 | 162.23
2018-01-09 02:30 | 171.32 | 161.47
2018-01-09 03:00 | 169.86 | 160.12
2018-01-09 03:30 | 169.63 | 160.06
2018-01-09 04:00 | 168.55 | 159.12
2018-01-09 04:30 | 168.83 | 159.47
2018-01-09 05:00 | 169.86 | 160.75
2018-01-09 05:30 | 170.13 | 161.23
2018-01-09 06:00 | 171.05 | 162.49
2018-01-09 06:30 | 173.34 | 164.3
2018-01-09 07:00 | 204.15 | 194.29
2018-01-09 07:30 | 229.27 | 219.82
2018-01-09 08:00 | 237.15 | 227.38
2018-01-09 08:30 | 238.99 | 229.36
2018-01-09 09:00 | 238.95 | 229.61
2018-01-09 09:30 | 238.36 | 229.08
2018-01-09 10:00 | 239.39 | 230.69
2018-01-09 10:30 | 239.6 | 230.93
2018-01-09 11:00 | 241.14 | 232.93
2018-01-09 11:30 | 241.7 | 233.56
2018-01-09 12:00 | 243.15 | 234.97
2018-01-09 12:30 | 245.18 | 236.74
2018-01-09 13:00 | 246.9 | 238.85
2018-01-09 13:30 | 248.04 | 240.11
2018-01-09 14:00 | 248.74 | 240.92
2018-01-09 14:30 | 249.59 | 242.01
2018-01-09 15:00 | 250.38 | 243.04
2018-01-09 15:30 | 251.72 | 244.54
2018-01-09 16:00 | 252.53 | 245.54
2018-01-09 16:30 | 254.7 | 247.96
2018-01-09 17:00 | 256.71 | 250.31
2018-01-09 17:30 | 257.52 | 250.96
2018-01-09 18:00 | 259.65 | 253.19
2018-01-09 18:30 | 260.56 | 254.01
2018-01-09 19:00 | 260.99 | 254.53
2018-01-09 19:30 | 260.75 | 254.36
2018-01-09 20:00 | 259.39 | 252.98
2018-01-09 20:30 | 257.39 | 250.44
2018-01-09 21:00 | 254.15 | 246.55
2018-01-09 21:30 | 250.55 | 243.67
2018-01-09 22:00 | 248.08 | 240.36
2018-01-09 22:30 | 245.99 | 237.47
2018-01-09 23:00 | 243.26 | 235.11
2018-01-09 23:30 | 241.18 | 233.36
2018-01-10 | 223.93 | 216.01
2018-01-10 00:30 | 191.17 | 182.77
2018-01-10 01:00 | 177.78 | 169.07
2018-01-10 01:30 | 177.7 | 168.88
2018-01-10 02:00 | 176.84 | 167.81
2018-01-10 02:30 | 175.95 | 166.76
2018-01-10 03:00 | 176.11 | 166.56
2018-01-10 03:30 | 175.29 | 166.16
2018-01-10 04:00 | 174.7 | 165.5
2018-01-10 04:30 | 174.61 | 165.44
2018-01-10 05:00 | 175.22 | 166.08
2018-01-10 05:30 | 175.29 | 166.42
2018-01-10 06:00 | 175.19 | 166.51
2018-01-10 06:30 | 178.02 | 168.33
2018-01-10 07:00 | 206.78 | 197.01
2018-01-10 07:30 | 232.57 | 223.39
2018-01-10 08:00 | 240.48 | 231.16
2018-01-10 08:30 | 241.49 | 232.25
2018-01-10 09:00 | 242.2 | 232.87
2018-01-10 09:30 | 242.83 | 232.97
2018-01-10 10:00 | 243.76 | 234.21
2018-01-10 10:30 | 244.24 | 234.81
2018-01-10 11:00 | 245.2 | 235.92
2018-01-10 11:30 | 246.46 | 237.33
2018-01-10 12:00 | 247.8 | 238.83
2018-01-10 12:30 | 231.21 | 222.56
2018-01-10 13:00 | 230.11 | 221.65
2018-01-10 13:30 | 231.15 | 222.79
2018-01-10 14:00 | 232.09 | 224.07
2018-01-10 14:30 | 233.81 | 226.04
2018-01-10 15:00 | 240.13 | 232.25
2018-01-10 15:30 | 247.89 | 240.05
2018-01-10 16:00 | 256.46 | 248.46
2018-01-10 16:30 | 257.77 | 250.02
2018-01-10 17:00 | 259.76 | 252.26
2018-01-10 17:30 | 260.38 | 252.84
2018-01-10 18:00 | 261.7 | 254.2
2018-01-10 18:30 | 263.15 | 255.56
2018-01-10 19:00 | 262.86 | 255.54
2018-01-10 19:30 | 262.23 | 255.24
2018-01-10 20:00 | 261.4 | 254.47
2018-01-10 20:30 | 260.05 | 252.03
2018-01-10 21:00 | 257.27 | 248.23
2018-01-10 21:30 | 252.85 | 244.7
2018-01-10 22:00 | 249.59 | 241.17
2018-01-10 22:30 | 246.37 | 237.59
2018-01-10 23:00 | 244.38 | 235.36
2018-01-10 23:30 | 225.8 | 216.56
2018-01-11 | 189.3 | 180.22
2018-01-11 00:30 | 178.86 | 170.64
2018-01-11 01:00 | 177.67 | 169.33
2018-01-11 01:30 | 177.38 | 168.89
2018-01-11 02:00 | 176.8 | 168.14
2018-01-11 02:30 | 175.91 | 167.2
2018-01-11 03:00 | 175.49 | 166.74
2018-01-11 03:30 | 174.62 | 165.8
2018-01-11 04:00 | 174.07 | 165.02
2018-01-11 04:30 | 173.72 | 164.64
2018-01-11 05:00 | 173.89 | 164.64
2018-01-11 05:30 | 174.46 | 165.54
2018-01-11 06:00 | 174.99 | 166.06
2018-01-11 06:30 | 205.32 | 196.27
2018-01-11 07:00 | 232.56 | 222.33
2018-01-11 07:30 | 240.14 | 229.71
2018-01-11 08:00 | 240.36 | 229.76
2018-01-11 08:30 | 240.29 | 230.13
2018-01-11 09:00 | 240.7 | 230.72
2018-01-11 09:30 | 242.44 | 231.39
2018-01-11 10:00 | 243.47 | 232.39
2018-01-11 10:30 | 244.07 | 233.47
2018-01-11 11:00 | 243.74 | 234.33
2018-01-11 11:30 | 244.04 | 234.94
2018-01-11 12:00 | 245.19 | 236.26
2018-01-11 12:30 | 246.68 | 237.92
2018-01-11 13:00 | 248.27 | 239.55
2018-01-11 13:30 | 249.64 | 241.16
2018-01-11 14:00 | 250.38 | 242.59
2018-01-11 14:30 | 250.56 | 242.94
2018-01-11 15:00 | 251.37 | 243.55
2018-01-11 15:30 | 252.22 | 244.33
2018-01-11 16:00 | 252.4 | 244.91
2018-01-11 16:30 | 254.11 | 246.88
2018-01-11 17:00 | 256.45 | 249.41
2018-01-11 17:30 | 257.18 | 250.18
2018-01-11 18:00 | 258.28 | 251.28
2018-01-11 18:30 | 259.59 | 252.24
2018-01-11 19:00 | 260.2 | 252.67
2018-01-11 19:30 | 259.84 | 252.43
2018-01-11 20:00 | 259.25 | 251.71
2018-01-11 20:30 | 257.15 | 249.24
2018-01-11 21:00 | 253.83 | 245.49
2018-01-11 21:30 | 250.86 | 242.84
2018-01-11 22:00 | 248.23 | 240.05
2018-01-11 22:30 | 244.91 | 236.76
2018-01-11 23:00 | 242.89 | 234.05
2018-01-11 23:30 | 242.13 | 232.5
2018-01-12 | 240.31 | 230.55
2018-01-12 00:30 | 238.79 | 229.44
2018-01-12 01:00 | 238.08 | 228.51
2018-01-12 01:30 | 237.48 | 227.83
2018-01-12 02:00 | 236.87 | 227.11
2018-01-12 02:30 | 236.32 | 226.48
2018-01-12 03:00 | 235.9 | 225.98
2018-01-12 03:30 | 235.65 | 225.68
2018-01-12 04:00 | 235.42 | 225.36
2018-01-12 04:30 | 235.64 | 225.75
2018-01-12 05:00 | 235.65 | 226.09
2018-01-12 05:30 | 236.4 | 226.65
2018-01-12 06:00 | 237.31 | 227.59
2018-01-12 06:30 | 238.21 | 229.04
2018-01-12 07:00 | 239.04 | 230.13
2018-01-12 07:30 | 239.02 | 231.06
2018-01-12 08:00 | 239.1 | 231.49
2018-01-12 08:30 | 239.63 | 232.33
2018-01-12 09:00 | 239.93 | 232.28
2018-01-12 09:30 | 239.89 | 232.25
2018-01-12 10:00 | 241.02 | 233.71
2018-01-12 10:30 | 242.11 | 234.93
2018-01-12 11:00 | 242.92 | 235.98
2018-01-12 11:30 | 244.63 | 237.53
2018-01-12 12:00 | 246.62 | 238.95
2018-01-12 12:30 | 247.89 | 240.1
2018-01-12 13:00 | 249.15 | 241.42
2018-01-12 13:30 | 250.35 | 242.82
2018-01-12 14:00 | 251.05 | 243.72
2018-01-12 14:30 | 251.61 | 244.87
2018-01-12 15:00 | 252.01 | 245.48
2018-01-12 15:30 | 252.57 | 246.55
2018-01-12 16:00 | 254.15 | 248.25
2018-01-12 16:30 | 255.35 | 249.8
2018-01-12 17:00 | 257.51 | 252.04
2018-01-12 17:30 | 259.08 | 253.47
2018-01-12 18:00 | 260.75 | 254.98
2018-01-12 18:30 | 261.41 | 255.46
2018-01-12 19:00 | 261.38 | 255.41
2018-01-12 19:30 | 261.29 | 255.44
2018-01-12 20:00 | 260.44 | 254.54
2018-01-12 20:30 | 258.57 | 252.15
2018-01-12 21:00 | 256.58 | 249.44
2018-01-12 21:30 | 253.51 | 246.74
2018-01-12 22:00 | 250.57 | 243.46
2018-01-12 22:30 | 247.58 | 240.27
2018-01-12 23:00 | 245.25 | 237.42
2018-01-12 23:30 | 244.06 | 235.66
2018-01-13 | 242.3 | 233.63
2018-01-13 00:30 | 240.22 | 232.46
2018-01-13 01:00 | 239.46 | 231.44
2018-01-13 01:30 | 238.57 | 230.23
2018-01-13 02:00 | 237.97 | 229.23
2018-01-13 02:30 | 237.74 | 228.53
2018-01-13 03:00 | 237.58 | 228.18
2018-01-13 03:30 | 237.35 | 227.83
2018-01-13 04:00 | 236.99 | 227.55
2018-01-13 04:30 | 236.88 | 227.49
2018-01-13 05:00 | 237.08 | 227.77
2018-01-13 05:30 | 237.37 | 228.04
2018-01-13 06:00 | 237.37 | 228.08
2018-01-13 06:30 | 237.32 | 228.82
2018-01-13 07:00 | 237.19 | 229.4
2018-01-13 07:30 | 238.07 | 230.5
2018-01-13 08:00 | 238.44 | 231.05
2018-01-13 08:30 | 239.72 | 231.76
2018-01-13 09:00 | 212.05 | 204.36
2018-01-13 09:30 | 185.54 | 178.33
2018-01-13 10:00 | 187.3 | 180.38
2018-01-13 10:30 | 189.93 | 181.93
2018-01-13 11:00 | 192.48 | 183.94
2018-01-13 11:30 | 193.94 | 185.7
2018-01-13 12:00 | 204.47 | 196.5
2018-01-13 12:30 | 245.54 | 237.32
2018-01-13 13:00 | 252.32 | 243.19
2018-01-13 13:30 | 253.08 | 244.67
2018-01-13 14:00 | 253.56 | 245.52
2018-01-13 14:30 | 253.55 | 245.33
2018-01-13 15:00 | 253.45 | 245.44
2018-01-13 15:30 | 253.62 | 245.64
2018-01-13 16:00 | 253.46 | 245.33
2018-01-13 16:30 | 252.83 | 244.63
2018-01-13 17:00 | 224.42 | 216.79
2018-01-13 17:30 | 222 | 214.36
2018-01-13 18:00 | 221.86 | 214.52
2018-01-13 18:30 | 221.03 | 213.91
2018-01-13 19:00 | 224.03 | 218.81
2018-01-13 19:30 | 224.5 | 219.36
2018-01-13 20:00 | 224.37 | 219.15
2018-01-13 20:30 | 225.27 | 220.14
2018-01-13 21:00 | 239.01 | 231.55
2018-01-13 21:30 | 248.55 | 240.19
2018-01-13 22:00 | 245.85 | 237.49
2018-01-13 22:30 | 243.35 | 235.16
2018-01-13 23:00 | 241.67 | 233.18
2018-01-13 23:30 | 225.1 | 216.37
2018-01-14 | 189.81 | 180.87
2018-01-14 00:30 | 180.43 | 171.39
2018-01-14 01:00 | 179.4 | 170.63
2018-01-14 01:30 | 179.01 | 169.94
2018-01-14 02:00 | 178.19 | 168.79
2018-01-14 02:30 | 176.87 | 167.22
2018-01-14 03:00 | 176.45 | 166.73
2018-01-14 03:30 | 175.91 | 166.32
2018-01-14 04:00 | 175.27 | 165.65
2018-01-14 04:30 | 175.86 | 166.48
2018-01-14 05:00 | 175.8 | 166.39
2018-01-14 05:30 | 175.9 | 166.4
2018-01-14 06:00 | 175.56 | 166.01
2018-01-14 06:30 | 175.65 | 166.17
2018-01-14 07:00 | 176.57 | 167.33
2018-01-14 07:30 | 176.58 | 167.51
2018-01-14 08:00 | 177.55 | 168.01
2018-01-14 08:30 | 177.88 | 167.99
2018-01-14 09:00 | 179.37 | 168.29
2018-01-14 09:30 | 179.71 | 168.4
2018-01-14 10:00 | 179.92 | 168.2
2018-01-14 10:30 | 181.12 | 169.61
2018-01-14 11:00 | 185.38 | 173.63
2018-01-14 11:30 | 213.15 | 202.31
2018-01-14 12:00 | 238.54 | 227.94
2018-01-14 12:30 | 244.54 | 234.41
2018-01-14 13:00 | 245.01 | 235.13
2018-01-14 13:30 | 219.3 | 211.29
2018-01-14 14:00 | 215.07 | 207.05
2018-01-14 14:30 | 211.79 | 203.93
2018-01-14 15:00 | 210.47 | 202.3
2018-01-14 15:30 | 211.1 | 202.77
2018-01-14 16:00 | 212.18 | 203.8
2018-01-14 16:30 | 213.52 | 205.17
2018-01-14 17:00 | 215.11 | 206.63
2018-01-14 17:30 | 217.11 | 208.63
2018-01-14 18:00 | 217.86 | 209.53
2018-01-14 18:30 | 218.35 | 210.01
2018-01-14 19:00 | 218.04 | 209.59
2018-01-14 19:30 | 217.24 | 208.84
2018-01-14 20:00 | 216.86 | 208.36
2018-01-14 20:30 | 243.14 | 233.4
2018-01-14 21:00 | 247.23 | 237.34
2018-01-14 21:30 | 244.99 | 235.91
2018-01-14 22:00 | 242.37 | 233.49
2018-01-14 22:30 | 240.09 | 231.31
2018-01-14 23:00 | 238.77 | 229.77
2018-01-14 23:30 | 217.51 | 208.47
2018-01-15 | 180.38 | 171.06
2018-01-15 00:30 | 170.91 | 161.42
2018-01-15 01:00 | 170.38 | 160.94
2018-01-15 01:30 | 168.97 | 159.72
2018-01-15 02:00 | 168.64 | 159.6
2018-01-15 02:30 | 167.18 | 158.41
2018-01-15 03:00 | 166.46 | 157.74
2018-01-15 03:30 | 166.65 | 158.01
2018-01-15 04:00 | 166.33 | 158.1
2018-01-15 04:30 | 166.28 | 157.66
2018-01-15 05:00 | 167.55 | 158.43
2018-01-15 05:30 | 168.35 | 159.52
2018-01-15 06:00 | 168.67 | 160.53
2018-01-15 06:30 | 169.7 | 161.03
2018-01-15 07:00 | 172.97 | 162.85
2018-01-15 07:30 | 174.21 | 163.97
2018-01-15 08:00 | 175.03 | 164.45
2018-01-15 08:30 | 175.17 | 164.8
2018-01-15 09:00 | 177.45 | 167.71
2018-01-15 09:30 | 176.45 | 166.64
2018-01-15 10:00 | 205.16 | 195.63
2018-01-15 10:30 | 229.08 | 219.31
2018-01-15 11:00 | 236.31 | 226.78
2018-01-15 11:30 | 237.09 | 227.75
2018-01-15 12:00 | 238.19 | 228.89
2018-01-15 12:30 | 238.6 | 229.16
2018-01-15 13:00 | 239.03 | 229.6
2018-01-15 13:30 | 240.62 | 231.35
2018-01-15 14:00 | 241.72 | 232.84
2018-01-15 14:30 | 243.29 | 234.71
2018-01-15 15:00 | 243.59 | 235.07
2018-01-15 15:30 | 243.64 | 235.15
2018-01-15 16:00 | 244.73 | 236.49
2018-01-15 16:30 | 246.16 | 237.91
2018-01-15 17:00 | 247.87 | 239.93
2018-01-15 17:30 | 249.56 | 241.52
2018-01-15 18:00 | 250.71 | 243.34
2018-01-15 18:30 | 251.63 | 244.2
2018-01-15 19:00 | 252.05 | 244.74
2018-01-15 19:30 | 252.06 | 244.74
2018-01-15 20:00 | 252.21 | 244.74
2018-01-15 20:30 | 250.96 | 243.29
2018-01-15 21:00 | 248.26 | 240.16
2018-01-15 21:30 | 245.36 | 237.87
2018-01-15 22:00 | 224.3 | 216.86
2018-01-15 22:30 | 185.14 | 177.39
2018-01-15 23:00 | 175.23 | 167.01
2018-01-15 23:30 | 173.5 | 165.2
2018-01-16 | 172.79 | 164
2018-01-16 00:30 | 171.34 | 162.93
2018-01-16 01:00 | 170.25 | 162
2018-01-16 01:30 | 168.84 | 161.33
2018-01-16 02:00 | 168.47 | 160.6
2018-01-16 02:30 | 167.82 | 160.11
2018-01-16 03:00 | 167.55 | 159.83
2018-01-16 03:30 | 167.46 | 159.9
2018-01-16 04:00 | 166.88 | 159.37
2018-01-16 04:30 | 166.57 | 159.17
2018-01-16 05:00 | 166.87 | 159.76
2018-01-16 05:30 | 168.47 | 161.08
2018-01-16 06:00 | 169.49 | 161.94
2018-01-16 06:30 | 171.46 | 163.94
2018-01-16 07:00 | 173 | 164.51
2018-01-16 07:30 | 174.48 | 165.93
2018-01-16 08:00 | 175.32 | 167.05
2018-01-16 08:30 | 174.67 | 166.39
2018-01-16 09:00 | 175.34 | 166.95
2018-01-16 09:30 | 175.33 | 166.98
2018-01-16 10:00 | 176.12 | 167.44
2018-01-16 10:30 | 175.88 | 167.62
2018-01-16 11:00 | 175.58 | 167.9
2018-01-16 11:30 | 177.07 | 169.49
2018-01-16 12:00 | 177.98 | 170
2018-01-16 12:30 | 178.33 | 170.22
2018-01-16 13:00 | 179.94 | 171.97
2018-01-16 13:30 | 210.37 | 202.76
2018-01-16 14:00 | 237.29 | 229.8
2018-01-16 14:30 | 244.11 | 236.72
2018-01-16 15:00 | 244.93 | 237.51
2018-01-16 15:30 | 247.35 | 240.12
2018-01-16 16:00 | 248.04 | 240.85
2018-01-16 16:30 | 249 | 242.03
2018-01-16 17:00 | 251.05 | 243.78
2018-01-16 17:30 | 251.84 | 244.48
2018-01-16 18:00 | 253.46 | 246.18
2018-01-16 18:30 | 253.67 | 246.19
2018-01-16 19:00 | 253.09 | 245.61
2018-01-16 19:30 | 252.68 | 245.31
2018-01-16 20:00 | 252.44 | 244.97
2018-01-16 20:30 | 250.66 | 242.95
2018-01-16 21:00 | 247.07 | 238.78
2018-01-16 21:30 | 243.42 | 236.16
2018-01-16 22:00 | 221.41 | 214.03
2018-01-16 22:30 | 184.15 | 176.37
2018-01-16 23:00 | 173.55 | 165.49
2018-01-16 23:30 | 172.66 | 164.22
2018-01-17 | 170.72 | 162.8
2018-01-17 00:30 | 169.39 | 161.7
2018-01-17 01:00 | 168.26 | 161.27
2018-01-17 01:30 | 166.96 | 159.85
2018-01-17 02:00 | 167.04 | 159.21
2018-01-17 02:30 | 168.02 | 158.76
2018-01-17 03:00 | 167.51 | 158.21
2018-01-17 03:30 | 166.16 | 157.16
2018-01-17 04:00 | 166.21 | 157.41
2018-01-17 04:30 | 166.35 | 157.27
2018-01-17 05:00 | 167.37 | 157.96
2018-01-17 05:30 | 167.83 | 158.46
2018-01-17 06:00 | 169.83 | 160.36
2018-01-17 06:30 | 171.96 | 161.5
2018-01-17 07:00 | 174.39 | 163.49
2018-01-17 07:30 | 174.86 | 164.04
2018-01-17 08:00 | 174.48 | 163.79
2018-01-17 08:30 | 172.77 | 162.55
2018-01-17 09:00 | 172.42 | 162.3
2018-01-17 09:30 | 172.74 | 162.6
2018-01-17 10:00 | 173.34 | 163.7
2018-01-17 10:30 | 173.47 | 164.04
2018-01-17 11:00 | 202.23 | 193.77
2018-01-17 11:30 | 229.17 | 219.73
2018-01-17 12:00 | 236.86 | 226.91
2018-01-17 12:30 | 237.66 | 227.48
2018-01-17 13:00 | 239.86 | 229.85
2018-01-17 13:30 | 240.92 | 230.83
2018-01-17 14:00 | 241.94 | 232.28
2018-01-17 14:30 | 242.56 | 233.23
2018-01-17 15:00 | 243.86 | 234.56
2018-01-17 15:30 | 245.01 | 235.57
2018-01-17 16:00 | 246.8 | 237.6
2018-01-17 16:30 | 248 | 238.72
2018-01-17 17:00 | 249.42 | 239.92
2018-01-17 17:30 | 250.51 | 240.77
2018-01-17 18:00 | 251.3 | 241.36
2018-01-17 18:30 | 251.61 | 241.83
2018-01-17 19:00 | 252.29 | 242.44
2018-01-17 19:30 | 254.8 | 245.25
2018-01-17 20:00 | 256.99 | 247.67
2018-01-17 20:30 | 254.89 | 245.17
2018-01-17 21:00 | 252.03 | 242.14
2018-01-17 21:30 | 248.52 | 239.57
2018-01-17 22:00 | 245.45 | 235.67
2018-01-17 22:30 | 241.88 | 231.87
2018-01-17 23:00 | 238.42 | 229.5
2018-01-17 23:30 | 219.26 | 210.42
2018-01-18 | 181.83 | 172.81
2018-01-18 00:30 | 173.04 | 163.8
2018-01-18 01:00 | 171.45 | 162.23
2018-01-18 01:30 | 171.52 | 162.1
2018-01-18 02:00 | 170.38 | 161.65
2018-01-18 02:30 | 169.2 | 160.48
2018-01-18 03:00 | 169 | 160.3
2018-01-18 03:30 | 168.69 | 159.96
2018-01-18 04:00 | 168.38 | 159.71
2018-01-18 04:30 | 168.9 | 160.26
2018-01-18 05:00 | 169.26 | 161
2018-01-18 05:30 | 169.33 | 161.12
2018-01-18 06:00 | 173.42 | 162.3
2018-01-18 06:30 | 175.79 | 164.52
2018-01-18 07:00 | 177.22 | 165.88
2018-01-18 07:30 | 177.05 | 166.28
2018-01-18 08:00 | 177.57 | 167.73
2018-01-18 08:30 | 177.56 | 168.03
2018-01-18 09:00 | 178.65 | 168.94
2018-01-18 09:30 | 179.94 | 169.45
2018-01-18 10:00 | 180.74 | 170.35
2018-01-18 10:30 | 181.66 | 171.36
2018-01-18 11:00 | 181.88 | 172.07
2018-01-18 11:30 | 184.66 | 174.86
2018-01-18 12:00 | 212.76 | 204.4
2018-01-18 12:30 | 238.43 | 230.51
2018-01-18 13:00 | 246.28 | 238.48
2018-01-18 13:30 | 248.09 | 239.97
2018-01-18 14:00 | 250.08 | 242.6
2018-01-18 14:30 | 250.75 | 243.65
2018-01-18 15:00 | 250.71 | 243.88
2018-01-18 15:30 | 252.1 | 245.34
2018-01-18 16:00 | 253.42 | 246.89
2018-01-18 16:30 | 255.14 | 248.84
2018-01-18 17:00 | 256.23 | 249.94
2018-01-18 17:30 | 257.23 | 250.5
2018-01-18 18:00 | 259.73 | 252.14
2018-01-18 18:30 | 260.91 | 252.61
2018-01-18 19:00 | 261.37 | 253.06
2018-01-18 19:30 | 261.07 | 252.79
2018-01-18 20:00 | 260.53 | 252.26
2018-01-18 20:30 | 257.49 | 248.68
2018-01-18 21:00 | 253.8 | 244.32
2018-01-18 21:30 | 249.83 | 240.23
2018-01-18 22:00 | 246.04 | 236.28
2018-01-18 22:30 | 243.26 | 232.89
2018-01-18 23:00 | 241.04 | 230.41
2018-01-18 23:30 | 221.03 | 210.29
2018-01-19 | 183.13 | 173.22
2018-01-19 00:30 | 174.84 | 165.31
2018-01-19 01:00 | 174.74 | 165.31
2018-01-19 01:30 | 174.32 | 164.95
2018-01-19 02:00 | 173.29 | 164.14
2018-01-19 02:30 | 172.56 | 163.58
2018-01-19 03:00 | 172.24 | 163.39
2018-01-19 03:30 | 171.28 | 162.72
2018-01-19 04:00 | 170.49 | 162.11
2018-01-19 04:30 | 169.88 | 161.71
2018-01-19 05:00 | 170.18 | 161.08
2018-01-19 05:30 | 172.16 | 162.55
2018-01-19 06:00 | 172.63 | 163.38
2018-01-19 06:30 | 175.65 | 165.55
2018-01-19 07:00 | 178.38 | 167.68
2018-01-19 07:30 | 180.12 | 169.52
2018-01-19 08:00 | 180.47 | 170.44
2018-01-19 08:30 | 180.57 | 170.95
2018-01-19 09:00 | 181.5 | 171.78
2018-01-19 09:30 | 182.27 | 173
2018-01-19 10:00 | 184.62 | 175.71
2018-01-19 10:30 | 185 | 176.63
2018-01-19 11:00 | 186.84 | 178.67
2018-01-19 11:30 | 188.06 | 180.18
2018-01-19 12:00 | 189.04 | 181.68
2018-01-19 12:30 | 218.63 | 211.7
2018-01-19 13:00 | 244.99 | 237.8
2018-01-19 13:30 | 250.33 | 243.14
2018-01-19 14:00 | 251.62 | 244.87
2018-01-19 14:30 | 252.37 | 245.36
2018-01-19 15:00 | 253.51 | 245.92
2018-01-19 15:30 | 254.76 | 247.08
2018-01-19 16:00 | 256.49 | 248.78
2018-01-19 16:30 | 257.48 | 249.93
2018-01-19 17:00 | 259.04 | 251.23
2018-01-19 17:30 | 260.1 | 251.83
2018-01-19 18:00 | 260.69 | 252.47
2018-01-19 18:30 | 261.09 | 252.93
2018-01-19 19:00 | 261.33 | 253.23
2018-01-19 19:30 | 260.79 | 252.82
2018-01-19 20:00 | 259.05 | 250.91
2018-01-19 20:30 | 257.37 | 248.82
2018-01-19 21:00 | 237.39 | 227.3
2018-01-19 21:30 | 199.95 | 190.35
2018-01-19 22:00 | 189.16 | 179.47
2018-01-19 22:30 | 186.78 | 176.65
2018-01-19 23:00 | 184.59 | 173.58
2018-01-19 23:30 | 182.37 | 171.09
2018-01-20 | 180.37 | 169.28
2018-01-20 00:30 | 178.79 | 168.31
2018-01-20 01:00 | 174.96 | 164.95
2018-01-20 01:30 | 178.57 | 167.92
2018-01-20 02:00 | 179.54 | 169.03
2018-01-20 02:30 | 177.82 | 167.42
2018-01-20 03:00 | 176.93 | 166.59
2018-01-20 03:30 | 176.91 | 166.26
2018-01-20 04:00 | 176.55 | 165.76
2018-01-20 04:30 | 175.83 | 165.05
2018-01-20 05:00 | 175.93 | 165.16
2018-01-20 05:30 | 176.01 | 165.24
2018-01-20 06:00 | 176.06 | 165.1
2018-01-20 06:30 | 176.42 | 165.86
2018-01-20 07:00 | 176.74 | 166.48
2018-01-20 07:30 | 178.02 | 168.1
2018-01-20 08:00 | 180.23 | 168.94
2018-01-20 08:30 | 180.29 | 169.42
2018-01-20 09:00 | 181.85 | 171.29
2018-01-20 09:30 | 182.92 | 172.96
2018-01-20 10:00 | 184.21 | 175.42
2018-01-20 10:30 | 186.71 | 178.37
2018-01-20 11:00 | 188.22 | 179.63
2018-01-20 11:30 | 189.53 | 179.69
2018-01-20 12:00 | 190.26 | 180.58
2018-01-20 12:30 | 191.24 | 181.92
2018-01-20 13:00 | 192.36 | 183.93
2018-01-20 13:30 | 194.66 | 187.62
2018-01-20 14:00 | 195.82 | 189.67
2018-01-20 14:30 | 202.82 | 196.99
2018-01-20 15:00 | 203.88 | 198.52
2018-01-20 15:30 | 205 | 199.67
2018-01-20 16:00 | 206.76 | 200.78
2018-01-20 16:30 | 208.2 | 201.95
2018-01-20 17:00 | 208.55 | 202.38
2018-01-20 17:30 | 210.43 | 204.44
2018-01-20 18:00 | 213.79 | 207.91
2018-01-20 18:30 | 217.8 | 211.83
2018-01-20 19:00 | 217.73 | 211.66
2018-01-20 19:30 | 217.15 | 210.99
2018-01-20 20:00 | 215.87 | 209.65
2018-01-20 20:30 | 212.8 | 206.29
2018-01-20 21:00 | 208.72 | 202.48
2018-01-20 21:30 | 204.25 | 199.15
2018-01-20 22:00 | 201.19 | 196
2018-01-20 22:30 | 198.3 | 192.87
2018-01-20 23:00 | 195.67 | 189.93
2018-01-20 23:30 | 194.36 | 188.35
2018-01-21 | 192.55 | 186.54
2018-01-21 00:30 | 190.92 | 185.12
2018-01-21 01:00 | 189.31 | 183.88
2018-01-21 01:30 | 188.61 | 182.9
2018-01-21 02:00 | 188.56 | 182.66
2018-01-21 02:30 | 187.84 | 181.96
2018-01-21 03:00 | 187.31 | 181.6
2018-01-21 03:30 | 186.93 | 181.15
2018-01-21 04:00 | 186.25 | 180.54
2018-01-21 04:30 | 186.13 | 180.45
2018-01-21 05:00 | 186.04 | 180.43
2018-01-21 05:30 | 186 | 180.47
2018-01-21 06:00 | 185.58 | 180.07
2018-01-21 06:30 | 186.72 | 180.37
2018-01-21 07:00 | 187.37 | 181.02
2018-01-21 07:30 | 187.92 | 181.78
2018-01-21 08:00 | 188.96 | 182.12
2018-01-21 08:30 | 190.17 | 183.11
2018-01-21 09:00 | 190.22 | 183.48
2018-01-21 09:30 | 191.55 | 184.74
2018-01-21 10:00 | 192.63 | 186.14
2018-01-21 10:30 | 192.89 | 186.92
2018-01-21 11:00 | 193.81 | 187.88
2018-01-21 11:30 | 195.63 | 189.17
2018-01-21 12:00 | 197.19 | 190.78
2018-01-21 12:30 | 198.3 | 192.09
2018-01-21 13:00 | 201.09 | 194.56
2018-01-21 13:30 | 202.19 | 195.52
2018-01-21 14:00 | 203.72 | 197.4
2018-01-21 14:30 | 204.22 | 198.38
2018-01-21 15:00 | 205.38 | 200
2018-01-21 15:30 | 206.64 | 200.9
2018-01-21 16:00 | 207.84 | 202.46
2018-01-21 16:30 | 209.91 | 204.59
2018-01-21 17:00 | 210.81 | 205.51
2018-01-21 17:30 | 212.78 | 207.68
2018-01-21 18:00 | 213.89 | 209.3
2018-01-21 18:30 | 214.87 | 210.15
2018-01-21 19:00 | 214.89 | 210.18
2018-01-21 19:30 | 214.61 | 209.79
2018-01-21 20:00 | 213.16 | 208.04
2018-01-21 20:30 | 211.24 | 205.57
2018-01-21 21:00 | 207.88 | 201.68
2018-01-21 21:30 | 204.76 | 198.75
2018-01-21 22:00 | 201.73 | 195.3
2018-01-21 22:30 | 198.68 | 191.82
2018-01-21 23:00 | 196.49 | 189.35
2018-01-21 23:30 | 195.2 | 187.84
2018-01-22 | 184.87 | 177.45
2018-01-22 00:30 | 176.96 | 169.85
2018-01-22 01:00 | 176.04 | 168.88
2018-01-22 01:30 | 175.17 | 167.97
2018-01-22 02:00 | 174.63 | 167.56
2018-01-22 02:30 | 173.85 | 166.99
2018-01-22 03:00 | 173.34 | 166.52
2018-01-22 03:30 | 172.86 | 165.95
2018-01-22 04:00 | 173.15 | 165.93
2018-01-22 04:30 | 172.94 | 165.68
2018-01-22 05:00 | 173.72 | 166.44
2018-01-22 05:30 | 174.46 | 167.29
2018-01-22 06:00 | 175.13 | 168.24
2018-01-22 06:30 | 176.55 | 169.64
2018-01-22 07:00 | 189.78 | 182.66
2018-01-22 07:30 | 193.72 | 186.98
2018-01-22 08:00 | 194.46 | 187.85
2018-01-22 08:30 | 194.19 | 187.65
2018-01-22 09:00 | 196.79 | 189.73
2018-01-22 09:30 | 197.28 | 190.21
2018-01-22 10:00 | 198.48 | 191.77
2018-01-22 10:30 | 198.85 | 192.53
2018-01-22 11:00 | 200.81 | 194.35
2018-01-22 11:30 | 202.54 | 196.05
2018-01-22 12:00 | 203.58 | 197.21
2018-01-22 12:30 | 204.61 | 198.39
2018-01-22 13:00 | 208.01 | 201.47
2018-01-22 13:30 | 209.7 | 203.28
2018-01-22 14:00 | 210.67 | 204.69
2018-01-22 14:30 | 211.9 | 205.8
2018-01-22 15:00 | 212.44 | 206.54
2018-01-22 15:30 | 213.42 | 207.61
2018-01-22 16:00 | 215.19 | 209.87
2018-01-22 16:30 | 216.55 | 211.11
2018-01-22 17:00 | 218.25 | 212.83
2018-01-22 17:30 | 219.38 | 213.63
2018-01-22 18:00 | 221.56 | 215.83
2018-01-22 18:30 | 222.93 | 217.29
2018-01-22 19:00 | 223.04 | 217.5
2018-01-22 19:30 | 222.85 | 217.22
2018-01-22 20:00 | 221.65 | 215.79
2018-01-22 20:30 | 218.85 | 212.59
2018-01-22 21:00 | 213.83 | 207.92
2018-01-22 21:30 | 209.05 | 204.24
2018-01-22 22:00 | 205.16 | 200.05
2018-01-22 22:30 | 201.63 | 196.15
2018-01-22 23:00 | 199.23 | 193.36
2018-01-22 23:30 | 197.53 | 191.67
2018-01-23 | 185.9 | 180.51
2018-01-23 00:30 | 178.18 | 172.74
2018-01-23 01:00 | 177.15 | 171.56
2018-01-23 01:30 | 176.48 | 170.84
2018-01-23 02:00 | 175.58 | 169.85
2018-01-23 02:30 | 174.84 | 169.07
2018-01-23 03:00 | 174.17 | 168.38
2018-01-23 03:30 | 173.56 | 167.77
2018-01-23 04:00 | 173.49 | 167.71
2018-01-23 04:30 | 173.37 | 167.62
2018-01-23 05:00 | 174.22 | 168.53
2018-01-23 05:30 | 175.33 | 169.63
2018-01-23 06:00 | 176.31 | 170.45
2018-01-23 06:30 | 177.73 | 172.25
2018-01-23 07:00 | 177.97 | 172.87
2018-01-23 07:30 | 179.32 | 174.13
2018-01-23 08:00 | 180.6 | 175.27
2018-01-23 08:30 | 180.3 | 175.24
2018-01-23 09:00 | 181.1 | 175.84
2018-01-23 09:30 | 180.94 | 175.93
2018-01-23 10:00 | 193.44 | 188.68
2018-01-23 10:30 | 197.81 | 193.08
2018-01-23 11:00 | 199.19 | 194.58
2018-01-23 11:30 | 201.82 | 197.49
2018-01-23 12:00 | 203.13 | 198.98
2018-01-23 12:30 | 204.39 | 200.27
2018-01-23 13:00 | 207.36 | 203.14
2018-01-23 13:30 | 208.72 | 204.52
2018-01-23 14:00 | 210.8 | 206.61
2018-01-23 14:30 | 211.75 | 207.69
2018-01-23 15:00 | 212.36 | 208.35
2018-01-23 15:30 | 213.24 | 209.36
2018-01-23 16:00 | 215 | 211.59
2018-01-23 16:30 | 216.93 | 213.47
2018-01-23 17:00 | 218.64 | 215.13
2018-01-23 17:30 | 219.25 | 215.85
2018-01-23 18:00 | 221.6 | 218.3
2018-01-23 18:30 | 222.45 | 219.3
2018-01-23 19:00 | 223.03 | 219.9
2018-01-23 19:30 | 223.11 | 219.96
2018-01-23 20:00 | 222.2 | 218.88
2018-01-23 20:30 | 218.85 | 215.1
2018-01-23 21:00 | 214.83 | 210.49
2018-01-23 21:30 | 210.67 | 206.03
2018-01-23 22:00 | 207.05 | 201.88
2018-01-23 22:30 | 202.98 | 197.82
2018-01-23 23:00 | 199.9 | 194.59
2018-01-23 23:30 | 198.04 | 192.68
2018-01-24 | 187.32 | 182.11
2018-01-24 00:30 | 179.77 | 174.62
2018-01-24 01:00 | 178.49 | 173.13
2018-01-24 01:30 | 178.06 | 172.59
2018-01-24 02:00 | 176.94 | 171.49
2018-01-24 02:30 | 176.6 | 171.11
2018-01-24 03:00 | 175.82 | 170.26
2018-01-24 03:30 | 175.24 | 169.63
2018-01-24 04:00 | 175.04 | 169.43
2018-01-24 04:30 | 174.87 | 169.3
2018-01-24 05:00 | 175.39 | 169.85
2018-01-24 05:30 | 176.21 | 170.65
2018-01-24 06:00 | 177.1 | 171.53
2018-01-24 06:30 | 178.8 | 173.53
2018-01-24 07:00 | 180.38 | 175.1
2018-01-24 07:30 | 182.38 | 177.3
2018-01-24 08:00 | 182.74 | 177.73
2018-01-24 08:30 | 183.95 | 178.52
2018-01-24 09:00 | 184.01 | 178.76
2018-01-24 09:30 | 184.57 | 179.28
2018-01-24 10:00 | 186.17 | 181.1
2018-01-24 10:30 | 186.56 | 181.56
2018-01-24 11:00 | 198.07 | 193.17
2018-01-24 11:30 | 203.63 | 198.69
2018-01-24 12:00 | 205.69 | 200.71
2018-01-24 12:30 | 207.03 | 202.07
2018-01-24 13:00 | 207.66 | 202.98
2018-01-24 13:30 | 209.25 | 204.96
2018-01-24 14:00 | 210.76 | 206.68
2018-01-24 14:30 | 212.61 | 208.31
2018-01-24 15:00 | 226.52 | 222.25
2018-01-24 15:30 | 227.8 | 223.28
2018-01-24 16:00 | 229.08 | 224.82
2018-01-24 16:30 | 230.77 | 226.39
2018-01-24 17:00 | 232.26 | 227.83
2018-01-24 17:30 | 233.3 | 228.64
2018-01-24 18:00 | 235.04 | 230.94
2018-01-24 18:30 | 235.58 | 231.51
2018-01-24 19:00 | 235.57 | 231.48
2018-01-24 19:30 | 236 | 231.76
2018-01-24 20:00 | 235.15 | 230.84
2018-01-24 20:30 | 232 | 227.29
2018-01-24 21:00 | 227.75 | 222.78
2018-01-24 21:30 | 195.08 | 190.57
2018-01-24 22:00 | 176.53 | 171.7
2018-01-24 22:30 | 173.18 | 168
2018-01-24 23:00 | 170.98 | 165.08
2018-01-24 23:30 | 169.59 | 163.52
2018-01-25 | 167.13 | 161.36
2018-01-25 00:30 | 165.49 | 159.63
2018-01-25 01:00 | 164.27 | 158.33
2018-01-25 01:30 | 163.47 | 157.41
2018-01-25 02:00 | 162.93 | 156.69
2018-01-25 02:30 | 162.36 | 156.09
2018-01-25 03:00 | 161.78 | 155.46
2018-01-25 03:30 | 161.59 | 155.26
2018-01-25 04:00 | 161 | 154.73
2018-01-25 04:30 | 161.09 | 154.84
2018-01-25 05:00 | 162.08 | 155.97
2018-01-25 05:30 | 162.84 | 156.33
2018-01-25 06:00 | 164.38 | 157.63
2018-01-25 06:30 | 166.52 | 159.92
2018-01-25 07:00 | 168.27 | 161.24
2018-01-25 07:30 | 170.32 | 163.1
2018-01-25 08:00 | 171.44 | 164.13
2018-01-25 08:30 | 171.98 | 164.55
2018-01-25 09:00 | 172.36 | 164.9
2018-01-25 09:30 | 190.79 | 184.2
2018-01-25 10:00 | 194.15 | 187.94
2018-01-25 10:30 | 194.54 | 188.41
2018-01-25 11:00 | 196.59 | 190.47
2018-01-25 11:30 | 198.1 | 192.17
2018-01-25 12:00 | 199.78 | 194.02
2018-01-25 12:30 | 200.92 | 195.19
2018-01-25 13:00 | 208.21 | 202.28
2018-01-25 13:30 | 213.09 | 207.53
2018-01-25 14:00 | 217.02 | 211.43
2018-01-25 14:30 | 225.78 | 220.47
2018-01-25 15:00 | 226.61 | 221.39
2018-01-25 15:30 | 227.05 | 221.91
2018-01-25 16:00 | 228.34 | 223.45
2018-01-25 16:30 | 229.49 | 224.32
2018-01-25 17:00 | 242.81 | 237.55
2018-01-25 17:30 | 258.19 | 252.81
2018-01-25 18:00 | 261.1 | 255.83
2018-01-25 18:30 | 261.86 | 256.58
2018-01-25 19:00 | 261.99 | 256.75
2018-01-25 19:30 | 262.37 | 257.11
2018-01-25 20:00 | 262.36 | 256.89
2018-01-25 20:30 | 260.16 | 254.31
2018-01-25 21:00 | 256.67 | 250.23
2018-01-25 21:30 | 236.33 | 230.47
2018-01-25 22:00 | 198.48 | 192.62
2018-01-25 22:30 | 187.98 | 181.35
2018-01-25 23:00 | 185.6 | 178.54
2018-01-25 23:30 | 182.43 | 175.52
2018-01-26 | 179.89 | 173.76
2018-01-26 00:30 | 178.99 | 172.91
2018-01-26 01:00 | 176.71 | 170.88
2018-01-26 01:30 | 176.12 | 170.26
2018-01-26 02:00 | 175.83 | 169.73
2018-01-26 02:30 | 174.35 | 168.18
2018-01-26 03:00 | 173.38 | 167.33
2018-01-26 03:30 | 172.87 | 167.04
2018-01-26 04:00 | 172.88 | 167.09
2018-01-26 04:30 | 171.67 | 165.92
2018-01-26 05:00 | 172.25 | 166.53
2018-01-26 05:30 | 171.93 | 166.18
2018-01-26 06:00 | 171.59 | 165.75
2018-01-26 06:30 | 172.43 | 166.58
2018-01-26 07:00 | 173.05 | 167.08
2018-01-26 07:30 | 174.1 | 168.28
2018-01-26 08:00 | 174.86 | 168.61
2018-01-26 08:30 | 175.6 | 169.07
2018-01-26 09:00 | 176.41 | 170.2
2018-01-26 09:30 | 177.63 | 171.51
2018-01-26 10:00 | 178.55 | 172.56
2018-01-26 10:30 | 179.59 | 173.86
2018-01-26 11:00 | 180.47 | 174.51
2018-01-26 11:30 | 211.27 | 205.08
2018-01-26 12:00 | 238.31 | 232.28
2018-01-26 12:30 | 244.76 | 238.79
2018-01-26 13:00 | 246.2 | 240.16
2018-01-26 13:30 | 247.86 | 242.04
2018-01-26 14:00 | 249.48 | 244.23
2018-01-26 14:30 | 250.03 | 245.22
2018-01-26 15:00 | 251.39 | 246.72
2018-01-26 15:30 | 252.36 | 247.65
2018-01-26 16:00 | 252.37 | 247.47
2018-01-26 16:30 | 253.44 | 248.46
2018-01-26 17:00 | 254.09 | 249.11
2018-01-26 17:30 | 252.73 | 247.25
2018-01-26 18:00 | 251.66 | 246.09
2018-01-26 18:30 | 250.84 | 245.24
2018-01-26 19:00 | 251.82 | 246.26
2018-01-26 19:30 | 252.28 | 246.77
2018-01-26 20:00 | 252.52 | 247.05
2018-01-26 20:30 | 251.24 | 245.31
2018-01-26 21:00 | 248.99 | 242.85
2018-01-26 21:30 | 246.04 | 240.62
2018-01-26 22:00 | 243.35 | 237.87
2018-01-26 22:30 | 241.39 | 235.66
2018-01-26 23:00 | 239.62 | 233.59
2018-01-26 23:30 | 220.6 | 214.95
2018-01-27 | 184.31 | 178.13
2018-01-27 00:30 | 177.01 | 170.5
2018-01-27 01:00 | 175.17 | 168.92
2018-01-27 01:30 | 174.67 | 168.45
2018-01-27 02:00 | 173.66 | 167.29
2018-01-27 02:30 | 172.85 | 166.64
2018-01-27 03:00 | 172.35 | 166.14
2018-01-27 03:30 | 171.68 | 165.48
2018-01-27 04:00 | 171.6 | 165.29
2018-01-27 04:30 | 171.38 | 164.96
2018-01-27 05:00 | 170.93 | 164.47
2018-01-27 05:30 | 171.3 | 164.97
2018-01-27 06:00 | 171.21 | 164.93
2018-01-27 06:30 | 171.47 | 165.01
2018-01-27 07:00 | 173.26 | 166.73
2018-01-27 07:30 | 175.09 | 168.05
2018-01-27 08:00 | 176.31 | 169.25
2018-01-27 08:30 | 176.47 | 169.2
2018-01-27 09:00 | 177.11 | 170.3
2018-01-27 09:30 | 178.8 | 172.92
2018-01-27 10:00 | 179.57 | 173.57
2018-01-27 10:30 | 182.25 | 174.74
2018-01-27 11:00 | 183.78 | 176.28
2018-01-27 11:30 | 185.92 | 178.63
2018-01-27 12:00 | 188.05 | 181.03
2018-01-27 12:30 | 190.36 | 183.33
2018-01-27 13:00 | 205.23 | 198.32
2018-01-27 13:30 | 243.87 | 237.43
2018-01-27 14:00 | 250.69 | 244.35
2018-01-27 14:30 | 249.88 | 243.15
2018-01-27 15:00 | 250.47 | 243.89
2018-01-27 15:30 | 251.64 | 245.09
2018-01-27 16:00 | 252.77 | 246.47
2018-01-27 16:30 | 253.73 | 247.9
2018-01-27 17:00 | 254.65 | 248.69
2018-01-27 17:30 | 257.09 | 251.05
2018-01-27 18:00 | 258.47 | 252.37
2018-01-27 18:30 | 258.56 | 252.54
2018-01-27 19:00 | 258.51 | 252.44
2018-01-27 19:30 | 259.15 | 252.92
2018-01-27 20:00 | 258.92 | 252.38
2018-01-27 20:30 | 257.7 | 250.59
2018-01-27 21:00 | 255.51 | 247.92
2018-01-27 21:30 | 252.68 | 245.9
2018-01-27 22:00 | 232.48 | 225.58
2018-01-27 22:30 | 195.03 | 187.76
2018-01-27 23:00 | 184.64 | 177.73
2018-01-27 23:30 | 183.44 | 176.21
2018-01-28 | 182.12 | 174.59
2018-01-28 00:30 | 180.75 | 173.19
2018-01-28 01:00 | 179.64 | 172.12
2018-01-28 01:30 | 178.43 | 170.54
2018-01-28 02:00 | 178.41 | 170.41
2018-01-28 02:30 | 177.22 | 168.97
2018-01-28 03:00 | 176.98 | 168.68
2018-01-28 03:30 | 175.9 | 167.55
2018-01-28 04:00 | 174.7 | 166.37
2018-01-28 04:30 | 174.55 | 166.33
2018-01-28 05:00 | 174.41 | 166.22
2018-01-28 05:30 | 174.28 | 166.24
2018-01-28 06:00 | 174.18 | 166.3
2018-01-28 06:30 | 174.23 | 166.69
2018-01-28 07:00 | 174.8 | 167.46
2018-01-28 07:30 | 174.85 | 167.92
2018-01-28 08:00 | 175.98 | 168.87
2018-01-28 08:30 | 175.68 | 168.67
2018-01-28 09:00 | 176.35 | 169.21
2018-01-28 09:30 | 175.98 | 168.97
2018-01-28 10:00 | 177.02 | 170.15
2018-01-28 10:30 | 178.88 | 171.95
2018-01-28 11:00 | 179.23 | 173
2018-01-28 11:30 | 180.72 | 174.96
2018-01-28 12:00 | 182.82 | 176.72
2018-01-28 12:30 | 183.84 | 178.36
2018-01-28 13:00 | 186.21 | 181.07
2018-01-28 13:30 | 187.48 | 182.5
2018-01-28 14:00 | 216.49 | 211.58
2018-01-28 14:30 | 241.94 | 236.76
2018-01-28 15:00 | 248.74 | 243.64
2018-01-28 15:30 | 249.42 | 244.18
2018-01-28 16:00 | 250.26 | 245.53
2018-01-28 16:30 | 251.57 | 247.01
2018-01-28 17:00 | 253.25 | 248.82
2018-01-28 17:30 | 254.75 | 250.46
2018-01-28 18:00 | 255.59 | 251.28
2018-01-28 18:30 | 255.96 | 251.91
2018-01-28 19:00 | 256.27 | 252.11
2018-01-28 19:30 | 256.55 | 252.38
2018-01-28 20:00 | 255.85 | 251.63
2018-01-28 20:30 | 254.06 | 249.4
2018-01-28 21:00 | 250.98 | 245.64
2018-01-28 21:30 | 231.15 | 225.63
2018-01-28 22:00 | 194.24 | 188.56
2018-01-28 22:30 | 183.58 | 176.97
2018-01-28 23:00 | 181.77 | 174.76
2018-01-28 23:30 | 179.4 | 172.95
2018-01-29 | 177.69 | 171.42
2018-01-29 00:30 | 176.77 | 170.64
2018-01-29 01:00 | 175.13 | 168.97
2018-01-29 01:30 | 174.46 | 168.23
2018-01-29 02:00 | 174.27 | 168.05
2018-01-29 02:30 | 173.47 | 167.11
2018-01-29 03:00 | 173.05 | 166.65
2018-01-29 03:30 | 172.02 | 165.58
2018-01-29 04:00 | 170.56 | 164.05
2018-01-29 04:30 | 170.27 | 163.73
2018-01-29 05:00 | 170.34 | 163.8
2018-01-29 05:30 | 171.01 | 164.54
2018-01-29 06:00 | 172.05 | 165.83
2018-01-29 06:30 | 174.66 | 166.88
2018-01-29 07:00 | 175.52 | 168.29
2018-01-29 07:30 | 176.55 | 169.86
2018-01-29 08:00 | 205.12 | 199.27
2018-01-29 08:30 | 225.78 | 219.56
2018-01-29 09:00 | 237.82 | 231.59
2018-01-29 09:30 | 239.83 | 233.26
2018-01-29 10:00 | 240.09 | 233.35
2018-01-29 10:30 | 240.29 | 233.73
2018-01-29 11:00 | 241.05 | 235.19
2018-01-29 11:30 | 241.45 | 235.63
2018-01-29 12:00 | 242.3 | 236.55
2018-01-29 12:30 | 243.35 | 237.6
2018-01-29 13:00 | 244.2 | 238.43
2018-01-29 13:30 | 244.47 | 238.48
2018-01-29 14:00 | 246.02 | 240.17
2018-01-29 14:30 | 247.15 | 241.44
2018-01-29 15:00 | 246.13 | 240.24
2018-01-29 15:30 | 246.97 | 241.03
2018-01-29 16:00 | 248.77 | 242.69
2018-01-29 16:30 | 249.9 | 243.74
2018-01-29 17:00 | 251.12 | 244.75
2018-01-29 17:30 | 250.91 | 244.66
2018-01-29 18:00 | 251.75 | 245.94
2018-01-29 18:30 | 252.31 | 246.42
2018-01-29 19:00 | 253.41 | 247.49
2018-01-29 19:30 | 253.77 | 247.83
2018-01-29 20:00 | 254.25 | 248.32
2018-01-29 20:30 | 251.91 | 245.63
2018-01-29 21:00 | 249.6 | 243.13
2018-01-29 21:30 | 246.18 | 240.63
2018-01-29 22:00 | 242.67 | 237.09
2018-01-29 22:30 | 240.18 | 234.37
2018-01-29 23:00 | 238.13 | 232.17
2018-01-29 23:30 | 220.59 | 214.61
2018-01-30 | 184.7 | 178.52
2018-01-30 00:30 | 174.27 | 168.17
2018-01-30 01:00 | 172.93 | 166.88
2018-01-30 01:30 | 173.07 | 166.91
2018-01-30 02:00 | 172.45 | 166.14
2018-01-30 02:30 | 171.97 | 165.76
2018-01-30 03:00 | 171.21 | 164.93
2018-01-30 03:30 | 170.56 | 164.36
2018-01-30 04:00 | 170.64 | 164.43
2018-01-30 04:30 | 170.26 | 164.09
2018-01-30 05:00 | 171.23 | 165.14
2018-01-30 05:30 | 172.03 | 165.93
2018-01-30 06:00 | 173.11 | 166.85
2018-01-30 06:30 | 174.33 | 167.93
2018-01-30 07:00 | 204.48 | 198.13
2018-01-30 07:30 | 230.16 | 224.5
2018-01-30 08:00 | 237.75 | 232.27
2018-01-30 08:30 | 238.15 | 232.92
2018-01-30 09:00 | 238.2 | 233.02
2018-01-30 09:30 | 238.55 | 232.98
2018-01-30 10:00 | 239.49 | 233.92
2018-01-30 10:30 | 239.89 | 234.11
2018-01-30 11:00 | 241.51 | 235.84
2018-01-30 11:30 | 242.49 | 237.04
2018-01-30 12:00 | 243.9 | 238.57
2018-01-30 12:30 | 245.53 | 240.19
2018-01-30 13:00 | 247.26 | 242.05
2018-01-30 13:30 | 248.21 | 243.12
2018-01-30 14:00 | 249.44 | 244.67
2018-01-30 14:30 | 250.11 | 245.57
2018-01-30 15:00 | 250.82 | 246.37
2018-01-30 15:30 | 234.43 | 230.95
2018-01-30 16:00 | 222.72 | 219.51
2018-01-30 16:30 | 221.89 | 218.57
2018-01-30 17:00 | 221.8 | 218.39
2018-01-30 17:30 | 221.82 | 218.25
2018-01-30 18:00 | 217.97 | 214.53
2018-01-30 18:30 | 206.07 | 202.86
2018-01-30 19:00 | 206.2 | 203.07
2018-01-30 19:30 | 207.34 | 204.21
2018-01-30 20:00 | 217.14 | 213.72
2018-01-30 20:30 | 225.36 | 221.51
2018-01-30 21:00 | 228.83 | 224.85
2018-01-30 21:30 | 229.72 | 226.72
2018-01-30 22:00 | 241.98 | 235.77
2018-01-30 22:30 | 244.61 | 237.07
2018-01-30 23:00 | 242.43 | 234.45
2018-01-30 23:30 | 224.32 | 216.08
2018-01-31 | 188.22 | 179.65
2018-01-31 00:30 | 177.86 | 169.42
2018-01-31 01:00 | 176.21 | 167.76
2018-01-31 01:30 | 175.04 | 166.98
2018-01-31 02:00 | 174.35 | 166.17
2018-01-31 02:30 | 173.67 | 165.88
2018-01-31 03:00 | 174.32 | 166.75
2018-01-31 03:30 | 174.14 | 166.49
2018-01-31 04:00 | 173.87 | 166.12
2018-01-31 04:30 | 174.23 | 166.48
2018-01-31 05:00 | 174.14 | 166.3
2018-01-31 05:30 | 174.92 | 167.14
2018-01-31 06:00 | 176.37 | 168.63
2018-01-31 06:30 | 206.59 | 199.41
2018-01-31 07:00 | 230.7 | 223.14
2018-01-31 07:30 | 239.65 | 231.23
2018-01-31 08:00 | 242.12 | 233.72
2018-01-31 08:30 | 242.98 | 234.17
2018-01-31 09:00 | 244.09 | 235.32
2018-01-31 09:30 | 244.06 | 235.33
2018-01-31 10:00 | 245.3 | 236.69
2018-01-31 10:30 | 246.94 | 238
2018-01-31 11:00 | 249.3 | 240.62
2018-01-31 11:30 | 250.19 | 241.5
2018-01-31 12:00 | 251.02 | 242.63
2018-01-31 12:30 | 252.25 | 243.77
2018-01-31 13:00 | 254.83 | 246.34
2018-01-31 13:30 | 256.24 | 248.09
2018-01-31 14:00 | 257.16 | 249.49
2018-01-31 14:30 | 242.7 | 236.12
2018-01-31 15:00 | 219.7 | 214.51
2018-01-31 15:30 | 218.82 | 213.73
2018-01-31 16:00 | 217.23 | 212.26
2018-01-31 16:30 | 218.37 | 213.72
2018-01-31 17:00 | 219.77 | 215.12
2018-01-31 17:30 | 220.61 | 215.86
2018-01-31 18:00 | 219.6 | 214.85
2018-01-31 18:30 | 254.47 | 247.29
2018-01-31 19:00 | 265.36 | 257.76
2018-01-31 19:30 | 265.4 | 257.71
2018-01-31 20:00 | 263.09 | 255.3
2018-01-31 20:30 | 241.23 | 234.54
2018-01-31 21:00 | 236.51 | 230.02
2018-01-31 21:30 | 233.49 | 227.03
2018-01-31 22:00 | 229.25 | 223.12
2018-01-31 22:30 | 226.53 | 220.25
2018-01-31 23:00 | 223.57 | 216.95
2018-01-31 23:30 | 221.52 | 214.48
2018-02-01 | 193.58 | 186.09
2018-02-01 00:30 | 181.91 | 175.25
2018-02-01 01:00 | 180.94 | 174.33
2018-02-01 01:30 | 179.51 | 173.06
2018-02-01 02:00 | 178.87 | 172.38
2018-02-01 02:30 | 178.05 | 171.47
2018-02-01 03:00 | 176.72 | 170.62
2018-02-01 03:30 | 176.05 | 170.13
2018-02-01 04:00 | 175.3 | 169.38
2018-02-01 04:30 | 175.13 | 169.26
2018-02-01 05:00 | 175.68 | 169.83
2018-02-01 05:30 | 177.01 | 171.23
2018-02-01 06:00 | 206.86 | 200.95
2018-02-01 06:30 | 228.62 | 222.39
2018-02-01 07:00 | 223.2 | 217.25
2018-02-01 07:30 | 222.28 | 216.71
2018-02-01 08:00 | 222.77 | 217.4
2018-02-01 08:30 | 223.13 | 217.11
2018-02-01 09:00 | 225.44 | 218.97
2018-02-01 09:30 | 224.38 | 217.91
2018-02-01 10:00 | 224.76 | 218.54
2018-02-01 10:30 | 224.15 | 217.81
2018-02-01 11:00 | 226.56 | 220.26
2018-02-01 11:30 | 227.83 | 221.61
2018-02-01 12:00 | 228.07 | 222.04
2018-02-01 12:30 | 228.77 | 222.8
2018-02-01 13:00 | 229.4 | 223.3
2018-02-01 13:30 | 231.47 | 225.71
2018-02-01 14:00 | 232.92 | 227.55
2018-02-01 14:30 | 232.92 | 227.52
2018-02-01 15:00 | 230.11 | 224.45
2018-02-01 15:30 | 229.81 | 224.11
2018-02-01 16:00 | 230.1 | 224.41
2018-02-01 16:30 | 230.73 | 224.96
2018-02-01 17:00 | 231.22 | 225.4
2018-02-01 17:30 | 230.58 | 224.69
2018-02-01 18:00 | 231.55 | 225.43
2018-02-01 18:30 | 231.77 | 225.52
2018-02-01 19:00 | 231.79 | 225.62
2018-02-01 19:30 | 231.61 | 225.49
2018-02-01 20:00 | 230.46 | 224.32
2018-02-01 20:30 | 229.06 | 222.62
2018-02-01 21:00 | 226.92 | 219.98
2018-02-01 21:30 | 214.24 | 207.41
2018-02-01 22:00 | 179.54 | 172.56
2018-02-01 22:30 | 170.31 | 163.05
2018-02-01 23:00 | 168.5 | 160.95
2018-02-01 23:30 | 167.75 | 160.28
2018-02-02 | 165.75 | 158.44
2018-02-02 00:30 | 163.84 | 157.2
2018-02-02 01:00 | 162.9 | 156.36
2018-02-02 01:30 | 162.79 | 155.9
2018-02-02 02:00 | 162.76 | 155.66
2018-02-02 02:30 | 162.55 | 155.82
2018-02-02 03:00 | 160.95 | 154.36
2018-02-02 03:30 | 161.05 | 154.44
2018-02-02 04:00 | 160.38 | 154.42
2018-02-02 04:30 | 159.85 | 153.77
2018-02-02 05:00 | 159.83 | 153.7
2018-02-02 05:30 | 160.97 | 154.98
2018-02-02 06:00 | 160.34 | 154.77
2018-02-02 06:30 | 189.32 | 183.8
2018-02-02 07:00 | 209.82 | 203.48
2018-02-02 07:30 | 214.02 | 207.8
2018-02-02 08:00 | 214.54 | 208.61
2018-02-02 08:30 | 215.41 | 209.43
2018-02-02 09:00 | 215.47 | 209.6
2018-02-02 09:30 | 215.89 | 209.92
2018-02-02 10:00 | 216.48 | 210.3
2018-02-02 10:30 | 216.92 | 210.48
2018-02-02 11:00 | 217.31 | 210.97
2018-02-02 11:30 | 218.65 | 212.18
2018-02-02 12:00 | 219.89 | 213.79
2018-02-02 12:30 | 218.41 | 212.53
2018-02-02 13:00 | 224.34 | 218.46
2018-02-02 13:30 | 226.87 | 220.94
2018-02-02 14:00 | 226.35 | 220.46
2018-02-02 14:30 | 226.63 | 220.54
2018-02-02 15:00 | 226.21 | 219.99
2018-02-02 15:30 | 225.45 | 219.11
2018-02-02 16:00 | 225.62 | 219.37
2018-02-02 16:30 | 226.07 | 219.78
2018-02-02 17:00 | 226.48 | 220.22
2018-02-02 17:30 | 226.23 | 219.77
2018-02-02 18:00 | 227.23 | 220.73
2018-02-02 18:30 | 228.67 | 222.11
2018-02-02 19:00 | 230.03 | 223.49
2018-02-02 19:30 | 229.51 | 223.03
2018-02-02 20:00 | 228.43 | 221.85
2018-02-02 20:30 | 227.32 | 220.56
2018-02-02 21:00 | 226.31 | 219.5
2018-02-02 21:30 | 204.15 | 198.48
2018-02-02 22:00 | 167.68 | 161.84
2018-02-02 22:30 | 159.56 | 153.61
2018-02-02 23:00 | 158.1 | 151.96
2018-02-02 23:30 | 157.95 | 151.81
2018-02-03 | 156.88 | 150.58
2018-02-03 00:30 | 155.64 | 149.15
2018-02-03 01:00 | 155.44 | 148.72
2018-02-03 01:30 | 155.01 | 148.27
2018-02-03 02:00 | 155.81 | 148.92
2018-02-03 02:30 | 155 | 148.1
2018-02-03 03:00 | 154.96 | 148.1
2018-02-03 03:30 | 154.93 | 148.05
2018-02-03 04:00 | 154.62 | 147.92
2018-02-03 04:30 | 154.67 | 148.23
2018-02-03 05:00 | 155.65 | 149.1
2018-02-03 05:30 | 156.18 | 149.65
2018-02-03 06:00 | 158.13 | 150.64
2018-02-03 06:30 | 158.79 | 150.73
2018-02-03 07:00 | 159.41 | 151.25
2018-02-03 07:30 | 160.95 | 152.86
2018-02-03 08:00 | 162.12 | 154.05
2018-02-03 08:30 | 163.42 | 154.88
2018-02-03 09:00 | 164.13 | 155.72
2018-02-03 09:30 | 164.05 | 155.78
2018-02-03 10:00 | 164.52 | 156.31
2018-02-03 10:30 | 163.74 | 155.5
2018-02-03 11:00 | 162.69 | 154.4
2018-02-03 11:30 | 163.11 | 154.45
2018-02-03 12:00 | 162.4 | 153.74
2018-02-03 12:30 | 162.31 | 153.62
2018-02-03 13:00 | 161.22 | 152.34
2018-02-03 13:30 | 159.53 | 150.57
2018-02-03 14:00 | 158.97 | 150
2018-02-03 14:30 | 159.22 | 150.14
2018-02-03 15:00 | 159 | 150.03
2018-02-03 15:30 | 159.2 | 150.37
2018-02-03 16:00 | 158.65 | 149.88
2018-02-03 16:30 | 160.2 | 151.45
2018-02-03 17:00 | 162.2 | 153.44
2018-02-03 17:30 | 163.45 | 155.01
2018-02-03 18:00 | 164.64 | 156.26
2018-02-03 18:30 | 164.33 | 156.18
2018-02-03 19:00 | 163.71 | 155.65
2018-02-03 19:30 | 163.87 | 155.88
2018-02-03 20:00 | 163.68 | 155.65
2018-02-03 20:30 | 162.74 | 154.43
2018-02-03 21:00 | 161.74 | 153.13
2018-02-03 21:30 | 161.44 | 152.91
2018-02-03 22:00 | 160.25 | 151.98
2018-02-03 22:30 | 160.01 | 151.52
2018-02-03 23:00 | 158 | 148.79
2018-02-03 23:30 | 157.36 | 148.45
2018-02-04 | 156.89 | 148.2
2018-02-04 00:30 | 155.71 | 147.4
2018-02-04 01:00 | 154.67 | 146.44
2018-02-04 01:30 | 154.29 | 146.08
2018-02-04 02:00 | 154.02 | 145.75
2018-02-04 02:30 | 153.61 | 145.52
2018-02-04 03:00 | 153.23 | 145.19
2018-02-04 03:30 | 153.41 | 145.57
2018-02-04 04:00 | 153.1 | 145.28
2018-02-04 04:30 | 153.44 | 145.74
2018-02-04 05:00 | 154.16 | 145.85
2018-02-04 05:30 | 154.81 | 146.46
2018-02-04 06:00 | 155.13 | 146.77
2018-02-04 06:30 | 155.42 | 146.83
2018-02-04 07:00 | 155.6 | 147.26
2018-02-04 07:30 | 155.21 | 147.78
2018-02-04 08:00 | 155.4 | 147.83
2018-02-04 08:30 | 155 | 147.17
2018-02-04 09:00 | 155.16 | 147.48
2018-02-04 09:30 | 154.52 | 146.62
2018-02-04 10:00 | 155.35 | 146.97
2018-02-04 10:30 | 154.39 | 146.41
2018-02-04 11:00 | 154.51 | 146.35
2018-02-04 11:30 | 154.69 | 146.47
2018-02-04 12:00 | 155.6 | 146.77
2018-02-04 12:30 | 155.7 | 147.1
2018-02-04 13:00 | 156.16 | 147.66
2018-02-04 13:30 | 155.98 | 147.59
2018-02-04 14:00 | 156.34 | 147.37
2018-02-04 14:30 | 160.39 | 151.58
2018-02-04 15:00 | 165.76 | 157.82
2018-02-04 15:30 | 166.64 | 158.5
2018-02-04 16:00 | 169.56 | 161.61
2018-02-04 16:30 | 170.47 | 163.03
2018-02-04 17:00 | 196.53 | 189.53
2018-02-04 17:30 | 222.85 | 215.96
2018-02-04 18:00 | 231.85 | 224.7
2018-02-04 18:30 | 233.04 | 225.67
2018-02-04 19:00 | 234.43 | 226.78
2018-02-04 19:30 | 235.03 | 227.23
2018-02-04 20:00 | 235.14 | 227.47
2018-02-04 20:30 | 234.46 | 226.67
2018-02-04 21:00 | 233.58 | 225.78
2018-02-04 21:30 | 232.32 | 224.71
2018-02-04 22:00 | 212.3 | 204.42
2018-02-04 22:30 | 174.91 | 165.83
2018-02-04 23:00 | 167.92 | 158.08
2018-02-04 23:30 | 166.62 | 156.94
2018-02-05 | 163.73 | 155.21
2018-02-05 00:30 | 162.42 | 154.89
2018-02-05 01:00 | 160.92 | 153.09
2018-02-05 01:30 | 160.33 | 152.76
2018-02-05 02:00 | 159.97 | 152.24
2018-02-05 02:30 | 160.39 | 152.2
2018-02-05 03:00 | 159.95 | 151.83
2018-02-05 03:30 | 159.52 | 151.43
2018-02-05 04:00 | 158.94 | 151.06
2018-02-05 04:30 | 159.14 | 151.67
2018-02-05 05:00 | 159.52 | 152.32
2018-02-05 05:30 | 160.42 | 153.76
2018-02-05 06:00 | 161.53 | 154.89
2018-02-05 06:30 | 164.51 | 154.93
2018-02-05 07:00 | 183.23 | 172.79
2018-02-05 07:30 | 199.68 | 189.79
2018-02-05 08:00 | 200.08 | 190.12
2018-02-05 08:30 | 216.23 | 206.72
2018-02-05 09:00 | 223.16 | 214.04
2018-02-05 09:30 | 222.24 | 213.08
2018-02-05 10:00 | 222.37 | 213.29
2018-02-05 10:30 | 222.19 | 213.32
2018-02-05 11:00 | 222.62 | 213.8
2018-02-05 11:30 | 222.55 | 213.8
2018-02-05 12:00 | 223.96 | 214.89
2018-02-05 12:30 | 224.23 | 215.2
2018-02-05 13:00 | 225.08 | 216.03
2018-02-05 13:30 | 226.03 | 217.11
2018-02-05 14:00 | 227.05 | 218.29
2018-02-05 14:30 | 227.45 | 218.81
2018-02-05 15:00 | 227.96 | 219.28
2018-02-05 15:30 | 229.24 | 220.74
2018-02-05 16:00 | 231.47 | 222.61
2018-02-05 16:30 | 232.62 | 223.18
2018-02-05 17:00 | 234.5 | 224.76
2018-02-05 17:30 | 235.89 | 225.82
2018-02-05 18:00 | 235.95 | 227.07
2018-02-05 18:30 | 237.08 | 228.26
2018-02-05 19:00 | 237.72 | 229.07
2018-02-05 19:30 | 238.14 | 229.59
2018-02-05 20:00 | 238.34 | 229.61
2018-02-05 20:30 | 236.78 | 227.78
2018-02-05 21:00 | 234.69 | 225.6
2018-02-05 21:30 | 214.76 | 206.2
2018-02-05 22:00 | 176.43 | 167.45
2018-02-05 22:30 | 167.29 | 157.94
2018-02-05 23:00 | 165.61 | 155.76
2018-02-05 23:30 | 164.25 | 154.67
2018-02-06 | 162.91 | 153.56
2018-02-06 00:30 | 160.98 | 151.98
2018-02-06 01:00 | 159.87 | 151.34
2018-02-06 01:30 | 159.49 | 150.94
2018-02-06 02:00 | 158.19 | 149.9
2018-02-06 02:30 | 158.2 | 149.71
2018-02-06 03:00 | 158.65 | 149.81
2018-02-06 03:30 | 157.78 | 148.85
2018-02-06 04:00 | 157.97 | 149.35
2018-02-06 04:30 | 158.19 | 149.68
2018-02-06 05:00 | 158.9 | 150.3
2018-02-06 05:30 | 160.04 | 151.41
2018-02-06 06:00 | 161.08 | 152.11
2018-02-06 06:30 | 162.84 | 154.13
2018-02-06 07:00 | 166.9 | 157.06
2018-02-06 07:30 | 165.75 | 156.01
2018-02-06 08:00 | 165.9 | 156.59
2018-02-06 08:30 | 165.51 | 156.47
2018-02-06 09:00 | 164.6 | 155.62
2018-02-06 09:30 | 164.05 | 154.91
2018-02-06 10:00 | 163.91 | 155.17
2018-02-06 10:30 | 164.45 | 155.7
2018-02-06 11:00 | 165.88 | 157.68
2018-02-06 11:30 | 166.62 | 158.54
2018-02-06 12:00 | 167.79 | 159.65
2018-02-06 12:30 | 169.3 | 160.74
2018-02-06 13:00 | 170.23 | 161.98
2018-02-06 13:30 | 170.81 | 162.41
2018-02-06 14:00 | 171.9 | 163.55
2018-02-06 14:30 | 172.61 | 164.43
2018-02-06 15:00 | 172.1 | 164.23
2018-02-06 15:30 | 172.89 | 164.04
2018-02-06 16:00 | 171.49 | 162.42
2018-02-06 16:30 | 172.87 | 163.31
2018-02-06 17:00 | 174.97 | 164.81
2018-02-06 17:30 | 176.92 | 166.68
2018-02-06 18:00 | 178.18 | 167.85
2018-02-06 18:30 | 179.99 | 169.24
2018-02-06 19:00 | 180.51 | 169.89
2018-02-06 19:30 | 180.29 | 169.84
2018-02-06 20:00 | 180.12 | 169.56
2018-02-06 20:30 | 178.05 | 167.01
2018-02-06 21:00 | 175.83 | 164.49
2018-02-06 21:30 | 172.3 | 162.41
2018-02-06 22:00 | 169.21 | 160.1
2018-02-06 22:30 | 167.21 | 157.74
2018-02-06 23:00 | 166.01 | 155.9
2018-02-06 23:30 | 164.26 | 154.03
2018-02-07 | 162.81 | 153.08
2018-02-07 00:30 | 161.03 | 151.62
2018-02-07 01:00 | 159.67 | 150.67
2018-02-07 01:30 | 159.04 | 150.17
2018-02-07 02:00 | 158.35 | 149.65
2018-02-07 02:30 | 158.02 | 149.12
2018-02-07 03:00 | 157.83 | 149.02
2018-02-07 03:30 | 157.68 | 148.79
2018-02-07 04:00 | 160.01 | 151.07
2018-02-07 04:30 | 159.95 | 151.42
2018-02-07 05:00 | 160.88 | 152.59
2018-02-07 05:30 | 162.37 | 153.39
2018-02-07 06:00 | 163.23 | 154.16
2018-02-07 06:30 | 165.77 | 156.6
2018-02-07 07:00 | 166.77 | 157.4
2018-02-07 07:30 | 168.27 | 158.77
2018-02-07 08:00 | 167.85 | 158.78
2018-02-07 08:30 | 166.21 | 157.67
2018-02-07 09:00 | 165.6 | 157.38
2018-02-07 09:30 | 175.06 | 166.63
2018-02-07 10:00 | 217.43 | 209.8
2018-02-07 10:30 | 225.31 | 217.73
2018-02-07 11:00 | 227.02 | 219.31
2018-02-07 11:30 | 228.26 | 220.4
2018-02-07 12:00 | 229.73 | 221.32
2018-02-07 12:30 | 230.21 | 221.74
2018-02-07 13:00 | 230.72 | 223.31
2018-02-07 13:30 | 231.63 | 224.55
2018-02-07 14:00 | 233.21 | 225.85
2018-02-07 14:30 | 233.92 | 226.95
2018-02-07 15:00 | 234.16 | 227.46
2018-02-07 15:30 | 234.62 | 227.59
2018-02-07 16:00 | 236.03 | 228.83
2018-02-07 16:30 | 236.65 | 229.74
2018-02-07 17:00 | 239.26 | 231.41
2018-02-07 17:30 | 241.04 | 232.64
2018-02-07 18:00 | 242.41 | 233.85
2018-02-07 18:30 | 243.48 | 234.8
2018-02-07 19:00 | 244.47 | 235.44
2018-02-07 19:30 | 245.46 | 236.25
2018-02-07 20:00 | 245.58 | 235.99
2018-02-07 20:30 | 243.95 | 233.84
2018-02-07 21:00 | 239.23 | 230.48
2018-02-07 21:30 | 216.47 | 209.42
2018-02-07 22:00 | 177.83 | 170.95
2018-02-07 22:30 | 168.04 | 160.78
2018-02-07 23:00 | 165.93 | 158.32
2018-02-07 23:30 | 164.06 | 156.65
2018-02-08 | 162.7 | 155.41
2018-02-08 00:30 | 161.18 | 154.22
2018-02-08 01:00 | 159.65 | 153.24
2018-02-08 01:30 | 161.57 | 152.97
2018-02-08 02:00 | 160.29 | 151.59
2018-02-08 02:30 | 160 | 151.11
2018-02-08 03:00 | 160.47 | 151.41
2018-02-08 03:30 | 159.98 | 150.94
2018-02-08 04:00 | 157.49 | 148.54
2018-02-08 04:30 | 156.44 | 147.43
2018-02-08 05:00 | 157.57 | 148.18
2018-02-08 05:30 | 158.58 | 149.27
2018-02-08 06:00 | 160.01 | 150.71
2018-02-08 06:30 | 161.75 | 152.75
2018-02-08 07:00 | 162.53 | 153.39
2018-02-08 07:30 | 164.58 | 154.76
2018-02-08 08:00 | 164.44 | 155.05
2018-02-08 08:30 | 191.88 | 183.18
2018-02-08 09:00 | 215.36 | 207.08
2018-02-08 09:30 | 224.25 | 216.19
2018-02-08 10:00 | 224.63 | 216.68
2018-02-08 10:30 | 225.36 | 217.2
2018-02-08 11:00 | 225.59 | 217.63
2018-02-08 11:30 | 226 | 218.48
2018-02-08 12:00 | 227.12 | 218.84
2018-02-08 12:30 | 228.87 | 220.12
2018-02-08 13:00 | 230.3 | 221.5
2018-02-08 13:30 | 231.14 | 222.48
2018-02-08 14:00 | 239.18 | 230.7
2018-02-08 14:30 | 243.88 | 235.45
2018-02-08 15:00 | 245.74 | 238.22
2018-02-08 15:30 | 244.87 | 238.38
2018-02-08 16:00 | 245.91 | 239.7
2018-02-08 16:30 | 247.59 | 240.23
2018-02-08 17:00 | 249.23 | 241.84
2018-02-08 17:30 | 250.62 | 242.64
2018-02-08 18:00 | 252.21 | 244.2
2018-02-08 18:30 | 253.76 | 245.47
2018-02-08 19:00 | 253.54 | 244.92
2018-02-08 19:30 | 251.35 | 242.59
2018-02-08 20:00 | 249.54 | 240.6
2018-02-08 20:30 | 247.26 | 238.34
2018-02-08 21:00 | 243.65 | 234.82
2018-02-08 21:30 | 223.36 | 214.1
2018-02-08 22:00 | 185.9 | 175.89
2018-02-08 22:30 | 176.17 | 166.54
2018-02-08 23:00 | 173.47 | 163.81
2018-02-08 23:30 | 172.13 | 163.28
2018-02-09 | 170.31 | 161.89
2018-02-09 00:30 | 169.18 | 160.92
2018-02-09 01:00 | 167.71 | 159.69
2018-02-09 01:30 | 166.84 | 159.38
2018-02-09 02:00 | 165.25 | 158.27
2018-02-09 02:30 | 165.32 | 158.27
2018-02-09 03:00 | 164.24 | 157.63
2018-02-09 03:30 | 163.7 | 156.8
2018-02-09 04:00 | 164.63 | 157.69
2018-02-09 04:30 | 165.08 | 157.91
2018-02-09 05:00 | 166.12 | 158.57
2018-02-09 05:30 | 166.57 | 159.45
2018-02-09 06:00 | 167.26 | 160.34
2018-02-09 06:30 | 172 | 162.38
2018-02-09 07:00 | 200.61 | 190.8
2018-02-09 07:30 | 227.26 | 218.04
2018-02-09 08:00 | 236.27 | 228.04
2018-02-09 08:30 | 235.37 | 227.68
2018-02-09 09:00 | 235.09 | 227.31
2018-02-09 09:30 | 235.7 | 227
2018-02-09 10:00 | 235.27 | 226.62
2018-02-09 10:30 | 234.82 | 226.21
2018-02-09 11:00 | 235.31 | 226.68
2018-02-09 11:30 | 237.07 | 228.2
2018-02-09 12:00 | 238.29 | 229.69
2018-02-09 12:30 | 238.58 | 230.17
2018-02-09 13:00 | 239.51 | 231.14
2018-02-09 13:30 | 239.79 | 231.84
2018-02-09 14:00 | 241.65 | 233.39
2018-02-09 14:30 | 243.39 | 234.48
2018-02-09 15:00 | 244.67 | 235.31
2018-02-09 15:30 | 245.74 | 236.23
2018-02-09 16:00 | 246.95 | 237.49
2018-02-09 16:30 | 249.62 | 239.97
2018-02-09 17:00 | 251.3 | 241.85
2018-02-09 17:30 | 252.22 | 242.54
2018-02-09 18:00 | 253.82 | 243.81
2018-02-09 18:30 | 253.06 | 244.76
2018-02-09 19:00 | 252.56 | 244.67
2018-02-09 19:30 | 252.28 | 244.55
2018-02-09 20:00 | 251.38 | 243.55
2018-02-09 20:30 | 249.27 | 241.16
2018-02-09 21:00 | 246.07 | 237.61
2018-02-09 21:30 | 242.9 | 235.59
2018-02-09 22:00 | 240.11 | 232.77
2018-02-09 22:30 | 238.11 | 230.51
2018-02-09 23:00 | 236.15 | 228.02
2018-02-09 23:30 | 216.34 | 208.27
2018-02-10 | 180.03 | 171.63
2018-02-10 00:30 | 170.57 | 163.28
2018-02-10 01:00 | 168.41 | 161.91
2018-02-10 01:30 | 168.07 | 161.15
2018-02-10 02:00 | 167.06 | 160.18
2018-02-10 02:30 | 166.58 | 159.66
2018-02-10 03:00 | 167.33 | 160.42
2018-02-10 03:30 | 166.38 | 159.31
2018-02-10 04:00 | 166.32 | 159.43
2018-02-10 04:30 | 165.48 | 158.46
2018-02-10 05:00 | 166.11 | 159.11
2018-02-10 05:30 | 165.58 | 158.51
2018-02-10 06:00 | 166.15 | 159.46
2018-02-10 06:30 | 167.05 | 160.63
2018-02-10 07:00 | 166.94 | 160.64
2018-02-10 07:30 | 168.98 | 162.2
2018-02-10 08:00 | 170.07 | 162.03
2018-02-10 08:30 | 170.87 | 163.11
2018-02-10 09:00 | 171.55 | 163.68
2018-02-10 09:30 | 172.39 | 164.42
2018-02-10 10:00 | 173.67 | 165.7
2018-02-10 10:30 | 174.7 | 166.68
2018-02-10 11:00 | 205.26 | 197.8
2018-02-10 11:30 | 225.09 | 217.74
2018-02-10 12:00 | 229.54 | 221.71
2018-02-10 12:30 | 240.56 | 232.53
2018-02-10 13:00 | 243.19 | 235
2018-02-10 13:30 | 244.69 | 235.8
2018-02-10 14:00 | 245.61 | 236.8
2018-02-10 14:30 | 246.21 | 237.83
2018-02-10 15:00 | 246.78 | 238.48
2018-02-10 15:30 | 248.97 | 240.36
2018-02-10 16:00 | 250.34 | 241.99
2018-02-10 16:30 | 252.69 | 244.59
2018-02-10 17:00 | 254.56 | 246.72
2018-02-10 17:30 | 256.76 | 249.11
2018-02-10 18:00 | 258.83 | 251.03
2018-02-10 18:30 | 259.6 | 251.73
2018-02-10 19:00 | 259.34 | 251.48
2018-02-10 19:30 | 259.1 | 251.21
2018-02-10 20:00 | 257.68 | 249.49
2018-02-10 20:30 | 254.91 | 246.47
2018-02-10 21:00 | 251.58 | 242.84
2018-02-10 21:30 | 247.54 | 239.74
2018-02-10 22:00 | 243.84 | 235.98
2018-02-10 22:30 | 241.24 | 232.97
2018-02-10 23:00 | 239.08 | 230.39
2018-02-10 23:30 | 220.95 | 212.21
2018-02-11 | 185.07 | 175.81
2018-02-11 00:30 | 175.79 | 166.87
2018-02-11 01:00 | 173.26 | 165.88
2018-02-11 01:30 | 172.33 | 164.89
2018-02-11 02:00 | 171.46 | 164.04
2018-02-11 02:30 | 171.58 | 163.73
2018-02-11 03:00 | 170.89 | 162.87
2018-02-11 03:30 | 170.57 | 162.69
2018-02-11 04:00 | 169.82 | 161.72
2018-02-11 04:30 | 168.48 | 160.71
2018-02-11 05:00 | 169.02 | 161.12
2018-02-11 05:30 | 168.74 | 161.35
2018-02-11 06:00 | 168.43 | 161.16
2018-02-11 06:30 | 168.54 | 161.23
2018-02-11 07:00 | 169.35 | 161.24
2018-02-11 07:30 | 171.62 | 163.81
2018-02-11 08:00 | 175.16 | 165.17
2018-02-11 08:30 | 176.5 | 165.86
2018-02-11 09:00 | 177.93 | 167.44
2018-02-11 09:30 | 179.75 | 169.06
2018-02-11 10:00 | 181.08 | 170.19
2018-02-11 10:30 | 197.9 | 187.64
2018-02-11 11:00 | 234.76 | 225.04
2018-02-11 11:30 | 241.35 | 233.47
2018-02-11 12:00 | 243.58 | 235.63
2018-02-11 12:30 | 245.52 | 237.6
2018-02-11 13:00 | 239.73 | 232.06
2018-02-11 13:30 | 240.12 | 232.37
2018-02-11 14:00 | 243.62 | 235.87
2018-02-11 14:30 | 244.69 | 237.19
2018-02-11 15:00 | 251.11 | 244
2018-02-11 15:30 | 252.16 | 245.51
2018-02-11 16:00 | 213.63 | 210.14
2018-02-11 16:30 | 211.72 | 208.25
2018-02-11 17:00 | 211.49 | 208.06
2018-02-11 17:30 | 210 | 206.54
2018-02-11 18:00 | 209.39 | 205.85
2018-02-11 18:30 | 210.52 | 206.84
2018-02-11 19:00 | 212.75 | 208.9
2018-02-11 19:30 | 211.45 | 207.37
2018-02-11 20:00 | 210.82 | 206.46
2018-02-11 20:30 | 215 | 210.86
2018-02-11 21:00 | 243.53 | 237.5
2018-02-11 21:30 | 248.96 | 242.89
2018-02-11 22:00 | 245.7 | 239.5
2018-02-11 22:30 | 242.61 | 236.07
2018-02-11 23:00 | 239.39 | 232.64
2018-02-11 23:30 | 238.12 | 231.22
2018-02-12 | 219.4 | 212.3
2018-02-12 00:30 | 185 | 177.14
2018-02-12 01:00 | 174.83 | 167.38
2018-02-12 01:30 | 173.74 | 166.2
2018-02-12 02:00 | 173.16 | 165.52
2018-02-12 02:30 | 172.4 | 164.64
2018-02-12 03:00 | 171.93 | 164.05
2018-02-12 03:30 | 170.92 | 163.31
2018-02-12 04:00 | 170.96 | 163.31
2018-02-12 04:30 | 171.09 | 163.59
2018-02-12 05:00 | 171.25 | 163.58
2018-02-12 05:30 | 172.6 | 164.82
2018-02-12 06:00 | 201.43 | 193.97
2018-02-12 06:30 | 219.9 | 212.48
2018-02-12 07:00 | 232.1 | 224.44
2018-02-12 07:30 | 236.64 | 229.06
2018-02-12 08:00 | 237.84 | 230.63
2018-02-12 08:30 | 239.2 | 232.27
2018-02-12 09:00 | 240.73 | 233.91
2018-02-12 09:30 | 242.15 | 235.38
2018-02-12 10:00 | 244.77 | 238.12
2018-02-12 10:30 | 246.38 | 239.91
2018-02-12 11:00 | 248.63 | 242.43
2018-02-12 11:30 | 249.68 | 243.69
2018-02-12 12:00 | 251.22 | 246.09
2018-02-12 12:30 | 254.15 | 249.46
2018-02-12 13:00 | 257.06 | 252.28
2018-02-12 13:30 | 257.92 | 253.18
2018-02-12 14:00 | 258.45 | 254.2
2018-02-12 14:30 | 247.05 | 243.09
2018-02-12 15:00 | 229.1 | 225.67
2018-02-12 15:30 | 230.81 | 227.45
2018-02-12 16:00 | 232.66 | 229.46
2018-02-12 16:30 | 234.08 | 230.84
2018-02-12 17:00 | 235.16 | 231.84
2018-02-12 17:30 | 234.15 | 230.69
2018-02-12 18:00 | 235.79 | 232.2
2018-02-12 18:30 | 235.94 | 232.3
2018-02-12 19:00 | 236.04 | 232.42
2018-02-12 19:30 | 235.42 | 231.78
2018-02-12 20:00 | 235.06 | 231.26
2018-02-12 20:30 | 232.85 | 228.82
2018-02-12 21:00 | 254.18 | 248.72
2018-02-12 21:30 | 255.15 | 249.8
2018-02-12 22:00 | 251.11 | 245.2
2018-02-12 22:30 | 248.28 | 241.89
2018-02-12 23:00 | 245.69 | 238.81
2018-02-12 23:30 | 243.73 | 236.67
2018-02-13 | 240.86 | 234.14
2018-02-13 00:30 | 238.89 | 231.87
2018-02-13 01:00 | 237.89 | 230.66
2018-02-13 01:30 | 219.36 | 212.93
2018-02-13 02:00 | 188 | 181.45
2018-02-13 02:30 | 177.66 | 170.84
2018-02-13 03:00 | 177.18 | 170.29
2018-02-13 03:30 | 176.83 | 169.81
2018-02-13 04:00 | 176.45 | 169.37
2018-02-13 04:30 | 176.5 | 169.5
2018-02-13 05:00 | 176.32 | 169.38
2018-02-13 05:30 | 178.45 | 170.5
2018-02-13 06:00 | 180.21 | 171.75
2018-02-13 06:30 | 181.86 | 173.54
2018-02-13 07:00 | 209.84 | 201.81
2018-02-13 07:30 | 229.29 | 221.34
2018-02-13 08:00 | 236.85 | 229.5
2018-02-13 08:30 | 243.39 | 236.63
2018-02-13 09:00 | 244.76 | 238.17
2018-02-13 09:30 | 245.55 | 238.9
2018-02-13 10:00 | 246.96 | 240.52
2018-02-13 10:30 | 247.36 | 241.06
2018-02-13 11:00 | 248.32 | 242.57
2018-02-13 11:30 | 250.67 | 245.12
2018-02-13 12:00 | 252.38 | 247.06
2018-02-13 12:30 | 237.73 | 232.86
2018-02-13 13:00 | 223.51 | 218.95
2018-02-13 13:30 | 225.27 | 220.68
2018-02-13 14:00 | 226.89 | 222.55
2018-02-13 14:30 | 216.3 | 212.58
2018-02-13 15:00 | 212.47 | 208.93
2018-02-13 15:30 | 211.48 | 208.06
2018-02-13 16:00 | 208.9 | 205.51
2018-02-13 16:30 | 207.79 | 204.53
2018-02-13 17:00 | 202.25 | 198.47
2018-02-13 17:30 | 199.5 | 194.33
2018-02-13 18:00 | 205.69 | 201.11
2018-02-13 18:30 | 205.56 | 201.3
2018-02-13 19:00 | 205.53 | 201.42
2018-02-13 19:30 | 205.81 | 201.54
2018-02-13 20:00 | 208.61 | 204.26
2018-02-13 20:30 | 213.18 | 208.65
2018-02-13 21:00 | 217.68 | 212.98
2018-02-13 21:30 | 244.84 | 239.73
2018-02-13 22:00 | 248.98 | 243.36
2018-02-13 22:30 | 245.06 | 239.14
2018-02-13 23:00 | 241.47 | 235.22
2018-02-13 23:30 | 222.35 | 215.84
2018-02-14 | 189.66 | 183.1
2018-02-14 00:30 | 179.17 | 172.44
2018-02-14 01:00 | 177.36 | 170.77
2018-02-14 01:30 | 175.96 | 169.62
2018-02-14 02:00 | 174.52 | 167.95
2018-02-14 02:30 | 174 | 167.37
2018-02-14 03:00 | 173.68 | 167.1
2018-02-14 03:30 | 173.53 | 166.93
2018-02-14 04:00 | 173.2 | 166.6
2018-02-14 04:30 | 173.01 | 166.56
2018-02-14 05:00 | 172.99 | 166.72
2018-02-14 05:30 | 173.53 | 167.46
2018-02-14 06:00 | 174.25 | 168.55
2018-02-14 06:30 | 203.81 | 198.16
2018-02-14 07:00 | 221.45 | 215.9
2018-02-14 07:30 | 225.6 | 220.22
2018-02-14 08:00 | 227.65 | 222.32
2018-02-14 08:30 | 228.32 | 223.19
2018-02-14 09:00 | 230.04 | 225.1
2018-02-14 09:30 | 232.05 | 227.02
2018-02-14 10:00 | 241.46 | 236.42
2018-02-14 10:30 | 245.38 | 240.47
2018-02-14 11:00 | 247.19 | 242.43
2018-02-14 11:30 | 249.09 | 244.21
2018-02-14 12:00 | 251.53 | 246.67
2018-02-14 12:30 | 253.05 | 247.82
2018-02-14 13:00 | 255.15 | 250.03
2018-02-14 13:30 | 256.48 | 251.27
2018-02-14 14:00 | 258.56 | 253.8
2018-02-14 14:30 | 242.77 | 238.79
2018-02-14 15:00 | 224.7 | 220.43
2018-02-14 15:30 | 221.35 | 216.82
2018-02-14 16:00 | 215.5 | 212.5
2018-02-14 16:30 | 215.52 | 212.59
2018-02-14 17:00 | 217.14 | 214.15
2018-02-14 17:30 | 215.93 | 212.83
2018-02-14 18:00 | 215.68 | 212.44
2018-02-14 18:30 | 217.09 | 213.77
2018-02-14 19:00 | 217.99 | 214.63
2018-02-14 19:30 | 219.08 | 215.38
2018-02-14 20:00 | 222.09 | 218.3
2018-02-14 20:30 | 224.24 | 220.46
2018-02-14 21:00 | 226.03 | 222.47
2018-02-14 21:30 | 227.9 | 224.73
2018-02-14 22:00 | 230.67 | 227.68
2018-02-14 22:30 | 233.07 | 230.29
2018-02-14 23:00 | 234.11 | 228.77
2018-02-14 23:30 | 236.82 | 229.57
2018-02-15 | 235.13 | 227.69
2018-02-15 00:30 | 233.23 | 225.82
2018-02-15 01:00 | 232.18 | 224.63
2018-02-15 01:30 | 231.7 | 224.11
2018-02-15 02:00 | 231.29 | 223.62
2018-02-15 02:30 | 229.74 | 221.9
2018-02-15 03:00 | 229.7 | 221.76
2018-02-15 03:30 | 229.15 | 221.33
2018-02-15 04:00 | 229.05 | 221.32
2018-02-15 04:30 | 229.12 | 221.45
2018-02-15 05:00 | 230.06 | 222.38
2018-02-15 05:30 | 232.1 | 224.69
2018-02-15 06:00 | 233.36 | 225.93
2018-02-15 06:30 | 235.3 | 227.36
2018-02-15 07:00 | 236.49 | 228.7
2018-02-15 07:30 | 237.44 | 230.14
2018-02-15 08:00 | 237.86 | 230.68
2018-02-15 08:30 | 238.54 | 231.6
2018-02-15 09:00 | 239.74 | 232.46
2018-02-15 09:30 | 240.36 | 233.15
2018-02-15 10:00 | 241.8 | 234.82
2018-02-15 10:30 | 242.41 | 235.72
2018-02-15 11:00 | 240.68 | 234.58
2018-02-15 11:30 | 224.16 | 220.88
2018-02-15 12:00 | 222.71 | 219.36
2018-02-15 12:30 | 220.78 | 217.3
2018-02-15 13:00 | 220.02 | 216.43
2018-02-15 13:30 | 218.74 | 215.02
2018-02-15 14:00 | 216.23 | 212.44
2018-02-15 14:30 | 215.19 | 211.38
2018-02-15 15:00 | 214.49 | 210.64
2018-02-15 15:30 | 213.23 | 209.22
2018-02-15 16:00 | 212.22 | 208.15
2018-02-15 16:30 | 211.84 | 207.64
2018-02-15 17:00 | 210.77 | 206.43
2018-02-15 17:30 | 210.97 | 206.52
2018-02-15 18:00 | 210.59 | 206.01
2018-02-15 18:30 | 211.01 | 206.33
2018-02-15 19:00 | 211.91 | 207.38
2018-02-15 19:30 | 213.09 | 208.6
2018-02-15 20:00 | 214.88 | 210.55
2018-02-15 20:30 | 218.35 | 214.45
2018-02-15 21:00 | 220.93 | 217.19
2018-02-15 21:30 | 223.38 | 220.14
2018-02-15 22:00 | 238.63 | 232.66
2018-02-15 22:30 | 243.45 | 236.19
2018-02-15 23:00 | 240.75 | 233.42
2018-02-15 23:30 | 238.88 | 231.3
2018-02-16 | 236.62 | 229.18
2018-02-16 00:30 | 234.8 | 227.9
2018-02-16 01:00 | 233.39 | 226.87
2018-02-16 01:30 | 220.53 | 213.91
2018-02-16 02:00 | 210.32 | 203.77
2018-02-16 02:30 | 209.72 | 203.06
2018-02-16 03:00 | 208.93 | 202.3
2018-02-16 03:30 | 208.08 | 201.32
2018-02-16 04:00 | 207.91 | 201.12
2018-02-16 04:30 | 208.12 | 201.3
2018-02-16 05:00 | 208.97 | 202.26
2018-02-16 05:30 | 209.44 | 202.92
2018-02-16 06:00 | 209.99 | 203.54
2018-02-16 06:30 | 212.11 | 205.48
2018-02-16 07:00 | 214.74 | 207.49
2018-02-16 07:30 | 217.76 | 209.89
2018-02-16 08:00 | 219.73 | 211.9
2018-02-16 08:30 | 220.52 | 212.76
2018-02-16 09:00 | 221.71 | 213.99
2018-02-16 09:30 | 222.17 | 214.72
2018-02-16 10:00 | 223.38 | 216.22
2018-02-16 10:30 | 224.2 | 216.96
2018-02-16 11:00 | 236.1 | 229.19
2018-02-16 11:30 | 244.25 | 237.58
2018-02-16 12:00 | 245.76 | 239.56
2018-02-16 12:30 | 246.84 | 240.84
2018-02-16 13:00 | 248.44 | 242.44
2018-02-16 13:30 | 249.38 | 243.53
2018-02-16 14:00 | 227.84 | 223.11
2018-02-16 14:30 | 217.71 | 214.24
2018-02-16 15:00 | 216.91 | 214.22
2018-02-16 15:30 | 215.22 | 212.4
2018-02-16 16:00 | 214.64 | 211.72
2018-02-16 16:30 | 214.11 | 211.07
2018-02-16 17:00 | 213.69 | 210.53
2018-02-16 17:30 | 214.38 | 211.07
2018-02-16 18:00 | 214.54 | 211.19
2018-02-16 18:30 | 215.74 | 212.39
2018-02-16 19:00 | 217.01 | 213.75
2018-02-16 19:30 | 217.97 | 214.75
2018-02-16 20:00 | 219.71 | 216.58
2018-02-16 20:30 | 243.41 | 237.64
2018-02-16 21:00 | 250.16 | 243.21
2018-02-16 21:30 | 246.82 | 240.55
2018-02-16 22:00 | 243.84 | 237.56
2018-02-16 22:30 | 241.1 | 234.51
2018-02-16 23:00 | 238.08 | 231.21
2018-02-16 23:30 | 236.72 | 229.58
2018-02-17 | 216.27 | 209.74
2018-02-17 00:30 | 181.54 | 174.71
2018-02-17 01:00 | 172.31 | 165.78
2018-02-17 01:30 | 171.06 | 164.56
2018-02-17 02:00 | 170.37 | 163.98
2018-02-17 02:30 | 169.46 | 163.12
2018-02-17 03:00 | 169.08 | 162.6
2018-02-17 03:30 | 168.33 | 161.73
2018-02-17 04:00 | 168.32 | 161.66
2018-02-17 04:30 | 168.28 | 161.62
2018-02-17 05:00 | 167.64 | 161.07
2018-02-17 05:30 | 167.67 | 161.24
2018-02-17 06:00 | 167.63 | 161.2
2018-02-17 06:30 | 167.87 | 161.44
2018-02-17 07:00 | 168.69 | 161.55
2018-02-17 07:30 | 170.98 | 163.36
2018-02-17 08:00 | 172.87 | 163.93
2018-02-17 08:30 | 173.52 | 164.73
2018-02-17 09:00 | 173.79 | 165.45
2018-02-17 09:30 | 174.4 | 166.25
2018-02-17 10:00 | 175.39 | 167.31
2018-02-17 10:30 | 178.23 | 169.16
2018-02-17 11:00 | 180.21 | 171.08
2018-02-17 11:30 | 182.21 | 173.17
2018-02-17 12:00 | 183.83 | 174.88
2018-02-17 12:30 | 185.4 | 176.92
2018-02-17 13:00 | 186.76 | 178.39
2018-02-17 13:30 | 186.99 | 179.59
2018-02-17 14:00 | 187.49 | 180.29
2018-02-17 14:30 | 188.48 | 181.4
2018-02-17 15:00 | 189.49 | 182.52
2018-02-17 15:30 | 216.08 | 209.43
2018-02-17 16:00 | 243.02 | 236.4
2018-02-17 16:30 | 249.95 | 243.28
2018-02-17 17:00 | 251.61 | 245.11
2018-02-17 17:30 | 254.05 | 247.63
2018-02-17 18:00 | 255.26 | 249.03
2018-02-17 18:30 | 255.35 | 249.2
2018-02-17 19:00 | 254.46 | 248.28
2018-02-17 19:30 | 253.91 | 247.73
2018-02-17 20:00 | 252.28 | 245.87
2018-02-17 20:30 | 250.05 | 243.06
2018-02-17 21:00 | 247.55 | 240.42
2018-02-17 21:30 | 227.54 | 221.06
2018-02-17 22:00 | 193.53 | 187.02
2018-02-17 22:30 | 180.26 | 173.79
2018-02-17 23:00 | 178.62 | 171.87
2018-02-17 23:30 | 177.41 | 170.64
2018-02-18 | 175.29 | 168.54
2018-02-18 00:30 | 173.42 | 167.15
2018-02-18 01:00 | 172.05 | 165.74
2018-02-18 01:30 | 171.18 | 164.85
2018-02-18 02:00 | 170.57 | 164.12
2018-02-18 02:30 | 170.06 | 163.63
2018-02-18 03:00 | 170.09 | 163.67
2018-02-18 03:30 | 169.17 | 162.66
2018-02-18 04:00 | 169.14 | 162.58
2018-02-18 04:30 | 168.78 | 162.22
2018-02-18 05:00 | 169.34 | 162.96
2018-02-18 05:30 | 168.67 | 162.36
2018-02-18 06:00 | 169.42 | 162.92
2018-02-18 06:30 | 168.08 | 161.52
2018-02-18 07:00 | 168.41 | 161.84
2018-02-18 07:30 | 169.38 | 162.68
2018-02-18 08:00 | 171.26 | 164.48
2018-02-18 08:30 | 172.19 | 165.18
2018-02-18 09:00 | 174.63 | 167.52
2018-02-18 09:30 | 176.18 | 168.8
2018-02-18 10:00 | 177.6 | 170.3
2018-02-18 10:30 | 178.65 | 171.65
2018-02-18 11:00 | 180.07 | 173.31
2018-02-18 11:30 | 181.65 | 174.89
2018-02-18 12:00 | 183.49 | 177.17
2018-02-18 12:30 | 185.88 | 179.72
2018-02-18 13:00 | 188.25 | 181.63
2018-02-18 13:30 | 190.35 | 183.57
2018-02-18 14:00 | 192.16 | 185.03
2018-02-18 14:30 | 191.45 | 184.44
2018-02-18 15:00 | 193.49 | 187
2018-02-18 15:30 | 221.49 | 215.01
2018-02-18 16:00 | 247.24 | 240.56
2018-02-18 16:30 | 254.79 | 248.07
2018-02-18 17:00 | 256.78 | 250.44
2018-02-18 17:30 | 257.84 | 251.55
2018-02-18 18:00 | 259.44 | 253.24
2018-02-18 18:30 | 260.61 | 254.64
2018-02-18 19:00 | 260.34 | 254.28
2018-02-18 19:30 | 259.34 | 253.36
2018-02-18 20:00 | 257.77 | 251.56
2018-02-18 20:30 | 254.92 | 248.28
2018-02-18 21:00 | 251.45 | 244.51
2018-02-18 21:30 | 231.15 | 224.79
2018-02-18 22:00 | 193.29 | 186.32
2018-02-18 22:30 | 182.64 | 175.55
2018-02-18 23:00 | 180.23 | 172.84
2018-02-18 23:30 | 179.06 | 171.62
2018-02-19 | 176.61 | 169.92
2018-02-19 00:30 | 175.09 | 168.47
2018-02-19 01:00 | 173.99 | 167.49
2018-02-19 01:30 | 172.8 | 166.2
2018-02-19 02:00 | 172.78 | 166.04
2018-02-19 02:30 | 171.7 | 164.67
2018-02-19 03:00 | 171.84 | 164.35
2018-02-19 03:30 | 171.71 | 164.14
2018-02-19 04:00 | 171.09 | 163.6
2018-02-19 04:30 | 170.84 | 163.46
2018-02-19 05:00 | 171.88 | 164.66
2018-02-19 05:30 | 172.67 | 165.62
2018-02-19 06:00 | 173.6 | 166.35
2018-02-19 06:30 | 175.91 | 168.07
2018-02-19 07:00 | 177.13 | 169.39
2018-02-19 07:30 | 179.8 | 172.02
2018-02-19 08:00 | 180.81 | 173.44
2018-02-19 08:30 | 181.73 | 174.63
2018-02-19 09:00 | 183.02 | 175.79
2018-02-19 09:30 | 183.93 | 176.81
2018-02-19 10:00 | 212.87 | 206.32
2018-02-19 10:30 | 237.44 | 230.97
2018-02-19 11:00 | 244.52 | 238.19
2018-02-19 11:30 | 245.71 | 239.69
2018-02-19 12:00 | 247.59 | 241.53
2018-02-19 12:30 | 250.28 | 244.48
2018-02-19 13:00 | 252.17 | 246.62
2018-02-19 13:30 | 253.52 | 248.06
2018-02-19 14:00 | 255.62 | 250.51
2018-02-19 14:30 | 255.07 | 250.03
2018-02-19 15:00 | 251.84 | 246.12
2018-02-19 15:30 | 250.76 | 244.89
2018-02-19 16:00 | 253.18 | 247.51
2018-02-19 16:30 | 253.82 | 248.12
2018-02-19 17:00 | 255.5 | 249.77
2018-02-19 17:30 | 254.47 | 248.1
2018-02-19 18:00 | 255.19 | 248.68
2018-02-19 18:30 | 256.58 | 250.05
2018-02-19 19:00 | 259.15 | 252.89
2018-02-19 19:30 | 259.08 | 252.49
2018-02-19 20:00 | 256.83 | 249.96
2018-02-19 20:30 | 253.99 | 246.71
2018-02-19 21:00 | 251.1 | 243.55
2018-02-19 21:30 | 246.86 | 240.13
2018-02-19 22:00 | 243.1 | 237.39
2018-02-19 22:30 | 223.39 | 217.51
2018-02-19 23:00 | 187.03 | 180.73
2018-02-19 23:30 | 178.18 | 171.49
2018-02-20 | 176.54 | 170.1
2018-02-20 00:30 | 175.48 | 169.1
2018-02-20 01:00 | 174.41 | 167.99
2018-02-20 01:30 | 173.88 | 167.36
2018-02-20 02:00 | 173.18 | 166.76
2018-02-20 02:30 | 172.81 | 166.52
2018-02-20 03:00 | 172.12 | 165.72
2018-02-20 03:30 | 172.05 | 165.8
2018-02-20 04:00 | 172.06 | 165.85
2018-02-20 04:30 | 172.16 | 165.77
2018-02-20 05:00 | 172.67 | 166.2
2018-02-20 05:30 | 173.78 | 167.5
2018-02-20 06:00 | 175.21 | 168.74
2018-02-20 06:30 | 174.58 | 167.89
2018-02-20 07:00 | 175.39 | 168.39
2018-02-20 07:30 | 230.6 | 224.57
2018-02-20 08:00 | 247.65 | 241.48
2018-02-20 08:30 | 247.49 | 241.57
2018-02-20 09:00 | 262.27 | 256.04
2018-02-20 09:30 | 267.72 | 259.94
2018-02-20 10:00 | 268.28 | 260.34
2018-02-20 10:30 | 267.73 | 260.79
2018-02-20 11:00 | 257.11 | 250.22
2018-02-20 11:30 | 248.16 | 240.71
2018-02-20 12:00 | 241.99 | 234.98
2018-02-20 12:30 | 243.18 | 236.61
2018-02-20 13:00 | 241.73 | 234.8
2018-02-20 13:30 | 237.02 | 229.83
2018-02-20 14:00 | 235.53 | 228.23
2018-02-20 14:30 | 236.15 | 228.46
2018-02-20 15:00 | 236.86 | 229.14
2018-02-20 15:30 | 235.57 | 227.89
2018-02-20 16:00 | 235.42 | 227.82
2018-02-20 16:30 | 235.32 | 227.8
2018-02-20 17:00 | 236.51 | 229.1
2018-02-20 17:30 | 238.12 | 230.07
2018-02-20 18:00 | 239.44 | 230.93
2018-02-20 18:30 | 240.16 | 231.6
2018-02-20 19:00 | 241.11 | 232.66
2018-02-20 19:30 | 241.79 | 233.26
2018-02-20 20:00 | 240.96 | 232.26
2018-02-20 20:30 | 239.44 | 230.5
2018-02-20 21:00 | 220.46 | 211.5
2018-02-20 21:30 | 212.77 | 205.12
2018-02-20 22:00 | 211.67 | 203.75
2018-02-20 22:30 | 208.87 | 201.3
2018-02-20 23:00 | 207.06 | 199.21
2018-02-20 23:30 | 206.14 | 198.17
2018-02-21 | 205.21 | 197.18
2018-02-21 00:30 | 204.37 | 196.4
2018-02-21 01:00 | 203.18 | 195.32
2018-02-21 01:30 | 202.75 | 194.76
2018-02-21 02:00 | 202.62 | 194.88
2018-02-21 02:30 | 204.44 | 196.43
2018-02-21 03:00 | 204.66 | 196.31
2018-02-21 03:30 | 205.02 | 196.48
2018-02-21 04:00 | 205.39 | 196.75
2018-02-21 04:30 | 205.04 | 196.52
2018-02-21 05:00 | 205.59 | 197.29
2018-02-21 05:30 | 206.69 | 198.53
2018-02-21 06:00 | 208.19 | 199.96
2018-02-21 06:30 | 224.72 | 216.41
2018-02-21 07:00 | 232.11 | 223.82
2018-02-21 07:30 | 233.62 | 225.45
2018-02-21 08:00 | 233.4 | 225.26
2018-02-21 08:30 | 233.11 | 225.01
2018-02-21 09:00 | 232.63 | 224.55
2018-02-21 09:30 | 232.06 | 223.89
2018-02-21 10:00 | 232.26 | 224.04
2018-02-21 10:30 | 231.57 | 223.33
2018-02-21 11:00 | 231.64 | 223.35
2018-02-21 11:30 | 231.38 | 223.04
2018-02-21 12:00 | 231.13 | 222.9
2018-02-21 12:30 | 231.06 | 222.83
2018-02-21 13:00 | 231.83 | 223.49
2018-02-21 13:30 | 232.6 | 224.42
2018-02-21 14:00 | 232.46 | 224.21
2018-02-21 14:30 | 232.98 | 224.64
2018-02-21 15:00 | 233.06 | 224.84
2018-02-21 15:30 | 233.87 | 225.74
2018-02-21 16:00 | 235.09 | 226.92
2018-02-21 16:30 | 235.43 | 227.1
2018-02-21 17:00 | 236.23 | 227.81
2018-02-21 17:30 | 236.7 | 228.27
2018-02-21 18:00 | 238.42 | 229.96
2018-02-21 18:30 | 239.72 | 231.34
2018-02-21 19:00 | 240.91 | 232.75
2018-02-21 19:30 | 241.69 | 233.41
2018-02-21 20:00 | 240.74 | 232.24
2018-02-21 20:30 | 240.29 | 231.55
2018-02-21 21:00 | 238.25 | 229.39
2018-02-21 21:30 | 236.58 | 228.99
2018-02-21 22:00 | 235.04 | 227.36
2018-02-21 22:30 | 233.16 | 225.28
2018-02-21 23:00 | 231.92 | 223.74
2018-02-21 23:30 | 230.78 | 222.7
2018-02-22 | 229.74 | 221.76
2018-02-22 00:30 | 228.88 | 220.8
2018-02-22 01:00 | 209.45 | 202.48
2018-02-22 01:30 | 172.66 | 165.77
2018-02-22 02:00 | 167.05 | 158.83
2018-02-22 02:30 | 166.05 | 157.4
2018-02-22 03:00 | 166.53 | 157.64
2018-02-22 03:30 | 166.82 | 157.81
2018-02-22 04:00 | 166.92 | 157.99
2018-02-22 04:30 | 167.15 | 158.25
2018-02-22 05:00 | 167.28 | 158.28
2018-02-22 05:30 | 168.26 | 159.35
2018-02-22 06:00 | 169.58 | 160.69
2018-02-22 06:30 | 172.28 | 162.06
2018-02-22 07:00 | 201.89 | 192.22
2018-02-22 07:30 | 227.61 | 218.46
2018-02-22 08:00 | 235.27 | 226.52
2018-02-22 08:30 | 235.15 | 226.41
2018-02-22 09:00 | 234.32 | 225.38
2018-02-22 09:30 | 234.12 | 225.13
2018-02-22 10:00 | 233.26 | 224.21
2018-02-22 10:30 | 232.22 | 223.08
2018-02-22 11:00 | 232.34 | 223.32
2018-02-22 11:30 | 233.77 | 224.6
2018-02-22 12:00 | 234.28 | 225.15
2018-02-22 12:30 | 235.35 | 226.15
2018-02-22 13:00 | 236.47 | 227.14
2018-02-22 13:30 | 235.99 | 226.49
2018-02-22 14:00 | 235.6 | 226.24
2018-02-22 14:30 | 235.44 | 225.93
2018-02-22 15:00 | 235.07 | 225.85
2018-02-22 15:30 | 236.61 | 227.26
2018-02-22 16:00 | 237.08 | 227.58
2018-02-22 16:30 | 237.87 | 228.07
2018-02-22 17:00 | 237.82 | 227.83
2018-02-22 17:30 | 238.37 | 228.31
2018-02-22 18:00 | 239.86 | 229.88
2018-02-22 18:30 | 241.13 | 230.91
2018-02-22 19:00 | 242.22 | 232.21
2018-02-22 19:30 | 243.59 | 233.6
2018-02-22 20:00 | 243.07 | 232.75
2018-02-22 20:30 | 241.74 | 231.22
2018-02-22 21:00 | 240.27 | 229.4
2018-02-22 21:30 | 238.71 | 228.58
2018-02-22 22:00 | 236.98 | 227
2018-02-22 22:30 | 234.89 | 224.69
2018-02-22 23:00 | 233.75 | 223.15
2018-02-22 23:30 | 233.14 | 222.29
2018-02-23 | 215.73 | 204.68
2018-02-23 00:30 | 178.56 | 168
2018-02-23 01:00 | 170.11 | 159.88
2018-02-23 01:30 | 169.27 | 160.03
2018-02-23 02:00 | 168.61 | 160.1
2018-02-23 02:30 | 168.33 | 159.82
2018-02-23 03:00 | 167.72 | 159.29
2018-02-23 03:30 | 167.45 | 158.93
2018-02-23 04:00 | 167.83 | 159.26
2018-02-23 04:30 | 168.22 | 159.71
2018-02-23 05:00 | 168.67 | 160.07
2018-02-23 05:30 | 169.63 | 160.83
2018-02-23 06:00 | 171.97 | 162.16
2018-02-23 06:30 | 173.47 | 163.87
2018-02-23 07:00 | 203.22 | 193.56
2018-02-23 07:30 | 227.37 | 218.99
2018-02-23 08:00 | 234.18 | 226.47
2018-02-23 08:30 | 233.12 | 225.42
2018-02-23 09:00 | 232.39 | 224.74
2018-02-23 09:30 | 231.93 | 224.02
2018-02-23 10:00 | 232.31 | 224.52
2018-02-23 10:30 | 232.12 | 224.26
2018-02-23 11:00 | 232.49 | 224.78
2018-02-23 11:30 | 233.08 | 225.33
2018-02-23 12:00 | 233.06 | 225.35
2018-02-23 12:30 | 234.24 | 226.38
2018-02-23 13:00 | 234.71 | 226.82
2018-02-23 13:30 | 234.78 | 227.02
2018-02-23 14:00 | 235.35 | 227.73
2018-02-23 14:30 | 235.58 | 227.96
2018-02-23 15:00 | 236.46 | 228.84
2018-02-23 15:30 | 239.22 | 231.7
2018-02-23 16:00 | 239.62 | 231.91
2018-02-23 16:30 | 239.43 | 231.81
2018-02-23 17:00 | 239.98 | 232.35
2018-02-23 17:30 | 240.48 | 232.55
2018-02-23 18:00 | 241.48 | 233.52
2018-02-23 18:30 | 245.97 | 238.52
2018-02-23 19:00 | 253.46 | 247.08
2018-02-23 19:30 | 255.49 | 249.04
2018-02-23 20:00 | 254.89 | 248.36
2018-02-23 20:30 | 253.67 | 247
2018-02-23 21:00 | 251.67 | 244.95
2018-02-23 21:30 | 248.93 | 243.32
2018-02-23 22:00 | 247.19 | 241.53
2018-02-23 22:30 | 245.13 | 239.2
2018-02-23 23:00 | 243.19 | 237.31
2018-02-23 23:30 | 241.94 | 235.79
2018-02-24 | 225.49 | 219.38
2018-02-24 00:30 | 189.81 | 183.93
2018-02-24 01:00 | 180.86 | 174.95
2018-02-24 01:30 | 179.95 | 173.89
2018-02-24 02:00 | 179.97 | 173.96
2018-02-24 02:30 | 179.77 | 173.8
2018-02-24 03:00 | 178.92 | 172.89
2018-02-24 03:30 | 179.08 | 173.02
2018-02-24 04:00 | 179.57 | 173.43
2018-02-24 04:30 | 179.04 | 172.96
2018-02-24 05:00 | 179.17 | 173.15
2018-02-24 05:30 | 179.39 | 173.52
2018-02-24 06:00 | 179.81 | 174.08
2018-02-24 06:30 | 180.35 | 174.92
2018-02-24 07:00 | 181.29 | 175.96
2018-02-24 07:30 | 181.59 | 176.49
2018-02-24 08:00 | 182.42 | 177.43
2018-02-24 08:30 | 182.15 | 177.11
2018-02-24 09:00 | 182.59 | 177.41
2018-02-24 09:30 | 182.79 | 177.86
2018-02-24 10:00 | 182.86 | 177.95
2018-02-24 10:30 | 183.24 | 178.26
2018-02-24 11:00 | 183.69 | 178.86
2018-02-24 11:30 | 211.22 | 206.45
2018-02-24 12:00 | 230.9 | 226.29
2018-02-24 12:30 | 243.24 | 238.39
2018-02-24 13:00 | 244.52 | 239.64
2018-02-24 13:30 | 244.59 | 239.73
2018-02-24 14:00 | 245.64 | 240.71
2018-02-24 14:30 | 241.27 | 235.61
2018-02-24 15:00 | 235.14 | 228.83
2018-02-24 15:30 | 234.39 | 227.96
2018-02-24 16:00 | 234.77 | 228.47
2018-02-24 16:30 | 236.27 | 230.27
2018-02-24 17:00 | 237.05 | 231.07
2018-02-24 17:30 | 238.94 | 232.81
2018-02-24 18:00 | 240.7 | 234.6
2018-02-24 18:30 | 241.81 | 235.71
2018-02-24 19:00 | 242.11 | 236.26
2018-02-24 19:30 | 242 | 236.21
2018-02-24 20:00 | 241.53 | 235.53
2018-02-24 20:30 | 239.83 | 233.67
2018-02-24 21:00 | 238.09 | 231.67
2018-02-24 21:30 | 237.25 | 230.53
2018-02-24 22:00 | 220.03 | 213.06
2018-02-24 22:30 | 185.36 | 178.17
2018-02-24 23:00 | 175.81 | 168.28
2018-02-24 23:30 | 175.22 | 167.2
2018-02-25 | 172.16 | 165.29
2018-02-25 00:30 | 171.07 | 164.42
2018-02-25 01:00 | 170.12 | 163.63
2018-02-25 01:30 | 169.71 | 163.64
2018-02-25 02:00 | 168.99 | 162.68
2018-02-25 02:30 | 168.65 | 162.52
2018-02-25 03:00 | 168.1 | 162.12
2018-02-25 03:30 | 168.35 | 161.52
2018-02-25 04:00 | 168.35 | 161.39
2018-02-25 04:30 | 168.17 | 161.11
2018-02-25 05:00 | 168.51 | 161.49
2018-02-25 05:30 | 168.81 | 161.82
2018-02-25 06:00 | 169.42 | 162.47
2018-02-25 06:30 | 169.97 | 162.84
2018-02-25 07:00 | 169.91 | 163.05
2018-02-25 07:30 | 171 | 164.24
2018-02-25 08:00 | 171.16 | 164.41
2018-02-25 08:30 | 171.85 | 164.81
2018-02-25 09:00 | 173.12 | 165.94
2018-02-25 09:30 | 173.5 | 164.98
2018-02-25 10:00 | 173.96 | 165.36
2018-02-25 10:30 | 174.62 | 166.27
2018-02-25 11:00 | 175.72 | 167.34
2018-02-25 11:30 | 177.3 | 169.06
2018-02-25 12:00 | 178.3 | 170.17
2018-02-25 12:30 | 179.98 | 172.11
2018-02-25 13:00 | 181.29 | 173.76
2018-02-25 13:30 | 182.3 | 175.14
2018-02-25 14:00 | 177.12 | 172.28
2018-02-25 14:30 | 172.79 | 170.74
2018-02-25 15:00 | 198.45 | 196.15
2018-02-25 15:30 | 221.47 | 218.87
2018-02-25 16:00 | 226.43 | 223.8
2018-02-25 16:30 | 226.34 | 223.62
2018-02-25 17:00 | 225.13 | 222.26
2018-02-25 17:30 | 222.84 | 219.79
2018-02-25 18:00 | 222.26 | 219.23
2018-02-25 18:30 | 223.73 | 220.74
2018-02-25 19:00 | 222.66 | 219.73
2018-02-25 19:30 | 222.78 | 219.87
2018-02-25 20:00 | 224.42 | 221.55
2018-02-25 20:30 | 227.14 | 224.38
2018-02-25 21:00 | 229.65 | 227.05
2018-02-25 21:30 | 216.95 | 211.44
2018-02-25 22:00 | 189 | 180.6
2018-02-25 22:30 | 181.06 | 172.38
2018-02-25 23:00 | 178.91 | 169.82
2018-02-25 23:30 | 178.51 | 169.25
2018-02-26 | 177.54 | 168.27
2018-02-26 00:30 | 176.27 | 167.04
2018-02-26 01:00 | 175.1 | 166.3
2018-02-26 01:30 | 173.83 | 165.63
2018-02-26 02:00 | 173.91 | 165.41
2018-02-26 02:30 | 173.31 | 164.78
2018-02-26 03:00 | 173.01 | 164.55
2018-02-26 03:30 | 173.03 | 164.45
2018-02-26 04:00 | 172.25 | 163.66
2018-02-26 04:30 | 171.97 | 163.72
2018-02-26 05:00 | 173.13 | 165.05
2018-02-26 05:30 | 174.17 | 165.55
2018-02-26 06:00 | 175.63 | 166.22
2018-02-26 06:30 | 177.72 | 168.04
2018-02-26 07:00 | 206.39 | 197.52
2018-02-26 07:30 | 231.84 | 222.97
2018-02-26 08:00 | 237.81 | 229.05
2018-02-26 08:30 | 237.93 | 229.46
2018-02-26 09:00 | 237.45 | 229.18
2018-02-26 09:30 | 240.26 | 232.22
2018-02-26 10:00 | 246.41 | 239.09
2018-02-26 10:30 | 242.17 | 234.22
2018-02-26 11:00 | 238.82 | 230.58
2018-02-26 11:30 | 239 | 230.7
2018-02-26 12:00 | 239.38 | 231.21
2018-02-26 12:30 | 240.4 | 232.16
2018-02-26 13:00 | 241.78 | 233.31
2018-02-26 13:30 | 242.87 | 234.47
2018-02-26 14:00 | 243.99 | 236.03
2018-02-26 14:30 | 242.44 | 234.87
2018-02-26 15:00 | 244.87 | 237.48
2018-02-26 15:30 | 229.84 | 224.08
2018-02-26 16:00 | 226.33 | 222.73
2018-02-26 16:30 | 225.7 | 222.03
2018-02-26 17:00 | 225.75 | 221.95
2018-02-26 17:30 | 226.31 | 222.38
2018-02-26 18:00 | 226.09 | 222.04
2018-02-26 18:30 | 226.01 | 221.88
2018-02-26 19:00 | 226.38 | 222.29
2018-02-26 19:30 | 226.68 | 222.53
2018-02-26 20:00 | 236.16 | 229.92
2018-02-26 20:30 | 247.7 | 238.58
2018-02-26 21:00 | 245.26 | 235.67
2018-02-26 21:30 | 242.12 | 233.38
2018-02-26 22:00 | 239.44 | 230.49
2018-02-26 22:30 | 236.77 | 227.89
2018-02-26 23:00 | 234.5 | 225.61
2018-02-26 23:30 | 233.47 | 224.39
2018-02-27 | 216.78 | 207.58
2018-02-27 00:30 | 183.92 | 175.46
2018-02-27 01:00 | 174.44 | 165.47
2018-02-27 01:30 | 173.35 | 164.2
2018-02-27 02:00 | 172.69 | 163.66
2018-02-27 02:30 | 171.3 | 161.89
2018-02-27 03:00 | 171.28 | 161.68
2018-02-27 03:30 | 171.11 | 161.43
2018-02-27 04:00 | 170.56 | 161.02
2018-02-27 04:30 | 170.65 | 161.44
2018-02-27 05:00 | 171.19 | 161.76
2018-02-27 05:30 | 171.85 | 162.61
2018-02-27 06:00 | 172.67 | 163
2018-02-27 06:30 | 176.3 | 165.33
2018-02-27 07:00 | 203.56 | 193.83
2018-02-27 07:30 | 226.47 | 218.85
2018-02-27 08:00 | 232.12 | 224.67
2018-02-27 08:30 | 231.97 | 224.53
2018-02-27 09:00 | 231.74 | 224.32
2018-02-27 09:30 | 232.22 | 224.58
2018-02-27 10:00 | 233.64 | 225.98
2018-02-27 10:30 | 233.95 | 226.42
2018-02-27 11:00 | 234.75 | 227.29
2018-02-27 11:30 | 235.63 | 228
2018-02-27 12:00 | 236.2 | 228.51
2018-02-27 12:30 | 237.15 | 229.47
2018-02-27 13:00 | 238.1 | 230.54
2018-02-27 13:30 | 239.12 | 231.5
2018-02-27 14:00 | 239.28 | 231.79
2018-02-27 14:30 | 241.02 | 233.91
2018-02-27 15:00 | 240.49 | 233.25
2018-02-27 15:30 | 240.54 | 233.19
2018-02-27 16:00 | 242.31 | 235.17
2018-02-27 16:30 | 243.56 | 236.34
2018-02-27 17:00 | 244.84 | 237.61
2018-02-27 17:30 | 245.79 | 238.49
2018-02-27 18:00 | 247.58 | 240.35
2018-02-27 18:30 | 249.4 | 242.17
2018-02-27 19:00 | 250.09 | 243
2018-02-27 19:30 | 250.92 | 243.77
2018-02-27 20:00 | 249.82 | 242.54
2018-02-27 20:30 | 248.11 | 240.49
2018-02-27 21:00 | 245.22 | 237.18
2018-02-27 21:30 | 242.79 | 235.52
2018-02-27 22:00 | 240.16 | 232.97
2018-02-27 22:30 | 237.58 | 230.76
2018-02-27 23:00 | 236.01 | 228.99
2018-02-27 23:30 | 235.66 | 228.3
2018-02-28 | 234.44 | 227.49
2018-02-28 00:30 | 233.07 | 226.18
2018-02-28 01:00 | 232.25 | 225.54
2018-02-28 01:30 | 231.61 | 225.11
2018-02-28 02:00 | 231.14 | 224.75
2018-02-28 02:30 | 230.92 | 224.18
2018-02-28 03:00 | 230.12 | 223.51
2018-02-28 03:30 | 229.94 | 223.33
2018-02-28 04:00 | 229.86 | 223.27
2018-02-28 04:30 | 229.74 | 223.15
2018-02-28 05:00 | 230.59 | 224.14
2018-02-28 05:30 | 231.66 | 225.54
2018-02-28 06:00 | 233.07 | 226.86
2018-02-28 06:30 | 234.77 | 228.44
2018-02-28 07:00 | 236.32 | 229.69
2018-02-28 07:30 | 237.61 | 230.82
2018-02-28 08:00 | 238.52 | 231.9
2018-02-28 08:30 | 238.48 | 231.65
2018-02-28 09:00 | 238.2 | 231.08
2018-02-28 09:30 | 236.64 | 229.39
2018-02-28 10:00 | 236.56 | 229.35
2018-02-28 10:30 | 235.87 | 228.85
2018-02-28 11:00 | 236.83 | 228.95
2018-02-28 11:30 | 237.67 | 229.83
2018-02-28 12:00 | 239 | 231.07
2018-02-28 12:30 | 240.09 | 232.2
2018-02-28 13:00 | 241.51 | 233.8
2018-02-28 13:30 | 242.94 | 235.6
2018-02-28 14:00 | 243.46 | 236.36
2018-02-28 14:30 | 245 | 238
2018-02-28 15:00 | 245.85 | 238.86
2018-02-28 15:30 | 246.39 | 239.42
2018-02-28 16:00 | 247.86 | 240.96
2018-02-28 16:30 | 249.36 | 242.35
2018-02-28 17:00 | 250.63 | 243.56
2018-02-28 17:30 | 251.31 | 244.01
2018-02-28 18:00 | 252.52 | 245.23
2018-02-28 18:30 | 253.76 | 246.53
2018-02-28 19:00 | 255.08 | 247.96
2018-02-28 19:30 | 256.36 | 249.1
2018-02-28 20:00 | 254.61 | 246.99
2018-02-28 20:30 | 251.75 | 244.7
2018-02-28 21:00 | 248.59 | 241.36
2018-02-28 21:30 | 245.34 | 239.17
2018-02-28 22:00 | 242.17 | 235.83
2018-02-28 22:30 | 239.64 | 233.15
2018-02-28 23:00 | 237.33 | 230.5
2018-02-28 23:30 | 236.4 | 229.46
2018-03-01 | 234.64 | 227.71
2018-03-01 00:30 | 233.61 | 226.65
2018-03-01 01:00 | 232.69 | 225.85
2018-03-01 01:30 | 231.76 | 225.03
2018-03-01 02:00 | 230.63 | 224.59
2018-03-01 02:30 | 230.47 | 224.21
2018-03-01 03:00 | 229.54 | 223.58
2018-03-01 03:30 | 229.17 | 223.17
2018-03-01 04:00 | 229.1 | 223.16
2018-03-01 04:30 | 229.21 | 223.34
2018-03-01 05:00 | 229.82 | 223.94
2018-03-01 05:30 | 230.82 | 225
2018-03-01 06:00 | 231.87 | 225.95
2018-03-01 06:30 | 233.95 | 227.52
2018-03-01 07:00 | 235.53 | 228.75
2018-03-01 07:30 | 236.76 | 230.42
2018-03-01 08:00 | 237.29 | 231.02
2018-03-01 08:30 | 237.53 | 231.01
2018-03-01 09:00 | 237.48 | 230.87
2018-03-01 09:30 | 237.61 | 231.07
2018-03-01 10:00 | 237.92 | 231.69
2018-03-01 10:30 | 238.69 | 232.45
2018-03-01 11:00 | 239.92 | 233.47
2018-03-01 11:30 | 241.4 | 234.86
2018-03-01 12:00 | 244.05 | 237.69
2018-03-01 12:30 | 246.02 | 239.76
2018-03-01 13:00 | 246.6 | 240.37
2018-03-01 13:30 | 248.65 | 242.73
2018-03-01 14:00 | 239.85 | 234.34
2018-03-01 14:30 | 224.49 | 218.3
2018-03-01 15:00 | 222.26 | 216.02
2018-03-01 15:30 | 224.37 | 218.3
2018-03-01 16:00 | 226.11 | 220.12
2018-03-01 16:30 | 227.99 | 221.63
2018-03-01 17:00 | 229.1 | 222.24
2018-03-01 17:30 | 229.61 | 222.33
2018-03-01 18:00 | 231.11 | 223.81
2018-03-01 18:30 | 232.26 | 224.77
2018-03-01 19:00 | 232.5 | 225.24
2018-03-01 19:30 | 233.54 | 226.2
2018-03-01 20:00 | 231.36 | 223.75
2018-03-01 20:30 | 229.21 | 220.63
2018-03-01 21:00 | 226.12 | 217.09
2018-03-01 21:30 | 222.5 | 214.38
2018-03-01 22:00 | 218.62 | 210.89
2018-03-01 22:30 | 214.66 | 207.16
2018-03-01 23:00 | 211.84 | 204.57
2018-03-01 23:30 | 210.92 | 203.28
2018-03-02 | 208.78 | 201.05
2018-03-02 00:30 | 207.76 | 199.83
2018-03-02 01:00 | 206.41 | 198.59
2018-03-02 01:30 | 205.55 | 197.74
2018-03-02 02:00 | 204.67 | 196.86
2018-03-02 02:30 | 204.18 | 196.21
2018-03-02 03:00 | 203.38 | 195.74
2018-03-02 03:30 | 203.21 | 195.34
2018-03-02 04:00 | 203 | 195.21
2018-03-02 04:30 | 203.54 | 195.66
2018-03-02 05:00 | 204.05 | 196.14
2018-03-02 05:30 | 205.2 | 197.39
2018-03-02 06:00 | 206.69 | 198.92
2018-03-02 06:30 | 207.77 | 200.25
2018-03-02 07:00 | 209.26 | 201.31
2018-03-02 07:30 | 210.59 | 202.71
2018-03-02 08:00 | 212.04 | 203.89
2018-03-02 08:30 | 212.08 | 204.18
2018-03-02 09:00 | 209.58 | 201.8
2018-03-02 09:30 | 210.62 | 202.79
2018-03-02 10:00 | 211.5 | 203.74
2018-03-02 10:30 | 213.35 | 205.73
2018-03-02 11:00 | 215.67 | 208.23
2018-03-02 11:30 | 217.63 | 210.25
2018-03-02 12:00 | 219.27 | 211.91
2018-03-02 12:30 | 220.46 | 213.19
2018-03-02 13:00 | 221.85 | 214.4
2018-03-02 13:30 | 223.68 | 216.3
2018-03-02 14:00 | 224.25 | 217.05
2018-03-02 14:30 | 224.74 | 217.58
2018-03-02 15:00 | 224.31 | 217.36
2018-03-02 15:30 | 225.33 | 218.53
2018-03-02 16:00 | 226.75 | 220.46
2018-03-02 16:30 | 226.97 | 220.53
2018-03-02 17:00 | 227.59 | 221.08
2018-03-02 17:30 | 227.53 | 220.86
2018-03-02 18:00 | 228.17 | 221.44
2018-03-02 18:30 | 228.07 | 221.22
2018-03-02 19:00 | 228.87 | 222.06
2018-03-02 19:30 | 229.17 | 222.29
2018-03-02 20:00 | 227.42 | 220.3
2018-03-02 20:30 | 225.37 | 217.93
2018-03-02 21:00 | 222.75 | 214.77
2018-03-02 21:30 | 219.92 | 213.04
2018-03-02 22:00 | 216.86 | 210.07
2018-03-02 22:30 | 214.78 | 207.82
2018-03-02 23:00 | 212.61 | 205.3
2018-03-02 23:30 | 211.5 | 203.89
2018-03-03 | 209.86 | 201.84
2018-03-03 00:30 | 208.2 | 200.6
2018-03-03 01:00 | 207.06 | 199.49
2018-03-03 01:30 | 206.42 | 198.75
2018-03-03 02:00 | 205.85 | 198.33
2018-03-03 02:30 | 204.95 | 197.7
2018-03-03 03:00 | 204.54 | 197.28
2018-03-03 03:30 | 204.27 | 196.97
2018-03-03 04:00 | 204.3 | 197.02
2018-03-03 04:30 | 204.33 | 197
2018-03-03 05:00 | 204.7 | 196.97
2018-03-03 05:30 | 204.64 | 197.11
2018-03-03 06:00 | 204.95 | 197.52
2018-03-03 06:30 | 205.46 | 197.67
2018-03-03 07:00 | 205.45 | 197.83
2018-03-03 07:30 | 206.41 | 198.45
2018-03-03 08:00 | 207.18 | 199.58
2018-03-03 08:30 | 206.96 | 199.46
2018-03-03 09:00 | 207.78 | 200.27
2018-03-03 09:30 | 209.45 | 202.14
2018-03-03 10:00 | 211.52 | 204.34
2018-03-03 10:30 | 211.52 | 204.3
2018-03-03 11:00 | 210.64 | 203.35
2018-03-03 11:30 | 211.99 | 204.91
2018-03-03 12:00 | 213.28 | 206.1
2018-03-03 12:30 | 214.15 | 206.88
2018-03-03 13:00 | 214.93 | 207.57
2018-03-03 13:30 | 214.53 | 207.16
2018-03-03 14:00 | 214.38 | 206.85
2018-03-03 14:30 | 214.61 | 207.26
2018-03-03 15:00 | 215.94 | 208.95
2018-03-03 15:30 | 218 | 210.48
2018-03-03 16:00 | 219.06 | 211.71
2018-03-03 16:30 | 218.13 | 210.29
2018-03-03 17:00 | 217.63 | 209.71
2018-03-03 17:30 | 217.19 | 209.04
2018-03-03 18:00 | 216.94 | 208.67
2018-03-03 18:30 | 216.97 | 208.77
2018-03-03 19:00 | 217.13 | 209.15
2018-03-03 19:30 | 216.71 | 208.48
2018-03-03 20:00 | 215.56 | 207.07
2018-03-03 20:30 | 213.98 | 205.06
2018-03-03 21:00 | 212.63 | 203.59
2018-03-03 21:30 | 210.16 | 202.22
2018-03-03 22:00 | 208.6 | 200.89
2018-03-03 22:30 | 207.59 | 199.73
2018-03-03 23:00 | 205.49 | 197.79
2018-03-03 23:30 | 204.92 | 196.96
2018-03-04 | 203.82 | 195.75
2018-03-04 00:30 | 202.82 | 194.88
2018-03-04 01:00 | 201.5 | 193.98
2018-03-04 01:30 | 172.66 | 164.85
2018-03-04 02:00 | 157.45 | 149.07
2018-03-04 02:30 | 157.15 | 148.67
2018-03-04 03:00 | 156.64 | 148.2
2018-03-04 03:30 | 155.95 | 147.62
2018-03-04 04:00 | 155.58 | 147.15
2018-03-04 04:30 | 155.33 | 146.98
2018-03-04 05:00 | 155.65 | 147.31
2018-03-04 05:30 | 156.01 | 147.72
2018-03-04 06:00 | 155.69 | 147.6
2018-03-04 06:30 | 155.9 | 148.05
2018-03-04 07:00 | 156.46 | 148.76
2018-03-04 07:30 | 157.29 | 149.78
2018-03-04 08:00 | 158.07 | 150.21
2018-03-04 08:30 | 158.36 | 150.55
2018-03-04 09:00 | 158.58 | 150.97
2018-03-04 09:30 | 160.01 | 151.43
2018-03-04 10:00 | 159.82 | 150.84
2018-03-04 10:30 | 191.35 | 182.3
2018-03-04 11:00 | 203.92 | 194.97
2018-03-04 11:30 | 204.59 | 195.66
2018-03-04 12:00 | 204.7 | 195.62
2018-03-04 12:30 | 205.96 | 196.79
2018-03-04 13:00 | 207.46 | 198.47
2018-03-04 13:30 | 208.81 | 199.67
2018-03-04 14:00 | 209.37 | 200.13
2018-03-04 14:30 | 209.27 | 200.22
2018-03-04 15:00 | 209.99 | 201.15
2018-03-04 15:30 | 209.08 | 205.56
2018-03-04 16:00 | 211.39 | 208.49
2018-03-04 16:30 | 213.44 | 210.55
2018-03-04 17:00 | 213.48 | 210.62
2018-03-04 17:30 | 212.24 | 209.43
2018-03-04 18:00 | 210.78 | 207.98
2018-03-04 18:30 | 211.25 | 208.38
2018-03-04 19:00 | 211.21 | 208.38
2018-03-04 19:30 | 211.06 | 208.13
2018-03-04 20:00 | 211.84 | 208.78
2018-03-04 20:30 | 212.14 | 208.91
2018-03-04 21:00 | 206.46 | 198.26
2018-03-04 21:30 | 206.42 | 197.86
2018-03-04 22:00 | 205.1 | 196.56
2018-03-04 22:30 | 202.57 | 193.87
2018-03-04 23:00 | 201.66 | 192.86
2018-03-04 23:30 | 200.74 | 192.24
2018-03-05 | 199.56 | 191.12
2018-03-05 00:30 | 198.74 | 190.43
2018-03-05 01:00 | 197.26 | 189.68
2018-03-05 01:30 | 196.63 | 188.97
2018-03-05 02:00 | 196.01 | 188.58
2018-03-05 02:30 | 195.69 | 188.37
2018-03-05 03:00 | 195.99 | 188.78
2018-03-05 03:30 | 196.59 | 189.28
2018-03-05 04:00 | 196.38 | 188.93
2018-03-05 04:30 | 197.31 | 189.91
2018-03-05 05:00 | 197.87 | 190.67
2018-03-05 05:30 | 199.12 | 191.71
2018-03-05 06:00 | 200.71 | 193.02
2018-03-05 06:30 | 202.68 | 194.8
2018-03-05 07:00 | 204.01 | 196.37
2018-03-05 07:30 | 206.34 | 198.23
2018-03-05 08:00 | 208.23 | 199.72
2018-03-05 08:30 | 207.35 | 198.94
2018-03-05 09:00 | 207.54 | 199.25
2018-03-05 09:30 | 207.32 | 199.11
2018-03-05 10:00 | 207.87 | 199.93
2018-03-05 10:30 | 207.82 | 199.86
2018-03-05 11:00 | 208.26 | 200.25
2018-03-05 11:30 | 207.56 | 199.42
2018-03-05 12:00 | 208.33 | 200.34
2018-03-05 12:30 | 208.19 | 200.08
2018-03-05 13:00 | 208.86 | 200.84
2018-03-05 13:30 | 210.23 | 202.41
2018-03-05 14:00 | 212.14 | 204.62
2018-03-05 14:30 | 211.54 | 204.05
2018-03-05 15:00 | 210.84 | 202.91
2018-03-05 15:30 | 211.22 | 202.44
2018-03-05 16:00 | 212.11 | 203.43
2018-03-05 16:30 | 212.17 | 203.32
2018-03-05 17:00 | 212.69 | 203.75
2018-03-05 17:30 | 213.01 | 203.83
2018-03-05 18:00 | 213.39 | 204.13
2018-03-05 18:30 | 215.07 | 205.94
2018-03-05 19:00 | 188.77 | 179.48
2018-03-05 19:30 | 172.65 | 162.77
2018-03-05 20:00 | 171.29 | 161.16
2018-03-05 20:30 | 170.01 | 159.42
2018-03-05 21:00 | 167.86 | 157.52
2018-03-05 21:30 | 164.63 | 156.39
2018-03-05 22:00 | 162.95 | 154.58
2018-03-05 22:30 | 161.01 | 152.54
2018-03-05 23:00 | 159.29 | 150.68
2018-03-05 23:30 | 158.71 | 149.98
2018-03-06 | 157.65 | 148.84
2018-03-06 00:30 | 156.32 | 147.88
2018-03-06 01:00 | 155.5 | 147.19
2018-03-06 01:30 | 154.61 | 146.56
2018-03-06 02:00 | 154.75 | 146.38
2018-03-06 02:30 | 154.76 | 146.1
2018-03-06 03:00 | 154.5 | 145.81
2018-03-06 03:30 | 154.25 | 145.52
2018-03-06 04:00 | 154.09 | 145.37
2018-03-06 04:30 | 154.21 | 145.94
2018-03-06 05:00 | 154.65 | 146.64
2018-03-06 05:30 | 155.81 | 148.05
2018-03-06 06:00 | 158.16 | 149.87
2018-03-06 06:30 | 160.34 | 152.09
2018-03-06 07:00 | 162.33 | 153.7
2018-03-06 07:30 | 163.77 | 155.17
2018-03-06 08:00 | 167 | 158.19
2018-03-06 08:30 | 165.37 | 156.76
2018-03-06 09:00 | 166.03 | 157.38
2018-03-06 09:30 | 166.28 | 157.57
2018-03-06 10:00 | 165.75 | 157.1
2018-03-06 10:30 | 165.39 | 156.78
2018-03-06 11:00 | 165.58 | 157.16
2018-03-06 11:30 | 165.82 | 157.1
2018-03-06 12:00 | 166.01 | 157.21
2018-03-06 12:30 | 196.95 | 188.37
2018-03-06 13:00 | 211.27 | 202.66
2018-03-06 13:30 | 211.02 | 202.48
2018-03-06 14:00 | 210.42 | 201.87
2018-03-06 14:30 | 209.7 | 201.33
2018-03-06 15:00 | 210.57 | 202.21
2018-03-06 15:30 | 210.57 | 202.19
2018-03-06 16:00 | 211.47 | 203.08
2018-03-06 16:30 | 211.14 | 202.71
2018-03-06 17:00 | 210.8 | 202.27
2018-03-06 17:30 | 211.37 | 202.7
2018-03-06 18:00 | 213.11 | 204.38
2018-03-06 18:30 | 213.98 | 205.3
2018-03-06 19:00 | 215.02 | 206.65
2018-03-06 19:30 | 214.79 | 205.8
2018-03-06 20:00 | 213.04 | 203.96
2018-03-06 20:30 | 212.37 | 203.01
2018-03-06 21:00 | 210.25 | 201.63
2018-03-06 21:30 | 208.96 | 201.03
2018-03-06 22:00 | 207.42 | 199.51
2018-03-06 22:30 | 206.02 | 198.06
2018-03-06 23:00 | 204.14 | 196.09
2018-03-06 23:30 | 203.57 | 195.68
2018-03-07 | 202.73 | 195.02
2018-03-07 00:30 | 171.49 | 163.65
2018-03-07 01:00 | 152.39 | 144.3
2018-03-07 01:30 | 151.59 | 143.78
2018-03-07 02:00 | 151.4 | 143.64
2018-03-07 02:30 | 151.11 | 143.26
2018-03-07 03:00 | 150.82 | 142.78
2018-03-07 03:30 | 150.18 | 142.22
2018-03-07 04:00 | 149.67 | 141.56
2018-03-07 04:30 | 149.9 | 142.09
2018-03-07 05:00 | 150.67 | 143.01
2018-03-07 05:30 | 151.38 | 143.75
2018-03-07 06:00 | 152.42 | 144.75
2018-03-07 06:30 | 186.41 | 179.8
2018-03-07 07:00 | 204.6 | 197.57
2018-03-07 07:30 | 205.93 | 199.06
2018-03-07 08:00 | 207.36 | 199.69
2018-03-07 08:30 | 207.28 | 199.07
2018-03-07 09:00 | 205.73 | 197.51
2018-03-07 09:30 | 205.66 | 197.44
2018-03-07 10:00 | 206.51 | 198.5
2018-03-07 10:30 | 205.92 | 197.97
2018-03-07 11:00 | 205.13 | 197.41
2018-03-07 11:30 | 205.58 | 197.57
2018-03-07 12:00 | 205.85 | 197.81
2018-03-07 12:30 | 205.71 | 197.71
2018-03-07 13:00 | 206.25 | 198.48
2018-03-07 13:30 | 206 | 198.11
2018-03-07 14:00 | 205.35 | 197.58
2018-03-07 14:30 | 206.78 | 198.73
2018-03-07 15:00 | 206.71 | 198.57
2018-03-07 15:30 | 206.86 | 198.65
2018-03-07 16:00 | 207.34 | 198.88
2018-03-07 16:30 | 208.22 | 199.66
2018-03-07 17:00 | 208.83 | 200.33
2018-03-07 17:30 | 209.3 | 200.72
2018-03-07 18:00 | 210.93 | 202.33
2018-03-07 18:30 | 210.74 | 201.82
2018-03-07 19:00 | 211.11 | 202.24
2018-03-07 19:30 | 211.11 | 202.1
2018-03-07 20:00 | 209.6 | 200.45
2018-03-07 20:30 | 209.04 | 199.58
2018-03-07 21:00 | 208.09 | 198.55
2018-03-07 21:30 | 206.29 | 197.98
2018-03-07 22:00 | 204.56 | 196.18
2018-03-07 22:30 | 203.84 | 195.24
2018-03-07 23:00 | 201.81 | 192.98
2018-03-07 23:30 | 170.15 | 160.56
2018-03-08 | 151.76 | 143
2018-03-08 00:30 | 150.87 | 142.47
2018-03-08 01:00 | 149.4 | 141.6
2018-03-08 01:30 | 148.65 | 141.16
2018-03-08 02:00 | 148.16 | 140.76
2018-03-08 02:30 | 148.33 | 140.68
2018-03-08 03:00 | 148.08 | 140.15
2018-03-08 03:30 | 148 | 140.27
2018-03-08 04:00 | 148.23 | 140.46
2018-03-08 04:30 | 149.07 | 141.02
2018-03-08 05:00 | 145.6 | 138.22
2018-03-08 05:30 | 139.63 | 131.87
2018-03-08 06:00 | 140.98 | 132.58
2018-03-08 06:30 | 137.17 | 128.22
2018-03-08 07:00 | 131.43 | 122.17
2018-03-08 07:30 | 125.83 | 118.65
2018-03-08 08:00 | 128.49 | 121.66
2018-03-08 08:30 | 127.4 | 120.56
2018-03-08 09:00 | 128.67 | 121.84
2018-03-08 09:30 | 130.88 | 125.2
2018-03-08 10:00 | 130.68 | 125.64
2018-03-08 10:30 | 130.39 | 125.44
2018-03-08 11:00 | 130.65 | 125.54
2018-03-08 11:30 | 130.58 | 125.45
2018-03-08 12:00 | 130.86 | 126
2018-03-08 12:30 | 130.65 | 125.47
2018-03-08 13:00 | 131.2 | 126.01
2018-03-08 13:30 | 131.04 | 126.13
2018-03-08 14:00 | 131.14 | 126.42
2018-03-08 14:30 | 131.31 | 126.72
2018-03-08 15:00 | 131.15 | 126.5
2018-03-08 15:30 | 131.95 | 127.13
2018-03-08 16:00 | 133.36 | 128.45
2018-03-08 16:30 | 133.38 | 128.38
2018-03-08 17:00 | 134.17 | 128.97
2018-03-08 17:30 | 134.25 | 128.97
2018-03-08 18:00 | 135.36 | 130.26
2018-03-08 18:30 | 137.17 | 132.01
2018-03-08 19:00 | 138.8 | 133.82
2018-03-08 19:30 | 139.23 | 134.21
2018-03-08 20:00 | 139.22 | 133.89
2018-03-08 20:30 | 138.17 | 132.6
2018-03-08 21:00 | 136.42 | 130.75
2018-03-08 21:30 | 135.04 | 130.36
2018-03-08 22:00 | 133.24 | 128.8
2018-03-08 22:30 | 133.04 | 126.78
2018-03-08 23:00 | 132 | 124.93
2018-03-08 23:30 | 131.02 | 124.37
2018-03-09 | 129.65 | 123.21
2018-03-09 00:30 | 128.77 | 122.46
2018-03-09 01:00 | 127.35 | 121.71
2018-03-09 01:30 | 126.86 | 121.26
2018-03-09 02:00 | 126.74 | 120.98
2018-03-09 02:30 | 126.23 | 120.44
2018-03-09 03:00 | 126.17 | 120.36
2018-03-09 03:30 | 126.27 | 120.4
2018-03-09 04:00 | 126.31 | 120.83
2018-03-09 04:30 | 126.58 | 121.09
2018-03-09 05:00 | 127.79 | 121.74
2018-03-09 05:30 | 128.99 | 123.03
2018-03-09 06:00 | 130.6 | 124.89
2018-03-09 06:30 | 133.07 | 126.59
2018-03-09 07:00 | 135.37 | 128.15
2018-03-09 07:30 | 136.75 | 129.6
2018-03-09 08:00 | 167.96 | 161.13
2018-03-09 08:30 | 181.99 | 175.39
2018-03-09 09:00 | 181.83 | 175.58
2018-03-09 09:30 | 181.03 | 174.92
2018-03-09 10:00 | 183.25 | 177.05
2018-03-09 10:30 | 184.97 | 178.35
2018-03-09 11:00 | 184.16 | 177.9
2018-03-09 11:30 | 173.69 | 167.62
2018-03-09 12:00 | 145.8 | 140.07
2018-03-09 12:30 | 154.32 | 149.29
2018-03-09 13:00 | 142.08 | 135.38
2018-03-09 13:30 | 143.21 | 136.33
2018-03-09 14:00 | 144.21 | 137.65
2018-03-09 14:30 | 143.99 | 137.76
2018-03-09 15:00 | 144.63 | 138.39
2018-03-09 15:30 | 144.88 | 138.24
2018-03-09 16:00 | 145.7 | 138.5
2018-03-09 16:30 | 146.04 | 138.78
2018-03-09 17:00 | 147.25 | 139.96
2018-03-09 17:30 | 148.13 | 140.44
2018-03-09 18:00 | 149.46 | 141.38
2018-03-09 18:30 | 173.77 | 165.79
2018-03-09 19:00 | 175.83 | 168.12
2018-03-09 19:30 | 176.71 | 168.82
2018-03-09 20:00 | 178.31 | 170.73
2018-03-09 20:30 | 178.19 | 170.93
2018-03-09 21:00 | 176.38 | 169.07
2018-03-09 21:30 | 156.05 | 149.53
2018-03-09 22:00 | 139.56 | 133.01
2018-03-09 22:30 | 137.62 | 131.04
2018-03-09 23:00 | 136.2 | 129.33
2018-03-09 23:30 | 135.74 | 128.83
2018-03-10 | 141.87 | 135.07
2018-03-10 00:30 | 153.04 | 146.72
2018-03-10 01:00 | 148.69 | 142.77
2018-03-10 01:30 | 147.3 | 141.33
2018-03-10 02:00 | 146.15 | 140.79
2018-03-10 02:30 | 145.23 | 140.24
2018-03-10 03:00 | 144.4 | 139.34
2018-03-10 03:30 | 144.42 | 139.66
2018-03-10 04:00 | 143.98 | 139.16
2018-03-10 04:30 | 143.89 | 139.07
2018-03-10 05:00 | 144.19 | 139.38
2018-03-10 05:30 | 132.21 | 127.32
2018-03-10 06:00 | 132.68 | 126.87
2018-03-10 06:30 | 135.41 | 127.88
2018-03-10 07:00 | 136.52 | 128.58
2018-03-10 07:30 | 137.08 | 128.86
2018-03-10 08:00 | 140.82 | 131.99
2018-03-10 08:30 | 142.27 | 131.83
2018-03-10 09:00 | 142.07 | 131.74
2018-03-10 09:30 | 141.65 | 131.22
2018-03-10 10:00 | 141.06 | 130.44
2018-03-10 10:30 | 140.51 | 129.46
2018-03-10 11:00 | 140.43 | 129.69
2018-03-10 11:30 | 139.47 | 129.05
2018-03-10 12:00 | 140.23 | 129.63
2018-03-10 12:30 | 141.42 | 130.79
2018-03-10 13:00 | 144.48 | 133.88
2018-03-10 13:30 | 142.93 | 132.01
2018-03-10 14:00 | 142.15 | 130.98
2018-03-10 14:30 | 143.13 | 132.17
2018-03-10 15:00 | 145.03 | 133.74
2018-03-10 15:30 | 147 | 135.46
2018-03-10 16:00 | 147.82 | 136.47
2018-03-10 16:30 | 145.82 | 134.35
2018-03-10 17:00 | 145.27 | 133.83
2018-03-10 17:30 | 146.65 | 135.55
2018-03-10 18:00 | 155.61 | 145.03
2018-03-10 18:30 | 162.91 | 152.75
2018-03-10 19:00 | 164.17 | 154.26
2018-03-10 19:30 | 164.74 | 154.75
2018-03-10 20:00 | 164.18 | 153.81
2018-03-10 20:30 | 163.71 | 153.08
2018-03-10 21:00 | 162.2 | 152.12
2018-03-10 21:30 | 160.31 | 150.78
2018-03-10 22:00 | 158.44 | 149.03
2018-03-10 22:30 | 157.15 | 147.59
2018-03-10 23:00 | 156.21 | 146.42
2018-03-10 23:30 | 154.93 | 145.63
2018-03-11 | 154.25 | 144.98
2018-03-11 00:30 | 154.59 | 145.19
2018-03-11 01:00 | 152.42 | 144.21
2018-03-11 01:30 | 152.57 | 143.78
2018-03-11 02:00 | 152.16 | 143.66
2018-03-11 02:30 | 150.49 | 142.68
2018-03-11 03:00 | 151.15 | 143.29
2018-03-11 03:30 | 151.05 | 143.1
2018-03-11 04:00 | 150.8 | 142.8
2018-03-11 04:30 | 150.41 | 142.35
2018-03-11 05:00 | 150.81 | 142.79
2018-03-11 05:30 | 151.28 | 143.39
2018-03-11 06:00 | 151.54 | 143.69
2018-03-11 06:30 | 152.11 | 144.36
2018-03-11 07:00 | 152.39 | 144.56
2018-03-11 07:30 | 152.78 | 145.34
2018-03-11 08:00 | 152.35 | 145.23
2018-03-11 08:30 | 151.86 | 145.08
2018-03-11 09:00 | 152.21 | 144.37
2018-03-11 09:30 | 152.34 | 144.21
2018-03-11 10:00 | 152.58 | 144.21
2018-03-11 10:30 | 152.04 | 143.57
2018-03-11 11:00 | 152.4 | 144.37
2018-03-11 11:30 | 152.85 | 144.73
2018-03-11 12:00 | 155 | 147.34
2018-03-11 12:30 | 155.88 | 148.4
2018-03-11 13:00 | 155.99 | 148.42
2018-03-11 13:30 | 155.82 | 148
2018-03-11 14:00 | 154.4 | 146.14
2018-03-11 14:30 | 154.54 | 146.3
2018-03-11 15:00 | 156 | 147.93
2018-03-11 15:30 | 167.52 | 159.72
2018-03-11 16:00 | 172.46 | 164.33
2018-03-11 16:30 | 167.04 | 159.02
2018-03-11 17:00 | 169.05 | 161.02
2018-03-11 17:30 | 174.81 | 166.05
2018-03-11 18:00 | 177.33 | 167.97
2018-03-11 18:30 | 178.35 | 169.14
2018-03-11 19:00 | 178.26 | 169.4
2018-03-11 19:30 | 178.64 | 169.46
2018-03-11 20:00 | 177.95 | 168.51
2018-03-11 20:30 | 175.74 | 165.87
2018-03-11 21:00 | 174.73 | 164.69
2018-03-11 21:30 | 174.01 | 164.04
2018-03-11 22:00 | 172.11 | 161.9
2018-03-11 22:30 | 171.71 | 161.1
2018-03-11 23:00 | 169.41 | 158.86
2018-03-11 23:30 | 168.82 | 158.76
2018-03-12 | 167.69 | 157.97
2018-03-12 00:30 | 167.04 | 157.83
2018-03-12 01:00 | 166.53 | 157.53
2018-03-12 01:30 | 165.79 | 156.91
2018-03-12 02:00 | 165.9 | 156.76
2018-03-12 02:30 | 165.8 | 156.77
2018-03-12 03:00 | 166.41 | 157.3
2018-03-12 03:30 | 166.47 | 157.42
2018-03-12 04:00 | 167.11 | 157.89
2018-03-12 04:30 | 167.98 | 158.81
2018-03-12 05:00 | 168.28 | 159.33
2018-03-12 05:30 | 169.17 | 160.81
2018-03-12 06:00 | 170.79 | 162.17
2018-03-12 06:30 | 173.85 | 164.73
2018-03-12 07:00 | 177.61 | 166.58
2018-03-12 07:30 | 178.39 | 167.5
2018-03-12 08:00 | 178.34 | 167.87
2018-03-12 08:30 | 176.68 | 166.56
2018-03-12 09:00 | 176.61 | 166.2
2018-03-12 09:30 | 175.01 | 164.6
2018-03-12 10:00 | 174.95 | 164.62
2018-03-12 10:30 | 175.25 | 164.92
2018-03-12 11:00 | 176.08 | 165.9
2018-03-12 11:30 | 175.79 | 165.55
2018-03-12 12:00 | 176.28 | 166.24
2018-03-12 12:30 | 177.5 | 167.45
2018-03-12 13:00 | 178.8 | 168.94
2018-03-12 13:30 | 179.13 | 169.06
2018-03-12 14:00 | 179.62 | 170.02
2018-03-12 14:30 | 181.09 | 171.45
2018-03-12 15:00 | 181.44 | 171.64
2018-03-12 15:30 | 181.77 | 171.61
2018-03-12 16:00 | 182.62 | 172.25
2018-03-12 16:30 | 183.56 | 173.12
2018-03-12 17:00 | 183.68 | 173.34
2018-03-12 17:30 | 184.76 | 174.3
2018-03-12 18:00 | 186.81 | 176.3
2018-03-12 18:30 | 187.63 | 177.14
2018-03-12 19:00 | 188.17 | 177.96
2018-03-12 19:30 | 188.05 | 177.79
2018-03-12 20:00 | 185.88 | 175.21
2018-03-12 20:30 | 184.64 | 173.72
2018-03-12 21:00 | 182.19 | 170.83
2018-03-12 21:30 | 180.24 | 169.64
2018-03-12 22:00 | 178.29 | 168.11
2018-03-12 22:30 | 176.83 | 165.83
2018-03-12 23:00 | 175.26 | 163.88
2018-03-12 23:30 | 173.86 | 162.35
2018-03-13 | 172.78 | 161.54
2018-03-13 00:30 | 170.77 | 160.62
2018-03-13 01:00 | 168.99 | 159.33
2018-03-13 01:30 | 168.88 | 159.44
2018-03-13 02:00 | 168.64 | 158.94
2018-03-13 02:30 | 167.59 | 158.76
2018-03-13 03:00 | 166.72 | 158.09
2018-03-13 03:30 | 167.06 | 158.48
2018-03-13 04:00 | 166.72 | 158.14
2018-03-13 04:30 | 167.38 | 158.95
2018-03-13 05:00 | 168.32 | 159.84
2018-03-13 05:30 | 169.19 | 161.04
2018-03-13 06:00 | 172.27 | 164.13
2018-03-13 06:30 | 175.63 | 167.03
2018-03-13 07:00 | 177.88 | 167.9
2018-03-13 07:30 | 179.33 | 169.37
2018-03-13 08:00 | 179.12 | 169.1
2018-03-13 08:30 | 178.78 | 168.78
2018-03-13 09:00 | 179.23 | 169.53
2018-03-13 09:30 | 178.6 | 170.08
2018-03-13 10:00 | 174.45 | 166.02
2018-03-13 10:30 | 173.48 | 165.5
2018-03-13 11:00 | 174.97 | 167.25
2018-03-13 11:30 | 178.39 | 171.04
2018-03-13 12:00 | 178.66 | 171.19
2018-03-13 12:30 | 179.96 | 172.64
2018-03-13 13:00 | 179.46 | 171.88
2018-03-13 13:30 | 180.56 | 173.39
2018-03-13 14:00 | 181.44 | 174.02
2018-03-13 14:30 | 182.47 | 175.17
2018-03-13 15:00 | 183.76 | 176.26
2018-03-13 15:30 | 184.21 | 176.74
2018-03-13 16:00 | 184.86 | 177.53
2018-03-13 16:30 | 185.93 | 178.54
2018-03-13 17:00 | 186.52 | 179.1
2018-03-13 17:30 | 187.16 | 179.85
2018-03-13 18:00 | 186.36 | 178.95
2018-03-13 18:30 | 187.17 | 179.56
2018-03-13 19:00 | 188.78 | 181.4
2018-03-13 19:30 | 188.85 | 181.22
2018-03-13 20:00 | 186.45 | 178.44
2018-03-13 20:30 | 185.18 | 176.76
2018-03-13 21:00 | 182.32 | 173.59
2018-03-13 21:30 | 180.13 | 172.38
2018-03-13 22:00 | 178.15 | 170.48
2018-03-13 22:30 | 176.18 | 168.76
2018-03-13 23:00 | 172.95 | 165.37
2018-03-13 23:30 | 171.79 | 164.82
2018-03-14 | 170.28 | 163.66
2018-03-14 00:30 | 169.42 | 162.95
2018-03-14 01:00 | 168.02 | 161.53
2018-03-14 01:30 | 167.92 | 160.68
2018-03-14 02:00 | 168.3 | 160.65
2018-03-14 02:30 | 167.56 | 159.54
2018-03-14 03:00 | 168.17 | 159.95
2018-03-14 03:30 | 168.27 | 160.1
2018-03-14 04:00 | 167.76 | 159.54
2018-03-14 04:30 | 168.06 | 160.02
2018-03-14 05:00 | 168.58 | 160.46
2018-03-14 05:30 | 169.9 | 161.99
2018-03-14 06:00 | 171.92 | 163.47
2018-03-14 06:30 | 174.83 | 165.67
2018-03-14 07:00 | 176.1 | 166.42
2018-03-14 07:30 | 177.37 | 167.88
2018-03-14 08:00 | 179.71 | 168.77
2018-03-14 08:30 | 178.6 | 167.69
2018-03-14 09:00 | 177.55 | 166.56
2018-03-14 09:30 | 176.12 | 165.25
2018-03-14 10:00 | 176.56 | 165.72
2018-03-14 10:30 | 175.76 | 164.95
2018-03-14 11:00 | 177.26 | 166.35
2018-03-14 11:30 | 178.09 | 166.47
2018-03-14 12:00 | 206.92 | 196.44
2018-03-14 12:30 | 223.3 | 213.03
2018-03-14 13:00 | 227.01 | 216.74
2018-03-14 13:30 | 228.73 | 218.77
2018-03-14 14:00 | 232.38 | 222.79
2018-03-14 14:30 | 233.99 | 224.48
2018-03-14 15:00 | 241.24 | 231.64
2018-03-14 15:30 | 242.39 | 232.99
2018-03-14 16:00 | 243.03 | 233.82
2018-03-14 16:30 | 243.95 | 234.14
2018-03-14 17:00 | 245.28 | 235.17
2018-03-14 17:30 | 245.48 | 236.32
2018-03-14 18:00 | 245.78 | 237.67
2018-03-14 18:30 | 247.37 | 239.37
2018-03-14 19:00 | 249.13 | 241.47
2018-03-14 19:30 | 249.2 | 241.47
2018-03-14 20:00 | 247.24 | 239.03
2018-03-14 20:30 | 245.54 | 237
2018-03-14 21:00 | 243.45 | 234.79
2018-03-14 21:30 | 240.56 | 233.1
2018-03-14 22:00 | 237.89 | 230.74
2018-03-14 22:30 | 235.9 | 228.51
2018-03-14 23:00 | 214.31 | 206.84
2018-03-14 23:30 | 178.62 | 170.92
2018-03-15 | 169.91 | 162.08
2018-03-15 00:30 | 169.05 | 161.78
2018-03-15 01:00 | 166.27 | 160
2018-03-15 01:30 | 166.37 | 159.92
2018-03-15 02:00 | 165.48 | 159.02
2018-03-15 02:30 | 165.5 | 159.22
2018-03-15 03:00 | 164.81 | 158.53
2018-03-15 03:30 | 164.99 | 158.69
2018-03-15 04:00 | 165.1 | 158.92
2018-03-15 04:30 | 165.29 | 159.04
2018-03-15 05:00 | 166.12 | 159.98
2018-03-15 05:30 | 167.05 | 161
2018-03-15 06:00 | 169 | 162.33
2018-03-15 06:30 | 171.44 | 164.5
2018-03-15 07:00 | 172.3 | 164.79
2018-03-15 07:30 | 173.82 | 166.43
2018-03-15 08:00 | 174.28 | 167.01
2018-03-15 08:30 | 173.21 | 166.23
2018-03-15 09:00 | 171.89 | 164.6
2018-03-15 09:30 | 171.62 | 164.01
2018-03-15 10:00 | 170.75 | 163.65
2018-03-15 10:30 | 170.08 | 163.36
2018-03-15 11:00 | 174.85 | 168.74
2018-03-15 11:30 | 180.85 | 175.16
2018-03-15 12:00 | 181.5 | 176.05
2018-03-15 12:30 | 181.05 | 175.34
2018-03-15 13:00 | 179.58 | 173.75
2018-03-15 13:30 | 208.29 | 203.07
2018-03-15 14:00 | 228.46 | 223.5
2018-03-15 14:30 | 229.72 | 224.78
2018-03-15 15:00 | 230.42 | 224.32
2018-03-15 15:30 | 232.38 | 225.4
2018-03-15 16:00 | 234.05 | 226.59
2018-03-15 16:30 | 233.52 | 225.61
2018-03-15 17:00 | 235.18 | 227.31
2018-03-15 17:30 | 235.61 | 227.45
2018-03-15 18:00 | 236.62 | 228.24
2018-03-15 18:30 | 237.27 | 229.18
2018-03-15 19:00 | 238.35 | 230.66
2018-03-15 19:30 | 238.45 | 230.47
2018-03-15 20:00 | 236.62 | 228.2
2018-03-15 20:30 | 234.41 | 225.58
2018-03-15 21:00 | 231.59 | 222.69
2018-03-15 21:30 | 229.4 | 221.17
2018-03-15 22:00 | 226.46 | 218.62
2018-03-15 22:30 | 224 | 215.96
2018-03-15 23:00 | 221.49 | 213.28
2018-03-15 23:30 | 209.42 | 201.58
2018-03-16 | 176.41 | 168.45
2018-03-16 00:30 | 168.26 | 160.37
2018-03-16 01:00 | 166.66 | 159.42
2018-03-16 01:30 | 166.36 | 159.05
2018-03-16 02:00 | 165.91 | 158.75
2018-03-16 02:30 | 165.23 | 157.98
2018-03-16 03:00 | 163.92 | 157.36
2018-03-16 03:30 | 163.97 | 157.66
2018-03-16 04:00 | 163.49 | 157.1
2018-03-16 04:30 | 164.11 | 157.75
2018-03-16 05:00 | 164.73 | 157.97
2018-03-16 05:30 | 166.1 | 159.5
2018-03-16 06:00 | 167.68 | 161.19
2018-03-16 06:30 | 169.61 | 162.98
2018-03-16 07:00 | 170.59 | 163.74
2018-03-16 07:30 | 170.92 | 164.39
2018-03-16 08:00 | 170.87 | 164.52
2018-03-16 08:30 | 170.33 | 164.27
2018-03-16 09:00 | 171.39 | 165.23
2018-03-16 09:30 | 170.44 | 164.71
2018-03-16 10:00 | 170.89 | 165.66
2018-03-16 10:30 | 172.77 | 167.23
2018-03-16 11:00 | 173.96 | 168.31
2018-03-16 11:30 | 175.16 | 169.28
2018-03-16 12:00 | 176.71 | 170.67
2018-03-16 12:30 | 177.26 | 171.17
2018-03-16 13:00 | 178.23 | 172.41
2018-03-16 13:30 | 206.77 | 201.03
2018-03-16 14:00 | 225.84 | 219.69
2018-03-16 14:30 | 229.5 | 223.4
2018-03-16 15:00 | 229.34 | 223.47
2018-03-16 15:30 | 230.85 | 225.05
2018-03-16 16:00 | 239.56 | 233.71
2018-03-16 16:30 | 241.96 | 236.12
2018-03-16 17:00 | 243.54 | 237.57
2018-03-16 17:30 | 243.84 | 237.74
2018-03-16 18:00 | 244.61 | 238.53
2018-03-16 18:30 | 245.03 | 238.96
2018-03-16 19:00 | 245.59 | 239.64
2018-03-16 19:30 | 245.32 | 239.3
2018-03-16 20:00 | 243.01 | 236.8
2018-03-16 20:30 | 241.18 | 234.87
2018-03-16 21:00 | 238.92 | 232.36
2018-03-16 21:30 | 237.46 | 231.42
2018-03-16 22:00 | 235.74 | 229.77
2018-03-16 22:30 | 234.21 | 227.86
2018-03-16 23:00 | 231.66 | 225.54
2018-03-16 23:30 | 230.39 | 224.19
2018-03-17 | 229.43 | 222.89
2018-03-17 00:30 | 228.16 | 221.74
2018-03-17 01:00 | 226.99 | 220.93
2018-03-17 01:30 | 226.62 | 220.66
2018-03-17 02:00 | 206.81 | 200.68
2018-03-17 02:30 | 170.83 | 164.63
2018-03-17 03:00 | 163.85 | 157.64
2018-03-17 03:30 | 163.94 | 157.83
2018-03-17 04:00 | 163.27 | 157.21
2018-03-17 04:30 | 163.54 | 157.5
2018-03-17 05:00 | 162.37 | 156.45
2018-03-17 05:30 | 164.02 | 158.34
2018-03-17 06:00 | 163.93 | 158.13
2018-03-17 06:30 | 165 | 159.08
2018-03-17 07:00 | 164.05 | 158.05
2018-03-17 07:30 | 165.52 | 159.98
2018-03-17 08:00 | 165.56 | 159.77
2018-03-17 08:30 | 166.03 | 159.81
2018-03-17 09:00 | 166.83 | 159.92
2018-03-17 09:30 | 166.77 | 159.98
2018-03-17 10:00 | 166.99 | 160.2
2018-03-17 10:30 | 167.85 | 160.87
2018-03-17 11:00 | 168.89 | 161.87
2018-03-17 11:30 | 169.64 | 162.57
2018-03-17 12:00 | 171.29 | 164.22
2018-03-17 12:30 | 172.48 | 165.42
2018-03-17 13:00 | 172.94 | 166.19
2018-03-17 13:30 | 172.8 | 166.55
2018-03-17 14:00 | 174.47 | 167.97
2018-03-17 14:30 | 175.46 | 169.23
2018-03-17 15:00 | 176.56 | 170.26
2018-03-17 15:30 | 186.04 | 179.54
2018-03-17 16:00 | 194.51 | 187.9
2018-03-17 16:30 | 197.68 | 190.89
2018-03-17 17:00 | 199.05 | 192.34
2018-03-17 17:30 | 200.51 | 193.88
2018-03-17 18:00 | 201.81 | 195.06
2018-03-17 18:30 | 201.22 | 194.55
2018-03-17 19:00 | 201.75 | 195.28
2018-03-17 19:30 | 201.17 | 194.51
2018-03-17 20:00 | 198.89 | 191.99
2018-03-17 20:30 | 191.58 | 184.36
2018-03-17 21:00 | 180.02 | 172.84
2018-03-17 21:30 | 176.69 | 170.05
2018-03-17 22:00 | 174.63 | 168.06
2018-03-17 22:30 | 172.87 | 166.26
2018-03-17 23:00 | 171.21 | 164.4
2018-03-17 23:30 | 169.85 | 162.83
2018-03-18 | 168.65 | 161.88
2018-03-18 00:30 | 168.48 | 161.48
2018-03-18 01:00 | 166.86 | 160.17
2018-03-18 01:30 | 165.76 | 159.65
2018-03-18 02:00 | 165.63 | 159.42
2018-03-18 02:30 | 164.68 | 158.78
2018-03-18 03:00 | 164.3 | 158.39
2018-03-18 03:30 | 163.79 | 157.91
2018-03-18 04:00 | 163.36 | 157.5
2018-03-18 04:30 | 162.84 | 157.08
2018-03-18 05:00 | 163.04 | 157.31
2018-03-18 05:30 | 163.17 | 157.33
2018-03-18 06:00 | 163.19 | 157.43
2018-03-18 06:30 | 163.7 | 158.18
2018-03-18 07:00 | 163.95 | 158.49
2018-03-18 07:30 | 164.24 | 158.56
2018-03-18 08:00 | 165.14 | 159.44
2018-03-18 08:30 | 165.21 | 159.57
2018-03-18 09:00 | 166.22 | 159.97
2018-03-18 09:30 | 167.09 | 160.47
2018-03-18 10:00 | 167.64 | 161.07
2018-03-18 10:30 | 168.53 | 161.49
2018-03-18 11:00 | 169.71 | 162.78
2018-03-18 11:30 | 170.7 | 163.85
2018-03-18 12:00 | 171.91 | 165.2
2018-03-18 12:30 | 173.69 | 167.01
2018-03-18 13:00 | 174.88 | 168.43
2018-03-18 13:30 | 175.56 | 169.26
2018-03-18 14:00 | 177.61 | 171.5
2018-03-18 14:30 | 178.09 | 172.12
2018-03-18 15:00 | 179.99 | 174.07
2018-03-18 15:30 | 190.84 | 184.01
2018-03-18 16:00 | 198.9 | 192.29
2018-03-18 16:30 | 201.59 | 195.1
2018-03-18 17:00 | 202.46 | 196.19
2018-03-18 17:30 | 203.37 | 197.19
2018-03-18 18:00 | 204.59 | 198.52
2018-03-18 18:30 | 204.82 | 199
2018-03-18 19:00 | 205.2 | 199.45
2018-03-18 19:30 | 203.82 | 197.71
2018-03-18 20:00 | 201.09 | 194.68
2018-03-18 20:30 | 198.43 | 191.56
2018-03-18 21:00 | 195.69 | 188.32
2018-03-18 21:30 | 192.81 | 186.2
2018-03-18 22:00 | 190.34 | 183.58
2018-03-18 22:30 | 188.19 | 181.15
2018-03-18 23:00 | 186.82 | 179.5
2018-03-18 23:30 | 181.09 | 173.58
2018-03-19 | 170.32 | 162.85
2018-03-19 00:30 | 167.74 | 160.27
2018-03-19 01:00 | 166.97 | 159.84
2018-03-19 01:30 | 166.23 | 159.4
2018-03-19 02:00 | 165.28 | 158.57
2018-03-19 02:30 | 164.53 | 157.95
2018-03-19 03:00 | 164.21 | 157.72
2018-03-19 03:30 | 163.93 | 157.49
2018-03-19 04:00 | 163.84 | 157.44
2018-03-19 04:30 | 164.12 | 157.91
2018-03-19 05:00 | 164.35 | 158.3
2018-03-19 05:30 | 165.59 | 159.74
2018-03-19 06:00 | 167.12 | 161.32
2018-03-19 06:30 | 168.33 | 162.62
2018-03-19 07:00 | 169.4 | 163.39
2018-03-19 07:30 | 170.14 | 164.47
2018-03-19 08:00 | 171.52 | 166.12
2018-03-19 08:30 | 172.19 | 166.13
2018-03-19 09:00 | 171.95 | 166.12
2018-03-19 09:30 | 171.99 | 166.05
2018-03-19 10:00 | 174.23 | 168.31
2018-03-19 10:30 | 183.43 | 177.37
2018-03-19 11:00 | 183.04 | 177.24
2018-03-19 11:30 | 189.71 | 183.73
2018-03-19 12:00 | 190.58 | 183.77
2018-03-19 12:30 | 195.4 | 188.28
2018-03-19 13:00 | 224.33 | 217.51
2018-03-19 13:30 | 243.99 | 237.26
2018-03-19 14:00 | 246.84 | 240.05
2018-03-19 14:30 | 248.31 | 241.48
2018-03-19 15:00 | 247.11 | 240.15
2018-03-19 15:30 | 247.99 | 241.02
2018-03-19 16:00 | 252.06 | 245.21
2018-03-19 16:30 | 252 | 244.82
2018-03-19 17:00 | 253.18 | 245.94
2018-03-19 17:30 | 253.91 | 246.39
2018-03-19 18:00 | 255.75 | 248.12
2018-03-19 18:30 | 256.53 | 248.96
2018-03-19 19:00 | 257.77 | 250.49
2018-03-19 19:30 | 257.09 | 249.41
2018-03-19 20:00 | 253.88 | 245.86
2018-03-19 20:30 | 252.56 | 243.96
2018-03-19 21:00 | 248.85 | 239.9
2018-03-19 21:30 | 245.92 | 237.81
2018-03-19 22:00 | 243.48 | 234.92
2018-03-19 22:30 | 240.73 | 232.21
2018-03-19 23:00 | 237.93 | 229.25
2018-03-19 23:30 | 236.33 | 227.96
2018-03-20 | 216.59 | 208.81
2018-03-20 00:30 | 181.13 | 173.75
2018-03-20 01:00 | 173.28 | 165.5
2018-03-20 01:30 | 172.91 | 165.03
2018-03-20 02:00 | 171.6 | 164.23
2018-03-20 02:30 | 171.01 | 164.11
2018-03-20 03:00 | 170.31 | 163.34
2018-03-20 03:30 | 170.32 | 163.39
2018-03-20 04:00 | 169.5 | 162.74
2018-03-20 04:30 | 169.44 | 162.76
2018-03-20 05:00 | 169.8 | 163.26
2018-03-20 05:30 | 171.17 | 164.34
2018-03-20 06:00 | 172.56 | 165.67
2018-03-20 06:30 | 174.98 | 168.12
2018-03-20 07:00 | 175.95 | 168.19
2018-03-20 07:30 | 176.43 | 168.45
2018-03-20 08:00 | 177.31 | 169.82
2018-03-20 08:30 | 176.73 | 169.35
2018-03-20 09:00 | 177.34 | 169.65
2018-03-20 09:30 | 177.55 | 169.83
2018-03-20 10:00 | 178.11 | 170.4
2018-03-20 10:30 | 178.34 | 171.03
2018-03-20 11:00 | 180.58 | 173.69
2018-03-20 11:30 | 181.39 | 174.92
2018-03-20 12:00 | 182.85 | 176.96
2018-03-20 12:30 | 182.49 | 176.92
2018-03-20 13:00 | 186.67 | 181.41
2018-03-20 13:30 | 189.71 | 184.39
2018-03-20 14:00 | 193.12 | 187.76
2018-03-20 14:30 | 193.16 | 187.64
2018-03-20 15:00 | 192.27 | 186.23
2018-03-20 15:30 | 193.4 | 187.51
2018-03-20 16:00 | 194.8 | 189.07
2018-03-20 16:30 | 195.91 | 190.19
2018-03-20 17:00 | 196.33 | 190.56
2018-03-20 17:30 | 225.54 | 219.58
2018-03-20 18:00 | 251.79 | 245.79
2018-03-20 18:30 | 259.12 | 253.16
2018-03-20 19:00 | 258.97 | 253.18
2018-03-20 19:30 | 257.58 | 251.58
2018-03-20 20:00 | 254.34 | 248.02
2018-03-20 20:30 | 251.3 | 244.41
2018-03-20 21:00 | 248.15 | 241.01
2018-03-20 21:30 | 227.53 | 220.78
2018-03-20 22:00 | 189.93 | 183.24
2018-03-20 22:30 | 177.9 | 171.3
2018-03-20 23:00 | 174.67 | 168.34
2018-03-20 23:30 | 173.73 | 167.1
2018-03-21 | 172.55 | 165.72
2018-03-21 00:30 | 170.53 | 164.27
2018-03-21 01:00 | 169.6 | 163.13
2018-03-21 01:30 | 169.25 | 162.53
2018-03-21 02:00 | 168.51 | 161.4
2018-03-21 02:30 | 167.86 | 161.19
2018-03-21 03:00 | 167.62 | 160.93
2018-03-21 03:30 | 167.23 | 160.48
2018-03-21 04:00 | 166.55 | 159.84
2018-03-21 04:30 | 167.37 | 160.77
2018-03-21 05:00 | 168.38 | 162.04
2018-03-21 05:30 | 167.91 | 161.91
2018-03-21 06:00 | 170.34 | 164.01
2018-03-21 06:30 | 172.19 | 165.27
2018-03-21 07:00 | 173.2 | 166.36
2018-03-21 07:30 | 173.78 | 167.24
2018-03-21 08:00 | 174.77 | 168.25
2018-03-21 08:30 | 173.97 | 167.47
2018-03-21 09:00 | 173.49 | 166.95
2018-03-21 09:30 | 172.17 | 165.34
2018-03-21 10:00 | 175.2 | 168.38
2018-03-21 10:30 | 177.88 | 171.54
2018-03-21 11:00 | 179.88 | 173.69
2018-03-21 11:30 | 180.44 | 174.2
2018-03-21 12:00 | 178.43 | 172.01
2018-03-21 12:30 | 179.23 | 172.86
2018-03-21 13:00 | 179.68 | 173.29
2018-03-21 13:30 | 179.24 | 172.96
2018-03-21 14:00 | 182.33 | 176.34
2018-03-21 14:30 | 182.96 | 177.05
2018-03-21 15:00 | 183.27 | 177.43
2018-03-21 15:30 | 183.73 | 177.96
2018-03-21 16:00 | 184.27 | 178.64
2018-03-21 16:30 | 185.23 | 179.47
2018-03-21 17:00 | 185.32 | 179.44
2018-03-21 17:30 | 185.54 | 179.47
2018-03-21 18:00 | 187.27 | 181.33
2018-03-21 18:30 | 188.05 | 182.27
2018-03-21 19:00 | 187.48 | 181.68
2018-03-21 19:30 | 188 | 182.05
2018-03-21 20:00 | 185.64 | 179.44
2018-03-21 20:30 | 183.33 | 176.98
2018-03-21 21:00 | 181.54 | 174.86
2018-03-21 21:30 | 179.1 | 172.95
2018-03-21 22:00 | 177.34 | 170.97
2018-03-21 22:30 | 174.84 | 168.49
2018-03-21 23:00 | 172.26 | 165.97
2018-03-21 23:30 | 171.39 | 165.05
2018-03-22 | 169.96 | 163.75
2018-03-22 00:30 | 168.16 | 162.55
2018-03-22 01:00 | 167.89 | 161.33
2018-03-22 01:30 | 169.23 | 161.17
2018-03-22 02:00 | 168.85 | 160.81
2018-03-22 02:30 | 168.67 | 160.78
2018-03-22 03:00 | 167.18 | 159.67
2018-03-22 03:30 | 167.09 | 159.72
2018-03-22 04:00 | 166.73 | 159.22
2018-03-22 04:30 | 167.33 | 159.43
2018-03-22 05:00 | 167.51 | 159.5
2018-03-22 05:30 | 168.99 | 161.15
2018-03-22 06:00 | 170.81 | 162.51
2018-03-22 06:30 | 172.43 | 164.05
2018-03-22 07:00 | 173.42 | 164.91
2018-03-22 07:30 | 175.61 | 167.57
2018-03-22 08:00 | 176.35 | 167.97
2018-03-22 08:30 | 176.06 | 167.68
2018-03-22 09:00 | 175.65 | 167.05
2018-03-22 09:30 | 203.72 | 195.32
2018-03-22 10:00 | 214.51 | 206.16
2018-03-22 10:30 | 214.65 | 206.53
2018-03-22 11:00 | 215.26 | 206.43
2018-03-22 11:30 | 215.82 | 206.84
2018-03-22 12:00 | 216.38 | 207.39
2018-03-22 12:30 | 215.16 | 205.93
2018-03-22 13:00 | 215.92 | 206.64
2018-03-22 13:30 | 216.84 | 207.38
2018-03-22 14:00 | 218.06 | 208.48
2018-03-22 14:30 | 220.01 | 210.68
2018-03-22 15:00 | 219.57 | 210.28
2018-03-22 15:30 | 233.98 | 224.92
2018-03-22 16:00 | 242.93 | 234.12
2018-03-22 16:30 | 243.8 | 234.91
2018-03-22 17:00 | 243.32 | 234.6
2018-03-22 17:30 | 243.61 | 234.79
2018-03-22 18:00 | 245.15 | 236.37
2018-03-22 18:30 | 245.59 | 236.92
2018-03-22 19:00 | 246.79 | 238.22
2018-03-22 19:30 | 246.17 | 237.4
2018-03-22 20:00 | 245.5 | 236.52
2018-03-22 20:30 | 243.66 | 234.49
2018-03-22 21:00 | 241.52 | 232.15
2018-03-22 21:30 | 220.21 | 211.73
2018-03-22 22:00 | 183.61 | 174.66
2018-03-22 22:30 | 175.09 | 165.73
2018-03-22 23:00 | 172.96 | 163.49
2018-03-22 23:30 | 171.5 | 162.01
2018-03-23 | 170.48 | 160.89
2018-03-23 00:30 | 169.15 | 160.23
2018-03-23 01:00 | 168.31 | 159.56
2018-03-23 01:30 | 168.31 | 159.41
2018-03-23 02:00 | 167.32 | 158.6
2018-03-23 02:30 | 167.1 | 158.44
2018-03-23 03:00 | 166.36 | 157.86
2018-03-23 03:30 | 166.09 | 157.57
2018-03-23 04:00 | 167.16 | 158.57
2018-03-23 04:30 | 167.13 | 158.51
2018-03-23 05:00 | 167.97 | 159.25
2018-03-23 05:30 | 168.46 | 160.11
2018-03-23 06:00 | 169.62 | 160.91
2018-03-23 06:30 | 172.87 | 163.54
2018-03-23 07:00 | 172.6 | 162.71
2018-03-23 07:30 | 170.91 | 160.99
2018-03-23 08:00 | 170.34 | 160.48
2018-03-23 08:30 | 167.41 | 157.69
2018-03-23 09:00 | 167.72 | 157.92
2018-03-23 09:30 | 166.82 | 156.96
2018-03-23 10:00 | 166.71 | 157.15
2018-03-23 10:30 | 166.91 | 156.96
2018-03-23 11:00 | 166.52 | 156.79
2018-03-23 11:30 | 166.55 | 156.56
2018-03-23 12:00 | 166.13 | 156.11
2018-03-23 12:30 | 166.02 | 155.81
2018-03-23 13:00 | 168.37 | 158.4
2018-03-23 13:30 | 170.01 | 160.78
2018-03-23 14:00 | 170.49 | 162.05
2018-03-23 14:30 | 171.46 | 162.49
2018-03-23 15:00 | 172.71 | 163.58
2018-03-23 15:30 | 180.42 | 170.05
2018-03-23 16:00 | 183.05 | 171.86
2018-03-23 16:30 | 185.05 | 173.68
2018-03-23 17:00 | 186.28 | 174.77
2018-03-23 17:30 | 186.25 | 174.45
2018-03-23 18:00 | 188.36 | 176.63
2018-03-23 18:30 | 187.81 | 176.61
2018-03-23 19:00 | 188.7 | 177.74
2018-03-23 19:30 | 188.08 | 176.98
2018-03-23 20:00 | 187.58 | 176.18
2018-03-23 20:30 | 185.89 | 174.37
2018-03-23 21:00 | 184.15 | 172.5
2018-03-23 21:30 | 182.1 | 171.68
2018-03-23 22:00 | 181.25 | 171.15
2018-03-23 22:30 | 179.79 | 169.38
2018-03-23 23:00 | 178.71 | 167.87
2018-03-23 23:30 | 177.54 | 166.24
2018-03-24 | 176.39 | 165.31
2018-03-24 00:30 | 175.1 | 164.69
2018-03-24 01:00 | 174.21 | 163.64
2018-03-24 01:30 | 173.85 | 163.38
2018-03-24 02:00 | 172.95 | 162.48
2018-03-24 02:30 | 172.92 | 162.41
2018-03-24 03:00 | 172.8 | 162.23
2018-03-24 03:30 | 172.32 | 161.94
2018-03-24 04:00 | 172.29 | 162.04
2018-03-24 04:30 | 171.67 | 161.62
2018-03-24 05:00 | 171.98 | 161.87
2018-03-24 05:30 | 172.65 | 162.75
2018-03-24 06:00 | 172.18 | 162.59
2018-03-24 06:30 | 173.57 | 164.21
2018-03-24 07:00 | 174.57 | 165.33
2018-03-24 07:30 | 175.69 | 165.59
2018-03-24 08:00 | 175.37 | 165.33
2018-03-24 08:30 | 173.39 | 163.22
2018-03-24 09:00 | 173.21 | 161.81
2018-03-24 09:30 | 173.03 | 161.39
2018-03-24 10:00 | 174.04 | 162.23
2018-03-24 10:30 | 173.96 | 162.09
2018-03-24 11:00 | 175.35 | 163.53
2018-03-24 11:30 | 176.24 | 164.6
2018-03-24 12:00 | 177.29 | 165.55
2018-03-24 12:30 | 178.68 | 166.96
2018-03-24 13:00 | 179.24 | 167.59
2018-03-24 13:30 | 180.35 | 168.75
2018-03-24 14:00 | 180.5 | 169.03
2018-03-24 14:30 | 180.77 | 169.45
2018-03-24 15:00 | 180.43 | 169.58
2018-03-24 15:30 | 181.86 | 170.75
2018-03-24 16:00 | 183.34 | 172.62
2018-03-24 16:30 | 184.51 | 173.71
2018-03-24 17:00 | 185.63 | 174.79
2018-03-24 17:30 | 186.2 | 175.14
2018-03-24 18:00 | 188.77 | 177.8
2018-03-24 18:30 | 188.68 | 177.47
2018-03-24 19:00 | 189.31 | 178.61
2018-03-24 19:30 | 188.12 | 177.86
2018-03-24 20:00 | 187.32 | 176.58
2018-03-24 20:30 | 185.41 | 175.05
2018-03-24 21:00 | 184.4 | 173.62
2018-03-24 21:30 | 182.83 | 172.66
2018-03-24 22:00 | 180.86 | 170.66
2018-03-24 22:30 | 179.47 | 169.17
2018-03-24 23:00 | 176.56 | 167.08
2018-03-24 23:30 | 176.06 | 166.64
2018-03-25 | 174.43 | 164.89
2018-03-25 00:30 | 173.77 | 164.43
2018-03-25 01:00 | 173.33 | 163.99
2018-03-25 01:30 | 171.73 | 163.16
2018-03-25 02:00 | 170 | 162.31
2018-03-25 02:30 | 169.89 | 162.18
2018-03-25 03:00 | 169.11 | 161.42
2018-03-25 03:30 | 168.44 | 160.7
2018-03-25 04:00 | 169.03 | 161.23
2018-03-25 04:30 | 168.99 | 161.13
2018-03-25 05:00 | 168.64 | 160.57
2018-03-25 05:30 | 168.49 | 160.8
2018-03-25 06:00 | 169.23 | 161.07
2018-03-25 06:30 | 170.29 | 162.1
2018-03-25 07:00 | 171.08 | 162.89
2018-03-25 07:30 | 171.37 | 163.33
2018-03-25 08:00 | 172.27 | 163.8
2018-03-25 08:30 | 170.45 | 161.84
2018-03-25 09:00 | 171.24 | 162.37
2018-03-25 09:30 | 171.79 | 162.17
2018-03-25 10:00 | 173.71 | 164.44
2018-03-25 10:30 | 175.33 | 166.37
2018-03-25 11:00 | 175.59 | 166.71
2018-03-25 11:30 | 175.7 | 166.77
2018-03-25 12:00 | 175 | 165.44
2018-03-25 12:30 | 175.04 | 165.74
2018-03-25 13:00 | 176.32 | 167.24
2018-03-25 13:30 | 176.39 | 167.48
2018-03-25 14:00 | 177.17 | 168.47
2018-03-25 14:30 | 178.61 | 170.06
2018-03-25 15:00 | 179.16 | 170.73
2018-03-25 15:30 | 181.44 | 173.37
2018-03-25 16:00 | 182.39 | 174.72
2018-03-25 16:30 | 183.87 | 176.37
2018-03-25 17:00 | 185.1 | 177.74
2018-03-25 17:30 | 185.97 | 178.96
2018-03-25 18:00 | 187.26 | 180.51
2018-03-25 18:30 | 188.34 | 181.76
2018-03-25 19:00 | 188.99 | 180.97
2018-03-25 19:30 | 187.46 | 178.97
2018-03-25 20:00 | 186.43 | 177.38
2018-03-25 20:30 | 186.14 | 176.5
2018-03-25 21:00 | 183.95 | 173.8
2018-03-25 21:30 | 182.11 | 172.01
2018-03-25 22:00 | 180.22 | 169.79
2018-03-25 22:30 | 178.62 | 167.85
2018-03-25 23:00 | 175.86 | 165.74
2018-03-25 23:30 | 175.46 | 165.25
2018-03-26 | 173.73 | 163.79
2018-03-26 00:30 | 173.04 | 163.37
2018-03-26 01:00 | 171.3 | 161.86
2018-03-26 01:30 | 171.88 | 162.29
2018-03-26 02:00 | 170.71 | 161.09
2018-03-26 02:30 | 170.51 | 160.88
2018-03-26 03:00 | 169.94 | 160.32
2018-03-26 03:30 | 169.49 | 159.95
2018-03-26 04:00 | 169.34 | 159.76
2018-03-26 04:30 | 169.23 | 160.15
2018-03-26 05:00 | 169.81 | 160.78
2018-03-26 05:30 | 170.18 | 161.63
2018-03-26 06:00 | 172.26 | 163.82
2018-03-26 06:30 | 173.71 | 164.99
2018-03-26 07:00 | 173.88 | 165.55
2018-03-26 07:30 | 174.73 | 166.86
2018-03-26 08:00 | 204.43 | 196.8
2018-03-26 08:30 | 228.83 | 221.54
2018-03-26 09:00 | 234.39 | 226.94
2018-03-26 09:30 | 225.97 | 218.42
2018-03-26 10:00 | 213.42 | 206.68
2018-03-26 10:30 | 211.4 | 204.27
2018-03-26 11:00 | 210.19 | 203.16
2018-03-26 11:30 | 217.74 | 212.12
2018-03-26 12:00 | 236.03 | 232.66
2018-03-26 12:30 | 214.16 | 208.28
2018-03-26 13:00 | 210.87 | 203.92
2018-03-26 13:30 | 221.41 | 214.18
2018-03-26 14:00 | 245.67 | 238.54
2018-03-26 14:30 | 246.11 | 237.94
2018-03-26 15:00 | 244.3 | 234.79
2018-03-26 15:30 | 242.96 | 233.55
2018-03-26 16:00 | 245.57 | 236.63
2018-03-26 16:30 | 246.06 | 236.99
2018-03-26 17:00 | 246.3 | 237.2
2018-03-26 17:30 | 245.95 | 236.58
2018-03-26 18:00 | 246.03 | 236.43
2018-03-26 18:30 | 248.21 | 238.81
2018-03-26 19:00 | 250.55 | 241.27
2018-03-26 19:30 | 249.75 | 240.06
2018-03-26 20:00 | 231.84 | 221.84
2018-03-26 20:30 | 194.73 | 183.91
2018-03-26 21:00 | 185.68 | 174.35
2018-03-26 21:30 | 183.92 | 173.11
2018-03-26 22:00 | 181.1 | 170.63
2018-03-26 22:30 | 179.38 | 168.54
2018-03-26 23:00 | 177.85 | 166.87
2018-03-26 23:30 | 176.92 | 165.82
2018-03-27 | 174.91 | 163.9
2018-03-27 00:30 | 173.19 | 162.45
2018-03-27 01:00 | 172.08 | 161.52
2018-03-27 01:30 | 171.46 | 160.79
2018-03-27 02:00 | 170.95 | 160.23
2018-03-27 02:30 | 170.22 | 159.67
2018-03-27 03:00 | 170.08 | 159.52
2018-03-27 03:30 | 169.81 | 159.23
2018-03-27 04:00 | 169.78 | 159.2
2018-03-27 04:30 | 169.27 | 158.81
2018-03-27 05:00 | 170.23 | 159.9
2018-03-27 05:30 | 170.59 | 160.71
2018-03-27 06:00 | 172.75 | 162.74
2018-03-27 06:30 | 173.62 | 163.58
2018-03-27 07:00 | 202.97 | 193.12
2018-03-27 07:30 | 226.02 | 216.93
2018-03-27 08:00 | 233.44 | 224.92
2018-03-27 08:30 | 232.52 | 223.96
2018-03-27 09:00 | 232.51 | 223.88
2018-03-27 09:30 | 231.46 | 222.74
2018-03-27 10:00 | 230.44 | 221.7
2018-03-27 10:30 | 229.66 | 221.14
2018-03-27 11:00 | 229.86 | 221.29
2018-03-27 11:30 | 230.91 | 222.43
2018-03-27 12:00 | 232.5 | 224.22
2018-03-27 12:30 | 233.75 | 225.45
2018-03-27 13:00 | 235.62 | 227.34
2018-03-27 13:30 | 236.49 | 228.34
2018-03-27 14:00 | 238.75 | 230.67
2018-03-27 14:30 | 240.48 | 232.56
2018-03-27 15:00 | 241.35 | 233.54
2018-03-27 15:30 | 242.01 | 234.38
2018-03-27 16:00 | 242.92 | 235.96
2018-03-27 16:30 | 244.01 | 236.85
2018-03-27 17:00 | 246.33 | 239.14
2018-03-27 17:30 | 247.34 | 240.11
2018-03-27 18:00 | 248.22 | 241.43
2018-03-27 18:30 | 249.33 | 242.78
2018-03-27 19:00 | 251.57 | 245.2
2018-03-27 19:30 | 250.06 | 243.18
2018-03-27 20:00 | 249.28 | 242.39
2018-03-27 20:30 | 247.14 | 240
2018-03-27 21:00 | 244.66 | 237.05
2018-03-27 21:30 | 223.34 | 216.32
2018-03-27 22:00 | 187.94 | 180.85
2018-03-27 22:30 | 177.43 | 169.91
2018-03-27 23:00 | 175.24 | 167.5
2018-03-27 23:30 | 174.9 | 166.65
2018-03-28 | 172.72 | 164.56
2018-03-28 00:30 | 172.03 | 163.79
2018-03-28 01:00 | 171.05 | 163.07
2018-03-28 01:30 | 169.24 | 161.68
2018-03-28 02:00 | 168.95 | 161.41
2018-03-28 02:30 | 168.91 | 161.32
2018-03-28 03:00 | 169.03 | 161.52
2018-03-28 03:30 | 168.49 | 160.97
2018-03-28 04:00 | 168.6 | 161.17
2018-03-28 04:30 | 167.85 | 160.68
2018-03-28 05:00 | 168.77 | 161.97
2018-03-28 05:30 | 169.46 | 162.8
2018-03-28 06:00 | 171.13 | 164.08
2018-03-28 06:30 | 172.71 | 165.96
2018-03-28 07:00 | 203.4 | 196.59
2018-03-28 07:30 | 229.14 | 222.74
2018-03-28 08:00 | 237.22 | 230.41
2018-03-28 08:30 | 236.75 | 229.64
2018-03-28 09:00 | 235.78 | 228.73
2018-03-28 09:30 | 235.28 | 228.19
2018-03-28 10:00 | 235.55 | 228.44
2018-03-28 10:30 | 235.95 | 228.9
2018-03-28 11:00 | 237.33 | 230.63
2018-03-28 11:30 | 238.58 | 231.87
2018-03-28 12:00 | 239.66 | 233.02
2018-03-28 12:30 | 239.56 | 233.05
2018-03-28 13:00 | 241.57 | 234.92
2018-03-28 13:30 | 244.1 | 237.25
2018-03-28 14:00 | 246 | 239.31
2018-03-28 14:30 | 246.46 | 239.95
2018-03-28 15:00 | 246.57 | 240.1
2018-03-28 15:30 | 247.4 | 240.74
2018-03-28 16:00 | 249.18 | 242.12
2018-03-28 16:30 | 250.18 | 243.12
2018-03-28 17:00 | 251.63 | 244.53
2018-03-28 17:30 | 251.41 | 244.02
2018-03-28 18:00 | 252.78 | 245.37
2018-03-28 18:30 | 253.68 | 246.31
2018-03-28 19:00 | 255.76 | 248.49
2018-03-28 19:30 | 255.28 | 247.64
2018-03-28 20:00 | 252.55 | 244.84
2018-03-28 20:30 | 250.7 | 242.64
2018-03-28 21:00 | 248.77 | 240.37
2018-03-28 21:30 | 246.17 | 238.65
2018-03-28 22:00 | 242.99 | 235.17
2018-03-28 22:30 | 240.93 | 232.78
2018-03-28 23:00 | 239.23 | 230.69
2018-03-28 23:30 | 237.12 | 229.06
2018-03-29 | 215.98 | 208.44
2018-03-29 00:30 | 180.36 | 173.1
2018-03-29 01:00 | 171.49 | 163.88
2018-03-29 01:30 | 170.87 | 163.04
2018-03-29 02:00 | 170.26 | 162.09
2018-03-29 02:30 | 169.28 | 161.37
2018-03-29 03:00 | 168.54 | 160.89
2018-03-29 03:30 | 168.54 | 161.07
2018-03-29 04:00 | 168.27 | 160.93
2018-03-29 04:30 | 168.59 | 161.32
2018-03-29 05:00 | 168.79 | 161.6
2018-03-29 05:30 | 169.95 | 163.17
2018-03-29 06:00 | 171.6 | 164.8
2018-03-29 06:30 | 173.58 | 166.3
2018-03-29 07:00 | 200.99 | 193.33
2018-03-29 07:30 | 222.38 | 214.83
2018-03-29 08:00 | 177.14 | 169.64
2018-03-29 08:30 | 171.8 | 164.94
2018-03-29 09:00 | 167.47 | 160.63
2018-03-29 09:30 | 166.27 | 159.41
2018-03-29 10:00 | 166.96 | 160.02
2018-03-29 10:30 | 167.32 | 160.43
2018-03-29 11:00 | 168.03 | 160.99
2018-03-29 11:30 | 169.22 | 162.03
2018-03-29 12:00 | 170.14 | 162.92
2018-03-29 12:30 | 171.23 | 163.88
2018-03-29 13:00 | 172.31 | 165.02
2018-03-29 13:30 | 172.17 | 165.38
2018-03-29 14:00 | 173.17 | 166.74
2018-03-29 14:30 | 174.63 | 168.34
2018-03-29 15:00 | 171.35 | 165.02
2018-03-29 15:30 | 172.67 | 166.07
2018-03-29 16:00 | 174.47 | 167.76
2018-03-29 16:30 | 176.31 | 169.55
2018-03-29 17:00 | 178.47 | 171.79
2018-03-29 17:30 | 179.43 | 172.47
2018-03-29 18:00 | 178.41 | 171.51
2018-03-29 18:30 | 177.69 | 170.88
2018-03-29 19:00 | 179.33 | 172.57
2018-03-29 19:30 | 178.22 | 171.46
2018-03-29 20:00 | 176.48 | 169.48
2018-03-29 20:30 | 175.1 | 167.83
2018-03-29 21:00 | 179.72 | 173.12
2018-03-29 21:30 | 179 | 173.23
2018-03-29 22:00 | 176.68 | 170.87
2018-03-29 22:30 | 175.31 | 169.36
2018-03-29 23:00 | 173.9 | 167.77
2018-03-29 23:30 | 172.58 | 166.54
2018-03-30 | 170.29 | 164.37
2018-03-30 00:30 | 168.87 | 163.04
2018-03-30 01:00 | 167.5 | 162.07
2018-03-30 01:30 | 166.67 | 161.32
2018-03-30 02:00 | 166.46 | 160.94
2018-03-30 02:30 | 165.44 | 159.98
2018-03-30 03:00 | 165 | 159.42
2018-03-30 03:30 | 164.71 | 159.14
2018-03-30 04:00 | 164.49 | 158.9
2018-03-30 04:30 | 164.73 | 159.15
2018-03-30 05:00 | 164.69 | 159.06
2018-03-30 05:30 | 164.36 | 158.75
2018-03-30 06:00 | 165.08 | 159.52
2018-03-30 06:30 | 165.35 | 159.85
2018-03-30 07:00 | 165.71 | 160.25
2018-03-30 07:30 | 166.78 | 161.47
2018-03-30 08:00 | 166.63 | 161.37
2018-03-30 08:30 | 167.15 | 161.94
2018-03-30 09:00 | 166.8 | 161.54
2018-03-30 09:30 | 167.16 | 161.96
2018-03-30 10:00 | 167.82 | 162.7
2018-03-30 10:30 | 168.4 | 163.1
2018-03-30 11:00 | 170.73 | 164.5
2018-03-30 11:30 | 171.98 | 165.57
2018-03-30 12:00 | 172.93 | 166.38
2018-03-30 12:30 | 174.83 | 168.17
2018-03-30 13:00 | 176.05 | 169.54
2018-03-30 13:30 | 177.54 | 170.93
2018-03-30 14:00 | 179.02 | 172.46
2018-03-30 14:30 | 179.59 | 173.04
2018-03-30 15:00 | 181.01 | 174.51
2018-03-30 15:30 | 182.14 | 175.83
2018-03-30 16:00 | 177.83 | 170.68
2018-03-30 16:30 | 175.83 | 168.14
2018-03-30 17:00 | 177.36 | 169.61
2018-03-30 17:30 | 179.01 | 171.36
2018-03-30 18:00 | 179.97 | 172.29
2018-03-30 18:30 | 179.94 | 171.97
2018-03-30 19:00 | 181.26 | 173.31
2018-03-30 19:30 | 180.61 | 172.4
2018-03-30 20:00 | 178.29 | 169.78
2018-03-30 20:30 | 177.5 | 169.73
2018-03-30 21:00 | 180.07 | 173.52
2018-03-30 21:30 | 179.84 | 174.12
2018-03-30 22:00 | 178.03 | 172.19
2018-03-30 22:30 | 176.2 | 170.4
2018-03-30 23:00 | 173.83 | 168.38
2018-03-30 23:30 | 172.87 | 167.44
2018-03-31 | 170.73 | 165.31
2018-03-31 00:30 | 170.19 | 164.24
2018-03-31 01:00 | 168.74 | 162.78
2018-03-31 01:30 | 167.79 | 162.12
2018-03-31 02:00 | 167.33 | 161.7
2018-03-31 02:30 | 166.72 | 161.07
2018-03-31 03:00 | 166.34 | 160.67
2018-03-31 03:30 | 165.78 | 159.93
2018-03-31 04:00 | 165.11 | 159.29
2018-03-31 04:30 | 165.16 | 159.45
2018-03-31 05:00 | 165.27 | 159.52
2018-03-31 05:30 | 165.09 | 159.42
2018-03-31 06:00 | 164.9 | 159.24
2018-03-31 06:30 | 165.57 | 159.81
2018-03-31 07:00 | 166.61 | 160.94
2018-03-31 07:30 | 168.26 | 162.41
2018-03-31 08:00 | 168.32 | 162.47
2018-03-31 08:30 | 168.31 | 162.56
2018-03-31 09:00 | 167.57 | 161.79
2018-03-31 09:30 | 167.48 | 161.43
2018-03-31 10:00 | 168 | 161.81
2018-03-31 10:30 | 168.51 | 162.17
2018-03-31 11:00 | 168.89 | 162.55
2018-03-31 11:30 | 169.7 | 163.42
2018-03-31 12:00 | 170.8 | 164.62
2018-03-31 12:30 | 172.01 | 165.93
2018-03-31 13:00 | 173.16 | 167.17
2018-03-31 13:30 | 174.42 | 168.47
2018-03-31 14:00 | 175.53 | 169.52
2018-03-31 14:30 | 176.82 | 170.82
2018-03-31 15:00 | 176.7 | 170.86
2018-03-31 15:30 | 171.57 | 165.24
2018-03-31 16:00 | 170.57 | 164.01
2018-03-31 16:30 | 171.87 | 165.43
2018-03-31 17:00 | 173.14 | 166.42
2018-03-31 17:30 | 174.56 | 167.98
2018-03-31 18:00 | 175.13 | 168.46
2018-03-31 18:30 | 175.19 | 168.76
2018-03-31 19:00 | 176.18 | 169.88
2018-03-31 19:30 | 175.35 | 168.7
2018-03-31 20:00 | 173.78 | 166.91
2018-03-31 20:30 | 172.55 | 165.26
2018-03-31 21:00 | 170.91 | 163.4
2018-03-31 21:30 | 169.93 | 162.79
2018-03-31 22:00 | 168.83 | 161.78
2018-03-31 22:30 | 167.39 | 160.18
2018-03-31 23:00 | 166.17 | 158.97
2018-03-31 23:30 | 165.31 | 158.16
2018-04-01 | 164.87 | 158.29
2018-04-01 00:30 | 167.64 | 161.98
2018-04-01 01:00 | 168.38 | 162.95
2018-04-01 01:30 | 167.74 | 162.33
2018-04-01 02:00 | 168.07 | 162.63
2018-04-01 02:30 | 168.87 | 161.84
2018-04-01 03:00 | 168.34 | 161.07
2018-04-01 03:30 | 167.55 | 160.15
2018-04-01 04:00 | 167.3 | 159.87
2018-04-01 04:30 | 166.97 | 159.47
2018-04-01 05:00 | 167.42 | 159.94
2018-04-01 05:30 | 167.21 | 159.69
2018-04-01 06:00 | 167.77 | 160.21
2018-04-01 06:30 | 168.03 | 160.46
2018-04-01 07:00 | 173.7 | 166.54
2018-04-01 07:30 | 179.78 | 173.09
2018-04-01 08:00 | 198.82 | 193.2
2018-04-01 08:30 | 199.33 | 193.73
2018-04-01 09:00 | 191.59 | 185.57
2018-04-01 09:30 | 177.84 | 171.08
2018-04-01 10:00 | 178.34 | 171.57
2018-04-01 10:30 | 178.54 | 171.62
2018-04-01 11:00 | 173.08 | 166.44
2018-04-01 11:30 | 167.91 | 161.39
2018-04-01 12:00 | 169.93 | 163.5
2018-04-01 12:30 | 172.22 | 165.87
2018-04-01 13:00 | 173.52 | 167.19
2018-04-01 13:30 | 175.18 | 169.11
2018-04-01 14:00 | 175.33 | 169.33
2018-04-01 14:30 | 175.29 | 169.36
2018-04-01 15:00 | 176.25 | 170.44
2018-04-01 15:30 | 177.78 | 172.06
2018-04-01 16:00 | 174.85 | 168
2018-04-01 16:30 | 173.13 | 166.09
2018-04-01 17:00 | 174.64 | 167.45
2018-04-01 17:30 | 175.76 | 169.19
2018-04-01 18:00 | 176.13 | 169.64
2018-04-01 18:30 | 176.06 | 169.57
2018-04-01 19:00 | 177.23 | 170.82
2018-04-01 19:30 | 176.1 | 169.35
2018-04-01 20:00 | 173.89 | 166.74
2018-04-01 20:30 | 173.25 | 165.74
2018-04-01 21:00 | 171.28 | 163.65
2018-04-01 21:30 | 169.7 | 162.4
2018-04-01 22:00 | 167.27 | 159.68
2018-04-01 22:30 | 166.36 | 158.76
2018-04-01 23:00 | 165.4 | 157.57
2018-04-01 23:30 | 168.23 | 161.16
2018-04-02 | 170.88 | 164.72
2018-04-02 00:30 | 169.39 | 163.36
2018-04-02 01:00 | 168.5 | 162.67
2018-04-02 01:30 | 167.89 | 162.08
2018-04-02 02:00 | 167.14 | 161.3
2018-04-02 02:30 | 167.04 | 161.18
2018-04-02 03:00 | 166.42 | 160.53
2018-04-02 03:30 | 166.36 | 160.4
2018-04-02 04:00 | 166.31 | 160.33
2018-04-02 04:30 | 167.14 | 161.17
2018-04-02 05:00 | 167.77 | 161.81
2018-04-02 05:30 | 168.45 | 162.51
2018-04-02 06:00 | 168.45 | 162.5
2018-04-02 06:30 | 168.84 | 162.95
2018-04-02 07:00 | 169.79 | 164
2018-04-02 07:30 | 170.04 | 164.41
2018-04-02 08:00 | 170.16 | 164.59
2018-04-02 08:30 | 169.54 | 164.05
2018-04-02 09:00 | 169.2 | 163.79
2018-04-02 09:30 | 169.43 | 163.94
2018-04-02 10:00 | 170.54 | 165.11
2018-04-02 10:30 | 170.97 | 165.68
2018-04-02 11:00 | 171.45 | 166.02
2018-04-02 11:30 | 172.01 | 166.6
2018-04-02 12:00 | 173.73 | 168.35
2018-04-02 12:30 | 175.05 | 169.64
2018-04-02 13:00 | 170.61 | 164.54
2018-04-02 13:30 | 168.79 | 162.44
2018-04-02 14:00 | 169.17 | 162.98
2018-04-02 14:30 | 169.78 | 163.71
2018-04-02 15:00 | 171.31 | 165.11
2018-04-02 15:30 | 172 | 165.66
2018-04-02 16:00 | 172.99 | 166.72
2018-04-02 16:30 | 174.4 | 167.96
2018-04-02 17:00 | 175.8 | 169.64
2018-04-02 17:30 | 177.74 | 171.91
2018-04-02 18:00 | 178.59 | 172.88
2018-04-02 18:30 | 179.77 | 174.13
2018-04-02 19:00 | 180.97 | 175.3
2018-04-02 19:30 | 179.76 | 173.85
2018-04-02 20:00 | 177.45 | 171.3
2018-04-02 20:30 | 175.68 | 169.28
2018-04-02 21:00 | 173.75 | 167.02
2018-04-02 21:30 | 171.91 | 165.38
2018-04-02 22:00 | 170.05 | 163.44
2018-04-02 22:30 | 168.24 | 161.74
2018-04-02 23:00 | 166.3 | 159.65
2018-04-02 23:30 | 165.5 | 158.87
2018-04-03 | 163.9 | 157.29
2018-04-03 00:30 | 162.31 | 156.08
2018-04-03 01:00 | 165.35 | 159.39
2018-04-03 01:30 | 166.32 | 160.42
2018-04-03 02:00 | 165.91 | 160
2018-04-03 02:30 | 165.42 | 159.51
2018-04-03 03:00 | 164.89 | 158.96
2018-04-03 03:30 | 164.31 | 158.34
2018-04-03 04:00 | 164.55 | 158.1
2018-04-03 04:30 | 164.69 | 158.42
2018-04-03 05:00 | 165.08 | 158.91
2018-04-03 05:30 | 165.79 | 159.81
2018-04-03 06:00 | 167.87 | 161.9
2018-04-03 06:30 | 170.23 | 163.93
2018-04-03 07:00 | 171.83 | 165.16
2018-04-03 07:30 | 168.84 | 161.38
2018-04-03 08:00 | 168.76 | 161.51
2018-04-03 08:30 | 169.32 | 162.15
2018-04-03 09:00 | 168.48 | 161.38
2018-04-03 09:30 | 168.32 | 161.06
2018-04-03 10:00 | 169.88 | 162.61
2018-04-03 10:30 | 170.39 | 163.1
2018-04-03 11:00 | 170.89 | 163.64
2018-04-03 11:30 | 171.85 | 164.8
2018-04-03 12:00 | 172.14 | 165
2018-04-03 12:30 | 173.52 | 166.34
2018-04-03 13:00 | 176.03 | 168.72
2018-04-03 13:30 | 176.43 | 169.12
2018-04-03 14:00 | 177.06 | 169.93
2018-04-03 14:30 | 176.94 | 170.1
2018-04-03 15:00 | 176.75 | 169.45
2018-04-03 15:30 | 177.3 | 170.21
2018-04-03 16:00 | 178.33 | 171.57
2018-04-03 16:30 | 178.91 | 172.07
2018-04-03 17:00 | 179.29 | 172.34
2018-04-03 17:30 | 178.91 | 171.95
2018-04-03 18:00 | 180.38 | 173.54
2018-04-03 18:30 | 182.35 | 175.69
2018-04-03 19:00 | 184.41 | 177.66
2018-04-03 19:30 | 182.12 | 175.72
2018-04-03 20:00 | 179.29 | 173.11
2018-04-03 20:30 | 177.98 | 171.18
2018-04-03 21:00 | 176.29 | 169.15
2018-04-03 21:30 | 174.05 | 167.33
2018-04-03 22:00 | 171.83 | 164.83
2018-04-03 22:30 | 168.57 | 161.89
2018-04-03 23:00 | 166.59 | 160.13
2018-04-03 23:30 | 166.26 | 159.47
2018-04-04 | 164.75 | 157.91
2018-04-04 00:30 | 164.54 | 158.19
2018-04-04 01:00 | 168.36 | 162.41
2018-04-04 01:30 | 169.71 | 163.77
2018-04-04 02:00 | 168.66 | 162.76
2018-04-04 02:30 | 167.83 | 161.89
2018-04-04 03:00 | 167.41 | 161.5
2018-04-04 03:30 | 167.58 | 161.6
2018-04-04 04:00 | 167.48 | 161.47
2018-04-04 04:30 | 167.45 | 161.39
2018-04-04 05:00 | 168.15 | 162.11
2018-04-04 05:30 | 169.02 | 163.15
2018-04-04 06:00 | 170.9 | 164.72
2018-04-04 06:30 | 172.93 | 166.1
2018-04-04 07:00 | 168.96 | 161.23
2018-04-04 07:30 | 168.07 | 160.78
2018-04-04 08:00 | 169.72 | 162.61
2018-04-04 08:30 | 169.4 | 162.61
2018-04-04 09:00 | 168.56 | 161.92
2018-04-04 09:30 | 167.47 | 160.57
2018-04-04 10:00 | 167.64 | 160.4
2018-04-04 10:30 | 166.99 | 159.77
2018-04-04 11:00 | 167.48 | 160.35
2018-04-04 11:30 | 167.17 | 160.02
2018-04-04 12:00 | 167.81 | 161.01
2018-04-04 12:30 | 168.94 | 162.17
2018-04-04 13:00 | 169.98 | 163.19
2018-04-04 13:30 | 171.89 | 164.75
2018-04-04 14:00 | 173.24 | 166.4
2018-04-04 14:30 | 173.88 | 167.06
2018-04-04 15:00 | 173.77 | 167.01
2018-04-04 15:30 | 173.91 | 167.16
2018-04-04 16:00 | 175 | 168.5
2018-04-04 16:30 | 175.25 | 168.89
2018-04-04 17:00 | 175.4 | 169.12
2018-04-04 17:30 | 174.9 | 169.17
2018-04-04 18:00 | 175.66 | 170.01
2018-04-04 18:30 | 177.25 | 171.57
2018-04-04 19:00 | 179.29 | 173.7
2018-04-04 19:30 | 178.07 | 172.24
2018-04-04 20:00 | 176.55 | 170.25
2018-04-04 20:30 | 174.72 | 168.25
2018-04-04 21:00 | 173.4 | 166.48
2018-04-04 21:30 | 172.07 | 165.57
2018-04-04 22:00 | 174.53 | 168.56
2018-04-04 22:30 | 173.9 | 167.84
2018-04-04 23:00 | 172.44 | 166.77
2018-04-04 23:30 | 171.4 | 165.63
2018-04-05 | 170.02 | 164.07
2018-04-05 00:30 | 168.93 | 162.84
2018-04-05 01:00 | 167.81 | 161.78
2018-04-05 01:30 | 167.38 | 161.38
2018-04-05 02:00 | 167.03 | 160.98
2018-04-05 02:30 | 166.34 | 160.21
2018-04-05 03:00 | 166.3 | 160.16
2018-04-05 03:30 | 165.72 | 159.56
2018-04-05 04:00 | 165.48 | 159.35
2018-04-05 04:30 | 165.1 | 158.98
2018-04-05 05:00 | 164.85 | 158.66
2018-04-05 05:30 | 165.91 | 159.92
2018-04-05 06:00 | 167.1 | 161.32
2018-04-05 06:30 | 168.99 | 163.08
2018-04-05 07:00 | 172.49 | 166.25
2018-04-05 07:30 | 173.34 | 167.26
2018-04-05 08:00 | 168.31 | 161.45
2018-04-05 08:30 | 167.64 | 160.7
2018-04-05 09:00 | 167.46 | 160.43
2018-04-05 09:30 | 166.25 | 159.05
2018-04-05 10:00 | 165.47 | 158.11
2018-04-05 10:30 | 167.11 | 159.87
2018-04-05 11:00 | 164.52 | 157.57
2018-04-05 11:30 | 164.41 | 157.67
2018-04-05 12:00 | 164.6 | 157.87
2018-04-05 12:30 | 166.54 | 159.88
2018-04-05 13:00 | 168.17 | 161.56
2018-04-05 13:30 | 169.51 | 163.12
2018-04-05 14:00 | 170.46 | 164.35
2018-04-05 14:30 | 171.58 | 165.3
2018-04-05 15:00 | 172.43 | 166
2018-04-05 15:30 | 172.07 | 165.56
2018-04-05 16:00 | 173.51 | 166.96
2018-04-05 16:30 | 174.72 | 168.07
2018-04-05 17:00 | 176.09 | 169.45
2018-04-05 17:30 | 180.28 | 173.47
2018-04-05 18:00 | 213.85 | 207.21
2018-04-05 18:30 | 219.64 | 213.28
2018-04-05 19:00 | 220.94 | 214.85
2018-04-05 19:30 | 219.72 | 213.49
2018-04-05 20:00 | 217.29 | 210.89
2018-04-05 20:30 | 215.08 | 208.29
2018-04-05 21:00 | 213.67 | 206.61
2018-04-05 21:30 | 212.11 | 205.78
2018-04-05 22:00 | 210.73 | 204.1
2018-04-05 22:30 | 208.26 | 201.61
2018-04-05 23:00 | 207.08 | 200.17
2018-04-05 23:30 | 206.44 | 199.67
2018-04-06 | 204.56 | 197.74
2018-04-06 00:30 | 204.06 | 197.27
2018-04-06 01:00 | 204.47 | 198.1
2018-04-06 01:30 | 204.33 | 198.59
2018-04-06 02:00 | 203.45 | 198.05
2018-04-06 02:30 | 203.67 | 198.07
2018-04-06 03:00 | 203.39 | 197.8
2018-04-06 03:30 | 203.22 | 197.6
2018-04-06 04:00 | 203.98 | 198.45
2018-04-06 04:30 | 203.96 | 198.45
2018-04-06 05:00 | 205.01 | 199.6
2018-04-06 05:30 | 206.1 | 201.03
2018-04-06 06:00 | 208.58 | 203.18
2018-04-06 06:30 | 211.5 | 205.56
2018-04-06 07:00 | 213.66 | 207.48
2018-04-06 07:30 | 214.01 | 207.97
2018-04-06 08:00 | 213.99 | 207.79
2018-04-06 08:30 | 213.68 | 207.61
2018-04-06 09:00 | 185.96 | 179.77
2018-04-06 09:30 | 172.05 | 165.67
2018-04-06 10:00 | 169.81 | 163.24
2018-04-06 10:30 | 167.92 | 160.86
2018-04-06 11:00 | 183 | 176.34
2018-04-06 11:30 | 207.57 | 201.16
2018-04-06 12:00 | 207.73 | 201.37
2018-04-06 12:30 | 207.88 | 201.3
2018-04-06 13:00 | 208.54 | 201.74
2018-04-06 13:30 | 208.97 | 202.18
2018-04-06 14:00 | 210.57 | 204.03
2018-04-06 14:30 | 210.67 | 204.24
2018-04-06 15:00 | 211.77 | 205.7
2018-04-06 15:30 | 220.84 | 215
2018-04-06 16:00 | 218.66 | 212.75
2018-04-06 16:30 | 221.02 | 215.1
2018-04-06 17:00 | 222.58 | 216.69
2018-04-06 17:30 | 225.93 | 219.96
2018-04-06 18:00 | 227.43 | 221.36
2018-04-06 18:30 | 228.86 | 222.73
2018-04-06 19:00 | 229.26 | 223.26
2018-04-06 19:30 | 226.43 | 220.15
2018-04-06 20:00 | 225.13 | 218.67
2018-04-06 20:30 | 223.87 | 217.18
2018-04-06 21:00 | 222.39 | 215.57
2018-04-06 21:30 | 220.29 | 214.05
2018-04-06 22:00 | 218.62 | 212.54
2018-04-06 22:30 | 217.05 | 210.72
2018-04-06 23:00 | 215.77 | 209.05
2018-04-06 23:30 | 214.02 | 207.71
2018-04-07 | 179.52 | 172.91
2018-04-07 00:30 | 168.87 | 162.61
2018-04-07 01:00 | 167.99 | 161.66
2018-04-07 01:30 | 167.49 | 161.33
2018-04-07 02:00 | 166.49 | 160.57
2018-04-07 02:30 | 166.31 | 160.44
2018-04-07 03:00 | 166.09 | 160.3
2018-04-07 03:30 | 166.01 | 160.08
2018-04-07 04:00 | 166.17 | 160
2018-04-07 04:30 | 165.96 | 159.53
2018-04-07 05:00 | 165.79 | 159.5
2018-04-07 05:30 | 166 | 159.89
2018-04-07 06:00 | 165.94 | 159.8
2018-04-07 06:30 | 167.36 | 161.38
2018-04-07 07:00 | 167.39 | 161.23
2018-04-07 07:30 | 167.59 | 161.58
2018-04-07 08:00 | 167.85 | 161.82
2018-04-07 08:30 | 167.96 | 161.95
2018-04-07 09:00 | 168.24 | 162.31
2018-04-07 09:30 | 167.66 | 161.94
2018-04-07 10:00 | 167.45 | 161.75
2018-04-07 10:30 | 166.74 | 161.26
2018-04-07 11:00 | 166.27 | 160.79
2018-04-07 11:30 | 166.8 | 161.33
2018-04-07 12:00 | 167.17 | 161.72
2018-04-07 12:30 | 167.53 | 161.91
2018-04-07 13:00 | 167.59 | 161.76
2018-04-07 13:30 | 168.44 | 162.7
2018-04-07 14:00 | 168.96 | 163.39
2018-04-07 14:30 | 169.44 | 163.77
2018-04-07 15:00 | 170.33 | 164.8
2018-04-07 15:30 | 171.59 | 166.14
2018-04-07 16:00 | 173.12 | 167.73
2018-04-07 16:30 | 174.46 | 169.01
2018-04-07 17:00 | 200.33 | 194.65
2018-04-07 17:30 | 219.42 | 213.52
2018-04-07 18:00 | 221.82 | 216.04
2018-04-07 18:30 | 222.55 | 216.73
2018-04-07 19:00 | 224.45 | 218.25
2018-04-07 19:30 | 222.91 | 216.43
2018-04-07 20:00 | 221.15 | 214.25
2018-04-07 20:30 | 220.06 | 212.76
2018-04-07 21:00 | 218.73 | 211.36
2018-04-07 21:30 | 217.12 | 210.74
2018-04-07 22:00 | 216.2 | 209.54
2018-04-07 22:30 | 214.89 | 208.03
2018-04-07 23:00 | 213.69 | 206.98
2018-04-07 23:30 | 212.91 | 206.31
2018-04-08 | 210.96 | 204.76
2018-04-08 00:30 | 178.05 | 171.85
2018-04-08 01:00 | 165.61 | 159.47
2018-04-08 01:30 | 164.62 | 158.58
2018-04-08 02:00 | 165.05 | 158.81
2018-04-08 02:30 | 164.88 | 158.23
2018-04-08 03:00 | 164.76 | 157.77
2018-04-08 03:30 | 163.85 | 157.05
2018-04-08 04:00 | 163.8 | 156.98
2018-04-08 04:30 | 163.53 | 156.7
2018-04-08 05:00 | 164.21 | 157.4
2018-04-08 05:30 | 163.95 | 157.04
2018-04-08 06:00 | 164.87 | 157.81
2018-04-08 06:30 | 165.35 | 158.24
2018-04-08 07:00 | 165.24 | 158.24
2018-04-08 07:30 | 165.45 | 159.05
2018-04-08 08:00 | 165.66 | 158.86
2018-04-08 08:30 | 164.64 | 157.87
2018-04-08 09:00 | 164.38 | 157.69
2018-04-08 09:30 | 165.26 | 158.59
2018-04-08 10:00 | 166.21 | 159.41
2018-04-08 10:30 | 167.5 | 159.68
2018-04-08 11:00 | 166.85 | 158.39
2018-04-08 11:30 | 167.5 | 158.79
2018-04-08 12:00 | 167.29 | 158.61
2018-04-08 12:30 | 168.48 | 159.79
2018-04-08 13:00 | 168.91 | 160.26
2018-04-08 13:30 | 170.86 | 162.27
2018-04-08 14:00 | 172.32 | 164.06
2018-04-08 14:30 | 172.6 | 164.55
2018-04-08 15:00 | 174.27 | 166.37
2018-04-08 15:30 | 204.25 | 196.84
2018-04-08 16:00 | 232.54 | 225.03
2018-04-08 16:30 | 241.01 | 233.47
2018-04-08 17:00 | 242.52 | 234.96
2018-04-08 17:30 | 245.61 | 237.86
2018-04-08 18:00 | 246.58 | 238.56
2018-04-08 18:30 | 248.15 | 240.38
2018-04-08 19:00 | 249.25 | 241.6
2018-04-08 19:30 | 247.6 | 239.66
2018-04-08 20:00 | 245.7 | 237.45
2018-04-08 20:30 | 243.57 | 234.91
2018-04-08 21:00 | 241.83 | 232.99
2018-04-08 21:30 | 240.36 | 232.22
2018-04-08 22:00 | 238.77 | 230.39
2018-04-08 22:30 | 236.68 | 228.66
2018-04-08 23:00 | 234.74 | 226.89
2018-04-08 23:30 | 233.89 | 226.19
2018-04-09 | 232.59 | 224.7
2018-04-09 00:30 | 214.47 | 206.44
2018-04-09 01:00 | 175.95 | 167.61
2018-04-09 01:30 | 165.91 | 157.44
2018-04-09 02:00 | 165.08 | 156.41
2018-04-09 02:30 | 165.25 | 156.51
2018-04-09 03:00 | 165.3 | 156.38
2018-04-09 03:30 | 165.72 | 156.72
2018-04-09 04:00 | 165.46 | 156.59
2018-04-09 04:30 | 165.2 | 156.12
2018-04-09 05:00 | 165.59 | 156.61
2018-04-09 05:30 | 166.58 | 158.08
2018-04-09 06:00 | 166.6 | 158.47
2018-04-09 06:30 | 169.41 | 161.32
2018-04-09 07:00 | 172.74 | 163.82
2018-04-09 07:30 | 176 | 166.28
2018-04-09 08:00 | 175.95 | 166.27
2018-04-09 08:30 | 175.9 | 166.46
2018-04-09 09:00 | 175.62 | 166.22
2018-04-09 09:30 | 175.48 | 165.92
2018-04-09 10:00 | 175.93 | 166.45
2018-04-09 10:30 | 173.97 | 166.48
2018-04-09 11:00 | 175 | 167.63
2018-04-09 11:30 | 175.26 | 167.99
2018-04-09 12:00 | 176.51 | 169.27
2018-04-09 12:30 | 176.66 | 169.56
2018-04-09 13:00 | 176.64 | 169.78
2018-04-09 13:30 | 178.78 | 171.9
2018-04-09 14:00 | 210.98 | 204.46
2018-04-09 14:30 | 238.24 | 231.73
2018-04-09 15:00 | 245.35 | 238.94
2018-04-09 15:30 | 246.53 | 240.35
2018-04-09 16:00 | 247.82 | 241.72
2018-04-09 16:30 | 248.52 | 242.42
2018-04-09 17:00 | 242.05 | 236.51
2018-04-09 17:30 | 230.07 | 227.75
2018-04-09 18:00 | 232.4 | 230.16
2018-04-09 18:30 | 233.22 | 230.99
2018-04-09 19:00 | 233.29 | 230.94
2018-04-09 19:30 | 245.36 | 239.91
2018-04-09 20:00 | 249.18 | 242.39
2018-04-09 20:30 | 247.36 | 240.16
2018-04-09 21:00 | 244.47 | 237.56
2018-04-09 21:30 | 242.9 | 236.02
2018-04-09 22:00 | 242.32 | 235.15
2018-04-09 22:30 | 240.15 | 233.23
2018-04-09 23:00 | 239.35 | 232.57
2018-04-09 23:30 | 237.77 | 231.82
2018-04-10 | 203.87 | 198.03
2018-04-10 00:30 | 169.82 | 163.83
2018-04-10 01:00 | 168.98 | 162.93
2018-04-10 01:30 | 168.81 | 162.7
2018-04-10 02:00 | 168.06 | 161.95
2018-04-10 02:30 | 168.29 | 162.17
2018-04-10 03:00 | 167.67 | 161.49
2018-04-10 03:30 | 167.64 | 161.5
2018-04-10 04:00 | 168.46 | 161.62
2018-04-10 04:30 | 168.92 | 162.2
2018-04-10 05:00 | 168.57 | 161.93
2018-04-10 05:30 | 168.78 | 162.44
2018-04-10 06:00 | 171.82 | 165.12
2018-04-10 06:30 | 174.73 | 167.46
2018-04-10 07:00 | 174.87 | 167.16
2018-04-10 07:30 | 175.17 | 167.78
2018-04-10 08:00 | 175.77 | 168.11
2018-04-10 08:30 | 174.75 | 166.95
2018-04-10 09:00 | 174.99 | 167.21
2018-04-10 09:30 | 175.85 | 168.19
2018-04-10 10:00 | 179.02 | 171.75
2018-04-10 10:30 | 179.1 | 171.87
2018-04-10 11:00 | 179.98 | 172.99
2018-04-10 11:30 | 180.03 | 173.03
2018-04-10 12:00 | 180.66 | 173.7
2018-04-10 12:30 | 181.48 | 174.46
2018-04-10 13:00 | 181.85 | 174.72
2018-04-10 13:30 | 181.33 | 174.05
2018-04-10 14:00 | 210.82 | 204.08
2018-04-10 14:30 | 240.58 | 234.12
2018-04-10 15:00 | 246.37 | 239.96
2018-04-10 15:30 | 248.99 | 242.55
2018-04-10 16:00 | 251.42 | 245.04
2018-04-10 16:30 | 252.43 | 245.87
2018-04-10 17:00 | 253.16 | 246.83
2018-04-10 17:30 | 254.96 | 248.88
2018-04-10 18:00 | 257.25 | 251.33
2018-04-10 18:30 | 259.43 | 253.29
2018-04-10 19:00 | 257.11 | 250.08
2018-04-10 19:30 | 252.94 | 244.93
2018-04-10 20:00 | 250.53 | 242.31
2018-04-10 20:30 | 248.07 | 239.34
2018-04-10 21:00 | 246.33 | 237.19
2018-04-10 21:30 | 244.53 | 235.85
2018-04-10 22:00 | 241.92 | 233.38
2018-04-10 22:30 | 239.53 | 230.85
2018-04-10 23:00 | 238.38 | 229.34
2018-04-10 23:30 | 237.03 | 228.1
2018-04-11 | 234.87 | 225.85
2018-04-11 00:30 | 236.43 | 227.6
2018-04-11 01:00 | 217.37 | 209.36
2018-04-11 01:30 | 179.3 | 170.77
2018-04-11 02:00 | 170.77 | 162.14
2018-04-11 02:30 | 170.88 | 161.95
2018-04-11 03:00 | 170.41 | 161.41
2018-04-11 03:30 | 170.02 | 161.05
2018-04-11 04:00 | 169.87 | 160.87
2018-04-11 04:30 | 170.21 | 161.1
2018-04-11 05:00 | 170.55 | 161.49
2018-04-11 05:30 | 171.33 | 162.54
2018-04-11 06:00 | 172.79 | 163.88
2018-04-11 06:30 | 174.75 | 165.42
2018-04-11 07:00 | 176.48 | 166.19
2018-04-11 07:30 | 205.28 | 195.38
2018-04-11 08:00 | 215.44 | 206.13
2018-04-11 08:30 | 232.4 | 223.29
2018-04-11 09:00 | 237.85 | 228.78
2018-04-11 09:30 | 237.96 | 228.7
2018-04-11 10:00 | 237.9 | 228.75
2018-04-11 10:30 | 237.64 | 228.63
2018-04-11 11:00 | 237.07 | 228
2018-04-11 11:30 | 236.91 | 227.98
2018-04-11 12:00 | 237.89 | 228.91
2018-04-11 12:30 | 238 | 228.82
2018-04-11 13:00 | 239.55 | 230.33
2018-04-11 13:30 | 240.16 | 231.49
2018-04-11 14:00 | 240.71 | 232.67
2018-04-11 14:30 | 241.18 | 232.91
2018-04-11 15:00 | 242.52 | 233.91
2018-04-11 15:30 | 243.86 | 234.87
2018-04-11 16:00 | 245.04 | 235.99
2018-04-11 16:30 | 246.26 | 237.34
2018-04-11 17:00 | 245.41 | 236.03
2018-04-11 17:30 | 245.58 | 235.79
2018-04-11 18:00 | 248.02 | 238.57
2018-04-11 18:30 | 250.34 | 240.93
2018-04-11 19:00 | 251.67 | 242.29
2018-04-11 19:30 | 247.7 | 240.02
2018-04-11 20:00 | 245.03 | 237.41
2018-04-11 20:30 | 243.54 | 235.62
2018-04-11 21:00 | 241.86 | 233.8
2018-04-11 21:30 | 239.49 | 232.57
2018-04-11 22:00 | 237.21 | 230.18
2018-04-11 22:30 | 235.63 | 228.18
2018-04-11 23:00 | 234.29 | 226.62
2018-04-11 23:30 | 213.46 | 206.06
2018-04-12 | 176.51 | 169.07
2018-04-12 00:30 | 168.61 | 160.9
2018-04-12 01:00 | 167.6 | 159.68
2018-04-12 01:30 | 165.82 | 158.88
2018-04-12 02:00 | 164.6 | 158.2
2018-04-12 02:30 | 163.81 | 157.58
2018-04-12 03:00 | 163.97 | 157.12
2018-04-12 03:30 | 164.21 | 157.2
2018-04-12 04:00 | 163.82 | 156.9
2018-04-12 04:30 | 164.01 | 156.87
2018-04-12 05:00 | 164.23 | 157.12
2018-04-12 05:30 | 165.34 | 158.35
2018-04-12 06:00 | 167.13 | 159.8
2018-04-12 06:30 | 169.32 | 161.4
2018-04-12 07:00 | 170.49 | 162.36
2018-04-12 07:30 | 170.58 | 162.47
2018-04-12 08:00 | 169.45 | 161.4
2018-04-12 08:30 | 170.2 | 161.99
2018-04-12 09:00 | 169.55 | 161.26
2018-04-12 09:30 | 169.35 | 161.07
2018-04-12 10:00 | 195.47 | 187.24
2018-04-12 10:30 | 223.18 | 215.04
2018-04-12 11:00 | 229.79 | 221.86
2018-04-12 11:30 | 230.15 | 222.14
2018-04-12 12:00 | 229.8 | 221.66
2018-04-12 12:30 | 229.62 | 221.5
2018-04-12 13:00 | 230.61 | 222.46
2018-04-12 13:30 | 232.77 | 224.67
2018-04-12 14:00 | 233.69 | 226.03
2018-04-12 14:30 | 233.83 | 226.15
2018-04-12 15:00 | 234.96 | 227.26
2018-04-12 15:30 | 236.35 | 228.85
2018-04-12 16:00 | 237.01 | 229.86
2018-04-12 16:30 | 237.95 | 230.89
2018-04-12 17:00 | 239.08 | 231.91
2018-04-12 17:30 | 239.11 | 232.14
2018-04-12 18:00 | 240.6 | 233.62
2018-04-12 18:30 | 243.08 | 235.96
2018-04-12 19:00 | 244.48 | 237.21
2018-04-12 19:30 | 242.76 | 235.1
2018-04-12 20:00 | 240.66 | 232.87
2018-04-12 20:30 | 238.71 | 230.68
2018-04-12 21:00 | 236.57 | 228.59
2018-04-12 21:30 | 234.6 | 227.09
2018-04-12 22:00 | 233.11 | 225.94
2018-04-12 22:30 | 230.78 | 223.67
2018-04-12 23:00 | 230.09 | 222.11
2018-04-12 23:30 | 229.05 | 221.45
2018-04-13 | 227.4 | 220.14
2018-04-13 00:30 | 206.89 | 199.87
2018-04-13 01:00 | 171.68 | 164.85
2018-04-13 01:30 | 162.97 | 156.37
2018-04-13 02:00 | 162.72 | 155.98
2018-04-13 02:30 | 161.95 | 155.35
2018-04-13 03:00 | 162.34 | 155.36
2018-04-13 03:30 | 162.48 | 155.34
2018-04-13 04:00 | 162.27 | 155.17
2018-04-13 04:30 | 162.4 | 155.74
2018-04-13 05:00 | 162.64 | 155.93
2018-04-13 05:30 | 163.29 | 156.88
2018-04-13 06:00 | 166.33 | 159.14
2018-04-13 06:30 | 168.08 | 160.65
2018-04-13 07:00 | 169.25 | 162.02
2018-04-13 07:30 | 169.98 | 162.88
2018-04-13 08:00 | 198.21 | 191.11
2018-04-13 08:30 | 207.54 | 200.49
2018-04-13 09:00 | 207.09 | 200.09
2018-04-13 09:30 | 206.16 | 198.89
2018-04-13 10:00 | 207.09 | 200
2018-04-13 10:30 | 207.15 | 200.01
2018-04-13 11:00 | 208.02 | 201.1
2018-04-13 11:30 | 208.48 | 201.57
2018-04-13 12:00 | 226.02 | 219.24
2018-04-13 12:30 | 232.82 | 226
2018-04-13 13:00 | 233.37 | 226.35
2018-04-13 13:30 | 234.97 | 228.15
2018-04-13 14:00 | 236.31 | 229.6
2018-04-13 14:30 | 236.84 | 229.95
2018-04-13 15:00 | 237.22 | 229.9
2018-04-13 15:30 | 237.85 | 230.62
2018-04-13 16:00 | 239.15 | 232.03
2018-04-13 16:30 | 238.89 | 231.9
2018-04-13 17:00 | 239.29 | 232.19
2018-04-13 17:30 | 238.92 | 231.65
2018-04-13 18:00 | 238.88 | 231.69
2018-04-13 18:30 | 240.58 | 233.67
2018-04-13 19:00 | 240.7 | 233.75
2018-04-13 19:30 | 239.4 | 232.03
2018-04-13 20:00 | 237.54 | 230.03
2018-04-13 20:30 | 236.73 | 229.23
2018-04-13 21:00 | 235.03 | 227.3
2018-04-13 21:30 | 234.12 | 227.43
2018-04-13 22:00 | 233.29 | 226.5
2018-04-13 22:30 | 231.67 | 224.75
2018-04-13 23:00 | 230.02 | 222.93
2018-04-13 23:30 | 212 | 204.63
2018-04-14 | 175.58 | 168.37
2018-04-14 00:30 | 165.92 | 158.87
2018-04-14 01:00 | 165.71 | 158.29
2018-04-14 01:30 | 165.64 | 158.01
2018-04-14 02:00 | 165.14 | 157.21
2018-04-14 02:30 | 165.12 | 157.1
2018-04-14 03:00 | 164.26 | 157.07
2018-04-14 03:30 | 164.28 | 157.08
2018-04-14 04:00 | 164.67 | 157.21
2018-04-14 04:30 | 164.48 | 157.06
2018-04-14 05:00 | 164.95 | 157.53
2018-04-14 05:30 | 164.67 | 157.26
2018-04-14 06:00 | 165.43 | 158.26
2018-04-14 06:30 | 166.25 | 158.87
2018-04-14 07:00 | 164.99 | 157.73
2018-04-14 07:30 | 164.7 | 157.68
2018-04-14 08:00 | 165.34 | 157.95
2018-04-14 08:30 | 165.42 | 157.98
2018-04-14 09:00 | 165.59 | 157.3
2018-04-14 09:30 | 164.88 | 155.91
2018-04-14 10:00 | 165.37 | 156.79
2018-04-14 10:30 | 164.4 | 156.06
2018-04-14 11:00 | 164.53 | 156.81
2018-04-14 11:30 | 164.72 | 156.92
2018-04-14 12:00 | 164.03 | 156.4
2018-04-14 12:30 | 165.17 | 157.55
2018-04-14 13:00 | 195.23 | 187.95
2018-04-14 13:30 | 221.67 | 214.33
2018-04-14 14:00 | 224.89 | 217.53
2018-04-14 14:30 | 224.52 | 216.99
2018-04-14 15:00 | 226.85 | 219.3
2018-04-14 15:30 | 228.51 | 221.1
2018-04-14 16:00 | 229.17 | 221.56
2018-04-14 16:30 | 230.29 | 222.62
2018-04-14 17:00 | 231.05 | 223.25
2018-04-14 17:30 | 233.23 | 224.77
2018-04-14 18:00 | 234.48 | 226.33
2018-04-14 18:30 | 235.96 | 227.95
2018-04-14 19:00 | 236.61 | 228.21
2018-04-14 19:30 | 235.6 | 226.91
2018-04-14 20:00 | 233.7 | 224.98
2018-04-14 20:30 | 232.45 | 223.57
2018-04-14 21:00 | 231.18 | 222.03
2018-04-14 21:30 | 197.21 | 187.66
2018-04-14 22:00 | 168.54 | 159.8
2018-04-14 22:30 | 166.88 | 158.13
2018-04-14 23:00 | 166.3 | 157.16
2018-04-14 23:30 | 164.81 | 155.94
2018-04-15 | 163.4 | 155.01
2018-04-15 00:30 | 162.3 | 154.25
2018-04-15 01:00 | 161.11 | 153.5
2018-04-15 01:30 | 160.7 | 152.99
2018-04-15 02:00 | 159.99 | 152.18
2018-04-15 02:30 | 159.91 | 152.07
2018-04-15 03:00 | 159.18 | 151.61
2018-04-15 03:30 | 159.01 | 151.35
2018-04-15 04:00 | 158.71 | 151.1
2018-04-15 04:30 | 158.98 | 151.25
2018-04-15 05:00 | 159.16 | 151.4
2018-04-15 05:30 | 159.79 | 152.05
2018-04-15 06:00 | 160.29 | 152.66
2018-04-15 06:30 | 160.96 | 153.37
2018-04-15 07:00 | 160.8 | 153.33
2018-04-15 07:30 | 158.81 | 151.57
2018-04-15 08:00 | 159.12 | 151.61
2018-04-15 08:30 | 159.18 | 151.48
2018-04-15 09:00 | 158.61 | 150.73
2018-04-15 09:30 | 157.82 | 149.9
2018-04-15 10:00 | 157.3 | 149.26
2018-04-15 10:30 | 157.51 | 149.24
2018-04-15 11:00 | 157.6 | 149.31
2018-04-15 11:30 | 158.23 | 149.82
2018-04-15 12:00 | 159.05 | 150.22
2018-04-15 12:30 | 160.29 | 151.42
2018-04-15 13:00 | 162.48 | 152.06
2018-04-15 13:30 | 163.34 | 152.52
2018-04-15 14:00 | 164.25 | 153.69
2018-04-15 14:30 | 164.84 | 154.08
2018-04-15 15:00 | 165.62 | 155.11
2018-04-15 15:30 | 167.48 | 157.09
2018-04-15 16:00 | 168.43 | 158.32
2018-04-15 16:30 | 197.81 | 187.99
2018-04-15 17:00 | 224.19 | 214.56
2018-04-15 17:30 | 231.89 | 222.28
2018-04-15 18:00 | 233.52 | 224.21
2018-04-15 18:30 | 234.61 | 225.41
2018-04-15 19:00 | 235.82 | 226.6
2018-04-15 19:30 | 234.67 | 225
2018-04-15 20:00 | 232.97 | 223.03
2018-04-15 20:30 | 231.13 | 221.54
2018-04-15 21:00 | 228.01 | 219.82
2018-04-15 21:30 | 208.21 | 200.69
2018-04-15 22:00 | 170.03 | 162.47
2018-04-15 22:30 | 160.25 | 152.94
2018-04-15 23:00 | 158.8 | 151.21
2018-04-15 23:30 | 157.38 | 150.29
2018-04-16 | 156.14 | 149.12
2018-04-16 00:30 | 155.62 | 148.47
2018-04-16 01:00 | 154.8 | 148.05
2018-04-16 01:30 | 154.27 | 147.62
2018-04-16 02:00 | 153.65 | 146.9
2018-04-16 02:30 | 153.25 | 146.32
2018-04-16 03:00 | 152.84 | 146.12
2018-04-16 03:30 | 152.55 | 145.89
2018-04-16 04:00 | 152.77 | 146.18
2018-04-16 04:30 | 153.01 | 146.48
2018-04-16 05:00 | 153.65 | 147.35
2018-04-16 05:30 | 154.68 | 148.55
2018-04-16 06:00 | 155.77 | 150.16
2018-04-16 06:30 | 159.33 | 153.46
2018-04-16 07:00 | 163.38 | 157.21
2018-04-16 07:30 | 165.75 | 159.22
2018-04-16 08:00 | 166.75 | 160.14
2018-04-16 08:30 | 165.9 | 159.15
2018-04-16 09:00 | 164.98 | 157.91
2018-04-16 09:30 | 163.21 | 156
2018-04-16 10:00 | 163.96 | 156.93
2018-04-16 10:30 | 164.35 | 157.13
2018-04-16 11:00 | 164.31 | 157.1
2018-04-16 11:30 | 164.78 | 157.5
2018-04-16 12:00 | 166.21 | 158.31
2018-04-16 12:30 | 195.04 | 187.71
2018-04-16 13:00 | 222.37 | 216.01
2018-04-16 13:30 | 229.77 | 223.3
2018-04-16 14:00 | 230.77 | 224.43
2018-04-16 14:30 | 231.52 | 225.08
2018-04-16 15:00 | 231.7 | 225.17
2018-04-16 15:30 | 230.82 | 224.08
2018-04-16 16:00 | 233.37 | 225.87
2018-04-16 16:30 | 234.82 | 227.21
2018-04-16 17:00 | 235.61 | 227.93
2018-04-16 17:30 | 235.95 | 228.11
2018-04-16 18:00 | 238.39 | 230.71
2018-04-16 18:30 | 241.08 | 233.68
2018-04-16 19:00 | 242.03 | 234.4
2018-04-16 19:30 | 239.96 | 231.94
2018-04-16 20:00 | 238.2 | 230.3
2018-04-16 20:30 | 237.47 | 229.63
2018-04-16 21:00 | 237.84 | 230.2
2018-04-16 21:30 | 236.97 | 230.01
2018-04-16 22:00 | 235.97 | 228.98
2018-04-16 22:30 | 234.39 | 227.46
2018-04-16 23:00 | 232.97 | 225.74
2018-04-16 23:30 | 213.15 | 206.33
2018-04-17 | 174.3 | 167.55
2018-04-17 00:30 | 165.57 | 158.56
2018-04-17 01:00 | 164.34 | 157.25
2018-04-17 01:30 | 164.85 | 157.22
2018-04-17 02:00 | 164.89 | 157.14
2018-04-17 02:30 | 165 | 157.51
2018-04-17 03:00 | 164.26 | 156.73
2018-04-17 03:30 | 164.44 | 156.85
2018-04-17 04:00 | 164.94 | 157.12
2018-04-17 04:30 | 164.94 | 157.49
2018-04-17 05:00 | 165.57 | 158.28
2018-04-17 05:30 | 166.08 | 158.93
2018-04-17 06:00 | 169.42 | 161.95
2018-04-17 06:30 | 172.84 | 164.84
2018-04-17 07:00 | 173.26 | 165.01
2018-04-17 07:30 | 174.78 | 166.49
2018-04-17 08:00 | 174.29 | 165.88
2018-04-17 08:30 | 172.66 | 164.08
2018-04-17 09:00 | 171.96 | 163.27
2018-04-17 09:30 | 171.24 | 162.48
2018-04-17 10:00 | 171.87 | 163.14
2018-04-17 10:30 | 171.72 | 163
2018-04-17 11:00 | 171.23 | 162.85
2018-04-17 11:30 | 170.96 | 162.73
2018-04-17 12:00 | 171.07 | 162.95
2018-04-17 12:30 | 172.2 | 163.98
2018-04-17 13:00 | 173.6 | 165.66
2018-04-17 13:30 | 174.08 | 166.59
2018-04-17 14:00 | 202.36 | 195.48
2018-04-17 14:30 | 232.4 | 225.7
2018-04-17 15:00 | 239.16 | 232.38
2018-04-17 15:30 | 240.97 | 233.99
2018-04-17 16:00 | 241.92 | 234.99
2018-04-17 16:30 | 244.13 | 237.09
2018-04-17 17:00 | 245.8 | 238.75
2018-04-17 17:30 | 244.13 | 237.33
2018-04-17 18:00 | 232.55 | 230.08
2018-04-17 18:30 | 230.96 | 228.36
2018-04-17 19:00 | 232.36 | 229.75
2018-04-17 19:30 | 235.22 | 232.73
2018-04-17 20:00 | 241.58 | 235.47
2018-04-17 20:30 | 245.13 | 237.67
2018-04-17 21:00 | 242.8 | 235.31
2018-04-17 21:30 | 241.72 | 234.74
2018-04-17 22:00 | 240.06 | 233.22
2018-04-17 22:30 | 237.54 | 230.67
2018-04-17 23:00 | 235.83 | 228.57
2018-04-17 23:30 | 234.61 | 227.45
2018-04-18 | 214.89 | 207.77
2018-04-18 00:30 | 176.44 | 168.85
2018-04-18 01:00 | 166.36 | 158.65
2018-04-18 01:30 | 165.65 | 158.08
2018-04-18 02:00 | 165.13 | 157.89
2018-04-18 02:30 | 165.31 | 157.89
2018-04-18 03:00 | 165.2 | 157.7
2018-04-18 03:30 | 165.21 | 157.66
2018-04-18 04:00 | 165.42 | 157.82
2018-04-18 04:30 | 166.02 | 158.53
2018-04-18 05:00 | 166.59 | 159.08
2018-04-18 05:30 | 167.86 | 160.08
2018-04-18 06:00 | 170.86 | 162.24
2018-04-18 06:30 | 173.76 | 164.98
2018-04-18 07:00 | 175.19 | 165.91
2018-04-18 07:30 | 176.39 | 167.73
2018-04-18 08:00 | 175.37 | 166.74
2018-04-18 08:30 | 174.28 | 165.77
2018-04-18 09:00 | 172.34 | 164.16
2018-04-18 09:30 | 171.3 | 163.03
2018-04-18 10:00 | 171.3 | 162.92
2018-04-18 10:30 | 171.78 | 163.42
2018-04-18 11:00 | 171.64 | 163.58
2018-04-18 11:30 | 172.36 | 164.41
2018-04-18 12:00 | 173.9 | 166.02
2018-04-18 12:30 | 174.64 | 166.53
2018-04-18 13:00 | 176.76 | 169.06
2018-04-18 13:30 | 178.88 | 171.27
2018-04-18 14:00 | 180.29 | 173.13
2018-04-18 14:30 | 180.26 | 173.36
2018-04-18 15:00 | 181.01 | 174.16
2018-04-18 15:30 | 180.85 | 173.87
2018-04-18 16:00 | 182.02 | 175.19
2018-04-18 16:30 | 213.44 | 206.74
2018-04-18 17:00 | 240.16 | 233.71
2018-04-18 17:30 | 245.61 | 238.91
2018-04-18 18:00 | 247 | 240.49
2018-04-18 18:30 | 249.75 | 243.44
2018-04-18 19:00 | 250.82 | 244.18
2018-04-18 19:30 | 248.43 | 241.71
2018-04-18 20:00 | 246.8 | 239.98
2018-04-18 20:30 | 244.4 | 237.35
2018-04-18 21:00 | 222.69 | 214.34
2018-04-18 21:30 | 235.52 | 228.88
2018-04-18 22:00 | 229.96 | 227.17
2018-04-18 22:30 | 239.9 | 238
2018-04-18 23:00 | 241.18 | 239.32
2018-04-18 23:30 | 241.74 | 239.99
2018-04-19 | 232.65 | 227.61
2018-04-19 00:30 | 214.72 | 208.71
2018-04-19 01:00 | 176.11 | 170.17
2018-04-19 01:30 | 167.1 | 161.33
2018-04-19 02:00 | 166.4 | 160.2
2018-04-19 02:30 | 166.15 | 160.18
2018-04-19 03:00 | 165.57 | 159.79
2018-04-19 03:30 | 165.78 | 159.67
2018-04-19 04:00 | 166.18 | 159.8
2018-04-19 04:30 | 166.88 | 160.44
2018-04-19 05:00 | 167.5 | 160.95
2018-04-19 05:30 | 166.15 | 159.74
2018-04-19 06:00 | 168.44 | 161.56
2018-04-19 06:30 | 170.65 | 163.71
2018-04-19 07:00 | 177.2 | 170.16
2018-04-19 07:30 | 224.96 | 218.33
2018-04-19 08:00 | 236.61 | 230.18
2018-04-19 08:30 | 235.89 | 229.12
2018-04-19 09:00 | 236.25 | 229.02
2018-04-19 09:30 | 236.69 | 229.32
2018-04-19 10:00 | 236.4 | 229.12
2018-04-19 10:30 | 236.49 | 229.16
2018-04-19 11:00 | 236.6 | 229.41
2018-04-19 11:30 | 238.24 | 230.97
2018-04-19 12:00 | 239.2 | 232
2018-04-19 12:30 | 238.68 | 231.41
2018-04-19 13:00 | 239.25 | 232.09
2018-04-19 13:30 | 239.57 | 232.47
2018-04-19 14:00 | 239.49 | 232.56
2018-04-19 14:30 | 239.94 | 233.55
2018-04-19 15:00 | 239.21 | 232.93
2018-04-19 15:30 | 237.79 | 231.46
2018-04-19 16:00 | 236.97 | 230.8
2018-04-19 16:30 | 237.72 | 235.8
2018-04-19 17:00 | 238.12 | 236.42
2018-04-19 17:30 | 237.52 | 235.75
2018-04-19 18:00 | 235.41 | 233.36
2018-04-19 18:30 | 233.69 | 231.58
2018-04-19 19:00 | 234.26 | 231.98
2018-04-19 19:30 | 237.04 | 234.55
2018-04-19 20:00 | 239.43 | 237.09
2018-04-19 20:30 | 239.89 | 237.69
2018-04-19 21:00 | 240.66 | 238.6
2018-04-19 21:30 | 240.68 | 238.98
2018-04-19 22:00 | 241 | 239.69
2018-04-19 22:30 | 242.24 | 240.98
2018-04-19 23:00 | 243.99 | 242.47
2018-04-19 23:30 | 244.05 | 242.63
2018-04-20 | 246.77 | 245.39
2018-04-20 00:30 | 246.89 | 245.66
2018-04-20 01:00 | 229.88 | 225.04
2018-04-20 01:30 | 211.4 | 205.26
2018-04-20 02:00 | 173.89 | 167.56
2018-04-20 02:30 | 165 | 158.52
2018-04-20 03:00 | 164.4 | 158.14
2018-04-20 03:30 | 165.72 | 159.13
2018-04-20 04:00 | 165.67 | 158.69
2018-04-20 04:30 | 164.74 | 157.34
2018-04-20 05:00 | 166.12 | 158.93
2018-04-20 05:30 | 167.58 | 160.71
2018-04-20 06:00 | 169.04 | 162.29
2018-04-20 06:30 | 186.15 | 179.65
2018-04-20 07:00 | 228.24 | 221.98
2018-04-20 07:30 | 236.6 | 230.67
2018-04-20 08:00 | 236.38 | 230.84
2018-04-20 08:30 | 234.64 | 229.19
2018-04-20 09:00 | 234.13 | 228.56
2018-04-20 09:30 | 233.88 | 228.31
2018-04-20 10:00 | 232.28 | 226.9
2018-04-20 10:30 | 213.4 | 208.06
2018-04-20 11:00 | 176.44 | 171.02
2018-04-20 11:30 | 168.82 | 163.13
2018-04-20 12:00 | 169.34 | 163.85
2018-04-20 12:30 | 169.49 | 164.41
2018-04-20 13:00 | 193.26 | 188.12
2018-04-20 13:30 | 224.83 | 220.46
2018-04-20 14:00 | 235.36 | 234.01
2018-04-20 14:30 | 235 | 233.61
2018-04-20 15:00 | 234.78 | 233.48
2018-04-20 15:30 | 234.65 | 233.34
2018-04-20 16:00 | 234.64 | 233.3
2018-04-20 16:30 | 235.85 | 234.59
2018-04-20 17:00 | 235.18 | 233.49
2018-04-20 17:30 | 235.75 | 233.69
2018-04-20 18:00 | 235.66 | 233.66
2018-04-20 18:30 | 235.23 | 233.2
2018-04-20 19:00 | 235.83 | 233.51
2018-04-20 19:30 | 237.66 | 235.2
2018-04-20 20:00 | 239.05 | 236.82
2018-04-20 20:30 | 240.01 | 237.94
2018-04-20 21:00 | 241.8 | 239.73
2018-04-20 21:30 | 241.87 | 240.1
2018-04-20 22:00 | 243.11 | 241.18
2018-04-20 22:30 | 244.49 | 242.41
2018-04-20 23:00 | 245.68 | 243.52
2018-04-20 23:30 | 246.48 | 244.54
2018-04-21 | 231.92 | 226.35
2018-04-21 00:30 | 230.65 | 224.01
2018-04-21 01:00 | 229.48 | 223.02
2018-04-21 01:30 | 229.26 | 222.95
2018-04-21 02:00 | 229.08 | 222.54
2018-04-21 02:30 | 209.92 | 203.36
2018-04-21 03:00 | 173.08 | 166.45
2018-04-21 03:30 | 163.04 | 156.23
2018-04-21 04:00 | 163.13 | 156.41
2018-04-21 04:30 | 162.54 | 155.78
2018-04-21 05:00 | 163.96 | 157.57
2018-04-21 05:30 | 163.51 | 157.06
2018-04-21 06:00 | 164.65 | 158.39
2018-04-21 06:30 | 166.32 | 159.62
2018-04-21 07:00 | 165.66 | 159.4
2018-04-21 07:30 | 162.56 | 156.59
2018-04-21 08:00 | 163.01 | 156.36
2018-04-21 08:30 | 163.04 | 156.65
2018-04-21 09:00 | 162.66 | 156.25
2018-04-21 09:30 | 161.82 | 155.31
2018-04-21 10:00 | 164.76 | 158.15
2018-04-21 10:30 | 165.14 | 158.79
2018-04-21 11:00 | 164.91 | 158.3
2018-04-21 11:30 | 165.01 | 158.4
2018-04-21 12:00 | 165.68 | 159.13
2018-04-21 12:30 | 165.75 | 158.65
2018-04-21 13:00 | 166.34 | 159.33
2018-04-21 13:30 | 167.43 | 160.56
2018-04-21 14:00 | 167.07 | 160.29
2018-04-21 14:30 | 168.77 | 161.75
2018-04-21 15:00 | 199.76 | 192.65
2018-04-21 15:30 | 226.49 | 219.87
2018-04-21 16:00 | 233.55 | 226.56
2018-04-21 16:30 | 235.46 | 228.29
2018-04-21 17:00 | 236.68 | 229.75
2018-04-21 17:30 | 238.06 | 231.02
2018-04-21 18:00 | 239.76 | 232.72
2018-04-21 18:30 | 241.85 | 234.75
2018-04-21 19:00 | 242.3 | 235.1
2018-04-21 19:30 | 241.7 | 234.28
2018-04-21 20:00 | 239.92 | 232.39
2018-04-21 20:30 | 238.06 | 230.52
2018-04-21 21:00 | 236.79 | 229.41
2018-04-21 21:30 | 235.35 | 228.6
2018-04-21 22:00 | 234.43 | 228.06
2018-04-21 22:30 | 233.3 | 226.63
2018-04-21 23:00 | 231.86 | 225.24
2018-04-21 23:30 | 230.98 | 224.8
2018-04-22 | 229.84 | 223.93
2018-04-22 00:30 | 228.77 | 223.31
2018-04-22 01:00 | 227.87 | 222.5
2018-04-22 01:30 | 227.31 | 222.04
2018-04-22 02:00 | 227.07 | 221.45
2018-04-22 02:30 | 227.14 | 221.4
2018-04-22 03:00 | 208.21 | 202.73
2018-04-22 03:30 | 170.5 | 165
2018-04-22 04:00 | 161.85 | 156.29
2018-04-22 04:30 | 161.67 | 156.09
2018-04-22 05:00 | 161.97 | 156.32
2018-04-22 05:30 | 161.94 | 156.26
2018-04-22 06:00 | 163.17 | 157.62
2018-04-22 06:30 | 164.22 | 158.65
2018-04-22 07:00 | 163.92 | 158.32
2018-04-22 07:30 | 164.6 | 159.22
2018-04-22 08:00 | 163.86 | 158.42
2018-04-22 08:30 | 164.27 | 158.68
2018-04-22 09:00 | 163.34 | 157.84
2018-04-22 09:30 | 163.36 | 157.53
2018-04-22 10:00 | 163.62 | 157.3
2018-04-22 10:30 | 162.66 | 156.52
2018-04-22 11:00 | 163.84 | 157.49
2018-04-22 11:30 | 163.97 | 157.51
2018-04-22 12:00 | 164.97 | 158.41
2018-04-22 12:30 | 164.85 | 158.26
2018-04-22 13:00 | 165.12 | 158.47
2018-04-22 13:30 | 164.5 | 158.11
2018-04-22 14:00 | 165.95 | 159.4
2018-04-22 14:30 | 167.89 | 161.23
2018-04-22 15:00 | 198.21 | 191.97
2018-04-22 15:30 | 226.88 | 220.57
2018-04-22 16:00 | 234.15 | 227.94
2018-04-22 16:30 | 235.83 | 229.36
2018-04-22 17:00 | 236.56 | 229.67
2018-04-22 17:30 | 237.38 | 230.31
2018-04-22 18:00 | 239.38 | 232.65
2018-04-22 18:30 | 236.14 | 232.65
2018-04-22 19:00 | 240.72 | 238.42
2018-04-22 19:30 | 241.95 | 239.66
2018-04-22 20:00 | 243.85 | 241.68
2018-04-22 20:30 | 245.94 | 243.96
2018-04-22 21:00 | 247.11 | 245.2
2018-04-22 21:30 | 235.08 | 229.69
2018-04-22 22:00 | 233.91 | 227.27
2018-04-22 22:30 | 231.95 | 225.32
2018-04-22 23:00 | 230.63 | 224.04
2018-04-22 23:30 | 230.31 | 223.82
2018-04-23 | 228.86 | 222.86
2018-04-23 00:30 | 208.92 | 203.09
2018-04-23 01:00 | 170.32 | 164.41
2018-04-23 01:30 | 160.71 | 154.65
2018-04-23 02:00 | 160.2 | 153.83
2018-04-23 02:30 | 159.95 | 153.53
2018-04-23 03:00 | 160.22 | 153.87
2018-04-23 03:30 | 159.71 | 153.29
2018-04-23 04:00 | 159.59 | 153.06
2018-04-23 04:30 | 160.92 | 154.01
2018-04-23 05:00 | 161.14 | 153.9
2018-04-23 05:30 | 161.66 | 155.16
2018-04-23 06:00 | 193.87 | 187.78
2018-04-23 06:30 | 225.85 | 219.79
2018-04-23 07:00 | 237.45 | 230.31
2018-04-23 07:30 | 239.58 | 232.09
2018-04-23 08:00 | 238.29 | 230.83
2018-04-23 08:30 | 237.15 | 229.54
2018-04-23 09:00 | 235.49 | 227.78
2018-04-23 09:30 | 232.59 | 224.75
2018-04-23 10:00 | 232.62 | 224.79
2018-04-23 10:30 | 217.02 | 209.44
2018-04-23 11:00 | 212.6 | 205.25
2018-04-23 11:30 | 211.88 | 204.48
2018-04-23 12:00 | 212.57 | 205.15
2018-04-23 12:30 | 212.18 | 204.52
2018-04-23 13:00 | 211.77 | 204.08
2018-04-23 13:30 | 211.35 | 203.5
2018-04-23 14:00 | 212.6 | 205.08
2018-04-23 14:30 | 231.65 | 224.25
2018-04-23 15:00 | 235.78 | 228.18
2018-04-23 15:30 | 236.02 | 228.33
2018-04-23 16:00 | 238.78 | 231.02
2018-04-23 16:30 | 240.13 | 232.31
2018-04-23 17:00 | 241.15 | 233.4
2018-04-23 17:30 | 240.93 | 233.06
2018-04-23 18:00 | 242.99 | 235.35
2018-04-23 18:30 | 244.68 | 236.45
2018-04-23 19:00 | 243.17 | 234.39
2018-04-23 19:30 | 240.12 | 231.02
2018-04-23 20:00 | 238.06 | 228.9
2018-04-23 20:30 | 236.82 | 227.6
2018-04-23 21:00 | 236 | 226.67
2018-04-23 21:30 | 235.72 | 227.47
2018-04-23 22:00 | 233.59 | 225.37
2018-04-23 22:30 | 231.44 | 223.32
2018-04-23 23:00 | 229.72 | 221.74
2018-04-23 23:30 | 228.6 | 220.84
2018-04-24 | 226.68 | 220.09
2018-04-24 00:30 | 206.91 | 200.88
2018-04-24 01:00 | 167.73 | 161.94
2018-04-24 01:30 | 158.9 | 152.74
2018-04-24 02:00 | 158.39 | 151.68
2018-04-24 02:30 | 158.58 | 151.73
2018-04-24 03:00 | 158.68 | 152.04
2018-04-24 03:30 | 158.54 | 151.97
2018-04-24 04:00 | 158.56 | 152.02
2018-04-24 04:30 | 158.51 | 151.75
2018-04-24 05:00 | 160.52 | 154
2018-04-24 05:30 | 160.25 | 153.79
2018-04-24 06:00 | 163.23 | 156.14
2018-04-24 06:30 | 166.67 | 158.94
2018-04-24 07:00 | 169.28 | 160.88
2018-04-24 07:30 | 170.66 | 162.62
2018-04-24 08:00 | 170.04 | 162.01
2018-04-24 08:30 | 167.78 | 159.37
2018-04-24 09:00 | 166.02 | 157.52
2018-04-24 09:30 | 165.57 | 157.39
2018-04-24 10:00 | 165.76 | 158.24
2018-04-24 10:30 | 165.02 | 157.67
2018-04-24 11:00 | 165.88 | 158.45
2018-04-24 11:30 | 166.77 | 159.52
2018-04-24 12:00 | 166.8 | 159.28
2018-04-24 12:30 | 167.81 | 159.95
2018-04-24 13:00 | 169.65 | 161.78
2018-04-24 13:30 | 169.24 | 161.97
2018-04-24 14:00 | 170.5 | 163.18
2018-04-24 14:30 | 171.66 | 163.84
2018-04-24 15:00 | 200.62 | 193.15
2018-04-24 15:30 | 226.65 | 219.28
2018-04-24 16:00 | 237.68 | 230.26
2018-04-24 16:30 | 239.61 | 232.33
2018-04-24 17:00 | 240.98 | 233.38
2018-04-24 17:30 | 240.54 | 232.91
2018-04-24 18:00 | 239.4 | 233.65
2018-04-24 18:30 | 238.51 | 235.33
2018-04-24 19:00 | 238.8 | 235.46
2018-04-24 19:30 | 240.93 | 237.46
2018-04-24 20:00 | 242.03 | 238.71
2018-04-24 20:30 | 243.1 | 239.79
2018-04-24 21:00 | 243.19 | 241.29
2018-04-24 21:30 | 235.53 | 230.99
2018-04-24 22:00 | 235.9 | 230.41
2018-04-24 22:30 | 234.51 | 228.93
2018-04-24 23:00 | 233.06 | 227.95
2018-04-24 23:30 | 231.78 | 227.11
2018-04-25 | 230.75 | 226.29
2018-04-25 00:30 | 230.02 | 225.41
2018-04-25 01:00 | 230.26 | 224.64
2018-04-25 01:30 | 230.48 | 224.56
2018-04-25 02:00 | 229.93 | 224.09
2018-04-25 02:30 | 230.13 | 224.21
2018-04-25 03:00 | 208.62 | 202.6
2018-04-25 03:30 | 171.22 | 165.07
2018-04-25 04:00 | 163.27 | 157.29
2018-04-25 04:30 | 163.48 | 157.45
2018-04-25 05:00 | 163.28 | 157.25
2018-04-25 05:30 | 163.69 | 157.47
2018-04-25 06:00 | 163.77 | 157.4
2018-04-25 06:30 | 164.48 | 158.2
2018-04-25 07:00 | 165.14 | 158.66
2018-04-25 07:30 | 163.98 | 157.91
2018-04-25 08:00 | 165.78 | 158.33
2018-04-25 08:30 | 163.97 | 156.91
2018-04-25 09:00 | 163.48 | 156.66
2018-04-25 09:30 | 162.21 | 155.48
2018-04-25 10:00 | 160.98 | 154.5
2018-04-25 10:30 | 161.09 | 154.06
2018-04-25 11:00 | 161.97 | 154.75
2018-04-25 11:30 | 162.57 | 155.39
2018-04-25 12:00 | 162.7 | 155.34
2018-04-25 12:30 | 162.79 | 155.3
2018-04-25 13:00 | 165.41 | 156.96
2018-04-25 13:30 | 165.24 | 156.98
2018-04-25 14:00 | 166.73 | 158.58
2018-04-25 14:30 | 167.52 | 159.17
2018-04-25 15:00 | 196.42 | 188.44
2018-04-25 15:30 | 224.93 | 216.93
2018-04-25 16:00 | 234.4 | 226.31
2018-04-25 16:30 | 237.14 | 229.07
2018-04-25 17:00 | 238.03 | 230.12
2018-04-25 17:30 | 240.07 | 232.03
2018-04-25 18:00 | 241.77 | 234.75
2018-04-25 18:30 | 242.56 | 236.71
2018-04-25 19:00 | 242.41 | 236.24
2018-04-25 19:30 | 240.64 | 234.29
2018-04-25 20:00 | 238.5 | 232.39
2018-04-25 20:30 | 237.29 | 231.17
2018-04-25 21:00 | 215.7 | 209.74
2018-04-25 21:30 | 177.77 | 172.67
2018-04-25 22:00 | 168.42 | 163.21
2018-04-25 22:30 | 167.16 | 161.52
2018-04-25 23:00 | 166.14 | 160.66
2018-04-25 23:30 | 165.23 | 159.66
2018-04-26 | 164.85 | 159.28
2018-04-26 00:30 | 164.69 | 158.99
2018-04-26 01:00 | 163.77 | 158.19
2018-04-26 01:30 | 163.22 | 157.64
2018-04-26 02:00 | 162.92 | 157.28
2018-04-26 02:30 | 162.18 | 156.52
2018-04-26 03:00 | 161.85 | 156.19
2018-04-26 03:30 | 162.75 | 157.01
2018-04-26 04:00 | 162.3 | 156.61
2018-04-26 04:30 | 162.7 | 157.1
2018-04-26 05:00 | 163.66 | 157.87
2018-04-26 05:30 | 165.11 | 159.42
2018-04-26 06:00 | 168.4 | 162.39
2018-04-26 06:30 | 172.35 | 165.83
2018-04-26 07:00 | 201.86 | 195.85
2018-04-26 07:30 | 232.46 | 226.55
2018-04-26 08:00 | 239.64 | 233.59
2018-04-26 08:30 | 238.91 | 233.4
2018-04-26 09:00 | 237.1 | 231.46
2018-04-26 09:30 | 235.1 | 229.21
2018-04-26 10:00 | 235.07 | 228.58
2018-04-26 10:30 | 233.44 | 226.84
2018-04-26 11:00 | 234.05 | 227.69
2018-04-26 11:30 | 233.78 | 227.65
2018-04-26 12:00 | 233.72 | 227.76
2018-04-26 12:30 | 234.21 | 228.18
2018-04-26 13:00 | 235.2 | 229.19
2018-04-26 13:30 | 235.93 | 229.65
2018-04-26 14:00 | 236.3 | 229.67
2018-04-26 14:30 | 236.69 | 230.09
2018-04-26 15:00 | 237.25 | 230.18
2018-04-26 15:30 | 237.57 | 230.41
2018-04-26 16:00 | 239.05 | 231.94
2018-04-26 16:30 | 239.75 | 232.56
2018-04-26 17:00 | 240.42 | 233.27
2018-04-26 17:30 | 231.68 | 224.93
2018-04-26 18:00 | 223.78 | 219.37
2018-04-26 18:30 | 236.89 | 233.66
2018-04-26 19:00 | 237.16 | 233.91
2018-04-26 19:30 | 239.35 | 236.33
2018-04-26 20:00 | 241.37 | 238.52
2018-04-26 20:30 | 242.55 | 239.87
2018-04-26 21:00 | 245.03 | 242.43
2018-04-26 21:30 | 245.32 | 242.73
2018-04-26 22:00 | 245.71 | 243.17
2018-04-26 22:30 | 246.79 | 244.42
2018-04-26 23:00 | 248.18 | 245.94
2018-04-26 23:30 | 248.35 | 246.39
2018-04-27 | 231.72 | 226.29
2018-04-27 00:30 | 216.73 | 209.48
2018-04-27 01:00 | 180.15 | 173.08
2018-04-27 01:30 | 163.55 | 157.14
2018-04-27 02:00 | 163.25 | 157.06
2018-04-27 02:30 | 162.99 | 156.68
2018-04-27 03:00 | 162.7 | 156.34
2018-04-27 03:30 | 161.74 | 155.55
2018-04-27 04:00 | 162.66 | 156.73
2018-04-27 04:30 | 163.2 | 157.08
2018-04-27 05:00 | 164.98 | 158.25
2018-04-27 05:30 | 166.81 | 160.11
2018-04-27 06:00 | 169.61 | 162.67
2018-04-27 06:30 | 172.84 | 165.29
2018-04-27 07:00 | 202.53 | 195.18
2018-04-27 07:30 | 231.42 | 224.85
2018-04-27 08:00 | 238.45 | 232.19
2018-04-27 08:30 | 237.2 | 231.28
2018-04-27 09:00 | 238.55 | 233.22
2018-04-27 09:30 | 237.37 | 231.91
2018-04-27 10:00 | 235.79 | 230.47
2018-04-27 10:30 | 233.87 | 227.96
2018-04-27 11:00 | 232.81 | 226.69
2018-04-27 11:30 | 232.72 | 226.28
2018-04-27 12:00 | 234.13 | 227.4
2018-04-27 12:30 | 234.03 | 226.81
2018-04-27 13:00 | 233.86 | 226.62
2018-04-27 13:30 | 234.69 | 227.56
2018-04-27 14:00 | 235.35 | 227.96
2018-04-27 14:30 | 234.99 | 227.43
2018-04-27 15:00 | 236.14 | 228.29
2018-04-27 15:30 | 237.28 | 229.39
2018-04-27 16:00 | 239.44 | 232.18
2018-04-27 16:30 | 240.46 | 233.3
2018-04-27 17:00 | 241.2 | 233.9
2018-04-27 17:30 | 242.75 | 235.35
2018-04-27 18:00 | 241.48 | 237.42
2018-04-27 18:30 | 244.51 | 242.19
2018-04-27 19:00 | 245.96 | 243.53
2018-04-27 19:30 | 247.45 | 245.06
2018-04-27 20:00 | 248.89 | 246.57
2018-04-27 20:30 | 249.99 | 247.74
2018-04-27 21:00 | 250.55 | 248.4
2018-04-27 21:30 | 239.14 | 233.05
2018-04-27 22:00 | 241.76 | 233.85
2018-04-27 22:30 | 239.06 | 231.94
2018-04-27 23:00 | 236.56 | 228.93
2018-04-27 23:30 | 235.27 | 228.14
2018-04-28 | 234.54 | 227.45
2018-04-28 00:30 | 234.41 | 227.76
2018-04-28 01:00 | 216.76 | 211.11
2018-04-28 01:30 | 180.5 | 174.49
2018-04-28 02:00 | 165.74 | 159.72
2018-04-28 02:30 | 165.37 | 159.19
2018-04-28 03:00 | 165.63 | 159.15
2018-04-28 03:30 | 165.88 | 159.12
2018-04-28 04:00 | 165.4 | 158.69
2018-04-28 04:30 | 165.65 | 158.9
2018-04-28 05:00 | 166.2 | 159.22
2018-04-28 05:30 | 166.75 | 160.4
2018-04-28 06:00 | 167.61 | 161.49
2018-04-28 06:30 | 169.39 | 162.89
2018-04-28 07:00 | 170.17 | 163.68
2018-04-28 07:30 | 167.67 | 161.92
2018-04-28 08:00 | 198.73 | 193.23
2018-04-28 08:30 | 226.22 | 219.43
2018-04-28 09:00 | 232.66 | 225.83
2018-04-28 09:30 | 231.16 | 224.6
2018-04-28 10:00 | 230.96 | 224.17
2018-04-28 10:30 | 231.05 | 223.68
2018-04-28 11:00 | 230.68 | 223.28
2018-04-28 11:30 | 230.66 | 222.78
2018-04-28 12:00 | 229.68 | 221.81
2018-04-28 12:30 | 229.88 | 222.07
2018-04-28 13:00 | 231.32 | 223.26
2018-04-28 13:30 | 232.28 | 224.23
2018-04-28 14:00 | 233.02 | 224.87
2018-04-28 14:30 | 233.65 | 225.2
2018-04-28 15:00 | 234.5 | 226.02
2018-04-28 15:30 | 234.88 | 226.42
2018-04-28 16:00 | 236.65 | 228.07
2018-04-28 16:30 | 238.36 | 229.88
2018-04-28 17:00 | 239.4 | 231.2
2018-04-28 17:30 | 240.65 | 232.7
2018-04-28 18:00 | 242.87 | 235.03
2018-04-28 18:30 | 245.24 | 237.07
2018-04-28 19:00 | 246.22 | 237.82
2018-04-28 19:30 | 244.57 | 236.03
2018-04-28 20:00 | 240.95 | 234.15
2018-04-28 20:30 | 239.26 | 232.39
2018-04-28 21:00 | 237.82 | 230.84
2018-04-28 21:30 | 237.54 | 231.05
2018-04-28 22:00 | 237.35 | 231.14
2018-04-28 22:30 | 235.72 | 229.68
2018-04-28 23:00 | 233.25 | 228.03
2018-04-28 23:30 | 216.38 | 211.23
2018-04-29 | 179.79 | 174.48
2018-04-29 00:30 | 164.26 | 158.41
2018-04-29 01:00 | 163.72 | 157.87
2018-04-29 01:30 | 162.28 | 156.49
2018-04-29 02:00 | 162.47 | 156.67
2018-04-29 02:30 | 162.23 | 156.43
2018-04-29 03:00 | 161.59 | 155.86
2018-04-29 03:30 | 161.18 | 155.47
2018-04-29 04:00 | 161.07 | 155.4
2018-04-29 04:30 | 160.66 | 155.03
2018-04-29 05:00 | 160.37 | 154.83
2018-04-29 05:30 | 161.24 | 155.66
2018-04-29 06:00 | 161.51 | 155.92
2018-04-29 06:30 | 162.84 | 157.38
2018-04-29 07:00 | 161.99 | 156.53
2018-04-29 07:30 | 159.87 | 154.41
2018-04-29 08:00 | 160.51 | 154.9
2018-04-29 08:30 | 160.19 | 154.06
2018-04-29 09:00 | 159.31 | 153.11
2018-04-29 09:30 | 158.17 | 152.33
2018-04-29 10:00 | 156.16 | 150.46
2018-04-29 10:30 | 155.12 | 149.37
2018-04-29 11:00 | 155.11 | 149.43
2018-04-29 11:30 | 156.8 | 149.65
2018-04-29 12:00 | 157.52 | 150.38
2018-04-29 12:30 | 158.1 | 151.05
2018-04-29 13:00 | 157.71 | 150.65
2018-04-29 13:30 | 158.34 | 151.07
2018-04-29 14:00 | 158.83 | 151.6
2018-04-29 14:30 | 159.86 | 151.7
2018-04-29 15:00 | 161.08 | 152.56
2018-04-29 15:30 | 160.45 | 151.75
2018-04-29 16:00 | 161.95 | 153.1
2018-04-29 16:30 | 190.68 | 182.06
2018-04-29 17:00 | 220 | 211.88
2018-04-29 17:30 | 231.16 | 223.08
2018-04-29 18:00 | 234.57 | 225.99
2018-04-29 18:30 | 235.27 | 228.15
2018-04-29 19:00 | 234.73 | 227.63
2018-04-29 19:30 | 233.64 | 226.13
2018-04-29 20:00 | 232.53 | 224.96
2018-04-29 20:30 | 231.39 | 223.66
2018-04-29 21:00 | 230.28 | 222.57
2018-04-29 21:30 | 229.4 | 222.99
2018-04-29 22:00 | 228.4 | 221.98
2018-04-29 22:30 | 226.71 | 220.41
2018-04-29 23:00 | 206.34 | 200.68
2018-04-29 23:30 | 170.43 | 164.72
2018-04-30 | 153.94 | 148.07
2018-04-30 00:30 | 153.45 | 147.59
2018-04-30 01:00 | 152.52 | 146.73
2018-04-30 01:30 | 152.4 | 146.56
2018-04-30 02:00 | 151.48 | 145.51
2018-04-30 02:30 | 151.77 | 145.83
2018-04-30 03:00 | 150.89 | 144.95
2018-04-30 03:30 | 151.07 | 145.14
2018-04-30 04:00 | 151.05 | 145.15
2018-04-30 04:30 | 151.66 | 145.81
2018-04-30 05:00 | 153.16 | 147.4
2018-04-30 05:30 | 154.79 | 148.92
2018-04-30 06:00 | 156.26 | 150.35
2018-04-30 06:30 | 193.28 | 187.62
2018-04-30 07:00 | 224.33 | 218.85
2018-04-30 07:30 | 236.45 | 230.39
2018-04-30 08:00 | 236.39 | 229.92
2018-04-30 08:30 | 233.58 | 227.39
2018-04-30 09:00 | 231.64 | 225.85
2018-04-30 09:30 | 232.74 | 226.92
2018-04-30 10:00 | 234.6 | 228.61
2018-04-30 10:30 | 233.38 | 226.62
2018-04-30 11:00 | 233.44 | 226.02
2018-04-30 11:30 | 235.09 | 225.84
2018-04-30 12:00 | 235.88 | 226.69
2018-04-30 12:30 | 235.67 | 226.33
2018-04-30 13:00 | 237.31 | 227.97
2018-04-30 13:30 | 237.55 | 228.23
2018-04-30 14:00 | 238.6 | 229.65
2018-04-30 14:30 | 238.32 | 229.41
2018-04-30 15:00 | 238.03 | 229.09
2018-04-30 15:30 | 238.68 | 229.83
2018-04-30 16:00 | 240.12 | 231.35
2018-04-30 16:30 | 241.5 | 232.84
2018-04-30 17:00 | 243.42 | 234.89
2018-04-30 17:30 | 244.2 | 239.94
2018-04-30 18:00 | 246.98 | 243.43
2018-04-30 18:30 | 245.86 | 241.88
2018-04-30 19:00 | 246.63 | 242.73
2018-04-30 19:30 | 250.14 | 246.05
2018-04-30 20:00 | 249.83 | 246.48
2018-04-30 20:30 | 244.72 | 236.82
2018-04-30 21:00 | 245.33 | 235.88
2018-04-30 21:30 | 243.52 | 234.84
2018-04-30 22:00 | 242.44 | 234.04
2018-04-30 22:30 | 239.64 | 232.02
2018-04-30 23:00 | 238.72 | 230.74
2018-04-30 23:30 | 237.02 | 229.47
2018-05-01 | 235.58 | 228.57
2018-05-01 00:30 | 212.44 | 205.46
2018-05-01 01:00 | 176.52 | 169.02
2018-05-01 01:30 | 167.5 | 159.88
2018-05-01 02:00 | 167.31 | 158.99
2018-05-01 02:30 | 166.86 | 157.83
2018-05-01 03:00 | 166.62 | 157.44
2018-05-01 03:30 | 167.57 | 158.3
2018-05-01 04:00 | 168.12 | 158.71
2018-05-01 04:30 | 168.56 | 159.21
2018-05-01 05:00 | 168.65 | 159.23
2018-05-01 05:30 | 170.25 | 161.1
2018-05-01 06:00 | 172.53 | 163.2
2018-05-01 06:30 | 175.66 | 166.44
2018-05-01 07:00 | 177.85 | 167.21
2018-05-01 07:30 | 209.97 | 199.91
2018-05-01 08:00 | 238.39 | 228.29
2018-05-01 08:30 | 242.43 | 232.29
2018-05-01 09:00 | 239.73 | 229.22
2018-05-01 09:30 | 238.63 | 228.14
2018-05-01 10:00 | 240.02 | 229.83
2018-05-01 10:30 | 222.14 | 211.87
2018-05-01 11:00 | 184.86 | 173.98
2018-05-01 11:30 | 174.1 | 162.55
2018-05-01 12:00 | 174.16 | 162.83
2018-05-01 12:30 | 173.88 | 162.65
2018-05-01 13:00 | 173.59 | 163.17
2018-05-01 13:30 | 173.78 | 163.57
2018-05-01 14:00 | 175.96 | 165.02
2018-05-01 14:30 | 177.52 | 165.9
2018-05-01 15:00 | 177.82 | 166.05
2018-05-01 15:30 | 179.37 | 167.68
2018-05-01 16:00 | 210.32 | 199.62
2018-05-01 16:30 | 239 | 228.52
2018-05-01 17:00 | 245.88 | 235.18
2018-05-01 17:30 | 247.33 | 236.17
2018-05-01 18:00 | 246.74 | 240.29
2018-05-01 18:30 | 247.73 | 242.63
2018-05-01 19:00 | 247.99 | 242.91
2018-05-01 19:30 | 250 | 239.59
2018-05-01 20:00 | 252.78 | 241
2018-05-01 20:30 | 258.18 | 249.57
2018-05-01 21:00 | 220.55 | 211.74
2018-05-01 21:30 | 208.93 | 201.03
2018-05-01 22:00 | 208.2 | 200.42
2018-05-01 22:30 | 206.95 | 199.44
2018-05-01 23:00 | 205.87 | 198.28
2018-05-01 23:30 | 203.86 | 196.83
2018-05-02 | 202.13 | 195.47
2018-05-02 00:30 | 201.86 | 195.34
2018-05-02 01:00 | 201.26 | 194.23
2018-05-02 01:30 | 200.5 | 193.73
2018-05-02 02:00 | 199.15 | 192.45
2018-05-02 02:30 | 198.49 | 191.62
2018-05-02 03:00 | 198.34 | 191.6
2018-05-02 03:30 | 197.68 | 190.93
2018-05-02 04:00 | 197.42 | 190.68
2018-05-02 04:30 | 198.78 | 192.05
2018-05-02 05:00 | 198.82 | 192.16
2018-05-02 05:30 | 200.58 | 193.92
2018-05-02 06:00 | 203.1 | 195.56
2018-05-02 06:30 | 206.94 | 198.38
2018-05-02 07:00 | 209.38 | 201.14
2018-05-02 07:30 | 210.33 | 203.25
2018-05-02 08:00 | 210.83 | 203.27
2018-05-02 08:30 | 208.2 | 200.52
2018-05-02 09:00 | 205.13 | 197.16
2018-05-02 09:30 | 202.62 | 194.51
2018-05-02 10:00 | 202.26 | 194.09
2018-05-02 10:30 | 201.46 | 194.87
2018-05-02 11:00 | 198.93 | 195.13
2018-05-02 11:30 | 194.95 | 190.5
2018-05-02 12:00 | 184.73 | 178.11
2018-05-02 12:30 | 181.96 | 174.79
2018-05-02 13:00 | 180.31 | 173.05
2018-05-02 13:30 | 178.8 | 171.13
2018-05-02 14:00 | 179.59 | 172.07
2018-05-02 14:30 | 181.02 | 173.47
2018-05-02 15:00 | 179.32 | 173.48
2018-05-02 15:30 | 210.01 | 204.29
2018-05-02 16:00 | 238.64 | 232.92
2018-05-02 16:30 | 243.01 | 237.04
2018-05-02 17:00 | 242.24 | 236.23
2018-05-02 17:30 | 242.19 | 235.49
2018-05-02 18:00 | 243.43 | 236.26
2018-05-02 18:30 | 246.45 | 239.27
2018-05-02 19:00 | 246.83 | 239.49
2018-05-02 19:30 | 244.5 | 237.28
2018-05-02 20:00 | 242.19 | 234.97
2018-05-02 20:30 | 242.23 | 234.88
2018-05-02 21:00 | 241.63 | 233.94
2018-05-02 21:30 | 222.17 | 215.02
2018-05-02 22:00 | 182.63 | 175.16
2018-05-02 22:30 | 171.99 | 164.8
2018-05-02 23:00 | 169.76 | 163.45
2018-05-02 23:30 | 170.86 | 164.84
2018-05-03 | 169 | 162.6
2018-05-03 00:30 | 167.85 | 161.76
2018-05-03 01:00 | 167.44 | 161.8
2018-05-03 01:30 | 166.69 | 160.74
2018-05-03 02:00 | 166.37 | 160.31
2018-05-03 02:30 | 165.99 | 159.72
2018-05-03 03:00 | 166.86 | 160.58
2018-05-03 03:30 | 167.22 | 160.94
2018-05-03 04:00 | 166.67 | 160.39
2018-05-03 04:30 | 164.81 | 158.62
2018-05-03 05:00 | 165.17 | 159.15
2018-05-03 05:30 | 167.1 | 161.4
2018-05-03 06:00 | 168.62 | 162.81
2018-05-03 06:30 | 171.88 | 165.92
2018-05-03 07:00 | 175.11 | 168.32
2018-05-03 07:30 | 177.37 | 170.13
2018-05-03 08:00 | 176.64 | 167.74
2018-05-03 08:30 | 175.81 | 166.93
2018-05-03 09:00 | 174.5 | 165.37
2018-05-03 09:30 | 173.42 | 164.23
2018-05-03 10:00 | 172.93 | 163.64
2018-05-03 10:30 | 172.19 | 162.64
2018-05-03 11:00 | 170.59 | 161.64
2018-05-03 11:30 | 170.66 | 161.82
2018-05-03 12:00 | 171.38 | 162.69
2018-05-03 12:30 | 172.71 | 163.92
2018-05-03 13:00 | 174.28 | 165.46
2018-05-03 13:30 | 174.96 | 166.1
2018-05-03 14:00 | 175.01 | 166.19
2018-05-03 14:30 | 176.75 | 167.38
2018-05-03 15:00 | 175.72 | 166.26
2018-05-03 15:30 | 174.74 | 165.22
2018-05-03 16:00 | 165.34 | 157.28
2018-05-03 16:30 | 207.68 | 198.74
2018-05-03 17:00 | 236.36 | 227.44
2018-05-03 17:30 | 241.54 | 232.55
2018-05-03 18:00 | 242.03 | 234.05
2018-05-03 18:30 | 245.44 | 237.86
2018-05-03 19:00 | 245.57 | 238.72
2018-05-03 19:30 | 244.45 | 237.41
2018-05-03 20:00 | 244.59 | 237.91
2018-05-03 20:30 | 243.97 | 237.16
2018-05-03 21:00 | 243.07 | 236.36
2018-05-03 21:30 | 224.52 | 218.6
2018-05-03 22:00 | 184.61 | 178.62
2018-05-03 22:30 | 175 | 169.02
2018-05-03 23:00 | 172.27 | 166.08
2018-05-03 23:30 | 171.63 | 165.25
2018-05-04 | 170.9 | 165.02
2018-05-04 00:30 | 170.14 | 164.22
2018-05-04 01:00 | 169.94 | 163.65
2018-05-04 01:30 | 167.33 | 161.19
2018-05-04 02:00 | 166.44 | 160.18
2018-05-04 02:30 | 166.77 | 160.26
2018-05-04 03:00 | 167.45 | 160.77
2018-05-04 03:30 | 167.54 | 160.88
2018-05-04 04:00 | 167.75 | 161.09
2018-05-04 04:30 | 168.75 | 162.24
2018-05-04 05:00 | 168.64 | 162.37
2018-05-04 05:30 | 170 | 163.96
2018-05-04 06:00 | 171.5 | 165.55
2018-05-04 06:30 | 175.62 | 168.48
2018-05-04 07:00 | 179.4 | 171.5
2018-05-04 07:30 | 191.85 | 182.41
2018-05-04 08:00 | 180.68 | 172.3
2018-05-04 08:30 | 179.81 | 171.34
2018-05-04 09:00 | 178.4 | 169.84
2018-05-04 09:30 | 176.45 | 167.75
2018-05-04 10:00 | 176.33 | 167.6
2018-05-04 10:30 | 176.66 | 167.74
2018-05-04 11:00 | 175.9 | 167.18
2018-05-04 11:30 | 174.45 | 165.73
2018-05-04 12:00 | 175.65 | 166.98
2018-05-04 12:30 | 176.69 | 167.76
2018-05-04 13:00 | 172.21 | 163.1
2018-05-04 13:30 | 163.7 | 154.67
2018-05-04 14:00 | 158.28 | 149.23
2018-05-04 14:30 | 156.86 | 147.76
2018-05-04 15:00 | 156.8 | 147.9
2018-05-04 15:30 | 157.22 | 148.42
2018-05-04 16:00 | 157.45 | 148.59
2018-05-04 16:30 | 184.78 | 176.06
2018-05-04 17:00 | 213.09 | 204.79
2018-05-04 17:30 | 226.58 | 218.27
2018-05-04 18:00 | 237.17 | 228.92
2018-05-04 18:30 | 231.88 | 223.64
2018-05-04 19:00 | 224.68 | 216.36
2018-05-04 19:30 | 224.09 | 215.52
2018-05-04 20:00 | 222.63 | 213.9
2018-05-04 20:30 | 221.74 | 212.85
2018-05-04 21:00 | 220.28 | 211.17
2018-05-04 21:30 | 203.07 | 194.66
2018-05-04 22:00 | 163.47 | 154.45
2018-05-04 22:30 | 153.12 | 143.5
2018-05-04 23:00 | 152.02 | 142.44
2018-05-04 23:30 | 150.93 | 141.41
2018-05-05 | 159.91 | 150.83
2018-05-05 00:30 | 166.76 | 158.35
2018-05-05 01:00 | 167.66 | 160.05
2018-05-05 01:30 | 165.54 | 158.16
2018-05-05 02:00 | 164.02 | 156.73
2018-05-05 02:30 | 164.09 | 156.75
2018-05-05 03:00 | 163.71 | 156.18
2018-05-05 03:30 | 163.34 | 155.79
2018-05-05 04:00 | 163.03 | 155.62
2018-05-05 04:30 | 163.78 | 156.33
2018-05-05 05:00 | 164.2 | 156.73
2018-05-05 05:30 | 164.2 | 156.79
2018-05-05 06:00 | 165.74 | 158.49
2018-05-05 06:30 | 164.41 | 156.95
2018-05-05 07:00 | 166.05 | 158.75
2018-05-05 07:30 | 165.55 | 158.59
2018-05-05 08:00 | 165.03 | 158.39
2018-05-05 08:30 | 164.73 | 158.45
2018-05-05 09:00 | 163.64 | 157.05
2018-05-05 09:30 | 164.03 | 157.51
2018-05-05 10:00 | 163.12 | 156.46
2018-05-05 10:30 | 161.88 | 155.13
2018-05-05 11:00 | 161.7 | 154.58
2018-05-05 11:30 | 161.59 | 153.97
2018-05-05 12:00 | 161.33 | 153.46
2018-05-05 12:30 | 160.88 | 152.75
2018-05-05 13:00 | 161.74 | 153.29
2018-05-05 13:30 | 161.01 | 152.53
2018-05-05 14:00 | 161.29 | 152.78
2018-05-05 14:30 | 161.28 | 152.85
2018-05-05 15:00 | 162.6 | 154.25
2018-05-05 15:30 | 163.89 | 155.8
2018-05-05 16:00 | 164.63 | 156.81
2018-05-05 16:30 | 166.72 | 158.95
2018-05-05 17:00 | 199.61 | 192.35
2018-05-05 17:30 | 229.42 | 221.77
2018-05-05 18:00 | 240.21 | 232.65
2018-05-05 18:30 | 243.17 | 235.44
2018-05-05 19:00 | 243.16 | 235.24
2018-05-05 19:30 | 242.11 | 234.05
2018-05-05 20:00 | 240.76 | 232.87
2018-05-05 20:30 | 239.43 | 231.31
2018-05-05 21:00 | 238.69 | 230.39
2018-05-05 21:30 | 218.37 | 210.43
2018-05-05 22:00 | 177.76 | 170.12
2018-05-05 22:30 | 167.19 | 159.5
2018-05-05 23:00 | 165.52 | 157.78
2018-05-05 23:30 | 165.76 | 158.13
2018-05-06 | 163.95 | 156.83
2018-05-06 00:30 | 163.39 | 156.51
2018-05-06 01:00 | 163.06 | 156.19
2018-05-06 01:30 | 160.54 | 154.33
2018-05-06 02:00 | 160.85 | 154.46
2018-05-06 02:30 | 161.23 | 154.76
2018-05-06 03:00 | 160.69 | 154.28
2018-05-06 03:30 | 160.29 | 153.99
2018-05-06 04:00 | 160.71 | 154.58
2018-05-06 04:30 | 160.12 | 153.96
2018-05-06 05:00 | 160.49 | 154.15
2018-05-06 05:30 | 161.13 | 154.79
2018-05-06 06:00 | 160.33 | 154.08
2018-05-06 06:30 | 161.01 | 154.92
2018-05-06 07:00 | 161.76 | 155.96
2018-05-06 07:30 | 162.37 | 156.72
2018-05-06 08:00 | 162.16 | 156.6
2018-05-06 08:30 | 162.82 | 157.25
2018-05-06 09:00 | 161.07 | 155.42
2018-05-06 09:30 | 159.53 | 153.84
2018-05-06 10:00 | 160.31 | 154.6
2018-05-06 10:30 | 159.97 | 154.34
2018-05-06 11:00 | 160.12 | 154.59
2018-05-06 11:30 | 159.41 | 153.87
2018-05-06 12:00 | 159.31 | 153.72
2018-05-06 12:30 | 160.13 | 154.14
2018-05-06 13:00 | 159.53 | 153.6
2018-05-06 13:30 | 189.87 | 184
2018-05-06 14:00 | 217.96 | 212.38
2018-05-06 14:30 | 225.67 | 220.09
2018-05-06 15:00 | 226.53 | 220.85
2018-05-06 15:30 | 227.49 | 221.95
2018-05-06 16:00 | 228.45 | 222.76
2018-05-06 16:30 | 229.68 | 223.93
2018-05-06 17:00 | 231.45 | 225.61
2018-05-06 17:30 | 231.42 | 224.97
2018-05-06 18:00 | 233.19 | 226.92
2018-05-06 18:30 | 235.37 | 229.06
2018-05-06 19:00 | 235.92 | 229.37
2018-05-06 19:30 | 235.42 | 228.6
2018-05-06 20:00 | 234.86 | 228.11
2018-05-06 20:30 | 234.22 | 227.49
2018-05-06 21:00 | 233.8 | 226.8
2018-05-06 21:30 | 234.28 | 227.51
2018-05-06 22:00 | 233.6 | 226.87
2018-05-06 22:30 | 231.54 | 225.18
2018-05-06 23:00 | 230.65 | 224.19
2018-05-06 23:30 | 229.88 | 223.68
2018-05-07 | 228.87 | 222.61
2018-05-07 00:30 | 228.74 | 222.59
2018-05-07 01:00 | 227.29 | 221.66
2018-05-07 01:30 | 226.33 | 220.74
2018-05-07 02:00 | 226.11 | 220.56
2018-05-07 02:30 | 225.56 | 220.15
2018-05-07 03:00 | 226.77 | 220.17
2018-05-07 03:30 | 226.65 | 220.06
2018-05-07 04:00 | 226.89 | 220.29
2018-05-07 04:30 | 226.94 | 220.28
2018-05-07 05:00 | 227.04 | 220.46
2018-05-07 05:30 | 226.98 | 220.41
2018-05-07 06:00 | 227.58 | 221.05
2018-05-07 06:30 | 228.73 | 222.49
2018-05-07 07:00 | 230.85 | 224.06
2018-05-07 07:30 | 232.77 | 225.51
2018-05-07 08:00 | 232.29 | 225.23
2018-05-07 08:30 | 215.02 | 207.74
2018-05-07 09:00 | 176.18 | 168.59
2018-05-07 09:30 | 166.75 | 159.11
2018-05-07 10:00 | 166.43 | 158.93
2018-05-07 10:30 | 165.02 | 156.62
2018-05-07 11:00 | 163.8 | 153.57
2018-05-07 11:30 | 163.66 | 153.02
2018-05-07 12:00 | 164.7 | 154.1
2018-05-07 12:30 | 165.12 | 154.67
2018-05-07 13:00 | 166.47 | 156.28
2018-05-07 13:30 | 166.92 | 156.63
2018-05-07 14:00 | 167.79 | 157.61
2018-05-07 14:30 | 167.52 | 157.45
2018-05-07 15:00 | 168.06 | 157.83
2018-05-07 15:30 | 167.33 | 156.43
2018-05-07 16:00 | 168.53 | 158.21
2018-05-07 16:30 | 169.82 | 159.69
2018-05-07 17:00 | 171.54 | 161.34
2018-05-07 17:30 | 174.1 | 164.58
2018-05-07 18:00 | 175.37 | 165.93
2018-05-07 18:30 | 177.85 | 168.62
2018-05-07 19:00 | 177.54 | 168.11
2018-05-07 19:30 | 176.64 | 166.92
2018-05-07 20:00 | 174.55 | 164.76
2018-05-07 20:30 | 173.81 | 163.65
2018-05-07 21:00 | 172.17 | 161.99
2018-05-07 21:30 | 171.92 | 162.09
2018-05-07 22:00 | 170.16 | 160.67
2018-05-07 22:30 | 168.77 | 159.03
2018-05-07 23:00 | 168.54 | 158.22
2018-05-07 23:30 | 168.17 | 157.62
2018-05-08 | 164.72 | 155.41
2018-05-08 00:30 | 164.49 | 155.24
2018-05-08 01:00 | 163.52 | 154.48
2018-05-08 01:30 | 163.4 | 154.15
2018-05-08 02:00 | 163.8 | 154.23
2018-05-08 02:30 | 163.51 | 154
2018-05-08 03:00 | 162.83 | 153.42
2018-05-08 03:30 | 162.88 | 153.45
2018-05-08 04:00 | 162.33 | 153.07
2018-05-08 04:30 | 164.21 | 154.94
2018-05-08 05:00 | 163.99 | 154.6
2018-05-08 05:30 | 165.83 | 156.43
2018-05-08 06:00 | 168.15 | 158.97
2018-05-08 06:30 | 173.36 | 164.78
2018-05-08 07:00 | 176.54 | 167.24
2018-05-08 07:30 | 179.96 | 170.49
2018-05-08 08:00 | 177.35 | 168.79
2018-05-08 08:30 | 174.89 | 166.34
2018-05-08 09:00 | 173.27 | 164.7
2018-05-08 09:30 | 172.18 | 163.64
2018-05-08 10:00 | 172.24 | 164.06
2018-05-08 10:30 | 200.78 | 192.85
2018-05-08 11:00 | 224.89 | 217
2018-05-08 11:30 | 232.57 | 224.37
2018-05-08 12:00 | 233.34 | 225.02
2018-05-08 12:30 | 232.46 | 224.12
2018-05-08 13:00 | 233.51 | 224.98
2018-05-08 13:30 | 237.22 | 228.55
2018-05-08 14:00 | 233.39 | 225.26
2018-05-08 14:30 | 235.58 | 227.08
2018-05-08 15:00 | 235.37 | 226.74
2018-05-08 15:30 | 235.42 | 226.78
2018-05-08 16:00 | 235.91 | 227.87
2018-05-08 16:30 | 237.39 | 229.36
2018-05-08 17:00 | 239.1 | 230.87
2018-05-08 17:30 | 239.65 | 231.12
2018-05-08 18:00 | 237.05 | 232.83
2018-05-08 18:30 | 239.06 | 235.72
2018-05-08 19:00 | 240.36 | 237.03
2018-05-08 19:30 | 241.8 | 238.53
2018-05-08 20:00 | 243.42 | 240.1
2018-05-08 20:30 | 239.93 | 231.33
2018-05-08 21:00 | 240.98 | 230.48
2018-05-08 21:30 | 222.65 | 212.97
2018-05-08 22:00 | 183.96 | 174.42
2018-05-08 22:30 | 172.29 | 162.37
2018-05-08 23:00 | 171.42 | 161.06
2018-05-08 23:30 | 170.94 | 160.69
2018-05-09 | 170.06 | 159.6
2018-05-09 00:30 | 169.33 | 159.47
2018-05-09 01:00 | 168.65 | 158.79
2018-05-09 01:30 | 167.9 | 157.88
2018-05-09 02:00 | 167.61 | 157.59
2018-05-09 02:30 | 166.74 | 157.02
2018-05-09 03:00 | 166.22 | 156.16
2018-05-09 03:30 | 166.59 | 156.74
2018-05-09 04:00 | 167.1 | 157.42
2018-05-09 04:30 | 167.37 | 157.78
2018-05-09 05:00 | 168.56 | 158.79
2018-05-09 05:30 | 169.46 | 159.98
2018-05-09 06:00 | 171.39 | 161.91
2018-05-09 06:30 | 175.69 | 166.88
2018-05-09 07:00 | 177.27 | 168.18
2018-05-09 07:30 | 179.31 | 170.26
2018-05-09 08:00 | 179.02 | 169.96
2018-05-09 08:30 | 177.89 | 168.47
2018-05-09 09:00 | 174.71 | 165.31
2018-05-09 09:30 | 173.02 | 163.75
2018-05-09 10:00 | 171.19 | 161.85
2018-05-09 10:30 | 170.03 | 160.73
2018-05-09 11:00 | 170.29 | 161.03
2018-05-09 11:30 | 169.54 | 160.37
2018-05-09 12:00 | 170.63 | 161.92
2018-05-09 12:30 | 170.12 | 161.32
2018-05-09 13:00 | 171.32 | 162.54
2018-05-09 13:30 | 171.06 | 162.17
2018-05-09 14:00 | 171.87 | 163.17
2018-05-09 14:30 | 171.71 | 163.2
2018-05-09 15:00 | 172.02 | 163.56
2018-05-09 15:30 | 173.22 | 164.7
2018-05-09 16:00 | 173.8 | 165.34
2018-05-09 16:30 | 205.68 | 197.47
2018-05-09 17:00 | 233.49 | 225.61
2018-05-09 17:30 | 236.97 | 232.68
2018-05-09 18:00 | 239.69 | 237.02
2018-05-09 18:30 | 239.6 | 236.8
2018-05-09 19:00 | 241.17 | 238.38
2018-05-09 19:30 | 243.58 | 240.88
2018-05-09 20:00 | 244.93 | 242.34
2018-05-09 20:30 | 246.25 | 243.64
2018-05-09 21:00 | 246.82 | 244.16
2018-05-09 21:30 | 239.21 | 232.09
2018-05-09 22:00 | 219.4 | 210.52
2018-05-09 22:30 | 179.12 | 169.14
2018-05-09 23:00 | 170.18 | 159.83
2018-05-09 23:30 | 169.15 | 158.83
2018-05-10 | 167.64 | 157.77
2018-05-10 00:30 | 167.75 | 158.32
2018-05-10 01:00 | 164.22 | 156.3
2018-05-10 01:30 | 164.01 | 155.89
2018-05-10 02:00 | 164.12 | 155.97
2018-05-10 02:30 | 163.94 | 155.74
2018-05-10 03:00 | 163.55 | 155.25
2018-05-10 03:30 | 162.92 | 154.46
2018-05-10 04:00 | 163.51 | 155.18
2018-05-10 04:30 | 164.22 | 155.92
2018-05-10 05:00 | 165.06 | 156.87
2018-05-10 05:30 | 166.62 | 158.87
2018-05-10 06:00 | 169.17 | 161.76
2018-05-10 06:30 | 172.86 | 165.35
2018-05-10 07:00 | 174.6 | 166.61
2018-05-10 07:30 | 177.33 | 169.29
2018-05-10 08:00 | 176.54 | 168.09
2018-05-10 08:30 | 174.43 | 165.47
2018-05-10 09:00 | 172.97 | 163.61
2018-05-10 09:30 | 171.32 | 161.49
2018-05-10 10:00 | 171.81 | 162.04
2018-05-10 10:30 | 170.91 | 161
2018-05-10 11:00 | 170.27 | 160.42
2018-05-10 11:30 | 169.76 | 159.78
2018-05-10 12:00 | 169.79 | 160.43
2018-05-10 12:30 | 171.36 | 161.92
2018-05-10 13:00 | 172.09 | 162.33
2018-05-10 13:30 | 171.88 | 162.28
2018-05-10 14:00 | 171.3 | 161.77
2018-05-10 14:30 | 173.37 | 164.06
2018-05-10 15:00 | 173.02 | 163.81
2018-05-10 15:30 | 173.63 | 164.51
2018-05-10 16:00 | 175.31 | 166.27
2018-05-10 16:30 | 176.07 | 166.99
2018-05-10 17:00 | 207.87 | 199.21
2018-05-10 17:30 | 235.82 | 227.14
2018-05-10 18:00 | 239 | 235.26
2018-05-10 18:30 | 240.88 | 237.48
2018-05-10 19:00 | 242.29 | 238.97
2018-05-10 19:30 | 243.6 | 240.29
2018-05-10 20:00 | 244.31 | 241.07
2018-05-10 20:30 | 245.21 | 242.11
2018-05-10 21:00 | 246.69 | 243.67
2018-05-10 21:30 | 239.82 | 232.44
2018-05-10 22:00 | 240.8 | 231.81
2018-05-10 22:30 | 239.74 | 230.63
2018-05-10 23:00 | 218.92 | 209.34
2018-05-10 23:30 | 181.63 | 171.11
2018-05-11 | 171.2 | 160.79
2018-05-11 00:30 | 171.15 | 161.65
2018-05-11 01:00 | 168.32 | 159.36
2018-05-11 01:30 | 167.85 | 158.97
2018-05-11 02:00 | 166.05 | 157.4
2018-05-11 02:30 | 166.24 | 157.52
2018-05-11 03:00 | 167.2 | 158.19
2018-05-11 03:30 | 166.76 | 157.62
2018-05-11 04:00 | 167.54 | 158.5
2018-05-11 04:30 | 167.2 | 158.15
2018-05-11 05:00 | 168.3 | 159.29
2018-05-11 05:30 | 166.98 | 158.42
2018-05-11 06:00 | 170.75 | 162.26
2018-05-11 06:30 | 174.45 | 165.77
2018-05-11 07:00 | 175.21 | 167.39
2018-05-11 07:30 | 176.34 | 168.6
2018-05-11 08:00 | 176.2 | 168.66
2018-05-11 08:30 | 173.83 | 166.47
2018-05-11 09:00 | 172.12 | 164.71
2018-05-11 09:30 | 170.13 | 162.83
2018-05-11 10:00 | 169.76 | 160.7
2018-05-11 10:30 | 169.23 | 160.08
2018-05-11 11:00 | 168 | 158.48
2018-05-11 11:30 | 165.93 | 156.55
2018-05-11 12:00 | 162.92 | 154.08
2018-05-11 12:30 | 163.63 | 154.36
2018-05-11 13:00 | 173.51 | 164.52
2018-05-11 13:30 | 174.07 | 166.12
2018-05-11 14:00 | 166.51 | 157.98
2018-05-11 14:30 | 163.74 | 154.92
2018-05-11 15:00 | 163.84 | 155.31
2018-05-11 15:30 | 164.71 | 156.51
2018-05-11 16:00 | 166.24 | 158.16
2018-05-11 16:30 | 167.91 | 159.94
2018-05-11 17:00 | 201.27 | 194.12
2018-05-11 17:30 | 230.73 | 223.78
2018-05-11 18:00 | 242.55 | 235.39
2018-05-11 18:30 | 245.54 | 238.41
2018-05-11 19:00 | 246.01 | 238.87
2018-05-11 19:30 | 245.82 | 238.22
2018-05-11 20:00 | 245.52 | 237.83
2018-05-11 20:30 | 245.31 | 237.43
2018-05-11 21:00 | 243.98 | 236.04
2018-05-11 21:30 | 223.44 | 216.61
2018-05-11 22:00 | 183.68 | 177.06
2018-05-11 22:30 | 173.29 | 166.49
2018-05-11 23:00 | 171.5 | 164.17
2018-05-11 23:30 | 171.06 | 164.56
2018-05-12 | 170.16 | 163.56
2018-05-12 00:30 | 170.11 | 163.41
2018-05-12 01:00 | 168.22 | 161.45
2018-05-12 01:30 | 170.05 | 163.08
2018-05-12 02:00 | 172.44 | 165.57
2018-05-12 02:30 | 172.31 | 165.35
2018-05-12 03:00 | 172.43 | 165.48
2018-05-12 03:30 | 172.46 | 165.56
2018-05-12 04:00 | 172.51 | 165.69
2018-05-12 04:30 | 168.12 | 161.17
2018-05-12 05:00 | 169.63 | 162.73
2018-05-12 05:30 | 173.18 | 166.47
2018-05-12 06:00 | 176.67 | 170.05
2018-05-12 06:30 | 178.61 | 172.17
2018-05-12 07:00 | 179.77 | 173.51
2018-05-12 07:30 | 179.9 | 173.86
2018-05-12 08:00 | 179.9 | 173.83
2018-05-12 08:30 | 174.07 | 167.82
2018-05-12 09:00 | 171.11 | 164.88
2018-05-12 09:30 | 170.17 | 163.92
2018-05-12 10:00 | 168.68 | 162.82
2018-05-12 10:30 | 166.49 | 160.45
2018-05-12 11:00 | 164.74 | 158.44
2018-05-12 11:30 | 163.9 | 157.64
2018-05-12 12:00 | 163.61 | 157.28
2018-05-12 12:30 | 163.01 | 156.65
2018-05-12 13:00 | 162.94 | 156.47
2018-05-12 13:30 | 161.49 | 154.79
2018-05-12 14:00 | 160.44 | 153.55
2018-05-12 14:30 | 160.64 | 153.73
2018-05-12 15:00 | 161.5 | 154.57
2018-05-12 15:30 | 163.16 | 156.1
2018-05-12 16:00 | 165.3 | 157.77
2018-05-12 16:30 | 202.09 | 193.46
2018-05-12 17:00 | 218.8 | 209.54
2018-05-12 17:30 | 220.22 | 211.93
2018-05-12 18:00 | 223.87 | 216.33
2018-05-12 18:30 | 225.35 | 218.05
2018-05-12 19:00 | 225.06 | 217.11
2018-05-12 19:30 | 224.05 | 215.62
2018-05-12 20:00 | 223.51 | 214.98
2018-05-12 20:30 | 222.76 | 214.24
2018-05-12 21:00 | 220.85 | 212.85
2018-05-12 21:30 | 188.54 | 180.72
2018-05-12 22:00 | 173.68 | 165.66
2018-05-12 22:30 | 171.32 | 165.02
2018-05-12 23:00 | 170.58 | 164.06
2018-05-12 23:30 | 169.46 | 162.84
2018-05-13 | 171.41 | 164.81
2018-05-13 00:30 | 171.17 | 164.63
2018-05-13 01:00 | 170.52 | 163.8
2018-05-13 01:30 | 169.45 | 162.64
2018-05-13 02:00 | 169.33 | 162.53
2018-05-13 02:30 | 171.34 | 164.58
2018-05-13 03:00 | 171.06 | 164.27
2018-05-13 03:30 | 171.19 | 164.37
2018-05-13 04:00 | 170.9 | 164.1
2018-05-13 04:30 | 166.14 | 159.16
2018-05-13 05:00 | 166.64 | 159.69
2018-05-13 05:30 | 168.43 | 161.59
2018-05-13 06:00 | 173.82 | 167.24
2018-05-13 06:30 | 174.94 | 168.49
2018-05-13 07:00 | 176.97 | 170.63
2018-05-13 07:30 | 177.49 | 171.19
2018-05-13 08:00 | 178.21 | 171.93
2018-05-13 08:30 | 177.04 | 170.83
2018-05-13 09:00 | 168.97 | 162.76
2018-05-13 09:30 | 167.22 | 160.8
2018-05-13 10:00 | 165.77 | 159.47
2018-05-13 10:30 | 164.08 | 157.97
2018-05-13 11:00 | 162.52 | 156.06
2018-05-13 11:30 | 162.53 | 156.07
2018-05-13 12:00 | 163.71 | 157.61
2018-05-13 12:30 | 163.42 | 157.29
2018-05-13 13:00 | 163.42 | 157
2018-05-13 13:30 | 163.85 | 157.46
2018-05-13 14:00 | 163.26 | 156.56
2018-05-13 14:30 | 161.92 | 154.93
2018-05-13 15:00 | 162.38 | 155.5
2018-05-13 15:30 | 163.79 | 156.96
2018-05-13 16:00 | 165.87 | 159.17
2018-05-13 16:30 | 168.17 | 161.55
2018-05-13 17:00 | 202.45 | 195.91
2018-05-13 17:30 | 233.47 | 226.31
2018-05-13 18:00 | 246.67 | 239.87
2018-05-13 18:30 | 248.71 | 242.06
2018-05-13 19:00 | 248.42 | 242.32
2018-05-13 19:30 | 246.76 | 240.33
2018-05-13 20:00 | 243.75 | 237.49
2018-05-13 20:30 | 242.81 | 236.52
2018-05-13 21:00 | 241.68 | 235.11
2018-05-13 21:30 | 222.73 | 216.37
2018-05-13 22:00 | 183.49 | 176.88
2018-05-13 22:30 | 171.95 | 165.11
2018-05-13 23:00 | 169.91 | 163.22
2018-05-13 23:30 | 169.42 | 163.01
2018-05-14 | 168.3 | 161.71
2018-05-14 00:30 | 167.47 | 160.88
2018-05-14 01:00 | 167.87 | 161.15
2018-05-14 01:30 | 167.19 | 160.35
2018-05-14 02:00 | 166.68 | 159.81
2018-05-14 02:30 | 170.13 | 163.38
2018-05-14 03:00 | 171.47 | 164.84
2018-05-14 03:30 | 171.4 | 164.71
2018-05-14 04:00 | 171.5 | 164.87
2018-05-14 04:30 | 172.06 | 165.49
2018-05-14 05:00 | 172.61 | 166.11
2018-05-14 05:30 | 175.04 | 168.67
2018-05-14 06:00 | 177.3 | 171.67
2018-05-14 06:30 | 180.88 | 175.56
2018-05-14 07:00 | 195.05 | 189.91
2018-05-14 07:30 | 227.48 | 222.65
2018-05-14 08:00 | 225.44 | 220.81
2018-05-14 08:30 | 222.52 | 217.69
2018-05-14 09:00 | 184.68 | 179.52
2018-05-14 09:30 | 171.99 | 166.56
2018-05-14 10:00 | 170.76 | 165.21
2018-05-14 10:30 | 169.68 | 163.93
2018-05-14 11:00 | 168.94 | 162.94
2018-05-14 11:30 | 168.24 | 162.17
2018-05-14 12:00 | 168.9 | 162.04
2018-05-14 12:30 | 168.44 | 161.59
2018-05-14 13:00 | 168.46 | 161.86
2018-05-14 13:30 | 168 | 161.64
2018-05-14 14:00 | 168.58 | 162.37
2018-05-14 14:30 | 168.42 | 162.34
2018-05-14 15:00 | 168.78 | 162.46
2018-05-14 15:30 | 170.32 | 163.46
2018-05-14 16:00 | 172.16 | 164.97
2018-05-14 16:30 | 203.91 | 196.88
2018-05-14 17:00 | 234.92 | 228.01
2018-05-14 17:30 | 243.06 | 236.14
2018-05-14 18:00 | 248.26 | 241.89
2018-05-14 18:30 | 251.98 | 245.81
2018-05-14 19:00 | 251.77 | 245.62
2018-05-14 19:30 | 250.29 | 243.7
2018-05-14 20:00 | 248.68 | 241.96
2018-05-14 20:30 | 247.1 | 240.76
2018-05-14 21:00 | 245.06 | 239.06
2018-05-14 21:30 | 243.84 | 238.51
2018-05-14 22:00 | 240.97 | 235.52
2018-05-14 22:30 | 238.77 | 232.88
2018-05-14 23:00 | 237.17 | 230.97
2018-05-14 23:30 | 235.2 | 229.37
2018-05-15 | 233.98 | 228.41
2018-05-15 00:30 | 216.24 | 209.73
2018-05-15 01:00 | 177.6 | 170.82
2018-05-15 01:30 | 171.84 | 164.59
2018-05-15 02:00 | 172.71 | 165.45
2018-05-15 02:30 | 172.15 | 164.91
2018-05-15 03:00 | 172.7 | 165.42
2018-05-15 03:30 | 172.59 | 165.4
2018-05-15 04:00 | 172.94 | 165.6
2018-05-15 04:30 | 169 | 161.32
2018-05-15 05:00 | 173.43 | 165.79
2018-05-15 05:30 | 176.72 | 169.47
2018-05-15 06:00 | 180.62 | 173.3
2018-05-15 06:30 | 189.92 | 183.19
2018-05-15 07:00 | 227.77 | 220.96
2018-05-15 07:30 | 230.7 | 224.94
2018-05-15 08:00 | 228.44 | 223.01
2018-05-15 08:30 | 223.85 | 218.56
2018-05-15 09:00 | 190.01 | 183.68
2018-05-15 09:30 | 173.25 | 165.86
2018-05-15 10:00 | 172.24 | 164.88
2018-05-15 10:30 | 170.71 | 163
2018-05-15 11:00 | 169.81 | 161.51
2018-05-15 11:30 | 169.36 | 160.66
2018-05-15 12:00 | 167.9 | 159.09
2018-05-15 12:30 | 167.94 | 158.92
2018-05-15 13:00 | 168.49 | 159.49
2018-05-15 13:30 | 169.2 | 160.14
2018-05-15 14:00 | 169.78 | 160.77
2018-05-15 14:30 | 170.8 | 161.88
2018-05-15 15:00 | 169.97 | 161.72
2018-05-15 15:30 | 169.22 | 161.48
2018-05-15 16:00 | 171.5 | 163.53
2018-05-15 16:30 | 172.36 | 164.38
2018-05-15 17:00 | 205.29 | 197.52
2018-05-15 17:30 | 237.85 | 229.82
2018-05-15 18:00 | 247.38 | 239.74
2018-05-15 18:30 | 251.67 | 244.37
2018-05-15 19:00 | 251.42 | 243.81
2018-05-15 19:30 | 250.34 | 242.51
2018-05-15 20:00 | 249.74 | 241.97
2018-05-15 20:30 | 248 | 240.71
2018-05-15 21:00 | 244.94 | 237.37
2018-05-15 21:30 | 243.61 | 236.62
2018-05-15 22:00 | 241.91 | 235.34
2018-05-15 22:30 | 240.32 | 233.07
2018-05-15 23:00 | 238.23 | 230.61
2018-05-15 23:30 | 220.92 | 213.97
2018-05-16 | 182.82 | 175.99
2018-05-16 00:30 | 170.12 | 163.14
2018-05-16 01:00 | 168.04 | 161.84
2018-05-16 01:30 | 167.19 | 160.92
2018-05-16 02:00 | 166.9 | 160.61
2018-05-16 02:30 | 167.02 | 160.63
2018-05-16 03:00 | 167.46 | 160.69
2018-05-16 03:30 | 167.4 | 160.49
2018-05-16 04:00 | 168.39 | 161.74
2018-05-16 04:30 | 168.1 | 161.58
2018-05-16 05:00 | 170.9 | 164.49
2018-05-16 05:30 | 170.99 | 164.66
2018-05-16 06:00 | 208.72 | 202.94
2018-05-16 06:30 | 225.87 | 219.83
2018-05-16 07:00 | 229.61 | 223.22
2018-05-16 07:30 | 197.33 | 190.91
2018-05-16 08:00 | 185 | 178.13
2018-05-16 08:30 | 181.55 | 173.92
2018-05-16 09:00 | 178.36 | 170.26
2018-05-16 09:30 | 175.22 | 166.57
2018-05-16 10:00 | 171.8 | 163.08
2018-05-16 10:30 | 170.66 | 161.78
2018-05-16 11:00 | 170.22 | 161.23
2018-05-16 11:30 | 169.57 | 160.64
2018-05-16 12:00 | 169.34 | 160.48
2018-05-16 12:30 | 168.72 | 159.68
2018-05-16 13:00 | 168.08 | 159.31
2018-05-16 13:30 | 168.44 | 159.68
2018-05-16 14:00 | 167.94 | 159.57
2018-05-16 14:30 | 168.71 | 160.5
2018-05-16 15:00 | 167.33 | 159.18
2018-05-16 15:30 | 168.14 | 160.21
2018-05-16 16:00 | 169.99 | 162.31
2018-05-16 16:30 | 172.46 | 164.57
2018-05-16 17:00 | 207.11 | 198.98
2018-05-16 17:30 | 238.73 | 230.54
2018-05-16 18:00 | 248.59 | 240.08
2018-05-16 18:30 | 253.32 | 244.96
2018-05-16 19:00 | 253.38 | 244.92
2018-05-16 19:30 | 251.73 | 243.91
2018-05-16 20:00 | 249.58 | 243.03
2018-05-16 20:30 | 248.42 | 242.28
2018-05-16 21:00 | 229.68 | 223.64
2018-05-16 21:30 | 188.79 | 183.21
2018-05-16 22:00 | 176.04 | 170.37
2018-05-16 22:30 | 174.09 | 168.17
2018-05-16 23:00 | 172.35 | 166.14
2018-05-16 23:30 | 170.25 | 164.18
2018-05-17 | 169.33 | 163.2
2018-05-17 00:30 | 168.06 | 161.84
2018-05-17 01:00 | 168.22 | 161.98
2018-05-17 01:30 | 168.13 | 161.9
2018-05-17 02:00 | 168 | 161.78
2018-05-17 02:30 | 166.95 | 160.48
2018-05-17 03:00 | 166.75 | 160.19
2018-05-17 03:30 | 167.07 | 160.4
2018-05-17 04:00 | 168.26 | 161.63
2018-05-17 04:30 | 168.6 | 161.96
2018-05-17 05:00 | 170.93 | 164.36
2018-05-17 05:30 | 172.79 | 166.38
2018-05-17 06:00 | 176.73 | 170.84
2018-05-17 06:30 | 212.69 | 207.2
2018-05-17 07:00 | 231.16 | 225.19
2018-05-17 07:30 | 233.74 | 227.76
2018-05-17 08:00 | 231.58 | 225.19
2018-05-17 08:30 | 227.08 | 220.23
2018-05-17 09:00 | 193.8 | 186.22
2018-05-17 09:30 | 175.56 | 167.34
2018-05-17 10:00 | 174.9 | 166.39
2018-05-17 10:30 | 173.36 | 164.97
2018-05-17 11:00 | 171.24 | 163.35
2018-05-17 11:30 | 170.5 | 162.52
2018-05-17 12:00 | 170.04 | 162.09
2018-05-17 12:30 | 170.3 | 162.43
2018-05-17 13:00 | 170.77 | 162.87
2018-05-17 13:30 | 170.18 | 162.47
2018-05-17 14:00 | 168.21 | 160.73
2018-05-17 14:30 | 168.82 | 161.54
2018-05-17 15:00 | 168.13 | 160.84
2018-05-17 15:30 | 168.16 | 160.97
2018-05-17 16:00 | 169.25 | 161.9
2018-05-17 16:30 | 170.6 | 163.35
2018-05-17 17:00 | 204.75 | 198.71
2018-05-17 17:30 | 231.89 | 228.52
2018-05-17 18:00 | 244.55 | 243.48
2018-05-17 18:30 | 243.07 | 241.9
2018-05-17 19:00 | 243.12 | 242
2018-05-17 19:30 | 244.55 | 243.51
2018-05-17 20:00 | 245.59 | 244.57
2018-05-17 20:30 | 245.92 | 244.91
2018-05-17 21:00 | 238.96 | 235.18
2018-05-17 21:30 | 239.36 | 235
2018-05-17 22:00 | 237.78 | 233.47
2018-05-17 22:30 | 235.73 | 231.21
2018-05-17 23:00 | 234.45 | 229.65
2018-05-17 23:30 | 233.06 | 228.45
2018-05-18 | 231.84 | 227.45
2018-05-18 00:30 | 231.47 | 227.07
2018-05-18 01:00 | 215.31 | 210.4
2018-05-18 01:30 | 176.49 | 170.29
2018-05-18 02:00 | 165.69 | 158.93
2018-05-18 02:30 | 165 | 158.25
2018-05-18 03:00 | 164.63 | 157.8
2018-05-18 03:30 | 164.79 | 157.91
2018-05-18 04:00 | 164.5 | 157.59
2018-05-18 04:30 | 165.11 | 158.18
2018-05-18 05:00 | 167.01 | 159.99
2018-05-18 05:30 | 168.27 | 161.39
2018-05-18 06:00 | 201.05 | 195.62
2018-05-18 06:30 | 217.03 | 212.47
2018-05-18 07:00 | 219.66 | 215.33
2018-05-18 07:30 | 221.1 | 217.1
2018-05-18 08:00 | 219.79 | 215.8
2018-05-18 08:30 | 215.58 | 211.55
2018-05-18 09:00 | 211.2 | 207.1
2018-05-18 09:30 | 177.82 | 172.91
2018-05-18 10:00 | 163.32 | 158.01
2018-05-18 10:30 | 163 | 157.63
2018-05-18 11:00 | 162.19 | 156.8
2018-05-18 11:30 | 161.05 | 155.63
2018-05-18 12:00 | 161.22 | 155.95
2018-05-18 12:30 | 160.3 | 154.94
2018-05-18 13:00 | 160.73 | 154.7
2018-05-18 13:30 | 161.45 | 155.35
2018-05-18 14:00 | 162.35 | 156.17
2018-05-18 14:30 | 163.68 | 157.5
2018-05-18 15:00 | 164 | 157.95
2018-05-18 15:30 | 165.13 | 159.23
2018-05-18 16:00 | 166.11 | 160.02
2018-05-18 16:30 | 199.83 | 193.81
2018-05-18 17:00 | 228.37 | 222.59
2018-05-18 17:30 | 234.57 | 228.79
2018-05-18 18:00 | 238.31 | 232.51
2018-05-18 18:30 | 240.95 | 235.29
2018-05-18 19:00 | 240.83 | 235.17
2018-05-18 19:30 | 239.36 | 233.45
2018-05-18 20:00 | 238.7 | 232.83
2018-05-18 20:30 | 237.73 | 232.2
2018-05-18 21:00 | 236.39 | 230.72
2018-05-18 21:30 | 237.06 | 231.18
2018-05-18 22:00 | 234.95 | 229.99
2018-05-18 22:30 | 232.73 | 227.69
2018-05-18 23:00 | 231.65 | 226.28
2018-05-18 23:30 | 230.46 | 225.84
2018-05-19 | 229.29 | 224.64
2018-05-19 00:30 | 212.65 | 207.55
2018-05-19 01:00 | 176.81 | 170.48
2018-05-19 01:30 | 162.75 | 156.02
2018-05-19 02:00 | 163.09 | 156.39
2018-05-19 02:30 | 161.71 | 155.05
2018-05-19 03:00 | 162.23 | 155.6
2018-05-19 03:30 | 162.14 | 155.49
2018-05-19 04:00 | 162.43 | 155.78
2018-05-19 04:30 | 163.04 | 156.47
2018-05-19 05:00 | 163.64 | 157.22
2018-05-19 05:30 | 164.74 | 158.4
2018-05-19 06:00 | 165.87 | 159.55
2018-05-19 06:30 | 169.46 | 163.3
2018-05-19 07:00 | 172.83 | 166.95
2018-05-19 07:30 | 172.33 | 166.17
2018-05-19 08:00 | 166.29 | 160.26
2018-05-19 08:30 | 164.13 | 158.16
2018-05-19 09:00 | 162.55 | 156.75
2018-05-19 09:30 | 160.42 | 154.58
2018-05-19 10:00 | 159.8 | 153.91
2018-05-19 10:30 | 157.9 | 151.72
2018-05-19 11:00 | 156.15 | 149.78
2018-05-19 11:30 | 155.38 | 148.88
2018-05-19 12:00 | 154.55 | 148.47
2018-05-19 12:30 | 153.44 | 147.2
2018-05-19 13:00 | 153.33 | 147.04
2018-05-19 13:30 | 154.54 | 147.99
2018-05-19 14:00 | 153.8 | 147.33
2018-05-19 14:30 | 154.44 | 148.02
2018-05-19 15:00 | 155.73 | 148.76
2018-05-19 15:30 | 156.42 | 149.83
2018-05-19 16:00 | 156.88 | 150.52
2018-05-19 16:30 | 158.31 | 152.04
2018-05-19 17:00 | 194.69 | 188.77
2018-05-19 17:30 | 225 | 219.11
2018-05-19 18:00 | 232.38 | 226.57
2018-05-19 18:30 | 234.87 | 228.58
2018-05-19 19:00 | 233.74 | 227.32
2018-05-19 19:30 | 231.51 | 225.13
2018-05-19 20:00 | 230.41 | 224.07
2018-05-19 20:30 | 230.54 | 224.11
2018-05-19 21:00 | 229.6 | 223.38
2018-05-19 21:30 | 228.03 | 222.68
2018-05-19 22:00 | 227.49 | 222.34
2018-05-19 22:30 | 227.24 | 221.64
2018-05-19 23:00 | 227.14 | 221.42
2018-05-19 23:30 | 225.96 | 220.68
2018-05-20 | 223.84 | 218.81
2018-05-20 00:30 | 206.84 | 201.74
2018-05-20 01:00 | 172.46 | 166.51
2018-05-20 01:30 | 157.4 | 150.61
2018-05-20 02:00 | 157.17 | 150.39
2018-05-20 02:30 | 157.6 | 150.84
2018-05-20 03:00 | 157.19 | 150.42
2018-05-20 03:30 | 156.98 | 150.19
2018-05-20 04:00 | 157.76 | 150.93
2018-05-20 04:30 | 158.13 | 151.44
2018-05-20 05:00 | 158.57 | 151.92
2018-05-20 05:30 | 159.22 | 152.61
2018-05-20 06:00 | 161.19 | 154.59
2018-05-20 06:30 | 162.39 | 155.77
2018-05-20 07:00 | 163.93 | 157.26
2018-05-20 07:30 | 164.61 | 157.85
2018-05-20 08:00 | 164.37 | 157.72
2018-05-20 08:30 | 163 | 156.75
2018-05-20 09:00 | 159.97 | 153.63
2018-05-20 09:30 | 157.06 | 150.8
2018-05-20 10:00 | 156.46 | 150.11
2018-05-20 10:30 | 155.1 | 148.72
2018-05-20 11:00 | 154.03 | 147.77
2018-05-20 11:30 | 157.82 | 151.73
2018-05-20 12:00 | 158 | 152.11
2018-05-20 12:30 | 158.75 | 152.76
2018-05-20 13:00 | 158.68 | 152.53
2018-05-20 13:30 | 158.78 | 152.61
2018-05-20 14:00 | 158.89 | 152.77
2018-05-20 14:30 | 158.4 | 152.41
2018-05-20 15:00 | 158.34 | 152.4
2018-05-20 15:30 | 159.03 | 153.12
2018-05-20 16:00 | 161.45 | 155.43
2018-05-20 16:30 | 173.3 | 167.67
2018-05-20 17:00 | 225.22 | 220.26
2018-05-20 17:30 | 236.82 | 231.16
2018-05-20 18:00 | 240.48 | 233.88
2018-05-20 18:30 | 243.06 | 236.75
2018-05-20 19:00 | 243.05 | 236.63
2018-05-20 19:30 | 241.29 | 234.5
2018-05-20 20:00 | 239.84 | 233.21
2018-05-20 20:30 | 238.93 | 232.46
2018-05-20 21:00 | 238.33 | 231.68
2018-05-20 21:30 | 236.06 | 230.3
2018-05-20 22:00 | 218.49 | 212.55
2018-05-20 22:30 | 181.85 | 175.19
2018-05-20 23:00 | 164.95 | 158.58
2018-05-20 23:30 | 164.6 | 158.33
2018-05-21 | 162.67 | 156.52
2018-05-21 00:30 | 163.61 | 157.48
2018-05-21 01:00 | 161.9 | 155.66
2018-05-21 01:30 | 162.24 | 155.95
2018-05-21 02:00 | 161.67 | 155.29
2018-05-21 02:30 | 160.83 | 154.43
2018-05-21 03:00 | 162.84 | 156.42
2018-05-21 03:30 | 161.83 | 155.29
2018-05-21 04:00 | 162.58 | 155.97
2018-05-21 04:30 | 163.88 | 157.32
2018-05-21 05:00 | 165.11 | 158.88
2018-05-21 05:30 | 167.2 | 161.33
2018-05-21 06:00 | 169.92 | 164.28
2018-05-21 06:30 | 206.59 | 201.84
2018-05-21 07:00 | 226.43 | 221.78
2018-05-21 07:30 | 229.26 | 224.75
2018-05-21 08:00 | 228.19 | 223.64
2018-05-21 08:30 | 223.86 | 219.19
2018-05-21 09:00 | 187.78 | 182.94
2018-05-21 09:30 | 169.31 | 163.78
2018-05-21 10:00 | 167.68 | 162.32
2018-05-21 10:30 | 165.32 | 159.93
2018-05-21 11:00 | 164.73 | 159.3
2018-05-21 11:30 | 163.96 | 158.57
2018-05-21 12:00 | 163.81 | 157.78
2018-05-21 12:30 | 162.81 | 156.62
2018-05-21 13:00 | 162.03 | 155.82
2018-05-21 13:30 | 161.88 | 155.64
2018-05-21 14:00 | 162.54 | 156.5
2018-05-21 14:30 | 162.59 | 156.63
2018-05-21 15:00 | 162.83 | 156.76
2018-05-21 15:30 | 163.65 | 157.7
2018-05-21 16:00 | 165.17 | 159.32
2018-05-21 16:30 | 199.75 | 194.28
2018-05-21 17:00 | 231.63 | 225.96
2018-05-21 17:30 | 239.39 | 233.83
2018-05-21 18:00 | 244.28 | 239.15
2018-05-21 18:30 | 247.61 | 242.57
2018-05-21 19:00 | 248.71 | 243.59
2018-05-21 19:30 | 247.84 | 242.6
2018-05-21 20:00 | 245.35 | 240.25
2018-05-21 20:30 | 244.65 | 239.52
2018-05-21 21:00 | 242.94 | 237.76
2018-05-21 21:30 | 241.21 | 236.5
2018-05-21 22:00 | 239.62 | 234.94
2018-05-21 22:30 | 237.7 | 232.67
2018-05-21 23:00 | 219.53 | 214.47
2018-05-21 23:30 | 183.15 | 177.6
2018-05-22 | 168.07 | 162.06
2018-05-22 00:30 | 167.95 | 161.87
2018-05-22 01:00 | 167.74 | 161.64
2018-05-22 01:30 | 167.04 | 160.96
2018-05-22 02:00 | 166.25 | 160.27
2018-05-22 02:30 | 165.58 | 159.61
2018-05-22 03:00 | 165.89 | 159.6
2018-05-22 03:30 | 165.93 | 159.48
2018-05-22 04:00 | 165.84 | 159.41
2018-05-22 04:30 | 166.67 | 160.32
2018-05-22 05:00 | 169.47 | 163.21
2018-05-22 05:30 | 170.29 | 164.12
2018-05-22 06:00 | 174.75 | 168.84
2018-05-22 06:30 | 178.75 | 173.07
2018-05-22 07:00 | 212.86 | 208.25
2018-05-22 07:30 | 229.59 | 225.62
2018-05-22 08:00 | 227.06 | 223.2
2018-05-22 08:30 | 223.11 | 219.15
2018-05-22 09:00 | 218.56 | 214.41
2018-05-22 09:30 | 186.09 | 181.31
2018-05-22 10:00 | 169.89 | 164.4
2018-05-22 10:30 | 168.48 | 162.53
2018-05-22 11:00 | 166.66 | 161.06
2018-05-22 11:30 | 165.96 | 160.34
2018-05-22 12:00 | 165.5 | 159.63
2018-05-22 12:30 | 164.25 | 158.35
2018-05-22 13:00 | 163.23 | 157.24
2018-05-22 13:30 | 163.56 | 157.54
2018-05-22 14:00 | 163.76 | 157.82
2018-05-22 14:30 | 164.47 | 158.6
2018-05-22 15:00 | 164.46 | 158.6
2018-05-22 15:30 | 164.61 | 158.79
2018-05-22 16:00 | 165.84 | 160.25
2018-05-22 16:30 | 199.31 | 194.54
2018-05-22 17:00 | 230.48 | 226.24
2018-05-22 17:30 | 237.08 | 232.81
2018-05-22 18:00 | 240.53 | 236.77
2018-05-22 18:30 | 243.92 | 240.35
2018-05-22 19:00 | 244.22 | 240.75
2018-05-22 19:30 | 244.17 | 240.6
2018-05-22 20:00 | 243.69 | 239.61
2018-05-22 20:30 | 243.57 | 239.29
2018-05-22 21:00 | 242.48 | 238.11
2018-05-22 21:30 | 241.45 | 237.51
2018-05-22 22:00 | 239.93 | 235.77
2018-05-22 22:30 | 237.77 | 233.28
2018-05-22 23:00 | 219.59 | 215.09
2018-05-22 23:30 | 183.52 | 178.34
2018-05-23 | 167.81 | 161.84
2018-05-23 00:30 | 168.19 | 161.84
2018-05-23 01:00 | 167.34 | 160.89
2018-05-23 01:30 | 166.51 | 160.06
2018-05-23 02:00 | 166.34 | 159.72
2018-05-23 02:30 | 166.64 | 160.27
2018-05-23 03:00 | 166 | 159.63
2018-05-23 03:30 | 165.99 | 159.67
2018-05-23 04:00 | 166.7 | 160.42
2018-05-23 04:30 | 167.31 | 161.17
2018-05-23 05:00 | 169.08 | 163.17
2018-05-23 05:30 | 171.01 | 165.29
2018-05-23 06:00 | 173.97 | 168.51
2018-05-23 06:30 | 178.92 | 173.89
2018-05-23 07:00 | 182.35 | 177.58
2018-05-23 07:30 | 184.65 | 180.09
2018-05-23 08:00 | 182.51 | 177.88
2018-05-23 08:30 | 178.36 | 173.6
2018-05-23 09:00 | 173.41 | 168.49
2018-05-23 09:30 | 169.76 | 164.43
2018-05-23 10:00 | 167.83 | 162.32
2018-05-23 10:30 | 166.01 | 160.35
2018-05-23 11:00 | 164.27 | 158.55
2018-05-23 11:30 | 163.66 | 157.88
2018-05-23 12:00 | 162.8 | 157.07
2018-05-23 12:30 | 162.49 | 156.77
2018-05-23 13:00 | 162.48 | 156.68
2018-05-23 13:30 | 162.96 | 156.82
2018-05-23 14:00 | 163.74 | 157.53
2018-05-23 14:30 | 164.63 | 158.34
2018-05-23 15:00 | 165.1 | 159.23
2018-05-23 15:30 | 165.91 | 160.07
2018-05-23 16:00 | 167.52 | 161.87
2018-05-23 16:30 | 168.97 | 163.19
2018-05-23 17:00 | 199.72 | 194.49
2018-05-23 17:30 | 230.44 | 225.49
2018-05-23 18:00 | 242.25 | 237.42
2018-05-23 18:30 | 246.09 | 241.49
2018-05-23 19:00 | 246.35 | 241.74
2018-05-23 19:30 | 244.86 | 240.05
2018-05-23 20:00 | 243.55 | 238.62
2018-05-23 20:30 | 242.26 | 237.35
2018-05-23 21:00 | 240.85 | 235.9
2018-05-23 21:30 | 238.82 | 234.3
2018-05-23 22:00 | 234.92 | 230.18
2018-05-23 22:30 | 233.34 | 228.59
2018-05-23 23:00 | 214.26 | 209.22
2018-05-23 23:30 | 176.99 | 171.23
2018-05-24 | 166.91 | 160.6
2018-05-24 00:30 | 166.63 | 160.43
2018-05-24 01:00 | 166.18 | 160.02
2018-05-24 01:30 | 164.45 | 158.23
2018-05-24 02:00 | 165.06 | 158.84
2018-05-24 02:30 | 164.8 | 158.63
2018-05-24 03:00 | 164.89 | 158.67
2018-05-24 03:30 | 164.78 | 158.44
2018-05-24 04:00 | 165.01 | 158.77
2018-05-24 04:30 | 166.42 | 160.26
2018-05-24 05:00 | 168.44 | 162.32
2018-05-24 05:30 | 169.17 | 163.12
2018-05-24 06:00 | 205.1 | 200.12
2018-05-24 06:30 | 220.18 | 215.69
2018-05-24 07:00 | 222.28 | 218.12
2018-05-24 07:30 | 224.25 | 220.37
2018-05-24 08:00 | 222.88 | 218.93
2018-05-24 08:30 | 220.32 | 216.18
2018-05-24 09:00 | 219.04 | 216.99
2018-05-24 09:30 | 187.49 | 184.71
2018-05-24 10:00 | 171.26 | 165.35
2018-05-24 10:30 | 169.66 | 163.45
2018-05-24 11:00 | 166.79 | 160.97
2018-05-24 11:30 | 163.36 | 157.36
2018-05-24 12:00 | 162.24 | 156.07
2018-05-24 12:30 | 160.89 | 154.43
2018-05-24 13:00 | 160.17 | 153.76
2018-05-24 13:30 | 162.56 | 155.93
2018-05-24 14:00 | 163.52 | 157.3
2018-05-24 14:30 | 165.79 | 159.46
2018-05-24 15:00 | 167.08 | 160.67
2018-05-24 15:30 | 167.34 | 161.03
2018-05-24 16:00 | 163.59 | 156.64
2018-05-24 16:30 | 163.54 | 156.27
2018-05-24 17:00 | 165.8 | 158.75
2018-05-24 17:30 | 166.85 | 160.09
2018-05-24 18:00 | 170.86 | 164.5
2018-05-24 18:30 | 173.15 | 166.81
2018-05-24 19:00 | 173.51 | 166.94
2018-05-24 19:30 | 172.75 | 165.73
2018-05-24 20:00 | 171.44 | 164.37
2018-05-24 20:30 | 170.16 | 163.2
2018-05-24 21:00 | 168.86 | 161.73
2018-05-24 21:30 | 167.74 | 160.87
2018-05-24 22:00 | 165.31 | 158.78
2018-05-24 22:30 | 163.11 | 156.34
2018-05-24 23:00 | 161.4 | 154.4
2018-05-24 23:30 | 160.29 | 153.36
2018-05-25 | 159.22 | 152.3
2018-05-25 00:30 | 158.04 | 152.04
2018-05-25 01:00 | 159.95 | 154.42
2018-05-25 01:30 | 159.37 | 154.01
2018-05-25 02:00 | 158.73 | 153.37
2018-05-25 02:30 | 158.35 | 152.98
2018-05-25 03:00 | 158.36 | 153.03
2018-05-25 03:30 | 157.75 | 152.31
2018-05-25 04:00 | 158.15 | 152.74
2018-05-25 04:30 | 158.21 | 152.9
2018-05-25 05:00 | 159.15 | 153.91
2018-05-25 05:30 | 160.35 | 155.25
2018-05-25 06:00 | 158.82 | 153.07
2018-05-25 06:30 | 164.23 | 158.65
2018-05-25 07:00 | 156.45 | 151.54
2018-05-25 07:30 | 139.77 | 135.94
2018-05-25 08:00 | 149.93 | 145.52
2018-05-25 08:30 | 163.13 | 158.32
2018-05-25 09:00 | 159.4 | 154.61
2018-05-25 09:30 | 156.18 | 151.39
2018-05-25 10:00 | 154.87 | 150.04
2018-05-25 10:30 | 152.32 | 147.43
2018-05-25 11:00 | 151.9 | 146.83
2018-05-25 11:30 | 152.81 | 147.39
2018-05-25 12:00 | 152.95 | 147.46
2018-05-25 12:30 | 151.28 | 145.87
2018-05-25 13:00 | 151.68 | 146.38
2018-05-25 13:30 | 152.24 | 147.5
2018-05-25 14:00 | 152.03 | 147.16
2018-05-25 14:30 | 155 | 149.67
2018-05-25 15:00 | 156.25 | 149.84
2018-05-25 15:30 | 160.6 | 154.4
2018-05-25 16:00 | 161.15 | 154.9
2018-05-25 16:30 | 157.79 | 150.81
2018-05-25 17:00 | 160.46 | 153.56
2018-05-25 17:30 | 161.66 | 154.85
2018-05-25 18:00 | 164.31 | 157.87
2018-05-25 18:30 | 166.33 | 159.92
2018-05-25 19:00 | 166.45 | 160.1
2018-05-25 19:30 | 164.97 | 158.36
2018-05-25 20:00 | 163.72 | 157.37
2018-05-25 20:30 | 162.54 | 156.22
2018-05-25 21:00 | 162.02 | 155.44
2018-05-25 21:30 | 161.36 | 155.33
2018-05-25 22:00 | 158.16 | 152.23
2018-05-25 22:30 | 158.46 | 152.45
2018-05-25 23:00 | 153.95 | 147.33
2018-05-25 23:30 | 157.83 | 152.29
2018-05-26 | 159.14 | 153.95
2018-05-26 00:30 | 156.94 | 151.56
2018-05-26 01:00 | 157.28 | 152.01
2018-05-26 01:30 | 156.81 | 151.51
2018-05-26 02:00 | 156.7 | 151.37
2018-05-26 02:30 | 155.92 | 150.59
2018-05-26 03:00 | 155.67 | 150.31
2018-05-26 03:30 | 155.99 | 150.65
2018-05-26 04:00 | 155.41 | 150.06
2018-05-26 04:30 | 155.96 | 150.6
2018-05-26 05:00 | 156.93 | 151.54
2018-05-26 05:30 | 157.84 | 152.5
2018-05-26 06:00 | 158.66 | 153.38
2018-05-26 06:30 | 160.35 | 155.17
2018-05-26 07:00 | 161.5 | 156.46
2018-05-26 07:30 | 162.67 | 157.96
2018-05-26 08:00 | 163.27 | 158.2
2018-05-26 08:30 | 156.45 | 152.04
2018-05-26 09:00 | 149.67 | 146.23
2018-05-26 09:30 | 149.57 | 145.73
2018-05-26 10:00 | 156.44 | 151.55
2018-05-26 10:30 | 154.61 | 150.03
2018-05-26 11:00 | 153.6 | 149.18
2018-05-26 11:30 | 152.56 | 148.13
2018-05-26 12:00 | 152.24 | 147.86
2018-05-26 12:30 | 150.98 | 146.69
2018-05-26 13:00 | 150.95 | 146.7
2018-05-26 13:30 | 150.96 | 146.41
2018-05-26 14:00 | 153.05 | 147.8
2018-05-26 14:30 | 153.56 | 148.3
2018-05-26 15:00 | 153.59 | 148.22
2018-05-26 15:30 | 154.48 | 149.04
2018-05-26 16:00 | 156.19 | 150.84
2018-05-26 16:30 | 157.81 | 152.62
2018-05-26 17:00 | 155.09 | 149
2018-05-26 17:30 | 156.9 | 150.73
2018-05-26 18:00 | 161.56 | 155.37
2018-05-26 18:30 | 163.11 | 157.02
2018-05-26 19:00 | 162.49 | 156.23
2018-05-26 19:30 | 161.4 | 154.96
2018-05-26 20:00 | 160.47 | 153.96
2018-05-26 20:30 | 160.25 | 153.67
2018-05-26 21:00 | 159.25 | 152.35
2018-05-26 21:30 | 158.22 | 151.85
2018-05-26 22:00 | 156.91 | 150.6
2018-05-26 22:30 | 154.77 | 148.58
2018-05-26 23:00 | 151.21 | 145.53
2018-05-26 23:30 | 153.63 | 148.22
2018-05-27 | 154.75 | 149.44
2018-05-27 00:30 | 154.11 | 148.82
2018-05-27 01:00 | 152.95 | 147.53
2018-05-27 01:30 | 152.43 | 147.01
2018-05-27 02:00 | 152.08 | 146.64
2018-05-27 02:30 | 151.61 | 146.15
2018-05-27 03:00 | 151.36 | 145.97
2018-05-27 03:30 | 151.21 | 145.82
2018-05-27 04:00 | 151.43 | 146.05
2018-05-27 04:30 | 151.1 | 145.66
2018-05-27 05:00 | 151.36 | 145.95
2018-05-27 05:30 | 152.57 | 147.22
2018-05-27 06:00 | 152.89 | 147.56
2018-05-27 06:30 | 153.96 | 148.72
2018-05-27 07:00 | 155.4 | 150.31
2018-05-27 07:30 | 157.38 | 152.45
2018-05-27 08:00 | 157.5 | 152.58
2018-05-27 08:30 | 151.11 | 147.14
2018-05-27 09:00 | 144.37 | 141.73
2018-05-27 09:30 | 143.54 | 140.64
2018-05-27 10:00 | 142.58 | 138.68
2018-05-27 10:30 | 142.23 | 138.31
2018-05-27 11:00 | 141.75 | 137.89
2018-05-27 11:30 | 140.8 | 137.07
2018-05-27 12:00 | 141.29 | 137.5
2018-05-27 12:30 | 141.64 | 137.79
2018-05-27 13:00 | 147.84 | 143.54
2018-05-27 13:30 | 157.93 | 152.62
2018-05-27 14:00 | 157.71 | 152.34
2018-05-27 14:30 | 157.91 | 152.44
2018-05-27 15:00 | 159.86 | 154.15
2018-05-27 15:30 | 161.52 | 156.05
2018-05-27 16:00 | 161.67 | 156.22
2018-05-27 16:30 | 163.43 | 157.37
2018-05-27 17:00 | 165.49 | 159.4
2018-05-27 17:30 | 167.61 | 161.97
2018-05-27 18:00 | 171.13 | 165.82
2018-05-27 18:30 | 172.93 | 167.84
2018-05-27 19:00 | 171.43 | 166.05
2018-05-27 19:30 | 169.37 | 163.84
2018-05-27 20:00 | 167.8 | 162.26
2018-05-27 20:30 | 167.07 | 161.41
2018-05-27 21:00 | 165.84 | 160.07
2018-05-27 21:30 | 164.68 | 159
2018-05-27 22:00 | 163.06 | 157.27
2018-05-27 22:30 | 160.63 | 155.34
2018-05-27 23:00 | 158.88 | 153.5
2018-05-27 23:30 | 158.49 | 153.08
2018-05-28 | 157.77 | 152.31
2018-05-28 00:30 | 156.86 | 151.43
2018-05-28 01:00 | 155.91 | 150.62
2018-05-28 01:30 | 155.8 | 150.55
2018-05-28 02:00 | 155.77 | 150.49
2018-05-28 02:30 | 155.12 | 149.75
2018-05-28 03:00 | 155.02 | 149.67
2018-05-28 03:30 | 155.02 | 149.62
2018-05-28 04:00 | 155.17 | 149.81
2018-05-28 04:30 | 155.91 | 150.56
2018-05-28 05:00 | 156 | 150.68
2018-05-28 05:30 | 157.39 | 152.19
2018-05-28 06:00 | 159.85 | 154.86
2018-05-28 06:30 | 164.09 | 159.45
2018-05-28 07:00 | 166.25 | 161.63
2018-05-28 07:30 | 168.59 | 164.1
2018-05-28 08:00 | 169.8 | 165.31
2018-05-28 08:30 | 167.95 | 163.49
2018-05-28 09:00 | 166.83 | 162.16
2018-05-28 09:30 | 164.45 | 159.58
2018-05-28 10:00 | 163.31 | 158.49
2018-05-28 10:30 | 162.89 | 157.82
2018-05-28 11:00 | 162.15 | 156.9
2018-05-28 11:30 | 159.78 | 154.55
2018-05-28 12:00 | 161.3 | 155.96
2018-05-28 12:30 | 161.54 | 156.08
2018-05-28 13:00 | 161.12 | 155.62
2018-05-28 13:30 | 162.16 | 156.49
2018-05-28 14:00 | 162.76 | 157.27
2018-05-28 14:30 | 163.45 | 158.04
2018-05-28 15:00 | 163.1 | 157.77
2018-05-28 15:30 | 163.22 | 157.83
2018-05-28 16:00 | 163.98 | 158.68
2018-05-28 16:30 | 164.72 | 159.46
2018-05-28 17:00 | 165.9 | 160.76
2018-05-28 17:30 | 168.98 | 163.72
2018-05-28 18:00 | 172.01 | 170.26
2018-05-28 18:30 | 175.38 | 174.06
2018-05-28 19:00 | 176.11 | 174.81
2018-05-28 19:30 | 178.18 | 176.95
2018-05-28 20:00 | 177.74 | 176.57
2018-05-28 20:30 | 171.1 | 166.43
2018-05-28 21:00 | 171.32 | 165.39
2018-05-28 21:30 | 169.79 | 164.25
2018-05-28 22:00 | 167.76 | 162.14
2018-05-28 22:30 | 166.05 | 160.58
2018-05-28 23:00 | 164.17 | 158.43
2018-05-28 23:30 | 163.5 | 157.68
2018-05-29 | 163 | 157.17
2018-05-29 00:30 | 161.44 | 156.11
2018-05-29 01:00 | 160.41 | 155.12
2018-05-29 01:30 | 160.14 | 154.81
2018-05-29 02:00 | 159.6 | 154.26
2018-05-29 02:30 | 159.47 | 154.09
2018-05-29 03:00 | 158.8 | 153.41
2018-05-29 03:30 | 158.69 | 153.32
2018-05-29 04:00 | 159.13 | 153.79
2018-05-29 04:30 | 159.23 | 153.9
2018-05-29 05:00 | 160.66 | 155.39
2018-05-29 05:30 | 162.38 | 157.19
2018-05-29 06:00 | 165.3 | 160.02
2018-05-29 06:30 | 160.22 | 155.66
2018-05-29 07:00 | 146.71 | 143.02
2018-05-29 07:30 | 145.13 | 141.27
2018-05-29 08:00 | 158.61 | 153.84
2018-05-29 08:30 | 159.78 | 154.84
2018-05-29 09:00 | 156.49 | 151.52
2018-05-29 09:30 | 153.98 | 148.93
2018-05-29 10:00 | 153.27 | 148.09
2018-05-29 10:30 | 151.75 | 146.53
2018-05-29 11:00 | 151.07 | 145.94
2018-05-29 11:30 | 150.82 | 145.7
2018-05-29 12:00 | 161.52 | 155.04
2018-05-29 12:30 | 162.17 | 155.99
2018-05-29 13:00 | 161.84 | 156.35
2018-05-29 13:30 | 163.01 | 157.37
2018-05-29 14:00 | 164.15 | 158.38
2018-05-29 14:30 | 164.3 | 158.72
2018-05-29 15:00 | 164.54 | 159.2
2018-05-29 15:30 | 165.2 | 159.92
2018-05-29 16:00 | 166.79 | 161.66
2018-05-29 16:30 | 167.28 | 162.23
2018-05-29 17:00 | 169.12 | 163.75
2018-05-29 17:30 | 171.28 | 165.44
2018-05-29 18:00 | 174.37 | 168.86
2018-05-29 18:30 | 175.66 | 170.33
2018-05-29 19:00 | 175.59 | 170.36
2018-05-29 19:30 | 166.98 | 160.67
2018-05-29 20:00 | 166.96 | 160.41
2018-05-29 20:30 | 166.22 | 159.74
2018-05-29 21:00 | 165.04 | 158.24
2018-05-29 21:30 | 163.4 | 157.22
2018-05-29 22:00 | 162.78 | 156.49
2018-05-29 22:30 | 162.42 | 156.65
2018-05-29 23:00 | 164.72 | 159.3
2018-05-29 23:30 | 163.43 | 157.96
2018-05-30 | 162.79 | 157.3
2018-05-30 00:30 | 162.08 | 156.62
2018-05-30 01:00 | 160.67 | 155.31
2018-05-30 01:30 | 159.76 | 154.5
2018-05-30 02:00 | 160.38 | 155.1
2018-05-30 02:30 | 159.02 | 153.83
2018-05-30 03:00 | 158.63 | 153.48
2018-05-30 03:30 | 158.63 | 153.4
2018-05-30 04:00 | 159.1 | 153.9
2018-05-30 04:30 | 159.75 | 154.58
2018-05-30 05:00 | 158.63 | 153.47
2018-05-30 05:30 | 160.19 | 155
2018-05-30 06:00 | 163.39 | 157.48
2018-05-30 06:30 | 166.86 | 161.19
2018-05-30 07:00 | 170.53 | 164.87
2018-05-30 07:30 | 173.39 | 167.74
2018-05-30 08:00 | 172.27 | 167.77
2018-05-30 08:30 | 168.99 | 164.43
2018-05-30 09:00 | 166.1 | 161.54
2018-05-30 09:30 | 164.95 | 160.17
2018-05-30 10:00 | 164.34 | 159.11
2018-05-30 10:30 | 162.85 | 157.38
2018-05-30 11:00 | 161.76 | 156.63
2018-05-30 11:30 | 161.08 | 155.72
2018-05-30 12:00 | 160.33 | 155.07
2018-05-30 12:30 | 160.42 | 155.14
2018-05-30 13:00 | 160.68 | 155.3
2018-05-30 13:30 | 161.14 | 155.78
2018-05-30 14:00 | 161.1 | 155.64
2018-05-30 14:30 | 159.97 | 154.62
2018-05-30 15:00 | 160.32 | 155.19
2018-05-30 15:30 | 160.43 | 155.42
2018-05-30 16:00 | 161.2 | 156.45
2018-05-30 16:30 | 163.18 | 158.04
2018-05-30 17:00 | 164.6 | 159.46
2018-05-30 17:30 | 167.79 | 162.57
2018-05-30 18:00 | 173.08 | 167.76
2018-05-30 18:30 | 176.48 | 171.29
2018-05-30 19:00 | 176.67 | 171.33
2018-05-30 19:30 | 174.3 | 168.54
2018-05-30 20:00 | 173.81 | 167.92
2018-05-30 20:30 | 172.4 | 167.45
2018-05-30 21:00 | 170.32 | 165.59
2018-05-30 21:30 | 168.27 | 163.8
2018-05-30 22:00 | 166.18 | 161.65
2018-05-30 22:30 | 163.37 | 158.83
2018-05-30 23:00 | 160.79 | 156.15
2018-05-30 23:30 | 160.12 | 155.46
2018-05-31 | 158.14 | 153.35
2018-05-31 00:30 | 158.33 | 153.5
2018-05-31 01:00 | 157.76 | 152.83
2018-05-31 01:30 | 157.39 | 152.57
2018-05-31 02:00 | 156.61 | 151.74
2018-05-31 02:30 | 156.87 | 151.96
2018-05-31 03:00 | 156.99 | 152.07
2018-05-31 03:30 | 156.19 | 151.26
2018-05-31 04:00 | 156.57 | 151.64
2018-05-31 04:30 | 158.05 | 153.17
2018-05-31 05:00 | 159.72 | 154.93
2018-05-31 05:30 | 162.11 | 157.43
2018-05-31 06:00 | 165.3 | 160.78
2018-05-31 06:30 | 170.89 | 166.57
2018-05-31 07:00 | 171.35 | 166.81
2018-05-31 07:30 | 176.3 | 171.67
2018-05-31 08:00 | 175.69 | 171.05
2018-05-31 08:30 | 171.12 | 166.49
2018-05-31 09:00 | 165.53 | 161.06
2018-05-31 09:30 | 164.52 | 160.14
2018-05-31 10:00 | 163.92 | 159.26
2018-05-31 10:30 | 162.53 | 157.88
2018-05-31 11:00 | 160.32 | 155.69
2018-05-31 11:30 | 158.85 | 154.18
2018-05-31 12:00 | 158.53 | 153.87
2018-05-31 12:30 | 157.64 | 152.92
2018-05-31 13:00 | 158.35 | 153.52
2018-05-31 13:30 | 158.48 | 153.58
2018-05-31 14:00 | 160.54 | 155.72
2018-05-31 14:30 | 162.01 | 157.26
2018-05-31 15:00 | 161.67 | 156.97
2018-05-31 15:30 | 161.56 | 157.01
2018-05-31 16:00 | 164.01 | 159.38
2018-05-31 16:30 | 166.03 | 161.05
2018-05-31 17:00 | 168.81 | 163.62
2018-05-31 17:30 | 171.22 | 166.02
2018-05-31 18:00 | 177.43 | 172.82
2018-05-31 18:30 | 181.16 | 176.6
2018-05-31 19:00 | 181.8 | 177.21
2018-05-31 19:30 | 179.91 | 175.15
2018-05-31 20:00 | 179.13 | 174.36
2018-05-31 20:30 | 177.24 | 172.48
2018-05-31 21:00 | 176.22 | 171.23
2018-05-31 21:30 | 174.37 | 169.92
2018-05-31 22:00 | 172.04 | 167.54
2018-05-31 22:30 | 169.24 | 164.62
2018-05-31 23:00 | 166.55 | 161.82
2018-05-31 23:30 | 165.28 | 160.51
2018-06-01 | 164.07 | 159.21
2018-06-01 00:30 | 162.49 | 157.6
2018-06-01 01:00 | 161.47 | 156.62
2018-06-01 01:30 | 161.16 | 156.36
2018-06-01 02:00 | 160.27 | 155.44
2018-06-01 02:30 | 159.51 | 154.61
2018-06-01 03:00 | 159.71 | 154.86
2018-06-01 03:30 | 160.39 | 155.54
2018-06-01 04:00 | 160.66 | 155.84
2018-06-01 04:30 | 161.7 | 156.88
2018-06-01 05:00 | 159.63 | 154.61
2018-06-01 05:30 | 162.43 | 157.52
2018-06-01 06:00 | 165.96 | 160.81
2018-06-01 06:30 | 171.24 | 166.25
2018-06-01 07:00 | 176.36 | 171.04
2018-06-01 07:30 | 179.53 | 175
2018-06-01 08:00 | 180.42 | 175.9
2018-06-01 08:30 | 176.6 | 171.95
2018-06-01 09:00 | 171.21 | 166.71
2018-06-01 09:30 | 167.43 | 162.74
2018-06-01 10:00 | 165.88 | 161.09
2018-06-01 10:30 | 162.18 | 157.1
2018-06-01 11:00 | 160.2 | 155.24
2018-06-01 11:30 | 158.6 | 153.6
2018-06-01 12:00 | 157.65 | 152.9
2018-06-01 12:30 | 156.81 | 152.02
2018-06-01 13:00 | 155.78 | 150.96
2018-06-01 13:30 | 154.71 | 149.8
2018-06-01 14:00 | 152.22 | 146.56
2018-06-01 14:30 | 175.02 | 169.76
2018-06-01 15:00 | 189.18 | 183.51
2018-06-01 15:30 | 192.52 | 185.95
2018-06-01 16:00 | 193.39 | 187.48
2018-06-01 16:30 | 195.77 | 190.34
2018-06-01 17:00 | 199.06 | 193.74
2018-06-01 17:30 | 202.63 | 197.35
2018-06-01 18:00 | 205.5 | 200.22
2018-06-01 18:30 | 208.45 | 202.86
2018-06-01 19:00 | 208.66 | 203.09
2018-06-01 19:30 | 208.17 | 202.63
2018-06-01 20:00 | 207.42 | 201.94
2018-06-01 20:30 | 206.98 | 201.41
2018-06-01 21:00 | 206.44 | 200.39
2018-06-01 21:30 | 204.56 | 199.63
2018-06-01 22:00 | 203.09 | 198.45
2018-06-01 22:30 | 171.05 | 165.4
2018-06-01 23:00 | 159.28 | 153.3
2018-06-01 23:30 | 157.19 | 151.07
2018-06-02 | 156.06 | 149.49
2018-06-02 00:30 | 156.5 | 149.55
2018-06-02 01:00 | 155.34 | 148.32
2018-06-02 01:30 | 155.05 | 148.38
2018-06-02 02:00 | 153.94 | 147.41
2018-06-02 02:30 | 153.88 | 147.33
2018-06-02 03:00 | 154.47 | 147.64
2018-06-02 03:30 | 154.15 | 147.29
2018-06-02 04:00 | 154.53 | 147.72
2018-06-02 04:30 | 154.87 | 148.09
2018-06-02 05:00 | 186.05 | 180.44
2018-06-02 05:30 | 199.01 | 193.78
2018-06-02 06:00 | 201.97 | 196.89
2018-06-02 06:30 | 204 | 199.09
2018-06-02 07:00 | 207.05 | 202.17
2018-06-02 07:30 | 209.82 | 204.95
2018-06-02 08:00 | 209.85 | 204.9
2018-06-02 08:30 | 208.13 | 203.01
2018-06-02 09:00 | 204.97 | 199.8
2018-06-02 09:30 | 201.1 | 196.14
2018-06-02 10:00 | 197.98 | 192.94
2018-06-02 10:30 | 166.09 | 160.12
2018-06-02 11:00 | 181.02 | 176.22
2018-06-02 11:30 | 193.76 | 189.58
2018-06-02 12:00 | 193.62 | 189.34
2018-06-02 12:30 | 195.69 | 191.29
2018-06-02 13:00 | 196.9 | 191.94
2018-06-02 13:30 | 195.35 | 190.19
2018-06-02 14:00 | 194.22 | 189.16
2018-06-02 14:30 | 194.56 | 189.62
2018-06-02 15:00 | 195.69 | 190.75
2018-06-02 15:30 | 198.96 | 193.88
2018-06-02 16:00 | 201.66 | 196.5
2018-06-02 16:30 | 203.69 | 198.53
2018-06-02 17:00 | 206.82 | 201.69
2018-06-02 17:30 | 210.3 | 205.34
2018-06-02 18:00 | 214.81 | 210.01
2018-06-02 18:30 | 217.45 | 212.71
2018-06-02 19:00 | 216.96 | 212.24
2018-06-02 19:30 | 215.57 | 210.87
2018-06-02 20:00 | 214.4 | 209.69
2018-06-02 20:30 | 213.69 | 208.91
2018-06-02 21:00 | 212.03 | 207.28
2018-06-02 21:30 | 211.31 | 206.6
2018-06-02 22:00 | 209.82 | 205.09
2018-06-02 22:30 | 207.92 | 203.17
2018-06-02 23:00 | 206.24 | 201.38
2018-06-02 23:30 | 205.36 | 200.47
2018-06-03 | 204.7 | 199.65
2018-06-03 00:30 | 203.94 | 198.81
2018-06-03 01:00 | 202.9 | 197.73
2018-06-03 01:30 | 202.51 | 197.35
2018-06-03 02:00 | 201.65 | 196.5
2018-06-03 02:30 | 201.29 | 196.11
2018-06-03 03:00 | 201.08 | 195.88
2018-06-03 03:30 | 200.83 | 195.67
2018-06-03 04:00 | 201.27 | 196.16
2018-06-03 04:30 | 201.68 | 196.59
2018-06-03 05:00 | 202.26 | 197.25
2018-06-03 05:30 | 203.42 | 198.4
2018-06-03 06:00 | 204.3 | 199.39
2018-06-03 06:30 | 205.61 | 200.88
2018-06-03 07:00 | 207.42 | 202.77
2018-06-03 07:30 | 210.09 | 205.4
2018-06-03 08:00 | 210.87 | 206.38
2018-06-03 08:30 | 210.07 | 205.51
2018-06-03 09:00 | 208.08 | 203.43
2018-06-03 09:30 | 204.83 | 200.15
2018-06-03 10:00 | 202.98 | 198.2
2018-06-03 10:30 | 200.27 | 195.37
2018-06-03 11:00 | 198.1 | 193.14
2018-06-03 11:30 | 196.51 | 191.57
2018-06-03 12:00 | 195.86 | 190.95
2018-06-03 12:30 | 195.61 | 190.66
2018-06-03 13:00 | 195.45 | 190.55
2018-06-03 13:30 | 195.32 | 190.35
2018-06-03 14:00 | 195.95 | 190.88
2018-06-03 14:30 | 196.93 | 191.91
2018-06-03 15:00 | 198.31 | 193.32
2018-06-03 15:30 | 199.38 | 194.33
2018-06-03 16:00 | 201.21 | 196.15
2018-06-03 16:30 | 202.77 | 197.83
2018-06-03 17:00 | 205.46 | 200.61
2018-06-03 17:30 | 208.82 | 204.2
2018-06-03 18:00 | 212.82 | 208.34
2018-06-03 18:30 | 215.19 | 210.82
2018-06-03 19:00 | 214.84 | 210.44
2018-06-03 19:30 | 213.79 | 209.24
2018-06-03 20:00 | 213.08 | 208.45
2018-06-03 20:30 | 211.5 | 206.78
2018-06-03 21:00 | 210.38 | 205.62
2018-06-03 21:30 | 209.13 | 204.19
2018-06-03 22:00 | 207.03 | 202.01
2018-06-03 22:30 | 204.84 | 199.76
2018-06-03 23:00 | 202.58 | 197.39
2018-06-03 23:30 | 201.39 | 196.02
2018-06-04 | 200.11 | 194.69
2018-06-04 00:30 | 199.97 | 194.53
2018-06-04 01:00 | 198.95 | 193.47
2018-06-04 01:30 | 198.2 | 192.84
2018-06-04 02:00 | 198.03 | 192.75
2018-06-04 02:30 | 198.25 | 192.96
2018-06-04 03:00 | 197.99 | 192.65
2018-06-04 03:30 | 198.43 | 193.12
2018-06-04 04:00 | 198.84 | 193.54
2018-06-04 04:30 | 199.28 | 194.09
2018-06-04 05:00 | 200.15 | 195.05
2018-06-04 05:30 | 202.75 | 197.73
2018-06-04 06:00 | 206.57 | 201.82
2018-06-04 06:30 | 211.37 | 206.93
2018-06-04 07:00 | 215.83 | 211.48
2018-06-04 07:30 | 218.43 | 214.39
2018-06-04 08:00 | 217.48 | 213.46
2018-06-04 08:30 | 214.24 | 210.05
2018-06-04 09:00 | 210.4 | 205.92
2018-06-04 09:30 | 206.23 | 201.65
2018-06-04 10:00 | 204.49 | 199.87
2018-06-04 10:30 | 202.84 | 198.03
2018-06-04 11:00 | 201.37 | 196.65
2018-06-04 11:30 | 200.2 | 195.49
2018-06-04 12:00 | 199.79 | 195.05
2018-06-04 12:30 | 198.04 | 193.37
2018-06-04 13:00 | 197.69 | 193.01
2018-06-04 13:30 | 198.2 | 193.51
2018-06-04 14:00 | 199.08 | 194.43
2018-06-04 14:30 | 199.09 | 194.53
2018-06-04 15:00 | 199.26 | 194.75
2018-06-04 15:30 | 200.16 | 195.66
2018-06-04 16:00 | 201.63 | 197.16
2018-06-04 16:30 | 202.93 | 198.38
2018-06-04 17:00 | 204.86 | 200.35
2018-06-04 17:30 | 212.48 | 210.95
2018-06-04 18:00 | 210.45 | 209.14
2018-06-04 18:30 | 212.33 | 211.14
2018-06-04 19:00 | 212.69 | 211.5
2018-06-04 19:30 | 214.46 | 213.29
2018-06-04 20:00 | 215.26 | 214.11
2018-06-04 20:30 | 215.83 | 214.7
2018-06-04 21:00 | 216.73 | 215.56
2018-06-04 21:30 | 207.85 | 204.35
2018-06-04 22:00 | 206.95 | 202.34
2018-06-04 22:30 | 204.8 | 200.1
2018-06-04 23:00 | 202.03 | 197.36
2018-06-04 23:30 | 200.93 | 196.22
2018-06-05 | 199.87 | 195.06
2018-06-05 00:30 | 199.79 | 194.9
2018-06-05 01:00 | 198.76 | 193.95
2018-06-05 01:30 | 197.83 | 193.01
2018-06-05 02:00 | 197.77 | 192.92
2018-06-05 02:30 | 197.59 | 192.75
2018-06-05 03:00 | 196.99 | 192.14
2018-06-05 03:30 | 197.26 | 192.36
2018-06-05 04:00 | 197.52 | 192.66
2018-06-05 04:30 | 198.82 | 193.89
2018-06-05 05:00 | 200.23 | 195.25
2018-06-05 05:30 | 202.68 | 197.83
2018-06-05 06:00 | 205.93 | 201.35
2018-06-05 06:30 | 210.75 | 206.47
2018-06-05 07:00 | 214.74 | 210.69
2018-06-05 07:30 | 217.13 | 213.34
2018-06-05 08:00 | 216.72 | 212.87
2018-06-05 08:30 | 212.86 | 208.81
2018-06-05 09:00 | 208.8 | 204.63
2018-06-05 09:30 | 204.71 | 200.4
2018-06-05 10:00 | 203.01 | 198.55
2018-06-05 10:30 | 201.35 | 196.76
2018-06-05 11:00 | 200.57 | 195.96
2018-06-05 11:30 | 200.34 | 195.66
2018-06-05 12:00 | 198.26 | 193.52
2018-06-05 12:30 | 167.97 | 162.01
2018-06-05 13:00 | 167.91 | 161.77
2018-06-05 13:30 | 165.95 | 160.44
2018-06-05 14:00 | 166.5 | 160.66
2018-06-05 14:30 | 167.01 | 161.13
2018-06-05 15:00 | 166.97 | 160.87
2018-06-05 15:30 | 167.62 | 161.74
2018-06-05 16:00 | 168.71 | 162.9
2018-06-05 16:30 | 173.41 | 169.51
2018-06-05 17:00 | 186.32 | 184.97
2018-06-05 17:30 | 185.04 | 183.54
2018-06-05 18:00 | 182.79 | 181
2018-06-05 18:30 | 179.7 | 178.14
2018-06-05 19:00 | 179.36 | 177.87
2018-06-05 19:30 | 180 | 178.51
2018-06-05 20:00 | 181.2 | 179.8
2018-06-05 20:30 | 181.55 | 180.15
2018-06-05 21:00 | 177.42 | 172.84
2018-06-05 21:30 | 179.77 | 174.44
2018-06-05 22:00 | 177.81 | 172.41
2018-06-05 22:30 | 174.96 | 169.67
2018-06-05 23:00 | 172.95 | 167.62
2018-06-05 23:30 | 171.33 | 166.28
2018-06-06 | 187.24 | 182.56
2018-06-06 00:30 | 201.39 | 196.48
2018-06-06 01:00 | 199.51 | 194.49
2018-06-06 01:30 | 198.6 | 193.53
2018-06-06 02:00 | 198.49 | 193.51
2018-06-06 02:30 | 198.22 | 193.22
2018-06-06 03:00 | 198.44 | 193.34
2018-06-06 03:30 | 198.74 | 193.63
2018-06-06 04:00 | 198.93 | 193.88
2018-06-06 04:30 | 199.65 | 194.67
2018-06-06 05:00 | 201.2 | 196.3
2018-06-06 05:30 | 203.35 | 198.58
2018-06-06 06:00 | 206.47 | 202.03
2018-06-06 06:30 | 210.65 | 206.49
2018-06-06 07:00 | 214.5 | 210.51
2018-06-06 07:30 | 217.78 | 214.05
2018-06-06 08:00 | 217.46 | 213.62
2018-06-06 08:30 | 213.02 | 208.99
2018-06-06 09:00 | 209.33 | 205.05
2018-06-06 09:30 | 206.16 | 201.69
2018-06-06 10:00 | 204.79 | 200.2
2018-06-06 10:30 | 202.71 | 197.93
2018-06-06 11:00 | 201.3 | 196.56
2018-06-06 11:30 | 200.6 | 195.88
2018-06-06 12:00 | 199.65 | 195.01
2018-06-06 12:30 | 198.63 | 193.8
2018-06-06 13:00 | 199 | 194.01
2018-06-06 13:30 | 199.83 | 194.71
2018-06-06 14:00 | 199.39 | 194.33
2018-06-06 14:30 | 200.81 | 195.65
2018-06-06 15:00 | 201.03 | 195.91
2018-06-06 15:30 | 200.99 | 195.98
2018-06-06 16:00 | 201.9 | 196.91
2018-06-06 16:30 | 203.46 | 198.47
2018-06-06 17:00 | 204.75 | 199.86
2018-06-06 17:30 | 207.95 | 203.07
2018-06-06 18:00 | 213.1 | 208.46
2018-06-06 18:30 | 216.73 | 212.26
2018-06-06 19:00 | 217.45 | 212.98
2018-06-06 19:30 | 215.96 | 211.43
2018-06-06 20:00 | 214.65 | 210.07
2018-06-06 20:30 | 213.24 | 208.66
2018-06-06 21:00 | 211.55 | 206.87
2018-06-06 21:30 | 211.52 | 206.79
2018-06-06 22:00 | 209.52 | 204.9
2018-06-06 22:30 | 207.09 | 202.48
2018-06-06 23:00 | 204.12 | 199.51
2018-06-06 23:30 | 202.11 | 197.44
2018-06-07 | 200.69 | 195.98
2018-06-07 00:30 | 200.32 | 195.57
2018-06-07 01:00 | 199.1 | 194.23
2018-06-07 01:30 | 198.02 | 193.15
2018-06-07 02:00 | 197.56 | 192.7
2018-06-07 02:30 | 197.17 | 192.3
2018-06-07 03:00 | 196.94 | 192.02
2018-06-07 03:30 | 196.54 | 191.56
2018-06-07 04:00 | 196.57 | 191.46
2018-06-07 04:30 | 197.2 | 192.14
2018-06-07 05:00 | 198.54 | 193.55
2018-06-07 05:30 | 200.63 | 195.73
2018-06-07 06:00 | 203.81 | 199.16
2018-06-07 06:30 | 208.03 | 203.78
2018-06-07 07:00 | 211.19 | 207.17
2018-06-07 07:30 | 214.4 | 210.6
2018-06-07 08:00 | 213.5 | 209.65
2018-06-07 08:30 | 209.7 | 205.71
2018-06-07 09:00 | 205.98 | 201.86
2018-06-07 09:30 | 202.13 | 197.83
2018-06-07 10:00 | 198.84 | 194.42
2018-06-07 10:30 | 193.04 | 188.74
2018-06-07 11:00 | 191.24 | 186.85
2018-06-07 11:30 | 190.65 | 186.27
2018-06-07 12:00 | 190.37 | 185.91
2018-06-07 12:30 | 189.21 | 184.74
2018-06-07 13:00 | 190.38 | 185.76
2018-06-07 13:30 | 191.39 | 186.72
2018-06-07 14:00 | 193.41 | 188.77
2018-06-07 14:30 | 196.32 | 191.51
2018-06-07 15:00 | 197.5 | 192.73
2018-06-07 15:30 | 198.37 | 193.68
2018-06-07 16:00 | 199.26 | 194.54
2018-06-07 16:30 | 200.89 | 196.08
2018-06-07 17:00 | 188.43 | 183.47
2018-06-07 17:30 | 173.23 | 167.17
2018-06-07 18:00 | 177.31 | 171.47
2018-06-07 18:30 | 181.32 | 175.56
2018-06-07 19:00 | 182.02 | 176.25
2018-06-07 19:30 | 180.95 | 175.02
2018-06-07 20:00 | 179.17 | 173.25
2018-06-07 20:30 | 179.64 | 173.6
2018-06-07 21:00 | 178.49 | 172.4
2018-06-07 21:30 | 177.06 | 171.3
2018-06-07 22:00 | 175.19 | 169.5
2018-06-07 22:30 | 173.2 | 167.37
2018-06-07 23:00 | 171.49 | 165.63
2018-06-07 23:30 | 170.47 | 164.66
2018-06-08 | 187.77 | 182.68
2018-06-08 00:30 | 199.95 | 194.82
2018-06-08 01:00 | 199.14 | 194.05
2018-06-08 01:30 | 198.39 | 193.28
2018-06-08 02:00 | 197.68 | 192.61
2018-06-08 02:30 | 197.34 | 192.21
2018-06-08 03:00 | 197.35 | 192.15
2018-06-08 03:30 | 197.45 | 192.26
2018-06-08 04:00 | 198.04 | 192.87
2018-06-08 04:30 | 198.68 | 193.56
2018-06-08 05:00 | 199.65 | 194.61
2018-06-08 05:30 | 201.32 | 196.36
2018-06-08 06:00 | 203.82 | 199.02
2018-06-08 06:30 | 207.83 | 203.09
2018-06-08 07:00 | 210.45 | 205.87
2018-06-08 07:30 | 212.64 | 208.25
2018-06-08 08:00 | 211.34 | 207.1
2018-06-08 08:30 | 208.24 | 203.96
2018-06-08 09:00 | 206.03 | 201.64
2018-06-08 09:30 | 202.76 | 198.32
2018-06-08 10:00 | 202.06 | 197.49
2018-06-08 10:30 | 200.18 | 195.63
2018-06-08 11:00 | 186.53 | 181.9
2018-06-08 11:30 | 165.38 | 159.3
2018-06-08 12:00 | 165.82 | 159.44
2018-06-08 12:30 | 165.3 | 158.73
2018-06-08 13:00 | 166.03 | 159.02
2018-06-08 13:30 | 167.31 | 160.02
2018-06-08 14:00 | 168.2 | 160.77
2018-06-08 14:30 | 167.77 | 161.23
2018-06-08 15:00 | 168.4 | 161.73
2018-06-08 15:30 | 168.77 | 161.88
2018-06-08 16:00 | 178.25 | 171.35
2018-06-08 16:30 | 180.53 | 173.51
2018-06-08 17:00 | 179.64 | 172.07
2018-06-08 17:30 | 179.86 | 171.83
2018-06-08 18:00 | 183.13 | 175.62
2018-06-08 18:30 | 185.35 | 177.91
2018-06-08 19:00 | 185.85 | 178.47
2018-06-08 19:30 | 185.41 | 177.86
2018-06-08 20:00 | 184.73 | 177.17
2018-06-08 20:30 | 184.58 | 176.95
2018-06-08 21:00 | 183.63 | 175.92
2018-06-08 21:30 | 181.86 | 175.09
2018-06-08 22:00 | 179.86 | 173.21
2018-06-08 22:30 | 178.93 | 171.82
2018-06-08 23:00 | 177.51 | 170.28
2018-06-08 23:30 | 176.24 | 169.17
2018-06-09 | 174.9 | 167.99
2018-06-09 00:30 | 167.09 | 160.93
2018-06-09 01:00 | 198.96 | 193.73
2018-06-09 01:30 | 198.78 | 193.44
2018-06-09 02:00 | 198.21 | 192.75
2018-06-09 02:30 | 197.99 | 192.46
2018-06-09 03:00 | 197.61 | 192.09
2018-06-09 03:30 | 197.32 | 191.8
2018-06-09 04:00 | 197.06 | 191.75
2018-06-09 04:30 | 197.4 | 192.08
2018-06-09 05:00 | 197.78 | 192.46
2018-06-09 05:30 | 198.37 | 193.1
2018-06-09 06:00 | 198.78 | 193.57
2018-06-09 06:30 | 200.13 | 195.03
2018-06-09 07:00 | 201.34 | 196.31
2018-06-09 07:30 | 202.92 | 197.9
2018-06-09 08:00 | 203.36 | 198.43
2018-06-09 08:30 | 203.43 | 198.45
2018-06-09 09:00 | 203.62 | 198.59
2018-06-09 09:30 | 202.27 | 197.21
2018-06-09 10:00 | 201.52 | 196.56
2018-06-09 10:30 | 199.33 | 194.34
2018-06-09 11:00 | 198.02 | 193.04
2018-06-09 11:30 | 197.72 | 192.73
2018-06-09 12:00 | 195.95 | 191.01
2018-06-09 12:30 | 195.17 | 190.17
2018-06-09 13:00 | 195.11 | 190.11
2018-06-09 13:30 | 195.9 | 190.88
2018-06-09 14:00 | 196.4 | 191.36
2018-06-09 14:30 | 196.6 | 191.6
2018-06-09 15:00 | 197.37 | 192.39
2018-06-09 15:30 | 199.09 | 193.85
2018-06-09 16:00 | 203.01 | 197.6
2018-06-09 16:30 | 204.54 | 199.19
2018-06-09 17:00 | 204.8 | 199.49
2018-06-09 17:30 | 206.75 | 201.54
2018-06-09 18:00 | 208.95 | 204.07
2018-06-09 18:30 | 210.49 | 205.66
2018-06-09 19:00 | 210.71 | 205.83
2018-06-09 19:30 | 209.6 | 204.67
2018-06-09 20:00 | 207.93 | 202.95
2018-06-09 20:30 | 206.79 | 201.77
2018-06-09 21:00 | 205.96 | 200.83
2018-06-09 21:30 | 205.96 | 200.7
2018-06-09 22:00 | 205.1 | 199.78
2018-06-09 22:30 | 203.09 | 197.81
2018-06-09 23:00 | 201.37 | 196.07
2018-06-09 23:30 | 200.64 | 195.15
2018-06-10 | 199.57 | 194.12
2018-06-10 00:30 | 198.93 | 193.57
2018-06-10 01:00 | 198.27 | 192.85
2018-06-10 01:30 | 198.05 | 192.63
2018-06-10 02:00 | 197.74 | 192.26
2018-06-10 02:30 | 197.76 | 192.18
2018-06-10 03:00 | 197.33 | 191.9
2018-06-10 03:30 | 196.9 | 191.4
2018-06-10 04:00 | 197 | 191.55
2018-06-10 04:30 | 197.44 | 191.95
2018-06-10 05:00 | 198.09 | 192.56
2018-06-10 05:30 | 198.47 | 193.05
2018-06-10 06:00 | 199.16 | 193.82
2018-06-10 06:30 | 200.92 | 195.69
2018-06-10 07:00 | 202.32 | 197.19
2018-06-10 07:30 | 204.13 | 199.09
2018-06-10 08:00 | 204.78 | 199.71
2018-06-10 08:30 | 203.87 | 198.74
2018-06-10 09:00 | 202.51 | 197.31
2018-06-10 09:30 | 201.35 | 196.04
2018-06-10 10:00 | 200.14 | 194.76
2018-06-10 10:30 | 198.68 | 193.32
2018-06-10 11:00 | 197.97 | 192.51
2018-06-10 11:30 | 197.81 | 192.33
2018-06-10 12:00 | 198.14 | 192.63
2018-06-10 12:30 | 198.19 | 192.74
2018-06-10 13:00 | 197.47 | 192.09
2018-06-10 13:30 | 197.57 | 192.18
2018-06-10 14:00 | 197.8 | 192.44
2018-06-10 14:30 | 198.58 | 193.32
2018-06-10 15:00 | 199.61 | 194.33
2018-06-10 15:30 | 201.11 | 195.88
2018-06-10 16:00 | 201.35 | 196.18
2018-06-10 16:30 | 202.93 | 197.78
2018-06-10 17:00 | 204.93 | 199.8
2018-06-10 17:30 | 207.08 | 202.05
2018-06-10 18:00 | 207.93 | 203.09
2018-06-10 18:30 | 209.41 | 204.6
2018-06-10 19:00 | 208.87 | 204.06
2018-06-10 19:30 | 207.83 | 202.98
2018-06-10 20:00 | 206.33 | 201.39
2018-06-10 20:30 | 205.49 | 200.48
2018-06-10 21:00 | 203.86 | 198.81
2018-06-10 21:30 | 203.23 | 198.06
2018-06-10 22:00 | 202.08 | 196.83
2018-06-10 22:30 | 200.75 | 195.43
2018-06-10 23:00 | 199.24 | 193.85
2018-06-10 23:30 | 198.83 | 193.32
2018-06-11 | 198.3 | 192.59
2018-06-11 00:30 | 197.24 | 191.59
2018-06-11 01:00 | 196.29 | 190.82
2018-06-11 01:30 | 195.2 | 189.8
2018-06-11 02:00 | 194.98 | 189.59
2018-06-11 02:30 | 195.16 | 189.77
2018-06-11 03:00 | 194.93 | 189.52
2018-06-11 03:30 | 194.83 | 189.42
2018-06-11 04:00 | 195.13 | 189.75
2018-06-11 04:30 | 195.58 | 190.2
2018-06-11 05:00 | 196.16 | 190.84
2018-06-11 05:30 | 198.16 | 192.96
2018-06-11 06:00 | 200.49 | 195.45
2018-06-11 06:30 | 205.66 | 200.81
2018-06-11 07:00 | 210.07 | 205.32
2018-06-11 07:30 | 213.63 | 209.19
2018-06-11 08:00 | 213.03 | 208.68
2018-06-11 08:30 | 209.74 | 205.3
2018-06-11 09:00 | 206.83 | 202.26
2018-06-11 09:30 | 203.71 | 199
2018-06-11 10:00 | 202.64 | 197.88
2018-06-11 10:30 | 200.71 | 195.78
2018-06-11 11:00 | 200.82 | 195.84
2018-06-11 11:30 | 201.93 | 196.82
2018-06-11 12:00 | 203.34 | 198.1
2018-06-11 12:30 | 202.41 | 197.15
2018-06-11 13:00 | 202.25 | 196.9
2018-06-11 13:30 | 202.15 | 196.76
2018-06-11 14:00 | 202.58 | 197.34
2018-06-11 14:30 | 202.9 | 197.7
2018-06-11 15:00 | 203.34 | 198.1
2018-06-11 15:30 | 204.18 | 198.95
2018-06-11 16:00 | 206.43 | 201.23
2018-06-11 16:30 | 207.13 | 201.81
2018-06-11 17:00 | 208.51 | 203.24
2018-06-11 17:30 | 210.22 | 204.93
2018-06-11 18:00 | 214.69 | 209.56
2018-06-11 18:30 | 217.72 | 212.71
2018-06-11 19:00 | 217.69 | 212.66
2018-06-11 19:30 | 216.11 | 211.04
2018-06-11 20:00 | 214.98 | 209.92
2018-06-11 20:30 | 214.14 | 209.07
2018-06-11 21:00 | 211.75 | 206.67
2018-06-11 21:30 | 210.54 | 205.34
2018-06-11 22:00 | 208.7 | 203.5
2018-06-11 22:30 | 206.82 | 201.53
2018-06-11 23:00 | 204.74 | 199.38
2018-06-11 23:30 | 203.8 | 198.44
2018-06-12 | 202.52 | 197.15
2018-06-12 00:30 | 201.94 | 196.5
2018-06-12 01:00 | 201.34 | 195.95
2018-06-12 01:30 | 200.93 | 195.62
2018-06-12 02:00 | 200.93 | 195.6
2018-06-12 02:30 | 200.38 | 195.08
2018-06-12 03:00 | 200.52 | 195.2
2018-06-12 03:30 | 200.02 | 194.65
2018-06-12 04:00 | 200.14 | 194.8
2018-06-12 04:30 | 201.05 | 195.71
2018-06-12 05:00 | 202.04 | 196.79
2018-06-12 05:30 | 204.08 | 198.93
2018-06-12 06:00 | 206.78 | 201.58
2018-06-12 06:30 | 211.02 | 206.02
2018-06-12 07:00 | 213.6 | 208.84
2018-06-12 07:30 | 216.07 | 211.47
2018-06-12 08:00 | 215.17 | 210.61
2018-06-12 08:30 | 212.43 | 207.72
2018-06-12 09:00 | 209.71 | 204.94
2018-06-12 09:30 | 206.14 | 201.24
2018-06-12 10:00 | 205.15 | 200.27
2018-06-12 10:30 | 203.64 | 198.69
2018-06-12 11:00 | 202.63 | 197.74
2018-06-12 11:30 | 201.02 | 196.08
2018-06-12 12:00 | 200.38 | 195.46
2018-06-12 12:30 | 200.17 | 195.18
2018-06-12 13:00 | 199.69 | 194.73
2018-06-12 13:30 | 200.47 | 195.34
2018-06-12 14:00 | 201.12 | 196.05
2018-06-12 14:30 | 201.8 | 196.78
2018-06-12 15:00 | 202.82 | 197.74
2018-06-12 15:30 | 203.76 | 198.73
2018-06-12 16:00 | 205.12 | 200.13
2018-06-12 16:30 | 206.25 | 201.21
2018-06-12 17:00 | 207.47 | 202.42
2018-06-12 17:30 | 209.04 | 203.91
2018-06-12 18:00 | 213.27 | 208.24
2018-06-12 18:30 | 215.22 | 210.3
2018-06-12 19:00 | 215.36 | 210.47
2018-06-12 19:30 | 213.74 | 208.85
2018-06-12 20:00 | 212.37 | 207.41
2018-06-12 20:30 | 211 | 206.03
2018-06-12 21:00 | 209.37 | 204.39
2018-06-12 21:30 | 208.45 | 203.33
2018-06-12 22:00 | 206.38 | 201.28
2018-06-12 22:30 | 204.29 | 199.15
2018-06-12 23:00 | 202.24 | 197.1
2018-06-12 23:30 | 200.77 | 195.66
2018-06-13 | 199.16 | 194.06
2018-06-13 00:30 | 198.08 | 193
2018-06-13 01:00 | 199.78 | 194.46
2018-06-13 01:30 | 201.49 | 195.98
2018-06-13 02:00 | 203.2 | 197.49
2018-06-13 02:30 | 202.19 | 196.53
2018-06-13 03:00 | 201.64 | 196.02
2018-06-13 03:30 | 200.93 | 195.25
2018-06-13 04:00 | 201.52 | 195.78
2018-06-13 04:30 | 202.26 | 196.51
2018-06-13 05:00 | 203.71 | 197.98
2018-06-13 05:30 | 206.16 | 200.51
2018-06-13 06:00 | 208.32 | 202.88
2018-06-13 06:30 | 211.77 | 206.57
2018-06-13 07:00 | 215.19 | 210.17
2018-06-13 07:30 | 217.92 | 213.13
2018-06-13 08:00 | 217.56 | 212.85
2018-06-13 08:30 | 216.26 | 211.47
2018-06-13 09:00 | 213.08 | 208.36
2018-06-13 09:30 | 211.26 | 206.59
2018-06-13 10:00 | 210.73 | 206.07
2018-06-13 10:30 | 208.72 | 204.02
2018-06-13 11:00 | 207.1 | 202.41
2018-06-13 11:30 | 206.41 | 201.64
2018-06-13 12:00 | 206.6 | 201.88
2018-06-13 12:30 | 205.86 | 201.11
2018-06-13 13:00 | 205.74 | 200.95
2018-06-13 13:30 | 205.35 | 200.5
2018-06-13 14:00 | 205.35 | 200.62
2018-06-13 14:30 | 199.73 | 195.67
2018-06-13 15:00 | 193.21 | 190.3
2018-06-13 15:30 | 190.73 | 187.86
2018-06-13 16:00 | 202.47 | 198.01
2018-06-13 16:30 | 204 | 199.51
2018-06-13 17:00 | 205.12 | 200.57
2018-06-13 17:30 | 211.2 | 206.38
2018-06-13 18:00 | 216.58 | 211.93
2018-06-13 18:30 | 218.77 | 214.23
2018-06-13 19:00 | 218.36 | 213.83
2018-06-13 19:30 | 216.69 | 212.12
2018-06-13 20:00 | 215.18 | 210.58
2018-06-13 20:30 | 214.22 | 209.57
2018-06-13 21:00 | 212.34 | 207.61
2018-06-13 21:30 | 211.22 | 206.45
2018-06-13 22:00 | 209.07 | 204.18
2018-06-13 22:30 | 206.48 | 201.6
2018-06-13 23:00 | 204 | 199.06
2018-06-13 23:30 | 203.04 | 198.03
2018-06-14 | 201.81 | 196.73
2018-06-14 00:30 | 201.15 | 195.95
2018-06-14 01:00 | 200.27 | 195.07
2018-06-14 01:30 | 200.01 | 194.82
2018-06-14 02:00 | 199.29 | 194.07
2018-06-14 02:30 | 198.89 | 193.65
2018-06-14 03:00 | 198.91 | 193.58
2018-06-14 03:30 | 198.89 | 193.57
2018-06-14 04:00 | 198.8 | 193.51
2018-06-14 04:30 | 199.65 | 194.42
2018-06-14 05:00 | 200.19 | 195.03
2018-06-14 05:30 | 202.24 | 197.18
2018-06-14 06:00 | 205.12 | 200.23
2018-06-14 06:30 | 209.65 | 204.85
2018-06-14 07:00 | 212.72 | 208.13
2018-06-14 07:30 | 216.04 | 211.61
2018-06-14 08:00 | 215.91 | 211.47
2018-06-14 08:30 | 213.29 | 208.73
2018-06-14 09:00 | 210.42 | 205.75
2018-06-14 09:30 | 206.31 | 201.64
2018-06-14 10:00 | 205.87 | 201.11
2018-06-14 10:30 | 204.03 | 199.28
2018-06-14 11:00 | 203.23 | 198.56
2018-06-14 11:30 | 203.25 | 198.48
2018-06-14 12:00 | 203.02 | 198.2
2018-06-14 12:30 | 201.44 | 196.62
2018-06-14 13:00 | 200.72 | 195.83
2018-06-14 13:30 | 199.85 | 194.92
2018-06-14 14:00 | 200.26 | 195.43
2018-06-14 14:30 | 201.21 | 196.4
2018-06-14 15:00 | 201.22 | 196.4
2018-06-14 15:30 | 201.34 | 196.51
2018-06-14 16:00 | 203.06 | 198.18
2018-06-14 16:30 | 204.25 | 199.31
2018-06-14 17:00 | 205.95 | 200.95
2018-06-14 17:30 | 208.98 | 204.03
2018-06-14 18:00 | 213.5 | 208.8
2018-06-14 18:30 | 217.53 | 212.95
2018-06-14 19:00 | 218.59 | 214.02
2018-06-14 19:30 | 217.02 | 212.41
2018-06-14 20:00 | 215.79 | 211.19
2018-06-14 20:30 | 215.06 | 210.43
2018-06-14 21:00 | 213.27 | 208.59
2018-06-14 21:30 | 211.74 | 207.02
2018-06-14 22:00 | 210.03 | 205.21
2018-06-14 22:30 | 207.28 | 202.48
2018-06-14 23:00 | 205.37 | 200.49
2018-06-14 23:30 | 203.59 | 198.76
2018-06-15 | 202.41 | 197.44
2018-06-15 00:30 | 201.86 | 196.78
2018-06-15 01:00 | 200.86 | 195.78
2018-06-15 01:30 | 199.88 | 194.81
2018-06-15 02:00 | 199.1 | 194.02
2018-06-15 02:30 | 198.93 | 193.86
2018-06-15 03:00 | 198.45 | 193.24
2018-06-15 03:30 | 198.52 | 193.3
2018-06-15 04:00 | 198.61 | 193.42
2018-06-15 04:30 | 199.42 | 194.32
2018-06-15 05:00 | 200.98 | 195.94
2018-06-15 05:30 | 202.69 | 197.89
2018-06-15 06:00 | 205.88 | 201.34
2018-06-15 06:30 | 209.97 | 205.83
2018-06-15 07:00 | 213.38 | 209.51
2018-06-15 07:30 | 216.55 | 212.76
2018-06-15 08:00 | 216.36 | 212.54
2018-06-15 08:30 | 213.11 | 209.13
2018-06-15 09:00 | 209.75 | 205.6
2018-06-15 09:30 | 205.91 | 201.58
2018-06-15 10:00 | 204.56 | 199.99
2018-06-15 10:30 | 202.27 | 197.49
2018-06-15 11:00 | 200.5 | 195.81
2018-06-15 11:30 | 199.38 | 194.67
2018-06-15 12:00 | 198.45 | 193.74
2018-06-15 12:30 | 198.01 | 193.14
2018-06-15 13:00 | 197.81 | 192.79
2018-06-15 13:30 | 197.33 | 192.27
2018-06-15 14:00 | 197.79 | 192.7
2018-06-15 14:30 | 198.18 | 193.1
2018-06-15 15:00 | 199.19 | 194.1
2018-06-15 15:30 | 200.58 | 195.49
2018-06-15 16:00 | 201.87 | 196.75
2018-06-15 16:30 | 203.67 | 198.64
2018-06-15 17:00 | 205.8 | 200.76
2018-06-15 17:30 | 208.56 | 203.54
2018-06-15 18:00 | 213.02 | 208.14
2018-06-15 18:30 | 216.6 | 211.92
2018-06-15 19:00 | 216.71 | 212.1
2018-06-15 19:30 | 216.02 | 211.42
2018-06-15 20:00 | 215.6 | 210.97
2018-06-15 20:30 | 215.19 | 210.6
2018-06-15 21:00 | 214.04 | 209.43
2018-06-15 21:30 | 213.52 | 208.79
2018-06-15 22:00 | 212.08 | 207.28
2018-06-15 22:30 | 209.97 | 205.06
2018-06-15 23:00 | 207.97 | 202.95
2018-06-15 23:30 | 206.63 | 201.52
2018-06-16 | 205.27 | 200.15
2018-06-16 00:30 | 203.77 | 198.79
2018-06-16 01:00 | 202.21 | 197.38
2018-06-16 01:30 | 201.33 | 196.54
2018-06-16 02:00 | 200.86 | 196.07
2018-06-16 02:30 | 200.87 | 195.93
2018-06-16 03:00 | 200.79 | 195.83
2018-06-16 03:30 | 201.14 | 196.18
2018-06-16 04:00 | 201.46 | 196.52
2018-06-16 04:30 | 201.72 | 196.8
2018-06-16 05:00 | 202.19 | 197.32
2018-06-16 05:30 | 204.04 | 199.19
2018-06-16 06:00 | 205.73 | 200.95
2018-06-16 06:30 | 208.66 | 204.06
2018-06-16 07:00 | 211.03 | 206.49
2018-06-16 07:30 | 212.24 | 207.79
2018-06-16 08:00 | 212.5 | 208.18
2018-06-16 08:30 | 210.61 | 206.29
2018-06-16 09:00 | 208.06 | 203.64
2018-06-16 09:30 | 205.48 | 200.93
2018-06-16 10:00 | 202.52 | 197.83
2018-06-16 10:30 | 199.96 | 195.2
2018-06-16 11:00 | 197.77 | 192.96
2018-06-16 11:30 | 196.31 | 191.49
2018-06-16 12:00 | 194.93 | 190.17
2018-06-16 12:30 | 194.39 | 189.62
2018-06-16 13:00 | 194.1 | 189.28
2018-06-16 13:30 | 194.09 | 189.24
2018-06-16 14:00 | 194.58 | 189.71
2018-06-16 14:30 | 194.41 | 189.55
2018-06-16 15:00 | 195.14 | 190.26
2018-06-16 15:30 | 196.88 | 191.93
2018-06-16 16:00 | 199.4 | 194.12
2018-06-16 16:30 | 203.21 | 197.87
2018-06-16 17:00 | 175.81 | 168.8
2018-06-16 17:30 | 184.1 | 175.98
2018-06-16 18:00 | 189.36 | 182.32
2018-06-16 18:30 | 190.87 | 184.27
2018-06-16 19:00 | 187.4 | 181.6
2018-06-16 19:30 | 187.48 | 181.51
2018-06-16 20:00 | 186.83 | 180.91
2018-06-16 20:30 | 182.6 | 177.56
2018-06-16 21:00 | 210.48 | 205.91
2018-06-16 21:30 | 210.2 | 205.74
2018-06-16 22:00 | 209 | 204.49
2018-06-16 22:30 | 206.65 | 202.02
2018-06-16 23:00 | 205.1 | 200.29
2018-06-16 23:30 | 203.96 | 199.1
2018-06-17 | 202.94 | 197.95
2018-06-17 00:30 | 201.96 | 196.91
2018-06-17 01:00 | 201.39 | 196.21
2018-06-17 01:30 | 200.96 | 195.89
2018-06-17 02:00 | 201.01 | 196.01
2018-06-17 02:30 | 201.02 | 195.9
2018-06-17 03:00 | 200.55 | 195.42
2018-06-17 03:30 | 199.87 | 194.8
2018-06-17 04:00 | 199.52 | 194.54
2018-06-17 04:30 | 199.7 | 194.76
2018-06-17 05:00 | 200.38 | 195.46
2018-06-17 05:30 | 201.32 | 196.44
2018-06-17 06:00 | 202.34 | 197.51
2018-06-17 06:30 | 204.08 | 199.4
2018-06-17 07:00 | 206.48 | 201.97
2018-06-17 07:30 | 209.32 | 204.94
2018-06-17 08:00 | 210.35 | 206.01
2018-06-17 08:30 | 209.65 | 205.28
2018-06-17 09:00 | 207.81 | 203.35
2018-06-17 09:30 | 205.21 | 200.66
2018-06-17 10:00 | 203.36 | 198.73
2018-06-17 10:30 | 200.97 | 196.29
2018-06-17 11:00 | 198.4 | 193.73
2018-06-17 11:30 | 195.82 | 191.19
2018-06-17 12:00 | 194.3 | 189.67
2018-06-17 12:30 | 194.4 | 189.66
2018-06-17 13:00 | 193.82 | 189.1
2018-06-17 13:30 | 193.9 | 189.14
2018-06-17 14:00 | 198.01 | 192.96
2018-06-17 14:30 | 198.19 | 193.17
2018-06-17 15:00 | 198.44 | 193.45
2018-06-17 15:30 | 198.53 | 193.69
2018-06-17 16:00 | 200.51 | 195.67
2018-06-17 16:30 | 204 | 199.21
2018-06-17 17:00 | 207.64 | 202.74
2018-06-17 17:30 | 210.06 | 205
2018-06-17 18:00 | 187.31 | 180.91
2018-06-17 18:30 | 189.69 | 183.29
2018-06-17 19:00 | 190.31 | 183.93
2018-06-17 19:30 | 189.25 | 182.71
2018-06-17 20:00 | 188.15 | 181.44
2018-06-17 20:30 | 187.18 | 180.42
2018-06-17 21:00 | 185.79 | 178.79
2018-06-17 21:30 | 184.7 | 177.72
2018-06-17 22:00 | 182.6 | 175.39
2018-06-17 22:30 | 179.97 | 172.28
2018-06-17 23:00 | 177.74 | 169.89
2018-06-17 23:30 | 175.81 | 168.06
2018-06-18 | 174.18 | 166.68
2018-06-18 00:30 | 173.43 | 166.12
2018-06-18 01:00 | 191.44 | 185.8
2018-06-18 01:30 | 203.62 | 198.45
2018-06-18 02:00 | 203.25 | 198.12
2018-06-18 02:30 | 203.21 | 198.04
2018-06-18 03:00 | 202.83 | 197.67
2018-06-18 03:30 | 203.05 | 197.93
2018-06-18 04:00 | 203.55 | 198.46
2018-06-18 04:30 | 203.91 | 198.93
2018-06-18 05:00 | 205.3 | 200.45
2018-06-18 05:30 | 207.51 | 202.97
2018-06-18 06:00 | 210.35 | 206.05
2018-06-18 06:30 | 216 | 211.97
2018-06-18 07:00 | 220.05 | 216.35
2018-06-18 07:30 | 224.49 | 221.05
2018-06-18 08:00 | 222.91 | 219.49
2018-06-18 08:30 | 217.68 | 214.22
2018-06-18 09:00 | 214.29 | 210.59
2018-06-18 09:30 | 209.43 | 205.43
2018-06-18 10:00 | 206.93 | 202.86
2018-06-18 10:30 | 203.34 | 199.35
2018-06-18 11:00 | 201.55 | 197.55
2018-06-18 11:30 | 200.38 | 196.37
2018-06-18 12:00 | 199.75 | 195.74
2018-06-18 12:30 | 199.77 | 195.45
2018-06-18 13:00 | 201.59 | 196.96
2018-06-18 13:30 | 202 | 197.26
2018-06-18 14:00 | 202.09 | 197.42
2018-06-18 14:30 | 203.34 | 198.6
2018-06-18 15:00 | 202.44 | 197.67
2018-06-18 15:30 | 204.09 | 199.37
2018-06-18 16:00 | 206.12 | 201.51
2018-06-18 16:30 | 190.54 | 184.94
2018-06-18 17:00 | 181.59 | 174.45
2018-06-18 17:30 | 189.84 | 184.51
2018-06-18 18:00 | 191.46 | 189.26
2018-06-18 18:30 | 189.5 | 187.12
2018-06-18 19:00 | 190 | 187.57
2018-06-18 19:30 | 191.42 | 189
2018-06-18 20:00 | 192.04 | 189.58
2018-06-18 20:30 | 193.14 | 190.68
2018-06-18 21:00 | 195.69 | 189.6
2018-06-18 21:30 | 199.66 | 193.35
2018-06-18 22:00 | 197.52 | 191.08
2018-06-18 22:30 | 194.69 | 188.04
2018-06-18 23:00 | 191.64 | 184.96
2018-06-18 23:30 | 189.68 | 182.93
2018-06-19 | 175.06 | 168.75
2018-06-19 00:30 | 187.89 | 183.19
2018-06-19 01:00 | 202.47 | 198.09
2018-06-19 01:30 | 200.65 | 196.43
2018-06-19 02:00 | 200.27 | 195.97
2018-06-19 02:30 | 199.91 | 195.65
2018-06-19 03:00 | 199.73 | 195.43
2018-06-19 03:30 | 199.55 | 195.16
2018-06-19 04:00 | 199.43 | 195.12
2018-06-19 04:30 | 200.79 | 196.47
2018-06-19 05:00 | 202.17 | 197.95
2018-06-19 05:30 | 205.19 | 201.03
2018-06-19 06:00 | 208.6 | 204.68
2018-06-19 06:30 | 214.6 | 211
2018-06-19 07:00 | 202.59 | 200.11
2018-06-19 07:30 | 207.21 | 204.98
2018-06-19 08:00 | 210.06 | 208.75
2018-06-19 08:30 | 212.46 | 211.04
2018-06-19 09:00 | 208.38 | 205.8
2018-06-19 09:30 | 207.42 | 204.27
2018-06-19 10:00 | 206.19 | 202.88
2018-06-19 10:30 | 205.14 | 201.58
2018-06-19 11:00 | 204.05 | 200.2
2018-06-19 11:30 | 202.78 | 198.7
2018-06-19 12:00 | 202.69 | 198.33
2018-06-19 12:30 | 202.49 | 198.08
2018-06-19 13:00 | 202.81 | 198.24
2018-06-19 13:30 | 202.76 | 198.17
2018-06-19 14:00 | 202.35 | 197.94
2018-06-19 14:30 | 202.58 | 198.2
2018-06-19 15:00 | 202.13 | 197.78
2018-06-19 15:30 | 202.6 | 198.31
2018-06-19 16:00 | 204.42 | 200.3
2018-06-19 16:30 | 207.64 | 203.34
2018-06-19 17:00 | 213.47 | 208.93
2018-06-19 17:30 | 194.66 | 187.84
2018-06-19 18:00 | 189.25 | 180.86
2018-06-19 18:30 | 186.6 | 181.23
2018-06-19 19:00 | 188.07 | 182.93
2018-06-19 19:30 | 189.71 | 184.52
2018-06-19 20:00 | 196.53 | 189.15
2018-06-19 20:30 | 201.4 | 193.52
2018-06-19 21:00 | 200.14 | 192.75
2018-06-19 21:30 | 178.54 | 172.63
2018-06-19 22:00 | 201.06 | 196.41
2018-06-19 22:30 | 216.96 | 212.76
2018-06-19 23:00 | 213.68 | 209.26
2018-06-19 23:30 | 211.81 | 207.33
2018-06-20 | 210.45 | 205.9
2018-06-20 00:30 | 209.55 | 204.94
2018-06-20 01:00 | 208.57 | 203.77
2018-06-20 01:30 | 207.6 | 202.77
2018-06-20 02:00 | 206.98 | 202.29
2018-06-20 02:30 | 207.08 | 202.41
2018-06-20 03:00 | 206.54 | 201.8
2018-06-20 03:30 | 206.5 | 201.7
2018-06-20 04:00 | 206.9 | 202.07
2018-06-20 04:30 | 207.94 | 203.17
2018-06-20 05:00 | 209.76 | 205.08
2018-06-20 05:30 | 212.07 | 207.66
2018-06-20 06:00 | 215.16 | 211.09
2018-06-20 06:30 | 220.56 | 216.87
2018-06-20 07:00 | 224.22 | 220.84
2018-06-20 07:30 | 227.64 | 224.53
2018-06-20 08:00 | 227.37 | 224.27
2018-06-20 08:30 | 224.09 | 220.78
2018-06-20 09:00 | 220.2 | 216.6
2018-06-20 09:30 | 216.22 | 212.31
2018-06-20 10:00 | 212.78 | 208.75
2018-06-20 10:30 | 209.61 | 205.28
2018-06-20 11:00 | 207.37 | 202.8
2018-06-20 11:30 | 206.11 | 201.48
2018-06-20 12:00 | 205.11 | 200.44
2018-06-20 12:30 | 204.02 | 199.29
2018-06-20 13:00 | 204.17 | 199.24
2018-06-20 13:30 | 203.56 | 198.59
2018-06-20 14:00 | 203.64 | 198.74
2018-06-20 14:30 | 203.82 | 198.96
2018-06-20 15:00 | 201.49 | 196.72
2018-06-20 15:30 | 201.53 | 196.92
2018-06-20 16:00 | 202.4 | 197.8
2018-06-20 16:30 | 203.85 | 199.12
2018-06-20 17:00 | 208.61 | 203.86
2018-06-20 17:30 | 212.49 | 207.86
2018-06-20 18:00 | 219.31 | 214.83
2018-06-20 18:30 | 223.07 | 219
2018-06-20 19:00 | 223.35 | 219.33
2018-06-20 19:30 | 221.78 | 217.74
2018-06-20 20:00 | 220.75 | 216.69
2018-06-20 20:30 | 220.12 | 215.96
2018-06-20 21:00 | 218.08 | 213.86
2018-06-20 21:30 | 218.48 | 214
2018-06-20 22:00 | 214.11 | 209.67
2018-06-20 22:30 | 211.47 | 206.91
2018-06-20 23:00 | 209.5 | 204.88
2018-06-20 23:30 | 207.53 | 202.86
2018-06-21 | 206.21 | 201.49
2018-06-21 00:30 | 205.46 | 200.6
2018-06-21 01:00 | 204.22 | 199.32
2018-06-21 01:30 | 203.5 | 198.73
2018-06-21 02:00 | 202.92 | 198.15
2018-06-21 02:30 | 202.39 | 197.67
2018-06-21 03:00 | 202.04 | 197.28
2018-06-21 03:30 | 202 | 197.23
2018-06-21 04:00 | 202.57 | 197.86
2018-06-21 04:30 | 203.28 | 198.62
2018-06-21 05:00 | 204.88 | 200.3
2018-06-21 05:30 | 207.85 | 203.32
2018-06-21 06:00 | 211.59 | 207
2018-06-21 06:30 | 216.95 | 212.63
2018-06-21 07:00 | 221.12 | 217.07
2018-06-21 07:30 | 224.32 | 220.44
2018-06-21 08:00 | 223.43 | 219.46
2018-06-21 08:30 | 219.42 | 215.22
2018-06-21 09:00 | 214.27 | 209.99
2018-06-21 09:30 | 209.46 | 205.07
2018-06-21 10:00 | 206.87 | 202.31
2018-06-21 10:30 | 203.91 | 199.28
2018-06-21 11:00 | 202.97 | 198.28
2018-06-21 11:30 | 202.45 | 197.63
2018-06-21 12:00 | 200.7 | 195.92
2018-06-21 12:30 | 199.6 | 194.62
2018-06-21 13:00 | 199.67 | 194.63
2018-06-21 13:30 | 199.65 | 194.58
2018-06-21 14:00 | 199.98 | 194.98
2018-06-21 14:30 | 200.4 | 195.5
2018-06-21 15:00 | 200.02 | 195.09
2018-06-21 15:30 | 201.11 | 196.21
2018-06-21 16:00 | 202.2 | 197.45
2018-06-21 16:30 | 203.65 | 198.9
2018-06-21 17:00 | 206.3 | 201.52
2018-06-21 17:30 | 209.12 | 204.42
2018-06-21 18:00 | 214.41 | 209.95
2018-06-21 18:30 | 218.19 | 213.89
2018-06-21 19:00 | 219.22 | 214.97
2018-06-21 19:30 | 219.13 | 214.79
2018-06-21 20:00 | 218.22 | 213.82
2018-06-21 20:30 | 216.91 | 212.54
2018-06-21 21:00 | 215.13 | 210.75
2018-06-21 21:30 | 214.43 | 210.01
2018-06-21 22:00 | 212.21 | 207.74
2018-06-21 22:30 | 210.09 | 205.46
2018-06-21 23:00 | 207.44 | 202.84
2018-06-21 23:30 | 205.68 | 200.9
2018-06-22 | 204.16 | 199.24
2018-06-22 00:30 | 203.24 | 198.31
2018-06-22 01:00 | 201.94 | 197.15
2018-06-22 01:30 | 201.32 | 196.55
2018-06-22 02:00 | 200.71 | 195.84
2018-06-22 02:30 | 201.59 | 196.6
2018-06-22 03:00 | 201.02 | 196.01
2018-06-22 03:30 | 200.47 | 195.53
2018-06-22 04:00 | 201.35 | 196.41
2018-06-22 04:30 | 202.1 | 197.2
2018-06-22 05:00 | 203.39 | 198.6
2018-06-22 05:30 | 205.89 | 201.17
2018-06-22 06:00 | 209.15 | 204.52
2018-06-22 06:30 | 214.3 | 209.87
2018-06-22 07:00 | 218.42 | 214.24
2018-06-22 07:30 | 221.6 | 217.65
2018-06-22 08:00 | 221.26 | 217.38
2018-06-22 08:30 | 217.06 | 213.02
2018-06-22 09:00 | 212.99 | 208.76
2018-06-22 09:30 | 207.78 | 203.49
2018-06-22 10:00 | 205.44 | 201.09
2018-06-22 10:30 | 201.92 | 197.41
2018-06-22 11:00 | 200.83 | 196.37
2018-06-22 11:30 | 199.85 | 195.28
2018-06-22 12:00 | 200.21 | 195.23
2018-06-22 12:30 | 199.57 | 194.35
2018-06-22 13:00 | 199.78 | 194.41
2018-06-22 13:30 | 199 | 193.58
2018-06-22 14:00 | 199.15 | 193.71
2018-06-22 14:30 | 199.49 | 194.03
2018-06-22 15:00 | 200.88 | 195.5
2018-06-22 15:30 | 201.62 | 196.27
2018-06-22 16:00 | 202.07 | 196.96
2018-06-22 16:30 | 204.2 | 199.06
2018-06-22 17:00 | 200.32 | 194.12
2018-06-22 17:30 | 175.19 | 166.62
2018-06-22 18:00 | 189.76 | 181.02
2018-06-22 18:30 | 193.69 | 185.34
2018-06-22 19:00 | 193.76 | 185.57
2018-06-22 19:30 | 192.15 | 183.8
2018-06-22 20:00 | 191.84 | 183.16
2018-06-22 20:30 | 190.93 | 182.09
2018-06-22 21:00 | 190.14 | 181.26
2018-06-22 21:30 | 190.36 | 181.76
2018-06-22 22:00 | 189.06 | 180.29
2018-06-22 22:30 | 187.59 | 178.37
2018-06-22 23:00 | 187.7 | 180.64
2018-06-22 23:30 | 204.43 | 199.22
2018-06-23 | 203.22 | 197.97
2018-06-23 00:30 | 202.9 | 197.63
2018-06-23 01:00 | 201.7 | 196.24
2018-06-23 01:30 | 201.53 | 195.99
2018-06-23 02:00 | 201.16 | 195.61
2018-06-23 02:30 | 200.51 | 195.05
2018-06-23 03:00 | 200.13 | 194.66
2018-06-23 03:30 | 199.94 | 194.45
2018-06-23 04:00 | 200.24 | 194.76
2018-06-23 04:30 | 200.36 | 194.92
2018-06-23 05:00 | 200.93 | 195.56
2018-06-23 05:30 | 202.1 | 196.9
2018-06-23 06:00 | 203.05 | 197.93
2018-06-23 06:30 | 205.26 | 200.42
2018-06-23 07:00 | 207.46 | 202.85
2018-06-23 07:30 | 210.53 | 205.9
2018-06-23 08:00 | 211.25 | 206.66
2018-06-23 08:30 | 209.7 | 205.04
2018-06-23 09:00 | 207.11 | 202.35
2018-06-23 09:30 | 205.05 | 200.14
2018-06-23 10:00 | 202.84 | 197.79
2018-06-23 10:30 | 200.66 | 195.38
2018-06-23 11:00 | 199.19 | 193.67
2018-06-23 11:30 | 198.35 | 192.71
2018-06-23 12:00 | 197.07 | 191.56
2018-06-23 12:30 | 196.38 | 190.85
2018-06-23 13:00 | 196.58 | 191.07
2018-06-23 13:30 | 196.85 | 191.36
2018-06-23 14:00 | 196.27 | 190.71
2018-06-23 14:30 | 195.94 | 190.36
2018-06-23 15:00 | 195.84 | 190.26
2018-06-23 15:30 | 196.91 | 191.37
2018-06-23 16:00 | 198.22 | 192.75
2018-06-23 16:30 | 199.59 | 194.18
2018-06-23 17:00 | 201.55 | 196.32
2018-06-23 17:30 | 205.17 | 200.32
2018-06-23 18:00 | 209.33 | 204.74
2018-06-23 18:30 | 210.99 | 206.86
2018-06-23 19:00 | 211.03 | 206.91
2018-06-23 19:30 | 209.57 | 205.41
2018-06-23 20:00 | 209.12 | 204.89
2018-06-23 20:30 | 209.58 | 205.17
2018-06-23 21:00 | 208.76 | 204.27
2018-06-23 21:30 | 207.58 | 203.08
2018-06-23 22:00 | 205.32 | 200.72
2018-06-23 22:30 | 203.05 | 198.28
2018-06-23 23:00 | 201.49 | 196.55
2018-06-23 23:30 | 201.04 | 195.87
2018-06-24 | 199.9 | 194.6
2018-06-24 00:30 | 198.65 | 193.44
2018-06-24 01:00 | 197.51 | 192.23
2018-06-24 01:30 | 197.09 | 191.73
2018-06-24 02:00 | 197.88 | 192.37
2018-06-24 02:30 | 197.58 | 192.07
2018-06-24 03:00 | 196.85 | 191.33
2018-06-24 03:30 | 197.07 | 191.52
2018-06-24 04:00 | 197.35 | 191.77
2018-06-24 04:30 | 198.01 | 192.47
2018-06-24 05:00 | 198.23 | 192.81
2018-06-24 05:30 | 198.75 | 193.46
2018-06-24 06:00 | 199.67 | 194.51
2018-06-24 06:30 | 201.54 | 196.66
2018-06-24 07:00 | 203.54 | 198.79
2018-06-24 07:30 | 205.93 | 201.25
2018-06-24 08:00 | 206.94 | 202.26
2018-06-24 08:30 | 206.71 | 202
2018-06-24 09:00 | 205.25 | 200.5
2018-06-24 09:30 | 202.01 | 197.12
2018-06-24 10:00 | 200.36 | 195.4
2018-06-24 10:30 | 198.49 | 193.41
2018-06-24 11:00 | 196.63 | 191.44
2018-06-24 11:30 | 196.49 | 191.21
2018-06-24 12:00 | 196.24 | 190.85
2018-06-24 12:30 | 195.44 | 189.92
2018-06-24 13:00 | 195.47 | 190
2018-06-24 13:30 | 194.88 | 189.45
2018-06-24 14:00 | 195.27 | 189.69
2018-06-24 14:30 | 195.71 | 190.23
2018-06-24 15:00 | 196.64 | 191.16
2018-06-24 15:30 | 196.93 | 191.39
2018-06-24 16:00 | 197.98 | 192.49
2018-06-24 16:30 | 200.29 | 194.89
2018-06-24 17:00 | 202.1 | 196.86
2018-06-24 17:30 | 205.02 | 201.78
2018-06-24 18:00 | 213.43 | 212.35
2018-06-24 18:30 | 212.08 | 211.01
2018-06-24 19:00 | 212.4 | 211.29
2018-06-24 19:30 | 213.08 | 211.92
2018-06-24 20:00 | 213.95 | 212.76
2018-06-24 20:30 | 215.4 | 214.17
2018-06-24 21:00 | 216.33 | 215.12
2018-06-24 21:30 | 206.32 | 202.77
2018-06-24 22:00 | 206.12 | 201.48
2018-06-24 22:30 | 204.83 | 199.97
2018-06-24 23:00 | 202.33 | 197.26
2018-06-24 23:30 | 201.49 | 196.24
2018-06-25 | 199.99 | 194.54
2018-06-25 00:30 | 199.82 | 194.28
2018-06-25 01:00 | 199.67 | 193.98
2018-06-25 01:30 | 200.03 | 194.2
2018-06-25 02:00 | 199.02 | 193.23
2018-06-25 02:30 | 197.91 | 192.19
2018-06-25 03:00 | 197.62 | 191.89
2018-06-25 03:30 | 197.93 | 192.21
2018-06-25 04:00 | 197.77 | 192.09
2018-06-25 04:30 | 199.37 | 193.77
2018-06-25 05:00 | 201.54 | 195.98
2018-06-25 05:30 | 203.86 | 198.53
2018-06-25 06:00 | 206.7 | 201.81
2018-06-25 06:30 | 211.1 | 206.93
2018-06-25 07:00 | 215.57 | 211.67
2018-06-25 07:30 | 218.39 | 214.94
2018-06-25 08:00 | 219.68 | 216.27
2018-06-25 08:30 | 217.73 | 214.22
2018-06-25 09:00 | 213.56 | 209.86
2018-06-25 09:30 | 209.66 | 205.61
2018-06-25 10:00 | 207.51 | 203.27
2018-06-25 10:30 | 205.1 | 200.77
2018-06-25 11:00 | 203.52 | 199.14
2018-06-25 11:30 | 202.28 | 197.75
2018-06-25 12:00 | 201.29 | 196.72
2018-06-25 12:30 | 199.98 | 195.39
2018-06-25 13:00 | 198.74 | 194.1
2018-06-25 13:30 | 198.37 | 193.74
2018-06-25 14:00 | 198.4 | 193.81
2018-06-25 14:30 | 198.31 | 193.68
2018-06-25 15:00 | 198.48 | 193.77
2018-06-25 15:30 | 199.89 | 195.14
2018-06-25 16:00 | 200.52 | 195.99
2018-06-25 16:30 | 201.38 | 196.91
2018-06-25 17:00 | 203.72 | 199.32
2018-06-25 17:30 | 207.61 | 203.26
2018-06-25 18:00 | 213.19 | 209.34
2018-06-25 18:30 | 216.84 | 213.39
2018-06-25 19:00 | 217.11 | 213.78
2018-06-25 19:30 | 215.77 | 212.5
2018-06-25 20:00 | 214.16 | 210.81
2018-06-25 20:30 | 213.13 | 209.66
2018-06-25 21:00 | 211.12 | 207.42
2018-06-25 21:30 | 210.48 | 206.52
2018-06-25 22:00 | 208.89 | 204.71
2018-06-25 22:30 | 206.54 | 201.93
2018-06-25 23:00 | 204.05 | 199.34
2018-06-25 23:30 | 202.81 | 197.94
2018-06-26 | 201.26 | 196.2
2018-06-26 00:30 | 200.95 | 195.8
2018-06-26 01:00 | 199.73 | 194.47
2018-06-26 01:30 | 199.53 | 194.21
2018-06-26 02:00 | 198.51 | 193.17
2018-06-26 02:30 | 198.36 | 192.95
2018-06-26 03:00 | 198.77 | 193.27
2018-06-26 03:30 | 198.71 | 193.21
2018-06-26 04:00 | 198.73 | 193.31
2018-06-26 04:30 | 198.79 | 193.5
2018-06-26 05:00 | 199.59 | 194.46
2018-06-26 05:30 | 201.76 | 196.81
2018-06-26 06:00 | 204.32 | 199.89
2018-06-26 06:30 | 208.5 | 204.49
2018-06-26 07:00 | 212.43 | 208.72
2018-06-26 07:30 | 215.38 | 212.14
2018-06-26 08:00 | 215.93 | 212.74
2018-06-26 08:30 | 213.07 | 209.76
2018-06-26 09:00 | 210.65 | 207.04
2018-06-26 09:30 | 207.05 | 203.15
2018-06-26 10:00 | 205.43 | 201.34
2018-06-26 10:30 | 203.09 | 198.91
2018-06-26 11:00 | 201.63 | 197.41
2018-06-26 11:30 | 200.09 | 195.8
2018-06-26 12:00 | 199.35 | 194.91
2018-06-26 12:30 | 199.64 | 195.09
2018-06-26 13:00 | 200.43 | 195.86
2018-06-26 13:30 | 200.44 | 195.9
2018-06-26 14:00 | 200.21 | 195.74
2018-06-26 14:30 | 200.58 | 196.18
2018-06-26 15:00 | 201.25 | 196.67
2018-06-26 15:30 | 202.71 | 198
2018-06-26 16:00 | 204.14 | 199.6
2018-06-26 16:30 | 205.28 | 200.75
2018-06-26 17:00 | 206.14 | 201.67
2018-06-26 17:30 | 208.3 | 204.17
2018-06-26 18:00 | 212.19 | 210.83
2018-06-26 18:30 | 212.54 | 211.27
2018-06-26 19:00 | 212.97 | 211.66
2018-06-26 19:30 | 213.85 | 212.51
2018-06-26 20:00 | 215.4 | 214.06
2018-06-26 20:30 | 215.53 | 214.21
2018-06-26 21:00 | 216.6 | 215.24
2018-06-26 21:30 | 207.43 | 204.1
2018-06-26 22:00 | 206.89 | 202.54
2018-06-26 22:30 | 204.74 | 200.17
2018-06-26 23:00 | 202.59 | 197.82
2018-06-26 23:30 | 201.62 | 196.66
2018-06-27 | 200.33 | 195.22
2018-06-27 00:30 | 199.62 | 194.44
2018-06-27 01:00 | 198.24 | 193.04
2018-06-27 01:30 | 197.71 | 192.3
2018-06-27 02:00 | 197.57 | 192
2018-06-27 02:30 | 196.98 | 191.41
2018-06-27 03:00 | 196.6 | 190.97
2018-06-27 03:30 | 196.89 | 191.26
2018-06-27 04:00 | 197.89 | 192.23
2018-06-27 04:30 | 198.84 | 193.25
2018-06-27 05:00 | 199.69 | 194.15
2018-06-27 05:30 | 199.69 | 194.23
2018-06-27 06:00 | 201.14 | 196.12
2018-06-27 06:30 | 203.5 | 199.33
2018-06-27 07:00 | 206.42 | 202.48
2018-06-27 07:30 | 210.15 | 206.26
2018-06-27 08:00 | 219.68 | 213.95
2018-06-27 08:30 | 218.06 | 212.3
2018-06-27 09:00 | 216.41 | 210.32
2018-06-27 09:30 | 214.98 | 208.65
2018-06-27 10:00 | 214.89 | 208.25
2018-06-27 10:30 | 214.99 | 207.84
2018-06-27 11:00 | 214.13 | 207.06
2018-06-27 11:30 | 213.82 | 206.57
2018-06-27 12:00 | 213.17 | 205.98
2018-06-27 12:30 | 213 | 205.68
2018-06-27 13:00 | 212.5 | 205.03
2018-06-27 13:30 | 211.26 | 203.69
2018-06-27 14:00 | 210.78 | 203.27
2018-06-27 14:30 | 211.13 | 203.39
2018-06-27 15:00 | 211.36 | 203.48
2018-06-27 15:30 | 211.65 | 203.94
2018-06-27 16:00 | 212.22 | 204.55
2018-06-27 16:30 | 213.85 | 206.21
2018-06-27 17:00 | 215.29 | 207.75
2018-06-27 17:30 | 217.09 | 209.83
2018-06-27 18:00 | 220.69 | 214.15
2018-06-27 18:30 | 223.55 | 217.45
2018-06-27 19:00 | 223.72 | 217.62
2018-06-27 19:30 | 222.48 | 216.04
2018-06-27 20:00 | 221.05 | 214.41
2018-06-27 20:30 | 219.65 | 212.88
2018-06-27 21:00 | 217.41 | 210.52
2018-06-27 21:30 | 215.73 | 208.88
2018-06-27 22:00 | 213.98 | 206.55
2018-06-27 22:30 | 211.63 | 203.74
2018-06-27 23:00 | 209.54 | 201.31
2018-06-27 23:30 | 207.44 | 198.89
2018-06-28 | 206.57 | 198.01
2018-06-28 00:30 | 204.63 | 197.65
2018-06-28 01:00 | 197.05 | 191.11
2018-06-28 01:30 | 194.13 | 188.58
2018-06-28 02:00 | 193.36 | 187.77
2018-06-28 02:30 | 192.52 | 186.89
2018-06-28 03:00 | 192.86 | 187.2
2018-06-28 03:30 | 193.04 | 187.41
2018-06-28 04:00 | 193.36 | 187.75
2018-06-28 04:30 | 193.69 | 188.17
2018-06-28 05:00 | 194.06 | 188.78
2018-06-28 05:30 | 195.51 | 190.53
2018-06-28 06:00 | 197.64 | 192.98
2018-06-28 06:30 | 201.87 | 197.52
2018-06-28 07:00 | 204.67 | 200.76
2018-06-28 07:30 | 207.68 | 204.05
2018-06-28 08:00 | 207.24 | 203.73
2018-06-28 08:30 | 206.17 | 202.58
2018-06-28 09:00 | 204.33 | 200.69
2018-06-28 09:30 | 202.99 | 198.96
2018-06-28 10:00 | 202.25 | 198.08
2018-06-28 10:30 | 201.37 | 197.01
2018-06-28 11:00 | 200.93 | 196.47
2018-06-28 11:30 | 201.2 | 196.55
2018-06-28 12:00 | 201.07 | 196.25
2018-06-28 12:30 | 200 | 195.12
2018-06-28 13:00 | 200.46 | 195.44
2018-06-28 13:30 | 199.97 | 194.94
2018-06-28 14:00 | 200.15 | 195.24
2018-06-28 14:30 | 198.84 | 193.92
2018-06-28 15:00 | 198.13 | 193.04
2018-06-28 15:30 | 198.17 | 193.4
2018-06-28 16:00 | 197.94 | 193.37
2018-06-28 16:30 | 199.33 | 194.88
2018-06-28 17:00 | 200.99 | 196.54
2018-06-28 17:30 | 204.63 | 200.2
2018-06-28 18:00 | 210.09 | 205.83
2018-06-28 18:30 | 213.61 | 209.57
2018-06-28 19:00 | 213.79 | 209.82
2018-06-28 19:30 | 213.34 | 209.32
2018-06-28 20:00 | 212.05 | 208
2018-06-28 20:30 | 210.61 | 206.51
2018-06-28 21:00 | 209.29 | 205.08
2018-06-28 21:30 | 208.37 | 203.96
2018-06-28 22:00 | 206.65 | 202.08
2018-06-28 22:30 | 204.07 | 199.37
2018-06-28 23:00 | 202.09 | 197.35
2018-06-28 23:30 | 200.57 | 195.72
2018-06-29 | 198.92 | 194.01
2018-06-29 00:30 | 198.01 | 193.16
2018-06-29 01:00 | 196.51 | 191.66
2018-06-29 01:30 | 195.91 | 191.11
2018-06-29 02:00 | 196.07 | 191.25
2018-06-29 02:30 | 195.39 | 190.6
2018-06-29 03:00 | 194.56 | 189.76
2018-06-29 03:30 | 194.94 | 190.01
2018-06-29 04:00 | 195.68 | 190.72
2018-06-29 04:30 | 196.42 | 191.48
2018-06-29 05:00 | 197.73 | 192.83
2018-06-29 05:30 | 199.68 | 194.91
2018-06-29 06:00 | 202.59 | 198.04
2018-06-29 06:30 | 206.55 | 202.41
2018-06-29 07:00 | 210.3 | 206.38
2018-06-29 07:30 | 213.95 | 210.23
2018-06-29 08:00 | 213.21 | 209.46
2018-06-29 08:30 | 211.62 | 207.73
2018-06-29 09:00 | 207.72 | 203.69
2018-06-29 09:30 | 204.28 | 199.97
2018-06-29 10:00 | 201.58 | 197.22
2018-06-29 10:30 | 199.96 | 195.53
2018-06-29 11:00 | 197.55 | 193.01
2018-06-29 11:30 | 195.79 | 191.22
2018-06-29 12:00 | 194.45 | 189.85
2018-06-29 12:30 | 193.16 | 188.56
2018-06-29 13:00 | 192.88 | 188.18
2018-06-29 13:30 | 192.96 | 188.13
2018-06-29 14:00 | 193.71 | 188.64
2018-06-29 14:30 | 193.98 | 188.95
2018-06-29 15:00 | 194.21 | 189.27
2018-06-29 15:30 | 194.97 | 190.11
2018-06-29 16:00 | 196.36 | 191.65
2018-06-29 16:30 | 197.64 | 192.87
2018-06-29 17:00 | 199.45 | 194.63
2018-06-29 17:30 | 201.43 | 196.47
2018-06-29 18:00 | 205.23 | 200.4
2018-06-29 18:30 | 207.63 | 202.92
2018-06-29 19:00 | 207.85 | 203.12
2018-06-29 19:30 | 206.73 | 201.99
2018-06-29 20:00 | 206.04 | 201.25
2018-06-29 20:30 | 205.2 | 200.33
2018-06-29 21:00 | 203.99 | 199.06
2018-06-29 21:30 | 203.1 | 198.04
2018-06-29 22:00 | 202.06 | 196.89
2018-06-29 22:30 | 200.46 | 195.19
2018-06-29 23:00 | 199 | 193.65
2018-06-29 23:30 | 198.23 | 192.73
2018-06-30 | 196.5 | 190.96
2018-06-30 00:30 | 195.61 | 189.97
2018-06-30 01:00 | 194.47 | 188.82
2018-06-30 01:30 | 193.27 | 187.68
2018-06-30 02:00 | 193.04 | 187.43
2018-06-30 02:30 | 192.45 | 186.81
2018-06-30 03:00 | 192.07 | 186.44
2018-06-30 03:30 | 192.22 | 186.57
2018-06-30 04:00 | 192.7 | 187
2018-06-30 04:30 | 192.76 | 187.09
2018-06-30 05:00 | 193.06 | 187.44
2018-06-30 05:30 | 193.74 | 188.17
2018-06-30 06:00 | 194.92 | 189.46
2018-06-30 06:30 | 196.42 | 191.1
2018-06-30 07:00 | 198.31 | 193.08
2018-06-30 07:30 | 199.9 | 194.79
2018-06-30 08:00 | 200.23 | 195.22
2018-06-30 08:30 | 198.84 | 193.94
2018-06-30 09:00 | 196.11 | 191.21
2018-06-30 09:30 | 194.28 | 189.21
2018-06-30 10:00 | 193.9 | 188.75
2018-06-30 10:30 | 192.82 | 187.73
2018-06-30 11:00 | 192.14 | 187.1
2018-06-30 11:30 | 191.71 | 186.61
2018-06-30 12:00 | 191.12 | 185.98
2018-06-30 12:30 | 191.7 | 186.4
2018-06-30 13:00 | 191.37 | 186.02
2018-06-30 13:30 | 191.71 | 186.34
2018-06-30 14:00 | 191.79 | 186.43
2018-06-30 14:30 | 192.44 | 187.06
2018-06-30 15:00 | 192.29 | 186.92
2018-06-30 15:30 | 193.46 | 188.11
2018-06-30 16:00 | 195.74 | 190.42
2018-06-30 16:30 | 197.01 | 191.59
2018-06-30 17:00 | 198.52 | 193.1
2018-06-30 17:30 | 201.09 | 195.82
2018-06-30 18:00 | 204.26 | 199.22
2018-06-30 18:30 | 205.87 | 200.92
2018-06-30 19:00 | 205.8 | 200.85
2018-06-30 19:30 | 204.5 | 199.51
2018-06-30 20:00 | 203.57 | 198.46
2018-06-30 20:30 | 202.96 | 197.74
2018-06-30 21:00 | 202.18 | 196.84
2018-06-30 21:30 | 202.11 | 196.73
2018-06-30 22:00 | 201.12 | 195.82
2018-06-30 22:30 | 199.51 | 194.11
2018-06-30 23:00 | 197.89 | 192.47
2018-06-30 23:30 | 197.35 | 191.72
2018-07-01 | 195.75 | 190
2018-07-01 00:30 | 195.45 | 189.75
2018-07-01 01:00 | 194.28 | 188.53
2018-07-01 01:30 | 193.32 | 187.56
2018-07-01 02:00 | 192.62 | 186.83
2018-07-01 02:30 | 192.57 | 186.72
2018-07-01 03:00 | 192.14 | 186.28
2018-07-01 03:30 | 192.67 | 186.75
2018-07-01 04:00 | 192.41 | 186.51
2018-07-01 04:30 | 193.09 | 187.17
2018-07-01 05:00 | 193.42 | 187.56
2018-07-01 05:30 | 193.88 | 188.05
2018-07-01 06:00 | 194.5 | 188.7
2018-07-01 06:30 | 195.61 | 189.91
2018-07-01 07:00 | 196.83 | 191.23
2018-07-01 07:30 | 198.94 | 193.44
2018-07-01 08:00 | 199.95 | 194.49
2018-07-01 08:30 | 199.92 | 194.54
2018-07-01 09:00 | 199.55 | 194.24
2018-07-01 09:30 | 198.75 | 193.39
2018-07-01 10:00 | 198.33 | 192.94
2018-07-01 10:30 | 194.28 | 189.22
2018-07-01 11:00 | 193.43 | 188.34
2018-07-01 11:30 | 194.4 | 189.17
2018-07-01 12:00 | 192.85 | 187.73
2018-07-01 12:30 | 193.71 | 188.45
2018-07-01 13:00 | 194.46 | 189.18
2018-07-01 13:30 | 192.81 | 187.63
2018-07-01 14:00 | 194.09 | 188.73
2018-07-01 14:30 | 193.23 | 188.07
2018-07-01 15:00 | 193.77 | 188.57
2018-07-01 15:30 | 194.96 | 189.65
2018-07-01 16:00 | 199.49 | 193.75
2018-07-01 16:30 | 200.04 | 194.49
2018-07-01 17:00 | 201.78 | 196.52
2018-07-01 17:30 | 203.96 | 198.81
2018-07-01 18:00 | 207.63 | 202.7
2018-07-01 18:30 | 209.65 | 204.86
2018-07-01 19:00 | 209.07 | 204.33
2018-07-01 19:30 | 207.91 | 202.97
2018-07-01 20:00 | 206.76 | 201.65
2018-07-01 20:30 | 205.79 | 200.66
2018-07-01 21:00 | 204.19 | 199.03
2018-07-01 21:30 | 203.14 | 197.84
2018-07-01 22:00 | 201.43 | 195.99
2018-07-01 22:30 | 199.85 | 194.23
2018-07-01 23:00 | 198.14 | 192.59
2018-07-01 23:30 | 197.28 | 191.57
2018-07-02 | 196.07 | 190.32
2018-07-02 00:30 | 195.4 | 189.63
2018-07-02 01:00 | 194.6 | 188.89
2018-07-02 01:30 | 193.85 | 188.16
2018-07-02 02:00 | 193.56 | 187.86
2018-07-02 02:30 | 193.48 | 187.78
2018-07-02 03:00 | 192.97 | 187.26
2018-07-02 03:30 | 193.06 | 187.34
2018-07-02 04:00 | 193.3 | 187.57
2018-07-02 04:30 | 193.86 | 188.15
2018-07-02 05:00 | 194.69 | 189.02
2018-07-02 05:30 | 195.71 | 190.29
2018-07-02 06:00 | 197.64 | 192.41
2018-07-02 06:30 | 200.45 | 195.31
2018-07-02 07:00 | 203 | 197.9
2018-07-02 07:30 | 206.15 | 201.17
2018-07-02 08:00 | 207.57 | 202.56
2018-07-02 08:30 | 207.27 | 202.27
2018-07-02 09:00 | 206.28 | 201.3
2018-07-02 09:30 | 205.71 | 200.74
2018-07-02 10:00 | 203 | 198.17
2018-07-02 10:30 | 200.01 | 195.39
2018-07-02 11:00 | 199.4 | 194.66
2018-07-02 11:30 | 198.6 | 193.82
2018-07-02 12:00 | 198.89 | 194.03
2018-07-02 12:30 | 199.64 | 194.71
2018-07-02 13:00 | 198.66 | 193.7
2018-07-02 13:30 | 198.41 | 193.42
2018-07-02 14:00 | 198.39 | 193.4
2018-07-02 14:30 | 201.43 | 196.09
2018-07-02 15:00 | 201.95 | 196.68
2018-07-02 15:30 | 201.97 | 196.77
2018-07-02 16:00 | 202.76 | 197.61
2018-07-02 16:30 | 204.48 | 199.33
2018-07-02 17:00 | 206.59 | 201.45
2018-07-02 17:30 | 208.76 | 203.73
2018-07-02 18:00 | 213.42 | 208.62
2018-07-02 18:30 | 217.05 | 212.41
2018-07-02 19:00 | 217.09 | 212.54
2018-07-02 19:30 | 215.24 | 210.65
2018-07-02 20:00 | 213.46 | 208.85
2018-07-02 20:30 | 212.71 | 208.01
2018-07-02 21:00 | 211.12 | 206.38
2018-07-02 21:30 | 209.16 | 204.25
2018-07-02 22:00 | 207.29 | 202.22
2018-07-02 22:30 | 205.39 | 200.19
2018-07-02 23:00 | 203.44 | 198.15
2018-07-02 23:30 | 201.7 | 196.41
2018-07-03 | 199.99 | 194.55
2018-07-03 00:30 | 198.95 | 193.37
2018-07-03 01:00 | 197.91 | 192.33
2018-07-03 01:30 | 197.12 | 191.53
2018-07-03 02:00 | 196.77 | 191.15
2018-07-03 02:30 | 196.74 | 191.07
2018-07-03 03:00 | 196.22 | 190.67
2018-07-03 03:30 | 195.76 | 190.22
2018-07-03 04:00 | 195.73 | 190.21
2018-07-03 04:30 | 196.22 | 190.75
2018-07-03 05:00 | 197.32 | 191.89
2018-07-03 05:30 | 198.44 | 193.08
2018-07-03 06:00 | 200.86 | 195.74
2018-07-03 06:30 | 203.57 | 198.61
2018-07-03 07:00 | 204.29 | 199.58
2018-07-03 07:30 | 207.56 | 202.82
2018-07-03 08:00 | 208.66 | 203.94
2018-07-03 08:30 | 207.14 | 202.35
2018-07-03 09:00 | 204.53 | 199.77
2018-07-03 09:30 | 201.82 | 196.99
2018-07-03 10:00 | 200.82 | 195.82
2018-07-03 10:30 | 199.38 | 194.31
2018-07-03 11:00 | 197.97 | 192.83
2018-07-03 11:30 | 197.17 | 191.97
2018-07-03 12:00 | 196.29 | 191.06
2018-07-03 12:30 | 195.33 | 190.19
2018-07-03 13:00 | 195.5 | 190.26
2018-07-03 13:30 | 193.98 | 188.77
2018-07-03 14:00 | 193.64 | 188.43
2018-07-03 14:30 | 195.63 | 190.29
2018-07-03 15:00 | 196.18 | 190.88
2018-07-03 15:30 | 196.58 | 191.31
2018-07-03 16:00 | 197.75 | 192.47
2018-07-03 16:30 | 199.91 | 194.63
2018-07-03 17:00 | 201.78 | 196.61
2018-07-03 17:30 | 204.06 | 199
2018-07-03 18:00 | 209.27 | 204.46
2018-07-03 18:30 | 213.42 | 208.91
2018-07-03 19:00 | 213.9 | 209.5
2018-07-03 19:30 | 212.81 | 208.39
2018-07-03 20:00 | 211.65 | 207.16
2018-07-03 20:30 | 211.37 | 206.86
2018-07-03 21:00 | 209.1 | 204.54
2018-07-03 21:30 | 208.29 | 203.67
2018-07-03 22:00 | 206.48 | 201.75
2018-07-03 22:30 | 204.66 | 199.71
2018-07-03 23:00 | 202.41 | 197.33
2018-07-03 23:30 | 201.29 | 196.14
2018-07-04 | 199.82 | 194.52
2018-07-04 00:30 | 198.97 | 193.54
2018-07-04 01:00 | 197.66 | 192.03
2018-07-04 01:30 | 196.84 | 191.11
2018-07-04 02:00 | 196.39 | 190.67
2018-07-04 02:30 | 196.03 | 190.33
2018-07-04 03:00 | 195.77 | 190.03
2018-07-04 03:30 | 196.07 | 190.36
2018-07-04 04:00 | 196.54 | 190.83
2018-07-04 04:30 | 196.81 | 191.15
2018-07-04 05:00 | 197.73 | 192.16
2018-07-04 05:30 | 199.21 | 193.81
2018-07-04 06:00 | 201.88 | 196.83
2018-07-04 06:30 | 206.08 | 201.33
2018-07-04 07:00 | 209.28 | 204.63
2018-07-04 07:30 | 211.61 | 207.09
2018-07-04 08:00 | 211.51 | 207
2018-07-04 08:30 | 208.44 | 203.82
2018-07-04 09:00 | 204.31 | 199.62
2018-07-04 09:30 | 200.57 | 195.64
2018-07-04 10:00 | 198.81 | 193.75
2018-07-04 10:30 | 196.68 | 191.57
2018-07-04 11:00 | 194.97 | 189.76
2018-07-04 11:30 | 193.88 | 188.62
2018-07-04 12:00 | 193.17 | 187.86
2018-07-04 12:30 | 192.58 | 187.25
2018-07-04 13:00 | 192.55 | 187.15
2018-07-04 13:30 | 193.23 | 187.75
2018-07-04 14:00 | 194.1 | 188.59
2018-07-04 14:30 | 194.99 | 189.47
2018-07-04 15:00 | 195.63 | 190.18
2018-07-04 15:30 | 196.15 | 190.8
2018-07-04 16:00 | 197.26 | 191.97
2018-07-04 16:30 | 199.44 | 194.13
2018-07-04 17:00 | 201.87 | 196.43
2018-07-04 17:30 | 204.28 | 198.85
2018-07-04 18:00 | 208.04 | 202.83
2018-07-04 18:30 | 212.03 | 207.05
2018-07-04 19:00 | 212.76 | 207.84
2018-07-04 19:30 | 210.97 | 206.04
2018-07-04 20:00 | 209.1 | 204.12
2018-07-04 20:30 | 208.51 | 203.48
2018-07-04 21:00 | 207.57 | 202.44
2018-07-04 21:30 | 207.22 | 201.99
2018-07-04 22:00 | 205.01 | 199.66
2018-07-04 22:30 | 202.81 | 197.38
2018-07-04 23:00 | 201.09 | 195.59
2018-07-04 23:30 | 200 | 194.42
2018-07-05 | 198.52 | 192.78
2018-07-05 00:30 | 198.23 | 192.28
2018-07-05 01:00 | 196.31 | 190.35
2018-07-05 01:30 | 195.37 | 189.42
2018-07-05 02:00 | 195.05 | 189.04
2018-07-05 02:30 | 194.98 | 188.89
2018-07-05 03:00 | 194.76 | 188.68
2018-07-05 03:30 | 194.96 | 188.89
2018-07-05 04:00 | 195.61 | 189.54
2018-07-05 04:30 | 196.13 | 190.12
2018-07-05 05:00 | 196.74 | 190.8
2018-07-05 05:30 | 198.28 | 192.46
2018-07-05 06:00 | 200.23 | 194.76
2018-07-05 06:30 | 203.43 | 198.27
2018-07-05 07:00 | 205.44 | 200.34
2018-07-05 07:30 | 207.86 | 202.86
2018-07-05 08:00 | 206.81 | 201.86
2018-07-05 08:30 | 204.6 | 199.55
2018-07-05 09:00 | 201.91 | 196.85
2018-07-05 09:30 | 199.22 | 194.05
2018-07-05 10:00 | 198.26 | 192.98
2018-07-05 10:30 | 197.25 | 191.93
2018-07-05 11:00 | 196.8 | 191.46
2018-07-05 11:30 | 196.58 | 191.16
2018-07-05 12:00 | 196.37 | 190.89
2018-07-05 12:30 | 195.05 | 189.71
2018-07-05 13:00 | 193.11 | 187.81
2018-07-05 13:30 | 193.28 | 187.9
2018-07-05 14:00 | 193.61 | 188.23
2018-07-05 14:30 | 194.2 | 188.89
2018-07-05 15:00 | 196.38 | 191.13
2018-07-05 15:30 | 199.04 | 193.75
2018-07-05 16:00 | 200.15 | 194.91
2018-07-05 16:30 | 201.96 | 196.62
2018-07-05 17:00 | 203.93 | 198.59
2018-07-05 17:30 | 205.75 | 200.45
2018-07-05 18:00 | 209.64 | 204.49
2018-07-05 18:30 | 212.62 | 207.62
2018-07-05 19:00 | 212.99 | 208
2018-07-05 19:30 | 212.01 | 207.01
2018-07-05 20:00 | 210.28 | 205.25
2018-07-05 20:30 | 209.52 | 204.24
2018-07-05 21:00 | 208.23 | 202.79
2018-07-05 21:30 | 207.95 | 202.4
2018-07-05 22:00 | 206.28 | 200.65
2018-07-05 22:30 | 204.46 | 198.75
2018-07-05 23:00 | 202.98 | 197.12
2018-07-05 23:30 | 201.85 | 195.94
2018-07-06 | 200.59 | 194.62
2018-07-06 00:30 | 199.11 | 193.06
2018-07-06 01:00 | 198.05 | 191.97
2018-07-06 01:30 | 197.37 | 191.21
2018-07-06 02:00 | 197.21 | 191.02
2018-07-06 02:30 | 196.74 | 190.54
2018-07-06 03:00 | 196.57 | 190.36
2018-07-06 03:30 | 196.18 | 189.94
2018-07-06 04:00 | 196.28 | 190.06
2018-07-06 04:30 | 197.21 | 191
2018-07-06 05:00 | 198.28 | 192.11
2018-07-06 05:30 | 200.09 | 194.02
2018-07-06 06:00 | 201.46 | 195.64
2018-07-06 06:30 | 204.31 | 198.84
2018-07-06 07:00 | 206.25 | 201.02
2018-07-06 07:30 | 208.13 | 203.07
2018-07-06 08:00 | 208.56 | 203.56
2018-07-06 08:30 | 208.63 | 203.41
2018-07-06 09:00 | 207.68 | 202.47
2018-07-06 09:30 | 205.27 | 200.18
2018-07-06 10:00 | 203.91 | 198.75
2018-07-06 10:30 | 201.7 | 196.59
2018-07-06 11:00 | 199.67 | 194.6
2018-07-06 11:30 | 197.86 | 192.55
2018-07-06 12:00 | 197.07 | 191.75
2018-07-06 12:30 | 196.37 | 191.16
2018-07-06 13:00 | 197.25 | 191.96
2018-07-06 13:30 | 197.34 | 192.01
2018-07-06 14:00 | 197.37 | 192.04
2018-07-06 14:30 | 197.38 | 192.06
2018-07-06 15:00 | 197.97 | 192.69
2018-07-06 15:30 | 198.5 | 193.31
2018-07-06 16:00 | 200.44 | 195.1
2018-07-06 16:30 | 202.01 | 196.63
2018-07-06 17:00 | 182.87 | 175.31
2018-07-06 17:30 | 162.8 | 153.32
2018-07-06 18:00 | 164.24 | 155.15
2018-07-06 18:30 | 166.36 | 157.34
2018-07-06 19:00 | 166.4 | 157.25
2018-07-06 19:30 | 164.99 | 155.48
2018-07-06 20:00 | 165.69 | 156.05
2018-07-06 20:30 | 165.66 | 156.47
2018-07-06 21:00 | 163.66 | 154.53
2018-07-06 21:30 | 164.72 | 155.19
2018-07-06 22:00 | 165.24 | 154.98
2018-07-06 22:30 | 163.38 | 153.01
2018-07-06 23:00 | 161.57 | 150.63
2018-07-06 23:30 | 159.83 | 148.68
2018-07-07 | 158.45 | 147.81
2018-07-07 00:30 | 157.54 | 147.26
2018-07-07 01:00 | 155.71 | 146.11
2018-07-07 01:30 | 155.58 | 146.24
2018-07-07 02:00 | 155.08 | 145.51
2018-07-07 02:30 | 155.3 | 145.77
2018-07-07 03:00 | 154.92 | 145.38
2018-07-07 03:30 | 154.63 | 145.08
2018-07-07 04:00 | 155.03 | 145.51
2018-07-07 04:30 | 155.08 | 145.68
2018-07-07 05:00 | 155.5 | 146.18
2018-07-07 05:30 | 155.65 | 146.36
2018-07-07 06:00 | 156.32 | 147.16
2018-07-07 06:30 | 158.39 | 149.11
2018-07-07 07:00 | 159.64 | 150.52
2018-07-07 07:30 | 161.16 | 152.34
2018-07-07 08:00 | 162.08 | 153
2018-07-07 08:30 | 161.54 | 152.56
2018-07-07 09:00 | 161.78 | 152.84
2018-07-07 09:30 | 159.9 | 150.65
2018-07-07 10:00 | 159.21 | 149.67
2018-07-07 10:30 | 157.56 | 147.52
2018-07-07 11:00 | 156.2 | 146.07
2018-07-07 11:30 | 156.01 | 145.66
2018-07-07 12:00 | 157.44 | 145.86
2018-07-07 12:30 | 158.12 | 146.57
2018-07-07 13:00 | 157.12 | 145.86
2018-07-07 13:30 | 163.61 | 152.43
2018-07-07 14:00 | 174.96 | 163.89
2018-07-07 14:30 | 175.32 | 164.16
2018-07-07 15:00 | 176.26 | 165.01
2018-07-07 15:30 | 177.54 | 166.35
2018-07-07 16:00 | 179.24 | 168.17
2018-07-07 16:30 | 180.97 | 169.99
2018-07-07 17:00 | 183.4 | 172.64
2018-07-07 17:30 | 187.56 | 176.63
2018-07-07 18:00 | 192.07 | 180.97
2018-07-07 18:30 | 195.16 | 184.37
2018-07-07 19:00 | 195.55 | 184.73
2018-07-07 19:30 | 193.23 | 182.23
2018-07-07 20:00 | 191.49 | 180.65
2018-07-07 20:30 | 191.87 | 181.07
2018-07-07 21:00 | 190.92 | 180.13
2018-07-07 21:30 | 190.41 | 180.42
2018-07-07 22:00 | 190.11 | 180.07
2018-07-07 22:30 | 189.22 | 179.05
2018-07-07 23:00 | 187.58 | 177.47
2018-07-07 23:30 | 186.22 | 176.41
2018-07-08 | 184.32 | 174.98
2018-07-08 00:30 | 183.86 | 174.64
2018-07-08 01:00 | 181.8 | 172.71
2018-07-08 01:30 | 180.86 | 172.03
2018-07-08 02:00 | 180.82 | 172.25
2018-07-08 02:30 | 180.84 | 171.75
2018-07-08 03:00 | 181.4 | 172.07
2018-07-08 03:30 | 181.12 | 171.82
2018-07-08 04:00 | 180.82 | 171.57
2018-07-08 04:30 | 181.14 | 171.94
2018-07-08 05:00 | 182.3 | 173.1
2018-07-08 05:30 | 182.82 | 173.83
2018-07-08 06:00 | 183.96 | 175.16
2018-07-08 06:30 | 185.11 | 176.24
2018-07-08 07:00 | 188.41 | 179.43
2018-07-08 07:30 | 190.03 | 181.04
2018-07-08 08:00 | 191.41 | 182.72
2018-07-08 08:30 | 190.64 | 182.1
2018-07-08 09:00 | 188.53 | 179.83
2018-07-08 09:30 | 186.86 | 177.92
2018-07-08 10:00 | 185.32 | 176.29
2018-07-08 10:30 | 182.94 | 173.83
2018-07-08 11:00 | 180.75 | 171.76
2018-07-08 11:30 | 178.97 | 170.11
2018-07-08 12:00 | 177.64 | 168.53
2018-07-08 12:30 | 177.56 | 168.3
2018-07-08 13:00 | 177.18 | 167.49
2018-07-08 13:30 | 176.81 | 166.99
2018-07-08 14:00 | 176.95 | 167
2018-07-08 14:30 | 177.14 | 167.03
2018-07-08 15:00 | 177.83 | 167.63
2018-07-08 15:30 | 179.59 | 169.2
2018-07-08 16:00 | 181.51 | 170.91
2018-07-08 16:30 | 183.97 | 173.46
2018-07-08 17:00 | 185.93 | 175.74
2018-07-08 17:30 | 191.22 | 179.96
2018-07-08 18:00 | 196.04 | 184.8
2018-07-08 18:30 | 199.7 | 189.09
2018-07-08 19:00 | 200.96 | 190.35
2018-07-08 19:30 | 200.65 | 189.92
2018-07-08 20:00 | 199.53 | 188.53
2018-07-08 20:30 | 199.68 | 188.35
2018-07-08 21:00 | 197.97 | 186.42
2018-07-08 21:30 | 196.55 | 185.46
2018-07-08 22:00 | 194.28 | 182.7
2018-07-08 22:30 | 192.53 | 180.66
2018-07-08 23:00 | 190.52 | 178.2
2018-07-08 23:30 | 189.6 | 177.31
2018-07-09 | 187.61 | 175.53
2018-07-09 00:30 | 186.71 | 175.07
2018-07-09 01:00 | 185.13 | 173.71
2018-07-09 01:30 | 184.4 | 173.24
2018-07-09 02:00 | 184.25 | 173.4
2018-07-09 02:30 | 183.92 | 173.11
2018-07-09 03:00 | 183.92 | 173.22
2018-07-09 03:30 | 184.21 | 173.63
2018-07-09 04:00 | 185.06 | 174.64
2018-07-09 04:30 | 185.89 | 175.74
2018-07-09 05:00 | 186.23 | 176.32
2018-07-09 05:30 | 188.84 | 179.27
2018-07-09 06:00 | 191.25 | 181.95
2018-07-09 06:30 | 173.77 | 164.85
2018-07-09 07:00 | 186.87 | 178.61
2018-07-09 07:30 | 202.28 | 195.67
2018-07-09 08:00 | 220.35 | 215.63
2018-07-09 08:30 | 217.71 | 212.96
2018-07-09 09:00 | 214.46 | 209.64
2018-07-09 09:30 | 210.5 | 205.64
2018-07-09 10:00 | 209.01 | 203.86
2018-07-09 10:30 | 204.76 | 199.68
2018-07-09 11:00 | 197.07 | 192.62
2018-07-09 11:30 | 197.26 | 192.49
2018-07-09 12:00 | 171.68 | 164.2
2018-07-09 12:30 | 176.72 | 167.93
2018-07-09 13:00 | 176.09 | 166.43
2018-07-09 13:30 | 177.07 | 167.59
2018-07-09 14:00 | 178.06 | 168.65
2018-07-09 14:30 | 179.76 | 170.52
2018-07-09 15:00 | 179.52 | 170.34
2018-07-09 15:30 | 180.47 | 171.35
2018-07-09 16:00 | 181.55 | 172.56
2018-07-09 16:30 | 182.53 | 173.36
2018-07-09 17:00 | 185.35 | 176.16
2018-07-09 17:30 | 188.01 | 179.09
2018-07-09 18:00 | 192.56 | 184.09
2018-07-09 18:30 | 197.81 | 189.63
2018-07-09 19:00 | 199.29 | 191.2
2018-07-09 19:30 | 198.59 | 190.17
2018-07-09 20:00 | 198.13 | 189.34
2018-07-09 20:30 | 196.84 | 188.24
2018-07-09 21:00 | 195.74 | 187.03
2018-07-09 21:30 | 194.02 | 185.96
2018-07-09 22:00 | 191.99 | 183.65
2018-07-09 22:30 | 189.55 | 180.95
2018-07-09 23:00 | 187.21 | 178.34
2018-07-09 23:30 | 185.8 | 176.95
2018-07-10 | 183.8 | 174.92
2018-07-10 00:30 | 183.31 | 174.61
2018-07-10 01:00 | 182.48 | 173.97
2018-07-10 01:30 | 181.66 | 173.39
2018-07-10 02:00 | 181.49 | 173.68
2018-07-10 02:30 | 181.53 | 173.59
2018-07-10 03:00 | 181.36 | 173.47
2018-07-10 03:30 | 181.48 | 173.41
2018-07-10 04:00 | 182.1 | 174.05
2018-07-10 04:30 | 183.13 | 175.03
2018-07-10 05:00 | 184.93 | 176.94
2018-07-10 05:30 | 187.02 | 179.43
2018-07-10 06:00 | 190.85 | 183.01
2018-07-10 06:30 | 195.43 | 187.44
2018-07-10 07:00 | 198.73 | 191.26
2018-07-10 07:30 | 201.34 | 193.91
2018-07-10 08:00 | 200.78 | 193.59
2018-07-10 08:30 | 197.29 | 189.82
2018-07-10 09:00 | 192.78 | 184.81
2018-07-10 09:30 | 187.64 | 179.73
2018-07-10 10:00 | 184.77 | 176.38
2018-07-10 10:30 | 181.79 | 172.88
2018-07-10 11:00 | 178.22 | 169.13
2018-07-10 11:30 | 174.57 | 165.18
2018-07-10 12:00 | 171.54 | 162.02
2018-07-10 12:30 | 170.72 | 160.81
2018-07-10 13:00 | 170.38 | 159.95
2018-07-10 13:30 | 169.95 | 159.47
2018-07-10 14:00 | 169.37 | 159.32
2018-07-10 14:30 | 168.48 | 158.48
2018-07-10 15:00 | 168.48 | 158.6
2018-07-10 15:30 | 170.1 | 160.29
2018-07-10 16:00 | 172.79 | 163.02
2018-07-10 16:30 | 172.82 | 163.31
2018-07-10 17:00 | 177.02 | 167.64
2018-07-10 17:30 | 181.7 | 172.61
2018-07-10 18:00 | 188.56 | 180.18
2018-07-10 18:30 | 193.32 | 185.36
2018-07-10 19:00 | 195.67 | 187.83
2018-07-10 19:30 | 195.3 | 187.3
2018-07-10 20:00 | 194.78 | 186.82
2018-07-10 20:30 | 194.4 | 186.41
2018-07-10 21:00 | 193.43 | 185.08
2018-07-10 21:30 | 192.44 | 184.4
2018-07-10 22:00 | 190.63 | 182.58
2018-07-10 22:30 | 187.31 | 179.14
2018-07-10 23:00 | 184.37 | 175.8
2018-07-10 23:30 | 183.04 | 174.43
2018-07-11 | 181.1 | 172.28
2018-07-11 00:30 | 181.23 | 172.45
2018-07-11 01:00 | 179.76 | 171.4
2018-07-11 01:30 | 177.8 | 170.17
2018-07-11 02:00 | 177.16 | 169.77
2018-07-11 02:30 | 176.58 | 169.83
2018-07-11 03:00 | 176.4 | 169.6
2018-07-11 03:30 | 176.95 | 170.09
2018-07-11 04:00 | 177.42 | 170.51
2018-07-11 04:30 | 179.1 | 172.33
2018-07-11 05:00 | 179.89 | 173.25
2018-07-11 05:30 | 181.21 | 174.85
2018-07-11 06:00 | 184.93 | 177.71
2018-07-11 06:30 | 189.35 | 182.22
2018-07-11 07:00 | 192.86 | 186.08
2018-07-11 07:30 | 196 | 189.28
2018-07-11 08:00 | 195.58 | 188.99
2018-07-11 08:30 | 191.73 | 184.92
2018-07-11 09:00 | 187.87 | 180.57
2018-07-11 09:30 | 182.87 | 175.43
2018-07-11 10:00 | 179.01 | 171.02
2018-07-11 10:30 | 175.45 | 166.97
2018-07-11 11:00 | 172.77 | 163.89
2018-07-11 11:30 | 171.2 | 162.09
2018-07-11 12:00 | 170.97 | 161.69
2018-07-11 12:30 | 170.63 | 161.23
2018-07-11 13:00 | 170.14 | 160.32
2018-07-11 13:30 | 169.64 | 159.65
2018-07-11 14:00 | 169.37 | 159.61
2018-07-11 14:30 | 169.48 | 159.81
2018-07-11 15:00 | 169.58 | 159.87
2018-07-11 15:30 | 170.1 | 160.46
2018-07-11 16:00 | 171.1 | 161.68
2018-07-11 16:30 | 172.93 | 163.48
2018-07-11 17:00 | 175.33 | 166.11
2018-07-11 17:30 | 178.19 | 169.45
2018-07-11 18:00 | 184.17 | 176.22
2018-07-11 18:30 | 188.91 | 181.52
2018-07-11 19:00 | 190.1 | 182.54
2018-07-11 19:30 | 188.83 | 181.1
2018-07-11 20:00 | 187.57 | 179.93
2018-07-11 20:30 | 186.95 | 179.02
2018-07-11 21:00 | 185.71 | 177.42
2018-07-11 21:30 | 185.66 | 177.8
2018-07-11 22:00 | 183.28 | 175.3
2018-07-11 22:30 | 180.85 | 172.73
2018-07-11 23:00 | 179.03 | 170.44
2018-07-11 23:30 | 176.77 | 168.09
2018-07-12 | 174.49 | 166.16
2018-07-12 00:30 | 173.89 | 165.22
2018-07-12 01:00 | 172.54 | 164.19
2018-07-12 01:30 | 171.62 | 163.41
2018-07-12 02:00 | 171.02 | 163.06
2018-07-12 02:30 | 170.89 | 162.86
2018-07-12 03:00 | 171.53 | 162.33
2018-07-12 03:30 | 171.77 | 162.38
2018-07-12 04:00 | 172.33 | 163.13
2018-07-12 04:30 | 173.44 | 164.43
2018-07-12 05:00 | 174.9 | 166.02
2018-07-12 05:30 | 177.1 | 168.5
2018-07-12 06:00 | 179.72 | 171.29
2018-07-12 06:30 | 189.01 | 180.4
2018-07-12 07:00 | 192.72 | 184.87
2018-07-12 07:30 | 188.51 | 180.87
2018-07-12 08:00 | 188.09 | 180.56
2018-07-12 08:30 | 185.62 | 177.73
2018-07-12 09:00 | 182.7 | 173.97
2018-07-12 09:30 | 178.92 | 169.83
2018-07-12 10:00 | 175.28 | 165.61
2018-07-12 10:30 | 172.95 | 162.74
2018-07-12 11:00 | 170.84 | 160.21
2018-07-12 11:30 | 168.15 | 158.02
2018-07-12 12:00 | 165.58 | 156.36
2018-07-12 12:30 | 163.36 | 153.97
2018-07-12 13:00 | 163.24 | 153.51
2018-07-12 13:30 | 164.44 | 154.58
2018-07-12 14:00 | 165.35 | 155.62
2018-07-12 14:30 | 165.7 | 156.14
2018-07-12 15:00 | 165.77 | 156.21
2018-07-12 15:30 | 166.99 | 157.4
2018-07-12 16:00 | 168.49 | 159.11
2018-07-12 16:30 | 170.48 | 161.29
2018-07-12 17:00 | 171.44 | 162.31
2018-07-12 17:30 | 174.14 | 164.98
2018-07-12 18:00 | 178.87 | 170.62
2018-07-12 18:30 | 182.78 | 174.89
2018-07-12 19:00 | 183.69 | 175.82
2018-07-12 19:30 | 183.54 | 175.45
2018-07-12 20:00 | 183.39 | 175.46
2018-07-12 20:30 | 182.73 | 174.88
2018-07-12 21:00 | 181.6 | 173.6
2018-07-12 21:30 | 181.05 | 172.97
2018-07-12 22:00 | 178.88 | 170.61
2018-07-12 22:30 | 176.72 | 168.64
2018-07-12 23:00 | 174.4 | 166.2
2018-07-12 23:30 | 172.56 | 164.12
2018-07-13 | 171.22 | 162.68
2018-07-13 00:30 | 171.37 | 162.27
2018-07-13 01:00 | 169.8 | 161.04
2018-07-13 01:30 | 169.11 | 160.94
2018-07-13 02:00 | 168.72 | 160.46
2018-07-13 02:30 | 168.6 | 160.33
2018-07-13 03:00 | 168.27 | 160.04
2018-07-13 03:30 | 168.38 | 160
2018-07-13 04:00 | 169.3 | 160.96
2018-07-13 04:30 | 169.99 | 161.69
2018-07-13 05:00 | 171.55 | 163.33
2018-07-13 05:30 | 173.72 | 165.84
2018-07-13 06:00 | 176.41 | 168.7
2018-07-13 06:30 | 180.06 | 172.45
2018-07-13 07:00 | 183.98 | 176.91
2018-07-13 07:30 | 187.73 | 180.94
2018-07-13 08:00 | 187.58 | 181.1
2018-07-13 08:30 | 184.59 | 177.97
2018-07-13 09:00 | 180.48 | 173.37
2018-07-13 09:30 | 176.64 | 169.23
2018-07-13 10:00 | 173.59 | 166.05
2018-07-13 10:30 | 172.23 | 164.38
2018-07-13 11:00 | 171.05 | 163.2
2018-07-13 11:30 | 169.2 | 160.98
2018-07-13 12:00 | 154.02 | 146.19
2018-07-13 12:30 | 154.45 | 147.5
2018-07-13 13:00 | 154.14 | 146.91
2018-07-13 13:30 | 153.52 | 146.18
2018-07-13 14:00 | 153.15 | 146.51
2018-07-13 14:30 | 153.28 | 146.65
2018-07-13 15:00 | 154.52 | 147.7
2018-07-13 15:30 | 155.98 | 149.2
2018-07-13 16:00 | 146.26 | 139.85
2018-07-13 16:30 | 148.83 | 144.57
2018-07-13 17:00 | 166.03 | 163.26
2018-07-13 17:30 | 180.79 | 177.67
2018-07-13 18:00 | 190.79 | 187.53
2018-07-13 18:30 | 196.19 | 193.07
2018-07-13 19:00 | 197.57 | 194.53
2018-07-13 19:30 | 197.79 | 194.76
2018-07-13 20:00 | 197.31 | 194.3
2018-07-13 20:30 | 196.74 | 193.7
2018-07-13 21:00 | 195.38 | 192.25
2018-07-13 21:30 | 195 | 191.82
2018-07-13 22:00 | 193.58 | 190.35
2018-07-13 22:30 | 190.96 | 187.6
2018-07-13 23:00 | 189.01 | 185.55
2018-07-13 23:30 | 187.7 | 184.19
2018-07-14 | 186.03 | 182.44
2018-07-14 00:30 | 185.1 | 181.44
2018-07-14 01:00 | 183.89 | 180.15
2018-07-14 01:30 | 183.11 | 179.3
2018-07-14 02:00 | 182.23 | 178.36
2018-07-14 02:30 | 181.81 | 177.8
2018-07-14 03:00 | 181.55 | 177.55
2018-07-14 03:30 | 182.47 | 178.59
2018-07-14 04:00 | 182.76 | 178.93
2018-07-14 04:30 | 182.99 | 179.21
2018-07-14 05:00 | 184.33 | 180.58
2018-07-14 05:30 | 185.56 | 181.89
2018-07-14 06:00 | 187.29 | 183.7
2018-07-14 06:30 | 189.22 | 185.81
2018-07-14 07:00 | 191.99 | 188.67
2018-07-14 07:30 | 194.3 | 191.08
2018-07-14 08:00 | 195.47 | 192.36
2018-07-14 08:30 | 192.97 | 189.94
2018-07-14 09:00 | 189.56 | 186.54
2018-07-14 09:30 | 185.94 | 182.93
2018-07-14 10:00 | 182.52 | 179.43
2018-07-14 10:30 | 179.21 | 175.99
2018-07-14 11:00 | 175.45 | 172.13
2018-07-14 11:30 | 172.19 | 168.79
2018-07-14 12:00 | 170.95 | 167.51
2018-07-14 12:30 | 169.82 | 166.31
2018-07-14 13:00 | 170.91 | 167.4
2018-07-14 13:30 | 171.76 | 168.07
2018-07-14 14:00 | 173.49 | 169.61
2018-07-14 14:30 | 173.48 | 169.43
2018-07-14 15:00 | 174.5 | 170.5
2018-07-14 15:30 | 176.11 | 172.18
2018-07-14 16:00 | 178.16 | 174.29
2018-07-14 16:30 | 180.79 | 176.94
2018-07-14 17:00 | 184.3 | 180.49
2018-07-14 17:30 | 188.75 | 185.14
2018-07-14 18:00 | 194.33 | 191.03
2018-07-14 18:30 | 198.56 | 195.43
2018-07-14 19:00 | 199.3 | 196.24
2018-07-14 19:30 | 199.19 | 196.17
2018-07-14 20:00 | 198.16 | 195.12
2018-07-14 20:30 | 197.93 | 194.84
2018-07-14 21:00 | 197 | 193.86
2018-07-14 21:30 | 196.48 | 193.34
2018-07-14 22:00 | 194.48 | 191.32
2018-07-14 22:30 | 191.97 | 188.73
2018-07-14 23:00 | 189.88 | 186.58
2018-07-14 23:30 | 188.78 | 185.29
2018-07-15 | 187.03 | 183.42
2018-07-15 00:30 | 186.12 | 182.46
2018-07-15 01:00 | 184.51 | 180.9
2018-07-15 01:30 | 183.48 | 179.85
2018-07-15 02:00 | 182.93 | 179.3
2018-07-15 02:30 | 182.99 | 179.35
2018-07-15 03:00 | 183.39 | 179.61
2018-07-15 03:30 | 183.29 | 179.54
2018-07-15 04:00 | 183.43 | 179.7
2018-07-15 04:30 | 183.74 | 180.03
2018-07-15 05:00 | 184.12 | 180.47
2018-07-15 05:30 | 185.11 | 181.54
2018-07-15 06:00 | 186.44 | 182.96
2018-07-15 06:30 | 188 | 184.63
2018-07-15 07:00 | 189.96 | 186.77
2018-07-15 07:30 | 192.03 | 189.04
2018-07-15 08:00 | 192.7 | 189.8
2018-07-15 08:30 | 191.32 | 188.45
2018-07-15 09:00 | 188.59 | 185.66
2018-07-15 09:30 | 184.97 | 181.94
2018-07-15 10:00 | 180.93 | 177.88
2018-07-15 10:30 | 177.68 | 174.52
2018-07-15 11:00 | 175.78 | 172.53
2018-07-15 11:30 | 173.49 | 170.19
2018-07-15 12:00 | 172.59 | 169.12
2018-07-15 12:30 | 172.47 | 168.86
2018-07-15 13:00 | 172.6 | 168.89
2018-07-15 13:30 | 172.68 | 168.92
2018-07-15 14:00 | 172.45 | 168.68
2018-07-15 14:30 | 173.18 | 169.43
2018-07-15 15:00 | 174.5 | 170.66
2018-07-15 15:30 | 176.38 | 172.48
2018-07-15 16:00 | 178.95 | 175.09
2018-07-15 16:30 | 182.28 | 178.35
2018-07-15 17:00 | 185.69 | 181.62
2018-07-15 17:30 | 190.91 | 186.99
2018-07-15 18:00 | 196.29 | 192.76
2018-07-15 18:30 | 201.01 | 197.72
2018-07-15 19:00 | 202.29 | 199.07
2018-07-15 19:30 | 201.8 | 198.57
2018-07-15 20:00 | 200.75 | 197.45
2018-07-15 20:30 | 199.45 | 196.19
2018-07-15 21:00 | 197.93 | 194.61
2018-07-15 21:30 | 196.29 | 192.89
2018-07-15 22:00 | 194.12 | 190.6
2018-07-15 22:30 | 191.06 | 187.38
2018-07-15 23:00 | 188.99 | 185.14
2018-07-15 23:30 | 188.12 | 183.91
2018-07-16 | 185.92 | 181.86
2018-07-16 00:30 | 184.42 | 180.33
2018-07-16 01:00 | 183.18 | 178.95
2018-07-16 01:30 | 182.11 | 177.97
2018-07-16 02:00 | 181.54 | 177.38
2018-07-16 02:30 | 181.09 | 176.91
2018-07-16 03:00 | 181 | 176.81
2018-07-16 03:30 | 181.49 | 177.26
2018-07-16 04:00 | 181.87 | 177.67
2018-07-16 04:30 | 183.02 | 178.91
2018-07-16 05:00 | 184.1 | 180.13
2018-07-16 05:30 | 186.39 | 182.6
2018-07-16 06:00 | 189.98 | 186.51
2018-07-16 06:30 | 195.35 | 192.22
2018-07-16 07:00 | 201.3 | 198.25
2018-07-16 07:30 | 204.91 | 202.05
2018-07-16 08:00 | 205.54 | 202.74
2018-07-16 08:30 | 201.74 | 198.77
2018-07-16 09:00 | 198.74 | 195.6
2018-07-16 09:30 | 194.21 | 191.03
2018-07-16 10:00 | 190.85 | 187.6
2018-07-16 10:30 | 188.09 | 184.77
2018-07-16 11:00 | 185.55 | 182.13
2018-07-16 11:30 | 184.16 | 180.64
2018-07-16 12:00 | 183.36 | 179.84
2018-07-16 12:30 | 182.37 | 178.8
2018-07-16 13:00 | 183.57 | 179.66
2018-07-16 13:30 | 185.47 | 181.22
2018-07-16 14:00 | 185.37 | 180.99
2018-07-16 14:30 | 184.95 | 180.56
2018-07-16 15:00 | 185.48 | 181.09
2018-07-16 15:30 | 185.79 | 181.42
2018-07-16 16:00 | 187.53 | 183.23
2018-07-16 16:30 | 189.4 | 185.02
2018-07-16 17:00 | 169.88 | 163.81
2018-07-16 17:30 | 157.79 | 150.4
2018-07-16 18:00 | 163.38 | 156.51
2018-07-16 18:30 | 168.42 | 162.05
2018-07-16 19:00 | 169.53 | 163.5
2018-07-16 19:30 | 169.09 | 163
2018-07-16 20:00 | 167.98 | 161.84
2018-07-16 20:30 | 167.25 | 161.01
2018-07-16 21:00 | 164.82 | 158.29
2018-07-16 21:30 | 161.28 | 154.82
2018-07-16 22:00 | 159.11 | 152.59
2018-07-16 22:30 | 182.54 | 177.83
2018-07-16 23:00 | 193.09 | 189.14
2018-07-16 23:30 | 191.18 | 187.19
2018-07-17 | 189.6 | 185.58
2018-07-17 00:30 | 189.15 | 185.07
2018-07-17 01:00 | 187.83 | 183.61
2018-07-17 01:30 | 187.01 | 182.78
2018-07-17 02:00 | 186.58 | 182.37
2018-07-17 02:30 | 186.42 | 182.22
2018-07-17 03:00 | 186.12 | 181.85
2018-07-17 03:30 | 186.28 | 182
2018-07-17 04:00 | 186.89 | 182.62
2018-07-17 04:30 | 187.9 | 183.7
2018-07-17 05:00 | 189.91 | 185.84
2018-07-17 05:30 | 192.84 | 188.99
2018-07-17 06:00 | 195.45 | 191.74
2018-07-17 06:30 | 202.37 | 198.95
2018-07-17 07:00 | 207.29 | 204.16
2018-07-17 07:30 | 211.22 | 208.43
2018-07-17 08:00 | 211.06 | 208.37
2018-07-17 08:30 | 205.4 | 202.56
2018-07-17 09:00 | 199.14 | 196.14
2018-07-17 09:30 | 194.52 | 191.28
2018-07-17 10:00 | 191.01 | 187.71
2018-07-17 10:30 | 187.53 | 184.02
2018-07-17 11:00 | 185.56 | 181.91
2018-07-17 11:30 | 184.27 | 180.53
2018-07-17 12:00 | 183.12 | 179.38
2018-07-17 12:30 | 181.69 | 177.85
2018-07-17 13:00 | 181.43 | 177.56
2018-07-17 13:30 | 180.81 | 176.91
2018-07-17 14:00 | 180.75 | 176.94
2018-07-17 14:30 | 180.79 | 176.99
2018-07-17 15:00 | 181.79 | 177.88
2018-07-17 15:30 | 182.97 | 179.08
2018-07-17 16:00 | 185.23 | 181.36
2018-07-17 16:30 | 186.21 | 182.33
2018-07-17 17:00 | 188.27 | 184.38
2018-07-17 17:30 | 190.91 | 187.08
2018-07-17 18:00 | 196.94 | 193.29
2018-07-17 18:30 | 203.37 | 199.95
2018-07-17 19:00 | 205.38 | 202
2018-07-17 19:30 | 205.02 | 201.63
2018-07-17 20:00 | 204.36 | 200.92
2018-07-17 20:30 | 203.77 | 200.32
2018-07-17 21:00 | 202.47 | 198.99
2018-07-17 21:30 | 199.32 | 195.72
2018-07-17 22:00 | 197.57 | 193.85
2018-07-17 22:30 | 195.38 | 191.52
2018-07-17 23:00 | 192.75 | 188.79
2018-07-17 23:30 | 191.51 | 187.43
2018-07-18 | 189.7 | 185.53
2018-07-18 00:30 | 188.72 | 184.6
2018-07-18 01:00 | 187.36 | 183.17
2018-07-18 01:30 | 186.43 | 182.27
2018-07-18 02:00 | 186.06 | 181.89
2018-07-18 02:30 | 185.66 | 181.63
2018-07-18 03:00 | 185.36 | 181.32
2018-07-18 03:30 | 185.12 | 181.06
2018-07-18 04:00 | 185.68 | 181.62
2018-07-18 04:30 | 186.65 | 182.64
2018-07-18 05:00 | 188.5 | 184.6
2018-07-18 05:30 | 191.12 | 187.46
2018-07-18 06:00 | 194.62 | 191.15
2018-07-18 06:30 | 199.95 | 196.66
2018-07-18 07:00 | 204.18 | 201.16
2018-07-18 07:30 | 207.84 | 205.06
2018-07-18 08:00 | 206.95 | 204.21
2018-07-18 08:30 | 202.95 | 200.02
2018-07-18 09:00 | 197.54 | 194.29
2018-07-18 09:30 | 192.67 | 189.24
2018-07-18 10:00 | 189.79 | 186.2
2018-07-18 10:30 | 186.64 | 182.99
2018-07-18 11:00 | 184.31 | 180.49
2018-07-18 11:30 | 183.48 | 179.56
2018-07-18 12:00 | 182.43 | 178.52
2018-07-18 12:30 | 181.68 | 177.77
2018-07-18 13:00 | 181.37 | 177.41
2018-07-18 13:30 | 181.22 | 177.2
2018-07-18 14:00 | 181.53 | 177.62
2018-07-18 14:30 | 182.58 | 178.59
2018-07-18 15:00 | 183.4 | 179.41
2018-07-18 15:30 | 184.8 | 180.83
2018-07-18 16:00 | 186 | 182
2018-07-18 16:30 | 187.21 | 183.19
2018-07-18 17:00 | 189.21 | 185.13
2018-07-18 17:30 | 191.53 | 187.48
2018-07-18 18:00 | 196.38 | 192.5
2018-07-18 18:30 | 200.86 | 197.26
2018-07-18 19:00 | 203.31 | 199.74
2018-07-18 19:30 | 203.09 | 199.47
2018-07-18 20:00 | 202.53 | 198.93
2018-07-18 20:30 | 202.56 | 198.95
2018-07-18 21:00 | 200.98 | 197.31
2018-07-18 21:30 | 198.37 | 194.59
2018-07-18 22:00 | 196.89 | 192.99
2018-07-18 22:30 | 194.44 | 190.37
2018-07-18 23:00 | 192.42 | 188.23
2018-07-18 23:30 | 190.81 | 186.52
2018-07-19 | 189.37 | 185.01
2018-07-19 00:30 | 189.17 | 184.72
2018-07-19 01:00 | 188.25 | 183.7
2018-07-19 01:30 | 187.28 | 182.61
2018-07-19 02:00 | 186.56 | 181.93
2018-07-19 02:30 | 186.53 | 181.89
2018-07-19 03:00 | 186.27 | 181.59
2018-07-19 03:30 | 186.3 | 181.63
2018-07-19 04:00 | 186.62 | 181.96
2018-07-19 04:30 | 187.81 | 183.2
2018-07-19 05:00 | 189.42 | 184.94
2018-07-19 05:30 | 192.17 | 187.92
2018-07-19 06:00 | 195.54 | 191.64
2018-07-19 06:30 | 200.71 | 197.05
2018-07-19 07:00 | 205.41 | 202.11
2018-07-19 07:30 | 207.88 | 204.88
2018-07-19 08:00 | 206.99 | 203.82
2018-07-19 08:30 | 201.74 | 198.26
2018-07-19 09:00 | 192.3 | 188.06
2018-07-19 09:30 | 153.77 | 147.46
2018-07-19 10:00 | 149.41 | 143.03
2018-07-19 10:30 | 147.83 | 141.13
2018-07-19 11:00 | 147.01 | 139.94
2018-07-19 11:30 | 145.79 | 138.66
2018-07-19 12:00 | 145.71 | 138.32
2018-07-19 12:30 | 145.59 | 138.17
2018-07-19 13:00 | 154.3 | 147.49
2018-07-19 13:30 | 153.95 | 147.05
2018-07-19 14:00 | 154.07 | 146.95
2018-07-19 14:30 | 170.66 | 164.84
2018-07-19 15:00 | 182.89 | 178.52
2018-07-19 15:30 | 184.54 | 180.35
2018-07-19 16:00 | 186.12 | 182.03
2018-07-19 16:30 | 188.31 | 184.18
2018-07-19 17:00 | 190.01 | 185.91
2018-07-19 17:30 | 192.39 | 188.24
2018-07-19 18:00 | 196.56 | 192.59
2018-07-19 18:30 | 200.12 | 196.28
2018-07-19 19:00 | 199.19 | 195.51
2018-07-19 19:30 | 198.51 | 194.76
2018-07-19 20:00 | 197.29 | 193.52
2018-07-19 20:30 | 193.65 | 190.07
2018-07-19 21:00 | 190.8 | 187.24
2018-07-19 21:30 | 186.25 | 182.59
2018-07-19 22:00 | 183.76 | 180.04
2018-07-19 22:30 | 181.94 | 178.16
2018-07-19 23:00 | 175.02 | 171.31
2018-07-19 23:30 | 164.58 | 161.03
2018-07-20 | 163.18 | 159.55
2018-07-20 00:30 | 162.39 | 158.8
2018-07-20 01:00 | 161.13 | 157.63
2018-07-20 01:30 | 160.56 | 157.12
2018-07-20 02:00 | 160.11 | 156.58
2018-07-20 02:30 | 159.64 | 156.09
2018-07-20 03:00 | 159.59 | 156.02
2018-07-20 03:30 | 159.32 | 155.73
2018-07-20 04:00 | 159.86 | 156.29
2018-07-20 04:30 | 160.1 | 156.59
2018-07-20 05:00 | 161.35 | 157.87
2018-07-20 05:30 | 162.68 | 159.29
2018-07-20 06:00 | 164.51 | 161.3
2018-07-20 06:30 | 167.28 | 164.23
2018-07-20 07:00 | 170.35 | 167.44
2018-07-20 07:30 | 172.57 | 169.8
2018-07-20 08:00 | 172.29 | 169.5
2018-07-20 08:30 | 172.28 | 169.41
2018-07-20 09:00 | 168.75 | 165.83
2018-07-20 09:30 | 164.84 | 161.91
2018-07-20 10:00 | 163.92 | 160.97
2018-07-20 10:30 | 162.26 | 159.27
2018-07-20 11:00 | 161.63 | 158.71
2018-07-20 11:30 | 159.97 | 157.13
2018-07-20 12:00 | 158.6 | 155.69
2018-07-20 12:30 | 158.06 | 155.09
2018-07-20 13:00 | 156.46 | 153.39
2018-07-20 13:30 | 155.98 | 152.73
2018-07-20 14:00 | 156.53 | 153.19
2018-07-20 14:30 | 159.15 | 155.65
2018-07-20 15:00 | 161.61 | 158.13
2018-07-20 15:30 | 162.59 | 159.2
2018-07-20 16:00 | 164.68 | 161.24
2018-07-20 16:30 | 166.23 | 162.73
2018-07-20 17:00 | 168.98 | 165.47
2018-07-20 17:30 | 172.46 | 168.97
2018-07-20 18:00 | 176.74 | 173.49
2018-07-20 18:30 | 180.46 | 177.37
2018-07-20 19:00 | 181.61 | 178.56
2018-07-20 19:30 | 180.47 | 177.44
2018-07-20 20:00 | 179.92 | 176.86
2018-07-20 20:30 | 179.39 | 176.28
2018-07-20 21:00 | 177.96 | 174.71
2018-07-20 21:30 | 175.37 | 172.07
2018-07-20 22:00 | 175.72 | 172.43
2018-07-20 22:30 | 173.61 | 170.18
2018-07-20 23:00 | 172.16 | 168.64
2018-07-20 23:30 | 170.99 | 167.4
2018-07-21 | 169.21 | 165.53
2018-07-21 00:30 | 168.5 | 164.76
2018-07-21 01:00 | 167.66 | 163.84
2018-07-21 01:30 | 166.91 | 163.12
2018-07-21 02:00 | 166.56 | 162.87
2018-07-21 02:30 | 166.25 | 162.56
2018-07-21 03:00 | 166.06 | 162.39
2018-07-21 03:30 | 166.43 | 162.77
2018-07-21 04:00 | 167 | 163.36
2018-07-21 04:30 | 167.43 | 163.81
2018-07-21 05:00 | 167.93 | 164.36
2018-07-21 05:30 | 169.06 | 165.57
2018-07-21 06:00 | 170.35 | 166.97
2018-07-21 06:30 | 173.05 | 169.79
2018-07-21 07:00 | 176 | 172.85
2018-07-21 07:30 | 178.45 | 175.39
2018-07-21 08:00 | 179 | 176.01
2018-07-21 08:30 | 178.15 | 175.08
2018-07-21 09:00 | 174.11 | 170.96
2018-07-21 09:30 | 171.8 | 168.6
2018-07-21 10:00 | 169.25 | 165.86
2018-07-21 10:30 | 165.24 | 161.72
2018-07-21 11:00 | 163.44 | 159.9
2018-07-21 11:30 | 161.69 | 158.08
2018-07-21 12:00 | 160.49 | 156.78
2018-07-21 12:30 | 160.07 | 156.34
2018-07-21 13:00 | 159.28 | 155.53
2018-07-21 13:30 | 158.84 | 155.1
2018-07-21 14:00 | 158.71 | 154.95
2018-07-21 14:30 | 160.29 | 156.55
2018-07-21 15:00 | 170.42 | 166.53
2018-07-21 15:30 | 175.21 | 171.18
2018-07-21 16:00 | 177.08 | 173.07
2018-07-21 16:30 | 178.57 | 174.62
2018-07-21 17:00 | 180.53 | 176.74
2018-07-21 17:30 | 182.15 | 178.69
2018-07-21 18:00 | 188.33 | 185.02
2018-07-21 18:30 | 193.05 | 189.8
2018-07-21 19:00 | 194.6 | 191.32
2018-07-21 19:30 | 194.03 | 190.78
2018-07-21 20:00 | 194.34 | 191.06
2018-07-21 20:30 | 193.71 | 190.42
2018-07-21 21:00 | 192.45 | 189.13
2018-07-21 21:30 | 192.29 | 188.91
2018-07-21 22:00 | 190.76 | 187.26
2018-07-21 22:30 | 189.17 | 185.6
2018-07-21 23:00 | 187.34 | 183.68
2018-07-21 23:30 | 185.88 | 182.11
2018-07-22 | 184.3 | 180.49
2018-07-22 00:30 | 183.16 | 179.24
2018-07-22 01:00 | 181.57 | 177.69
2018-07-22 01:30 | 180.66 | 176.79
2018-07-22 02:00 | 180.11 | 176.19
2018-07-22 02:30 | 179.81 | 175.9
2018-07-22 03:00 | 179.45 | 175.51
2018-07-22 03:30 | 179.67 | 175.75
2018-07-22 04:00 | 179.18 | 175.28
2018-07-22 04:30 | 180.27 | 176.39
2018-07-22 05:00 | 181.03 | 177.22
2018-07-22 05:30 | 181.36 | 177.59
2018-07-22 06:00 | 183.3 | 179.61
2018-07-22 06:30 | 184.3 | 180.77
2018-07-22 07:00 | 185.69 | 182.32
2018-07-22 07:30 | 188.03 | 184.87
2018-07-22 08:00 | 188.26 | 185.22
2018-07-22 08:30 | 186.71 | 183.73
2018-07-22 09:00 | 183.03 | 180.1
2018-07-22 09:30 | 178.81 | 175.87
2018-07-22 10:00 | 175.48 | 172.57
2018-07-22 10:30 | 171.61 | 168.55
2018-07-22 11:00 | 169.3 | 166.23
2018-07-22 11:30 | 167.6 | 164.41
2018-07-22 12:00 | 166.24 | 163
2018-07-22 12:30 | 163.58 | 160.42
2018-07-22 13:00 | 161.77 | 158.67
2018-07-22 13:30 | 161.76 | 158.6
2018-07-22 14:00 | 161.95 | 158.77
2018-07-22 14:30 | 162.83 | 159.58
2018-07-22 15:00 | 166.2 | 162.75
2018-07-22 15:30 | 169.15 | 165.56
2018-07-22 16:00 | 171.66 | 168.01
2018-07-22 16:30 | 174.69 | 171
2018-07-22 17:00 | 178.22 | 174.52
2018-07-22 17:30 | 182.49 | 179
2018-07-22 18:00 | 187.57 | 184.26
2018-07-22 18:30 | 191.98 | 188.93
2018-07-22 19:00 | 193.57 | 190.63
2018-07-22 19:30 | 193.11 | 190.17
2018-07-22 20:00 | 191.97 | 188.96
2018-07-22 20:30 | 191.28 | 188.25
2018-07-22 21:00 | 189.98 | 186.88
2018-07-22 21:30 | 188.78 | 185.51
2018-07-22 22:00 | 186.87 | 183.56
2018-07-22 22:30 | 184.41 | 180.97
2018-07-22 23:00 | 181.53 | 178
2018-07-22 23:30 | 180.41 | 176.8
2018-07-23 | 178.52 | 174.85
2018-07-23 00:30 | 178.58 | 174.83
2018-07-23 01:00 | 177.48 | 173.59
2018-07-23 01:30 | 176.83 | 172.88
2018-07-23 02:00 | 176.93 | 172.96
2018-07-23 02:30 | 176.74 | 172.77
2018-07-23 03:00 | 176.87 | 172.91
2018-07-23 03:30 | 176.73 | 172.78
2018-07-23 04:00 | 177.08 | 173.16
2018-07-23 04:30 | 178.17 | 174.29
2018-07-23 05:00 | 179.96 | 176.18
2018-07-23 05:30 | 182.62 | 179.02
2018-07-23 06:00 | 185.76 | 182.57
2018-07-23 06:30 | 191.52 | 188.62
2018-07-23 07:00 | 197.37 | 194.66
2018-07-23 07:30 | 201.49 | 199.04
2018-07-23 08:00 | 200.87 | 198.33
2018-07-23 08:30 | 196.48 | 193.81
2018-07-23 09:00 | 192.01 | 189.17
2018-07-23 09:30 | 188.01 | 184.99
2018-07-23 10:00 | 185.89 | 182.6
2018-07-23 10:30 | 183.1 | 179.7
2018-07-23 11:00 | 180.73 | 177.29
2018-07-23 11:30 | 179.07 | 175.68
2018-07-23 12:00 | 179 | 175.54
2018-07-23 12:30 | 178.92 | 175.22
2018-07-23 13:00 | 177.64 | 173.91
2018-07-23 13:30 | 177.1 | 173.32
2018-07-23 14:00 | 176.96 | 173.23
2018-07-23 14:30 | 177.58 | 173.84
2018-07-23 15:00 | 177.56 | 173.73
2018-07-23 15:30 | 178.46 | 174.63
2018-07-23 16:00 | 180.12 | 176.29
2018-07-23 16:30 | 181.72 | 177.79
2018-07-23 17:00 | 183.58 | 179.61
2018-07-23 17:30 | 186.4 | 182.43
2018-07-23 18:00 | 191.21 | 187.49
2018-07-23 18:30 | 197.8 | 194.32
2018-07-23 19:00 | 199.21 | 195.93
2018-07-23 19:30 | 198.2 | 194.9
2018-07-23 20:00 | 197.72 | 194.4
2018-07-23 20:30 | 197.34 | 194.01
2018-07-23 21:00 | 196.33 | 192.91
2018-07-23 21:30 | 193.16 | 189.66
2018-07-23 22:00 | 190.95 | 187.37
2018-07-23 22:30 | 188.53 | 184.87
2018-07-23 23:00 | 185.5 | 181.75
2018-07-23 23:30 | 183.93 | 180
2018-07-24 | 182.48 | 178.51
2018-07-24 00:30 | 181.76 | 177.78
2018-07-24 01:00 | 181.02 | 176.94
2018-07-24 01:30 | 180.42 | 176.3
2018-07-24 02:00 | 180.03 | 175.91
2018-07-24 02:30 | 180.32 | 176.17
2018-07-24 03:00 | 180.04 | 175.86
2018-07-24 03:30 | 179.98 | 175.77
2018-07-24 04:00 | 180.18 | 175.99
2018-07-24 04:30 | 181.23 | 177.1
2018-07-24 05:00 | 182.55 | 178.51
2018-07-24 05:30 | 184.85 | 180.96
2018-07-24 06:00 | 187.64 | 184.05
2018-07-24 06:30 | 192.64 | 189.29
2018-07-24 07:00 | 196.4 | 193.32
2018-07-24 07:30 | 199.63 | 196.78
2018-07-24 08:00 | 198.43 | 195.57
2018-07-24 08:30 | 195.15 | 192.07
2018-07-24 09:00 | 189.72 | 186.4
2018-07-24 09:30 | 185.93 | 182.32
2018-07-24 10:00 | 183.77 | 180.14
2018-07-24 10:30 | 181.51 | 177.73
2018-07-24 11:00 | 179.66 | 175.89
2018-07-24 11:30 | 178.14 | 174.43
2018-07-24 12:00 | 176.85 | 173.1
2018-07-24 12:30 | 176.38 | 172.54
2018-07-24 13:00 | 176.5 | 172.63
2018-07-24 13:30 | 176.21 | 172.31
2018-07-24 14:00 | 176.36 | 172.58
2018-07-24 14:30 | 176.59 | 172.83
2018-07-24 15:00 | 176.69 | 172.96
2018-07-24 15:30 | 177.44 | 173.76
2018-07-24 16:00 | 178.49 | 174.84
2018-07-24 16:30 | 179.86 | 176.1
2018-07-24 17:00 | 181.6 | 177.78
2018-07-24 17:30 | 184.43 | 180.4
2018-07-24 18:00 | 156.83 | 149.85
2018-07-24 18:30 | 171.96 | 164.91
2018-07-24 19:00 | 174.62 | 167.57
2018-07-24 19:30 | 174.03 | 166.86
2018-07-24 20:00 | 173.84 | 166.51
2018-07-24 20:30 | 173.15 | 165.76
2018-07-24 21:00 | 171.61 | 164.19
2018-07-24 21:30 | 168.23 | 161.56
2018-07-24 22:00 | 166.19 | 159.47
2018-07-24 22:30 | 163.02 | 156.47
2018-07-24 23:00 | 161.38 | 154.62
2018-07-24 23:30 | 159.83 | 153.08
2018-07-25 | 159.52 | 151.64
2018-07-25 00:30 | 159.32 | 151.33
2018-07-25 01:00 | 157.67 | 150.18
2018-07-25 01:30 | 156.69 | 149.69
2018-07-25 02:00 | 156.02 | 149.3
2018-07-25 02:30 | 155.94 | 149.17
2018-07-25 03:00 | 155.87 | 149.1
2018-07-25 03:30 | 155.74 | 148.15
2018-07-25 04:00 | 157.08 | 148.75
2018-07-25 04:30 | 158.5 | 150.15
2018-07-25 05:00 | 160.09 | 151.94
2018-07-25 05:30 | 162.73 | 154.33
2018-07-25 06:00 | 166.85 | 158.03
2018-07-25 06:30 | 170.46 | 162.1
2018-07-25 07:00 | 174.27 | 166.19
2018-07-25 07:30 | 175.88 | 168.57
2018-07-25 08:00 | 176.44 | 169.06
2018-07-25 08:30 | 173.79 | 166.22
2018-07-25 09:00 | 169.44 | 161.12
2018-07-25 09:30 | 166.22 | 157.55
2018-07-25 10:00 | 162.94 | 153.94
2018-07-25 10:30 | 163.73 | 154.46
2018-07-25 11:00 | 162.26 | 152.7
2018-07-25 11:30 | 160.81 | 151.37
2018-07-25 12:00 | 160.18 | 151.79
2018-07-25 12:30 | 159.51 | 151.21
2018-07-25 13:00 | 159.5 | 150.99
2018-07-25 13:30 | 160.06 | 151.48
2018-07-25 14:00 | 159.92 | 151.63
2018-07-25 14:30 | 160.27 | 152.12
2018-07-25 15:00 | 160.3 | 151.76
2018-07-25 15:30 | 161.2 | 152.52
2018-07-25 16:00 | 161.23 | 152.77
2018-07-25 16:30 | 161.74 | 153.16
2018-07-25 17:00 | 163.18 | 154.86
2018-07-25 17:30 | 165.16 | 157.05
2018-07-25 18:00 | 168.71 | 161.01
2018-07-25 18:30 | 172.89 | 165.35
2018-07-25 19:00 | 174.33 | 166.93
2018-07-25 19:30 | 172.77 | 165.41
2018-07-25 20:00 | 170.44 | 162.85
2018-07-25 20:30 | 173.06 | 167.74
2018-07-25 21:00 | 186.52 | 183.06
2018-07-25 21:30 | 184.1 | 180.5
2018-07-25 22:00 | 182.74 | 179.05
2018-07-25 22:30 | 180.27 | 176.5
2018-07-25 23:00 | 178.04 | 174.15
2018-07-25 23:30 | 176.6 | 172.57
2018-07-26 | 175.49 | 171.34
2018-07-26 00:30 | 175.04 | 170.81
2018-07-26 01:00 | 173.86 | 169.66
2018-07-26 01:30 | 173.22 | 169.14
2018-07-26 02:00 | 172.83 | 168.75
2018-07-26 02:30 | 172.4 | 168.33
2018-07-26 03:00 | 172.23 | 168.17
2018-07-26 03:30 | 172.19 | 168.15
2018-07-26 04:00 | 172.32 | 168.34
2018-07-26 04:30 | 172.86 | 168.92
2018-07-26 05:00 | 173.92 | 170.07
2018-07-26 05:30 | 175.95 | 172.18
2018-07-26 06:00 | 179.75 | 176.23
2018-07-26 06:30 | 185.23 | 181.91
2018-07-26 07:00 | 189.6 | 186.4
2018-07-26 07:30 | 193.08 | 190.03
2018-07-26 08:00 | 192.16 | 189.23
2018-07-26 08:30 | 188.82 | 185.75
2018-07-26 09:00 | 183.54 | 180.39
2018-07-26 09:30 | 180.35 | 177.11
2018-07-26 10:00 | 178.16 | 174.82
2018-07-26 10:30 | 176.18 | 172.75
2018-07-26 11:00 | 174.96 | 171.46
2018-07-26 11:30 | 173.94 | 170.4
2018-07-26 12:00 | 173.26 | 169.72
2018-07-26 12:30 | 172.58 | 169.05
2018-07-26 13:00 | 171.9 | 168.36
2018-07-26 13:30 | 171.67 | 168.15
2018-07-26 14:00 | 172.16 | 168.71
2018-07-26 14:30 | 173.01 | 169.5
2018-07-26 15:00 | 174.48 | 170.88
2018-07-26 15:30 | 175.26 | 171.67
2018-07-26 16:00 | 176.32 | 172.8
2018-07-26 16:30 | 177.88 | 174.29
2018-07-26 17:00 | 179.5 | 175.91
2018-07-26 17:30 | 181.89 | 178.19
2018-07-26 18:00 | 185.29 | 181.66
2018-07-26 18:30 | 189 | 185.44
2018-07-26 19:00 | 190.39 | 186.96
2018-07-26 19:30 | 189.65 | 186.26
2018-07-26 20:00 | 188.48 | 185.04
2018-07-26 20:30 | 187.23 | 183.78
2018-07-26 21:00 | 185.14 | 181.71
2018-07-26 21:30 | 182.67 | 179.2
2018-07-26 22:00 | 181.41 | 177.86
2018-07-26 22:30 | 179.52 | 175.85
2018-07-26 23:00 | 177.57 | 173.87
2018-07-26 23:30 | 176.36 | 172.66
2018-07-27 | 175 | 171.2
2018-07-27 00:30 | 174.59 | 170.78
2018-07-27 01:00 | 173.53 | 169.62
2018-07-27 01:30 | 173.27 | 169.26
2018-07-27 02:00 | 173.25 | 169.18
2018-07-27 02:30 | 172.9 | 168.83
2018-07-27 03:00 | 172.67 | 168.61
2018-07-27 03:30 | 172.32 | 168.28
2018-07-27 04:00 | 172.75 | 168.73
2018-07-27 04:30 | 173.26 | 169.29
2018-07-27 05:00 | 174.54 | 170.59
2018-07-27 05:30 | 176.7 | 172.83
2018-07-27 06:00 | 178.53 | 174.97
2018-07-27 06:30 | 182.96 | 179.55
2018-07-27 07:00 | 185.94 | 182.68
2018-07-27 07:30 | 189.21 | 186.05
2018-07-27 08:00 | 189.65 | 186.47
2018-07-27 08:30 | 187.64 | 184.32
2018-07-27 09:00 | 182.93 | 179.47
2018-07-27 09:30 | 180.14 | 176.61
2018-07-27 10:00 | 178.05 | 174.55
2018-07-27 10:30 | 176.08 | 172.46
2018-07-27 11:00 | 173.93 | 170.38
2018-07-27 11:30 | 172.85 | 169.22
2018-07-27 12:00 | 172.55 | 168.84
2018-07-27 12:30 | 171.98 | 168.22
2018-07-27 13:00 | 172.39 | 168.5
2018-07-27 13:30 | 172.89 | 169.07
2018-07-27 14:00 | 172.35 | 168.66
2018-07-27 14:30 | 166.32 | 162.92
2018-07-27 15:00 | 158.02 | 154.93
2018-07-27 15:30 | 158.92 | 155.89
2018-07-27 16:00 | 160.87 | 157.8
2018-07-27 16:30 | 162.07 | 159.04
2018-07-27 17:00 | 164.34 | 161.3
2018-07-27 17:30 | 172.57 | 169.33
2018-07-27 18:00 | 177.55 | 174.2
2018-07-27 18:30 | 181.86 | 178.53
2018-07-27 19:00 | 182.59 | 179.29
2018-07-27 19:30 | 181.98 | 178.65
2018-07-27 20:00 | 180.97 | 177.57
2018-07-27 20:30 | 180.82 | 177.41
2018-07-27 21:00 | 179.06 | 175.6
2018-07-27 21:30 | 177.37 | 173.76
2018-07-27 22:00 | 176.49 | 172.8
2018-07-27 22:30 | 175.25 | 171.44
2018-07-27 23:00 | 173.94 | 170.11
2018-07-27 23:30 | 173.31 | 169.47
2018-07-28 | 172.23 | 168.4
2018-07-28 00:30 | 171.32 | 167.59
2018-07-28 01:00 | 170.5 | 166.63
2018-07-28 01:30 | 169.55 | 165.62
2018-07-28 02:00 | 169.43 | 165.44
2018-07-28 02:30 | 168.87 | 164.89
2018-07-28 03:00 | 168.51 | 164.55
2018-07-28 03:30 | 168.64 | 164.66
2018-07-28 04:00 | 169.14 | 165.14
2018-07-28 04:30 | 169.58 | 165.62
2018-07-28 05:00 | 170.14 | 166.2
2018-07-28 05:30 | 170.79 | 166.89
2018-07-28 06:00 | 172.12 | 168.29
2018-07-28 06:30 | 173.6 | 169.96
2018-07-28 07:00 | 175.03 | 171.48
2018-07-28 07:30 | 176.71 | 173.18
2018-07-28 08:00 | 177.25 | 173.48
2018-07-28 08:30 | 177.36 | 173.49
2018-07-28 09:00 | 176.81 | 172.92
2018-07-28 09:30 | 176.32 | 172.34
2018-07-28 10:00 | 174.84 | 170.85
2018-07-28 10:30 | 171.05 | 167.25
2018-07-28 11:00 | 173.72 | 169.67
2018-07-28 11:30 | 174.29 | 170.12
2018-07-28 12:00 | 174.32 | 170.12
2018-07-28 12:30 | 174.33 | 170.04
2018-07-28 13:00 | 173.6 | 169.35
2018-07-28 13:30 | 173.63 | 169.39
2018-07-28 14:00 | 180.2 | 175.78
2018-07-28 14:30 | 179.58 | 175.21
2018-07-28 15:00 | 175.2 | 171
2018-07-28 15:30 | 176 | 171.9
2018-07-28 16:00 | 177.11 | 173.05
2018-07-28 16:30 | 182.09 | 178.01
2018-07-28 17:00 | 193.1 | 188.68
2018-07-28 17:30 | 196.74 | 192.31
2018-07-28 18:00 | 199.14 | 194.88
2018-07-28 18:30 | 201.81 | 197.58
2018-07-28 19:00 | 201.87 | 197.69
2018-07-28 19:30 | 199.98 | 195.78
2018-07-28 20:00 | 198.56 | 194.34
2018-07-28 20:30 | 198.04 | 193.66
2018-07-28 21:00 | 197.23 | 192.68
2018-07-28 21:30 | 197.37 | 192.73
2018-07-28 22:00 | 197.12 | 192.35
2018-07-28 22:30 | 188.23 | 183.89
2018-07-28 23:00 | 185.52 | 181.28
2018-07-28 23:30 | 185.92 | 181.45
2018-07-29 | 184.45 | 180.09
2018-07-29 00:30 | 183.81 | 179.41
2018-07-29 01:00 | 185.36 | 180.77
2018-07-29 01:30 | 187.02 | 182.4
2018-07-29 02:00 | 186.98 | 182.22
2018-07-29 02:30 | 188.21 | 183.33
2018-07-29 03:00 | 190.31 | 185.25
2018-07-29 03:30 | 190.21 | 185.16
2018-07-29 04:00 | 190.79 | 185.69
2018-07-29 04:30 | 191.32 | 186.21
2018-07-29 05:00 | 191.55 | 186.46
2018-07-29 05:30 | 192.15 | 187.01
2018-07-29 06:00 | 192.81 | 187.71
2018-07-29 06:30 | 193.04 | 188.07
2018-07-29 07:00 | 194.39 | 189.51
2018-07-29 07:30 | 196.5 | 191.62
2018-07-29 08:00 | 198.34 | 193.46
2018-07-29 08:30 | 199.28 | 194.62
2018-07-29 09:00 | 199.3 | 194.66
2018-07-29 09:30 | 199 | 194.35
2018-07-29 10:00 | 197.24 | 192.54
2018-07-29 10:30 | 195.45 | 190.66
2018-07-29 11:00 | 194.29 | 189.41
2018-07-29 11:30 | 193.66 | 188.78
2018-07-29 12:00 | 194.31 | 189.47
2018-07-29 12:30 | 193.25 | 188.3
2018-07-29 13:00 | 193.34 | 188.26
2018-07-29 13:30 | 194.05 | 188.98
2018-07-29 14:00 | 196.06 | 190.95
2018-07-29 14:30 | 196.69 | 191.57
2018-07-29 15:00 | 197.56 | 192.46
2018-07-29 15:30 | 197.76 | 192.7
2018-07-29 16:00 | 198.97 | 193.9
2018-07-29 16:30 | 200.83 | 195.74
2018-07-29 17:00 | 201.91 | 196.87
2018-07-29 17:30 | 203.76 | 198.66
2018-07-29 18:00 | 206.28 | 201.3
2018-07-29 18:30 | 208.89 | 204.04
2018-07-29 19:00 | 209.63 | 204.81
2018-07-29 19:30 | 208.74 | 203.85
2018-07-29 20:00 | 207.4 | 202.45
2018-07-29 20:30 | 206.7 | 201.69
2018-07-29 21:00 | 205.95 | 200.78
2018-07-29 21:30 | 205.01 | 199.71
2018-07-29 22:00 | 204.09 | 198.99
2018-07-29 22:30 | 202.08 | 196.96
2018-07-29 23:00 | 200.23 | 194.96
2018-07-29 23:30 | 199.7 | 194.18
2018-07-30 | 198.58 | 193.02
2018-07-30 00:30 | 198.38 | 192.77
2018-07-30 01:00 | 197.56 | 191.91
2018-07-30 01:30 | 197.13 | 191.49
2018-07-30 02:00 | 196.6 | 190.98
2018-07-30 02:30 | 196.71 | 191.13
2018-07-30 03:00 | 196.38 | 190.92
2018-07-30 03:30 | 196.42 | 190.99
2018-07-30 04:00 | 196.83 | 191.4
2018-07-30 04:30 | 197.61 | 192.22
2018-07-30 05:00 | 198.76 | 193.44
2018-07-30 05:30 | 200.7 | 195.55
2018-07-30 06:00 | 203.6 | 198.77
2018-07-30 06:30 | 208.67 | 204.11
2018-07-30 07:00 | 214.98 | 210.39
2018-07-30 07:30 | 218.67 | 214.38
2018-07-30 08:00 | 218.08 | 213.78
2018-07-30 08:30 | 214.65 | 210.11
2018-07-30 09:00 | 210.31 | 205.65
2018-07-30 09:30 | 206.72 | 201.9
2018-07-30 10:00 | 204.57 | 199.71
2018-07-30 10:30 | 203.03 | 198.1
2018-07-30 11:00 | 202.02 | 197.05
2018-07-30 11:30 | 200.76 | 195.77
2018-07-30 12:00 | 200.06 | 195.07
2018-07-30 12:30 | 198.98 | 193.8
2018-07-30 13:00 | 197.69 | 192.4
2018-07-30 13:30 | 197.87 | 192.61
2018-07-30 14:00 | 197.92 | 192.74
2018-07-30 14:30 | 198.03 | 192.83
2018-07-30 15:00 | 198.4 | 193.2
2018-07-30 15:30 | 200.03 | 194.8
2018-07-30 16:00 | 202.42 | 197.24
2018-07-30 16:30 | 203.81 | 198.61
2018-07-30 17:00 | 205.73 | 200.58
2018-07-30 17:30 | 208.04 | 202.96
2018-07-30 18:00 | 212.71 | 207.84
2018-07-30 18:30 | 217.71 | 213.05
2018-07-30 19:00 | 219.5 | 214.97
2018-07-30 19:30 | 218.83 | 214.29
2018-07-30 20:00 | 218.19 | 213.65
2018-07-30 20:30 | 217.21 | 212.65
2018-07-30 21:00 | 216.07 | 211.45
2018-07-30 21:30 | 215.13 | 210.38
2018-07-30 22:00 | 213.51 | 208.72
2018-07-30 22:30 | 211.02 | 206.07
2018-07-30 23:00 | 208.66 | 203.63
2018-07-30 23:30 | 207.37 | 202.28
2018-07-31 | 206.13 | 200.87
2018-07-31 00:30 | 205.59 | 200.27
2018-07-31 01:00 | 204.45 | 199.13
2018-07-31 01:30 | 204.01 | 198.7
2018-07-31 02:00 | 203.59 | 198.3
2018-07-31 02:30 | 203.82 | 198.52
2018-07-31 03:00 | 204.31 | 198.98
2018-07-31 03:30 | 205.28 | 199.86
2018-07-31 04:00 | 206.01 | 200.55
2018-07-31 04:30 | 206.94 | 201.57
2018-07-31 05:00 | 207.65 | 202.47
2018-07-31 05:30 | 203.57 | 199.14
2018-07-31 06:00 | 198.13 | 194.39
2018-07-31 06:30 | 197.94 | 194.39
2018-07-31 07:00 | 200.65 | 197.45
2018-07-31 07:30 | 206.37 | 203.27
2018-07-31 08:00 | 205.59 | 202.48
2018-07-31 08:30 | 199.81 | 196.53
2018-07-31 09:00 | 193.41 | 189.98
2018-07-31 09:30 | 188.51 | 184.94
2018-07-31 10:00 | 186.07 | 182.28
2018-07-31 10:30 | 182.75 | 178.94
2018-07-31 11:00 | 181.73 | 177.84
2018-07-31 11:30 | 180.37 | 176.45
2018-07-31 12:00 | 179.5 | 175.54
2018-07-31 12:30 | 179.19 | 175.16
2018-07-31 13:00 | 179.27 | 175.17
2018-07-31 13:30 | 179.17 | 175.01
2018-07-31 14:00 | 179.44 | 175.35
2018-07-31 14:30 | 179.99 | 175.89
2018-07-31 15:00 | 180.1 | 175.96
2018-07-31 15:30 | 181.43 | 177.12
2018-07-31 16:00 | 182.83 | 178.53
2018-07-31 16:30 | 183.9 | 179.54
2018-07-31 17:00 | 185.09 | 180.8
2018-07-31 17:30 | 187.11 | 182.81
2018-07-31 18:00 | 191.76 | 187.55
2018-07-31 18:30 | 197.42 | 193.39
2018-07-31 19:00 | 199.73 | 195.81
2018-07-31 19:30 | 199.3 | 195.38
2018-07-31 20:00 | 197.73 | 193.76
2018-07-31 20:30 | 197.92 | 193.87
2018-07-31 21:00 | 197.08 | 192.94
2018-07-31 21:30 | 196.34 | 192.25
2018-07-31 22:00 | 193.64 | 189.64
2018-07-31 22:30 | 190.83 | 186.8
2018-07-31 23:00 | 188.5 | 184.38
2018-07-31 23:30 | 186.99 | 182.75
2018-08-01 | 186.03 | 181.8
2018-08-01 00:30 | 185.01 | 180.7
2018-08-01 01:00 | 183.82 | 179.41
2018-08-01 01:30 | 182.9 | 178.47
2018-08-01 02:00 | 182.59 | 178.26
2018-08-01 02:30 | 182.73 | 178.48
2018-08-01 03:00 | 182.28 | 177.96
2018-08-01 03:30 | 181.8 | 177.42
2018-08-01 04:00 | 182.46 | 178.11
2018-08-01 04:30 | 183.15 | 178.88
2018-08-01 05:00 | 184.72 | 180.54
2018-08-01 05:30 | 186.92 | 182.94
2018-08-01 06:00 | 190.69 | 186.89
2018-08-01 06:30 | 195.53 | 191.99
2018-08-01 07:00 | 199.15 | 195.89
2018-08-01 07:30 | 202.32 | 199.3
2018-08-01 08:00 | 200.72 | 197.71
2018-08-01 08:30 | 195.64 | 192.48
2018-08-01 09:00 | 190.06 | 186.77
2018-08-01 09:30 | 184.06 | 180.55
2018-08-01 10:00 | 181.25 | 177.69
2018-08-01 10:30 | 179.11 | 175.32
2018-08-01 11:00 | 178.47 | 174.69
2018-08-01 11:30 | 176.86 | 173.13
2018-08-01 12:00 | 174.68 | 171.01
2018-08-01 12:30 | 173.23 | 169.48
2018-08-01 13:00 | 172.95 | 169.21
2018-08-01 13:30 | 173.3 | 169.56
2018-08-01 14:00 | 173.78 | 170.06
2018-08-01 14:30 | 174.42 | 170.79
2018-08-01 15:00 | 174.72 | 171.07
2018-08-01 15:30 | 175.45 | 171.75
2018-08-01 16:00 | 177.52 | 173.79
2018-08-01 16:30 | 179.12 | 175.28
2018-08-01 17:00 | 180.77 | 176.9
2018-08-01 17:30 | 182.94 | 179.1
2018-08-01 18:00 | 186.74 | 182.99
2018-08-01 18:30 | 199.74 | 195.89
2018-08-01 19:00 | 205.78 | 201.8
2018-08-01 19:30 | 203.44 | 199.6
2018-08-01 20:00 | 203.37 | 199.45
2018-08-01 20:30 | 204.54 | 200.5
2018-08-01 21:00 | 202.79 | 198.69
2018-08-01 21:30 | 202.45 | 198.2
2018-08-01 22:00 | 201.07 | 196.73
2018-08-01 22:30 | 199.27 | 194.87
2018-08-01 23:00 | 196.79 | 192.38
2018-08-01 23:30 | 195.38 | 190.87
2018-08-02 | 194.06 | 189.56
2018-08-02 00:30 | 192.96 | 188.51
2018-08-02 01:00 | 191.72 | 187.18
2018-08-02 01:30 | 191.08 | 186.45
2018-08-02 02:00 | 190.16 | 185.52
2018-08-02 02:30 | 190.29 | 185.69
2018-08-02 03:00 | 189.93 | 185.37
2018-08-02 03:30 | 190.08 | 185.59
2018-08-02 04:00 | 190.66 | 186.18
2018-08-02 04:30 | 191.29 | 186.87
2018-08-02 05:00 | 192.86 | 188.49
2018-08-02 05:30 | 195.39 | 191.09
2018-08-02 06:00 | 198.34 | 194.46
2018-08-02 06:30 | 203.75 | 200.01
2018-08-02 07:00 | 207.83 | 204.31
2018-08-02 07:30 | 211.33 | 207.95
2018-08-02 08:00 | 210.11 | 206.71
2018-08-02 08:30 | 206.18 | 202.53
2018-08-02 09:00 | 201.55 | 197.75
2018-08-02 09:30 | 197.33 | 193.25
2018-08-02 10:00 | 195.82 | 191.61
2018-08-02 10:30 | 194.69 | 190.35
2018-08-02 11:00 | 194.39 | 189.92
2018-08-02 11:30 | 193.87 | 189.37
2018-08-02 12:00 | 193.14 | 188.56
2018-08-02 12:30 | 193.36 | 188.63
2018-08-02 13:00 | 192.93 | 188.15
2018-08-02 13:30 | 192.81 | 188.06
2018-08-02 14:00 | 193.43 | 188.76
2018-08-02 14:30 | 193.76 | 189.13
2018-08-02 15:00 | 194.59 | 189.86
2018-08-02 15:30 | 195.39 | 190.65
2018-08-02 16:00 | 195.96 | 191.38
2018-08-02 16:30 | 197.21 | 192.59
2018-08-02 17:00 | 198.57 | 193.88
2018-08-02 17:30 | 200.76 | 196.04
2018-08-02 18:00 | 204.25 | 199.67
2018-08-02 18:30 | 207.88 | 203.46
2018-08-02 19:00 | 209.6 | 205.33
2018-08-02 19:30 | 209.19 | 204.89
2018-08-02 20:00 | 208.07 | 203.7
2018-08-02 20:30 | 208.29 | 203.74
2018-08-02 21:00 | 206.97 | 202.29
2018-08-02 21:30 | 206.73 | 201.93
2018-08-02 22:00 | 204.94 | 200.13
2018-08-02 22:30 | 202.87 | 198
2018-08-02 23:00 | 200.73 | 195.88
2018-08-02 23:30 | 199.77 | 194.88
2018-08-03 | 198.44 | 193.41
2018-08-03 00:30 | 197.76 | 192.67
2018-08-03 01:00 | 196.6 | 191.49
2018-08-03 01:30 | 195.95 | 190.89
2018-08-03 02:00 | 195.4 | 190.33
2018-08-03 02:30 | 194.86 | 189.88
2018-08-03 03:00 | 194.69 | 189.72
2018-08-03 03:30 | 194.38 | 189.46
2018-08-03 04:00 | 194.78 | 189.85
2018-08-03 04:30 | 195.31 | 190.46
2018-08-03 05:00 | 196.16 | 191.37
2018-08-03 05:30 | 198.11 | 193.34
2018-08-03 06:00 | 200.72 | 196.06
2018-08-03 06:30 | 204.45 | 199.94
2018-08-03 07:00 | 207.48 | 203.13
2018-08-03 07:30 | 209.46 | 205.23
2018-08-03 08:00 | 208.5 | 204.23
2018-08-03 08:30 | 205.65 | 201.3
2018-08-03 09:00 | 202.45 | 197.78
2018-08-03 09:30 | 199.46 | 194.69
2018-08-03 10:00 | 197.5 | 192.84
2018-08-03 10:30 | 195.9 | 191.15
2018-08-03 11:00 | 194.9 | 190.22
2018-08-03 11:30 | 194.45 | 189.73
2018-08-03 12:00 | 194 | 189.24
2018-08-03 12:30 | 192.64 | 187.86
2018-08-03 13:00 | 192.66 | 187.69
2018-08-03 13:30 | 192.98 | 187.97
2018-08-03 14:00 | 193.25 | 188.24
2018-08-03 14:30 | 193.95 | 188.94
2018-08-03 15:00 | 194.11 | 189.12
2018-08-03 15:30 | 195.09 | 190.16
2018-08-03 16:00 | 196.64 | 191.72
2018-08-03 16:30 | 197.69 | 192.79
2018-08-03 17:00 | 199.49 | 194.64
2018-08-03 17:30 | 194.87 | 190.57
2018-08-03 18:00 | 185.28 | 181.62
2018-08-03 18:30 | 183.21 | 179.46
2018-08-03 19:00 | 182.74 | 178.9
2018-08-03 19:30 | 184.78 | 181.18
2018-08-03 20:00 | 184.75 | 181.16
2018-08-03 20:30 | 195.88 | 191.43
2018-08-03 21:00 | 202.61 | 197.74
2018-08-03 21:30 | 201.9 | 197.03
2018-08-03 22:00 | 201.09 | 196.11
2018-08-03 22:30 | 199.83 | 194.81
2018-08-03 23:00 | 199.3 | 194.25
2018-08-03 23:30 | 198.66 | 193.58
2018-08-04 | 197.12 | 192.06
2018-08-04 00:30 | 196.69 | 191.61
2018-08-04 01:00 | 196.07 | 190.88
2018-08-04 01:30 | 195.17 | 190.07
2018-08-04 02:00 | 194.87 | 189.72
2018-08-04 02:30 | 194.24 | 189.03
2018-08-04 03:00 | 194.05 | 188.82
2018-08-04 03:30 | 193.48 | 188.19
2018-08-04 04:00 | 194.17 | 188.99
2018-08-04 04:30 | 194.36 | 189.19
2018-08-04 05:00 | 194.85 | 189.7
2018-08-04 05:30 | 195.69 | 190.55
2018-08-04 06:00 | 197.27 | 192.18
2018-08-04 06:30 | 198.89 | 193.93
2018-08-04 07:00 | 200.63 | 195.77
2018-08-04 07:30 | 202.62 | 197.77
2018-08-04 08:00 | 202.82 | 197.98
2018-08-04 08:30 | 206.92 | 201.68
2018-08-04 09:00 | 206.99 | 201.54
2018-08-04 09:30 | 204.46 | 199.03
2018-08-04 10:00 | 203.03 | 197.62
2018-08-04 10:30 | 201.53 | 196.09
2018-08-04 11:00 | 201.63 | 196.1
2018-08-04 11:30 | 198.54 | 193.12
2018-08-04 12:00 | 196.17 | 190.81
2018-08-04 12:30 | 193.82 | 188.62
2018-08-04 13:00 | 192.27 | 187.23
2018-08-04 13:30 | 191.89 | 186.87
2018-08-04 14:00 | 192.09 | 187.01
2018-08-04 14:30 | 192.9 | 187.81
2018-08-04 15:00 | 193.32 | 188.27
2018-08-04 15:30 | 194.49 | 189.5
2018-08-04 16:00 | 196.27 | 191.24
2018-08-04 16:30 | 198.21 | 193.21
2018-08-04 17:00 | 200.38 | 195.35
2018-08-04 17:30 | 202.65 | 197.57
2018-08-04 18:00 | 206 | 201.13
2018-08-04 18:30 | 209.06 | 204.4
2018-08-04 19:00 | 209.95 | 205.39
2018-08-04 19:30 | 209.84 | 205.32
2018-08-04 20:00 | 209.04 | 204.5
2018-08-04 20:30 | 208.48 | 203.94
2018-08-04 21:00 | 207.79 | 203.23
2018-08-04 21:30 | 207.45 | 202.82
2018-08-04 22:00 | 206.47 | 201.71
2018-08-04 22:30 | 204.86 | 200.01
2018-08-04 23:00 | 203.27 | 198.35
2018-08-04 23:30 | 202.4 | 197.39
2018-08-05 | 201.36 | 196.2
2018-08-05 00:30 | 200.65 | 195.48
2018-08-05 01:00 | 199.53 | 194.29
2018-08-05 01:30 | 199.07 | 193.8
2018-08-05 02:00 | 198.38 | 193.12
2018-08-05 02:30 | 198.16 | 192.94
2018-08-05 03:00 | 197.97 | 192.74
2018-08-05 03:30 | 198.03 | 192.79
2018-08-05 04:00 | 198.2 | 192.97
2018-08-05 04:30 | 198.6 | 193.37
2018-08-05 05:00 | 199.11 | 193.9
2018-08-05 05:30 | 199.97 | 194.83
2018-08-05 06:00 | 200.89 | 195.76
2018-08-05 06:30 | 201.83 | 196.8
2018-08-05 07:00 | 203.99 | 198.99
2018-08-05 07:30 | 205.4 | 200.44
2018-08-05 08:00 | 205.95 | 200.95
2018-08-05 08:30 | 208.8 | 203.53
2018-08-05 09:00 | 210.85 | 205.53
2018-08-05 09:30 | 207.74 | 202.44
2018-08-05 10:00 | 202.95 | 197.94
2018-08-05 10:30 | 200.45 | 195.4
2018-08-05 11:00 | 200.03 | 194.92
2018-08-05 11:30 | 192.93 | 188.2
2018-08-05 12:00 | 191.11 | 186.49
2018-08-05 12:30 | 190.48 | 185.86
2018-08-05 13:00 | 189.6 | 184.92
2018-08-05 13:30 | 189.37 | 184.7
2018-08-05 14:00 | 190.43 | 185.76
2018-08-05 14:30 | 190.63 | 185.98
2018-08-05 15:00 | 191.72 | 187.01
2018-08-05 15:30 | 193.4 | 188.69
2018-08-05 16:00 | 194.77 | 190.11
2018-08-05 16:30 | 196.32 | 191.71
2018-08-05 17:00 | 197.6 | 193.05
2018-08-05 17:30 | 199.79 | 195.03
2018-08-05 18:00 | 202.36 | 197.79
2018-08-05 18:30 | 204.59 | 200.14
2018-08-05 19:00 | 204.99 | 200.52
2018-08-05 19:30 | 203.31 | 198.81
2018-08-05 20:00 | 201.68 | 197.12
2018-08-05 20:30 | 200.95 | 196.31
2018-08-05 21:00 | 199.83 | 195.13
2018-08-05 21:30 | 198.37 | 193.68
2018-08-05 22:00 | 197.54 | 192.76
2018-08-05 22:30 | 196.01 | 191.05
2018-08-05 23:00 | 194.62 | 189.56
2018-08-05 23:30 | 193.58 | 188.53
2018-08-06 | 192.87 | 187.73
2018-08-06 00:30 | 192.35 | 187.19
2018-08-06 01:00 | 191.04 | 185.9
2018-08-06 01:30 | 190.27 | 185.1
2018-08-06 02:00 | 189.96 | 184.8
2018-08-06 02:30 | 189.51 | 184.36
2018-08-06 03:00 | 189.48 | 184.32
2018-08-06 03:30 | 189.63 | 184.48
2018-08-06 04:00 | 189.5 | 184.37
2018-08-06 04:30 | 190.41 | 185.28
2018-08-06 05:00 | 191.12 | 186.01
2018-08-06 05:30 | 192.29 | 187.22
2018-08-06 06:00 | 194.71 | 189.71
2018-08-06 06:30 | 197.75 | 193.2
2018-08-06 07:00 | 199.68 | 195.46
2018-08-06 07:30 | 201.57 | 197.44
2018-08-06 08:00 | 201.73 | 197.55
2018-08-06 08:30 | 200.08 | 195.87
2018-08-06 09:00 | 197.7 | 193.45
2018-08-06 09:30 | 195.94 | 191.7
2018-08-06 10:00 | 195.27 | 190.98
2018-08-06 10:30 | 194.89 | 190.6
2018-08-06 11:00 | 193.57 | 189.32
2018-08-06 11:30 | 193.52 | 189.33
2018-08-06 12:00 | 194.3 | 190.15
2018-08-06 12:30 | 193.36 | 189.24
2018-08-06 13:00 | 192.87 | 188.78
2018-08-06 13:30 | 192.57 | 188.5
2018-08-06 14:00 | 192.01 | 188.07
2018-08-06 14:30 | 189.27 | 185.49
2018-08-06 15:00 | 189.21 | 185.38
2018-08-06 15:30 | 190.06 | 185.97
2018-08-06 16:00 | 191.42 | 187.3
2018-08-06 16:30 | 194.28 | 189.92
2018-08-06 17:00 | 199.09 | 194.46
2018-08-06 17:30 | 201.73 | 197.1
2018-08-06 18:00 | 205.59 | 201
2018-08-06 18:30 | 209.07 | 204.93
2018-08-06 19:00 | 210.05 | 206.06
2018-08-06 19:30 | 208.07 | 203.99
2018-08-06 20:00 | 205.99 | 201.89
2018-08-06 20:30 | 205.15 | 201.06
2018-08-06 21:00 | 203.17 | 199.08
2018-08-06 21:30 | 202.38 | 198.3
2018-08-06 22:00 | 200.25 | 196.08
2018-08-06 22:30 | 198.61 | 194.38
2018-08-06 23:00 | 196.32 | 192.06
2018-08-06 23:30 | 194.82 | 190.38
2018-08-07 | 193.6 | 189.11
2018-08-07 00:30 | 192.55 | 188.18
2018-08-07 01:00 | 191.11 | 186.56
2018-08-07 01:30 | 190.46 | 185.84
2018-08-07 02:00 | 189.38 | 184.89
2018-08-07 02:30 | 188.55 | 184.11
2018-08-07 03:00 | 188.81 | 184.4
2018-08-07 03:30 | 188.09 | 183.75
2018-08-07 04:00 | 188.5 | 184.17
2018-08-07 04:30 | 189.1 | 184.81
2018-08-07 05:00 | 190.64 | 186.42
2018-08-07 05:30 | 193.64 | 189.55
2018-08-07 06:00 | 197.36 | 193.55
2018-08-07 06:30 | 202.74 | 198.98
2018-08-07 07:00 | 201.08 | 197.85
2018-08-07 07:30 | 194.46 | 191.64
2018-08-07 08:00 | 193.78 | 190.89
2018-08-07 08:30 | 161.32 | 156.05
2018-08-07 09:00 | 169.43 | 163.18
2018-08-07 09:30 | 165.39 | 159.39
2018-08-07 10:00 | 161.22 | 155.08
2018-08-07 10:30 | 159.5 | 153.09
2018-08-07 11:00 | 166.6 | 159.79
2018-08-07 11:30 | 171.13 | 163.46
2018-08-07 12:00 | 170.28 | 162.38
2018-08-07 12:30 | 167.91 | 159.84
2018-08-07 13:00 | 172.88 | 164.49
2018-08-07 13:30 | 176.85 | 168.19
2018-08-07 14:00 | 175.8 | 167.34
2018-08-07 14:30 | 175.79 | 167.32
2018-08-07 15:00 | 177.02 | 168.43
2018-08-07 15:30 | 179.02 | 170.35
2018-08-07 16:00 | 181.41 | 172.93
2018-08-07 16:30 | 183.14 | 174.6
2018-08-07 17:00 | 185.45 | 176.61
2018-08-07 17:30 | 189.22 | 179.6
2018-08-07 18:00 | 192.48 | 183.1
2018-08-07 18:30 | 196.29 | 187.39
2018-08-07 19:00 | 199.34 | 190.66
2018-08-07 19:30 | 198.56 | 190.02
2018-08-07 20:00 | 197.98 | 189.37
2018-08-07 20:30 | 197.6 | 188.85
2018-08-07 21:00 | 196.3 | 187.44
2018-08-07 21:30 | 194.36 | 186.24
2018-08-07 22:00 | 191.89 | 183.66
2018-08-07 22:30 | 189.6 | 181.09
2018-08-07 23:00 | 187.14 | 178.48
2018-08-07 23:30 | 184.56 | 176.53
2018-08-08 | 183.01 | 174.66
2018-08-08 00:30 | 182.38 | 173.91
2018-08-08 01:00 | 180.17 | 171.77
2018-08-08 01:30 | 179.57 | 170.54
2018-08-08 02:00 | 178.16 | 169.85
2018-08-08 02:30 | 178.13 | 169.66
2018-08-08 03:00 | 177.72 | 169.28
2018-08-08 03:30 | 177.36 | 168.95
2018-08-08 04:00 | 176.45 | 168.19
2018-08-08 04:30 | 170.95 | 164.41
2018-08-08 05:00 | 196.92 | 192.5
2018-08-08 05:30 | 199.09 | 194.77
2018-08-08 06:00 | 202.5 | 198.55
2018-08-08 06:30 | 207.05 | 203.43
2018-08-08 07:00 | 207.03 | 203.54
2018-08-08 07:30 | 206.46 | 203.22
2018-08-08 08:00 | 202.17 | 199.06
2018-08-08 08:30 | 166.04 | 161.07
2018-08-08 09:00 | 163.16 | 156.87
2018-08-08 09:30 | 166.79 | 160.2
2018-08-08 10:00 | 163.79 | 156.97
2018-08-08 10:30 | 161.8 | 154.29
2018-08-08 11:00 | 163.13 | 155.15
2018-08-08 11:30 | 161.96 | 153.77
2018-08-08 12:00 | 160.4 | 152.1
2018-08-08 12:30 | 159.52 | 150.93
2018-08-08 13:00 | 159.07 | 150.12
2018-08-08 13:30 | 159.17 | 149.83
2018-08-08 14:00 | 159.24 | 150.45
2018-08-08 14:30 | 172.15 | 163.01
2018-08-08 15:00 | 170.29 | 161.34
2018-08-08 15:30 | 173.03 | 164.22
2018-08-08 16:00 | 166.46 | 157.53
2018-08-08 16:30 | 163.27 | 154.69
2018-08-08 17:00 | 165.48 | 157.19
2018-08-08 17:30 | 169.05 | 160.2
2018-08-08 18:00 | 173.58 | 164.54
2018-08-08 18:30 | 176.92 | 168.47
2018-08-08 19:00 | 179.47 | 171.24
2018-08-08 19:30 | 179.06 | 170.5
2018-08-08 20:00 | 179.17 | 170.67
2018-08-08 20:30 | 158.68 | 150.17
2018-08-08 21:00 | 152.51 | 144.06
2018-08-08 21:30 | 152.16 | 143.5
2018-08-08 22:00 | 150.06 | 141.06
2018-08-08 22:30 | 147.19 | 137.83
2018-08-08 23:00 | 145.42 | 135.54
2018-08-08 23:30 | 142.68 | 133.39
2018-08-09 | 141.2 | 132
2018-08-09 00:30 | 141.02 | 131.71
2018-08-09 01:00 | 139.34 | 130.14
2018-08-09 01:30 | 138.83 | 129.84
2018-08-09 02:00 | 138.25 | 129.4
2018-08-09 02:30 | 136.37 | 129.02
2018-08-09 03:00 | 135.19 | 128.35
2018-08-09 03:30 | 135.93 | 128.93
2018-08-09 04:00 | 136.98 | 129.92
2018-08-09 04:30 | 137.88 | 130.92
2018-08-09 05:00 | 159.67 | 152.8
2018-08-09 05:30 | 171.72 | 165.21
2018-08-09 06:00 | 176.36 | 169.37
2018-08-09 06:30 | 181.46 | 175.12
2018-08-09 07:00 | 186.59 | 180.06
2018-08-09 07:30 | 189.23 | 182.94
2018-08-09 08:00 | 186.37 | 179.98
2018-08-09 08:30 | 181.59 | 174.43
2018-08-09 09:00 | 176.69 | 169.08
2018-08-09 09:30 | 171.69 | 163.9
2018-08-09 10:00 | 168.31 | 160.27
2018-08-09 10:30 | 145.2 | 136.9
2018-08-09 11:00 | 138.31 | 129.86
2018-08-09 11:30 | 166.3 | 160.14
2018-08-09 12:00 | 180.47 | 176.39
2018-08-09 12:30 | 179.98 | 175.81
2018-08-09 13:00 | 180.42 | 176.15
2018-08-09 13:30 | 180.42 | 176.16
2018-08-09 14:00 | 181.15 | 176.94
2018-08-09 14:30 | 180.8 | 176.63
2018-08-09 15:00 | 180.87 | 176.71
2018-08-09 15:30 | 181.94 | 177.8
2018-08-09 16:00 | 183.65 | 179.52
2018-08-09 16:30 | 184.9 | 180.63
2018-08-09 17:00 | 187.32 | 182.99
2018-08-09 17:30 | 189.54 | 185.16
2018-08-09 18:00 | 193.01 | 188.78
2018-08-09 18:30 | 197.81 | 193.85
2018-08-09 19:00 | 200.82 | 197.01
2018-08-09 19:30 | 200.79 | 196.94
2018-08-09 20:00 | 200.17 | 196.18
2018-08-09 20:30 | 199.67 | 195.64
2018-08-09 21:00 | 198.49 | 194.44
2018-08-09 21:30 | 198.47 | 194.36
2018-08-09 22:00 | 197.52 | 193.28
2018-08-09 22:30 | 195.49 | 191.18
2018-08-09 23:00 | 193.59 | 189.22
2018-08-09 23:30 | 191.76 | 187.29
2018-08-10 | 190.56 | 186.03
2018-08-10 00:30 | 190.1 | 185.61
2018-08-10 01:00 | 188.83 | 184.25
2018-08-10 01:30 | 187.78 | 183.26
2018-08-10 02:00 | 187.4 | 182.83
2018-08-10 02:30 | 187.4 | 182.83
2018-08-10 03:00 | 187.07 | 182.49
2018-08-10 03:30 | 187.64 | 183.08
2018-08-10 04:00 | 188.07 | 183.52
2018-08-10 04:30 | 188.88 | 184.38
2018-08-10 05:00 | 190.04 | 185.71
2018-08-10 05:30 | 192.44 | 188.25
2018-08-10 06:00 | 195.45 | 191.27
2018-08-10 06:30 | 200.82 | 196.91
2018-08-10 07:00 | 204.77 | 201.02
2018-08-10 07:30 | 207.79 | 204.15
2018-08-10 08:00 | 205.44 | 201.77
2018-08-10 08:30 | 200.58 | 196.75
2018-08-10 09:00 | 194.66 | 190.75
2018-08-10 09:30 | 191.32 | 187.19
2018-08-10 10:00 | 191.63 | 187.34
2018-08-10 10:30 | 197.35 | 192.58
2018-08-10 11:00 | 196.22 | 191.48
2018-08-10 11:30 | 192.26 | 187.79
2018-08-10 12:00 | 183.51 | 179.58
2018-08-10 12:30 | 183.03 | 178.94
2018-08-10 13:00 | 169.17 | 162.41
2018-08-10 13:30 | 162.95 | 152.68
2018-08-10 14:00 | 175.54 | 165.14
2018-08-10 14:30 | 178.27 | 167.84
2018-08-10 15:00 | 179.37 | 169.02
2018-08-10 15:30 | 179.85 | 169.41
2018-08-10 16:00 | 180.27 | 170.05
2018-08-10 16:30 | 181.05 | 171.18
2018-08-10 17:00 | 182.43 | 172.76
2018-08-10 17:30 | 184.09 | 174.21
2018-08-10 18:00 | 186.53 | 176.83
2018-08-10 18:30 | 189.64 | 180.14
2018-08-10 19:00 | 190.75 | 181.29
2018-08-10 19:30 | 189.39 | 180.23
2018-08-10 20:00 | 177.33 | 169.25
2018-08-10 20:30 | 202.28 | 197.65
2018-08-10 21:00 | 202.29 | 197.93
2018-08-10 21:30 | 202.11 | 197.66
2018-08-10 22:00 | 200.9 | 196.39
2018-08-10 22:30 | 199.54 | 194.95
2018-08-10 23:00 | 198.1 | 193.43
2018-08-10 23:30 | 197.13 | 192.39
2018-08-11 | 195.78 | 190.97
2018-08-11 00:30 | 195.09 | 190.34
2018-08-11 01:00 | 193.78 | 188.96
2018-08-11 01:30 | 193.02 | 188.1
2018-08-11 02:00 | 192.67 | 187.7
2018-08-11 02:30 | 192.2 | 187.23
2018-08-11 03:00 | 191.95 | 187
2018-08-11 03:30 | 191.87 | 186.94
2018-08-11 04:00 | 191.8 | 186.89
2018-08-11 04:30 | 191.78 | 186.9
2018-08-11 05:00 | 192.22 | 187.36
2018-08-11 05:30 | 192.97 | 188.3
2018-08-11 06:00 | 193.8 | 189.19
2018-08-11 06:30 | 196.02 | 191.42
2018-08-11 07:00 | 197.74 | 193.24
2018-08-11 07:30 | 199.1 | 194.66
2018-08-11 08:00 | 200.51 | 195.85
2018-08-11 08:30 | 198.14 | 193.45
2018-08-11 09:00 | 193.43 | 188.33
2018-08-11 09:30 | 166.29 | 159.2
2018-08-11 10:00 | 164.77 | 157.26
2018-08-11 10:30 | 161.35 | 153.91
2018-08-11 11:00 | 159.46 | 151.94
2018-08-11 11:30 | 160.94 | 153.5
2018-08-11 12:00 | 160.43 | 152.88
2018-08-11 12:30 | 160.09 | 152.3
2018-08-11 13:00 | 159.3 | 151.82
2018-08-11 13:30 | 159.72 | 151.68
2018-08-11 14:00 | 160.56 | 152.24
2018-08-11 14:30 | 162.14 | 153.11
2018-08-11 15:00 | 176.21 | 169.31
2018-08-11 15:30 | 189.78 | 184.84
2018-08-11 16:00 | 191.85 | 186.85
2018-08-11 16:30 | 195.55 | 190.35
2018-08-11 17:00 | 197.73 | 192.55
2018-08-11 17:30 | 200.1 | 195.03
2018-08-11 18:00 | 201.69 | 196.8
2018-08-11 18:30 | 204.43 | 199.63
2018-08-11 19:00 | 204.77 | 200
2018-08-11 19:30 | 204.62 | 199.77
2018-08-11 20:00 | 204.07 | 199.12
2018-08-11 20:30 | 203.22 | 198.21
2018-08-11 21:00 | 202.69 | 197.67
2018-08-11 21:30 | 202.5 | 197.38
2018-08-11 22:00 | 201.17 | 195.6
2018-08-11 22:30 | 175.76 | 166.85
2018-08-11 23:00 | 176.61 | 164.99
2018-08-11 23:30 | 184.2 | 173.49
2018-08-12 | 183.45 | 172.98
2018-08-12 00:30 | 181.96 | 171.29
2018-08-12 01:00 | 178.89 | 168.35
2018-08-12 01:30 | 176.83 | 167.13
2018-08-12 02:00 | 176.16 | 166.33
2018-08-12 02:30 | 176.13 | 166.22
2018-08-12 03:00 | 177.04 | 167.05
2018-08-12 03:30 | 177.09 | 166.98
2018-08-12 04:00 | 177.7 | 167.74
2018-08-12 04:30 | 178.36 | 168.57
2018-08-12 05:00 | 178.43 | 168.6
2018-08-12 05:30 | 179.46 | 169.8
2018-08-12 06:00 | 180.27 | 170.42
2018-08-12 06:30 | 181.48 | 171.23
2018-08-12 07:00 | 187.09 | 177.79
2018-08-12 07:30 | 193.43 | 185.07
2018-08-12 08:00 | 191.64 | 183.5
2018-08-12 08:30 | 190.04 | 182.12
2018-08-12 09:00 | 189.01 | 180.9
2018-08-12 09:30 | 187.27 | 179.09
2018-08-12 10:00 | 184.7 | 176.49
2018-08-12 10:30 | 180.94 | 172.86
2018-08-12 11:00 | 180.62 | 172.34
2018-08-12 11:30 | 180.11 | 171.73
2018-08-12 12:00 | 180.7 | 172.06
2018-08-12 12:30 | 181.67 | 173.31
2018-08-12 13:00 | 180.06 | 171.6
2018-08-12 13:30 | 179.89 | 171.37
2018-08-12 14:00 | 179.96 | 169.43
2018-08-12 14:30 | 181.05 | 170.3
2018-08-12 15:00 | 179.87 | 169.78
2018-08-12 15:30 | 176.94 | 165.98
2018-08-12 16:00 | 178.56 | 167.1
2018-08-12 16:30 | 182.44 | 171.75
2018-08-12 17:00 | 184.86 | 174.52
2018-08-12 17:30 | 188.35 | 178.29
2018-08-12 18:00 | 191.16 | 181.59
2018-08-12 18:30 | 194.89 | 185.28
2018-08-12 19:00 | 197.83 | 187.98
2018-08-12 19:30 | 197.31 | 187.32
2018-08-12 20:00 | 194.62 | 184.19
2018-08-12 20:30 | 189.77 | 178.03
2018-08-12 21:00 | 188.61 | 178.15
2018-08-12 21:30 | 187.54 | 177.69
2018-08-12 22:00 | 186.93 | 177.1
2018-08-12 22:30 | 185.36 | 175.6
2018-08-12 23:00 | 182.47 | 173.45
2018-08-12 23:30 | 181.58 | 173
2018-08-13 | 179.66 | 171.47
2018-08-13 00:30 | 179.45 | 171.41
2018-08-13 01:00 | 178.87 | 170.12
2018-08-13 01:30 | 178.87 | 169.94
2018-08-13 02:00 | 177.9 | 168.85
2018-08-13 02:30 | 178.09 | 168.94
2018-08-13 03:00 | 177.69 | 168.4
2018-08-13 03:30 | 177.87 | 168.58
2018-08-13 04:00 | 177.76 | 168.48
2018-08-13 04:30 | 179.12 | 169.94
2018-08-13 05:00 | 180.41 | 171.34
2018-08-13 05:30 | 183.15 | 173.57
2018-08-13 06:00 | 186.46 | 177.01
2018-08-13 06:30 | 191.05 | 182.27
2018-08-13 07:00 | 195.33 | 187.33
2018-08-13 07:30 | 195.7 | 188.5
2018-08-13 08:00 | 193.53 | 186.73
2018-08-13 08:30 | 189.71 | 182.69
2018-08-13 09:00 | 187.61 | 179.65
2018-08-13 09:30 | 185.47 | 176.9
2018-08-13 10:00 | 183.99 | 175.1
2018-08-13 10:30 | 182.05 | 172.66
2018-08-13 11:00 | 181.39 | 171.74
2018-08-13 11:30 | 179.31 | 169
2018-08-13 12:00 | 178.79 | 167.72
2018-08-13 12:30 | 178.68 | 168.47
2018-08-13 13:00 | 177.94 | 167.29
2018-08-13 13:30 | 178.56 | 168.27
2018-08-13 14:00 | 180.48 | 170.32
2018-08-13 14:30 | 181 | 170.57
2018-08-13 15:00 | 181.92 | 171.26
2018-08-13 15:30 | 184.35 | 173.47
2018-08-13 16:00 | 186.46 | 175.39
2018-08-13 16:30 | 186.99 | 176.35
2018-08-13 17:00 | 189.44 | 178.37
2018-08-13 17:30 | 193.82 | 182.29
2018-08-13 18:00 | 198.3 | 187.23
2018-08-13 18:30 | 200.15 | 191.45
2018-08-13 19:00 | 202.77 | 194.65
2018-08-13 19:30 | 202.82 | 194.3
2018-08-13 20:00 | 202.3 | 193.62
2018-08-13 20:30 | 201.16 | 192.46
2018-08-13 21:00 | 200.11 | 191.53
2018-08-13 21:30 | 198.39 | 190.29
2018-08-13 22:00 | 196.18 | 188
2018-08-13 22:30 | 193.83 | 185.36
2018-08-13 23:00 | 192.47 | 183.82
2018-08-13 23:30 | 191.04 | 182.41
2018-08-14 | 189.72 | 181.25
2018-08-14 00:30 | 189.44 | 180.97
2018-08-14 01:00 | 187.08 | 179.65
2018-08-14 01:30 | 188.06 | 179.17
2018-08-14 02:00 | 188.36 | 178.96
2018-08-14 02:30 | 188.37 | 178.82
2018-08-14 03:00 | 188.74 | 178.76
2018-08-14 03:30 | 188.63 | 178.7
2018-08-14 04:00 | 188.56 | 178.91
2018-08-14 04:30 | 189.69 | 180.19
2018-08-14 05:00 | 191.53 | 182.29
2018-08-14 05:30 | 193.8 | 184.99
2018-08-14 06:00 | 197.66 | 188.95
2018-08-14 06:30 | 203.65 | 194.82
2018-08-14 07:00 | 208.51 | 200.22
2018-08-14 07:30 | 209.13 | 201.34
2018-08-14 08:00 | 207.86 | 199.84
2018-08-14 08:30 | 201.28 | 192.66
2018-08-14 09:00 | 196.33 | 187.1
2018-08-14 09:30 | 192.03 | 182.04
2018-08-14 10:00 | 185.31 | 175.99
2018-08-14 10:30 | 174.15 | 165.87
2018-08-14 11:00 | 171.87 | 163.44
2018-08-14 11:30 | 171.56 | 163.03
2018-08-14 12:00 | 171.04 | 162.5
2018-08-14 12:30 | 170.11 | 161.49
2018-08-14 13:00 | 170.22 | 161.46
2018-08-14 13:30 | 170.12 | 161.22
2018-08-14 14:00 | 169.7 | 160.96
2018-08-14 14:30 | 169.48 | 160.77
2018-08-14 15:00 | 170.29 | 161.51
2018-08-14 15:30 | 171.29 | 162.43
2018-08-14 16:00 | 172.85 | 164.16
2018-08-14 16:30 | 173.27 | 164.78
2018-08-14 17:00 | 175.89 | 166.82
2018-08-14 17:30 | 179.01 | 169.64
2018-08-14 18:00 | 180.03 | 170.03
2018-08-14 18:30 | 196.33 | 185.06
2018-08-14 19:00 | 201.41 | 190.4
2018-08-14 19:30 | 199.29 | 188.06
2018-08-14 20:00 | 198.63 | 187.31
2018-08-14 20:30 | 198.45 | 187.17
2018-08-14 21:00 | 197.53 | 186.1
2018-08-14 21:30 | 196.28 | 185.37
2018-08-14 22:00 | 194.38 | 183.48
2018-08-14 22:30 | 193.01 | 181.37
2018-08-14 23:00 | 191.05 | 179.13
2018-08-14 23:30 | 190.6 | 180.09
2018-08-15 | 188.47 | 179.68
2018-08-15 00:30 | 188.88 | 179.53
2018-08-15 01:00 | 187.7 | 178.68
2018-08-15 01:30 | 187.35 | 178.23
2018-08-15 02:00 | 187.52 | 178.09
2018-08-15 02:30 | 187.75 | 178.21
2018-08-15 03:00 | 188.37 | 178.84
2018-08-15 03:30 | 188.91 | 179.31
2018-08-15 04:00 | 189.64 | 180.08
2018-08-15 04:30 | 190.4 | 180.76
2018-08-15 05:00 | 191.07 | 181.4
2018-08-15 05:30 | 193.29 | 184.18
2018-08-15 06:00 | 196.83 | 188.42
2018-08-15 06:30 | 202.4 | 194.18
2018-08-15 07:00 | 202.1 | 194.47
2018-08-15 07:30 | 198.75 | 195.09
2018-08-15 08:00 | 199.56 | 195.91
2018-08-15 08:30 | 201.1 | 197.37
2018-08-15 09:00 | 191.78 | 184.14
2018-08-15 09:30 | 186.09 | 176.55
2018-08-15 10:00 | 183.15 | 173.27
2018-08-15 10:30 | 183.82 | 173.46
2018-08-15 11:00 | 183.04 | 172.81
2018-08-15 11:30 | 181.07 | 170.76
2018-08-15 12:00 | 170.32 | 161.58
2018-08-15 12:30 | 169.21 | 160.42
2018-08-15 13:00 | 168.89 | 159.9
2018-08-15 13:30 | 168.76 | 159.78
2018-08-15 14:00 | 168.76 | 159.97
2018-08-15 14:30 | 167.96 | 159.39
2018-08-15 15:00 | 167.97 | 159.32
2018-08-15 15:30 | 168.86 | 160.2
2018-08-15 16:00 | 170.43 | 161.91
2018-08-15 16:30 | 170.89 | 162.35
2018-08-15 17:00 | 173.03 | 164.25
2018-08-15 17:30 | 174.1 | 165.26
2018-08-15 18:00 | 176.74 | 168.21
2018-08-15 18:30 | 176.68 | 170.71
2018-08-15 19:00 | 182.05 | 179.13
2018-08-15 19:30 | 181.9 | 179.07
2018-08-15 20:00 | 182.87 | 180.05
2018-08-15 20:30 | 177.96 | 170.8
2018-08-15 21:00 | 178.09 | 170.32
2018-08-15 21:30 | 176.91 | 169.88
2018-08-15 22:00 | 175.44 | 168.57
2018-08-15 22:30 | 173.62 | 166.68
2018-08-15 23:00 | 171.94 | 164.91
2018-08-15 23:30 | 170.36 | 163.42
2018-08-16 | 169.04 | 162.12
2018-08-16 00:30 | 168.51 | 161.4
2018-08-16 01:00 | 167.85 | 160.58
2018-08-16 01:30 | 166.61 | 159.33
2018-08-16 02:00 | 166.73 | 159.51
2018-08-16 02:30 | 166.11 | 158.87
2018-08-16 03:00 | 166.17 | 158.98
2018-08-16 03:30 | 166.25 | 159.05
2018-08-16 04:00 | 166.71 | 159.52
2018-08-16 04:30 | 167.84 | 160.73
2018-08-16 05:00 | 169.27 | 162.31
2018-08-16 05:30 | 171.6 | 164.93
2018-08-16 06:00 | 175.34 | 168.46
2018-08-16 06:30 | 180.37 | 174
2018-08-16 07:00 | 153.39 | 148.33
2018-08-16 07:30 | 170.96 | 165.78
2018-08-16 08:00 | 152.58 | 148.23
2018-08-16 08:30 | 183.36 | 181.66
2018-08-16 09:00 | 161.47 | 157.29
2018-08-16 09:30 | 156.54 | 151.56
2018-08-16 10:00 | 158.05 | 153.1
2018-08-16 10:30 | 164.44 | 157.68
2018-08-16 11:00 | 167.07 | 159.61
2018-08-16 11:30 | 167.23 | 159.59
2018-08-16 12:00 | 167.08 | 159.33
2018-08-16 12:30 | 166.49 | 158.25
2018-08-16 13:00 | 167.55 | 158.69
2018-08-16 13:30 | 168.07 | 159.1
2018-08-16 14:00 | 168.91 | 159.99
2018-08-16 14:30 | 169.74 | 160.72
2018-08-16 15:00 | 170.12 | 160.94
2018-08-16 15:30 | 170.74 | 161.61
2018-08-16 16:00 | 171.71 | 162.71
2018-08-16 16:30 | 172.33 | 163.76
2018-08-16 17:00 | 171.99 | 164.11
2018-08-16 17:30 | 189 | 186.41
2018-08-16 18:00 | 187.16 | 184.64
2018-08-16 18:30 | 185.27 | 182.64
2018-08-16 19:00 | 184.82 | 182.07
2018-08-16 19:30 | 185.87 | 183.26
2018-08-16 20:00 | 186.81 | 184.29
2018-08-16 20:30 | 178.76 | 171.87
2018-08-16 21:00 | 179.59 | 171.35
2018-08-16 21:30 | 179.12 | 171.03
2018-08-16 22:00 | 177.9 | 169.67
2018-08-16 22:30 | 176.28 | 167.92
2018-08-16 23:00 | 184.94 | 177.78
2018-08-16 23:30 | 202.05 | 196.73
2018-08-17 | 200.54 | 195.11
2018-08-17 00:30 | 200.16 | 194.7
2018-08-17 01:00 | 198.85 | 193.39
2018-08-17 01:30 | 198.46 | 192.98
2018-08-17 02:00 | 197.87 | 192.42
2018-08-17 02:30 | 197.37 | 191.95
2018-08-17 03:00 | 197.09 | 191.71
2018-08-17 03:30 | 197.4 | 192.06
2018-08-17 04:00 | 197.71 | 192.39
2018-08-17 04:30 | 198.59 | 193.33
2018-08-17 05:00 | 199.92 | 194.7
2018-08-17 05:30 | 202.38 | 197.26
2018-08-17 06:00 | 205.08 | 201.57
2018-08-17 06:30 | 199.35 | 194.85
2018-08-17 07:00 | 203.48 | 199.73
2018-08-17 07:30 | 217.27 | 215.87
2018-08-17 08:00 | 216.88 | 215.55
2018-08-17 08:30 | 219.86 | 218.45
2018-08-17 09:00 | 222.03 | 220.53
2018-08-17 09:30 | 203.93 | 199.93
2018-08-17 10:00 | 200.14 | 195.08
2018-08-17 10:30 | 198.27 | 192.95
2018-08-17 11:00 | 194.71 | 189.68
2018-08-17 11:30 | 191.82 | 187.12
2018-08-17 12:00 | 191.79 | 187
2018-08-17 12:30 | 191.88 | 186.94
2018-08-17 13:00 | 192.07 | 186.96
2018-08-17 13:30 | 191.93 | 186.77
2018-08-17 14:00 | 193.23 | 188.02
2018-08-17 14:30 | 193.71 | 188.42
2018-08-17 15:00 | 169.23 | 161.56
2018-08-17 15:30 | 166.84 | 158.72
2018-08-17 16:00 | 168.15 | 158.74
2018-08-17 16:30 | 179.3 | 169.74
2018-08-17 17:00 | 182.45 | 172.6
2018-08-17 17:30 | 184.6 | 174.31
2018-08-17 18:00 | 186.11 | 176.07
2018-08-17 18:30 | 187.95 | 178.23
2018-08-17 19:00 | 190.36 | 180.94
2018-08-17 19:30 | 190.54 | 180.81
2018-08-17 20:00 | 189.5 | 179.92
2018-08-17 20:30 | 189.45 | 180.01
2018-08-17 21:00 | 188.9 | 179.24
2018-08-17 21:30 | 187.95 | 178.91
2018-08-17 22:00 | 187.53 | 178.38
2018-08-17 22:30 | 185.57 | 176.57
2018-08-17 23:00 | 183.76 | 174.43
2018-08-17 23:30 | 183.5 | 173.98
2018-08-18 | 181.99 | 172.82
2018-08-18 00:30 | 180.22 | 171.42
2018-08-18 01:00 | 178.92 | 170.1
2018-08-18 01:30 | 179.37 | 169.28
2018-08-18 02:00 | 178.68 | 168.93
2018-08-18 02:30 | 177.68 | 168.58
2018-08-18 03:00 | 178.49 | 169.38
2018-08-18 03:30 | 178.8 | 169.49
2018-08-18 04:00 | 178.96 | 169.56
2018-08-18 04:30 | 178.24 | 168.92
2018-08-18 05:00 | 180.47 | 171.24
2018-08-18 05:30 | 181.32 | 172.22
2018-08-18 06:00 | 183.51 | 174.57
2018-08-18 06:30 | 184.94 | 176.51
2018-08-18 07:00 | 187.27 | 178.36
2018-08-18 07:30 | 188.09 | 178.99
2018-08-18 08:00 | 186.7 | 177.29
2018-08-18 08:30 | 183.46 | 173.3
2018-08-18 09:00 | 180.73 | 170.88
2018-08-18 09:30 | 180.43 | 170.05
2018-08-18 10:00 | 178.34 | 168.8
2018-08-18 10:30 | 175.1 | 166.04
2018-08-18 11:00 | 174.48 | 165.16
2018-08-18 11:30 | 173.92 | 164.64
2018-08-18 12:00 | 172.99 | 163.56
2018-08-18 12:30 | 172.4 | 162.95
2018-08-18 13:00 | 172.33 | 162.81
2018-08-18 13:30 | 172.15 | 162.52
2018-08-18 14:00 | 167.31 | 157.26
2018-08-18 14:30 | 159.5 | 149.23
2018-08-18 15:00 | 153.78 | 142.72
2018-08-18 15:30 | 166.28 | 155.14
2018-08-18 16:00 | 166.7 | 155.6
2018-08-18 16:30 | 167.4 | 155.27
2018-08-18 17:00 | 167.03 | 155.2
2018-08-18 17:30 | 167.96 | 155.77
2018-08-18 18:00 | 161.97 | 149.66
2018-08-18 18:30 | 164.28 | 152.11
2018-08-18 19:00 | 165.19 | 152.98
2018-08-18 19:30 | 164.18 | 151.86
2018-08-18 20:00 | 162.62 | 150.34
2018-08-18 20:30 | 161.86 | 149.57
2018-08-18 21:00 | 161.2 | 148.76
2018-08-18 21:30 | 160.26 | 148.31
2018-08-18 22:00 | 159.26 | 147.58
2018-08-18 22:30 | 172.54 | 160.6
2018-08-18 23:00 | 174.52 | 162.87
2018-08-18 23:30 | 173.43 | 162.18
2018-08-19 | 172.28 | 160.96
2018-08-19 00:30 | 170.54 | 160.62
2018-08-19 01:00 | 170.2 | 160.23
2018-08-19 01:30 | 169.34 | 160.18
2018-08-19 02:00 | 168.97 | 159.47
2018-08-19 02:30 | 169.5 | 160
2018-08-19 03:00 | 168.78 | 159.34
2018-08-19 03:30 | 168.73 | 159.31
2018-08-19 04:00 | 168.62 | 159.22
2018-08-19 04:30 | 168.51 | 159.13
2018-08-19 05:00 | 169.31 | 159.96
2018-08-19 05:30 | 169.98 | 160.65
2018-08-19 06:00 | 170.58 | 161.46
2018-08-19 06:30 | 171.29 | 162.24
2018-08-19 07:00 | 174.05 | 164.9
2018-08-19 07:30 | 173.78 | 164.78
2018-08-19 08:00 | 175.21 | 166.55
2018-08-19 08:30 | 173.66 | 164.67
2018-08-19 09:00 | 172.68 | 163.77
2018-08-19 09:30 | 170.39 | 161.62
2018-08-19 10:00 | 169.8 | 160.84
2018-08-19 10:30 | 166.15 | 157.53
2018-08-19 11:00 | 161.17 | 153.46
2018-08-19 11:30 | 163.3 | 154.99
2018-08-19 12:00 | 166.01 | 157.59
2018-08-19 12:30 | 166.1 | 157.4
2018-08-19 13:00 | 166.03 | 157.67
2018-08-19 13:30 | 171.4 | 163.28
2018-08-19 14:00 | 197.87 | 189.84
2018-08-19 14:30 | 202.3 | 193.09
2018-08-19 15:00 | 204.49 | 194.36
2018-08-19 15:30 | 204.14 | 193.95
2018-08-19 16:00 | 204.46 | 194.56
2018-08-19 16:30 | 205.56 | 195.62
2018-08-19 17:00 | 207.94 | 199.31
2018-08-19 17:30 | 210.88 | 202.09
2018-08-19 18:00 | 215.18 | 206.17
2018-08-19 18:30 | 220.43 | 210.82
2018-08-19 19:00 | 222.31 | 212.72
2018-08-19 19:30 | 222.01 | 212.4
2018-08-19 20:00 | 220.48 | 210.91
2018-08-19 20:30 | 219.67 | 210.16
2018-08-19 21:00 | 218.24 | 208.87
2018-08-19 21:30 | 217.21 | 207.43
2018-08-19 22:00 | 215.92 | 205.75
2018-08-19 22:30 | 211.84 | 202.54
2018-08-19 23:00 | 209.06 | 200.46
2018-08-19 23:30 | 208.22 | 199.53
2018-08-20 | 206.8 | 198.32
2018-08-20 00:30 | 205.56 | 197.52
2018-08-20 01:00 | 204.78 | 196.51
2018-08-20 01:30 | 202.91 | 196.12
2018-08-20 02:00 | 201.53 | 195.04
2018-08-20 02:30 | 202.25 | 195.6
2018-08-20 03:00 | 202.48 | 195.93
2018-08-20 03:30 | 202.38 | 195.9
2018-08-20 04:00 | 202.97 | 196.35
2018-08-20 04:30 | 203.83 | 197.17
2018-08-20 05:00 | 205.57 | 198.73
2018-08-20 05:30 | 208.77 | 201.68
2018-08-20 06:00 | 211.7 | 204.78
2018-08-20 06:30 | 220.43 | 214.46
2018-08-20 07:00 | 229.16 | 223.33
2018-08-20 07:30 | 236.59 | 231.25
2018-08-20 08:00 | 247.49 | 241.57
2018-08-20 08:30 | 243.79 | 237.12
2018-08-20 09:00 | 242.1 | 235.05
2018-08-20 09:30 | 239.37 | 232.17
2018-08-20 10:00 | 238.27 | 230.82
2018-08-20 10:30 | 238.52 | 231.06
2018-08-20 11:00 | 223.16 | 215.58
2018-08-20 11:30 | 214.16 | 206.16
2018-08-20 12:00 | 207.9 | 199.41
2018-08-20 12:30 | 204.91 | 195.55
2018-08-20 13:00 | 204.39 | 194.62
2018-08-20 13:30 | 204.19 | 193.95
2018-08-20 14:00 | 204.43 | 194.25
2018-08-20 14:30 | 204.62 | 194.45
2018-08-20 15:00 | 204.44 | 193.99
2018-08-20 15:30 | 205.12 | 194.66
2018-08-20 16:00 | 205.71 | 195.61
2018-08-20 16:30 | 207.19 | 197.29
2018-08-20 17:00 | 209.62 | 200.1
2018-08-20 17:30 | 213.18 | 203.79
2018-08-20 18:00 | 218.38 | 209.62
2018-08-20 18:30 | 224.15 | 215.33
2018-08-20 19:00 | 228.08 | 219.21
2018-08-20 19:30 | 228.35 | 219.2
2018-08-20 20:00 | 226.57 | 217.36
2018-08-20 20:30 | 226.59 | 217.37
2018-08-20 21:00 | 224.31 | 214.81
2018-08-20 21:30 | 222.12 | 212.81
2018-08-20 22:00 | 219.71 | 209.94
2018-08-20 22:30 | 217.59 | 207.7
2018-08-20 23:00 | 214.97 | 204.97
2018-08-20 23:30 | 213.28 | 203.3
2018-08-21 | 211.44 | 201.55
2018-08-21 00:30 | 209.81 | 201.12
2018-08-21 01:00 | 209.19 | 200.84
2018-08-21 01:30 | 207.31 | 199.48
2018-08-21 02:00 | 207.88 | 200.08
2018-08-21 02:30 | 208.22 | 200.12
2018-08-21 03:00 | 207.97 | 199.76
2018-08-21 03:30 | 207.76 | 200.38
2018-08-21 04:00 | 208.42 | 201.33
2018-08-21 04:30 | 209.79 | 202.85
2018-08-21 05:00 | 211.53 | 204.68
2018-08-21 05:30 | 216.13 | 207.76
2018-08-21 06:00 | 219.97 | 211.76
2018-08-21 06:30 | 226.49 | 218.73
2018-08-21 07:00 | 232.14 | 224.53
2018-08-21 07:30 | 218.99 | 213.83
2018-08-21 08:00 | 219.4 | 214.9
2018-08-21 08:30 | 225.49 | 221.39
2018-08-21 09:00 | 221 | 213.94
2018-08-21 09:30 | 218.36 | 209.66
2018-08-21 10:00 | 214.99 | 205.95
2018-08-21 10:30 | 211.24 | 202.11
2018-08-21 11:00 | 207.88 | 199.95
2018-08-21 11:30 | 210.52 | 202.48
2018-08-21 12:00 | 209.54 | 201.76
2018-08-21 12:30 | 209.04 | 200.65
2018-08-21 13:00 | 209.18 | 200.49
2018-08-21 13:30 | 207.83 | 199.15
2018-08-21 14:00 | 207.55 | 199.41
2018-08-21 14:30 | 206.76 | 198.65
2018-08-21 15:00 | 206.9 | 198.9
2018-08-21 15:30 | 207.44 | 199.64
2018-08-21 16:00 | 193.04 | 184.57
2018-08-21 16:30 | 185.33 | 176.85
2018-08-21 17:00 | 195.94 | 187.96
2018-08-21 17:30 | 219.86 | 212.84
2018-08-21 18:00 | 206.51 | 201
2018-08-21 18:30 | 202.22 | 196.47
2018-08-21 19:00 | 190.81 | 187.3
2018-08-21 19:30 | 174.01 | 171.15
2018-08-21 20:00 | 175.61 | 173.23
2018-08-21 20:30 | 176.18 | 173.83
2018-08-21 21:00 | 176 | 173.62
2018-08-21 21:30 | 176.03 | 170.02
2018-08-21 22:00 | 177.34 | 170.25
2018-08-21 22:30 | 176.08 | 168.49
2018-08-21 23:00 | 173.81 | 166
2018-08-21 23:30 | 170.94 | 163.81
2018-08-22 | 170.42 | 163.79
2018-08-22 00:30 | 169.65 | 162.56
2018-08-22 01:00 | 169.32 | 162.17
2018-08-22 01:30 | 166.8 | 160.23
2018-08-22 02:00 | 167.44 | 160.88
2018-08-22 02:30 | 168.44 | 161.39
2018-08-22 03:00 | 166.95 | 160.86
2018-08-22 03:30 | 167.07 | 161.92
2018-08-22 04:00 | 164.78 | 159.73
2018-08-22 04:30 | 196.62 | 191.75
2018-08-22 05:00 | 210.04 | 205.28
2018-08-22 05:30 | 211.84 | 207.47
2018-08-22 06:00 | 216.38 | 212.27
2018-08-22 06:30 | 199.5 | 196.43
2018-08-22 07:00 | 176.47 | 173.38
2018-08-22 07:30 | 193.24 | 191.57
2018-08-22 08:00 | 207.7 | 206.83
2018-08-22 08:30 | 201.89 | 200.98
2018-08-22 09:00 | 175.4 | 172.06
2018-08-22 09:30 | 173.14 | 168.77
2018-08-22 10:00 | 167.17 | 162.75
2018-08-22 10:30 | 160.37 | 154.87
2018-08-22 11:00 | 158.79 | 153.31
2018-08-22 11:30 | 157.97 | 151.71
2018-08-22 12:00 | 156.37 | 150.1
2018-08-22 12:30 | 154.66 | 148.41
2018-08-22 13:00 | 156.58 | 150.51
2018-08-22 13:30 | 162.55 | 156.7
2018-08-22 14:00 | 160.47 | 154.54
2018-08-22 14:30 | 156.13 | 149.99
2018-08-22 15:00 | 156.56 | 150.32
2018-08-22 15:30 | 157.76 | 151.47
2018-08-22 16:00 | 162.11 | 155.81
2018-08-22 16:30 | 168.73 | 162.69
2018-08-22 17:00 | 172.52 | 166.53
2018-08-22 17:30 | 199.47 | 192.99
2018-08-22 18:00 | 206.86 | 202.27
2018-08-22 18:30 | 228.7 | 226.4
2018-08-22 19:00 | 231.37 | 228.71
2018-08-22 19:30 | 201.07 | 198.47
2018-08-22 20:00 | 178.23 | 175.67
2018-08-22 20:30 | 178.7 | 176.25
2018-08-22 21:00 | 179.3 | 176.86
2018-08-22 21:30 | 179.41 | 177.24
2018-08-22 22:00 | 179.44 | 177.44
2018-08-22 22:30 | 181.45 | 179.42
2018-08-22 23:00 | 172.37 | 165.02
2018-08-22 23:30 | 173.04 | 164.49
2018-08-23 | 170.03 | 162.73
2018-08-23 00:30 | 169.54 | 162.64
2018-08-23 01:00 | 169.21 | 162.5
2018-08-23 01:30 | 168.04 | 161.46
2018-08-23 02:00 | 168.63 | 162.09
2018-08-23 02:30 | 167.85 | 161.23
2018-08-23 03:00 | 168.85 | 161.88
2018-08-23 03:30 | 168.01 | 161.04
2018-08-23 04:00 | 170.04 | 163.17
2018-08-23 04:30 | 170.48 | 163.41
2018-08-23 05:00 | 172.09 | 165.18
2018-08-23 05:30 | 174.95 | 168.38
2018-08-23 06:00 | 179.56 | 172.86
2018-08-23 06:30 | 194.99 | 188.03
2018-08-23 07:00 | 244.5 | 238.83
2018-08-23 07:30 | 253.6 | 248.53
2018-08-23 08:00 | 251.56 | 245.72
2018-08-23 08:30 | 239.74 | 233.4
2018-08-23 09:00 | 208.64 | 201.39
2018-08-23 09:30 | 204.11 | 196.42
2018-08-23 10:00 | 201.48 | 193.4
2018-08-23 10:30 | 198.38 | 190.22
2018-08-23 11:00 | 177.33 | 168.58
2018-08-23 11:30 | 171.3 | 164.05
2018-08-23 12:00 | 177.24 | 170.01
2018-08-23 12:30 | 190.45 | 183.06
2018-08-23 13:00 | 189.99 | 182.4
2018-08-23 13:30 | 189.92 | 182.17
2018-08-23 14:00 | 169.85 | 161.92
2018-08-23 14:30 | 156.34 | 148.23
2018-08-23 15:00 | 159.2 | 150.9
2018-08-23 15:30 | 199.7 | 191.94
2018-08-23 16:00 | 207.24 | 199.63
2018-08-23 16:30 | 210.71 | 203.7
2018-08-23 17:00 | 212.21 | 205.22
2018-08-23 17:30 | 217.12 | 212.76
2018-08-23 18:00 | 193.99 | 192.41
2018-08-23 18:30 | 179.42 | 177.81
2018-08-23 19:00 | 177.56 | 175.83
2018-08-23 19:30 | 178.16 | 176.47
2018-08-23 20:00 | 179.83 | 178.09
2018-08-23 20:30 | 179.81 | 178.2
2018-08-23 21:00 | 179.79 | 178.15
2018-08-23 21:30 | 179.91 | 178.4
2018-08-23 22:00 | 173.67 | 169.2
2018-08-23 22:30 | 171.16 | 163.95
2018-08-23 23:00 | 173.22 | 167.38
2018-08-23 23:30 | 202.49 | 197.12
2018-08-24 | 210.67 | 205.24
2018-08-24 00:30 | 210.22 | 204.18
2018-08-24 01:00 | 207.99 | 202.03
2018-08-24 01:30 | 206.54 | 200.67
2018-08-24 02:00 | 204.74 | 198.44
2018-08-24 02:30 | 204.05 | 197.25
2018-08-24 03:00 | 205.24 | 198.63
2018-08-24 03:30 | 205.32 | 198.76
2018-08-24 04:00 | 206.16 | 199.45
2018-08-24 04:30 | 206.86 | 200.03
2018-08-24 05:00 | 208.2 | 201.91
2018-08-24 05:30 | 209.84 | 203.32
2018-08-24 06:00 | 212.94 | 206.13
2018-08-24 06:30 | 222.08 | 216.4
2018-08-24 07:00 | 250.32 | 247.11
2018-08-24 07:30 | 249.14 | 245.77
2018-08-24 08:00 | 249.89 | 246.72
2018-08-24 08:30 | 247 | 243.83
2018-08-24 09:00 | 236.74 | 233.66
2018-08-24 09:30 | 221.87 | 218.79
2018-08-24 10:00 | 230.76 | 223.8
2018-08-24 10:30 | 231.14 | 222.02
2018-08-24 11:00 | 228.9 | 219.69
2018-08-24 11:30 | 231.52 | 221.84
2018-08-24 12:00 | 230.57 | 220.69
2018-08-24 12:30 | 229.09 | 218.84
2018-08-24 13:00 | 229.8 | 219.44
2018-08-24 13:30 | 227.3 | 217.11
2018-08-24 14:00 | 227.57 | 217.13
2018-08-24 14:30 | 224.13 | 213.95
2018-08-24 15:00 | 193.35 | 188.7
2018-08-24 15:30 | 194.06 | 189.46
2018-08-24 16:00 | 195.31 | 190.77
2018-08-24 16:30 | 197.08 | 192.5
2018-08-24 17:00 | 195.92 | 191.7
2018-08-24 17:30 | 191.93 | 189.38
2018-08-24 18:00 | 215.8 | 214.56
2018-08-24 18:30 | 214.89 | 213.62
2018-08-24 19:00 | 214.72 | 213.45
2018-08-24 19:30 | 215.52 | 214.29
2018-08-24 20:00 | 216.56 | 215.4
2018-08-24 20:30 | 216.53 | 215.41
2018-08-24 21:00 | 216.26 | 215.18
2018-08-24 21:30 | 200.77 | 197.05
2018-08-24 22:00 | 199.25 | 194.65
2018-08-24 22:30 | 197.54 | 192.89
2018-08-24 23:00 | 196.55 | 191.86
2018-08-24 23:30 | 195.74 | 191.07
2018-08-25 | 194.27 | 189.57
2018-08-25 00:30 | 193.77 | 188.99
2018-08-25 01:00 | 192.7 | 187.81
2018-08-25 01:30 | 192.03 | 187.15
2018-08-25 02:00 | 191.29 | 186.43
2018-08-25 02:30 | 191.55 | 186.68
2018-08-25 03:00 | 191.5 | 186.59
2018-08-25 03:30 | 191.34 | 186.39
2018-08-25 04:00 | 191.3 | 186.33
2018-08-25 04:30 | 191.01 | 186.13
2018-08-25 05:00 | 191.1 | 186.25
2018-08-25 05:30 | 192.02 | 187.16
2018-08-25 06:00 | 192.76 | 187.92
2018-08-25 06:30 | 193.91 | 189.24
2018-08-25 07:00 | 195.46 | 190.92
2018-08-25 07:30 | 197.23 | 192.77
2018-08-25 08:00 | 198.74 | 194.25
2018-08-25 08:30 | 200.29 | 195.79
2018-08-25 09:00 | 178.42 | 171.54
2018-08-25 09:30 | 178.92 | 169.69
2018-08-25 10:00 | 181.85 | 172.33
2018-08-25 10:30 | 181.59 | 171.67
2018-08-25 11:00 | 180.95 | 171.24
2018-08-25 11:30 | 179.68 | 169.34
2018-08-25 12:00 | 180.27 | 169.77
2018-08-25 12:30 | 179.26 | 167.99
2018-08-25 13:00 | 180.26 | 168.8
2018-08-25 13:30 | 190.2 | 182.98
2018-08-25 14:00 | 197.99 | 192.5
2018-08-25 14:30 | 164.9 | 156.38
2018-08-25 15:00 | 194.75 | 190.25
2018-08-25 15:30 | 198.69 | 195.72
2018-08-25 16:00 | 199.1 | 195.74
2018-08-25 16:30 | 198.85 | 195.38
2018-08-25 17:00 | 197.66 | 194.06
2018-08-25 17:30 | 198.58 | 196.53
2018-08-25 18:00 | 213.51 | 212.42
2018-08-25 18:30 | 212.75 | 211.71
2018-08-25 19:00 | 214.29 | 213.4
2018-08-25 19:30 | 215.12 | 214.28
2018-08-25 20:00 | 215.27 | 214.48
2018-08-25 20:30 | 215.64 | 214.84
2018-08-25 21:00 | 215.93 | 215.13
2018-08-25 21:30 | 217.12 | 216.27
2018-08-25 22:00 | 198.79 | 196.95
2018-08-25 22:30 | 176.17 | 167.11
2018-08-25 23:00 | 184.24 | 173.56
2018-08-25 23:30 | 183.79 | 172.83
2018-08-26 | 182.98 | 171.63
2018-08-26 00:30 | 181.86 | 171.05
2018-08-26 01:00 | 180.77 | 170.46
2018-08-26 01:30 | 180.2 | 169.75
2018-08-26 02:00 | 179.52 | 169.17
2018-08-26 02:30 | 179.09 | 168.77
2018-08-26 03:00 | 178.9 | 168.5
2018-08-26 03:30 | 179.18 | 168.66
2018-08-26 04:00 | 179.23 | 168.75
2018-08-26 04:30 | 179.26 | 168.59
2018-08-26 05:00 | 179.68 | 169.07
2018-08-26 05:30 | 180.31 | 169.73
2018-08-26 06:00 | 180.71 | 170.22
2018-08-26 06:30 | 182.12 | 171.97
2018-08-26 07:00 | 183.41 | 173.52
2018-08-26 07:30 | 184.82 | 175.04
2018-08-26 08:00 | 185.65 | 175.71
2018-08-26 08:30 | 184.49 | 174.73
2018-08-26 09:00 | 183.19 | 173.12
2018-08-26 09:30 | 181.43 | 171.21
2018-08-26 10:00 | 179.77 | 169.11
2018-08-26 10:30 | 176.82 | 165.81
2018-08-26 11:00 | 174.83 | 163.47
2018-08-26 11:30 | 174.3 | 163.01
2018-08-26 12:00 | 173.54 | 162.06
2018-08-26 12:30 | 174.01 | 162.35
2018-08-26 13:00 | 175.71 | 163.75
2018-08-26 13:30 | 175.47 | 163.45
2018-08-26 14:00 | 173.82 | 162.87
2018-08-26 14:30 | 174.24 | 163.16
2018-08-26 15:00 | 174.83 | 163.9
2018-08-26 15:30 | 175.7 | 164.97
2018-08-26 16:00 | 177.12 | 166.53
2018-08-26 16:30 | 179.04 | 168.61
2018-08-26 17:00 | 181.48 | 171.34
2018-08-26 17:30 | 183.98 | 174.19
2018-08-26 18:00 | 187.34 | 177.86
2018-08-26 18:30 | 190.74 | 181.78
2018-08-26 19:00 | 192.17 | 183.62
2018-08-26 19:30 | 191 | 182.33
2018-08-26 20:00 | 189.86 | 180.96
2018-08-26 20:30 | 187.57 | 178.34
2018-08-26 21:00 | 186.58 | 177.41
2018-08-26 21:30 | 171.95 | 163.78
2018-08-26 22:00 | 186.44 | 180.89
2018-08-26 22:30 | 195.62 | 191.16
2018-08-26 23:00 | 193.69 | 189.17
2018-08-26 23:30 | 192.78 | 188.13
2018-08-27 | 191.76 | 186.93
2018-08-27 00:30 | 191.31 | 186.52
2018-08-27 01:00 | 190.01 | 185.22
2018-08-27 01:30 | 189.49 | 184.69
2018-08-27 02:00 | 189.17 | 184.33
2018-08-27 02:30 | 189.19 | 184.35
2018-08-27 03:00 | 189.15 | 184.32
2018-08-27 03:30 | 189.08 | 184.27
2018-08-27 04:00 | 189.72 | 184.74
2018-08-27 04:30 | 190.9 | 185.93
2018-08-27 05:00 | 192.04 | 187.15
2018-08-27 05:30 | 193.9 | 189.14
2018-08-27 06:00 | 196.42 | 191.96
2018-08-27 06:30 | 200.92 | 196.86
2018-08-27 07:00 | 204.6 | 200.66
2018-08-27 07:30 | 206.12 | 202.35
2018-08-27 08:00 | 204.65 | 200.82
2018-08-27 08:30 | 200.72 | 196.82
2018-08-27 09:00 | 197.44 | 193.46
2018-08-27 09:30 | 194.07 | 190.16
2018-08-27 10:00 | 192.61 | 188.57
2018-08-27 10:30 | 190.94 | 186.94
2018-08-27 11:00 | 190.01 | 185.93
2018-08-27 11:30 | 189.82 | 185.63
2018-08-27 12:00 | 189.25 | 185.06
2018-08-27 12:30 | 188.07 | 183.93
2018-08-27 13:00 | 187.97 | 183.73
2018-08-27 13:30 | 187.65 | 183.54
2018-08-27 14:00 | 188.13 | 184.13
2018-08-27 14:30 | 174.19 | 167.84
2018-08-27 15:00 | 166.4 | 156.2
2018-08-27 15:30 | 176.3 | 166.09
2018-08-27 16:00 | 178.27 | 167.68
2018-08-27 16:30 | 179.05 | 168.7
2018-08-27 17:00 | 184.55 | 177.03
2018-08-27 17:30 | 200.02 | 196.93
2018-08-27 18:00 | 197.65 | 194.43
2018-08-27 18:30 | 196 | 192.53
2018-08-27 19:00 | 194.64 | 191.08
2018-08-27 19:30 | 195.46 | 192.05
2018-08-27 20:00 | 182.03 | 179.43
2018-08-27 20:30 | 209.51 | 208.64
2018-08-27 21:00 | 201.44 | 198.25
2018-08-27 21:30 | 202.46 | 198.42
2018-08-27 22:00 | 201.37 | 197.17
2018-08-27 22:30 | 199.21 | 194.89
2018-08-27 23:00 | 197.09 | 192.62
2018-08-27 23:30 | 196.16 | 191.5
2018-08-28 | 194.86 | 190.16
2018-08-28 00:30 | 194.43 | 189.8
2018-08-28 01:00 | 193.51 | 188.83
2018-08-28 01:30 | 192.84 | 188.21
2018-08-28 02:00 | 192.44 | 187.67
2018-08-28 02:30 | 192.11 | 187.25
2018-08-28 03:00 | 192.35 | 187.72
2018-08-28 03:30 | 191.88 | 187.19
2018-08-28 04:00 | 193.19 | 188.66
2018-08-28 04:30 | 194.15 | 189.63
2018-08-28 05:00 | 194.61 | 189.99
2018-08-28 05:30 | 197.46 | 192.9
2018-08-28 06:00 | 200.3 | 196.02
2018-08-28 06:30 | 205.41 | 201.51
2018-08-28 07:00 | 209.19 | 205.45
2018-08-28 07:30 | 211.09 | 207.56
2018-08-28 08:00 | 208.04 | 204.47
2018-08-28 08:30 | 203.04 | 199.31
2018-08-28 09:00 | 199.29 | 195.37
2018-08-28 09:30 | 195.96 | 191.77
2018-08-28 10:00 | 194.36 | 189.93
2018-08-28 10:30 | 193.02 | 188.59
2018-08-28 11:00 | 191.96 | 187.52
2018-08-28 11:30 | 190.64 | 186.26
2018-08-28 12:00 | 189.99 | 185.66
2018-08-28 12:30 | 189.63 | 185.19
2018-08-28 13:00 | 189.38 | 184.87
2018-08-28 13:30 | 189.11 | 184.54
2018-08-28 14:00 | 190.94 | 186.42
2018-08-28 14:30 | 193.96 | 189.25
2018-08-28 15:00 | 194.61 | 189.82
2018-08-28 15:30 | 195.71 | 190.89
2018-08-28 16:00 | 193.88 | 189.35
2018-08-28 16:30 | 194.11 | 189.6
2018-08-28 17:00 | 195.32 | 190.87
2018-08-28 17:30 | 197.58 | 193.14
2018-08-28 18:00 | 200.82 | 196.57
2018-08-28 18:30 | 205.02 | 200.99
2018-08-28 19:00 | 208.04 | 204.13
2018-08-28 19:30 | 207.54 | 203.63
2018-08-28 20:00 | 206.43 | 202.55
2018-08-28 20:30 | 206.09 | 202.21
2018-08-28 21:00 | 204.79 | 200.9
2018-08-28 21:30 | 204 | 200.02
2018-08-28 22:00 | 202.33 | 198.3
2018-08-28 22:30 | 199.87 | 195.83
2018-08-28 23:00 | 197.92 | 193.79
2018-08-28 23:30 | 196.51 | 192.27
2018-08-29 | 195.21 | 190.89
2018-08-29 00:30 | 194.59 | 190.3
2018-08-29 01:00 | 193.7 | 189.29
2018-08-29 01:30 | 193 | 188.46
2018-08-29 02:00 | 192.78 | 188.08
2018-08-29 02:30 | 192.48 | 187.8
2018-08-29 03:00 | 192.44 | 187.74
2018-08-29 03:30 | 192.59 | 187.95
2018-08-29 04:00 | 192.67 | 188.07
2018-08-29 04:30 | 193.65 | 189.1
2018-08-29 05:00 | 195.32 | 190.86
2018-08-29 05:30 | 197.98 | 193.56
2018-08-29 06:00 | 200.23 | 196.27
2018-08-29 06:30 | 180.49 | 177.86
2018-08-29 07:00 | 178.22 | 175.48
2018-08-29 07:30 | 177.8 | 174.9
2018-08-29 08:00 | 179.29 | 176.36
2018-08-29 08:30 | 197.6 | 193.8
2018-08-29 09:00 | 199.7 | 195.55
2018-08-29 09:30 | 196.75 | 192.38
2018-08-29 10:00 | 195.49 | 191.08
2018-08-29 10:30 | 193.67 | 189.26
2018-08-29 11:00 | 192.92 | 188.33
2018-08-29 11:30 | 191.63 | 187.12
2018-08-29 12:00 | 191.23 | 186.6
2018-08-29 12:30 | 190.78 | 186.11
2018-08-29 13:00 | 191.17 | 186.41
2018-08-29 13:30 | 191.33 | 186.55
2018-08-29 14:00 | 183.62 | 178.13
2018-08-29 14:30 | 165.57 | 158.22
2018-08-29 15:00 | 167.04 | 159.5
2018-08-29 15:30 | 167.75 | 160.33
2018-08-29 16:00 | 169.49 | 162.19
2018-08-29 16:30 | 170.63 | 163.44
2018-08-29 17:00 | 172.13 | 165.03
2018-08-29 17:30 | 174.13 | 167.04
2018-08-29 18:00 | 176.42 | 169.74
2018-08-29 18:30 | 180.94 | 178.2
2018-08-29 19:00 | 184.18 | 182.62
2018-08-29 19:30 | 185.18 | 183.53
2018-08-29 20:00 | 185.51 | 183.89
2018-08-29 20:30 | 186.47 | 184.62
2018-08-29 21:00 | 187.29 | 185.45
2018-08-29 21:30 | 187.52 | 185.89
2018-08-29 22:00 | 204.25 | 203.22
2018-08-29 22:30 | 206.91 | 205.97
2018-08-29 23:00 | 195.44 | 191.94
2018-08-29 23:30 | 227.83 | 222.78
2018-08-30 | 230.25 | 225.22
2018-08-30 00:30 | 230.56 | 225.08
2018-08-30 01:00 | 228.69 | 223.18
2018-08-30 01:30 | 228.6 | 223.32
2018-08-30 02:00 | 228.07 | 223.01
2018-08-30 02:30 | 227.71 | 222.75
2018-08-30 03:00 | 227.31 | 222.41
2018-08-30 03:30 | 227.26 | 222.3
2018-08-30 04:00 | 227.69 | 222.73
2018-08-30 04:30 | 228.34 | 223.38
2018-08-30 05:00 | 229.29 | 224.25
2018-08-30 05:30 | 231.27 | 226.46
2018-08-30 06:00 | 232.64 | 228.82
2018-08-30 06:30 | 250.29 | 248.93
2018-08-30 07:00 | 247.94 | 246.47
2018-08-30 07:30 | 246.29 | 244.83
2018-08-30 08:00 | 246.83 | 245.34
2018-08-30 08:30 | 235.15 | 231.41
2018-08-30 09:00 | 230.75 | 225.67
2018-08-30 09:30 | 226.85 | 221.28
2018-08-30 10:00 | 224.87 | 218.61
2018-08-30 10:30 | 222.64 | 216.54
2018-08-30 11:00 | 221.63 | 215.83
2018-08-30 11:30 | 223.39 | 217.68
2018-08-30 12:00 | 223.02 | 217.19
2018-08-30 12:30 | 221.93 | 215.94
2018-08-30 13:00 | 221.57 | 215.67
2018-08-30 13:30 | 221.7 | 215.75
2018-08-30 14:00 | 222 | 216.08
2018-08-30 14:30 | 222.44 | 216.43
2018-08-30 15:00 | 222.95 | 216.99
2018-08-30 15:30 | 223.31 | 217.4
2018-08-30 16:00 | 224.21 | 218.28
2018-08-30 16:30 | 224.93 | 219.17
2018-08-30 17:00 | 226.22 | 220.24
2018-08-30 17:30 | 233.87 | 230.52
2018-08-30 18:00 | 242.99 | 241.08
2018-08-30 18:30 | 241.06 | 239.16
2018-08-30 19:00 | 240.64 | 238.69
2018-08-30 19:30 | 241.64 | 239.74
2018-08-30 20:00 | 242.73 | 241
2018-08-30 20:30 | 244.13 | 242.48
2018-08-30 21:00 | 242.97 | 241.35
2018-08-30 21:30 | 242.33 | 240.73
2018-08-30 22:00 | 230.11 | 225.29
2018-08-30 22:30 | 227.3 | 221.06
2018-08-30 23:00 | 224.95 | 218.62
2018-08-30 23:30 | 223.77 | 217.91
2018-08-31 | 222.61 | 216.86
2018-08-31 00:30 | 222.26 | 216.45
2018-08-31 01:00 | 221.85 | 215.93
2018-08-31 01:30 | 221.4 | 215.36
2018-08-31 02:00 | 220.65 | 214.82
2018-08-31 02:30 | 221.11 | 215.04
2018-08-31 03:00 | 221.28 | 215.07
2018-08-31 03:30 | 221.4 | 215.24
2018-08-31 04:00 | 221.53 | 215.35
2018-08-31 04:30 | 222.33 | 216.1
2018-08-31 05:00 | 223.09 | 216.87
2018-08-31 05:30 | 224.77 | 218.65
2018-08-31 06:00 | 226.99 | 220.95
2018-08-31 06:30 | 230.18 | 224.92
2018-08-31 07:00 | 232.62 | 227.58
2018-08-31 07:30 | 234.11 | 228.93
2018-08-31 08:00 | 231.72 | 226.45
2018-08-31 08:30 | 228.4 | 223.1
2018-08-31 09:00 | 224.51 | 219.14
2018-08-31 09:30 | 223 | 217.27
2018-08-31 10:00 | 221.99 | 216.15
2018-08-31 10:30 | 221.56 | 215.56
2018-08-31 11:00 | 221.64 | 215.76
2018-08-31 11:30 | 221.12 | 215.08
2018-08-31 12:00 | 221.42 | 215.36
2018-08-31 12:30 | 221.62 | 215.27
2018-08-31 13:00 | 221.75 | 215.5
2018-08-31 13:30 | 222.55 | 216.38
2018-08-31 14:00 | 223.32 | 216.99
2018-08-31 14:30 | 223.43 | 217.18
2018-08-31 15:00 | 223.79 | 217.72
2018-08-31 15:30 | 224.27 | 217.97
2018-08-31 16:00 | 225.78 | 219.39
2018-08-31 16:30 | 226.42 | 220.32
2018-08-31 17:00 | 231.31 | 227.39
2018-08-31 17:30 | 216.75 | 215.1
2018-08-31 18:00 | 163.1 | 162.22
2018-08-31 18:30 | 161.19 | 160.44
2018-08-31 19:00 | 160.34 | 159.63
2018-08-31 19:30 | 161.41 | 160.67
2018-08-31 20:00 | 161.9 | 161.15
2018-08-31 20:30 | 162.03 | 161.27
2018-08-31 21:00 | 163.12 | 162.37
2018-08-31 21:30 | 146.27 | 142.78
2018-08-31 22:00 | 144.59 | 139.81
2018-08-31 22:30 | 143.1 | 138.24
2018-08-31 23:00 | 142.02 | 137.13
2018-08-31 23:30 | 141.3 | 136.37
2018-09-01 | 139.93 | 134.82
2018-09-01 00:30 | 139.67 | 134.52
2018-09-01 01:00 | 139.03 | 133.82
2018-09-01 01:30 | 138.56 | 133.48
2018-09-01 02:00 | 138.6 | 133.49
2018-09-01 02:30 | 138.65 | 133.61
2018-09-01 03:00 | 138.53 | 133.51
2018-09-01 03:30 | 138.44 | 133.45
2018-09-01 04:00 | 138.52 | 133.45
2018-09-01 04:30 | 138.48 | 133.39
2018-09-01 05:00 | 138.74 | 133.66
2018-09-01 05:30 | 139.56 | 134.47
2018-09-01 06:00 | 140.95 | 135.9
2018-09-01 06:30 | 142.86 | 137.91
2018-09-01 07:00 | 144.04 | 139.27
2018-09-01 07:30 | 143.79 | 139.12
2018-09-01 08:00 | 142.91 | 138.28
2018-09-01 08:30 | 141.17 | 136.58
2018-09-01 09:00 | 139.4 | 134.81
2018-09-01 09:30 | 137.23 | 132.75
2018-09-01 10:00 | 135.83 | 131.41
2018-09-01 10:30 | 134.16 | 129.77
2018-09-01 11:00 | 132.97 | 128.59
2018-09-01 11:30 | 133.08 | 128.43
2018-09-01 12:00 | 132.76 | 128.17
2018-09-01 12:30 | 132.23 | 127.67
2018-09-01 13:00 | 132 | 127.37
2018-09-01 13:30 | 131.34 | 126.64
2018-09-01 14:00 | 132.1 | 127.45
2018-09-01 14:30 | 131.43 | 126.82
2018-09-01 15:00 | 131.86 | 127.27
2018-09-01 15:30 | 132.55 | 128
2018-09-01 16:00 | 134.89 | 130.27
2018-09-01 16:30 | 138.81 | 132.93
2018-09-01 17:00 | 140.67 | 135.45
2018-09-01 17:30 | 143.63 | 138.31
2018-09-01 18:00 | 149.21 | 145.75
2018-09-01 18:30 | 160.65 | 159.59
2018-09-01 19:00 | 160.39 | 159.31
2018-09-01 19:30 | 161.38 | 160.34
2018-09-01 20:00 | 162.43 | 161.4
2018-09-01 20:30 | 162.74 | 161.7
2018-09-01 21:00 | 163.24 | 162.18
2018-09-01 21:30 | 163.79 | 162.69
2018-09-01 22:00 | 164.64 | 163.53
2018-09-01 22:30 | 145.75 | 140.94
2018-09-01 23:00 | 142.25 | 135.68
2018-09-01 23:30 | 142.38 | 135.79
2018-09-02 | 141.59 | 134.91
2018-09-02 00:30 | 140.84 | 134.19
2018-09-02 01:00 | 140.06 | 133.41
2018-09-02 01:30 | 139.8 | 133.19
2018-09-02 02:00 | 139.89 | 133.32
2018-09-02 02:30 | 139.63 | 133.08
2018-09-02 03:00 | 139.31 | 132.75
2018-09-02 03:30 | 139.11 | 132.53
2018-09-02 04:00 | 139.29 | 132.69
2018-09-02 04:30 | 139.63 | 133.03
2018-09-02 05:00 | 140.14 | 133.59
2018-09-02 05:30 | 140.96 | 134.42
2018-09-02 06:00 | 141.69 | 135.18
2018-09-02 06:30 | 143.01 | 136.61
2018-09-02 07:00 | 144.49 | 138.14
2018-09-02 07:30 | 145.12 | 138.91
2018-09-02 08:00 | 143.9 | 137.9
2018-09-02 08:30 | 143.14 | 137.15
2018-09-02 09:00 | 141.19 | 135.07
2018-09-02 09:30 | 139.61 | 133.4
2018-09-02 10:00 | 139.6 | 133.31
2018-09-02 10:30 | 138.07 | 131.69
2018-09-02 11:00 | 137.01 | 130.63
2018-09-02 11:30 | 136.71 | 130.41
2018-09-02 12:00 | 137.72 | 131.48
2018-09-02 12:30 | 138.79 | 132.83
2018-09-02 13:00 | 141.12 | 135.97
2018-09-02 13:30 | 143.09 | 138.32
2018-09-02 14:00 | 143.89 | 139.22
2018-09-02 14:30 | 149.27 | 140.29
2018-09-02 15:00 | 148.79 | 139.4
2018-09-02 15:30 | 148.09 | 140.96
2018-09-02 16:00 | 153.51 | 148.08
2018-09-02 16:30 | 157.84 | 152.87
2018-09-02 17:00 | 160.28 | 155.85
2018-09-02 17:30 | 163.74 | 160.16
2018-09-02 18:00 | 189.64 | 188.91
2018-09-02 18:30 | 190.05 | 189.06
2018-09-02 19:00 | 189.89 | 188.9
2018-09-02 19:30 | 190.57 | 189.7
2018-09-02 20:00 | 191.66 | 190.81
2018-09-02 20:30 | 194.46 | 193.5
2018-09-02 21:00 | 196.81 | 195.82
2018-09-02 21:30 | 198.9 | 197.68
2018-09-02 22:00 | 199.37 | 198.25
2018-09-02 22:30 | 179.56 | 175.45
2018-09-02 23:00 | 176.27 | 170.82
2018-09-02 23:30 | 176.42 | 170.76
2018-09-03 | 174.88 | 169.21
2018-09-03 00:30 | 174.26 | 168.69
2018-09-03 01:00 | 173.15 | 167.54
2018-09-03 01:30 | 172 | 166.53
2018-09-03 02:00 | 171.68 | 166.18
2018-09-03 02:30 | 171.55 | 165.93
2018-09-03 03:00 | 171.31 | 165.63
2018-09-03 03:30 | 171.55 | 165.88
2018-09-03 04:00 | 171.74 | 166.13
2018-09-03 04:30 | 172.55 | 166.97
2018-09-03 05:00 | 173.86 | 168.33
2018-09-03 05:30 | 175.27 | 169.88
2018-09-03 06:00 | 177.73 | 172.69
2018-09-03 06:30 | 181.5 | 176.96
2018-09-03 07:00 | 185.74 | 181.16
2018-09-03 07:30 | 182.49 | 178.33
2018-09-03 08:00 | 167.13 | 164.18
2018-09-03 08:30 | 168.2 | 165.56
2018-09-03 09:00 | 170.61 | 167.92
2018-09-03 09:30 | 174.89 | 170.43
2018-09-03 10:00 | 178.33 | 173.19
2018-09-03 10:30 | 179.17 | 173.82
2018-09-03 11:00 | 180.96 | 175.35
2018-09-03 11:30 | 182.06 | 177.34
2018-09-03 12:00 | 181.94 | 178.39
2018-09-03 12:30 | 182.02 | 178.41
2018-09-03 13:00 | 184.44 | 180.55
2018-09-03 13:30 | 186.28 | 182.18
2018-09-03 14:00 | 186.95 | 182.87
2018-09-03 14:30 | 188.7 | 184.59
2018-09-03 15:00 | 190.45 | 186.22
2018-09-03 15:30 | 190.7 | 186.5
2018-09-03 16:00 | 191.93 | 187.78
2018-09-03 16:30 | 193.2 | 188.88
2018-09-03 17:00 | 194.4 | 190.16
2018-09-03 17:30 | 209.15 | 208.16
2018-09-03 18:00 | 210.42 | 209.58
2018-09-03 18:30 | 208.65 | 207.82
2018-09-03 19:00 | 207.26 | 206.43
2018-09-03 19:30 | 208.26 | 207.44
2018-09-03 20:00 | 210.07 | 209.32
2018-09-03 20:30 | 210 | 209.23
2018-09-03 21:00 | 196.49 | 193.32
2018-09-03 21:30 | 195.56 | 191.48
2018-09-03 22:00 | 194.56 | 190.38
2018-09-03 22:30 | 192.29 | 188.06
2018-09-03 23:00 | 190.19 | 185.95
2018-09-03 23:30 | 189.37 | 185.09
2018-09-04 | 187.67 | 183.34
2018-09-04 00:30 | 186.85 | 182.59
2018-09-04 01:00 | 186.1 | 181.91
2018-09-04 01:30 | 185.67 | 181.49
2018-09-04 02:00 | 184.84 | 180.72
2018-09-04 02:30 | 184.24 | 180.05
2018-09-04 03:00 | 183.99 | 179.81
2018-09-04 03:30 | 184.03 | 179.85
2018-09-04 04:00 | 184.46 | 180.23
2018-09-04 04:30 | 185.24 | 180.95
2018-09-04 05:00 | 186.04 | 181.68
2018-09-04 05:30 | 187.93 | 183.59
2018-09-04 06:00 | 190.56 | 186.37
2018-09-04 06:30 | 193.81 | 189.82
2018-09-04 07:00 | 197.24 | 193.21
2018-09-04 07:30 | 201.98 | 197.75
2018-09-04 08:00 | 201.8 | 197.44
2018-09-04 08:30 | 200.2 | 195.93
2018-09-04 09:00 | 197.68 | 193.35
2018-09-04 09:30 | 195.72 | 191.43
2018-09-04 10:00 | 189.21 | 185.57
2018-09-04 10:30 | 188.9 | 185.27
2018-09-04 11:00 | 188.68 | 185.12
2018-09-04 11:30 | 191.29 | 187.45
2018-09-04 12:00 | 190.21 | 186.43
2018-09-04 12:30 | 188.68 | 185.05
2018-09-04 13:00 | 191.26 | 187.31
2018-09-04 13:30 | 192.78 | 188.61
2018-09-04 14:00 | 194.46 | 190.34
2018-09-04 14:30 | 195.27 | 191.17
2018-09-04 15:00 | 198.07 | 193.72
2018-09-04 15:30 | 200.46 | 195.83
2018-09-04 16:00 | 200.61 | 196.13
2018-09-04 16:30 | 196.9 | 192.91
2018-09-04 17:00 | 211.07 | 209.72
2018-09-04 17:30 | 216.09 | 215.19
2018-09-04 18:00 | 213.36 | 212.45
2018-09-04 18:30 | 211.21 | 210.3
2018-09-04 19:00 | 209.55 | 208.64
2018-09-04 19:30 | 210.25 | 209.43
2018-09-04 20:00 | 211.85 | 211.05
2018-09-04 20:30 | 212.45 | 211.63
2018-09-04 21:00 | 214.06 | 213.22
2018-09-04 21:30 | 215.15 | 214.2
2018-09-04 22:00 | 201.66 | 198.24
2018-09-04 22:30 | 198.76 | 194.37
2018-09-04 23:00 | 196.29 | 191.84
2018-09-04 23:30 | 194.79 | 190.22
2018-09-05 | 193.98 | 189.34
2018-09-05 00:30 | 193.18 | 188.54
2018-09-05 01:00 | 191.36 | 186.78
2018-09-05 01:30 | 190.49 | 185.99
2018-09-05 02:00 | 190.24 | 185.75
2018-09-05 02:30 | 189.79 | 185.24
2018-09-05 03:00 | 189.84 | 185.27
2018-09-05 03:30 | 190.05 | 185.21
2018-09-05 04:00 | 189.59 | 184.64
2018-09-05 04:30 | 190.92 | 186.11
2018-09-05 05:00 | 192.07 | 187.29
2018-09-05 05:30 | 193.93 | 189.24
2018-09-05 06:00 | 195.69 | 191.32
2018-09-05 06:30 | 199.55 | 195.22
2018-09-05 07:00 | 203.94 | 201.16
2018-09-05 07:30 | 215.21 | 214.12
2018-09-05 08:00 | 215.12 | 214.02
2018-09-05 08:30 | 216.35 | 215.22
2018-09-05 09:00 | 197.3 | 193.97
2018-09-05 09:30 | 191.11 | 186.85
2018-09-05 10:00 | 188.66 | 184.43
2018-09-05 10:30 | 185.93 | 181.88
2018-09-05 11:00 | 179.52 | 175.82
2018-09-05 11:30 | 179.29 | 175.59
2018-09-05 12:00 | 181.53 | 177.65
2018-09-05 12:30 | 181.49 | 177.56
2018-09-05 13:00 | 181.25 | 177.33
2018-09-05 13:30 | 181.21 | 177.25
2018-09-05 14:00 | 181.29 | 177.52
2018-09-05 14:30 | 179.06 | 175.86
2018-09-05 15:00 | 178.24 | 175.04
2018-09-05 15:30 | 180.02 | 176.59
2018-09-05 16:00 | 182.36 | 178.88
2018-09-05 16:30 | 198.98 | 198.07
2018-09-05 17:00 | 204.51 | 203.87
2018-09-05 17:30 | 205.16 | 204.39
2018-09-05 18:00 | 204.73 | 203.87
2018-09-05 18:30 | 203.19 | 202.21
2018-09-05 19:00 | 202.09 | 201.11
2018-09-05 19:30 | 204.02 | 203.03
2018-09-05 20:00 | 205.45 | 204.56
2018-09-05 20:30 | 205.05 | 204.25
2018-09-05 21:00 | 206.25 | 205.45
2018-09-05 21:30 | 206.39 | 205.38
2018-09-05 22:00 | 206.31 | 205.48
2018-09-05 22:30 | 206.43 | 205.67
2018-09-05 23:00 | 185.33 | 182.04
2018-09-05 23:30 | 181.28 | 177.11
2018-09-06 | 179.71 | 175.51
2018-09-06 00:30 | 179.32 | 175.09
2018-09-06 01:00 | 178.85 | 174.53
2018-09-06 01:30 | 178.46 | 174.2
2018-09-06 02:00 | 177.6 | 173.36
2018-09-06 02:30 | 176.93 | 172.67
2018-09-06 03:00 | 176.27 | 172.01
2018-09-06 03:30 | 175.6 | 171.34
2018-09-06 04:00 | 176 | 171.75
2018-09-06 04:30 | 176.46 | 172.29
2018-09-06 05:00 | 177.63 | 173.37
2018-09-06 05:30 | 178.93 | 174.83
2018-09-06 06:00 | 183.33 | 179.35
2018-09-06 06:30 | 189.71 | 185.65
2018-09-06 07:00 | 195.76 | 192.98
2018-09-06 07:30 | 205.45 | 204.4
2018-09-06 08:00 | 199.34 | 198.52
2018-09-06 08:30 | 200.65 | 199.75
2018-09-06 09:00 | 201.7 | 200.75
2018-09-06 09:30 | 178.63 | 176.02
2018-09-06 10:00 | 173.52 | 169.86
2018-09-06 10:30 | 172.29 | 168.55
2018-09-06 11:00 | 171.1 | 167.44
2018-09-06 11:30 | 168.08 | 164.68
2018-09-06 12:00 | 168.47 | 165.04
2018-09-06 12:30 | 168.61 | 165.2
2018-09-06 13:00 | 171.32 | 167.53
2018-09-06 13:30 | 174.15 | 170.06
2018-09-06 14:00 | 176.01 | 172.06
2018-09-06 14:30 | 176.97 | 173.06
2018-09-06 15:00 | 177.74 | 173.87
2018-09-06 15:30 | 179.4 | 175.66
2018-09-06 16:00 | 190.7 | 189.62
2018-09-06 16:30 | 200.88 | 200.16
2018-09-06 17:00 | 200.06 | 199.35
2018-09-06 17:30 | 199.15 | 198.5
2018-09-06 18:00 | 197.96 | 197.28
2018-09-06 18:30 | 196.81 | 196.19
2018-09-06 19:00 | 196.28 | 195.66
2018-09-06 19:30 | 197.35 | 196.76
2018-09-06 20:00 | 198.84 | 198.26
2018-09-06 20:30 | 199.32 | 198.76
2018-09-06 21:00 | 200.46 | 199.88
2018-09-06 21:30 | 200.14 | 199.58
2018-09-06 22:00 | 183.36 | 180.28
2018-09-06 22:30 | 180.54 | 176.43
2018-09-06 23:00 | 178.84 | 174.7
2018-09-06 23:30 | 178.06 | 173.82
2018-09-07 | 176.94 | 172.53
2018-09-07 00:30 | 176.41 | 172.03
2018-09-07 01:00 | 175.28 | 170.86
2018-09-07 01:30 | 174.46 | 170.35
2018-09-07 02:00 | 173.77 | 169.65
2018-09-07 02:30 | 173.58 | 169.22
2018-09-07 03:00 | 173.18 | 168.8
2018-09-07 03:30 | 172.94 | 168.57
2018-09-07 04:00 | 172.92 | 168.56
2018-09-07 04:30 | 173.46 | 169.16
2018-09-07 05:00 | 173.76 | 169.52
2018-09-07 05:30 | 175.1 | 170.9
2018-09-07 06:00 | 176.73 | 172.61
2018-09-07 06:30 | 179.22 | 175.38
2018-09-07 07:00 | 181.09 | 177.43
2018-09-07 07:30 | 182.04 | 178.52
2018-09-07 08:00 | 181.32 | 177.83
2018-09-07 08:30 | 179.72 | 176.25
2018-09-07 09:00 | 177.85 | 174.24
2018-09-07 09:30 | 176.39 | 172.69
2018-09-07 10:00 | 175.46 | 171.82
2018-09-07 10:30 | 175.16 | 171.47
2018-09-07 11:00 | 175.6 | 172.01
2018-09-07 11:30 | 175.58 | 172.02
2018-09-07 12:00 | 175.43 | 171.73
2018-09-07 12:30 | 174.88 | 171.14
2018-09-07 13:00 | 175.76 | 172.06
2018-09-07 13:30 | 177.06 | 173.34
2018-09-07 14:00 | 176.2 | 172.55
2018-09-07 14:30 | 177.14 | 173.48
2018-09-07 15:00 | 177.44 | 173.65
2018-09-07 15:30 | 178.03 | 174.25
2018-09-07 16:00 | 179.41 | 175.78
2018-09-07 16:30 | 180.96 | 177.23
2018-09-07 17:00 | 175.49 | 172.48
2018-09-07 17:30 | 196.62 | 195.76
2018-09-07 18:00 | 197.5 | 196.07
2018-09-07 18:30 | 197.23 | 195.59
2018-09-07 19:00 | 196.44 | 194.78
2018-09-07 19:30 | 197.01 | 195.41
2018-09-07 20:00 | 198.04 | 196.47
2018-09-07 20:30 | 198.65 | 197.03
2018-09-07 21:00 | 183.16 | 179.59
2018-09-07 21:30 | 182.13 | 178.14
2018-09-07 22:00 | 181.02 | 176.94
2018-09-07 22:30 | 179.42 | 175.35
2018-09-07 23:00 | 178.08 | 173.93
2018-09-07 23:30 | 177.22 | 173.04
2018-09-08 | 176.04 | 171.79
2018-09-08 00:30 | 175.8 | 171.49
2018-09-08 01:00 | 174.74 | 170.38
2018-09-08 01:30 | 174.03 | 169.66
2018-09-08 02:00 | 173.31 | 168.93
2018-09-08 02:30 | 172.97 | 168.58
2018-09-08 03:00 | 172.41 | 168.04
2018-09-08 03:30 | 172.24 | 167.86
2018-09-08 04:00 | 172.17 | 167.8
2018-09-08 04:30 | 172.2 | 167.85
2018-09-08 05:00 | 172.34 | 168.02
2018-09-08 05:30 | 172.87 | 168.55
2018-09-08 06:00 | 173.74 | 169.45
2018-09-08 06:30 | 174.96 | 170.76
2018-09-08 07:00 | 175.3 | 171.15
2018-09-08 07:30 | 176.28 | 172.17
2018-09-08 08:00 | 175.79 | 171.82
2018-09-08 08:30 | 174.98 | 171.04
2018-09-08 09:00 | 173.81 | 169.71
2018-09-08 09:30 | 173.08 | 168.98
2018-09-08 10:00 | 172.73 | 168.7
2018-09-08 10:30 | 171.77 | 167.87
2018-09-08 11:00 | 170.27 | 166.38
2018-09-08 11:30 | 169.75 | 165.88
2018-09-08 12:00 | 169.4 | 165.51
2018-09-08 12:30 | 169.14 | 165.28
2018-09-08 13:00 | 169.31 | 165.38
2018-09-08 13:30 | 169.16 | 165.2
2018-09-08 14:00 | 169.75 | 165.81
2018-09-08 14:30 | 170 | 166.06
2018-09-08 15:00 | 170.88 | 166.91
2018-09-08 15:30 | 172.56 | 168.62
2018-09-08 16:00 | 174.22 | 170.27
2018-09-08 16:30 | 176.06 | 172.03
2018-09-08 17:00 | 178.26 | 174.19
2018-09-08 17:30 | 180.6 | 176.56
2018-09-08 18:00 | 182.64 | 178.65
2018-09-08 18:30 | 184.78 | 180.92
2018-09-08 19:00 | 185.69 | 181.92
2018-09-08 19:30 | 185.08 | 181.26
2018-09-08 20:00 | 183.7 | 179.81
2018-09-08 20:30 | 182.59 | 178.68
2018-09-08 21:00 | 181.79 | 177.89
2018-09-08 21:30 | 181.1 | 177.08
2018-09-08 22:00 | 179.94 | 175.86
2018-09-08 22:30 | 178.77 | 174.68
2018-09-08 23:00 | 177.57 | 173.42
2018-09-08 23:30 | 176.78 | 172.55
2018-09-09 | 175.88 | 171.56
2018-09-09 00:30 | 175.42 | 171.05
2018-09-09 01:00 | 174.32 | 170
2018-09-09 01:30 | 173.78 | 169.53
2018-09-09 02:00 | 173.45 | 169.16
2018-09-09 02:30 | 173.09 | 168.85
2018-09-09 03:00 | 172.81 | 168.56
2018-09-09 03:30 | 172.72 | 168.48
2018-09-09 04:00 | 172.52 | 168.23
2018-09-09 04:30 | 172.77 | 168.45
2018-09-09 05:00 | 173.03 | 168.71
2018-09-09 05:30 | 173.98 | 169.65
2018-09-09 06:00 | 174.8 | 170.42
2018-09-09 06:30 | 176.09 | 171.8
2018-09-09 07:00 | 176.61 | 172.42
2018-09-09 07:30 | 177.23 | 173.01
2018-09-09 08:00 | 176.53 | 172.52
2018-09-09 08:30 | 175.57 | 171.6
2018-09-09 09:00 | 174.49 | 170.5
2018-09-09 09:30 | 173.15 | 169.07
2018-09-09 10:00 | 171.82 | 167.63
2018-09-09 10:30 | 170.61 | 166.47
2018-09-09 11:00 | 169.4 | 165.35
2018-09-09 11:30 | 169.13 | 165
2018-09-09 12:00 | 168.85 | 164.77
2018-09-09 12:30 | 168.84 | 164.83
2018-09-09 13:00 | 169 | 164.96
2018-09-09 13:30 | 168.94 | 164.95
2018-09-09 14:00 | 168.76 | 164.81
2018-09-09 14:30 | 169.29 | 165.34
2018-09-09 15:00 | 169.85 | 165.89
2018-09-09 15:30 | 171.29 | 167.29
2018-09-09 16:00 | 173.25 | 169.25
2018-09-09 16:30 | 174.88 | 170.8
2018-09-09 17:00 | 176.6 | 172.47
2018-09-09 17:30 | 179.27 | 175.17
2018-09-09 18:00 | 182.15 | 178.15
2018-09-09 18:30 | 185.67 | 181.73
2018-09-09 19:00 | 187.41 | 183.55
2018-09-09 19:30 | 186.62 | 182.72
2018-09-09 20:00 | 184.63 | 180.63
2018-09-09 20:30 | 183.66 | 179.61
2018-09-09 21:00 | 182.45 | 178.33
2018-09-09 21:30 | 182.12 | 178.09
2018-09-09 22:00 | 180.54 | 176.67
2018-09-09 22:30 | 178.68 | 174.66
2018-09-09 23:00 | 177.23 | 173.15
2018-09-09 23:30 | 176.51 | 172.13
2018-09-10 | 175.88 | 171.38
2018-09-10 00:30 | 175.74 | 171.29
2018-09-10 01:00 | 175.04 | 170.46
2018-09-10 01:30 | 173.73 | 169.22
2018-09-10 02:00 | 173.41 | 168.88
2018-09-10 02:30 | 173.01 | 168.5
2018-09-10 03:00 | 172.88 | 168.34
2018-09-10 03:30 | 172.94 | 168.41
2018-09-10 04:00 | 172.93 | 168.46
2018-09-10 04:30 | 173.68 | 169.28
2018-09-10 05:00 | 174.74 | 170.39
2018-09-10 05:30 | 176.44 | 172.28
2018-09-10 06:00 | 179.14 | 175.41
2018-09-10 06:30 | 183.11 | 179.56
2018-09-10 07:00 | 185.64 | 182.21
2018-09-10 07:30 | 187.6 | 184.23
2018-09-10 08:00 | 186.29 | 182.9
2018-09-10 08:30 | 182.52 | 179.1
2018-09-10 09:00 | 179.67 | 176.19
2018-09-10 09:30 | 177.25 | 173.69
2018-09-10 10:00 | 175.65 | 172.13
2018-09-10 10:30 | 174.3 | 170.65
2018-09-10 11:00 | 174.32 | 170.54
2018-09-10 11:30 | 173.32 | 169.72
2018-09-10 12:00 | 172.8 | 169.18
2018-09-10 12:30 | 171.95 | 168.33
2018-09-10 13:00 | 172.84 | 169.12
2018-09-10 13:30 | 173.77 | 169.94
2018-09-10 14:00 | 173.76 | 169.99
2018-09-10 14:30 | 174.54 | 170.89
2018-09-10 15:00 | 175.52 | 171.83
2018-09-10 15:30 | 177.01 | 173.22
2018-09-10 16:00 | 178.33 | 174.66
2018-09-10 16:30 | 179.4 | 175.7
2018-09-10 17:00 | 181.68 | 177.93
2018-09-10 17:30 | 183.36 | 179.6
2018-09-10 18:00 | 185.27 | 181.54
2018-09-10 18:30 | 188.23 | 184.54
2018-09-10 19:00 | 189.98 | 186.36
2018-09-10 19:30 | 187.74 | 184.18
2018-09-10 20:00 | 186.18 | 182.61
2018-09-10 20:30 | 185.09 | 181.44
2018-09-10 21:00 | 184.27 | 180.37
2018-09-10 21:30 | 183.52 | 179.66
2018-09-10 22:00 | 182.33 | 178.53
2018-09-10 22:30 | 180.48 | 176.67
2018-09-10 23:00 | 179.25 | 175.22
2018-09-10 23:30 | 178.52 | 174.36
2018-09-11 | 177.22 | 173.07
2018-09-11 00:30 | 176.49 | 172.33
2018-09-11 01:00 | 176.2 | 171.9
2018-09-11 01:30 | 175.17 | 170.94
2018-09-11 02:00 | 174.86 | 170.56
2018-09-11 02:30 | 174.78 | 170.42
2018-09-11 03:00 | 174.62 | 170.22
2018-09-11 03:30 | 174.42 | 170.15
2018-09-11 04:00 | 174.68 | 170.4
2018-09-11 04:30 | 175.44 | 171.22
2018-09-11 05:00 | 176.26 | 172.11
2018-09-11 05:30 | 177.98 | 173.86
2018-09-11 06:00 | 180.47 | 176.6
2018-09-11 06:30 | 183.75 | 180.03
2018-09-11 07:00 | 185.95 | 182.17
2018-09-11 07:30 | 186.95 | 183.19
2018-09-11 08:00 | 174.26 | 171.1
2018-09-11 08:30 | 162.17 | 159.27
2018-09-11 09:00 | 159.27 | 156.39
2018-09-11 09:30 | 152.05 | 149.1
2018-09-11 10:00 | 148.66 | 145.78
2018-09-11 10:30 | 147.42 | 144.53
2018-09-11 11:00 | 148.43 | 145.54
2018-09-11 11:30 | 149.67 | 146.81
2018-09-11 12:00 | 149.71 | 146.84
2018-09-11 12:30 | 148.59 | 145.73
2018-09-11 13:00 | 146.79 | 143.92
2018-09-11 13:30 | 146.41 | 143.61
2018-09-11 14:00 | 147.48 | 144.75
2018-09-11 14:30 | 147.87 | 145.15
2018-09-11 15:00 | 158.83 | 155.72
2018-09-11 15:30 | 170.23 | 166.8
2018-09-11 16:00 | 174.73 | 171.26
2018-09-11 16:30 | 173.02 | 169.84
2018-09-11 17:00 | 174.01 | 170.89
2018-09-11 17:30 | 174.82 | 171.67
2018-09-11 18:00 | 176.27 | 173.19
2018-09-11 18:30 | 178.27 | 175.33
2018-09-11 19:00 | 180.45 | 177.61
2018-09-11 19:30 | 179.29 | 176.44
2018-09-11 20:00 | 177.69 | 174.79
2018-09-11 20:30 | 176.78 | 173.88
2018-09-11 21:00 | 175.02 | 172.08
2018-09-11 21:30 | 174.83 | 171.87
2018-09-11 22:00 | 173.93 | 170.81
2018-09-11 22:30 | 172.26 | 169.08
2018-09-11 23:00 | 170.87 | 167.64
2018-09-11 23:30 | 169.74 | 166.45
2018-09-12 | 168.86 | 165.49
2018-09-12 00:30 | 168.23 | 164.88
2018-09-12 01:00 | 166.85 | 163.45
2018-09-12 01:30 | 165.83 | 162.51
2018-09-12 02:00 | 165.35 | 161.98
2018-09-12 02:30 | 164.73 | 161.33
2018-09-12 03:00 | 164.78 | 161.33
2018-09-12 03:30 | 165.16 | 161.7
2018-09-12 04:00 | 165.07 | 161.64
2018-09-12 04:30 | 166.26 | 162.85
2018-09-12 05:00 | 167.72 | 164.27
2018-09-12 05:30 | 169.22 | 165.79
2018-09-12 06:00 | 170.33 | 167
2018-09-12 06:30 | 173.11 | 170.05
2018-09-12 07:00 | 174.65 | 171.7
2018-09-12 07:30 | 175.43 | 172.48
2018-09-12 08:00 | 174.01 | 171.01
2018-09-12 08:30 | 172 | 168.97
2018-09-12 09:00 | 169.61 | 166.69
2018-09-12 09:30 | 167.33 | 164.47
2018-09-12 10:00 | 166.65 | 163.78
2018-09-12 10:30 | 166.51 | 163.49
2018-09-12 11:00 | 167.02 | 163.88
2018-09-12 11:30 | 166.83 | 163.72
2018-09-12 12:00 | 166.99 | 163.91
2018-09-12 12:30 | 166.32 | 163.35
2018-09-12 13:00 | 167.43 | 164.28
2018-09-12 13:30 | 167.66 | 164.57
2018-09-12 14:00 | 168.76 | 165.74
2018-09-12 14:30 | 169.55 | 166.49
2018-09-12 15:00 | 171.18 | 167.95
2018-09-12 15:30 | 172.27 | 169.07
2018-09-12 16:00 | 173.62 | 170.52
2018-09-12 16:30 | 174.03 | 170.95
2018-09-12 17:00 | 175.37 | 172.3
2018-09-12 17:30 | 176.66 | 173.53
2018-09-12 18:00 | 178.3 | 175.19
2018-09-12 18:30 | 180.63 | 177.62
2018-09-12 19:00 | 182.16 | 179.17
2018-09-12 19:30 | 180.64 | 177.58
2018-09-12 20:00 | 178.86 | 175.73
2018-09-12 20:30 | 177.33 | 174.14
2018-09-12 21:00 | 175.95 | 172.73
2018-09-12 21:30 | 175.08 | 171.66
2018-09-12 22:00 | 173.9 | 170.38
2018-09-12 22:30 | 171.72 | 168.12
2018-09-12 23:00 | 170.18 | 166.54
2018-09-12 23:30 | 169.16 | 165.61
2018-09-13 | 168.28 | 164.74
2018-09-13 00:30 | 168 | 164.34
2018-09-13 01:00 | 166.98 | 163.31
2018-09-13 01:30 | 166.6 | 162.92
2018-09-13 02:00 | 166.23 | 162.54
2018-09-13 02:30 | 165.42 | 161.74
2018-09-13 03:00 | 165.26 | 161.43
2018-09-13 03:30 | 165.18 | 161.49
2018-09-13 04:00 | 165.09 | 161.41
2018-09-13 04:30 | 165.71 | 162.04
2018-09-13 05:00 | 166.48 | 162.86
2018-09-13 05:30 | 168.45 | 164.87
2018-09-13 06:00 | 171.06 | 167.69
2018-09-13 06:30 | 174.24 | 171.03
2018-09-13 07:00 | 176.26 | 173.13
2018-09-13 07:30 | 176.84 | 173.81
2018-09-13 08:00 | 176.13 | 173.12
2018-09-13 08:30 | 173.93 | 170.94
2018-09-13 09:00 | 172.07 | 169.03
2018-09-13 09:30 | 171.83 | 168.6
2018-09-13 10:00 | 172.57 | 169.22
2018-09-13 10:30 | 171.73 | 168.39
2018-09-13 11:00 | 171.86 | 168.55
2018-09-13 11:30 | 172.48 | 169.11
2018-09-13 12:00 | 173.23 | 169.75
2018-09-13 12:30 | 173.52 | 170.17
2018-09-13 13:00 | 175.19 | 171.69
2018-09-13 13:30 | 175.88 | 172.3
2018-09-13 14:00 | 177.1 | 173.6
2018-09-13 14:30 | 177.99 | 174.52
2018-09-13 15:00 | 179.74 | 176.13
2018-09-13 15:30 | 181.23 | 177.59
2018-09-13 16:00 | 182.52 | 179.01
2018-09-13 16:30 | 183.4 | 179.83
2018-09-13 17:00 | 184.32 | 180.74
2018-09-13 17:30 | 184.9 | 181.42
2018-09-13 18:00 | 186.63 | 183.11
2018-09-13 18:30 | 187.54 | 184.15
2018-09-13 19:00 | 188.94 | 185.59
2018-09-13 19:30 | 187.62 | 184.21
2018-09-13 20:00 | 186.31 | 182.78
2018-09-13 20:30 | 185.18 | 181.64
2018-09-13 21:00 | 183.26 | 179.7
2018-09-13 21:30 | 182.75 | 179.16
2018-09-13 22:00 | 181.22 | 177.46
2018-09-13 22:30 | 179.35 | 175.51
2018-09-13 23:00 | 177.48 | 173.61
2018-09-13 23:30 | 176.88 | 172.97
2018-09-14 | 175.73 | 171.75
2018-09-14 00:30 | 174.93 | 170.91
2018-09-14 01:00 | 174.13 | 169.99
2018-09-14 01:30 | 173.39 | 169.2
2018-09-14 02:00 | 173.33 | 169.07
2018-09-14 02:30 | 172.73 | 168.43
2018-09-14 03:00 | 172.5 | 168.26
2018-09-14 03:30 | 172.38 | 168.15
2018-09-14 04:00 | 172.39 | 168.17
2018-09-14 04:30 | 173.04 | 168.82
2018-09-14 05:00 | 173.64 | 169.46
2018-09-14 05:30 | 174.79 | 170.87
2018-09-14 06:00 | 176.41 | 172.64
2018-09-14 06:30 | 179.56 | 175.81
2018-09-14 07:00 | 180.7 | 176.82
2018-09-14 07:30 | 181.54 | 177.64
2018-09-14 08:00 | 181.04 | 177.32
2018-09-14 08:30 | 178.58 | 174.93
2018-09-14 09:00 | 171.96 | 168.87
2018-09-14 09:30 | 169.67 | 166.58
2018-09-14 10:00 | 169.69 | 166.53
2018-09-14 10:30 | 169.27 | 165.99
2018-09-14 11:00 | 170.09 | 166.83
2018-09-14 11:30 | 170.63 | 167.37
2018-09-14 12:00 | 171.19 | 167.93
2018-09-14 12:30 | 171.59 | 168.29
2018-09-14 13:00 | 172.72 | 169.41
2018-09-14 13:30 | 173.12 | 169.81
2018-09-14 14:00 | 173.8 | 170.57
2018-09-14 14:30 | 174.98 | 171.8
2018-09-14 15:00 | 176.66 | 173.34
2018-09-14 15:30 | 179.22 | 175.78
2018-09-14 16:00 | 181.21 | 177.77
2018-09-14 16:30 | 182.64 | 179.27
2018-09-14 17:00 | 184.05 | 180.8
2018-09-14 17:30 | 184.83 | 181.55
2018-09-14 18:00 | 185.24 | 181.91
2018-09-14 18:30 | 186.24 | 182.93
2018-09-14 19:00 | 186.83 | 183.57
2018-09-14 19:30 | 186.01 | 182.77
2018-09-14 20:00 | 184.23 | 180.95
2018-09-14 20:30 | 182.88 | 179.59
2018-09-14 21:00 | 181.93 | 178.56
2018-09-14 21:30 | 181.6 | 178.05
2018-09-14 22:00 | 180.57 | 176.92
2018-09-14 22:30 | 179.68 | 175.93
2018-09-14 23:00 | 178.12 | 174.37
2018-09-14 23:30 | 177.78 | 173.93
2018-09-15 | 176.81 | 172.98
2018-09-15 00:30 | 176.22 | 172.42
2018-09-15 01:00 | 175 | 171.14
2018-09-15 01:30 | 174.21 | 170.26
2018-09-15 02:00 | 173.89 | 169.89
2018-09-15 02:30 | 173.54 | 169.5
2018-09-15 03:00 | 173.36 | 169.33
2018-09-15 03:30 | 173.11 | 169.05
2018-09-15 04:00 | 173.43 | 169.39
2018-09-15 04:30 | 173.62 | 169.51
2018-09-15 05:00 | 174.13 | 170
2018-09-15 05:30 | 175.38 | 171.24
2018-09-15 06:00 | 176.21 | 172.08
2018-09-15 06:30 | 177.38 | 173.33
2018-09-15 07:00 | 178.01 | 174.03
2018-09-15 07:30 | 178.82 | 174.83
2018-09-15 08:00 | 178.65 | 174.61
2018-09-15 08:30 | 177.85 | 173.86
2018-09-15 09:00 | 177.31 | 173.28
2018-09-15 09:30 | 176.32 | 172.29
2018-09-15 10:00 | 175.89 | 171.83
2018-09-15 10:30 | 175.56 | 171.52
2018-09-15 11:00 | 175.84 | 171.79
2018-09-15 11:30 | 176.12 | 172
2018-09-15 12:00 | 176.48 | 172.35
2018-09-15 12:30 | 177.3 | 173.26
2018-09-15 13:00 | 178.23 | 174.11
2018-09-15 13:30 | 179.17 | 175.07
2018-09-15 14:00 | 179.83 | 175.76
2018-09-15 14:30 | 181.33 | 177.36
2018-09-15 15:00 | 182.39 | 178.42
2018-09-15 15:30 | 183.55 | 179.56
2018-09-15 16:00 | 184.9 | 181.03
2018-09-15 16:30 | 187.05 | 183.2
2018-09-15 17:00 | 188.91 | 185.14
2018-09-15 17:30 | 189.94 | 186.11
2018-09-15 18:00 | 190.12 | 186.23
2018-09-15 18:30 | 191.32 | 187.46
2018-09-15 19:00 | 191.87 | 188.1
2018-09-15 19:30 | 191.17 | 187.34
2018-09-15 20:00 | 189.18 | 185.33
2018-09-15 20:30 | 187.49 | 183.62
2018-09-15 21:00 | 186.22 | 182.16
2018-09-15 21:30 | 185.77 | 181.67
2018-09-15 22:00 | 184.48 | 180.56
2018-09-15 22:30 | 182.95 | 178.96
2018-09-15 23:00 | 181.87 | 177.64
2018-09-15 23:30 | 180.94 | 176.63
2018-09-16 | 180.43 | 176.03
2018-09-16 00:30 | 179.45 | 175.1
2018-09-16 01:00 | 177.98 | 173.64
2018-09-16 01:30 | 177.57 | 173.26
2018-09-16 02:00 | 176.9 | 172.53
2018-09-16 02:30 | 176.54 | 172.14
2018-09-16 03:00 | 176.32 | 171.9
2018-09-16 03:30 | 176.13 | 171.65
2018-09-16 04:00 | 176 | 171.54
2018-09-16 04:30 | 176.12 | 171.7
2018-09-16 05:00 | 176.3 | 171.84
2018-09-16 05:30 | 176.26 | 171.85
2018-09-16 06:00 | 176.71 | 172.36
2018-09-16 06:30 | 177.53 | 173.16
2018-09-16 07:00 | 178 | 173.63
2018-09-16 07:30 | 178.81 | 174.65
2018-09-16 08:00 | 179.15 | 174.96
2018-09-16 08:30 | 178.2 | 173.98
2018-09-16 09:00 | 179.08 | 172.71
2018-09-16 09:30 | 179.06 | 171.63
2018-09-16 10:00 | 178.18 | 170.72
2018-09-16 10:30 | 176.99 | 169.38
2018-09-16 11:00 | 176.35 | 168.88
2018-09-16 11:30 | 176.42 | 169.01
2018-09-16 12:00 | 176.67 | 169.11
2018-09-16 12:30 | 176.5 | 169.02
2018-09-16 13:00 | 176.11 | 168.65
2018-09-16 13:30 | 175.98 | 168.49
2018-09-16 14:00 | 175.71 | 168.15
2018-09-16 14:30 | 175.95 | 168.36
2018-09-16 15:00 | 176.69 | 169.08
2018-09-16 15:30 | 178.08 | 170.42
2018-09-16 16:00 | 179.75 | 172.21
2018-09-16 16:30 | 181.82 | 174.38
2018-09-16 17:00 | 182.11 | 176.77
2018-09-16 17:30 | 182.96 | 180.93
2018-09-16 18:00 | 201.21 | 200.44
2018-09-16 18:30 | 200.62 | 199.61
2018-09-16 19:00 | 200.18 | 199.1
2018-09-16 19:30 | 201.34 | 200.22
2018-09-16 20:00 | 202.8 | 201.68
2018-09-16 20:30 | 203.12 | 202.12
2018-09-16 21:00 | 203.48 | 202.49
2018-09-16 21:30 | 203.49 | 202.41
2018-09-16 22:00 | 204.15 | 203.08
2018-09-16 22:30 | 205.22 | 204.44
2018-09-16 23:00 | 183.51 | 180.13
2018-09-16 23:30 | 180.29 | 175.89
2018-09-17 | 179.52 | 175.09
2018-09-17 00:30 | 179.11 | 174.65
2018-09-17 01:00 | 178.07 | 173.57
2018-09-17 01:30 | 177.68 | 173.12
2018-09-17 02:00 | 177.09 | 172.55
2018-09-17 02:30 | 177.14 | 172.62
2018-09-17 03:00 | 176.44 | 172.01
2018-09-17 03:30 | 176.85 | 172.41
2018-09-17 04:00 | 176.96 | 172.52
2018-09-17 04:30 | 177.71 | 173.24
2018-09-17 05:00 | 178.91 | 174.6
2018-09-17 05:30 | 181.12 | 176.89
2018-09-17 06:00 | 183.77 | 179.77
2018-09-17 06:30 | 188.88 | 185.13
2018-09-17 07:00 | 191.35 | 187.76
2018-09-17 07:30 | 191.57 | 187.98
2018-09-17 08:00 | 189.71 | 185.97
2018-09-17 08:30 | 185.88 | 182.02
2018-09-17 09:00 | 182.45 | 178.62
2018-09-17 09:30 | 179.83 | 176.03
2018-09-17 10:00 | 178.33 | 174.46
2018-09-17 10:30 | 176.34 | 172.31
2018-09-17 11:00 | 172.86 | 169.12
2018-09-17 11:30 | 172.8 | 169
2018-09-17 12:00 | 174.5 | 170.45
2018-09-17 12:30 | 173.98 | 170.02
2018-09-17 13:00 | 174.09 | 170.12
2018-09-17 13:30 | 174.86 | 170.82
2018-09-17 14:00 | 175.18 | 171.25
2018-09-17 14:30 | 175.41 | 171.48
2018-09-17 15:00 | 176.58 | 172.59
2018-09-17 15:30 | 177.68 | 173.64
2018-09-17 16:00 | 178.67 | 174.75
2018-09-17 16:30 | 180.53 | 176.61
2018-09-17 17:00 | 183.07 | 179.03
2018-09-17 17:30 | 184.97 | 180.94
2018-09-17 18:00 | 186.59 | 182.63
2018-09-17 18:30 | 190.67 | 186.82
2018-09-17 19:00 | 192.92 | 189.18
2018-09-17 19:30 | 192.19 | 188.49
2018-09-17 20:00 | 190.62 | 186.89
2018-09-17 20:30 | 189.68 | 185.99
2018-09-17 21:00 | 188.05 | 184.24
2018-09-17 21:30 | 187.36 | 183.31
2018-09-17 22:00 | 185.82 | 181.63
2018-09-17 22:30 | 184.12 | 179.84
2018-09-17 23:00 | 182.29 | 177.94
2018-09-17 23:30 | 181.22 | 176.87
2018-09-18 | 179.86 | 175.61
2018-09-18 00:30 | 179.27 | 175.06
2018-09-18 01:00 | 178.32 | 173.99
2018-09-18 01:30 | 177.97 | 173.63
2018-09-18 02:00 | 177.42 | 173.05
2018-09-18 02:30 | 177.04 | 172.66
2018-09-18 03:00 | 176.94 | 172.56
2018-09-18 03:30 | 176.78 | 172.44
2018-09-18 04:00 | 176.78 | 172.47
2018-09-18 04:30 | 177.49 | 173.2
2018-09-18 05:00 | 178.32 | 174.07
2018-09-18 05:30 | 180.26 | 176.02
2018-09-18 06:00 | 182.56 | 178.48
2018-09-18 06:30 | 185.88 | 181.88
2018-09-18 07:00 | 187.92 | 183.96
2018-09-18 07:30 | 187.84 | 183.93
2018-09-18 08:00 | 186.67 | 182.88
2018-09-18 08:30 | 183.16 | 179.35
2018-09-18 09:00 | 180.87 | 176.83
2018-09-18 09:30 | 178.23 | 174.15
2018-09-18 10:00 | 177.26 | 173.24
2018-09-18 10:30 | 176.06 | 172
2018-09-18 11:00 | 175.52 | 171.54
2018-09-18 11:30 | 175.68 | 171.72
2018-09-18 12:00 | 176.16 | 172.16
2018-09-18 12:30 | 175.83 | 171.92
2018-09-18 13:00 | 176.88 | 172.89
2018-09-18 13:30 | 177.86 | 173.84
2018-09-18 14:00 | 178.98 | 175.13
2018-09-18 14:30 | 180.53 | 176.65
2018-09-18 15:00 | 181.46 | 177.53
2018-09-18 15:30 | 182.64 | 178.7
2018-09-18 16:00 | 183.7 | 179.78
2018-09-18 16:30 | 184.8 | 180.93
2018-09-18 17:00 | 185.91 | 182.12
2018-09-18 17:30 | 187.05 | 183.2
2018-09-18 18:00 | 188.37 | 184.59
2018-09-18 18:30 | 190.29 | 186.64
2018-09-18 19:00 | 192.04 | 188.42
2018-09-18 19:30 | 190.89 | 187.26
2018-09-18 20:00 | 189.23 | 185.58
2018-09-18 20:30 | 187.71 | 184.08
2018-09-18 21:00 | 186.28 | 182.55
2018-09-18 21:30 | 185.67 | 181.73
2018-09-18 22:00 | 184.07 | 180.2
2018-09-18 22:30 | 182.06 | 178.03
2018-09-18 23:00 | 180.24 | 176.23
2018-09-18 23:30 | 180.27 | 176.06
2018-09-19 | 179.39 | 175.06
2018-09-19 00:30 | 178.85 | 174.63
2018-09-19 01:00 | 177.63 | 173.41
2018-09-19 01:30 | 177.23 | 172.96
2018-09-19 02:00 | 177.04 | 172.67
2018-09-19 02:30 | 176.7 | 172.29
2018-09-19 03:00 | 176.22 | 171.88
2018-09-19 03:30 | 176.33 | 171.99
2018-09-19 04:00 | 176.24 | 171.92
2018-09-19 04:30 | 176.65 | 172.29
2018-09-19 05:00 | 177.29 | 172.97
2018-09-19 05:30 | 178.11 | 173.79
2018-09-19 06:00 | 179.33 | 175.05
2018-09-19 06:30 | 181.52 | 177.6
2018-09-19 07:00 | 183.11 | 179.18
2018-09-19 07:30 | 183.85 | 180.03
2018-09-19 08:00 | 183.21 | 179.37
2018-09-19 08:30 | 180.61 | 176.83
2018-09-19 09:00 | 178.66 | 174.86
2018-09-19 09:30 | 176.75 | 172.73
2018-09-19 10:00 | 173.68 | 170.2
2018-09-19 10:30 | 172.24 | 168.89
2018-09-19 11:00 | 174.36 | 170.81
2018-09-19 11:30 | 175.49 | 171.81
2018-09-19 12:00 | 175.94 | 172.21
2018-09-19 12:30 | 176.44 | 172.66
2018-09-19 13:00 | 178.02 | 174.15
2018-09-19 13:30 | 179.02 | 175.23
2018-09-19 14:00 | 180.46 | 176.75
2018-09-19 14:30 | 180.84 | 177.19
2018-09-19 15:00 | 182.84 | 179.18
2018-09-19 15:30 | 183.68 | 180.02
2018-09-19 16:00 | 185.89 | 182.15
2018-09-19 16:30 | 186.26 | 182.47
2018-09-19 17:00 | 187.48 | 183.82
2018-09-19 17:30 | 186.33 | 182.82
2018-09-19 18:00 | 196.03 | 195.2
2018-09-19 18:30 | 195.25 | 194.4
2018-09-19 19:00 | 194.98 | 194.12
2018-09-19 19:30 | 195.49 | 194.67
2018-09-19 20:00 | 196.62 | 195.9
2018-09-19 20:30 | 174.35 | 172.25
2018-09-19 21:00 | 182.43 | 178.71
2018-09-19 21:30 | 187.08 | 183.1
2018-09-19 22:00 | 185.1 | 181.15
2018-09-19 22:30 | 183.27 | 179.22
2018-09-19 23:00 | 181.02 | 176.98
2018-09-19 23:30 | 180.24 | 176.29
2018-09-20 | 179.57 | 175.56
2018-09-20 00:30 | 178.98 | 174.87
2018-09-20 01:00 | 177.64 | 173.43
2018-09-20 01:30 | 177.23 | 173.01
2018-09-20 02:00 | 176.43 | 172.19
2018-09-20 02:30 | 176.06 | 171.79
2018-09-20 03:00 | 175.25 | 170.94
2018-09-20 03:30 | 175.31 | 170.95
2018-09-20 04:00 | 175.2 | 170.71
2018-09-20 04:30 | 174.97 | 170.68
2018-09-20 05:00 | 175.45 | 171.3
2018-09-20 05:30 | 176.84 | 172.69
2018-09-20 06:00 | 178.57 | 174.52
2018-09-20 06:30 | 181.44 | 177.49
2018-09-20 07:00 | 183.09 | 179.15
2018-09-20 07:30 | 184.05 | 180.07
2018-09-20 08:00 | 184.01 | 180.07
2018-09-20 08:30 | 182.05 | 178.15
2018-09-20 09:00 | 179.53 | 175.59
2018-09-20 09:30 | 176.93 | 173.05
2018-09-20 10:00 | 176.81 | 172.78
2018-09-20 10:30 | 175.34 | 171.28
2018-09-20 11:00 | 175.28 | 171.24
2018-09-20 11:30 | 175.53 | 171.64
2018-09-20 12:00 | 175.91 | 172
2018-09-20 12:30 | 175 | 171.11
2018-09-20 13:00 | 175.12 | 170.99
2018-09-20 13:30 | 175.19 | 171.05
2018-09-20 14:00 | 176.55 | 172.24
2018-09-20 14:30 | 177.01 | 172.8
2018-09-20 15:00 | 177.34 | 173.12
2018-09-20 15:30 | 177.47 | 173.5
2018-09-20 16:00 | 179.26 | 175.19
2018-09-20 16:30 | 181.02 | 176.91
2018-09-20 17:00 | 182.67 | 178.6
2018-09-20 17:30 | 184.58 | 180.54
2018-09-20 18:00 | 186.83 | 182.77
2018-09-20 18:30 | 189.86 | 185.8
2018-09-20 19:00 | 192.3 | 188.37
2018-09-20 19:30 | 192.1 | 188.2
2018-09-20 20:00 | 190.77 | 186.81
2018-09-20 20:30 | 189.89 | 185.85
2018-09-20 21:00 | 188.68 | 184.56
2018-09-20 21:30 | 188.17 | 184.13
2018-09-20 22:00 | 186.51 | 182.53
2018-09-20 22:30 | 184.64 | 180.59
2018-09-20 23:00 | 183.3 | 179.21
2018-09-20 23:30 | 182.36 | 178.16
2018-09-21 | 180.81 | 176.53
2018-09-21 00:30 | 180.14 | 175.86
2018-09-21 01:00 | 178.31 | 174.2
2018-09-21 01:30 | 176.52 | 172.58
2018-09-21 02:00 | 176.06 | 172.15
2018-09-21 02:30 | 175.63 | 171.61
2018-09-21 03:00 | 175.46 | 171.45
2018-09-21 03:30 | 175.81 | 171.67
2018-09-21 04:00 | 175.7 | 171.53
2018-09-21 04:30 | 176.48 | 172.43
2018-09-21 05:00 | 177.77 | 173.77
2018-09-21 05:30 | 179.36 | 175.5
2018-09-21 06:00 | 182.03 | 178.31
2018-09-21 06:30 | 185.54 | 181.79
2018-09-21 07:00 | 186.92 | 183.26
2018-09-21 07:30 | 187.46 | 183.83
2018-09-21 08:00 | 185.4 | 181.78
2018-09-21 08:30 | 182.56 | 178.82
2018-09-21 09:00 | 180.07 | 176.3
2018-09-21 09:30 | 177.28 | 173.63
2018-09-21 10:00 | 176.11 | 172.49
2018-09-21 10:30 | 174.96 | 171.31
2018-09-21 11:00 | 164.88 | 161.13
2018-09-21 11:30 | 149.65 | 145.53
2018-09-21 12:00 | 151.37 | 145.48
2018-09-21 12:30 | 150.25 | 145.04
2018-09-21 13:00 | 155.87 | 150.84
2018-09-21 13:30 | 168.21 | 163.85
2018-09-21 14:00 | 164.39 | 160.92
2018-09-21 14:30 | 168.07 | 164.58
2018-09-21 15:00 | 168.35 | 165.06
2018-09-21 15:30 | 169.32 | 166.05
2018-09-21 16:00 | 173.34 | 170.08
2018-09-21 16:30 | 178.82 | 175.41
2018-09-21 17:00 | 183.45 | 179.86
2018-09-21 17:30 | 187.1 | 183.32
2018-09-21 18:00 | 180.02 | 176.53
2018-09-21 18:30 | 182.45 | 178.96
2018-09-21 19:00 | 184.53 | 180.97
2018-09-21 19:30 | 184.33 | 180.77
2018-09-21 20:00 | 183.26 | 179.67
2018-09-21 20:30 | 181.65 | 177.9
2018-09-21 21:00 | 180.62 | 176.85
2018-09-21 21:30 | 180.3 | 176.57
2018-09-21 22:00 | 178.82 | 175.03
2018-09-21 22:30 | 177.41 | 173.59
2018-09-21 23:00 | 176.08 | 172.24
2018-09-21 23:30 | 175.03 | 171.14
2018-09-22 | 173.34 | 169.46
2018-09-22 00:30 | 173.2 | 169.28
2018-09-22 01:00 | 172.43 | 168.4
2018-09-22 01:30 | 171.96 | 167.95
2018-09-22 02:00 | 171.62 | 167.58
2018-09-22 02:30 | 171.5 | 167.44
2018-09-22 03:00 | 171.18 | 167.1
2018-09-22 03:30 | 171.04 | 166.99
2018-09-22 04:00 | 171.33 | 167.31
2018-09-22 04:30 | 171.85 | 167.82
2018-09-22 05:00 | 172.55 | 168.53
2018-09-22 05:30 | 173.44 | 169.42
2018-09-22 06:00 | 174.71 | 170.71
2018-09-22 06:30 | 176.25 | 171.89
2018-09-22 07:00 | 175.91 | 171.97
2018-09-22 07:30 | 175.65 | 171.8
2018-09-22 08:00 | 174.82 | 171.12
2018-09-22 08:30 | 173.48 | 169.83
2018-09-22 09:00 | 171.84 | 168.14
2018-09-22 09:30 | 170.77 | 167.06
2018-09-22 10:00 | 170.63 | 166.9
2018-09-22 10:30 | 169.73 | 166.02
2018-09-22 11:00 | 169.29 | 165.65
2018-09-22 11:30 | 169.11 | 165.49
2018-09-22 12:00 | 170.11 | 166.51
2018-09-22 12:30 | 168.86 | 165.3
2018-09-22 13:00 | 168.9 | 165.35
2018-09-22 13:30 | 177.7 | 173.82
2018-09-22 14:00 | 181.97 | 177.83
2018-09-22 14:30 | 184.41 | 180.14
2018-09-22 15:00 | 184.57 | 180.24
2018-09-22 15:30 | 186.84 | 182.45
2018-09-22 16:00 | 189 | 184.55
2018-09-22 16:30 | 191.78 | 187.24
2018-09-22 17:00 | 191.29 | 187.02
2018-09-22 17:30 | 190.94 | 186.62
2018-09-22 18:00 | 192.33 | 188.09
2018-09-22 18:30 | 193.7 | 189.7
2018-09-22 19:00 | 195.05 | 191.18
2018-09-22 19:30 | 194.51 | 190.64
2018-09-22 20:00 | 194.05 | 190.11
2018-09-22 20:30 | 193.18 | 189.2
2018-09-22 21:00 | 191.07 | 187.12
2018-09-22 21:30 | 190.03 | 186.07
2018-09-22 22:00 | 188.58 | 184.62
2018-09-22 22:30 | 187.12 | 183.14
2018-09-22 23:00 | 185.2 | 181.15
2018-09-22 23:30 | 184.77 | 180.65
2018-09-23 | 184.32 | 180.16
2018-09-23 00:30 | 183.78 | 179.55
2018-09-23 01:00 | 183.15 | 178.83
2018-09-23 01:30 | 182.46 | 178.34
2018-09-23 02:00 | 182.1 | 177.87
2018-09-23 02:30 | 181.86 | 177.7
2018-09-23 03:00 | 181.28 | 177.13
2018-09-23 03:30 | 181.68 | 177.42
2018-09-23 04:00 | 182.35 | 178.08
2018-09-23 04:30 | 182.67 | 178.35
2018-09-23 05:00 | 182.58 | 178.3
2018-09-23 05:30 | 181.92 | 177.58
2018-09-23 06:00 | 182.58 | 178.24
2018-09-23 06:30 | 183.97 | 179.67
2018-09-23 07:00 | 184.47 | 180.18
2018-09-23 07:30 | 184.65 | 180.33
2018-09-23 08:00 | 183.32 | 179.04
2018-09-23 08:30 | 181.68 | 177.56
2018-09-23 09:00 | 178.98 | 175.17
2018-09-23 09:30 | 177.09 | 173.17
2018-09-23 10:00 | 179.47 | 175.42
2018-09-23 10:30 | 179.52 | 175.4
2018-09-23 11:00 | 181.61 | 177.27
2018-09-23 11:30 | 182.08 | 177.78
2018-09-23 12:00 | 182.42 | 178.11
2018-09-23 12:30 | 182.99 | 178.67
2018-09-23 13:00 | 181.99 | 177.73
2018-09-23 13:30 | 177 | 173.24
2018-09-23 14:00 | 175.16 | 171.63
2018-09-23 14:30 | 176.76 | 173.21
2018-09-23 15:00 | 180.66 | 176.85
2018-09-23 15:30 | 185.25 | 180.99
2018-09-23 16:00 | 189.33 | 184.83
2018-09-23 16:30 | 191.03 | 186.65
2018-09-23 17:00 | 193.43 | 189.13
2018-09-23 17:30 | 195.81 | 191.62
2018-09-23 18:00 | 198.32 | 194.02
2018-09-23 18:30 | 199.92 | 195.64
2018-09-23 19:00 | 201.33 | 197.11
2018-09-23 19:30 | 200.61 | 196.25
2018-09-23 20:00 | 198.44 | 194
2018-09-23 20:30 | 197.22 | 192.74
2018-09-23 21:00 | 195.53 | 191.03
2018-09-23 21:30 | 194.71 | 190.18
2018-09-23 22:00 | 193.41 | 188.79
2018-09-23 22:30 | 191.59 | 186.86
2018-09-23 23:00 | 190.13 | 185.47
2018-09-23 23:30 | 189.59 | 184.83
2018-09-24 | 188.45 | 183.61
2018-09-24 00:30 | 187.48 | 182.7
2018-09-24 01:00 | 186.39 | 181.66
2018-09-24 01:30 | 186.12 | 181.38
2018-09-24 02:00 | 185.95 | 181.09
2018-09-24 02:30 | 185.98 | 180.98
2018-09-24 03:00 | 185.69 | 180.68
2018-09-24 03:30 | 185.77 | 180.76
2018-09-24 04:00 | 186.19 | 181.18
2018-09-24 04:30 | 186.6 | 181.64
2018-09-24 05:00 | 187.56 | 182.63
2018-09-24 05:30 | 188.89 | 184.04
2018-09-24 06:00 | 190.56 | 185.78
2018-09-24 06:30 | 192.25 | 187.89
2018-09-24 07:00 | 192.54 | 188.37
2018-09-24 07:30 | 191.93 | 187.98
2018-09-24 08:00 | 191.47 | 187.47
2018-09-24 08:30 | 190.38 | 186.54
2018-09-24 09:00 | 188.58 | 184.72
2018-09-24 09:30 | 187.8 | 183.85
2018-09-24 10:00 | 187.09 | 183.13
2018-09-24 10:30 | 188.26 | 184.14
2018-09-24 11:00 | 187.77 | 183.82
2018-09-24 11:30 | 188.98 | 185.01
2018-09-24 12:00 | 189.79 | 185.79
2018-09-24 12:30 | 190.98 | 186.72
2018-09-24 13:00 | 190.95 | 186.69
2018-09-24 13:30 | 191.47 | 187.16
2018-09-24 14:00 | 191.95 | 187.81
2018-09-24 14:30 | 193.11 | 189.01
2018-09-24 15:00 | 194.09 | 189.9
2018-09-24 15:30 | 196.97 | 192.54
2018-09-24 16:00 | 198.97 | 194.5
2018-09-24 16:30 | 200.52 | 196.19
2018-09-24 17:00 | 202.02 | 197.72
2018-09-24 17:30 | 202.71 | 198.37
2018-09-24 18:00 | 203.8 | 199.49
2018-09-24 18:30 | 205.68 | 201.43
2018-09-24 19:00 | 207.45 | 203.25
2018-09-24 19:30 | 206.41 | 202.19
2018-09-24 20:00 | 203.84 | 199.61
2018-09-24 20:30 | 202.96 | 198.64
2018-09-24 21:00 | 201.38 | 197
2018-09-24 21:30 | 200.08 | 195.64
2018-09-24 22:00 | 198.38 | 193.81
2018-09-24 22:30 | 196.58 | 191.97
2018-09-24 23:00 | 194.7 | 190.12
2018-09-24 23:30 | 194.07 | 189.54
2018-09-25 | 192.91 | 188.34
2018-09-25 00:30 | 192.41 | 187.84
2018-09-25 01:00 | 191.18 | 186.66
2018-09-25 01:30 | 190.47 | 185.96
2018-09-25 02:00 | 190.06 | 185.49
2018-09-25 02:30 | 189.17 | 184.63
2018-09-25 03:00 | 189.12 | 184.61
2018-09-25 03:30 | 188.93 | 184.37
2018-09-25 04:00 | 188.58 | 184.09
2018-09-25 04:30 | 189.21 | 184.72
2018-09-25 05:00 | 189.92 | 185.41
2018-09-25 05:30 | 190.63 | 186.22
2018-09-25 06:00 | 192.11 | 187.9
2018-09-25 06:30 | 193.85 | 189.77
2018-09-25 07:00 | 194.57 | 190.54
2018-09-25 07:30 | 195.94 | 191.87
2018-09-25 08:00 | 196.23 | 192.18
2018-09-25 08:30 | 195.67 | 191.67
2018-09-25 09:00 | 194.33 | 190.23
2018-09-25 09:30 | 194.28 | 189.83
2018-09-25 10:00 | 197.41 | 192.75
2018-09-25 10:30 | 191.73 | 187.66
2018-09-25 11:00 | 190.75 | 186.69
2018-09-25 11:30 | 190.77 | 186.65
2018-09-25 12:00 | 191.7 | 187.53
2018-09-25 12:30 | 192.49 | 188.25
2018-09-25 13:00 | 193.46 | 189.18
2018-09-25 13:30 | 194.39 | 190.06
2018-09-25 14:00 | 195.97 | 191.74
2018-09-25 14:30 | 195.3 | 191.29
2018-09-25 15:00 | 196.39 | 192.17
2018-09-25 15:30 | 197.12 | 192.88
2018-09-25 16:00 | 198.01 | 193.82
2018-09-25 16:30 | 199.2 | 194.88
2018-09-25 17:00 | 199.51 | 195.31
2018-09-25 17:30 | 201.09 | 196.94
2018-09-25 18:00 | 189.57 | 186.25
2018-09-25 18:30 | 209.16 | 207.8
2018-09-25 19:00 | 212.41 | 211.13
2018-09-25 19:30 | 213.04 | 211.86
2018-09-25 20:00 | 214.72 | 213.61
2018-09-25 20:30 | 202.94 | 199.47
2018-09-25 21:00 | 202.28 | 197.91
2018-09-25 21:30 | 201.58 | 197.13
2018-09-25 22:00 | 199.81 | 195.52
2018-09-25 22:30 | 197.76 | 193.33
2018-09-25 23:00 | 195.67 | 191.27
2018-09-25 23:30 | 195.02 | 190.58
2018-09-26 | 193.37 | 188.88
2018-09-26 00:30 | 193.59 | 188.92
2018-09-26 01:00 | 192.65 | 187.91
2018-09-26 01:30 | 191.96 | 187.29
2018-09-26 02:00 | 191.33 | 186.6
2018-09-26 02:30 | 190.97 | 186.24
2018-09-26 03:00 | 191.21 | 186.42
2018-09-26 03:30 | 191.02 | 186.37
2018-09-26 04:00 | 190.8 | 186.18
2018-09-26 04:30 | 191.13 | 186.54
2018-09-26 05:00 | 192.23 | 187.66
2018-09-26 05:30 | 193.16 | 188.65
2018-09-26 06:00 | 194.93 | 190.54
2018-09-26 06:30 | 196.94 | 192.66
2018-09-26 07:00 | 197.25 | 193.08
2018-09-26 07:30 | 198.11 | 193.93
2018-09-26 08:00 | 197.68 | 193.41
2018-09-26 08:30 | 195.94 | 191.77
2018-09-26 09:00 | 194.07 | 189.94
2018-09-26 09:30 | 192.75 | 188.56
2018-09-26 10:00 | 193.06 | 188.92
2018-09-26 10:30 | 193.15 | 188.95
2018-09-26 11:00 | 193.17 | 188.98
2018-09-26 11:30 | 193.83 | 189.57
2018-09-26 12:00 | 194.4 | 190.22
2018-09-26 12:30 | 195.12 | 190.88
2018-09-26 13:00 | 195.83 | 191.65
2018-09-26 13:30 | 197.55 | 193.35
2018-09-26 14:00 | 198.47 | 194.35
2018-09-26 14:30 | 199.47 | 195.29
2018-09-26 15:00 | 200.37 | 196.05
2018-09-26 15:30 | 201.36 | 197.03
2018-09-26 16:00 | 201.7 | 197.46
2018-09-26 16:30 | 202.94 | 198.57
2018-09-26 17:00 | 203.85 | 199.51
2018-09-26 17:30 | 204.29 | 200.05
2018-09-26 18:00 | 209.42 | 208.04
2018-09-26 18:30 | 212.89 | 211.75
2018-09-26 19:00 | 211.78 | 210.66
2018-09-26 19:30 | 212.88 | 211.74
2018-09-26 20:00 | 214.57 | 213.52
2018-09-26 20:30 | 216.31 | 215.31
2018-09-26 21:00 | 218.18 | 217.12
2018-09-26 21:30 | 203.5 | 199.82
2018-09-26 22:00 | 201.4 | 196.95
2018-09-26 22:30 | 198.92 | 194.59
2018-09-26 23:00 | 197.58 | 193.26
2018-09-26 23:30 | 196.59 | 192.16
2018-09-27 | 195.6 | 191.02
2018-09-27 00:30 | 195.42 | 190.63
2018-09-27 01:00 | 194.48 | 189.64
2018-09-27 01:30 | 193.8 | 188.94
2018-09-27 02:00 | 193.87 | 189.09
2018-09-27 02:30 | 193.1 | 188.24
2018-09-27 03:00 | 192.94 | 188.14
2018-09-27 03:30 | 192.85 | 188.01
2018-09-27 04:00 | 192.69 | 187.92
2018-09-27 04:30 | 192.96 | 188.21
2018-09-27 05:00 | 193.66 | 188.94
2018-09-27 05:30 | 194.28 | 189.56
2018-09-27 06:00 | 195.64 | 191.04
2018-09-27 06:30 | 197.78 | 193.53
2018-09-27 07:00 | 198.34 | 194.02
2018-09-27 07:30 | 199.01 | 194.55
2018-09-27 08:00 | 198.9 | 194.48
2018-09-27 08:30 | 197.59 | 193.15
2018-09-27 09:00 | 195.78 | 191.42
2018-09-27 09:30 | 194.5 | 190.21
2018-09-27 10:00 | 194.22 | 189.99
2018-09-27 10:30 | 193.94 | 189.7
2018-09-27 11:00 | 194.26 | 190.04
2018-09-27 11:30 | 194.72 | 190.47
2018-09-27 12:00 | 195.02 | 190.81
2018-09-27 12:30 | 195.44 | 191.19
2018-09-27 13:00 | 196.55 | 192.3
2018-09-27 13:30 | 197.81 | 193.48
2018-09-27 14:00 | 198.96 | 194.71
2018-09-27 14:30 | 197.98 | 193.97
2018-09-27 15:00 | 199.23 | 195.17
2018-09-27 15:30 | 200.63 | 196.48
2018-09-27 16:00 | 202.23 | 198.14
2018-09-27 16:30 | 203.98 | 199.99
2018-09-27 17:00 | 205.73 | 201.64
2018-09-27 17:30 | 207.81 | 203.49
2018-09-27 18:00 | 208.96 | 204.54
2018-09-27 18:30 | 209.94 | 207.66
2018-09-27 19:00 | 214.07 | 212.73
2018-09-27 19:30 | 213.72 | 212.56
2018-09-27 20:00 | 215.43 | 214.32
2018-09-27 20:30 | 216.74 | 215.66
2018-09-27 21:00 | 204.16 | 200.73
2018-09-27 21:30 | 202.89 | 198.57
2018-09-27 22:00 | 201.93 | 197.44
2018-09-27 22:30 | 200.1 | 195.54
2018-09-27 23:00 | 199.04 | 194.37
2018-09-27 23:30 | 198.17 | 193.42
2018-09-28 | 196.14 | 191.5
2018-09-28 00:30 | 195.4 | 190.83
2018-09-28 01:00 | 194.69 | 189.9
2018-09-28 01:30 | 194 | 189.32
2018-09-28 02:00 | 193.2 | 188.52
2018-09-28 02:30 | 193.36 | 188.6
2018-09-28 03:00 | 193.05 | 188.21
2018-09-28 03:30 | 192.99 | 188.23
2018-09-28 04:00 | 193.03 | 188.24
2018-09-28 04:30 | 193.4 | 188.6
2018-09-28 05:00 | 193.81 | 189.13
2018-09-28 05:30 | 194.99 | 190.35
2018-09-28 06:00 | 196.34 | 191.84
2018-09-28 06:30 | 198.44 | 193.91
2018-09-28 07:00 | 198.76 | 194.26
2018-09-28 07:30 | 198.62 | 194.33
2018-09-28 08:00 | 197.27 | 193.11
2018-09-28 08:30 | 190.52 | 186.79
2018-09-28 09:00 | 191.27 | 187.42
2018-09-28 09:30 | 189.4 | 185.61
2018-09-28 10:00 | 190.56 | 186.72
2018-09-28 10:30 | 190.45 | 186.54
2018-09-28 11:00 | 190.21 | 186.43
2018-09-28 11:30 | 189.6 | 185.95
2018-09-28 12:00 | 190.67 | 187.01
2018-09-28 12:30 | 189.92 | 186.22
2018-09-28 13:00 | 191.97 | 188.24
2018-09-28 13:30 | 191.4 | 187.81
2018-09-28 14:00 | 193.35 | 189.77
2018-09-28 14:30 | 197.79 | 194.04
2018-09-28 15:00 | 200.55 | 196.59
2018-09-28 15:30 | 199.71 | 195.81
2018-09-28 16:00 | 201.48 | 197.53
2018-09-28 16:30 | 203.15 | 199.14
2018-09-28 17:00 | 204.14 | 200.11
2018-09-28 17:30 | 205.29 | 201.25
2018-09-28 18:00 | 205.85 | 201.79
2018-09-28 18:30 | 206.53 | 202.5
2018-09-28 19:00 | 206.71 | 202.61
2018-09-28 19:30 | 205.23 | 201.11
2018-09-28 20:00 | 203.05 | 198.88
2018-09-28 20:30 | 201.74 | 197.54
2018-09-28 21:00 | 199.94 | 195.67
2018-09-28 21:30 | 199.64 | 195.15
2018-09-28 22:00 | 198.24 | 193.71
2018-09-28 22:30 | 196.7 | 192.11
2018-09-28 23:00 | 195.11 | 190.36
2018-09-28 23:30 | 194.66 | 189.81
2018-09-29 | 193.14 | 188.27
2018-09-29 00:30 | 192.78 | 187.95
2018-09-29 01:00 | 191.76 | 187.1
2018-09-29 01:30 | 191.09 | 186.38
2018-09-29 02:00 | 190.45 | 185.76
2018-09-29 02:30 | 190.23 | 185.49
2018-09-29 03:00 | 190.05 | 185.3
2018-09-29 03:30 | 189.74 | 185
2018-09-29 04:00 | 189.18 | 184.46
2018-09-29 04:30 | 189.25 | 184.53
2018-09-29 05:00 | 189.52 | 184.77
2018-09-29 05:30 | 189.83 | 185.13
2018-09-29 06:00 | 190.64 | 185.99
2018-09-29 06:30 | 191.11 | 186.59
2018-09-29 07:00 | 191.06 | 186.61
2018-09-29 07:30 | 191.28 | 186.86
2018-09-29 08:00 | 191.34 | 186.91
2018-09-29 08:30 | 191.11 | 186.69
2018-09-29 09:00 | 190.05 | 185.76
2018-09-29 09:30 | 190.19 | 185.87
2018-09-29 10:00 | 190.41 | 186.13
2018-09-29 10:30 | 189.79 | 185.55
2018-09-29 11:00 | 188.98 | 184.89
2018-09-29 11:30 | 189.64 | 185.5
2018-09-29 12:00 | 190.29 | 186.16
2018-09-29 12:30 | 191.17 | 186.98
2018-09-29 13:00 | 191.58 | 187.4
2018-09-29 13:30 | 192.22 | 188.02
2018-09-29 14:00 | 193.27 | 189.01
2018-09-29 14:30 | 193.75 | 189.45
2018-09-29 15:00 | 195.18 | 190.78
2018-09-29 15:30 | 196.72 | 192.27
2018-09-29 16:00 | 197.81 | 193.46
2018-09-29 16:30 | 199.42 | 195.03
2018-09-29 17:00 | 200.82 | 196.45
2018-09-29 17:30 | 200.54 | 196.23
2018-09-29 18:00 | 201.22 | 197.27
2018-09-29 18:30 | 202.06 | 197.96
2018-09-29 19:00 | 203.02 | 198.97
2018-09-29 19:30 | 201.88 | 197.81
2018-09-29 20:00 | 200.17 | 196.01
2018-09-29 20:30 | 199.03 | 194.8
2018-09-29 21:00 | 197.49 | 193.18
2018-09-29 21:30 | 197.12 | 192.75
2018-09-29 22:00 | 195.92 | 191.48
2018-09-29 22:30 | 194.04 | 189.57
2018-09-29 23:00 | 192.65 | 188.18
2018-09-29 23:30 | 191.95 | 187.41
2018-09-30 | 190.76 | 186.12
2018-09-30 00:30 | 190.08 | 185.54
2018-09-30 01:00 | 188.58 | 184.01
2018-09-30 01:30 | 187.98 | 183.42
2018-09-30 02:00 | 187.53 | 182.96
2018-09-30 02:30 | 187.07 | 182.49
2018-09-30 03:00 | 186.87 | 182.25
2018-09-30 03:30 | 186.6 | 182
2018-09-30 04:00 | 186.39 | 181.84
2018-09-30 04:30 | 186.58 | 181.99
2018-09-30 05:00 | 186.94 | 182.29
2018-09-30 05:30 | 186.44 | 181.69
2018-09-30 06:00 | 186.56 | 181.74
2018-09-30 06:30 | 187.38 | 182.62
2018-09-30 07:00 | 187.14 | 182.45
2018-09-30 07:30 | 187.14 | 182.53
2018-09-30 08:00 | 187.2 | 182.46
2018-09-30 08:30 | 187.11 | 182.37
2018-09-30 09:00 | 185.36 | 180.66
2018-09-30 09:30 | 185.2 | 180.45
2018-09-30 10:00 | 183.4 | 178.8
2018-09-30 10:30 | 183.26 | 178.73
2018-09-30 11:00 | 182.13 | 177.65
2018-09-30 11:30 | 182.09 | 177.62
2018-09-30 12:00 | 182.07 | 177.59
2018-09-30 12:30 | 170.75 | 166.23
2018-09-30 13:00 | 170.46 | 165.8
2018-09-30 13:30 | 171.15 | 166.42
2018-09-30 14:00 | 172.09 | 167.31
2018-09-30 14:30 | 173.75 | 169.26
2018-09-30 15:00 | 179.57 | 175.43
2018-09-30 15:30 | 182.66 | 178.41
2018-09-30 16:00 | 184.83 | 180.64
2018-09-30 16:30 | 186.86 | 182.6
2018-09-30 17:00 | 190.84 | 186.48
2018-09-30 17:30 | 193.62 | 189.35
2018-09-30 18:00 | 194.73 | 190.46
2018-09-30 18:30 | 195.86 | 191.7
2018-09-30 19:00 | 197.11 | 193.03
2018-09-30 19:30 | 195.46 | 191.41
2018-09-30 20:00 | 193.32 | 189.25
2018-09-30 20:30 | 191.84 | 187.73
2018-09-30 21:00 | 191 | 186.88
2018-09-30 21:30 | 189.76 | 185.57
2018-09-30 22:00 | 188.91 | 184.66
2018-09-30 22:30 | 187.39 | 183.06
2018-09-30 23:00 | 185.85 | 181.47
2018-09-30 23:30 | 185.33 | 180.91
2018-10-01 | 184.09 | 179.58
2018-10-01 00:30 | 183.46 | 178.81
2018-10-01 01:00 | 182.52 | 177.78
2018-10-01 01:30 | 182.14 | 177.38
2018-10-01 02:00 | 181.86 | 177.09
2018-10-01 02:30 | 182.15 | 177.3
2018-10-01 03:00 | 182 | 177.16
2018-10-01 03:30 | 181.73 | 176.95
2018-10-01 04:00 | 181.76 | 176.95
2018-10-01 04:30 | 181.87 | 177.06
2018-10-01 05:00 | 181.98 | 177.17
2018-10-01 05:30 | 182.87 | 178.03
2018-10-01 06:00 | 183.52 | 178.69
2018-10-01 06:30 | 184.52 | 179.78
2018-10-01 07:00 | 184.79 | 180.04
2018-10-01 07:30 | 184.38 | 179.77
2018-10-01 08:00 | 184.41 | 179.92
2018-10-01 08:30 | 183.82 | 179.74
2018-10-01 09:00 | 183.24 | 179.09
2018-10-01 09:30 | 181.49 | 177.34
2018-10-01 10:00 | 181.11 | 177.05
2018-10-01 10:30 | 180.99 | 176.9
2018-10-01 11:00 | 180.72 | 176.67
2018-10-01 11:30 | 181.56 | 177.38
2018-10-01 12:00 | 182.42 | 178.07
2018-10-01 12:30 | 183.06 | 178.92
2018-10-01 13:00 | 183.79 | 179.68
2018-10-01 13:30 | 184.76 | 180.6
2018-10-01 14:00 | 185.6 | 181.45
2018-10-01 14:30 | 187.11 | 182.95
2018-10-01 15:00 | 188.78 | 184.61
2018-10-01 15:30 | 191.17 | 186.72
2018-10-01 16:00 | 193.54 | 189.09
2018-10-01 16:30 | 195.84 | 191.33
2018-10-01 17:00 | 197.72 | 193.25
2018-10-01 17:30 | 199.74 | 195.39
2018-10-01 18:00 | 201.42 | 197.04
2018-10-01 18:30 | 203.06 | 198.83
2018-10-01 19:00 | 204.71 | 200.58
2018-10-01 19:30 | 203.29 | 199.13
2018-10-01 20:00 | 201.22 | 196.95
2018-10-01 20:30 | 199.42 | 195.12
2018-10-01 21:00 | 198.29 | 193.85
2018-10-01 21:30 | 197.49 | 192.95
2018-10-01 22:00 | 196.35 | 191.62
2018-10-01 22:30 | 194.49 | 189.58
2018-10-01 23:00 | 193.02 | 188.1
2018-10-01 23:30 | 192.02 | 187.11
2018-10-02 | 190.6 | 185.74
2018-10-02 00:30 | 190.21 | 185.39
2018-10-02 01:00 | 189.06 | 184.35
2018-10-02 01:30 | 188.7 | 183.97
2018-10-02 02:00 | 188.2 | 183.48
2018-10-02 02:30 | 187.86 | 183.09
2018-10-02 03:00 | 187.55 | 182.81
2018-10-02 03:30 | 187.13 | 182.38
2018-10-02 04:00 | 187 | 182.28
2018-10-02 04:30 | 187.25 | 182.56
2018-10-02 05:00 | 187.71 | 183.05
2018-10-02 05:30 | 189.04 | 184.39
2018-10-02 06:00 | 190.09 | 185.65
2018-10-02 06:30 | 191.99 | 187.88
2018-10-02 07:00 | 192.41 | 188.41
2018-10-02 07:30 | 192.97 | 188.88
2018-10-02 08:00 | 191.4 | 187.4
2018-10-02 08:30 | 188.92 | 185.07
2018-10-02 09:00 | 187.08 | 183.32
2018-10-02 09:30 | 185.09 | 181.25
2018-10-02 10:00 | 184.95 | 181.15
2018-10-02 10:30 | 184.97 | 181.15
2018-10-02 11:00 | 185.98 | 181.97
2018-10-02 11:30 | 188.35 | 184.16
2018-10-02 12:00 | 190.6 | 186.41
2018-10-02 12:30 | 191.15 | 186.99
2018-10-02 13:00 | 192.48 | 188.31
2018-10-02 13:30 | 192.76 | 188.6
2018-10-02 14:00 | 193.86 | 190.06
2018-10-02 14:30 | 195.28 | 191.54
2018-10-02 15:00 | 196.75 | 192.83
2018-10-02 15:30 | 198.16 | 194.08
2018-10-02 16:00 | 199.79 | 195.37
2018-10-02 16:30 | 201.37 | 197.02
2018-10-02 17:00 | 202.66 | 198.32
2018-10-02 17:30 | 203 | 198.54
2018-10-02 18:00 | 204.02 | 199.59
2018-10-02 18:30 | 205.38 | 200.96
2018-10-02 19:00 | 206.81 | 202.51
2018-10-02 19:30 | 205.97 | 201.64
2018-10-02 20:00 | 203.4 | 198.95
2018-10-02 20:30 | 202.07 | 197.47
2018-10-02 21:00 | 199.96 | 195.25
2018-10-02 21:30 | 199.14 | 194.29
2018-10-02 22:00 | 197.86 | 192.92
2018-10-02 22:30 | 195.78 | 190.76
2018-10-02 23:00 | 194.34 | 189.23
2018-10-02 23:30 | 193.25 | 188.03
2018-10-03 | 192.09 | 186.84
2018-10-03 00:30 | 192.14 | 186.75
2018-10-03 01:00 | 190.75 | 185.39
2018-10-03 01:30 | 190.22 | 184.87
2018-10-03 02:00 | 189.83 | 184.46
2018-10-03 02:30 | 189.64 | 184.27
2018-10-03 03:00 | 189.15 | 183.88
2018-10-03 03:30 | 188.82 | 183.52
2018-10-03 04:00 | 188.69 | 183.43
2018-10-03 04:30 | 189.28 | 184.03
2018-10-03 05:00 | 189.69 | 184.47
2018-10-03 05:30 | 190.8 | 185.6
2018-10-03 06:00 | 191.77 | 186.55
2018-10-03 06:30 | 193.32 | 188.35
2018-10-03 07:00 | 193.28 | 188.37
2018-10-03 07:30 | 194.09 | 189.53
2018-10-03 08:00 | 193.38 | 189.01
2018-10-03 08:30 | 191.95 | 187.57
2018-10-03 09:00 | 190.74 | 186.3
2018-10-03 09:30 | 189.78 | 185.12
2018-10-03 10:00 | 190.41 | 185.81
2018-10-03 10:30 | 189.48 | 184.93
2018-10-03 11:00 | 190.07 | 185.6
2018-10-03 11:30 | 189.89 | 185.45
2018-10-03 12:00 | 191.47 | 186.96
2018-10-03 12:30 | 191.45 | 186.86
2018-10-03 13:00 | 193.14 | 188.63
2018-10-03 13:30 | 193.8 | 189.37
2018-10-03 14:00 | 195.63 | 191.47
2018-10-03 14:30 | 196.66 | 192.61
2018-10-03 15:00 | 198.45 | 194.15
2018-10-03 15:30 | 199.22 | 194.97
2018-10-03 16:00 | 200.59 | 196.25
2018-10-03 16:30 | 201.65 | 197.05
2018-10-03 17:00 | 203.35 | 198.69
2018-10-03 17:30 | 203.81 | 199.06
2018-10-03 18:00 | 204.52 | 199.7
2018-10-03 18:30 | 206.39 | 201.62
2018-10-03 19:00 | 207.64 | 203.11
2018-10-03 19:30 | 206.46 | 201.87
2018-10-03 20:00 | 203.55 | 198.9
2018-10-03 20:30 | 202.24 | 197.52
2018-10-03 21:00 | 200.33 | 195.54
2018-10-03 21:30 | 199.47 | 194.62
2018-10-03 22:00 | 198.06 | 193.06
2018-10-03 22:30 | 196.11 | 190.93
2018-10-03 23:00 | 194.37 | 189.13
2018-10-03 23:30 | 193.53 | 188.14
2018-10-04 | 192.58 | 187.18
2018-10-04 00:30 | 191.81 | 186.35
2018-10-04 01:00 | 190.88 | 185.4
2018-10-04 01:30 | 190.16 | 184.72
2018-10-04 02:00 | 189.68 | 184.33
2018-10-04 02:30 | 189.47 | 184.1
2018-10-04 03:00 | 189.02 | 183.66
2018-10-04 03:30 | 188.81 | 183.47
2018-10-04 04:00 | 188.66 | 183.28
2018-10-04 04:30 | 188.83 | 183.53
2018-10-04 05:00 | 189.5 | 184.17
2018-10-04 05:30 | 190.42 | 185.16
2018-10-04 06:00 | 192.16 | 187.13
2018-10-04 06:30 | 193.83 | 189.04
2018-10-04 07:00 | 194.94 | 190.24
2018-10-04 07:30 | 195.53 | 191.15
2018-10-04 08:00 | 196.44 | 192.15
2018-10-04 08:30 | 195.57 | 191.4
2018-10-04 09:00 | 195.2 | 191.06
2018-10-04 09:30 | 194.23 | 189.96
2018-10-04 10:00 | 194.58 | 190.34
2018-10-04 10:30 | 193.8 | 189.5
2018-10-04 11:00 | 193.56 | 189.39
2018-10-04 11:30 | 193.76 | 189.38
2018-10-04 12:00 | 195.06 | 190.82
2018-10-04 12:30 | 194.85 | 190.49
2018-10-04 13:00 | 194.22 | 189.7
2018-10-04 13:30 | 194.39 | 189.92
2018-10-04 14:00 | 193.86 | 189.74
2018-10-04 14:30 | 194.53 | 190.21
2018-10-04 15:00 | 195.22 | 190.83
2018-10-04 15:30 | 194.55 | 190.16
2018-10-04 16:00 | 195.95 | 191.65
2018-10-04 16:30 | 197.09 | 192.68
2018-10-04 17:00 | 197.88 | 193.01
2018-10-04 17:30 | 198.94 | 194.14
2018-10-04 18:00 | 200.92 | 196.1
2018-10-04 18:30 | 202.05 | 197.29
2018-10-04 19:00 | 203.75 | 199.05
2018-10-04 19:30 | 203.08 | 198.35
2018-10-04 20:00 | 201.79 | 197.01
2018-10-04 20:30 | 200.57 | 195.7
2018-10-04 21:00 | 198.98 | 194.07
2018-10-04 21:30 | 198.37 | 193.34
2018-10-04 22:00 | 197.33 | 192.2
2018-10-04 22:30 | 195.19 | 190.08
2018-10-04 23:00 | 193.15 | 188.06
2018-10-04 23:30 | 192.99 | 187.73
2018-10-05 | 192.7 | 187.28
2018-10-05 00:30 | 192.53 | 187.13
2018-10-05 01:00 | 191.8 | 186.25
2018-10-05 01:30 | 190.51 | 185.12
2018-10-05 02:00 | 189.67 | 184.2
2018-10-05 02:30 | 189.19 | 183.7
2018-10-05 03:00 | 188.89 | 183.46
2018-10-05 03:30 | 188.86 | 183.43
2018-10-05 04:00 | 189 | 183.53
2018-10-05 04:30 | 189.27 | 183.82
2018-10-05 05:00 | 189.6 | 184.14
2018-10-05 05:30 | 190.76 | 185.35
2018-10-05 06:00 | 192.44 | 187.24
2018-10-05 06:30 | 194.84 | 189.84
2018-10-05 07:00 | 195.32 | 190.47
2018-10-05 07:30 | 195.92 | 191.36
2018-10-05 08:00 | 195.39 | 190.85
2018-10-05 08:30 | 194.08 | 189.56
2018-10-05 09:00 | 193.32 | 188.94
2018-10-05 09:30 | 191.87 | 187.55
2018-10-05 10:00 | 191.1 | 186.91
2018-10-05 10:30 | 191.34 | 187.03
2018-10-05 11:00 | 191.02 | 186.66
2018-10-05 11:30 | 192.98 | 188.59
2018-10-05 12:00 | 193.12 | 188.65
2018-10-05 12:30 | 193.48 | 188.79
2018-10-05 13:00 | 194.21 | 189.49
2018-10-05 13:30 | 194.24 | 189.44
2018-10-05 14:00 | 193.17 | 188.41
2018-10-05 14:30 | 194.24 | 189.52
2018-10-05 15:00 | 193.72 | 188.93
2018-10-05 15:30 | 193.25 | 188.53
2018-10-05 16:00 | 194.69 | 189.96
2018-10-05 16:30 | 195.9 | 191.17
2018-10-05 17:00 | 197.08 | 192.41
2018-10-05 17:30 | 197.73 | 192.94
2018-10-05 18:00 | 198.69 | 193.51
2018-10-05 18:30 | 200.02 | 195.02
2018-10-05 19:00 | 202.14 | 197.23
2018-10-05 19:30 | 201.76 | 196.85
2018-10-05 20:00 | 200.74 | 195.76
2018-10-05 20:30 | 199.82 | 194.78
2018-10-05 21:00 | 199.13 | 194.04
2018-10-05 21:30 | 198.98 | 193.88
2018-10-05 22:00 | 197.72 | 192.56
2018-10-05 22:30 | 196.06 | 190.87
2018-10-05 23:00 | 195.11 | 189.9
2018-10-05 23:30 | 194.72 | 189.41
2018-10-06 | 193.46 | 188.22
2018-10-06 00:30 | 192.93 | 187.71
2018-10-06 01:00 | 191.97 | 186.76
2018-10-06 01:30 | 191.15 | 185.91
2018-10-06 02:00 | 190.44 | 185.26
2018-10-06 02:30 | 190.51 | 185.19
2018-10-06 03:00 | 190.29 | 184.89
2018-10-06 03:30 | 190.48 | 185.07
2018-10-06 04:00 | 190.01 | 184.62
2018-10-06 04:30 | 190.01 | 184.66
2018-10-06 05:00 | 190.33 | 184.94
2018-10-06 05:30 | 190.63 | 185.24
2018-10-06 06:00 | 190.99 | 185.71
2018-10-06 06:30 | 191.42 | 186.18
2018-10-06 07:00 | 191.95 | 186.76
2018-10-06 07:30 | 192.7 | 187.67
2018-10-06 08:00 | 192.95 | 187.97
2018-10-06 08:30 | 192.86 | 187.95
2018-10-06 09:00 | 192.63 | 187.69
2018-10-06 09:30 | 191.63 | 186.85
2018-10-06 10:00 | 190.78 | 186.06
2018-10-06 10:30 | 189.97 | 185.09
2018-10-06 11:00 | 189.02 | 184.2
2018-10-06 11:30 | 188.53 | 183.79
2018-10-06 12:00 | 188.72 | 183.67
2018-10-06 12:30 | 188.5 | 183.45
2018-10-06 13:00 | 189.27 | 184.23
2018-10-06 13:30 | 189.66 | 184.58
2018-10-06 14:00 | 190.51 | 185.36
2018-10-06 14:30 | 190.95 | 185.87
2018-10-06 15:00 | 191.63 | 186.62
2018-10-06 15:30 | 193.22 | 188.27
2018-10-06 16:00 | 194.59 | 189.63
2018-10-06 16:30 | 195.98 | 191
2018-10-06 17:00 | 197.97 | 193.01
2018-10-06 17:30 | 199.29 | 194.4
2018-10-06 18:00 | 200.3 | 195.5
2018-10-06 18:30 | 202.01 | 197.28
2018-10-06 19:00 | 203.13 | 198.59
2018-10-06 19:30 | 202.68 | 198.15
2018-10-06 20:00 | 201.23 | 196.54
2018-10-06 20:30 | 200.04 | 195.28
2018-10-06 21:00 | 199.01 | 194.09
2018-10-06 21:30 | 198.78 | 193.73
2018-10-06 22:00 | 198.01 | 192.88
2018-10-06 22:30 | 196.45 | 191.27
2018-10-06 23:00 | 195 | 189.8
2018-10-06 23:30 | 194.1 | 188.88
2018-10-07 | 193.19 | 187.79
2018-10-07 00:30 | 192.44 | 187.08
2018-10-07 01:00 | 191.95 | 186.59
2018-10-07 01:30 | 191.13 | 185.79
2018-10-07 02:00 | 190.33 | 185.02
2018-10-07 02:30 | 190.06 | 184.87
2018-10-07 03:00 | 189.43 | 184.33
2018-10-07 03:30 | 189.4 | 184.28
2018-10-07 04:00 | 189.57 | 184.24
2018-10-07 04:30 | 189.43 | 184.13
2018-10-07 05:00 | 189.85 | 184.56
2018-10-07 05:30 | 190.5 | 185.22
2018-10-07 06:00 | 190.09 | 184.9
2018-10-07 06:30 | 190.78 | 185.47
2018-10-07 07:00 | 190.9 | 185.57
2018-10-07 07:30 | 191.29 | 186.05
2018-10-07 08:00 | 190.51 | 185.32
2018-10-07 08:30 | 190.07 | 184.88
2018-10-07 09:00 | 189.49 | 184.42
2018-10-07 09:30 | 188.76 | 183.84
2018-10-07 10:00 | 188.56 | 183.76
2018-10-07 10:30 | 188.41 | 183.62
2018-10-07 11:00 | 189.57 | 184.66
2018-10-07 11:30 | 190.08 | 185.16
2018-10-07 12:00 | 190.26 | 185.35
2018-10-07 12:30 | 190.35 | 185.46
2018-10-07 13:00 | 190.59 | 185.65
2018-10-07 13:30 | 191.27 | 186.24
2018-10-07 14:00 | 192.06 | 187.03
2018-10-07 14:30 | 192.19 | 187.34
2018-10-07 15:00 | 192.99 | 188.21
2018-10-07 15:30 | 193.37 | 188.64
2018-10-07 16:00 | 193.77 | 189.19
2018-10-07 16:30 | 196.77 | 192.23
2018-10-07 17:00 | 198.5 | 194.04
2018-10-07 17:30 | 199.96 | 195.6
2018-10-07 18:00 | 200.54 | 196.1
2018-10-07 18:30 | 202 | 197.46
2018-10-07 19:00 | 203.45 | 198.93
2018-10-07 19:30 | 202.78 | 198.22
2018-10-07 20:00 | 200.46 | 195.87
2018-10-07 20:30 | 198.93 | 194.29
2018-10-07 21:00 | 197.5 | 192.83
2018-10-07 21:30 | 197.07 | 192.32
2018-10-07 22:00 | 195.21 | 190.32
2018-10-07 22:30 | 193.46 | 188.43
2018-10-07 23:00 | 191.76 | 186.65
2018-10-07 23:30 | 191.26 | 186.06
2018-10-08 | 190.32 | 185.18
2018-10-08 00:30 | 189.92 | 184.73
2018-10-08 01:00 | 189.11 | 183.89
2018-10-08 01:30 | 188.83 | 183.6
2018-10-08 02:00 | 188.27 | 183.03
2018-10-08 02:30 | 188.01 | 182.76
2018-10-08 03:00 | 188 | 182.73
2018-10-08 03:30 | 187.92 | 182.66
2018-10-08 04:00 | 187.74 | 182.49
2018-10-08 04:30 | 188.1 | 182.86
2018-10-08 05:00 | 188.84 | 183.63
2018-10-08 05:30 | 189.65 | 184.48
2018-10-08 06:00 | 190.21 | 185.25
2018-10-08 06:30 | 192.77 | 188.08
2018-10-08 07:00 | 195.56 | 190.74
2018-10-08 07:30 | 195.93 | 191.29
2018-10-08 08:00 | 195.43 | 190.85
2018-10-08 08:30 | 193.7 | 189.07
2018-10-08 09:00 | 192.81 | 188.14
2018-10-08 09:30 | 191.3 | 186.76
2018-10-08 10:00 | 191.34 | 186.71
2018-10-08 10:30 | 191.42 | 186.74
2018-10-08 11:00 | 194.92 | 190.05
2018-10-08 11:30 | 196.04 | 191.16
2018-10-08 12:00 | 197.18 | 192.37
2018-10-08 12:30 | 197.72 | 192.9
2018-10-08 13:00 | 198.61 | 193.71
2018-10-08 13:30 | 198.96 | 193.94
2018-10-08 14:00 | 199.55 | 194.73
2018-10-08 14:30 | 201.19 | 196.36
2018-10-08 15:00 | 201.93 | 197.08
2018-10-08 15:30 | 203.26 | 198.38
2018-10-08 16:00 | 205.03 | 200.24
2018-10-08 16:30 | 206.88 | 202.07
2018-10-08 17:00 | 207.65 | 202.79
2018-10-08 17:30 | 207.51 | 202.68
2018-10-08 18:00 | 208.4 | 203.65
2018-10-08 18:30 | 210.24 | 205.6
2018-10-08 19:00 | 211.91 | 207.35
2018-10-08 19:30 | 210.94 | 206.37
2018-10-08 20:00 | 208.13 | 203.51
2018-10-08 20:30 | 206.18 | 201.52
2018-10-08 21:00 | 204.66 | 199.8
2018-10-08 21:30 | 203.39 | 198.42
2018-10-08 22:00 | 201.71 | 196.63
2018-10-08 22:30 | 199.59 | 194.52
2018-10-08 23:00 | 197.64 | 192.55
2018-10-08 23:30 | 197.24 | 191.99
2018-10-09 | 195.9 | 190.59
2018-10-09 00:30 | 195.47 | 190.15
2018-10-09 01:00 | 194.78 | 189.46
2018-10-09 01:30 | 194.61 | 189.2
2018-10-09 02:00 | 194.08 | 188.68
2018-10-09 02:30 | 193.66 | 188.26
2018-10-09 03:00 | 193.48 | 188.03
2018-10-09 03:30 | 193.13 | 187.65
2018-10-09 04:00 | 193.17 | 187.62
2018-10-09 04:30 | 192.69 | 187.22
2018-10-09 05:00 | 192.23 | 186.94
2018-10-09 05:30 | 192.77 | 187.65
2018-10-09 06:00 | 194.15 | 189.35
2018-10-09 06:30 | 196.2 | 191.38
2018-10-09 07:00 | 197.27 | 192.16
2018-10-09 07:30 | 197.17 | 192.31
2018-10-09 08:00 | 195.29 | 190.68
2018-10-09 08:30 | 195.8 | 191.11
2018-10-09 09:00 | 194.78 | 190.09
2018-10-09 09:30 | 194.41 | 189.45
2018-10-09 10:00 | 193.28 | 188.01
2018-10-09 10:30 | 193.65 | 188.37
2018-10-09 11:00 | 193.62 | 188.49
2018-10-09 11:30 | 193.6 | 188.68
2018-10-09 12:00 | 193.97 | 189.09
2018-10-09 12:30 | 196.18 | 191.41
2018-10-09 13:00 | 197.2 | 192.5
2018-10-09 13:30 | 196.64 | 191.99
2018-10-09 14:00 | 196.97 | 192.72
2018-10-09 14:30 | 198.9 | 194.5
2018-10-09 15:00 | 201.76 | 197.23
2018-10-09 15:30 | 202.46 | 197.98
2018-10-09 16:00 | 148.27 | 143.18
2018-10-09 16:30 | 176.46 | 173.32
2018-10-09 17:00 | 194.01 | 189.79
2018-10-09 17:30 | 196.62 | 192.29
2018-10-09 18:00 | 200.6 | 196.13
2018-10-09 18:30 | 203.2 | 198.92
2018-10-09 19:00 | 207.82 | 203.53
2018-10-09 19:30 | 206.48 | 202.19
2018-10-09 20:00 | 208.24 | 203.53
2018-10-09 20:30 | 199.78 | 195.79
2018-10-09 21:00 | 188.6 | 184.66
2018-10-09 21:30 | 186.4 | 182.34
2018-10-09 22:00 | 185.83 | 181.8
2018-10-09 22:30 | 187.58 | 183.41
2018-10-09 23:00 | 189.23 | 184.84
2018-10-09 23:30 | 189.98 | 185.33
2018-10-10 | 188.73 | 184.09
2018-10-10 00:30 | 188.12 | 183.56
2018-10-10 01:00 | 187.42 | 182.75
2018-10-10 01:30 | 187.43 | 182.68
2018-10-10 02:00 | 187.23 | 182.47
2018-10-10 02:30 | 187 | 182
2018-10-10 03:00 | 187.03 | 182.05
2018-10-10 03:30 | 185.94 | 181.05
2018-10-10 04:00 | 185.62 | 180.73
2018-10-10 04:30 | 185.96 | 181.09
2018-10-10 05:00 | 186.54 | 181.64
2018-10-10 05:30 | 186.7 | 181.93
2018-10-10 06:00 | 187.43 | 182.95
2018-10-10 06:30 | 190.13 | 185.86
2018-10-10 07:00 | 192.07 | 187.8
2018-10-10 07:30 | 193.63 | 189.34
2018-10-10 08:00 | 193.77 | 189.49
2018-10-10 08:30 | 194.38 | 189.84
2018-10-10 09:00 | 194.96 | 190.37
2018-10-10 09:30 | 195.45 | 190.91
2018-10-10 10:00 | 196.68 | 192.04
2018-10-10 10:30 | 198.36 | 193.58
2018-10-10 11:00 | 200.29 | 195.59
2018-10-10 11:30 | 200.42 | 195.7
2018-10-10 12:00 | 200.2 | 195.55
2018-10-10 12:30 | 200.05 | 195.36
2018-10-10 13:00 | 201.69 | 197.03
2018-10-10 13:30 | 201.18 | 196.57
2018-10-10 14:00 | 201.11 | 196.66
2018-10-10 14:30 | 201.94 | 197.48
2018-10-10 15:00 | 201.86 | 197.29
2018-10-10 15:30 | 202.74 | 198.28
2018-10-10 16:00 | 203.63 | 199.14
2018-10-10 16:30 | 205 | 200.38
2018-10-10 17:00 | 206.65 | 201.96
2018-10-10 17:30 | 206.63 | 201.98
2018-10-10 18:00 | 207.69 | 203.03
2018-10-10 18:30 | 208.95 | 204.38
2018-10-10 19:00 | 210.82 | 206.3
2018-10-10 19:30 | 209.29 | 204.81
2018-10-10 20:00 | 207.52 | 202.93
2018-10-10 20:30 | 205.56 | 200.82
2018-10-10 21:00 | 203.67 | 198.48
2018-10-10 21:30 | 202.92 | 197.68
2018-10-10 22:00 | 200.97 | 195.71
2018-10-10 22:30 | 198.6 | 193.28
2018-10-10 23:00 | 196.84 | 191.44
2018-10-10 23:30 | 196.18 | 190.67
2018-10-11 | 195.04 | 189.38
2018-10-11 00:30 | 194.38 | 188.92
2018-10-11 01:00 | 193.57 | 187.96
2018-10-11 01:30 | 193.07 | 187.47
2018-10-11 02:00 | 192.54 | 186.99
2018-10-11 02:30 | 192 | 186.5
2018-10-11 03:00 | 191.39 | 185.89
2018-10-11 03:30 | 191.03 | 185.52
2018-10-11 04:00 | 191.19 | 185.65
2018-10-11 04:30 | 191.43 | 185.92
2018-10-11 05:00 | 191.82 | 186.32
2018-10-11 05:30 | 193.39 | 188.05
2018-10-11 06:00 | 195.09 | 189.9
2018-10-11 06:30 | 197.11 | 192.03
2018-10-11 07:00 | 198.45 | 193.47
2018-10-11 07:30 | 198.8 | 193.84
2018-10-11 08:00 | 198.42 | 193.59
2018-10-11 08:30 | 197.07 | 192.23
2018-10-11 09:00 | 195.91 | 191.04
2018-10-11 09:30 | 195.33 | 190.49
2018-10-11 10:00 | 196.26 | 191.34
2018-10-11 10:30 | 195.39 | 190.39
2018-10-11 11:00 | 196.2 | 191.31
2018-10-11 11:30 | 196.39 | 191.59
2018-10-11 12:00 | 197.43 | 192.7
2018-10-11 12:30 | 196.63 | 192.04
2018-10-11 13:00 | 197.95 | 193.34
2018-10-11 13:30 | 194.74 | 190.41
2018-10-11 14:00 | 194.66 | 190.56
2018-10-11 14:30 | 195.49 | 191.42
2018-10-11 15:00 | 196.08 | 191.98
2018-10-11 15:30 | 200.16 | 195.8
2018-10-11 16:00 | 203.08 | 198.54
2018-10-11 16:30 | 204.57 | 199.91
2018-10-11 17:00 | 206.27 | 201.6
2018-10-11 17:30 | 206.88 | 202.19
2018-10-11 18:00 | 208.04 | 203.28
2018-10-11 18:30 | 193.43 | 189.4
2018-10-11 19:00 | 179.52 | 176.03
2018-10-11 19:30 | 200.73 | 198.82
2018-10-11 20:00 | 211.73 | 210.29
2018-10-11 20:30 | 204.85 | 200.98
2018-10-11 21:00 | 203.32 | 198.4
2018-10-11 21:30 | 202.65 | 197.67
2018-10-11 22:00 | 201.05 | 195.97
2018-10-11 22:30 | 199.58 | 194.33
2018-10-11 23:00 | 197.71 | 192.46
2018-10-11 23:30 | 196.81 | 191.51
2018-10-12 | 195.89 | 190.53
2018-10-12 00:30 | 195.3 | 189.95
2018-10-12 01:00 | 194.19 | 188.94
2018-10-12 01:30 | 193.58 | 188.32
2018-10-12 02:00 | 192.9 | 187.68
2018-10-12 02:30 | 192.3 | 187.09
2018-10-12 03:00 | 192.12 | 186.92
2018-10-12 03:30 | 192.61 | 187.37
2018-10-12 04:00 | 192.5 | 187.29
2018-10-12 04:30 | 192.77 | 187.52
2018-10-12 05:00 | 193.54 | 188.23
2018-10-12 05:30 | 195.19 | 189.88
2018-10-12 06:00 | 197.18 | 191.84
2018-10-12 06:30 | 199.79 | 194.63
2018-10-12 07:00 | 201.69 | 196.58
2018-10-12 07:30 | 202.69 | 197.59
2018-10-12 08:00 | 203.6 | 198.6
2018-10-12 08:30 | 203.42 | 198.49
2018-10-12 09:00 | 202.46 | 197.55
2018-10-12 09:30 | 200.58 | 195.73
2018-10-12 10:00 | 200.91 | 196.1
2018-10-12 10:30 | 199.8 | 194.85
2018-10-12 11:00 | 199.91 | 195.05
2018-10-12 11:30 | 199.98 | 195.13
2018-10-12 12:00 | 200.21 | 195.35
2018-10-12 12:30 | 199.9 | 194.99
2018-10-12 13:00 | 200.36 | 195.42
2018-10-12 13:30 | 199.33 | 194.38
2018-10-12 14:00 | 199.41 | 194.46
2018-10-12 14:30 | 199.96 | 195.03
2018-10-12 15:00 | 199.65 | 194.74
2018-10-12 15:30 | 199.47 | 194.62
2018-10-12 16:00 | 201.08 | 196.23
2018-10-12 16:30 | 201.71 | 196.84
2018-10-12 17:00 | 202.32 | 197.49
2018-10-12 17:30 | 203.61 | 198.77
2018-10-12 18:00 | 203.6 | 198.62
2018-10-12 18:30 | 204.32 | 199.39
2018-10-12 19:00 | 205.05 | 200.12
2018-10-12 19:30 | 204.1 | 199.17
2018-10-12 20:00 | 202.94 | 198
2018-10-12 20:30 | 202.05 | 196.92
2018-10-12 21:00 | 200.84 | 195.67
2018-10-12 21:30 | 200.69 | 195.37
2018-10-12 22:00 | 200.13 | 194.79
2018-10-12 22:30 | 198.08 | 192.76
2018-10-12 23:00 | 197.11 | 191.65
2018-10-12 23:30 | 196.75 | 191.17
2018-10-13 | 195.32 | 189.8
2018-10-13 00:30 | 194.29 | 188.8
2018-10-13 01:00 | 193.4 | 187.92
2018-10-13 01:30 | 192.23 | 186.79
2018-10-13 02:00 | 192 | 186.57
2018-10-13 02:30 | 192.23 | 186.57
2018-10-13 03:00 | 192.41 | 186.63
2018-10-13 03:30 | 191.37 | 185.92
2018-10-13 04:00 | 191.4 | 185.88
2018-10-13 04:30 | 191.26 | 185.71
2018-10-13 05:00 | 191.36 | 185.87
2018-10-13 05:30 | 191.68 | 186.23
2018-10-13 06:00 | 192.18 | 186.72
2018-10-13 06:30 | 192.84 | 187.43
2018-10-13 07:00 | 195.89 | 190.35
2018-10-13 07:30 | 197.06 | 191.51
2018-10-13 08:00 | 194.29 | 188.82
2018-10-13 08:30 | 192.86 | 187.84
2018-10-13 09:00 | 193.7 | 188.59
2018-10-13 09:30 | 193.96 | 188.8
2018-10-13 10:00 | 193.66 | 188.53
2018-10-13 10:30 | 193.32 | 188.19
2018-10-13 11:00 | 192.52 | 187.47
2018-10-13 11:30 | 193.03 | 187.92
2018-10-13 12:00 | 193.33 | 188.18
2018-10-13 12:30 | 193.74 | 188.59
2018-10-13 13:00 | 192.74 | 187.58
2018-10-13 13:30 | 193.33 | 188.12
2018-10-13 14:00 | 193.17 | 188.04
2018-10-13 14:30 | 193.59 | 188.52
2018-10-13 15:00 | 195.14 | 189.84
2018-10-13 15:30 | 196.26 | 190.98
2018-10-13 16:00 | 197.48 | 192.11
2018-10-13 16:30 | 198.34 | 192.79
2018-10-13 17:00 | 199.06 | 193.57
2018-10-13 17:30 | 200.12 | 194.86
2018-10-13 18:00 | 201.47 | 196.29
2018-10-13 18:30 | 202.41 | 197.4
2018-10-13 19:00 | 203.93 | 198.98
2018-10-13 19:30 | 202.56 | 197.59
2018-10-13 20:00 | 201.53 | 196.5
2018-10-13 20:30 | 200.1 | 194.99
2018-10-13 21:00 | 198.75 | 193.5
2018-10-13 21:30 | 198.44 | 193.08
2018-10-13 22:00 | 197.67 | 192.25
2018-10-13 22:30 | 196.21 | 190.78
2018-10-13 23:00 | 194.83 | 189.36
2018-10-13 23:30 | 194.31 | 188.84
2018-10-14 | 193.27 | 187.72
2018-10-14 00:30 | 192.74 | 187.19
2018-10-14 01:00 | 191.91 | 186.24
2018-10-14 01:30 | 191.2 | 185.56
2018-10-14 02:00 | 191.09 | 185.41
2018-10-14 02:30 | 191.34 | 185.64
2018-10-14 03:00 | 190.8 | 185.14
2018-10-14 03:30 | 190.76 | 185.06
2018-10-14 04:00 | 190.42 | 184.84
2018-10-14 04:30 | 190.23 | 184.65
2018-10-14 05:00 | 190.18 | 184.59
2018-10-14 05:30 | 190.93 | 185.32
2018-10-14 06:00 | 191.33 | 185.63
2018-10-14 06:30 | 191.48 | 185.84
2018-10-14 07:00 | 191.84 | 186.3
2018-10-14 07:30 | 191.83 | 186.48
2018-10-14 08:00 | 192.56 | 187.15
2018-10-14 08:30 | 191.51 | 186.36
2018-10-14 09:00 | 190.08 | 185.28
2018-10-14 09:30 | 190.82 | 186.13
2018-10-14 10:00 | 190.31 | 185.64
2018-10-14 10:30 | 189.44 | 184.7
2018-10-14 11:00 | 189.23 | 184.32
2018-10-14 11:30 | 189.35 | 184.51
2018-10-14 12:00 | 189.44 | 184.71
2018-10-14 12:30 | 189.29 | 184.51
2018-10-14 13:00 | 189.51 | 184.69
2018-10-14 13:30 | 190.39 | 185.49
2018-10-14 14:00 | 190.56 | 185.67
2018-10-14 14:30 | 191.19 | 186.33
2018-10-14 15:00 | 191.78 | 187
2018-10-14 15:30 | 192.55 | 187.89
2018-10-14 16:00 | 193.46 | 188.84
2018-10-14 16:30 | 195.67 | 191.02
2018-10-14 17:00 | 195.59 | 191.05
2018-10-14 17:30 | 195.57 | 191.29
2018-10-14 18:00 | 196.12 | 191.8
2018-10-14 18:30 | 201.76 | 198.76
2018-10-14 19:00 | 212.84 | 211.61
2018-10-14 19:30 | 212.96 | 211.73
2018-10-14 20:00 | 214.6 | 213.41
2018-10-14 20:30 | 201.56 | 197.68
2018-10-14 21:00 | 200.14 | 195.06
2018-10-14 21:30 | 199.44 | 194.21
2018-10-14 22:00 | 198.23 | 192.82
2018-10-14 22:30 | 196.28 | 190.75
2018-10-14 23:00 | 194.94 | 189.32
2018-10-14 23:30 | 194.09 | 188.6
2018-10-15 | 192.74 | 187.33
2018-10-15 00:30 | 192.34 | 186.9
2018-10-15 01:00 | 191.69 | 186.15
2018-10-15 01:30 | 191.2 | 185.47
2018-10-15 02:00 | 190.55 | 184.86
2018-10-15 02:30 | 190.01 | 184.32
2018-10-15 03:00 | 189.72 | 183.98
2018-10-15 03:30 | 189.82 | 184.1
2018-10-15 04:00 | 190.05 | 184.28
2018-10-15 04:30 | 190.45 | 184.72
2018-10-15 05:00 | 191.33 | 185.6
2018-10-15 05:30 | 192.01 | 186.61
2018-10-15 06:00 | 192.52 | 187.4
2018-10-15 06:30 | 194.87 | 189.97
2018-10-15 07:00 | 197.04 | 192.02
2018-10-15 07:30 | 197.51 | 192.68
2018-10-15 08:00 | 196.07 | 191.4
2018-10-15 08:30 | 194.27 | 189.47
2018-10-15 09:00 | 192.53 | 187.73
2018-10-15 09:30 | 191.38 | 186.59
2018-10-15 10:00 | 192.08 | 187.21
2018-10-15 10:30 | 192.24 | 187.36
2018-10-15 11:00 | 192.34 | 187.52
2018-10-15 11:30 | 193.45 | 188.6
2018-10-15 12:00 | 194.11 | 189.2
2018-10-15 12:30 | 194.63 | 189.68
2018-10-15 13:00 | 196.07 | 191.04
2018-10-15 13:30 | 197.2 | 192.13
2018-10-15 14:00 | 198.83 | 194
2018-10-15 14:30 | 199.98 | 195.25
2018-10-15 15:00 | 200.31 | 195.62
2018-10-15 15:30 | 200.75 | 196.13
2018-10-15 16:00 | 202.52 | 198.02
2018-10-15 16:30 | 202.89 | 198.47
2018-10-15 17:00 | 204.03 | 201.19
2018-10-15 17:30 | 209.34 | 208.23
2018-10-15 18:00 | 207.54 | 206.46
2018-10-15 18:30 | 207.14 | 206.08
2018-10-15 19:00 | 206.46 | 205.42
2018-10-15 19:30 | 207.29 | 206.31
2018-10-15 20:00 | 201.37 | 198.07
2018-10-15 20:30 | 202.22 | 198.03
2018-10-15 21:00 | 200.38 | 196.08
2018-10-15 21:30 | 199.46 | 195.02
2018-10-15 22:00 | 197.84 | 193.22
2018-10-15 22:30 | 195.37 | 190.68
2018-10-15 23:00 | 194.11 | 189.37
2018-10-15 23:30 | 192.94 | 188.15
2018-10-16 | 191.58 | 186.55
2018-10-16 00:30 | 190.84 | 185.77
2018-10-16 01:00 | 190.6 | 185.73
2018-10-16 01:30 | 189.67 | 184.91
2018-10-16 02:00 | 189.23 | 184.32
2018-10-16 02:30 | 188.61 | 183.64
2018-10-16 03:00 | 188.59 | 183.62
2018-10-16 03:30 | 188.4 | 183.43
2018-10-16 04:00 | 188.42 | 183.46
2018-10-16 04:30 | 188.88 | 183.91
2018-10-16 05:00 | 189.47 | 184.5
2018-10-16 05:30 | 190.47 | 185.55
2018-10-16 06:00 | 191.52 | 186.91
2018-10-16 06:30 | 193.92 | 189.32
2018-10-16 07:00 | 195.24 | 190.6
2018-10-16 07:30 | 195.95 | 191.42
2018-10-16 08:00 | 195.26 | 190.61
2018-10-16 08:30 | 193.93 | 189.26
2018-10-16 09:00 | 191.28 | 186.8
2018-10-16 09:30 | 177.83 | 173.89
2018-10-16 10:00 | 175.7 | 171.79
2018-10-16 10:30 | 175.69 | 171.79
2018-10-16 11:00 | 174.59 | 170.76
2018-10-16 11:30 | 174.87 | 171.08
2018-10-16 12:00 | 175.79 | 172.04
2018-10-16 12:30 | 177.22 | 173.51
2018-10-16 13:00 | 178.4 | 174.68
2018-10-16 13:30 | 179.34 | 175.63
2018-10-16 14:00 | 179.72 | 176.1
2018-10-16 14:30 | 180.78 | 177.2
2018-10-16 15:00 | 181.02 | 177.47
2018-10-16 15:30 | 181.6 | 178.08
2018-10-16 16:00 | 180.7 | 177.5
2018-10-16 16:30 | 190.05 | 189.4
2018-10-16 17:00 | 189.45 | 188.86
2018-10-16 17:30 | 190.13 | 189.54
2018-10-16 18:00 | 198.51 | 197.72
2018-10-16 18:30 | 199.45 | 198.76
2018-10-16 19:00 | 198.69 | 197.99
2018-10-16 19:30 | 200.21 | 199.54
2018-10-16 20:00 | 201.83 | 201.15
2018-10-16 20:30 | 203.12 | 202.42
2018-10-16 21:00 | 206.6 | 205.84
2018-10-16 21:30 | 209.84 | 208.99
2018-10-16 22:00 | 197.92 | 194.57
2018-10-16 22:30 | 195.9 | 191.33
2018-10-16 23:00 | 194.73 | 190.04
2018-10-16 23:30 | 194.76 | 189.96
2018-10-17 | 193.88 | 188.95
2018-10-17 00:30 | 193.25 | 188.3
2018-10-17 01:00 | 192.44 | 187.4
2018-10-17 01:30 | 191.79 | 186.75
2018-10-17 02:00 | 190.65 | 185.73
2018-10-17 02:30 | 190.59 | 185.67
2018-10-17 03:00 | 190.39 | 185.44
2018-10-17 03:30 | 189.65 | 184.67
2018-10-17 04:00 | 189.27 | 184.28
2018-10-17 04:30 | 189.66 | 184.66
2018-10-17 05:00 | 189.93 | 185
2018-10-17 05:30 | 190.51 | 185.44
2018-10-17 06:00 | 191.74 | 186.86
2018-10-17 06:30 | 193.99 | 189.37
2018-10-17 07:00 | 194.57 | 190.05
2018-10-17 07:30 | 195.19 | 190.6
2018-10-17 08:00 | 194.92 | 190.37
2018-10-17 08:30 | 193.21 | 188.75
2018-10-17 09:00 | 192 | 187.61
2018-10-17 09:30 | 190.47 | 185.98
2018-10-17 10:00 | 191.58 | 187.09
2018-10-17 10:30 | 191.08 | 187.04
2018-10-17 11:00 | 193.09 | 189.1
2018-10-17 11:30 | 194.54 | 190.49
2018-10-17 12:00 | 195.54 | 191.48
2018-10-17 12:30 | 196.26 | 192.34
2018-10-17 13:00 | 198.86 | 194.92
2018-10-17 13:30 | 199.34 | 195.48
2018-10-17 14:00 | 200.68 | 197
2018-10-17 14:30 | 202.09 | 198.5
2018-10-17 15:00 | 203.35 | 199.77
2018-10-17 15:30 | 202.36 | 198.64
2018-10-17 16:00 | 202.33 | 198.66
2018-10-17 16:30 | 204 | 201.77
2018-10-17 17:00 | 211.49 | 210.56
2018-10-17 17:30 | 212.09 | 211.11
2018-10-17 18:00 | 211.34 | 210.36
2018-10-17 18:30 | 211.26 | 210.26
2018-10-17 19:00 | 210.82 | 209.81
2018-10-17 19:30 | 212.3 | 211.21
2018-10-17 20:00 | 213 | 211.91
2018-10-17 20:30 | 213.2 | 212.08
2018-10-17 21:00 | 213.11 | 211.99
2018-10-17 21:30 | 214.7 | 213.64
2018-10-17 22:00 | 217.23 | 216.14
2018-10-17 22:30 | 218.57 | 217.38
2018-10-17 23:00 | 198.13 | 194.43
2018-10-17 23:30 | 195.29 | 190.43
2018-10-18 | 194.09 | 189.23
2018-10-18 00:30 | 193.71 | 188.81
2018-10-18 01:00 | 192.49 | 187.8
2018-10-18 01:30 | 191.69 | 186.97
2018-10-18 02:00 | 191.02 | 186.29
2018-10-18 02:30 | 190.76 | 185.91
2018-10-18 03:00 | 190.32 | 185.45
2018-10-18 03:30 | 189.25 | 184.33
2018-10-18 04:00 | 189.65 | 184.72
2018-10-18 04:30 | 189.81 | 184.9
2018-10-18 05:00 | 190.11 | 185.19
2018-10-18 05:30 | 191.3 | 186.34
2018-10-18 06:00 | 192.25 | 187.62
2018-10-18 06:30 | 209.97 | 208.37
2018-10-18 07:00 | 218.97 | 218.03
2018-10-18 07:30 | 189.08 | 186.45
2018-10-18 08:00 | 194.73 | 190.67
2018-10-18 08:30 | 193.94 | 189.84
2018-10-18 09:00 | 192.47 | 188.34
2018-10-18 09:30 | 191.17 | 186.99
2018-10-18 10:00 | 192.07 | 187.88
2018-10-18 10:30 | 192.57 | 188.43
2018-10-18 11:00 | 193.46 | 189.42
2018-10-18 11:30 | 194.56 | 190.48
2018-10-18 12:00 | 195.4 | 191.39
2018-10-18 12:30 | 197 | 192.86
2018-10-18 13:00 | 198.87 | 194.77
2018-10-18 13:30 | 199.24 | 195.25
2018-10-18 14:00 | 199.88 | 195.96
2018-10-18 14:30 | 200.63 | 196.75
2018-10-18 15:00 | 201.66 | 197.81
2018-10-18 15:30 | 201.64 | 197.84
2018-10-18 16:00 | 203.63 | 199.83
2018-10-18 16:30 | 204 | 199.92
2018-10-18 17:00 | 202.96 | 199.71
2018-10-18 17:30 | 209.81 | 208.85
2018-10-18 18:00 | 209.04 | 208.13
2018-10-18 18:30 | 209.38 | 208.49
2018-10-18 19:00 | 208.74 | 207.83
2018-10-18 19:30 | 210.07 | 209.15
2018-10-18 20:00 | 213.64 | 212.77
2018-10-18 20:30 | 215.47 | 214.58
2018-10-18 21:00 | 216.08 | 215.19
2018-10-18 21:30 | 216.21 | 215.29
2018-10-18 22:00 | 200.87 | 197.29
2018-10-18 22:30 | 198.01 | 193.42
2018-10-18 23:00 | 196.49 | 191.87
2018-10-18 23:30 | 195.39 | 190.73
2018-10-19 | 194.07 | 189.49
2018-10-19 00:30 | 193.19 | 188.61
2018-10-19 01:00 | 192.18 | 187.66
2018-10-19 01:30 | 191.7 | 187.1
2018-10-19 02:00 | 191.52 | 186.83
2018-10-19 02:30 | 191.17 | 186.46
2018-10-19 03:00 | 191.22 | 186.49
2018-10-19 03:30 | 190.91 | 186.19
2018-10-19 04:00 | 190.78 | 186.01
2018-10-19 04:30 | 190.65 | 185.88
2018-10-19 05:00 | 190.99 | 186.25
2018-10-19 05:30 | 191.9 | 187.23
2018-10-19 06:00 | 192.81 | 188.33
2018-10-19 06:30 | 194.61 | 190.25
2018-10-19 07:00 | 195.54 | 191.2
2018-10-19 07:30 | 196.13 | 191.9
2018-10-19 08:00 | 196.2 | 191.96
2018-10-19 08:30 | 195 | 190.76
2018-10-19 09:00 | 194.28 | 190.04
2018-10-19 09:30 | 194.09 | 189.75
2018-10-19 10:00 | 193.86 | 189.73
2018-10-19 10:30 | 192.86 | 188.83
2018-10-19 11:00 | 194.19 | 190.2
2018-10-19 11:30 | 194.67 | 190.66
2018-10-19 12:00 | 196.3 | 192.29
2018-10-19 12:30 | 197.35 | 193.19
2018-10-19 13:00 | 198.86 | 194.79
2018-10-19 13:30 | 199.35 | 195.26
2018-10-19 14:00 | 200.18 | 196.21
2018-10-19 14:30 | 201.45 | 197.65
2018-10-19 15:00 | 202.41 | 198.54
2018-10-19 15:30 | 202.83 | 198.95
2018-10-19 16:00 | 204.76 | 200.88
2018-10-19 16:30 | 205.74 | 201.96
2018-10-19 17:00 | 207.55 | 203.7
2018-10-19 17:30 | 208.1 | 204.13
2018-10-19 18:00 | 207.9 | 203.99
2018-10-19 18:30 | 208.2 | 204.3
2018-10-19 19:00 | 208.88 | 204.99
2018-10-19 19:30 | 208.65 | 204.78
2018-10-19 20:00 | 206.86 | 202.94
2018-10-19 20:30 | 205.15 | 201.18
2018-10-19 21:00 | 203.36 | 199.35
2018-10-19 21:30 | 202.83 | 198.65
2018-10-19 22:00 | 201.57 | 197.35
2018-10-19 22:30 | 199.63 | 195.33
2018-10-19 23:00 | 198.44 | 194.03
2018-10-19 23:30 | 197.45 | 192.92
2018-10-20 | 196.17 | 191.75
2018-10-20 00:30 | 196.29 | 191.67
2018-10-20 01:00 | 195.05 | 190.39
2018-10-20 01:30 | 194.51 | 189.85
2018-10-20 02:00 | 193.8 | 189.13
2018-10-20 02:30 | 193.69 | 189.01
2018-10-20 03:00 | 193.13 | 188.46
2018-10-20 03:30 | 192.93 | 188.26
2018-10-20 04:00 | 193.15 | 188.47
2018-10-20 04:30 | 193.22 | 188.51
2018-10-20 05:00 | 193.34 | 188.64
2018-10-20 05:30 | 193.6 | 188.92
2018-10-20 06:00 | 193.85 | 189.19
2018-10-20 06:30 | 194.43 | 189.72
2018-10-20 07:00 | 194.62 | 190.15
2018-10-20 07:30 | 194.34 | 190.02
2018-10-20 08:00 | 193.58 | 189.17
2018-10-20 08:30 | 191.33 | 186.92
2018-10-20 09:00 | 191.21 | 186.7
2018-10-20 09:30 | 191.49 | 187.02
2018-10-20 10:00 | 192.1 | 187.68
2018-10-20 10:30 | 192.52 | 188.1
2018-10-20 11:00 | 193.18 | 188.78
2018-10-20 11:30 | 194.58 | 190.17
2018-10-20 12:00 | 196.44 | 191.97
2018-10-20 12:30 | 196.4 | 192.01
2018-10-20 13:00 | 197.38 | 193.11
2018-10-20 13:30 | 198.39 | 194.24
2018-10-20 14:00 | 199.16 | 195.15
2018-10-20 14:30 | 202.17 | 197.99
2018-10-20 15:00 | 204.56 | 200.19
2018-10-20 15:30 | 204.84 | 200.74
2018-10-20 16:00 | 205.29 | 201.13
2018-10-20 16:30 | 203.64 | 199.26
2018-10-20 17:00 | 206.28 | 201.82
2018-10-20 17:30 | 206.57 | 202.19
2018-10-20 18:00 | 207.39 | 203.11
2018-10-20 18:30 | 209.95 | 208.69
2018-10-20 19:00 | 212.93 | 211.95
2018-10-20 19:30 | 216 | 215
2018-10-20 20:00 | 216.56 | 215.61
2018-10-20 20:30 | 216.77 | 215.8
2018-10-20 21:00 | 217.54 | 216.51
2018-10-20 21:30 | 216.25 | 215.2
2018-10-20 22:00 | 215.97 | 214.96
2018-10-20 22:30 | 198.88 | 194.69
2018-10-20 23:00 | 194.92 | 189.9
2018-10-20 23:30 | 195.46 | 190.61
2018-10-21 | 194.25 | 189.32
2018-10-21 00:30 | 193.54 | 188.69
2018-10-21 01:00 | 192.58 | 187.85
2018-10-21 01:30 | 192 | 187.07
2018-10-21 02:00 | 191.6 | 186.67
2018-10-21 02:30 | 191.4 | 186.45
2018-10-21 03:00 | 190.96 | 186.02
2018-10-21 03:30 | 190.36 | 185.41
2018-10-21 04:00 | 190.43 | 185.48
2018-10-21 04:30 | 190.62 | 185.68
2018-10-21 05:00 | 190.64 | 185.71
2018-10-21 05:30 | 191.33 | 186.38
2018-10-21 06:00 | 190.95 | 185.95
2018-10-21 06:30 | 191.38 | 186.42
2018-10-21 07:00 | 191.61 | 186.7
2018-10-21 07:30 | 192.1 | 187.38
2018-10-21 08:00 | 192.55 | 187.94
2018-10-21 08:30 | 191.86 | 187.2
2018-10-21 09:00 | 191.44 | 186.72
2018-10-21 09:30 | 191.02 | 186.17
2018-10-21 10:00 | 191.23 | 186.46
2018-10-21 10:30 | 191.4 | 186.57
2018-10-21 11:00 | 191.16 | 186.44
2018-10-21 11:30 | 190.84 | 186.36
2018-10-21 12:00 | 190.62 | 186.13
2018-10-21 12:30 | 190.85 | 186.37
2018-10-21 13:00 | 191.94 | 187.45
2018-10-21 13:30 | 193.07 | 188.51
2018-10-21 14:00 | 193.76 | 189.2
2018-10-21 14:30 | 194.29 | 189.72
2018-10-21 15:00 | 194.36 | 189.77
2018-10-21 15:30 | 195.56 | 190.99
2018-10-21 16:00 | 196.45 | 191.93
2018-10-21 16:30 | 198.37 | 193.98
2018-10-21 17:00 | 200.21 | 195.83
2018-10-21 17:30 | 201.31 | 196.87
2018-10-21 18:00 | 202.65 | 198.26
2018-10-21 18:30 | 203.35 | 199.06
2018-10-21 19:00 | 204.59 | 200.51
2018-10-21 19:30 | 203.21 | 200
2018-10-21 20:00 | 213.47 | 212.51
2018-10-21 20:30 | 213.84 | 212.92
2018-10-21 21:00 | 214.81 | 213.85
2018-10-21 21:30 | 215.09 | 214.09
2018-10-21 22:00 | 214.76 | 213.85
2018-10-21 22:30 | 215.73 | 214.73
2018-10-21 23:00 | 194.77 | 190.96
2018-10-21 23:30 | 191.62 | 186.78
2018-10-22 | 190.49 | 185.7
2018-10-22 00:30 | 189.91 | 185.14
2018-10-22 01:00 | 189.15 | 184.32
2018-10-22 01:30 | 188.51 | 183.7
2018-10-22 02:00 | 188.33 | 183.55
2018-10-22 02:30 | 187.94 | 183.17
2018-10-22 03:00 | 187.84 | 183.1
2018-10-22 03:30 | 187.5 | 182.76
2018-10-22 04:00 | 187.83 | 183.1
2018-10-22 04:30 | 188.19 | 183.48
2018-10-22 05:00 | 188.59 | 183.86
2018-10-22 05:30 | 189.3 | 184.58
2018-10-22 06:00 | 190.54 | 185.92
2018-10-22 06:30 | 191.81 | 187.57
2018-10-22 07:00 | 193.5 | 189.2
2018-10-22 07:30 | 185.13 | 181.11
2018-10-22 08:00 | 179.01 | 174.81
2018-10-22 08:30 | 178.87 | 174.88
2018-10-22 09:00 | 179.76 | 175.97
2018-10-22 09:30 | 179.4 | 175.62
2018-10-22 10:00 | 180.65 | 176.59
2018-10-22 10:30 | 180.88 | 176.91
2018-10-22 11:00 | 187.85 | 183.99
2018-10-22 11:30 | 195.03 | 190.69
2018-10-22 12:00 | 198.57 | 194.05
2018-10-22 12:30 | 198.29 | 193.84
2018-10-22 13:00 | 198.82 | 194.72
2018-10-22 13:30 | 199.58 | 195.6
2018-10-22 14:00 | 200.81 | 196.84
2018-10-22 14:30 | 202.3 | 198.34
2018-10-22 15:00 | 203.24 | 199.24
2018-10-22 15:30 | 204.07 | 200.08
2018-10-22 16:00 | 197.88 | 193.53
2018-10-22 16:30 | 193.85 | 192.38
2018-10-22 17:00 | 186.57 | 185.08
2018-10-22 17:30 | 179.93 | 178.25
2018-10-22 18:00 | 178.56 | 176.76
2018-10-22 18:30 | 179.66 | 177.86
2018-10-22 19:00 | 180.22 | 178.39
2018-10-22 19:30 | 181.49 | 179.63
2018-10-22 20:00 | 183 | 181.14
2018-10-22 20:30 | 184.21 | 182.33
2018-10-22 21:00 | 186.05 | 184.09
2018-10-22 21:30 | 176.3 | 171.17
2018-10-22 22:00 | 174.71 | 167.87
2018-10-22 22:30 | 173.21 | 166.17
2018-10-22 23:00 | 171.27 | 164.24
2018-10-22 23:30 | 170.42 | 163.3
2018-10-23 | 169.18 | 162.22
2018-10-23 00:30 | 184.27 | 178.91
2018-10-23 01:00 | 194.37 | 189.57
2018-10-23 01:30 | 193.66 | 188.84
2018-10-23 02:00 | 193.21 | 188.34
2018-10-23 02:30 | 192.74 | 187.8
2018-10-23 03:00 | 192.7 | 187.57
2018-10-23 03:30 | 192.12 | 187.01
2018-10-23 04:00 | 192.3 | 187.19
2018-10-23 04:30 | 192.56 | 187.46
2018-10-23 05:00 | 192.73 | 187.67
2018-10-23 05:30 | 193.76 | 188.88
2018-10-23 06:00 | 194.69 | 190.06
2018-10-23 06:30 | 197.25 | 192.61
2018-10-23 07:00 | 197.98 | 193.3
2018-10-23 07:30 | 198.76 | 194.25
2018-10-23 08:00 | 198.57 | 194
2018-10-23 08:30 | 197.52 | 192.83
2018-10-23 09:00 | 196.53 | 191.81
2018-10-23 09:30 | 195.41 | 190.64
2018-10-23 10:00 | 196.87 | 192.21
2018-10-23 10:30 | 197.93 | 193.43
2018-10-23 11:00 | 198.79 | 194.37
2018-10-23 11:30 | 199.61 | 195.16
2018-10-23 12:00 | 200.84 | 196.46
2018-10-23 12:30 | 201.38 | 196.98
2018-10-23 13:00 | 203.12 | 198.67
2018-10-23 13:30 | 203.83 | 199.36
2018-10-23 14:00 | 204.93 | 200.56
2018-10-23 14:30 | 206.35 | 202.03
2018-10-23 15:00 | 207.38 | 202.99
2018-10-23 15:30 | 208.23 | 203.97
2018-10-23 16:00 | 210 | 205.92
2018-10-23 16:30 | 212.22 | 208.13
2018-10-23 17:00 | 214.37 | 210.36
2018-10-23 17:30 | 215.05 | 211.12
2018-10-23 18:00 | 216.42 | 212.6
2018-10-23 18:30 | 216.89 | 213.12
2018-10-23 19:00 | 209.93 | 207.26
2018-10-23 19:30 | 185.53 | 184.28
2018-10-23 20:00 | 177.29 | 175.65
2018-10-23 20:30 | 179.79 | 175.04
2018-10-23 21:00 | 180.34 | 174.4
2018-10-23 21:30 | 178.33 | 172.52
2018-10-23 22:00 | 176.66 | 170.88
2018-10-23 22:30 | 173.94 | 168.23
2018-10-23 23:00 | 172.38 | 166.52
2018-10-23 23:30 | 186.36 | 181.46
2018-10-24 | 197.35 | 192.76
2018-10-24 00:30 | 196.01 | 191.54
2018-10-24 01:00 | 195.18 | 190.62
2018-10-24 01:30 | 194.67 | 190.14
2018-10-24 02:00 | 193.79 | 189.23
2018-10-24 02:30 | 193.28 | 188.7
2018-10-24 03:00 | 192.89 | 188.33
2018-10-24 03:30 | 192.49 | 187.92
2018-10-24 04:00 | 192.39 | 187.85
2018-10-24 04:30 | 192.7 | 188.17
2018-10-24 05:00 | 193.36 | 188.8
2018-10-24 05:30 | 194.37 | 189.84
2018-10-24 06:00 | 194.86 | 190.33
2018-10-24 06:30 | 196.52 | 192.22
2018-10-24 07:00 | 197.38 | 193.1
2018-10-24 07:30 | 198.75 | 194.6
2018-10-24 08:00 | 198.21 | 194.19
2018-10-24 08:30 | 198.09 | 194.08
2018-10-24 09:00 | 198.29 | 194.27
2018-10-24 09:30 | 198.34 | 194.27
2018-10-24 10:00 | 199.32 | 195.16
2018-10-24 10:30 | 200.28 | 196.18
2018-10-24 11:00 | 200.6 | 196.7
2018-10-24 11:30 | 201.55 | 197.89
2018-10-24 12:00 | 200.96 | 197.4
2018-10-24 12:30 | 200.75 | 197.36
2018-10-24 13:00 | 201.54 | 198.19
2018-10-24 13:30 | 203.2 | 199.71
2018-10-24 14:00 | 204.6 | 201.25
2018-10-24 14:30 | 205.86 | 202.56
2018-10-24 15:00 | 207.05 | 203.72
2018-10-24 15:30 | 208.5 | 205.24
2018-10-24 16:00 | 212.08 | 208.83
2018-10-24 16:30 | 213.2 | 209.92
2018-10-24 17:00 | 214.64 | 211.21
2018-10-24 17:30 | 215.96 | 212.22
2018-10-24 18:00 | 197.35 | 191.97
2018-10-24 18:30 | 191.66 | 185.39
2018-10-24 19:00 | 187.5 | 181.36
2018-10-24 19:30 | 189.6 | 184.32
2018-10-24 20:00 | 186.96 | 181.21
2018-10-24 20:30 | 185.01 | 179.14
2018-10-24 21:00 | 181.36 | 175.62
2018-10-24 21:30 | 179.06 | 173.57
2018-10-24 22:00 | 176.64 | 171.04
2018-10-24 22:30 | 174.22 | 168.17
2018-10-24 23:00 | 172.68 | 166.46
2018-10-24 23:30 | 188.21 | 183.18
2018-10-25 | 197.89 | 193.31
2018-10-25 00:30 | 197 | 192.29
2018-10-25 01:00 | 195.65 | 191.01
2018-10-25 01:30 | 194.73 | 190.04
2018-10-25 02:00 | 193.77 | 188.94
2018-10-25 02:30 | 193.11 | 188.18
2018-10-25 03:00 | 192.42 | 187.44
2018-10-25 03:30 | 192.33 | 187.39
2018-10-25 04:00 | 192.88 | 188.03
2018-10-25 04:30 | 192.64 | 187.78
2018-10-25 05:00 | 193.34 | 188.55
2018-10-25 05:30 | 194.06 | 189.27
2018-10-25 06:00 | 194.91 | 190.34
2018-10-25 06:30 | 197.47 | 192.99
2018-10-25 07:00 | 184.73 | 178.22
2018-10-25 07:30 | 174.07 | 166.15
2018-10-25 08:00 | 173.93 | 165.99
2018-10-25 08:30 | 173.48 | 165.68
2018-10-25 09:00 | 172.7 | 165.41
2018-10-25 09:30 | 172.25 | 165.12
2018-10-25 10:00 | 172.57 | 165.77
2018-10-25 10:30 | 173.18 | 166.4
2018-10-25 11:00 | 174.53 | 167.4
2018-10-25 11:30 | 176 | 168.82
2018-10-25 12:00 | 177.95 | 170.6
2018-10-25 12:30 | 180.16 | 172.92
2018-10-25 13:00 | 182.58 | 175.3
2018-10-25 13:30 | 184.19 | 177.03
2018-10-25 14:00 | 186.31 | 179.09
2018-10-25 14:30 | 187.7 | 180.58
2018-10-25 15:00 | 188.75 | 181.83
2018-10-25 15:30 | 188.94 | 182.26
2018-10-25 16:00 | 190.04 | 183.78
2018-10-25 16:30 | 191.61 | 185.2
2018-10-25 17:00 | 193.08 | 186.5
2018-10-25 17:30 | 192.35 | 185.15
2018-10-25 18:00 | 201.53 | 194.07
2018-10-25 18:30 | 203.09 | 195.69
2018-10-25 19:00 | 202.51 | 195.2
2018-10-25 19:30 | 189.24 | 182.41
2018-10-25 20:00 | 191.71 | 184.81
2018-10-25 20:30 | 194.33 | 187.06
2018-10-25 21:00 | 192.88 | 185.03
2018-10-25 21:30 | 190.42 | 183.62
2018-10-25 22:00 | 188.46 | 181.94
2018-10-25 22:30 | 185.48 | 178.94
2018-10-25 23:00 | 183.39 | 177.22
2018-10-25 23:30 | 182.97 | 175.89
2018-10-26 | 182.12 | 174.54
2018-10-26 00:30 | 180.85 | 173.37
2018-10-26 01:00 | 179.4 | 172.19
2018-10-26 01:30 | 179.13 | 171.41
2018-10-26 02:00 | 178.75 | 171.13
2018-10-26 02:30 | 178.26 | 170.71
2018-10-26 03:00 | 177.61 | 169.84
2018-10-26 03:30 | 176.8 | 168.9
2018-10-26 04:00 | 176.92 | 169.1
2018-10-26 04:30 | 176.93 | 169.13
2018-10-26 05:00 | 176.88 | 169.27
2018-10-26 05:30 | 177.2 | 170.04
2018-10-26 06:00 | 178.03 | 171.1
2018-10-26 06:30 | 181.99 | 173.42
2018-10-26 07:00 | 183.43 | 174.3
2018-10-26 07:30 | 184.41 | 175.56
2018-10-26 08:00 | 182.76 | 174.47
2018-10-26 08:30 | 181.77 | 173.46
2018-10-26 09:00 | 182.42 | 174.27
2018-10-26 09:30 | 182.16 | 173.98
2018-10-26 10:00 | 182.98 | 174.97
2018-10-26 10:30 | 183.17 | 174.99
2018-10-26 11:00 | 184.96 | 176.29
2018-10-26 11:30 | 185.99 | 177.58
2018-10-26 12:00 | 186.8 | 178.58
2018-10-26 12:30 | 188.37 | 179.73
2018-10-26 13:00 | 190.53 | 181.79
2018-10-26 13:30 | 191.87 | 183.38
2018-10-26 14:00 | 193.01 | 184.57
2018-10-26 14:30 | 195.1 | 186.49
2018-10-26 15:00 | 195.75 | 187.26
2018-10-26 15:30 | 195.36 | 188.62
2018-10-26 16:00 | 196.86 | 190.22
2018-10-26 16:30 | 198.55 | 191.98
2018-10-26 17:00 | 201.21 | 194.23
2018-10-26 17:30 | 201.29 | 194.13
2018-10-26 18:00 | 201.59 | 194.31
2018-10-26 18:30 | 201.18 | 193.88
2018-10-26 19:00 | 199.43 | 192.19
2018-10-26 19:30 | 199.36 | 192.16
2018-10-26 20:00 | 197.38 | 189.8
2018-10-26 20:30 | 194.52 | 186.3
2018-10-26 21:00 | 191.95 | 183.65
2018-10-26 21:30 | 189.08 | 181.87
2018-10-26 22:00 | 187.35 | 180.12
2018-10-26 22:30 | 185.37 | 177.91
2018-10-26 23:00 | 184.32 | 176.59
2018-10-26 23:30 | 182.25 | 174.63
2018-10-27 | 181.71 | 173.52
2018-10-27 00:30 | 180.36 | 172.75
2018-10-27 01:00 | 178.75 | 171.11
2018-10-27 01:30 | 177.75 | 170.31
2018-10-27 02:00 | 177.06 | 169.48
2018-10-27 02:30 | 177.48 | 169.12
2018-10-27 03:00 | 177.2 | 168.9
2018-10-27 03:30 | 176.65 | 168.22
2018-10-27 04:00 | 176.56 | 168.08
2018-10-27 04:30 | 176.31 | 167.96
2018-10-27 05:00 | 177.02 | 168.72
2018-10-27 05:30 | 175.92 | 167.71
2018-10-27 06:00 | 176.93 | 168.41
2018-10-27 06:30 | 177.18 | 168.63
2018-10-27 07:00 | 177.13 | 168.97
2018-10-27 07:30 | 178.54 | 169.97
2018-10-27 08:00 | 178.51 | 169.79
2018-10-27 08:30 | 178.89 | 169.9
2018-10-27 09:00 | 179.42 | 170.34
2018-10-27 09:30 | 179.97 | 171.06
2018-10-27 10:00 | 180.66 | 171.83
2018-10-27 10:30 | 182.17 | 173.53
2018-10-27 11:00 | 183.24 | 174.57
2018-10-27 11:30 | 185.34 | 176.44
2018-10-27 12:00 | 186.66 | 177.8
2018-10-27 12:30 | 188.3 | 179.48
2018-10-27 13:00 | 189 | 180.39
2018-10-27 13:30 | 188.86 | 180.23
2018-10-27 14:00 | 189.14 | 180.53
2018-10-27 14:30 | 190.21 | 181.98
2018-10-27 15:00 | 191.43 | 183.17
2018-10-27 15:30 | 192.92 | 184.66
2018-10-27 16:00 | 195.04 | 186.57
2018-10-27 16:30 | 197.06 | 188.63
2018-10-27 17:00 | 198.84 | 190.47
2018-10-27 17:30 | 200.43 | 192.2
2018-10-27 18:00 | 201.56 | 193.23
2018-10-27 18:30 | 202.33 | 194.01
2018-10-27 19:00 | 201.95 | 194.01
2018-10-27 19:30 | 190.55 | 187.22
2018-10-27 20:00 | 191.16 | 187.78
2018-10-27 20:30 | 195.22 | 192.04
2018-10-27 21:00 | 194.81 | 188.21
2018-10-27 21:30 | 193.39 | 186.91
2018-10-27 22:00 | 188.77 | 181.87
2018-10-27 22:30 | 183.59 | 176.04
2018-10-27 23:00 | 181.92 | 174.13
2018-10-27 23:30 | 180.86 | 173.06
2018-10-28 | 178.99 | 171.74
2018-10-28 00:30 | 178.39 | 171.09
2018-10-28 01:00 | 178.07 | 170.16
2018-10-28 01:30 | 177.41 | 169.47
2018-10-28 02:00 | 176.42 | 168.73
2018-10-28 02:30 | 175.89 | 168.56
2018-10-28 03:00 | 175.53 | 168.23
2018-10-28 03:30 | 175.23 | 167.92
2018-10-28 04:00 | 175.3 | 168.05
2018-10-28 04:30 | 174.87 | 167.5
2018-10-28 05:00 | 175.1 | 167.76
2018-10-28 05:30 | 174.92 | 167.75
2018-10-28 06:00 | 174.55 | 167.26
2018-10-28 06:30 | 175.37 | 168.55
2018-10-28 07:00 | 176.63 | 169.24
2018-10-28 07:30 | 177.18 | 169.54
2018-10-28 08:00 | 177.84 | 170.26
2018-10-28 08:30 | 178.47 | 169.86
2018-10-28 09:00 | 179.56 | 170.02
2018-10-28 09:30 | 179.38 | 170.51
2018-10-28 10:00 | 158.29 | 148.49
2018-10-28 10:30 | 156.13 | 146.18
2018-10-28 11:00 | 155.96 | 146.42
2018-10-28 11:30 | 157.32 | 147.38
2018-10-28 12:00 | 157.43 | 148.65
2018-10-28 12:30 | 159.73 | 151.32
2018-10-28 13:00 | 160.56 | 152.12
2018-10-28 13:30 | 162 | 153.93
2018-10-28 14:00 | 163.06 | 154.9
2018-10-28 14:30 | 163.72 | 155.42
2018-10-28 15:00 | 164.89 | 156.72
2018-10-28 15:30 | 165.8 | 157.5
2018-10-28 16:00 | 166.57 | 158.4
2018-10-28 16:30 | 167.34 | 159.4
2018-10-28 17:00 | 167.69 | 159.63
2018-10-28 17:30 | 168.47 | 160.4
2018-10-28 18:00 | 169.88 | 161.81
2018-10-28 18:30 | 163.68 | 160.43
2018-10-28 19:00 | 165.08 | 162.45
2018-10-28 19:30 | 165.51 | 162.82
2018-10-28 20:00 | 166.33 | 163.53
2018-10-28 20:30 | 161.93 | 156.21
2018-10-28 21:00 | 162.3 | 155.18
2018-10-28 21:30 | 160.98 | 153.72
2018-10-28 22:00 | 158.49 | 151.79
2018-10-28 22:30 | 156.19 | 150
2018-10-28 23:00 | 154.75 | 148.55
2018-10-28 23:30 | 154.57 | 147.88
2018-10-29 | 152.73 | 146.18
2018-10-29 00:30 | 152.24 | 145.81
2018-10-29 01:00 | 151.2 | 144.71
2018-10-29 01:30 | 150.95 | 144.32
2018-10-29 02:00 | 150.18 | 143.47
2018-10-29 02:30 | 149.43 | 142.78
2018-10-29 03:00 | 149.37 | 142.73
2018-10-29 03:30 | 149.2 | 142.52
2018-10-29 04:00 | 149 | 142.3
2018-10-29 04:30 | 148.68 | 142.04
2018-10-29 05:00 | 149.22 | 142.75
2018-10-29 05:30 | 150.94 | 143.62
2018-10-29 06:00 | 154.48 | 145.47
2018-10-29 06:30 | 156.44 | 147.32
2018-10-29 07:00 | 158.73 | 150.36
2018-10-29 07:30 | 160.57 | 151.74
2018-10-29 08:00 | 160.49 | 151.7
2018-10-29 08:30 | 159.57 | 150.73
2018-10-29 09:00 | 159.12 | 150.38
2018-10-29 09:30 | 157.54 | 149.74
2018-10-29 10:00 | 161.13 | 153.91
2018-10-29 10:30 | 182.49 | 175.27
2018-10-29 11:00 | 183.39 | 175.98
2018-10-29 11:30 | 184.28 | 176.49
2018-10-29 12:00 | 185.99 | 178.09
2018-10-29 12:30 | 187.18 | 179.05
2018-10-29 13:00 | 189.51 | 181.48
2018-10-29 13:30 | 190.32 | 182.36
2018-10-29 14:00 | 190.96 | 183.08
2018-10-29 14:30 | 192.41 | 184.57
2018-10-29 15:00 | 192.58 | 184.72
2018-10-29 15:30 | 192.97 | 185.24
2018-10-29 16:00 | 194.13 | 186.38
2018-10-29 16:30 | 195.69 | 187.78
2018-10-29 17:00 | 197.05 | 189.26
2018-10-29 17:30 | 198.4 | 190.64
2018-10-29 18:00 | 198.7 | 190.87
2018-10-29 18:30 | 198.83 | 190.9
2018-10-29 19:00 | 199.86 | 192.13
2018-10-29 19:30 | 198.81 | 190.9
2018-10-29 20:00 | 197.17 | 188.95
2018-10-29 20:30 | 195.85 | 187.31
2018-10-29 21:00 | 193.75 | 185.2
2018-10-29 21:30 | 190.92 | 183.54
2018-10-29 22:00 | 187.99 | 180.9
2018-10-29 22:30 | 185.33 | 178.11
2018-10-29 23:00 | 183.58 | 176.17
2018-10-29 23:30 | 182.98 | 174.97
2018-10-30 | 180.91 | 173.24
2018-10-30 00:30 | 180.49 | 173.25
2018-10-30 01:00 | 179.71 | 172.45
2018-10-30 01:30 | 179.03 | 171.63
2018-10-30 02:00 | 178.62 | 171.11
2018-10-30 02:30 | 178.28 | 170.67
2018-10-30 03:00 | 178.07 | 170.45
2018-10-30 03:30 | 177.83 | 170.18
2018-10-30 04:00 | 177.76 | 170.1
2018-10-30 04:30 | 177.92 | 170.3
2018-10-30 05:00 | 178.94 | 171.44
2018-10-30 05:30 | 179.95 | 172.62
2018-10-30 06:00 | 181.41 | 174.21
2018-10-30 06:30 | 185.16 | 176.79
2018-10-30 07:00 | 187.12 | 177.88
2018-10-30 07:30 | 188.43 | 179.47
2018-10-30 08:00 | 189.17 | 180.09
2018-10-30 08:30 | 187.54 | 178.35
2018-10-30 09:00 | 186.92 | 177.52
2018-10-30 09:30 | 185.66 | 175.93
2018-10-30 10:00 | 184.18 | 174.19
2018-10-30 10:30 | 183.82 | 173.98
2018-10-30 11:00 | 182.68 | 172.69
2018-10-30 11:30 | 183.19 | 173.28
2018-10-30 12:00 | 184.21 | 174.15
2018-10-30 12:30 | 184.68 | 174.51
2018-10-30 13:00 | 185.33 | 175.27
2018-10-30 13:30 | 187.66 | 177.82
2018-10-30 14:00 | 189.11 | 179.37
2018-10-30 14:30 | 189.81 | 180.29
2018-10-30 15:00 | 189.87 | 180.48
2018-10-30 15:30 | 190.39 | 180.98
2018-10-30 16:00 | 191.64 | 181.91
2018-10-30 16:30 | 192.46 | 182.56
2018-10-30 17:00 | 193.03 | 182.92
2018-10-30 17:30 | 192.64 | 182.4
2018-10-30 18:00 | 192.79 | 182.55
2018-10-30 18:30 | 193.26 | 183.05
2018-10-30 19:00 | 194.24 | 184.12
2018-10-30 19:30 | 194.75 | 184.39
2018-10-30 20:00 | 193.62 | 183.02
2018-10-30 20:30 | 191.84 | 181.19
2018-10-30 21:00 | 190.22 | 179.48
2018-10-30 21:30 | 188.83 | 178.65
2018-10-30 22:00 | 186.84 | 177.24
2018-10-30 22:30 | 184.84 | 175.02
2018-10-30 23:00 | 182.76 | 173.35
2018-10-30 23:30 | 181.43 | 172.51
2018-10-31 | 180.89 | 171.53
2018-10-31 00:30 | 180.5 | 170.6
2018-10-31 01:00 | 179.45 | 169.39
2018-10-31 01:30 | 178.6 | 168.45
2018-10-31 02:00 | 178.04 | 167.8
2018-10-31 02:30 | 177.56 | 167.21
2018-10-31 03:00 | 177.57 | 167.25
2018-10-31 03:30 | 177.27 | 166.93
2018-10-31 04:00 | 177.12 | 166.89
2018-10-31 04:30 | 177.43 | 167.24
2018-10-31 05:00 | 178.12 | 167.8
2018-10-31 05:30 | 179.42 | 169.43
2018-10-31 06:00 | 179.8 | 170.37
2018-10-31 06:30 | 183 | 172.71
2018-10-31 07:00 | 172.94 | 163.83
2018-10-31 07:30 | 173.71 | 164.29
2018-10-31 08:00 | 181.94 | 171.68
2018-10-31 08:30 | 184.16 | 173.94
2018-10-31 09:00 | 183.58 | 172.74
2018-10-31 09:30 | 183.38 | 172.31
2018-10-31 10:00 | 182.65 | 172.82
2018-10-31 10:30 | 181.46 | 171.92
2018-10-31 11:00 | 181.39 | 172.34
2018-10-31 11:30 | 182.32 | 172.9
2018-10-31 12:00 | 184.04 | 174.84
2018-10-31 12:30 | 184.57 | 175.21
2018-10-31 13:00 | 186.25 | 176.43
2018-10-31 13:30 | 187.09 | 177.56
2018-10-31 14:00 | 186.78 | 177.47
2018-10-31 14:30 | 188.59 | 179.36
2018-10-31 15:00 | 188.78 | 179.47
2018-10-31 15:30 | 186.17 | 179.3
2018-10-31 16:00 | 187.7 | 183.82
2018-10-31 16:30 | 188.38 | 184.48
2018-10-31 17:00 | 187.59 | 183.5
2018-10-31 17:30 | 185.72 | 181.46
2018-10-31 18:00 | 185.37 | 181.23
2018-10-31 18:30 | 185.89 | 181.61
2018-10-31 19:00 | 185.07 | 180.78
2018-10-31 19:30 | 184.42 | 179.96
2018-10-31 20:00 | 186.23 | 181.62
2018-10-31 20:30 | 187.82 | 183.1
2018-10-31 21:00 | 188.65 | 179.19
2018-10-31 21:30 | 189.4 | 179.43
2018-10-31 22:00 | 187.27 | 177.97
2018-10-31 22:30 | 187.91 | 178.68
2018-10-31 23:00 | 186.16 | 177.56
2018-10-31 23:30 | 184.7 | 176.39
2018-11-01 | 183.95 | 175.14
2018-11-01 00:30 | 183.46 | 174.22
2018-11-01 01:00 | 183.44 | 173.69
2018-11-01 01:30 | 183.19 | 173.39
2018-11-01 02:00 | 183.35 | 173.63
2018-11-01 02:30 | 183.11 | 173.28
2018-11-01 03:00 | 182.74 | 172.91
2018-11-01 03:30 | 182.2 | 172.49
2018-11-01 04:00 | 182.35 | 172.69
2018-11-01 04:30 | 182.33 | 172.67
2018-11-01 05:00 | 182.71 | 173.18
2018-11-01 05:30 | 183.66 | 174.27
2018-11-01 06:00 | 184.54 | 175.28
2018-11-01 06:30 | 186.66 | 177.86
2018-11-01 07:00 | 188.34 | 179.43
2018-11-01 07:30 | 189.43 | 180.13
2018-11-01 08:00 | 189.18 | 179.38
2018-11-01 08:30 | 188.4 | 178.87
2018-11-01 09:00 | 188.06 | 178.66
2018-11-01 09:30 | 187.72 | 177.82
2018-11-01 10:00 | 188.23 | 178.62
2018-11-01 10:30 | 187.84 | 178.14
2018-11-01 11:00 | 188.41 | 178.86
2018-11-01 11:30 | 189.35 | 179.96
2018-11-01 12:00 | 190.14 | 180.55
2018-11-01 12:30 | 190.58 | 180.49
2018-11-01 13:00 | 191.61 | 182.35
2018-11-01 13:30 | 192.17 | 182.63
2018-11-01 14:00 | 193.04 | 183.55
2018-11-01 14:30 | 194.55 | 184.82
2018-11-01 15:00 | 195.29 | 185.38
2018-11-01 15:30 | 195.11 | 185.62
2018-11-01 16:00 | 186.47 | 181.6
2018-11-01 16:30 | 186.38 | 182.18
2018-11-01 17:00 | 185.27 | 181.09
2018-11-01 17:30 | 185.37 | 181.15
2018-11-01 18:00 | 185.48 | 181.25
2018-11-01 18:30 | 186.49 | 182.17
2018-11-01 19:00 | 186.43 | 182.28
2018-11-01 19:30 | 187.29 | 183.11
2018-11-01 20:00 | 189.03 | 184.92
2018-11-01 20:30 | 191.73 | 187.31
2018-11-01 21:00 | 193.69 | 185
2018-11-01 21:30 | 196.3 | 185.86
2018-11-01 22:00 | 192.95 | 183.64
2018-11-01 22:30 | 191.15 | 181.58
2018-11-01 23:00 | 189.72 | 179.76
2018-11-01 23:30 | 188.04 | 178.46
2018-11-02 | 185.82 | 177.07
2018-11-02 00:30 | 184.92 | 176.1
2018-11-02 01:00 | 183.85 | 174.93
2018-11-02 01:30 | 184.13 | 174.46
2018-11-02 02:00 | 183.84 | 173.81
2018-11-02 02:30 | 183.22 | 173.06
2018-11-02 03:00 | 182.99 | 172.87
2018-11-02 03:30 | 182.57 | 172.49
2018-11-02 04:00 | 182.51 | 172.4
2018-11-02 04:30 | 182.58 | 172.57
2018-11-02 05:00 | 182.93 | 172.84
2018-11-02 05:30 | 183.91 | 174
2018-11-02 06:00 | 184.77 | 175.58
2018-11-02 06:30 | 186.59 | 177.63
2018-11-02 07:00 | 188.56 | 178.46
2018-11-02 07:30 | 187.12 | 178.05
2018-11-02 08:00 | 186.65 | 177.49
2018-11-02 08:30 | 186.22 | 176.47
2018-11-02 09:00 | 186.06 | 175.63
2018-11-02 09:30 | 185.25 | 174.77
2018-11-02 10:00 | 184.6 | 174.66
2018-11-02 10:30 | 184.33 | 174.42
2018-11-02 11:00 | 184.76 | 175
2018-11-02 11:30 | 185.78 | 175.89
2018-11-02 12:00 | 186.81 | 176.92
2018-11-02 12:30 | 187.92 | 177.95
2018-11-02 13:00 | 189.13 | 179.44
2018-11-02 13:30 | 189.31 | 180.25
2018-11-02 14:00 | 190.35 | 180.96
2018-11-02 14:30 | 192.13 | 182.58
2018-11-02 15:00 | 192.76 | 183.62
2018-11-02 15:30 | 193.45 | 184.25
2018-11-02 16:00 | 188.7 | 182.07
2018-11-02 16:30 | 186.21 | 181.92
2018-11-02 17:00 | 185.52 | 181.15
2018-11-02 17:30 | 185.91 | 181.28
2018-11-02 18:00 | 186.5 | 181.78
2018-11-02 18:30 | 187.39 | 182.65
2018-11-02 19:00 | 187.61 | 182.96
2018-11-02 19:30 | 189.15 | 184.43
2018-11-02 20:00 | 190.75 | 185.9
2018-11-02 20:30 | 192.87 | 188.02
2018-11-02 21:00 | 192.45 | 183.03
2018-11-02 21:30 | 192.45 | 183.65
2018-11-02 22:00 | 190.71 | 181.83
2018-11-02 22:30 | 188.79 | 179.66
2018-11-02 23:00 | 187.58 | 178.51
2018-11-02 23:30 | 186.54 | 178.21
2018-11-03 | 185.09 | 176.79
2018-11-03 00:30 | 185.04 | 176.32
2018-11-03 01:00 | 184.01 | 175.1
2018-11-03 01:30 | 183.4 | 174.46
2018-11-03 02:00 | 182.06 | 173.71
2018-11-03 02:30 | 181.56 | 173.37
2018-11-03 03:00 | 181.41 | 173.3
2018-11-03 03:30 | 181.11 | 172.98
2018-11-03 04:00 | 181 | 172.85
2018-11-03 04:30 | 180.87 | 172.75
2018-11-03 05:00 | 181.08 | 172.96
2018-11-03 05:30 | 181.41 | 173.29
2018-11-03 06:00 | 181.69 | 173.54
2018-11-03 06:30 | 182.31 | 174.38
2018-11-03 07:00 | 183.69 | 175.4
2018-11-03 07:30 | 185.37 | 175.97
2018-11-03 08:00 | 184.77 | 175.39
2018-11-03 08:30 | 183.6 | 174.46
2018-11-03 09:00 | 183.14 | 173.79
2018-11-03 09:30 | 182.76 | 173.42
2018-11-03 10:00 | 183.75 | 173.98
2018-11-03 10:30 | 183.79 | 173.73
2018-11-03 11:00 | 184.6 | 174.47
2018-11-03 11:30 | 185.58 | 175.63
2018-11-03 12:00 | 186.86 | 177.24
2018-11-03 12:30 | 188.73 | 179.16
2018-11-03 13:00 | 189.85 | 180.53
2018-11-03 13:30 | 191 | 181.79
2018-11-03 14:00 | 192.55 | 183.55
2018-11-03 14:30 | 194.54 | 184.77
2018-11-03 15:00 | 196.7 | 186.9
2018-11-03 15:30 | 198.16 | 188.39
2018-11-03 16:00 | 200.86 | 191.03
2018-11-03 16:30 | 202.78 | 193.12
2018-11-03 17:00 | 204.47 | 195
2018-11-03 17:30 | 206.11 | 196.69
2018-11-03 18:00 | 206.84 | 197.37
2018-11-03 18:30 | 199.83 | 191.47
2018-11-03 19:00 | 182.81 | 178.11
2018-11-03 19:30 | 183.93 | 179.07
2018-11-03 20:00 | 186.38 | 181.37
2018-11-03 20:30 | 188.68 | 183.6
2018-11-03 21:00 | 191 | 185.99
2018-11-03 21:30 | 192.03 | 187.44
2018-11-03 22:00 | 193.38 | 188.76
2018-11-03 22:30 | 195.48 | 190.91
2018-11-03 23:00 | 196.76 | 192.82
2018-11-03 23:30 | 197.01 | 193.44
2018-11-04 | 187.88 | 180.03
2018-11-04 00:30 | 187.97 | 178.84
2018-11-04 01:00 | 186.61 | 177.27
2018-11-04 01:30 | 186.11 | 176.71
2018-11-04 02:00 | 185.11 | 175.7
2018-11-04 02:30 | 184.76 | 175.35
2018-11-04 03:00 | 184.56 | 174.98
2018-11-04 03:30 | 183.59 | 173.95
2018-11-04 04:00 | 183.43 | 173.77
2018-11-04 04:30 | 183.58 | 173.94
2018-11-04 05:00 | 183.38 | 173.75
2018-11-04 05:30 | 183.1 | 173.4
2018-11-04 06:00 | 183.19 | 173.52
2018-11-04 06:30 | 183.16 | 173.74
2018-11-04 07:00 | 183.23 | 174
2018-11-04 07:30 | 183.38 | 174.41
2018-11-04 08:00 | 182.23 | 173.36
2018-11-04 08:30 | 181.94 | 172.67
2018-11-04 09:00 | 182.22 | 172.73
2018-11-04 09:30 | 182.32 | 172.69
2018-11-04 10:00 | 184.74 | 174.9
2018-11-04 10:30 | 185 | 175.32
2018-11-04 11:00 | 185.95 | 176.44
2018-11-04 11:30 | 188.2 | 178.75
2018-11-04 12:00 | 190.47 | 181.32
2018-11-04 12:30 | 192.24 | 183.03
2018-11-04 13:00 | 193.7 | 184.47
2018-11-04 13:30 | 194.73 | 185.52
2018-11-04 14:00 | 196.36 | 186.88
2018-11-04 14:30 | 197.74 | 188.5
2018-11-04 15:00 | 199.73 | 190.7
2018-11-04 15:30 | 201.76 | 193.02
2018-11-04 16:00 | 203.06 | 194.68
2018-11-04 16:30 | 205.11 | 196.7
2018-11-04 17:00 | 207.97 | 199.25
2018-11-04 17:30 | 211.12 | 202.39
2018-11-04 18:00 | 204 | 195.31
2018-11-04 18:30 | 174.08 | 168.48
2018-11-04 19:00 | 177.17 | 170.64
2018-11-04 19:30 | 210.64 | 202.42
2018-11-04 20:00 | 208.09 | 199.39
2018-11-04 20:30 | 204.69 | 195.51
2018-11-04 21:00 | 201.36 | 191.97
2018-11-04 21:30 | 197.04 | 188.93
2018-11-04 22:00 | 193.63 | 185.32
2018-11-04 22:30 | 190.78 | 182.1
2018-11-04 23:00 | 188.36 | 179.56
2018-11-04 23:30 | 187.64 | 178.43
2018-11-05 | 186.36 | 177.17
2018-11-05 00:30 | 185.03 | 176.28
2018-11-05 01:00 | 184.32 | 175.4
2018-11-05 01:30 | 183.49 | 174.53
2018-11-05 02:00 | 182.62 | 173.86
2018-11-05 02:30 | 182.2 | 173.59
2018-11-05 03:00 | 181.53 | 172.86
2018-11-05 03:30 | 181.52 | 172.77
2018-11-05 04:00 | 181.08 | 172.36
2018-11-05 04:30 | 181.8 | 172.97
2018-11-05 05:00 | 182.19 | 173.34
2018-11-05 05:30 | 182.55 | 173.85
2018-11-05 06:00 | 183.17 | 174.74
2018-11-05 06:30 | 186.48 | 178.01
2018-11-05 07:00 | 188.45 | 179.45
2018-11-05 07:30 | 190.71 | 180.91
2018-11-05 08:00 | 191.88 | 181.58
2018-11-05 08:30 | 192.63 | 182.44
2018-11-05 09:00 | 193.24 | 183.13
2018-11-05 09:30 | 193.68 | 183.48
2018-11-05 10:00 | 195.44 | 185.44
2018-11-05 10:30 | 196.02 | 186.14
2018-11-05 11:00 | 198.01 | 188.41
2018-11-05 11:30 | 199.03 | 189.85
2018-11-05 12:00 | 200.61 | 191.54
2018-11-05 12:30 | 202.11 | 193.34
2018-11-05 13:00 | 204.85 | 195.95
2018-11-05 13:30 | 206.5 | 197.73
2018-11-05 14:00 | 207.92 | 199.63
2018-11-05 14:30 | 209.43 | 201.36
2018-11-05 15:00 | 210.67 | 202.65
2018-11-05 15:30 | 212.28 | 204.18
2018-11-05 16:00 | 213.86 | 206.32
2018-11-05 16:30 | 215.01 | 206.88
2018-11-05 17:00 | 216.24 | 207.05
2018-11-05 17:30 | 217.08 | 207.73
2018-11-05 18:00 | 218.11 | 208.69
2018-11-05 18:30 | 216.81 | 208.74
2018-11-05 19:00 | 217.44 | 209.63
2018-11-05 19:30 | 217.86 | 209.89
2018-11-05 20:00 | 216.43 | 207.96
2018-11-05 20:30 | 213.09 | 204.03
2018-11-05 21:00 | 209.75 | 200
2018-11-05 21:30 | 206.77 | 196.95
2018-11-05 22:00 | 202.42 | 192.87
2018-11-05 22:30 | 199.47 | 189.87
2018-11-05 23:00 | 197.34 | 187.37
2018-11-05 23:30 | 196.31 | 185.98
2018-11-06 | 194.19 | 184.01
2018-11-06 00:30 | 192.99 | 182.97
2018-11-06 01:00 | 191.62 | 181.55
2018-11-06 01:30 | 190.65 | 180.48
2018-11-06 02:00 | 189.67 | 179.37
2018-11-06 02:30 | 189.19 | 178.77
2018-11-06 03:00 | 188.65 | 178.15
2018-11-06 03:30 | 188.16 | 177.6
2018-11-06 04:00 | 188.17 | 177.68
2018-11-06 04:30 | 187.78 | 177.42
2018-11-06 05:00 | 188.35 | 178.07
2018-11-06 05:30 | 189.04 | 178.88
2018-11-06 06:00 | 190.19 | 179.95
2018-11-06 06:30 | 193.23 | 182.39
2018-11-06 07:00 | 195.71 | 184.17
2018-11-06 07:30 | 197.15 | 186.18
2018-11-06 08:00 | 197.98 | 187.13
2018-11-06 08:30 | 199.41 | 188.9
2018-11-06 09:00 | 200.2 | 189.81
2018-11-06 09:30 | 200.95 | 190.7
2018-11-06 10:00 | 202.99 | 193.05
2018-11-06 10:30 | 203.84 | 193.82
2018-11-06 11:00 | 204.54 | 194.52
2018-11-06 11:30 | 206.37 | 196.32
2018-11-06 12:00 | 206.26 | 196.6
2018-11-06 12:30 | 206.01 | 196.37
2018-11-06 13:00 | 207.64 | 197.83
2018-11-06 13:30 | 208.63 | 198.91
2018-11-06 14:00 | 209.7 | 200.29
2018-11-06 14:30 | 210.38 | 200.79
2018-11-06 15:00 | 211.89 | 202.3
2018-11-06 15:30 | 212.12 | 202.43
2018-11-06 16:00 | 213.49 | 204.09
2018-11-06 16:30 | 214.63 | 205.34
2018-11-06 17:00 | 215.39 | 206.31
2018-11-06 17:30 | 215.17 | 206.31
2018-11-06 18:00 | 216.68 | 207.94
2018-11-06 18:30 | 216.6 | 207.69
2018-11-06 19:00 | 217.49 | 208.74
2018-11-06 19:30 | 217.83 | 209
2018-11-06 20:00 | 215.27 | 205.88
2018-11-06 20:30 | 212.37 | 202.69
2018-11-06 21:00 | 208.73 | 198.65
2018-11-06 21:30 | 205.56 | 195.18
2018-11-06 22:00 | 203.03 | 192.1
2018-11-06 22:30 | 199.6 | 188.24
2018-11-06 23:00 | 197.23 | 186.1
2018-11-06 23:30 | 195.26 | 184.57
2018-11-07 | 193.48 | 182.62
2018-11-07 00:30 | 192.14 | 181.26
2018-11-07 01:00 | 190.68 | 179.69
2018-11-07 01:30 | 190.43 | 179.15
2018-11-07 02:00 | 189.4 | 178.59
2018-11-07 02:30 | 188.9 | 178
2018-11-07 03:00 | 187.85 | 177.75
2018-11-07 03:30 | 186.85 | 176.95
2018-11-07 04:00 | 186.84 | 176.96
2018-11-07 04:30 | 186.4 | 176.74
2018-11-07 05:00 | 186.94 | 177.35
2018-11-07 05:30 | 187.64 | 178.39
2018-11-07 06:00 | 189.18 | 179.73
2018-11-07 06:30 | 192.2 | 182.24
2018-11-07 07:00 | 193.55 | 183.29
2018-11-07 07:30 | 195.25 | 185.17
2018-11-07 08:00 | 195.04 | 185.14
2018-11-07 08:30 | 194.79 | 184.97
2018-11-07 09:00 | 194.46 | 184.72
2018-11-07 09:30 | 194.95 | 185.11
2018-11-07 10:00 | 195.57 | 185.94
2018-11-07 10:30 | 195.42 | 185.74
2018-11-07 11:00 | 196.18 | 186.69
2018-11-07 11:30 | 197.63 | 188.03
2018-11-07 12:00 | 199.04 | 189.68
2018-11-07 12:30 | 199.13 | 190.19
2018-11-07 13:00 | 200.08 | 191.31
2018-11-07 13:30 | 200.99 | 192.03
2018-11-07 14:00 | 201.7 | 193.08
2018-11-07 14:30 | 202.83 | 194.14
2018-11-07 15:00 | 203.24 | 194.56
2018-11-07 15:30 | 203.54 | 194.79
2018-11-07 16:00 | 203.67 | 195.21
2018-11-07 16:30 | 203.45 | 194.96
2018-11-07 17:00 | 202.5 | 193.8
2018-11-07 17:30 | 201.75 | 192.68
2018-11-07 18:00 | 201.71 | 192.57
2018-11-07 18:30 | 202.2 | 192.99
2018-11-07 19:00 | 202.8 | 193.55
2018-11-07 19:30 | 201.89 | 192.14
2018-11-07 20:00 | 199.85 | 189.59
2018-11-07 20:30 | 198.04 | 187.61
2018-11-07 21:00 | 196 | 185.31
2018-11-07 21:30 | 194.02 | 183.75
2018-11-07 22:00 | 191.8 | 181.46
2018-11-07 22:30 | 189.59 | 179.15
2018-11-07 23:00 | 188.08 | 177.77
2018-11-07 23:30 | 186.59 | 176.42
2018-11-08 | 185.31 | 175.12
2018-11-08 00:30 | 184.07 | 174.18
2018-11-08 01:00 | 182.45 | 172.83
2018-11-08 01:30 | 182.27 | 172.55
2018-11-08 02:00 | 181.98 | 172.25
2018-11-08 02:30 | 181.45 | 171.62
2018-11-08 03:00 | 181.3 | 171.4
2018-11-08 03:30 | 180.79 | 170.8
2018-11-08 04:00 | 180.66 | 170.59
2018-11-08 04:30 | 180.94 | 170.9
2018-11-08 05:00 | 181.11 | 171.21
2018-11-08 05:30 | 181.63 | 171.77
2018-11-08 06:00 | 182.92 | 172.75
2018-11-08 06:30 | 187.29 | 176.71
2018-11-08 07:00 | 190.31 | 179.43
2018-11-08 07:30 | 190.79 | 180.19
2018-11-08 08:00 | 189.81 | 179.32
2018-11-08 08:30 | 187.72 | 176.73
2018-11-08 09:00 | 185.07 | 173.35
2018-11-08 09:30 | 182.88 | 170.9
2018-11-08 10:00 | 181.3 | 168.91
2018-11-08 10:30 | 179.35 | 166.89
2018-11-08 11:00 | 177.98 | 165.44
2018-11-08 11:30 | 177.29 | 164.75
2018-11-08 12:00 | 176.84 | 164.32
2018-11-08 12:30 | 177.84 | 165.23
2018-11-08 13:00 | 177.76 | 164.95
2018-11-08 13:30 | 178.78 | 166
2018-11-08 14:00 | 180.14 | 167.6
2018-11-08 14:30 | 180.5 | 167.46
2018-11-08 15:00 | 181.13 | 168.25
2018-11-08 15:30 | 183.54 | 171.67
2018-11-08 16:00 | 186.73 | 175.48
2018-11-08 16:30 | 186.69 | 175.2
2018-11-08 17:00 | 187.3 | 175.8
2018-11-08 17:30 | 189.17 | 177.55
2018-11-08 18:00 | 190.99 | 179.36
2018-11-08 18:30 | 179.38 | 168.77
2018-11-08 19:00 | 151.6 | 142.6
2018-11-08 19:30 | 144.95 | 135.7
2018-11-08 20:00 | 140.37 | 130.61
2018-11-08 20:30 | 139.88 | 130.95
2018-11-08 21:00 | 139.57 | 130.73
2018-11-08 21:30 | 138.02 | 129.78
2018-11-08 22:00 | 135.63 | 127.75
2018-11-08 22:30 | 132.48 | 124.23
2018-11-08 23:00 | 130.37 | 122.16
2018-11-08 23:30 | 129.61 | 121.56
2018-11-09 | 128.75 | 120.71
2018-11-09 00:30 | 128.05 | 120.49
2018-11-09 01:00 | 128.8 | 120.22
2018-11-09 01:30 | 131.8 | 124.27
2018-11-09 02:00 | 144.78 | 138.37
2018-11-09 02:30 | 151.71 | 144.15
2018-11-09 03:00 | 156.3 | 148.35
2018-11-09 03:30 | 156.63 | 148.68
2018-11-09 04:00 | 156.31 | 148.47
2018-11-09 04:30 | 154.68 | 146.66
2018-11-09 05:00 | 154.98 | 147.07
2018-11-09 05:30 | 156.88 | 149.25
2018-11-09 06:00 | 158.61 | 151.24
2018-11-09 06:30 | 155.83 | 148.26
2018-11-09 07:00 | 155.04 | 146.76
2018-11-09 07:30 | 154.61 | 146.36
2018-11-09 08:00 | 152.84 | 144.33
2018-11-09 08:30 | 148.47 | 139.24
2018-11-09 09:00 | 151.34 | 141.9
2018-11-09 09:30 | 156.1 | 146.53
2018-11-09 10:00 | 157.77 | 148.34
2018-11-09 10:30 | 160.27 | 150.62
2018-11-09 11:00 | 146.17 | 136.44
2018-11-09 11:30 | 148.1 | 138.72
2018-11-09 12:00 | 148.93 | 139.53
2018-11-09 12:30 | 148.87 | 139.36
2018-11-09 13:00 | 150.42 | 140.94
2018-11-09 13:30 | 153.68 | 144.09
2018-11-09 14:00 | 155.94 | 146.22
2018-11-09 14:30 | 156.82 | 147.23
2018-11-09 15:00 | 156.84 | 147.81
2018-11-09 15:30 | 156.82 | 147.85
2018-11-09 16:00 | 159.48 | 150.34
2018-11-09 16:30 | 160.5 | 151.48
2018-11-09 17:00 | 160.94 | 152.03
2018-11-09 17:30 | 162 | 153.09
2018-11-09 18:00 | 162.75 | 153.9
2018-11-09 18:30 | 162.89 | 154.15
2018-11-09 19:00 | 163.7 | 155.11
2018-11-09 19:30 | 164.11 | 155.48
2018-11-09 20:00 | 162.38 | 153.72
2018-11-09 20:30 | 160.88 | 152.12
2018-11-09 21:00 | 160.48 | 151.59
2018-11-09 21:30 | 159.99 | 151.3
2018-11-09 22:00 | 159.11 | 150.51
2018-11-09 22:30 | 156.92 | 148.17
2018-11-09 23:00 | 155.19 | 146.18
2018-11-09 23:30 | 154.83 | 145.08
2018-11-10 | 153.21 | 143.63
2018-11-10 00:30 | 151.93 | 142.56
2018-11-10 01:00 | 150.41 | 141.49
2018-11-10 01:30 | 149.34 | 140.39
2018-11-10 02:00 | 148.94 | 140.13
2018-11-10 02:30 | 148.26 | 139.52
2018-11-10 03:00 | 148.2 | 139.43
2018-11-10 03:30 | 147.71 | 138.91
2018-11-10 04:00 | 147.48 | 138.74
2018-11-10 04:30 | 147.01 | 138.28
2018-11-10 05:00 | 147.68 | 138.97
2018-11-10 05:30 | 147.71 | 138.96
2018-11-10 06:00 | 148.47 | 139.66
2018-11-10 06:30 | 148.64 | 140.23
2018-11-10 07:00 | 149.17 | 140.87
2018-11-10 07:30 | 149.18 | 140.74
2018-11-10 08:00 | 149.39 | 141.04
2018-11-10 08:30 | 149.17 | 140.9
2018-11-10 09:00 | 150.97 | 141.85
2018-11-10 09:30 | 151.95 | 142.54
2018-11-10 10:00 | 151.54 | 142.25
2018-11-10 10:30 | 151.43 | 142.08
2018-11-10 11:00 | 151.76 | 142.34
2018-11-10 11:30 | 152.64 | 143.41
2018-11-10 12:00 | 153.76 | 144.48
2018-11-10 12:30 | 155.06 | 145.75
2018-11-10 13:00 | 155.5 | 146.28
2018-11-10 13:30 | 155.58 | 146.45
2018-11-10 14:00 | 156.92 | 147.45
2018-11-10 14:30 | 157.87 | 148.47
2018-11-10 15:00 | 159.1 | 149.76
2018-11-10 15:30 | 160.62 | 151.33
2018-11-10 16:00 | 162.49 | 153.4
2018-11-10 16:30 | 164.11 | 154.85
2018-11-10 17:00 | 165.35 | 156.15
2018-11-10 17:30 | 166.37 | 157.36
2018-11-10 18:00 | 167.45 | 158.56
2018-11-10 18:30 | 167.49 | 158.68
2018-11-10 19:00 | 167.74 | 158.69
2018-11-10 19:30 | 168.33 | 158.56
2018-11-10 20:00 | 166.67 | 156.79
2018-11-10 20:30 | 164.85 | 154.69
2018-11-10 21:00 | 162.97 | 152.51
2018-11-10 21:30 | 162.41 | 152.01
2018-11-10 22:00 | 160.88 | 150.53
2018-11-10 22:30 | 159.14 | 148.85
2018-11-10 23:00 | 157.77 | 147.68
2018-11-10 23:30 | 156.17 | 146.03
2018-11-11 | 154.54 | 144.89
2018-11-11 00:30 | 153.42 | 143.77
2018-11-11 01:00 | 150.93 | 141.51
2018-11-11 01:30 | 150.55 | 141.28
2018-11-11 02:00 | 149.92 | 140.56
2018-11-11 02:30 | 149.47 | 140.08
2018-11-11 03:00 | 149.05 | 139.66
2018-11-11 03:30 | 146.36 | 137.03
2018-11-11 04:00 | 143.6 | 134.54
2018-11-11 04:30 | 147.22 | 139
2018-11-11 05:00 | 149.47 | 141.52
2018-11-11 05:30 | 149.49 | 141.39
2018-11-11 06:00 | 151.1 | 143.22
2018-11-11 06:30 | 155.54 | 146.89
2018-11-11 07:00 | 158.69 | 149.52
2018-11-11 07:30 | 159.14 | 150.02
2018-11-11 08:00 | 159.29 | 150.49
2018-11-11 08:30 | 160.96 | 152.72
2018-11-11 09:00 | 161.84 | 154.26
2018-11-11 09:30 | 163.44 | 156.41
2018-11-11 10:00 | 164.4 | 157.34
2018-11-11 10:30 | 164.64 | 157.41
2018-11-11 11:00 | 167.4 | 160.69
2018-11-11 11:30 | 168.9 | 162.25
2018-11-11 12:00 | 172.33 | 165.79
2018-11-11 12:30 | 190.63 | 183.79
2018-11-11 13:00 | 191.38 | 184.45
2018-11-11 13:30 | 192.49 | 185.63
2018-11-11 14:00 | 192.4 | 185.58
2018-11-11 14:30 | 193.94 | 187.27
2018-11-11 15:00 | 196.45 | 188.01
2018-11-11 15:30 | 198.82 | 190.37
2018-11-11 16:00 | 197.78 | 191.3
2018-11-11 16:30 | 199.26 | 192.61
2018-11-11 17:00 | 230.74 | 223.86
2018-11-11 17:30 | 242.21 | 235.44
2018-11-11 18:00 | 243.46 | 236.43
2018-11-11 18:30 | 244.62 | 237.24
2018-11-11 19:00 | 240.96 | 234.41
2018-11-11 19:30 | 240.54 | 237.45
2018-11-11 20:00 | 241.59 | 238.48
2018-11-11 20:30 | 243.12 | 240.08
2018-11-11 21:00 | 237.71 | 231.61
2018-11-11 21:30 | 237.78 | 231.1
2018-11-11 22:00 | 235.67 | 229.2
2018-11-11 22:30 | 232.87 | 226.73
2018-11-11 23:00 | 231.49 | 225.32
2018-11-11 23:30 | 230.97 | 224.7
2018-11-12 | 229.77 | 223.71
2018-11-12 00:30 | 229.22 | 223.02
2018-11-12 01:00 | 228.63 | 222.14
2018-11-12 01:30 | 228.46 | 221.98
2018-11-12 02:00 | 227.77 | 221.24
2018-11-12 02:30 | 227.59 | 221.01
2018-11-12 03:00 | 227.16 | 220.68
2018-11-12 03:30 | 226.89 | 220.52
2018-11-12 04:00 | 226.67 | 220.3
2018-11-12 04:30 | 227.12 | 220.72
2018-11-12 05:00 | 227.91 | 221.52
2018-11-12 05:30 | 229.02 | 222.68
2018-11-12 06:00 | 229.71 | 223.52
2018-11-12 06:30 | 232.44 | 226.47
2018-11-12 07:00 | 234.05 | 227.12
2018-11-12 07:30 | 235.24 | 227.73
2018-11-12 08:00 | 234.83 | 227.48
2018-11-12 08:30 | 233.91 | 226.78
2018-11-12 09:00 | 233.4 | 226.27
2018-11-12 09:30 | 232.93 | 225.82
2018-11-12 10:00 | 233.62 | 226.48
2018-11-12 10:30 | 233.63 | 226.33
2018-11-12 11:00 | 234.24 | 227.11
2018-11-12 11:30 | 234.74 | 227.42
2018-11-12 12:00 | 235.74 | 228.43
2018-11-12 12:30 | 236.67 | 229.51
2018-11-12 13:00 | 238.4 | 231.34
2018-11-12 13:30 | 240.07 | 232.65
2018-11-12 14:00 | 241.81 | 234.81
2018-11-12 14:30 | 242.76 | 235.78
2018-11-12 15:00 | 242.99 | 236.21
2018-11-12 15:30 | 243.66 | 237.07
2018-11-12 16:00 | 245.53 | 238.66
2018-11-12 16:30 | 248.11 | 241.25
2018-11-12 17:00 | 248.94 | 241.9
2018-11-12 17:30 | 250.17 | 242.83
2018-11-12 18:00 | 251.11 | 243.64
2018-11-12 18:30 | 251.53 | 243.93
2018-11-12 19:00 | 252.53 | 245.19
2018-11-12 19:30 | 252.72 | 245.65
2018-11-12 20:00 | 249.6 | 243.48
2018-11-12 20:30 | 247.72 | 241.36
2018-11-12 21:00 | 245.54 | 238.89
2018-11-12 21:30 | 243.7 | 237.25
2018-11-12 22:00 | 241.39 | 235.09
2018-11-12 22:30 | 238.51 | 232.62
2018-11-12 23:00 | 236.62 | 230.58
2018-11-12 23:30 | 235.62 | 229.62
2018-11-13 | 234.2 | 228.67
2018-11-13 00:30 | 233.95 | 227.9
2018-11-13 01:00 | 233.24 | 226.87
2018-11-13 01:30 | 232.99 | 226.48
2018-11-13 02:00 | 232.57 | 225.96
2018-11-13 02:30 | 231.77 | 225.03
2018-11-13 03:00 | 231.69 | 224.94
2018-11-13 03:30 | 231.14 | 224.41
2018-11-13 04:00 | 230.79 | 224.11
2018-11-13 04:30 | 230.84 | 224.32
2018-11-13 05:00 | 231.22 | 224.6
2018-11-13 05:30 | 232.23 | 225.68
2018-11-13 06:00 | 232.75 | 226.36
2018-11-13 06:30 | 234.77 | 227.67
2018-11-13 07:00 | 236.1 | 228.08
2018-11-13 07:30 | 236.39 | 228.77
2018-11-13 08:00 | 235.26 | 228.52
2018-11-13 08:30 | 234.61 | 227.9
2018-11-13 09:00 | 234.05 | 227.42
2018-11-13 09:30 | 234.03 | 227.04
2018-11-13 10:00 | 234.57 | 227.64
2018-11-13 10:30 | 234.14 | 227.3
2018-11-13 11:00 | 234.85 | 227.96
2018-11-13 11:30 | 235.79 | 228.88
2018-11-13 12:00 | 236.93 | 230.13
2018-11-13 12:30 | 236.93 | 230.17
2018-11-13 13:00 | 238.53 | 231.76
2018-11-13 13:30 | 240.32 | 233.49
2018-11-13 14:00 | 241.72 | 235.09
2018-11-13 14:30 | 243.45 | 236.85
2018-11-13 15:00 | 244.53 | 237.95
2018-11-13 15:30 | 245.08 | 238.68
2018-11-13 16:00 | 246.71 | 240.43
2018-11-13 16:30 | 248.57 | 242.25
2018-11-13 17:00 | 249.97 | 243.59
2018-11-13 17:30 | 250.86 | 244.2
2018-11-13 18:00 | 251.83 | 245.12
2018-11-13 18:30 | 252.16 | 245.47
2018-11-13 19:00 | 253.32 | 246.75
2018-11-13 19:30 | 253.73 | 247.11
2018-11-13 20:00 | 251.56 | 244.74
2018-11-13 20:30 | 248.85 | 241.92
2018-11-13 21:00 | 246.26 | 239.17
2018-11-13 21:30 | 244.24 | 237.39
2018-11-13 22:00 | 241.78 | 234.94
2018-11-13 22:30 | 239.43 | 232.77
2018-11-13 23:00 | 237.42 | 230.77
2018-11-13 23:30 | 236.16 | 229.82
2018-11-14 | 234.67 | 228.69
2018-11-14 00:30 | 233.13 | 227.75
2018-11-14 01:00 | 232.28 | 226.89
2018-11-14 01:30 | 231.46 | 226.07
2018-11-14 02:00 | 231.2 | 225.83
2018-11-14 02:30 | 230.28 | 224.92
2018-11-14 03:00 | 229.95 | 224.63
2018-11-14 03:30 | 230.44 | 225.06
2018-11-14 04:00 | 230.3 | 224.95
2018-11-14 04:30 | 230.8 | 225.53
2018-11-14 05:00 | 231.76 | 226.55
2018-11-14 05:30 | 233.67 | 227.41
2018-11-14 06:00 | 234.61 | 228.42
2018-11-14 06:30 | 236.41 | 230.36
2018-11-14 07:00 | 236.79 | 230.74
2018-11-14 07:30 | 237.69 | 231.5
2018-11-14 08:00 | 238.29 | 231.99
2018-11-14 08:30 | 237.63 | 230.99
2018-11-14 09:00 | 237.58 | 230.83
2018-11-14 09:30 | 238.18 | 231.17
2018-11-14 10:00 | 238.36 | 231.2
2018-11-14 10:30 | 238.57 | 231.37
2018-11-14 11:00 | 238.81 | 231.63
2018-11-14 11:30 | 239.22 | 232.49
2018-11-14 12:00 | 238.49 | 231.87
2018-11-14 12:30 | 239.97 | 233.37
2018-11-14 13:00 | 240.07 | 233.32
2018-11-14 13:30 | 241.28 | 234.52
2018-11-14 14:00 | 242.21 | 235.66
2018-11-14 14:30 | 243.71 | 237.21
2018-11-14 15:00 | 243.67 | 237.16
2018-11-14 15:30 | 243.91 | 237.52
2018-11-14 16:00 | 245.13 | 239
2018-11-14 16:30 | 244.99 | 239.04
2018-11-14 17:00 | 245.12 | 239.2
2018-11-14 17:30 | 245.25 | 239.12
2018-11-14 18:00 | 245.83 | 239.69
2018-11-14 18:30 | 246.46 | 240.04
2018-11-14 19:00 | 247.95 | 241.67
2018-11-14 19:30 | 249.02 | 242.67
2018-11-14 20:00 | 248.64 | 242.03
2018-11-14 20:30 | 246.44 | 239.66
2018-11-14 21:00 | 244.22 | 237.2
2018-11-14 21:30 | 243.22 | 236.19
2018-11-14 22:00 | 241.36 | 234.14
2018-11-14 22:30 | 239.17 | 232.02
2018-11-14 23:00 | 237.77 | 230.53
2018-11-14 23:30 | 235.8 | 228.68
2018-11-15 | 234.52 | 227.32
2018-11-15 00:30 | 232.73 | 225.71
2018-11-15 01:00 | 231.76 | 224.76
2018-11-15 01:30 | 230.52 | 223.52
2018-11-15 02:00 | 229.92 | 223.07
2018-11-15 02:30 | 229.48 | 222.55
2018-11-15 03:00 | 229.24 | 222.3
2018-11-15 03:30 | 229.15 | 222.17
2018-11-15 04:00 | 228.89 | 221.9
2018-11-15 04:30 | 228.91 | 221.96
2018-11-15 05:00 | 229.89 | 222.73
2018-11-15 05:30 | 231.08 | 223.93
2018-11-15 06:00 | 231.59 | 224.6
2018-11-15 06:30 | 233.34 | 226.45
2018-11-15 07:00 | 234.22 | 227.31
2018-11-15 07:30 | 235.16 | 228.12
2018-11-15 08:00 | 235.42 | 228.57
2018-11-15 08:30 | 234.84 | 227.87
2018-11-15 09:00 | 235.44 | 228.42
2018-11-15 09:30 | 234.39 | 227.38
2018-11-15 10:00 | 235.11 | 228.25
2018-11-15 10:30 | 236.16 | 229.38
2018-11-15 11:00 | 238.27 | 231.58
2018-11-15 11:30 | 239.38 | 232.85
2018-11-15 12:00 | 241.08 | 234.41
2018-11-15 12:30 | 242.6 | 235.89
2018-11-15 13:00 | 244.29 | 237.39
2018-11-15 13:30 | 245.53 | 238.74
2018-11-15 14:00 | 246.54 | 240.2
2018-11-15 14:30 | 246.89 | 240.66
2018-11-15 15:00 | 248.35 | 242.11
2018-11-15 15:30 | 248.35 | 242.12
2018-11-15 16:00 | 248.89 | 242.74
2018-11-15 16:30 | 250.18 | 243.95
2018-11-15 17:00 | 251.73 | 245.59
2018-11-15 17:30 | 251.87 | 245.65
2018-11-15 18:00 | 252.65 | 246.38
2018-11-15 18:30 | 253.1 | 246.79
2018-11-15 19:00 | 253.61 | 247.43
2018-11-15 19:30 | 253.96 | 247.72
2018-11-15 20:00 | 251.48 | 245.06
2018-11-15 20:30 | 248.68 | 242.04
2018-11-15 21:00 | 245.86 | 239.14
2018-11-15 21:30 | 243.06 | 236.88
2018-11-15 22:00 | 240.16 | 234.06
2018-11-15 22:30 | 237.22 | 230.93
2018-11-15 23:00 | 235.71 | 229.23
2018-11-15 23:30 | 234.8 | 228.15
2018-11-16 | 233.31 | 226.85
2018-11-16 00:30 | 233.03 | 226.66
2018-11-16 01:00 | 231.01 | 225.66
2018-11-16 01:30 | 230.14 | 224.74
2018-11-16 02:00 | 229.52 | 224.08
2018-11-16 02:30 | 229.29 | 223.81
2018-11-16 03:00 | 228.7 | 223.18
2018-11-16 03:30 | 228.59 | 223.03
2018-11-16 04:00 | 228.5 | 222.95
2018-11-16 04:30 | 228.94 | 223.46
2018-11-16 05:00 | 229.46 | 224.02
2018-11-16 05:30 | 229.89 | 224.55
2018-11-16 06:00 | 230.56 | 225.43
2018-11-16 06:30 | 232.44 | 227.25
2018-11-16 07:00 | 234.36 | 228.42
2018-11-16 07:30 | 235.05 | 229.2
2018-11-16 08:00 | 234.84 | 228.83
2018-11-16 08:30 | 234.79 | 228.42
2018-11-16 09:00 | 235.42 | 229.16
2018-11-16 09:30 | 236.21 | 229.86
2018-11-16 10:00 | 237.19 | 231.05
2018-11-16 10:30 | 237.2 | 231.06
2018-11-16 11:00 | 238.79 | 232.7
2018-11-16 11:30 | 240.33 | 234.48
2018-11-16 12:00 | 242.25 | 236.56
2018-11-16 12:30 | 244.11 | 238.17
2018-11-16 13:00 | 245.72 | 239.62
2018-11-16 13:30 | 247.18 | 241.03
2018-11-16 14:00 | 248.59 | 242.58
2018-11-16 14:30 | 249.04 | 243.18
2018-11-16 15:00 | 248.87 | 242.93
2018-11-16 15:30 | 250.18 | 244.32
2018-11-16 16:00 | 252.32 | 246.5
2018-11-16 16:30 | 254.33 | 248.52
2018-11-16 17:00 | 255.57 | 249.31
2018-11-16 17:30 | 255.72 | 249.77
2018-11-16 18:00 | 254.45 | 249.38
2018-11-16 18:30 | 253.61 | 248.51
2018-11-16 19:00 | 253.48 | 248.48
2018-11-16 19:30 | 254.98 | 248.7
2018-11-16 20:00 | 253.35 | 246.43
2018-11-16 20:30 | 250.56 | 243.5
2018-11-16 21:00 | 247.66 | 240.35
2018-11-16 21:30 | 246.77 | 239.12
2018-11-16 22:00 | 244.12 | 236.38
2018-11-16 22:30 | 241.59 | 233.7
2018-11-16 23:00 | 239.84 | 231.74
2018-11-16 23:30 | 238.44 | 230.29
2018-11-17 | 236.69 | 228.73
2018-11-17 00:30 | 235.04 | 227.35
2018-11-17 01:00 | 233.77 | 226.45
2018-11-17 01:30 | 231.51 | 225.77
2018-11-17 02:00 | 230.61 | 225.27
2018-11-17 02:30 | 230.06 | 224.74
2018-11-17 03:00 | 229.62 | 224.32
2018-11-17 03:30 | 229.27 | 223.9
2018-11-17 04:00 | 229.05 | 223.64
2018-11-17 04:30 | 229.18 | 223.63
2018-11-17 05:00 | 229.32 | 223.75
2018-11-17 05:30 | 230.78 | 223.55
2018-11-17 06:00 | 231.26 | 223.82
2018-11-17 06:30 | 231.51 | 224.2
2018-11-17 07:00 | 232.19 | 225
2018-11-17 07:30 | 232.23 | 225.33
2018-11-17 08:00 | 233.67 | 226.1
2018-11-17 08:30 | 235.5 | 226.06
2018-11-17 09:00 | 235.73 | 226.66
2018-11-17 09:30 | 235.65 | 226.86
2018-11-17 10:00 | 236.74 | 227.73
2018-11-17 10:30 | 237.67 | 228.78
2018-11-17 11:00 | 238.83 | 230.03
2018-11-17 11:30 | 240.48 | 231.66
2018-11-17 12:00 | 239.18 | 231.45
2018-11-17 12:30 | 241.29 | 233.54
2018-11-17 13:00 | 243.32 | 235.18
2018-11-17 13:30 | 244.26 | 236.59
2018-11-17 14:00 | 245.08 | 237.98
2018-11-17 14:30 | 244.69 | 237.86
2018-11-17 15:00 | 244.65 | 237.93
2018-11-17 15:30 | 248.45 | 241.33
2018-11-17 16:00 | 247.04 | 239.88
2018-11-17 16:30 | 246.45 | 239.3
2018-11-17 17:00 | 246.99 | 239.91
2018-11-17 17:30 | 248.46 | 241.51
2018-11-17 18:00 | 249.08 | 242.11
2018-11-17 18:30 | 247.63 | 240.62
2018-11-17 19:00 | 247.42 | 240.41
2018-11-17 19:30 | 248.22 | 241.04
2018-11-17 20:00 | 246.6 | 239.26
2018-11-17 20:30 | 244.21 | 236.78
2018-11-17 21:00 | 242.07 | 234.34
2018-11-17 21:30 | 241.47 | 233.55
2018-11-17 22:00 | 239.62 | 231.66
2018-11-17 22:30 | 237.29 | 229.77
2018-11-17 23:00 | 235.18 | 228.37
2018-11-17 23:30 | 234.58 | 227.69
2018-11-18 | 232.87 | 226.08
2018-11-18 00:30 | 231.53 | 225.22
2018-11-18 01:00 | 229.99 | 223.6
2018-11-18 01:30 | 229.5 | 223
2018-11-18 02:00 | 228.59 | 222.22
2018-11-18 02:30 | 228.15 | 221.76
2018-11-18 03:00 | 227.85 | 221.51
2018-11-18 03:30 | 227.9 | 221.51
2018-11-18 04:00 | 227.88 | 221.49
2018-11-18 04:30 | 228.02 | 221.64
2018-11-18 05:00 | 227.97 | 221.55
2018-11-18 05:30 | 228.03 | 221.5
2018-11-18 06:00 | 228.12 | 221.57
2018-11-18 06:30 | 228.56 | 222.21
2018-11-18 07:00 | 228.82 | 222.67
2018-11-18 07:30 | 228.64 | 222.61
2018-11-18 08:00 | 228.91 | 222.91
2018-11-18 08:30 | 228.99 | 222.88
2018-11-18 09:00 | 229.17 | 222.92
2018-11-18 09:30 | 229.2 | 223.19
2018-11-18 10:00 | 229.88 | 223.91
2018-11-18 10:30 | 230.56 | 224.66
2018-11-18 11:00 | 231.6 | 225.73
2018-11-18 11:30 | 233.27 | 227.55
2018-11-18 12:00 | 235.43 | 229.78
2018-11-18 12:30 | 238.21 | 232.71
2018-11-18 13:00 | 240.87 | 235.66
2018-11-18 13:30 | 242.17 | 237.02
2018-11-18 14:00 | 242.79 | 238.07
2018-11-18 14:30 | 242.82 | 236.91
2018-11-18 15:00 | 239.77 | 233.65
2018-11-18 15:30 | 240.37 | 234.13
2018-11-18 16:00 | 240.97 | 236.2
2018-11-18 16:30 | 241.16 | 236.24
2018-11-18 17:00 | 240.7 | 235.86
2018-11-18 17:30 | 240 | 235.17
2018-11-18 18:00 | 240.86 | 236.08
2018-11-18 18:30 | 241 | 236.11
2018-11-18 19:00 | 241.52 | 236.63
2018-11-18 19:30 | 241.65 | 236.72
2018-11-18 20:00 | 240.21 | 235.16
2018-11-18 20:30 | 238.66 | 233.45
2018-11-18 21:00 | 236.97 | 231.66
2018-11-18 21:30 | 236.2 | 230.7
2018-11-18 22:00 | 234.39 | 229.26
2018-11-18 22:30 | 232.32 | 227.53
2018-11-18 23:00 | 230.92 | 225.96
2018-11-18 23:30 | 230.36 | 225.26
2018-11-19 | 229.43 | 224.29
2018-11-19 00:30 | 229.32 | 224.15
2018-11-19 01:00 | 228.73 | 223.5
2018-11-19 01:30 | 228.35 | 223.02
2018-11-19 02:00 | 227.86 | 222.54
2018-11-19 02:30 | 227.8 | 222.45
2018-11-19 03:00 | 227.57 | 222.19
2018-11-19 03:30 | 227.81 | 222.49
2018-11-19 04:00 | 227.86 | 222.54
2018-11-19 04:30 | 227.91 | 222.69
2018-11-19 05:00 | 228.76 | 223.51
2018-11-19 05:30 | 229.63 | 224.44
2018-11-19 06:00 | 230.46 | 225.43
2018-11-19 06:30 | 232.35 | 227.25
2018-11-19 07:00 | 233.77 | 228.33
2018-11-19 07:30 | 235.31 | 229.82
2018-11-19 08:00 | 235.65 | 230.2
2018-11-19 08:30 | 234.38 | 229.06
2018-11-19 09:00 | 233.7 | 228.49
2018-11-19 09:30 | 233.12 | 227.77
2018-11-19 10:00 | 233.38 | 227.92
2018-11-19 10:30 | 233.78 | 227.94
2018-11-19 11:00 | 233.41 | 227.53
2018-11-19 11:30 | 234.55 | 228.6
2018-11-19 12:00 | 234.7 | 228.84
2018-11-19 12:30 | 233.42 | 227.59
2018-11-19 13:00 | 234.06 | 228.28
2018-11-19 13:30 | 234.56 | 228.71
2018-11-19 14:00 | 235.96 | 230.18
2018-11-19 14:30 | 237.29 | 231.47
2018-11-19 15:00 | 237.81 | 231.87
2018-11-19 15:30 | 238.63 | 232.78
2018-11-19 16:00 | 240.38 | 234.61
2018-11-19 16:30 | 241.99 | 236.28
2018-11-19 17:00 | 242.67 | 237.02
2018-11-19 17:30 | 243.23 | 237.41
2018-11-19 18:00 | 244.05 | 238.18
2018-11-19 18:30 | 243.69 | 237.84
2018-11-19 19:00 | 243.89 | 238.06
2018-11-19 19:30 | 245.87 | 239.99
2018-11-19 20:00 | 244.61 | 238.66
2018-11-19 20:30 | 242.61 | 236.42
2018-11-19 21:00 | 240.88 | 234.74
2018-11-19 21:30 | 239.12 | 233.74
2018-11-19 22:00 | 236.92 | 231.45
2018-11-19 22:30 | 234.25 | 228.72
2018-11-19 23:00 | 232.33 | 226.78
2018-11-19 23:30 | 231.01 | 226.07
2018-11-20 | 229.11 | 224.51
2018-11-20 00:30 | 228.78 | 223.65
2018-11-20 01:00 | 227.6 | 222.64
2018-11-20 01:30 | 227.53 | 222.51
2018-11-20 02:00 | 226.9 | 221.95
2018-11-20 02:30 | 226.78 | 221.81
2018-11-20 03:00 | 226.14 | 221.13
2018-11-20 03:30 | 226.03 | 221.01
2018-11-20 04:00 | 225.6 | 220.61
2018-11-20 04:30 | 226.01 | 220.89
2018-11-20 05:00 | 226.66 | 221.56
2018-11-20 05:30 | 228.09 | 222.99
2018-11-20 06:00 | 228.77 | 223.91
2018-11-20 06:30 | 230.64 | 225.78
2018-11-20 07:00 | 231.45 | 226.77
2018-11-20 07:30 | 232.36 | 227.58
2018-11-20 08:00 | 232.55 | 227.81
2018-11-20 08:30 | 231.29 | 226.5
2018-11-20 09:00 | 230.37 | 225.6
2018-11-20 09:30 | 228.69 | 224.31
2018-11-20 10:00 | 227.92 | 224.41
2018-11-20 10:30 | 228.68 | 225.18
2018-11-20 11:00 | 229.12 | 225.66
2018-11-20 11:30 | 228.71 | 225.26
2018-11-20 12:00 | 229.06 | 225.64
2018-11-20 12:30 | 229.4 | 226.04
2018-11-20 13:00 | 230.17 | 226.81
2018-11-20 13:30 | 227.76 | 224.3
2018-11-20 14:00 | 228.75 | 225.36
2018-11-20 14:30 | 229.65 | 226.25
2018-11-20 15:00 | 230.41 | 226.97
2018-11-20 15:30 | 228.95 | 225.49
2018-11-20 16:00 | 232.51 | 229.16
2018-11-20 16:30 | 232.28 | 228.87
2018-11-20 17:00 | 232.67 | 229.07
2018-11-20 17:30 | 232.33 | 228.67
2018-11-20 18:00 | 233.44 | 229.76
2018-11-20 18:30 | 234.47 | 230.55
2018-11-20 19:00 | 234.98 | 231.04
2018-11-20 19:30 | 235.65 | 231.44
2018-11-20 20:00 | 234.18 | 229.77
2018-11-20 20:30 | 232.13 | 227.6
2018-11-20 21:00 | 229.88 | 225.18
2018-11-20 21:30 | 228.5 | 223.85
2018-11-20 22:00 | 227.17 | 222.53
2018-11-20 22:30 | 224.8 | 220.07
2018-11-20 23:00 | 223.69 | 219.06
2018-11-20 23:30 | 222.42 | 218
2018-11-21 | 221.18 | 216.91
2018-11-21 00:30 | 220.5 | 216.15
2018-11-21 01:00 | 219.69 | 215.27
2018-11-21 01:30 | 219.84 | 215.54
2018-11-21 02:00 | 220.25 | 216.03
2018-11-21 02:30 | 219.79 | 215.61
2018-11-21 03:00 | 219.51 | 215.31
2018-11-21 03:30 | 219.36 | 215.17
2018-11-21 04:00 | 219.78 | 215.61
2018-11-21 04:30 | 219.76 | 215.64
2018-11-21 05:00 | 220.62 | 216.52
2018-11-21 05:30 | 221.92 | 217.87
2018-11-21 06:00 | 222.77 | 218.7
2018-11-21 06:30 | 224.76 | 220.42
2018-11-21 07:00 | 226.48 | 221.66
2018-11-21 07:30 | 227.3 | 222.38
2018-11-21 08:00 | 226.68 | 222.65
2018-11-21 08:30 | 225.61 | 221.84
2018-11-21 09:00 | 226.66 | 222.97
2018-11-21 09:30 | 226.43 | 222.75
2018-11-21 10:00 | 227.01 | 223.31
2018-11-21 10:30 | 225.85 | 222.14
2018-11-21 11:00 | 225.52 | 221.82
2018-11-21 11:30 | 225.98 | 222.31
2018-11-21 12:00 | 225.96 | 222.3
2018-11-21 12:30 | 226.79 | 223.16
2018-11-21 13:00 | 225.37 | 221.65
2018-11-21 13:30 | 225.74 | 222
2018-11-21 14:00 | 226.41 | 222.73
2018-11-21 14:30 | 225.93 | 222.27
2018-11-21 15:00 | 224.97 | 221.21
2018-11-21 15:30 | 224.45 | 220.67
2018-11-21 16:00 | 224.31 | 220.61
2018-11-21 16:30 | 223.54 | 219.83
2018-11-21 17:00 | 223.85 | 220.13
2018-11-21 17:30 | 223.88 | 220.09
2018-11-21 18:00 | 225.5 | 221.72
2018-11-21 18:30 | 212.45 | 209.3
2018-11-21 19:00 | 199.24 | 196.24
2018-11-21 19:30 | 197.89 | 194.93
2018-11-21 20:00 | 197.89 | 194.91
2018-11-21 20:30 | 198.06 | 195.15
2018-11-21 21:00 | 212.37 | 208.05
2018-11-21 21:30 | 216.7 | 212.03
2018-11-21 22:00 | 214.41 | 209.69
2018-11-21 22:30 | 213.33 | 208.53
2018-11-21 23:00 | 212.08 | 207.32
2018-11-21 23:30 | 211.53 | 207.13
2018-11-22 | 210.59 | 206.17
2018-11-22 00:30 | 209.61 | 205.27
2018-11-22 01:00 | 208.86 | 204.41
2018-11-22 01:30 | 208.39 | 203.7
2018-11-22 02:00 | 208.09 | 203.38
2018-11-22 02:30 | 207.82 | 203.05
2018-11-22 03:00 | 207.59 | 202.81
2018-11-22 03:30 | 207.12 | 202.29
2018-11-22 04:00 | 206 | 201.04
2018-11-22 04:30 | 205.9 | 200.96
2018-11-22 05:00 | 207.37 | 201.75
2018-11-22 05:30 | 208 | 202.5
2018-11-22 06:00 | 208.84 | 203.19
2018-11-22 06:30 | 210.44 | 204.64
2018-11-22 07:00 | 211.91 | 205.57
2018-11-22 07:30 | 213.42 | 207.27
2018-11-22 08:00 | 212.86 | 206.54
2018-11-22 08:30 | 212.16 | 205.8
2018-11-22 09:00 | 210.63 | 204.26
2018-11-22 09:30 | 208.66 | 202.7
2018-11-22 10:00 | 209.32 | 203.82
2018-11-22 10:30 | 208.14 | 202.44
2018-11-22 11:00 | 206.9 | 201.27
2018-11-22 11:30 | 207.21 | 201.43
2018-11-22 12:00 | 208.28 | 202.66
2018-11-22 12:30 | 207.93 | 202.17
2018-11-22 13:00 | 209.76 | 203.93
2018-11-22 13:30 | 211.8 | 205.98
2018-11-22 14:00 | 212.22 | 206.67
2018-11-22 14:30 | 213.33 | 207.99
2018-11-22 15:00 | 214.04 | 208.73
2018-11-22 15:30 | 213.76 | 208.32
2018-11-22 16:00 | 214.16 | 208.87
2018-11-22 16:30 | 215.1 | 209.6
2018-11-22 17:00 | 215.74 | 210.21
2018-11-22 17:30 | 216.59 | 210.99
2018-11-22 18:00 | 217.8 | 212.14
2018-11-22 18:30 | 219.27 | 213.53
2018-11-22 19:00 | 220.76 | 215.19
2018-11-22 19:30 | 221.79 | 216.25
2018-11-22 20:00 | 222.21 | 215.29
2018-11-22 20:30 | 221.67 | 214.04
2018-11-22 21:00 | 220.24 | 212.4
2018-11-22 21:30 | 219.01 | 212.12
2018-11-22 22:00 | 216.99 | 210.52
2018-11-22 22:30 | 215.31 | 208.83
2018-11-22 23:00 | 214.21 | 207.37
2018-11-22 23:30 | 213.71 | 206.61
2018-11-23 | 212.01 | 205.28
2018-11-23 00:30 | 211.1 | 204.28
2018-11-23 01:00 | 209.74 | 202.75
2018-11-23 01:30 | 209.77 | 202.59
2018-11-23 02:00 | 208.05 | 200.71
2018-11-23 02:30 | 207.98 | 200.55
2018-11-23 03:00 | 208.27 | 201.07
2018-11-23 03:30 | 208.05 | 200.86
2018-11-23 04:00 | 208.6 | 201.39
2018-11-23 04:30 | 208.75 | 201.53
2018-11-23 05:00 | 209.85 | 202.64
2018-11-23 05:30 | 211.23 | 203.37
2018-11-23 06:00 | 213.21 | 205.1
2018-11-23 06:30 | 214.09 | 206.07
2018-11-23 07:00 | 214.58 | 206.44
2018-11-23 07:30 | 214.81 | 206.71
2018-11-23 08:00 | 214.66 | 206.39
2018-11-23 08:30 | 214.4 | 206.21
2018-11-23 09:00 | 212.24 | 203.82
2018-11-23 09:30 | 211.94 | 203.12
2018-11-23 10:00 | 212.17 | 203.46
2018-11-23 10:30 | 211.82 | 203.21
2018-11-23 11:00 | 211.56 | 202.84
2018-11-23 11:30 | 212.04 | 203.4
2018-11-23 12:00 | 212.47 | 203.7
2018-11-23 12:30 | 211.27 | 202.46
2018-11-23 13:00 | 211.43 | 202.47
2018-11-23 13:30 | 211.66 | 202.6
2018-11-23 14:00 | 211.4 | 202.35
2018-11-23 14:30 | 213.09 | 203.99
2018-11-23 15:00 | 213.77 | 204.75
2018-11-23 15:30 | 214.15 | 205.26
2018-11-23 16:00 | 214.85 | 206.2
2018-11-23 16:30 | 215.67 | 207.15
2018-11-23 17:00 | 234.27 | 231.12
2018-11-23 17:30 | 234.2 | 231.08
2018-11-23 18:00 | 233.66 | 230.53
2018-11-23 18:30 | 233.66 | 230.55
2018-11-23 19:00 | 233.53 | 230.48
2018-11-23 19:30 | 233.73 | 230.64
2018-11-23 20:00 | 233.85 | 230.85
2018-11-23 20:30 | 234.67 | 231.77
2018-11-23 21:00 | 220.03 | 213.45
2018-11-23 21:30 | 219.32 | 211.65
2018-11-23 22:00 | 217.93 | 210.31
2018-11-23 22:30 | 215.71 | 208.77
2018-11-23 23:00 | 214.06 | 207.17
2018-11-23 23:30 | 214.32 | 207.22
2018-11-24 | 212.5 | 205.27
2018-11-24 00:30 | 211.98 | 204.83
2018-11-24 01:00 | 211.04 | 204.06
2018-11-24 01:30 | 210.64 | 203.6
2018-11-24 02:00 | 210.76 | 203.68
2018-11-24 02:30 | 210.65 | 203.54
2018-11-24 03:00 | 210.52 | 203.39
2018-11-24 03:30 | 209.63 | 202.49
2018-11-24 04:00 | 210.52 | 203.46
2018-11-24 04:30 | 209.98 | 202.81
2018-11-24 05:00 | 209.28 | 202.09
2018-11-24 05:30 | 208.5 | 201.26
2018-11-24 06:00 | 209.12 | 201.83
2018-11-24 06:30 | 208.5 | 201.42
2018-11-24 07:00 | 207.93 | 200.89
2018-11-24 07:30 | 208.09 | 200.83
2018-11-24 08:00 | 207.67 | 200.5
2018-11-24 08:30 | 209.67 | 202.32
2018-11-24 09:00 | 210.53 | 202.96
2018-11-24 09:30 | 210.12 | 202.51
2018-11-24 10:00 | 209.23 | 201.62
2018-11-24 10:30 | 209.59 | 201.96
2018-11-24 11:00 | 209.32 | 201.5
2018-11-24 11:30 | 208.58 | 200.94
2018-11-24 12:00 | 208.65 | 201
2018-11-24 12:30 | 208.74 | 201.02
2018-11-24 13:00 | 209.37 | 201.59
2018-11-24 13:30 | 210.32 | 202.47
2018-11-24 14:00 | 210.26 | 202.49
2018-11-24 14:30 | 210.53 | 202.85
2018-11-24 15:00 | 211.33 | 203.69
2018-11-24 15:30 | 213 | 205.38
2018-11-24 16:00 | 214.96 | 207.3
2018-11-24 16:30 | 217.33 | 209.64
2018-11-24 17:00 | 218.74 | 211.24
2018-11-24 17:30 | 220.7 | 213.03
2018-11-24 18:00 | 222.5 | 214.83
2018-11-24 18:30 | 222.88 | 215.24
2018-11-24 19:00 | 223.57 | 215.91
2018-11-24 19:30 | 224.15 | 216.28
2018-11-24 20:00 | 223.81 | 215.69
2018-11-24 20:30 | 221.87 | 213.66
2018-11-24 21:00 | 221.52 | 213.21
2018-11-24 21:30 | 220.68 | 212.83
2018-11-24 22:00 | 218.9 | 210.99
2018-11-24 22:30 | 218.02 | 210.18
2018-11-24 23:00 | 215.76 | 207.83
2018-11-24 23:30 | 214.99 | 207.24
2018-11-25 | 213.93 | 206.49
2018-11-25 00:30 | 212.93 | 205.54
2018-11-25 01:00 | 212.71 | 205.25
2018-11-25 01:30 | 211.72 | 204.21
2018-11-25 02:00 | 211.25 | 203.79
2018-11-25 02:30 | 211.05 | 203.64
2018-11-25 03:00 | 210.97 | 203.47
2018-11-25 03:30 | 210.5 | 203.02
2018-11-25 04:00 | 210.36 | 202.86
2018-11-25 04:30 | 210.65 | 203.05
2018-11-25 05:00 | 210.73 | 202.99
2018-11-25 05:30 | 211.7 | 203.86
2018-11-25 06:00 | 211.31 | 203.4
2018-11-25 06:30 | 211.32 | 203.58
2018-11-25 07:00 | 211.88 | 204.51
2018-11-25 07:30 | 211.24 | 203.96
2018-11-25 08:00 | 211.92 | 203.26
2018-11-25 08:30 | 211.28 | 202.15
2018-11-25 09:00 | 211.14 | 202.22
2018-11-25 09:30 | 211.73 | 202.77
2018-11-25 10:00 | 211.62 | 203.49
2018-11-25 10:30 | 212.17 | 204.15
2018-11-25 11:00 | 212.68 | 204.55
2018-11-25 11:30 | 213.89 | 205.78
2018-11-25 12:00 | 215.96 | 207.89
2018-11-25 12:30 | 217.67 | 210.21
2018-11-25 13:00 | 218.61 | 211.89
2018-11-25 13:30 | 220.23 | 213.52
2018-11-25 14:00 | 221.02 | 213.78
2018-11-25 14:30 | 222.17 | 215.01
2018-11-25 15:00 | 223.12 | 216.08
2018-11-25 15:30 | 224.25 | 217.22
2018-11-25 16:00 | 225.49 | 218.09
2018-11-25 16:30 | 225.15 | 217.07
2018-11-25 17:00 | 227.44 | 219.86
2018-11-25 17:30 | 226.56 | 220.15
2018-11-25 18:00 | 216.53 | 213.57
2018-11-25 18:30 | 216.97 | 213.98
2018-11-25 19:00 | 217.2 | 213.95
2018-11-25 19:30 | 198.18 | 191.46
2018-11-25 20:00 | 207.64 | 202.66
2018-11-25 20:30 | 223.95 | 220.64
2018-11-25 21:00 | 226.2 | 222.83
2018-11-25 21:30 | 206.38 | 201.07
2018-11-25 22:00 | 200.89 | 194.66
2018-11-25 22:30 | 202.84 | 196.75
2018-11-25 23:00 | 213.77 | 205.36
2018-11-25 23:30 | 216.79 | 207.7
2018-11-26 | 215.1 | 206.67
2018-11-26 00:30 | 213.96 | 205.8
2018-11-26 01:00 | 212.71 | 204.58
2018-11-26 01:30 | 211.33 | 204
2018-11-26 02:00 | 210.42 | 203.01
2018-11-26 02:30 | 210.14 | 202.69
2018-11-26 03:00 | 209.86 | 202.37
2018-11-26 03:30 | 210.27 | 202.77
2018-11-26 04:00 | 210.06 | 202.52
2018-11-26 04:30 | 210.31 | 202.86
2018-11-26 05:00 | 211.07 | 203.61
2018-11-26 05:30 | 211.53 | 204.13
2018-11-26 06:00 | 212.47 | 205.14
2018-11-26 06:30 | 213.89 | 206.57
2018-11-26 07:00 | 215.22 | 207.25
2018-11-26 07:30 | 216.95 | 207.71
2018-11-26 08:00 | 217.49 | 208.17
2018-11-26 08:30 | 217.36 | 208.08
2018-11-26 09:00 | 217.02 | 207.75
2018-11-26 09:30 | 217.2 | 207.83
2018-11-26 10:00 | 217.86 | 208.43
2018-11-26 10:30 | 218.17 | 208.66
2018-11-26 11:00 | 218.59 | 209.02
2018-11-26 11:30 | 219.23 | 209.82
2018-11-26 12:00 | 220.25 | 210.93
2018-11-26 12:30 | 220.58 | 211.3
2018-11-26 13:00 | 222.05 | 212.76
2018-11-26 13:30 | 223.11 | 214.03
2018-11-26 14:00 | 224.76 | 215.85
2018-11-26 14:30 | 226.84 | 217.94
2018-11-26 15:00 | 227.38 | 218.64
2018-11-26 15:30 | 227.41 | 219.27
2018-11-26 16:00 | 228.19 | 220.7
2018-11-26 16:30 | 229.42 | 221.91
2018-11-26 17:00 | 231.05 | 223.64
2018-11-26 17:30 | 232.72 | 224.64
2018-11-26 18:00 | 234.2 | 226.35
2018-11-26 18:30 | 234.2 | 226.57
2018-11-26 19:00 | 234.8 | 227.2
2018-11-26 19:30 | 235.48 | 227.9
2018-11-26 20:00 | 234.16 | 226.26
2018-11-26 20:30 | 231.71 | 223.5
2018-11-26 21:00 | 229.08 | 220.66
2018-11-26 21:30 | 226.53 | 218.81
2018-11-26 22:00 | 224.19 | 216.39
2018-11-26 22:30 | 221.18 | 213.54
2018-11-26 23:00 | 219.43 | 211.63
2018-11-26 23:30 | 217.84 | 210.13
2018-11-27 | 216.07 | 208.34
2018-11-27 00:30 | 215.55 | 207.85
2018-11-27 01:00 | 214.53 | 206.92
2018-11-27 01:30 | 214.1 | 206.04
2018-11-27 02:00 | 213.23 | 205.69
2018-11-27 02:30 | 212.77 | 205.27
2018-11-27 03:00 | 212.78 | 205.17
2018-11-27 03:30 | 212.6 | 204.87
2018-11-27 04:00 | 212.64 | 204.8
2018-11-27 04:30 | 213.56 | 205.82
2018-11-27 05:00 | 214.25 | 206.46
2018-11-27 05:30 | 215.19 | 207.51
2018-11-27 06:00 | 215.63 | 207.97
2018-11-27 06:30 | 217.72 | 210.15
2018-11-27 07:00 | 218.59 | 210.6
2018-11-27 07:30 | 219.26 | 211.7
2018-11-27 08:00 | 219.71 | 211.26
2018-11-27 08:30 | 218.98 | 209.86
2018-11-27 09:00 | 219.17 | 210.23
2018-11-27 09:30 | 217.99 | 209.15
2018-11-27 10:00 | 218.64 | 209.7
2018-11-27 10:30 | 218.89 | 209.81
2018-11-27 11:00 | 219.56 | 210.58
2018-11-27 11:30 | 221.37 | 212.44
2018-11-27 12:00 | 223.53 | 214.6
2018-11-27 12:30 | 224.4 | 215.55
2018-11-27 13:00 | 225.45 | 216.55
2018-11-27 13:30 | 225.67 | 216.74
2018-11-27 14:00 | 227.51 | 218.42
2018-11-27 14:30 | 232.12 | 223.21
2018-11-27 15:00 | 232.57 | 224.1
2018-11-27 15:30 | 234.12 | 225.95
2018-11-27 16:00 | 235.59 | 227.88
2018-11-27 16:30 | 236.71 | 228.95
2018-11-27 17:00 | 238.29 | 230.47
2018-11-27 17:30 | 236.38 | 228.19
2018-11-27 18:00 | 239.26 | 231.36
2018-11-27 18:30 | 239.24 | 231.36
2018-11-27 19:00 | 239.22 | 231.41
2018-11-27 19:30 | 237.93 | 229.88
2018-11-27 20:00 | 236 | 227.69
2018-11-27 20:30 | 233.63 | 225.25
2018-11-27 21:00 | 229.12 | 221.55
2018-11-27 21:30 | 226.39 | 219.17
2018-11-27 22:00 | 223.85 | 216.56
2018-11-27 22:30 | 220.68 | 213.41
2018-11-27 23:00 | 216.16 | 211.43
2018-11-27 23:30 | 214.32 | 210.18
2018-11-28 | 206.9 | 201.28
2018-11-28 00:30 | 202.12 | 194.75
2018-11-28 01:00 | 200.63 | 193.15
2018-11-28 01:30 | 200.33 | 193.02
2018-11-28 02:00 | 199.88 | 192.43
2018-11-28 02:30 | 198.85 | 191.48
2018-11-28 03:00 | 198.67 | 191.33
2018-11-28 03:30 | 197.84 | 190.53
2018-11-28 04:00 | 197.54 | 190.18
2018-11-28 04:30 | 197.43 | 190.17
2018-11-28 05:00 | 197.83 | 190.55
2018-11-28 05:30 | 198.27 | 191.15
2018-11-28 06:00 | 199.74 | 192.11
2018-11-28 06:30 | 201.21 | 193.56
2018-11-28 07:00 | 202.12 | 194.17
2018-11-28 07:30 | 203.58 | 194.95
2018-11-28 08:00 | 202.35 | 193.64
2018-11-28 08:30 | 203.69 | 195.14
2018-11-28 09:00 | 201.52 | 192.81
2018-11-28 09:30 | 201.37 | 193.3
2018-11-28 10:00 | 203.45 | 195.86
2018-11-28 10:30 | 204.47 | 196.76
2018-11-28 11:00 | 204.55 | 196.97
2018-11-28 11:30 | 205.16 | 197.5
2018-11-28 12:00 | 205.8 | 198.22
2018-11-28 12:30 | 205.18 | 197.74
2018-11-28 13:00 | 206.48 | 198.73
2018-11-28 13:30 | 207.36 | 199.35
2018-11-28 14:00 | 208.14 | 200.38
2018-11-28 14:30 | 208.87 | 201.33
2018-11-28 15:00 | 208.78 | 201.18
2018-11-28 15:30 | 209.46 | 201.93
2018-11-28 16:00 | 211.1 | 203.79
2018-11-28 16:30 | 212.51 | 204.92
2018-11-28 17:00 | 213.77 | 206.08
2018-11-28 17:30 | 214.6 | 207
2018-11-28 18:00 | 214.51 | 206.51
2018-11-28 18:30 | 214.02 | 205.68
2018-11-28 19:00 | 214.45 | 206.16
2018-11-28 19:30 | 215.05 | 206.58
2018-11-28 20:00 | 214.43 | 205.72
2018-11-28 20:30 | 212.93 | 204.04
2018-11-28 21:00 | 210.86 | 201.92
2018-11-28 21:30 | 209.24 | 200.87
2018-11-28 22:00 | 207.37 | 198.87
2018-11-28 22:30 | 204.75 | 196.3
2018-11-28 23:00 | 203.37 | 194.78
2018-11-28 23:30 | 202.33 | 193.72
2018-11-29 | 200.45 | 192.28
2018-11-29 00:30 | 199.22 | 191.3
2018-11-29 01:00 | 198.38 | 190.7
2018-11-29 01:30 | 197.74 | 190.01
2018-11-29 02:00 | 198.23 | 189.76
2018-11-29 02:30 | 197.78 | 189.33
2018-11-29 03:00 | 197.4 | 188.92
2018-11-29 03:30 | 196.98 | 188.42
2018-11-29 04:00 | 197.16 | 188.4
2018-11-29 04:30 | 197.48 | 188.72
2018-11-29 05:00 | 197.85 | 189.2
2018-11-29 05:30 | 197.48 | 188.62
2018-11-29 06:00 | 198.41 | 189.37
2018-11-29 06:30 | 202.52 | 192.16
2018-11-29 07:00 | 203.49 | 192.73
2018-11-29 07:30 | 200.95 | 190.78
2018-11-29 08:00 | 198.4 | 189.94
2018-11-29 08:30 | 206.67 | 199.26
2018-11-29 09:00 | 202.81 | 195.57
2018-11-29 09:30 | 199.09 | 191.93
2018-11-29 10:00 | 199.15 | 191.97
2018-11-29 10:30 | 199.64 | 192.39
2018-11-29 11:00 | 200.65 | 193.31
2018-11-29 11:30 | 201.61 | 194.24
2018-11-29 12:00 | 202.68 | 195.37
2018-11-29 12:30 | 203.69 | 196.34
2018-11-29 13:00 | 205.25 | 197.86
2018-11-29 13:30 | 206.04 | 198.34
2018-11-29 14:00 | 207.62 | 200.08
2018-11-29 14:30 | 208.92 | 200.85
2018-11-29 15:00 | 209.42 | 201.23
2018-11-29 15:30 | 209.66 | 201.41
2018-11-29 16:00 | 211.8 | 203.57
2018-11-29 16:30 | 213.65 | 205.37
2018-11-29 17:00 | 215.1 | 206.78
2018-11-29 17:30 | 215.93 | 207.4
2018-11-29 18:00 | 217.38 | 208.92
2018-11-29 18:30 | 217.89 | 209.38
2018-11-29 19:00 | 218.61 | 210.24
2018-11-29 19:30 | 219.27 | 210.71
2018-11-29 20:00 | 218.96 | 210.26
2018-11-29 20:30 | 218.23 | 209.21
2018-11-29 21:00 | 216.22 | 207.17
2018-11-29 21:30 | 214.34 | 205.84
2018-11-29 22:00 | 212.17 | 203.75
2018-11-29 22:30 | 209.81 | 201.25
2018-11-29 23:00 | 208.11 | 199.54
2018-11-29 23:30 | 207.32 | 198.66
2018-11-30 | 205.62 | 197.14
2018-11-30 00:30 | 204.68 | 196.03
2018-11-30 01:00 | 203.41 | 195.25
2018-11-30 01:30 | 202.7 | 194.49
2018-11-30 02:00 | 202.39 | 194.29
2018-11-30 02:30 | 201.84 | 193.62
2018-11-30 03:00 | 201.84 | 193.5
2018-11-30 03:30 | 201.35 | 193.01
2018-11-30 04:00 | 201.96 | 193.66
2018-11-30 04:30 | 202.54 | 194.35
2018-11-30 05:00 | 203.1 | 195
2018-11-30 05:30 | 203.89 | 195.85
2018-11-30 06:00 | 204.53 | 196.75
2018-11-30 06:30 | 206.32 | 198.08
2018-11-30 07:00 | 206.49 | 198.14
2018-11-30 07:30 | 207.27 | 198.69
2018-11-30 08:00 | 207.34 | 198.83
2018-11-30 08:30 | 206.04 | 197.57
2018-11-30 09:00 | 203.58 | 197.1
2018-11-30 09:30 | 202.44 | 196.76
2018-11-30 10:00 | 200.89 | 193.95
2018-11-30 10:30 | 196.46 | 187.4
2018-11-30 11:00 | 195.36 | 185.84
2018-11-30 11:30 | 196.02 | 186.72
2018-11-30 12:00 | 196.84 | 187.64
2018-11-30 12:30 | 197.37 | 187.9
2018-11-30 13:00 | 198.89 | 189.51
2018-11-30 13:30 | 199.99 | 190.69
2018-11-30 14:00 | 201.25 | 191.99
2018-11-30 14:30 | 202.32 | 193.17
2018-11-30 15:00 | 203.38 | 194.27
2018-11-30 15:30 | 204.21 | 194.86
2018-11-30 16:00 | 207.16 | 197.38
2018-11-30 16:30 | 207.83 | 197.9
2018-11-30 17:00 | 206.24 | 196.27
2018-11-30 17:30 | 206.91 | 196.73
2018-11-30 18:00 | 207.12 | 196.85
2018-11-30 18:30 | 206.86 | 196.48
2018-11-30 19:00 | 206.05 | 195.66
2018-11-30 19:30 | 206.61 | 196.05
2018-11-30 20:00 | 204.88 | 194.22
2018-11-30 20:30 | 201.71 | 192.24
2018-11-30 21:00 | 198.62 | 189.34
2018-11-30 21:30 | 196.49 | 187.79
2018-11-30 22:00 | 194.52 | 186.09
2018-11-30 22:30 | 193 | 184.44
2018-11-30 23:00 | 192.03 | 183.31
2018-11-30 23:30 | 190.65 | 182.09
2018-12-01 | 188.92 | 180.46
2018-12-01 00:30 | 188.27 | 179.73
2018-12-01 01:00 | 186.97 | 178.57
2018-12-01 01:30 | 186.31 | 177.85
2018-12-01 02:00 | 185.78 | 177.36
2018-12-01 02:30 | 185.29 | 176.88
2018-12-01 03:00 | 184.77 | 176.35
2018-12-01 03:30 | 184.76 | 176.31
2018-12-01 04:00 | 184.87 | 176.41
2018-12-01 04:30 | 184.96 | 176.6
2018-12-01 05:00 | 185.25 | 176.85
2018-12-01 05:30 | 186.42 | 177.71
2018-12-01 06:00 | 185.64 | 177.22
2018-12-01 06:30 | 184.22 | 175.72
2018-12-01 07:00 | 184.48 | 176.16
2018-12-01 07:30 | 186.43 | 177.94
2018-12-01 08:00 | 186.57 | 177.73
2018-12-01 08:30 | 187.05 | 178.19
2018-12-01 09:00 | 187.64 | 178.31
2018-12-01 09:30 | 187.88 | 178.53
2018-12-01 10:00 | 188.56 | 178.9
2018-12-01 10:30 | 188.91 | 179.41
2018-12-01 11:00 | 188.85 | 179.21
2018-12-01 11:30 | 187.3 | 177.2
2018-12-01 12:00 | 190.12 | 180.2
2018-12-01 12:30 | 191.81 | 181.97
2018-12-01 13:00 | 190.79 | 180.97
2018-12-01 13:30 | 189.59 | 178.94
2018-12-01 14:00 | 190.03 | 179.41
2018-12-01 14:30 | 190.19 | 179.7
2018-12-01 15:00 | 190.57 | 180.78
2018-12-01 15:30 | 188.41 | 180.17
2018-12-01 16:00 | 190.41 | 182.11
2018-12-01 16:30 | 192.68 | 184.26
2018-12-01 17:00 | 194.22 | 185.95
2018-12-01 17:30 | 195.43 | 187.2
2018-12-01 18:00 | 196.76 | 188.67
2018-12-01 18:30 | 196.5 | 188.43
2018-12-01 19:00 | 196.35 | 188.2
2018-12-01 19:30 | 196.23 | 187.98
2018-12-01 20:00 | 194.67 | 186.3
2018-12-01 20:30 | 192.23 | 183.52
2018-12-01 21:00 | 188.3 | 179.33
2018-12-01 21:30 | 185.5 | 177.45
2018-12-01 22:00 | 182.27 | 174.23
2018-12-01 22:30 | 179.6 | 171.92
2018-12-01 23:00 | 177.87 | 170.11
2018-12-01 23:30 | 176.18 | 168.64
2018-12-02 | 173.85 | 166.51
2018-12-02 00:30 | 172.27 | 164.99
2018-12-02 01:00 | 171.43 | 164.09
2018-12-02 01:30 | 170.6 | 163.19
2018-12-02 02:00 | 168.85 | 161.45
2018-12-02 02:30 | 167.21 | 159.97
2018-12-02 03:00 | 165.94 | 158.68
2018-12-02 03:30 | 164.72 | 157.6
2018-12-02 04:00 | 163.8 | 156.78
2018-12-02 04:30 | 163.38 | 156.41
2018-12-02 05:00 | 163.31 | 156.44
2018-12-02 05:30 | 162.78 | 155.65
2018-12-02 06:00 | 148.04 | 140.9
2018-12-02 06:30 | 148.67 | 142.03
2018-12-02 07:00 | 148.56 | 142.25
2018-12-02 07:30 | 147.83 | 141.37
2018-12-02 08:00 | 149 | 142.26
2018-12-02 08:30 | 149.66 | 143.15
2018-12-02 09:00 | 148.58 | 142.11
2018-12-02 09:30 | 156.69 | 149.92
2018-12-02 10:00 | 168.33 | 160.75
2018-12-02 10:30 | 174.33 | 166.36
2018-12-02 11:00 | 174.78 | 166.89
2018-12-02 11:30 | 176.26 | 168.54
2018-12-02 12:00 | 178.32 | 170.78
2018-12-02 12:30 | 180.16 | 173.03
2018-12-02 13:00 | 182 | 175.05
2018-12-02 13:30 | 183 | 176.11
2018-12-02 14:00 | 179.1 | 172.31
2018-12-02 14:30 | 155.53 | 152.35
2018-12-02 15:00 | 169.66 | 164.16
2018-12-02 15:30 | 183.14 | 176.45
2018-12-02 16:00 | 185.33 | 178.96
2018-12-02 16:30 | 162.46 | 157.57
2018-12-02 17:00 | 152.55 | 146.96
2018-12-02 17:30 | 201.11 | 194.32
2018-12-02 18:00 | 202.67 | 196.28
2018-12-02 18:30 | 203.32 | 196.96
2018-12-02 19:00 | 202.14 | 195.69
2018-12-02 19:30 | 202.69 | 196.31
2018-12-02 20:00 | 202.28 | 195.41
2018-12-02 20:30 | 199.56 | 192.24
2018-12-02 21:00 | 196.37 | 188.42
2018-12-02 21:30 | 193.7 | 185.61
2018-12-02 22:00 | 189.39 | 181.21
2018-12-02 22:30 | 185.27 | 176.93
2018-12-02 23:00 | 183.89 | 175.07
2018-12-02 23:30 | 182.22 | 173.07
2018-12-03 | 159.09 | 149.57
2018-12-03 00:30 | 152.58 | 143.63
2018-12-03 01:00 | 151.37 | 142.46
2018-12-03 01:30 | 150.06 | 141.25
2018-12-03 02:00 | 148.94 | 140.23
2018-12-03 02:30 | 148.02 | 139.17
2018-12-03 03:00 | 146.89 | 137.98
2018-12-03 03:30 | 146.09 | 137.06
2018-12-03 04:00 | 146.04 | 136.81
2018-12-03 04:30 | 145.89 | 136.81
2018-12-03 05:00 | 145.61 | 136.56
2018-12-03 05:30 | 145.8 | 136.95
2018-12-03 06:00 | 147.32 | 138.42
2018-12-03 06:30 | 149.99 | 140.4
2018-12-03 07:00 | 153.7 | 141.73
2018-12-03 07:30 | 153.36 | 142.9
2018-12-03 08:00 | 152.69 | 142.21
2018-12-03 08:30 | 152.59 | 142.28
2018-12-03 09:00 | 152.57 | 142.21
2018-12-03 09:30 | 152.31 | 142.03
2018-12-03 10:00 | 166.23 | 156.74
2018-12-03 10:30 | 169.66 | 160.12
2018-12-03 11:00 | 170.41 | 160.96
2018-12-03 11:30 | 171.62 | 162.34
2018-12-03 12:00 | 172.62 | 163.56
2018-12-03 12:30 | 173.03 | 163.99
2018-12-03 13:00 | 165.2 | 155.83
2018-12-03 13:30 | 164.21 | 154.79
2018-12-03 14:00 | 165.35 | 156.12
2018-12-03 14:30 | 166.51 | 157.59
2018-12-03 15:00 | 167.08 | 158.21
2018-12-03 15:30 | 167.66 | 158.8
2018-12-03 16:00 | 187.63 | 178.66
2018-12-03 16:30 | 193.92 | 184.97
2018-12-03 17:00 | 195.31 | 186.36
2018-12-03 17:30 | 195.71 | 186.42
2018-12-03 18:00 | 196.16 | 186.73
2018-12-03 18:30 | 197.14 | 187.78
2018-12-03 19:00 | 197.67 | 188.32
2018-12-03 19:30 | 197.44 | 187.83
2018-12-03 20:00 | 195.99 | 186.17
2018-12-03 20:30 | 193.23 | 183.27
2018-12-03 21:00 | 169.61 | 159.18
2018-12-03 21:30 | 165.65 | 156.65
2018-12-03 22:00 | 163.01 | 154.28
2018-12-03 22:30 | 159.2 | 150.01
2018-12-03 23:00 | 173.35 | 162.59
2018-12-03 23:30 | 177.48 | 166.85
2018-12-04 | 175.81 | 165.27
2018-12-04 00:30 | 174.88 | 164.74
2018-12-04 01:00 | 174.74 | 164.55
2018-12-04 01:30 | 174.54 | 164.32
2018-12-04 02:00 | 174.22 | 163.87
2018-12-04 02:30 | 173.97 | 163.55
2018-12-04 03:00 | 173.34 | 162.76
2018-12-04 03:30 | 172.68 | 162.07
2018-12-04 04:00 | 172.81 | 162.3
2018-12-04 04:30 | 173.1 | 162.73
2018-12-04 05:00 | 173.59 | 163.65
2018-12-04 05:30 | 173.98 | 164.15
2018-12-04 06:00 | 174.46 | 164.89
2018-12-04 06:30 | 174.98 | 164.76
2018-12-04 07:00 | 175.37 | 164.28
2018-12-04 07:30 | 176.45 | 165.27
2018-12-04 08:00 | 176.71 | 165.65
2018-12-04 08:30 | 177.92 | 166.84
2018-12-04 09:00 | 178.97 | 167.88
2018-12-04 09:30 | 178.19 | 167.26
2018-12-04 10:00 | 174.94 | 163.88
2018-12-04 10:30 | 173.52 | 162.72
2018-12-04 11:00 | 174.19 | 163.37
2018-12-04 11:30 | 174.18 | 163.18
2018-12-04 12:00 | 175.26 | 164.15
2018-12-04 12:30 | 175.74 | 164.55
2018-12-04 13:00 | 175.38 | 164.12
2018-12-04 13:30 | 176.76 | 165.32
2018-12-04 14:00 | 177.37 | 166.25
2018-12-04 14:30 | 176.99 | 166.54
2018-12-04 15:00 | 177.66 | 167.58
2018-12-04 15:30 | 183.77 | 174.05
2018-12-04 16:00 | 183.8 | 174.02
2018-12-04 16:30 | 181.05 | 172.02
2018-12-04 17:00 | 185.03 | 176.19
2018-12-04 17:30 | 197.33 | 188.62
2018-12-04 18:00 | 199.25 | 190.56
2018-12-04 18:30 | 200.6 | 191.87
2018-12-04 19:00 | 200 | 190.99
2018-12-04 19:30 | 199.93 | 190.69
2018-12-04 20:00 | 199.48 | 190.1
2018-12-04 20:30 | 198.24 | 188.47
2018-12-04 21:00 | 195.65 | 185.94
2018-12-04 21:30 | 192.84 | 184.8
2018-12-04 22:00 | 190.52 | 182.44
2018-12-04 22:30 | 187.92 | 179.71
2018-12-04 23:00 | 186.24 | 177.89
2018-12-04 23:30 | 154.98 | 145.57
2018-12-05 | 142.22 | 132.92
2018-12-05 00:30 | 141.64 | 132.5
2018-12-05 01:00 | 140.46 | 131.67
2018-12-05 01:30 | 139.79 | 131.07
2018-12-05 02:00 | 139.5 | 130.59
2018-12-05 02:30 | 138.75 | 130.34
2018-12-05 03:00 | 137.57 | 129.77
2018-12-05 03:30 | 136.34 | 129.71
2018-12-05 04:00 | 136.52 | 129.93
2018-12-05 04:30 | 136.42 | 130.03
2018-12-05 05:00 | 136.56 | 130.14
2018-12-05 05:30 | 168.64 | 162.88
2018-12-05 06:00 | 179.65 | 174.12
2018-12-05 06:30 | 182.16 | 176.8
2018-12-05 07:00 | 183.99 | 177.5
2018-12-05 07:30 | 176.49 | 168.94
2018-12-05 08:00 | 169.61 | 161.29
2018-12-05 08:30 | 171.84 | 163.55
2018-12-05 09:00 | 179.81 | 171.49
2018-12-05 09:30 | 181.82 | 173.58
2018-12-05 10:00 | 183.24 | 175.21
2018-12-05 10:30 | 184.55 | 176.34
2018-12-05 11:00 | 185.43 | 177.46
2018-12-05 11:30 | 187.17 | 179.02
2018-12-05 12:00 | 188.85 | 180.83
2018-12-05 12:30 | 190.74 | 182.66
2018-12-05 13:00 | 190.6 | 182.62
2018-12-05 13:30 | 192.16 | 184.09
2018-12-05 14:00 | 193.78 | 186.04
2018-12-05 14:30 | 193.01 | 185.02
2018-12-05 15:00 | 193.67 | 185.9
2018-12-05 15:30 | 193.58 | 186.22
2018-12-05 16:00 | 195.75 | 188.6
2018-12-05 16:30 | 196.08 | 189.03
2018-12-05 17:00 | 197.64 | 190.95
2018-12-05 17:30 | 195.21 | 188.23
2018-12-05 18:00 | 194.25 | 187.26
2018-12-05 18:30 | 194.73 | 187.71
2018-12-05 19:00 | 194.62 | 187.92
2018-12-05 19:30 | 194.26 | 187.39
2018-12-05 20:00 | 193.87 | 186.44
2018-12-05 20:30 | 192.74 | 184.93
2018-12-05 21:00 | 190.34 | 182.25
2018-12-05 21:30 | 188.7 | 180.5
2018-12-05 22:00 | 186.13 | 178.22
2018-12-05 22:30 | 183.22 | 175.94
2018-12-05 23:00 | 181.96 | 174.46
2018-12-05 23:30 | 180.14 | 173.06
2018-12-06 | 177.17 | 171.23
2018-12-06 00:30 | 176.51 | 170.65
2018-12-06 01:00 | 175.77 | 169.76
2018-12-06 01:30 | 176.17 | 168.9
2018-12-06 02:00 | 176.04 | 168.6
2018-12-06 02:30 | 175.49 | 167.83
2018-12-06 03:00 | 175.22 | 167.44
2018-12-06 03:30 | 175.45 | 167.27
2018-12-06 04:00 | 152.31 | 143.88
2018-12-06 04:30 | 140.16 | 131.69
2018-12-06 05:00 | 141.24 | 132.9
2018-12-06 05:30 | 141.12 | 132.98
2018-12-06 06:00 | 142.33 | 133.45
2018-12-06 06:30 | 145.6 | 135.22
2018-12-06 07:00 | 147.21 | 135.75
2018-12-06 07:30 | 148.35 | 137.06
2018-12-06 08:00 | 147.02 | 135.83
2018-12-06 08:30 | 134.02 | 124.66
2018-12-06 09:00 | 126.55 | 119.09
2018-12-06 09:30 | 125.53 | 118.18
2018-12-06 10:00 | 125.22 | 118.19
2018-12-06 10:30 | 128.75 | 121.58
2018-12-06 11:00 | 139.69 | 130.96
2018-12-06 11:30 | 144.9 | 134.41
2018-12-06 12:00 | 146.85 | 136.7
2018-12-06 12:30 | 149.07 | 138.84
2018-12-06 13:00 | 149.61 | 139.76
2018-12-06 13:30 | 150.29 | 140.59
2018-12-06 14:00 | 152.18 | 142.63
2018-12-06 14:30 | 153.08 | 143.26
2018-12-06 15:00 | 152.91 | 142.81
2018-12-06 15:30 | 154.77 | 144.76
2018-12-06 16:00 | 156.66 | 146.89
2018-12-06 16:30 | 158.08 | 148.34
2018-12-06 17:00 | 158.78 | 149.1
2018-12-06 17:30 | 162.01 | 152.54
2018-12-06 18:00 | 163.79 | 154.39
2018-12-06 18:30 | 163.85 | 154.51
2018-12-06 19:00 | 163.58 | 154.27
2018-12-06 19:30 | 163.09 | 153.66
2018-12-06 20:00 | 163.05 | 153.3
2018-12-06 20:30 | 161.89 | 151.75
2018-12-06 21:00 | 159.41 | 149.09
2018-12-06 21:30 | 157.58 | 147.97
2018-12-06 22:00 | 154.93 | 145.78
2018-12-06 22:30 | 152.25 | 143.39
2018-12-06 23:00 | 150.51 | 141.35
2018-12-06 23:30 | 149.74 | 139.78
2018-12-07 | 148.69 | 138.11
2018-12-07 00:30 | 148.14 | 137.42
2018-12-07 01:00 | 146.78 | 136.21
2018-12-07 01:30 | 145.21 | 135.1
2018-12-07 02:00 | 144.72 | 134.77
2018-12-07 02:30 | 144.01 | 133.96
2018-12-07 03:00 | 142.84 | 133.45
2018-12-07 03:30 | 141.7 | 132.33
2018-12-07 04:00 | 141.38 | 131.99
2018-12-07 04:30 | 141.88 | 132.53
2018-12-07 05:00 | 142.12 | 132.79
2018-12-07 05:30 | 142.47 | 133.09
2018-12-07 06:00 | 144.23 | 134.1
2018-12-07 06:30 | 145.69 | 134.75
2018-12-07 07:00 | 146.3 | 135.67
2018-12-07 07:30 | 146.56 | 136.02
2018-12-07 08:00 | 146.14 | 135.82
2018-12-07 08:30 | 146.3 | 135.65
2018-12-07 09:00 | 146.24 | 135.42
2018-12-07 09:30 | 146.86 | 136.11
2018-12-07 10:00 | 150.88 | 140.17
2018-12-07 10:30 | 154.19 | 143.52
2018-12-07 11:00 | 153.35 | 143.64
2018-12-07 11:30 | 153.3 | 143.53
2018-12-07 12:00 | 154.46 | 144.07
2018-12-07 12:30 | 155.28 | 144.6
2018-12-07 13:00 | 157.95 | 147.13
2018-12-07 13:30 | 159.54 | 148.3
2018-12-07 14:00 | 160.67 | 149.48
2018-12-07 14:30 | 162.68 | 151.74
2018-12-07 15:00 | 167.1 | 156.42
2018-12-07 15:30 | 177.43 | 167.13
2018-12-07 16:00 | 180.05 | 169.47
2018-12-07 16:30 | 180.89 | 171.06
2018-12-07 17:00 | 177.95 | 168.18
2018-12-07 17:30 | 171.38 | 160.78
2018-12-07 18:00 | 172.62 | 162.41
2018-12-07 18:30 | 181.04 | 170.19
2018-12-07 19:00 | 192.01 | 180.88
2018-12-07 19:30 | 192.5 | 181.36
2018-12-07 20:00 | 192.58 | 181.11
2018-12-07 20:30 | 191.7 | 179.73
2018-12-07 21:00 | 170.18 | 157.96
2018-12-07 21:30 | 165.17 | 154.69
2018-12-07 22:00 | 163.89 | 153.35
2018-12-07 22:30 | 160.21 | 150.23
2018-12-07 23:00 | 158.64 | 148.44
2018-12-07 23:30 | 157.33 | 147.46
2018-12-08 | 171.4 | 164.14
2018-12-08 00:30 | 174.55 | 167.84
2018-12-08 01:00 | 173.05 | 166.5
2018-12-08 01:30 | 172.06 | 165.37
2018-12-08 02:00 | 171.32 | 164.45
2018-12-08 02:30 | 170.68 | 163.62
2018-12-08 03:00 | 170.55 | 163.34
2018-12-08 03:30 | 170.04 | 162.8
2018-12-08 04:00 | 169.99 | 162.78
2018-12-08 04:30 | 169.98 | 162.78
2018-12-08 05:00 | 169.94 | 162.75
2018-12-08 05:30 | 169.39 | 162.18
2018-12-08 06:00 | 169.98 | 162.79
2018-12-08 06:30 | 170.71 | 163.74
2018-12-08 07:00 | 171.34 | 164.26
2018-12-08 07:30 | 172.17 | 165.02
2018-12-08 08:00 | 172.52 | 165.3
2018-12-08 08:30 | 172.09 | 164.83
2018-12-08 09:00 | 171.85 | 164.65
2018-12-08 09:30 | 170.12 | 163.1
2018-12-08 10:00 | 170.67 | 163.67
2018-12-08 10:30 | 171.25 | 163.99
2018-12-08 11:00 | 171.49 | 164.21
2018-12-08 11:30 | 175.01 | 167.55
2018-12-08 12:00 | 173.71 | 166.41
2018-12-08 12:30 | 164.31 | 156.91
2018-12-08 13:00 | 164.96 | 157.54
2018-12-08 13:30 | 164.22 | 156.96
2018-12-08 14:00 | 166.73 | 159.19
2018-12-08 14:30 | 166.7 | 159.2
2018-12-08 15:00 | 162.08 | 153.4
2018-12-08 15:30 | 164.15 | 155.35
2018-12-08 16:00 | 166.17 | 157.15
2018-12-08 16:30 | 167.2 | 158.35
2018-12-08 17:00 | 169.03 | 160.72
2018-12-08 17:30 | 170.66 | 162.54
2018-12-08 18:00 | 171.7 | 163.69
2018-12-08 18:30 | 172.29 | 164.09
2018-12-08 19:00 | 172.45 | 164.15
2018-12-08 19:30 | 172.84 | 164.51
2018-12-08 20:00 | 172.11 | 163.61
2018-12-08 20:30 | 170.76 | 161.96
2018-12-08 21:00 | 169.07 | 160.01
2018-12-08 21:30 | 166.88 | 158.47
2018-12-08 22:00 | 164.92 | 156.65
2018-12-08 22:30 | 163.21 | 154.54
2018-12-08 23:00 | 161.24 | 152.44
2018-12-08 23:30 | 160.3 | 151.77
2018-12-09 | 159.24 | 150.59
2018-12-09 00:30 | 158.19 | 149.55
2018-12-09 01:00 | 156.64 | 148.82
2018-12-09 01:30 | 155.7 | 148.13
2018-12-09 02:00 | 154.53 | 147.61
2018-12-09 02:30 | 154.18 | 147.2
2018-12-09 03:00 | 153.53 | 146.54
2018-12-09 03:30 | 153.6 | 146.54
2018-12-09 04:00 | 153.06 | 145.94
2018-12-09 04:30 | 152.81 | 145.65
2018-12-09 05:00 | 152.75 | 145.65
2018-12-09 05:30 | 152.37 | 145.33
2018-12-09 06:00 | 152.69 | 145.73
2018-12-09 06:30 | 153.05 | 146.09
2018-12-09 07:00 | 152.66 | 145.85
2018-12-09 07:30 | 152.8 | 146.07
2018-12-09 08:00 | 152.72 | 146.13
2018-12-09 08:30 | 152.99 | 146.73
2018-12-09 09:00 | 152.71 | 145.95
2018-12-09 09:30 | 152.92 | 145.94
2018-12-09 10:00 | 153.16 | 146.45
2018-12-09 10:30 | 153.75 | 146.45
2018-12-09 11:00 | 154.7 | 147.27
2018-12-09 11:30 | 155.55 | 148.16
2018-12-09 12:00 | 156.42 | 149.31
2018-12-09 12:30 | 157.82 | 150.73
2018-12-09 13:00 | 158.69 | 152.1
2018-12-09 13:30 | 159.48 | 152.99
2018-12-09 14:00 | 161.04 | 154.37
2018-12-09 14:30 | 161.85 | 155.21
2018-12-09 15:00 | 163.13 | 156.63
2018-12-09 15:30 | 164.33 | 157.93
2018-12-09 16:00 | 165.54 | 159.21
2018-12-09 16:30 | 168.23 | 162.13
2018-12-09 17:00 | 169.84 | 163.89
2018-12-09 17:30 | 171.56 | 165.51
2018-12-09 18:00 | 173.47 | 167.38
2018-12-09 18:30 | 174.01 | 167.89
2018-12-09 19:00 | 173.63 | 167.29
2018-12-09 19:30 | 173.87 | 167.41
2018-12-09 20:00 | 173.17 | 166.49
2018-12-09 20:30 | 171.62 | 164.47
2018-12-09 21:00 | 168.67 | 161.25
2018-12-09 21:30 | 166.96 | 159.72
2018-12-09 22:00 | 164.37 | 156.94
2018-12-09 22:30 | 162.28 | 154.57
2018-12-09 23:00 | 160.38 | 152.48
2018-12-09 23:30 | 159.68 | 151.69
2018-12-10 | 158.06 | 150.33
2018-12-10 00:30 | 157.2 | 149.44
2018-12-10 01:00 | 155.95 | 148.38
2018-12-10 01:30 | 154.63 | 147.62
2018-12-10 02:00 | 154.07 | 146.68
2018-12-10 02:30 | 153.5 | 146.42
2018-12-10 03:00 | 152.94 | 146.34
2018-12-10 03:30 | 152.95 | 146.2
2018-12-10 04:00 | 152.36 | 145.7
2018-12-10 04:30 | 152.93 | 146.39
2018-12-10 05:00 | 153.62 | 147.2
2018-12-10 05:30 | 154.05 | 147.75
2018-12-10 06:00 | 154.87 | 148.95
2018-12-10 06:30 | 156.83 | 150.59
2018-12-10 07:00 | 158.57 | 151.64
2018-12-10 07:30 | 160.18 | 152.67
2018-12-10 08:00 | 160.33 | 152.96
2018-12-10 08:30 | 160.21 | 152.98
2018-12-10 09:00 | 160.69 | 153.17
2018-12-10 09:30 | 160.19 | 152.22
2018-12-10 10:00 | 160.6 | 153
2018-12-10 10:30 | 160.66 | 153.32
2018-12-10 11:00 | 160.82 | 153.64
2018-12-10 11:30 | 162.56 | 155.43
2018-12-10 12:00 | 163.53 | 156.29
2018-12-10 12:30 | 164.46 | 156.75
2018-12-10 13:00 | 166.17 | 158.73
2018-12-10 13:30 | 166.31 | 158.38
2018-12-10 14:00 | 193.94 | 184.57
2018-12-10 14:30 | 210.84 | 201.69
2018-12-10 15:00 | 214.79 | 205.8
2018-12-10 15:30 | 216.11 | 206.96
2018-12-10 16:00 | 218.04 | 208.78
2018-12-10 16:30 | 219.46 | 210.26
2018-12-10 17:00 | 220.28 | 211.85
2018-12-10 17:30 | 221.59 | 212.69
2018-12-10 18:00 | 223.99 | 215.1
2018-12-10 18:30 | 225.4 | 216.66
2018-12-10 19:00 | 225.93 | 217.47
2018-12-10 19:30 | 226.56 | 218.11
2018-12-10 20:00 | 225.63 | 216.9
2018-12-10 20:30 | 222.73 | 213.47
2018-12-10 21:00 | 219.81 | 210.02
2018-12-10 21:30 | 216.91 | 207.05
2018-12-10 22:00 | 213.78 | 203.69
2018-12-10 22:30 | 200.38 | 190.01
2018-12-10 23:00 | 172.46 | 162.87
2018-12-10 23:30 | 164.16 | 155.86
2018-12-11 | 162.71 | 154.47
2018-12-11 00:30 | 161.6 | 153.38
2018-12-11 01:00 | 160.24 | 152.14
2018-12-11 01:30 | 159.46 | 151.2
2018-12-11 02:00 | 158.67 | 150.73
2018-12-11 02:30 | 157.5 | 149.79
2018-12-11 03:00 | 157.22 | 149.51
2018-12-11 03:30 | 156.48 | 148.65
2018-12-11 04:00 | 156.42 | 148.75
2018-12-11 04:30 | 156.66 | 149.24
2018-12-11 05:00 | 157.44 | 149.59
2018-12-11 05:30 | 158.14 | 150.35
2018-12-11 06:00 | 159.15 | 151.68
2018-12-11 06:30 | 161.35 | 153.88
2018-12-11 07:00 | 161.85 | 153.66
2018-12-11 07:30 | 162.7 | 154.49
2018-12-11 08:00 | 163.35 | 155.1
2018-12-11 08:30 | 163.39 | 154.67
2018-12-11 09:00 | 164.05 | 155.16
2018-12-11 09:30 | 164.12 | 155.23
2018-12-11 10:00 | 163.92 | 155.52
2018-12-11 10:30 | 163.03 | 154.36
2018-12-11 11:00 | 163.21 | 154.54
2018-12-11 11:30 | 162.95 | 156.2
2018-12-11 12:00 | 163.55 | 157.68
2018-12-11 12:30 | 164.01 | 158.16
2018-12-11 13:00 | 182.83 | 176.81
2018-12-11 13:30 | 208.4 | 202.45
2018-12-11 14:00 | 202.62 | 196.85
2018-12-11 14:30 | 210.04 | 204.61
2018-12-11 15:00 | 212.4 | 207.01
2018-12-11 15:30 | 214.16 | 208.64
2018-12-11 16:00 | 216.75 | 210.99
2018-12-11 16:30 | 206.77 | 202.04
2018-12-11 17:00 | 188.75 | 185.97
2018-12-11 17:30 | 189.64 | 186.35
2018-12-11 18:00 | 223.75 | 218.13
2018-12-11 18:30 | 224.55 | 218.75
2018-12-11 19:00 | 225.04 | 219.24
2018-12-11 19:30 | 224.81 | 219.04
2018-12-11 20:00 | 223.62 | 217.65
2018-12-11 20:30 | 221.49 | 215.15
2018-12-11 21:00 | 218.42 | 211.72
2018-12-11 21:30 | 214.31 | 208.74
2018-12-11 22:00 | 211.12 | 205.37
2018-12-11 22:30 | 208.08 | 202.18
2018-12-11 23:00 | 196.93 | 191.05
2018-12-11 23:30 | 169.03 | 162.96
2018-12-12 | 161.39 | 155.54
2018-12-12 00:30 | 160.58 | 154.77
2018-12-12 01:00 | 159.38 | 153.52
2018-12-12 01:30 | 158.67 | 152.84
2018-12-12 02:00 | 157.99 | 152.15
2018-12-12 02:30 | 157.37 | 151.53
2018-12-12 03:00 | 156.7 | 150.81
2018-12-12 03:30 | 156.16 | 150.25
2018-12-12 04:00 | 156.26 | 150.34
2018-12-12 04:30 | 156.08 | 150.22
2018-12-12 05:00 | 156.42 | 150.62
2018-12-12 05:30 | 157.21 | 151.38
2018-12-12 06:00 | 158.28 | 152.45
2018-12-12 06:30 | 160.29 | 154.52
2018-12-12 07:00 | 161.39 | 155.03
2018-12-12 07:30 | 162.39 | 155.94
2018-12-12 08:00 | 163.16 | 156.68
2018-12-12 08:30 | 163.31 | 156.74
2018-12-12 09:00 | 163.5 | 156.82
2018-12-12 09:30 | 163.94 | 157.31
2018-12-12 10:00 | 164.89 | 158.16
2018-12-12 10:30 | 199.98 | 193.4
2018-12-12 11:00 | 206.52 | 199.97
2018-12-12 11:30 | 207.71 | 201.1
2018-12-12 12:00 | 208.26 | 201.92
2018-12-12 12:30 | 210.12 | 204.1
2018-12-12 13:00 | 211.82 | 205.76
2018-12-12 13:30 | 213.49 | 207.46
2018-12-12 14:00 | 215.39 | 209.73
2018-12-12 14:30 | 215.56 | 209.57
2018-12-12 15:00 | 213.88 | 207.71
2018-12-12 15:30 | 215.99 | 209.63
2018-12-12 16:00 | 217.22 | 210.67
2018-12-12 16:30 | 217.99 | 211.36
2018-12-12 17:00 | 194.99 | 190.78
2018-12-12 17:30 | 197.6 | 193.96
2018-12-12 18:00 | 198.19 | 195.2
2018-12-12 18:30 | 198.95 | 195.69
2018-12-12 19:00 | 199.63 | 196.34
2018-12-12 19:30 | 200.41 | 197.14
2018-12-12 20:00 | 201.67 | 198.46
2018-12-12 20:30 | 203.09 | 200.01
2018-12-12 21:00 | 204.61 | 201.94
2018-12-12 21:30 | 204.75 | 203.13
2018-12-12 22:00 | 206.69 | 205.32
2018-12-12 22:30 | 200.55 | 195.57
2018-12-12 23:00 | 200.4 | 193.88
2018-12-12 23:30 | 199.07 | 192.7
2018-12-13 | 189.13 | 182.7
2018-12-13 00:30 | 161.49 | 155.01
2018-12-13 01:00 | 154.96 | 148.74
2018-12-13 01:30 | 154.04 | 147.77
2018-12-13 02:00 | 153.62 | 147.47
2018-12-13 02:30 | 152.9 | 146.73
2018-12-13 03:00 | 152.72 | 146.54
2018-12-13 03:30 | 152.74 | 146.47
2018-12-13 04:00 | 152.98 | 146.65
2018-12-13 04:30 | 153.07 | 146.76
2018-12-13 05:00 | 153.56 | 147.35
2018-12-13 05:30 | 154.27 | 148.11
2018-12-13 06:00 | 155.41 | 149.31
2018-12-13 06:30 | 155.43 | 149.37
2018-12-13 07:00 | 157.4 | 150.06
2018-12-13 07:30 | 158.18 | 150.88
2018-12-13 08:00 | 158.99 | 151.69
2018-12-13 08:30 | 159.2 | 151.67
2018-12-13 09:00 | 158.56 | 150.76
2018-12-13 09:30 | 157.37 | 149.67
2018-12-13 10:00 | 167.9 | 159.44
2018-12-13 10:30 | 199.58 | 191.7
2018-12-13 11:00 | 201.07 | 193.48
2018-12-13 11:30 | 201.16 | 193.87
2018-12-13 12:00 | 202.5 | 195.01
2018-12-13 12:30 | 203.97 | 196.43
2018-12-13 13:00 | 205.93 | 198.48
2018-12-13 13:30 | 206.22 | 198.73
2018-12-13 14:00 | 208.33 | 201.26
2018-12-13 14:30 | 210.19 | 203.16
2018-12-13 15:00 | 208.8 | 201.87
2018-12-13 15:30 | 209.49 | 202.77
2018-12-13 16:00 | 209.59 | 202.91
2018-12-13 16:30 | 208.82 | 201.91
2018-12-13 17:00 | 208.76 | 201.36
2018-12-13 17:30 | 208.87 | 200.97
2018-12-13 18:00 | 209.66 | 202.01
2018-12-13 18:30 | 209.82 | 201.95
2018-12-13 19:00 | 209.61 | 201.97
2018-12-13 19:30 | 208.53 | 200.8
2018-12-13 20:00 | 208.44 | 200.6
2018-12-13 20:30 | 207.21 | 199.23
2018-12-13 21:00 | 205.68 | 197.45
2018-12-13 21:30 | 204.09 | 196.26
2018-12-13 22:00 | 202.3 | 194.43
2018-12-13 22:30 | 191.2 | 183.6
2018-12-13 23:00 | 162.9 | 155.93
2018-12-13 23:30 | 156.6 | 150.46
2018-12-14 | 155.14 | 149.04
2018-12-14 00:30 | 154.57 | 148.36
2018-12-14 01:00 | 152.71 | 146.25
2018-12-14 01:30 | 151.87 | 145.31
2018-12-14 02:00 | 151.38 | 144.79
2018-12-14 02:30 | 151.12 | 144.54
2018-12-14 03:00 | 150.99 | 144.58
2018-12-14 03:30 | 150.22 | 143.56
2018-12-14 04:00 | 150.62 | 144.07
2018-12-14 04:30 | 150.8 | 144.34
2018-12-14 05:00 | 151.62 | 145.25
2018-12-14 05:30 | 158.11 | 152.04
2018-12-14 06:00 | 180.12 | 174.51
2018-12-14 06:30 | 183.63 | 177.6
2018-12-14 07:00 | 185.74 | 178.16
2018-12-14 07:30 | 187.29 | 178.85
2018-12-14 08:00 | 186.84 | 178.32
2018-12-14 08:30 | 186.96 | 178.53
2018-12-14 09:00 | 186.73 | 178.23
2018-12-14 09:30 | 183.74 | 176.33
2018-12-14 10:00 | 186.25 | 179.66
2018-12-14 10:30 | 184.99 | 178.81
2018-12-14 11:00 | 184.36 | 178.37
2018-12-14 11:30 | 185.19 | 179.24
2018-12-14 12:00 | 190.6 | 186.46
2018-12-14 12:30 | 192.25 | 188.03
2018-12-14 13:00 | 193.36 | 189.02
2018-12-14 13:30 | 194.44 | 190.03
2018-12-14 14:00 | 195.27 | 191.03
2018-12-14 14:30 | 195.45 | 191.35
2018-12-14 15:00 | 196.49 | 192.48
2018-12-14 15:30 | 191.49 | 187.01
2018-12-14 16:00 | 170.86 | 164.82
2018-12-14 16:30 | 172.85 | 166.77
2018-12-14 17:00 | 173.27 | 167.25
2018-12-14 17:30 | 173.44 | 167.34
2018-12-14 18:00 | 172.44 | 166.25
2018-12-14 18:30 | 168.9 | 162.33
2018-12-14 19:00 | 168.49 | 161.36
2018-12-14 19:30 | 178.22 | 171.19
2018-12-14 20:00 | 184.06 | 177.72
2018-12-14 20:30 | 192.75 | 186.57
2018-12-14 21:00 | 193.99 | 188
2018-12-14 21:30 | 191.53 | 186.86
2018-12-14 22:00 | 190.71 | 186.08
2018-12-14 22:30 | 189.45 | 184.66
2018-12-14 23:00 | 188.05 | 183.12
2018-12-14 23:30 | 187.03 | 182.44
2018-12-15 | 185.61 | 180.92
2018-12-15 00:30 | 184.13 | 179.91
2018-12-15 01:00 | 183.29 | 179.14
2018-12-15 01:30 | 182.64 | 178.54
2018-12-15 02:00 | 182.31 | 178.18
2018-12-15 02:30 | 182.29 | 178.16
2018-12-15 03:00 | 182.13 | 178.02
2018-12-15 03:30 | 182.01 | 177.86
2018-12-15 04:00 | 181.4 | 177.19
2018-12-15 04:30 | 181.16 | 176.97
2018-12-15 05:00 | 180.93 | 176.66
2018-12-15 05:30 | 180.68 | 176.32
2018-12-15 06:00 | 180.18 | 175.81
2018-12-15 06:30 | 180.79 | 176.45
2018-12-15 07:00 | 180.96 | 176.57
2018-12-15 07:30 | 181.87 | 176.28
2018-12-15 08:00 | 182.01 | 175.51
2018-12-15 08:30 | 182.11 | 175.69
2018-12-15 09:00 | 182.35 | 175.96
2018-12-15 09:30 | 182.2 | 175.81
2018-12-15 10:00 | 182.29 | 175.86
2018-12-15 10:30 | 181.9 | 175.72
2018-12-15 11:00 | 182.2 | 176.61
2018-12-15 11:30 | 184.46 | 176.93
2018-12-15 12:00 | 184.35 | 176.54
2018-12-15 12:30 | 185.3 | 177.34
2018-12-15 13:00 | 187.2 | 179.26
2018-12-15 13:30 | 189.39 | 181.34
2018-12-15 14:00 | 191.39 | 183.27
2018-12-15 14:30 | 193.56 | 185.97
2018-12-15 15:00 | 193.04 | 185.57
2018-12-15 15:30 | 193.86 | 186.4
2018-12-15 16:00 | 195.52 | 187.92
2018-12-15 16:30 | 197.71 | 190.11
2018-12-15 17:00 | 200.15 | 192.71
2018-12-15 17:30 | 199.98 | 193.94
2018-12-15 18:00 | 199.39 | 193.35
2018-12-15 18:30 | 200.44 | 193.61
2018-12-15 19:00 | 201.79 | 195.34
2018-12-15 19:30 | 202.27 | 195.65
2018-12-15 20:00 | 201.14 | 194.61
2018-12-15 20:30 | 199.33 | 193.3
2018-12-15 21:00 | 197.54 | 191.27
2018-12-15 21:30 | 194.76 | 190.09
2018-12-15 22:00 | 192.32 | 188.45
2018-12-15 22:30 | 190.45 | 186.61
2018-12-15 23:00 | 188.87 | 184.92
2018-12-15 23:30 | 188.62 | 184.5
2018-12-16 | 187.28 | 183.01
2018-12-16 00:30 | 186.04 | 181.73
2018-12-16 01:00 | 184.6 | 180.55
2018-12-16 01:30 | 183.97 | 179.86
2018-12-16 02:00 | 183.56 | 179.5
2018-12-16 02:30 | 183.09 | 179.02
2018-12-16 03:00 | 182.69 | 178.56
2018-12-16 03:30 | 182.54 | 178.39
2018-12-16 04:00 | 182.49 | 178.29
2018-12-16 04:30 | 182.61 | 178.26
2018-12-16 05:00 | 182.73 | 178.26
2018-12-16 05:30 | 182.93 | 178.38
2018-12-16 06:00 | 182.79 | 178.38
2018-12-16 06:30 | 182.88 | 178.81
2018-12-16 07:00 | 183.63 | 179.54
2018-12-16 07:30 | 184.23 | 179.59
2018-12-16 08:00 | 185.31 | 179.87
2018-12-16 08:30 | 186.65 | 181.07
2018-12-16 09:00 | 186.81 | 181.07
2018-12-16 09:30 | 187.82 | 181.43
2018-12-16 10:00 | 188.51 | 181.7
2018-12-16 10:30 | 187.94 | 181.46
2018-12-16 11:00 | 188.77 | 182.53
2018-12-16 11:30 | 189.16 | 182.59
2018-12-16 12:00 | 188.76 | 182.29
2018-12-16 12:30 | 188.53 | 182.05
2018-12-16 13:00 | 192.48 | 186.71
2018-12-16 13:30 | 194.39 | 189.17
2018-12-16 14:00 | 192.46 | 186.84
2018-12-16 14:30 | 193.23 | 187.6
2018-12-16 15:00 | 194.27 | 188.79
2018-12-16 15:30 | 194.56 | 189.11
2018-12-16 16:00 | 195.97 | 190.38
2018-12-16 16:30 | 202.97 | 197.25
2018-12-16 17:00 | 206.14 | 200.45
2018-12-16 17:30 | 210.24 | 204.56
2018-12-16 18:00 | 213.1 | 207.52
2018-12-16 18:30 | 213.56 | 207.81
2018-12-16 19:00 | 212.95 | 206.86
2018-12-16 19:30 | 209.75 | 203.71
2018-12-16 20:00 | 210.85 | 204.58
2018-12-16 20:30 | 211.66 | 205.07
2018-12-16 21:00 | 210.15 | 203.29
2018-12-16 21:30 | 207.47 | 200.7
2018-12-16 22:00 | 199.77 | 193.28
2018-12-16 22:30 | 197.14 | 190.72
2018-12-16 23:00 | 195.53 | 188.98
2018-12-16 23:30 | 194.85 | 188.66
2018-12-17 | 179.62 | 173.52
2018-12-17 00:30 | 175.35 | 169.37
2018-12-17 01:00 | 173.82 | 168.37
2018-12-17 01:30 | 173.72 | 167.78
2018-12-17 02:00 | 172.88 | 166.57
2018-12-17 02:30 | 172.81 | 166.53
2018-12-17 03:00 | 172.2 | 166.06
2018-12-17 03:30 | 171.4 | 165.3
2018-12-17 04:00 | 171.89 | 165.71
2018-12-17 04:30 | 172.35 | 166.09
2018-12-17 05:00 | 173.17 | 166.56
2018-12-17 05:30 | 173.3 | 167.31
2018-12-17 06:00 | 174.14 | 168.16
2018-12-17 06:30 | 191.14 | 184.82
2018-12-17 07:00 | 195.55 | 188.38
2018-12-17 07:30 | 197.63 | 190.22
2018-12-17 08:00 | 199.4 | 191.28
2018-12-17 08:30 | 199.94 | 191.78
2018-12-17 09:00 | 200.1 | 192.06
2018-12-17 09:30 | 199.96 | 191.95
2018-12-17 10:00 | 200.88 | 193
2018-12-17 10:30 | 201.02 | 193.71
2018-12-17 11:00 | 202.01 | 195.13
2018-12-17 11:30 | 203.47 | 196.11
2018-12-17 12:00 | 205.22 | 197.84
2018-12-17 12:30 | 206.19 | 198.78
2018-12-17 13:00 | 207.74 | 200.07
2018-12-17 13:30 | 209.76 | 201.87
2018-12-17 14:00 | 211.56 | 204.26
2018-12-17 14:30 | 211.32 | 204.31
2018-12-17 15:00 | 212.04 | 204.87
2018-12-17 15:30 | 214.31 | 206.86
2018-12-17 16:00 | 215.51 | 208.42
2018-12-17 16:30 | 216.37 | 209.19
2018-12-17 17:00 | 217.96 | 210.55
2018-12-17 17:30 | 219.17 | 211.63
2018-12-17 18:00 | 221.72 | 214.16
2018-12-17 18:30 | 222.25 | 214.43
2018-12-17 19:00 | 220.49 | 214.23
2018-12-17 19:30 | 220.1 | 214.24
2018-12-17 20:00 | 219.54 | 213.6
2018-12-17 20:30 | 216.86 | 210.5
2018-12-17 21:00 | 214.36 | 207.87
2018-12-17 21:30 | 211.57 | 205.37
2018-12-17 22:00 | 207.98 | 202.12
2018-12-17 22:30 | 205.07 | 198.84
2018-12-17 23:00 | 189.22 | 182.78
2018-12-17 23:30 | 183.76 | 178.33
2018-12-18 | 180.63 | 175.62
2018-12-18 00:30 | 180.27 | 174.47
2018-12-18 01:00 | 178.35 | 173.58
2018-12-18 01:30 | 177.72 | 172.91
2018-12-18 02:00 | 177.75 | 172.77
2018-12-18 02:30 | 176.38 | 171.28
2018-12-18 03:00 | 175.83 | 170.53
2018-12-18 03:30 | 174.8 | 169.58
2018-12-18 04:00 | 174.73 | 169.52
2018-12-18 04:30 | 174.91 | 169.84
2018-12-18 05:00 | 175.11 | 169.89
2018-12-18 05:30 | 175.68 | 170.36
2018-12-18 06:00 | 180.16 | 171.57
2018-12-18 06:30 | 196.89 | 188.3
2018-12-18 07:00 | 200.77 | 192.28
2018-12-18 07:30 | 200.51 | 193.7
2018-12-18 08:00 | 200.29 | 193.77
2018-12-18 08:30 | 200.54 | 194.26
2018-12-18 09:00 | 200.67 | 194.58
2018-12-18 09:30 | 202.67 | 196.46
2018-12-18 10:00 | 210.72 | 205.23
2018-12-18 10:30 | 212.02 | 206.73
2018-12-18 11:00 | 212.9 | 207.75
2018-12-18 11:30 | 214.39 | 209.12
2018-12-18 12:00 | 216 | 210.82
2018-12-18 12:30 | 217.11 | 211.86
2018-12-18 13:00 | 219.43 | 214.47
2018-12-18 13:30 | 221.22 | 216.24
2018-12-18 14:00 | 222.73 | 217.73
2018-12-18 14:30 | 223.48 | 218.46
2018-12-18 15:00 | 225.46 | 220.28
2018-12-18 15:30 | 226.11 | 221
2018-12-18 16:00 | 227.81 | 222.65
2018-12-18 16:30 | 229.67 | 224.49
2018-12-18 17:00 | 231.19 | 226.01
2018-12-18 17:30 | 232.84 | 227.48
2018-12-18 18:00 | 235 | 229.74
2018-12-18 18:30 | 235.9 | 230.67
2018-12-18 19:00 | 236.07 | 230.72
2018-12-18 19:30 | 236.22 | 230.84
2018-12-18 20:00 | 235.6 | 229.95
2018-12-18 20:30 | 233.19 | 227.14
2018-12-18 21:00 | 229.7 | 223.46
2018-12-18 21:30 | 225.16 | 219.91
2018-12-18 22:00 | 222.07 | 216.5
2018-12-18 22:30 | 210.75 | 204.72
2018-12-18 23:00 | 191.75 | 185.5
2018-12-18 23:30 | 187.48 | 181.17
2018-12-19 | 184.86 | 178.34
2018-12-19 00:30 | 183.72 | 177.4
2018-12-19 01:00 | 181.27 | 175.78
2018-12-19 01:30 | 180.62 | 175.19
2018-12-19 02:00 | 179.89 | 174.63
2018-12-19 02:30 | 179.32 | 174.1
2018-12-19 03:00 | 179.03 | 173.84
2018-12-19 03:30 | 178.38 | 173.07
2018-12-19 04:00 | 178.17 | 172.8
2018-12-19 04:30 | 177.51 | 172.63
2018-12-19 05:00 | 177.67 | 172.85
2018-12-19 05:30 | 177.6 | 172.7
2018-12-19 06:00 | 178.57 | 173.57
2018-12-19 06:30 | 195.25 | 190.16
2018-12-19 07:00 | 206.58 | 201.8
2018-12-19 07:30 | 209.47 | 204.15
2018-12-19 08:00 | 209.6 | 203.95
2018-12-19 08:30 | 210.41 | 204.15
2018-12-19 09:00 | 210.53 | 204.35
2018-12-19 09:30 | 210.2 | 204.2
2018-12-19 10:00 | 211.8 | 206.06
2018-12-19 10:30 | 212.2 | 206.78
2018-12-19 11:00 | 213.06 | 207.87
2018-12-19 11:30 | 214.1 | 208.93
2018-12-19 12:00 | 215.86 | 210.78
2018-12-19 12:30 | 217.51 | 212.37
2018-12-19 13:00 | 219.28 | 214.28
2018-12-19 13:30 | 220.45 | 215.57
2018-12-19 14:00 | 222.28 | 217.4
2018-12-19 14:30 | 223.42 | 218.85
2018-12-19 15:00 | 225.11 | 220.86
2018-12-19 15:30 | 227.59 | 223.1
2018-12-19 16:00 | 230.06 | 225.33
2018-12-19 16:30 | 231.85 | 227.1
2018-12-19 17:00 | 233.86 | 229.1
2018-12-19 17:30 | 235.88 | 230.95
2018-12-19 18:00 | 237.59 | 232.72
2018-12-19 18:30 | 238.3 | 233.53
2018-12-19 19:00 | 237.49 | 232.95
2018-12-19 19:30 | 236.61 | 232.11
2018-12-19 20:00 | 236.33 | 231.51
2018-12-19 20:30 | 235.09 | 229.51
2018-12-19 21:00 | 232 | 225.97
2018-12-19 21:30 | 229.55 | 223.39
2018-12-19 22:00 | 225.77 | 219.96
2018-12-19 22:30 | 214.53 | 208.89
2018-12-19 23:00 | 195.17 | 189.64
2018-12-19 23:30 | 190.26 | 185.16
2018-12-20 | 187.47 | 182.22
2018-12-20 00:30 | 187.03 | 181.42
2018-12-20 01:00 | 184.47 | 178.81
2018-12-20 01:30 | 184.36 | 178.62
2018-12-20 02:00 | 184.19 | 178.43
2018-12-20 02:30 | 183.17 | 177.69
2018-12-20 03:00 | 182.82 | 177.27
2018-12-20 03:30 | 182.44 | 176.92
2018-12-20 04:00 | 182.15 | 176.54
2018-12-20 04:30 | 182.49 | 176.88
2018-12-20 05:00 | 182.39 | 176.69
2018-12-20 05:30 | 182.76 | 177.4
2018-12-20 06:00 | 183.18 | 178.46
2018-12-20 06:30 | 200.03 | 194.69
2018-12-20 07:00 | 205.37 | 198.62
2018-12-20 07:30 | 207.94 | 200.49
2018-12-20 08:00 | 207.96 | 200.93
2018-12-20 08:30 | 208.38 | 201.5
2018-12-20 09:00 | 208.64 | 201.63
2018-12-20 09:30 | 208.84 | 201.59
2018-12-20 10:00 | 209.51 | 202.76
2018-12-20 10:30 | 209.95 | 203.38
2018-12-20 11:00 | 210.09 | 203.53
2018-12-20 11:30 | 211.59 | 204.94
2018-12-20 12:00 | 212.87 | 206.17
2018-12-20 12:30 | 214.36 | 207.44
2018-12-20 13:00 | 216.38 | 209.44
2018-12-20 13:30 | 217.51 | 210.69
2018-12-20 14:00 | 218.89 | 212.89
2018-12-20 14:30 | 220.14 | 214.56
2018-12-20 15:00 | 221.16 | 216.06
2018-12-20 15:30 | 221.9 | 217.18
2018-12-20 16:00 | 224.96 | 219.75
2018-12-20 16:30 | 227.62 | 222.19
2018-12-20 17:00 | 229.13 | 224.26
2018-12-20 17:30 | 230.41 | 225.42
2018-12-20 18:00 | 231.39 | 226.35
2018-12-20 18:30 | 230.64 | 225.41
2018-12-20 19:00 | 230.9 | 225.55
2018-12-20 19:30 | 229.37 | 224.02
2018-12-20 20:00 | 228.52 | 222.88
2018-12-20 20:30 | 227.04 | 220.88
2018-12-20 21:00 | 223.83 | 217.34
2018-12-20 21:30 | 220.15 | 214.79
2018-12-20 22:00 | 216.02 | 210.76
2018-12-20 22:30 | 211.53 | 206.48
2018-12-20 23:00 | 209.17 | 203.82
2018-12-20 23:30 | 206.96 | 201.51
2018-12-21 | 205.68 | 199.86
2018-12-21 00:30 | 204.56 | 198.92
2018-12-21 01:00 | 203.26 | 197.55
2018-12-21 01:30 | 202.27 | 196.45
2018-12-21 02:00 | 201.69 | 195.66
2018-12-21 02:30 | 201.04 | 194.95
2018-12-21 03:00 | 200.28 | 194.54
2018-12-21 03:30 | 199.54 | 193.92
2018-12-21 04:00 | 199.07 | 193.36
2018-12-21 04:30 | 198.84 | 192.99
2018-12-21 05:00 | 199.24 | 193.37
2018-12-21 05:30 | 199.42 | 193.76
2018-12-21 06:00 | 200.44 | 194.27
2018-12-21 06:30 | 204.71 | 196.37
2018-12-21 07:00 | 206.32 | 198.39
2018-12-21 07:30 | 214.66 | 208.32
2018-12-21 08:00 | 217.26 | 211.45
2018-12-21 08:30 | 218.46 | 212.75
2018-12-21 09:00 | 219.71 | 214.07
2018-12-21 09:30 | 220.21 | 214.3
2018-12-21 10:00 | 220.76 | 215.02
2018-12-21 10:30 | 220.66 | 215.01
2018-12-21 11:00 | 221.66 | 216.16
2018-12-21 11:30 | 224.24 | 218.67
2018-12-21 12:00 | 225.6 | 220.04
2018-12-21 12:30 | 227.33 | 222.06
2018-12-21 13:00 | 230.03 | 224.82
2018-12-21 13:30 | 231.55 | 226.37
2018-12-21 14:00 | 231.28 | 226.06
2018-12-21 14:30 | 232.8 | 227.77
2018-12-21 15:00 | 234.12 | 229.32
2018-12-21 15:30 | 233.97 | 229.26
2018-12-21 16:00 | 233.62 | 229.12
2018-12-21 16:30 | 221.16 | 217.76
2018-12-21 17:00 | 191.1 | 189.19
2018-12-21 17:30 | 197.86 | 194.58
2018-12-21 18:00 | 229.07 | 224.09
2018-12-21 18:30 | 233.85 | 228.59
2018-12-21 19:00 | 211.98 | 206.52
2018-12-21 19:30 | 205.15 | 199.56
2018-12-21 20:00 | 204.11 | 198.35
2018-12-21 20:30 | 202.08 | 196.52
2018-12-21 21:00 | 199.88 | 193.84
2018-12-21 21:30 | 197.72 | 191.88
2018-12-21 22:00 | 194.54 | 189.21
2018-12-21 22:30 | 190.41 | 185.35
2018-12-21 23:00 | 188.67 | 183.66
2018-12-21 23:30 | 186.96 | 182.25
2018-12-22 | 183.85 | 179.33
2018-12-22 00:30 | 183.58 | 178.79
2018-12-22 01:00 | 182.69 | 177.79
2018-12-22 01:30 | 181.55 | 176.33
2018-12-22 02:00 | 181.28 | 175.84
2018-12-22 02:30 | 181.41 | 176.01
2018-12-22 03:00 | 179.97 | 174.68
2018-12-22 03:30 | 179.66 | 174.27
2018-12-22 04:00 | 179.12 | 173.72
2018-12-22 04:30 | 179.29 | 173.78
2018-12-22 05:00 | 178.88 | 173.28
2018-12-22 05:30 | 178.26 | 172.71
2018-12-22 06:00 | 177.77 | 172.5
2018-12-22 06:30 | 177.36 | 172.4
2018-12-22 07:00 | 177.68 | 172.94
2018-12-22 07:30 | 178.2 | 173.45
2018-12-22 08:00 | 177.93 | 173.15
2018-12-22 08:30 | 178.06 | 173.28
2018-12-22 09:00 | 177.18 | 172.33
2018-12-22 09:30 | 175.89 | 171.21
2018-12-22 10:00 | 176.88 | 171.9
2018-12-22 10:30 | 176.97 | 171.67
2018-12-22 11:00 | 178.13 | 172.61
2018-12-22 11:30 | 178.81 | 172.96
2018-12-22 12:00 | 181.5 | 174.55
2018-12-22 12:30 | 183.93 | 176.47
2018-12-22 13:00 | 184.89 | 177.44
2018-12-22 13:30 | 186.01 | 178.87
2018-12-22 14:00 | 186.25 | 179.38
2018-12-22 14:30 | 186.94 | 180.42
2018-12-22 15:00 | 187.76 | 181.33
2018-12-22 15:30 | 188.86 | 182.49
2018-12-22 16:00 | 190.44 | 184.22
2018-12-22 16:30 | 191.12 | 185.21
2018-12-22 17:00 | 192.58 | 186.63
2018-12-22 17:30 | 194.29 | 188.16
2018-12-22 18:00 | 195.85 | 189.49
2018-12-22 18:30 | 195.79 | 189.25
2018-12-22 19:00 | 194.88 | 188
2018-12-22 19:30 | 192.88 | 186.76
2018-12-22 20:00 | 191.14 | 185.44
2018-12-22 20:30 | 189.09 | 183.45
2018-12-22 21:00 | 187.39 | 181.59
2018-12-22 21:30 | 184.86 | 179.44
2018-12-22 22:00 | 182.64 | 177.67
2018-12-22 22:30 | 182.08 | 176.63
2018-12-22 23:00 | 179.88 | 174.8
2018-12-22 23:30 | 178.91 | 173.88
2018-12-23 | 177.5 | 172.44
2018-12-23 00:30 | 176.55 | 171.3
2018-12-23 01:00 | 175.16 | 169.88
2018-12-23 01:30 | 174.64 | 169.52
2018-12-23 02:00 | 173.97 | 168.86
2018-12-23 02:30 | 173.81 | 168.71
2018-12-23 03:00 | 173.61 | 168.52
2018-12-23 03:30 | 173.44 | 168.32
2018-12-23 04:00 | 173.19 | 168.04
2018-12-23 04:30 | 173.5 | 168.36
2018-12-23 05:00 | 173.17 | 168.02
2018-12-23 05:30 | 173.23 | 168.01
2018-12-23 06:00 | 173.74 | 168.54
2018-12-23 06:30 | 173.78 | 168.63
2018-12-23 07:00 | 174.18 | 169.01
2018-12-23 07:30 | 173.81 | 168.78
2018-12-23 08:00 | 173.66 | 168.7
2018-12-23 08:30 | 173.72 | 168.79
2018-12-23 09:00 | 173.08 | 168.16
2018-12-23 09:30 | 174.78 | 169.16
2018-12-23 10:00 | 174.72 | 168.9
2018-12-23 10:30 | 174.8 | 168.86
2018-12-23 11:00 | 174.9 | 168.92
2018-12-23 11:30 | 175.8 | 169.96
2018-12-23 12:00 | 176.84 | 170.99
2018-12-23 12:30 | 178.6 | 172.7
2018-12-23 13:00 | 180.11 | 174.03
2018-12-23 13:30 | 180.5 | 174.55
2018-12-23 14:00 | 181.88 | 176.16
2018-12-23 14:30 | 183.03 | 177.13
2018-12-23 15:00 | 184.26 | 178.05
2018-12-23 15:30 | 172.78 | 166.44
2018-12-23 16:00 | 174.56 | 167.91
2018-12-23 16:30 | 172.51 | 166.35
2018-12-23 17:00 | 173.27 | 166.94
2018-12-23 17:30 | 188.67 | 182.66
2018-12-23 18:00 | 191.17 | 185.13
2018-12-23 18:30 | 191.67 | 185.67
2018-12-23 19:00 | 191.42 | 185.24
2018-12-23 19:30 | 191.29 | 184.91
2018-12-23 20:00 | 191.52 | 185.01
2018-12-23 20:30 | 190.98 | 184.35
2018-12-23 21:00 | 188.96 | 182.32
2018-12-23 21:30 | 187.16 | 181.13
2018-12-23 22:00 | 185.63 | 179.5
2018-12-23 22:30 | 182.51 | 176.49
2018-12-23 23:00 | 180.76 | 174.69
2018-12-23 23:30 | 179.81 | 173.88
2018-12-24 | 178.24 | 172.94
2018-12-24 00:30 | 177.29 | 172.17
2018-12-24 01:00 | 176.16 | 170.97
2018-12-24 01:30 | 175.32 | 170.1
2018-12-24 02:00 | 174.72 | 169.5
2018-12-24 02:30 | 174.45 | 169.16
2018-12-24 03:00 | 173.91 | 168.57
2018-12-24 03:30 | 173.81 | 168.36
2018-12-24 04:00 | 173.54 | 168.06
2018-12-24 04:30 | 174.16 | 168.76
2018-12-24 05:00 | 173.28 | 167.84
2018-12-24 05:30 | 174.26 | 168.84
2018-12-24 06:00 | 175.26 | 169
2018-12-24 06:30 | 176.08 | 169.83
2018-12-24 07:00 | 176.18 | 170.16
2018-12-24 07:30 | 176.87 | 170.82
2018-12-24 08:00 | 177.08 | 170.56
2018-12-24 08:30 | 166.22 | 159.47
2018-12-24 09:00 | 160.04 | 152.67
2018-12-24 09:30 | 160.28 | 152.25
2018-12-24 10:00 | 159.84 | 151.6
2018-12-24 10:30 | 160.04 | 152.41
2018-12-24 11:00 | 161.07 | 153.26
2018-12-24 11:30 | 162.4 | 154.81
2018-12-24 12:00 | 162.89 | 155.72
2018-12-24 12:30 | 163.7 | 156.53
2018-12-24 13:00 | 164.69 | 157.58
2018-12-24 13:30 | 164.87 | 158.05
2018-12-24 14:00 | 166.75 | 159.95
2018-12-24 14:30 | 167.81 | 161.17
2018-12-24 15:00 | 169.1 | 162.29
2018-12-24 15:30 | 170.26 | 163.48
2018-12-24 16:00 | 172.38 | 166.05
2018-12-24 16:30 | 182.88 | 176.04
2018-12-24 17:00 | 190.64 | 183.41
2018-12-24 17:30 | 191.45 | 184.28
2018-12-24 18:00 | 192.62 | 185.3
2018-12-24 18:30 | 192.76 | 184.97
2018-12-24 19:00 | 192.25 | 184.05
2018-12-24 19:30 | 191.76 | 183.46
2018-12-24 20:00 | 191.27 | 182.89
2018-12-24 20:30 | 190.67 | 182.33
2018-12-24 21:00 | 189.21 | 180.91
2018-12-24 21:30 | 188.45 | 180.46
2018-12-24 22:00 | 186.81 | 179.02
2018-12-24 22:30 | 185.34 | 177.12
2018-12-24 23:00 | 183.16 | 175.54
2018-12-24 23:30 | 181.04 | 174.9
2018-12-25 | 178.62 | 173.12
2018-12-25 00:30 | 177.91 | 172.43
2018-12-25 01:00 | 177.01 | 171.43
2018-12-25 01:30 | 176.06 | 170.47
2018-12-25 02:00 | 175.53 | 169.82
2018-12-25 02:30 | 175.22 | 169.54
2018-12-25 03:00 | 174.75 | 169.23
2018-12-25 03:30 | 174.36 | 168.81
2018-12-25 04:00 | 174.02 | 168.43
2018-12-25 04:30 | 174.08 | 168.44
2018-12-25 05:00 | 173.99 | 168.28
2018-12-25 05:30 | 173.89 | 168.37
2018-12-25 06:00 | 174 | 168.54
2018-12-25 06:30 | 174.22 | 168.87
2018-12-25 07:00 | 174.19 | 168.98
2018-12-25 07:30 | 174.01 | 168.84
2018-12-25 08:00 | 172.7 | 167.55
2018-12-25 08:30 | 172.85 | 167.53
2018-12-25 09:00 | 172.03 | 166.41
2018-12-25 09:30 | 172.54 | 166.39
2018-12-25 10:00 | 172.19 | 165.88
2018-12-25 10:30 | 172.18 | 165.68
2018-12-25 11:00 | 172.04 | 165.29
2018-12-25 11:30 | 172.99 | 165.89
2018-12-25 12:00 | 174.19 | 166.59
2018-12-25 12:30 | 174.58 | 166.8
2018-12-25 13:00 | 174.67 | 167.32
2018-12-25 13:30 | 175.65 | 168.13
2018-12-25 14:00 | 175.74 | 168.29
2018-12-25 14:30 | 177.24 | 169.85
2018-12-25 15:00 | 177.88 | 170.48
2018-12-25 15:30 | 179.9 | 172.1
2018-12-25 16:00 | 182.25 | 174.34
2018-12-25 16:30 | 183.3 | 175.2
2018-12-25 17:00 | 184.85 | 177.07
2018-12-25 17:30 | 186.68 | 178.63
2018-12-25 18:00 | 188.37 | 179.71
2018-12-25 18:30 | 188.04 | 180.37
2018-12-25 19:00 | 187.01 | 179.97
2018-12-25 19:30 | 186.11 | 179.23
2018-12-25 20:00 | 185.72 | 178.83
2018-12-25 20:30 | 185.5 | 178.74
2018-12-25 21:00 | 183.91 | 177.17
2018-12-25 21:30 | 182.56 | 176.8
2018-12-25 22:00 | 180.49 | 175.59
2018-12-25 22:30 | 178.82 | 173.83
2018-12-25 23:00 | 177.72 | 172.63
2018-12-25 23:30 | 177.05 | 171.99
2018-12-26 | 175.74 | 170.31
2018-12-26 00:30 | 175.26 | 170.01
2018-12-26 01:00 | 174.73 | 169.39
2018-12-26 01:30 | 173.99 | 168.64
2018-12-26 02:00 | 173.81 | 168.47
2018-12-26 02:30 | 173.65 | 168.27
2018-12-26 03:00 | 173.4 | 168.04
2018-12-26 03:30 | 173.18 | 167.83
2018-12-26 04:00 | 172.87 | 167.49
2018-12-26 04:30 | 173.1 | 167.62
2018-12-26 05:00 | 172.93 | 167.51
2018-12-26 05:30 | 172.83 | 167.41
2018-12-26 06:00 | 172.6 | 167.3
2018-12-26 06:30 | 172.97 | 167.69
2018-12-26 07:00 | 172.8 | 167.47
2018-12-26 07:30 | 173.52 | 168.15
2018-12-26 08:00 | 160.04 | 154.43
2018-12-26 08:30 | 158.03 | 151.4
2018-12-26 09:00 | 158.29 | 151.39
2018-12-26 09:30 | 157.74 | 150.04
2018-12-26 10:00 | 158.29 | 150.54
2018-12-26 10:30 | 158.8 | 151.06
2018-12-26 11:00 | 159.68 | 151.74
2018-12-26 11:30 | 165.65 | 157.57
2018-12-26 12:00 | 171.65 | 162.76
2018-12-26 12:30 | 172.36 | 163.31
2018-12-26 13:00 | 173.38 | 164.91
2018-12-26 13:30 | 180.94 | 172.55
2018-12-26 14:00 | 182.12 | 174.01
2018-12-26 14:30 | 182.99 | 175.15
2018-12-26 15:00 | 183.9 | 176.46
2018-12-26 15:30 | 185.86 | 178.23
2018-12-26 16:00 | 187.3 | 179.79
2018-12-26 16:30 | 189.52 | 182.33
2018-12-26 17:00 | 190.7 | 183.92
2018-12-26 17:30 | 192.91 | 186.19
2018-12-26 18:00 | 194.76 | 187.54
2018-12-26 18:30 | 195.41 | 187.69
2018-12-26 19:00 | 193.59 | 187.65
2018-12-26 19:30 | 192.76 | 186.57
2018-12-26 20:00 | 192.06 | 185.84
2018-12-26 20:30 | 191.31 | 184.82
2018-12-26 21:00 | 189.57 | 182.66
2018-12-26 21:30 | 187.54 | 181.67
2018-12-26 22:00 | 185.83 | 179.88
2018-12-26 22:30 | 183.66 | 177.52
2018-12-26 23:00 | 181.65 | 175.99
2018-12-26 23:30 | 180.31 | 175.08
2018-12-27 | 178.85 | 173.57
2018-12-27 00:30 | 178.12 | 172.64
2018-12-27 01:00 | 176.8 | 171.48
2018-12-27 01:30 | 176.34 | 171.02
2018-12-27 02:00 | 175.87 | 170.45
2018-12-27 02:30 | 175.57 | 170.22
2018-12-27 03:00 | 175.17 | 169.87
2018-12-27 03:30 | 174.44 | 169.11
2018-12-27 04:00 | 174.22 | 168.87
2018-12-27 04:30 | 173.77 | 168.42
2018-12-27 05:00 | 173.93 | 168.61
2018-12-27 05:30 | 174.23 | 168.94
2018-12-27 06:00 | 174.46 | 169.1
2018-12-27 06:30 | 177.01 | 171.81
2018-12-27 07:00 | 177.76 | 172.95
2018-12-27 07:30 | 178.13 | 173.48
2018-12-27 08:00 | 177.54 | 172.93
2018-12-27 08:30 | 177.95 | 173.22
2018-12-27 09:00 | 177.73 | 173.08
2018-12-27 09:30 | 177.76 | 173.13
2018-12-27 10:00 | 177.95 | 173.35
2018-12-27 10:30 | 178.13 | 173.58
2018-12-27 11:00 | 179.77 | 174.4
2018-12-27 11:30 | 181.06 | 175.1
2018-12-27 12:00 | 182.49 | 175.88
2018-12-27 12:30 | 184.15 | 177.45
2018-12-27 13:00 | 184.72 | 178.26
2018-12-27 13:30 | 186.51 | 180.03
2018-12-27 14:00 | 188.21 | 181.65
2018-12-27 14:30 | 189.23 | 182.32
2018-12-27 15:00 | 190.67 | 183.85
2018-12-27 15:30 | 192.8 | 185.97
2018-12-27 16:00 | 194.98 | 188.12
2018-12-27 16:30 | 197.45 | 191.06
2018-12-27 17:00 | 199.22 | 192.5
2018-12-27 17:30 | 201.41 | 194.7
2018-12-27 18:00 | 202.3 | 195.44
2018-12-27 18:30 | 204.1 | 196.97
2018-12-27 19:00 | 201.73 | 196.05
2018-12-27 19:30 | 199.68 | 194.33
2018-12-27 20:00 | 199.27 | 193.86
2018-12-27 20:30 | 197.39 | 191.82
2018-12-27 21:00 | 195.14 | 189.23
2018-12-27 21:30 | 178.36 | 173.05
2018-12-27 22:00 | 173.2 | 168.18
2018-12-27 22:30 | 170.73 | 165.67
2018-12-27 23:00 | 168.96 | 163.74
2018-12-27 23:30 | 167.99 | 162.67
2018-12-28 | 166.62 | 161.18
2018-12-28 00:30 | 165.71 | 160.2
2018-12-28 01:00 | 164.53 | 159.06
2018-12-28 01:30 | 163.49 | 158.12
2018-12-28 02:00 | 162.99 | 157.47
2018-12-28 02:30 | 162.44 | 156.93
2018-12-28 03:00 | 161.7 | 156.09
2018-12-28 03:30 | 161.76 | 156.12
2018-12-28 04:00 | 161.49 | 155.82
2018-12-28 04:30 | 161.48 | 155.77
2018-12-28 05:00 | 161.3 | 155.6
2018-12-28 05:30 | 161.31 | 155.63
2018-12-28 06:00 | 161.22 | 155.61
2018-12-28 06:30 | 161.65 | 156.27
2018-12-28 07:00 | 162.27 | 157.02
2018-12-28 07:30 | 162.37 | 156.83
2018-12-28 08:00 | 162.23 | 156.78
2018-12-28 08:30 | 162.06 | 156.62
2018-12-28 09:00 | 161.76 | 156.35
2018-12-28 09:30 | 161.67 | 156.24
2018-12-28 10:00 | 162.13 | 156.72
2018-12-28 10:30 | 162.49 | 157.01
2018-12-28 11:00 | 163.45 | 158.01
2018-12-28 11:30 | 165.09 | 159.53
2018-12-28 12:00 | 166.76 | 161.19
2018-12-28 12:30 | 167.73 | 162.27
2018-12-28 13:00 | 170.4 | 164.87
2018-12-28 13:30 | 173.91 | 168.2
2018-12-28 14:00 | 174.79 | 168.94
2018-12-28 14:30 | 175.08 | 169.42
2018-12-28 15:00 | 174.12 | 168.46
2018-12-28 15:30 | 175.04 | 169.73
2018-12-28 16:00 | 177.09 | 171.44
2018-12-28 16:30 | 179.44 | 173.9
2018-12-28 17:00 | 181.87 | 176.52
2018-12-28 17:30 | 205.89 | 200.5
2018-12-28 18:00 | 228.05 | 222.23
2018-12-28 18:30 | 229.09 | 222.94
2018-12-28 19:00 | 228.97 | 222.55
2018-12-28 19:30 | 228.34 | 221.87
2018-12-28 20:00 | 228.05 | 221.28
2018-12-28 20:30 | 226.84 | 219.78
2018-12-28 21:00 | 224.06 | 217.38
2018-12-28 21:30 | 189.77 | 184.2
2018-12-28 22:00 | 175.88 | 170.65
2018-12-28 22:30 | 173.21 | 167.66
2018-12-28 23:00 | 171.24 | 165.74
2018-12-28 23:30 | 169.22 | 163.94
2018-12-29 | 168.07 | 162.71
2018-12-29 00:30 | 166.68 | 161.47
2018-12-29 01:00 | 165.6 | 160.22
2018-12-29 01:30 | 164.92 | 159.46
2018-12-29 02:00 | 163.86 | 158.51
2018-12-29 02:30 | 163.32 | 157.95
2018-12-29 03:00 | 162.85 | 157.47
2018-12-29 03:30 | 162.54 | 156.99
2018-12-29 04:00 | 162.28 | 156.68
2018-12-29 04:30 | 162.43 | 156.82
2018-12-29 05:00 | 162.74 | 157.1
2018-12-29 05:30 | 162.23 | 156.58
2018-12-29 06:00 | 162.21 | 156.53
2018-12-29 06:30 | 162.38 | 156.78
2018-12-29 07:00 | 160.17 | 154.89
2018-12-29 07:30 | 160.09 | 154.66
2018-12-29 08:00 | 159.18 | 153.54
2018-12-29 08:30 | 157.37 | 151.87
2018-12-29 09:00 | 154.91 | 149.76
2018-12-29 09:30 | 155.98 | 150.76
2018-12-29 10:00 | 158.35 | 152.82
2018-12-29 10:30 | 159.42 | 153.32
2018-12-29 11:00 | 160.14 | 154.5
2018-12-29 11:30 | 160.97 | 155.68
2018-12-29 12:00 | 162.31 | 157.04
2018-12-29 12:30 | 162.06 | 156.89
2018-12-29 13:00 | 164.17 | 158.68
2018-12-29 13:30 | 165.26 | 159.62
2018-12-29 14:00 | 166.8 | 161.06
2018-12-29 14:30 | 167.31 | 161.56
2018-12-29 15:00 | 170.61 | 164.69
2018-12-29 15:30 | 173.2 | 167.22
2018-12-29 16:00 | 174.52 | 167.79
2018-12-29 16:30 | 179.77 | 173.31
2018-12-29 17:00 | 198.33 | 192.14
2018-12-29 17:30 | 220.64 | 214.61
2018-12-29 18:00 | 225.11 | 219.02
2018-12-29 18:30 | 226.13 | 219.93
2018-12-29 19:00 | 226.59 | 220.21
2018-12-29 19:30 | 226.43 | 220.16
2018-12-29 20:00 | 226.23 | 219.87
2018-12-29 20:30 | 225.36 | 218.5
2018-12-29 21:00 | 223.42 | 216.32
2018-12-29 21:30 | 200.08 | 193.19
2018-12-29 22:00 | 191.45 | 184.46
2018-12-29 22:30 | 189.24 | 181.95
2018-12-29 23:00 | 189.09 | 181.4
2018-12-29 23:30 | 187.43 | 179.68
2018-12-30 | 185.52 | 178.29
2018-12-30 00:30 | 184.75 | 177.59
2018-12-30 01:00 | 182.79 | 176.16
2018-12-30 01:30 | 181.98 | 175.14
2018-12-30 02:00 | 181.4 | 174.63
2018-12-30 02:30 | 180.67 | 173.94
2018-12-30 03:00 | 180.15 | 173.48
2018-12-30 03:30 | 179.66 | 172.82
2018-12-30 04:00 | 179.61 | 172.66
2018-12-30 04:30 | 179.4 | 172.49
2018-12-30 05:00 | 179.32 | 172.33
2018-12-30 05:30 | 179.1 | 172.13
2018-12-30 06:00 | 178.85 | 172.03
2018-12-30 06:30 | 179.22 | 172.75
2018-12-30 07:00 | 178.63 | 172.32
2018-12-30 07:30 | 179.01 | 172.54
2018-12-30 08:00 | 179.89 | 171.86
2018-12-30 08:30 | 179.87 | 171.51
2018-12-30 09:00 | 179.35 | 171.55
2018-12-30 09:30 | 179.02 | 171.84
2018-12-30 10:00 | 179.25 | 172.1
2018-12-30 10:30 | 179.96 | 172.77
2018-12-30 11:00 | 185.48 | 178.47
2018-12-30 11:30 | 198.11 | 190.8
2018-12-30 12:00 | 199.83 | 192.44
2018-12-30 12:30 | 201.01 | 193.52
2018-12-30 13:00 | 202.16 | 195.14
2018-12-30 13:30 | 203.57 | 196.13
2018-12-30 14:00 | 204.12 | 196.88
2018-12-30 14:30 | 230.85 | 223.7
2018-12-30 15:00 | 246.89 | 240
2018-12-30 15:30 | 248.43 | 241.51
2018-12-30 16:00 | 250.58 | 243.21
2018-12-30 16:30 | 252.76 | 245.34
2018-12-30 17:00 | 253.85 | 246.78
2018-12-30 17:30 | 253.6 | 248.06
2018-12-30 18:00 | 255.91 | 250.45
2018-12-30 18:30 | 257.37 | 251.82
2018-12-30 19:00 | 258.05 | 252.42
2018-12-30 19:30 | 257.87 | 252.22
2018-12-30 20:00 | 257.48 | 251.78
2018-12-30 20:30 | 255.98 | 249.87
2018-12-30 21:00 | 253.48 | 246.74
2018-12-30 21:30 | 251.07 | 245.2
2018-12-30 22:00 | 213.97 | 209.06
2018-12-30 22:30 | 176.17 | 171.07
2018-12-30 23:00 | 173.32 | 167.87
2018-12-30 23:30 | 171.85 | 166.3
2018-12-31 | 169.41 | 164.37
2018-12-31 00:30 | 168.82 | 163.74
2018-12-31 01:00 | 168.09 | 162.72
2018-12-31 01:30 | 167.39 | 162.15
2018-12-31 02:00 | 166.95 | 161.49
2018-12-31 02:30 | 166.06 | 160.56
2018-12-31 03:00 | 165.87 | 160.2
2018-12-31 03:30 | 165.23 | 159.44
2018-12-31 04:00 | 165.87 | 160.02
2018-12-31 04:30 | 165.79 | 160.01
2018-12-31 05:00 | 165.61 | 159.95
2018-12-31 05:30 | 164.7 | 159.22
2018-12-31 06:00 | 164.77 | 159.41
2018-12-31 06:30 | 165.91 | 160.77
2018-12-31 07:00 | 166.98 | 161.89
2018-12-31 07:30 | 167.71 | 162.14
2018-12-31 08:00 | 167.36 | 161.69
2018-12-31 08:30 | 167.01 | 161.28
2018-12-31 09:00 | 166.33 | 160.78
2018-12-31 09:30 | 169.35 | 163.9
2018-12-31 10:00 | 170.46 | 164.92
2018-12-31 10:30 | 170.59 | 165.1
2018-12-31 11:00 | 171.22 | 166.32
2018-12-31 11:30 | 173.64 | 167.97
2018-12-31 12:00 | 175.28 | 169.53
2018-12-31 12:30 | 176.77 | 171.04
2018-12-31 13:00 | 177.99 | 172.12
2018-12-31 13:30 | 179.13 | 173.2
2018-12-31 14:00 | 217.83 | 211.62
2018-12-31 14:30 | 246.12 | 240.03
2018-12-31 15:00 | 247.45 | 241.42
2018-12-31 15:30 | 249.1 | 242.86
2018-12-31 16:00 | 250.21 | 243.81
2018-12-31 16:30 | 252.3 | 245.8
2018-12-31 17:00 | 254.03 | 247.63
2018-12-31 17:30 | 255.12 | 248.73
2018-12-31 18:00 | 256.7 | 250.93
2018-12-31 18:30 | 256.47 | 250.43
2018-12-31 19:00 | 255.07 | 248.88
2018-12-31 19:30 | 253.69 | 247.41
2018-12-31 20:00 | 216.49 | 210.06
2018-12-31 20:30 | 184.89 | 178.04
2018-12-31 21:00 | 182.36 | 175.5
2018-12-31 21:30 | 178.82 | 173.33
2018-12-31 22:00 | 177.33 | 171.79
2018-12-31 22:30 | 175.37 | 169.34
2018-12-31 23:00 | 173.85 | 167.76
2018-12-31 23:30 | 173.98 | 167.72
2019-01-01 | 171.94 | 165.74
2019-01-01 00:30 | 170.72 | 164.54
2019-01-01 01:00 | 169.51 | 163.36
2019-01-01 01:30 | 168.44 | 162.29
2019-01-01 02:00 | 167.26 | 160.97
2019-01-01 02:30 | 166.65 | 160.09
2019-01-01 03:00 | 165.93 | 159.4
2019-01-01 03:30 | 165.17 | 158.48
2019-01-01 04:00 | 165.14 | 158.23
2019-01-01 04:30 | 165.1 | 158.47
2019-01-01 05:00 | 164 | 157.33
2019-01-01 05:30 | 164.27 | 157.8
2019-01-01 06:00 | 164.51 | 158.35
2019-01-01 06:30 | 164.43 | 158.45
2019-01-01 07:00 | 165.08 | 159.53
2019-01-01 07:30 | 164.54 | 159.25
2019-01-01 08:00 | 165.28 | 159.82
2019-01-01 08:30 | 164.48 | 159.08
2019-01-01 09:00 | 165.41 | 159.78
2019-01-01 09:30 | 165.25 | 159.56
2019-01-01 10:00 | 165.95 | 160.35
2019-01-01 10:30 | 166.86 | 161.53
2019-01-01 11:00 | 167.92 | 162.41
2019-01-01 11:30 | 169.48 | 163.6
2019-01-01 12:00 | 192.98 | 187.11
2019-01-01 12:30 | 206.16 | 200.6
2019-01-01 13:00 | 226.15 | 220.45
2019-01-01 13:30 | 240.11 | 234.47
2019-01-01 14:00 | 243.73 | 237.63
2019-01-01 14:30 | 244.83 | 238.75
2019-01-01 15:00 | 246.62 | 240.37
2019-01-01 15:30 | 248.66 | 242.15
2019-01-01 16:00 | 250.5 | 244.01
2019-01-01 16:30 | 251.82 | 245.33
2019-01-01 17:00 | 254.19 | 247.67
2019-01-01 17:30 | 256.62 | 249.98
2019-01-01 18:00 | 258.55 | 252.68
2019-01-01 18:30 | 259.35 | 253.31
2019-01-01 19:00 | 259.8 | 253.41
2019-01-01 19:30 | 259.37 | 252.89
2019-01-01 20:00 | 258.54 | 252.05
2019-01-01 20:30 | 256.75 | 250.12
2019-01-01 21:00 | 253.51 | 246.79
2019-01-01 21:30 | 250.29 | 244.87
2019-01-01 22:00 | 247.86 | 242.23
2019-01-01 22:30 | 235.73 | 230.01
2019-01-01 23:00 | 213.63 | 207.66
2019-01-01 23:30 | 180.7 | 174.66
2019-01-02 | 171.71 | 165.86
2019-01-02 00:30 | 170.74 | 164.97
2019-01-02 01:00 | 169.12 | 163.56
2019-01-02 01:30 | 168.84 | 163.03
2019-01-02 02:00 | 168.48 | 162.52
2019-01-02 02:30 | 168.14 | 162.13
2019-01-02 03:00 | 167.79 | 161.81
2019-01-02 03:30 | 167.34 | 161.24
2019-01-02 04:00 | 167.36 | 161.15
2019-01-02 04:30 | 167.12 | 160.98
2019-01-02 05:00 | 166.91 | 160.81
2019-01-02 05:30 | 166.53 | 160.71
2019-01-02 06:00 | 166.71 | 161.42
2019-01-02 06:30 | 167.48 | 161.95
2019-01-02 07:00 | 168.36 | 162.48
2019-01-02 07:30 | 168.63 | 163.25
2019-01-02 08:00 | 169.53 | 163.33
2019-01-02 08:30 | 170.18 | 163.09
2019-01-02 09:00 | 170.72 | 163.58
2019-01-02 09:30 | 171.24 | 164.33
2019-01-02 10:00 | 171.86 | 165.05
2019-01-02 10:30 | 172.37 | 165.74
2019-01-02 11:00 | 173.84 | 167.43
2019-01-02 11:30 | 174.97 | 168.14
2019-01-02 12:00 | 177.26 | 170.62
2019-01-02 12:30 | 206.2 | 200.06
2019-01-02 13:00 | 236.5 | 230.13
2019-01-02 13:30 | 249.15 | 242.28
2019-01-02 14:00 | 250.77 | 243.97
2019-01-02 14:30 | 251.97 | 244.76
2019-01-02 15:00 | 254.07 | 246.78
2019-01-02 15:30 | 255.44 | 248.07
2019-01-02 16:00 | 256.28 | 250.21
2019-01-02 16:30 | 256.72 | 250.95
2019-01-02 17:00 | 257.53 | 252.17
2019-01-02 17:30 | 258.68 | 253.13
2019-01-02 18:00 | 260.47 | 254.71
2019-01-02 18:30 | 260.59 | 254.82
2019-01-02 19:00 | 261.08 | 255.32
2019-01-02 19:30 | 260.98 | 255.41
2019-01-02 20:00 | 259.45 | 255.02
2019-01-02 20:30 | 257.22 | 252.66
2019-01-02 21:00 | 254.34 | 249.62
2019-01-02 21:30 | 250.7 | 247.04
2019-01-02 22:00 | 247.3 | 243.58
2019-01-02 22:30 | 244.25 | 240.29
2019-01-02 23:00 | 219.23 | 215.31
2019-01-02 23:30 | 179.79 | 175.27
2019-01-03 | 171.81 | 166.84
2019-01-03 00:30 | 171.13 | 166.17
2019-01-03 01:00 | 169.91 | 165.05
2019-01-03 01:30 | 168.4 | 163.5
2019-01-03 02:00 | 168.25 | 163.28
2019-01-03 02:30 | 167.13 | 162.18
2019-01-03 03:00 | 166.35 | 161.36
2019-01-03 03:30 | 165.67 | 160.63
2019-01-03 04:00 | 165.64 | 160.65
2019-01-03 04:30 | 165.24 | 160.24
2019-01-03 05:00 | 165.48 | 160.46
2019-01-03 05:30 | 165.33 | 160.27
2019-01-03 06:00 | 165.6 | 160.48
2019-01-03 06:30 | 166.82 | 161.87
2019-01-03 07:00 | 171.52 | 166.15
2019-01-03 07:30 | 163.01 | 156.24
2019-01-03 08:00 | 160.98 | 154.5
2019-01-03 08:30 | 160.25 | 154
2019-01-03 09:00 | 161.41 | 155.04
2019-01-03 09:30 | 161.26 | 154.61
2019-01-03 10:00 | 161.72 | 155.14
2019-01-03 10:30 | 163.07 | 156.12
2019-01-03 11:00 | 163.79 | 156.97
2019-01-03 11:30 | 178.46 | 171.61
2019-01-03 12:00 | 229.41 | 222.98
2019-01-03 12:30 | 238.48 | 231.74
2019-01-03 13:00 | 240.21 | 233.72
2019-01-03 13:30 | 241.64 | 235.34
2019-01-03 14:00 | 241.53 | 235.71
2019-01-03 14:30 | 240.95 | 235.38
2019-01-03 15:00 | 242.57 | 237.05
2019-01-03 15:30 | 243.37 | 237.44
2019-01-03 16:00 | 242.68 | 236.94
2019-01-03 16:30 | 244.66 | 238.67
2019-01-03 17:00 | 246.09 | 240.04
2019-01-03 17:30 | 247.8 | 241.36
2019-01-03 18:00 | 248.06 | 241.41
2019-01-03 18:30 | 247.56 | 241.81
2019-01-03 19:00 | 248.04 | 242.73
2019-01-03 19:30 | 247.88 | 242.58
2019-01-03 20:00 | 247.46 | 242.08
2019-01-03 20:30 | 246.25 | 240.62
2019-01-03 21:00 | 243.33 | 237.31
2019-01-03 21:30 | 239.37 | 234.15
2019-01-03 22:00 | 236.25 | 231.14
2019-01-03 22:30 | 233.41 | 228.23
2019-01-03 23:00 | 231.31 | 225.89
2019-01-03 23:30 | 212.92 | 207.58
2019-01-04 | 173.31 | 168.02
2019-01-04 00:30 | 160.06 | 154.65
2019-01-04 01:00 | 158.73 | 153.86
2019-01-04 01:30 | 157.53 | 152.91
2019-01-04 02:00 | 157.18 | 152.59
2019-01-04 02:30 | 156.54 | 151.93
2019-01-04 03:00 | 156.09 | 151.39
2019-01-04 03:30 | 155.34 | 150.51
2019-01-04 04:00 | 155.68 | 150.88
2019-01-04 04:30 | 155.58 | 150.9
2019-01-04 05:00 | 155.24 | 150.61
2019-01-04 05:30 | 155.48 | 150.97
2019-01-04 06:00 | 155.68 | 151.14
2019-01-04 06:30 | 175.1 | 169.86
2019-01-04 07:00 | 222.81 | 215.94
2019-01-04 07:30 | 227.66 | 221.54
2019-01-04 08:00 | 228.31 | 221.96
2019-01-04 08:30 | 228.96 | 222.31
2019-01-04 09:00 | 229.84 | 222.96
2019-01-04 09:30 | 231.18 | 224.38
2019-01-04 10:00 | 231.49 | 225.03
2019-01-04 10:30 | 231.83 | 225.32
2019-01-04 11:00 | 232.36 | 226.05
2019-01-04 11:30 | 233.18 | 226.74
2019-01-04 12:00 | 235.52 | 229.42
2019-01-04 12:30 | 236.55 | 230.87
2019-01-04 13:00 | 237.71 | 232.02
2019-01-04 13:30 | 239.58 | 233.82
2019-01-04 14:00 | 240.72 | 235.11
2019-01-04 14:30 | 241.76 | 236.29
2019-01-04 15:00 | 243.28 | 237.5
2019-01-04 15:30 | 244.73 | 238.58
2019-01-04 16:00 | 247.37 | 241.11
2019-01-04 16:30 | 249.41 | 242.85
2019-01-04 17:00 | 249.83 | 243.15
2019-01-04 17:30 | 247.98 | 241.98
2019-01-04 18:00 | 246.7 | 242.36
2019-01-04 18:30 | 247.38 | 242.87
2019-01-04 19:00 | 247.86 | 243.34
2019-01-04 19:30 | 247.89 | 243.31
2019-01-04 20:00 | 248.34 | 243.74
2019-01-04 20:30 | 247.96 | 243.24
2019-01-04 21:00 | 246.05 | 241.25
2019-01-04 21:30 | 242.96 | 238.92
2019-01-04 22:00 | 240.27 | 236.58
2019-01-04 22:30 | 238.48 | 234.49
2019-01-04 23:00 | 236.38 | 232.26
2019-01-04 23:30 | 234.9 | 230.8
2019-01-05 | 215.21 | 211.21
2019-01-05 00:30 | 174.82 | 170.54
2019-01-05 01:00 | 161.04 | 156.4
2019-01-05 01:30 | 159.98 | 155.3
2019-01-05 02:00 | 159.22 | 154.4
2019-01-05 02:30 | 158.66 | 153.91
2019-01-05 03:00 | 158.99 | 154.25
2019-01-05 03:30 | 158.33 | 153.56
2019-01-05 04:00 | 157.67 | 152.9
2019-01-05 04:30 | 157.82 | 153.08
2019-01-05 05:00 | 157.61 | 152.77
2019-01-05 05:30 | 156.64 | 151.96
2019-01-05 06:00 | 156.49 | 151.85
2019-01-05 06:30 | 156.55 | 151.98
2019-01-05 07:00 | 158.19 | 153.48
2019-01-05 07:30 | 158.79 | 153.95
2019-01-05 08:00 | 160.17 | 154.45
2019-01-05 08:30 | 160.45 | 154.32
2019-01-05 09:00 | 160.65 | 154.68
2019-01-05 09:30 | 193.71 | 187.83
2019-01-05 10:00 | 223.34 | 217.06
2019-01-05 10:30 | 228.46 | 222.38
2019-01-05 11:00 | 230.32 | 223.76
2019-01-05 11:30 | 231.71 | 225.28
2019-01-05 12:00 | 232.52 | 226.29
2019-01-05 12:30 | 234.06 | 227.95
2019-01-05 13:00 | 235.37 | 229.17
2019-01-05 13:30 | 236.23 | 229.89
2019-01-05 14:00 | 236.66 | 230.33
2019-01-05 14:30 | 237.65 | 230.98
2019-01-05 15:00 | 238.72 | 232.49
2019-01-05 15:30 | 239.58 | 233.24
2019-01-05 16:00 | 241.9 | 235.8
2019-01-05 16:30 | 243.6 | 237.49
2019-01-05 17:00 | 245.46 | 239.67
2019-01-05 17:30 | 247.33 | 241.43
2019-01-05 18:00 | 248.84 | 243.52
2019-01-05 18:30 | 250.19 | 244.94
2019-01-05 19:00 | 250.53 | 245.25
2019-01-05 19:30 | 250.18 | 244.84
2019-01-05 20:00 | 250.22 | 244.62
2019-01-05 20:30 | 247.71 | 241.9
2019-01-05 21:00 | 244.87 | 239.15
2019-01-05 21:30 | 242.51 | 237.62
2019-01-05 22:00 | 239.79 | 234.94
2019-01-05 22:30 | 237.35 | 232.3
2019-01-05 23:00 | 235.41 | 230.32
2019-01-05 23:30 | 234.13 | 228.94
2019-01-06 | 215.08 | 209.71
2019-01-06 00:30 | 175.27 | 169.67
2019-01-06 01:00 | 161.86 | 156.36
2019-01-06 01:30 | 160.93 | 155.52
2019-01-06 02:00 | 160.12 | 154.72
2019-01-06 02:30 | 159.28 | 153.77
2019-01-06 03:00 | 158.79 | 153.24
2019-01-06 03:30 | 158.45 | 152.91
2019-01-06 04:00 | 157.98 | 152.46
2019-01-06 04:30 | 157.35 | 151.9
2019-01-06 05:00 | 157.61 | 152.11
2019-01-06 05:30 | 157.29 | 152.04
2019-01-06 06:00 | 157.52 | 152.28
2019-01-06 06:30 | 157.61 | 152.56
2019-01-06 07:00 | 158.11 | 153.28
2019-01-06 07:30 | 158.09 | 153.28
2019-01-06 08:00 | 157.2 | 152.34
2019-01-06 08:30 | 157.74 | 152.62
2019-01-06 09:00 | 158.09 | 152.91
2019-01-06 09:30 | 158.78 | 153.5
2019-01-06 10:00 | 160.08 | 154.68
2019-01-06 10:30 | 161.42 | 155.8
2019-01-06 11:00 | 162.65 | 156.9
2019-01-06 11:30 | 164.69 | 159.15
2019-01-06 12:00 | 166.37 | 160.88
2019-01-06 12:30 | 168.06 | 162.67
2019-01-06 13:00 | 169.34 | 164
2019-01-06 13:30 | 170.01 | 164.82
2019-01-06 14:00 | 171.2 | 166.21
2019-01-06 14:30 | 171.45 | 166.8
2019-01-06 15:00 | 172.36 | 167.64
2019-01-06 15:30 | 174.54 | 169.37
2019-01-06 16:00 | 176.42 | 171.25
2019-01-06 16:30 | 209.98 | 204.83
2019-01-06 17:00 | 241.91 | 236.8
2019-01-06 17:30 | 248.1 | 242.83
2019-01-06 18:00 | 248.71 | 243.46
2019-01-06 18:30 | 249.05 | 243.78
2019-01-06 19:00 | 249.28 | 243.86
2019-01-06 19:30 | 249.44 | 244.03
2019-01-06 20:00 | 248.47 | 242.96
2019-01-06 20:30 | 246.81 | 240.95
2019-01-06 21:00 | 243.35 | 237.06
2019-01-06 21:30 | 240.25 | 234.6
2019-01-06 22:00 | 236.9 | 231.3
2019-01-06 22:30 | 234.38 | 228.42
2019-01-06 23:00 | 232.66 | 226.35
2019-01-06 23:30 | 192.66 | 186.29
2019-01-07 | 161.47 | 155.84
2019-01-07 00:30 | 160.71 | 155.25
2019-01-07 01:00 | 158.85 | 154.13
2019-01-07 01:30 | 157.99 | 153.13
2019-01-07 02:00 | 157.6 | 152.66
2019-01-07 02:30 | 157.01 | 152.05
2019-01-07 03:00 | 156.46 | 151.45
2019-01-07 03:30 | 156.09 | 151.06
2019-01-07 04:00 | 156.06 | 150.99
2019-01-07 04:30 | 156.52 | 151.46
2019-01-07 05:00 | 156.46 | 151.38
2019-01-07 05:30 | 156.68 | 151.7
2019-01-07 06:00 | 156.15 | 151.4
2019-01-07 06:30 | 189.76 | 185.37
2019-01-07 07:00 | 220.95 | 216.15
2019-01-07 07:30 | 229.6 | 223.37
2019-01-07 08:00 | 231.65 | 224.69
2019-01-07 08:30 | 232.35 | 225.57
2019-01-07 09:00 | 232.02 | 225.39
2019-01-07 09:30 | 232.3 | 225.57
2019-01-07 10:00 | 232.04 | 225.92
2019-01-07 10:30 | 232.46 | 226.53
2019-01-07 11:00 | 233.53 | 227.51
2019-01-07 11:30 | 235.4 | 229.52
2019-01-07 12:00 | 236.33 | 230.78
2019-01-07 12:30 | 237.16 | 231.64
2019-01-07 13:00 | 238.69 | 233.71
2019-01-07 13:30 | 239.39 | 234.55
2019-01-07 14:00 | 241.49 | 236.53
2019-01-07 14:30 | 241.96 | 237.06
2019-01-07 15:00 | 242.52 | 237.68
2019-01-07 15:30 | 244.3 | 239.45
2019-01-07 16:00 | 245.46 | 240.61
2019-01-07 16:30 | 246.82 | 241.81
2019-01-07 17:00 | 247.57 | 242.52
2019-01-07 17:30 | 247.7 | 242.49
2019-01-07 18:00 | 249.16 | 243.97
2019-01-07 18:30 | 250.11 | 244.93
2019-01-07 19:00 | 250.53 | 245.21
2019-01-07 19:30 | 250.22 | 244.84
2019-01-07 20:00 | 249.96 | 244.53
2019-01-07 20:30 | 247.79 | 242.04
2019-01-07 21:00 | 244.49 | 238.91
2019-01-07 21:30 | 241.39 | 236.85
2019-01-07 22:00 | 238.43 | 233.81
2019-01-07 22:30 | 235.66 | 230.88
2019-01-07 23:00 | 234.08 | 229.11
2019-01-07 23:30 | 232.55 | 227.51
2019-01-08 | 212.77 | 208.36
2019-01-08 00:30 | 172.71 | 168.25
2019-01-08 01:00 | 160.08 | 155.45
2019-01-08 01:30 | 158.91 | 154.2
2019-01-08 02:00 | 158.13 | 153.23
2019-01-08 02:30 | 157.87 | 152.88
2019-01-08 03:00 | 156.84 | 151.95
2019-01-08 03:30 | 156.37 | 151.63
2019-01-08 04:00 | 156.66 | 151.96
2019-01-08 04:30 | 156.56 | 151.84
2019-01-08 05:00 | 156.86 | 152.07
2019-01-08 05:30 | 157.22 | 152.55
2019-01-08 06:00 | 157.08 | 152.52
2019-01-08 06:30 | 193.61 | 188.53
2019-01-08 07:00 | 225.06 | 218.32
2019-01-08 07:30 | 224.77 | 218.07
2019-01-08 08:00 | 220.45 | 213.98
2019-01-08 08:30 | 223.49 | 216.89
2019-01-08 09:00 | 225.63 | 219.03
2019-01-08 09:30 | 225.37 | 218.59
2019-01-08 10:00 | 226.04 | 219.37
2019-01-08 10:30 | 227.34 | 220.15
2019-01-08 11:00 | 227.76 | 220.6
2019-01-08 11:30 | 225.69 | 218.64
2019-01-08 12:00 | 226.7 | 219.93
2019-01-08 12:30 | 226.43 | 219.82
2019-01-08 13:00 | 226.34 | 220.13
2019-01-08 13:30 | 226.58 | 220.62
2019-01-08 14:00 | 227.89 | 222.03
2019-01-08 14:30 | 229.63 | 223.72
2019-01-08 15:00 | 230.04 | 224.47
2019-01-08 15:30 | 230.73 | 225.32
2019-01-08 16:00 | 231.82 | 226.19
2019-01-08 16:30 | 232.79 | 227
2019-01-08 17:00 | 234.48 | 228.88
2019-01-08 17:30 | 236.04 | 230.24
2019-01-08 18:00 | 237.23 | 231.39
2019-01-08 18:30 | 238.41 | 232.54
2019-01-08 19:00 | 238.81 | 232.82
2019-01-08 19:30 | 239.18 | 233.16
2019-01-08 20:00 | 238.85 | 232.71
2019-01-08 20:30 | 236.86 | 230.55
2019-01-08 21:00 | 232.91 | 227.71
2019-01-08 21:30 | 229.6 | 225.54
2019-01-08 22:00 | 226.68 | 222.58
2019-01-08 22:30 | 224.26 | 219.91
2019-01-08 23:00 | 222.05 | 217.47
2019-01-08 23:30 | 220.78 | 216.2
2019-01-09 | 201.44 | 197.01
2019-01-09 00:30 | 161.33 | 156.75
2019-01-09 01:00 | 148.76 | 144.14
2019-01-09 01:30 | 147.34 | 142.96
2019-01-09 02:00 | 147.15 | 142.9
2019-01-09 02:30 | 146.75 | 142.55
2019-01-09 03:00 | 145.64 | 141.31
2019-01-09 03:30 | 145.87 | 141.36
2019-01-09 04:00 | 144.57 | 140.11
2019-01-09 04:30 | 145.02 | 140.67
2019-01-09 05:00 | 145.31 | 140.99
2019-01-09 05:30 | 145.18 | 140.85
2019-01-09 06:00 | 146.01 | 141.72
2019-01-09 06:30 | 147.48 | 143.05
2019-01-09 07:00 | 182.35 | 176.94
2019-01-09 07:30 | 213.33 | 207.88
2019-01-09 08:00 | 219.09 | 213.57
2019-01-09 08:30 | 219.64 | 214.02
2019-01-09 09:00 | 219.83 | 214.35
2019-01-09 09:30 | 219.58 | 214.24
2019-01-09 10:00 | 219.49 | 214.24
2019-01-09 10:30 | 220.09 | 214.93
2019-01-09 11:00 | 220.88 | 215.8
2019-01-09 11:30 | 220.74 | 215.64
2019-01-09 12:00 | 221.37 | 216.24
2019-01-09 12:30 | 222.68 | 217.6
2019-01-09 13:00 | 227.56 | 222.67
2019-01-09 13:30 | 231.36 | 226.33
2019-01-09 14:00 | 230.4 | 225.16
2019-01-09 14:30 | 229.13 | 223.77
2019-01-09 15:00 | 229.34 | 223.94
2019-01-09 15:30 | 230.94 | 225.58
2019-01-09 16:00 | 231.39 | 226.12
2019-01-09 16:30 | 232.61 | 227.03
2019-01-09 17:00 | 232.87 | 227.21
2019-01-09 17:30 | 233.62 | 227.8
2019-01-09 18:00 | 234.7 | 228.73
2019-01-09 18:30 | 235.29 | 229.3
2019-01-09 19:00 | 235.17 | 229.41
2019-01-09 19:30 | 235.75 | 229.98
2019-01-09 20:00 | 235.96 | 230.09
2019-01-09 20:30 | 234.77 | 228.7
2019-01-09 21:00 | 232.71 | 226.77
2019-01-09 21:30 | 230.21 | 225.31
2019-01-09 22:00 | 227.12 | 222.44
2019-01-09 22:30 | 224.36 | 219.61
2019-01-09 23:00 | 222.38 | 217.46
2019-01-09 23:30 | 221.37 | 216.17
2019-01-10 | 202.59 | 197.54
2019-01-10 00:30 | 165.03 | 159.75
2019-01-10 01:00 | 150.81 | 145.26
2019-01-10 01:30 | 150.22 | 144.61
2019-01-10 02:00 | 149.85 | 144.3
2019-01-10 02:30 | 148.66 | 143.68
2019-01-10 03:00 | 147.75 | 143.04
2019-01-10 03:30 | 148.03 | 143.33
2019-01-10 04:00 | 147.89 | 143.2
2019-01-10 04:30 | 147.72 | 143.08
2019-01-10 05:00 | 148.46 | 143.92
2019-01-10 05:30 | 149.11 | 144.64
2019-01-10 06:00 | 149.49 | 145.07
2019-01-10 06:30 | 160.28 | 156.04
2019-01-10 07:00 | 211.23 | 206.46
2019-01-10 07:30 | 220.13 | 215.21
2019-01-10 08:00 | 220.25 | 215.38
2019-01-10 08:30 | 220.83 | 215.91
2019-01-10 09:00 | 221.17 | 216.18
2019-01-10 09:30 | 221.97 | 216.96
2019-01-10 10:00 | 222.25 | 217.35
2019-01-10 10:30 | 221.99 | 217.19
2019-01-10 11:00 | 222.87 | 218.16
2019-01-10 11:30 | 224.02 | 219.35
2019-01-10 12:00 | 224.65 | 220.15
2019-01-10 12:30 | 225.94 | 221.38
2019-01-10 13:00 | 227.46 | 223
2019-01-10 13:30 | 228.24 | 223.9
2019-01-10 14:00 | 230.08 | 225.99
2019-01-10 14:30 | 231.85 | 227.75
2019-01-10 15:00 | 233.14 | 229.07
2019-01-10 15:30 | 233.87 | 229.81
2019-01-10 16:00 | 235.85 | 231.9
2019-01-10 16:30 | 237.25 | 233.18
2019-01-10 17:00 | 238.26 | 233.64
2019-01-10 17:30 | 239.39 | 234.61
2019-01-10 18:00 | 240.81 | 236.11
2019-01-10 18:30 | 242.4 | 237.67
2019-01-10 19:00 | 242.81 | 238.04
2019-01-10 19:30 | 243.45 | 238.69
2019-01-10 20:00 | 243.5 | 238.67
2019-01-10 20:30 | 241.75 | 236.6
2019-01-10 21:00 | 238.48 | 233.12
2019-01-10 21:30 | 234.55 | 230.62
2019-01-10 22:00 | 231.09 | 227.33
2019-01-10 22:30 | 227.78 | 223.86
2019-01-10 23:00 | 225.54 | 221.5
2019-01-10 23:30 | 223.78 | 219.48
2019-01-11 | 205.16 | 200.96
2019-01-11 00:30 | 166.47 | 162.21
2019-01-11 01:00 | 151.63 | 147.57
2019-01-11 01:30 | 150.89 | 146.9
2019-01-11 02:00 | 149.98 | 145.9
2019-01-11 02:30 | 148.85 | 144.68
2019-01-11 03:00 | 148.65 | 144.45
2019-01-11 03:30 | 148.12 | 143.96
2019-01-11 04:00 | 148.07 | 144
2019-01-11 04:30 | 147.88 | 143.9
2019-01-11 05:00 | 148.81 | 144.89
2019-01-11 05:30 | 148.71 | 144.84
2019-01-11 06:00 | 148.5 | 144.66
2019-01-11 06:30 | 183.22 | 179.41
2019-01-11 07:00 | 198.3 | 194.17
2019-01-11 07:30 | 200.57 | 194.98
2019-01-11 08:00 | 201.05 | 195.41
2019-01-11 08:30 | 200.87 | 195.27
2019-01-11 09:00 | 200.02 | 194.5
2019-01-11 09:30 | 199.33 | 193.88
2019-01-11 10:00 | 199.08 | 193.75
2019-01-11 10:30 | 199.76 | 194.33
2019-01-11 11:00 | 200.5 | 195.32
2019-01-11 11:30 | 201.86 | 196.88
2019-01-11 12:00 | 220.38 | 215.49
2019-01-11 12:30 | 226.32 | 221.24
2019-01-11 13:00 | 227.06 | 222.04
2019-01-11 13:30 | 227.42 | 223.45
2019-01-11 14:00 | 228.69 | 224.64
2019-01-11 14:30 | 230.15 | 225.69
2019-01-11 15:00 | 231.6 | 227.42
2019-01-11 15:30 | 233.27 | 228.77
2019-01-11 16:00 | 235.88 | 230.96
2019-01-11 16:30 | 237.59 | 232.54
2019-01-11 17:00 | 238.87 | 233.91
2019-01-11 17:30 | 239 | 234.48
2019-01-11 18:00 | 240.07 | 235.66
2019-01-11 18:30 | 239.55 | 234.98
2019-01-11 19:00 | 239.88 | 235.22
2019-01-11 19:30 | 239.52 | 234.8
2019-01-11 20:00 | 239.06 | 234.35
2019-01-11 20:30 | 237.28 | 232.33
2019-01-11 21:00 | 234.72 | 229.85
2019-01-11 21:30 | 215.4 | 211.7
2019-01-11 22:00 | 207.58 | 204.2
2019-01-11 22:30 | 204.22 | 201.14
2019-01-11 23:00 | 202.53 | 199.3
2019-01-11 23:30 | 201.16 | 197.75
2019-01-12 | 199.49 | 196
2019-01-12 00:30 | 167.67 | 164.04
2019-01-12 01:00 | 151.57 | 147.63
2019-01-12 01:30 | 150.3 | 146.32
2019-01-12 02:00 | 148.87 | 144.91
2019-01-12 02:30 | 149.85 | 145.33
2019-01-12 03:00 | 149.82 | 144.39
2019-01-12 03:30 | 148.71 | 143.26
2019-01-12 04:00 | 148.19 | 143.03
2019-01-12 04:30 | 148.54 | 143.36
2019-01-12 05:00 | 148.2 | 143.11
2019-01-12 05:30 | 147.84 | 142.65
2019-01-12 06:00 | 147.62 | 142.7
2019-01-12 06:30 | 148.12 | 143.65
2019-01-12 07:00 | 148.05 | 143.89
2019-01-12 07:30 | 181.23 | 177.07
2019-01-12 08:00 | 194.85 | 190.8
2019-01-12 08:30 | 196.93 | 191.77
2019-01-12 09:00 | 198.37 | 192.16
2019-01-12 09:30 | 198.89 | 192.71
2019-01-12 10:00 | 199.98 | 193.6
2019-01-12 10:30 | 200.69 | 194.71
2019-01-12 11:00 | 202.66 | 196.75
2019-01-12 11:30 | 204.45 | 198.34
2019-01-12 12:00 | 206.09 | 199.96
2019-01-12 12:30 | 223.53 | 217.53
2019-01-12 13:00 | 231.24 | 225.95
2019-01-12 13:30 | 225.03 | 219.81
2019-01-12 14:00 | 234.72 | 228.92
2019-01-12 14:30 | 237.55 | 231.79
2019-01-12 15:00 | 240.67 | 234.66
2019-01-12 15:30 | 242.15 | 236.09
2019-01-12 16:00 | 241.51 | 235.94
2019-01-12 16:30 | 243.27 | 237.89
2019-01-12 17:00 | 246.05 | 240.97
2019-01-12 17:30 | 250.55 | 244.35
2019-01-12 18:00 | 252.74 | 246.73
2019-01-12 18:30 | 253.84 | 247.65
2019-01-12 19:00 | 253.75 | 247.58
2019-01-12 19:30 | 253.34 | 246.98
2019-01-12 20:00 | 253.25 | 246.74
2019-01-12 20:30 | 250.18 | 243.46
2019-01-12 21:00 | 245.42 | 239.92
2019-01-12 21:30 | 240.56 | 236.39
2019-01-12 22:00 | 238 | 233.73
2019-01-12 22:30 | 235.27 | 230.8
2019-01-12 23:00 | 217.06 | 212.61
2019-01-12 23:30 | 178.97 | 174.5
2019-01-13 | 161.77 | 157.18
2019-01-13 00:30 | 161.17 | 156.43
2019-01-13 01:00 | 160.23 | 155.48
2019-01-13 01:30 | 158.64 | 154.02
2019-01-13 02:00 | 158.92 | 154.25
2019-01-13 02:30 | 158.1 | 153.2
2019-01-13 03:00 | 158.03 | 152.99
2019-01-13 03:30 | 157.41 | 152.41
2019-01-13 04:00 | 157.21 | 152.23
2019-01-13 04:30 | 156.66 | 151.74
2019-01-13 05:00 | 159.93 | 155.2
2019-01-13 05:30 | 160.2 | 155.43
2019-01-13 06:00 | 159.45 | 154.52
2019-01-13 06:30 | 160.44 | 155.6
2019-01-13 07:00 | 159.12 | 154.67
2019-01-13 07:30 | 159.29 | 154.83
2019-01-13 08:00 | 160.21 | 155.71
2019-01-13 08:30 | 158.76 | 153.75
2019-01-13 09:00 | 158.4 | 152.03
2019-01-13 09:30 | 159.24 | 152.58
2019-01-13 10:00 | 161.11 | 154.59
2019-01-13 10:30 | 153.39 | 147.89
2019-01-13 11:00 | 141.94 | 137.66
2019-01-13 11:30 | 168.36 | 162.7
2019-01-13 12:00 | 169.72 | 164.04
2019-01-13 12:30 | 171.77 | 166.01
2019-01-13 13:00 | 172.92 | 167.33
2019-01-13 13:30 | 174.99 | 169.39
2019-01-13 14:00 | 174.91 | 169.21
2019-01-13 14:30 | 175.87 | 169.78
2019-01-13 15:00 | 176.38 | 170.34
2019-01-13 15:30 | 209.12 | 203.46
2019-01-13 16:00 | 231.03 | 225.7
2019-01-13 16:30 | 243.79 | 238.6
2019-01-13 17:00 | 248.88 | 243.78
2019-01-13 17:30 | 250.97 | 245.35
2019-01-13 18:00 | 252.44 | 246.7
2019-01-13 18:30 | 253.75 | 248.08
2019-01-13 19:00 | 254.23 | 248.47
2019-01-13 19:30 | 254.14 | 248.39
2019-01-13 20:00 | 252.94 | 247.06
2019-01-13 20:30 | 250.27 | 244.65
2019-01-13 21:00 | 246.33 | 240.6
2019-01-13 21:30 | 243.23 | 238.14
2019-01-13 22:00 | 223.33 | 218.18
2019-01-13 22:30 | 185.44 | 179.98
2019-01-13 23:00 | 168.42 | 162.31
2019-01-13 23:30 | 166.59 | 160.46
2019-01-14 | 164.53 | 158.32
2019-01-14 00:30 | 162.39 | 157.35
2019-01-14 01:00 | 160.18 | 155.62
2019-01-14 01:30 | 158.78 | 154.16
2019-01-14 02:00 | 157.01 | 152.34
2019-01-14 02:30 | 155.49 | 150.75
2019-01-14 03:00 | 155.19 | 150.47
2019-01-14 03:30 | 154.31 | 149.54
2019-01-14 04:00 | 154.66 | 149.84
2019-01-14 04:30 | 154.23 | 149.43
2019-01-14 05:00 | 154.54 | 149.86
2019-01-14 05:30 | 155.12 | 150.58
2019-01-14 06:00 | 156.05 | 151.45
2019-01-14 06:30 | 192.17 | 187.11
2019-01-14 07:00 | 222.81 | 216.81
2019-01-14 07:30 | 229.2 | 222.98
2019-01-14 08:00 | 230.68 | 223.97
2019-01-14 08:30 | 230.24 | 223.72
2019-01-14 09:00 | 233.25 | 226.5
2019-01-14 09:30 | 233.44 | 226.6
2019-01-14 10:00 | 233.87 | 227.42
2019-01-14 10:30 | 234.46 | 228.04
2019-01-14 11:00 | 235.95 | 229.33
2019-01-14 11:30 | 237.35 | 230.81
2019-01-14 12:00 | 237.99 | 231.54
2019-01-14 12:30 | 238.82 | 232.55
2019-01-14 13:00 | 240.25 | 233.58
2019-01-14 13:30 | 241.24 | 234.78
2019-01-14 14:00 | 242.24 | 236.25
2019-01-14 14:30 | 246.01 | 240.36
2019-01-14 15:00 | 246.51 | 240.09
2019-01-14 15:30 | 246.33 | 239.99
2019-01-14 16:00 | 247.67 | 241.57
2019-01-14 16:30 | 249.46 | 243.42
2019-01-14 17:00 | 250.53 | 244.61
2019-01-14 17:30 | 252.59 | 246.26
2019-01-14 18:00 | 254.73 | 248.29
2019-01-14 18:30 | 255.81 | 249.43
2019-01-14 19:00 | 256.74 | 250.37
2019-01-14 19:30 | 256.27 | 250
2019-01-14 20:00 | 256.34 | 250
2019-01-14 20:30 | 253.61 | 247.29
2019-01-14 21:00 | 248.75 | 243.08
2019-01-14 21:30 | 245.08 | 239.74
2019-01-14 22:00 | 240.74 | 236.04
2019-01-14 22:30 | 237.01 | 232.73
2019-01-14 23:00 | 234.74 | 230.24
2019-01-14 23:30 | 232.64 | 228.41
2019-01-15 | 230.08 | 226.3
2019-01-15 00:30 | 228.77 | 225.19
2019-01-15 01:00 | 227.35 | 223.77
2019-01-15 01:30 | 227.07 | 223.22
2019-01-15 02:00 | 227.17 | 222.73
2019-01-15 02:30 | 226.4 | 221.98
2019-01-15 03:00 | 225.93 | 221.45
2019-01-15 03:30 | 225.43 | 220.94
2019-01-15 04:00 | 225.41 | 220.79
2019-01-15 04:30 | 225.83 | 221.21
2019-01-15 05:00 | 225.84 | 221.25
2019-01-15 05:30 | 226.42 | 221.94
2019-01-15 06:00 | 228.16 | 223.15
2019-01-15 06:30 | 230.81 | 224.87
2019-01-15 07:00 | 232.14 | 226.13
2019-01-15 07:30 | 234.25 | 228.15
2019-01-15 08:00 | 234.8 | 228.78
2019-01-15 08:30 | 234.4 | 228.57
2019-01-15 09:00 | 220.26 | 213.54
2019-01-15 09:30 | 215.58 | 209.13
2019-01-15 10:00 | 232.06 | 225.49
2019-01-15 10:30 | 237.67 | 231.22
2019-01-15 11:00 | 238.65 | 232.36
2019-01-15 11:30 | 239.85 | 233.66
2019-01-15 12:00 | 241.18 | 235.15
2019-01-15 12:30 | 242.45 | 236.47
2019-01-15 13:00 | 243.71 | 237.87
2019-01-15 13:30 | 245.14 | 239.51
2019-01-15 14:00 | 247.41 | 241.87
2019-01-15 14:30 | 248.6 | 243.06
2019-01-15 15:00 | 249.37 | 244.04
2019-01-15 15:30 | 250.05 | 244.95
2019-01-15 16:00 | 251.73 | 246.74
2019-01-15 16:30 | 253.79 | 248.54
2019-01-15 17:00 | 255.3 | 250.08
2019-01-15 17:30 | 256.05 | 250.77
2019-01-15 18:00 | 257.61 | 252.37
2019-01-15 18:30 | 258.96 | 253.72
2019-01-15 19:00 | 259.61 | 254.72
2019-01-15 19:30 | 259.89 | 254.95
2019-01-15 20:00 | 258.88 | 253.78
2019-01-15 20:30 | 255.85 | 250.38
2019-01-15 21:00 | 252.19 | 245.87
2019-01-15 21:30 | 247.38 | 241.98
2019-01-15 22:00 | 243.49 | 237.79
2019-01-15 22:30 | 239.37 | 233.45
2019-01-15 23:00 | 237.49 | 231.13
2019-01-15 23:30 | 235.8 | 229.35
2019-01-16 | 233.71 | 227.27
2019-01-16 00:30 | 232.16 | 225.91
2019-01-16 01:00 | 230.39 | 224.81
2019-01-16 01:30 | 228.49 | 223.47
2019-01-16 02:00 | 227.87 | 222.81
2019-01-16 02:30 | 227.14 | 221.93
2019-01-16 03:00 | 227.15 | 221.84
2019-01-16 03:30 | 226.61 | 221.44
2019-01-16 04:00 | 226.21 | 221.21
2019-01-16 04:30 | 226.5 | 221.63
2019-01-16 05:00 | 226.93 | 222.01
2019-01-16 05:30 | 226.67 | 221.84
2019-01-16 06:00 | 227.52 | 222.12
2019-01-16 06:30 | 229.86 | 224.09
2019-01-16 07:00 | 230.35 | 224.61
2019-01-16 07:30 | 232.28 | 226.67
2019-01-16 08:00 | 233.95 | 227.85
2019-01-16 08:30 | 234.17 | 228.51
2019-01-16 09:00 | 234.44 | 228.98
2019-01-16 09:30 | 235.15 | 229.48
2019-01-16 10:00 | 236.22 | 230.7
2019-01-16 10:30 | 236.55 | 231.59
2019-01-16 11:00 | 237.83 | 233.01
2019-01-16 11:30 | 239.92 | 234.76
2019-01-16 12:00 | 241.88 | 236.74
2019-01-16 12:30 | 242.69 | 237.79
2019-01-16 13:00 | 245.14 | 240.52
2019-01-16 13:30 | 245.98 | 241.3
2019-01-16 14:00 | 248.32 | 243.78
2019-01-16 14:30 | 249.42 | 244.98
2019-01-16 15:00 | 250.05 | 245.74
2019-01-16 15:30 | 251.2 | 247.09
2019-01-16 16:00 | 252.7 | 248.84
2019-01-16 16:30 | 254.12 | 250.03
2019-01-16 17:00 | 256.23 | 251.94
2019-01-16 17:30 | 256.06 | 251.38
2019-01-16 18:00 | 259.8 | 255.32
2019-01-16 18:30 | 261.68 | 257.24
2019-01-16 19:00 | 262.74 | 258.31
2019-01-16 19:30 | 262.68 | 258.13
2019-01-16 20:00 | 261.83 | 257.36
2019-01-16 20:30 | 258.96 | 254.24
2019-01-16 21:00 | 255.15 | 249.92
2019-01-16 21:30 | 250.81 | 245.64
2019-01-16 22:00 | 248.06 | 242.54
2019-01-16 22:30 | 244.6 | 238.86
2019-01-16 23:00 | 242 | 236.09
2019-01-16 23:30 | 240.64 | 234.58
2019-01-17 | 238.39 | 232.21
2019-01-17 00:30 | 237.18 | 231.31
2019-01-17 01:00 | 235.52 | 229.9
2019-01-17 01:30 | 234.73 | 228.91
2019-01-17 02:00 | 233.67 | 227.88
2019-01-17 02:30 | 233.11 | 226.98
2019-01-17 03:00 | 233.12 | 226.9
2019-01-17 03:30 | 232.31 | 226.27
2019-01-17 04:00 | 231.42 | 225.14
2019-01-17 04:30 | 230.57 | 224.44
2019-01-17 05:00 | 230.08 | 224.31
2019-01-17 05:30 | 230.97 | 225.63
2019-01-17 06:00 | 230.8 | 225.63
2019-01-17 06:30 | 233.8 | 228.43
2019-01-17 07:00 | 233.94 | 228.66
2019-01-17 07:30 | 241.13 | 235.94
2019-01-17 08:00 | 242.53 | 237.52
2019-01-17 08:30 | 244.95 | 240.17
2019-01-17 09:00 | 247.42 | 243.02
2019-01-17 09:30 | 249.53 | 244.45
2019-01-17 10:00 | 250.89 | 245.7
2019-01-17 10:30 | 250.77 | 245.59
2019-01-17 11:00 | 252.34 | 247.37
2019-01-17 11:30 | 255.74 | 251.01
2019-01-17 12:00 | 252.85 | 248.16
2019-01-17 12:30 | 253.07 | 248.13
2019-01-17 13:00 | 256.42 | 251.56
2019-01-17 13:30 | 258.38 | 253.35
2019-01-17 14:00 | 258.18 | 253.72
2019-01-17 14:30 | 259.56 | 254.8
2019-01-17 15:00 | 259.3 | 254.61
2019-01-17 15:30 | 260.65 | 256.03
2019-01-17 16:00 | 262.09 | 257.56
2019-01-17 16:30 | 262.8 | 258.26
2019-01-17 17:00 | 264.7 | 260.23
2019-01-17 17:30 | 265.77 | 261.03
2019-01-17 18:00 | 267.58 | 262.84
2019-01-17 18:30 | 268.74 | 263.79
2019-01-17 19:00 | 269.38 | 264.14
2019-01-17 19:30 | 267.95 | 262.78
2019-01-17 20:00 | 268.3 | 263.23
2019-01-17 20:30 | 266.35 | 260.79
2019-01-17 21:00 | 263.42 | 257.4
2019-01-17 21:30 | 259.8 | 253.59
2019-01-17 22:00 | 255.58 | 249.29
2019-01-17 22:30 | 251.83 | 245.44
2019-01-17 23:00 | 249.43 | 243.27
2019-01-17 23:30 | 247.29 | 240.81
2019-01-18 | 244.98 | 238.24
2019-01-18 00:30 | 244.11 | 236.86
2019-01-18 01:00 | 241.74 | 235.72
2019-01-18 01:30 | 240.83 | 234.7
2019-01-18 02:00 | 239.56 | 233.78
2019-01-18 02:30 | 238.69 | 232.81
2019-01-18 03:00 | 237.84 | 232.17
2019-01-18 03:30 | 237.37 | 231.91
2019-01-18 04:00 | 236.93 | 231.46
2019-01-18 04:30 | 236.67 | 231.11
2019-01-18 05:00 | 237.29 | 231.72
2019-01-18 05:30 | 238.18 | 232.67
2019-01-18 06:00 | 237.19 | 231.89
2019-01-18 06:30 | 240.89 | 234.85
2019-01-18 07:00 | 242.33 | 235.96
2019-01-18 07:30 | 243.17 | 237.59
2019-01-18 08:00 | 241.51 | 236.11
2019-01-18 08:30 | 241.2 | 235.8
2019-01-18 09:00 | 242.48 | 236.97
2019-01-18 09:30 | 241.8 | 236.18
2019-01-18 10:00 | 241.53 | 236.28
2019-01-18 10:30 | 241.71 | 236.11
2019-01-18 11:00 | 244.21 | 238.25
2019-01-18 11:30 | 245.3 | 239.5
2019-01-18 12:00 | 246.73 | 240.76
2019-01-18 12:30 | 247.95 | 241.51
2019-01-18 13:00 | 248.38 | 241.75
2019-01-18 13:30 | 249.47 | 242.96
2019-01-18 14:00 | 250.77 | 244.5
2019-01-18 14:30 | 252.61 | 246.42
2019-01-18 15:00 | 255.66 | 249.82
2019-01-18 15:30 | 256.12 | 250.64
2019-01-18 16:00 | 257.35 | 252.27
2019-01-18 16:30 | 260.02 | 254.9
2019-01-18 17:00 | 259.29 | 254.21
2019-01-18 17:30 | 259.46 | 253.85
2019-01-18 18:00 | 261.64 | 256.07
2019-01-18 18:30 | 262.71 | 256.95
2019-01-18 19:00 | 262.7 | 256.73
2019-01-18 19:30 | 262.43 | 256.46
2019-01-18 20:00 | 261.32 | 255.3
2019-01-18 20:30 | 259.4 | 252.98
2019-01-18 21:00 | 255.83 | 249.42
2019-01-18 21:30 | 253.2 | 246.68
2019-01-18 22:00 | 249.65 | 243.07
2019-01-18 22:30 | 247.1 | 240.36
2019-01-18 23:00 | 244.88 | 237.78
2019-01-18 23:30 | 244.64 | 237.69
2019-01-19 | 242.41 | 236.16
2019-01-19 00:30 | 240.87 | 235.28
2019-01-19 01:00 | 238.99 | 233.81
2019-01-19 01:30 | 237.94 | 232.65
2019-01-19 02:00 | 237.37 | 232.02
2019-01-19 02:30 | 236.33 | 231.51
2019-01-19 03:00 | 235.16 | 230.9
2019-01-19 03:30 | 234.98 | 230.68
2019-01-19 04:00 | 234.31 | 230.08
2019-01-19 04:30 | 233.88 | 229.64
2019-01-19 05:00 | 234.49 | 230.23
2019-01-19 05:30 | 233.92 | 229.74
2019-01-19 06:00 | 233.58 | 229.5
2019-01-19 06:30 | 234.65 | 230.66
2019-01-19 07:00 | 234.85 | 230.97
2019-01-19 07:30 | 234.96 | 231.28
2019-01-19 08:00 | 235.02 | 231.28
2019-01-19 08:30 | 238.67 | 234.67
2019-01-19 09:00 | 239.32 | 235.5
2019-01-19 09:30 | 240.98 | 236.49
2019-01-19 10:00 | 242.1 | 237.31
2019-01-19 10:30 | 242.83 | 238.18
2019-01-19 11:00 | 243.92 | 239.11
2019-01-19 11:30 | 245.89 | 240.68
2019-01-19 12:00 | 247.38 | 242.17
2019-01-19 12:30 | 248.62 | 243.43
2019-01-19 13:00 | 249.96 | 244.77
2019-01-19 13:30 | 251.26 | 245.95
2019-01-19 14:00 | 252.25 | 247.06
2019-01-19 14:30 | 253.3 | 248.18
2019-01-19 15:00 | 254.38 | 249.41
2019-01-19 15:30 | 257.22 | 252.54
2019-01-19 16:00 | 258.85 | 254.42
2019-01-19 16:30 | 260.56 | 256.24
2019-01-19 17:00 | 261.3 | 257.05
2019-01-19 17:30 | 264.02 | 259.94
2019-01-19 18:00 | 266.8 | 262.68
2019-01-19 18:30 | 267.69 | 263.54
2019-01-19 19:00 | 267.62 | 263.4
2019-01-19 19:30 | 266.67 | 262.41
2019-01-19 20:00 | 265.92 | 261.54
2019-01-19 20:30 | 263.69 | 259.05
2019-01-19 21:00 | 261.47 | 256.49
2019-01-19 21:30 | 258.22 | 253.62
2019-01-19 22:00 | 254.87 | 250.01
2019-01-19 22:30 | 252.04 | 246.89
2019-01-19 23:00 | 249.61 | 244.41
2019-01-19 23:30 | 248 | 242.6
2019-01-20 | 246 | 240.66
2019-01-20 00:30 | 244.04 | 239.31
2019-01-20 01:00 | 242.22 | 238.05
2019-01-20 01:30 | 241.01 | 237.04
2019-01-20 02:00 | 240.06 | 236
2019-01-20 02:30 | 239.47 | 235.34
2019-01-20 03:00 | 238.77 | 234.58
2019-01-20 03:30 | 237.97 | 233.86
2019-01-20 04:00 | 237.49 | 233.42
2019-01-20 04:30 | 237.48 | 233.4
2019-01-20 05:00 | 237.52 | 233.42
2019-01-20 05:30 | 237.54 | 233.46
2019-01-20 06:00 | 237.6 | 233.54
2019-01-20 06:30 | 237.98 | 233.99
2019-01-20 07:00 | 238.41 | 234.59
2019-01-20 07:30 | 239.05 | 235.28
2019-01-20 08:00 | 239.14 | 235.06
2019-01-20 08:30 | 239.93 | 235.74
2019-01-20 09:00 | 241 | 236.71
2019-01-20 09:30 | 242.81 | 238.15
2019-01-20 10:00 | 244.07 | 239.26
2019-01-20 10:30 | 245.02 | 240.13
2019-01-20 11:00 | 246.66 | 241.41
2019-01-20 11:30 | 247.82 | 242.79
2019-01-20 12:00 | 249.59 | 244.55
2019-01-20 12:30 | 250.95 | 246.09
2019-01-20 13:00 | 252.53 | 247.67
2019-01-20 13:30 | 254.23 | 249.26
2019-01-20 14:00 | 255.42 | 250.36
2019-01-20 14:30 | 256.67 | 251.59
2019-01-20 15:00 | 257.99 | 252.96
2019-01-20 15:30 | 259.36 | 254.5
2019-01-20 16:00 | 261.92 | 257.55
2019-01-20 16:30 | 264.51 | 259.53
2019-01-20 17:00 | 266.98 | 261.86
2019-01-20 17:30 | 268.46 | 263.46
2019-01-20 18:00 | 270.69 | 265.82
2019-01-20 18:30 | 271.41 | 266.54
2019-01-20 19:00 | 271.41 | 266.37
2019-01-20 19:30 | 271.23 | 266.2
2019-01-20 20:00 | 270 | 264.81
2019-01-20 20:30 | 268.17 | 262.6
2019-01-20 21:00 | 264.94 | 259.11
2019-01-20 21:30 | 260.38 | 255.48
2019-01-20 22:00 | 256.58 | 251.55
2019-01-20 22:30 | 253.64 | 248.14
2019-01-20 23:00 | 251.57 | 245.84
2019-01-20 23:30 | 249.69 | 243.86
2019-01-21 | 248.03 | 242.15
2019-01-21 00:30 | 247.1 | 241.47
2019-01-21 01:00 | 245.71 | 240.3
2019-01-21 01:30 | 245.52 | 239.94
2019-01-21 02:00 | 244.36 | 238.91
2019-01-21 02:30 | 243.15 | 237.77
2019-01-21 03:00 | 242.45 | 237
2019-01-21 03:30 | 241.9 | 236.45
2019-01-21 04:00 | 241.93 | 236.54
2019-01-21 04:30 | 241.99 | 236.59
2019-01-21 05:00 | 242.12 | 236.82
2019-01-21 05:30 | 242.78 | 237.67
2019-01-21 06:00 | 243.21 | 238.3
2019-01-21 06:30 | 246.15 | 240.73
2019-01-21 07:00 | 247.48 | 241.41
2019-01-21 07:30 | 249.39 | 243.18
2019-01-21 08:00 | 249.98 | 243.8
2019-01-21 08:30 | 249.43 | 243.55
2019-01-21 09:00 | 250.17 | 244.36
2019-01-21 09:30 | 250.91 | 244.83
2019-01-21 10:00 | 255.58 | 249.96
2019-01-21 10:30 | 255.23 | 249.9
2019-01-21 11:00 | 254.55 | 249.16
2019-01-21 11:30 | 253.14 | 247.59
2019-01-21 12:00 | 253.88 | 248.27
2019-01-21 12:30 | 257.07 | 251.77
2019-01-21 13:00 | 261.07 | 256.18
2019-01-21 13:30 | 262.8 | 258.28
2019-01-21 14:00 | 263.81 | 259.25
2019-01-21 14:30 | 262.12 | 257.52
2019-01-21 15:00 | 262.07 | 257.62
2019-01-21 15:30 | 263.43 | 258.97
2019-01-21 16:00 | 264.76 | 260.42
2019-01-21 16:30 | 264.81 | 260.31
2019-01-21 17:00 | 266.9 | 262.31
2019-01-21 17:30 | 267.03 | 262.36
2019-01-21 18:00 | 269.34 | 265.21
2019-01-21 18:30 | 270.36 | 266.24
2019-01-21 19:00 | 271.17 | 267.27
2019-01-21 19:30 | 271.95 | 268.05
2019-01-21 20:00 | 271.46 | 267.49
2019-01-21 20:30 | 269.19 | 264.92
2019-01-21 21:00 | 266.39 | 261.63
2019-01-21 21:30 | 262.36 | 258.16
2019-01-21 22:00 | 258.3 | 254.03
2019-01-21 22:30 | 255.5 | 250.86
2019-01-21 23:00 | 252.75 | 248.09
2019-01-21 23:30 | 250.75 | 246.06
2019-01-22 | 249.26 | 244.25
2019-01-22 00:30 | 248.24 | 243.36
2019-01-22 01:00 | 247.63 | 242.76
2019-01-22 01:30 | 246.88 | 241.93
2019-01-22 02:00 | 244.55 | 239.74
2019-01-22 02:30 | 243.46 | 238.86
2019-01-22 03:00 | 243.07 | 238.52
2019-01-22 03:30 | 242.42 | 237.91
2019-01-22 04:00 | 242.64 | 238.14
2019-01-22 04:30 | 242.18 | 237.62
2019-01-22 05:00 | 241.55 | 236.92
2019-01-22 05:30 | 242.63 | 238.02
2019-01-22 06:00 | 242.98 | 238.51
2019-01-22 06:30 | 244.88 | 239.93
2019-01-22 07:00 | 246.46 | 240.9
2019-01-22 07:30 | 248.86 | 242.83
2019-01-22 08:00 | 248.03 | 242.13
2019-01-22 08:30 | 248.34 | 242.62
2019-01-22 09:00 | 248.64 | 243.04
2019-01-22 09:30 | 248.47 | 243.22
2019-01-22 10:00 | 249.31 | 244.22
2019-01-22 10:30 | 249.18 | 244.18
2019-01-22 11:00 | 250.6 | 245.29
2019-01-22 11:30 | 251.97 | 246.58
2019-01-22 12:00 | 252.61 | 247.66
2019-01-22 12:30 | 252.72 | 248.01
2019-01-22 13:00 | 254.83 | 249.88
2019-01-22 13:30 | 256.59 | 251.95
2019-01-22 14:00 | 257.57 | 253.32
2019-01-22 14:30 | 258.97 | 254.95
2019-01-22 15:00 | 260.87 | 256.59
2019-01-22 15:30 | 262.7 | 258.42
2019-01-22 16:00 | 263.65 | 259.35
2019-01-22 16:30 | 265.16 | 260.87
2019-01-22 17:00 | 266.4 | 262.23
2019-01-22 17:30 | 268.51 | 264.22
2019-01-22 18:00 | 271.46 | 267.17
2019-01-22 18:30 | 274.01 | 269.54
2019-01-22 19:00 | 273.88 | 269.89
2019-01-22 19:30 | 274.01 | 269.98
2019-01-22 20:00 | 273.3 | 269.14
2019-01-22 20:30 | 271.13 | 266.66
2019-01-22 21:00 | 266.83 | 261.8
2019-01-22 21:30 | 262.37 | 258.12
2019-01-22 22:00 | 258.38 | 253.87
2019-01-22 22:30 | 254.66 | 249.73
2019-01-22 23:00 | 252.79 | 247.46
2019-01-22 23:30 | 251.16 | 245.95
2019-01-23 | 248.1 | 243.37
2019-01-23 00:30 | 247 | 242.93
2019-01-23 01:00 | 245.24 | 241.85
2019-01-23 01:30 | 244.84 | 241.48
2019-01-23 02:00 | 243.85 | 240.44
2019-01-23 02:30 | 242.88 | 239.5
2019-01-23 03:00 | 242.14 | 238.77
2019-01-23 03:30 | 241.56 | 238.21
2019-01-23 04:00 | 241.29 | 237.9
2019-01-23 04:30 | 241.39 | 238.06
2019-01-23 05:00 | 241.55 | 238.3
2019-01-23 05:30 | 241.92 | 238.52
2019-01-23 06:00 | 243.74 | 239.35
2019-01-23 06:30 | 246.89 | 241.35
2019-01-23 07:00 | 248.19 | 241.94
2019-01-23 07:30 | 249.07 | 243.2
2019-01-23 08:00 | 249.1 | 243.47
2019-01-23 08:30 | 248.98 | 243.68
2019-01-23 09:00 | 249.22 | 243.98
2019-01-23 09:30 | 248.19 | 243.15
2019-01-23 10:00 | 248.96 | 243.86
2019-01-23 10:30 | 249.34 | 244.49
2019-01-23 11:00 | 250.05 | 245.31
2019-01-23 11:30 | 251.29 | 246.76
2019-01-23 12:00 | 251.3 | 247.17
2019-01-23 12:30 | 252.82 | 248.71
2019-01-23 13:00 | 255.26 | 250.82
2019-01-23 13:30 | 258.07 | 253.75
2019-01-23 14:00 | 259.52 | 255.52
2019-01-23 14:30 | 261.51 | 257.6
2019-01-23 15:00 | 262.11 | 258.2
2019-01-23 15:30 | 263.85 | 260.02
2019-01-23 16:00 | 248.29 | 244.65
2019-01-23 16:30 | 220.89 | 217.67
2019-01-23 17:00 | 219.9 | 216.77
2019-01-23 17:30 | 220.61 | 217.36
2019-01-23 18:00 | 259.11 | 254.87
2019-01-23 18:30 | 272.21 | 267.5
2019-01-23 19:00 | 272.37 | 267.6
2019-01-23 19:30 | 272.51 | 267.71
2019-01-23 20:00 | 271.13 | 266.26
2019-01-23 20:30 | 267.67 | 262.55
2019-01-23 21:00 | 263.9 | 258.91
2019-01-23 21:30 | 260.43 | 256.16
2019-01-23 22:00 | 255.78 | 251.31
2019-01-23 22:30 | 252.81 | 247.99
2019-01-23 23:00 | 250.23 | 245.13
2019-01-23 23:30 | 248.42 | 243.24
2019-01-24 | 246.43 | 241.23
2019-01-24 00:30 | 245.44 | 240.29
2019-01-24 01:00 | 243.95 | 239.59
2019-01-24 01:30 | 243.27 | 238.65
2019-01-24 02:00 | 242.48 | 237.67
2019-01-24 02:30 | 241.19 | 236.3
2019-01-24 03:00 | 240.15 | 235.65
2019-01-24 03:30 | 239.31 | 234.74
2019-01-24 04:00 | 238.8 | 234.11
2019-01-24 04:30 | 238.86 | 234.21
2019-01-24 05:00 | 238.95 | 234.31
2019-01-24 05:30 | 240.48 | 235.39
2019-01-24 06:00 | 241.85 | 236.61
2019-01-24 06:30 | 244.77 | 238.1
2019-01-24 07:00 | 246.63 | 239.92
2019-01-24 07:30 | 249.78 | 243.48
2019-01-24 08:00 | 250.1 | 244.07
2019-01-24 08:30 | 250.32 | 244.39
2019-01-24 09:00 | 250 | 244.49
2019-01-24 09:30 | 251.19 | 245.65
2019-01-24 10:00 | 252.47 | 247.3
2019-01-24 10:30 | 253.19 | 248.34
2019-01-24 11:00 | 255.07 | 250.06
2019-01-24 11:30 | 257.11 | 251.64
2019-01-24 12:00 | 258.97 | 253.63
2019-01-24 12:30 | 258.6 | 253.27
2019-01-24 13:00 | 260.07 | 254.85
2019-01-24 13:30 | 262.86 | 257.85
2019-01-24 14:00 | 265.86 | 261.71
2019-01-24 14:30 | 266.91 | 262.94
2019-01-24 15:00 | 267.7 | 263.83
2019-01-24 15:30 | 269.43 | 265.2
2019-01-24 16:00 | 269.57 | 265.9
2019-01-24 16:30 | 269.75 | 265.7
2019-01-24 17:00 | 270.56 | 266.35
2019-01-24 17:30 | 272.35 | 268.01
2019-01-24 18:00 | 274.06 | 269.85
2019-01-24 18:30 | 275.03 | 270.77
2019-01-24 19:00 | 276.43 | 272.12
2019-01-24 19:30 | 275.55 | 271.27
2019-01-24 20:00 | 274.35 | 269.92
2019-01-24 20:30 | 271.75 | 266.9
2019-01-24 21:00 | 268.99 | 263.67
2019-01-24 21:30 | 265.4 | 260.67
2019-01-24 22:00 | 261.01 | 255.98
2019-01-24 22:30 | 258.27 | 252.98
2019-01-24 23:00 | 255.52 | 249.92
2019-01-24 23:30 | 253.96 | 248.35
2019-01-25 | 252.96 | 247.38
2019-01-25 00:30 | 252.1 | 246.38
2019-01-25 01:00 | 250.57 | 244.9
2019-01-25 01:30 | 249.4 | 243.69
2019-01-25 02:00 | 248.91 | 243.15
2019-01-25 02:30 | 247.58 | 242.27
2019-01-25 03:00 | 246.36 | 241.38
2019-01-25 03:30 | 245.29 | 240.41
2019-01-25 04:00 | 244.76 | 239.81
2019-01-25 04:30 | 244.58 | 239.46
2019-01-25 05:00 | 245.45 | 240.4
2019-01-25 05:30 | 245.9 | 240.8
2019-01-25 06:00 | 246.68 | 241.87
2019-01-25 06:30 | 248.27 | 243.1
2019-01-25 07:00 | 249.65 | 244.52
2019-01-25 07:30 | 250.28 | 245.41
2019-01-25 08:00 | 249.66 | 244.87
2019-01-25 08:30 | 249.32 | 244.67
2019-01-25 09:00 | 250.17 | 245.54
2019-01-25 09:30 | 249.63 | 244.75
2019-01-25 10:00 | 249.86 | 244.92
2019-01-25 10:30 | 249.6 | 244.45
2019-01-25 11:00 | 250.97 | 245.52
2019-01-25 11:30 | 251.96 | 246.47
2019-01-25 12:00 | 252.41 | 247.22
2019-01-25 12:30 | 254.15 | 249.59
2019-01-25 13:00 | 256.4 | 251.39
2019-01-25 13:30 | 257.59 | 252.44
2019-01-25 14:00 | 258.63 | 253.83
2019-01-25 14:30 | 259.86 | 255.64
2019-01-25 15:00 | 260.16 | 255.92
2019-01-25 15:30 | 261.68 | 257.28
2019-01-25 16:00 | 264.61 | 260.14
2019-01-25 16:30 | 266.74 | 262.21
2019-01-25 17:00 | 268.66 | 264.1
2019-01-25 17:30 | 268.62 | 263.89
2019-01-25 18:00 | 270.07 | 265.17
2019-01-25 18:30 | 270.41 | 265.61
2019-01-25 19:00 | 269.96 | 265
2019-01-25 19:30 | 270.71 | 265.57
2019-01-25 20:00 | 269.95 | 264.84
2019-01-25 20:30 | 268.85 | 263.22
2019-01-25 21:00 | 266.06 | 260.47
2019-01-25 21:30 | 262.74 | 257.7
2019-01-25 22:00 | 259.6 | 254.26
2019-01-25 22:30 | 257.24 | 251.42
2019-01-25 23:00 | 255.32 | 249.15
2019-01-25 23:30 | 253.32 | 247.25
2019-01-26 | 250.24 | 244.86
2019-01-26 00:30 | 249.01 | 243.58
2019-01-26 01:00 | 248.12 | 242.83
2019-01-26 01:30 | 247.05 | 241.78
2019-01-26 02:00 | 246.23 | 240.89
2019-01-26 02:30 | 245.62 | 240.27
2019-01-26 03:00 | 245.19 | 239.81
2019-01-26 03:30 | 244.34 | 238.95
2019-01-26 04:00 | 243.58 | 238.22
2019-01-26 04:30 | 243.52 | 238.17
2019-01-26 05:00 | 243.29 | 237.89
2019-01-26 05:30 | 243.17 | 237.79
2019-01-26 06:00 | 242.89 | 237.58
2019-01-26 06:30 | 243.18 | 238.08
2019-01-26 07:00 | 242.11 | 237.24
2019-01-26 07:30 | 242.97 | 238.11
2019-01-26 08:00 | 242.31 | 237.23
2019-01-26 08:30 | 243.73 | 238.15
2019-01-26 09:00 | 245.28 | 239.79
2019-01-26 09:30 | 246.3 | 240.62
2019-01-26 10:00 | 246.84 | 241.42
2019-01-26 10:30 | 247.04 | 242.1
2019-01-26 11:00 | 249.1 | 243.06
2019-01-26 11:30 | 250.46 | 244.11
2019-01-26 12:00 | 250.9 | 244.66
2019-01-26 12:30 | 251.82 | 245.54
2019-01-26 13:00 | 253.52 | 247.32
2019-01-26 13:30 | 254.47 | 248.06
2019-01-26 14:00 | 254.97 | 248.44
2019-01-26 14:30 | 256.07 | 249.74
2019-01-26 15:00 | 258.44 | 252.21
2019-01-26 15:30 | 258.99 | 254.17
2019-01-26 16:00 | 243.46 | 238.84
2019-01-26 16:30 | 208.05 | 202.29
2019-01-26 17:00 | 209.79 | 203.93
2019-01-26 17:30 | 210.88 | 205.15
2019-01-26 18:00 | 211.85 | 206.21
2019-01-26 18:30 | 212.43 | 206.86
2019-01-26 19:00 | 212.45 | 206.96
2019-01-26 19:30 | 211.84 | 206.29
2019-01-26 20:00 | 211.75 | 206.08
2019-01-26 20:30 | 209.47 | 203.51
2019-01-26 21:00 | 207.15 | 200.93
2019-01-26 21:30 | 204.08 | 198.7
2019-01-26 22:00 | 200.52 | 195.65
2019-01-26 22:30 | 198.14 | 192.99
2019-01-26 23:00 | 197.37 | 192.27
2019-01-26 23:30 | 194.65 | 189.28
2019-01-27 | 192.02 | 186.55
2019-01-27 00:30 | 191 | 185.49
2019-01-27 01:00 | 189.24 | 183.96
2019-01-27 01:30 | 188.12 | 182.74
2019-01-27 02:00 | 187.83 | 182.39
2019-01-27 02:30 | 186.98 | 181.56
2019-01-27 03:00 | 186.64 | 181.13
2019-01-27 03:30 | 186.14 | 180.66
2019-01-27 04:00 | 185.49 | 180.14
2019-01-27 04:30 | 185.14 | 179.71
2019-01-27 05:00 | 185.19 | 179.52
2019-01-27 05:30 | 184.56 | 178.87
2019-01-27 06:00 | 184.59 | 178.94
2019-01-27 06:30 | 185.29 | 179.64
2019-01-27 07:00 | 187.38 | 181.26
2019-01-27 07:30 | 187.97 | 181.67
2019-01-27 08:00 | 187.86 | 181.57
2019-01-27 08:30 | 188.08 | 181.68
2019-01-27 09:00 | 188.23 | 181.87
2019-01-27 09:30 | 187.54 | 181.18
2019-01-27 10:00 | 187.9 | 181.5
2019-01-27 10:30 | 188.12 | 181.9
2019-01-27 11:00 | 188.69 | 182.3
2019-01-27 11:30 | 190.99 | 184.64
2019-01-27 12:00 | 194.78 | 188.25
2019-01-27 12:30 | 197.15 | 190.61
2019-01-27 13:00 | 198.72 | 192.29
2019-01-27 13:30 | 200.02 | 193.69
2019-01-27 14:00 | 201.39 | 194.99
2019-01-27 14:30 | 202.49 | 195.81
2019-01-27 15:00 | 204.03 | 197.53
2019-01-27 15:30 | 205.73 | 199.39
2019-01-27 16:00 | 207.3 | 201.03
2019-01-27 16:30 | 209.55 | 203.31
2019-01-27 17:00 | 211.24 | 205.16
2019-01-27 17:30 | 212.53 | 206.59
2019-01-27 18:00 | 215.12 | 209.34
2019-01-27 18:30 | 216.05 | 210.33
2019-01-27 19:00 | 215.78 | 210.03
2019-01-27 19:30 | 215.62 | 209.94
2019-01-27 20:00 | 214.24 | 208.52
2019-01-27 20:30 | 211.65 | 205.67
2019-01-27 21:00 | 208.2 | 201.89
2019-01-27 21:30 | 204.98 | 198.86
2019-01-27 22:00 | 202.19 | 195.89
2019-01-27 22:30 | 199.5 | 192.77
2019-01-27 23:00 | 197.72 | 191.05
2019-01-27 23:30 | 195.22 | 189.4
2019-01-28 | 193.77 | 187.87
2019-01-28 00:30 | 192.98 | 186.91
2019-01-28 01:00 | 191.97 | 185.9
2019-01-28 01:30 | 190.97 | 185.02
2019-01-28 02:00 | 189.82 | 183.92
2019-01-28 02:30 | 189.12 | 183.33
2019-01-28 03:00 | 188.03 | 182.12
2019-01-28 03:30 | 186.47 | 180.41
2019-01-28 04:00 | 185.84 | 179.87
2019-01-28 04:30 | 185.9 | 179.93
2019-01-28 05:00 | 185.91 | 180.05
2019-01-28 05:30 | 186.27 | 180.44
2019-01-28 06:00 | 186.35 | 180.68
2019-01-28 06:30 | 186.76 | 180.95
2019-01-28 07:00 | 186.95 | 181.07
2019-01-28 07:30 | 187.1 | 181.22
2019-01-28 08:00 | 186.9 | 181.06
2019-01-28 08:30 | 185.87 | 180.08
2019-01-28 09:00 | 186.11 | 180.29
2019-01-28 09:30 | 187.41 | 180.87
2019-01-28 10:00 | 187.69 | 180.99
2019-01-28 10:30 | 188.3 | 181.59
2019-01-28 11:00 | 189.53 | 182.9
2019-01-28 11:30 | 191.13 | 184.7
2019-01-28 12:00 | 193.37 | 187.22
2019-01-28 12:30 | 197.26 | 191.24
2019-01-28 13:00 | 198.17 | 192.4
2019-01-28 13:30 | 200.54 | 194.56
2019-01-28 14:00 | 201.34 | 195.47
2019-01-28 14:30 | 201.67 | 195.42
2019-01-28 15:00 | 201.24 | 194.8
2019-01-28 15:30 | 202.38 | 196.01
2019-01-28 16:00 | 202.94 | 196.82
2019-01-28 16:30 | 204.6 | 198.32
2019-01-28 17:00 | 205.69 | 199.11
2019-01-28 17:30 | 207.78 | 201.31
2019-01-28 18:00 | 210.01 | 203.7
2019-01-28 18:30 | 211.03 | 205.13
2019-01-28 19:00 | 211.34 | 205.49
2019-01-28 19:30 | 211.06 | 205.19
2019-01-28 20:00 | 210.16 | 204.09
2019-01-28 20:30 | 207.28 | 200.78
2019-01-28 21:00 | 203.76 | 196.86
2019-01-28 21:30 | 200.68 | 194.28
2019-01-28 22:00 | 197.32 | 190.96
2019-01-28 22:30 | 194 | 187.06
2019-01-28 23:00 | 192.33 | 185.23
2019-01-28 23:30 | 190.87 | 183.73
2019-01-29 | 189.66 | 182.48
2019-01-29 00:30 | 188.62 | 181.54
2019-01-29 01:00 | 187.47 | 180.42
2019-01-29 01:30 | 186.52 | 179.41
2019-01-29 02:00 | 186.18 | 178.97
2019-01-29 02:30 | 184.87 | 177.93
2019-01-29 03:00 | 184.07 | 177.12
2019-01-29 03:30 | 183.74 | 176.58
2019-01-29 04:00 | 183.04 | 175.87
2019-01-29 04:30 | 183.09 | 175.99
2019-01-29 05:00 | 183.83 | 176.82
2019-01-29 05:30 | 184.68 | 177.77
2019-01-29 06:00 | 186.08 | 178.85
2019-01-29 06:30 | 188.06 | 180.46
2019-01-29 07:00 | 189.8 | 181.88
2019-01-29 07:30 | 191.34 | 183.39
2019-01-29 08:00 | 192.31 | 184.39
2019-01-29 08:30 | 192.12 | 184.14
2019-01-29 09:00 | 192.12 | 184.24
2019-01-29 09:30 | 191.23 | 183.51
2019-01-29 10:00 | 191.34 | 183.79
2019-01-29 10:30 | 192.4 | 184.8
2019-01-29 11:00 | 193.76 | 186.36
2019-01-29 11:30 | 194.21 | 186.62
2019-01-29 12:00 | 195.6 | 187.44
2019-01-29 12:30 | 195.44 | 187.17
2019-01-29 13:00 | 196.85 | 188.72
2019-01-29 13:30 | 198.88 | 190.92
2019-01-29 14:00 | 201.18 | 193.88
2019-01-29 14:30 | 201.06 | 193.79
2019-01-29 15:00 | 202.28 | 194.72
2019-01-29 15:30 | 202.66 | 195.09
2019-01-29 16:00 | 205.17 | 197.29
2019-01-29 16:30 | 205.05 | 197.46
2019-01-29 17:00 | 205.87 | 198.4
2019-01-29 17:30 | 206.92 | 199.52
2019-01-29 18:00 | 208.13 | 200.77
2019-01-29 18:30 | 208.4 | 201.14
2019-01-29 19:00 | 209.37 | 202.25
2019-01-29 19:30 | 209.85 | 202.71
2019-01-29 20:00 | 209.37 | 202.13
2019-01-29 20:30 | 207.08 | 199.48
2019-01-29 21:00 | 204.82 | 196.8
2019-01-29 21:30 | 202.38 | 194.72
2019-01-29 22:00 | 198.5 | 190.72
2019-01-29 22:30 | 195.05 | 187.06
2019-01-29 23:00 | 192.84 | 184.83
2019-01-29 23:30 | 191.65 | 183.54
2019-01-30 | 189.97 | 181.87
2019-01-30 00:30 | 189.24 | 181.06
2019-01-30 01:00 | 188.09 | 180.07
2019-01-30 01:30 | 187.29 | 179.04
2019-01-30 02:00 | 186.89 | 178.45
2019-01-30 02:30 | 185.95 | 177.66
2019-01-30 03:00 | 185.52 | 177.12
2019-01-30 03:30 | 184.99 | 176.6
2019-01-30 04:00 | 184.84 | 176.54
2019-01-30 04:30 | 184.64 | 176.3
2019-01-30 05:00 | 185.36 | 177.02
2019-01-30 05:30 | 185.44 | 177.14
2019-01-30 06:00 | 186.52 | 177.95
2019-01-30 06:30 | 187.84 | 179.65
2019-01-30 07:00 | 189.05 | 180.57
2019-01-30 07:30 | 190.1 | 181.99
2019-01-30 08:00 | 189.13 | 181.66
2019-01-30 08:30 | 189.02 | 181.15
2019-01-30 09:00 | 188.21 | 180.11
2019-01-30 09:30 | 188.97 | 180.87
2019-01-30 10:00 | 189.05 | 180.89
2019-01-30 10:30 | 188.7 | 180.4
2019-01-30 11:00 | 189.33 | 181.23
2019-01-30 11:30 | 189.77 | 181.86
2019-01-30 12:00 | 191.37 | 183.79
2019-01-30 12:30 | 192.43 | 184.9
2019-01-30 13:00 | 192.98 | 185.19
2019-01-30 13:30 | 194.1 | 186.33
2019-01-30 14:00 | 195.57 | 187.78
2019-01-30 14:30 | 196.22 | 188.57
2019-01-30 15:00 | 196.8 | 189.15
2019-01-30 15:30 | 197.43 | 189.7
2019-01-30 16:00 | 198.97 | 191.36
2019-01-30 16:30 | 200.08 | 192.34
2019-01-30 17:00 | 200.25 | 193.02
2019-01-30 17:30 | 200.26 | 194.22
2019-01-30 18:00 | 201 | 195.36
2019-01-30 18:30 | 201.68 | 196.1
2019-01-30 19:00 | 201.87 | 196.37
2019-01-30 19:30 | 202.31 | 196.79
2019-01-30 20:00 | 201.5 | 195.78
2019-01-30 20:30 | 199.11 | 193.15
2019-01-30 21:00 | 196.8 | 190.51
2019-01-30 21:30 | 194.78 | 188.25
2019-01-30 22:00 | 192.44 | 186
2019-01-30 22:30 | 188.37 | 182.67
2019-01-30 23:00 | 185.28 | 179.83
2019-01-30 23:30 | 184.78 | 179.14
2019-01-31 | 183.13 | 177.62
2019-01-31 00:30 | 182.25 | 176.64
2019-01-31 01:00 | 180.99 | 175.24
2019-01-31 01:30 | 180.14 | 174.17
2019-01-31 02:00 | 179.53 | 173.72
2019-01-31 02:30 | 178.77 | 172.46
2019-01-31 03:00 | 179.06 | 172.42
2019-01-31 03:30 | 179.12 | 172.39
2019-01-31 04:00 | 179.06 | 172.32
2019-01-31 04:30 | 178.75 | 172.06
2019-01-31 05:00 | 178.77 | 172.01
2019-01-31 05:30 | 173.5 | 167.43
2019-01-31 06:00 | 165.22 | 159.89
2019-01-31 06:30 | 159.12 | 154.09
2019-01-31 07:00 | 163.49 | 158.55
2019-01-31 07:30 | 154.8 | 150.01
2019-01-31 08:00 | 149.41 | 144.27
2019-01-31 08:30 | 146.79 | 141.43
2019-01-31 09:00 | 147.33 | 142.07
2019-01-31 09:30 | 149.27 | 143.84
2019-01-31 10:00 | 150.8 | 145.36
2019-01-31 10:30 | 146.37 | 141.16
2019-01-31 11:00 | 147.13 | 142.12
2019-01-31 11:30 | 148.16 | 143.18
2019-01-31 12:00 | 149.71 | 144.74
2019-01-31 12:30 | 150.19 | 145.36
2019-01-31 13:00 | 151.43 | 146.63
2019-01-31 13:30 | 152.35 | 147.52
2019-01-31 14:00 | 155.57 | 150.88
2019-01-31 14:30 | 157.13 | 152.6
2019-01-31 15:00 | 157.16 | 152.73
2019-01-31 15:30 | 158.77 | 154.48
2019-01-31 16:00 | 160.51 | 156.17
2019-01-31 16:30 | 162.16 | 157.77
2019-01-31 17:00 | 163.4 | 159.03
2019-01-31 17:30 | 163.08 | 158.62
2019-01-31 18:00 | 164.45 | 160.06
2019-01-31 18:30 | 164.86 | 160.52
2019-01-31 19:00 | 165.3 | 160.91
2019-01-31 19:30 | 165 | 160.62
2019-01-31 20:00 | 163.55 | 159.1
2019-01-31 20:30 | 161.33 | 156.72
2019-01-31 21:00 | 158.51 | 153.82
2019-01-31 21:30 | 155.45 | 150.76
2019-01-31 22:00 | 152.88 | 148.28
2019-01-31 22:30 | 150.74 | 146
2019-01-31 23:00 | 148.71 | 143.86
2019-01-31 23:30 | 147.01 | 142.17
2019-02-01 | 143.69 | 139.07
2019-02-01 00:30 | 143.2 | 138.52
2019-02-01 01:00 | 142.35 | 137.58
2019-02-01 01:30 | 141.54 | 136.73
2019-02-01 02:00 | 141.09 | 136.24
2019-02-01 02:30 | 140.19 | 135.32
2019-02-01 03:00 | 139.66 | 134.75
2019-02-01 03:30 | 139.37 | 134.45
2019-02-01 04:00 | 138.84 | 133.95
2019-02-01 04:30 | 138.71 | 133.87
2019-02-01 05:00 | 138.96 | 134.15
2019-02-01 05:30 | 139.71 | 134.95
2019-02-01 06:00 | 140.71 | 135.87
2019-02-01 06:30 | 141.92 | 136.92
2019-02-01 07:00 | 143.27 | 138.02
2019-02-01 07:30 | 144.16 | 139
2019-02-01 08:00 | 145.29 | 140.11
2019-02-01 08:30 | 145.95 | 140.85
2019-02-01 09:00 | 145.57 | 140.34
2019-02-01 09:30 | 145.38 | 140.13
2019-02-01 10:00 | 146.15 | 141.02
2019-02-01 10:30 | 147.16 | 141.88
2019-02-01 11:00 | 149.14 | 143.91
2019-02-01 11:30 | 153.46 | 148.37
2019-02-01 12:00 | 161.43 | 156.78
2019-02-01 12:30 | 162.93 | 158.11
2019-02-01 13:00 | 163.87 | 158.93
2019-02-01 13:30 | 165.16 | 160.2
2019-02-01 14:00 | 166.25 | 161.19
2019-02-01 14:30 | 166.86 | 162.13
2019-02-01 15:00 | 166.18 | 161.61
2019-02-01 15:30 | 166.73 | 162.27
2019-02-01 16:00 | 168.04 | 163.93
2019-02-01 16:30 | 169.55 | 165.5
2019-02-01 17:00 | 170.43 | 166.37
2019-02-01 17:30 | 170.46 | 166.28
2019-02-01 18:00 | 171.17 | 167.06
2019-02-01 18:30 | 171.07 | 167.01
2019-02-01 19:00 | 171.34 | 167.32
2019-02-01 19:30 | 170.89 | 166.92
2019-02-01 20:00 | 170.59 | 166.6
2019-02-01 20:30 | 168.72 | 164.6
2019-02-01 21:00 | 166.56 | 162.31
2019-02-01 21:30 | 164.9 | 160.58
2019-02-01 22:00 | 162.53 | 158.13
2019-02-01 22:30 | 160.22 | 155.88
2019-02-01 23:00 | 158.42 | 153.95
2019-02-01 23:30 | 157.2 | 152.65
2019-02-02 | 155.51 | 150.87
2019-02-02 00:30 | 154.4 | 149.78
2019-02-02 01:00 | 152.81 | 148.27
2019-02-02 01:30 | 151.87 | 147.27
2019-02-02 02:00 | 151.12 | 146.49
2019-02-02 02:30 | 150.6 | 145.95
2019-02-02 03:00 | 150.1 | 145.44
2019-02-02 03:30 | 149.51 | 144.8
2019-02-02 04:00 | 148.97 | 144.33
2019-02-02 04:30 | 148.5 | 143.81
2019-02-02 05:00 | 148.44 | 143.72
2019-02-02 05:30 | 148.68 | 143.96
2019-02-02 06:00 | 148.99 | 144.27
2019-02-02 06:30 | 149.17 | 144.48
2019-02-02 07:00 | 149.8 | 145.04
2019-02-02 07:30 | 150.27 | 145.62
2019-02-02 08:00 | 149.76 | 145.3
2019-02-02 08:30 | 150.33 | 145.95
2019-02-02 09:00 | 150.23 | 145.78
2019-02-02 09:30 | 150.21 | 145.64
2019-02-02 10:00 | 150.65 | 146.05
2019-02-02 10:30 | 151.59 | 147.05
2019-02-02 11:00 | 151.75 | 147.23
2019-02-02 11:30 | 152.11 | 147.59
2019-02-02 12:00 | 152.61 | 148.25
2019-02-02 12:30 | 152.65 | 148.44
2019-02-02 13:00 | 155.23 | 150.6
2019-02-02 13:30 | 157.06 | 151.98
2019-02-02 14:00 | 157.91 | 152.76
2019-02-02 14:30 | 158.37 | 153.26
2019-02-02 15:00 | 158.37 | 153.54
2019-02-02 15:30 | 157.97 | 153.6
2019-02-02 16:00 | 158.82 | 154.53
2019-02-02 16:30 | 160.19 | 155.97
2019-02-02 17:00 | 161.27 | 157.16
2019-02-02 17:30 | 162.74 | 158.73
2019-02-02 18:00 | 158.47 | 154.18
2019-02-02 18:30 | 171.16 | 166.29
2019-02-02 19:00 | 175.09 | 170.16
2019-02-02 19:30 | 175.67 | 170.79
2019-02-02 20:00 | 175.63 | 170.75
2019-02-02 20:30 | 174.13 | 169.07
2019-02-02 21:00 | 171.98 | 166.62
2019-02-02 21:30 | 170.78 | 165.56
2019-02-02 22:00 | 169.78 | 164.41
2019-02-02 22:30 | 167.42 | 162.09
2019-02-02 23:00 | 144.2 | 138.92
2019-02-02 23:30 | 141.6 | 136.34
2019-02-03 | 140.33 | 135.23
2019-02-03 00:30 | 138.88 | 133.86
2019-02-03 01:00 | 137.59 | 132.71
2019-02-03 01:30 | 136.1 | 131.38
2019-02-03 02:00 | 135.34 | 130.65
2019-02-03 02:30 | 134.48 | 129.73
2019-02-03 03:00 | 133.97 | 129.28
2019-02-03 03:30 | 133.54 | 128.82
2019-02-03 04:00 | 133.32 | 128.62
2019-02-03 04:30 | 132.8 | 128.02
2019-02-03 05:00 | 132.44 | 127.62
2019-02-03 05:30 | 132.47 | 127.77
2019-02-03 06:00 | 132.03 | 127.42
2019-02-03 06:30 | 132.68 | 128.16
2019-02-03 07:00 | 148.3 | 143.56
2019-02-03 07:30 | 157.87 | 152.78
2019-02-03 08:00 | 158.96 | 152.87
2019-02-03 08:30 | 158.7 | 152.58
2019-02-03 09:00 | 159.19 | 152.82
2019-02-03 09:30 | 159.33 | 151.88
2019-02-03 10:00 | 159.41 | 151.66
2019-02-03 10:30 | 160.37 | 152.23
2019-02-03 11:00 | 160.17 | 152.07
2019-02-03 11:30 | 161.6 | 153.77
2019-02-03 12:00 | 163.6 | 155.72
2019-02-03 12:30 | 165.21 | 157.39
2019-02-03 13:00 | 166.34 | 158.73
2019-02-03 13:30 | 166.68 | 159.18
2019-02-03 14:00 | 167.98 | 160.67
2019-02-03 14:30 | 169.23 | 162.01
2019-02-03 15:00 | 172.96 | 165.53
2019-02-03 15:30 | 174.11 | 166.76
2019-02-03 16:00 | 176.49 | 169.29
2019-02-03 16:30 | 178.25 | 171.5
2019-02-03 17:00 | 179.9 | 173.15
2019-02-03 17:30 | 181.07 | 174.57
2019-02-03 18:00 | 182.7 | 176.12
2019-02-03 18:30 | 183.77 | 177.08
2019-02-03 19:00 | 184.1 | 177.56
2019-02-03 19:30 | 184.42 | 178
2019-02-03 20:00 | 184.18 | 177.72
2019-02-03 20:30 | 182.4 | 175.63
2019-02-03 21:00 | 179.82 | 172.83
2019-02-03 21:30 | 177.14 | 170.73
2019-02-03 22:00 | 174.53 | 167.88
2019-02-03 22:30 | 172.14 | 164.96
2019-02-03 23:00 | 149.62 | 142.4
2019-02-03 23:30 | 145.41 | 138.32
2019-02-04 | 143.67 | 136.31
2019-02-04 00:30 | 143.1 | 135.38
2019-02-04 01:00 | 141.86 | 134.37
2019-02-04 01:30 | 140.84 | 133.22
2019-02-04 02:00 | 140.41 | 132.82
2019-02-04 02:30 | 139.33 | 131.7
2019-02-04 03:00 | 139.1 | 131.46
2019-02-04 03:30 | 138.09 | 130.51
2019-02-04 04:00 | 137.93 | 130.37
2019-02-04 04:30 | 138.61 | 131.23
2019-02-04 05:00 | 138.16 | 130.8
2019-02-04 05:30 | 139.19 | 132.15
2019-02-04 06:00 | 155.39 | 148.47
2019-02-04 06:30 | 168.06 | 160.44
2019-02-04 07:00 | 168.23 | 161.42
2019-02-04 07:30 | 169.08 | 162.62
2019-02-04 08:00 | 167.05 | 160.96
2019-02-04 08:30 | 162.39 | 156.58
2019-02-04 09:00 | 159.7 | 154.03
2019-02-04 09:30 | 163.38 | 157.22
2019-02-04 10:00 | 167.74 | 161.31
2019-02-04 10:30 | 168.32 | 161.62
2019-02-04 11:00 | 168.26 | 161.75
2019-02-04 11:30 | 168.21 | 161.81
2019-02-04 12:00 | 169.43 | 163.15
2019-02-04 12:30 | 171.32 | 164.85
2019-02-04 13:00 | 173.29 | 166.55
2019-02-04 13:30 | 174.72 | 168.15
2019-02-04 14:00 | 177.14 | 170.71
2019-02-04 14:30 | 178.24 | 171.78
2019-02-04 15:00 | 178.65 | 172.15
2019-02-04 15:30 | 179.69 | 173.33
2019-02-04 16:00 | 181.14 | 175.45
2019-02-04 16:30 | 182.35 | 176.81
2019-02-04 17:00 | 183.34 | 177.78
2019-02-04 17:30 | 184.31 | 178.57
2019-02-04 18:00 | 186.36 | 180.66
2019-02-04 18:30 | 187.7 | 181.98
2019-02-04 19:00 | 189.07 | 183.25
2019-02-04 19:30 | 189.2 | 183.36
2019-02-04 20:00 | 187.86 | 182.07
2019-02-04 20:30 | 185.48 | 179.14
2019-02-04 21:00 | 183.12 | 176.13
2019-02-04 21:30 | 179.09 | 173.1
2019-02-04 22:00 | 175.38 | 169.47
2019-02-04 22:30 | 172.95 | 166.59
2019-02-04 23:00 | 170.65 | 164.38
2019-02-04 23:30 | 148.96 | 142.91
2019-02-05 | 143.97 | 138.08
2019-02-05 00:30 | 142.59 | 136.67
2019-02-05 01:00 | 140.73 | 134.78
2019-02-05 01:30 | 140.2 | 134.18
2019-02-05 02:00 | 139.43 | 133.6
2019-02-05 02:30 | 138.55 | 132.67
2019-02-05 03:00 | 137.92 | 132.01
2019-02-05 03:30 | 137.72 | 131.86
2019-02-05 04:00 | 136.27 | 130.44
2019-02-05 04:30 | 137.49 | 131.99
2019-02-05 05:00 | 137.84 | 132.38
2019-02-05 05:30 | 138.47 | 133.21
2019-02-05 06:00 | 154 | 148.22
2019-02-05 06:30 | 164.62 | 158.59
2019-02-05 07:00 | 165.67 | 159.53
2019-02-05 07:30 | 166.79 | 160.78
2019-02-05 08:00 | 167.69 | 161.71
2019-02-05 08:30 | 167.23 | 161.35
2019-02-05 09:00 | 166.84 | 161.03
2019-02-05 09:30 | 168.66 | 163.38
2019-02-05 10:00 | 168.78 | 163.54
2019-02-05 10:30 | 169.32 | 163.72
2019-02-05 11:00 | 168.73 | 162.83
2019-02-05 11:30 | 170.68 | 164.84
2019-02-05 12:00 | 172.77 | 167
2019-02-05 12:30 | 173.26 | 167.55
2019-02-05 13:00 | 175.44 | 169.86
2019-02-05 13:30 | 178.12 | 172.69
2019-02-05 14:00 | 180.02 | 175.15
2019-02-05 14:30 | 181.67 | 176.88
2019-02-05 15:00 | 180.73 | 175.58
2019-02-05 15:30 | 180.69 | 175.37
2019-02-05 16:00 | 181.59 | 176.49
2019-02-05 16:30 | 182.69 | 177.58
2019-02-05 17:00 | 185.18 | 180.08
2019-02-05 17:30 | 186.06 | 180.89
2019-02-05 18:00 | 188.07 | 182.85
2019-02-05 18:30 | 189.28 | 184.06
2019-02-05 19:00 | 189.69 | 184.49
2019-02-05 19:30 | 189.67 | 184.61
2019-02-05 20:00 | 189.09 | 183.83
2019-02-05 20:30 | 187.06 | 181.54
2019-02-05 21:00 | 184.01 | 178.3
2019-02-05 21:30 | 181.03 | 175.7
2019-02-05 22:00 | 177.45 | 172.24
2019-02-05 22:30 | 174.14 | 168.75
2019-02-05 23:00 | 172.23 | 166.64
2019-02-05 23:30 | 171.24 | 165.38
2019-02-06 | 169.21 | 163.88
2019-02-06 00:30 | 167.64 | 162.6
2019-02-06 01:00 | 166.25 | 161.34
2019-02-06 01:30 | 165.51 | 160.47
2019-02-06 02:00 | 164.48 | 159.25
2019-02-06 02:30 | 164.04 | 158.74
2019-02-06 03:00 | 163.5 | 158.27
2019-02-06 03:30 | 163.37 | 158.01
2019-02-06 04:00 | 163.43 | 157.95
2019-02-06 04:30 | 163.04 | 157.58
2019-02-06 05:00 | 163.08 | 157.72
2019-02-06 05:30 | 163.78 | 158.75
2019-02-06 06:00 | 164.91 | 159.86
2019-02-06 06:30 | 166.79 | 161.86
2019-02-06 07:00 | 168.34 | 163.32
2019-02-06 07:30 | 170.09 | 164.85
2019-02-06 08:00 | 170.87 | 165.54
2019-02-06 08:30 | 169.5 | 164.19
2019-02-06 09:00 | 169.86 | 164.51
2019-02-06 09:30 | 167.08 | 161.63
2019-02-06 10:00 | 163.4 | 157.93
2019-02-06 10:30 | 161.95 | 156.62
2019-02-06 11:00 | 162.86 | 157.75
2019-02-06 11:30 | 159.31 | 154.62
2019-02-06 12:00 | 159.11 | 154.51
2019-02-06 12:30 | 160.05 | 155.53
2019-02-06 13:00 | 160.87 | 156.42
2019-02-06 13:30 | 162.9 | 157.99
2019-02-06 14:00 | 164.21 | 159.34
2019-02-06 14:30 | 164.3 | 159.53
2019-02-06 15:00 | 164.6 | 159.69
2019-02-06 15:30 | 165.33 | 160.41
2019-02-06 16:00 | 165.87 | 161.31
2019-02-06 16:30 | 166.26 | 161.7
2019-02-06 17:00 | 166.7 | 161.94
2019-02-06 17:30 | 168.02 | 162.88
2019-02-06 18:00 | 168.01 | 162.81
2019-02-06 18:30 | 169.33 | 164.14
2019-02-06 19:00 | 176.13 | 170.79
2019-02-06 19:30 | 181.71 | 176.4
2019-02-06 20:00 | 181.76 | 176.42
2019-02-06 20:30 | 179.86 | 174.28
2019-02-06 21:00 | 176.73 | 170.72
2019-02-06 21:30 | 173.82 | 168.24
2019-02-06 22:00 | 171.23 | 165.55
2019-02-06 22:30 | 169.39 | 163.49
2019-02-06 23:00 | 168.85 | 162.9
2019-02-06 23:30 | 168.18 | 162.24
2019-02-07 | 166.19 | 160.84
2019-02-07 00:30 | 164.88 | 159.55
2019-02-07 01:00 | 163.67 | 158.25
2019-02-07 01:30 | 162.67 | 157.02
2019-02-07 02:00 | 162.04 | 156.41
2019-02-07 02:30 | 161.16 | 155.56
2019-02-07 03:00 | 160.33 | 154.74
2019-02-07 03:30 | 160.21 | 154.68
2019-02-07 04:00 | 159.92 | 154.28
2019-02-07 04:30 | 160.16 | 154.74
2019-02-07 05:00 | 160.89 | 155.51
2019-02-07 05:30 | 161.76 | 156.32
2019-02-07 06:00 | 162.72 | 157.53
2019-02-07 06:30 | 165.11 | 159.72
2019-02-07 07:00 | 165.86 | 160.48
2019-02-07 07:30 | 167.31 | 161.58
2019-02-07 08:00 | 167.34 | 161.74
2019-02-07 08:30 | 167.92 | 161.96
2019-02-07 09:00 | 168.98 | 163.32
2019-02-07 09:30 | 168.29 | 162.35
2019-02-07 10:00 | 169.18 | 163.22
2019-02-07 10:30 | 164.41 | 158.65
2019-02-07 11:00 | 165.05 | 159.35
2019-02-07 11:30 | 166.67 | 161.08
2019-02-07 12:00 | 167.8 | 162.05
2019-02-07 12:30 | 167.59 | 161.87
2019-02-07 13:00 | 169.67 | 163.97
2019-02-07 13:30 | 173.08 | 167.38
2019-02-07 14:00 | 174.11 | 168.22
2019-02-07 14:30 | 174.31 | 168.37
2019-02-07 15:00 | 174.84 | 168.87
2019-02-07 15:30 | 173.93 | 168.16
2019-02-07 16:00 | 176.55 | 171.03
2019-02-07 16:30 | 176.65 | 170.94
2019-02-07 17:00 | 176.05 | 170.33
2019-02-07 17:30 | 177.07 | 171.21
2019-02-07 18:00 | 179.18 | 173.44
2019-02-07 18:30 | 180.37 | 174.5
2019-02-07 19:00 | 180.91 | 175.15
2019-02-07 19:30 | 182.25 | 176.54
2019-02-07 20:00 | 182.2 | 176.51
2019-02-07 20:30 | 180.35 | 174.28
2019-02-07 21:00 | 178.3 | 171.86
2019-02-07 21:30 | 176.01 | 169.67
2019-02-07 22:00 | 173.65 | 167.24
2019-02-07 22:30 | 170.95 | 164.29
2019-02-07 23:00 | 169.08 | 162.63
2019-02-07 23:30 | 167.16 | 161.15
2019-02-08 | 144.28 | 138.39
2019-02-08 00:30 | 140.95 | 135.09
2019-02-08 01:00 | 139.04 | 133.28
2019-02-08 01:30 | 137.56 | 131.9
2019-02-08 02:00 | 136.57 | 131.4
2019-02-08 02:30 | 135.56 | 130.63
2019-02-08 03:00 | 135.66 | 130.61
2019-02-08 03:30 | 135.08 | 130.11
2019-02-08 04:00 | 134.49 | 129.41
2019-02-08 04:30 | 134.76 | 129.72
2019-02-08 05:00 | 134.94 | 129.97
2019-02-08 05:30 | 135.86 | 130.98
2019-02-08 06:00 | 137.48 | 132.46
2019-02-08 06:30 | 139.42 | 134.53
2019-02-08 07:00 | 156.18 | 150.79
2019-02-08 07:30 | 166.22 | 161.09
2019-02-08 08:00 | 166.26 | 161.33
2019-02-08 08:30 | 168.88 | 163.71
2019-02-08 09:00 | 170.91 | 165.53
2019-02-08 09:30 | 170.38 | 165.08
2019-02-08 10:00 | 171.46 | 166.33
2019-02-08 10:30 | 173.74 | 169.41
2019-02-08 11:00 | 174.8 | 170.66
2019-02-08 11:30 | 176.02 | 171.79
2019-02-08 12:00 | 177.16 | 173.11
2019-02-08 12:30 | 178.5 | 174.32
2019-02-08 13:00 | 178.18 | 173.73
2019-02-08 13:30 | 178.6 | 173.02
2019-02-08 14:00 | 179.73 | 174.29
2019-02-08 14:30 | 180.16 | 174.54
2019-02-08 15:00 | 180.71 | 175.06
2019-02-08 15:30 | 181.92 | 176.26
2019-02-08 16:00 | 184.81 | 179.35
2019-02-08 16:30 | 186.32 | 180.92
2019-02-08 17:00 | 188.78 | 183.28
2019-02-08 17:30 | 188.57 | 182.87
2019-02-08 18:00 | 189.98 | 184.33
2019-02-08 18:30 | 190.29 | 184.61
2019-02-08 19:00 | 190.25 | 184.65
2019-02-08 19:30 | 189.88 | 184.35
2019-02-08 20:00 | 189.01 | 183.35
2019-02-08 20:30 | 187.28 | 181.31
2019-02-08 21:00 | 185.47 | 179.06
2019-02-08 21:30 | 182.22 | 176.38
2019-02-08 22:00 | 180.09 | 174.09
2019-02-08 22:30 | 178.02 | 171.87
2019-02-08 23:00 | 175.8 | 169.51
2019-02-08 23:30 | 174.46 | 168.01
2019-02-09 | 172.88 | 166.33
2019-02-09 00:30 | 171.94 | 165.7
2019-02-09 01:00 | 170.19 | 164.16
2019-02-09 01:30 | 169.53 | 163.59
2019-02-09 02:00 | 168.69 | 162.69
2019-02-09 02:30 | 168.37 | 162.29
2019-02-09 03:00 | 168 | 161.91
2019-02-09 03:30 | 167.33 | 161.29
2019-02-09 04:00 | 167.46 | 161.45
2019-02-09 04:30 | 167.15 | 161.09
2019-02-09 05:00 | 167.27 | 161.24
2019-02-09 05:30 | 167.42 | 161.49
2019-02-09 06:00 | 167.16 | 161.27
2019-02-09 06:30 | 167.82 | 162
2019-02-09 07:00 | 168.54 | 162.86
2019-02-09 07:30 | 169.61 | 163.43
2019-02-09 08:00 | 170.18 | 163.93
2019-02-09 08:30 | 170.02 | 163.44
2019-02-09 09:00 | 170.52 | 163.75
2019-02-09 09:30 | 170.66 | 163.56
2019-02-09 10:00 | 171.52 | 164.34
2019-02-09 10:30 | 172.37 | 165.32
2019-02-09 11:00 | 173.46 | 166.62
2019-02-09 11:30 | 175.24 | 168.59
2019-02-09 12:00 | 177.27 | 170.74
2019-02-09 12:30 | 179.39 | 172.75
2019-02-09 13:00 | 181.19 | 174.64
2019-02-09 13:30 | 182.58 | 176.07
2019-02-09 14:00 | 184.52 | 178.04
2019-02-09 14:30 | 186.4 | 180.02
2019-02-09 15:00 | 188.08 | 181.97
2019-02-09 15:30 | 188.16 | 182.04
2019-02-09 16:00 | 188.37 | 182.29
2019-02-09 16:30 | 188.74 | 182.51
2019-02-09 17:00 | 188.99 | 182.92
2019-02-09 17:30 | 191.39 | 185.65
2019-02-09 18:00 | 193.82 | 188.16
2019-02-09 18:30 | 194.3 | 188.7
2019-02-09 19:00 | 194.49 | 188.72
2019-02-09 19:30 | 194.49 | 188.64
2019-02-09 20:00 | 193.51 | 187.49
2019-02-09 20:30 | 190.98 | 184.51
2019-02-09 21:00 | 187.92 | 181
2019-02-09 21:30 | 185.51 | 178.54
2019-02-09 22:00 | 182.66 | 175.63
2019-02-09 22:30 | 179.81 | 173.08
2019-02-09 23:00 | 178.06 | 171.15
2019-02-09 23:30 | 176.72 | 169.82
2019-02-10 | 174.88 | 168.03
2019-02-10 00:30 | 173.04 | 166.83
2019-02-10 01:00 | 171.7 | 165.68
2019-02-10 01:30 | 170.9 | 164.6
2019-02-10 02:00 | 170 | 163.99
2019-02-10 02:30 | 168.97 | 163.19
2019-02-10 03:00 | 168.31 | 162.43
2019-02-10 03:30 | 166.96 | 161.12
2019-02-10 04:00 | 166.55 | 160.68
2019-02-10 04:30 | 166.43 | 160.53
2019-02-10 05:00 | 166.41 | 160.53
2019-02-10 05:30 | 166.97 | 161.08
2019-02-10 06:00 | 167.02 | 160.76
2019-02-10 06:30 | 167.69 | 161.15
2019-02-10 07:00 | 167.23 | 160.82
2019-02-10 07:30 | 166.62 | 160.42
2019-02-10 08:00 | 166.33 | 160.21
2019-02-10 08:30 | 165.83 | 159.74
2019-02-10 09:00 | 165.41 | 159.41
2019-02-10 09:30 | 165.41 | 159.49
2019-02-10 10:00 | 166.39 | 160.42
2019-02-10 10:30 | 166.95 | 160.75
2019-02-10 11:00 | 168.13 | 162.05
2019-02-10 11:30 | 169.16 | 163.21
2019-02-10 12:00 | 169.49 | 163.46
2019-02-10 12:30 | 170.52 | 164.41
2019-02-10 13:00 | 171.8 | 165.75
2019-02-10 13:30 | 173.74 | 167.97
2019-02-10 14:00 | 175.77 | 170.1
2019-02-10 14:30 | 175.64 | 169.91
2019-02-10 15:00 | 176.77 | 171.08
2019-02-10 15:30 | 178.61 | 172.85
2019-02-10 16:00 | 181.09 | 175.47
2019-02-10 16:30 | 185.36 | 179.42
2019-02-10 17:00 | 188.07 | 182.44
2019-02-10 17:30 | 189.72 | 184.13
2019-02-10 18:00 | 190.98 | 185.76
2019-02-10 18:30 | 191.55 | 186.29
2019-02-10 19:00 | 191.94 | 186.6
2019-02-10 19:30 | 192.07 | 186.62
2019-02-10 20:00 | 191.14 | 185.57
2019-02-10 20:30 | 188.48 | 182.57
2019-02-10 21:00 | 185.47 | 179.39
2019-02-10 21:30 | 182.89 | 176.75
2019-02-10 22:00 | 180.53 | 174.11
2019-02-10 22:30 | 177.88 | 171.29
2019-02-10 23:00 | 175.71 | 169.22
2019-02-10 23:30 | 174.56 | 167.92
2019-02-11 | 172.89 | 166.26
2019-02-11 00:30 | 172.2 | 165.4
2019-02-11 01:00 | 171.19 | 164.11
2019-02-11 01:30 | 170.76 | 163.63
2019-02-11 02:00 | 169.22 | 162.03
2019-02-11 02:30 | 166.65 | 159.46
2019-02-11 03:00 | 165.32 | 158.36
2019-02-11 03:30 | 164.77 | 158.08
2019-02-11 04:00 | 164.62 | 157.85
2019-02-11 04:30 | 164.62 | 157.9
2019-02-11 05:00 | 164.99 | 158.28
2019-02-11 05:30 | 165.86 | 159.28
2019-02-11 06:00 | 166.46 | 160.22
2019-02-11 06:30 | 168.81 | 162.41
2019-02-11 07:00 | 170.95 | 164.12
2019-02-11 07:30 | 172.49 | 165.6
2019-02-11 08:00 | 173.51 | 166.81
2019-02-11 08:30 | 173.13 | 166.79
2019-02-11 09:00 | 173.06 | 166.91
2019-02-11 09:30 | 173.64 | 167.43
2019-02-11 10:00 | 174.51 | 168.51
2019-02-11 10:30 | 174.64 | 168.6
2019-02-11 11:00 | 176.16 | 170.29
2019-02-11 11:30 | 177.14 | 171.35
2019-02-11 12:00 | 178.12 | 172.38
2019-02-11 12:30 | 179.91 | 174.36
2019-02-11 13:00 | 181.31 | 176.05
2019-02-11 13:30 | 183.6 | 177.88
2019-02-11 14:00 | 185.2 | 179.7
2019-02-11 14:30 | 186.25 | 180.89
2019-02-11 15:00 | 184.78 | 179.65
2019-02-11 15:30 | 179.33 | 174.64
2019-02-11 16:00 | 187.93 | 183.18
2019-02-11 16:30 | 191.39 | 186.57
2019-02-11 17:00 | 193.25 | 188.5
2019-02-11 17:30 | 194.34 | 189.44
2019-02-11 18:00 | 196.26 | 191.35
2019-02-11 18:30 | 197.27 | 192.31
2019-02-11 19:00 | 197.81 | 192.83
2019-02-11 19:30 | 197.28 | 192.18
2019-02-11 20:00 | 195.45 | 190.13
2019-02-11 20:30 | 192.32 | 186.7
2019-02-11 21:00 | 188.35 | 182.33
2019-02-11 21:30 | 185.17 | 179.1
2019-02-11 22:00 | 181.81 | 175.48
2019-02-11 22:30 | 178.62 | 172.09
2019-02-11 23:00 | 176.3 | 169.61
2019-02-11 23:30 | 174.78 | 167.95
2019-02-12 | 172 | 165.31
2019-02-12 00:30 | 170.05 | 163.71
2019-02-12 01:00 | 147.97 | 141.81
2019-02-12 01:30 | 142.74 | 136.67
2019-02-12 02:00 | 142.82 | 136.82
2019-02-12 02:30 | 142.11 | 136.04
2019-02-12 03:00 | 141.45 | 135.3
2019-02-12 03:30 | 141.16 | 135
2019-02-12 04:00 | 141.14 | 134.82
2019-02-12 04:30 | 141.51 | 135.27
2019-02-12 05:00 | 141.47 | 135.31
2019-02-12 05:30 | 143.31 | 137.32
2019-02-12 06:00 | 145.1 | 138.9
2019-02-12 06:30 | 147.15 | 140.49
2019-02-12 07:00 | 165.98 | 159.2
2019-02-12 07:30 | 175.91 | 169.22
2019-02-12 08:00 | 176.23 | 169.53
2019-02-12 08:30 | 176.81 | 170.35
2019-02-12 09:00 | 177.09 | 170.8
2019-02-12 09:30 | 178.33 | 172.26
2019-02-12 10:00 | 180.83 | 175.02
2019-02-12 10:30 | 182.46 | 176.19
2019-02-12 11:00 | 183.11 | 176.73
2019-02-12 11:30 | 183.66 | 176.98
2019-02-12 12:00 | 185.79 | 178.63
2019-02-12 12:30 | 186.46 | 179.85
2019-02-12 13:00 | 187.84 | 181.17
2019-02-12 13:30 | 189.9 | 183.15
2019-02-12 14:00 | 191.78 | 184.81
2019-02-12 14:30 | 193 | 186.08
2019-02-12 15:00 | 192.52 | 185.81
2019-02-12 15:30 | 193.8 | 187.31
2019-02-12 16:00 | 195.47 | 189.51
2019-02-12 16:30 | 196.87 | 190.7
2019-02-12 17:00 | 199.24 | 193.28
2019-02-12 17:30 | 200.77 | 194.86
2019-02-12 18:00 | 202.23 | 196.51
2019-02-12 18:30 | 203.86 | 198.15
2019-02-12 19:00 | 203.12 | 197.24
2019-02-12 19:30 | 202.43 | 196.45
2019-02-12 20:00 | 201.6 | 195.42
2019-02-12 20:30 | 197.25 | 190.61
2019-02-12 21:00 | 191.75 | 184.96
2019-02-12 21:30 | 185.46 | 179.31
2019-02-12 22:00 | 180.97 | 174.74
2019-02-12 22:30 | 177.14 | 170.98
2019-02-12 23:00 | 175.46 | 169.34
2019-02-12 23:30 | 173.52 | 167.12
2019-02-13 | 171.31 | 165.1
2019-02-13 00:30 | 169.37 | 163.14
2019-02-13 01:00 | 167.66 | 161.6
2019-02-13 01:30 | 166.66 | 160.58
2019-02-13 02:00 | 166.11 | 160.06
2019-02-13 02:30 | 165.93 | 159.8
2019-02-13 03:00 | 165.48 | 159.26
2019-02-13 03:30 | 165.81 | 159.18
2019-02-13 04:00 | 165.37 | 158.73
2019-02-13 04:30 | 165.2 | 158.7
2019-02-13 05:00 | 165.43 | 159.03
2019-02-13 05:30 | 166.25 | 160.04
2019-02-13 06:00 | 167.74 | 161.72
2019-02-13 06:30 | 168.95 | 163.42
2019-02-13 07:00 | 170.25 | 164.42
2019-02-13 07:30 | 174.69 | 166.61
2019-02-13 08:00 | 177.94 | 167.24
2019-02-13 08:30 | 176.78 | 167.55
2019-02-13 09:00 | 176.51 | 167.64
2019-02-13 09:30 | 177.52 | 167.81
2019-02-13 10:00 | 173.95 | 168.92
2019-02-13 10:30 | 174.93 | 170.14
2019-02-13 11:00 | 175.98 | 171.64
2019-02-13 11:30 | 178.08 | 173.28
2019-02-13 12:00 | 176.29 | 173.32
2019-02-13 12:30 | 177.2 | 174.85
2019-02-13 13:00 | 179.34 | 176.98
2019-02-13 13:30 | 179.85 | 177.53
2019-02-13 14:00 | 180.87 | 178.84
2019-02-13 14:30 | 182 | 180.02
2019-02-13 15:00 | 181.91 | 180.04
2019-02-13 15:30 | 189.33 | 187.4
2019-02-13 16:00 | 169.91 | 168.39
2019-02-13 16:30 | 167.68 | 166.27
2019-02-13 17:00 | 170.6 | 169.11
2019-02-13 17:30 | 173.2 | 171.69
2019-02-13 18:00 | 173.55 | 172.04
2019-02-13 18:30 | 175.02 | 173.47
2019-02-13 19:00 | 174.49 | 173
2019-02-13 19:30 | 174.15 | 172.76
2019-02-13 20:00 | 176.89 | 175.45
2019-02-13 20:30 | 181.77 | 180.12
2019-02-13 21:00 | 180.74 | 179.32
2019-02-13 21:30 | 181.69 | 180.09
2019-02-13 22:00 | 185.07 | 183.29
2019-02-13 22:30 | 187.93 | 186.11
2019-02-13 23:00 | 179.56 | 177.19
2019-02-13 23:30 | 178.05 | 175.31
2019-02-14 | 175.15 | 172.27
2019-02-14 00:30 | 174.47 | 171.45
2019-02-14 01:00 | 174.18 | 171.13
2019-02-14 01:30 | 173.02 | 169.92
2019-02-14 02:00 | 173.55 | 170.32
2019-02-14 02:30 | 172.79 | 169.53
2019-02-14 03:00 | 172.77 | 169.48
2019-02-14 03:30 | 172.11 | 168.81
2019-02-14 04:00 | 172.37 | 169.02
2019-02-14 04:30 | 172.47 | 169.12
2019-02-14 05:00 | 172.72 | 169.36
2019-02-14 05:30 | 172.51 | 168.9
2019-02-14 06:00 | 173.36 | 169.74
2019-02-14 06:30 | 174.9 | 171.41
2019-02-14 07:00 | 178.86 | 175.27
2019-02-14 07:30 | 180.76 | 177.2
2019-02-14 08:00 | 180.48 | 177.04
2019-02-14 08:30 | 179.46 | 176.02
2019-02-14 09:00 | 177.07 | 173.71
2019-02-14 09:30 | 175.41 | 172.07
2019-02-14 10:00 | 174.83 | 171.57
2019-02-14 10:30 | 174.2 | 170.92
2019-02-14 11:00 | 174.01 | 170.7
2019-02-14 11:30 | 174.42 | 171.02
2019-02-14 12:00 | 175.43 | 172.09
2019-02-14 12:30 | 176.91 | 173.51
2019-02-14 13:00 | 178.69 | 175.33
2019-02-14 13:30 | 181.28 | 177.81
2019-02-14 14:00 | 183.31 | 180.16
2019-02-14 14:30 | 184.82 | 181.81
2019-02-14 15:00 | 185.75 | 182.74
2019-02-14 15:30 | 186.83 | 183.86
2019-02-14 16:00 | 188.4 | 185.49
2019-02-14 16:30 | 189.63 | 186.56
2019-02-14 17:00 | 191.48 | 188.38
2019-02-14 17:30 | 193.33 | 190.17
2019-02-14 18:00 | 195.63 | 192.47
2019-02-14 18:30 | 196.3 | 193.17
2019-02-14 19:00 | 196.24 | 193.03
2019-02-14 19:30 | 195.62 | 192.36
2019-02-14 20:00 | 194.02 | 190.69
2019-02-14 20:30 | 187.64 | 184.19
2019-02-14 21:00 | 184.34 | 180.64
2019-02-14 21:30 | 182.49 | 178.85
2019-02-14 22:00 | 179.76 | 176.09
2019-02-14 22:30 | 177.84 | 174.19
2019-02-14 23:00 | 176 | 172.41
2019-02-14 23:30 | 174.93 | 171.46
2019-02-15 | 173.87 | 170.29
2019-02-15 00:30 | 173.48 | 169.8
2019-02-15 01:00 | 172.59 | 168.98
2019-02-15 01:30 | 172.07 | 168.47
2019-02-15 02:00 | 171.38 | 167.82
2019-02-15 02:30 | 171.33 | 167.8
2019-02-15 03:00 | 171.17 | 167.68
2019-02-15 03:30 | 171.21 | 167.75
2019-02-15 04:00 | 170.65 | 167.25
2019-02-15 04:30 | 171.64 | 168.28
2019-02-15 05:00 | 172.38 | 169.04
2019-02-15 05:30 | 173.76 | 170.45
2019-02-15 06:00 | 174.5 | 171.24
2019-02-15 06:30 | 176.95 | 173.73
2019-02-15 07:00 | 178.23 | 174.87
2019-02-15 07:30 | 179.71 | 176.38
2019-02-15 08:00 | 180.42 | 177.13
2019-02-15 08:30 | 179.95 | 176.71
2019-02-15 09:00 | 180.5 | 177.38
2019-02-15 09:30 | 181.1 | 177.93
2019-02-15 10:00 | 181.52 | 178.58
2019-02-15 10:30 | 181.56 | 178.51
2019-02-15 11:00 | 182.89 | 179.9
2019-02-15 11:30 | 186.4 | 183.28
2019-02-15 12:00 | 187.91 | 184.78
2019-02-15 12:30 | 191.01 | 187.79
2019-02-15 13:00 | 193.14 | 190.08
2019-02-15 13:30 | 194.61 | 191.56
2019-02-15 14:00 | 196.89 | 193.86
2019-02-15 14:30 | 197.37 | 194.37
2019-02-15 15:00 | 198.6 | 195.64
2019-02-15 15:30 | 200.07 | 197.22
2019-02-15 16:00 | 199.5 | 197.01
2019-02-15 16:30 | 201.58 | 199
2019-02-15 17:00 | 202.48 | 199.88
2019-02-15 17:30 | 202.94 | 200.34
2019-02-15 18:00 | 203.47 | 200.91
2019-02-15 18:30 | 203.56 | 200.97
2019-02-15 19:00 | 203.56 | 200.94
2019-02-15 19:30 | 202.71 | 200.07
2019-02-15 20:00 | 202.06 | 199.39
2019-02-15 20:30 | 199.77 | 196.88
2019-02-15 21:00 | 196.59 | 193.49
2019-02-15 21:30 | 194.67 | 191.5
2019-02-15 22:00 | 192.17 | 188.96
2019-02-15 22:30 | 189.19 | 186.08
2019-02-15 23:00 | 186.89 | 183.7
2019-02-15 23:30 | 184.58 | 181.45
2019-02-16 | 183.21 | 180.02
2019-02-16 00:30 | 182.21 | 178.92
2019-02-16 01:00 | 181.39 | 178
2019-02-16 01:30 | 181.23 | 177.61
2019-02-16 02:00 | 180.38 | 176.76
2019-02-16 02:30 | 179.9 | 176.22
2019-02-16 03:00 | 179.66 | 175.87
2019-02-16 03:30 | 179.65 | 175.8
2019-02-16 04:00 | 179.63 | 175.81
2019-02-16 04:30 | 179.78 | 175.95
2019-02-16 05:00 | 179.68 | 175.87
2019-02-16 05:30 | 180.06 | 176.26
2019-02-16 06:00 | 180.01 | 176.28
2019-02-16 06:30 | 181 | 177.3
2019-02-16 07:00 | 181.77 | 177.92
2019-02-16 07:30 | 182.48 | 178.4
2019-02-16 08:00 | 182.37 | 178.16
2019-02-16 08:30 | 182.25 | 178.05
2019-02-16 09:00 | 182.23 | 178.09
2019-02-16 09:30 | 182.84 | 178.84
2019-02-16 10:00 | 182.86 | 179.04
2019-02-16 10:30 | 182.58 | 179.07
2019-02-16 11:00 | 183.07 | 179.74
2019-02-16 11:30 | 184.18 | 181.01
2019-02-16 12:00 | 185.88 | 182.81
2019-02-16 12:30 | 187.23 | 184.15
2019-02-16 13:00 | 188.87 | 185.73
2019-02-16 13:30 | 189.88 | 186.71
2019-02-16 14:00 | 190.31 | 187.26
2019-02-16 14:30 | 191.22 | 188.25
2019-02-16 15:00 | 192.43 | 189.48
2019-02-16 15:30 | 193.81 | 190.98
2019-02-16 16:00 | 194.68 | 191.84
2019-02-16 16:30 | 195.52 | 192.69
2019-02-16 17:00 | 196.46 | 193.67
2019-02-16 17:30 | 198.07 | 195.32
2019-02-16 18:00 | 199.01 | 196.21
2019-02-16 18:30 | 199.45 | 196.66
2019-02-16 19:00 | 199.63 | 196.79
2019-02-16 19:30 | 199.27 | 196.45
2019-02-16 20:00 | 197.79 | 194.86
2019-02-16 20:30 | 195.07 | 191.99
2019-02-16 21:00 | 192.37 | 189.11
2019-02-16 21:30 | 190.29 | 186.94
2019-02-16 22:00 | 188.13 | 184.59
2019-02-16 22:30 | 185.6 | 182.31
2019-02-16 23:00 | 183.91 | 180.58
2019-02-16 23:30 | 182.71 | 179.32
2019-02-17 | 181.07 | 177.73
2019-02-17 00:30 | 180.26 | 176.94
2019-02-17 01:00 | 179.64 | 176.25
2019-02-17 01:30 | 178.74 | 175.32
2019-02-17 02:00 | 178.22 | 174.5
2019-02-17 02:30 | 177.81 | 174.12
2019-02-17 03:00 | 177.24 | 173.53
2019-02-17 03:30 | 176.63 | 173.06
2019-02-17 04:00 | 176.6 | 173.09
2019-02-17 04:30 | 176.21 | 172.69
2019-02-17 05:00 | 175.93 | 172.4
2019-02-17 05:30 | 176.16 | 172.62
2019-02-17 06:00 | 176.15 | 172.74
2019-02-17 06:30 | 176.72 | 173.4
2019-02-17 07:00 | 176.24 | 172.91
2019-02-17 07:30 | 175.99 | 172.62
2019-02-17 08:00 | 176.39 | 172.97
2019-02-17 08:30 | 176.61 | 173.18
2019-02-17 09:00 | 175.93 | 172.63
2019-02-17 09:30 | 176.26 | 172.98
2019-02-17 10:00 | 177.02 | 173.69
2019-02-17 10:30 | 178.57 | 175.12
2019-02-17 11:00 | 179.29 | 175.81
2019-02-17 11:30 | 180.87 | 177.42
2019-02-17 12:00 | 182.83 | 179.32
2019-02-17 12:30 | 184.63 | 180.96
2019-02-17 13:00 | 176.72 | 172.97
2019-02-17 13:30 | 180.97 | 176.85
2019-02-17 14:00 | 182.45 | 178.41
2019-02-17 14:30 | 182.72 | 178.67
2019-02-17 15:00 | 184.23 | 180.38
2019-02-17 15:30 | 185.4 | 181.65
2019-02-17 16:00 | 187.49 | 183.82
2019-02-17 16:30 | 189.5 | 185.9
2019-02-17 17:00 | 192.1 | 188.46
2019-02-17 17:30 | 194.24 | 190.73
2019-02-17 18:00 | 194.79 | 191.41
2019-02-17 18:30 | 195.08 | 191.7
2019-02-17 19:00 | 194 | 190.87
2019-02-17 19:30 | 193.53 | 190.39
2019-02-17 20:00 | 191.62 | 188.33
2019-02-17 20:30 | 188.25 | 184.75
2019-02-17 21:00 | 184.87 | 181.13
2019-02-17 21:30 | 181.74 | 177.94
2019-02-17 22:00 | 178.21 | 174.3
2019-02-17 22:30 | 175.6 | 171.38
2019-02-17 23:00 | 173.29 | 168.93
2019-02-17 23:30 | 171.82 | 167.44
2019-02-18 | 170.2 | 165.88
2019-02-18 00:30 | 168.76 | 164.52
2019-02-18 01:00 | 167.61 | 163.5
2019-02-18 01:30 | 166.32 | 162.21
2019-02-18 02:00 | 166.06 | 161.94
2019-02-18 02:30 | 165.63 | 161.51
2019-02-18 03:00 | 165.15 | 161.02
2019-02-18 03:30 | 164.84 | 160.73
2019-02-18 04:00 | 164.65 | 160.53
2019-02-18 04:30 | 164.46 | 160.37
2019-02-18 05:00 | 164.87 | 160.82
2019-02-18 05:30 | 165.86 | 161.92
2019-02-18 06:00 | 166.6 | 162.77
2019-02-18 06:30 | 168.43 | 164.75
2019-02-18 07:00 | 169.58 | 165.71
2019-02-18 07:30 | 172.36 | 168.48
2019-02-18 08:00 | 173.04 | 169.21
2019-02-18 08:30 | 175 | 171.1
2019-02-18 09:00 | 175.58 | 171.58
2019-02-18 09:30 | 167.85 | 163.51
2019-02-18 10:00 | 166.32 | 161.95
2019-02-18 10:30 | 167.07 | 162.67
2019-02-18 11:00 | 168.54 | 164.41
2019-02-18 11:30 | 170.19 | 166.22
2019-02-18 12:00 | 172.26 | 168.32
2019-02-18 12:30 | 173.47 | 169.53
2019-02-18 13:00 | 176.25 | 172.34
2019-02-18 13:30 | 178.15 | 174.24
2019-02-18 14:00 | 179.96 | 176.35
2019-02-18 14:30 | 182.07 | 178.57
2019-02-18 15:00 | 181.62 | 178.16
2019-02-18 15:30 | 183.47 | 180.07
2019-02-18 16:00 | 185.8 | 182.51
2019-02-18 16:30 | 186.61 | 183.25
2019-02-18 17:00 | 189.43 | 186.05
2019-02-18 17:30 | 190.59 | 187.1
2019-02-18 18:00 | 192.16 | 188.81
2019-02-18 18:30 | 193.28 | 190.01
2019-02-18 19:00 | 193.31 | 190
2019-02-18 19:30 | 192.21 | 188.87
2019-02-18 20:00 | 189.26 | 185.71
2019-02-18 20:30 | 185.19 | 181.31
2019-02-18 21:00 | 180.8 | 176.58
2019-02-18 21:30 | 176.2 | 172.02
2019-02-18 22:00 | 172.67 | 168.31
2019-02-18 22:30 | 169.09 | 164.66
2019-02-18 23:00 | 166.41 | 161.88
2019-02-18 23:30 | 164.9 | 160.37
2019-02-19 | 163.5 | 158.72
2019-02-19 00:30 | 162.28 | 157.39
2019-02-19 01:00 | 161.08 | 156.27
2019-02-19 01:30 | 160.92 | 156.11
2019-02-19 02:00 | 160.03 | 155.29
2019-02-19 02:30 | 159.93 | 155.21
2019-02-19 03:00 | 159.08 | 154.28
2019-02-19 03:30 | 158.87 | 154.03
2019-02-19 04:00 | 158.37 | 153.54
2019-02-19 04:30 | 158.32 | 153.51
2019-02-19 05:00 | 158.85 | 154.05
2019-02-19 05:30 | 159.85 | 155.14
2019-02-19 06:00 | 161.02 | 156.45
2019-02-19 06:30 | 163.18 | 158.61
2019-02-19 07:00 | 164.44 | 159.74
2019-02-19 07:30 | 166.23 | 161.79
2019-02-19 08:00 | 167.32 | 163.14
2019-02-19 08:30 | 167.84 | 163.8
2019-02-19 09:00 | 168.42 | 164.37
2019-02-19 09:30 | 169.49 | 165.47
2019-02-19 10:00 | 171.23 | 167.25
2019-02-19 10:30 | 172.68 | 168.67
2019-02-19 11:00 | 177.98 | 174.15
2019-02-19 11:30 | 186.57 | 183.01
2019-02-19 12:00 | 188.37 | 184.87
2019-02-19 12:30 | 191.25 | 187.68
2019-02-19 13:00 | 193.66 | 190.22
2019-02-19 13:30 | 196.09 | 192.78
2019-02-19 14:00 | 198.06 | 194.8
2019-02-19 14:30 | 199.38 | 196.15
2019-02-19 15:00 | 199.95 | 196.54
2019-02-19 15:30 | 186.42 | 183.44
2019-02-19 16:00 | 158.17 | 155.83
2019-02-19 16:30 | 157.03 | 154.75
2019-02-19 17:00 | 156.5 | 154.23
2019-02-19 17:30 | 190.48 | 187.12
2019-02-19 18:00 | 200.03 | 196.75
2019-02-19 18:30 | 214.73 | 211.49
2019-02-19 19:00 | 218.2 | 214.92
2019-02-19 19:30 | 218.06 | 214.73
2019-02-19 20:00 | 215.49 | 211.95
2019-02-19 20:30 | 212.22 | 208.2
2019-02-19 21:00 | 207.92 | 203.7
2019-02-19 21:30 | 202.92 | 198.48
2019-02-19 22:00 | 199.56 | 194.95
2019-02-19 22:30 | 195.21 | 190.64
2019-02-19 23:00 | 192.4 | 187.79
2019-02-19 23:30 | 190.77 | 186.2
2019-02-20 | 188.52 | 183.91
2019-02-20 00:30 | 187.18 | 182.74
2019-02-20 01:00 | 185.37 | 180.91
2019-02-20 01:30 | 183.52 | 179.46
2019-02-20 02:00 | 182.19 | 178.2
2019-02-20 02:30 | 181.48 | 177.48
2019-02-20 03:00 | 180.43 | 176.43
2019-02-20 03:30 | 179.93 | 175.92
2019-02-20 04:00 | 179.3 | 175.27
2019-02-20 04:30 | 179.16 | 175.14
2019-02-20 05:00 | 179.4 | 175.42
2019-02-20 05:30 | 180.28 | 175.74
2019-02-20 06:00 | 180.7 | 176.26
2019-02-20 06:30 | 182.87 | 178.5
2019-02-20 07:00 | 183.47 | 178.84
2019-02-20 07:30 | 184.77 | 180.24
2019-02-20 08:00 | 185.62 | 180.97
2019-02-20 08:30 | 185.61 | 181
2019-02-20 09:00 | 185.84 | 181.37
2019-02-20 09:30 | 185.54 | 181.12
2019-02-20 10:00 | 188.19 | 183.86
2019-02-20 10:30 | 192.56 | 188.61
2019-02-20 11:00 | 197 | 193.8
2019-02-20 11:30 | 190.44 | 187.35
2019-02-20 12:00 | 194.2 | 191.33
2019-02-20 12:30 | 196.06 | 193.22
2019-02-20 13:00 | 198.14 | 195.34
2019-02-20 13:30 | 200.3 | 197.45
2019-02-20 14:00 | 201.97 | 199.3
2019-02-20 14:30 | 206 | 203.08
2019-02-20 15:00 | 206.9 | 203.92
2019-02-20 15:30 | 231.4 | 228.4
2019-02-20 16:00 | 253.31 | 250.51
2019-02-20 16:30 | 256.78 | 254.12
2019-02-20 17:00 | 259.16 | 256.68
2019-02-20 17:30 | 260.07 | 257.47
2019-02-20 18:00 | 261.96 | 259.29
2019-02-20 18:30 | 263.22 | 260.42
2019-02-20 19:00 | 264.25 | 261.38
2019-02-20 19:30 | 263.62 | 260.74
2019-02-20 20:00 | 261.3 | 258.36
2019-02-20 20:30 | 258.69 | 255.36
2019-02-20 21:00 | 256.77 | 253.02
2019-02-20 21:30 | 253.49 | 249.55
2019-02-20 22:00 | 248.36 | 245.15
2019-02-20 22:30 | 244.46 | 241.43
2019-02-20 23:00 | 242.03 | 239.18
2019-02-20 23:30 | 240.1 | 237.26
2019-02-21 | 237.95 | 235.1
2019-02-21 00:30 | 235.7 | 232.93
2019-02-21 01:00 | 234.53 | 231.76
2019-02-21 01:30 | 233.14 | 230.32
2019-02-21 02:00 | 231.43 | 228.5
2019-02-21 02:30 | 231.57 | 228.55
2019-02-21 03:00 | 231.24 | 228.18
2019-02-21 03:30 | 230.5 | 227.37
2019-02-21 04:00 | 230.58 | 227.46
2019-02-21 04:30 | 230.26 | 227.16
2019-02-21 05:00 | 230.44 | 227.39
2019-02-21 05:30 | 231.38 | 228.4
2019-02-21 06:00 | 232.16 | 229.07
2019-02-21 06:30 | 234.17 | 230.74
2019-02-21 07:00 | 236.17 | 232.07
2019-02-21 07:30 | 236.63 | 232.73
2019-02-21 08:00 | 236.69 | 232.9
2019-02-21 08:30 | 235.99 | 232.35
2019-02-21 09:00 | 235.87 | 232.18
2019-02-21 09:30 | 235.46 | 231.65
2019-02-21 10:00 | 236.27 | 232.41
2019-02-21 10:30 | 237.09 | 233.34
2019-02-21 11:00 | 238.23 | 234.65
2019-02-21 11:30 | 239.93 | 236.41
2019-02-21 12:00 | 240.82 | 237.33
2019-02-21 12:30 | 241.14 | 237.78
2019-02-21 13:00 | 242.74 | 239.57
2019-02-21 13:30 | 244.88 | 241.82
2019-02-21 14:00 | 227.99 | 225.03
2019-02-21 14:30 | 190.66 | 186.97
2019-02-21 15:00 | 190.23 | 186.76
2019-02-21 15:30 | 219.1 | 216.22
2019-02-21 16:00 | 231.59 | 228.88
2019-02-21 16:30 | 232.88 | 230.11
2019-02-21 17:00 | 235.51 | 232.76
2019-02-21 17:30 | 236.72 | 233.92
2019-02-21 18:00 | 248.23 | 245.6
2019-02-21 18:30 | 260.44 | 257.8
2019-02-21 19:00 | 262.22 | 259.49
2019-02-21 19:30 | 261.61 | 258.71
2019-02-21 20:00 | 259.1 | 255.87
2019-02-21 20:30 | 256.65 | 253.33
2019-02-21 21:00 | 252.7 | 249.14
2019-02-21 21:30 | 249.49 | 246.2
2019-02-21 22:00 | 245.78 | 242.77
2019-02-21 22:30 | 242.63 | 239.77
2019-02-21 23:00 | 240.62 | 237.7
2019-02-21 23:30 | 239.14 | 236.12
2019-02-22 | 237.98 | 234.72
2019-02-22 00:30 | 237.09 | 233.86
2019-02-22 01:00 | 236.35 | 233.22
2019-02-22 01:30 | 236.71 | 233.49
2019-02-22 02:00 | 236.56 | 233.31
2019-02-22 02:30 | 235.68 | 232.51
2019-02-22 03:00 | 235.8 | 232.67
2019-02-22 03:30 | 235.11 | 231.98
2019-02-22 04:00 | 235.52 | 232.39
2019-02-22 04:30 | 235.29 | 232.15
2019-02-22 05:00 | 235.79 | 232.62
2019-02-22 05:30 | 236.8 | 233.81
2019-02-22 06:00 | 236.86 | 233.88
2019-02-22 06:30 | 240.06 | 236.67
2019-02-22 07:00 | 241.3 | 237.89
2019-02-22 07:30 | 242.32 | 239.14
2019-02-22 08:00 | 242.33 | 239.35
2019-02-22 08:30 | 241.81 | 238.94
2019-02-22 09:00 | 241.67 | 238.8
2019-02-22 09:30 | 241.72 | 238.77
2019-02-22 10:00 | 241.97 | 239.06
2019-02-22 10:30 | 240.84 | 237.96
2019-02-22 11:00 | 241.26 | 238.64
2019-02-22 11:30 | 243.32 | 240.64
2019-02-22 12:00 | 243.76 | 241.07
2019-02-22 12:30 | 245.14 | 242.45
2019-02-22 13:00 | 246.96 | 244.14
2019-02-22 13:30 | 248.53 | 245.66
2019-02-22 14:00 | 249.69 | 246.79
2019-02-22 14:30 | 250.79 | 247.89
2019-02-22 15:00 | 250.7 | 247.8
2019-02-22 15:30 | 251.62 | 248.88
2019-02-22 16:00 | 252.62 | 250.04
2019-02-22 16:30 | 254.12 | 251.59
2019-02-22 17:00 | 256.03 | 253.21
2019-02-22 17:30 | 256.87 | 253.85
2019-02-22 18:00 | 258 | 255.08
2019-02-22 18:30 | 258.33 | 255.45
2019-02-22 19:00 | 258.97 | 256
2019-02-22 19:30 | 259.2 | 256.18
2019-02-22 20:00 | 257.88 | 254.79
2019-02-22 20:30 | 255.67 | 252.44
2019-02-22 21:00 | 253.14 | 249.75
2019-02-22 21:30 | 250.16 | 247.19
2019-02-22 22:00 | 247.63 | 244.98
2019-02-22 22:30 | 245 | 242.23
2019-02-22 23:00 | 242.24 | 239.35
2019-02-22 23:30 | 240.64 | 237.67
2019-02-23 | 239.26 | 236.42
2019-02-23 00:30 | 238.25 | 235.28
2019-02-23 01:00 | 221.95 | 218.35
2019-02-23 01:30 | 186.33 | 180.28
2019-02-23 02:00 | 175.06 | 168.33
2019-02-23 02:30 | 173.61 | 166.89
2019-02-23 03:00 | 173.37 | 166.61
2019-02-23 03:30 | 172.62 | 165.83
2019-02-23 04:00 | 172.15 | 165.43
2019-02-23 04:30 | 171.64 | 164.89
2019-02-23 05:00 | 171.56 | 164.88
2019-02-23 05:30 | 171.3 | 164.4
2019-02-23 06:00 | 171.61 | 164.63
2019-02-23 06:30 | 171.35 | 164.77
2019-02-23 07:00 | 170.2 | 163.55
2019-02-23 07:30 | 171.41 | 164.67
2019-02-23 08:00 | 170.82 | 164.42
2019-02-23 08:30 | 170.7 | 164.61
2019-02-23 09:00 | 170.27 | 164.28
2019-02-23 09:30 | 168.36 | 163.04
2019-02-23 10:00 | 168.74 | 163.71
2019-02-23 10:30 | 169.05 | 163.93
2019-02-23 11:00 | 169.2 | 164.13
2019-02-23 11:30 | 170.44 | 165.42
2019-02-23 12:00 | 170.96 | 166.04
2019-02-23 12:30 | 172.08 | 167.19
2019-02-23 13:00 | 173.45 | 168.63
2019-02-23 13:30 | 174.56 | 169.73
2019-02-23 14:00 | 175.38 | 170.91
2019-02-23 14:30 | 176.81 | 172.37
2019-02-23 15:00 | 177.84 | 173.34
2019-02-23 15:30 | 178.99 | 174.55
2019-02-23 16:00 | 180.99 | 176.4
2019-02-23 16:30 | 183.59 | 179.09
2019-02-23 17:00 | 215.72 | 212.62
2019-02-23 17:30 | 245.28 | 242.01
2019-02-23 18:00 | 251.97 | 248.67
2019-02-23 18:30 | 251.68 | 248.37
2019-02-23 19:00 | 251.4 | 248.08
2019-02-23 19:30 | 251.1 | 247.57
2019-02-23 20:00 | 249.28 | 245.54
2019-02-23 20:30 | 248.11 | 244.04
2019-02-23 21:00 | 245.29 | 242.23
2019-02-23 21:30 | 243.51 | 240.59
2019-02-23 22:00 | 226.12 | 222.39
2019-02-23 22:30 | 187.92 | 182.23
2019-02-23 23:00 | 175.76 | 169.51
2019-02-23 23:30 | 175.08 | 168.79
2019-02-24 | 173.02 | 165.95
2019-02-24 00:30 | 172.51 | 165.56
2019-02-24 01:00 | 171.58 | 164.11
2019-02-24 01:30 | 170.74 | 163.33
2019-02-24 02:00 | 168.53 | 162.25
2019-02-24 02:30 | 167.9 | 161.74
2019-02-24 03:00 | 168.47 | 162.32
2019-02-24 03:30 | 168.01 | 161.72
2019-02-24 04:00 | 167.84 | 161.44
2019-02-24 04:30 | 168.1 | 161.71
2019-02-24 05:00 | 167.66 | 161.24
2019-02-24 05:30 | 167.26 | 161.18
2019-02-24 06:00 | 167.04 | 161.41
2019-02-24 06:30 | 167.06 | 161.66
2019-02-24 07:00 | 167.21 | 161.94
2019-02-24 07:30 | 167.74 | 162.27
2019-02-24 08:00 | 168.59 | 162.46
2019-02-24 08:30 | 168.08 | 162.1
2019-02-24 09:00 | 167.66 | 161.88
2019-02-24 09:30 | 165.34 | 160.41
2019-02-24 10:00 | 165.08 | 160.78
2019-02-24 10:30 | 165.85 | 161.49
2019-02-24 11:00 | 165.51 | 161.34
2019-02-24 11:30 | 167.84 | 163.63
2019-02-24 12:00 | 168.82 | 164.83
2019-02-24 12:30 | 170.63 | 166.55
2019-02-24 13:00 | 173.35 | 169.15
2019-02-24 13:30 | 174.77 | 170.35
2019-02-24 14:00 | 176.5 | 172.4
2019-02-24 14:30 | 176.72 | 173.08
2019-02-24 15:00 | 176.56 | 173.09
2019-02-24 15:30 | 178.26 | 174.85
2019-02-24 16:00 | 211.72 | 208.7
2019-02-24 16:30 | 224.83 | 221.96
2019-02-24 17:00 | 227.39 | 224.14
2019-02-24 17:30 | 229.46 | 225.75
2019-02-24 18:00 | 231.58 | 227.96
2019-02-24 18:30 | 232.58 | 228.93
2019-02-24 19:00 | 231.92 | 228.92
2019-02-24 19:30 | 231.33 | 228.82
2019-02-24 20:00 | 229.4 | 226.89
2019-02-24 20:30 | 226.57 | 223.8
2019-02-24 21:00 | 224.34 | 221.56
2019-02-24 21:30 | 222.21 | 219.37
2019-02-24 22:00 | 220.07 | 217.03
2019-02-24 22:30 | 217.5 | 214.41
2019-02-24 23:00 | 183.86 | 180.12
2019-02-24 23:30 | 170.66 | 165.95
2019-02-25 | 170.17 | 164.44
2019-02-25 00:30 | 169.24 | 163.47
2019-02-25 01:00 | 169.88 | 163.04
2019-02-25 01:30 | 170 | 163.04
2019-02-25 02:00 | 168.77 | 162.42
2019-02-25 02:30 | 168.12 | 161.73
2019-02-25 03:00 | 167.01 | 160.73
2019-02-25 03:30 | 166.9 | 160.58
2019-02-25 04:00 | 165.51 | 159.3
2019-02-25 04:30 | 166 | 159.93
2019-02-25 05:00 | 166.63 | 160.69
2019-02-25 05:30 | 167.51 | 161.62
2019-02-25 06:00 | 167.53 | 162.92
2019-02-25 06:30 | 200.19 | 196.9
2019-02-25 07:00 | 228.07 | 225.21
2019-02-25 07:30 | 234.23 | 231.55
2019-02-25 08:00 | 237.39 | 234.24
2019-02-25 08:30 | 237.45 | 234
2019-02-25 09:00 | 236.83 | 233.49
2019-02-25 09:30 | 236.48 | 232.96
2019-02-25 10:00 | 236.74 | 233.34
2019-02-25 10:30 | 235.46 | 232.01
2019-02-25 11:00 | 233.27 | 229.98
2019-02-25 11:30 | 235.12 | 231.91
2019-02-25 12:00 | 236.98 | 233.67
2019-02-25 12:30 | 237.84 | 234.52
2019-02-25 13:00 | 240.24 | 236.39
2019-02-25 13:30 | 243.23 | 238.33
2019-02-25 14:00 | 245.48 | 240.88
2019-02-25 14:30 | 245.87 | 241.16
2019-02-25 15:00 | 248.15 | 242.45
2019-02-25 15:30 | 248.99 | 243.01
2019-02-25 16:00 | 251.45 | 245.41
2019-02-25 16:30 | 252.79 | 246.92
2019-02-25 17:00 | 254.34 | 248.41
2019-02-25 17:30 | 254.75 | 248.43
2019-02-25 18:00 | 256.48 | 250.01
2019-02-25 18:30 | 256.13 | 249.61
2019-02-25 19:00 | 256.97 | 250.56
2019-02-25 19:30 | 257.77 | 251.07
2019-02-25 20:00 | 256.72 | 249.85
2019-02-25 20:30 | 253.22 | 246.8
2019-02-25 21:00 | 250.07 | 244.23
2019-02-25 21:30 | 247.43 | 242.44
2019-02-25 22:00 | 244.57 | 239.87
2019-02-25 22:30 | 241.89 | 236.97
2019-02-25 23:00 | 239.92 | 235.01
2019-02-25 23:30 | 239.01 | 234.06
2019-02-26 | 236.73 | 232.02
2019-02-26 00:30 | 217.65 | 213.4
2019-02-26 01:00 | 178.34 | 174.14
2019-02-26 01:30 | 167.17 | 162.4
2019-02-26 02:00 | 166.67 | 161.8
2019-02-26 02:30 | 166.19 | 161.34
2019-02-26 03:00 | 166.35 | 161.37
2019-02-26 03:30 | 165.91 | 160.89
2019-02-26 04:00 | 165.67 | 160.52
2019-02-26 04:30 | 165.74 | 160.65
2019-02-26 05:00 | 165.98 | 160.94
2019-02-26 05:30 | 166.8 | 162.03
2019-02-26 06:00 | 167.8 | 162.85
2019-02-26 06:30 | 202.34 | 197.6
2019-02-26 07:00 | 230.14 | 224.55
2019-02-26 07:30 | 237.16 | 232.01
2019-02-26 08:00 | 238.39 | 233.42
2019-02-26 08:30 | 238.42 | 233.46
2019-02-26 09:00 | 237.17 | 232.29
2019-02-26 09:30 | 236.47 | 231.35
2019-02-26 10:00 | 238.34 | 232.71
2019-02-26 10:30 | 238.79 | 232.99
2019-02-26 11:00 | 238.65 | 232.62
2019-02-26 11:30 | 239.06 | 233.03
2019-02-26 12:00 | 237.94 | 231.96
2019-02-26 12:30 | 238.13 | 232.25
2019-02-26 13:00 | 239.72 | 233.62
2019-02-26 13:30 | 241.87 | 235.86
2019-02-26 14:00 | 243.42 | 237.46
2019-02-26 14:30 | 244.5 | 238.64
2019-02-26 15:00 | 245.87 | 240.19
2019-02-26 15:30 | 246.43 | 241.06
2019-02-26 16:00 | 248.41 | 243.45
2019-02-26 16:30 | 249.49 | 244.5
2019-02-26 17:00 | 251.44 | 246.01
2019-02-26 17:30 | 253.07 | 247.36
2019-02-26 18:00 | 254.46 | 248.52
2019-02-26 18:30 | 256.1 | 249.81
2019-02-26 19:00 | 257.93 | 251.6
2019-02-26 19:30 | 258.19 | 251.87
2019-02-26 20:00 | 256.27 | 249.77
2019-02-26 20:30 | 253.07 | 246.47
2019-02-26 21:00 | 251.2 | 244.23
2019-02-26 21:30 | 248.03 | 241.66
2019-02-26 22:00 | 244.53 | 238.44
2019-02-26 22:30 | 241.61 | 235.28
2019-02-26 23:00 | 239.34 | 232.91
2019-02-26 23:30 | 237.74 | 231.6
2019-02-27 | 234.14 | 229.78
2019-02-27 00:30 | 233.66 | 229.26
2019-02-27 01:00 | 215.65 | 211.33
2019-02-27 01:30 | 177.6 | 173.26
2019-02-27 02:00 | 165.53 | 161.03
2019-02-27 02:30 | 164.96 | 160.38
2019-02-27 03:00 | 164.89 | 160.35
2019-02-27 03:30 | 164.14 | 159.53
2019-02-27 04:00 | 164.05 | 159.49
2019-02-27 04:30 | 163.88 | 159.44
2019-02-27 05:00 | 163.7 | 159.28
2019-02-27 05:30 | 164.69 | 160.17
2019-02-27 06:00 | 165.93 | 160.4
2019-02-27 06:30 | 200.17 | 194.19
2019-02-27 07:00 | 228.8 | 222.13
2019-02-27 07:30 | 237.07 | 230.38
2019-02-27 08:00 | 237.83 | 231.74
2019-02-27 08:30 | 236.3 | 230.99
2019-02-27 09:00 | 236.59 | 230.37
2019-02-27 09:30 | 235.71 | 229.46
2019-02-27 10:00 | 235.83 | 229.79
2019-02-27 10:30 | 235.03 | 228.85
2019-02-27 11:00 | 236.48 | 230.14
2019-02-27 11:30 | 238.42 | 231.98
2019-02-27 12:00 | 239.5 | 233.05
2019-02-27 12:30 | 240.21 | 233.65
2019-02-27 13:00 | 238.41 | 232.07
2019-02-27 13:30 | 236.53 | 230.68
2019-02-27 14:00 | 238.67 | 233.21
2019-02-27 14:30 | 237.82 | 232.51
2019-02-27 15:00 | 237.27 | 231.77
2019-02-27 15:30 | 237.89 | 232.55
2019-02-27 16:00 | 239.52 | 234.72
2019-02-27 16:30 | 241.45 | 236.45
2019-02-27 17:00 | 243.53 | 238.67
2019-02-27 17:30 | 244.24 | 239.24
2019-02-27 18:00 | 245.57 | 240.43
2019-02-27 18:30 | 246.94 | 241.39
2019-02-27 19:00 | 248.06 | 242.54
2019-02-27 19:30 | 248.34 | 242.78
2019-02-27 20:00 | 246.97 | 241.11
2019-02-27 20:30 | 244.77 | 238.68
2019-02-27 21:00 | 240.31 | 235.53
2019-02-27 21:30 | 238.36 | 234.21
2019-02-27 22:00 | 234.26 | 231.04
2019-02-27 22:30 | 231.8 | 228.82
2019-02-27 23:00 | 229.55 | 226.44
2019-02-27 23:30 | 228.31 | 225.3
2019-02-28 | 227 | 223.65
2019-02-28 00:30 | 226.6 | 222.77
2019-02-28 01:00 | 208.92 | 205.29
2019-02-28 01:30 | 168.73 | 165.5
2019-02-28 02:00 | 158.66 | 155.41
2019-02-28 02:30 | 157.29 | 153.99
2019-02-28 03:00 | 157.2 | 153.83
2019-02-28 03:30 | 157.19 | 153.73
2019-02-28 04:00 | 156.94 | 153.41
2019-02-28 04:30 | 157.24 | 153.79
2019-02-28 05:00 | 157.82 | 154.39
2019-02-28 05:30 | 159.1 | 155.56
2019-02-28 06:00 | 160.2 | 156.72
2019-02-28 06:30 | 194.7 | 191.3
2019-02-28 07:00 | 222.31 | 218.59
2019-02-28 07:30 | 225.03 | 220.92
2019-02-28 08:00 | 222.82 | 218.75
2019-02-28 08:30 | 218.76 | 214.96
2019-02-28 09:00 | 216.68 | 212.97
2019-02-28 09:30 | 215.05 | 211.55
2019-02-28 10:00 | 215.4 | 211.92
2019-02-28 10:30 | 214.32 | 210.36
2019-02-28 11:00 | 214.99 | 210.79
2019-02-28 11:30 | 215.04 | 210.72
2019-02-28 12:00 | 215.88 | 211.53
2019-02-28 12:30 | 216.5 | 211.96
2019-02-28 13:00 | 217.53 | 213.34
2019-02-28 13:30 | 219.1 | 215.01
2019-02-28 14:00 | 221.23 | 216.86
2019-02-28 14:30 | 224.09 | 219.69
2019-02-28 15:00 | 224.97 | 220.84
2019-02-28 15:30 | 226.41 | 221.65
2019-02-28 16:00 | 226.41 | 222.08
2019-02-28 16:30 | 227.09 | 222.63
2019-02-28 17:00 | 228.29 | 223.75
2019-02-28 17:30 | 227.59 | 222.8
2019-02-28 18:00 | 229.02 | 224.15
2019-02-28 18:30 | 230.66 | 225.72
2019-02-28 19:00 | 231.54 | 226.46
2019-02-28 19:30 | 232.04 | 226.84
2019-02-28 20:00 | 230.43 | 225.11
2019-02-28 20:30 | 228.17 | 222.37
2019-02-28 21:00 | 226.08 | 219.98
2019-02-28 21:30 | 223.21 | 218.13
2019-02-28 22:00 | 221.05 | 216.03
2019-02-28 22:30 | 219.38 | 214.19
2019-02-28 23:00 | 217.7 | 212.59
2019-02-28 23:30 | 218.7 | 214.07
2019-03-01 | 216.94 | 212.25
2019-03-01 00:30 | 216.27 | 211.75
2019-03-01 01:00 | 197.29 | 193.62
2019-03-01 01:30 | 157.57 | 153.84
2019-03-01 02:00 | 146.73 | 142.88
2019-03-01 02:30 | 146.15 | 142.14
2019-03-01 03:00 | 145.71 | 141.83
2019-03-01 03:30 | 145.16 | 141.52
2019-03-01 04:00 | 144.82 | 141.19
2019-03-01 04:30 | 145.05 | 141.45
2019-03-01 05:00 | 145.48 | 141.89
2019-03-01 05:30 | 146.81 | 142.91
2019-03-01 06:00 | 148.1 | 144.16
2019-03-01 06:30 | 181.97 | 178.4
2019-03-01 07:00 | 209.88 | 205.63
2019-03-01 07:30 | 219.54 | 214.82
2019-03-01 08:00 | 220.55 | 216.02
2019-03-01 08:30 | 219.04 | 214.58
2019-03-01 09:00 | 217.72 | 213.5
2019-03-01 09:30 | 217.21 | 212.81
2019-03-01 10:00 | 218.3 | 214.04
2019-03-01 10:30 | 217.96 | 213.55
2019-03-01 11:00 | 217.21 | 213.14
2019-03-01 11:30 | 217.59 | 213.26
2019-03-01 12:00 | 218.81 | 214.51
2019-03-01 12:30 | 219.69 | 215.38
2019-03-01 13:00 | 220.45 | 215.94
2019-03-01 13:30 | 220.77 | 216.08
2019-03-01 14:00 | 221.37 | 216.79
2019-03-01 14:30 | 222.75 | 218.17
2019-03-01 15:00 | 223.17 | 218.64
2019-03-01 15:30 | 223.02 | 218.27
2019-03-01 16:00 | 224.86 | 220.1
2019-03-01 16:30 | 225.17 | 220.49
2019-03-01 17:00 | 224.52 | 219.77
2019-03-01 17:30 | 226.09 | 221.09
2019-03-01 18:00 | 226.18 | 221.69
2019-03-01 18:30 | 226.34 | 221.81
2019-03-01 19:00 | 227.03 | 222.57
2019-03-01 19:30 | 227.38 | 222.94
2019-03-01 20:00 | 226.53 | 221.9
2019-03-01 20:30 | 224.68 | 219.74
2019-03-01 21:00 | 222.8 | 217.76
2019-03-01 21:30 | 222.17 | 217.49
2019-03-01 22:00 | 220.91 | 216.03
2019-03-01 22:30 | 218.93 | 213.93
2019-03-01 23:00 | 217.04 | 212.57
2019-03-01 23:30 | 216.32 | 211.8
2019-03-02 | 214.42 | 210.09
2019-03-02 00:30 | 213.76 | 209.35
2019-03-02 01:00 | 212.15 | 207.96
2019-03-02 01:30 | 210.77 | 207.11
2019-03-02 02:00 | 210.4 | 206.76
2019-03-02 02:30 | 210.41 | 206.85
2019-03-02 03:00 | 209.91 | 206.32
2019-03-02 03:30 | 210.42 | 206.99
2019-03-02 04:00 | 210.17 | 206.69
2019-03-02 04:30 | 209.95 | 206.51
2019-03-02 05:00 | 210.01 | 206.54
2019-03-02 05:30 | 210.38 | 206.86
2019-03-02 06:00 | 210.68 | 207.21
2019-03-02 06:30 | 211.51 | 208.17
2019-03-02 07:00 | 212.32 | 208.72
2019-03-02 07:30 | 212.65 | 209.14
2019-03-02 08:00 | 211.45 | 208.02
2019-03-02 08:30 | 212.27 | 207.62
2019-03-02 09:00 | 211.46 | 207.17
2019-03-02 09:30 | 211.01 | 206.92
2019-03-02 10:00 | 210.19 | 206.27
2019-03-02 10:30 | 193.44 | 189.77
2019-03-02 11:00 | 189.87 | 185.8
2019-03-02 11:30 | 190.26 | 186.49
2019-03-02 12:00 | 192.21 | 187
2019-03-02 12:30 | 194.26 | 188.28
2019-03-02 13:00 | 193.88 | 188.14
2019-03-02 13:30 | 194.8 | 188.58
2019-03-02 14:00 | 197.03 | 190.27
2019-03-02 14:30 | 195.45 | 189.78
2019-03-02 15:00 | 194.92 | 189.83
2019-03-02 15:30 | 213.76 | 209.05
2019-03-02 16:00 | 219.15 | 213.84
2019-03-02 16:30 | 221.02 | 216.07
2019-03-02 17:00 | 222.56 | 217.53
2019-03-02 17:30 | 224.5 | 219.32
2019-03-02 18:00 | 226.16 | 220.65
2019-03-02 18:30 | 227.67 | 222.05
2019-03-02 19:00 | 228.6 | 222.96
2019-03-02 19:30 | 228.96 | 223.49
2019-03-02 20:00 | 227.87 | 222.12
2019-03-02 20:30 | 225.92 | 220.13
2019-03-02 21:00 | 224.04 | 218.37
2019-03-02 21:30 | 222.57 | 217.18
2019-03-02 22:00 | 220.33 | 215.32
2019-03-02 22:30 | 218.69 | 213.37
2019-03-02 23:00 | 217.67 | 212.18
2019-03-02 23:30 | 216.92 | 211.53
2019-03-03 | 215.44 | 210.06
2019-03-03 00:30 | 213.96 | 209.59
2019-03-03 01:00 | 212.62 | 208.37
2019-03-03 01:30 | 212.63 | 208.01
2019-03-03 02:00 | 211.5 | 207.27
2019-03-03 02:30 | 210.92 | 206.8
2019-03-03 03:00 | 210.72 | 206.58
2019-03-03 03:30 | 210.59 | 206.37
2019-03-03 04:00 | 210.21 | 205.89
2019-03-03 04:30 | 209.63 | 205.33
2019-03-03 05:00 | 210.06 | 205.78
2019-03-03 05:30 | 209.89 | 205.8
2019-03-03 06:00 | 210.99 | 206.09
2019-03-03 06:30 | 211.66 | 206.49
2019-03-03 07:00 | 211.27 | 206.24
2019-03-03 07:30 | 212.21 | 206.99
2019-03-03 08:00 | 211.51 | 206.31
2019-03-03 08:30 | 211.22 | 205.79
2019-03-03 09:00 | 210.64 | 204.91
2019-03-03 09:30 | 211.14 | 204.12
2019-03-03 10:00 | 210.86 | 204.58
2019-03-03 10:30 | 211.09 | 204.29
2019-03-03 11:00 | 211.88 | 205.08
2019-03-03 11:30 | 212.59 | 205.74
2019-03-03 12:00 | 213.13 | 206.36
2019-03-03 12:30 | 214.02 | 207.72
2019-03-03 13:00 | 215.14 | 208.86
2019-03-03 13:30 | 216.23 | 209.84
2019-03-03 14:00 | 217.99 | 211.41
2019-03-03 14:30 | 217.39 | 211.21
2019-03-03 15:00 | 218.52 | 212.26
2019-03-03 15:30 | 219.83 | 212.94
2019-03-03 16:00 | 220.96 | 214.54
2019-03-03 16:30 | 221.88 | 215.25
2019-03-03 17:00 | 224.5 | 217.91
2019-03-03 17:30 | 225.94 | 219.59
2019-03-03 18:00 | 226.42 | 221.28
2019-03-03 18:30 | 227.66 | 222.45
2019-03-03 19:00 | 228.44 | 223.63
2019-03-03 19:30 | 228.29 | 223.91
2019-03-03 20:00 | 226.85 | 222.35
2019-03-03 20:30 | 225.24 | 220.59
2019-03-03 21:00 | 223.29 | 218.14
2019-03-03 21:30 | 221.51 | 216.4
2019-03-03 22:00 | 219.36 | 214.6
2019-03-03 22:30 | 217.73 | 212.81
2019-03-03 23:00 | 216.26 | 211.38
2019-03-03 23:30 | 215.33 | 210.69
2019-03-04 | 213.83 | 209.44
2019-03-04 00:30 | 212.62 | 209.02
2019-03-04 01:00 | 211.96 | 208.37
2019-03-04 01:30 | 211.49 | 207.82
2019-03-04 02:00 | 211.65 | 207.48
2019-03-04 02:30 | 210.91 | 206.66
2019-03-04 03:00 | 210.57 | 206.29
2019-03-04 03:30 | 210.48 | 206.14
2019-03-04 04:00 | 210.64 | 206.16
2019-03-04 04:30 | 210.66 | 206.39
2019-03-04 05:00 | 211.49 | 207.04
2019-03-04 05:30 | 196.42 | 190.34
2019-03-04 06:00 | 194.11 | 187.94
2019-03-04 06:30 | 195.64 | 189.64
2019-03-04 07:00 | 196.16 | 190.6
2019-03-04 07:30 | 197.08 | 191.5
2019-03-04 08:00 | 197.32 | 191.48
2019-03-04 08:30 | 195.04 | 190
2019-03-04 09:00 | 194.14 | 189.25
2019-03-04 09:30 | 192.58 | 187.9
2019-03-04 10:00 | 192.64 | 188.01
2019-03-04 10:30 | 193.07 | 188.09
2019-03-04 11:00 | 193.63 | 188.65
2019-03-04 11:30 | 194.51 | 189.61
2019-03-04 12:00 | 195.8 | 190.93
2019-03-04 12:30 | 211.71 | 206.76
2019-03-04 13:00 | 218.42 | 213.41
2019-03-04 13:30 | 220.53 | 215.5
2019-03-04 14:00 | 221.05 | 216.51
2019-03-04 14:30 | 221.85 | 217.39
2019-03-04 15:00 | 222.17 | 217.85
2019-03-04 15:30 | 217.42 | 213.27
2019-03-04 16:00 | 165.63 | 161.39
2019-03-04 16:30 | 190.48 | 187.34
2019-03-04 17:00 | 172.99 | 169.04
2019-03-04 17:30 | 168.1 | 164.03
2019-03-04 18:00 | 176.22 | 172.9
2019-03-04 18:30 | 178.15 | 174.61
2019-03-04 19:00 | 180.22 | 176.7
2019-03-04 19:30 | 180.36 | 176.86
2019-03-04 20:00 | 178.46 | 174.92
2019-03-04 20:30 | 177.1 | 173.29
2019-03-04 21:00 | 173.96 | 169.97
2019-03-04 21:30 | 171.58 | 168.01
2019-03-04 22:00 | 168.65 | 165.32
2019-03-04 22:30 | 165.86 | 162.53
2019-03-04 23:00 | 163.95 | 160.48
2019-03-04 23:30 | 162.79 | 159.22
2019-03-05 | 161.16 | 157.7
2019-03-05 00:30 | 159.79 | 156.43
2019-03-05 01:00 | 159.52 | 155.79
2019-03-05 01:30 | 158.68 | 154.87
2019-03-05 02:00 | 158.28 | 154.33
2019-03-05 02:30 | 157.55 | 153.92
2019-03-05 03:00 | 156.97 | 153.34
2019-03-05 03:30 | 156.67 | 153.09
2019-03-05 04:00 | 156.66 | 152.96
2019-03-05 04:30 | 157.02 | 153.27
2019-03-05 05:00 | 157.38 | 153.65
2019-03-05 05:30 | 158.35 | 154.82
2019-03-05 06:00 | 159.52 | 155.8
2019-03-05 06:30 | 160.26 | 156.37
2019-03-05 07:00 | 160.91 | 157.26
2019-03-05 07:30 | 159.7 | 155.78
2019-03-05 08:00 | 162.09 | 158.35
2019-03-05 08:30 | 161.23 | 157.64
2019-03-05 09:00 | 161.02 | 157.37
2019-03-05 09:30 | 160.15 | 156.57
2019-03-05 10:00 | 160.69 | 157.1
2019-03-05 10:30 | 161.12 | 157.38
2019-03-05 11:00 | 163.07 | 159.28
2019-03-05 11:30 | 163.79 | 160.15
2019-03-05 12:00 | 164.79 | 161.21
2019-03-05 12:30 | 165.61 | 162.13
2019-03-05 13:00 | 166.63 | 163.07
2019-03-05 13:30 | 168.3 | 164.81
2019-03-05 14:00 | 169.71 | 166.31
2019-03-05 14:30 | 174.99 | 171.44
2019-03-05 15:00 | 178.59 | 174.84
2019-03-05 15:30 | 181.09 | 177.25
2019-03-05 16:00 | 181.25 | 177.47
2019-03-05 16:30 | 182.76 | 178.92
2019-03-05 17:00 | 184.65 | 180.86
2019-03-05 17:30 | 185.93 | 182.07
2019-03-05 18:00 | 187.08 | 183.24
2019-03-05 18:30 | 187.32 | 183.32
2019-03-05 19:00 | 188.75 | 184.81
2019-03-05 19:30 | 196.88 | 192.45
2019-03-05 20:00 | 204.59 | 200.03
2019-03-05 20:30 | 202.25 | 197.32
2019-03-05 21:00 | 199.38 | 194.33
2019-03-05 21:30 | 197.89 | 193.26
2019-03-05 22:00 | 196.37 | 191.35
2019-03-05 22:30 | 194.4 | 188.71
2019-03-05 23:00 | 192.49 | 186.68
2019-03-05 23:30 | 190.93 | 185.32
2019-03-06 | 188.82 | 183.83
2019-03-06 00:30 | 187.58 | 182.96
2019-03-06 01:00 | 187.32 | 182.58
2019-03-06 01:30 | 186.97 | 182.22
2019-03-06 02:00 | 187.02 | 182.2
2019-03-06 02:30 | 187.03 | 182.19
2019-03-06 03:00 | 187.42 | 182.51
2019-03-06 03:30 | 187.07 | 182.09
2019-03-06 04:00 | 187.19 | 182.25
2019-03-06 04:30 | 187.08 | 182.17
2019-03-06 05:00 | 187.09 | 182.26
2019-03-06 05:30 | 188.5 | 183.21
2019-03-06 06:00 | 189.46 | 184
2019-03-06 06:30 | 191.23 | 185.87
2019-03-06 07:00 | 192.52 | 186.54
2019-03-06 07:30 | 194.33 | 188.43
2019-03-06 08:00 | 192.99 | 187.51
2019-03-06 08:30 | 192.62 | 186.53
2019-03-06 09:00 | 193.72 | 187.21
2019-03-06 09:30 | 193.53 | 187.2
2019-03-06 10:00 | 194.15 | 187.81
2019-03-06 10:30 | 194.32 | 188.11
2019-03-06 11:00 | 195.68 | 190
2019-03-06 11:30 | 196.76 | 191.44
2019-03-06 12:00 | 198.25 | 193.46
2019-03-06 12:30 | 199.9 | 195.63
2019-03-06 13:00 | 200.01 | 195.72
2019-03-06 13:30 | 201.59 | 198.04
2019-03-06 14:00 | 203.27 | 199.95
2019-03-06 14:30 | 205.86 | 202.47
2019-03-06 15:00 | 206.42 | 202.98
2019-03-06 15:30 | 208.27 | 204.92
2019-03-06 16:00 | 210.93 | 207.65
2019-03-06 16:30 | 210.35 | 206.7
2019-03-06 17:00 | 212.15 | 208.47
2019-03-06 17:30 | 213.65 | 210.1
2019-03-06 18:00 | 214.95 | 212.04
2019-03-06 18:30 | 215.9 | 213.04
2019-03-06 19:00 | 217.01 | 213.99
2019-03-06 19:30 | 217.46 | 214.11
2019-03-06 20:00 | 214.94 | 211.19
2019-03-06 20:30 | 210.91 | 206.67
2019-03-06 21:00 | 207.71 | 202.95
2019-03-06 21:30 | 203.39 | 199.27
2019-03-06 22:00 | 199.13 | 194.96
2019-03-06 22:30 | 195.75 | 191.75
2019-03-06 23:00 | 194.21 | 189.48
2019-03-06 23:30 | 192.79 | 187.89
2019-03-07 | 191.08 | 186.34
2019-03-07 00:30 | 189.68 | 185.16
2019-03-07 01:00 | 188.79 | 184.02
2019-03-07 01:30 | 188.58 | 183.35
2019-03-07 02:00 | 188.29 | 183
2019-03-07 02:30 | 187.7 | 182.42
2019-03-07 03:00 | 187.36 | 182.13
2019-03-07 03:30 | 187.29 | 182
2019-03-07 04:00 | 187.01 | 181.7
2019-03-07 04:30 | 186.8 | 181.59
2019-03-07 05:00 | 187.38 | 182.3
2019-03-07 05:30 | 188.2 | 183.36
2019-03-07 06:00 | 189.82 | 184.4
2019-03-07 06:30 | 190.74 | 185.66
2019-03-07 07:00 | 192.29 | 186.82
2019-03-07 07:30 | 192.48 | 187.39
2019-03-07 08:00 | 191.81 | 187.32
2019-03-07 08:30 | 190.53 | 186.23
2019-03-07 09:00 | 190.11 | 185.79
2019-03-07 09:30 | 189.54 | 185.31
2019-03-07 10:00 | 189.13 | 185.22
2019-03-07 10:30 | 189.8 | 185.63
2019-03-07 11:00 | 190.66 | 186.52
2019-03-07 11:30 | 191.58 | 187.38
2019-03-07 12:00 | 193.48 | 189.47
2019-03-07 12:30 | 178.88 | 175.14
2019-03-07 13:00 | 178.4 | 174.88
2019-03-07 13:30 | 180.43 | 177.05
2019-03-07 14:00 | 182.57 | 179.43
2019-03-07 14:30 | 182.55 | 179.59
2019-03-07 15:00 | 185.17 | 181.49
2019-03-07 15:30 | 201.53 | 197.6
2019-03-07 16:00 | 228.05 | 223.97
2019-03-07 16:30 | 237.22 | 232.96
2019-03-07 17:00 | 238.61 | 234.5
2019-03-07 17:30 | 239.98 | 235.71
2019-03-07 18:00 | 241.03 | 236.53
2019-03-07 18:30 | 241.23 | 236.55
2019-03-07 19:00 | 204.63 | 200.39
2019-03-07 19:30 | 172.15 | 168.07
2019-03-07 20:00 | 169.94 | 165.6
2019-03-07 20:30 | 167.43 | 162.58
2019-03-07 21:00 | 164.27 | 158.91
2019-03-07 21:30 | 161.28 | 156.38
2019-03-07 22:00 | 157.68 | 152.73
2019-03-07 22:30 | 155.15 | 150.45
2019-03-07 23:00 | 153.41 | 148.52
2019-03-07 23:30 | 152.17 | 147.11
2019-03-08 | 150.99 | 145.87
2019-03-08 00:30 | 150 | 144.86
2019-03-08 01:00 | 149.53 | 144.36
2019-03-08 01:30 | 148.86 | 143.55
2019-03-08 02:00 | 148.26 | 142.68
2019-03-08 02:30 | 148.36 | 142.9
2019-03-08 03:00 | 148.5 | 143
2019-03-08 03:30 | 148.14 | 142.53
2019-03-08 04:00 | 148.03 | 142.38
2019-03-08 04:30 | 148 | 142.44
2019-03-08 05:00 | 148.95 | 143.43
2019-03-08 05:30 | 149.59 | 144.29
2019-03-08 06:00 | 150.61 | 145.45
2019-03-08 06:30 | 151.96 | 146.99
2019-03-08 07:00 | 152.72 | 147.94
2019-03-08 07:30 | 154.16 | 149.87
2019-03-08 08:00 | 153.98 | 149.72
2019-03-08 08:30 | 153.71 | 149.56
2019-03-08 09:00 | 153.74 | 149.53
2019-03-08 09:30 | 153.4 | 149.06
2019-03-08 10:00 | 154.1 | 149.81
2019-03-08 10:30 | 153.74 | 149.38
2019-03-08 11:00 | 155.24 | 151.02
2019-03-08 11:30 | 155.93 | 152.03
2019-03-08 12:00 | 156.77 | 152.95
2019-03-08 12:30 | 158.49 | 154.82
2019-03-08 13:00 | 159.86 | 156.08
2019-03-08 13:30 | 160.49 | 156.69
2019-03-08 14:00 | 161.73 | 158.02
2019-03-08 14:30 | 163.13 | 159.6
2019-03-08 15:00 | 165.44 | 162.08
2019-03-08 15:30 | 166.8 | 163.8
2019-03-08 16:00 | 169.03 | 166.31
2019-03-08 16:30 | 194.39 | 191.82
2019-03-08 17:00 | 223.65 | 220.66
2019-03-08 17:30 | 238.83 | 235.1
2019-03-08 18:00 | 241.78 | 237.86
2019-03-08 18:30 | 242.96 | 238.85
2019-03-08 19:00 | 244.17 | 240.04
2019-03-08 19:30 | 243.91 | 239.78
2019-03-08 20:00 | 242.42 | 238.04
2019-03-08 20:30 | 240.27 | 235.55
2019-03-08 21:00 | 238 | 232.94
2019-03-08 21:30 | 236.47 | 231.54
2019-03-08 22:00 | 233.44 | 229.2
2019-03-08 22:30 | 231.06 | 227.04
2019-03-08 23:00 | 229.43 | 225.21
2019-03-08 23:30 | 228.22 | 223.98
2019-03-09 | 226.23 | 221.78
2019-03-09 00:30 | 224.98 | 221
2019-03-09 01:00 | 222.87 | 219.02
2019-03-09 01:30 | 222.47 | 218.52
2019-03-09 02:00 | 221.85 | 217.94
2019-03-09 02:30 | 221.13 | 217.26
2019-03-09 03:00 | 220.41 | 216.53
2019-03-09 03:30 | 220.14 | 216.17
2019-03-09 04:00 | 220.2 | 216.21
2019-03-09 04:30 | 219.99 | 215.88
2019-03-09 05:00 | 219.02 | 214.95
2019-03-09 05:30 | 218.69 | 214.72
2019-03-09 06:00 | 218.27 | 214.14
2019-03-09 06:30 | 217.82 | 214.03
2019-03-09 07:00 | 217.76 | 214.32
2019-03-09 07:30 | 218.72 | 215.1
2019-03-09 08:00 | 220.08 | 215.81
2019-03-09 08:30 | 203.5 | 199.37
2019-03-09 09:00 | 165.19 | 160.9
2019-03-09 09:30 | 152.55 | 148.44
2019-03-09 10:00 | 153.28 | 149.33
2019-03-09 10:30 | 155.78 | 151.81
2019-03-09 11:00 | 158.53 | 154.71
2019-03-09 11:30 | 160.45 | 156.49
2019-03-09 12:00 | 162.05 | 158.41
2019-03-09 12:30 | 163.06 | 158.99
2019-03-09 13:00 | 160.66 | 153.95
2019-03-09 13:30 | 157.12 | 150.31
2019-03-09 14:00 | 156.9 | 150.62
2019-03-09 14:30 | 158.43 | 152.2
2019-03-09 15:00 | 159.51 | 153.41
2019-03-09 15:30 | 160.68 | 154.44
2019-03-09 16:00 | 160.77 | 154.39
2019-03-09 16:30 | 164.04 | 158.22
2019-03-09 17:00 | 196.7 | 191.15
2019-03-09 17:30 | 225.25 | 219.69
2019-03-09 18:00 | 232.45 | 226.88
2019-03-09 18:30 | 232.69 | 226.98
2019-03-09 19:00 | 231.27 | 225.6
2019-03-09 19:30 | 231.06 | 225.2
2019-03-09 20:00 | 229.92 | 223.81
2019-03-09 20:30 | 227.69 | 221.32
2019-03-09 21:00 | 225.86 | 219
2019-03-09 21:30 | 223.76 | 217.07
2019-03-09 22:00 | 220.22 | 215.08
2019-03-09 22:30 | 217.84 | 213.48
2019-03-09 23:00 | 216.4 | 211.89
2019-03-09 23:30 | 198.53 | 194.04
2019-03-10 | 158.05 | 153.62
2019-03-10 00:30 | 145.26 | 140.65
2019-03-10 01:00 | 144.89 | 140.49
2019-03-10 01:30 | 144.31 | 139.92
2019-03-10 02:00 | 143.91 | 139.51
2019-03-10 02:30 | 143.22 | 138.94
2019-03-10 03:00 | 142.69 | 138.63
2019-03-10 03:30 | 142.31 | 138.29
2019-03-10 04:00 | 141.62 | 137.59
2019-03-10 04:30 | 141.36 | 137.22
2019-03-10 05:00 | 142.02 | 137.81
2019-03-10 05:30 | 141.45 | 137.27
2019-03-10 06:00 | 141.27 | 137.17
2019-03-10 06:30 | 141.54 | 137.62
2019-03-10 07:00 | 141.18 | 137.22
2019-03-10 07:30 | 142.4 | 138.34
2019-03-10 08:00 | 145.05 | 140.4
2019-03-10 08:30 | 146.79 | 140.06
2019-03-10 09:00 | 147.62 | 140.61
2019-03-10 09:30 | 148.41 | 141.76
2019-03-10 10:00 | 150.52 | 144.42
2019-03-10 10:30 | 151.13 | 145.1
2019-03-10 11:00 | 153.09 | 146.93
2019-03-10 11:30 | 153.99 | 147.08
2019-03-10 12:00 | 156.81 | 150.64
2019-03-10 12:30 | 157.57 | 152.15
2019-03-10 13:00 | 159.37 | 154.93
2019-03-10 13:30 | 159.8 | 155.4
2019-03-10 14:00 | 161.54 | 157.64
2019-03-10 14:30 | 193.64 | 189.7
2019-03-10 15:00 | 221.57 | 216.95
2019-03-10 15:30 | 228.04 | 223.45
2019-03-10 16:00 | 229.09 | 224.42
2019-03-10 16:30 | 230.48 | 225.55
2019-03-10 17:00 | 232.13 | 227.31
2019-03-10 17:30 | 233.88 | 228.98
2019-03-10 18:00 | 235.69 | 230.47
2019-03-10 18:30 | 235.82 | 230.39
2019-03-10 19:00 | 235.59 | 230.18
2019-03-10 19:30 | 235.31 | 229.9
2019-03-10 20:00 | 233.79 | 228.44
2019-03-10 20:30 | 231.14 | 225.3
2019-03-10 21:00 | 227.79 | 221.44
2019-03-10 21:30 | 224.93 | 219.52
2019-03-10 22:00 | 221.34 | 216.55
2019-03-10 22:30 | 218.85 | 213.82
2019-03-10 23:00 | 217.31 | 212.04
2019-03-10 23:30 | 216.43 | 210.99
2019-03-11 | 215.4 | 209.58
2019-03-11 00:30 | 215.18 | 208.8
2019-03-11 01:00 | 214.39 | 208.04
2019-03-11 01:30 | 213.24 | 207.57
2019-03-11 02:00 | 213.08 | 207.31
2019-03-11 02:30 | 212.79 | 207
2019-03-11 03:00 | 212.27 | 206.54
2019-03-11 03:30 | 211.64 | 205.97
2019-03-11 04:00 | 211.06 | 205.36
2019-03-11 04:30 | 210.6 | 205.28
2019-03-11 05:00 | 210.94 | 205.77
2019-03-11 05:30 | 211.87 | 206.59
2019-03-11 06:00 | 214.39 | 207.82
2019-03-11 06:30 | 215.41 | 209.38
2019-03-11 07:00 | 216.6 | 210.71
2019-03-11 07:30 | 217.64 | 212.06
2019-03-11 08:00 | 217.91 | 212.62
2019-03-11 08:30 | 218.48 | 213.28
2019-03-11 09:00 | 219.03 | 213.95
2019-03-11 09:30 | 219.94 | 214.21
2019-03-11 10:00 | 220.92 | 215.21
2019-03-11 10:30 | 222.01 | 216.31
2019-03-11 11:00 | 223.62 | 218.02
2019-03-11 11:30 | 225.19 | 219.89
2019-03-11 12:00 | 226.71 | 221.67
2019-03-11 12:30 | 230.27 | 224.93
2019-03-11 13:00 | 242.2 | 236.97
2019-03-11 13:30 | 243.34 | 238.54
2019-03-11 14:00 | 244.26 | 239.94
2019-03-11 14:30 | 246.33 | 242.1
2019-03-11 15:00 | 246.76 | 242.5
2019-03-11 15:30 | 247.72 | 243.64
2019-03-11 16:00 | 249.31 | 245.29
2019-03-11 16:30 | 249.88 | 245.72
2019-03-11 17:00 | 250.6 | 246.46
2019-03-11 17:30 | 250.72 | 246.39
2019-03-11 18:00 | 251.84 | 247.5
2019-03-11 18:30 | 253.61 | 249.07
2019-03-11 19:00 | 254.56 | 250.19
2019-03-11 19:30 | 253.97 | 249.35
2019-03-11 20:00 | 250.82 | 245.68
2019-03-11 20:30 | 246.85 | 241.78
2019-03-11 21:00 | 242.96 | 237.75
2019-03-11 21:30 | 240.05 | 234.44
2019-03-11 22:00 | 237.16 | 230.97
2019-03-11 22:30 | 233.77 | 227.6
2019-03-11 23:00 | 230.61 | 225.17
2019-03-11 23:30 | 228.76 | 223.69
2019-03-12 | 226.91 | 221.74
2019-03-12 00:30 | 225.68 | 220.92
2019-03-12 01:00 | 224.42 | 219.51
2019-03-12 01:30 | 223.32 | 218.62
2019-03-12 02:00 | 206.54 | 201.89
2019-03-12 02:30 | 201.05 | 196.39
2019-03-12 03:00 | 200.35 | 195.76
2019-03-12 03:30 | 200.21 | 195.6
2019-03-12 04:00 | 200.19 | 195.68
2019-03-12 04:30 | 199.91 | 195.49
2019-03-12 05:00 | 200.46 | 196.12
2019-03-12 05:30 | 200.91 | 196.67
2019-03-12 06:00 | 202.21 | 198.29
2019-03-12 06:30 | 220.61 | 216.77
2019-03-12 07:00 | 226.32 | 222.45
2019-03-12 07:30 | 227.62 | 223.98
2019-03-12 08:00 | 228.05 | 224.75
2019-03-12 08:30 | 227.62 | 224.67
2019-03-12 09:00 | 228.98 | 226.04
2019-03-12 09:30 | 229.13 | 226.06
2019-03-12 10:00 | 229.31 | 226.32
2019-03-12 10:30 | 229.24 | 226.05
2019-03-12 11:00 | 231.35 | 228.07
2019-03-12 11:30 | 234.95 | 231.85
2019-03-12 12:00 | 236.31 | 233.41
2019-03-12 12:30 | 239.19 | 236.46
2019-03-12 13:00 | 240.73 | 238.08
2019-03-12 13:30 | 244.36 | 241.57
2019-03-12 14:00 | 247.22 | 244.59
2019-03-12 14:30 | 247.29 | 244.85
2019-03-12 15:00 | 245.22 | 242.58
2019-03-12 15:30 | 244.62 | 241.86
2019-03-12 16:00 | 245.44 | 242.61
2019-03-12 16:30 | 246 | 243.03
2019-03-12 17:00 | 248.08 | 245.04
2019-03-12 17:30 | 247.75 | 244.73
2019-03-12 18:00 | 209.67 | 207.48
2019-03-12 18:30 | 212.06 | 209.82
2019-03-12 19:00 | 213.01 | 210.74
2019-03-12 19:30 | 214.02 | 211.69
2019-03-12 20:00 | 216.75 | 214.47
2019-03-12 20:30 | 242.45 | 238.95
2019-03-12 21:00 | 246.01 | 241.62
2019-03-12 21:30 | 239.49 | 235.83
2019-03-12 22:00 | 235.38 | 231.46
2019-03-12 22:30 | 231.98 | 227.44
2019-03-12 23:00 | 229.55 | 224.87
2019-03-12 23:30 | 228.41 | 223.52
2019-03-13 | 225.97 | 221.18
2019-03-13 00:30 | 223.44 | 219.3
2019-03-13 01:00 | 222.32 | 218.28
2019-03-13 01:30 | 221.79 | 217.72
2019-03-13 02:00 | 220.93 | 217.28
2019-03-13 02:30 | 220.16 | 216.67
2019-03-13 03:00 | 218.93 | 215.45
2019-03-13 03:30 | 218.46 | 215
2019-03-13 04:00 | 218.17 | 214.72
2019-03-13 04:30 | 218.62 | 215.08
2019-03-13 05:00 | 218.97 | 215.24
2019-03-13 05:30 | 219.06 | 215.63
2019-03-13 06:00 | 219.86 | 216.7
2019-03-13 06:30 | 220.1 | 217.17
2019-03-13 07:00 | 221.07 | 218.29
2019-03-13 07:30 | 221.9 | 218.92
2019-03-13 08:00 | 221.88 | 219.44
2019-03-13 08:30 | 222.17 | 219.92
2019-03-13 09:00 | 221.55 | 219.31
2019-03-13 09:30 | 221.36 | 219.05
2019-03-13 10:00 | 222.33 | 219.76
2019-03-13 10:30 | 223.22 | 220.47
2019-03-13 11:00 | 225.25 | 222.26
2019-03-13 11:30 | 226.79 | 224.04
2019-03-13 12:00 | 228.38 | 225.58
2019-03-13 12:30 | 230.36 | 227.39
2019-03-13 13:00 | 232.16 | 229.17
2019-03-13 13:30 | 233.74 | 231.03
2019-03-13 14:00 | 236.09 | 233.69
2019-03-13 14:30 | 237.16 | 234.79
2019-03-13 15:00 | 240.35 | 238.09
2019-03-13 15:30 | 245.38 | 243.07
2019-03-13 16:00 | 250.19 | 248.04
2019-03-13 16:30 | 254.71 | 252.63
2019-03-13 17:00 | 255.78 | 253.64
2019-03-13 17:30 | 255.04 | 252.7
2019-03-13 18:00 | 255.21 | 252.85
2019-03-13 18:30 | 254.33 | 251.85
2019-03-13 19:00 | 252.38 | 250.03
2019-03-13 19:30 | 251.31 | 248.82
2019-03-13 20:00 | 239.44 | 236.74
2019-03-13 20:30 | 237.33 | 234.21
2019-03-13 21:00 | 233.61 | 230.51
2019-03-13 21:30 | 231.24 | 228.6
2019-03-13 22:00 | 226.97 | 224.66
2019-03-13 22:30 | 223.2 | 221.01
2019-03-13 23:00 | 220.73 | 218.43
2019-03-13 23:30 | 219.04 | 216.72
2019-03-14 | 216.88 | 214.57
2019-03-14 00:30 | 215.74 | 213.2
2019-03-14 01:00 | 213.97 | 211.3
2019-03-14 01:30 | 212.57 | 210.03
2019-03-14 02:00 | 211.71 | 209.29
2019-03-14 02:30 | 211.31 | 208.83
2019-03-14 03:00 | 210.78 | 208.34
2019-03-14 03:30 | 209.98 | 207.57
2019-03-14 04:00 | 209.88 | 207.42
2019-03-14 04:30 | 210.03 | 207.6
2019-03-14 05:00 | 210.8 | 208.41
2019-03-14 05:30 | 211.47 | 209.11
2019-03-14 06:00 | 212.96 | 210.48
2019-03-14 06:30 | 214.41 | 211.89
2019-03-14 07:00 | 216.01 | 213.11
2019-03-14 07:30 | 217.05 | 214.15
2019-03-14 08:00 | 218.08 | 215.5
2019-03-14 08:30 | 218.32 | 215.89
2019-03-14 09:00 | 217.74 | 215.32
2019-03-14 09:30 | 218.34 | 216
2019-03-14 10:00 | 221.92 | 219.72
2019-03-14 10:30 | 233.08 | 230.54
2019-03-14 11:00 | 232.07 | 229.7
2019-03-14 11:30 | 233.28 | 231.02
2019-03-14 12:00 | 233.78 | 231.61
2019-03-14 12:30 | 234.21 | 231.99
2019-03-14 13:00 | 238.16 | 235.88
2019-03-14 13:30 | 243.03 | 240.81
2019-03-14 14:00 | 245.58 | 243.43
2019-03-14 14:30 | 245.23 | 243.1
2019-03-14 15:00 | 207.8 | 205.14
2019-03-14 15:30 | 184.64 | 181.55
2019-03-14 16:00 | 174.37 | 171.69
2019-03-14 16:30 | 175.44 | 173.04
2019-03-14 17:00 | 204.09 | 201.47
2019-03-14 17:30 | 242.86 | 239.72
2019-03-14 18:00 | 249.9 | 246.32
2019-03-14 18:30 | 250.08 | 246.4
2019-03-14 19:00 | 250.93 | 247.13
2019-03-14 19:30 | 251.41 | 247.4
2019-03-14 20:00 | 249.33 | 245.33
2019-03-14 20:30 | 245.61 | 241.3
2019-03-14 21:00 | 241.89 | 238.48
2019-03-14 21:30 | 239.98 | 236.66
2019-03-14 22:00 | 237.34 | 234.01
2019-03-14 22:30 | 234.5 | 231.14
2019-03-14 23:00 | 232.44 | 229.47
2019-03-14 23:30 | 231.46 | 228.51
2019-03-15 | 229.07 | 226.18
2019-03-15 00:30 | 228.8 | 225.79
2019-03-15 01:00 | 227.04 | 224.25
2019-03-15 01:30 | 226.48 | 223.87
2019-03-15 02:00 | 225.91 | 223.16
2019-03-15 02:30 | 225.34 | 222.48
2019-03-15 03:00 | 224.98 | 222.06
2019-03-15 03:30 | 225.25 | 222.42
2019-03-15 04:00 | 224.55 | 221.72
2019-03-15 04:30 | 225.02 | 222.19
2019-03-15 05:00 | 225.93 | 223.04
2019-03-15 05:30 | 226.59 | 223.97
2019-03-15 06:00 | 227.33 | 224.75
2019-03-15 06:30 | 228.99 | 226.43
2019-03-15 07:00 | 230.43 | 227.88
2019-03-15 07:30 | 231.38 | 228.87
2019-03-15 08:00 | 231.93 | 229.6
2019-03-15 08:30 | 231.59 | 229.27
2019-03-15 09:00 | 231.4 | 229.1
2019-03-15 09:30 | 232.14 | 229.78
2019-03-15 10:00 | 232.55 | 230.21
2019-03-15 10:30 | 232.9 | 230.48
2019-03-15 11:00 | 233.88 | 231.49
2019-03-15 11:30 | 235.4 | 233.03
2019-03-15 12:00 | 236.71 | 234.45
2019-03-15 12:30 | 238.76 | 236.48
2019-03-15 13:00 | 241.1 | 238.75
2019-03-15 13:30 | 238.88 | 236.02
2019-03-15 14:00 | 238.27 | 235.45
2019-03-15 14:30 | 238.43 | 235.41
2019-03-15 15:00 | 237.64 | 234.66
2019-03-15 15:30 | 237.52 | 234.35
2019-03-15 16:00 | 238.01 | 234.56
2019-03-15 16:30 | 239.44 | 236.07
2019-03-15 17:00 | 240.9 | 237.51
2019-03-15 17:30 | 239.33 | 235.83
2019-03-15 18:00 | 240.13 | 236.58
2019-03-15 18:30 | 240.98 | 237
2019-03-15 19:00 | 242.83 | 238.98
2019-03-15 19:30 | 241.84 | 238.4
2019-03-15 20:00 | 240.17 | 236.72
2019-03-15 20:30 | 238.69 | 234.94
2019-03-15 21:00 | 237.11 | 233.25
2019-03-15 21:30 | 235.8 | 232.83
2019-03-15 22:00 | 234 | 230.74
2019-03-15 22:30 | 231.8 | 228.43
2019-03-15 23:00 | 230.28 | 227.17
2019-03-15 23:30 | 230.76 | 227.77
2019-03-16 | 213.7 | 210.56
2019-03-16 00:30 | 178.19 | 173.63
2019-03-16 01:00 | 165.17 | 159.35
2019-03-16 01:30 | 164.49 | 159.19
2019-03-16 02:00 | 163.74 | 158.79
2019-03-16 02:30 | 163.6 | 158.79
2019-03-16 03:00 | 163.34 | 158.49
2019-03-16 03:30 | 163.8 | 158.91
2019-03-16 04:00 | 163.82 | 158.82
2019-03-16 04:30 | 163.6 | 158.52
2019-03-16 05:00 | 164.14 | 159.38
2019-03-16 05:30 | 164.17 | 159.42
2019-03-16 06:00 | 165.05 | 159.75
2019-03-16 06:30 | 167.57 | 161.32
2019-03-16 07:00 | 167.3 | 162.05
2019-03-16 07:30 | 197.36 | 193.71
2019-03-16 08:00 | 224.98 | 221.84
2019-03-16 08:30 | 229.28 | 226.18
2019-03-16 09:00 | 229.79 | 226.23
2019-03-16 09:30 | 232.07 | 228.38
2019-03-16 10:00 | 219.02 | 215.52
2019-03-16 10:30 | 210.85 | 206.78
2019-03-16 11:00 | 211.11 | 207.29
2019-03-16 11:30 | 211.65 | 207.9
2019-03-16 12:00 | 211.62 | 207.82
2019-03-16 12:30 | 193.48 | 188.92
2019-03-16 13:00 | 183.06 | 178.21
2019-03-16 13:30 | 199.8 | 194.54
2019-03-16 14:00 | 210.83 | 205.49
2019-03-16 14:30 | 211.71 | 206.38
2019-03-16 15:00 | 212.91 | 207.64
2019-03-16 15:30 | 216.32 | 211.34
2019-03-16 16:00 | 218.84 | 214.32
2019-03-16 16:30 | 219.66 | 214.87
2019-03-16 17:00 | 219.39 | 214.68
2019-03-16 17:30 | 219.35 | 214.85
2019-03-16 18:00 | 219.45 | 214.7
2019-03-16 18:30 | 217.61 | 213.93
2019-03-16 19:00 | 218.35 | 214.64
2019-03-16 19:30 | 218.09 | 213.93
2019-03-16 20:00 | 217.09 | 212.78
2019-03-16 20:30 | 215.63 | 211.12
2019-03-16 21:00 | 213.64 | 209.41
2019-03-16 21:30 | 212.17 | 208.42
2019-03-16 22:00 | 210.6 | 206.64
2019-03-16 22:30 | 206.93 | 203.44
2019-03-16 23:00 | 205.94 | 202.52
2019-03-16 23:30 | 205.39 | 201.9
2019-03-17 | 204.48 | 200.95
2019-03-17 00:30 | 204.34 | 200.35
2019-03-17 01:00 | 202.65 | 199.1
2019-03-17 01:30 | 202.42 | 198.66
2019-03-17 02:00 | 201.88 | 198.01
2019-03-17 02:30 | 201.33 | 197.67
2019-03-17 03:00 | 200.82 | 197.18
2019-03-17 03:30 | 200.57 | 196.92
2019-03-17 04:00 | 200.61 | 197.04
2019-03-17 04:30 | 201.56 | 197.61
2019-03-17 05:00 | 202.28 | 198.13
2019-03-17 05:30 | 202.6 | 198
2019-03-17 06:00 | 202.03 | 197.69
2019-03-17 06:30 | 201.89 | 198.16
2019-03-17 07:00 | 202.02 | 198.26
2019-03-17 07:30 | 202.13 | 198.4
2019-03-17 08:00 | 202.83 | 198.42
2019-03-17 08:30 | 202.15 | 197.73
2019-03-17 09:00 | 201.99 | 197.31
2019-03-17 09:30 | 201.33 | 196.7
2019-03-17 10:00 | 200.65 | 196.54
2019-03-17 10:30 | 201.15 | 197.34
2019-03-17 11:00 | 201.74 | 197.99
2019-03-17 11:30 | 202.65 | 198.9
2019-03-17 12:00 | 203.57 | 199.89
2019-03-17 12:30 | 206.78 | 202.78
2019-03-17 13:00 | 207.51 | 203.57
2019-03-17 13:30 | 208.85 | 204.36
2019-03-17 14:00 | 213.56 | 208.95
2019-03-17 14:30 | 214.77 | 210.49
2019-03-17 15:00 | 215.29 | 211.12
2019-03-17 15:30 | 214.21 | 209.85
2019-03-17 16:00 | 215.64 | 211.22
2019-03-17 16:30 | 217.09 | 212.64
2019-03-17 17:00 | 218.82 | 214.17
2019-03-17 17:30 | 218.27 | 214.4
2019-03-17 18:00 | 217.89 | 214.67
2019-03-17 18:30 | 218.2 | 214.54
2019-03-17 19:00 | 218.4 | 214.72
2019-03-17 19:30 | 218.22 | 214.37
2019-03-17 20:00 | 216.75 | 212.81
2019-03-17 20:30 | 216.08 | 212.01
2019-03-17 21:00 | 214.13 | 209.5
2019-03-17 21:30 | 212.21 | 207.98
2019-03-17 22:00 | 210.06 | 206.24
2019-03-17 22:30 | 208.46 | 204.81
2019-03-17 23:00 | 206.68 | 203.19
2019-03-17 23:30 | 206.57 | 203.13
2019-03-18 | 206 | 202.49
2019-03-18 00:30 | 205.27 | 201.54
2019-03-18 01:00 | 203.85 | 199.95
2019-03-18 01:30 | 203.22 | 199.29
2019-03-18 02:00 | 203.24 | 199.21
2019-03-18 02:30 | 203.04 | 199.03
2019-03-18 03:00 | 203.02 | 198.9
2019-03-18 03:30 | 202.64 | 198.56
2019-03-18 04:00 | 202.58 | 198.58
2019-03-18 04:30 | 202.74 | 198.77
2019-03-18 05:00 | 203.28 | 199.25
2019-03-18 05:30 | 204.34 | 200.15
2019-03-18 06:00 | 205.75 | 201.81
2019-03-18 06:30 | 206.67 | 203.54
2019-03-18 07:00 | 206.85 | 203.71
2019-03-18 07:30 | 221.24 | 218.08
2019-03-18 08:00 | 229.74 | 226.33
2019-03-18 08:30 | 229.71 | 226.66
2019-03-18 09:00 | 229.43 | 226.35
2019-03-18 09:30 | 228.9 | 225.91
2019-03-18 10:00 | 229.59 | 226.64
2019-03-18 10:30 | 229.75 | 226.85
2019-03-18 11:00 | 230.83 | 227.55
2019-03-18 11:30 | 232.18 | 228.65
2019-03-18 12:00 | 233.33 | 229.95
2019-03-18 12:30 | 236.08 | 232.21
2019-03-18 13:00 | 234.11 | 230.77
2019-03-18 13:30 | 236.56 | 232.84
2019-03-18 14:00 | 238.22 | 234.45
2019-03-18 14:30 | 239.11 | 235.58
2019-03-18 15:00 | 240.15 | 236.57
2019-03-18 15:30 | 239.15 | 235.67
2019-03-18 16:00 | 240.46 | 237.08
2019-03-18 16:30 | 241.68 | 238.2
2019-03-18 17:00 | 244.55 | 241.1
2019-03-18 17:30 | 246.43 | 242.74
2019-03-18 18:00 | 247.97 | 244.25
2019-03-18 18:30 | 248.45 | 244.56
2019-03-18 19:00 | 249.31 | 245.85
2019-03-18 19:30 | 248.96 | 245.36
2019-03-18 20:00 | 246.18 | 242.66
2019-03-18 20:30 | 244.03 | 240.41
2019-03-18 21:00 | 241.77 | 237.6
2019-03-18 21:30 | 239.04 | 234.84
2019-03-18 22:00 | 236.25 | 232.34
2019-03-18 22:30 | 233.74 | 229.81
2019-03-18 23:00 | 231.82 | 227.85
2019-03-18 23:30 | 231.81 | 227.83
2019-03-19 | 229.79 | 226.5
2019-03-19 00:30 | 229 | 225.89
2019-03-19 01:00 | 228.82 | 225.66
2019-03-19 01:30 | 227.68 | 224.44
2019-03-19 02:00 | 227.1 | 223.83
2019-03-19 02:30 | 226.19 | 222.91
2019-03-19 03:00 | 226.24 | 222.94
2019-03-19 03:30 | 226.52 | 223.17
2019-03-19 04:00 | 226.26 | 222.91
2019-03-19 04:30 | 226.5 | 223.2
2019-03-19 05:00 | 227.19 | 223.92
2019-03-19 05:30 | 228.17 | 224.91
2019-03-19 06:00 | 229.25 | 226.21
2019-03-19 06:30 | 230.88 | 227.69
2019-03-19 07:00 | 231.78 | 228.72
2019-03-19 07:30 | 233.31 | 230.37
2019-03-19 08:00 | 232.69 | 229.88
2019-03-19 08:30 | 232.25 | 229.47
2019-03-19 09:00 | 232.47 | 229.69
2019-03-19 09:30 | 232.84 | 230.15
2019-03-19 10:00 | 234.29 | 231.58
2019-03-19 10:30 | 237.26 | 234.58
2019-03-19 11:00 | 237.65 | 235.02
2019-03-19 11:30 | 237.9 | 235.25
2019-03-19 12:00 | 238.43 | 235.75
2019-03-19 12:30 | 238.7 | 235.76
2019-03-19 13:00 | 238.99 | 235.75
2019-03-19 13:30 | 239.76 | 236.41
2019-03-19 14:00 | 241.71 | 238.31
2019-03-19 14:30 | 244.65 | 241.18
2019-03-19 15:00 | 245.34 | 241.44
2019-03-19 15:30 | 245.88 | 241.99
2019-03-19 16:00 | 247.84 | 244.02
2019-03-19 16:30 | 250.03 | 246.31
2019-03-19 17:00 | 251.12 | 247.36
2019-03-19 17:30 | 252.28 | 248.24
2019-03-19 18:00 | 253.7 | 249.54
2019-03-19 18:30 | 253.94 | 249.54
2019-03-19 19:00 | 253.84 | 249.46
2019-03-19 19:30 | 252.44 | 248.56
2019-03-19 20:00 | 249.73 | 246.39
2019-03-19 20:30 | 247.06 | 243.52
2019-03-19 21:00 | 243.89 | 239.98
2019-03-19 21:30 | 242.04 | 237.94
2019-03-19 22:00 | 238.86 | 234.98
2019-03-19 22:30 | 236.42 | 232.35
2019-03-19 23:00 | 234.39 | 230.34
2019-03-19 23:30 | 233.53 | 229.26
2019-03-20 | 231.25 | 227.11
2019-03-20 00:30 | 229.56 | 226.37
2019-03-20 01:00 | 228.46 | 225.28
2019-03-20 01:30 | 227.87 | 224.73
2019-03-20 02:00 | 227.72 | 224.49
2019-03-20 02:30 | 227.19 | 223.92
2019-03-20 03:00 | 226.47 | 223.18
2019-03-20 03:30 | 226.37 | 223.03
2019-03-20 04:00 | 226.04 | 222.71
2019-03-20 04:30 | 225.85 | 222.51
2019-03-20 05:00 | 226.37 | 223.08
2019-03-20 05:30 | 226.76 | 223.44
2019-03-20 06:00 | 226.86 | 223.61
2019-03-20 06:30 | 228.31 | 225.23
2019-03-20 07:00 | 229.94 | 226.79
2019-03-20 07:30 | 230.76 | 227.97
2019-03-20 08:00 | 231.45 | 228.66
2019-03-20 08:30 | 230.57 | 227.58
2019-03-20 09:00 | 231.7 | 228.7
2019-03-20 09:30 | 231.54 | 228.49
2019-03-20 10:00 | 232.58 | 229.62
2019-03-20 10:30 | 232.9 | 229.91
2019-03-20 11:00 | 235.53 | 232.6
2019-03-20 11:30 | 236.66 | 233.96
2019-03-20 12:00 | 239.04 | 236.41
2019-03-20 12:30 | 241 | 238.32
2019-03-20 13:00 | 241.87 | 239.12
2019-03-20 13:30 | 242.06 | 239.37
2019-03-20 14:00 | 244.41 | 241.67
2019-03-20 14:30 | 245.3 | 242.55
2019-03-20 15:00 | 246.36 | 243.63
2019-03-20 15:30 | 246.99 | 244.26
2019-03-20 16:00 | 249.13 | 246.5
2019-03-20 16:30 | 250.38 | 247.69
2019-03-20 17:00 | 252.25 | 249.63
2019-03-20 17:30 | 253.49 | 250.81
2019-03-20 18:00 | 254.77 | 252.07
2019-03-20 18:30 | 255.88 | 252.93
2019-03-20 19:00 | 256.61 | 253.54
2019-03-20 19:30 | 255.47 | 252.27
2019-03-20 20:00 | 252.53 | 249.08
2019-03-20 20:30 | 249.2 | 245.58
2019-03-20 21:00 | 245.92 | 242.07
2019-03-20 21:30 | 244.14 | 240.26
2019-03-20 22:00 | 241.42 | 237.35
2019-03-20 22:30 | 238.64 | 234.37
2019-03-20 23:00 | 236.52 | 232.05
2019-03-20 23:30 | 235.48 | 230.99
2019-03-21 | 233.49 | 229.1
2019-03-21 00:30 | 233.01 | 228.55
2019-03-21 01:00 | 232.24 | 227.87
2019-03-21 01:30 | 232.35 | 228
2019-03-21 02:00 | 231.95 | 227.51
2019-03-21 02:30 | 230.68 | 226.28
2019-03-21 03:00 | 231.36 | 226.93
2019-03-21 03:30 | 230.92 | 226.38
2019-03-21 04:00 | 230.81 | 226.19
2019-03-21 04:30 | 231.19 | 226.37
2019-03-21 05:00 | 231.68 | 226.79
2019-03-21 05:30 | 232.34 | 227.61
2019-03-21 06:00 | 233.96 | 229.47
2019-03-21 06:30 | 235.38 | 230.98
2019-03-21 07:00 | 236.84 | 232.59
2019-03-21 07:30 | 237.75 | 233.73
2019-03-21 08:00 | 237.75 | 234.03
2019-03-21 08:30 | 236.32 | 232.73
2019-03-21 09:00 | 236.87 | 233.35
2019-03-21 09:30 | 236.16 | 232.7
2019-03-21 10:00 | 236.62 | 233.34
2019-03-21 10:30 | 236.38 | 233.12
2019-03-21 11:00 | 237.73 | 234.68
2019-03-21 11:30 | 238.7 | 235.94
2019-03-21 12:00 | 240.81 | 238.01
2019-03-21 12:30 | 242.14 | 239.26
2019-03-21 13:00 | 244.68 | 241.58
2019-03-21 13:30 | 245.91 | 242.71
2019-03-21 14:00 | 247.63 | 244.28
2019-03-21 14:30 | 249.45 | 246.11
2019-03-21 15:00 | 249.94 | 246.5
2019-03-21 15:30 | 250.34 | 246.91
2019-03-21 16:00 | 252.61 | 249.29
2019-03-21 16:30 | 254.02 | 250.65
2019-03-21 17:00 | 255.32 | 251.88
2019-03-21 17:30 | 256.3 | 252.74
2019-03-21 18:00 | 257.67 | 254.14
2019-03-21 18:30 | 258.16 | 254.44
2019-03-21 19:00 | 259.32 | 255.68
2019-03-21 19:30 | 256.99 | 253.18
2019-03-21 20:00 | 254.03 | 249.97
2019-03-21 20:30 | 251.55 | 247.17
2019-03-21 21:00 | 248.58 | 243.76
2019-03-21 21:30 | 246.16 | 241.47
2019-03-21 22:00 | 242.24 | 237.73
2019-03-21 22:30 | 239.77 | 234.98
2019-03-21 23:00 | 237.83 | 232.96
2019-03-21 23:30 | 236.09 | 231.94
2019-03-22 | 234.47 | 230.82
2019-03-22 00:30 | 233.08 | 229.21
2019-03-22 01:00 | 232.5 | 228.61
2019-03-22 01:30 | 232.01 | 228.14
2019-03-22 02:00 | 231.54 | 227.67
2019-03-22 02:30 | 230.76 | 226.83
2019-03-22 03:00 | 229.93 | 226.01
2019-03-22 03:30 | 229.61 | 225.57
2019-03-22 04:00 | 229.51 | 225.4
2019-03-22 04:30 | 229.76 | 225.7
2019-03-22 05:00 | 230.75 | 226.75
2019-03-22 05:30 | 231.6 | 227.71
2019-03-22 06:00 | 232.39 | 228.59
2019-03-22 06:30 | 234.37 | 230.69
2019-03-22 07:00 | 233.77 | 229.93
2019-03-22 07:30 | 236.51 | 231.91
2019-03-22 08:00 | 237.43 | 232.54
2019-03-22 08:30 | 236.84 | 232.16
2019-03-22 09:00 | 237.11 | 232.33
2019-03-22 09:30 | 237.23 | 232.42
2019-03-22 10:00 | 237.93 | 233.17
2019-03-22 10:30 | 238.43 | 233.81
2019-03-22 11:00 | 238.96 | 234.4
2019-03-22 11:30 | 239.34 | 235.09
2019-03-22 12:00 | 240.42 | 236.54
2019-03-22 12:30 | 241.85 | 237.8
2019-03-22 13:00 | 243.38 | 239.36
2019-03-22 13:30 | 245.24 | 241.29
2019-03-22 14:00 | 246.74 | 243.13
2019-03-22 14:30 | 247.97 | 244.32
2019-03-22 15:00 | 248.79 | 245.19
2019-03-22 15:30 | 248.67 | 245.08
2019-03-22 16:00 | 251.4 | 247.84
2019-03-22 16:30 | 252.22 | 248.29
2019-03-22 17:00 | 252.69 | 248.21
2019-03-22 17:30 | 252.71 | 248.02
2019-03-22 18:00 | 251.91 | 248.45
2019-03-22 18:30 | 252.06 | 248.65
2019-03-22 19:00 | 252.98 | 249.56
2019-03-22 19:30 | 252.1 | 248.56
2019-03-22 20:00 | 250.02 | 246.26
2019-03-22 20:30 | 248.73 | 244.8
2019-03-22 21:00 | 245.74 | 241.73
2019-03-22 21:30 | 243.31 | 240.02
2019-03-22 22:00 | 241.33 | 237.99
2019-03-22 22:30 | 239.29 | 235.88
2019-03-22 23:00 | 237.35 | 234.17
2019-03-22 23:30 | 236.3 | 233.09
2019-03-23 | 234.57 | 231.32
2019-03-23 00:30 | 233.84 | 230.43
2019-03-23 01:00 | 216.2 | 212.84
2019-03-23 01:30 | 210.5 | 207.09
2019-03-23 02:00 | 210.47 | 206.84
2019-03-23 02:30 | 210.35 | 206.69
2019-03-23 03:00 | 209.84 | 206.2
2019-03-23 03:30 | 209.53 | 205.84
2019-03-23 04:00 | 209.18 | 205.43
2019-03-23 04:30 | 209.07 | 205.29
2019-03-23 05:00 | 209.26 | 205.55
2019-03-23 05:30 | 209.22 | 205.54
2019-03-23 06:00 | 209.96 | 206.22
2019-03-23 06:30 | 225.97 | 222.68
2019-03-23 07:00 | 230.97 | 227.75
2019-03-23 07:30 | 232.27 | 229.05
2019-03-23 08:00 | 232.48 | 229.39
2019-03-23 08:30 | 231.99 | 228.8
2019-03-23 09:00 | 232.16 | 229.02
2019-03-23 09:30 | 231.24 | 228.21
2019-03-23 10:00 | 231.22 | 228.29
2019-03-23 10:30 | 231.78 | 228.76
2019-03-23 11:00 | 232.72 | 229.5
2019-03-23 11:30 | 233.92 | 230.48
2019-03-23 12:00 | 235.4 | 232.06
2019-03-23 12:30 | 237.13 | 233.8
2019-03-23 13:00 | 238.05 | 234.77
2019-03-23 13:30 | 239.46 | 236.03
2019-03-23 14:00 | 240.8 | 237.68
2019-03-23 14:30 | 241.84 | 239.02
2019-03-23 15:00 | 243.09 | 240.41
2019-03-23 15:30 | 245.43 | 242.71
2019-03-23 16:00 | 247.01 | 244.28
2019-03-23 16:30 | 248.99 | 246.43
2019-03-23 17:00 | 250.48 | 247.95
2019-03-23 17:30 | 252.04 | 249.39
2019-03-23 18:00 | 253.2 | 250.49
2019-03-23 18:30 | 253.32 | 250.57
2019-03-23 19:00 | 253.78 | 251.07
2019-03-23 19:30 | 252.81 | 249.98
2019-03-23 20:00 | 250.6 | 247.71
2019-03-23 20:30 | 248.14 | 245.07
2019-03-23 21:00 | 245.94 | 242.57
2019-03-23 21:30 | 243.81 | 240.83
2019-03-23 22:00 | 241.8 | 238.72
2019-03-23 22:30 | 239.42 | 236.15
2019-03-23 23:00 | 237.93 | 234.65
2019-03-23 23:30 | 236.8 | 233.65
2019-03-24 | 235.11 | 232.02
2019-03-24 00:30 | 234.33 | 231.27
2019-03-24 01:00 | 232.92 | 229.84
2019-03-24 01:30 | 215.52 | 212.05
2019-03-24 02:00 | 210.53 | 206.85
2019-03-24 02:30 | 210.62 | 206.88
2019-03-24 03:00 | 210.05 | 206.16
2019-03-24 03:30 | 209.65 | 205.54
2019-03-24 04:00 | 209.78 | 205.58
2019-03-24 04:30 | 209.24 | 205.15
2019-03-24 05:00 | 208.44 | 204.71
2019-03-24 05:30 | 208.67 | 204.99
2019-03-24 06:00 | 209.62 | 205.83
2019-03-24 06:30 | 225.56 | 222.2
2019-03-24 07:00 | 229.94 | 226.68
2019-03-24 07:30 | 230.42 | 227.15
2019-03-24 08:00 | 230.77 | 227.54
2019-03-24 08:30 | 230.55 | 227.45
2019-03-24 09:00 | 230.7 | 227.62
2019-03-24 09:30 | 231.37 | 228.31
2019-03-24 10:00 | 231.52 | 228.58
2019-03-24 10:30 | 232.75 | 229.85
2019-03-24 11:00 | 235.83 | 232.76
2019-03-24 11:30 | 237.73 | 234.68
2019-03-24 12:00 | 238.98 | 235.5
2019-03-24 12:30 | 240.68 | 237.14
2019-03-24 13:00 | 241.88 | 238.66
2019-03-24 13:30 | 243.26 | 240.28
2019-03-24 14:00 | 244.47 | 241.38
2019-03-24 14:30 | 245.65 | 242.6
2019-03-24 15:00 | 247.36 | 244.31
2019-03-24 15:30 | 248.97 | 245.6
2019-03-24 16:00 | 251.44 | 247.99
2019-03-24 16:30 | 253.43 | 249.98
2019-03-24 17:00 | 254.64 | 251.2
2019-03-24 17:30 | 256.48 | 253
2019-03-24 18:00 | 258.03 | 254.57
2019-03-24 18:30 | 258.36 | 254.89
2019-03-24 19:00 | 259 | 255.59
2019-03-24 19:30 | 257.12 | 253.46
2019-03-24 20:00 | 254.38 | 250.42
2019-03-24 20:30 | 252.26 | 248
2019-03-24 21:00 | 248.81 | 245.03
2019-03-24 21:30 | 246.39 | 243.65
2019-03-24 22:00 | 242.99 | 240.15
2019-03-24 22:30 | 240.44 | 237.49
2019-03-24 23:00 | 238.34 | 235.26
2019-03-24 23:30 | 237.63 | 234.53
2019-03-25 | 235.75 | 232.59
2019-03-25 00:30 | 219.39 | 215.7
2019-03-25 01:00 | 213.07 | 209.19
2019-03-25 01:30 | 212.25 | 208.34
2019-03-25 02:00 | 211.57 | 207.72
2019-03-25 02:30 | 210.9 | 207.06
2019-03-25 03:00 | 210.02 | 206.17
2019-03-25 03:30 | 209.88 | 206.03
2019-03-25 04:00 | 209.35 | 205.47
2019-03-25 04:30 | 209.49 | 205.63
2019-03-25 05:00 | 209.93 | 206.17
2019-03-25 05:30 | 211.11 | 207.42
2019-03-25 06:00 | 212.37 | 208.87
2019-03-25 06:30 | 228.99 | 225.82
2019-03-25 07:00 | 235.39 | 232.36
2019-03-25 07:30 | 237.77 | 234.6
2019-03-25 08:00 | 238.29 | 235.32
2019-03-25 08:30 | 238.55 | 235.76
2019-03-25 09:00 | 238.54 | 235.77
2019-03-25 09:30 | 238.58 | 235.76
2019-03-25 10:00 | 239.02 | 236.27
2019-03-25 10:30 | 240.86 | 238.05
2019-03-25 11:00 | 239.26 | 236.3
2019-03-25 11:30 | 242.62 | 239.74
2019-03-25 12:00 | 244.43 | 241.49
2019-03-25 12:30 | 244.28 | 241.27
2019-03-25 13:00 | 245.41 | 242.38
2019-03-25 13:30 | 246.46 | 243.49
2019-03-25 14:00 | 247.11 | 244.24
2019-03-25 14:30 | 244.76 | 241.81
2019-03-25 15:00 | 245.74 | 242.77
2019-03-25 15:30 | 245.18 | 242.16
2019-03-25 16:00 | 245.74 | 242.66
2019-03-25 16:30 | 245.9 | 242.69
2019-03-25 17:00 | 245.42 | 242.3
2019-03-25 17:30 | 244.74 | 241.76
2019-03-25 18:00 | 244.77 | 241.89
2019-03-25 18:30 | 246.53 | 243.58
2019-03-25 19:00 | 249.51 | 246.67
2019-03-25 19:30 | 249.44 | 246.44
2019-03-25 20:00 | 247.47 | 244.42
2019-03-25 20:30 | 245.64 | 242.4
2019-03-25 21:00 | 243.18 | 239.83
2019-03-25 21:30 | 240.8 | 237.81
2019-03-25 22:00 | 237.51 | 234.57
2019-03-25 22:30 | 235.55 | 232.51
2019-03-25 23:00 | 234.02 | 230.89
2019-03-25 23:30 | 234.06 | 230.98
2019-03-26 | 232.51 | 229.37
2019-03-26 00:30 | 231.8 | 228.59
2019-03-26 01:00 | 230.88 | 227.6
2019-03-26 01:30 | 230.8 | 227.53
2019-03-26 02:00 | 230.63 | 227.41
2019-03-26 02:30 | 229.95 | 226.65
2019-03-26 03:00 | 229.71 | 226.39
2019-03-26 03:30 | 228.97 | 225.66
2019-03-26 04:00 | 229.1 | 225.78
2019-03-26 04:30 | 229.5 | 226.21
2019-03-26 05:00 | 230.31 | 227.02
2019-03-26 05:30 | 230.7 | 227.43
2019-03-26 06:00 | 231.35 | 228.1
2019-03-26 06:30 | 233.58 | 230.25
2019-03-26 07:00 | 234.59 | 231.36
2019-03-26 07:30 | 236.24 | 232.98
2019-03-26 08:00 | 235.15 | 231.86
2019-03-26 08:30 | 235.37 | 231.93
2019-03-26 09:00 | 233.52 | 230.06
2019-03-26 09:30 | 232.63 | 228.98
2019-03-26 10:00 | 232.27 | 228.61
2019-03-26 10:30 | 230.45 | 226.93
2019-03-26 11:00 | 229.53 | 226.13
2019-03-26 11:30 | 230.37 | 226.95
2019-03-26 12:00 | 230.46 | 227
2019-03-26 12:30 | 231.11 | 227.51
2019-03-26 13:00 | 231.38 | 227.86
2019-03-26 13:30 | 232.01 | 228.53
2019-03-26 14:00 | 233.35 | 229.75
2019-03-26 14:30 | 232.81 | 228.96
2019-03-26 15:00 | 231.83 | 227.83
2019-03-26 15:30 | 231.84 | 227.69
2019-03-26 16:00 | 231.75 | 227.7
2019-03-26 16:30 | 231.09 | 227.27
2019-03-26 17:00 | 231.8 | 227.78
2019-03-26 17:30 | 231.82 | 228.1
2019-03-26 18:00 | 232.91 | 229
2019-03-26 18:30 | 233.81 | 230.03
2019-03-26 19:00 | 236.34 | 232.83
2019-03-26 19:30 | 235.24 | 231.66
2019-03-26 20:00 | 234.94 | 231.21
2019-03-26 20:30 | 234.2 | 230.33
2019-03-26 21:00 | 232.92 | 228.93
2019-03-26 21:30 | 231.15 | 227.76
2019-03-26 22:00 | 229.09 | 225.68
2019-03-26 22:30 | 226.25 | 222.78
2019-03-26 23:00 | 226.1 | 222.49
2019-03-26 23:30 | 226.21 | 222.75
2019-03-27 | 225.46 | 221.88
2019-03-27 00:30 | 225.35 | 221.54
2019-03-27 01:00 | 224.41 | 220.78
2019-03-27 01:30 | 223.3 | 219.68
2019-03-27 02:00 | 222.93 | 219.29
2019-03-27 02:30 | 223.01 | 219.36
2019-03-27 03:00 | 222.88 | 219.21
2019-03-27 03:30 | 223.35 | 219.64
2019-03-27 04:00 | 223.63 | 219.85
2019-03-27 04:30 | 224.67 | 221
2019-03-27 05:00 | 225.65 | 222.08
2019-03-27 05:30 | 226.23 | 222.1
2019-03-27 06:00 | 226.62 | 222.17
2019-03-27 06:30 | 228.06 | 223.26
2019-03-27 07:00 | 228.51 | 223.62
2019-03-27 07:30 | 228.9 | 224.12
2019-03-27 08:00 | 229.69 | 224.84
2019-03-27 08:30 | 229.32 | 224.42
2019-03-27 09:00 | 228.79 | 223.91
2019-03-27 09:30 | 228.51 | 223.57
2019-03-27 10:00 | 228.78 | 223.83
2019-03-27 10:30 | 228.46 | 223.36
2019-03-27 11:00 | 227.92 | 222.95
2019-03-27 11:30 | 227.71 | 222.67
2019-03-27 12:00 | 227.65 | 222.63
2019-03-27 12:30 | 226.81 | 221.91
2019-03-27 13:00 | 228.56 | 223.7
2019-03-27 13:30 | 232.94 | 227.86
2019-03-27 14:00 | 227.29 | 222.36
2019-03-27 14:30 | 221.61 | 216.79
2019-03-27 15:00 | 230.23 | 225.22
2019-03-27 15:30 | 231.3 | 226.41
2019-03-27 16:00 | 229.93 | 225.15
2019-03-27 16:30 | 230.48 | 225.78
2019-03-27 17:00 | 230.98 | 226.26
2019-03-27 17:30 | 232.14 | 227.35
2019-03-27 18:00 | 233.94 | 229.18
2019-03-27 18:30 | 236.25 | 231.42
2019-03-27 19:00 | 237.59 | 232.74
2019-03-27 19:30 | 236.48 | 232.11
2019-03-27 20:00 | 234.63 | 230.18
2019-03-27 20:30 | 233.29 | 228.54
2019-03-27 21:00 | 231.59 | 227.14
2019-03-27 21:30 | 230.88 | 226.73
2019-03-27 22:00 | 229.47 | 225.4
2019-03-27 22:30 | 227.46 | 223.32
2019-03-27 23:00 | 226.3 | 222.34
2019-03-27 23:30 | 225.63 | 221.52
2019-03-28 | 224.52 | 220.3
2019-03-28 00:30 | 224.97 | 221.1
2019-03-28 01:00 | 222.81 | 219.05
2019-03-28 01:30 | 222.48 | 218.63
2019-03-28 02:00 | 221.95 | 217.76
2019-03-28 02:30 | 222.16 | 217.93
2019-03-28 03:00 | 222.57 | 218.64
2019-03-28 03:30 | 223.38 | 219.37
2019-03-28 04:00 | 223.13 | 219.17
2019-03-28 04:30 | 223.4 | 219.52
2019-03-28 05:00 | 223.34 | 219.44
2019-03-28 05:30 | 224.07 | 219.98
2019-03-28 06:00 | 226.67 | 221.98
2019-03-28 06:30 | 228.79 | 223.09
2019-03-28 07:00 | 229.77 | 223.8
2019-03-28 07:30 | 228.95 | 223.72
2019-03-28 08:00 | 229.38 | 224.51
2019-03-28 08:30 | 228.75 | 224.01
2019-03-28 09:00 | 227.67 | 223.09
2019-03-28 09:30 | 227.37 | 222.75
2019-03-28 10:00 | 227.01 | 222.62
2019-03-28 10:30 | 225.97 | 221.72
2019-03-28 11:00 | 225.75 | 221.38
2019-03-28 11:30 | 227.41 | 223
2019-03-28 12:00 | 227.68 | 223.18
2019-03-28 12:30 | 227.19 | 222.64
2019-03-28 13:00 | 228.37 | 223.9
2019-03-28 13:30 | 228.9 | 224.29
2019-03-28 14:00 | 228.55 | 224.02
2019-03-28 14:30 | 228.5 | 224.15
2019-03-28 15:00 | 228.97 | 224.62
2019-03-28 15:30 | 229.57 | 225.27
2019-03-28 16:00 | 229.82 | 225.58
2019-03-28 16:30 | 229.45 | 225.14
2019-03-28 17:00 | 230.31 | 225.93
2019-03-28 17:30 | 230.16 | 225.55
2019-03-28 18:00 | 231.41 | 226.59
2019-03-28 18:30 | 233.32 | 228.5
2019-03-28 19:00 | 234.62 | 229.95
2019-03-28 19:30 | 234.39 | 229.44
2019-03-28 20:00 | 234.09 | 229.15
2019-03-28 20:30 | 233.03 | 227.81
2019-03-28 21:00 | 232.43 | 226.75
2019-03-28 21:30 | 231.57 | 226.15
2019-03-28 22:00 | 230.69 | 225.45
2019-03-28 22:30 | 229.42 | 224.22
2019-03-28 23:00 | 227.15 | 222.42
2019-03-28 23:30 | 225.48 | 221.66
2019-03-29 | 224.28 | 220.48
2019-03-29 00:30 | 223.81 | 220.08
2019-03-29 01:00 | 223.37 | 219.17
2019-03-29 01:30 | 222.98 | 218.66
2019-03-29 02:00 | 222.74 | 218.14
2019-03-29 02:30 | 222.87 | 218.25
2019-03-29 03:00 | 222.93 | 218.17
2019-03-29 03:30 | 222.66 | 217.99
2019-03-29 04:00 | 222.7 | 218.09
2019-03-29 04:30 | 223.36 | 218.76
2019-03-29 05:00 | 223.9 | 219.2
2019-03-29 05:30 | 225.87 | 220.23
2019-03-29 06:00 | 227.75 | 221.66
2019-03-29 06:30 | 228.65 | 222.81
2019-03-29 07:00 | 227.62 | 221.76
2019-03-29 07:30 | 213.1 | 207.18
2019-03-29 08:00 | 213.27 | 207.34
2019-03-29 08:30 | 222.58 | 216.51
2019-03-29 09:00 | 226.36 | 220.5
2019-03-29 09:30 | 225.15 | 219.3
2019-03-29 10:00 | 224.18 | 218.58
2019-03-29 10:30 | 223.84 | 218.47
2019-03-29 11:00 | 226.99 | 221.67
2019-03-29 11:30 | 228.73 | 223.08
2019-03-29 12:00 | 228.78 | 223.35
2019-03-29 12:30 | 228.49 | 223.17
2019-03-29 13:00 | 227.38 | 222.17
2019-03-29 13:30 | 226.18 | 221.01
2019-03-29 14:00 | 227.11 | 221.85
2019-03-29 14:30 | 227.5 | 221.95
2019-03-29 15:00 | 227.84 | 222.51
2019-03-29 15:30 | 228.17 | 222.95
2019-03-29 16:00 | 232.41 | 227.83
2019-03-29 16:30 | 231.55 | 226.99
2019-03-29 17:00 | 232.29 | 227.79
2019-03-29 17:30 | 233.02 | 228.16
2019-03-29 18:00 | 234.33 | 229.21
2019-03-29 18:30 | 235.45 | 230.31
2019-03-29 19:00 | 237.21 | 232.04
2019-03-29 19:30 | 236.46 | 231.06
2019-03-29 20:00 | 235.57 | 230.05
2019-03-29 20:30 | 233.1 | 228.19
2019-03-29 21:00 | 230.74 | 226.14
2019-03-29 21:30 | 229.82 | 225.56
2019-03-29 22:00 | 230.28 | 226.05
2019-03-29 22:30 | 229.02 | 224.8
2019-03-29 23:00 | 227.75 | 223.53
2019-03-29 23:30 | 227.89 | 223.51
2019-03-30 | 226.97 | 222.47
2019-03-30 00:30 | 227.86 | 223.4
2019-03-30 01:00 | 226.97 | 222.91
2019-03-30 01:30 | 225.67 | 222.15
2019-03-30 02:00 | 225.6 | 222.08
2019-03-30 02:30 | 225.46 | 221.94
2019-03-30 03:00 | 225.45 | 221.94
2019-03-30 03:30 | 224.99 | 221.46
2019-03-30 04:00 | 224.47 | 220.91
2019-03-30 04:30 | 221.89 | 218.3
2019-03-30 05:00 | 222.52 | 218.95
2019-03-30 05:30 | 223.38 | 219.83
2019-03-30 06:00 | 224.15 | 220.6
2019-03-30 06:30 | 223.86 | 220.36
2019-03-30 07:00 | 225.15 | 221.58
2019-03-30 07:30 | 224.17 | 220.64
2019-03-30 08:00 | 224.61 | 221.16
2019-03-30 08:30 | 224.96 | 221.02
2019-03-30 09:00 | 225 | 220.74
2019-03-30 09:30 | 225.08 | 220.17
2019-03-30 10:00 | 224.55 | 219.51
2019-03-30 10:30 | 223.45 | 218.36
2019-03-30 11:00 | 221.69 | 216.33
2019-03-30 11:30 | 222.03 | 216.62
2019-03-30 12:00 | 220.36 | 215.08
2019-03-30 12:30 | 219.63 | 214.35
2019-03-30 13:00 | 220.3 | 215.13
2019-03-30 13:30 | 220.59 | 215.48
2019-03-30 14:00 | 220.25 | 215.16
2019-03-30 14:30 | 220.76 | 215.66
2019-03-30 15:00 | 221.47 | 216.35
2019-03-30 15:30 | 221.03 | 215.99
2019-03-30 16:00 | 222.13 | 216.84
2019-03-30 16:30 | 223.74 | 218.5
2019-03-30 17:00 | 225.66 | 220.55
2019-03-30 17:30 | 228.68 | 223.43
2019-03-30 18:00 | 231.12 | 225.65
2019-03-30 18:30 | 232.26 | 226.8
2019-03-30 19:00 | 233.56 | 228.12
2019-03-30 19:30 | 232.66 | 227.17
2019-03-30 20:00 | 231.8 | 226.19
2019-03-30 20:30 | 229.49 | 225.17
2019-03-30 21:00 | 228.2 | 224.16
2019-03-30 21:30 | 227.11 | 223.58
2019-03-30 22:00 | 226.17 | 222.7
2019-03-30 22:30 | 225.04 | 221.54
2019-03-30 23:00 | 223.75 | 220.19
2019-03-30 23:30 | 224.35 | 220.77
2019-03-31 | 223.46 | 219.93
2019-03-31 00:30 | 223.12 | 219.56
2019-03-31 01:00 | 222.74 | 219.13
2019-03-31 01:30 | 222.39 | 218.77
2019-03-31 02:00 | 221.49 | 218.03
2019-03-31 02:30 | 221.72 | 218.27
2019-03-31 03:00 | 221.62 | 218.17
2019-03-31 03:30 | 221.65 | 218.22
2019-03-31 04:00 | 220.87 | 217.32
2019-03-31 04:30 | 221.83 | 218.26
2019-03-31 05:00 | 221.5 | 217.96
2019-03-31 05:30 | 223.27 | 219.77
2019-03-31 06:00 | 223.34 | 219.86
2019-03-31 06:30 | 224.29 | 220.8
2019-03-31 07:00 | 225.23 | 221.68
2019-03-31 07:30 | 224.28 | 220.7
2019-03-31 08:00 | 224.21 | 220.59
2019-03-31 08:30 | 221.66 | 218.26
2019-03-31 09:00 | 220.42 | 216.93
2019-03-31 09:30 | 218.41 | 214.2
2019-03-31 10:00 | 217.84 | 212.88
2019-03-31 10:30 | 217.49 | 212.55
2019-03-31 11:00 | 217.56 | 212.52
2019-03-31 11:30 | 217.46 | 212.27
2019-03-31 12:00 | 218.02 | 212.66
2019-03-31 12:30 | 218.54 | 213.33
2019-03-31 13:00 | 218.82 | 213.55
2019-03-31 13:30 | 219.92 | 214.84
2019-03-31 14:00 | 219.3 | 214.25
2019-03-31 14:30 | 219.58 | 214.45
2019-03-31 15:00 | 220.26 | 214.87
2019-03-31 15:30 | 221.5 | 216.11
2019-03-31 16:00 | 222.7 | 217.24
2019-03-31 16:30 | 225.16 | 219.89
2019-03-31 17:00 | 227.06 | 221.9
2019-03-31 17:30 | 230.01 | 224.61
2019-03-31 18:00 | 229.18 | 224.13
2019-03-31 18:30 | 229.42 | 224.25
2019-03-31 19:00 | 230.67 | 225.46
2019-03-31 19:30 | 230.4 | 225.17
2019-03-31 20:00 | 229.06 | 223.65
2019-03-31 20:30 | 227.24 | 222.21
2019-03-31 21:00 | 226.35 | 221.55
2019-03-31 21:30 | 225.75 | 220.89
2019-03-31 22:00 | 224.52 | 219.76
2019-03-31 22:30 | 223.16 | 218.51
2019-03-31 23:00 | 221.34 | 216.82
2019-03-31 23:30 | 220.56 | 216.45
2019-04-01 | 219.22 | 215.2
2019-04-01 00:30 | 218.63 | 214.81
2019-04-01 01:00 | 218.61 | 214.81
2019-04-01 01:30 | 217.66 | 213.87
2019-04-01 02:00 | 217.42 | 213.62
2019-04-01 02:30 | 218 | 214.04
2019-04-01 03:00 | 217.21 | 213.21
2019-04-01 03:30 | 217.23 | 213.26
2019-04-01 04:00 | 217.02 | 213.06
2019-04-01 04:30 | 217.87 | 214.11
2019-04-01 05:00 | 218.69 | 214.95
2019-04-01 05:30 | 219.34 | 215.58
2019-04-01 06:00 | 222.33 | 218.02
2019-04-01 06:30 | 225.03 | 220.67
2019-04-01 07:00 | 225.19 | 221.37
2019-04-01 07:30 | 226.95 | 223.12
2019-04-01 08:00 | 227.04 | 223.04
2019-04-01 08:30 | 220.49 | 216.84
2019-04-01 09:00 | 202.55 | 199.12
2019-04-01 09:30 | 200.75 | 196.77
2019-04-01 10:00 | 200.11 | 196.33
2019-04-01 10:30 | 211.09 | 207.11
2019-04-01 11:00 | 213.53 | 209.87
2019-04-01 11:30 | 216.98 | 213.28
2019-04-01 12:00 | 217.93 | 213.79
2019-04-01 12:30 | 216.62 | 212.32
2019-04-01 13:00 | 215.62 | 211.1
2019-04-01 13:30 | 216.59 | 211.14
2019-04-01 14:00 | 217.26 | 212.06
2019-04-01 14:30 | 218.54 | 213.41
2019-04-01 15:00 | 219.47 | 214.01
2019-04-01 15:30 | 221.24 | 215.32
2019-04-01 16:00 | 221.95 | 216.01
2019-04-01 16:30 | 223.46 | 217.52
2019-04-01 17:00 | 224.86 | 219.22
2019-04-01 17:30 | 226.82 | 221.13
2019-04-01 18:00 | 229.3 | 223.26
2019-04-01 18:30 | 231.99 | 226.8
2019-04-01 19:00 | 234.51 | 229.81
2019-04-01 19:30 | 234.49 | 229.52
2019-04-01 20:00 | 232.73 | 227.7
2019-04-01 20:30 | 230.94 | 226.19
2019-04-01 21:00 | 229.27 | 224.39
2019-04-01 21:30 | 228.4 | 224.15
2019-04-01 22:00 | 226.66 | 223.07
2019-04-01 22:30 | 225.31 | 221.62
2019-04-01 23:00 | 223.78 | 220.2
2019-04-01 23:30 | 223.42 | 219.57
2019-04-02 | 222.03 | 218.32
2019-04-02 00:30 | 220.84 | 217.17
2019-04-02 01:00 | 220.42 | 216.72
2019-04-02 01:30 | 220.22 | 216.54
2019-04-02 02:00 | 219.84 | 216.13
2019-04-02 02:30 | 219.73 | 216.01
2019-04-02 03:00 | 219.88 | 216.13
2019-04-02 03:30 | 220.52 | 216.77
2019-04-02 04:00 | 220.23 | 216.42
2019-04-02 04:30 | 220.71 | 216.94
2019-04-02 05:00 | 220.98 | 217.31
2019-04-02 05:30 | 222.42 | 218.76
2019-04-02 06:00 | 224.19 | 220.57
2019-04-02 06:30 | 226.64 | 222.54
2019-04-02 07:00 | 228.09 | 223.49
2019-04-02 07:30 | 227.57 | 222.24
2019-04-02 08:00 | 226.9 | 221.08
2019-04-02 08:30 | 224.55 | 219.09
2019-04-02 09:00 | 223.67 | 218.11
2019-04-02 09:30 | 222.83 | 216.84
2019-04-02 10:00 | 222.15 | 216.02
2019-04-02 10:30 | 221.36 | 215.23
2019-04-02 11:00 | 221.15 | 215.19
2019-04-02 11:30 | 220.96 | 214.97
2019-04-02 12:00 | 221.46 | 215.54
2019-04-02 12:30 | 221.17 | 214.87
2019-04-02 13:00 | 221.21 | 216.35
2019-04-02 13:30 | 222.25 | 217.46
2019-04-02 14:00 | 222.57 | 218.24
2019-04-02 14:30 | 223.13 | 218.79
2019-04-02 15:00 | 224.04 | 219.55
2019-04-02 15:30 | 225.7 | 221.13
2019-04-02 16:00 | 226.64 | 222.13
2019-04-02 16:30 | 227.9 | 223.41
2019-04-02 17:00 | 229.11 | 224.81
2019-04-02 17:30 | 231.43 | 226.95
2019-04-02 18:00 | 233.88 | 229.3
2019-04-02 18:30 | 236.98 | 232.3
2019-04-02 19:00 | 239.44 | 234.66
2019-04-02 19:30 | 238.73 | 233.85
2019-04-02 20:00 | 236.37 | 231.34
2019-04-02 20:30 | 234.9 | 229.69
2019-04-02 21:00 | 233.85 | 228.63
2019-04-02 21:30 | 232.8 | 228.37
2019-04-02 22:00 | 231.08 | 227.1
2019-04-02 22:30 | 229.41 | 225.44
2019-04-02 23:00 | 228.04 | 223.58
2019-04-02 23:30 | 227.86 | 223.53
2019-04-03 | 226.29 | 222.42
2019-04-03 00:30 | 225.34 | 221.46
2019-04-03 01:00 | 224.16 | 220.19
2019-04-03 01:30 | 223.08 | 219.2
2019-04-03 02:00 | 222.72 | 218.77
2019-04-03 02:30 | 222.58 | 218.64
2019-04-03 03:00 | 222.27 | 218.39
2019-04-03 03:30 | 222.34 | 218.44
2019-04-03 04:00 | 222.21 | 218.27
2019-04-03 04:30 | 222.94 | 218.99
2019-04-03 05:00 | 223.79 | 219.88
2019-04-03 05:30 | 225.2 | 221.37
2019-04-03 06:00 | 226.3 | 222.66
2019-04-03 06:30 | 230.14 | 225.55
2019-04-03 07:00 | 231.84 | 226.59
2019-04-03 07:30 | 230.01 | 225.33
2019-04-03 08:00 | 228.91 | 224.55
2019-04-03 08:30 | 226.86 | 221.97
2019-04-03 09:00 | 225.17 | 220.09
2019-04-03 09:30 | 223.66 | 218.48
2019-04-03 10:00 | 223.16 | 217.81
2019-04-03 10:30 | 222.44 | 216.91
2019-04-03 11:00 | 222.01 | 216.4
2019-04-03 11:30 | 222.23 | 216.8
2019-04-03 12:00 | 222.34 | 217.22
2019-04-03 12:30 | 221.7 | 216.95
2019-04-03 13:00 | 221.68 | 216.86
2019-04-03 13:30 | 222.5 | 217.66
2019-04-03 14:00 | 223.69 | 218.91
2019-04-03 14:30 | 225.49 | 220.45
2019-04-03 15:00 | 225.06 | 220.41
2019-04-03 15:30 | 227.32 | 222.68
2019-04-03 16:00 | 227.97 | 223.09
2019-04-03 16:30 | 229.09 | 224.27
2019-04-03 17:00 | 230.32 | 225.86
2019-04-03 17:30 | 231.82 | 227.1
2019-04-03 18:00 | 233.57 | 228.15
2019-04-03 18:30 | 236.58 | 231.08
2019-04-03 19:00 | 239.03 | 234.76
2019-04-03 19:30 | 238.58 | 234.32
2019-04-03 20:00 | 237.11 | 232.92
2019-04-03 20:30 | 235.4 | 230.93
2019-04-03 21:00 | 233.89 | 229.15
2019-04-03 21:30 | 232.57 | 228.29
2019-04-03 22:00 | 231.55 | 227.34
2019-04-03 22:30 | 229.29 | 225.35
2019-04-03 23:00 | 227.66 | 223.68
2019-04-03 23:30 | 227.07 | 222.97
2019-04-04 | 225.04 | 221.34
2019-04-04 00:30 | 225.13 | 221.3
2019-04-04 01:00 | 223.87 | 220.19
2019-04-04 01:30 | 223.65 | 219.96
2019-04-04 02:00 | 223.03 | 219.25
2019-04-04 02:30 | 221.09 | 216.9
2019-04-04 03:00 | 221.73 | 217.48
2019-04-04 03:30 | 222.36 | 218.18
2019-04-04 04:00 | 222.54 | 218.29
2019-04-04 04:30 | 223.55 | 219.19
2019-04-04 05:00 | 224.31 | 219.85
2019-04-04 05:30 | 225.44 | 220.99
2019-04-04 06:00 | 227.08 | 221.7
2019-04-04 06:30 | 229.76 | 224.48
2019-04-04 07:00 | 230.37 | 225.13
2019-04-04 07:30 | 228.57 | 223.33
2019-04-04 08:00 | 226.98 | 221.63
2019-04-04 08:30 | 226.08 | 220.86
2019-04-04 09:00 | 224.85 | 219.69
2019-04-04 09:30 | 223.69 | 218.92
2019-04-04 10:00 | 223.29 | 218.92
2019-04-04 10:30 | 221.62 | 216.67
2019-04-04 11:00 | 221.47 | 216.45
2019-04-04 11:30 | 221.51 | 216.37
2019-04-04 12:00 | 222.37 | 217.36
2019-04-04 12:30 | 222.97 | 217.86
2019-04-04 13:00 | 223.11 | 218.29
2019-04-04 13:30 | 222.83 | 218.24
2019-04-04 14:00 | 224.61 | 219.4
2019-04-04 14:30 | 225.39 | 219.85
2019-04-04 15:00 | 225.22 | 219.47
2019-04-04 15:30 | 226.91 | 221.22
2019-04-04 16:00 | 227.85 | 222.38
2019-04-04 16:30 | 227.66 | 223.27
2019-04-04 17:00 | 228.05 | 224.47
2019-04-04 17:30 | 230.28 | 226.38
2019-04-04 18:00 | 231.13 | 227.99
2019-04-04 18:30 | 235.4 | 232.29
2019-04-04 19:00 | 238.23 | 235
2019-04-04 19:30 | 238.78 | 235.55
2019-04-04 20:00 | 237.14 | 233.73
2019-04-04 20:30 | 236.4 | 232.63
2019-04-04 21:00 | 235.3 | 231.37
2019-04-04 21:30 | 234.12 | 230.57
2019-04-04 22:00 | 232.63 | 229.16
2019-04-04 22:30 | 230.18 | 226.86
2019-04-04 23:00 | 228.64 | 225.18
2019-04-04 23:30 | 228.21 | 224.81
2019-04-05 | 226.77 | 223.21
2019-04-05 00:30 | 226.05 | 222.34
2019-04-05 01:00 | 225.45 | 221.68
2019-04-05 01:30 | 224.45 | 220.71
2019-04-05 02:00 | 223.96 | 220.39
2019-04-05 02:30 | 223.33 | 219.72
2019-04-05 03:00 | 223.44 | 219.82
2019-04-05 03:30 | 223.29 | 219.67
2019-04-05 04:00 | 223.64 | 220.03
2019-04-05 04:30 | 223.84 | 220.22
2019-04-05 05:00 | 224.15 | 220.56
2019-04-05 05:30 | 224.18 | 220.67
2019-04-05 06:00 | 224.85 | 221.41
2019-04-05 06:30 | 227.48 | 223.55
2019-04-05 07:00 | 228.88 | 224.18
2019-04-05 07:30 | 227.78 | 222.7
2019-04-05 08:00 | 227.08 | 222.01
2019-04-05 08:30 | 225.56 | 220.41
2019-04-05 09:00 | 225.16 | 220.32
2019-04-05 09:30 | 224.32 | 219.53
2019-04-05 10:00 | 223.42 | 219.01
2019-04-05 10:30 | 222.77 | 218.33
2019-04-05 11:00 | 222.19 | 217.8
2019-04-05 11:30 | 222.79 | 218.22
2019-04-05 12:00 | 223.04 | 218.13
2019-04-05 12:30 | 223.7 | 218.57
2019-04-05 13:00 | 223.66 | 218.69
2019-04-05 13:30 | 222.61 | 217.91
2019-04-05 14:00 | 222.74 | 217.96
2019-04-05 14:30 | 222.9 | 218.3
2019-04-05 15:00 | 223.9 | 219.41
2019-04-05 15:30 | 224.84 | 220.14
2019-04-05 16:00 | 225.81 | 221.33
2019-04-05 16:30 | 228.26 | 223.72
2019-04-05 17:00 | 229.11 | 224.22
2019-04-05 17:30 | 231.74 | 226.75
2019-04-05 18:00 | 232.69 | 227.45
2019-04-05 18:30 | 234.23 | 228.61
2019-04-05 19:00 | 236.48 | 230.95
2019-04-05 19:30 | 235.98 | 230.39
2019-04-05 20:00 | 234.81 | 228.96
2019-04-05 20:30 | 234.66 | 228.87
2019-04-05 21:00 | 232.78 | 226.64
2019-04-05 21:30 | 231.61 | 226.67
2019-04-05 22:00 | 230.99 | 226.37
2019-04-05 22:30 | 229.99 | 225.19
2019-04-05 23:00 | 228.49 | 223.91
2019-04-05 23:30 | 227.19 | 223.03
2019-04-06 | 225.77 | 222.13
2019-04-06 00:30 | 225.12 | 221.56
2019-04-06 01:00 | 224.79 | 220.86
2019-04-06 01:30 | 224.44 | 220.73
2019-04-06 02:00 | 223.73 | 220.1
2019-04-06 02:30 | 223.33 | 219.54
2019-04-06 03:00 | 223.01 | 219.26
2019-04-06 03:30 | 222.72 | 219.08
2019-04-06 04:00 | 222.14 | 218.5
2019-04-06 04:30 | 222.49 | 218.73
2019-04-06 05:00 | 222.77 | 219.01
2019-04-06 05:30 | 223.46 | 219.63
2019-04-06 06:00 | 224.74 | 220.27
2019-04-06 06:30 | 226.52 | 221.49
2019-04-06 07:00 | 228.41 | 223.38
2019-04-06 07:30 | 225.96 | 221.38
2019-04-06 08:00 | 225.57 | 221.31
2019-04-06 08:30 | 224.72 | 219.62
2019-04-06 09:00 | 223.78 | 218.63
2019-04-06 09:30 | 223.43 | 218.04
2019-04-06 10:00 | 222.8 | 216.94
2019-04-06 10:30 | 222.49 | 216.58
2019-04-06 11:00 | 222.14 | 216.05
2019-04-06 11:30 | 222.04 | 216.06
2019-04-06 12:00 | 221.81 | 216.06
2019-04-06 12:30 | 221.35 | 215.97
2019-04-06 13:00 | 221.83 | 216.14
2019-04-06 13:30 | 221.91 | 215.98
2019-04-06 14:00 | 220.38 | 214.52
2019-04-06 14:30 | 221.81 | 216.4
2019-04-06 15:00 | 222.83 | 217.55
2019-04-06 15:30 | 223.35 | 218.47
2019-04-06 16:00 | 225.08 | 220.32
2019-04-06 16:30 | 226.77 | 221.44
2019-04-06 17:00 | 229.21 | 223.61
2019-04-06 17:30 | 231.12 | 226.47
2019-04-06 18:00 | 234.35 | 229.46
2019-04-06 18:30 | 236.47 | 231.18
2019-04-06 19:00 | 238.53 | 233.12
2019-04-06 19:30 | 238.33 | 232.78
2019-04-06 20:00 | 236.43 | 230.86
2019-04-06 20:30 | 235.6 | 229.91
2019-04-06 21:00 | 233.7 | 227.83
2019-04-06 21:30 | 232.16 | 226.95
2019-04-06 22:00 | 231.04 | 225.92
2019-04-06 22:30 | 228.97 | 224.05
2019-04-06 23:00 | 227.8 | 222.89
2019-04-06 23:30 | 227.44 | 222.57
2019-04-07 | 226.02 | 221.51
2019-04-07 00:30 | 224.91 | 221.05
2019-04-07 01:00 | 223.66 | 220.11
2019-04-07 01:30 | 223.34 | 219.71
2019-04-07 02:00 | 223.13 | 219.15
2019-04-07 02:30 | 222.81 | 218.43
2019-04-07 03:00 | 223.06 | 218.81
2019-04-07 03:30 | 221.79 | 217.92
2019-04-07 04:00 | 221.78 | 217.75
2019-04-07 04:30 | 221.82 | 217.66
2019-04-07 05:00 | 222.17 | 217.93
2019-04-07 05:30 | 222.57 | 218.36
2019-04-07 06:00 | 223.25 | 219.07
2019-04-07 06:30 | 224.15 | 220.06
2019-04-07 07:00 | 224.43 | 220.44
2019-04-07 07:30 | 222.12 | 218.4
2019-04-07 08:00 | 220.92 | 217.31
2019-04-07 08:30 | 220.89 | 215.69
2019-04-07 09:00 | 220.11 | 214.93
2019-04-07 09:30 | 218.67 | 213.76
2019-04-07 10:00 | 210.14 | 204.22
2019-04-07 10:30 | 197.16 | 191.81
2019-04-07 11:00 | 196.44 | 191.33
2019-04-07 11:30 | 197.38 | 192.17
2019-04-07 12:00 | 197.98 | 192.9
2019-04-07 12:30 | 198.73 | 193.6
2019-04-07 13:00 | 198.97 | 193.95
2019-04-07 13:30 | 199.5 | 194.27
2019-04-07 14:00 | 199.34 | 194.29
2019-04-07 14:30 | 200.08 | 194.93
2019-04-07 15:00 | 201.45 | 196.34
2019-04-07 15:30 | 204.14 | 198.57
2019-04-07 16:00 | 206.24 | 200.74
2019-04-07 16:30 | 224.49 | 219.15
2019-04-07 17:00 | 230 | 224.65
2019-04-07 17:30 | 233.16 | 227.63
2019-04-07 18:00 | 234.89 | 229.38
2019-04-07 18:30 | 238.39 | 232.72
2019-04-07 19:00 | 239.49 | 234.05
2019-04-07 19:30 | 239.01 | 233.31
2019-04-07 20:00 | 236.17 | 231.14
2019-04-07 20:30 | 233.54 | 229.24
2019-04-07 21:00 | 232.16 | 227.82
2019-04-07 21:30 | 230.9 | 226.66
2019-04-07 22:00 | 229.24 | 225.31
2019-04-07 22:30 | 226.34 | 222.79
2019-04-07 23:00 | 224.92 | 221.34
2019-04-07 23:30 | 224.63 | 220.89
2019-04-08 | 223.71 | 220
2019-04-08 00:30 | 223.1 | 219.18
2019-04-08 01:00 | 222.43 | 218.33
2019-04-08 01:30 | 222.08 | 217.98
2019-04-08 02:00 | 221.78 | 217.68
2019-04-08 02:30 | 221.49 | 217.3
2019-04-08 03:00 | 221.86 | 217.57
2019-04-08 03:30 | 221.51 | 217.35
2019-04-08 04:00 | 221.12 | 217.19
2019-04-08 04:30 | 221.57 | 217.4
2019-04-08 05:00 | 222.66 | 218.34
2019-04-08 05:30 | 224.32 | 219.83
2019-04-08 06:00 | 225.51 | 220.66
2019-04-08 06:30 | 226.49 | 221.75
2019-04-08 07:00 | 228.34 | 223.23
2019-04-08 07:30 | 227.28 | 222.72
2019-04-08 08:00 | 227.87 | 222.26
2019-04-08 08:30 | 225.45 | 220.62
2019-04-08 09:00 | 224.12 | 219.71
2019-04-08 09:30 | 222.93 | 218.63
2019-04-08 10:00 | 221.76 | 217.77
2019-04-08 10:30 | 221.65 | 217.64
2019-04-08 11:00 | 221.61 | 217.67
2019-04-08 11:30 | 222.08 | 218.11
2019-04-08 12:00 | 222.72 | 219.11
2019-04-08 12:30 | 223.74 | 219.83
2019-04-08 13:00 | 224.14 | 220.18
2019-04-08 13:30 | 225.98 | 222.03
2019-04-08 14:00 | 227.8 | 223.94
2019-04-08 14:30 | 228.17 | 224.11
2019-04-08 15:00 | 229.89 | 224.97
2019-04-08 15:30 | 231.23 | 226.24
2019-04-08 16:00 | 232.99 | 228.14
2019-04-08 16:30 | 233.96 | 229.22
2019-04-08 17:00 | 235.02 | 229.98
2019-04-08 17:30 | 236.77 | 231.61
2019-04-08 18:00 | 237.47 | 233.01
2019-04-08 18:30 | 244.96 | 236.23
2019-04-08 19:00 | 247.27 | 237.86
2019-04-08 19:30 | 246.15 | 236.26
2019-04-08 20:00 | 244.64 | 234.15
2019-04-08 20:30 | 243.12 | 232.73
2019-04-08 21:00 | 241.02 | 231.26
2019-04-08 21:30 | 238.75 | 230.67
2019-04-08 22:00 | 238.28 | 229.25
2019-04-08 22:30 | 236.13 | 228.15
2019-04-08 23:00 | 235.62 | 226.88
2019-04-08 23:30 | 235.57 | 226.27
2019-04-09 | 234.85 | 225.06
2019-04-09 00:30 | 234.6 | 224.3
2019-04-09 01:00 | 234.19 | 223.5
2019-04-09 01:30 | 233.37 | 222.95
2019-04-09 02:00 | 233.16 | 222.75
2019-04-09 02:30 | 233.26 | 222.45
2019-04-09 03:00 | 233.66 | 222.57
2019-04-09 03:30 | 232.77 | 221.89
2019-04-09 04:00 | 233.3 | 222.26
2019-04-09 04:30 | 233.08 | 222.27
2019-04-09 05:00 | 234.31 | 223.28
2019-04-09 05:30 | 235.44 | 224.49
2019-04-09 06:00 | 236.5 | 225.93
2019-04-09 06:30 | 238.73 | 227.83
2019-04-09 07:00 | 240.53 | 228.82
2019-04-09 07:30 | 237.35 | 225.29
2019-04-09 08:00 | 236.71 | 224.72
2019-04-09 08:30 | 234.4 | 223.17
2019-04-09 09:00 | 232.88 | 222.2
2019-04-09 09:30 | 230.44 | 220.67
2019-04-09 10:00 | 231.46 | 220.72
2019-04-09 10:30 | 233.34 | 222.84
2019-04-09 11:00 | 234.23 | 224.11
2019-04-09 11:30 | 234.45 | 224.42
2019-04-09 12:00 | 232.33 | 221.9
2019-04-09 12:30 | 232.74 | 222.22
2019-04-09 13:00 | 235.41 | 225.42
2019-04-09 13:30 | 238.12 | 227.42
2019-04-09 14:00 | 239.22 | 228.86
2019-04-09 14:30 | 239.54 | 228.89
2019-04-09 15:00 | 241.64 | 230.47
2019-04-09 15:30 | 245.72 | 235.07
2019-04-09 16:00 | 246.64 | 236.3
2019-04-09 16:30 | 245.78 | 235.25
2019-04-09 17:00 | 246.72 | 235.83
2019-04-09 17:30 | 247.94 | 236.45
2019-04-09 18:00 | 248.8 | 237.57
2019-04-09 18:30 | 252.05 | 240.75
2019-04-09 19:00 | 253.7 | 242.39
2019-04-09 19:30 | 252.25 | 240.81
2019-04-09 20:00 | 250.4 | 238.62
2019-04-09 20:30 | 250.75 | 238.88
2019-04-09 21:00 | 248.98 | 237.01
2019-04-09 21:30 | 247.85 | 236.09
2019-04-09 22:00 | 244.94 | 234.26
2019-04-09 22:30 | 242.67 | 232.19
2019-04-09 23:00 | 241.43 | 230.53
2019-04-09 23:30 | 240.34 | 229.69
2019-04-10 | 238.75 | 228.36
2019-04-10 00:30 | 236.88 | 227.4
2019-04-10 01:00 | 235.54 | 227.38
2019-04-10 01:30 | 235.14 | 226.97
2019-04-10 02:00 | 235.93 | 226.5
2019-04-10 02:30 | 236.07 | 226.31
2019-04-10 03:00 | 236.25 | 226.59
2019-04-10 03:30 | 235.9 | 226.58
2019-04-10 04:00 | 236.33 | 227.01
2019-04-10 04:30 | 235.79 | 225.84
2019-04-10 05:00 | 236.94 | 226.43
2019-04-10 05:30 | 238.48 | 228.2
2019-04-10 06:00 | 240.33 | 229.95
2019-04-10 06:30 | 242.81 | 231.98
2019-04-10 07:00 | 244.73 | 232.37
2019-04-10 07:30 | 242.1 | 229.34
2019-04-10 08:00 | 242.43 | 229.89
2019-04-10 08:30 | 237.72 | 225.97
2019-04-10 09:00 | 237.21 | 225.53
2019-04-10 09:30 | 237.54 | 225.42
2019-04-10 10:00 | 236.87 | 224.44
2019-04-10 10:30 | 236.97 | 223.85
2019-04-10 11:00 | 234.41 | 222.67
2019-04-10 11:30 | 234.01 | 222.24
2019-04-10 12:00 | 233.98 | 222.24
2019-04-10 12:30 | 236.93 | 225.72
2019-04-10 13:00 | 237.24 | 225.77
2019-04-10 13:30 | 237.81 | 225.71
2019-04-10 14:00 | 235.83 | 224.15
2019-04-10 14:30 | 236.31 | 225.37
2019-04-10 15:00 | 233.96 | 223.12
2019-04-10 15:30 | 220.53 | 209.88
2019-04-10 16:00 | 222.55 | 211.74
2019-04-10 16:30 | 236 | 224.45
2019-04-10 17:00 | 242.85 | 231.54
2019-04-10 17:30 | 245.32 | 233.56
2019-04-10 18:00 | 229.38 | 217.58
2019-04-10 18:30 | 226.87 | 214.98
2019-04-10 19:00 | 230.62 | 218.49
2019-04-10 19:30 | 226.79 | 217.7
2019-04-10 20:00 | 223.39 | 215.9
2019-04-10 20:30 | 222.78 | 215.08
2019-04-10 21:00 | 223.13 | 215.16
2019-04-10 21:30 | 223.26 | 215.55
2019-04-10 22:00 | 222.7 | 214.37
2019-04-10 22:30 | 220.49 | 211.6
2019-04-10 23:00 | 219.56 | 210.25
2019-04-10 23:30 | 219.31 | 209.58
2019-04-11 | 216.36 | 207.04
2019-04-11 00:30 | 212.65 | 204.29
2019-04-11 01:00 | 211.94 | 202.92
2019-04-11 01:30 | 211.63 | 202.32
2019-04-11 02:00 | 211.95 | 202.6
2019-04-11 02:30 | 212.01 | 202.59
2019-04-11 03:00 | 211.9 | 202.57
2019-04-11 03:30 | 211.97 | 202.52
2019-04-11 04:00 | 212.28 | 202.89
2019-04-11 04:30 | 213.4 | 203.75
2019-04-11 05:00 | 214.07 | 204.46
2019-04-11 05:30 | 215.95 | 205.97
2019-04-11 06:00 | 219.55 | 207.53
2019-04-11 06:30 | 221.33 | 209.36
2019-04-11 07:00 | 223.48 | 210.74
2019-04-11 07:30 | 218.3 | 206.53
2019-04-11 08:00 | 216.12 | 204.53
2019-04-11 08:30 | 214.23 | 202.97
2019-04-11 09:00 | 212.36 | 202.1
2019-04-11 09:30 | 211.46 | 201.24
2019-04-11 10:00 | 211.63 | 201.17
2019-04-11 10:30 | 211.54 | 200.48
2019-04-11 11:00 | 212.29 | 200.72
2019-04-11 11:30 | 212.25 | 200.57
2019-04-11 12:00 | 213.26 | 201.57
2019-04-11 12:30 | 213.28 | 201.53
2019-04-11 13:00 | 213.29 | 202.19
2019-04-11 13:30 | 229.62 | 218.92
2019-04-11 14:00 | 234.68 | 224.55
2019-04-11 14:30 | 235.33 | 225.63
2019-04-11 15:00 | 237.03 | 226.3
2019-04-11 15:30 | 238.25 | 227.61
2019-04-11 16:00 | 239.73 | 229.05
2019-04-11 16:30 | 241.82 | 230.98
2019-04-11 17:00 | 242.65 | 231.52
2019-04-11 17:30 | 243.32 | 232.11
2019-04-11 18:00 | 246.42 | 235.12
2019-04-11 18:30 | 249.35 | 238.3
2019-04-11 19:00 | 251.49 | 240.45
2019-04-11 19:30 | 250.14 | 238.62
2019-04-11 20:00 | 248.95 | 237.06
2019-04-11 20:30 | 245.94 | 235.48
2019-04-11 21:00 | 246.1 | 235.65
2019-04-11 21:30 | 246.45 | 236.19
2019-04-11 22:00 | 228.21 | 218.05
2019-04-11 22:30 | 221.8 | 211.37
2019-04-11 23:00 | 220.78 | 210.01
2019-04-11 23:30 | 220.15 | 209.45
2019-04-12 | 218.28 | 208.19
2019-04-12 00:30 | 217.53 | 207.9
2019-04-12 01:00 | 216.42 | 207.18
2019-04-12 01:30 | 215.88 | 206.6
2019-04-12 02:00 | 215.04 | 206.53
2019-04-12 02:30 | 215.01 | 206.55
2019-04-12 03:00 | 215.06 | 206.33
2019-04-12 03:30 | 214.91 | 206.12
2019-04-12 04:00 | 214.81 | 206.38
2019-04-12 04:30 | 214.78 | 206.32
2019-04-12 05:00 | 215.94 | 207.24
2019-04-12 05:30 | 217.9 | 208.67
2019-04-12 06:00 | 227.92 | 218.51
2019-04-12 06:30 | 239.47 | 228.94
2019-04-12 07:00 | 245.09 | 233.54
2019-04-12 07:30 | 240.2 | 229.85
2019-04-12 08:00 | 239.61 | 228.77
2019-04-12 08:30 | 238.64 | 226.44
2019-04-12 09:00 | 237.68 | 225.8
2019-04-12 09:30 | 236.81 | 225.24
2019-04-12 10:00 | 235.45 | 224.08
2019-04-12 10:30 | 235.51 | 223.27
2019-04-12 11:00 | 234.63 | 222.38
2019-04-12 11:30 | 234.58 | 222.28
2019-04-12 12:00 | 234.48 | 222.54
2019-04-12 12:30 | 235.24 | 223.01
2019-04-12 13:00 | 235.47 | 223.04
2019-04-12 13:30 | 236.35 | 223.98
2019-04-12 14:00 | 238.43 | 226.08
2019-04-12 14:30 | 238.16 | 225.89
2019-04-12 15:00 | 238.63 | 226.35
2019-04-12 15:30 | 239.66 | 227.05
2019-04-12 16:00 | 240.74 | 228.31
2019-04-12 16:30 | 245.35 | 236.71
2019-04-12 17:00 | 251.8 | 245.55
2019-04-12 17:30 | 252.85 | 246.18
2019-04-12 18:00 | 253.12 | 246.31
2019-04-12 18:30 | 252.59 | 245.68
2019-04-12 19:00 | 252.85 | 246.09
2019-04-12 19:30 | 253.7 | 246.9
2019-04-12 20:00 | 254.56 | 247.75
2019-04-12 20:30 | 255.1 | 248.27
2019-04-12 21:00 | 243.81 | 233.71
2019-04-12 21:30 | 243.98 | 234.56
2019-04-12 22:00 | 243.01 | 233.36
2019-04-12 22:30 | 241.22 | 231.94
2019-04-12 23:00 | 239.99 | 230.6
2019-04-12 23:30 | 239.29 | 229.98
2019-04-13 | 238.06 | 229.2
2019-04-13 00:30 | 237.02 | 227.82
2019-04-13 01:00 | 236.48 | 227.02
2019-04-13 01:30 | 236.64 | 226.72
2019-04-13 02:00 | 236.31 | 226.67
2019-04-13 02:30 | 235.46 | 226.07
2019-04-13 03:00 | 234.78 | 226.04
2019-04-13 03:30 | 234.61 | 225.77
2019-04-13 04:00 | 234.71 | 225.52
2019-04-13 04:30 | 235.56 | 226.02
2019-04-13 05:00 | 236.13 | 226.25
2019-04-13 05:30 | 236.16 | 226.69
2019-04-13 06:00 | 237.46 | 228.5
2019-04-13 06:30 | 237.5 | 228.91
2019-04-13 07:00 | 237.72 | 229.35
2019-04-13 07:30 | 233.67 | 224.88
2019-04-13 08:00 | 232.78 | 223.91
2019-04-13 08:30 | 215.49 | 206.48
2019-04-13 09:00 | 209.73 | 200.34
2019-04-13 09:30 | 209.66 | 200.05
2019-04-13 10:00 | 209.45 | 199.78
2019-04-13 10:30 | 208.55 | 198.77
2019-04-13 11:00 | 207.51 | 197.89
2019-04-13 11:30 | 176.61 | 166.61
2019-04-13 12:00 | 163.59 | 153.36
2019-04-13 12:30 | 164.94 | 154.78
2019-04-13 13:00 | 165.41 | 155.24
2019-04-13 13:30 | 165.96 | 155.86
2019-04-13 14:00 | 166.78 | 156.78
2019-04-13 14:30 | 200.46 | 191.56
2019-04-13 15:00 | 229.35 | 220.67
2019-04-13 15:30 | 233.67 | 224.66
2019-04-13 16:00 | 235.39 | 225.66
2019-04-13 16:30 | 237.76 | 227.61
2019-04-13 17:00 | 239.67 | 229.49
2019-04-13 17:30 | 241.72 | 231.24
2019-04-13 18:00 | 243.98 | 232.91
2019-04-13 18:30 | 245.81 | 234.63
2019-04-13 19:00 | 246.93 | 235.88
2019-04-13 19:30 | 245.26 | 234.21
2019-04-13 20:00 | 244.05 | 233.14
2019-04-13 20:30 | 242.34 | 231.65
2019-04-13 21:00 | 241.09 | 230.49
2019-04-13 21:30 | 241.48 | 231.6
2019-04-13 22:00 | 241.84 | 231.63
2019-04-13 22:30 | 240.35 | 230.16
2019-04-13 23:00 | 239.38 | 228.82
2019-04-13 23:30 | 239.19 | 228.3
2019-04-14 | 238.22 | 227.3
2019-04-14 00:30 | 236.06 | 227.25
2019-04-14 01:00 | 234.36 | 226.42
2019-04-14 01:30 | 235.01 | 225.47
2019-04-14 02:00 | 234.5 | 224.83
2019-04-14 02:30 | 234.42 | 224.93
2019-04-14 03:00 | 234.26 | 224.79
2019-04-14 03:30 | 233.89 | 224.27
2019-04-14 04:00 | 234.36 | 224.8
2019-04-14 04:30 | 217.74 | 208.05
2019-04-14 05:00 | 213.63 | 203.45
2019-04-14 05:30 | 214.03 | 203.79
2019-04-14 06:00 | 214.62 | 204.64
2019-04-14 06:30 | 214.73 | 205.24
2019-04-14 07:00 | 214.19 | 205.17
2019-04-14 07:30 | 210.77 | 202.56
2019-04-14 08:00 | 210.23 | 202.19
2019-04-14 08:30 | 181.93 | 171.22
2019-04-14 09:00 | 168.92 | 156.3
2019-04-14 09:30 | 168.47 | 154.59
2019-04-14 10:00 | 170.81 | 156.6
2019-04-14 10:30 | 170.21 | 156.49
2019-04-14 11:00 | 169.57 | 156.21
2019-04-14 11:30 | 170.34 | 156.63
2019-04-14 12:00 | 170.59 | 157.21
2019-04-14 12:30 | 171.73 | 157.98
2019-04-14 13:00 | 172.67 | 158.58
2019-04-14 13:30 | 202.93 | 190.32
2019-04-14 14:00 | 213.39 | 202.56
2019-04-14 14:30 | 214.4 | 203.78
2019-04-14 15:00 | 215.63 | 205.16
2019-04-14 15:30 | 215.95 | 205.89
2019-04-14 16:00 | 234.13 | 224.05
2019-04-14 16:30 | 240.07 | 230.06
2019-04-14 17:00 | 241.96 | 231.6
2019-04-14 17:30 | 240.36 | 229.52
2019-04-14 18:00 | 251.65 | 244.99
2019-04-14 18:30 | 251.2 | 244.57
2019-04-14 19:00 | 252 | 245.17
2019-04-14 19:30 | 252.82 | 246.08
2019-04-14 20:00 | 254.25 | 247.84
2019-04-14 20:30 | 241.93 | 231.47
2019-04-14 21:00 | 240.05 | 229
2019-04-14 21:30 | 239.38 | 228.44
2019-04-14 22:00 | 237.18 | 227.24
2019-04-14 22:30 | 235.41 | 225.21
2019-04-14 23:00 | 234.49 | 224.49
2019-04-14 23:30 | 233.47 | 223.03
2019-04-15 | 231.1 | 221.48
2019-04-15 00:30 | 231.05 | 221.63
2019-04-15 01:00 | 214.08 | 204.8
2019-04-15 01:30 | 209.13 | 200.37
2019-04-15 02:00 | 209.24 | 200.44
2019-04-15 02:30 | 208.47 | 199.63
2019-04-15 03:00 | 208.65 | 199.85
2019-04-15 03:30 | 208.56 | 199.85
2019-04-15 04:00 | 208.95 | 200.39
2019-04-15 04:30 | 209.54 | 200.83
2019-04-15 05:00 | 209.28 | 200.23
2019-04-15 05:30 | 209.8 | 201
2019-04-15 06:00 | 213.14 | 202.69
2019-04-15 06:30 | 231.93 | 219.52
2019-04-15 07:00 | 238.26 | 226.51
2019-04-15 07:30 | 239.92 | 228.37
2019-04-15 08:00 | 239.79 | 227.91
2019-04-15 08:30 | 237.46 | 225.82
2019-04-15 09:00 | 235.1 | 223.99
2019-04-15 09:30 | 235.06 | 224.18
2019-04-15 10:00 | 234.79 | 223.97
2019-04-15 10:30 | 235.28 | 224.13
2019-04-15 11:00 | 234.56 | 223.44
2019-04-15 11:30 | 234.57 | 223.4
2019-04-15 12:00 | 235.33 | 224.45
2019-04-15 12:30 | 235.51 | 224.71
2019-04-15 13:00 | 235.02 | 224.27
2019-04-15 13:30 | 236.08 | 225.17
2019-04-15 14:00 | 237.24 | 226.09
2019-04-15 14:30 | 237.9 | 226.73
2019-04-15 15:00 | 238.75 | 227.5
2019-04-15 15:30 | 240.33 | 228.65
2019-04-15 16:00 | 242.47 | 230.35
2019-04-15 16:30 | 243.44 | 231.56
2019-04-15 17:00 | 244.47 | 232.73
2019-04-15 17:30 | 245.7 | 233.63
2019-04-15 18:00 | 246.94 | 235.47
2019-04-15 18:30 | 249.87 | 238.87
2019-04-15 19:00 | 252.01 | 240.96
2019-04-15 19:30 | 250.14 | 238.98
2019-04-15 20:00 | 248.46 | 237.27
2019-04-15 20:30 | 247.28 | 236.1
2019-04-15 21:00 | 245.47 | 234.36
2019-04-15 21:30 | 244.12 | 233.78
2019-04-15 22:00 | 241.61 | 231.46
2019-04-15 22:30 | 239.91 | 229.84
2019-04-15 23:00 | 238.88 | 228.8
2019-04-15 23:30 | 238.37 | 228.36
2019-04-16 | 236.27 | 226.64
2019-04-16 00:30 | 235.71 | 226.35
2019-04-16 01:00 | 234.98 | 225.51
2019-04-16 01:30 | 234.79 | 225.22
2019-04-16 02:00 | 234.69 | 224.81
2019-04-16 02:30 | 234.21 | 224.29
2019-04-16 03:00 | 234.11 | 224.09
2019-04-16 03:30 | 234.93 | 224.69
2019-04-16 04:00 | 235.38 | 225.02
2019-04-16 04:30 | 235.63 | 225.06
2019-04-16 05:00 | 236.62 | 226.05
2019-04-16 05:30 | 237.02 | 226.65
2019-04-16 06:00 | 237.89 | 227.74
2019-04-16 06:30 | 241.28 | 230.17
2019-04-16 07:00 | 241.72 | 230.77
2019-04-16 07:30 | 240.22 | 229.82
2019-04-16 08:00 | 238.85 | 228.61
2019-04-16 08:30 | 236.59 | 226.36
2019-04-16 09:00 | 234.77 | 225.11
2019-04-16 09:30 | 231.37 | 221.81
2019-04-16 10:00 | 233.35 | 223.33
2019-04-16 10:30 | 232.59 | 222.54
2019-04-16 11:00 | 232.78 | 222.16
2019-04-16 11:30 | 233.48 | 222.08
2019-04-16 12:00 | 233.17 | 222.46
2019-04-16 12:30 | 234.28 | 223.4
2019-04-16 13:00 | 233.77 | 223.13
2019-04-16 13:30 | 234.85 | 224.31
2019-04-16 14:00 | 235.85 | 225.54
2019-04-16 14:30 | 237.73 | 227.03
2019-04-16 15:00 | 239.4 | 228.26
2019-04-16 15:30 | 239.63 | 228.24
2019-04-16 16:00 | 241.27 | 230.12
2019-04-16 16:30 | 241.75 | 230.33
2019-04-16 17:00 | 243.21 | 231.62
2019-04-16 17:30 | 244.64 | 232.58
2019-04-16 18:00 | 247.81 | 235.34
2019-04-16 18:30 | 249.94 | 238.66
2019-04-16 19:00 | 250.69 | 240.02
2019-04-16 19:30 | 249.61 | 238.77
2019-04-16 20:00 | 247.46 | 236.85
2019-04-16 20:30 | 246.18 | 235.31
2019-04-16 21:00 | 246.63 | 235.54
2019-04-16 21:30 | 246.22 | 235.72
2019-04-16 22:00 | 244.13 | 234.27
2019-04-16 22:30 | 241.97 | 231.77
2019-04-16 23:00 | 241.43 | 230.82
2019-04-16 23:30 | 239.76 | 229.8
2019-04-17 | 237.89 | 228.34
2019-04-17 00:30 | 237.33 | 228.09
2019-04-17 01:00 | 235.76 | 226.83
2019-04-17 01:30 | 235.11 | 226.37
2019-04-17 02:00 | 234.69 | 226.27
2019-04-17 02:30 | 218.89 | 209.85
2019-04-17 03:00 | 214.49 | 205.07
2019-04-17 03:30 | 214.68 | 204.95
2019-04-17 04:00 | 214.34 | 204.56
2019-04-17 04:30 | 214.42 | 204.72
2019-04-17 05:00 | 214.96 | 205.37
2019-04-17 05:30 | 215.92 | 206.78
2019-04-17 06:00 | 216.19 | 207.15
2019-04-17 06:30 | 219.55 | 210.94
2019-04-17 07:00 | 236.99 | 226.56
2019-04-17 07:30 | 237.72 | 227.75
2019-04-17 08:00 | 236.82 | 227.16
2019-04-17 08:30 | 236.18 | 226.12
2019-04-17 09:00 | 234.64 | 224.53
2019-04-17 09:30 | 216.27 | 206.34
2019-04-17 10:00 | 176.69 | 166.02
2019-04-17 10:30 | 165.44 | 154.83
2019-04-17 11:00 | 164.06 | 153.6
2019-04-17 11:30 | 166.19 | 156.18
2019-04-17 12:00 | 199.77 | 190.35
2019-04-17 12:30 | 231.51 | 222.08
2019-04-17 13:00 | 233.77 | 224.64
2019-04-17 13:30 | 234.9 | 225.54
2019-04-17 14:00 | 235.6 | 226.41
2019-04-17 14:30 | 236.48 | 227.39
2019-04-17 15:00 | 236.98 | 228.04
2019-04-17 15:30 | 238.93 | 229.98
2019-04-17 16:00 | 240.19 | 231.33
2019-04-17 16:30 | 242.1 | 232.64
2019-04-17 17:00 | 243.07 | 233.19
2019-04-17 17:30 | 244.73 | 234.42
2019-04-17 18:00 | 246.88 | 236.41
2019-04-17 18:30 | 249.12 | 238.72
2019-04-17 19:00 | 251.32 | 240.75
2019-04-17 19:30 | 250 | 239.32
2019-04-17 20:00 | 247.14 | 236.33
2019-04-17 20:30 | 246.17 | 235.46
2019-04-17 21:00 | 246.9 | 236.27
2019-04-17 21:30 | 246.97 | 236.55
2019-04-17 22:00 | 245.65 | 235.39
2019-04-17 22:30 | 243.74 | 232.95
2019-04-17 23:00 | 242.91 | 232.09
2019-04-17 23:30 | 241 | 231.08
2019-04-18 | 239.3 | 229.35
2019-04-18 00:30 | 239.36 | 229.14
2019-04-18 01:00 | 236.72 | 227.95
2019-04-18 01:30 | 236.55 | 227.38
2019-04-18 02:00 | 236.38 | 227.04
2019-04-18 02:30 | 235.3 | 225.97
2019-04-18 03:00 | 219.69 | 210.5
2019-04-18 03:30 | 215.29 | 205.84
2019-04-18 04:00 | 215.44 | 205.97
2019-04-18 04:30 | 216.45 | 206.96
2019-04-18 05:00 | 216.92 | 207.43
2019-04-18 05:30 | 218.23 | 209.02
2019-04-18 06:00 | 218.84 | 209.7
2019-04-18 06:30 | 220.88 | 211.53
2019-04-18 07:00 | 222.93 | 212.78
2019-04-18 07:30 | 220.31 | 208.44
2019-04-18 08:00 | 217.64 | 206.95
2019-04-18 08:30 | 215.87 | 205.15
2019-04-18 09:00 | 216.74 | 205.74
2019-04-18 09:30 | 215.29 | 204.09
2019-04-18 10:00 | 214.6 | 203.68
2019-04-18 10:30 | 213.68 | 202.45
2019-04-18 11:00 | 213.8 | 202.49
2019-04-18 11:30 | 214.2 | 202.12
2019-04-18 12:00 | 215.24 | 204.33
2019-04-18 12:30 | 213.77 | 203.14
2019-04-18 13:00 | 214.88 | 204.26
2019-04-18 13:30 | 233.06 | 222.28
2019-04-18 14:00 | 238.44 | 227.91
2019-04-18 14:30 | 239.29 | 228.97
2019-04-18 15:00 | 239.65 | 229.75
2019-04-18 15:30 | 241.4 | 230.99
2019-04-18 16:00 | 243.35 | 232.46
2019-04-18 16:30 | 243.85 | 232.98
2019-04-18 17:00 | 245.93 | 234.85
2019-04-18 17:30 | 246.8 | 235.54
2019-04-18 18:00 | 248.8 | 236.98
2019-04-18 18:30 | 251.4 | 239.58
2019-04-18 19:00 | 253.34 | 241.46
2019-04-18 19:30 | 252.76 | 240.49
2019-04-18 20:00 | 251.21 | 238.74
2019-04-18 20:30 | 250.25 | 237.64
2019-04-18 21:00 | 249.91 | 237.65
2019-04-18 21:30 | 249.07 | 237.79
2019-04-18 22:00 | 247.51 | 236.65
2019-04-18 22:30 | 245.97 | 235.6
2019-04-18 23:00 | 243.13 | 233.91
2019-04-18 23:30 | 241.95 | 233.25
2019-04-19 | 239.62 | 231.49
2019-04-19 00:30 | 221.92 | 213.72
2019-04-19 01:00 | 215.97 | 207.57
2019-04-19 01:30 | 215.4 | 206.96
2019-04-19 02:00 | 214.76 | 206.37
2019-04-19 02:30 | 215.05 | 206.14
2019-04-19 03:00 | 215.12 | 205.91
2019-04-19 03:30 | 215.45 | 205.99
2019-04-19 04:00 | 215.41 | 205.95
2019-04-19 04:30 | 216.27 | 206.56
2019-04-19 05:00 | 217.14 | 207.26
2019-04-19 05:30 | 219.25 | 209.51
2019-04-19 06:00 | 219.5 | 210.01
2019-04-19 06:30 | 220.36 | 211.15
2019-04-19 07:00 | 219.37 | 210.32
2019-04-19 07:30 | 181.05 | 172.27
2019-04-19 08:00 | 167.15 | 157.14
2019-04-19 08:30 | 168.84 | 157.54
2019-04-19 09:00 | 166.99 | 154.84
2019-04-19 09:30 | 167.55 | 154.65
2019-04-19 10:00 | 164.96 | 152.55
2019-04-19 10:30 | 166.59 | 152.08
2019-04-19 11:00 | 167.39 | 153.02
2019-04-19 11:30 | 168.96 | 154.86
2019-04-19 12:00 | 167.07 | 152.55
2019-04-19 12:30 | 168.04 | 154.01
2019-04-19 13:00 | 168.42 | 154.45
2019-04-19 13:30 | 169.17 | 155.2
2019-04-19 14:00 | 169.54 | 155.97
2019-04-19 14:30 | 171.18 | 157.59
2019-04-19 15:00 | 172.44 | 157.71
2019-04-19 15:30 | 205.23 | 191.67
2019-04-19 16:00 | 235.68 | 222.75
2019-04-19 16:30 | 241.14 | 229.06
2019-04-19 17:00 | 242.75 | 230.58
2019-04-19 17:30 | 243.39 | 231.12
2019-04-19 18:00 | 243.71 | 233.61
2019-04-19 18:30 | 245.5 | 235.26
2019-04-19 19:00 | 246.16 | 235.73
2019-04-19 19:30 | 245.2 | 234.46
2019-04-19 20:00 | 243.55 | 232.5
2019-04-19 20:30 | 242.41 | 231.49
2019-04-19 21:00 | 241.65 | 230.87
2019-04-19 21:30 | 240.1 | 230.94
2019-04-19 22:00 | 238.98 | 230.03
2019-04-19 22:30 | 237.69 | 228.53
2019-04-19 23:00 | 236.09 | 227.18
2019-04-19 23:30 | 235.16 | 226.44
2019-04-20 | 233.77 | 225.32
2019-04-20 00:30 | 217.23 | 208.12
2019-04-20 01:00 | 182.12 | 171.69
2019-04-20 01:30 | 166.93 | 155.98
2019-04-20 02:00 | 164.37 | 154.63
2019-04-20 02:30 | 163.35 | 154.26
2019-04-20 03:00 | 163.42 | 154.28
2019-04-20 03:30 | 163.28 | 153.94
2019-04-20 04:00 | 162.66 | 153.06
2019-04-20 04:30 | 163.73 | 154.16
2019-04-20 05:00 | 163.62 | 153.83
2019-04-20 05:30 | 164.35 | 154.89
2019-04-20 06:00 | 164.21 | 155.11
2019-04-20 06:30 | 165.38 | 156.3
2019-04-20 07:00 | 166.69 | 157.68
2019-04-20 07:30 | 166.42 | 157.41
2019-04-20 08:00 | 169.08 | 159.2
2019-04-20 08:30 | 169.28 | 159.46
2019-04-20 09:00 | 167.99 | 158.37
2019-04-20 09:30 | 166.11 | 156.04
2019-04-20 10:00 | 166.93 | 156.59
2019-04-20 10:30 | 164.11 | 153.71
2019-04-20 11:00 | 164.23 | 153.86
2019-04-20 11:30 | 165.61 | 155.07
2019-04-20 12:00 | 166.59 | 154.97
2019-04-20 12:30 | 166.73 | 154.68
2019-04-20 13:00 | 168.96 | 156.57
2019-04-20 13:30 | 168.14 | 156.23
2019-04-20 14:00 | 169.18 | 157.82
2019-04-20 14:30 | 203.71 | 192.51
2019-04-20 15:00 | 232.01 | 221.68
2019-04-20 15:30 | 236.43 | 226.08
2019-04-20 16:00 | 237.74 | 227.24
2019-04-20 16:30 | 239.26 | 229.07
2019-04-20 17:00 | 240.8 | 230.64
2019-04-20 17:30 | 200.24 | 189.68
2019-04-20 18:00 | 178.33 | 168.76
2019-04-20 18:30 | 180.83 | 173.84
2019-04-20 19:00 | 181.48 | 174.13
2019-04-20 19:30 | 170.65 | 163.1
2019-04-20 20:00 | 167.95 | 160.22
2019-04-20 20:30 | 167.19 | 159.24
2019-04-20 21:00 | 165.1 | 158.15
2019-04-20 21:30 | 164.38 | 157.86
2019-04-20 22:00 | 163.47 | 156.98
2019-04-20 22:30 | 162.2 | 155.61
2019-04-20 23:00 | 160.57 | 153.99
2019-04-20 23:30 | 160.08 | 153.66
2019-04-21 | 158.5 | 152.46
2019-04-21 00:30 | 158.36 | 151.99
2019-04-21 01:00 | 158 | 150.92
2019-04-21 01:30 | 157.24 | 150.07
2019-04-21 02:00 | 156.69 | 149.54
2019-04-21 02:30 | 156.42 | 149.11
2019-04-21 03:00 | 156.16 | 148.97
2019-04-21 03:30 | 155.88 | 148.64
2019-04-21 04:00 | 155.48 | 148.46
2019-04-21 04:30 | 155.93 | 148.72
2019-04-21 05:00 | 155.64 | 148.55
2019-04-21 05:30 | 155.86 | 149.18
2019-04-21 06:00 | 156.2 | 149.51
2019-04-21 06:30 | 156.73 | 149.94
2019-04-21 07:00 | 156.54 | 149.64
2019-04-21 07:30 | 157.11 | 150.76
2019-04-21 08:00 | 157.31 | 150.74
2019-04-21 08:30 | 157.15 | 150.56
2019-04-21 09:00 | 158.03 | 150.54
2019-04-21 09:30 | 156.73 | 149.44
2019-04-21 10:00 | 156.32 | 148.87
2019-04-21 10:30 | 155.59 | 148.36
2019-04-21 11:00 | 155.36 | 147.81
2019-04-21 11:30 | 156.07 | 148.14
2019-04-21 12:00 | 156.23 | 148.6
2019-04-21 12:30 | 157.3 | 149.84
2019-04-21 13:00 | 158.23 | 151.11
2019-04-21 13:30 | 158.6 | 151.56
2019-04-21 14:00 | 159.53 | 152.5
2019-04-21 14:30 | 159.89 | 153.17
2019-04-21 15:00 | 161.09 | 153.98
2019-04-21 15:30 | 162.19 | 155.66
2019-04-21 16:00 | 164.29 | 156.73
2019-04-21 16:30 | 165.79 | 158.23
2019-04-21 17:00 | 167.23 | 159.55
2019-04-21 17:30 | 169.11 | 161.03
2019-04-21 18:00 | 170.88 | 161.75
2019-04-21 18:30 | 172.62 | 163.03
2019-04-21 19:00 | 172.69 | 162.62
2019-04-21 19:30 | 175.6 | 165.1
2019-04-21 20:00 | 199.3 | 189.44
2019-04-21 20:30 | 225.05 | 215.43
2019-04-21 21:00 | 228.38 | 218.18
2019-04-21 21:30 | 229.11 | 218.86
2019-04-21 22:00 | 226.54 | 216.66
2019-04-21 22:30 | 224.98 | 215.66
2019-04-21 23:00 | 223.9 | 214.54
2019-04-21 23:30 | 222.96 | 213.61
2019-04-22 | 221.49 | 212.75
2019-04-22 00:30 | 219.76 | 212.16
2019-04-22 01:00 | 218.64 | 211.13
2019-04-22 01:30 | 217.49 | 210.2
2019-04-22 02:00 | 217.18 | 209.93
2019-04-22 02:30 | 209.09 | 201.58
2019-04-22 03:00 | 207.6 | 200.03
2019-04-22 03:30 | 207.4 | 199.69
2019-04-22 04:00 | 207.07 | 199.39
2019-04-22 04:30 | 206.85 | 199.5
2019-04-22 05:00 | 206.93 | 199.64
2019-04-22 05:30 | 207.52 | 200.25
2019-04-22 06:00 | 208.34 | 201.04
2019-04-22 06:30 | 209.38 | 202.22
2019-04-22 07:00 | 210.83 | 203.73
2019-04-22 07:30 | 211.5 | 205.14
2019-04-22 08:00 | 211.74 | 205.39
2019-04-22 08:30 | 211.8 | 204.8
2019-04-22 09:00 | 211.49 | 204.16
2019-04-22 09:30 | 211.4 | 203.92
2019-04-22 10:00 | 209.78 | 202.33
2019-04-22 10:30 | 208.95 | 200.92
2019-04-22 11:00 | 224.24 | 216.32
2019-04-22 11:30 | 229.17 | 220.5
2019-04-22 12:00 | 229.02 | 220.21
2019-04-22 12:30 | 230.95 | 222.38
2019-04-22 13:00 | 232.08 | 223.5
2019-04-22 13:30 | 232.66 | 224.07
2019-04-22 14:00 | 232.95 | 224.35
2019-04-22 14:30 | 233.44 | 224.99
2019-04-22 15:00 | 234.67 | 226.17
2019-04-22 15:30 | 237.1 | 228.01
2019-04-22 16:00 | 237.61 | 228.15
2019-04-22 16:30 | 236.69 | 227.46
2019-04-22 17:00 | 238.67 | 229.32
2019-04-22 17:30 | 240.88 | 231.36
2019-04-22 18:00 | 245.96 | 241.39
2019-04-22 18:30 | 249.63 | 245.78
2019-04-22 19:00 | 250.45 | 246.53
2019-04-22 19:30 | 251.48 | 247.29
2019-04-22 20:00 | 241.97 | 233.01
2019-04-22 20:30 | 241.88 | 231.54
2019-04-22 21:00 | 240.12 | 229.6
2019-04-22 21:30 | 238.44 | 227.5
2019-04-22 22:00 | 236.66 | 226.3
2019-04-22 22:30 | 234.68 | 224.43
2019-04-22 23:00 | 233.98 | 223.74
2019-04-22 23:30 | 234.01 | 223.91
2019-04-23 | 232.75 | 223.46
2019-04-23 00:30 | 232.16 | 223.09
2019-04-23 01:00 | 230.32 | 222.49
2019-04-23 01:30 | 229.26 | 221.78
2019-04-23 02:00 | 229.33 | 221.76
2019-04-23 02:30 | 228.83 | 221.47
2019-04-23 03:00 | 228.52 | 221.05
2019-04-23 03:30 | 228.82 | 221.19
2019-04-23 04:00 | 228.7 | 221.09
2019-04-23 04:30 | 229.36 | 221.52
2019-04-23 05:00 | 229.83 | 222.03
2019-04-23 05:30 | 230.63 | 223.13
2019-04-23 06:00 | 231.71 | 224.21
2019-04-23 06:30 | 234.04 | 226.1
2019-04-23 07:00 | 236.62 | 228.06
2019-04-23 07:30 | 238.8 | 230.29
2019-04-23 08:00 | 239.56 | 231.08
2019-04-23 08:30 | 239.49 | 230.47
2019-04-23 09:00 | 239.3 | 230.27
2019-04-23 09:30 | 239.03 | 229.75
2019-04-23 10:00 | 239.91 | 230.18
2019-04-23 10:30 | 239.67 | 229.78
2019-04-23 11:00 | 239.61 | 229.74
2019-04-23 11:30 | 238.71 | 228.83
2019-04-23 12:00 | 237.78 | 227.84
2019-04-23 12:30 | 237.64 | 227.46
2019-04-23 13:00 | 237.96 | 227.69
2019-04-23 13:30 | 237.23 | 226.7
2019-04-23 14:00 | 237.55 | 227.31
2019-04-23 14:30 | 235.91 | 227.46
2019-04-23 15:00 | 235.91 | 227.63
2019-04-23 15:30 | 235.86 | 227.71
2019-04-23 16:00 | 236.39 | 228.51
2019-04-23 16:30 | 236.61 | 228.93
2019-04-23 17:00 | 237.28 | 229.83
2019-04-23 17:30 | 238.44 | 230.87
2019-04-23 18:00 | 240.83 | 233.15
2019-04-23 18:30 | 245.24 | 237.78
2019-04-23 19:00 | 246.75 | 239.05
2019-04-23 19:30 | 245.61 | 237.68
2019-04-23 20:00 | 244.12 | 236.12
2019-04-23 20:30 | 243.91 | 235.5
2019-04-23 21:00 | 243.57 | 235.26
2019-04-23 21:30 | 242.83 | 235.2
2019-04-23 22:00 | 240.7 | 233.1
2019-04-23 22:30 | 239.53 | 232.37
2019-04-23 23:00 | 238.93 | 231.3
2019-04-23 23:30 | 238.47 | 230.5
2019-04-24 | 236.96 | 229.26
2019-04-24 00:30 | 234.95 | 227.84
2019-04-24 01:00 | 233.57 | 226.55
2019-04-24 01:30 | 234.38 | 226.73
2019-04-24 02:00 | 234.11 | 226.62
2019-04-24 02:30 | 234.25 | 226.51
2019-04-24 03:00 | 234.44 | 226.61
2019-04-24 03:30 | 234.06 | 226.32
2019-04-24 04:00 | 234.8 | 226.97
2019-04-24 04:30 | 235.5 | 227.46
2019-04-24 05:00 | 236.22 | 228.16
2019-04-24 05:30 | 237.21 | 229.37
2019-04-24 06:00 | 238.51 | 230.93
2019-04-24 06:30 | 241.23 | 233.45
2019-04-24 07:00 | 244.87 | 236.71
2019-04-24 07:30 | 244 | 235.66
2019-04-24 08:00 | 244.07 | 235.83
2019-04-24 08:30 | 244.36 | 236.38
2019-04-24 09:00 | 243.42 | 234.95
2019-04-24 09:30 | 242.5 | 233.45
2019-04-24 10:00 | 243.51 | 234.76
2019-04-24 10:30 | 249.39 | 243.21
2019-04-24 11:00 | 249.35 | 243.21
2019-04-24 11:30 | 248.94 | 242.75
2019-04-24 12:00 | 249.09 | 242.86
2019-04-24 12:30 | 248.73 | 242.35
2019-04-24 13:00 | 248.61 | 242.2
2019-04-24 13:30 | 246 | 239.47
2019-04-24 14:00 | 241.04 | 233.86
2019-04-24 14:30 | 241.75 | 235.06
2019-04-24 15:00 | 240.1 | 233.66
2019-04-24 15:30 | 239.64 | 233.16
2019-04-24 16:00 | 240.27 | 233.83
2019-04-24 16:30 | 240.03 | 233.29
2019-04-24 17:00 | 242.27 | 234.01
2019-04-24 17:30 | 243.89 | 235.59
2019-04-24 18:00 | 246.65 | 237.38
2019-04-24 18:30 | 250.33 | 240.57
2019-04-24 19:00 | 250.55 | 240.75
2019-04-24 19:30 | 249.6 | 239.56
2019-04-24 20:00 | 247.34 | 238.14
2019-04-24 20:30 | 245.96 | 237.44
2019-04-24 21:00 | 246.54 | 237.75
2019-04-24 21:30 | 245.35 | 237.26
2019-04-24 22:00 | 244.89 | 237.12
2019-04-24 22:30 | 244.48 | 236.22
2019-04-24 23:00 | 243.43 | 234.73
2019-04-24 23:30 | 243.05 | 234.49
2019-04-25 | 241.43 | 233.33
2019-04-25 00:30 | 240.21 | 232.54
2019-04-25 01:00 | 239.19 | 231.21
2019-04-25 01:30 | 238.37 | 230.64
2019-04-25 02:00 | 238.85 | 231.11
2019-04-25 02:30 | 239 | 231.16
2019-04-25 03:00 | 236.4 | 230.05
2019-04-25 03:30 | 235.5 | 229.62
2019-04-25 04:00 | 236.39 | 230.31
2019-04-25 04:30 | 236.47 | 230.36
2019-04-25 05:00 | 237.04 | 230.96
2019-04-25 05:30 | 238.2 | 232.3
2019-04-25 06:00 | 238.36 | 232.67
2019-04-25 06:30 | 238.68 | 233.24
2019-04-25 07:00 | 239.56 | 234.16
2019-04-25 07:30 | 236.57 | 229.9
2019-04-25 08:00 | 237.1 | 229.7
2019-04-25 08:30 | 236.42 | 228.2
2019-04-25 09:00 | 235.22 | 226.46
2019-04-25 09:30 | 234.53 | 225.68
2019-04-25 10:00 | 233.97 | 225.38
2019-04-25 10:30 | 232.38 | 223.41
2019-04-25 11:00 | 230.46 | 221.48
2019-04-25 11:30 | 230.78 | 221.83
2019-04-25 12:00 | 229.82 | 221.2
2019-04-25 12:30 | 227.91 | 219.9
2019-04-25 13:00 | 228.25 | 220.29
2019-04-25 13:30 | 229.49 | 221.63
2019-04-25 14:00 | 229.67 | 221.87
2019-04-25 14:30 | 229.35 | 221.31
2019-04-25 15:00 | 229.92 | 221.96
2019-04-25 15:30 | 229.92 | 221.79
2019-04-25 16:00 | 231.35 | 223.37
2019-04-25 16:30 | 231.7 | 224.05
2019-04-25 17:00 | 232.87 | 225.34
2019-04-25 17:30 | 235.16 | 227.74
2019-04-25 18:00 | 237.15 | 230.1
2019-04-25 18:30 | 240.9 | 233.88
2019-04-25 19:00 | 242.23 | 234.96
2019-04-25 19:30 | 241.48 | 233.8
2019-04-25 20:00 | 239.24 | 231.36
2019-04-25 20:30 | 238.43 | 230.47
2019-04-25 21:00 | 238.54 | 230.47
2019-04-25 21:30 | 239.19 | 231.09
2019-04-25 22:00 | 237.73 | 229.65
2019-04-25 22:30 | 235.75 | 227.73
2019-04-25 23:00 | 234.18 | 225.99
2019-04-25 23:30 | 233.84 | 225.94
2019-04-26 | 232.57 | 224.77
2019-04-26 00:30 | 232.39 | 224.46
2019-04-26 01:00 | 231.2 | 223.29
2019-04-26 01:30 | 230.3 | 222.73
2019-04-26 02:00 | 230.14 | 222.35
2019-04-26 02:30 | 230.04 | 222.1
2019-04-26 03:00 | 230 | 221.91
2019-04-26 03:30 | 230.16 | 222.16
2019-04-26 04:00 | 230.41 | 222.43
2019-04-26 04:30 | 230.84 | 222.84
2019-04-26 05:00 | 231.12 | 223.21
2019-04-26 05:30 | 232.59 | 224.77
2019-04-26 06:00 | 233.47 | 225.88
2019-04-26 06:30 | 234.69 | 227.7
2019-04-26 07:00 | 236.75 | 229.53
2019-04-26 07:30 | 237.08 | 229.91
2019-04-26 08:00 | 237.5 | 229.71
2019-04-26 08:30 | 236.18 | 227.6
2019-04-26 09:00 | 233.98 | 225.93
2019-04-26 09:30 | 232.55 | 224.49
2019-04-26 10:00 | 232.11 | 222.93
2019-04-26 10:30 | 232.23 | 222.12
2019-04-26 11:00 | 231.09 | 221.2
2019-04-26 11:30 | 230.45 | 220.65
2019-04-26 12:00 | 230.49 | 220.62
2019-04-26 12:30 | 231.11 | 221.35
2019-04-26 13:00 | 230.49 | 220.77
2019-04-26 13:30 | 231.73 | 222.07
2019-04-26 14:00 | 232.53 | 223.13
2019-04-26 14:30 | 232.7 | 223.33
2019-04-26 15:00 | 233.32 | 224.11
2019-04-26 15:30 | 235.09 | 225.8
2019-04-26 16:00 | 236.2 | 227.06
2019-04-26 16:30 | 237.07 | 228.08
2019-04-26 17:00 | 237.33 | 228.82
2019-04-26 17:30 | 238.47 | 229.57
2019-04-26 18:00 | 240.11 | 231.38
2019-04-26 18:30 | 243.21 | 234.43
2019-04-26 19:00 | 244.63 | 235.57
2019-04-26 19:30 | 244.4 | 234.91
2019-04-26 20:00 | 243.54 | 233.82
2019-04-26 20:30 | 242.96 | 232.94
2019-04-26 21:00 | 243.36 | 232.96
2019-04-26 21:30 | 242.5 | 233.03
2019-04-26 22:00 | 241.46 | 232.45
2019-04-26 22:30 | 240.11 | 231.02
2019-04-26 23:00 | 239.74 | 230.33
2019-04-26 23:30 | 239.01 | 229.63
2019-04-27 | 236.76 | 228.8
2019-04-27 00:30 | 236.04 | 228.18
2019-04-27 01:00 | 234.34 | 227.41
2019-04-27 01:30 | 233.42 | 226.17
2019-04-27 02:00 | 233.76 | 226.54
2019-04-27 02:30 | 233.64 | 226.36
2019-04-27 03:00 | 233.54 | 226.2
2019-04-27 03:30 | 233.65 | 226.33
2019-04-27 04:00 | 233.71 | 226.39
2019-04-27 04:30 | 233.73 | 226.41
2019-04-27 05:00 | 234.04 | 226.83
2019-04-27 05:30 | 235.05 | 227.95
2019-04-27 06:00 | 238.41 | 231.71
2019-04-27 06:30 | 239.38 | 232.73
2019-04-27 07:00 | 240.59 | 234.05
2019-04-27 07:30 | 236.62 | 229.92
2019-04-27 08:00 | 235 | 228.47
2019-04-27 08:30 | 234.2 | 227.51
2019-04-27 09:00 | 233.48 | 226.74
2019-04-27 09:30 | 231.75 | 225.46
2019-04-27 10:00 | 230.86 | 223.63
2019-04-27 10:30 | 229.51 | 221.72
2019-04-27 11:00 | 227.86 | 220.11
2019-04-27 11:30 | 227.84 | 219.64
2019-04-27 12:00 | 228.79 | 219.48
2019-04-27 12:30 | 228.17 | 218.98
2019-04-27 13:00 | 227.51 | 217.91
2019-04-27 13:30 | 227.36 | 217.8
2019-04-27 14:00 | 228.43 | 218.44
2019-04-27 14:30 | 229.53 | 219.28
2019-04-27 15:00 | 230.61 | 220.2
2019-04-27 15:30 | 232.19 | 221.73
2019-04-27 16:00 | 233.87 | 223.41
2019-04-27 16:30 | 235.82 | 225.7
2019-04-27 17:00 | 237.42 | 227.79
2019-04-27 17:30 | 239.9 | 230
2019-04-27 18:00 | 242.38 | 232.47
2019-04-27 18:30 | 245.31 | 235.31
2019-04-27 19:00 | 246.33 | 236.24
2019-04-27 19:30 | 245.32 | 235.01
2019-04-27 20:00 | 242.48 | 233.56
2019-04-27 20:30 | 242.61 | 233.57
2019-04-27 21:00 | 240.89 | 231.97
2019-04-27 21:30 | 240.51 | 231.83
2019-04-27 22:00 | 239.19 | 230.58
2019-04-27 22:30 | 237.89 | 229.65
2019-04-27 23:00 | 236.7 | 228.16
2019-04-27 23:30 | 236.37 | 227.9
2019-04-28 | 233.62 | 226.52
2019-04-28 00:30 | 233.51 | 226.24
2019-04-28 01:00 | 232.06 | 225.07
2019-04-28 01:30 | 230.79 | 224.38
2019-04-28 02:00 | 229.97 | 223.5
2019-04-28 02:30 | 229.92 | 223.41
2019-04-28 03:00 | 230.53 | 223.98
2019-04-28 03:30 | 230.62 | 223.9
2019-04-28 04:00 | 230.92 | 224.15
2019-04-28 04:30 | 229.39 | 222.59
2019-04-28 05:00 | 229.87 | 223.08
2019-04-28 05:30 | 230.59 | 223.14
2019-04-28 06:00 | 233.26 | 225.92
2019-04-28 06:30 | 233.99 | 227.03
2019-04-28 07:00 | 234.66 | 227.89
2019-04-28 07:30 | 232.97 | 226.45
2019-04-28 08:00 | 232.56 | 226.23
2019-04-28 08:30 | 232.3 | 225.61
2019-04-28 09:00 | 231.87 | 224.91
2019-04-28 09:30 | 232.48 | 224.2
2019-04-28 10:00 | 230.64 | 221.8
2019-04-28 10:30 | 228.91 | 220.15
2019-04-28 11:00 | 229.68 | 220.77
2019-04-28 11:30 | 230.07 | 221.72
2019-04-28 12:00 | 229.25 | 221.09
2019-04-28 12:30 | 230.02 | 221.27
2019-04-28 13:00 | 231.28 | 221.27
2019-04-28 13:30 | 231.2 | 221.33
2019-04-28 14:00 | 229.93 | 221.55
2019-04-28 14:30 | 230.8 | 222.26
2019-04-28 15:00 | 231.71 | 222.73
2019-04-28 15:30 | 234.04 | 224.18
2019-04-28 16:00 | 235.45 | 224.67
2019-04-28 16:30 | 235.73 | 225.14
2019-04-28 17:00 | 238.33 | 227.83
2019-04-28 17:30 | 240.96 | 230.56
2019-04-28 18:00 | 241.86 | 233.81
2019-04-28 18:30 | 253.53 | 250.68
2019-04-28 19:00 | 253.12 | 250.21
2019-04-28 19:30 | 253.88 | 250.91
2019-04-28 20:00 | 254.22 | 251.29
2019-04-28 20:30 | 243.27 | 236.32
2019-04-28 21:00 | 239.96 | 232.51
2019-04-28 21:30 | 238.55 | 231.68
2019-04-28 22:00 | 237.61 | 230.38
2019-04-28 22:30 | 235.76 | 228.88
2019-04-28 23:00 | 234.53 | 227.47
2019-04-28 23:30 | 233.7 | 226.54
2019-04-29 | 231.98 | 225.36
2019-04-29 00:30 | 231.22 | 225.12
2019-04-29 01:00 | 231.65 | 225.07
2019-04-29 01:30 | 230.41 | 224.68
2019-04-29 02:00 | 231.21 | 224.48
2019-04-29 02:30 | 231.36 | 224.17
2019-04-29 03:00 | 231.28 | 223.77
2019-04-29 03:30 | 231.32 | 223.77
2019-04-29 04:00 | 231.15 | 223.87
2019-04-29 04:30 | 231.03 | 223.63
2019-04-29 05:00 | 232.19 | 224.76
2019-04-29 05:30 | 233.12 | 225.85
2019-04-29 06:00 | 235.19 | 228.11
2019-04-29 06:30 | 239.16 | 230.75
2019-04-29 07:00 | 240.83 | 232.91
2019-04-29 07:30 | 240.35 | 231.47
2019-04-29 08:00 | 238.34 | 229.52
2019-04-29 08:30 | 234.59 | 226.33
2019-04-29 09:00 | 234.89 | 226.92
2019-04-29 09:30 | 232.95 | 224.91
2019-04-29 10:00 | 231.88 | 223.84
2019-04-29 10:30 | 230.24 | 221.88
2019-04-29 11:00 | 229.32 | 221.1
2019-04-29 11:30 | 228.97 | 220.68
2019-04-29 12:00 | 228.42 | 219.9
2019-04-29 12:30 | 228.37 | 219.73
2019-04-29 13:00 | 227.87 | 219.34
2019-04-29 13:30 | 228.08 | 219.48
2019-04-29 14:00 | 228.57 | 220.37
2019-04-29 14:30 | 229.21 | 221.46
2019-04-29 15:00 | 230.32 | 222.64
2019-04-29 15:30 | 232.82 | 224.84
2019-04-29 16:00 | 233.85 | 226.03
2019-04-29 16:30 | 235.21 | 227.28
2019-04-29 17:00 | 236.99 | 228.91
2019-04-29 17:30 | 239.6 | 231.14
2019-04-29 18:00 | 243.3 | 234.35
2019-04-29 18:30 | 247.87 | 238.72
2019-04-29 19:00 | 248.22 | 238.89
2019-04-29 19:30 | 247.07 | 237.44
2019-04-29 20:00 | 245.33 | 236.01
2019-04-29 20:30 | 242.6 | 234.9
2019-04-29 21:00 | 240.23 | 232.78
2019-04-29 21:30 | 238.66 | 232.57
2019-04-29 22:00 | 237.34 | 231.56
2019-04-29 22:30 | 236.16 | 230.24
2019-04-29 23:00 | 234.74 | 228.91
2019-04-29 23:30 | 234.22 | 227.74
2019-04-30 | 233.15 | 226.52
2019-04-30 00:30 | 232.72 | 226.15
2019-04-30 01:00 | 231.76 | 225.13
2019-04-30 01:30 | 231.83 | 224.52
2019-04-30 02:00 | 232.02 | 224.62
2019-04-30 02:30 | 231.84 | 224.68
2019-04-30 03:00 | 231.49 | 224.37
2019-04-30 03:30 | 231.65 | 224.4
2019-04-30 04:00 | 232.15 | 224.86
2019-04-30 04:30 | 230.8 | 223.58
2019-04-30 05:00 | 231.02 | 223.91
2019-04-30 05:30 | 232.19 | 225.27
2019-04-30 06:00 | 234.37 | 227.42
2019-04-30 06:30 | 235.51 | 228.36
2019-04-30 07:00 | 238.59 | 230.16
2019-04-30 07:30 | 238.47 | 229.82
2019-04-30 08:00 | 238.39 | 229.77
2019-04-30 08:30 | 236.68 | 227.94
2019-04-30 09:00 | 235.19 | 226.47
2019-04-30 09:30 | 197.65 | 188.92
2019-04-30 10:00 | 168.48 | 159.82
2019-04-30 10:30 | 167.92 | 159.06
2019-04-30 11:00 | 168.2 | 159.37
2019-04-30 11:30 | 167.27 | 158.2
2019-04-30 12:00 | 167.17 | 158.4
2019-04-30 12:30 | 166.83 | 157.76
2019-04-30 13:00 | 166.24 | 157.41
2019-04-30 13:30 | 167.29 | 158.24
2019-04-30 14:00 | 169.12 | 160.85
2019-04-30 14:30 | 168.98 | 160.76
2019-04-30 15:00 | 201.38 | 193.78
2019-04-30 15:30 | 231.17 | 223.7
2019-04-30 16:00 | 237.69 | 229.77
2019-04-30 16:30 | 238.03 | 229.9
2019-04-30 17:00 | 238.49 | 230.17
2019-04-30 17:30 | 246.39 | 240.88
2019-04-30 18:00 | 256.08 | 251.75
2019-04-30 18:30 | 254.09 | 249.85
2019-04-30 19:00 | 253.8 | 249.5
2019-04-30 19:30 | 229.53 | 222.58
2019-04-30 20:00 | 241.18 | 232.34
2019-04-30 20:30 | 245.58 | 236.17
2019-04-30 21:00 | 244.66 | 234.76
2019-04-30 21:30 | 243.85 | 234.17
2019-04-30 22:00 | 242.89 | 232.91
2019-04-30 22:30 | 241.18 | 230.94
2019-04-30 23:00 | 239.91 | 229.04
2019-04-30 23:30 | 237.06 | 228.1
2019-05-01 | 234.06 | 226.72
2019-05-01 00:30 | 232.61 | 226
2019-05-01 01:00 | 231.92 | 225.25
2019-05-01 01:30 | 231.35 | 224.79
2019-05-01 02:00 | 231.11 | 224.44
2019-05-01 02:30 | 231.08 | 224.25
2019-05-01 03:00 | 231.12 | 224.19
2019-05-01 03:30 | 231.27 | 224.29
2019-05-01 04:00 | 231.34 | 224.3
2019-05-01 04:30 | 232.01 | 225.2
2019-05-01 05:00 | 232.5 | 225.8
2019-05-01 05:30 | 234.49 | 227.81
2019-05-01 06:00 | 236.9 | 229.48
2019-05-01 06:30 | 239.9 | 232.2
2019-05-01 07:00 | 243.26 | 234.38
2019-05-01 07:30 | 242.56 | 233.83
2019-05-01 08:00 | 242.03 | 233.69
2019-05-01 08:30 | 240.69 | 232.62
2019-05-01 09:00 | 239.11 | 231.18
2019-05-01 09:30 | 236.95 | 228.85
2019-05-01 10:00 | 234.94 | 227.29
2019-05-01 10:30 | 234.79 | 227.09
2019-05-01 11:00 | 234.05 | 226.4
2019-05-01 11:30 | 237.48 | 229.71
2019-05-01 12:00 | 239.34 | 231.42
2019-05-01 12:30 | 239.59 | 231.34
2019-05-01 13:00 | 238.51 | 230.31
2019-05-01 13:30 | 239.65 | 231.16
2019-05-01 14:00 | 239.9 | 232.06
2019-05-01 14:30 | 240.32 | 231.45
2019-05-01 15:00 | 240.93 | 231.65
2019-05-01 15:30 | 242.31 | 233.3
2019-05-01 16:00 | 243.94 | 234.82
2019-05-01 16:30 | 244.66 | 235.48
2019-05-01 17:00 | 245.19 | 235.92
2019-05-01 17:30 | 246.32 | 237.26
2019-05-01 18:00 | 252.49 | 248.07
2019-05-01 18:30 | 255.5 | 251.45
2019-05-01 19:00 | 254.3 | 250.51
2019-05-01 19:30 | 229.31 | 223.52
2019-05-01 20:00 | 242.23 | 234.9
2019-05-01 20:30 | 247.76 | 240.03
2019-05-01 21:00 | 248.81 | 240.55
2019-05-01 21:30 | 249 | 240.9
2019-05-01 22:00 | 247.06 | 239.67
2019-05-01 22:30 | 246.48 | 239.02
2019-05-01 23:00 | 244.46 | 237.96
2019-05-01 23:30 | 242.01 | 235.41
2019-05-02 | 240.23 | 233.9
2019-05-02 00:30 | 239.18 | 232.47
2019-05-02 01:00 | 238.13 | 231.41
2019-05-02 01:30 | 238.03 | 230.9
2019-05-02 02:00 | 237.36 | 230.3
2019-05-02 02:30 | 236.07 | 229
2019-05-02 03:00 | 237.39 | 230.16
2019-05-02 03:30 | 236.95 | 229.83
2019-05-02 04:00 | 237.36 | 230.35
2019-05-02 04:30 | 236.52 | 229.44
2019-05-02 05:00 | 239.2 | 232.04
2019-05-02 05:30 | 242.02 | 234.05
2019-05-02 06:00 | 244.03 | 235.7
2019-05-02 06:30 | 245.84 | 238.15
2019-05-02 07:00 | 248.44 | 240.36
2019-05-02 07:30 | 245.81 | 237.62
2019-05-02 08:00 | 244.08 | 235.09
2019-05-02 08:30 | 241.32 | 232.99
2019-05-02 09:00 | 241.33 | 232.06
2019-05-02 09:30 | 239.59 | 230.96
2019-05-02 10:00 | 237.31 | 229.27
2019-05-02 10:30 | 237.14 | 228.88
2019-05-02 11:00 | 235.69 | 227.84
2019-05-02 11:30 | 236.1 | 228.56
2019-05-02 12:00 | 235.72 | 228.3
2019-05-02 12:30 | 235.58 | 228.33
2019-05-02 13:00 | 236.29 | 228.96
2019-05-02 13:30 | 236.69 | 229.16
2019-05-02 14:00 | 237.32 | 229.82
2019-05-02 14:30 | 238.34 | 230.83
2019-05-02 15:00 | 240.3 | 232.53
2019-05-02 15:30 | 241.79 | 234.11
2019-05-02 16:00 | 243.81 | 236.08
2019-05-02 16:30 | 243.63 | 235.79
2019-05-02 17:00 | 244.99 | 237.29
2019-05-02 17:30 | 245.93 | 238.24
2019-05-02 18:00 | 249.27 | 241.74
2019-05-02 18:30 | 253.41 | 245.82
2019-05-02 19:00 | 254.26 | 246.44
2019-05-02 19:30 | 253.49 | 245.49
2019-05-02 20:00 | 251 | 243.03
2019-05-02 20:30 | 249.96 | 242.02
2019-05-02 21:00 | 248.87 | 241.34
2019-05-02 21:30 | 248.01 | 242.62
2019-05-02 22:00 | 247.12 | 241.62
2019-05-02 22:30 | 245.05 | 239.9
2019-05-02 23:00 | 243.85 | 238.55
2019-05-02 23:30 | 245.52 | 239.95
2019-05-03 | 242.62 | 237.02
2019-05-03 00:30 | 240.49 | 234.94
2019-05-03 01:00 | 239.63 | 233.47
2019-05-03 01:30 | 239.45 | 232.85
2019-05-03 02:00 | 238.66 | 232.43
2019-05-03 02:30 | 238.25 | 231.94
2019-05-03 03:00 | 238.19 | 231.99
2019-05-03 03:30 | 238.18 | 231.98
2019-05-03 04:00 | 238.56 | 232.27
2019-05-03 04:30 | 239.01 | 232.85
2019-05-03 05:00 | 239.91 | 233.87
2019-05-03 05:30 | 241.17 | 235.46
2019-05-03 06:00 | 243.13 | 237.82
2019-05-03 06:30 | 245.51 | 240.19
2019-05-03 07:00 | 251.77 | 242.96
2019-05-03 07:30 | 247.44 | 239.33
2019-05-03 08:00 | 247.16 | 239.21
2019-05-03 08:30 | 244.97 | 236.7
2019-05-03 09:00 | 243.36 | 233.76
2019-05-03 09:30 | 241.98 | 233.27
2019-05-03 10:00 | 240.73 | 232.91
2019-05-03 10:30 | 239.06 | 231.09
2019-05-03 11:00 | 239.36 | 231.52
2019-05-03 11:30 | 238.7 | 230.9
2019-05-03 12:00 | 239.3 | 231.54
2019-05-03 12:30 | 240.55 | 232.6
2019-05-03 13:00 | 241 | 232.82
2019-05-03 13:30 | 241.54 | 233.4
2019-05-03 14:00 | 240.4 | 232.05
2019-05-03 14:30 | 241.8 | 233.27
2019-05-03 15:00 | 241.19 | 232.72
2019-05-03 15:30 | 240.72 | 232.28
2019-05-03 16:00 | 237.48 | 229.05
2019-05-03 16:30 | 237.88 | 229.56
2019-05-03 17:00 | 238.36 | 230.13
2019-05-03 17:30 | 239.61 | 231.32
2019-05-03 18:00 | 241.72 | 233.53
2019-05-03 18:30 | 244.58 | 236.32
2019-05-03 19:00 | 244.98 | 236.52
2019-05-03 19:30 | 243.63 | 235.08
2019-05-03 20:00 | 242.12 | 233.6
2019-05-03 20:30 | 241.54 | 233.05
2019-05-03 21:00 | 241.1 | 233.05
2019-05-03 21:30 | 240.49 | 234.14
2019-05-03 22:00 | 239.55 | 233.53
2019-05-03 22:30 | 237.59 | 232
2019-05-03 23:00 | 236.8 | 231.09
2019-05-03 23:30 | 236.34 | 230.42
2019-05-04 | 235.5 | 229.7
2019-05-04 00:30 | 234.99 | 228.73
2019-05-04 01:00 | 234.75 | 228.12
2019-05-04 01:30 | 234.1 | 227.55
2019-05-04 02:00 | 233.59 | 227.01
2019-05-04 02:30 | 233.65 | 226.89
2019-05-04 03:00 | 232.9 | 226.21
2019-05-04 03:30 | 232.87 | 226.07
2019-05-04 04:00 | 232.92 | 226.23
2019-05-04 04:30 | 232.95 | 225.99
2019-05-04 05:00 | 233.11 | 226.09
2019-05-04 05:30 | 233.18 | 226.27
2019-05-04 06:00 | 233.68 | 226.92
2019-05-04 06:30 | 234.59 | 228.17
2019-05-04 07:00 | 234.61 | 228.23
2019-05-04 07:30 | 232.44 | 226.27
2019-05-04 08:00 | 233.66 | 226.87
2019-05-04 08:30 | 235.03 | 227.79
2019-05-04 09:00 | 235.35 | 227.45
2019-05-04 09:30 | 235.12 | 225.95
2019-05-04 10:00 | 234.07 | 224.78
2019-05-04 10:30 | 232.85 | 223.16
2019-05-04 11:00 | 232 | 222.01
2019-05-04 11:30 | 233.43 | 223.73
2019-05-04 12:00 | 231.66 | 223.54
2019-05-04 12:30 | 230.59 | 222.4
2019-05-04 13:00 | 228.17 | 219.6
2019-05-04 13:30 | 227.42 | 218.72
2019-05-04 14:00 | 226.24 | 217.52
2019-05-04 14:30 | 226.28 | 217.49
2019-05-04 15:00 | 227.64 | 218.76
2019-05-04 15:30 | 228.6 | 219.62
2019-05-04 16:00 | 229.83 | 220.78
2019-05-04 16:30 | 231.28 | 222.34
2019-05-04 17:00 | 233.4 | 224.72
2019-05-04 17:30 | 236.76 | 228.14
2019-05-04 18:00 | 245.1 | 240.27
2019-05-04 18:30 | 255.65 | 252.97
2019-05-04 19:00 | 256.18 | 253.45
2019-05-04 19:30 | 257.79 | 255.03
2019-05-04 20:00 | 242.03 | 235.13
2019-05-04 20:30 | 241.37 | 233.03
2019-05-04 21:00 | 241.4 | 233.17
2019-05-04 21:30 | 241.41 | 233.71
2019-05-04 22:00 | 240.49 | 232.72
2019-05-04 22:30 | 239.45 | 231.38
2019-05-04 23:00 | 239.06 | 230.75
2019-05-04 23:30 | 237.93 | 230.6
2019-05-05 | 236.2 | 229.14
2019-05-05 00:30 | 235.82 | 228.85
2019-05-05 01:00 | 234.94 | 227.86
2019-05-05 01:30 | 234.81 | 227.55
2019-05-05 02:00 | 234.15 | 226.89
2019-05-05 02:30 | 234.24 | 226.9
2019-05-05 03:00 | 233.11 | 226.85
2019-05-05 03:30 | 232.87 | 226.82
2019-05-05 04:00 | 233.14 | 227.04
2019-05-05 04:30 | 233.52 | 227.44
2019-05-05 05:00 | 233.63 | 227.58
2019-05-05 05:30 | 234.45 | 228.48
2019-05-05 06:00 | 235.25 | 229.34
2019-05-05 06:30 | 236.04 | 230.48
2019-05-05 07:00 | 235.74 | 230.41
2019-05-05 07:30 | 234.19 | 229.12
2019-05-05 08:00 | 233.31 | 228.53
2019-05-05 08:30 | 232.09 | 227.58
2019-05-05 09:00 | 231.75 | 226.22
2019-05-05 09:30 | 229.33 | 223.82
2019-05-05 10:00 | 227.51 | 222.2
2019-05-05 10:30 | 226.35 | 221.04
2019-05-05 11:00 | 225.07 | 219.72
2019-05-05 11:30 | 225.28 | 219.79
2019-05-05 12:00 | 225.56 | 219.97
2019-05-05 12:30 | 224.6 | 218.88
2019-05-05 13:00 | 224.29 | 218.5
2019-05-05 13:30 | 223.4 | 217.84
2019-05-05 14:00 | 225.2 | 217.72
2019-05-05 14:30 | 227.02 | 218.32
2019-05-05 15:00 | 229.58 | 220.35
2019-05-05 15:30 | 230.57 | 221.4
2019-05-05 16:00 | 232.99 | 223.56
2019-05-05 16:30 | 235.22 | 225.77
2019-05-05 17:00 | 237.78 | 228.34
2019-05-05 17:30 | 240.56 | 230.58
2019-05-05 18:00 | 243.42 | 233.53
2019-05-05 18:30 | 246.01 | 236.15
2019-05-05 19:00 | 245.55 | 235.53
2019-05-05 19:30 | 244.68 | 234.62
2019-05-05 20:00 | 243.75 | 233.74
2019-05-05 20:30 | 242.22 | 233.49
2019-05-05 21:00 | 240.08 | 232.15
2019-05-05 21:30 | 238.15 | 231.46
2019-05-05 22:00 | 236.79 | 230.72
2019-05-05 22:30 | 235.29 | 229.07
2019-05-05 23:00 | 234.55 | 228.19
2019-05-05 23:30 | 233.22 | 227.34
2019-05-06 | 232.96 | 226.75
2019-05-06 00:30 | 232.48 | 226.13
2019-05-06 01:00 | 231.64 | 225.36
2019-05-06 01:30 | 230.62 | 224.22
2019-05-06 02:00 | 230.41 | 224
2019-05-06 02:30 | 230.16 | 223.63
2019-05-06 03:00 | 230.26 | 223.71
2019-05-06 03:30 | 230.27 | 223.69
2019-05-06 04:00 | 230.22 | 223.6
2019-05-06 04:30 | 230.93 | 224.36
2019-05-06 05:00 | 231.14 | 224.63
2019-05-06 05:30 | 232.06 | 225.66
2019-05-06 06:00 | 233.05 | 226.75
2019-05-06 06:30 | 234.62 | 228.75
2019-05-06 07:00 | 236.12 | 230.71
2019-05-06 07:30 | 236.84 | 231.88
2019-05-06 08:00 | 239.28 | 234.42
2019-05-06 08:30 | 223.1 | 218.21
2019-05-06 09:00 | 216.19 | 211.38
2019-05-06 09:30 | 213.64 | 208.66
2019-05-06 10:00 | 212.98 | 207.18
2019-05-06 10:30 | 213.29 | 207.46
2019-05-06 11:00 | 211.91 | 206.07
2019-05-06 11:30 | 211.38 | 205.35
2019-05-06 12:00 | 211.86 | 204.66
2019-05-06 12:30 | 214.73 | 204.81
2019-05-06 13:00 | 210.99 | 201.62
2019-05-06 13:30 | 208.35 | 199.22
2019-05-06 14:00 | 207.78 | 198.89
2019-05-06 14:30 | 208.08 | 199.15
2019-05-06 15:00 | 209.08 | 200.02
2019-05-06 15:30 | 210.58 | 201.37
2019-05-06 16:00 | 227.26 | 217.96
2019-05-06 16:30 | 237.29 | 226.83
2019-05-06 17:00 | 240.54 | 231.66
2019-05-06 17:30 | 257.95 | 253.59
2019-05-06 18:00 | 254.99 | 250.66
2019-05-06 18:30 | 253.28 | 248.73
2019-05-06 19:00 | 251.81 | 249.01
2019-05-06 19:30 | 251.97 | 249.99
2019-05-06 20:00 | 252.58 | 250.64
2019-05-06 20:30 | 252.7 | 250.74
2019-05-06 21:00 | 241.95 | 237.4
2019-05-06 21:30 | 243.3 | 238.11
2019-05-06 22:00 | 242.11 | 236.63
2019-05-06 22:30 | 239.48 | 234.26
2019-05-06 23:00 | 238.37 | 233.22
2019-05-06 23:30 | 238.38 | 233.13
2019-05-07 | 233.77 | 229.02
2019-05-07 00:30 | 232.08 | 227.79
2019-05-07 01:00 | 231.34 | 227.12
2019-05-07 01:30 | 230.53 | 226.4
2019-05-07 02:00 | 230.42 | 226.23
2019-05-07 02:30 | 229.69 | 225.53
2019-05-07 03:00 | 229.64 | 225.48
2019-05-07 03:30 | 230.26 | 225.92
2019-05-07 04:00 | 230.18 | 225.67
2019-05-07 04:30 | 231.65 | 227.2
2019-05-07 05:00 | 233.67 | 229.3
2019-05-07 05:30 | 235.52 | 231.19
2019-05-07 06:00 | 237.78 | 233.67
2019-05-07 06:30 | 241.78 | 237.94
2019-05-07 07:00 | 245.35 | 241.33
2019-05-07 07:30 | 241.88 | 237.52
2019-05-07 08:00 | 239.48 | 235.07
2019-05-07 08:30 | 235.58 | 230.76
2019-05-07 09:00 | 232.88 | 227.79
2019-05-07 09:30 | 230.73 | 225.38
2019-05-07 10:00 | 213.11 | 207.92
2019-05-07 10:30 | 209.49 | 204.3
2019-05-07 11:00 | 208.06 | 202.9
2019-05-07 11:30 | 207.01 | 202.11
2019-05-07 12:00 | 207.35 | 202.37
2019-05-07 12:30 | 207.84 | 202.3
2019-05-07 13:00 | 207.71 | 202.07
2019-05-07 13:30 | 208.71 | 202.65
2019-05-07 14:00 | 209.2 | 203.31
2019-05-07 14:30 | 209.69 | 203.64
2019-05-07 15:00 | 210.44 | 204.42
2019-05-07 15:30 | 211.43 | 205.5
2019-05-07 16:00 | 220.9 | 215.17
2019-05-07 16:30 | 224.44 | 218.66
2019-05-07 17:00 | 226.5 | 220.77
2019-05-07 17:30 | 229.36 | 223.61
2019-05-07 18:00 | 238.53 | 236.88
2019-05-07 18:30 | 239.91 | 238.52
2019-05-07 19:00 | 239.91 | 238.49
2019-05-07 19:30 | 239.8 | 238.46
2019-05-07 20:00 | 240.53 | 239.29
2019-05-07 20:30 | 233.44 | 228.91
2019-05-07 21:00 | 234.84 | 229.03
2019-05-07 21:30 | 234.46 | 229.36
2019-05-07 22:00 | 234.08 | 229.09
2019-05-07 22:30 | 230.53 | 225.35
2019-05-07 23:00 | 228.89 | 223.45
2019-05-07 23:30 | 227.67 | 222.13
2019-05-08 | 226.87 | 221.85
2019-05-08 00:30 | 225.91 | 221.26
2019-05-08 01:00 | 225.75 | 220.98
2019-05-08 01:30 | 225.64 | 220.77
2019-05-08 02:00 | 223.96 | 219.04
2019-05-08 02:30 | 224.96 | 220.07
2019-05-08 03:00 | 224.19 | 219.3
2019-05-08 03:30 | 224.36 | 219.5
2019-05-08 04:00 | 224.13 | 219.26
2019-05-08 04:30 | 224.88 | 220.02
2019-05-08 05:00 | 223.65 | 218.78
2019-05-08 05:30 | 224.86 | 220.08
2019-05-08 06:00 | 228.09 | 223.77
2019-05-08 06:30 | 231.38 | 227.53
2019-05-08 07:00 | 235.61 | 231.04
2019-05-08 07:30 | 233.12 | 228.24
2019-05-08 08:00 | 233.91 | 228.97
2019-05-08 08:30 | 229.39 | 223.85
2019-05-08 09:00 | 224.9 | 219.07
2019-05-08 09:30 | 221.54 | 215.7
2019-05-08 10:00 | 222.84 | 217.13
2019-05-08 10:30 | 221.22 | 215.85
2019-05-08 11:00 | 219.89 | 214.36
2019-05-08 11:30 | 219.13 | 213.72
2019-05-08 12:00 | 218.61 | 212.89
2019-05-08 12:30 | 219.67 | 213.55
2019-05-08 13:00 | 218.88 | 212.77
2019-05-08 13:30 | 219.7 | 213.3
2019-05-08 14:00 | 228.08 | 221.64
2019-05-08 14:30 | 231.86 | 225.63
2019-05-08 15:00 | 233.1 | 226.8
2019-05-08 15:30 | 233.59 | 227.3
2019-05-08 16:00 | 234.91 | 228.91
2019-05-08 16:30 | 236.11 | 230.3
2019-05-08 17:00 | 238.48 | 232.62
2019-05-08 17:30 | 240.17 | 234.45
2019-05-08 18:00 | 243.27 | 238.51
2019-05-08 18:30 | 246 | 241.36
2019-05-08 19:00 | 248.34 | 243.59
2019-05-08 19:30 | 247.52 | 242.55
2019-05-08 20:00 | 246.76 | 241.72
2019-05-08 20:30 | 246.22 | 241.09
2019-05-08 21:00 | 245.32 | 240.47
2019-05-08 21:30 | 245.41 | 241.13
2019-05-08 22:00 | 243.43 | 239.43
2019-05-08 22:30 | 241.3 | 237.13
2019-05-08 23:00 | 239.59 | 235.43
2019-05-08 23:30 | 238.3 | 234.64
2019-05-09 | 237.69 | 233.85
2019-05-09 00:30 | 236.93 | 232.93
2019-05-09 01:00 | 235.99 | 232
2019-05-09 01:30 | 235.64 | 231.46
2019-05-09 02:00 | 235.31 | 231.06
2019-05-09 02:30 | 234.98 | 230.72
2019-05-09 03:00 | 235.27 | 230.99
2019-05-09 03:30 | 235.25 | 230.98
2019-05-09 04:00 | 235.28 | 231.01
2019-05-09 04:30 | 236.42 | 232.28
2019-05-09 05:00 | 237.87 | 233.8
2019-05-09 05:30 | 239.35 | 235.45
2019-05-09 06:00 | 241.91 | 238.34
2019-05-09 06:30 | 244.81 | 241.54
2019-05-09 07:00 | 248.79 | 245.24
2019-05-09 07:30 | 244.68 | 240.64
2019-05-09 08:00 | 243.6 | 239.16
2019-05-09 08:30 | 239.14 | 234.64
2019-05-09 09:00 | 235.88 | 230.91
2019-05-09 09:30 | 232.82 | 228.08
2019-05-09 10:00 | 232.07 | 227.7
2019-05-09 10:30 | 231.48 | 227
2019-05-09 11:00 | 230.21 | 225.46
2019-05-09 11:30 | 230.23 | 225.21
2019-05-09 12:00 | 229.42 | 224.42
2019-05-09 12:30 | 229.96 | 224.84
2019-05-09 13:00 | 229.6 | 224.69
2019-05-09 13:30 | 230.11 | 225.19
2019-05-09 14:00 | 230.71 | 225.52
2019-05-09 14:30 | 231.81 | 226.22
2019-05-09 15:00 | 232.51 | 226.56
2019-05-09 15:30 | 233.08 | 227.18
2019-05-09 16:00 | 234.67 | 228.72
2019-05-09 16:30 | 236.31 | 230.35
2019-05-09 17:00 | 237.98 | 231.98
2019-05-09 17:30 | 240.74 | 234.39
2019-05-09 18:00 | 243.49 | 237.34
2019-05-09 18:30 | 247.52 | 241.68
2019-05-09 19:00 | 248.58 | 242.8
2019-05-09 19:30 | 246.94 | 240.99
2019-05-09 20:00 | 245.84 | 239.75
2019-05-09 20:30 | 245.88 | 239.65
2019-05-09 21:00 | 245.99 | 239.82
2019-05-09 21:30 | 246.52 | 240.78
2019-05-09 22:00 | 244.81 | 239.31
2019-05-09 22:30 | 242.36 | 236.86
2019-05-09 23:00 | 240.74 | 235.3
2019-05-09 23:30 | 239.36 | 233.75
2019-05-10 | 237.97 | 232.47
2019-05-10 00:30 | 236.18 | 231.61
2019-05-10 01:00 | 231.73 | 227.38
2019-05-10 01:30 | 230.28 | 225.75
2019-05-10 02:00 | 230.09 | 225.47
2019-05-10 02:30 | 229.8 | 225.19
2019-05-10 03:00 | 230.26 | 225.58
2019-05-10 03:30 | 230.18 | 225.45
2019-05-10 04:00 | 230.25 | 225.52
2019-05-10 04:30 | 230.95 | 226.33
2019-05-10 05:00 | 231.49 | 227.1
2019-05-10 05:30 | 232.94 | 228.62
2019-05-10 06:00 | 235.3 | 230.64
2019-05-10 06:30 | 238.11 | 233.36
2019-05-10 07:00 | 239.75 | 235.24
2019-05-10 07:30 | 238.53 | 234.17
2019-05-10 08:00 | 245.61 | 241.83
2019-05-10 08:30 | 243.82 | 239.98
2019-05-10 09:00 | 240.99 | 237.22
2019-05-10 09:30 | 239.46 | 235.88
2019-05-10 10:00 | 236.45 | 232.61
2019-05-10 10:30 | 229.09 | 224.34
2019-05-10 11:00 | 226.21 | 221.1
2019-05-10 11:30 | 224.06 | 218.88
2019-05-10 12:00 | 223.35 | 218.23
2019-05-10 12:30 | 223.66 | 218.46
2019-05-10 13:00 | 224.07 | 218.61
2019-05-10 13:30 | 222.03 | 216.44
2019-05-10 14:00 | 221.33 | 215.48
2019-05-10 14:30 | 222.22 | 216.07
2019-05-10 15:00 | 223.3 | 217.26
2019-05-10 15:30 | 224.94 | 218.75
2019-05-10 16:00 | 226.64 | 220.43
2019-05-10 16:30 | 228.86 | 222.72
2019-05-10 17:00 | 231.11 | 225.1
2019-05-10 17:30 | 234.16 | 228.17
2019-05-10 18:00 | 237.59 | 232.09
2019-05-10 18:30 | 240.64 | 235.39
2019-05-10 19:00 | 241.56 | 236.29
2019-05-10 19:30 | 241.12 | 235.76
2019-05-10 20:00 | 242.45 | 237.47
2019-05-10 20:30 | 244.69 | 239.78
2019-05-10 21:00 | 244.49 | 239.6
2019-05-10 21:30 | 245.03 | 240.04
2019-05-10 22:00 | 244.12 | 239.08
2019-05-10 22:30 | 242.82 | 237.53
2019-05-10 23:00 | 239.56 | 234
2019-05-10 23:30 | 237.03 | 231.98
2019-05-11 | 235.26 | 230.87
2019-05-11 00:30 | 234.74 | 230.24
2019-05-11 01:00 | 233.92 | 229.31
2019-05-11 01:30 | 233.25 | 228.68
2019-05-11 02:00 | 231.8 | 227.26
2019-05-11 02:30 | 231.77 | 227.23
2019-05-11 03:00 | 231.19 | 226.65
2019-05-11 03:30 | 232.53 | 227.93
2019-05-11 04:00 | 233.13 | 228.49
2019-05-11 04:30 | 233.33 | 228.68
2019-05-11 05:00 | 234.41 | 229.78
2019-05-11 05:30 | 235.59 | 231.04
2019-05-11 06:00 | 237.18 | 232.71
2019-05-11 06:30 | 238.91 | 234.7
2019-05-11 07:00 | 240.78 | 236.67
2019-05-11 07:30 | 239.63 | 235.58
2019-05-11 08:00 | 238.29 | 234.29
2019-05-11 08:30 | 236.23 | 232.29
2019-05-11 09:00 | 234.71 | 230.74
2019-05-11 09:30 | 232.71 | 228.4
2019-05-11 10:00 | 230.12 | 225.78
2019-05-11 10:30 | 228.36 | 223.94
2019-05-11 11:00 | 226.9 | 222.32
2019-05-11 11:30 | 225.32 | 220.68
2019-05-11 12:00 | 225.41 | 220.76
2019-05-11 12:30 | 223.97 | 219.15
2019-05-11 13:00 | 224.31 | 219.38
2019-05-11 13:30 | 223.8 | 219.01
2019-05-11 14:00 | 206.94 | 202.23
2019-05-11 14:30 | 204.07 | 199.27
2019-05-11 15:00 | 204.42 | 199.61
2019-05-11 15:30 | 206.11 | 201.34
2019-05-11 16:00 | 208.45 | 203.75
2019-05-11 16:30 | 227.05 | 222.36
2019-05-11 17:00 | 235.49 | 230
2019-05-11 17:30 | 239.94 | 233.74
2019-05-11 18:00 | 246.83 | 244.54
2019-05-11 18:30 | 249.41 | 247.59
2019-05-11 19:00 | 249.47 | 247.57
2019-05-11 19:30 | 249.36 | 247.45
2019-05-11 20:00 | 242.49 | 238.17
2019-05-11 20:30 | 243.73 | 238.93
2019-05-11 21:00 | 242.94 | 238.04
2019-05-11 21:30 | 243.26 | 239.11
2019-05-11 22:00 | 242.5 | 238.59
2019-05-11 22:30 | 240.53 | 236.65
2019-05-11 23:00 | 238.7 | 234.72
2019-05-11 23:30 | 237.3 | 233.16
2019-05-12 | 236.78 | 232.34
2019-05-12 00:30 | 235.59 | 231.39
2019-05-12 01:00 | 233.75 | 229.49
2019-05-12 01:30 | 233.91 | 229.55
2019-05-12 02:00 | 233.73 | 229.36
2019-05-12 02:30 | 233.28 | 228.87
2019-05-12 03:00 | 233.46 | 229.05
2019-05-12 03:30 | 233.2 | 228.79
2019-05-12 04:00 | 233.7 | 229.3
2019-05-12 04:30 | 234.33 | 229.95
2019-05-12 05:00 | 234.88 | 230.53
2019-05-12 05:30 | 235.6 | 231.28
2019-05-12 06:00 | 237.06 | 232.81
2019-05-12 06:30 | 239.27 | 235.15
2019-05-12 07:00 | 241.5 | 237.5
2019-05-12 07:30 | 238.31 | 234.14
2019-05-12 08:00 | 237.85 | 233.93
2019-05-12 08:30 | 219.51 | 215.26
2019-05-12 09:00 | 214.21 | 209.16
2019-05-12 09:30 | 210.37 | 205.31
2019-05-12 10:00 | 207.63 | 202.19
2019-05-12 10:30 | 175.66 | 170.14
2019-05-12 11:00 | 160.04 | 154.17
2019-05-12 11:30 | 161.3 | 155.39
2019-05-12 12:00 | 162.32 | 156.37
2019-05-12 12:30 | 161.9 | 155.82
2019-05-12 13:00 | 160.35 | 154.18
2019-05-12 13:30 | 157.59 | 151.14
2019-05-12 14:00 | 159.24 | 152.03
2019-05-12 14:30 | 159.22 | 151.88
2019-05-12 15:00 | 159.6 | 152.56
2019-05-12 15:30 | 193.42 | 186.77
2019-05-12 16:00 | 222.65 | 216.07
2019-05-12 16:30 | 229.96 | 223.69
2019-05-12 17:00 | 233.56 | 227.75
2019-05-12 17:30 | 235.57 | 229.2
2019-05-12 18:00 | 247.23 | 245.23
2019-05-12 18:30 | 245.39 | 243.32
2019-05-12 19:00 | 246.15 | 244.08
2019-05-12 19:30 | 246.7 | 244.68
2019-05-12 20:00 | 242.07 | 238.99
2019-05-12 20:30 | 242.11 | 235.98
2019-05-12 21:00 | 240.85 | 235.79
2019-05-12 21:30 | 240.39 | 235.58
2019-05-12 22:00 | 238.58 | 233.59
2019-05-12 22:30 | 236.84 | 231.48
2019-05-12 23:00 | 235.22 | 229.68
2019-05-12 23:30 | 233.67 | 228.37
2019-05-13 | 230.81 | 226.44
2019-05-13 00:30 | 230.48 | 226.06
2019-05-13 01:00 | 229.22 | 224.81
2019-05-13 01:30 | 229.14 | 224.55
2019-05-13 02:00 | 228.82 | 224.22
2019-05-13 02:30 | 228.34 | 223.68
2019-05-13 03:00 | 226.51 | 221.79
2019-05-13 03:30 | 226.32 | 221.61
2019-05-13 04:00 | 225.95 | 221.27
2019-05-13 04:30 | 226.58 | 221.95
2019-05-13 05:00 | 227.52 | 222.94
2019-05-13 05:30 | 230.25 | 225.94
2019-05-13 06:00 | 233.07 | 228.81
2019-05-13 06:30 | 236.85 | 232.76
2019-05-13 07:00 | 240.22 | 236.12
2019-05-13 07:30 | 240.12 | 236.54
2019-05-13 08:00 | 238.91 | 235.56
2019-05-13 08:30 | 236.22 | 232.84
2019-05-13 09:00 | 232.5 | 229.02
2019-05-13 09:30 | 228.7 | 224.9
2019-05-13 10:00 | 226.98 | 222.74
2019-05-13 10:30 | 227.53 | 223.1
2019-05-13 11:00 | 226.27 | 221.65
2019-05-13 11:30 | 225.93 | 221.1
2019-05-13 12:00 | 226.04 | 221.3
2019-05-13 12:30 | 224.15 | 219.17
2019-05-13 13:00 | 224.09 | 219.11
2019-05-13 13:30 | 224.13 | 219.23
2019-05-13 14:00 | 224.61 | 219.87
2019-05-13 14:30 | 225.1 | 220.46
2019-05-13 15:00 | 225.75 | 221.09
2019-05-13 15:30 | 225.83 | 221.3
2019-05-13 16:00 | 226.45 | 222.07
2019-05-13 16:30 | 227.61 | 223.32
2019-05-13 17:00 | 230.2 | 225.84
2019-05-13 17:30 | 239.19 | 237.19
2019-05-13 18:00 | 245.06 | 244
2019-05-13 18:30 | 242.15 | 241.13
2019-05-13 19:00 | 242.38 | 241.35
2019-05-13 19:30 | 243.57 | 242.43
2019-05-13 20:00 | 244.02 | 242.91
2019-05-13 20:30 | 236.86 | 232.87
2019-05-13 21:00 | 239.36 | 234.14
2019-05-13 21:30 | 239.72 | 235.04
2019-05-13 22:00 | 238.88 | 234.27
2019-05-13 22:30 | 237.04 | 231.95
2019-05-13 23:00 | 235.57 | 230.2
2019-05-13 23:30 | 234.94 | 229.65
2019-05-14 | 232.8 | 227.46
2019-05-14 00:30 | 232.55 | 227.79
2019-05-14 01:00 | 230.96 | 226.36
2019-05-14 01:30 | 230.31 | 225.59
2019-05-14 02:00 | 230.14 | 225.36
2019-05-14 02:30 | 229.41 | 224.58
2019-05-14 03:00 | 229.63 | 224.81
2019-05-14 03:30 | 229.73 | 224.94
2019-05-14 04:00 | 229.17 | 224.38
2019-05-14 04:30 | 230.37 | 225.6
2019-05-14 05:00 | 230.81 | 226.1
2019-05-14 05:30 | 231.99 | 227.5
2019-05-14 06:00 | 235.16 | 229.64
2019-05-14 06:30 | 238.69 | 233.13
2019-05-14 07:00 | 239.53 | 234.55
2019-05-14 07:30 | 237.56 | 232.33
2019-05-14 08:00 | 236.91 | 231.73
2019-05-14 08:30 | 234.82 | 229.61
2019-05-14 09:00 | 232.41 | 227
2019-05-14 09:30 | 235.73 | 232.03
2019-05-14 10:00 | 251.95 | 250.35
2019-05-14 10:30 | 253.34 | 251.45
2019-05-14 11:00 | 249.36 | 247.16
2019-05-14 11:30 | 223.31 | 219.11
2019-05-14 12:00 | 222.73 | 218.47
2019-05-14 12:30 | 222.71 | 217.73
2019-05-14 13:00 | 227 | 220.47
2019-05-14 13:30 | 228.19 | 221.65
2019-05-14 14:00 | 228.13 | 221.71
2019-05-14 14:30 | 228.01 | 221.61
2019-05-14 15:00 | 229.21 | 222.68
2019-05-14 15:30 | 230.1 | 223.91
2019-05-14 16:00 | 231.21 | 225.18
2019-05-14 16:30 | 232.26 | 226.43
2019-05-14 17:00 | 233.86 | 228.19
2019-05-14 17:30 | 234.49 | 230.76
2019-05-14 18:00 | 246.65 | 245.21
2019-05-14 18:30 | 245.47 | 243.96
2019-05-14 19:00 | 246.27 | 244.77
2019-05-14 19:30 | 246.66 | 245.2
2019-05-14 20:00 | 247.7 | 246.25
2019-05-14 20:30 | 248.75 | 247.29
2019-05-14 21:00 | 239.82 | 235.3
2019-05-14 21:30 | 241.59 | 236.4
2019-05-14 22:00 | 239.69 | 234.65
2019-05-14 22:30 | 238.07 | 232.74
2019-05-14 23:00 | 236.88 | 231.24
2019-05-14 23:30 | 235.79 | 229.88
2019-05-15 | 234.78 | 228.96
2019-05-15 00:30 | 233.45 | 227.94
2019-05-15 01:00 | 231.76 | 227.5
2019-05-15 01:30 | 230.76 | 226.49
2019-05-15 02:00 | 230.58 | 226.34
2019-05-15 02:30 | 230.15 | 225.91
2019-05-15 03:00 | 230.15 | 225.93
2019-05-15 03:30 | 230.53 | 226.31
2019-05-15 04:00 | 230.94 | 226.76
2019-05-15 04:30 | 231.19 | 227.03
2019-05-15 05:00 | 232.28 | 228.16
2019-05-15 05:30 | 233.93 | 229.77
2019-05-15 06:00 | 235.62 | 231.6
2019-05-15 06:30 | 239.06 | 235.22
2019-05-15 07:00 | 241.45 | 237.87
2019-05-15 07:30 | 238.61 | 235.03
2019-05-15 08:00 | 238.47 | 234.83
2019-05-15 08:30 | 235.73 | 231.95
2019-05-15 09:00 | 231.24 | 227.25
2019-05-15 09:30 | 230.29 | 225.98
2019-05-15 10:00 | 230.9 | 226.83
2019-05-15 10:30 | 232.73 | 228.98
2019-05-15 11:00 | 231.67 | 227.82
2019-05-15 11:30 | 225.46 | 221.12
2019-05-15 12:00 | 226.15 | 221.74
2019-05-15 12:30 | 226.13 | 221.76
2019-05-15 13:00 | 225.93 | 221.61
2019-05-15 13:30 | 227.88 | 223.22
2019-05-15 14:00 | 229.18 | 224.53
2019-05-15 14:30 | 229 | 224.49
2019-05-15 15:00 | 230 | 225.36
2019-05-15 15:30 | 229.72 | 225.05
2019-05-15 16:00 | 230.87 | 226.48
2019-05-15 16:30 | 232.12 | 228.69
2019-05-15 17:00 | 248.93 | 247.73
2019-05-15 17:30 | 248.63 | 247.46
2019-05-15 18:00 | 248.25 | 247.21
2019-05-15 18:30 | 246.8 | 245.56
2019-05-15 19:00 | 247.24 | 245.84
2019-05-15 19:30 | 248.1 | 246.52
2019-05-15 20:00 | 248.93 | 247.5
2019-05-15 20:30 | 240.68 | 236.22
2019-05-15 21:00 | 241.53 | 236.06
2019-05-15 21:30 | 242.21 | 236.88
2019-05-15 22:00 | 240.96 | 235.46
2019-05-15 22:30 | 238.9 | 232.88
2019-05-15 23:00 | 237.79 | 231.8
2019-05-15 23:30 | 237.02 | 230.94
2019-05-16 | 234.42 | 229.78
2019-05-16 00:30 | 234.02 | 229.1
2019-05-16 01:00 | 232.79 | 228.38
2019-05-16 01:30 | 232.18 | 227.82
2019-05-16 02:00 | 231.98 | 227.7
2019-05-16 02:30 | 231.43 | 226.98
2019-05-16 03:00 | 231.5 | 226.97
2019-05-16 03:30 | 231.53 | 226.98
2019-05-16 04:00 | 231.97 | 227.41
2019-05-16 04:30 | 232.42 | 227.92
2019-05-16 05:00 | 233.12 | 228.7
2019-05-16 05:30 | 234.44 | 229.99
2019-05-16 06:00 | 235.98 | 231.74
2019-05-16 06:30 | 239.92 | 235.8
2019-05-16 07:00 | 243.74 | 238.54
2019-05-16 07:30 | 240.31 | 235.06
2019-05-16 08:00 | 239.87 | 234.62
2019-05-16 08:30 | 237.39 | 232.09
2019-05-16 09:00 | 234.92 | 229.69
2019-05-16 09:30 | 233.19 | 227.69
2019-05-16 10:00 | 231.15 | 225.63
2019-05-16 10:30 | 229.66 | 223.75
2019-05-16 11:00 | 229.55 | 223.27
2019-05-16 11:30 | 229.11 | 222.84
2019-05-16 12:00 | 227.96 | 222.24
2019-05-16 12:30 | 228.01 | 222.46
2019-05-16 13:00 | 228.31 | 222.91
2019-05-16 13:30 | 228.36 | 223
2019-05-16 14:00 | 230.08 | 224.74
2019-05-16 14:30 | 230.22 | 224.96
2019-05-16 15:00 | 230.91 | 225.33
2019-05-16 15:30 | 232.67 | 226.94
2019-05-16 16:00 | 233.46 | 227.7
2019-05-16 16:30 | 234.26 | 228.73
2019-05-16 17:00 | 233.94 | 228.96
2019-05-16 17:30 | 250.55 | 248.57
2019-05-16 18:00 | 249.51 | 246.92
2019-05-16 18:30 | 248.7 | 246.07
2019-05-16 19:00 | 249.39 | 246.61
2019-05-16 19:30 | 249.66 | 246.91
2019-05-16 20:00 | 249.77 | 247.2
2019-05-16 20:30 | 249.72 | 247.33
2019-05-16 21:00 | 240.33 | 235.72
2019-05-16 21:30 | 241.06 | 235.87
2019-05-16 22:00 | 239.56 | 234.74
2019-05-16 22:30 | 238.4 | 233.27
2019-05-16 23:00 | 237.07 | 231.64
2019-05-16 23:30 | 236.58 | 231.11
2019-05-17 | 234.74 | 229.18
2019-05-17 00:30 | 234.01 | 228.64
2019-05-17 01:00 | 232.54 | 227.8
2019-05-17 01:30 | 231.06 | 226.67
2019-05-17 02:00 | 230.68 | 226.3
2019-05-17 02:30 | 229.97 | 225.55
2019-05-17 03:00 | 229.97 | 225.43
2019-05-17 03:30 | 230.44 | 225.99
2019-05-17 04:00 | 230.08 | 225.57
2019-05-17 04:30 | 230.6 | 226
2019-05-17 05:00 | 231.22 | 226.63
2019-05-17 05:30 | 232.28 | 227.9
2019-05-17 06:00 | 187.24 | 182.03
2019-05-17 06:30 | 169.57 | 164.18
2019-05-17 07:00 | 171.61 | 166.31
2019-05-17 07:30 | 168.56 | 163.24
2019-05-17 08:00 | 167.24 | 162.18
2019-05-17 08:30 | 163.07 | 158.24
2019-05-17 09:00 | 192.42 | 187.84
2019-05-17 09:30 | 218.83 | 214.45
2019-05-17 10:00 | 223.29 | 219.3
2019-05-17 10:30 | 224.55 | 220.33
2019-05-17 11:00 | 223.52 | 219.26
2019-05-17 11:30 | 223.56 | 219
2019-05-17 12:00 | 224.14 | 219.26
2019-05-17 12:30 | 224.54 | 219.75
2019-05-17 13:00 | 226.34 | 221.33
2019-05-17 13:30 | 227.5 | 222.58
2019-05-17 14:00 | 227.97 | 223.26
2019-05-17 14:30 | 228.82 | 224.13
2019-05-17 15:00 | 228.83 | 224.15
2019-05-17 15:30 | 230.46 | 225.95
2019-05-17 16:00 | 231.77 | 227.39
2019-05-17 16:30 | 233.9 | 230.59
2019-05-17 17:00 | 253.29 | 252.12
2019-05-17 17:30 | 252.54 | 251.42
2019-05-17 18:00 | 250.92 | 249.86
2019-05-17 18:30 | 248.12 | 247.09
2019-05-17 19:00 | 247.4 | 246.32
2019-05-17 19:30 | 246.56 | 245.46
2019-05-17 20:00 | 230.92 | 229.72
2019-05-17 20:30 | 193.61 | 192.07
2019-05-17 21:00 | 180.65 | 178.94
2019-05-17 21:30 | 169.95 | 165.32
2019-05-17 22:00 | 170.44 | 164.75
2019-05-17 22:30 | 168.97 | 163.22
2019-05-17 23:00 | 167.44 | 161.69
2019-05-17 23:30 | 166.01 | 160.08
2019-05-18 | 165.16 | 159.25
2019-05-18 00:30 | 165.22 | 159.02
2019-05-18 01:00 | 165.17 | 158.74
2019-05-18 01:30 | 164.74 | 158.13
2019-05-18 02:00 | 164.24 | 157.55
2019-05-18 02:30 | 164.38 | 157.56
2019-05-18 03:00 | 164.06 | 157.27
2019-05-18 03:30 | 163.98 | 157.25
2019-05-18 04:00 | 164.07 | 157.38
2019-05-18 04:30 | 165 | 158.35
2019-05-18 05:00 | 165.23 | 158.65
2019-05-18 05:30 | 165.37 | 158.84
2019-05-18 06:00 | 168.13 | 161.7
2019-05-18 06:30 | 169.6 | 163.34
2019-05-18 07:00 | 170.4 | 164.3
2019-05-18 07:30 | 166.01 | 159.93
2019-05-18 08:00 | 165.05 | 159.42
2019-05-18 08:30 | 197.25 | 192.2
2019-05-18 09:00 | 225.98 | 220.62
2019-05-18 09:30 | 229.61 | 223.88
2019-05-18 10:00 | 231.07 | 223.95
2019-05-18 10:30 | 231.27 | 222.59
2019-05-18 11:00 | 229.57 | 220.36
2019-05-18 11:30 | 228.56 | 220.06
2019-05-18 12:00 | 228.07 | 219.95
2019-05-18 12:30 | 211.53 | 203.47
2019-05-18 13:00 | 174.95 | 166.63
2019-05-18 13:30 | 161.41 | 153.13
2019-05-18 14:00 | 161.5 | 153.73
2019-05-18 14:30 | 164.08 | 156.43
2019-05-18 15:00 | 166.96 | 159.43
2019-05-18 15:30 | 200.04 | 192.73
2019-05-18 16:00 | 230.31 | 223.1
2019-05-18 16:30 | 237.01 | 229.45
2019-05-18 17:00 | 239.16 | 230.91
2019-05-18 17:30 | 243.26 | 237.12
2019-05-18 18:00 | 253.63 | 250.58
2019-05-18 18:30 | 253.25 | 250.27
2019-05-18 19:00 | 253.41 | 250.22
2019-05-18 19:30 | 253.47 | 250.02
2019-05-18 20:00 | 244.52 | 236.58
2019-05-18 20:30 | 244.69 | 234.9
2019-05-18 21:00 | 243.25 | 233.09
2019-05-18 21:30 | 243.32 | 233.36
2019-05-18 22:00 | 241.42 | 232.74
2019-05-18 22:30 | 241.14 | 232.35
2019-05-18 23:00 | 240.47 | 231.42
2019-05-18 23:30 | 238.92 | 231.09
2019-05-19 | 236.95 | 229.89
2019-05-19 00:30 | 236.45 | 229.36
2019-05-19 01:00 | 235.57 | 228.49
2019-05-19 01:30 | 235.54 | 227.73
2019-05-19 02:00 | 234.44 | 227.24
2019-05-19 02:30 | 234.07 | 226.96
2019-05-19 03:00 | 234.08 | 226.86
2019-05-19 03:30 | 234.06 | 226.48
2019-05-19 04:00 | 233.95 | 226.48
2019-05-19 04:30 | 234.17 | 226.83
2019-05-19 05:00 | 234.52 | 227.23
2019-05-19 05:30 | 234.7 | 227.33
2019-05-19 06:00 | 235.34 | 227.99
2019-05-19 06:30 | 236.46 | 229.18
2019-05-19 07:00 | 237.67 | 230.45
2019-05-19 07:30 | 235.12 | 228.08
2019-05-19 08:00 | 235.38 | 228.26
2019-05-19 08:30 | 235.39 | 227.02
2019-05-19 09:00 | 233.78 | 225.01
2019-05-19 09:30 | 232.93 | 222.8
2019-05-19 10:00 | 232.43 | 221.64
2019-05-19 10:30 | 231.26 | 220.55
2019-05-19 11:00 | 230.56 | 219.95
2019-05-19 11:30 | 230.07 | 218.97
2019-05-19 12:00 | 229.53 | 218.18
2019-05-19 12:30 | 229.5 | 218.35
2019-05-19 13:00 | 228.87 | 217.67
2019-05-19 13:30 | 229.24 | 218.08
2019-05-19 14:00 | 229.86 | 218.91
2019-05-19 14:30 | 230.47 | 219.2
2019-05-19 15:00 | 231.96 | 220.12
2019-05-19 15:30 | 233.66 | 221.88
2019-05-19 16:00 | 236.1 | 223.88
2019-05-19 16:30 | 234.45 | 224.35
2019-05-19 17:00 | 239.95 | 232.24
2019-05-19 17:30 | 252.55 | 247.33
2019-05-19 18:00 | 251.65 | 246.01
2019-05-19 18:30 | 250.09 | 244.25
2019-05-19 19:00 | 250.59 | 244.73
2019-05-19 19:30 | 250.31 | 244.36
2019-05-19 20:00 | 248.37 | 242.48
2019-05-19 20:30 | 239.02 | 228.76
2019-05-19 21:00 | 237.96 | 227.37
2019-05-19 21:30 | 236.62 | 226.81
2019-05-19 22:00 | 236.17 | 226.11
2019-05-19 22:30 | 234.87 | 224.77
2019-05-19 23:00 | 233.13 | 223.54
2019-05-19 23:30 | 232.8 | 223.4
2019-05-20 | 231.73 | 223.45
2019-05-20 00:30 | 232.32 | 223.02
2019-05-20 01:00 | 231.13 | 222.17
2019-05-20 01:30 | 230.92 | 222.85
2019-05-20 02:00 | 230.93 | 222.68
2019-05-20 02:30 | 231.67 | 222.55
2019-05-20 03:00 | 231.42 | 222.4
2019-05-20 03:30 | 231 | 221.88
2019-05-20 04:00 | 231.87 | 223.01
2019-05-20 04:30 | 231.54 | 222.57
2019-05-20 05:00 | 232.66 | 223.74
2019-05-20 05:30 | 233.89 | 225.13
2019-05-20 06:00 | 236.94 | 227.12
2019-05-20 06:30 | 240.24 | 230.07
2019-05-20 07:00 | 243.19 | 233.33
2019-05-20 07:30 | 241.4 | 233.25
2019-05-20 08:00 | 241.32 | 233.36
2019-05-20 08:30 | 238.8 | 230.82
2019-05-20 09:00 | 235.57 | 226.65
2019-05-20 09:30 | 233.33 | 224.25
2019-05-20 10:00 | 232.31 | 223.08
2019-05-20 10:30 | 232.99 | 224.03
2019-05-20 11:00 | 233.36 | 224.3
2019-05-20 11:30 | 233.92 | 224.99
2019-05-20 12:00 | 233.41 | 224.34
2019-05-20 12:30 | 232.01 | 222.82
2019-05-20 13:00 | 231.39 | 222.15
2019-05-20 13:30 | 233.02 | 223.31
2019-05-20 14:00 | 233.5 | 223.92
2019-05-20 14:30 | 234.83 | 225.18
2019-05-20 15:00 | 236.69 | 226.72
2019-05-20 15:30 | 239.03 | 228.78
2019-05-20 16:00 | 240 | 229.88
2019-05-20 16:30 | 239.43 | 229.92
2019-05-20 17:00 | 241.1 | 234.08
2019-05-20 17:30 | 253.27 | 249.02
2019-05-20 18:00 | 251.47 | 247.04
2019-05-20 18:30 | 250.02 | 245.4
2019-05-20 19:00 | 248.38 | 243.87
2019-05-20 19:30 | 248.07 | 243.62
2019-05-20 20:00 | 248.45 | 244.03
2019-05-20 20:30 | 244.88 | 235.34
2019-05-20 21:00 | 246.06 | 235.2
2019-05-20 21:30 | 244.64 | 234.81
2019-05-20 22:00 | 242.96 | 233.88
2019-05-20 22:30 | 241.59 | 232.39
2019-05-20 23:00 | 239.34 | 230.6
2019-05-20 23:30 | 238.33 | 230.14
2019-05-21 | 236.37 | 228.66
2019-05-21 00:30 | 236.34 | 228.53
2019-05-21 01:00 | 235.73 | 227.86
2019-05-21 01:30 | 234.94 | 227.41
2019-05-21 02:00 | 234.54 | 227.03
2019-05-21 02:30 | 233.95 | 226.64
2019-05-21 03:00 | 233.54 | 226.24
2019-05-21 03:30 | 233.92 | 226.47
2019-05-21 04:00 | 234.38 | 226.93
2019-05-21 04:30 | 233.74 | 226.32
2019-05-21 05:00 | 233.07 | 225.72
2019-05-21 05:30 | 235.23 | 227.18
2019-05-21 06:00 | 237.9 | 228.78
2019-05-21 06:30 | 242.04 | 232.79
2019-05-21 07:00 | 244.53 | 235.9
2019-05-21 07:30 | 243.5 | 234.82
2019-05-21 08:00 | 243.74 | 234.29
2019-05-21 08:30 | 241.55 | 232.02
2019-05-21 09:00 | 238.79 | 228.05
2019-05-21 09:30 | 233.12 | 224.65
2019-05-21 10:00 | 231.33 | 223.13
2019-05-21 10:30 | 230.19 | 221.71
2019-05-21 11:00 | 230.3 | 221.29
2019-05-21 11:30 | 230.29 | 220.91
2019-05-21 12:00 | 229.36 | 220.34
2019-05-21 12:30 | 229.87 | 220.5
2019-05-21 13:00 | 230.04 | 220.34
2019-05-21 13:30 | 229.33 | 219.69
2019-05-21 14:00 | 228.39 | 219.11
2019-05-21 14:30 | 228.02 | 219.72
2019-05-21 15:00 | 229.84 | 221.58
2019-05-21 15:30 | 232.46 | 223.38
2019-05-21 16:00 | 232.8 | 223.2
2019-05-21 16:30 | 235.67 | 228.55
2019-05-21 17:00 | 246.02 | 241.86
2019-05-21 17:30 | 245.66 | 241.31
2019-05-21 18:00 | 243.16 | 238.88
2019-05-21 18:30 | 241.43 | 237.12
2019-05-21 19:00 | 241.88 | 237.59
2019-05-21 19:30 | 243.56 | 239.08
2019-05-21 20:00 | 244.64 | 240.12
2019-05-21 20:30 | 238.88 | 229.41
2019-05-21 21:00 | 239.4 | 228.67
2019-05-21 21:30 | 237.7 | 228.14
2019-05-21 22:00 | 233.76 | 226.67
2019-05-21 22:30 | 232.75 | 225.36
2019-05-21 23:00 | 231.86 | 223.96
2019-05-21 23:30 | 231.41 | 223.7
2019-05-22 | 230.52 | 223.4
2019-05-22 00:30 | 230.2 | 223
2019-05-22 01:00 | 230.07 | 222.66
2019-05-22 01:30 | 229.4 | 222.08
2019-05-22 02:00 | 229.79 | 221.97
2019-05-22 02:30 | 230.17 | 221.55
2019-05-22 03:00 | 230.33 | 221.4
2019-05-22 03:30 | 230.51 | 221.4
2019-05-22 04:00 | 230.55 | 221.9
2019-05-22 04:30 | 231.17 | 222.5
2019-05-22 05:00 | 232.5 | 223.61
2019-05-22 05:30 | 234.45 | 225.16
2019-05-22 06:00 | 237.95 | 227.6
2019-05-22 06:30 | 241.03 | 230.98
2019-05-22 07:00 | 241.6 | 233.42
2019-05-22 07:30 | 242.02 | 233.53
2019-05-22 08:00 | 242.13 | 232.98
2019-05-22 08:30 | 240.65 | 230.42
2019-05-22 09:00 | 235.82 | 226.97
2019-05-22 09:30 | 233.81 | 225.1
2019-05-22 10:00 | 231.96 | 223.51
2019-05-22 10:30 | 230.35 | 221.87
2019-05-22 11:00 | 229.36 | 221.4
2019-05-22 11:30 | 228.23 | 220.62
2019-05-22 12:00 | 228.99 | 221.03
2019-05-22 12:30 | 228.69 | 220.76
2019-05-22 13:00 | 227.99 | 220.3
2019-05-22 13:30 | 228.68 | 220.88
2019-05-22 14:00 | 227.09 | 218.8
2019-05-22 14:30 | 226.74 | 218.58
2019-05-22 15:00 | 225.62 | 217.67
2019-05-22 15:30 | 226.09 | 217.54
2019-05-22 16:00 | 227.77 | 219.46
2019-05-22 16:30 | 241.27 | 237.84
2019-05-22 17:00 | 244.09 | 240.33
2019-05-22 17:30 | 246.76 | 242.58
2019-05-22 18:00 | 245.87 | 241.86
2019-05-22 18:30 | 245.03 | 240.9
2019-05-22 19:00 | 243.94 | 239.9
2019-05-22 19:30 | 244 | 239.78
2019-05-22 20:00 | 246.78 | 242.38
2019-05-22 20:30 | 248.07 | 243.52
2019-05-22 21:00 | 238.1 | 229.83
2019-05-22 21:30 | 237.28 | 228.71
2019-05-22 22:00 | 234.83 | 226.29
2019-05-22 22:30 | 232.95 | 224.23
2019-05-22 23:00 | 232.22 | 223.17
2019-05-22 23:30 | 231.98 | 223.01
2019-05-23 | 232.33 | 223.17
2019-05-23 00:30 | 231.47 | 223.25
2019-05-23 01:00 | 230.91 | 223.37
2019-05-23 01:30 | 230.22 | 222.6
2019-05-23 02:00 | 229.74 | 221.86
2019-05-23 02:30 | 229.96 | 222
2019-05-23 03:00 | 229.75 | 221.53
2019-05-23 03:30 | 229.71 | 221.29
2019-05-23 04:00 | 230.25 | 221.76
2019-05-23 04:30 | 230.94 | 222.44
2019-05-23 05:00 | 232.13 | 223.67
2019-05-23 05:30 | 232.9 | 224.83
2019-05-23 06:00 | 234.14 | 226.63
2019-05-23 06:30 | 237.8 | 230.88
2019-05-23 07:00 | 240.55 | 232.59
2019-05-23 07:30 | 240.36 | 232.42
2019-05-23 08:00 | 239.75 | 231.4
2019-05-23 08:30 | 237.28 | 229.03
2019-05-23 09:00 | 234.06 | 225.84
2019-05-23 09:30 | 231.29 | 223.23
2019-05-23 10:00 | 228.8 | 220.75
2019-05-23 10:30 | 228.58 | 220.44
2019-05-23 11:00 | 212.91 | 204.93
2019-05-23 11:30 | 206.7 | 198.77
2019-05-23 12:00 | 206.71 | 198.85
2019-05-23 12:30 | 204.47 | 195.82
2019-05-23 13:00 | 203.61 | 194.73
2019-05-23 13:30 | 204.31 | 195.29
2019-05-23 14:00 | 204.13 | 195.13
2019-05-23 14:30 | 206.1 | 197.4
2019-05-23 15:00 | 204.85 | 195.87
2019-05-23 15:30 | 206.06 | 197.28
2019-05-23 16:00 | 206.73 | 198.01
2019-05-23 16:30 | 207.86 | 199.54
2019-05-23 17:00 | 209.39 | 200.93
2019-05-23 17:30 | 214.01 | 207.27
2019-05-23 18:00 | 224.72 | 221.11
2019-05-23 18:30 | 224.19 | 220.53
2019-05-23 19:00 | 225.58 | 221.77
2019-05-23 19:30 | 227.32 | 223.4
2019-05-23 20:00 | 228.51 | 224.65
2019-05-23 20:30 | 219.27 | 210.65
2019-05-23 21:00 | 219.45 | 209.27
2019-05-23 21:30 | 218.27 | 208.73
2019-05-23 22:00 | 215.68 | 206.16
2019-05-23 22:30 | 213.85 | 204.15
2019-05-23 23:00 | 212.88 | 202.75
2019-05-23 23:30 | 212.08 | 202.01
2019-05-24 | 210.68 | 201.24
2019-05-24 00:30 | 210.41 | 200.65
2019-05-24 01:00 | 209.59 | 200.2
2019-05-24 01:30 | 209.33 | 199.94
2019-05-24 02:00 | 209.01 | 199.67
2019-05-24 02:30 | 208.1 | 198.63
2019-05-24 03:00 | 208.45 | 198.61
2019-05-24 03:30 | 210.64 | 200.7
2019-05-24 04:00 | 210.14 | 200.15
2019-05-24 04:30 | 210.34 | 200.14
2019-05-24 05:00 | 211.26 | 201
2019-05-24 05:30 | 212.64 | 202.88
2019-05-24 06:00 | 214.61 | 205.52
2019-05-24 06:30 | 217.19 | 209.28
2019-05-24 07:00 | 213.75 | 207.53
2019-05-24 07:30 | 198.93 | 193.42
2019-05-24 08:00 | 200.57 | 195.07
2019-05-24 08:30 | 201.09 | 195.59
2019-05-24 09:00 | 206.72 | 199.14
2019-05-24 09:30 | 208.29 | 199.75
2019-05-24 10:00 | 205.34 | 196.45
2019-05-24 10:30 | 203.67 | 194.81
2019-05-24 11:00 | 202.63 | 194.18
2019-05-24 11:30 | 202.02 | 193.14
2019-05-24 12:00 | 202.45 | 193.67
2019-05-24 12:30 | 203.45 | 194.95
2019-05-24 13:00 | 205.65 | 197.26
2019-05-24 13:30 | 208.35 | 199.87
2019-05-24 14:00 | 209.84 | 201.1
2019-05-24 14:30 | 209.15 | 200.08
2019-05-24 15:00 | 209.04 | 199.95
2019-05-24 15:30 | 208.02 | 198.53
2019-05-24 16:00 | 208.83 | 199.43
2019-05-24 16:30 | 208.49 | 199.18
2019-05-24 17:00 | 210.88 | 202.65
2019-05-24 17:30 | 228.8 | 224.23
2019-05-24 18:00 | 227.67 | 223.14
2019-05-24 18:30 | 226.88 | 222.44
2019-05-24 19:00 | 227.68 | 223.46
2019-05-24 19:30 | 227.32 | 224.66
2019-05-24 20:00 | 215.93 | 210.06
2019-05-24 20:30 | 216.09 | 209.72
2019-05-24 21:00 | 214.29 | 207.97
2019-05-24 21:30 | 214.57 | 208.79
2019-05-24 22:00 | 213.07 | 207.51
2019-05-24 22:30 | 212.62 | 206.89
2019-05-24 23:00 | 211.82 | 206.19
2019-05-24 23:30 | 210.11 | 203.89
2019-05-25 | 209.1 | 202.78
2019-05-25 00:30 | 209.15 | 202.65
2019-05-25 01:00 | 207.28 | 201.35
2019-05-25 01:30 | 206.71 | 200.92
2019-05-25 02:00 | 206.64 | 200.63
2019-05-25 02:30 | 206.59 | 200.58
2019-05-25 03:00 | 206.5 | 200.26
2019-05-25 03:30 | 206.13 | 199.74
2019-05-25 04:00 | 206.07 | 199.59
2019-05-25 04:30 | 206.58 | 200.16
2019-05-25 05:00 | 207.47 | 201.09
2019-05-25 05:30 | 208.62 | 202.43
2019-05-25 06:00 | 209.08 | 203.18
2019-05-25 06:30 | 209.91 | 204.56
2019-05-25 07:00 | 208.81 | 203.69
2019-05-25 07:30 | 208.52 | 203.37
2019-05-25 08:00 | 208.7 | 203.64
2019-05-25 08:30 | 208.11 | 202.77
2019-05-25 09:00 | 206.66 | 201.28
2019-05-25 09:30 | 204.71 | 198.85
2019-05-25 10:00 | 204.08 | 197.7
2019-05-25 10:30 | 203.47 | 196.99
2019-05-25 11:00 | 202.2 | 195.99
2019-05-25 11:30 | 201.23 | 194.75
2019-05-25 12:00 | 201.85 | 195.28
2019-05-25 12:30 | 203.11 | 196.48
2019-05-25 13:00 | 202.98 | 196.17
2019-05-25 13:30 | 202.09 | 195.32
2019-05-25 14:00 | 201.85 | 195.09
2019-05-25 14:30 | 201.72 | 194.95
2019-05-25 15:00 | 202.99 | 196.2
2019-05-25 15:30 | 204.34 | 197.67
2019-05-25 16:00 | 203.08 | 196.68
2019-05-25 16:30 | 203.96 | 197.53
2019-05-25 17:00 | 205.74 | 199.57
2019-05-25 17:30 | 207.39 | 201.46
2019-05-25 18:00 | 224.09 | 222.41
2019-05-25 18:30 | 224.87 | 223.21
2019-05-25 19:00 | 225.58 | 223.9
2019-05-25 19:30 | 212.22 | 207.22
2019-05-25 20:00 | 211.97 | 205.8
2019-05-25 20:30 | 210.98 | 204.72
2019-05-25 21:00 | 209.99 | 203.8
2019-05-25 21:30 | 209.92 | 203.67
2019-05-25 22:00 | 208.09 | 202.24
2019-05-25 22:30 | 207.63 | 202
2019-05-25 23:00 | 206.01 | 200.25
2019-05-25 23:30 | 204.95 | 198.89
2019-05-26 | 203.99 | 197.87
2019-05-26 00:30 | 204.05 | 197.81
2019-05-26 01:00 | 203.59 | 197.18
2019-05-26 01:30 | 204.2 | 197.6
2019-05-26 02:00 | 204.15 | 197.6
2019-05-26 02:30 | 204.14 | 197.47
2019-05-26 03:00 | 204.31 | 197.6
2019-05-26 03:30 | 204.28 | 197.58
2019-05-26 04:00 | 204.37 | 197.69
2019-05-26 04:30 | 204.18 | 197.48
2019-05-26 05:00 | 204.74 | 198.06
2019-05-26 05:30 | 205.81 | 199.28
2019-05-26 06:00 | 206.22 | 199.77
2019-05-26 06:30 | 209.17 | 203.14
2019-05-26 07:00 | 210.97 | 205.06
2019-05-26 07:30 | 212.39 | 206.31
2019-05-26 08:00 | 212.41 | 206.46
2019-05-26 08:30 | 209.82 | 203.73
2019-05-26 09:00 | 208.24 | 201.55
2019-05-26 09:30 | 206.33 | 199.17
2019-05-26 10:00 | 204.5 | 196.61
2019-05-26 10:30 | 202.02 | 194.1
2019-05-26 11:00 | 201.1 | 192.97
2019-05-26 11:30 | 200.45 | 192.44
2019-05-26 12:00 | 200.22 | 192.21
2019-05-26 12:30 | 199.5 | 191.26
2019-05-26 13:00 | 204.46 | 196.18
2019-05-26 13:30 | 200.6 | 192.24
2019-05-26 14:00 | 198.89 | 190.57
2019-05-26 14:30 | 200.37 | 192
2019-05-26 15:00 | 200.56 | 191.92
2019-05-26 15:30 | 202.24 | 194
2019-05-26 16:00 | 203.32 | 195.22
2019-05-26 16:30 | 206.03 | 196.67
2019-05-26 17:00 | 209.21 | 200.42
2019-05-26 17:30 | 225.32 | 220.91
2019-05-26 18:00 | 223.52 | 219.82
2019-05-26 18:30 | 222.78 | 219.13
2019-05-26 19:00 | 223.22 | 219.19
2019-05-26 19:30 | 224.72 | 220.45
2019-05-26 20:00 | 225.28 | 221.45
2019-05-26 20:30 | 225.83 | 222.15
2019-05-26 21:00 | 226.3 | 222.81
2019-05-26 21:30 | 226.74 | 223.74
2019-05-26 22:00 | 213.39 | 205.55
2019-05-26 22:30 | 211.31 | 202.02
2019-05-26 23:00 | 209.09 | 200.43
2019-05-26 23:30 | 207.85 | 199.82
2019-05-27 | 206.65 | 198.77
2019-05-27 00:30 | 206.65 | 199.08
2019-05-27 01:00 | 205.24 | 198.41
2019-05-27 01:30 | 205.6 | 198.72
2019-05-27 02:00 | 205.53 | 198.5
2019-05-27 02:30 | 205.31 | 198.12
2019-05-27 03:00 | 205 | 197.8
2019-05-27 03:30 | 205.23 | 198.14
2019-05-27 04:00 | 204.91 | 197.68
2019-05-27 04:30 | 204.94 | 197.89
2019-05-27 05:00 | 205.58 | 198.8
2019-05-27 05:30 | 206.85 | 200.68
2019-05-27 06:00 | 209.55 | 203.36
2019-05-27 06:30 | 215.63 | 208.57
2019-05-27 07:00 | 219.81 | 212.5
2019-05-27 07:30 | 219.91 | 212.88
2019-05-27 08:00 | 222.41 | 215.3
2019-05-27 08:30 | 216.51 | 209.6
2019-05-27 09:00 | 212.85 | 205.2
2019-05-27 09:30 | 210.14 | 202.36
2019-05-27 10:00 | 176.51 | 168.7
2019-05-27 10:30 | 164.83 | 157.52
2019-05-27 11:00 | 164.38 | 157.14
2019-05-27 11:30 | 163.47 | 156.48
2019-05-27 12:00 | 164.14 | 156.7
2019-05-27 12:30 | 164.36 | 156.71
2019-05-27 13:00 | 164.3 | 156.7
2019-05-27 13:30 | 163.61 | 155.1
2019-05-27 14:00 | 162.98 | 154.69
2019-05-27 14:30 | 192.09 | 184.52
2019-05-27 15:00 | 204.87 | 197.18
2019-05-27 15:30 | 210.38 | 202.7
2019-05-27 16:00 | 210.45 | 202.92
2019-05-27 16:30 | 208.47 | 200.68
2019-05-27 17:00 | 212.39 | 206.71
2019-05-27 17:30 | 226.25 | 223.7
2019-05-27 18:00 | 222.96 | 220.72
2019-05-27 18:30 | 221.54 | 219.22
2019-05-27 19:00 | 223.65 | 221.28
2019-05-27 19:30 | 224.77 | 222.34
2019-05-27 20:00 | 226.21 | 223.76
2019-05-27 20:30 | 227.18 | 224.61
2019-05-27 21:00 | 227.76 | 224.99
2019-05-27 21:30 | 229.72 | 226.97
2019-05-27 22:00 | 220.17 | 214
2019-05-27 22:30 | 217.99 | 209.67
2019-05-27 23:00 | 216.87 | 208.15
2019-05-27 23:30 | 215.84 | 207.27
2019-05-28 | 215.11 | 206.64
2019-05-28 00:30 | 213.75 | 206.45
2019-05-28 01:00 | 212.92 | 205.91
2019-05-28 01:30 | 212.84 | 205.66
2019-05-28 02:00 | 211.88 | 204.53
2019-05-28 02:30 | 212.15 | 204.59
2019-05-28 03:00 | 212.01 | 204.39
2019-05-28 03:30 | 213.32 | 205.74
2019-05-28 04:00 | 214 | 206.47
2019-05-28 04:30 | 214.87 | 207.45
2019-05-28 05:00 | 216.83 | 209.84
2019-05-28 05:30 | 220.25 | 213.93
2019-05-28 06:00 | 223.13 | 217.27
2019-05-28 06:30 | 228.61 | 222.09
2019-05-28 07:00 | 232.49 | 225.2
2019-05-28 07:30 | 232.37 | 225.39
2019-05-28 08:00 | 230.61 | 223.62
2019-05-28 08:30 | 224.2 | 216.99
2019-05-28 09:00 | 219.03 | 211.36
2019-05-28 09:30 | 215.2 | 207.59
2019-05-28 10:00 | 213.25 | 205.43
2019-05-28 10:30 | 209.98 | 202.03
2019-05-28 11:00 | 208.73 | 200.71
2019-05-28 11:30 | 208.49 | 201.27
2019-05-28 12:00 | 207.22 | 200.94
2019-05-28 12:30 | 205.13 | 198.2
2019-05-28 13:00 | 203.04 | 195.88
2019-05-28 13:30 | 203.76 | 196.23
2019-05-28 14:00 | 205.23 | 196.91
2019-05-28 14:30 | 205.91 | 197.26
2019-05-28 15:00 | 206.47 | 197.32
2019-05-28 15:30 | 212.66 | 203.53
2019-05-28 16:00 | 220.34 | 211.8
2019-05-28 16:30 | 220.56 | 213.93
2019-05-28 17:00 | 224.5 | 220
2019-05-28 17:30 | 238.09 | 235.38
2019-05-28 18:00 | 233.81 | 231.12
2019-05-28 18:30 | 230.93 | 228.26
2019-05-28 19:00 | 231.42 | 228.69
2019-05-28 19:30 | 231.64 | 228.92
2019-05-28 20:00 | 232.76 | 230.11
2019-05-28 20:30 | 234.33 | 231.68
2019-05-28 21:00 | 231 | 224.68
2019-05-28 21:30 | 232.07 | 224.68
2019-05-28 22:00 | 229.23 | 222.55
2019-05-28 22:30 | 227.16 | 220.7
2019-05-28 23:00 | 225.76 | 219.05
2019-05-28 23:30 | 223.7 | 216.95
2019-05-29 | 222.06 | 215.47
2019-05-29 00:30 | 221.81 | 215.41
2019-05-29 01:00 | 220.74 | 215.51
2019-05-29 01:30 | 219.37 | 215.12
2019-05-29 02:00 | 219.96 | 215.01
2019-05-29 02:30 | 219.82 | 214.51
2019-05-29 03:00 | 220.2 | 214.9
2019-05-29 03:30 | 220.39 | 215.62
2019-05-29 04:00 | 221.91 | 216.99
2019-05-29 04:30 | 223.45 | 218.61
2019-05-29 05:00 | 224.69 | 219.99
2019-05-29 05:30 | 226.93 | 222.66
2019-05-29 06:00 | 230.88 | 226.11
2019-05-29 06:30 | 236.08 | 231.28
2019-05-29 07:00 | 254.4 | 248.81
2019-05-29 07:30 | 258.25 | 252.72
2019-05-29 08:00 | 255.33 | 250.14
2019-05-29 08:30 | 251.16 | 246.16
2019-05-29 09:00 | 246.61 | 241.54
2019-05-29 09:30 | 243.13 | 237.57
2019-05-29 10:00 | 223.23 | 217.95
2019-05-29 10:30 | 216.48 | 210.98
2019-05-29 11:00 | 211.45 | 206.3
2019-05-29 11:30 | 211.67 | 206.6
2019-05-29 12:00 | 213.03 | 207.75
2019-05-29 12:30 | 213.78 | 208.8
2019-05-29 13:00 | 213.58 | 207.91
2019-05-29 13:30 | 213.05 | 207.88
2019-05-29 14:00 | 213.63 | 208.34
2019-05-29 14:30 | 214.12 | 208.85
2019-05-29 15:00 | 215.47 | 210.15
2019-05-29 15:30 | 216.02 | 210.23
2019-05-29 16:00 | 215.1 | 208.91
2019-05-29 16:30 | 231.14 | 223.76
2019-05-29 17:00 | 236.51 | 228.81
2019-05-29 17:30 | 240.42 | 232.82
2019-05-29 18:00 | 245.77 | 238.54
2019-05-29 18:30 | 251.23 | 244.13
2019-05-29 19:00 | 252.14 | 245.09
2019-05-29 19:30 | 252.09 | 244.76
2019-05-29 20:00 | 250.97 | 243.8
2019-05-29 20:30 | 249.92 | 242.75
2019-05-29 21:00 | 248.12 | 240.97
2019-05-29 21:30 | 246.44 | 239.86
2019-05-29 22:00 | 244.11 | 237.98
2019-05-29 22:30 | 241.93 | 235.63
2019-05-29 23:00 | 240.44 | 233.95
2019-05-29 23:30 | 222.75 | 216.7
2019-05-30 | 215.66 | 209.94
2019-05-30 00:30 | 215.49 | 209.52
2019-05-30 01:00 | 214.72 | 208.64
2019-05-30 01:30 | 214.01 | 208.02
2019-05-30 02:00 | 213.84 | 208.04
2019-05-30 02:30 | 213.94 | 207.76
2019-05-30 03:00 | 214.56 | 208.21
2019-05-30 03:30 | 215.17 | 208.73
2019-05-30 04:00 | 216.2 | 209.46
2019-05-30 04:30 | 217.14 | 210.49
2019-05-30 05:00 | 219.42 | 212.96
2019-05-30 05:30 | 221.55 | 215.75
2019-05-30 06:00 | 225.7 | 219.38
2019-05-30 06:30 | 230.12 | 224.13
2019-05-30 07:00 | 229.42 | 225.6
2019-05-30 07:30 | 233.12 | 229.86
2019-05-30 08:00 | 234.19 | 229.97
2019-05-30 08:30 | 234.43 | 230.34
2019-05-30 09:00 | 221.05 | 213.16
2019-05-30 09:30 | 219.22 | 212.16
2019-05-30 10:00 | 214.43 | 207.64
2019-05-30 10:30 | 211.54 | 204.44
2019-05-30 11:00 | 210.53 | 203.27
2019-05-30 11:30 | 210.92 | 204.18
2019-05-30 12:00 | 210.84 | 204.06
2019-05-30 12:30 | 209.62 | 202.96
2019-05-30 13:00 | 208.96 | 202.55
2019-05-30 13:30 | 209.35 | 202.57
2019-05-30 14:00 | 209.8 | 202.99
2019-05-30 14:30 | 210.19 | 203.44
2019-05-30 15:00 | 210.63 | 203.69
2019-05-30 15:30 | 212.25 | 205.24
2019-05-30 16:00 | 214.93 | 207.85
2019-05-30 16:30 | 216.54 | 209.71
2019-05-30 17:00 | 222.29 | 215.58
2019-05-30 17:30 | 227.83 | 221.04
2019-05-30 18:00 | 232.43 | 229.64
2019-05-30 18:30 | 247.66 | 245.09
2019-05-30 19:00 | 247.07 | 244.5
2019-05-30 19:30 | 247.97 | 245.4
2019-05-30 20:00 | 249.15 | 244.38
2019-05-30 20:30 | 252.76 | 247.25
2019-05-30 21:00 | 251.28 | 245.45
2019-05-30 21:30 | 249.61 | 244.38
2019-05-30 22:00 | 247.6 | 242.23
2019-05-30 22:30 | 243.98 | 239.14
2019-05-30 23:00 | 242.2 | 236.94
2019-05-30 23:30 | 239.46 | 234.75
2019-05-31 | 238.12 | 233.57
2019-05-31 00:30 | 237.43 | 232.55
2019-05-31 01:00 | 236.24 | 231.66
2019-05-31 01:30 | 236.03 | 231.25
2019-05-31 02:00 | 235.59 | 230.88
2019-05-31 02:30 | 235.92 | 230.76
2019-05-31 03:00 | 235.05 | 230.41
2019-05-31 03:30 | 235.92 | 231.13
2019-05-31 04:00 | 236.49 | 231.56
2019-05-31 04:30 | 237.62 | 232.79
2019-05-31 05:00 | 239.09 | 234.48
2019-05-31 05:30 | 241.76 | 237.16
2019-05-31 06:00 | 246.37 | 240.49
2019-05-31 06:30 | 249.59 | 243.57
2019-05-31 07:00 | 252.22 | 248.27
2019-05-31 07:30 | 252.42 | 248.7
2019-05-31 08:00 | 252.98 | 249.27
2019-05-31 08:30 | 254.58 | 251.05
2019-05-31 09:00 | 257.54 | 253.78
2019-05-31 09:30 | 243.45 | 237.79
2019-05-31 10:00 | 236.79 | 231.18
2019-05-31 10:30 | 235.22 | 229.58
2019-05-31 11:00 | 235.47 | 229.75
2019-05-31 11:30 | 233.98 | 228.26
2019-05-31 12:00 | 232.95 | 227
2019-05-31 12:30 | 232.48 | 226.32
2019-05-31 13:00 | 231.01 | 225.19
2019-05-31 13:30 | 231.11 | 225
2019-05-31 14:00 | 231.73 | 225.51
2019-05-31 14:30 | 232.48 | 226.26
2019-05-31 15:00 | 232.5 | 226.21
2019-05-31 15:30 | 233.35 | 227.04
2019-05-31 16:00 | 235.24 | 228.89
2019-05-31 16:30 | 241.04 | 236.77
2019-05-31 17:00 | 256.03 | 254.03
2019-05-31 17:30 | 253.9 | 251.93
2019-05-31 18:00 | 249.83 | 248.04
2019-05-31 18:30 | 247.45 | 245.8
2019-05-31 19:00 | 246.2 | 244.6
2019-05-31 19:30 | 247.07 | 245.39
2019-05-31 20:00 | 247.55 | 245.86
2019-05-31 20:30 | 248.72 | 244.31
2019-05-31 21:00 | 251.8 | 246.41
2019-05-31 21:30 | 249.29 | 244.52
2019-05-31 22:00 | 247.85 | 243.01
2019-05-31 22:30 | 244.99 | 239.98
2019-05-31 23:00 | 243.52 | 238.04
2019-05-31 23:30 | 241.79 | 236.38
2019-06-01 | 240.34 | 234.96
2019-06-01 00:30 | 238.83 | 234.3
2019-06-01 01:00 | 237.69 | 233.27
2019-06-01 01:30 | 237.67 | 232.47
2019-06-01 02:00 | 237.34 | 231.95
2019-06-01 02:30 | 237.05 | 231.73
2019-06-01 03:00 | 237.54 | 231.54
2019-06-01 03:30 | 237.58 | 231.16
2019-06-01 04:00 | 238.51 | 231.82
2019-06-01 04:30 | 239.37 | 232.5
2019-06-01 05:00 | 240.04 | 233.07
2019-06-01 05:30 | 241.21 | 234.56
2019-06-01 06:00 | 243.78 | 237.7
2019-06-01 06:30 | 244.63 | 239.12
2019-06-01 07:00 | 246.38 | 241.2
2019-06-01 07:30 | 248.68 | 243.08
2019-06-01 08:00 | 250.05 | 243.78
2019-06-01 08:30 | 249.29 | 243.08
2019-06-01 09:00 | 248.96 | 243.01
2019-06-01 09:30 | 245.76 | 240.2
2019-06-01 10:00 | 243.76 | 238.03
2019-06-01 10:30 | 240.95 | 235.02
2019-06-01 11:00 | 238.8 | 232.89
2019-06-01 11:30 | 236.16 | 230.73
2019-06-01 12:00 | 235.67 | 230.02
2019-06-01 12:30 | 235.43 | 229.93
2019-06-01 13:00 | 234.11 | 228.4
2019-06-01 13:30 | 234.29 | 228.17
2019-06-01 14:00 | 234.61 | 228.44
2019-06-01 14:30 | 234.28 | 227.91
2019-06-01 15:00 | 234.94 | 228.15
2019-06-01 15:30 | 237.98 | 231.07
2019-06-01 16:00 | 240.39 | 233.41
2019-06-01 16:30 | 242.61 | 235.8
2019-06-01 17:00 | 250.22 | 246.83
2019-06-01 17:30 | 254.22 | 251.74
2019-06-01 18:00 | 251.89 | 249.53
2019-06-01 18:30 | 250.76 | 248.46
2019-06-01 19:00 | 251.62 | 249.32
2019-06-01 19:30 | 253.16 | 250.59
2019-06-01 20:00 | 253.61 | 251.13
2019-06-01 20:30 | 254.14 | 251.78
2019-06-01 21:00 | 254.69 | 252.63
2019-06-01 21:30 | 254.86 | 253.34
2019-06-01 22:00 | 243.22 | 238.96
2019-06-01 22:30 | 242.12 | 236.58
2019-06-01 23:00 | 240.05 | 234.08
2019-06-01 23:30 | 238.93 | 233.37
2019-06-02 | 236.69 | 230.98
2019-06-02 00:30 | 236.17 | 230.45
2019-06-02 01:00 | 235.39 | 229.92
2019-06-02 01:30 | 234.24 | 228.99
2019-06-02 02:00 | 233.4 | 228.11
2019-06-02 02:30 | 233.45 | 228.04
2019-06-02 03:00 | 232.79 | 227.38
2019-06-02 03:30 | 232.59 | 227.37
2019-06-02 04:00 | 232.23 | 227.22
2019-06-02 04:30 | 232.86 | 227.67
2019-06-02 05:00 | 232.71 | 227.36
2019-06-02 05:30 | 234.33 | 228.83
2019-06-02 06:00 | 235.42 | 229.6
2019-06-02 06:30 | 236.95 | 231.26
2019-06-02 07:00 | 238.41 | 233.14
2019-06-02 07:30 | 241.09 | 236.02
2019-06-02 08:00 | 241.52 | 236.64
2019-06-02 08:30 | 241.53 | 236.76
2019-06-02 09:00 | 240.96 | 235.69
2019-06-02 09:30 | 240.95 | 235.48
2019-06-02 10:00 | 240.08 | 234.24
2019-06-02 10:30 | 236.6 | 230.25
2019-06-02 11:00 | 233.71 | 227.3
2019-06-02 11:30 | 233.15 | 226.76
2019-06-02 12:00 | 232.39 | 226.22
2019-06-02 12:30 | 232.17 | 226.15
2019-06-02 13:00 | 233.55 | 227.26
2019-06-02 13:30 | 231.34 | 224.59
2019-06-02 14:00 | 231.23 | 224.49
2019-06-02 14:30 | 231.99 | 225.02
2019-06-02 15:00 | 233.19 | 226.08
2019-06-02 15:30 | 234.25 | 227.25
2019-06-02 16:00 | 235.44 | 228.4
2019-06-02 16:30 | 239.4 | 234.23
2019-06-02 17:00 | 253.89 | 251.37
2019-06-02 17:30 | 251.73 | 249.26
2019-06-02 18:00 | 249.19 | 246.55
2019-06-02 18:30 | 248.04 | 245.46
2019-06-02 19:00 | 248.98 | 246.39
2019-06-02 19:30 | 249.37 | 246.67
2019-06-02 20:00 | 250.61 | 247.87
2019-06-02 20:30 | 250.03 | 247.34
2019-06-02 21:00 | 251.42 | 248.84
2019-06-02 21:30 | 242.19 | 236.16
2019-06-02 22:00 | 241.35 | 234.27
2019-06-02 22:30 | 239.23 | 231.84
2019-06-02 23:00 | 237.28 | 229.74
2019-06-02 23:30 | 235.74 | 228.57
2019-06-03 | 233.89 | 227.13
2019-06-03 00:30 | 233.7 | 226.85
2019-06-03 01:00 | 232.97 | 226.06
2019-06-03 01:30 | 232.36 | 225.34
2019-06-03 02:00 | 232.48 | 225.32
2019-06-03 02:30 | 231.76 | 224.48
2019-06-03 03:00 | 232.42 | 225.07
2019-06-03 03:30 | 231.82 | 224.38
2019-06-03 04:00 | 232.86 | 225.61
2019-06-03 04:30 | 232.9 | 225.82
2019-06-03 05:00 | 234.16 | 227.32
2019-06-03 05:30 | 235.65 | 229.24
2019-06-03 06:00 | 220.58 | 215.79
2019-06-03 06:30 | 244.46 | 241.82
2019-06-03 07:00 | 253.2 | 250.15
2019-06-03 07:30 | 254.85 | 250.9
2019-06-03 08:00 | 255.37 | 251.09
2019-06-03 08:30 | 258.11 | 253.87
2019-06-03 09:00 | 261.78 | 257.17
2019-06-03 09:30 | 247.93 | 241.45
2019-06-03 10:00 | 244.73 | 236.6
2019-06-03 10:30 | 241.74 | 233.4
2019-06-03 11:00 | 240.62 | 232.35
2019-06-03 11:30 | 238.92 | 230.49
2019-06-03 12:00 | 239.12 | 230.82
2019-06-03 12:30 | 235.5 | 226.78
2019-06-03 13:00 | 233.57 | 224.63
2019-06-03 13:30 | 232.49 | 223.4
2019-06-03 14:00 | 232.89 | 223.85
2019-06-03 14:30 | 232.61 | 223.59
2019-06-03 15:00 | 233.21 | 225.01
2019-06-03 15:30 | 235 | 225.96
2019-06-03 16:00 | 242.9 | 227.42
2019-06-03 16:30 | 245.7 | 231.58
2019-06-03 17:00 | 249.8 | 243.62
2019-06-03 17:30 | 255.97 | 249.22
2019-06-03 18:00 | 254.43 | 244.81
2019-06-03 18:30 | 252.84 | 242.64
2019-06-03 19:00 | 252.87 | 242.37
2019-06-03 19:30 | 253.2 | 242.93
2019-06-03 20:00 | 254.1 | 244.07
2019-06-03 20:30 | 254.34 | 244.08
2019-06-03 21:00 | 254.44 | 246.2
2019-06-03 21:30 | 247.61 | 242.13
2019-06-03 22:00 | 251.93 | 242.26
2019-06-03 22:30 | 251.84 | 238.48
2019-06-03 23:00 | 250.09 | 237.31
2019-06-03 23:30 | 248.13 | 235.84
2019-06-04 | 245.92 | 233.62
2019-06-04 00:30 | 245.96 | 232.67
2019-06-04 01:00 | 244.82 | 230.39
2019-06-04 01:30 | 244.04 | 229.21
2019-06-04 02:00 | 244.02 | 229.53
2019-06-04 02:30 | 243.11 | 229.21
2019-06-04 03:00 | 241.94 | 227.4
2019-06-04 03:30 | 241.91 | 226.65
2019-06-04 04:00 | 243.1 | 227.63
2019-06-04 04:30 | 243.76 | 228.37
2019-06-04 05:00 | 245.46 | 230.15
2019-06-04 05:30 | 248.01 | 233.7
2019-06-04 06:00 | 251.18 | 237.56
2019-06-04 06:30 | 240.29 | 228.7
2019-06-04 07:00 | 231.88 | 223.4
2019-06-04 07:30 | 248.57 | 241.77
2019-06-04 08:00 | 249.28 | 242.67
2019-06-04 08:30 | 242.4 | 233.33
2019-06-04 09:00 | 250.41 | 242.49
2019-06-04 09:30 | 244.58 | 234.84
2019-06-04 10:00 | 250.38 | 243.68
2019-06-04 10:30 | 257.57 | 251.94
2019-06-04 11:00 | 260.71 | 255.64
2019-06-04 11:30 | 242.98 | 233.16
2019-06-04 12:00 | 240.82 | 228.67
2019-06-04 12:30 | 240.66 | 228.27
2019-06-04 13:00 | 230.46 | 225.37
2019-06-04 13:30 | 229.61 | 224.51
2019-06-04 14:00 | 231.92 | 225.54
2019-06-04 14:30 | 233.04 | 226.85
2019-06-04 15:00 | 234.42 | 228.4
2019-06-04 15:30 | 238.83 | 233.1
2019-06-04 16:00 | 242.64 | 236.47
2019-06-04 16:30 | 245.43 | 239.27
2019-06-04 17:00 | 247.02 | 242.2
2019-06-04 17:30 | 257.64 | 254.68
2019-06-04 18:00 | 251.07 | 248.32
2019-06-04 18:30 | 247.25 | 244.52
2019-06-04 19:00 | 243.8 | 240.6
2019-06-04 19:30 | 249 | 246.06
2019-06-04 20:00 | 250.44 | 247.41
2019-06-04 20:30 | 253.03 | 249.92
2019-06-04 21:00 | 255.36 | 252.16
2019-06-04 21:30 | 256.28 | 253.7
2019-06-04 22:00 | 257.79 | 254.68
2019-06-04 22:30 | 260.54 | 257.09
2019-06-04 23:00 | 262.57 | 259
2019-06-04 23:30 | 250.77 | 242.88
2019-06-05 | 249.16 | 240.51
2019-06-05 00:30 | 248.12 | 239.28
2019-06-05 01:00 | 245.11 | 237.83
2019-06-05 01:30 | 245.15 | 238.23
2019-06-05 02:00 | 244.22 | 237.05
2019-06-05 02:30 | 243.87 | 236.67
2019-06-05 03:00 | 243.21 | 235.86
2019-06-05 03:30 | 243.63 | 236.15
2019-06-05 04:00 | 243.19 | 235.8
2019-06-05 04:30 | 245.71 | 238.56
2019-06-05 05:00 | 247.35 | 240.3
2019-06-05 05:30 | 251.05 | 243.66
2019-06-05 06:00 | 254.21 | 247.17
2019-06-05 06:30 | 228.01 | 224.79
2019-06-05 07:00 | 181.8 | 179.99
2019-06-05 07:30 | 179.95 | 177.17
2019-06-05 08:00 | 177.28 | 175.57
2019-06-05 08:30 | 179.41 | 177.65
2019-06-05 09:00 | 176.57 | 173.59
2019-06-05 09:30 | 174.45 | 168.76
2019-06-05 10:00 | 170.09 | 164.29
2019-06-05 10:30 | 165.69 | 159.81
2019-06-05 11:00 | 163.67 | 157.43
2019-06-05 11:30 | 162.02 | 155.09
2019-06-05 12:00 | 162.28 | 155.48
2019-06-05 12:30 | 159.93 | 152.68
2019-06-05 13:00 | 159.28 | 152.29
2019-06-05 13:30 | 159.91 | 152.36
2019-06-05 14:00 | 160.98 | 153.45
2019-06-05 14:30 | 162.99 | 155.3
2019-06-05 15:00 | 163.34 | 155.79
2019-06-05 15:30 | 164.42 | 157.19
2019-06-05 16:00 | 166.36 | 159.13
2019-06-05 16:30 | 167.05 | 159.79
2019-06-05 17:00 | 169.63 | 162.55
2019-06-05 17:30 | 171.01 | 167.72
2019-06-05 18:00 | 170.42 | 167.85
2019-06-05 18:30 | 174.03 | 170.16
2019-06-05 19:00 | 193.7 | 189.42
2019-06-05 19:30 | 203.59 | 199.41
2019-06-05 20:00 | 238.07 | 229.93
2019-06-05 20:30 | 254.86 | 244.99
2019-06-05 21:00 | 254.62 | 244.34
2019-06-05 21:30 | 253.39 | 243.43
2019-06-05 22:00 | 250.89 | 241.57
2019-06-05 22:30 | 248.19 | 238.68
2019-06-05 23:00 | 245.45 | 235.59
2019-06-05 23:30 | 243.29 | 233.45
2019-06-06 | 240.76 | 231.08
2019-06-06 00:30 | 240.48 | 230.65
2019-06-06 01:00 | 239.22 | 229.02
2019-06-06 01:30 | 239.63 | 228.65
2019-06-06 02:00 | 238.51 | 227.85
2019-06-06 02:30 | 240.1 | 229.62
2019-06-06 03:00 | 238.46 | 227.22
2019-06-06 03:30 | 237.97 | 226.88
2019-06-06 04:00 | 238.57 | 227.38
2019-06-06 04:30 | 241.69 | 230.66
2019-06-06 05:00 | 245.75 | 235.62
2019-06-06 05:30 | 244.7 | 235.56
2019-06-06 06:00 | 204.72 | 197.36
2019-06-06 06:30 | 196.27 | 192.47
2019-06-06 07:00 | 200.49 | 198.26
2019-06-06 07:30 | 199.67 | 197.25
2019-06-06 08:00 | 199.26 | 196.7
2019-06-06 08:30 | 198.37 | 195.41
2019-06-06 09:00 | 222.49 | 218.63
2019-06-06 09:30 | 244.11 | 238.36
2019-06-06 10:00 | 241.77 | 233.91
2019-06-06 10:30 | 238.68 | 231.38
2019-06-06 11:00 | 236.06 | 228.5
2019-06-06 11:30 | 235.19 | 227.48
2019-06-06 12:00 | 233.41 | 226.07
2019-06-06 12:30 | 232.89 | 225.78
2019-06-06 13:00 | 232.56 | 225.43
2019-06-06 13:30 | 232.42 | 225.32
2019-06-06 14:00 | 233.35 | 225.95
2019-06-06 14:30 | 233.52 | 225.88
2019-06-06 15:00 | 235.16 | 227.11
2019-06-06 15:30 | 236.36 | 228.37
2019-06-06 16:00 | 238.39 | 230.63
2019-06-06 16:30 | 240.14 | 232.32
2019-06-06 17:00 | 243.77 | 238.25
2019-06-06 17:30 | 253.85 | 251.25
2019-06-06 18:00 | 241.13 | 237.84
2019-06-06 18:30 | 219.65 | 213.96
2019-06-06 19:00 | 220.62 | 215.19
2019-06-06 19:30 | 220.25 | 214.66
2019-06-06 20:00 | 217.43 | 212
2019-06-06 20:30 | 217.51 | 211.83
2019-06-06 21:00 | 217.51 | 211.92
2019-06-06 21:30 | 218.31 | 212.7
2019-06-06 22:00 | 244.96 | 238.74
2019-06-06 22:30 | 248.31 | 242.47
2019-06-06 23:00 | 246.53 | 240.3
2019-06-06 23:30 | 245.05 | 238.69
2019-06-07 | 244.24 | 238.03
2019-06-07 00:30 | 242.72 | 236.14
2019-06-07 01:00 | 241.48 | 234.79
2019-06-07 01:30 | 240.67 | 234.22
2019-06-07 02:00 | 240.72 | 234.35
2019-06-07 02:30 | 239.93 | 234.33
2019-06-07 03:00 | 240.74 | 235.05
2019-06-07 03:30 | 240.9 | 235.12
2019-06-07 04:00 | 241.46 | 235.58
2019-06-07 04:30 | 242.61 | 236.76
2019-06-07 05:00 | 243.58 | 238.07
2019-06-07 05:30 | 246.18 | 241.03
2019-06-07 06:00 | 250.51 | 244.53
2019-06-07 06:30 | 239.46 | 234.54
2019-06-07 07:00 | 218.47 | 213.54
2019-06-07 07:30 | 222.62 | 217.68
2019-06-07 08:00 | 219.5 | 214.5
2019-06-07 08:30 | 219.21 | 214.26
2019-06-07 09:00 | 222.18 | 217.13
2019-06-07 09:30 | 226.77 | 221.71
2019-06-07 10:00 | 244.15 | 237.09
2019-06-07 10:30 | 242.6 | 234.59
2019-06-07 11:00 | 239.96 | 231.52
2019-06-07 11:30 | 237.84 | 229.33
2019-06-07 12:00 | 237.44 | 228.49
2019-06-07 12:30 | 239.09 | 229.65
2019-06-07 13:00 | 239.3 | 230.11
2019-06-07 13:30 | 239.18 | 229.16
2019-06-07 14:00 | 239.33 | 229.64
2019-06-07 14:30 | 240.39 | 230.63
2019-06-07 15:00 | 241.82 | 231.93
2019-06-07 15:30 | 242.09 | 232.33
2019-06-07 16:00 | 243.48 | 234.19
2019-06-07 16:30 | 244.11 | 234.75
2019-06-07 17:00 | 246.67 | 237.16
2019-06-07 17:30 | 248.91 | 239.45
2019-06-07 18:00 | 252.43 | 243.42
2019-06-07 18:30 | 254.7 | 245.93
2019-06-07 19:00 | 254.66 | 246.02
2019-06-07 19:30 | 254.3 | 245.49
2019-06-07 20:00 | 253.76 | 244.63
2019-06-07 20:30 | 252.83 | 243.45
2019-06-07 21:00 | 250.96 | 241.71
2019-06-07 21:30 | 249.36 | 240.89
2019-06-07 22:00 | 248.12 | 239.44
2019-06-07 22:30 | 245.98 | 237.51
2019-06-07 23:00 | 242.88 | 235.58
2019-06-07 23:30 | 240.15 | 234.27
2019-06-08 | 240.26 | 232.86
2019-06-08 00:30 | 239.55 | 231.49
2019-06-08 01:00 | 237.38 | 230.14
2019-06-08 01:30 | 237.11 | 229.61
2019-06-08 02:00 | 236.8 | 229.07
2019-06-08 02:30 | 236.14 | 228.75
2019-06-08 03:00 | 236.86 | 229.26
2019-06-08 03:30 | 235.68 | 228.71
2019-06-08 04:00 | 236.3 | 228.88
2019-06-08 04:30 | 236.73 | 229.15
2019-06-08 05:00 | 237.86 | 230.45
2019-06-08 05:30 | 238.47 | 231.37
2019-06-08 06:00 | 238.79 | 231.95
2019-06-08 06:30 | 240.61 | 233.4
2019-06-08 07:00 | 242.54 | 235.07
2019-06-08 07:30 | 243.17 | 235.9
2019-06-08 08:00 | 245.64 | 237.19
2019-06-08 08:30 | 246.2 | 237.77
2019-06-08 09:00 | 246.47 | 238.15
2019-06-08 09:30 | 247.06 | 237.89
2019-06-08 10:00 | 247.53 | 238.26
2019-06-08 10:30 | 246.45 | 237.53
2019-06-08 11:00 | 243.81 | 236.36
2019-06-08 11:30 | 243.97 | 236.43
2019-06-08 12:00 | 243.2 | 235.7
2019-06-08 12:30 | 244.23 | 236.39
2019-06-08 13:00 | 243.98 | 235.99
2019-06-08 13:30 | 243.18 | 234.93
2019-06-08 14:00 | 242.73 | 234.53
2019-06-08 14:30 | 242.84 | 234.58
2019-06-08 15:00 | 243.46 | 235.18
2019-06-08 15:30 | 243.69 | 235.21
2019-06-08 16:00 | 244.12 | 235.56
2019-06-08 16:30 | 246.32 | 237.32
2019-06-08 17:00 | 248.35 | 239.41
2019-06-08 17:30 | 251.12 | 242.02
2019-06-08 18:00 | 253.88 | 245.52
2019-06-08 18:30 | 255.02 | 246.9
2019-06-08 19:00 | 254.39 | 245.69
2019-06-08 19:30 | 254.52 | 245.22
2019-06-08 20:00 | 253.31 | 243.91
2019-06-08 20:30 | 251.97 | 243.81
2019-06-08 21:00 | 248.96 | 241.05
2019-06-08 21:30 | 249 | 241.18
2019-06-08 22:00 | 247.54 | 239.57
2019-06-08 22:30 | 245.14 | 237.9
2019-06-08 23:00 | 243.39 | 235.93
2019-06-08 23:30 | 242.18 | 235.05
2019-06-09 | 239.75 | 233.45
2019-06-09 00:30 | 239.49 | 232.88
2019-06-09 01:00 | 239.08 | 231.97
2019-06-09 01:30 | 239.35 | 231.04
2019-06-09 02:00 | 239.36 | 231.04
2019-06-09 02:30 | 238.14 | 230.38
2019-06-09 03:00 | 237.75 | 230.28
2019-06-09 03:30 | 237.77 | 230.05
2019-06-09 04:00 | 238.21 | 230.24
2019-06-09 04:30 | 238.08 | 230.18
2019-06-09 05:00 | 238.18 | 230.3
2019-06-09 05:30 | 238.4 | 230.65
2019-06-09 06:00 | 239.65 | 232.04
2019-06-09 06:30 | 240.78 | 233.34
2019-06-09 07:00 | 242.28 | 234.8
2019-06-09 07:30 | 241.56 | 234.86
2019-06-09 08:00 | 242.49 | 235.92
2019-06-09 08:30 | 242.47 | 236.24
2019-06-09 09:00 | 242.97 | 235.99
2019-06-09 09:30 | 241.01 | 233.85
2019-06-09 10:00 | 240.38 | 233.11
2019-06-09 10:30 | 238.68 | 231.54
2019-06-09 11:00 | 249.41 | 242.29
2019-06-09 11:30 | 239 | 231.59
2019-06-09 12:00 | 193.44 | 187.86
2019-06-09 12:30 | 187.75 | 181.12
2019-06-09 13:00 | 178.87 | 169.34
2019-06-09 13:30 | 170.67 | 161.3
2019-06-09 14:00 | 168.82 | 161.65
2019-06-09 14:30 | 169.27 | 161.99
2019-06-09 15:00 | 168.7 | 161.37
2019-06-09 15:30 | 197.97 | 191.05
2019-06-09 16:00 | 229.39 | 222.51
2019-06-09 16:30 | 240.63 | 233.3
2019-06-09 17:00 | 242.63 | 234.81
2019-06-09 17:30 | 243.64 | 237
2019-06-09 18:00 | 246.9 | 240.83
2019-06-09 18:30 | 249.8 | 244.16
2019-06-09 19:00 | 249.86 | 244.51
2019-06-09 19:30 | 250.07 | 244.59
2019-06-09 20:00 | 248.61 | 243.32
2019-06-09 20:30 | 247.97 | 242.66
2019-06-09 21:00 | 246.25 | 240.94
2019-06-09 21:30 | 245.18 | 240.73
2019-06-09 22:00 | 242.76 | 238.86
2019-06-09 22:30 | 241.12 | 237.05
2019-06-09 23:00 | 238.72 | 234.62
2019-06-09 23:30 | 237.45 | 233.4
2019-06-10 | 236.6 | 232.46
2019-06-10 00:30 | 236.48 | 231.68
2019-06-10 01:00 | 236.26 | 231.38
2019-06-10 01:30 | 235.11 | 230.31
2019-06-10 02:00 | 235.92 | 231.09
2019-06-10 02:30 | 236.01 | 231
2019-06-10 03:00 | 236.14 | 231.01
2019-06-10 03:30 | 236.68 | 231.53
2019-06-10 04:00 | 236.98 | 231.78
2019-06-10 04:30 | 237.36 | 232.47
2019-06-10 05:00 | 238.67 | 233.91
2019-06-10 05:30 | 241.02 | 235.96
2019-06-10 06:00 | 243.53 | 238.35
2019-06-10 06:30 | 247.65 | 242.93
2019-06-10 07:00 | 250.99 | 246.78
2019-06-10 07:30 | 252.17 | 247.98
2019-06-10 08:00 | 250.38 | 246.15
2019-06-10 08:30 | 247.07 | 242.69
2019-06-10 09:00 | 243.52 | 239.04
2019-06-10 09:30 | 240.23 | 235.48
2019-06-10 10:00 | 236.48 | 231.55
2019-06-10 10:30 | 234.72 | 229.54
2019-06-10 11:00 | 231.98 | 226.92
2019-06-10 11:30 | 231.87 | 226.34
2019-06-10 12:00 | 232.5 | 226.82
2019-06-10 12:30 | 231.6 | 225.65
2019-06-10 13:00 | 230.33 | 224.46
2019-06-10 13:30 | 230.56 | 224.67
2019-06-10 14:00 | 231.47 | 225.84
2019-06-10 14:30 | 233.61 | 227.98
2019-06-10 15:00 | 234.48 | 228.74
2019-06-10 15:30 | 235.67 | 229.88
2019-06-10 16:00 | 235.83 | 229.81
2019-06-10 16:30 | 237.89 | 231.55
2019-06-10 17:00 | 239.93 | 233.32
2019-06-10 17:30 | 242.25 | 235.83
2019-06-10 18:00 | 246.57 | 240.41
2019-06-10 18:30 | 250.1 | 243.94
2019-06-10 19:00 | 250.28 | 243.99
2019-06-10 19:30 | 249.63 | 243.09
2019-06-10 20:00 | 248.34 | 241.7
2019-06-10 20:30 | 247.78 | 240.96
2019-06-10 21:00 | 246.31 | 239.2
2019-06-10 21:30 | 245.52 | 238.83
2019-06-10 22:00 | 241.62 | 237.61
2019-06-10 22:30 | 238.78 | 235.15
2019-06-10 23:00 | 236.87 | 233.23
2019-06-10 23:30 | 236.46 | 232.83
2019-06-11 | 235.08 | 231.07
2019-06-11 00:30 | 234.65 | 230.46
2019-06-11 01:00 | 234.69 | 229.58
2019-06-11 01:30 | 233.76 | 228.77
2019-06-11 02:00 | 234.06 | 228.88
2019-06-11 02:30 | 233.31 | 228.27
2019-06-11 03:00 | 233.12 | 228.41
2019-06-11 03:30 | 233 | 228.39
2019-06-11 04:00 | 232.99 | 228.48
2019-06-11 04:30 | 233.59 | 229.03
2019-06-11 05:00 | 234.62 | 230.15
2019-06-11 05:30 | 236.56 | 232.71
2019-06-11 06:00 | 238.73 | 235.17
2019-06-11 06:30 | 242.56 | 239.12
2019-06-11 07:00 | 247.5 | 243.48
2019-06-11 07:30 | 247.5 | 243.55
2019-06-11 08:00 | 245.46 | 241.96
2019-06-11 08:30 | 241.98 | 238.63
2019-06-11 09:00 | 237.48 | 234.05
2019-06-11 09:30 | 234.16 | 230.55
2019-06-11 10:00 | 232.76 | 229.14
2019-06-11 10:30 | 230.93 | 227.3
2019-06-11 11:00 | 229.48 | 225.86
2019-06-11 11:30 | 229.42 | 225.39
2019-06-11 12:00 | 228.99 | 225.13
2019-06-11 12:30 | 229.21 | 225.04
2019-06-11 13:00 | 229.46 | 225.62
2019-06-11 13:30 | 230.41 | 226.67
2019-06-11 14:00 | 231.02 | 227.26
2019-06-11 14:30 | 231.25 | 227.59
2019-06-11 15:00 | 231.86 | 227.92
2019-06-11 15:30 | 232.79 | 228.73
2019-06-11 16:00 | 234.53 | 230.42
2019-06-11 16:30 | 235.66 | 231.67
2019-06-11 17:00 | 232.27 | 228.94
2019-06-11 17:30 | 229.62 | 226.36
2019-06-11 18:00 | 245.17 | 240.78
2019-06-11 18:30 | 249.31 | 245.08
2019-06-11 19:00 | 249.41 | 245.16
2019-06-11 19:30 | 248.11 | 243.68
2019-06-11 20:00 | 247.38 | 242.81
2019-06-11 20:30 | 246.47 | 241.85
2019-06-11 21:00 | 245.14 | 240.57
2019-06-11 21:30 | 243.88 | 239.78
2019-06-11 22:00 | 242.96 | 238.88
2019-06-11 22:30 | 240.24 | 236.18
2019-06-11 23:00 | 238.15 | 234.05
2019-06-11 23:30 | 235.81 | 231.39
2019-06-12 | 231.42 | 227.13
2019-06-12 00:30 | 232.16 | 227.81
2019-06-12 01:00 | 233.46 | 229.64
2019-06-12 01:30 | 233.13 | 229.47
2019-06-12 02:00 | 233.2 | 229.4
2019-06-12 02:30 | 233.09 | 229.23
2019-06-12 03:00 | 232.52 | 228.66
2019-06-12 03:30 | 232.62 | 228.76
2019-06-12 04:00 | 233.24 | 229.51
2019-06-12 04:30 | 233.62 | 229.92
2019-06-12 05:00 | 234.77 | 231.11
2019-06-12 05:30 | 236.03 | 232.58
2019-06-12 06:00 | 237.97 | 234.41
2019-06-12 06:30 | 241.9 | 238.25
2019-06-12 07:00 | 242.19 | 238.54
2019-06-12 07:30 | 242.8 | 239.23
2019-06-12 08:00 | 241.52 | 238.29
2019-06-12 08:30 | 240.47 | 237.46
2019-06-12 09:00 | 236.96 | 233.9
2019-06-12 09:30 | 233.19 | 230
2019-06-12 10:00 | 230.06 | 226.91
2019-06-12 10:30 | 228.18 | 224.93
2019-06-12 11:00 | 228.11 | 224.95
2019-06-12 11:30 | 227.89 | 224.75
2019-06-12 12:00 | 226.89 | 223.79
2019-06-12 12:30 | 226.23 | 222.9
2019-06-12 13:00 | 226.08 | 222.49
2019-06-12 13:30 | 226.44 | 222.7
2019-06-12 14:00 | 227.17 | 223.46
2019-06-12 14:30 | 228.53 | 224.46
2019-06-12 15:00 | 229.32 | 225.04
2019-06-12 15:30 | 230.64 | 226.28
2019-06-12 16:00 | 232.93 | 228.43
2019-06-12 16:30 | 233.98 | 229.52
2019-06-12 17:00 | 236.46 | 232.51
2019-06-12 17:30 | 238.92 | 235.17
2019-06-12 18:00 | 243.3 | 239.21
2019-06-12 18:30 | 247.57 | 243.75
2019-06-12 19:00 | 247.45 | 243.52
2019-06-12 19:30 | 246.68 | 242.52
2019-06-12 20:00 | 245.61 | 241.37
2019-06-12 20:30 | 244.66 | 240.36
2019-06-12 21:00 | 243.15 | 238.9
2019-06-12 21:30 | 242.57 | 238.41
2019-06-12 22:00 | 241.53 | 237.06
2019-06-12 22:30 | 239.42 | 234.91
2019-06-12 23:00 | 237.87 | 233.33
2019-06-12 23:30 | 236.42 | 232.06
2019-06-13 | 235.14 | 230.71
2019-06-13 00:30 | 234.31 | 229.75
2019-06-13 01:00 | 233.97 | 229.16
2019-06-13 01:30 | 232.9 | 227.97
2019-06-13 02:00 | 232.95 | 227.75
2019-06-13 02:30 | 231.57 | 227.55
2019-06-13 03:00 | 231.08 | 227.19
2019-06-13 03:30 | 231.26 | 227.35
2019-06-13 04:00 | 231.05 | 227.17
2019-06-13 04:30 | 231.9 | 228.07
2019-06-13 05:00 | 233.38 | 229.59
2019-06-13 05:30 | 235.13 | 231.53
2019-06-13 06:00 | 237.32 | 233.94
2019-06-13 06:30 | 240.76 | 237.65
2019-06-13 07:00 | 243.88 | 240.82
2019-06-13 07:30 | 244.46 | 241.2
2019-06-13 08:00 | 244.01 | 240.89
2019-06-13 08:30 | 240.6 | 237.48
2019-06-13 09:00 | 237.99 | 234.36
2019-06-13 09:30 | 234.38 | 230.9
2019-06-13 10:00 | 232.7 | 228.97
2019-06-13 10:30 | 230.04 | 226.54
2019-06-13 11:00 | 228.72 | 225.09
2019-06-13 11:30 | 228.88 | 225.22
2019-06-13 12:00 | 228.77 | 225.07
2019-06-13 12:30 | 229.24 | 224.45
2019-06-13 13:00 | 229.35 | 224.2
2019-06-13 13:30 | 229.38 | 224.37
2019-06-13 14:00 | 230.53 | 225.33
2019-06-13 14:30 | 231.43 | 226.41
2019-06-13 15:00 | 232.46 | 227.27
2019-06-13 15:30 | 232.93 | 227.94
2019-06-13 16:00 | 232.44 | 229.07
2019-06-13 16:30 | 233.04 | 229.96
2019-06-13 17:00 | 234.38 | 231.33
2019-06-13 17:30 | 236.28 | 233.23
2019-06-13 18:00 | 240.14 | 237.11
2019-06-13 18:30 | 244.71 | 241.75
2019-06-13 19:00 | 244.79 | 241.85
2019-06-13 19:30 | 243.74 | 240.8
2019-06-13 20:00 | 243.03 | 240.05
2019-06-13 20:30 | 239.6 | 236.56
2019-06-13 21:00 | 241.33 | 238.28
2019-06-13 21:30 | 240.5 | 237.46
2019-06-13 22:00 | 239.67 | 236.48
2019-06-13 22:30 | 237.66 | 234.25
2019-06-13 23:00 | 236.03 | 232.66
2019-06-13 23:30 | 235.1 | 231.53
2019-06-14 | 234.09 | 229.82
2019-06-14 00:30 | 234.13 | 229.36
2019-06-14 01:00 | 232.76 | 228.4
2019-06-14 01:30 | 232.84 | 228.2
2019-06-14 02:00 | 231.88 | 227.47
2019-06-14 02:30 | 231.67 | 227.45
2019-06-14 03:00 | 231.42 | 227.34
2019-06-14 03:30 | 231.78 | 227.85
2019-06-14 04:00 | 232.65 | 227.79
2019-06-14 04:30 | 233.14 | 228.28
2019-06-14 05:00 | 234.41 | 229.5
2019-06-14 05:30 | 236.09 | 230.97
2019-06-14 06:00 | 237.95 | 232.63
2019-06-14 06:30 | 238.32 | 234.58
2019-06-14 07:00 | 240.55 | 237.72
2019-06-14 07:30 | 241.11 | 238.37
2019-06-14 08:00 | 240.93 | 238.14
2019-06-14 08:30 | 238.73 | 235.87
2019-06-14 09:00 | 236.63 | 233.73
2019-06-14 09:30 | 232.58 | 229.57
2019-06-14 10:00 | 230.62 | 227.52
2019-06-14 10:30 | 230.51 | 227.47
2019-06-14 11:00 | 230.2 | 227.25
2019-06-14 11:30 | 229.12 | 226.21
2019-06-14 12:00 | 228.48 | 225.57
2019-06-14 12:30 | 227.05 | 224.04
2019-06-14 13:00 | 226.42 | 223.38
2019-06-14 13:30 | 226.29 | 223.23
2019-06-14 14:00 | 226.72 | 223.62
2019-06-14 14:30 | 227.36 | 224.21
2019-06-14 15:00 | 229.26 | 226.03
2019-06-14 15:30 | 230.27 | 226.92
2019-06-14 16:00 | 231.62 | 228.47
2019-06-14 16:30 | 232.83 | 229.64
2019-06-14 17:00 | 234.65 | 231.42
2019-06-14 17:30 | 236.45 | 233.35
2019-06-14 18:00 | 239.11 | 236.12
2019-06-14 18:30 | 241.82 | 238.8
2019-06-14 19:00 | 241.54 | 238.52
2019-06-14 19:30 | 240.92 | 237.83
2019-06-14 20:00 | 240.31 | 237.12
2019-06-14 20:30 | 239.72 | 236.54
2019-06-14 21:00 | 239.16 | 235.91
2019-06-14 21:30 | 241.2 | 237.93
2019-06-14 22:00 | 242.35 | 238.99
2019-06-14 22:30 | 240.36 | 236.97
2019-06-14 23:00 | 239.32 | 235.41
2019-06-14 23:30 | 240.07 | 235
2019-06-15 | 239.31 | 233.9
2019-06-15 00:30 | 238.87 | 233.82
2019-06-15 01:00 | 237.71 | 232.72
2019-06-15 01:30 | 236.68 | 231.27
2019-06-15 02:00 | 236.53 | 230.81
2019-06-15 02:30 | 236.27 | 230.83
2019-06-15 03:00 | 235.26 | 230.26
2019-06-15 03:30 | 238.48 | 233.51
2019-06-15 04:00 | 236.86 | 232.51
2019-06-15 04:30 | 236.03 | 232.27
2019-06-15 05:00 | 235.81 | 232.27
2019-06-15 05:30 | 236.85 | 233.13
2019-06-15 06:00 | 238.26 | 234.57
2019-06-15 06:30 | 240.63 | 236.53
2019-06-15 07:00 | 242.88 | 238.34
2019-06-15 07:30 | 241.71 | 237.71
2019-06-15 08:00 | 241.36 | 237.95
2019-06-15 08:30 | 240.64 | 237.14
2019-06-15 09:00 | 239.18 | 235.68
2019-06-15 09:30 | 236.49 | 232.86
2019-06-15 10:00 | 234.42 | 231.02
2019-06-15 10:30 | 234.19 | 230.84
2019-06-15 11:00 | 231.98 | 228.65
2019-06-15 11:30 | 230.7 | 227.36
2019-06-15 12:00 | 229.65 | 226.33
2019-06-15 12:30 | 229.54 | 226.14
2019-06-15 13:00 | 229.04 | 225.58
2019-06-15 13:30 | 228.91 | 225.52
2019-06-15 14:00 | 228.23 | 224.86
2019-06-15 14:30 | 228.2 | 224.76
2019-06-15 15:00 | 229.6 | 226.07
2019-06-15 15:30 | 231.07 | 227.3
2019-06-15 16:00 | 232.79 | 228.78
2019-06-15 16:30 | 234.92 | 231.2
2019-06-15 17:00 | 237.36 | 233.62
2019-06-15 17:30 | 240.58 | 236.56
2019-06-15 18:00 | 244.57 | 240.99
2019-06-15 18:30 | 247 | 243.55
2019-06-15 19:00 | 246.26 | 242.77
2019-06-15 19:30 | 245.34 | 241.83
2019-06-15 20:00 | 244.56 | 240.98
2019-06-15 20:30 | 243.61 | 239.93
2019-06-15 21:00 | 242.63 | 239.04
2019-06-15 21:30 | 242.33 | 238.6
2019-06-15 22:00 | 241.29 | 237.6
2019-06-15 22:30 | 240.14 | 236.12
2019-06-15 23:00 | 239.58 | 234.69
2019-06-15 23:30 | 238.87 | 233.83
2019-06-16 | 237.72 | 232.43
2019-06-16 00:30 | 237.05 | 231.89
2019-06-16 01:00 | 236.28 | 231.46
2019-06-16 01:30 | 234.4 | 230.12
2019-06-16 02:00 | 234.46 | 230.09
2019-06-16 02:30 | 234.46 | 230.3
2019-06-16 03:00 | 234.21 | 230.26
2019-06-16 03:30 | 233.79 | 230.13
2019-06-16 04:00 | 234.44 | 230.74
2019-06-16 04:30 | 234.28 | 230.63
2019-06-16 05:00 | 234.91 | 231.31
2019-06-16 05:30 | 235.78 | 232.17
2019-06-16 06:00 | 236.53 | 232.96
2019-06-16 06:30 | 238.19 | 234.35
2019-06-16 07:00 | 240.68 | 236.67
2019-06-16 07:30 | 242 | 237.71
2019-06-16 08:00 | 243.53 | 238.68
2019-06-16 08:30 | 241.91 | 238.6
2019-06-16 09:00 | 239.64 | 236.42
2019-06-16 09:30 | 237 | 233.63
2019-06-16 10:00 | 235.02 | 231.65
2019-06-16 10:30 | 232.75 | 229.35
2019-06-16 11:00 | 235.83 | 232.6
2019-06-16 11:30 | 235.32 | 232.24
2019-06-16 12:00 | 234.84 | 231.68
2019-06-16 12:30 | 233.09 | 229.87
2019-06-16 13:00 | 232.13 | 228.79
2019-06-16 13:30 | 231.66 | 228.32
2019-06-16 14:00 | 231.37 | 228
2019-06-16 14:30 | 229.49 | 226.04
2019-06-16 15:00 | 230.01 | 226.67
2019-06-16 15:30 | 232.37 | 228.65
2019-06-16 16:00 | 235.57 | 230.77
2019-06-16 16:30 | 230.64 | 227.26
2019-06-16 17:00 | 225.11 | 222.74
2019-06-16 17:30 | 220.4 | 218.06
2019-06-16 18:00 | 219.44 | 217.09
2019-06-16 18:30 | 244.28 | 241.24
2019-06-16 19:00 | 246.93 | 243.66
2019-06-16 19:30 | 247.27 | 243.77
2019-06-16 20:00 | 246.02 | 242.33
2019-06-16 20:30 | 244.99 | 241.27
2019-06-16 21:00 | 243.86 | 239.8
2019-06-16 21:30 | 243.71 | 238.69
2019-06-16 22:00 | 242.71 | 237.27
2019-06-16 22:30 | 240.95 | 235.42
2019-06-16 23:00 | 238.63 | 233.41
2019-06-16 23:30 | 237.69 | 232.98
2019-06-17 | 236.37 | 231.71
2019-06-17 00:30 | 236.32 | 231.47
2019-06-17 01:00 | 235.51 | 231.35
2019-06-17 01:30 | 234.49 | 230.43
2019-06-17 02:00 | 234.74 | 230.59
2019-06-17 02:30 | 234.08 | 230.08
2019-06-17 03:00 | 234.65 | 230.47
2019-06-17 03:30 | 234.81 | 230.75
2019-06-17 04:00 | 235.34 | 231.46
2019-06-17 04:30 | 235.7 | 231.92
2019-06-17 05:00 | 237.05 | 233.32
2019-06-17 05:30 | 240.31 | 236.61
2019-06-17 06:00 | 242.95 | 239.2
2019-06-17 06:30 | 247.53 | 244.17
2019-06-17 07:00 | 252.07 | 249.13
2019-06-17 07:30 | 255.07 | 252.22
2019-06-17 08:00 | 254.71 | 251.8
2019-06-17 08:30 | 250.21 | 247.28
2019-06-17 09:00 | 246.6 | 243.57
2019-06-17 09:30 | 242.92 | 239.85
2019-06-17 10:00 | 240.61 | 237.51
2019-06-17 10:30 | 237.63 | 234.45
2019-06-17 11:00 | 236.22 | 232.93
2019-06-17 11:30 | 234.17 | 231.01
2019-06-17 12:00 | 233.58 | 230.36
2019-06-17 12:30 | 233.01 | 229.66
2019-06-17 13:00 | 232.45 | 229.23
2019-06-17 13:30 | 232.41 | 229.05
2019-06-17 14:00 | 233.87 | 229.83
2019-06-17 14:30 | 233.9 | 229.91
2019-06-17 15:00 | 235.71 | 231.94
2019-06-17 15:30 | 236.75 | 233.15
2019-06-17 16:00 | 238.46 | 235.04
2019-06-17 16:30 | 240.35 | 237.07
2019-06-17 17:00 | 243.09 | 239.9
2019-06-17 17:30 | 246.32 | 243.21
2019-06-17 18:00 | 252.12 | 249.33
2019-06-17 18:30 | 257.83 | 255.16
2019-06-17 19:00 | 258.88 | 256.21
2019-06-17 19:30 | 258.28 | 255.61
2019-06-17 20:00 | 257.87 | 254.98
2019-06-17 20:30 | 256.56 | 253.63
2019-06-17 21:00 | 255.02 | 251.93
2019-06-17 21:30 | 253.37 | 250.27
2019-06-17 22:00 | 250.67 | 247.54
2019-06-17 22:30 | 248.51 | 245.12
2019-06-17 23:00 | 246.02 | 242.57
2019-06-17 23:30 | 245.54 | 241.44
2019-06-18 | 244.57 | 239.9
2019-06-18 00:30 | 244.25 | 239.63
2019-06-18 01:00 | 242.97 | 238.21
2019-06-18 01:30 | 242.4 | 237.31
2019-06-18 02:00 | 242.84 | 237.3
2019-06-18 02:30 | 242.55 | 237
2019-06-18 03:00 | 242.61 | 237.07
2019-06-18 03:30 | 243.3 | 237.86
2019-06-18 04:00 | 243.64 | 238.32
2019-06-18 04:30 | 244.64 | 239.27
2019-06-18 05:00 | 246.03 | 240.77
2019-06-18 05:30 | 249.32 | 243.9
2019-06-18 06:00 | 252.27 | 248.01
2019-06-18 06:30 | 256.54 | 253.39
2019-06-18 07:00 | 225.47 | 222.96
2019-06-18 07:30 | 220.26 | 217.79
2019-06-18 08:00 | 220.07 | 217.64
2019-06-18 08:30 | 221.03 | 218.8
2019-06-18 09:00 | 241.44 | 238.71
2019-06-18 09:30 | 244.2 | 241.22
2019-06-18 10:00 | 240.68 | 237.74
2019-06-18 10:30 | 237.37 | 234.25
2019-06-18 11:00 | 236.16 | 233.02
2019-06-18 11:30 | 233.73 | 230.74
2019-06-18 12:00 | 232.86 | 229.81
2019-06-18 12:30 | 232.91 | 229.57
2019-06-18 13:00 | 233.18 | 229.58
2019-06-18 13:30 | 233.55 | 229.71
2019-06-18 14:00 | 232.76 | 229.42
2019-06-18 14:30 | 233.44 | 230.3
2019-06-18 15:00 | 233.71 | 230.59
2019-06-18 15:30 | 236.61 | 233.58
2019-06-18 16:00 | 237.35 | 234.39
2019-06-18 16:30 | 238.99 | 235.94
2019-06-18 17:00 | 242.41 | 239.12
2019-06-18 17:30 | 225.42 | 222.84
2019-06-18 18:00 | 218.26 | 215.33
2019-06-18 18:30 | 216.61 | 213.56
2019-06-18 19:00 | 217.67 | 214.69
2019-06-18 19:30 | 217.28 | 214.26
2019-06-18 20:00 | 217.67 | 214.67
2019-06-18 20:30 | 217.87 | 214.95
2019-06-18 21:00 | 243.91 | 240.45
2019-06-18 21:30 | 250.36 | 247.31
2019-06-18 22:00 | 247.61 | 244.58
2019-06-18 22:30 | 244.58 | 241.43
2019-06-18 23:00 | 242.74 | 239.48
2019-06-18 23:30 | 240.98 | 237.76
2019-06-19 | 239.8 | 236.48
2019-06-19 00:30 | 239.23 | 235.51
2019-06-19 01:00 | 238.83 | 234.71
2019-06-19 01:30 | 239.03 | 234.13
2019-06-19 02:00 | 238.83 | 233.71
2019-06-19 02:30 | 238.71 | 233.74
2019-06-19 03:00 | 238.07 | 233.14
2019-06-19 03:30 | 239.13 | 234.18
2019-06-19 04:00 | 239.43 | 234.55
2019-06-19 04:30 | 240.61 | 235.95
2019-06-19 05:00 | 242.23 | 237.69
2019-06-19 05:30 | 245.35 | 240.6
2019-06-19 06:00 | 248.54 | 244.35
2019-06-19 06:30 | 253.33 | 249.96
2019-06-19 07:00 | 257.12 | 254.08
2019-06-19 07:30 | 229.45 | 227.37
2019-06-19 08:00 | 218.58 | 216.42
2019-06-19 08:30 | 218.22 | 216.2
2019-06-19 09:00 | 240.96 | 238.35
2019-06-19 09:30 | 244.96 | 241.62
2019-06-19 10:00 | 206.56 | 202
2019-06-19 10:30 | 174.89 | 169.22
2019-06-19 11:00 | 173.24 | 167.47
2019-06-19 11:30 | 171.99 | 165.99
2019-06-19 12:00 | 171.62 | 165.54
2019-06-19 12:30 | 170.09 | 163.92
2019-06-19 13:00 | 169.36 | 162.91
2019-06-19 13:30 | 169.65 | 162.39
2019-06-19 14:00 | 200.96 | 195.23
2019-06-19 14:30 | 228.29 | 223.58
2019-06-19 15:00 | 233.32 | 228.79
2019-06-19 15:30 | 235.1 | 230.66
2019-06-19 16:00 | 240.04 | 235.82
2019-06-19 16:30 | 240.67 | 236.56
2019-06-19 17:00 | 243.3 | 239.38
2019-06-19 17:30 | 247.54 | 243.87
2019-06-19 18:00 | 253 | 249.75
2019-06-19 18:30 | 257.26 | 254.31
2019-06-19 19:00 | 258.23 | 255.3
2019-06-19 19:30 | 256.85 | 253.89
2019-06-19 20:00 | 255.65 | 252.7
2019-06-19 20:30 | 253.72 | 250.81
2019-06-19 21:00 | 251.9 | 248.96
2019-06-19 21:30 | 249.9 | 246.98
2019-06-19 22:00 | 248.03 | 245.1
2019-06-19 22:30 | 245.7 | 242.65
2019-06-19 23:00 | 243.89 | 240.52
2019-06-19 23:30 | 243.56 | 239.24
2019-06-20 | 241.31 | 236.49
2019-06-20 00:30 | 241.75 | 237.07
2019-06-20 01:00 | 241.22 | 235.8
2019-06-20 01:30 | 241.02 | 235.52
2019-06-20 02:00 | 239.94 | 235.14
2019-06-20 02:30 | 238.6 | 234.89
2019-06-20 03:00 | 238.98 | 235.34
2019-06-20 03:30 | 238.35 | 234.79
2019-06-20 04:00 | 238.55 | 234.96
2019-06-20 04:30 | 239.57 | 236.12
2019-06-20 05:00 | 241.44 | 237.98
2019-06-20 05:30 | 244.46 | 240.97
2019-06-20 06:00 | 247.78 | 244.2
2019-06-20 06:30 | 251.63 | 248.92
2019-06-20 07:00 | 256.45 | 253.86
2019-06-20 07:30 | 260.18 | 257.6
2019-06-20 08:00 | 256.81 | 254.26
2019-06-20 08:30 | 251.93 | 249.42
2019-06-20 09:00 | 246.96 | 244.01
2019-06-20 09:30 | 242.42 | 239.17
2019-06-20 10:00 | 239.27 | 235.44
2019-06-20 10:30 | 236.91 | 232.54
2019-06-20 11:00 | 236.34 | 231.62
2019-06-20 11:30 | 235.02 | 230.11
2019-06-20 12:00 | 233.71 | 228.88
2019-06-20 12:30 | 233.66 | 228.65
2019-06-20 13:00 | 233.38 | 228.18
2019-06-20 13:30 | 234.22 | 228.63
2019-06-20 14:00 | 235.39 | 229.55
2019-06-20 14:30 | 235.52 | 229.55
2019-06-20 15:00 | 235.79 | 229.57
2019-06-20 15:30 | 236.62 | 230.95
2019-06-20 16:00 | 237.77 | 232.54
2019-06-20 16:30 | 239.66 | 234.67
2019-06-20 17:00 | 243.45 | 238.46
2019-06-20 17:30 | 236.79 | 232.34
2019-06-20 18:00 | 217.46 | 213.68
2019-06-20 18:30 | 221.61 | 217.97
2019-06-20 19:00 | 222.42 | 218.97
2019-06-20 19:30 | 221.38 | 218.06
2019-06-20 20:00 | 220.38 | 217.17
2019-06-20 20:30 | 218.9 | 215.58
2019-06-20 21:00 | 247.7 | 244.29
2019-06-20 21:30 | 255.53 | 251.69
2019-06-20 22:00 | 252.81 | 248.97
2019-06-20 22:30 | 250.6 | 246.54
2019-06-20 23:00 | 248.27 | 244.17
2019-06-20 23:30 | 246.81 | 242.08
2019-06-21 | 246.26 | 239.9
2019-06-21 00:30 | 247.1 | 239.75
2019-06-21 01:00 | 245.99 | 238.53
2019-06-21 01:30 | 245.92 | 238.29
2019-06-21 02:00 | 245.81 | 237.68
2019-06-21 02:30 | 245.64 | 237.7
2019-06-21 03:00 | 245.53 | 237.62
2019-06-21 03:30 | 245.79 | 237.82
2019-06-21 04:00 | 246.16 | 238.23
2019-06-21 04:30 | 247.23 | 239.55
2019-06-21 05:00 | 248.64 | 241.1
2019-06-21 05:30 | 251.21 | 243.9
2019-06-21 06:00 | 254.46 | 247.74
2019-06-21 06:30 | 258.84 | 253.24
2019-06-21 07:00 | 263.01 | 258.8
2019-06-21 07:30 | 241.69 | 238.08
2019-06-21 08:00 | 218.94 | 216.87
2019-06-21 08:30 | 214.99 | 213.84
2019-06-21 09:00 | 240.6 | 238.68
2019-06-21 09:30 | 246.92 | 244.4
2019-06-21 10:00 | 242.64 | 240
2019-06-21 10:30 | 239.23 | 236.47
2019-06-21 11:00 | 238.22 | 235.5
2019-06-21 11:30 | 236.74 | 233.96
2019-06-21 12:00 | 235.2 | 232.42
2019-06-21 12:30 | 236.43 | 233.61
2019-06-21 13:00 | 236.19 | 233.31
2019-06-21 13:30 | 236.26 | 233.42
2019-06-21 14:00 | 236.54 | 233.72
2019-06-21 14:30 | 237.27 | 234.42
2019-06-21 15:00 | 237.16 | 234.31
2019-06-21 15:30 | 237.39 | 234.45
2019-06-21 16:00 | 239.16 | 236.07
2019-06-21 16:30 | 242.56 | 239.56
2019-06-21 17:00 | 245.93 | 242.88
2019-06-21 17:30 | 250.37 | 247.25
2019-06-21 18:00 | 256.66 | 253.79
2019-06-21 18:30 | 261.4 | 258.65
2019-06-21 19:00 | 262.03 | 259.25
2019-06-21 19:30 | 261.93 | 259.07
2019-06-21 20:00 | 260.44 | 258.02
2019-06-21 20:30 | 259.37 | 256.97
2019-06-21 21:00 | 257.68 | 255.25
2019-06-21 21:30 | 256.86 | 254.38
2019-06-21 22:00 | 254.24 | 251.61
2019-06-21 22:30 | 251.71 | 248.93
2019-06-21 23:00 | 249.34 | 246.47
2019-06-21 23:30 | 247.69 | 244.71
2019-06-22 | 246.2 | 243.2
2019-06-22 00:30 | 245.65 | 242.31
2019-06-22 01:00 | 243.64 | 239.91
2019-06-22 01:30 | 242.84 | 239.03
2019-06-22 02:00 | 242.53 | 238.63
2019-06-22 02:30 | 241.77 | 237.86
2019-06-22 03:00 | 242.58 | 238.73
2019-06-22 03:30 | 242.86 | 239.2
2019-06-22 04:00 | 243.66 | 240.25
2019-06-22 04:30 | 244.69 | 241.3
2019-06-22 05:00 | 245.38 | 242.03
2019-06-22 05:30 | 246.5 | 243.5
2019-06-22 06:00 | 248.92 | 246.08
2019-06-22 06:30 | 251.45 | 248.79
2019-06-22 07:00 | 253.38 | 250.81
2019-06-22 07:30 | 254.46 | 251.64
2019-06-22 08:00 | 255.8 | 252.44
2019-06-22 08:30 | 254.24 | 251.52
2019-06-22 09:00 | 252.03 | 249.29
2019-06-22 09:30 | 248.46 | 245.83
2019-06-22 10:00 | 243.85 | 241.12
2019-06-22 10:30 | 239.87 | 237.1
2019-06-22 11:00 | 203.73 | 199.69
2019-06-22 11:30 | 173.99 | 168.67
2019-06-22 12:00 | 171.89 | 166.24
2019-06-22 12:30 | 171.54 | 165.24
2019-06-22 13:00 | 170.63 | 164.16
2019-06-22 13:30 | 170.05 | 163.64
2019-06-22 14:00 | 169.09 | 162.44
2019-06-22 14:30 | 169.7 | 162.82
2019-06-22 15:00 | 204.9 | 200.21
2019-06-22 15:30 | 233.7 | 230.29
2019-06-22 16:00 | 235.73 | 232.46
2019-06-22 16:30 | 238.37 | 235.45
2019-06-22 17:00 | 242.54 | 239.67
2019-06-22 17:30 | 246.78 | 244.18
2019-06-22 18:00 | 252.68 | 250.35
2019-06-22 18:30 | 257.01 | 254.78
2019-06-22 19:00 | 257.57 | 255.25
2019-06-22 19:30 | 256.51 | 254.09
2019-06-22 20:00 | 255.71 | 253.33
2019-06-22 20:30 | 254.71 | 252.29
2019-06-22 21:00 | 253.8 | 251.3
2019-06-22 21:30 | 252.95 | 250.46
2019-06-22 22:00 | 250.13 | 247.65
2019-06-22 22:30 | 249.56 | 246.98
2019-06-22 23:00 | 248.23 | 245.48
2019-06-22 23:30 | 246.43 | 243.69
2019-06-23 | 244.99 | 242.16
2019-06-23 00:30 | 244.57 | 241.56
2019-06-23 01:00 | 243.43 | 240.42
2019-06-23 01:30 | 243.67 | 240.61
2019-06-23 02:00 | 243.16 | 240.08
2019-06-23 02:30 | 242.93 | 239.82
2019-06-23 03:00 | 242.9 | 239.81
2019-06-23 03:30 | 243.36 | 240.21
2019-06-23 04:00 | 243.77 | 240.65
2019-06-23 04:30 | 244.28 | 241.26
2019-06-23 05:00 | 245.21 | 242.22
2019-06-23 05:30 | 246.63 | 243.66
2019-06-23 06:00 | 247.09 | 244.09
2019-06-23 06:30 | 249.39 | 246.27
2019-06-23 07:00 | 252.64 | 249.69
2019-06-23 07:30 | 253.59 | 250.5
2019-06-23 08:00 | 254.49 | 251.75
2019-06-23 08:30 | 253.15 | 250.57
2019-06-23 09:00 | 249.17 | 246.57
2019-06-23 09:30 | 245.32 | 242.59
2019-06-23 10:00 | 240.99 | 238.32
2019-06-23 10:30 | 237.89 | 234.97
2019-06-23 11:00 | 234.42 | 231.44
2019-06-23 11:30 | 231.66 | 228.66
2019-06-23 12:00 | 229.52 | 226.44
2019-06-23 12:30 | 230.81 | 227.27
2019-06-23 13:00 | 231.19 | 227.72
2019-06-23 13:30 | 230.81 | 227.57
2019-06-23 14:00 | 230.29 | 226.78
2019-06-23 14:30 | 230.64 | 227.25
2019-06-23 15:00 | 231.61 | 227.95
2019-06-23 15:30 | 234.18 | 230.57
2019-06-23 16:00 | 236.19 | 232.58
2019-06-23 16:30 | 238.7 | 235.73
2019-06-23 17:00 | 241.97 | 239.17
2019-06-23 17:30 | 246.88 | 244.21
2019-06-23 18:00 | 251.28 | 248.77
2019-06-23 18:30 | 256.35 | 253.99
2019-06-23 19:00 | 257.16 | 254.81
2019-06-23 19:30 | 256.77 | 254.4
2019-06-23 20:00 | 255.38 | 252.97
2019-06-23 20:30 | 253.58 | 251.08
2019-06-23 21:00 | 251.9 | 249.32
2019-06-23 21:30 | 250.73 | 248.02
2019-06-23 22:00 | 248.88 | 245.93
2019-06-23 22:30 | 240.64 | 237.56
2019-06-23 23:00 | 226 | 222.78
2019-06-23 23:30 | 224.36 | 221.17
2019-06-24 | 223.29 | 220
2019-06-24 00:30 | 222.69 | 219.15
2019-06-24 01:00 | 222.65 | 218.7
2019-06-24 01:30 | 223.23 | 217.41
2019-06-24 02:00 | 222.64 | 216.75
2019-06-24 02:30 | 222.78 | 216.92
2019-06-24 03:00 | 222.66 | 216.97
2019-06-24 03:30 | 223.02 | 217.36
2019-06-24 04:00 | 223.12 | 217.6
2019-06-24 04:30 | 224.26 | 218.79
2019-06-24 05:00 | 226.29 | 220.75
2019-06-24 05:30 | 228.61 | 223.32
2019-06-24 06:00 | 231.42 | 227.27
2019-06-24 06:30 | 236.87 | 233.15
2019-06-24 07:00 | 241.77 | 238.99
2019-06-24 07:30 | 243.34 | 241.18
2019-06-24 08:00 | 242.13 | 239.97
2019-06-24 08:30 | 238.15 | 235.88
2019-06-24 09:00 | 233.67 | 231.12
2019-06-24 09:30 | 227.41 | 224.59
2019-06-24 10:00 | 223.27 | 220.32
2019-06-24 10:30 | 219.71 | 216.57
2019-06-24 11:00 | 230.87 | 227.77
2019-06-24 11:30 | 234.5 | 231.22
2019-06-24 12:00 | 233.64 | 230.36
2019-06-24 12:30 | 233.05 | 229.79
2019-06-24 13:00 | 231.67 | 228.7
2019-06-24 13:30 | 232.13 | 228.68
2019-06-24 14:00 | 232.91 | 229.05
2019-06-24 14:30 | 233.54 | 229.85
2019-06-24 15:00 | 234.93 | 231.11
2019-06-24 15:30 | 236.5 | 232.45
2019-06-24 16:00 | 238.02 | 233.95
2019-06-24 16:30 | 241.01 | 236.71
2019-06-24 17:00 | 234.13 | 230.67
2019-06-24 17:30 | 220.84 | 217.84
2019-06-24 18:00 | 217.18 | 214.18
2019-06-24 18:30 | 221.51 | 218.15
2019-06-24 19:00 | 223.35 | 219.91
2019-06-24 19:30 | 254.65 | 251.08
2019-06-24 20:00 | 260.23 | 256.63
2019-06-24 20:30 | 259.95 | 256.2
2019-06-24 21:00 | 256.3 | 253.42
2019-06-24 21:30 | 254.33 | 251.59
2019-06-24 22:00 | 252.09 | 249.24
2019-06-24 22:30 | 250.13 | 246.45
2019-06-24 23:00 | 248.25 | 244.03
2019-06-24 23:30 | 245.48 | 242.15
2019-06-25 | 243.34 | 240.24
2019-06-25 00:30 | 242.7 | 239.42
2019-06-25 01:00 | 241.9 | 238.12
2019-06-25 01:30 | 241.24 | 237.74
2019-06-25 02:00 | 239.83 | 236.5
2019-06-25 02:30 | 239.79 | 236.54
2019-06-25 03:00 | 239.26 | 236.02
2019-06-25 03:30 | 239.74 | 236.56
2019-06-25 04:00 | 239.93 | 236.76
2019-06-25 04:30 | 241.19 | 238.1
2019-06-25 05:00 | 242.89 | 239.86
2019-06-25 05:30 | 245.88 | 242.99
2019-06-25 06:00 | 248.74 | 246.05
2019-06-25 06:30 | 253.07 | 250.5
2019-06-25 07:00 | 235.15 | 232.7
2019-06-25 07:30 | 217.49 | 215.2
2019-06-25 08:00 | 218.79 | 216.31
2019-06-25 08:30 | 217.21 | 214.89
2019-06-25 09:00 | 243.66 | 240.96
2019-06-25 09:30 | 246.91 | 244.11
2019-06-25 10:00 | 243.14 | 240.39
2019-06-25 10:30 | 241.58 | 238.74
2019-06-25 11:00 | 239.15 | 236.22
2019-06-25 11:30 | 237.22 | 234.19
2019-06-25 12:00 | 235.48 | 232.53
2019-06-25 12:30 | 234.79 | 231.84
2019-06-25 13:00 | 234.18 | 231.29
2019-06-25 13:30 | 234.09 | 231.18
2019-06-25 14:00 | 234.43 | 231.46
2019-06-25 14:30 | 234.96 | 232.1
2019-06-25 15:00 | 233.92 | 231.07
2019-06-25 15:30 | 235.75 | 232.98
2019-06-25 16:00 | 236.81 | 233.9
2019-06-25 16:30 | 238.51 | 235.57
2019-06-25 17:00 | 241.32 | 238.31
2019-06-25 17:30 | 231.35 | 228.52
2019-06-25 18:00 | 217.04 | 214.4
2019-06-25 18:30 | 218.05 | 215.32
2019-06-25 19:00 | 219.29 | 216.53
2019-06-25 19:30 | 218.39 | 215.64
2019-06-25 20:00 | 247.16 | 243.68
2019-06-25 20:30 | 253.51 | 249.67
2019-06-25 21:00 | 251.94 | 247.93
2019-06-25 21:30 | 249.78 | 246.56
2019-06-25 22:00 | 247.3 | 244.31
2019-06-25 22:30 | 245.12 | 242
2019-06-25 23:00 | 242.04 | 238.89
2019-06-25 23:30 | 241.21 | 237.66
2019-06-26 | 239.33 | 235.59
2019-06-26 00:30 | 238.4 | 235.28
2019-06-26 01:00 | 236.71 | 233.35
2019-06-26 01:30 | 236.88 | 233.06
2019-06-26 02:00 | 236.36 | 232.06
2019-06-26 02:30 | 236.98 | 232.67
2019-06-26 03:00 | 236.21 | 232.29
2019-06-26 03:30 | 236.07 | 232.53
2019-06-26 04:00 | 236.14 | 232.72
2019-06-26 04:30 | 237.29 | 233.94
2019-06-26 05:00 | 237.97 | 234.72
2019-06-26 05:30 | 240.03 | 236.72
2019-06-26 06:00 | 242.7 | 239.31
2019-06-26 06:30 | 245.92 | 242.68
2019-06-26 07:00 | 250.35 | 246.71
2019-06-26 07:30 | 250.91 | 247.16
2019-06-26 08:00 | 249.52 | 246.82
2019-06-26 08:30 | 245.74 | 243.03
2019-06-26 09:00 | 243.63 | 240.75
2019-06-26 09:30 | 240.5 | 237.45
2019-06-26 10:00 | 237.28 | 234.31
2019-06-26 10:30 | 235.5 | 232.42
2019-06-26 11:00 | 233.54 | 230.5
2019-06-26 11:30 | 232.78 | 229.58
2019-06-26 12:00 | 231.59 | 228.29
2019-06-26 12:30 | 231.94 | 228.55
2019-06-26 13:00 | 231.35 | 228
2019-06-26 13:30 | 230.84 | 227.23
2019-06-26 14:00 | 230.98 | 227.43
2019-06-26 14:30 | 231.08 | 227.57
2019-06-26 15:00 | 232.99 | 229.29
2019-06-26 15:30 | 235.59 | 231.83
2019-06-26 16:00 | 236.31 | 232.56
2019-06-26 16:30 | 237.95 | 234.11
2019-06-26 17:00 | 239.98 | 236.39
2019-06-26 17:30 | 229.77 | 226.9
2019-06-26 18:00 | 218.28 | 215.98
2019-06-26 18:30 | 215.74 | 213.3
2019-06-26 19:00 | 215.69 | 213.22
2019-06-26 19:30 | 223 | 220.2
2019-06-26 20:00 | 249.93 | 246.16
2019-06-26 20:30 | 248.39 | 244.75
2019-06-26 21:00 | 246.62 | 243.17
2019-06-26 21:30 | 245.63 | 242.58
2019-06-26 22:00 | 242.9 | 239.76
2019-06-26 22:30 | 241.31 | 238.11
2019-06-26 23:00 | 238.48 | 235.26
2019-06-26 23:30 | 237.71 | 234.48
2019-06-27 | 236.17 | 232.75
2019-06-27 00:30 | 235.96 | 232.4
2019-06-27 01:00 | 234.82 | 231.29
2019-06-27 01:30 | 233.97 | 230.66
2019-06-27 02:00 | 233.91 | 230.07
2019-06-27 02:30 | 233.68 | 229.89
2019-06-27 03:00 | 233.8 | 230.22
2019-06-27 03:30 | 234.02 | 230.46
2019-06-27 04:00 | 234.16 | 230.68
2019-06-27 04:30 | 234.73 | 231.29
2019-06-27 05:00 | 236.36 | 233.2
2019-06-27 05:30 | 238.01 | 234.66
2019-06-27 06:00 | 240.97 | 236.72
2019-06-27 06:30 | 244.62 | 241.11
2019-06-27 07:00 | 248.64 | 244.92
2019-06-27 07:30 | 249.52 | 245.99
2019-06-27 08:00 | 248.24 | 244.46
2019-06-27 08:30 | 245.3 | 241.05
2019-06-27 09:00 | 243.23 | 237.09
2019-06-27 09:30 | 240.99 | 233.3
2019-06-27 10:00 | 237.94 | 229.85
2019-06-27 10:30 | 237.28 | 226.75
2019-06-27 11:00 | 240.01 | 224.5
2019-06-27 11:30 | 234.7 | 226.59
2019-06-27 12:00 | 234.78 | 226.7
2019-06-27 12:30 | 234.49 | 227.29
2019-06-27 13:00 | 232.38 | 226.59
2019-06-27 13:30 | 233.16 | 227.37
2019-06-27 14:00 | 233.15 | 227.57
2019-06-27 14:30 | 233.76 | 228.42
2019-06-27 15:00 | 233.52 | 228.51
2019-06-27 15:30 | 234.59 | 229.9
2019-06-27 16:00 | 235.45 | 230.7
2019-06-27 16:30 | 235.67 | 231.12
2019-06-27 17:00 | 237.16 | 233.25
2019-06-27 17:30 | 239.46 | 235.47
2019-06-27 18:00 | 243.16 | 239.33
2019-06-27 18:30 | 247.09 | 243.47
2019-06-27 19:00 | 247.86 | 244.28
2019-06-27 19:30 | 247.62 | 244.06
2019-06-27 20:00 | 245.91 | 242.27
2019-06-27 20:30 | 245.53 | 241.88
2019-06-27 21:00 | 244.61 | 240.94
2019-06-27 21:30 | 243.91 | 239.6
2019-06-27 22:00 | 243.74 | 238.72
2019-06-27 22:30 | 242.49 | 236.69
2019-06-27 23:00 | 240.77 | 234.26
2019-06-27 23:30 | 239.84 | 233.43
2019-06-28 | 238.37 | 231.78
2019-06-28 00:30 | 237.37 | 230.78
2019-06-28 01:00 | 236.99 | 229.74
2019-06-28 01:30 | 238.5 | 229.28
2019-06-28 02:00 | 237.05 | 228.91
2019-06-28 02:30 | 234.91 | 228.1
2019-06-28 03:00 | 235.57 | 228.71
2019-06-28 03:30 | 235.45 | 228.63
2019-06-28 04:00 | 234.9 | 228.1
2019-06-28 04:30 | 236.34 | 229.54
2019-06-28 05:00 | 237.43 | 230.84
2019-06-28 05:30 | 237.85 | 232.3
2019-06-28 06:00 | 240.37 | 234.96
2019-06-28 06:30 | 243.62 | 238.44
2019-06-28 07:00 | 247.21 | 242.28
2019-06-28 07:30 | 247.04 | 242.58
2019-06-28 08:00 | 246.54 | 242.23
2019-06-28 08:30 | 244.05 | 239.63
2019-06-28 09:00 | 242.21 | 237.54
2019-06-28 09:30 | 239.32 | 234.39
2019-06-28 10:00 | 237.04 | 232.42
2019-06-28 10:30 | 218.87 | 213.24
2019-06-28 11:00 | 212.87 | 206.89
2019-06-28 11:30 | 209.24 | 205.37
2019-06-28 12:00 | 210.14 | 206.59
2019-06-28 12:30 | 210.6 | 206.79
2019-06-28 13:00 | 208.97 | 205.33
2019-06-28 13:30 | 208.65 | 205.05
2019-06-28 14:00 | 208.62 | 205.05
2019-06-28 14:30 | 209.38 | 205.88
2019-06-28 15:00 | 222.48 | 219.26
2019-06-28 15:30 | 230.65 | 227.53
2019-06-28 16:00 | 231.07 | 228.03
2019-06-28 16:30 | 233.07 | 230.07
2019-06-28 17:00 | 234.99 | 232.09
2019-06-28 17:30 | 237.56 | 234.69
2019-06-28 18:00 | 240.56 | 237.71
2019-06-28 18:30 | 244.24 | 241.41
2019-06-28 19:00 | 244.65 | 241.85
2019-06-28 19:30 | 244.15 | 241.34
2019-06-28 20:00 | 242.88 | 240.15
2019-06-28 20:30 | 242.81 | 240.04
2019-06-28 21:00 | 241.19 | 238.36
2019-06-28 21:30 | 240.89 | 238.03
2019-06-28 22:00 | 239.71 | 236.74
2019-06-28 22:30 | 238.63 | 235.56
2019-06-28 23:00 | 236.77 | 233.66
2019-06-28 23:30 | 236.13 | 232.97
2019-06-29 | 234.52 | 231.21
2019-06-29 00:30 | 234.79 | 231.49
2019-06-29 01:00 | 234.47 | 231.26
2019-06-29 01:30 | 215.98 | 211.41
2019-06-29 02:00 | 182.04 | 173.54
2019-06-29 02:30 | 171.73 | 162.39
2019-06-29 03:00 | 172.29 | 162.98
2019-06-29 03:30 | 171.77 | 162.45
2019-06-29 04:00 | 172.27 | 163.1
2019-06-29 04:30 | 172.3 | 163.23
2019-06-29 05:00 | 173.54 | 164.54
2019-06-29 05:30 | 173.79 | 164.63
2019-06-29 06:00 | 175.55 | 166.2
2019-06-29 06:30 | 177.37 | 168.1
2019-06-29 07:00 | 178.58 | 169.3
2019-06-29 07:30 | 179.57 | 170.69
2019-06-29 08:00 | 178.17 | 169.56
2019-06-29 08:30 | 177.3 | 168.27
2019-06-29 09:00 | 174.04 | 165.64
2019-06-29 09:30 | 171.96 | 164.53
2019-06-29 10:00 | 170.86 | 163.2
2019-06-29 10:30 | 168.81 | 160.76
2019-06-29 11:00 | 167.66 | 159.41
2019-06-29 11:30 | 165.87 | 157.73
2019-06-29 12:00 | 165.1 | 157.17
2019-06-29 12:30 | 167.75 | 156.27
2019-06-29 13:00 | 171.05 | 156.54
2019-06-29 13:30 | 170.32 | 156.1
2019-06-29 14:00 | 170.52 | 156.49
2019-06-29 14:30 | 169.57 | 155.87
2019-06-29 15:00 | 169.76 | 156.57
2019-06-29 15:30 | 200.58 | 190.77
2019-06-29 16:00 | 227.53 | 220.17
2019-06-29 16:30 | 235.1 | 228.49
2019-06-29 17:00 | 236.94 | 230.91
2019-06-29 17:30 | 238.9 | 233.64
2019-06-29 18:00 | 241.92 | 237.39
2019-06-29 18:30 | 243.74 | 239.44
2019-06-29 19:00 | 243.82 | 239.53
2019-06-29 19:30 | 242.69 | 238.52
2019-06-29 20:00 | 242.29 | 238.12
2019-06-29 20:30 | 241.29 | 236.97
2019-06-29 21:00 | 241.41 | 236.26
2019-06-29 21:30 | 241.22 | 235.67
2019-06-29 22:00 | 240.7 | 234.73
2019-06-29 22:30 | 240.69 | 233.67
2019-06-29 23:00 | 239.09 | 231.74
2019-06-29 23:30 | 238.08 | 230.75
2019-06-30 | 236.65 | 229.44
2019-06-30 00:30 | 236.38 | 229.05
2019-06-30 01:00 | 235.94 | 228.48
2019-06-30 01:30 | 218.87 | 209.9
2019-06-30 02:00 | 184.15 | 171.15
2019-06-30 02:30 | 176.56 | 161.12
2019-06-30 03:00 | 175.43 | 160.01
2019-06-30 03:30 | 176.08 | 160.68
2019-06-30 04:00 | 175.97 | 160.75
2019-06-30 04:30 | 175.99 | 160.68
2019-06-30 05:00 | 177.23 | 161.69
2019-06-30 05:30 | 177.75 | 162.58
2019-06-30 06:00 | 178.59 | 163.48
2019-06-30 06:30 | 180.03 | 164.92
2019-06-30 07:00 | 182.31 | 167.38
2019-06-30 07:30 | 183.56 | 168.73
2019-06-30 08:00 | 183.63 | 168.59
2019-06-30 08:30 | 183.43 | 167.87
2019-06-30 09:00 | 182.73 | 166.4
2019-06-30 09:30 | 181.1 | 164.06
2019-06-30 10:00 | 180.27 | 162.2
2019-06-30 10:30 | 178.32 | 160.1
2019-06-30 11:00 | 176.11 | 158.42
2019-06-30 11:30 | 175.37 | 157.5
2019-06-30 12:00 | 172.51 | 156.51
2019-06-30 12:30 | 174.88 | 157.57
2019-06-30 13:00 | 174.58 | 156.22
2019-06-30 13:30 | 175.57 | 156.93
2019-06-30 14:00 | 175.57 | 157.13
2019-06-30 14:30 | 175.69 | 157.51
2019-06-30 15:00 | 177.15 | 158.45
2019-06-30 15:30 | 206.42 | 192.39
2019-06-30 16:00 | 232.53 | 222.19
2019-06-30 16:30 | 237.56 | 228.68
2019-06-30 17:00 | 237.2 | 229.49
2019-06-30 17:30 | 207.95 | 198.18
2019-06-30 18:00 | 210.42 | 201.75
2019-06-30 18:30 | 212.85 | 204.72
2019-06-30 19:00 | 213.69 | 205.55
2019-06-30 19:30 | 212.44 | 204.18
2019-06-30 20:00 | 212 | 203.55
2019-06-30 20:30 | 211.65 | 203.17
2019-06-30 21:00 | 209.51 | 201.09
2019-06-30 21:30 | 209 | 200.15
2019-06-30 22:00 | 207.97 | 198.09
2019-06-30 22:30 | 206.36 | 196.28
2019-06-30 23:00 | 206.38 | 195.35
2019-06-30 23:30 | 206.99 | 195.56
2019-07-01 | 206.37 | 193.83
2019-07-01 00:30 | 205.5 | 193.22
2019-07-01 01:00 | 205.15 | 192.95
2019-07-01 01:30 | 204.77 | 192.57
2019-07-01 02:00 | 204.29 | 191.83
2019-07-01 02:30 | 203.82 | 191.4
2019-07-01 03:00 | 204.31 | 191.79
2019-07-01 03:30 | 204.58 | 192.24
2019-07-01 04:00 | 204.75 | 192.82
2019-07-01 04:30 | 204.34 | 192.38
2019-07-01 05:00 | 207.03 | 195.14
2019-07-01 05:30 | 208.25 | 196.56
2019-07-01 06:00 | 209.91 | 198.75
2019-07-01 06:30 | 213.43 | 204.63
2019-07-01 07:00 | 216.14 | 209.04
2019-07-01 07:30 | 219.26 | 212.1
2019-07-01 08:00 | 221.1 | 213.52
2019-07-01 08:30 | 219.35 | 210.98
2019-07-01 09:00 | 215.5 | 207.31
2019-07-01 09:30 | 211.47 | 203.62
2019-07-01 10:00 | 209.04 | 201.26
2019-07-01 10:30 | 205.76 | 197.71
2019-07-01 11:00 | 204.22 | 195.93
2019-07-01 11:30 | 203.53 | 195.5
2019-07-01 12:00 | 202.35 | 194.29
2019-07-01 12:30 | 202.16 | 193.93
2019-07-01 13:00 | 201.01 | 192.87
2019-07-01 13:30 | 201.4 | 193.15
2019-07-01 14:00 | 201.88 | 193.63
2019-07-01 14:30 | 202.78 | 194.73
2019-07-01 15:00 | 204.28 | 196.44
2019-07-01 15:30 | 205.14 | 197.34
2019-07-01 16:00 | 206.32 | 198.9
2019-07-01 16:30 | 207.57 | 200.16
2019-07-01 17:00 | 209.06 | 202.02
2019-07-01 17:30 | 210.11 | 204.26
2019-07-01 18:00 | 213.82 | 208.67
2019-07-01 18:30 | 218.35 | 213.7
2019-07-01 19:00 | 219.37 | 214.82
2019-07-01 19:30 | 217.33 | 212.73
2019-07-01 20:00 | 217.04 | 212.41
2019-07-01 20:30 | 215.92 | 211.48
2019-07-01 21:00 | 213.29 | 208.57
2019-07-01 21:30 | 213.3 | 207.83
2019-07-01 22:00 | 212.41 | 206.1
2019-07-01 22:30 | 210.16 | 202.66
2019-07-01 23:00 | 209.7 | 202.1
2019-07-01 23:30 | 208.46 | 200.7
2019-07-02 | 207.04 | 198.03
2019-07-02 00:30 | 209.15 | 198.02
2019-07-02 01:00 | 208.35 | 197.34
2019-07-02 01:30 | 208.53 | 197.5
2019-07-02 02:00 | 207.99 | 196.58
2019-07-02 02:30 | 209.93 | 197.35
2019-07-02 03:00 | 209.39 | 196.82
2019-07-02 03:30 | 208.78 | 196.26
2019-07-02 04:00 | 209.88 | 197.37
2019-07-02 04:30 | 210.13 | 197.66
2019-07-02 05:00 | 211.41 | 199.09
2019-07-02 05:30 | 212.82 | 200.5
2019-07-02 06:00 | 214.72 | 203.36
2019-07-02 06:30 | 216.11 | 207.68
2019-07-02 07:00 | 218.81 | 210.76
2019-07-02 07:30 | 218.73 | 212.66
2019-07-02 08:00 | 218.81 | 213.34
2019-07-02 08:30 | 216.09 | 210.47
2019-07-02 09:00 | 212.68 | 206.94
2019-07-02 09:30 | 210 | 204.34
2019-07-02 10:00 | 206.61 | 200.89
2019-07-02 10:30 | 204.16 | 198.32
2019-07-02 11:00 | 202.43 | 195.52
2019-07-02 11:30 | 200.78 | 193.93
2019-07-02 12:00 | 201.63 | 194.64
2019-07-02 12:30 | 219.66 | 213.56
2019-07-02 13:00 | 223.3 | 217.58
2019-07-02 13:30 | 231.95 | 226.64
2019-07-02 14:00 | 234.87 | 229.63
2019-07-02 14:30 | 235.44 | 230.24
2019-07-02 15:00 | 234.86 | 229.5
2019-07-02 15:30 | 235.54 | 230.46
2019-07-02 16:00 | 235.05 | 230.98
2019-07-02 16:30 | 236.02 | 232.44
2019-07-02 17:00 | 237.51 | 234
2019-07-02 17:30 | 240.22 | 236.71
2019-07-02 18:00 | 243.43 | 240.33
2019-07-02 18:30 | 246.62 | 243.97
2019-07-02 19:00 | 247.86 | 245.22
2019-07-02 19:30 | 246.85 | 244.22
2019-07-02 20:00 | 245.48 | 242.66
2019-07-02 20:30 | 245.32 | 242.53
2019-07-02 21:00 | 243.48 | 240.49
2019-07-02 21:30 | 243.4 | 239.81
2019-07-02 22:00 | 242.11 | 238.31
2019-07-02 22:30 | 239.88 | 235.98
2019-07-02 23:00 | 238.69 | 234.77
2019-07-02 23:30 | 237.34 | 233.16
2019-07-03 | 237.19 | 231.64
2019-07-03 00:30 | 237.51 | 231.27
2019-07-03 01:00 | 236.66 | 230.15
2019-07-03 01:30 | 236.12 | 229.76
2019-07-03 02:00 | 236.27 | 229.73
2019-07-03 02:30 | 235.84 | 229.23
2019-07-03 03:00 | 235.64 | 229.07
2019-07-03 03:30 | 236.29 | 229.78
2019-07-03 04:00 | 236.83 | 230.44
2019-07-03 04:30 | 237.4 | 231.15
2019-07-03 05:00 | 239.7 | 233.46
2019-07-03 05:30 | 241.78 | 235.51
2019-07-03 06:00 | 243.92 | 238.13
2019-07-03 06:30 | 245.59 | 241.41
2019-07-03 07:00 | 248.73 | 245.18
2019-07-03 07:30 | 251.32 | 248.05
2019-07-03 08:00 | 251.39 | 248
2019-07-03 08:30 | 249.97 | 246.49
2019-07-03 09:00 | 246.21 | 242.75
2019-07-03 09:30 | 244.57 | 240.68
2019-07-03 10:00 | 240.41 | 236.28
2019-07-03 10:30 | 237.75 | 233.16
2019-07-03 11:00 | 236.88 | 232.6
2019-07-03 11:30 | 233.97 | 229.89
2019-07-03 12:00 | 232.34 | 228.18
2019-07-03 12:30 | 231.82 | 227.65
2019-07-03 13:00 | 231.04 | 226.86
2019-07-03 13:30 | 231.92 | 227.64
2019-07-03 14:00 | 232.74 | 228.62
2019-07-03 14:30 | 233.06 | 228.92
2019-07-03 15:00 | 233.76 | 229.67
2019-07-03 15:30 | 233.69 | 229.65
2019-07-03 16:00 | 236.22 | 232.29
2019-07-03 16:30 | 237.23 | 233.29
2019-07-03 17:00 | 239.15 | 235.28
2019-07-03 17:30 | 241.22 | 237.57
2019-07-03 18:00 | 245.32 | 242.01
2019-07-03 18:30 | 249.37 | 246.44
2019-07-03 19:00 | 250.54 | 247.68
2019-07-03 19:30 | 250.4 | 247.48
2019-07-03 20:00 | 248.81 | 245.85
2019-07-03 20:30 | 247.56 | 244.52
2019-07-03 21:00 | 246.44 | 243.28
2019-07-03 21:30 | 245.93 | 242.08
2019-07-03 22:00 | 244.87 | 240.3
2019-07-03 22:30 | 242.11 | 237.39
2019-07-03 23:00 | 241.02 | 236.25
2019-07-03 23:30 | 241.21 | 235.24
2019-07-04 | 239.67 | 232.92
2019-07-04 00:30 | 240.18 | 232.42
2019-07-04 01:00 | 239.59 | 231.39
2019-07-04 01:30 | 239.31 | 230.3
2019-07-04 02:00 | 239.19 | 229.67
2019-07-04 02:30 | 240.25 | 229.74
2019-07-04 03:00 | 239.66 | 229.16
2019-07-04 03:30 | 239.68 | 229.23
2019-07-04 04:00 | 240.17 | 229.84
2019-07-04 04:30 | 239.72 | 229.5
2019-07-04 05:00 | 240.44 | 230.46
2019-07-04 05:30 | 241.43 | 231.63
2019-07-04 06:00 | 241.9 | 233.07
2019-07-04 06:30 | 242.61 | 236.3
2019-07-04 07:00 | 243.41 | 239.42
2019-07-04 07:30 | 244.56 | 240.89
2019-07-04 08:00 | 245.96 | 241.92
2019-07-04 08:30 | 243.85 | 239.61
2019-07-04 09:00 | 241.41 | 237.25
2019-07-04 09:30 | 239.53 | 235.04
2019-07-04 10:00 | 236.26 | 231.96
2019-07-04 10:30 | 235.6 | 231.31
2019-07-04 11:00 | 234.17 | 229.81
2019-07-04 11:30 | 232.49 | 228.02
2019-07-04 12:00 | 231.73 | 227.46
2019-07-04 12:30 | 231.55 | 227.28
2019-07-04 13:00 | 231.63 | 227.19
2019-07-04 13:30 | 231.97 | 227.62
2019-07-04 14:00 | 233.33 | 229.28
2019-07-04 14:30 | 233.95 | 229.75
2019-07-04 15:00 | 235.18 | 231.13
2019-07-04 15:30 | 235.67 | 231.82
2019-07-04 16:00 | 236.92 | 233.02
2019-07-04 16:30 | 238.06 | 234.08
2019-07-04 17:00 | 239.35 | 235.76
2019-07-04 17:30 | 241 | 237.28
2019-07-04 18:00 | 244.03 | 240.49
2019-07-04 18:30 | 247.69 | 244.66
2019-07-04 19:00 | 248.58 | 245.59
2019-07-04 19:30 | 247.99 | 245.03
2019-07-04 20:00 | 246.9 | 243.82
2019-07-04 20:30 | 245.75 | 242.59
2019-07-04 21:00 | 244.8 | 241.56
2019-07-04 21:30 | 244.94 | 241.1
2019-07-04 22:00 | 243.47 | 239.76
2019-07-04 22:30 | 241.7 | 237.52
2019-07-04 23:00 | 240.19 | 236.1
2019-07-04 23:30 | 240.2 | 234.43
2019-07-05 | 240.02 | 233.2
2019-07-05 00:30 | 239.25 | 231.81
2019-07-05 01:00 | 238.82 | 231.19
2019-07-05 01:30 | 238.06 | 230.56
2019-07-05 02:00 | 237.35 | 229.9
2019-07-05 02:30 | 237.64 | 230.21
2019-07-05 03:00 | 237.42 | 230.04
2019-07-05 03:30 | 237.25 | 229.91
2019-07-05 04:00 | 237.28 | 229.93
2019-07-05 04:30 | 237.82 | 230.53
2019-07-05 05:00 | 239.01 | 231.77
2019-07-05 05:30 | 225.39 | 217.07
2019-07-05 06:00 | 222.58 | 214.68
2019-07-05 06:30 | 224.52 | 217.19
2019-07-05 07:00 | 228.75 | 221.75
2019-07-05 07:30 | 229.18 | 222.68
2019-07-05 08:00 | 229.91 | 223.59
2019-07-05 08:30 | 240.93 | 235.22
2019-07-05 09:00 | 244.64 | 239.49
2019-07-05 09:30 | 242.36 | 237.29
2019-07-05 10:00 | 240.23 | 235.06
2019-07-05 10:30 | 237.1 | 231.67
2019-07-05 11:00 | 236.35 | 230.82
2019-07-05 11:30 | 235.31 | 229.91
2019-07-05 12:00 | 234.75 | 228.96
2019-07-05 12:30 | 233.74 | 227.93
2019-07-05 13:00 | 235.15 | 229.48
2019-07-05 13:30 | 236.07 | 230.54
2019-07-05 14:00 | 235.95 | 230.48
2019-07-05 14:30 | 236.36 | 230.91
2019-07-05 15:00 | 237.37 | 231.97
2019-07-05 15:30 | 237.43 | 232.12
2019-07-05 16:00 | 238.25 | 232.88
2019-07-05 16:30 | 239.61 | 234.09
2019-07-05 17:00 | 241.73 | 236.19
2019-07-05 17:30 | 243.25 | 237.73
2019-07-05 18:00 | 246.19 | 241.02
2019-07-05 18:30 | 250.07 | 245.3
2019-07-05 19:00 | 250.28 | 245.48
2019-07-05 19:30 | 249.76 | 245.17
2019-07-05 20:00 | 248.84 | 243.95
2019-07-05 20:30 | 247.84 | 242.76
2019-07-05 21:00 | 247.72 | 242.23
2019-07-05 21:30 | 247.32 | 241.06
2019-07-05 22:00 | 246.4 | 240.29
2019-07-05 22:30 | 245.22 | 238.89
2019-07-05 23:00 | 244.8 | 237.34
2019-07-05 23:30 | 245.03 | 236.3
2019-07-06 | 243.6 | 234.69
2019-07-06 00:30 | 243.31 | 234.04
2019-07-06 01:00 | 240.5 | 233.05
2019-07-06 01:30 | 239.26 | 231.57
2019-07-06 02:00 | 239.53 | 231.47
2019-07-06 02:30 | 238.74 | 230.66
2019-07-06 03:00 | 239.04 | 230.97
2019-07-06 03:30 | 238.36 | 230.31
2019-07-06 04:00 | 238.8 | 230.73
2019-07-06 04:30 | 238.9 | 230.88
2019-07-06 05:00 | 239.64 | 231.66
2019-07-06 05:30 | 239.86 | 232.22
2019-07-06 06:00 | 239.71 | 233.07
2019-07-06 06:30 | 241.03 | 235.12
2019-07-06 07:00 | 243.12 | 237.33
2019-07-06 07:30 | 242.52 | 236.71
2019-07-06 08:00 | 243.41 | 237.5
2019-07-06 08:30 | 243.81 | 238.07
2019-07-06 09:00 | 242.01 | 237.51
2019-07-06 09:30 | 240.59 | 236.45
2019-07-06 10:00 | 240.12 | 235.87
2019-07-06 10:30 | 236.56 | 232.41
2019-07-06 11:00 | 235.31 | 231.17
2019-07-06 11:30 | 235.56 | 231.47
2019-07-06 12:00 | 234.46 | 230.4
2019-07-06 12:30 | 233.86 | 229.69
2019-07-06 13:00 | 232.53 | 228.07
2019-07-06 13:30 | 231.15 | 226.77
2019-07-06 14:00 | 234.02 | 229.71
2019-07-06 14:30 | 234.01 | 229.59
2019-07-06 15:00 | 234.02 | 229.62
2019-07-06 15:30 | 234.48 | 230.12
2019-07-06 16:00 | 236.28 | 231.72
2019-07-06 16:30 | 237.22 | 232.94
2019-07-06 17:00 | 238.62 | 234.65
2019-07-06 17:30 | 240.92 | 236.87
2019-07-06 18:00 | 247.23 | 243.2
2019-07-06 18:30 | 250.01 | 246.03
2019-07-06 19:00 | 249 | 245.02
2019-07-06 19:30 | 249.62 | 245.65
2019-07-06 20:00 | 248.2 | 244.14
2019-07-06 20:30 | 246.5 | 242.34
2019-07-06 21:00 | 246.47 | 241.67
2019-07-06 21:30 | 245.43 | 240.54
2019-07-06 22:00 | 244.25 | 239.29
2019-07-06 22:30 | 242.4 | 237.59
2019-07-06 23:00 | 241.43 | 236.71
2019-07-06 23:30 | 240.47 | 235.75
2019-07-07 | 240.37 | 234.34
2019-07-07 00:30 | 240.01 | 233.45
2019-07-07 01:00 | 239.37 | 232.51
2019-07-07 01:30 | 239 | 231.86
2019-07-07 02:00 | 222 | 213.65
2019-07-07 02:30 | 184.89 | 173.28
2019-07-07 03:00 | 175.12 | 162.35
2019-07-07 03:30 | 174.97 | 162.18
2019-07-07 04:00 | 174.61 | 161.81
2019-07-07 04:30 | 175.25 | 162.51
2019-07-07 05:00 | 175.76 | 163.07
2019-07-07 05:30 | 176.21 | 163.49
2019-07-07 06:00 | 177.2 | 164.37
2019-07-07 06:30 | 178.31 | 165.57
2019-07-07 07:00 | 179.11 | 166.3
2019-07-07 07:30 | 208.48 | 198.65
2019-07-07 08:00 | 236.86 | 229.22
2019-07-07 08:30 | 243.4 | 235.96
2019-07-07 09:00 | 242.42 | 234.73
2019-07-07 09:30 | 240.62 | 232.76
2019-07-07 10:00 | 239.75 | 231.85
2019-07-07 10:30 | 236.76 | 228.75
2019-07-07 11:00 | 235 | 227.09
2019-07-07 11:30 | 235.96 | 228.48
2019-07-07 12:00 | 234.11 | 227.06
2019-07-07 12:30 | 233.69 | 226.87
2019-07-07 13:00 | 233.73 | 227.03
2019-07-07 13:30 | 234.88 | 228
2019-07-07 14:00 | 235.3 | 228.72
2019-07-07 14:30 | 235.91 | 229.33
2019-07-07 15:00 | 236.7 | 229.95
2019-07-07 15:30 | 237.35 | 230.64
2019-07-07 16:00 | 238.29 | 231.5
2019-07-07 16:30 | 239.22 | 232.62
2019-07-07 17:00 | 241.85 | 235.39
2019-07-07 17:30 | 242.38 | 238.4
2019-07-07 18:00 | 244.72 | 240.87
2019-07-07 18:30 | 247.82 | 243.49
2019-07-07 19:00 | 248.46 | 244.21
2019-07-07 19:30 | 246.89 | 242.88
2019-07-07 20:00 | 245.5 | 241.5
2019-07-07 20:30 | 244.71 | 240.56
2019-07-07 21:00 | 243.66 | 239.57
2019-07-07 21:30 | 242.95 | 238.52
2019-07-07 22:00 | 242.71 | 237.28
2019-07-07 22:30 | 241.58 | 236.11
2019-07-07 23:00 | 240.1 | 234.36
2019-07-07 23:30 | 239.47 | 233.55
2019-07-08 | 238.39 | 232.45
2019-07-08 00:30 | 239.38 | 231.85
2019-07-08 01:00 | 239.21 | 230.92
2019-07-08 01:30 | 238.88 | 230.67
2019-07-08 02:00 | 238.08 | 229.91
2019-07-08 02:30 | 237.94 | 230.09
2019-07-08 03:00 | 236.49 | 229.78
2019-07-08 03:30 | 236.37 | 229.83
2019-07-08 04:00 | 236.78 | 230.27
2019-07-08 04:30 | 237 | 230.46
2019-07-08 05:00 | 238.1 | 231.54
2019-07-08 05:30 | 239.01 | 232.29
2019-07-08 06:00 | 240.69 | 234.23
2019-07-08 06:30 | 242.41 | 237.32
2019-07-08 07:00 | 244.08 | 239.52
2019-07-08 07:30 | 245.76 | 240.66
2019-07-08 08:00 | 246.29 | 241.53
2019-07-08 08:30 | 246.21 | 241.49
2019-07-08 09:00 | 245.18 | 240.28
2019-07-08 09:30 | 242.54 | 237.77
2019-07-08 10:00 | 241.99 | 237.34
2019-07-08 10:30 | 239.95 | 235.35
2019-07-08 11:00 | 238.01 | 233.69
2019-07-08 11:30 | 236.86 | 232.78
2019-07-08 12:00 | 235.07 | 230.87
2019-07-08 12:30 | 235.6 | 231.49
2019-07-08 13:00 | 235.92 | 232.17
2019-07-08 13:30 | 234.56 | 231.13
2019-07-08 14:00 | 234.84 | 231.4
2019-07-08 14:30 | 236.83 | 233.4
2019-07-08 15:00 | 237.93 | 234.49
2019-07-08 15:30 | 237.77 | 234.52
2019-07-08 16:00 | 238.92 | 235.76
2019-07-08 16:30 | 239.83 | 236.53
2019-07-08 17:00 | 241.26 | 237.73
2019-07-08 17:30 | 243.99 | 240.51
2019-07-08 18:00 | 226.08 | 223.26
2019-07-08 18:30 | 221.96 | 219.08
2019-07-08 19:00 | 221.28 | 218.37
2019-07-08 19:30 | 221.75 | 218.98
2019-07-08 20:00 | 243.91 | 240.69
2019-07-08 20:30 | 248.64 | 245.31
2019-07-08 21:00 | 247.07 | 243.83
2019-07-08 21:30 | 246.4 | 242.56
2019-07-08 22:00 | 244.95 | 241.15
2019-07-08 22:30 | 242.79 | 238.95
2019-07-08 23:00 | 241.01 | 237.17
2019-07-08 23:30 | 239.95 | 235.8
2019-07-09 | 238.5 | 234.08
2019-07-09 00:30 | 238.85 | 233.14
2019-07-09 01:00 | 240.61 | 233.31
2019-07-09 01:30 | 239.18 | 231.96
2019-07-09 02:00 | 237.92 | 230.61
2019-07-09 02:30 | 238.14 | 230.89
2019-07-09 03:00 | 238.34 | 230.38
2019-07-09 03:30 | 239.38 | 230.99
2019-07-09 04:00 | 239.58 | 231.25
2019-07-09 04:30 | 240.64 | 232.38
2019-07-09 05:00 | 242.06 | 233.85
2019-07-09 05:30 | 243.71 | 235.55
2019-07-09 06:00 | 245.02 | 237.47
2019-07-09 06:30 | 245.13 | 239.86
2019-07-09 07:00 | 246.94 | 242.72
2019-07-09 07:30 | 247.83 | 243.08
2019-07-09 08:00 | 248.61 | 243.32
2019-07-09 08:30 | 247.39 | 242.04
2019-07-09 09:00 | 245 | 239.97
2019-07-09 09:30 | 242.33 | 237.7
2019-07-09 10:00 | 243.03 | 237.86
2019-07-09 10:30 | 241.15 | 235.82
2019-07-09 11:00 | 239.35 | 234.15
2019-07-09 11:30 | 238.34 | 233.27
2019-07-09 12:00 | 238.47 | 232.84
2019-07-09 12:30 | 237.28 | 231.73
2019-07-09 13:00 | 236 | 230.89
2019-07-09 13:30 | 236.25 | 230.71
2019-07-09 14:00 | 235.25 | 229.91
2019-07-09 14:30 | 235.66 | 230.23
2019-07-09 15:00 | 236.39 | 230.83
2019-07-09 15:30 | 237.5 | 231.86
2019-07-09 16:00 | 238.13 | 232.47
2019-07-09 16:30 | 239.9 | 234.63
2019-07-09 17:00 | 241.47 | 236.56
2019-07-09 17:30 | 243.99 | 239.51
2019-07-09 18:00 | 250 | 245.67
2019-07-09 18:30 | 254.53 | 250.36
2019-07-09 19:00 | 254.76 | 250.69
2019-07-09 19:30 | 254 | 249.97
2019-07-09 20:00 | 253.14 | 248.95
2019-07-09 20:30 | 252.47 | 248.36
2019-07-09 21:00 | 250.69 | 246.6
2019-07-09 21:30 | 250.08 | 245.62
2019-07-09 22:00 | 249.19 | 243.62
2019-07-09 22:30 | 247.51 | 241.67
2019-07-09 23:00 | 245.84 | 239.98
2019-07-09 23:30 | 244.14 | 238.15
2019-07-10 | 243.2 | 236.99
2019-07-10 00:30 | 243.11 | 235.32
2019-07-10 01:00 | 242.06 | 234.19
2019-07-10 01:30 | 241.58 | 233.95
2019-07-10 02:00 | 240.98 | 233.37
2019-07-10 02:30 | 240.8 | 233.22
2019-07-10 03:00 | 241.03 | 233.69
2019-07-10 03:30 | 240.94 | 233.76
2019-07-10 04:00 | 240.69 | 233.61
2019-07-10 04:30 | 241.69 | 234.59
2019-07-10 05:00 | 243.29 | 236.19
2019-07-10 05:30 | 245.37 | 238.15
2019-07-10 06:00 | 247.69 | 240.94
2019-07-10 06:30 | 249.36 | 244.12
2019-07-10 07:00 | 251.4 | 247.42
2019-07-10 07:30 | 251.55 | 247.9
2019-07-10 08:00 | 252.47 | 248.7
2019-07-10 08:30 | 249.26 | 245.35
2019-07-10 09:00 | 246.5 | 242.82
2019-07-10 09:30 | 243.3 | 239.73
2019-07-10 10:00 | 239.99 | 236.11
2019-07-10 10:30 | 236.23 | 232.07
2019-07-10 11:00 | 234.29 | 229.32
2019-07-10 11:30 | 235.71 | 230.78
2019-07-10 12:00 | 233.92 | 229.78
2019-07-10 12:30 | 232.7 | 228.77
2019-07-10 13:00 | 231.7 | 227.72
2019-07-10 13:30 | 232.36 | 228.35
2019-07-10 14:00 | 232.45 | 228.76
2019-07-10 14:30 | 233.06 | 229.66
2019-07-10 15:00 | 233.27 | 229.97
2019-07-10 15:30 | 234.11 | 230.97
2019-07-10 16:00 | 235.75 | 232.53
2019-07-10 16:30 | 237.45 | 234.29
2019-07-10 17:00 | 239.75 | 236.59
2019-07-10 17:30 | 242.81 | 239.55
2019-07-10 18:00 | 248 | 243.8
2019-07-10 18:30 | 253.73 | 249.66
2019-07-10 19:00 | 255.17 | 250.96
2019-07-10 19:30 | 255.01 | 250.56
2019-07-10 20:00 | 253.73 | 249.17
2019-07-10 20:30 | 252.93 | 248.54
2019-07-10 21:00 | 251.33 | 246.75
2019-07-10 21:30 | 251.5 | 246.39
2019-07-10 22:00 | 249.48 | 244.2
2019-07-10 22:30 | 247.42 | 242.16
2019-07-10 23:00 | 245.87 | 240.9
2019-07-10 23:30 | 244.8 | 239.95
2019-07-11 | 242.82 | 237.59
2019-07-11 00:30 | 242.45 | 236.69
2019-07-11 01:00 | 242.59 | 234.87
2019-07-11 01:30 | 242.32 | 234.63
2019-07-11 02:00 | 240.69 | 233.41
2019-07-11 02:30 | 240.22 | 232.86
2019-07-11 03:00 | 240.11 | 233.01
2019-07-11 03:30 | 240.25 | 233.18
2019-07-11 04:00 | 240.53 | 233.42
2019-07-11 04:30 | 241.43 | 234.5
2019-07-11 05:00 | 242.42 | 235.61
2019-07-11 05:30 | 244.19 | 237.34
2019-07-11 06:00 | 246.71 | 240.15
2019-07-11 06:30 | 248.57 | 242.92
2019-07-11 07:00 | 251.18 | 246.17
2019-07-11 07:30 | 252.11 | 247.49
2019-07-11 08:00 | 251.15 | 246.55
2019-07-11 08:30 | 249.73 | 244.83
2019-07-11 09:00 | 244.61 | 240.03
2019-07-11 09:30 | 239.28 | 234.84
2019-07-11 10:00 | 235.05 | 230.9
2019-07-11 10:30 | 233.78 | 229.47
2019-07-11 11:00 | 233.51 | 229.23
2019-07-11 11:30 | 232.38 | 227.64
2019-07-11 12:00 | 232.05 | 227.4
2019-07-11 12:30 | 231.47 | 226.73
2019-07-11 13:00 | 231.35 | 226.14
2019-07-11 13:30 | 231.86 | 226.46
2019-07-11 14:00 | 231.76 | 226.4
2019-07-11 14:30 | 232.71 | 227.3
2019-07-11 15:00 | 233.3 | 228.04
2019-07-11 15:30 | 234.28 | 229.27
2019-07-11 16:00 | 236.36 | 231.25
2019-07-11 16:30 | 238.84 | 233.77
2019-07-11 17:00 | 241.35 | 236.49
2019-07-11 17:30 | 243.41 | 238.71
2019-07-11 18:00 | 246.81 | 242.45
2019-07-11 18:30 | 251.22 | 246.97
2019-07-11 19:00 | 253.44 | 249.15
2019-07-11 19:30 | 253.58 | 249.4
2019-07-11 20:00 | 252.04 | 247.9
2019-07-11 20:30 | 251.64 | 247.6
2019-07-11 21:00 | 250.44 | 246.27
2019-07-11 21:30 | 250.81 | 246.09
2019-07-11 22:00 | 248.9 | 244.04
2019-07-11 22:30 | 246.21 | 241.52
2019-07-11 23:00 | 244.57 | 239.84
2019-07-11 23:30 | 242.93 | 238.4
2019-07-12 | 242.34 | 236.92
2019-07-12 00:30 | 242.02 | 236.05
2019-07-12 01:00 | 241.45 | 234.89
2019-07-12 01:30 | 240.11 | 233.67
2019-07-12 02:00 | 240.27 | 233.89
2019-07-12 02:30 | 240.02 | 233.69
2019-07-12 03:00 | 241.08 | 233.84
2019-07-12 03:30 | 242.24 | 234.01
2019-07-12 04:00 | 242.34 | 233.99
2019-07-12 04:30 | 242.89 | 234.98
2019-07-12 05:00 | 244.4 | 236.55
2019-07-12 05:30 | 246.11 | 238.6
2019-07-12 06:00 | 247.29 | 240.8
2019-07-12 06:30 | 249.11 | 243.74
2019-07-12 07:00 | 252.02 | 247.02
2019-07-12 07:30 | 252.37 | 248.01
2019-07-12 08:00 | 252.43 | 247.89
2019-07-12 08:30 | 250.09 | 245.25
2019-07-12 09:00 | 246.26 | 241.07
2019-07-12 09:30 | 240.85 | 235.55
2019-07-12 10:00 | 237.45 | 232.12
2019-07-12 10:30 | 235.98 | 230.42
2019-07-12 11:00 | 233.14 | 228.01
2019-07-12 11:30 | 232.31 | 227.17
2019-07-12 12:00 | 230.73 | 225.74
2019-07-12 12:30 | 230.26 | 226.31
2019-07-12 13:00 | 229.44 | 225.4
2019-07-12 13:30 | 228.69 | 224.69
2019-07-12 14:00 | 228.58 | 224.68
2019-07-12 14:30 | 230 | 226.16
2019-07-12 15:00 | 230.66 | 226.72
2019-07-12 15:30 | 232.55 | 228.85
2019-07-12 16:00 | 234.75 | 231.2
2019-07-12 16:30 | 236.63 | 232.98
2019-07-12 17:00 | 238.14 | 234.68
2019-07-12 17:30 | 240.94 | 237.34
2019-07-12 18:00 | 245.1 | 240.86
2019-07-12 18:30 | 248.35 | 244.36
2019-07-12 19:00 | 248.78 | 244.65
2019-07-12 19:30 | 246.9 | 242.73
2019-07-12 20:00 | 247.22 | 243.01
2019-07-12 20:30 | 246.6 | 242.43
2019-07-12 21:00 | 246.74 | 242.97
2019-07-12 21:30 | 248.09 | 242.73
2019-07-12 22:00 | 247.62 | 242.18
2019-07-12 22:30 | 246.06 | 240.56
2019-07-12 23:00 | 243.86 | 238.74
2019-07-12 23:30 | 243.76 | 238.35
2019-07-13 | 242.51 | 236.01
2019-07-13 00:30 | 242.58 | 235.65
2019-07-13 01:00 | 242.16 | 234.69
2019-07-13 01:30 | 240.86 | 234.33
2019-07-13 02:00 | 239.63 | 233.48
2019-07-13 02:30 | 239.46 | 233.55
2019-07-13 03:00 | 239.29 | 233.45
2019-07-13 03:30 | 239.64 | 233.76
2019-07-13 04:00 | 239.84 | 233.84
2019-07-13 04:30 | 240.46 | 234.63
2019-07-13 05:00 | 241.63 | 235.75
2019-07-13 05:30 | 243.1 | 237.05
2019-07-13 06:00 | 243.94 | 238.3
2019-07-13 06:30 | 245.74 | 239.89
2019-07-13 07:00 | 248.26 | 241.9
2019-07-13 07:30 | 248.58 | 241.32
2019-07-13 08:00 | 247.65 | 241.47
2019-07-13 08:30 | 243.97 | 239.53
2019-07-13 09:00 | 242.54 | 237.76
2019-07-13 09:30 | 239.23 | 234.65
2019-07-13 10:00 | 236.16 | 231.67
2019-07-13 10:30 | 232.92 | 229.09
2019-07-13 11:00 | 231.98 | 226.54
2019-07-13 11:30 | 231.67 | 224.57
2019-07-13 12:00 | 232.83 | 226.17
2019-07-13 12:30 | 230.11 | 224.63
2019-07-13 13:00 | 228.42 | 224.18
2019-07-13 13:30 | 228.06 | 223.72
2019-07-13 14:00 | 227.15 | 223.07
2019-07-13 14:30 | 229.11 | 224.81
2019-07-13 15:00 | 229.79 | 225.7
2019-07-13 15:30 | 231.54 | 227.44
2019-07-13 16:00 | 233.06 | 229.44
2019-07-13 16:30 | 235.44 | 231.92
2019-07-13 17:00 | 239.36 | 235.37
2019-07-13 17:30 | 243.01 | 238.84
2019-07-13 18:00 | 246.76 | 243.17
2019-07-13 18:30 | 249.14 | 245.8
2019-07-13 19:00 | 249.32 | 245.93
2019-07-13 19:30 | 248.92 | 245.46
2019-07-13 20:00 | 248.61 | 244.78
2019-07-13 20:30 | 247.79 | 244.06
2019-07-13 21:00 | 247.08 | 243.6
2019-07-13 21:30 | 247.69 | 243.63
2019-07-13 22:00 | 246.14 | 241.84
2019-07-13 22:30 | 244.3 | 239.88
2019-07-13 23:00 | 242.93 | 238.71
2019-07-13 23:30 | 241.75 | 237.15
2019-07-14 | 240.42 | 235.61
2019-07-14 00:30 | 240.52 | 234.96
2019-07-14 01:00 | 239.49 | 233.41
2019-07-14 01:30 | 240.01 | 233.41
2019-07-14 02:00 | 239.28 | 232.79
2019-07-14 02:30 | 238.95 | 232.75
2019-07-14 03:00 | 238.53 | 232.45
2019-07-14 03:30 | 239.28 | 233.33
2019-07-14 04:00 | 239.28 | 233.36
2019-07-14 04:30 | 240 | 234.09
2019-07-14 05:00 | 241.1 | 235.21
2019-07-14 05:30 | 242.34 | 236.31
2019-07-14 06:00 | 244.38 | 238.18
2019-07-14 06:30 | 246.32 | 239.78
2019-07-14 07:00 | 248.54 | 241.75
2019-07-14 07:30 | 251.4 | 244.43
2019-07-14 08:00 | 252.37 | 245.15
2019-07-14 08:30 | 250.1 | 242.85
2019-07-14 09:00 | 246.8 | 239.23
2019-07-14 09:30 | 244.8 | 237.41
2019-07-14 10:00 | 241.48 | 234.53
2019-07-14 10:30 | 238.61 | 232.1
2019-07-14 11:00 | 236.5 | 229.86
2019-07-14 11:30 | 236.72 | 229.55
2019-07-14 12:00 | 234.65 | 227.68
2019-07-14 12:30 | 234 | 226.62
2019-07-14 13:00 | 233.57 | 226.02
2019-07-14 13:30 | 232.24 | 225.25
2019-07-14 14:00 | 232.71 | 225.65
2019-07-14 14:30 | 232.63 | 226.62
2019-07-14 15:00 | 232.98 | 227.12
2019-07-14 15:30 | 235.2 | 229.58
2019-07-14 16:00 | 236.72 | 231.13
2019-07-14 16:30 | 240.49 | 234.99
2019-07-14 17:00 | 244.6 | 239.02
2019-07-14 17:30 | 248.72 | 244.48
2019-07-14 18:00 | 254.4 | 250.73
2019-07-14 18:30 | 256.46 | 253.38
2019-07-14 19:00 | 255.63 | 252.75
2019-07-14 19:30 | 254.74 | 251.87
2019-07-14 20:00 | 256.03 | 253.09
2019-07-14 20:30 | 254.63 | 251.74
2019-07-14 21:00 | 253.73 | 250.01
2019-07-14 21:30 | 253.8 | 248.58
2019-07-14 22:00 | 250.7 | 245.6
2019-07-14 22:30 | 248.38 | 242.9
2019-07-14 23:00 | 245.65 | 240.19
2019-07-14 23:30 | 244.08 | 238.5
2019-07-15 | 243.06 | 237.15
2019-07-15 00:30 | 242.64 | 236.37
2019-07-15 01:00 | 242.54 | 234.91
2019-07-15 01:30 | 242.47 | 234.6
2019-07-15 02:00 | 242.11 | 234.11
2019-07-15 02:30 | 241.98 | 234.21
2019-07-15 03:00 | 241.98 | 234.1
2019-07-15 03:30 | 241.43 | 234.05
2019-07-15 04:00 | 242.29 | 235.17
2019-07-15 04:30 | 242.91 | 235.99
2019-07-15 05:00 | 244.46 | 237.74
2019-07-15 05:30 | 246.16 | 239.47
2019-07-15 06:00 | 249.98 | 244.47
2019-07-15 06:30 | 254.45 | 249.59
2019-07-15 07:00 | 259.69 | 255.74
2019-07-15 07:30 | 262.83 | 259.3
2019-07-15 08:00 | 264.1 | 260.62
2019-07-15 08:30 | 258.15 | 254.46
2019-07-15 09:00 | 254.14 | 250.11
2019-07-15 09:30 | 249.22 | 244.98
2019-07-15 10:00 | 246.2 | 242
2019-07-15 10:30 | 242.64 | 238.63
2019-07-15 11:00 | 241.42 | 236.9
2019-07-15 11:30 | 240.39 | 235.13
2019-07-15 12:00 | 239.61 | 234.32
2019-07-15 12:30 | 237.94 | 232.56
2019-07-15 13:00 | 237.21 | 231.72
2019-07-15 13:30 | 236.44 | 230.8
2019-07-15 14:00 | 236.33 | 230.5
2019-07-15 14:30 | 236.29 | 230.51
2019-07-15 15:00 | 236.96 | 231.17
2019-07-15 15:30 | 238.93 | 233.02
2019-07-15 16:00 | 240.29 | 234.61
2019-07-15 16:30 | 242.56 | 237.12
2019-07-15 17:00 | 244.36 | 240.06
2019-07-15 17:30 | 248.83 | 244.9
2019-07-15 18:00 | 256.4 | 252.48
2019-07-15 18:30 | 262.6 | 258.91
2019-07-15 19:00 | 264.59 | 260.98
2019-07-15 19:30 | 263.97 | 260.58
2019-07-15 20:00 | 263.1 | 259.6
2019-07-15 20:30 | 260.85 | 257.59
2019-07-15 21:00 | 258.4 | 254.71
2019-07-15 21:30 | 258.08 | 253.27
2019-07-15 22:00 | 255.23 | 249.98
2019-07-15 22:30 | 253.02 | 247.5
2019-07-15 23:00 | 249.86 | 244.58
2019-07-15 23:30 | 248.55 | 243.21
2019-07-16 | 247.37 | 241.3
2019-07-16 00:30 | 247.51 | 241.05
2019-07-16 01:00 | 246.78 | 239.7
2019-07-16 01:30 | 246.43 | 238.93
2019-07-16 02:00 | 246.55 | 239.03
2019-07-16 02:30 | 246.26 | 238.69
2019-07-16 03:00 | 246.41 | 238.9
2019-07-16 03:30 | 247.1 | 239.57
2019-07-16 04:00 | 246.46 | 238.89
2019-07-16 04:30 | 248.84 | 241.06
2019-07-16 05:00 | 251.33 | 243.43
2019-07-16 05:30 | 253.14 | 245.99
2019-07-16 06:00 | 257.13 | 250.26
2019-07-16 06:30 | 259.89 | 255.05
2019-07-16 07:00 | 264.55 | 260.24
2019-07-16 07:30 | 266.58 | 261.94
2019-07-16 08:00 | 264.47 | 259.8
2019-07-16 08:30 | 259.27 | 254.33
2019-07-16 09:00 | 254.39 | 248.94
2019-07-16 09:30 | 249.52 | 244.16
2019-07-16 10:00 | 247.26 | 241.71
2019-07-16 10:30 | 245.47 | 238.58
2019-07-16 11:00 | 243.16 | 236.2
2019-07-16 11:30 | 241.85 | 234.97
2019-07-16 12:00 | 240.47 | 234.14
2019-07-16 12:30 | 239.01 | 233.05
2019-07-16 13:00 | 237.24 | 231.65
2019-07-16 13:30 | 236.1 | 230.8
2019-07-16 14:00 | 236.69 | 231.39
2019-07-16 14:30 | 237.21 | 231.84
2019-07-16 15:00 | 236.76 | 231.68
2019-07-16 15:30 | 236.4 | 231.9
2019-07-16 16:00 | 237.58 | 233.29
2019-07-16 16:30 | 240.18 | 235.99
2019-07-16 17:00 | 241.79 | 238.37
2019-07-16 17:30 | 245.68 | 242.27
2019-07-16 18:00 | 251.11 | 247.79
2019-07-16 18:30 | 259.08 | 256.03
2019-07-16 19:00 | 262.08 | 259.01
2019-07-16 19:30 | 262.01 | 258.9
2019-07-16 20:00 | 260.54 | 257.34
2019-07-16 20:30 | 259.62 | 256.31
2019-07-16 21:00 | 257.51 | 254
2019-07-16 21:30 | 257.07 | 252.71
2019-07-16 22:00 | 255.52 | 250.63
2019-07-16 22:30 | 252.71 | 247.05
2019-07-16 23:00 | 250.1 | 244.17
2019-07-16 23:30 | 248.8 | 242.64
2019-07-17 | 247.95 | 240.9
2019-07-17 00:30 | 247.59 | 240.39
2019-07-17 01:00 | 247.25 | 239.14
2019-07-17 01:30 | 245.57 | 238.46
2019-07-17 02:00 | 244.41 | 237.67
2019-07-17 02:30 | 244.62 | 237.9
2019-07-17 03:00 | 245.22 | 238.49
2019-07-17 03:30 | 245.16 | 238.67
2019-07-17 04:00 | 245.91 | 239.52
2019-07-17 04:30 | 247.22 | 240.76
2019-07-17 05:00 | 248.35 | 241.72
2019-07-17 05:30 | 250.92 | 244.73
2019-07-17 06:00 | 253.8 | 248.75
2019-07-17 06:30 | 258.67 | 255.05
2019-07-17 07:00 | 264.07 | 259.58
2019-07-17 07:30 | 265.99 | 261.08
2019-07-17 08:00 | 264.77 | 259.65
2019-07-17 08:30 | 259.55 | 253.8
2019-07-17 09:00 | 254.37 | 248.42
2019-07-17 09:30 | 250.11 | 243.4
2019-07-17 10:00 | 245.36 | 239.48
2019-07-17 10:30 | 241.47 | 236.38
2019-07-17 11:00 | 238.43 | 233.81
2019-07-17 11:30 | 236.64 | 232.26
2019-07-17 12:00 | 235.51 | 230.89
2019-07-17 12:30 | 233.28 | 229.08
2019-07-17 13:00 | 230.72 | 226.62
2019-07-17 13:30 | 231.37 | 227.16
2019-07-17 14:00 | 230.93 | 226.98
2019-07-17 14:30 | 234.16 | 230.09
2019-07-17 15:00 | 235.81 | 231.44
2019-07-17 15:30 | 236.58 | 232.69
2019-07-17 16:00 | 238.06 | 234.43
2019-07-17 16:30 | 240.43 | 236.75
2019-07-17 17:00 | 243.56 | 239.83
2019-07-17 17:30 | 245.97 | 242.84
2019-07-17 18:00 | 252.15 | 248.91
2019-07-17 18:30 | 258.17 | 255.05
2019-07-17 19:00 | 261.44 | 258.38
2019-07-17 19:30 | 261.9 | 258.92
2019-07-17 20:00 | 260.6 | 257.57
2019-07-17 20:30 | 261.25 | 258.09
2019-07-17 21:00 | 258.28 | 255.22
2019-07-17 21:30 | 258.72 | 253.42
2019-07-17 22:00 | 256.8 | 251.07
2019-07-17 22:30 | 253.39 | 247.73
2019-07-17 23:00 | 250.47 | 244.66
2019-07-17 23:30 | 250.42 | 243.8
2019-07-18 | 249.63 | 242
2019-07-18 00:30 | 248.72 | 241.01
2019-07-18 01:00 | 247.57 | 239.73
2019-07-18 01:30 | 246.8 | 239.16
2019-07-18 02:00 | 246.62 | 239.1
2019-07-18 02:30 | 246.31 | 238.48
2019-07-18 03:00 | 244.36 | 236.35
2019-07-18 03:30 | 245.1 | 237.03
2019-07-18 04:00 | 245.31 | 237.24
2019-07-18 04:30 | 246.73 | 238.78
2019-07-18 05:00 | 249.38 | 241.81
2019-07-18 05:30 | 251.68 | 245.73
2019-07-18 06:00 | 254.92 | 250
2019-07-18 06:30 | 245.23 | 241.61
2019-07-18 07:00 | 221.3 | 218.36
2019-07-18 07:30 | 224.28 | 219.44
2019-07-18 08:00 | 223.11 | 217.96
2019-07-18 08:30 | 219.97 | 213.75
2019-07-18 09:00 | 221.95 | 215.34
2019-07-18 09:30 | 228.93 | 222.75
2019-07-18 10:00 | 243.63 | 237.65
2019-07-18 10:30 | 238.54 | 234.13
2019-07-18 11:00 | 235.97 | 231.8
2019-07-18 11:30 | 234.02 | 229.55
2019-07-18 12:00 | 231.61 | 227.11
2019-07-18 12:30 | 229.84 | 225.29
2019-07-18 13:00 | 229.21 | 224.75
2019-07-18 13:30 | 229.45 | 225.43
2019-07-18 14:00 | 230.16 | 226.4
2019-07-18 14:30 | 231.77 | 227.92
2019-07-18 15:00 | 233.66 | 229.57
2019-07-18 15:30 | 234.86 | 230.86
2019-07-18 16:00 | 235.86 | 232.06
2019-07-18 16:30 | 238.61 | 234.54
2019-07-18 17:00 | 241.1 | 237.36
2019-07-18 17:30 | 244.42 | 241.3
2019-07-18 18:00 | 249.25 | 246.41
2019-07-18 18:30 | 256.42 | 253.64
2019-07-18 19:00 | 259.22 | 256.47
2019-07-18 19:30 | 259.5 | 256.86
2019-07-18 20:00 | 259.39 | 256.7
2019-07-18 20:30 | 258.23 | 255.57
2019-07-18 21:00 | 257.17 | 254.51
2019-07-18 21:30 | 255.8 | 252.66
2019-07-18 22:00 | 254.32 | 250.98
2019-07-18 22:30 | 251.28 | 247.78
2019-07-18 23:00 | 249.1 | 244.88
2019-07-18 23:30 | 248.18 | 243.39
2019-07-19 | 246.39 | 241.72
2019-07-19 00:30 | 246.1 | 241.2
2019-07-19 01:00 | 244.64 | 239.57
2019-07-19 01:30 | 245.19 | 239.13
2019-07-19 02:00 | 244.7 | 238.82
2019-07-19 02:30 | 244.4 | 238.92
2019-07-19 03:00 | 244.09 | 238.89
2019-07-19 03:30 | 243.46 | 238.81
2019-07-19 04:00 | 244 | 239.8
2019-07-19 04:30 | 244.83 | 240.81
2019-07-19 05:00 | 246.99 | 243.12
2019-07-19 05:30 | 250.78 | 246.59
2019-07-19 06:00 | 254.61 | 250.16
2019-07-19 06:30 | 241.93 | 238.96
2019-07-19 07:00 | 221.52 | 218.84
2019-07-19 07:30 | 223.89 | 220.75
2019-07-19 08:00 | 222.49 | 219.78
2019-07-19 08:30 | 218.94 | 215.77
2019-07-19 09:00 | 220.43 | 216.81
2019-07-19 09:30 | 223.11 | 220.48
2019-07-19 10:00 | 237.4 | 234.45
2019-07-19 10:30 | 239.66 | 236.41
2019-07-19 11:00 | 237.44 | 233.83
2019-07-19 11:30 | 235.34 | 231.25
2019-07-19 12:00 | 235.58 | 230.4
2019-07-19 12:30 | 234.68 | 229.47
2019-07-19 13:00 | 233.97 | 229.17
2019-07-19 13:30 | 234.24 | 229.25
2019-07-19 14:00 | 234.84 | 229.82
2019-07-19 14:30 | 235.87 | 230.37
2019-07-19 15:00 | 236.53 | 230.99
2019-07-19 15:30 | 238.22 | 233.21
2019-07-19 16:00 | 241.18 | 236.48
2019-07-19 16:30 | 242.84 | 238.52
2019-07-19 17:00 | 244.94 | 241.11
2019-07-19 17:30 | 246.53 | 243.22
2019-07-19 18:00 | 250.86 | 247.66
2019-07-19 18:30 | 256.83 | 253.56
2019-07-19 19:00 | 259.18 | 255.9
2019-07-19 19:30 | 259.63 | 256.2
2019-07-19 20:00 | 259.35 | 256.09
2019-07-19 20:30 | 258.49 | 255.47
2019-07-19 21:00 | 257.64 | 254.55
2019-07-19 21:30 | 257 | 253.94
2019-07-19 22:00 | 255.09 | 252
2019-07-19 22:30 | 253.22 | 249.8
2019-07-19 23:00 | 251.69 | 247.59
2019-07-19 23:30 | 251.12 | 246.43
2019-07-20 | 248.22 | 244.14
2019-07-20 00:30 | 248.01 | 243.86
2019-07-20 01:00 | 248.33 | 242.32
2019-07-20 01:30 | 248.59 | 242.11
2019-07-20 02:00 | 247.55 | 241.35
2019-07-20 02:30 | 246.9 | 241.34
2019-07-20 03:00 | 246.49 | 241.52
2019-07-20 03:30 | 245.63 | 241.02
2019-07-20 04:00 | 246.1 | 241.71
2019-07-20 04:30 | 246.7 | 242.46
2019-07-20 05:00 | 248.08 | 243.9
2019-07-20 05:30 | 249.91 | 245.76
2019-07-20 06:00 | 251.52 | 247.19
2019-07-20 06:30 | 254.45 | 250.08
2019-07-20 07:00 | 257.12 | 252.76
2019-07-20 07:30 | 257.1 | 253.63
2019-07-20 08:00 | 257.46 | 253.72
2019-07-20 08:30 | 254.78 | 251.32
2019-07-20 09:00 | 250.57 | 247.49
2019-07-20 09:30 | 246.05 | 243.27
2019-07-20 10:00 | 243.11 | 239.31
2019-07-20 10:30 | 240.97 | 235.58
2019-07-20 11:00 | 236.52 | 232.29
2019-07-20 11:30 | 232.55 | 229.55
2019-07-20 12:00 | 231.07 | 227.81
2019-07-20 12:30 | 232.02 | 228.64
2019-07-20 13:00 | 232.73 | 229.33
2019-07-20 13:30 | 231.93 | 228.71
2019-07-20 14:00 | 230.54 | 227.38
2019-07-20 14:30 | 230.33 | 227.25
2019-07-20 15:00 | 231.46 | 228.36
2019-07-20 15:30 | 232.83 | 229.63
2019-07-20 16:00 | 234.85 | 231.49
2019-07-20 16:30 | 237.29 | 233.72
2019-07-20 17:00 | 239.27 | 235.76
2019-07-20 17:30 | 242.83 | 238.95
2019-07-20 18:00 | 245.27 | 242.05
2019-07-20 18:30 | 248.82 | 245.72
2019-07-20 19:00 | 249.68 | 246.54
2019-07-20 19:30 | 249.45 | 246.31
2019-07-20 20:00 | 249.87 | 246.72
2019-07-20 20:30 | 249.24 | 246.09
2019-07-20 21:00 | 248.51 | 245.34
2019-07-20 21:30 | 247.42 | 244.48
2019-07-20 22:00 | 246.5 | 243.56
2019-07-20 22:30 | 244.3 | 241.28
2019-07-20 23:00 | 243.11 | 239.93
2019-07-20 23:30 | 242.93 | 239.53
2019-07-21 | 241.53 | 237.78
2019-07-21 00:30 | 240.64 | 236.96
2019-07-21 01:00 | 240.34 | 236.31
2019-07-21 01:30 | 239.89 | 235.42
2019-07-21 02:00 | 239.66 | 235.22
2019-07-21 02:30 | 239.23 | 234.89
2019-07-21 03:00 | 238.7 | 234.52
2019-07-21 03:30 | 238.57 | 234.41
2019-07-21 04:00 | 239.21 | 235.09
2019-07-21 04:30 | 239.27 | 235.16
2019-07-21 05:00 | 240.3 | 236.12
2019-07-21 05:30 | 241.02 | 236.73
2019-07-21 06:00 | 242.29 | 237.8
2019-07-21 06:30 | 244.19 | 239.68
2019-07-21 07:00 | 246.16 | 241.53
2019-07-21 07:30 | 248.45 | 243.37
2019-07-21 08:00 | 247.51 | 243.52
2019-07-21 08:30 | 246 | 242.14
2019-07-21 09:00 | 243.5 | 239.89
2019-07-21 09:30 | 240.47 | 237.37
2019-07-21 10:00 | 237.67 | 234.72
2019-07-21 10:30 | 233.66 | 230.79
2019-07-21 11:00 | 230.58 | 227.56
2019-07-21 11:30 | 228.89 | 225.85
2019-07-21 12:00 | 228.38 | 225.02
2019-07-21 12:30 | 228.92 | 225.53
2019-07-21 13:00 | 227.8 | 224.52
2019-07-21 13:30 | 228.62 | 225.26
2019-07-21 14:00 | 229.31 | 225.99
2019-07-21 14:30 | 230.71 | 227.47
2019-07-21 15:00 | 231.39 | 228.06
2019-07-21 15:30 | 232.6 | 229.15
2019-07-21 16:00 | 234.36 | 230.49
2019-07-21 16:30 | 236.23 | 232.45
2019-07-21 17:00 | 238.52 | 234.45
2019-07-21 17:30 | 241.43 | 236.56
2019-07-21 18:00 | 242.98 | 238.75
2019-07-21 18:30 | 244.18 | 240.88
2019-07-21 19:00 | 244.46 | 241.27
2019-07-21 19:30 | 243.41 | 240.15
2019-07-21 20:00 | 243.33 | 240.03
2019-07-21 20:30 | 242.5 | 239.27
2019-07-21 21:00 | 240.23 | 236.77
2019-07-21 21:30 | 238.62 | 235.14
2019-07-21 22:00 | 237.28 | 233.67
2019-07-21 22:30 | 235.21 | 231.79
2019-07-21 23:00 | 233.37 | 229.97
2019-07-21 23:30 | 232.54 | 229.06
2019-07-22 | 232.33 | 228.75
2019-07-22 00:30 | 232.63 | 228.76
2019-07-22 01:00 | 232 | 227.76
2019-07-22 01:30 | 231.14 | 226.9
2019-07-22 02:00 | 230.93 | 226.82
2019-07-22 02:30 | 230.18 | 226.19
2019-07-22 03:00 | 230.94 | 226.87
2019-07-22 03:30 | 231.32 | 227.17
2019-07-22 04:00 | 231.19 | 227.03
2019-07-22 04:30 | 232.08 | 227.97
2019-07-22 05:00 | 233.37 | 229.09
2019-07-22 05:30 | 234.91 | 231.16
2019-07-22 06:00 | 237.29 | 234.06
2019-07-22 06:30 | 241.27 | 238.37
2019-07-22 07:00 | 245.2 | 241.98
2019-07-22 07:30 | 248 | 245.21
2019-07-22 08:00 | 249.22 | 246.72
2019-07-22 08:30 | 244.88 | 242.24
2019-07-22 09:00 | 240.43 | 237.71
2019-07-22 09:30 | 235.47 | 232.61
2019-07-22 10:00 | 232.17 | 229.37
2019-07-22 10:30 | 229.18 | 226.24
2019-07-22 11:00 | 229.69 | 226.87
2019-07-22 11:30 | 228.92 | 225.99
2019-07-22 12:00 | 228.73 | 225.23
2019-07-22 12:30 | 229.95 | 224.87
2019-07-22 13:00 | 229.78 | 224.37
2019-07-22 13:30 | 228.86 | 223.83
2019-07-22 14:00 | 229.78 | 224.41
2019-07-22 14:30 | 230.72 | 225.06
2019-07-22 15:00 | 232.13 | 226.59
2019-07-22 15:30 | 233.13 | 227.52
2019-07-22 16:00 | 234.99 | 229.54
2019-07-22 16:30 | 236.05 | 231.39
2019-07-22 17:00 | 238.81 | 234.47
2019-07-22 17:30 | 241.34 | 236.76
2019-07-22 18:00 | 245.11 | 240.23
2019-07-22 18:30 | 249.95 | 245.32
2019-07-22 19:00 | 251.07 | 246.7
2019-07-22 19:30 | 250.23 | 245.86
2019-07-22 20:00 | 248.68 | 244.39
2019-07-22 20:30 | 248.16 | 243.81
2019-07-22 21:00 | 246.39 | 241.93
2019-07-22 21:30 | 245.06 | 241.04
2019-07-22 22:00 | 244.04 | 240.03
2019-07-22 22:30 | 241.6 | 237.26
2019-07-22 23:00 | 240.05 | 235.45
2019-07-22 23:30 | 238.1 | 233.74
2019-07-23 | 236.53 | 232.22
2019-07-23 00:30 | 237.01 | 233.26
2019-07-23 01:00 | 234.67 | 231.3
2019-07-23 01:30 | 233.55 | 230.13
2019-07-23 02:00 | 232.08 | 228.49
2019-07-23 02:30 | 231.22 | 227.49
2019-07-23 03:00 | 231.71 | 227.95
2019-07-23 03:30 | 232.08 | 228.44
2019-07-23 04:00 | 232.67 | 228.98
2019-07-23 04:30 | 233.48 | 229.9
2019-07-23 05:00 | 235.3 | 231.8
2019-07-23 05:30 | 237.83 | 233.96
2019-07-23 06:00 | 241.41 | 236.8
2019-07-23 06:30 | 246.37 | 242.16
2019-07-23 07:00 | 250.08 | 246.39
2019-07-23 07:30 | 250.66 | 246.9
2019-07-23 08:00 | 248.69 | 244.85
2019-07-23 08:30 | 245.4 | 241.24
2019-07-23 09:00 | 241.01 | 236.81
2019-07-23 09:30 | 236.67 | 232.25
2019-07-23 10:00 | 232.49 | 228.1
2019-07-23 10:30 | 230.31 | 226.01
2019-07-23 11:00 | 228.79 | 224.91
2019-07-23 11:30 | 228.22 | 224.17
2019-07-23 12:00 | 227.03 | 223.25
2019-07-23 12:30 | 226.75 | 222.52
2019-07-23 13:00 | 226.82 | 222.06
2019-07-23 13:30 | 226.29 | 221.67
2019-07-23 14:00 | 226.95 | 221.99
2019-07-23 14:30 | 227.24 | 222.49
2019-07-23 15:00 | 228.37 | 223.38
2019-07-23 15:30 | 230.26 | 225.35
2019-07-23 16:00 | 231.39 | 226.73
2019-07-23 16:30 | 233.57 | 228.16
2019-07-23 17:00 | 236.51 | 230.92
2019-07-23 17:30 | 241.59 | 235.25
2019-07-23 18:00 | 245.21 | 239.11
2019-07-23 18:30 | 250.29 | 244.46
2019-07-23 19:00 | 251.6 | 245.8
2019-07-23 19:30 | 250.56 | 244.82
2019-07-23 20:00 | 249.3 | 244.54
2019-07-23 20:30 | 248.57 | 243.84
2019-07-23 21:00 | 246.97 | 242.18
2019-07-23 21:30 | 246.05 | 242.45
2019-07-23 22:00 | 244.45 | 241.04
2019-07-23 22:30 | 242.55 | 239.29
2019-07-23 23:00 | 240.46 | 237.22
2019-07-23 23:30 | 239.12 | 235.85
2019-07-24 | 237.9 | 234.5
2019-07-24 00:30 | 235.78 | 232.35
2019-07-24 01:00 | 235.2 | 231.86
2019-07-24 01:30 | 235.4 | 232.13
2019-07-24 02:00 | 235.17 | 231.84
2019-07-24 02:30 | 234.66 | 231.28
2019-07-24 03:00 | 235.16 | 231.82
2019-07-24 03:30 | 235.3 | 231.91
2019-07-24 04:00 | 235.47 | 232.13
2019-07-24 04:30 | 236.62 | 233.25
2019-07-24 05:00 | 238.8 | 235.42
2019-07-24 05:30 | 242.14 | 238.79
2019-07-24 06:00 | 244.96 | 241.64
2019-07-24 06:30 | 252.41 | 248.03
2019-07-24 07:00 | 257.52 | 252.76
2019-07-24 07:30 | 258.26 | 254.1
2019-07-24 08:00 | 256.43 | 252.39
2019-07-24 08:30 | 251.71 | 247.42
2019-07-24 09:00 | 246.39 | 241.83
2019-07-24 09:30 | 241.49 | 236.52
2019-07-24 10:00 | 243.33 | 238.8
2019-07-24 10:30 | 241.07 | 236.57
2019-07-24 11:00 | 232.76 | 228.81
2019-07-24 11:30 | 232.39 | 228.62
2019-07-24 12:00 | 231.81 | 227.78
2019-07-24 12:30 | 231.19 | 226.75
2019-07-24 13:00 | 230.47 | 225.97
2019-07-24 13:30 | 231.19 | 226.48
2019-07-24 14:00 | 231.18 | 226.92
2019-07-24 14:30 | 231.36 | 227.11
2019-07-24 15:00 | 230.97 | 226.77
2019-07-24 15:30 | 231.74 | 227.45
2019-07-24 16:00 | 233.24 | 228.57
2019-07-24 16:30 | 234.86 | 230.17
2019-07-24 17:00 | 237.19 | 231.9
2019-07-24 17:30 | 239.06 | 233.72
2019-07-24 18:00 | 243.29 | 237.95
2019-07-24 18:30 | 249.43 | 244.36
2019-07-24 19:00 | 252.2 | 247.18
2019-07-24 19:30 | 251.36 | 246.53
2019-07-24 20:00 | 250.89 | 245.94
2019-07-24 20:30 | 250.1 | 245.14
2019-07-24 21:00 | 249.31 | 244.22
2019-07-24 21:30 | 247.6 | 243.34
2019-07-24 22:00 | 245.36 | 241.16
2019-07-24 22:30 | 243.21 | 239.16
2019-07-24 23:00 | 241.84 | 237.78
2019-07-24 23:30 | 240.09 | 236.19
2019-07-25 | 238.52 | 234.89
2019-07-25 00:30 | 237.87 | 234.48
2019-07-25 01:00 | 237.01 | 233.65
2019-07-25 01:30 | 236.46 | 232.98
2019-07-25 02:00 | 235.97 | 232.24
2019-07-25 02:30 | 236.49 | 232.7
2019-07-25 03:00 | 236.5 | 232.69
2019-07-25 03:30 | 237.05 | 232.87
2019-07-25 04:00 | 237.6 | 233.48
2019-07-25 04:30 | 238.26 | 234.57
2019-07-25 05:00 | 239.98 | 236.24
2019-07-25 05:30 | 243.16 | 239.55
2019-07-25 06:00 | 247.05 | 242.8
2019-07-25 06:30 | 251.84 | 248.05
2019-07-25 07:00 | 256.93 | 252.7
2019-07-25 07:30 | 236.72 | 232.9
2019-07-25 08:00 | 217.43 | 213.88
2019-07-25 08:30 | 220.56 | 216.97
2019-07-25 09:00 | 224.6 | 221.16
2019-07-25 09:30 | 236.92 | 232.21
2019-07-25 10:00 | 237.08 | 232.49
2019-07-25 10:30 | 234.62 | 230.26
2019-07-25 11:00 | 230.05 | 225.79
2019-07-25 11:30 | 231.65 | 227.65
2019-07-25 12:00 | 231.34 | 227.08
2019-07-25 12:30 | 230.63 | 226.13
2019-07-25 13:00 | 229.03 | 224.5
2019-07-25 13:30 | 228.79 | 224.17
2019-07-25 14:00 | 229.54 | 225.1
2019-07-25 14:30 | 230.84 | 226.31
2019-07-25 15:00 | 230.86 | 226.11
2019-07-25 15:30 | 232.51 | 227.2
2019-07-25 16:00 | 234.74 | 228.52
2019-07-25 16:30 | 237.82 | 231.33
2019-07-25 17:00 | 240.69 | 233.96
2019-07-25 17:30 | 240.55 | 234.69
2019-07-25 18:00 | 244.66 | 238.69
2019-07-25 18:30 | 250.54 | 244.45
2019-07-25 19:00 | 253.05 | 247.04
2019-07-25 19:30 | 253.39 | 247.32
2019-07-25 20:00 | 252.36 | 246.43
2019-07-25 20:30 | 251.4 | 245.89
2019-07-25 21:00 | 248.71 | 243.35
2019-07-25 21:30 | 247.29 | 242.94
2019-07-25 22:00 | 245.82 | 241.46
2019-07-25 22:30 | 244.2 | 239.11
2019-07-25 23:00 | 242.52 | 237.3
2019-07-25 23:30 | 241.1 | 236.09
2019-07-26 | 238.49 | 234.23
2019-07-26 00:30 | 238.23 | 234.18
2019-07-26 01:00 | 236.61 | 233.04
2019-07-26 01:30 | 235.78 | 232.28
2019-07-26 02:00 | 235.86 | 232.3
2019-07-26 02:30 | 235.28 | 231.6
2019-07-26 03:00 | 235.39 | 231.72
2019-07-26 03:30 | 235.57 | 231.93
2019-07-26 04:00 | 235.64 | 231.93
2019-07-26 04:30 | 236.91 | 233.29
2019-07-26 05:00 | 238.2 | 234.66
2019-07-26 05:30 | 240.33 | 237.08
2019-07-26 06:00 | 243.53 | 240.07
2019-07-26 06:30 | 248.59 | 244.66
2019-07-26 07:00 | 244.25 | 240.76
2019-07-26 07:30 | 216.14 | 213.43
2019-07-26 08:00 | 214.99 | 212.53
2019-07-26 08:30 | 217.13 | 214.8
2019-07-26 09:00 | 237.26 | 234.3
2019-07-26 09:30 | 239.83 | 236.67
2019-07-26 10:00 | 235.49 | 232.43
2019-07-26 10:30 | 231.39 | 228.22
2019-07-26 11:00 | 228.61 | 225.43
2019-07-26 11:30 | 228.2 | 224.79
2019-07-26 12:00 | 227.73 | 224.14
2019-07-26 12:30 | 227.61 | 224.4
2019-07-26 13:00 | 228.61 | 225.07
2019-07-26 13:30 | 228.11 | 224.44
2019-07-26 14:00 | 228.09 | 224.61
2019-07-26 14:30 | 228.81 | 224.83
2019-07-26 15:00 | 229.03 | 224.47
2019-07-26 15:30 | 230.09 | 225.44
2019-07-26 16:00 | 231.7 | 226.74
2019-07-26 16:30 | 233.22 | 228.1
2019-07-26 17:00 | 232.95 | 227.48
2019-07-26 17:30 | 238.02 | 231.86
2019-07-26 18:00 | 240.44 | 234.31
2019-07-26 18:30 | 244.66 | 238.53
2019-07-26 19:00 | 245.81 | 239.77
2019-07-26 19:30 | 245.95 | 239.76
2019-07-26 20:00 | 244.88 | 238.84
2019-07-26 20:30 | 244.98 | 238.96
2019-07-26 21:00 | 244.36 | 238.25
2019-07-26 21:30 | 242.43 | 237.43
2019-07-26 22:00 | 240.92 | 236.1
2019-07-26 22:30 | 239.45 | 234.62
2019-07-26 23:00 | 239.15 | 233.73
2019-07-26 23:30 | 237.27 | 232.35
2019-07-27 | 235.35 | 231.39
2019-07-27 00:30 | 234.45 | 230.35
2019-07-27 01:00 | 233.15 | 229.51
2019-07-27 01:30 | 232.3 | 228.54
2019-07-27 02:00 | 231.95 | 228.19
2019-07-27 02:30 | 232.8 | 228.07
2019-07-27 03:00 | 234.5 | 228
2019-07-27 03:30 | 234.69 | 228.33
2019-07-27 04:00 | 234.11 | 228.35
2019-07-27 04:30 | 235.13 | 228.94
2019-07-27 05:00 | 236.33 | 229.83
2019-07-27 05:30 | 237.41 | 231.03
2019-07-27 06:00 | 238.83 | 232.32
2019-07-27 06:30 | 240.7 | 234
2019-07-27 07:00 | 242.98 | 236.83
2019-07-27 07:30 | 240.56 | 235.86
2019-07-27 08:00 | 240.67 | 236.38
2019-07-27 08:30 | 238.24 | 234.07
2019-07-27 09:00 | 234.56 | 230.54
2019-07-27 09:30 | 231.36 | 226.84
2019-07-27 10:00 | 227.57 | 223.3
2019-07-27 10:30 | 225.62 | 221.38
2019-07-27 11:00 | 226.44 | 221.95
2019-07-27 11:30 | 226.03 | 221.75
2019-07-27 12:00 | 225.11 | 220.7
2019-07-27 12:30 | 225.08 | 220.21
2019-07-27 13:00 | 224.48 | 219.84
2019-07-27 13:30 | 224.85 | 220.02
2019-07-27 14:00 | 225.1 | 220.32
2019-07-27 14:30 | 225.04 | 219.98
2019-07-27 15:00 | 225.75 | 220.59
2019-07-27 15:30 | 226.98 | 222.02
2019-07-27 16:00 | 229.59 | 224.33
2019-07-27 16:30 | 231.88 | 226.32
2019-07-27 17:00 | 234.83 | 229.16
2019-07-27 17:30 | 237.43 | 231.42
2019-07-27 18:00 | 240.42 | 233.43
2019-07-27 18:30 | 244.65 | 237.44
2019-07-27 19:00 | 244.46 | 238.74
2019-07-27 19:30 | 245.04 | 239.06
2019-07-27 20:00 | 244.48 | 238.11
2019-07-27 20:30 | 243.54 | 237.57
2019-07-27 21:00 | 243.04 | 236.85
2019-07-27 21:30 | 241.57 | 236.18
2019-07-27 22:00 | 240.65 | 235.27
2019-07-27 22:30 | 239.31 | 234.1
2019-07-27 23:00 | 237.85 | 232.67
2019-07-27 23:30 | 237.28 | 232.66
2019-07-28 | 234.45 | 230.79
2019-07-28 00:30 | 234.47 | 230.57
2019-07-28 01:00 | 233.41 | 229.48
2019-07-28 01:30 | 233.32 | 229.77
2019-07-28 02:00 | 232.7 | 229.2
2019-07-28 02:30 | 232.79 | 229.16
2019-07-28 03:00 | 233.13 | 229.58
2019-07-28 03:30 | 232.71 | 229.09
2019-07-28 04:00 | 232.89 | 229.35
2019-07-28 04:30 | 232.06 | 228.15
2019-07-28 05:00 | 232.32 | 228.34
2019-07-28 05:30 | 234.2 | 230.52
2019-07-28 06:00 | 235.36 | 231.72
2019-07-28 06:30 | 238 | 234.46
2019-07-28 07:00 | 239.15 | 235.74
2019-07-28 07:30 | 241.02 | 237.63
2019-07-28 08:00 | 242.24 | 239.1
2019-07-28 08:30 | 240.01 | 236.84
2019-07-28 09:00 | 237.38 | 234.23
2019-07-28 09:30 | 234.57 | 231.42
2019-07-28 10:00 | 232.94 | 229.47
2019-07-28 10:30 | 230.68 | 227.3
2019-07-28 11:00 | 229.12 | 225.33
2019-07-28 11:30 | 228.6 | 224.51
2019-07-28 12:00 | 227.77 | 223.6
2019-07-28 12:30 | 227.31 | 222.91
2019-07-28 13:00 | 226.32 | 222.02
2019-07-28 13:30 | 226.28 | 222.12
2019-07-28 14:00 | 226.18 | 221.83
2019-07-28 14:30 | 227.02 | 222.36
2019-07-28 15:00 | 228.27 | 223.25
2019-07-28 15:30 | 229.73 | 224.67
2019-07-28 16:00 | 231.3 | 226.4
2019-07-28 16:30 | 234.73 | 229.77
2019-07-28 17:00 | 237.5 | 232.8
2019-07-28 17:30 | 242.08 | 235.76
2019-07-28 18:00 | 246.17 | 239.74
2019-07-28 18:30 | 250.12 | 244.91
2019-07-28 19:00 | 251.21 | 246.23
2019-07-28 19:30 | 249.92 | 245.01
2019-07-28 20:00 | 248.85 | 244.09
2019-07-28 20:30 | 247.9 | 243.32
2019-07-28 21:00 | 246.53 | 241.92
2019-07-28 21:30 | 245.86 | 241.4
2019-07-28 22:00 | 245.52 | 240.32
2019-07-28 22:30 | 243.81 | 238.64
2019-07-28 23:00 | 242.3 | 237.35
2019-07-28 23:30 | 240.34 | 235.83
2019-07-29 | 238.64 | 234.52
2019-07-29 00:30 | 237.24 | 233.79
2019-07-29 01:00 | 236.82 | 233.35
2019-07-29 01:30 | 236.76 | 232.94
2019-07-29 02:00 | 237.03 | 233.14
2019-07-29 02:30 | 237.35 | 232.93
2019-07-29 03:00 | 238.05 | 233.4
2019-07-29 03:30 | 237.78 | 232.8
2019-07-29 04:00 | 238.61 | 233.19
2019-07-29 04:30 | 239.63 | 234.39
2019-07-29 05:00 | 241.35 | 236.42
2019-07-29 05:30 | 243.49 | 239.08
2019-07-29 06:00 | 246.17 | 242.3
2019-07-29 06:30 | 250.96 | 246.33
2019-07-29 07:00 | 237.68 | 233.53
2019-07-29 07:30 | 176.64 | 173.14
2019-07-29 08:00 | 170.17 | 166.85
2019-07-29 08:30 | 172.16 | 169.05
2019-07-29 09:00 | 190.64 | 186.72
2019-07-29 09:30 | 191.81 | 187.58
2019-07-29 10:00 | 188.85 | 184.6
2019-07-29 10:30 | 185.77 | 181.47
2019-07-29 11:00 | 185.62 | 181.18
2019-07-29 11:30 | 184.3 | 179.97
2019-07-29 12:00 | 182.84 | 178.46
2019-07-29 12:30 | 182.38 | 177.73
2019-07-29 13:00 | 181.61 | 177.03
2019-07-29 13:30 | 181.67 | 176.84
2019-07-29 14:00 | 182.23 | 177.44
2019-07-29 14:30 | 182.82 | 177.95
2019-07-29 15:00 | 183.07 | 178.31
2019-07-29 15:30 | 184.6 | 179.8
2019-07-29 16:00 | 186.34 | 181.11
2019-07-29 16:30 | 188.51 | 183.18
2019-07-29 17:00 | 191.08 | 185.71
2019-07-29 17:30 | 193.83 | 188.3
2019-07-29 18:00 | 197.83 | 191.9
2019-07-29 18:30 | 198.64 | 192.67
2019-07-29 19:00 | 212.32 | 206.32
2019-07-29 19:30 | 222.14 | 215.92
2019-07-29 20:00 | 221.32 | 214.96
2019-07-29 20:30 | 219.08 | 212.75
2019-07-29 21:00 | 217.33 | 212.27
2019-07-29 21:30 | 215.34 | 211.41
2019-07-29 22:00 | 213.23 | 209.46
2019-07-29 22:30 | 212.39 | 208.52
2019-07-29 23:00 | 210.53 | 206.56
2019-07-29 23:30 | 209.59 | 205.78
2019-07-30 | 208.02 | 204.12
2019-07-30 00:30 | 207.46 | 203.39
2019-07-30 01:00 | 206.36 | 202.24
2019-07-30 01:30 | 206.21 | 202.03
2019-07-30 02:00 | 205.92 | 201.84
2019-07-30 02:30 | 206.37 | 202.4
2019-07-30 03:00 | 206.88 | 202.65
2019-07-30 03:30 | 207.61 | 203.2
2019-07-30 04:00 | 207.86 | 203.48
2019-07-30 04:30 | 209.46 | 205.13
2019-07-30 05:00 | 210.76 | 206.47
2019-07-30 05:30 | 213.27 | 209.29
2019-07-30 06:00 | 215.71 | 212.12
2019-07-30 06:30 | 221.41 | 217.48
2019-07-30 07:00 | 225.86 | 221.87
2019-07-30 07:30 | 194.77 | 191.11
2019-07-30 08:00 | 182.32 | 178.95
2019-07-30 08:30 | 171.52 | 168.1
2019-07-30 09:00 | 171.58 | 168.42
2019-07-30 09:30 | 188.12 | 183.25
2019-07-30 10:00 | 204.76 | 199.52
2019-07-30 10:30 | 206.97 | 201.99
2019-07-30 11:00 | 226.4 | 221.66
2019-07-30 11:30 | 229.06 | 224.24
2019-07-30 12:00 | 228.13 | 223.41
2019-07-30 12:30 | 227.82 | 222.69
2019-07-30 13:00 | 227.47 | 222.11
2019-07-30 13:30 | 228.46 | 222.67
2019-07-30 14:00 | 228.75 | 223.2
2019-07-30 14:30 | 229.74 | 223.85
2019-07-30 15:00 | 229.98 | 224.05
2019-07-30 15:30 | 231.77 | 225.72
2019-07-30 16:00 | 214.37 | 208.72
2019-07-30 16:30 | 205.21 | 199.96
2019-07-30 17:00 | 206.76 | 201.91
2019-07-30 17:30 | 209.02 | 204.26
2019-07-30 18:00 | 212.78 | 208.15
2019-07-30 18:30 | 216.63 | 212.16
2019-07-30 19:00 | 216.14 | 211.88
2019-07-30 19:30 | 195.64 | 190.34
2019-07-30 20:00 | 183.23 | 177.1
2019-07-30 20:30 | 182.05 | 175.91
2019-07-30 21:00 | 180.48 | 174.04
2019-07-30 21:30 | 179.19 | 173.2
2019-07-30 22:00 | 177.85 | 171.8
2019-07-30 22:30 | 176.35 | 170.17
2019-07-30 23:00 | 174.36 | 168.1
2019-07-30 23:30 | 173.28 | 167.04
2019-07-31 | 172.06 | 165.77
2019-07-31 00:30 | 171.11 | 164.78
2019-07-31 01:00 | 170.07 | 163.54
2019-07-31 01:30 | 169.79 | 163.2
2019-07-31 02:00 | 168.62 | 162
2019-07-31 02:30 | 168.5 | 161.81
2019-07-31 03:00 | 168.55 | 161.82
2019-07-31 03:30 | 168.48 | 161.78
2019-07-31 04:00 | 168.71 | 162.07
2019-07-31 04:30 | 170.1 | 163.51
2019-07-31 05:00 | 171.59 | 165.15
2019-07-31 05:30 | 173.71 | 167.64
2019-07-31 06:00 | 168.68 | 163.52
2019-07-31 06:30 | 158.22 | 154.03
2019-07-31 07:00 | 156.45 | 152.21
2019-07-31 07:30 | 187.89 | 185.83
2019-07-31 08:00 | 188.88 | 186.88
2019-07-31 08:30 | 191.3 | 189.02
2019-07-31 09:00 | 187.19 | 184.13
2019-07-31 09:30 | 172.65 | 166.54
2019-07-31 10:00 | 173.48 | 167.4
2019-07-31 10:30 | 170.93 | 164.86
2019-07-31 11:00 | 169.24 | 163.28
2019-07-31 11:30 | 168.23 | 162.14
2019-07-31 12:00 | 167.95 | 161.61
2019-07-31 12:30 | 186.37 | 180.99
2019-07-31 13:00 | 194.21 | 188.77
2019-07-31 13:30 | 194.23 | 188.97
2019-07-31 14:00 | 194.81 | 190.2
2019-07-31 14:30 | 193.58 | 189.1
2019-07-31 15:00 | 194.26 | 189.59
2019-07-31 15:30 | 196.69 | 191.78
2019-07-31 16:00 | 198.43 | 193.48
2019-07-31 16:30 | 198.05 | 193.06
2019-07-31 17:00 | 200 | 194.88
2019-07-31 17:30 | 204.98 | 199.91
2019-07-31 18:00 | 195.58 | 190.2
2019-07-31 18:30 | 193.38 | 187.88
2019-07-31 19:00 | 194.76 | 189.23
2019-07-31 19:30 | 185.93 | 179.68
2019-07-31 20:00 | 184.25 | 177.8
2019-07-31 20:30 | 183.11 | 177.05
2019-07-31 21:00 | 181.72 | 175.8
2019-07-31 21:30 | 180.02 | 174.15
2019-07-31 22:00 | 177.91 | 171.63
2019-07-31 22:30 | 175.67 | 169.44
2019-07-31 23:00 | 173.98 | 167.4
2019-07-31 23:30 | 172.83 | 166.18
2019-08-01 | 171.36 | 164.71
2019-08-01 00:30 | 170.18 | 163.94
2019-08-01 01:00 | 168.98 | 162.73
2019-08-01 01:30 | 168.39 | 162.03
2019-08-01 02:00 | 168.37 | 161.95
2019-08-01 02:30 | 168.14 | 161.57
2019-08-01 03:00 | 168.36 | 161.73
2019-08-01 03:30 | 168.21 | 161.58
2019-08-01 04:00 | 168.62 | 162
2019-08-01 04:30 | 169.53 | 163.03
2019-08-01 05:00 | 170.85 | 164.55
2019-08-01 05:30 | 173.18 | 167.07
2019-08-01 06:00 | 176.22 | 169.96
2019-08-01 06:30 | 179.45 | 173.61
2019-08-01 07:00 | 183.18 | 177.55
2019-08-01 07:30 | 185.65 | 179.96
2019-08-01 08:00 | 184.99 | 179.28
2019-08-01 08:30 | 182.44 | 176.55
2019-08-01 09:00 | 178.4 | 172.26
2019-08-01 09:30 | 174.59 | 168.33
2019-08-01 10:00 | 171.9 | 165.61
2019-08-01 10:30 | 170.12 | 163.48
2019-08-01 11:00 | 164.59 | 158.01
2019-08-01 11:30 | 156.11 | 149.15
2019-08-01 12:00 | 155.14 | 147.55
2019-08-01 12:30 | 158.49 | 150.75
2019-08-01 13:00 | 160.27 | 153.44
2019-08-01 13:30 | 160.08 | 152.66
2019-08-01 14:00 | 161.6 | 154.53
2019-08-01 14:30 | 161.18 | 154.1
2019-08-01 15:00 | 162.26 | 155.1
2019-08-01 15:30 | 163.2 | 156.37
2019-08-01 16:00 | 162.57 | 156.26
2019-08-01 16:30 | 164.41 | 158.03
2019-08-01 17:00 | 166.48 | 160.29
2019-08-01 17:30 | 169.93 | 164.41
2019-08-01 18:00 | 174.58 | 169.18
2019-08-01 18:30 | 178.15 | 172.73
2019-08-01 19:00 | 180.33 | 175.08
2019-08-01 19:30 | 179.2 | 173.93
2019-08-01 20:00 | 177.07 | 171.84
2019-08-01 20:30 | 175.82 | 170.49
2019-08-01 21:00 | 173.95 | 168.67
2019-08-01 21:30 | 173.4 | 167.91
2019-08-01 22:00 | 172.09 | 166.51
2019-08-01 22:30 | 170.04 | 164.26
2019-08-01 23:00 | 168.47 | 162.04
2019-08-01 23:30 | 166.47 | 160.76
2019-08-02 | 165.54 | 159.52
2019-08-02 00:30 | 164.7 | 158.94
2019-08-02 01:00 | 163.18 | 157.37
2019-08-02 01:30 | 163.02 | 157.17
2019-08-02 02:00 | 162.54 | 156.94
2019-08-02 02:30 | 162.41 | 156.67
2019-08-02 03:00 | 162.6 | 156.75
2019-08-02 03:30 | 162.97 | 156.99
2019-08-02 04:00 | 163.48 | 157.53
2019-08-02 04:30 | 164.38 | 158.48
2019-08-02 05:00 | 165.75 | 159.96
2019-08-02 05:30 | 167.63 | 162.12
2019-08-02 06:00 | 170.92 | 165.15
2019-08-02 06:30 | 174.97 | 169.31
2019-08-02 07:00 | 179.12 | 173.02
2019-08-02 07:30 | 182.74 | 176.9
2019-08-02 08:00 | 180.3 | 175.15
2019-08-02 08:30 | 175.71 | 170.17
2019-08-02 09:00 | 171.75 | 165.44
2019-08-02 09:30 | 167.84 | 161.26
2019-08-02 10:00 | 165.01 | 158.04
2019-08-02 10:30 | 163.11 | 155.78
2019-08-02 11:00 | 160.86 | 153.22
2019-08-02 11:30 | 160.07 | 152.08
2019-08-02 12:00 | 159.78 | 151.93
2019-08-02 12:30 | 161.29 | 153.34
2019-08-02 13:00 | 160.45 | 152.14
2019-08-02 13:30 | 162.74 | 154.71
2019-08-02 14:00 | 166.77 | 158.88
2019-08-02 14:30 | 183.62 | 176.19
2019-08-02 15:00 | 172.48 | 164.87
2019-08-02 15:30 | 181.17 | 173.48
2019-08-02 16:00 | 213.08 | 205.56
2019-08-02 16:30 | 233.76 | 226.98
2019-08-02 17:00 | 237.12 | 230.62
2019-08-02 17:30 | 239.36 | 232.74
2019-08-02 18:00 | 229.13 | 223.83
2019-08-02 18:30 | 223.06 | 218.28
2019-08-02 19:00 | 222.27 | 217.37
2019-08-02 19:30 | 223.01 | 218.28
2019-08-02 20:00 | 239.56 | 233.91
2019-08-02 20:30 | 244.91 | 238.72
2019-08-02 21:00 | 243.64 | 237.39
2019-08-02 21:30 | 242.98 | 237.47
2019-08-02 22:00 | 241.53 | 235.93
2019-08-02 22:30 | 239.34 | 233.99
2019-08-02 23:00 | 238.87 | 232.99
2019-08-02 23:30 | 237.95 | 231.76
2019-08-03 | 237 | 230.85
2019-08-03 00:30 | 235.54 | 229.89
2019-08-03 01:00 | 234.45 | 229.3
2019-08-03 01:30 | 233.78 | 228.58
2019-08-03 02:00 | 232.98 | 228.11
2019-08-03 02:30 | 232.6 | 227.75
2019-08-03 03:00 | 232.64 | 227.68
2019-08-03 03:30 | 232.77 | 227.82
2019-08-03 04:00 | 232.51 | 227.78
2019-08-03 04:30 | 233.47 | 228.76
2019-08-03 05:00 | 234.52 | 229.49
2019-08-03 05:30 | 235.88 | 230.95
2019-08-03 06:00 | 237.93 | 233.2
2019-08-03 06:30 | 240.06 | 235.2
2019-08-03 07:00 | 242.03 | 237.55
2019-08-03 07:30 | 243.18 | 239.04
2019-08-03 08:00 | 242.99 | 238.74
2019-08-03 08:30 | 240.33 | 236.18
2019-08-03 09:00 | 238.42 | 233.11
2019-08-03 09:30 | 236.17 | 230.49
2019-08-03 10:00 | 233.18 | 227.34
2019-08-03 10:30 | 229.78 | 225.51
2019-08-03 11:00 | 228.63 | 224.15
2019-08-03 11:30 | 227.7 | 223.3
2019-08-03 12:00 | 227.4 | 222.56
2019-08-03 12:30 | 226.08 | 221.45
2019-08-03 13:00 | 225.3 | 220.39
2019-08-03 13:30 | 225.44 | 220.17
2019-08-03 14:00 | 226.84 | 221.46
2019-08-03 14:30 | 227.34 | 221.24
2019-08-03 15:00 | 228.45 | 222.1
2019-08-03 15:30 | 229.93 | 223.46
2019-08-03 16:00 | 232.22 | 225.96
2019-08-03 16:30 | 233.67 | 227.83
2019-08-03 17:00 | 235.4 | 229.93
2019-08-03 17:30 | 238.59 | 232.91
2019-08-03 18:00 | 243.08 | 237.06
2019-08-03 18:30 | 245.96 | 239.82
2019-08-03 19:00 | 246.8 | 240.79
2019-08-03 19:30 | 245.95 | 239.86
2019-08-03 20:00 | 245.27 | 239.21
2019-08-03 20:30 | 244.59 | 238.6
2019-08-03 21:00 | 243.15 | 236.99
2019-08-03 21:30 | 243.63 | 237.42
2019-08-03 22:00 | 242.46 | 236.04
2019-08-03 22:30 | 241 | 234.62
2019-08-03 23:00 | 239.51 | 233.11
2019-08-03 23:30 | 238.83 | 232.81
2019-08-04 | 236.37 | 231.13
2019-08-04 00:30 | 235.06 | 230.54
2019-08-04 01:00 | 234.34 | 230.03
2019-08-04 01:30 | 233.15 | 228.85
2019-08-04 02:00 | 233.14 | 228.74
2019-08-04 02:30 | 233.17 | 228.49
2019-08-04 03:00 | 233.65 | 228.74
2019-08-04 03:30 | 233.11 | 228.23
2019-08-04 04:00 | 233.91 | 229.18
2019-08-04 04:30 | 236.9 | 232.54
2019-08-04 05:00 | 238.54 | 234.33
2019-08-04 05:30 | 238.93 | 234.8
2019-08-04 06:00 | 240.5 | 236.61
2019-08-04 06:30 | 242.11 | 238.33
2019-08-04 07:00 | 244.25 | 239.89
2019-08-04 07:30 | 245.25 | 241.73
2019-08-04 08:00 | 244.65 | 241.26
2019-08-04 08:30 | 243.24 | 239.78
2019-08-04 09:00 | 241.26 | 237.46
2019-08-04 09:30 | 238.72 | 234.37
2019-08-04 10:00 | 235.63 | 231.32
2019-08-04 10:30 | 232.82 | 228.71
2019-08-04 11:00 | 230.18 | 226.06
2019-08-04 11:30 | 229.13 | 225.27
2019-08-04 12:00 | 229.27 | 223.86
2019-08-04 12:30 | 229.56 | 223.74
2019-08-04 13:00 | 229.53 | 223.61
2019-08-04 13:30 | 229.18 | 223.24
2019-08-04 14:00 | 229.42 | 223.35
2019-08-04 14:30 | 230.05 | 224.2
2019-08-04 15:00 | 231.35 | 224.34
2019-08-04 15:30 | 233.77 | 226.11
2019-08-04 16:00 | 233.69 | 227.38
2019-08-04 16:30 | 236.17 | 229.86
2019-08-04 17:00 | 238.49 | 232.38
2019-08-04 17:30 | 243.32 | 236.28
2019-08-04 18:00 | 247.39 | 241.04
2019-08-04 18:30 | 250.62 | 245.21
2019-08-04 19:00 | 251.77 | 246.55
2019-08-04 19:30 | 251.11 | 246.5
2019-08-04 20:00 | 250.72 | 246.11
2019-08-04 20:30 | 250.2 | 245.66
2019-08-04 21:00 | 249.53 | 244.96
2019-08-04 21:30 | 248.66 | 244.56
2019-08-04 22:00 | 247.95 | 243.81
2019-08-04 22:30 | 246.12 | 242.04
2019-08-04 23:00 | 243.53 | 239.51
2019-08-04 23:30 | 242.5 | 238.6
2019-08-05 | 241.44 | 237.26
2019-08-05 00:30 | 240.58 | 236.57
2019-08-05 01:00 | 239.87 | 236.01
2019-08-05 01:30 | 239.28 | 235.44
2019-08-05 02:00 | 238.05 | 234.46
2019-08-05 02:30 | 237.32 | 233.68
2019-08-05 03:00 | 237.57 | 233.77
2019-08-05 03:30 | 237.77 | 233.88
2019-08-05 04:00 | 238.31 | 234.43
2019-08-05 04:30 | 239.65 | 235.87
2019-08-05 05:00 | 241.36 | 237.66
2019-08-05 05:30 | 243.49 | 239.95
2019-08-05 06:00 | 246.87 | 243.45
2019-08-05 06:30 | 252.16 | 248.32
2019-08-05 07:00 | 257.38 | 253.39
2019-08-05 07:30 | 259.82 | 256.23
2019-08-05 08:00 | 258.13 | 254.7
2019-08-05 08:30 | 253.39 | 249.71
2019-08-05 09:00 | 248.53 | 244.69
2019-08-05 09:30 | 245.18 | 240.24
2019-08-05 10:00 | 243.07 | 236.98
2019-08-05 10:30 | 239.49 | 233.51
2019-08-05 11:00 | 236.83 | 230.85
2019-08-05 11:30 | 235.29 | 229.58
2019-08-05 12:00 | 235.79 | 230.61
2019-08-05 12:30 | 235.41 | 230.08
2019-08-05 13:00 | 235.75 | 230.05
2019-08-05 13:30 | 236.09 | 230.55
2019-08-05 14:00 | 236.42 | 231.03
2019-08-05 14:30 | 236.57 | 231
2019-08-05 15:00 | 236.12 | 230.61
2019-08-05 15:30 | 238.09 | 232.74
2019-08-05 16:00 | 239.58 | 234.22
2019-08-05 16:30 | 243.23 | 235.47
2019-08-05 17:00 | 245.5 | 237.73
2019-08-05 17:30 | 247.38 | 239.76
2019-08-05 18:00 | 242.38 | 235.04
2019-08-05 18:30 | 226.55 | 219.56
2019-08-05 19:00 | 224.42 | 217.26
2019-08-05 19:30 | 224.3 | 217.19
2019-08-05 20:00 | 225.29 | 218.39
2019-08-05 20:30 | 225.96 | 218.99
2019-08-05 21:00 | 226.96 | 220.49
2019-08-05 21:30 | 246.52 | 240.75
2019-08-05 22:00 | 251.77 | 246.05
2019-08-05 22:30 | 249.39 | 243.69
2019-08-05 23:00 | 247.77 | 241.62
2019-08-05 23:30 | 247.2 | 240.91
2019-08-06 | 244.88 | 238.36
2019-08-06 00:30 | 244.25 | 237.97
2019-08-06 01:00 | 243.02 | 237.12
2019-08-06 01:30 | 242.17 | 236.56
2019-08-06 02:00 | 241.77 | 236.03
2019-08-06 02:30 | 242.37 | 235.71
2019-08-06 03:00 | 243 | 236.04
2019-08-06 03:30 | 243 | 235.9
2019-08-06 04:00 | 243.67 | 236.5
2019-08-06 04:30 | 245.05 | 237.97
2019-08-06 05:00 | 246.25 | 239.4
2019-08-06 05:30 | 248.89 | 242.07
2019-08-06 06:00 | 250.59 | 243.88
2019-08-06 06:30 | 255.82 | 248.96
2019-08-06 07:00 | 259.55 | 252.72
2019-08-06 07:30 | 262.32 | 255.02
2019-08-06 08:00 | 260.67 | 253.7
2019-08-06 08:30 | 255.92 | 248.6
2019-08-06 09:00 | 250.87 | 243.52
2019-08-06 09:30 | 246.64 | 239.41
2019-08-06 10:00 | 243.04 | 235.65
2019-08-06 10:30 | 240.84 | 232.83
2019-08-06 11:00 | 240.76 | 232.44
2019-08-06 11:30 | 240.17 | 231.81
2019-08-06 12:00 | 240.35 | 232.02
2019-08-06 12:30 | 241.76 | 232.92
2019-08-06 13:00 | 240.76 | 231.66
2019-08-06 13:30 | 239.91 | 230.81
2019-08-06 14:00 | 240.96 | 231.5
2019-08-06 14:30 | 240.83 | 231.43
2019-08-06 15:00 | 241.12 | 231.53
2019-08-06 15:30 | 241.68 | 231.52
2019-08-06 16:00 | 243.66 | 233.96
2019-08-06 16:30 | 244.45 | 235.09
2019-08-06 17:00 | 246.2 | 237.07
2019-08-06 17:30 | 234.83 | 226.74
2019-08-06 18:00 | 231.9 | 223.78
2019-08-06 18:30 | 229.41 | 221.04
2019-08-06 19:00 | 228.74 | 220.35
2019-08-06 19:30 | 229.37 | 221.19
2019-08-06 20:00 | 230.29 | 222.44
2019-08-06 20:30 | 230.55 | 222.81
2019-08-06 21:00 | 248.35 | 239.34
2019-08-06 21:30 | 252.21 | 244.28
2019-08-06 22:00 | 250.65 | 242.58
2019-08-06 22:30 | 248.74 | 240.9
2019-08-06 23:00 | 246.55 | 238.4
2019-08-06 23:30 | 245.72 | 237.61
2019-08-07 | 244.39 | 235.83
2019-08-07 00:30 | 242.7 | 235.21
2019-08-07 01:00 | 241.21 | 234.23
2019-08-07 01:30 | 239.96 | 233.25
2019-08-07 02:00 | 239.71 | 233.22
2019-08-07 02:30 | 239.62 | 232.87
2019-08-07 03:00 | 239.52 | 232.76
2019-08-07 03:30 | 239.1 | 232.4
2019-08-07 04:00 | 239.55 | 232.63
2019-08-07 04:30 | 240.16 | 233.15
2019-08-07 05:00 | 241.39 | 234.37
2019-08-07 05:30 | 243.06 | 236.34
2019-08-07 06:00 | 245.6 | 238.63
2019-08-07 06:30 | 248.07 | 241.89
2019-08-07 07:00 | 252.56 | 245.64
2019-08-07 07:30 | 232.13 | 225.9
2019-08-07 08:00 | 223.41 | 216.99
2019-08-07 08:30 | 222.89 | 218.83
2019-08-07 09:00 | 224.14 | 220.46
2019-08-07 09:30 | 239.59 | 234.19
2019-08-07 10:00 | 243.26 | 237.05
2019-08-07 10:30 | 240.2 | 234.05
2019-08-07 11:00 | 238.63 | 232.57
2019-08-07 11:30 | 239.82 | 233.82
2019-08-07 12:00 | 238.2 | 232.46
2019-08-07 12:30 | 237.77 | 231.43
2019-08-07 13:00 | 238.55 | 232.49
2019-08-07 13:30 | 239.31 | 233.13
2019-08-07 14:00 | 240.03 | 233.71
2019-08-07 14:30 | 239.57 | 233.54
2019-08-07 15:00 | 239.05 | 232.95
2019-08-07 15:30 | 239.05 | 233.04
2019-08-07 16:00 | 239.73 | 233.05
2019-08-07 16:30 | 241.75 | 235.44
2019-08-07 17:00 | 243.17 | 236.93
2019-08-07 17:30 | 229.17 | 224.54
2019-08-07 18:00 | 226.46 | 221.67
2019-08-07 18:30 | 225.26 | 219.99
2019-08-07 19:00 | 224.06 | 218.57
2019-08-07 19:30 | 225.03 | 219.66
2019-08-07 20:00 | 225.73 | 220.56
2019-08-07 20:30 | 226.08 | 220.99
2019-08-07 21:00 | 227 | 221.96
2019-08-07 21:30 | 226.33 | 222.36
2019-08-07 22:00 | 237.97 | 233.12
2019-08-07 22:30 | 242.1 | 236.85
2019-08-07 23:00 | 240.83 | 235.33
2019-08-07 23:30 | 239.91 | 234.2
2019-08-08 | 238.07 | 232.35
2019-08-08 00:30 | 236.77 | 231.39
2019-08-08 01:00 | 235.52 | 230.67
2019-08-08 01:30 | 234.93 | 230.22
2019-08-08 02:00 | 234.23 | 229.66
2019-08-08 02:30 | 234.09 | 229.5
2019-08-08 03:00 | 233.75 | 229.15
2019-08-08 03:30 | 234.28 | 229.79
2019-08-08 04:00 | 234.4 | 229.76
2019-08-08 04:30 | 235.5 | 230.74
2019-08-08 05:00 | 236.49 | 231.72
2019-08-08 05:30 | 238.77 | 234.16
2019-08-08 06:00 | 241.88 | 237.01
2019-08-08 06:30 | 245.81 | 241.04
2019-08-08 07:00 | 249.43 | 244.34
2019-08-08 07:30 | 245.47 | 240.29
2019-08-08 08:00 | 222.19 | 218.41
2019-08-08 08:30 | 224.18 | 220.55
2019-08-08 09:00 | 224.4 | 220.83
2019-08-08 09:30 | 230.48 | 226.25
2019-08-08 10:00 | 235.5 | 230.53
2019-08-08 10:30 | 233.74 | 228.96
2019-08-08 11:00 | 231.45 | 226.68
2019-08-08 11:30 | 231.6 | 226.69
2019-08-08 12:00 | 231.05 | 226.07
2019-08-08 12:30 | 231.63 | 226.04
2019-08-08 13:00 | 231.36 | 225.51
2019-08-08 13:30 | 232.16 | 226.22
2019-08-08 14:00 | 232.17 | 226.52
2019-08-08 14:30 | 233.24 | 227.54
2019-08-08 15:00 | 233.51 | 227.97
2019-08-08 15:30 | 235.12 | 229.36
2019-08-08 16:00 | 236.21 | 230.3
2019-08-08 16:30 | 236.9 | 231.26
2019-08-08 17:00 | 236.93 | 231.48
2019-08-08 17:30 | 239.51 | 232.08
2019-08-08 18:00 | 244.67 | 234.34
2019-08-08 18:30 | 245.38 | 235.99
2019-08-08 19:00 | 245.7 | 237.09
2019-08-08 19:30 | 244.43 | 235.6
2019-08-08 20:00 | 243.18 | 234.08
2019-08-08 20:30 | 242.56 | 233.33
2019-08-08 21:00 | 242.65 | 233.93
2019-08-08 21:30 | 241.95 | 235.31
2019-08-08 22:00 | 240.85 | 234.47
2019-08-08 22:30 | 239.49 | 233.46
2019-08-08 23:00 | 237.92 | 232.06
2019-08-08 23:30 | 238.99 | 233.7
2019-08-09 | 237.45 | 232.17
2019-08-09 00:30 | 236.41 | 231.03
2019-08-09 01:00 | 236.61 | 230.36
2019-08-09 01:30 | 236.11 | 229.99
2019-08-09 02:00 | 235.5 | 229.85
2019-08-09 02:30 | 235.34 | 229.68
2019-08-09 03:00 | 235.89 | 230.11
2019-08-09 03:30 | 236.08 | 230.17
2019-08-09 04:00 | 236.59 | 230.73
2019-08-09 04:30 | 237.86 | 232.25
2019-08-09 05:00 | 238.8 | 233.15
2019-08-09 05:30 | 241.12 | 235.55
2019-08-09 06:00 | 244.82 | 238.97
2019-08-09 06:30 | 249.82 | 243.56
2019-08-09 07:00 | 254.41 | 247.5
2019-08-09 07:30 | 252.81 | 246.27
2019-08-09 08:00 | 254.38 | 248.11
2019-08-09 08:30 | 248.74 | 243.89
2019-08-09 09:00 | 242.53 | 238.98
2019-08-09 09:30 | 237.95 | 234.93
2019-08-09 10:00 | 235.61 | 232.32
2019-08-09 10:30 | 233.39 | 229.72
2019-08-09 11:00 | 231.34 | 227.62
2019-08-09 11:30 | 230.04 | 226.11
2019-08-09 12:00 | 229.29 | 225.4
2019-08-09 12:30 | 227.89 | 223.68
2019-08-09 13:00 | 226.97 | 222.61
2019-08-09 13:30 | 227.74 | 223.84
2019-08-09 14:00 | 227.47 | 223.6
2019-08-09 14:30 | 227.98 | 223.99
2019-08-09 15:00 | 229.47 | 225
2019-08-09 15:30 | 232.18 | 227.42
2019-08-09 16:00 | 233.9 | 228.41
2019-08-09 16:30 | 236.05 | 230.73
2019-08-09 17:00 | 238.4 | 233.29
2019-08-09 17:30 | 241.45 | 236.17
2019-08-09 18:00 | 245.3 | 239.98
2019-08-09 18:30 | 248.73 | 243.61
2019-08-09 19:00 | 250.44 | 245.26
2019-08-09 19:30 | 250.03 | 244.63
2019-08-09 20:00 | 249.24 | 243.79
2019-08-09 20:30 | 247.71 | 242.35
2019-08-09 21:00 | 247.05 | 241.54
2019-08-09 21:30 | 247.1 | 241.44
2019-08-09 22:00 | 245.58 | 240.27
2019-08-09 22:30 | 243.94 | 238.66
2019-08-09 23:00 | 242.2 | 237.22
2019-08-09 23:30 | 239.98 | 235.69
2019-08-10 | 238.41 | 234.39
2019-08-10 00:30 | 237.45 | 233.75
2019-08-10 01:00 | 236.36 | 232.69
2019-08-10 01:30 | 235.53 | 231.99
2019-08-10 02:00 | 236.02 | 231.35
2019-08-10 02:30 | 236.07 | 231.18
2019-08-10 03:00 | 235.67 | 230.85
2019-08-10 03:30 | 235.76 | 230.9
2019-08-10 04:00 | 235.96 | 230.78
2019-08-10 04:30 | 236.62 | 231.19
2019-08-10 05:00 | 237.72 | 232.3
2019-08-10 05:30 | 238.75 | 233.41
2019-08-10 06:00 | 240.08 | 234.94
2019-08-10 06:30 | 242.35 | 237.29
2019-08-10 07:00 | 243.95 | 239.21
2019-08-10 07:30 | 245.14 | 241.17
2019-08-10 08:00 | 244.13 | 240.08
2019-08-10 08:30 | 242.53 | 237.91
2019-08-10 09:00 | 240.17 | 235.66
2019-08-10 09:30 | 202.55 | 197.48
2019-08-10 10:00 | 171.49 | 166.12
2019-08-10 10:30 | 170.61 | 165.94
2019-08-10 11:00 | 168.9 | 163.83
2019-08-10 11:30 | 167.62 | 163.33
2019-08-10 12:00 | 166.48 | 162.55
2019-08-10 12:30 | 165.67 | 161.52
2019-08-10 13:00 | 164.07 | 159.82
2019-08-10 13:30 | 163.15 | 158.79
2019-08-10 14:00 | 163.44 | 159.05
2019-08-10 14:30 | 164.67 | 159.81
2019-08-10 15:00 | 198.53 | 193.47
2019-08-10 15:30 | 228.56 | 222.03
2019-08-10 16:00 | 236.87 | 228.87
2019-08-10 16:30 | 239 | 231.04
2019-08-10 17:00 | 241.57 | 233.99
2019-08-10 17:30 | 245.58 | 237.76
2019-08-10 18:00 | 250.53 | 242.03
2019-08-10 18:30 | 253.43 | 244.93
2019-08-10 19:00 | 254.66 | 246.35
2019-08-10 19:30 | 254.23 | 245.9
2019-08-10 20:00 | 253.5 | 245.2
2019-08-10 20:30 | 253.08 | 244.93
2019-08-10 21:00 | 251.47 | 243.5
2019-08-10 21:30 | 250.57 | 243.35
2019-08-10 22:00 | 248.96 | 241.93
2019-08-10 22:30 | 246.56 | 239.81
2019-08-10 23:00 | 243.6 | 237.7
2019-08-10 23:30 | 242.6 | 237.17
2019-08-11 | 240.92 | 235.83
2019-08-11 00:30 | 241.14 | 235.58
2019-08-11 01:00 | 239.54 | 234.35
2019-08-11 01:30 | 239.12 | 234.06
2019-08-11 02:00 | 238.58 | 233.24
2019-08-11 02:30 | 238.18 | 232.74
2019-08-11 03:00 | 237.98 | 232.86
2019-08-11 03:30 | 238.05 | 232.73
2019-08-11 04:00 | 238.34 | 232.86
2019-08-11 04:30 | 239.41 | 233.96
2019-08-11 05:00 | 240.27 | 234.93
2019-08-11 05:30 | 241.24 | 235.93
2019-08-11 06:00 | 242.6 | 237.27
2019-08-11 06:30 | 244.07 | 239.16
2019-08-11 07:00 | 245.37 | 240.97
2019-08-11 07:30 | 247.1 | 243.02
2019-08-11 08:00 | 248.18 | 243.55
2019-08-11 08:30 | 247.36 | 240.99
2019-08-11 09:00 | 245.27 | 238.24
2019-08-11 09:30 | 242.73 | 235.7
2019-08-11 10:00 | 203.26 | 196.98
2019-08-11 10:30 | 172.72 | 166.29
2019-08-11 11:00 | 169.48 | 163.58
2019-08-11 11:30 | 168.12 | 162.12
2019-08-11 12:00 | 167.37 | 161.93
2019-08-11 12:30 | 166.45 | 160.23
2019-08-11 13:00 | 166.53 | 160.4
2019-08-11 13:30 | 166.15 | 160.12
2019-08-11 14:00 | 166.45 | 160.82
2019-08-11 14:30 | 167.47 | 160.87
2019-08-11 15:00 | 167.77 | 161.58
2019-08-11 15:30 | 169.67 | 163.03
2019-08-11 16:00 | 202.55 | 196.15
2019-08-11 16:30 | 233.25 | 226.11
2019-08-11 17:00 | 241.93 | 234.65
2019-08-11 17:30 | 247.22 | 239.42
2019-08-11 18:00 | 253.81 | 245.21
2019-08-11 18:30 | 256.8 | 250.38
2019-08-11 19:00 | 258.3 | 251.79
2019-08-11 19:30 | 257.73 | 251.16
2019-08-11 20:00 | 256.04 | 249.51
2019-08-11 20:30 | 255.36 | 248.78
2019-08-11 21:00 | 253.72 | 247.08
2019-08-11 21:30 | 252.19 | 245.88
2019-08-11 22:00 | 250.46 | 243.77
2019-08-11 22:30 | 247.71 | 241.24
2019-08-11 23:00 | 246.43 | 239.82
2019-08-11 23:30 | 244.02 | 237.96
2019-08-12 | 242.13 | 236.57
2019-08-12 00:30 | 241.55 | 236.38
2019-08-12 01:00 | 240.52 | 235.51
2019-08-12 01:30 | 240.19 | 235.12
2019-08-12 02:00 | 241.19 | 236.12
2019-08-12 02:30 | 240.67 | 235.67
2019-08-12 03:00 | 240.94 | 235.89
2019-08-12 03:30 | 241.41 | 236.33
2019-08-12 04:00 | 241.63 | 236.64
2019-08-12 04:30 | 242.72 | 237.86
2019-08-12 05:00 | 244.33 | 239.57
2019-08-12 05:30 | 246.18 | 241.68
2019-08-12 06:00 | 248.57 | 244.28
2019-08-12 06:30 | 252.01 | 248
2019-08-12 07:00 | 253.3 | 249.04
2019-08-12 07:30 | 256.1 | 251.36
2019-08-12 08:00 | 252.63 | 248.62
2019-08-12 08:30 | 239.41 | 235.07
2019-08-12 09:00 | 223.93 | 219.15
2019-08-12 09:30 | 219.81 | 215.42
2019-08-12 10:00 | 216.82 | 212.22
2019-08-12 10:30 | 216.62 | 210.91
2019-08-12 11:00 | 215.88 | 210.13
2019-08-12 11:30 | 214.02 | 208.51
2019-08-12 12:00 | 212.14 | 206.98
2019-08-12 12:30 | 210.69 | 205.43
2019-08-12 13:00 | 209.37 | 204.16
2019-08-12 13:30 | 209.02 | 203.71
2019-08-12 14:00 | 207.53 | 201.98
2019-08-12 14:30 | 208.88 | 203.37
2019-08-12 15:00 | 208.4 | 203.11
2019-08-12 15:30 | 210.45 | 204.22
2019-08-12 16:00 | 214.25 | 207.63
2019-08-12 16:30 | 217.47 | 210.47
2019-08-12 17:00 | 220.48 | 214.16
2019-08-12 17:30 | 225.25 | 219.13
2019-08-12 18:00 | 230.44 | 224.26
2019-08-12 18:30 | 231.45 | 225.74
2019-08-12 19:00 | 238.94 | 233.69
2019-08-12 19:30 | 212.44 | 207.32
2019-08-12 20:00 | 148.38 | 143.7
2019-08-12 20:30 | 147.03 | 142.41
2019-08-12 21:00 | 148.08 | 143.37
2019-08-12 21:30 | 148.61 | 144.09
2019-08-12 22:00 | 173.47 | 167.38
2019-08-12 22:30 | 178.26 | 171.76
2019-08-12 23:00 | 176.21 | 169.59
2019-08-12 23:30 | 174.88 | 168.42
2019-08-13 | 173.27 | 166.73
2019-08-13 00:30 | 172.65 | 166.15
2019-08-13 01:00 | 171.05 | 164.98
2019-08-13 01:30 | 170.38 | 164.62
2019-08-13 02:00 | 169.9 | 164.28
2019-08-13 02:30 | 168.34 | 162.64
2019-08-13 03:00 | 169.06 | 163.45
2019-08-13 03:30 | 169.15 | 163.71
2019-08-13 04:00 | 170.48 | 165
2019-08-13 04:30 | 172.47 | 166.87
2019-08-13 05:00 | 174.54 | 169.06
2019-08-13 05:30 | 177.28 | 171.35
2019-08-13 06:00 | 181.25 | 175.23
2019-08-13 06:30 | 185.19 | 180.14
2019-08-13 07:00 | 189.95 | 185.32
2019-08-13 07:30 | 190.86 | 186.96
2019-08-13 08:00 | 187.87 | 183.95
2019-08-13 08:30 | 182.84 | 178.49
2019-08-13 09:00 | 176.37 | 171.65
2019-08-13 09:30 | 170.49 | 165.25
2019-08-13 10:00 | 167.04 | 161.59
2019-08-13 10:30 | 164.43 | 158.31
2019-08-13 11:00 | 163.29 | 157.01
2019-08-13 11:30 | 161.83 | 155.44
2019-08-13 12:00 | 161.23 | 154.75
2019-08-13 12:30 | 160.93 | 153.97
2019-08-13 13:00 | 161.88 | 154.79
2019-08-13 13:30 | 164.23 | 157
2019-08-13 14:00 | 157.89 | 150.97
2019-08-13 14:30 | 169.34 | 163.92
2019-08-13 15:00 | 188.32 | 183.94
2019-08-13 15:30 | 194.43 | 190.35
2019-08-13 16:00 | 198.32 | 194.06
2019-08-13 16:30 | 202.58 | 198.01
2019-08-13 17:00 | 205.55 | 201
2019-08-13 17:30 | 195.54 | 191.47
2019-08-13 18:00 | 189.67 | 185.94
2019-08-13 18:30 | 175.34 | 170.86
2019-08-13 19:00 | 159.04 | 152.74
2019-08-13 19:30 | 168.94 | 162.65
2019-08-13 20:00 | 169.71 | 163.39
2019-08-13 20:30 | 170.64 | 164.35
2019-08-13 21:00 | 171.71 | 165.4
2019-08-13 21:30 | 172.42 | 166.44
2019-08-13 22:00 | 176.08 | 170.7
2019-08-13 22:30 | 195.25 | 188.54
2019-08-13 23:00 | 198.89 | 191.7
2019-08-13 23:30 | 197.52 | 190.68
2019-08-14 | 195.31 | 188.95
2019-08-14 00:30 | 194.82 | 189.03
2019-08-14 01:00 | 193.38 | 187.84
2019-08-14 01:30 | 192.82 | 187.47
2019-08-14 02:00 | 191.72 | 186.26
2019-08-14 02:30 | 191.64 | 185.99
2019-08-14 03:00 | 192.03 | 186.47
2019-08-14 03:30 | 192.01 | 186.46
2019-08-14 04:00 | 192.58 | 186.99
2019-08-14 04:30 | 193.66 | 188.04
2019-08-14 05:00 | 196.02 | 190.56
2019-08-14 05:30 | 199.22 | 193.98
2019-08-14 06:00 | 202.45 | 197.39
2019-08-14 06:30 | 205.94 | 201.58
2019-08-14 07:00 | 211.37 | 206.52
2019-08-14 07:30 | 213.1 | 208.49
2019-08-14 08:00 | 210.53 | 205.68
2019-08-14 08:30 | 205.46 | 199.94
2019-08-14 09:00 | 199.35 | 193.59
2019-08-14 09:30 | 190.6 | 184.43
2019-08-14 10:00 | 174.67 | 168.48
2019-08-14 10:30 | 172.61 | 166.42
2019-08-14 11:00 | 171.48 | 165.24
2019-08-14 11:30 | 170.07 | 163.96
2019-08-14 12:00 | 168.74 | 162.92
2019-08-14 12:30 | 166.55 | 160.69
2019-08-14 13:00 | 146.91 | 140.46
2019-08-14 13:30 | 169.67 | 162.76
2019-08-14 14:00 | 181.93 | 174.99
2019-08-14 14:30 | 182.95 | 176.04
2019-08-14 15:00 | 183.45 | 176.48
2019-08-14 15:30 | 173.55 | 167.47
2019-08-14 16:00 | 162.87 | 156.49
2019-08-14 16:30 | 165.36 | 158.8
2019-08-14 17:00 | 168.07 | 161.06
2019-08-14 17:30 | 166.53 | 160.12
2019-08-14 18:00 | 194.24 | 188.6
2019-08-14 18:30 | 209.15 | 203.31
2019-08-14 19:00 | 223.48 | 217.37
2019-08-14 19:30 | 226.49 | 220.57
2019-08-14 20:00 | 227.28 | 221.45
2019-08-14 20:30 | 227.14 | 221.33
2019-08-14 21:00 | 227.74 | 221.8
2019-08-14 21:30 | 226.51 | 222.17
2019-08-14 22:00 | 244.64 | 239.68
2019-08-14 22:30 | 248.1 | 243.3
2019-08-14 23:00 | 245.72 | 241.66
2019-08-14 23:30 | 244.86 | 240.57
2019-08-15 | 242.78 | 239.25
2019-08-15 00:30 | 242.54 | 238.5
2019-08-15 01:00 | 241.45 | 237.49
2019-08-15 01:30 | 240.56 | 236.67
2019-08-15 02:00 | 240.44 | 236.43
2019-08-15 02:30 | 241.7 | 236.63
2019-08-15 03:00 | 241.2 | 236.16
2019-08-15 03:30 | 240.8 | 235.64
2019-08-15 04:00 | 241.92 | 236.7
2019-08-15 04:30 | 243.02 | 237.93
2019-08-15 05:00 | 244.93 | 240.11
2019-08-15 05:30 | 245.76 | 241.04
2019-08-15 06:00 | 248.27 | 243.65
2019-08-15 06:30 | 253.51 | 248.32
2019-08-15 07:00 | 250.48 | 245.12
2019-08-15 07:30 | 219.9 | 215.74
2019-08-15 08:00 | 220.67 | 216.91
2019-08-15 08:30 | 223.23 | 219.41
2019-08-15 09:00 | 226.82 | 222.93
2019-08-15 09:30 | 240.99 | 237.66
2019-08-15 10:00 | 240.72 | 235.42
2019-08-15 10:30 | 235.77 | 229.9
2019-08-15 11:00 | 235.02 | 228.82
2019-08-15 11:30 | 235.26 | 228.84
2019-08-15 12:00 | 235.64 | 228.91
2019-08-15 12:30 | 236.24 | 229.8
2019-08-15 13:00 | 238.38 | 231.94
2019-08-15 13:30 | 238.23 | 231.59
2019-08-15 14:00 | 239.21 | 232.4
2019-08-15 14:30 | 239.34 | 232.51
2019-08-15 15:00 | 240.28 | 232.81
2019-08-15 15:30 | 240.86 | 233.85
2019-08-15 16:00 | 240.14 | 233.52
2019-08-15 16:30 | 241.16 | 234.39
2019-08-15 17:00 | 242.38 | 235.87
2019-08-15 17:30 | 244.95 | 238.71
2019-08-15 18:00 | 250.13 | 246.2
2019-08-15 18:30 | 253.11 | 249.42
2019-08-15 19:00 | 252.83 | 249.1
2019-08-15 19:30 | 252.07 | 248.27
2019-08-15 20:00 | 251.98 | 248.26
2019-08-15 20:30 | 251.21 | 247.58
2019-08-15 21:00 | 247.46 | 241.64
2019-08-15 21:30 | 246.93 | 241.16
2019-08-15 22:00 | 245.22 | 239.95
2019-08-15 22:30 | 242.13 | 237.1
2019-08-15 23:00 | 240.98 | 235.73
2019-08-15 23:30 | 239.92 | 234.47
2019-08-16 | 237.89 | 233.14
2019-08-16 00:30 | 237.21 | 232.33
2019-08-16 01:00 | 236.49 | 231.48
2019-08-16 01:30 | 235.18 | 229.98
2019-08-16 02:00 | 235.35 | 230.24
2019-08-16 02:30 | 234.8 | 229.84
2019-08-16 03:00 | 235.06 | 230.21
2019-08-16 03:30 | 234.73 | 229.66
2019-08-16 04:00 | 235.61 | 230.38
2019-08-16 04:30 | 236.38 | 231.18
2019-08-16 05:00 | 237.02 | 231.98
2019-08-16 05:30 | 239.37 | 234.62
2019-08-16 06:00 | 242.15 | 237.41
2019-08-16 06:30 | 244.48 | 240.25
2019-08-16 07:00 | 250.05 | 247.08
2019-08-16 07:30 | 249.29 | 245.57
2019-08-16 08:00 | 249.2 | 245.85
2019-08-16 08:30 | 249.22 | 246.56
2019-08-16 09:00 | 249.46 | 247.07
2019-08-16 09:30 | 240.27 | 234.94
2019-08-16 10:00 | 236.81 | 230.33
2019-08-16 10:30 | 237.17 | 230.62
2019-08-16 11:00 | 236.03 | 229.35
2019-08-16 11:30 | 235.94 | 229.52
2019-08-16 12:00 | 235.92 | 229.49
2019-08-16 12:30 | 236.41 | 229.92
2019-08-16 13:00 | 236.11 | 229.24
2019-08-16 13:30 | 236.94 | 229.76
2019-08-16 14:00 | 236.57 | 230.09
2019-08-16 14:30 | 236.22 | 229.84
2019-08-16 15:00 | 236.76 | 229.73
2019-08-16 15:30 | 236.99 | 229.82
2019-08-16 16:00 | 239.32 | 231.85
2019-08-16 16:30 | 240.82 | 233.43
2019-08-16 17:00 | 243.17 | 235.78
2019-08-16 17:30 | 244.12 | 237.28
2019-08-16 18:00 | 246.7 | 239.79
2019-08-16 18:30 | 248.54 | 241.79
2019-08-16 19:00 | 249.66 | 243.09
2019-08-16 19:30 | 249.45 | 242.69
2019-08-16 20:00 | 247.81 | 240.8
2019-08-16 20:30 | 246.85 | 239.53
2019-08-16 21:00 | 245.92 | 238.49
2019-08-16 21:30 | 244.25 | 237.8
2019-08-16 22:00 | 243.21 | 236.94
2019-08-16 22:30 | 241.14 | 235.66
2019-08-16 23:00 | 239.74 | 234.17
2019-08-16 23:30 | 239.13 | 233.82
2019-08-17 | 237.02 | 232.12
2019-08-17 00:30 | 236.53 | 231.6
2019-08-17 01:00 | 235.56 | 230.89
2019-08-17 01:30 | 234.79 | 230.19
2019-08-17 02:00 | 233.86 | 229.48
2019-08-17 02:30 | 233.51 | 229.13
2019-08-17 03:00 | 233.35 | 228.67
2019-08-17 03:30 | 233.16 | 228.42
2019-08-17 04:00 | 233.78 | 229.1
2019-08-17 04:30 | 234.52 | 229.76
2019-08-17 05:00 | 235 | 230.24
2019-08-17 05:30 | 235.79 | 231.03
2019-08-17 06:00 | 236.49 | 231.98
2019-08-17 06:30 | 238.26 | 233.8
2019-08-17 07:00 | 240.04 | 235.34
2019-08-17 07:30 | 239.93 | 235.48
2019-08-17 08:00 | 238.57 | 234.61
2019-08-17 08:30 | 237.23 | 233.34
2019-08-17 09:00 | 234.38 | 230.29
2019-08-17 09:30 | 230.27 | 226.24
2019-08-17 10:00 | 214.89 | 210.63
2019-08-17 10:30 | 178.56 | 173.86
2019-08-17 11:00 | 164.38 | 159.37
2019-08-17 11:30 | 164.2 | 159.22
2019-08-17 12:00 | 163.4 | 158.1
2019-08-17 12:30 | 164.25 | 158.85
2019-08-17 13:00 | 164.22 | 158.83
2019-08-17 13:30 | 164.21 | 159.02
2019-08-17 14:00 | 164.42 | 159.15
2019-08-17 14:30 | 165.55 | 160.44
2019-08-17 15:00 | 167.16 | 161.27
2019-08-17 15:30 | 170.99 | 164.95
2019-08-17 16:00 | 205.23 | 198.75
2019-08-17 16:30 | 234.19 | 226.98
2019-08-17 17:00 | 240.21 | 232.82
2019-08-17 17:30 | 243.35 | 236.08
2019-08-17 18:00 | 245.91 | 238.4
2019-08-17 18:30 | 247.47 | 240.03
2019-08-17 19:00 | 248.09 | 240.59
2019-08-17 19:30 | 246.8 | 238.87
2019-08-17 20:00 | 246.29 | 238.03
2019-08-17 20:30 | 245.34 | 237.06
2019-08-17 21:00 | 244.37 | 236.05
2019-08-17 21:30 | 243.79 | 236.58
2019-08-17 22:00 | 243.22 | 236.25
2019-08-17 22:30 | 241.23 | 234.5
2019-08-17 23:00 | 239.38 | 232.84
2019-08-17 23:30 | 238.9 | 232.44
2019-08-18 | 236.39 | 231.83
2019-08-18 00:30 | 235.44 | 230.62
2019-08-18 01:00 | 233.45 | 228.56
2019-08-18 01:30 | 231.94 | 227.13
2019-08-18 02:00 | 237.06 | 228.94
2019-08-18 02:30 | 237.54 | 228.88
2019-08-18 03:00 | 237.67 | 228.7
2019-08-18 03:30 | 237.66 | 228.66
2019-08-18 04:00 | 237.96 | 228.93
2019-08-18 04:30 | 238.14 | 229.3
2019-08-18 05:00 | 238.52 | 229.77
2019-08-18 05:30 | 239.11 | 230.42
2019-08-18 06:00 | 238.84 | 230.33
2019-08-18 06:30 | 239.96 | 232.11
2019-08-18 07:00 | 241.06 | 233.33
2019-08-18 07:30 | 240.69 | 233.89
2019-08-18 08:00 | 239.33 | 232.45
2019-08-18 08:30 | 238.25 | 230.61
2019-08-18 09:00 | 220.89 | 212.63
2019-08-18 09:30 | 184.87 | 175.36
2019-08-18 10:00 | 171.87 | 162.02
2019-08-18 10:30 | 171.34 | 160.25
2019-08-18 11:00 | 170.63 | 159.34
2019-08-18 11:30 | 170.19 | 158.99
2019-08-18 12:00 | 169.53 | 158.8
2019-08-18 12:30 | 171.57 | 159.54
2019-08-18 13:00 | 171.84 | 158.54
2019-08-18 13:30 | 172.57 | 159.37
2019-08-18 14:00 | 172.56 | 159.78
2019-08-18 14:30 | 197.96 | 186.45
2019-08-18 15:00 | 227.75 | 217.67
2019-08-18 15:30 | 234.68 | 227.34
2019-08-18 16:00 | 237.11 | 229.1
2019-08-18 16:30 | 238.44 | 230.62
2019-08-18 17:00 | 241.39 | 232.93
2019-08-18 17:30 | 242.94 | 235.41
2019-08-18 18:00 | 245.63 | 237.88
2019-08-18 18:30 | 248.43 | 240.68
2019-08-18 19:00 | 249.5 | 241.7
2019-08-18 19:30 | 247.6 | 239.56
2019-08-18 20:00 | 246.84 | 238.7
2019-08-18 20:30 | 245.26 | 236.76
2019-08-18 21:00 | 243.27 | 235.65
2019-08-18 21:30 | 241.8 | 235.08
2019-08-18 22:00 | 240.28 | 234.18
2019-08-18 22:30 | 237.84 | 232.01
2019-08-18 23:00 | 236.38 | 230.91
2019-08-18 23:30 | 236.35 | 231.32
2019-08-19 | 234 | 229.07
2019-08-19 00:30 | 233.66 | 229.44
2019-08-19 01:00 | 231.91 | 227.47
2019-08-19 01:30 | 232.21 | 227.78
2019-08-19 02:00 | 231.39 | 226.96
2019-08-19 02:30 | 231.21 | 226.72
2019-08-19 03:00 | 231.11 | 226.47
2019-08-19 03:30 | 231.28 | 226.65
2019-08-19 04:00 | 231.65 | 227.01
2019-08-19 04:30 | 232.62 | 228.13
2019-08-19 05:00 | 233.15 | 228.79
2019-08-19 05:30 | 234.18 | 230.03
2019-08-19 06:00 | 236.02 | 231.83
2019-08-19 06:30 | 240.08 | 236.25
2019-08-19 07:00 | 243.38 | 239.01
2019-08-19 07:30 | 245.43 | 240.42
2019-08-19 08:00 | 244.37 | 239.16
2019-08-19 08:30 | 223.15 | 218.08
2019-08-19 09:00 | 231.73 | 226.77
2019-08-19 09:30 | 237.21 | 231.82
2019-08-19 10:00 | 235.95 | 230.11
2019-08-19 10:30 | 234.16 | 228.28
2019-08-19 11:00 | 233.53 | 227.46
2019-08-19 11:30 | 232.91 | 226.97
2019-08-19 12:00 | 232.88 | 226.94
2019-08-19 12:30 | 232.33 | 226.11
2019-08-19 13:00 | 232.08 | 225.87
2019-08-19 13:30 | 232.27 | 225.98
2019-08-19 14:00 | 232.46 | 225.91
2019-08-19 14:30 | 232.66 | 226.64
2019-08-19 15:00 | 233.62 | 227.7
2019-08-19 15:30 | 235.14 | 229.28
2019-08-19 16:00 | 237.61 | 230.97
2019-08-19 16:30 | 240.48 | 233.32
2019-08-19 17:00 | 242.73 | 235.46
2019-08-19 17:30 | 246.26 | 238.68
2019-08-19 18:00 | 251.61 | 243.11
2019-08-19 18:30 | 256.93 | 248.67
2019-08-19 19:00 | 258.44 | 250.42
2019-08-19 19:30 | 259.67 | 251.73
2019-08-19 20:00 | 258.6 | 250.63
2019-08-19 20:30 | 257.55 | 249.58
2019-08-19 21:00 | 254.5 | 247.46
2019-08-19 21:30 | 250.1 | 244.48
2019-08-19 22:00 | 248.17 | 242.39
2019-08-19 22:30 | 245.3 | 239.69
2019-08-19 23:00 | 243.26 | 236.95
2019-08-19 23:30 | 242.04 | 236.12
2019-08-20 | 239.59 | 234.25
2019-08-20 00:30 | 240.14 | 234.54
2019-08-20 01:00 | 239.3 | 233.43
2019-08-20 01:30 | 238.47 | 232.43
2019-08-20 02:00 | 238.69 | 232.54
2019-08-20 02:30 | 238.97 | 232.71
2019-08-20 03:00 | 238.86 | 232.58
2019-08-20 03:30 | 239.28 | 233.13
2019-08-20 04:00 | 239.7 | 233.55
2019-08-20 04:30 | 240.16 | 234.08
2019-08-20 05:00 | 242.67 | 236.92
2019-08-20 05:30 | 244.07 | 238.72
2019-08-20 06:00 | 247.59 | 241.9
2019-08-20 06:30 | 253.13 | 247.23
2019-08-20 07:00 | 257.59 | 251.86
2019-08-20 07:30 | 228.85 | 224.13
2019-08-20 08:00 | 224.9 | 220.48
2019-08-20 08:30 | 226 | 221.99
2019-08-20 09:00 | 235.29 | 230.25
2019-08-20 09:30 | 243.4 | 237.37
2019-08-20 10:00 | 241.23 | 235.09
2019-08-20 10:30 | 238.6 | 232.87
2019-08-20 11:00 | 236.41 | 230.31
2019-08-20 11:30 | 234.99 | 229.05
2019-08-20 12:00 | 234.53 | 228.83
2019-08-20 12:30 | 234.25 | 228.32
2019-08-20 13:00 | 233 | 227.51
2019-08-20 13:30 | 232.44 | 227.14
2019-08-20 14:00 | 232.62 | 227.2
2019-08-20 14:30 | 232.97 | 227.7
2019-08-20 15:00 | 233.62 | 228.46
2019-08-20 15:30 | 234.68 | 229.53
2019-08-20 16:00 | 237.05 | 231.65
2019-08-20 16:30 | 238.93 | 232.72
2019-08-20 17:00 | 242.54 | 235.86
2019-08-20 17:30 | 246.33 | 239.49
2019-08-20 18:00 | 249.69 | 242.54
2019-08-20 18:30 | 253.73 | 246.56
2019-08-20 19:00 | 255.49 | 248.33
2019-08-20 19:30 | 254.32 | 247.17
2019-08-20 20:00 | 252.77 | 245.52
2019-08-20 20:30 | 252.57 | 244.99
2019-08-20 21:00 | 250.13 | 242.46
2019-08-20 21:30 | 249.25 | 241.19
2019-08-20 22:00 | 247.27 | 239.09
2019-08-20 22:30 | 244.32 | 235.92
2019-08-20 23:00 | 242.36 | 233.93
2019-08-20 23:30 | 239.68 | 233.17
2019-08-21 | 237.82 | 231.08
2019-08-21 00:30 | 236.42 | 230.96
2019-08-21 01:00 | 234.92 | 229.6
2019-08-21 01:30 | 234.81 | 229.57
2019-08-21 02:00 | 234.16 | 228.72
2019-08-21 02:30 | 234.14 | 228.57
2019-08-21 03:00 | 234.35 | 228.83
2019-08-21 03:30 | 234.58 | 229.09
2019-08-21 04:00 | 235.16 | 229.72
2019-08-21 04:30 | 236.78 | 231.56
2019-08-21 05:00 | 238.82 | 233.7
2019-08-21 05:30 | 241.66 | 237.02
2019-08-21 06:00 | 245.85 | 241.08
2019-08-21 06:30 | 250.23 | 245.3
2019-08-21 07:00 | 253.8 | 248.59
2019-08-21 07:30 | 255.34 | 249.41
2019-08-21 08:00 | 252.86 | 247.51
2019-08-21 08:30 | 248.58 | 243.23
2019-08-21 09:00 | 244.8 | 238.75
2019-08-21 09:30 | 242.18 | 235.63
2019-08-21 10:00 | 239.49 | 232.56
2019-08-21 10:30 | 237.2 | 229.53
2019-08-21 11:00 | 235.93 | 227.89
2019-08-21 11:30 | 234.84 | 226.78
2019-08-21 12:00 | 234.15 | 226.1
2019-08-21 12:30 | 232.89 | 224.71
2019-08-21 13:00 | 232.16 | 223.89
2019-08-21 13:30 | 233.02 | 224.41
2019-08-21 14:00 | 233.07 | 224.77
2019-08-21 14:30 | 232.81 | 225.33
2019-08-21 15:00 | 233.12 | 225.61
2019-08-21 15:30 | 234.04 | 226.64
2019-08-21 16:00 | 235.07 | 228.33
2019-08-21 16:30 | 236.6 | 229.71
2019-08-21 17:00 | 239.96 | 232.62
2019-08-21 17:30 | 242.72 | 234.97
2019-08-21 18:00 | 245.9 | 238.65
2019-08-21 18:30 | 249.91 | 243.4
2019-08-21 19:00 | 252.89 | 246.78
2019-08-21 19:30 | 252.12 | 245.95
2019-08-21 20:00 | 250.5 | 244.08
2019-08-21 20:30 | 249.16 | 242.95
2019-08-21 21:00 | 248.07 | 242.3
2019-08-21 21:30 | 247.41 | 241.22
2019-08-21 22:00 | 245.39 | 238.86
2019-08-21 22:30 | 242.31 | 236.85
2019-08-21 23:00 | 240.71 | 234.75
2019-08-21 23:30 | 239.37 | 233.54
2019-08-22 | 237.28 | 232.27
2019-08-22 00:30 | 236.26 | 230.81
2019-08-22 01:00 | 236.02 | 230.42
2019-08-22 01:30 | 234.58 | 229.59
2019-08-22 02:00 | 235.65 | 229.19
2019-08-22 02:30 | 236.04 | 229.3
2019-08-22 03:00 | 235.91 | 229.11
2019-08-22 03:30 | 236.3 | 229.4
2019-08-22 04:00 | 236.62 | 229.79
2019-08-22 04:30 | 237.68 | 231.01
2019-08-22 05:00 | 239.12 | 232.9
2019-08-22 05:30 | 241.12 | 235.7
2019-08-22 06:00 | 244.64 | 239.03
2019-08-22 06:30 | 249.87 | 243.78
2019-08-22 07:00 | 253.3 | 247.69
2019-08-22 07:30 | 253.65 | 248.54
2019-08-22 08:00 | 251.88 | 246.73
2019-08-22 08:30 | 250.81 | 245.64
2019-08-22 09:00 | 245.97 | 239.98
2019-08-22 09:30 | 241.68 | 235.4
2019-08-22 10:00 | 222.14 | 215.33
2019-08-22 10:30 | 189.27 | 181.88
2019-08-22 11:00 | 183.51 | 175.16
2019-08-22 11:30 | 182.49 | 173.96
2019-08-22 12:00 | 182.08 | 173.3
2019-08-22 12:30 | 181.79 | 173.06
2019-08-22 13:00 | 181.18 | 172.49
2019-08-22 13:30 | 181.73 | 172.74
2019-08-22 14:00 | 181.96 | 173.12
2019-08-22 14:30 | 182.44 | 173.75
2019-08-22 15:00 | 183.32 | 174.08
2019-08-22 15:30 | 209.38 | 200.01
2019-08-22 16:00 | 234.15 | 223.93
2019-08-22 16:30 | 241.87 | 232.32
2019-08-22 17:00 | 243.35 | 234.78
2019-08-22 17:30 | 247.7 | 237.91
2019-08-22 18:00 | 249.8 | 241.34
2019-08-22 18:30 | 253.47 | 245.71
2019-08-22 19:00 | 255.95 | 248.36
2019-08-22 19:30 | 254.7 | 247.2
2019-08-22 20:00 | 252.73 | 245.38
2019-08-22 20:30 | 252.04 | 244.65
2019-08-22 21:00 | 251.3 | 243.68
2019-08-22 21:30 | 248.95 | 242.11
2019-08-22 22:00 | 247.94 | 241.04
2019-08-22 22:30 | 244.83 | 238.7
2019-08-22 23:00 | 242.73 | 236.61
2019-08-22 23:30 | 241.38 | 235.66
2019-08-23 | 239.88 | 233.73
2019-08-23 00:30 | 239.59 | 233.42
2019-08-23 01:00 | 237.71 | 232.47
2019-08-23 01:30 | 236.47 | 231.54
2019-08-23 02:00 | 236.31 | 231.47
2019-08-23 02:30 | 236.39 | 231.08
2019-08-23 03:00 | 236.36 | 230.85
2019-08-23 03:30 | 237.12 | 231.51
2019-08-23 04:00 | 236.98 | 231.44
2019-08-23 04:30 | 238.21 | 232.91
2019-08-23 05:00 | 239.15 | 234.07
2019-08-23 05:30 | 241.71 | 236.38
2019-08-23 06:00 | 245.01 | 239.32
2019-08-23 06:30 | 248.81 | 244.07
2019-08-23 07:00 | 251.99 | 247.42
2019-08-23 07:30 | 252.87 | 248.43
2019-08-23 08:00 | 249.51 | 244.58
2019-08-23 08:30 | 245.75 | 240.35
2019-08-23 09:00 | 241.52 | 235.99
2019-08-23 09:30 | 237.2 | 231.71
2019-08-23 10:00 | 235.1 | 229.16
2019-08-23 10:30 | 233.25 | 226.8
2019-08-23 11:00 | 231.32 | 224.78
2019-08-23 11:30 | 229.14 | 222.92
2019-08-23 12:00 | 229.42 | 223.28
2019-08-23 12:30 | 230.67 | 223.5
2019-08-23 13:00 | 229.74 | 222.44
2019-08-23 13:30 | 230.07 | 222.88
2019-08-23 14:00 | 230.57 | 223.32
2019-08-23 14:30 | 230.56 | 223.25
2019-08-23 15:00 | 231.24 | 224.3
2019-08-23 15:30 | 232.35 | 225.42
2019-08-23 16:00 | 234.2 | 227.43
2019-08-23 16:30 | 237.48 | 230.18
2019-08-23 17:00 | 239.41 | 232.17
2019-08-23 17:30 | 241.77 | 234.43
2019-08-23 18:00 | 243.73 | 235.78
2019-08-23 18:30 | 247.05 | 239.26
2019-08-23 19:00 | 248.8 | 241.01
2019-08-23 19:30 | 248.52 | 240.7
2019-08-23 20:00 | 248.39 | 240.16
2019-08-23 20:30 | 248.15 | 239.72
2019-08-23 21:00 | 246.59 | 238.23
2019-08-23 21:30 | 245.89 | 238.25
2019-08-23 22:00 | 244.14 | 237.21
2019-08-23 22:30 | 242.24 | 235.18
2019-08-23 23:00 | 240.56 | 233.26
2019-08-23 23:30 | 239.89 | 232.76
2019-08-24 | 237.82 | 232.05
2019-08-24 00:30 | 237.07 | 232.2
2019-08-24 01:00 | 235.6 | 230.78
2019-08-24 01:30 | 235.62 | 230.54
2019-08-24 02:00 | 235.52 | 230.4
2019-08-24 02:30 | 235.59 | 230.09
2019-08-24 03:00 | 236.15 | 230.52
2019-08-24 03:30 | 235.43 | 230.04
2019-08-24 04:00 | 236.29 | 230.6
2019-08-24 04:30 | 236.3 | 230.68
2019-08-24 05:00 | 236.63 | 231.15
2019-08-24 05:30 | 237.59 | 232.48
2019-08-24 06:00 | 239.18 | 234.05
2019-08-24 06:30 | 240.27 | 235.52
2019-08-24 07:00 | 241.29 | 236.55
2019-08-24 07:30 | 241.19 | 236.81
2019-08-24 08:00 | 239.96 | 235.63
2019-08-24 08:30 | 238.77 | 233.67
2019-08-24 09:00 | 236.89 | 231.11
2019-08-24 09:30 | 218.48 | 211.47
2019-08-24 10:00 | 176.13 | 169.19
2019-08-24 10:30 | 161.06 | 154.3
2019-08-24 11:00 | 158.05 | 151.27
2019-08-24 11:30 | 158.51 | 152.43
2019-08-24 12:00 | 158.24 | 151.33
2019-08-24 12:30 | 157.96 | 151.28
2019-08-24 13:00 | 156.31 | 150.48
2019-08-24 13:30 | 156.49 | 149.87
2019-08-24 14:00 | 156.25 | 150.39
2019-08-24 14:30 | 157.09 | 151.05
2019-08-24 15:00 | 158.27 | 151.93
2019-08-24 15:30 | 190.35 | 184.8
2019-08-24 16:00 | 223.07 | 216.8
2019-08-24 16:30 | 233.48 | 225.83
2019-08-24 17:00 | 235.69 | 228.3
2019-08-24 17:30 | 238.4 | 230.61
2019-08-24 18:00 | 241.85 | 233.18
2019-08-24 18:30 | 244.31 | 235.44
2019-08-24 19:00 | 245.55 | 236.55
2019-08-24 19:30 | 243.58 | 235.52
2019-08-24 20:00 | 242.36 | 233.97
2019-08-24 20:30 | 242.33 | 233.83
2019-08-24 21:00 | 241.83 | 232.93
2019-08-24 21:30 | 240.03 | 232.66
2019-08-24 22:00 | 238.9 | 231.78
2019-08-24 22:30 | 238.08 | 231.02
2019-08-24 23:00 | 236.19 | 229.43
2019-08-24 23:30 | 234.78 | 228.61
2019-08-25 | 233.85 | 228
2019-08-25 00:30 | 232.54 | 227.76
2019-08-25 01:00 | 232.03 | 226.47
2019-08-25 01:30 | 232.4 | 226.39
2019-08-25 02:00 | 231.8 | 225.77
2019-08-25 02:30 | 232.15 | 225.66
2019-08-25 03:00 | 232.57 | 225.78
2019-08-25 03:30 | 232.29 | 225.32
2019-08-25 04:00 | 232.64 | 225.77
2019-08-25 04:30 | 232.56 | 225.84
2019-08-25 05:00 | 233.94 | 226.88
2019-08-25 05:30 | 234.59 | 227.67
2019-08-25 06:00 | 235.31 | 228.36
2019-08-25 06:30 | 236.09 | 229.32
2019-08-25 07:00 | 236.36 | 230.19
2019-08-25 07:30 | 235.91 | 230.14
2019-08-25 08:00 | 236.13 | 230.26
2019-08-25 08:30 | 234.84 | 228.66
2019-08-25 09:00 | 234.11 | 227.61
2019-08-25 09:30 | 230.7 | 224.74
2019-08-25 10:00 | 211.09 | 205.76
2019-08-25 10:30 | 174.03 | 167.85
2019-08-25 11:00 | 159.02 | 152.38
2019-08-25 11:30 | 157.85 | 150.87
2019-08-25 12:00 | 159.79 | 153.39
2019-08-25 12:30 | 158.69 | 152.08
2019-08-25 13:00 | 159.52 | 152.98
2019-08-25 13:30 | 159.52 | 152.71
2019-08-25 14:00 | 158.5 | 152.08
2019-08-25 14:30 | 159.03 | 152.27
2019-08-25 15:00 | 160.99 | 154.24
2019-08-25 15:30 | 196.01 | 188.93
2019-08-25 16:00 | 227.01 | 219.88
2019-08-25 16:30 | 234.96 | 228.13
2019-08-25 17:00 | 233.33 | 226.88
2019-08-25 17:30 | 228.13 | 221.93
2019-08-25 18:00 | 227.1 | 220.13
2019-08-25 18:30 | 226.1 | 218.99
2019-08-25 19:00 | 225.65 | 218.51
2019-08-25 19:30 | 226.25 | 219.21
2019-08-25 20:00 | 227.29 | 220.32
2019-08-25 20:30 | 228.13 | 221.07
2019-08-25 21:00 | 229.03 | 221.83
2019-08-25 21:30 | 238.75 | 230.11
2019-08-25 22:00 | 239.78 | 232.16
2019-08-25 22:30 | 238.28 | 230.42
2019-08-25 23:00 | 236.38 | 228.75
2019-08-25 23:30 | 235.51 | 228.32
2019-08-26 | 234.92 | 227.36
2019-08-26 00:30 | 233.75 | 226.61
2019-08-26 01:00 | 231.92 | 225.96
2019-08-26 01:30 | 231.13 | 225.56
2019-08-26 02:00 | 231.27 | 225.55
2019-08-26 02:30 | 230.69 | 225
2019-08-26 03:00 | 230.57 | 224.93
2019-08-26 03:30 | 230.27 | 224.61
2019-08-26 04:00 | 230.88 | 225.25
2019-08-26 04:30 | 231.44 | 225.99
2019-08-26 05:00 | 232.81 | 227.21
2019-08-26 05:30 | 234.19 | 228.69
2019-08-26 06:00 | 236.42 | 231.15
2019-08-26 06:30 | 240.53 | 235.2
2019-08-26 07:00 | 243.75 | 237.83
2019-08-26 07:30 | 244.9 | 239.37
2019-08-26 08:00 | 243.59 | 237.89
2019-08-26 08:30 | 240.67 | 234.78
2019-08-26 09:00 | 236.98 | 231.08
2019-08-26 09:30 | 217.81 | 211.86
2019-08-26 10:00 | 175.39 | 169.41
2019-08-26 10:30 | 162.54 | 156.56
2019-08-26 11:00 | 160.49 | 154.29
2019-08-26 11:30 | 159.19 | 152.52
2019-08-26 12:00 | 159.29 | 152.33
2019-08-26 12:30 | 159.86 | 153
2019-08-26 13:00 | 158.82 | 152.29
2019-08-26 13:30 | 159.15 | 153.05
2019-08-26 14:00 | 161.21 | 155.1
2019-08-26 14:30 | 163.08 | 157.79
2019-08-26 15:00 | 164.74 | 159.68
2019-08-26 15:30 | 198.66 | 193.15
2019-08-26 16:00 | 230.86 | 225.09
2019-08-26 16:30 | 238.08 | 232.17
2019-08-26 17:00 | 239.41 | 233.44
2019-08-26 17:30 | 241.54 | 235.03
2019-08-26 18:00 | 244.41 | 237.12
2019-08-26 18:30 | 247.78 | 240.91
2019-08-26 19:00 | 248.96 | 242.06
2019-08-26 19:30 | 247.97 | 240.53
2019-08-26 20:00 | 246.63 | 238.91
2019-08-26 20:30 | 245.66 | 237.87
2019-08-26 21:00 | 243.73 | 235.71
2019-08-26 21:30 | 241.96 | 234.18
2019-08-26 22:00 | 239.61 | 232.64
2019-08-26 22:30 | 238.14 | 231.09
2019-08-26 23:00 | 235.61 | 229
2019-08-26 23:30 | 235.11 | 228.46
2019-08-27 | 233.83 | 227.08
2019-08-27 00:30 | 232.95 | 226.73
2019-08-27 01:00 | 231.35 | 225.76
2019-08-27 01:30 | 230.67 | 225.08
2019-08-27 02:00 | 229.83 | 224.61
2019-08-27 02:30 | 229.27 | 223.84
2019-08-27 03:00 | 229.77 | 224.39
2019-08-27 03:30 | 229.61 | 224.39
2019-08-27 04:00 | 229.63 | 224.42
2019-08-27 04:30 | 229.98 | 224.85
2019-08-27 05:00 | 231.38 | 226.26
2019-08-27 05:30 | 232.97 | 227.75
2019-08-27 06:00 | 236.11 | 230.32
2019-08-27 06:30 | 240.13 | 234.19
2019-08-27 07:00 | 243.74 | 237.76
2019-08-27 07:30 | 245.34 | 239.55
2019-08-27 08:00 | 243.05 | 237.16
2019-08-27 08:30 | 239.51 | 233.61
2019-08-27 09:00 | 236.37 | 230.54
2019-08-27 09:30 | 217.62 | 211.87
2019-08-27 10:00 | 186.1 | 179.44
2019-08-27 10:30 | 203.57 | 197.31
2019-08-27 11:00 | 225.61 | 219.67
2019-08-27 11:30 | 231.74 | 225.75
2019-08-27 12:00 | 231 | 225.27
2019-08-27 12:30 | 232.25 | 226.21
2019-08-27 13:00 | 231.37 | 225.39
2019-08-27 13:30 | 232.43 | 226.09
2019-08-27 14:00 | 231.89 | 225.22
2019-08-27 14:30 | 232.93 | 225.95
2019-08-27 15:00 | 233.97 | 226.78
2019-08-27 15:30 | 234.01 | 227.36
2019-08-27 16:00 | 235.2 | 228.68
2019-08-27 16:30 | 238.15 | 231.58
2019-08-27 17:00 | 240.29 | 233.51
2019-08-27 17:30 | 242.32 | 234.93
2019-08-27 18:00 | 243.81 | 236.28
2019-08-27 18:30 | 247.98 | 240.5
2019-08-27 19:00 | 249 | 241.72
2019-08-27 19:30 | 247.73 | 240.54
2019-08-27 20:00 | 246.05 | 238.81
2019-08-27 20:30 | 244.51 | 237.23
2019-08-27 21:00 | 243.51 | 235.99
2019-08-27 21:30 | 241.31 | 234.29
2019-08-27 22:00 | 239.73 | 232.83
2019-08-27 22:30 | 237.86 | 231.09
2019-08-27 23:00 | 236.4 | 229.54
2019-08-27 23:30 | 235.76 | 228.81
2019-08-28 | 234.34 | 227.54
2019-08-28 00:30 | 233.95 | 227.17
2019-08-28 01:00 | 232.94 | 226.24
2019-08-28 01:30 | 232.16 | 225.64
2019-08-28 02:00 | 230.76 | 224.59
2019-08-28 02:30 | 230.73 | 224.6
2019-08-28 03:00 | 230.62 | 224.49
2019-08-28 03:30 | 231.15 | 225.22
2019-08-28 04:00 | 231.05 | 225.16
2019-08-28 04:30 | 231.94 | 225.94
2019-08-28 05:00 | 232.98 | 227.02
2019-08-28 05:30 | 234.52 | 228.81
2019-08-28 06:00 | 236.86 | 231.17
2019-08-28 06:30 | 241.39 | 235.09
2019-08-28 07:00 | 244.45 | 238.04
2019-08-28 07:30 | 246.6 | 240.42
2019-08-28 08:00 | 246.64 | 240.68
2019-08-28 08:30 | 244.63 | 238.77
2019-08-28 09:00 | 241.51 | 235.67
2019-08-28 09:30 | 239.28 | 233.47
2019-08-28 10:00 | 237.92 | 232.36
2019-08-28 10:30 | 235.91 | 230.04
2019-08-28 11:00 | 235.93 | 229.78
2019-08-28 11:30 | 236.05 | 229.82
2019-08-28 12:00 | 234.16 | 227.9
2019-08-28 12:30 | 232.47 | 226.22
2019-08-28 13:00 | 232.9 | 226.67
2019-08-28 13:30 | 233.89 | 227.59
2019-08-28 14:00 | 235.98 | 229.21
2019-08-28 14:30 | 235.88 | 229.58
2019-08-28 15:00 | 237.06 | 230.47
2019-08-28 15:30 | 238.2 | 231.56
2019-08-28 16:00 | 239.05 | 232.27
2019-08-28 16:30 | 239.74 | 232.9
2019-08-28 17:00 | 241.94 | 235.1
2019-08-28 17:30 | 245.02 | 237.45
2019-08-28 18:00 | 247.85 | 240.52
2019-08-28 18:30 | 252.03 | 245.07
2019-08-28 19:00 | 253.54 | 246.68
2019-08-28 19:30 | 253.07 | 246
2019-08-28 20:00 | 251.39 | 244.26
2019-08-28 20:30 | 250.44 | 243.41
2019-08-28 21:00 | 248.56 | 241.51
2019-08-28 21:30 | 246.93 | 240.23
2019-08-28 22:00 | 245.4 | 238.62
2019-08-28 22:30 | 243.3 | 236.71
2019-08-28 23:00 | 240.87 | 234.09
2019-08-28 23:30 | 240.12 | 233.82
2019-08-29 | 238.2 | 231.96
2019-08-29 00:30 | 237.73 | 231.66
2019-08-29 01:00 | 237.14 | 230.62
2019-08-29 01:30 | 236.68 | 230.04
2019-08-29 02:00 | 236.4 | 230.01
2019-08-29 02:30 | 235.71 | 229.67
2019-08-29 03:00 | 235.61 | 229.47
2019-08-29 03:30 | 235.14 | 228.95
2019-08-29 04:00 | 234.93 | 229.21
2019-08-29 04:30 | 236.9 | 230.53
2019-08-29 05:00 | 237.6 | 231.29
2019-08-29 05:30 | 239.05 | 233.14
2019-08-29 06:00 | 241.36 | 235.42
2019-08-29 06:30 | 245.3 | 238.84
2019-08-29 07:00 | 249.68 | 242.91
2019-08-29 07:30 | 250.81 | 244.02
2019-08-29 08:00 | 249.91 | 243.21
2019-08-29 08:30 | 246.72 | 239.96
2019-08-29 09:00 | 243.89 | 237.12
2019-08-29 09:30 | 240.62 | 234.06
2019-08-29 10:00 | 238.61 | 232.1
2019-08-29 10:30 | 237.48 | 231.11
2019-08-29 11:00 | 237.22 | 230.46
2019-08-29 11:30 | 236.6 | 230.09
2019-08-29 12:00 | 235.96 | 229.55
2019-08-29 12:30 | 234.59 | 228.04
2019-08-29 13:00 | 232.1 | 225.72
2019-08-29 13:30 | 231.98 | 225.51
2019-08-29 14:00 | 232.19 | 225.65
2019-08-29 14:30 | 233.54 | 226.93
2019-08-29 15:00 | 233.82 | 227.04
2019-08-29 15:30 | 235.22 | 228.52
2019-08-29 16:00 | 236.34 | 229.34
2019-08-29 16:30 | 238.32 | 231.18
2019-08-29 17:00 | 240.51 | 233.35
2019-08-29 17:30 | 243.41 | 236.01
2019-08-29 18:00 | 246.93 | 238.64
2019-08-29 18:30 | 251.25 | 243.42
2019-08-29 19:00 | 253.42 | 246.31
2019-08-29 19:30 | 252.37 | 245.09
2019-08-29 20:00 | 251.21 | 243.8
2019-08-29 20:30 | 250.41 | 243.1
2019-08-29 21:00 | 249.2 | 241.72
2019-08-29 21:30 | 248.97 | 241.79
2019-08-29 22:00 | 247.08 | 239.67
2019-08-29 22:30 | 244.44 | 237.11
2019-08-29 23:00 | 244.24 | 236.73
2019-08-29 23:30 | 242.24 | 234.73
2019-08-30 | 240.36 | 233.13
2019-08-30 00:30 | 239.47 | 232.78
2019-08-30 01:00 | 237.95 | 231.7
2019-08-30 01:30 | 237.24 | 231.17
2019-08-30 02:00 | 237.09 | 230.78
2019-08-30 02:30 | 237.06 | 230.43
2019-08-30 03:00 | 237.05 | 230.78
2019-08-30 03:30 | 237.65 | 231.4
2019-08-30 04:00 | 237.94 | 231.97
2019-08-30 04:30 | 238.05 | 232.29
2019-08-30 05:00 | 240.05 | 234.38
2019-08-30 05:30 | 242.35 | 236.88
2019-08-30 06:00 | 245.42 | 240.36
2019-08-30 06:30 | 249.56 | 244.19
2019-08-30 07:00 | 252.16 | 247.16
2019-08-30 07:30 | 252.31 | 247.66
2019-08-30 08:00 | 250.76 | 245.31
2019-08-30 08:30 | 245.88 | 240.74
2019-08-30 09:00 | 241.38 | 236.59
2019-08-30 09:30 | 237.43 | 232.21
2019-08-30 10:00 | 234.45 | 228.94
2019-08-30 10:30 | 233.76 | 228.37
2019-08-30 11:00 | 230.99 | 225.73
2019-08-30 11:30 | 231.19 | 225.84
2019-08-30 12:00 | 230.59 | 224.77
2019-08-30 12:30 | 214.2 | 208.25
2019-08-30 13:00 | 175.2 | 169.63
2019-08-30 13:30 | 161.33 | 156.01
2019-08-30 14:00 | 161.47 | 155.89
2019-08-30 14:30 | 162.4 | 157.01
2019-08-30 15:00 | 162.03 | 156.72
2019-08-30 15:30 | 163.49 | 158.36
2019-08-30 16:00 | 201.14 | 195.62
2019-08-30 16:30 | 232.37 | 226.55
2019-08-30 17:00 | 239.9 | 234
2019-08-30 17:30 | 243.38 | 236.52
2019-08-30 18:00 | 246.8 | 239.29
2019-08-30 18:30 | 249.82 | 242.98
2019-08-30 19:00 | 251.79 | 245.01
2019-08-30 19:30 | 251.06 | 244.08
2019-08-30 20:00 | 249.95 | 242.82
2019-08-30 20:30 | 250.5 | 243.3
2019-08-30 21:00 | 249.44 | 242.08
2019-08-30 21:30 | 248.41 | 242.36
2019-08-30 22:00 | 246.97 | 240.95
2019-08-30 22:30 | 245.13 | 238.93
2019-08-30 23:00 | 243.04 | 236.65
2019-08-30 23:30 | 241.31 | 234.78
2019-08-31 | 238.85 | 232.05
2019-08-31 00:30 | 237.79 | 231.29
2019-08-31 01:00 | 235.91 | 230.57
2019-08-31 01:30 | 234.76 | 229.78
2019-08-31 02:00 | 234.9 | 229.85
2019-08-31 02:30 | 234.3 | 229.17
2019-08-31 03:00 | 234.53 | 229.31
2019-08-31 03:30 | 235.2 | 229.41
2019-08-31 04:00 | 236.06 | 229.86
2019-08-31 04:30 | 236.52 | 230.31
2019-08-31 05:00 | 237.87 | 231.59
2019-08-31 05:30 | 239.6 | 233.05
2019-08-31 06:00 | 240.69 | 234.19
2019-08-31 06:30 | 242.39 | 236.86
2019-08-31 07:00 | 242.65 | 238.26
2019-08-31 07:30 | 242.09 | 238.07
2019-08-31 08:00 | 241.39 | 237.43
2019-08-31 08:30 | 238.44 | 234.17
2019-08-31 09:00 | 219.66 | 214.6
2019-08-31 09:30 | 180.37 | 174.84
2019-08-31 10:00 | 163.01 | 156.74
2019-08-31 10:30 | 161 | 153.5
2019-08-31 11:00 | 160.03 | 152.07
2019-08-31 11:30 | 159.56 | 151.41
2019-08-31 12:00 | 159.94 | 151.44
2019-08-31 12:30 | 159.86 | 150.61
2019-08-31 13:00 | 158.68 | 149.99
2019-08-31 13:30 | 158.59 | 150.31
2019-08-31 14:00 | 159 | 150.54
2019-08-31 14:30 | 159.4 | 150.85
2019-08-31 15:00 | 160.63 | 151.72
2019-08-31 15:30 | 196.41 | 187.52
2019-08-31 16:00 | 226.35 | 217.06
2019-08-31 16:30 | 235.87 | 225.67
2019-08-31 17:00 | 238.81 | 229.11
2019-08-31 17:30 | 231.99 | 224.09
2019-08-31 18:00 | 229.28 | 221.58
2019-08-31 18:30 | 227.41 | 220.13
2019-08-31 19:00 | 226.67 | 219.11
2019-08-31 19:30 | 226.96 | 219.47
2019-08-31 20:00 | 226.85 | 219.36
2019-08-31 20:30 | 240.69 | 231.92
2019-08-31 21:00 | 243.85 | 234.94
2019-08-31 21:30 | 243.04 | 235.31
2019-08-31 22:00 | 241.97 | 234.44
2019-08-31 22:30 | 240.44 | 233.38
2019-08-31 23:00 | 239.3 | 232.31
2019-08-31 23:30 | 237.73 | 231.43
2019-09-01 | 236.93 | 231.45
2019-09-01 00:30 | 236.4 | 230.67
2019-09-01 01:00 | 235.28 | 229.76
2019-09-01 01:30 | 234.96 | 229.51
2019-09-01 02:00 | 234.93 | 229.23
2019-09-01 02:30 | 234.5 | 229.26
2019-09-01 03:00 | 233.08 | 227.94
2019-09-01 03:30 | 234.78 | 228.9
2019-09-01 04:00 | 235.54 | 229.16
2019-09-01 04:30 | 236.68 | 229.92
2019-09-01 05:00 | 237.85 | 230.69
2019-09-01 05:30 | 239.36 | 231.61
2019-09-01 06:00 | 240.37 | 233.25
2019-09-01 06:30 | 240.68 | 234.38
2019-09-01 07:00 | 242.34 | 236.2
2019-09-01 07:30 | 241.25 | 236.48
2019-09-01 08:00 | 239.65 | 235.36
2019-09-01 08:30 | 240.33 | 233.46
2019-09-01 09:00 | 220.82 | 213.24
2019-09-01 09:30 | 182.38 | 174.58
2019-09-01 10:00 | 165.81 | 157.43
2019-09-01 10:30 | 163.58 | 155.36
2019-09-01 11:00 | 164.05 | 154.49
2019-09-01 11:30 | 160.43 | 152.25
2019-09-01 12:00 | 160.61 | 152.42
2019-09-01 12:30 | 158.02 | 151.73
2019-09-01 13:00 | 157.73 | 151.04
2019-09-01 13:30 | 157.38 | 151.15
2019-09-01 14:00 | 157.5 | 151.25
2019-09-01 14:30 | 158.3 | 151.85
2019-09-01 15:00 | 159.81 | 153.1
2019-09-01 15:30 | 162.54 | 153.82
2019-09-01 16:00 | 165.88 | 156.37
2019-09-01 16:30 | 167.98 | 158.17
2019-09-01 17:00 | 203.58 | 193.96
2019-09-01 17:30 | 235.5 | 226.12
2019-09-01 18:00 | 241.95 | 232.99
2019-09-01 18:30 | 245.48 | 236.52
2019-09-01 19:00 | 246.4 | 238.19
2019-09-01 19:30 | 245.39 | 237.72
2019-09-01 20:00 | 243.76 | 236.4
2019-09-01 20:30 | 243.03 | 235.79
2019-09-01 21:00 | 242.24 | 234.95
2019-09-01 21:30 | 241.97 | 234.83
2019-09-01 22:00 | 240.76 | 233.51
2019-09-01 22:30 | 237.81 | 231.44
2019-09-01 23:00 | 236.13 | 229.72
2019-09-01 23:30 | 234.85 | 228.94
2019-09-02 | 234.05 | 228.2
2019-09-02 00:30 | 233.59 | 228.31
2019-09-02 01:00 | 233.07 | 227.31
2019-09-02 01:30 | 233.25 | 226.64
2019-09-02 02:00 | 233.52 | 226.26
2019-09-02 02:30 | 233.16 | 226.26
2019-09-02 03:00 | 232.56 | 225.79
2019-09-02 03:30 | 233.87 | 226.99
2019-09-02 04:00 | 234.61 | 227.5
2019-09-02 04:30 | 235.47 | 228.55
2019-09-02 05:00 | 236.91 | 229.88
2019-09-02 05:30 | 238.65 | 231.99
2019-09-02 06:00 | 242.48 | 235.37
2019-09-02 06:30 | 245.27 | 239.21
2019-09-02 07:00 | 249.05 | 242.88
2019-09-02 07:30 | 249.88 | 244.18
2019-09-02 08:00 | 246.47 | 240.59
2019-09-02 08:30 | 241.76 | 235.44
2019-09-02 09:00 | 221.34 | 214.34
2019-09-02 09:30 | 180.5 | 173.12
2019-09-02 10:00 | 167.34 | 159.61
2019-09-02 10:30 | 165.66 | 157.98
2019-09-02 11:00 | 163.64 | 155.89
2019-09-02 11:30 | 163.14 | 155
2019-09-02 12:00 | 162.62 | 154.49
2019-09-02 12:30 | 162.73 | 154.47
2019-09-02 13:00 | 161.77 | 153.31
2019-09-02 13:30 | 162.69 | 154.76
2019-09-02 14:00 | 162.91 | 154.92
2019-09-02 14:30 | 163.51 | 155.8
2019-09-02 15:00 | 163.74 | 156.49
2019-09-02 15:30 | 165.85 | 158.09
2019-09-02 16:00 | 200.61 | 193.15
2019-09-02 16:30 | 230.64 | 222.96
2019-09-02 17:00 | 239.7 | 231.03
2019-09-02 17:30 | 242.02 | 233.34
2019-09-02 18:00 | 242.83 | 235.2
2019-09-02 18:30 | 247 | 239.4
2019-09-02 19:00 | 247.96 | 240.56
2019-09-02 19:30 | 246.75 | 239.18
2019-09-02 20:00 | 246.37 | 238.81
2019-09-02 20:30 | 245.08 | 237.4
2019-09-02 21:00 | 243.57 | 236.34
2019-09-02 21:30 | 242.02 | 235.75
2019-09-02 22:00 | 240.48 | 234.49
2019-09-02 22:30 | 238.16 | 231.92
2019-09-02 23:00 | 237.02 | 230.4
2019-09-02 23:30 | 236.24 | 229.95
2019-09-03 | 235.33 | 228.66
2019-09-03 00:30 | 234.28 | 227.97
2019-09-03 01:00 | 233.26 | 227.15
2019-09-03 01:30 | 231.39 | 226.06
2019-09-03 02:00 | 231.19 | 226.13
2019-09-03 02:30 | 231.02 | 225.9
2019-09-03 03:00 | 231.27 | 226.21
2019-09-03 03:30 | 231.63 | 226.56
2019-09-03 04:00 | 232.19 | 227.21
2019-09-03 04:30 | 232.76 | 228.04
2019-09-03 05:00 | 233.92 | 229.23
2019-09-03 05:30 | 236.04 | 231.6
2019-09-03 06:00 | 239.43 | 234.64
2019-09-03 06:30 | 243.03 | 238.86
2019-09-03 07:00 | 246.61 | 242.16
2019-09-03 07:30 | 245.55 | 241.22
2019-09-03 08:00 | 243.11 | 238.32
2019-09-03 08:30 | 221.89 | 216.99
2019-09-03 09:00 | 181.44 | 176.29
2019-09-03 09:30 | 166.61 | 160.65
2019-09-03 10:00 | 164.14 | 157.95
2019-09-03 10:30 | 163.91 | 156.73
2019-09-03 11:00 | 163.29 | 155.15
2019-09-03 11:30 | 163.22 | 155.04
2019-09-03 12:00 | 162.4 | 154.41
2019-09-03 12:30 | 162.15 | 154.03
2019-09-03 13:00 | 162.08 | 154.38
2019-09-03 13:30 | 163.07 | 155.55
2019-09-03 14:00 | 162.78 | 156.27
2019-09-03 14:30 | 163.83 | 157.37
2019-09-03 15:00 | 164.52 | 158.49
2019-09-03 15:30 | 166.23 | 160.08
2019-09-03 16:00 | 198.75 | 192.18
2019-09-03 16:30 | 228.05 | 220.59
2019-09-03 17:00 | 236.62 | 229.03
2019-09-03 17:30 | 242.04 | 234.13
2019-09-03 18:00 | 244.74 | 236.51
2019-09-03 18:30 | 246.71 | 239.1
2019-09-03 19:00 | 247.87 | 240.62
2019-09-03 19:30 | 246.01 | 238.83
2019-09-03 20:00 | 244.01 | 236.53
2019-09-03 20:30 | 242.68 | 234.76
2019-09-03 21:00 | 240.92 | 233.36
2019-09-03 21:30 | 238.82 | 232.04
2019-09-03 22:00 | 237.24 | 230.44
2019-09-03 22:30 | 236.06 | 229
2019-09-03 23:00 | 234.7 | 227.56
2019-09-03 23:30 | 234.02 | 226.84
2019-09-04 | 232.36 | 225.28
2019-09-04 00:30 | 232.39 | 225.08
2019-09-04 01:00 | 230.68 | 224.51
2019-09-04 01:30 | 229.73 | 223.94
2019-09-04 02:00 | 229.36 | 223.26
2019-09-04 02:30 | 228.78 | 222.27
2019-09-04 03:00 | 228.61 | 222.05
2019-09-04 03:30 | 228.19 | 221.49
2019-09-04 04:00 | 228.37 | 221.56
2019-09-04 04:30 | 229.44 | 222.58
2019-09-04 05:00 | 231.08 | 224.17
2019-09-04 05:30 | 232.57 | 226.15
2019-09-04 06:00 | 235.98 | 229.93
2019-09-04 06:30 | 240.67 | 234.36
2019-09-04 07:00 | 243.58 | 236.59
2019-09-04 07:30 | 243.4 | 235.95
2019-09-04 08:00 | 226.33 | 217.97
2019-09-04 08:30 | 216.11 | 208.59
2019-09-04 09:00 | 214.53 | 206.81
2019-09-04 09:30 | 212.47 | 204.03
2019-09-04 10:00 | 209.62 | 201.24
2019-09-04 10:30 | 207.45 | 199.09
2019-09-04 11:00 | 183.95 | 175.44
2019-09-04 11:30 | 163.48 | 154.48
2019-09-04 12:00 | 164.88 | 155.5
2019-09-04 12:30 | 164.64 | 155.04
2019-09-04 13:00 | 165.17 | 155.77
2019-09-04 13:30 | 166.4 | 157.48
2019-09-04 14:00 | 166.27 | 157.98
2019-09-04 14:30 | 166.47 | 158.35
2019-09-04 15:00 | 167.97 | 159.44
2019-09-04 15:30 | 169.26 | 160.77
2019-09-04 16:00 | 172.4 | 162.72
2019-09-04 16:30 | 174.04 | 164.27
2019-09-04 17:00 | 175.66 | 165.98
2019-09-04 17:30 | 209.12 | 199.42
2019-09-04 18:00 | 238.9 | 230.78
2019-09-04 18:30 | 245.87 | 239.15
2019-09-04 19:00 | 246.75 | 240.51
2019-09-04 19:30 | 245.29 | 239.13
2019-09-04 20:00 | 242.72 | 236.55
2019-09-04 20:30 | 240.93 | 234.43
2019-09-04 21:00 | 239.13 | 232.47
2019-09-04 21:30 | 237.46 | 231.42
2019-09-04 22:00 | 235.24 | 229.15
2019-09-04 22:30 | 233.37 | 227.18
2019-09-04 23:00 | 233.02 | 225.87
2019-09-04 23:30 | 232.56 | 224.85
2019-09-05 | 231.43 | 224.14
2019-09-05 00:30 | 231.13 | 223.71
2019-09-05 01:00 | 229.46 | 222.81
2019-09-05 01:30 | 228.53 | 221.9
2019-09-05 02:00 | 228.39 | 221.59
2019-09-05 02:30 | 227.75 | 221.26
2019-09-05 03:00 | 227.01 | 220.8
2019-09-05 03:30 | 227.2 | 219.91
2019-09-05 04:00 | 226.63 | 219.42
2019-09-05 04:30 | 227.79 | 220.7
2019-09-05 05:00 | 228.84 | 221.92
2019-09-05 05:30 | 231.11 | 224.14
2019-09-05 06:00 | 235.9 | 227.72
2019-09-05 06:30 | 239 | 230.87
2019-09-05 07:00 | 241.84 | 233.75
2019-09-05 07:30 | 245.01 | 238.07
2019-09-05 08:00 | 244.25 | 237.21
2019-09-05 08:30 | 241.69 | 233.9
2019-09-05 09:00 | 222.18 | 214.38
2019-09-05 09:30 | 184.25 | 175.76
2019-09-05 10:00 | 169.62 | 159.77
2019-09-05 10:30 | 168.65 | 159.12
2019-09-05 11:00 | 170.91 | 159.24
2019-09-05 11:30 | 169.4 | 159.79
2019-09-05 12:00 | 169.25 | 161.33
2019-09-05 12:30 | 170.16 | 161.92
2019-09-05 13:00 | 169.21 | 161.41
2019-09-05 13:30 | 169.39 | 163.5
2019-09-05 14:00 | 169.93 | 164.43
2019-09-05 14:30 | 169.82 | 164.82
2019-09-05 15:00 | 170.77 | 165.9
2019-09-05 15:30 | 171.74 | 166.75
2019-09-05 16:00 | 173.1 | 168.04
2019-09-05 16:30 | 174.91 | 169.8
2019-09-05 17:00 | 176.89 | 171.91
2019-09-05 17:30 | 212.55 | 207.31
2019-09-05 18:00 | 241.79 | 236.52
2019-09-05 18:30 | 249.06 | 243.79
2019-09-05 19:00 | 250.63 | 245.2
2019-09-05 19:30 | 249.26 | 243.76
2019-09-05 20:00 | 247.2 | 241.38
2019-09-05 20:30 | 245.88 | 240.17
2019-09-05 21:00 | 244.26 | 238.57
2019-09-05 21:30 | 243.59 | 238.26
2019-09-05 22:00 | 239.25 | 234.33
2019-09-05 22:30 | 230.82 | 226.65
2019-09-05 23:00 | 231.46 | 225.15
2019-09-05 23:30 | 231.77 | 225.51
2019-09-06 | 227.45 | 221.41
2019-09-06 00:30 | 229.1 | 223.31
2019-09-06 01:00 | 228.26 | 223.25
2019-09-06 01:30 | 227.29 | 222.18
2019-09-06 02:00 | 226.93 | 221.8
2019-09-06 02:30 | 227.76 | 222.19
2019-09-06 03:00 | 227.95 | 222.38
2019-09-06 03:30 | 228.64 | 223.01
2019-09-06 04:00 | 230.01 | 224.27
2019-09-06 04:30 | 232.02 | 226.26
2019-09-06 05:00 | 234.1 | 228.39
2019-09-06 05:30 | 236.75 | 231.33
2019-09-06 06:00 | 238.75 | 233.63
2019-09-06 06:30 | 242.53 | 236.68
2019-09-06 07:00 | 244.73 | 237.59
2019-09-06 07:30 | 246.01 | 238.58
2019-09-06 08:00 | 244.09 | 236.8
2019-09-06 08:30 | 240.98 | 234.32
2019-09-06 09:00 | 221.1 | 214.76
2019-09-06 09:30 | 182.58 | 175.54
2019-09-06 10:00 | 169.02 | 161.26
2019-09-06 10:30 | 167.65 | 160.36
2019-09-06 11:00 | 167.43 | 159.86
2019-09-06 11:30 | 167.39 | 160.06
2019-09-06 12:00 | 167.93 | 160.66
2019-09-06 12:30 | 170.08 | 162.1
2019-09-06 13:00 | 171.35 | 162.64
2019-09-06 13:30 | 171.57 | 163.29
2019-09-06 14:00 | 172.48 | 164.62
2019-09-06 14:30 | 173.46 | 165.93
2019-09-06 15:00 | 175.49 | 166.82
2019-09-06 15:30 | 208.43 | 199.53
2019-09-06 16:00 | 238.8 | 231.12
2019-09-06 16:30 | 245.24 | 237.38
2019-09-06 17:00 | 248.05 | 239.07
2019-09-06 17:30 | 248.93 | 239.15
2019-09-06 18:00 | 250.71 | 240.82
2019-09-06 18:30 | 251.67 | 242.3
2019-09-06 19:00 | 249.99 | 242.37
2019-09-06 19:30 | 248.54 | 241.04
2019-09-06 20:00 | 247.16 | 239.41
2019-09-06 20:30 | 246.33 | 238.23
2019-09-06 21:00 | 244.7 | 237.02
2019-09-06 21:30 | 240.39 | 233.73
2019-09-06 22:00 | 242.14 | 235.6
2019-09-06 22:30 | 240.26 | 233.76
2019-09-06 23:00 | 238.04 | 232.06
2019-09-06 23:30 | 239.93 | 231.67
2019-09-07 | 239.94 | 230.51
2019-09-07 00:30 | 239.49 | 229.47
2019-09-07 01:00 | 242.33 | 228.97
2019-09-07 01:30 | 242.49 | 228
2019-09-07 02:00 | 242.83 | 227.69
2019-09-07 02:30 | 242.46 | 226.74
2019-09-07 03:00 | 243.3 | 226.77
2019-09-07 03:30 | 226.98 | 209.89
2019-09-07 04:00 | 190.63 | 173
2019-09-07 04:30 | 177.35 | 159.23
2019-09-07 05:00 | 177.34 | 159.02
2019-09-07 05:30 | 178.49 | 160.34
2019-09-07 06:00 | 178.74 | 161.24
2019-09-07 06:30 | 178.06 | 162.4
2019-09-07 07:00 | 177.37 | 163.14
2019-09-07 07:30 | 178.16 | 163.9
2019-09-07 08:00 | 179.82 | 162.98
2019-09-07 08:30 | 181 | 162.25
2019-09-07 09:00 | 180.38 | 161.1
2019-09-07 09:30 | 179.66 | 159.4
2019-09-07 10:00 | 178.78 | 159.1
2019-09-07 10:30 | 178.02 | 157.03
2019-09-07 11:00 | 177.16 | 156.3
2019-09-07 11:30 | 175.5 | 155.52
2019-09-07 12:00 | 174.87 | 154.97
2019-09-07 12:30 | 175.42 | 155.12
2019-09-07 13:00 | 174.55 | 154.76
2019-09-07 13:30 | 175 | 154.68
2019-09-07 14:00 | 174.35 | 154.7
2019-09-07 14:30 | 175.53 | 155.09
2019-09-07 15:00 | 177.27 | 156.54
2019-09-07 15:30 | 181.29 | 158.04
2019-09-07 16:00 | 182.06 | 160.1
2019-09-07 16:30 | 182 | 162.46
2019-09-07 17:00 | 209.53 | 197.85
2019-09-07 17:30 | 239.29 | 229.97
2019-09-07 18:00 | 246.49 | 237.69
2019-09-07 18:30 | 248.09 | 239.53
2019-09-07 19:00 | 248.78 | 240.21
2019-09-07 19:30 | 248.43 | 239.61
2019-09-07 20:00 | 247.85 | 238.78
2019-09-07 20:30 | 246.08 | 237.48
2019-09-07 21:00 | 244.49 | 235.63
2019-09-07 21:30 | 243.71 | 235.76
2019-09-07 22:00 | 242.58 | 234.87
2019-09-07 22:30 | 241.23 | 233.82
2019-09-07 23:00 | 240.12 | 232.43
2019-09-07 23:30 | 239.34 | 232.65
2019-09-08 | 238.17 | 231.25
2019-09-08 00:30 | 220.37 | 214.18
2019-09-08 01:00 | 184.05 | 177
2019-09-08 01:30 | 168.81 | 161.88
2019-09-08 02:00 | 169.59 | 161.79
2019-09-08 02:30 | 169.93 | 161.82
2019-09-08 03:00 | 169.38 | 161.08
2019-09-08 03:30 | 169.63 | 161.26
2019-09-08 04:00 | 170.38 | 162.26
2019-09-08 04:30 | 205.17 | 197.41
2019-09-08 05:00 | 227.78 | 220.12
2019-09-08 05:30 | 228.08 | 220.84
2019-09-08 06:00 | 229.16 | 222.26
2019-09-08 06:30 | 229.33 | 223.54
2019-09-08 07:00 | 229.43 | 224.72
2019-09-08 07:30 | 194.03 | 189.24
2019-09-08 08:00 | 171.66 | 166.35
2019-09-08 08:30 | 169.97 | 163.64
2019-09-08 09:00 | 170.24 | 162.73
2019-09-08 09:30 | 168.83 | 161.57
2019-09-08 10:00 | 166.9 | 159.46
2019-09-08 10:30 | 164.82 | 157.94
2019-09-08 11:00 | 163.88 | 156.55
2019-09-08 11:30 | 164.44 | 155.98
2019-09-08 12:00 | 164.74 | 155.98
2019-09-08 12:30 | 164.36 | 154.89
2019-09-08 13:00 | 164.13 | 154.48
2019-09-08 13:30 | 163.51 | 154.89
2019-09-08 14:00 | 163.22 | 154.9
2019-09-08 14:30 | 163.3 | 154.92
2019-09-08 15:00 | 163.95 | 156.12
2019-09-08 15:30 | 165.83 | 158.06
2019-09-08 16:00 | 169.39 | 160.42
2019-09-08 16:30 | 173.28 | 163.16
2019-09-08 17:00 | 209.46 | 199.9
2019-09-08 17:30 | 233.32 | 224.25
2019-09-08 18:00 | 237.88 | 229.5
2019-09-08 18:30 | 239.97 | 232.37
2019-09-08 19:00 | 240.89 | 233.38
2019-09-08 19:30 | 240.43 | 232.96
2019-09-08 20:00 | 238.85 | 231
2019-09-08 20:30 | 237.8 | 229.27
2019-09-08 21:00 | 236.68 | 228.17
2019-09-08 21:30 | 235.65 | 227.98
2019-09-08 22:00 | 234.16 | 226.6
2019-09-08 22:30 | 232.7 | 224.59
2019-09-08 23:00 | 230.42 | 223.12
2019-09-08 23:30 | 229.07 | 222.27
2019-09-09 | 227.79 | 221.43
2019-09-09 00:30 | 227.72 | 220.95
2019-09-09 01:00 | 218.7 | 212.6
2019-09-09 01:30 | 181.19 | 175.99
2019-09-09 02:00 | 167.76 | 162.54
2019-09-09 02:30 | 167.86 | 162.51
2019-09-09 03:00 | 168.24 | 162.81
2019-09-09 03:30 | 168.55 | 162.77
2019-09-09 04:00 | 168.54 | 162.69
2019-09-09 04:30 | 169.84 | 164.22
2019-09-09 05:00 | 169.69 | 164.68
2019-09-09 05:30 | 172.68 | 167.82
2019-09-09 06:00 | 175.01 | 169.82
2019-09-09 06:30 | 178.89 | 174.61
2019-09-09 07:00 | 181.06 | 176.69
2019-09-09 07:30 | 181.4 | 176.81
2019-09-09 08:00 | 179.76 | 175.37
2019-09-09 08:30 | 176.02 | 171.49
2019-09-09 09:00 | 172.3 | 167.18
2019-09-09 09:30 | 169.22 | 163.74
2019-09-09 10:00 | 168.34 | 162.52
2019-09-09 10:30 | 167.29 | 160.89
2019-09-09 11:00 | 166.49 | 159.67
2019-09-09 11:30 | 165.35 | 158.51
2019-09-09 12:00 | 165.29 | 158.32
2019-09-09 12:30 | 164.61 | 157.52
2019-09-09 13:00 | 163.92 | 157.39
2019-09-09 13:30 | 165.45 | 158.94
2019-09-09 14:00 | 165.72 | 159
2019-09-09 14:30 | 165.23 | 158.96
2019-09-09 15:00 | 166.29 | 160.23
2019-09-09 15:30 | 168.96 | 161.61
2019-09-09 16:00 | 171.14 | 163.19
2019-09-09 16:30 | 172.99 | 164.93
2019-09-09 17:00 | 209.49 | 201.37
2019-09-09 17:30 | 232.55 | 223.86
2019-09-09 18:00 | 239.6 | 231.32
2019-09-09 18:30 | 252.17 | 244.25
2019-09-09 19:00 | 256.65 | 248.82
2019-09-09 19:30 | 255.68 | 247.8
2019-09-09 20:00 | 253.65 | 245.64
2019-09-09 20:30 | 251.47 | 244.94
2019-09-09 21:00 | 249.91 | 243.43
2019-09-09 21:30 | 248.64 | 242.03
2019-09-09 22:00 | 246.08 | 239.82
2019-09-09 22:30 | 243.75 | 237.22
2019-09-09 23:00 | 241.23 | 235.23
2019-09-09 23:30 | 239.75 | 234.04
2019-09-10 | 238.88 | 233.26
2019-09-10 00:30 | 238.16 | 232.62
2019-09-10 01:00 | 237.48 | 231.68
2019-09-10 01:30 | 237.33 | 231.54
2019-09-10 02:00 | 236.41 | 230.79
2019-09-10 02:30 | 235.45 | 230.14
2019-09-10 03:00 | 235.41 | 230.14
2019-09-10 03:30 | 235.49 | 230.39
2019-09-10 04:00 | 235.7 | 230.61
2019-09-10 04:30 | 236.71 | 231.78
2019-09-10 05:00 | 238.71 | 233.99
2019-09-10 05:30 | 242.12 | 236.8
2019-09-10 06:00 | 245.93 | 240.32
2019-09-10 06:30 | 249.93 | 245.16
2019-09-10 07:00 | 251.45 | 247.02
2019-09-10 07:30 | 252.28 | 247.83
2019-09-10 08:00 | 250.24 | 245.35
2019-09-10 08:30 | 247.19 | 241.88
2019-09-10 09:00 | 243.46 | 237.35
2019-09-10 09:30 | 224.7 | 217.91
2019-09-10 10:00 | 184.34 | 176.86
2019-09-10 10:30 | 170.28 | 162.46
2019-09-10 11:00 | 169.63 | 161.29
2019-09-10 11:30 | 167.59 | 159.47
2019-09-10 12:00 | 167.43 | 158.97
2019-09-10 12:30 | 166.79 | 158.53
2019-09-10 13:00 | 166.15 | 157.95
2019-09-10 13:30 | 165.73 | 158.11
2019-09-10 14:00 | 165.91 | 158.61
2019-09-10 14:30 | 165.92 | 159.31
2019-09-10 15:00 | 167.69 | 160.84
2019-09-10 15:30 | 174.25 | 167.38
2019-09-10 16:00 | 175.02 | 167.69
2019-09-10 16:30 | 209.38 | 202.42
2019-09-10 17:00 | 241.25 | 234.02
2019-09-10 17:30 | 249.21 | 241.87
2019-09-10 18:00 | 251.64 | 245.82
2019-09-10 18:30 | 254.88 | 249.82
2019-09-10 19:00 | 256.82 | 252.16
2019-09-10 19:30 | 255.86 | 250.98
2019-09-10 20:00 | 255.16 | 250.18
2019-09-10 20:30 | 254.08 | 248.9
2019-09-10 21:00 | 252.07 | 246.14
2019-09-10 21:30 | 250.6 | 244.12
2019-09-10 22:00 | 247.92 | 240.99
2019-09-10 22:30 | 245.15 | 238.51
2019-09-10 23:00 | 243.38 | 236.58
2019-09-10 23:30 | 241.62 | 235.94
2019-09-11 | 238.7 | 233.69
2019-09-11 00:30 | 238.76 | 233.84
2019-09-11 01:00 | 237.86 | 232.57
2019-09-11 01:30 | 236.79 | 231.25
2019-09-11 02:00 | 236.2 | 230.67
2019-09-11 02:30 | 235.9 | 230.28
2019-09-11 03:00 | 235.69 | 230.09
2019-09-11 03:30 | 236.2 | 230.54
2019-09-11 04:00 | 236.17 | 230.53
2019-09-11 04:30 | 237.3 | 231.78
2019-09-11 05:00 | 239.38 | 234.05
2019-09-11 05:30 | 242.07 | 236.41
2019-09-11 06:00 | 245.78 | 239.45
2019-09-11 06:30 | 249.7 | 244.66
2019-09-11 07:00 | 252.48 | 247.57
2019-09-11 07:30 | 252.23 | 247.48
2019-09-11 08:00 | 249.75 | 244.51
2019-09-11 08:30 | 245.48 | 239.63
2019-09-11 09:00 | 225.11 | 218.7
2019-09-11 09:30 | 183.77 | 176.96
2019-09-11 10:00 | 168.7 | 161.72
2019-09-11 10:30 | 165.55 | 158.95
2019-09-11 11:00 | 195.87 | 189.96
2019-09-11 11:30 | 209.7 | 203.96
2019-09-11 12:00 | 210.47 | 203.8
2019-09-11 12:30 | 210.43 | 202.95
2019-09-11 13:00 | 209.97 | 202.7
2019-09-11 13:30 | 210.23 | 203.34
2019-09-11 14:00 | 222.78 | 215.8
2019-09-11 14:30 | 230.71 | 223.43
2019-09-11 15:00 | 231.33 | 224
2019-09-11 15:30 | 233.25 | 225.8
2019-09-11 16:00 | 234.18 | 226.99
2019-09-11 16:30 | 236.06 | 229.28
2019-09-11 17:00 | 238.19 | 231.43
2019-09-11 17:30 | 240.92 | 233.61
2019-09-11 18:00 | 243.84 | 236.37
2019-09-11 18:30 | 247.8 | 239.96
2019-09-11 19:00 | 250.32 | 242.67
2019-09-11 19:30 | 249.58 | 242.01
2019-09-11 20:00 | 247.31 | 240.28
2019-09-11 20:30 | 246.78 | 240.1
2019-09-11 21:00 | 245.03 | 238.49
2019-09-11 21:30 | 243.97 | 237.77
2019-09-11 22:00 | 242.86 | 236.26
2019-09-11 22:30 | 241.08 | 234.3
2019-09-11 23:00 | 239.84 | 232.53
2019-09-11 23:30 | 238.41 | 231.6
2019-09-12 | 236.74 | 230.62
2019-09-12 00:30 | 236.57 | 230.46
2019-09-12 01:00 | 235.56 | 229.8
2019-09-12 01:30 | 234.56 | 229.04
2019-09-12 02:00 | 234.03 | 228.74
2019-09-12 02:30 | 233.75 | 228.48
2019-09-12 03:00 | 233.88 | 228.48
2019-09-12 03:30 | 234.68 | 229.06
2019-09-12 04:00 | 235.65 | 229.61
2019-09-12 04:30 | 237.49 | 230.86
2019-09-12 05:00 | 238.74 | 231.81
2019-09-12 05:30 | 240.79 | 234.34
2019-09-12 06:00 | 242.64 | 236.39
2019-09-12 06:30 | 246.52 | 241.21
2019-09-12 07:00 | 249.54 | 243.43
2019-09-12 07:30 | 249.09 | 243.23
2019-09-12 08:00 | 245.25 | 239.7
2019-09-12 08:30 | 241.43 | 235.25
2019-09-12 09:00 | 237.49 | 231.39
2019-09-12 09:30 | 217.13 | 210.55
2019-09-12 10:00 | 176.26 | 170.94
2019-09-12 10:30 | 162.92 | 157.24
2019-09-12 11:00 | 163.29 | 156.14
2019-09-12 11:30 | 163.96 | 156.74
2019-09-12 12:00 | 163.95 | 156.75
2019-09-12 12:30 | 163.26 | 155.93
2019-09-12 13:00 | 163.48 | 155.77
2019-09-12 13:30 | 163.61 | 156.17
2019-09-12 14:00 | 163.89 | 157.36
2019-09-12 14:30 | 163.56 | 156.95
2019-09-12 15:00 | 166.6 | 160.05
2019-09-12 15:30 | 169.23 | 162.81
2019-09-12 16:00 | 171.3 | 164.88
2019-09-12 16:30 | 204.88 | 198.96
2019-09-12 17:00 | 236.33 | 230.51
2019-09-12 17:30 | 243.72 | 237.56
2019-09-12 18:00 | 245.9 | 239.72
2019-09-12 18:30 | 250.1 | 244.07
2019-09-12 19:00 | 250.94 | 244.18
2019-09-12 19:30 | 249.52 | 242.7
2019-09-12 20:00 | 248.31 | 241.27
2019-09-12 20:30 | 247.63 | 240.09
2019-09-12 21:00 | 246.33 | 239.07
2019-09-12 21:30 | 245.23 | 238.48
2019-09-12 22:00 | 244.28 | 237.43
2019-09-12 22:30 | 241.74 | 234.68
2019-09-12 23:00 | 240.4 | 233.03
2019-09-12 23:30 | 238.36 | 230.93
2019-09-13 | 236.25 | 229.38
2019-09-13 00:30 | 235.18 | 228.64
2019-09-13 01:00 | 234.51 | 228.41
2019-09-13 01:30 | 233.6 | 228
2019-09-13 02:00 | 233.12 | 227.33
2019-09-13 02:30 | 232.54 | 226.92
2019-09-13 03:00 | 232.96 | 227.49
2019-09-13 03:30 | 233.43 | 228.02
2019-09-13 04:00 | 233.75 | 228.44
2019-09-13 04:30 | 234.37 | 229.18
2019-09-13 05:00 | 234.72 | 229.91
2019-09-13 05:30 | 237.51 | 232.43
2019-09-13 06:00 | 240.36 | 235.3
2019-09-13 06:30 | 244.5 | 239.69
2019-09-13 07:00 | 247.81 | 242.23
2019-09-13 07:30 | 247.76 | 241.91
2019-09-13 08:00 | 244.18 | 238.06
2019-09-13 08:30 | 240.2 | 233.75
2019-09-13 09:00 | 238.27 | 231.82
2019-09-13 09:30 | 219.58 | 213.4
2019-09-13 10:00 | 180.34 | 173.05
2019-09-13 10:30 | 165.96 | 158.47
2019-09-13 11:00 | 165.01 | 157.62
2019-09-13 11:30 | 161.66 | 154.62
2019-09-13 12:00 | 158.49 | 152.04
2019-09-13 12:30 | 159.1 | 151.77
2019-09-13 13:00 | 158.86 | 152.09
2019-09-13 13:30 | 161.56 | 154.79
2019-09-13 14:00 | 164.88 | 158.65
2019-09-13 14:30 | 165.1 | 158.74
2019-09-13 15:00 | 198.15 | 192.07
2019-09-13 15:30 | 228.45 | 222.42
2019-09-13 16:00 | 237.26 | 230.73
2019-09-13 16:30 | 239.17 | 232.63
2019-09-13 17:00 | 242.14 | 234.99
2019-09-13 17:30 | 243.14 | 235.86
2019-09-13 18:00 | 244.46 | 236.98
2019-09-13 18:30 | 245.84 | 238.39
2019-09-13 19:00 | 246.91 | 239.55
2019-09-13 19:30 | 246.5 | 238.87
2019-09-13 20:00 | 244.44 | 236.8
2019-09-13 20:30 | 243.04 | 235.18
2019-09-13 21:00 | 243.04 | 235.14
2019-09-13 21:30 | 241.58 | 234.45
2019-09-13 22:00 | 241.22 | 233.99
2019-09-13 22:30 | 239.42 | 232.44
2019-09-13 23:00 | 238.43 | 231.5
2019-09-13 23:30 | 236.93 | 230.55
2019-09-14 | 236.34 | 229.68
2019-09-14 00:30 | 235.03 | 229.14
2019-09-14 01:00 | 234.49 | 228.8
2019-09-14 01:30 | 233.05 | 227.4
2019-09-14 02:00 | 232.14 | 226.57
2019-09-14 02:30 | 232.66 | 226.37
2019-09-14 03:00 | 232.4 | 226.12
2019-09-14 03:30 | 232.37 | 225.85
2019-09-14 04:00 | 232.2 | 225.73
2019-09-14 04:30 | 233 | 226.59
2019-09-14 05:00 | 234.02 | 227.75
2019-09-14 05:30 | 234.7 | 228.47
2019-09-14 06:00 | 235.75 | 229.68
2019-09-14 06:30 | 236.93 | 231.59
2019-09-14 07:00 | 237.08 | 231.78
2019-09-14 07:30 | 236.77 | 231.28
2019-09-14 08:00 | 217.34 | 211.9
2019-09-14 08:30 | 180.08 | 175.07
2019-09-14 09:00 | 164.57 | 158.63
2019-09-14 09:30 | 165.55 | 158.49
2019-09-14 10:00 | 163.95 | 156.45
2019-09-14 10:30 | 163.04 | 154.96
2019-09-14 11:00 | 162.42 | 153.85
2019-09-14 11:30 | 162 | 153.35
2019-09-14 12:00 | 162.64 | 153.76
2019-09-14 12:30 | 163.19 | 153.96
2019-09-14 13:00 | 162.3 | 153.13
2019-09-14 13:30 | 161.08 | 151.82
2019-09-14 14:00 | 159.84 | 151
2019-09-14 14:30 | 160.41 | 151.93
2019-09-14 15:00 | 162.17 | 153.97
2019-09-14 15:30 | 165.77 | 156.81
2019-09-14 16:00 | 166.24 | 158.43
2019-09-14 16:30 | 168.04 | 160.4
2019-09-14 17:00 | 203.53 | 195.79
2019-09-14 17:30 | 236.1 | 228.29
2019-09-14 18:00 | 243.16 | 235.55
2019-09-14 18:30 | 244.46 | 236.78
2019-09-14 19:00 | 245.83 | 238.07
2019-09-14 19:30 | 244.31 | 236.31
2019-09-14 20:00 | 243.54 | 235.2
2019-09-14 20:30 | 242.16 | 233.67
2019-09-14 21:00 | 240.41 | 232.6
2019-09-14 21:30 | 239.64 | 232.12
2019-09-14 22:00 | 238.62 | 231.24
2019-09-14 22:30 | 236.98 | 229.67
2019-09-14 23:00 | 235.91 | 228.8
2019-09-14 23:30 | 234.99 | 228.14
2019-09-15 | 233.87 | 227.03
2019-09-15 00:30 | 233 | 226.69
2019-09-15 01:00 | 231.17 | 225.42
2019-09-15 01:30 | 230.26 | 224.51
2019-09-15 02:00 | 230.03 | 224.47
2019-09-15 02:30 | 213.56 | 208.15
2019-09-15 03:00 | 208.88 | 203.63
2019-09-15 03:30 | 210.83 | 204.52
2019-09-15 04:00 | 211.14 | 205.38
2019-09-15 04:30 | 210.7 | 205.04
2019-09-15 05:00 | 211.16 | 205.35
2019-09-15 05:30 | 211.56 | 205.84
2019-09-15 06:00 | 212.13 | 207.11
2019-09-15 06:30 | 213.99 | 208.63
2019-09-15 07:00 | 215.15 | 208.95
2019-09-15 07:30 | 182.1 | 176.06
2019-09-15 08:00 | 165.17 | 159.79
2019-09-15 08:30 | 164.46 | 159.12
2019-09-15 09:00 | 163.49 | 157.95
2019-09-15 09:30 | 161.12 | 155.56
2019-09-15 10:00 | 157.72 | 152.36
2019-09-15 10:30 | 156.14 | 150.61
2019-09-15 11:00 | 154.6 | 148.9
2019-09-15 11:30 | 153.73 | 147.83
2019-09-15 12:00 | 155.06 | 148.57
2019-09-15 12:30 | 157.12 | 149.53
2019-09-15 13:00 | 157.09 | 149.14
2019-09-15 13:30 | 158.21 | 149.76
2019-09-15 14:00 | 158.34 | 150.62
2019-09-15 14:30 | 161.35 | 151.5
2019-09-15 15:00 | 160.6 | 151.91
2019-09-15 15:30 | 163.09 | 154.17
2019-09-15 16:00 | 165.71 | 157.13
2019-09-15 16:30 | 169.05 | 159.49
2019-09-15 17:00 | 171.86 | 161.38
2019-09-15 17:30 | 200.2 | 192.35
2019-09-15 18:00 | 232.29 | 224.51
2019-09-15 18:30 | 238.49 | 230.55
2019-09-15 19:00 | 239.87 | 231.89
2019-09-15 19:30 | 237.72 | 229.74
2019-09-15 20:00 | 236 | 228.25
2019-09-15 20:30 | 234.7 | 226.88
2019-09-15 21:00 | 233.6 | 225.43
2019-09-15 21:30 | 233.04 | 224.87
2019-09-15 22:00 | 232.4 | 224.28
2019-09-15 22:30 | 230.97 | 222.41
2019-09-15 23:00 | 228.71 | 220.56
2019-09-15 23:30 | 226.61 | 219.55
2019-09-16 | 225.51 | 218.74
2019-09-16 00:30 | 227.17 | 218.75
2019-09-16 01:00 | 225.8 | 217.94
2019-09-16 01:30 | 225.15 | 217.79
2019-09-16 02:00 | 224.33 | 217.45
2019-09-16 02:30 | 223.88 | 217.2
2019-09-16 03:00 | 223.93 | 217.22
2019-09-16 03:30 | 224.25 | 217.04
2019-09-16 04:00 | 224.95 | 217.37
2019-09-16 04:30 | 225.44 | 218.23
2019-09-16 05:00 | 225.72 | 219.02
2019-09-16 05:30 | 228.55 | 220.85
2019-09-16 06:00 | 231.7 | 222.92
2019-09-16 06:30 | 234.22 | 225.83
2019-09-16 07:00 | 236.08 | 228.46
2019-09-16 07:30 | 240.41 | 233.53
2019-09-16 08:00 | 238.45 | 231.28
2019-09-16 08:30 | 234.93 | 227.98
2019-09-16 09:00 | 232.17 | 225.54
2019-09-16 09:30 | 216.33 | 209.03
2019-09-16 10:00 | 211.28 | 204.23
2019-09-16 10:30 | 210.22 | 203.03
2019-09-16 11:00 | 208.9 | 201.81
2019-09-16 11:30 | 209.29 | 202.56
2019-09-16 12:00 | 209.62 | 202.71
2019-09-16 12:30 | 210.35 | 203.24
2019-09-16 13:00 | 211.21 | 203.94
2019-09-16 13:30 | 213.08 | 205.4
2019-09-16 14:00 | 213.89 | 206.48
2019-09-16 14:30 | 213.8 | 207.09
2019-09-16 15:00 | 214.51 | 208
2019-09-16 15:30 | 233.13 | 226.75
2019-09-16 16:00 | 239.31 | 233.13
2019-09-16 16:30 | 241.36 | 234.7
2019-09-16 17:00 | 243.03 | 236.47
2019-09-16 17:30 | 245.02 | 237.79
2019-09-16 18:00 | 246.95 | 239.64
2019-09-16 18:30 | 249.45 | 242.17
2019-09-16 19:00 | 250.62 | 243.62
2019-09-16 19:30 | 248.67 | 241.68
2019-09-16 20:00 | 247.15 | 239.7
2019-09-16 20:30 | 245.81 | 237.84
2019-09-16 21:00 | 243.06 | 235.09
2019-09-16 21:30 | 241.98 | 234.23
2019-09-16 22:00 | 240.7 | 233.32
2019-09-16 22:30 | 238.91 | 231.57
2019-09-16 23:00 | 237.85 | 229.75
2019-09-16 23:30 | 236.31 | 228.75
2019-09-17 | 234 | 227.9
2019-09-17 00:30 | 233.61 | 227.23
2019-09-17 01:00 | 232.21 | 226.88
2019-09-17 01:30 | 231.24 | 225.86
2019-09-17 02:00 | 233.03 | 225.66
2019-09-17 02:30 | 232.63 | 225.55
2019-09-17 03:00 | 232.78 | 225.43
2019-09-17 03:30 | 232.24 | 225.17
2019-09-17 04:00 | 232.17 | 225.09
2019-09-17 04:30 | 233.2 | 225.51
2019-09-17 05:00 | 235.68 | 226.73
2019-09-17 05:30 | 236.63 | 228.04
2019-09-17 06:00 | 238.76 | 230.26
2019-09-17 06:30 | 239.93 | 233.35
2019-09-17 07:00 | 241.62 | 235.15
2019-09-17 07:30 | 242.17 | 235.31
2019-09-17 08:00 | 240.49 | 234.26
2019-09-17 08:30 | 221.29 | 215.03
2019-09-17 09:00 | 183.33 | 176.69
2019-09-17 09:30 | 166.7 | 160.16
2019-09-17 10:00 | 165.57 | 159.04
2019-09-17 10:30 | 164.87 | 158.3
2019-09-17 11:00 | 165.64 | 158.63
2019-09-17 11:30 | 165.91 | 158.76
2019-09-17 12:00 | 166.67 | 159.55
2019-09-17 12:30 | 167.51 | 159.89
2019-09-17 13:00 | 170.66 | 163.21
2019-09-17 13:30 | 171.85 | 165.4
2019-09-17 14:00 | 173.61 | 166.73
2019-09-17 14:30 | 175.82 | 168.73
2019-09-17 15:00 | 212.18 | 204.77
2019-09-17 15:30 | 239.58 | 231.56
2019-09-17 16:00 | 241.69 | 233.59
2019-09-17 16:30 | 243.06 | 235.11
2019-09-17 17:00 | 243.77 | 236.76
2019-09-17 17:30 | 245.86 | 239.04
2019-09-17 18:00 | 248.19 | 241.1
2019-09-17 18:30 | 251.08 | 243.84
2019-09-17 19:00 | 252.92 | 245.72
2019-09-17 19:30 | 250.52 | 243.03
2019-09-17 20:00 | 248.03 | 240.47
2019-09-17 20:30 | 247.28 | 239.7
2019-09-17 21:00 | 246.2 | 238.62
2019-09-17 21:30 | 245.42 | 237.99
2019-09-17 22:00 | 243 | 236.04
2019-09-17 22:30 | 241.69 | 234.75
2019-09-17 23:00 | 239.65 | 232.48
2019-09-17 23:30 | 239.77 | 232.24
2019-09-18 | 238.57 | 230.94
2019-09-18 00:30 | 237.48 | 230.3
2019-09-18 01:00 | 235.57 | 229.32
2019-09-18 01:30 | 234.94 | 229.03
2019-09-18 02:00 | 235.24 | 228.83
2019-09-18 02:30 | 234.8 | 228.79
2019-09-18 03:00 | 234.58 | 228.78
2019-09-18 03:30 | 234.19 | 228.31
2019-09-18 04:00 | 234.24 | 229.03
2019-09-18 04:30 | 234.49 | 229.53
2019-09-18 05:00 | 235.02 | 230.84
2019-09-18 05:30 | 238.23 | 232.46
2019-09-18 06:00 | 242.01 | 235.24
2019-09-18 06:30 | 246.21 | 238.97
2019-09-18 07:00 | 246.79 | 239.66
2019-09-18 07:30 | 247.33 | 240.32
2019-09-18 08:00 | 244.93 | 238.06
2019-09-18 08:30 | 241.38 | 234.31
2019-09-18 09:00 | 238.38 | 231.21
2019-09-18 09:30 | 235.75 | 228.62
2019-09-18 10:00 | 216.34 | 209.96
2019-09-18 10:30 | 179.59 | 172.86
2019-09-18 11:00 | 165.22 | 158.36
2019-09-18 11:30 | 164.44 | 157.8
2019-09-18 12:00 | 164.23 | 157.55
2019-09-18 12:30 | 164.17 | 157.59
2019-09-18 13:00 | 163.89 | 157.22
2019-09-18 13:30 | 198.55 | 192.06
2019-09-18 14:00 | 221.62 | 214.54
2019-09-18 14:30 | 229.11 | 221.37
2019-09-18 15:00 | 236.37 | 228.13
2019-09-18 15:30 | 237.82 | 229.33
2019-09-18 16:00 | 239.46 | 230.94
2019-09-18 16:30 | 240.49 | 233.07
2019-09-18 17:00 | 242.05 | 234.73
2019-09-18 17:30 | 243.82 | 236.31
2019-09-18 18:00 | 245.6 | 237.87
2019-09-18 18:30 | 248.17 | 240.59
2019-09-18 19:00 | 250.22 | 242.81
2019-09-18 19:30 | 250.6 | 243.28
2019-09-18 20:00 | 249.09 | 241.72
2019-09-18 20:30 | 247.81 | 239.95
2019-09-18 21:00 | 246.45 | 238.36
2019-09-18 21:30 | 246.82 | 238.41
2019-09-18 22:00 | 243.19 | 236.16
2019-09-18 22:30 | 240.21 | 234.38
2019-09-18 23:00 | 239.45 | 233.4
2019-09-18 23:30 | 238.55 | 233.02
2019-09-19 | 236.61 | 231.16
2019-09-19 00:30 | 236.08 | 231.36
2019-09-19 01:00 | 235.7 | 230.38
2019-09-19 01:30 | 235.48 | 229.94
2019-09-19 02:00 | 234.25 | 229.15
2019-09-19 02:30 | 235.1 | 229.32
2019-09-19 03:00 | 235.67 | 229.46
2019-09-19 03:30 | 236.05 | 229.65
2019-09-19 04:00 | 236.61 | 229.6
2019-09-19 04:30 | 237.59 | 230.49
2019-09-19 05:00 | 238.68 | 232.01
2019-09-19 05:30 | 239.7 | 233.73
2019-09-19 06:00 | 240.94 | 235.97
2019-09-19 06:30 | 244.83 | 239.57
2019-09-19 07:00 | 247.06 | 241.27
2019-09-19 07:30 | 246.56 | 240.42
2019-09-19 08:00 | 244.59 | 237.77
2019-09-19 08:30 | 205.22 | 199.52
2019-09-19 09:00 | 170.84 | 165.28
2019-09-19 09:30 | 167.93 | 162.31
2019-09-19 10:00 | 167.4 | 161.67
2019-09-19 10:30 | 166.47 | 161.02
2019-09-19 11:00 | 166.14 | 160.4
2019-09-19 11:30 | 166.23 | 160.17
2019-09-19 12:00 | 166.11 | 160.13
2019-09-19 12:30 | 166.38 | 159.79
2019-09-19 13:00 | 166.54 | 159.96
2019-09-19 13:30 | 167.55 | 161.11
2019-09-19 14:00 | 169.43 | 162.47
2019-09-19 14:30 | 170.16 | 163.36
2019-09-19 15:00 | 170.59 | 163.87
2019-09-19 15:30 | 205.39 | 197.58
2019-09-19 16:00 | 236.16 | 228.79
2019-09-19 16:30 | 242.29 | 234.24
2019-09-19 17:00 | 244.04 | 235.96
2019-09-19 17:30 | 244.82 | 237.48
2019-09-19 18:00 | 246.56 | 239.15
2019-09-19 18:30 | 248.79 | 241.23
2019-09-19 19:00 | 251.2 | 243.87
2019-09-19 19:30 | 249.97 | 242.61
2019-09-19 20:00 | 247.75 | 240.09
2019-09-19 20:30 | 246.76 | 238.95
2019-09-19 21:00 | 244.97 | 237.7
2019-09-19 21:30 | 243.87 | 237.26
2019-09-19 22:00 | 242.13 | 235.58
2019-09-19 22:30 | 241.09 | 234
2019-09-19 23:00 | 239.72 | 232.34
2019-09-19 23:30 | 239.03 | 231.69
2019-09-20 | 236.86 | 230.76
2019-09-20 00:30 | 236.48 | 230.27
2019-09-20 01:00 | 235.42 | 229.99
2019-09-20 01:30 | 235.1 | 229.14
2019-09-20 02:00 | 234.65 | 228.95
2019-09-20 02:30 | 234.62 | 228.57
2019-09-20 03:00 | 234.85 | 228.26
2019-09-20 03:30 | 234.73 | 228.18
2019-09-20 04:00 | 234.96 | 228.52
2019-09-20 04:30 | 235.03 | 228.89
2019-09-20 05:00 | 236.26 | 229.92
2019-09-20 05:30 | 237.15 | 231.26
2019-09-20 06:00 | 239.08 | 233.1
2019-09-20 06:30 | 240.24 | 234.75
2019-09-20 07:00 | 243.05 | 236.69
2019-09-20 07:30 | 243.84 | 236.56
2019-09-20 08:00 | 241.1 | 234.19
2019-09-20 08:30 | 237.74 | 230.78
2019-09-20 09:00 | 202.52 | 196.11
2019-09-20 09:30 | 169.27 | 162.3
2019-09-20 10:00 | 168.51 | 161.93
2019-09-20 10:30 | 167.73 | 161.35
2019-09-20 11:00 | 167.66 | 161.36
2019-09-20 11:30 | 167.17 | 160.89
2019-09-20 12:00 | 167.25 | 161.02
2019-09-20 12:30 | 168.74 | 162.15
2019-09-20 13:00 | 170.22 | 163.16
2019-09-20 13:30 | 204.2 | 196.97
2019-09-20 14:00 | 233.05 | 226.02
2019-09-20 14:30 | 237.65 | 230.35
2019-09-20 15:00 | 238.71 | 231.06
2019-09-20 15:30 | 238.94 | 231.62
2019-09-20 16:00 | 241.85 | 233.93
2019-09-20 16:30 | 243.1 | 234.98
2019-09-20 17:00 | 243.51 | 236.08
2019-09-20 17:30 | 244.98 | 237.52
2019-09-20 18:00 | 246.62 | 239.41
2019-09-20 18:30 | 248.12 | 241.02
2019-09-20 19:00 | 249.69 | 242.49
2019-09-20 19:30 | 248.89 | 241.65
2019-09-20 20:00 | 247.09 | 239.88
2019-09-20 20:30 | 245.94 | 238.69
2019-09-20 21:00 | 244.09 | 237.27
2019-09-20 21:30 | 243.4 | 236.85
2019-09-20 22:00 | 242.74 | 235.88
2019-09-20 22:30 | 240.55 | 234.19
2019-09-20 23:00 | 239.52 | 233.12
2019-09-20 23:30 | 238.17 | 232.12
2019-09-21 | 236.56 | 230.67
2019-09-21 00:30 | 235.84 | 230.41
2019-09-21 01:00 | 234.96 | 229.72
2019-09-21 01:30 | 234.6 | 229.08
2019-09-21 02:00 | 234.88 | 228.89
2019-09-21 02:30 | 233.89 | 227.95
2019-09-21 03:00 | 233.51 | 227.9
2019-09-21 03:30 | 233.48 | 228.27
2019-09-21 04:00 | 233.54 | 227.96
2019-09-21 04:30 | 216.86 | 211.29
2019-09-21 05:00 | 181.81 | 176.08
2019-09-21 05:30 | 167.27 | 162.26
2019-09-21 06:00 | 168.51 | 162.91
2019-09-21 06:30 | 170.61 | 164.26
2019-09-21 07:00 | 169.79 | 164.69
2019-09-21 07:30 | 168.64 | 164.07
2019-09-21 08:00 | 170.58 | 164.36
2019-09-21 08:30 | 169.89 | 162.51
2019-09-21 09:00 | 168.63 | 160.78
2019-09-21 09:30 | 166.02 | 159.2
2019-09-21 10:00 | 165 | 158.55
2019-09-21 10:30 | 164.26 | 158.3
2019-09-21 11:00 | 163.13 | 157.54
2019-09-21 11:30 | 162.06 | 157.11
2019-09-21 12:00 | 163.21 | 157.65
2019-09-21 12:30 | 162.62 | 157.49
2019-09-21 13:00 | 162.68 | 157.29
2019-09-21 13:30 | 163.92 | 158.86
2019-09-21 14:00 | 165.22 | 159.26
2019-09-21 14:30 | 166.27 | 160.03
2019-09-21 15:00 | 168.1 | 160.73
2019-09-21 15:30 | 168.47 | 162.38
2019-09-21 16:00 | 170.9 | 164.42
2019-09-21 16:30 | 206.24 | 199.64
2019-09-21 17:00 | 236.99 | 229.83
2019-09-21 17:30 | 242.69 | 236.34
2019-09-21 18:00 | 243.96 | 238.12
2019-09-21 18:30 | 245.77 | 239.95
2019-09-21 19:00 | 247.67 | 241.47
2019-09-21 19:30 | 246.7 | 240.55
2019-09-21 20:00 | 244.79 | 238.92
2019-09-21 20:30 | 243.35 | 237.53
2019-09-21 21:00 | 242.06 | 236.32
2019-09-21 21:30 | 241.25 | 235.19
2019-09-21 22:00 | 239.97 | 234.09
2019-09-21 22:30 | 238.83 | 232.82
2019-09-21 23:00 | 237.57 | 231.77
2019-09-21 23:30 | 236.92 | 231.36
2019-09-22 | 235.92 | 230.17
2019-09-22 00:30 | 235.53 | 229.84
2019-09-22 01:00 | 234.17 | 228.82
2019-09-22 01:30 | 233.84 | 228.76
2019-09-22 02:00 | 234.37 | 229.16
2019-09-22 02:30 | 233.83 | 228.23
2019-09-22 03:00 | 233.88 | 227.89
2019-09-22 03:30 | 234.57 | 227.88
2019-09-22 04:00 | 234.55 | 228.01
2019-09-22 04:30 | 233.98 | 227.69
2019-09-22 05:00 | 218.37 | 211.91
2019-09-22 05:30 | 182.28 | 175.89
2019-09-22 06:00 | 168 | 161.87
2019-09-22 06:30 | 167.87 | 162.74
2019-09-22 07:00 | 167.95 | 162.22
2019-09-22 07:30 | 167.96 | 162.75
2019-09-22 08:00 | 167.58 | 162.86
2019-09-22 08:30 | 167.13 | 161.36
2019-09-22 09:00 | 166.49 | 159.96
2019-09-22 09:30 | 164.89 | 158.24
2019-09-22 10:00 | 164.95 | 158.31
2019-09-22 10:30 | 164.76 | 158.36
2019-09-22 11:00 | 164.96 | 158.04
2019-09-22 11:30 | 165.04 | 158.1
2019-09-22 12:00 | 164.67 | 158.38
2019-09-22 12:30 | 164.99 | 158.73
2019-09-22 13:00 | 165.64 | 159.59
2019-09-22 13:30 | 166.41 | 160.49
2019-09-22 14:00 | 165.71 | 159.48
2019-09-22 14:30 | 165.54 | 159.33
2019-09-22 15:00 | 167.35 | 161.43
2019-09-22 15:30 | 198.77 | 193.79
2019-09-22 16:00 | 231.56 | 225.75
2019-09-22 16:30 | 238.83 | 233.07
2019-09-22 17:00 | 243.84 | 236.38
2019-09-22 17:30 | 246.07 | 237.87
2019-09-22 18:00 | 247.31 | 239.95
2019-09-22 18:30 | 237.55 | 231
2019-09-22 19:00 | 224.49 | 218.53
2019-09-22 19:30 | 225.53 | 219.9
2019-09-22 20:00 | 226.89 | 221.22
2019-09-22 20:30 | 227.26 | 221.91
2019-09-22 21:00 | 228.75 | 223.28
2019-09-22 21:30 | 228.61 | 223.52
2019-09-22 22:00 | 236.45 | 231.04
2019-09-22 22:30 | 237.43 | 232.28
2019-09-22 23:00 | 236.28 | 231.24
2019-09-22 23:30 | 236.36 | 230.76
2019-09-23 | 235.54 | 229.98
2019-09-23 00:30 | 235.02 | 229.54
2019-09-23 01:00 | 234.23 | 228.91
2019-09-23 01:30 | 234.88 | 228.45
2019-09-23 02:00 | 235.61 | 228.18
2019-09-23 02:30 | 235.67 | 227.73
2019-09-23 03:00 | 235.54 | 227.77
2019-09-23 03:30 | 234.39 | 227.27
2019-09-23 04:00 | 234.91 | 227.36
2019-09-23 04:30 | 235.63 | 228.01
2019-09-23 05:00 | 236.6 | 229.04
2019-09-23 05:30 | 236.41 | 229.32
2019-09-23 06:00 | 238.58 | 230.89
2019-09-23 06:30 | 240.49 | 232.45
2019-09-23 07:00 | 241.59 | 233.55
2019-09-23 07:30 | 241.77 | 234.05
2019-09-23 08:00 | 242.08 | 233.92
2019-09-23 08:30 | 238.12 | 231.73
2019-09-23 09:00 | 201.04 | 194.4
2019-09-23 09:30 | 168.53 | 160.86
2019-09-23 10:00 | 165.89 | 159.5
2019-09-23 10:30 | 164.3 | 158.41
2019-09-23 11:00 | 163.03 | 157.84
2019-09-23 11:30 | 163.61 | 158.16
2019-09-23 12:00 | 164.03 | 158.15
2019-09-23 12:30 | 164.98 | 158.41
2019-09-23 13:00 | 165.6 | 158.76
2019-09-23 13:30 | 166.92 | 160.09
2019-09-23 14:00 | 201.31 | 194.6
2019-09-23 14:30 | 230.75 | 223.68
2019-09-23 15:00 | 235.72 | 227.55
2019-09-23 15:30 | 235.75 | 229.07
2019-09-23 16:00 | 238.46 | 230.96
2019-09-23 16:30 | 234.81 | 227.97
2019-09-23 17:00 | 228.9 | 222.9
2019-09-23 17:30 | 229.02 | 222.46
2019-09-23 18:00 | 228.37 | 221.43
2019-09-23 18:30 | 225.06 | 217.95
2019-09-23 19:00 | 223.59 | 216.35
2019-09-23 19:30 | 225.1 | 218
2019-09-23 20:00 | 225.59 | 218.77
2019-09-23 20:30 | 226.96 | 220.26
2019-09-23 21:00 | 226.81 | 220.87
2019-09-23 21:30 | 226.75 | 221.35
2019-09-23 22:00 | 227.01 | 222.03
2019-09-23 22:30 | 228.47 | 223.95
2019-09-23 23:00 | 230.28 | 225.45
2019-09-23 23:30 | 230.2 | 225.84
2019-09-24 | 231.08 | 226.29
2019-09-24 00:30 | 230.94 | 224.55
2019-09-24 01:00 | 231.4 | 224.7
2019-09-24 01:30 | 230.7 | 223.88
2019-09-24 02:00 | 230 | 223.37
2019-09-24 02:30 | 230.01 | 222.87
2019-09-24 03:00 | 230.41 | 222.91
2019-09-24 03:30 | 231.44 | 223.09
2019-09-24 04:00 | 231.26 | 222.65
2019-09-24 04:30 | 231.84 | 223.63
2019-09-24 05:00 | 231.09 | 224.07
2019-09-24 05:30 | 233.08 | 225.81
2019-09-24 06:00 | 234.45 | 227.76
2019-09-24 06:30 | 235.24 | 229.69
2019-09-24 07:00 | 236.81 | 230.45
2019-09-24 07:30 | 237.43 | 231.39
2019-09-24 08:00 | 237.53 | 230.7
2019-09-24 08:30 | 234.72 | 226.9
2019-09-24 09:00 | 232.85 | 224.59
2019-09-24 09:30 | 212.19 | 204.56
2019-09-24 10:00 | 174.58 | 166.42
2019-09-24 10:30 | 163.94 | 155.06
2019-09-24 11:00 | 159.43 | 154.13
2019-09-24 11:30 | 159.4 | 154
2019-09-24 12:00 | 160.12 | 154.63
2019-09-24 12:30 | 163.28 | 157.58
2019-09-24 13:00 | 160.23 | 154.64
2019-09-24 13:30 | 192.52 | 187.76
2019-09-24 14:00 | 223.66 | 218.62
2019-09-24 14:30 | 230.1 | 224.94
2019-09-24 15:00 | 231.39 | 225.97
2019-09-24 15:30 | 232.79 | 226.51
2019-09-24 16:00 | 234.25 | 226.7
2019-09-24 16:30 | 226.73 | 221.17
2019-09-24 17:00 | 226.18 | 220.8
2019-09-24 17:30 | 226.16 | 220.13
2019-09-24 18:00 | 252.91 | 249.13
2019-09-24 18:30 | 253.82 | 249.9
2019-09-24 19:00 | 253.55 | 249.37
2019-09-24 19:30 | 254.04 | 250.08
2019-09-24 20:00 | 255 | 251.48
2019-09-24 20:30 | 255.8 | 252.55
2019-09-24 21:00 | 256.63 | 253.61
2019-09-24 21:30 | 257.79 | 254.45
2019-09-24 22:00 | 258.86 | 255.72
2019-09-24 22:30 | 259.62 | 256.72
2019-09-24 23:00 | 260.7 | 257.98
2019-09-24 23:30 | 260.45 | 258.39
2019-09-25 | 261.84 | 259.43
2019-09-25 00:30 | 262.54 | 259.44
2019-09-25 01:00 | 237.45 | 231.08
2019-09-25 01:30 | 230.49 | 223.97
2019-09-25 02:00 | 229.62 | 223.39
2019-09-25 02:30 | 229.42 | 223.29
2019-09-25 03:00 | 230.01 | 223.46
2019-09-25 03:30 | 230.3 | 222.98
2019-09-25 04:00 | 230.34 | 223.02
2019-09-25 04:30 | 230.68 | 223.75
2019-09-25 05:00 | 231.15 | 224.29
2019-09-25 05:30 | 232.44 | 225.82
2019-09-25 06:00 | 233.06 | 226.63
2019-09-25 06:30 | 235.16 | 228.65
2019-09-25 07:00 | 237.01 | 230.01
2019-09-25 07:30 | 238.41 | 231.23
2019-09-25 08:00 | 237.11 | 229.81
2019-09-25 08:30 | 232.96 | 227.32
2019-09-25 09:00 | 230.92 | 225.61
2019-09-25 09:30 | 227.49 | 220.7
2019-09-25 10:00 | 232.12 | 223.92
2019-09-25 10:30 | 234.47 | 227.8
2019-09-25 11:00 | 230.95 | 226.19
2019-09-25 11:30 | 229.51 | 223.45
2019-09-25 12:00 | 233.1 | 227.38
2019-09-25 12:30 | 232.96 | 227.09
2019-09-25 13:00 | 234.74 | 227.34
2019-09-25 13:30 | 236.29 | 228.04
2019-09-25 14:00 | 235.83 | 228.37
2019-09-25 14:30 | 235.85 | 227.62
2019-09-25 15:00 | 235.87 | 227.7
2019-09-25 15:30 | 236.15 | 228.23
2019-09-25 16:00 | 237.4 | 229.8
2019-09-25 16:30 | 250.44 | 247.24
2019-09-25 17:00 | 255.21 | 252.08
2019-09-25 17:30 | 254.33 | 251.02
2019-09-25 18:00 | 253.53 | 250.76
2019-09-25 18:30 | 252.48 | 250.27
2019-09-25 19:00 | 252.3 | 249.46
2019-09-25 19:30 | 254 | 251.21
2019-09-25 20:00 | 254.7 | 252.04
2019-09-25 20:30 | 254.5 | 252.29
2019-09-25 21:00 | 256.01 | 253.68
2019-09-25 21:30 | 256.57 | 254.67
2019-09-25 22:00 | 257.74 | 255.83
2019-09-25 22:30 | 258.55 | 256.57
2019-09-25 23:00 | 255 | 252.7
2019-09-25 23:30 | 234.19 | 227.66
2019-09-26 | 232.04 | 226.25
2019-09-26 00:30 | 231.75 | 225.97
2019-09-26 01:00 | 231.27 | 225.01
2019-09-26 01:30 | 229.82 | 224.07
2019-09-26 02:00 | 229.51 | 224.02
2019-09-26 02:30 | 229.03 | 223.52
2019-09-26 03:00 | 228.65 | 223.05
2019-09-26 03:30 | 228.94 | 223.32
2019-09-26 04:00 | 229.09 | 223.33
2019-09-26 04:30 | 229.64 | 223.94
2019-09-26 05:00 | 231.69 | 224.63
2019-09-26 05:30 | 232.48 | 225.83
2019-09-26 06:00 | 233.9 | 227.65
2019-09-26 06:30 | 235.82 | 229.28
2019-09-26 07:00 | 237.97 | 230.37
2019-09-26 07:30 | 239.17 | 231
2019-09-26 08:00 | 238.77 | 230.61
2019-09-26 08:30 | 236.88 | 228.63
2019-09-26 09:00 | 237.75 | 229.78
2019-09-26 09:30 | 236.82 | 228.32
2019-09-26 10:00 | 235.63 | 226.84
2019-09-26 10:30 | 234.2 | 225.44
2019-09-26 11:00 | 232.71 | 224.35
2019-09-26 11:30 | 231.96 | 223.47
2019-09-26 12:00 | 230.25 | 222.37
2019-09-26 12:30 | 231.48 | 223.12
2019-09-26 13:00 | 232.58 | 223.51
2019-09-26 13:30 | 233.66 | 225.13
2019-09-26 14:00 | 235.07 | 226.83
2019-09-26 14:30 | 235.61 | 227.29
2019-09-26 15:00 | 236.03 | 227.32
2019-09-26 15:30 | 236.23 | 227.38
2019-09-26 16:00 | 236.83 | 227.7
2019-09-26 16:30 | 236.77 | 227.75
2019-09-26 17:00 | 237.77 | 228.71
2019-09-26 17:30 | 238.32 | 228.95
2019-09-26 18:00 | 224.84 | 217.25
2019-09-26 18:30 | 223.8 | 216.29
2019-09-26 19:00 | 222.48 | 214.98
2019-09-26 19:30 | 223.05 | 215.37
2019-09-26 20:00 | 225.16 | 217.37
2019-09-26 20:30 | 225.98 | 218.52
2019-09-26 21:00 | 227.08 | 219.69
2019-09-26 21:30 | 226.42 | 219.54
2019-09-26 22:00 | 227.35 | 220.42
2019-09-26 22:30 | 228.4 | 221.56
2019-09-26 23:00 | 229.48 | 222.45
2019-09-26 23:30 | 229.59 | 222.69
2019-09-27 | 230.76 | 222.45
2019-09-27 00:30 | 231.06 | 224.12
2019-09-27 01:00 | 229.68 | 223.31
2019-09-27 01:30 | 230.25 | 223.17
2019-09-27 02:00 | 230.5 | 222.59
2019-09-27 02:30 | 229 | 223.33
2019-09-27 03:00 | 227.37 | 222.27
2019-09-27 03:30 | 227.99 | 222.95
2019-09-27 04:00 | 228.86 | 223.6
2019-09-27 04:30 | 229.7 | 224.43
2019-09-27 05:00 | 230.37 | 225.14
2019-09-27 05:30 | 231.04 | 226.38
2019-09-27 06:00 | 232.52 | 228.02
2019-09-27 06:30 | 233.97 | 229.64
2019-09-27 07:00 | 234.84 | 229.88
2019-09-27 07:30 | 233.02 | 228.63
2019-09-27 08:00 | 229.68 | 225.41
2019-09-27 08:30 | 227.24 | 223.09
2019-09-27 09:00 | 225.38 | 221.32
2019-09-27 09:30 | 225.77 | 221.74
2019-09-27 10:00 | 225.21 | 221.26
2019-09-27 10:30 | 209.25 | 203.72
2019-09-27 11:00 | 175.28 | 167.81
2019-09-27 11:30 | 161.51 | 153.24
2019-09-27 12:00 | 162.85 | 154.6
2019-09-27 12:30 | 164.17 | 155.4
2019-09-27 13:00 | 166.3 | 158.57
2019-09-27 13:30 | 165.82 | 158.05
2019-09-27 14:00 | 165.25 | 157.66
2019-09-27 14:30 | 196.97 | 190.85
2019-09-27 15:00 | 217.37 | 212.49
2019-09-27 15:30 | 222.75 | 218.2
2019-09-27 16:00 | 229.74 | 224.91
2019-09-27 16:30 | 230.5 | 225.52
2019-09-27 17:00 | 231.21 | 226.43
2019-09-27 17:30 | 232.02 | 227.48
2019-09-27 18:00 | 232.95 | 228.95
2019-09-27 18:30 | 234.52 | 230.61
2019-09-27 19:00 | 235.36 | 231.46
2019-09-27 19:30 | 235.21 | 231.31
2019-09-27 20:00 | 234.31 | 230.4
2019-09-27 20:30 | 232.7 | 228.67
2019-09-27 21:00 | 231.82 | 227.77
2019-09-27 21:30 | 231.22 | 227.14
2019-09-27 22:00 | 230.13 | 225.92
2019-09-27 22:30 | 229.1 | 224.91
2019-09-27 23:00 | 227.82 | 223.58
2019-09-27 23:30 | 227.03 | 222.74
2019-09-28 | 226.27 | 221.92
2019-09-28 00:30 | 225.06 | 220.74
2019-09-28 01:00 | 224.36 | 219.94
2019-09-28 01:30 | 223.88 | 219.39
2019-09-28 02:00 | 223.82 | 219.23
2019-09-28 02:30 | 223.12 | 218.5
2019-09-28 03:00 | 223.27 | 218.69
2019-09-28 03:30 | 222.89 | 218.39
2019-09-28 04:00 | 223.12 | 218.56
2019-09-28 04:30 | 222.99 | 218.42
2019-09-28 05:00 | 223.7 | 219.16
2019-09-28 05:30 | 224.05 | 219.46
2019-09-28 06:00 | 224.01 | 219.48
2019-09-28 06:30 | 224.9 | 220.49
2019-09-28 07:00 | 210.58 | 204.57
2019-09-28 07:30 | 176.95 | 168.88
2019-09-28 08:00 | 164.38 | 155.85
2019-09-28 08:30 | 163.51 | 155.08
2019-09-28 09:00 | 162.66 | 154.21
2019-09-28 09:30 | 161.53 | 152.93
2019-09-28 10:00 | 161.5 | 152.91
2019-09-28 10:30 | 161.05 | 152.55
2019-09-28 11:00 | 160.56 | 152.22
2019-09-28 11:30 | 160.79 | 152.61
2019-09-28 12:00 | 161.95 | 153.77
2019-09-28 12:30 | 164.17 | 156.07
2019-09-28 13:00 | 165.04 | 157.08
2019-09-28 13:30 | 165.16 | 157.4
2019-09-28 14:00 | 165 | 157.2
2019-09-28 14:30 | 165.28 | 157.41
2019-09-28 15:00 | 165.92 | 158.14
2019-09-28 15:30 | 197.47 | 191.24
2019-09-28 16:00 | 218.31 | 213.51
2019-09-28 16:30 | 228.5 | 224.36
2019-09-28 17:00 | 229.42 | 225.37
2019-09-28 17:30 | 231.3 | 227.16
2019-09-28 18:00 | 234.48 | 230.29
2019-09-28 18:30 | 235.25 | 231.06
2019-09-28 19:00 | 236.34 | 232.15
2019-09-28 19:30 | 234.86 | 230.43
2019-09-28 20:00 | 233.02 | 228.53
2019-09-28 20:30 | 231.59 | 227.22
2019-09-28 21:00 | 230.02 | 225.92
2019-09-28 21:30 | 229.8 | 225.63
2019-09-28 22:00 | 228.8 | 224.47
2019-09-28 22:30 | 228.8 | 224.54
2019-09-28 23:00 | 228.06 | 223.77
2019-09-28 23:30 | 227.41 | 223.04
2019-09-29 | 226.92 | 222.32
2019-09-29 00:30 | 226.2 | 221.71
2019-09-29 01:00 | 225.73 | 221.31
2019-09-29 01:30 | 224.83 | 220.47
2019-09-29 02:00 | 224.56 | 220.21
2019-09-29 02:30 | 224.46 | 220.03
2019-09-29 03:00 | 224.17 | 219.72
2019-09-29 03:30 | 223.84 | 219.43
2019-09-29 04:00 | 222.88 | 218.52
2019-09-29 04:30 | 223.59 | 219.27
2019-09-29 05:00 | 224.15 | 219.82
2019-09-29 05:30 | 224.79 | 220.47
2019-09-29 06:00 | 225.14 | 220.81
2019-09-29 06:30 | 225.93 | 221.52
2019-09-29 07:00 | 210.1 | 204.02
2019-09-29 07:30 | 176.17 | 167.78
2019-09-29 08:00 | 164 | 154.31
2019-09-29 08:30 | 162.71 | 153.11
2019-09-29 09:00 | 161.87 | 152.9
2019-09-29 09:30 | 160.92 | 151.75
2019-09-29 10:00 | 160.76 | 151.63
2019-09-29 10:30 | 160.03 | 151.62
2019-09-29 11:00 | 159.66 | 151.27
2019-09-29 11:30 | 159.59 | 151.26
2019-09-29 12:00 | 160.45 | 152.11
2019-09-29 12:30 | 161.38 | 153.12
2019-09-29 13:00 | 161.99 | 153.72
2019-09-29 13:30 | 162.53 | 154.27
2019-09-29 14:00 | 162.88 | 154.78
2019-09-29 14:30 | 163.83 | 155.88
2019-09-29 15:00 | 165.9 | 157.91
2019-09-29 15:30 | 167.69 | 159.73
2019-09-29 16:00 | 168.59 | 160.52
2019-09-29 16:30 | 202.74 | 196.53
2019-09-29 17:00 | 231.05 | 226.63
2019-09-29 17:30 | 235.53 | 231.14
2019-09-29 18:00 | 237.46 | 233.18
2019-09-29 18:30 | 239 | 234.86
2019-09-29 19:00 | 240.17 | 235.99
2019-09-29 19:30 | 238.52 | 234.39
2019-09-29 20:00 | 236.55 | 232.32
2019-09-29 20:30 | 234.98 | 230.6
2019-09-29 21:00 | 233.86 | 229.3
2019-09-29 21:30 | 235.19 | 230.5
2019-09-29 22:00 | 233.79 | 229.06
2019-09-29 22:30 | 232.02 | 227.27
2019-09-29 23:00 | 230.03 | 225.33
2019-09-29 23:30 | 229.28 | 224.74
2019-09-30 | 228.33 | 223.81
2019-09-30 00:30 | 227.96 | 223.42
2019-09-30 01:00 | 227.39 | 222.81
2019-09-30 01:30 | 226.87 | 222.22
2019-09-30 02:00 | 226.68 | 221.95
2019-09-30 02:30 | 226.57 | 221.86
2019-09-30 03:00 | 227.81 | 223.25
2019-09-30 03:30 | 227.98 | 223.41
2019-09-30 04:00 | 228.22 | 223.64
2019-09-30 04:30 | 228 | 223.49
2019-09-30 05:00 | 227.51 | 223.09
2019-09-30 05:30 | 229.59 | 224.79
2019-09-30 06:00 | 231.48 | 226.56
2019-09-30 06:30 | 232.09 | 228.12
2019-09-30 07:00 | 231.44 | 227.56
2019-09-30 07:30 | 230.24 | 226.34
2019-09-30 08:00 | 229.2 | 225.07
2019-09-30 08:30 | 227.62 | 223.4
2019-09-30 09:00 | 226.12 | 221.87
2019-09-30 09:30 | 224.29 | 220.07
2019-09-30 10:00 | 210.64 | 205.28
2019-09-30 10:30 | 176.34 | 169.46
2019-09-30 11:00 | 162.02 | 154.45
2019-09-30 11:30 | 161.43 | 153.83
2019-09-30 12:00 | 162.28 | 154.72
2019-09-30 12:30 | 161.95 | 154.35
2019-09-30 13:00 | 162.33 | 154.67
2019-09-30 13:30 | 162.86 | 155.43
2019-09-30 14:00 | 195.27 | 189.25
2019-09-30 14:30 | 221.46 | 217.25
2019-09-30 15:00 | 226.78 | 222.93
2019-09-30 15:30 | 228.68 | 224.51
2019-09-30 16:00 | 230.18 | 226.12
2019-09-30 16:30 | 231.4 | 227.21
2019-09-30 17:00 | 233.84 | 229.34
2019-09-30 17:30 | 234.54 | 230.4
2019-09-30 18:00 | 235.63 | 231.61
2019-09-30 18:30 | 237.29 | 233.23
2019-09-30 19:00 | 242.02 | 238.2
2019-09-30 19:30 | 241.86 | 237.96
2019-09-30 20:00 | 239.28 | 235.23
2019-09-30 20:30 | 237.29 | 233.21
2019-09-30 21:00 | 236.54 | 232.24
2019-09-30 21:30 | 235.71 | 231.46
2019-09-30 22:00 | 234.33 | 230.08
2019-09-30 22:30 | 232.41 | 227.98
2019-09-30 23:00 | 231.13 | 226.66
2019-09-30 23:30 | 230.79 | 226.38
2019-10-01 | 229.45 | 224.95
2019-10-01 00:30 | 228.73 | 224.2
2019-10-01 01:00 | 227.98 | 223.6
2019-10-01 01:30 | 226.91 | 222.48
2019-10-01 02:00 | 226.49 | 222.1
2019-10-01 02:30 | 225.15 | 220.76
2019-10-01 03:00 | 224.83 | 220.44
2019-10-01 03:30 | 224.89 | 220.53
2019-10-01 04:00 | 225.03 | 220.65
2019-10-01 04:30 | 225.64 | 221.3
2019-10-01 05:00 | 226.23 | 221.91
2019-10-01 05:30 | 227.78 | 223.48
2019-10-01 06:00 | 229.23 | 225.05
2019-10-01 06:30 | 230.95 | 226.81
2019-10-01 07:00 | 230.86 | 226.71
2019-10-01 07:30 | 213.93 | 208.81
2019-10-01 08:00 | 180.07 | 173.49
2019-10-01 08:30 | 164.63 | 157.34
2019-10-01 09:00 | 162.58 | 155.09
2019-10-01 09:30 | 160.96 | 153.31
2019-10-01 10:00 | 161.51 | 153.86
2019-10-01 10:30 | 160 | 152.49
2019-10-01 11:00 | 160.82 | 153.43
2019-10-01 11:30 | 161.09 | 153.64
2019-10-01 12:00 | 161.96 | 154.55
2019-10-01 12:30 | 162 | 154.49
2019-10-01 13:00 | 162.98 | 155.3
2019-10-01 13:30 | 195.73 | 189.91
2019-10-01 14:00 | 224.31 | 220.42
2019-10-01 14:30 | 228.59 | 224.87
2019-10-01 15:00 | 231.64 | 227.58
2019-10-01 15:30 | 232.97 | 228.83
2019-10-01 16:00 | 233.59 | 229.25
2019-10-01 16:30 | 234.13 | 229.62
2019-10-01 17:00 | 234.55 | 229.84
2019-10-01 17:30 | 235.66 | 230.82
2019-10-01 18:00 | 238.49 | 233.52
2019-10-01 18:30 | 240.63 | 235.93
2019-10-01 19:00 | 242.41 | 238.6
2019-10-01 19:30 | 241.04 | 237.24
2019-10-01 20:00 | 238.59 | 234.59
2019-10-01 20:30 | 238.51 | 234.54
2019-10-01 21:00 | 236.96 | 232.91
2019-10-01 21:30 | 236.31 | 232.2
2019-10-01 22:00 | 235.2 | 231.05
2019-10-01 22:30 | 233.25 | 229.08
2019-10-01 23:00 | 231.69 | 227.45
2019-10-01 23:30 | 231 | 226.79
2019-10-02 | 230.07 | 225.82
2019-10-02 00:30 | 230.03 | 225.76
2019-10-02 01:00 | 228.93 | 224.7
2019-10-02 01:30 | 228.13 | 223.89
2019-10-02 02:00 | 228.43 | 224.15
2019-10-02 02:30 | 227.86 | 223.59
2019-10-02 03:00 | 227.8 | 223.49
2019-10-02 03:30 | 227.86 | 223.54
2019-10-02 04:00 | 228.06 | 223.72
2019-10-02 04:30 | 228.55 | 224.21
2019-10-02 05:00 | 229.1 | 224.84
2019-10-02 05:30 | 230.72 | 226.44
2019-10-02 06:00 | 232.02 | 227.92
2019-10-02 06:30 | 234.2 | 230.38
2019-10-02 07:00 | 234.21 | 230.45
2019-10-02 07:30 | 218.75 | 213.81
2019-10-02 08:00 | 183.6 | 176.93
2019-10-02 08:30 | 168.33 | 161.03
2019-10-02 09:00 | 166.92 | 158.9
2019-10-02 09:30 | 164.86 | 156.67
2019-10-02 10:00 | 166.12 | 157.73
2019-10-02 10:30 | 164.13 | 156.02
2019-10-02 11:00 | 164.27 | 155.5
2019-10-02 11:30 | 164.35 | 155.94
2019-10-02 12:00 | 165.3 | 156.59
2019-10-02 12:30 | 165.22 | 157.31
2019-10-02 13:00 | 166.32 | 157.42
2019-10-02 13:30 | 166.67 | 158.34
2019-10-02 14:00 | 166.66 | 159.14
2019-10-02 14:30 | 197.43 | 191.91
2019-10-02 15:00 | 224.4 | 220.89
2019-10-02 15:30 | 230.47 | 226.96
2019-10-02 16:00 | 232.74 | 228.82
2019-10-02 16:30 | 234.46 | 230.45
2019-10-02 17:00 | 236.93 | 232.62
2019-10-02 17:30 | 238.85 | 234.55
2019-10-02 18:00 | 223.95 | 220.11
2019-10-02 18:30 | 221.91 | 218.79
2019-10-02 19:00 | 221.07 | 217.91
2019-10-02 19:30 | 221.99 | 218.82
2019-10-02 20:00 | 223.48 | 220.37
2019-10-02 20:30 | 224.85 | 221.76
2019-10-02 21:00 | 235.39 | 231.62
2019-10-02 21:30 | 238.66 | 235.15
2019-10-02 22:00 | 237.14 | 233.52
2019-10-02 22:30 | 234.76 | 231.06
2019-10-02 23:00 | 232.48 | 228.82
2019-10-02 23:30 | 231.37 | 227.65
2019-10-03 | 229.91 | 226.15
2019-10-03 00:30 | 229.42 | 225.62
2019-10-03 01:00 | 228.58 | 224.75
2019-10-03 01:30 | 227.39 | 223.34
2019-10-03 02:00 | 226.79 | 222.82
2019-10-03 02:30 | 226.37 | 222.44
2019-10-03 03:00 | 226.15 | 222.21
2019-10-03 03:30 | 225.98 | 221.99
2019-10-03 04:00 | 226.27 | 222.26
2019-10-03 04:30 | 226.88 | 222.76
2019-10-03 05:00 | 227.39 | 223.27
2019-10-03 05:30 | 228.75 | 224.78
2019-10-03 06:00 | 230.13 | 226.37
2019-10-03 06:30 | 231.97 | 228.42
2019-10-03 07:00 | 232.25 | 228.51
2019-10-03 07:30 | 232.9 | 228.87
2019-10-03 08:00 | 230.47 | 227.04
2019-10-03 08:30 | 228.17 | 224.79
2019-10-03 09:00 | 209.55 | 205.65
2019-10-03 09:30 | 174.37 | 168.71
2019-10-03 10:00 | 159.91 | 153.21
2019-10-03 10:30 | 159.06 | 152.78
2019-10-03 11:00 | 160.53 | 152.72
2019-10-03 11:30 | 160.95 | 152.49
2019-10-03 12:00 | 160.14 | 153.41
2019-10-03 12:30 | 160.73 | 153.21
2019-10-03 13:00 | 161.64 | 154.05
2019-10-03 13:30 | 162.22 | 154.75
2019-10-03 14:00 | 163.93 | 156.35
2019-10-03 14:30 | 164.01 | 156.3
2019-10-03 15:00 | 166.22 | 157.94
2019-10-03 15:30 | 198.36 | 192.05
2019-10-03 16:00 | 225.98 | 221.88
2019-10-03 16:30 | 233.31 | 229.53
2019-10-03 17:00 | 235.33 | 231.56
2019-10-03 17:30 | 232.25 | 228.66
2019-10-03 18:00 | 220.2 | 217.35
2019-10-03 18:30 | 220.15 | 217.25
2019-10-03 19:00 | 219.13 | 216.11
2019-10-03 19:30 | 219.69 | 216.63
2019-10-03 20:00 | 220.48 | 217.32
2019-10-03 20:30 | 221.34 | 218.3
2019-10-03 21:00 | 223.13 | 220.13
2019-10-03 21:30 | 223.22 | 220.1
2019-10-03 22:00 | 231.29 | 227.31
2019-10-03 22:30 | 232.73 | 228.47
2019-10-03 23:00 | 231.14 | 226.73
2019-10-03 23:30 | 230.08 | 225.65
2019-10-04 | 229.19 | 224.79
2019-10-04 00:30 | 229.2 | 224.85
2019-10-04 01:00 | 228.69 | 224.36
2019-10-04 01:30 | 227.96 | 223.65
2019-10-04 02:00 | 227.85 | 223.5
2019-10-04 02:30 | 227.4 | 223.02
2019-10-04 03:00 | 226.87 | 222.55
2019-10-04 03:30 | 226.87 | 222.66
2019-10-04 04:00 | 227.02 | 222.81
2019-10-04 04:30 | 227.25 | 223.05
2019-10-04 05:00 | 227.79 | 223.62
2019-10-04 05:30 | 230.03 | 225.84
2019-10-04 06:00 | 232.08 | 228.04
2019-10-04 06:30 | 233.11 | 229.25
2019-10-04 07:00 | 233.04 | 229.33
2019-10-04 07:30 | 231.96 | 228.35
2019-10-04 08:00 | 229.61 | 225.99
2019-10-04 08:30 | 212.56 | 207.55
2019-10-04 09:00 | 178.84 | 172.17
2019-10-04 09:30 | 163.93 | 156.62
2019-10-04 10:00 | 163.65 | 156.27
2019-10-04 10:30 | 163.18 | 155.84
2019-10-04 11:00 | 163.28 | 155.98
2019-10-04 11:30 | 163.18 | 155.8
2019-10-04 12:00 | 164.72 | 157.37
2019-10-04 12:30 | 164.61 | 157.23
2019-10-04 13:00 | 166.42 | 159.02
2019-10-04 13:30 | 167.39 | 159.93
2019-10-04 14:00 | 168.31 | 160.93
2019-10-04 14:30 | 168.6 | 161.33
2019-10-04 15:00 | 170.57 | 163.11
2019-10-04 15:30 | 172.13 | 164.55
2019-10-04 16:00 | 173.67 | 166.2
2019-10-04 16:30 | 175.89 | 168.42
2019-10-04 17:00 | 177.74 | 170.48
2019-10-04 17:30 | 210.87 | 205.01
2019-10-04 18:00 | 237.55 | 233.45
2019-10-04 18:30 | 243.69 | 240.06
2019-10-04 19:00 | 244.86 | 241.35
2019-10-04 19:30 | 244.26 | 240.74
2019-10-04 20:00 | 241.75 | 238.18
2019-10-04 20:30 | 240.65 | 237.01
2019-10-04 21:00 | 238.94 | 235.15
2019-10-04 21:30 | 239.49 | 234.89
2019-10-04 22:00 | 238.07 | 233.46
2019-10-04 22:30 | 235.64 | 231.51
2019-10-04 23:00 | 235.05 | 230.67
2019-10-04 23:30 | 234.07 | 229.59
2019-10-05 | 232.95 | 228.85
2019-10-05 00:30 | 231.77 | 227.62
2019-10-05 01:00 | 231.41 | 227.28
2019-10-05 01:30 | 230.17 | 226.05
2019-10-05 02:00 | 229.98 | 225.86
2019-10-05 02:30 | 229.59 | 225.41
2019-10-05 03:00 | 229.1 | 224.81
2019-10-05 03:30 | 228.81 | 224.51
2019-10-05 04:00 | 228.35 | 223.98
2019-10-05 04:30 | 228.59 | 224.32
2019-10-05 05:00 | 229.68 | 225.48
2019-10-05 05:30 | 230.44 | 226.24
2019-10-05 06:00 | 230.73 | 226.48
2019-10-05 06:30 | 230.68 | 226.42
2019-10-05 07:00 | 215.13 | 209.15
2019-10-05 07:30 | 181.05 | 173.32
2019-10-05 08:00 | 153.72 | 146.56
2019-10-05 08:30 | 176.24 | 171.14
2019-10-05 09:00 | 194.66 | 189.83
2019-10-05 09:30 | 193.56 | 189.03
2019-10-05 10:00 | 192.32 | 187.87
2019-10-05 10:30 | 190.02 | 185.76
2019-10-05 11:00 | 188.75 | 184.69
2019-10-05 11:30 | 190.27 | 186.12
2019-10-05 12:00 | 191.44 | 187.38
2019-10-05 12:30 | 192.88 | 188.82
2019-10-05 13:00 | 193.7 | 189.68
2019-10-05 13:30 | 196.84 | 192.76
2019-10-05 14:00 | 199.43 | 195.33
2019-10-05 14:30 | 202.3 | 197.96
2019-10-05 15:00 | 204.67 | 200.32
2019-10-05 15:30 | 206.31 | 202.16
2019-10-05 16:00 | 208.17 | 204.07
2019-10-05 16:30 | 210.86 | 206.71
2019-10-05 17:00 | 212.76 | 208.74
2019-10-05 17:30 | 214.89 | 210.86
2019-10-05 18:00 | 215.91 | 211.97
2019-10-05 18:30 | 215.34 | 211.5
2019-10-05 19:00 | 215.92 | 211.97
2019-10-05 19:30 | 214.32 | 210.49
2019-10-05 20:00 | 211.52 | 207.57
2019-10-05 20:30 | 209 | 204.8
2019-10-05 21:00 | 207.32 | 202.93
2019-10-05 21:30 | 206.37 | 201.86
2019-10-05 22:00 | 204.68 | 200.09
2019-10-05 22:30 | 203.2 | 198.52
2019-10-05 23:00 | 201.41 | 196.62
2019-10-05 23:30 | 201.33 | 196.34
2019-10-06 | 200.15 | 195.29
2019-10-06 00:30 | 199.35 | 194.43
2019-10-06 01:00 | 198.19 | 193.36
2019-10-06 01:30 | 197.81 | 192.91
2019-10-06 02:00 | 197.29 | 192.37
2019-10-06 02:30 | 196.85 | 191.89
2019-10-06 03:00 | 196.54 | 191.6
2019-10-06 03:30 | 196.13 | 191.16
2019-10-06 04:00 | 196.11 | 191.08
2019-10-06 04:30 | 196.14 | 191.13
2019-10-06 05:00 | 196.08 | 191.09
2019-10-06 05:30 | 196.62 | 191.66
2019-10-06 06:00 | 197.04 | 192.16
2019-10-06 06:30 | 197.15 | 192.35
2019-10-06 07:00 | 196.45 | 191.74
2019-10-06 07:30 | 196.04 | 191.42
2019-10-06 08:00 | 195.41 | 190.78
2019-10-06 08:30 | 194.72 | 190.14
2019-10-06 09:00 | 194.61 | 190.12
2019-10-06 09:30 | 193.98 | 189.54
2019-10-06 10:00 | 194.33 | 189.83
2019-10-06 10:30 | 194.71 | 190.13
2019-10-06 11:00 | 195.74 | 191.3
2019-10-06 11:30 | 198.4 | 194.08
2019-10-06 12:00 | 195.13 | 191.28
2019-10-06 12:30 | 196 | 192.22
2019-10-06 13:00 | 197.28 | 193.51
2019-10-06 13:30 | 198.34 | 194.85
2019-10-06 14:00 | 199.63 | 196.15
2019-10-06 14:30 | 202.19 | 198.6
2019-10-06 15:00 | 203.35 | 199.83
2019-10-06 15:30 | 205.7 | 202.27
2019-10-06 16:00 | 207.76 | 204.41
2019-10-06 16:30 | 212.31 | 208.73
2019-10-06 17:00 | 214.49 | 211.11
2019-10-06 17:30 | 202.45 | 199.27
2019-10-06 18:00 | 189.35 | 184.73
2019-10-06 18:30 | 191.44 | 186.02
2019-10-06 19:00 | 191.64 | 185.99
2019-10-06 19:30 | 189.48 | 183.72
2019-10-06 20:00 | 186.28 | 180.8
2019-10-06 20:30 | 183.33 | 177.94
2019-10-06 21:00 | 181.02 | 175.41
2019-10-06 21:30 | 179.52 | 174.1
2019-10-06 22:00 | 177.61 | 172.06
2019-10-06 22:30 | 175.95 | 170.16
2019-10-06 23:00 | 173.98 | 168.01
2019-10-06 23:30 | 172.96 | 167.13
2019-10-07 | 185.11 | 180.32
2019-10-07 00:30 | 195 | 190.78
2019-10-07 01:00 | 194.2 | 189.9
2019-10-07 01:30 | 193.65 | 189.35
2019-10-07 02:00 | 193 | 188.66
2019-10-07 02:30 | 192.19 | 187.99
2019-10-07 03:00 | 191.89 | 187.61
2019-10-07 03:30 | 191.46 | 187.16
2019-10-07 04:00 | 191.19 | 186.89
2019-10-07 04:30 | 191.01 | 186.72
2019-10-07 05:00 | 191.02 | 186.71
2019-10-07 05:30 | 191.33 | 187.01
2019-10-07 06:00 | 191.67 | 187.35
2019-10-07 06:30 | 192.22 | 188.14
2019-10-07 07:00 | 192.68 | 188.75
2019-10-07 07:30 | 192.52 | 188.61
2019-10-07 08:00 | 192.6 | 188.78
2019-10-07 08:30 | 192.69 | 188.92
2019-10-07 09:00 | 193.09 | 189.31
2019-10-07 09:30 | 193.81 | 190.15
2019-10-07 10:00 | 195.37 | 191.67
2019-10-07 10:30 | 197.06 | 193.31
2019-10-07 11:00 | 198.42 | 194.63
2019-10-07 11:30 | 200.79 | 196.98
2019-10-07 12:00 | 202.93 | 199.15
2019-10-07 12:30 | 205.44 | 201.59
2019-10-07 13:00 | 208.34 | 204.32
2019-10-07 13:30 | 211.58 | 207.54
2019-10-07 14:00 | 212 | 208.06
2019-10-07 14:30 | 212.99 | 209.3
2019-10-07 15:00 | 214.78 | 211.04
2019-10-07 15:30 | 217.73 | 213.98
2019-10-07 16:00 | 221.3 | 217.35
2019-10-07 16:30 | 206.38 | 201.72
2019-10-07 17:00 | 194.25 | 188.6
2019-10-07 17:30 | 195.36 | 189.97
2019-10-07 18:00 | 197.2 | 191.56
2019-10-07 18:30 | 197.99 | 192.33
2019-10-07 19:00 | 198.63 | 193.09
2019-10-07 19:30 | 196.66 | 190.93
2019-10-07 20:00 | 192.94 | 186.82
2019-10-07 20:30 | 189.18 | 183.09
2019-10-07 21:00 | 185.54 | 179.46
2019-10-07 21:30 | 183.3 | 177.21
2019-10-07 22:00 | 180.68 | 174.47
2019-10-07 22:30 | 177.94 | 171.55
2019-10-07 23:00 | 175.75 | 169.19
2019-10-07 23:30 | 175.16 | 168.69
2019-10-08 | 173.51 | 167.25
2019-10-08 00:30 | 172.46 | 166.32
2019-10-08 01:00 | 171.71 | 165.49
2019-10-08 01:30 | 171.19 | 164.85
2019-10-08 02:00 | 170.75 | 164.44
2019-10-08 02:30 | 170.1 | 163.82
2019-10-08 03:00 | 174.2 | 168.56
2019-10-08 03:30 | 176.23 | 170.79
2019-10-08 04:00 | 176.14 | 170.8
2019-10-08 04:30 | 176.5 | 171.21
2019-10-08 05:00 | 176.94 | 171.46
2019-10-08 05:30 | 171.4 | 164.88
2019-10-08 06:00 | 172.61 | 165.98
2019-10-08 06:30 | 174.95 | 168.42
2019-10-08 07:00 | 176.26 | 169.77
2019-10-08 07:30 | 181.65 | 176.04
2019-10-08 08:00 | 178.81 | 173.26
2019-10-08 08:30 | 160.77 | 154.41
2019-10-08 09:00 | 160.15 | 153.63
2019-10-08 09:30 | 161.12 | 154.45
2019-10-08 10:00 | 161.41 | 155.11
2019-10-08 10:30 | 162.62 | 156.14
2019-10-08 11:00 | 166.35 | 160.44
2019-10-08 11:30 | 168.27 | 162.68
2019-10-08 12:00 | 174.25 | 168.7
2019-10-08 12:30 | 174.48 | 168.62
2019-10-08 13:00 | 176.53 | 170.25
2019-10-08 13:30 | 177.38 | 171.38
2019-10-08 14:00 | 177.43 | 171.4
2019-10-08 14:30 | 178.8 | 172.65
2019-10-08 15:00 | 178.31 | 172.24
2019-10-08 15:30 | 180.48 | 173.94
2019-10-08 16:00 | 188.89 | 182.29
2019-10-08 16:30 | 190.28 | 183.6
2019-10-08 17:00 | 192.06 | 185.44
2019-10-08 17:30 | 193.17 | 186.22
2019-10-08 18:00 | 194.27 | 187.13
2019-10-08 18:30 | 181.68 | 176.99
2019-10-08 19:00 | 186.93 | 183.39
2019-10-08 19:30 | 189.33 | 185.7
2019-10-08 20:00 | 192.64 | 188.93
2019-10-08 20:30 | 193.95 | 190.17
2019-10-08 21:00 | 170.98 | 165.26
2019-10-08 21:30 | 167.26 | 160.99
2019-10-08 22:00 | 180.37 | 173.18
2019-10-08 22:30 | 182.43 | 175.22
2019-10-08 23:00 | 180.92 | 173.68
2019-10-08 23:30 | 180.45 | 173.15
2019-10-09 | 179.33 | 171.75
2019-10-09 00:30 | 178.93 | 171.19
2019-10-09 01:00 | 178.41 | 170.57
2019-10-09 01:30 | 177.85 | 170.15
2019-10-09 02:00 | 177.71 | 169.94
2019-10-09 02:30 | 177.83 | 170.04
2019-10-09 03:00 | 177.96 | 170.2
2019-10-09 03:30 | 176.77 | 169.02
2019-10-09 04:00 | 175.56 | 167.84
2019-10-09 04:30 | 175.1 | 167.45
2019-10-09 05:00 | 175.83 | 168.27
2019-10-09 05:30 | 177.1 | 169.68
2019-10-09 06:00 | 179.03 | 171.39
2019-10-09 06:30 | 181.52 | 174.02
2019-10-09 07:00 | 182.11 | 174.46
2019-10-09 07:30 | 179.5 | 171.97
2019-10-09 08:00 | 161.09 | 154.01
2019-10-09 08:30 | 169.83 | 163.74
2019-10-09 09:00 | 197.68 | 193.21
2019-10-09 09:30 | 197.45 | 192.71
2019-10-09 10:00 | 186.13 | 180.71
2019-10-09 10:30 | 164.65 | 157.79
2019-10-09 11:00 | 163.06 | 156.03
2019-10-09 11:30 | 164.81 | 156.61
2019-10-09 12:00 | 173.04 | 164.69
2019-10-09 12:30 | 173.23 | 165.06
2019-10-09 13:00 | 172.89 | 165.56
2019-10-09 13:30 | 154.19 | 147.25
2019-10-09 14:00 | 189.56 | 184.67
2019-10-09 14:30 | 199.96 | 195.38
2019-10-09 15:00 | 200.86 | 196.34
2019-10-09 15:30 | 202.79 | 198.19
2019-10-09 16:00 | 190.2 | 184.36
2019-10-09 16:30 | 171.29 | 162.54
2019-10-09 17:00 | 182.5 | 173.81
2019-10-09 17:30 | 185.34 | 176.11
2019-10-09 18:00 | 187.38 | 178.38
2019-10-09 18:30 | 189.26 | 180.89
2019-10-09 19:00 | 191.3 | 183.55
2019-10-09 19:30 | 190.93 | 183.1
2019-10-09 20:00 | 189.09 | 181.19
2019-10-09 20:30 | 187.72 | 179.99
2019-10-09 21:00 | 185.45 | 178.12
2019-10-09 21:30 | 184.75 | 177.48
2019-10-09 22:00 | 183.87 | 176.47
2019-10-09 22:30 | 181.28 | 174.16
2019-10-09 23:00 | 179.94 | 172.87
2019-10-09 23:30 | 178.84 | 171.65
2019-10-10 | 175.37 | 167.64
2019-10-10 00:30 | 175.05 | 166.71
2019-10-10 01:00 | 174.64 | 166.58
2019-10-10 01:30 | 173.33 | 165.94
2019-10-10 02:00 | 173.43 | 166.28
2019-10-10 02:30 | 173.62 | 166.46
2019-10-10 03:00 | 173.3 | 166.21
2019-10-10 03:30 | 171.94 | 164.85
2019-10-10 04:00 | 172.39 | 165.3
2019-10-10 04:30 | 174.26 | 167.31
2019-10-10 05:00 | 175.03 | 168.07
2019-10-10 05:30 | 176 | 169.26
2019-10-10 06:00 | 177.64 | 171.19
2019-10-10 06:30 | 179.89 | 173.6
2019-10-10 07:00 | 180.48 | 173.76
2019-10-10 07:30 | 176.37 | 168.98
2019-10-10 08:00 | 168.94 | 162.72
2019-10-10 08:30 | 201.43 | 196.75
2019-10-10 09:00 | 200.42 | 195.79
2019-10-10 09:30 | 198.68 | 193.97
2019-10-10 10:00 | 198.62 | 193.77
2019-10-10 10:30 | 198.03 | 193.3
2019-10-10 11:00 | 198.02 | 193.42
2019-10-10 11:30 | 197.93 | 193.38
2019-10-10 12:00 | 197.99 | 193.45
2019-10-10 12:30 | 198.33 | 193.64
2019-10-10 13:00 | 198.71 | 193.9
2019-10-10 13:30 | 200.05 | 195.3
2019-10-10 14:00 | 201.09 | 196.4
2019-10-10 14:30 | 202.27 | 197.64
2019-10-10 15:00 | 199.48 | 195.15
2019-10-10 15:30 | 200.85 | 196.49
2019-10-10 16:00 | 204.22 | 199.56
2019-10-10 16:30 | 192.39 | 186.37
2019-10-10 17:00 | 175.35 | 166.93
2019-10-10 17:30 | 187.63 | 177.55
2019-10-10 18:00 | 191.03 | 180.59
2019-10-10 18:30 | 193.43 | 183.06
2019-10-10 19:00 | 196.03 | 185.89
2019-10-10 19:30 | 195.3 | 185.21
2019-10-10 20:00 | 194.01 | 183.85
2019-10-10 20:30 | 192.49 | 181.98
2019-10-10 21:00 | 190.44 | 179.73
2019-10-10 21:30 | 189.72 | 179.41
2019-10-10 22:00 | 187.5 | 178.55
2019-10-10 22:30 | 183.96 | 175.51
2019-10-10 23:00 | 182.52 | 173.96
2019-10-10 23:30 | 182.1 | 173.27
2019-10-11 | 181.41 | 172.29
2019-10-11 00:30 | 181.1 | 172.04
2019-10-11 01:00 | 180.33 | 171.27
2019-10-11 01:30 | 179.17 | 170.06
2019-10-11 02:00 | 178.2 | 168.96
2019-10-11 02:30 | 177.91 | 168.96
2019-10-11 03:00 | 177.38 | 168.82
2019-10-11 03:30 | 177.32 | 168.98
2019-10-11 04:00 | 178.58 | 169.36
2019-10-11 04:30 | 179.93 | 170.01
2019-10-11 05:00 | 181.2 | 171.13
2019-10-11 05:30 | 182.48 | 172.61
2019-10-11 06:00 | 183.8 | 174.42
2019-10-11 06:30 | 185.75 | 176.85
2019-10-11 07:00 | 186.44 | 176.79
2019-10-11 07:30 | 185.78 | 175.91
2019-10-11 08:00 | 183.17 | 173.53
2019-10-11 08:30 | 181.51 | 172.21
2019-10-11 09:00 | 180.14 | 171.14
2019-10-11 09:30 | 178.34 | 169.21
2019-10-11 10:00 | 179.44 | 170.08
2019-10-11 10:30 | 178.93 | 168.87
2019-10-11 11:00 | 177.55 | 167.71
2019-10-11 11:30 | 177.47 | 168.05
2019-10-11 12:00 | 179.35 | 169.55
2019-10-11 12:30 | 178.67 | 169.34
2019-10-11 13:00 | 179.84 | 170.19
2019-10-11 13:30 | 179.9 | 170.38
2019-10-11 14:00 | 181.21 | 171.57
2019-10-11 14:30 | 180.57 | 171.27
2019-10-11 15:00 | 181.08 | 171.71
2019-10-11 15:30 | 181.98 | 172.4
2019-10-11 16:00 | 183.83 | 174.43
2019-10-11 16:30 | 185.46 | 176.16
2019-10-11 17:00 | 187.34 | 178.04
2019-10-11 17:30 | 188.92 | 179.61
2019-10-11 18:00 | 189.85 | 180.55
2019-10-11 18:30 | 190.29 | 181.14
2019-10-11 19:00 | 191.53 | 182.47
2019-10-11 19:30 | 191.64 | 182.58
2019-10-11 20:00 | 190.39 | 181.15
2019-10-11 20:30 | 188.93 | 179.9
2019-10-11 21:00 | 187.52 | 178.72
2019-10-11 21:30 | 186.93 | 178.12
2019-10-11 22:00 | 185.63 | 177.08
2019-10-11 22:30 | 183.62 | 175.44
2019-10-11 23:00 | 182.69 | 174.02
2019-10-11 23:30 | 182.32 | 173.54
2019-10-12 | 180.2 | 172.02
2019-10-12 00:30 | 179.82 | 171.59
2019-10-12 01:00 | 179.16 | 170.77
2019-10-12 01:30 | 179.2 | 170.35
2019-10-12 02:00 | 178.64 | 169.85
2019-10-12 02:30 | 178.31 | 169.61
2019-10-12 03:00 | 178.23 | 169.58
2019-10-12 03:30 | 177.73 | 169.16
2019-10-12 04:00 | 177.8 | 169.32
2019-10-12 04:30 | 177.58 | 168.95
2019-10-12 05:00 | 177.54 | 168.85
2019-10-12 05:30 | 179.3 | 169.51
2019-10-12 06:00 | 180.79 | 170.1
2019-10-12 06:30 | 181.11 | 170.67
2019-10-12 07:00 | 179.36 | 169.41
2019-10-12 07:30 | 177.66 | 167.37
2019-10-12 08:00 | 179.28 | 169.2
2019-10-12 08:30 | 175.94 | 167.15
2019-10-12 09:00 | 174.8 | 165.75
2019-10-12 09:30 | 174.25 | 165.35
2019-10-12 10:00 | 174.71 | 165.89
2019-10-12 10:30 | 174.72 | 165.78
2019-10-12 11:00 | 175.41 | 165.7
2019-10-12 11:30 | 175.98 | 166.17
2019-10-12 12:00 | 172.13 | 164
2019-10-12 12:30 | 169.31 | 161.44
2019-10-12 13:00 | 168.76 | 162.16
2019-10-12 13:30 | 168.07 | 162
2019-10-12 14:00 | 167.98 | 162.3
2019-10-12 14:30 | 169.25 | 162.92
2019-10-12 15:00 | 170.57 | 163.67
2019-10-12 15:30 | 171.9 | 165.4
2019-10-12 16:00 | 174.2 | 167
2019-10-12 16:30 | 176.78 | 169.08
2019-10-12 17:00 | 179.18 | 171.14
2019-10-12 17:30 | 181.82 | 173.55
2019-10-12 18:00 | 183.61 | 175.52
2019-10-12 18:30 | 185.11 | 177.04
2019-10-12 19:00 | 185.16 | 177.09
2019-10-12 19:30 | 184.35 | 176.6
2019-10-12 20:00 | 183.38 | 175.5
2019-10-12 20:30 | 182.52 | 174.44
2019-10-12 21:00 | 181.56 | 173.36
2019-10-12 21:30 | 181.77 | 174.18
2019-10-12 22:00 | 181.08 | 173.45
2019-10-12 22:30 | 180.34 | 172.52
2019-10-12 23:00 | 176.14 | 169.12
2019-10-12 23:30 | 176.79 | 167
2019-10-13 | 178.53 | 167.88
2019-10-13 00:30 | 179.75 | 168.94
2019-10-13 01:00 | 178.71 | 167.85
2019-10-13 01:30 | 177.86 | 166.95
2019-10-13 02:00 | 177.78 | 166.91
2019-10-13 02:30 | 177.72 | 166.25
2019-10-13 03:00 | 179.05 | 166.16
2019-10-13 03:30 | 179.05 | 166.03
2019-10-13 04:00 | 178.48 | 165.63
2019-10-13 04:30 | 178.56 | 165.57
2019-10-13 05:00 | 179.2 | 166.24
2019-10-13 05:30 | 179.13 | 166.19
2019-10-13 06:00 | 180.32 | 167.07
2019-10-13 06:30 | 180.27 | 167.56
2019-10-13 07:00 | 177.84 | 165.97
2019-10-13 07:30 | 175.54 | 163.95
2019-10-13 08:00 | 173.81 | 162.7
2019-10-13 08:30 | 174.38 | 162.8
2019-10-13 09:00 | 174.57 | 162.96
2019-10-13 09:30 | 173.33 | 162.94
2019-10-13 10:00 | 172.01 | 162.93
2019-10-13 10:30 | 172.58 | 162.68
2019-10-13 11:00 | 172.42 | 162.37
2019-10-13 11:30 | 172.2 | 162.44
2019-10-13 12:00 | 162.15 | 152.85
2019-10-13 12:30 | 164.54 | 156.23
2019-10-13 13:00 | 165.11 | 156.75
2019-10-13 13:30 | 165.29 | 156.83
2019-10-13 14:00 | 166.36 | 157.91
2019-10-13 14:30 | 166.75 | 158.81
2019-10-13 15:00 | 168.39 | 160.39
2019-10-13 15:30 | 170.48 | 162.41
2019-10-13 16:00 | 172.63 | 164.59
2019-10-13 16:30 | 174.71 | 166.82
2019-10-13 17:00 | 177.12 | 169.31
2019-10-13 17:30 | 179.38 | 171.59
2019-10-13 18:00 | 181.6 | 173.9
2019-10-13 18:30 | 174.77 | 167.62
2019-10-13 19:00 | 159.57 | 153.22
2019-10-13 19:30 | 160.19 | 153.94
2019-10-13 20:00 | 161.36 | 155.19
2019-10-13 20:30 | 162.76 | 156.75
2019-10-13 21:00 | 163.75 | 157.87
2019-10-13 21:30 | 173.37 | 166.27
2019-10-13 22:00 | 175.59 | 168.32
2019-10-13 22:30 | 173.57 | 166.45
2019-10-13 23:00 | 172.08 | 164.88
2019-10-13 23:30 | 171.58 | 164.35
2019-10-14 | 170.52 | 163.28
2019-10-14 00:30 | 170.48 | 162.97
2019-10-14 01:00 | 185.6 | 179.8
2019-10-14 01:30 | 196.45 | 191.64
2019-10-14 02:00 | 196.06 | 191.11
2019-10-14 02:30 | 195.63 | 190.68
2019-10-14 03:00 | 195.45 | 190.46
2019-10-14 03:30 | 195.47 | 190.48
2019-10-14 04:00 | 195.89 | 190.87
2019-10-14 04:30 | 195.98 | 191.01
2019-10-14 05:00 | 196.44 | 191.5
2019-10-14 05:30 | 196.81 | 191.92
2019-10-14 06:00 | 197.75 | 192.97
2019-10-14 06:30 | 199.28 | 194.86
2019-10-14 07:00 | 200.63 | 196.33
2019-10-14 07:30 | 201.1 | 196.64
2019-10-14 08:00 | 200.36 | 195.28
2019-10-14 08:30 | 197.57 | 193.18
2019-10-14 09:00 | 196.18 | 192.16
2019-10-14 09:30 | 196.26 | 192.19
2019-10-14 10:00 | 196.17 | 191.93
2019-10-14 10:30 | 196.16 | 192.13
2019-10-14 11:00 | 196.55 | 192.55
2019-10-14 11:30 | 198.05 | 193.9
2019-10-14 12:00 | 200.29 | 195.71
2019-10-14 12:30 | 200.83 | 196.66
2019-10-14 13:00 | 202.7 | 198.44
2019-10-14 13:30 | 205.16 | 201.06
2019-10-14 14:00 | 207.38 | 203.4
2019-10-14 14:30 | 209.41 | 205.52
2019-10-14 15:00 | 210.73 | 206.8
2019-10-14 15:30 | 213.22 | 209.34
2019-10-14 16:00 | 215.39 | 211.55
2019-10-14 16:30 | 216.39 | 212.56
2019-10-14 17:00 | 217.6 | 213.84
2019-10-14 17:30 | 218.06 | 214.25
2019-10-14 18:00 | 219.38 | 215.43
2019-10-14 18:30 | 201.6 | 197.9
2019-10-14 19:00 | 189.77 | 186.24
2019-10-14 19:30 | 188.62 | 185.2
2019-10-14 20:00 | 185.82 | 182.44
2019-10-14 20:30 | 182.74 | 179.39
2019-10-14 21:00 | 183.02 | 179.73
2019-10-14 21:30 | 206.27 | 202.17
2019-10-14 22:00 | 209.57 | 205.37
2019-10-14 22:30 | 206.87 | 202.66
2019-10-14 23:00 | 204.53 | 200.22
2019-10-14 23:30 | 203.75 | 199.27
2019-10-15 | 202.06 | 197.49
2019-10-15 00:30 | 200.93 | 196.38
2019-10-15 01:00 | 199.92 | 195.36
2019-10-15 01:30 | 198.89 | 194.31
2019-10-15 02:00 | 198.55 | 193.87
2019-10-15 02:30 | 197.87 | 193.17
2019-10-15 03:00 | 197.29 | 192.54
2019-10-15 03:30 | 196.79 | 192.04
2019-10-15 04:00 | 196.75 | 191.97
2019-10-15 04:30 | 196.61 | 191.85
2019-10-15 05:00 | 197.03 | 192.28
2019-10-15 05:30 | 197.81 | 193.2
2019-10-15 06:00 | 198.95 | 194.47
2019-10-15 06:30 | 201.03 | 196.7
2019-10-15 07:00 | 201.91 | 197.31
2019-10-15 07:30 | 202.4 | 198.02
2019-10-15 08:00 | 201.3 | 196.97
2019-10-15 08:30 | 200.03 | 195.8
2019-10-15 09:00 | 199.43 | 195.21
2019-10-15 09:30 | 198.63 | 194.43
2019-10-15 10:00 | 199.21 | 194.95
2019-10-15 10:30 | 200.2 | 195.99
2019-10-15 11:00 | 200.9 | 196.65
2019-10-15 11:30 | 202.13 | 197.96
2019-10-15 12:00 | 203.66 | 199.56
2019-10-15 12:30 | 204.9 | 200.89
2019-10-15 13:00 | 206.86 | 202.75
2019-10-15 13:30 | 209.27 | 205.29
2019-10-15 14:00 | 211.01 | 206.99
2019-10-15 14:30 | 212.47 | 208.54
2019-10-15 15:00 | 213.01 | 209.13
2019-10-15 15:30 | 214.8 | 211.03
2019-10-15 16:00 | 217.58 | 213.9
2019-10-15 16:30 | 219.6 | 216
2019-10-15 17:00 | 221.84 | 218.33
2019-10-15 17:30 | 222.82 | 219.32
2019-10-15 18:00 | 224.25 | 220.67
2019-10-15 18:30 | 224.6 | 220.82
2019-10-15 19:00 | 225.45 | 221.76
2019-10-15 19:30 | 223.43 | 219.73
2019-10-15 20:00 | 219.43 | 215.62
2019-10-15 20:30 | 216.4 | 212.45
2019-10-15 21:00 | 213.15 | 208.94
2019-10-15 21:30 | 211.19 | 206.89
2019-10-15 22:00 | 208.29 | 203.9
2019-10-15 22:30 | 204.76 | 200.35
2019-10-15 23:00 | 202.66 | 198.17
2019-10-15 23:30 | 201.79 | 197.16
2019-10-16 | 200.04 | 195.42
2019-10-16 00:30 | 199.44 | 194.68
2019-10-16 01:00 | 198.22 | 193.55
2019-10-16 01:30 | 197.49 | 192.87
2019-10-16 02:00 | 197.03 | 192.43
2019-10-16 02:30 | 196.68 | 191.99
2019-10-16 03:00 | 196.35 | 191.54
2019-10-16 03:30 | 196.42 | 191.6
2019-10-16 04:00 | 196.27 | 191.48
2019-10-16 04:30 | 196.69 | 191.93
2019-10-16 05:00 | 197.15 | 192.44
2019-10-16 05:30 | 198.03 | 193.49
2019-10-16 06:00 | 199.13 | 194.61
2019-10-16 06:30 | 201.33 | 197.01
2019-10-16 07:00 | 193.9 | 190.33
2019-10-16 07:30 | 193.12 | 189.83
2019-10-16 08:00 | 193.38 | 190.07
2019-10-16 08:30 | 202.15 | 198.09
2019-10-16 09:00 | 202.78 | 198.62
2019-10-16 09:30 | 201.04 | 197.09
2019-10-16 10:00 | 195.75 | 192.06
2019-10-16 10:30 | 197.85 | 194.1
2019-10-16 11:00 | 201.14 | 197.33
2019-10-16 11:30 | 207.96 | 203.76
2019-10-16 12:00 | 209.84 | 205.79
2019-10-16 12:30 | 213.02 | 208.84
2019-10-16 13:00 | 217.53 | 213.18
2019-10-16 13:30 | 219.57 | 215.45
2019-10-16 14:00 | 219.81 | 216.09
2019-10-16 14:30 | 220.16 | 216.55
2019-10-16 15:00 | 221.36 | 217.83
2019-10-16 15:30 | 222.67 | 219.17
2019-10-16 16:00 | 223.84 | 220.53
2019-10-16 16:30 | 225.7 | 222.38
2019-10-16 17:00 | 227.01 | 223.68
2019-10-16 17:30 | 227.89 | 224.5
2019-10-16 18:00 | 228.85 | 225.27
2019-10-16 18:30 | 230.58 | 226.96
2019-10-16 19:00 | 232.26 | 228.7
2019-10-16 19:30 | 230.38 | 226.87
2019-10-16 20:00 | 227.18 | 223.56
2019-10-16 20:30 | 224.13 | 220.42
2019-10-16 21:00 | 220.46 | 216.62
2019-10-16 21:30 | 218.68 | 214.65
2019-10-16 22:00 | 215.25 | 211.13
2019-10-16 22:30 | 212.52 | 208.34
2019-10-16 23:00 | 210.43 | 206.17
2019-10-16 23:30 | 208.91 | 204.63
2019-10-17 | 207.77 | 203.29
2019-10-17 00:30 | 206.36 | 201.9
2019-10-17 01:00 | 205.68 | 201.13
2019-10-17 01:30 | 204.65 | 200.05
2019-10-17 02:00 | 203.93 | 199.3
2019-10-17 02:30 | 203.55 | 198.87
2019-10-17 03:00 | 202.96 | 198.26
2019-10-17 03:30 | 202.41 | 197.69
2019-10-17 04:00 | 202.41 | 197.64
2019-10-17 04:30 | 202.59 | 197.84
2019-10-17 05:00 | 203.07 | 198.3
2019-10-17 05:30 | 204.18 | 199.48
2019-10-17 06:00 | 205.22 | 200.53
2019-10-17 06:30 | 205.69 | 201.23
2019-10-17 07:00 | 209.08 | 204.57
2019-10-17 07:30 | 210.62 | 206.39
2019-10-17 08:00 | 210.46 | 206.22
2019-10-17 08:30 | 210.19 | 205.94
2019-10-17 09:00 | 209.49 | 205.27
2019-10-17 09:30 | 208.76 | 204.52
2019-10-17 10:00 | 209.64 | 205.35
2019-10-17 10:30 | 210.47 | 206.29
2019-10-17 11:00 | 211.75 | 207.62
2019-10-17 11:30 | 213.16 | 209.01
2019-10-17 12:00 | 215.36 | 211.38
2019-10-17 12:30 | 218.6 | 214.49
2019-10-17 13:00 | 212.66 | 208.97
2019-10-17 13:30 | 213.57 | 209.94
2019-10-17 14:00 | 217.33 | 213.56
2019-10-17 14:30 | 216.93 | 213.25
2019-10-17 15:00 | 213.98 | 210.57
2019-10-17 15:30 | 213.83 | 210.64
2019-10-17 16:00 | 216.52 | 213.24
2019-10-17 16:30 | 217.5 | 214.14
2019-10-17 17:00 | 218.32 | 214.76
2019-10-17 17:30 | 218.92 | 215.32
2019-10-17 18:00 | 219.58 | 215.99
2019-10-17 18:30 | 220.16 | 216.58
2019-10-17 19:00 | 221.76 | 218.19
2019-10-17 19:30 | 220.06 | 216.48
2019-10-17 20:00 | 217.41 | 213.68
2019-10-17 20:30 | 214.52 | 210.57
2019-10-17 21:00 | 212.44 | 208.3
2019-10-17 21:30 | 210.17 | 205.98
2019-10-17 22:00 | 207.88 | 203.6
2019-10-17 22:30 | 205.64 | 201.29
2019-10-17 23:00 | 203.87 | 199.46
2019-10-17 23:30 | 202.76 | 198.26
2019-10-18 | 201.41 | 196.85
2019-10-18 00:30 | 200.45 | 195.76
2019-10-18 01:00 | 199.65 | 194.77
2019-10-18 01:30 | 199.16 | 194.14
2019-10-18 02:00 | 198.71 | 193.6
2019-10-18 02:30 | 198.44 | 193.29
2019-10-18 03:00 | 198.11 | 192.96
2019-10-18 03:30 | 197.94 | 192.78
2019-10-18 04:00 | 198.03 | 192.87
2019-10-18 04:30 | 198.34 | 193.24
2019-10-18 05:00 | 198.34 | 193.4
2019-10-18 05:30 | 199.24 | 194.39
2019-10-18 06:00 | 199.92 | 195.22
2019-10-18 06:30 | 201.12 | 196.68
2019-10-18 07:00 | 201.87 | 197.43
2019-10-18 07:30 | 202.11 | 197.75
2019-10-18 08:00 | 201.05 | 196.75
2019-10-18 08:30 | 199.23 | 194.97
2019-10-18 09:00 | 198.36 | 194.07
2019-10-18 09:30 | 197.13 | 192.96
2019-10-18 10:00 | 196.96 | 192.85
2019-10-18 10:30 | 197.3 | 193.18
2019-10-18 11:00 | 197.66 | 193.64
2019-10-18 11:30 | 198.16 | 194.1
2019-10-18 12:00 | 198.92 | 194.64
2019-10-18 12:30 | 199.34 | 195
2019-10-18 13:00 | 201.21 | 196.76
2019-10-18 13:30 | 202.42 | 197.98
2019-10-18 14:00 | 203.1 | 199
2019-10-18 14:30 | 205.04 | 201.05
2019-10-18 15:00 | 206.21 | 202.21
2019-10-18 15:30 | 207.32 | 203.45
2019-10-18 16:00 | 209.88 | 205.94
2019-10-18 16:30 | 212.18 | 208.33
2019-10-18 17:00 | 213.35 | 209.5
2019-10-18 17:30 | 186.63 | 183.14
2019-10-18 18:00 | 185.69 | 182.22
2019-10-18 18:30 | 185.81 | 182.31
2019-10-18 19:00 | 185.17 | 181.67
2019-10-18 19:30 | 185.07 | 181.69
2019-10-18 20:00 | 186.86 | 183.51
2019-10-18 20:30 | 187.73 | 184.4
2019-10-18 21:00 | 189.41 | 186.01
2019-10-18 21:30 | 190.37 | 186.79
2019-10-18 22:00 | 199.23 | 194.76
2019-10-18 22:30 | 203.59 | 198.96
2019-10-18 23:00 | 201.79 | 197.11
2019-10-18 23:30 | 201.06 | 196.28
2019-10-19 | 199.81 | 194.94
2019-10-19 00:30 | 198.4 | 193.54
2019-10-19 01:00 | 197.58 | 192.41
2019-10-19 01:30 | 197.27 | 192.11
2019-10-19 02:00 | 196.49 | 191.37
2019-10-19 02:30 | 196.42 | 191.29
2019-10-19 03:00 | 196.28 | 191.16
2019-10-19 03:30 | 196.08 | 190.96
2019-10-19 04:00 | 195.88 | 190.75
2019-10-19 04:30 | 196.11 | 190.97
2019-10-19 05:00 | 196.39 | 191.25
2019-10-19 05:30 | 197.02 | 191.88
2019-10-19 06:00 | 196.94 | 191.76
2019-10-19 06:30 | 197.53 | 192.31
2019-10-19 07:00 | 197.62 | 192.66
2019-10-19 07:30 | 197.21 | 192.36
2019-10-19 08:00 | 196.72 | 191.95
2019-10-19 08:30 | 195.76 | 191.09
2019-10-19 09:00 | 195.56 | 190.98
2019-10-19 09:30 | 195.27 | 190.7
2019-10-19 10:00 | 194.84 | 190.23
2019-10-19 10:30 | 194.59 | 190.12
2019-10-19 11:00 | 194.37 | 189.95
2019-10-19 11:30 | 195.44 | 191
2019-10-19 12:00 | 196.63 | 192.16
2019-10-19 12:30 | 196.84 | 192.46
2019-10-19 13:00 | 197.58 | 193.13
2019-10-19 13:30 | 198.46 | 194.16
2019-10-19 14:00 | 199.03 | 194.72
2019-10-19 14:30 | 200.46 | 196.09
2019-10-19 15:00 | 202.08 | 197.7
2019-10-19 15:30 | 203.95 | 199.56
2019-10-19 16:00 | 206.21 | 201.86
2019-10-19 16:30 | 208.14 | 203.96
2019-10-19 17:00 | 210.2 | 206.08
2019-10-19 17:30 | 212.01 | 207.93
2019-10-19 18:00 | 212.58 | 208.57
2019-10-19 18:30 | 212.52 | 208.53
2019-10-19 19:00 | 212.48 | 208.5
2019-10-19 19:30 | 211.65 | 207.55
2019-10-19 20:00 | 209.41 | 205.15
2019-10-19 20:30 | 207.58 | 203.18
2019-10-19 21:00 | 205.61 | 201.14
2019-10-19 21:30 | 204.14 | 199.44
2019-10-19 22:00 | 202.13 | 197.32
2019-10-19 22:30 | 200.57 | 195.57
2019-10-19 23:00 | 199.27 | 194.09
2019-10-19 23:30 | 198.63 | 193.37
2019-10-20 | 197.41 | 192.23
2019-10-20 00:30 | 196.79 | 191.61
2019-10-20 01:00 | 196.12 | 190.94
2019-10-20 01:30 | 195.69 | 190.45
2019-10-20 02:00 | 194.91 | 189.6
2019-10-20 02:30 | 194.98 | 189.67
2019-10-20 03:00 | 194.76 | 189.43
2019-10-20 03:30 | 194.72 | 189.38
2019-10-20 04:00 | 194.62 | 189.27
2019-10-20 04:30 | 194.81 | 189.45
2019-10-20 05:00 | 194.89 | 189.52
2019-10-20 05:30 | 195.08 | 189.76
2019-10-20 06:00 | 195.38 | 190.03
2019-10-20 06:30 | 195.57 | 190.11
2019-10-20 07:00 | 194.88 | 189.58
2019-10-20 07:30 | 194.74 | 189.51
2019-10-20 08:00 | 194.41 | 189.13
2019-10-20 08:30 | 193.16 | 188.12
2019-10-20 09:00 | 192.22 | 187.23
2019-10-20 09:30 | 191.64 | 186.61
2019-10-20 10:00 | 191.75 | 186.76
2019-10-20 10:30 | 191.39 | 186.36
2019-10-20 11:00 | 191.14 | 186.21
2019-10-20 11:30 | 191.61 | 186.71
2019-10-20 12:00 | 191.93 | 187.03
2019-10-20 12:30 | 192.3 | 187.43
2019-10-20 13:00 | 192.58 | 187.75
2019-10-20 13:30 | 193.27 | 188.53
2019-10-20 14:00 | 193.83 | 189.17
2019-10-20 14:30 | 194.68 | 190.07
2019-10-20 15:00 | 196.09 | 191.56
2019-10-20 15:30 | 197.54 | 193.08
2019-10-20 16:00 | 199.37 | 194.98
2019-10-20 16:30 | 201.65 | 197.36
2019-10-20 17:00 | 204.01 | 199.75
2019-10-20 17:30 | 205.85 | 201.55
2019-10-20 18:00 | 195.45 | 191.78
2019-10-20 18:30 | 187.75 | 184.44
2019-10-20 19:00 | 187.18 | 183.92
2019-10-20 19:30 | 187.76 | 184.39
2019-10-20 20:00 | 189.42 | 185.56
2019-10-20 20:30 | 201.12 | 196.54
2019-10-20 21:00 | 203.33 | 198.6
2019-10-20 21:30 | 202.16 | 197.38
2019-10-20 22:00 | 200.66 | 195.83
2019-10-20 22:30 | 198.8 | 193.89
2019-10-20 23:00 | 197.48 | 192.46
2019-10-20 23:30 | 196.98 | 191.9
2019-10-21 | 196.02 | 190.79
2019-10-21 00:30 | 195.32 | 190.14
2019-10-21 01:00 | 194.62 | 189.43
2019-10-21 01:30 | 194.16 | 188.97
2019-10-21 02:00 | 194.16 | 188.94
2019-10-21 02:30 | 193.74 | 188.49
2019-10-21 03:00 | 193.89 | 188.51
2019-10-21 03:30 | 193.99 | 188.52
2019-10-21 04:00 | 193.74 | 188.24
2019-10-21 04:30 | 194.35 | 188.83
2019-10-21 05:00 | 194.78 | 189.5
2019-10-21 05:30 | 196.32 | 191.19
2019-10-21 06:00 | 197.12 | 192.1
2019-10-21 06:30 | 198.28 | 193.49
2019-10-21 07:00 | 198.18 | 193.56
2019-10-21 07:30 | 198.4 | 194
2019-10-21 08:00 | 197.29 | 192.96
2019-10-21 08:30 | 195.78 | 191.46
2019-10-21 09:00 | 194.36 | 190.03
2019-10-21 09:30 | 193.07 | 188.89
2019-10-21 10:00 | 193.3 | 189.05
2019-10-21 10:30 | 193.18 | 189.04
2019-10-21 11:00 | 193.69 | 189.55
2019-10-21 11:30 | 194.07 | 189.91
2019-10-21 12:00 | 194.36 | 190.22
2019-10-21 12:30 | 194.77 | 190.47
2019-10-21 13:00 | 196.16 | 191.76
2019-10-21 13:30 | 197.87 | 193.58
2019-10-21 14:00 | 199.55 | 194.86
2019-10-21 14:30 | 200.32 | 196.04
2019-10-21 15:00 | 201.43 | 196.96
2019-10-21 15:30 | 202.51 | 198.19
2019-10-21 16:00 | 204.85 | 200.54
2019-10-21 16:30 | 205.98 | 201.63
2019-10-21 17:00 | 207.63 | 203.26
2019-10-21 17:30 | 208.16 | 203.9
2019-10-21 18:00 | 187.69 | 184.03
2019-10-21 18:30 | 187.53 | 183.32
2019-10-21 19:00 | 186.68 | 182.52
2019-10-21 19:30 | 186.69 | 183.14
2019-10-21 20:00 | 187.78 | 184.51
2019-10-21 20:30 | 204.53 | 200.03
2019-10-21 21:00 | 207.25 | 202.36
2019-10-21 21:30 | 206.55 | 201.49
2019-10-21 22:00 | 204.69 | 199.58
2019-10-21 22:30 | 202.4 | 197.31
2019-10-21 23:00 | 200.49 | 195.38
2019-10-21 23:30 | 199.7 | 194.42
2019-10-22 | 198.46 | 193.04
2019-10-22 00:30 | 198.01 | 192.51
2019-10-22 01:00 | 197.14 | 191.63
2019-10-22 01:30 | 196.66 | 191.09
2019-10-22 02:00 | 195.91 | 190.27
2019-10-22 02:30 | 195.75 | 190.08
2019-10-22 03:00 | 195.61 | 189.94
2019-10-22 03:30 | 195.69 | 190.02
2019-10-22 04:00 | 195.97 | 190.26
2019-10-22 04:30 | 196.25 | 190.57
2019-10-22 05:00 | 196.92 | 191.24
2019-10-22 05:30 | 198.25 | 192.67
2019-10-22 06:00 | 199.3 | 193.97
2019-10-22 06:30 | 200.25 | 195.47
2019-10-22 07:00 | 200.69 | 196.21
2019-10-22 07:30 | 200.72 | 196.39
2019-10-22 08:00 | 199.4 | 195.11
2019-10-22 08:30 | 197.42 | 193.08
2019-10-22 09:00 | 196.22 | 191.75
2019-10-22 09:30 | 195.36 | 190.89
2019-10-22 10:00 | 195.37 | 190.93
2019-10-22 10:30 | 195.05 | 190.56
2019-10-22 11:00 | 195.65 | 191.13
2019-10-22 11:30 | 196.29 | 191.76
2019-10-22 12:00 | 196.9 | 192.55
2019-10-22 12:30 | 197.72 | 193.47
2019-10-22 13:00 | 199.36 | 194.83
2019-10-22 13:30 | 200.33 | 195.85
2019-10-22 14:00 | 202.02 | 197.66
2019-10-22 14:30 | 203.14 | 198.83
2019-10-22 15:00 | 204.61 | 200.23
2019-10-22 15:30 | 205.42 | 201.15
2019-10-22 16:00 | 207.77 | 203.53
2019-10-22 16:30 | 209.5 | 205.23
2019-10-22 17:00 | 210.9 | 206.79
2019-10-22 17:30 | 211.93 | 207.79
2019-10-22 18:00 | 213.37 | 209.22
2019-10-22 18:30 | 214.59 | 210.31
2019-10-22 19:00 | 216.47 | 212.28
2019-10-22 19:30 | 215.92 | 211.67
2019-10-22 20:00 | 213.03 | 208.73
2019-10-22 20:30 | 211.06 | 206.54
2019-10-22 21:00 | 208.48 | 203.84
2019-10-22 21:30 | 207.34 | 202.42
2019-10-22 22:00 | 205.48 | 200.57
2019-10-22 22:30 | 203.45 | 198.56
2019-10-22 23:00 | 201.45 | 196.37
2019-10-22 23:30 | 200.64 | 195.53
2019-10-23 | 199.33 | 194.1
2019-10-23 00:30 | 198.51 | 193.12
2019-10-23 01:00 | 197.7 | 192.3
2019-10-23 01:30 | 197.17 | 191.83
2019-10-23 02:00 | 196.46 | 191.16
2019-10-23 02:30 | 196.34 | 191.01
2019-10-23 03:00 | 195.98 | 190.56
2019-10-23 03:30 | 195.82 | 190.38
2019-10-23 04:00 | 196.11 | 190.69
2019-10-23 04:30 | 196.21 | 190.77
2019-10-23 05:00 | 197.04 | 191.63
2019-10-23 05:30 | 198.41 | 193.12
2019-10-23 06:00 | 199.45 | 194.31
2019-10-23 06:30 | 201.04 | 196.13
2019-10-23 07:00 | 201.77 | 197.05
2019-10-23 07:30 | 201.87 | 197.34
2019-10-23 08:00 | 200.98 | 196.54
2019-10-23 08:30 | 198.85 | 194.37
2019-10-23 09:00 | 197.63 | 193.01
2019-10-23 09:30 | 196.45 | 191.87
2019-10-23 10:00 | 197.02 | 192.27
2019-10-23 10:30 | 197.1 | 192.47
2019-10-23 11:00 | 197.54 | 192.96
2019-10-23 11:30 | 198.64 | 194.11
2019-10-23 12:00 | 198.97 | 194.67
2019-10-23 12:30 | 199.22 | 195.03
2019-10-23 13:00 | 200.79 | 196.46
2019-10-23 13:30 | 202.01 | 197.62
2019-10-23 14:00 | 203.71 | 199.37
2019-10-23 14:30 | 205.09 | 200.8
2019-10-23 15:00 | 206.4 | 202.09
2019-10-23 15:30 | 207.3 | 203.21
2019-10-23 16:00 | 209.37 | 205.17
2019-10-23 16:30 | 211.13 | 206.97
2019-10-23 17:00 | 212.67 | 208.27
2019-10-23 17:30 | 213.78 | 209.42
2019-10-23 18:00 | 215.04 | 210.65
2019-10-23 18:30 | 215.82 | 211.34
2019-10-23 19:00 | 217.37 | 213.15
2019-10-23 19:30 | 216.54 | 212.37
2019-10-23 20:00 | 213.93 | 209.61
2019-10-23 20:30 | 212.09 | 207.62
2019-10-23 21:00 | 209.77 | 205.06
2019-10-23 21:30 | 208.32 | 203.67
2019-10-23 22:00 | 206.62 | 201.75
2019-10-23 22:30 | 204.88 | 199.78
2019-10-23 23:00 | 203.43 | 198.27
2019-10-23 23:30 | 202.61 | 197.28
2019-10-24 | 201.76 | 196.53
2019-10-24 00:30 | 201.22 | 196.11
2019-10-24 01:00 | 199.56 | 194.35
2019-10-24 01:30 | 198.6 | 193.33
2019-10-24 02:00 | 198.21 | 193.02
2019-10-24 02:30 | 197.91 | 192.71
2019-10-24 03:00 | 197.75 | 192.52
2019-10-24 03:30 | 197.61 | 192.34
2019-10-24 04:00 | 197.57 | 192.31
2019-10-24 04:30 | 197.65 | 192.42
2019-10-24 05:00 | 198.23 | 192.99
2019-10-24 05:30 | 199.19 | 193.99
2019-10-24 06:00 | 200.56 | 195.5
2019-10-24 06:30 | 202.2 | 197.25
2019-10-24 07:00 | 203.24 | 198.29
2019-10-24 07:30 | 203.23 | 198.54
2019-10-24 08:00 | 201.83 | 197.14
2019-10-24 08:30 | 200.42 | 195.81
2019-10-24 09:00 | 198.93 | 194.16
2019-10-24 09:30 | 198.72 | 193.96
2019-10-24 10:00 | 198.41 | 193.62
2019-10-24 10:30 | 198.5 | 193.87
2019-10-24 11:00 | 198.75 | 194.08
2019-10-24 11:30 | 199.4 | 194.71
2019-10-24 12:00 | 200.33 | 195.73
2019-10-24 12:30 | 201.25 | 196.58
2019-10-24 13:00 | 202.81 | 198.13
2019-10-24 13:30 | 204.21 | 199.75
2019-10-24 14:00 | 205.34 | 200.9
2019-10-24 14:30 | 207.43 | 202.95
2019-10-24 15:00 | 210.14 | 205.61
2019-10-24 15:30 | 211.12 | 206.66
2019-10-24 16:00 | 212.74 | 208.29
2019-10-24 16:30 | 214.38 | 210.01
2019-10-24 17:00 | 216.32 | 211.9
2019-10-24 17:30 | 211.26 | 206.88
2019-10-24 18:00 | 185.63 | 182.15
2019-10-24 18:30 | 184.86 | 181.53
2019-10-24 19:00 | 185.53 | 182.06
2019-10-24 19:30 | 185.34 | 181.94
2019-10-24 20:00 | 187.02 | 183.71
2019-10-24 20:30 | 208.89 | 204.57
2019-10-24 21:00 | 212.4 | 207.74
2019-10-24 21:30 | 211.41 | 206.48
2019-10-24 22:00 | 208.99 | 204.19
2019-10-24 22:30 | 206.71 | 201.74
2019-10-24 23:00 | 205.46 | 200.19
2019-10-24 23:30 | 205 | 199.73
2019-10-25 | 203.96 | 198.67
2019-10-25 00:30 | 202.61 | 197.33
2019-10-25 01:00 | 201.82 | 196.39
2019-10-25 01:30 | 201.37 | 195.87
2019-10-25 02:00 | 200.7 | 195.12
2019-10-25 02:30 | 200.14 | 194.48
2019-10-25 03:00 | 199.56 | 193.88
2019-10-25 03:30 | 199.58 | 193.93
2019-10-25 04:00 | 199.71 | 194.07
2019-10-25 04:30 | 199.88 | 194.29
2019-10-25 05:00 | 200.28 | 194.67
2019-10-25 05:30 | 201.07 | 195.53
2019-10-25 06:00 | 202.25 | 197.07
2019-10-25 06:30 | 203.5 | 198.49
2019-10-25 07:00 | 204.98 | 199.9
2019-10-25 07:30 | 205.16 | 200.2
2019-10-25 08:00 | 203.73 | 198.93
2019-10-25 08:30 | 203.15 | 198.27
2019-10-25 09:00 | 201.62 | 196.71
2019-10-25 09:30 | 200.94 | 196.18
2019-10-25 10:00 | 200.85 | 196.17
2019-10-25 10:30 | 201.85 | 197.07
2019-10-25 11:00 | 202.92 | 198.09
2019-10-25 11:30 | 204.28 | 199.41
2019-10-25 12:00 | 205.25 | 200.39
2019-10-25 12:30 | 205.71 | 200.84
2019-10-25 13:00 | 207.33 | 202.51
2019-10-25 13:30 | 208.5 | 203.56
2019-10-25 14:00 | 209.34 | 204.47
2019-10-25 14:30 | 210.77 | 205.99
2019-10-25 15:00 | 211.08 | 206.51
2019-10-25 15:30 | 212.22 | 207.69
2019-10-25 16:00 | 214.47 | 210.12
2019-10-25 16:30 | 216.47 | 212.31
2019-10-25 17:00 | 218.55 | 214.43
2019-10-25 17:30 | 219.25 | 215.01
2019-10-25 18:00 | 220.46 | 216.03
2019-10-25 18:30 | 220.16 | 215.68
2019-10-25 19:00 | 220.09 | 215.69
2019-10-25 19:30 | 219 | 214.6
2019-10-25 20:00 | 215.93 | 211.47
2019-10-25 20:30 | 214.05 | 209.47
2019-10-25 21:00 | 212.01 | 207.27
2019-10-25 21:30 | 210.84 | 205.9
2019-10-25 22:00 | 209.59 | 204.57
2019-10-25 22:30 | 207.87 | 202.73
2019-10-25 23:00 | 206.01 | 200.82
2019-10-25 23:30 | 205.73 | 200.53
2019-10-26 | 204.58 | 199.35
2019-10-26 00:30 | 203.59 | 198.3
2019-10-26 01:00 | 202.6 | 197.27
2019-10-26 01:30 | 201.83 | 196.6
2019-10-26 02:00 | 201.39 | 196.19
2019-10-26 02:30 | 200.75 | 195.53
2019-10-26 03:00 | 200.1 | 194.86
2019-10-26 03:30 | 199.79 | 194.56
2019-10-26 04:00 | 199.62 | 194.39
2019-10-26 04:30 | 199.48 | 194.22
2019-10-26 05:00 | 199.9 | 194.6
2019-10-26 05:30 | 200.47 | 195.11
2019-10-26 06:00 | 200.92 | 195.55
2019-10-26 06:30 | 201.48 | 196.16
2019-10-26 07:00 | 202.14 | 196.82
2019-10-26 07:30 | 177.41 | 171.32
2019-10-26 08:00 | 171.68 | 164.35
2019-10-26 08:30 | 174.84 | 167.47
2019-10-26 09:00 | 175.92 | 168.62
2019-10-26 09:30 | 176.28 | 168.91
2019-10-26 10:00 | 164.01 | 156.2
2019-10-26 10:30 | 169.31 | 162.54
2019-10-26 11:00 | 170.75 | 164.11
2019-10-26 11:30 | 171.95 | 165.32
2019-10-26 12:00 | 173.07 | 166.48
2019-10-26 12:30 | 180.2 | 174.45
2019-10-26 13:00 | 182.92 | 177.25
2019-10-26 13:30 | 184.31 | 178.72
2019-10-26 14:00 | 185.54 | 180.03
2019-10-26 14:30 | 186.81 | 181.41
2019-10-26 15:00 | 182.34 | 176.11
2019-10-26 15:30 | 182.44 | 175.14
2019-10-26 16:00 | 182.03 | 175.08
2019-10-26 16:30 | 163.65 | 157.06
2019-10-26 17:00 | 164.89 | 158.2
2019-10-26 17:30 | 165.88 | 159.16
2019-10-26 18:00 | 167.25 | 160.53
2019-10-26 18:30 | 167.51 | 160.83
2019-10-26 19:00 | 167.11 | 160.47
2019-10-26 19:30 | 166.3 | 159.66
2019-10-26 20:00 | 163.64 | 157.06
2019-10-26 20:30 | 164.14 | 157.67
2019-10-26 21:00 | 165.5 | 159.13
2019-10-26 21:30 | 185.06 | 178.08
2019-10-26 22:00 | 190.11 | 182.84
2019-10-26 22:30 | 187.85 | 180.32
2019-10-26 23:00 | 186.36 | 178.67
2019-10-26 23:30 | 185.97 | 178.35
2019-10-27 | 184.6 | 177.03
2019-10-27 00:30 | 162 | 154.73
2019-10-27 01:00 | 177.4 | 171.09
2019-10-27 01:30 | 180.07 | 173.77
2019-10-27 02:00 | 179.59 | 173.2
2019-10-27 02:30 | 178.9 | 172.46
2019-10-27 03:00 | 178.38 | 171.87
2019-10-27 03:30 | 177.9 | 171.37
2019-10-27 04:00 | 177.96 | 171.42
2019-10-27 04:30 | 178.14 | 171.57
2019-10-27 05:00 | 177.94 | 171.47
2019-10-27 05:30 | 178.12 | 171.74
2019-10-27 06:00 | 178.17 | 171.77
2019-10-27 06:30 | 178.33 | 171.8
2019-10-27 07:00 | 178.06 | 171.64
2019-10-27 07:30 | 188.38 | 182.66
2019-10-27 08:00 | 198.72 | 193.69
2019-10-27 08:30 | 198.16 | 193.2
2019-10-27 09:00 | 197.64 | 192.66
2019-10-27 09:30 | 197.24 | 192.28
2019-10-27 10:00 | 196.98 | 192.1
2019-10-27 10:30 | 196.77 | 191.86
2019-10-27 11:00 | 197.35 | 192.49
2019-10-27 11:30 | 198.43 | 193.48
2019-10-27 12:00 | 199.82 | 194.97
2019-10-27 12:30 | 201.08 | 196.31
2019-10-27 13:00 | 202.59 | 197.84
2019-10-27 13:30 | 203.99 | 199.32
2019-10-27 14:00 | 205.13 | 200.53
2019-10-27 14:30 | 206.69 | 202.14
2019-10-27 15:00 | 208.6 | 204.07
2019-10-27 15:30 | 210.35 | 205.86
2019-10-27 16:00 | 189.94 | 184.46
2019-10-27 16:30 | 187.22 | 180.24
2019-10-27 17:00 | 192.33 | 185.26
2019-10-27 17:30 | 194.51 | 187.87
2019-10-27 18:00 | 190.44 | 184.34
2019-10-27 18:30 | 164.06 | 158.45
2019-10-27 19:00 | 164.57 | 158.63
2019-10-27 19:30 | 165.07 | 159.28
2019-10-27 20:00 | 166.68 | 161.16
2019-10-27 20:30 | 168.46 | 163.14
2019-10-27 21:00 | 186.22 | 179.5
2019-10-27 21:30 | 190.12 | 183.32
2019-10-27 22:00 | 188.7 | 181.96
2019-10-27 22:30 | 186.72 | 179.6
2019-10-27 23:00 | 185.5 | 178.24
2019-10-27 23:30 | 185.01 | 177.69
2019-10-28 | 183.64 | 176.46
2019-10-28 00:30 | 182.83 | 175.72
2019-10-28 01:00 | 181.71 | 174.94
2019-10-28 01:30 | 157.56 | 150.89
2019-10-28 02:00 | 154.84 | 148.36
2019-10-28 02:30 | 154.87 | 148.41
2019-10-28 03:00 | 154.63 | 148.02
2019-10-28 03:30 | 154.07 | 147.53
2019-10-28 04:00 | 153.67 | 147.19
2019-10-28 04:30 | 153.2 | 146.8
2019-10-28 05:00 | 153.42 | 146.93
2019-10-28 05:30 | 171.65 | 164.78
2019-10-28 06:00 | 182.81 | 176.34
2019-10-28 06:30 | 183.42 | 177.03
2019-10-28 07:00 | 184.21 | 177.04
2019-10-28 07:30 | 183.94 | 176.76
2019-10-28 08:00 | 182.86 | 175.44
2019-10-28 08:30 | 182.46 | 174.97
2019-10-28 09:00 | 181.34 | 173.95
2019-10-28 09:30 | 180.31 | 172.76
2019-10-28 10:00 | 180.63 | 173.08
2019-10-28 10:30 | 180.59 | 172.96
2019-10-28 11:00 | 180.92 | 173.15
2019-10-28 11:30 | 182.27 | 174.4
2019-10-28 12:00 | 182.66 | 174.83
2019-10-28 12:30 | 183.17 | 175.33
2019-10-28 13:00 | 184.34 | 176.45
2019-10-28 13:30 | 185.76 | 178.6
2019-10-28 14:00 | 186.41 | 179.7
2019-10-28 14:30 | 188.66 | 181.9
2019-10-28 15:00 | 190.6 | 183.53
2019-10-28 15:30 | 191.41 | 184.45
2019-10-28 16:00 | 192.93 | 186.1
2019-10-28 16:30 | 194.1 | 187.22
2019-10-28 17:00 | 194.72 | 187.79
2019-10-28 17:30 | 181.76 | 175.08
2019-10-28 18:00 | 169.05 | 162.46
2019-10-28 18:30 | 168.67 | 161.9
2019-10-28 19:00 | 168.29 | 161.44
2019-10-28 19:30 | 168.74 | 162.03
2019-10-28 20:00 | 169.73 | 163.25
2019-10-28 20:30 | 171.16 | 164.74
2019-10-28 21:00 | 187.17 | 180.67
2019-10-28 21:30 | 189.13 | 183.03
2019-10-28 22:00 | 185.48 | 179.82
2019-10-28 22:30 | 182.84 | 177.43
2019-10-28 23:00 | 181.62 | 176.18
2019-10-28 23:30 | 180.87 | 175.38
2019-10-29 | 180.9 | 174.35
2019-10-29 00:30 | 180.16 | 173.67
2019-10-29 01:00 | 179.26 | 173.11
2019-10-29 01:30 | 157.6 | 151.78
2019-10-29 02:00 | 155.2 | 149.58
2019-10-29 02:30 | 154.98 | 149.54
2019-10-29 03:00 | 154.76 | 149.14
2019-10-29 03:30 | 153.86 | 148.3
2019-10-29 04:00 | 154.11 | 148.65
2019-10-29 04:30 | 153.75 | 148.44
2019-10-29 05:00 | 155.11 | 149.8
2019-10-29 05:30 | 171.06 | 165.32
2019-10-29 06:00 | 181.74 | 176.44
2019-10-29 06:30 | 184.25 | 178.85
2019-10-29 07:00 | 185.13 | 179.52
2019-10-29 07:30 | 185.49 | 179.64
2019-10-29 08:00 | 184.09 | 178.35
2019-10-29 08:30 | 182.79 | 176.99
2019-10-29 09:00 | 160.14 | 154.29
2019-10-29 09:30 | 157.54 | 151.12
2019-10-29 10:00 | 158.97 | 152.59
2019-10-29 10:30 | 159.94 | 153.5
2019-10-29 11:00 | 160.12 | 153.69
2019-10-29 11:30 | 161.87 | 155.59
2019-10-29 12:00 | 163.1 | 156.87
2019-10-29 12:30 | 163.98 | 157.9
2019-10-29 13:00 | 166.32 | 159.98
2019-10-29 13:30 | 166.79 | 160.79
2019-10-29 14:00 | 167.88 | 162.11
2019-10-29 14:30 | 167.96 | 162
2019-10-29 15:00 | 168.23 | 162.55
2019-10-29 15:30 | 168.23 | 162.48
2019-10-29 16:00 | 181.34 | 174.92
2019-10-29 16:30 | 191.23 | 184.72
2019-10-29 17:00 | 169.64 | 163.68
2019-10-29 17:30 | 166.46 | 160.54
2019-10-29 18:00 | 166.54 | 160.51
2019-10-29 18:30 | 166.31 | 160.04
2019-10-29 19:00 | 165.72 | 159.48
2019-10-29 19:30 | 166.62 | 160.43
2019-10-29 20:00 | 167.16 | 161.04
2019-10-29 20:30 | 168.16 | 162.05
2019-10-29 21:00 | 186.43 | 178.76
2019-10-29 21:30 | 190.98 | 182.95
2019-10-29 22:00 | 187.68 | 181
2019-10-29 22:30 | 185.57 | 178.78
2019-10-29 23:00 | 183.54 | 177.03
2019-10-29 23:30 | 183.08 | 176.62
2019-10-30 | 181.91 | 175.51
2019-10-30 00:30 | 180.73 | 174.81
2019-10-30 01:00 | 179.33 | 173.82
2019-10-30 01:30 | 179.45 | 173.62
2019-10-30 02:00 | 178.86 | 172.97
2019-10-30 02:30 | 178.24 | 172.68
2019-10-30 03:00 | 178.19 | 172.58
2019-10-30 03:30 | 178.04 | 172.13
2019-10-30 04:00 | 179.09 | 172.39
2019-10-30 04:30 | 179.05 | 172.36
2019-10-30 05:00 | 179.81 | 173.2
2019-10-30 05:30 | 181 | 174.4
2019-10-30 06:00 | 181.93 | 175.48
2019-10-30 06:30 | 184.94 | 178.15
2019-10-30 07:00 | 186.75 | 179.78
2019-10-30 07:30 | 187.82 | 180.77
2019-10-30 08:00 | 186.48 | 179.94
2019-10-30 08:30 | 185.52 | 178.67
2019-10-30 09:00 | 184.5 | 177.52
2019-10-30 09:30 | 184.29 | 176.91
2019-10-30 10:00 | 184.35 | 177.01
2019-10-30 10:30 | 183.32 | 175.88
2019-10-30 11:00 | 182.88 | 175.46
2019-10-30 11:30 | 182.63 | 175.65
2019-10-30 12:00 | 182.62 | 175.89
2019-10-30 12:30 | 181.08 | 175.21
2019-10-30 13:00 | 181.19 | 175.67
2019-10-30 13:30 | 181.84 | 176.56
2019-10-30 14:00 | 181.03 | 175.9
2019-10-30 14:30 | 182.19 | 177.05
2019-10-30 15:00 | 181.93 | 176.7
2019-10-30 15:30 | 169.17 | 163.66
2019-10-30 16:00 | 181.97 | 176.4
2019-10-30 16:30 | 183.62 | 177.89
2019-10-30 17:00 | 177.92 | 172.8
2019-10-30 17:30 | 170.12 | 165.46
2019-10-30 18:00 | 169.05 | 164.24
2019-10-30 18:30 | 168.6 | 163.59
2019-10-30 19:00 | 168.15 | 163.23
2019-10-30 19:30 | 168.58 | 163.78
2019-10-30 20:00 | 169.51 | 164.86
2019-10-30 20:30 | 168.92 | 164.32
2019-10-30 21:00 | 163.18 | 158.74
2019-10-30 21:30 | 163.34 | 158.98
2019-10-30 22:00 | 163.95 | 159.71
2019-10-30 22:30 | 165.11 | 160.88
2019-10-30 23:00 | 165.95 | 161.77
2019-10-30 23:30 | 169.45 | 163.39
2019-10-31 | 170.78 | 164
2019-10-31 00:30 | 170 | 163.36
2019-10-31 01:00 | 169.15 | 162.52
2019-10-31 01:30 | 168.79 | 162.02
2019-10-31 02:00 | 168.57 | 161.82
2019-10-31 02:30 | 168.27 | 161.54
2019-10-31 03:00 | 168.43 | 161.61
2019-10-31 03:30 | 168.12 | 161.44
2019-10-31 04:00 | 168.11 | 161.5
2019-10-31 04:30 | 168.34 | 161.69
2019-10-31 05:00 | 168.34 | 161.8
2019-10-31 05:30 | 169.6 | 163.26
2019-10-31 06:00 | 171.17 | 164.76
2019-10-31 06:30 | 173.56 | 167.18
2019-10-31 07:00 | 174.39 | 167.98
2019-10-31 07:30 | 174.79 | 168.48
2019-10-31 08:00 | 173.94 | 167.39
2019-10-31 08:30 | 173.75 | 167.17
2019-10-31 09:00 | 174.04 | 167.28
2019-10-31 09:30 | 172.88 | 165.77
2019-10-31 10:00 | 171.99 | 164.92
2019-10-31 10:30 | 171.29 | 164.24
2019-10-31 11:00 | 171.43 | 164.5
2019-10-31 11:30 | 171.72 | 164.85
2019-10-31 12:00 | 172.56 | 165.56
2019-10-31 12:30 | 171.71 | 164.6
2019-10-31 13:00 | 172.72 | 165.43
2019-10-31 13:30 | 173.26 | 166.17
2019-10-31 14:00 | 173.09 | 166.27
2019-10-31 14:30 | 174.2 | 167.29
2019-10-31 15:00 | 175.27 | 168.47
2019-10-31 15:30 | 176.04 | 169.24
2019-10-31 16:00 | 176.98 | 170.21
2019-10-31 16:30 | 178.48 | 171.45
2019-10-31 17:00 | 180.96 | 173.87
2019-10-31 17:30 | 181.17 | 174.49
2019-10-31 18:00 | 181.57 | 174.97
2019-10-31 18:30 | 182.19 | 175.58
2019-10-31 19:00 | 184.18 | 177.62
2019-10-31 19:30 | 184.05 | 177.46
2019-10-31 20:00 | 182.37 | 175.87
2019-10-31 20:30 | 181.12 | 174.4
2019-10-31 21:00 | 180.01 | 173.2
2019-10-31 21:30 | 178.94 | 172.19
2019-10-31 22:00 | 177.4 | 170.49
2019-10-31 22:30 | 175.28 | 168.34
2019-10-31 23:00 | 173.99 | 166.83
2019-10-31 23:30 | 173.23 | 166.29
2019-11-01 | 171.46 | 164.89
2019-11-01 00:30 | 170.47 | 164.11
2019-11-01 01:00 | 169.62 | 163.2
2019-11-01 01:30 | 168.98 | 162.5
2019-11-01 02:00 | 168.79 | 162.04
2019-11-01 02:30 | 168.92 | 161.93
2019-11-01 03:00 | 168.7 | 161.68
2019-11-01 03:30 | 168.74 | 161.7
2019-11-01 04:00 | 168.79 | 161.8
2019-11-01 04:30 | 169.09 | 162.02
2019-11-01 05:00 | 169.86 | 162.69
2019-11-01 05:30 | 171.06 | 163.78
2019-11-01 06:00 | 172.13 | 165
2019-11-01 06:30 | 173.23 | 166.41
2019-11-01 07:00 | 174.52 | 167.7
2019-11-01 07:30 | 173.37 | 167.07
2019-11-01 08:00 | 172.79 | 166.46
2019-11-01 08:30 | 171.64 | 165.14
2019-11-01 09:00 | 170.81 | 164.24
2019-11-01 09:30 | 169.75 | 162.91
2019-11-01 10:00 | 170.7 | 163.74
2019-11-01 10:30 | 170.52 | 163.41
2019-11-01 11:00 | 170.57 | 163.58
2019-11-01 11:30 | 170.53 | 163.79
2019-11-01 12:00 | 171.42 | 164.72
2019-11-01 12:30 | 172.21 | 165.44
2019-11-01 13:00 | 173.71 | 166.83
2019-11-01 13:30 | 173.96 | 167.16
2019-11-01 14:00 | 174.97 | 167.94
2019-11-01 14:30 | 174.09 | 166.35
2019-11-01 15:00 | 185.5 | 177.89
2019-11-01 15:30 | 186.62 | 178.84
2019-11-01 16:00 | 174.92 | 168.17
2019-11-01 16:30 | 170.16 | 163.37
2019-11-01 17:00 | 169.49 | 162.93
2019-11-01 17:30 | 169.68 | 163.18
2019-11-01 18:00 | 169.36 | 162.6
2019-11-01 18:30 | 169.19 | 162.32
2019-11-01 19:00 | 168.78 | 161.86
2019-11-01 19:30 | 169.03 | 162.13
2019-11-01 20:00 | 169.98 | 163.08
2019-11-01 20:30 | 170.41 | 164.24
2019-11-01 21:00 | 184.82 | 179.03
2019-11-01 21:30 | 188.79 | 182.99
2019-11-01 22:00 | 187.22 | 181.5
2019-11-01 22:30 | 185.68 | 180.15
2019-11-01 23:00 | 184.81 | 179.01
2019-11-01 23:30 | 184.33 | 178.54
2019-11-02 | 183.54 | 177.23
2019-11-02 00:30 | 181.79 | 176.07
2019-11-02 01:00 | 180.97 | 175.23
2019-11-02 01:30 | 180.63 | 174.67
2019-11-02 02:00 | 183.12 | 173.96
2019-11-02 02:30 | 186.78 | 174.01
2019-11-02 03:00 | 187.19 | 173.94
2019-11-02 03:30 | 187.36 | 173.86
2019-11-02 04:00 | 187.03 | 173.79
2019-11-02 04:30 | 187.07 | 173.69
2019-11-02 05:00 | 187.62 | 173.89
2019-11-02 05:30 | 187.49 | 173.9
2019-11-02 06:00 | 188.03 | 174.44
2019-11-02 06:30 | 187.42 | 174.79
2019-11-02 07:00 | 186.04 | 174.65
2019-11-02 07:30 | 185.96 | 174.12
2019-11-02 08:00 | 186.12 | 173.14
2019-11-02 08:30 | 185.24 | 172
2019-11-02 09:00 | 185.02 | 171.75
2019-11-02 09:30 | 184.51 | 170.95
2019-11-02 10:00 | 184.37 | 170.59
2019-11-02 10:30 | 182.98 | 169.57
2019-11-02 11:00 | 182.85 | 169.81
2019-11-02 11:30 | 183.98 | 170.52
2019-11-02 12:00 | 185 | 171.42
2019-11-02 12:30 | 185.43 | 172.05
2019-11-02 13:00 | 187.02 | 173.1
2019-11-02 13:30 | 187.58 | 173.92
2019-11-02 14:00 | 188.55 | 174.77
2019-11-02 14:30 | 190.28 | 176.13
2019-11-02 15:00 | 190.75 | 177.02
2019-11-02 15:30 | 192.46 | 178.61
2019-11-02 16:00 | 193.82 | 180.03
2019-11-02 16:30 | 196.11 | 182.51
2019-11-02 17:00 | 197.71 | 183.97
2019-11-02 17:30 | 199.81 | 186.06
2019-11-02 18:00 | 200.48 | 187.08
2019-11-02 18:30 | 199.81 | 187.17
2019-11-02 19:00 | 200.2 | 187.16
2019-11-02 19:30 | 200.89 | 187.77
2019-11-02 20:00 | 199.84 | 186.36
2019-11-02 20:30 | 198.74 | 185.16
2019-11-02 21:00 | 197.28 | 183.77
2019-11-02 21:30 | 195.24 | 183.17
2019-11-02 22:00 | 193.36 | 181.83
2019-11-02 22:30 | 191 | 180.2
2019-11-02 23:00 | 189.32 | 178.71
2019-11-02 23:30 | 189.14 | 177.81
2019-11-03 | 188.33 | 176.64
2019-11-03 00:30 | 188 | 175.84
2019-11-03 01:00 | 187.61 | 175.4
2019-11-03 01:30 | 187.16 | 174.68
2019-11-03 02:00 | 186.91 | 174.11
2019-11-03 02:30 | 186.59 | 173.68
2019-11-03 03:00 | 186.09 | 173.19
2019-11-03 03:30 | 185.78 | 173.06
2019-11-03 04:00 | 185.3 | 172.94
2019-11-03 04:30 | 185.79 | 173.32
2019-11-03 05:00 | 185.59 | 173.02
2019-11-03 05:30 | 186.1 | 173.38
2019-11-03 06:00 | 186.15 | 173.53
2019-11-03 06:30 | 185.34 | 173.74
2019-11-03 07:00 | 185.02 | 173.79
2019-11-03 07:30 | 184.36 | 173.13
2019-11-03 08:00 | 185.26 | 172.48
2019-11-03 08:30 | 185.86 | 172.13
2019-11-03 09:00 | 184.87 | 171.43
2019-11-03 09:30 | 185.21 | 171.09
2019-11-03 10:00 | 184.81 | 171.18
2019-11-03 10:30 | 183.85 | 170.49
2019-11-03 11:00 | 183.52 | 170.61
2019-11-03 11:30 | 184.27 | 171.06
2019-11-03 12:00 | 185.64 | 172.49
2019-11-03 12:30 | 186.71 | 173.88
2019-11-03 13:00 | 188.65 | 175.95
2019-11-03 13:30 | 189.9 | 177.33
2019-11-03 14:00 | 192.01 | 179.51
2019-11-03 14:30 | 192.48 | 180.07
2019-11-03 15:00 | 192.73 | 180.08
2019-11-03 15:30 | 193.51 | 180.8
2019-11-03 16:00 | 193.84 | 181
2019-11-03 16:30 | 195.28 | 182.67
2019-11-03 17:00 | 197.55 | 184.01
2019-11-03 17:30 | 199.33 | 185.11
2019-11-03 18:00 | 200.24 | 185.8
2019-11-03 18:30 | 196.5 | 183.76
2019-11-03 19:00 | 172.65 | 160.77
2019-11-03 19:30 | 172.77 | 161.03
2019-11-03 20:00 | 173.68 | 162.34
2019-11-03 20:30 | 173.53 | 163.37
2019-11-03 21:00 | 174.5 | 165.17
2019-11-03 21:30 | 175.18 | 165.55
2019-11-03 22:00 | 184.64 | 173.49
2019-11-03 22:30 | 187.12 | 175.59
2019-11-03 23:00 | 185.35 | 174.12
2019-11-03 23:30 | 185.86 | 173.63
2019-11-04 | 184.68 | 172.47
2019-11-04 00:30 | 184.74 | 172.16
2019-11-04 01:00 | 184.24 | 171.49
2019-11-04 01:30 | 184.37 | 171
2019-11-04 02:00 | 184.28 | 170.78
2019-11-04 02:30 | 183.97 | 170.26
2019-11-04 03:00 | 184.01 | 170.36
2019-11-04 03:30 | 183.85 | 170.3
2019-11-04 04:00 | 183.74 | 170.24
2019-11-04 04:30 | 184 | 170.54
2019-11-04 05:00 | 184.46 | 171.13
2019-11-04 05:30 | 184.84 | 172.28
2019-11-04 06:00 | 186.94 | 173.07
2019-11-04 06:30 | 188.95 | 175.04
2019-11-04 07:00 | 190.27 | 175.79
2019-11-04 07:30 | 189.99 | 176.3
2019-11-04 08:00 | 190.17 | 176.03
2019-11-04 08:30 | 189.27 | 175.6
2019-11-04 09:00 | 187.78 | 173.88
2019-11-04 09:30 | 186.49 | 172.39
2019-11-04 10:00 | 184.86 | 171.09
2019-11-04 10:30 | 184.14 | 170.35
2019-11-04 11:00 | 184.82 | 170.6
2019-11-04 11:30 | 185.77 | 171.18
2019-11-04 12:00 | 186.64 | 171.92
2019-11-04 12:30 | 187.27 | 172.49
2019-11-04 13:00 | 188.77 | 174.03
2019-11-04 13:30 | 190.7 | 176.05
2019-11-04 14:00 | 190.39 | 175.8
2019-11-04 14:30 | 192.01 | 177.52
2019-11-04 15:00 | 192.32 | 177.56
2019-11-04 15:30 | 191.87 | 178.96
2019-11-04 16:00 | 192.26 | 180.3
2019-11-04 16:30 | 193.24 | 181.52
2019-11-04 17:00 | 194.37 | 182.79
2019-11-04 17:30 | 195.57 | 184.04
2019-11-04 18:00 | 197 | 185.55
2019-11-04 18:30 | 197.8 | 186.26
2019-11-04 19:00 | 199.07 | 187.74
2019-11-04 19:30 | 199.61 | 188.07
2019-11-04 20:00 | 198.29 | 186.48
2019-11-04 20:30 | 196.86 | 184.69
2019-11-04 21:00 | 193.77 | 181.89
2019-11-04 21:30 | 192.06 | 180.91
2019-11-04 22:00 | 190.24 | 179.04
2019-11-04 22:30 | 188.33 | 177.09
2019-11-04 23:00 | 187.64 | 176.22
2019-11-04 23:30 | 188.23 | 176.54
2019-11-05 | 187.22 | 175.57
2019-11-05 00:30 | 187.61 | 174.66
2019-11-05 01:00 | 185.78 | 174.33
2019-11-05 01:30 | 185.34 | 173.65
2019-11-05 02:00 | 185.48 | 173.23
2019-11-05 02:30 | 185.95 | 173.34
2019-11-05 03:00 | 185.65 | 173.15
2019-11-05 03:30 | 185.71 | 173.12
2019-11-05 04:00 | 186 | 173.42
2019-11-05 04:30 | 186.09 | 173.6
2019-11-05 05:00 | 188.27 | 174.27
2019-11-05 05:30 | 189.69 | 175.42
2019-11-05 06:00 | 191.88 | 176.63
2019-11-05 06:30 | 193.02 | 178.6
2019-11-05 07:00 | 193.84 | 179.25
2019-11-05 07:30 | 192.98 | 178.7
2019-11-05 08:00 | 191.1 | 177.46
2019-11-05 08:30 | 166.32 | 151.72
2019-11-05 09:00 | 161.03 | 145.74
2019-11-05 09:30 | 160.87 | 145.27
2019-11-05 10:00 | 158.91 | 145.05
2019-11-05 10:30 | 160.06 | 145.26
2019-11-05 11:00 | 161.68 | 145.88
2019-11-05 11:30 | 162.35 | 146.01
2019-11-05 12:00 | 162.12 | 146.12
2019-11-05 12:30 | 162.08 | 146.23
2019-11-05 13:00 | 162.68 | 146.51
2019-11-05 13:30 | 163.17 | 147.29
2019-11-05 14:00 | 163.33 | 147.81
2019-11-05 14:30 | 162.48 | 147.31
2019-11-05 15:00 | 162.1 | 147.7
2019-11-05 15:30 | 162.13 | 147.72
2019-11-05 16:00 | 180.6 | 166.51
2019-11-05 16:30 | 192.48 | 178.48
2019-11-05 17:00 | 194.64 | 180.92
2019-11-05 17:30 | 196.73 | 182.86
2019-11-05 18:00 | 199.01 | 185.17
2019-11-05 18:30 | 200.76 | 186.77
2019-11-05 19:00 | 202.25 | 188.74
2019-11-05 19:30 | 202.67 | 189.11
2019-11-05 20:00 | 201.54 | 187.5
2019-11-05 20:30 | 200.94 | 186.46
2019-11-05 21:00 | 199.12 | 184.27
2019-11-05 21:30 | 198.28 | 184.13
2019-11-05 22:00 | 197.14 | 182.62
2019-11-05 22:30 | 196.01 | 181.27
2019-11-05 23:00 | 193.75 | 179.29
2019-11-05 23:30 | 192.43 | 177.97
2019-11-06 | 189.62 | 174.89
2019-11-06 00:30 | 187.76 | 174.39
2019-11-06 01:00 | 186.61 | 173.66
2019-11-06 01:30 | 185.71 | 173.23
2019-11-06 02:00 | 184.57 | 172.92
2019-11-06 02:30 | 184.59 | 173.1
2019-11-06 03:00 | 184.09 | 172.65
2019-11-06 03:30 | 184.55 | 173.11
2019-11-06 04:00 | 184.64 | 173.04
2019-11-06 04:30 | 185.3 | 173.69
2019-11-06 05:00 | 186.42 | 174.92
2019-11-06 05:30 | 187.18 | 176.13
2019-11-06 06:00 | 187.8 | 177.09
2019-11-06 06:30 | 187.82 | 177.69
2019-11-06 07:00 | 189.8 | 177.91
2019-11-06 07:30 | 192.16 | 178.98
2019-11-06 08:00 | 191.78 | 178.86
2019-11-06 08:30 | 172.42 | 161.79
2019-11-06 09:00 | 188.78 | 184.02
2019-11-06 09:30 | 189.16 | 184.77
2019-11-06 10:00 | 189.48 | 184.95
2019-11-06 10:30 | 192.07 | 187.48
2019-11-06 11:00 | 192.35 | 187.79
2019-11-06 11:30 | 192.44 | 187.93
2019-11-06 12:00 | 193.16 | 188.71
2019-11-06 12:30 | 193.41 | 188.88
2019-11-06 13:00 | 195.42 | 190.56
2019-11-06 13:30 | 197.92 | 193.05
2019-11-06 14:00 | 199.28 | 194.5
2019-11-06 14:30 | 200.61 | 195.75
2019-11-06 15:00 | 202.11 | 197.33
2019-11-06 15:30 | 203.23 | 198.6
2019-11-06 16:00 | 204.97 | 200.45
2019-11-06 16:30 | 207.15 | 202.61
2019-11-06 17:00 | 209 | 204.52
2019-11-06 17:30 | 210.4 | 206.01
2019-11-06 18:00 | 211.68 | 207.39
2019-11-06 18:30 | 212.98 | 208.53
2019-11-06 19:00 | 214.32 | 209.78
2019-11-06 19:30 | 213.84 | 209.33
2019-11-06 20:00 | 211.96 | 207.42
2019-11-06 20:30 | 209.86 | 205.3
2019-11-06 21:00 | 207.64 | 202.99
2019-11-06 21:30 | 206.3 | 201.57
2019-11-06 22:00 | 204.41 | 199.62
2019-11-06 22:30 | 201.87 | 196.93
2019-11-06 23:00 | 200.52 | 195.41
2019-11-06 23:30 | 200.11 | 194.99
2019-11-07 | 198.92 | 193.76
2019-11-07 00:30 | 198.07 | 192.84
2019-11-07 01:00 | 196.96 | 191.59
2019-11-07 01:30 | 196.71 | 191.25
2019-11-07 02:00 | 195.86 | 190.38
2019-11-07 02:30 | 194.82 | 189.34
2019-11-07 03:00 | 194.1 | 188.63
2019-11-07 03:30 | 194.1 | 188.59
2019-11-07 04:00 | 194.47 | 188.83
2019-11-07 04:30 | 195.02 | 189.39
2019-11-07 05:00 | 195.87 | 190.32
2019-11-07 05:30 | 197.53 | 191.92
2019-11-07 06:00 | 189.4 | 184.17
2019-11-07 06:30 | 167.74 | 162.48
2019-11-07 07:00 | 182.32 | 175.76
2019-11-07 07:30 | 184.24 | 178
2019-11-07 08:00 | 183.62 | 177.5
2019-11-07 08:30 | 182.44 | 176.43
2019-11-07 09:00 | 181.44 | 175.25
2019-11-07 09:30 | 181.24 | 174.39
2019-11-07 10:00 | 180.99 | 174.38
2019-11-07 10:30 | 181.32 | 174.69
2019-11-07 11:00 | 182.99 | 175.72
2019-11-07 11:30 | 183.81 | 176.3
2019-11-07 12:00 | 184.77 | 177.31
2019-11-07 12:30 | 185.41 | 178.32
2019-11-07 13:00 | 187.11 | 179.7
2019-11-07 13:30 | 188.84 | 181.8
2019-11-07 14:00 | 190.53 | 183.25
2019-11-07 14:30 | 191.73 | 184.67
2019-11-07 15:00 | 192.84 | 185.46
2019-11-07 15:30 | 194 | 186.76
2019-11-07 16:00 | 196.59 | 189.16
2019-11-07 16:30 | 198.84 | 191.61
2019-11-07 17:00 | 200.62 | 193.26
2019-11-07 17:30 | 203 | 195.36
2019-11-07 18:00 | 205.34 | 197.72
2019-11-07 18:30 | 205.13 | 198.35
2019-11-07 19:00 | 206.06 | 199.36
2019-11-07 19:30 | 205.4 | 198.55
2019-11-07 20:00 | 202.99 | 195.95
2019-11-07 20:30 | 200.64 | 193.49
2019-11-07 21:00 | 197.92 | 190.65
2019-11-07 21:30 | 195.35 | 188.63
2019-11-07 22:00 | 193.19 | 186.25
2019-11-07 22:30 | 190.19 | 183.08
2019-11-07 23:00 | 188.19 | 180.98
2019-11-07 23:30 | 187.33 | 180.1
2019-11-08 | 184.81 | 177.82
2019-11-08 00:30 | 183.87 | 177.36
2019-11-08 01:00 | 182.97 | 176.3
2019-11-08 01:30 | 182.19 | 175.68
2019-11-08 02:00 | 181.27 | 174.61
2019-11-08 02:30 | 180.75 | 174.48
2019-11-08 03:00 | 180.04 | 173.99
2019-11-08 03:30 | 179.13 | 173.06
2019-11-08 04:00 | 178.71 | 172.67
2019-11-08 04:30 | 178.95 | 172.95
2019-11-08 05:00 | 179.45 | 173.53
2019-11-08 05:30 | 180.4 | 174.62
2019-11-08 06:00 | 182.03 | 175.96
2019-11-08 06:30 | 184.71 | 177.34
2019-11-08 07:00 | 185.52 | 177.31
2019-11-08 07:30 | 185.63 | 177.49
2019-11-08 08:00 | 165.58 | 158.28
2019-11-08 08:30 | 156.42 | 148.7
2019-11-08 09:00 | 156.65 | 148.93
2019-11-08 09:30 | 156.96 | 148.81
2019-11-08 10:00 | 158.1 | 149.93
2019-11-08 10:30 | 158.94 | 150.89
2019-11-08 11:00 | 160.3 | 152.24
2019-11-08 11:30 | 161.58 | 153.6
2019-11-08 12:00 | 163.09 | 155.26
2019-11-08 12:30 | 163.82 | 155.97
2019-11-08 13:00 | 177.45 | 169.16
2019-11-08 13:30 | 187.48 | 179.49
2019-11-08 14:00 | 189.01 | 180.93
2019-11-08 14:30 | 190.29 | 181.99
2019-11-08 15:00 | 192.2 | 184.39
2019-11-08 15:30 | 194.14 | 186.75
2019-11-08 16:00 | 195.91 | 188.67
2019-11-08 16:30 | 198.13 | 190.93
2019-11-08 17:00 | 182.92 | 175.68
2019-11-08 17:30 | 167.34 | 159.99
2019-11-08 18:00 | 167.89 | 160.47
2019-11-08 18:30 | 168.08 | 160.41
2019-11-08 19:00 | 168.31 | 161.03
2019-11-08 19:30 | 167.4 | 160.58
2019-11-08 20:00 | 167.32 | 160.56
2019-11-08 20:30 | 168.72 | 162.1
2019-11-08 21:00 | 169.84 | 163.79
2019-11-08 21:30 | 186.8 | 180.99
2019-11-08 22:00 | 189.46 | 183.46
2019-11-08 22:30 | 187.7 | 181.43
2019-11-08 23:00 | 186.02 | 179.56
2019-11-08 23:30 | 185.32 | 178.86
2019-11-09 | 184.09 | 177.68
2019-11-09 00:30 | 182.98 | 176.62
2019-11-09 01:00 | 182.01 | 175.6
2019-11-09 01:30 | 157.48 | 151.03
2019-11-09 02:00 | 186.31 | 180.92
2019-11-09 02:30 | 197.81 | 192.51
2019-11-09 03:00 | 198.04 | 192.81
2019-11-09 03:30 | 197.85 | 192.69
2019-11-09 04:00 | 197.74 | 192.58
2019-11-09 04:30 | 197.4 | 192.24
2019-11-09 05:00 | 197.67 | 192.55
2019-11-09 05:30 | 198.38 | 193.19
2019-11-09 06:00 | 198.58 | 193.32
2019-11-09 06:30 | 198.43 | 193.18
2019-11-09 07:00 | 198.19 | 192.93
2019-11-09 07:30 | 197.46 | 192.23
2019-11-09 08:00 | 195.99 | 190.9
2019-11-09 08:30 | 194.5 | 189.51
2019-11-09 09:00 | 193.51 | 188.14
2019-11-09 09:30 | 191.76 | 186.68
2019-11-09 10:00 | 191.12 | 186.06
2019-11-09 10:30 | 190.5 | 185.21
2019-11-09 11:00 | 190.05 | 184.71
2019-11-09 11:30 | 189.66 | 184.34
2019-11-09 12:00 | 189.99 | 184.63
2019-11-09 12:30 | 189.91 | 184.64
2019-11-09 13:00 | 189.91 | 184.65
2019-11-09 13:30 | 190.36 | 185.1
2019-11-09 14:00 | 190.66 | 185.31
2019-11-09 14:30 | 191.64 | 186.21
2019-11-09 15:00 | 192.76 | 187.28
2019-11-09 15:30 | 194.24 | 188.72
2019-11-09 16:00 | 196.52 | 191.06
2019-11-09 16:30 | 198.81 | 193.42
2019-11-09 17:00 | 201.56 | 196.23
2019-11-09 17:30 | 204.2 | 198.87
2019-11-09 18:00 | 206.01 | 200.74
2019-11-09 18:30 | 207.3 | 202.37
2019-11-09 19:00 | 208.21 | 203.49
2019-11-09 19:30 | 208.53 | 203.84
2019-11-09 20:00 | 207.1 | 202.36
2019-11-09 20:30 | 205.17 | 200.4
2019-11-09 21:00 | 202.89 | 198.11
2019-11-09 21:30 | 202.59 | 197.65
2019-11-09 22:00 | 201.76 | 196.76
2019-11-09 22:30 | 199.8 | 194.75
2019-11-09 23:00 | 198.57 | 193.44
2019-11-09 23:30 | 198.23 | 193.15
2019-11-10 | 197.5 | 192.36
2019-11-10 00:30 | 196.87 | 191.6
2019-11-10 01:00 | 196.05 | 190.7
2019-11-10 01:30 | 195.63 | 190.33
2019-11-10 02:00 | 195.03 | 189.84
2019-11-10 02:30 | 195.15 | 189.85
2019-11-10 03:00 | 195.03 | 189.67
2019-11-10 03:30 | 194.93 | 189.55
2019-11-10 04:00 | 194.82 | 189.46
2019-11-10 04:30 | 194.97 | 189.61
2019-11-10 05:00 | 195.4 | 189.98
2019-11-10 05:30 | 195.41 | 189.99
2019-11-10 06:00 | 195.53 | 190.13
2019-11-10 06:30 | 195.2 | 189.78
2019-11-10 07:00 | 194.74 | 189.36
2019-11-10 07:30 | 193.93 | 188.62
2019-11-10 08:00 | 193.04 | 187.78
2019-11-10 08:30 | 192.13 | 186.97
2019-11-10 09:00 | 191.06 | 186
2019-11-10 09:30 | 190.8 | 185.61
2019-11-10 10:00 | 190.15 | 184.85
2019-11-10 10:30 | 190.92 | 185.53
2019-11-10 11:00 | 189.58 | 184.31
2019-11-10 11:30 | 189.69 | 184.45
2019-11-10 12:00 | 190.61 | 185.4
2019-11-10 12:30 | 191.14 | 185.89
2019-11-10 13:00 | 191.8 | 186.61
2019-11-10 13:30 | 192.07 | 186.86
2019-11-10 14:00 | 192.79 | 187.56
2019-11-10 14:30 | 194.36 | 189.14
2019-11-10 15:00 | 195.66 | 190.51
2019-11-10 15:30 | 197.74 | 192.59
2019-11-10 16:00 | 200.64 | 195.45
2019-11-10 16:30 | 202.73 | 197.75
2019-11-10 17:00 | 205.61 | 200.65
2019-11-10 17:30 | 208.12 | 203.12
2019-11-10 18:00 | 210.54 | 205.62
2019-11-10 18:30 | 211.03 | 206.2
2019-11-10 19:00 | 211.96 | 207.18
2019-11-10 19:30 | 211.89 | 207.11
2019-11-10 20:00 | 209.84 | 205.17
2019-11-10 20:30 | 207.93 | 203.21
2019-11-10 21:00 | 206.09 | 201.29
2019-11-10 21:30 | 205.37 | 200.52
2019-11-10 22:00 | 203.51 | 198.55
2019-11-10 22:30 | 201.22 | 196.21
2019-11-10 23:00 | 199.78 | 194.65
2019-11-10 23:30 | 199.07 | 193.94
2019-11-11 | 197.72 | 192.67
2019-11-11 00:30 | 197.74 | 192.47
2019-11-11 01:00 | 196.78 | 191.49
2019-11-11 01:30 | 196.16 | 190.84
2019-11-11 02:00 | 195.52 | 190.19
2019-11-11 02:30 | 195.27 | 189.94
2019-11-11 03:00 | 194.88 | 189.57
2019-11-11 03:30 | 194.58 | 189.22
2019-11-11 04:00 | 194.74 | 189.4
2019-11-11 04:30 | 195.03 | 189.7
2019-11-11 05:00 | 195.61 | 190.31
2019-11-11 05:30 | 196.69 | 191.4
2019-11-11 06:00 | 197.57 | 192.65
2019-11-11 06:30 | 198.4 | 193.72
2019-11-11 07:00 | 198.77 | 194.1
2019-11-11 07:30 | 199.28 | 194.76
2019-11-11 08:00 | 198.45 | 193.94
2019-11-11 08:30 | 197.73 | 193.22
2019-11-11 09:00 | 196.42 | 191.93
2019-11-11 09:30 | 195.06 | 190.57
2019-11-11 10:00 | 195.41 | 190.85
2019-11-11 10:30 | 195.95 | 191.5
2019-11-11 11:00 | 196.22 | 191.78
2019-11-11 11:30 | 196.65 | 192.26
2019-11-11 12:00 | 197.85 | 193.51
2019-11-11 12:30 | 198.71 | 194.33
2019-11-11 13:00 | 200.3 | 195.83
2019-11-11 13:30 | 202.1 | 197.7
2019-11-11 14:00 | 203.7 | 199.34
2019-11-11 14:30 | 205.42 | 201.08
2019-11-11 15:00 | 206.36 | 202.01
2019-11-11 15:30 | 208.23 | 203.88
2019-11-11 16:00 | 210.81 | 206.51
2019-11-11 16:30 | 212.79 | 208.47
2019-11-11 17:00 | 215.09 | 210.82
2019-11-11 17:30 | 216.92 | 212.65
2019-11-11 18:00 | 218.62 | 214.43
2019-11-11 18:30 | 218.79 | 214.61
2019-11-11 19:00 | 219.48 | 215.33
2019-11-11 19:30 | 218.39 | 214.27
2019-11-11 20:00 | 215.33 | 211.2
2019-11-11 20:30 | 212.41 | 208.16
2019-11-11 21:00 | 209.24 | 204.93
2019-11-11 21:30 | 207.47 | 203.15
2019-11-11 22:00 | 205.11 | 200.73
2019-11-11 22:30 | 202.72 | 198.22
2019-11-11 23:00 | 200.23 | 195.64
2019-11-11 23:30 | 199.84 | 194.98
2019-11-12 | 198.56 | 193.88
2019-11-12 00:30 | 197.92 | 193.26
2019-11-12 01:00 | 196.71 | 191.94
2019-11-12 01:30 | 196.1 | 191.29
2019-11-12 02:00 | 195.16 | 190.3
2019-11-12 02:30 | 194.83 | 189.94
2019-11-12 03:00 | 194.28 | 189.34
2019-11-12 03:30 | 194.14 | 189.15
2019-11-12 04:00 | 194.14 | 189.19
2019-11-12 04:30 | 194.32 | 189.36
2019-11-12 05:00 | 195.02 | 190.01
2019-11-12 05:30 | 196.07 | 191.04
2019-11-12 06:00 | 196.98 | 192.02
2019-11-12 06:30 | 198.34 | 193.47
2019-11-12 07:00 | 198.79 | 194.02
2019-11-12 07:30 | 199.02 | 194.34
2019-11-12 08:00 | 197.97 | 193.34
2019-11-12 08:30 | 197.12 | 192.53
2019-11-12 09:00 | 196.57 | 192.14
2019-11-12 09:30 | 196.68 | 192.33
2019-11-12 10:00 | 198.18 | 193.79
2019-11-12 10:30 | 199.14 | 194.86
2019-11-12 11:00 | 200.63 | 196.32
2019-11-12 11:30 | 202.32 | 198.04
2019-11-12 12:00 | 204.34 | 200.3
2019-11-12 12:30 | 205.79 | 201.77
2019-11-12 13:00 | 208.54 | 204.4
2019-11-12 13:30 | 210.49 | 206.45
2019-11-12 14:00 | 214.8 | 210.75
2019-11-12 14:30 | 200.17 | 196.56
2019-11-12 15:00 | 182.62 | 178.12
2019-11-12 15:30 | 187.89 | 182.72
2019-11-12 16:00 | 199.56 | 194.27
2019-11-12 16:30 | 201.94 | 196.37
2019-11-12 17:00 | 204.72 | 199.25
2019-11-12 17:30 | 206.91 | 201.44
2019-11-12 18:00 | 187.65 | 182.41
2019-11-12 18:30 | 177.52 | 172.27
2019-11-12 19:00 | 177.65 | 172.51
2019-11-12 19:30 | 175.94 | 170.97
2019-11-12 20:00 | 172.73 | 167.63
2019-11-12 20:30 | 197.06 | 191.79
2019-11-12 21:00 | 198.01 | 193.02
2019-11-12 21:30 | 194.99 | 190.2
2019-11-12 22:00 | 191.87 | 187.04
2019-11-12 22:30 | 188.98 | 184.11
2019-11-12 23:00 | 186.8 | 181.87
2019-11-12 23:30 | 185.66 | 180.72
2019-11-13 | 183.83 | 179
2019-11-13 00:30 | 182.62 | 177.92
2019-11-13 01:00 | 181.63 | 176.99
2019-11-13 01:30 | 181.35 | 176.62
2019-11-13 02:00 | 181.14 | 176.31
2019-11-13 02:30 | 180.63 | 175.65
2019-11-13 03:00 | 180.23 | 175.08
2019-11-13 03:30 | 180.47 | 175.24
2019-11-13 04:00 | 180.13 | 174.87
2019-11-13 04:30 | 180.56 | 175.35
2019-11-13 05:00 | 181 | 175.86
2019-11-13 05:30 | 182.03 | 176.98
2019-11-13 06:00 | 182.79 | 178.1
2019-11-13 06:30 | 184.75 | 179.46
2019-11-13 07:00 | 185.92 | 179.77
2019-11-13 07:30 | 171.07 | 164.98
2019-11-13 08:00 | 190.8 | 186.54
2019-11-13 08:30 | 197.65 | 193.59
2019-11-13 09:00 | 195.31 | 191.37
2019-11-13 09:30 | 193.82 | 189.76
2019-11-13 10:00 | 193.97 | 189.86
2019-11-13 10:30 | 194.36 | 190.21
2019-11-13 11:00 | 195.29 | 191.01
2019-11-13 11:30 | 195.68 | 191.54
2019-11-13 12:00 | 196.14 | 192
2019-11-13 12:30 | 196.76 | 192.6
2019-11-13 13:00 | 197.96 | 193.77
2019-11-13 13:30 | 199.2 | 195.1
2019-11-13 14:00 | 200 | 196.03
2019-11-13 14:30 | 200.1 | 196.25
2019-11-13 15:00 | 201.88 | 197.87
2019-11-13 15:30 | 201.57 | 197.54
2019-11-13 16:00 | 208.34 | 204.22
2019-11-13 16:30 | 212.29 | 208.2
2019-11-13 17:00 | 189.66 | 185.1
2019-11-13 17:30 | 185.3 | 180.35
2019-11-13 18:00 | 179.42 | 174.15
2019-11-13 18:30 | 190.27 | 184.19
2019-11-13 19:00 | 201.54 | 195.47
2019-11-13 19:30 | 201.85 | 195.73
2019-11-13 20:00 | 200.08 | 193.98
2019-11-13 20:30 | 198.11 | 191.72
2019-11-13 21:00 | 196.16 | 189.78
2019-11-13 21:30 | 194.65 | 188.68
2019-11-13 22:00 | 192.58 | 186.74
2019-11-13 22:30 | 190.38 | 184.35
2019-11-13 23:00 | 188.18 | 182.52
2019-11-13 23:30 | 186.59 | 181.91
2019-11-14 | 185.78 | 180.45
2019-11-14 00:30 | 184.9 | 179.84
2019-11-14 01:00 | 183.83 | 178.73
2019-11-14 01:30 | 170.86 | 166.03
2019-11-14 02:00 | 196.15 | 191.19
2019-11-14 02:30 | 195.77 | 190.78
2019-11-14 03:00 | 195.67 | 190.58
2019-11-14 03:30 | 195.24 | 190.12
2019-11-14 04:00 | 195.19 | 190.05
2019-11-14 04:30 | 195.38 | 190.25
2019-11-14 05:00 | 195.95 | 190.82
2019-11-14 05:30 | 196.69 | 191.73
2019-11-14 06:00 | 197.05 | 192.06
2019-11-14 06:30 | 196.6 | 191.99
2019-11-14 07:00 | 196.64 | 192.13
2019-11-14 07:30 | 197.19 | 192.57
2019-11-14 08:00 | 195.18 | 190.63
2019-11-14 08:30 | 193.94 | 189.34
2019-11-14 09:00 | 192.62 | 188.15
2019-11-14 09:30 | 191.98 | 187.46
2019-11-14 10:00 | 192.25 | 187.72
2019-11-14 10:30 | 192.06 | 187.62
2019-11-14 11:00 | 192.11 | 187.74
2019-11-14 11:30 | 189.92 | 185.77
2019-11-14 12:00 | 190.3 | 186.29
2019-11-14 12:30 | 184.26 | 180.76
2019-11-14 13:00 | 180.15 | 177.02
2019-11-14 13:30 | 187.34 | 183.95
2019-11-14 14:00 | 194.04 | 190.28
2019-11-14 14:30 | 197.86 | 193.95
2019-11-14 15:00 | 200.76 | 196.78
2019-11-14 15:30 | 204.08 | 200.01
2019-11-14 16:00 | 206 | 202.01
2019-11-14 16:30 | 186.4 | 181.6
2019-11-14 17:00 | 182.37 | 175.88
2019-11-14 17:30 | 195.24 | 188.57
2019-11-14 18:00 | 197.36 | 191.3
2019-11-14 18:30 | 198.26 | 192.51
2019-11-14 19:00 | 198.93 | 193.24
2019-11-14 19:30 | 199.36 | 193.6
2019-11-14 20:00 | 197.94 | 192
2019-11-14 20:30 | 195.65 | 189.47
2019-11-14 21:00 | 193.33 | 187.06
2019-11-14 21:30 | 191.04 | 185.33
2019-11-14 22:00 | 189.08 | 183.42
2019-11-14 22:30 | 186.76 | 180.96
2019-11-14 23:00 | 159.01 | 153.2
2019-11-14 23:30 | 182.77 | 177.85
2019-11-15 | 198.23 | 193.31
2019-11-15 00:30 | 197.75 | 192.82
2019-11-15 01:00 | 196.68 | 191.69
2019-11-15 01:30 | 195.85 | 190.88
2019-11-15 02:00 | 195.75 | 190.79
2019-11-15 02:30 | 195.43 | 190.35
2019-11-15 03:00 | 194.68 | 189.49
2019-11-15 03:30 | 194.76 | 189.66
2019-11-15 04:00 | 195.19 | 190.12
2019-11-15 04:30 | 195.46 | 190.39
2019-11-15 05:00 | 196.18 | 191.12
2019-11-15 05:30 | 196.99 | 192
2019-11-15 06:00 | 197.59 | 192.59
2019-11-15 06:30 | 198.21 | 193.45
2019-11-15 07:00 | 198.22 | 193.56
2019-11-15 07:30 | 198.21 | 193.76
2019-11-15 08:00 | 197.01 | 192.63
2019-11-15 08:30 | 196.39 | 191.95
2019-11-15 09:00 | 195.32 | 190.89
2019-11-15 09:30 | 195.46 | 191.12
2019-11-15 10:00 | 196.01 | 191.76
2019-11-15 10:30 | 197.17 | 192.82
2019-11-15 11:00 | 198.47 | 194.13
2019-11-15 11:30 | 199.38 | 195.08
2019-11-15 12:00 | 200.59 | 196.35
2019-11-15 12:30 | 202.64 | 198.29
2019-11-15 13:00 | 179.98 | 175.17
2019-11-15 13:30 | 175.93 | 169.71
2019-11-15 14:00 | 185.69 | 179.33
2019-11-15 14:30 | 187.34 | 181.08
2019-11-15 15:00 | 189.2 | 183.05
2019-11-15 15:30 | 191.01 | 184.94
2019-11-15 16:00 | 194.52 | 188.66
2019-11-15 16:30 | 198.33 | 192.57
2019-11-15 17:00 | 200.07 | 194.46
2019-11-15 17:30 | 200.25 | 195.15
2019-11-15 18:00 | 201.19 | 196.06
2019-11-15 18:30 | 201.78 | 196.39
2019-11-15 19:00 | 201.82 | 196.36
2019-11-15 19:30 | 202.75 | 196.98
2019-11-15 20:00 | 201.01 | 195.01
2019-11-15 20:30 | 198.78 | 192.54
2019-11-15 21:00 | 196.24 | 189.91
2019-11-15 21:30 | 194.73 | 188.79
2019-11-15 22:00 | 192.73 | 186.62
2019-11-15 22:30 | 189.29 | 182.66
2019-11-15 23:00 | 186.51 | 179.55
2019-11-15 23:30 | 185.14 | 178.12
2019-11-16 | 184.13 | 177.52
2019-11-16 00:30 | 182.41 | 176.2
2019-11-16 01:00 | 181.51 | 175.53
2019-11-16 01:30 | 180.14 | 174.61
2019-11-16 02:00 | 158.21 | 152.88
2019-11-16 02:30 | 180.97 | 176.44
2019-11-16 03:00 | 197.64 | 192.73
2019-11-16 03:30 | 197.87 | 192.94
2019-11-16 04:00 | 197.62 | 192.67
2019-11-16 04:30 | 197.5 | 192.52
2019-11-16 05:00 | 197.48 | 192.5
2019-11-16 05:30 | 197.57 | 192.58
2019-11-16 06:00 | 197.23 | 192.28
2019-11-16 06:30 | 198.08 | 193.24
2019-11-16 07:00 | 197.93 | 193.28
2019-11-16 07:30 | 198.44 | 193.84
2019-11-16 08:00 | 198.83 | 193.91
2019-11-16 08:30 | 200.39 | 194.25
2019-11-16 09:00 | 199.32 | 193.23
2019-11-16 09:30 | 172.92 | 165.88
2019-11-16 10:00 | 173.23 | 165.54
2019-11-16 10:30 | 183.07 | 174.96
2019-11-16 11:00 | 184.47 | 176.25
2019-11-16 11:30 | 185.62 | 177.12
2019-11-16 12:00 | 186.92 | 178.62
2019-11-16 12:30 | 188.21 | 180.12
2019-11-16 13:00 | 189.23 | 181.52
2019-11-16 13:30 | 190.01 | 182.45
2019-11-16 14:00 | 190.66 | 183.38
2019-11-16 14:30 | 191.66 | 184.34
2019-11-16 15:00 | 187.7 | 180.89
2019-11-16 15:30 | 166.13 | 159.91
2019-11-16 16:00 | 167.89 | 161.62
2019-11-16 16:30 | 169.51 | 163.25
2019-11-16 17:00 | 171.27 | 165.27
2019-11-16 17:30 | 172.83 | 166.83
2019-11-16 18:00 | 173.52 | 167.54
2019-11-16 18:30 | 172.83 | 167.44
2019-11-16 19:00 | 171.69 | 166.57
2019-11-16 19:30 | 169.88 | 164.67
2019-11-16 20:00 | 167.51 | 162.22
2019-11-16 20:30 | 165.91 | 160.76
2019-11-16 21:00 | 165.32 | 160.34
2019-11-16 21:30 | 166.65 | 161.96
2019-11-16 22:00 | 168.34 | 163.63
2019-11-16 22:30 | 183.2 | 177.61
2019-11-16 23:00 | 188.61 | 182.4
2019-11-16 23:30 | 188.11 | 181.89
2019-11-17 | 187.12 | 180.79
2019-11-17 00:30 | 186.68 | 180
2019-11-17 01:00 | 185.69 | 179.11
2019-11-17 01:30 | 183.98 | 177.14
2019-11-17 02:00 | 183.78 | 176.91
2019-11-17 02:30 | 183.21 | 176.17
2019-11-17 03:00 | 182.48 | 175.34
2019-11-17 03:30 | 182.24 | 175.06
2019-11-17 04:00 | 181.78 | 174.56
2019-11-17 04:30 | 181.56 | 174.25
2019-11-17 05:00 | 181.88 | 174.5
2019-11-17 05:30 | 181.88 | 174.45
2019-11-17 06:00 | 181.97 | 174.59
2019-11-17 06:30 | 181.63 | 174.64
2019-11-17 07:00 | 164.58 | 157.84
2019-11-17 07:30 | 186.17 | 179.96
2019-11-17 08:00 | 198.45 | 192.12
2019-11-17 08:30 | 198.2 | 192.07
2019-11-17 09:00 | 198.28 | 192.22
2019-11-17 09:30 | 198.39 | 192.35
2019-11-17 10:00 | 197.05 | 191.5
2019-11-17 10:30 | 197.45 | 192.17
2019-11-17 11:00 | 198.71 | 193.34
2019-11-17 11:30 | 200.33 | 195.07
2019-11-17 12:00 | 204.31 | 198.86
2019-11-17 12:30 | 207.75 | 202.32
2019-11-17 13:00 | 209.57 | 204.21
2019-11-17 13:30 | 209.97 | 204.76
2019-11-17 14:00 | 212.57 | 207.45
2019-11-17 14:30 | 188.08 | 182.73
2019-11-17 15:00 | 184.64 | 178.04
2019-11-17 15:30 | 193.16 | 186.63
2019-11-17 16:00 | 195.69 | 189.72
2019-11-17 16:30 | 199.33 | 194.14
2019-11-17 17:00 | 204.36 | 199.83
2019-11-17 17:30 | 205.19 | 200.61
2019-11-17 18:00 | 207.87 | 203.76
2019-11-17 18:30 | 190.69 | 187.51
2019-11-17 19:00 | 178.12 | 174.59
2019-11-17 19:30 | 172.21 | 167.73
2019-11-17 20:00 | 167.12 | 162.14
2019-11-17 20:30 | 166.62 | 161.49
2019-11-17 21:00 | 191.84 | 185.08
2019-11-17 21:30 | 192.48 | 185.4
2019-11-17 22:00 | 184.28 | 176.59
2019-11-17 22:30 | 182.02 | 174.01
2019-11-17 23:00 | 179.58 | 171.46
2019-11-17 23:30 | 178.7 | 170.47
2019-11-18 | 177.96 | 169.8
2019-11-18 00:30 | 176.99 | 168.97
2019-11-18 01:00 | 175.88 | 167.96
2019-11-18 01:30 | 175.13 | 167.02
2019-11-18 02:00 | 174.74 | 166.56
2019-11-18 02:30 | 174.19 | 165.92
2019-11-18 03:00 | 173.42 | 165.03
2019-11-18 03:30 | 173.31 | 164.88
2019-11-18 04:00 | 173.15 | 164.74
2019-11-18 04:30 | 172.19 | 163.86
2019-11-18 05:00 | 172.29 | 164.03
2019-11-18 05:30 | 172.77 | 164.59
2019-11-18 06:00 | 173.08 | 165.23
2019-11-18 06:30 | 174.96 | 166.98
2019-11-18 07:00 | 176.42 | 168.01
2019-11-18 07:30 | 176.66 | 168.35
2019-11-18 08:00 | 175.65 | 167.18
2019-11-18 08:30 | 189.18 | 182.52
2019-11-18 09:00 | 201.52 | 195.48
2019-11-18 09:30 | 201.57 | 195.55
2019-11-18 10:00 | 202.38 | 196.37
2019-11-18 10:30 | 203.06 | 197.16
2019-11-18 11:00 | 203.58 | 197.76
2019-11-18 11:30 | 204.19 | 198.5
2019-11-18 12:00 | 206.08 | 200.49
2019-11-18 12:30 | 207.02 | 201.48
2019-11-18 13:00 | 208.89 | 203.33
2019-11-18 13:30 | 211.33 | 205.94
2019-11-18 14:00 | 212.78 | 207.59
2019-11-18 14:30 | 214.37 | 209.33
2019-11-18 15:00 | 215.58 | 210.67
2019-11-18 15:30 | 216.92 | 212.04
2019-11-18 16:00 | 192.77 | 186.47
2019-11-18 16:30 | 189.84 | 183.4
2019-11-18 17:00 | 188.26 | 181.72
2019-11-18 17:30 | 195.37 | 188.97
2019-11-18 18:00 | 183.91 | 177.78
2019-11-18 18:30 | 165.68 | 160.12
2019-11-18 19:00 | 165.64 | 160.86
2019-11-18 19:30 | 166.22 | 161.44
2019-11-18 20:00 | 163.15 | 158.04
2019-11-18 20:30 | 161.16 | 155.59
2019-11-18 21:00 | 163.32 | 157.72
2019-11-18 21:30 | 164.86 | 159.44
2019-11-18 22:00 | 179.96 | 173.19
2019-11-18 22:30 | 185 | 177.6
2019-11-18 23:00 | 183.09 | 175.31
2019-11-18 23:30 | 181.97 | 174.38
2019-11-19 | 178.16 | 170.56
2019-11-19 00:30 | 180.19 | 171.76
2019-11-19 01:00 | 179.35 | 170.42
2019-11-19 01:30 | 178.31 | 169.8
2019-11-19 02:00 | 177.78 | 168.9
2019-11-19 02:30 | 178.08 | 169.05
2019-11-19 03:00 | 178.65 | 169.74
2019-11-19 03:30 | 178.93 | 169.95
2019-11-19 04:00 | 178.89 | 170.16
2019-11-19 04:30 | 157.66 | 149.15
2019-11-19 05:00 | 181.16 | 174.5
2019-11-19 05:30 | 200.08 | 193.43
2019-11-19 06:00 | 199.25 | 192.97
2019-11-19 06:30 | 200.18 | 194.42
2019-11-19 07:00 | 200.64 | 195.05
2019-11-19 07:30 | 201.61 | 196.23
2019-11-19 08:00 | 201.99 | 196.6
2019-11-19 08:30 | 201.63 | 196.32
2019-11-19 09:00 | 200.61 | 196.32
2019-11-19 09:30 | 200.42 | 196.56
2019-11-19 10:00 | 202.03 | 197.91
2019-11-19 10:30 | 203.01 | 198.98
2019-11-19 11:00 | 204.24 | 200.26
2019-11-19 11:30 | 205.4 | 201.45
2019-11-19 12:00 | 207.12 | 203.22
2019-11-19 12:30 | 210.21 | 206.14
2019-11-19 13:00 | 188.04 | 183.44
2019-11-19 13:30 | 181.27 | 175.56
2019-11-19 14:00 | 191.3 | 185.93
2019-11-19 14:30 | 193.36 | 188.12
2019-11-19 15:00 | 194.28 | 189.29
2019-11-19 15:30 | 195.85 | 190.72
2019-11-19 16:00 | 198.73 | 193.58
2019-11-19 16:30 | 200.58 | 195.26
2019-11-19 17:00 | 203.72 | 198.2
2019-11-19 17:30 | 205.66 | 199.88
2019-11-19 18:00 | 207.06 | 201.26
2019-11-19 18:30 | 208.9 | 202.91
2019-11-19 19:00 | 209.67 | 203.59
2019-11-19 19:30 | 208.72 | 203.06
2019-11-19 20:00 | 205.27 | 200.14
2019-11-19 20:30 | 200.92 | 195.45
2019-11-19 21:00 | 197.12 | 191.55
2019-11-19 21:30 | 193.93 | 188.66
2019-11-19 22:00 | 190.93 | 185.72
2019-11-19 22:30 | 187.84 | 182.44
2019-11-19 23:00 | 186.09 | 180.68
2019-11-19 23:30 | 185.32 | 179.91
2019-11-20 | 182.22 | 176.76
2019-11-20 00:30 | 181.12 | 175.69
2019-11-20 01:00 | 180.34 | 174.47
2019-11-20 01:30 | 179.66 | 173.75
2019-11-20 02:00 | 178.85 | 172.73
2019-11-20 02:30 | 178.44 | 172.28
2019-11-20 03:00 | 177.64 | 171.46
2019-11-20 03:30 | 177.77 | 171.58
2019-11-20 04:00 | 177.65 | 171.45
2019-11-20 04:30 | 178.12 | 171.95
2019-11-20 05:00 | 178.4 | 172.26
2019-11-20 05:30 | 179.14 | 173.15
2019-11-20 06:00 | 179.63 | 173.79
2019-11-20 06:30 | 181.67 | 175.93
2019-11-20 07:00 | 182.28 | 176.62
2019-11-20 07:30 | 183.25 | 177.5
2019-11-20 08:00 | 183.03 | 177.33
2019-11-20 08:30 | 182.91 | 177.36
2019-11-20 09:00 | 183.52 | 178.1
2019-11-20 09:30 | 184.47 | 178.82
2019-11-20 10:00 | 186.67 | 180.94
2019-11-20 10:30 | 188.01 | 182.38
2019-11-20 11:00 | 189.6 | 184.06
2019-11-20 11:30 | 191.51 | 185.91
2019-11-20 12:00 | 193.2 | 187.63
2019-11-20 12:30 | 194.69 | 188.95
2019-11-20 13:00 | 196.31 | 190.48
2019-11-20 13:30 | 198.61 | 192.91
2019-11-20 14:00 | 200.4 | 194.87
2019-11-20 14:30 | 201.67 | 196.37
2019-11-20 15:00 | 203.22 | 198.06
2019-11-20 15:30 | 204.66 | 199.57
2019-11-20 16:00 | 207.35 | 202.44
2019-11-20 16:30 | 202.93 | 198.21
2019-11-20 17:00 | 178.97 | 174.61
2019-11-20 17:30 | 181.75 | 177.38
2019-11-20 18:00 | 183.43 | 179.13
2019-11-20 18:30 | 184.06 | 179.74
2019-11-20 19:00 | 183.54 | 179.24
2019-11-20 19:30 | 182.94 | 178.59
2019-11-20 20:00 | 202.7 | 197.74
2019-11-20 20:30 | 210.01 | 204.46
2019-11-20 21:00 | 205.66 | 199.63
2019-11-20 21:30 | 201.32 | 195.23
2019-11-20 22:00 | 197.81 | 191.28
2019-11-20 22:30 | 194.55 | 187.69
2019-11-20 23:00 | 191.92 | 184.93
2019-11-20 23:30 | 189.69 | 182.85
2019-11-21 | 187.79 | 180.79
2019-11-21 00:30 | 186.9 | 179.96
2019-11-21 01:00 | 185.98 | 179.07
2019-11-21 01:30 | 185.63 | 178.67
2019-11-21 02:00 | 184.72 | 177.61
2019-11-21 02:30 | 184.82 | 177.66
2019-11-21 03:00 | 184.8 | 177.61
2019-11-21 03:30 | 184.75 | 177.55
2019-11-21 04:00 | 184.91 | 177.73
2019-11-21 04:30 | 184.95 | 177.8
2019-11-21 05:00 | 185.59 | 178.56
2019-11-21 05:30 | 186.58 | 179.62
2019-11-21 06:00 | 187.47 | 180.82
2019-11-21 06:30 | 188.94 | 182.72
2019-11-21 07:00 | 189.83 | 183.47
2019-11-21 07:30 | 191.22 | 185.15
2019-11-21 08:00 | 190.77 | 184.94
2019-11-21 08:30 | 189.93 | 184.28
2019-11-21 09:00 | 190.19 | 184.7
2019-11-21 09:30 | 190.32 | 184.84
2019-11-21 10:00 | 191.3 | 185.83
2019-11-21 10:30 | 192.58 | 187.49
2019-11-21 11:00 | 193.41 | 188.35
2019-11-21 11:30 | 194.72 | 189.8
2019-11-21 12:00 | 196.41 | 191.52
2019-11-21 12:30 | 198.91 | 193.42
2019-11-21 13:00 | 201.59 | 195.95
2019-11-21 13:30 | 203.47 | 197.99
2019-11-21 14:00 | 205.57 | 200.27
2019-11-21 14:30 | 206.69 | 201.28
2019-11-21 15:00 | 207.66 | 202.54
2019-11-21 15:30 | 208.63 | 203.57
2019-11-21 16:00 | 210.35 | 205.36
2019-11-21 16:30 | 211.69 | 206.66
2019-11-21 17:00 | 213.55 | 208.49
2019-11-21 17:30 | 215.14 | 209.83
2019-11-21 18:00 | 216.2 | 210.86
2019-11-21 18:30 | 216.91 | 211.37
2019-11-21 19:00 | 217.34 | 211.89
2019-11-21 19:30 | 217.74 | 212.14
2019-11-21 20:00 | 215.37 | 209.6
2019-11-21 20:30 | 212.37 | 206.4
2019-11-21 21:00 | 207.8 | 202.73
2019-11-21 21:30 | 204.49 | 199.38
2019-11-21 22:00 | 200.94 | 196.08
2019-11-21 22:30 | 197.46 | 192.56
2019-11-21 23:00 | 194.72 | 189.96
2019-11-21 23:30 | 193.58 | 188.61
2019-11-22 | 191.52 | 186.31
2019-11-22 00:30 | 190.47 | 185.28
2019-11-22 01:00 | 188.68 | 184.06
2019-11-22 01:30 | 187.82 | 183.2
2019-11-22 02:00 | 186.88 | 182.13
2019-11-22 02:30 | 186.2 | 181.42
2019-11-22 03:00 | 185.35 | 180.63
2019-11-22 03:30 | 185.52 | 180.09
2019-11-22 04:00 | 185 | 179.48
2019-11-22 04:30 | 185.13 | 179.51
2019-11-22 05:00 | 185.52 | 179.94
2019-11-22 05:30 | 186.09 | 180.7
2019-11-22 06:00 | 186.56 | 181.37
2019-11-22 06:30 | 188.01 | 183.27
2019-11-22 07:00 | 189.08 | 184.06
2019-11-22 07:30 | 188.79 | 183.76
2019-11-22 08:00 | 187.49 | 182.8
2019-11-22 08:30 | 185.78 | 181.52
2019-11-22 09:00 | 185.66 | 181.55
2019-11-22 09:30 | 185.53 | 181.01
2019-11-22 10:00 | 187.26 | 182.76
2019-11-22 10:30 | 188.35 | 183.98
2019-11-22 11:00 | 188.55 | 184.3
2019-11-22 11:30 | 188.79 | 184.36
2019-11-22 12:00 | 189.94 | 185.35
2019-11-22 12:30 | 191.35 | 186.92
2019-11-22 13:00 | 194.36 | 190.13
2019-11-22 13:30 | 198.35 | 194.45
2019-11-22 14:00 | 199.79 | 195.93
2019-11-22 14:30 | 201.66 | 197.21
2019-11-22 15:00 | 200.54 | 195.92
2019-11-22 15:30 | 201.36 | 196.78
2019-11-22 16:00 | 203.52 | 199.05
2019-11-22 16:30 | 205.04 | 200.67
2019-11-22 17:00 | 206.39 | 201.55
2019-11-22 17:30 | 207.03 | 201.34
2019-11-22 18:00 | 207.08 | 201
2019-11-22 18:30 | 206.51 | 201.18
2019-11-22 19:00 | 205.7 | 200.79
2019-11-22 19:30 | 205.55 | 200.61
2019-11-22 20:00 | 204.19 | 199.13
2019-11-22 20:30 | 202.1 | 196.97
2019-11-22 21:00 | 200.12 | 194.66
2019-11-22 21:30 | 197.99 | 192.34
2019-11-22 22:00 | 195.69 | 190.14
2019-11-22 22:30 | 192.5 | 187.27
2019-11-22 23:00 | 190.5 | 185.57
2019-11-22 23:30 | 189.54 | 184.56
2019-11-23 | 187.71 | 182.95
2019-11-23 00:30 | 186.91 | 182.24
2019-11-23 01:00 | 185.71 | 180.95
2019-11-23 01:30 | 185.02 | 180.37
2019-11-23 02:00 | 184.11 | 179.42
2019-11-23 02:30 | 183.99 | 179.24
2019-11-23 03:00 | 183.61 | 178.83
2019-11-23 03:30 | 183.21 | 178.39
2019-11-23 04:00 | 182.92 | 178.08
2019-11-23 04:30 | 182.84 | 178.05
2019-11-23 05:00 | 182.73 | 177.9
2019-11-23 05:30 | 182.95 | 178.06
2019-11-23 06:00 | 182.29 | 177.45
2019-11-23 06:30 | 182.22 | 177.64
2019-11-23 07:00 | 183.27 | 178.23
2019-11-23 07:30 | 183.86 | 179.16
2019-11-23 08:00 | 182.98 | 178.08
2019-11-23 08:30 | 183.95 | 177.61
2019-11-23 09:00 | 184.57 | 177.45
2019-11-23 09:30 | 184.51 | 177.36
2019-11-23 10:00 | 183.1 | 177.34
2019-11-23 10:30 | 183.27 | 177.71
2019-11-23 11:00 | 183.94 | 178.39
2019-11-23 11:30 | 185.59 | 179.91
2019-11-23 12:00 | 187.7 | 182.12
2019-11-23 12:30 | 189.22 | 183.66
2019-11-23 13:00 | 190.72 | 185.18
2019-11-23 13:30 | 191.86 | 186.32
2019-11-23 14:00 | 193 | 187.6
2019-11-23 14:30 | 194.07 | 188.87
2019-11-23 15:00 | 196.79 | 191.69
2019-11-23 15:30 | 196.99 | 191.88
2019-11-23 16:00 | 198.72 | 193.19
2019-11-23 16:30 | 199.85 | 194.24
2019-11-23 17:00 | 200.39 | 194.73
2019-11-23 17:30 | 199.43 | 193.61
2019-11-23 18:00 | 199.22 | 193.23
2019-11-23 18:30 | 199.53 | 193.44
2019-11-23 19:00 | 199.42 | 193.32
2019-11-23 19:30 | 199.11 | 192.93
2019-11-23 20:00 | 197.83 | 191.35
2019-11-23 20:30 | 175.64 | 168.87
2019-11-23 21:00 | 168.74 | 161.83
2019-11-23 21:30 | 167.77 | 160.82
2019-11-23 22:00 | 164.66 | 158.75
2019-11-23 22:30 | 162.92 | 157.01
2019-11-23 23:00 | 160.96 | 155.5
2019-11-23 23:30 | 159.79 | 154.66
2019-11-24 | 158.68 | 153.52
2019-11-24 00:30 | 158.15 | 153.01
2019-11-24 01:00 | 156.96 | 151.74
2019-11-24 01:30 | 154.95 | 149.71
2019-11-24 02:00 | 153.7 | 148.44
2019-11-24 02:30 | 153.14 | 147.84
2019-11-24 03:00 | 152.93 | 147.6
2019-11-24 03:30 | 152.51 | 147.17
2019-11-24 04:00 | 151.47 | 146.07
2019-11-24 04:30 | 151.87 | 146.52
2019-11-24 05:00 | 151.51 | 146.14
2019-11-24 05:30 | 151.61 | 146.23
2019-11-24 06:00 | 153.07 | 147.78
2019-11-24 06:30 | 152.79 | 147.5
2019-11-24 07:00 | 152.52 | 147.31
2019-11-24 07:30 | 153.4 | 147.67
2019-11-24 08:00 | 154.51 | 148.87
2019-11-24 08:30 | 154.75 | 149.09
2019-11-24 09:00 | 155.11 | 148.89
2019-11-24 09:30 | 154.97 | 148.63
2019-11-24 10:00 | 155.99 | 149.74
2019-11-24 10:30 | 156.47 | 150.06
2019-11-24 11:00 | 157.39 | 150.87
2019-11-24 11:30 | 158.47 | 152.12
2019-11-24 12:00 | 159.35 | 153.02
2019-11-24 12:30 | 161.28 | 155.08
2019-11-24 13:00 | 161.78 | 155.77
2019-11-24 13:30 | 163.44 | 157.62
2019-11-24 14:00 | 165.89 | 160.21
2019-11-24 14:30 | 167.47 | 161.72
2019-11-24 15:00 | 167.69 | 162.04
2019-11-24 15:30 | 171.25 | 165.73
2019-11-24 16:00 | 188.64 | 183.1
2019-11-24 16:30 | 190.45 | 184.76
2019-11-24 17:00 | 190.91 | 185.08
2019-11-24 17:30 | 191.62 | 185.79
2019-11-24 18:00 | 192.57 | 186.67
2019-11-24 18:30 | 193.05 | 187.05
2019-11-24 19:00 | 193.27 | 187.23
2019-11-24 19:30 | 193.25 | 187.15
2019-11-24 20:00 | 190.7 | 184.8
2019-11-24 20:30 | 188.73 | 182.5
2019-11-24 21:00 | 186.56 | 180.06
2019-11-24 21:30 | 184.78 | 178.12
2019-11-24 22:00 | 182.39 | 175.91
2019-11-24 22:30 | 180.07 | 173.6
2019-11-24 23:00 | 178.36 | 171.92
2019-11-24 23:30 | 177.21 | 170.87
2019-11-25 | 176.06 | 169.66
2019-11-25 00:30 | 175.1 | 168.76
2019-11-25 01:00 | 174.41 | 167.93
2019-11-25 01:30 | 173.54 | 167.12
2019-11-25 02:00 | 173.1 | 166.85
2019-11-25 02:30 | 172.36 | 166.37
2019-11-25 03:00 | 171.86 | 165.86
2019-11-25 03:30 | 171.42 | 165.42
2019-11-25 04:00 | 171.68 | 165.69
2019-11-25 04:30 | 172.04 | 166.08
2019-11-25 05:00 | 172.64 | 166.73
2019-11-25 05:30 | 173.41 | 167.53
2019-11-25 06:00 | 174.19 | 168.55
2019-11-25 06:30 | 175.45 | 169.99
2019-11-25 07:00 | 176.84 | 171.17
2019-11-25 07:30 | 177.71 | 172.02
2019-11-25 08:00 | 177.08 | 171.56
2019-11-25 08:30 | 176.02 | 170.39
2019-11-25 09:00 | 175.91 | 170.42
2019-11-25 09:30 | 174.99 | 169.75
2019-11-25 10:00 | 175.71 | 170.38
2019-11-25 10:30 | 176.42 | 171.44
2019-11-25 11:00 | 177.25 | 172.33
2019-11-25 11:30 | 177.77 | 173.13
2019-11-25 12:00 | 179.4 | 174.86
2019-11-25 12:30 | 181.03 | 176.54
2019-11-25 13:00 | 183.49 | 178.87
2019-11-25 13:30 | 186.02 | 181.63
2019-11-25 14:00 | 187.85 | 183.68
2019-11-25 14:30 | 190.54 | 186.65
2019-11-25 15:00 | 192.25 | 188.22
2019-11-25 15:30 | 193.65 | 189.34
2019-11-25 16:00 | 193.05 | 187.84
2019-11-25 16:30 | 199 | 192.25
2019-11-25 17:00 | 197.24 | 189.82
2019-11-25 17:30 | 198.53 | 191.2
2019-11-25 18:00 | 201.75 | 194.62
2019-11-25 18:30 | 199.87 | 192.63
2019-11-25 19:00 | 171.13 | 164.66
2019-11-25 19:30 | 171.66 | 165.13
2019-11-25 20:00 | 172.92 | 166.52
2019-11-25 20:30 | 173.56 | 167.22
2019-11-25 21:00 | 174.81 | 168.35
2019-11-25 21:30 | 149.17 | 142.94
2019-11-25 22:00 | 159.01 | 151.33
2019-11-25 22:30 | 160.16 | 152.05
2019-11-25 23:00 | 158.33 | 150.21
2019-11-25 23:30 | 157.12 | 149.14
2019-11-26 | 155.27 | 147.8
2019-11-26 00:30 | 154.81 | 147.41
2019-11-26 01:00 | 154.45 | 147.13
2019-11-26 01:30 | 153.22 | 146.02
2019-11-26 02:00 | 152.4 | 145.1
2019-11-26 02:30 | 152.1 | 144.83
2019-11-26 03:00 | 151.48 | 144.3
2019-11-26 03:30 | 151.06 | 143.93
2019-11-26 04:00 | 151.03 | 143.89
2019-11-26 04:30 | 151.15 | 144.07
2019-11-26 05:00 | 151.51 | 144.99
2019-11-26 05:30 | 153.27 | 145.5
2019-11-26 06:00 | 154.71 | 147.31
2019-11-26 06:30 | 157.41 | 150.08
2019-11-26 07:00 | 158.6 | 150.97
2019-11-26 07:30 | 159.95 | 152.19
2019-11-26 08:00 | 159.36 | 151.1
2019-11-26 08:30 | 158.99 | 150.66
2019-11-26 09:00 | 158.38 | 149.77
2019-11-26 09:30 | 159.66 | 150.83
2019-11-26 10:00 | 160.79 | 151.85
2019-11-26 10:30 | 161.96 | 153.52
2019-11-26 11:00 | 162.76 | 154.48
2019-11-26 11:30 | 164.35 | 156.42
2019-11-26 12:00 | 166.35 | 158.49
2019-11-26 12:30 | 169.37 | 161.13
2019-11-26 13:00 | 170.05 | 161.75
2019-11-26 13:30 | 171.72 | 163.9
2019-11-26 14:00 | 192.03 | 184.64
2019-11-26 14:30 | 201.19 | 194.1
2019-11-26 15:00 | 202.28 | 195.01
2019-11-26 15:30 | 205.46 | 198.09
2019-11-26 16:00 | 204.63 | 197.12
2019-11-26 16:30 | 205.38 | 197.74
2019-11-26 17:00 | 206.21 | 198.64
2019-11-26 17:30 | 207.09 | 199.32
2019-11-26 18:00 | 208.21 | 200.37
2019-11-26 18:30 | 208.12 | 200.09
2019-11-26 19:00 | 188.25 | 181.08
2019-11-26 19:30 | 172.1 | 164.51
2019-11-26 20:00 | 170.22 | 162.6
2019-11-26 20:30 | 165.72 | 158.96
2019-11-26 21:00 | 163.85 | 157.06
2019-11-26 21:30 | 189.88 | 182.27
2019-11-26 22:00 | 192.75 | 185.26
2019-11-26 22:30 | 190.22 | 182.41
2019-11-26 23:00 | 188.21 | 179.99
2019-11-26 23:30 | 187.03 | 179.07
2019-11-27 | 185.75 | 178
2019-11-27 00:30 | 185.14 | 177.49
2019-11-27 01:00 | 184.43 | 176.76
2019-11-27 01:30 | 182.98 | 175.54
2019-11-27 02:00 | 182.47 | 174.94
2019-11-27 02:30 | 181.67 | 174.46
2019-11-27 03:00 | 181.18 | 173.96
2019-11-27 03:30 | 181.02 | 173.78
2019-11-27 04:00 | 180.93 | 173.69
2019-11-27 04:30 | 180.97 | 173.76
2019-11-27 05:00 | 181.35 | 174.31
2019-11-27 05:30 | 181.9 | 174.97
2019-11-27 06:00 | 184.18 | 176.33
2019-11-27 06:30 | 186.3 | 178.1
2019-11-27 07:00 | 187.11 | 178.77
2019-11-27 07:30 | 187.8 | 179.37
2019-11-27 08:00 | 187.24 | 178.51
2019-11-27 08:30 | 171.15 | 162.86
2019-11-27 09:00 | 188.86 | 183.27
2019-11-27 09:30 | 198.53 | 193.94
2019-11-27 10:00 | 197.87 | 193.27
2019-11-27 10:30 | 198.68 | 194.1
2019-11-27 11:00 | 200.02 | 195.4
2019-11-27 11:30 | 201.85 | 197.26
2019-11-27 12:00 | 203.5 | 198.98
2019-11-27 12:30 | 204.76 | 200.25
2019-11-27 13:00 | 206.45 | 201.83
2019-11-27 13:30 | 208.84 | 204.32
2019-11-27 14:00 | 210.66 | 206.42
2019-11-27 14:30 | 212.69 | 208.55
2019-11-27 15:00 | 214.04 | 209.88
2019-11-27 15:30 | 216.19 | 212.07
2019-11-27 16:00 | 213.86 | 209.46
2019-11-27 16:30 | 187.19 | 180.91
2019-11-27 17:00 | 194.37 | 187.37
2019-11-27 17:30 | 204.2 | 197.04
2019-11-27 18:00 | 206.39 | 199.08
2019-11-27 18:30 | 207.61 | 200.11
2019-11-27 19:00 | 208.26 | 200.69
2019-11-27 19:30 | 208.31 | 200.67
2019-11-27 20:00 | 205.93 | 198.18
2019-11-27 20:30 | 202.67 | 194.47
2019-11-27 21:00 | 200.11 | 191.79
2019-11-27 21:30 | 198.04 | 190
2019-11-27 22:00 | 195.01 | 187.01
2019-11-27 22:30 | 192.15 | 184.21
2019-11-27 23:00 | 190.1 | 182.01
2019-11-27 23:30 | 189.25 | 181.19
2019-11-28 | 187.16 | 179.33
2019-11-28 00:30 | 183.71 | 176.08
2019-11-28 01:00 | 169.93 | 162.77
2019-11-28 01:30 | 188.55 | 183.21
2019-11-28 02:00 | 199.3 | 194.56
2019-11-28 02:30 | 198.61 | 193.72
2019-11-28 03:00 | 198.49 | 193.49
2019-11-28 03:30 | 197.91 | 192.85
2019-11-28 04:00 | 197.93 | 192.85
2019-11-28 04:30 | 198.29 | 193.19
2019-11-28 05:00 | 199.25 | 194.29
2019-11-28 05:30 | 199.98 | 195.03
2019-11-28 06:00 | 200.43 | 195.56
2019-11-28 06:30 | 202.38 | 197.63
2019-11-28 07:00 | 203.16 | 198.49
2019-11-28 07:30 | 203.57 | 199.16
2019-11-28 08:00 | 202.9 | 198.56
2019-11-28 08:30 | 202.64 | 198.28
2019-11-28 09:00 | 202.81 | 198.47
2019-11-28 09:30 | 202.74 | 198.49
2019-11-28 10:00 | 203.92 | 199.7
2019-11-28 10:30 | 205.25 | 201.12
2019-11-28 11:00 | 207.06 | 202.88
2019-11-28 11:30 | 208.96 | 204.78
2019-11-28 12:00 | 211.44 | 207.31
2019-11-28 12:30 | 214.02 | 209.9
2019-11-28 13:00 | 208.56 | 203.15
2019-11-28 13:30 | 189.4 | 180.73
2019-11-28 14:00 | 201.58 | 193.13
2019-11-28 14:30 | 204.05 | 195.87
2019-11-28 15:00 | 204.59 | 196.19
2019-11-28 15:30 | 206.29 | 197.96
2019-11-28 16:00 | 209.43 | 201.23
2019-11-28 16:30 | 210.98 | 202.21
2019-11-28 17:00 | 212.59 | 203.73
2019-11-28 17:30 | 214.32 | 205.2
2019-11-28 18:00 | 215.58 | 206.26
2019-11-28 18:30 | 215.41 | 207.61
2019-11-28 19:00 | 215.97 | 208.21
2019-11-28 19:30 | 215.83 | 208.04
2019-11-28 20:00 | 214.3 | 206.22
2019-11-28 20:30 | 211.58 | 203.29
2019-11-28 21:00 | 207.65 | 198.99
2019-11-28 21:30 | 204.34 | 196.15
2019-11-28 22:00 | 200.59 | 192.31
2019-11-28 22:30 | 197.92 | 189.35
2019-11-28 23:00 | 195.85 | 187.07
2019-11-28 23:30 | 194.73 | 185.89
2019-11-29 | 192.83 | 184.31
2019-11-29 00:30 | 191.63 | 182.85
2019-11-29 01:00 | 168.76 | 160.36
2019-11-29 01:30 | 194.63 | 189.77
2019-11-29 02:00 | 200.65 | 196.38
2019-11-29 02:30 | 199.93 | 195.56
2019-11-29 03:00 | 199.13 | 194.76
2019-11-29 03:30 | 198.34 | 193.91
2019-11-29 04:00 | 197.23 | 192.67
2019-11-29 04:30 | 197.22 | 192.68
2019-11-29 05:00 | 197.72 | 193.23
2019-11-29 05:30 | 198.35 | 193.88
2019-11-29 06:00 | 198.89 | 194.58
2019-11-29 06:30 | 200.86 | 196.76
2019-11-29 07:00 | 201.93 | 198.1
2019-11-29 07:30 | 201.51 | 199.21
2019-11-29 08:00 | 201.37 | 199.14
2019-11-29 08:30 | 201.11 | 198.91
2019-11-29 09:00 | 200.81 | 198.67
2019-11-29 09:30 | 201.07 | 198.96
2019-11-29 10:00 | 202.74 | 200.51
2019-11-29 10:30 | 206.56 | 204.08
2019-11-29 11:00 | 208.55 | 206.02
2019-11-29 11:30 | 210.97 | 208.44
2019-11-29 12:00 | 212.68 | 210.27
2019-11-29 12:30 | 214.62 | 212.23
2019-11-29 13:00 | 200.17 | 196.64
2019-11-29 13:30 | 192.9 | 188.98
2019-11-29 14:00 | 189.9 | 185.93
2019-11-29 14:30 | 187.51 | 183.41
2019-11-29 15:00 | 194.67 | 190.73
2019-11-29 15:30 | 200.49 | 196.74
2019-11-29 16:00 | 207.05 | 202.65
2019-11-29 16:30 | 208.97 | 202.87
2019-11-29 17:00 | 208.58 | 201.36
2019-11-29 17:30 | 207.98 | 198.67
2019-11-29 18:00 | 209.58 | 200.61
2019-11-29 18:30 | 210.22 | 202.4
2019-11-29 19:00 | 210.13 | 202.77
2019-11-29 19:30 | 209.67 | 202.26
2019-11-29 20:00 | 208.79 | 201.26
2019-11-29 20:30 | 206.58 | 199
2019-11-29 21:00 | 204.93 | 197.36
2019-11-29 21:30 | 202.55 | 195.26
2019-11-29 22:00 | 200.54 | 192.96
2019-11-29 22:30 | 198.19 | 190.47
2019-11-29 23:00 | 196.57 | 189.18
2019-11-29 23:30 | 195.02 | 187.58
2019-11-30 | 193.72 | 186.16
2019-11-30 00:30 | 192.38 | 184.99
2019-11-30 01:00 | 190.44 | 183.98
2019-11-30 01:30 | 186.78 | 180
2019-11-30 02:00 | 163.94 | 157.28
2019-11-30 02:30 | 187.54 | 182.56
2019-11-30 03:00 | 198.51 | 194.3
2019-11-30 03:30 | 197.76 | 193.55
2019-11-30 04:00 | 197.51 | 193.27
2019-11-30 04:30 | 197.46 | 193.25
2019-11-30 05:00 | 197.49 | 193.28
2019-11-30 05:30 | 197.7 | 193.47
2019-11-30 06:00 | 197.56 | 193.31
2019-11-30 06:30 | 198.17 | 193.9
2019-11-30 07:00 | 198.52 | 194.22
2019-11-30 07:30 | 198.9 | 194.88
2019-11-30 08:00 | 199.37 | 195.29
2019-11-30 08:30 | 199.87 | 195.8
2019-11-30 09:00 | 200.05 | 196.08
2019-11-30 09:30 | 184.37 | 178.27
2019-11-30 10:00 | 178.24 | 171.25
2019-11-30 10:30 | 178.61 | 171.88
2019-11-30 11:00 | 180.62 | 174.1
2019-11-30 11:30 | 181.96 | 175.54
2019-11-30 12:00 | 183.64 | 177.35
2019-11-30 12:30 | 185.81 | 179.62
2019-11-30 13:00 | 188.14 | 181.93
2019-11-30 13:30 | 191.02 | 185.01
2019-11-30 14:00 | 192.64 | 186.54
2019-11-30 14:30 | 192.63 | 186.4
2019-11-30 15:00 | 192.85 | 186.66
2019-11-30 15:30 | 193.59 | 187.42
2019-11-30 16:00 | 194.5 | 188.37
2019-11-30 16:30 | 200.61 | 192.95
2019-11-30 17:00 | 209.51 | 202.21
2019-11-30 17:30 | 209.32 | 201.85
2019-11-30 18:00 | 209.49 | 202.08
2019-11-30 18:30 | 209.72 | 202.42
2019-11-30 19:00 | 208.92 | 201.58
2019-11-30 19:30 | 207.72 | 200.3
2019-11-30 20:00 | 205.38 | 197.68
2019-11-30 20:30 | 203.69 | 195.63
2019-11-30 21:00 | 201.22 | 192.86
2019-11-30 21:30 | 199.69 | 191.28
2019-11-30 22:00 | 197.98 | 189.39
2019-11-30 22:30 | 196.43 | 187.51
2019-11-30 23:00 | 194.52 | 185.79
2019-11-30 23:30 | 192.95 | 185.06
2019-12-01 | 165.22 | 157.12
2019-12-01 00:30 | 188.27 | 183.16
2019-12-01 01:00 | 196.75 | 192.59
2019-12-01 01:30 | 196.2 | 192.01
2019-12-01 02:00 | 195.67 | 191.42
2019-12-01 02:30 | 195.12 | 190.75
2019-12-01 03:00 | 194.62 | 190.16
2019-12-01 03:30 | 194.11 | 189.73
2019-12-01 04:00 | 193.93 | 189.54
2019-12-01 04:30 | 193.73 | 189.35
2019-12-01 05:00 | 193.67 | 189.38
2019-12-01 05:30 | 188.16 | 184.13
2019-12-01 06:00 | 185.73 | 180.15
2019-12-01 06:30 | 182.16 | 176.7
2019-12-01 07:00 | 174.04 | 168.87
2019-12-01 07:30 | 166.03 | 161.05
2019-12-01 08:00 | 166.22 | 161.3
2019-12-01 08:30 | 165.64 | 160.83
2019-12-01 09:00 | 166.1 | 160.95
2019-12-01 09:30 | 167.95 | 161.5
2019-12-01 10:00 | 174.65 | 167.99
2019-12-01 10:30 | 175.03 | 168.29
2019-12-01 11:00 | 175.03 | 168.21
2019-12-01 11:30 | 178.13 | 171.32
2019-12-01 12:00 | 178.36 | 171.44
2019-12-01 12:30 | 179.88 | 172.75
2019-12-01 13:00 | 180.22 | 173.17
2019-12-01 13:30 | 180.18 | 173.33
2019-12-01 14:00 | 181.99 | 175.18
2019-12-01 14:30 | 179.77 | 172.66
2019-12-01 15:00 | 180.43 | 173.09
2019-12-01 15:30 | 209.05 | 201.09
2019-12-01 16:00 | 220.73 | 212.98
2019-12-01 16:30 | 222.85 | 215.17
2019-12-01 17:00 | 224.5 | 216.4
2019-12-01 17:30 | 225.44 | 217.52
2019-12-01 18:00 | 226.38 | 218.63
2019-12-01 18:30 | 227.5 | 219.65
2019-12-01 19:00 | 228.25 | 220.5
2019-12-01 19:30 | 228.18 | 220.41
2019-12-01 20:00 | 227.2 | 219.26
2019-12-01 20:30 | 225.98 | 217.9
2019-12-01 21:00 | 224.43 | 216.08
2019-12-01 21:30 | 223.26 | 214.83
2019-12-01 22:00 | 221.8 | 213.24
2019-12-01 22:30 | 219.89 | 211.24
2019-12-01 23:00 | 217.81 | 209.93
2019-12-01 23:30 | 217.03 | 209.16
2019-12-02 | 215.77 | 207.9
2019-12-02 00:30 | 214.8 | 207.01
2019-12-02 01:00 | 213.7 | 206.07
2019-12-02 01:30 | 213.19 | 205.5
2019-12-02 02:00 | 212.65 | 205.1
2019-12-02 02:30 | 212.24 | 204.63
2019-12-02 03:00 | 212.03 | 204.17
2019-12-02 03:30 | 211.93 | 203.99
2019-12-02 04:00 | 212.1 | 204.11
2019-12-02 04:30 | 212.36 | 204.23
2019-12-02 05:00 | 213.04 | 204.97
2019-12-02 05:30 | 213.88 | 205.98
2019-12-02 06:00 | 214.43 | 206.9
2019-12-02 06:30 | 216.23 | 208.8
2019-12-02 07:00 | 217.14 | 209.63
2019-12-02 07:30 | 218.7 | 211.02
2019-12-02 08:00 | 218.95 | 210.78
2019-12-02 08:30 | 217.2 | 209.13
2019-12-02 09:00 | 215.89 | 207.71
2019-12-02 09:30 | 214.91 | 206.35
2019-12-02 10:00 | 214.49 | 205.8
2019-12-02 10:30 | 214 | 205.84
2019-12-02 11:00 | 213.73 | 205.63
2019-12-02 11:30 | 214.26 | 206.21
2019-12-02 12:00 | 215.18 | 207.04
2019-12-02 12:30 | 215.72 | 207.33
2019-12-02 13:00 | 217.61 | 209.42
2019-12-02 13:30 | 219.76 | 211.9
2019-12-02 14:00 | 221.13 | 213.23
2019-12-02 14:30 | 222.84 | 215.05
2019-12-02 15:00 | 223.51 | 215.79
2019-12-02 15:30 | 224.75 | 217.11
2019-12-02 16:00 | 226.83 | 219.16
2019-12-02 16:30 | 229.1 | 221.44
2019-12-02 17:00 | 231.61 | 223.89
2019-12-02 17:30 | 232.83 | 224.96
2019-12-02 18:00 | 234.21 | 226.25
2019-12-02 18:30 | 235.67 | 227.71
2019-12-02 19:00 | 236.69 | 228.63
2019-12-02 19:30 | 237.22 | 229.17
2019-12-02 20:00 | 236.22 | 228.06
2019-12-02 20:30 | 234.46 | 226.22
2019-12-02 21:00 | 230.9 | 223.73
2019-12-02 21:30 | 229.08 | 222.05
2019-12-02 22:00 | 227.05 | 220.04
2019-12-02 22:30 | 224.61 | 217.62
2019-12-02 23:00 | 221.65 | 214.55
2019-12-02 23:30 | 190.32 | 182.89
2019-12-03 | 164.28 | 157.97
2019-12-03 00:30 | 163.57 | 158.16
2019-12-03 01:00 | 166.05 | 160.95
2019-12-03 01:30 | 164.85 | 159.61
2019-12-03 02:00 | 164 | 158.7
2019-12-03 02:30 | 163.46 | 158.09
2019-12-03 03:00 | 163.17 | 157.72
2019-12-03 03:30 | 162.64 | 157.17
2019-12-03 04:00 | 162.74 | 157.27
2019-12-03 04:30 | 163.06 | 157.61
2019-12-03 05:00 | 163.53 | 158.12
2019-12-03 05:30 | 164.44 | 159.05
2019-12-03 06:00 | 164.89 | 159.66
2019-12-03 06:30 | 166.23 | 161.2
2019-12-03 07:00 | 166.37 | 161.4
2019-12-03 07:30 | 167.18 | 162.32
2019-12-03 08:00 | 166.3 | 161.49
2019-12-03 08:30 | 164.55 | 159.86
2019-12-03 09:00 | 163.81 | 159.18
2019-12-03 09:30 | 162.46 | 157.82
2019-12-03 10:00 | 162.3 | 157.56
2019-12-03 10:30 | 162.72 | 158.04
2019-12-03 11:00 | 162.92 | 158.24
2019-12-03 11:30 | 163.5 | 158.87
2019-12-03 12:00 | 164.49 | 159.86
2019-12-03 12:30 | 165.29 | 160.65
2019-12-03 13:00 | 166.56 | 161.86
2019-12-03 13:30 | 167.71 | 163.12
2019-12-03 14:00 | 169.45 | 164.86
2019-12-03 14:30 | 170.95 | 166.42
2019-12-03 15:00 | 172.3 | 167.72
2019-12-03 15:30 | 172.92 | 168.44
2019-12-03 16:00 | 174.57 | 170.13
2019-12-03 16:30 | 176.35 | 171.91
2019-12-03 17:00 | 178.98 | 174.55
2019-12-03 17:30 | 180.13 | 175.71
2019-12-03 18:00 | 181.78 | 177.4
2019-12-03 18:30 | 182.1 | 177.85
2019-12-03 19:00 | 181.77 | 177.61
2019-12-03 19:30 | 181.37 | 177.22
2019-12-03 20:00 | 180.45 | 176.22
2019-12-03 20:30 | 178.06 | 173.7
2019-12-03 21:00 | 175.72 | 171.17
2019-12-03 21:30 | 174.11 | 169.42
2019-12-03 22:00 | 171.74 | 166.89
2019-12-03 22:30 | 171.77 | 164.79
2019-12-03 23:00 | 169.88 | 162.43
2019-12-03 23:30 | 172.89 | 167.17
2019-12-04 | 178.85 | 173.82
2019-12-04 00:30 | 180.28 | 175.12
2019-12-04 01:00 | 178.8 | 173.72
2019-12-04 01:30 | 177.81 | 172.71
2019-12-04 02:00 | 177.58 | 172.38
2019-12-04 02:30 | 177.3 | 172.08
2019-12-04 03:00 | 177.24 | 172.03
2019-12-04 03:30 | 176.63 | 171.4
2019-12-04 04:00 | 176.62 | 171.39
2019-12-04 04:30 | 176.35 | 171.11
2019-12-04 05:00 | 176.89 | 171.62
2019-12-04 05:30 | 177.86 | 172.59
2019-12-04 06:00 | 178.74 | 173.6
2019-12-04 06:30 | 180.37 | 175.76
2019-12-04 07:00 | 180.71 | 176.13
2019-12-04 07:30 | 181.41 | 176.97
2019-12-04 08:00 | 181.02 | 176.58
2019-12-04 08:30 | 179.26 | 174.89
2019-12-04 09:00 | 177.25 | 172.81
2019-12-04 09:30 | 178.06 | 173.5
2019-12-04 10:00 | 180.09 | 175.38
2019-12-04 10:30 | 180.99 | 176.37
2019-12-04 11:00 | 182.57 | 177.93
2019-12-04 11:30 | 186.07 | 181.3
2019-12-04 12:00 | 188.3 | 183.47
2019-12-04 12:30 | 192.27 | 187
2019-12-04 13:00 | 197.45 | 192.92
2019-12-04 13:30 | 198.97 | 195.41
2019-12-04 14:00 | 200.52 | 197.11
2019-12-04 14:30 | 201.65 | 198.28
2019-12-04 15:00 | 202.73 | 199.34
2019-12-04 15:30 | 204.37 | 200.97
2019-12-04 16:00 | 200.86 | 196.5
2019-12-04 16:30 | 184.47 | 178.23
2019-12-04 17:00 | 195.2 | 188.11
2019-12-04 17:30 | 197.46 | 190.75
2019-12-04 18:00 | 191.19 | 184.99
2019-12-04 18:30 | 191.19 | 184.86
2019-12-04 19:00 | 206.33 | 199.84
2019-12-04 19:30 | 208.42 | 202
2019-12-04 20:00 | 207.4 | 200.85
2019-12-04 20:30 | 204.53 | 197.83
2019-12-04 21:00 | 201.71 | 194.69
2019-12-04 21:30 | 199.77 | 193.12
2019-12-04 22:00 | 197.24 | 190.47
2019-12-04 22:30 | 194.53 | 187.61
2019-12-04 23:00 | 192.19 | 185.12
2019-12-04 23:30 | 191.62 | 184.33
2019-12-05 | 190.22 | 182.3
2019-12-05 00:30 | 189.45 | 181.43
2019-12-05 01:00 | 188.18 | 180.27
2019-12-05 01:30 | 188.27 | 180.12
2019-12-05 02:00 | 187.67 | 179.59
2019-12-05 02:30 | 187.02 | 178.52
2019-12-05 03:00 | 187.35 | 178.75
2019-12-05 03:30 | 186.44 | 177.83
2019-12-05 04:00 | 187.03 | 178.46
2019-12-05 04:30 | 186.88 | 178.36
2019-12-05 05:00 | 187.84 | 179.31
2019-12-05 05:30 | 188.35 | 179.98
2019-12-05 06:00 | 188.06 | 180.13
2019-12-05 06:30 | 188.65 | 181.24
2019-12-05 07:00 | 190.49 | 182.16
2019-12-05 07:30 | 189.71 | 181.18
2019-12-05 08:00 | 190.41 | 181.31
2019-12-05 08:30 | 189.68 | 180.81
2019-12-05 09:00 | 189.71 | 180.86
2019-12-05 09:30 | 190.66 | 180.94
2019-12-05 10:00 | 191.79 | 181.81
2019-12-05 10:30 | 192.85 | 183.16
2019-12-05 11:00 | 193.49 | 183.65
2019-12-05 11:30 | 193.39 | 183.86
2019-12-05 12:00 | 194.88 | 185.26
2019-12-05 12:30 | 196.18 | 186.15
2019-12-05 13:00 | 198.06 | 187.79
2019-12-05 13:30 | 199.63 | 189.57
2019-12-05 14:00 | 201.13 | 191.25
2019-12-05 14:30 | 202.11 | 192.33
2019-12-05 15:00 | 203.24 | 193.4
2019-12-05 15:30 | 204.61 | 194.59
2019-12-05 16:00 | 205.83 | 196.6
2019-12-05 16:30 | 207.74 | 199.04
2019-12-05 17:00 | 194.24 | 188.38
2019-12-05 17:30 | 189.8 | 185.12
2019-12-05 18:00 | 188.65 | 184.35
2019-12-05 18:30 | 190.15 | 186.09
2019-12-05 19:00 | 192.04 | 187.83
2019-12-05 19:30 | 193.17 | 188.87
2019-12-05 20:00 | 194.75 | 190.43
2019-12-05 20:30 | 197.45 | 192.96
2019-12-05 21:00 | 200.08 | 195.5
2019-12-05 21:30 | 199.3 | 191.69
2019-12-05 22:00 | 199.53 | 190.45
2019-12-05 22:30 | 196.87 | 187.56
2019-12-05 23:00 | 194.8 | 185.2
2019-12-05 23:30 | 193.89 | 183.96
2019-12-06 | 191.53 | 181.54
2019-12-06 00:30 | 190.48 | 181.14
2019-12-06 01:00 | 189.56 | 180.32
2019-12-06 01:30 | 189.06 | 180.06
2019-12-06 02:00 | 188.36 | 179.42
2019-12-06 02:30 | 187.93 | 178.8
2019-12-06 03:00 | 187.21 | 178.64
2019-12-06 03:30 | 186.81 | 178.25
2019-12-06 04:00 | 187.34 | 178.11
2019-12-06 04:30 | 188.05 | 178.58
2019-12-06 05:00 | 188.38 | 178.77
2019-12-06 05:30 | 188.95 | 179.35
2019-12-06 06:00 | 190.36 | 181.3
2019-12-06 06:30 | 190.81 | 182.41
2019-12-06 07:00 | 191.29 | 182.47
2019-12-06 07:30 | 191.32 | 182.8
2019-12-06 08:00 | 190.78 | 182.51
2019-12-06 08:30 | 190.49 | 182.35
2019-12-06 09:00 | 190.34 | 182.31
2019-12-06 09:30 | 190.81 | 182.63
2019-12-06 10:00 | 192.89 | 184.48
2019-12-06 10:30 | 193.22 | 185.06
2019-12-06 11:00 | 193.26 | 185.25
2019-12-06 11:30 | 194.61 | 186.83
2019-12-06 12:00 | 196.5 | 188.83
2019-12-06 12:30 | 198.19 | 190.41
2019-12-06 13:00 | 199.92 | 192.17
2019-12-06 13:30 | 204.35 | 197.08
2019-12-06 14:00 | 206.55 | 199.32
2019-12-06 14:30 | 208.21 | 201.22
2019-12-06 15:00 | 209.34 | 202.61
2019-12-06 15:30 | 204.69 | 198.44
2019-12-06 16:00 | 190.81 | 187.28
2019-12-06 16:30 | 188.86 | 185.35
2019-12-06 17:00 | 187.53 | 184.14
2019-12-06 17:30 | 187.05 | 183.72
2019-12-06 18:00 | 186.61 | 183.24
2019-12-06 18:30 | 187.58 | 184.01
2019-12-06 19:00 | 189.43 | 185.62
2019-12-06 19:30 | 191.66 | 187.67
2019-12-06 20:00 | 193.21 | 189.18
2019-12-06 20:30 | 195.68 | 191.8
2019-12-06 21:00 | 197.89 | 193.96
2019-12-06 21:30 | 199.19 | 195.58
2019-12-06 22:00 | 200.67 | 197
2019-12-06 22:30 | 198.81 | 190.91
2019-12-06 23:00 | 199.73 | 189.85
2019-12-06 23:30 | 198.3 | 188.6
2019-12-07 | 196.73 | 186.67
2019-12-07 00:30 | 196.12 | 186.02
2019-12-07 01:00 | 195.39 | 185.19
2019-12-07 01:30 | 192.9 | 183.46
2019-12-07 02:00 | 190.68 | 182.54
2019-12-07 02:30 | 189.2 | 181.33
2019-12-07 03:00 | 188.31 | 180.35
2019-12-07 03:30 | 187.94 | 179.86
2019-12-07 04:00 | 188.11 | 179.93
2019-12-07 04:30 | 188.11 | 179.87
2019-12-07 05:00 | 188.24 | 179.94
2019-12-07 05:30 | 188.32 | 179.98
2019-12-07 06:00 | 187.68 | 179.26
2019-12-07 06:30 | 187.56 | 179.4
2019-12-07 07:00 | 187.08 | 179.29
2019-12-07 07:30 | 187.4 | 179.72
2019-12-07 08:00 | 187.5 | 179.72
2019-12-07 08:30 | 188.05 | 180.12
2019-12-07 09:00 | 189.18 | 181.37
2019-12-07 09:30 | 190.09 | 182.46
2019-12-07 10:00 | 191.61 | 183.93
2019-12-07 10:30 | 193.38 | 185.61
2019-12-07 11:00 | 194.49 | 187.04
2019-12-07 11:30 | 196.99 | 189.68
2019-12-07 12:00 | 199.06 | 191.65
2019-12-07 12:30 | 200.74 | 193.42
2019-12-07 13:00 | 202.01 | 195.04
2019-12-07 13:30 | 203.58 | 196.37
2019-12-07 14:00 | 204.76 | 197.55
2019-12-07 14:30 | 205.26 | 197.98
2019-12-07 15:00 | 207.16 | 199.77
2019-12-07 15:30 | 207.74 | 199.77
2019-12-07 16:00 | 209.46 | 201.39
2019-12-07 16:30 | 211.1 | 202.98
2019-12-07 17:00 | 213.55 | 205.6
2019-12-07 17:30 | 215.99 | 207.96
2019-12-07 18:00 | 218.04 | 210.06
2019-12-07 18:30 | 218.93 | 210.9
2019-12-07 19:00 | 218.26 | 209.99
2019-12-07 19:30 | 217.32 | 208.86
2019-12-07 20:00 | 215.3 | 206.73
2019-12-07 20:30 | 212.82 | 203.94
2019-12-07 21:00 | 209.71 | 200.22
2019-12-07 21:30 | 207.27 | 197.86
2019-12-07 22:00 | 204.52 | 195.06
2019-12-07 22:30 | 202.03 | 192.52
2019-12-07 23:00 | 199.7 | 189.85
2019-12-07 23:30 | 198.74 | 188.72
2019-12-08 | 197.34 | 187.29
2019-12-08 00:30 | 195.57 | 185.94
2019-12-08 01:00 | 194.52 | 185.04
2019-12-08 01:30 | 192.32 | 183.64
2019-12-08 02:00 | 191.47 | 182.76
2019-12-08 02:30 | 191.65 | 183.03
2019-12-08 03:00 | 193.05 | 184.68
2019-12-08 03:30 | 192.23 | 183.77
2019-12-08 04:00 | 191.45 | 182.94
2019-12-08 04:30 | 191.55 | 182.98
2019-12-08 05:00 | 190.96 | 182.31
2019-12-08 05:30 | 191.02 | 182.38
2019-12-08 06:00 | 189.05 | 180.64
2019-12-08 06:30 | 188.64 | 180.36
2019-12-08 07:00 | 188.52 | 180.93
2019-12-08 07:30 | 188.43 | 180.96
2019-12-08 08:00 | 188.69 | 181.14
2019-12-08 08:30 | 190.39 | 182.02
2019-12-08 09:00 | 191.43 | 182.56
2019-12-08 09:30 | 192.64 | 183.76
2019-12-08 10:00 | 193.96 | 185.15
2019-12-08 10:30 | 195.35 | 186.68
2019-12-08 11:00 | 197.47 | 188.91
2019-12-08 11:30 | 199.08 | 190.53
2019-12-08 12:00 | 201.74 | 193.1
2019-12-08 12:30 | 203.43 | 194.71
2019-12-08 13:00 | 205.57 | 196.89
2019-12-08 13:30 | 207 | 198.27
2019-12-08 14:00 | 209.43 | 200.76
2019-12-08 14:30 | 211.66 | 202.98
2019-12-08 15:00 | 214.82 | 206.76
2019-12-08 15:30 | 216.03 | 208.69
2019-12-08 16:00 | 217.77 | 210.54
2019-12-08 16:30 | 218.43 | 211.1
2019-12-08 17:00 | 220.74 | 213.48
2019-12-08 17:30 | 221.94 | 214.5
2019-12-08 18:00 | 223.33 | 216.12
2019-12-08 18:30 | 222.67 | 215.27
2019-12-08 19:00 | 222.78 | 215.2
2019-12-08 19:30 | 221.93 | 214.09
2019-12-08 20:00 | 219.42 | 211.37
2019-12-08 20:30 | 214.49 | 205.95
2019-12-08 21:00 | 211.13 | 202.01
2019-12-08 21:30 | 207.18 | 198.22
2019-12-08 22:00 | 202.67 | 193.85
2019-12-08 22:30 | 199.45 | 190.27
2019-12-08 23:00 | 196.84 | 187.48
2019-12-08 23:30 | 194.75 | 185.17
2019-12-09 | 192.38 | 183.24
2019-12-09 00:30 | 191.62 | 182.81
2019-12-09 01:00 | 190.57 | 181.66
2019-12-09 01:30 | 189.69 | 181.03
2019-12-09 02:00 | 187.87 | 179.84
2019-12-09 02:30 | 187.18 | 179.12
2019-12-09 03:00 | 187.08 | 179.11
2019-12-09 03:30 | 187.68 | 179.65
2019-12-09 04:00 | 188.02 | 179.9
2019-12-09 04:30 | 188.2 | 179.97
2019-12-09 05:00 | 189.08 | 180.55
2019-12-09 05:30 | 189.93 | 180.81
2019-12-09 06:00 | 190.56 | 181.45
2019-12-09 06:30 | 191.71 | 182.76
2019-12-09 07:00 | 193.65 | 184.25
2019-12-09 07:30 | 195.09 | 185.51
2019-12-09 08:00 | 195.48 | 185.96
2019-12-09 08:30 | 195.9 | 186.4
2019-12-09 09:00 | 196.65 | 186.97
2019-12-09 09:30 | 197.38 | 187.58
2019-12-09 10:00 | 199.89 | 190.42
2019-12-09 10:30 | 201.89 | 193.08
2019-12-09 11:00 | 203.22 | 194.48
2019-12-09 11:30 | 204.11 | 195.4
2019-12-09 12:00 | 206.1 | 197.46
2019-12-09 12:30 | 207.6 | 198.94
2019-12-09 13:00 | 209.33 | 200.8
2019-12-09 13:30 | 211.35 | 203.34
2019-12-09 14:00 | 213.06 | 205.42
2019-12-09 14:30 | 215.75 | 208.08
2019-12-09 15:00 | 216.27 | 208.23
2019-12-09 15:30 | 217.4 | 209.59
2019-12-09 16:00 | 218.87 | 210.99
2019-12-09 16:30 | 220.11 | 212.04
2019-12-09 17:00 | 221.54 | 213.83
2019-12-09 17:30 | 222.94 | 215.15
2019-12-09 18:00 | 224.47 | 216.71
2019-12-09 18:30 | 225.5 | 217.78
2019-12-09 19:00 | 226.12 | 218.29
2019-12-09 19:30 | 225.42 | 217.53
2019-12-09 20:00 | 222.9 | 214.77
2019-12-09 20:30 | 218.01 | 211.08
2019-12-09 21:00 | 213.26 | 205.86
2019-12-09 21:30 | 209.88 | 202.54
2019-12-09 22:00 | 206.41 | 198.64
2019-12-09 22:30 | 203.49 | 195.32
2019-12-09 23:00 | 200.79 | 192.59
2019-12-09 23:30 | 198.92 | 190.46
2019-12-10 | 197.19 | 188.68
2019-12-10 00:30 | 196.25 | 187.53
2019-12-10 01:00 | 195.29 | 186.54
2019-12-10 01:30 | 194.15 | 185.62
2019-12-10 02:00 | 193.33 | 184.67
2019-12-10 02:30 | 192.48 | 183.52
2019-12-10 03:00 | 192.82 | 183.64
2019-12-10 03:30 | 192.4 | 183.17
2019-12-10 04:00 | 192.63 | 183.31
2019-12-10 04:30 | 192.79 | 183.38
2019-12-10 05:00 | 193.14 | 183.71
2019-12-10 05:30 | 193.44 | 184.13
2019-12-10 06:00 | 193.43 | 184.48
2019-12-10 06:30 | 194.91 | 186.26
2019-12-10 07:00 | 196.28 | 187.66
2019-12-10 07:30 | 197.21 | 188.86
2019-12-10 08:00 | 197.45 | 189.08
2019-12-10 08:30 | 197.55 | 188.98
2019-12-10 09:00 | 197.54 | 188.9
2019-12-10 09:30 | 197.42 | 188.75
2019-12-10 10:00 | 198.57 | 189.91
2019-12-10 10:30 | 199.5 | 191.33
2019-12-10 11:00 | 200.56 | 192.46
2019-12-10 11:30 | 201.82 | 193.73
2019-12-10 12:00 | 204.02 | 196.15
2019-12-10 12:30 | 205.67 | 197.89
2019-12-10 13:00 | 208.12 | 200.34
2019-12-10 13:30 | 209.85 | 202.66
2019-12-10 14:00 | 211.41 | 204.6
2019-12-10 14:30 | 213.23 | 206.49
2019-12-10 15:00 | 214.97 | 208.34
2019-12-10 15:30 | 216.13 | 209.71
2019-12-10 16:00 | 217.59 | 211.68
2019-12-10 16:30 | 220.44 | 214.6
2019-12-10 17:00 | 222.67 | 216.93
2019-12-10 17:30 | 223.29 | 217.58
2019-12-10 18:00 | 223.83 | 218.13
2019-12-10 18:30 | 223.88 | 217.99
2019-12-10 19:00 | 224.57 | 218.44
2019-12-10 19:30 | 224.16 | 217.88
2019-12-10 20:00 | 222.65 | 216.24
2019-12-10 20:30 | 219.6 | 212.84
2019-12-10 21:00 | 215.91 | 208.52
2019-12-10 21:30 | 212.16 | 204.83
2019-12-10 22:00 | 207.7 | 200.36
2019-12-10 22:30 | 204.7 | 196.85
2019-12-10 23:00 | 202.04 | 193.92
2019-12-10 23:30 | 200.53 | 192.13
2019-12-11 | 197.71 | 189.38
2019-12-11 00:30 | 195.85 | 187.39
2019-12-11 01:00 | 194.95 | 186.34
2019-12-11 01:30 | 193.26 | 184.76
2019-12-11 02:00 | 192.39 | 184.07
2019-12-11 02:30 | 190.39 | 182.7
2019-12-11 03:00 | 189.49 | 182.26
2019-12-11 03:30 | 188.82 | 181.49
2019-12-11 04:00 | 188.48 | 180.86
2019-12-11 04:30 | 188.42 | 180.81
2019-12-11 05:00 | 189.05 | 181.57
2019-12-11 05:30 | 189.64 | 182.38
2019-12-11 06:00 | 190.67 | 183.67
2019-12-11 06:30 | 192.68 | 185.52
2019-12-11 07:00 | 194.13 | 186.82
2019-12-11 07:30 | 195.87 | 188.6
2019-12-11 08:00 | 196.15 | 188.91
2019-12-11 08:30 | 196.39 | 189.2
2019-12-11 09:00 | 197.73 | 190.51
2019-12-11 09:30 | 198.76 | 191.4
2019-12-11 10:00 | 200.1 | 192.69
2019-12-11 10:30 | 201.44 | 194.28
2019-12-11 11:00 | 202.78 | 195.58
2019-12-11 11:30 | 204.31 | 196.76
2019-12-11 12:00 | 206.39 | 198.78
2019-12-11 12:30 | 207.71 | 200.42
2019-12-11 13:00 | 210.64 | 203.52
2019-12-11 13:30 | 213.54 | 206.63
2019-12-11 14:00 | 215.22 | 208.24
2019-12-11 14:30 | 217.79 | 211.04
2019-12-11 15:00 | 218.56 | 211.34
2019-12-11 15:30 | 220.07 | 213.04
2019-12-11 16:00 | 222.15 | 215.25
2019-12-11 16:30 | 220.91 | 213.43
2019-12-11 17:00 | 221.96 | 214.33
2019-12-11 17:30 | 221.94 | 214.02
2019-12-11 18:00 | 223.7 | 216.03
2019-12-11 18:30 | 224.01 | 216.35
2019-12-11 19:00 | 224.87 | 217.5
2019-12-11 19:30 | 223.6 | 216.15
2019-12-11 20:00 | 221.58 | 213.96
2019-12-11 20:30 | 216.95 | 208.76
2019-12-11 21:00 | 214.14 | 205.06
2019-12-11 21:30 | 210.25 | 201.45
2019-12-11 22:00 | 201.85 | 193.37
2019-12-11 22:30 | 192.46 | 185.38
2019-12-11 23:00 | 216.08 | 211.8
2019-12-11 23:30 | 215.3 | 210.96
2019-12-12 | 213.32 | 208.91
2019-12-12 00:30 | 211.78 | 207.32
2019-12-12 01:00 | 210.72 | 206.25
2019-12-12 01:30 | 209.63 | 205.15
2019-12-12 02:00 | 208.8 | 204.32
2019-12-12 02:30 | 207.69 | 203.19
2019-12-12 03:00 | 203.39 | 198.38
2019-12-12 03:30 | 178.74 | 172.11
2019-12-12 04:00 | 178.59 | 171.77
2019-12-12 04:30 | 178.68 | 171.88
2019-12-12 05:00 | 179.42 | 172.69
2019-12-12 05:30 | 179.45 | 172.82
2019-12-12 06:00 | 179.89 | 173.45
2019-12-12 06:30 | 181.37 | 175.15
2019-12-12 07:00 | 181.88 | 175.56
2019-12-12 07:30 | 185.62 | 178.53
2019-12-12 08:00 | 193.2 | 185.91
2019-12-12 08:30 | 194.85 | 187.86
2019-12-12 09:00 | 194.94 | 188.01
2019-12-12 09:30 | 193.55 | 186.44
2019-12-12 10:00 | 196.14 | 189.12
2019-12-12 10:30 | 197.92 | 190.79
2019-12-12 11:00 | 199.13 | 191.83
2019-12-12 11:30 | 199.54 | 192.4
2019-12-12 12:00 | 201.77 | 194.92
2019-12-12 12:30 | 203.46 | 196.64
2019-12-12 13:00 | 205.56 | 198.63
2019-12-12 13:30 | 207.31 | 200.97
2019-12-12 14:00 | 208.51 | 202.34
2019-12-12 14:30 | 210.29 | 204.09
2019-12-12 15:00 | 207.84 | 201.75
2019-12-12 15:30 | 211.11 | 204.91
2019-12-12 16:00 | 214.93 | 207.42
2019-12-12 16:30 | 217.4 | 209.96
2019-12-12 17:00 | 219.67 | 212.32
2019-12-12 17:30 | 189.63 | 182.08
2019-12-12 18:00 | 191 | 183.47
2019-12-12 18:30 | 191.7 | 184.12
2019-12-12 19:00 | 191.58 | 183.97
2019-12-12 19:30 | 190.85 | 183.29
2019-12-12 20:00 | 188.13 | 180.39
2019-12-12 20:30 | 184.4 | 176.63
2019-12-12 21:00 | 208.16 | 199.83
2019-12-12 21:30 | 209.79 | 201.59
2019-12-12 22:00 | 206.26 | 197.57
2019-12-12 22:30 | 202.46 | 193.33
2019-12-12 23:00 | 199.68 | 190.11
2019-12-12 23:30 | 197.62 | 188.57
2019-12-13 | 194.14 | 186.21
2019-12-13 00:30 | 192.79 | 185.05
2019-12-13 01:00 | 191.95 | 184.06
2019-12-13 01:30 | 191.56 | 183.51
2019-12-13 02:00 | 184.5 | 176.34
2019-12-13 02:30 | 181.1 | 174.59
2019-12-13 03:00 | 201.52 | 197.06
2019-12-13 03:30 | 200.61 | 195.97
2019-12-13 04:00 | 200.08 | 195.41
2019-12-13 04:30 | 200.15 | 195.51
2019-12-13 05:00 | 200.29 | 195.67
2019-12-13 05:30 | 200.29 | 195.71
2019-12-13 06:00 | 200.33 | 195.83
2019-12-13 06:30 | 201.49 | 197.22
2019-12-13 07:00 | 204.21 | 199.85
2019-12-13 07:30 | 205.5 | 201.36
2019-12-13 08:00 | 205.06 | 201.04
2019-12-13 08:30 | 206.17 | 202.16
2019-12-13 09:00 | 206.12 | 202.18
2019-12-13 09:30 | 205.7 | 201.73
2019-12-13 10:00 | 206.74 | 202.85
2019-12-13 10:30 | 207.88 | 204.08
2019-12-13 11:00 | 208.01 | 204.31
2019-12-13 11:30 | 209.01 | 205.33
2019-12-13 12:00 | 211.19 | 207.5
2019-12-13 12:30 | 212.8 | 209.07
2019-12-13 13:00 | 215.21 | 211.45
2019-12-13 13:30 | 219.01 | 215.03
2019-12-13 14:00 | 205.93 | 200.69
2019-12-13 14:30 | 198.83 | 191.51
2019-12-13 15:00 | 205.28 | 198.29
2019-12-13 15:30 | 207.53 | 200.52
2019-12-13 16:00 | 180.91 | 174.42
2019-12-13 16:30 | 173.07 | 166.98
2019-12-13 17:00 | 174.19 | 168.22
2019-12-13 17:30 | 173.79 | 167.85
2019-12-13 18:00 | 172.83 | 167.36
2019-12-13 18:30 | 173.6 | 168.18
2019-12-13 19:00 | 165.89 | 160.46
2019-12-13 19:30 | 163.24 | 157.9
2019-12-13 20:00 | 161.7 | 156.37
2019-12-13 20:30 | 186.41 | 180.48
2019-12-13 21:00 | 190.51 | 184.28
2019-12-13 21:30 | 188.85 | 182.33
2019-12-13 22:00 | 186.36 | 179.48
2019-12-13 22:30 | 183.81 | 176.86
2019-12-13 23:00 | 182.07 | 175.12
2019-12-13 23:30 | 181.2 | 173.69
2019-12-14 | 175.17 | 167.35
2019-12-14 00:30 | 169.91 | 163.76
2019-12-14 01:00 | 190.11 | 185.36
2019-12-14 01:30 | 189.18 | 184.57
2019-12-14 02:00 | 188.63 | 184
2019-12-14 02:30 | 188.3 | 183.67
2019-12-14 03:00 | 187.69 | 183.08
2019-12-14 03:30 | 186.8 | 182.14
2019-12-14 04:00 | 186.67 | 182
2019-12-14 04:30 | 186.58 | 181.93
2019-12-14 05:00 | 186.61 | 181.94
2019-12-14 05:30 | 186.45 | 181.8
2019-12-14 06:00 | 185.99 | 181.32
2019-12-14 06:30 | 186.26 | 181.7
2019-12-14 07:00 | 186.96 | 182.16
2019-12-14 07:30 | 163.53 | 156.6
2019-12-14 08:00 | 153.88 | 146.21
2019-12-14 08:30 | 143.96 | 135.99
2019-12-14 09:00 | 144.8 | 136.39
2019-12-14 09:30 | 145.71 | 136.95
2019-12-14 10:00 | 146.48 | 137.64
2019-12-14 10:30 | 146.97 | 138.85
2019-12-14 11:00 | 149.07 | 141.04
2019-12-14 11:30 | 149.9 | 142.18
2019-12-14 12:00 | 151.77 | 144.26
2019-12-14 12:30 | 153.06 | 145.6
2019-12-14 13:00 | 153.55 | 146.14
2019-12-14 13:30 | 165.07 | 157.33
2019-12-14 14:00 | 184.2 | 176.57
2019-12-14 14:30 | 185.5 | 177.86
2019-12-14 15:00 | 187.49 | 179.94
2019-12-14 15:30 | 188.57 | 181.21
2019-12-14 16:00 | 190.95 | 183.73
2019-12-14 16:30 | 193.13 | 186.27
2019-12-14 17:00 | 194.9 | 188.33
2019-12-14 17:30 | 196.59 | 190.11
2019-12-14 18:00 | 198.44 | 191.87
2019-12-14 18:30 | 198.72 | 192.04
2019-12-14 19:00 | 198.7 | 191.92
2019-12-14 19:30 | 197.82 | 190.89
2019-12-14 20:00 | 197.04 | 190.12
2019-12-14 20:30 | 194.83 | 187.64
2019-12-14 21:00 | 191.63 | 184.16
2019-12-14 21:30 | 189.66 | 181.79
2019-12-14 22:00 | 187.25 | 178.84
2019-12-14 22:30 | 185.28 | 176.72
2019-12-14 23:00 | 183.12 | 174.36
2019-12-14 23:30 | 182.02 | 173.07
2019-12-15 | 180.11 | 170.92
2019-12-15 00:30 | 178.81 | 169.76
2019-12-15 01:00 | 177.15 | 168.54
2019-12-15 01:30 | 175.44 | 167.49
2019-12-15 02:00 | 175.06 | 167.05
2019-12-15 02:30 | 169.38 | 161.21
2019-12-15 03:00 | 164.77 | 157.65
2019-12-15 03:30 | 185.86 | 180.94
2019-12-15 04:00 | 185.73 | 180.79
2019-12-15 04:30 | 185.98 | 181.04
2019-12-15 05:00 | 185.79 | 180.85
2019-12-15 05:30 | 185.51 | 180.59
2019-12-15 06:00 | 185.6 | 180.68
2019-12-15 06:30 | 186.11 | 181.19
2019-12-15 07:00 | 186.33 | 181.71
2019-12-15 07:30 | 186.38 | 181.88
2019-12-15 08:00 | 186.54 | 182.06
2019-12-15 08:30 | 186.15 | 181.92
2019-12-15 09:00 | 187.21 | 183.02
2019-12-15 09:30 | 188.76 | 184.59
2019-12-15 10:00 | 190.28 | 186.14
2019-12-15 10:30 | 191.79 | 187.66
2019-12-15 11:00 | 192.93 | 188.89
2019-12-15 11:30 | 193.43 | 189.4
2019-12-15 12:00 | 172.24 | 168.55
2019-12-15 12:30 | 174.65 | 169.53
2019-12-15 13:00 | 175.52 | 170.86
2019-12-15 13:30 | 177.38 | 172.97
2019-12-15 14:00 | 185.33 | 181.15
2019-12-15 14:30 | 181.57 | 177.14
2019-12-15 15:00 | 189.63 | 184.75
2019-12-15 15:30 | 196.34 | 190.67
2019-12-15 16:00 | 197.03 | 191.32
2019-12-15 16:30 | 199.91 | 194.41
2019-12-15 17:00 | 201.19 | 195.93
2019-12-15 17:30 | 203.3 | 198.1
2019-12-15 18:00 | 204.77 | 199.76
2019-12-15 18:30 | 205.87 | 200.85
2019-12-15 19:00 | 204.96 | 199.8
2019-12-15 19:30 | 171.87 | 167.03
2019-12-15 20:00 | 170.69 | 165.82
2019-12-15 20:30 | 167.99 | 163.08
2019-12-15 21:00 | 163.6 | 158.71
2019-12-15 21:30 | 160.29 | 155.36
2019-12-15 22:00 | 156 | 151.53
2019-12-15 22:30 | 180.35 | 174.46
2019-12-15 23:00 | 185.89 | 179.3
2019-12-15 23:30 | 184.7 | 177.82
2019-12-16 | 182.78 | 175.95
2019-12-16 00:30 | 181.79 | 174.87
2019-12-16 01:00 | 180.02 | 173.57
2019-12-16 01:30 | 179.1 | 172.68
2019-12-16 02:00 | 178.89 | 172.36
2019-12-16 02:30 | 178.49 | 171.89
2019-12-16 03:00 | 177.58 | 170.89
2019-12-16 03:30 | 177.16 | 170.43
2019-12-16 04:00 | 174.92 | 168.13
2019-12-16 04:30 | 174.35 | 167.59
2019-12-16 05:00 | 174.6 | 167.82
2019-12-16 05:30 | 175.22 | 168.59
2019-12-16 06:00 | 176.67 | 169.63
2019-12-16 06:30 | 177.4 | 170.76
2019-12-16 07:00 | 153.19 | 146.53
2019-12-16 07:30 | 151.12 | 143.53
2019-12-16 08:00 | 152.85 | 145.33
2019-12-16 08:30 | 154.96 | 147.53
2019-12-16 09:00 | 176.34 | 169
2019-12-16 09:30 | 185.85 | 178.55
2019-12-16 10:00 | 187.28 | 180.07
2019-12-16 10:30 | 188.25 | 181.68
2019-12-16 11:00 | 189.92 | 183.24
2019-12-16 11:30 | 191.19 | 184.18
2019-12-16 12:00 | 191.96 | 184.89
2019-12-16 12:30 | 192.72 | 185.7
2019-12-16 13:00 | 193.15 | 186.31
2019-12-16 13:30 | 194.82 | 188.09
2019-12-16 14:00 | 196.18 | 189.81
2019-12-16 14:30 | 197.24 | 191.3
2019-12-16 15:00 | 197.05 | 191.19
2019-12-16 15:30 | 169.08 | 163.61
2019-12-16 16:00 | 161 | 157
2019-12-16 16:30 | 159.68 | 155.87
2019-12-16 17:00 | 157.9 | 154.18
2019-12-16 17:30 | 158.11 | 154.24
2019-12-16 18:00 | 157.52 | 153.52
2019-12-16 18:30 | 157.78 | 153.67
2019-12-16 19:00 | 160.04 | 155.74
2019-12-16 19:30 | 161.73 | 157.2
2019-12-16 20:00 | 163.69 | 159.04
2019-12-16 20:30 | 166.66 | 161.97
2019-12-16 21:00 | 195.55 | 188.52
2019-12-16 21:30 | 201.06 | 193.7
2019-12-16 22:00 | 197.06 | 189.64
2019-12-16 22:30 | 193.2 | 185.49
2019-12-16 23:00 | 189.76 | 182.18
2019-12-16 23:30 | 186.76 | 179.12
2019-12-17 | 182.93 | 175.88
2019-12-17 00:30 | 169.84 | 163.36
2019-12-17 01:00 | 183.9 | 178.73
2019-12-17 01:30 | 197.01 | 192.99
2019-12-17 02:00 | 195.79 | 191.72
2019-12-17 02:30 | 194.77 | 190.62
2019-12-17 03:00 | 194.22 | 189.97
2019-12-17 03:30 | 193.44 | 189.09
2019-12-17 04:00 | 192.85 | 188.43
2019-12-17 04:30 | 191.85 | 187.3
2019-12-17 05:00 | 191.83 | 187.32
2019-12-17 05:30 | 192.4 | 187.89
2019-12-17 06:00 | 193.16 | 188.8
2019-12-17 06:30 | 194.15 | 190.13
2019-12-17 07:00 | 194.97 | 191.15
2019-12-17 07:30 | 196.13 | 192.54
2019-12-17 08:00 | 196.67 | 193.12
2019-12-17 08:30 | 197.31 | 193.75
2019-12-17 09:00 | 197.43 | 193.82
2019-12-17 09:30 | 197.06 | 193.44
2019-12-17 10:00 | 198.74 | 195.09
2019-12-17 10:30 | 200 | 196.51
2019-12-17 11:00 | 200.98 | 197.46
2019-12-17 11:30 | 202.99 | 199.51
2019-12-17 12:00 | 204.73 | 201.36
2019-12-17 12:30 | 206.36 | 203.28
2019-12-17 13:00 | 209.41 | 206.27
2019-12-17 13:30 | 211.99 | 208.92
2019-12-17 14:00 | 213.64 | 210.59
2019-12-17 14:30 | 215.16 | 212.19
2019-12-17 15:00 | 217.21 | 214.17
2019-12-17 15:30 | 219.14 | 216.19
2019-12-17 16:00 | 221.3 | 218.49
2019-12-17 16:30 | 223.52 | 220.75
2019-12-17 17:00 | 226.09 | 223.45
2019-12-17 17:30 | 227.1 | 224.49
2019-12-17 18:00 | 228.8 | 226.35
2019-12-17 18:30 | 228.84 | 226.46
2019-12-17 19:00 | 229.44 | 227.15
2019-12-17 19:30 | 229.24 | 226.95
2019-12-17 20:00 | 227.62 | 225.19
2019-12-17 20:30 | 224.51 | 221.83
2019-12-17 21:00 | 219.83 | 216.93
2019-12-17 21:30 | 216.63 | 213.37
2019-12-17 22:00 | 211.85 | 208.38
2019-12-17 22:30 | 208.96 | 205.37
2019-12-17 23:00 | 206.27 | 202.55
2019-12-17 23:30 | 204.26 | 200.45
2019-12-18 | 202.33 | 198.23
2019-12-18 00:30 | 201.6 | 197.34
2019-12-18 01:00 | 200.43 | 196.13
2019-12-18 01:30 | 199.36 | 194.97
2019-12-18 02:00 | 198.06 | 193.59
2019-12-18 02:30 | 196.91 | 192.36
2019-12-18 03:00 | 196.05 | 191.46
2019-12-18 03:30 | 195.35 | 190.7
2019-12-18 04:00 | 194.83 | 190.18
2019-12-18 04:30 | 194.95 | 190.32
2019-12-18 05:00 | 194.82 | 190.21
2019-12-18 05:30 | 195.1 | 190.48
2019-12-18 06:00 | 195.4 | 190.89
2019-12-18 06:30 | 196.98 | 192.76
2019-12-18 07:00 | 197.86 | 193.72
2019-12-18 07:30 | 196.49 | 192.85
2019-12-18 08:00 | 188.41 | 185.1
2019-12-18 08:30 | 182.28 | 179.05
2019-12-18 09:00 | 175.08 | 172.18
2019-12-18 09:30 | 170.11 | 167.36
2019-12-18 10:00 | 171.56 | 168.83
2019-12-18 10:30 | 182.84 | 179.61
2019-12-18 11:00 | 198.95 | 195.21
2019-12-18 11:30 | 200.14 | 196.45
2019-12-18 12:00 | 201.57 | 197.87
2019-12-18 12:30 | 203.12 | 199.44
2019-12-18 13:00 | 204.91 | 201.2
2019-12-18 13:30 | 206.9 | 203.34
2019-12-18 14:00 | 208.95 | 205.61
2019-12-18 14:30 | 211.17 | 207.96
2019-12-18 15:00 | 212.42 | 209.31
2019-12-18 15:30 | 214.4 | 211.4
2019-12-18 16:00 | 216.55 | 213.64
2019-12-18 16:30 | 219.15 | 216.19
2019-12-18 17:00 | 222.65 | 219.66
2019-12-18 17:30 | 228.85 | 225.44
2019-12-18 18:00 | 230.66 | 226.45
2019-12-18 18:30 | 204.47 | 198.22
2019-12-18 19:00 | 216.13 | 209.36
2019-12-18 19:30 | 213.18 | 206.47
2019-12-18 20:00 | 211.72 | 204.87
2019-12-18 20:30 | 209.82 | 202.48
2019-12-18 21:00 | 207.33 | 199.4
2019-12-18 21:30 | 205.39 | 197.71
2019-12-18 22:00 | 200.89 | 193.37
2019-12-18 22:30 | 197.36 | 189.67
2019-12-18 23:00 | 195.01 | 187.14
2019-12-18 23:30 | 194.7 | 186.75
2019-12-19 | 193.03 | 185.02
2019-12-19 00:30 | 192.07 | 184
2019-12-19 01:00 | 190.63 | 182.38
2019-12-19 01:30 | 186.02 | 178.03
2019-12-19 02:00 | 178.71 | 171.16
2019-12-19 02:30 | 177.64 | 169.93
2019-12-19 03:00 | 176.96 | 169.13
2019-12-19 03:30 | 176.28 | 168.43
2019-12-19 04:00 | 175.63 | 167.75
2019-12-19 04:30 | 175.43 | 167.61
2019-12-19 05:00 | 175.7 | 167.97
2019-12-19 05:30 | 175.82 | 168.17
2019-12-19 06:00 | 175.63 | 168.17
2019-12-19 06:30 | 176.59 | 169.46
2019-12-19 07:00 | 177.04 | 170.18
2019-12-19 07:30 | 173.24 | 167.03
2019-12-19 08:00 | 166.7 | 160.48
2019-12-19 08:30 | 160.64 | 154.42
2019-12-19 09:00 | 154.43 | 148.34
2019-12-19 09:30 | 150.94 | 145.16
2019-12-19 10:00 | 154.69 | 149.27
2019-12-19 10:30 | 156.09 | 150.89
2019-12-19 11:00 | 172.98 | 167
2019-12-19 11:30 | 177.94 | 172.16
2019-12-19 12:00 | 179.18 | 173.43
2019-12-19 12:30 | 194.21 | 189.82
2019-12-19 13:00 | 204.04 | 200.72
2019-12-19 13:30 | 207.66 | 204.42
2019-12-19 14:00 | 209.35 | 206.23
2019-12-19 14:30 | 213.92 | 210.65
2019-12-19 15:00 | 216.77 | 213.41
2019-12-19 15:30 | 223.16 | 219.48
2019-12-19 16:00 | 225.66 | 222.16
2019-12-19 16:30 | 227.66 | 224.25
2019-12-19 17:00 | 229.89 | 226.56
2019-12-19 17:30 | 231.66 | 228.28
2019-12-19 18:00 | 233.05 | 229.79
2019-12-19 18:30 | 233.41 | 230.15
2019-12-19 19:00 | 233.56 | 230.23
2019-12-19 19:30 | 232.58 | 229.24
2019-12-19 20:00 | 230.66 | 227.35
2019-12-19 20:30 | 227.78 | 224.36
2019-12-19 21:00 | 223.85 | 220.17
2019-12-19 21:30 | 221.07 | 217.23
2019-12-19 22:00 | 218.21 | 214.13
2019-12-19 22:30 | 214.48 | 210.22
2019-12-19 23:00 | 212.33 | 208.02
2019-12-19 23:30 | 211 | 206.63
2019-12-20 | 209.08 | 204.71
2019-12-20 00:30 | 208.13 | 203.59
2019-12-20 01:00 | 206.65 | 202.02
2019-12-20 01:30 | 205.47 | 200.95
2019-12-20 02:00 | 204.41 | 199.89
2019-12-20 02:30 | 203.87 | 199.3
2019-12-20 03:00 | 202.76 | 198.19
2019-12-20 03:30 | 202.27 | 197.64
2019-12-20 04:00 | 202.01 | 197.39
2019-12-20 04:30 | 201.61 | 196.97
2019-12-20 05:00 | 201.74 | 197.12
2019-12-20 05:30 | 202.07 | 197.52
2019-12-20 06:00 | 202.17 | 197.67
2019-12-20 06:30 | 203.16 | 198.67
2019-12-20 07:00 | 202.53 | 198.37
2019-12-20 07:30 | 201.13 | 197.24
2019-12-20 08:00 | 198.4 | 193.89
2019-12-20 08:30 | 177.22 | 170.97
2019-12-20 09:00 | 178.52 | 172.19
2019-12-20 09:30 | 179.31 | 172.98
2019-12-20 10:00 | 180.71 | 174.3
2019-12-20 10:30 | 182.24 | 175.8
2019-12-20 11:00 | 184.26 | 177.71
2019-12-20 11:30 | 186.46 | 179.98
2019-12-20 12:00 | 184.89 | 178.5
2019-12-20 12:30 | 196.41 | 189.49
2019-12-20 13:00 | 196.98 | 189.57
2019-12-20 13:30 | 197.87 | 190.2
2019-12-20 14:00 | 199.57 | 192.02
2019-12-20 14:30 | 200.75 | 193.41
2019-12-20 15:00 | 202.41 | 195.4
2019-12-20 15:30 | 204.61 | 197.53
2019-12-20 16:00 | 206.32 | 199.54
2019-12-20 16:30 | 209.27 | 202.87
2019-12-20 17:00 | 211.39 | 205.12
2019-12-20 17:30 | 212.55 | 205.94
2019-12-20 18:00 | 212.78 | 205.89
2019-12-20 18:30 | 213.31 | 206.31
2019-12-20 19:00 | 212.94 | 205.67
2019-12-20 19:30 | 211.99 | 204.69
2019-12-20 20:00 | 211.12 | 203.69
2019-12-20 20:30 | 208.84 | 201.01
2019-12-20 21:00 | 206.01 | 197.77
2019-12-20 21:30 | 202.91 | 194.94
2019-12-20 22:00 | 199.57 | 191.23
2019-12-20 22:30 | 197.24 | 188.61
2019-12-20 23:00 | 195.68 | 186.68
2019-12-20 23:30 | 194.97 | 185.78
2019-12-21 | 193.1 | 184.02
2019-12-21 00:30 | 191.5 | 182.69
2019-12-21 01:00 | 189.81 | 181.22
2019-12-21 01:30 | 188.42 | 179.97
2019-12-21 02:00 | 187.24 | 178.67
2019-12-21 02:30 | 186.35 | 177.78
2019-12-21 03:00 | 185.84 | 177.09
2019-12-21 03:30 | 185.06 | 176.18
2019-12-21 04:00 | 184.96 | 175.95
2019-12-21 04:30 | 184.86 | 175.8
2019-12-21 05:00 | 184.84 | 175.74
2019-12-21 05:30 | 184.42 | 175.17
2019-12-21 06:00 | 183.76 | 174.69
2019-12-21 06:30 | 182.76 | 174.14
2019-12-21 07:00 | 182.61 | 174.61
2019-12-21 07:30 | 183.37 | 174.75
2019-12-21 08:00 | 182.82 | 174.52
2019-12-21 08:30 | 183.05 | 174.71
2019-12-21 09:00 | 183.25 | 174.94
2019-12-21 09:30 | 184.7 | 175.7
2019-12-21 10:00 | 185.81 | 176.34
2019-12-21 10:30 | 186.06 | 176.83
2019-12-21 11:00 | 186.79 | 177.92
2019-12-21 11:30 | 188.63 | 179.68
2019-12-21 12:00 | 190.75 | 181.36
2019-12-21 12:30 | 192.04 | 182.81
2019-12-21 13:00 | 194.02 | 184.69
2019-12-21 13:30 | 196.1 | 186.82
2019-12-21 14:00 | 197.88 | 188.43
2019-12-21 14:30 | 200.73 | 191.72
2019-12-21 15:00 | 201.78 | 193.1
2019-12-21 15:30 | 204.08 | 195.83
2019-12-21 16:00 | 206.78 | 198.64
2019-12-21 16:30 | 209.69 | 201.7
2019-12-21 17:00 | 183.9 | 175.89
2019-12-21 17:30 | 182.02 | 173.8
2019-12-21 18:00 | 183.66 | 175.38
2019-12-21 18:30 | 184.04 | 175.69
2019-12-21 19:00 | 183.55 | 175.09
2019-12-21 19:30 | 182.33 | 173.88
2019-12-21 20:00 | 180.54 | 171.95
2019-12-21 20:30 | 205.29 | 196.77
2019-12-21 21:00 | 207.4 | 198.91
2019-12-21 21:30 | 204.39 | 196.28
2019-12-21 22:00 | 200.57 | 192.49
2019-12-21 22:30 | 197.07 | 189.13
2019-12-21 23:00 | 194.52 | 186.35
2019-12-21 23:30 | 193.27 | 184.86
2019-12-22 | 190.03 | 182.15
2019-12-22 00:30 | 189.12 | 180.56
2019-12-22 01:00 | 187.94 | 179.28
2019-12-22 01:30 | 187.26 | 178.57
2019-12-22 02:00 | 186.11 | 177.55
2019-12-22 02:30 | 185.35 | 176.65
2019-12-22 03:00 | 185.26 | 176.26
2019-12-22 03:30 | 184.89 | 175.59
2019-12-22 04:00 | 184.72 | 175.34
2019-12-22 04:30 | 184.54 | 175.12
2019-12-22 05:00 | 184.61 | 175.2
2019-12-22 05:30 | 184.25 | 174.71
2019-12-22 06:00 | 183.78 | 174.4
2019-12-22 06:30 | 183.5 | 174.77
2019-12-22 07:00 | 183.11 | 175.19
2019-12-22 07:30 | 184.51 | 176.03
2019-12-22 08:00 | 186.14 | 177.64
2019-12-22 08:30 | 188.16 | 180.37
2019-12-22 09:00 | 190 | 181.15
2019-12-22 09:30 | 192.15 | 182.53
2019-12-22 10:00 | 192.56 | 182.43
2019-12-22 10:30 | 192.75 | 182.67
2019-12-22 11:00 | 195.01 | 184.53
2019-12-22 11:30 | 196.78 | 186.67
2019-12-22 12:00 | 198.89 | 189.15
2019-12-22 12:30 | 200.72 | 190.71
2019-12-22 13:00 | 202.26 | 192.09
2019-12-22 13:30 | 203.74 | 193.56
2019-12-22 14:00 | 205.21 | 195.12
2019-12-22 14:30 | 207.31 | 197.21
2019-12-22 15:00 | 207.82 | 197.67
2019-12-22 15:30 | 210.6 | 200.4
2019-12-22 16:00 | 213.88 | 203.8
2019-12-22 16:30 | 216 | 206.24
2019-12-22 17:00 | 217.79 | 208.34
2019-12-22 17:30 | 218.5 | 210.25
2019-12-22 18:00 | 220.47 | 212.92
2019-12-22 18:30 | 221.14 | 213.69
2019-12-22 19:00 | 221.87 | 214.55
2019-12-22 19:30 | 221.45 | 214.04
2019-12-22 20:00 | 219.98 | 212.36
2019-12-22 20:30 | 217.46 | 209.61
2019-12-22 21:00 | 214.52 | 206.33
2019-12-22 21:30 | 210.65 | 203.17
2019-12-22 22:00 | 206.84 | 199.05
2019-12-22 22:30 | 203.7 | 195.82
2019-12-22 23:00 | 201.43 | 193.29
2019-12-22 23:30 | 199.75 | 191.48
2019-12-23 | 197.24 | 189.25
2019-12-23 00:30 | 195.96 | 187.99
2019-12-23 01:00 | 193.52 | 186.39
2019-12-23 01:30 | 192.41 | 185.64
2019-12-23 02:00 | 191.72 | 184.79
2019-12-23 02:30 | 191.24 | 184.21
2019-12-23 03:00 | 190.45 | 183.35
2019-12-23 03:30 | 189.93 | 182.67
2019-12-23 04:00 | 189.02 | 181.63
2019-12-23 04:30 | 188.52 | 181.12
2019-12-23 05:00 | 188.41 | 181.07
2019-12-23 05:30 | 188.21 | 180.88
2019-12-23 06:00 | 188.17 | 180.89
2019-12-23 06:30 | 188.87 | 181.27
2019-12-23 07:00 | 189.21 | 181.71
2019-12-23 07:30 | 189.68 | 182.03
2019-12-23 08:00 | 189.6 | 182.11
2019-12-23 08:30 | 189.3 | 181.93
2019-12-23 09:00 | 189.03 | 181.66
2019-12-23 09:30 | 188.17 | 180.74
2019-12-23 10:00 | 187.29 | 179.88
2019-12-23 10:30 | 188.03 | 180.62
2019-12-23 11:00 | 188.94 | 181.53
2019-12-23 11:30 | 191.55 | 184.53
2019-12-23 12:00 | 193.02 | 185.89
2019-12-23 12:30 | 194.99 | 187.96
2019-12-23 13:00 | 197.17 | 190.07
2019-12-23 13:30 | 198.85 | 191.79
2019-12-23 14:00 | 200.43 | 193.36
2019-12-23 14:30 | 202.57 | 195.34
2019-12-23 15:00 | 205.08 | 197.8
2019-12-23 15:30 | 207.15 | 199.73
2019-12-23 16:00 | 208.82 | 201.7
2019-12-23 16:30 | 211.09 | 204.07
2019-12-23 17:00 | 213.11 | 206.2
2019-12-23 17:30 | 214.16 | 207.08
2019-12-23 18:00 | 216.07 | 208.97
2019-12-23 18:30 | 216.89 | 209.78
2019-12-23 19:00 | 218.01 | 210.77
2019-12-23 19:30 | 217.83 | 210.51
2019-12-23 20:00 | 217.35 | 209.81
2019-12-23 20:30 | 215.51 | 207.62
2019-12-23 21:00 | 212.51 | 204.17
2019-12-23 21:30 | 209.4 | 201.65
2019-12-23 22:00 | 205.76 | 197.93
2019-12-23 22:30 | 202.54 | 194.61
2019-12-23 23:00 | 200.08 | 191.58
2019-12-23 23:30 | 199.07 | 190.37
2019-12-24 | 196.67 | 188.42
2019-12-24 00:30 | 194.34 | 186.39
2019-12-24 01:00 | 193.46 | 185.43
2019-12-24 01:30 | 192.96 | 184.51
2019-12-24 02:00 | 192.65 | 183.48
2019-12-24 02:30 | 192.09 | 182.38
2019-12-24 03:00 | 191.07 | 181
2019-12-24 03:30 | 190.21 | 180.16
2019-12-24 04:00 | 185.76 | 175.54
2019-12-24 04:30 | 170.58 | 160.92
2019-12-24 05:00 | 170.19 | 160.72
2019-12-24 05:30 | 170.54 | 161.02
2019-12-24 06:00 | 170.69 | 161.45
2019-12-24 06:30 | 171.69 | 162.22
2019-12-24 07:00 | 172.97 | 163.32
2019-12-24 07:30 | 174.53 | 164.42
2019-12-24 08:00 | 174.64 | 164.6
2019-12-24 08:30 | 175.45 | 166.84
2019-12-24 09:00 | 176.39 | 168.02
2019-12-24 09:30 | 177.56 | 169.19
2019-12-24 10:00 | 185.7 | 176.52
2019-12-24 10:30 | 193.86 | 184.93
2019-12-24 11:00 | 195.16 | 186.16
2019-12-24 11:30 | 196.7 | 188.22
2019-12-24 12:00 | 197.83 | 189.58
2019-12-24 12:30 | 199.53 | 191.06
2019-12-24 13:00 | 201.55 | 193.4
2019-12-24 13:30 | 203.08 | 195.05
2019-12-24 14:00 | 203.7 | 195.63
2019-12-24 14:30 | 206.23 | 198.19
2019-12-24 15:00 | 208.55 | 200.66
2019-12-24 15:30 | 208.71 | 200.95
2019-12-24 16:00 | 207.89 | 200.24
2019-12-24 16:30 | 208.93 | 201.64
2019-12-24 17:00 | 211.17 | 203.76
2019-12-24 17:30 | 212.1 | 204.52
2019-12-24 18:00 | 213.28 | 205.57
2019-12-24 18:30 | 214.16 | 206.27
2019-12-24 19:00 | 214.06 | 205.88
2019-12-24 19:30 | 213.37 | 205.06
2019-12-24 20:00 | 212.67 | 204.29
2019-12-24 20:30 | 211.74 | 202.9
2019-12-24 21:00 | 208.87 | 199.74
2019-12-24 21:30 | 206.21 | 197.43
2019-12-24 22:00 | 202.88 | 194.33
2019-12-24 22:30 | 199.59 | 191.38
2019-12-24 23:00 | 196.75 | 189.04
2019-12-24 23:30 | 195.06 | 187.11
2019-12-25 | 193.29 | 185.11
2019-12-25 00:30 | 191.21 | 183.52
2019-12-25 01:00 | 189.73 | 182.11
2019-12-25 01:30 | 189.32 | 180.75
2019-12-25 02:00 | 189.45 | 179.9
2019-12-25 02:30 | 185.51 | 176.01
2019-12-25 03:00 | 168.34 | 158.86
2019-12-25 03:30 | 166.36 | 156.96
2019-12-25 04:00 | 166.02 | 156.57
2019-12-25 04:30 | 165.37 | 155.91
2019-12-25 05:00 | 164.61 | 155.56
2019-12-25 05:30 | 164.34 | 155.22
2019-12-25 06:00 | 163.94 | 154.86
2019-12-25 06:30 | 163.98 | 155.37
2019-12-25 07:00 | 163.63 | 155.79
2019-12-25 07:30 | 164.04 | 156.29
2019-12-25 08:00 | 164.66 | 156.8
2019-12-25 08:30 | 165.49 | 156.99
2019-12-25 09:00 | 166.34 | 156.68
2019-12-25 09:30 | 167.31 | 157.34
2019-12-25 10:00 | 168.93 | 158.75
2019-12-25 10:30 | 170.03 | 159.9
2019-12-25 11:00 | 170.94 | 160.91
2019-12-25 11:30 | 172.68 | 162.44
2019-12-25 12:00 | 173.57 | 163.4
2019-12-25 12:30 | 174.16 | 163.99
2019-12-25 13:00 | 174.75 | 164.98
2019-12-25 13:30 | 174.9 | 165.48
2019-12-25 14:00 | 175.39 | 166.17
2019-12-25 14:30 | 177.05 | 168.07
2019-12-25 15:00 | 178.33 | 169.54
2019-12-25 15:30 | 180.37 | 170.73
2019-12-25 16:00 | 182.67 | 172.41
2019-12-25 16:30 | 182.04 | 173.01
2019-12-25 17:00 | 183.63 | 174.9
2019-12-25 17:30 | 184.21 | 175.19
2019-12-25 18:00 | 185.62 | 176.25
2019-12-25 18:30 | 184.37 | 176.17
2019-12-25 19:00 | 183.36 | 175.19
2019-12-25 19:30 | 182.27 | 174.12
2019-12-25 20:00 | 180.97 | 172.78
2019-12-25 20:30 | 180.02 | 171.74
2019-12-25 21:00 | 179.26 | 170.67
2019-12-25 21:30 | 178.22 | 169.51
2019-12-25 22:00 | 176.56 | 167.54
2019-12-25 22:30 | 174.83 | 165.43
2019-12-25 23:00 | 172.91 | 163.39
2019-12-25 23:30 | 171.51 | 161.97
2019-12-26 | 168.98 | 160.02
2019-12-26 00:30 | 167.68 | 158.77
2019-12-26 01:00 | 166.83 | 157.69
2019-12-26 01:30 | 166.04 | 156.77
2019-12-26 02:00 | 165.6 | 156.22
2019-12-26 02:30 | 164.96 | 155.39
2019-12-26 03:00 | 163.97 | 154.23
2019-12-26 03:30 | 163.44 | 153.66
2019-12-26 04:00 | 162.74 | 152.95
2019-12-26 04:30 | 162.89 | 153.26
2019-12-26 05:00 | 162.12 | 152.61
2019-12-26 05:30 | 161.86 | 152.36
2019-12-26 06:00 | 161.44 | 152.08
2019-12-26 06:30 | 160.9 | 152.32
2019-12-26 07:00 | 159.98 | 152.32
2019-12-26 07:30 | 160.01 | 151.71
2019-12-26 08:00 | 160.19 | 151.6
2019-12-26 08:30 | 160.32 | 150.71
2019-12-26 09:00 | 160.82 | 150.89
2019-12-26 09:30 | 162.01 | 151.38
2019-12-26 10:00 | 162.61 | 151.65
2019-12-26 10:30 | 163.1 | 152.29
2019-12-26 11:00 | 164.06 | 153.6
2019-12-26 11:30 | 164.92 | 154.63
2019-12-26 12:00 | 165.95 | 155.82
2019-12-26 12:30 | 167.5 | 157.29
2019-12-26 13:00 | 168.79 | 159.18
2019-12-26 13:30 | 170.23 | 160.77
2019-12-26 14:00 | 171.72 | 162.09
2019-12-26 14:30 | 173.33 | 163.75
2019-12-26 15:00 | 174.38 | 165.16
2019-12-26 15:30 | 175.46 | 166.12
2019-12-26 16:00 | 191.36 | 181.67
2019-12-26 16:30 | 201.18 | 191.64
2019-12-26 17:00 | 202.35 | 192.84
2019-12-26 17:30 | 204.36 | 194.82
2019-12-26 18:00 | 205.91 | 196.46
2019-12-26 18:30 | 207.11 | 197.68
2019-12-26 19:00 | 207.59 | 197.95
2019-12-26 19:30 | 206.73 | 197.6
2019-12-26 20:00 | 205.8 | 197.06
2019-12-26 20:30 | 204.99 | 196.06
2019-12-26 21:00 | 203.01 | 193.7
2019-12-26 21:30 | 201.01 | 192.08
2019-12-26 22:00 | 177.32 | 168.7
2019-12-26 22:30 | 171.43 | 163.2
2019-12-26 23:00 | 169.95 | 161.55
2019-12-26 23:30 | 168.18 | 160.08
2019-12-27 | 166 | 158
2019-12-27 00:30 | 165.99 | 156.94
2019-12-27 01:00 | 164.42 | 155.55
2019-12-27 01:30 | 163.24 | 154.39
2019-12-27 02:00 | 162.31 | 153.36
2019-12-27 02:30 | 161.76 | 152.7
2019-12-27 03:00 | 161.94 | 152.83
2019-12-27 03:30 | 160.99 | 151.81
2019-12-27 04:00 | 190.86 | 184.79
2019-12-27 04:30 | 200.69 | 195.69
2019-12-27 05:00 | 200.61 | 195.62
2019-12-27 05:30 | 200.98 | 196
2019-12-27 06:00 | 200.93 | 195.99
2019-12-27 06:30 | 201.55 | 196.68
2019-12-27 07:00 | 202.49 | 197.63
2019-12-27 07:30 | 202.51 | 197.79
2019-12-27 08:00 | 201.6 | 197.03
2019-12-27 08:30 | 201.19 | 196.66
2019-12-27 09:00 | 201.09 | 196.59
2019-12-27 09:30 | 200.6 | 196.16
2019-12-27 10:00 | 201.03 | 196.42
2019-12-27 10:30 | 202.36 | 197.59
2019-12-27 11:00 | 191.86 | 186.09
2019-12-27 11:30 | 176.49 | 169.02
2019-12-27 12:00 | 177.08 | 169.85
2019-12-27 12:30 | 178.46 | 171.43
2019-12-27 13:00 | 179.76 | 172.85
2019-12-27 13:30 | 180.16 | 173.49
2019-12-27 14:00 | 180.69 | 174.22
2019-12-27 14:30 | 181.74 | 175.25
2019-12-27 15:00 | 183.19 | 176.29
2019-12-27 15:30 | 187.01 | 179.07
2019-12-27 16:00 | 195.18 | 187.3
2019-12-27 16:30 | 198.3 | 190.58
2019-12-27 17:00 | 201.24 | 193.55
2019-12-27 17:30 | 203.72 | 196.07
2019-12-27 18:00 | 204.94 | 197.39
2019-12-27 18:30 | 205.93 | 198.27
2019-12-27 19:00 | 206.08 | 198.16
2019-12-27 19:30 | 206.2 | 198.34
2019-12-27 20:00 | 205.64 | 197.78
2019-12-27 20:30 | 204.18 | 196.07
2019-12-27 21:00 | 201.9 | 193.39
2019-12-27 21:30 | 199.57 | 191.49
2019-12-27 22:00 | 197.06 | 188.77
2019-12-27 22:30 | 194.82 | 186.78
2019-12-27 23:00 | 192.83 | 184.71
2019-12-27 23:30 | 192.53 | 184
2019-12-28 | 190.31 | 182.06
2019-12-28 00:30 | 188.91 | 181.18
2019-12-28 01:00 | 164.78 | 156.88
2019-12-28 01:30 | 159.57 | 151.61
2019-12-28 02:00 | 159.71 | 151.7
2019-12-28 02:30 | 158.81 | 150.7
2019-12-28 03:00 | 158.34 | 150.2
2019-12-28 03:30 | 157.77 | 149.51
2019-12-28 04:00 | 157.19 | 149.01
2019-12-28 04:30 | 156.63 | 148.5
2019-12-28 05:00 | 156.18 | 148.07
2019-12-28 05:30 | 156.36 | 148.17
2019-12-28 06:00 | 156.27 | 148.2
2019-12-28 06:30 | 156.69 | 149.14
2019-12-28 07:00 | 158.09 | 150.42
2019-12-28 07:30 | 157.3 | 149.83
2019-12-28 08:00 | 157.16 | 149.52
2019-12-28 08:30 | 159.4 | 149.42
2019-12-28 09:00 | 174.02 | 164.79
2019-12-28 09:30 | 183.94 | 174.14
2019-12-28 10:00 | 184.08 | 174.87
2019-12-28 10:30 | 184.68 | 175.76
2019-12-28 11:00 | 184.73 | 175.82
2019-12-28 11:30 | 185.07 | 176.52
2019-12-28 12:00 | 186.32 | 177.56
2019-12-28 12:30 | 185.85 | 177.17
2019-12-28 13:00 | 186.88 | 177.84
2019-12-28 13:30 | 188.59 | 179.96
2019-12-28 14:00 | 189.84 | 180.97
2019-12-28 14:30 | 189.84 | 180.93
2019-12-28 15:00 | 190.93 | 182.23
2019-12-28 15:30 | 193.45 | 184.51
2019-12-28 16:00 | 195.63 | 186.11
2019-12-28 16:30 | 198.71 | 188.5
2019-12-28 17:00 | 200.72 | 190.64
2019-12-28 17:30 | 203.51 | 193.22
2019-12-28 18:00 | 205.41 | 195.32
2019-12-28 18:30 | 207.06 | 196.84
2019-12-28 19:00 | 206.5 | 197.58
2019-12-28 19:30 | 205.95 | 197.2
2019-12-28 20:00 | 205.17 | 196.34
2019-12-28 20:30 | 203.47 | 194.37
2019-12-28 21:00 | 201.08 | 192.07
2019-12-28 21:30 | 198.95 | 190.12
2019-12-28 22:00 | 196.08 | 187.26
2019-12-28 22:30 | 193.53 | 184.84
2019-12-28 23:00 | 191.06 | 182.79
2019-12-28 23:30 | 168.42 | 160.05
2019-12-29 | 165.31 | 156.47
2019-12-29 00:30 | 164.04 | 155.77
2019-12-29 01:00 | 162.75 | 154.25
2019-12-29 01:30 | 161.76 | 153.08
2019-12-29 02:00 | 161.65 | 152.94
2019-12-29 02:30 | 161.29 | 152.46
2019-12-29 03:00 | 160.78 | 151.8
2019-12-29 03:30 | 160.13 | 151.15
2019-12-29 04:00 | 156.91 | 147.89
2019-12-29 04:30 | 140.56 | 131.64
2019-12-29 05:00 | 140.73 | 131.77
2019-12-29 05:30 | 140.53 | 131.56
2019-12-29 06:00 | 140.53 | 130.99
2019-12-29 06:30 | 154.12 | 140.37
2019-12-29 07:00 | 165.58 | 151.12
2019-12-29 07:30 | 165.36 | 151.42
2019-12-29 08:00 | 164.97 | 150.11
2019-12-29 08:30 | 164.17 | 149.43
2019-12-29 09:00 | 164.55 | 149.33
2019-12-29 09:30 | 165.17 | 149.35
2019-12-29 10:00 | 165.2 | 149.34
2019-12-29 10:30 | 165.32 | 150.01
2019-12-29 11:00 | 165.95 | 150.95
2019-12-29 11:30 | 168.05 | 152.27
2019-12-29 12:00 | 169.6 | 154.25
2019-12-29 12:30 | 171.03 | 155.83
2019-12-29 13:00 | 173.86 | 158.24
2019-12-29 13:30 | 175.95 | 159.34
2019-12-29 14:00 | 178.11 | 160.89
2019-12-29 14:30 | 179.2 | 162.52
2019-12-29 15:00 | 177.72 | 165.04
2019-12-29 15:30 | 177.19 | 167.26
2019-12-29 16:00 | 177.12 | 168.45
2019-12-29 16:30 | 180.03 | 171.41
2019-12-29 17:00 | 182.74 | 173.66
2019-12-29 17:30 | 184.15 | 175.29
2019-12-29 18:00 | 200.8 | 191.54
2019-12-29 18:30 | 209.72 | 200.41
2019-12-29 19:00 | 209.53 | 201.3
2019-12-29 19:30 | 208.46 | 200.54
2019-12-29 20:00 | 207.35 | 199.29
2019-12-29 20:30 | 205.16 | 196.76
2019-12-29 21:00 | 201.94 | 193.34
2019-12-29 21:30 | 181.56 | 169.9
2019-12-29 22:00 | 178.22 | 163.99
2019-12-29 22:30 | 175.76 | 160.91
2019-12-29 23:00 | 173.62 | 159.07
2019-12-29 23:30 | 172.7 | 158.75
2019-12-30 | 170.32 | 156.84
2019-12-30 00:30 | 169.17 | 155.56
2019-12-30 01:00 | 168.45 | 154.55
2019-12-30 01:30 | 168.02 | 153.86
2019-12-30 02:00 | 167.59 | 153.08
2019-12-30 02:30 | 167.26 | 152.57
2019-12-30 03:00 | 166.92 | 151.64
2019-12-30 03:30 | 166.06 | 150.68
2019-12-30 04:00 | 165.74 | 150.25
2019-12-30 04:30 | 165.05 | 149.62
2019-12-30 05:00 | 165.02 | 149.68
2019-12-30 05:30 | 165.07 | 149.58
2019-12-30 06:00 | 165.14 | 149.72
2019-12-30 06:30 | 164.15 | 149.55
2019-12-30 07:00 | 162.64 | 148.61
2019-12-30 07:30 | 163.29 | 148.16
2019-12-30 08:00 | 163.84 | 147.78
2019-12-30 08:30 | 166.29 | 148.55
2019-12-30 09:00 | 165.35 | 148.79
2019-12-30 09:30 | 165.24 | 149.04
2019-12-30 10:00 | 166.18 | 150.2
2019-12-30 10:30 | 166.55 | 151.26
2019-12-30 11:00 | 165.83 | 151.21
2019-12-30 11:30 | 166.45 | 153.29
2019-12-30 12:00 | 170.07 | 156.31
2019-12-30 12:30 | 171.21 | 157.47
2019-12-30 13:00 | 171.78 | 158.74
2019-12-30 13:30 | 174.8 | 161.57
2019-12-30 14:00 | 176.37 | 163.08
2019-12-30 14:30 | 176.42 | 163.89
2019-12-30 15:00 | 179.76 | 166.56
2019-12-30 15:30 | 182.89 | 167.67
2019-12-30 16:00 | 182.73 | 167.87
2019-12-30 16:30 | 185.31 | 171.09
2019-12-30 17:00 | 201.95 | 188.69
2019-12-30 17:30 | 212.71 | 198.79
2019-12-30 18:00 | 212.2 | 200.73
2019-12-30 18:30 | 213.04 | 201.63
2019-12-30 19:00 | 213.45 | 202.51
2019-12-30 19:30 | 212.87 | 201.78
2019-12-30 20:00 | 211.52 | 200.34
2019-12-30 20:30 | 209.41 | 197.84
2019-12-30 21:00 | 206.63 | 194.43
2019-12-30 21:30 | 204.05 | 192.32
2019-12-30 22:00 | 200.94 | 189.3
2019-12-30 22:30 | 198.36 | 186.54
2019-12-30 23:00 | 173.77 | 161.52
2019-12-30 23:30 | 168.18 | 156.34
2019-12-31 | 166.02 | 154.63
2019-12-31 00:30 | 164.16 | 153.71
2019-12-31 01:00 | 162.39 | 152.33
2019-12-31 01:30 | 162.33 | 151.92
2019-12-31 02:00 | 161.6 | 150.1
2019-12-31 02:30 | 161.26 | 149.55
2019-12-31 03:00 | 160.48 | 148.53
2019-12-31 03:30 | 159.71 | 147.68
2019-12-31 04:00 | 159.37 | 147.28
2019-12-31 04:30 | 159.65 | 147.54
2019-12-31 05:00 | 159.83 | 147.81
2019-12-31 05:30 | 158.84 | 146.73
2019-12-31 06:00 | 159.13 | 147.25
2019-12-31 06:30 | 159.74 | 148.71
2019-12-31 07:00 | 159.26 | 149.54
2019-12-31 07:30 | 160.67 | 150.65
2019-12-31 08:00 | 162.3 | 151.07
2019-12-31 08:30 | 163.16 | 151.96
2019-12-31 09:00 | 163.67 | 152.31
2019-12-31 09:30 | 165.09 | 153.02
2019-12-31 10:00 | 166.06 | 153.56
2019-12-31 10:30 | 168.17 | 155.58
2019-12-31 11:00 | 168.07 | 155.28
2019-12-31 11:30 | 170.32 | 157.36
2019-12-31 12:00 | 172.66 | 159.65
2019-12-31 12:30 | 175.03 | 161.99
2019-12-31 13:00 | 176.5 | 164.17
2019-12-31 13:30 | 177.68 | 165.83
2019-12-31 14:00 | 179.87 | 167.91
2019-12-31 14:30 | 182.54 | 170.93
2019-12-31 15:00 | 182.62 | 172.11
2019-12-31 15:30 | 183.02 | 173.32
2019-12-31 16:00 | 184.37 | 175.23
2019-12-31 16:30 | 187.09 | 177.77
2019-12-31 17:00 | 202.88 | 193.12
2019-12-31 17:30 | 212.97 | 202.94
2019-12-31 18:00 | 215.7 | 205.15
2019-12-31 18:30 | 216.63 | 205.55
2019-12-31 19:00 | 216.21 | 205.04
2019-12-31 19:30 | 214.6 | 204.07
2019-12-31 20:00 | 213.59 | 202.85
2019-12-31 20:30 | 189.73 | 178.73
2019-12-31 21:00 | 183.59 | 172.25
2019-12-31 21:30 | 181.45 | 170.16
2019-12-31 22:00 | 179.35 | 167.95
2019-12-31 22:30 | 177.6 | 165.6
2019-12-31 23:00 | 176.28 | 164.23
2019-12-31 23:30 | 174.3 | 162.79
2020-01-01 | 171.56 | 161.15
2020-01-01 00:30 | 169.85 | 159.77
2020-01-01 01:00 | 168.9 | 158.74
2020-01-01 01:30 | 168.44 | 157.5
2020-01-01 02:00 | 168 | 156.97
2020-01-01 02:30 | 166.81 | 155.96
2020-01-01 03:00 | 166.09 | 155.15
2020-01-01 03:30 | 165.53 | 154.51
2020-01-01 04:00 | 165.08 | 153.9
2020-01-01 04:30 | 164.83 | 153.55
2020-01-01 05:00 | 164.73 | 153.4
2020-01-01 05:30 | 164.55 | 153.08
2020-01-01 06:00 | 164.68 | 153.23
2020-01-01 06:30 | 164.16 | 153.13
2020-01-01 07:00 | 163.98 | 153.67
2020-01-01 07:30 | 164.12 | 153.08
2020-01-01 08:00 | 164.7 | 153.44
2020-01-01 08:30 | 165.37 | 153.45
2020-01-01 09:00 | 166.14 | 153.53
2020-01-01 09:30 | 167.65 | 155.34
2020-01-01 10:00 | 169.28 | 156.47
2020-01-01 10:30 | 170.94 | 157.8
2020-01-01 11:00 | 172.57 | 159.64
2020-01-01 11:30 | 175.2 | 161.76
2020-01-01 12:00 | 176.7 | 164.73
2020-01-01 12:30 | 178.17 | 167.06
2020-01-01 13:00 | 180.12 | 168.99
2020-01-01 13:30 | 181.51 | 170.84
2020-01-01 14:00 | 183.68 | 172.33
2020-01-01 14:30 | 185.69 | 174.31
2020-01-01 15:00 | 187.28 | 175.83
2020-01-01 15:30 | 189.61 | 178.16
2020-01-01 16:00 | 191.85 | 180.46
2020-01-01 16:30 | 194.68 | 183.36
2020-01-01 17:00 | 197.21 | 186.16
2020-01-01 17:30 | 199.05 | 188.04
2020-01-01 18:00 | 200.75 | 189.78
2020-01-01 18:30 | 201.2 | 189.94
2020-01-01 19:00 | 200.27 | 190.27
2020-01-01 19:30 | 199.17 | 189.18
2020-01-01 20:00 | 197.4 | 187.07
2020-01-01 20:30 | 194.49 | 183.9
2020-01-01 21:00 | 191.55 | 180.49
2020-01-01 21:30 | 187.66 | 176.84
2020-01-01 22:00 | 183.49 | 172.63
2020-01-01 22:30 | 180.26 | 169.18
2020-01-01 23:00 | 177.86 | 166.53
2020-01-01 23:30 | 175.25 | 164.89
2020-01-02 | 172.88 | 162.79
2020-01-02 00:30 | 171.95 | 161.73
2020-01-02 01:00 | 170.24 | 160.36
2020-01-02 01:30 | 169.05 | 159
2020-01-02 02:00 | 167.47 | 157.8
2020-01-02 02:30 | 166.71 | 156.99
2020-01-02 03:00 | 166.33 | 156.4
2020-01-02 03:30 | 165.81 | 155.72
2020-01-02 04:00 | 165.52 | 155.34
2020-01-02 04:30 | 165.08 | 154.87
2020-01-02 05:00 | 165.18 | 154.82
2020-01-02 05:30 | 164.96 | 154.61
2020-01-02 06:00 | 164.79 | 154.53
2020-01-02 06:30 | 166.36 | 155.99
2020-01-02 07:00 | 167.87 | 156.71
2020-01-02 07:30 | 169.35 | 157.36
2020-01-02 08:00 | 170.61 | 157.68
2020-01-02 08:30 | 170.13 | 157.63
2020-01-02 09:00 | 167.35 | 156.27
2020-01-02 09:30 | 165.71 | 155.01
2020-01-02 10:00 | 165.91 | 155.21
2020-01-02 10:30 | 166.96 | 156.52
2020-01-02 11:00 | 169.21 | 158.94
2020-01-02 11:30 | 170.97 | 160.99
2020-01-02 12:00 | 172.61 | 163.07
2020-01-02 12:30 | 174.79 | 165.08
2020-01-02 13:00 | 176.74 | 167.19
2020-01-02 13:30 | 178.37 | 168.89
2020-01-02 14:00 | 180.58 | 171.21
2020-01-02 14:30 | 205.51 | 195.99
2020-01-02 15:00 | 214.06 | 204.61
2020-01-02 15:30 | 215.93 | 206.52
2020-01-02 16:00 | 216.92 | 207.55
2020-01-02 16:30 | 215.57 | 205.83
2020-01-02 17:00 | 218.01 | 208.61
2020-01-02 17:30 | 219.09 | 209.6
2020-01-02 18:00 | 220.7 | 211.26
2020-01-02 18:30 | 221.27 | 211.7
2020-01-02 19:00 | 222.43 | 212.56
2020-01-02 19:30 | 194.62 | 184.34
2020-01-02 20:00 | 186.89 | 175.12
2020-01-02 20:30 | 186.35 | 174.81
2020-01-02 21:00 | 182.42 | 170.68
2020-01-02 21:30 | 204.19 | 191.96
2020-01-02 22:00 | 208.2 | 196.53
2020-01-02 22:30 | 201.29 | 190.41
2020-01-02 23:00 | 201.21 | 194.65
2020-01-02 23:30 | 213.97 | 209.98
2020-01-03 | 210.92 | 206.83
2020-01-03 00:30 | 209.08 | 204.86
2020-01-03 01:00 | 208.12 | 203.91
2020-01-03 01:30 | 207.1 | 202.92
2020-01-03 02:00 | 206.57 | 202.39
2020-01-03 02:30 | 205.47 | 201.3
2020-01-03 03:00 | 205.13 | 200.95
2020-01-03 03:30 | 204.34 | 200.12
2020-01-03 04:00 | 203.72 | 199.49
2020-01-03 04:30 | 203.61 | 199.37
2020-01-03 05:00 | 203.64 | 199.44
2020-01-03 05:30 | 204.08 | 199.98
2020-01-03 06:00 | 203.78 | 199.71
2020-01-03 06:30 | 203.69 | 199.59
2020-01-03 07:00 | 205.07 | 201.03
2020-01-03 07:30 | 206.17 | 202.1
2020-01-03 08:00 | 206.92 | 202.94
2020-01-03 08:30 | 207.74 | 203.77
2020-01-03 09:00 | 208.77 | 204.59
2020-01-03 09:30 | 209.39 | 205.12
2020-01-03 10:00 | 211.13 | 206.83
2020-01-03 10:30 | 212.34 | 208.08
2020-01-03 11:00 | 213.84 | 209.67
2020-01-03 11:30 | 214.81 | 210.74
2020-01-03 12:00 | 217.8 | 213.73
2020-01-03 12:30 | 219.82 | 215.74
2020-01-03 13:00 | 221.26 | 217.31
2020-01-03 13:30 | 223.14 | 219.32
2020-01-03 14:00 | 225.41 | 221.59
2020-01-03 14:30 | 199.24 | 192.95
2020-01-03 15:00 | 199.94 | 191.76
2020-01-03 15:30 | 210.68 | 201.68
2020-01-03 16:00 | 211.63 | 202.97
2020-01-03 16:30 | 214.06 | 205.38
2020-01-03 17:00 | 215.43 | 206.7
2020-01-03 17:30 | 216.49 | 207.41
2020-01-03 18:00 | 217.41 | 208.64
2020-01-03 18:30 | 217 | 209.5
2020-01-03 19:00 | 217.29 | 209.81
2020-01-03 19:30 | 216.93 | 209.52
2020-01-03 20:00 | 215.94 | 208.53
2020-01-03 20:30 | 213.9 | 206.25
2020-01-03 21:00 | 210.43 | 202.47
2020-01-03 21:30 | 207.84 | 199.51
2020-01-03 22:00 | 204.35 | 196.11
2020-01-03 22:30 | 201.24 | 192.85
2020-01-03 23:00 | 198.72 | 190.01
2020-01-03 23:30 | 199.42 | 193.56
2020-01-04 | 211.66 | 207.51
2020-01-04 00:30 | 209.98 | 205.81
2020-01-04 01:00 | 208.39 | 204.2
2020-01-04 01:30 | 207.41 | 203.16
2020-01-04 02:00 | 206.32 | 202.1
2020-01-04 02:30 | 205.52 | 201.28
2020-01-04 03:00 | 205.22 | 200.94
2020-01-04 03:30 | 204.41 | 200.09
2020-01-04 04:00 | 203.71 | 199.37
2020-01-04 04:30 | 203.24 | 198.89
2020-01-04 05:00 | 202.81 | 198.5
2020-01-04 05:30 | 202.59 | 198.27
2020-01-04 06:00 | 201.1 | 196.84
2020-01-04 06:30 | 201.31 | 197.09
2020-01-04 07:00 | 201.91 | 197.74
2020-01-04 07:30 | 202.26 | 198.07
2020-01-04 08:00 | 202.23 | 198
2020-01-04 08:30 | 203.51 | 199.31
2020-01-04 09:00 | 205.17 | 200.86
2020-01-04 09:30 | 190.06 | 183.19
2020-01-04 10:00 | 180.59 | 171.62
2020-01-04 10:30 | 190.55 | 181.14
2020-01-04 11:00 | 193.32 | 183.37
2020-01-04 11:30 | 194.07 | 184.46
2020-01-04 12:00 | 195.42 | 186.16
2020-01-04 12:30 | 196.93 | 187.49
2020-01-04 13:00 | 198.01 | 188.4
2020-01-04 13:30 | 197.2 | 187.19
2020-01-04 14:00 | 199.03 | 189.08
2020-01-04 14:30 | 200.6 | 190.86
2020-01-04 15:00 | 201.32 | 192.14
2020-01-04 15:30 | 202.44 | 194.19
2020-01-04 16:00 | 204.77 | 196.86
2020-01-04 16:30 | 206.87 | 198.37
2020-01-04 17:00 | 211.12 | 202.84
2020-01-04 17:30 | 213.66 | 205.46
2020-01-04 18:00 | 216.48 | 207.93
2020-01-04 18:30 | 217.81 | 208.92
2020-01-04 19:00 | 217.37 | 209.14
2020-01-04 19:30 | 215.37 | 208.53
2020-01-04 20:00 | 214.77 | 207.82
2020-01-04 20:30 | 212.39 | 205.17
2020-01-04 21:00 | 209.46 | 201.28
2020-01-04 21:30 | 206.4 | 197.42
2020-01-04 22:00 | 201.71 | 192.64
2020-01-04 22:30 | 179.13 | 170.57
2020-01-04 23:00 | 206.54 | 201.72
2020-01-04 23:30 | 212.4 | 208.26
2020-01-05 | 210.15 | 205.96
2020-01-05 00:30 | 208.51 | 204.32
2020-01-05 01:00 | 205.97 | 202.03
2020-01-05 01:30 | 204.11 | 200.01
2020-01-05 02:00 | 203.31 | 199.16
2020-01-05 02:30 | 202.45 | 198.22
2020-01-05 03:00 | 201.91 | 197.68
2020-01-05 03:30 | 201 | 196.82
2020-01-05 04:00 | 200.11 | 195.91
2020-01-05 04:30 | 199.58 | 195.35
2020-01-05 05:00 | 199.38 | 195.17
2020-01-05 05:30 | 199.22 | 195.01
2020-01-05 06:00 | 198.81 | 194.56
2020-01-05 06:30 | 199 | 194.74
2020-01-05 07:00 | 199.41 | 195.08
2020-01-05 07:30 | 198.83 | 194.59
2020-01-05 08:00 | 198.76 | 194.48
2020-01-05 08:30 | 199 | 194.69
2020-01-05 09:00 | 199.22 | 194.9
2020-01-05 09:30 | 199.45 | 195.39
2020-01-05 10:00 | 200.41 | 196.48
2020-01-05 10:30 | 201.7 | 197.64
2020-01-05 11:00 | 203.55 | 199.54
2020-01-05 11:30 | 207.09 | 202.98
2020-01-05 12:00 | 209.83 | 205.75
2020-01-05 12:30 | 212.01 | 207.96
2020-01-05 13:00 | 214.05 | 210.08
2020-01-05 13:30 | 216.06 | 212.11
2020-01-05 14:00 | 217.51 | 213.6
2020-01-05 14:30 | 219.24 | 215.45
2020-01-05 15:00 | 220.47 | 216.76
2020-01-05 15:30 | 222.12 | 218.51
2020-01-05 16:00 | 224.92 | 221.25
2020-01-05 16:30 | 221.25 | 216.51
2020-01-05 17:00 | 198.97 | 191.3
2020-01-05 17:30 | 215.7 | 208.23
2020-01-05 18:00 | 219.3 | 211.99
2020-01-05 18:30 | 220.13 | 212.98
2020-01-05 19:00 | 220.24 | 213.43
2020-01-05 19:30 | 219.86 | 213.07
2020-01-05 20:00 | 217.76 | 211.82
2020-01-05 20:30 | 213.21 | 207.08
2020-01-05 21:00 | 187.67 | 181.18
2020-01-05 21:30 | 213.32 | 209.02
2020-01-05 22:00 | 217.8 | 213.96
2020-01-05 22:30 | 214.24 | 210.32
2020-01-05 23:00 | 211.72 | 207.68
2020-01-05 23:30 | 210.28 | 206.23
2020-01-06 | 208.52 | 204.44
2020-01-06 00:30 | 207.39 | 203.29
2020-01-06 01:00 | 205.76 | 201.7
2020-01-06 01:30 | 204.75 | 200.71
2020-01-06 02:00 | 203.72 | 199.7
2020-01-06 02:30 | 203.09 | 199.07
2020-01-06 03:00 | 202.37 | 198.34
2020-01-06 03:30 | 201.82 | 197.79
2020-01-06 04:00 | 201.61 | 197.6
2020-01-06 04:30 | 201.49 | 197.5
2020-01-06 05:00 | 201.04 | 196.99
2020-01-06 05:30 | 200.62 | 196.61
2020-01-06 06:00 | 200.81 | 196.77
2020-01-06 06:30 | 202.48 | 198.45
2020-01-06 07:00 | 204.11 | 200.17
2020-01-06 07:30 | 204.53 | 200.8
2020-01-06 08:00 | 205.72 | 201.98
2020-01-06 08:30 | 206.43 | 202.7
2020-01-06 09:00 | 207.6 | 203.76
2020-01-06 09:30 | 184.68 | 180.81
2020-01-06 10:00 | 155.95 | 152.34
2020-01-06 10:30 | 156.63 | 153.03
2020-01-06 11:00 | 157.92 | 154.35
2020-01-06 11:30 | 159.56 | 155.98
2020-01-06 12:00 | 161.68 | 158.1
2020-01-06 12:30 | 163.95 | 160.25
2020-01-06 13:00 | 174.15 | 170.02
2020-01-06 13:30 | 233.87 | 229.6
2020-01-06 14:00 | 247.03 | 242.84
2020-01-06 14:30 | 248.88 | 244.76
2020-01-06 15:00 | 251.11 | 247.03
2020-01-06 15:30 | 253.11 | 248.99
2020-01-06 16:00 | 255.21 | 251.13
2020-01-06 16:30 | 257.72 | 253.94
2020-01-06 17:00 | 259.37 | 255.65
2020-01-06 17:30 | 260.71 | 256.93
2020-01-06 18:00 | 234.47 | 231.13
2020-01-06 18:30 | 223.7 | 220.62
2020-01-06 19:00 | 224.32 | 221.06
2020-01-06 19:30 | 224.23 | 220.85
2020-01-06 20:00 | 222.6 | 219.01
2020-01-06 20:30 | 220.05 | 216.27
2020-01-06 21:00 | 215.1 | 211.56
2020-01-06 21:30 | 211.66 | 208.19
2020-01-06 22:00 | 208.14 | 204.36
2020-01-06 22:30 | 205.06 | 200.98
2020-01-06 23:00 | 203.17 | 199.18
2020-01-06 23:30 | 170.31 | 166.63
2020-01-07 | 158.48 | 154.76
2020-01-07 00:30 | 157.2 | 153.49
2020-01-07 01:00 | 156.12 | 152.35
2020-01-07 01:30 | 154.95 | 151.19
2020-01-07 02:00 | 154.01 | 150.32
2020-01-07 02:30 | 153.11 | 149.36
2020-01-07 03:00 | 152.96 | 149.07
2020-01-07 03:30 | 152.62 | 148.7
2020-01-07 04:00 | 152.29 | 148.3
2020-01-07 04:30 | 152.44 | 148.4
2020-01-07 05:00 | 152.63 | 148.54
2020-01-07 05:30 | 153.28 | 149.28
2020-01-07 06:00 | 153.99 | 150.02
2020-01-07 06:30 | 168.79 | 165.15
2020-01-07 07:00 | 193.83 | 190.25
2020-01-07 07:30 | 194.56 | 191.28
2020-01-07 08:00 | 194.53 | 191.41
2020-01-07 08:30 | 195.23 | 192.15
2020-01-07 09:00 | 194.9 | 191.67
2020-01-07 09:30 | 168.07 | 164.64
2020-01-07 10:00 | 157.68 | 154.14
2020-01-07 10:30 | 174.04 | 170.85
2020-01-07 11:00 | 194.77 | 191.62
2020-01-07 11:30 | 199.49 | 196.32
2020-01-07 12:00 | 200.3 | 197.22
2020-01-07 12:30 | 201.57 | 198.55
2020-01-07 13:00 | 203.8 | 200.83
2020-01-07 13:30 | 205.95 | 203.01
2020-01-07 14:00 | 207.81 | 204.97
2020-01-07 14:30 | 208.98 | 206.11
2020-01-07 15:00 | 210.62 | 207.79
2020-01-07 15:30 | 211.76 | 208.85
2020-01-07 16:00 | 213.15 | 210.21
2020-01-07 16:30 | 214.28 | 211.35
2020-01-07 17:00 | 215.36 | 212.46
2020-01-07 17:30 | 216.36 | 213.47
2020-01-07 18:00 | 217.89 | 215.03
2020-01-07 18:30 | 219.09 | 216.26
2020-01-07 19:00 | 219.44 | 216.58
2020-01-07 19:30 | 218.9 | 216.01
2020-01-07 20:00 | 217.62 | 214.79
2020-01-07 20:30 | 215.3 | 212.28
2020-01-07 21:00 | 211.98 | 208.72
2020-01-07 21:30 | 209.11 | 205.88
2020-01-07 22:00 | 205.69 | 202.41
2020-01-07 22:30 | 202.42 | 199.15
2020-01-07 23:00 | 200.26 | 196.92
2020-01-07 23:30 | 198.49 | 195.25
2020-01-08 | 196.28 | 193.02
2020-01-08 00:30 | 195.27 | 192.03
2020-01-08 01:00 | 193.64 | 190.3
2020-01-08 01:30 | 166.29 | 162.24
2020-01-08 02:00 | 153.13 | 149.27
2020-01-08 02:30 | 152.57 | 148.68
2020-01-08 03:00 | 152.16 | 148.31
2020-01-08 03:30 | 152.07 | 148.23
2020-01-08 04:00 | 151.85 | 147.98
2020-01-08 04:30 | 151.75 | 147.87
2020-01-08 05:00 | 151.39 | 147.52
2020-01-08 05:30 | 151.67 | 147.79
2020-01-08 06:00 | 152.04 | 148.2
2020-01-08 06:30 | 153.45 | 149.78
2020-01-08 07:00 | 154.81 | 151.14
2020-01-08 07:30 | 155.75 | 152.23
2020-01-08 08:00 | 155.97 | 152.49
2020-01-08 08:30 | 156.27 | 152.85
2020-01-08 09:00 | 156.81 | 153.4
2020-01-08 09:30 | 157.14 | 153.56
2020-01-08 10:00 | 158.51 | 154.79
2020-01-08 10:30 | 175.31 | 172.04
2020-01-08 11:00 | 195.05 | 192.14
2020-01-08 11:30 | 199.79 | 196.85
2020-01-08 12:00 | 201.43 | 198.44
2020-01-08 12:30 | 203.4 | 200.34
2020-01-08 13:00 | 205.5 | 202.54
2020-01-08 13:30 | 207.17 | 204.22
2020-01-08 14:00 | 209.28 | 206.45
2020-01-08 14:30 | 211.29 | 208.49
2020-01-08 15:00 | 212.48 | 209.66
2020-01-08 15:30 | 214.7 | 211.98
2020-01-08 16:00 | 216.24 | 213.73
2020-01-08 16:30 | 217.24 | 214.69
2020-01-08 17:00 | 247.65 | 245.01
2020-01-08 17:30 | 261.63 | 258.82
2020-01-08 18:00 | 264.51 | 261.69
2020-01-08 18:30 | 266.37 | 263.57
2020-01-08 19:00 | 267.41 | 264.61
2020-01-08 19:30 | 266.61 | 263.68
2020-01-08 20:00 | 265.05 | 261.98
2020-01-08 20:30 | 261.97 | 258.7
2020-01-08 21:00 | 254.55 | 250.9
2020-01-08 21:30 | 221.44 | 218
2020-01-08 22:00 | 176.46 | 173.02
2020-01-08 22:30 | 165.19 | 161.64
2020-01-08 23:00 | 162.84 | 159.01
2020-01-08 23:30 | 161.69 | 157.82
2020-01-09 | 159.45 | 155.58
2020-01-09 00:30 | 157.85 | 153.95
2020-01-09 01:00 | 156.29 | 152.34
2020-01-09 01:30 | 154.82 | 150.89
2020-01-09 02:00 | 154.35 | 150.4
2020-01-09 02:30 | 153.32 | 149.26
2020-01-09 03:00 | 152.79 | 148.6
2020-01-09 03:30 | 152.35 | 148.14
2020-01-09 04:00 | 152.02 | 147.81
2020-01-09 04:30 | 151.72 | 147.48
2020-01-09 05:00 | 153.34 | 148.98
2020-01-09 05:30 | 152.77 | 148.49
2020-01-09 06:00 | 151.75 | 147.6
2020-01-09 06:30 | 152.97 | 149.04
2020-01-09 07:00 | 153.7 | 150.02
2020-01-09 07:30 | 154.86 | 151.39
2020-01-09 08:00 | 165.75 | 162.38
2020-01-09 08:30 | 190.69 | 187.32
2020-01-09 09:00 | 221.93 | 218.55
2020-01-09 09:30 | 235.63 | 232.73
2020-01-09 10:00 | 236.71 | 234.19
2020-01-09 10:30 | 237.87 | 235.41
2020-01-09 11:00 | 239.97 | 237.57
2020-01-09 11:30 | 242.04 | 239.26
2020-01-09 12:00 | 243.92 | 241.12
2020-01-09 12:30 | 245.87 | 242.94
2020-01-09 13:00 | 248.46 | 245.66
2020-01-09 13:30 | 250.58 | 247.83
2020-01-09 14:00 | 252.99 | 250.29
2020-01-09 14:30 | 255.3 | 252.71
2020-01-09 15:00 | 255.99 | 253.56
2020-01-09 15:30 | 257.46 | 255.06
2020-01-09 16:00 | 260.24 | 257.8
2020-01-09 16:30 | 262.37 | 259.8
2020-01-09 17:00 | 262.12 | 259.59
2020-01-09 17:30 | 264.22 | 261.65
2020-01-09 18:00 | 267.93 | 265.62
2020-01-09 18:30 | 268.74 | 266.84
2020-01-09 19:00 | 269.24 | 267.19
2020-01-09 19:30 | 270.05 | 268.03
2020-01-09 20:00 | 268.74 | 266.43
2020-01-09 20:30 | 235.23 | 232.75
2020-01-09 21:00 | 188.72 | 186.11
2020-01-09 21:30 | 179.12 | 176.42
2020-01-09 22:00 | 174.95 | 171.91
2020-01-09 22:30 | 171.66 | 168.31
2020-01-09 23:00 | 168.88 | 165.38
2020-01-09 23:30 | 166.98 | 163.34
2020-01-10 | 164.85 | 161.07
2020-01-10 00:30 | 163.56 | 159.61
2020-01-10 01:00 | 162.4 | 158.27
2020-01-10 01:30 | 161.43 | 156.66
2020-01-10 02:00 | 160.5 | 155.57
2020-01-10 02:30 | 159.6 | 154.58
2020-01-10 03:00 | 158.84 | 153.75
2020-01-10 03:30 | 158.5 | 153.39
2020-01-10 04:00 | 158.04 | 152.89
2020-01-10 04:30 | 157.87 | 152.71
2020-01-10 05:00 | 157.53 | 152.33
2020-01-10 05:30 | 157.88 | 152.72
2020-01-10 06:00 | 157.83 | 152.7
2020-01-10 06:30 | 158.54 | 153.59
2020-01-10 07:00 | 159.6 | 154.71
2020-01-10 07:30 | 160.35 | 155.59
2020-01-10 08:00 | 160.46 | 155.81
2020-01-10 08:30 | 159.87 | 155.28
2020-01-10 09:00 | 159.85 | 155.35
2020-01-10 09:30 | 160.24 | 155.51
2020-01-10 10:00 | 179.85 | 175.83
2020-01-10 10:30 | 197.52 | 193.5
2020-01-10 11:00 | 198.45 | 195.26
2020-01-10 11:30 | 199.83 | 196.7
2020-01-10 12:00 | 201.87 | 198.71
2020-01-10 12:30 | 202.63 | 199.52
2020-01-10 13:00 | 205.05 | 201.99
2020-01-10 13:30 | 206.87 | 203.86
2020-01-10 14:00 | 208.85 | 205.92
2020-01-10 14:30 | 209.89 | 206.98
2020-01-10 15:00 | 212.3 | 209.46
2020-01-10 15:30 | 214.42 | 211.73
2020-01-10 16:00 | 217.29 | 214.66
2020-01-10 16:30 | 219.28 | 216.77
2020-01-10 17:00 | 221.07 | 218.73
2020-01-10 17:30 | 221.4 | 219.2
2020-01-10 18:00 | 248.98 | 247.07
2020-01-10 18:30 | 264.02 | 261.98
2020-01-10 19:00 | 264 | 261.83
2020-01-10 19:30 | 262.77 | 260.49
2020-01-10 20:00 | 261.63 | 259.31
2020-01-10 20:30 | 259 | 256.49
2020-01-10 21:00 | 254.5 | 251.61
2020-01-10 21:30 | 250.68 | 247.72
2020-01-10 22:00 | 245.91 | 242.77
2020-01-10 22:30 | 241.88 | 238.52
2020-01-10 23:00 | 239.08 | 235.35
2020-01-10 23:30 | 207.6 | 203.96
2020-01-11 | 174.59 | 171.19
2020-01-11 00:30 | 172.53 | 169.13
2020-01-11 01:00 | 170.97 | 167.52
2020-01-11 01:30 | 170.13 | 166.66
2020-01-11 02:00 | 170.02 | 166.38
2020-01-11 02:30 | 169.26 | 165.58
2020-01-11 03:00 | 168.78 | 165.09
2020-01-11 03:30 | 168.21 | 164.53
2020-01-11 04:00 | 168.43 | 164.27
2020-01-11 04:30 | 170.45 | 163.71
2020-01-11 05:00 | 171.21 | 164.83
2020-01-11 05:30 | 178.26 | 174.68
2020-01-11 06:00 | 180.51 | 176.83
2020-01-11 06:30 | 182.42 | 178.7
2020-01-11 07:00 | 183.37 | 179.71
2020-01-11 07:30 | 184.96 | 181.28
2020-01-11 08:00 | 185.83 | 182.25
2020-01-11 08:30 | 185.69 | 182.22
2020-01-11 09:00 | 187.28 | 183.97
2020-01-11 09:30 | 188.25 | 184.88
2020-01-11 10:00 | 189.33 | 185.89
2020-01-11 10:30 | 189.82 | 186.31
2020-01-11 11:00 | 189.95 | 186.44
2020-01-11 11:30 | 192.02 | 188.57
2020-01-11 12:00 | 194.6 | 191.08
2020-01-11 12:30 | 197.25 | 193.65
2020-01-11 13:00 | 200.24 | 196.6
2020-01-11 13:30 | 204.2 | 200.74
2020-01-11 14:00 | 207.38 | 203.86
2020-01-11 14:30 | 208.76 | 205.21
2020-01-11 15:00 | 213.03 | 209.36
2020-01-11 15:30 | 216.04 | 212.4
2020-01-11 16:00 | 216.79 | 213.13
2020-01-11 16:30 | 203.07 | 199.06
2020-01-11 17:00 | 212.42 | 208.16
2020-01-11 17:30 | 223 | 218.83
2020-01-11 18:00 | 211.21 | 206.67
2020-01-11 18:30 | 217.36 | 213.21
2020-01-11 19:00 | 225.85 | 221.61
2020-01-11 19:30 | 225.47 | 221.21
2020-01-11 20:00 | 223.5 | 219.25
2020-01-11 20:30 | 221.43 | 217.02
2020-01-11 21:00 | 219.12 | 214.38
2020-01-11 21:30 | 218.29 | 213.37
2020-01-11 22:00 | 215.48 | 210.45
2020-01-11 22:30 | 211.4 | 207.72
2020-01-11 23:00 | 210.08 | 206.77
2020-01-11 23:30 | 208.94 | 205.55
2020-01-12 | 207.58 | 204.02
2020-01-12 00:30 | 207.35 | 203.65
2020-01-12 01:00 | 205.96 | 202.23
2020-01-12 01:30 | 205.02 | 201.3
2020-01-12 02:00 | 203.97 | 200.25
2020-01-12 02:30 | 202.93 | 199.24
2020-01-12 03:00 | 202.3 | 198.6
2020-01-12 03:30 | 201.18 | 197.49
2020-01-12 04:00 | 200 | 196.35
2020-01-12 04:30 | 199.49 | 195.86
2020-01-12 05:00 | 199.34 | 195.72
2020-01-12 05:30 | 198.91 | 195.31
2020-01-12 06:00 | 198.37 | 194.72
2020-01-12 06:30 | 198.29 | 194.64
2020-01-12 07:00 | 198.72 | 195.01
2020-01-12 07:30 | 198.73 | 195.1
2020-01-12 08:00 | 198.23 | 194.72
2020-01-12 08:30 | 198.6 | 195.04
2020-01-12 09:00 | 198.78 | 195.24
2020-01-12 09:30 | 199.71 | 196.2
2020-01-12 10:00 | 200.88 | 197.32
2020-01-12 10:30 | 201.9 | 198.28
2020-01-12 11:00 | 204.02 | 200.32
2020-01-12 11:30 | 206.1 | 202.46
2020-01-12 12:00 | 209.04 | 205.44
2020-01-12 12:30 | 211.38 | 207.77
2020-01-12 13:00 | 214.52 | 210.9
2020-01-12 13:30 | 216.82 | 213.21
2020-01-12 14:00 | 219.45 | 215.71
2020-01-12 14:30 | 221.64 | 217.93
2020-01-12 15:00 | 222.37 | 218.69
2020-01-12 15:30 | 222.72 | 219.11
2020-01-12 16:00 | 144.21 | 141.76
2020-01-12 16:30 | 144.66 | 141.91
2020-01-12 17:00 | 147.68 | 144.31
2020-01-12 17:30 | 158.67 | 156.06
2020-01-12 18:00 | 171.54 | 169.64
2020-01-12 18:30 | 182.41 | 180.83
2020-01-12 19:00 | 197.36 | 195.17
2020-01-12 19:30 | 205.77 | 203.29
2020-01-12 20:00 | 209.67 | 207.02
2020-01-12 20:30 | 218.84 | 215.75
2020-01-12 21:00 | 207.52 | 204.76
2020-01-12 21:30 | 190.88 | 188.47
2020-01-12 22:00 | 186.56 | 184.15
2020-01-12 22:30 | 183.41 | 180.87
2020-01-12 23:00 | 181.17 | 178.48
2020-01-12 23:30 | 179.97 | 177.29
2020-01-13 | 178.68 | 176.04
2020-01-13 00:30 | 177.44 | 174.8
2020-01-13 01:00 | 176.21 | 173.42
2020-01-13 01:30 | 175.13 | 172.28
2020-01-13 02:00 | 174.83 | 171.99
2020-01-13 02:30 | 173.96 | 171.14
2020-01-13 03:00 | 173.41 | 170.58
2020-01-13 03:30 | 172.72 | 169.89
2020-01-13 04:00 | 172.74 | 169.91
2020-01-13 04:30 | 173.24 | 170.42
2020-01-13 05:00 | 173.72 | 170.91
2020-01-13 05:30 | 173.85 | 171.07
2020-01-13 06:00 | 174.03 | 171.28
2020-01-13 06:30 | 175.51 | 172.91
2020-01-13 07:00 | 176.61 | 174.2
2020-01-13 07:30 | 177.68 | 175.35
2020-01-13 08:00 | 176.52 | 174.19
2020-01-13 08:30 | 176.41 | 174.11
2020-01-13 09:00 | 178.58 | 176.22
2020-01-13 09:30 | 180.3 | 177.77
2020-01-13 10:00 | 181.91 | 179.27
2020-01-13 10:30 | 188.18 | 185.31
2020-01-13 11:00 | 192.75 | 189.81
2020-01-13 11:30 | 196.77 | 193.68
2020-01-13 12:00 | 198.75 | 195.65
2020-01-13 12:30 | 201.86 | 198.62
2020-01-13 13:00 | 204.12 | 200.91
2020-01-13 13:30 | 205.83 | 202.81
2020-01-13 14:00 | 207.01 | 204.12
2020-01-13 14:30 | 201.78 | 199.4
2020-01-13 15:00 | 199.19 | 197.09
2020-01-13 15:30 | 199.6 | 197.6
2020-01-13 16:00 | 201.94 | 199.9
2020-01-13 16:30 | 208.14 | 205.68
2020-01-13 17:00 | 217.89 | 214.88
2020-01-13 17:30 | 218.23 | 215.25
2020-01-13 18:00 | 220.31 | 217.37
2020-01-13 18:30 | 221.73 | 218.82
2020-01-13 19:00 | 222.24 | 219.34
2020-01-13 19:30 | 221.79 | 218.87
2020-01-13 20:00 | 220.78 | 217.83
2020-01-13 20:30 | 217.63 | 214.57
2020-01-13 21:00 | 214.02 | 210.79
2020-01-13 21:30 | 211.52 | 208.19
2020-01-13 22:00 | 208.47 | 204.97
2020-01-13 22:30 | 205.05 | 201.46
2020-01-13 23:00 | 203.07 | 199.28
2020-01-13 23:30 | 201.39 | 197.63
2020-01-14 | 199.63 | 195.67
2020-01-14 00:30 | 198.47 | 194.62
2020-01-14 01:00 | 197.02 | 193.22
2020-01-14 01:30 | 196.12 | 192.29
2020-01-14 02:00 | 195.09 | 191.37
2020-01-14 02:30 | 194.1 | 190.34
2020-01-14 03:00 | 193.68 | 189.84
2020-01-14 03:30 | 192.8 | 188.94
2020-01-14 04:00 | 192.93 | 189.07
2020-01-14 04:30 | 192.98 | 189.12
2020-01-14 05:00 | 193.22 | 189.28
2020-01-14 05:30 | 193.54 | 189.61
2020-01-14 06:00 | 193.38 | 189.48
2020-01-14 06:30 | 194.63 | 190.9
2020-01-14 07:00 | 195.62 | 192
2020-01-14 07:30 | 196.84 | 193.42
2020-01-14 08:00 | 197.48 | 194.09
2020-01-14 08:30 | 198.42 | 195.05
2020-01-14 09:00 | 197.92 | 194.56
2020-01-14 09:30 | 197 | 193.55
2020-01-14 10:00 | 197.34 | 193.89
2020-01-14 10:30 | 198.37 | 195.08
2020-01-14 11:00 | 199.42 | 196.21
2020-01-14 11:30 | 201.07 | 197.88
2020-01-14 12:00 | 203.99 | 200.83
2020-01-14 12:30 | 206.3 | 203.16
2020-01-14 13:00 | 208 | 204.86
2020-01-14 13:30 | 210.92 | 207.83
2020-01-14 14:00 | 213.88 | 210.83
2020-01-14 14:30 | 215.63 | 212.65
2020-01-14 15:00 | 219.17 | 216.22
2020-01-14 15:30 | 225.17 | 222.11
2020-01-14 16:00 | 228.73 | 225.58
2020-01-14 16:30 | 231.87 | 228.37
2020-01-14 17:00 | 234.64 | 231.03
2020-01-14 17:30 | 231.57 | 228.24
2020-01-14 18:00 | 230.12 | 227.01
2020-01-14 18:30 | 231.65 | 228.64
2020-01-14 19:00 | 232.22 | 229.27
2020-01-14 19:30 | 231.85 | 228.88
2020-01-14 20:00 | 231.09 | 228.02
2020-01-14 20:30 | 226.02 | 222.83
2020-01-14 21:00 | 221.01 | 217.68
2020-01-14 21:30 | 218.49 | 215.12
2020-01-14 22:00 | 215.1 | 211.54
2020-01-14 22:30 | 212.9 | 209.21
2020-01-14 23:00 | 210.86 | 207.02
2020-01-14 23:30 | 211.23 | 207.23
2020-01-15 | 210.42 | 206.37
2020-01-15 00:30 | 209.09 | 205.05
2020-01-15 01:00 | 207.32 | 203.32
2020-01-15 01:30 | 206.76 | 202.81
2020-01-15 02:00 | 205.41 | 201.48
2020-01-15 02:30 | 204.69 | 200.76
2020-01-15 03:00 | 204.12 | 200.21
2020-01-15 03:30 | 203.73 | 199.79
2020-01-15 04:00 | 203.72 | 199.77
2020-01-15 04:30 | 203.5 | 199.59
2020-01-15 05:00 | 203.66 | 199.74
2020-01-15 05:30 | 204.01 | 200.16
2020-01-15 06:00 | 204.04 | 200.21
2020-01-15 06:30 | 206.49 | 202.57
2020-01-15 07:00 | 208.64 | 204.65
2020-01-15 07:30 | 211.35 | 207.38
2020-01-15 08:00 | 212.61 | 208.79
2020-01-15 08:30 | 212.46 | 208.74
2020-01-15 09:00 | 212.28 | 208.68
2020-01-15 09:30 | 212.55 | 208.95
2020-01-15 10:00 | 213.39 | 209.81
2020-01-15 10:30 | 214.45 | 210.89
2020-01-15 11:00 | 214.83 | 211.23
2020-01-15 11:30 | 216.17 | 212.57
2020-01-15 12:00 | 219.04 | 215.44
2020-01-15 12:30 | 221.56 | 217.81
2020-01-15 13:00 | 223.84 | 220.17
2020-01-15 13:30 | 226.59 | 223.07
2020-01-15 14:00 | 227.69 | 224.27
2020-01-15 14:30 | 226.7 | 223.1
2020-01-15 15:00 | 225.97 | 221.95
2020-01-15 15:30 | 228.91 | 225.07
2020-01-15 16:00 | 229.29 | 225.44
2020-01-15 16:30 | 229.92 | 225.92
2020-01-15 17:00 | 208.3 | 203.19
2020-01-15 17:30 | 192.59 | 185.52
2020-01-15 18:00 | 202.49 | 195.4
2020-01-15 18:30 | 203.07 | 195.89
2020-01-15 19:00 | 202.86 | 195.77
2020-01-15 19:30 | 202.76 | 195.6
2020-01-15 20:00 | 202.59 | 195.33
2020-01-15 20:30 | 197.73 | 190.29
2020-01-15 21:00 | 182.67 | 175.35
2020-01-15 21:30 | 212.23 | 207.26
2020-01-15 22:00 | 217.32 | 213.12
2020-01-15 22:30 | 214.58 | 210.35
2020-01-15 23:00 | 212.39 | 208.11
2020-01-15 23:30 | 211.13 | 206.88
2020-01-16 | 209.18 | 204.88
2020-01-16 00:30 | 208.11 | 203.86
2020-01-16 01:00 | 207.14 | 202.84
2020-01-16 01:30 | 206.54 | 202.17
2020-01-16 02:00 | 206.07 | 201.73
2020-01-16 02:30 | 205.26 | 200.94
2020-01-16 03:00 | 204.69 | 200.39
2020-01-16 03:30 | 204.15 | 199.89
2020-01-16 04:00 | 203.65 | 199.41
2020-01-16 04:30 | 203.85 | 199.62
2020-01-16 05:00 | 204.37 | 200.16
2020-01-16 05:30 | 205.23 | 201.04
2020-01-16 06:00 | 205.42 | 201.31
2020-01-16 06:30 | 206.7 | 202.56
2020-01-16 07:00 | 207.99 | 203.87
2020-01-16 07:30 | 209.21 | 205.27
2020-01-16 08:00 | 209.29 | 205.39
2020-01-16 08:30 | 209.28 | 205.39
2020-01-16 09:00 | 210.5 | 206.53
2020-01-16 09:30 | 211.07 | 207.08
2020-01-16 10:00 | 211.35 | 207.39
2020-01-16 10:30 | 211.84 | 207.95
2020-01-16 11:00 | 213.33 | 209.45
2020-01-16 11:30 | 215.44 | 211.73
2020-01-16 12:00 | 217.41 | 213.78
2020-01-16 12:30 | 217.14 | 213.37
2020-01-16 13:00 | 219.53 | 215.73
2020-01-16 13:30 | 220.66 | 217.07
2020-01-16 14:00 | 221.18 | 217.7
2020-01-16 14:30 | 225.22 | 221.65
2020-01-16 15:00 | 226.67 | 223.04
2020-01-16 15:30 | 227.99 | 224.34
2020-01-16 16:00 | 229.03 | 225.41
2020-01-16 16:30 | 227.27 | 223.79
2020-01-16 17:00 | 227.32 | 223.83
2020-01-16 17:30 | 223.36 | 219.78
2020-01-16 18:00 | 188.05 | 182.71
2020-01-16 18:30 | 191.77 | 185.43
2020-01-16 19:00 | 198.45 | 192.05
2020-01-16 19:30 | 197.42 | 190.87
2020-01-16 20:00 | 194.6 | 188.87
2020-01-16 20:30 | 192.7 | 186.73
2020-01-16 21:00 | 191.08 | 184.93
2020-01-16 21:30 | 170.8 | 165.08
2020-01-16 22:00 | 200.12 | 195.69
2020-01-16 22:30 | 206.72 | 202.04
2020-01-16 23:00 | 205.87 | 201.13
2020-01-16 23:30 | 204.19 | 199.36
2020-01-17 | 201.76 | 196.88
2020-01-17 00:30 | 200.87 | 195.93
2020-01-17 01:00 | 199.97 | 194.98
2020-01-17 01:30 | 199.29 | 194.21
2020-01-17 02:00 | 199.52 | 194.35
2020-01-17 02:30 | 199.73 | 194.5
2020-01-17 03:00 | 199.7 | 194.45
2020-01-17 03:30 | 199.21 | 193.84
2020-01-17 04:00 | 199.06 | 193.64
2020-01-17 04:30 | 199.15 | 193.74
2020-01-17 05:00 | 199.69 | 194.39
2020-01-17 05:30 | 199.88 | 194.75
2020-01-17 06:00 | 200.06 | 195.04
2020-01-17 06:30 | 200.75 | 195.91
2020-01-17 07:00 | 201.17 | 196.59
2020-01-17 07:30 | 202.26 | 198.04
2020-01-17 08:00 | 202.57 | 198.45
2020-01-17 08:30 | 202.83 | 198.85
2020-01-17 09:00 | 202.73 | 198.69
2020-01-17 09:30 | 202.36 | 198.25
2020-01-17 10:00 | 202.32 | 198.25
2020-01-17 10:30 | 198.61 | 194.96
2020-01-17 11:00 | 197.93 | 194.32
2020-01-17 11:30 | 197.77 | 194.14
2020-01-17 12:00 | 199.51 | 195.65
2020-01-17 12:30 | 202.76 | 198.6
2020-01-17 13:00 | 203.42 | 199.33
2020-01-17 13:30 | 202.98 | 198.9
2020-01-17 14:00 | 203.04 | 198.98
2020-01-17 14:30 | 204.26 | 200.17
2020-01-17 15:00 | 206.9 | 202.76
2020-01-17 15:30 | 208.26 | 204.15
2020-01-17 16:00 | 208.56 | 204.49
2020-01-17 16:30 | 209.03 | 204.98
2020-01-17 17:00 | 209.97 | 206.2
2020-01-17 17:30 | 210.09 | 206.25
2020-01-17 18:00 | 210.81 | 206.96
2020-01-17 18:30 | 211.16 | 207.25
2020-01-17 19:00 | 211.74 | 207.89
2020-01-17 19:30 | 212.03 | 208.21
2020-01-17 20:00 | 211.21 | 207.4
2020-01-17 20:30 | 209.9 | 206.01
2020-01-17 21:00 | 207.9 | 203.77
2020-01-17 21:30 | 206.65 | 202.3
2020-01-17 22:00 | 205.25 | 200.78
2020-01-17 22:30 | 203.55 | 198.96
2020-01-17 23:00 | 202.1 | 197.43
2020-01-17 23:30 | 201.63 | 196.94
2020-01-18 | 200.22 | 195.47
2020-01-18 00:30 | 199.63 | 194.88
2020-01-18 01:00 | 199 | 194.14
2020-01-18 01:30 | 198.39 | 193.47
2020-01-18 02:00 | 198.17 | 193.22
2020-01-18 02:30 | 197.73 | 192.78
2020-01-18 03:00 | 197.45 | 192.4
2020-01-18 03:30 | 197.21 | 192.12
2020-01-18 04:00 | 197.04 | 191.94
2020-01-18 04:30 | 196.89 | 191.74
2020-01-18 05:00 | 197.01 | 191.87
2020-01-18 05:30 | 197.64 | 192.51
2020-01-18 06:00 | 197.34 | 192.19
2020-01-18 06:30 | 197.56 | 192.53
2020-01-18 07:00 | 197.41 | 192.47
2020-01-18 07:30 | 197.74 | 192.94
2020-01-18 08:00 | 197.79 | 193.03
2020-01-18 08:30 | 197.54 | 192.85
2020-01-18 09:00 | 197.1 | 192.49
2020-01-18 09:30 | 198.15 | 192.55
2020-01-18 10:00 | 198.72 | 193.08
2020-01-18 10:30 | 198.31 | 192.74
2020-01-18 11:00 | 198.88 | 193.46
2020-01-18 11:30 | 199.11 | 193.83
2020-01-18 12:00 | 200.29 | 195.12
2020-01-18 12:30 | 201.3 | 196.21
2020-01-18 13:00 | 201.96 | 196.97
2020-01-18 13:30 | 203.7 | 198.72
2020-01-18 14:00 | 204.68 | 199.78
2020-01-18 14:30 | 204.08 | 199.25
2020-01-18 15:00 | 206.22 | 201.54
2020-01-18 15:30 | 206.52 | 201.98
2020-01-18 16:00 | 207.23 | 202.95
2020-01-18 16:30 | 208.53 | 204.47
2020-01-18 17:00 | 210.36 | 206.46
2020-01-18 17:30 | 211.99 | 208.34
2020-01-18 18:00 | 213.19 | 209.73
2020-01-18 18:30 | 214.2 | 210.83
2020-01-18 19:00 | 214.22 | 210.85
2020-01-18 19:30 | 214.3 | 210.94
2020-01-18 20:00 | 214 | 210.61
2020-01-18 20:30 | 212.38 | 208.8
2020-01-18 21:00 | 209.68 | 205.8
2020-01-18 21:30 | 208.76 | 204.7
2020-01-18 22:00 | 206.87 | 202.52
2020-01-18 22:30 | 205.39 | 200.81
2020-01-18 23:00 | 203.96 | 199.13
2020-01-18 23:30 | 203.16 | 198.22
2020-01-19 | 201.72 | 196.58
2020-01-19 00:30 | 201.25 | 196.05
2020-01-19 01:00 | 200.29 | 194.92
2020-01-19 01:30 | 199.9 | 194.4
2020-01-19 02:00 | 199.45 | 193.9
2020-01-19 02:30 | 199.15 | 193.54
2020-01-19 03:00 | 198.97 | 193.23
2020-01-19 03:30 | 198.64 | 192.84
2020-01-19 04:00 | 198.57 | 192.67
2020-01-19 04:30 | 198.3 | 192.36
2020-01-19 05:00 | 198.63 | 192.71
2020-01-19 05:30 | 198.25 | 192.31
2020-01-19 06:00 | 198.23 | 192.23
2020-01-19 06:30 | 197.91 | 191.9
2020-01-19 07:00 | 198.2 | 192.19
2020-01-19 07:30 | 197.99 | 192.12
2020-01-19 08:00 | 197.54 | 191.83
2020-01-19 08:30 | 197.29 | 191.73
2020-01-19 09:00 | 197.64 | 192.17
2020-01-19 09:30 | 198.14 | 192.81
2020-01-19 10:00 | 199.07 | 193.83
2020-01-19 10:30 | 200.15 | 195.01
2020-01-19 11:00 | 201.78 | 196.73
2020-01-19 11:30 | 204.1 | 199.25
2020-01-19 12:00 | 205.73 | 201.1
2020-01-19 12:30 | 208.29 | 203.76
2020-01-19 13:00 | 211.01 | 206.91
2020-01-19 13:30 | 212.56 | 208.68
2020-01-19 14:00 | 214.8 | 210.79
2020-01-19 14:30 | 184.66 | 179.66
2020-01-19 15:00 | 186.1 | 180.43
2020-01-19 15:30 | 196.16 | 190.77
2020-01-19 16:00 | 197.7 | 192.23
2020-01-19 16:30 | 198.31 | 193.24
2020-01-19 17:00 | 198.15 | 193.24
2020-01-19 17:30 | 199.57 | 194.66
2020-01-19 18:00 | 200.85 | 195.92
2020-01-19 18:30 | 202.31 | 197.64
2020-01-19 19:00 | 203.65 | 198.94
2020-01-19 19:30 | 203.59 | 198.59
2020-01-19 20:00 | 202.26 | 196.33
2020-01-19 20:30 | 200.7 | 194.52
2020-01-19 21:00 | 197.97 | 191.22
2020-01-19 21:30 | 192.05 | 185.2
2020-01-19 22:00 | 188.75 | 182.66
2020-01-19 22:30 | 185.38 | 178.79
2020-01-19 23:00 | 183.74 | 176.87
2020-01-19 23:30 | 170.12 | 163.64
2020-01-20 | 199 | 193.87
2020-01-20 00:30 | 206.9 | 201.9
2020-01-20 01:00 | 205.89 | 200.87
2020-01-20 01:30 | 205.14 | 200.07
2020-01-20 02:00 | 204.84 | 199.78
2020-01-20 02:30 | 204.68 | 199.49
2020-01-20 03:00 | 204.28 | 199.01
2020-01-20 03:30 | 204.19 | 198.89
2020-01-20 04:00 | 204.39 | 199.12
2020-01-20 04:30 | 204.62 | 199.36
2020-01-20 05:00 | 205.06 | 199.88
2020-01-20 05:30 | 205.86 | 200.79
2020-01-20 06:00 | 205.93 | 200.95
2020-01-20 06:30 | 207.37 | 202.4
2020-01-20 07:00 | 208.32 | 203.52
2020-01-20 07:30 | 209.14 | 204.64
2020-01-20 08:00 | 209.17 | 204.91
2020-01-20 08:30 | 209.41 | 205.16
2020-01-20 09:00 | 211.25 | 206.8
2020-01-20 09:30 | 176.67 | 171.32
2020-01-20 10:00 | 182.13 | 176.07
2020-01-20 10:30 | 190.59 | 184.66
2020-01-20 11:00 | 190.51 | 184.5
2020-01-20 11:30 | 196.01 | 190.64
2020-01-20 12:00 | 197.85 | 192.59
2020-01-20 12:30 | 197.41 | 193.1
2020-01-20 13:00 | 193.87 | 188.38
2020-01-20 13:30 | 192.79 | 186.91
2020-01-20 14:00 | 197.87 | 192.47
2020-01-20 14:30 | 198.77 | 193.78
2020-01-20 15:00 | 169.29 | 164.85
2020-01-20 15:30 | 172.1 | 167.58
2020-01-20 16:00 | 174.39 | 169.63
2020-01-20 16:30 | 179.78 | 176.55
2020-01-20 17:00 | 178.21 | 175.03
2020-01-20 17:30 | 177.17 | 173.85
2020-01-20 18:00 | 175.22 | 171.76
2020-01-20 18:30 | 174.57 | 171.04
2020-01-20 19:00 | 174.5 | 170.95
2020-01-20 19:30 | 175.21 | 171.67
2020-01-20 20:00 | 175.78 | 172.27
2020-01-20 20:30 | 173.91 | 168.28
2020-01-20 21:00 | 172.01 | 165.59
2020-01-20 21:30 | 195.72 | 188.89
2020-01-20 22:00 | 198.92 | 191.64
2020-01-20 22:30 | 196.21 | 188.46
2020-01-20 23:00 | 190.95 | 182.83
2020-01-20 23:30 | 172.75 | 164.8
2020-01-21 | 202.06 | 196.91
2020-01-21 00:30 | 207.76 | 203.03
2020-01-21 01:00 | 206.14 | 201.33
2020-01-21 01:30 | 204.38 | 199.5
2020-01-21 02:00 | 204.2 | 199.29
2020-01-21 02:30 | 202.98 | 198.06
2020-01-21 03:00 | 202.59 | 197.63
2020-01-21 03:30 | 202 | 196.94
2020-01-21 04:00 | 201.18 | 196.09
2020-01-21 04:30 | 201.08 | 195.96
2020-01-21 05:00 | 200.92 | 195.74
2020-01-21 05:30 | 201.25 | 196.1
2020-01-21 06:00 | 201.6 | 196.54
2020-01-21 06:30 | 202.42 | 197.55
2020-01-21 07:00 | 203.39 | 198.62
2020-01-21 07:30 | 203.81 | 199.26
2020-01-21 08:00 | 204.03 | 199.52
2020-01-21 08:30 | 205.06 | 200.58
2020-01-21 09:00 | 204.79 | 200.35
2020-01-21 09:30 | 200.65 | 196.51
2020-01-21 10:00 | 199.27 | 195.2
2020-01-21 10:30 | 207.32 | 202.91
2020-01-21 11:00 | 208.42 | 204.13
2020-01-21 11:30 | 209.77 | 205.61
2020-01-21 12:00 | 211.98 | 207.9
2020-01-21 12:30 | 213.55 | 209.46
2020-01-21 13:00 | 197.37 | 192.19
2020-01-21 13:30 | 189.63 | 182.37
2020-01-21 14:00 | 197.58 | 190.59
2020-01-21 14:30 | 199.57 | 192.75
2020-01-21 15:00 | 201.11 | 194.42
2020-01-21 15:30 | 202.91 | 196.61
2020-01-21 16:00 | 204.53 | 198.33
2020-01-21 16:30 | 206.57 | 200.43
2020-01-21 17:00 | 193.53 | 187.66
2020-01-21 17:30 | 178.6 | 172.78
2020-01-21 18:00 | 180.7 | 174.91
2020-01-21 18:30 | 182.17 | 176.34
2020-01-21 19:00 | 182.59 | 176.63
2020-01-21 19:30 | 181.49 | 175.54
2020-01-21 20:00 | 178.57 | 172.64
2020-01-21 20:30 | 175.09 | 169.07
2020-01-21 21:00 | 199.32 | 191.96
2020-01-21 21:30 | 202.35 | 194.21
2020-01-21 22:00 | 199.59 | 190.88
2020-01-21 22:30 | 194.84 | 185.9
2020-01-21 23:00 | 174.29 | 166.47
2020-01-21 23:30 | 198.03 | 192.94
2020-01-22 | 207.37 | 202.74
2020-01-22 00:30 | 206.42 | 201.66
2020-01-22 01:00 | 205.09 | 200.34
2020-01-22 01:30 | 204.1 | 199.26
2020-01-22 02:00 | 203.43 | 198.55
2020-01-22 02:30 | 202.9 | 197.99
2020-01-22 03:00 | 202.59 | 197.65
2020-01-22 03:30 | 202.25 | 197.26
2020-01-22 04:00 | 202.14 | 197.16
2020-01-22 04:30 | 202.29 | 197.36
2020-01-22 05:00 | 202.56 | 197.61
2020-01-22 05:30 | 203.52 | 198.66
2020-01-22 06:00 | 203.98 | 199.35
2020-01-22 06:30 | 204.88 | 200.51
2020-01-22 07:00 | 205.62 | 201.35
2020-01-22 07:30 | 207.42 | 203.3
2020-01-22 08:00 | 208.17 | 204.09
2020-01-22 08:30 | 209.41 | 205.53
2020-01-22 09:00 | 210.5 | 206.63
2020-01-22 09:30 | 211.86 | 207.98
2020-01-22 10:00 | 216.55 | 212.41
2020-01-22 10:30 | 207.97 | 204.17
2020-01-22 11:00 | 208.69 | 205.16
2020-01-22 11:30 | 209.83 | 206.44
2020-01-22 12:00 | 211.14 | 207.74
2020-01-22 12:30 | 213.65 | 210.15
2020-01-22 13:00 | 208.56 | 204.1
2020-01-22 13:30 | 198.53 | 192.12
2020-01-22 14:00 | 207.41 | 200.69
2020-01-22 14:30 | 198.17 | 191.85
2020-01-22 15:00 | 174.05 | 168.16
2020-01-22 15:30 | 175.16 | 169.15
2020-01-22 16:00 | 176.51 | 170.55
2020-01-22 16:30 | 176.25 | 170.23
2020-01-22 17:00 | 176.32 | 170.34
2020-01-22 17:30 | 176.8 | 170.74
2020-01-22 18:00 | 175.91 | 169.85
2020-01-22 18:30 | 176.3 | 170.13
2020-01-22 19:00 | 176.27 | 169.78
2020-01-22 19:30 | 175.77 | 169.2
2020-01-22 20:00 | 202.85 | 195.29
2020-01-22 20:30 | 208.1 | 200.6
2020-01-22 21:00 | 205.56 | 197.85
2020-01-22 21:30 | 186.5 | 178.76
2020-01-22 22:00 | 206.3 | 201.6
2020-01-22 22:30 | 213.83 | 210.25
2020-01-22 23:00 | 211.92 | 208.22
2020-01-22 23:30 | 211.1 | 207.31
2020-01-23 | 209.15 | 205.32
2020-01-23 00:30 | 208.15 | 204.24
2020-01-23 01:00 | 207.3 | 203.34
2020-01-23 01:30 | 206.93 | 202.95
2020-01-23 02:00 | 206.3 | 202.27
2020-01-23 02:30 | 205.78 | 201.71
2020-01-23 03:00 | 205.57 | 201.51
2020-01-23 03:30 | 205.24 | 201.17
2020-01-23 04:00 | 205.45 | 201.37
2020-01-23 04:30 | 205.89 | 201.84
2020-01-23 05:00 | 206.36 | 202.31
2020-01-23 05:30 | 207.04 | 203.09
2020-01-23 06:00 | 208.01 | 204.18
2020-01-23 06:30 | 209.48 | 205.71
2020-01-23 07:00 | 210.61 | 206.78
2020-01-23 07:30 | 212.25 | 208.53
2020-01-23 08:00 | 213.27 | 209.65
2020-01-23 08:30 | 213.78 | 210.21
2020-01-23 09:00 | 214.9 | 211.38
2020-01-23 09:30 | 213.57 | 209.9
2020-01-23 10:00 | 195.19 | 190.03
2020-01-23 10:30 | 174.48 | 167.86
2020-01-23 11:00 | 172.55 | 166.18
2020-01-23 11:30 | 174.33 | 168.45
2020-01-23 12:00 | 174.31 | 168.24
2020-01-23 12:30 | 193.03 | 186.83
2020-01-23 13:00 | 202.31 | 195.93
2020-01-23 13:30 | 203.63 | 197.57
2020-01-23 14:00 | 202.88 | 197.7
2020-01-23 14:30 | 203.94 | 198.95
2020-01-23 15:00 | 205.15 | 200.12
2020-01-23 15:30 | 207.73 | 202.75
2020-01-23 16:00 | 207.87 | 203.02
2020-01-23 16:30 | 183.92 | 179.2
2020-01-23 17:00 | 179.19 | 174.44
2020-01-23 17:30 | 180.45 | 175.51
2020-01-23 18:00 | 182.11 | 177.05
2020-01-23 18:30 | 184.15 | 179.14
2020-01-23 19:00 | 183.49 | 178.54
2020-01-23 19:30 | 183.89 | 178.84
2020-01-23 20:00 | 182.22 | 177.17
2020-01-23 20:30 | 179.69 | 174.55
2020-01-23 21:00 | 191.34 | 185.49
2020-01-23 21:30 | 188.29 | 182
2020-01-23 22:00 | 194.02 | 188.35
2020-01-23 22:30 | 219.5 | 215.97
2020-01-23 23:00 | 216.63 | 213.11
2020-01-23 23:30 | 215.03 | 211.46
2020-01-24 | 212.83 | 209.25
2020-01-24 00:30 | 211.2 | 207.54
2020-01-24 01:00 | 210.1 | 206.39
2020-01-24 01:30 | 208.85 | 205.12
2020-01-24 02:00 | 208.15 | 204.42
2020-01-24 02:30 | 206.71 | 203.03
2020-01-24 03:00 | 206.06 | 202.41
2020-01-24 03:30 | 205.34 | 201.63
2020-01-24 04:00 | 205.59 | 201.91
2020-01-24 04:30 | 205.65 | 201.97
2020-01-24 05:00 | 205.89 | 202.22
2020-01-24 05:30 | 206.66 | 203.05
2020-01-24 06:00 | 207.73 | 204.16
2020-01-24 06:30 | 209.43 | 205.78
2020-01-24 07:00 | 210.16 | 206.4
2020-01-24 07:30 | 212.13 | 208.45
2020-01-24 08:00 | 212.78 | 209.17
2020-01-24 08:30 | 211.94 | 208.46
2020-01-24 09:00 | 210.21 | 206.94
2020-01-24 09:30 | 207.87 | 204.64
2020-01-24 10:00 | 209.3 | 205.98
2020-01-24 10:30 | 211.23 | 207.88
2020-01-24 11:00 | 212.67 | 209.27
2020-01-24 11:30 | 213.27 | 209.84
2020-01-24 12:00 | 195.09 | 190.24
2020-01-24 12:30 | 191.84 | 185.1
2020-01-24 13:00 | 199.22 | 192.34
2020-01-24 13:30 | 198.43 | 191.41
2020-01-24 14:00 | 198.71 | 191.88
2020-01-24 14:30 | 199 | 192.34
2020-01-24 15:00 | 201.73 | 195.07
2020-01-24 15:30 | 202.45 | 196
2020-01-24 16:00 | 203.91 | 197.53
2020-01-24 16:30 | 204.42 | 197.9
2020-01-24 17:00 | 174.93 | 168.66
2020-01-24 17:30 | 170.39 | 164.09
2020-01-24 18:00 | 171.42 | 165.1
2020-01-24 18:30 | 171.14 | 164.88
2020-01-24 19:00 | 170.88 | 164.54
2020-01-24 19:30 | 170.36 | 163.99
2020-01-24 20:00 | 169.7 | 163.35
2020-01-24 20:30 | 167.85 | 161.38
2020-01-24 21:00 | 165.36 | 158.92
2020-01-24 21:30 | 192.68 | 185.06
2020-01-24 22:00 | 184.22 | 177.43
2020-01-24 22:30 | 200.42 | 195.83
2020-01-24 23:00 | 209.31 | 205.47
2020-01-24 23:30 | 208.21 | 204.36
2020-01-25 | 206.8 | 202.92
2020-01-25 00:30 | 205.36 | 201.36
2020-01-25 01:00 | 204.37 | 200.21
2020-01-25 01:30 | 203.24 | 199.06
2020-01-25 02:00 | 202.63 | 198.44
2020-01-25 02:30 | 202.02 | 197.9
2020-01-25 03:00 | 201.47 | 197.49
2020-01-25 03:30 | 201.04 | 197.04
2020-01-25 04:00 | 201.04 | 197.05
2020-01-25 04:30 | 200.89 | 196.89
2020-01-25 05:00 | 200.5 | 196.5
2020-01-25 05:30 | 200.98 | 197.01
2020-01-25 06:00 | 200.59 | 196.61
2020-01-25 06:30 | 200.46 | 196.53
2020-01-25 07:00 | 200.93 | 196.87
2020-01-25 07:30 | 180.4 | 174.59
2020-01-25 08:00 | 178.11 | 170.37
2020-01-25 08:30 | 184.89 | 177.09
2020-01-25 09:00 | 185.88 | 177.99
2020-01-25 09:30 | 187.55 | 179.03
2020-01-25 10:00 | 188.45 | 179.8
2020-01-25 10:30 | 188.83 | 180.22
2020-01-25 11:00 | 190.29 | 181.75
2020-01-25 11:30 | 191.64 | 183.24
2020-01-25 12:00 | 193.05 | 184.79
2020-01-25 12:30 | 194.43 | 186.38
2020-01-25 13:00 | 195.25 | 186.98
2020-01-25 13:30 | 197.52 | 189.01
2020-01-25 14:00 | 198.46 | 189.97
2020-01-25 14:30 | 199.46 | 191.07
2020-01-25 15:00 | 201.26 | 192.91
2020-01-25 15:30 | 202.43 | 194.23
2020-01-25 16:00 | 202.4 | 194.4
2020-01-25 16:30 | 203.84 | 195.97
2020-01-25 17:00 | 206.31 | 198.71
2020-01-25 17:30 | 207.89 | 200.62
2020-01-25 18:00 | 209.51 | 202.34
2020-01-25 18:30 | 210.2 | 202.96
2020-01-25 19:00 | 209.7 | 202.13
2020-01-25 19:30 | 207.34 | 199.36
2020-01-25 20:00 | 205.62 | 197.73
2020-01-25 20:30 | 203.48 | 195.31
2020-01-25 21:00 | 200.44 | 191.9
2020-01-25 21:30 | 198.71 | 190.31
2020-01-25 22:00 | 196.32 | 187.75
2020-01-25 22:30 | 194.31 | 185.28
2020-01-25 23:00 | 192.77 | 183.29
2020-01-25 23:30 | 190.92 | 182.27
2020-01-26 | 189.16 | 180.46
2020-01-26 00:30 | 188.49 | 179.73
2020-01-26 01:00 | 187.26 | 178.5
2020-01-26 01:30 | 186.28 | 177.84
2020-01-26 02:00 | 185.78 | 177.41
2020-01-26 02:30 | 185.46 | 176.96
2020-01-26 03:00 | 184.57 | 175.76
2020-01-26 03:30 | 184.54 | 175.71
2020-01-26 04:00 | 184.46 | 175.64
2020-01-26 04:30 | 184.5 | 175.72
2020-01-26 05:00 | 184.49 | 175.81
2020-01-26 05:30 | 184.67 | 175.99
2020-01-26 06:00 | 184.58 | 175.85
2020-01-26 06:30 | 184.13 | 175.67
2020-01-26 07:00 | 184.16 | 175.4
2020-01-26 07:30 | 183.96 | 175.54
2020-01-26 08:00 | 183.57 | 175.13
2020-01-26 08:30 | 182.52 | 173.96
2020-01-26 09:00 | 160.62 | 151.46
2020-01-26 09:30 | 187.88 | 182.44
2020-01-26 10:00 | 196.95 | 193.18
2020-01-26 10:30 | 196.65 | 193.05
2020-01-26 11:00 | 196.67 | 193.27
2020-01-26 11:30 | 198.1 | 194.64
2020-01-26 12:00 | 199.08 | 195.66
2020-01-26 12:30 | 200.37 | 196.98
2020-01-26 13:00 | 201.79 | 198.39
2020-01-26 13:30 | 203.12 | 199.74
2020-01-26 14:00 | 206.39 | 202.71
2020-01-26 14:30 | 209.44 | 205.65
2020-01-26 15:00 | 211.14 | 207.37
2020-01-26 15:30 | 212.89 | 209.13
2020-01-26 16:00 | 192.25 | 186.43
2020-01-26 16:30 | 190.78 | 182.91
2020-01-26 17:00 | 199.43 | 191.62
2020-01-26 17:30 | 201.7 | 193.78
2020-01-26 18:00 | 203.8 | 195.85
2020-01-26 18:30 | 204.66 | 196.61
2020-01-26 19:00 | 204.4 | 196.17
2020-01-26 19:30 | 204.33 | 196.16
2020-01-26 20:00 | 203.47 | 195.23
2020-01-26 20:30 | 201.84 | 193.44
2020-01-26 21:00 | 199.4 | 190.64
2020-01-26 21:30 | 177.11 | 169.05
2020-01-26 22:00 | 201.89 | 197.29
2020-01-26 22:30 | 209.53 | 206.01
2020-01-26 23:00 | 207.4 | 203.81
2020-01-26 23:30 | 206.27 | 202.64
2020-01-27 | 205.14 | 201.36
2020-01-27 00:30 | 204.18 | 200.27
2020-01-27 01:00 | 202.96 | 198.98
2020-01-27 01:30 | 201.95 | 197.94
2020-01-27 02:00 | 201.58 | 197.52
2020-01-27 02:30 | 201 | 196.95
2020-01-27 03:00 | 200.64 | 196.56
2020-01-27 03:30 | 199.91 | 195.82
2020-01-27 04:00 | 199.93 | 195.8
2020-01-27 04:30 | 199.41 | 195.32
2020-01-27 05:00 | 199.49 | 195.41
2020-01-27 05:30 | 199.87 | 195.79
2020-01-27 06:00 | 199.5 | 195.43
2020-01-27 06:30 | 199.56 | 195.52
2020-01-27 07:00 | 199.55 | 195.56
2020-01-27 07:30 | 199.57 | 195.72
2020-01-27 08:00 | 199.25 | 195.45
2020-01-27 08:30 | 199.63 | 195.82
2020-01-27 09:00 | 199.25 | 195.45
2020-01-27 09:30 | 199.25 | 195.43
2020-01-27 10:00 | 200.15 | 196.38
2020-01-27 10:30 | 199.72 | 195.86
2020-01-27 11:00 | 200.81 | 196.96
2020-01-27 11:30 | 203.72 | 199.89
2020-01-27 12:00 | 205.88 | 202.14
2020-01-27 12:30 | 207.32 | 203.59
2020-01-27 13:00 | 207.46 | 203.76
2020-01-27 13:30 | 208.6 | 204.92
2020-01-27 14:00 | 210.19 | 206.54
2020-01-27 14:30 | 211.85 | 208.11
2020-01-27 15:00 | 212.85 | 209.15
2020-01-27 15:30 | 212.94 | 209.29
2020-01-27 16:00 | 215.42 | 211.76
2020-01-27 16:30 | 216.55 | 213
2020-01-27 17:00 | 218.87 | 215.5
2020-01-27 17:30 | 220.08 | 216.72
2020-01-27 18:00 | 222.03 | 218.69
2020-01-27 18:30 | 222.69 | 219.39
2020-01-27 19:00 | 223.08 | 219.83
2020-01-27 19:30 | 222.64 | 219.39
2020-01-27 20:00 | 221.41 | 218.19
2020-01-27 20:30 | 218.68 | 215.42
2020-01-27 21:00 | 215.71 | 212.41
2020-01-27 21:30 | 213.45 | 210.04
2020-01-27 22:00 | 210.38 | 206.85
2020-01-27 22:30 | 207.48 | 203.8
2020-01-27 23:00 | 205.37 | 201.68
2020-01-27 23:30 | 204.5 | 200.79
2020-01-28 | 202.79 | 198.99
2020-01-28 00:30 | 201.88 | 198.07
2020-01-28 01:00 | 200.99 | 197.1
2020-01-28 01:30 | 200.59 | 196.61
2020-01-28 02:00 | 200.13 | 196.15
2020-01-28 02:30 | 199.42 | 195.46
2020-01-28 03:00 | 198.82 | 194.87
2020-01-28 03:30 | 198.3 | 194.35
2020-01-28 04:00 | 198.45 | 194.51
2020-01-28 04:30 | 198.39 | 194.49
2020-01-28 05:00 | 198.65 | 194.74
2020-01-28 05:30 | 199.63 | 195.78
2020-01-28 06:00 | 200.16 | 196.39
2020-01-28 06:30 | 201.67 | 197.98
2020-01-28 07:00 | 202.63 | 199.02
2020-01-28 07:30 | 204.3 | 200.78
2020-01-28 08:00 | 203.92 | 200.46
2020-01-28 08:30 | 203.48 | 200.01
2020-01-28 09:00 | 203.12 | 199.63
2020-01-28 09:30 | 203.45 | 199.99
2020-01-28 10:00 | 204.05 | 200.61
2020-01-28 10:30 | 206.16 | 202.68
2020-01-28 11:00 | 186.22 | 182.1
2020-01-28 11:30 | 184.74 | 179.59
2020-01-28 12:00 | 189.7 | 184.62
2020-01-28 12:30 | 190.51 | 185.58
2020-01-28 13:00 | 193.54 | 188.78
2020-01-28 13:30 | 197.79 | 193.21
2020-01-28 14:00 | 198.83 | 194.28
2020-01-28 14:30 | 200.47 | 195.92
2020-01-28 15:00 | 201.33 | 196.73
2020-01-28 15:30 | 200.94 | 196.25
2020-01-28 16:00 | 201.17 | 196.38
2020-01-28 16:30 | 202.76 | 197.89
2020-01-28 17:00 | 204.7 | 199.93
2020-01-28 17:30 | 206.18 | 201.13
2020-01-28 18:00 | 208.98 | 204.03
2020-01-28 18:30 | 210.06 | 204.97
2020-01-28 19:00 | 211.01 | 206.61
2020-01-28 19:30 | 209.67 | 205.67
2020-01-28 20:00 | 207.96 | 203.77
2020-01-28 20:30 | 186.35 | 182.13
2020-01-28 21:00 | 210.84 | 207.45
2020-01-28 21:30 | 217.41 | 214.1
2020-01-28 22:00 | 213.65 | 210.21
2020-01-28 22:30 | 210.44 | 206.86
2020-01-28 23:00 | 208.21 | 204.56
2020-01-28 23:30 | 206.98 | 203.3
2020-01-29 | 205.16 | 201.55
2020-01-29 00:30 | 204.19 | 200.5
2020-01-29 01:00 | 202.93 | 199.22
2020-01-29 01:30 | 201.66 | 197.94
2020-01-29 02:00 | 200.29 | 196.54
2020-01-29 02:30 | 199.37 | 195.48
2020-01-29 03:00 | 199.38 | 195.47
2020-01-29 03:30 | 198.47 | 194.54
2020-01-29 04:00 | 198.28 | 194.3
2020-01-29 04:30 | 198.11 | 194.17
2020-01-29 05:00 | 198.44 | 194.55
2020-01-29 05:30 | 199.61 | 195.78
2020-01-29 06:00 | 200.13 | 196.37
2020-01-29 06:30 | 202.32 | 198.69
2020-01-29 07:00 | 203.88 | 200.25
2020-01-29 07:30 | 205.3 | 201.86
2020-01-29 08:00 | 205.75 | 202.28
2020-01-29 08:30 | 206.79 | 203.27
2020-01-29 09:00 | 207.05 | 203.58
2020-01-29 09:30 | 206.41 | 203.07
2020-01-29 10:00 | 207.47 | 204.05
2020-01-29 10:30 | 208.91 | 205.57
2020-01-29 11:00 | 209.44 | 206.2
2020-01-29 11:30 | 178.56 | 175.54
2020-01-29 12:00 | 191.01 | 187.45
2020-01-29 12:30 | 194.98 | 190.92
2020-01-29 13:00 | 196 | 191.96
2020-01-29 13:30 | 198 | 194.06
2020-01-29 14:00 | 199.89 | 195.92
2020-01-29 14:30 | 201.18 | 197.21
2020-01-29 15:00 | 202.64 | 198.52
2020-01-29 15:30 | 203.18 | 199.11
2020-01-29 16:00 | 206.26 | 202.21
2020-01-29 16:30 | 185.84 | 182.14
2020-01-29 17:00 | 179.51 | 176.17
2020-01-29 17:30 | 180.55 | 177.11
2020-01-29 18:00 | 182.52 | 178.99
2020-01-29 18:30 | 183.97 | 180.39
2020-01-29 19:00 | 184.31 | 180.65
2020-01-29 19:30 | 184.34 | 180.69
2020-01-29 20:00 | 182.94 | 179.46
2020-01-29 20:30 | 207.88 | 203.94
2020-01-29 21:00 | 207.73 | 203.66
2020-01-29 21:30 | 213.31 | 209.98
2020-01-29 22:00 | 220.52 | 217.21
2020-01-29 22:30 | 216.98 | 213.47
2020-01-29 23:00 | 214.3 | 210.72
2020-01-29 23:30 | 212.49 | 208.88
2020-01-30 | 210.38 | 206.75
2020-01-30 00:30 | 208.79 | 205.14
2020-01-30 01:00 | 207.81 | 204.01
2020-01-30 01:30 | 206.7 | 202.91
2020-01-30 02:00 | 205.83 | 202.06
2020-01-30 02:30 | 204.58 | 200.84
2020-01-30 03:00 | 204.12 | 200.39
2020-01-30 03:30 | 203.73 | 199.99
2020-01-30 04:00 | 203.36 | 199.62
2020-01-30 04:30 | 203.62 | 199.9
2020-01-30 05:00 | 203.8 | 200.1
2020-01-30 05:30 | 204.45 | 200.77
2020-01-30 06:00 | 204.98 | 201.3
2020-01-30 06:30 | 206.89 | 203.15
2020-01-30 07:00 | 208.75 | 205.04
2020-01-30 07:30 | 210.23 | 206.84
2020-01-30 08:00 | 211.15 | 207.74
2020-01-30 08:30 | 211.14 | 207.85
2020-01-30 09:00 | 210.97 | 207.72
2020-01-30 09:30 | 210.73 | 207.52
2020-01-30 10:00 | 212.05 | 208.72
2020-01-30 10:30 | 213.8 | 210.55
2020-01-30 11:00 | 215.03 | 211.87
2020-01-30 11:30 | 217.47 | 214.28
2020-01-30 12:00 | 184.48 | 181.66
2020-01-30 12:30 | 195.24 | 192.02
2020-01-30 13:00 | 199.86 | 196.42
2020-01-30 13:30 | 201.12 | 198.11
2020-01-30 14:00 | 202.8 | 199.85
2020-01-30 14:30 | 204.59 | 201.73
2020-01-30 15:00 | 204.9 | 202.02
2020-01-30 15:30 | 205.94 | 203.2
2020-01-30 16:00 | 209.72 | 206.97
2020-01-30 16:30 | 176.83 | 174.76
2020-01-30 17:00 | 166.61 | 164.85
2020-01-30 17:30 | 166.28 | 164
2020-01-30 18:00 | 165.7 | 163.57
2020-01-30 18:30 | 165.63 | 163.3
2020-01-30 19:00 | 166.47 | 163.85
2020-01-30 19:30 | 167.12 | 164.58
2020-01-30 20:00 | 168.47 | 166.09
2020-01-30 20:30 | 170.87 | 168.34
2020-01-30 21:00 | 173.72 | 171.45
2020-01-30 21:30 | 198.16 | 194.89
2020-01-30 22:00 | 202.73 | 198.61
2020-01-30 22:30 | 198.67 | 194.69
2020-01-30 23:00 | 196.08 | 192.08
2020-01-30 23:30 | 194.58 | 190.57
2020-01-31 | 192.36 | 188.33
2020-01-31 00:30 | 170.1 | 165.78
2020-01-31 01:00 | 188.66 | 184.85
2020-01-31 01:30 | 206.61 | 202.94
2020-01-31 02:00 | 205.53 | 201.76
2020-01-31 02:30 | 204.27 | 200.57
2020-01-31 03:00 | 204.02 | 200.3
2020-01-31 03:30 | 203.37 | 199.64
2020-01-31 04:00 | 202.84 | 199.09
2020-01-31 04:30 | 202.72 | 198.97
2020-01-31 05:00 | 202.94 | 199.2
2020-01-31 05:30 | 203.57 | 199.87
2020-01-31 06:00 | 204.2 | 200.62
2020-01-31 06:30 | 206.23 | 202.62
2020-01-31 07:00 | 207.61 | 204.1
2020-01-31 07:30 | 209.37 | 205.87
2020-01-31 08:00 | 209.54 | 206.26
2020-01-31 08:30 | 208.88 | 205.64
2020-01-31 09:00 | 208.68 | 205.44
2020-01-31 09:30 | 208.53 | 205.26
2020-01-31 10:00 | 210.43 | 207.04
2020-01-31 10:30 | 182.06 | 178.66
2020-01-31 11:00 | 183.19 | 179.18
2020-01-31 11:30 | 192.14 | 188.03
2020-01-31 12:00 | 191.22 | 187.46
2020-01-31 12:30 | 182.49 | 178.9
2020-01-31 13:00 | 181.36 | 177.77
2020-01-31 13:30 | 182.2 | 178.75
2020-01-31 14:00 | 186.11 | 182.76
2020-01-31 14:30 | 196.57 | 192.39
2020-01-31 15:00 | 200.53 | 196.87
2020-01-31 15:30 | 202.57 | 198.88
2020-01-31 16:00 | 206.66 | 202.84
2020-01-31 16:30 | 209.15 | 205.47
2020-01-31 17:00 | 210.95 | 207.54
2020-01-31 17:30 | 212.66 | 209.06
2020-01-31 18:00 | 189.18 | 186.31
2020-01-31 18:30 | 168.31 | 165.58
2020-01-31 19:00 | 169.24 | 166.28
2020-01-31 19:30 | 170.39 | 167.37
2020-01-31 20:00 | 204.21 | 200.5
2020-01-31 20:30 | 213.21 | 209.05
2020-01-31 21:00 | 210.26 | 205.8
2020-01-31 21:30 | 207.41 | 202.79
2020-01-31 22:00 | 204.91 | 200.02
2020-01-31 22:30 | 202.02 | 197.06
2020-01-31 23:00 | 197.45 | 192.78
2020-01-31 23:30 | 195.34 | 190.89
2020-02-01 | 192.87 | 188.68
2020-02-01 00:30 | 191.24 | 187.16
2020-02-01 01:00 | 189.54 | 185.64
2020-02-01 01:30 | 166.94 | 163.14
2020-02-01 02:00 | 196.53 | 193.01
2020-02-01 02:30 | 203.84 | 200.14
2020-02-01 03:00 | 203.39 | 199.68
2020-02-01 03:30 | 202.42 | 198.71
2020-02-01 04:00 | 201.52 | 197.8
2020-02-01 04:30 | 201.19 | 197.49
2020-02-01 05:00 | 200.96 | 197.26
2020-02-01 05:30 | 200.97 | 197.29
2020-02-01 06:00 | 200.68 | 196.94
2020-02-01 06:30 | 200.8 | 197.2
2020-02-01 07:00 | 201.54 | 198.05
2020-02-01 07:30 | 202.22 | 198.71
2020-02-01 08:00 | 202.08 | 198.61
2020-02-01 08:30 | 202.59 | 199.14
2020-02-01 09:00 | 202.97 | 199.54
2020-02-01 09:30 | 203.34 | 199.92
2020-02-01 10:00 | 203.93 | 200.56
2020-02-01 10:30 | 205.1 | 201.72
2020-02-01 11:00 | 206.51 | 203.16
2020-02-01 11:30 | 209.28 | 205.83
2020-02-01 12:00 | 184.37 | 180.13
2020-02-01 12:30 | 185.74 | 180.46
2020-02-01 13:00 | 195.53 | 190.34
2020-02-01 13:30 | 197.19 | 191.92
2020-02-01 14:00 | 198.75 | 193.37
2020-02-01 14:30 | 199.78 | 194.3
2020-02-01 15:00 | 201.23 | 195.58
2020-02-01 15:30 | 202.69 | 197.3
2020-02-01 16:00 | 204.09 | 198.98
2020-02-01 16:30 | 206.15 | 201.16
2020-02-01 17:00 | 194.88 | 190.81
2020-02-01 17:30 | 174.58 | 172.08
2020-02-01 18:00 | 173.74 | 171.15
2020-02-01 18:30 | 173.35 | 170.61
2020-02-01 19:00 | 173.88 | 171.12
2020-02-01 19:30 | 175.2 | 172.46
2020-02-01 20:00 | 176.28 | 173.52
2020-02-01 20:30 | 179.06 | 176.22
2020-02-01 21:00 | 181.94 | 178.89
2020-02-01 21:30 | 183.7 | 180.79
2020-02-01 22:00 | 185.8 | 183.06
2020-02-01 22:30 | 188.22 | 185.43
2020-02-01 23:00 | 192.04 | 187.44
2020-02-01 23:30 | 194.2 | 189.24
2020-02-02 | 192.6 | 187.54
2020-02-02 00:30 | 191.35 | 186.13
2020-02-02 01:00 | 190.06 | 184.95
2020-02-02 01:30 | 188.39 | 183.98
2020-02-02 02:00 | 188.14 | 183.62
2020-02-02 02:30 | 187.52 | 182.9
2020-02-02 03:00 | 187.23 | 182.49
2020-02-02 03:30 | 186.29 | 181.72
2020-02-02 04:00 | 188.17 | 184.26
2020-02-02 04:30 | 203.1 | 199.1
2020-02-02 05:00 | 203.03 | 199.02
2020-02-02 05:30 | 203.02 | 199.02
2020-02-02 06:00 | 202.81 | 198.78
2020-02-02 06:30 | 202.44 | 198.5
2020-02-02 07:00 | 202.54 | 198.84
2020-02-02 07:30 | 203.21 | 199.51
2020-02-02 08:00 | 202.95 | 199.27
2020-02-02 08:30 | 202.24 | 198.62
2020-02-02 09:00 | 201.81 | 198.28
2020-02-02 09:30 | 199.66 | 196.49
2020-02-02 10:00 | 201.3 | 198.11
2020-02-02 10:30 | 202.43 | 199.15
2020-02-02 11:00 | 204.39 | 201.03
2020-02-02 11:30 | 206.77 | 203.45
2020-02-02 12:00 | 209.19 | 205.93
2020-02-02 12:30 | 211.05 | 207.86
2020-02-02 13:00 | 213.77 | 210.54
2020-02-02 13:30 | 185.53 | 182.1
2020-02-02 14:00 | 191.25 | 187.08
2020-02-02 14:30 | 203.39 | 199.29
2020-02-02 15:00 | 204.5 | 200.58
2020-02-02 15:30 | 206.88 | 203.18
2020-02-02 16:00 | 208.95 | 205.26
2020-02-02 16:30 | 211.73 | 207.95
2020-02-02 17:00 | 213.33 | 209.68
2020-02-02 17:30 | 215.34 | 211.66
2020-02-02 18:00 | 210.07 | 206.71
2020-02-02 18:30 | 171.04 | 168.57
2020-02-02 19:00 | 170.65 | 168.22
2020-02-02 19:30 | 171.85 | 169.48
2020-02-02 20:00 | 173.47 | 170.99
2020-02-02 20:30 | 175.87 | 173.4
2020-02-02 21:00 | 199.85 | 196.23
2020-02-02 21:30 | 204.63 | 200.59
2020-02-02 22:00 | 198.37 | 194.32
2020-02-02 22:30 | 201.38 | 197.89
2020-02-02 23:00 | 213.52 | 210.05
2020-02-02 23:30 | 211.68 | 208.17
2020-02-03 | 209.81 | 206.06
2020-02-03 00:30 | 208.81 | 205.06
2020-02-03 01:00 | 207.76 | 203.96
2020-02-03 01:30 | 207.05 | 203.24
2020-02-03 02:00 | 206.24 | 202.39
2020-02-03 02:30 | 205.4 | 201.54
2020-02-03 03:00 | 205.09 | 201.22
2020-02-03 03:30 | 204.61 | 200.74
2020-02-03 04:00 | 204.15 | 200.25
2020-02-03 04:30 | 204.25 | 200.36
2020-02-03 05:00 | 204.46 | 200.61
2020-02-03 05:30 | 205.33 | 201.52
2020-02-03 06:00 | 205.58 | 201.84
2020-02-03 06:30 | 207.04 | 203.39
2020-02-03 07:00 | 208.79 | 205.14
2020-02-03 07:30 | 210.79 | 207.3
2020-02-03 08:00 | 210.72 | 207.39
2020-02-03 08:30 | 208.24 | 205.23
2020-02-03 09:00 | 208.54 | 205.55
2020-02-03 09:30 | 208.15 | 205.14
2020-02-03 10:00 | 209.65 | 206.56
2020-02-03 10:30 | 211.69 | 208.7
2020-02-03 11:00 | 213.1 | 210.3
2020-02-03 11:30 | 215.07 | 212.28
2020-02-03 12:00 | 217.22 | 214.48
2020-02-03 12:30 | 219.55 | 216.85
2020-02-03 13:00 | 223.53 | 220.76
2020-02-03 13:30 | 227.57 | 224.44
2020-02-03 14:00 | 205.69 | 202.32
2020-02-03 14:30 | 195.94 | 191.78
2020-02-03 15:00 | 193.71 | 189.33
2020-02-03 15:30 | 193.99 | 189.77
2020-02-03 16:00 | 194.94 | 190.64
2020-02-03 16:30 | 196.31 | 191.84
2020-02-03 17:00 | 195.46 | 190.64
2020-02-03 17:30 | 193.35 | 188.25
2020-02-03 18:00 | 187.74 | 183.38
2020-02-03 18:30 | 180.89 | 178.42
2020-02-03 19:00 | 182.39 | 180.02
2020-02-03 19:30 | 183.27 | 181.14
2020-02-03 20:00 | 181.66 | 179.78
2020-02-03 20:30 | 182.6 | 180.69
2020-02-03 21:00 | 183.3 | 179.01
2020-02-03 21:30 | 185.97 | 180.94
2020-02-03 22:00 | 183.76 | 178.66
2020-02-03 22:30 | 182.19 | 177.06
2020-02-03 23:00 | 198.35 | 193.91
2020-02-03 23:30 | 207.32 | 202.93
2020-02-04 | 205.89 | 201.48
2020-02-04 00:30 | 205.06 | 200.58
2020-02-04 01:00 | 204.46 | 200.06
2020-02-04 01:30 | 203.67 | 199.33
2020-02-04 02:00 | 203.52 | 199.2
2020-02-04 02:30 | 202.57 | 198.19
2020-02-04 03:00 | 202.15 | 197.8
2020-02-04 03:30 | 201.7 | 197.35
2020-02-04 04:00 | 201.48 | 197.17
2020-02-04 04:30 | 201.68 | 197.36
2020-02-04 05:00 | 202.1 | 197.86
2020-02-04 05:30 | 203.05 | 198.89
2020-02-04 06:00 | 203.86 | 199.6
2020-02-04 06:30 | 205.78 | 201.48
2020-02-04 07:00 | 206.66 | 202.41
2020-02-04 07:30 | 207.99 | 203.95
2020-02-04 08:00 | 208.21 | 204.21
2020-02-04 08:30 | 207.36 | 203.58
2020-02-04 09:00 | 207.22 | 203.5
2020-02-04 09:30 | 207.04 | 203.27
2020-02-04 10:00 | 208 | 204.13
2020-02-04 10:30 | 210.18 | 206.39
2020-02-04 11:00 | 211.32 | 207.55
2020-02-04 11:30 | 213.14 | 209.46
2020-02-04 12:00 | 215.4 | 211.76
2020-02-04 12:30 | 216.31 | 212.62
2020-02-04 13:00 | 217.26 | 213.51
2020-02-04 13:30 | 219.35 | 215.68
2020-02-04 14:00 | 220.74 | 217.2
2020-02-04 14:30 | 221.94 | 218.59
2020-02-04 15:00 | 221.9 | 218.68
2020-02-04 15:30 | 221.6 | 218.53
2020-02-04 16:00 | 222.4 | 219.25
2020-02-04 16:30 | 222.56 | 219.3
2020-02-04 17:00 | 225.3 | 221.93
2020-02-04 17:30 | 200.85 | 196.83
2020-02-04 18:00 | 195.49 | 190.95
2020-02-04 18:30 | 200.79 | 196.07
2020-02-04 19:00 | 200.83 | 196.13
2020-02-04 19:30 | 199.47 | 194.6
2020-02-04 20:00 | 196.09 | 190.97
2020-02-04 20:30 | 183.27 | 178.39
2020-02-04 21:00 | 201.82 | 197.79
2020-02-04 21:30 | 212.92 | 209.08
2020-02-04 22:00 | 210.67 | 206.63
2020-02-04 22:30 | 207.57 | 203.45
2020-02-04 23:00 | 205.74 | 201.52
2020-02-04 23:30 | 204.82 | 200.62
2020-02-05 | 203.48 | 199.33
2020-02-05 00:30 | 202.17 | 197.98
2020-02-05 01:00 | 201.33 | 197.07
2020-02-05 01:30 | 200.73 | 196.39
2020-02-05 02:00 | 199.56 | 195.19
2020-02-05 02:30 | 199.15 | 194.71
2020-02-05 03:00 | 199.6 | 195.13
2020-02-05 03:30 | 198.86 | 194.4
2020-02-05 04:00 | 197.94 | 193.53
2020-02-05 04:30 | 197.8 | 193.46
2020-02-05 05:00 | 197.85 | 193.6
2020-02-05 05:30 | 198.42 | 194.29
2020-02-05 06:00 | 199.4 | 195.28
2020-02-05 06:30 | 200.67 | 196.59
2020-02-05 07:00 | 203.22 | 199.25
2020-02-05 07:30 | 204.58 | 200.78
2020-02-05 08:00 | 204.75 | 201.01
2020-02-05 08:30 | 204.8 | 201.06
2020-02-05 09:00 | 204.16 | 200.39
2020-02-05 09:30 | 202.73 | 198.92
2020-02-05 10:00 | 203.14 | 199.33
2020-02-05 10:30 | 204.06 | 200.2
2020-02-05 11:00 | 204.08 | 200.24
2020-02-05 11:30 | 203.62 | 199.81
2020-02-05 12:00 | 203.57 | 199.77
2020-02-05 12:30 | 203.05 | 199.28
2020-02-05 13:00 | 204.45 | 200.61
2020-02-05 13:30 | 204.71 | 200.94
2020-02-05 14:00 | 203.89 | 200.14
2020-02-05 14:30 | 203.58 | 199.81
2020-02-05 15:00 | 201.63 | 197.79
2020-02-05 15:30 | 202.86 | 199.04
2020-02-05 16:00 | 203.48 | 199.67
2020-02-05 16:30 | 203.48 | 199.68
2020-02-05 17:00 | 203.68 | 199.75
2020-02-05 17:30 | 204.3 | 200.33
2020-02-05 18:00 | 205.39 | 201.44
2020-02-05 18:30 | 205.56 | 201.63
2020-02-05 19:00 | 206.17 | 202.23
2020-02-05 19:30 | 206.57 | 202.62
2020-02-05 20:00 | 205.59 | 201.61
2020-02-05 20:30 | 204.49 | 200.47
2020-02-05 21:00 | 202.61 | 198.55
2020-02-05 21:30 | 201.99 | 197.84
2020-02-05 22:00 | 200.49 | 196.16
2020-02-05 22:30 | 198.6 | 194.2
2020-02-05 23:00 | 197.12 | 192.58
2020-02-05 23:30 | 196.98 | 192.49
2020-02-06 | 195.87 | 191.36
2020-02-06 00:30 | 195.54 | 191.05
2020-02-06 01:00 | 195.28 | 190.78
2020-02-06 01:30 | 194.73 | 190.06
2020-02-06 02:00 | 193.92 | 189.16
2020-02-06 02:30 | 193.69 | 188.89
2020-02-06 03:00 | 193.45 | 188.65
2020-02-06 03:30 | 193.68 | 188.88
2020-02-06 04:00 | 193.4 | 188.63
2020-02-06 04:30 | 193.62 | 188.86
2020-02-06 05:00 | 194.07 | 189.35
2020-02-06 05:30 | 194.83 | 190.21
2020-02-06 06:00 | 195.81 | 191.36
2020-02-06 06:30 | 197.9 | 193.73
2020-02-06 07:00 | 199.2 | 195.09
2020-02-06 07:30 | 200.88 | 196.85
2020-02-06 08:00 | 200.94 | 196.91
2020-02-06 08:30 | 200.55 | 196.7
2020-02-06 09:00 | 200.41 | 196.57
2020-02-06 09:30 | 199.88 | 196.1
2020-02-06 10:00 | 200.76 | 196.97
2020-02-06 10:30 | 200.71 | 196.87
2020-02-06 11:00 | 198.92 | 195.07
2020-02-06 11:30 | 198.36 | 194.58
2020-02-06 12:00 | 198.53 | 194.83
2020-02-06 12:30 | 198.53 | 194.83
2020-02-06 13:00 | 199.8 | 196
2020-02-06 13:30 | 200.86 | 197.22
2020-02-06 14:00 | 202.15 | 198.6
2020-02-06 14:30 | 202.92 | 199.34
2020-02-06 15:00 | 203.59 | 200.04
2020-02-06 15:30 | 203.25 | 199.79
2020-02-06 16:00 | 204.94 | 201.41
2020-02-06 16:30 | 206.38 | 202.81
2020-02-06 17:00 | 206.7 | 203.15
2020-02-06 17:30 | 206.57 | 202.96
2020-02-06 18:00 | 208.01 | 204.37
2020-02-06 18:30 | 208.95 | 205.32
2020-02-06 19:00 | 209.37 | 205.71
2020-02-06 19:30 | 209.45 | 205.79
2020-02-06 20:00 | 208.77 | 205.11
2020-02-06 20:30 | 206.96 | 203.21
2020-02-06 21:00 | 204.29 | 200.37
2020-02-06 21:30 | 204.02 | 200.05
2020-02-06 22:00 | 202.38 | 198.38
2020-02-06 22:30 | 200.27 | 196.29
2020-02-06 23:00 | 198.87 | 194.84
2020-02-06 23:30 | 198.05 | 193.91
2020-02-07 | 197.26 | 193.07
2020-02-07 00:30 | 196.22 | 191.99
2020-02-07 01:00 | 195.43 | 191.09
2020-02-07 01:30 | 194.99 | 190.58
2020-02-07 02:00 | 194.65 | 190.24
2020-02-07 02:30 | 194.23 | 189.74
2020-02-07 03:00 | 194.41 | 189.91
2020-02-07 03:30 | 194.13 | 189.64
2020-02-07 04:00 | 194.29 | 189.79
2020-02-07 04:30 | 194.68 | 190.2
2020-02-07 05:00 | 195.08 | 190.63
2020-02-07 05:30 | 196.03 | 191.76
2020-02-07 06:00 | 196.71 | 192.56
2020-02-07 06:30 | 198.21 | 194.28
2020-02-07 07:00 | 200.15 | 196.43
2020-02-07 07:30 | 201.11 | 197.53
2020-02-07 08:00 | 201.2 | 197.67
2020-02-07 08:30 | 200.79 | 197.21
2020-02-07 09:00 | 199.76 | 196.24
2020-02-07 09:30 | 198.51 | 194.95
2020-02-07 10:00 | 198.73 | 195.21
2020-02-07 10:30 | 198.64 | 195.16
2020-02-07 11:00 | 199.81 | 196.17
2020-02-07 11:30 | 201.72 | 198.09
2020-02-07 12:00 | 201.87 | 198.2
2020-02-07 12:30 | 202.21 | 198.47
2020-02-07 13:00 | 202.6 | 198.79
2020-02-07 13:30 | 203.16 | 199.39
2020-02-07 14:00 | 204.64 | 200.97
2020-02-07 14:30 | 205.42 | 201.8
2020-02-07 15:00 | 206.48 | 202.86
2020-02-07 15:30 | 208.1 | 204.54
2020-02-07 16:00 | 209.71 | 206.16
2020-02-07 16:30 | 211.3 | 207.74
2020-02-07 17:00 | 212.02 | 208.45
2020-02-07 17:30 | 212.29 | 208.63
2020-02-07 18:00 | 212.78 | 209.05
2020-02-07 18:30 | 213.3 | 209.61
2020-02-07 19:00 | 212.96 | 209.34
2020-02-07 19:30 | 213.15 | 209.53
2020-02-07 20:00 | 212.65 | 209.02
2020-02-07 20:30 | 211.16 | 207.49
2020-02-07 21:00 | 209.04 | 205.31
2020-02-07 21:30 | 207.71 | 203.86
2020-02-07 22:00 | 206.31 | 202.39
2020-02-07 22:30 | 204.53 | 200.51
2020-02-07 23:00 | 202.8 | 198.7
2020-02-07 23:30 | 202.15 | 198.06
2020-02-08 | 200.6 | 196.49
2020-02-08 00:30 | 199.59 | 195.64
2020-02-08 01:00 | 198.67 | 194.69
2020-02-08 01:30 | 197.94 | 193.84
2020-02-08 02:00 | 197.8 | 193.45
2020-02-08 02:30 | 197.18 | 192.81
2020-02-08 03:00 | 197.22 | 192.87
2020-02-08 03:30 | 196.86 | 192.51
2020-02-08 04:00 | 196.77 | 192.41
2020-02-08 04:30 | 196.58 | 192.25
2020-02-08 05:00 | 196.91 | 192.58
2020-02-08 05:30 | 197.11 | 192.79
2020-02-08 06:00 | 197.47 | 193.13
2020-02-08 06:30 | 198.01 | 193.67
2020-02-08 07:00 | 198.59 | 193.92
2020-02-08 07:30 | 199.39 | 194.37
2020-02-08 08:00 | 199.74 | 194.84
2020-02-08 08:30 | 199.2 | 194.34
2020-02-08 09:00 | 199.12 | 194.41
2020-02-08 09:30 | 198.82 | 194.28
2020-02-08 10:00 | 198.39 | 193.89
2020-02-08 10:30 | 199.7 | 195.24
2020-02-08 11:00 | 199.15 | 194.7
2020-02-08 11:30 | 198.55 | 194.16
2020-02-08 12:00 | 198.11 | 193.88
2020-02-08 12:30 | 199.88 | 196.12
2020-02-08 13:00 | 198.47 | 194.94
2020-02-08 13:30 | 197.82 | 194.22
2020-02-08 14:00 | 195.72 | 191.98
2020-02-08 14:30 | 196.7 | 193
2020-02-08 15:00 | 196.37 | 192.61
2020-02-08 15:30 | 197.74 | 194.09
2020-02-08 16:00 | 197.89 | 194.25
2020-02-08 16:30 | 198.95 | 195.39
2020-02-08 17:00 | 200.14 | 196.62
2020-02-08 17:30 | 201.06 | 197.55
2020-02-08 18:00 | 202.55 | 199.11
2020-02-08 18:30 | 203.51 | 200.13
2020-02-08 19:00 | 203.88 | 200.5
2020-02-08 19:30 | 204.44 | 201.06
2020-02-08 20:00 | 203.82 | 200.36
2020-02-08 20:30 | 202.19 | 198.58
2020-02-08 21:00 | 199.95 | 196.15
2020-02-08 21:30 | 199.06 | 195.19
2020-02-08 22:00 | 197.81 | 193.87
2020-02-08 22:30 | 196.12 | 192.05
2020-02-08 23:00 | 194.97 | 190.87
2020-02-08 23:30 | 194.12 | 189.95
2020-02-09 | 192.73 | 188.47
2020-02-09 00:30 | 192.12 | 187.84
2020-02-09 01:00 | 191.3 | 186.9
2020-02-09 01:30 | 190.89 | 186.43
2020-02-09 02:00 | 190.59 | 186.1
2020-02-09 02:30 | 190.17 | 185.67
2020-02-09 03:00 | 190.16 | 185.65
2020-02-09 03:30 | 190.05 | 185.54
2020-02-09 04:00 | 189.71 | 185.19
2020-02-09 04:30 | 189.71 | 185.19
2020-02-09 05:00 | 189.42 | 184.92
2020-02-09 05:30 | 189.68 | 185.21
2020-02-09 06:00 | 189.51 | 185.03
2020-02-09 06:30 | 189.51 | 185.1
2020-02-09 07:00 | 188.93 | 184.5
2020-02-09 07:30 | 189.42 | 185.01
2020-02-09 08:00 | 189.24 | 184.97
2020-02-09 08:30 | 189.1 | 184.9
2020-02-09 09:00 | 188.1 | 184.01
2020-02-09 09:30 | 189.03 | 184.86
2020-02-09 10:00 | 190.13 | 185.94
2020-02-09 10:30 | 191.31 | 187.15
2020-02-09 11:00 | 192.13 | 188.09
2020-02-09 11:30 | 193.18 | 189.15
2020-02-09 12:00 | 194.99 | 191
2020-02-09 12:30 | 197.29 | 193.31
2020-02-09 13:00 | 198.55 | 194.62
2020-02-09 13:30 | 200.28 | 196.37
2020-02-09 14:00 | 197.83 | 194.24
2020-02-09 14:30 | 199.01 | 195.47
2020-02-09 15:00 | 200.71 | 197.11
2020-02-09 15:30 | 206.54 | 202.8
2020-02-09 16:00 | 209.12 | 205.29
2020-02-09 16:30 | 210.25 | 206.65
2020-02-09 17:00 | 212.3 | 208.78
2020-02-09 17:30 | 213.07 | 209.6
2020-02-09 18:00 | 213.53 | 210.04
2020-02-09 18:30 | 213.85 | 210.44
2020-02-09 19:00 | 214.09 | 210.71
2020-02-09 19:30 | 213.64 | 210.23
2020-02-09 20:00 | 212.79 | 209.32
2020-02-09 20:30 | 210.65 | 207.09
2020-02-09 21:00 | 208.32 | 204.67
2020-02-09 21:30 | 206.62 | 202.9
2020-02-09 22:00 | 204.35 | 200.43
2020-02-09 22:30 | 201.99 | 198.01
2020-02-09 23:00 | 199.97 | 195.96
2020-02-09 23:30 | 199.21 | 195.03
2020-02-10 | 198.01 | 193.76
2020-02-10 00:30 | 197.6 | 193.32
2020-02-10 01:00 | 196.48 | 192.18
2020-02-10 01:30 | 196 | 191.68
2020-02-10 02:00 | 195.31 | 190.97
2020-02-10 02:30 | 194.44 | 190.11
2020-02-10 03:00 | 194.2 | 189.89
2020-02-10 03:30 | 194.28 | 189.89
2020-02-10 04:00 | 194.14 | 189.77
2020-02-10 04:30 | 194.44 | 190.15
2020-02-10 05:00 | 194.84 | 190.58
2020-02-10 05:30 | 195.69 | 191.6
2020-02-10 06:00 | 196.25 | 192.29
2020-02-10 06:30 | 197.98 | 194.08
2020-02-10 07:00 | 198.58 | 194.74
2020-02-10 07:30 | 199.99 | 196.33
2020-02-10 08:00 | 199.93 | 196.3
2020-02-10 08:30 | 200.38 | 196.79
2020-02-10 09:00 | 197.29 | 193.95
2020-02-10 09:30 | 195.73 | 192.45
2020-02-10 10:00 | 195.83 | 192.54
2020-02-10 10:30 | 197.73 | 194.54
2020-02-10 11:00 | 199.42 | 196.23
2020-02-10 11:30 | 200.4 | 197.28
2020-02-10 12:00 | 201.34 | 198.27
2020-02-10 12:30 | 203.78 | 200.92
2020-02-10 13:00 | 201.59 | 198.93
2020-02-10 13:30 | 199.01 | 196.4
2020-02-10 14:00 | 201.43 | 198.73
2020-02-10 14:30 | 208.02 | 204.85
2020-02-10 15:00 | 207.95 | 204.75
2020-02-10 15:30 | 206.02 | 202.81
2020-02-10 16:00 | 206.68 | 203.54
2020-02-10 16:30 | 203.84 | 200.88
2020-02-10 17:00 | 204.42 | 200.91
2020-02-10 17:30 | 205.34 | 201.95
2020-02-10 18:00 | 206.92 | 203.52
2020-02-10 18:30 | 208.15 | 204.78
2020-02-10 19:00 | 208.22 | 204.83
2020-02-10 19:30 | 207.83 | 204.4
2020-02-10 20:00 | 207 | 203.48
2020-02-10 20:30 | 206.08 | 202.55
2020-02-10 21:00 | 203.99 | 200.38
2020-02-10 21:30 | 202.32 | 198.62
2020-02-10 22:00 | 200.7 | 196.93
2020-02-10 22:30 | 198.11 | 194.23
2020-02-10 23:00 | 196.71 | 192.79
2020-02-10 23:30 | 196.11 | 192.05
2020-02-11 | 194.89 | 190.76
2020-02-11 00:30 | 194.04 | 189.97
2020-02-11 01:00 | 193.19 | 189.18
2020-02-11 01:30 | 192.61 | 188.55
2020-02-11 02:00 | 192.1 | 188.07
2020-02-11 02:30 | 191.98 | 187.92
2020-02-11 03:00 | 191.85 | 187.78
2020-02-11 03:30 | 191.82 | 187.57
2020-02-11 04:00 | 191.64 | 187.37
2020-02-11 04:30 | 192.15 | 187.91
2020-02-11 05:00 | 192.57 | 188.37
2020-02-11 05:30 | 193.64 | 189.51
2020-02-11 06:00 | 194.19 | 190.09
2020-02-11 06:30 | 195.76 | 191.88
2020-02-11 07:00 | 196.01 | 192.27
2020-02-11 07:30 | 196.88 | 193.39
2020-02-11 08:00 | 196.63 | 193.19
2020-02-11 08:30 | 195.98 | 192.57
2020-02-11 09:00 | 195.56 | 192.12
2020-02-11 09:30 | 194.96 | 191.57
2020-02-11 10:00 | 195.91 | 192.6
2020-02-11 10:30 | 196.77 | 193.5
2020-02-11 11:00 | 198.69 | 195.44
2020-02-11 11:30 | 200.71 | 197.44
2020-02-11 12:00 | 200.39 | 197.18
2020-02-11 12:30 | 200.95 | 197.71
2020-02-11 13:00 | 201.15 | 197.94
2020-02-11 13:30 | 202.84 | 199.69
2020-02-11 14:00 | 204.77 | 201.75
2020-02-11 14:30 | 206.62 | 203.77
2020-02-11 15:00 | 205.89 | 202.92
2020-02-11 15:30 | 204.81 | 201.46
2020-02-11 16:00 | 207.2 | 203.76
2020-02-11 16:30 | 185.92 | 182.63
2020-02-11 17:00 | 175.93 | 171.67
2020-02-11 17:30 | 181.82 | 177.29
2020-02-11 18:00 | 183.21 | 178.71
2020-02-11 18:30 | 184.78 | 180.37
2020-02-11 19:00 | 185.9 | 181.47
2020-02-11 19:30 | 177.69 | 175.02
2020-02-11 20:00 | 177.11 | 175.49
2020-02-11 20:30 | 178.65 | 176.94
2020-02-11 21:00 | 181.14 | 179.31
2020-02-11 21:30 | 177.6 | 173.69
2020-02-11 22:00 | 178.5 | 173.93
2020-02-11 22:30 | 176.16 | 171.36
2020-02-11 23:00 | 165.07 | 159.86
2020-02-11 23:30 | 178.18 | 173.34
2020-02-12 | 191.02 | 186.88
2020-02-12 00:30 | 190.83 | 186.74
2020-02-12 01:00 | 188.77 | 184.73
2020-02-12 01:30 | 188.33 | 184.28
2020-02-12 02:00 | 188.02 | 183.94
2020-02-12 02:30 | 187.78 | 183.49
2020-02-12 03:00 | 187.65 | 183.23
2020-02-12 03:30 | 187.53 | 183.11
2020-02-12 04:00 | 187.31 | 182.89
2020-02-12 04:30 | 187.67 | 183.28
2020-02-12 05:00 | 189.44 | 184.9
2020-02-12 05:30 | 185.21 | 180.56
2020-02-12 06:00 | 160.05 | 153.18
2020-02-12 06:30 | 173.71 | 166.35
2020-02-12 07:00 | 175.63 | 167.51
2020-02-12 07:30 | 176.37 | 169.05
2020-02-12 08:00 | 175.99 | 168.93
2020-02-12 08:30 | 174.98 | 168.17
2020-02-12 09:00 | 174.11 | 167.21
2020-02-12 09:30 | 173.57 | 166.45
2020-02-12 10:00 | 174.87 | 166.81
2020-02-12 10:30 | 174.53 | 167.3
2020-02-12 11:00 | 175.42 | 168.21
2020-02-12 11:30 | 176.76 | 169.41
2020-02-12 12:00 | 178.59 | 171.61
2020-02-12 12:30 | 180.61 | 173.41
2020-02-12 13:00 | 182.3 | 175.06
2020-02-12 13:30 | 183.97 | 176.79
2020-02-12 14:00 | 185.42 | 178.48
2020-02-12 14:30 | 186.69 | 179.82
2020-02-12 15:00 | 186.7 | 179.93
2020-02-12 15:30 | 187.42 | 180.68
2020-02-12 16:00 | 188.75 | 182.23
2020-02-12 16:30 | 188.65 | 182.02
2020-02-12 17:00 | 191.51 | 184.95
2020-02-12 17:30 | 192.94 | 186.34
2020-02-12 18:00 | 173.51 | 166.84
2020-02-12 18:30 | 197.94 | 194.13
2020-02-12 19:00 | 210.72 | 208.01
2020-02-12 19:30 | 210.69 | 207.99
2020-02-12 20:00 | 210.06 | 207.26
2020-02-12 20:30 | 207.53 | 204.63
2020-02-12 21:00 | 204.72 | 201.69
2020-02-12 21:30 | 203.52 | 200.2
2020-02-12 22:00 | 200.98 | 197.52
2020-02-12 22:30 | 198.53 | 194.87
2020-02-12 23:00 | 196.93 | 193.26
2020-02-12 23:30 | 195.92 | 192.29
2020-02-13 | 194.03 | 190.44
2020-02-13 00:30 | 192.6 | 188.96
2020-02-13 01:00 | 191.84 | 188.11
2020-02-13 01:30 | 191.38 | 187.58
2020-02-13 02:00 | 190.68 | 186.87
2020-02-13 02:30 | 190.22 | 186.37
2020-02-13 03:00 | 189.85 | 186.02
2020-02-13 03:30 | 189.6 | 185.72
2020-02-13 04:00 | 189.39 | 185.5
2020-02-13 04:30 | 189.55 | 185.69
2020-02-13 05:00 | 189.68 | 185.95
2020-02-13 05:30 | 190.96 | 187.43
2020-02-13 06:00 | 191.53 | 187.65
2020-02-13 06:30 | 172.19 | 167.17
2020-02-13 07:00 | 169.83 | 164.35
2020-02-13 07:30 | 171.14 | 165.94
2020-02-13 08:00 | 171.57 | 165.96
2020-02-13 08:30 | 156.49 | 149.51
2020-02-13 09:00 | 169.08 | 162.06
2020-02-13 09:30 | 175.18 | 168.54
2020-02-13 10:00 | 176.05 | 169
2020-02-13 10:30 | 179.1 | 171.7
2020-02-13 11:00 | 179.34 | 171.77
2020-02-13 11:30 | 179.52 | 171.88
2020-02-13 12:00 | 178.84 | 171.28
2020-02-13 12:30 | 180.5 | 173.07
2020-02-13 13:00 | 180.58 | 173.28
2020-02-13 13:30 | 183.09 | 175.48
2020-02-13 14:00 | 184.15 | 176.7
2020-02-13 14:30 | 183.36 | 175.9
2020-02-13 15:00 | 182.72 | 175.39
2020-02-13 15:30 | 183.53 | 176.15
2020-02-13 16:00 | 185.67 | 178.22
2020-02-13 16:30 | 185.49 | 177.98
2020-02-13 17:00 | 186.72 | 179.19
2020-02-13 17:30 | 187.98 | 179.78
2020-02-13 18:00 | 188.88 | 180.44
2020-02-13 18:30 | 187.98 | 180.83
2020-02-13 19:00 | 188.84 | 181.74
2020-02-13 19:30 | 189 | 181.9
2020-02-13 20:00 | 187.94 | 180.89
2020-02-13 20:30 | 186.36 | 179.19
2020-02-13 21:00 | 183.61 | 176.56
2020-02-13 21:30 | 181.42 | 174.63
2020-02-13 22:00 | 178.81 | 171.98
2020-02-13 22:30 | 176.65 | 169.6
2020-02-13 23:00 | 174.76 | 167.8
2020-02-13 23:30 | 173.48 | 166.67
2020-02-14 | 172.08 | 165.1
2020-02-14 00:30 | 171.14 | 164.21
2020-02-14 01:00 | 157.13 | 151.02
2020-02-14 01:30 | 175.32 | 171.24
2020-02-14 02:00 | 184.88 | 181.48
2020-02-14 02:30 | 184.36 | 180.89
2020-02-14 03:00 | 184.05 | 180.58
2020-02-14 03:30 | 184.11 | 180.64
2020-02-14 04:00 | 183.84 | 180.37
2020-02-14 04:30 | 183.96 | 180.5
2020-02-14 05:00 | 184.45 | 180.97
2020-02-14 05:30 | 185.48 | 182.08
2020-02-14 06:00 | 186.28 | 183.05
2020-02-14 06:30 | 188.41 | 185.19
2020-02-14 07:00 | 165.34 | 160.31
2020-02-14 07:30 | 164.51 | 159.37
2020-02-14 08:00 | 164.81 | 159.73
2020-02-14 08:30 | 164.06 | 158.92
2020-02-14 09:00 | 163.16 | 157.92
2020-02-14 09:30 | 163.07 | 157.78
2020-02-14 10:00 | 163.3 | 157.97
2020-02-14 10:30 | 163.64 | 158.49
2020-02-14 11:00 | 165.64 | 160.6
2020-02-14 11:30 | 168.06 | 161.63
2020-02-14 12:00 | 175.78 | 169.59
2020-02-14 12:30 | 177 | 170.94
2020-02-14 13:00 | 179.46 | 172.95
2020-02-14 13:30 | 180.32 | 173.01
2020-02-14 14:00 | 181.5 | 174.29
2020-02-14 14:30 | 181.66 | 174.37
2020-02-14 15:00 | 181.53 | 174.67
2020-02-14 15:30 | 182.22 | 175.37
2020-02-14 16:00 | 186.62 | 179.53
2020-02-14 16:30 | 186.37 | 179.08
2020-02-14 17:00 | 186.9 | 179.77
2020-02-14 17:30 | 186.93 | 179.38
2020-02-14 18:00 | 187.49 | 180.15
2020-02-14 18:30 | 186.82 | 180.39
2020-02-14 19:00 | 187.12 | 180.59
2020-02-14 19:30 | 187.47 | 181.08
2020-02-14 20:00 | 162.54 | 157
2020-02-14 20:30 | 151.89 | 146.47
2020-02-14 21:00 | 149.56 | 144.12
2020-02-14 21:30 | 148 | 142.64
2020-02-14 22:00 | 169.92 | 163.58
2020-02-14 22:30 | 177.29 | 170.4
2020-02-14 23:00 | 175.66 | 168.61
2020-02-14 23:30 | 174.97 | 167.71
2020-02-15 | 171.98 | 165.21
2020-02-15 00:30 | 169.64 | 163.88
2020-02-15 01:00 | 165.13 | 160.2
2020-02-15 01:30 | 184.8 | 181.58
2020-02-15 02:00 | 184.34 | 181.08
2020-02-15 02:30 | 184.22 | 180.97
2020-02-15 03:00 | 183.35 | 180.13
2020-02-15 03:30 | 183.05 | 179.81
2020-02-15 04:00 | 182.98 | 179.72
2020-02-15 04:30 | 182.83 | 179.57
2020-02-15 05:00 | 182.83 | 179.6
2020-02-15 05:30 | 182.94 | 179.71
2020-02-15 06:00 | 182.63 | 179.4
2020-02-15 06:30 | 183.23 | 180
2020-02-15 07:00 | 183.53 | 180.34
2020-02-15 07:30 | 184.16 | 181.17
2020-02-15 08:00 | 183.53 | 180.51
2020-02-15 08:30 | 183.25 | 180.29
2020-02-15 09:00 | 182.99 | 180.02
2020-02-15 09:30 | 184.01 | 181.05
2020-02-15 10:00 | 184.53 | 181.63
2020-02-15 10:30 | 185.66 | 182.8
2020-02-15 11:00 | 187.84 | 184.94
2020-02-15 11:30 | 189.57 | 186.73
2020-02-15 12:00 | 190.36 | 187.52
2020-02-15 12:30 | 191.41 | 188.57
2020-02-15 13:00 | 192.79 | 189.95
2020-02-15 13:30 | 194.11 | 191.29
2020-02-15 14:00 | 195.76 | 192.99
2020-02-15 14:30 | 195.71 | 192.99
2020-02-15 15:00 | 194.21 | 191.75
2020-02-15 15:30 | 198.59 | 196.02
2020-02-15 16:00 | 168.33 | 163.08
2020-02-15 16:30 | 157.59 | 155.01
2020-02-15 17:00 | 164.22 | 161.66
2020-02-15 17:30 | 162.96 | 160.38
2020-02-15 18:00 | 162.26 | 159.61
2020-02-15 18:30 | 162.98 | 160.24
2020-02-15 19:00 | 164.24 | 161.28
2020-02-15 19:30 | 165.14 | 162.25
2020-02-15 20:00 | 166.35 | 163.5
2020-02-15 20:30 | 167.72 | 164.79
2020-02-15 21:00 | 170.62 | 167.52
2020-02-15 21:30 | 164.44 | 160.95
2020-02-15 22:00 | 163.32 | 159.59
2020-02-15 22:30 | 153.47 | 150.34
2020-02-15 23:00 | 176.97 | 173.57
2020-02-15 23:30 | 195.09 | 191.47
2020-02-16 | 191.13 | 187.67
2020-02-16 00:30 | 189.19 | 185.73
2020-02-16 01:00 | 188.15 | 184.61
2020-02-16 01:30 | 187.47 | 183.85
2020-02-16 02:00 | 187.1 | 183.49
2020-02-16 02:30 | 186.04 | 182.53
2020-02-16 03:00 | 184.93 | 181.43
2020-02-16 03:30 | 184.35 | 180.97
2020-02-16 04:00 | 183.56 | 180.31
2020-02-16 04:30 | 183.23 | 180.02
2020-02-16 05:00 | 183.03 | 179.8
2020-02-16 05:30 | 183.21 | 179.97
2020-02-16 06:00 | 183.06 | 179.8
2020-02-16 06:30 | 183.14 | 179.85
2020-02-16 07:00 | 183.35 | 180.12
2020-02-16 07:30 | 184.39 | 181.14
2020-02-16 08:00 | 184.66 | 181.39
2020-02-16 08:30 | 185.28 | 182.09
2020-02-16 09:00 | 186.77 | 183.65
2020-02-16 09:30 | 188.53 | 185.42
2020-02-16 10:00 | 190.61 | 187.47
2020-02-16 10:30 | 191.56 | 188.44
2020-02-16 11:00 | 193.02 | 190.02
2020-02-16 11:30 | 195.33 | 192.35
2020-02-16 12:00 | 197.05 | 194.18
2020-02-16 12:30 | 199.27 | 196.38
2020-02-16 13:00 | 201.2 | 198.34
2020-02-16 13:30 | 203.59 | 200.73
2020-02-16 14:00 | 205.47 | 202.54
2020-02-16 14:30 | 208.05 | 205.06
2020-02-16 15:00 | 210.37 | 207.3
2020-02-16 15:30 | 186.68 | 181.33
2020-02-16 16:00 | 187.61 | 181.29
2020-02-16 16:30 | 197.57 | 191.57
2020-02-16 17:00 | 199.31 | 193.51
2020-02-16 17:30 | 185.84 | 181.14
2020-02-16 18:00 | 160.94 | 157.4
2020-02-16 18:30 | 159.22 | 155.59
2020-02-16 19:00 | 159.64 | 155.98
2020-02-16 19:30 | 160.8 | 156.94
2020-02-16 20:00 | 162.55 | 158.57
2020-02-16 20:30 | 165.67 | 161.49
2020-02-16 21:00 | 168.28 | 163.9
2020-02-16 21:30 | 167.16 | 162.72
2020-02-16 22:00 | 183.2 | 177.11
2020-02-16 22:30 | 178.81 | 172.87
2020-02-16 23:00 | 193.04 | 189.24
2020-02-16 23:30 | 202.14 | 198.95
2020-02-17 | 199.99 | 196.77
2020-02-17 00:30 | 198.73 | 195.58
2020-02-17 01:00 | 198.27 | 195.15
2020-02-17 01:30 | 197.59 | 194.42
2020-02-17 02:00 | 196.91 | 193.73
2020-02-17 02:30 | 196.3 | 193.11
2020-02-17 03:00 | 195.7 | 192.51
2020-02-17 03:30 | 195.33 | 192.13
2020-02-17 04:00 | 195.05 | 191.84
2020-02-17 04:30 | 195 | 191.78
2020-02-17 05:00 | 195.51 | 192.27
2020-02-17 05:30 | 196.31 | 193.13
2020-02-17 06:00 | 197.25 | 194.2
2020-02-17 06:30 | 198.79 | 195.79
2020-02-17 07:00 | 200.67 | 197.67
2020-02-17 07:30 | 202.79 | 199.93
2020-02-17 08:00 | 203.98 | 201.11
2020-02-17 08:30 | 204.49 | 201.45
2020-02-17 09:00 | 172.52 | 167.84
2020-02-17 09:30 | 177.45 | 171.88
2020-02-17 10:00 | 186.98 | 181.23
2020-02-17 10:30 | 187.42 | 181.9
2020-02-17 11:00 | 189.33 | 183.48
2020-02-17 11:30 | 191.64 | 185.78
2020-02-17 12:00 | 192.86 | 186.88
2020-02-17 12:30 | 193.77 | 187.68
2020-02-17 13:00 | 195.43 | 189.24
2020-02-17 13:30 | 197.22 | 191.4
2020-02-17 14:00 | 198.93 | 193.29
2020-02-17 14:30 | 203.55 | 198.18
2020-02-17 15:00 | 204.09 | 198.52
2020-02-17 15:30 | 204.67 | 199.01
2020-02-17 16:00 | 203.9 | 198.32
2020-02-17 16:30 | 169.51 | 165.4
2020-02-17 17:00 | 163.12 | 159.1
2020-02-17 17:30 | 162.26 | 158.11
2020-02-17 18:00 | 161.13 | 156.91
2020-02-17 18:30 | 161.39 | 156.99
2020-02-17 19:00 | 166.2 | 161.73
2020-02-17 19:30 | 168.03 | 163.58
2020-02-17 20:00 | 169.19 | 164.62
2020-02-17 20:30 | 169.03 | 164.45
2020-02-17 21:00 | 191.5 | 186.03
2020-02-17 21:30 | 195.63 | 189.74
2020-02-17 22:00 | 191.67 | 186.03
2020-02-17 22:30 | 188.51 | 182.93
2020-02-17 23:00 | 184.66 | 180.31
2020-02-17 23:30 | 204.66 | 201.49
2020-02-18 | 203.04 | 199.63
2020-02-18 00:30 | 201.23 | 197.74
2020-02-18 01:00 | 199.23 | 195.71
2020-02-18 01:30 | 198 | 194.51
2020-02-18 02:00 | 197.53 | 194.06
2020-02-18 02:30 | 197.54 | 194.14
2020-02-18 03:00 | 197.33 | 193.94
2020-02-18 03:30 | 196.87 | 193.48
2020-02-18 04:00 | 196.86 | 193.47
2020-02-18 04:30 | 196.97 | 193.59
2020-02-18 05:00 | 197.57 | 194.21
2020-02-18 05:30 | 198.13 | 194.84
2020-02-18 06:00 | 198.44 | 195.2
2020-02-18 06:30 | 200.35 | 197.23
2020-02-18 07:00 | 201.96 | 198.85
2020-02-18 07:30 | 204.09 | 201.09
2020-02-18 08:00 | 204.08 | 201.1
2020-02-18 08:30 | 203.97 | 200.98
2020-02-18 09:00 | 204.34 | 201.42
2020-02-18 09:30 | 204.4 | 201.5
2020-02-18 10:00 | 203.1 | 200.01
2020-02-18 10:30 | 205.73 | 202.87
2020-02-18 11:00 | 207.17 | 204.5
2020-02-18 11:30 | 207.94 | 205.34
2020-02-18 12:00 | 210.49 | 207.95
2020-02-18 12:30 | 212.06 | 209.66
2020-02-18 13:00 | 214.81 | 212.35
2020-02-18 13:30 | 194.99 | 191.87
2020-02-18 14:00 | 191.7 | 188.41
2020-02-18 14:30 | 199.38 | 196.15
2020-02-18 15:00 | 202.69 | 199.84
2020-02-18 15:30 | 202.32 | 199.47
2020-02-18 16:00 | 189.8 | 186.97
2020-02-18 16:30 | 161.73 | 158.24
2020-02-18 17:00 | 159.4 | 154.84
2020-02-18 17:30 | 167.59 | 163.5
2020-02-18 18:00 | 170.9 | 167.16
2020-02-18 18:30 | 170.27 | 166.48
2020-02-18 19:00 | 174.37 | 170.57
2020-02-18 19:30 | 176.81 | 173.17
2020-02-18 20:00 | 175.52 | 172.28
2020-02-18 20:30 | 177.44 | 173.94
2020-02-18 21:00 | 186.45 | 180.5
2020-02-18 21:30 | 189.78 | 183.56
2020-02-18 22:00 | 186.7 | 180.65
2020-02-18 22:30 | 183.74 | 177.6
2020-02-18 23:00 | 181.53 | 175.25
2020-02-18 23:30 | 179.5 | 173.09
2020-02-19 | 178.83 | 172.4
2020-02-19 00:30 | 178.06 | 171.37
2020-02-19 01:00 | 176.11 | 169.37
2020-02-19 01:30 | 179.53 | 173.14
2020-02-19 02:00 | 177.9 | 171.84
2020-02-19 02:30 | 177.4 | 171.41
2020-02-19 03:00 | 177.31 | 171.26
2020-02-19 03:30 | 176.71 | 170.73
2020-02-19 04:00 | 176.33 | 170.43
2020-02-19 04:30 | 176.19 | 170.23
2020-02-19 05:00 | 176.71 | 170.75
2020-02-19 05:30 | 177.93 | 171.71
2020-02-19 06:00 | 178.21 | 172.07
2020-02-19 06:30 | 179.52 | 173.69
2020-02-19 07:00 | 181.06 | 175.12
2020-02-19 07:30 | 182.24 | 176.62
2020-02-19 08:00 | 162.01 | 156.49
2020-02-19 08:30 | 157.42 | 151.99
2020-02-19 09:00 | 180.17 | 176.08
2020-02-19 09:30 | 200.16 | 196.98
2020-02-19 10:00 | 200.76 | 197.55
2020-02-19 10:30 | 201.28 | 198.14
2020-02-19 11:00 | 201.95 | 198.87
2020-02-19 11:30 | 202.57 | 199.52
2020-02-19 12:00 | 203.98 | 200.91
2020-02-19 12:30 | 205.5 | 202.41
2020-02-19 13:00 | 206.84 | 203.79
2020-02-19 13:30 | 207.29 | 204.38
2020-02-19 14:00 | 209.45 | 206.65
2020-02-19 14:30 | 211.15 | 208.35
2020-02-19 15:00 | 212.7 | 209.94
2020-02-19 15:30 | 213.79 | 211.18
2020-02-19 16:00 | 211.3 | 208.7
2020-02-19 16:30 | 187.08 | 183.26
2020-02-19 17:00 | 191.33 | 187.03
2020-02-19 17:30 | 191.21 | 187.25
2020-02-19 18:00 | 165.45 | 162.63
2020-02-19 18:30 | 165.39 | 162.4
2020-02-19 19:00 | 166.28 | 163.12
2020-02-19 19:30 | 167.27 | 163.81
2020-02-19 20:00 | 168.7 | 165.52
2020-02-19 20:30 | 171.17 | 168.02
2020-02-19 21:00 | 174.59 | 171.18
2020-02-19 21:30 | 175.65 | 172.65
2020-02-19 22:00 | 152.59 | 148.44
2020-02-19 22:30 | 152.23 | 148.21
2020-02-19 23:00 | 150.44 | 146.44
2020-02-19 23:30 | 157.25 | 154.96
2020-02-20 | 171.29 | 169.69
2020-02-20 00:30 | 172 | 170.39
2020-02-20 01:00 | 187.73 | 184.69
2020-02-20 01:30 | 192.07 | 188.61
2020-02-20 02:00 | 191.44 | 187.97
2020-02-20 02:30 | 190.68 | 187.22
2020-02-20 03:00 | 190.53 | 187.07
2020-02-20 03:30 | 190.15 | 186.65
2020-02-20 04:00 | 189.8 | 186.23
2020-02-20 04:30 | 189.73 | 185.98
2020-02-20 05:00 | 189.74 | 186
2020-02-20 05:30 | 191.17 | 187.67
2020-02-20 06:00 | 191.78 | 188.28
2020-02-20 06:30 | 193.1 | 189.59
2020-02-20 07:00 | 194.04 | 190.52
2020-02-20 07:30 | 194.55 | 191.23
2020-02-20 08:00 | 193.98 | 190.71
2020-02-20 08:30 | 193.24 | 189.86
2020-02-20 09:00 | 192.26 | 188.83
2020-02-20 09:30 | 188.66 | 185.59
2020-02-20 10:00 | 188.35 | 185.37
2020-02-20 10:30 | 188.55 | 185.59
2020-02-20 11:00 | 189.37 | 186.33
2020-02-20 11:30 | 174.4 | 170.07
2020-02-20 12:00 | 172.99 | 167.08
2020-02-20 12:30 | 182.86 | 176.89
2020-02-20 13:00 | 184.57 | 178.86
2020-02-20 13:30 | 185.47 | 180.52
2020-02-20 14:00 | 186.79 | 182.08
2020-02-20 14:30 | 188.25 | 183.65
2020-02-20 15:00 | 189.56 | 185.08
2020-02-20 15:30 | 190.72 | 186.36
2020-02-20 16:00 | 192.42 | 188.17
2020-02-20 16:30 | 194.58 | 190.4
2020-02-20 17:00 | 196.8 | 192.75
2020-02-20 17:30 | 197.66 | 193.41
2020-02-20 18:00 | 198.94 | 194.66
2020-02-20 18:30 | 192.22 | 188.6
2020-02-20 19:00 | 178.34 | 176.4
2020-02-20 19:30 | 178.5 | 176.58
2020-02-20 20:00 | 179.54 | 177.56
2020-02-20 20:30 | 181.36 | 179.43
2020-02-20 21:00 | 183.27 | 181.46
2020-02-20 21:30 | 185.12 | 183.16
2020-02-20 22:00 | 187.27 | 185.4
2020-02-20 22:30 | 162.22 | 159.41
2020-02-20 23:00 | 178.56 | 173.5
2020-02-20 23:30 | 181.2 | 174.93
2020-02-21 | 155.46 | 148.69
2020-02-21 00:30 | 182.05 | 178.05
2020-02-21 01:00 | 189.15 | 185.8
2020-02-21 01:30 | 188.57 | 185.18
2020-02-21 02:00 | 187.65 | 184.22
2020-02-21 02:30 | 187.55 | 184.07
2020-02-21 03:00 | 187.27 | 183.8
2020-02-21 03:30 | 186.92 | 183.48
2020-02-21 04:00 | 186.83 | 183.4
2020-02-21 04:30 | 186.59 | 183.16
2020-02-21 05:00 | 187.11 | 183.67
2020-02-21 05:30 | 188.01 | 184.62
2020-02-21 06:00 | 188.93 | 185.63
2020-02-21 06:30 | 190.54 | 187.36
2020-02-21 07:00 | 191.28 | 188.15
2020-02-21 07:30 | 191.64 | 188.54
2020-02-21 08:00 | 191.36 | 188.23
2020-02-21 08:30 | 191.2 | 188.01
2020-02-21 09:00 | 190.35 | 187.18
2020-02-21 09:30 | 186.83 | 184
2020-02-21 10:00 | 187.25 | 184.54
2020-02-21 10:30 | 171.52 | 168.12
2020-02-21 11:00 | 167.35 | 163.45
2020-02-21 11:30 | 169.13 | 165.26
2020-02-21 12:00 | 175.23 | 171.09
2020-02-21 12:30 | 185.72 | 181.47
2020-02-21 13:00 | 186.98 | 182.6
2020-02-21 13:30 | 188.48 | 183.95
2020-02-21 14:00 | 190 | 185.43
2020-02-21 14:30 | 190.04 | 185.18
2020-02-21 15:00 | 189.72 | 184.66
2020-02-21 15:30 | 190.7 | 185.74
2020-02-21 16:00 | 193.17 | 188.46
2020-02-21 16:30 | 195.41 | 190.96
2020-02-21 17:00 | 197.29 | 193.11
2020-02-21 17:30 | 198.27 | 194.01
2020-02-21 18:00 | 199.31 | 195.05
2020-02-21 18:30 | 199.61 | 195.51
2020-02-21 19:00 | 199.46 | 195.32
2020-02-21 19:30 | 199.11 | 194.92
2020-02-21 20:00 | 197.56 | 193.2
2020-02-21 20:30 | 195.69 | 191.13
2020-02-21 21:00 | 193.42 | 188.55
2020-02-21 21:30 | 189.97 | 185.2
2020-02-21 22:00 | 187.31 | 182.89
2020-02-21 22:30 | 185.22 | 180.74
2020-02-21 23:00 | 183.57 | 179
2020-02-21 23:30 | 182.77 | 178.25
2020-02-22 | 181.37 | 176.82
2020-02-22 00:30 | 180.72 | 176.3
2020-02-22 01:00 | 153.26 | 148.97
2020-02-22 01:30 | 181.79 | 178.51
2020-02-22 02:00 | 190 | 186.91
2020-02-22 02:30 | 189.81 | 186.59
2020-02-22 03:00 | 189.97 | 186.75
2020-02-22 03:30 | 189.74 | 186.53
2020-02-22 04:00 | 189.5 | 186.24
2020-02-22 04:30 | 189.36 | 186.12
2020-02-22 05:00 | 189.5 | 186.27
2020-02-22 05:30 | 189.77 | 186.54
2020-02-22 06:00 | 189.91 | 186.67
2020-02-22 06:30 | 190.74 | 187.47
2020-02-22 07:00 | 190.54 | 187.52
2020-02-22 07:30 | 190.84 | 187.74
2020-02-22 08:00 | 190.99 | 187.92
2020-02-22 08:30 | 190.94 | 187.99
2020-02-22 09:00 | 192.01 | 189.11
2020-02-22 09:30 | 192.15 | 189.32
2020-02-22 10:00 | 193.55 | 190.42
2020-02-22 10:30 | 192.11 | 188.76
2020-02-22 11:00 | 195.67 | 192.29
2020-02-22 11:30 | 197.57 | 194.18
2020-02-22 12:00 | 194.62 | 191.21
2020-02-22 12:30 | 194.73 | 191.3
2020-02-22 13:00 | 195.5 | 192.09
2020-02-22 13:30 | 195.95 | 192.5
2020-02-22 14:00 | 197.55 | 194.12
2020-02-22 14:30 | 197.42 | 193.98
2020-02-22 15:00 | 198.74 | 195.31
2020-02-22 15:30 | 196.98 | 193.53
2020-02-22 16:00 | 197.16 | 193.68
2020-02-22 16:30 | 197.76 | 194.26
2020-02-22 17:00 | 198.02 | 194.51
2020-02-22 17:30 | 196.98 | 193.48
2020-02-22 18:00 | 197.49 | 194.04
2020-02-22 18:30 | 198.18 | 194.73
2020-02-22 19:00 | 198.29 | 194.85
2020-02-22 19:30 | 197.68 | 194.18
2020-02-22 20:00 | 196.21 | 192.7
2020-02-22 20:30 | 195 | 191.47
2020-02-22 21:00 | 193.83 | 190.2
2020-02-22 21:30 | 193.62 | 189.92
2020-02-22 22:00 | 192.77 | 188.98
2020-02-22 22:30 | 191.61 | 187.77
2020-02-22 23:00 | 190.69 | 186.81
2020-02-22 23:30 | 190.08 | 186.06
2020-02-23 | 188.66 | 184.6
2020-02-23 00:30 | 188.13 | 184.07
2020-02-23 01:00 | 187.28 | 183.21
2020-02-23 01:30 | 186.36 | 182.31
2020-02-23 02:00 | 185.93 | 181.87
2020-02-23 02:30 | 185.77 | 181.74
2020-02-23 03:00 | 186.06 | 181.99
2020-02-23 03:30 | 185.84 | 181.79
2020-02-23 04:00 | 185.87 | 181.8
2020-02-23 04:30 | 185.64 | 181.55
2020-02-23 05:00 | 186.35 | 182.22
2020-02-23 05:30 | 186.09 | 181.96
2020-02-23 06:00 | 185.65 | 181.56
2020-02-23 06:30 | 186.05 | 181.96
2020-02-23 07:00 | 186.92 | 182.84
2020-02-23 07:30 | 188.53 | 184.52
2020-02-23 08:00 | 189.97 | 186.02
2020-02-23 08:30 | 190.65 | 186.67
2020-02-23 09:00 | 190.65 | 186.79
2020-02-23 09:30 | 191.21 | 187.41
2020-02-23 10:00 | 191.47 | 187.7
2020-02-23 10:30 | 190.06 | 186.41
2020-02-23 11:00 | 191.04 | 187.42
2020-02-23 11:30 | 191.35 | 187.77
2020-02-23 12:00 | 191.22 | 187.7
2020-02-23 12:30 | 190.47 | 186.96
2020-02-23 13:00 | 190.24 | 186.74
2020-02-23 13:30 | 189.92 | 186.38
2020-02-23 14:00 | 188.61 | 185.17
2020-02-23 14:30 | 189.79 | 186.41
2020-02-23 15:00 | 190.11 | 186.63
2020-02-23 15:30 | 190.79 | 187.29
2020-02-23 16:00 | 191.18 | 187.74
2020-02-23 16:30 | 192.43 | 188.85
2020-02-23 17:00 | 194.11 | 190.47
2020-02-23 17:30 | 194.83 | 191.26
2020-02-23 18:00 | 196.74 | 193.21
2020-02-23 18:30 | 197.23 | 193.72
2020-02-23 19:00 | 197.75 | 194.3
2020-02-23 19:30 | 196.87 | 193.41
2020-02-23 20:00 | 195.57 | 192.12
2020-02-23 20:30 | 194.6 | 191.11
2020-02-23 21:00 | 192.94 | 189.38
2020-02-23 21:30 | 192.81 | 189.09
2020-02-23 22:00 | 192.02 | 188.16
2020-02-23 22:30 | 190.76 | 186.82
2020-02-23 23:00 | 189.56 | 185.49
2020-02-23 23:30 | 189.43 | 185.31
2020-02-24 | 188.42 | 184.32
2020-02-24 00:30 | 187.7 | 183.76
2020-02-24 01:00 | 187.25 | 183.27
2020-02-24 01:30 | 186.3 | 182.35
2020-02-24 02:00 | 185.95 | 182
2020-02-24 02:30 | 185.9 | 181.99
2020-02-24 03:00 | 185.87 | 181.92
2020-02-24 03:30 | 185.56 | 181.63
2020-02-24 04:00 | 185.68 | 181.73
2020-02-24 04:30 | 185.79 | 181.89
2020-02-24 05:00 | 186.33 | 182.46
2020-02-24 05:30 | 187.69 | 183.85
2020-02-24 06:00 | 188.95 | 185.21
2020-02-24 06:30 | 191.21 | 187.62
2020-02-24 07:00 | 192.84 | 189.32
2020-02-24 07:30 | 193.63 | 190.25
2020-02-24 08:00 | 193.88 | 190.33
2020-02-24 08:30 | 193.21 | 189.64
2020-02-24 09:00 | 192.94 | 189.44
2020-02-24 09:30 | 191.99 | 188.43
2020-02-24 10:00 | 191.89 | 188.36
2020-02-24 10:30 | 191.74 | 188.16
2020-02-24 11:00 | 191.31 | 187.81
2020-02-24 11:30 | 190.75 | 187.24
2020-02-24 12:00 | 189.95 | 186.44
2020-02-24 12:30 | 190.99 | 187.48
2020-02-24 13:00 | 175.36 | 171.06
2020-02-24 13:30 | 170.97 | 165.36
2020-02-24 14:00 | 178.31 | 172.38
2020-02-24 14:30 | 178.77 | 172.91
2020-02-24 15:00 | 177.54 | 171.73
2020-02-24 15:30 | 179.1 | 172.87
2020-02-24 16:00 | 180.94 | 174.33
2020-02-24 16:30 | 182.26 | 175.53
2020-02-24 17:00 | 182.65 | 175.96
2020-02-24 17:30 | 181.84 | 174.94
2020-02-24 18:00 | 183.45 | 176.62
2020-02-24 18:30 | 185.09 | 178.19
2020-02-24 19:00 | 186.23 | 179.38
2020-02-24 19:30 | 185.06 | 178.56
2020-02-24 20:00 | 182.68 | 177.01
2020-02-24 20:30 | 181.91 | 176.12
2020-02-24 21:00 | 157.23 | 151.31
2020-02-24 21:30 | 183.59 | 179.69
2020-02-24 22:00 | 192.43 | 188.88
2020-02-24 22:30 | 190.9 | 187.32
2020-02-24 23:00 | 189.92 | 186.27
2020-02-24 23:30 | 189.08 | 185.41
2020-02-25 | 187.81 | 184.1
2020-02-25 00:30 | 187.39 | 183.54
2020-02-25 01:00 | 186.75 | 182.92
2020-02-25 01:30 | 185.95 | 182.13
2020-02-25 02:00 | 186.1 | 182.24
2020-02-25 02:30 | 185.98 | 182.14
2020-02-25 03:00 | 185.57 | 181.73
2020-02-25 03:30 | 185.88 | 182
2020-02-25 04:00 | 185.65 | 181.79
2020-02-25 04:30 | 185.95 | 182.12
2020-02-25 05:00 | 186.45 | 182.65
2020-02-25 05:30 | 187.47 | 183.72
2020-02-25 06:00 | 188.73 | 185.06
2020-02-25 06:30 | 190.97 | 187.51
2020-02-25 07:00 | 192.51 | 189.03
2020-02-25 07:30 | 193.67 | 190.38
2020-02-25 08:00 | 193.18 | 189.93
2020-02-25 08:30 | 192.55 | 189.28
2020-02-25 09:00 | 191.92 | 188.64
2020-02-25 09:30 | 191.36 | 188.06
2020-02-25 10:00 | 191.74 | 188.45
2020-02-25 10:30 | 192.23 | 188.99
2020-02-25 11:00 | 193.13 | 189.8
2020-02-25 11:30 | 194 | 190.75
2020-02-25 12:00 | 195.11 | 191.86
2020-02-25 12:30 | 197.47 | 194.12
2020-02-25 13:00 | 172.3 | 168.57
2020-02-25 13:30 | 173.74 | 169.26
2020-02-25 14:00 | 183.76 | 179.47
2020-02-25 14:30 | 184.36 | 179.89
2020-02-25 15:00 | 187.25 | 183.21
2020-02-25 15:30 | 187.79 | 183.57
2020-02-25 16:00 | 189.45 | 185.1
2020-02-25 16:30 | 190.29 | 185.68
2020-02-25 17:00 | 191.84 | 186.72
2020-02-25 17:30 | 191.96 | 186.48
2020-02-25 18:00 | 192.25 | 186.77
2020-02-25 18:30 | 193.26 | 187.76
2020-02-25 19:00 | 194.47 | 188.7
2020-02-25 19:30 | 194.58 | 188.71
2020-02-25 20:00 | 193.53 | 187.38
2020-02-25 20:30 | 190.47 | 183.97
2020-02-25 21:00 | 169.86 | 163.05
2020-02-25 21:30 | 196.65 | 192.35
2020-02-25 22:00 | 202.95 | 198.97
2020-02-25 22:30 | 199.48 | 195.94
2020-02-25 23:00 | 197.96 | 194.3
2020-02-25 23:30 | 196.02 | 192.11
2020-02-26 | 194.66 | 190.18
2020-02-26 00:30 | 194.86 | 190.34
2020-02-26 01:00 | 194.25 | 189.68
2020-02-26 01:30 | 193.9 | 189.16
2020-02-26 02:00 | 193.72 | 188.93
2020-02-26 02:30 | 193.14 | 188.28
2020-02-26 03:00 | 193.26 | 188.4
2020-02-26 03:30 | 192.81 | 187.93
2020-02-26 04:00 | 192.54 | 187.63
2020-02-26 04:30 | 192.74 | 187.87
2020-02-26 05:00 | 193.26 | 188.4
2020-02-26 05:30 | 193.84 | 189.09
2020-02-26 06:00 | 195.21 | 190.65
2020-02-26 06:30 | 196.73 | 192.37
2020-02-26 07:00 | 198.05 | 193.9
2020-02-26 07:30 | 199.77 | 195.77
2020-02-26 08:00 | 199.42 | 195.53
2020-02-26 08:30 | 198.74 | 194.89
2020-02-26 09:00 | 198.53 | 194.68
2020-02-26 09:30 | 198.27 | 194.41
2020-02-26 10:00 | 197.19 | 193.3
2020-02-26 10:30 | 198.61 | 194.93
2020-02-26 11:00 | 199.93 | 196.4
2020-02-26 11:30 | 199.39 | 196.01
2020-02-26 12:00 | 200.67 | 197.42
2020-02-26 12:30 | 200.97 | 197.71
2020-02-26 13:00 | 204.45 | 201.33
2020-02-26 13:30 | 204.75 | 201.62
2020-02-26 14:00 | 204.48 | 201.47
2020-02-26 14:30 | 204.88 | 201.94
2020-02-26 15:00 | 204.21 | 201.23
2020-02-26 15:30 | 205.18 | 202.29
2020-02-26 16:00 | 206.81 | 204.11
2020-02-26 16:30 | 207.81 | 205.04
2020-02-26 17:00 | 184.92 | 180.91
2020-02-26 17:30 | 180.53 | 174.8
2020-02-26 18:00 | 189.77 | 184.81
2020-02-26 18:30 | 191.29 | 186.76
2020-02-26 19:00 | 191.91 | 187.62
2020-02-26 19:30 | 192.17 | 187.7
2020-02-26 20:00 | 191.19 | 186.37
2020-02-26 20:30 | 189.8 | 184.34
2020-02-26 21:00 | 166.55 | 160.57
2020-02-26 21:30 | 191.28 | 187.31
2020-02-26 22:00 | 200.91 | 197.35
2020-02-26 22:30 | 198.9 | 195.08
2020-02-26 23:00 | 196.52 | 192.58
2020-02-26 23:30 | 195.84 | 191.86
2020-02-27 | 194.07 | 190.02
2020-02-27 00:30 | 193.43 | 189.38
2020-02-27 01:00 | 192.42 | 188.29
2020-02-27 01:30 | 191.65 | 187.48
2020-02-27 02:00 | 188.95 | 184.7
2020-02-27 02:30 | 189.26 | 185.04
2020-02-27 03:00 | 189.52 | 185.29
2020-02-27 03:30 | 189.74 | 185.51
2020-02-27 04:00 | 189.4 | 185.17
2020-02-27 04:30 | 189.5 | 185.27
2020-02-27 05:00 | 190.16 | 185.96
2020-02-27 05:30 | 191.04 | 186.97
2020-02-27 06:00 | 191.83 | 187.98
2020-02-27 06:30 | 194.17 | 190.56
2020-02-27 07:00 | 195.22 | 191.63
2020-02-27 07:30 | 196.54 | 193.2
2020-02-27 08:00 | 196.56 | 193.18
2020-02-27 08:30 | 195.37 | 192
2020-02-27 09:00 | 195.14 | 191.83
2020-02-27 09:30 | 195.16 | 191.82
2020-02-27 10:00 | 195.7 | 192.29
2020-02-27 10:30 | 195.88 | 192.56
2020-02-27 11:00 | 197.44 | 194.12
2020-02-27 11:30 | 199.53 | 196.26
2020-02-27 12:00 | 200.79 | 197.6
2020-02-27 12:30 | 203.19 | 199.99
2020-02-27 13:00 | 204.22 | 201.05
2020-02-27 13:30 | 203.83 | 200.96
2020-02-27 14:00 | 204.97 | 202.19
2020-02-27 14:30 | 206.97 | 204.27
2020-02-27 15:00 | 207.96 | 205.3
2020-02-27 15:30 | 206.32 | 203.75
2020-02-27 16:00 | 208.88 | 206.37
2020-02-27 16:30 | 180.37 | 176.77
2020-02-27 17:00 | 177.85 | 173.07
2020-02-27 17:30 | 186.96 | 181.93
2020-02-27 18:00 | 188.91 | 183.56
2020-02-27 18:30 | 190.01 | 184.62
2020-02-27 19:00 | 189.88 | 184.54
2020-02-27 19:30 | 188.34 | 182.96
2020-02-27 20:00 | 187.84 | 182.32
2020-02-27 20:30 | 185.19 | 179.5
2020-02-27 21:00 | 162.6 | 157.19
2020-02-27 21:30 | 189.75 | 186.3
2020-02-27 22:00 | 196.57 | 193.47
2020-02-27 22:30 | 194.3 | 191.06
2020-02-27 23:00 | 192.52 | 189.28
2020-02-27 23:30 | 191.99 | 188.62
2020-02-28 | 190.65 | 187.24
2020-02-28 00:30 | 189.98 | 186.49
2020-02-28 01:00 | 188.93 | 185.27
2020-02-28 01:30 | 188.14 | 184.46
2020-02-28 02:00 | 187.77 | 184.06
2020-02-28 02:30 | 187.29 | 183.43
2020-02-28 03:00 | 187.21 | 183.33
2020-02-28 03:30 | 187.11 | 183.22
2020-02-28 04:00 | 186.79 | 182.92
2020-02-28 04:30 | 187.04 | 183.19
2020-02-28 05:00 | 187.2 | 183.38
2020-02-28 05:30 | 187.99 | 184.18
2020-02-28 06:00 | 188.9 | 185.35
2020-02-28 06:30 | 191.04 | 187.8
2020-02-28 07:00 | 192.66 | 189.41
2020-02-28 07:30 | 193.67 | 190.52
2020-02-28 08:00 | 192.79 | 189.65
2020-02-28 08:30 | 191.56 | 188.5
2020-02-28 09:00 | 190.1 | 187.12
2020-02-28 09:30 | 188.55 | 185.41
2020-02-28 10:00 | 188.5 | 185.31
2020-02-28 10:30 | 190.57 | 187.4
2020-02-28 11:00 | 191.61 | 188.44
2020-02-28 11:30 | 193.14 | 189.95
2020-02-28 12:00 | 193.42 | 190.36
2020-02-28 12:30 | 193.88 | 190.79
2020-02-28 13:00 | 195.14 | 191.89
2020-02-28 13:30 | 195.59 | 192.37
2020-02-28 14:00 | 195.84 | 192.67
2020-02-28 14:30 | 196.18 | 193.07
2020-02-28 15:00 | 196.81 | 193.78
2020-02-28 15:30 | 197.5 | 194.49
2020-02-28 16:00 | 199.07 | 196.13
2020-02-28 16:30 | 201.75 | 198.7
2020-02-28 17:00 | 182.92 | 179.08
2020-02-28 17:30 | 176 | 170.87
2020-02-28 18:00 | 184.61 | 179.31
2020-02-28 18:30 | 184.83 | 179.76
2020-02-28 19:00 | 184.51 | 179.37
2020-02-28 19:30 | 183.98 | 178.76
2020-02-28 20:00 | 182.27 | 176.93
2020-02-28 20:30 | 179.63 | 174.8
2020-02-28 21:00 | 177.38 | 172.39
2020-02-28 21:30 | 156.61 | 151.95
2020-02-28 22:00 | 185.45 | 181.94
2020-02-28 22:30 | 192.69 | 189.14
2020-02-28 23:00 | 190.72 | 187.16
2020-02-28 23:30 | 189.92 | 186.38
2020-02-29 | 188.58 | 184.95
2020-02-29 00:30 | 187.36 | 183.69
2020-02-29 01:00 | 186.7 | 182.88
2020-02-29 01:30 | 185.95 | 182.05
2020-02-29 02:00 | 185.38 | 181.46
2020-02-29 02:30 | 184.93 | 180.95
2020-02-29 03:00 | 184.39 | 180.38
2020-02-29 03:30 | 184.53 | 180.49
2020-02-29 04:00 | 184.38 | 180.32
2020-02-29 04:30 | 184.51 | 180.45
2020-02-29 05:00 | 185.14 | 181.08
2020-02-29 05:30 | 185.19 | 181.19
2020-02-29 06:00 | 185.62 | 181.67
2020-02-29 06:30 | 185.92 | 181.97
2020-02-29 07:00 | 186.09 | 182.25
2020-02-29 07:30 | 186 | 182.18
2020-02-29 08:00 | 185.58 | 181.99
2020-02-29 08:30 | 185.06 | 181.46
2020-02-29 09:00 | 184.46 | 180.93
2020-02-29 09:30 | 183.75 | 180.17
2020-02-29 10:00 | 181.37 | 178.05
2020-02-29 10:30 | 181.49 | 178.17
2020-02-29 11:00 | 182.04 | 178.74
2020-02-29 11:30 | 183.18 | 179.97
2020-02-29 12:00 | 182.6 | 179.53
2020-02-29 12:30 | 185.63 | 182.45
2020-02-29 13:00 | 187.76 | 184.51
2020-02-29 13:30 | 189.18 | 185.95
2020-02-29 14:00 | 190.09 | 186.86
2020-02-29 14:30 | 191.64 | 188.42
2020-02-29 15:00 | 193.4 | 190.16
2020-02-29 15:30 | 194.12 | 191
2020-02-29 16:00 | 195.91 | 192.83
2020-02-29 16:30 | 197.98 | 194.94
2020-02-29 17:00 | 200.5 | 197.53
2020-02-29 17:30 | 202.4 | 199.63
2020-02-29 18:00 | 199.01 | 196.74
2020-02-29 18:30 | 188.6 | 187.86
2020-02-29 19:00 | 184.25 | 183.22
2020-02-29 19:30 | 171.62 | 169.36
2020-02-29 20:00 | 181.44 | 180.23
2020-02-29 20:30 | 171.2 | 169.22
2020-02-29 21:00 | 166.18 | 163.94
2020-02-29 21:30 | 191.9 | 188.9
2020-02-29 22:00 | 196.15 | 192.88
2020-02-29 22:30 | 194.43 | 191.09
2020-02-29 23:00 | 192.8 | 189.25
2020-02-29 23:30 | 192.26 | 188.61
2020-03-01 | 190.97 | 187.26
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 950 | 950 | 950 | 950 | 950 | 950
Transformers | H077T02 | 475 | 475 | 475 | 475 | 475 | 475
| H077T03 | 475 | 475 | 475 | 475 | 475 | 475

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2017-03-24 10:50 | H077 275KV 2 TRANSFORMER | TRANSFORMER | HV Maint | 11496.4333
2018-10-25 19:10 | 8890 - S005 Western Downs to H077 Columboola | FEEDER | Storm | 0.083333
2019-07-07 13:34 | 8892 - H077 Columboola to H076 Wandoan South | FEEDER | Secondary system malfunction or failure | 1.5667