## Cover Page
AER Rule | Field Name | Value(s)
1 | Transmission line ID | Swanbank to Redbank Plains/West Darra
2 | Constraint primary driver | Asset Condition
3 | Location of constraint (start, decimal degrees, latitude and longitude) | -27.655 | 152.818
4 | Location of constraint (end, decimal degrees, latitude and longitude) | -27.563 | 152.901
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
5 | Forecast asset rating (MVA) | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730
6 | Forecast maximum demand 10% PoE (MVA) | 337.97 | 339.64 | 334.62 | 338.95 | 341.55 | 350.12 | 346.37 | 348.43 | 347 | 379.31 | 379.31
| Forecast maximum demand 50% PoE (MVA) | 264.42 | 264.74 | 261.02 | 303.49 | 313.92 | 313.42 | 332.99 | 337.74 | 323.39 | 418.1 | 418.1
7 | Voltage Level (kV) | Financial year 2021: 110
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
8 | Maximum load at risk (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maximum load at risk (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Energy at risk (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Preferred investment | Financial year 2021: Line refit works on the 110kV transmission lines between Swanbank, Redbank Plains and West Darra substations
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
11 | Capital cost ($m, nominal) | Financial year 2030: 11
12 | Operating cost ($m, nominal) | Financial year 2030: 0.22; Financial year 2031: 0.22
13 | Preferred investment cost accuracy | Financial year 2021: 0.3
14 | Preferred investment proposed timing | Financial year 2021: 2030-06-30
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
15 | Demand reduction to defer by 1 year (MVA)
16 | Annual deferall value ($m, nominal)
17 | Historic load trace
18 | Historic line rating
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
19 | Annual economic cost of constraint ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | VCR ($m/MWh) | Financial year 2021: 0.04003
21 | Annual constraint duration
22 | Constraint duration on peak demand day

## 17. Historic load trace
Date/Time | Load (MVA) | Load (MW) | Load switching affected? | Blackstone Goodna | Date/Time | Load (MVA) | Load (MW) | Load switching affected? | Goodna West Darra
2017-03-01 00:30 | 53 | 53 |  |  | 42795.0208 | 75 | 72
2017-03-01 01:00 | 48 | 48 |  |  | 42795.0417 | 68 | 66
2017-03-01 01:30 | 45 | 45 |  |  | 42795.0625 | 65 | 61
2017-03-01 02:00 | 43 | 43 |  |  | 42795.0833 | 63 | 60
2017-03-01 02:30 | 42 | 41 |  |  | 42795.1042 | 62 | 59
2017-03-01 03:00 | 42 | 41 |  |  | 42795.125 | 61 | 58
2017-03-01 03:30 | 42 | 41 |  |  | 42795.1458 | 60 | 57
2017-03-01 04:00 | 41 | 40 |  |  | 42795.1667 | 60 | 56
2017-03-01 04:30 | 42 | 42 |  |  | 42795.1875 | 61 | 58
2017-03-01 05:00 | 45 | 45 |  |  | 42795.2083 | 65 | 61
2017-03-01 05:30 | 49 | 49 |  |  | 42795.2292 | 68 | 65
2017-03-01 06:00 | 52 | 52 |  |  | 42795.25 | 74 | 71
2017-03-01 06:30 | 61 | 61 |  |  | 42795.2708 | 85 | 84
2017-03-01 07:00 | 67 | 67 |  |  | 42795.2917 | 93 | 92
2017-03-01 07:30 | 73 | 73 |  |  | 42795.3125 | 101 | 100
2017-03-01 08:00 | 73 | 73 |  |  | 42795.3333 | 105 | 101
2017-03-01 08:30 | 75 | 75 |  |  | 42795.3542 | 108 | 104
2017-03-01 09:00 | 75 | 75 |  |  | 42795.375 | 111 | 105
2017-03-01 09:30 | 77 | 76 |  |  | 42795.3958 | 115 | 108
2017-03-01 10:00 | 78 | 78 |  |  | 42795.4167 | 116 | 110
2017-03-01 10:30 | 79 | 79 |  |  | 42795.4375 | 117 | 111
2017-03-01 11:00 | 81 | 80 |  |  | 42795.4583 | 118 | 111
2017-03-01 11:30 | 80 | 80 |  |  | 42795.4792 | 116 | 110
2017-03-01 12:00 | 80 | 80 |  |  | 42795.5 | 120 | 113
2017-03-01 12:30 | 80 | 80 |  |  | 42795.5208 | 121 | 113
2017-03-01 13:00 | 82 | 82 |  |  | 42795.5417 | 122 | 114
2017-03-01 13:30 | 83 | 83 |  |  | 42795.5625 | 122 | 114
2017-03-01 14:00 | 85 | 85 |  |  | 42795.5833 | 121 | 113
2017-03-01 14:30 | 85 | 85 |  |  | 42795.6042 | 123 | 115
2017-03-01 15:00 | 85 | 85 |  |  | 42795.625 | 125 | 118
2017-03-01 15:30 | 85 | 85 |  |  | 42795.6458 | 129 | 120
2017-03-01 16:00 | 88 | 88 |  |  | 42795.6667 | 131 | 122
2017-03-01 16:30 | 89 | 89 |  |  | 42795.6875 | 129 | 121
2017-03-01 17:00 | 91 | 91 |  |  | 42795.7083 | 128 | 121
2017-03-01 17:30 | 91 | 91 |  |  | 42795.7292 | 124 | 117
2017-03-01 18:00 | 89 | 88 |  |  | 42795.75 | 115 | 113
2017-03-01 18:30 | 87 | 86 |  |  | 42795.7708 | 111 | 110
2017-03-01 19:00 | 92 | 90 |  |  | 42795.7917 | 115 | 115
2017-03-01 19:30 | 91 | 90 |  |  | 42795.8125 | 115 | 114
2017-03-01 20:00 | 89 | 88 |  |  | 42795.8333 | 111 | 111
2017-03-01 20:30 | 88 | 87 |  |  | 42795.8542 | 110 | 109
2017-03-01 21:00 | 83 | 82 |  |  | 42795.875 | 104 | 104
2017-03-01 21:30 | 78 | 77 |  |  | 42795.8958 | 99 | 98
2017-03-01 22:00 | 73 | 71 |  |  | 42795.9167 | 95 | 94
2017-03-01 22:30 | 71 | 70 |  |  | 42795.9375 | 92 | 91
2017-03-01 23:00 | 73 | 72 |  |  | 42795.9583 | 93 | 92
2017-03-01 23:30 | 69 | 68 |  |  | 42795.9792 | 89 | 89
2017-03-02 | 62 | 61 |  |  | 42796 | 82 | 81
2017-03-02 00:30 | 58 | 56 |  |  | 42796.0208 | 76 | 75
2017-03-02 01:00 | 56 | 54 |  |  | 42796.0417 | 73 | 72
2017-03-02 01:30 | 52 | 50 |  |  | 42796.0625 | 69 | 68
2017-03-02 02:00 | 50 | 49 |  |  | 42796.0833 | 67 | 66
2017-03-02 02:30 | 50 | 48 |  |  | 42796.1042 | 66 | 65
2017-03-02 03:00 | 50 | 48 |  |  | 42796.125 | 66 | 65
2017-03-02 03:30 | 48 | 46 |  |  | 42796.1458 | 64 | 63
2017-03-02 04:00 | 47 | 45 |  |  | 42796.1667 | 65 | 64
2017-03-02 04:30 | 48 | 47 |  |  | 42796.1875 | 65 | 64
2017-03-02 05:00 | 50 | 48 |  |  | 42796.2083 | 66 | 65
2017-03-02 05:30 | 52 | 50 |  |  | 42796.2292 | 70 | 70
2017-03-02 06:00 | 57 | 55 |  |  | 42796.25 | 76 | 76
2017-03-02 06:30 | 63 | 62 |  |  | 42796.2708 | 89 | 88
2017-03-02 07:00 | 70 | 68 |  |  | 42796.2917 | 96 | 96
2017-03-02 07:30 | 77 | 74 |  |  | 42796.3125 | 104 | 103
2017-03-02 08:00 | 77 | 75 |  |  | 42796.3333 | 107 | 106
2017-03-02 08:30 | 79 | 77 |  |  | 42796.3542 | 110 | 107
2017-03-02 09:00 | 87 | 86 |  |  | 42796.375 | 126 | 122
2017-03-02 09:30 | 91 | 91 |  |  | 42796.3958 | 133 | 129
2017-03-02 10:00 | 91 | 90 |  |  | 42796.4167 | 133 | 129
2017-03-02 10:30 | 91 | 91 |  |  | 42796.4375 | 133 | 127
2017-03-02 11:00 | 92 | 92 |  |  | 42796.4583 | 136 | 129
2017-03-02 11:30 | 90 | 90 |  |  | 42796.4792 | 135 | 127
2017-03-02 12:00 | 97 | 97 |  |  | 42796.5 | 142 | 136
2017-03-02 12:30 | 101 | 101 |  |  | 42796.5208 | 145 | 137
2017-03-02 13:00 | 103 | 103 |  |  | 42796.5417 | 143 | 136
2017-03-02 13:30 | 95 | 95 |  |  | 42796.5625 | 140 | 132
2017-03-02 14:00 | 97 | 97 |  |  | 42796.5833 | 145 | 138
2017-03-02 14:30 | 99 | 99 |  |  | 42796.6042 | 148 | 139
2017-03-02 15:00 | 98 | 98 |  |  | 42796.625 | 148 | 139
2017-03-02 15:30 | 101 | 101 |  |  | 42796.6458 | 145 | 138
2017-03-02 16:00 | 102 | 102 |  |  | 42796.6667 | 146 | 139
2017-03-02 16:30 | 100 | 100 |  |  | 42796.6875 | 145 | 138
2017-03-02 17:00 | 92 | 92 |  |  | 42796.7083 | 131 | 124
2017-03-02 17:30 | 91 | 90 |  |  | 42796.7292 | 126 | 118
2017-03-02 18:00 | 91 | 90 |  |  | 42796.75 | 117 | 116
2017-03-02 18:30 | 93 | 90 |  |  | 42796.7708 | 114 | 114
2017-03-02 19:00 | 97 | 94 |  |  | 42796.7917 | 120 | 119
2017-03-02 19:30 | 97 | 94 |  |  | 42796.8125 | 119 | 119
2017-03-02 20:00 | 96 | 94 |  |  | 42796.8333 | 119 | 119
2017-03-02 20:30 | 96 | 94 |  |  | 42796.8542 | 118 | 118
2017-03-02 21:00 | 92 | 88 |  |  | 42796.875 | 111 | 111
2017-03-02 21:30 | 86 | 82 |  |  | 42796.8958 | 105 | 104
2017-03-02 22:00 | 82 | 79 |  |  | 42796.9167 | 101 | 100
2017-03-02 22:30 | 79 | 76 |  |  | 42796.9375 | 98 | 97
2017-03-02 23:00 | 81 | 76 |  |  | 42796.9583 | 98 | 98
2017-03-02 23:30 | 74 | 72 |  |  | 42796.9792 | 94 | 94
2017-03-03 | 67 | 65 |  |  | 42797 | 86 | 85
2017-03-03 00:30 | 63 | 61 |  |  | 42797.0208 | 82 | 81
2017-03-03 01:00 | 60 | 58 |  |  | 42797.0417 | 77 | 76
2017-03-03 01:30 | 55 | 53 |  |  | 42797.0625 | 71 | 70
2017-03-03 02:00 | 53 | 51 |  |  | 42797.0833 | 69 | 68
2017-03-03 02:30 | 52 | 51 |  |  | 42797.1042 | 68 | 67
2017-03-03 03:00 | 51 | 50 |  |  | 42797.125 | 68 | 67
2017-03-03 03:30 | 51 | 50 |  |  | 42797.1458 | 67 | 66
2017-03-03 04:00 | 51 | 50 |  |  | 42797.1667 | 67 | 65
2017-03-03 04:30 | 50 | 49 |  |  | 42797.1875 | 66 | 64
2017-03-03 05:00 | 51 | 49 |  |  | 42797.2083 | 67 | 66
2017-03-03 05:30 | 56 | 54 |  |  | 42797.2292 | 72 | 72
2017-03-03 06:00 | 59 | 57 |  |  | 42797.25 | 77 | 76
2017-03-03 06:30 | 67 | 65 |  |  | 42797.2708 | 88 | 88
2017-03-03 07:00 | 71 | 70 |  |  | 42797.2917 | 97 | 96
2017-03-03 07:30 | 76 | 75 |  |  | 42797.3125 | 105 | 105
2017-03-03 08:00 | 77 | 76 |  |  | 42797.3333 | 109 | 107
2017-03-03 08:30 | 78 | 76 |  |  | 42797.3542 | 110 | 109
2017-03-03 09:00 | 82 | 81 |  |  | 42797.375 | 115 | 113
2017-03-03 09:30 | 89 | 87 |  |  | 42797.3958 | 122 | 120
2017-03-03 10:00 | 100 | 96 |  |  | 42797.4167 | 139 | 134
2017-03-03 10:30 | 100 | 97 |  |  | 42797.4375 | 137 | 133
2017-03-03 11:00 | 100 | 97 |  |  | 42797.4583 | 137 | 132
2017-03-03 11:30 | 101 | 98 |  |  | 42797.4792 | 137 | 133
2017-03-03 12:00 | 105 | 102 |  |  | 42797.5 | 141 | 137
2017-03-03 12:30 | 104 | 101 |  |  | 42797.5208 | 143 | 139
2017-03-03 13:00 | 107 | 104 |  |  | 42797.5417 | 147 | 142
2017-03-03 13:30 | 107 | 104 |  |  | 42797.5625 | 144 | 139
2017-03-03 14:00 | 102 | 99 |  |  | 42797.5833 | 142 | 137
2017-03-03 14:30 | 102 | 101 |  |  | 42797.6042 | 146 | 143
2017-03-03 15:00 | 104 | 104 |  |  | 42797.625 | 148 | 146
2017-03-03 15:30 | 107 | 104 |  |  | 42797.6458 | 152 | 146
2017-03-03 16:00 | 106 | 99 |  |  | 42797.6667 | 149 | 136
2017-03-03 16:30 | 104 | 97 |  |  | 42797.6875 | 143 | 129
2017-03-03 17:00 | 104 | 96 |  |  | 42797.7083 | 141 | 126
2017-03-03 17:30 | 101 | 93 |  |  | 42797.7292 | 134 | 122
2017-03-03 18:00 | 95 | 89 |  |  | 42797.75 | 124 | 115
2017-03-03 18:30 | 90 | 88 |  |  | 42797.7708 | 114 | 112
2017-03-03 19:00 | 93 | 89 |  |  | 42797.7917 | 118 | 113
2017-03-03 19:30 | 92 | 87 |  |  | 42797.8125 | 116 | 111
2017-03-03 20:00 | 91 | 86 |  |  | 42797.8333 | 115 | 110
2017-03-03 20:30 | 90 | 85 |  |  | 42797.8542 | 113 | 107
2017-03-03 21:00 | 83 | 80 |  |  | 42797.875 | 103 | 101
2017-03-03 21:30 | 78 | 76 |  |  | 42797.8958 | 97 | 96
2017-03-03 22:00 | 80 | 74 |  |  | 42797.9167 | 94 | 94
2017-03-03 22:30 | 80 | 70 |  |  | 42797.9375 | 91 | 91
2017-03-03 23:00 | 83 | 74 |  |  | 42797.9583 | 94 | 94
2017-03-03 23:30 | 81 | 71 |  |  | 42797.9792 | 92 | 91
2017-03-04 | 75 | 65 |  |  | 42798 | 84 | 83
2017-03-04 00:30 | 71 | 60 |  |  | 42798.0208 | 80 | 79
2017-03-04 01:00 | 68 | 57 |  |  | 42798.0417 | 75 | 75
2017-03-04 01:30 | 63 | 51 |  |  | 42798.0625 | 71 | 70
2017-03-04 02:00 | 61 | 49 |  |  | 42798.0833 | 68 | 67
2017-03-04 02:30 | 61 | 48 |  |  | 42798.1042 | 66 | 65
2017-03-04 03:00 | 62 | 48 |  |  | 42798.125 | 66 | 65
2017-03-04 03:30 | 62 | 48 |  |  | 42798.1458 | 65 | 64
2017-03-04 04:00 | 62 | 47 |  |  | 42798.1667 | 65 | 64
2017-03-04 04:30 | 62 | 48 |  |  | 42798.1875 | 64 | 63
2017-03-04 05:00 | 61 | 47 |  |  | 42798.2083 | 65 | 64
2017-03-04 05:30 | 62 | 48 |  |  | 42798.2292 | 67 | 66
2017-03-04 06:00 | 62 | 50 |  |  | 42798.25 | 68 | 67
2017-03-04 06:30 | 63 | 50 |  |  | 42798.2708 | 71 | 70
2017-03-04 07:00 | 65 | 54 |  |  | 42798.2917 | 75 | 74
2017-03-04 07:30 | 63 | 52 |  |  | 42798.3125 | 74 | 74
2017-03-04 08:00 | 63 | 52 |  |  | 42798.3333 | 76 | 76
2017-03-04 08:30 | 65 | 55 |  |  | 42798.3542 | 77 | 77
2017-03-04 09:00 | 68 | 59 |  |  | 42798.375 | 84 | 84
2017-03-04 09:30 | 79 | 72 |  |  | 42798.3958 | 98 | 98
2017-03-04 10:00 | 80 | 74 |  |  | 42798.4167 | 101 | 101
2017-03-04 10:30 | 80 | 75 |  |  | 42798.4375 | 102 | 102
2017-03-04 11:00 | 79 | 73 |  |  | 42798.4583 | 101 | 101
2017-03-04 11:30 | 77 | 72 |  |  | 42798.4792 | 96 | 96
2017-03-04 12:00 | 77 | 71 |  |  | 42798.5 | 95 | 95
2017-03-04 12:30 | 77 | 72 |  |  | 42798.5208 | 100 | 100
2017-03-04 13:00 | 81 | 76 |  |  | 42798.5417 | 101 | 101
2017-03-04 13:30 | 83 | 79 |  |  | 42798.5625 | 103 | 103
2017-03-04 14:00 | 86 | 81 |  |  | 42798.5833 | 105 | 105
2017-03-04 14:30 | 87 | 82 |  |  | 42798.6042 | 107 | 107
2017-03-04 15:00 | 86 | 82 |  |  | 42798.625 | 104 | 104
2017-03-04 15:30 | 84 | 79 |  |  | 42798.6458 | 104 | 104
2017-03-04 16:00 | 81 | 76 |  |  | 42798.6667 | 101 | 101
2017-03-04 16:30 | 82 | 78 |  |  | 42798.6875 | 102 | 102
2017-03-04 17:00 | 82 | 78 |  |  | 42798.7083 | 102 | 102
2017-03-04 17:30 | 81 | 76 |  |  | 42798.7292 | 99 | 99
2017-03-04 18:00 | 80 | 74 |  |  | 42798.75 | 98 | 98
2017-03-04 18:30 | 83 | 76 |  |  | 42798.7708 | 99 | 99
2017-03-04 19:00 | 87 | 79 |  |  | 42798.7917 | 104 | 103
2017-03-04 19:30 | 86 | 78 |  |  | 42798.8125 | 103 | 102
2017-03-04 20:00 | 85 | 79 |  |  | 42798.8333 | 103 | 103
2017-03-04 20:30 | 84 | 76 |  |  | 42798.8542 | 100 | 100
2017-03-04 21:00 | 82 | 74 |  |  | 42798.875 | 97 | 96
2017-03-04 21:30 | 79 | 71 |  |  | 42798.8958 | 93 | 92
2017-03-04 22:00 | 78 | 70 |  |  | 42798.9167 | 92 | 91
2017-03-04 22:30 | 77 | 69 |  |  | 42798.9375 | 89 | 88
2017-03-04 23:00 | 84 | 71 |  |  | 42798.9583 | 92 | 90
2017-03-04 23:30 | 84 | 70 |  |  | 42798.9792 | 91 | 89
2017-03-05 | 79 | 64 |  |  | 42799 | 84 | 83
2017-03-05 00:30 | 71 | 59 |  |  | 42799.0208 | 79 | 79
2017-03-05 01:00 | 68 | 55 |  |  | 42799.0417 | 73 | 72
2017-03-05 01:30 | 64 | 50 |  |  | 42799.0625 | 67 | 67
2017-03-05 02:00 | 63 | 47 |  |  | 42799.0833 | 63 | 63
2017-03-05 02:30 | 62 | 46 |  |  | 42799.1042 | 61 | 61
2017-03-05 03:00 | 60 | 43 |  |  | 42799.125 | 59 | 59
2017-03-05 03:30 | 59 | 42 |  |  | 42799.1458 | 58 | 57
2017-03-05 04:00 | 58 | 41 |  |  | 42799.1667 | 58 | 58
2017-03-05 04:30 | 58 | 41 |  |  | 42799.1875 | 57 | 57
2017-03-05 05:00 | 58 | 41 |  |  | 42799.2083 | 57 | 57
2017-03-05 05:30 | 58 | 41 |  |  | 42799.2292 | 59 | 58
2017-03-05 06:00 | 60 | 44 |  |  | 42799.25 | 62 | 62
2017-03-05 06:30 | 60 | 43 |  |  | 42799.2708 | 62 | 62
2017-03-05 07:00 | 60 | 44 |  |  | 42799.2917 | 65 | 64
2017-03-05 07:30 | 60 | 45 |  |  | 42799.3125 | 66 | 66
2017-03-05 08:00 | 62 | 48 |  |  | 42799.3333 | 69 | 69
2017-03-05 08:30 | 68 | 56 |  |  | 42799.3542 | 76 | 76
2017-03-05 09:00 | 72 | 62 |  |  | 42799.375 | 83 | 82
2017-03-05 09:30 | 68 | 59 |  |  | 42799.3958 | 81 | 81
2017-03-05 10:00 | 67 | 58 |  |  | 42799.4167 | 79 | 79
2017-03-05 10:30 | 69 | 59 |  |  | 42799.4375 | 80 | 80
2017-03-05 11:00 | 73 | 64 |  |  | 42799.4583 | 85 | 85
2017-03-05 11:30 | 75 | 67 |  |  | 42799.4792 | 87 | 87
2017-03-05 12:00 | 76 | 67 |  |  | 42799.5 | 88 | 88
2017-03-05 12:30 | 76 | 67 |  |  | 42799.5208 | 86 | 86
2017-03-05 13:00 | 78 | 71 |  |  | 42799.5417 | 91 | 91
2017-03-05 13:30 | 82 | 74 |  |  | 42799.5625 | 94 | 94
2017-03-05 14:00 | 87 | 78 |  |  | 42799.5833 | 96 | 95
2017-03-05 14:30 | 91 | 79 |  |  | 42799.6042 | 102 | 98
2017-03-05 15:00 | 95 | 80 |  |  | 42799.625 | 105 | 98
2017-03-05 15:30 | 99 | 84 |  |  | 42799.6458 | 110 | 103
2017-03-05 16:00 | 102 | 88 |  |  | 42799.6667 | 113 | 107
2017-03-05 16:30 | 102 | 88 |  |  | 42799.6875 | 114 | 106
2017-03-05 17:00 | 103 | 89 |  |  | 42799.7083 | 115 | 107
2017-03-05 17:30 | 102 | 88 |  |  | 42799.7292 | 114 | 107
2017-03-05 18:00 | 104 | 88 |  |  | 42799.75 | 116 | 107
2017-03-05 18:30 | 104 | 88 |  |  | 42799.7708 | 117 | 109
2017-03-05 19:00 | 103 | 90 |  |  | 42799.7917 | 120 | 113
2017-03-05 19:30 | 101 | 90 |  |  | 42799.8125 | 116 | 112
2017-03-05 20:00 | 102 | 90 |  |  | 42799.8333 | 116 | 112
2017-03-05 20:30 | 101 | 90 |  |  | 42799.8542 | 114 | 110
2017-03-05 21:00 | 97 | 84 |  |  | 42799.875 | 108 | 104
2017-03-05 21:30 | 91 | 79 |  |  | 42799.8958 | 101 | 98
2017-03-05 22:00 | 89 | 78 |  |  | 42799.9167 | 100 | 97
2017-03-05 22:30 | 84 | 72 |  |  | 42799.9375 | 95 | 93
2017-03-05 23:00 | 85 | 72 |  |  | 42799.9583 | 94 | 92
2017-03-05 23:30 | 82 | 70 |  |  | 42799.9792 | 90 | 89
2017-03-06 | 77 | 64 |  |  | 42800 | 84 | 83
2017-03-06 00:30 | 74 | 60 |  |  | 42800.0208 | 80 | 79
2017-03-06 01:00 | 72 | 57 |  |  | 42800.0417 | 76 | 75
2017-03-06 01:30 | 69 | 54 |  |  | 42800.0625 | 73 | 72
2017-03-06 02:00 | 66 | 52 |  |  | 42800.0833 | 70 | 69
2017-03-06 02:30 | 64 | 50 |  |  | 42800.1042 | 67 | 67
2017-03-06 03:00 | 64 | 50 |  |  | 42800.125 | 67 | 67
2017-03-06 03:30 | 63 | 49 |  |  | 42800.1458 | 65 | 64
2017-03-06 04:00 | 64 | 49 |  |  | 42800.1667 | 65 | 65
2017-03-06 04:30 | 62 | 47 |  |  | 42800.1875 | 64 | 63
2017-03-06 05:00 | 62 | 49 |  |  | 42800.2083 | 66 | 65
2017-03-06 05:30 | 63 | 52 |  |  | 42800.2292 | 71 | 70
2017-03-06 06:00 | 66 | 58 |  |  | 42800.25 | 78 | 78
2017-03-06 06:30 | 74 | 67 |  |  | 42800.2708 | 91 | 91
2017-03-06 07:00 | 80 | 71 |  |  | 42800.2917 | 96 | 96
2017-03-06 07:30 | 86 | 78 |  |  | 42800.3125 | 106 | 106
2017-03-06 08:00 | 91 | 82 |  |  | 42800.3333 | 113 | 112
2017-03-06 08:30 | 93 | 83 |  |  | 42800.3542 | 115 | 114
2017-03-06 09:00 | 93 | 86 |  |  | 42800.375 | 117 | 116
2017-03-06 09:30 | 95 | 89 |  |  | 42800.3958 | 120 | 119
2017-03-06 10:00 | 96 | 90 |  |  | 42800.4167 | 120 | 120
2017-03-06 10:30 | 96 | 91 |  |  | 42800.4375 | 121 | 120
2017-03-06 11:00 | 97 | 91 |  |  | 42800.4583 | 121 | 121
2017-03-06 11:30 | 97 | 91 |  |  | 42800.4792 | 122 | 122
2017-03-06 12:00 | 98 | 93 |  |  | 42800.5 | 124 | 124
2017-03-06 12:30 | 102 | 95 |  |  | 42800.5208 | 129 | 128
2017-03-06 13:00 | 103 | 95 |  |  | 42800.5417 | 131 | 129
2017-03-06 13:30 | 104 | 97 |  |  | 42800.5625 | 131 | 129
2017-03-06 14:00 | 106 | 99 |  |  | 42800.5833 | 133 | 131
2017-03-06 14:30 | 109 | 103 |  |  | 42800.6042 | 135 | 133
2017-03-06 15:00 | 108 | 101 |  |  | 42800.625 | 133 | 131
2017-03-06 15:30 | 107 | 99 |  |  | 42800.6458 | 129 | 128
2017-03-06 16:00 | 110 | 103 |  |  | 42800.6667 | 133 | 132
2017-03-06 16:30 | 106 | 99 |  |  | 42800.6875 | 132 | 131
2017-03-06 17:00 | 101 | 95 |  |  | 42800.7083 | 130 | 128
2017-03-06 17:30 | 102 | 93 |  |  | 42800.7292 | 125 | 125
2017-03-06 18:00 | 105 | 90 |  |  | 42800.75 | 120 | 120
2017-03-06 18:30 | 102 | 87 |  |  | 42800.7708 | 115 | 115
2017-03-06 19:00 | 103 | 88 |  |  | 42800.7917 | 118 | 117
2017-03-06 19:30 | 102 | 87 |  |  | 42800.8125 | 117 | 117
2017-03-06 20:00 | 101 | 86 |  |  | 42800.8333 | 114 | 114
2017-03-06 20:30 | 99 | 84 |  |  | 42800.8542 | 112 | 112
2017-03-06 21:00 | 102 | 87 |  |  | 42800.875 | 111 | 110
2017-03-06 21:30 | 98 | 82 |  |  | 42800.8958 | 105 | 104
2017-03-06 22:00 | 96 | 78 |  |  | 42800.9167 | 100 | 99
2017-03-06 22:30 | 79 | 73 |  |  | 42800.9375 | 94 | 92
2017-03-06 23:00 | 76 | 72 |  |  | 42800.9583 | 95 | 92
2017-03-06 23:30 | 73 | 68 |  |  | 42800.9792 | 91 | 88
2017-03-07 | 68 | 64 |  |  | 42801 | 85 | 81
2017-03-07 00:30 | 64 | 59 |  |  | 42801.0208 | 82 | 79
2017-03-07 01:00 | 64 | 56 |  |  | 42801.0417 | 79 | 76
2017-03-07 01:30 | 62 | 53 |  |  | 42801.0625 | 74 | 71
2017-03-07 02:00 | 59 | 50 |  |  | 42801.0833 | 70 | 67
2017-03-07 02:30 | 57 | 48 |  |  | 42801.1042 | 69 | 66
2017-03-07 03:00 | 57 | 47 |  |  | 42801.125 | 68 | 64
2017-03-07 03:30 | 55 | 46 |  |  | 42801.1458 | 64 | 61
2017-03-07 04:00 | 56 | 47 |  |  | 42801.1667 | 64 | 61
2017-03-07 04:30 | 55 | 46 |  |  | 42801.1875 | 64 | 61
2017-03-07 05:00 | 57 | 49 |  |  | 42801.2083 | 68 | 65
2017-03-07 05:30 | 60 | 52 |  |  | 42801.2292 | 75 | 71
2017-03-07 06:00 | 66 | 58 |  |  | 42801.25 | 81 | 77
2017-03-07 06:30 | 67 | 65 |  |  | 42801.2708 | 89 | 88
2017-03-07 07:00 | 70 | 69 |  |  | 42801.2917 | 95 | 95
2017-03-07 07:30 | 75 | 75 |  |  | 42801.3125 | 103 | 103
2017-03-07 08:00 | 79 | 78 |  |  | 42801.3333 | 107 | 106
2017-03-07 08:30 | 78 | 77 |  |  | 42801.3542 | 109 | 108
2017-03-07 09:00 | 77 | 77 |  |  | 42801.375 | 109 | 109
2017-03-07 09:30 | 84 | 84 |  |  | 42801.3958 | 109 | 109
2017-03-07 10:00 | 84 | 84 |  |  | 42801.4167 | 109 | 108
2017-03-07 10:30 | 84 | 83 |  |  | 42801.4375 | 109 | 108
2017-03-07 11:00 | 84 | 84 |  |  | 42801.4583 | 108 | 107
2017-03-07 11:30 | 82 | 82 |  |  | 42801.4792 | 108 | 107
2017-03-07 12:00 | 83 | 83 |  |  | 42801.5 | 109 | 108
2017-03-07 12:30 | 82 | 82 |  |  | 42801.5208 | 113 | 112
2017-03-07 13:00 | 84 | 83 |  |  | 42801.5417 | 114 | 113
2017-03-07 13:30 | 87 | 86 |  |  | 42801.5625 | 116 | 116
2017-03-07 14:00 | 89 | 89 |  |  | 42801.5833 | 118 | 117
2017-03-07 14:30 | 91 | 90 |  |  | 42801.6042 | 119 | 119
2017-03-07 15:00 | 91 | 91 |  |  | 42801.625 | 121 | 121
2017-03-07 15:30 | 90 | 90 |  |  | 42801.6458 | 118 | 117
2017-03-07 16:00 | 91 | 90 |  |  | 42801.6667 | 118 | 117
2017-03-07 16:30 | 91 | 90 |  |  | 42801.6875 | 119 | 118
2017-03-07 17:00 | 91 | 91 |  |  | 42801.7083 | 119 | 118
2017-03-07 17:30 | 91 | 90 |  |  | 42801.7292 | 117 | 115
2017-03-07 18:00 | 88 | 88 |  |  | 42801.75 | 113 | 112
2017-03-07 18:30 | 84 | 84 |  |  | 42801.7708 | 109 | 107
2017-03-07 19:00 | 87 | 86 |  |  | 42801.7917 | 111 | 109
2017-03-07 19:30 | 84 | 84 |  |  | 42801.8125 | 108 | 107
2017-03-07 20:00 | 82 | 81 |  |  | 42801.8333 | 105 | 104
2017-03-07 20:30 | 81 | 81 |  |  | 42801.8542 | 103 | 102
2017-03-07 21:00 | 77 | 77 |  |  | 42801.875 | 99 | 99
2017-03-07 21:30 | 75 | 75 |  |  | 42801.8958 | 95 | 94
2017-03-07 22:00 | 73 | 73 |  |  | 42801.9167 | 93 | 93
2017-03-07 22:30 | 69 | 68 |  |  | 42801.9375 | 88 | 88
2017-03-07 23:00 | 67 | 67 |  |  | 42801.9583 | 86 | 85
2017-03-07 23:30 | 63 | 61 |  |  | 42801.9792 | 80 | 79
2017-03-08 | 59 | 56 |  |  | 42802 | 77 | 76
2017-03-08 00:30 | 56 | 53 |  |  | 42802.0208 | 74 | 73
2017-03-08 01:00 | 57 | 53 |  |  | 42802.0417 | 73 | 71
2017-03-08 01:30 | 55 | 51 |  |  | 42802.0625 | 70 | 68
2017-03-08 02:00 | 54 | 50 |  |  | 42802.0833 | 68 | 66
2017-03-08 02:30 | 52 | 48 |  |  | 42802.1042 | 66 | 64
2017-03-08 03:00 | 49 | 45 |  |  | 42802.125 | 64 | 62
2017-03-08 03:30 | 49 | 46 |  |  | 42802.1458 | 64 | 62
2017-03-08 04:00 | 48 | 45 |  |  | 42802.1667 | 63 | 61
2017-03-08 04:30 | 49 | 46 |  |  | 42802.1875 | 64 | 62
2017-03-08 05:00 | 50 | 48 |  |  | 42802.2083 | 66 | 65
2017-03-08 05:30 | 52 | 50 |  |  | 42802.2292 | 69 | 69
2017-03-08 06:00 | 52 | 51 |  |  | 42802.25 | 69 | 69
2017-03-08 06:30 | 57 | 56 |  |  | 42802.2708 | 78 | 77
2017-03-08 07:00 | 60 | 60 |  |  | 42802.2917 | 84 | 84
2017-03-08 07:30 | 66 | 65 |  |  | 42802.3125 | 93 | 93
2017-03-08 08:00 | 69 | 69 |  |  | 42802.3333 | 97 | 97
2017-03-08 08:30 | 69 | 69 |  |  | 42802.3542 | 97 | 97
2017-03-08 09:00 | 77 | 76 |  |  | 42802.375 | 109 | 109
2017-03-08 09:30 | 77 | 77 |  |  | 42802.3958 | 108 | 108
2017-03-08 10:00 | 80 | 80 |  |  | 42802.4167 | 111 | 111
2017-03-08 10:30 | 79 | 79 |  |  | 42802.4375 | 111 | 110
2017-03-08 11:00 | 81 | 81 |  |  | 42802.4583 | 112 | 112
2017-03-08 11:30 | 72 | 71 |  |  | 42802.4792 | 102 | 102
2017-03-08 12:00 | 72 | 71 |  |  | 42802.5 | 101 | 101
2017-03-08 12:30 | 73 | 73 |  |  | 42802.5208 | 104 | 104
2017-03-08 13:00 | 74 | 73 |  |  | 42802.5417 | 103 | 103
2017-03-08 13:30 | 75 | 74 |  |  | 42802.5625 | 106 | 106
2017-03-08 14:00 | 75 | 75 |  |  | 42802.5833 | 105 | 105
2017-03-08 14:30 | 75 | 75 |  |  | 42802.6042 | 105 | 105
2017-03-08 15:00 | 79 | 79 |  |  | 42802.625 | 110 | 110
2017-03-08 15:30 | 83 | 82 |  |  | 42802.6458 | 113 | 113
2017-03-08 16:00 | 83 | 82 |  |  | 42802.6667 | 113 | 113
2017-03-08 16:30 | 82 | 82 |  |  | 42802.6875 | 112 | 112
2017-03-08 17:00 | 81 | 80 |  |  | 42802.7083 | 110 | 109
2017-03-08 17:30 | 76 | 75 |  |  | 42802.7292 | 102 | 102
2017-03-08 18:00 | 73 | 72 |  |  | 42802.75 | 98 | 97
2017-03-08 18:30 | 73 | 72 |  |  | 42802.7708 | 96 | 96
2017-03-08 19:00 | 77 | 77 |  |  | 42802.7917 | 100 | 99
2017-03-08 19:30 | 76 | 75 |  |  | 42802.8125 | 98 | 98
2017-03-08 20:00 | 76 | 75 |  |  | 42802.8333 | 96 | 96
2017-03-08 20:30 | 72 | 71 |  |  | 42802.8542 | 93 | 92
2017-03-08 21:00 | 68 | 67 |  |  | 42802.875 | 89 | 89
2017-03-08 21:30 | 64 | 63 |  |  | 42802.8958 | 84 | 83
2017-03-08 22:00 | 60 | 59 |  |  | 42802.9167 | 79 | 78
2017-03-08 22:30 | 58 | 57 |  |  | 42802.9375 | 74 | 74
2017-03-08 23:00 | 59 | 57 |  |  | 42802.9583 | 77 | 75
2017-03-08 23:30 | 57 | 55 |  |  | 42802.9792 | 75 | 74
2017-03-09 | 52 | 50 |  |  | 42803 | 69 | 68
2017-03-09 00:30 | 51 | 50 |  |  | 42803.0208 | 70 | 69
2017-03-09 01:00 | 53 | 50 |  |  | 42803.0417 | 69 | 68
2017-03-09 01:30 | 48 | 46 |  |  | 42803.0625 | 64 | 63
2017-03-09 02:00 | 46 | 43 |  |  | 42803.0833 | 61 | 60
2017-03-09 02:30 | 44 | 41 |  |  | 42803.1042 | 59 | 57
2017-03-09 03:00 | 42 | 38 |  |  | 42803.125 | 56 | 54
2017-03-09 03:30 | 42 | 39 |  |  | 42803.1458 | 55 | 54
2017-03-09 04:00 | 43 | 40 |  |  | 42803.1667 | 56 | 54
2017-03-09 04:30 | 43 | 40 |  |  | 42803.1875 | 56 | 55
2017-03-09 05:00 | 43 | 41 |  |  | 42803.2083 | 57 | 56
2017-03-09 05:30 | 46 | 45 |  |  | 42803.2292 | 62 | 61
2017-03-09 06:00 | 52 | 51 |  |  | 42803.25 | 68 | 68
2017-03-09 06:30 | 59 | 58 |  |  | 42803.2708 | 80 | 79
2017-03-09 07:00 | 64 | 63 |  |  | 42803.2917 | 87 | 87
2017-03-09 07:30 | 68 | 67 |  |  | 42803.3125 | 93 | 93
2017-03-09 08:00 | 68 | 67 |  |  | 42803.3333 | 94 | 94
2017-03-09 08:30 | 70 | 70 |  |  | 42803.3542 | 95 | 95
2017-03-09 09:00 | 70 | 70 |  |  | 42803.375 | 97 | 96
2017-03-09 09:30 | 71 | 71 |  |  | 42803.3958 | 98 | 98
2017-03-09 10:00 | 70 | 70 |  |  | 42803.4167 | 96 | 96
2017-03-09 10:30 | 70 | 70 |  |  | 42803.4375 | 96 | 96
2017-03-09 11:00 | 70 | 70 |  |  | 42803.4583 | 96 | 96
2017-03-09 11:30 | 74 | 74 |  |  | 42803.4792 | 103 | 103
2017-03-09 12:00 | 77 | 77 |  |  | 42803.5 | 105 | 105
2017-03-09 12:30 | 77 | 77 |  |  | 42803.5208 | 106 | 106
2017-03-09 13:00 | 79 | 78 |  |  | 42803.5417 | 106 | 106
2017-03-09 13:30 | 78 | 77 |  |  | 42803.5625 | 107 | 107
2017-03-09 14:00 | 76 | 75 |  |  | 42803.5833 | 104 | 103
2017-03-09 14:30 | 81 | 80 |  |  | 42803.6042 | 111 | 110
2017-03-09 15:00 | 79 | 78 |  |  | 42803.625 | 110 | 108
2017-03-09 15:30 | 80 | 79 |  |  | 42803.6458 | 109 | 107
2017-03-09 16:00 | 83 | 82 |  |  | 42803.6667 | 113 | 111
2017-03-09 16:30 | 84 | 82 |  |  | 42803.6875 | 113 | 112
2017-03-09 17:00 | 84 | 83 |  |  | 42803.7083 | 113 | 111
2017-03-09 17:30 | 84 | 82 |  |  | 42803.7292 | 112 | 109
2017-03-09 18:00 | 82 | 80 |  |  | 42803.75 | 111 | 108
2017-03-09 18:30 | 84 | 82 |  |  | 42803.7708 | 112 | 109
2017-03-09 19:00 | 89 | 88 |  |  | 42803.7917 | 117 | 114
2017-03-09 19:30 | 90 | 88 |  |  | 42803.8125 | 117 | 114
2017-03-09 20:00 | 88 | 86 |  |  | 42803.8333 | 116 | 112
2017-03-09 20:30 | 85 | 83 |  |  | 42803.8542 | 110 | 108
2017-03-09 21:00 | 79 | 78 |  |  | 42803.875 | 103 | 101
2017-03-09 21:30 | 66 | 66 |  |  | 42803.8958 | 86 | 86
2017-03-09 22:00 | 61 | 60 |  |  | 42803.9167 | 80 | 79
2017-03-09 22:30 | 57 | 56 |  |  | 42803.9375 | 76 | 75
2017-03-09 23:00 | 60 | 59 |  |  | 42803.9583 | 78 | 77
2017-03-09 23:30 | 57 | 55 |  |  | 42803.9792 | 74 | 73
2017-03-10 | 52 | 50 |  |  | 42804 | 68 | 67
2017-03-10 00:30 | 50 | 48 |  |  | 42804.0208 | 68 | 66
2017-03-10 01:00 | 47 | 45 |  |  | 42804.0417 | 64 | 62
2017-03-10 01:30 | 45 | 43 |  |  | 42804.0625 | 60 | 58
2017-03-10 02:00 | 46 | 43 |  |  | 42804.0833 | 59 | 57
2017-03-10 02:30 | 45 | 42 |  |  | 42804.1042 | 58 | 56
2017-03-10 03:00 | 43 | 39 |  |  | 42804.125 | 56 | 54
2017-03-10 03:30 | 43 | 39 |  |  | 42804.1458 | 56 | 53
2017-03-10 04:00 | 43 | 39 |  |  | 42804.1667 | 55 | 53
2017-03-10 04:30 | 44 | 41 |  |  | 42804.1875 | 57 | 55
2017-03-10 05:00 | 45 | 43 |  |  | 42804.2083 | 59 | 57
2017-03-10 05:30 | 48 | 46 |  |  | 42804.2292 | 64 | 63
2017-03-10 06:00 | 52 | 50 |  |  | 42804.25 | 69 | 68
2017-03-10 06:30 | 58 | 57 |  |  | 42804.2708 | 78 | 78
2017-03-10 07:00 | 61 | 61 |  |  | 42804.2917 | 85 | 85
2017-03-10 07:30 | 62 | 62 |  |  | 42804.3125 | 89 | 89
2017-03-10 08:00 | 64 | 64 |  |  | 42804.3333 | 91 | 90
2017-03-10 08:30 | 66 | 65 |  |  | 42804.3542 | 92 | 92
2017-03-10 09:00 | 65 | 64 |  |  | 42804.375 | 91 | 91
2017-03-10 09:30 | 65 | 64 |  |  | 42804.3958 | 92 | 92
2017-03-10 10:00 | 65 | 64 |  |  | 42804.4167 | 92 | 91
2017-03-10 10:30 | 67 | 66 |  |  | 42804.4375 | 94 | 93
2017-03-10 11:00 | 66 | 66 |  |  | 42804.4583 | 94 | 93
2017-03-10 11:30 | 66 | 66 |  |  | 42804.4792 | 96 | 94
2017-03-10 12:00 | 65 | 64 |  |  | 42804.5 | 93 | 92
2017-03-10 12:30 | 66 | 65 |  |  | 42804.5208 | 95 | 94
2017-03-10 13:00 | 68 | 67 |  |  | 42804.5417 | 97 | 95
2017-03-10 13:30 | 69 | 68 |  |  | 42804.5625 | 96 | 96
2017-03-10 14:00 | 72 | 71 |  |  | 42804.5833 | 98 | 98
2017-03-10 14:30 | 74 | 73 |  |  | 42804.6042 | 101 | 101
2017-03-10 15:00 | 76 | 75 |  |  | 42804.625 | 101 | 101
2017-03-10 15:30 | 78 | 76 |  |  | 42804.6458 | 103 | 103
2017-03-10 16:00 | 82 | 80 |  |  | 42804.6667 | 106 | 106
2017-03-10 16:30 | 84 | 82 |  |  | 42804.6875 | 107 | 107
2017-03-10 17:00 | 85 | 82 |  |  | 42804.7083 | 107 | 107
2017-03-10 17:30 | 84 | 81 |  |  | 42804.7292 | 104 | 104
2017-03-10 18:00 | 79 | 75 |  |  | 42804.75 | 97 | 97
2017-03-10 18:30 | 76 | 72 |  |  | 42804.7708 | 94 | 93
2017-03-10 19:00 | 79 | 76 |  |  | 42804.7917 | 97 | 97
2017-03-10 19:30 | 76 | 73 |  |  | 42804.8125 | 94 | 94
2017-03-10 20:00 | 74 | 71 |  |  | 42804.8333 | 91 | 91
2017-03-10 20:30 | 72 | 69 |  |  | 42804.8542 | 88 | 88
2017-03-10 21:00 | 67 | 65 |  |  | 42804.875 | 85 | 85
2017-03-10 21:30 | 63 | 60 |  |  | 42804.8958 | 79 | 79
2017-03-10 22:00 | 62 | 59 |  |  | 42804.9167 | 80 | 80
2017-03-10 22:30 | 63 | 59 |  |  | 42804.9375 | 79 | 79
2017-03-10 23:00 | 66 | 62 |  |  | 42804.9583 | 82 | 82
2017-03-10 23:30 | 63 | 58 |  |  | 42804.9792 | 78 | 78
2017-03-11 | 58 | 52 |  |  | 42805 | 71 | 71
2017-03-11 00:30 | 58 | 50 |  |  | 42805.0208 | 69 | 69
2017-03-11 01:00 | 57 | 49 |  |  | 42805.0417 | 67 | 67
2017-03-11 01:30 | 56 | 47 |  |  | 42805.0625 | 64 | 63
2017-03-11 02:00 | 60 | 44 |  |  | 42805.0833 | 60 | 59
2017-03-11 02:30 | 62 | 41 |  |  | 42805.1042 | 58 | 56
2017-03-11 03:00 | 61 | 39 |  |  | 42805.125 | 57 | 54
2017-03-11 03:30 | 61 | 39 |  |  | 42805.1458 | 56 | 54
2017-03-11 04:00 | 60 | 38 |  |  | 42805.1667 | 55 | 53
2017-03-11 04:30 | 60 | 38 |  |  | 42805.1875 | 56 | 53
2017-03-11 05:00 | 60 | 39 |  |  | 42805.2083 | 56 | 54
2017-03-11 05:30 | 62 | 41 |  |  | 42805.2292 | 59 | 57
2017-03-11 06:00 | 63 | 43 |  |  | 42805.25 | 60 | 58
2017-03-11 06:30 | 63 | 43 |  |  | 42805.2708 | 63 | 61
2017-03-11 07:00 | 63 | 45 |  |  | 42805.2917 | 65 | 63
2017-03-11 07:30 | 64 | 47 |  |  | 42805.3125 | 72 | 71
2017-03-11 08:00 | 67 | 50 |  |  | 42805.3333 | 78 | 77
2017-03-11 08:30 | 69 | 53 |  |  | 42805.3542 | 80 | 79
2017-03-11 09:00 | 69 | 54 |  |  | 42805.375 | 81 | 81
2017-03-11 09:30 | 70 | 55 |  |  | 42805.3958 | 82 | 81
2017-03-11 10:00 | 67 | 52 |  |  | 42805.4167 | 76 | 76
2017-03-11 10:30 | 65 | 52 |  |  | 42805.4375 | 72 | 72
2017-03-11 11:00 | 66 | 53 |  |  | 42805.4583 | 75 | 74
2017-03-11 11:30 | 65 | 52 |  |  | 42805.4792 | 74 | 73
2017-03-11 12:00 | 65 | 53 |  |  | 42805.5 | 72 | 72
2017-03-11 12:30 | 65 | 53 |  |  | 42805.5208 | 71 | 71
2017-03-11 13:00 | 66 | 54 |  |  | 42805.5417 | 71 | 71
2017-03-11 13:30 | 67 | 55 |  |  | 42805.5625 | 72 | 72
2017-03-11 14:00 | 67 | 57 |  |  | 42805.5833 | 72 | 72
2017-03-11 14:30 | 68 | 59 |  |  | 42805.6042 | 73 | 73
2017-03-11 15:00 | 70 | 61 |  |  | 42805.625 | 75 | 75
2017-03-11 15:30 | 72 | 61 |  |  | 42805.6458 | 75 | 75
2017-03-11 16:00 | 73 | 63 |  |  | 42805.6667 | 78 | 77
2017-03-11 16:30 | 75 | 63 |  |  | 42805.6875 | 80 | 79
2017-03-11 17:00 | 77 | 65 |  |  | 42805.7083 | 82 | 82
2017-03-11 17:30 | 68 | 66 |  |  | 42805.7292 | 82 | 82
2017-03-11 18:00 | 66 | 64 |  |  | 42805.75 | 82 | 81
2017-03-11 18:30 | 67 | 65 |  |  | 42805.7708 | 84 | 84
2017-03-11 19:00 | 70 | 68 |  |  | 42805.7917 | 89 | 89
2017-03-11 19:30 | 71 | 70 |  |  | 42805.8125 | 90 | 90
2017-03-11 20:00 | 70 | 69 |  |  | 42805.8333 | 88 | 87
2017-03-11 20:30 | 68 | 67 |  |  | 42805.8542 | 87 | 86
2017-03-11 21:00 | 64 | 64 |  |  | 42805.875 | 83 | 83
2017-03-11 21:30 | 63 | 62 |  |  | 42805.8958 | 79 | 79
2017-03-11 22:00 | 60 | 59 |  |  | 42805.9167 | 78 | 77
2017-03-11 22:30 | 57 | 56 |  |  | 42805.9375 | 73 | 72
2017-03-11 23:00 | 57 | 56 |  |  | 42805.9583 | 73 | 72
2017-03-11 23:30 | 57 | 55 |  |  | 42805.9792 | 71 | 71
2017-03-12 | 53 | 51 |  |  | 42806 | 67 | 66
2017-03-12 00:30 | 52 | 50 |  |  | 42806.0208 | 67 | 66
2017-03-12 01:00 | 52 | 50 |  |  | 42806.0417 | 66 | 66
2017-03-12 01:30 | 48 | 45 |  |  | 42806.0625 | 61 | 60
2017-03-12 02:00 | 47 | 44 |  |  | 42806.0833 | 59 | 58
2017-03-12 02:30 | 46 | 42 |  |  | 42806.1042 | 58 | 57
2017-03-12 03:00 | 44 | 40 |  |  | 42806.125 | 56 | 55
2017-03-12 03:30 | 44 | 40 |  |  | 42806.1458 | 55 | 53
2017-03-12 04:00 | 43 | 39 |  |  | 42806.1667 | 55 | 53
2017-03-12 04:30 | 43 | 39 |  |  | 42806.1875 | 55 | 53
2017-03-12 05:00 | 43 | 38 |  |  | 42806.2083 | 54 | 52
2017-03-12 05:30 | 43 | 39 |  |  | 42806.2292 | 54 | 52
2017-03-12 06:00 | 42 | 38 |  |  | 42806.25 | 55 | 54
2017-03-12 06:30 | 43 | 39 |  |  | 42806.2708 | 57 | 55
2017-03-12 07:00 | 44 | 40 |  |  | 42806.2917 | 58 | 57
2017-03-12 07:30 | 44 | 41 |  |  | 42806.3125 | 59 | 58
2017-03-12 08:00 | 44 | 42 |  |  | 42806.3333 | 59 | 58
2017-03-12 08:30 | 45 | 43 |  |  | 42806.3542 | 60 | 60
2017-03-12 09:00 | 49 | 47 |  |  | 42806.375 | 66 | 66
2017-03-12 09:30 | 55 | 54 |  |  | 42806.3958 | 74 | 73
2017-03-12 10:00 | 57 | 56 |  |  | 42806.4167 | 76 | 75
2017-03-12 10:30 | 57 | 57 |  |  | 42806.4375 | 74 | 74
2017-03-12 11:00 | 50 | 49 |  |  | 42806.4583 | 70 | 70
2017-03-12 11:30 | 37 | 36 |  |  | 42806.4792 | 66 | 66
2017-03-12 12:00 | 38 | 37 |  |  | 42806.5 | 66 | 66
2017-03-12 12:30 | 43 | 41 |  |  | 42806.5208 | 70 | 69
2017-03-12 13:00 | 65 | 63 |  |  | 42806.5417 | 81 | 80
2017-03-12 13:30 | 65 | 64 |  |  | 42806.5625 | 82 | 81
2017-03-12 14:00 | 67 | 66 |  |  | 42806.5833 | 82 | 81
2017-03-12 14:30 | 70 | 69 |  |  | 42806.6042 | 87 | 86
2017-03-12 15:00 | 74 | 73 |  |  | 42806.625 | 90 | 89
2017-03-12 15:30 | 76 | 75 |  |  | 42806.6458 | 93 | 92
2017-03-12 16:00 | 76 | 75 |  |  | 42806.6667 | 92 | 91
2017-03-12 16:30 | 79 | 78 |  |  | 42806.6875 | 94 | 93
2017-03-12 17:00 | 85 | 83 |  |  | 42806.7083 | 98 | 97
2017-03-12 17:30 | 85 | 83 |  |  | 42806.7292 | 98 | 96
2017-03-12 18:00 | 84 | 82 |  |  | 42806.75 | 98 | 97
2017-03-12 18:30 | 85 | 84 |  |  | 42806.7708 | 102 | 100
2017-03-12 19:00 | 88 | 87 |  |  | 42806.7917 | 107 | 106
2017-03-12 19:30 | 88 | 86 |  |  | 42806.8125 | 106 | 105
2017-03-12 20:00 | 87 | 85 |  |  | 42806.8333 | 105 | 104
2017-03-12 20:30 | 83 | 82 |  |  | 42806.8542 | 103 | 102
2017-03-12 21:00 | 80 | 78 |  |  | 42806.875 | 99 | 98
2017-03-12 21:30 | 75 | 74 |  |  | 42806.8958 | 94 | 94
2017-03-12 22:00 | 72 | 72 |  |  | 42806.9167 | 91 | 91
2017-03-12 22:30 | 67 | 67 |  |  | 42806.9375 | 85 | 85
2017-03-12 23:00 | 66 | 65 |  |  | 42806.9583 | 83 | 83
2017-03-12 23:30 | 63 | 62 |  |  | 42806.9792 | 79 | 79
2017-03-13 | 59 | 59 |  |  | 42807 | 75 | 75
2017-03-13 00:30 | 56 | 55 |  |  | 42807.0208 | 73 | 72
2017-03-13 01:00 | 56 | 55 |  |  | 42807.0417 | 73 | 72
2017-03-13 01:30 | 55 | 53 |  |  | 42807.0625 | 69 | 69
2017-03-13 02:00 | 53 | 51 |  |  | 42807.0833 | 67 | 66
2017-03-13 02:30 | 51 | 49 |  |  | 42807.1042 | 65 | 64
2017-03-13 03:00 | 50 | 48 |  |  | 42807.125 | 63 | 62
2017-03-13 03:30 | 49 | 48 |  |  | 42807.1458 | 62 | 62
2017-03-13 04:00 | 49 | 47 |  |  | 42807.1667 | 62 | 62
2017-03-13 04:30 | 48 | 46 |  |  | 42807.1875 | 62 | 61
2017-03-13 05:00 | 49 | 48 |  |  | 42807.2083 | 63 | 62
2017-03-13 05:30 | 52 | 51 |  |  | 42807.2292 | 67 | 67
2017-03-13 06:00 | 57 | 56 |  |  | 42807.25 | 73 | 73
2017-03-13 06:30 | 62 | 62 |  |  | 42807.2708 | 83 | 83
2017-03-13 07:00 | 71 | 69 |  |  | 42807.2917 | 92 | 92
2017-03-13 07:30 | 79 | 78 |  |  | 42807.3125 | 103 | 103
2017-03-13 08:00 | 86 | 85 |  |  | 42807.3333 | 113 | 113
2017-03-13 08:30 | 93 | 88 |  |  | 42807.3542 | 118 | 117
2017-03-13 09:00 | 92 | 87 |  |  | 42807.375 | 117 | 115
2017-03-13 09:30 | 94 | 88 |  |  | 42807.3958 | 117 | 116
2017-03-13 10:00 | 96 | 90 |  |  | 42807.4167 | 118 | 116
2017-03-13 10:30 | 92 | 87 |  |  | 42807.4375 | 114 | 113
2017-03-13 11:00 | 87 | 82 |  |  | 42807.4583 | 110 | 109
2017-03-13 11:30 | 86 | 81 |  |  | 42807.4792 | 109 | 108
2017-03-13 12:00 | 87 | 82 |  |  | 42807.5 | 111 | 110
2017-03-13 12:30 | 86 | 81 |  |  | 42807.5208 | 106 | 105
2017-03-13 13:00 | 85 | 80 |  |  | 42807.5417 | 106 | 105
2017-03-13 13:30 | 88 | 84 |  |  | 42807.5625 | 111 | 110
2017-03-13 14:00 | 90 | 86 |  |  | 42807.5833 | 114 | 113
2017-03-13 14:30 | 91 | 88 |  |  | 42807.6042 | 115 | 115
2017-03-13 15:00 | 92 | 89 |  |  | 42807.625 | 117 | 116
2017-03-13 15:30 | 92 | 87 |  |  | 42807.6458 | 115 | 115
2017-03-13 16:00 | 94 | 89 |  |  | 42807.6667 | 116 | 116
2017-03-13 16:30 | 93 | 89 |  |  | 42807.6875 | 116 | 115
2017-03-13 17:00 | 95 | 90 |  |  | 42807.7083 | 117 | 116
2017-03-13 17:30 | 91 | 86 |  |  | 42807.7292 | 112 | 112
2017-03-13 18:00 | 89 | 86 |  |  | 42807.75 | 109 | 109
2017-03-13 18:30 | 88 | 85 |  |  | 42807.7708 | 107 | 107
2017-03-13 19:00 | 92 | 90 |  |  | 42807.7917 | 111 | 111
2017-03-13 19:30 | 90 | 88 |  |  | 42807.8125 | 108 | 108
2017-03-13 20:00 | 91 | 89 |  |  | 42807.8333 | 108 | 108
2017-03-13 20:30 | 89 | 87 |  |  | 42807.8542 | 105 | 105
2017-03-13 21:00 | 84 | 82 |  |  | 42807.875 | 99 | 99
2017-03-13 21:30 | 80 | 78 |  |  | 42807.8958 | 93 | 93
2017-03-13 22:00 | 76 | 73 |  |  | 42807.9167 | 89 | 89
2017-03-13 22:30 | 70 | 67 |  |  | 42807.9375 | 83 | 83
2017-03-13 23:00 | 68 | 66 |  |  | 42807.9583 | 81 | 81
2017-03-13 23:30 | 65 | 62 |  |  | 42807.9792 | 78 | 78
2017-03-14 | 59 | 56 |  |  | 42808 | 73 | 71
2017-03-14 00:30 | 56 | 54 |  |  | 42808.0208 | 71 | 69
2017-03-14 01:00 | 55 | 52 |  |  | 42808.0417 | 69 | 67
2017-03-14 01:30 | 53 | 50 |  |  | 42808.0625 | 65 | 64
2017-03-14 02:00 | 52 | 49 |  |  | 42808.0833 | 64 | 62
2017-03-14 02:30 | 48 | 45 |  |  | 42808.1042 | 61 | 59
2017-03-14 03:00 | 47 | 44 |  |  | 42808.125 | 58 | 56
2017-03-14 03:30 | 45 | 42 |  |  | 42808.1458 | 57 | 55
2017-03-14 04:00 | 45 | 41 |  |  | 42808.1667 | 56 | 54
2017-03-14 04:30 | 46 | 42 |  |  | 42808.1875 | 56 | 54
2017-03-14 05:00 | 47 | 44 |  |  | 42808.2083 | 59 | 57
2017-03-14 05:30 | 51 | 47 |  |  | 42808.2292 | 63 | 62
2017-03-14 06:00 | 56 | 52 |  |  | 42808.25 | 68 | 67
2017-03-14 06:30 | 63 | 60 |  |  | 42808.2708 | 81 | 80
2017-03-14 07:00 | 70 | 67 |  |  | 42808.2917 | 92 | 90
2017-03-14 07:30 | 74 | 72 |  |  | 42808.3125 | 100 | 99
2017-03-14 08:00 | 78 | 76 |  |  | 42808.3333 | 104 | 104
2017-03-14 08:30 | 78 | 76 |  |  | 42808.3542 | 106 | 106
2017-03-14 09:00 | 79 | 76 |  |  | 42808.375 | 113 | 113
2017-03-14 09:30 | 84 | 81 |  |  | 42808.3958 | 117 | 117
2017-03-14 10:00 | 81 | 78 |  |  | 42808.4167 | 115 | 114
2017-03-14 10:30 | 82 | 78 |  |  | 42808.4375 | 114 | 114
2017-03-14 11:00 | 84 | 83 |  |  | 42808.4583 | 116 | 116
2017-03-14 11:30 | 93 | 92 |  |  | 42808.4792 | 126 | 126
2017-03-14 12:00 | 89 | 87 |  |  | 42808.5 | 127 | 127
2017-03-14 12:30 | 84 | 81 |  |  | 42808.5208 | 117 | 117
2017-03-14 13:00 | 83 | 81 |  |  | 42808.5417 | 113 | 113
2017-03-14 13:30 | 86 | 85 |  |  | 42808.5625 | 119 | 119
2017-03-14 14:00 | 89 | 87 |  |  | 42808.5833 | 123 | 123
2017-03-14 14:30 | 86 | 84 |  |  | 42808.6042 | 121 | 121
2017-03-14 15:00 | 88 | 85 |  |  | 42808.625 | 123 | 123
2017-03-14 15:30 | 86 | 83 |  |  | 42808.6458 | 119 | 119
2017-03-14 16:00 | 86 | 84 |  |  | 42808.6667 | 117 | 117
2017-03-14 16:30 | 91 | 89 |  |  | 42808.6875 | 122 | 122
2017-03-14 17:00 | 92 | 90 |  |  | 42808.7083 | 121 | 121
2017-03-14 17:30 | 90 | 88 |  |  | 42808.7292 | 118 | 118
2017-03-14 18:00 | 88 | 85 |  |  | 42808.75 | 115 | 114
2017-03-14 18:30 | 87 | 85 |  |  | 42808.7708 | 112 | 112
2017-03-14 19:00 | 89 | 86 |  |  | 42808.7917 | 113 | 113
2017-03-14 19:30 | 85 | 82 |  |  | 42808.8125 | 110 | 110
2017-03-14 20:00 | 81 | 78 |  |  | 42808.8333 | 105 | 105
2017-03-14 20:30 | 78 | 77 |  |  | 42808.8542 | 104 | 103
2017-03-14 21:00 | 74 | 73 |  |  | 42808.875 | 97 | 97
2017-03-14 21:30 | 72 | 71 |  |  | 42808.8958 | 94 | 94
2017-03-14 22:00 | 72 | 70 |  |  | 42808.9167 | 93 | 93
2017-03-14 22:30 | 67 | 65 |  |  | 42808.9375 | 85 | 85
2017-03-14 23:00 | 66 | 63 |  |  | 42808.9583 | 83 | 83
2017-03-14 23:30 | 62 | 59 |  |  | 42808.9792 | 79 | 79
2017-03-15 | 60 | 54 |  |  | 42809 | 73 | 73
2017-03-15 00:30 | 60 | 54 |  |  | 42809.0208 | 74 | 74
2017-03-15 01:00 | 59 | 52 |  |  | 42809.0417 | 71 | 71
2017-03-15 01:30 | 58 | 50 |  |  | 42809.0625 | 67 | 67
2017-03-15 02:00 | 54 | 46 |  |  | 42809.0833 | 62 | 62
2017-03-15 02:30 | 53 | 44 |  |  | 42809.1042 | 61 | 61
2017-03-15 03:00 | 52 | 44 |  |  | 42809.125 | 60 | 60
2017-03-15 03:30 | 52 | 44 |  |  | 42809.1458 | 60 | 60
2017-03-15 04:00 | 52 | 44 |  |  | 42809.1667 | 60 | 60
2017-03-15 04:30 | 52 | 44 |  |  | 42809.1875 | 60 | 60
2017-03-15 05:00 | 50 | 43 |  |  | 42809.2083 | 59 | 59
2017-03-15 05:30 | 53 | 47 |  |  | 42809.2292 | 65 | 65
2017-03-15 06:00 | 58 | 53 |  |  | 42809.25 | 73 | 73
2017-03-15 06:30 | 64 | 62 |  |  | 42809.2708 | 86 | 86
2017-03-15 07:00 | 69 | 67 |  |  | 42809.2917 | 94 | 93
2017-03-15 07:30 | 72 | 71 |  |  | 42809.3125 | 103 | 102
2017-03-15 08:00 | 75 | 73 |  |  | 42809.3333 | 105 | 104
2017-03-15 08:30 | 77 | 75 |  |  | 42809.3542 | 109 | 109
2017-03-15 09:00 | 74 | 73 |  |  | 42809.375 | 107 | 107
2017-03-15 09:30 | 75 | 74 |  |  | 42809.3958 | 108 | 108
2017-03-15 10:00 | 77 | 76 |  |  | 42809.4167 | 110 | 110
2017-03-15 10:30 | 79 | 78 |  |  | 42809.4375 | 112 | 112
2017-03-15 11:00 | 77 | 77 |  |  | 42809.4583 | 114 | 113
2017-03-15 11:30 | 79 | 78 |  |  | 42809.4792 | 113 | 112
2017-03-15 12:00 | 78 | 77 |  |  | 42809.5 | 113 | 112
2017-03-15 12:30 | 75 | 74 |  |  | 42809.5208 | 110 | 110
2017-03-15 13:00 | 79 | 77 |  |  | 42809.5417 | 112 | 111
2017-03-15 13:30 | 79 | 78 |  |  | 42809.5625 | 111 | 110
2017-03-15 14:00 | 80 | 79 |  |  | 42809.5833 | 116 | 115
2017-03-15 14:30 | 82 | 81 |  |  | 42809.6042 | 116 | 115
2017-03-15 15:00 | 80 | 79 |  |  | 42809.625 | 113 | 113
2017-03-15 15:30 | 83 | 81 |  |  | 42809.6458 | 116 | 116
2017-03-15 16:00 | 82 | 80 |  |  | 42809.6667 | 115 | 115
2017-03-15 16:30 | 83 | 81 |  |  | 42809.6875 | 115 | 115
2017-03-15 17:00 | 85 | 83 |  |  | 42809.7083 | 117 | 117
2017-03-15 17:30 | 84 | 82 |  |  | 42809.7292 | 114 | 114
2017-03-15 18:00 | 81 | 80 |  |  | 42809.75 | 109 | 109
2017-03-15 18:30 | 78 | 78 |  |  | 42809.7708 | 108 | 106
2017-03-15 19:00 | 79 | 78 |  |  | 42809.7917 | 108 | 107
2017-03-15 19:30 | 77 | 76 |  |  | 42809.8125 | 107 | 106
2017-03-15 20:00 | 76 | 75 |  |  | 42809.8333 | 106 | 105
2017-03-15 20:30 | 72 | 71 |  |  | 42809.8542 | 99 | 98
2017-03-15 21:00 | 70 | 69 |  |  | 42809.875 | 95 | 95
2017-03-15 21:30 | 66 | 64 |  |  | 42809.8958 | 89 | 88
2017-03-15 22:00 | 62 | 61 |  |  | 42809.9167 | 84 | 84
2017-03-15 22:30 | 57 | 56 |  |  | 42809.9375 | 79 | 77
2017-03-15 23:00 | 57 | 54 |  |  | 42809.9583 | 77 | 75
2017-03-15 23:30 | 55 | 52 |  |  | 42809.9792 | 73 | 71
2017-03-16 | 49 | 46 |  |  | 42810 | 68 | 65
2017-03-16 00:30 | 51 | 47 |  |  | 42810.0208 | 70 | 68
2017-03-16 01:00 | 51 | 47 |  |  | 42810.0417 | 68 | 66
2017-03-16 01:30 | 49 | 45 |  |  | 42810.0625 | 64 | 63
2017-03-16 02:00 | 47 | 43 |  |  | 42810.0833 | 62 | 61
2017-03-16 02:30 | 45 | 40 |  |  | 42810.1042 | 59 | 57
2017-03-16 03:00 | 44 | 39 |  |  | 42810.125 | 56 | 55
2017-03-16 03:30 | 43 | 38 |  |  | 42810.1458 | 55 | 53
2017-03-16 04:00 | 41 | 37 |  |  | 42810.1667 | 54 | 52
2017-03-16 04:30 | 42 | 38 |  |  | 42810.1875 | 56 | 54
2017-03-16 05:00 | 44 | 40 |  |  | 42810.2083 | 60 | 58
2017-03-16 05:30 | 47 | 44 |  |  | 42810.2292 | 65 | 63
2017-03-16 06:00 | 50 | 49 |  |  | 42810.25 | 71 | 69
2017-03-16 06:30 | 57 | 56 |  |  | 42810.2708 | 83 | 80
2017-03-16 07:00 | 63 | 63 |  |  | 42810.2917 | 91 | 90
2017-03-16 07:30 | 69 | 67 |  |  | 42810.3125 | 99 | 99
2017-03-16 08:00 | 71 | 68 |  |  | 42810.3333 | 102 | 102
2017-03-16 08:30 | 70 | 68 |  |  | 42810.3542 | 103 | 103
2017-03-16 09:00 | 72 | 70 |  |  | 42810.375 | 106 | 105
2017-03-16 09:30 | 71 | 69 |  |  | 42810.3958 | 105 | 104
2017-03-16 10:00 | 74 | 71 |  |  | 42810.4167 | 110 | 109
2017-03-16 10:30 | 78 | 76 |  |  | 42810.4375 | 112 | 111
2017-03-16 11:00 | 77 | 75 |  |  | 42810.4583 | 115 | 114
2017-03-16 11:30 | 76 | 73 |  |  | 42810.4792 | 113 | 113
2017-03-16 12:00 | 78 | 75 |  |  | 42810.5 | 115 | 114
2017-03-16 12:30 | 82 | 78 |  |  | 42810.5208 | 119 | 119
2017-03-16 13:00 | 81 | 79 |  |  | 42810.5417 | 119 | 119
2017-03-16 13:30 | 84 | 82 |  |  | 42810.5625 | 124 | 124
2017-03-16 14:00 | 91 | 88 |  |  | 42810.5833 | 128 | 128
2017-03-16 14:30 | 93 | 91 |  |  | 42810.6042 | 132 | 132
2017-03-16 15:00 | 93 | 91 |  |  | 42810.625 | 131 | 131
2017-03-16 15:30 | 88 | 86 |  |  | 42810.6458 | 125 | 125
2017-03-16 16:00 | 86 | 84 |  |  | 42810.6667 | 125 | 125
2017-03-16 16:30 | 87 | 85 |  |  | 42810.6875 | 125 | 125
2017-03-16 17:00 | 88 | 85 |  |  | 42810.7083 | 124 | 124
2017-03-16 17:30 | 87 | 84 |  |  | 42810.7292 | 121 | 121
2017-03-16 18:00 | 85 | 83 |  |  | 42810.75 | 119 | 119
2017-03-16 18:30 | 84 | 82 |  |  | 42810.7708 | 117 | 117
2017-03-16 19:00 | 89 | 87 |  |  | 42810.7917 | 121 | 121
2017-03-16 19:30 | 88 | 86 |  |  | 42810.8125 | 119 | 119
2017-03-16 20:00 | 87 | 85 |  |  | 42810.8333 | 118 | 118
2017-03-16 20:30 | 84 | 83 |  |  | 42810.8542 | 116 | 116
2017-03-16 21:00 | 81 | 80 |  |  | 42810.875 | 111 | 109
2017-03-16 21:30 | 74 | 74 |  |  | 42810.8958 | 104 | 101
2017-03-16 22:00 | 70 | 70 |  |  | 42810.9167 | 100 | 97
2017-03-16 22:30 | 66 | 66 |  |  | 42810.9375 | 94 | 91
2017-03-16 23:00 | 66 | 66 |  |  | 42810.9583 | 91 | 88
2017-03-16 23:30 | 60 | 60 |  |  | 42810.9792 | 87 | 84
2017-03-17 | 52 | 52 |  |  | 42811 | 78 | 76
2017-03-17 00:30 | 52 | 51 |  |  | 42811.0208 | 77 | 74
2017-03-17 01:00 | 51 | 49 |  |  | 42811.0417 | 72 | 70
2017-03-17 01:30 | 48 | 45 |  |  | 42811.0625 | 68 | 65
2017-03-17 02:00 | 48 | 46 |  |  | 42811.0833 | 66 | 63
2017-03-17 02:30 | 45 | 42 |  |  | 42811.1042 | 63 | 60
2017-03-17 03:00 | 43 | 40 |  |  | 42811.125 | 61 | 57
2017-03-17 03:30 | 42 | 39 |  |  | 42811.1458 | 60 | 56
2017-03-17 04:00 | 42 | 38 |  |  | 42811.1667 | 58 | 55
2017-03-17 04:30 | 41 | 38 |  |  | 42811.1875 | 59 | 55
2017-03-17 05:00 | 42 | 40 |  |  | 42811.2083 | 62 | 58
2017-03-17 05:30 | 46 | 44 |  |  | 42811.2292 | 68 | 64
2017-03-17 06:00 | 48 | 47 |  |  | 42811.25 | 73 | 68
2017-03-17 06:30 | 51 | 51 |  |  | 42811.2708 | 79 | 76
2017-03-17 07:00 | 58 | 58 |  |  | 42811.2917 | 89 | 86
2017-03-17 07:30 | 64 | 63 |  |  | 42811.3125 | 98 | 96
2017-03-17 08:00 | 67 | 66 |  |  | 42811.3333 | 104 | 101
2017-03-17 08:30 | 71 | 69 |  |  | 42811.3542 | 109 | 105
2017-03-17 09:00 | 72 | 71 |  |  | 42811.375 | 111 | 109
2017-03-17 09:30 | 76 | 75 |  |  | 42811.3958 | 114 | 113
2017-03-17 10:00 | 76 | 76 |  |  | 42811.4167 | 115 | 114
2017-03-17 10:30 | 76 | 76 |  |  | 42811.4375 | 115 | 115
2017-03-17 11:00 | 77 | 77 |  |  | 42811.4583 | 116 | 116
2017-03-17 11:30 | 79 | 79 |  |  | 42811.4792 | 117 | 117
2017-03-17 12:00 | 86 | 86 |  |  | 42811.5 | 121 | 121
2017-03-17 12:30 | 89 | 89 |  |  | 42811.5208 | 124 | 123
2017-03-17 13:00 | 98 | 98 |  |  | 42811.5417 | 131 | 130
2017-03-17 13:30 | 106 | 106 |  |  | 42811.5625 | 140 | 138
2017-03-17 14:00 | 91 | 90 |  |  | 42811.5833 | 128 | 126
2017-03-17 14:30 | 84 | 84 |  |  | 42811.6042 | 118 | 117
2017-03-17 15:00 | 83 | 83 |  |  | 42811.625 | 114 | 114
2017-03-17 15:30 | 78 | 78 |  |  | 42811.6458 | 119 | 119
2017-03-17 16:00 | 75 | 75 |  |  | 42811.6667 | 108 | 108
2017-03-17 16:30 | 77 | 77 |  |  | 42811.6875 | 111 | 110
2017-03-17 17:00 | 78 | 78 |  |  | 42811.7083 | 111 | 110
2017-03-17 17:30 | 77 | 77 |  |  | 42811.7292 | 109 | 108
2017-03-17 18:00 | 75 | 74 |  |  | 42811.75 | 105 | 104
2017-03-17 18:30 | 78 | 78 |  |  | 42811.7708 | 102 | 102
2017-03-17 19:00 | 82 | 81 |  |  | 42811.7917 | 105 | 105
2017-03-17 19:30 | 80 | 80 |  |  | 42811.8125 | 103 | 103
2017-03-17 20:00 | 78 | 78 |  |  | 42811.8333 | 101 | 100
2017-03-17 20:30 | 74 | 74 |  |  | 42811.8542 | 98 | 97
2017-03-17 21:00 | 71 | 70 |  |  | 42811.875 | 93 | 92
2017-03-17 21:30 | 67 | 67 |  |  | 42811.8958 | 89 | 88
2017-03-17 22:00 | 64 | 64 |  |  | 42811.9167 | 85 | 84
2017-03-17 22:30 | 62 | 62 |  |  | 42811.9375 | 81 | 80
2017-03-17 23:00 | 60 | 60 |  |  | 42811.9583 | 79 | 78
2017-03-17 23:30 | 58 | 58 |  |  | 42811.9792 | 77 | 76
2017-03-18 | 55 | 55 |  |  | 42812 | 72 | 72
2017-03-18 00:30 | 54 | 54 |  |  | 42812.0208 | 71 | 70
2017-03-18 01:00 | 52 | 51 |  |  | 42812.0417 | 69 | 68
2017-03-18 01:30 | 48 | 48 |  |  | 42812.0625 | 64 | 63
2017-03-18 02:00 | 46 | 46 |  |  | 42812.0833 | 61 | 60
2017-03-18 02:30 | 44 | 44 |  |  | 42812.1042 | 60 | 59
2017-03-18 03:00 | 42 | 42 |  |  | 42812.125 | 56 | 55
2017-03-18 03:30 | 41 | 41 |  |  | 42812.1458 | 55 | 54
2017-03-18 04:00 | 41 | 40 |  |  | 42812.1667 | 55 | 54
2017-03-18 04:30 | 40 | 39 |  |  | 42812.1875 | 54 | 53
2017-03-18 05:00 | 41 | 41 |  |  | 42812.2083 | 54 | 53
2017-03-18 05:30 | 42 | 42 |  |  | 42812.2292 | 56 | 55
2017-03-18 06:00 | 43 | 43 |  |  | 42812.25 | 58 | 57
2017-03-18 06:30 | 44 | 44 |  |  | 42812.2708 | 61 | 60
2017-03-18 07:00 | 46 | 46 |  |  | 42812.2917 | 66 | 64
2017-03-18 07:30 | 52 | 52 |  |  | 42812.3125 | 74 | 73
2017-03-18 08:00 | 55 | 55 |  |  | 42812.3333 | 77 | 77
2017-03-18 08:30 | 58 | 58 |  |  | 42812.3542 | 81 | 80
2017-03-18 09:00 | 60 | 59 |  |  | 42812.375 | 84 | 84
2017-03-18 09:30 | 58 | 58 |  |  | 42812.3958 | 83 | 83
2017-03-18 10:00 | 58 | 57 |  |  | 42812.4167 | 82 | 82
2017-03-18 10:30 | 59 | 59 |  |  | 42812.4375 | 84 | 84
2017-03-18 11:00 | 62 | 62 |  |  | 42812.4583 | 86 | 86
2017-03-18 11:30 | 65 | 65 |  |  | 42812.4792 | 91 | 91
2017-03-18 12:00 | 67 | 67 |  |  | 42812.5 | 90 | 90
2017-03-18 12:30 | 67 | 67 |  |  | 42812.5208 | 88 | 88
2017-03-18 13:00 | 67 | 67 |  |  | 42812.5417 | 91 | 91
2017-03-18 13:30 | 69 | 69 |  |  | 42812.5625 | 92 | 92
2017-03-18 14:00 | 70 | 70 |  |  | 42812.5833 | 91 | 91
2017-03-18 14:30 | 73 | 73 |  |  | 42812.6042 | 92 | 92
2017-03-18 15:00 | 75 | 75 |  |  | 42812.625 | 96 | 96
2017-03-18 15:30 | 81 | 80 |  |  | 42812.6458 | 101 | 101
2017-03-18 16:00 | 83 | 81 |  |  | 42812.6667 | 103 | 103
2017-03-18 16:30 | 83 | 82 |  |  | 42812.6875 | 103 | 101
2017-03-18 17:00 | 85 | 82 |  |  | 42812.7083 | 104 | 102
2017-03-18 17:30 | 83 | 80 |  |  | 42812.7292 | 102 | 99
2017-03-18 18:00 | 79 | 77 |  |  | 42812.75 | 100 | 98
2017-03-18 18:30 | 78 | 76 |  |  | 42812.7708 | 100 | 99
2017-03-18 19:00 | 81 | 79 |  |  | 42812.7917 | 104 | 103
2017-03-18 19:30 | 78 | 76 |  |  | 42812.8125 | 100 | 99
2017-03-18 20:00 | 76 | 75 |  |  | 42812.8333 | 99 | 99
2017-03-18 20:30 | 76 | 75 |  |  | 42812.8542 | 100 | 100
2017-03-18 21:00 | 77 | 76 |  |  | 42812.875 | 98 | 98
2017-03-18 21:30 | 74 | 74 |  |  | 42812.8958 | 94 | 94
2017-03-18 22:00 | 71 | 71 |  |  | 42812.9167 | 91 | 91
2017-03-18 22:30 | 66 | 66 |  |  | 42812.9375 | 84 | 84
2017-03-18 23:00 | 65 | 64 |  |  | 42812.9583 | 81 | 81
2017-03-18 23:30 | 61 | 60 |  |  | 42812.9792 | 77 | 76
2017-03-19 | 56 | 54 |  |  | 42813 | 70 | 70
2017-03-19 00:30 | 55 | 53 |  |  | 42813.0208 | 69 | 69
2017-03-19 01:00 | 52 | 50 |  |  | 42813.0417 | 66 | 66
2017-03-19 01:30 | 48 | 46 |  |  | 42813.0625 | 60 | 60
2017-03-19 02:00 | 45 | 43 |  |  | 42813.0833 | 57 | 57
2017-03-19 02:30 | 43 | 41 |  |  | 42813.1042 | 54 | 54
2017-03-19 03:00 | 41 | 39 |  |  | 42813.125 | 52 | 52
2017-03-19 03:30 | 41 | 39 |  |  | 42813.1458 | 50 | 50
2017-03-19 04:00 | 38 | 36 |  |  | 42813.1667 | 49 | 49
2017-03-19 04:30 | 39 | 37 |  |  | 42813.1875 | 49 | 49
2017-03-19 05:00 | 39 | 37 |  |  | 42813.2083 | 49 | 49
2017-03-19 05:30 | 40 | 38 |  |  | 42813.2292 | 51 | 51
2017-03-19 06:00 | 40 | 38 |  |  | 42813.25 | 52 | 52
2017-03-19 06:30 | 39 | 38 |  |  | 42813.2708 | 53 | 53
2017-03-19 07:00 | 39 | 38 |  |  | 42813.2917 | 54 | 54
2017-03-19 07:30 | 42 | 40 |  |  | 42813.3125 | 58 | 58
2017-03-19 08:00 | 44 | 43 |  |  | 42813.3333 | 63 | 63
2017-03-19 08:30 | 45 | 45 |  |  | 42813.3542 | 67 | 67
2017-03-19 09:00 | 52 | 51 |  |  | 42813.375 | 72 | 72
2017-03-19 09:30 | 57 | 57 |  |  | 42813.3958 | 76 | 76
2017-03-19 10:00 | 58 | 58 |  |  | 42813.4167 | 79 | 78
2017-03-19 10:30 | 57 | 57 |  |  | 42813.4375 | 78 | 78
2017-03-19 11:00 | 55 | 55 |  |  | 42813.4583 | 76 | 75
2017-03-19 11:30 | 52 | 52 |  |  | 42813.4792 | 74 | 74
2017-03-19 12:00 | 52 | 52 |  |  | 42813.5 | 72 | 72
2017-03-19 12:30 | 55 | 55 |  |  | 42813.5208 | 74 | 73
2017-03-19 13:00 | 61 | 61 |  |  | 42813.5417 | 79 | 79
2017-03-19 13:30 | 61 | 61 |  |  | 42813.5625 | 80 | 79
2017-03-19 14:00 | 59 | 59 |  |  | 42813.5833 | 79 | 79
2017-03-19 14:30 | 64 | 64 |  |  | 42813.6042 | 84 | 83
2017-03-19 15:00 | 64 | 64 |  |  | 42813.625 | 86 | 86
2017-03-19 15:30 | 65 | 65 |  |  | 42813.6458 | 86 | 85
2017-03-19 16:00 | 67 | 67 |  |  | 42813.6667 | 86 | 86
2017-03-19 16:30 | 68 | 68 |  |  | 42813.6875 | 88 | 88
2017-03-19 17:00 | 69 | 69 |  |  | 42813.7083 | 90 | 90
2017-03-19 17:30 | 70 | 69 |  |  | 42813.7292 | 90 | 90
2017-03-19 18:00 | 72 | 71 |  |  | 42813.75 | 92 | 91
2017-03-19 18:30 | 74 | 74 |  |  | 42813.7708 | 95 | 95
2017-03-19 19:00 | 77 | 77 |  |  | 42813.7917 | 99 | 99
2017-03-19 19:30 | 74 | 74 |  |  | 42813.8125 | 96 | 96
2017-03-19 20:00 | 70 | 70 |  |  | 42813.8333 | 93 | 93
2017-03-19 20:30 | 70 | 70 |  |  | 42813.8542 | 92 | 92
2017-03-19 21:00 | 67 | 66 |  |  | 42813.875 | 86 | 86
2017-03-19 21:30 | 65 | 64 |  |  | 42813.8958 | 83 | 83
2017-03-19 22:00 | 62 | 61 |  |  | 42813.9167 | 80 | 80
2017-03-19 22:30 | 57 | 56 |  |  | 42813.9375 | 75 | 75
2017-03-19 23:00 | 55 | 54 |  |  | 42813.9583 | 72 | 72
2017-03-19 23:30 | 53 | 52 |  |  | 42813.9792 | 69 | 68
2017-03-20 | 50 | 48 |  |  | 42814 | 64 | 64
2017-03-20 00:30 | 46 | 45 |  |  | 42814.0208 | 61 | 61
2017-03-20 01:00 | 44 | 43 |  |  | 42814.0417 | 59 | 59
2017-03-20 01:30 | 41 | 39 |  |  | 42814.0625 | 56 | 56
2017-03-20 02:00 | 40 | 38 |  |  | 42814.0833 | 53 | 53
2017-03-20 02:30 | 39 | 36 |  |  | 42814.1042 | 50 | 50
2017-03-20 03:00 | 36 | 33 |  |  | 42814.125 | 46 | 46
2017-03-20 03:30 | 35 | 33 |  |  | 42814.1458 | 46 | 46
2017-03-20 04:00 | 35 | 33 |  |  | 42814.1667 | 46 | 46
2017-03-20 04:30 | 36 | 34 |  |  | 42814.1875 | 46 | 46
2017-03-20 05:00 | 37 | 36 |  |  | 42814.2083 | 49 | 49
2017-03-20 05:30 | 41 | 40 |  |  | 42814.2292 | 54 | 54
2017-03-20 06:00 | 47 | 45 |  |  | 42814.25 | 61 | 60
2017-03-20 06:30 | 53 | 52 |  |  | 42814.2708 | 72 | 72
2017-03-20 07:00 | 62 | 60 |  |  | 42814.2917 | 83 | 81
2017-03-20 07:30 | 69 | 67 |  |  | 42814.3125 | 92 | 90
2017-03-20 08:00 | 70 | 69 |  |  | 42814.3333 | 96 | 95
2017-03-20 08:30 | 72 | 71 |  |  | 42814.3542 | 104 | 102
2017-03-20 09:00 | 77 | 77 |  |  | 42814.375 | 107 | 106
2017-03-20 09:30 | 81 | 81 |  |  | 42814.3958 | 112 | 111
2017-03-20 10:00 | 82 | 82 |  |  | 42814.4167 | 111 | 110
2017-03-20 10:30 | 80 | 79 |  |  | 42814.4375 | 112 | 111
2017-03-20 11:00 | 80 | 80 |  |  | 42814.4583 | 112 | 111
2017-03-20 11:30 | 79 | 77 |  |  | 42814.4792 | 106 | 104
2017-03-20 12:00 | 82 | 79 |  |  | 42814.5 | 116 | 109
2017-03-20 12:30 | 86 | 83 |  |  | 42814.5208 | 122 | 115
2017-03-20 13:00 | 86 | 83 |  |  | 42814.5417 | 117 | 109
2017-03-20 13:30 | 85 | 81 |  |  | 42814.5625 | 116 | 108
2017-03-20 14:00 | 87 | 83 |  |  | 42814.5833 | 118 | 110
2017-03-20 14:30 | 86 | 83 |  |  | 42814.6042 | 119 | 111
2017-03-20 15:00 | 86 | 83 |  |  | 42814.625 | 118 | 109
2017-03-20 15:30 | 80 | 79 |  |  | 42814.6458 | 117 | 104
2017-03-20 16:00 | 78 | 78 |  |  | 42814.6667 | 109 | 104
2017-03-20 16:30 | 80 | 80 |  |  | 42814.6875 | 111 | 105
2017-03-20 17:00 | 80 | 80 |  |  | 42814.7083 | 110 | 104
2017-03-20 17:30 | 77 | 77 |  |  | 42814.7292 | 108 | 102
2017-03-20 18:00 | 72 | 72 |  |  | 42814.75 | 100 | 96
2017-03-20 18:30 | 72 | 72 |  |  | 42814.7708 | 96 | 94
2017-03-20 19:00 | 73 | 72 |  |  | 42814.7917 | 96 | 95
2017-03-20 19:30 | 71 | 70 |  |  | 42814.8125 | 92 | 91
2017-03-20 20:00 | 71 | 70 |  |  | 42814.8333 | 91 | 90
2017-03-20 20:30 | 71 | 70 |  |  | 42814.8542 | 90 | 89
2017-03-20 21:00 | 68 | 67 |  |  | 42814.875 | 85 | 83
2017-03-20 21:30 | 64 | 62 |  |  | 42814.8958 | 79 | 78
2017-03-20 22:00 | 62 | 61 |  |  | 42814.9167 | 78 | 77
2017-03-20 22:30 | 58 | 57 |  |  | 42814.9375 | 72 | 71
2017-03-20 23:00 | 57 | 56 |  |  | 42814.9583 | 71 | 69
2017-03-20 23:30 | 55 | 54 |  |  | 42814.9792 | 69 | 68
2017-03-21 | 49 | 49 |  |  | 42815 | 64 | 62
2017-03-21 00:30 | 48 | 48 |  |  | 42815.0208 | 63 | 62
2017-03-21 01:00 | 46 | 46 |  |  | 42815.0417 | 59 | 58
2017-03-21 01:30 | 43 | 43 |  |  | 42815.0625 | 55 | 54
2017-03-21 02:00 | 40 | 40 |  |  | 42815.0833 | 52 | 50
2017-03-21 02:30 | 40 | 40 |  |  | 42815.1042 | 53 | 52
2017-03-21 03:00 | 39 | 39 |  |  | 42815.125 | 53 | 51
2017-03-21 03:30 | 40 | 40 |  |  | 42815.1458 | 54 | 52
2017-03-21 04:00 | 40 | 40 |  |  | 42815.1667 | 54 | 52
2017-03-21 04:30 | 39 | 39 |  |  | 42815.1875 | 53 | 52
2017-03-21 05:00 | 40 | 40 |  |  | 42815.2083 | 56 | 54
2017-03-21 05:30 | 47 | 46 |  |  | 42815.2292 | 64 | 62
2017-03-21 06:00 | 52 | 52 |  |  | 42815.25 | 69 | 68
2017-03-21 06:30 | 59 | 59 |  |  | 42815.2708 | 81 | 80
2017-03-21 07:00 | 66 | 66 |  |  | 42815.2917 | 94 | 92
2017-03-21 07:30 | 71 | 71 |  |  | 42815.3125 | 104 | 101
2017-03-21 08:00 | 72 | 71 |  |  | 42815.3333 | 110 | 103
2017-03-21 08:30 | 74 | 73 |  |  | 42815.3542 | 110 | 106
2017-03-21 09:00 | 76 | 74 |  |  | 42815.375 | 110 | 108
2017-03-21 09:30 | 78 | 77 |  |  | 42815.3958 | 115 | 112
2017-03-21 10:00 | 80 | 79 |  |  | 42815.4167 | 116 | 114
2017-03-21 10:30 | 78 | 77 |  |  | 42815.4375 | 113 | 111
2017-03-21 11:00 | 77 | 76 |  |  | 42815.4583 | 111 | 109
2017-03-21 11:30 | 77 | 76 |  |  | 42815.4792 | 112 | 110
2017-03-21 12:00 | 79 | 77 |  |  | 42815.5 | 112 | 110
2017-03-21 12:30 | 78 | 75 |  |  | 42815.5208 | 112 | 110
2017-03-21 13:00 | 78 | 75 |  |  | 42815.5417 | 112 | 110
2017-03-21 13:30 | 78 | 76 |  |  | 42815.5625 | 113 | 110
2017-03-21 14:00 | 80 | 78 |  |  | 42815.5833 | 114 | 112
2017-03-21 14:30 | 80 | 78 |  |  | 42815.6042 | 114 | 111
2017-03-21 15:00 | 81 | 77 |  |  | 42815.625 | 115 | 112
2017-03-21 15:30 | 82 | 78 |  |  | 42815.6458 | 117 | 113
2017-03-21 16:00 | 83 | 79 |  |  | 42815.6667 | 117 | 113
2017-03-21 16:30 | 85 | 81 |  |  | 42815.6875 | 119 | 114
2017-03-21 17:00 | 87 | 83 |  |  | 42815.7083 | 120 | 115
2017-03-21 17:30 | 87 | 82 |  |  | 42815.7292 | 118 | 113
2017-03-21 18:00 | 86 | 81 |  |  | 42815.75 | 117 | 112
2017-03-21 18:30 | 88 | 83 |  |  | 42815.7708 | 117 | 111
2017-03-21 19:00 | 89 | 85 |  |  | 42815.7917 | 118 | 112
2017-03-21 19:30 | 85 | 82 |  |  | 42815.8125 | 111 | 109
2017-03-21 20:00 | 82 | 80 |  |  | 42815.8333 | 110 | 108
2017-03-21 20:30 | 80 | 79 |  |  | 42815.8542 | 106 | 105
2017-03-21 21:00 | 76 | 75 |  |  | 42815.875 | 99 | 98
2017-03-21 21:30 | 72 | 72 |  |  | 42815.8958 | 96 | 96
2017-03-21 22:00 | 70 | 69 |  |  | 42815.9167 | 92 | 92
2017-03-21 22:30 | 65 | 64 |  |  | 42815.9375 | 85 | 84
2017-03-21 23:00 | 63 | 62 |  |  | 42815.9583 | 83 | 82
2017-03-21 23:30 | 58 | 57 |  |  | 42815.9792 | 79 | 79
2017-03-22 | 54 | 53 |  |  | 42816 | 73 | 73
2017-03-22 00:30 | 51 | 50 |  |  | 42816.0208 | 70 | 70
2017-03-22 01:00 | 48 | 47 |  |  | 42816.0417 | 66 | 66
2017-03-22 01:30 | 45 | 44 |  |  | 42816.0625 | 63 | 63
2017-03-22 02:00 | 44 | 42 |  |  | 42816.0833 | 60 | 59
2017-03-22 02:30 | 42 | 40 |  |  | 42816.1042 | 58 | 58
2017-03-22 03:00 | 40 | 40 |  |  | 42816.125 | 57 | 57
2017-03-22 03:30 | 40 | 39 |  |  | 42816.1458 | 57 | 57
2017-03-22 04:00 | 40 | 39 |  |  | 42816.1667 | 58 | 58
2017-03-22 04:30 | 42 | 41 |  |  | 42816.1875 | 59 | 59
2017-03-22 05:00 | 47 | 47 |  |  | 42816.2083 | 63 | 63
2017-03-22 05:30 | 51 | 50 |  |  | 42816.2292 | 69 | 69
2017-03-22 06:00 | 57 | 56 |  |  | 42816.25 | 77 | 77
2017-03-22 06:30 | 64 | 64 |  |  | 42816.2708 | 87 | 87
2017-03-22 07:00 | 71 | 70 |  |  | 42816.2917 | 97 | 97
2017-03-22 07:30 | 75 | 73 |  |  | 42816.3125 | 104 | 103
2017-03-22 08:00 | 76 | 75 |  |  | 42816.3333 | 106 | 105
2017-03-22 08:30 | 75 | 74 |  |  | 42816.3542 | 106 | 106
2017-03-22 09:00 | 76 | 75 |  |  | 42816.375 | 109 | 108
2017-03-22 09:30 | 79 | 78 |  |  | 42816.3958 | 113 | 112
2017-03-22 10:00 | 79 | 79 |  |  | 42816.4167 | 115 | 115
2017-03-22 10:30 | 79 | 78 |  |  | 42816.4375 | 116 | 115
2017-03-22 11:00 | 80 | 80 |  |  | 42816.4583 | 116 | 115
2017-03-22 11:30 | 82 | 81 |  |  | 42816.4792 | 116 | 115
2017-03-22 12:00 | 82 | 82 |  |  | 42816.5 | 116 | 115
2017-03-22 12:30 | 83 | 82 |  |  | 42816.5208 | 115 | 114
2017-03-22 13:00 | 82 | 81 |  |  | 42816.5417 | 112 | 111
2017-03-22 13:30 | 80 | 79 |  |  | 42816.5625 | 112 | 111
2017-03-22 14:00 | 80 | 78 |  |  | 42816.5833 | 113 | 112
2017-03-22 14:30 | 79 | 77 |  |  | 42816.6042 | 112 | 111
2017-03-22 15:00 | 78 | 76 |  |  | 42816.625 | 111 | 110
2017-03-22 15:30 | 79 | 77 |  |  | 42816.6458 | 112 | 110
2017-03-22 16:00 | 79 | 77 |  |  | 42816.6667 | 113 | 111
2017-03-22 16:30 | 80 | 78 |  |  | 42816.6875 | 113 | 111
2017-03-22 17:00 | 80 | 78 |  |  | 42816.7083 | 112 | 110
2017-03-22 17:30 | 78 | 75 |  |  | 42816.7292 | 108 | 105
2017-03-22 18:00 | 75 | 72 |  |  | 42816.75 | 105 | 101
2017-03-22 18:30 | 76 | 73 |  |  | 42816.7708 | 102 | 100
2017-03-22 19:00 | 77 | 75 |  |  | 42816.7917 | 104 | 101
2017-03-22 19:30 | 75 | 73 |  |  | 42816.8125 | 101 | 99
2017-03-22 20:00 | 73 | 72 |  |  | 42816.8333 | 99 | 97
2017-03-22 20:30 | 71 | 70 |  |  | 42816.8542 | 96 | 94
2017-03-22 21:00 | 67 | 65 |  |  | 42816.875 | 90 | 89
2017-03-22 21:30 | 64 | 61 |  |  | 42816.8958 | 86 | 83
2017-03-22 22:00 | 58 | 57 |  |  | 42816.9167 | 80 | 79
2017-03-22 22:30 | 56 | 55 |  |  | 42816.9375 | 77 | 77
2017-03-22 23:00 | 61 | 60 |  |  | 42816.9583 | 82 | 81
2017-03-22 23:30 | 59 | 57 |  |  | 42816.9792 | 79 | 78
2017-03-23 | 54 | 52 |  |  | 42817 | 74 | 73
2017-03-23 00:30 | 51 | 49 |  |  | 42817.0208 | 72 | 71
2017-03-23 01:00 | 51 | 49 |  |  | 42817.0417 | 70 | 69
2017-03-23 01:30 | 47 | 43 |  |  | 42817.0625 | 66 | 64
2017-03-23 02:00 | 45 | 41 |  |  | 42817.0833 | 63 | 61
2017-03-23 02:30 | 45 | 41 |  |  | 42817.1042 | 61 | 59
2017-03-23 03:00 | 44 | 39 |  |  | 42817.125 | 60 | 58
2017-03-23 03:30 | 44 | 40 |  |  | 42817.1458 | 59 | 57
2017-03-23 04:00 | 43 | 39 |  |  | 42817.1667 | 59 | 57
2017-03-23 04:30 | 43 | 40 |  |  | 42817.1875 | 59 | 57
2017-03-23 05:00 | 46 | 43 |  |  | 42817.2083 | 64 | 62
2017-03-23 05:30 | 51 | 49 |  |  | 42817.2292 | 68 | 67
2017-03-23 06:00 | 56 | 54 |  |  | 42817.25 | 74 | 73
2017-03-23 06:30 | 60 | 59 |  |  | 42817.2708 | 84 | 83
2017-03-23 07:00 | 67 | 66 |  |  | 42817.2917 | 93 | 92
2017-03-23 07:30 | 72 | 72 |  |  | 42817.3125 | 101 | 101
2017-03-23 08:00 | 72 | 72 |  |  | 42817.3333 | 103 | 102
2017-03-23 08:30 | 75 | 75 |  |  | 42817.3542 | 106 | 105
2017-03-23 09:00 | 78 | 78 |  |  | 42817.375 | 109 | 108
2017-03-23 09:30 | 81 | 80 |  |  | 42817.3958 | 112 | 111
2017-03-23 10:00 | 80 | 80 |  |  | 42817.4167 | 112 | 112
2017-03-23 10:30 | 79 | 79 |  |  | 42817.4375 | 112 | 112
2017-03-23 11:00 | 78 | 78 |  |  | 42817.4583 | 112 | 112
2017-03-23 11:30 | 77 | 77 |  |  | 42817.4792 | 110 | 110
2017-03-23 12:00 | 79 | 79 |  |  | 42817.5 | 106 | 106
2017-03-23 12:30 | 77 | 77 |  |  | 42817.5208 | 106 | 106
2017-03-23 13:00 | 72 | 72 |  |  | 42817.5417 | 105 | 105
2017-03-23 13:30 | 75 | 75 |  |  | 42817.5625 | 107 | 107
2017-03-23 14:00 | 78 | 78 |  |  | 42817.5833 | 110 | 110
2017-03-23 14:30 | 80 | 80 |  |  | 42817.6042 | 113 | 113
2017-03-23 15:00 | 77 | 77 |  |  | 42817.625 | 110 | 109
2017-03-23 15:30 | 78 | 78 |  |  | 42817.6458 | 108 | 108
2017-03-23 16:00 | 79 | 79 |  |  | 42817.6667 | 110 | 110
2017-03-23 16:30 | 79 | 79 |  |  | 42817.6875 | 112 | 111
2017-03-23 17:00 | 81 | 80 |  |  | 42817.7083 | 112 | 111
2017-03-23 17:30 | 79 | 79 |  |  | 42817.7292 | 109 | 108
2017-03-23 18:00 | 78 | 77 |  |  | 42817.75 | 106 | 104
2017-03-23 18:30 | 79 | 78 |  |  | 42817.7708 | 108 | 104
2017-03-23 19:00 | 84 | 81 |  |  | 42817.7917 | 116 | 107
2017-03-23 19:30 | 82 | 79 |  |  | 42817.8125 | 113 | 104
2017-03-23 20:00 | 80 | 77 |  |  | 42817.8333 | 110 | 102
2017-03-23 20:30 | 80 | 78 |  |  | 42817.8542 | 108 | 101
2017-03-23 21:00 | 77 | 74 |  |  | 42817.875 | 103 | 95
2017-03-23 21:30 | 70 | 66 |  |  | 42817.8958 | 96 | 88
2017-03-23 22:00 | 65 | 63 |  |  | 42817.9167 | 90 | 85
2017-03-23 22:30 | 62 | 62 |  |  | 42817.9375 | 82 | 82
2017-03-23 23:00 | 66 | 66 |  |  | 42817.9583 | 85 | 84
2017-03-23 23:30 | 62 | 61 |  |  | 42817.9792 | 81 | 80
2017-03-24 | 56 | 56 |  |  | 42818 | 75 | 74
2017-03-24 00:30 | 54 | 53 |  |  | 42818.0208 | 71 | 71
2017-03-24 01:00 | 50 | 50 |  |  | 42818.0417 | 68 | 68
2017-03-24 01:30 | 48 | 47 |  |  | 42818.0625 | 63 | 63
2017-03-24 02:00 | 45 | 43 |  |  | 42818.0833 | 60 | 59
2017-03-24 02:30 | 43 | 42 |  |  | 42818.1042 | 59 | 58
2017-03-24 03:00 | 44 | 42 |  |  | 42818.125 | 59 | 58
2017-03-24 03:30 | 43 | 42 |  |  | 42818.1458 | 58 | 58
2017-03-24 04:00 | 43 | 41 |  |  | 42818.1667 | 58 | 57
2017-03-24 04:30 | 43 | 41 |  |  | 42818.1875 | 58 | 58
2017-03-24 05:00 | 48 | 46 |  |  | 42818.2083 | 63 | 62
2017-03-24 05:30 | 49 | 48 |  |  | 42818.2292 | 66 | 66
2017-03-24 06:00 | 55 | 54 |  |  | 42818.25 | 74 | 74
2017-03-24 06:30 | 63 | 62 |  |  | 42818.2708 | 86 | 86
2017-03-24 07:00 | 66 | 66 |  |  | 42818.2917 | 92 | 92
2017-03-24 07:30 | 72 | 72 |  |  | 42818.3125 | 100 | 99
2017-03-24 08:00 | 74 | 74 |  |  | 42818.3333 | 103 | 103
2017-03-24 08:30 | 75 | 75 |  |  | 42818.3542 | 106 | 106
2017-03-24 09:00 | 77 | 77 |  |  | 42818.375 | 110 | 110
2017-03-24 09:30 | 79 | 79 |  |  | 42818.3958 | 111 | 111
2017-03-24 10:00 | 79 | 79 |  |  | 42818.4167 | 111 | 111
2017-03-24 10:30 | 79 | 79 |  |  | 42818.4375 | 112 | 112
2017-03-24 11:00 | 79 | 79 |  |  | 42818.4583 | 109 | 109
2017-03-24 11:30 | 80 | 80 |  |  | 42818.4792 | 110 | 110
2017-03-24 12:00 | 81 | 81 |  |  | 42818.5 | 113 | 112
2017-03-24 12:30 | 82 | 82 |  |  | 42818.5208 | 116 | 115
2017-03-24 13:00 | 83 | 83 |  |  | 42818.5417 | 119 | 118
2017-03-24 13:30 | 84 | 84 |  |  | 42818.5625 | 118 | 118
2017-03-24 14:00 | 84 | 84 |  |  | 42818.5833 | 115 | 114
2017-03-24 14:30 | 81 | 81 |  |  | 42818.6042 | 110 | 108
2017-03-24 15:00 | 77 | 77 |  |  | 42818.625 | 108 | 107
2017-03-24 15:30 | 77 | 77 |  |  | 42818.6458 | 107 | 106
2017-03-24 16:00 | 79 | 78 |  |  | 42818.6667 | 107 | 106
2017-03-24 16:30 | 79 | 78 |  |  | 42818.6875 | 106 | 105
2017-03-24 17:00 | 78 | 77 |  |  | 42818.7083 | 104 | 103
2017-03-24 17:30 | 76 | 75 |  |  | 42818.7292 | 101 | 100
2017-03-24 18:00 | 73 | 72 |  |  | 42818.75 | 97 | 95
2017-03-24 18:30 | 72 | 72 |  |  | 42818.7708 | 94 | 94
2017-03-24 19:00 | 68 | 68 |  |  | 42818.7917 | 90 | 90
2017-03-24 19:30 | 65 | 65 |  |  | 42818.8125 | 86 | 86
2017-03-24 20:00 | 65 | 65 |  |  | 42818.8333 | 87 | 87
2017-03-24 20:30 | 65 | 65 |  |  | 42818.8542 | 86 | 86
2017-03-24 21:00 | 61 | 61 |  |  | 42818.875 | 80 | 80
2017-03-24 21:30 | 58 | 58 |  |  | 42818.8958 | 78 | 77
2017-03-24 22:00 | 55 | 55 |  |  | 42818.9167 | 75 | 74
2017-03-24 22:30 | 55 | 54 |  |  | 42818.9375 | 73 | 72
2017-03-24 23:00 | 59 | 58 |  |  | 42818.9583 | 75 | 74
2017-03-24 23:30 | 57 | 54 |  |  | 42818.9792 | 74 | 72
2017-03-25 | 55 | 49 |  |  | 42819 | 69 | 66
2017-03-25 00:30 | 53 | 46 |  |  | 42819.0208 | 66 | 63
2017-03-25 01:00 | 51 | 44 |  |  | 42819.0417 | 63 | 60
2017-03-25 01:30 | 49 | 42 |  |  | 42819.0625 | 59 | 56
2017-03-25 02:00 | 47 | 39 |  |  | 42819.0833 | 56 | 52
2017-03-25 02:30 | 45 | 36 |  |  | 42819.1042 | 54 | 50
2017-03-25 03:00 | 43 | 34 |  |  | 42819.125 | 51 | 47
2017-03-25 03:30 | 43 | 33 |  |  | 42819.1458 | 51 | 47
2017-03-25 04:00 | 42 | 33 |  |  | 42819.1667 | 52 | 47
2017-03-25 04:30 | 44 | 34 |  |  | 42819.1875 | 52 | 48
2017-03-25 05:00 | 45 | 36 |  |  | 42819.2083 | 54 | 49
2017-03-25 05:30 | 44 | 36 |  |  | 42819.2292 | 55 | 51
2017-03-25 06:00 | 44 | 36 |  |  | 42819.25 | 56 | 52
2017-03-25 06:30 | 47 | 39 |  |  | 42819.2708 | 60 | 57
2017-03-25 07:00 | 48 | 41 |  |  | 42819.2917 | 62 | 59
2017-03-25 07:30 | 48 | 42 |  |  | 42819.3125 | 65 | 62
2017-03-25 08:00 | 51 | 46 |  |  | 42819.3333 | 72 | 70
2017-03-25 08:30 | 53 | 49 |  |  | 42819.3542 | 76 | 75
2017-03-25 09:00 | 57 | 54 |  |  | 42819.375 | 81 | 80
2017-03-25 09:30 | 62 | 59 |  |  | 42819.3958 | 86 | 85
2017-03-25 10:00 | 63 | 61 |  |  | 42819.4167 | 87 | 86
2017-03-25 10:30 | 59 | 57 |  |  | 42819.4375 | 80 | 79
2017-03-25 11:00 | 57 | 55 |  |  | 42819.4583 | 77 | 76
2017-03-25 11:30 | 55 | 53 |  |  | 42819.4792 | 73 | 72
2017-03-25 12:00 | 54 | 51 |  |  | 42819.5 | 71 | 70
2017-03-25 12:30 | 55 | 53 |  |  | 42819.5208 | 71 | 70
2017-03-25 13:00 | 54 | 52 |  |  | 42819.5417 | 72 | 71
2017-03-25 13:30 | 55 | 53 |  |  | 42819.5625 | 75 | 74
2017-03-25 14:00 | 56 | 54 |  |  | 42819.5833 | 74 | 73
2017-03-25 14:30 | 55 | 52 |  |  | 42819.6042 | 70 | 69
2017-03-25 15:00 | 55 | 52 |  |  | 42819.625 | 71 | 70
2017-03-25 15:30 | 57 | 55 |  |  | 42819.6458 | 74 | 73
2017-03-25 16:00 | 60 | 57 |  |  | 42819.6667 | 76 | 75
2017-03-25 16:30 | 61 | 59 |  |  | 42819.6875 | 78 | 76
2017-03-25 17:00 | 65 | 63 |  |  | 42819.7083 | 82 | 81
2017-03-25 17:30 | 63 | 61 |  |  | 42819.7292 | 80 | 78
2017-03-25 18:00 | 62 | 58 |  |  | 42819.75 | 78 | 77
2017-03-25 18:30 | 64 | 61 |  |  | 42819.7708 | 82 | 81
2017-03-25 19:00 | 67 | 64 |  |  | 42819.7917 | 85 | 83
2017-03-25 19:30 | 66 | 63 |  |  | 42819.8125 | 84 | 83
2017-03-25 20:00 | 63 | 61 |  |  | 42819.8333 | 81 | 80
2017-03-25 20:30 | 62 | 60 |  |  | 42819.8542 | 79 | 78
2017-03-25 21:00 | 58 | 55 |  |  | 42819.875 | 75 | 74
2017-03-25 21:30 | 58 | 54 |  |  | 42819.8958 | 73 | 71
2017-03-25 22:00 | 56 | 52 |  |  | 42819.9167 | 71 | 69
2017-03-25 22:30 | 55 | 49 |  |  | 42819.9375 | 69 | 66
2017-03-25 23:00 | 59 | 54 |  |  | 42819.9583 | 71 | 68
2017-03-25 23:30 | 57 | 50 |  |  | 42819.9792 | 70 | 66
2017-03-26 | 54 | 46 |  |  | 42820 | 65 | 62
2017-03-26 00:30 | 51 | 44 |  |  | 42820.0208 | 62 | 58
2017-03-26 01:00 | 49 | 41 |  |  | 42820.0417 | 59 | 55
2017-03-26 01:30 | 45 | 37 |  |  | 42820.0625 | 54 | 50
2017-03-26 02:00 | 42 | 33 |  |  | 42820.0833 | 49 | 45
2017-03-26 02:30 | 40 | 30 |  |  | 42820.1042 | 46 | 41
2017-03-26 03:00 | 38 | 27 |  |  | 42820.125 | 44 | 38
2017-03-26 03:30 | 38 | 27 |  |  | 42820.1458 | 43 | 38
2017-03-26 04:00 | 38 | 27 |  |  | 42820.1667 | 43 | 38
2017-03-26 04:30 | 38 | 27 |  |  | 42820.1875 | 43 | 38
2017-03-26 05:00 | 39 | 28 |  |  | 42820.2083 | 44 | 39
2017-03-26 05:30 | 39 | 29 |  |  | 42820.2292 | 45 | 39
2017-03-26 06:00 | 39 | 29 |  |  | 42820.25 | 46 | 40
2017-03-26 06:30 | 40 | 29 |  |  | 42820.2708 | 48 | 43
2017-03-26 07:00 | 42 | 32 |  |  | 42820.2917 | 51 | 47
2017-03-26 07:30 | 41 | 32 |  |  | 42820.3125 | 52 | 48
2017-03-26 08:00 | 42 | 35 |  |  | 42820.3333 | 54 | 51
2017-03-26 08:30 | 43 | 37 |  |  | 42820.3542 | 56 | 53
2017-03-26 09:00 | 44 | 39 |  |  | 42820.375 | 59 | 57
2017-03-26 09:30 | 50 | 46 |  |  | 42820.3958 | 66 | 64
2017-03-26 10:00 | 52 | 49 |  |  | 42820.4167 | 68 | 67
2017-03-26 10:30 | 53 | 49 |  |  | 42820.4375 | 66 | 65
2017-03-26 11:00 | 53 | 51 |  |  | 42820.4583 | 67 | 67
2017-03-26 11:30 | 52 | 49 |  |  | 42820.4792 | 67 | 67
2017-03-26 12:00 | 52 | 50 |  |  | 42820.5 | 67 | 67
2017-03-26 12:30 | 52 | 50 |  |  | 42820.5208 | 66 | 65
2017-03-26 13:00 | 55 | 54 |  |  | 42820.5417 | 68 | 67
2017-03-26 13:30 | 59 | 57 |  |  | 42820.5625 | 70 | 70
2017-03-26 14:00 | 60 | 59 |  |  | 42820.5833 | 73 | 73
2017-03-26 14:30 | 61 | 60 |  |  | 42820.6042 | 76 | 75
2017-03-26 15:00 | 65 | 63 |  |  | 42820.625 | 77 | 77
2017-03-26 15:30 | 69 | 67 |  |  | 42820.6458 | 85 | 84
2017-03-26 16:00 | 70 | 68 |  |  | 42820.6667 | 85 | 84
2017-03-26 16:30 | 72 | 69 |  |  | 42820.6875 | 87 | 86
2017-03-26 17:00 | 74 | 72 |  |  | 42820.7083 | 88 | 86
2017-03-26 17:30 | 73 | 71 |  |  | 42820.7292 | 87 | 86
2017-03-26 18:00 | 73 | 70 |  |  | 42820.75 | 87 | 86
2017-03-26 18:30 | 75 | 73 |  |  | 42820.7708 | 91 | 89
2017-03-26 19:00 | 77 | 75 |  |  | 42820.7917 | 94 | 93
2017-03-26 19:30 | 76 | 73 |  |  | 42820.8125 | 92 | 91
2017-03-26 20:00 | 73 | 70 |  |  | 42820.8333 | 90 | 89
2017-03-26 20:30 | 69 | 67 |  |  | 42820.8542 | 87 | 86
2017-03-26 21:00 | 65 | 63 |  |  | 42820.875 | 82 | 81
2017-03-26 21:30 | 63 | 60 |  |  | 42820.8958 | 79 | 77
2017-03-26 22:00 | 59 | 56 |  |  | 42820.9167 | 75 | 73
2017-03-26 22:30 | 58 | 55 |  |  | 42820.9375 | 73 | 71
2017-03-26 23:00 | 59 | 55 |  |  | 42820.9583 | 73 | 71
2017-03-26 23:30 | 57 | 52 |  |  | 42820.9792 | 70 | 67
2017-03-27 | 52 | 47 |  |  | 42821 | 64 | 62
2017-03-27 00:30 | 49 | 44 |  |  | 42821.0208 | 61 | 58
2017-03-27 01:00 | 47 | 40 |  |  | 42821.0417 | 58 | 55
2017-03-27 01:30 | 46 | 40 |  |  | 42821.0625 | 55 | 52
2017-03-27 02:00 | 45 | 38 |  |  | 42821.0833 | 53 | 49
2017-03-27 02:30 | 43 | 35 |  |  | 42821.1042 | 51 | 47
2017-03-27 03:00 | 42 | 34 |  |  | 42821.125 | 49 | 45
2017-03-27 03:30 | 40 | 31 |  |  | 42821.1458 | 47 | 43
2017-03-27 04:00 | 40 | 31 |  |  | 42821.1667 | 47 | 43
2017-03-27 04:30 | 41 | 33 |  |  | 42821.1875 | 48 | 44
2017-03-27 05:00 | 42 | 35 |  |  | 42821.2083 | 51 | 48
2017-03-27 05:30 | 43 | 38 |  |  | 42821.2292 | 55 | 53
2017-03-27 06:00 | 47 | 43 |  |  | 42821.25 | 62 | 60
2017-03-27 06:30 | 57 | 54 |  |  | 42821.2708 | 74 | 74
2017-03-27 07:00 | 65 | 63 |  |  | 42821.2917 | 86 | 85
2017-03-27 07:30 | 68 | 67 |  |  | 42821.3125 | 92 | 92
2017-03-27 08:00 | 70 | 68 |  |  | 42821.3333 | 97 | 96
2017-03-27 08:30 | 72 | 71 |  |  | 42821.3542 | 101 | 100
2017-03-27 09:00 | 76 | 75 |  |  | 42821.375 | 105 | 104
2017-03-27 09:30 | 76 | 75 |  |  | 42821.3958 | 106 | 106
2017-03-27 10:00 | 76 | 76 |  |  | 42821.4167 | 106 | 106
2017-03-27 10:30 | 79 | 78 |  |  | 42821.4375 | 107 | 107
2017-03-27 11:00 | 80 | 79 |  |  | 42821.4583 | 109 | 108
2017-03-27 11:30 | 78 | 76 |  |  | 42821.4792 | 106 | 103
2017-03-27 12:00 | 77 | 74 |  |  | 42821.5 | 109 | 104
2017-03-27 12:30 | 80 | 77 |  |  | 42821.5208 | 111 | 105
2017-03-27 13:00 | 83 | 80 |  |  | 42821.5417 | 112 | 107
2017-03-27 13:30 | 122 | 120 |  |  | 42821.5625 | 78 | 72
2017-03-27 14:00 | 142 | 140 |  |  | 42821.5833 | 64 | 56
2017-03-27 14:30 | 142 | 140 |  |  | 42821.6042 | 67 | 58
2017-03-27 15:00 | 142 | 140 |  |  | 42821.625 | 66 | 56
2017-03-27 15:30 | 143 | 141 |  |  | 42821.6458 | 65 | 55
2017-03-27 16:00 | 145 | 144 |  |  | 42821.6667 | 67 | 56
2017-03-27 16:30 | 96 | 94 |  |  | 42821.6875 | 105 | 101
2017-03-27 17:00 | 86 | 83 |  |  | 42821.7083 | 113 | 109
2017-03-27 17:30 | 84 | 81 |  |  | 42821.7292 | 108 | 104
2017-03-27 18:00 | 80 | 79 |  |  | 42821.75 | 103 | 102
2017-03-27 18:30 | 79 | 78 |  |  | 42821.7708 | 101 | 100
2017-03-27 19:00 | 80 | 79 |  |  | 42821.7917 | 102 | 101
2017-03-27 19:30 | 76 | 75 |  |  | 42821.8125 | 96 | 96
2017-03-27 20:00 | 74 | 74 |  |  | 42821.8333 | 94 | 94
2017-03-27 20:30 | 72 | 72 |  |  | 42821.8542 | 91 | 91
2017-03-27 21:00 | 67 | 67 |  |  | 42821.875 | 86 | 86
2017-03-27 21:30 | 64 | 64 |  |  | 42821.8958 | 80 | 80
2017-03-27 22:00 | 59 | 59 |  |  | 42821.9167 | 75 | 75
2017-03-27 22:30 | 55 | 55 |  |  | 42821.9375 | 71 | 71
2017-03-27 23:00 | 56 | 55 |  |  | 42821.9583 | 70 | 70
2017-03-27 23:30 | 51 | 50 |  |  | 42821.9792 | 66 | 66
2017-03-28 | 48 | 47 |  |  | 42822 | 63 | 62
2017-03-28 00:30 | 44 | 43 |  |  | 42822.0208 | 59 | 59
2017-03-28 01:00 | 45 | 44 |  |  | 42822.0417 | 58 | 58
2017-03-28 01:30 | 44 | 41 |  |  | 42822.0625 | 54 | 54
2017-03-28 02:00 | 42 | 39 |  |  | 42822.0833 | 51 | 50
2017-03-28 02:30 | 40 | 37 |  |  | 42822.1042 | 50 | 49
2017-03-28 03:00 | 38 | 35 |  |  | 42822.125 | 45 | 45
2017-03-28 03:30 | 36 | 33 |  |  | 42822.1458 | 43 | 43
2017-03-28 04:00 | 36 | 32 |  |  | 42822.1667 | 43 | 43
2017-03-28 04:30 | 36 | 32 |  |  | 42822.1875 | 45 | 44
2017-03-28 05:00 | 38 | 34 |  |  | 42822.2083 | 48 | 48
2017-03-28 05:30 | 41 | 39 |  |  | 42822.2292 | 53 | 52
2017-03-28 06:00 | 46 | 45 |  |  | 42822.25 | 60 | 60
2017-03-28 06:30 | 55 | 54 |  |  | 42822.2708 | 73 | 73
2017-03-28 07:00 | 63 | 62 |  |  | 42822.2917 | 85 | 85
2017-03-28 07:30 | 66 | 65 |  |  | 42822.3125 | 92 | 91
2017-03-28 08:00 | 69 | 68 |  |  | 42822.3333 | 96 | 96
2017-03-28 08:30 | 80 | 70 |  |  | 42822.3542 | 104 | 99
2017-03-28 09:00 | 87 | 71 |  |  | 42822.375 | 111 | 102
2017-03-28 09:30 | 88 | 73 |  |  | 42822.3958 | 112 | 104
2017-03-28 10:00 | 87 | 72 |  |  | 42822.4167 | 114 | 106
2017-03-28 10:30 | 89 | 73 |  |  | 42822.4375 | 113 | 105
2017-03-28 11:00 | 90 | 75 |  |  | 42822.4583 | 113 | 107
2017-03-28 11:30 | 88 | 74 |  |  | 42822.4792 | 112 | 105
2017-03-28 12:00 | 87 | 73 |  |  | 42822.5 | 111 | 105
2017-03-28 12:30 | 87 | 74 |  |  | 42822.5208 | 110 | 104
2017-03-28 13:00 | 89 | 76 |  |  | 42822.5417 | 111 | 105
2017-03-28 13:30 | 91 | 78 |  |  | 42822.5625 | 113 | 107
2017-03-28 14:00 | 92 | 80 |  |  | 42822.5833 | 115 | 109
2017-03-28 14:30 | 97 | 82 |  |  | 42822.6042 | 120 | 111
2017-03-28 15:00 | 97 | 82 |  |  | 42822.625 | 120 | 111
2017-03-28 15:30 | 98 | 82 |  |  | 42822.6458 | 120 | 110
2017-03-28 16:00 | 100 | 84 |  |  | 42822.6667 | 122 | 111
2017-03-28 16:30 | 100 | 85 |  |  | 42822.6875 | 121 | 112
2017-03-28 17:00 | 97 | 84 |  |  | 42822.7083 | 118 | 110
2017-03-28 17:30 | 96 | 80 |  |  | 42822.7292 | 114 | 103
2017-03-28 18:00 | 90 | 78 |  |  | 42822.75 | 108 | 103
2017-03-28 18:30 | 90 | 78 |  |  | 42822.7708 | 106 | 101
2017-03-28 19:00 | 92 | 79 |  |  | 42822.7917 | 107 | 102
2017-03-28 19:30 | 87 | 76 |  |  | 42822.8125 | 101 | 97
2017-03-28 20:00 | 84 | 75 |  |  | 42822.8333 | 98 | 95
2017-03-28 20:30 | 80 | 73 |  |  | 42822.8542 | 95 | 93
2017-03-28 21:00 | 72 | 69 |  |  | 42822.875 | 88 | 87
2017-03-28 21:30 | 68 | 65 |  |  | 42822.8958 | 83 | 83
2017-03-28 22:00 | 65 | 62 |  |  | 42822.9167 | 80 | 80
2017-03-28 22:30 | 61 | 58 |  |  | 42822.9375 | 75 | 75
2017-03-28 23:00 | 60 | 56 |  |  | 42822.9583 | 72 | 71
2017-03-28 23:30 | 56 | 50 |  |  | 42822.9792 | 69 | 68
2017-03-29 | 53 | 48 |  |  | 42823 | 65 | 64
2017-03-29 00:30 | 52 | 45 |  |  | 42823.0208 | 62 | 61
2017-03-29 01:00 | 50 | 42 |  |  | 42823.0417 | 59 | 58
2017-03-29 01:30 | 48 | 40 |  |  | 42823.0625 | 54 | 54
2017-03-29 02:00 | 45 | 36 |  |  | 42823.0833 | 50 | 50
2017-03-29 02:30 | 44 | 35 |  |  | 42823.1042 | 47 | 47
2017-03-29 03:00 | 43 | 33 |  |  | 42823.125 | 48 | 48
2017-03-29 03:30 | 43 | 34 |  |  | 42823.1458 | 48 | 48
2017-03-29 04:00 | 44 | 34 |  |  | 42823.1667 | 48 | 48
2017-03-29 04:30 | 45 | 37 |  |  | 42823.1875 | 49 | 49
2017-03-29 05:00 | 47 | 40 |  |  | 42823.2083 | 55 | 55
2017-03-29 05:30 | 50 | 45 |  |  | 42823.2292 | 61 | 60
2017-03-29 06:00 | 56 | 50 |  |  | 42823.25 | 66 | 66
2017-03-29 06:30 | 63 | 59 |  |  | 42823.2708 | 79 | 78
2017-03-29 07:00 | 70 | 67 |  |  | 42823.2917 | 91 | 91
2017-03-29 07:30 | 78 | 74 |  |  | 42823.3125 | 102 | 102
2017-03-29 08:00 | 78 | 74 |  |  | 42823.3333 | 104 | 104
2017-03-29 08:30 | 81 | 78 |  |  | 42823.3542 | 110 | 110
2017-03-29 09:00 | 85 | 82 |  |  | 42823.375 | 115 | 115
2017-03-29 09:30 | 89 | 85 |  |  | 42823.3958 | 118 | 117
2017-03-29 10:00 | 91 | 85 |  |  | 42823.4167 | 117 | 115
2017-03-29 10:30 | 89 | 84 |  |  | 42823.4375 | 113 | 112
2017-03-29 11:00 | 90 | 84 |  |  | 42823.4583 | 114 | 113
2017-03-29 11:30 | 89 | 83 |  |  | 42823.4792 | 112 | 110
2017-03-29 12:00 | 88 | 83 |  |  | 42823.5 | 113 | 112
2017-03-29 12:30 | 84 | 77 |  |  | 42823.5208 | 110 | 109
2017-03-29 13:00 | 80 | 73 |  |  | 42823.5417 | 107 | 106
2017-03-29 13:30 | 81 | 78 |  |  | 42823.5625 | 109 | 108
2017-03-29 14:00 | 85 | 82 |  |  | 42823.5833 | 110 | 110
2017-03-29 14:30 | 87 | 85 |  |  | 42823.6042 | 115 | 114
2017-03-29 15:00 | 89 | 86 |  |  | 42823.625 | 115 | 114
2017-03-29 15:30 | 86 | 82 |  |  | 42823.6458 | 112 | 111
2017-03-29 16:00 | 85 | 81 |  |  | 42823.6667 | 112 | 111
2017-03-29 16:30 | 83 | 79 |  |  | 42823.6875 | 109 | 108
2017-03-29 17:00 | 82 | 78 |  |  | 42823.7083 | 108 | 107
2017-03-29 17:30 | 82 | 78 |  |  | 42823.7292 | 105 | 103
2017-03-29 18:00 | 84 | 79 |  |  | 42823.75 | 105 | 103
2017-03-29 18:30 | 82 | 76 |  |  | 42823.7708 | 102 | 99
2017-03-29 19:00 | 82 | 77 |  |  | 42823.7917 | 102 | 101
2017-03-29 19:30 | 79 | 76 |  |  | 42823.8125 | 100 | 99
2017-03-29 20:00 | 76 | 74 |  |  | 42823.8333 | 97 | 97
2017-03-29 20:30 | 75 | 73 |  |  | 42823.8542 | 95 | 95
2017-03-29 21:00 | 70 | 68 |  |  | 42823.875 | 88 | 88
2017-03-29 21:30 | 66 | 62 |  |  | 42823.8958 | 83 | 83
2017-03-29 22:00 | 64 | 60 |  |  | 42823.9167 | 80 | 80
2017-03-29 22:30 | 66 | 61 |  |  | 42823.9375 | 82 | 82
2017-03-29 23:00 | 65 | 60 |  |  | 42823.9583 | 79 | 79
2017-03-29 23:30 | 61 | 55 |  |  | 42823.9792 | 75 | 75
2017-03-30 | 60 | 52 |  |  | 42824 | 71 | 71
2017-03-30 00:30 | 56 | 49 |  |  | 42824.0208 | 65 | 65
2017-03-30 01:00 | 52 | 45 |  |  | 42824.0417 | 60 | 60
2017-03-30 01:30 | 49 | 41 |  |  | 42824.0625 | 57 | 56
2017-03-30 02:00 | 49 | 40 |  |  | 42824.0833 | 55 | 55
2017-03-30 02:30 | 47 | 39 |  |  | 42824.1042 | 54 | 53
2017-03-30 03:00 | 46 | 37 |  |  | 42824.125 | 52 | 52
2017-03-30 03:30 | 45 | 36 |  |  | 42824.1458 | 51 | 51
2017-03-30 04:00 | 46 | 37 |  |  | 42824.1667 | 51 | 51
2017-03-30 04:30 | 47 | 37 |  |  | 42824.1875 | 52 | 52
2017-03-30 05:00 | 42 | 41 |  |  | 42824.2083 | 57 | 56
2017-03-30 05:30 | 46 | 45 |  |  | 42824.2292 | 62 | 61
2017-03-30 06:00 | 51 | 50 |  |  | 42824.25 | 70 | 68
2017-03-30 06:30 | 64 | 60 |  |  | 42824.2708 | 90 | 83
2017-03-30 07:00 | 71 | 68 |  |  | 42824.2917 | 100 | 94
2017-03-30 07:30 | 78 | 75 |  |  | 42824.3125 | 110 | 105
2017-03-30 08:00 | 79 | 77 |  |  | 42824.3333 | 113 | 109
2017-03-30 08:30 | 82 | 80 |  |  | 42824.3542 | 117 | 114
2017-03-30 09:00 | 86 | 83 |  |  | 42824.375 | 118 | 115
2017-03-30 09:30 | 89 | 86 |  |  | 42824.3958 | 120 | 116
2017-03-30 10:00 | 88 | 86 |  |  | 42824.4167 | 117 | 114
2017-03-30 10:30 | 85 | 84 |  |  | 42824.4375 | 110 | 110
2017-03-30 11:00 | 82 | 81 |  |  | 42824.4583 | 109 | 108
2017-03-30 11:30 | 81 | 79 |  |  | 42824.4792 | 105 | 104
2017-03-30 12:00 | 79 | 78 |  |  | 42824.5 | 103 | 102
2017-03-30 12:30 | 76 | 74 |  |  | 42824.5208 | 101 | 100
2017-03-30 13:00 | 74 | 73 |  |  | 42824.5417 | 101 | 100
2017-03-30 13:30 | 72 | 71 |  |  | 42824.5625 | 99 | 99
2017-03-30 14:00 | 71 | 70 |  |  | 42824.5833 | 98 | 98
2017-03-30 14:30 | 70 | 69 |  |  | 42824.6042 | 96 | 96
2017-03-30 15:00 | 69 | 68 |  |  | 42824.625 | 97 | 97
2017-03-30 15:30 | 67 | 66 |  |  | 42824.6458 | 95 | 95
2017-03-30 16:00 | 66 | 64 |  |  | 42824.6667 | 93 | 92
2017-03-30 16:30 | 66 | 65 |  |  | 42824.6875 | 94 | 94
2017-03-30 17:00 | 66 | 65 |  |  | 42824.7083 | 95 | 94
2017-03-30 17:30 | 66 | 65 |  |  | 42824.7292 | 94 | 94
2017-03-30 18:00 | 65 | 64 |  |  | 42824.75 | 91 | 91
2017-03-30 18:30 | 66 | 65 |  |  | 42824.7708 | 92 | 92
2017-03-30 19:00 | 68 | 66 |  |  | 42824.7917 | 94 | 94
2017-03-30 19:30 | 66 | 64 |  |  | 42824.8125 | 90 | 89
2017-03-30 20:00 | 64 | 63 |  |  | 42824.8333 | 88 | 87
2017-03-30 20:30 | 64 | 62 |  |  | 42824.8542 | 84 | 84
2017-03-30 21:00 | 60 | 59 |  |  | 42824.875 | 79 | 79
2017-03-30 21:30 | 56 | 55 |  |  | 42824.8958 | 75 | 74
2017-03-30 22:00 | 54 | 52 |  |  | 42824.9167 | 73 | 71
2017-03-30 22:30 | 54 | 51 |  |  | 42824.9375 | 72 | 70
2017-03-30 23:00 | 54 | 51 |  |  | 42824.9583 | 70 | 68
2017-03-30 23:30 | 50 | 46 |  |  | 42824.9792 | 66 | 64
2017-03-31 | 47 | 43 |  |  | 42825 | 64 | 63
2017-03-31 00:30 | 44 | 41 |  |  | 42825.0208 | 60 | 58
2017-03-31 01:00 | 42 | 38 |  |  | 42825.0417 | 56 | 54
2017-03-31 01:30 | 40 | 36 |  |  | 42825.0625 | 53 | 51
2017-03-31 02:00 | 40 | 36 |  |  | 42825.0833 | 53 | 51
2017-03-31 02:30 | 40 | 36 |  |  | 42825.1042 | 53 | 51
2017-03-31 03:00 | 40 | 36 |  |  | 42825.125 | 54 | 51
2017-03-31 03:30 | 40 | 36 |  |  | 42825.1458 | 51 | 49
2017-03-31 04:00 | 40 | 36 |  |  | 42825.1667 | 51 | 49
2017-03-31 04:30 | 40 | 36 |  |  | 42825.1875 | 50 | 48
2017-03-31 05:00 | 41 | 38 |  |  | 42825.2083 | 52 | 50
2017-03-31 05:30 | 45 | 43 |  |  | 42825.2292 | 56 | 54
2017-03-31 06:00 | 47 | 45 |  |  | 42825.25 | 62 | 61
2017-03-31 06:30 | 52 | 51 |  |  | 42825.2708 | 70 | 70
2017-03-31 07:00 | 56 | 56 |  |  | 42825.2917 | 78 | 77
2017-03-31 07:30 | 62 | 62 |  |  | 42825.3125 | 86 | 86
2017-03-31 08:00 | 64 | 64 |  |  | 42825.3333 | 89 | 89
2017-03-31 08:30 | 65 | 65 |  |  | 42825.3542 | 90 | 90
2017-03-31 09:00 | 66 | 66 |  |  | 42825.375 | 91 | 91
2017-03-31 09:30 | 68 | 67 |  |  | 42825.3958 | 94 | 92
2017-03-31 10:00 | 68 | 67 |  |  | 42825.4167 | 94 | 91
2017-03-31 10:30 | 70 | 68 |  |  | 42825.4375 | 95 | 92
2017-03-31 11:00 | 71 | 69 |  |  | 42825.4583 | 95 | 92
2017-03-31 11:30 | 69 | 68 |  |  | 42825.4792 | 93 | 90
2017-03-31 12:00 | 68 | 66 |  |  | 42825.5 | 93 | 90
2017-03-31 12:30 | 70 | 68 |  |  | 42825.5208 | 94 | 92
2017-03-31 13:00 | 74 | 73 |  |  | 42825.5417 | 99 | 96
2017-03-31 13:30 | 78 | 77 |  |  | 42825.5625 | 103 | 100
2017-03-31 14:00 | 78 | 76 |  |  | 42825.5833 | 105 | 102
2017-03-31 14:30 | 79 | 77 |  |  | 42825.6042 | 107 | 104
2017-03-31 15:00 | 79 | 77 |  |  | 42825.625 | 107 | 104
2017-03-31 15:30 | 79 | 77 |  |  | 42825.6458 | 108 | 105
2017-03-31 16:00 | 78 | 75 |  |  | 42825.6667 | 106 | 101
2017-03-31 16:30 | 78 | 75 |  |  | 42825.6875 | 106 | 101
2017-03-31 17:00 | 79 | 76 |  |  | 42825.7083 | 105 | 100
2017-03-31 17:30 | 77 | 73 |  |  | 42825.7292 | 101 | 96
2017-03-31 18:00 | 73 | 69 |  |  | 42825.75 | 97 | 90
2017-03-31 18:30 | 70 | 66 |  |  | 42825.7708 | 95 | 88
2017-03-31 19:00 | 71 | 67 |  |  | 42825.7917 | 96 | 89
2017-03-31 19:30 | 69 | 64 |  |  | 42825.8125 | 93 | 85
2017-03-31 20:00 | 67 | 62 |  |  | 42825.8333 | 90 | 83
2017-03-31 20:30 | 65 | 61 |  |  | 42825.8542 | 88 | 82
2017-03-31 21:00 | 61 | 58 |  |  | 42825.875 | 84 | 77
2017-03-31 21:30 | 58 | 56 |  |  | 42825.8958 | 78 | 75
2017-03-31 22:00 | 57 | 53 |  |  | 42825.9167 | 77 | 74
2017-03-31 22:30 | 56 | 52 |  |  | 42825.9375 | 77 | 73
2017-03-31 23:00 | 56 | 51 |  |  | 42825.9583 | 74 | 70
2017-03-31 23:30 | 52 | 47 |  |  | 42825.9792 | 69 | 65
2017-04-01 | 46 | 40 |  |  | 42826 | 63 | 58
2017-04-01 00:30 | 43 | 37 |  |  | 42826.0208 | 59 | 53
2017-04-01 01:00 | 42 | 34 |  |  | 42826.0417 | 56 | 49
2017-04-01 01:30 | 39 | 33 |  |  | 42826.0625 | 56 | 47
2017-04-01 02:00 | 34 | 31 |  |  | 42826.0833 | 58 | 44
2017-04-01 02:30 | 33 | 31 |  |  | 42826.1042 | 56 | 42
2017-04-01 03:00 | 32 | 31 |  |  | 42826.125 | 52 | 42
2017-04-01 03:30 | 32 | 31 |  |  | 42826.1458 | 52 | 42
2017-04-01 04:00 | 32 | 30 |  |  | 42826.1667 | 51 | 41
2017-04-01 04:30 | 32 | 31 |  |  | 42826.1875 | 51 | 41
2017-04-01 05:00 | 32 | 31 |  |  | 42826.2083 | 51 | 41
2017-04-01 05:30 | 31 | 31 |  |  | 42826.2292 | 52 | 43
2017-04-01 06:00 | 31 | 31 |  |  | 42826.25 | 53 | 45
2017-04-01 06:30 | 31 | 30 |  |  | 42826.2708 | 53 | 45
2017-04-01 07:00 | 31 | 31 |  |  | 42826.2917 | 55 | 47
2017-04-01 07:30 | 33 | 33 |  |  | 42826.3125 | 56 | 50
2017-04-01 08:00 | 35 | 34 |  |  | 42826.3333 | 57 | 52
2017-04-01 08:30 | 36 | 36 |  |  | 42826.3542 | 59 | 55
2017-04-01 09:00 | 38 | 38 |  |  | 42826.375 | 60 | 57
2017-04-01 09:30 | 39 | 39 |  |  | 42826.3958 | 61 | 58
2017-04-01 10:00 | 40 | 40 |  |  | 42826.4167 | 61 | 58
2017-04-01 10:30 | 42 | 42 |  |  | 42826.4375 | 61 | 59
2017-04-01 11:00 | 41 | 41 |  |  | 42826.4583 | 60 | 57
2017-04-01 11:30 | 42 | 42 |  |  | 42826.4792 | 60 | 58
2017-04-01 12:00 | 41 | 41 |  |  | 42826.5 | 60 | 57
2017-04-01 12:30 | 40 | 40 |  |  | 42826.5208 | 58 | 55
2017-04-01 13:00 | 41 | 41 |  |  | 42826.5417 | 60 | 57
2017-04-01 13:30 | 42 | 42 |  |  | 42826.5625 | 62 | 60
2017-04-01 14:00 | 42 | 42 |  |  | 42826.5833 | 62 | 59
2017-04-01 14:30 | 44 | 43 |  |  | 42826.6042 | 64 | 61
2017-04-01 15:00 | 46 | 46 |  |  | 42826.625 | 67 | 64
2017-04-01 15:30 | 48 | 48 |  |  | 42826.6458 | 70 | 66
2017-04-01 16:00 | 49 | 49 |  |  | 42826.6667 | 73 | 68
2017-04-01 16:30 | 51 | 50 |  |  | 42826.6875 | 78 | 70
2017-04-01 17:00 | 51 | 50 |  |  | 42826.7083 | 79 | 70
2017-04-01 17:30 | 50 | 50 |  |  | 42826.7292 | 78 | 69
2017-04-01 18:00 | 51 | 50 |  |  | 42826.75 | 78 | 69
2017-04-01 18:30 | 52 | 51 |  |  | 42826.7708 | 79 | 70
2017-04-01 19:00 | 52 | 51 |  |  | 42826.7917 | 81 | 72
2017-04-01 19:30 | 52 | 52 |  |  | 42826.8125 | 80 | 71
2017-04-01 20:00 | 52 | 51 |  |  | 42826.8333 | 80 | 70
2017-04-01 20:30 | 50 | 49 |  |  | 42826.8542 | 78 | 67
2017-04-01 21:00 | 48 | 47 |  |  | 42826.875 | 75 | 64
2017-04-01 21:30 | 46 | 46 |  |  | 42826.8958 | 70 | 63
2017-04-01 22:00 | 46 | 45 |  |  | 42826.9167 | 69 | 63
2017-04-01 22:30 | 45 | 45 |  |  | 42826.9375 | 69 | 63
2017-04-01 23:00 | 45 | 45 |  |  | 42826.9583 | 66 | 60
2017-04-01 23:30 | 40 | 40 |  |  | 42826.9792 | 62 | 55
2017-04-02 | 37 | 36 |  |  | 42827 | 59 | 51
2017-04-02 00:30 | 34 | 33 |  |  | 42827.0208 | 56 | 46
2017-04-02 01:00 | 32 | 31 |  |  | 42827.0417 | 53 | 42
2017-04-02 01:30 | 30 | 29 |  |  | 42827.0625 | 51 | 40
2017-04-02 02:00 | 27 | 25 |  |  | 42827.0833 | 47 | 36
2017-04-02 02:30 | 25 | 23 |  |  | 42827.1042 | 46 | 33
2017-04-02 03:00 | 25 | 23 |  |  | 42827.125 | 46 | 33
2017-04-02 03:30 | 24 | 23 |  |  | 42827.1458 | 45 | 33
2017-04-02 04:00 | 23 | 21 |  |  | 42827.1667 | 44 | 32
2017-04-02 04:30 | 23 | 21 |  |  | 42827.1875 | 44 | 32
2017-04-02 05:00 | 24 | 23 |  |  | 42827.2083 | 45 | 33
2017-04-02 05:30 | 25 | 23 |  |  | 42827.2292 | 46 | 34
2017-04-02 06:00 | 25 | 23 |  |  | 42827.25 | 46 | 34
2017-04-02 06:30 | 25 | 23 |  |  | 42827.2708 | 47 | 35
2017-04-02 07:00 | 25 | 23 |  |  | 42827.2917 | 48 | 37
2017-04-02 07:30 | 25 | 23 |  |  | 42827.3125 | 50 | 39
2017-04-02 08:00 | 25 | 24 |  |  | 42827.3333 | 50 | 40
2017-04-02 08:30 | 29 | 28 |  |  | 42827.3542 | 52 | 44
2017-04-02 09:00 | 32 | 31 |  |  | 42827.375 | 56 | 49
2017-04-02 09:30 | 37 | 37 |  |  | 42827.3958 | 59 | 53
2017-04-02 10:00 | 40 | 40 |  |  | 42827.4167 | 65 | 60
2017-04-02 10:30 | 42 | 41 |  |  | 42827.4375 | 65 | 60
2017-04-02 11:00 | 43 | 42 |  |  | 42827.4583 | 67 | 62
2017-04-02 11:30 | 43 | 43 |  |  | 42827.4792 | 66 | 61
2017-04-02 12:00 | 43 | 42 |  |  | 42827.5 | 63 | 57
2017-04-02 12:30 | 42 | 42 |  |  | 42827.5208 | 63 | 58
2017-04-02 13:00 | 42 | 42 |  |  | 42827.5417 | 64 | 59
2017-04-02 13:30 | 41 | 41 |  |  | 42827.5625 | 64 | 58
2017-04-02 14:00 | 43 | 43 |  |  | 42827.5833 | 66 | 61
2017-04-02 14:30 | 48 | 48 |  |  | 42827.6042 | 72 | 67
2017-04-02 15:00 | 47 | 46 |  |  | 42827.625 | 70 | 65
2017-04-02 15:30 | 45 | 45 |  |  | 42827.6458 | 70 | 64
2017-04-02 16:00 | 47 | 47 |  |  | 42827.6667 | 71 | 66
2017-04-02 16:30 | 50 | 49 |  |  | 42827.6875 | 74 | 69
2017-04-02 17:00 | 53 | 52 |  |  | 42827.7083 | 78 | 72
2017-04-02 17:30 | 56 | 54 |  |  | 42827.7292 | 84 | 73
2017-04-02 18:00 | 57 | 55 |  |  | 42827.75 | 85 | 74
2017-04-02 18:30 | 58 | 56 |  |  | 42827.7708 | 87 | 77
2017-04-02 19:00 | 60 | 58 |  |  | 42827.7917 | 90 | 80
2017-04-02 19:30 | 58 | 56 |  |  | 42827.8125 | 87 | 77
2017-04-02 20:00 | 56 | 55 |  |  | 42827.8333 | 84 | 75
2017-04-02 20:30 | 56 | 54 |  |  | 42827.8542 | 83 | 73
2017-04-02 21:00 | 53 | 51 |  |  | 42827.875 | 79 | 69
2017-04-02 21:30 | 50 | 49 |  |  | 42827.8958 | 74 | 67
2017-04-02 22:00 | 48 | 47 |  |  | 42827.9167 | 72 | 65
2017-04-02 22:30 | 46 | 45 |  |  | 42827.9375 | 70 | 63
2017-04-02 23:00 | 43 | 42 |  |  | 42827.9583 | 65 | 58
2017-04-02 23:30 | 40 | 39 |  |  | 42827.9792 | 62 | 54
2017-04-03 | 36 | 35 |  |  | 42828 | 59 | 51
2017-04-03 00:30 | 33 | 31 |  |  | 42828.0208 | 54 | 44
2017-04-03 01:00 | 29 | 28 |  |  | 42828.0417 | 50 | 39
2017-04-03 01:30 | 27 | 27 |  |  | 42828.0625 | 47 | 39
2017-04-03 02:00 | 28 | 28 |  |  | 42828.0833 | 47 | 40
2017-04-03 02:30 | 26 | 25 |  |  | 42828.1042 | 45 | 36
2017-04-03 03:00 | 24 | 23 |  |  | 42828.125 | 43 | 34
2017-04-03 03:30 | 23 | 22 |  |  | 42828.1458 | 42 | 33
2017-04-03 04:00 | 25 | 24 |  |  | 42828.1667 | 44 | 35
2017-04-03 04:30 | 27 | 27 |  |  | 42828.1875 | 46 | 37
2017-04-03 05:00 | 28 | 28 |  |  | 42828.2083 | 46 | 39
2017-04-03 05:30 | 30 | 30 |  |  | 42828.2292 | 48 | 42
2017-04-03 06:00 | 35 | 35 |  |  | 42828.25 | 53 | 48
2017-04-03 06:30 | 40 | 39 |  |  | 42828.2708 | 65 | 57
2017-04-03 07:00 | 45 | 45 |  |  | 42828.2917 | 71 | 64
2017-04-03 07:30 | 47 | 47 |  |  | 42828.3125 | 76 | 69
2017-04-03 08:00 | 48 | 48 |  |  | 42828.3333 | 79 | 73
2017-04-03 08:30 | 49 | 49 |  |  | 42828.3542 | 78 | 73
2017-04-03 09:00 | 50 | 50 |  |  | 42828.375 | 80 | 76
2017-04-03 09:30 | 53 | 53 |  |  | 42828.3958 | 83 | 79
2017-04-03 10:00 | 58 | 57 |  |  | 42828.4167 | 87 | 84
2017-04-03 10:30 | 59 | 57 |  |  | 42828.4375 | 85 | 83
2017-04-03 11:00 | 55 | 52 |  |  | 42828.4583 | 81 | 79
2017-04-03 11:30 | 58 | 57 |  |  | 42828.4792 | 87 | 84
2017-04-03 12:00 | 61 | 59 |  |  | 42828.5 | 89 | 86
2017-04-03 12:30 | 61 | 60 |  |  | 42828.5208 | 89 | 85
2017-04-03 13:00 | 60 | 59 |  |  | 42828.5417 | 87 | 83
2017-04-03 13:30 | 55 | 54 |  |  | 42828.5625 | 83 | 79
2017-04-03 14:00 | 61 | 60 |  |  | 42828.5833 | 90 | 86
2017-04-03 14:30 | 65 | 64 |  |  | 42828.6042 | 93 | 89
2017-04-03 15:00 | 62 | 61 |  |  | 42828.625 | 91 | 87
2017-04-03 15:30 | 57 | 57 |  |  | 42828.6458 | 88 | 83
2017-04-03 16:00 | 58 | 57 |  |  | 42828.6667 | 88 | 83
2017-04-03 16:30 | 61 | 60 |  |  | 42828.6875 | 90 | 85
2017-04-03 17:00 | 60 | 60 |  |  | 42828.7083 | 89 | 83
2017-04-03 17:30 | 60 | 60 |  |  | 42828.7292 | 87 | 81
2017-04-03 18:00 | 61 | 60 |  |  | 42828.75 | 86 | 80
2017-04-03 18:30 | 59 | 59 |  |  | 42828.7708 | 84 | 78
2017-04-03 19:00 | 60 | 59 |  |  | 42828.7917 | 84 | 79
2017-04-03 19:30 | 58 | 56 |  |  | 42828.8125 | 79 | 75
2017-04-03 20:00 | 56 | 55 |  |  | 42828.8333 | 77 | 73
2017-04-03 20:30 | 55 | 53 |  |  | 42828.8542 | 75 | 71
2017-04-03 21:00 | 53 | 51 |  |  | 42828.875 | 67 | 66
2017-04-03 21:30 | 51 | 50 |  |  | 42828.8958 | 67 | 65
2017-04-03 22:00 | 49 | 47 |  |  | 42828.9167 | 65 | 64
2017-04-03 22:30 | 49 | 47 |  |  | 42828.9375 | 63 | 63
2017-04-03 23:00 | 48 | 46 |  |  | 42828.9583 | 61 | 60
2017-04-03 23:30 | 44 | 41 |  |  | 42828.9792 | 56 | 55
2017-04-04 | 37 | 36 |  |  | 42829 | 50 | 48
2017-04-04 00:30 | 33 | 32 |  |  | 42829.0208 | 46 | 44
2017-04-04 01:00 | 32 | 30 |  |  | 42829.0417 | 42 | 40
2017-04-04 01:30 | 30 | 29 |  |  | 42829.0625 | 42 | 39
2017-04-04 02:00 | 28 | 27 |  |  | 42829.0833 | 40 | 37
2017-04-04 02:30 | 28 | 26 |  |  | 42829.1042 | 38 | 35
2017-04-04 03:00 | 25 | 23 |  |  | 42829.125 | 37 | 33
2017-04-04 03:30 | 23 | 22 |  |  | 42829.1458 | 35 | 32
2017-04-04 04:00 | 24 | 23 |  |  | 42829.1667 | 37 | 33
2017-04-04 04:30 | 26 | 24 |  |  | 42829.1875 | 37 | 34
2017-04-04 05:00 | 28 | 26 |  |  | 42829.2083 | 39 | 36
2017-04-04 05:30 | 32 | 31 |  |  | 42829.2292 | 43 | 40
2017-04-04 06:00 | 35 | 33 |  |  | 42829.25 | 48 | 46
2017-04-04 06:30 | 39 | 37 |  |  | 42829.2708 | 54 | 53
2017-04-04 07:00 | 43 | 41 |  |  | 42829.2917 | 61 | 60
2017-04-04 07:30 | 45 | 43 |  |  | 42829.3125 | 65 | 65
2017-04-04 08:00 | 48 | 45 |  |  | 42829.3333 | 68 | 68
2017-04-04 08:30 | 55 | 52 |  |  | 42829.3542 | 75 | 75
2017-04-04 09:00 | 55 | 51 |  |  | 42829.375 | 74 | 74
2017-04-04 09:30 | 50 | 49 |  |  | 42829.3958 | 74 | 72
2017-04-04 10:00 | 51 | 50 |  |  | 42829.4167 | 77 | 74
2017-04-04 10:30 | 57 | 56 |  |  | 42829.4375 | 83 | 81
2017-04-04 11:00 | 57 | 57 |  |  | 42829.4583 | 86 | 83
2017-04-04 11:30 | 55 | 54 |  |  | 42829.4792 | 83 | 80
2017-04-04 12:00 | 60 | 59 |  |  | 42829.5 | 85 | 82
2017-04-04 12:30 | 52 | 52 |  |  | 42829.5208 | 81 | 77
2017-04-04 13:00 | 55 | 55 |  |  | 42829.5417 | 79 | 75
2017-04-04 13:30 | 59 | 58 |  |  | 42829.5625 | 83 | 79
2017-04-04 14:00 | 54 | 54 |  |  | 42829.5833 | 79 | 75
2017-04-04 14:30 | 59 | 59 |  |  | 42829.6042 | 82 | 78
2017-04-04 15:00 | 55 | 54 |  |  | 42829.625 | 80 | 76
2017-04-04 15:30 | 59 | 58 |  |  | 42829.6458 | 81 | 78
2017-04-04 16:00 | 56 | 56 |  |  | 42829.6667 | 82 | 78
2017-04-04 16:30 | 59 | 58 |  |  | 42829.6875 | 85 | 81
2017-04-04 17:00 | 60 | 60 |  |  | 42829.7083 | 88 | 84
2017-04-04 17:30 | 60 | 60 |  |  | 42829.7292 | 85 | 80
2017-04-04 18:00 | 58 | 58 |  |  | 42829.75 | 84 | 78
2017-04-04 18:30 | 59 | 59 |  |  | 42829.7708 | 84 | 78
2017-04-04 19:00 | 61 | 61 |  |  | 42829.7917 | 85 | 79
2017-04-04 19:30 | 60 | 59 |  |  | 42829.8125 | 79 | 76
2017-04-04 20:00 | 57 | 55 |  |  | 42829.8333 | 74 | 74
2017-04-04 20:30 | 56 | 54 |  |  | 42829.8542 | 71 | 71
2017-04-04 21:00 | 53 | 50 |  |  | 42829.875 | 65 | 65
2017-04-04 21:30 | 49 | 47 |  |  | 42829.8958 | 62 | 61
2017-04-04 22:00 | 46 | 44 |  |  | 42829.9167 | 60 | 59
2017-04-04 22:30 | 46 | 44 |  |  | 42829.9375 | 60 | 60
2017-04-04 23:00 | 45 | 43 |  |  | 42829.9583 | 58 | 58
2017-04-04 23:30 | 40 | 39 |  |  | 42829.9792 | 54 | 52
2017-04-05 | 36 | 35 |  |  | 42830 | 48 | 46
2017-04-05 00:30 | 33 | 31 |  |  | 42830.0208 | 44 | 41
2017-04-05 01:00 | 30 | 28 |  |  | 42830.0417 | 40 | 37
2017-04-05 01:30 | 28 | 26 |  |  | 42830.0625 | 37 | 34
2017-04-05 02:00 | 26 | 25 |  |  | 42830.0833 | 36 | 33
2017-04-05 02:30 | 26 | 24 |  |  | 42830.1042 | 36 | 33
2017-04-05 03:00 | 25 | 23 |  |  | 42830.125 | 34 | 31
2017-04-05 03:30 | 26 | 25 |  |  | 42830.1458 | 36 | 34
2017-04-05 04:00 | 28 | 26 |  |  | 42830.1667 | 38 | 35
2017-04-05 04:30 | 28 | 27 |  |  | 42830.1875 | 38 | 35
2017-04-05 05:00 | 31 | 29 |  |  | 42830.2083 | 41 | 39
2017-04-05 05:30 | 34 | 33 |  |  | 42830.2292 | 46 | 43
2017-04-05 06:00 | 38 | 37 |  |  | 42830.25 | 50 | 49
2017-04-05 06:30 | 43 | 41 |  |  | 42830.2708 | 58 | 57
2017-04-05 07:00 | 45 | 45 |  |  | 42830.2917 | 66 | 63
2017-04-05 07:30 | 49 | 49 |  |  | 42830.3125 | 72 | 70
2017-04-05 08:00 | 52 | 52 |  |  | 42830.3333 | 79 | 76
2017-04-05 08:30 | 56 | 56 |  |  | 42830.3542 | 84 | 78
2017-04-05 09:00 | 56 | 56 |  |  | 42830.375 | 81 | 76
2017-04-05 09:30 | 55 | 55 |  |  | 42830.3958 | 80 | 75
2017-04-05 10:00 | 56 | 56 |  |  | 42830.4167 | 82 | 79
2017-04-05 10:30 | 57 | 57 |  |  | 42830.4375 | 84 | 79
2017-04-05 11:00 | 60 | 60 |  |  | 42830.4583 | 86 | 81
2017-04-05 11:30 | 59 | 59 |  |  | 42830.4792 | 85 | 80
2017-04-05 12:00 | 58 | 58 |  |  | 42830.5 | 86 | 80
2017-04-05 12:30 | 56 | 55 |  |  | 42830.5208 | 83 | 77
2017-04-05 13:00 | 55 | 55 |  |  | 42830.5417 | 84 | 77
2017-04-05 13:30 | 55 | 54 |  |  | 42830.5625 | 81 | 73
2017-04-05 14:00 | 54 | 54 |  |  | 42830.5833 | 81 | 74
2017-04-05 14:30 | 54 | 54 |  |  | 42830.6042 | 81 | 73
2017-04-05 15:00 | 51 | 51 |  |  | 42830.625 | 82 | 75
2017-04-05 15:30 | 56 | 56 |  |  | 42830.6458 | 86 | 78
2017-04-05 16:00 | 58 | 58 |  |  | 42830.6667 | 87 | 78
2017-04-05 16:30 | 58 | 58 |  |  | 42830.6875 | 88 | 80
2017-04-05 17:00 | 59 | 58 |  |  | 42830.7083 | 90 | 81
2017-04-05 17:30 | 62 | 62 |  |  | 42830.7292 | 91 | 82
2017-04-05 18:00 | 62 | 61 |  |  | 42830.75 | 91 | 81
2017-04-05 18:30 | 60 | 59 |  |  | 42830.7708 | 88 | 77
2017-04-05 19:00 | 60 | 59 |  |  | 42830.7917 | 89 | 78
2017-04-05 19:30 | 57 | 57 |  |  | 42830.8125 | 84 | 76
2017-04-05 20:00 | 55 | 55 |  |  | 42830.8333 | 81 | 72
2017-04-05 20:30 | 52 | 52 |  |  | 42830.8542 | 78 | 69
2017-04-05 21:00 | 49 | 49 |  |  | 42830.875 | 75 | 65
2017-04-05 21:30 | 48 | 48 |  |  | 42830.8958 | 75 | 63
2017-04-05 22:00 | 47 | 47 |  |  | 42830.9167 | 73 | 65
2017-04-05 22:30 | 47 | 47 |  |  | 42830.9375 | 70 | 65
2017-04-05 23:00 | 46 | 46 |  |  | 42830.9583 | 67 | 63
2017-04-05 23:30 | 43 | 43 |  |  | 42830.9792 | 66 | 61
2017-04-06 | 41 | 41 |  |  | 42831 | 62 | 57
2017-04-06 00:30 | 37 | 37 |  |  | 42831.0208 | 57 | 52
2017-04-06 01:00 | 35 | 35 |  |  | 42831.0417 | 54 | 48
2017-04-06 01:30 | 34 | 34 |  |  | 42831.0625 | 51 | 47
2017-04-06 02:00 | 34 | 34 |  |  | 42831.0833 | 50 | 46
2017-04-06 02:30 | 31 | 31 |  |  | 42831.1042 | 46 | 42
2017-04-06 03:00 | 29 | 29 |  |  | 42831.125 | 43 | 39
2017-04-06 03:30 | 27 | 27 |  |  | 42831.1458 | 42 | 39
2017-04-06 04:00 | 28 | 28 |  |  | 42831.1667 | 43 | 39
2017-04-06 04:30 | 30 | 30 |  |  | 42831.1875 | 45 | 41
2017-04-06 05:00 | 30 | 30 |  |  | 42831.2083 | 45 | 42
2017-04-06 05:30 | 32 | 32 |  |  | 42831.2292 | 47 | 45
2017-04-06 06:00 | 36 | 36 |  |  | 42831.25 | 52 | 50
2017-04-06 06:30 | 42 | 42 |  |  | 42831.2708 | 62 | 60
2017-04-06 07:00 | 45 | 45 |  |  | 42831.2917 | 67 | 64
2017-04-06 07:30 | 48 | 48 |  |  | 42831.3125 | 74 | 70
2017-04-06 08:00 | 51 | 51 |  |  | 42831.3333 | 77 | 73
2017-04-06 08:30 | 53 | 53 |  |  | 42831.3542 | 79 | 76
2017-04-06 09:00 | 51 | 51 |  |  | 42831.375 | 77 | 74
2017-04-06 09:30 | 58 | 58 |  |  | 42831.3958 | 82 | 80
2017-04-06 10:00 | 57 | 57 |  |  | 42831.4167 | 83 | 81
2017-04-06 10:30 | 56 | 56 |  |  | 42831.4375 | 81 | 78
2017-04-06 11:00 | 59 | 59 |  |  | 42831.4583 | 86 | 83
2017-04-06 11:30 | 59 | 59 |  |  | 42831.4792 | 83 | 80
2017-04-06 12:00 | 53 | 53 |  |  | 42831.5 | 80 | 76
2017-04-06 12:30 | 54 | 54 |  |  | 42831.5208 | 82 | 78
2017-04-06 13:00 | 57 | 57 |  |  | 42831.5417 | 83 | 79
2017-04-06 13:30 | 57 | 57 |  |  | 42831.5625 | 82 | 79
2017-04-06 14:00 | 57 | 57 |  |  | 42831.5833 | 83 | 79
2017-04-06 14:30 | 61 | 61 |  |  | 42831.6042 | 92 | 89
2017-04-06 15:00 | 60 | 60 |  |  | 42831.625 | 86 | 83
2017-04-06 15:30 | 62 | 62 |  |  | 42831.6458 | 94 | 90
2017-04-06 16:00 | 71 | 71 |  |  | 42831.6667 | 111 | 107
2017-04-06 16:30 | 57 | 57 |  |  | 42831.6875 | 83 | 79
2017-04-06 17:00 | 58 | 58 |  |  | 42831.7083 | 84 | 80
2017-04-06 17:30 | 59 | 59 |  |  | 42831.7292 | 84 | 80
2017-04-06 18:00 | 60 | 60 |  |  | 42831.75 | 85 | 81
2017-04-06 18:30 | 61 | 61 |  |  | 42831.7708 | 86 | 81
2017-04-06 19:00 | 62 | 62 |  |  | 42831.7917 | 88 | 82
2017-04-06 19:30 | 59 | 59 |  |  | 42831.8125 | 84 | 77
2017-04-06 20:00 | 57 | 57 |  |  | 42831.8333 | 80 | 74
2017-04-06 20:30 | 55 | 55 |  |  | 42831.8542 | 77 | 72
2017-04-06 21:00 | 52 | 51 |  |  | 42831.875 | 70 | 68
2017-04-06 21:30 | 49 | 49 |  |  | 42831.8958 | 66 | 63
2017-04-06 22:00 | 47 | 47 |  |  | 42831.9167 | 65 | 62
2017-04-06 22:30 | 45 | 45 |  |  | 42831.9375 | 65 | 61
2017-04-06 23:00 | 43 | 43 |  |  | 42831.9583 | 62 | 58
2017-04-06 23:30 | 39 | 39 |  |  | 42831.9792 | 58 | 54
2017-04-07 | 35 | 35 |  |  | 42832 | 53 | 48
2017-04-07 00:30 | 31 | 31 |  |  | 42832.0208 | 48 | 43
2017-04-07 01:00 | 28 | 28 |  |  | 42832.0417 | 45 | 38
2017-04-07 01:30 | 28 | 28 |  |  | 42832.0625 | 45 | 39
2017-04-07 02:00 | 29 | 28 |  |  | 42832.0833 | 46 | 40
2017-04-07 02:30 | 29 | 29 |  |  | 42832.1042 | 47 | 40
2017-04-07 03:00 | 28 | 27 |  |  | 42832.125 | 45 | 38
2017-04-07 03:30 | 28 | 28 |  |  | 42832.1458 | 44 | 39
2017-04-07 04:00 | 30 | 30 |  |  | 42832.1667 | 44 | 41
2017-04-07 04:30 | 31 | 31 |  |  | 42832.1875 | 45 | 41
2017-04-07 05:00 | 34 | 34 |  |  | 42832.2083 | 48 | 45
2017-04-07 05:30 | 35 | 35 |  |  | 42832.2292 | 49 | 47
2017-04-07 06:00 | 41 | 40 |  |  | 42832.25 | 55 | 53
2017-04-07 06:30 | 47 | 46 |  |  | 42832.2708 | 63 | 62
2017-04-07 07:00 | 50 | 49 |  |  | 42832.2917 | 69 | 69
2017-04-07 07:30 | 51 | 50 |  |  | 42832.3125 | 72 | 72
2017-04-07 08:00 | 54 | 53 |  |  | 42832.3333 | 76 | 75
2017-04-07 08:30 | 54 | 54 |  |  | 42832.3542 | 82 | 79
2017-04-07 09:00 | 56 | 56 |  |  | 42832.375 | 82 | 79
2017-04-07 09:30 | 58 | 58 |  |  | 42832.3958 | 84 | 81
2017-04-07 10:00 | 59 | 59 |  |  | 42832.4167 | 86 | 83
2017-04-07 10:30 | 61 | 61 |  |  | 42832.4375 | 89 | 87
2017-04-07 11:00 | 60 | 60 |  |  | 42832.4583 | 88 | 84
2017-04-07 11:30 | 58 | 58 |  |  | 42832.4792 | 83 | 79
2017-04-07 12:00 | 59 | 59 |  |  | 42832.5 | 79 | 75
2017-04-07 12:30 | 67 | 66 |  |  | 42832.5208 | 73 | 68
2017-04-07 13:00 | 54 | 54 |  |  | 42832.5417 | 81 | 76
2017-04-07 13:30 | 56 | 56 |  |  | 42832.5625 | 83 | 77
2017-04-07 14:00 | 54 | 54 |  |  | 42832.5833 | 82 | 76
2017-04-07 14:30 | 53 | 53 |  |  | 42832.6042 | 80 | 73
2017-04-07 15:00 | 54 | 54 |  |  | 42832.625 | 82 | 76
2017-04-07 15:30 | 55 | 55 |  |  | 42832.6458 | 87 | 81
2017-04-07 16:00 | 58 | 58 |  |  | 42832.6667 | 88 | 82
2017-04-07 16:30 | 60 | 59 |  |  | 42832.6875 | 88 | 82
2017-04-07 17:00 | 59 | 59 |  |  | 42832.7083 | 90 | 83
2017-04-07 17:30 | 59 | 59 |  |  | 42832.7292 | 88 | 82
2017-04-07 18:00 | 57 | 56 |  |  | 42832.75 | 85 | 80
2017-04-07 18:30 | 56 | 56 |  |  | 42832.7708 | 84 | 79
2017-04-07 19:00 | 57 | 57 |  |  | 42832.7917 | 82 | 79
2017-04-07 19:30 | 56 | 55 |  |  | 42832.8125 | 77 | 76
2017-04-07 20:00 | 55 | 55 |  |  | 42832.8333 | 75 | 74
2017-04-07 20:30 | 53 | 53 |  |  | 42832.8542 | 73 | 72
2017-04-07 21:00 | 51 | 51 |  |  | 42832.875 | 70 | 69
2017-04-07 21:30 | 48 | 48 |  |  | 42832.8958 | 66 | 65
2017-04-07 22:00 | 47 | 47 |  |  | 42832.9167 | 66 | 65
2017-04-07 22:30 | 48 | 47 |  |  | 42832.9375 | 67 | 67
2017-04-07 23:00 | 47 | 47 |  |  | 42832.9583 | 65 | 64
2017-04-07 23:30 | 43 | 42 |  |  | 42832.9792 | 61 | 60
2017-04-08 | 39 | 39 |  |  | 42833 | 57 | 57
2017-04-08 00:30 | 36 | 36 |  |  | 42833.0208 | 53 | 52
2017-04-08 01:00 | 35 | 34 |  |  | 42833.0417 | 50 | 49
2017-04-08 01:30 | 33 | 33 |  |  | 42833.0625 | 48 | 47
2017-04-08 02:00 | 31 | 31 |  |  | 42833.0833 | 47 | 45
2017-04-08 02:30 | 30 | 30 |  |  | 42833.1042 | 46 | 45
2017-04-08 03:00 | 30 | 30 |  |  | 42833.125 | 45 | 44
2017-04-08 03:30 | 31 | 31 |  |  | 42833.1458 | 45 | 43
2017-04-08 04:00 | 31 | 31 |  |  | 42833.1667 | 45 | 44
2017-04-08 04:30 | 33 | 33 |  |  | 42833.1875 | 46 | 45
2017-04-08 05:00 | 35 | 35 |  |  | 42833.2083 | 48 | 47
2017-04-08 05:30 | 35 | 35 |  |  | 42833.2292 | 50 | 49
2017-04-08 06:00 | 37 | 37 |  |  | 42833.25 | 51 | 50
2017-04-08 06:30 | 39 | 39 |  |  | 42833.2708 | 56 | 55
2017-04-08 07:00 | 42 | 42 |  |  | 42833.2917 | 60 | 59
2017-04-08 07:30 | 42 | 42 |  |  | 42833.3125 | 60 | 59
2017-04-08 08:00 | 42 | 42 |  |  | 42833.3333 | 61 | 61
2017-04-08 08:30 | 43 | 42 |  |  | 42833.3542 | 61 | 61
2017-04-08 09:00 | 44 | 43 |  |  | 42833.375 | 63 | 62
2017-04-08 09:30 | 45 | 44 |  |  | 42833.3958 | 64 | 64
2017-04-08 10:00 | 48 | 47 |  |  | 42833.4167 | 69 | 69
2017-04-08 10:30 | 52 | 51 |  |  | 42833.4375 | 72 | 72
2017-04-08 11:00 | 47 | 46 |  |  | 42833.4583 | 67 | 67
2017-04-08 11:30 | 48 | 47 |  |  | 42833.4792 | 66 | 66
2017-04-08 12:00 | 51 | 49 |  |  | 42833.5 | 70 | 70
2017-04-08 12:30 | 52 | 50 |  |  | 42833.5208 | 69 | 69
2017-04-08 13:00 | 52 | 51 |  |  | 42833.5417 | 68 | 68
2017-04-08 13:30 | 50 | 48 |  |  | 42833.5625 | 67 | 67
2017-04-08 14:00 | 50 | 49 |  |  | 42833.5833 | 67 | 67
2017-04-08 14:30 | 48 | 47 |  |  | 42833.6042 | 64 | 63
2017-04-08 15:00 | 48 | 48 |  |  | 42833.625 | 65 | 65
2017-04-08 15:30 | 51 | 51 |  |  | 42833.6458 | 69 | 69
2017-04-08 16:00 | 52 | 51 |  |  | 42833.6667 | 70 | 70
2017-04-08 16:30 | 52 | 51 |  |  | 42833.6875 | 70 | 70
2017-04-08 17:00 | 53 | 53 |  |  | 42833.7083 | 73 | 72
2017-04-08 17:30 | 52 | 52 |  |  | 42833.7292 | 72 | 72
2017-04-08 18:00 | 53 | 53 |  |  | 42833.75 | 74 | 73
2017-04-08 18:30 | 54 | 54 |  |  | 42833.7708 | 76 | 75
2017-04-08 19:00 | 57 | 57 |  |  | 42833.7917 | 77 | 76
2017-04-08 19:30 | 54 | 54 |  |  | 42833.8125 | 75 | 74
2017-04-08 20:00 | 53 | 53 |  |  | 42833.8333 | 76 | 75
2017-04-08 20:30 | 53 | 53 |  |  | 42833.8542 | 77 | 77
2017-04-08 21:00 | 51 | 50 |  |  | 42833.875 | 74 | 73
2017-04-08 21:30 | 49 | 49 |  |  | 42833.8958 | 71 | 70
2017-04-08 22:00 | 49 | 48 |  |  | 42833.9167 | 70 | 69
2017-04-08 22:30 | 50 | 50 |  |  | 42833.9375 | 73 | 71
2017-04-08 23:00 | 53 | 53 |  |  | 42833.9583 | 75 | 73
2017-04-08 23:30 | 48 | 48 |  |  | 42833.9792 | 68 | 66
2017-04-09 | 44 | 44 |  |  | 42834 | 62 | 60
2017-04-09 00:30 | 39 | 39 |  |  | 42834.0208 | 58 | 55
2017-04-09 01:00 | 36 | 36 |  |  | 42834.0417 | 53 | 51
2017-04-09 01:30 | 34 | 34 |  |  | 42834.0625 | 51 | 48
2017-04-09 02:00 | 33 | 33 |  |  | 42834.0833 | 50 | 47
2017-04-09 02:30 | 33 | 33 |  |  | 42834.1042 | 49 | 46
2017-04-09 03:00 | 31 | 31 |  |  | 42834.125 | 48 | 45
2017-04-09 03:30 | 30 | 30 |  |  | 42834.1458 | 47 | 44
2017-04-09 04:00 | 30 | 30 |  |  | 42834.1667 | 45 | 42
2017-04-09 04:30 | 30 | 30 |  |  | 42834.1875 | 46 | 43
2017-04-09 05:00 | 32 | 32 |  |  | 42834.2083 | 47 | 44
2017-04-09 05:30 | 31 | 31 |  |  | 42834.2292 | 48 | 45
2017-04-09 06:00 | 31 | 31 |  |  | 42834.25 | 49 | 46
2017-04-09 06:30 | 32 | 32 |  |  | 42834.2708 | 50 | 47
2017-04-09 07:00 | 34 | 34 |  |  | 42834.2917 | 51 | 49
2017-04-09 07:30 | 34 | 34 |  |  | 42834.3125 | 52 | 49
2017-04-09 08:00 | 33 | 32 |  |  | 42834.3333 | 52 | 49
2017-04-09 08:30 | 33 | 33 |  |  | 42834.3542 | 53 | 51
2017-04-09 09:00 | 34 | 34 |  |  | 42834.375 | 54 | 53
2017-04-09 09:30 | 37 | 37 |  |  | 42834.3958 | 56 | 55
2017-04-09 10:00 | 38 | 38 |  |  | 42834.4167 | 58 | 57
2017-04-09 10:30 | 42 | 42 |  |  | 42834.4375 | 60 | 59
2017-04-09 11:00 | 46 | 46 |  |  | 42834.4583 | 64 | 63
2017-04-09 11:30 | 46 | 46 |  |  | 42834.4792 | 64 | 63
2017-04-09 12:00 | 45 | 45 |  |  | 42834.5 | 62 | 61
2017-04-09 12:30 | 45 | 44 |  |  | 42834.5208 | 64 | 63
2017-04-09 13:00 | 46 | 45 |  |  | 42834.5417 | 64 | 63
2017-04-09 13:30 | 47 | 47 |  |  | 42834.5625 | 63 | 62
2017-04-09 14:00 | 47 | 47 |  |  | 42834.5833 | 64 | 63
2017-04-09 14:30 | 51 | 51 |  |  | 42834.6042 | 70 | 69
2017-04-09 15:00 | 52 | 52 |  |  | 42834.625 | 69 | 68
2017-04-09 15:30 | 52 | 52 |  |  | 42834.6458 | 67 | 66
2017-04-09 16:00 | 54 | 54 |  |  | 42834.6667 | 71 | 70
2017-04-09 16:30 | 55 | 55 |  |  | 42834.6875 | 73 | 72
2017-04-09 17:00 | 55 | 55 |  |  | 42834.7083 | 74 | 74
2017-04-09 17:30 | 54 | 54 |  |  | 42834.7292 | 74 | 74
2017-04-09 18:00 | 56 | 56 |  |  | 42834.75 | 77 | 76
2017-04-09 18:30 | 59 | 58 |  |  | 42834.7708 | 80 | 79
2017-04-09 19:00 | 59 | 59 |  |  | 42834.7917 | 82 | 81
2017-04-09 19:30 | 58 | 57 |  |  | 42834.8125 | 79 | 78
2017-04-09 20:00 | 56 | 56 |  |  | 42834.8333 | 78 | 77
2017-04-09 20:30 | 55 | 55 |  |  | 42834.8542 | 77 | 76
2017-04-09 21:00 | 51 | 51 |  |  | 42834.875 | 72 | 71
2017-04-09 21:30 | 48 | 48 |  |  | 42834.8958 | 68 | 67
2017-04-09 22:00 | 46 | 46 |  |  | 42834.9167 | 67 | 66
2017-04-09 22:30 | 47 | 47 |  |  | 42834.9375 | 70 | 69
2017-04-09 23:00 | 50 | 50 |  |  | 42834.9583 | 71 | 70
2017-04-09 23:30 | 46 | 46 |  |  | 42834.9792 | 68 | 66
2017-04-10 | 42 | 42 |  |  | 42835 | 62 | 60
2017-04-10 00:30 | 39 | 39 |  |  | 42835.0208 | 57 | 55
2017-04-10 01:00 | 37 | 37 |  |  | 42835.0417 | 55 | 53
2017-04-10 01:30 | 35 | 35 |  |  | 42835.0625 | 53 | 50
2017-04-10 02:00 | 33 | 33 |  |  | 42835.0833 | 52 | 49
2017-04-10 02:30 | 33 | 33 |  |  | 42835.1042 | 52 | 49
2017-04-10 03:00 | 33 | 33 |  |  | 42835.125 | 50 | 47
2017-04-10 03:30 | 33 | 33 |  |  | 42835.1458 | 50 | 46
2017-04-10 04:00 | 34 | 34 |  |  | 42835.1667 | 50 | 47
2017-04-10 04:30 | 36 | 36 |  |  | 42835.1875 | 51 | 49
2017-04-10 05:00 | 36 | 36 |  |  | 42835.2083 | 52 | 50
2017-04-10 05:30 | 40 | 40 |  |  | 42835.2292 | 57 | 55
2017-04-10 06:00 | 44 | 44 |  |  | 42835.25 | 62 | 61
2017-04-10 06:30 | 50 | 50 |  |  | 42835.2708 | 72 | 71
2017-04-10 07:00 | 54 | 54 |  |  | 42835.2917 | 78 | 76
2017-04-10 07:30 | 57 | 57 |  |  | 42835.3125 | 85 | 83
2017-04-10 08:00 | 60 | 59 |  |  | 42835.3333 | 85 | 85
2017-04-10 08:30 | 59 | 58 |  |  | 42835.3542 | 85 | 84
2017-04-10 09:00 | 60 | 59 |  |  | 42835.375 | 86 | 85
2017-04-10 09:30 | 60 | 59 |  |  | 42835.3958 | 87 | 87
2017-04-10 10:00 | 61 | 59 |  |  | 42835.4167 | 88 | 88
2017-04-10 10:30 | 62 | 60 |  |  | 42835.4375 | 87 | 87
2017-04-10 11:00 | 63 | 61 |  |  | 42835.4583 | 89 | 88
2017-04-10 11:30 | 65 | 63 |  |  | 42835.4792 | 88 | 88
2017-04-10 12:00 | 65 | 63 |  |  | 42835.5 | 91 | 91
2017-04-10 12:30 | 65 | 63 |  |  | 42835.5208 | 90 | 89
2017-04-10 13:00 | 63 | 61 |  |  | 42835.5417 | 88 | 88
2017-04-10 13:30 | 64 | 62 |  |  | 42835.5625 | 87 | 87
2017-04-10 14:00 | 63 | 61 |  |  | 42835.5833 | 89 | 89
2017-04-10 14:30 | 63 | 63 |  |  | 42835.6042 | 97 | 92
2017-04-10 15:00 | 66 | 66 |  |  | 42835.625 | 103 | 95
2017-04-10 15:30 | 68 | 68 |  |  | 42835.6458 | 107 | 98
2017-04-10 16:00 | 70 | 70 |  |  | 42835.6667 | 108 | 100
2017-04-10 16:30 | 71 | 71 |  |  | 42835.6875 | 110 | 101
2017-04-10 17:00 | 70 | 70 |  |  | 42835.7083 | 109 | 99
2017-04-10 17:30 | 69 | 69 |  |  | 42835.7292 | 106 | 95
2017-04-10 18:00 | 68 | 68 |  |  | 42835.75 | 104 | 93
2017-04-10 18:30 | 67 | 67 |  |  | 42835.7708 | 102 | 90
2017-04-10 19:00 | 68 | 67 |  |  | 42835.7917 | 107 | 89
2017-04-10 19:30 | 65 | 65 |  |  | 42835.8125 | 104 | 86
2017-04-10 20:00 | 61 | 61 |  |  | 42835.8333 | 98 | 84
2017-04-10 20:30 | 59 | 58 |  |  | 42835.8542 | 95 | 82
2017-04-10 21:00 | 58 | 55 |  |  | 42835.875 | 80 | 74
2017-04-10 21:30 | 55 | 51 |  |  | 42835.8958 | 72 | 68
2017-04-10 22:00 | 52 | 49 |  |  | 42835.9167 | 70 | 66
2017-04-10 22:30 | 53 | 49 |  |  | 42835.9375 | 71 | 67
2017-04-10 23:00 | 53 | 51 |  |  | 42835.9583 | 73 | 68
2017-04-10 23:30 | 50 | 47 |  |  | 42835.9792 | 69 | 64
2017-04-11 | 46 | 42 |  |  | 42836 | 64 | 58
2017-04-11 00:30 | 39 | 37 |  |  | 42836.0208 | 58 | 52
2017-04-11 01:00 | 36 | 34 |  |  | 42836.0417 | 54 | 47
2017-04-11 01:30 | 34 | 32 |  |  | 42836.0625 | 53 | 45
2017-04-11 02:00 | 33 | 30 |  |  | 42836.0833 | 50 | 42
2017-04-11 02:30 | 30 | 28 |  |  | 42836.1042 | 49 | 41
2017-04-11 03:00 | 30 | 26 |  |  | 42836.125 | 48 | 40
2017-04-11 03:30 | 31 | 27 |  |  | 42836.1458 | 48 | 39
2017-04-11 04:00 | 30 | 26 |  |  | 42836.1667 | 48 | 39
2017-04-11 04:30 | 30 | 27 |  |  | 42836.1875 | 49 | 40
2017-04-11 05:00 | 33 | 31 |  |  | 42836.2083 | 53 | 45
2017-04-11 05:30 | 40 | 37 |  |  | 42836.2292 | 59 | 53
2017-04-11 06:00 | 45 | 42 |  |  | 42836.25 | 62 | 57
2017-04-11 06:30 | 50 | 46 |  |  | 42836.2708 | 69 | 65
2017-04-11 07:00 | 54 | 49 |  |  | 42836.2917 | 72 | 70
2017-04-11 07:30 | 58 | 52 |  |  | 42836.3125 | 76 | 75
2017-04-11 08:00 | 61 | 54 |  |  | 42836.3333 | 79 | 78
2017-04-11 08:30 | 60 | 55 |  |  | 42836.3542 | 82 | 80
2017-04-11 09:00 | 59 | 54 |  |  | 42836.375 | 82 | 79
2017-04-11 09:30 | 55 | 50 |  |  | 42836.3958 | 79 | 77
2017-04-11 10:00 | 54 | 50 |  |  | 42836.4167 | 80 | 77
2017-04-11 10:30 | 56 | 50 |  |  | 42836.4375 | 77 | 76
2017-04-11 11:00 | 57 | 51 |  |  | 42836.4583 | 79 | 78
2017-04-11 11:30 | 58 | 52 |  |  | 42836.4792 | 80 | 79
2017-04-11 12:00 | 58 | 52 |  |  | 42836.5 | 79 | 77
2017-04-11 12:30 | 57 | 52 |  |  | 42836.5208 | 80 | 78
2017-04-11 13:00 | 56 | 51 |  |  | 42836.5417 | 81 | 78
2017-04-11 13:30 | 57 | 53 |  |  | 42836.5625 | 84 | 81
2017-04-11 14:00 | 59 | 55 |  |  | 42836.5833 | 86 | 82
2017-04-11 14:30 | 60 | 57 |  |  | 42836.6042 | 88 | 84
2017-04-11 15:00 | 66 | 64 |  |  | 42836.625 | 93 | 89
2017-04-11 15:30 | 69 | 67 |  |  | 42836.6458 | 96 | 92
2017-04-11 16:00 | 70 | 69 |  |  | 42836.6667 | 99 | 94
2017-04-11 16:30 | 72 | 71 |  |  | 42836.6875 | 101 | 95
2017-04-11 17:00 | 74 | 72 |  |  | 42836.7083 | 103 | 98
2017-04-11 17:30 | 75 | 73 |  |  | 42836.7292 | 103 | 97
2017-04-11 18:00 | 75 | 73 |  |  | 42836.75 | 103 | 96
2017-04-11 18:30 | 74 | 72 |  |  | 42836.7708 | 100 | 93
2017-04-11 19:00 | 74 | 73 |  |  | 42836.7917 | 100 | 93
2017-04-11 19:30 | 71 | 70 |  |  | 42836.8125 | 97 | 89
2017-04-11 20:00 | 66 | 65 |  |  | 42836.8333 | 93 | 85
2017-04-11 20:30 | 64 | 63 |  |  | 42836.8542 | 92 | 83
2017-04-11 21:00 | 61 | 60 |  |  | 42836.875 | 86 | 78
2017-04-11 21:30 | 58 | 56 |  |  | 42836.8958 | 80 | 73
2017-04-11 22:00 | 56 | 54 |  |  | 42836.9167 | 80 | 73
2017-04-11 22:30 | 58 | 57 |  |  | 42836.9375 | 82 | 75
2017-04-11 23:00 | 59 | 58 |  |  | 42836.9583 | 81 | 74
2017-04-11 23:30 | 54 | 53 |  |  | 42836.9792 | 76 | 69
2017-04-12 | 49 | 48 |  |  | 42837 | 70 | 63
2017-04-12 00:30 | 45 | 44 |  |  | 42837.0208 | 67 | 59
2017-04-12 01:00 | 44 | 43 |  |  | 42837.0417 | 66 | 57
2017-04-12 01:30 | 42 | 41 |  |  | 42837.0625 | 64 | 54
2017-04-12 02:00 | 40 | 39 |  |  | 42837.0833 | 62 | 52
2017-04-12 02:30 | 39 | 38 |  |  | 42837.1042 | 62 | 51
2017-04-12 03:00 | 37 | 36 |  |  | 42837.125 | 59 | 49
2017-04-12 03:30 | 37 | 36 |  |  | 42837.1458 | 59 | 48
2017-04-12 04:00 | 37 | 36 |  |  | 42837.1667 | 58 | 47
2017-04-12 04:30 | 38 | 37 |  |  | 42837.1875 | 60 | 49
2017-04-12 05:00 | 39 | 38 |  |  | 42837.2083 | 61 | 50
2017-04-12 05:30 | 43 | 42 |  |  | 42837.2292 | 65 | 55
2017-04-12 06:00 | 48 | 46 |  |  | 42837.25 | 70 | 62
2017-04-12 06:30 | 55 | 54 |  |  | 42837.2708 | 78 | 71
2017-04-12 07:00 | 58 | 57 |  |  | 42837.2917 | 82 | 76
2017-04-12 07:30 | 60 | 58 |  |  | 42837.3125 | 88 | 81
2017-04-12 08:00 | 60 | 58 |  |  | 42837.3333 | 87 | 81
2017-04-12 08:30 | 60 | 58 |  |  | 42837.3542 | 87 | 82
2017-04-12 09:00 | 62 | 61 |  |  | 42837.375 | 93 | 88
2017-04-12 09:30 | 61 | 59 |  |  | 42837.3958 | 87 | 83
2017-04-12 10:00 | 61 | 59 |  |  | 42837.4167 | 86 | 82
2017-04-12 10:30 | 62 | 60 |  |  | 42837.4375 | 88 | 85
2017-04-12 11:00 | 61 | 60 |  |  | 42837.4583 | 86 | 84
2017-04-12 11:30 | 60 | 60 |  |  | 42837.4792 | 84 | 83
2017-04-12 12:00 | 61 | 61 |  |  | 42837.5 | 84 | 83
2017-04-12 12:30 | 61 | 61 |  |  | 42837.5208 | 85 | 84
2017-04-12 13:00 | 62 | 62 |  |  | 42837.5417 | 87 | 86
2017-04-12 13:30 | 64 | 63 |  |  | 42837.5625 | 89 | 88
2017-04-12 14:00 | 66 | 66 |  |  | 42837.5833 | 92 | 91
2017-04-12 14:30 | 68 | 68 |  |  | 42837.6042 | 93 | 92
2017-04-12 15:00 | 69 | 68 |  |  | 42837.625 | 94 | 93
2017-04-12 15:30 | 69 | 69 |  |  | 42837.6458 | 97 | 96
2017-04-12 16:00 | 70 | 70 |  |  | 42837.6667 | 97 | 95
2017-04-12 16:30 | 71 | 71 |  |  | 42837.6875 | 99 | 98
2017-04-12 17:00 | 72 | 72 |  |  | 42837.7083 | 100 | 99
2017-04-12 17:30 | 71 | 71 |  |  | 42837.7292 | 97 | 95
2017-04-12 18:00 | 70 | 70 |  |  | 42837.75 | 95 | 93
2017-04-12 18:30 | 70 | 70 |  |  | 42837.7708 | 96 | 92
2017-04-12 19:00 | 70 | 70 |  |  | 42837.7917 | 96 | 91
2017-04-12 19:30 | 66 | 66 |  |  | 42837.8125 | 92 | 88
2017-04-12 20:00 | 64 | 64 |  |  | 42837.8333 | 90 | 85
2017-04-12 20:30 | 63 | 63 |  |  | 42837.8542 | 90 | 84
2017-04-12 21:00 | 58 | 58 |  |  | 42837.875 | 81 | 77
2017-04-12 21:30 | 54 | 54 |  |  | 42837.8958 | 75 | 72
2017-04-12 22:00 | 53 | 53 |  |  | 42837.9167 | 74 | 71
2017-04-12 22:30 | 56 | 56 |  |  | 42837.9375 | 77 | 74
2017-04-12 23:00 | 58 | 58 |  |  | 42837.9583 | 78 | 74
2017-04-12 23:30 | 52 | 51 |  |  | 42837.9792 | 73 | 68
2017-04-13 | 47 | 47 |  |  | 42838 | 67 | 63
2017-04-13 00:30 | 42 | 41 |  |  | 42838.0208 | 62 | 57
2017-04-13 01:00 | 38 | 37 |  |  | 42838.0417 | 58 | 52
2017-04-13 01:30 | 37 | 36 |  |  | 42838.0625 | 56 | 49
2017-04-13 02:00 | 34 | 34 |  |  | 42838.0833 | 53 | 47
2017-04-13 02:30 | 33 | 33 |  |  | 42838.1042 | 53 | 46
2017-04-13 03:00 | 33 | 33 |  |  | 42838.125 | 51 | 47
2017-04-13 03:30 | 34 | 33 |  |  | 42838.1458 | 51 | 46
2017-04-13 04:00 | 34 | 33 |  |  | 42838.1667 | 51 | 46
2017-04-13 04:30 | 36 | 36 |  |  | 42838.1875 | 53 | 48
2017-04-13 05:00 | 38 | 38 |  |  | 42838.2083 | 55 | 51
2017-04-13 05:30 | 42 | 42 |  |  | 42838.2292 | 59 | 55
2017-04-13 06:00 | 47 | 47 |  |  | 42838.25 | 65 | 62
2017-04-13 06:30 | 53 | 53 |  |  | 42838.2708 | 72 | 70
2017-04-13 07:00 | 57 | 57 |  |  | 42838.2917 | 79 | 77
2017-04-13 07:30 | 59 | 59 |  |  | 42838.3125 | 82 | 82
2017-04-13 08:00 | 59 | 59 |  |  | 42838.3333 | 84 | 83
2017-04-13 08:30 | 60 | 60 |  |  | 42838.3542 | 87 | 84
2017-04-13 09:00 | 59 | 59 |  |  | 42838.375 | 86 | 84
2017-04-13 09:30 | 60 | 60 |  |  | 42838.3958 | 87 | 85
2017-04-13 10:00 | 61 | 61 |  |  | 42838.4167 | 87 | 86
2017-04-13 10:30 | 61 | 61 |  |  | 42838.4375 | 87 | 86
2017-04-13 11:00 | 61 | 61 |  |  | 42838.4583 | 88 | 87
2017-04-13 11:30 | 60 | 60 |  |  | 42838.4792 | 88 | 86
2017-04-13 12:00 | 59 | 59 |  |  | 42838.5 | 87 | 86
2017-04-13 12:30 | 57 | 57 |  |  | 42838.5208 | 88 | 84
2017-04-13 13:00 | 59 | 58 |  |  | 42838.5417 | 89 | 85
2017-04-13 13:30 | 59 | 59 |  |  | 42838.5625 | 89 | 86
2017-04-13 14:00 | 59 | 59 |  |  | 42838.5833 | 89 | 85
2017-04-13 14:30 | 59 | 59 |  |  | 42838.6042 | 86 | 81
2017-04-13 15:00 | 58 | 58 |  |  | 42838.625 | 86 | 82
2017-04-13 15:30 | 60 | 60 |  |  | 42838.6458 | 89 | 85
2017-04-13 16:00 | 62 | 62 |  |  | 42838.6667 | 91 | 86
2017-04-13 16:30 | 63 | 63 |  |  | 42838.6875 | 93 | 87
2017-04-13 17:00 | 63 | 63 |  |  | 42838.7083 | 92 | 86
2017-04-13 17:30 | 60 | 60 |  |  | 42838.7292 | 89 | 82
2017-04-13 18:00 | 61 | 61 |  |  | 42838.75 | 88 | 82
2017-04-13 18:30 | 62 | 61 |  |  | 42838.7708 | 88 | 81
2017-04-13 19:00 | 62 | 61 |  |  | 42838.7917 | 89 | 81
2017-04-13 19:30 | 58 | 58 |  |  | 42838.8125 | 88 | 76
2017-04-13 20:00 | 55 | 55 |  |  | 42838.8333 | 86 | 72
2017-04-13 20:30 | 57 | 54 |  |  | 42838.8542 | 77 | 71
2017-04-13 21:00 | 55 | 52 |  |  | 42838.875 | 71 | 65
2017-04-13 21:30 | 50 | 47 |  |  | 42838.8958 | 66 | 60
2017-04-13 22:00 | 47 | 44 |  |  | 42838.9167 | 66 | 59
2017-04-13 22:30 | 48 | 46 |  |  | 42838.9375 | 69 | 62
2017-04-13 23:00 | 48 | 47 |  |  | 42838.9583 | 69 | 61
2017-04-13 23:30 | 45 | 44 |  |  | 42838.9792 | 66 | 58
2017-04-14 | 42 | 40 |  |  | 42839 | 61 | 55
2017-04-14 00:30 | 38 | 37 |  |  | 42839.0208 | 58 | 50
2017-04-14 01:00 | 39 | 37 |  |  | 42839.0417 | 57 | 49
2017-04-14 01:30 | 36 | 34 |  |  | 42839.0625 | 55 | 46
2017-04-14 02:00 | 35 | 33 |  |  | 42839.0833 | 53 | 44
2017-04-14 02:30 | 32 | 30 |  |  | 42839.1042 | 51 | 41
2017-04-14 03:00 | 30 | 28 |  |  | 42839.125 | 50 | 40
2017-04-14 03:30 | 29 | 28 |  |  | 42839.1458 | 50 | 39
2017-04-14 04:00 | 30 | 28 |  |  | 42839.1667 | 51 | 39
2017-04-14 04:30 | 31 | 29 |  |  | 42839.1875 | 51 | 40
2017-04-14 05:00 | 32 | 30 |  |  | 42839.2083 | 51 | 40
2017-04-14 05:30 | 32 | 30 |  |  | 42839.2292 | 52 | 41
2017-04-14 06:00 | 31 | 30 |  |  | 42839.25 | 53 | 42
2017-04-14 06:30 | 30 | 28 |  |  | 42839.2708 | 54 | 43
2017-04-14 07:00 | 30 | 28 |  |  | 42839.2917 | 54 | 44
2017-04-14 07:30 | 30 | 28 |  |  | 42839.3125 | 54 | 45
2017-04-14 08:00 | 30 | 28 |  |  | 42839.3333 | 53 | 45
2017-04-14 08:30 | 33 | 31 |  |  | 42839.3542 | 54 | 47
2017-04-14 09:00 | 33 | 31 |  |  | 42839.375 | 55 | 49
2017-04-14 09:30 | 33 | 31 |  |  | 42839.3958 | 53 | 47
2017-04-14 10:00 | 37 | 34 |  |  | 42839.4167 | 54 | 47
2017-04-14 10:30 | 38 | 35 |  |  | 42839.4375 | 55 | 50
2017-04-14 11:00 | 39 | 37 |  |  | 42839.4583 | 56 | 51
2017-04-14 11:30 | 37 | 34 |  |  | 42839.4792 | 53 | 48
2017-04-14 12:00 | 34 | 31 |  |  | 42839.5 | 55 | 48
2017-04-14 12:30 | 35 | 33 |  |  | 42839.5208 | 54 | 48
2017-04-14 13:00 | 39 | 38 |  |  | 42839.5417 | 58 | 52
2017-04-14 13:30 | 37 | 35 |  |  | 42839.5625 | 55 | 49
2017-04-14 14:00 | 37 | 35 |  |  | 42839.5833 | 59 | 53
2017-04-14 14:30 | 36 | 34 |  |  | 42839.6042 | 57 | 50
2017-04-14 15:00 | 37 | 35 |  |  | 42839.625 | 56 | 50
2017-04-14 15:30 | 39 | 38 |  |  | 42839.6458 | 62 | 53
2017-04-14 16:00 | 40 | 38 |  |  | 42839.6667 | 63 | 55
2017-04-14 16:30 | 40 | 38 |  |  | 42839.6875 | 64 | 56
2017-04-14 17:00 | 40 | 39 |  |  | 42839.7083 | 64 | 56
2017-04-14 17:30 | 41 | 40 |  |  | 42839.7292 | 65 | 57
2017-04-14 18:00 | 42 | 41 |  |  | 42839.75 | 67 | 59
2017-04-14 18:30 | 46 | 44 |  |  | 42839.7708 | 70 | 63
2017-04-14 19:00 | 47 | 46 |  |  | 42839.7917 | 70 | 63
2017-04-14 19:30 | 43 | 42 |  |  | 42839.8125 | 68 | 60
2017-04-14 20:00 | 42 | 41 |  |  | 42839.8333 | 66 | 57
2017-04-14 20:30 | 41 | 40 |  |  | 42839.8542 | 65 | 57
2017-04-14 21:00 | 39 | 38 |  |  | 42839.875 | 64 | 54
2017-04-14 21:30 | 36 | 36 |  |  | 42839.8958 | 62 | 52
2017-04-14 22:00 | 37 | 36 |  |  | 42839.9167 | 62 | 52
2017-04-14 22:30 | 39 | 38 |  |  | 42839.9375 | 64 | 55
2017-04-14 23:00 | 40 | 39 |  |  | 42839.9583 | 65 | 56
2017-04-14 23:30 | 39 | 38 |  |  | 42839.9792 | 63 | 54
2017-04-15 | 37 | 36 |  |  | 42840 | 62 | 51
2017-04-15 00:30 | 34 | 33 |  |  | 42840.0208 | 58 | 47
2017-04-15 01:00 | 31 | 30 |  |  | 42840.0417 | 55 | 42
2017-04-15 01:30 | 30 | 29 |  |  | 42840.0625 | 53 | 40
2017-04-15 02:00 | 28 | 27 |  |  | 42840.0833 | 52 | 39
2017-04-15 02:30 | 26 | 25 |  |  | 42840.1042 | 52 | 37
2017-04-15 03:00 | 24 | 23 |  |  | 42840.125 | 51 | 34
2017-04-15 03:30 | 24 | 23 |  |  | 42840.1458 | 51 | 35
2017-04-15 04:00 | 25 | 24 |  |  | 42840.1667 | 50 | 33
2017-04-15 04:30 | 26 | 24 |  |  | 42840.1875 | 50 | 34
2017-04-15 05:00 | 26 | 24 |  |  | 42840.2083 | 51 | 35
2017-04-15 05:30 | 27 | 26 |  |  | 42840.2292 | 52 | 37
2017-04-15 06:00 | 29 | 28 |  |  | 42840.25 | 53 | 40
2017-04-15 06:30 | 29 | 28 |  |  | 42840.2708 | 53 | 40
2017-04-15 07:00 | 30 | 29 |  |  | 42840.2917 | 56 | 43
2017-04-15 07:30 | 31 | 30 |  |  | 42840.3125 | 57 | 45
2017-04-15 08:00 | 31 | 30 |  |  | 42840.3333 | 56 | 45
2017-04-15 08:30 | 32 | 31 |  |  | 42840.3542 | 57 | 47
2017-04-15 09:00 | 35 | 34 |  |  | 42840.375 | 59 | 50
2017-04-15 09:30 | 37 | 36 |  |  | 42840.3958 | 61 | 52
2017-04-15 10:00 | 39 | 38 |  |  | 42840.4167 | 60 | 52
2017-04-15 10:30 | 38 | 36 |  |  | 42840.4375 | 58 | 50
2017-04-15 11:00 | 37 | 36 |  |  | 42840.4583 | 57 | 49
2017-04-15 11:30 | 38 | 36 |  |  | 42840.4792 | 57 | 50
2017-04-15 12:00 | 38 | 36 |  |  | 42840.5 | 58 | 51
2017-04-15 12:30 | 38 | 36 |  |  | 42840.5208 | 57 | 50
2017-04-15 13:00 | 38 | 36 |  |  | 42840.5417 | 57 | 50
2017-04-15 13:30 | 37 | 35 |  |  | 42840.5625 | 58 | 52
2017-04-15 14:00 | 38 | 37 |  |  | 42840.5833 | 58 | 52
2017-04-15 14:30 | 40 | 38 |  |  | 42840.6042 | 59 | 53
2017-04-15 15:00 | 41 | 39 |  |  | 42840.625 | 60 | 54
2017-04-15 15:30 | 43 | 41 |  |  | 42840.6458 | 61 | 55
2017-04-15 16:00 | 45 | 43 |  |  | 42840.6667 | 63 | 58
2017-04-15 16:30 | 47 | 45 |  |  | 42840.6875 | 67 | 62
2017-04-15 17:00 | 49 | 47 |  |  | 42840.7083 | 70 | 65
2017-04-15 17:30 | 50 | 48 |  |  | 42840.7292 | 70 | 65
2017-04-15 18:00 | 50 | 49 |  |  | 42840.75 | 72 | 66
2017-04-15 18:30 | 52 | 51 |  |  | 42840.7708 | 77 | 68
2017-04-15 19:00 | 51 | 50 |  |  | 42840.7917 | 77 | 69
2017-04-15 19:30 | 48 | 47 |  |  | 42840.8125 | 73 | 65
2017-04-15 20:00 | 47 | 46 |  |  | 42840.8333 | 72 | 64
2017-04-15 20:30 | 46 | 45 |  |  | 42840.8542 | 71 | 64
2017-04-15 21:00 | 44 | 43 |  |  | 42840.875 | 69 | 60
2017-04-15 21:30 | 42 | 41 |  |  | 42840.8958 | 66 | 58
2017-04-15 22:00 | 41 | 40 |  |  | 42840.9167 | 65 | 57
2017-04-15 22:30 | 42 | 41 |  |  | 42840.9375 | 65 | 58
2017-04-15 23:00 | 44 | 44 |  |  | 42840.9583 | 68 | 59
2017-04-15 23:30 | 41 | 41 |  |  | 42840.9792 | 64 | 55
2017-04-16 | 39 | 38 |  |  | 42841 | 63 | 52
2017-04-16 00:30 | 35 | 34 |  |  | 42841.0208 | 59 | 47
2017-04-16 01:00 | 32 | 31 |  |  | 42841.0417 | 56 | 43
2017-04-16 01:30 | 29 | 28 |  |  | 42841.0625 | 53 | 40
2017-04-16 02:00 | 28 | 27 |  |  | 42841.0833 | 53 | 40
2017-04-16 02:30 | 27 | 26 |  |  | 42841.1042 | 50 | 38
2017-04-16 03:00 | 27 | 25 |  |  | 42841.125 | 48 | 37
2017-04-16 03:30 | 29 | 26 |  |  | 42841.1458 | 45 | 38
2017-04-16 04:00 | 30 | 26 |  |  | 42841.1667 | 43 | 37
2017-04-16 04:30 | 30 | 25 |  |  | 42841.1875 | 43 | 37
2017-04-16 05:00 | 30 | 26 |  |  | 42841.2083 | 43 | 37
2017-04-16 05:30 | 31 | 27 |  |  | 42841.2292 | 44 | 38
2017-04-16 06:00 | 32 | 28 |  |  | 42841.25 | 45 | 40
2017-04-16 06:30 | 32 | 28 |  |  | 42841.2708 | 48 | 42
2017-04-16 07:00 | 33 | 29 |  |  | 42841.2917 | 49 | 44
2017-04-16 07:30 | 32 | 28 |  |  | 42841.3125 | 48 | 43
2017-04-16 08:00 | 32 | 29 |  |  | 42841.3333 | 48 | 43
2017-04-16 08:30 | 34 | 30 |  |  | 42841.3542 | 49 | 46
2017-04-16 09:00 | 33 | 29 |  |  | 42841.375 | 49 | 45
2017-04-16 09:30 | 37 | 33 |  |  | 42841.3958 | 51 | 49
2017-04-16 10:00 | 36 | 32 |  |  | 42841.4167 | 50 | 47
2017-04-16 10:30 | 38 | 34 |  |  | 42841.4375 | 51 | 49
2017-04-16 11:00 | 38 | 33 |  |  | 42841.4583 | 50 | 48
2017-04-16 11:30 | 39 | 35 |  |  | 42841.4792 | 51 | 49
2017-04-16 12:00 | 39 | 34 |  |  | 42841.5 | 50 | 48
2017-04-16 12:30 | 39 | 34 |  |  | 42841.5208 | 52 | 51
2017-04-16 13:00 | 38 | 33 |  |  | 42841.5417 | 49 | 48
2017-04-16 13:30 | 40 | 35 |  |  | 42841.5625 | 48 | 46
2017-04-16 14:00 | 40 | 35 |  |  | 42841.5833 | 50 | 48
2017-04-16 14:30 | 39 | 34 |  |  | 42841.6042 | 50 | 48
2017-04-16 15:00 | 42 | 38 |  |  | 42841.625 | 53 | 51
2017-04-16 15:30 | 44 | 39 |  |  | 42841.6458 | 55 | 53
2017-04-16 16:00 | 44 | 40 |  |  | 42841.6667 | 58 | 56
2017-04-16 16:30 | 47 | 43 |  |  | 42841.6875 | 61 | 60
2017-04-16 17:00 | 48 | 45 |  |  | 42841.7083 | 65 | 62
2017-04-16 17:30 | 48 | 45 |  |  | 42841.7292 | 64 | 61
2017-04-16 18:00 | 48 | 46 |  |  | 42841.75 | 67 | 63
2017-04-16 18:30 | 49 | 48 |  |  | 42841.7708 | 71 | 65
2017-04-16 19:00 | 51 | 50 |  |  | 42841.7917 | 74 | 67
2017-04-16 19:30 | 49 | 48 |  |  | 42841.8125 | 72 | 65
2017-04-16 20:00 | 49 | 47 |  |  | 42841.8333 | 70 | 64
2017-04-16 20:30 | 48 | 46 |  |  | 42841.8542 | 69 | 63
2017-04-16 21:00 | 46 | 44 |  |  | 42841.875 | 63 | 60
2017-04-16 21:30 | 43 | 41 |  |  | 42841.8958 | 60 | 56
2017-04-16 22:00 | 43 | 40 |  |  | 42841.9167 | 60 | 57
2017-04-16 22:30 | 44 | 41 |  |  | 42841.9375 | 63 | 59
2017-04-16 23:00 | 45 | 43 |  |  | 42841.9583 | 63 | 58
2017-04-16 23:30 | 41 | 39 |  |  | 42841.9792 | 60 | 56
2017-04-17 | 38 | 36 |  |  | 42842 | 56 | 51
2017-04-17 00:30 | 35 | 33 |  |  | 42842.0208 | 52 | 46
2017-04-17 01:00 | 32 | 30 |  |  | 42842.0417 | 50 | 42
2017-04-17 01:30 | 29 | 27 |  |  | 42842.0625 | 47 | 39
2017-04-17 02:00 | 30 | 27 |  |  | 42842.0833 | 46 | 40
2017-04-17 02:30 | 30 | 26 |  |  | 42842.1042 | 43 | 38
2017-04-17 03:00 | 29 | 25 |  |  | 42842.125 | 42 | 36
2017-04-17 03:30 | 29 | 25 |  |  | 42842.1458 | 42 | 36
2017-04-17 04:00 | 29 | 25 |  |  | 42842.1667 | 42 | 36
2017-04-17 04:30 | 28 | 24 |  |  | 42842.1875 | 42 | 36
2017-04-17 05:00 | 29 | 25 |  |  | 42842.2083 | 43 | 37
2017-04-17 05:30 | 30 | 26 |  |  | 42842.2292 | 44 | 39
2017-04-17 06:00 | 32 | 28 |  |  | 42842.25 | 47 | 41
2017-04-17 06:30 | 33 | 30 |  |  | 42842.2708 | 48 | 44
2017-04-17 07:00 | 32 | 29 |  |  | 42842.2917 | 48 | 44
2017-04-17 07:30 | 32 | 29 |  |  | 42842.3125 | 49 | 46
2017-04-17 08:00 | 34 | 31 |  |  | 42842.3333 | 51 | 48
2017-04-17 08:30 | 35 | 31 |  |  | 42842.3542 | 53 | 51
2017-04-17 09:00 | 37 | 33 |  |  | 42842.375 | 54 | 52
2017-04-17 09:30 | 39 | 35 |  |  | 42842.3958 | 55 | 54
2017-04-17 10:00 | 42 | 38 |  |  | 42842.4167 | 57 | 56
2017-04-17 10:30 | 42 | 38 |  |  | 42842.4375 | 57 | 55
2017-04-17 11:00 | 41 | 37 |  |  | 42842.4583 | 56 | 54
2017-04-17 11:30 | 41 | 38 |  |  | 42842.4792 | 57 | 55
2017-04-17 12:00 | 42 | 39 |  |  | 42842.5 | 59 | 57
2017-04-17 12:30 | 42 | 39 |  |  | 42842.5208 | 59 | 57
2017-04-17 13:00 | 43 | 40 |  |  | 42842.5417 | 59 | 57
2017-04-17 13:30 | 46 | 42 |  |  | 42842.5625 | 60 | 59
2017-04-17 14:00 | 48 | 44 |  |  | 42842.5833 | 62 | 60
2017-04-17 14:30 | 50 | 45 |  |  | 42842.6042 | 62 | 61
2017-04-17 15:00 | 49 | 44 |  |  | 42842.625 | 62 | 61
2017-04-17 15:30 | 48 | 44 |  |  | 42842.6458 | 64 | 62
2017-04-17 16:00 | 51 | 47 |  |  | 42842.6667 | 68 | 66
2017-04-17 16:30 | 53 | 49 |  |  | 42842.6875 | 72 | 70
2017-04-17 17:00 | 56 | 53 |  |  | 42842.7083 | 76 | 75
2017-04-17 17:30 | 57 | 54 |  |  | 42842.7292 | 77 | 75
2017-04-17 18:00 | 63 | 60 |  |  | 42842.75 | 83 | 81
2017-04-17 18:30 | 63 | 61 |  |  | 42842.7708 | 83 | 79
2017-04-17 19:00 | 59 | 58 |  |  | 42842.7917 | 83 | 77
2017-04-17 19:30 | 55 | 54 |  |  | 42842.8125 | 79 | 73
2017-04-17 20:00 | 54 | 53 |  |  | 42842.8333 | 78 | 72
2017-04-17 20:30 | 51 | 50 |  |  | 42842.8542 | 76 | 69
2017-04-17 21:00 | 48 | 47 |  |  | 42842.875 | 71 | 65
2017-04-17 21:30 | 49 | 45 |  |  | 42842.8958 | 66 | 62
2017-04-17 22:00 | 47 | 44 |  |  | 42842.9167 | 65 | 62
2017-04-17 22:30 | 48 | 45 |  |  | 42842.9375 | 67 | 64
2017-04-17 23:00 | 49 | 45 |  |  | 42842.9583 | 66 | 63
2017-04-17 23:30 | 45 | 42 |  |  | 42842.9792 | 63 | 59
2017-04-18 | 39 | 37 |  |  | 42843 | 59 | 54
2017-04-18 00:30 | 36 | 34 |  |  | 42843.0208 | 54 | 48
2017-04-18 01:00 | 32 | 29 |  |  | 42843.0417 | 51 | 45
2017-04-18 01:30 | 31 | 29 |  |  | 42843.0625 | 50 | 44
2017-04-18 02:00 | 30 | 27 |  |  | 42843.0833 | 48 | 41
2017-04-18 02:30 | 30 | 27 |  |  | 42843.1042 | 48 | 41
2017-04-18 03:00 | 29 | 26 |  |  | 42843.125 | 46 | 39
2017-04-18 03:30 | 30 | 27 |  |  | 42843.1458 | 46 | 39
2017-04-18 04:00 | 31 | 28 |  |  | 42843.1667 | 46 | 39
2017-04-18 04:30 | 33 | 29 |  |  | 42843.1875 | 48 | 42
2017-04-18 05:00 | 34 | 30 |  |  | 42843.2083 | 50 | 44
2017-04-18 05:30 | 38 | 35 |  |  | 42843.2292 | 53 | 49
2017-04-18 06:00 | 44 | 40 |  |  | 42843.25 | 59 | 55
2017-04-18 06:30 | 49 | 46 |  |  | 42843.2708 | 68 | 65
2017-04-18 07:00 | 57 | 54 |  |  | 42843.2917 | 78 | 76
2017-04-18 07:30 | 60 | 57 |  |  | 42843.3125 | 82 | 81
2017-04-18 08:00 | 60 | 57 |  |  | 42843.3333 | 83 | 82
2017-04-18 08:30 | 59 | 56 |  |  | 42843.3542 | 84 | 82
2017-04-18 09:00 | 60 | 56 |  |  | 42843.375 | 84 | 83
2017-04-18 09:30 | 60 | 56 |  |  | 42843.3958 | 86 | 85
2017-04-18 10:00 | 60 | 56 |  |  | 42843.4167 | 88 | 87
2017-04-18 10:30 | 57 | 55 |  |  | 42843.4375 | 87 | 84
2017-04-18 11:00 | 57 | 55 |  |  | 42843.4583 | 87 | 83
2017-04-18 11:30 | 60 | 58 |  |  | 42843.4792 | 89 | 85
2017-04-18 12:00 | 59 | 57 |  |  | 42843.5 | 89 | 85
2017-04-18 12:30 | 60 | 58 |  |  | 42843.5208 | 88 | 84
2017-04-18 13:00 | 60 | 58 |  |  | 42843.5417 | 89 | 86
2017-04-18 13:30 | 62 | 59 |  |  | 42843.5625 | 91 | 88
2017-04-18 14:00 | 64 | 61 |  |  | 42843.5833 | 92 | 89
2017-04-18 14:30 | 63 | 61 |  |  | 42843.6042 | 92 | 88
2017-04-18 15:00 | 65 | 64 |  |  | 42843.625 | 95 | 90
2017-04-18 15:30 | 62 | 61 |  |  | 42843.6458 | 94 | 89
2017-04-18 16:00 | 62 | 61 |  |  | 42843.6667 | 97 | 91
2017-04-18 16:30 | 63 | 62 |  |  | 42843.6875 | 98 | 92
2017-04-18 17:00 | 66 | 65 |  |  | 42843.7083 | 100 | 94
2017-04-18 17:30 | 66 | 66 |  |  | 42843.7292 | 99 | 92
2017-04-18 18:00 | 66 | 66 |  |  | 42843.75 | 100 | 92
2017-04-18 18:30 | 66 | 66 |  |  | 42843.7708 | 99 | 91
2017-04-18 19:00 | 66 | 65 |  |  | 42843.7917 | 99 | 91
2017-04-18 19:30 | 64 | 63 |  |  | 42843.8125 | 97 | 88
2017-04-18 20:00 | 61 | 60 |  |  | 42843.8333 | 94 | 85
2017-04-18 20:30 | 61 | 60 |  |  | 42843.8542 | 92 | 83
2017-04-18 21:00 | 57 | 56 |  |  | 42843.875 | 84 | 77
2017-04-18 21:30 | 55 | 53 |  |  | 42843.8958 | 79 | 73
2017-04-18 22:00 | 52 | 50 |  |  | 42843.9167 | 76 | 71
2017-04-18 22:30 | 53 | 52 |  |  | 42843.9375 | 78 | 72
2017-04-18 23:00 | 54 | 52 |  |  | 42843.9583 | 78 | 72
2017-04-18 23:30 | 50 | 49 |  |  | 42843.9792 | 74 | 67
2017-04-19 | 45 | 43 |  |  | 42844 | 68 | 61
2017-04-19 00:30 | 40 | 39 |  |  | 42844.0208 | 64 | 56
2017-04-19 01:00 | 37 | 36 |  |  | 42844.0417 | 61 | 51
2017-04-19 01:30 | 34 | 33 |  |  | 42844.0625 | 58 | 48
2017-04-19 02:00 | 33 | 32 |  |  | 42844.0833 | 57 | 47
2017-04-19 02:30 | 33 | 31 |  |  | 42844.1042 | 57 | 46
2017-04-19 03:00 | 32 | 30 |  |  | 42844.125 | 56 | 45
2017-04-19 03:30 | 32 | 30 |  |  | 42844.1458 | 55 | 44
2017-04-19 04:00 | 32 | 31 |  |  | 42844.1667 | 54 | 43
2017-04-19 04:30 | 32 | 31 |  |  | 42844.1875 | 55 | 44
2017-04-19 05:00 | 34 | 33 |  |  | 42844.2083 | 57 | 47
2017-04-19 05:30 | 39 | 37 |  |  | 42844.2292 | 60 | 52
2017-04-19 06:00 | 46 | 44 |  |  | 42844.25 | 66 | 60
2017-04-19 06:30 | 53 | 51 |  |  | 42844.2708 | 75 | 71
2017-04-19 07:00 | 60 | 57 |  |  | 42844.2917 | 83 | 79
2017-04-19 07:30 | 63 | 60 |  |  | 42844.3125 | 88 | 85
2017-04-19 08:00 | 63 | 60 |  |  | 42844.3333 | 90 | 86
2017-04-19 08:30 | 62 | 59 |  |  | 42844.3542 | 89 | 85
2017-04-19 09:00 | 61 | 58 |  |  | 42844.375 | 87 | 84
2017-04-19 09:30 | 63 | 58 |  |  | 42844.3958 | 87 | 85
2017-04-19 10:00 | 63 | 59 |  |  | 42844.4167 | 90 | 87
2017-04-19 10:30 | 63 | 59 |  |  | 42844.4375 | 90 | 88
2017-04-19 11:00 | 63 | 60 |  |  | 42844.4583 | 90 | 87
2017-04-19 11:30 | 61 | 58 |  |  | 42844.4792 | 88 | 85
2017-04-19 12:00 | 62 | 58 |  |  | 42844.5 | 87 | 84
2017-04-19 12:30 | 62 | 58 |  |  | 42844.5208 | 86 | 83
2017-04-19 13:00 | 61 | 57 |  |  | 42844.5417 | 88 | 85
2017-04-19 13:30 | 65 | 62 |  |  | 42844.5625 | 90 | 87
2017-04-19 14:00 | 61 | 58 |  |  | 42844.5833 | 90 | 87
2017-04-19 14:30 | 62 | 59 |  |  | 42844.6042 | 90 | 86
2017-04-19 15:00 | 60 | 57 |  |  | 42844.625 | 88 | 85
2017-04-19 15:30 | 59 | 57 |  |  | 42844.6458 | 89 | 85
2017-04-19 16:00 | 63 | 61 |  |  | 42844.6667 | 93 | 89
2017-04-19 16:30 | 65 | 63 |  |  | 42844.6875 | 95 | 90
2017-04-19 17:00 | 67 | 65 |  |  | 42844.7083 | 97 | 92
2017-04-19 17:30 | 66 | 64 |  |  | 42844.7292 | 95 | 89
2017-04-19 18:00 | 66 | 65 |  |  | 42844.75 | 95 | 89
2017-04-19 18:30 | 66 | 64 |  |  | 42844.7708 | 95 | 88
2017-04-19 19:00 | 66 | 65 |  |  | 42844.7917 | 95 | 87
2017-04-19 19:30 | 64 | 62 |  |  | 42844.8125 | 92 | 85
2017-04-19 20:00 | 62 | 61 |  |  | 42844.8333 | 91 | 83
2017-04-19 20:30 | 61 | 60 |  |  | 42844.8542 | 90 | 82
2017-04-19 21:00 | 58 | 56 |  |  | 42844.875 | 85 | 77
2017-04-19 21:30 | 58 | 55 |  |  | 42844.8958 | 79 | 74
2017-04-19 22:00 | 56 | 54 |  |  | 42844.9167 | 79 | 74
2017-04-19 22:30 | 57 | 56 |  |  | 42844.9375 | 81 | 76
2017-04-19 23:00 | 56 | 55 |  |  | 42844.9583 | 80 | 74
2017-04-19 23:30 | 52 | 51 |  |  | 42844.9792 | 75 | 68
2017-04-20 | 47 | 45 |  |  | 42845 | 70 | 62
2017-04-20 00:30 | 41 | 40 |  |  | 42845.0208 | 65 | 57
2017-04-20 01:00 | 38 | 37 |  |  | 42845.0417 | 62 | 52
2017-04-20 01:30 | 36 | 35 |  |  | 42845.0625 | 60 | 49
2017-04-20 02:00 | 36 | 34 |  |  | 42845.0833 | 57 | 49
2017-04-20 02:30 | 35 | 32 |  |  | 42845.1042 | 56 | 48
2017-04-20 03:00 | 34 | 31 |  |  | 42845.125 | 55 | 46
2017-04-20 03:30 | 34 | 32 |  |  | 42845.1458 | 54 | 45
2017-04-20 04:00 | 35 | 32 |  |  | 42845.1667 | 55 | 46
2017-04-20 04:30 | 35 | 33 |  |  | 42845.1875 | 55 | 46
2017-04-20 05:00 | 38 | 36 |  |  | 42845.2083 | 57 | 50
2017-04-20 05:30 | 43 | 41 |  |  | 42845.2292 | 62 | 56
2017-04-20 06:00 | 47 | 45 |  |  | 42845.25 | 66 | 61
2017-04-20 06:30 | 53 | 50 |  |  | 42845.2708 | 75 | 71
2017-04-20 07:00 | 60 | 57 |  |  | 42845.2917 | 83 | 80
2017-04-20 07:30 | 63 | 61 |  |  | 42845.3125 | 91 | 87
2017-04-20 08:00 | 63 | 60 |  |  | 42845.3333 | 89 | 86
2017-04-20 08:30 | 63 | 59 |  |  | 42845.3542 | 89 | 87
2017-04-20 09:00 | 64 | 60 |  |  | 42845.375 | 89 | 86
2017-04-20 09:30 | 65 | 61 |  |  | 42845.3958 | 92 | 89
2017-04-20 10:00 | 65 | 61 |  |  | 42845.4167 | 90 | 88
2017-04-20 10:30 | 61 | 57 |  |  | 42845.4375 | 87 | 84
2017-04-20 11:00 | 62 | 59 |  |  | 42845.4583 | 89 | 86
2017-04-20 11:30 | 62 | 58 |  |  | 42845.4792 | 87 | 84
2017-04-20 12:00 | 62 | 58 |  |  | 42845.5 | 86 | 83
2017-04-20 12:30 | 59 | 56 |  |  | 42845.5208 | 86 | 82
2017-04-20 13:00 | 60 | 57 |  |  | 42845.5417 | 87 | 84
2017-04-20 13:30 | 61 | 58 |  |  | 42845.5625 | 87 | 84
2017-04-20 14:00 | 63 | 59 |  |  | 42845.5833 | 90 | 87
2017-04-20 14:30 | 66 | 62 |  |  | 42845.6042 | 94 | 91
2017-04-20 15:00 | 66 | 63 |  |  | 42845.625 | 95 | 92
2017-04-20 15:30 | 66 | 63 |  |  | 42845.6458 | 93 | 90
2017-04-20 16:00 | 63 | 60 |  |  | 42845.6667 | 91 | 87
2017-04-20 16:30 | 64 | 61 |  |  | 42845.6875 | 93 | 89
2017-04-20 17:00 | 65 | 63 |  |  | 42845.7083 | 96 | 92
2017-04-20 17:30 | 65 | 64 |  |  | 42845.7292 | 97 | 90
2017-04-20 18:00 | 67 | 66 |  |  | 42845.75 | 100 | 92
2017-04-20 18:30 | 66 | 65 |  |  | 42845.7708 | 98 | 89
2017-04-20 19:00 | 66 | 66 |  |  | 42845.7917 | 100 | 89
2017-04-20 19:30 | 62 | 61 |  |  | 42845.8125 | 96 | 85
2017-04-20 20:00 | 60 | 59 |  |  | 42845.8333 | 92 | 82
2017-04-20 20:30 | 60 | 59 |  |  | 42845.8542 | 88 | 80
2017-04-20 21:00 | 57 | 56 |  |  | 42845.875 | 83 | 76
2017-04-20 21:30 | 53 | 51 |  |  | 42845.8958 | 75 | 70
2017-04-20 22:00 | 52 | 49 |  |  | 42845.9167 | 74 | 69
2017-04-20 22:30 | 54 | 51 |  |  | 42845.9375 | 76 | 71
2017-04-20 23:00 | 53 | 51 |  |  | 42845.9583 | 74 | 68
2017-04-20 23:30 | 49 | 47 |  |  | 42845.9792 | 71 | 65
2017-04-21 | 43 | 41 |  |  | 42846 | 65 | 57
2017-04-21 00:30 | 38 | 36 |  |  | 42846.0208 | 58 | 50
2017-04-21 01:00 | 35 | 33 |  |  | 42846.0417 | 55 | 46
2017-04-21 01:30 | 32 | 30 |  |  | 42846.0625 | 51 | 42
2017-04-21 02:00 | 31 | 28 |  |  | 42846.0833 | 50 | 41
2017-04-21 02:30 | 30 | 28 |  |  | 42846.1042 | 49 | 40
2017-04-21 03:00 | 28 | 26 |  |  | 42846.125 | 48 | 39
2017-04-21 03:30 | 28 | 26 |  |  | 42846.1458 | 47 | 38
2017-04-21 04:00 | 28 | 25 |  |  | 42846.1667 | 48 | 38
2017-04-21 04:30 | 28 | 25 |  |  | 42846.1875 | 48 | 38
2017-04-21 05:00 | 31 | 27 |  |  | 42846.2083 | 49 | 41
2017-04-21 05:30 | 36 | 33 |  |  | 42846.2292 | 54 | 47
2017-04-21 06:00 | 42 | 39 |  |  | 42846.25 | 60 | 55
2017-04-21 06:30 | 49 | 45 |  |  | 42846.2708 | 70 | 67
2017-04-21 07:00 | 57 | 52 |  |  | 42846.2917 | 79 | 77
2017-04-21 07:30 | 58 | 55 |  |  | 42846.3125 | 85 | 81
2017-04-21 08:00 | 57 | 54 |  |  | 42846.3333 | 87 | 81
2017-04-21 08:30 | 55 | 52 |  |  | 42846.3542 | 86 | 81
2017-04-21 09:00 | 54 | 51 |  |  | 42846.375 | 84 | 80
2017-04-21 09:30 | 55 | 52 |  |  | 42846.3958 | 84 | 80
2017-04-21 10:00 | 57 | 54 |  |  | 42846.4167 | 88 | 83
2017-04-21 10:30 | 57 | 55 |  |  | 42846.4375 | 90 | 85
2017-04-21 11:00 | 56 | 54 |  |  | 42846.4583 | 87 | 82
2017-04-21 11:30 | 52 | 50 |  |  | 42846.4792 | 84 | 79
2017-04-21 12:00 | 54 | 51 |  |  | 42846.5 | 85 | 80
2017-04-21 12:30 | 52 | 50 |  |  | 42846.5208 | 84 | 79
2017-04-21 13:00 | 51 | 49 |  |  | 42846.5417 | 84 | 79
2017-04-21 13:30 | 53 | 50 |  |  | 42846.5625 | 85 | 79
2017-04-21 14:00 | 57 | 55 |  |  | 42846.5833 | 88 | 82
2017-04-21 14:30 | 58 | 56 |  |  | 42846.6042 | 87 | 81
2017-04-21 15:00 | 55 | 53 |  |  | 42846.625 | 87 | 80
2017-04-21 15:30 | 52 | 50 |  |  | 42846.6458 | 85 | 77
2017-04-21 16:00 | 52 | 50 |  |  | 42846.6667 | 85 | 78
2017-04-21 16:30 | 52 | 51 |  |  | 42846.6875 | 87 | 79
2017-04-21 17:00 | 56 | 55 |  |  | 42846.7083 | 89 | 81
2017-04-21 17:30 | 55 | 54 |  |  | 42846.7292 | 86 | 78
2017-04-21 18:00 | 55 | 54 |  |  | 42846.75 | 87 | 78
2017-04-21 18:30 | 53 | 52 |  |  | 42846.7708 | 86 | 76
2017-04-21 19:00 | 52 | 51 |  |  | 42846.7917 | 85 | 75
2017-04-21 19:30 | 51 | 49 |  |  | 42846.8125 | 81 | 72
2017-04-21 20:00 | 51 | 49 |  |  | 42846.8333 | 78 | 71
2017-04-21 20:30 | 51 | 48 |  |  | 42846.8542 | 76 | 70
2017-04-21 21:00 | 51 | 47 |  |  | 42846.875 | 71 | 67
2017-04-21 21:30 | 48 | 44 |  |  | 42846.8958 | 67 | 62
2017-04-21 22:00 | 47 | 42 |  |  | 42846.9167 | 68 | 64
2017-04-21 22:30 | 48 | 45 |  |  | 42846.9375 | 70 | 65
2017-04-21 23:00 | 49 | 47 |  |  | 42846.9583 | 70 | 65
2017-04-21 23:30 | 45 | 43 |  |  | 42846.9792 | 67 | 61
2017-04-22 | 40 | 38 |  |  | 42847 | 61 | 54
2017-04-22 00:30 | 34 | 32 |  |  | 42847.0208 | 57 | 49
2017-04-22 01:00 | 33 | 31 |  |  | 42847.0417 | 56 | 46
2017-04-22 01:30 | 31 | 29 |  |  | 42847.0625 | 54 | 44
2017-04-22 02:00 | 30 | 28 |  |  | 42847.0833 | 51 | 41
2017-04-22 02:30 | 28 | 26 |  |  | 42847.1042 | 50 | 39
2017-04-22 03:00 | 28 | 25 |  |  | 42847.125 | 48 | 37
2017-04-22 03:30 | 27 | 25 |  |  | 42847.1458 | 48 | 37
2017-04-22 04:00 | 28 | 25 |  |  | 42847.1667 | 47 | 36
2017-04-22 04:30 | 27 | 25 |  |  | 42847.1875 | 48 | 37
2017-04-22 05:00 | 29 | 26 |  |  | 42847.2083 | 50 | 39
2017-04-22 05:30 | 30 | 28 |  |  | 42847.2292 | 51 | 41
2017-04-22 06:00 | 32 | 30 |  |  | 42847.25 | 53 | 44
2017-04-22 06:30 | 34 | 31 |  |  | 42847.2708 | 56 | 48
2017-04-22 07:00 | 37 | 35 |  |  | 42847.2917 | 60 | 53
2017-04-22 07:30 | 41 | 39 |  |  | 42847.3125 | 64 | 57
2017-04-22 08:00 | 45 | 43 |  |  | 42847.3333 | 69 | 63
2017-04-22 08:30 | 48 | 46 |  |  | 42847.3542 | 72 | 68
2017-04-22 09:00 | 51 | 49 |  |  | 42847.375 | 76 | 71
2017-04-22 09:30 | 52 | 50 |  |  | 42847.3958 | 76 | 72
2017-04-22 10:00 | 54 | 52 |  |  | 42847.4167 | 80 | 75
2017-04-22 10:30 | 53 | 52 |  |  | 42847.4375 | 78 | 74
2017-04-22 11:00 | 51 | 49 |  |  | 42847.4583 | 74 | 69
2017-04-22 11:30 | 50 | 48 |  |  | 42847.4792 | 74 | 69
2017-04-22 12:00 | 49 | 47 |  |  | 42847.5 | 74 | 69
2017-04-22 12:30 | 45 | 43 |  |  | 42847.5208 | 69 | 64
2017-04-22 13:00 | 45 | 43 |  |  | 42847.5417 | 64 | 59
2017-04-22 13:30 | 44 | 42 |  |  | 42847.5625 | 62 | 57
2017-04-22 14:00 | 42 | 40 |  |  | 42847.5833 | 61 | 55
2017-04-22 14:30 | 43 | 41 |  |  | 42847.6042 | 64 | 59
2017-04-22 15:00 | 44 | 42 |  |  | 42847.625 | 66 | 61
2017-04-22 15:30 | 46 | 44 |  |  | 42847.6458 | 69 | 63
2017-04-22 16:00 | 46 | 44 |  |  | 42847.6667 | 71 | 65
2017-04-22 16:30 | 48 | 47 |  |  | 42847.6875 | 74 | 68
2017-04-22 17:00 | 51 | 50 |  |  | 42847.7083 | 78 | 73
2017-04-22 17:30 | 52 | 51 |  |  | 42847.7292 | 78 | 73
2017-04-22 18:00 | 54 | 53 |  |  | 42847.75 | 79 | 75
2017-04-22 18:30 | 56 | 54 |  |  | 42847.7708 | 81 | 76
2017-04-22 19:00 | 56 | 55 |  |  | 42847.7917 | 82 | 77
2017-04-22 19:30 | 54 | 53 |  |  | 42847.8125 | 80 | 74
2017-04-22 20:00 | 52 | 51 |  |  | 42847.8333 | 78 | 72
2017-04-22 20:30 | 51 | 50 |  |  | 42847.8542 | 77 | 71
2017-04-22 21:00 | 49 | 47 |  |  | 42847.875 | 73 | 67
2017-04-22 21:30 | 47 | 45 |  |  | 42847.8958 | 70 | 65
2017-04-22 22:00 | 46 | 44 |  |  | 42847.9167 | 71 | 65
2017-04-22 22:30 | 47 | 45 |  |  | 42847.9375 | 72 | 66
2017-04-22 23:00 | 48 | 46 |  |  | 42847.9583 | 72 | 66
2017-04-22 23:30 | 45 | 44 |  |  | 42847.9792 | 70 | 63
2017-04-23 | 42 | 41 |  |  | 42848 | 66 | 59
2017-04-23 00:30 | 38 | 37 |  |  | 42848.0208 | 62 | 53
2017-04-23 01:00 | 35 | 34 |  |  | 42848.0417 | 58 | 49
2017-04-23 01:30 | 34 | 32 |  |  | 42848.0625 | 56 | 46
2017-04-23 02:00 | 32 | 30 |  |  | 42848.0833 | 55 | 44
2017-04-23 02:30 | 32 | 30 |  |  | 42848.1042 | 54 | 43
2017-04-23 03:00 | 30 | 28 |  |  | 42848.125 | 52 | 41
2017-04-23 03:30 | 29 | 27 |  |  | 42848.1458 | 51 | 40
2017-04-23 04:00 | 30 | 28 |  |  | 42848.1667 | 52 | 40
2017-04-23 04:30 | 30 | 28 |  |  | 42848.1875 | 51 | 40
2017-04-23 05:00 | 29 | 27 |  |  | 42848.2083 | 52 | 41
2017-04-23 05:30 | 29 | 27 |  |  | 42848.2292 | 53 | 42
2017-04-23 06:00 | 30 | 28 |  |  | 42848.25 | 53 | 43
2017-04-23 06:30 | 29 | 28 |  |  | 42848.2708 | 55 | 44
2017-04-23 07:00 | 31 | 30 |  |  | 42848.2917 | 56 | 46
2017-04-23 07:30 | 32 | 31 |  |  | 42848.3125 | 56 | 46
2017-04-23 08:00 | 33 | 32 |  |  | 42848.3333 | 57 | 48
2017-04-23 08:30 | 34 | 32 |  |  | 42848.3542 | 58 | 50
2017-04-23 09:00 | 37 | 35 |  |  | 42848.375 | 60 | 53
2017-04-23 09:30 | 38 | 36 |  |  | 42848.3958 | 62 | 55
2017-04-23 10:00 | 38 | 36 |  |  | 42848.4167 | 62 | 56
2017-04-23 10:30 | 40 | 38 |  |  | 42848.4375 | 61 | 56
2017-04-23 11:00 | 40 | 37 |  |  | 42848.4583 | 61 | 55
2017-04-23 11:30 | 42 | 40 |  |  | 42848.4792 | 63 | 57
2017-04-23 12:00 | 43 | 41 |  |  | 42848.5 | 64 | 59
2017-04-23 12:30 | 45 | 42 |  |  | 42848.5208 | 63 | 58
2017-04-23 13:00 | 46 | 43 |  |  | 42848.5417 | 64 | 59
2017-04-23 13:30 | 44 | 41 |  |  | 42848.5625 | 64 | 60
2017-04-23 14:00 | 45 | 43 |  |  | 42848.5833 | 64 | 60
2017-04-23 14:30 | 44 | 41 |  |  | 42848.6042 | 64 | 59
2017-04-23 15:00 | 44 | 42 |  |  | 42848.625 | 65 | 61
2017-04-23 15:30 | 44 | 42 |  |  | 42848.6458 | 66 | 62
2017-04-23 16:00 | 51 | 50 |  |  | 42848.6667 | 73 | 68
2017-04-23 16:30 | 54 | 53 |  |  | 42848.6875 | 76 | 72
2017-04-23 17:00 | 54 | 53 |  |  | 42848.7083 | 79 | 73
2017-04-23 17:30 | 57 | 56 |  |  | 42848.7292 | 82 | 75
2017-04-23 18:00 | 60 | 59 |  |  | 42848.75 | 84 | 79
2017-04-23 18:30 | 63 | 62 |  |  | 42848.7708 | 87 | 81
2017-04-23 19:00 | 64 | 63 |  |  | 42848.7917 | 89 | 83
2017-04-23 19:30 | 62 | 62 |  |  | 42848.8125 | 86 | 81
2017-04-23 20:00 | 61 | 60 |  |  | 42848.8333 | 84 | 79
2017-04-23 20:30 | 58 | 58 |  |  | 42848.8542 | 81 | 76
2017-04-23 21:00 | 55 | 54 |  |  | 42848.875 | 77 | 72
2017-04-23 21:30 | 51 | 50 |  |  | 42848.8958 | 72 | 67
2017-04-23 22:00 | 49 | 48 |  |  | 42848.9167 | 70 | 66
2017-04-23 22:30 | 49 | 47 |  |  | 42848.9375 | 71 | 67
2017-04-23 23:00 | 50 | 48 |  |  | 42848.9583 | 71 | 66
2017-04-23 23:30 | 46 | 45 |  |  | 42848.9792 | 67 | 62
2017-04-24 | 38 | 37 |  |  | 42849 | 59 | 54
2017-04-24 00:30 | 35 | 33 |  |  | 42849.0208 | 55 | 48
2017-04-24 01:00 | 33 | 31 |  |  | 42849.0417 | 53 | 46
2017-04-24 01:30 | 33 | 30 |  |  | 42849.0625 | 51 | 43
2017-04-24 02:00 | 32 | 29 |  |  | 42849.0833 | 50 | 43
2017-04-24 02:30 | 30 | 27 |  |  | 42849.1042 | 49 | 41
2017-04-24 03:00 | 30 | 27 |  |  | 42849.125 | 48 | 40
2017-04-24 03:30 | 30 | 27 |  |  | 42849.1458 | 49 | 41
2017-04-24 04:00 | 31 | 28 |  |  | 42849.1667 | 51 | 43
2017-04-24 04:30 | 31 | 29 |  |  | 42849.1875 | 51 | 43
2017-04-24 05:00 | 32 | 29 |  |  | 42849.2083 | 52 | 45
2017-04-24 05:30 | 36 | 34 |  |  | 42849.2292 | 57 | 50
2017-04-24 06:00 | 44 | 41 |  |  | 42849.25 | 62 | 58
2017-04-24 06:30 | 50 | 47 |  |  | 42849.2708 | 72 | 68
2017-04-24 07:00 | 59 | 57 |  |  | 42849.2917 | 81 | 79
2017-04-24 07:30 | 62 | 61 |  |  | 42849.3125 | 87 | 85
2017-04-24 08:00 | 63 | 61 |  |  | 42849.3333 | 89 | 86
2017-04-24 08:30 | 59 | 58 |  |  | 42849.3542 | 88 | 85
2017-04-24 09:00 | 55 | 53 |  |  | 42849.375 | 85 | 82
2017-04-24 09:30 | 55 | 53 |  |  | 42849.3958 | 84 | 80
2017-04-24 10:00 | 54 | 53 |  |  | 42849.4167 | 85 | 80
2017-04-24 10:30 | 56 | 55 |  |  | 42849.4375 | 86 | 82
2017-04-24 11:00 | 58 | 57 |  |  | 42849.4583 | 88 | 84
2017-04-24 11:30 | 57 | 55 |  |  | 42849.4792 | 87 | 83
2017-04-24 12:00 | 57 | 55 |  |  | 42849.5 | 88 | 84
2017-04-24 12:30 | 59 | 58 |  |  | 42849.5208 | 92 | 88
2017-04-24 13:00 | 65 | 64 |  |  | 42849.5417 | 95 | 91
2017-04-24 13:30 | 64 | 63 |  |  | 42849.5625 | 94 | 90
2017-04-24 14:00 | 65 | 64 |  |  | 42849.5833 | 93 | 88
2017-04-24 14:30 | 68 | 67 |  |  | 42849.6042 | 94 | 90
2017-04-24 15:00 | 66 | 66 |  |  | 42849.625 | 94 | 90
2017-04-24 15:30 | 63 | 62 |  |  | 42849.6458 | 93 | 87
2017-04-24 16:00 | 65 | 64 |  |  | 42849.6667 | 94 | 89
2017-04-24 16:30 | 66 | 66 |  |  | 42849.6875 | 96 | 91
2017-04-24 17:00 | 67 | 67 |  |  | 42849.7083 | 98 | 92
2017-04-24 17:30 | 66 | 66 |  |  | 42849.7292 | 98 | 90
2017-04-24 18:00 | 66 | 66 |  |  | 42849.75 | 98 | 89
2017-04-24 18:30 | 65 | 65 |  |  | 42849.7708 | 96 | 87
2017-04-24 19:00 | 67 | 67 |  |  | 42849.7917 | 96 | 88
2017-04-24 19:30 | 65 | 64 |  |  | 42849.8125 | 94 | 85
2017-04-24 20:00 | 62 | 62 |  |  | 42849.8333 | 91 | 82
2017-04-24 20:30 | 58 | 58 |  |  | 42849.8542 | 88 | 79
2017-04-24 21:00 | 54 | 54 |  |  | 42849.875 | 82 | 74
2017-04-24 21:30 | 52 | 51 |  |  | 42849.8958 | 79 | 70
2017-04-24 22:00 | 49 | 48 |  |  | 42849.9167 | 73 | 68
2017-04-24 22:30 | 53 | 51 |  |  | 42849.9375 | 75 | 70
2017-04-24 23:00 | 53 | 51 |  |  | 42849.9583 | 74 | 69
2017-04-24 23:30 | 49 | 48 |  |  | 42849.9792 | 71 | 65
2017-04-25 | 45 | 43 |  |  | 42850 | 65 | 60
2017-04-25 00:30 | 39 | 38 |  |  | 42850.0208 | 60 | 53
2017-04-25 01:00 | 35 | 34 |  |  | 42850.0417 | 56 | 49
2017-04-25 01:30 | 33 | 31 |  |  | 42850.0625 | 53 | 45
2017-04-25 02:00 | 32 | 30 |  |  | 42850.0833 | 52 | 43
2017-04-25 02:30 | 32 | 30 |  |  | 42850.1042 | 51 | 42
2017-04-25 03:00 | 29 | 27 |  |  | 42850.125 | 49 | 40
2017-04-25 03:30 | 29 | 27 |  |  | 42850.1458 | 49 | 39
2017-04-25 04:00 | 29 | 27 |  |  | 42850.1667 | 50 | 40
2017-04-25 04:30 | 31 | 29 |  |  | 42850.1875 | 51 | 41
2017-04-25 05:00 | 31 | 29 |  |  | 42850.2083 | 51 | 42
2017-04-25 05:30 | 31 | 30 |  |  | 42850.2292 | 51 | 42
2017-04-25 06:00 | 32 | 31 |  |  | 42850.25 | 54 | 45
2017-04-25 06:30 | 34 | 33 |  |  | 42850.2708 | 57 | 49
2017-04-25 07:00 | 35 | 34 |  |  | 42850.2917 | 58 | 51
2017-04-25 07:30 | 37 | 35 |  |  | 42850.3125 | 60 | 53
2017-04-25 08:00 | 38 | 36 |  |  | 42850.3333 | 60 | 54
2017-04-25 08:30 | 38 | 36 |  |  | 42850.3542 | 61 | 56
2017-04-25 09:00 | 40 | 37 |  |  | 42850.375 | 60 | 56
2017-04-25 09:30 | 42 | 40 |  |  | 42850.3958 | 62 | 58
2017-04-25 10:00 | 43 | 41 |  |  | 42850.4167 | 62 | 58
2017-04-25 10:30 | 44 | 41 |  |  | 42850.4375 | 64 | 61
2017-04-25 11:00 | 42 | 39 |  |  | 42850.4583 | 60 | 57
2017-04-25 11:30 | 42 | 39 |  |  | 42850.4792 | 60 | 57
2017-04-25 12:00 | 42 | 39 |  |  | 42850.5 | 61 | 58
2017-04-25 12:30 | 41 | 39 |  |  | 42850.5208 | 62 | 58
2017-04-25 13:00 | 42 | 39 |  |  | 42850.5417 | 62 | 57
2017-04-25 13:30 | 42 | 39 |  |  | 42850.5625 | 62 | 57
2017-04-25 14:00 | 44 | 41 |  |  | 42850.5833 | 63 | 58
2017-04-25 14:30 | 44 | 41 |  |  | 42850.6042 | 63 | 58
2017-04-25 15:00 | 44 | 42 |  |  | 42850.625 | 65 | 61
2017-04-25 15:30 | 46 | 43 |  |  | 42850.6458 | 68 | 64
2017-04-25 16:00 | 48 | 47 |  |  | 42850.6667 | 71 | 67
2017-04-25 16:30 | 51 | 50 |  |  | 42850.6875 | 76 | 72
2017-04-25 17:00 | 53 | 52 |  |  | 42850.7083 | 79 | 75
2017-04-25 17:30 | 54 | 54 |  |  | 42850.7292 | 83 | 77
2017-04-25 18:00 | 58 | 57 |  |  | 42850.75 | 87 | 80
2017-04-25 18:30 | 58 | 58 |  |  | 42850.7708 | 89 | 81
2017-04-25 19:00 | 61 | 60 |  |  | 42850.7917 | 90 | 83
2017-04-25 19:30 | 60 | 59 |  |  | 42850.8125 | 88 | 82
2017-04-25 20:00 | 61 | 59 |  |  | 42850.8333 | 87 | 81
2017-04-25 20:30 | 59 | 58 |  |  | 42850.8542 | 85 | 80
2017-04-25 21:00 | 57 | 55 |  |  | 42850.875 | 80 | 75
2017-04-25 21:30 | 53 | 51 |  |  | 42850.8958 | 77 | 71
2017-04-25 22:00 | 50 | 49 |  |  | 42850.9167 | 75 | 69
2017-04-25 22:30 | 51 | 50 |  |  | 42850.9375 | 75 | 70
2017-04-25 23:00 | 52 | 52 |  |  | 42850.9583 | 77 | 71
2017-04-25 23:30 | 50 | 49 |  |  | 42850.9792 | 75 | 68
2017-04-26 | 45 | 44 |  |  | 42851 | 68 | 61
2017-04-26 00:30 | 40 | 39 |  |  | 42851.0208 | 64 | 55
2017-04-26 01:00 | 37 | 36 |  |  | 42851.0417 | 61 | 52
2017-04-26 01:30 | 35 | 34 |  |  | 42851.0625 | 58 | 49
2017-04-26 02:00 | 36 | 35 |  |  | 42851.0833 | 58 | 49
2017-04-26 02:30 | 35 | 34 |  |  | 42851.1042 | 56 | 47
2017-04-26 03:00 | 33 | 32 |  |  | 42851.125 | 55 | 45
2017-04-26 03:30 | 32 | 31 |  |  | 42851.1458 | 54 | 44
2017-04-26 04:00 | 32 | 31 |  |  | 42851.1667 | 54 | 44
2017-04-26 04:30 | 34 | 32 |  |  | 42851.1875 | 56 | 46
2017-04-26 05:00 | 36 | 35 |  |  | 42851.2083 | 58 | 49
2017-04-26 05:30 | 41 | 40 |  |  | 42851.2292 | 63 | 55
2017-04-26 06:00 | 47 | 45 |  |  | 42851.25 | 69 | 63
2017-04-26 06:30 | 54 | 52 |  |  | 42851.2708 | 78 | 73
2017-04-26 07:00 | 59 | 58 |  |  | 42851.2917 | 86 | 82
2017-04-26 07:30 | 60 | 59 |  |  | 42851.3125 | 93 | 86
2017-04-26 08:00 | 60 | 60 |  |  | 42851.3333 | 94 | 88
2017-04-26 08:30 | 58 | 57 |  |  | 42851.3542 | 90 | 85
2017-04-26 09:00 | 58 | 56 |  |  | 42851.375 | 90 | 86
2017-04-26 09:30 | 57 | 56 |  |  | 42851.3958 | 96 | 89
2017-04-26 10:00 | 68 | 67 |  |  | 42851.4167 | 103 | 97
2017-04-26 10:30 | 66 | 65 |  |  | 42851.4375 | 101 | 94
2017-04-26 11:00 | 63 | 62 |  |  | 42851.4583 | 97 | 90
2017-04-26 11:30 | 67 | 65 |  |  | 42851.4792 | 99 | 93
2017-04-26 12:00 | 70 | 69 |  |  | 42851.5 | 104 | 98
2017-04-26 12:30 | 70 | 69 |  |  | 42851.5208 | 104 | 98
2017-04-26 13:00 | 71 | 70 |  |  | 42851.5417 | 106 | 100
2017-04-26 13:30 | 71 | 69 |  |  | 42851.5625 | 104 | 98
2017-04-26 14:00 | 70 | 69 |  |  | 42851.5833 | 104 | 97
2017-04-26 14:30 | 70 | 69 |  |  | 42851.6042 | 104 | 98
2017-04-26 15:00 | 71 | 70 |  |  | 42851.625 | 107 | 100
2017-04-26 15:30 | 70 | 70 |  |  | 42851.6458 | 107 | 99
2017-04-26 16:00 | 70 | 69 |  |  | 42851.6667 | 105 | 98
2017-04-26 16:30 | 71 | 70 |  |  | 42851.6875 | 106 | 98
2017-04-26 17:00 | 72 | 71 |  |  | 42851.7083 | 107 | 99
2017-04-26 17:30 | 72 | 71 |  |  | 42851.7292 | 106 | 98
2017-04-26 18:00 | 72 | 71 |  |  | 42851.75 | 106 | 97
2017-04-26 18:30 | 68 | 68 |  |  | 42851.7708 | 102 | 92
2017-04-26 19:00 | 70 | 69 |  |  | 42851.7917 | 99 | 93
2017-04-26 19:30 | 67 | 66 |  |  | 42851.8125 | 97 | 90
2017-04-26 20:00 | 67 | 65 |  |  | 42851.8333 | 94 | 88
2017-04-26 20:30 | 64 | 63 |  |  | 42851.8542 | 92 | 85
2017-04-26 21:00 | 61 | 60 |  |  | 42851.875 | 87 | 80
2017-04-26 21:30 | 59 | 57 |  |  | 42851.8958 | 79 | 74
2017-04-26 22:00 | 58 | 56 |  |  | 42851.9167 | 79 | 74
2017-04-26 22:30 | 59 | 57 |  |  | 42851.9375 | 82 | 76
2017-04-26 23:00 | 59 | 57 |  |  | 42851.9583 | 81 | 74
2017-04-26 23:30 | 54 | 52 |  |  | 42851.9792 | 76 | 69
2017-04-27 | 48 | 46 |  |  | 42852 | 69 | 62
2017-04-27 00:30 | 42 | 40 |  |  | 42852.0208 | 62 | 55
2017-04-27 01:00 | 39 | 37 |  |  | 42852.0417 | 59 | 51
2017-04-27 01:30 | 37 | 35 |  |  | 42852.0625 | 56 | 48
2017-04-27 02:00 | 34 | 32 |  |  | 42852.0833 | 55 | 46
2017-04-27 02:30 | 33 | 31 |  |  | 42852.1042 | 53 | 44
2017-04-27 03:00 | 30 | 28 |  |  | 42852.125 | 50 | 42
2017-04-27 03:30 | 31 | 29 |  |  | 42852.1458 | 51 | 42
2017-04-27 04:00 | 32 | 30 |  |  | 42852.1667 | 51 | 42
2017-04-27 04:30 | 32 | 30 |  |  | 42852.1875 | 51 | 42
2017-04-27 05:00 | 34 | 32 |  |  | 42852.2083 | 54 | 45
2017-04-27 05:30 | 39 | 37 |  |  | 42852.2292 | 59 | 53
2017-04-27 06:00 | 46 | 44 |  |  | 42852.25 | 66 | 60
2017-04-27 06:30 | 54 | 52 |  |  | 42852.2708 | 75 | 71
2017-04-27 07:00 | 59 | 56 |  |  | 42852.2917 | 82 | 79
2017-04-27 07:30 | 61 | 59 |  |  | 42852.3125 | 89 | 85
2017-04-27 08:00 | 61 | 58 |  |  | 42852.3333 | 90 | 85
2017-04-27 08:30 | 60 | 57 |  |  | 42852.3542 | 88 | 84
2017-04-27 09:00 | 59 | 56 |  |  | 42852.375 | 86 | 82
2017-04-27 09:30 | 59 | 55 |  |  | 42852.3958 | 84 | 79
2017-04-27 10:00 | 49 | 46 |  |  | 42852.4167 | 77 | 72
2017-04-27 10:30 | 46 | 43 |  |  | 42852.4375 | 76 | 70
2017-04-27 11:00 | 54 | 50 |  |  | 42852.4583 | 77 | 72
2017-04-27 11:30 | 54 | 50 |  |  | 42852.4792 | 76 | 71
2017-04-27 12:00 | 53 | 49 |  |  | 42852.5 | 76 | 71
2017-04-27 12:30 | 55 | 52 |  |  | 42852.5208 | 81 | 76
2017-04-27 13:00 | 54 | 51 |  |  | 42852.5417 | 83 | 75
2017-04-27 13:30 | 56 | 53 |  |  | 42852.5625 | 88 | 80
2017-04-27 14:00 | 55 | 53 |  |  | 42852.5833 | 89 | 80
2017-04-27 14:30 | 57 | 53 |  |  | 42852.6042 | 83 | 77
2017-04-27 15:00 | 58 | 55 |  |  | 42852.625 | 86 | 81
2017-04-27 15:30 | 60 | 57 |  |  | 42852.6458 | 87 | 82
2017-04-27 16:00 | 64 | 61 |  |  | 42852.6667 | 91 | 86
2017-04-27 16:30 | 66 | 63 |  |  | 42852.6875 | 94 | 89
2017-04-27 17:00 | 68 | 65 |  |  | 42852.7083 | 97 | 91
2017-04-27 17:30 | 68 | 66 |  |  | 42852.7292 | 96 | 90
2017-04-27 18:00 | 68 | 66 |  |  | 42852.75 | 96 | 90
2017-04-27 18:30 | 66 | 63 |  |  | 42852.7708 | 94 | 87
2017-04-27 19:00 | 68 | 66 |  |  | 42852.7917 | 97 | 89
2017-04-27 19:30 | 66 | 65 |  |  | 42852.8125 | 95 | 87
2017-04-27 20:00 | 65 | 64 |  |  | 42852.8333 | 94 | 85
2017-04-27 20:30 | 65 | 63 |  |  | 42852.8542 | 93 | 85
2017-04-27 21:00 | 62 | 60 |  |  | 42852.875 | 90 | 82
2017-04-27 21:30 | 60 | 57 |  |  | 42852.8958 | 83 | 77
2017-04-27 22:00 | 58 | 55 |  |  | 42852.9167 | 82 | 77
2017-04-27 22:30 | 58 | 55 |  |  | 42852.9375 | 83 | 77
2017-04-27 23:00 | 56 | 54 |  |  | 42852.9583 | 82 | 74
2017-04-27 23:30 | 53 | 51 |  |  | 42852.9792 | 77 | 70
2017-04-28 | 49 | 47 |  |  | 42853 | 71 | 64
2017-04-28 00:30 | 45 | 43 |  |  | 42853.0208 | 67 | 59
2017-04-28 01:00 | 43 | 41 |  |  | 42853.0417 | 64 | 55
2017-04-28 01:30 | 41 | 38 |  |  | 42853.0625 | 62 | 52
2017-04-28 02:00 | 38 | 35 |  |  | 42853.0833 | 59 | 49
2017-04-28 02:30 | 37 | 34 |  |  | 42853.1042 | 57 | 47
2017-04-28 03:00 | 35 | 31 |  |  | 42853.125 | 56 | 45
2017-04-28 03:30 | 34 | 31 |  |  | 42853.1458 | 55 | 45
2017-04-28 04:00 | 34 | 30 |  |  | 42853.1667 | 54 | 44
2017-04-28 04:30 | 35 | 31 |  |  | 42853.1875 | 54 | 44
2017-04-28 05:00 | 36 | 32 |  |  | 42853.2083 | 56 | 47
2017-04-28 05:30 | 43 | 39 |  |  | 42853.2292 | 61 | 54
2017-04-28 06:00 | 49 | 45 |  |  | 42853.25 | 69 | 63
2017-04-28 06:30 | 58 | 54 |  |  | 42853.2708 | 79 | 76
2017-04-28 07:00 | 67 | 61 |  |  | 42853.2917 | 87 | 85
2017-04-28 07:30 | 66 | 61 |  |  | 42853.3125 | 93 | 89
2017-04-28 08:00 | 63 | 58 |  |  | 42853.3333 | 91 | 87
2017-04-28 08:30 | 64 | 58 |  |  | 42853.3542 | 91 | 87
2017-04-28 09:00 | 61 | 56 |  |  | 42853.375 | 89 | 85
2017-04-28 09:30 | 55 | 53 |  |  | 42853.3958 | 87 | 81
2017-04-28 10:00 | 55 | 53 |  |  | 42853.4167 | 86 | 80
2017-04-28 10:30 | 53 | 51 |  |  | 42853.4375 | 82 | 76
2017-04-28 11:00 | 53 | 51 |  |  | 42853.4583 | 81 | 76
2017-04-28 11:30 | 55 | 52 |  |  | 42853.4792 | 81 | 76
2017-04-28 12:00 | 54 | 51 |  |  | 42853.5 | 82 | 77
2017-04-28 12:30 | 53 | 50 |  |  | 42853.5208 | 82 | 77
2017-04-28 13:00 | 57 | 54 |  |  | 42853.5417 | 87 | 82
2017-04-28 13:30 | 59 | 57 |  |  | 42853.5625 | 87 | 82
2017-04-28 14:00 | 61 | 59 |  |  | 42853.5833 | 90 | 85
2017-04-28 14:30 | 57 | 55 |  |  | 42853.6042 | 88 | 83
2017-04-28 15:00 | 57 | 55 |  |  | 42853.625 | 88 | 83
2017-04-28 15:30 | 59 | 58 |  |  | 42853.6458 | 90 | 84
2017-04-28 16:00 | 60 | 58 |  |  | 42853.6667 | 91 | 86
2017-04-28 16:30 | 61 | 60 |  |  | 42853.6875 | 93 | 87
2017-04-28 17:00 | 62 | 61 |  |  | 42853.7083 | 95 | 88
2017-04-28 17:30 | 61 | 60 |  |  | 42853.7292 | 95 | 87
2017-04-28 18:00 | 60 | 60 |  |  | 42853.75 | 96 | 85
2017-04-28 18:30 | 59 | 59 |  |  | 42853.7708 | 97 | 82
2017-04-28 19:00 | 61 | 61 |  |  | 42853.7917 | 98 | 85
2017-04-28 19:30 | 58 | 58 |  |  | 42853.8125 | 97 | 82
2017-04-28 20:00 | 58 | 58 |  |  | 42853.8333 | 93 | 81
2017-04-28 20:30 | 58 | 57 |  |  | 42853.8542 | 89 | 80
2017-04-28 21:00 | 55 | 53 |  |  | 42853.875 | 81 | 74
2017-04-28 21:30 | 53 | 51 |  |  | 42853.8958 | 78 | 72
2017-04-28 22:00 | 50 | 49 |  |  | 42853.9167 | 76 | 70
2017-04-28 22:30 | 51 | 49 |  |  | 42853.9375 | 75 | 69
2017-04-28 23:00 | 51 | 50 |  |  | 42853.9583 | 75 | 68
2017-04-28 23:30 | 48 | 47 |  |  | 42853.9792 | 72 | 64
2017-04-29 | 43 | 42 |  |  | 42854 | 67 | 58
2017-04-29 00:30 | 38 | 37 |  |  | 42854.0208 | 62 | 53
2017-04-29 01:00 | 35 | 34 |  |  | 42854.0417 | 59 | 48
2017-04-29 01:30 | 33 | 32 |  |  | 42854.0625 | 57 | 46
2017-04-29 02:00 | 30 | 29 |  |  | 42854.0833 | 56 | 44
2017-04-29 02:30 | 29 | 28 |  |  | 42854.1042 | 54 | 41
2017-04-29 03:00 | 28 | 27 |  |  | 42854.125 | 53 | 40
2017-04-29 03:30 | 28 | 27 |  |  | 42854.1458 | 53 | 40
2017-04-29 04:00 | 28 | 26 |  |  | 42854.1667 | 53 | 40
2017-04-29 04:30 | 27 | 26 |  |  | 42854.1875 | 53 | 41
2017-04-29 05:00 | 30 | 28 |  |  | 42854.2083 | 54 | 41
2017-04-29 05:30 | 31 | 29 |  |  | 42854.2292 | 56 | 44
2017-04-29 06:00 | 33 | 32 |  |  | 42854.25 | 58 | 46
2017-04-29 06:30 | 34 | 33 |  |  | 42854.2708 | 58 | 49
2017-04-29 07:00 | 35 | 34 |  |  | 42854.2917 | 60 | 51
2017-04-29 07:30 | 38 | 37 |  |  | 42854.3125 | 63 | 54
2017-04-29 08:00 | 42 | 40 |  |  | 42854.3333 | 67 | 59
2017-04-29 08:30 | 41 | 39 |  |  | 42854.3542 | 66 | 60
2017-04-29 09:00 | 43 | 41 |  |  | 42854.375 | 67 | 61
2017-04-29 09:30 | 44 | 42 |  |  | 42854.3958 | 68 | 62
2017-04-29 10:00 | 42 | 40 |  |  | 42854.4167 | 65 | 60
2017-04-29 10:30 | 42 | 39 |  |  | 42854.4375 | 64 | 58
2017-04-29 11:00 | 42 | 39 |  |  | 42854.4583 | 62 | 57
2017-04-29 11:30 | 40 | 37 |  |  | 42854.4792 | 60 | 55
2017-04-29 12:00 | 40 | 38 |  |  | 42854.5 | 60 | 55
2017-04-29 12:30 | 39 | 36 |  |  | 42854.5208 | 59 | 54
2017-04-29 13:00 | 39 | 37 |  |  | 42854.5417 | 60 | 54
2017-04-29 13:30 | 41 | 39 |  |  | 42854.5625 | 62 | 57
2017-04-29 14:00 | 44 | 42 |  |  | 42854.5833 | 63 | 58
2017-04-29 14:30 | 44 | 42 |  |  | 42854.6042 | 63 | 58
2017-04-29 15:00 | 45 | 43 |  |  | 42854.625 | 65 | 60
2017-04-29 15:30 | 47 | 44 |  |  | 42854.6458 | 68 | 63
2017-04-29 16:00 | 51 | 49 |  |  | 42854.6667 | 73 | 68
2017-04-29 16:30 | 54 | 52 |  |  | 42854.6875 | 77 | 72
2017-04-29 17:00 | 56 | 55 |  |  | 42854.7083 | 80 | 75
2017-04-29 17:30 | 56 | 55 |  |  | 42854.7292 | 81 | 76
2017-04-29 18:00 | 57 | 56 |  |  | 42854.75 | 82 | 77
2017-04-29 18:30 | 58 | 57 |  |  | 42854.7708 | 83 | 78
2017-04-29 19:00 | 58 | 57 |  |  | 42854.7917 | 83 | 78
2017-04-29 19:30 | 56 | 55 |  |  | 42854.8125 | 81 | 76
2017-04-29 20:00 | 54 | 53 |  |  | 42854.8333 | 79 | 74
2017-04-29 20:30 | 54 | 53 |  |  | 42854.8542 | 80 | 74
2017-04-29 21:00 | 52 | 51 |  |  | 42854.875 | 76 | 71
2017-04-29 21:30 | 50 | 49 |  |  | 42854.8958 | 74 | 68
2017-04-29 22:00 | 50 | 49 |  |  | 42854.9167 | 75 | 68
2017-04-29 22:30 | 50 | 49 |  |  | 42854.9375 | 76 | 69
2017-04-29 23:00 | 52 | 51 |  |  | 42854.9583 | 76 | 68
2017-04-29 23:30 | 48 | 47 |  |  | 42854.9792 | 72 | 65
2017-04-30 | 44 | 43 |  |  | 42855 | 68 | 59
2017-04-30 00:30 | 40 | 39 |  |  | 42855.0208 | 64 | 55
2017-04-30 01:00 | 38 | 37 |  |  | 42855.0417 | 62 | 51
2017-04-30 01:30 | 35 | 34 |  |  | 42855.0625 | 60 | 48
2017-04-30 02:00 | 33 | 32 |  |  | 42855.0833 | 58 | 46
2017-04-30 02:30 | 34 | 33 |  |  | 42855.1042 | 57 | 45
2017-04-30 03:00 | 33 | 32 |  |  | 42855.125 | 56 | 44
2017-04-30 03:30 | 33 | 32 |  |  | 42855.1458 | 56 | 44
2017-04-30 04:00 | 33 | 32 |  |  | 42855.1667 | 55 | 43
2017-04-30 04:30 | 34 | 33 |  |  | 42855.1875 | 55 | 44
2017-04-30 05:00 | 35 | 33 |  |  | 42855.2083 | 54 | 45
2017-04-30 05:30 | 35 | 33 |  |  | 42855.2292 | 56 | 46
2017-04-30 06:00 | 35 | 33 |  |  | 42855.25 | 56 | 48
2017-04-30 06:30 | 36 | 35 |  |  | 42855.2708 | 59 | 50
2017-04-30 07:00 | 37 | 35 |  |  | 42855.2917 | 60 | 52
2017-04-30 07:30 | 38 | 36 |  |  | 42855.3125 | 61 | 54
2017-04-30 08:00 | 39 | 38 |  |  | 42855.3333 | 61 | 55
2017-04-30 08:30 | 39 | 38 |  |  | 42855.3542 | 62 | 56
2017-04-30 09:00 | 41 | 39 |  |  | 42855.375 | 63 | 57
2017-04-30 09:30 | 41 | 39 |  |  | 42855.3958 | 62 | 57
2017-04-30 10:00 | 41 | 38 |  |  | 42855.4167 | 62 | 56
2017-04-30 10:30 | 42 | 40 |  |  | 42855.4375 | 61 | 56
2017-04-30 11:00 | 42 | 39 |  |  | 42855.4583 | 61 | 56
2017-04-30 11:30 | 42 | 40 |  |  | 42855.4792 | 61 | 56
2017-04-30 12:00 | 39 | 39 |  |  | 42855.5 | 60 | 56
2017-04-30 12:30 | 42 | 40 |  |  | 42855.5208 | 60 | 56
2017-04-30 13:00 | 42 | 40 |  |  | 42855.5417 | 61 | 58
2017-04-30 13:30 | 43 | 41 |  |  | 42855.5625 | 62 | 59
2017-04-30 14:00 | 46 | 44 |  |  | 42855.5833 | 65 | 61
2017-04-30 14:30 | 46 | 44 |  |  | 42855.6042 | 64 | 61
2017-04-30 15:00 | 48 | 46 |  |  | 42855.625 | 66 | 63
2017-04-30 15:30 | 50 | 48 |  |  | 42855.6458 | 68 | 65
2017-04-30 16:00 | 51 | 49 |  |  | 42855.6667 | 70 | 67
2017-04-30 16:30 | 51 | 49 |  |  | 42855.6875 | 73 | 69
2017-04-30 17:00 | 56 | 53 |  |  | 42855.7083 | 77 | 73
2017-04-30 17:30 | 58 | 56 |  |  | 42855.7292 | 78 | 74
2017-04-30 18:00 | 62 | 60 |  |  | 42855.75 | 82 | 77
2017-04-30 18:30 | 64 | 60 |  |  | 42855.7708 | 84 | 78
2017-04-30 19:00 | 64 | 60 |  |  | 42855.7917 | 86 | 79
2017-04-30 19:30 | 63 | 59 |  |  | 42855.8125 | 83 | 76
2017-04-30 20:00 | 60 | 56 |  |  | 42855.8333 | 81 | 73
2017-04-30 20:30 | 58 | 54 |  |  | 42855.8542 | 80 | 73
2017-04-30 21:00 | 55 | 52 |  |  | 42855.875 | 75 | 68
2017-04-30 21:30 | 52 | 48 |  |  | 42855.8958 | 73 | 66
2017-04-30 22:00 | 52 | 48 |  |  | 42855.9167 | 73 | 66
2017-04-30 22:30 | 53 | 49 |  |  | 42855.9375 | 74 | 66
2017-04-30 23:00 | 54 | 49 |  |  | 42855.9583 | 73 | 66
2017-04-30 23:30 | 51 | 46 |  |  | 42855.9792 | 70 | 62
2017-05-01 | 48 | 43 |  |  | 42856 | 66 | 57
2017-05-01 00:30 | 44 | 39 |  |  | 42856.0208 | 62 | 52
2017-05-01 01:00 | 42 | 37 |  |  | 42856.0417 | 59 | 50
2017-05-01 01:30 | 41 | 36 |  |  | 42856.0625 | 58 | 49
2017-05-01 02:00 | 40 | 34 |  |  | 42856.0833 | 57 | 48
2017-05-01 02:30 | 39 | 34 |  |  | 42856.1042 | 56 | 47
2017-05-01 03:00 | 40 | 34 |  |  | 42856.125 | 54 | 45
2017-05-01 03:30 | 39 | 33 |  |  | 42856.1458 | 54 | 45
2017-05-01 04:00 | 40 | 35 |  |  | 42856.1667 | 55 | 46
2017-05-01 04:30 | 41 | 36 |  |  | 42856.1875 | 56 | 47
2017-05-01 05:00 | 41 | 36 |  |  | 42856.2083 | 56 | 47
2017-05-01 05:30 | 42 | 37 |  |  | 42856.2292 | 57 | 48
2017-05-01 06:00 | 43 | 38 |  |  | 42856.25 | 61 | 52
2017-05-01 06:30 | 43 | 37 |  |  | 42856.2708 | 62 | 54
2017-05-01 07:00 | 43 | 38 |  |  | 42856.2917 | 63 | 55
2017-05-01 07:30 | 44 | 39 |  |  | 42856.3125 | 65 | 58
2017-05-01 08:00 | 45 | 41 |  |  | 42856.3333 | 66 | 60
2017-05-01 08:30 | 46 | 42 |  |  | 42856.3542 | 67 | 61
2017-05-01 09:00 | 46 | 42 |  |  | 42856.375 | 67 | 62
2017-05-01 09:30 | 45 | 41 |  |  | 42856.3958 | 66 | 61
2017-05-01 10:00 | 44 | 40 |  |  | 42856.4167 | 65 | 60
2017-05-01 10:30 | 44 | 41 |  |  | 42856.4375 | 65 | 61
2017-05-01 11:00 | 43 | 40 |  |  | 42856.4583 | 64 | 60
2017-05-01 11:30 | 45 | 42 |  |  | 42856.4792 | 65 | 62
2017-05-01 12:00 | 46 | 43 |  |  | 42856.5 | 66 | 62
2017-05-01 12:30 | 45 | 42 |  |  | 42856.5208 | 66 | 63
2017-05-01 13:00 | 44 | 42 |  |  | 42856.5417 | 68 | 64
2017-05-01 13:30 | 47 | 44 |  |  | 42856.5625 | 69 | 65
2017-05-01 14:00 | 47 | 45 |  |  | 42856.5833 | 70 | 66
2017-05-01 14:30 | 48 | 45 |  |  | 42856.6042 | 70 | 66
2017-05-01 15:00 | 50 | 47 |  |  | 42856.625 | 71 | 68
2017-05-01 15:30 | 50 | 48 |  |  | 42856.6458 | 73 | 70
2017-05-01 16:00 | 52 | 50 |  |  | 42856.6667 | 76 | 72
2017-05-01 16:30 | 54 | 52 |  |  | 42856.6875 | 80 | 76
2017-05-01 17:00 | 57 | 55 |  |  | 42856.7083 | 82 | 79
2017-05-01 17:30 | 61 | 59 |  |  | 42856.7292 | 86 | 82
2017-05-01 18:00 | 64 | 62 |  |  | 42856.75 | 89 | 85
2017-05-01 18:30 | 64 | 62 |  |  | 42856.7708 | 89 | 85
2017-05-01 19:00 | 63 | 60 |  |  | 42856.7917 | 88 | 83
2017-05-01 19:30 | 62 | 60 |  |  | 42856.8125 | 86 | 81
2017-05-01 20:00 | 61 | 58 |  |  | 42856.8333 | 85 | 80
2017-05-01 20:30 | 60 | 57 |  |  | 42856.8542 | 85 | 79
2017-05-01 21:00 | 59 | 56 |  |  | 42856.875 | 82 | 77
2017-05-01 21:30 | 56 | 53 |  |  | 42856.8958 | 78 | 72
2017-05-01 22:00 | 54 | 50 |  |  | 42856.9167 | 77 | 71
2017-05-01 22:30 | 54 | 51 |  |  | 42856.9375 | 77 | 71
2017-05-01 23:00 | 53 | 49 |  |  | 42856.9583 | 76 | 68
2017-05-01 23:30 | 49 | 45 |  |  | 42856.9792 | 72 | 64
2017-05-02 | 46 | 40 |  |  | 42857 | 67 | 59
2017-05-02 00:30 | 44 | 38 |  |  | 42857.0208 | 64 | 55
2017-05-02 01:00 | 43 | 38 |  |  | 42857.0417 | 62 | 54
2017-05-02 01:30 | 41 | 35 |  |  | 42857.0625 | 60 | 52
2017-05-02 02:00 | 41 | 35 |  |  | 42857.0833 | 58 | 50
2017-05-02 02:30 | 39 | 34 |  |  | 42857.1042 | 57 | 49
2017-05-02 03:00 | 39 | 34 |  |  | 42857.125 | 57 | 48
2017-05-02 03:30 | 38 | 32 |  |  | 42857.1458 | 55 | 46
2017-05-02 04:00 | 38 | 32 |  |  | 42857.1667 | 54 | 45
2017-05-02 04:30 | 38 | 33 |  |  | 42857.1875 | 55 | 46
2017-05-02 05:00 | 40 | 36 |  |  | 42857.2083 | 58 | 51
2017-05-02 05:30 | 43 | 41 |  |  | 42857.2292 | 62 | 55
2017-05-02 06:00 | 48 | 47 |  |  | 42857.25 | 68 | 63
2017-05-02 06:30 | 57 | 56 |  |  | 42857.2708 | 78 | 75
2017-05-02 07:00 | 64 | 63 |  |  | 42857.2917 | 87 | 83
2017-05-02 07:30 | 66 | 65 |  |  | 42857.3125 | 92 | 89
2017-05-02 08:00 | 67 | 67 |  |  | 42857.3333 | 94 | 91
2017-05-02 08:30 | 68 | 67 |  |  | 42857.3542 | 95 | 92
2017-05-02 09:00 | 64 | 63 |  |  | 42857.375 | 93 | 90
2017-05-02 09:30 | 61 | 60 |  |  | 42857.3958 | 91 | 86
2017-05-02 10:00 | 61 | 59 |  |  | 42857.4167 | 90 | 85
2017-05-02 10:30 | 62 | 61 |  |  | 42857.4375 | 90 | 86
2017-05-02 11:00 | 61 | 60 |  |  | 42857.4583 | 90 | 86
2017-05-02 11:30 | 62 | 61 |  |  | 42857.4792 | 91 | 87
2017-05-02 12:00 | 64 | 63 |  |  | 42857.5 | 94 | 90
2017-05-02 12:30 | 64 | 63 |  |  | 42857.5208 | 94 | 89
2017-05-02 13:00 | 63 | 62 |  |  | 42857.5417 | 93 | 89
2017-05-02 13:30 | 64 | 63 |  |  | 42857.5625 | 93 | 89
2017-05-02 14:00 | 64 | 63 |  |  | 42857.5833 | 95 | 91
2017-05-02 14:30 | 67 | 66 |  |  | 42857.6042 | 98 | 93
2017-05-02 15:00 | 67 | 66 |  |  | 42857.625 | 99 | 94
2017-05-02 15:30 | 70 | 68 |  |  | 42857.6458 | 101 | 96
2017-05-02 16:00 | 70 | 69 |  |  | 42857.6667 | 102 | 97
2017-05-02 16:30 | 71 | 70 |  |  | 42857.6875 | 104 | 98
2017-05-02 17:00 | 73 | 71 |  |  | 42857.7083 | 105 | 99
2017-05-02 17:30 | 73 | 72 |  |  | 42857.7292 | 105 | 99
2017-05-02 18:00 | 73 | 71 |  |  | 42857.75 | 104 | 97
2017-05-02 18:30 | 71 | 69 |  |  | 42857.7708 | 101 | 94
2017-05-02 19:00 | 73 | 70 |  |  | 42857.7917 | 102 | 95
2017-05-02 19:30 | 72 | 70 |  |  | 42857.8125 | 100 | 94
2017-05-02 20:00 | 69 | 67 |  |  | 42857.8333 | 97 | 91
2017-05-02 20:30 | 68 | 67 |  |  | 42857.8542 | 91 | 90
2017-05-02 21:00 | 67 | 65 |  |  | 42857.875 | 88 | 88
2017-05-02 21:30 | 65 | 62 |  |  | 42857.8958 | 83 | 82
2017-05-02 22:00 | 62 | 57 |  |  | 42857.9167 | 80 | 80
2017-05-02 22:30 | 61 | 57 |  |  | 42857.9375 | 80 | 79
2017-05-02 23:00 | 59 | 55 |  |  | 42857.9583 | 75 | 75
2017-05-02 23:30 | 56 | 51 |  |  | 42857.9792 | 71 | 70
2017-05-03 | 51 | 45 |  |  | 42858 | 63 | 63
2017-05-03 00:30 | 48 | 41 |  |  | 42858.0208 | 59 | 58
2017-05-03 01:00 | 46 | 39 |  |  | 42858.0417 | 57 | 56
2017-05-03 01:30 | 45 | 37 |  |  | 42858.0625 | 54 | 54
2017-05-03 02:00 | 43 | 35 |  |  | 42858.0833 | 52 | 51
2017-05-03 02:30 | 43 | 36 |  |  | 42858.1042 | 52 | 51
2017-05-03 03:00 | 43 | 35 |  |  | 42858.125 | 51 | 50
2017-05-03 03:30 | 43 | 35 |  |  | 42858.1458 | 51 | 51
2017-05-03 04:00 | 43 | 35 |  |  | 42858.1667 | 51 | 50
2017-05-03 04:30 | 44 | 37 |  |  | 42858.1875 | 53 | 52
2017-05-03 05:00 | 46 | 39 |  |  | 42858.2083 | 56 | 55
2017-05-03 05:30 | 50 | 45 |  |  | 42858.2292 | 62 | 61
2017-05-03 06:00 | 55 | 51 |  |  | 42858.25 | 70 | 70
2017-05-03 06:30 | 63 | 61 |  |  | 42858.2708 | 81 | 81
2017-05-03 07:00 | 69 | 68 |  |  | 42858.2917 | 90 | 90
2017-05-03 07:30 | 74 | 73 |  |  | 42858.3125 | 97 | 97
2017-05-03 08:00 | 76 | 72 |  |  | 42858.3333 | 99 | 96
2017-05-03 08:30 | 76 | 71 |  |  | 42858.3542 | 100 | 97
2017-05-03 09:00 | 74 | 68 |  |  | 42858.375 | 100 | 95
2017-05-03 09:30 | 71 | 64 |  |  | 42858.3958 | 97 | 92
2017-05-03 10:00 | 71 | 64 |  |  | 42858.4167 | 96 | 92
2017-05-03 10:30 | 71 | 65 |  |  | 42858.4375 | 96 | 91
2017-05-03 11:00 | 71 | 65 |  |  | 42858.4583 | 96 | 91
2017-05-03 11:30 | 72 | 66 |  |  | 42858.4792 | 96 | 92
2017-05-03 12:00 | 69 | 63 |  |  | 42858.5 | 97 | 93
2017-05-03 12:30 | 70 | 64 |  |  | 42858.5208 | 99 | 94
2017-05-03 13:00 | 71 | 65 |  |  | 42858.5417 | 99 | 94
2017-05-03 13:30 | 74 | 69 |  |  | 42858.5625 | 102 | 98
2017-05-03 14:00 | 76 | 71 |  |  | 42858.5833 | 104 | 99
2017-05-03 14:30 | 76 | 71 |  |  | 42858.6042 | 103 | 99
2017-05-03 15:00 | 77 | 72 |  |  | 42858.625 | 103 | 98
2017-05-03 15:30 | 74 | 68 |  |  | 42858.6458 | 100 | 95
2017-05-03 16:00 | 74 | 68 |  |  | 42858.6667 | 100 | 95
2017-05-03 16:30 | 75 | 69 |  |  | 42858.6875 | 101 | 96
2017-05-03 17:00 | 77 | 71 |  |  | 42858.7083 | 104 | 98
2017-05-03 17:30 | 78 | 71 |  |  | 42858.7292 | 103 | 97
2017-05-03 18:00 | 80 | 73 |  |  | 42858.75 | 103 | 96
2017-05-03 18:30 | 78 | 72 |  |  | 42858.7708 | 98 | 93
2017-05-03 19:00 | 77 | 73 |  |  | 42858.7917 | 96 | 94
2017-05-03 19:30 | 74 | 71 |  |  | 42858.8125 | 92 | 91
2017-05-03 20:00 | 69 | 67 |  |  | 42858.8333 | 88 | 88
2017-05-03 20:30 | 68 | 66 |  |  | 42858.8542 | 87 | 87
2017-05-03 21:00 | 64 | 63 |  |  | 42858.875 | 83 | 83
2017-05-03 21:30 | 60 | 59 |  |  | 42858.8958 | 79 | 79
2017-05-03 22:00 | 58 | 56 |  |  | 42858.9167 | 78 | 78
2017-05-03 22:30 | 56 | 54 |  |  | 42858.9375 | 75 | 75
2017-05-03 23:00 | 54 | 52 |  |  | 42858.9583 | 71 | 71
2017-05-03 23:30 | 51 | 47 |  |  | 42858.9792 | 66 | 66
2017-05-04 | 46 | 42 |  |  | 42859 | 59 | 59
2017-05-04 00:30 | 43 | 38 |  |  | 42859.0208 | 55 | 55
2017-05-04 01:00 | 41 | 35 |  |  | 42859.0417 | 50 | 50
2017-05-04 01:30 | 40 | 34 |  |  | 42859.0625 | 49 | 49
2017-05-04 02:00 | 37 | 29 |  |  | 42859.0833 | 46 | 46
2017-05-04 02:30 | 38 | 30 |  |  | 42859.1042 | 46 | 46
2017-05-04 03:00 | 39 | 32 |  |  | 42859.125 | 47 | 47
2017-05-04 03:30 | 39 | 31 |  |  | 42859.1458 | 48 | 48
2017-05-04 04:00 | 39 | 32 |  |  | 42859.1667 | 48 | 48
2017-05-04 04:30 | 41 | 34 |  |  | 42859.1875 | 50 | 50
2017-05-04 05:00 | 43 | 37 |  |  | 42859.2083 | 53 | 53
2017-05-04 05:30 | 47 | 42 |  |  | 42859.2292 | 58 | 58
2017-05-04 06:00 | 52 | 49 |  |  | 42859.25 | 67 | 67
2017-05-04 06:30 | 57 | 55 |  |  | 42859.2708 | 76 | 76
2017-05-04 07:00 | 60 | 59 |  |  | 42859.2917 | 83 | 83
2017-05-04 07:30 | 65 | 64 |  |  | 42859.3125 | 89 | 89
2017-05-04 08:00 | 66 | 64 |  |  | 42859.3333 | 91 | 91
2017-05-04 08:30 | 66 | 65 |  |  | 42859.3542 | 92 | 92
2017-05-04 09:00 | 67 | 65 |  |  | 42859.375 | 93 | 93
2017-05-04 09:30 | 64 | 63 |  |  | 42859.3958 | 91 | 90
2017-05-04 10:00 | 67 | 66 |  |  | 42859.4167 | 94 | 94
2017-05-04 10:30 | 68 | 67 |  |  | 42859.4375 | 96 | 96
2017-05-04 11:00 | 69 | 68 |  |  | 42859.4583 | 93 | 93
2017-05-04 11:30 | 68 | 68 |  |  | 42859.4792 | 94 | 94
2017-05-04 12:00 | 68 | 68 |  |  | 42859.5 | 95 | 95
2017-05-04 12:30 | 69 | 68 |  |  | 42859.5208 | 96 | 96
2017-05-04 13:00 | 69 | 68 |  |  | 42859.5417 | 93 | 93
2017-05-04 13:30 | 67 | 66 |  |  | 42859.5625 | 92 | 92
2017-05-04 14:00 | 67 | 66 |  |  | 42859.5833 | 93 | 93
2017-05-04 14:30 | 68 | 67 |  |  | 42859.6042 | 94 | 94
2017-05-04 15:00 | 68 | 67 |  |  | 42859.625 | 94 | 94
2017-05-04 15:30 | 67 | 65 |  |  | 42859.6458 | 94 | 94
2017-05-04 16:00 | 70 | 68 |  |  | 42859.6667 | 95 | 95
2017-05-04 16:30 | 70 | 68 |  |  | 42859.6875 | 96 | 96
2017-05-04 17:00 | 72 | 70 |  |  | 42859.7083 | 97 | 97
2017-05-04 17:30 | 72 | 70 |  |  | 42859.7292 | 97 | 97
2017-05-04 18:00 | 71 | 69 |  |  | 42859.75 | 95 | 95
2017-05-04 18:30 | 71 | 66 |  |  | 42859.7708 | 92 | 90
2017-05-04 19:00 | 72 | 67 |  |  | 42859.7917 | 94 | 92
2017-05-04 19:30 | 73 | 68 |  |  | 42859.8125 | 93 | 91
2017-05-04 20:00 | 71 | 67 |  |  | 42859.8333 | 91 | 90
2017-05-04 20:30 | 69 | 65 |  |  | 42859.8542 | 89 | 87
2017-05-04 21:00 | 64 | 61 |  |  | 42859.875 | 83 | 82
2017-05-04 21:30 | 59 | 55 |  |  | 42859.8958 | 78 | 78
2017-05-04 22:00 | 59 | 55 |  |  | 42859.9167 | 79 | 78
2017-05-04 22:30 | 59 | 54 |  |  | 42859.9375 | 75 | 74
2017-05-04 23:00 | 59 | 53 |  |  | 42859.9583 | 72 | 71
2017-05-04 23:30 | 54 | 48 |  |  | 42859.9792 | 68 | 67
2017-05-05 | 50 | 43 |  |  | 42860 | 63 | 61
2017-05-05 00:30 | 49 | 40 |  |  | 42860.0208 | 59 | 58
2017-05-05 01:00 | 48 | 39 |  |  | 42860.0417 | 57 | 55
2017-05-05 01:30 | 47 | 37 |  |  | 42860.0625 | 54 | 53
2017-05-05 02:00 | 45 | 35 |  |  | 42860.0833 | 52 | 49
2017-05-05 02:30 | 46 | 36 |  |  | 42860.1042 | 52 | 50
2017-05-05 03:00 | 45 | 35 |  |  | 42860.125 | 51 | 49
2017-05-05 03:30 | 46 | 36 |  |  | 42860.1458 | 52 | 50
2017-05-05 04:00 | 45 | 36 |  |  | 42860.1667 | 52 | 50
2017-05-05 04:30 | 45 | 36 |  |  | 42860.1875 | 52 | 50
2017-05-05 05:00 | 48 | 39 |  |  | 42860.2083 | 56 | 54
2017-05-05 05:30 | 50 | 43 |  |  | 42860.2292 | 60 | 59
2017-05-05 06:00 | 56 | 50 |  |  | 42860.25 | 68 | 68
2017-05-05 06:30 | 60 | 55 |  |  | 42860.2708 | 76 | 76
2017-05-05 07:00 | 65 | 60 |  |  | 42860.2917 | 86 | 84
2017-05-05 07:30 | 66 | 63 |  |  | 42860.3125 | 91 | 90
2017-05-05 08:00 | 64 | 63 |  |  | 42860.3333 | 91 | 91
2017-05-05 08:30 | 65 | 64 |  |  | 42860.3542 | 93 | 93
2017-05-05 09:00 | 64 | 63 |  |  | 42860.375 | 92 | 92
2017-05-05 09:30 | 63 | 62 |  |  | 42860.3958 | 90 | 90
2017-05-05 10:00 | 64 | 63 |  |  | 42860.4167 | 90 | 90
2017-05-05 10:30 | 65 | 65 |  |  | 42860.4375 | 92 | 92
2017-05-05 11:00 | 68 | 67 |  |  | 42860.4583 | 94 | 94
2017-05-05 11:30 | 65 | 65 |  |  | 42860.4792 | 92 | 92
2017-05-05 12:00 | 64 | 64 |  |  | 42860.5 | 89 | 89
2017-05-05 12:30 | 63 | 62 |  |  | 42860.5208 | 88 | 88
2017-05-05 13:00 | 64 | 63 |  |  | 42860.5417 | 90 | 90
2017-05-05 13:30 | 64 | 63 |  |  | 42860.5625 | 90 | 90
2017-05-05 14:00 | 65 | 65 |  |  | 42860.5833 | 89 | 89
2017-05-05 14:30 | 63 | 63 |  |  | 42860.6042 | 89 | 89
2017-05-05 15:00 | 64 | 64 |  |  | 42860.625 | 89 | 89
2017-05-05 15:30 | 64 | 63 |  |  | 42860.6458 | 90 | 90
2017-05-05 16:00 | 65 | 64 |  |  | 42860.6667 | 90 | 90
2017-05-05 16:30 | 65 | 65 |  |  | 42860.6875 | 92 | 92
2017-05-05 17:00 | 68 | 66 |  |  | 42860.7083 | 93 | 92
2017-05-05 17:30 | 67 | 65 |  |  | 42860.7292 | 91 | 89
2017-05-05 18:00 | 66 | 64 |  |  | 42860.75 | 90 | 89
2017-05-05 18:30 | 64 | 61 |  |  | 42860.7708 | 86 | 84
2017-05-05 19:00 | 66 | 63 |  |  | 42860.7917 | 87 | 86
2017-05-05 19:30 | 65 | 62 |  |  | 42860.8125 | 84 | 83
2017-05-05 20:00 | 62 | 58 |  |  | 42860.8333 | 81 | 79
2017-05-05 20:30 | 62 | 58 |  |  | 42860.8542 | 81 | 80
2017-05-05 21:00 | 61 | 53 |  |  | 42860.875 | 76 | 73
2017-05-05 21:30 | 61 | 51 |  |  | 42860.8958 | 72 | 69
2017-05-05 22:00 | 59 | 48 |  |  | 42860.9167 | 71 | 67
2017-05-05 22:30 | 61 | 49 |  |  | 42860.9375 | 73 | 69
2017-05-05 23:00 | 63 | 51 |  |  | 42860.9583 | 73 | 69
2017-05-05 23:30 | 62 | 48 |  |  | 42860.9792 | 71 | 66
2017-05-06 | 59 | 44 |  |  | 42861 | 66 | 61
2017-05-06 00:30 | 57 | 41 |  |  | 42861.0208 | 62 | 56
2017-05-06 01:00 | 55 | 36 |  |  | 42861.0417 | 59 | 52
2017-05-06 01:30 | 54 | 34 |  |  | 42861.0625 | 57 | 49
2017-05-06 02:00 | 53 | 32 |  |  | 42861.0833 | 54 | 47
2017-05-06 02:30 | 52 | 32 |  |  | 42861.1042 | 54 | 46
2017-05-06 03:00 | 52 | 30 |  |  | 42861.125 | 52 | 44
2017-05-06 03:30 | 51 | 30 |  |  | 42861.1458 | 52 | 43
2017-05-06 04:00 | 51 | 30 |  |  | 42861.1667 | 51 | 43
2017-05-06 04:30 | 52 | 31 |  |  | 42861.1875 | 51 | 43
2017-05-06 05:00 | 52 | 32 |  |  | 42861.2083 | 52 | 44
2017-05-06 05:30 | 53 | 34 |  |  | 42861.2292 | 55 | 47
2017-05-06 06:00 | 53 | 37 |  |  | 42861.25 | 57 | 50
2017-05-06 06:30 | 54 | 37 |  |  | 42861.2708 | 58 | 52
2017-05-06 07:00 | 56 | 41 |  |  | 42861.2917 | 62 | 57
2017-05-06 07:30 | 56 | 42 |  |  | 42861.3125 | 65 | 60
2017-05-06 08:00 | 55 | 42 |  |  | 42861.3333 | 65 | 61
2017-05-06 08:30 | 56 | 44 |  |  | 42861.3542 | 67 | 63
2017-05-06 09:00 | 56 | 45 |  |  | 42861.375 | 68 | 64
2017-05-06 09:30 | 57 | 46 |  |  | 42861.3958 | 67 | 64
2017-05-06 10:00 | 55 | 44 |  |  | 42861.4167 | 66 | 63
2017-05-06 10:30 | 55 | 43 |  |  | 42861.4375 | 65 | 62
2017-05-06 11:00 | 57 | 46 |  |  | 42861.4583 | 67 | 65
2017-05-06 11:30 | 55 | 44 |  |  | 42861.4792 | 64 | 62
2017-05-06 12:00 | 54 | 43 |  |  | 42861.5 | 65 | 62
2017-05-06 12:30 | 54 | 42 |  |  | 42861.5208 | 63 | 60
2017-05-06 13:00 | 52 | 39 |  |  | 42861.5417 | 58 | 55
2017-05-06 13:30 | 52 | 39 |  |  | 42861.5625 | 59 | 57
2017-05-06 14:00 | 54 | 43 |  |  | 42861.5833 | 61 | 59
2017-05-06 14:30 | 54 | 42 |  |  | 42861.6042 | 62 | 60
2017-05-06 15:00 | 55 | 42 |  |  | 42861.625 | 64 | 62
2017-05-06 15:30 | 56 | 45 |  |  | 42861.6458 | 66 | 64
2017-05-06 16:00 | 60 | 49 |  |  | 42861.6667 | 70 | 68
2017-05-06 16:30 | 61 | 50 |  |  | 42861.6875 | 72 | 69
2017-05-06 17:00 | 65 | 55 |  |  | 42861.7083 | 78 | 75
2017-05-06 17:30 | 66 | 55 |  |  | 42861.7292 | 79 | 77
2017-05-06 18:00 | 64 | 56 |  |  | 42861.75 | 80 | 77
2017-05-06 18:30 | 65 | 56 |  |  | 42861.7708 | 80 | 77
2017-05-06 19:00 | 67 | 59 |  |  | 42861.7917 | 82 | 79
2017-05-06 19:30 | 66 | 57 |  |  | 42861.8125 | 80 | 77
2017-05-06 20:00 | 64 | 55 |  |  | 42861.8333 | 78 | 75
2017-05-06 20:30 | 62 | 54 |  |  | 42861.8542 | 77 | 75
2017-05-06 21:00 | 60 | 52 |  |  | 42861.875 | 74 | 71
2017-05-06 21:30 | 57 | 49 |  |  | 42861.8958 | 69 | 66
2017-05-06 22:00 | 58 | 49 |  |  | 42861.9167 | 70 | 67
2017-05-06 22:30 | 58 | 49 |  |  | 42861.9375 | 71 | 68
2017-05-06 23:00 | 59 | 50 |  |  | 42861.9583 | 70 | 67
2017-05-06 23:30 | 57 | 47 |  |  | 42861.9792 | 67 | 63
2017-05-07 | 55 | 44 |  |  | 42862 | 64 | 60
2017-05-07 00:30 | 52 | 40 |  |  | 42862.0208 | 59 | 55
2017-05-07 01:00 | 49 | 37 |  |  | 42862.0417 | 55 | 50
2017-05-07 01:30 | 48 | 34 |  |  | 42862.0625 | 53 | 48
2017-05-07 02:00 | 45 | 33 |  |  | 42862.0833 | 49 | 45
2017-05-07 02:30 | 44 | 30 |  |  | 42862.1042 | 47 | 43
2017-05-07 03:00 | 42 | 28 |  |  | 42862.125 | 44 | 40
2017-05-07 03:30 | 42 | 27 |  |  | 42862.1458 | 44 | 40
2017-05-07 04:00 | 42 | 29 |  |  | 42862.1667 | 45 | 41
2017-05-07 04:30 | 42 | 28 |  |  | 42862.1875 | 45 | 41
2017-05-07 05:00 | 43 | 27 |  |  | 42862.2083 | 46 | 41
2017-05-07 05:30 | 43 | 29 |  |  | 42862.2292 | 47 | 43
2017-05-07 06:00 | 43 | 29 |  |  | 42862.25 | 48 | 44
2017-05-07 06:30 | 44 | 30 |  |  | 42862.2708 | 49 | 45
2017-05-07 07:00 | 45 | 32 |  |  | 42862.2917 | 52 | 48
2017-05-07 07:30 | 46 | 33 |  |  | 42862.3125 | 54 | 50
2017-05-07 08:00 | 47 | 35 |  |  | 42862.3333 | 56 | 52
2017-05-07 08:30 | 49 | 39 |  |  | 42862.3542 | 58 | 55
2017-05-07 09:00 | 50 | 41 |  |  | 42862.375 | 60 | 57
2017-05-07 09:30 | 51 | 42 |  |  | 42862.3958 | 61 | 58
2017-05-07 10:00 | 51 | 42 |  |  | 42862.4167 | 63 | 60
2017-05-07 10:30 | 51 | 42 |  |  | 42862.4375 | 62 | 59
2017-05-07 11:00 | 51 | 42 |  |  | 42862.4583 | 61 | 59
2017-05-07 11:30 | 51 | 42 |  |  | 42862.4792 | 61 | 58
2017-05-07 12:00 | 49 | 40 |  |  | 42862.5 | 61 | 59
2017-05-07 12:30 | 49 | 40 |  |  | 42862.5208 | 61 | 59
2017-05-07 13:00 | 49 | 40 |  |  | 42862.5417 | 60 | 58
2017-05-07 13:30 | 49 | 40 |  |  | 42862.5625 | 59 | 57
2017-05-07 14:00 | 49 | 40 |  |  | 42862.5833 | 59 | 57
2017-05-07 14:30 | 52 | 43 |  |  | 42862.6042 | 61 | 60
2017-05-07 15:00 | 55 | 47 |  |  | 42862.625 | 66 | 64
2017-05-07 15:30 | 56 | 49 |  |  | 42862.6458 | 67 | 66
2017-05-07 16:00 | 59 | 52 |  |  | 42862.6667 | 71 | 69
2017-05-07 16:30 | 62 | 55 |  |  | 42862.6875 | 75 | 73
2017-05-07 17:00 | 66 | 59 |  |  | 42862.7083 | 80 | 78
2017-05-07 17:30 | 69 | 62 |  |  | 42862.7292 | 83 | 81
2017-05-07 18:00 | 70 | 63 |  |  | 42862.75 | 86 | 84
2017-05-07 18:30 | 70 | 62 |  |  | 42862.7708 | 84 | 82
2017-05-07 19:00 | 70 | 63 |  |  | 42862.7917 | 85 | 83
2017-05-07 19:30 | 69 | 61 |  |  | 42862.8125 | 84 | 82
2017-05-07 20:00 | 68 | 60 |  |  | 42862.8333 | 82 | 79
2017-05-07 20:30 | 65 | 58 |  |  | 42862.8542 | 81 | 79
2017-05-07 21:00 | 63 | 56 |  |  | 42862.875 | 77 | 75
2017-05-07 21:30 | 61 | 53 |  |  | 42862.8958 | 74 | 72
2017-05-07 22:00 | 59 | 51 |  |  | 42862.9167 | 72 | 70
2017-05-07 22:30 | 59 | 51 |  |  | 42862.9375 | 72 | 70
2017-05-07 23:00 | 60 | 51 |  |  | 42862.9583 | 71 | 68
2017-05-07 23:30 | 58 | 47 |  |  | 42862.9792 | 68 | 65
2017-05-08 | 54 | 43 |  |  | 42863 | 64 | 60
2017-05-08 00:30 | 52 | 39 |  |  | 42863.0208 | 60 | 55
2017-05-08 01:00 | 49 | 35 |  |  | 42863.0417 | 55 | 50
2017-05-08 01:30 | 48 | 33 |  |  | 42863.0625 | 52 | 46
2017-05-08 02:00 | 45 | 31 |  |  | 42863.0833 | 49 | 45
2017-05-08 02:30 | 44 | 30 |  |  | 42863.1042 | 49 | 44
2017-05-08 03:00 | 44 | 30 |  |  | 42863.125 | 48 | 43
2017-05-08 03:30 | 45 | 31 |  |  | 42863.1458 | 48 | 43
2017-05-08 04:00 | 45 | 31 |  |  | 42863.1667 | 48 | 44
2017-05-08 04:30 | 46 | 33 |  |  | 42863.1875 | 50 | 46
2017-05-08 05:00 | 47 | 35 |  |  | 42863.2083 | 52 | 49
2017-05-08 05:30 | 50 | 40 |  |  | 42863.2292 | 58 | 55
2017-05-08 06:00 | 54 | 48 |  |  | 42863.25 | 64 | 62
2017-05-08 06:30 | 59 | 54 |  |  | 42863.2708 | 74 | 73
2017-05-08 07:00 | 64 | 60 |  |  | 42863.2917 | 81 | 81
2017-05-08 07:30 | 67 | 64 |  |  | 42863.3125 | 88 | 88
2017-05-08 08:00 | 67 | 64 |  |  | 42863.3333 | 89 | 88
2017-05-08 08:30 | 65 | 63 |  |  | 42863.3542 | 88 | 87
2017-05-08 09:00 | 68 | 66 |  |  | 42863.375 | 95 | 94
2017-05-08 09:30 | 73 | 71 |  |  | 42863.3958 | 101 | 101
2017-05-08 10:00 | 74 | 73 |  |  | 42863.4167 | 99 | 99
2017-05-08 10:30 | 68 | 66 |  |  | 42863.4375 | 104 | 104
2017-05-08 11:00 | 60 | 58 |  |  | 42863.4583 | 106 | 105
2017-05-08 11:30 | 77 | 75 |  |  | 42863.4792 | 99 | 99
2017-05-08 12:00 | 71 | 69 |  |  | 42863.5 | 98 | 98
2017-05-08 12:30 | 70 | 69 |  |  | 42863.5208 | 98 | 98
2017-05-08 13:00 | 72 | 70 |  |  | 42863.5417 | 97 | 97
2017-05-08 13:30 | 73 | 72 |  |  | 42863.5625 | 99 | 99
2017-05-08 14:00 | 71 | 70 |  |  | 42863.5833 | 98 | 98
2017-05-08 14:30 | 68 | 67 |  |  | 42863.6042 | 94 | 94
2017-05-08 15:00 | 69 | 67 |  |  | 42863.625 | 95 | 95
2017-05-08 15:30 | 71 | 70 |  |  | 42863.6458 | 97 | 97
2017-05-08 16:00 | 74 | 72 |  |  | 42863.6667 | 97 | 96
2017-05-08 16:30 | 75 | 73 |  |  | 42863.6875 | 96 | 96
2017-05-08 17:00 | 75 | 73 |  |  | 42863.7083 | 98 | 97
2017-05-08 17:30 | 77 | 73 |  |  | 42863.7292 | 98 | 96
2017-05-08 18:00 | 77 | 72 |  |  | 42863.75 | 98 | 96
2017-05-08 18:30 | 76 | 71 |  |  | 42863.7708 | 96 | 93
2017-05-08 19:00 | 77 | 72 |  |  | 42863.7917 | 96 | 92
2017-05-08 19:30 | 76 | 70 |  |  | 42863.8125 | 94 | 90
2017-05-08 20:00 | 74 | 69 |  |  | 42863.8333 | 91 | 89
2017-05-08 20:30 | 71 | 67 |  |  | 42863.8542 | 90 | 88
2017-05-08 21:00 | 69 | 64 |  |  | 42863.875 | 86 | 84
2017-05-08 21:30 | 63 | 59 |  |  | 42863.8958 | 79 | 79
2017-05-08 22:00 | 63 | 58 |  |  | 42863.9167 | 77 | 76
2017-05-08 22:30 | 64 | 59 |  |  | 42863.9375 | 78 | 76
2017-05-08 23:00 | 65 | 58 |  |  | 42863.9583 | 77 | 74
2017-05-08 23:30 | 62 | 55 |  |  | 42863.9792 | 73 | 70
2017-05-09 | 58 | 50 |  |  | 42864 | 68 | 65
2017-05-09 00:30 | 55 | 45 |  |  | 42864.0208 | 63 | 59
2017-05-09 01:00 | 52 | 42 |  |  | 42864.0417 | 58 | 54
2017-05-09 01:30 | 49 | 38 |  |  | 42864.0625 | 54 | 49
2017-05-09 02:00 | 48 | 38 |  |  | 42864.0833 | 52 | 48
2017-05-09 02:30 | 47 | 37 |  |  | 42864.1042 | 52 | 48
2017-05-09 03:00 | 46 | 35 |  |  | 42864.125 | 50 | 46
2017-05-09 03:30 | 46 | 35 |  |  | 42864.1458 | 49 | 45
2017-05-09 04:00 | 47 | 36 |  |  | 42864.1667 | 50 | 46
2017-05-09 04:30 | 47 | 37 |  |  | 42864.1875 | 51 | 48
2017-05-09 05:00 | 48 | 39 |  |  | 42864.2083 | 54 | 51
2017-05-09 05:30 | 50 | 43 |  |  | 42864.2292 | 58 | 56
2017-05-09 06:00 | 55 | 49 |  |  | 42864.25 | 65 | 64
2017-05-09 06:30 | 61 | 57 |  |  | 42864.2708 | 76 | 75
2017-05-09 07:00 | 65 | 61 |  |  | 42864.2917 | 83 | 82
2017-05-09 07:30 | 66 | 63 |  |  | 42864.3125 | 88 | 87
2017-05-09 08:00 | 65 | 60 |  |  | 42864.3333 | 87 | 86
2017-05-09 08:30 | 64 | 58 |  |  | 42864.3542 | 86 | 84
2017-05-09 09:00 | 64 | 58 |  |  | 42864.375 | 86 | 85
2017-05-09 09:30 | 65 | 60 |  |  | 42864.3958 | 89 | 88
2017-05-09 10:00 | 67 | 62 |  |  | 42864.4167 | 91 | 90
2017-05-09 10:30 | 65 | 60 |  |  | 42864.4375 | 89 | 88
2017-05-09 11:00 | 64 | 59 |  |  | 42864.4583 | 86 | 85
2017-05-09 11:30 | 63 | 58 |  |  | 42864.4792 | 84 | 82
2017-05-09 12:00 | 62 | 57 |  |  | 42864.5 | 85 | 83
2017-05-09 12:30 | 62 | 57 |  |  | 42864.5208 | 86 | 84
2017-05-09 13:00 | 65 | 59 |  |  | 42864.5417 | 86 | 84
2017-05-09 13:30 | 63 | 58 |  |  | 42864.5625 | 85 | 84
2017-05-09 14:00 | 61 | 56 |  |  | 42864.5833 | 82 | 81
2017-05-09 14:30 | 61 | 56 |  |  | 42864.6042 | 80 | 79
2017-05-09 15:00 | 63 | 57 |  |  | 42864.625 | 84 | 82
2017-05-09 15:30 | 64 | 59 |  |  | 42864.6458 | 85 | 84
2017-05-09 16:00 | 70 | 65 |  |  | 42864.6667 | 90 | 89
2017-05-09 16:30 | 74 | 68 |  |  | 42864.6875 | 95 | 93
2017-05-09 17:00 | 76 | 70 |  |  | 42864.7083 | 96 | 94
2017-05-09 17:30 | 75 | 70 |  |  | 42864.7292 | 95 | 93
2017-05-09 18:00 | 75 | 70 |  |  | 42864.75 | 95 | 91
2017-05-09 18:30 | 75 | 68 |  |  | 42864.7708 | 93 | 89
2017-05-09 19:00 | 75 | 70 |  |  | 42864.7917 | 94 | 90
2017-05-09 19:30 | 74 | 68 |  |  | 42864.8125 | 92 | 89
2017-05-09 20:00 | 70 | 66 |  |  | 42864.8333 | 87 | 86
2017-05-09 20:30 | 69 | 66 |  |  | 42864.8542 | 87 | 86
2017-05-09 21:00 | 66 | 62 |  |  | 42864.875 | 82 | 81
2017-05-09 21:30 | 64 | 60 |  |  | 42864.8958 | 79 | 77
2017-05-09 22:00 | 64 | 59 |  |  | 42864.9167 | 79 | 77
2017-05-09 22:30 | 62 | 57 |  |  | 42864.9375 | 78 | 76
2017-05-09 23:00 | 63 | 56 |  |  | 42864.9583 | 75 | 74
2017-05-09 23:30 | 62 | 54 |  |  | 42864.9792 | 73 | 71
2017-05-10 | 59 | 51 |  |  | 42865 | 69 | 67
2017-05-10 00:30 | 55 | 46 |  |  | 42865.0208 | 63 | 61
2017-05-10 01:00 | 50 | 40 |  |  | 42865.0417 | 56 | 54
2017-05-10 01:30 | 48 | 37 |  |  | 42865.0625 | 53 | 50
2017-05-10 02:00 | 48 | 36 |  |  | 42865.0833 | 52 | 48
2017-05-10 02:30 | 46 | 35 |  |  | 42865.1042 | 50 | 47
2017-05-10 03:00 | 45 | 33 |  |  | 42865.125 | 50 | 46
2017-05-10 03:30 | 45 | 34 |  |  | 42865.1458 | 50 | 46
2017-05-10 04:00 | 45 | 34 |  |  | 42865.1667 | 50 | 46
2017-05-10 04:30 | 45 | 35 |  |  | 42865.1875 | 51 | 47
2017-05-10 05:00 | 47 | 37 |  |  | 42865.2083 | 54 | 52
2017-05-10 05:30 | 50 | 42 |  |  | 42865.2292 | 59 | 57
2017-05-10 06:00 | 54 | 48 |  |  | 42865.25 | 65 | 63
2017-05-10 06:30 | 62 | 55 |  |  | 42865.2708 | 76 | 73
2017-05-10 07:00 | 66 | 62 |  |  | 42865.2917 | 85 | 83
2017-05-10 07:30 | 72 | 69 |  |  | 42865.3125 | 94 | 93
2017-05-10 08:00 | 70 | 67 |  |  | 42865.3333 | 94 | 92
2017-05-10 08:30 | 70 | 67 |  |  | 42865.3542 | 94 | 93
2017-05-10 09:00 | 71 | 68 |  |  | 42865.375 | 96 | 95
2017-05-10 09:30 | 72 | 69 |  |  | 42865.3958 | 96 | 95
2017-05-10 10:00 | 73 | 70 |  |  | 42865.4167 | 97 | 96
2017-05-10 10:30 | 73 | 70 |  |  | 42865.4375 | 96 | 95
2017-05-10 11:00 | 73 | 70 |  |  | 42865.4583 | 96 | 95
2017-05-10 11:30 | 72 | 69 |  |  | 42865.4792 | 93 | 92
2017-05-10 12:00 | 71 | 68 |  |  | 42865.5 | 93 | 92
2017-05-10 12:30 | 71 | 68 |  |  | 42865.5208 | 93 | 91
2017-05-10 13:00 | 69 | 65 |  |  | 42865.5417 | 90 | 89
2017-05-10 13:30 | 69 | 65 |  |  | 42865.5625 | 92 | 91
2017-05-10 14:00 | 71 | 67 |  |  | 42865.5833 | 92 | 91
2017-05-10 14:30 | 69 | 65 |  |  | 42865.6042 | 90 | 88
2017-05-10 15:00 | 69 | 65 |  |  | 42865.625 | 91 | 90
2017-05-10 15:30 | 68 | 64 |  |  | 42865.6458 | 90 | 89
2017-05-10 16:00 | 70 | 66 |  |  | 42865.6667 | 92 | 90
2017-05-10 16:30 | 73 | 69 |  |  | 42865.6875 | 96 | 94
2017-05-10 17:00 | 75 | 70 |  |  | 42865.7083 | 98 | 96
2017-05-10 17:30 | 75 | 70 |  |  | 42865.7292 | 98 | 95
2017-05-10 18:00 | 74 | 68 |  |  | 42865.75 | 96 | 91
2017-05-10 18:30 | 73 | 67 |  |  | 42865.7708 | 92 | 87
2017-05-10 19:00 | 73 | 67 |  |  | 42865.7917 | 92 | 87
2017-05-10 19:30 | 72 | 66 |  |  | 42865.8125 | 90 | 86
2017-05-10 20:00 | 71 | 64 |  |  | 42865.8333 | 89 | 83
2017-05-10 20:30 | 70 | 64 |  |  | 42865.8542 | 86 | 81
2017-05-10 21:00 | 67 | 60 |  |  | 42865.875 | 81 | 77
2017-05-10 21:30 | 61 | 56 |  |  | 42865.8958 | 74 | 72
2017-05-10 22:00 | 59 | 54 |  |  | 42865.9167 | 73 | 71
2017-05-10 22:30 | 60 | 56 |  |  | 42865.9375 | 74 | 73
2017-05-10 23:00 | 61 | 56 |  |  | 42865.9583 | 74 | 73
2017-05-10 23:30 | 58 | 53 |  |  | 42865.9792 | 71 | 69
2017-05-11 | 55 | 47 |  |  | 42866 | 66 | 64
2017-05-11 00:30 | 52 | 43 |  |  | 42866.0208 | 60 | 57
2017-05-11 01:00 | 50 | 40 |  |  | 42866.0417 | 55 | 52
2017-05-11 01:30 | 47 | 35 |  |  | 42866.0625 | 51 | 48
2017-05-11 02:00 | 45 | 34 |  |  | 42866.0833 | 50 | 46
2017-05-11 02:30 | 45 | 33 |  |  | 42866.1042 | 49 | 46
2017-05-11 03:00 | 44 | 32 |  |  | 42866.125 | 48 | 45
2017-05-11 03:30 | 44 | 32 |  |  | 42866.1458 | 48 | 44
2017-05-11 04:00 | 43 | 32 |  |  | 42866.1667 | 48 | 44
2017-05-11 04:30 | 45 | 34 |  |  | 42866.1875 | 50 | 46
2017-05-11 05:00 | 46 | 36 |  |  | 42866.2083 | 53 | 50
2017-05-11 05:30 | 50 | 42 |  |  | 42866.2292 | 58 | 55
2017-05-11 06:00 | 55 | 50 |  |  | 42866.25 | 65 | 64
2017-05-11 06:30 | 62 | 57 |  |  | 42866.2708 | 76 | 75
2017-05-11 07:00 | 66 | 63 |  |  | 42866.2917 | 86 | 85
2017-05-11 07:30 | 69 | 67 |  |  | 42866.3125 | 90 | 90
2017-05-11 08:00 | 65 | 63 |  |  | 42866.3333 | 87 | 87
2017-05-11 08:30 | 62 | 59 |  |  | 42866.3542 | 85 | 84
2017-05-11 09:00 | 62 | 58 |  |  | 42866.375 | 82 | 81
2017-05-11 09:30 | 59 | 56 |  |  | 42866.3958 | 79 | 78
2017-05-11 10:00 | 58 | 55 |  |  | 42866.4167 | 77 | 77
2017-05-11 10:30 | 59 | 56 |  |  | 42866.4375 | 79 | 79
2017-05-11 11:00 | 58 | 55 |  |  | 42866.4583 | 78 | 78
2017-05-11 11:30 | 56 | 53 |  |  | 42866.4792 | 75 | 74
2017-05-11 12:00 | 53 | 50 |  |  | 42866.5 | 73 | 73
2017-05-11 12:30 | 52 | 49 |  |  | 42866.5208 | 74 | 74
2017-05-11 13:00 | 54 | 51 |  |  | 42866.5417 | 75 | 75
2017-05-11 13:30 | 56 | 53 |  |  | 42866.5625 | 78 | 77
2017-05-11 14:00 | 56 | 53 |  |  | 42866.5833 | 76 | 76
2017-05-11 14:30 | 54 | 52 |  |  | 42866.6042 | 76 | 76
2017-05-11 15:00 | 56 | 53 |  |  | 42866.625 | 79 | 78
2017-05-11 15:30 | 58 | 55 |  |  | 42866.6458 | 81 | 80
2017-05-11 16:00 | 61 | 57 |  |  | 42866.6667 | 82 | 81
2017-05-11 16:30 | 62 | 58 |  |  | 42866.6875 | 83 | 82
2017-05-11 17:00 | 66 | 63 |  |  | 42866.7083 | 88 | 86
2017-05-11 17:30 | 66 | 62 |  |  | 42866.7292 | 87 | 85
2017-05-11 18:00 | 66 | 62 |  |  | 42866.75 | 85 | 82
2017-05-11 18:30 | 67 | 62 |  |  | 42866.7708 | 86 | 81
2017-05-11 19:00 | 70 | 65 |  |  | 42866.7917 | 89 | 85
2017-05-11 19:30 | 71 | 64 |  |  | 42866.8125 | 88 | 83
2017-05-11 20:00 | 70 | 64 |  |  | 42866.8333 | 87 | 82
2017-05-11 20:30 | 69 | 63 |  |  | 42866.8542 | 87 | 82
2017-05-11 21:00 | 64 | 60 |  |  | 42866.875 | 80 | 77
2017-05-11 21:30 | 59 | 54 |  |  | 42866.8958 | 73 | 70
2017-05-11 22:00 | 57 | 52 |  |  | 42866.9167 | 71 | 69
2017-05-11 22:30 | 59 | 53 |  |  | 42866.9375 | 74 | 71
2017-05-11 23:00 | 61 | 54 |  |  | 42866.9583 | 74 | 70
2017-05-11 23:30 | 59 | 50 |  |  | 42866.9792 | 72 | 67
2017-05-12 | 57 | 48 |  |  | 42867 | 67 | 62
2017-05-12 00:30 | 54 | 43 |  |  | 42867.0208 | 62 | 57
2017-05-12 01:00 | 51 | 40 |  |  | 42867.0417 | 57 | 53
2017-05-12 01:30 | 48 | 38 |  |  | 42867.0625 | 54 | 50
2017-05-12 02:00 | 46 | 35 |  |  | 42867.0833 | 50 | 47
2017-05-12 02:30 | 45 | 33 |  |  | 42867.1042 | 50 | 47
2017-05-12 03:00 | 45 | 33 |  |  | 42867.125 | 49 | 46
2017-05-12 03:30 | 43 | 30 |  |  | 42867.1458 | 45 | 41
2017-05-12 04:00 | 41 | 28 |  |  | 42867.1667 | 43 | 39
2017-05-12 04:30 | 42 | 29 |  |  | 42867.1875 | 44 | 39
2017-05-12 05:00 | 44 | 33 |  |  | 42867.2083 | 48 | 44
2017-05-12 05:30 | 49 | 41 |  |  | 42867.2292 | 56 | 54
2017-05-12 06:00 | 56 | 50 |  |  | 42867.25 | 66 | 65
2017-05-12 06:30 | 61 | 57 |  |  | 42867.2708 | 76 | 75
2017-05-12 07:00 | 68 | 64 |  |  | 42867.2917 | 86 | 85
2017-05-12 07:30 | 69 | 68 |  |  | 42867.3125 | 92 | 92
2017-05-12 08:00 | 67 | 66 |  |  | 42867.3333 | 92 | 92
2017-05-12 08:30 | 68 | 68 |  |  | 42867.3542 | 94 | 94
2017-05-12 09:00 | 66 | 66 |  |  | 42867.375 | 93 | 92
2017-05-12 09:30 | 61 | 60 |  |  | 42867.3958 | 87 | 87
2017-05-12 10:00 | 57 | 56 |  |  | 42867.4167 | 82 | 82
2017-05-12 10:30 | 57 | 56 |  |  | 42867.4375 | 81 | 81
2017-05-12 11:00 | 61 | 61 |  |  | 42867.4583 | 84 | 84
2017-05-12 11:30 | 59 | 59 |  |  | 42867.4792 | 80 | 80
2017-05-12 12:00 | 56 | 56 |  |  | 42867.5 | 80 | 80
2017-05-12 12:30 | 63 | 62 |  |  | 42867.5208 | 89 | 89
2017-05-12 13:00 | 68 | 68 |  |  | 42867.5417 | 90 | 90
2017-05-12 13:30 | 64 | 64 |  |  | 42867.5625 | 84 | 83
2017-05-12 14:00 | 62 | 62 |  |  | 42867.5833 | 84 | 84
2017-05-12 14:30 | 62 | 62 |  |  | 42867.6042 | 82 | 82
2017-05-12 15:00 | 64 | 63 |  |  | 42867.625 | 85 | 85
2017-05-12 15:30 | 62 | 61 |  |  | 42867.6458 | 85 | 85
2017-05-12 16:00 | 66 | 66 |  |  | 42867.6667 | 87 | 87
2017-05-12 16:30 | 69 | 68 |  |  | 42867.6875 | 90 | 90
2017-05-12 17:00 | 72 | 71 |  |  | 42867.7083 | 92 | 92
2017-05-12 17:30 | 68 | 67 |  |  | 42867.7292 | 88 | 88
2017-05-12 18:00 | 66 | 65 |  |  | 42867.75 | 86 | 86
2017-05-12 18:30 | 65 | 64 |  |  | 42867.7708 | 84 | 84
2017-05-12 19:00 | 65 | 64 |  |  | 42867.7917 | 84 | 84
2017-05-12 19:30 | 63 | 62 |  |  | 42867.8125 | 82 | 81
2017-05-12 20:00 | 62 | 61 |  |  | 42867.8333 | 81 | 81
2017-05-12 20:30 | 62 | 62 |  |  | 42867.8542 | 81 | 81
2017-05-12 21:00 | 59 | 59 |  |  | 42867.875 | 77 | 76
2017-05-12 21:30 | 56 | 55 |  |  | 42867.8958 | 73 | 72
2017-05-12 22:00 | 56 | 55 |  |  | 42867.9167 | 75 | 74
2017-05-12 22:30 | 56 | 55 |  |  | 42867.9375 | 76 | 76
2017-05-12 23:00 | 57 | 55 |  |  | 42867.9583 | 75 | 75
2017-05-12 23:30 | 55 | 53 |  |  | 42867.9792 | 72 | 71
2017-05-13 | 52 | 50 |  |  | 42868 | 68 | 68
2017-05-13 00:30 | 48 | 45 |  |  | 42868.0208 | 61 | 60
2017-05-13 01:00 | 46 | 43 |  |  | 42868.0417 | 60 | 59
2017-05-13 01:30 | 43 | 40 |  |  | 42868.0625 | 56 | 55
2017-05-13 02:00 | 40 | 37 |  |  | 42868.0833 | 52 | 51
2017-05-13 02:30 | 40 | 35 |  |  | 42868.1042 | 50 | 48
2017-05-13 03:00 | 48 | 35 |  |  | 42868.125 | 52 | 47
2017-05-13 03:30 | 47 | 34 |  |  | 42868.1458 | 49 | 45
2017-05-13 04:00 | 47 | 33 |  |  | 42868.1667 | 49 | 45
2017-05-13 04:30 | 46 | 32 |  |  | 42868.1875 | 49 | 44
2017-05-13 05:00 | 47 | 34 |  |  | 42868.2083 | 50 | 46
2017-05-13 05:30 | 48 | 36 |  |  | 42868.2292 | 53 | 49
2017-05-13 06:00 | 49 | 38 |  |  | 42868.25 | 56 | 52
2017-05-13 06:30 | 50 | 40 |  |  | 42868.2708 | 57 | 54
2017-05-13 07:00 | 51 | 42 |  |  | 42868.2917 | 60 | 57
2017-05-13 07:30 | 54 | 45 |  |  | 42868.3125 | 65 | 63
2017-05-13 08:00 | 56 | 49 |  |  | 42868.3333 | 70 | 69
2017-05-13 08:30 | 59 | 53 |  |  | 42868.3542 | 77 | 76
2017-05-13 09:00 | 58 | 53 |  |  | 42868.375 | 77 | 76
2017-05-13 09:30 | 55 | 51 |  |  | 42868.3958 | 74 | 73
2017-05-13 10:00 | 55 | 50 |  |  | 42868.4167 | 74 | 73
2017-05-13 10:30 | 55 | 51 |  |  | 42868.4375 | 74 | 73
2017-05-13 11:00 | 57 | 52 |  |  | 42868.4583 | 74 | 73
2017-05-13 11:30 | 60 | 56 |  |  | 42868.4792 | 82 | 81
2017-05-13 12:00 | 64 | 61 |  |  | 42868.5 | 84 | 84
2017-05-13 12:30 | 64 | 61 |  |  | 42868.5208 | 79 | 78
2017-05-13 13:00 | 61 | 58 |  |  | 42868.5417 | 76 | 75
2017-05-13 13:30 | 60 | 57 |  |  | 42868.5625 | 77 | 77
2017-05-13 14:00 | 62 | 58 |  |  | 42868.5833 | 77 | 76
2017-05-13 14:30 | 62 | 57 |  |  | 42868.6042 | 77 | 76
2017-05-13 15:00 | 62 | 57 |  |  | 42868.625 | 76 | 75
2017-05-13 15:30 | 61 | 56 |  |  | 42868.6458 | 75 | 74
2017-05-13 16:00 | 60 | 55 |  |  | 42868.6667 | 76 | 75
2017-05-13 16:30 | 61 | 56 |  |  | 42868.6875 | 79 | 78
2017-05-13 17:00 | 60 | 55 |  |  | 42868.7083 | 79 | 78
2017-05-13 17:30 | 62 | 57 |  |  | 42868.7292 | 82 | 81
2017-05-13 18:00 | 64 | 59 |  |  | 42868.75 | 84 | 82
2017-05-13 18:30 | 66 | 61 |  |  | 42868.7708 | 85 | 83
2017-05-13 19:00 | 67 | 62 |  |  | 42868.7917 | 87 | 85
2017-05-13 19:30 | 66 | 61 |  |  | 42868.8125 | 85 | 83
2017-05-13 20:00 | 65 | 59 |  |  | 42868.8333 | 84 | 81
2017-05-13 20:30 | 65 | 59 |  |  | 42868.8542 | 83 | 81
2017-05-13 21:00 | 62 | 55 |  |  | 42868.875 | 78 | 77
2017-05-13 21:30 | 60 | 53 |  |  | 42868.8958 | 75 | 73
2017-05-13 22:00 | 60 | 52 |  |  | 42868.9167 | 76 | 73
2017-05-13 22:30 | 62 | 54 |  |  | 42868.9375 | 78 | 76
2017-05-13 23:00 | 62 | 53 |  |  | 42868.9583 | 77 | 74
2017-05-13 23:30 | 59 | 49 |  |  | 42868.9792 | 73 | 70
2017-05-14 | 57 | 46 |  |  | 42869 | 70 | 66
2017-05-14 00:30 | 53 | 41 |  |  | 42869.0208 | 64 | 59
2017-05-14 01:00 | 51 | 39 |  |  | 42869.0417 | 60 | 55
2017-05-14 01:30 | 48 | 36 |  |  | 42869.0625 | 55 | 52
2017-05-14 02:00 | 46 | 34 |  |  | 42869.0833 | 53 | 49
2017-05-14 02:30 | 47 | 34 |  |  | 42869.1042 | 52 | 49
2017-05-14 03:00 | 46 | 32 |  |  | 42869.125 | 51 | 47
2017-05-14 03:30 | 46 | 32 |  |  | 42869.1458 | 50 | 47
2017-05-14 04:00 | 45 | 30 |  |  | 42869.1667 | 49 | 45
2017-05-14 04:30 | 45 | 31 |  |  | 42869.1875 | 49 | 45
2017-05-14 05:00 | 44 | 31 |  |  | 42869.2083 | 49 | 46
2017-05-14 05:30 | 45 | 32 |  |  | 42869.2292 | 51 | 48
2017-05-14 06:00 | 46 | 33 |  |  | 42869.25 | 53 | 50
2017-05-14 06:30 | 48 | 36 |  |  | 42869.2708 | 55 | 52
2017-05-14 07:00 | 49 | 37 |  |  | 42869.2917 | 57 | 54
2017-05-14 07:30 | 50 | 38 |  |  | 42869.3125 | 60 | 57
2017-05-14 08:00 | 52 | 42 |  |  | 42869.3333 | 64 | 62
2017-05-14 08:30 | 55 | 46 |  |  | 42869.3542 | 68 | 66
2017-05-14 09:00 | 56 | 48 |  |  | 42869.375 | 70 | 68
2017-05-14 09:30 | 57 | 50 |  |  | 42869.3958 | 69 | 67
2017-05-14 10:00 | 56 | 49 |  |  | 42869.4167 | 73 | 71
2017-05-14 10:30 | 59 | 53 |  |  | 42869.4375 | 75 | 74
2017-05-14 11:00 | 60 | 53 |  |  | 42869.4583 | 75 | 74
2017-05-14 11:30 | 60 | 54 |  |  | 42869.4792 | 75 | 74
2017-05-14 12:00 | 59 | 53 |  |  | 42869.5 | 74 | 73
2017-05-14 12:30 | 56 | 49 |  |  | 42869.5208 | 70 | 69
2017-05-14 13:00 | 57 | 50 |  |  | 42869.5417 | 72 | 70
2017-05-14 13:30 | 58 | 52 |  |  | 42869.5625 | 72 | 71
2017-05-14 14:00 | 59 | 52 |  |  | 42869.5833 | 72 | 71
2017-05-14 14:30 | 57 | 50 |  |  | 42869.6042 | 71 | 69
2017-05-14 15:00 | 58 | 51 |  |  | 42869.625 | 72 | 70
2017-05-14 15:30 | 60 | 53 |  |  | 42869.6458 | 75 | 73
2017-05-14 16:00 | 61 | 55 |  |  | 42869.6667 | 78 | 77
2017-05-14 16:30 | 65 | 58 |  |  | 42869.6875 | 81 | 80
2017-05-14 17:00 | 68 | 62 |  |  | 42869.7083 | 85 | 84
2017-05-14 17:30 | 68 | 62 |  |  | 42869.7292 | 87 | 85
2017-05-14 18:00 | 69 | 62 |  |  | 42869.75 | 87 | 85
2017-05-14 18:30 | 71 | 64 |  |  | 42869.7708 | 89 | 86
2017-05-14 19:00 | 71 | 65 |  |  | 42869.7917 | 90 | 87
2017-05-14 19:30 | 70 | 63 |  |  | 42869.8125 | 88 | 85
2017-05-14 20:00 | 69 | 61 |  |  | 42869.8333 | 86 | 83
2017-05-14 20:30 | 68 | 60 |  |  | 42869.8542 | 86 | 83
2017-05-14 21:00 | 66 | 59 |  |  | 42869.875 | 82 | 80
2017-05-14 21:30 | 65 | 57 |  |  | 42869.8958 | 80 | 77
2017-05-14 22:00 | 63 | 55 |  |  | 42869.9167 | 78 | 75
2017-05-14 22:30 | 63 | 55 |  |  | 42869.9375 | 79 | 76
2017-05-14 23:00 | 62 | 54 |  |  | 42869.9583 | 76 | 73
2017-05-14 23:30 | 61 | 51 |  |  | 42869.9792 | 74 | 70
2017-05-15 | 60 | 49 |  |  | 42870 | 71 | 68
2017-05-15 00:30 | 54 | 45 |  |  | 42870.0208 | 66 | 62
2017-05-15 01:00 | 44 | 41 |  |  | 42870.0417 | 59 | 58
2017-05-15 01:30 | 41 | 38 |  |  | 42870.0625 | 56 | 55
2017-05-15 02:00 | 39 | 36 |  |  | 42870.0833 | 54 | 52
2017-05-15 02:30 | 39 | 36 |  |  | 42870.1042 | 53 | 52
2017-05-15 03:00 | 38 | 34 |  |  | 42870.125 | 52 | 51
2017-05-15 03:30 | 39 | 36 |  |  | 42870.1458 | 52 | 51
2017-05-15 04:00 | 37 | 34 |  |  | 42870.1667 | 50 | 49
2017-05-15 04:30 | 38 | 35 |  |  | 42870.1875 | 51 | 50
2017-05-15 05:00 | 40 | 38 |  |  | 42870.2083 | 54 | 53
2017-05-15 05:30 | 45 | 43 |  |  | 42870.2292 | 61 | 60
2017-05-15 06:00 | 53 | 52 |  |  | 42870.25 | 70 | 69
2017-05-15 06:30 | 60 | 60 |  |  | 42870.2708 | 81 | 81
2017-05-15 07:00 | 64 | 64 |  |  | 42870.2917 | 88 | 88
2017-05-15 07:30 | 70 | 70 |  |  | 42870.3125 | 96 | 96
2017-05-15 08:00 | 69 | 69 |  |  | 42870.3333 | 97 | 97
2017-05-15 08:30 | 68 | 68 |  |  | 42870.3542 | 97 | 97
2017-05-15 09:00 | 66 | 66 |  |  | 42870.375 | 95 | 95
2017-05-15 09:30 | 67 | 67 |  |  | 42870.3958 | 94 | 94
2017-05-15 10:00 | 66 | 66 |  |  | 42870.4167 | 93 | 93
2017-05-15 10:30 | 65 | 65 |  |  | 42870.4375 | 92 | 91
2017-05-15 11:00 | 63 | 63 |  |  | 42870.4583 | 90 | 90
2017-05-15 11:30 | 62 | 62 |  |  | 42870.4792 | 90 | 89
2017-05-15 12:00 | 62 | 62 |  |  | 42870.5 | 88 | 88
2017-05-15 12:30 | 63 | 63 |  |  | 42870.5208 | 88 | 88
2017-05-15 13:00 | 65 | 65 |  |  | 42870.5417 | 87 | 86
2017-05-15 13:30 | 70 | 69 |  |  | 42870.5625 | 95 | 94
2017-05-15 14:00 | 70 | 69 |  |  | 42870.5833 | 98 | 97
2017-05-15 14:30 | 71 | 70 |  |  | 42870.6042 | 98 | 98
2017-05-15 15:00 | 72 | 70 |  |  | 42870.625 | 102 | 101
2017-05-15 15:30 | 73 | 72 |  |  | 42870.6458 | 102 | 102
2017-05-15 16:00 | 74 | 73 |  |  | 42870.6667 | 104 | 104
2017-05-15 16:30 | 75 | 74 |  |  | 42870.6875 | 105 | 105
2017-05-15 17:00 | 76 | 75 |  |  | 42870.7083 | 106 | 106
2017-05-15 17:30 | 76 | 76 |  |  | 42870.7292 | 105 | 105
2017-05-15 18:00 | 75 | 75 |  |  | 42870.75 | 103 | 103
2017-05-15 18:30 | 72 | 72 |  |  | 42870.7708 | 99 | 98
2017-05-15 19:00 | 74 | 74 |  |  | 42870.7917 | 100 | 100
2017-05-15 19:30 | 76 | 75 |  |  | 42870.8125 | 100 | 100
2017-05-15 20:00 | 73 | 73 |  |  | 42870.8333 | 98 | 98
2017-05-15 20:30 | 70 | 69 |  |  | 42870.8542 | 94 | 94
2017-05-15 21:00 | 67 | 66 |  |  | 42870.875 | 89 | 89
2017-05-15 21:30 | 62 | 61 |  |  | 42870.8958 | 84 | 83
2017-05-15 22:00 | 62 | 60 |  |  | 42870.9167 | 84 | 83
2017-05-15 22:30 | 61 | 59 |  |  | 42870.9375 | 82 | 81
2017-05-15 23:00 | 60 | 58 |  |  | 42870.9583 | 80 | 78
2017-05-15 23:30 | 58 | 56 |  |  | 42870.9792 | 77 | 75
2017-05-16 | 54 | 51 |  |  | 42871 | 72 | 71
2017-05-16 00:30 | 49 | 46 |  |  | 42871.0208 | 65 | 64
2017-05-16 01:00 | 45 | 42 |  |  | 42871.0417 | 60 | 59
2017-05-16 01:30 | 41 | 38 |  |  | 42871.0625 | 55 | 54
2017-05-16 02:00 | 40 | 37 |  |  | 42871.0833 | 53 | 52
2017-05-16 02:30 | 40 | 37 |  |  | 42871.1042 | 53 | 52
2017-05-16 03:00 | 39 | 36 |  |  | 42871.125 | 52 | 51
2017-05-16 03:30 | 40 | 36 |  |  | 42871.1458 | 53 | 51
2017-05-16 04:00 | 40 | 37 |  |  | 42871.1667 | 54 | 52
2017-05-16 04:30 | 41 | 38 |  |  | 42871.1875 | 54 | 53
2017-05-16 05:00 | 41 | 39 |  |  | 42871.2083 | 56 | 54
2017-05-16 05:30 | 46 | 44 |  |  | 42871.2292 | 61 | 60
2017-05-16 06:00 | 54 | 53 |  |  | 42871.25 | 70 | 70
2017-05-16 06:30 | 60 | 59 |  |  | 42871.2708 | 80 | 80
2017-05-16 07:00 | 64 | 63 |  |  | 42871.2917 | 88 | 88
2017-05-16 07:30 | 68 | 68 |  |  | 42871.3125 | 97 | 97
2017-05-16 08:00 | 67 | 67 |  |  | 42871.3333 | 96 | 96
2017-05-16 08:30 | 67 | 66 |  |  | 42871.3542 | 96 | 96
2017-05-16 09:00 | 64 | 64 |  |  | 42871.375 | 92 | 92
2017-05-16 09:30 | 60 | 60 |  |  | 42871.3958 | 87 | 87
2017-05-16 10:00 | 59 | 59 |  |  | 42871.4167 | 87 | 87
2017-05-16 10:30 | 60 | 60 |  |  | 42871.4375 | 87 | 87
2017-05-16 11:00 | 61 | 61 |  |  | 42871.4583 | 88 | 88
2017-05-16 11:30 | 61 | 61 |  |  | 42871.4792 | 87 | 87
2017-05-16 12:00 | 61 | 61 |  |  | 42871.5 | 87 | 87
2017-05-16 12:30 | 60 | 60 |  |  | 42871.5208 | 86 | 86
2017-05-16 13:00 | 60 | 60 |  |  | 42871.5417 | 87 | 87
2017-05-16 13:30 | 62 | 62 |  |  | 42871.5625 | 89 | 89
2017-05-16 14:00 | 63 | 63 |  |  | 42871.5833 | 90 | 90
2017-05-16 14:30 | 64 | 64 |  |  | 42871.6042 | 90 | 90
2017-05-16 15:00 | 67 | 67 |  |  | 42871.625 | 94 | 94
2017-05-16 15:30 | 69 | 69 |  |  | 42871.6458 | 96 | 96
2017-05-16 16:00 | 71 | 71 |  |  | 42871.6667 | 99 | 99
2017-05-16 16:30 | 72 | 72 |  |  | 42871.6875 | 100 | 100
2017-05-16 17:00 | 74 | 73 |  |  | 42871.7083 | 102 | 102
2017-05-16 17:30 | 73 | 73 |  |  | 42871.7292 | 101 | 100
2017-05-16 18:00 | 72 | 71 |  |  | 42871.75 | 100 | 99
2017-05-16 18:30 | 72 | 71 |  |  | 42871.7708 | 98 | 96
2017-05-16 19:00 | 73 | 72 |  |  | 42871.7917 | 99 | 97
2017-05-16 19:30 | 72 | 71 |  |  | 42871.8125 | 97 | 95
2017-05-16 20:00 | 71 | 71 |  |  | 42871.8333 | 96 | 96
2017-05-16 20:30 | 69 | 69 |  |  | 42871.8542 | 93 | 93
2017-05-16 21:00 | 67 | 66 |  |  | 42871.875 | 89 | 89
2017-05-16 21:30 | 64 | 63 |  |  | 42871.8958 | 85 | 85
2017-05-16 22:00 | 63 | 63 |  |  | 42871.9167 | 84 | 84
2017-05-16 22:30 | 61 | 60 |  |  | 42871.9375 | 82 | 81
2017-05-16 23:00 | 60 | 59 |  |  | 42871.9583 | 80 | 79
2017-05-16 23:30 | 58 | 56 |  |  | 42871.9792 | 76 | 75
2017-05-17 | 56 | 53 |  |  | 42872 | 73 | 72
2017-05-17 00:30 | 50 | 47 |  |  | 42872.0208 | 66 | 65
2017-05-17 01:00 | 47 | 44 |  |  | 42872.0417 | 62 | 60
2017-05-17 01:30 | 44 | 41 |  |  | 42872.0625 | 58 | 56
2017-05-17 02:00 | 43 | 40 |  |  | 42872.0833 | 56 | 54
2017-05-17 02:30 | 42 | 40 |  |  | 42872.1042 | 55 | 54
2017-05-17 03:00 | 42 | 38 |  |  | 42872.125 | 54 | 53
2017-05-17 03:30 | 40 | 37 |  |  | 42872.1458 | 54 | 53
2017-05-17 04:00 | 40 | 36 |  |  | 42872.1667 | 52 | 51
2017-05-17 04:30 | 39 | 36 |  |  | 42872.1875 | 53 | 51
2017-05-17 05:00 | 43 | 40 |  |  | 42872.2083 | 57 | 55
2017-05-17 05:30 | 45 | 43 |  |  | 42872.2292 | 60 | 59
2017-05-17 06:00 | 50 | 49 |  |  | 42872.25 | 68 | 67
2017-05-17 06:30 | 56 | 56 |  |  | 42872.2708 | 77 | 77
2017-05-17 07:00 | 62 | 62 |  |  | 42872.2917 | 88 | 88
2017-05-17 07:30 | 68 | 67 |  |  | 42872.3125 | 95 | 95
2017-05-17 08:00 | 67 | 67 |  |  | 42872.3333 | 95 | 95
2017-05-17 08:30 | 64 | 64 |  |  | 42872.3542 | 93 | 93
2017-05-17 09:00 | 62 | 62 |  |  | 42872.375 | 91 | 91
2017-05-17 09:30 | 61 | 61 |  |  | 42872.3958 | 90 | 90
2017-05-17 10:00 | 57 | 57 |  |  | 42872.4167 | 85 | 85
2017-05-17 10:30 | 58 | 58 |  |  | 42872.4375 | 84 | 84
2017-05-17 11:00 | 60 | 60 |  |  | 42872.4583 | 89 | 89
2017-05-17 11:30 | 62 | 62 |  |  | 42872.4792 | 91 | 91
2017-05-17 12:00 | 61 | 61 |  |  | 42872.5 | 89 | 89
2017-05-17 12:30 | 60 | 60 |  |  | 42872.5208 | 88 | 88
2017-05-17 13:00 | 62 | 62 |  |  | 42872.5417 | 89 | 89
2017-05-17 13:30 | 64 | 64 |  |  | 42872.5625 | 91 | 91
2017-05-17 14:00 | 63 | 62 |  |  | 42872.5833 | 90 | 90
2017-05-17 14:30 | 63 | 63 |  |  | 42872.6042 | 89 | 89
2017-05-17 15:00 | 61 | 61 |  |  | 42872.625 | 89 | 89
2017-05-17 15:30 | 62 | 62 |  |  | 42872.6458 | 89 | 89
2017-05-17 16:00 | 64 | 64 |  |  | 42872.6667 | 93 | 92
2017-05-17 16:30 | 67 | 66 |  |  | 42872.6875 | 96 | 96
2017-05-17 17:00 | 70 | 69 |  |  | 42872.7083 | 98 | 98
2017-05-17 17:30 | 71 | 71 |  |  | 42872.7292 | 100 | 99
2017-05-17 18:00 | 70 | 70 |  |  | 42872.75 | 103 | 99
2017-05-17 18:30 | 69 | 68 |  |  | 42872.7708 | 103 | 96
2017-05-17 19:00 | 70 | 69 |  |  | 42872.7917 | 103 | 96
2017-05-17 19:30 | 69 | 68 |  |  | 42872.8125 | 100 | 94
2017-05-17 20:00 | 67 | 67 |  |  | 42872.8333 | 92 | 92
2017-05-17 20:30 | 64 | 64 |  |  | 42872.8542 | 91 | 91
2017-05-17 21:00 | 62 | 62 |  |  | 42872.875 | 86 | 86
2017-05-17 21:30 | 61 | 61 |  |  | 42872.8958 | 83 | 83
2017-05-17 22:00 | 58 | 58 |  |  | 42872.9167 | 80 | 80
2017-05-17 22:30 | 57 | 57 |  |  | 42872.9375 | 80 | 80
2017-05-17 23:00 | 55 | 55 |  |  | 42872.9583 | 78 | 78
2017-05-17 23:30 | 52 | 52 |  |  | 42872.9792 | 73 | 73
2017-05-18 | 50 | 50 |  |  | 42873 | 71 | 70
2017-05-18 00:30 | 46 | 46 |  |  | 42873.0208 | 64 | 64
2017-05-18 01:00 | 41 | 41 |  |  | 42873.0417 | 59 | 58
2017-05-18 01:30 | 38 | 38 |  |  | 42873.0625 | 55 | 55
2017-05-18 02:00 | 36 | 36 |  |  | 42873.0833 | 53 | 52
2017-05-18 02:30 | 35 | 35 |  |  | 42873.1042 | 51 | 51
2017-05-18 03:00 | 34 | 34 |  |  | 42873.125 | 51 | 51
2017-05-18 03:30 | 34 | 34 |  |  | 42873.1458 | 51 | 51
2017-05-18 04:00 | 34 | 34 |  |  | 42873.1667 | 51 | 51
2017-05-18 04:30 | 36 | 36 |  |  | 42873.1875 | 51 | 51
2017-05-18 05:00 | 37 | 37 |  |  | 42873.2083 | 54 | 53
2017-05-18 05:30 | 42 | 42 |  |  | 42873.2292 | 59 | 59
2017-05-18 06:00 | 48 | 48 |  |  | 42873.25 | 66 | 66
2017-05-18 06:30 | 54 | 54 |  |  | 42873.2708 | 75 | 75
2017-05-18 07:00 | 61 | 61 |  |  | 42873.2917 | 86 | 86
2017-05-18 07:30 | 68 | 67 |  |  | 42873.3125 | 97 | 97
2017-05-18 08:00 | 72 | 71 |  |  | 42873.3333 | 102 | 101
2017-05-18 08:30 | 73 | 73 |  |  | 42873.3542 | 104 | 104
2017-05-18 09:00 | 71 | 70 |  |  | 42873.375 | 100 | 100
2017-05-18 09:30 | 68 | 67 |  |  | 42873.3958 | 98 | 97
2017-05-18 10:00 | 68 | 67 |  |  | 42873.4167 | 98 | 97
2017-05-18 10:30 | 68 | 67 |  |  | 42873.4375 | 98 | 97
2017-05-18 11:00 | 68 | 67 |  |  | 42873.4583 | 98 | 98
2017-05-18 11:30 | 68 | 67 |  |  | 42873.4792 | 97 | 96
2017-05-18 12:00 | 69 | 68 |  |  | 42873.5 | 97 | 97
2017-05-18 12:30 | 66 | 66 |  |  | 42873.5208 | 96 | 95
2017-05-18 13:00 | 66 | 65 |  |  | 42873.5417 | 96 | 95
2017-05-18 13:30 | 67 | 67 |  |  | 42873.5625 | 96 | 95
2017-05-18 14:00 | 68 | 67 |  |  | 42873.5833 | 98 | 97
2017-05-18 14:30 | 68 | 67 |  |  | 42873.6042 | 96 | 96
2017-05-18 15:00 | 69 | 68 |  |  | 42873.625 | 98 | 98
2017-05-18 15:30 | 69 | 69 |  |  | 42873.6458 | 99 | 98
2017-05-18 16:00 | 70 | 70 |  |  | 42873.6667 | 100 | 100
2017-05-18 16:30 | 70 | 70 |  |  | 42873.6875 | 100 | 100
2017-05-18 17:00 | 71 | 71 |  |  | 42873.7083 | 103 | 103
2017-05-18 17:30 | 72 | 72 |  |  | 42873.7292 | 103 | 103
2017-05-18 18:00 | 70 | 70 |  |  | 42873.75 | 100 | 100
2017-05-18 18:30 | 68 | 68 |  |  | 42873.7708 | 97 | 97
2017-05-18 19:00 | 70 | 70 |  |  | 42873.7917 | 97 | 97
2017-05-18 19:30 | 69 | 69 |  |  | 42873.8125 | 96 | 95
2017-05-18 20:00 | 67 | 67 |  |  | 42873.8333 | 93 | 93
2017-05-18 20:30 | 67 | 67 |  |  | 42873.8542 | 94 | 94
2017-05-18 21:00 | 65 | 65 |  |  | 42873.875 | 91 | 91
2017-05-18 21:30 | 62 | 62 |  |  | 42873.8958 | 85 | 85
2017-05-18 22:00 | 59 | 59 |  |  | 42873.9167 | 82 | 81
2017-05-18 22:30 | 59 | 59 |  |  | 42873.9375 | 82 | 82
2017-05-18 23:00 | 58 | 58 |  |  | 42873.9583 | 79 | 79
2017-05-18 23:30 | 53 | 53 |  |  | 42873.9792 | 74 | 74
2017-05-19 | 50 | 50 |  |  | 42874 | 72 | 71
2017-05-19 00:30 | 47 | 47 |  |  | 42874.0208 | 67 | 67
2017-05-19 01:00 | 43 | 43 |  |  | 42874.0417 | 61 | 61
2017-05-19 01:30 | 39 | 39 |  |  | 42874.0625 | 57 | 57
2017-05-19 02:00 | 38 | 38 |  |  | 42874.0833 | 56 | 55
2017-05-19 02:30 | 38 | 38 |  |  | 42874.1042 | 54 | 54
2017-05-19 03:00 | 38 | 38 |  |  | 42874.125 | 54 | 54
2017-05-19 03:30 | 37 | 37 |  |  | 42874.1458 | 54 | 53
2017-05-19 04:00 | 36 | 36 |  |  | 42874.1667 | 53 | 53
2017-05-19 04:30 | 39 | 39 |  |  | 42874.1875 | 55 | 55
2017-05-19 05:00 | 41 | 41 |  |  | 42874.2083 | 58 | 58
2017-05-19 05:30 | 46 | 46 |  |  | 42874.2292 | 65 | 65
2017-05-19 06:00 | 52 | 52 |  |  | 42874.25 | 73 | 73
2017-05-19 06:30 | 58 | 58 |  |  | 42874.2708 | 83 | 83
2017-05-19 07:00 | 63 | 63 |  |  | 42874.2917 | 91 | 91
2017-05-19 07:30 | 71 | 71 |  |  | 42874.3125 | 103 | 103
2017-05-19 08:00 | 73 | 72 |  |  | 42874.3333 | 107 | 106
2017-05-19 08:30 | 74 | 73 |  |  | 42874.3542 | 108 | 107
2017-05-19 09:00 | 75 | 74 |  |  | 42874.375 | 107 | 107
2017-05-19 09:30 | 73 | 71 |  |  | 42874.3958 | 105 | 104
2017-05-19 10:00 | 73 | 72 |  |  | 42874.4167 | 105 | 104
2017-05-19 10:30 | 74 | 73 |  |  | 42874.4375 | 104 | 103
2017-05-19 11:00 | 75 | 74 |  |  | 42874.4583 | 106 | 105
2017-05-19 11:30 | 74 | 72 |  |  | 42874.4792 | 103 | 103
2017-05-19 12:00 | 74 | 73 |  |  | 42874.5 | 103 | 103
2017-05-19 12:30 | 74 | 73 |  |  | 42874.5208 | 104 | 103
2017-05-19 13:00 | 74 | 73 |  |  | 42874.5417 | 103 | 103
2017-05-19 13:30 | 73 | 72 |  |  | 42874.5625 | 102 | 101
2017-05-19 14:00 | 75 | 74 |  |  | 42874.5833 | 104 | 104
2017-05-19 14:30 | 74 | 73 |  |  | 42874.6042 | 103 | 103
2017-05-19 15:00 | 73 | 72 |  |  | 42874.625 | 102 | 101
2017-05-19 15:30 | 73 | 72 |  |  | 42874.6458 | 101 | 101
2017-05-19 16:00 | 74 | 73 |  |  | 42874.6667 | 103 | 103
2017-05-19 16:30 | 75 | 74 |  |  | 42874.6875 | 105 | 105
2017-05-19 17:00 | 79 | 79 |  |  | 42874.7083 | 108 | 108
2017-05-19 17:30 | 80 | 80 |  |  | 42874.7292 | 108 | 108
2017-05-19 18:00 | 79 | 79 |  |  | 42874.75 | 105 | 105
2017-05-19 18:30 | 76 | 76 |  |  | 42874.7708 | 100 | 100
2017-05-19 19:00 | 76 | 75 |  |  | 42874.7917 | 101 | 101
2017-05-19 19:30 | 73 | 72 |  |  | 42874.8125 | 98 | 98
2017-05-19 20:00 | 71 | 70 |  |  | 42874.8333 | 95 | 95
2017-05-19 20:30 | 69 | 69 |  |  | 42874.8542 | 94 | 94
2017-05-19 21:00 | 66 | 66 |  |  | 42874.875 | 89 | 89
2017-05-19 21:30 | 63 | 62 |  |  | 42874.8958 | 86 | 86
2017-05-19 22:00 | 62 | 62 |  |  | 42874.9167 | 86 | 86
2017-05-19 22:30 | 64 | 63 |  |  | 42874.9375 | 87 | 87
2017-05-19 23:00 | 63 | 63 |  |  | 42874.9583 | 86 | 86
2017-05-19 23:30 | 59 | 59 |  |  | 42874.9792 | 80 | 80
2017-05-20 | 54 | 54 |  |  | 42875 | 74 | 74
2017-05-20 00:30 | 49 | 49 |  |  | 42875.0208 | 68 | 68
2017-05-20 01:00 | 46 | 46 |  |  | 42875.0417 | 64 | 64
2017-05-20 01:30 | 44 | 44 |  |  | 42875.0625 | 61 | 60
2017-05-20 02:00 | 45 | 43 |  |  | 42875.0833 | 60 | 58
2017-05-20 02:30 | 47 | 43 |  |  | 42875.1042 | 60 | 58
2017-05-20 03:00 | 46 | 43 |  |  | 42875.125 | 59 | 58
2017-05-20 03:30 | 47 | 45 |  |  | 42875.1458 | 59 | 58
2017-05-20 04:00 | 46 | 44 |  |  | 42875.1667 | 60 | 59
2017-05-20 04:30 | 44 | 41 |  |  | 42875.1875 | 58 | 56
2017-05-20 05:00 | 44 | 41 |  |  | 42875.2083 | 57 | 56
2017-05-20 05:30 | 45 | 43 |  |  | 42875.2292 | 60 | 58
2017-05-20 06:00 | 47 | 45 |  |  | 42875.25 | 62 | 61
2017-05-20 06:30 | 49 | 47 |  |  | 42875.2708 | 65 | 64
2017-05-20 07:00 | 49 | 47 |  |  | 42875.2917 | 67 | 67
2017-05-20 07:30 | 51 | 49 |  |  | 42875.3125 | 70 | 69
2017-05-20 08:00 | 51 | 49 |  |  | 42875.3333 | 72 | 71
2017-05-20 08:30 | 53 | 52 |  |  | 42875.3542 | 75 | 75
2017-05-20 09:00 | 54 | 53 |  |  | 42875.375 | 76 | 76
2017-05-20 09:30 | 54 | 53 |  |  | 42875.3958 | 76 | 76
2017-05-20 10:00 | 54 | 53 |  |  | 42875.4167 | 76 | 75
2017-05-20 10:30 | 55 | 54 |  |  | 42875.4375 | 77 | 77
2017-05-20 11:00 | 56 | 55 |  |  | 42875.4583 | 77 | 77
2017-05-20 11:30 | 59 | 58 |  |  | 42875.4792 | 77 | 77
2017-05-20 12:00 | 58 | 57 |  |  | 42875.5 | 79 | 78
2017-05-20 12:30 | 58 | 57 |  |  | 42875.5208 | 78 | 78
2017-05-20 13:00 | 58 | 57 |  |  | 42875.5417 | 78 | 78
2017-05-20 13:30 | 57 | 56 |  |  | 42875.5625 | 75 | 74
2017-05-20 14:00 | 51 | 50 |  |  | 42875.5833 | 68 | 68
2017-05-20 14:30 | 52 | 50 |  |  | 42875.6042 | 71 | 70
2017-05-20 15:00 | 53 | 52 |  |  | 42875.625 | 71 | 71
2017-05-20 15:30 | 53 | 52 |  |  | 42875.6458 | 72 | 72
2017-05-20 16:00 | 56 | 55 |  |  | 42875.6667 | 75 | 75
2017-05-20 16:30 | 57 | 56 |  |  | 42875.6875 | 76 | 76
2017-05-20 17:00 | 59 | 57 |  |  | 42875.7083 | 78 | 78
2017-05-20 17:30 | 60 | 59 |  |  | 42875.7292 | 79 | 79
2017-05-20 18:00 | 60 | 59 |  |  | 42875.75 | 80 | 79
2017-05-20 18:30 | 61 | 59 |  |  | 42875.7708 | 81 | 80
2017-05-20 19:00 | 62 | 60 |  |  | 42875.7917 | 81 | 80
2017-05-20 19:30 | 63 | 61 |  |  | 42875.8125 | 81 | 81
2017-05-20 20:00 | 61 | 60 |  |  | 42875.8333 | 80 | 79
2017-05-20 20:30 | 60 | 58 |  |  | 42875.8542 | 78 | 78
2017-05-20 21:00 | 58 | 57 |  |  | 42875.875 | 75 | 75
2017-05-20 21:30 | 55 | 54 |  |  | 42875.8958 | 73 | 73
2017-05-20 22:00 | 55 | 54 |  |  | 42875.9167 | 73 | 72
2017-05-20 22:30 | 56 | 54 |  |  | 42875.9375 | 76 | 75
2017-05-20 23:00 | 58 | 56 |  |  | 42875.9583 | 76 | 75
2017-05-20 23:30 | 55 | 53 |  |  | 42875.9792 | 72 | 71
2017-05-21 | 53 | 51 |  |  | 42876 | 69 | 67
2017-05-21 00:30 | 50 | 47 |  |  | 42876.0208 | 65 | 63
2017-05-21 01:00 | 47 | 44 |  |  | 42876.0417 | 60 | 58
2017-05-21 01:30 | 45 | 42 |  |  | 42876.0625 | 58 | 56
2017-05-21 02:00 | 42 | 39 |  |  | 42876.0833 | 54 | 52
2017-05-21 02:30 | 40 | 37 |  |  | 42876.1042 | 52 | 50
2017-05-21 03:00 | 39 | 36 |  |  | 42876.125 | 50 | 48
2017-05-21 03:30 | 39 | 36 |  |  | 42876.1458 | 50 | 49
2017-05-21 04:00 | 38 | 34 |  |  | 42876.1667 | 49 | 47
2017-05-21 04:30 | 36 | 32 |  |  | 42876.1875 | 47 | 45
2017-05-21 05:00 | 34 | 31 |  |  | 42876.2083 | 45 | 44
2017-05-21 05:30 | 33 | 29 |  |  | 42876.2292 | 44 | 43
2017-05-21 06:00 | 32 | 29 |  |  | 42876.25 | 45 | 43
2017-05-21 06:30 | 34 | 30 |  |  | 42876.2708 | 46 | 45
2017-05-21 07:00 | 35 | 32 |  |  | 42876.2917 | 49 | 48
2017-05-21 07:30 | 36 | 33 |  |  | 42876.3125 | 52 | 51
2017-05-21 08:00 | 36 | 33 |  |  | 42876.3333 | 51 | 50
2017-05-21 08:30 | 36 | 34 |  |  | 42876.3542 | 52 | 52
2017-05-21 09:00 | 37 | 35 |  |  | 42876.375 | 54 | 53
2017-05-21 09:30 | 37 | 36 |  |  | 42876.3958 | 52 | 51
2017-05-21 10:00 | 37 | 36 |  |  | 42876.4167 | 52 | 52
2017-05-21 10:30 | 40 | 39 |  |  | 42876.4375 | 55 | 54
2017-05-21 11:00 | 40 | 39 |  |  | 42876.4583 | 53 | 53
2017-05-21 11:30 | 41 | 40 |  |  | 42876.4792 | 52 | 52
2017-05-21 12:00 | 45 | 44 |  |  | 42876.5 | 59 | 59
2017-05-21 12:30 | 44 | 43 |  |  | 42876.5208 | 60 | 60
2017-05-21 13:00 | 45 | 43 |  |  | 42876.5417 | 61 | 61
2017-05-21 13:30 | 44 | 43 |  |  | 42876.5625 | 60 | 60
2017-05-21 14:00 | 46 | 45 |  |  | 42876.5833 | 61 | 61
2017-05-21 14:30 | 45 | 44 |  |  | 42876.6042 | 60 | 60
2017-05-21 15:00 | 46 | 45 |  |  | 42876.625 | 63 | 63
2017-05-21 15:30 | 49 | 48 |  |  | 42876.6458 | 67 | 67
2017-05-21 16:00 | 52 | 52 |  |  | 42876.6667 | 71 | 71
2017-05-21 16:30 | 52 | 51 |  |  | 42876.6875 | 71 | 71
2017-05-21 17:00 | 54 | 53 |  |  | 42876.7083 | 74 | 74
2017-05-21 17:30 | 57 | 56 |  |  | 42876.7292 | 78 | 78
2017-05-21 18:00 | 61 | 59 |  |  | 42876.75 | 80 | 78
2017-05-21 18:30 | 60 | 58 |  |  | 42876.7708 | 78 | 77
2017-05-21 19:00 | 59 | 57 |  |  | 42876.7917 | 79 | 79
2017-05-21 19:30 | 60 | 57 |  |  | 42876.8125 | 78 | 77
2017-05-21 20:00 | 59 | 57 |  |  | 42876.8333 | 78 | 77
2017-05-21 20:30 | 58 | 57 |  |  | 42876.8542 | 78 | 77
2017-05-21 21:00 | 55 | 54 |  |  | 42876.875 | 74 | 73
2017-05-21 21:30 | 54 | 52 |  |  | 42876.8958 | 71 | 70
2017-05-21 22:00 | 51 | 49 |  |  | 42876.9167 | 69 | 67
2017-05-21 22:30 | 52 | 49 |  |  | 42876.9375 | 69 | 68
2017-05-21 23:00 | 51 | 48 |  |  | 42876.9583 | 67 | 65
2017-05-21 23:30 | 48 | 45 |  |  | 42876.9792 | 64 | 62
2017-05-22 | 45 | 42 |  |  | 42877 | 61 | 59
2017-05-22 00:30 | 43 | 39 |  |  | 42877.0208 | 57 | 56
2017-05-22 01:00 | 41 | 37 |  |  | 42877.0417 | 53 | 52
2017-05-22 01:30 | 38 | 34 |  |  | 42877.0625 | 51 | 49
2017-05-22 02:00 | 36 | 32 |  |  | 42877.0833 | 47 | 46
2017-05-22 02:30 | 34 | 30 |  |  | 42877.1042 | 46 | 45
2017-05-22 03:00 | 33 | 29 |  |  | 42877.125 | 45 | 44
2017-05-22 03:30 | 33 | 28 |  |  | 42877.1458 | 45 | 43
2017-05-22 04:00 | 35 | 30 |  |  | 42877.1667 | 47 | 46
2017-05-22 04:30 | 37 | 33 |  |  | 42877.1875 | 49 | 48
2017-05-22 05:00 | 40 | 36 |  |  | 42877.2083 | 53 | 52
2017-05-22 05:30 | 44 | 42 |  |  | 42877.2292 | 59 | 58
2017-05-22 06:00 | 48 | 46 |  |  | 42877.25 | 63 | 62
2017-05-22 06:30 | 54 | 53 |  |  | 42877.2708 | 73 | 73
2017-05-22 07:00 | 58 | 58 |  |  | 42877.2917 | 82 | 82
2017-05-22 07:30 | 60 | 60 |  |  | 42877.3125 | 87 | 87
2017-05-22 08:00 | 61 | 61 |  |  | 42877.3333 | 89 | 89
2017-05-22 08:30 | 60 | 60 |  |  | 42877.3542 | 88 | 88
2017-05-22 09:00 | 60 | 60 |  |  | 42877.375 | 88 | 88
2017-05-22 09:30 | 59 | 59 |  |  | 42877.3958 | 86 | 86
2017-05-22 10:00 | 59 | 59 |  |  | 42877.4167 | 86 | 85
2017-05-22 10:30 | 61 | 61 |  |  | 42877.4375 | 87 | 87
2017-05-22 11:00 | 63 | 62 |  |  | 42877.4583 | 89 | 89
2017-05-22 11:30 | 64 | 64 |  |  | 42877.4792 | 91 | 91
2017-05-22 12:00 | 63 | 63 |  |  | 42877.5 | 91 | 91
2017-05-22 12:30 | 64 | 64 |  |  | 42877.5208 | 91 | 91
2017-05-22 13:00 | 65 | 65 |  |  | 42877.5417 | 92 | 92
2017-05-22 13:30 | 67 | 67 |  |  | 42877.5625 | 94 | 94
2017-05-22 14:00 | 68 | 68 |  |  | 42877.5833 | 95 | 95
2017-05-22 14:30 | 67 | 67 |  |  | 42877.6042 | 94 | 94
2017-05-22 15:00 | 67 | 67 |  |  | 42877.625 | 95 | 95
2017-05-22 15:30 | 69 | 68 |  |  | 42877.6458 | 95 | 94
2017-05-22 16:00 | 68 | 68 |  |  | 42877.6667 | 96 | 95
2017-05-22 16:30 | 71 | 70 |  |  | 42877.6875 | 98 | 98
2017-05-22 17:00 | 73 | 73 |  |  | 42877.7083 | 100 | 100
2017-05-22 17:30 | 73 | 73 |  |  | 42877.7292 | 99 | 99
2017-05-22 18:00 | 74 | 74 |  |  | 42877.75 | 99 | 98
2017-05-22 18:30 | 72 | 72 |  |  | 42877.7708 | 95 | 95
2017-05-22 19:00 | 72 | 72 |  |  | 42877.7917 | 95 | 95
2017-05-22 19:30 | 70 | 70 |  |  | 42877.8125 | 93 | 93
2017-05-22 20:00 | 68 | 68 |  |  | 42877.8333 | 91 | 91
2017-05-22 20:30 | 66 | 66 |  |  | 42877.8542 | 89 | 88
2017-05-22 21:00 | 63 | 63 |  |  | 42877.875 | 84 | 83
2017-05-22 21:30 | 58 | 58 |  |  | 42877.8958 | 79 | 78
2017-05-22 22:00 | 56 | 56 |  |  | 42877.9167 | 78 | 78
2017-05-22 22:30 | 56 | 56 |  |  | 42877.9375 | 78 | 77
2017-05-22 23:00 | 56 | 56 |  |  | 42877.9583 | 75 | 75
2017-05-22 23:30 | 52 | 52 |  |  | 42877.9792 | 71 | 70
2017-05-23 | 47 | 47 |  |  | 42878 | 66 | 66
2017-05-23 00:30 | 41 | 41 |  |  | 42878.0208 | 58 | 58
2017-05-23 01:00 | 38 | 38 |  |  | 42878.0417 | 54 | 54
2017-05-23 01:30 | 37 | 35 |  |  | 42878.0625 | 51 | 50
2017-05-23 02:00 | 37 | 33 |  |  | 42878.0833 | 50 | 49
2017-05-23 02:30 | 37 | 35 |  |  | 42878.1042 | 50 | 49
2017-05-23 03:00 | 36 | 33 |  |  | 42878.125 | 48 | 48
2017-05-23 03:30 | 35 | 33 |  |  | 42878.1458 | 48 | 47
2017-05-23 04:00 | 35 | 32 |  |  | 42878.1667 | 47 | 46
2017-05-23 04:30 | 36 | 34 |  |  | 42878.1875 | 49 | 48
2017-05-23 05:00 | 37 | 35 |  |  | 42878.2083 | 51 | 51
2017-05-23 05:30 | 42 | 40 |  |  | 42878.2292 | 57 | 57
2017-05-23 06:00 | 47 | 46 |  |  | 42878.25 | 65 | 64
2017-05-23 06:30 | 54 | 51 |  |  | 42878.2708 | 74 | 74
2017-05-23 07:00 | 63 | 56 |  |  | 42878.2917 | 83 | 81
2017-05-23 07:30 | 68 | 60 |  |  | 42878.3125 | 89 | 88
2017-05-23 08:00 | 68 | 62 |  |  | 42878.3333 | 92 | 90
2017-05-23 08:30 | 68 | 62 |  |  | 42878.3542 | 93 | 92
2017-05-23 09:00 | 68 | 62 |  |  | 42878.375 | 94 | 92
2017-05-23 09:30 | 66 | 60 |  |  | 42878.3958 | 90 | 88
2017-05-23 10:00 | 62 | 56 |  |  | 42878.4167 | 88 | 86
2017-05-23 10:30 | 63 | 57 |  |  | 42878.4375 | 88 | 86
2017-05-23 11:00 | 64 | 58 |  |  | 42878.4583 | 89 | 87
2017-05-23 11:30 | 63 | 57 |  |  | 42878.4792 | 89 | 87
2017-05-23 12:00 | 64 | 59 |  |  | 42878.5 | 91 | 89
2017-05-23 12:30 | 65 | 59 |  |  | 42878.5208 | 91 | 89
2017-05-23 13:00 | 67 | 61 |  |  | 42878.5417 | 92 | 90
2017-05-23 13:30 | 67 | 61 |  |  | 42878.5625 | 93 | 91
2017-05-23 14:00 | 68 | 61 |  |  | 42878.5833 | 93 | 91
2017-05-23 14:30 | 69 | 62 |  |  | 42878.6042 | 93 | 91
2017-05-23 15:00 | 67 | 61 |  |  | 42878.625 | 92 | 91
2017-05-23 15:30 | 70 | 63 |  |  | 42878.6458 | 94 | 93
2017-05-23 16:00 | 72 | 66 |  |  | 42878.6667 | 98 | 97
2017-05-23 16:30 | 74 | 68 |  |  | 42878.6875 | 98 | 97
2017-05-23 17:00 | 75 | 68 |  |  | 42878.7083 | 99 | 98
2017-05-23 17:30 | 75 | 68 |  |  | 42878.7292 | 98 | 98
2017-05-23 18:00 | 76 | 68 |  |  | 42878.75 | 97 | 97
2017-05-23 18:30 | 75 | 68 |  |  | 42878.7708 | 94 | 93
2017-05-23 19:00 | 75 | 67 |  |  | 42878.7917 | 93 | 93
2017-05-23 19:30 | 74 | 66 |  |  | 42878.8125 | 91 | 91
2017-05-23 20:00 | 65 | 64 |  |  | 42878.8333 | 87 | 86
2017-05-23 20:30 | 63 | 62 |  |  | 42878.8542 | 86 | 86
2017-05-23 21:00 | 57 | 57 |  |  | 42878.875 | 79 | 79
2017-05-23 21:30 | 54 | 54 |  |  | 42878.8958 | 75 | 74
2017-05-23 22:00 | 52 | 51 |  |  | 42878.9167 | 73 | 72
2017-05-23 22:30 | 55 | 54 |  |  | 42878.9375 | 75 | 74
2017-05-23 23:00 | 54 | 53 |  |  | 42878.9583 | 73 | 72
2017-05-23 23:30 | 51 | 49 |  |  | 42878.9792 | 68 | 67
2017-05-24 | 47 | 44 |  |  | 42879 | 63 | 62
2017-05-24 00:30 | 44 | 40 |  |  | 42879.0208 | 58 | 57
2017-05-24 01:00 | 41 | 38 |  |  | 42879.0417 | 55 | 53
2017-05-24 01:30 | 37 | 34 |  |  | 42879.0625 | 51 | 49
2017-05-24 02:00 | 36 | 32 |  |  | 42879.0833 | 49 | 47
2017-05-24 02:30 | 35 | 31 |  |  | 42879.1042 | 48 | 46
2017-05-24 03:00 | 35 | 31 |  |  | 42879.125 | 47 | 45
2017-05-24 03:30 | 34 | 30 |  |  | 42879.1458 | 46 | 45
2017-05-24 04:00 | 34 | 30 |  |  | 42879.1667 | 46 | 45
2017-05-24 04:30 | 33 | 30 |  |  | 42879.1875 | 46 | 45
2017-05-24 05:00 | 35 | 32 |  |  | 42879.2083 | 49 | 47
2017-05-24 05:30 | 41 | 39 |  |  | 42879.2292 | 56 | 55
2017-05-24 06:00 | 47 | 46 |  |  | 42879.25 | 63 | 62
2017-05-24 06:30 | 56 | 55 |  |  | 42879.2708 | 77 | 76
2017-05-24 07:00 | 62 | 60 |  |  | 42879.2917 | 85 | 83
2017-05-24 07:30 | 70 | 65 |  |  | 42879.3125 | 99 | 91
2017-05-24 08:00 | 67 | 63 |  |  | 42879.3333 | 97 | 91
2017-05-24 08:30 | 66 | 63 |  |  | 42879.3542 | 96 | 90
2017-05-24 09:00 | 67 | 64 |  |  | 42879.375 | 98 | 92
2017-05-24 09:30 | 66 | 63 |  |  | 42879.3958 | 96 | 90
2017-05-24 10:00 | 64 | 61 |  |  | 42879.4167 | 91 | 85
2017-05-24 10:30 | 61 | 58 |  |  | 42879.4375 | 88 | 82
2017-05-24 11:00 | 60 | 57 |  |  | 42879.4583 | 87 | 82
2017-05-24 11:30 | 60 | 56 |  |  | 42879.4792 | 89 | 83
2017-05-24 12:00 | 61 | 57 |  |  | 42879.5 | 90 | 85
2017-05-24 12:30 | 63 | 59 |  |  | 42879.5208 | 92 | 87
2017-05-24 13:00 | 64 | 61 |  |  | 42879.5417 | 93 | 88
2017-05-24 13:30 | 67 | 63 |  |  | 42879.5625 | 96 | 90
2017-05-24 14:00 | 68 | 64 |  |  | 42879.5833 | 96 | 91
2017-05-24 14:30 | 68 | 64 |  |  | 42879.6042 | 97 | 92
2017-05-24 15:00 | 67 | 64 |  |  | 42879.625 | 98 | 93
2017-05-24 15:30 | 70 | 66 |  |  | 42879.6458 | 101 | 96
2017-05-24 16:00 | 73 | 69 |  |  | 42879.6667 | 104 | 99
2017-05-24 16:30 | 75 | 72 |  |  | 42879.6875 | 108 | 102
2017-05-24 17:00 | 78 | 75 |  |  | 42879.7083 | 110 | 105
2017-05-24 17:30 | 79 | 76 |  |  | 42879.7292 | 110 | 105
2017-05-24 18:00 | 78 | 75 |  |  | 42879.75 | 107 | 101
2017-05-24 18:30 | 77 | 72 |  |  | 42879.7708 | 105 | 97
2017-05-24 19:00 | 77 | 72 |  |  | 42879.7917 | 104 | 96
2017-05-24 19:30 | 74 | 71 |  |  | 42879.8125 | 99 | 94
2017-05-24 20:00 | 68 | 68 |  |  | 42879.8333 | 92 | 92
2017-05-24 20:30 | 67 | 67 |  |  | 42879.8542 | 90 | 90
2017-05-24 21:00 | 63 | 63 |  |  | 42879.875 | 84 | 84
2017-05-24 21:30 | 59 | 59 |  |  | 42879.8958 | 79 | 79
2017-05-24 22:00 | 57 | 56 |  |  | 42879.9167 | 77 | 77
2017-05-24 22:30 | 52 | 52 |  |  | 42879.9375 | 73 | 73
2017-05-24 23:00 | 48 | 48 |  |  | 42879.9583 | 68 | 68
2017-05-24 23:30 | 46 | 45 |  |  | 42879.9792 | 66 | 65
2017-05-25 | 46 | 45 |  |  | 42880 | 64 | 64
2017-05-25 00:30 | 44 | 42 |  |  | 42880.0208 | 60 | 59
2017-05-25 01:00 | 42 | 38 |  |  | 42880.0417 | 57 | 55
2017-05-25 01:30 | 38 | 34 |  |  | 42880.0625 | 53 | 51
2017-05-25 02:00 | 38 | 34 |  |  | 42880.0833 | 51 | 50
2017-05-25 02:30 | 38 | 33 |  |  | 42880.1042 | 51 | 50
2017-05-25 03:00 | 38 | 34 |  |  | 42880.125 | 51 | 49
2017-05-25 03:30 | 35 | 31 |  |  | 42880.1458 | 49 | 47
2017-05-25 04:00 | 34 | 30 |  |  | 42880.1667 | 48 | 46
2017-05-25 04:30 | 38 | 34 |  |  | 42880.1875 | 50 | 49
2017-05-25 05:00 | 39 | 36 |  |  | 42880.2083 | 53 | 52
2017-05-25 05:30 | 42 | 40 |  |  | 42880.2292 | 58 | 57
2017-05-25 06:00 | 49 | 48 |  |  | 42880.25 | 66 | 65
2017-05-25 06:30 | 54 | 53 |  |  | 42880.2708 | 74 | 74
2017-05-25 07:00 | 58 | 57 |  |  | 42880.2917 | 81 | 81
2017-05-25 07:30 | 64 | 63 |  |  | 42880.3125 | 89 | 89
2017-05-25 08:00 | 61 | 61 |  |  | 42880.3333 | 88 | 88
2017-05-25 08:30 | 60 | 60 |  |  | 42880.3542 | 88 | 88
2017-05-25 09:00 | 59 | 58 |  |  | 42880.375 | 86 | 86
2017-05-25 09:30 | 58 | 57 |  |  | 42880.3958 | 84 | 84
2017-05-25 10:00 | 57 | 56 |  |  | 42880.4167 | 84 | 84
2017-05-25 10:30 | 57 | 57 |  |  | 42880.4375 | 84 | 84
2017-05-25 11:00 | 60 | 60 |  |  | 42880.4583 | 85 | 85
2017-05-25 11:30 | 57 | 57 |  |  | 42880.4792 | 82 | 82
2017-05-25 12:00 | 58 | 57 |  |  | 42880.5 | 84 | 84
2017-05-25 12:30 | 59 | 59 |  |  | 42880.5208 | 87 | 87
2017-05-25 13:00 | 60 | 60 |  |  | 42880.5417 | 88 | 88
2017-05-25 13:30 | 62 | 62 |  |  | 42880.5625 | 88 | 88
2017-05-25 14:00 | 61 | 60 |  |  | 42880.5833 | 88 | 88
2017-05-25 14:30 | 60 | 60 |  |  | 42880.6042 | 88 | 88
2017-05-25 15:00 | 61 | 61 |  |  | 42880.625 | 90 | 90
2017-05-25 15:30 | 62 | 61 |  |  | 42880.6458 | 89 | 89
2017-05-25 16:00 | 65 | 64 |  |  | 42880.6667 | 91 | 91
2017-05-25 16:30 | 67 | 66 |  |  | 42880.6875 | 95 | 94
2017-05-25 17:00 | 70 | 68 |  |  | 42880.7083 | 98 | 98
2017-05-25 17:30 | 69 | 68 |  |  | 42880.7292 | 97 | 97
2017-05-25 18:00 | 69 | 69 |  |  | 42880.75 | 97 | 96
2017-05-25 18:30 | 68 | 67 |  |  | 42880.7708 | 92 | 92
2017-05-25 19:00 | 70 | 69 |  |  | 42880.7917 | 93 | 93
2017-05-25 19:30 | 68 | 68 |  |  | 42880.8125 | 92 | 91
2017-05-25 20:00 | 67 | 67 |  |  | 42880.8333 | 90 | 90
2017-05-25 20:30 | 65 | 65 |  |  | 42880.8542 | 88 | 88
2017-05-25 21:00 | 63 | 63 |  |  | 42880.875 | 84 | 84
2017-05-25 21:30 | 58 | 58 |  |  | 42880.8958 | 78 | 78
2017-05-25 22:00 | 55 | 55 |  |  | 42880.9167 | 75 | 75
2017-05-25 22:30 | 55 | 54 |  |  | 42880.9375 | 74 | 74
2017-05-25 23:00 | 55 | 54 |  |  | 42880.9583 | 73 | 72
2017-05-25 23:30 | 52 | 50 |  |  | 42880.9792 | 69 | 69
2017-05-26 | 48 | 46 |  |  | 42881 | 64 | 64
2017-05-26 00:30 | 44 | 42 |  |  | 42881.0208 | 60 | 60
2017-05-26 01:00 | 40 | 38 |  |  | 42881.0417 | 54 | 54
2017-05-26 01:30 | 37 | 34 |  |  | 42881.0625 | 50 | 50
2017-05-26 02:00 | 37 | 34 |  |  | 42881.0833 | 49 | 49
2017-05-26 02:30 | 37 | 34 |  |  | 42881.1042 | 50 | 49
2017-05-26 03:00 | 37 | 34 |  |  | 42881.125 | 50 | 49
2017-05-26 03:30 | 37 | 34 |  |  | 42881.1458 | 49 | 48
2017-05-26 04:00 | 34 | 31 |  |  | 42881.1667 | 46 | 45
2017-05-26 04:30 | 36 | 33 |  |  | 42881.1875 | 49 | 48
2017-05-26 05:00 | 39 | 37 |  |  | 42881.2083 | 52 | 51
2017-05-26 05:30 | 42 | 40 |  |  | 42881.2292 | 57 | 57
2017-05-26 06:00 | 47 | 46 |  |  | 42881.25 | 64 | 64
2017-05-26 06:30 | 51 | 51 |  |  | 42881.2708 | 74 | 74
2017-05-26 07:00 | 56 | 54 |  |  | 42881.2917 | 81 | 80
2017-05-26 07:30 | 59 | 59 |  |  | 42881.3125 | 87 | 86
2017-05-26 08:00 | 46 | 45 |  |  | 42881.3333 | 81 | 80
2017-05-26 08:30 | 35 | 35 |  |  | 42881.3542 | 75 | 74
2017-05-26 09:00 | 38 | 37 |  |  | 42881.375 | 76 | 76
2017-05-26 09:30 | 38 | 37 |  |  | 42881.3958 | 75 | 75
2017-05-26 10:00 | 38 | 36 |  |  | 42881.4167 | 75 | 75
2017-05-26 10:30 | 37 | 37 |  |  | 42881.4375 | 75 | 75
2017-05-26 11:00 | 39 | 38 |  |  | 42881.4583 | 75 | 75
2017-05-26 11:30 | 38 | 38 |  |  | 42881.4792 | 74 | 74
2017-05-26 12:00 | 38 | 38 |  |  | 42881.5 | 75 | 75
2017-05-26 12:30 | 38 | 38 |  |  | 42881.5208 | 75 | 75
2017-05-26 13:00 | 38 | 38 |  |  | 42881.5417 | 76 | 76
2017-05-26 13:30 | 40 | 39 |  |  | 42881.5625 | 77 | 77
2017-05-26 14:00 | 40 | 40 |  |  | 42881.5833 | 77 | 77
2017-05-26 14:30 | 39 | 39 |  |  | 42881.6042 | 77 | 77
2017-05-26 15:00 | 39 | 39 |  |  | 42881.625 | 77 | 77
2017-05-26 15:30 | 40 | 40 |  |  | 42881.6458 | 77 | 77
2017-05-26 16:00 | 43 | 42 |  |  | 42881.6667 | 78 | 78
2017-05-26 16:30 | 44 | 44 |  |  | 42881.6875 | 81 | 80
2017-05-26 17:00 | 46 | 45 |  |  | 42881.7083 | 82 | 81
2017-05-26 17:30 | 44 | 43 |  |  | 42881.7292 | 79 | 78
2017-05-26 18:00 | 43 | 41 |  |  | 42881.75 | 77 | 75
2017-05-26 18:30 | 42 | 40 |  |  | 42881.7708 | 74 | 71
2017-05-26 19:00 | 42 | 39 |  |  | 42881.7917 | 75 | 72
2017-05-26 19:30 | 42 | 39 |  |  | 42881.8125 | 74 | 72
2017-05-26 20:00 | 41 | 39 |  |  | 42881.8333 | 74 | 72
2017-05-26 20:30 | 40 | 39 |  |  | 42881.8542 | 71 | 71
2017-05-26 21:00 | 39 | 38 |  |  | 42881.875 | 68 | 68
2017-05-26 21:30 | 37 | 37 |  |  | 42881.8958 | 64 | 64
2017-05-26 22:00 | 35 | 34 |  |  | 42881.9167 | 62 | 62
2017-05-26 22:30 | 35 | 34 |  |  | 42881.9375 | 63 | 62
2017-05-26 23:00 | 36 | 35 |  |  | 42881.9583 | 62 | 61
2017-05-26 23:30 | 34 | 33 |  |  | 42881.9792 | 59 | 58
2017-05-27 | 34 | 32 |  |  | 42882 | 56 | 55
2017-05-27 00:30 | 30 | 26 |  |  | 42882.0208 | 50 | 48
2017-05-27 01:00 | 28 | 24 |  |  | 42882.0417 | 47 | 45
2017-05-27 01:30 | 26 | 22 |  |  | 42882.0625 | 44 | 42
2017-05-27 02:00 | 26 | 22 |  |  | 42882.0833 | 43 | 42
2017-05-27 02:30 | 25 | 22 |  |  | 42882.1042 | 43 | 42
2017-05-27 03:00 | 25 | 21 |  |  | 42882.125 | 42 | 41
2017-05-27 03:30 | 30 | 21 |  |  | 42882.1458 | 43 | 41
2017-05-27 04:00 | 31 | 21 |  |  | 42882.1667 | 42 | 39
2017-05-27 04:30 | 29 | 18 |  |  | 42882.1875 | 40 | 37
2017-05-27 05:00 | 29 | 18 |  |  | 42882.2083 | 40 | 37
2017-05-27 05:30 | 30 | 19 |  |  | 42882.2292 | 42 | 40
2017-05-27 06:00 | 31 | 21 |  |  | 42882.25 | 44 | 42
2017-05-27 06:30 | 31 | 22 |  |  | 42882.2708 | 48 | 46
2017-05-27 07:00 | 32 | 23 |  |  | 42882.2917 | 50 | 49
2017-05-27 07:30 | 33 | 24 |  |  | 42882.3125 | 53 | 52
2017-05-27 08:00 | 32 | 24 |  |  | 42882.3333 | 54 | 53
2017-05-27 08:30 | 32 | 25 |  |  | 42882.3542 | 56 | 55
2017-05-27 09:00 | 33 | 26 |  |  | 42882.375 | 56 | 56
2017-05-27 09:30 | 33 | 26 |  |  | 42882.3958 | 56 | 56
2017-05-27 10:00 | 34 | 27 |  |  | 42882.4167 | 57 | 57
2017-05-27 10:30 | 36 | 29 |  |  | 42882.4375 | 57 | 57
2017-05-27 11:00 | 36 | 30 |  |  | 42882.4583 | 57 | 57
2017-05-27 11:30 | 37 | 31 |  |  | 42882.4792 | 57 | 57
2017-05-27 12:00 | 38 | 32 |  |  | 42882.5 | 60 | 59
2017-05-27 12:30 | 38 | 33 |  |  | 42882.5208 | 60 | 60
2017-05-27 13:00 | 39 | 32 |  |  | 42882.5417 | 59 | 59
2017-05-27 13:30 | 38 | 32 |  |  | 42882.5625 | 60 | 60
2017-05-27 14:00 | 38 | 32 |  |  | 42882.5833 | 58 | 58
2017-05-27 14:30 | 37 | 31 |  |  | 42882.6042 | 57 | 57
2017-05-27 15:00 | 36 | 29 |  |  | 42882.625 | 58 | 58
2017-05-27 15:30 | 37 | 30 |  |  | 42882.6458 | 59 | 59
2017-05-27 16:00 | 38 | 32 |  |  | 42882.6667 | 61 | 61
2017-05-27 16:30 | 39 | 32 |  |  | 42882.6875 | 63 | 62
2017-05-27 17:00 | 40 | 34 |  |  | 42882.7083 | 66 | 66
2017-05-27 17:30 | 42 | 36 |  |  | 42882.7292 | 70 | 69
2017-05-27 18:00 | 42 | 36 |  |  | 42882.75 | 70 | 69
2017-05-27 18:30 | 42 | 36 |  |  | 42882.7708 | 69 | 68
2017-05-27 19:00 | 43 | 37 |  |  | 42882.7917 | 71 | 69
2017-05-27 19:30 | 40 | 34 |  |  | 42882.8125 | 67 | 66
2017-05-27 20:00 | 39 | 34 |  |  | 42882.8333 | 67 | 67
2017-05-27 20:30 | 38 | 34 |  |  | 42882.8542 | 67 | 67
2017-05-27 21:00 | 37 | 32 |  |  | 42882.875 | 63 | 63
2017-05-27 21:30 | 36 | 31 |  |  | 42882.8958 | 61 | 60
2017-05-27 22:00 | 36 | 31 |  |  | 42882.9167 | 62 | 61
2017-05-27 22:30 | 34 | 29 |  |  | 42882.9375 | 60 | 60
2017-05-27 23:00 | 35 | 29 |  |  | 42882.9583 | 58 | 57
2017-05-27 23:30 | 33 | 27 |  |  | 42882.9792 | 56 | 55
2017-05-28 | 34 | 25 |  |  | 42883 | 53 | 52
2017-05-28 00:30 | 34 | 24 |  |  | 42883.0208 | 49 | 48
2017-05-28 01:00 | 32 | 22 |  |  | 42883.0417 | 46 | 45
2017-05-28 01:30 | 32 | 21 |  |  | 42883.0625 | 43 | 42
2017-05-28 02:00 | 28 | 18 |  |  | 42883.0833 | 41 | 39
2017-05-28 02:30 | 28 | 17 |  |  | 42883.1042 | 40 | 37
2017-05-28 03:00 | 27 | 15 |  |  | 42883.125 | 38 | 36
2017-05-28 03:30 | 26 | 15 |  |  | 42883.1458 | 38 | 36
2017-05-28 04:00 | 27 | 15 |  |  | 42883.1667 | 38 | 36
2017-05-28 04:30 | 25 | 15 |  |  | 42883.1875 | 37 | 35
2017-05-28 05:00 | 27 | 15 |  |  | 42883.2083 | 39 | 36
2017-05-28 05:30 | 26 | 15 |  |  | 42883.2292 | 39 | 36
2017-05-28 06:00 | 27 | 15 |  |  | 42883.25 | 39 | 37
2017-05-28 06:30 | 29 | 17 |  |  | 42883.2708 | 42 | 40
2017-05-28 07:00 | 30 | 19 |  |  | 42883.2917 | 46 | 44
2017-05-28 07:30 | 30 | 19 |  |  | 42883.3125 | 47 | 45
2017-05-28 08:00 | 31 | 20 |  |  | 42883.3333 | 48 | 46
2017-05-28 08:30 | 31 | 21 |  |  | 42883.3542 | 49 | 48
2017-05-28 09:00 | 30 | 21 |  |  | 42883.375 | 48 | 47
2017-05-28 09:30 | 30 | 22 |  |  | 42883.3958 | 50 | 49
2017-05-28 10:00 | 30 | 21 |  |  | 42883.4167 | 50 | 49
2017-05-28 10:30 | 30 | 21 |  |  | 42883.4375 | 50 | 49
2017-05-28 11:00 | 30 | 22 |  |  | 42883.4583 | 50 | 49
2017-05-28 11:30 | 31 | 24 |  |  | 42883.4792 | 50 | 50
2017-05-28 12:00 | 32 | 26 |  |  | 42883.5 | 52 | 51
2017-05-28 12:30 | 33 | 26 |  |  | 42883.5208 | 54 | 54
2017-05-28 13:00 | 32 | 26 |  |  | 42883.5417 | 52 | 52
2017-05-28 13:30 | 32 | 25 |  |  | 42883.5625 | 53 | 52
2017-05-28 14:00 | 33 | 27 |  |  | 42883.5833 | 53 | 52
2017-05-28 14:30 | 33 | 27 |  |  | 42883.6042 | 53 | 53
2017-05-28 15:00 | 33 | 26 |  |  | 42883.625 | 54 | 54
2017-05-28 15:30 | 33 | 25 |  |  | 42883.6458 | 54 | 54
2017-05-28 16:00 | 35 | 28 |  |  | 42883.6667 | 59 | 58
2017-05-28 16:30 | 38 | 32 |  |  | 42883.6875 | 63 | 63
2017-05-28 17:00 | 40 | 33 |  |  | 42883.7083 | 67 | 66
2017-05-28 17:30 | 43 | 37 |  |  | 42883.7292 | 71 | 70
2017-05-28 18:00 | 43 | 38 |  |  | 42883.75 | 72 | 72
2017-05-28 18:30 | 44 | 39 |  |  | 42883.7708 | 72 | 71
2017-05-28 19:00 | 44 | 39 |  |  | 42883.7917 | 74 | 73
2017-05-28 19:30 | 43 | 38 |  |  | 42883.8125 | 71 | 70
2017-05-28 20:00 | 41 | 36 |  |  | 42883.8333 | 70 | 69
2017-05-28 20:30 | 40 | 35 |  |  | 42883.8542 | 68 | 67
2017-05-28 21:00 | 38 | 33 |  |  | 42883.875 | 64 | 63
2017-05-28 21:30 | 36 | 31 |  |  | 42883.8958 | 61 | 60
2017-05-28 22:00 | 36 | 30 |  |  | 42883.9167 | 62 | 61
2017-05-28 22:30 | 37 | 29 |  |  | 42883.9375 | 60 | 58
2017-05-28 23:00 | 36 | 27 |  |  | 42883.9583 | 57 | 55
2017-05-28 23:30 | 35 | 25 |  |  | 42883.9792 | 54 | 53
2017-05-29 | 35 | 24 |  |  | 42884 | 52 | 50
2017-05-29 00:30 | 34 | 22 |  |  | 42884.0208 | 48 | 45
2017-05-29 01:00 | 32 | 19 |  |  | 42884.0417 | 44 | 42
2017-05-29 01:30 | 30 | 18 |  |  | 42884.0625 | 42 | 40
2017-05-29 02:00 | 29 | 18 |  |  | 42884.0833 | 40 | 38
2017-05-29 02:30 | 28 | 17 |  |  | 42884.1042 | 40 | 37
2017-05-29 03:00 | 27 | 16 |  |  | 42884.125 | 39 | 37
2017-05-29 03:30 | 27 | 16 |  |  | 42884.1458 | 38 | 36
2017-05-29 04:00 | 25 | 15 |  |  | 42884.1667 | 37 | 35
2017-05-29 04:30 | 26 | 16 |  |  | 42884.1875 | 38 | 36
2017-05-29 05:00 | 28 | 18 |  |  | 42884.2083 | 40 | 39
2017-05-29 05:30 | 30 | 21 |  |  | 42884.2292 | 46 | 45
2017-05-29 06:00 | 34 | 27 |  |  | 42884.25 | 53 | 52
2017-05-29 06:30 | 34 | 31 |  |  | 42884.2708 | 62 | 62
2017-05-29 07:00 | 38 | 36 |  |  | 42884.2917 | 70 | 70
2017-05-29 07:30 | 41 | 39 |  |  | 42884.3125 | 75 | 75
2017-05-29 08:00 | 40 | 38 |  |  | 42884.3333 | 76 | 76
2017-05-29 08:30 | 41 | 37 |  |  | 42884.3542 | 75 | 75
2017-05-29 09:00 | 40 | 37 |  |  | 42884.375 | 75 | 75
2017-05-29 09:30 | 40 | 37 |  |  | 42884.3958 | 73 | 73
2017-05-29 10:00 | 39 | 37 |  |  | 42884.4167 | 73 | 73
2017-05-29 10:30 | 40 | 38 |  |  | 42884.4375 | 73 | 73
2017-05-29 11:00 | 39 | 37 |  |  | 42884.4583 | 72 | 72
2017-05-29 11:30 | 40 | 38 |  |  | 42884.4792 | 73 | 73
2017-05-29 12:00 | 40 | 38 |  |  | 42884.5 | 73 | 73
2017-05-29 12:30 | 39 | 37 |  |  | 42884.5208 | 73 | 73
2017-05-29 13:00 | 39 | 36 |  |  | 42884.5417 | 73 | 73
2017-05-29 13:30 | 39 | 37 |  |  | 42884.5625 | 73 | 73
2017-05-29 14:00 | 41 | 39 |  |  | 42884.5833 | 75 | 74
2017-05-29 14:30 | 41 | 38 |  |  | 42884.6042 | 74 | 74
2017-05-29 15:00 | 42 | 39 |  |  | 42884.625 | 76 | 76
2017-05-29 15:30 | 44 | 40 |  |  | 42884.6458 | 77 | 76
2017-05-29 16:00 | 44 | 40 |  |  | 42884.6667 | 78 | 77
2017-05-29 16:30 | 44 | 40 |  |  | 42884.6875 | 79 | 78
2017-05-29 17:00 | 46 | 41 |  |  | 42884.7083 | 80 | 79
2017-05-29 17:30 | 47 | 42 |  |  | 42884.7292 | 80 | 78
2017-05-29 18:00 | 48 | 43 |  |  | 42884.75 | 81 | 79
2017-05-29 18:30 | 47 | 40 |  |  | 42884.7708 | 77 | 75
2017-05-29 19:00 | 49 | 41 |  |  | 42884.7917 | 79 | 76
2017-05-29 19:30 | 48 | 41 |  |  | 42884.8125 | 77 | 74
2017-05-29 20:00 | 46 | 39 |  |  | 42884.8333 | 74 | 72
2017-05-29 20:30 | 42 | 38 |  |  | 42884.8542 | 73 | 72
2017-05-29 21:00 | 40 | 37 |  |  | 42884.875 | 67 | 67
2017-05-29 21:30 | 37 | 34 |  |  | 42884.8958 | 63 | 63
2017-05-29 22:00 | 38 | 33 |  |  | 42884.9167 | 63 | 62
2017-05-29 22:30 | 38 | 33 |  |  | 42884.9375 | 62 | 62
2017-05-29 23:00 | 37 | 31 |  |  | 42884.9583 | 58 | 57
2017-05-29 23:30 | 36 | 29 |  |  | 42884.9792 | 56 | 55
2017-05-30 | 35 | 27 |  |  | 42885 | 53 | 52
2017-05-30 00:30 | 31 | 23 |  |  | 42885.0208 | 47 | 46
2017-05-30 01:00 | 30 | 20 |  |  | 42885.0417 | 43 | 42
2017-05-30 01:30 | 30 | 19 |  |  | 42885.0625 | 42 | 40
2017-05-30 02:00 | 29 | 19 |  |  | 42885.0833 | 41 | 40
2017-05-30 02:30 | 29 | 19 |  |  | 42885.1042 | 41 | 39
2017-05-30 03:00 | 28 | 17 |  |  | 42885.125 | 40 | 38
2017-05-30 03:30 | 29 | 17 |  |  | 42885.1458 | 40 | 38
2017-05-30 04:00 | 28 | 15 |  |  | 42885.1667 | 38 | 36
2017-05-30 04:30 | 28 | 17 |  |  | 42885.1875 | 39 | 37
2017-05-30 05:00 | 28 | 18 |  |  | 42885.2083 | 41 | 39
2017-05-30 05:30 | 29 | 19 |  |  | 42885.2292 | 43 | 42
2017-05-30 06:00 | 30 | 23 |  |  | 42885.25 | 48 | 47
2017-05-30 06:30 | 33 | 27 |  |  | 42885.2708 | 58 | 58
2017-05-30 07:00 | 39 | 31 |  |  | 42885.2917 | 67 | 65
2017-05-30 07:30 | 41 | 36 |  |  | 42885.3125 | 75 | 74
2017-05-30 08:00 | 43 | 38 |  |  | 42885.3333 | 79 | 78
2017-05-30 08:30 | 41 | 36 |  |  | 42885.3542 | 76 | 75
2017-05-30 09:00 | 39 | 34 |  |  | 42885.375 | 73 | 72
2017-05-30 09:30 | 36 | 31 |  |  | 42885.3958 | 69 | 68
2017-05-30 10:00 | 37 | 32 |  |  | 42885.4167 | 68 | 68
2017-05-30 10:30 | 37 | 33 |  |  | 42885.4375 | 68 | 68
2017-05-30 11:00 | 37 | 33 |  |  | 42885.4583 | 67 | 66
2017-05-30 11:30 | 36 | 32 |  |  | 42885.4792 | 66 | 65
2017-05-30 12:00 | 36 | 32 |  |  | 42885.5 | 67 | 66
2017-05-30 12:30 | 37 | 33 |  |  | 42885.5208 | 68 | 68
2017-05-30 13:00 | 38 | 33 |  |  | 42885.5417 | 69 | 68
2017-05-30 13:30 | 38 | 34 |  |  | 42885.5625 | 71 | 71
2017-05-30 14:00 | 40 | 36 |  |  | 42885.5833 | 73 | 73
2017-05-30 14:30 | 40 | 36 |  |  | 42885.6042 | 73 | 73
2017-05-30 15:00 | 40 | 37 |  |  | 42885.625 | 74 | 74
2017-05-30 15:30 | 42 | 37 |  |  | 42885.6458 | 77 | 76
2017-05-30 16:00 | 49 | 37 |  |  | 42885.6667 | 85 | 78
2017-05-30 16:30 | 53 | 41 |  |  | 42885.6875 | 89 | 81
2017-05-30 17:00 | 47 | 40 |  |  | 42885.7083 | 87 | 81
2017-05-30 17:30 | 51 | 43 |  |  | 42885.7292 | 90 | 83
2017-05-30 18:00 | 53 | 44 |  |  | 42885.75 | 89 | 82
2017-05-30 18:30 | 53 | 43 |  |  | 42885.7708 | 88 | 79
2017-05-30 19:00 | 51 | 44 |  |  | 42885.7917 | 85 | 80
2017-05-30 19:30 | 48 | 43 |  |  | 42885.8125 | 82 | 78
2017-05-30 20:00 | 44 | 40 |  |  | 42885.8333 | 78 | 76
2017-05-30 20:30 | 40 | 35 |  |  | 42885.8542 | 75 | 72
2017-05-30 21:00 | 39 | 33 |  |  | 42885.875 | 72 | 69
2017-05-30 21:30 | 40 | 31 |  |  | 42885.8958 | 68 | 65
2017-05-30 22:00 | 45 | 30 |  |  | 42885.9167 | 69 | 64
2017-05-30 22:30 | 51 | 30 |  |  | 42885.9375 | 70 | 63
2017-05-30 23:00 | 45 | 29 |  |  | 42885.9583 | 63 | 59
2017-05-30 23:30 | 40 | 28 |  |  | 42885.9792 | 57 | 57
2017-05-31 | 38 | 25 |  |  | 42886 | 54 | 53
2017-05-31 00:30 | 36 | 22 |  |  | 42886.0208 | 49 | 48
2017-05-31 01:00 | 35 | 20 |  |  | 42886.0417 | 45 | 44
2017-05-31 01:30 | 33 | 17 |  |  | 42886.0625 | 41 | 41
2017-05-31 02:00 | 29 | 16 |  |  | 42886.0833 | 40 | 40
2017-05-31 02:30 | 31 | 15 |  |  | 42886.1042 | 38 | 38
2017-05-31 03:00 | 30 | 14 |  |  | 42886.125 | 38 | 37
2017-05-31 03:30 | 30 | 13 |  |  | 42886.1458 | 36 | 36
2017-05-31 04:00 | 28 | 13 |  |  | 42886.1667 | 36 | 36
2017-05-31 04:30 | 30 | 14 |  |  | 42886.1875 | 37 | 36
2017-05-31 05:00 | 30 | 16 |  |  | 42886.2083 | 40 | 40
2017-05-31 05:30 | 30 | 17 |  |  | 42886.2292 | 43 | 43
2017-05-31 06:00 | 33 | 22 |  |  | 42886.25 | 49 | 49
2017-05-31 06:30 | 33 | 27 |  |  | 42886.2708 | 59 | 59
2017-05-31 07:00 | 37 | 32 |  |  | 42886.2917 | 68 | 68
2017-05-31 07:30 | 42 | 37 |  |  | 42886.3125 | 76 | 76
2017-05-31 08:00 | 42 | 36 |  |  | 42886.3333 | 78 | 77
2017-05-31 08:30 | 42 | 36 |  |  | 42886.3542 | 78 | 78
2017-05-31 09:00 | 42 | 36 |  |  | 42886.375 | 76 | 75
2017-05-31 09:30 | 41 | 35 |  |  | 42886.3958 | 74 | 73
2017-05-31 10:00 | 40 | 34 |  |  | 42886.4167 | 72 | 72
2017-05-31 10:30 | 38 | 35 |  |  | 42886.4375 | 72 | 72
2017-05-31 11:00 | 34 | 33 |  |  | 42886.4583 | 69 | 69
2017-05-31 11:30 | 33 | 32 |  |  | 42886.4792 | 68 | 68
2017-05-31 12:00 | 34 | 32 |  |  | 42886.5 | 68 | 68
2017-05-31 12:30 | 35 | 33 |  |  | 42886.5208 | 69 | 69
2017-05-31 13:00 | 36 | 35 |  |  | 42886.5417 | 71 | 71
2017-05-31 13:30 | 37 | 36 |  |  | 42886.5625 | 72 | 72
2017-05-31 14:00 | 39 | 37 |  |  | 42886.5833 | 73 | 72
2017-05-31 14:30 | 36 | 35 |  |  | 42886.6042 | 71 | 71
2017-05-31 15:00 | 35 | 33 |  |  | 42886.625 | 70 | 70
2017-05-31 15:30 | 36 | 34 |  |  | 42886.6458 | 72 | 72
2017-05-31 16:00 | 37 | 35 |  |  | 42886.6667 | 73 | 73
2017-05-31 16:30 | 42 | 38 |  |  | 42886.6875 | 77 | 76
2017-05-31 17:00 | 45 | 40 |  |  | 42886.7083 | 78 | 77
2017-05-31 17:30 | 44 | 39 |  |  | 42886.7292 | 78 | 76
2017-05-31 18:00 | 45 | 40 |  |  | 42886.75 | 78 | 77
2017-05-31 18:30 | 45 | 41 |  |  | 42886.7708 | 76 | 75
2017-05-31 19:00 | 47 | 42 |  |  | 42886.7917 | 78 | 77
2017-05-31 19:30 | 44 | 40 |  |  | 42886.8125 | 76 | 74
2017-05-31 20:00 | 39 | 36 |  |  | 42886.8333 | 72 | 72
2017-05-31 20:30 | 37 | 33 |  |  | 42886.8542 | 68 | 68
2017-05-31 21:00 | 34 | 31 |  |  | 42886.875 | 65 | 65
2017-05-31 21:30 | 33 | 27 |  |  | 42886.8958 | 61 | 60
2017-05-31 22:00 | 33 | 27 |  |  | 42886.9167 | 61 | 60
2017-05-31 22:30 | 34 | 28 |  |  | 42886.9375 | 60 | 60
2017-05-31 23:00 | 36 | 29 |  |  | 42886.9583 | 59 | 59
2017-05-31 23:30 | 35 | 27 |  |  | 42886.9792 | 56 | 55
2017-06-01 | 32 | 22 |  |  | 42887 | 51 | 50
2017-06-01 00:30 | 31 | 20 |  |  | 42887.0208 | 47 | 45
2017-06-01 01:00 | 29 | 18 |  |  | 42887.0417 | 44 | 42
2017-06-01 01:30 | 28 | 15 |  |  | 42887.0625 | 41 | 39
2017-06-01 02:00 | 29 | 16 |  |  | 42887.0833 | 41 | 38
2017-06-01 02:30 | 28 | 15 |  |  | 42887.1042 | 40 | 36
2017-06-01 03:00 | 27 | 14 |  |  | 42887.125 | 39 | 36
2017-06-01 03:30 | 28 | 14 |  |  | 42887.1458 | 39 | 36
2017-06-01 04:00 | 28 | 14 |  |  | 42887.1667 | 40 | 37
2017-06-01 04:30 | 28 | 16 |  |  | 42887.1875 | 41 | 38
2017-06-01 05:00 | 27 | 17 |  |  | 42887.2083 | 42 | 39
2017-06-01 05:30 | 30 | 20 |  |  | 42887.2292 | 46 | 44
2017-06-01 06:00 | 32 | 24 |  |  | 42887.25 | 52 | 51
2017-06-01 06:30 | 40 | 29 |  |  | 42887.2708 | 65 | 61
2017-06-01 07:00 | 50 | 32 |  |  | 42887.2917 | 81 | 69
2017-06-01 07:30 | 48 | 35 |  |  | 42887.3125 | 86 | 76
2017-06-01 08:00 | 46 | 34 |  |  | 42887.3333 | 85 | 76
2017-06-01 08:30 | 45 | 32 |  |  | 42887.3542 | 83 | 74
2017-06-01 09:00 | 47 | 32 |  |  | 42887.375 | 81 | 72
2017-06-01 09:30 | 52 | 30 |  |  | 42887.3958 | 78 | 68
2017-06-01 10:00 | 43 | 29 |  |  | 42887.4167 | 69 | 65
2017-06-01 10:30 | 41 | 29 |  |  | 42887.4375 | 67 | 65
2017-06-01 11:00 | 40 | 29 |  |  | 42887.4583 | 66 | 64
2017-06-01 11:30 | 38 | 27 |  |  | 42887.4792 | 64 | 62
2017-06-01 12:00 | 38 | 23 |  |  | 42887.5 | 62 | 60
2017-06-01 12:30 | 38 | 25 |  |  | 42887.5208 | 63 | 60
2017-06-01 13:00 | 36 | 24 |  |  | 42887.5417 | 62 | 60
2017-06-01 13:30 | 37 | 24 |  |  | 42887.5625 | 63 | 61
2017-06-01 14:00 | 38 | 26 |  |  | 42887.5833 | 64 | 63
2017-06-01 14:30 | 38 | 26 |  |  | 42887.6042 | 65 | 64
2017-06-01 15:00 | 38 | 27 |  |  | 42887.625 | 66 | 65
2017-06-01 15:30 | 40 | 27 |  |  | 42887.6458 | 67 | 64
2017-06-01 16:00 | 40 | 27 |  |  | 42887.6667 | 67 | 65
2017-06-01 16:30 | 41 | 27 |  |  | 42887.6875 | 69 | 66
2017-06-01 17:00 | 49 | 30 |  |  | 42887.7083 | 75 | 69
2017-06-01 17:30 | 53 | 33 |  |  | 42887.7292 | 81 | 71
2017-06-01 18:00 | 54 | 33 |  |  | 42887.75 | 82 | 70
2017-06-01 18:30 | 53 | 31 |  |  | 42887.7708 | 80 | 69
2017-06-01 19:00 | 54 | 34 |  |  | 42887.7917 | 81 | 71
2017-06-01 19:30 | 51 | 33 |  |  | 42887.8125 | 79 | 70
2017-06-01 20:00 | 50 | 34 |  |  | 42887.8333 | 79 | 70
2017-06-01 20:30 | 49 | 35 |  |  | 42887.8542 | 76 | 69
2017-06-01 21:00 | 41 | 32 |  |  | 42887.875 | 67 | 65
2017-06-01 21:30 | 40 | 29 |  |  | 42887.8958 | 63 | 61
2017-06-01 22:00 | 37 | 27 |  |  | 42887.9167 | 61 | 60
2017-06-01 22:30 | 34 | 27 |  |  | 42887.9375 | 59 | 59
2017-06-01 23:00 | 35 | 28 |  |  | 42887.9583 | 57 | 57
2017-06-01 23:30 | 35 | 25 |  |  | 42887.9792 | 52 | 52
2017-06-02 | 36 | 23 |  |  | 42888 | 49 | 49
2017-06-02 00:30 | 36 | 20 |  |  | 42888.0208 | 45 | 44
2017-06-02 01:00 | 34 | 18 |  |  | 42888.0417 | 41 | 40
2017-06-02 01:30 | 33 | 17 |  |  | 42888.0625 | 39 | 38
2017-06-02 02:00 | 33 | 16 |  |  | 42888.0833 | 39 | 38
2017-06-02 02:30 | 32 | 16 |  |  | 42888.1042 | 37 | 36
2017-06-02 03:00 | 32 | 16 |  |  | 42888.125 | 36 | 36
2017-06-02 03:30 | 32 | 15 |  |  | 42888.1458 | 36 | 35
2017-06-02 04:00 | 32 | 14 |  |  | 42888.1667 | 34 | 33
2017-06-02 04:30 | 31 | 14 |  |  | 42888.1875 | 35 | 34
2017-06-02 05:00 | 32 | 17 |  |  | 42888.2083 | 38 | 37
2017-06-02 05:30 | 32 | 20 |  |  | 42888.2292 | 41 | 41
2017-06-02 06:00 | 33 | 23 |  |  | 42888.25 | 47 | 47
2017-06-02 06:30 | 37 | 31 |  |  | 42888.2708 | 61 | 61
2017-06-02 07:00 | 42 | 36 |  |  | 42888.2917 | 70 | 70
2017-06-02 07:30 | 51 | 39 |  |  | 42888.3125 | 78 | 75
2017-06-02 08:00 | 48 | 36 |  |  | 42888.3333 | 75 | 73
2017-06-02 08:30 | 46 | 32 |  |  | 42888.3542 | 74 | 71
2017-06-02 09:00 | 43 | 26 |  |  | 42888.375 | 68 | 66
2017-06-02 09:30 | 42 | 25 |  |  | 42888.3958 | 65 | 64
2017-06-02 10:00 | 40 | 25 |  |  | 42888.4167 | 63 | 62
2017-06-02 10:30 | 61 | 43 |  |  | 42888.4375 | 72 | 69
2017-06-02 11:00 | 60 | 43 |  |  | 42888.4583 | 72 | 69
2017-06-02 11:30 | 59 | 42 |  |  | 42888.4792 | 71 | 69
2017-06-02 12:00 | 59 | 42 |  |  | 42888.5 | 71 | 69
2017-06-02 12:30 | 59 | 44 |  |  | 42888.5208 | 73 | 71
2017-06-02 13:00 | 60 | 45 |  |  | 42888.5417 | 73 | 71
2017-06-02 13:30 | 61 | 46 |  |  | 42888.5625 | 73 | 71
2017-06-02 14:00 | 61 | 46 |  |  | 42888.5833 | 74 | 71
2017-06-02 14:30 | 62 | 47 |  |  | 42888.6042 | 74 | 71
2017-06-02 15:00 | 63 | 49 |  |  | 42888.625 | 76 | 73
2017-06-02 15:30 | 65 | 50 |  |  | 42888.6458 | 79 | 75
2017-06-02 16:00 | 67 | 52 |  |  | 42888.6667 | 80 | 76
2017-06-02 16:30 | 67 | 52 |  |  | 42888.6875 | 80 | 76
2017-06-02 17:00 | 69 | 53 |  |  | 42888.7083 | 82 | 77
2017-06-02 17:30 | 72 | 56 |  |  | 42888.7292 | 85 | 80
2017-06-02 18:00 | 74 | 60 |  |  | 42888.75 | 87 | 82
2017-06-02 18:30 | 74 | 58 |  |  | 42888.7708 | 85 | 78
2017-06-02 19:00 | 75 | 59 |  |  | 42888.7917 | 86 | 79
2017-06-02 19:30 | 74 | 57 |  |  | 42888.8125 | 83 | 76
2017-06-02 20:00 | 72 | 55 |  |  | 42888.8333 | 81 | 75
2017-06-02 20:30 | 66 | 54 |  |  | 42888.8542 | 76 | 73
2017-06-02 21:00 | 65 | 52 |  |  | 42888.875 | 73 | 70
2017-06-02 21:30 | 63 | 49 |  |  | 42888.8958 | 70 | 67
2017-06-02 22:00 | 62 | 46 |  |  | 42888.9167 | 70 | 66
2017-06-02 22:30 | 60 | 44 |  |  | 42888.9375 | 67 | 63
2017-06-02 23:00 | 61 | 43 |  |  | 42888.9583 | 66 | 61
2017-06-02 23:30 | 62 | 41 |  |  | 42888.9792 | 64 | 58
2017-06-03 | 60 | 38 |  |  | 42889 | 61 | 55
2017-06-03 00:30 | 60 | 34 |  |  | 42889.0208 | 57 | 49
2017-06-03 01:00 | 59 | 31 |  |  | 42889.0417 | 54 | 46
2017-06-03 01:30 | 59 | 30 |  |  | 42889.0625 | 51 | 43
2017-06-03 02:00 | 58 | 28 |  |  | 42889.0833 | 50 | 42
2017-06-03 02:30 | 57 | 27 |  |  | 42889.1042 | 49 | 41
2017-06-03 03:00 | 56 | 24 |  |  | 42889.125 | 46 | 38
2017-06-03 03:30 | 56 | 24 |  |  | 42889.1458 | 45 | 37
2017-06-03 04:00 | 55 | 23 |  |  | 42889.1667 | 44 | 36
2017-06-03 04:30 | 55 | 23 |  |  | 42889.1875 | 43 | 35
2017-06-03 05:00 | 55 | 23 |  |  | 42889.2083 | 45 | 37
2017-06-03 05:30 | 54 | 24 |  |  | 42889.2292 | 45 | 38
2017-06-03 06:00 | 53 | 24 |  |  | 42889.25 | 46 | 40
2017-06-03 06:30 | 53 | 26 |  |  | 42889.2708 | 48 | 43
2017-06-03 07:00 | 56 | 31 |  |  | 42889.2917 | 54 | 49
2017-06-03 07:30 | 57 | 34 |  |  | 42889.3125 | 58 | 53
2017-06-03 08:00 | 58 | 34 |  |  | 42889.3333 | 59 | 55
2017-06-03 08:30 | 58 | 34 |  |  | 42889.3542 | 59 | 56
2017-06-03 09:00 | 58 | 35 |  |  | 42889.375 | 60 | 56
2017-06-03 09:30 | 56 | 33 |  |  | 42889.3958 | 57 | 54
2017-06-03 10:00 | 56 | 33 |  |  | 42889.4167 | 57 | 53
2017-06-03 10:30 | 57 | 33 |  |  | 42889.4375 | 56 | 53
2017-06-03 11:00 | 57 | 33 |  |  | 42889.4583 | 55 | 52
2017-06-03 11:30 | 55 | 32 |  |  | 42889.4792 | 54 | 51
2017-06-03 12:00 | 55 | 31 |  |  | 42889.5 | 53 | 49
2017-06-03 12:30 | 56 | 32 |  |  | 42889.5208 | 53 | 50
2017-06-03 13:00 | 56 | 33 |  |  | 42889.5417 | 53 | 50
2017-06-03 13:30 | 57 | 33 |  |  | 42889.5625 | 54 | 51
2017-06-03 14:00 | 57 | 34 |  |  | 42889.5833 | 55 | 52
2017-06-03 14:30 | 57 | 34 |  |  | 42889.6042 | 55 | 52
2017-06-03 15:00 | 57 | 35 |  |  | 42889.625 | 56 | 53
2017-06-03 15:30 | 57 | 36 |  |  | 42889.6458 | 57 | 54
2017-06-03 16:00 | 60 | 41 |  |  | 42889.6667 | 62 | 60
2017-06-03 16:30 | 64 | 46 |  |  | 42889.6875 | 68 | 65
2017-06-03 17:00 | 66 | 47 |  |  | 42889.7083 | 71 | 67
2017-06-03 17:30 | 68 | 50 |  |  | 42889.7292 | 74 | 69
2017-06-03 18:00 | 69 | 50 |  |  | 42889.75 | 75 | 70
2017-06-03 18:30 | 69 | 48 |  |  | 42889.7708 | 74 | 69
2017-06-03 19:00 | 70 | 50 |  |  | 42889.7917 | 76 | 71
2017-06-03 19:30 | 71 | 50 |  |  | 42889.8125 | 76 | 70
2017-06-03 20:00 | 69 | 48 |  |  | 42889.8333 | 75 | 69
2017-06-03 20:30 | 68 | 47 |  |  | 42889.8542 | 72 | 67
2017-06-03 21:00 | 67 | 46 |  |  | 42889.875 | 70 | 65
2017-06-03 21:30 | 65 | 44 |  |  | 42889.8958 | 68 | 62
2017-06-03 22:00 | 65 | 43 |  |  | 42889.9167 | 68 | 62
2017-06-03 22:30 | 63 | 41 |  |  | 42889.9375 | 65 | 59
2017-06-03 23:00 | 63 | 40 |  |  | 42889.9583 | 64 | 58
2017-06-03 23:30 | 63 | 38 |  |  | 42889.9792 | 63 | 56
2017-06-04 | 63 | 37 |  |  | 42890 | 61 | 53
2017-06-04 00:30 | 61 | 35 |  |  | 42890.0208 | 58 | 51
2017-06-04 01:00 | 60 | 33 |  |  | 42890.0417 | 54 | 47
2017-06-04 01:30 | 58 | 29 |  |  | 42890.0625 | 52 | 44
2017-06-04 02:00 | 58 | 28 |  |  | 42890.0833 | 51 | 42
2017-06-04 02:30 | 58 | 27 |  |  | 42890.1042 | 50 | 40
2017-06-04 03:00 | 58 | 27 |  |  | 42890.125 | 49 | 40
2017-06-04 03:30 | 58 | 26 |  |  | 42890.1458 | 48 | 39
2017-06-04 04:00 | 58 | 26 |  |  | 42890.1667 | 49 | 39
2017-06-04 04:30 | 59 | 27 |  |  | 42890.1875 | 50 | 41
2017-06-04 05:00 | 59 | 27 |  |  | 42890.2083 | 49 | 40
2017-06-04 05:30 | 59 | 28 |  |  | 42890.2292 | 50 | 41
2017-06-04 06:00 | 58 | 27 |  |  | 42890.25 | 50 | 42
2017-06-04 06:30 | 57 | 27 |  |  | 42890.2708 | 51 | 44
2017-06-04 07:00 | 58 | 29 |  |  | 42890.2917 | 53 | 46
2017-06-04 07:30 | 60 | 31 |  |  | 42890.3125 | 56 | 49
2017-06-04 08:00 | 60 | 33 |  |  | 42890.3333 | 58 | 52
2017-06-04 08:30 | 60 | 35 |  |  | 42890.3542 | 59 | 53
2017-06-04 09:00 | 60 | 37 |  |  | 42890.375 | 60 | 55
2017-06-04 09:30 | 61 | 35 |  |  | 42890.3958 | 61 | 54
2017-06-04 10:00 | 61 | 35 |  |  | 42890.4167 | 59 | 53
2017-06-04 10:30 | 61 | 35 |  |  | 42890.4375 | 58 | 52
2017-06-04 11:00 | 61 | 35 |  |  | 42890.4583 | 58 | 52
2017-06-04 11:30 | 62 | 36 |  |  | 42890.4792 | 58 | 52
2017-06-04 12:00 | 62 | 36 |  |  | 42890.5 | 58 | 52
2017-06-04 12:30 | 60 | 34 |  |  | 42890.5208 | 57 | 51
2017-06-04 13:00 | 60 | 35 |  |  | 42890.5417 | 58 | 52
2017-06-04 13:30 | 61 | 36 |  |  | 42890.5625 | 58 | 52
2017-06-04 14:00 | 60 | 35 |  |  | 42890.5833 | 57 | 51
2017-06-04 14:30 | 61 | 36 |  |  | 42890.6042 | 59 | 53
2017-06-04 15:00 | 62 | 38 |  |  | 42890.625 | 61 | 55
2017-06-04 15:30 | 64 | 41 |  |  | 42890.6458 | 65 | 60
2017-06-04 16:00 | 65 | 44 |  |  | 42890.6667 | 68 | 63
2017-06-04 16:30 | 69 | 49 |  |  | 42890.6875 | 73 | 68
2017-06-04 17:00 | 72 | 54 |  |  | 42890.7083 | 79 | 74
2017-06-04 17:30 | 72 | 56 |  |  | 42890.7292 | 80 | 76
2017-06-04 18:00 | 67 | 59 |  |  | 42890.75 | 82 | 79
2017-06-04 18:30 | 68 | 59 |  |  | 42890.7708 | 82 | 79
2017-06-04 19:00 | 68 | 59 |  |  | 42890.7917 | 83 | 80
2017-06-04 19:30 | 67 | 58 |  |  | 42890.8125 | 82 | 78
2017-06-04 20:00 | 66 | 57 |  |  | 42890.8333 | 79 | 75
2017-06-04 20:30 | 64 | 55 |  |  | 42890.8542 | 78 | 74
2017-06-04 21:00 | 61 | 52 |  |  | 42890.875 | 74 | 72
2017-06-04 21:30 | 59 | 50 |  |  | 42890.8958 | 71 | 68
2017-06-04 22:00 | 59 | 49 |  |  | 42890.9167 | 72 | 69
2017-06-04 22:30 | 58 | 48 |  |  | 42890.9375 | 70 | 67
2017-06-04 23:00 | 64 | 46 |  |  | 42890.9583 | 69 | 64
2017-06-04 23:30 | 64 | 45 |  |  | 42890.9792 | 68 | 62
2017-06-05 | 63 | 42 |  |  | 42891 | 66 | 59
2017-06-05 00:30 | 63 | 40 |  |  | 42891.0208 | 63 | 56
2017-06-05 01:00 | 61 | 37 |  |  | 42891.0417 | 60 | 52
2017-06-05 01:30 | 60 | 35 |  |  | 42891.0625 | 58 | 48
2017-06-05 02:00 | 58 | 31 |  |  | 42891.0833 | 55 | 44
2017-06-05 02:30 | 58 | 30 |  |  | 42891.1042 | 54 | 44
2017-06-05 03:00 | 57 | 29 |  |  | 42891.125 | 53 | 43
2017-06-05 03:30 | 57 | 29 |  |  | 42891.1458 | 53 | 43
2017-06-05 04:00 | 55 | 30 |  |  | 42891.1667 | 50 | 43
2017-06-05 04:30 | 56 | 31 |  |  | 42891.1875 | 51 | 43
2017-06-05 05:00 | 55 | 33 |  |  | 42891.2083 | 53 | 46
2017-06-05 05:30 | 57 | 38 |  |  | 42891.2292 | 57 | 52
2017-06-05 06:00 | 59 | 45 |  |  | 42891.25 | 64 | 61
2017-06-05 06:30 | 62 | 55 |  |  | 42891.2708 | 75 | 73
2017-06-05 07:00 | 67 | 61 |  |  | 42891.2917 | 85 | 83
2017-06-05 07:30 | 72 | 65 |  |  | 42891.3125 | 92 | 90
2017-06-05 08:00 | 71 | 64 |  |  | 42891.3333 | 92 | 89
2017-06-05 08:30 | 70 | 59 |  |  | 42891.3542 | 87 | 84
2017-06-05 09:00 | 87 | 56 |  |  | 42891.375 | 101 | 81
2017-06-05 09:30 | 99 | 55 |  |  | 42891.3958 | 119 | 82
2017-06-05 10:00 | 96 | 55 |  |  | 42891.4167 | 117 | 80
2017-06-05 10:30 | 94 | 54 |  |  | 42891.4375 | 115 | 79
2017-06-05 11:00 | 92 | 54 |  |  | 42891.4583 | 113 | 78
2017-06-05 11:30 | 74 | 53 |  |  | 42891.4792 | 88 | 76
2017-06-05 12:00 | 70 | 53 |  |  | 42891.5 | 85 | 77
2017-06-05 12:30 | 70 | 52 |  |  | 42891.5208 | 85 | 77
2017-06-05 13:00 | 70 | 52 |  |  | 42891.5417 | 85 | 77
2017-06-05 13:30 | 71 | 54 |  |  | 42891.5625 | 87 | 79
2017-06-05 14:00 | 73 | 57 |  |  | 42891.5833 | 88 | 80
2017-06-05 14:30 | 75 | 59 |  |  | 42891.6042 | 89 | 81
2017-06-05 15:00 | 74 | 59 |  |  | 42891.625 | 89 | 82
2017-06-05 15:30 | 77 | 62 |  |  | 42891.6458 | 93 | 85
2017-06-05 16:00 | 81 | 64 |  |  | 42891.6667 | 97 | 88
2017-06-05 16:30 | 86 | 66 |  |  | 42891.6875 | 101 | 88
2017-06-05 17:00 | 90 | 68 |  |  | 42891.7083 | 105 | 90
2017-06-05 17:30 | 94 | 71 |  |  | 42891.7292 | 110 | 92
2017-06-05 18:00 | 97 | 73 |  |  | 42891.75 | 113 | 93
2017-06-05 18:30 | 97 | 72 |  |  | 42891.7708 | 110 | 90
2017-06-05 19:00 | 95 | 74 |  |  | 42891.7917 | 107 | 91
2017-06-05 19:30 | 89 | 71 |  |  | 42891.8125 | 100 | 89
2017-06-05 20:00 | 77 | 67 |  |  | 42891.8333 | 87 | 85
2017-06-05 20:30 | 76 | 66 |  |  | 42891.8542 | 85 | 83
2017-06-05 21:00 | 74 | 63 |  |  | 42891.875 | 81 | 79
2017-06-05 21:30 | 72 | 61 |  |  | 42891.8958 | 77 | 76
2017-06-05 22:00 | 68 | 59 |  |  | 42891.9167 | 76 | 75
2017-06-05 22:30 | 67 | 58 |  |  | 42891.9375 | 76 | 74
2017-06-05 23:00 | 67 | 57 |  |  | 42891.9583 | 73 | 71
2017-06-05 23:30 | 65 | 54 |  |  | 42891.9792 | 71 | 69
2017-06-06 | 60 | 47 |  |  | 42892 | 65 | 62
2017-06-06 00:30 | 57 | 41 |  |  | 42892.0208 | 58 | 55
2017-06-06 01:00 | 57 | 41 |  |  | 42892.0417 | 55 | 52
2017-06-06 01:30 | 55 | 38 |  |  | 42892.0625 | 52 | 49
2017-06-06 02:00 | 53 | 34 |  |  | 42892.0833 | 50 | 46
2017-06-06 02:30 | 53 | 34 |  |  | 42892.1042 | 50 | 46
2017-06-06 03:00 | 52 | 33 |  |  | 42892.125 | 49 | 45
2017-06-06 03:30 | 52 | 33 |  |  | 42892.1458 | 50 | 45
2017-06-06 04:00 | 52 | 33 |  |  | 42892.1667 | 48 | 44
2017-06-06 04:30 | 51 | 34 |  |  | 42892.1875 | 49 | 45
2017-06-06 05:00 | 52 | 37 |  |  | 42892.2083 | 51 | 48
2017-06-06 05:30 | 54 | 43 |  |  | 42892.2292 | 56 | 54
2017-06-06 06:00 | 55 | 50 |  |  | 42892.25 | 65 | 64
2017-06-06 06:30 | 62 | 59 |  |  | 42892.2708 | 77 | 77
2017-06-06 07:00 | 67 | 64 |  |  | 42892.2917 | 85 | 84
2017-06-06 07:30 | 73 | 70 |  |  | 42892.3125 | 94 | 93
2017-06-06 08:00 | 74 | 69 |  |  | 42892.3333 | 95 | 93
2017-06-06 08:30 | 68 | 63 |  |  | 42892.3542 | 91 | 89
2017-06-06 09:00 | 66 | 61 |  |  | 42892.375 | 87 | 86
2017-06-06 09:30 | 64 | 58 |  |  | 42892.3958 | 83 | 81
2017-06-06 10:00 | 63 | 56 |  |  | 42892.4167 | 82 | 80
2017-06-06 10:30 | 63 | 55 |  |  | 42892.4375 | 79 | 77
2017-06-06 11:00 | 59 | 53 |  |  | 42892.4583 | 75 | 75
2017-06-06 11:30 | 57 | 52 |  |  | 42892.4792 | 74 | 73
2017-06-06 12:00 | 57 | 51 |  |  | 42892.5 | 75 | 74
2017-06-06 12:30 | 60 | 52 |  |  | 42892.5208 | 76 | 74
2017-06-06 13:00 | 58 | 51 |  |  | 42892.5417 | 75 | 73
2017-06-06 13:30 | 58 | 50 |  |  | 42892.5625 | 75 | 73
2017-06-06 14:00 | 59 | 52 |  |  | 42892.5833 | 75 | 73
2017-06-06 14:30 | 61 | 54 |  |  | 42892.6042 | 78 | 76
2017-06-06 15:00 | 61 | 54 |  |  | 42892.625 | 78 | 76
2017-06-06 15:30 | 61 | 54 |  |  | 42892.6458 | 78 | 77
2017-06-06 16:00 | 62 | 55 |  |  | 42892.6667 | 80 | 78
2017-06-06 16:30 | 65 | 57 |  |  | 42892.6875 | 83 | 81
2017-06-06 17:00 | 69 | 57 |  |  | 42892.7083 | 88 | 82
2017-06-06 17:30 | 71 | 60 |  |  | 42892.7292 | 89 | 83
2017-06-06 18:00 | 72 | 61 |  |  | 42892.75 | 91 | 84
2017-06-06 18:30 | 73 | 61 |  |  | 42892.7708 | 90 | 83
2017-06-06 19:00 | 74 | 62 |  |  | 42892.7917 | 89 | 82
2017-06-06 19:30 | 73 | 61 |  |  | 42892.8125 | 89 | 81
2017-06-06 20:00 | 70 | 60 |  |  | 42892.8333 | 86 | 80
2017-06-06 20:30 | 69 | 59 |  |  | 42892.8542 | 84 | 79
2017-06-06 21:00 | 68 | 58 |  |  | 42892.875 | 83 | 76
2017-06-06 21:30 | 66 | 54 |  |  | 42892.8958 | 80 | 71
2017-06-06 22:00 | 69 | 54 |  |  | 42892.9167 | 81 | 73
2017-06-06 22:30 | 73 | 54 |  |  | 42892.9375 | 81 | 73
2017-06-06 23:00 | 71 | 52 |  |  | 42892.9583 | 77 | 70
2017-06-06 23:30 | 68 | 48 |  |  | 42892.9792 | 73 | 65
2017-06-07 | 66 | 45 |  |  | 42893 | 70 | 62
2017-06-07 00:30 | 65 | 40 |  |  | 42893.0208 | 65 | 56
2017-06-07 01:00 | 63 | 36 |  |  | 42893.0417 | 61 | 51
2017-06-07 01:30 | 61 | 32 |  |  | 42893.0625 | 57 | 46
2017-06-07 02:00 | 60 | 30 |  |  | 42893.0833 | 56 | 45
2017-06-07 02:30 | 61 | 31 |  |  | 42893.1042 | 57 | 45
2017-06-07 03:00 | 61 | 29 |  |  | 42893.125 | 56 | 43
2017-06-07 03:30 | 61 | 29 |  |  | 42893.1458 | 56 | 42
2017-06-07 04:00 | 62 | 30 |  |  | 42893.1667 | 57 | 44
2017-06-07 04:30 | 63 | 34 |  |  | 42893.1875 | 59 | 47
2017-06-07 05:00 | 63 | 37 |  |  | 42893.2083 | 61 | 50
2017-06-07 05:30 | 64 | 41 |  |  | 42893.2292 | 65 | 56
2017-06-07 06:00 | 68 | 50 |  |  | 42893.25 | 73 | 66
2017-06-07 06:30 | 67 | 59 |  |  | 42893.2708 | 82 | 79
2017-06-07 07:00 | 68 | 64 |  |  | 42893.2917 | 90 | 88
2017-06-07 07:30 | 73 | 70 |  |  | 42893.3125 | 97 | 96
2017-06-07 08:00 | 70 | 66 |  |  | 42893.3333 | 96 | 93
2017-06-07 08:30 | 68 | 61 |  |  | 42893.3542 | 92 | 89
2017-06-07 09:00 | 68 | 54 |  |  | 42893.375 | 87 | 82
2017-06-07 09:30 | 63 | 48 |  |  | 42893.3958 | 81 | 76
2017-06-07 10:00 | 65 | 45 |  |  | 42893.4167 | 78 | 72
2017-06-07 10:30 | 65 | 43 |  |  | 42893.4375 | 76 | 68
2017-06-07 11:00 | 65 | 42 |  |  | 42893.4583 | 73 | 67
2017-06-07 11:30 | 64 | 41 |  |  | 42893.4792 | 72 | 65
2017-06-07 12:00 | 62 | 41 |  |  | 42893.5 | 70 | 66
2017-06-07 12:30 | 60 | 43 |  |  | 42893.5208 | 71 | 68
2017-06-07 13:00 | 59 | 42 |  |  | 42893.5417 | 70 | 67
2017-06-07 13:30 | 59 | 43 |  |  | 42893.5625 | 71 | 68
2017-06-07 14:00 | 60 | 44 |  |  | 42893.5833 | 71 | 69
2017-06-07 14:30 | 61 | 46 |  |  | 42893.6042 | 73 | 71
2017-06-07 15:00 | 62 | 47 |  |  | 42893.625 | 75 | 73
2017-06-07 15:30 | 64 | 50 |  |  | 42893.6458 | 79 | 76
2017-06-07 16:00 | 67 | 52 |  |  | 42893.6667 | 82 | 79
2017-06-07 16:30 | 68 | 56 |  |  | 42893.6875 | 85 | 82
2017-06-07 17:00 | 72 | 60 |  |  | 42893.7083 | 89 | 86
2017-06-07 17:30 | 81 | 68 |  |  | 42893.7292 | 97 | 93
2017-06-07 18:00 | 84 | 71 |  |  | 42893.75 | 99 | 94
2017-06-07 18:30 | 84 | 69 |  |  | 42893.7708 | 96 | 90
2017-06-07 19:00 | 86 | 72 |  |  | 42893.7917 | 99 | 92
2017-06-07 19:30 | 85 | 70 |  |  | 42893.8125 | 98 | 92
2017-06-07 20:00 | 82 | 68 |  |  | 42893.8333 | 96 | 91
2017-06-07 20:30 | 79 | 64 |  |  | 42893.8542 | 92 | 87
2017-06-07 21:00 | 76 | 61 |  |  | 42893.875 | 89 | 83
2017-06-07 21:30 | 76 | 59 |  |  | 42893.8958 | 86 | 79
2017-06-07 22:00 | 74 | 57 |  |  | 42893.9167 | 84 | 78
2017-06-07 22:30 | 71 | 53 |  |  | 42893.9375 | 80 | 73
2017-06-07 23:00 | 69 | 51 |  |  | 42893.9583 | 78 | 71
2017-06-07 23:30 | 67 | 47 |  |  | 42893.9792 | 73 | 66
2017-06-08 | 64 | 41 |  |  | 42894 | 69 | 61
2017-06-08 00:30 | 65 | 38 |  |  | 42894.0208 | 66 | 56
2017-06-08 01:00 | 65 | 36 |  |  | 42894.0417 | 63 | 52
2017-06-08 01:30 | 65 | 32 |  |  | 42894.0625 | 60 | 48
2017-06-08 02:00 | 62 | 28 |  |  | 42894.0833 | 56 | 43
2017-06-08 02:30 | 62 | 27 |  |  | 42894.1042 | 56 | 43
2017-06-08 03:00 | 62 | 27 |  |  | 42894.125 | 55 | 42
2017-06-08 03:30 | 62 | 26 |  |  | 42894.1458 | 55 | 41
2017-06-08 04:00 | 62 | 26 |  |  | 42894.1667 | 54 | 41
2017-06-08 04:30 | 62 | 28 |  |  | 42894.1875 | 56 | 43
2017-06-08 05:00 | 62 | 32 |  |  | 42894.2083 | 59 | 47
2017-06-08 05:30 | 65 | 40 |  |  | 42894.2292 | 65 | 56
2017-06-08 06:00 | 68 | 48 |  |  | 42894.25 | 71 | 64
2017-06-08 06:30 | 67 | 58 |  |  | 42894.2708 | 81 | 78
2017-06-08 07:00 | 68 | 64 |  |  | 42894.2917 | 90 | 88
2017-06-08 07:30 | 74 | 71 |  |  | 42894.3125 | 99 | 98
2017-06-08 08:00 | 71 | 68 |  |  | 42894.3333 | 98 | 97
2017-06-08 08:30 | 66 | 62 |  |  | 42894.3542 | 92 | 91
2017-06-08 09:00 | 58 | 54 |  |  | 42894.375 | 84 | 84
2017-06-08 09:30 | 56 | 50 |  |  | 42894.3958 | 78 | 77
2017-06-08 10:00 | 55 | 47 |  |  | 42894.4167 | 75 | 74
2017-06-08 10:30 | 54 | 47 |  |  | 42894.4375 | 74 | 73
2017-06-08 11:00 | 52 | 45 |  |  | 42894.4583 | 72 | 71
2017-06-08 11:30 | 58 | 45 |  |  | 42894.4792 | 71 | 70
2017-06-08 12:00 | 56 | 42 |  |  | 42894.5 | 69 | 67
2017-06-08 12:30 | 55 | 41 |  |  | 42894.5208 | 68 | 66
2017-06-08 13:00 | 57 | 45 |  |  | 42894.5417 | 71 | 69
2017-06-08 13:30 | 58 | 47 |  |  | 42894.5625 | 72 | 71
2017-06-08 14:00 | 60 | 51 |  |  | 42894.5833 | 74 | 73
2017-06-08 14:30 | 61 | 51 |  |  | 42894.6042 | 75 | 74
2017-06-08 15:00 | 62 | 52 |  |  | 42894.625 | 76 | 75
2017-06-08 15:30 | 64 | 54 |  |  | 42894.6458 | 78 | 77
2017-06-08 16:00 | 70 | 61 |  |  | 42894.6667 | 85 | 83
2017-06-08 16:30 | 74 | 63 |  |  | 42894.6875 | 89 | 87
2017-06-08 17:00 | 78 | 67 |  |  | 42894.7083 | 93 | 91
2017-06-08 17:30 | 77 | 73 |  |  | 42894.7292 | 98 | 97
2017-06-08 18:00 | 80 | 75 |  |  | 42894.75 | 102 | 98
2017-06-08 18:30 | 79 | 72 |  |  | 42894.7708 | 98 | 94
2017-06-08 19:00 | 80 | 73 |  |  | 42894.7917 | 100 | 95
2017-06-08 19:30 | 81 | 74 |  |  | 42894.8125 | 101 | 96
2017-06-08 20:00 | 80 | 72 |  |  | 42894.8333 | 99 | 93
2017-06-08 20:30 | 78 | 70 |  |  | 42894.8542 | 97 | 91
2017-06-08 21:00 | 75 | 67 |  |  | 42894.875 | 94 | 88
2017-06-08 21:30 | 71 | 64 |  |  | 42894.8958 | 88 | 83
2017-06-08 22:00 | 68 | 62 |  |  | 42894.9167 | 85 | 82
2017-06-08 22:30 | 66 | 61 |  |  | 42894.9375 | 82 | 79
2017-06-08 23:00 | 66 | 58 |  |  | 42894.9583 | 79 | 75
2017-06-08 23:30 | 64 | 54 |  |  | 42894.9792 | 75 | 71
2017-06-09 | 60 | 50 |  |  | 42895 | 71 | 66
2017-06-09 00:30 | 58 | 46 |  |  | 42895.0208 | 66 | 61
2017-06-09 01:00 | 55 | 42 |  |  | 42895.0417 | 61 | 55
2017-06-09 01:30 | 54 | 38 |  |  | 42895.0625 | 58 | 51
2017-06-09 02:00 | 52 | 35 |  |  | 42895.0833 | 55 | 48
2017-06-09 02:30 | 60 | 34 |  |  | 42895.1042 | 57 | 45
2017-06-09 03:00 | 65 | 32 |  |  | 42895.125 | 58 | 43
2017-06-09 03:30 | 66 | 32 |  |  | 42895.1458 | 58 | 44
2017-06-09 04:00 | 64 | 31 |  |  | 42895.1667 | 56 | 41
2017-06-09 04:30 | 65 | 32 |  |  | 42895.1875 | 58 | 43
2017-06-09 05:00 | 66 | 36 |  |  | 42895.2083 | 60 | 47
2017-06-09 05:30 | 67 | 42 |  |  | 42895.2292 | 65 | 55
2017-06-09 06:00 | 71 | 52 |  |  | 42895.25 | 73 | 66
2017-06-09 06:30 | 74 | 62 |  |  | 42895.2708 | 90 | 80
2017-06-09 07:00 | 84 | 71 |  |  | 42895.2917 | 104 | 93
2017-06-09 07:30 | 89 | 76 |  |  | 42895.3125 | 112 | 101
2017-06-09 08:00 | 92 | 73 |  |  | 42895.3333 | 115 | 99
2017-06-09 08:30 | 88 | 67 |  |  | 42895.3542 | 110 | 95
2017-06-09 09:00 | 95 | 65 |  |  | 42895.375 | 112 | 91
2017-06-09 09:30 | 96 | 63 |  |  | 42895.3958 | 109 | 88
2017-06-09 10:00 | 83 | 59 |  |  | 42895.4167 | 91 | 82
2017-06-09 10:30 | 75 | 56 |  |  | 42895.4375 | 82 | 78
2017-06-09 11:00 | 74 | 54 |  |  | 42895.4583 | 80 | 76
2017-06-09 11:30 | 73 | 53 |  |  | 42895.4792 | 79 | 74
2017-06-09 12:00 | 47 | 37 |  |  | 42895.5 | 68 | 67
2017-06-09 12:30 | 47 | 36 |  |  | 42895.5208 | 69 | 67
2017-06-09 13:00 | 47 | 36 |  |  | 42895.5417 | 70 | 69
2017-06-09 13:30 | 50 | 39 |  |  | 42895.5625 | 71 | 70
2017-06-09 14:00 | 48 | 37 |  |  | 42895.5833 | 71 | 70
2017-06-09 14:30 | 48 | 37 |  |  | 42895.6042 | 71 | 70
2017-06-09 15:00 | 49 | 38 |  |  | 42895.625 | 71 | 69
2017-06-09 15:30 | 49 | 38 |  |  | 42895.6458 | 72 | 70
2017-06-09 16:00 | 50 | 38 |  |  | 42895.6667 | 72 | 70
2017-06-09 16:30 | 51 | 39 |  |  | 42895.6875 | 74 | 71
2017-06-09 17:00 | 50 | 39 |  |  | 42895.7083 | 75 | 73
2017-06-09 17:30 | 48 | 40 |  |  | 42895.7292 | 76 | 74
2017-06-09 18:00 | 48 | 40 |  |  | 42895.75 | 75 | 72
2017-06-09 18:30 | 48 | 39 |  |  | 42895.7708 | 73 | 69
2017-06-09 19:00 | 48 | 39 |  |  | 42895.7917 | 74 | 71
2017-06-09 19:30 | 48 | 39 |  |  | 42895.8125 | 72 | 69
2017-06-09 20:00 | 45 | 38 |  |  | 42895.8333 | 70 | 68
2017-06-09 20:30 | 47 | 36 |  |  | 42895.8542 | 69 | 66
2017-06-09 21:00 | 52 | 34 |  |  | 42895.875 | 67 | 62
2017-06-09 21:30 | 51 | 30 |  |  | 42895.8958 | 63 | 57
2017-06-09 22:00 | 51 | 30 |  |  | 42895.9167 | 64 | 58
2017-06-09 22:30 | 51 | 30 |  |  | 42895.9375 | 64 | 58
2017-06-09 23:00 | 50 | 30 |  |  | 42895.9583 | 63 | 57
2017-06-09 23:30 | 49 | 28 |  |  | 42895.9792 | 60 | 53
2017-06-10 | 50 | 28 |  |  | 42896 | 59 | 52
2017-06-10 00:30 | 48 | 24 |  |  | 42896.0208 | 55 | 47
2017-06-10 01:00 | 49 | 24 |  |  | 42896.0417 | 53 | 45
2017-06-10 01:30 | 48 | 22 |  |  | 42896.0625 | 51 | 42
2017-06-10 02:00 | 47 | 20 |  |  | 42896.0833 | 49 | 39
2017-06-10 02:30 | 46 | 19 |  |  | 42896.1042 | 48 | 38
2017-06-10 03:00 | 46 | 18 |  |  | 42896.125 | 47 | 36
2017-06-10 03:30 | 46 | 18 |  |  | 42896.1458 | 46 | 35
2017-06-10 04:00 | 46 | 17 |  |  | 42896.1667 | 45 | 34
2017-06-10 04:30 | 46 | 17 |  |  | 42896.1875 | 45 | 34
2017-06-10 05:00 | 45 | 17 |  |  | 42896.2083 | 45 | 34
2017-06-10 05:30 | 44 | 17 |  |  | 42896.2292 | 47 | 36
2017-06-10 06:00 | 45 | 20 |  |  | 42896.25 | 49 | 40
2017-06-10 06:30 | 46 | 21 |  |  | 42896.2708 | 51 | 43
2017-06-10 07:00 | 45 | 23 |  |  | 42896.2917 | 54 | 47
2017-06-10 07:30 | 47 | 25 |  |  | 42896.3125 | 57 | 50
2017-06-10 08:00 | 46 | 26 |  |  | 42896.3333 | 58 | 52
2017-06-10 08:30 | 47 | 27 |  |  | 42896.3542 | 59 | 54
2017-06-10 09:00 | 43 | 24 |  |  | 42896.375 | 54 | 50
2017-06-10 09:30 | 41 | 22 |  |  | 42896.3958 | 53 | 48
2017-06-10 10:00 | 42 | 23 |  |  | 42896.4167 | 51 | 47
2017-06-10 10:30 | 43 | 23 |  |  | 42896.4375 | 50 | 46
2017-06-10 11:00 | 42 | 23 |  |  | 42896.4583 | 51 | 46
2017-06-10 11:30 | 42 | 24 |  |  | 42896.4792 | 52 | 48
2017-06-10 12:00 | 42 | 24 |  |  | 42896.5 | 52 | 48
2017-06-10 12:30 | 45 | 27 |  |  | 42896.5208 | 51 | 47
2017-06-10 13:00 | 44 | 27 |  |  | 42896.5417 | 53 | 48
2017-06-10 13:30 | 44 | 26 |  |  | 42896.5625 | 52 | 47
2017-06-10 14:00 | 43 | 23 |  |  | 42896.5833 | 51 | 46
2017-06-10 14:30 | 43 | 24 |  |  | 42896.6042 | 51 | 46
2017-06-10 15:00 | 42 | 23 |  |  | 42896.625 | 51 | 47
2017-06-10 15:30 | 43 | 23 |  |  | 42896.6458 | 51 | 45
2017-06-10 16:00 | 44 | 25 |  |  | 42896.6667 | 54 | 49
2017-06-10 16:30 | 46 | 27 |  |  | 42896.6875 | 57 | 52
2017-06-10 17:00 | 48 | 30 |  |  | 42896.7083 | 61 | 57
2017-06-10 17:30 | 52 | 34 |  |  | 42896.7292 | 66 | 62
2017-06-10 18:00 | 53 | 34 |  |  | 42896.75 | 67 | 62
2017-06-10 18:30 | 53 | 34 |  |  | 42896.7708 | 67 | 63
2017-06-10 19:00 | 54 | 36 |  |  | 42896.7917 | 69 | 64
2017-06-10 19:30 | 52 | 34 |  |  | 42896.8125 | 66 | 62
2017-06-10 20:00 | 53 | 34 |  |  | 42896.8333 | 67 | 63
2017-06-10 20:30 | 53 | 33 |  |  | 42896.8542 | 67 | 62
2017-06-10 21:00 | 51 | 31 |  |  | 42896.875 | 65 | 59
2017-06-10 21:30 | 51 | 30 |  |  | 42896.8958 | 63 | 57
2017-06-10 22:00 | 52 | 32 |  |  | 42896.9167 | 66 | 61
2017-06-10 22:30 | 52 | 32 |  |  | 42896.9375 | 66 | 60
2017-06-10 23:00 | 53 | 31 |  |  | 42896.9583 | 65 | 58
2017-06-10 23:30 | 51 | 28 |  |  | 42896.9792 | 62 | 55
2017-06-11 | 50 | 28 |  |  | 42897 | 60 | 54
2017-06-11 00:30 | 49 | 26 |  |  | 42897.0208 | 55 | 47
2017-06-11 01:00 | 48 | 23 |  |  | 42897.0417 | 53 | 44
2017-06-11 01:30 | 48 | 22 |  |  | 42897.0625 | 52 | 42
2017-06-11 02:00 | 46 | 20 |  |  | 42897.0833 | 50 | 40
2017-06-11 02:30 | 46 | 21 |  |  | 42897.1042 | 48 | 41
2017-06-11 03:00 | 43 | 21 |  |  | 42897.125 | 45 | 40
2017-06-11 03:30 | 44 | 21 |  |  | 42897.1458 | 46 | 41
2017-06-11 04:00 | 43 | 21 |  |  | 42897.1667 | 46 | 41
2017-06-11 04:30 | 41 | 21 |  |  | 42897.1875 | 45 | 40
2017-06-11 05:00 | 43 | 22 |  |  | 42897.2083 | 46 | 41
2017-06-11 05:30 | 43 | 22 |  |  | 42897.2292 | 46 | 41
2017-06-11 06:00 | 44 | 23 |  |  | 42897.25 | 48 | 43
2017-06-11 06:30 | 44 | 23 |  |  | 42897.2708 | 51 | 46
2017-06-11 07:00 | 44 | 24 |  |  | 42897.2917 | 52 | 48
2017-06-11 07:30 | 45 | 25 |  |  | 42897.3125 | 54 | 50
2017-06-11 08:00 | 46 | 27 |  |  | 42897.3333 | 56 | 53
2017-06-11 08:30 | 47 | 29 |  |  | 42897.3542 | 63 | 60
2017-06-11 09:00 | 49 | 34 |  |  | 42897.375 | 66 | 64
2017-06-11 09:30 | 49 | 34 |  |  | 42897.3958 | 66 | 64
2017-06-11 10:00 | 49 | 34 |  |  | 42897.4167 | 65 | 63
2017-06-11 10:30 | 49 | 34 |  |  | 42897.4375 | 63 | 61
2017-06-11 11:00 | 50 | 36 |  |  | 42897.4583 | 64 | 62
2017-06-11 11:30 | 51 | 36 |  |  | 42897.4792 | 66 | 64
2017-06-11 12:00 | 50 | 35 |  |  | 42897.5 | 66 | 63
2017-06-11 12:30 | 50 | 35 |  |  | 42897.5208 | 65 | 63
2017-06-11 13:00 | 48 | 33 |  |  | 42897.5417 | 61 | 59
2017-06-11 13:30 | 48 | 32 |  |  | 42897.5625 | 62 | 60
2017-06-11 14:00 | 49 | 34 |  |  | 42897.5833 | 61 | 58
2017-06-11 14:30 | 48 | 33 |  |  | 42897.6042 | 60 | 57
2017-06-11 15:00 | 49 | 32 |  |  | 42897.625 | 60 | 57
2017-06-11 15:30 | 49 | 32 |  |  | 42897.6458 | 60 | 57
2017-06-11 16:00 | 50 | 33 |  |  | 42897.6667 | 62 | 60
2017-06-11 16:30 | 51 | 35 |  |  | 42897.6875 | 66 | 64
2017-06-11 17:00 | 53 | 38 |  |  | 42897.7083 | 71 | 68
2017-06-11 17:30 | 55 | 42 |  |  | 42897.7292 | 73 | 71
2017-06-11 18:00 | 55 | 41 |  |  | 42897.75 | 73 | 71
2017-06-11 18:30 | 55 | 42 |  |  | 42897.7708 | 74 | 71
2017-06-11 19:00 | 56 | 43 |  |  | 42897.7917 | 75 | 73
2017-06-11 19:30 | 55 | 42 |  |  | 42897.8125 | 74 | 72
2017-06-11 20:00 | 54 | 41 |  |  | 42897.8333 | 73 | 71
2017-06-11 20:30 | 55 | 41 |  |  | 42897.8542 | 73 | 71
2017-06-11 21:00 | 54 | 40 |  |  | 42897.875 | 70 | 68
2017-06-11 21:30 | 54 | 39 |  |  | 42897.8958 | 69 | 67
2017-06-11 22:00 | 54 | 39 |  |  | 42897.9167 | 71 | 68
2017-06-11 22:30 | 55 | 40 |  |  | 42897.9375 | 71 | 68
2017-06-11 23:00 | 52 | 37 |  |  | 42897.9583 | 68 | 65
2017-06-11 23:30 | 50 | 36 |  |  | 42897.9792 | 65 | 63
2017-06-12 | 50 | 35 |  |  | 42898 | 62 | 59
2017-06-12 00:30 | 48 | 32 |  |  | 42898.0208 | 57 | 54
2017-06-12 01:00 | 47 | 29 |  |  | 42898.0417 | 53 | 50
2017-06-12 01:30 | 46 | 26 |  |  | 42898.0625 | 49 | 45
2017-06-12 02:00 | 43 | 23 |  |  | 42898.0833 | 46 | 42
2017-06-12 02:30 | 43 | 21 |  |  | 42898.1042 | 43 | 39
2017-06-12 03:00 | 41 | 18 |  |  | 42898.125 | 41 | 36
2017-06-12 03:30 | 41 | 18 |  |  | 42898.1458 | 40 | 35
2017-06-12 04:00 | 40 | 17 |  |  | 42898.1667 | 40 | 36
2017-06-12 04:30 | 41 | 20 |  |  | 42898.1875 | 41 | 37
2017-06-12 05:00 | 41 | 21 |  |  | 42898.2083 | 44 | 40
2017-06-12 05:30 | 43 | 25 |  |  | 42898.2292 | 49 | 45
2017-06-12 06:00 | 45 | 31 |  |  | 42898.25 | 56 | 53
2017-06-12 06:30 | 47 | 38 |  |  | 42898.2708 | 65 | 65
2017-06-12 07:00 | 49 | 43 |  |  | 42898.2917 | 75 | 74
2017-06-12 07:30 | 48 | 47 |  |  | 42898.3125 | 82 | 82
2017-06-12 08:00 | 49 | 47 |  |  | 42898.3333 | 83 | 83
2017-06-12 08:30 | 45 | 44 |  |  | 42898.3542 | 80 | 80
2017-06-12 09:00 | 40 | 39 |  |  | 42898.375 | 72 | 72
2017-06-12 09:30 | 40 | 39 |  |  | 42898.3958 | 71 | 71
2017-06-12 10:00 | 41 | 40 |  |  | 42898.4167 | 71 | 71
2017-06-12 10:30 | 43 | 42 |  |  | 42898.4375 | 74 | 74
2017-06-12 11:00 | 44 | 43 |  |  | 42898.4583 | 75 | 75
2017-06-12 11:30 | 42 | 42 |  |  | 42898.4792 | 73 | 73
2017-06-12 12:00 | 42 | 41 |  |  | 42898.5 | 70 | 70
2017-06-12 12:30 | 43 | 42 |  |  | 42898.5208 | 74 | 74
2017-06-12 13:00 | 45 | 44 |  |  | 42898.5417 | 75 | 75
2017-06-12 13:30 | 46 | 45 |  |  | 42898.5625 | 76 | 76
2017-06-12 14:00 | 45 | 44 |  |  | 42898.5833 | 75 | 75
2017-06-12 14:30 | 43 | 42 |  |  | 42898.6042 | 73 | 73
2017-06-12 15:00 | 42 | 40 |  |  | 42898.625 | 72 | 72
2017-06-12 15:30 | 43 | 42 |  |  | 42898.6458 | 74 | 74
2017-06-12 16:00 | 44 | 42 |  |  | 42898.6667 | 76 | 76
2017-06-12 16:30 | 43 | 42 |  |  | 42898.6875 | 76 | 76
2017-06-12 17:00 | 45 | 44 |  |  | 42898.7083 | 78 | 78
2017-06-12 17:30 | 46 | 45 |  |  | 42898.7292 | 79 | 79
2017-06-12 18:00 | 46 | 45 |  |  | 42898.75 | 78 | 78
2017-06-12 18:30 | 46 | 46 |  |  | 42898.7708 | 76 | 76
2017-06-12 19:00 | 48 | 47 |  |  | 42898.7917 | 78 | 78
2017-06-12 19:30 | 49 | 47 |  |  | 42898.8125 | 78 | 78
2017-06-12 20:00 | 47 | 46 |  |  | 42898.8333 | 77 | 77
2017-06-12 20:30 | 47 | 46 |  |  | 42898.8542 | 76 | 76
2017-06-12 21:00 | 45 | 44 |  |  | 42898.875 | 74 | 74
2017-06-12 21:30 | 41 | 39 |  |  | 42898.8958 | 67 | 67
2017-06-12 22:00 | 42 | 36 |  |  | 42898.9167 | 65 | 65
2017-06-12 22:30 | 45 | 35 |  |  | 42898.9375 | 65 | 63
2017-06-12 23:00 | 45 | 33 |  |  | 42898.9583 | 59 | 58
2017-06-12 23:30 | 43 | 30 |  |  | 42898.9792 | 57 | 56
2017-06-13 | 43 | 30 |  |  | 42899 | 55 | 54
2017-06-13 00:30 | 44 | 29 |  |  | 42899.0208 | 53 | 51
2017-06-13 01:00 | 42 | 27 |  |  | 42899.0417 | 48 | 46
2017-06-13 01:30 | 41 | 24 |  |  | 42899.0625 | 45 | 43
2017-06-13 02:00 | 41 | 22 |  |  | 42899.0833 | 43 | 41
2017-06-13 02:30 | 41 | 22 |  |  | 42899.1042 | 41 | 39
2017-06-13 03:00 | 40 | 22 |  |  | 42899.125 | 41 | 39
2017-06-13 03:30 | 38 | 20 |  |  | 42899.1458 | 40 | 38
2017-06-13 04:00 | 38 | 19 |  |  | 42899.1667 | 38 | 36
2017-06-13 04:30 | 39 | 19 |  |  | 42899.1875 | 39 | 37
2017-06-13 05:00 | 37 | 20 |  |  | 42899.2083 | 40 | 38
2017-06-13 05:30 | 39 | 24 |  |  | 42899.2292 | 46 | 44
2017-06-13 06:00 | 41 | 30 |  |  | 42899.25 | 52 | 51
2017-06-13 06:30 | 40 | 35 |  |  | 42899.2708 | 63 | 62
2017-06-13 07:00 | 41 | 40 |  |  | 42899.2917 | 72 | 72
2017-06-13 07:30 | 45 | 45 |  |  | 42899.3125 | 81 | 81
2017-06-13 08:00 | 45 | 43 |  |  | 42899.3333 | 80 | 79
2017-06-13 08:30 | 42 | 40 |  |  | 42899.3542 | 78 | 77
2017-06-13 09:00 | 44 | 42 |  |  | 42899.375 | 80 | 79
2017-06-13 09:30 | 45 | 43 |  |  | 42899.3958 | 80 | 79
2017-06-13 10:00 | 46 | 43 |  |  | 42899.4167 | 80 | 80
2017-06-13 10:30 | 47 | 45 |  |  | 42899.4375 | 82 | 81
2017-06-13 11:00 | 48 | 46 |  |  | 42899.4583 | 83 | 82
2017-06-13 11:30 | 48 | 46 |  |  | 42899.4792 | 82 | 82
2017-06-13 12:00 | 48 | 45 |  |  | 42899.5 | 84 | 83
2017-06-13 12:30 | 48 | 46 |  |  | 42899.5208 | 86 | 85
2017-06-13 13:00 | 48 | 46 |  |  | 42899.5417 | 87 | 86
2017-06-13 13:30 | 50 | 48 |  |  | 42899.5625 | 89 | 88
2017-06-13 14:00 | 49 | 47 |  |  | 42899.5833 | 87 | 86
2017-06-13 14:30 | 47 | 44 |  |  | 42899.6042 | 82 | 82
2017-06-13 15:00 | 48 | 44 |  |  | 42899.625 | 83 | 82
2017-06-13 15:30 | 49 | 44 |  |  | 42899.6458 | 84 | 82
2017-06-13 16:00 | 48 | 44 |  |  | 42899.6667 | 84 | 83
2017-06-13 16:30 | 50 | 46 |  |  | 42899.6875 | 85 | 84
2017-06-13 17:00 | 53 | 49 |  |  | 42899.7083 | 90 | 88
2017-06-13 17:30 | 54 | 49 |  |  | 42899.7292 | 90 | 86
2017-06-13 18:00 | 52 | 46 |  |  | 42899.75 | 87 | 82
2017-06-13 18:30 | 43 | 36 |  |  | 42899.7708 | 81 | 76
2017-06-13 19:00 | 41 | 34 |  |  | 42899.7917 | 80 | 75
2017-06-13 19:30 | 46 | 33 |  |  | 42899.8125 | 81 | 74
2017-06-13 20:00 | 46 | 31 |  |  | 42899.8333 | 78 | 70
2017-06-13 20:30 | 45 | 29 |  |  | 42899.8542 | 76 | 67
2017-06-13 21:00 | 43 | 27 |  |  | 42899.875 | 70 | 64
2017-06-13 21:30 | 46 | 34 |  |  | 42899.8958 | 69 | 65
2017-06-13 22:00 | 43 | 34 |  |  | 42899.9167 | 66 | 65
2017-06-13 22:30 | 42 | 34 |  |  | 42899.9375 | 64 | 63
2017-06-13 23:00 | 41 | 33 |  |  | 42899.9583 | 60 | 59
2017-06-13 23:30 | 48 | 30 |  |  | 42899.9792 | 58 | 55
2017-06-14 | 44 | 30 |  |  | 42900 | 56 | 54
2017-06-14 00:30 | 41 | 25 |  |  | 42900.0208 | 49 | 48
2017-06-14 01:00 | 41 | 22 |  |  | 42900.0417 | 45 | 44
2017-06-14 01:30 | 40 | 21 |  |  | 42900.0625 | 43 | 40
2017-06-14 02:00 | 39 | 19 |  |  | 42900.0833 | 40 | 37
2017-06-14 02:30 | 38 | 20 |  |  | 42900.1042 | 40 | 37
2017-06-14 03:00 | 39 | 19 |  |  | 42900.125 | 39 | 37
2017-06-14 03:30 | 37 | 18 |  |  | 42900.1458 | 39 | 36
2017-06-14 04:00 | 38 | 18 |  |  | 42900.1667 | 39 | 36
2017-06-14 04:30 | 38 | 19 |  |  | 42900.1875 | 39 | 36
2017-06-14 05:00 | 38 | 20 |  |  | 42900.2083 | 41 | 38
2017-06-14 05:30 | 39 | 23 |  |  | 42900.2292 | 45 | 43
2017-06-14 06:00 | 43 | 28 |  |  | 42900.25 | 54 | 51
2017-06-14 06:30 | 46 | 32 |  |  | 42900.2708 | 62 | 60
2017-06-14 07:00 | 47 | 37 |  |  | 42900.2917 | 70 | 68
2017-06-14 07:30 | 50 | 42 |  |  | 42900.3125 | 80 | 79
2017-06-14 08:00 | 53 | 45 |  |  | 42900.3333 | 84 | 83
2017-06-14 08:30 | 55 | 46 |  |  | 42900.3542 | 86 | 85
2017-06-14 09:00 | 53 | 44 |  |  | 42900.375 | 82 | 81
2017-06-14 09:30 | 54 | 45 |  |  | 42900.3958 | 84 | 83
2017-06-14 10:00 | 56 | 48 |  |  | 42900.4167 | 84 | 83
2017-06-14 10:30 | 54 | 46 |  |  | 42900.4375 | 81 | 80
2017-06-14 11:00 | 54 | 45 |  |  | 42900.4583 | 78 | 76
2017-06-14 11:30 | 53 | 44 |  |  | 42900.4792 | 75 | 74
2017-06-14 12:00 | 50 | 41 |  |  | 42900.5 | 74 | 73
2017-06-14 12:30 | 50 | 42 |  |  | 42900.5208 | 74 | 73
2017-06-14 13:00 | 51 | 43 |  |  | 42900.5417 | 80 | 79
2017-06-14 13:30 | 53 | 45 |  |  | 42900.5625 | 80 | 79
2017-06-14 14:00 | 53 | 45 |  |  | 42900.5833 | 80 | 79
2017-06-14 14:30 | 52 | 44 |  |  | 42900.6042 | 78 | 77
2017-06-14 15:00 | 49 | 40 |  |  | 42900.625 | 75 | 74
2017-06-14 15:30 | 50 | 41 |  |  | 42900.6458 | 77 | 76
2017-06-14 16:00 | 51 | 42 |  |  | 42900.6667 | 79 | 78
2017-06-14 16:30 | 52 | 43 |  |  | 42900.6875 | 81 | 79
2017-06-14 17:00 | 50 | 46 |  |  | 42900.7083 | 85 | 84
2017-06-14 17:30 | 52 | 47 |  |  | 42900.7292 | 86 | 85
2017-06-14 18:00 | 52 | 46 |  |  | 42900.75 | 85 | 83
2017-06-14 18:30 | 52 | 45 |  |  | 42900.7708 | 83 | 80
2017-06-14 19:00 | 53 | 46 |  |  | 42900.7917 | 84 | 81
2017-06-14 19:30 | 53 | 47 |  |  | 42900.8125 | 84 | 81
2017-06-14 20:00 | 51 | 45 |  |  | 42900.8333 | 81 | 78
2017-06-14 20:30 | 48 | 42 |  |  | 42900.8542 | 78 | 75
2017-06-14 21:00 | 44 | 40 |  |  | 42900.875 | 74 | 72
2017-06-14 21:30 | 40 | 36 |  |  | 42900.8958 | 66 | 66
2017-06-14 22:00 | 40 | 36 |  |  | 42900.9167 | 68 | 66
2017-06-14 22:30 | 39 | 34 |  |  | 42900.9375 | 66 | 65
2017-06-14 23:00 | 38 | 33 |  |  | 42900.9583 | 63 | 61
2017-06-14 23:30 | 35 | 30 |  |  | 42900.9792 | 58 | 56
2017-06-15 | 34 | 28 |  |  | 42901 | 55 | 53
2017-06-15 00:30 | 35 | 25 |  |  | 42901.0208 | 51 | 48
2017-06-15 01:00 | 35 | 24 |  |  | 42901.0417 | 48 | 45
2017-06-15 01:30 | 34 | 22 |  |  | 42901.0625 | 45 | 42
2017-06-15 02:00 | 32 | 20 |  |  | 42901.0833 | 43 | 40
2017-06-15 02:30 | 31 | 18 |  |  | 42901.1042 | 42 | 38
2017-06-15 03:00 | 31 | 19 |  |  | 42901.125 | 43 | 39
2017-06-15 03:30 | 32 | 19 |  |  | 42901.1458 | 43 | 40
2017-06-15 04:00 | 30 | 17 |  |  | 42901.1667 | 42 | 38
2017-06-15 04:30 | 30 | 19 |  |  | 42901.1875 | 43 | 39
2017-06-15 05:00 | 30 | 19 |  |  | 42901.2083 | 44 | 41
2017-06-15 05:30 | 32 | 23 |  |  | 42901.2292 | 48 | 46
2017-06-15 06:00 | 33 | 27 |  |  | 42901.25 | 54 | 53
2017-06-15 06:30 | 37 | 31 |  |  | 42901.2708 | 62 | 61
2017-06-15 07:00 | 43 | 37 |  |  | 42901.2917 | 73 | 69
2017-06-15 07:30 | 45 | 40 |  |  | 42901.3125 | 78 | 76
2017-06-15 08:00 | 45 | 41 |  |  | 42901.3333 | 79 | 77
2017-06-15 08:30 | 47 | 43 |  |  | 42901.3542 | 81 | 80
2017-06-15 09:00 | 46 | 44 |  |  | 42901.375 | 80 | 79
2017-06-15 09:30 | 43 | 40 |  |  | 42901.3958 | 75 | 74
2017-06-15 10:00 | 43 | 40 |  |  | 42901.4167 | 73 | 72
2017-06-15 10:30 | 43 | 40 |  |  | 42901.4375 | 74 | 73
2017-06-15 11:00 | 44 | 41 |  |  | 42901.4583 | 76 | 75
2017-06-15 11:30 | 46 | 43 |  |  | 42901.4792 | 80 | 80
2017-06-15 12:00 | 44 | 41 |  |  | 42901.5 | 75 | 74
2017-06-15 12:30 | 42 | 38 |  |  | 42901.5208 | 71 | 70
2017-06-15 13:00 | 43 | 40 |  |  | 42901.5417 | 75 | 73
2017-06-15 13:30 | 43 | 40 |  |  | 42901.5625 | 76 | 75
2017-06-15 14:00 | 45 | 42 |  |  | 42901.5833 | 78 | 77
2017-06-15 14:30 | 45 | 42 |  |  | 42901.6042 | 76 | 75
2017-06-15 15:00 | 44 | 41 |  |  | 42901.625 | 75 | 74
2017-06-15 15:30 | 43 | 40 |  |  | 42901.6458 | 75 | 74
2017-06-15 16:00 | 44 | 40 |  |  | 42901.6667 | 76 | 75
2017-06-15 16:30 | 45 | 41 |  |  | 42901.6875 | 78 | 76
2017-06-15 17:00 | 49 | 44 |  |  | 42901.7083 | 81 | 80
2017-06-15 17:30 | 51 | 45 |  |  | 42901.7292 | 83 | 80
2017-06-15 18:00 | 47 | 44 |  |  | 42901.75 | 82 | 79
2017-06-15 18:30 | 48 | 44 |  |  | 42901.7708 | 82 | 78
2017-06-15 19:00 | 47 | 44 |  |  | 42901.7917 | 83 | 79
2017-06-15 19:30 | 48 | 45 |  |  | 42901.8125 | 80 | 78
2017-06-15 20:00 | 44 | 43 |  |  | 42901.8333 | 76 | 76
2017-06-15 20:30 | 41 | 41 |  |  | 42901.8542 | 74 | 74
2017-06-15 21:00 | 39 | 38 |  |  | 42901.875 | 70 | 70
2017-06-15 21:30 | 36 | 36 |  |  | 42901.8958 | 66 | 66
2017-06-15 22:00 | 35 | 35 |  |  | 42901.9167 | 65 | 65
2017-06-15 22:30 | 36 | 36 |  |  | 42901.9375 | 66 | 66
2017-06-15 23:00 | 36 | 35 |  |  | 42901.9583 | 63 | 63
2017-06-15 23:30 | 35 | 34 |  |  | 42901.9792 | 61 | 61
2017-06-16 | 32 | 31 |  |  | 42902 | 57 | 57
2017-06-16 00:30 | 30 | 29 |  |  | 42902.0208 | 53 | 53
2017-06-16 01:00 | 29 | 26 |  |  | 42902.0417 | 47 | 47
2017-06-16 01:30 | 26 | 23 |  |  | 42902.0625 | 44 | 44
2017-06-16 02:00 | 24 | 22 |  |  | 42902.0833 | 43 | 43
2017-06-16 02:30 | 24 | 21 |  |  | 42902.1042 | 41 | 41
2017-06-16 03:00 | 23 | 20 |  |  | 42902.125 | 41 | 40
2017-06-16 03:30 | 23 | 20 |  |  | 42902.1458 | 40 | 40
2017-06-16 04:00 | 22 | 20 |  |  | 42902.1667 | 40 | 40
2017-06-16 04:30 | 25 | 22 |  |  | 42902.1875 | 42 | 42
2017-06-16 05:00 | 26 | 24 |  |  | 42902.2083 | 45 | 45
2017-06-16 05:30 | 31 | 29 |  |  | 42902.2292 | 51 | 51
2017-06-16 06:00 | 34 | 33 |  |  | 42902.25 | 58 | 58
2017-06-16 06:30 | 41 | 37 |  |  | 42902.2708 | 68 | 66
2017-06-16 07:00 | 42 | 39 |  |  | 42902.2917 | 75 | 73
2017-06-16 07:30 | 44 | 41 |  |  | 42902.3125 | 81 | 79
2017-06-16 08:00 | 43 | 39 |  |  | 42902.3333 | 80 | 77
2017-06-16 08:30 | 42 | 39 |  |  | 42902.3542 | 80 | 78
2017-06-16 09:00 | 43 | 40 |  |  | 42902.375 | 81 | 78
2017-06-16 09:30 | 43 | 40 |  |  | 42902.3958 | 79 | 77
2017-06-16 10:00 | 42 | 39 |  |  | 42902.4167 | 79 | 76
2017-06-16 10:30 | 44 | 41 |  |  | 42902.4375 | 79 | 77
2017-06-16 11:00 | 43 | 40 |  |  | 42902.4583 | 82 | 80
2017-06-16 11:30 | 43 | 41 |  |  | 42902.4792 | 81 | 78
2017-06-16 12:00 | 43 | 40 |  |  | 42902.5 | 80 | 78
2017-06-16 12:30 | 43 | 41 |  |  | 42902.5208 | 81 | 78
2017-06-16 13:00 | 43 | 40 |  |  | 42902.5417 | 77 | 75
2017-06-16 13:30 | 40 | 38 |  |  | 42902.5625 | 74 | 73
2017-06-16 14:00 | 40 | 38 |  |  | 42902.5833 | 73 | 72
2017-06-16 14:30 | 40 | 37 |  |  | 42902.6042 | 74 | 73
2017-06-16 15:00 | 42 | 40 |  |  | 42902.625 | 77 | 76
2017-06-16 15:30 | 43 | 39 |  |  | 42902.6458 | 77 | 75
2017-06-16 16:00 | 44 | 40 |  |  | 42902.6667 | 77 | 76
2017-06-16 16:30 | 45 | 40 |  |  | 42902.6875 | 77 | 75
2017-06-16 17:00 | 68 | 66 |  |  | 42902.7083 | 91 | 90
2017-06-16 17:30 | 73 | 71 |  |  | 42902.7292 | 97 | 96
2017-06-16 18:00 | 72 | 71 |  |  | 42902.75 | 95 | 94
2017-06-16 18:30 | 70 | 69 |  |  | 42902.7708 | 92 | 90
2017-06-16 19:00 | 71 | 69 |  |  | 42902.7917 | 92 | 90
2017-06-16 19:30 | 69 | 66 |  |  | 42902.8125 | 90 | 88
2017-06-16 20:00 | 66 | 63 |  |  | 42902.8333 | 86 | 84
2017-06-16 20:30 | 62 | 62 |  |  | 42902.8542 | 81 | 81
2017-06-16 21:00 | 61 | 61 |  |  | 42902.875 | 80 | 80
2017-06-16 21:30 | 58 | 57 |  |  | 42902.8958 | 75 | 75
2017-06-16 22:00 | 56 | 56 |  |  | 42902.9167 | 75 | 75
2017-06-16 22:30 | 56 | 55 |  |  | 42902.9375 | 74 | 74
2017-06-16 23:00 | 55 | 54 |  |  | 42902.9583 | 72 | 72
2017-06-16 23:30 | 52 | 51 |  |  | 42902.9792 | 69 | 69
2017-06-17 | 50 | 49 |  |  | 42903 | 66 | 66
2017-06-17 00:30 | 48 | 46 |  |  | 42903.0208 | 61 | 61
2017-06-17 01:00 | 45 | 43 |  |  | 42903.0417 | 57 | 57
2017-06-17 01:30 | 42 | 40 |  |  | 42903.0625 | 53 | 53
2017-06-17 02:00 | 40 | 38 |  |  | 42903.0833 | 50 | 50
2017-06-17 02:30 | 38 | 36 |  |  | 42903.1042 | 49 | 49
2017-06-17 03:00 | 38 | 36 |  |  | 42903.125 | 47 | 47
2017-06-17 03:30 | 35 | 32 |  |  | 42903.1458 | 45 | 45
2017-06-17 04:00 | 33 | 31 |  |  | 42903.1667 | 44 | 44
2017-06-17 04:30 | 34 | 32 |  |  | 42903.1875 | 44 | 44
2017-06-17 05:00 | 35 | 33 |  |  | 42903.2083 | 45 | 45
2017-06-17 05:30 | 35 | 33 |  |  | 42903.2292 | 46 | 46
2017-06-17 06:00 | 38 | 36 |  |  | 42903.25 | 50 | 50
2017-06-17 06:30 | 40 | 39 |  |  | 42903.2708 | 53 | 53
2017-06-17 07:00 | 41 | 40 |  |  | 42903.2917 | 56 | 56
2017-06-17 07:30 | 43 | 42 |  |  | 42903.3125 | 59 | 59
2017-06-17 08:00 | 46 | 45 |  |  | 42903.3333 | 62 | 62
2017-06-17 08:30 | 50 | 49 |  |  | 42903.3542 | 68 | 68
2017-06-17 09:00 | 51 | 50 |  |  | 42903.375 | 69 | 69
2017-06-17 09:30 | 50 | 50 |  |  | 42903.3958 | 69 | 69
2017-06-17 10:00 | 48 | 48 |  |  | 42903.4167 | 66 | 66
2017-06-17 10:30 | 47 | 46 |  |  | 42903.4375 | 66 | 65
2017-06-17 11:00 | 47 | 47 |  |  | 42903.4583 | 66 | 65
2017-06-17 11:30 | 45 | 44 |  |  | 42903.4792 | 64 | 63
2017-06-17 12:00 | 44 | 44 |  |  | 42903.5 | 64 | 64
2017-06-17 12:30 | 44 | 43 |  |  | 42903.5208 | 61 | 61
2017-06-17 13:00 | 47 | 47 |  |  | 42903.5417 | 65 | 64
2017-06-17 13:30 | 49 | 49 |  |  | 42903.5625 | 67 | 66
2017-06-17 14:00 | 50 | 50 |  |  | 42903.5833 | 66 | 66
2017-06-17 14:30 | 49 | 48 |  |  | 42903.6042 | 65 | 64
2017-06-17 15:00 | 50 | 50 |  |  | 42903.625 | 67 | 66
2017-06-17 15:30 | 49 | 49 |  |  | 42903.6458 | 67 | 67
2017-06-17 16:00 | 49 | 49 |  |  | 42903.6667 | 68 | 68
2017-06-17 16:30 | 52 | 52 |  |  | 42903.6875 | 70 | 70
2017-06-17 17:00 | 55 | 55 |  |  | 42903.7083 | 75 | 75
2017-06-17 17:30 | 61 | 60 |  |  | 42903.7292 | 79 | 79
2017-06-17 18:00 | 61 | 60 |  |  | 42903.75 | 80 | 80
2017-06-17 18:30 | 61 | 60 |  |  | 42903.7708 | 80 | 80
2017-06-17 19:00 | 62 | 62 |  |  | 42903.7917 | 80 | 80
2017-06-17 19:30 | 60 | 60 |  |  | 42903.8125 | 78 | 78
2017-06-17 20:00 | 59 | 58 |  |  | 42903.8333 | 77 | 77
2017-06-17 20:30 | 59 | 58 |  |  | 42903.8542 | 77 | 77
2017-06-17 21:00 | 56 | 56 |  |  | 42903.875 | 73 | 73
2017-06-17 21:30 | 55 | 54 |  |  | 42903.8958 | 72 | 72
2017-06-17 22:00 | 53 | 53 |  |  | 42903.9167 | 72 | 72
2017-06-17 22:30 | 54 | 53 |  |  | 42903.9375 | 70 | 70
2017-06-17 23:00 | 52 | 51 |  |  | 42903.9583 | 68 | 68
2017-06-17 23:30 | 51 | 50 |  |  | 42903.9792 | 65 | 65
2017-06-18 | 50 | 49 |  |  | 42904 | 64 | 64
2017-06-18 00:30 | 47 | 45 |  |  | 42904.0208 | 60 | 60
2017-06-18 01:00 | 42 | 40 |  |  | 42904.0417 | 54 | 54
2017-06-18 01:30 | 40 | 38 |  |  | 42904.0625 | 51 | 51
2017-06-18 02:00 | 36 | 33 |  |  | 42904.0833 | 47 | 47
2017-06-18 02:30 | 35 | 33 |  |  | 42904.1042 | 45 | 45
2017-06-18 03:00 | 34 | 31 |  |  | 42904.125 | 44 | 44
2017-06-18 03:30 | 33 | 30 |  |  | 42904.1458 | 43 | 43
2017-06-18 04:00 | 33 | 30 |  |  | 42904.1667 | 42 | 42
2017-06-18 04:30 | 31 | 28 |  |  | 42904.1875 | 41 | 40
2017-06-18 05:00 | 32 | 29 |  |  | 42904.2083 | 42 | 41
2017-06-18 05:30 | 34 | 31 |  |  | 42904.2292 | 44 | 44
2017-06-18 06:00 | 35 | 33 |  |  | 42904.25 | 47 | 47
2017-06-18 06:30 | 37 | 35 |  |  | 42904.2708 | 50 | 50
2017-06-18 07:00 | 39 | 37 |  |  | 42904.2917 | 54 | 53
2017-06-18 07:30 | 38 | 36 |  |  | 42904.3125 | 54 | 54
2017-06-18 08:00 | 40 | 38 |  |  | 42904.3333 | 56 | 56
2017-06-18 08:30 | 41 | 40 |  |  | 42904.3542 | 58 | 58
2017-06-18 09:00 | 42 | 41 |  |  | 42904.375 | 59 | 59
2017-06-18 09:30 | 43 | 42 |  |  | 42904.3958 | 59 | 59
2017-06-18 10:00 | 43 | 42 |  |  | 42904.4167 | 58 | 58
2017-06-18 10:30 | 44 | 43 |  |  | 42904.4375 | 57 | 57
2017-06-18 11:00 | 43 | 42 |  |  | 42904.4583 | 56 | 56
2017-06-18 11:30 | 40 | 39 |  |  | 42904.4792 | 53 | 53
2017-06-18 12:00 | 38 | 37 |  |  | 42904.5 | 54 | 54
2017-06-18 12:30 | 38 | 37 |  |  | 42904.5208 | 54 | 54
2017-06-18 13:00 | 38 | 37 |  |  | 42904.5417 | 53 | 53
2017-06-18 13:30 | 40 | 39 |  |  | 42904.5625 | 55 | 55
2017-06-18 14:00 | 42 | 41 |  |  | 42904.5833 | 56 | 56
2017-06-18 14:30 | 41 | 40 |  |  | 42904.6042 | 55 | 55
2017-06-18 15:00 | 43 | 42 |  |  | 42904.625 | 58 | 58
2017-06-18 15:30 | 46 | 45 |  |  | 42904.6458 | 62 | 62
2017-06-18 16:00 | 49 | 49 |  |  | 42904.6667 | 66 | 66
2017-06-18 16:30 | 53 | 53 |  |  | 42904.6875 | 70 | 70
2017-06-18 17:00 | 56 | 55 |  |  | 42904.7083 | 74 | 74
2017-06-18 17:30 | 59 | 59 |  |  | 42904.7292 | 78 | 78
2017-06-18 18:00 | 61 | 61 |  |  | 42904.75 | 78 | 78
2017-06-18 18:30 | 60 | 59 |  |  | 42904.7708 | 76 | 76
2017-06-18 19:00 | 61 | 60 |  |  | 42904.7917 | 79 | 79
2017-06-18 19:30 | 62 | 60 |  |  | 42904.8125 | 79 | 79
2017-06-18 20:00 | 60 | 58 |  |  | 42904.8333 | 78 | 78
2017-06-18 20:30 | 61 | 60 |  |  | 42904.8542 | 79 | 79
2017-06-18 21:00 | 57 | 56 |  |  | 42904.875 | 74 | 74
2017-06-18 21:30 | 55 | 55 |  |  | 42904.8958 | 72 | 72
2017-06-18 22:00 | 55 | 54 |  |  | 42904.9167 | 73 | 73
2017-06-18 22:30 | 54 | 53 |  |  | 42904.9375 | 72 | 72
2017-06-18 23:00 | 52 | 51 |  |  | 42904.9583 | 68 | 68
2017-06-18 23:30 | 48 | 47 |  |  | 42904.9792 | 65 | 65
2017-06-19 | 48 | 47 |  |  | 42905 | 61 | 61
2017-06-19 00:30 | 43 | 42 |  |  | 42905.0208 | 55 | 54
2017-06-19 01:00 | 39 | 37 |  |  | 42905.0417 | 50 | 50
2017-06-19 01:30 | 36 | 34 |  |  | 42905.0625 | 47 | 47
2017-06-19 02:00 | 35 | 32 |  |  | 42905.0833 | 45 | 45
2017-06-19 02:30 | 33 | 30 |  |  | 42905.1042 | 43 | 43
2017-06-19 03:00 | 33 | 30 |  |  | 42905.125 | 43 | 43
2017-06-19 03:30 | 33 | 31 |  |  | 42905.1458 | 43 | 42
2017-06-19 04:00 | 32 | 30 |  |  | 42905.1667 | 41 | 41
2017-06-19 04:30 | 34 | 32 |  |  | 42905.1875 | 43 | 43
2017-06-19 05:00 | 35 | 33 |  |  | 42905.2083 | 45 | 45
2017-06-19 05:30 | 39 | 38 |  |  | 42905.2292 | 51 | 51
2017-06-19 06:00 | 46 | 46 |  |  | 42905.25 | 60 | 60
2017-06-19 06:30 | 56 | 56 |  |  | 42905.2708 | 72 | 72
2017-06-19 07:00 | 61 | 61 |  |  | 42905.2917 | 82 | 82
2017-06-19 07:30 | 66 | 66 |  |  | 42905.3125 | 90 | 89
2017-06-19 08:00 | 66 | 66 |  |  | 42905.3333 | 91 | 91
2017-06-19 08:30 | 69 | 69 |  |  | 42905.3542 | 97 | 96
2017-06-19 09:00 | 67 | 67 |  |  | 42905.375 | 97 | 97
2017-06-19 09:30 | 65 | 65 |  |  | 42905.3958 | 93 | 93
2017-06-19 10:00 | 65 | 65 |  |  | 42905.4167 | 93 | 92
2017-06-19 10:30 | 66 | 66 |  |  | 42905.4375 | 92 | 91
2017-06-19 11:00 | 65 | 65 |  |  | 42905.4583 | 91 | 90
2017-06-19 11:30 | 64 | 64 |  |  | 42905.4792 | 90 | 89
2017-06-19 12:00 | 66 | 66 |  |  | 42905.5 | 93 | 92
2017-06-19 12:30 | 76 | 76 |  |  | 42905.5208 | 102 | 101
2017-06-19 13:00 | 77 | 77 |  |  | 42905.5417 | 102 | 102
2017-06-19 13:30 | 72 | 72 |  |  | 42905.5625 | 98 | 98
2017-06-19 14:00 | 70 | 70 |  |  | 42905.5833 | 94 | 94
2017-06-19 14:30 | 69 | 69 |  |  | 42905.6042 | 93 | 93
2017-06-19 15:00 | 71 | 71 |  |  | 42905.625 | 95 | 95
2017-06-19 15:30 | 73 | 73 |  |  | 42905.6458 | 97 | 97
2017-06-19 16:00 | 73 | 73 |  |  | 42905.6667 | 98 | 98
2017-06-19 16:30 | 75 | 75 |  |  | 42905.6875 | 101 | 101
2017-06-19 17:00 | 79 | 79 |  |  | 42905.7083 | 105 | 105
2017-06-19 17:30 | 85 | 83 |  |  | 42905.7292 | 111 | 109
2017-06-19 18:00 | 88 | 83 |  |  | 42905.75 | 116 | 106
2017-06-19 18:30 | 78 | 74 |  |  | 42905.7708 | 101 | 94
2017-06-19 19:00 | 76 | 74 |  |  | 42905.7917 | 98 | 95
2017-06-19 19:30 | 74 | 72 |  |  | 42905.8125 | 94 | 91
2017-06-19 20:00 | 72 | 70 |  |  | 42905.8333 | 92 | 89
2017-06-19 20:30 | 71 | 70 |  |  | 42905.8542 | 91 | 89
2017-06-19 21:00 | 67 | 67 |  |  | 42905.875 | 84 | 84
2017-06-19 21:30 | 63 | 63 |  |  | 42905.8958 | 79 | 79
2017-06-19 22:00 | 63 | 63 |  |  | 42905.9167 | 79 | 79
2017-06-19 22:30 | 60 | 60 |  |  | 42905.9375 | 76 | 76
2017-06-19 23:00 | 58 | 58 |  |  | 42905.9583 | 73 | 73
2017-06-19 23:30 | 55 | 55 |  |  | 42905.9792 | 70 | 70
2017-06-20 | 51 | 51 |  |  | 42906 | 65 | 65
2017-06-20 00:30 | 46 | 45 |  |  | 42906.0208 | 60 | 60
2017-06-20 01:00 | 42 | 41 |  |  | 42906.0417 | 55 | 55
2017-06-20 01:30 | 39 | 38 |  |  | 42906.0625 | 51 | 50
2017-06-20 02:00 | 36 | 35 |  |  | 42906.0833 | 47 | 47
2017-06-20 02:30 | 36 | 35 |  |  | 42906.1042 | 47 | 47
2017-06-20 03:00 | 34 | 34 |  |  | 42906.125 | 46 | 46
2017-06-20 03:30 | 35 | 35 |  |  | 42906.1458 | 46 | 46
2017-06-20 04:00 | 34 | 33 |  |  | 42906.1667 | 45 | 45
2017-06-20 04:30 | 35 | 34 |  |  | 42906.1875 | 47 | 47
2017-06-20 05:00 | 38 | 38 |  |  | 42906.2083 | 50 | 50
2017-06-20 05:30 | 43 | 43 |  |  | 42906.2292 | 56 | 56
2017-06-20 06:00 | 50 | 50 |  |  | 42906.25 | 64 | 64
2017-06-20 06:30 | 60 | 59 |  |  | 42906.2708 | 78 | 78
2017-06-20 07:00 | 66 | 66 |  |  | 42906.2917 | 87 | 87
2017-06-20 07:30 | 68 | 68 |  |  | 42906.3125 | 91 | 91
2017-06-20 08:00 | 68 | 68 |  |  | 42906.3333 | 93 | 93
2017-06-20 08:30 | 73 | 73 |  |  | 42906.3542 | 104 | 104
2017-06-20 09:00 | 71 | 71 |  |  | 42906.375 | 102 | 102
2017-06-20 09:30 | 73 | 73 |  |  | 42906.3958 | 102 | 101
2017-06-20 10:00 | 71 | 71 |  |  | 42906.4167 | 101 | 100
2017-06-20 10:30 | 69 | 68 |  |  | 42906.4375 | 97 | 97
2017-06-20 11:00 | 68 | 68 |  |  | 42906.4583 | 98 | 98
2017-06-20 11:30 | 71 | 71 |  |  | 42906.4792 | 96 | 96
2017-06-20 12:00 | 72 | 72 |  |  | 42906.5 | 97 | 97
2017-06-20 12:30 | 72 | 71 |  |  | 42906.5208 | 100 | 100
2017-06-20 13:00 | 71 | 71 |  |  | 42906.5417 | 98 | 97
2017-06-20 13:30 | 70 | 70 |  |  | 42906.5625 | 96 | 95
2017-06-20 14:00 | 73 | 73 |  |  | 42906.5833 | 97 | 97
2017-06-20 14:30 | 73 | 73 |  |  | 42906.6042 | 96 | 95
2017-06-20 15:00 | 73 | 72 |  |  | 42906.625 | 95 | 95
2017-06-20 15:30 | 72 | 72 |  |  | 42906.6458 | 98 | 97
2017-06-20 16:00 | 73 | 72 |  |  | 42906.6667 | 99 | 98
2017-06-20 16:30 | 76 | 75 |  |  | 42906.6875 | 102 | 102
2017-06-20 17:00 | 73 | 72 |  |  | 42906.7083 | 96 | 95
2017-06-20 17:30 | 73 | 72 |  |  | 42906.7292 | 94 | 92
2017-06-20 18:00 | 73 | 72 |  |  | 42906.75 | 93 | 91
2017-06-20 18:30 | 70 | 69 |  |  | 42906.7708 | 90 | 88
2017-06-20 19:00 | 70 | 69 |  |  | 42906.7917 | 89 | 87
2017-06-20 19:30 | 68 | 67 |  |  | 42906.8125 | 87 | 85
2017-06-20 20:00 | 67 | 66 |  |  | 42906.8333 | 85 | 84
2017-06-20 20:30 | 67 | 66 |  |  | 42906.8542 | 85 | 85
2017-06-20 21:00 | 65 | 65 |  |  | 42906.875 | 81 | 81
2017-06-20 21:30 | 63 | 62 |  |  | 42906.8958 | 78 | 78
2017-06-20 22:00 | 61 | 60 |  |  | 42906.9167 | 76 | 75
2017-06-20 22:30 | 58 | 58 |  |  | 42906.9375 | 74 | 73
2017-06-20 23:00 | 58 | 57 |  |  | 42906.9583 | 72 | 71
2017-06-20 23:30 | 56 | 55 |  |  | 42906.9792 | 70 | 69
2017-06-21 | 52 | 51 |  |  | 42907 | 66 | 65
2017-06-21 00:30 | 48 | 46 |  |  | 42907.0208 | 60 | 59
2017-06-21 01:00 | 42 | 40 |  |  | 42907.0417 | 54 | 53
2017-06-21 01:30 | 39 | 36 |  |  | 42907.0625 | 50 | 49
2017-06-21 02:00 | 37 | 34 |  |  | 42907.0833 | 49 | 47
2017-06-21 02:30 | 36 | 33 |  |  | 42907.1042 | 47 | 45
2017-06-21 03:00 | 36 | 32 |  |  | 42907.125 | 47 | 45
2017-06-21 03:30 | 35 | 32 |  |  | 42907.1458 | 47 | 45
2017-06-21 04:00 | 36 | 32 |  |  | 42907.1667 | 47 | 45
2017-06-21 04:30 | 37 | 34 |  |  | 42907.1875 | 47 | 45
2017-06-21 05:00 | 38 | 36 |  |  | 42907.2083 | 50 | 48
2017-06-21 05:30 | 46 | 44 |  |  | 42907.2292 | 58 | 56
2017-06-21 06:00 | 52 | 51 |  |  | 42907.25 | 66 | 66
2017-06-21 06:30 | 58 | 58 |  |  | 42907.2708 | 77 | 76
2017-06-21 07:00 | 62 | 61 |  |  | 42907.2917 | 84 | 84
2017-06-21 07:30 | 69 | 69 |  |  | 42907.3125 | 95 | 95
2017-06-21 08:00 | 69 | 69 |  |  | 42907.3333 | 95 | 95
2017-06-21 08:30 | 67 | 67 |  |  | 42907.3542 | 93 | 93
2017-06-21 09:00 | 64 | 64 |  |  | 42907.375 | 91 | 91
2017-06-21 09:30 | 67 | 67 |  |  | 42907.3958 | 96 | 96
2017-06-21 10:00 | 65 | 65 |  |  | 42907.4167 | 91 | 91
2017-06-21 10:30 | 62 | 62 |  |  | 42907.4375 | 88 | 88
2017-06-21 11:00 | 59 | 59 |  |  | 42907.4583 | 84 | 84
2017-06-21 11:30 | 60 | 60 |  |  | 42907.4792 | 84 | 84
2017-06-21 12:00 | 61 | 61 |  |  | 42907.5 | 86 | 86
2017-06-21 12:30 | 63 | 63 |  |  | 42907.5208 | 89 | 89
2017-06-21 13:00 | 65 | 65 |  |  | 42907.5417 | 90 | 90
2017-06-21 13:30 | 67 | 67 |  |  | 42907.5625 | 92 | 92
2017-06-21 14:00 | 68 | 68 |  |  | 42907.5833 | 92 | 92
2017-06-21 14:30 | 68 | 68 |  |  | 42907.6042 | 92 | 92
2017-06-21 15:00 | 69 | 69 |  |  | 42907.625 | 94 | 94
2017-06-21 15:30 | 69 | 69 |  |  | 42907.6458 | 94 | 94
2017-06-21 16:00 | 73 | 73 |  |  | 42907.6667 | 98 | 98
2017-06-21 16:30 | 74 | 74 |  |  | 42907.6875 | 100 | 100
2017-06-21 17:00 | 79 | 78 |  |  | 42907.7083 | 104 | 104
2017-06-21 17:30 | 82 | 81 |  |  | 42907.7292 | 108 | 107
2017-06-21 18:00 | 79 | 76 |  |  | 42907.75 | 104 | 98
2017-06-21 18:30 | 79 | 75 |  |  | 42907.7708 | 103 | 96
2017-06-21 19:00 | 78 | 73 |  |  | 42907.7917 | 102 | 93
2017-06-21 19:30 | 76 | 70 |  |  | 42907.8125 | 98 | 91
2017-06-21 20:00 | 73 | 68 |  |  | 42907.8333 | 94 | 89
2017-06-21 20:30 | 72 | 68 |  |  | 42907.8542 | 92 | 87
2017-06-21 21:00 | 67 | 66 |  |  | 42907.875 | 83 | 83
2017-06-21 21:30 | 63 | 62 |  |  | 42907.8958 | 79 | 79
2017-06-21 22:00 | 63 | 62 |  |  | 42907.9167 | 79 | 79
2017-06-21 22:30 | 60 | 59 |  |  | 42907.9375 | 77 | 77
2017-06-21 23:00 | 59 | 58 |  |  | 42907.9583 | 74 | 74
2017-06-21 23:30 | 57 | 55 |  |  | 42907.9792 | 70 | 70
2017-06-22 | 51 | 49 |  |  | 42908 | 64 | 64
2017-06-22 00:30 | 44 | 41 |  |  | 42908.0208 | 56 | 56
2017-06-22 01:00 | 40 | 37 |  |  | 42908.0417 | 49 | 49
2017-06-22 01:30 | 37 | 33 |  |  | 42908.0625 | 47 | 46
2017-06-22 02:00 | 38 | 34 |  |  | 42908.0833 | 47 | 46
2017-06-22 02:30 | 37 | 33 |  |  | 42908.1042 | 45 | 44
2017-06-22 03:00 | 35 | 30 |  |  | 42908.125 | 44 | 43
2017-06-22 03:30 | 35 | 30 |  |  | 42908.1458 | 44 | 43
2017-06-22 04:00 | 35 | 30 |  |  | 42908.1667 | 43 | 43
2017-06-22 04:30 | 37 | 33 |  |  | 42908.1875 | 46 | 46
2017-06-22 05:00 | 39 | 36 |  |  | 42908.2083 | 50 | 50
2017-06-22 05:30 | 47 | 45 |  |  | 42908.2292 | 59 | 58
2017-06-22 06:00 | 53 | 52 |  |  | 42908.25 | 67 | 67
2017-06-22 06:30 | 59 | 59 |  |  | 42908.2708 | 77 | 77
2017-06-22 07:00 | 65 | 64 |  |  | 42908.2917 | 85 | 85
2017-06-22 07:30 | 73 | 72 |  |  | 42908.3125 | 94 | 94
2017-06-22 08:00 | 76 | 76 |  |  | 42908.3333 | 96 | 95
2017-06-22 08:30 | 75 | 75 |  |  | 42908.3542 | 96 | 96
2017-06-22 09:00 | 74 | 74 |  |  | 42908.375 | 96 | 96
2017-06-22 09:30 | 71 | 71 |  |  | 42908.3958 | 95 | 94
2017-06-22 10:00 | 68 | 68 |  |  | 42908.4167 | 90 | 90
2017-06-22 10:30 | 67 | 67 |  |  | 42908.4375 | 87 | 87
2017-06-22 11:00 | 65 | 65 |  |  | 42908.4583 | 85 | 84
2017-06-22 11:30 | 64 | 64 |  |  | 42908.4792 | 83 | 83
2017-06-22 12:00 | 65 | 65 |  |  | 42908.5 | 85 | 85
2017-06-22 12:30 | 67 | 67 |  |  | 42908.5208 | 89 | 88
2017-06-22 13:00 | 65 | 65 |  |  | 42908.5417 | 91 | 90
2017-06-22 13:30 | 65 | 65 |  |  | 42908.5625 | 91 | 91
2017-06-22 14:00 | 68 | 68 |  |  | 42908.5833 | 92 | 92
2017-06-22 14:30 | 68 | 68 |  |  | 42908.6042 | 93 | 93
2017-06-22 15:00 | 68 | 68 |  |  | 42908.625 | 94 | 94
2017-06-22 15:30 | 69 | 68 |  |  | 42908.6458 | 94 | 94
2017-06-22 16:00 | 67 | 66 |  |  | 42908.6667 | 88 | 88
2017-06-22 16:30 | 69 | 69 |  |  | 42908.6875 | 91 | 91
2017-06-22 17:00 | 72 | 71 |  |  | 42908.7083 | 94 | 94
2017-06-22 17:30 | 74 | 73 |  |  | 42908.7292 | 95 | 94
2017-06-22 18:00 | 73 | 72 |  |  | 42908.75 | 94 | 93
2017-06-22 18:30 | 73 | 71 |  |  | 42908.7708 | 92 | 90
2017-06-22 19:00 | 74 | 71 |  |  | 42908.7917 | 94 | 91
2017-06-22 19:30 | 74 | 71 |  |  | 42908.8125 | 93 | 90
2017-06-22 20:00 | 74 | 71 |  |  | 42908.8333 | 92 | 90
2017-06-22 20:30 | 74 | 71 |  |  | 42908.8542 | 91 | 89
2017-06-22 21:00 | 70 | 66 |  |  | 42908.875 | 87 | 83
2017-06-22 21:30 | 64 | 62 |  |  | 42908.8958 | 82 | 80
2017-06-22 22:00 | 64 | 62 |  |  | 42908.9167 | 83 | 81
2017-06-22 22:30 | 62 | 60 |  |  | 42908.9375 | 82 | 81
2017-06-22 23:00 | 61 | 59 |  |  | 42908.9583 | 77 | 77
2017-06-22 23:30 | 58 | 56 |  |  | 42908.9792 | 72 | 72
2017-06-23 | 54 | 51 |  |  | 42909 | 68 | 68
2017-06-23 00:30 | 49 | 45 |  |  | 42909.0208 | 61 | 60
2017-06-23 01:00 | 45 | 41 |  |  | 42909.0417 | 56 | 55
2017-06-23 01:30 | 43 | 39 |  |  | 42909.0625 | 52 | 52
2017-06-23 02:00 | 43 | 38 |  |  | 42909.0833 | 52 | 51
2017-06-23 02:30 | 42 | 38 |  |  | 42909.1042 | 51 | 50
2017-06-23 03:00 | 41 | 37 |  |  | 42909.125 | 50 | 50
2017-06-23 03:30 | 40 | 36 |  |  | 42909.1458 | 49 | 48
2017-06-23 04:00 | 40 | 36 |  |  | 42909.1667 | 48 | 48
2017-06-23 04:30 | 40 | 36 |  |  | 42909.1875 | 49 | 49
2017-06-23 05:00 | 42 | 38 |  |  | 42909.2083 | 52 | 52
2017-06-23 05:30 | 48 | 45 |  |  | 42909.2292 | 60 | 60
2017-06-23 06:00 | 52 | 51 |  |  | 42909.25 | 67 | 67
2017-06-23 06:30 | 61 | 61 |  |  | 42909.2708 | 80 | 80
2017-06-23 07:00 | 67 | 67 |  |  | 42909.2917 | 90 | 90
2017-06-23 07:30 | 70 | 70 |  |  | 42909.3125 | 96 | 96
2017-06-23 08:00 | 69 | 69 |  |  | 42909.3333 | 96 | 96
2017-06-23 08:30 | 68 | 68 |  |  | 42909.3542 | 95 | 95
2017-06-23 09:00 | 64 | 64 |  |  | 42909.375 | 90 | 90
2017-06-23 09:30 | 61 | 61 |  |  | 42909.3958 | 86 | 85
2017-06-23 10:00 | 60 | 59 |  |  | 42909.4167 | 83 | 83
2017-06-23 10:30 | 60 | 59 |  |  | 42909.4375 | 82 | 82
2017-06-23 11:00 | 58 | 57 |  |  | 42909.4583 | 81 | 81
2017-06-23 11:30 | 56 | 55 |  |  | 42909.4792 | 78 | 78
2017-06-23 12:00 | 55 | 55 |  |  | 42909.5 | 79 | 79
2017-06-23 12:30 | 57 | 56 |  |  | 42909.5208 | 79 | 79
2017-06-23 13:00 | 57 | 57 |  |  | 42909.5417 | 79 | 79
2017-06-23 13:30 | 58 | 58 |  |  | 42909.5625 | 81 | 81
2017-06-23 14:00 | 58 | 58 |  |  | 42909.5833 | 81 | 81
2017-06-23 14:30 | 59 | 59 |  |  | 42909.6042 | 82 | 81
2017-06-23 15:00 | 58 | 58 |  |  | 42909.625 | 80 | 80
2017-06-23 15:30 | 59 | 58 |  |  | 42909.6458 | 82 | 82
2017-06-23 16:00 | 61 | 61 |  |  | 42909.6667 | 84 | 84
2017-06-23 16:30 | 65 | 65 |  |  | 42909.6875 | 88 | 88
2017-06-23 17:00 | 66 | 66 |  |  | 42909.7083 | 89 | 88
2017-06-23 17:30 | 69 | 68 |  |  | 42909.7292 | 91 | 90
2017-06-23 18:00 | 71 | 69 |  |  | 42909.75 | 91 | 90
2017-06-23 18:30 | 70 | 68 |  |  | 42909.7708 | 90 | 89
2017-06-23 19:00 | 69 | 68 |  |  | 42909.7917 | 89 | 89
2017-06-23 19:30 | 68 | 67 |  |  | 42909.8125 | 87 | 87
2017-06-23 20:00 | 67 | 66 |  |  | 42909.8333 | 85 | 85
2017-06-23 20:30 | 65 | 64 |  |  | 42909.8542 | 84 | 83
2017-06-23 21:00 | 64 | 63 |  |  | 42909.875 | 81 | 81
2017-06-23 21:30 | 61 | 60 |  |  | 42909.8958 | 78 | 78
2017-06-23 22:00 | 61 | 61 |  |  | 42909.9167 | 80 | 80
2017-06-23 22:30 | 60 | 59 |  |  | 42909.9375 | 78 | 78
2017-06-23 23:00 | 58 | 58 |  |  | 42909.9583 | 75 | 75
2017-06-23 23:30 | 56 | 55 |  |  | 42909.9792 | 72 | 72
2017-06-24 | 53 | 51 |  |  | 42910 | 67 | 67
2017-06-24 00:30 | 48 | 46 |  |  | 42910.0208 | 62 | 61
2017-06-24 01:00 | 45 | 43 |  |  | 42910.0417 | 58 | 57
2017-06-24 01:30 | 42 | 41 |  |  | 42910.0625 | 56 | 55
2017-06-24 02:00 | 42 | 39 |  |  | 42910.0833 | 53 | 53
2017-06-24 02:30 | 42 | 39 |  |  | 42910.1042 | 52 | 52
2017-06-24 03:00 | 41 | 38 |  |  | 42910.125 | 52 | 51
2017-06-24 03:30 | 40 | 37 |  |  | 42910.1458 | 51 | 50
2017-06-24 04:00 | 39 | 36 |  |  | 42910.1667 | 48 | 47
2017-06-24 04:30 | 39 | 36 |  |  | 42910.1875 | 49 | 48
2017-06-24 05:00 | 39 | 36 |  |  | 42910.2083 | 49 | 49
2017-06-24 05:30 | 41 | 39 |  |  | 42910.2292 | 51 | 51
2017-06-24 06:00 | 42 | 40 |  |  | 42910.25 | 54 | 54
2017-06-24 06:30 | 45 | 43 |  |  | 42910.2708 | 58 | 58
2017-06-24 07:00 | 47 | 45 |  |  | 42910.2917 | 62 | 62
2017-06-24 07:30 | 48 | 47 |  |  | 42910.3125 | 64 | 64
2017-06-24 08:00 | 49 | 48 |  |  | 42910.3333 | 66 | 66
2017-06-24 08:30 | 50 | 49 |  |  | 42910.3542 | 70 | 70
2017-06-24 09:00 | 50 | 50 |  |  | 42910.375 | 70 | 70
2017-06-24 09:30 | 49 | 48 |  |  | 42910.3958 | 67 | 67
2017-06-24 10:00 | 47 | 47 |  |  | 42910.4167 | 66 | 66
2017-06-24 10:30 | 47 | 46 |  |  | 42910.4375 | 64 | 64
2017-06-24 11:00 | 46 | 45 |  |  | 42910.4583 | 63 | 63
2017-06-24 11:30 | 45 | 44 |  |  | 42910.4792 | 62 | 62
2017-06-24 12:00 | 45 | 44 |  |  | 42910.5 | 61 | 61
2017-06-24 12:30 | 45 | 44 |  |  | 42910.5208 | 61 | 61
2017-06-24 13:00 | 45 | 44 |  |  | 42910.5417 | 60 | 60
2017-06-24 13:30 | 45 | 44 |  |  | 42910.5625 | 60 | 60
2017-06-24 14:00 | 45 | 44 |  |  | 42910.5833 | 60 | 60
2017-06-24 14:30 | 45 | 44 |  |  | 42910.6042 | 59 | 59
2017-06-24 15:00 | 46 | 45 |  |  | 42910.625 | 61 | 61
2017-06-24 15:30 | 48 | 46 |  |  | 42910.6458 | 64 | 64
2017-06-24 16:00 | 51 | 50 |  |  | 42910.6667 | 69 | 69
2017-06-24 16:30 | 55 | 53 |  |  | 42910.6875 | 70 | 70
2017-06-24 17:00 | 57 | 55 |  |  | 42910.7083 | 74 | 74
2017-06-24 17:30 | 59 | 58 |  |  | 42910.7292 | 76 | 76
2017-06-24 18:00 | 60 | 58 |  |  | 42910.75 | 77 | 77
2017-06-24 18:30 | 60 | 58 |  |  | 42910.7708 | 78 | 77
2017-06-24 19:00 | 60 | 58 |  |  | 42910.7917 | 79 | 78
2017-06-24 19:30 | 61 | 58 |  |  | 42910.8125 | 78 | 77
2017-06-24 20:00 | 62 | 60 |  |  | 42910.8333 | 79 | 78
2017-06-24 20:30 | 61 | 58 |  |  | 42910.8542 | 78 | 77
2017-06-24 21:00 | 58 | 56 |  |  | 42910.875 | 74 | 73
2017-06-24 21:30 | 55 | 53 |  |  | 42910.8958 | 71 | 71
2017-06-24 22:00 | 55 | 53 |  |  | 42910.9167 | 72 | 72
2017-06-24 22:30 | 54 | 53 |  |  | 42910.9375 | 71 | 71
2017-06-24 23:00 | 53 | 51 |  |  | 42910.9583 | 68 | 68
2017-06-24 23:30 | 52 | 50 |  |  | 42910.9792 | 67 | 66
2017-06-25 | 49 | 47 |  |  | 42911 | 64 | 63
2017-06-25 00:30 | 45 | 42 |  |  | 42911.0208 | 57 | 56
2017-06-25 01:00 | 42 | 39 |  |  | 42911.0417 | 53 | 52
2017-06-25 01:30 | 41 | 38 |  |  | 42911.0625 | 53 | 52
2017-06-25 02:00 | 41 | 37 |  |  | 42911.0833 | 53 | 52
2017-06-25 02:30 | 39 | 36 |  |  | 42911.1042 | 51 | 49
2017-06-25 03:00 | 39 | 35 |  |  | 42911.125 | 49 | 48
2017-06-25 03:30 | 39 | 35 |  |  | 42911.1458 | 49 | 48
2017-06-25 04:00 | 37 | 34 |  |  | 42911.1667 | 47 | 46
2017-06-25 04:30 | 37 | 34 |  |  | 42911.1875 | 47 | 46
2017-06-25 05:00 | 39 | 36 |  |  | 42911.2083 | 50 | 50
2017-06-25 05:30 | 39 | 36 |  |  | 42911.2292 | 51 | 50
2017-06-25 06:00 | 40 | 38 |  |  | 42911.25 | 52 | 51
2017-06-25 06:30 | 41 | 39 |  |  | 42911.2708 | 54 | 54
2017-06-25 07:00 | 42 | 40 |  |  | 42911.2917 | 56 | 56
2017-06-25 07:30 | 46 | 43 |  |  | 42911.3125 | 60 | 60
2017-06-25 08:00 | 47 | 44 |  |  | 42911.3333 | 62 | 60
2017-06-25 08:30 | 47 | 44 |  |  | 42911.3542 | 63 | 61
2017-06-25 09:00 | 48 | 45 |  |  | 42911.375 | 64 | 62
2017-06-25 09:30 | 48 | 45 |  |  | 42911.3958 | 65 | 64
2017-06-25 10:00 | 50 | 47 |  |  | 42911.4167 | 65 | 63
2017-06-25 10:30 | 49 | 46 |  |  | 42911.4375 | 61 | 59
2017-06-25 11:00 | 45 | 43 |  |  | 42911.4583 | 59 | 58
2017-06-25 11:30 | 43 | 40 |  |  | 42911.4792 | 56 | 55
2017-06-25 12:00 | 41 | 39 |  |  | 42911.5 | 56 | 55
2017-06-25 12:30 | 43 | 41 |  |  | 42911.5208 | 56 | 55
2017-06-25 13:00 | 44 | 41 |  |  | 42911.5417 | 56 | 56
2017-06-25 13:30 | 44 | 41 |  |  | 42911.5625 | 57 | 56
2017-06-25 14:00 | 43 | 41 |  |  | 42911.5833 | 57 | 56
2017-06-25 14:30 | 44 | 42 |  |  | 42911.6042 | 57 | 56
2017-06-25 15:00 | 45 | 42 |  |  | 42911.625 | 58 | 57
2017-06-25 15:30 | 47 | 45 |  |  | 42911.6458 | 61 | 60
2017-06-25 16:00 | 50 | 48 |  |  | 42911.6667 | 66 | 65
2017-06-25 16:30 | 54 | 52 |  |  | 42911.6875 | 70 | 69
2017-06-25 17:00 | 57 | 55 |  |  | 42911.7083 | 74 | 74
2017-06-25 17:30 | 62 | 60 |  |  | 42911.7292 | 79 | 78
2017-06-25 18:00 | 63 | 61 |  |  | 42911.75 | 81 | 80
2017-06-25 18:30 | 62 | 60 |  |  | 42911.7708 | 80 | 79
2017-06-25 19:00 | 62 | 60 |  |  | 42911.7917 | 82 | 82
2017-06-25 19:30 | 63 | 61 |  |  | 42911.8125 | 82 | 81
2017-06-25 20:00 | 63 | 61 |  |  | 42911.8333 | 82 | 81
2017-06-25 20:30 | 64 | 62 |  |  | 42911.8542 | 83 | 81
2017-06-25 21:00 | 63 | 60 |  |  | 42911.875 | 79 | 78
2017-06-25 21:30 | 59 | 57 |  |  | 42911.8958 | 76 | 74
2017-06-25 22:00 | 59 | 56 |  |  | 42911.9167 | 76 | 74
2017-06-25 22:30 | 59 | 56 |  |  | 42911.9375 | 75 | 73
2017-06-25 23:00 | 56 | 53 |  |  | 42911.9583 | 71 | 69
2017-06-25 23:30 | 53 | 50 |  |  | 42911.9792 | 68 | 66
2017-06-26 | 52 | 48 |  |  | 42912 | 65 | 63
2017-06-26 00:30 | 48 | 43 |  |  | 42912.0208 | 60 | 57
2017-06-26 01:00 | 44 | 39 |  |  | 42912.0417 | 54 | 51
2017-06-26 01:30 | 42 | 37 |  |  | 42912.0625 | 52 | 49
2017-06-26 02:00 | 42 | 37 |  |  | 42912.0833 | 51 | 49
2017-06-26 02:30 | 39 | 35 |  |  | 42912.1042 | 50 | 48
2017-06-26 03:00 | 40 | 36 |  |  | 42912.125 | 50 | 48
2017-06-26 03:30 | 39 | 35 |  |  | 42912.1458 | 49 | 47
2017-06-26 04:00 | 38 | 34 |  |  | 42912.1667 | 47 | 46
2017-06-26 04:30 | 39 | 36 |  |  | 42912.1875 | 49 | 48
2017-06-26 05:00 | 40 | 38 |  |  | 42912.2083 | 52 | 51
2017-06-26 05:30 | 47 | 45 |  |  | 42912.2292 | 59 | 59
2017-06-26 06:00 | 53 | 52 |  |  | 42912.25 | 66 | 66
2017-06-26 06:30 | 59 | 58 |  |  | 42912.2708 | 75 | 75
2017-06-26 07:00 | 61 | 61 |  |  | 42912.2917 | 83 | 83
2017-06-26 07:30 | 67 | 67 |  |  | 42912.3125 | 90 | 90
2017-06-26 08:00 | 67 | 67 |  |  | 42912.3333 | 92 | 92
2017-06-26 08:30 | 66 | 66 |  |  | 42912.3542 | 92 | 92
2017-06-26 09:00 | 67 | 67 |  |  | 42912.375 | 90 | 90
2017-06-26 09:30 | 64 | 64 |  |  | 42912.3958 | 87 | 87
2017-06-26 10:00 | 63 | 63 |  |  | 42912.4167 | 86 | 86
2017-06-26 10:30 | 62 | 62 |  |  | 42912.4375 | 82 | 82
2017-06-26 11:00 | 60 | 60 |  |  | 42912.4583 | 81 | 80
2017-06-26 11:30 | 56 | 55 |  |  | 42912.4792 | 75 | 74
2017-06-26 12:00 | 53 | 53 |  |  | 42912.5 | 71 | 71
2017-06-26 12:30 | 54 | 54 |  |  | 42912.5208 | 73 | 73
2017-06-26 13:00 | 61 | 61 |  |  | 42912.5417 | 80 | 80
2017-06-26 13:30 | 63 | 63 |  |  | 42912.5625 | 83 | 83
2017-06-26 14:00 | 64 | 64 |  |  | 42912.5833 | 83 | 83
2017-06-26 14:30 | 64 | 64 |  |  | 42912.6042 | 84 | 84
2017-06-26 15:00 | 65 | 65 |  |  | 42912.625 | 85 | 85
2017-06-26 15:30 | 67 | 66 |  |  | 42912.6458 | 86 | 86
2017-06-26 16:00 | 69 | 69 |  |  | 42912.6667 | 89 | 89
2017-06-26 16:30 | 71 | 71 |  |  | 42912.6875 | 91 | 90
2017-06-26 17:00 | 73 | 73 |  |  | 42912.7083 | 93 | 92
2017-06-26 17:30 | 76 | 75 |  |  | 42912.7292 | 94 | 93
2017-06-26 18:00 | 75 | 75 |  |  | 42912.75 | 94 | 93
2017-06-26 18:30 | 74 | 73 |  |  | 42912.7708 | 91 | 90
2017-06-26 19:00 | 75 | 74 |  |  | 42912.7917 | 93 | 92
2017-06-26 19:30 | 75 | 74 |  |  | 42912.8125 | 92 | 91
2017-06-26 20:00 | 74 | 73 |  |  | 42912.8333 | 91 | 90
2017-06-26 20:30 | 73 | 72 |  |  | 42912.8542 | 89 | 88
2017-06-26 21:00 | 69 | 69 |  |  | 42912.875 | 83 | 83
2017-06-26 21:30 | 64 | 64 |  |  | 42912.8958 | 79 | 78
2017-06-26 22:00 | 64 | 64 |  |  | 42912.9167 | 79 | 79
2017-06-26 22:30 | 60 | 60 |  |  | 42912.9375 | 75 | 75
2017-06-26 23:00 | 58 | 57 |  |  | 42912.9583 | 72 | 71
2017-06-26 23:30 | 54 | 53 |  |  | 42912.9792 | 67 | 67
2017-06-27 | 51 | 49 |  |  | 42913 | 63 | 63
2017-06-27 00:30 | 46 | 44 |  |  | 42913.0208 | 57 | 55
2017-06-27 01:00 | 41 | 39 |  |  | 42913.0417 | 52 | 50
2017-06-27 01:30 | 38 | 36 |  |  | 42913.0625 | 49 | 48
2017-06-27 02:00 | 37 | 35 |  |  | 42913.0833 | 47 | 46
2017-06-27 02:30 | 37 | 35 |  |  | 42913.1042 | 46 | 46
2017-06-27 03:00 | 38 | 36 |  |  | 42913.125 | 47 | 46
2017-06-27 03:30 | 37 | 34 |  |  | 42913.1458 | 46 | 45
2017-06-27 04:00 | 37 | 35 |  |  | 42913.1667 | 46 | 45
2017-06-27 04:30 | 39 | 37 |  |  | 42913.1875 | 47 | 46
2017-06-27 05:00 | 41 | 39 |  |  | 42913.2083 | 50 | 49
2017-06-27 05:30 | 44 | 43 |  |  | 42913.2292 | 55 | 54
2017-06-27 06:00 | 50 | 50 |  |  | 42913.25 | 62 | 62
2017-06-27 06:30 | 56 | 56 |  |  | 42913.2708 | 71 | 70
2017-06-27 07:00 | 59 | 59 |  |  | 42913.2917 | 77 | 76
2017-06-27 07:30 | 64 | 64 |  |  | 42913.3125 | 86 | 86
2017-06-27 08:00 | 65 | 65 |  |  | 42913.3333 | 87 | 87
2017-06-27 08:30 | 63 | 63 |  |  | 42913.3542 | 85 | 85
2017-06-27 09:00 | 65 | 65 |  |  | 42913.375 | 88 | 88
2017-06-27 09:30 | 63 | 63 |  |  | 42913.3958 | 86 | 86
2017-06-27 10:00 | 65 | 65 |  |  | 42913.4167 | 88 | 88
2017-06-27 10:30 | 61 | 61 |  |  | 42913.4375 | 82 | 81
2017-06-27 11:00 | 61 | 61 |  |  | 42913.4583 | 82 | 82
2017-06-27 11:30 | 61 | 60 |  |  | 42913.4792 | 83 | 83
2017-06-27 12:00 | 60 | 59 |  |  | 42913.5 | 82 | 82
2017-06-27 12:30 | 65 | 64 |  |  | 42913.5208 | 85 | 85
2017-06-27 13:00 | 57 | 56 |  |  | 42913.5417 | 83 | 83
2017-06-27 13:30 | 56 | 54 |  |  | 42913.5625 | 82 | 82
2017-06-27 14:00 | 57 | 55 |  |  | 42913.5833 | 81 | 81
2017-06-27 14:30 | 54 | 53 |  |  | 42913.6042 | 78 | 78
2017-06-27 15:00 | 52 | 51 |  |  | 42913.625 | 77 | 77
2017-06-27 15:30 | 53 | 51 |  |  | 42913.6458 | 76 | 75
2017-06-27 16:00 | 54 | 52 |  |  | 42913.6667 | 77 | 77
2017-06-27 16:30 | 64 | 63 |  |  | 42913.6875 | 86 | 85
2017-06-27 17:00 | 67 | 66 |  |  | 42913.7083 | 89 | 88
2017-06-27 17:30 | 72 | 71 |  |  | 42913.7292 | 94 | 92
2017-06-27 18:00 | 72 | 71 |  |  | 42913.75 | 92 | 90
2017-06-27 18:30 | 71 | 70 |  |  | 42913.7708 | 90 | 87
2017-06-27 19:00 | 72 | 71 |  |  | 42913.7917 | 91 | 88
2017-06-27 19:30 | 71 | 70 |  |  | 42913.8125 | 89 | 87
2017-06-27 20:00 | 70 | 70 |  |  | 42913.8333 | 88 | 88
2017-06-27 20:30 | 71 | 71 |  |  | 42913.8542 | 88 | 88
2017-06-27 21:00 | 68 | 67 |  |  | 42913.875 | 84 | 84
2017-06-27 21:30 | 63 | 62 |  |  | 42913.8958 | 79 | 79
2017-06-27 22:00 | 61 | 61 |  |  | 42913.9167 | 78 | 78
2017-06-27 22:30 | 59 | 59 |  |  | 42913.9375 | 75 | 75
2017-06-27 23:00 | 56 | 55 |  |  | 42913.9583 | 70 | 70
2017-06-27 23:30 | 53 | 52 |  |  | 42913.9792 | 69 | 69
2017-06-28 | 50 | 49 |  |  | 42914 | 65 | 65
2017-06-28 00:30 | 44 | 43 |  |  | 42914.0208 | 57 | 57
2017-06-28 01:00 | 40 | 39 |  |  | 42914.0417 | 52 | 52
2017-06-28 01:30 | 37 | 36 |  |  | 42914.0625 | 48 | 47
2017-06-28 02:00 | 36 | 34 |  |  | 42914.0833 | 45 | 45
2017-06-28 02:30 | 35 | 34 |  |  | 42914.1042 | 45 | 45
2017-06-28 03:00 | 35 | 34 |  |  | 42914.125 | 45 | 45
2017-06-28 03:30 | 35 | 33 |  |  | 42914.1458 | 44 | 44
2017-06-28 04:00 | 34 | 33 |  |  | 42914.1667 | 44 | 44
2017-06-28 04:30 | 35 | 34 |  |  | 42914.1875 | 45 | 45
2017-06-28 05:00 | 38 | 37 |  |  | 42914.2083 | 47 | 47
2017-06-28 05:30 | 42 | 41 |  |  | 42914.2292 | 53 | 53
2017-06-28 06:00 | 48 | 48 |  |  | 42914.25 | 61 | 61
2017-06-28 06:30 | 53 | 53 |  |  | 42914.2708 | 70 | 69
2017-06-28 07:00 | 55 | 55 |  |  | 42914.2917 | 76 | 76
2017-06-28 07:30 | 59 | 58 |  |  | 42914.3125 | 82 | 82
2017-06-28 08:00 | 58 | 57 |  |  | 42914.3333 | 82 | 82
2017-06-28 08:30 | 57 | 57 |  |  | 42914.3542 | 82 | 81
2017-06-28 09:00 | 58 | 58 |  |  | 42914.375 | 81 | 81
2017-06-28 09:30 | 57 | 57 |  |  | 42914.3958 | 80 | 80
2017-06-28 10:00 | 55 | 55 |  |  | 42914.4167 | 77 | 77
2017-06-28 10:30 | 55 | 55 |  |  | 42914.4375 | 77 | 77
2017-06-28 11:00 | 55 | 55 |  |  | 42914.4583 | 77 | 77
2017-06-28 11:30 | 57 | 56 |  |  | 42914.4792 | 80 | 79
2017-06-28 12:00 | 56 | 56 |  |  | 42914.5 | 79 | 78
2017-06-28 12:30 | 56 | 55 |  |  | 42914.5208 | 77 | 77
2017-06-28 13:00 | 56 | 56 |  |  | 42914.5417 | 76 | 76
2017-06-28 13:30 | 56 | 56 |  |  | 42914.5625 | 77 | 77
2017-06-28 14:00 | 57 | 56 |  |  | 42914.5833 | 78 | 78
2017-06-28 14:30 | 57 | 57 |  |  | 42914.6042 | 77 | 77
2017-06-28 15:00 | 59 | 59 |  |  | 42914.625 | 79 | 79
2017-06-28 15:30 | 61 | 61 |  |  | 42914.6458 | 81 | 81
2017-06-28 16:00 | 64 | 64 |  |  | 42914.6667 | 84 | 84
2017-06-28 16:30 | 66 | 65 |  |  | 42914.6875 | 86 | 86
2017-06-28 17:00 | 66 | 66 |  |  | 42914.7083 | 87 | 86
2017-06-28 17:30 | 67 | 67 |  |  | 42914.7292 | 87 | 87
2017-06-28 18:00 | 66 | 66 |  |  | 42914.75 | 85 | 85
2017-06-28 18:30 | 65 | 65 |  |  | 42914.7708 | 82 | 81
2017-06-28 19:00 | 69 | 68 |  |  | 42914.7917 | 85 | 84
2017-06-28 19:30 | 68 | 67 |  |  | 42914.8125 | 84 | 83
2017-06-28 20:00 | 67 | 66 |  |  | 42914.8333 | 84 | 83
2017-06-28 20:30 | 68 | 68 |  |  | 42914.8542 | 85 | 84
2017-06-28 21:00 | 65 | 65 |  |  | 42914.875 | 81 | 81
2017-06-28 21:30 | 61 | 61 |  |  | 42914.8958 | 77 | 77
2017-06-28 22:00 | 62 | 62 |  |  | 42914.9167 | 77 | 77
2017-06-28 22:30 | 60 | 59 |  |  | 42914.9375 | 76 | 76
2017-06-28 23:00 | 55 | 55 |  |  | 42914.9583 | 70 | 70
2017-06-28 23:30 | 52 | 51 |  |  | 42914.9792 | 67 | 67
2017-06-29 | 47 | 46 |  |  | 42915 | 61 | 61
2017-06-29 00:30 | 43 | 42 |  |  | 42915.0208 | 56 | 56
2017-06-29 01:00 | 41 | 39 |  |  | 42915.0417 | 52 | 52
2017-06-29 01:30 | 40 | 38 |  |  | 42915.0625 | 49 | 49
2017-06-29 02:00 | 39 | 37 |  |  | 42915.0833 | 49 | 48
2017-06-29 02:30 | 38 | 37 |  |  | 42915.1042 | 48 | 48
2017-06-29 03:00 | 39 | 37 |  |  | 42915.125 | 49 | 49
2017-06-29 03:30 | 39 | 37 |  |  | 42915.1458 | 50 | 49
2017-06-29 04:00 | 39 | 38 |  |  | 42915.1667 | 49 | 49
2017-06-29 04:30 | 39 | 37 |  |  | 42915.1875 | 49 | 49
2017-06-29 05:00 | 41 | 39 |  |  | 42915.2083 | 51 | 50
2017-06-29 05:30 | 44 | 43 |  |  | 42915.2292 | 56 | 55
2017-06-29 06:00 | 49 | 49 |  |  | 42915.25 | 62 | 62
2017-06-29 06:30 | 55 | 55 |  |  | 42915.2708 | 72 | 72
2017-06-29 07:00 | 61 | 60 |  |  | 42915.2917 | 81 | 81
2017-06-29 07:30 | 64 | 64 |  |  | 42915.3125 | 88 | 88
2017-06-29 08:00 | 63 | 63 |  |  | 42915.3333 | 89 | 89
2017-06-29 08:30 | 62 | 62 |  |  | 42915.3542 | 88 | 88
2017-06-29 09:00 | 61 | 61 |  |  | 42915.375 | 86 | 86
2017-06-29 09:30 | 60 | 60 |  |  | 42915.3958 | 84 | 84
2017-06-29 10:00 | 59 | 59 |  |  | 42915.4167 | 83 | 82
2017-06-29 10:30 | 59 | 59 |  |  | 42915.4375 | 80 | 80
2017-06-29 11:00 | 59 | 59 |  |  | 42915.4583 | 79 | 79
2017-06-29 11:30 | 60 | 60 |  |  | 42915.4792 | 80 | 79
2017-06-29 12:00 | 59 | 59 |  |  | 42915.5 | 80 | 79
2017-06-29 12:30 | 59 | 59 |  |  | 42915.5208 | 80 | 79
2017-06-29 13:00 | 60 | 60 |  |  | 42915.5417 | 81 | 81
2017-06-29 13:30 | 62 | 62 |  |  | 42915.5625 | 82 | 82
2017-06-29 14:00 | 63 | 63 |  |  | 42915.5833 | 83 | 83
2017-06-29 14:30 | 63 | 63 |  |  | 42915.6042 | 84 | 84
2017-06-29 15:00 | 63 | 63 |  |  | 42915.625 | 85 | 84
2017-06-29 15:30 | 62 | 62 |  |  | 42915.6458 | 84 | 84
2017-06-29 16:00 | 65 | 65 |  |  | 42915.6667 | 87 | 86
2017-06-29 16:30 | 68 | 68 |  |  | 42915.6875 | 90 | 90
2017-06-29 17:00 | 69 | 69 |  |  | 42915.7083 | 91 | 91
2017-06-29 17:30 | 71 | 71 |  |  | 42915.7292 | 91 | 91
2017-06-29 18:00 | 72 | 72 |  |  | 42915.75 | 90 | 90
2017-06-29 18:30 | 70 | 70 |  |  | 42915.7708 | 87 | 87
2017-06-29 19:00 | 72 | 72 |  |  | 42915.7917 | 89 | 89
2017-06-29 19:30 | 72 | 72 |  |  | 42915.8125 | 88 | 88
2017-06-29 20:00 | 72 | 72 |  |  | 42915.8333 | 89 | 89
2017-06-29 20:30 | 74 | 74 |  |  | 42915.8542 | 90 | 90
2017-06-29 21:00 | 70 | 70 |  |  | 42915.875 | 85 | 84
2017-06-29 21:30 | 65 | 65 |  |  | 42915.8958 | 79 | 79
2017-06-29 22:00 | 63 | 63 |  |  | 42915.9167 | 79 | 79
2017-06-29 22:30 | 61 | 61 |  |  | 42915.9375 | 77 | 77
2017-06-29 23:00 | 58 | 58 |  |  | 42915.9583 | 73 | 72
2017-06-29 23:30 | 56 | 55 |  |  | 42915.9792 | 70 | 70
2017-06-30 | 51 | 50 |  |  | 42916 | 65 | 64
2017-06-30 00:30 | 46 | 44 |  |  | 42916.0208 | 58 | 57
2017-06-30 01:00 | 44 | 42 |  |  | 42916.0417 | 55 | 54
2017-06-30 01:30 | 41 | 39 |  |  | 42916.0625 | 51 | 51
2017-06-30 02:00 | 40 | 38 |  |  | 42916.0833 | 50 | 50
2017-06-30 02:30 | 38 | 36 |  |  | 42916.1042 | 49 | 49
2017-06-30 03:00 | 37 | 36 |  |  | 42916.125 | 49 | 49
2017-06-30 03:30 | 38 | 37 |  |  | 42916.1458 | 49 | 49
2017-06-30 04:00 | 36 | 35 |  |  | 42916.1667 | 47 | 47
2017-06-30 04:30 | 38 | 37 |  |  | 42916.1875 | 49 | 49
2017-06-30 05:00 | 39 | 38 |  |  | 42916.2083 | 50 | 50
2017-06-30 05:30 | 42 | 42 |  |  | 42916.2292 | 55 | 55
2017-06-30 06:00 | 47 | 46 |  |  | 42916.25 | 62 | 61
2017-06-30 06:30 | 53 | 52 |  |  | 42916.2708 | 70 | 70
2017-06-30 07:00 | 58 | 57 |  |  | 42916.2917 | 81 | 80
2017-06-30 07:30 | 64 | 61 |  |  | 42916.3125 | 89 | 87
2017-06-30 08:00 | 64 | 62 |  |  | 42916.3333 | 90 | 88
2017-06-30 08:30 | 65 | 63 |  |  | 42916.3542 | 92 | 91
2017-06-30 09:00 | 70 | 68 |  |  | 42916.375 | 89 | 88
2017-06-30 09:30 | 68 | 66 |  |  | 42916.3958 | 86 | 84
2017-06-30 10:00 | 67 | 65 |  |  | 42916.4167 | 83 | 82
2017-06-30 10:30 | 68 | 66 |  |  | 42916.4375 | 82 | 80
2017-06-30 11:00 | 66 | 64 |  |  | 42916.4583 | 80 | 78
2017-06-30 11:30 | 65 | 63 |  |  | 42916.4792 | 79 | 77
2017-06-30 12:00 | 63 | 61 |  |  | 42916.5 | 78 | 76
2017-06-30 12:30 | 63 | 61 |  |  | 42916.5208 | 79 | 78
2017-06-30 13:00 | 64 | 62 |  |  | 42916.5417 | 79 | 77
2017-06-30 13:30 | 64 | 62 |  |  | 42916.5625 | 79 | 77
2017-06-30 14:00 | 63 | 61 |  |  | 42916.5833 | 78 | 77
2017-06-30 14:30 | 64 | 62 |  |  | 42916.6042 | 77 | 75
2017-06-30 15:00 | 64 | 62 |  |  | 42916.625 | 78 | 76
2017-06-30 15:30 | 60 | 57 |  |  | 42916.6458 | 80 | 79
2017-06-30 16:00 | 61 | 59 |  |  | 42916.6667 | 81 | 79
2017-06-30 16:30 | 62 | 59 |  |  | 42916.6875 | 82 | 81
2017-06-30 17:00 | 62 | 60 |  |  | 42916.7083 | 84 | 83
2017-06-30 17:30 | 64 | 62 |  |  | 42916.7292 | 86 | 84
2017-06-30 18:00 | 62 | 60 |  |  | 42916.75 | 83 | 81
2017-06-30 18:30 | 59 | 57 |  |  | 42916.7708 | 79 | 77
2017-06-30 19:00 | 60 | 58 |  |  | 42916.7917 | 81 | 78
2017-06-30 19:30 | 62 | 59 |  |  | 42916.8125 | 82 | 79
2017-06-30 20:00 | 64 | 60 |  |  | 42916.8333 | 84 | 80
2017-06-30 20:30 | 60 | 57 |  |  | 42916.8542 | 81 | 78
2017-06-30 21:00 | 59 | 56 |  |  | 42916.875 | 80 | 76
2017-06-30 21:30 | 57 | 53 |  |  | 42916.8958 | 75 | 71
2017-06-30 22:00 | 54 | 53 |  |  | 42916.9167 | 72 | 72
2017-06-30 22:30 | 53 | 53 |  |  | 42916.9375 | 71 | 71
2017-06-30 23:00 | 51 | 51 |  |  | 42916.9583 | 67 | 67
2017-06-30 23:30 | 48 | 48 |  |  | 42916.9792 | 63 | 63
2017-07-01 | 44 | 43 |  |  | 42917 | 59 | 59
2017-07-01 00:30 | 41 | 40 |  |  | 42917.0208 | 54 | 54
2017-07-01 01:00 | 39 | 38 |  |  | 42917.0417 | 51 | 51
2017-07-01 01:30 | 36 | 35 |  |  | 42917.0625 | 47 | 47
2017-07-01 02:00 | 35 | 33 |  |  | 42917.0833 | 45 | 45
2017-07-01 02:30 | 36 | 35 |  |  | 42917.1042 | 46 | 46
2017-07-01 03:00 | 34 | 32 |  |  | 42917.125 | 45 | 45
2017-07-01 03:30 | 32 | 31 |  |  | 42917.1458 | 43 | 43
2017-07-01 04:00 | 31 | 30 |  |  | 42917.1667 | 42 | 42
2017-07-01 04:30 | 32 | 31 |  |  | 42917.1875 | 44 | 43
2017-07-01 05:00 | 33 | 33 |  |  | 42917.2083 | 45 | 45
2017-07-01 05:30 | 37 | 36 |  |  | 42917.2292 | 49 | 49
2017-07-01 06:00 | 38 | 37 |  |  | 42917.25 | 51 | 51
2017-07-01 06:30 | 38 | 38 |  |  | 42917.2708 | 53 | 52
2017-07-01 07:00 | 38 | 38 |  |  | 42917.2917 | 54 | 53
2017-07-01 07:30 | 40 | 40 |  |  | 42917.3125 | 60 | 59
2017-07-01 08:00 | 53 | 52 |  |  | 42917.3333 | 79 | 79
2017-07-01 08:30 | 55 | 55 |  |  | 42917.3542 | 82 | 82
2017-07-01 09:00 | 55 | 55 |  |  | 42917.375 | 82 | 82
2017-07-01 09:30 | 54 | 54 |  |  | 42917.3958 | 81 | 80
2017-07-01 10:00 | 53 | 53 |  |  | 42917.4167 | 78 | 78
2017-07-01 10:30 | 51 | 51 |  |  | 42917.4375 | 76 | 75
2017-07-01 11:00 | 51 | 51 |  |  | 42917.4583 | 75 | 75
2017-07-01 11:30 | 50 | 49 |  |  | 42917.4792 | 72 | 71
2017-07-01 12:00 | 47 | 47 |  |  | 42917.5 | 69 | 69
2017-07-01 12:30 | 46 | 45 |  |  | 42917.5208 | 69 | 68
2017-07-01 13:00 | 46 | 45 |  |  | 42917.5417 | 68 | 68
2017-07-01 13:30 | 45 | 45 |  |  | 42917.5625 | 68 | 67
2017-07-01 14:00 | 46 | 46 |  |  | 42917.5833 | 69 | 68
2017-07-01 14:30 | 47 | 46 |  |  | 42917.6042 | 69 | 68
2017-07-01 15:00 | 43 | 42 |  |  | 42917.625 | 63 | 62
2017-07-01 15:30 | 40 | 40 |  |  | 42917.6458 | 57 | 56
2017-07-01 16:00 | 44 | 44 |  |  | 42917.6667 | 61 | 59
2017-07-01 16:30 | 45 | 45 |  |  | 42917.6875 | 63 | 62
2017-07-01 17:00 | 47 | 47 |  |  | 42917.7083 | 66 | 65
2017-07-01 17:30 | 50 | 50 |  |  | 42917.7292 | 69 | 68
2017-07-01 18:00 | 52 | 52 |  |  | 42917.75 | 69 | 69
2017-07-01 18:30 | 52 | 52 |  |  | 42917.7708 | 71 | 70
2017-07-01 19:00 | 54 | 53 |  |  | 42917.7917 | 72 | 72
2017-07-01 19:30 | 57 | 56 |  |  | 42917.8125 | 74 | 74
2017-07-01 20:00 | 56 | 56 |  |  | 42917.8333 | 73 | 73
2017-07-01 20:30 | 54 | 53 |  |  | 42917.8542 | 71 | 71
2017-07-01 21:00 | 53 | 52 |  |  | 42917.875 | 69 | 69
2017-07-01 21:30 | 50 | 50 |  |  | 42917.8958 | 68 | 67
2017-07-01 22:00 | 51 | 51 |  |  | 42917.9167 | 69 | 68
2017-07-01 22:30 | 51 | 51 |  |  | 42917.9375 | 69 | 68
2017-07-01 23:00 | 52 | 52 |  |  | 42917.9583 | 68 | 68
2017-07-01 23:30 | 49 | 49 |  |  | 42917.9792 | 66 | 65
2017-07-02 | 49 | 49 |  |  | 42918 | 64 | 64
2017-07-02 00:30 | 45 | 45 |  |  | 42918.0208 | 59 | 59
2017-07-02 01:00 | 43 | 42 |  |  | 42918.0417 | 55 | 55
2017-07-02 01:30 | 40 | 39 |  |  | 42918.0625 | 53 | 53
2017-07-02 02:00 | 39 | 38 |  |  | 42918.0833 | 51 | 51
2017-07-02 02:30 | 37 | 36 |  |  | 42918.1042 | 49 | 48
2017-07-02 03:00 | 36 | 35 |  |  | 42918.125 | 46 | 46
2017-07-02 03:30 | 35 | 33 |  |  | 42918.1458 | 45 | 45
2017-07-02 04:00 | 33 | 31 |  |  | 42918.1667 | 43 | 43
2017-07-02 04:30 | 32 | 31 |  |  | 42918.1875 | 42 | 42
2017-07-02 05:00 | 30 | 29 |  |  | 42918.2083 | 41 | 41
2017-07-02 05:30 | 32 | 31 |  |  | 42918.2292 | 43 | 43
2017-07-02 06:00 | 34 | 33 |  |  | 42918.25 | 47 | 46
2017-07-02 06:30 | 35 | 34 |  |  | 42918.2708 | 47 | 47
2017-07-02 07:00 | 35 | 34 |  |  | 42918.2917 | 50 | 49
2017-07-02 07:30 | 37 | 37 |  |  | 42918.3125 | 55 | 54
2017-07-02 08:00 | 54 | 53 |  |  | 42918.3333 | 83 | 83
2017-07-02 08:30 | 52 | 51 |  |  | 42918.3542 | 83 | 83
2017-07-02 09:00 | 54 | 53 |  |  | 42918.375 | 84 | 84
2017-07-02 09:30 | 55 | 55 |  |  | 42918.3958 | 86 | 86
2017-07-02 10:00 | 54 | 53 |  |  | 42918.4167 | 83 | 83
2017-07-02 10:30 | 53 | 53 |  |  | 42918.4375 | 82 | 81
2017-07-02 11:00 | 51 | 50 |  |  | 42918.4583 | 76 | 76
2017-07-02 11:30 | 40 | 34 |  |  | 42918.4792 | 47 | 47
2017-07-02 12:00 | 39 | 33 |  |  | 42918.5 | 47 | 46
2017-07-02 12:30 | 39 | 33 |  |  | 42918.5208 | 46 | 46
2017-07-02 13:00 | 39 | 33 |  |  | 42918.5417 | 46 | 46
2017-07-02 13:30 | 39 | 32 |  |  | 42918.5625 | 46 | 46
2017-07-02 14:00 | 41 | 34 |  |  | 42918.5833 | 47 | 47
2017-07-02 14:30 | 41 | 34 |  |  | 42918.6042 | 47 | 47
2017-07-02 15:00 | 42 | 36 |  |  | 42918.625 | 49 | 49
2017-07-02 15:30 | 43 | 38 |  |  | 42918.6458 | 52 | 52
2017-07-02 16:00 | 45 | 39 |  |  | 42918.6667 | 55 | 55
2017-07-02 16:30 | 48 | 43 |  |  | 42918.6875 | 60 | 60
2017-07-02 17:00 | 53 | 49 |  |  | 42918.7083 | 67 | 67
2017-07-02 17:30 | 57 | 54 |  |  | 42918.7292 | 72 | 72
2017-07-02 18:00 | 59 | 55 |  |  | 42918.75 | 72 | 72
2017-07-02 18:30 | 61 | 56 |  |  | 42918.7708 | 73 | 72
2017-07-02 19:00 | 62 | 57 |  |  | 42918.7917 | 74 | 74
2017-07-02 19:30 | 63 | 58 |  |  | 42918.8125 | 75 | 75
2017-07-02 20:00 | 62 | 58 |  |  | 42918.8333 | 76 | 76
2017-07-02 20:30 | 59 | 55 |  |  | 42918.8542 | 73 | 73
2017-07-02 21:00 | 53 | 49 |  |  | 42918.875 | 65 | 65
2017-07-02 21:30 | 54 | 49 |  |  | 42918.8958 | 65 | 65
2017-07-02 22:00 | 56 | 51 |  |  | 42918.9167 | 68 | 68
2017-07-02 22:30 | 56 | 50 |  |  | 42918.9375 | 69 | 68
2017-07-02 23:00 | 56 | 49 |  |  | 42918.9583 | 65 | 65
2017-07-02 23:30 | 54 | 47 |  |  | 42918.9792 | 64 | 63
2017-07-03 | 52 | 46 |  |  | 42919 | 61 | 61
2017-07-03 00:30 | 49 | 42 |  |  | 42919.0208 | 57 | 56
2017-07-03 01:00 | 47 | 38 |  |  | 42919.0417 | 52 | 51
2017-07-03 01:30 | 44 | 35 |  |  | 42919.0625 | 49 | 48
2017-07-03 02:00 | 42 | 32 |  |  | 42919.0833 | 46 | 45
2017-07-03 02:30 | 40 | 29 |  |  | 42919.1042 | 43 | 42
2017-07-03 03:00 | 40 | 28 |  |  | 42919.125 | 42 | 41
2017-07-03 03:30 | 39 | 28 |  |  | 42919.1458 | 41 | 40
2017-07-03 04:00 | 39 | 27 |  |  | 42919.1667 | 40 | 39
2017-07-03 04:30 | 38 | 28 |  |  | 42919.1875 | 41 | 40
2017-07-03 05:00 | 38 | 29 |  |  | 42919.2083 | 42 | 41
2017-07-03 05:30 | 41 | 35 |  |  | 42919.2292 | 48 | 47
2017-07-03 06:00 | 49 | 46 |  |  | 42919.25 | 58 | 58
2017-07-03 06:30 | 56 | 55 |  |  | 42919.2708 | 69 | 69
2017-07-03 07:00 | 61 | 59 |  |  | 42919.2917 | 79 | 78
2017-07-03 07:30 | 65 | 62 |  |  | 42919.3125 | 87 | 86
2017-07-03 08:00 | 64 | 61 |  |  | 42919.3333 | 86 | 85
2017-07-03 08:30 | 63 | 59 |  |  | 42919.3542 | 83 | 81
2017-07-03 09:00 | 60 | 56 |  |  | 42919.375 | 81 | 80
2017-07-03 09:30 | 59 | 54 |  |  | 42919.3958 | 78 | 77
2017-07-03 10:00 | 57 | 53 |  |  | 42919.4167 | 77 | 76
2017-07-03 10:30 | 54 | 50 |  |  | 42919.4375 | 73 | 72
2017-07-03 11:00 | 53 | 47 |  |  | 42919.4583 | 72 | 70
2017-07-03 11:30 | 48 | 44 |  |  | 42919.4792 | 69 | 68
2017-07-03 12:00 | 49 | 45 |  |  | 42919.5 | 67 | 66
2017-07-03 12:30 | 49 | 45 |  |  | 42919.5208 | 68 | 66
2017-07-03 13:00 | 48 | 45 |  |  | 42919.5417 | 68 | 67
2017-07-03 13:30 | 50 | 46 |  |  | 42919.5625 | 68 | 67
2017-07-03 14:00 | 50 | 46 |  |  | 42919.5833 | 69 | 68
2017-07-03 14:30 | 56 | 53 |  |  | 42919.6042 | 74 | 72
2017-07-03 15:00 | 57 | 54 |  |  | 42919.625 | 75 | 74
2017-07-03 15:30 | 56 | 52 |  |  | 42919.6458 | 73 | 72
2017-07-03 16:00 | 56 | 51 |  |  | 42919.6667 | 73 | 71
2017-07-03 16:30 | 62 | 57 |  |  | 42919.6875 | 79 | 77
2017-07-03 17:00 | 68 | 63 |  |  | 42919.7083 | 84 | 81
2017-07-03 17:30 | 78 | 70 |  |  | 42919.7292 | 96 | 89
2017-07-03 18:00 | 83 | 71 |  |  | 42919.75 | 103 | 91
2017-07-03 18:30 | 82 | 69 |  |  | 42919.7708 | 99 | 86
2017-07-03 19:00 | 82 | 70 |  |  | 42919.7917 | 99 | 88
2017-07-03 19:30 | 83 | 71 |  |  | 42919.8125 | 99 | 88
2017-07-03 20:00 | 80 | 67 |  |  | 42919.8333 | 95 | 84
2017-07-03 20:30 | 76 | 63 |  |  | 42919.8542 | 92 | 81
2017-07-03 21:00 | 73 | 59 |  |  | 42919.875 | 89 | 77
2017-07-03 21:30 | 70 | 56 |  |  | 42919.8958 | 85 | 72
2017-07-03 22:00 | 69 | 56 |  |  | 42919.9167 | 81 | 71
2017-07-03 22:30 | 68 | 55 |  |  | 42919.9375 | 80 | 72
2017-07-03 23:00 | 61 | 54 |  |  | 42919.9583 | 71 | 68
2017-07-03 23:30 | 60 | 53 |  |  | 42919.9792 | 69 | 68
2017-07-04 | 59 | 51 |  |  | 42920 | 66 | 65
2017-07-04 00:30 | 54 | 45 |  |  | 42920.0208 | 60 | 58
2017-07-04 01:00 | 54 | 42 |  |  | 42920.0417 | 57 | 54
2017-07-04 01:30 | 53 | 41 |  |  | 42920.0625 | 55 | 50
2017-07-04 02:00 | 52 | 38 |  |  | 42920.0833 | 53 | 48
2017-07-04 02:30 | 52 | 39 |  |  | 42920.1042 | 53 | 48
2017-07-04 03:00 | 51 | 37 |  |  | 42920.125 | 51 | 46
2017-07-04 03:30 | 51 | 36 |  |  | 42920.1458 | 51 | 46
2017-07-04 04:00 | 50 | 35 |  |  | 42920.1667 | 51 | 45
2017-07-04 04:30 | 49 | 35 |  |  | 42920.1875 | 51 | 45
2017-07-04 05:00 | 48 | 35 |  |  | 42920.2083 | 51 | 46
2017-07-04 05:30 | 50 | 41 |  |  | 42920.2292 | 55 | 52
2017-07-04 06:00 | 54 | 47 |  |  | 42920.25 | 62 | 60
2017-07-04 06:30 | 59 | 51 |  |  | 42920.2708 | 70 | 66
2017-07-04 07:00 | 63 | 56 |  |  | 42920.2917 | 77 | 74
2017-07-04 07:30 | 63 | 61 |  |  | 42920.3125 | 84 | 83
2017-07-04 08:00 | 63 | 61 |  |  | 42920.3333 | 85 | 85
2017-07-04 08:30 | 59 | 58 |  |  | 42920.3542 | 82 | 82
2017-07-04 09:00 | 57 | 55 |  |  | 42920.375 | 80 | 79
2017-07-04 09:30 | 58 | 56 |  |  | 42920.3958 | 82 | 82
2017-07-04 10:00 | 57 | 55 |  |  | 42920.4167 | 80 | 80
2017-07-04 10:30 | 57 | 55 |  |  | 42920.4375 | 79 | 79
2017-07-04 11:00 | 56 | 54 |  |  | 42920.4583 | 77 | 76
2017-07-04 11:30 | 55 | 52 |  |  | 42920.4792 | 76 | 75
2017-07-04 12:00 | 54 | 51 |  |  | 42920.5 | 75 | 75
2017-07-04 12:30 | 55 | 53 |  |  | 42920.5208 | 77 | 76
2017-07-04 13:00 | 56 | 53 |  |  | 42920.5417 | 78 | 78
2017-07-04 13:30 | 56 | 54 |  |  | 42920.5625 | 79 | 79
2017-07-04 14:00 | 57 | 54 |  |  | 42920.5833 | 79 | 79
2017-07-04 14:30 | 57 | 55 |  |  | 42920.6042 | 78 | 78
2017-07-04 15:00 | 58 | 56 |  |  | 42920.625 | 80 | 79
2017-07-04 15:30 | 58 | 55 |  |  | 42920.6458 | 79 | 78
2017-07-04 16:00 | 57 | 55 |  |  | 42920.6667 | 77 | 76
2017-07-04 16:30 | 58 | 56 |  |  | 42920.6875 | 77 | 76
2017-07-04 17:00 | 60 | 58 |  |  | 42920.7083 | 78 | 77
2017-07-04 17:30 | 61 | 59 |  |  | 42920.7292 | 79 | 78
2017-07-04 18:00 | 64 | 60 |  |  | 42920.75 | 79 | 77
2017-07-04 18:30 | 61 | 57 |  |  | 42920.7708 | 78 | 75
2017-07-04 19:00 | 65 | 61 |  |  | 42920.7917 | 80 | 77
2017-07-04 19:30 | 64 | 61 |  |  | 42920.8125 | 79 | 77
2017-07-04 20:00 | 62 | 59 |  |  | 42920.8333 | 76 | 74
2017-07-04 20:30 | 64 | 60 |  |  | 42920.8542 | 79 | 77
2017-07-04 21:00 | 67 | 55 |  |  | 42920.875 | 74 | 70
2017-07-04 21:30 | 65 | 52 |  |  | 42920.8958 | 71 | 66
2017-07-04 22:00 | 64 | 51 |  |  | 42920.9167 | 71 | 66
2017-07-04 22:30 | 65 | 49 |  |  | 42920.9375 | 71 | 64
2017-07-04 23:00 | 67 | 49 |  |  | 42920.9583 | 69 | 62
2017-07-04 23:30 | 65 | 47 |  |  | 42920.9792 | 66 | 59
2017-07-05 | 63 | 44 |  |  | 42921 | 63 | 56
2017-07-05 00:30 | 59 | 38 |  |  | 42921.0208 | 57 | 49
2017-07-05 01:00 | 58 | 34 |  |  | 42921.0417 | 53 | 43
2017-07-05 01:30 | 57 | 33 |  |  | 42921.0625 | 52 | 42
2017-07-05 02:00 | 58 | 32 |  |  | 42921.0833 | 52 | 42
2017-07-05 02:30 | 58 | 30 |  |  | 42921.1042 | 51 | 40
2017-07-05 03:00 | 56 | 27 |  |  | 42921.125 | 49 | 37
2017-07-05 03:30 | 56 | 28 |  |  | 42921.1458 | 49 | 37
2017-07-05 04:00 | 55 | 28 |  |  | 42921.1667 | 48 | 36
2017-07-05 04:30 | 57 | 31 |  |  | 42921.1875 | 49 | 38
2017-07-05 05:00 | 57 | 33 |  |  | 42921.2083 | 52 | 42
2017-07-05 05:30 | 59 | 39 |  |  | 42921.2292 | 56 | 48
2017-07-05 06:00 | 59 | 45 |  |  | 42921.25 | 62 | 56
2017-07-05 06:30 | 61 | 52 |  |  | 42921.2708 | 70 | 66
2017-07-05 07:00 | 65 | 56 |  |  | 42921.2917 | 76 | 73
2017-07-05 07:30 | 68 | 61 |  |  | 42921.3125 | 84 | 82
2017-07-05 08:00 | 67 | 64 |  |  | 42921.3333 | 80 | 79
2017-07-05 08:30 | 104 | 102 |  |  | 42921.3542 | 36 | 34
2017-07-05 09:00 | 98 | 97 |  |  | 42921.375 | 34 | 31
2017-07-05 09:30 | 94 | 93 |  |  | 42921.3958 | 32 | 29
2017-07-05 10:00 | 89 | 88 |  |  | 42921.4167 | 29 | 26
2017-07-05 10:30 | 87 | 86 |  |  | 42921.4375 | 29 | 26
2017-07-05 11:00 | 84 | 83 |  |  | 42921.4583 | 28 | 25
2017-07-05 11:30 | 84 | 83 |  |  | 42921.4792 | 29 | 26
2017-07-05 12:00 | 82 | 81 |  |  | 42921.5 | 29 | 26
2017-07-05 12:30 | 81 | 80 |  |  | 42921.5208 | 28 | 25
2017-07-05 13:00 | 84 | 82 |  |  | 42921.5417 | 28 | 25
2017-07-05 13:30 | 84 | 82 |  |  | 42921.5625 | 29 | 25
2017-07-05 14:00 | 86 | 85 |  |  | 42921.5833 | 29 | 25
2017-07-05 14:30 | 87 | 86 |  |  | 42921.6042 | 28 | 24
2017-07-05 15:00 | 90 | 88 |  |  | 42921.625 | 29 | 24
2017-07-05 15:30 | 94 | 91 |  |  | 42921.6458 | 30 | 24
2017-07-05 16:00 | 100 | 98 |  |  | 42921.6667 | 33 | 27
2017-07-05 16:30 | 105 | 102 |  |  | 42921.6875 | 35 | 28
2017-07-05 17:00 | 69 | 65 |  |  | 42921.7083 | 77 | 73
2017-07-05 17:30 | 66 | 61 |  |  | 42921.7292 | 84 | 80
2017-07-05 18:00 | 66 | 61 |  |  | 42921.75 | 84 | 80
2017-07-05 18:30 | 66 | 60 |  |  | 42921.7708 | 83 | 78
2017-07-05 19:00 | 67 | 61 |  |  | 42921.7917 | 84 | 78
2017-07-05 19:30 | 66 | 59 |  |  | 42921.8125 | 82 | 77
2017-07-05 20:00 | 64 | 59 |  |  | 42921.8333 | 79 | 76
2017-07-05 20:30 | 63 | 58 |  |  | 42921.8542 | 78 | 75
2017-07-05 21:00 | 61 | 55 |  |  | 42921.875 | 74 | 71
2017-07-05 21:30 | 59 | 53 |  |  | 42921.8958 | 72 | 69
2017-07-05 22:00 | 59 | 52 |  |  | 42921.9167 | 72 | 68
2017-07-05 22:30 | 59 | 54 |  |  | 42921.9375 | 72 | 69
2017-07-05 23:00 | 58 | 52 |  |  | 42921.9583 | 69 | 67
2017-07-05 23:30 | 56 | 48 |  |  | 42921.9792 | 66 | 63
2017-07-06 | 52 | 44 |  |  | 42922 | 60 | 58
2017-07-06 00:30 | 50 | 39 |  |  | 42922.0208 | 56 | 53
2017-07-06 01:00 | 49 | 37 |  |  | 42922.0417 | 54 | 49
2017-07-06 01:30 | 49 | 35 |  |  | 42922.0625 | 51 | 47
2017-07-06 02:00 | 47 | 34 |  |  | 42922.0833 | 50 | 45
2017-07-06 02:30 | 46 | 32 |  |  | 42922.1042 | 49 | 44
2017-07-06 03:00 | 46 | 31 |  |  | 42922.125 | 49 | 43
2017-07-06 03:30 | 45 | 31 |  |  | 42922.1458 | 48 | 43
2017-07-06 04:00 | 45 | 31 |  |  | 42922.1667 | 48 | 42
2017-07-06 04:30 | 45 | 32 |  |  | 42922.1875 | 49 | 44
2017-07-06 05:00 | 47 | 35 |  |  | 42922.2083 | 51 | 47
2017-07-06 05:30 | 49 | 40 |  |  | 42922.2292 | 55 | 51
2017-07-06 06:00 | 51 | 43 |  |  | 42922.25 | 59 | 56
2017-07-06 06:30 | 57 | 48 |  |  | 42922.2708 | 68 | 64
2017-07-06 07:00 | 62 | 53 |  |  | 42922.2917 | 78 | 72
2017-07-06 07:30 | 69 | 58 |  |  | 42922.3125 | 91 | 81
2017-07-06 08:00 | 66 | 59 |  |  | 42922.3333 | 89 | 83
2017-07-06 08:30 | 60 | 57 |  |  | 42922.3542 | 83 | 81
2017-07-06 09:00 | 57 | 54 |  |  | 42922.375 | 79 | 77
2017-07-06 09:30 | 55 | 52 |  |  | 42922.3958 | 75 | 73
2017-07-06 10:00 | 54 | 51 |  |  | 42922.4167 | 73 | 71
2017-07-06 10:30 | 52 | 50 |  |  | 42922.4375 | 71 | 70
2017-07-06 11:00 | 51 | 49 |  |  | 42922.4583 | 70 | 69
2017-07-06 11:30 | 49 | 48 |  |  | 42922.4792 | 69 | 68
2017-07-06 12:00 | 48 | 48 |  |  | 42922.5 | 68 | 68
2017-07-06 12:30 | 48 | 47 |  |  | 42922.5208 | 68 | 68
2017-07-06 13:00 | 49 | 48 |  |  | 42922.5417 | 68 | 68
2017-07-06 13:30 | 50 | 49 |  |  | 42922.5625 | 68 | 68
2017-07-06 14:00 | 51 | 50 |  |  | 42922.5833 | 69 | 69
2017-07-06 14:30 | 52 | 50 |  |  | 42922.6042 | 69 | 69
2017-07-06 15:00 | 54 | 52 |  |  | 42922.625 | 72 | 72
2017-07-06 15:30 | 56 | 53 |  |  | 42922.6458 | 74 | 73
2017-07-06 16:00 | 58 | 56 |  |  | 42922.6667 | 76 | 75
2017-07-06 16:30 | 61 | 58 |  |  | 42922.6875 | 80 | 79
2017-07-06 17:00 | 63 | 61 |  |  | 42922.7083 | 83 | 82
2017-07-06 17:30 | 66 | 62 |  |  | 42922.7292 | 85 | 83
2017-07-06 18:00 | 72 | 63 |  |  | 42922.75 | 92 | 84
2017-07-06 18:30 | 73 | 64 |  |  | 42922.7708 | 93 | 84
2017-07-06 19:00 | 73 | 64 |  |  | 42922.7917 | 91 | 83
2017-07-06 19:30 | 71 | 62 |  |  | 42922.8125 | 88 | 79
2017-07-06 20:00 | 69 | 61 |  |  | 42922.8333 | 86 | 79
2017-07-06 20:30 | 65 | 60 |  |  | 42922.8542 | 82 | 78
2017-07-06 21:00 | 62 | 56 |  |  | 42922.875 | 76 | 72
2017-07-06 21:30 | 59 | 51 |  |  | 42922.8958 | 71 | 66
2017-07-06 22:00 | 60 | 51 |  |  | 42922.9167 | 71 | 66
2017-07-06 22:30 | 60 | 50 |  |  | 42922.9375 | 71 | 66
2017-07-06 23:00 | 62 | 52 |  |  | 42922.9583 | 73 | 67
2017-07-06 23:30 | 61 | 50 |  |  | 42922.9792 | 70 | 64
2017-07-07 | 59 | 46 |  |  | 42923 | 68 | 60
2017-07-07 00:30 | 56 | 40 |  |  | 42923.0208 | 62 | 52
2017-07-07 01:00 | 53 | 37 |  |  | 42923.0417 | 57 | 48
2017-07-07 01:30 | 49 | 32 |  |  | 42923.0625 | 52 | 43
2017-07-07 02:00 | 48 | 30 |  |  | 42923.0833 | 50 | 40
2017-07-07 02:30 | 44 | 30 |  |  | 42923.1042 | 47 | 41
2017-07-07 03:00 | 43 | 28 |  |  | 42923.125 | 45 | 39
2017-07-07 03:30 | 43 | 27 |  |  | 42923.1458 | 44 | 38
2017-07-07 04:00 | 43 | 28 |  |  | 42923.1667 | 45 | 39
2017-07-07 04:30 | 44 | 29 |  |  | 42923.1875 | 45 | 40
2017-07-07 05:00 | 44 | 30 |  |  | 42923.2083 | 46 | 41
2017-07-07 05:30 | 45 | 34 |  |  | 42923.2292 | 50 | 46
2017-07-07 06:00 | 50 | 42 |  |  | 42923.25 | 57 | 54
2017-07-07 06:30 | 55 | 49 |  |  | 42923.2708 | 66 | 64
2017-07-07 07:00 | 57 | 52 |  |  | 42923.2917 | 73 | 71
2017-07-07 07:30 | 62 | 59 |  |  | 42923.3125 | 83 | 81
2017-07-07 08:00 | 64 | 59 |  |  | 42923.3333 | 85 | 82
2017-07-07 08:30 | 64 | 58 |  |  | 42923.3542 | 87 | 84
2017-07-07 09:00 | 63 | 59 |  |  | 42923.375 | 85 | 83
2017-07-07 09:30 | 62 | 59 |  |  | 42923.3958 | 85 | 84
2017-07-07 10:00 | 65 | 62 |  |  | 42923.4167 | 88 | 87
2017-07-07 10:30 | 68 | 65 |  |  | 42923.4375 | 91 | 90
2017-07-07 11:00 | 68 | 65 |  |  | 42923.4583 | 91 | 89
2017-07-07 11:30 | 68 | 64 |  |  | 42923.4792 | 91 | 88
2017-07-07 12:00 | 69 | 64 |  |  | 42923.5 | 91 | 88
2017-07-07 12:30 | 70 | 66 |  |  | 42923.5208 | 92 | 89
2017-07-07 13:00 | 68 | 64 |  |  | 42923.5417 | 90 | 86
2017-07-07 13:30 | 67 | 62 |  |  | 42923.5625 | 87 | 84
2017-07-07 14:00 | 66 | 61 |  |  | 42923.5833 | 87 | 84
2017-07-07 14:30 | 63 | 59 |  |  | 42923.6042 | 84 | 81
2017-07-07 15:00 | 63 | 58 |  |  | 42923.625 | 83 | 80
2017-07-07 15:30 | 64 | 59 |  |  | 42923.6458 | 83 | 79
2017-07-07 16:00 | 65 | 59 |  |  | 42923.6667 | 84 | 80
2017-07-07 16:30 | 65 | 59 |  |  | 42923.6875 | 86 | 80
2017-07-07 17:00 | 66 | 60 |  |  | 42923.7083 | 87 | 81
2017-07-07 17:30 | 68 | 61 |  |  | 42923.7292 | 88 | 82
2017-07-07 18:00 | 70 | 62 |  |  | 42923.75 | 88 | 81
2017-07-07 18:30 | 69 | 62 |  |  | 42923.7708 | 85 | 79
2017-07-07 19:00 | 69 | 63 |  |  | 42923.7917 | 85 | 81
2017-07-07 19:30 | 67 | 61 |  |  | 42923.8125 | 82 | 78
2017-07-07 20:00 | 65 | 59 |  |  | 42923.8333 | 80 | 75
2017-07-07 20:30 | 63 | 57 |  |  | 42923.8542 | 78 | 73
2017-07-07 21:00 | 59 | 53 |  |  | 42923.875 | 74 | 68
2017-07-07 21:30 | 57 | 49 |  |  | 42923.8958 | 72 | 65
2017-07-07 22:00 | 56 | 47 |  |  | 42923.9167 | 71 | 64
2017-07-07 22:30 | 52 | 47 |  |  | 42923.9375 | 65 | 64
2017-07-07 23:00 | 51 | 45 |  |  | 42923.9583 | 62 | 61
2017-07-07 23:30 | 49 | 42 |  |  | 42923.9792 | 59 | 58
2017-07-08 | 46 | 38 |  |  | 42924 | 54 | 52
2017-07-08 00:30 | 43 | 33 |  |  | 42924.0208 | 48 | 46
2017-07-08 01:00 | 42 | 31 |  |  | 42924.0417 | 46 | 43
2017-07-08 01:30 | 42 | 31 |  |  | 42924.0625 | 46 | 43
2017-07-08 02:00 | 41 | 30 |  |  | 42924.0833 | 44 | 41
2017-07-08 02:30 | 41 | 28 |  |  | 42924.1042 | 42 | 39
2017-07-08 03:00 | 40 | 26 |  |  | 42924.125 | 42 | 38
2017-07-08 03:30 | 40 | 26 |  |  | 42924.1458 | 42 | 38
2017-07-08 04:00 | 41 | 28 |  |  | 42924.1667 | 43 | 39
2017-07-08 04:30 | 42 | 29 |  |  | 42924.1875 | 45 | 41
2017-07-08 05:00 | 41 | 29 |  |  | 42924.2083 | 44 | 40
2017-07-08 05:30 | 43 | 31 |  |  | 42924.2292 | 46 | 43
2017-07-08 06:00 | 43 | 32 |  |  | 42924.25 | 48 | 45
2017-07-08 06:30 | 44 | 34 |  |  | 42924.2708 | 50 | 48
2017-07-08 07:00 | 47 | 34 |  |  | 42924.2917 | 56 | 50
2017-07-08 07:30 | 44 | 36 |  |  | 42924.3125 | 55 | 51
2017-07-08 08:00 | 44 | 38 |  |  | 42924.3333 | 61 | 59
2017-07-08 08:30 | 48 | 42 |  |  | 42924.3542 | 69 | 67
2017-07-08 09:00 | 47 | 42 |  |  | 42924.375 | 69 | 67
2017-07-08 09:30 | 46 | 41 |  |  | 42924.3958 | 68 | 66
2017-07-08 10:00 | 46 | 41 |  |  | 42924.4167 | 67 | 65
2017-07-08 10:30 | 44 | 39 |  |  | 42924.4375 | 63 | 62
2017-07-08 11:00 | 44 | 38 |  |  | 42924.4583 | 63 | 61
2017-07-08 11:30 | 50 | 37 |  |  | 42924.4792 | 62 | 58
2017-07-08 12:00 | 51 | 36 |  |  | 42924.5 | 60 | 56
2017-07-08 12:30 | 50 | 34 |  |  | 42924.5208 | 58 | 54
2017-07-08 13:00 | 50 | 34 |  |  | 42924.5417 | 58 | 54
2017-07-08 13:30 | 51 | 34 |  |  | 42924.5625 | 58 | 53
2017-07-08 14:00 | 48 | 32 |  |  | 42924.5833 | 52 | 48
2017-07-08 14:30 | 46 | 30 |  |  | 42924.6042 | 46 | 44
2017-07-08 15:00 | 47 | 32 |  |  | 42924.625 | 49 | 46
2017-07-08 15:30 | 48 | 34 |  |  | 42924.6458 | 51 | 49
2017-07-08 16:00 | 51 | 38 |  |  | 42924.6667 | 57 | 54
2017-07-08 16:30 | 52 | 39 |  |  | 42924.6875 | 58 | 56
2017-07-08 17:00 | 51 | 42 |  |  | 42924.7083 | 64 | 61
2017-07-08 17:30 | 46 | 45 |  |  | 42924.7292 | 65 | 64
2017-07-08 18:00 | 49 | 48 |  |  | 42924.75 | 68 | 67
2017-07-08 18:30 | 50 | 49 |  |  | 42924.7708 | 70 | 68
2017-07-08 19:00 | 52 | 51 |  |  | 42924.7917 | 72 | 70
2017-07-08 19:30 | 51 | 50 |  |  | 42924.8125 | 70 | 69
2017-07-08 20:00 | 50 | 48 |  |  | 42924.8333 | 70 | 68
2017-07-08 20:30 | 53 | 51 |  |  | 42924.8542 | 71 | 69
2017-07-08 21:00 | 49 | 47 |  |  | 42924.875 | 67 | 65
2017-07-08 21:30 | 48 | 45 |  |  | 42924.8958 | 65 | 63
2017-07-08 22:00 | 49 | 46 |  |  | 42924.9167 | 66 | 64
2017-07-08 22:30 | 49 | 47 |  |  | 42924.9375 | 66 | 64
2017-07-08 23:00 | 49 | 47 |  |  | 42924.9583 | 64 | 63
2017-07-08 23:30 | 47 | 45 |  |  | 42924.9792 | 62 | 61
2017-07-09 | 43 | 41 |  |  | 42925 | 57 | 56
2017-07-09 00:30 | 39 | 37 |  |  | 42925.0208 | 52 | 51
2017-07-09 01:00 | 35 | 32 |  |  | 42925.0417 | 47 | 46
2017-07-09 01:30 | 33 | 30 |  |  | 42925.0625 | 44 | 43
2017-07-09 02:00 | 32 | 28 |  |  | 42925.0833 | 43 | 42
2017-07-09 02:30 | 31 | 26 |  |  | 42925.1042 | 41 | 40
2017-07-09 03:00 | 30 | 25 |  |  | 42925.125 | 39 | 38
2017-07-09 03:30 | 30 | 26 |  |  | 42925.1458 | 39 | 39
2017-07-09 04:00 | 29 | 26 |  |  | 42925.1667 | 39 | 39
2017-07-09 04:30 | 29 | 25 |  |  | 42925.1875 | 39 | 38
2017-07-09 05:00 | 28 | 25 |  |  | 42925.2083 | 39 | 38
2017-07-09 05:30 | 29 | 27 |  |  | 42925.2292 | 40 | 39
2017-07-09 06:00 | 29 | 27 |  |  | 42925.25 | 40 | 40
2017-07-09 06:30 | 30 | 27 |  |  | 42925.2708 | 42 | 42
2017-07-09 07:00 | 32 | 29 |  |  | 42925.2917 | 44 | 44
2017-07-09 07:30 | 34 | 31 |  |  | 42925.3125 | 49 | 48
2017-07-09 08:00 | 37 | 35 |  |  | 42925.3333 | 52 | 52
2017-07-09 08:30 | 39 | 37 |  |  | 42925.3542 | 54 | 54
2017-07-09 09:00 | 38 | 36 |  |  | 42925.375 | 53 | 53
2017-07-09 09:30 | 38 | 36 |  |  | 42925.3958 | 53 | 53
2017-07-09 10:00 | 39 | 38 |  |  | 42925.4167 | 52 | 52
2017-07-09 10:30 | 40 | 38 |  |  | 42925.4375 | 53 | 53
2017-07-09 11:00 | 40 | 39 |  |  | 42925.4583 | 53 | 53
2017-07-09 11:30 | 37 | 35 |  |  | 42925.4792 | 50 | 50
2017-07-09 12:00 | 36 | 34 |  |  | 42925.5 | 48 | 48
2017-07-09 12:30 | 34 | 32 |  |  | 42925.5208 | 47 | 47
2017-07-09 13:00 | 35 | 32 |  |  | 42925.5417 | 48 | 47
2017-07-09 13:30 | 37 | 34 |  |  | 42925.5625 | 50 | 50
2017-07-09 14:00 | 35 | 33 |  |  | 42925.5833 | 49 | 48
2017-07-09 14:30 | 37 | 35 |  |  | 42925.6042 | 50 | 50
2017-07-09 15:00 | 40 | 38 |  |  | 42925.625 | 52 | 52
2017-07-09 15:30 | 39 | 37 |  |  | 42925.6458 | 52 | 52
2017-07-09 16:00 | 46 | 42 |  |  | 42925.6667 | 59 | 57
2017-07-09 16:30 | 52 | 49 |  |  | 42925.6875 | 66 | 64
2017-07-09 17:00 | 55 | 52 |  |  | 42925.7083 | 72 | 70
2017-07-09 17:30 | 61 | 53 |  |  | 42925.7292 | 83 | 71
2017-07-09 18:00 | 65 | 56 |  |  | 42925.75 | 88 | 73
2017-07-09 18:30 | 63 | 55 |  |  | 42925.7708 | 87 | 74
2017-07-09 19:00 | 63 | 55 |  |  | 42925.7917 | 88 | 75
2017-07-09 19:30 | 69 | 54 |  |  | 42925.8125 | 90 | 74
2017-07-09 20:00 | 72 | 53 |  |  | 42925.8333 | 90 | 71
2017-07-09 20:30 | 70 | 51 |  |  | 42925.8542 | 89 | 70
2017-07-09 21:00 | 68 | 50 |  |  | 42925.875 | 83 | 67
2017-07-09 21:30 | 64 | 48 |  |  | 42925.8958 | 79 | 66
2017-07-09 22:00 | 60 | 46 |  |  | 42925.9167 | 74 | 64
2017-07-09 22:30 | 54 | 45 |  |  | 42925.9375 | 67 | 63
2017-07-09 23:00 | 54 | 44 |  |  | 42925.9583 | 65 | 61
2017-07-09 23:30 | 48 | 41 |  |  | 42925.9792 | 59 | 58
2017-07-10 | 45 | 38 |  |  | 42926 | 55 | 54
2017-07-10 00:30 | 43 | 35 |  |  | 42926.0208 | 52 | 50
2017-07-10 01:00 | 41 | 31 |  |  | 42926.0417 | 47 | 45
2017-07-10 01:30 | 40 | 29 |  |  | 42926.0625 | 45 | 43
2017-07-10 02:00 | 39 | 29 |  |  | 42926.0833 | 44 | 42
2017-07-10 02:30 | 40 | 30 |  |  | 42926.1042 | 45 | 43
2017-07-10 03:00 | 40 | 29 |  |  | 42926.125 | 44 | 41
2017-07-10 03:30 | 40 | 29 |  |  | 42926.1458 | 44 | 41
2017-07-10 04:00 | 40 | 30 |  |  | 42926.1667 | 45 | 42
2017-07-10 04:30 | 40 | 30 |  |  | 42926.1875 | 44 | 41
2017-07-10 05:00 | 41 | 32 |  |  | 42926.2083 | 45 | 43
2017-07-10 05:30 | 44 | 38 |  |  | 42926.2292 | 51 | 49
2017-07-10 06:00 | 47 | 44 |  |  | 42926.25 | 58 | 58
2017-07-10 06:30 | 53 | 52 |  |  | 42926.2708 | 68 | 68
2017-07-10 07:00 | 60 | 60 |  |  | 42926.2917 | 81 | 81
2017-07-10 07:30 | 67 | 67 |  |  | 42926.3125 | 91 | 91
2017-07-10 08:00 | 67 | 66 |  |  | 42926.3333 | 92 | 91
2017-07-10 08:30 | 62 | 60 |  |  | 42926.3542 | 89 | 88
2017-07-10 09:00 | 59 | 57 |  |  | 42926.375 | 83 | 82
2017-07-10 09:30 | 57 | 56 |  |  | 42926.3958 | 85 | 84
2017-07-10 10:00 | 57 | 56 |  |  | 42926.4167 | 82 | 81
2017-07-10 10:30 | 58 | 57 |  |  | 42926.4375 | 82 | 81
2017-07-10 11:00 | 57 | 55 |  |  | 42926.4583 | 80 | 79
2017-07-10 11:30 | 51 | 50 |  |  | 42926.4792 | 73 | 72
2017-07-10 12:00 | 51 | 51 |  |  | 42926.5 | 70 | 70
2017-07-10 12:30 | 49 | 49 |  |  | 42926.5208 | 69 | 69
2017-07-10 13:00 | 49 | 49 |  |  | 42926.5417 | 70 | 70
2017-07-10 13:30 | 51 | 50 |  |  | 42926.5625 | 72 | 72
2017-07-10 14:00 | 51 | 50 |  |  | 42926.5833 | 71 | 71
2017-07-10 14:30 | 54 | 54 |  |  | 42926.6042 | 74 | 74
2017-07-10 15:00 | 54 | 54 |  |  | 42926.625 | 75 | 75
2017-07-10 15:30 | 56 | 56 |  |  | 42926.6458 | 76 | 76
2017-07-10 16:00 | 58 | 56 |  |  | 42926.6667 | 77 | 76
2017-07-10 16:30 | 61 | 59 |  |  | 42926.6875 | 80 | 79
2017-07-10 17:00 | 62 | 61 |  |  | 42926.7083 | 83 | 83
2017-07-10 17:30 | 68 | 66 |  |  | 42926.7292 | 87 | 86
2017-07-10 18:00 | 69 | 67 |  |  | 42926.75 | 88 | 87
2017-07-10 18:30 | 68 | 66 |  |  | 42926.7708 | 85 | 84
2017-07-10 19:00 | 69 | 67 |  |  | 42926.7917 | 86 | 86
2017-07-10 19:30 | 68 | 67 |  |  | 42926.8125 | 86 | 86
2017-07-10 20:00 | 66 | 65 |  |  | 42926.8333 | 85 | 84
2017-07-10 20:30 | 66 | 65 |  |  | 42926.8542 | 83 | 83
2017-07-10 21:00 | 62 | 61 |  |  | 42926.875 | 78 | 78
2017-07-10 21:30 | 57 | 57 |  |  | 42926.8958 | 73 | 73
2017-07-10 22:00 | 55 | 54 |  |  | 42926.9167 | 71 | 71
2017-07-10 22:30 | 53 | 52 |  |  | 42926.9375 | 70 | 70
2017-07-10 23:00 | 56 | 54 |  |  | 42926.9583 | 70 | 69
2017-07-10 23:30 | 53 | 51 |  |  | 42926.9792 | 65 | 65
2017-07-11 | 49 | 46 |  |  | 42927 | 60 | 60
2017-07-11 00:30 | 43 | 39 |  |  | 42927.0208 | 52 | 51
2017-07-11 01:00 | 39 | 34 |  |  | 42927.0417 | 47 | 45
2017-07-11 01:30 | 38 | 32 |  |  | 42927.0625 | 46 | 44
2017-07-11 02:00 | 38 | 32 |  |  | 42927.0833 | 44 | 42
2017-07-11 02:30 | 38 | 32 |  |  | 42927.1042 | 44 | 42
2017-07-11 03:00 | 37 | 31 |  |  | 42927.125 | 44 | 42
2017-07-11 03:30 | 38 | 31 |  |  | 42927.1458 | 45 | 43
2017-07-11 04:00 | 38 | 32 |  |  | 42927.1667 | 45 | 43
2017-07-11 04:30 | 39 | 34 |  |  | 42927.1875 | 47 | 45
2017-07-11 05:00 | 41 | 37 |  |  | 42927.2083 | 50 | 48
2017-07-11 05:30 | 45 | 42 |  |  | 42927.2292 | 54 | 54
2017-07-11 06:00 | 50 | 47 |  |  | 42927.25 | 62 | 60
2017-07-11 06:30 | 61 | 55 |  |  | 42927.2708 | 79 | 72
2017-07-11 07:00 | 66 | 62 |  |  | 42927.2917 | 88 | 83
2017-07-11 07:30 | 69 | 66 |  |  | 42927.3125 | 96 | 92
2017-07-11 08:00 | 56 | 53 |  |  | 42927.3333 | 92 | 88
2017-07-11 08:30 | 39 | 36 |  |  | 42927.3542 | 84 | 80
2017-07-11 09:00 | 37 | 33 |  |  | 42927.375 | 79 | 74
2017-07-11 09:30 | 36 | 32 |  |  | 42927.3958 | 75 | 71
2017-07-11 10:00 | 34 | 30 |  |  | 42927.4167 | 72 | 68
2017-07-11 10:30 | 35 | 29 |  |  | 42927.4375 | 70 | 65
2017-07-11 11:00 | 33 | 28 |  |  | 42927.4583 | 67 | 62
2017-07-11 11:30 | 33 | 28 |  |  | 42927.4792 | 66 | 62
2017-07-11 12:00 | 33 | 28 |  |  | 42927.5 | 66 | 62
2017-07-11 12:30 | 33 | 28 |  |  | 42927.5208 | 65 | 62
2017-07-11 13:00 | 34 | 29 |  |  | 42927.5417 | 65 | 62
2017-07-11 13:30 | 33 | 30 |  |  | 42927.5625 | 66 | 62
2017-07-11 14:00 | 33 | 30 |  |  | 42927.5833 | 66 | 62
2017-07-11 14:30 | 33 | 30 |  |  | 42927.6042 | 66 | 63
2017-07-11 15:00 | 33 | 29 |  |  | 42927.625 | 67 | 63
2017-07-11 15:30 | 48 | 44 |  |  | 42927.6458 | 75 | 71
2017-07-11 16:00 | 57 | 54 |  |  | 42927.6667 | 80 | 77
2017-07-11 16:30 | 58 | 55 |  |  | 42927.6875 | 83 | 79
2017-07-11 17:00 | 62 | 58 |  |  | 42927.7083 | 87 | 82
2017-07-11 17:30 | 65 | 60 |  |  | 42927.7292 | 93 | 85
2017-07-11 18:00 | 66 | 60 |  |  | 42927.75 | 94 | 83
2017-07-11 18:30 | 65 | 59 |  |  | 42927.7708 | 92 | 81
2017-07-11 19:00 | 69 | 64 |  |  | 42927.7917 | 97 | 86
2017-07-11 19:30 | 70 | 65 |  |  | 42927.8125 | 94 | 86
2017-07-11 20:00 | 68 | 64 |  |  | 42927.8333 | 93 | 85
2017-07-11 20:30 | 68 | 64 |  |  | 42927.8542 | 92 | 85
2017-07-11 21:00 | 65 | 61 |  |  | 42927.875 | 88 | 80
2017-07-11 21:30 | 59 | 57 |  |  | 42927.8958 | 78 | 75
2017-07-11 22:00 | 57 | 56 |  |  | 42927.9167 | 76 | 75
2017-07-11 22:30 | 56 | 56 |  |  | 42927.9375 | 73 | 73
2017-07-11 23:00 | 58 | 58 |  |  | 42927.9583 | 74 | 74
2017-07-11 23:30 | 53 | 53 |  |  | 42927.9792 | 69 | 69
2017-07-12 | 48 | 48 |  |  | 42928 | 63 | 63
2017-07-12 00:30 | 41 | 41 |  |  | 42928.0208 | 55 | 55
2017-07-12 01:00 | 37 | 36 |  |  | 42928.0417 | 49 | 49
2017-07-12 01:30 | 37 | 36 |  |  | 42928.0625 | 47 | 47
2017-07-12 02:00 | 34 | 33 |  |  | 42928.0833 | 44 | 44
2017-07-12 02:30 | 34 | 32 |  |  | 42928.1042 | 44 | 44
2017-07-12 03:00 | 34 | 33 |  |  | 42928.125 | 44 | 44
2017-07-12 03:30 | 34 | 32 |  |  | 42928.1458 | 43 | 43
2017-07-12 04:00 | 35 | 33 |  |  | 42928.1667 | 44 | 44
2017-07-12 04:30 | 35 | 33 |  |  | 42928.1875 | 45 | 44
2017-07-12 05:00 | 36 | 35 |  |  | 42928.2083 | 46 | 46
2017-07-12 05:30 | 41 | 40 |  |  | 42928.2292 | 51 | 51
2017-07-12 06:00 | 48 | 48 |  |  | 42928.25 | 60 | 60
2017-07-12 06:30 | 57 | 57 |  |  | 42928.2708 | 73 | 73
2017-07-12 07:00 | 63 | 63 |  |  | 42928.2917 | 84 | 83
2017-07-12 07:30 | 68 | 68 |  |  | 42928.3125 | 92 | 92
2017-07-12 08:00 | 70 | 68 |  |  | 42928.3333 | 94 | 92
2017-07-12 08:30 | 67 | 65 |  |  | 42928.3542 | 92 | 90
2017-07-12 09:00 | 61 | 61 |  |  | 42928.375 | 86 | 86
2017-07-12 09:30 | 57 | 57 |  |  | 42928.3958 | 81 | 81
2017-07-12 10:00 | 54 | 54 |  |  | 42928.4167 | 78 | 78
2017-07-12 10:30 | 53 | 53 |  |  | 42928.4375 | 76 | 75
2017-07-12 11:00 | 52 | 52 |  |  | 42928.4583 | 74 | 74
2017-07-12 11:30 | 51 | 51 |  |  | 42928.4792 | 73 | 72
2017-07-12 12:00 | 50 | 49 |  |  | 42928.5 | 72 | 71
2017-07-12 12:30 | 49 | 49 |  |  | 42928.5208 | 72 | 71
2017-07-12 13:00 | 50 | 50 |  |  | 42928.5417 | 74 | 73
2017-07-12 13:30 | 53 | 53 |  |  | 42928.5625 | 77 | 76
2017-07-12 14:00 | 53 | 53 |  |  | 42928.5833 | 78 | 77
2017-07-12 14:30 | 56 | 56 |  |  | 42928.6042 | 80 | 79
2017-07-12 15:00 | 55 | 55 |  |  | 42928.625 | 80 | 79
2017-07-12 15:30 | 52 | 52 |  |  | 42928.6458 | 77 | 76
2017-07-12 16:00 | 55 | 55 |  |  | 42928.6667 | 79 | 78
2017-07-12 16:30 | 57 | 57 |  |  | 42928.6875 | 81 | 80
2017-07-12 17:00 | 60 | 60 |  |  | 42928.7083 | 84 | 84
2017-07-12 17:30 | 65 | 64 |  |  | 42928.7292 | 90 | 89
2017-07-12 18:00 | 69 | 67 |  |  | 42928.75 | 94 | 90
2017-07-12 18:30 | 69 | 67 |  |  | 42928.7708 | 93 | 90
2017-07-12 19:00 | 70 | 68 |  |  | 42928.7917 | 94 | 90
2017-07-12 19:30 | 68 | 66 |  |  | 42928.8125 | 91 | 88
2017-07-12 20:00 | 67 | 66 |  |  | 42928.8333 | 89 | 87
2017-07-12 20:30 | 67 | 66 |  |  | 42928.8542 | 88 | 87
2017-07-12 21:00 | 62 | 61 |  |  | 42928.875 | 83 | 81
2017-07-12 21:30 | 60 | 58 |  |  | 42928.8958 | 80 | 78
2017-07-12 22:00 | 59 | 56 |  |  | 42928.9167 | 79 | 77
2017-07-12 22:30 | 59 | 57 |  |  | 42928.9375 | 80 | 78
2017-07-12 23:00 | 58 | 56 |  |  | 42928.9583 | 76 | 74
2017-07-12 23:30 | 53 | 53 |  |  | 42928.9792 | 69 | 69
2017-07-13 | 49 | 47 |  |  | 42929 | 62 | 62
2017-07-13 00:30 | 45 | 41 |  |  | 42929.0208 | 56 | 55
2017-07-13 01:00 | 42 | 38 |  |  | 42929.0417 | 52 | 52
2017-07-13 01:30 | 41 | 36 |  |  | 42929.0625 | 49 | 49
2017-07-13 02:00 | 40 | 34 |  |  | 42929.0833 | 48 | 48
2017-07-13 02:30 | 39 | 34 |  |  | 42929.1042 | 48 | 47
2017-07-13 03:00 | 38 | 32 |  |  | 42929.125 | 46 | 46
2017-07-13 03:30 | 37 | 31 |  |  | 42929.1458 | 44 | 44
2017-07-13 04:00 | 38 | 32 |  |  | 42929.1667 | 45 | 44
2017-07-13 04:30 | 39 | 34 |  |  | 42929.1875 | 46 | 46
2017-07-13 05:00 | 39 | 35 |  |  | 42929.2083 | 48 | 47
2017-07-13 05:30 | 43 | 40 |  |  | 42929.2292 | 53 | 53
2017-07-13 06:00 | 50 | 49 |  |  | 42929.25 | 62 | 62
2017-07-13 06:30 | 57 | 57 |  |  | 42929.2708 | 75 | 75
2017-07-13 07:00 | 66 | 66 |  |  | 42929.2917 | 87 | 87
2017-07-13 07:30 | 73 | 73 |  |  | 42929.3125 | 97 | 97
2017-07-13 08:00 | 72 | 72 |  |  | 42929.3333 | 98 | 98
2017-07-13 08:30 | 69 | 69 |  |  | 42929.3542 | 96 | 96
2017-07-13 09:00 | 63 | 63 |  |  | 42929.375 | 89 | 89
2017-07-13 09:30 | 58 | 58 |  |  | 42929.3958 | 82 | 82
2017-07-13 10:00 | 57 | 56 |  |  | 42929.4167 | 81 | 81
2017-07-13 10:30 | 56 | 55 |  |  | 42929.4375 | 77 | 77
2017-07-13 11:00 | 54 | 54 |  |  | 42929.4583 | 76 | 76
2017-07-13 11:30 | 55 | 55 |  |  | 42929.4792 | 76 | 76
2017-07-13 12:00 | 55 | 55 |  |  | 42929.5 | 76 | 76
2017-07-13 12:30 | 56 | 56 |  |  | 42929.5208 | 79 | 79
2017-07-13 13:00 | 57 | 57 |  |  | 42929.5417 | 79 | 79
2017-07-13 13:30 | 56 | 56 |  |  | 42929.5625 | 78 | 78
2017-07-13 14:00 | 56 | 55 |  |  | 42929.5833 | 77 | 77
2017-07-13 14:30 | 59 | 59 |  |  | 42929.6042 | 78 | 78
2017-07-13 15:00 | 60 | 60 |  |  | 42929.625 | 80 | 80
2017-07-13 15:30 | 57 | 57 |  |  | 42929.6458 | 78 | 78
2017-07-13 16:00 | 58 | 58 |  |  | 42929.6667 | 81 | 81
2017-07-13 16:30 | 61 | 60 |  |  | 42929.6875 | 83 | 83
2017-07-13 17:00 | 64 | 64 |  |  | 42929.7083 | 86 | 86
2017-07-13 17:30 | 67 | 67 |  |  | 42929.7292 | 90 | 89
2017-07-13 18:00 | 72 | 71 |  |  | 42929.75 | 94 | 93
2017-07-13 18:30 | 73 | 72 |  |  | 42929.7708 | 94 | 93
2017-07-13 19:00 | 75 | 74 |  |  | 42929.7917 | 95 | 94
2017-07-13 19:30 | 74 | 74 |  |  | 42929.8125 | 94 | 94
2017-07-13 20:00 | 72 | 71 |  |  | 42929.8333 | 91 | 90
2017-07-13 20:30 | 71 | 70 |  |  | 42929.8542 | 90 | 89
2017-07-13 21:00 | 68 | 68 |  |  | 42929.875 | 87 | 86
2017-07-13 21:30 | 64 | 63 |  |  | 42929.8958 | 81 | 80
2017-07-13 22:00 | 62 | 61 |  |  | 42929.9167 | 79 | 78
2017-07-13 22:30 | 62 | 59 |  |  | 42929.9375 | 78 | 77
2017-07-13 23:00 | 61 | 57 |  |  | 42929.9583 | 74 | 73
2017-07-13 23:30 | 56 | 53 |  |  | 42929.9792 | 69 | 68
2017-07-14 | 53 | 49 |  |  | 42930 | 64 | 63
2017-07-14 00:30 | 53 | 46 |  |  | 42930.0208 | 60 | 59
2017-07-14 01:00 | 49 | 41 |  |  | 42930.0417 | 54 | 53
2017-07-14 01:30 | 47 | 39 |  |  | 42930.0625 | 51 | 50
2017-07-14 02:00 | 44 | 34 |  |  | 42930.0833 | 47 | 46
2017-07-14 02:30 | 44 | 33 |  |  | 42930.1042 | 47 | 45
2017-07-14 03:00 | 44 | 32 |  |  | 42930.125 | 47 | 45
2017-07-14 03:30 | 45 | 34 |  |  | 42930.1458 | 48 | 46
2017-07-14 04:00 | 45 | 35 |  |  | 42930.1667 | 48 | 46
2017-07-14 04:30 | 44 | 35 |  |  | 42930.1875 | 48 | 46
2017-07-14 05:00 | 46 | 38 |  |  | 42930.2083 | 51 | 49
2017-07-14 05:30 | 50 | 41 |  |  | 42930.2292 | 59 | 53
2017-07-14 06:00 | 52 | 49 |  |  | 42930.25 | 68 | 64
2017-07-14 06:30 | 62 | 60 |  |  | 42930.2708 | 81 | 78
2017-07-14 07:00 | 69 | 68 |  |  | 42930.2917 | 91 | 89
2017-07-14 07:30 | 73 | 73 |  |  | 42930.3125 | 98 | 98
2017-07-14 08:00 | 71 | 71 |  |  | 42930.3333 | 98 | 97
2017-07-14 08:30 | 66 | 66 |  |  | 42930.3542 | 93 | 92
2017-07-14 09:00 | 59 | 59 |  |  | 42930.375 | 84 | 84
2017-07-14 09:30 | 55 | 55 |  |  | 42930.3958 | 80 | 79
2017-07-14 10:00 | 53 | 53 |  |  | 42930.4167 | 78 | 76
2017-07-14 10:30 | 51 | 51 |  |  | 42930.4375 | 76 | 74
2017-07-14 11:00 | 49 | 48 |  |  | 42930.4583 | 72 | 70
2017-07-14 11:30 | 48 | 48 |  |  | 42930.4792 | 71 | 69
2017-07-14 12:00 | 49 | 48 |  |  | 42930.5 | 72 | 70
2017-07-14 12:30 | 48 | 47 |  |  | 42930.5208 | 71 | 69
2017-07-14 13:00 | 46 | 46 |  |  | 42930.5417 | 71 | 69
2017-07-14 13:30 | 48 | 47 |  |  | 42930.5625 | 73 | 72
2017-07-14 14:00 | 49 | 49 |  |  | 42930.5833 | 74 | 73
2017-07-14 14:30 | 50 | 49 |  |  | 42930.6042 | 73 | 72
2017-07-14 15:00 | 50 | 50 |  |  | 42930.625 | 72 | 72
2017-07-14 15:30 | 49 | 49 |  |  | 42930.6458 | 72 | 71
2017-07-14 16:00 | 53 | 52 |  |  | 42930.6667 | 73 | 73
2017-07-14 16:30 | 56 | 56 |  |  | 42930.6875 | 78 | 78
2017-07-14 17:00 | 61 | 61 |  |  | 42930.7083 | 83 | 82
2017-07-14 17:30 | 63 | 63 |  |  | 42930.7292 | 84 | 84
2017-07-14 18:00 | 66 | 65 |  |  | 42930.75 | 86 | 86
2017-07-14 18:30 | 65 | 65 |  |  | 42930.7708 | 84 | 83
2017-07-14 19:00 | 65 | 65 |  |  | 42930.7917 | 85 | 85
2017-07-14 19:30 | 64 | 64 |  |  | 42930.8125 | 83 | 82
2017-07-14 20:00 | 63 | 63 |  |  | 42930.8333 | 82 | 82
2017-07-14 20:30 | 65 | 65 |  |  | 42930.8542 | 83 | 82
2017-07-14 21:00 | 63 | 63 |  |  | 42930.875 | 81 | 81
2017-07-14 21:30 | 58 | 57 |  |  | 42930.8958 | 75 | 75
2017-07-14 22:00 | 55 | 55 |  |  | 42930.9167 | 72 | 72
2017-07-14 22:30 | 56 | 54 |  |  | 42930.9375 | 72 | 72
2017-07-14 23:00 | 56 | 53 |  |  | 42930.9583 | 70 | 69
2017-07-14 23:30 | 52 | 48 |  |  | 42930.9792 | 63 | 63
2017-07-15 | 48 | 44 |  |  | 42931 | 58 | 57
2017-07-15 00:30 | 46 | 41 |  |  | 42931.0208 | 55 | 54
2017-07-15 01:00 | 44 | 37 |  |  | 42931.0417 | 51 | 50
2017-07-15 01:30 | 40 | 33 |  |  | 42931.0625 | 46 | 45
2017-07-15 02:00 | 38 | 30 |  |  | 42931.0833 | 43 | 42
2017-07-15 02:30 | 37 | 29 |  |  | 42931.1042 | 42 | 40
2017-07-15 03:00 | 37 | 30 |  |  | 42931.125 | 41 | 40
2017-07-15 03:30 | 37 | 29 |  |  | 42931.1458 | 41 | 40
2017-07-15 04:00 | 37 | 29 |  |  | 42931.1667 | 41 | 39
2017-07-15 04:30 | 35 | 28 |  |  | 42931.1875 | 40 | 40
2017-07-15 05:00 | 34 | 29 |  |  | 42931.2083 | 41 | 40
2017-07-15 05:30 | 34 | 30 |  |  | 42931.2292 | 44 | 42
2017-07-15 06:00 | 36 | 32 |  |  | 42931.25 | 47 | 45
2017-07-15 06:30 | 37 | 35 |  |  | 42931.2708 | 49 | 48
2017-07-15 07:00 | 40 | 37 |  |  | 42931.2917 | 54 | 53
2017-07-15 07:30 | 43 | 41 |  |  | 42931.3125 | 57 | 57
2017-07-15 08:00 | 43 | 42 |  |  | 42931.3333 | 59 | 59
2017-07-15 08:30 | 44 | 44 |  |  | 42931.3542 | 61 | 61
2017-07-15 09:00 | 44 | 43 |  |  | 42931.375 | 61 | 60
2017-07-15 09:30 | 41 | 41 |  |  | 42931.3958 | 58 | 58
2017-07-15 10:00 | 40 | 39 |  |  | 42931.4167 | 54 | 54
2017-07-15 10:30 | 38 | 37 |  |  | 42931.4375 | 51 | 51
2017-07-15 11:00 | 38 | 37 |  |  | 42931.4583 | 51 | 51
2017-07-15 11:30 | 38 | 37 |  |  | 42931.4792 | 51 | 51
2017-07-15 12:00 | 37 | 36 |  |  | 42931.5 | 50 | 50
2017-07-15 12:30 | 36 | 35 |  |  | 42931.5208 | 50 | 50
2017-07-15 13:00 | 37 | 35 |  |  | 42931.5417 | 50 | 50
2017-07-15 13:30 | 39 | 38 |  |  | 42931.5625 | 53 | 52
2017-07-15 14:00 | 39 | 38 |  |  | 42931.5833 | 51 | 50
2017-07-15 14:30 | 39 | 38 |  |  | 42931.6042 | 51 | 51
2017-07-15 15:00 | 40 | 39 |  |  | 42931.625 | 53 | 52
2017-07-15 15:30 | 41 | 40 |  |  | 42931.6458 | 53 | 52
2017-07-15 16:00 | 43 | 42 |  |  | 42931.6667 | 56 | 56
2017-07-15 16:30 | 43 | 42 |  |  | 42931.6875 | 58 | 58
2017-07-15 17:00 | 47 | 46 |  |  | 42931.7083 | 63 | 62
2017-07-15 17:30 | 49 | 47 |  |  | 42931.7292 | 65 | 63
2017-07-15 18:00 | 57 | 52 |  |  | 42931.75 | 76 | 69
2017-07-15 18:30 | 58 | 53 |  |  | 42931.7708 | 78 | 70
2017-07-15 19:00 | 58 | 53 |  |  | 42931.7917 | 78 | 70
2017-07-15 19:30 | 55 | 50 |  |  | 42931.8125 | 75 | 67
2017-07-15 20:00 | 54 | 50 |  |  | 42931.8333 | 73 | 68
2017-07-15 20:30 | 52 | 48 |  |  | 42931.8542 | 72 | 66
2017-07-15 21:00 | 50 | 46 |  |  | 42931.875 | 69 | 63
2017-07-15 21:30 | 49 | 45 |  |  | 42931.8958 | 65 | 61
2017-07-15 22:00 | 46 | 45 |  |  | 42931.9167 | 62 | 62
2017-07-15 22:30 | 48 | 48 |  |  | 42931.9375 | 64 | 64
2017-07-15 23:00 | 48 | 47 |  |  | 42931.9583 | 63 | 63
2017-07-15 23:30 | 47 | 45 |  |  | 42931.9792 | 61 | 60
2017-07-16 | 43 | 41 |  |  | 42932 | 57 | 56
2017-07-16 00:30 | 38 | 36 |  |  | 42932.0208 | 49 | 48
2017-07-16 01:00 | 35 | 32 |  |  | 42932.0417 | 45 | 44
2017-07-16 01:30 | 33 | 30 |  |  | 42932.0625 | 44 | 43
2017-07-16 02:00 | 31 | 27 |  |  | 42932.0833 | 39 | 38
2017-07-16 02:30 | 30 | 26 |  |  | 42932.1042 | 38 | 37
2017-07-16 03:00 | 31 | 27 |  |  | 42932.125 | 38 | 37
2017-07-16 03:30 | 31 | 27 |  |  | 42932.1458 | 40 | 38
2017-07-16 04:00 | 31 | 27 |  |  | 42932.1667 | 40 | 38
2017-07-16 04:30 | 30 | 26 |  |  | 42932.1875 | 38 | 36
2017-07-16 05:00 | 31 | 27 |  |  | 42932.2083 | 39 | 37
2017-07-16 05:30 | 32 | 29 |  |  | 42932.2292 | 41 | 40
2017-07-16 06:00 | 34 | 31 |  |  | 42932.25 | 43 | 42
2017-07-16 06:30 | 36 | 33 |  |  | 42932.2708 | 47 | 46
2017-07-16 07:00 | 38 | 35 |  |  | 42932.2917 | 51 | 50
2017-07-16 07:30 | 38 | 35 |  |  | 42932.3125 | 51 | 50
2017-07-16 08:00 | 40 | 37 |  |  | 42932.3333 | 53 | 52
2017-07-16 08:30 | 39 | 37 |  |  | 42932.3542 | 53 | 52
2017-07-16 09:00 | 41 | 37 |  |  | 42932.375 | 55 | 53
2017-07-16 09:30 | 40 | 36 |  |  | 42932.3958 | 54 | 52
2017-07-16 10:00 | 44 | 41 |  |  | 42932.4167 | 55 | 53
2017-07-16 10:30 | 46 | 43 |  |  | 42932.4375 | 58 | 57
2017-07-16 11:00 | 44 | 40 |  |  | 42932.4583 | 54 | 53
2017-07-16 11:30 | 39 | 36 |  |  | 42932.4792 | 48 | 46
2017-07-16 12:00 | 39 | 36 |  |  | 42932.5 | 48 | 46
2017-07-16 12:30 | 39 | 36 |  |  | 42932.5208 | 49 | 47
2017-07-16 13:00 | 39 | 36 |  |  | 42932.5417 | 50 | 49
2017-07-16 13:30 | 39 | 37 |  |  | 42932.5625 | 50 | 49
2017-07-16 14:00 | 40 | 38 |  |  | 42932.5833 | 50 | 49
2017-07-16 14:30 | 40 | 37 |  |  | 42932.6042 | 49 | 48
2017-07-16 15:00 | 42 | 39 |  |  | 42932.625 | 53 | 52
2017-07-16 15:30 | 43 | 40 |  |  | 42932.6458 | 54 | 53
2017-07-16 16:00 | 44 | 41 |  |  | 42932.6667 | 56 | 54
2017-07-16 16:30 | 50 | 47 |  |  | 42932.6875 | 62 | 60
2017-07-16 17:00 | 51 | 51 |  |  | 42932.7083 | 66 | 66
2017-07-16 17:30 | 53 | 53 |  |  | 42932.7292 | 67 | 67
2017-07-16 18:00 | 60 | 59 |  |  | 42932.75 | 74 | 74
2017-07-16 18:30 | 62 | 61 |  |  | 42932.7708 | 77 | 77
2017-07-16 19:00 | 64 | 63 |  |  | 42932.7917 | 77 | 77
2017-07-16 19:30 | 60 | 59 |  |  | 42932.8125 | 74 | 74
2017-07-16 20:00 | 59 | 58 |  |  | 42932.8333 | 73 | 73
2017-07-16 20:30 | 58 | 57 |  |  | 42932.8542 | 73 | 73
2017-07-16 21:00 | 56 | 54 |  |  | 42932.875 | 69 | 69
2017-07-16 21:30 | 55 | 53 |  |  | 42932.8958 | 67 | 67
2017-07-16 22:00 | 53 | 52 |  |  | 42932.9167 | 67 | 67
2017-07-16 22:30 | 51 | 48 |  |  | 42932.9375 | 66 | 65
2017-07-16 23:00 | 49 | 46 |  |  | 42932.9583 | 62 | 62
2017-07-16 23:30 | 46 | 44 |  |  | 42932.9792 | 59 | 59
2017-07-17 | 43 | 40 |  |  | 42933 | 55 | 55
2017-07-17 00:30 | 38 | 38 |  |  | 42933.0208 | 51 | 51
2017-07-17 01:00 | 37 | 36 |  |  | 42933.0417 | 49 | 49
2017-07-17 01:30 | 35 | 35 |  |  | 42933.0625 | 49 | 49
2017-07-17 02:00 | 33 | 33 |  |  | 42933.0833 | 46 | 46
2017-07-17 02:30 | 32 | 32 |  |  | 42933.1042 | 45 | 45
2017-07-17 03:00 | 32 | 32 |  |  | 42933.125 | 44 | 44
2017-07-17 03:30 | 33 | 33 |  |  | 42933.1458 | 44 | 44
2017-07-17 04:00 | 34 | 34 |  |  | 42933.1667 | 46 | 46
2017-07-17 04:30 | 38 | 38 |  |  | 42933.1875 | 49 | 49
2017-07-17 05:00 | 39 | 39 |  |  | 42933.2083 | 49 | 49
2017-07-17 05:30 | 42 | 41 |  |  | 42933.2292 | 51 | 51
2017-07-17 06:00 | 45 | 45 |  |  | 42933.25 | 57 | 57
2017-07-17 06:30 | 56 | 56 |  |  | 42933.2708 | 71 | 71
2017-07-17 07:00 | 63 | 62 |  |  | 42933.2917 | 82 | 81
2017-07-17 07:30 | 69 | 69 |  |  | 42933.3125 | 93 | 91
2017-07-17 08:00 | 67 | 67 |  |  | 42933.3333 | 91 | 90
2017-07-17 08:30 | 62 | 62 |  |  | 42933.3542 | 86 | 85
2017-07-17 09:00 | 56 | 56 |  |  | 42933.375 | 79 | 79
2017-07-17 09:30 | 53 | 53 |  |  | 42933.3958 | 75 | 75
2017-07-17 10:00 | 51 | 51 |  |  | 42933.4167 | 72 | 72
2017-07-17 10:30 | 50 | 50 |  |  | 42933.4375 | 69 | 69
2017-07-17 11:00 | 49 | 49 |  |  | 42933.4583 | 69 | 69
2017-07-17 11:30 | 50 | 50 |  |  | 42933.4792 | 70 | 70
2017-07-17 12:00 | 50 | 50 |  |  | 42933.5 | 70 | 70
2017-07-17 12:30 | 52 | 52 |  |  | 42933.5208 | 73 | 73
2017-07-17 13:00 | 54 | 54 |  |  | 42933.5417 | 74 | 74
2017-07-17 13:30 | 54 | 54 |  |  | 42933.5625 | 74 | 74
2017-07-17 14:00 | 56 | 56 |  |  | 42933.5833 | 75 | 75
2017-07-17 14:30 | 57 | 57 |  |  | 42933.6042 | 76 | 76
2017-07-17 15:00 | 58 | 58 |  |  | 42933.625 | 79 | 79
2017-07-17 15:30 | 58 | 58 |  |  | 42933.6458 | 79 | 79
2017-07-17 16:00 | 62 | 62 |  |  | 42933.6667 | 82 | 82
2017-07-17 16:30 | 66 | 66 |  |  | 42933.6875 | 87 | 86
2017-07-17 17:00 | 68 | 68 |  |  | 42933.7083 | 88 | 86
2017-07-17 17:30 | 70 | 69 |  |  | 42933.7292 | 90 | 88
2017-07-17 18:00 | 73 | 73 |  |  | 42933.75 | 93 | 91
2017-07-17 18:30 | 73 | 72 |  |  | 42933.7708 | 92 | 89
2017-07-17 19:00 | 75 | 74 |  |  | 42933.7917 | 92 | 90
2017-07-17 19:30 | 72 | 71 |  |  | 42933.8125 | 89 | 87
2017-07-17 20:00 | 71 | 70 |  |  | 42933.8333 | 89 | 86
2017-07-17 20:30 | 71 | 70 |  |  | 42933.8542 | 88 | 86
2017-07-17 21:00 | 66 | 66 |  |  | 42933.875 | 83 | 81
2017-07-17 21:30 | 63 | 63 |  |  | 42933.8958 | 80 | 77
2017-07-17 22:00 | 61 | 61 |  |  | 42933.9167 | 79 | 77
2017-07-17 22:30 | 58 | 58 |  |  | 42933.9375 | 74 | 74
2017-07-17 23:00 | 54 | 54 |  |  | 42933.9583 | 71 | 70
2017-07-17 23:30 | 48 | 48 |  |  | 42933.9792 | 65 | 64
2017-07-18 | 46 | 46 |  |  | 42934 | 61 | 60
2017-07-18 00:30 | 40 | 40 |  |  | 42934.0208 | 54 | 52
2017-07-18 01:00 | 36 | 35 |  |  | 42934.0417 | 48 | 46
2017-07-18 01:30 | 33 | 32 |  |  | 42934.0625 | 45 | 43
2017-07-18 02:00 | 33 | 32 |  |  | 42934.0833 | 45 | 43
2017-07-18 02:30 | 35 | 34 |  |  | 42934.1042 | 45 | 44
2017-07-18 03:00 | 32 | 31 |  |  | 42934.125 | 43 | 41
2017-07-18 03:30 | 32 | 31 |  |  | 42934.1458 | 43 | 42
2017-07-18 04:00 | 32 | 31 |  |  | 42934.1667 | 43 | 42
2017-07-18 04:30 | 32 | 31 |  |  | 42934.1875 | 44 | 43
2017-07-18 05:00 | 32 | 31 |  |  | 42934.2083 | 45 | 43
2017-07-18 05:30 | 34 | 33 |  |  | 42934.2292 | 48 | 47
2017-07-18 06:00 | 42 | 42 |  |  | 42934.25 | 55 | 55
2017-07-18 06:30 | 49 | 49 |  |  | 42934.2708 | 67 | 66
2017-07-18 07:00 | 54 | 54 |  |  | 42934.2917 | 77 | 76
2017-07-18 07:30 | 62 | 61 |  |  | 42934.3125 | 87 | 85
2017-07-18 08:00 | 64 | 64 |  |  | 42934.3333 | 89 | 88
2017-07-18 08:30 | 60 | 60 |  |  | 42934.3542 | 88 | 87
2017-07-18 09:00 | 57 | 56 |  |  | 42934.375 | 85 | 83
2017-07-18 09:30 | 53 | 53 |  |  | 42934.3958 | 81 | 80
2017-07-18 10:00 | 52 | 52 |  |  | 42934.4167 | 78 | 77
2017-07-18 10:30 | 52 | 52 |  |  | 42934.4375 | 76 | 74
2017-07-18 11:00 | 51 | 51 |  |  | 42934.4583 | 74 | 73
2017-07-18 11:30 | 51 | 51 |  |  | 42934.4792 | 74 | 72
2017-07-18 12:00 | 50 | 50 |  |  | 42934.5 | 73 | 72
2017-07-18 12:30 | 50 | 50 |  |  | 42934.5208 | 75 | 74
2017-07-18 13:00 | 51 | 51 |  |  | 42934.5417 | 75 | 74
2017-07-18 13:30 | 55 | 55 |  |  | 42934.5625 | 77 | 76
2017-07-18 14:00 | 57 | 57 |  |  | 42934.5833 | 80 | 79
2017-07-18 14:30 | 58 | 58 |  |  | 42934.6042 | 81 | 80
2017-07-18 15:00 | 59 | 59 |  |  | 42934.625 | 83 | 82
2017-07-18 15:30 | 59 | 59 |  |  | 42934.6458 | 83 | 82
2017-07-18 16:00 | 60 | 60 |  |  | 42934.6667 | 85 | 84
2017-07-18 16:30 | 63 | 63 |  |  | 42934.6875 | 87 | 86
2017-07-18 17:00 | 64 | 64 |  |  | 42934.7083 | 89 | 86
2017-07-18 17:30 | 66 | 66 |  |  | 42934.7292 | 91 | 87
2017-07-18 18:00 | 69 | 68 |  |  | 42934.75 | 93 | 88
2017-07-18 18:30 | 69 | 68 |  |  | 42934.7708 | 91 | 86
2017-07-18 19:00 | 70 | 69 |  |  | 42934.7917 | 92 | 87
2017-07-18 19:30 | 69 | 68 |  |  | 42934.8125 | 89 | 86
2017-07-18 20:00 | 67 | 66 |  |  | 42934.8333 | 88 | 84
2017-07-18 20:30 | 66 | 66 |  |  | 42934.8542 | 87 | 84
2017-07-18 21:00 | 62 | 62 |  |  | 42934.875 | 82 | 79
2017-07-18 21:30 | 58 | 57 |  |  | 42934.8958 | 76 | 74
2017-07-18 22:00 | 56 | 56 |  |  | 42934.9167 | 75 | 73
2017-07-18 22:30 | 54 | 53 |  |  | 42934.9375 | 72 | 70
2017-07-18 23:00 | 51 | 51 |  |  | 42934.9583 | 69 | 67
2017-07-18 23:30 | 46 | 45 |  |  | 42934.9792 | 62 | 61
2017-07-19 | 41 | 40 |  |  | 42935 | 56 | 56
2017-07-19 00:30 | 37 | 37 |  |  | 42935.0208 | 50 | 49
2017-07-19 01:00 | 35 | 34 |  |  | 42935.0417 | 46 | 45
2017-07-19 01:30 | 32 | 32 |  |  | 42935.0625 | 43 | 42
2017-07-19 02:00 | 30 | 29 |  |  | 42935.0833 | 42 | 41
2017-07-19 02:30 | 30 | 29 |  |  | 42935.1042 | 41 | 41
2017-07-19 03:00 | 32 | 31 |  |  | 42935.125 | 42 | 41
2017-07-19 03:30 | 34 | 33 |  |  | 42935.1458 | 45 | 43
2017-07-19 04:00 | 35 | 35 |  |  | 42935.1667 | 46 | 45
2017-07-19 04:30 | 36 | 36 |  |  | 42935.1875 | 48 | 46
2017-07-19 05:00 | 38 | 38 |  |  | 42935.2083 | 50 | 49
2017-07-19 05:30 | 38 | 38 |  |  | 42935.2292 | 51 | 50
2017-07-19 06:00 | 44 | 42 |  |  | 42935.25 | 56 | 56
2017-07-19 06:30 | 70 | 52 |  |  | 42935.2708 | 73 | 70
2017-07-19 07:00 | 78 | 58 |  |  | 42935.2917 | 84 | 79
2017-07-19 07:30 | 85 | 66 |  |  | 42935.3125 | 93 | 89
2017-07-19 08:00 | 77 | 65 |  |  | 42935.3333 | 91 | 91
2017-07-19 08:30 | 68 | 61 |  |  | 42935.3542 | 88 | 88
2017-07-19 09:00 | 66 | 58 |  |  | 42935.375 | 84 | 84
2017-07-19 09:30 | 64 | 56 |  |  | 42935.3958 | 81 | 81
2017-07-19 10:00 | 63 | 52 |  |  | 42935.4167 | 77 | 76
2017-07-19 10:30 | 65 | 49 |  |  | 42935.4375 | 76 | 71
2017-07-19 11:00 | 65 | 48 |  |  | 42935.4583 | 75 | 69
2017-07-19 11:30 | 64 | 47 |  |  | 42935.4792 | 73 | 67
2017-07-19 12:00 | 63 | 46 |  |  | 42935.5 | 74 | 68
2017-07-19 12:30 | 64 | 46 |  |  | 42935.5208 | 73 | 68
2017-07-19 13:00 | 64 | 46 |  |  | 42935.5417 | 73 | 67
2017-07-19 13:30 | 64 | 46 |  |  | 42935.5625 | 74 | 68
2017-07-19 14:00 | 67 | 50 |  |  | 42935.5833 | 77 | 71
2017-07-19 14:30 | 71 | 54 |  |  | 42935.6042 | 80 | 75
2017-07-19 15:00 | 71 | 56 |  |  | 42935.625 | 83 | 78
2017-07-19 15:30 | 72 | 57 |  |  | 42935.6458 | 83 | 79
2017-07-19 16:00 | 75 | 61 |  |  | 42935.6667 | 87 | 83
2017-07-19 16:30 | 75 | 64 |  |  | 42935.6875 | 88 | 86
2017-07-19 17:00 | 77 | 68 |  |  | 42935.7083 | 91 | 90
2017-07-19 17:30 | 79 | 71 |  |  | 42935.7292 | 93 | 92
2017-07-19 18:00 | 83 | 75 |  |  | 42935.75 | 96 | 94
2017-07-19 18:30 | 80 | 74 |  |  | 42935.7708 | 94 | 94
2017-07-19 19:00 | 83 | 77 |  |  | 42935.7917 | 96 | 96
2017-07-19 19:30 | 82 | 76 |  |  | 42935.8125 | 95 | 95
2017-07-19 20:00 | 81 | 75 |  |  | 42935.8333 | 93 | 93
2017-07-19 20:30 | 81 | 74 |  |  | 42935.8542 | 93 | 93
2017-07-19 21:00 | 80 | 73 |  |  | 42935.875 | 89 | 89
2017-07-19 21:30 | 78 | 70 |  |  | 42935.8958 | 86 | 85
2017-07-19 22:00 | 75 | 65 |  |  | 42935.9167 | 83 | 83
2017-07-19 22:30 | 75 | 61 |  |  | 42935.9375 | 83 | 80
2017-07-19 23:00 | 73 | 60 |  |  | 42935.9583 | 80 | 77
2017-07-19 23:30 | 71 | 56 |  |  | 42935.9792 | 76 | 73
2017-07-20 | 66 | 51 |  |  | 42936 | 70 | 66
2017-07-20 00:30 | 59 | 42 |  |  | 42936.0208 | 62 | 58
2017-07-20 01:00 | 56 | 38 |  |  | 42936.0417 | 56 | 52
2017-07-20 01:30 | 55 | 38 |  |  | 42936.0625 | 55 | 51
2017-07-20 02:00 | 52 | 35 |  |  | 42936.0833 | 53 | 48
2017-07-20 02:30 | 51 | 35 |  |  | 42936.1042 | 51 | 47
2017-07-20 03:00 | 51 | 34 |  |  | 42936.125 | 50 | 46
2017-07-20 03:30 | 51 | 34 |  |  | 42936.1458 | 48 | 44
2017-07-20 04:00 | 51 | 34 |  |  | 42936.1667 | 49 | 45
2017-07-20 04:30 | 53 | 37 |  |  | 42936.1875 | 52 | 48
2017-07-20 05:00 | 55 | 39 |  |  | 42936.2083 | 56 | 52
2017-07-20 05:30 | 60 | 45 |  |  | 42936.2292 | 61 | 57
2017-07-20 06:00 | 67 | 52 |  |  | 42936.25 | 70 | 66
2017-07-20 06:30 | 73 | 58 |  |  | 42936.2708 | 81 | 77
2017-07-20 07:00 | 81 | 65 |  |  | 42936.2917 | 91 | 86
2017-07-20 07:30 | 89 | 73 |  |  | 42936.3125 | 103 | 97
2017-07-20 08:00 | 91 | 75 |  |  | 42936.3333 | 98 | 92
2017-07-20 08:30 | 90 | 73 |  |  | 42936.3542 | 96 | 91
2017-07-20 09:00 | 85 | 68 |  |  | 42936.375 | 90 | 85
2017-07-20 09:30 | 81 | 64 |  |  | 42936.3958 | 85 | 79
2017-07-20 10:00 | 79 | 60 |  |  | 42936.4167 | 81 | 75
2017-07-20 10:30 | 76 | 56 |  |  | 42936.4375 | 75 | 69
2017-07-20 11:00 | 75 | 54 |  |  | 42936.4583 | 74 | 67
2017-07-20 11:30 | 75 | 54 |  |  | 42936.4792 | 73 | 66
2017-07-20 12:00 | 74 | 54 |  |  | 42936.5 | 72 | 65
2017-07-20 12:30 | 74 | 53 |  |  | 42936.5208 | 72 | 65
2017-07-20 13:00 | 74 | 53 |  |  | 42936.5417 | 71 | 64
2017-07-20 13:30 | 76 | 54 |  |  | 42936.5625 | 73 | 65
2017-07-20 14:00 | 75 | 54 |  |  | 42936.5833 | 67 | 62
2017-07-20 14:30 | 75 | 55 |  |  | 42936.6042 | 67 | 62
2017-07-20 15:00 | 74 | 54 |  |  | 42936.625 | 67 | 62
2017-07-20 15:30 | 71 | 52 |  |  | 42936.6458 | 73 | 68
2017-07-20 16:00 | 70 | 51 |  |  | 42936.6667 | 75 | 70
2017-07-20 16:30 | 73 | 56 |  |  | 42936.6875 | 80 | 76
2017-07-20 17:00 | 75 | 60 |  |  | 42936.7083 | 84 | 81
2017-07-20 17:30 | 78 | 65 |  |  | 42936.7292 | 87 | 85
2017-07-20 18:00 | 83 | 71 |  |  | 42936.75 | 92 | 90
2017-07-20 18:30 | 82 | 72 |  |  | 42936.7708 | 91 | 89
2017-07-20 19:00 | 83 | 73 |  |  | 42936.7917 | 93 | 92
2017-07-20 19:30 | 82 | 72 |  |  | 42936.8125 | 91 | 90
2017-07-20 20:00 | 79 | 70 |  |  | 42936.8333 | 89 | 87
2017-07-20 20:30 | 79 | 70 |  |  | 42936.8542 | 89 | 88
2017-07-20 21:00 | 78 | 67 |  |  | 42936.875 | 86 | 84
2017-07-20 21:30 | 74 | 62 |  |  | 42936.8958 | 80 | 78
2017-07-20 22:00 | 72 | 58 |  |  | 42936.9167 | 80 | 77
2017-07-20 22:30 | 70 | 56 |  |  | 42936.9375 | 78 | 75
2017-07-20 23:00 | 67 | 55 |  |  | 42936.9583 | 75 | 72
2017-07-20 23:30 | 61 | 50 |  |  | 42936.9792 | 68 | 66
2017-07-21 | 58 | 46 |  |  | 42937 | 61 | 59
2017-07-21 00:30 | 52 | 39 |  |  | 42937.0208 | 53 | 51
2017-07-21 01:00 | 48 | 34 |  |  | 42937.0417 | 49 | 46
2017-07-21 01:30 | 50 | 35 |  |  | 42937.0625 | 49 | 46
2017-07-21 02:00 | 49 | 35 |  |  | 42937.0833 | 50 | 47
2017-07-21 02:30 | 47 | 34 |  |  | 42937.1042 | 48 | 46
2017-07-21 03:00 | 46 | 32 |  |  | 42937.125 | 47 | 44
2017-07-21 03:30 | 46 | 32 |  |  | 42937.1458 | 46 | 44
2017-07-21 04:00 | 46 | 32 |  |  | 42937.1667 | 46 | 44
2017-07-21 04:30 | 50 | 36 |  |  | 42937.1875 | 49 | 47
2017-07-21 05:00 | 54 | 40 |  |  | 42937.2083 | 54 | 52
2017-07-21 05:30 | 61 | 48 |  |  | 42937.2292 | 61 | 58
2017-07-21 06:00 | 66 | 52 |  |  | 42937.25 | 68 | 65
2017-07-21 06:30 | 77 | 62 |  |  | 42937.2708 | 81 | 78
2017-07-21 07:00 | 82 | 71 |  |  | 42937.2917 | 93 | 92
2017-07-21 07:30 | 86 | 78 |  |  | 42937.3125 | 102 | 101
2017-07-21 08:00 | 84 | 76 |  |  | 42937.3333 | 102 | 100
2017-07-21 08:30 | 79 | 70 |  |  | 42937.3542 | 97 | 95
2017-07-21 09:00 | 74 | 64 |  |  | 42937.375 | 91 | 89
2017-07-21 09:30 | 71 | 58 |  |  | 42937.3958 | 85 | 82
2017-07-21 10:00 | 72 | 56 |  |  | 42937.4167 | 84 | 80
2017-07-21 10:30 | 69 | 53 |  |  | 42937.4375 | 80 | 75
2017-07-21 11:00 | 68 | 50 |  |  | 42937.4583 | 78 | 72
2017-07-21 11:30 | 70 | 50 |  |  | 42937.4792 | 80 | 71
2017-07-21 12:00 | 70 | 49 |  |  | 42937.5 | 79 | 71
2017-07-21 12:30 | 70 | 49 |  |  | 42937.5208 | 79 | 71
2017-07-21 13:00 | 70 | 49 |  |  | 42937.5417 | 79 | 70
2017-07-21 13:30 | 69 | 48 |  |  | 42937.5625 | 77 | 70
2017-07-21 14:00 | 68 | 47 |  |  | 42937.5833 | 76 | 69
2017-07-21 14:30 | 69 | 48 |  |  | 42937.6042 | 76 | 69
2017-07-21 15:00 | 69 | 50 |  |  | 42937.625 | 77 | 71
2017-07-21 15:30 | 71 | 53 |  |  | 42937.6458 | 80 | 74
2017-07-21 16:00 | 73 | 56 |  |  | 42937.6667 | 83 | 79
2017-07-21 16:30 | 74 | 59 |  |  | 42937.6875 | 86 | 82
2017-07-21 17:00 | 78 | 66 |  |  | 42937.7083 | 90 | 88
2017-07-21 17:30 | 78 | 69 |  |  | 42937.7292 | 91 | 89
2017-07-21 18:00 | 80 | 71 |  |  | 42937.75 | 93 | 92
2017-07-21 18:30 | 80 | 72 |  |  | 42937.7708 | 93 | 92
2017-07-21 19:00 | 81 | 73 |  |  | 42937.7917 | 94 | 93
2017-07-21 19:30 | 81 | 73 |  |  | 42937.8125 | 93 | 92
2017-07-21 20:00 | 79 | 71 |  |  | 42937.8333 | 90 | 89
2017-07-21 20:30 | 79 | 70 |  |  | 42937.8542 | 89 | 88
2017-07-21 21:00 | 77 | 68 |  |  | 42937.875 | 87 | 85
2017-07-21 21:30 | 77 | 66 |  |  | 42937.8958 | 83 | 82
2017-07-21 22:00 | 75 | 64 |  |  | 42937.9167 | 82 | 80
2017-07-21 22:30 | 73 | 62 |  |  | 42937.9375 | 81 | 79
2017-07-21 23:00 | 68 | 56 |  |  | 42937.9583 | 75 | 73
2017-07-21 23:30 | 66 | 52 |  |  | 42937.9792 | 72 | 70
2017-07-22 | 63 | 49 |  |  | 42938 | 68 | 66
2017-07-22 00:30 | 57 | 45 |  |  | 42938.0208 | 62 | 59
2017-07-22 01:00 | 54 | 42 |  |  | 42938.0417 | 58 | 55
2017-07-22 01:30 | 54 | 41 |  |  | 42938.0625 | 57 | 54
2017-07-22 02:00 | 51 | 39 |  |  | 42938.0833 | 56 | 54
2017-07-22 02:30 | 51 | 39 |  |  | 42938.1042 | 55 | 53
2017-07-22 03:00 | 49 | 37 |  |  | 42938.125 | 52 | 50
2017-07-22 03:30 | 49 | 36 |  |  | 42938.1458 | 50 | 47
2017-07-22 04:00 | 40 | 34 |  |  | 42938.1667 | 47 | 46
2017-07-22 04:30 | 41 | 36 |  |  | 42938.1875 | 49 | 48
2017-07-22 05:00 | 42 | 38 |  |  | 42938.2083 | 50 | 49
2017-07-22 05:30 | 44 | 39 |  |  | 42938.2292 | 53 | 52
2017-07-22 06:00 | 46 | 41 |  |  | 42938.25 | 56 | 55
2017-07-22 06:30 | 50 | 44 |  |  | 42938.2708 | 61 | 60
2017-07-22 07:00 | 52 | 47 |  |  | 42938.2917 | 65 | 64
2017-07-22 07:30 | 55 | 50 |  |  | 42938.3125 | 69 | 68
2017-07-22 08:00 | 52 | 51 |  |  | 42938.3333 | 71 | 70
2017-07-22 08:30 | 53 | 52 |  |  | 42938.3542 | 73 | 72
2017-07-22 09:00 | 54 | 53 |  |  | 42938.375 | 74 | 73
2017-07-22 09:30 | 52 | 50 |  |  | 42938.3958 | 71 | 70
2017-07-22 10:00 | 50 | 48 |  |  | 42938.4167 | 68 | 67
2017-07-22 10:30 | 45 | 43 |  |  | 42938.4375 | 61 | 60
2017-07-22 11:00 | 43 | 40 |  |  | 42938.4583 | 57 | 57
2017-07-22 11:30 | 46 | 39 |  |  | 42938.4792 | 55 | 53
2017-07-22 12:00 | 45 | 38 |  |  | 42938.5 | 54 | 51
2017-07-22 12:30 | 45 | 38 |  |  | 42938.5208 | 53 | 51
2017-07-22 13:00 | 44 | 37 |  |  | 42938.5417 | 53 | 51
2017-07-22 13:30 | 45 | 38 |  |  | 42938.5625 | 53 | 51
2017-07-22 14:00 | 45 | 38 |  |  | 42938.5833 | 52 | 51
2017-07-22 14:30 | 46 | 40 |  |  | 42938.6042 | 54 | 53
2017-07-22 15:00 | 47 | 40 |  |  | 42938.625 | 56 | 54
2017-07-22 15:30 | 47 | 41 |  |  | 42938.6458 | 57 | 56
2017-07-22 16:00 | 49 | 43 |  |  | 42938.6667 | 59 | 58
2017-07-22 16:30 | 53 | 47 |  |  | 42938.6875 | 65 | 63
2017-07-22 17:00 | 58 | 54 |  |  | 42938.7083 | 72 | 71
2017-07-22 17:30 | 61 | 58 |  |  | 42938.7292 | 75 | 75
2017-07-22 18:00 | 65 | 62 |  |  | 42938.75 | 80 | 79
2017-07-22 18:30 | 67 | 64 |  |  | 42938.7708 | 82 | 82
2017-07-22 19:00 | 68 | 65 |  |  | 42938.7917 | 83 | 83
2017-07-22 19:30 | 68 | 64 |  |  | 42938.8125 | 83 | 82
2017-07-22 20:00 | 69 | 64 |  |  | 42938.8333 | 83 | 82
2017-07-22 20:30 | 70 | 65 |  |  | 42938.8542 | 84 | 82
2017-07-22 21:00 | 69 | 64 |  |  | 42938.875 | 81 | 80
2017-07-22 21:30 | 68 | 62 |  |  | 42938.8958 | 79 | 78
2017-07-22 22:00 | 68 | 62 |  |  | 42938.9167 | 79 | 77
2017-07-22 22:30 | 59 | 57 |  |  | 42938.9375 | 74 | 73
2017-07-22 23:00 | 55 | 53 |  |  | 42938.9583 | 69 | 68
2017-07-22 23:30 | 51 | 48 |  |  | 42938.9792 | 65 | 64
2017-07-23 | 47 | 44 |  |  | 42939 | 60 | 60
2017-07-23 00:30 | 44 | 41 |  |  | 42939.0208 | 56 | 55
2017-07-23 01:00 | 39 | 36 |  |  | 42939.0417 | 50 | 50
2017-07-23 01:30 | 38 | 34 |  |  | 42939.0625 | 48 | 47
2017-07-23 02:00 | 36 | 32 |  |  | 42939.0833 | 47 | 46
2017-07-23 02:30 | 35 | 31 |  |  | 42939.1042 | 45 | 44
2017-07-23 03:00 | 34 | 30 |  |  | 42939.125 | 45 | 43
2017-07-23 03:30 | 35 | 31 |  |  | 42939.1458 | 45 | 44
2017-07-23 04:00 | 35 | 31 |  |  | 42939.1667 | 44 | 43
2017-07-23 04:30 | 35 | 31 |  |  | 42939.1875 | 46 | 45
2017-07-23 05:00 | 35 | 32 |  |  | 42939.2083 | 46 | 45
2017-07-23 05:30 | 35 | 31 |  |  | 42939.2292 | 45 | 44
2017-07-23 06:00 | 39 | 35 |  |  | 42939.25 | 49 | 47
2017-07-23 06:30 | 37 | 33 |  |  | 42939.2708 | 49 | 48
2017-07-23 07:00 | 36 | 32 |  |  | 42939.2917 | 49 | 48
2017-07-23 07:30 | 39 | 35 |  |  | 42939.3125 | 54 | 53
2017-07-23 08:00 | 43 | 39 |  |  | 42939.3333 | 58 | 57
2017-07-23 08:30 | 45 | 40 |  |  | 42939.3542 | 59 | 57
2017-07-23 09:00 | 45 | 40 |  |  | 42939.375 | 60 | 58
2017-07-23 09:30 | 45 | 40 |  |  | 42939.3958 | 60 | 58
2017-07-23 10:00 | 43 | 38 |  |  | 42939.4167 | 57 | 55
2017-07-23 10:30 | 42 | 37 |  |  | 42939.4375 | 55 | 53
2017-07-23 11:00 | 40 | 35 |  |  | 42939.4583 | 54 | 51
2017-07-23 11:30 | 41 | 36 |  |  | 42939.4792 | 53 | 51
2017-07-23 12:00 | 41 | 36 |  |  | 42939.5 | 53 | 51
2017-07-23 12:30 | 40 | 36 |  |  | 42939.5208 | 52 | 50
2017-07-23 13:00 | 40 | 36 |  |  | 42939.5417 | 53 | 50
2017-07-23 13:30 | 41 | 36 |  |  | 42939.5625 | 53 | 51
2017-07-23 14:00 | 42 | 37 |  |  | 42939.5833 | 53 | 51
2017-07-23 14:30 | 43 | 39 |  |  | 42939.6042 | 54 | 52
2017-07-23 15:00 | 43 | 38 |  |  | 42939.625 | 54 | 52
2017-07-23 15:30 | 45 | 40 |  |  | 42939.6458 | 57 | 55
2017-07-23 16:00 | 48 | 43 |  |  | 42939.6667 | 61 | 59
2017-07-23 16:30 | 50 | 46 |  |  | 42939.6875 | 65 | 63
2017-07-23 17:00 | 55 | 51 |  |  | 42939.7083 | 71 | 69
2017-07-23 17:30 | 62 | 59 |  |  | 42939.7292 | 77 | 76
2017-07-23 18:00 | 67 | 66 |  |  | 42939.75 | 83 | 83
2017-07-23 18:30 | 70 | 69 |  |  | 42939.7708 | 85 | 85
2017-07-23 19:00 | 70 | 69 |  |  | 42939.7917 | 87 | 87
2017-07-23 19:30 | 68 | 67 |  |  | 42939.8125 | 86 | 86
2017-07-23 20:00 | 68 | 67 |  |  | 42939.8333 | 85 | 85
2017-07-23 20:30 | 68 | 67 |  |  | 42939.8542 | 86 | 85
2017-07-23 21:00 | 66 | 65 |  |  | 42939.875 | 83 | 82
2017-07-23 21:30 | 64 | 62 |  |  | 42939.8958 | 79 | 79
2017-07-23 22:00 | 61 | 59 |  |  | 42939.9167 | 77 | 77
2017-07-23 22:30 | 58 | 56 |  |  | 42939.9375 | 75 | 74
2017-07-23 23:00 | 56 | 53 |  |  | 42939.9583 | 72 | 71
2017-07-23 23:30 | 52 | 50 |  |  | 42939.9792 | 67 | 67
2017-07-24 | 49 | 46 |  |  | 42940 | 63 | 62
2017-07-24 00:30 | 45 | 43 |  |  | 42940.0208 | 58 | 57
2017-07-24 01:00 | 44 | 42 |  |  | 42940.0417 | 55 | 55
2017-07-24 01:30 | 42 | 40 |  |  | 42940.0625 | 54 | 53
2017-07-24 02:00 | 38 | 35 |  |  | 42940.0833 | 49 | 48
2017-07-24 02:30 | 37 | 34 |  |  | 42940.1042 | 47 | 46
2017-07-24 03:00 | 36 | 33 |  |  | 42940.125 | 47 | 46
2017-07-24 03:30 | 36 | 32 |  |  | 42940.1458 | 45 | 44
2017-07-24 04:00 | 37 | 33 |  |  | 42940.1667 | 46 | 45
2017-07-24 04:30 | 38 | 35 |  |  | 42940.1875 | 48 | 47
2017-07-24 05:00 | 41 | 38 |  |  | 42940.2083 | 51 | 50
2017-07-24 05:30 | 47 | 43 |  |  | 42940.2292 | 57 | 56
2017-07-24 06:00 | 56 | 52 |  |  | 42940.25 | 67 | 66
2017-07-24 06:30 | 66 | 62 |  |  | 42940.2708 | 82 | 80
2017-07-24 07:00 | 75 | 71 |  |  | 42940.2917 | 94 | 93
2017-07-24 07:30 | 86 | 83 |  |  | 42940.3125 | 108 | 108
2017-07-24 08:00 | 85 | 82 |  |  | 42940.3333 | 107 | 107
2017-07-24 08:30 | 79 | 76 |  |  | 42940.3542 | 104 | 103
2017-07-24 09:00 | 70 | 66 |  |  | 42940.375 | 94 | 93
2017-07-24 09:30 | 66 | 62 |  |  | 42940.3958 | 87 | 87
2017-07-24 10:00 | 63 | 59 |  |  | 42940.4167 | 82 | 82
2017-07-24 10:30 | 62 | 57 |  |  | 42940.4375 | 79 | 78
2017-07-24 11:00 | 61 | 56 |  |  | 42940.4583 | 78 | 77
2017-07-24 11:30 | 62 | 56 |  |  | 42940.4792 | 78 | 76
2017-07-24 12:00 | 59 | 53 |  |  | 42940.5 | 75 | 74
2017-07-24 12:30 | 57 | 51 |  |  | 42940.5208 | 74 | 73
2017-07-24 13:00 | 57 | 51 |  |  | 42940.5417 | 73 | 72
2017-07-24 13:30 | 59 | 53 |  |  | 42940.5625 | 74 | 73
2017-07-24 14:00 | 60 | 55 |  |  | 42940.5833 | 75 | 74
2017-07-24 14:30 | 61 | 55 |  |  | 42940.6042 | 76 | 75
2017-07-24 15:00 | 62 | 56 |  |  | 42940.625 | 78 | 78
2017-07-24 15:30 | 63 | 58 |  |  | 42940.6458 | 80 | 79
2017-07-24 16:00 | 65 | 61 |  |  | 42940.6667 | 83 | 82
2017-07-24 16:30 | 67 | 63 |  |  | 42940.6875 | 86 | 85
2017-07-24 17:00 | 70 | 67 |  |  | 42940.7083 | 89 | 89
2017-07-24 17:30 | 73 | 70 |  |  | 42940.7292 | 91 | 91
2017-07-24 18:00 | 78 | 76 |  |  | 42940.75 | 95 | 95
2017-07-24 18:30 | 79 | 77 |  |  | 42940.7708 | 96 | 96
2017-07-24 19:00 | 81 | 79 |  |  | 42940.7917 | 98 | 98
2017-07-24 19:30 | 79 | 77 |  |  | 42940.8125 | 96 | 96
2017-07-24 20:00 | 78 | 77 |  |  | 42940.8333 | 95 | 95
2017-07-24 20:30 | 78 | 76 |  |  | 42940.8542 | 94 | 94
2017-07-24 21:00 | 77 | 74 |  |  | 42940.875 | 91 | 91
2017-07-24 21:30 | 74 | 69 |  |  | 42940.8958 | 86 | 85
2017-07-24 22:00 | 71 | 66 |  |  | 42940.9167 | 84 | 83
2017-07-24 22:30 | 69 | 64 |  |  | 42940.9375 | 82 | 81
2017-07-24 23:00 | 64 | 60 |  |  | 42940.9583 | 78 | 77
2017-07-24 23:30 | 58 | 53 |  |  | 42940.9792 | 73 | 72
2017-07-25 | 52 | 48 |  |  | 42941 | 66 | 65
2017-07-25 00:30 | 47 | 43 |  |  | 42941.0208 | 60 | 58
2017-07-25 01:00 | 44 | 40 |  |  | 42941.0417 | 55 | 54
2017-07-25 01:30 | 45 | 41 |  |  | 42941.0625 | 54 | 53
2017-07-25 02:00 | 45 | 42 |  |  | 42941.0833 | 55 | 54
2017-07-25 02:30 | 48 | 44 |  |  | 42941.1042 | 58 | 55
2017-07-25 03:00 | 46 | 42 |  |  | 42941.125 | 57 | 55
2017-07-25 03:30 | 46 | 43 |  |  | 42941.1458 | 58 | 55
2017-07-25 04:00 | 47 | 43 |  |  | 42941.1667 | 58 | 56
2017-07-25 04:30 | 49 | 45 |  |  | 42941.1875 | 59 | 57
2017-07-25 05:00 | 51 | 46 |  |  | 42941.2083 | 62 | 59
2017-07-25 05:30 | 55 | 51 |  |  | 42941.2292 | 66 | 64
2017-07-25 06:00 | 58 | 55 |  |  | 42941.25 | 71 | 69
2017-07-25 06:30 | 66 | 63 |  |  | 42941.2708 | 82 | 81
2017-07-25 07:00 | 76 | 72 |  |  | 42941.2917 | 96 | 95
2017-07-25 07:30 | 86 | 82 |  |  | 42941.3125 | 110 | 108
2017-07-25 08:00 | 84 | 82 |  |  | 42941.3333 | 109 | 109
2017-07-25 08:30 | 77 | 75 |  |  | 42941.3542 | 104 | 104
2017-07-25 09:00 | 68 | 66 |  |  | 42941.375 | 94 | 94
2017-07-25 09:30 | 62 | 59 |  |  | 42941.3958 | 86 | 86
2017-07-25 10:00 | 60 | 57 |  |  | 42941.4167 | 82 | 82
2017-07-25 10:30 | 58 | 54 |  |  | 42941.4375 | 78 | 78
2017-07-25 11:00 | 57 | 52 |  |  | 42941.4583 | 77 | 77
2017-07-25 11:30 | 58 | 53 |  |  | 42941.4792 | 76 | 75
2017-07-25 12:00 | 57 | 52 |  |  | 42941.5 | 76 | 75
2017-07-25 12:30 | 57 | 51 |  |  | 42941.5208 | 76 | 75
2017-07-25 13:00 | 60 | 51 |  |  | 42941.5417 | 76 | 73
2017-07-25 13:30 | 60 | 51 |  |  | 42941.5625 | 76 | 73
2017-07-25 14:00 | 60 | 52 |  |  | 42941.5833 | 77 | 74
2017-07-25 14:30 | 62 | 55 |  |  | 42941.6042 | 78 | 76
2017-07-25 15:00 | 62 | 56 |  |  | 42941.625 | 80 | 78
2017-07-25 15:30 | 64 | 57 |  |  | 42941.6458 | 82 | 79
2017-07-25 16:00 | 67 | 60 |  |  | 42941.6667 | 85 | 83
2017-07-25 16:30 | 68 | 63 |  |  | 42941.6875 | 88 | 86
2017-07-25 17:00 | 70 | 67 |  |  | 42941.7083 | 90 | 89
2017-07-25 17:30 | 73 | 69 |  |  | 42941.7292 | 91 | 91
2017-07-25 18:00 | 75 | 73 |  |  | 42941.75 | 94 | 93
2017-07-25 18:30 | 75 | 74 |  |  | 42941.7708 | 94 | 94
2017-07-25 19:00 | 78 | 76 |  |  | 42941.7917 | 96 | 96
2017-07-25 19:30 | 76 | 74 |  |  | 42941.8125 | 95 | 95
2017-07-25 20:00 | 73 | 72 |  |  | 42941.8333 | 92 | 92
2017-07-25 20:30 | 74 | 72 |  |  | 42941.8542 | 92 | 92
2017-07-25 21:00 | 73 | 71 |  |  | 42941.875 | 90 | 90
2017-07-25 21:30 | 68 | 65 |  |  | 42941.8958 | 83 | 83
2017-07-25 22:00 | 65 | 63 |  |  | 42941.9167 | 81 | 81
2017-07-25 22:30 | 64 | 61 |  |  | 42941.9375 | 80 | 80
2017-07-25 23:00 | 63 | 60 |  |  | 42941.9583 | 78 | 77
2017-07-25 23:30 | 57 | 54 |  |  | 42941.9792 | 71 | 71
2017-07-26 | 52 | 49 |  |  | 42942 | 65 | 65
2017-07-26 00:30 | 45 | 42 |  |  | 42942.0208 | 57 | 57
2017-07-26 01:00 | 42 | 39 |  |  | 42942.0417 | 53 | 52
2017-07-26 01:30 | 40 | 38 |  |  | 42942.0625 | 52 | 52
2017-07-26 02:00 | 40 | 38 |  |  | 42942.0833 | 51 | 51
2017-07-26 02:30 | 39 | 37 |  |  | 42942.1042 | 50 | 50
2017-07-26 03:00 | 39 | 37 |  |  | 42942.125 | 49 | 49
2017-07-26 03:30 | 40 | 38 |  |  | 42942.1458 | 49 | 48
2017-07-26 04:00 | 39 | 39 |  |  | 42942.1667 | 52 | 52
2017-07-26 04:30 | 43 | 43 |  |  | 42942.1875 | 54 | 54
2017-07-26 05:00 | 45 | 45 |  |  | 42942.2083 | 56 | 56
2017-07-26 05:30 | 49 | 49 |  |  | 42942.2292 | 60 | 60
2017-07-26 06:00 | 54 | 54 |  |  | 42942.25 | 69 | 69
2017-07-26 06:30 | 63 | 63 |  |  | 42942.2708 | 83 | 83
2017-07-26 07:00 | 71 | 71 |  |  | 42942.2917 | 98 | 95
2017-07-26 07:30 | 79 | 79 |  |  | 42942.3125 | 112 | 108
2017-07-26 08:00 | 78 | 78 |  |  | 42942.3333 | 113 | 109
2017-07-26 08:30 | 72 | 71 |  |  | 42942.3542 | 108 | 103
2017-07-26 09:00 | 68 | 65 |  |  | 42942.375 | 101 | 94
2017-07-26 09:30 | 65 | 62 |  |  | 42942.3958 | 96 | 89
2017-07-26 10:00 | 60 | 60 |  |  | 42942.4167 | 84 | 84
2017-07-26 10:30 | 56 | 56 |  |  | 42942.4375 | 78 | 78
2017-07-26 11:00 | 53 | 53 |  |  | 42942.4583 | 76 | 75
2017-07-26 11:30 | 51 | 51 |  |  | 42942.4792 | 73 | 72
2017-07-26 12:00 | 50 | 50 |  |  | 42942.5 | 73 | 72
2017-07-26 12:30 | 50 | 50 |  |  | 42942.5208 | 72 | 72
2017-07-26 13:00 | 52 | 52 |  |  | 42942.5417 | 74 | 73
2017-07-26 13:30 | 54 | 54 |  |  | 42942.5625 | 78 | 77
2017-07-26 14:00 | 55 | 55 |  |  | 42942.5833 | 78 | 78
2017-07-26 14:30 | 56 | 56 |  |  | 42942.6042 | 79 | 79
2017-07-26 15:00 | 57 | 57 |  |  | 42942.625 | 80 | 80
2017-07-26 15:30 | 59 | 59 |  |  | 42942.6458 | 83 | 82
2017-07-26 16:00 | 61 | 61 |  |  | 42942.6667 | 83 | 83
2017-07-26 16:30 | 63 | 63 |  |  | 42942.6875 | 85 | 85
2017-07-26 17:00 | 63 | 63 |  |  | 42942.7083 | 85 | 85
2017-07-26 17:30 | 66 | 65 |  |  | 42942.7292 | 88 | 88
2017-07-26 18:00 | 69 | 69 |  |  | 42942.75 | 92 | 91
2017-07-26 18:30 | 73 | 71 |  |  | 42942.7708 | 102 | 93
2017-07-26 19:00 | 74 | 73 |  |  | 42942.7917 | 101 | 94
2017-07-26 19:30 | 71 | 70 |  |  | 42942.8125 | 100 | 92
2017-07-26 20:00 | 71 | 70 |  |  | 42942.8333 | 97 | 92
2017-07-26 20:30 | 69 | 68 |  |  | 42942.8542 | 95 | 89
2017-07-26 21:00 | 64 | 64 |  |  | 42942.875 | 83 | 83
2017-07-26 21:30 | 60 | 59 |  |  | 42942.8958 | 79 | 78
2017-07-26 22:00 | 60 | 59 |  |  | 42942.9167 | 79 | 78
2017-07-26 22:30 | 59 | 57 |  |  | 42942.9375 | 78 | 76
2017-07-26 23:00 | 57 | 54 |  |  | 42942.9583 | 73 | 71
2017-07-26 23:30 | 51 | 47 |  |  | 42942.9792 | 67 | 65
2017-07-27 | 48 | 45 |  |  | 42943 | 64 | 62
2017-07-27 00:30 | 44 | 41 |  |  | 42943.0208 | 58 | 56
2017-07-27 01:00 | 42 | 40 |  |  | 42943.0417 | 54 | 53
2017-07-27 01:30 | 39 | 39 |  |  | 42943.0625 | 52 | 51
2017-07-27 02:00 | 38 | 38 |  |  | 42943.0833 | 51 | 51
2017-07-27 02:30 | 37 | 37 |  |  | 42943.1042 | 50 | 50
2017-07-27 03:00 | 36 | 36 |  |  | 42943.125 | 51 | 50
2017-07-27 03:30 | 37 | 36 |  |  | 42943.1458 | 50 | 49
2017-07-27 04:00 | 37 | 36 |  |  | 42943.1667 | 51 | 50
2017-07-27 04:30 | 38 | 38 |  |  | 42943.1875 | 51 | 50
2017-07-27 05:00 | 40 | 40 |  |  | 42943.2083 | 54 | 53
2017-07-27 05:30 | 44 | 42 |  |  | 42943.2292 | 58 | 57
2017-07-27 06:00 | 50 | 48 |  |  | 42943.25 | 64 | 63
2017-07-27 06:30 | 55 | 55 |  |  | 42943.2708 | 74 | 74
2017-07-27 07:00 | 65 | 65 |  |  | 42943.2917 | 87 | 87
2017-07-27 07:30 | 71 | 71 |  |  | 42943.3125 | 99 | 97
2017-07-27 08:00 | 65 | 65 |  |  | 42943.3333 | 95 | 93
2017-07-27 08:30 | 58 | 58 |  |  | 42943.3542 | 90 | 88
2017-07-27 09:00 | 53 | 53 |  |  | 42943.375 | 85 | 83
2017-07-27 09:30 | 51 | 51 |  |  | 42943.3958 | 81 | 79
2017-07-27 10:00 | 49 | 49 |  |  | 42943.4167 | 77 | 76
2017-07-27 10:30 | 51 | 48 |  |  | 42943.4375 | 74 | 72
2017-07-27 11:00 | 50 | 47 |  |  | 42943.4583 | 73 | 71
2017-07-27 11:30 | 50 | 46 |  |  | 42943.4792 | 74 | 71
2017-07-27 12:00 | 49 | 46 |  |  | 42943.5 | 73 | 70
2017-07-27 12:30 | 48 | 44 |  |  | 42943.5208 | 71 | 68
2017-07-27 13:00 | 48 | 45 |  |  | 42943.5417 | 73 | 69
2017-07-27 13:30 | 50 | 45 |  |  | 42943.5625 | 74 | 70
2017-07-27 14:00 | 50 | 46 |  |  | 42943.5833 | 73 | 69
2017-07-27 14:30 | 53 | 49 |  |  | 42943.6042 | 75 | 71
2017-07-27 15:00 | 53 | 49 |  |  | 42943.625 | 76 | 73
2017-07-27 15:30 | 54 | 51 |  |  | 42943.6458 | 78 | 75
2017-07-27 16:00 | 57 | 54 |  |  | 42943.6667 | 81 | 78
2017-07-27 16:30 | 59 | 57 |  |  | 42943.6875 | 85 | 82
2017-07-27 17:00 | 63 | 61 |  |  | 42943.7083 | 88 | 85
2017-07-27 17:30 | 63 | 62 |  |  | 42943.7292 | 87 | 86
2017-07-27 18:00 | 68 | 67 |  |  | 42943.75 | 91 | 91
2017-07-27 18:30 | 68 | 68 |  |  | 42943.7708 | 91 | 91
2017-07-27 19:00 | 69 | 69 |  |  | 42943.7917 | 92 | 92
2017-07-27 19:30 | 67 | 67 |  |  | 42943.8125 | 91 | 90
2017-07-27 20:00 | 66 | 65 |  |  | 42943.8333 | 88 | 88
2017-07-27 20:30 | 65 | 65 |  |  | 42943.8542 | 87 | 87
2017-07-27 21:00 | 64 | 63 |  |  | 42943.875 | 84 | 84
2017-07-27 21:30 | 60 | 60 |  |  | 42943.8958 | 78 | 78
2017-07-27 22:00 | 58 | 57 |  |  | 42943.9167 | 80 | 79
2017-07-27 22:30 | 56 | 55 |  |  | 42943.9375 | 77 | 77
2017-07-27 23:00 | 57 | 57 |  |  | 42943.9583 | 73 | 73
2017-07-27 23:30 | 52 | 51 |  |  | 42943.9792 | 68 | 68
2017-07-28 | 50 | 49 |  |  | 42944 | 65 | 65
2017-07-28 00:30 | 46 | 45 |  |  | 42944.0208 | 61 | 60
2017-07-28 01:00 | 41 | 40 |  |  | 42944.0417 | 57 | 56
2017-07-28 01:30 | 40 | 40 |  |  | 42944.0625 | 55 | 53
2017-07-28 02:00 | 39 | 38 |  |  | 42944.0833 | 53 | 51
2017-07-28 02:30 | 39 | 38 |  |  | 42944.1042 | 53 | 51
2017-07-28 03:00 | 40 | 39 |  |  | 42944.125 | 53 | 51
2017-07-28 03:30 | 41 | 40 |  |  | 42944.1458 | 53 | 51
2017-07-28 04:00 | 41 | 40 |  |  | 42944.1667 | 52 | 50
2017-07-28 04:30 | 40 | 39 |  |  | 42944.1875 | 52 | 51
2017-07-28 05:00 | 41 | 39 |  |  | 42944.2083 | 54 | 52
2017-07-28 05:30 | 45 | 43 |  |  | 42944.2292 | 58 | 55
2017-07-28 06:00 | 51 | 50 |  |  | 42944.25 | 65 | 64
2017-07-28 06:30 | 59 | 58 |  |  | 42944.2708 | 77 | 76
2017-07-28 07:00 | 68 | 66 |  |  | 42944.2917 | 90 | 88
2017-07-28 07:30 | 76 | 75 |  |  | 42944.3125 | 100 | 99
2017-07-28 08:00 | 75 | 74 |  |  | 42944.3333 | 101 | 100
2017-07-28 08:30 | 69 | 68 |  |  | 42944.3542 | 95 | 94
2017-07-28 09:00 | 63 | 61 |  |  | 42944.375 | 88 | 86
2017-07-28 09:30 | 59 | 56 |  |  | 42944.3958 | 84 | 81
2017-07-28 10:00 | 56 | 53 |  |  | 42944.4167 | 81 | 77
2017-07-28 10:30 | 56 | 53 |  |  | 42944.4375 | 78 | 74
2017-07-28 11:00 | 56 | 53 |  |  | 42944.4583 | 78 | 75
2017-07-28 11:30 | 54 | 51 |  |  | 42944.4792 | 76 | 73
2017-07-28 12:00 | 54 | 51 |  |  | 42944.5 | 76 | 72
2017-07-28 12:30 | 52 | 49 |  |  | 42944.5208 | 74 | 70
2017-07-28 13:00 | 51 | 48 |  |  | 42944.5417 | 74 | 70
2017-07-28 13:30 | 54 | 50 |  |  | 42944.5625 | 75 | 71
2017-07-28 14:00 | 54 | 50 |  |  | 42944.5833 | 75 | 70
2017-07-28 14:30 | 53 | 49 |  |  | 42944.6042 | 75 | 71
2017-07-28 15:00 | 55 | 51 |  |  | 42944.625 | 78 | 74
2017-07-28 15:30 | 58 | 55 |  |  | 42944.6458 | 81 | 77
2017-07-28 16:00 | 62 | 59 |  |  | 42944.6667 | 84 | 81
2017-07-28 16:30 | 66 | 63 |  |  | 42944.6875 | 87 | 85
2017-07-28 17:00 | 67 | 65 |  |  | 42944.7083 | 89 | 87
2017-07-28 17:30 | 68 | 67 |  |  | 42944.7292 | 90 | 89
2017-07-28 18:00 | 69 | 68 |  |  | 42944.75 | 90 | 90
2017-07-28 18:30 | 66 | 66 |  |  | 42944.7708 | 86 | 86
2017-07-28 19:00 | 67 | 67 |  |  | 42944.7917 | 87 | 86
2017-07-28 19:30 | 65 | 65 |  |  | 42944.8125 | 84 | 84
2017-07-28 20:00 | 64 | 64 |  |  | 42944.8333 | 83 | 83
2017-07-28 20:30 | 65 | 64 |  |  | 42944.8542 | 82 | 82
2017-07-28 21:00 | 63 | 63 |  |  | 42944.875 | 79 | 79
2017-07-28 21:30 | 60 | 59 |  |  | 42944.8958 | 75 | 75
2017-07-28 22:00 | 57 | 57 |  |  | 42944.9167 | 74 | 74
2017-07-28 22:30 | 58 | 58 |  |  | 42944.9375 | 75 | 75
2017-07-28 23:00 | 59 | 58 |  |  | 42944.9583 | 73 | 73
2017-07-28 23:30 | 57 | 56 |  |  | 42944.9792 | 72 | 71
2017-07-29 | 51 | 50 |  |  | 42945 | 66 | 66
2017-07-29 00:30 | 48 | 47 |  |  | 42945.0208 | 60 | 60
2017-07-29 01:00 | 44 | 43 |  |  | 42945.0417 | 55 | 54
2017-07-29 01:30 | 40 | 38 |  |  | 42945.0625 | 50 | 49
2017-07-29 02:00 | 38 | 37 |  |  | 42945.0833 | 48 | 47
2017-07-29 02:30 | 37 | 36 |  |  | 42945.1042 | 47 | 46
2017-07-29 03:00 | 38 | 35 |  |  | 42945.125 | 46 | 45
2017-07-29 03:30 | 37 | 34 |  |  | 42945.1458 | 44 | 43
2017-07-29 04:00 | 36 | 34 |  |  | 42945.1667 | 45 | 44
2017-07-29 04:30 | 36 | 34 |  |  | 42945.1875 | 47 | 46
2017-07-29 05:00 | 37 | 35 |  |  | 42945.2083 | 47 | 46
2017-07-29 05:30 | 37 | 35 |  |  | 42945.2292 | 48 | 47
2017-07-29 06:00 | 38 | 35 |  |  | 42945.25 | 49 | 48
2017-07-29 06:30 | 39 | 37 |  |  | 42945.2708 | 52 | 51
2017-07-29 07:00 | 41 | 38 |  |  | 42945.2917 | 56 | 54
2017-07-29 07:30 | 44 | 42 |  |  | 42945.3125 | 60 | 58
2017-07-29 08:00 | 45 | 43 |  |  | 42945.3333 | 62 | 60
2017-07-29 08:30 | 42 | 41 |  |  | 42945.3542 | 59 | 59
2017-07-29 09:00 | 42 | 41 |  |  | 42945.375 | 58 | 58
2017-07-29 09:30 | 42 | 41 |  |  | 42945.3958 | 58 | 57
2017-07-29 10:00 | 40 | 39 |  |  | 42945.4167 | 55 | 55
2017-07-29 10:30 | 39 | 38 |  |  | 42945.4375 | 53 | 53
2017-07-29 11:00 | 38 | 37 |  |  | 42945.4583 | 52 | 52
2017-07-29 11:30 | 36 | 36 |  |  | 42945.4792 | 50 | 50
2017-07-29 12:00 | 35 | 35 |  |  | 42945.5 | 50 | 50
2017-07-29 12:30 | 34 | 34 |  |  | 42945.5208 | 48 | 48
2017-07-29 13:00 | 35 | 35 |  |  | 42945.5417 | 49 | 49
2017-07-29 13:30 | 35 | 35 |  |  | 42945.5625 | 50 | 50
2017-07-29 14:00 | 36 | 35 |  |  | 42945.5833 | 49 | 49
2017-07-29 14:30 | 36 | 35 |  |  | 42945.6042 | 49 | 49
2017-07-29 15:00 | 36 | 36 |  |  | 42945.625 | 50 | 50
2017-07-29 15:30 | 37 | 37 |  |  | 42945.6458 | 51 | 51
2017-07-29 16:00 | 39 | 39 |  |  | 42945.6667 | 55 | 55
2017-07-29 16:30 | 42 | 42 |  |  | 42945.6875 | 59 | 59
2017-07-29 17:00 | 48 | 48 |  |  | 42945.7083 | 66 | 66
2017-07-29 17:30 | 52 | 52 |  |  | 42945.7292 | 69 | 69
2017-07-29 18:00 | 54 | 54 |  |  | 42945.75 | 72 | 72
2017-07-29 18:30 | 58 | 58 |  |  | 42945.7708 | 75 | 75
2017-07-29 19:00 | 58 | 58 |  |  | 42945.7917 | 77 | 76
2017-07-29 19:30 | 58 | 58 |  |  | 42945.8125 | 74 | 74
2017-07-29 20:00 | 57 | 56 |  |  | 42945.8333 | 74 | 74
2017-07-29 20:30 | 56 | 56 |  |  | 42945.8542 | 73 | 73
2017-07-29 21:00 | 54 | 54 |  |  | 42945.875 | 71 | 70
2017-07-29 21:30 | 51 | 51 |  |  | 42945.8958 | 67 | 67
2017-07-29 22:00 | 50 | 48 |  |  | 42945.9167 | 66 | 65
2017-07-29 22:30 | 50 | 48 |  |  | 42945.9375 | 66 | 65
2017-07-29 23:00 | 50 | 47 |  |  | 42945.9583 | 63 | 62
2017-07-29 23:30 | 46 | 43 |  |  | 42945.9792 | 60 | 58
2017-07-30 | 43 | 39 |  |  | 42946 | 55 | 53
2017-07-30 00:30 | 39 | 35 |  |  | 42946.0208 | 49 | 47
2017-07-30 01:00 | 38 | 33 |  |  | 42946.0417 | 46 | 44
2017-07-30 01:30 | 37 | 33 |  |  | 42946.0625 | 46 | 45
2017-07-30 02:00 | 36 | 32 |  |  | 42946.0833 | 45 | 44
2017-07-30 02:30 | 36 | 32 |  |  | 42946.1042 | 44 | 43
2017-07-30 03:00 | 38 | 34 |  |  | 42946.125 | 46 | 44
2017-07-30 03:30 | 39 | 35 |  |  | 42946.1458 | 47 | 45
2017-07-30 04:00 | 39 | 35 |  |  | 42946.1667 | 46 | 45
2017-07-30 04:30 | 38 | 34 |  |  | 42946.1875 | 47 | 45
2017-07-30 05:00 | 39 | 34 |  |  | 42946.2083 | 47 | 45
2017-07-30 05:30 | 39 | 35 |  |  | 42946.2292 | 48 | 46
2017-07-30 06:00 | 39 | 35 |  |  | 42946.25 | 48 | 46
2017-07-30 06:30 | 37 | 34 |  |  | 42946.2708 | 48 | 46
2017-07-30 07:00 | 37 | 33 |  |  | 42946.2917 | 48 | 47
2017-07-30 07:30 | 38 | 34 |  |  | 42946.3125 | 51 | 50
2017-07-30 08:00 | 40 | 36 |  |  | 42946.3333 | 53 | 52
2017-07-30 08:30 | 41 | 37 |  |  | 42946.3542 | 55 | 54
2017-07-30 09:00 | 40 | 37 |  |  | 42946.375 | 55 | 54
2017-07-30 09:30 | 40 | 37 |  |  | 42946.3958 | 54 | 53
2017-07-30 10:00 | 38 | 35 |  |  | 42946.4167 | 52 | 51
2017-07-30 10:30 | 38 | 34 |  |  | 42946.4375 | 50 | 49
2017-07-30 11:00 | 37 | 34 |  |  | 42946.4583 | 48 | 47
2017-07-30 11:30 | 38 | 34 |  |  | 42946.4792 | 47 | 46
2017-07-30 12:00 | 37 | 34 |  |  | 42946.5 | 47 | 46
2017-07-30 12:30 | 37 | 33 |  |  | 42946.5208 | 47 | 46
2017-07-30 13:00 | 37 | 34 |  |  | 42946.5417 | 48 | 46
2017-07-30 13:30 | 37 | 34 |  |  | 42946.5625 | 48 | 47
2017-07-30 14:00 | 38 | 34 |  |  | 42946.5833 | 48 | 47
2017-07-30 14:30 | 38 | 34 |  |  | 42946.6042 | 48 | 46
2017-07-30 15:00 | 39 | 36 |  |  | 42946.625 | 50 | 49
2017-07-30 15:30 | 41 | 38 |  |  | 42946.6458 | 53 | 52
2017-07-30 16:00 | 42 | 39 |  |  | 42946.6667 | 55 | 54
2017-07-30 16:30 | 47 | 43 |  |  | 42946.6875 | 61 | 59
2017-07-30 17:00 | 55 | 50 |  |  | 42946.7083 | 66 | 65
2017-07-30 17:30 | 71 | 57 |  |  | 42946.7292 | 74 | 74
2017-07-30 18:00 | 75 | 63 |  |  | 42946.75 | 81 | 81
2017-07-30 18:30 | 77 | 65 |  |  | 42946.7708 | 83 | 83
2017-07-30 19:00 | 79 | 67 |  |  | 42946.7917 | 84 | 84
2017-07-30 19:30 | 77 | 64 |  |  | 42946.8125 | 82 | 82
2017-07-30 20:00 | 76 | 62 |  |  | 42946.8333 | 80 | 80
2017-07-30 20:30 | 76 | 62 |  |  | 42946.8542 | 79 | 79
2017-07-30 21:00 | 73 | 59 |  |  | 42946.875 | 77 | 77
2017-07-30 21:30 | 69 | 55 |  |  | 42946.8958 | 73 | 73
2017-07-30 22:00 | 67 | 52 |  |  | 42946.9167 | 73 | 73
2017-07-30 22:30 | 65 | 50 |  |  | 42946.9375 | 71 | 71
2017-07-30 23:00 | 63 | 47 |  |  | 42946.9583 | 67 | 67
2017-07-30 23:30 | 50 | 44 |  |  | 42946.9792 | 61 | 60
2017-07-31 | 46 | 41 |  |  | 42947 | 59 | 57
2017-07-31 00:30 | 44 | 39 |  |  | 42947.0208 | 56 | 53
2017-07-31 01:00 | 42 | 36 |  |  | 42947.0417 | 53 | 50
2017-07-31 01:30 | 39 | 32 |  |  | 42947.0625 | 50 | 46
2017-07-31 02:00 | 37 | 30 |  |  | 42947.0833 | 47 | 43
2017-07-31 02:30 | 37 | 30 |  |  | 42947.1042 | 47 | 43
2017-07-31 03:00 | 37 | 30 |  |  | 42947.125 | 46 | 42
2017-07-31 03:30 | 37 | 29 |  |  | 42947.1458 | 45 | 40
2017-07-31 04:00 | 36 | 29 |  |  | 42947.1667 | 45 | 40
2017-07-31 04:30 | 37 | 31 |  |  | 42947.1875 | 47 | 43
2017-07-31 05:00 | 39 | 35 |  |  | 42947.2083 | 51 | 47
2017-07-31 05:30 | 43 | 40 |  |  | 42947.2292 | 55 | 53
2017-07-31 06:00 | 48 | 46 |  |  | 42947.25 | 62 | 60
2017-07-31 06:30 | 56 | 55 |  |  | 42947.2708 | 74 | 73
2017-07-31 07:00 | 63 | 62 |  |  | 42947.2917 | 85 | 84
2017-07-31 07:30 | 71 | 70 |  |  | 42947.3125 | 96 | 96
2017-07-31 08:00 | 71 | 71 |  |  | 42947.3333 | 97 | 97
2017-07-31 08:30 | 67 | 66 |  |  | 42947.3542 | 94 | 94
2017-07-31 09:00 | 62 | 62 |  |  | 42947.375 | 90 | 89
2017-07-31 09:30 | 58 | 58 |  |  | 42947.3958 | 83 | 82
2017-07-31 10:00 | 56 | 56 |  |  | 42947.4167 | 79 | 79
2017-07-31 10:30 | 54 | 53 |  |  | 42947.4375 | 75 | 75
2017-07-31 11:00 | 52 | 52 |  |  | 42947.4583 | 73 | 73
2017-07-31 11:30 | 51 | 51 |  |  | 42947.4792 | 72 | 71
2017-07-31 12:00 | 51 | 51 |  |  | 42947.5 | 72 | 71
2017-07-31 12:30 | 52 | 52 |  |  | 42947.5208 | 73 | 73
2017-07-31 13:00 | 52 | 52 |  |  | 42947.5417 | 73 | 73
2017-07-31 13:30 | 53 | 53 |  |  | 42947.5625 | 74 | 74
2017-07-31 14:00 | 53 | 53 |  |  | 42947.5833 | 72 | 72
2017-07-31 14:30 | 54 | 54 |  |  | 42947.6042 | 74 | 74
2017-07-31 15:00 | 53 | 53 |  |  | 42947.625 | 75 | 75
2017-07-31 15:30 | 54 | 54 |  |  | 42947.6458 | 74 | 74
2017-07-31 16:00 | 58 | 56 |  |  | 42947.6667 | 80 | 76
2017-07-31 16:30 | 62 | 58 |  |  | 42947.6875 | 86 | 79
2017-07-31 17:00 | 69 | 64 |  |  | 42947.7083 | 92 | 84
2017-07-31 17:30 | 70 | 66 |  |  | 42947.7292 | 93 | 85
2017-07-31 18:00 | 72 | 68 |  |  | 42947.75 | 94 | 86
2017-07-31 18:30 | 71 | 67 |  |  | 42947.7708 | 94 | 85
2017-07-31 19:00 | 73 | 69 |  |  | 42947.7917 | 96 | 86
2017-07-31 19:30 | 70 | 67 |  |  | 42947.8125 | 92 | 84
2017-07-31 20:00 | 70 | 66 |  |  | 42947.8333 | 91 | 83
2017-07-31 20:30 | 70 | 66 |  |  | 42947.8542 | 91 | 83
2017-07-31 21:00 | 68 | 63 |  |  | 42947.875 | 87 | 78
2017-07-31 21:30 | 67 | 61 |  |  | 42947.8958 | 84 | 74
2017-07-31 22:00 | 63 | 56 |  |  | 42947.9167 | 82 | 72
2017-07-31 22:30 | 60 | 52 |  |  | 42947.9375 | 78 | 67
2017-07-31 23:00 | 55 | 47 |  |  | 42947.9583 | 73 | 61
2017-07-31 23:30 | 52 | 43 |  |  | 42947.9792 | 69 | 57
2017-08-01 | 51 | 41 |  |  | 42948 | 67 | 55
2017-08-01 00:30 | 42 | 37 |  |  | 42948.0208 | 53 | 49
2017-08-01 01:00 | 39 | 35 |  |  | 42948.0417 | 48 | 45
2017-08-01 01:30 | 38 | 32 |  |  | 42948.0625 | 47 | 43
2017-08-01 02:00 | 37 | 31 |  |  | 42948.0833 | 46 | 42
2017-08-01 02:30 | 38 | 32 |  |  | 42948.1042 | 46 | 42
2017-08-01 03:00 | 37 | 31 |  |  | 42948.125 | 45 | 41
2017-08-01 03:30 | 35 | 29 |  |  | 42948.1458 | 44 | 40
2017-08-01 04:00 | 35 | 29 |  |  | 42948.1667 | 43 | 39
2017-08-01 04:30 | 36 | 31 |  |  | 42948.1875 | 45 | 41
2017-08-01 05:00 | 37 | 32 |  |  | 42948.2083 | 47 | 44
2017-08-01 05:30 | 41 | 38 |  |  | 42948.2292 | 52 | 50
2017-08-01 06:00 | 47 | 45 |  |  | 42948.25 | 58 | 57
2017-08-01 06:30 | 52 | 50 |  |  | 42948.2708 | 67 | 66
2017-08-01 07:00 | 61 | 58 |  |  | 42948.2917 | 79 | 76
2017-08-01 07:30 | 70 | 65 |  |  | 42948.3125 | 92 | 86
2017-08-01 08:00 | 73 | 66 |  |  | 42948.3333 | 93 | 84
2017-08-01 08:30 | 110 | 104 |  |  | 42948.3542 | 45 | 34
2017-08-01 09:00 | 103 | 97 |  |  | 42948.375 | 43 | 31
2017-08-01 09:30 | 101 | 95 |  |  | 42948.3958 | 44 | 32
2017-08-01 10:00 | 97 | 91 |  |  | 42948.4167 | 44 | 33
2017-08-01 10:30 | 93 | 87 |  |  | 42948.4375 | 40 | 30
2017-08-01 11:00 | 87 | 85 |  |  | 42948.4583 | 31 | 30
2017-08-01 11:30 | 86 | 84 |  |  | 42948.4792 | 31 | 29
2017-08-01 12:00 | 85 | 84 |  |  | 42948.5 | 32 | 30
2017-08-01 12:30 | 83 | 81 |  |  | 42948.5208 | 30 | 30
2017-08-01 13:00 | 84 | 83 |  |  | 42948.5417 | 30 | 30
2017-08-01 13:30 | 85 | 84 |  |  | 42948.5625 | 31 | 30
2017-08-01 14:00 | 86 | 86 |  |  | 42948.5833 | 30 | 29
2017-08-01 14:30 | 88 | 87 |  |  | 42948.6042 | 31 | 30
2017-08-01 15:00 | 89 | 89 |  |  | 42948.625 | 31 | 30
2017-08-01 15:30 | 91 | 90 |  |  | 42948.6458 | 30 | 29
2017-08-01 16:00 | 95 | 94 |  |  | 42948.6667 | 31 | 31
2017-08-01 16:30 | 99 | 98 |  |  | 42948.6875 | 32 | 32
2017-08-01 17:00 | 105 | 104 |  |  | 42948.7083 | 33 | 33
2017-08-01 17:30 | 111 | 110 |  |  | 42948.7292 | 35 | 35
2017-08-01 18:00 | 117 | 117 |  |  | 42948.75 | 36 | 35
2017-08-01 18:30 | 116 | 116 |  |  | 42948.7708 | 33 | 33
2017-08-01 19:00 | 118 | 118 |  |  | 42948.7917 | 32 | 32
2017-08-01 19:30 | 117 | 117 |  |  | 42948.8125 | 32 | 32
2017-08-01 20:00 | 114 | 113 |  |  | 42948.8333 | 30 | 30
2017-08-01 20:30 | 113 | 113 |  |  | 42948.8542 | 30 | 30
2017-08-01 21:00 | 108 | 108 |  |  | 42948.875 | 27 | 27
2017-08-01 21:30 | 101 | 101 |  |  | 42948.8958 | 22 | 22
2017-08-01 22:00 | 98 | 98 |  |  | 42948.9167 | 23 | 23
2017-08-01 22:30 | 96 | 96 |  |  | 42948.9375 | 26 | 24
2017-08-01 23:00 | 92 | 92 |  |  | 42948.9583 | 24 | 22
2017-08-01 23:30 | 86 | 86 |  |  | 42948.9792 | 23 | 20
2017-08-02 | 81 | 81 |  |  | 42949 | 23 | 20
2017-08-02 00:30 | 75 | 75 |  |  | 42949.0208 | 21 | 17
2017-08-02 01:00 | 71 | 71 |  |  | 42949.0417 | 20 | 16
2017-08-02 01:30 | 69 | 69 |  |  | 42949.0625 | 18 | 15
2017-08-02 02:00 | 67 | 67 |  |  | 42949.0833 | 17 | 14
2017-08-02 02:30 | 67 | 67 |  |  | 42949.1042 | 18 | 15
2017-08-02 03:00 | 67 | 67 |  |  | 42949.125 | 18 | 15
2017-08-02 03:30 | 68 | 67 |  |  | 42949.1458 | 20 | 16
2017-08-02 04:00 | 69 | 69 |  |  | 42949.1667 | 21 | 17
2017-08-02 04:30 | 72 | 72 |  |  | 42949.1875 | 20 | 16
2017-08-02 05:00 | 74 | 74 |  |  | 42949.2083 | 21 | 16
2017-08-02 05:30 | 81 | 81 |  |  | 42949.2292 | 21 | 17
2017-08-02 06:00 | 92 | 92 |  |  | 42949.25 | 25 | 20
2017-08-02 06:30 | 106 | 106 |  |  | 42949.2708 | 28 | 28
2017-08-02 07:00 | 119 | 119 |  |  | 42949.2917 | 38 | 36
2017-08-02 07:30 | 131 | 129 |  |  | 42949.3125 | 51 | 44
2017-08-02 08:00 | 128 | 125 |  |  | 42949.3333 | 52 | 43
2017-08-02 08:30 | 121 | 118 |  |  | 42949.3542 | 48 | 41
2017-08-02 09:00 | 110 | 108 |  |  | 42949.375 | 42 | 38
2017-08-02 09:30 | 104 | 102 |  |  | 42949.3958 | 40 | 35
2017-08-02 10:00 | 97 | 96 |  |  | 42949.4167 | 33 | 33
2017-08-02 10:30 | 92 | 92 |  |  | 42949.4375 | 32 | 32
2017-08-02 11:00 | 92 | 92 |  |  | 42949.4583 | 33 | 33
2017-08-02 11:30 | 92 | 92 |  |  | 42949.4792 | 36 | 35
2017-08-02 12:00 | 92 | 92 |  |  | 42949.5 | 36 | 35
2017-08-02 12:30 | 90 | 90 |  |  | 42949.5208 | 36 | 35
2017-08-02 13:00 | 91 | 91 |  |  | 42949.5417 | 36 | 34
2017-08-02 13:30 | 93 | 93 |  |  | 42949.5625 | 37 | 36
2017-08-02 14:00 | 94 | 94 |  |  | 42949.5833 | 37 | 36
2017-08-02 14:30 | 95 | 95 |  |  | 42949.6042 | 37 | 35
2017-08-02 15:00 | 95 | 95 |  |  | 42949.625 | 36 | 35
2017-08-02 15:30 | 96 | 96 |  |  | 42949.6458 | 36 | 35
2017-08-02 16:00 | 100 | 100 |  |  | 42949.6667 | 36 | 36
2017-08-02 16:30 | 104 | 104 |  |  | 42949.6875 | 36 | 36
2017-08-02 17:00 | 110 | 110 |  |  | 42949.7083 | 37 | 37
2017-08-02 17:30 | 114 | 114 |  |  | 42949.7292 | 37 | 36
2017-08-02 18:00 | 119 | 119 |  |  | 42949.75 | 36 | 35
2017-08-02 18:30 | 121 | 120 |  |  | 42949.7708 | 37 | 34
2017-08-02 19:00 | 123 | 123 |  |  | 42949.7917 | 38 | 35
2017-08-02 19:30 | 120 | 119 |  |  | 42949.8125 | 35 | 33
2017-08-02 20:00 | 118 | 118 |  |  | 42949.8333 | 33 | 31
2017-08-02 20:30 | 118 | 118 |  |  | 42949.8542 | 32 | 31
2017-08-02 21:00 | 113 | 113 |  |  | 42949.875 | 30 | 29
2017-08-02 21:30 | 107 | 107 |  |  | 42949.8958 | 27 | 26
2017-08-02 22:00 | 102 | 102 |  |  | 42949.9167 | 26 | 26
2017-08-02 22:30 | 99 | 99 |  |  | 42949.9375 | 27 | 27
2017-08-02 23:00 | 97 | 97 |  |  | 42949.9583 | 26 | 26
2017-08-02 23:30 | 91 | 90 |  |  | 42949.9792 | 23 | 23
2017-08-03 | 83 | 83 |  |  | 42950 | 21 | 21
2017-08-03 00:30 | 78 | 77 |  |  | 42950.0208 | 19 | 19
2017-08-03 01:00 | 73 | 72 |  |  | 42950.0417 | 16 | 16
2017-08-03 01:30 | 71 | 69 |  |  | 42950.0625 | 16 | 16
2017-08-03 02:00 | 69 | 68 |  |  | 42950.0833 | 15 | 15
2017-08-03 02:30 | 69 | 67 |  |  | 42950.1042 | 16 | 16
2017-08-03 03:00 | 68 | 67 |  |  | 42950.125 | 16 | 16
2017-08-03 03:30 | 67 | 65 |  |  | 42950.1458 | 14 | 14
2017-08-03 04:00 | 67 | 66 |  |  | 42950.1667 | 14 | 14
2017-08-03 04:30 | 70 | 68 |  |  | 42950.1875 | 15 | 15
2017-08-03 05:00 | 72 | 71 |  |  | 42950.2083 | 15 | 15
2017-08-03 05:30 | 80 | 79 |  |  | 42950.2292 | 16 | 16
2017-08-03 06:00 | 91 | 90 |  |  | 42950.25 | 22 | 21
2017-08-03 06:30 | 110 | 106 |  |  | 42950.2708 | 44 | 31
2017-08-03 07:00 | 123 | 121 |  |  | 42950.2917 | 51 | 39
2017-08-03 07:30 | 131 | 128 |  |  | 42950.3125 | 53 | 45
2017-08-03 08:00 | 115 | 111 |  |  | 42950.3333 | 43 | 32
2017-08-03 08:30 | 104 | 101 |  |  | 42950.3542 | 41 | 23
2017-08-03 09:00 | 96 | 92 |  |  | 42950.375 | 45 | 23
2017-08-03 09:30 | 91 | 87 |  |  | 42950.3958 | 45 | 21
2017-08-03 10:00 | 84 | 82 |  |  | 42950.4167 | 47 | 22
2017-08-03 10:30 | 78 | 76 |  |  | 42950.4375 | 48 | 15
2017-08-03 11:00 | 78 | 75 |  |  | 42950.4583 | 50 | 17
2017-08-03 11:30 | 79 | 77 |  |  | 42950.4792 | 52 | 19
2017-08-03 12:00 | 81 | 79 |  |  | 42950.5 | 53 | 23
2017-08-03 12:30 | 83 | 81 |  |  | 42950.5208 | 53 | 21
2017-08-03 13:00 | 86 | 84 |  |  | 42950.5417 | 53 | 24
2017-08-03 13:30 | 87 | 83 |  |  | 42950.5625 | 52 | 22
2017-08-03 14:00 | 86 | 83 |  |  | 42950.5833 | 53 | 23
2017-08-03 14:30 | 86 | 82 |  |  | 42950.6042 | 51 | 21
2017-08-03 15:00 | 93 | 90 |  |  | 42950.625 | 51 | 28
2017-08-03 15:30 | 103 | 100 |  |  | 42950.6458 | 55 | 37
2017-08-03 16:00 | 105 | 102 |  |  | 42950.6667 | 55 | 36
2017-08-03 16:30 | 108 | 105 |  |  | 42950.6875 | 54 | 36
2017-08-03 17:00 | 114 | 111 |  |  | 42950.7083 | 53 | 37
2017-08-03 17:30 | 124 | 116 |  |  | 42950.7292 | 43 | 37
2017-08-03 18:00 | 132 | 122 |  |  | 42950.75 | 40 | 38
2017-08-03 18:30 | 133 | 123 |  |  | 42950.7708 | 38 | 36
2017-08-03 19:00 | 136 | 126 |  |  | 42950.7917 | 40 | 39
2017-08-03 19:30 | 136 | 126 |  |  | 42950.8125 | 39 | 38
2017-08-03 20:00 | 134 | 124 |  |  | 42950.8333 | 39 | 37
2017-08-03 20:30 | 134 | 124 |  |  | 42950.8542 | 39 | 38
2017-08-03 21:00 | 129 | 118 |  |  | 42950.875 | 38 | 35
2017-08-03 21:30 | 121 | 110 |  |  | 42950.8958 | 34 | 30
2017-08-03 22:00 | 105 | 104 |  |  | 42950.9167 | 29 | 28
2017-08-03 22:30 | 99 | 98 |  |  | 42950.9375 | 26 | 26
2017-08-03 23:00 | 97 | 97 |  |  | 42950.9583 | 26 | 26
2017-08-03 23:30 | 94 | 93 |  |  | 42950.9792 | 27 | 27
2017-08-04 | 88 | 87 |  |  | 42951 | 26 | 26
2017-08-04 00:30 | 79 | 78 |  |  | 42951.0208 | 21 | 21
2017-08-04 01:00 | 75 | 73 |  |  | 42951.0417 | 19 | 19
2017-08-04 01:30 | 73 | 71 |  |  | 42951.0625 | 19 | 19
2017-08-04 02:00 | 72 | 70 |  |  | 42951.0833 | 19 | 19
2017-08-04 02:30 | 72 | 70 |  |  | 42951.1042 | 19 | 19
2017-08-04 03:00 | 70 | 68 |  |  | 42951.125 | 20 | 19
2017-08-04 03:30 | 70 | 68 |  |  | 42951.1458 | 18 | 18
2017-08-04 04:00 | 70 | 69 |  |  | 42951.1667 | 18 | 18
2017-08-04 04:30 | 73 | 71 |  |  | 42951.1875 | 20 | 20
2017-08-04 05:00 | 75 | 74 |  |  | 42951.2083 | 20 | 20
2017-08-04 05:30 | 80 | 79 |  |  | 42951.2292 | 20 | 20
2017-08-04 06:00 | 89 | 89 |  |  | 42951.25 | 23 | 22
2017-08-04 06:30 | 97 | 97 |  |  | 42951.2708 | 29 | 28
2017-08-04 07:00 | 107 | 107 |  |  | 42951.2917 | 36 | 34
2017-08-04 07:30 | 116 | 116 |  |  | 42951.3125 | 42 | 40
2017-08-04 08:00 | 113 | 113 |  |  | 42951.3333 | 42 | 41
2017-08-04 08:30 | 107 | 107 |  |  | 42951.3542 | 42 | 41
2017-08-04 09:00 | 102 | 102 |  |  | 42951.375 | 41 | 39
2017-08-04 09:30 | 97 | 97 |  |  | 42951.3958 | 40 | 38
2017-08-04 10:00 | 94 | 94 |  |  | 42951.4167 | 39 | 37
2017-08-04 10:30 | 93 | 93 |  |  | 42951.4375 | 40 | 38
2017-08-04 11:00 | 91 | 91 |  |  | 42951.4583 | 41 | 38
2017-08-04 11:30 | 91 | 91 |  |  | 42951.4792 | 41 | 38
2017-08-04 12:00 | 88 | 88 |  |  | 42951.5 | 40 | 37
2017-08-04 12:30 | 87 | 87 |  |  | 42951.5208 | 41 | 37
2017-08-04 13:00 | 87 | 87 |  |  | 42951.5417 | 41 | 38
2017-08-04 13:30 | 89 | 89 |  |  | 42951.5625 | 40 | 37
2017-08-04 14:00 | 90 | 90 |  |  | 42951.5833 | 40 | 37
2017-08-04 14:30 | 89 | 89 |  |  | 42951.6042 | 42 | 40
2017-08-04 15:00 | 55 | 55 |  |  | 42951.625 | 78 | 77
2017-08-04 15:30 | 54 | 54 |  |  | 42951.6458 | 77 | 76
2017-08-04 16:00 | 55 | 55 |  |  | 42951.6667 | 78 | 77
2017-08-04 16:30 | 55 | 55 |  |  | 42951.6875 | 79 | 78
2017-08-04 17:00 | 56 | 56 |  |  | 42951.7083 | 79 | 78
2017-08-04 17:30 | 56 | 56 |  |  | 42951.7292 | 78 | 78
2017-08-04 18:00 | 57 | 57 |  |  | 42951.75 | 79 | 79
2017-08-04 18:30 | 57 | 57 |  |  | 42951.7708 | 79 | 79
2017-08-04 19:00 | 58 | 58 |  |  | 42951.7917 | 80 | 80
2017-08-04 19:30 | 57 | 57 |  |  | 42951.8125 | 78 | 78
2017-08-04 20:00 | 55 | 55 |  |  | 42951.8333 | 76 | 76
2017-08-04 20:30 | 55 | 55 |  |  | 42951.8542 | 76 | 76
2017-08-04 21:00 | 53 | 53 |  |  | 42951.875 | 72 | 72
2017-08-04 21:30 | 52 | 52 |  |  | 42951.8958 | 71 | 71
2017-08-04 22:00 | 52 | 52 |  |  | 42951.9167 | 71 | 71
2017-08-04 22:30 | 51 | 51 |  |  | 42951.9375 | 71 | 71
2017-08-04 23:00 | 51 | 51 |  |  | 42951.9583 | 68 | 68
2017-08-04 23:30 | 48 | 47 |  |  | 42951.9792 | 65 | 64
2017-08-05 | 45 | 44 |  |  | 42952 | 61 | 60
2017-08-05 00:30 | 42 | 41 |  |  | 42952.0208 | 56 | 55
2017-08-05 01:00 | 40 | 39 |  |  | 42952.0417 | 54 | 54
2017-08-05 01:30 | 37 | 36 |  |  | 42952.0625 | 54 | 50
2017-08-05 02:00 | 36 | 36 |  |  | 42952.0833 | 53 | 49
2017-08-05 02:30 | 38 | 38 |  |  | 42952.1042 | 54 | 50
2017-08-05 03:00 | 39 | 39 |  |  | 42952.125 | 55 | 52
2017-08-05 03:30 | 39 | 39 |  |  | 42952.1458 | 55 | 52
2017-08-05 04:00 | 40 | 40 |  |  | 42952.1667 | 54 | 52
2017-08-05 04:30 | 38 | 38 |  |  | 42952.1875 | 54 | 51
2017-08-05 05:00 | 42 | 42 |  |  | 42952.2083 | 57 | 54
2017-08-05 05:30 | 40 | 40 |  |  | 42952.2292 | 55 | 52
2017-08-05 06:00 | 39 | 39 |  |  | 42952.25 | 54 | 51
2017-08-05 06:30 | 40 | 39 |  |  | 42952.2708 | 55 | 53
2017-08-05 07:00 | 40 | 40 |  |  | 42952.2917 | 56 | 55
2017-08-05 07:30 | 42 | 41 |  |  | 42952.3125 | 58 | 57
2017-08-05 08:00 | 45 | 44 |  |  | 42952.3333 | 61 | 60
2017-08-05 08:30 | 45 | 44 |  |  | 42952.3542 | 62 | 62
2017-08-05 09:00 | 45 | 45 |  |  | 42952.375 | 62 | 62
2017-08-05 09:30 | 43 | 43 |  |  | 42952.3958 | 59 | 59
2017-08-05 10:00 | 42 | 41 |  |  | 42952.4167 | 57 | 57
2017-08-05 10:30 | 41 | 40 |  |  | 42952.4375 | 56 | 56
2017-08-05 11:00 | 41 | 40 |  |  | 42952.4583 | 55 | 55
2017-08-05 11:30 | 40 | 39 |  |  | 42952.4792 | 53 | 53
2017-08-05 12:00 | 38 | 37 |  |  | 42952.5 | 51 | 51
2017-08-05 12:30 | 38 | 37 |  |  | 42952.5208 | 51 | 51
2017-08-05 13:00 | 38 | 37 |  |  | 42952.5417 | 51 | 50
2017-08-05 13:30 | 38 | 37 |  |  | 42952.5625 | 51 | 51
2017-08-05 14:00 | 41 | 40 |  |  | 42952.5833 | 54 | 54
2017-08-05 14:30 | 41 | 40 |  |  | 42952.6042 | 53 | 53
2017-08-05 15:00 | 46 | 46 |  |  | 42952.625 | 60 | 60
2017-08-05 15:30 | 48 | 48 |  |  | 42952.6458 | 63 | 62
2017-08-05 16:00 | 48 | 47 |  |  | 42952.6667 | 63 | 62
2017-08-05 16:30 | 49 | 48 |  |  | 42952.6875 | 66 | 65
2017-08-05 17:00 | 52 | 51 |  |  | 42952.7083 | 69 | 68
2017-08-05 17:30 | 50 | 50 |  |  | 42952.7292 | 67 | 67
2017-08-05 18:00 | 52 | 51 |  |  | 42952.75 | 70 | 69
2017-08-05 18:30 | 52 | 51 |  |  | 42952.7708 | 70 | 70
2017-08-05 19:00 | 52 | 51 |  |  | 42952.7917 | 72 | 71
2017-08-05 19:30 | 55 | 54 |  |  | 42952.8125 | 74 | 73
2017-08-05 20:00 | 54 | 53 |  |  | 42952.8333 | 72 | 71
2017-08-05 20:30 | 53 | 52 |  |  | 42952.8542 | 72 | 71
2017-08-05 21:00 | 52 | 51 |  |  | 42952.875 | 69 | 68
2017-08-05 21:30 | 50 | 49 |  |  | 42952.8958 | 67 | 66
2017-08-05 22:00 | 51 | 50 |  |  | 42952.9167 | 68 | 68
2017-08-05 22:30 | 51 | 50 |  |  | 42952.9375 | 68 | 68
2017-08-05 23:00 | 50 | 49 |  |  | 42952.9583 | 66 | 66
2017-08-05 23:30 | 48 | 47 |  |  | 42952.9792 | 63 | 62
2017-08-06 | 48 | 47 |  |  | 42953 | 62 | 61
2017-08-06 00:30 | 46 | 45 |  |  | 42953.0208 | 60 | 59
2017-08-06 01:00 | 45 | 43 |  |  | 42953.0417 | 57 | 57
2017-08-06 01:30 | 44 | 42 |  |  | 42953.0625 | 57 | 56
2017-08-06 02:00 | 44 | 42 |  |  | 42953.0833 | 55 | 55
2017-08-06 02:30 | 43 | 42 |  |  | 42953.1042 | 56 | 55
2017-08-06 03:00 | 42 | 41 |  |  | 42953.125 | 54 | 54
2017-08-06 03:30 | 42 | 41 |  |  | 42953.1458 | 54 | 54
2017-08-06 04:00 | 42 | 41 |  |  | 42953.1667 | 54 | 54
2017-08-06 04:30 | 42 | 40 |  |  | 42953.1875 | 54 | 54
2017-08-06 05:00 | 41 | 40 |  |  | 42953.2083 | 53 | 53
2017-08-06 05:30 | 39 | 38 |  |  | 42953.2292 | 52 | 52
2017-08-06 06:00 | 40 | 39 |  |  | 42953.25 | 53 | 52
2017-08-06 06:30 | 40 | 39 |  |  | 42953.2708 | 53 | 53
2017-08-06 07:00 | 40 | 39 |  |  | 42953.2917 | 55 | 55
2017-08-06 07:30 | 40 | 39 |  |  | 42953.3125 | 57 | 57
2017-08-06 08:00 | 44 | 43 |  |  | 42953.3333 | 62 | 62
2017-08-06 08:30 | 49 | 48 |  |  | 42953.3542 | 68 | 68
2017-08-06 09:00 | 51 | 51 |  |  | 42953.375 | 71 | 70
2017-08-06 09:30 | 48 | 48 |  |  | 42953.3958 | 68 | 68
2017-08-06 10:00 | 49 | 48 |  |  | 42953.4167 | 68 | 68
2017-08-06 10:30 | 49 | 48 |  |  | 42953.4375 | 66 | 66
2017-08-06 11:00 | 46 | 46 |  |  | 42953.4583 | 64 | 64
2017-08-06 11:30 | 46 | 45 |  |  | 42953.4792 | 61 | 61
2017-08-06 12:00 | 47 | 47 |  |  | 42953.5 | 58 | 58
2017-08-06 12:30 | 46 | 46 |  |  | 42953.5208 | 59 | 59
2017-08-06 13:00 | 47 | 46 |  |  | 42953.5417 | 60 | 60
2017-08-06 13:30 | 48 | 47 |  |  | 42953.5625 | 64 | 64
2017-08-06 14:00 | 47 | 47 |  |  | 42953.5833 | 65 | 65
2017-08-06 14:30 | 47 | 47 |  |  | 42953.6042 | 65 | 65
2017-08-06 15:00 | 48 | 47 |  |  | 42953.625 | 64 | 64
2017-08-06 15:30 | 50 | 49 |  |  | 42953.6458 | 66 | 66
2017-08-06 16:00 | 50 | 49 |  |  | 42953.6667 | 67 | 67
2017-08-06 16:30 | 51 | 50 |  |  | 42953.6875 | 69 | 69
2017-08-06 17:00 | 58 | 58 |  |  | 42953.7083 | 77 | 77
2017-08-06 17:30 | 62 | 61 |  |  | 42953.7292 | 79 | 79
2017-08-06 18:00 | 64 | 63 |  |  | 42953.75 | 80 | 80
2017-08-06 18:30 | 64 | 63 |  |  | 42953.7708 | 82 | 82
2017-08-06 19:00 | 63 | 62 |  |  | 42953.7917 | 81 | 81
2017-08-06 19:30 | 62 | 61 |  |  | 42953.8125 | 80 | 80
2017-08-06 20:00 | 60 | 59 |  |  | 42953.8333 | 79 | 79
2017-08-06 20:30 | 59 | 58 |  |  | 42953.8542 | 79 | 79
2017-08-06 21:00 | 56 | 56 |  |  | 42953.875 | 74 | 74
2017-08-06 21:30 | 56 | 55 |  |  | 42953.8958 | 72 | 72
2017-08-06 22:00 | 53 | 52 |  |  | 42953.9167 | 71 | 71
2017-08-06 22:30 | 52 | 51 |  |  | 42953.9375 | 71 | 71
2017-08-06 23:00 | 51 | 50 |  |  | 42953.9583 | 68 | 68
2017-08-06 23:30 | 47 | 46 |  |  | 42953.9792 | 64 | 64
2017-08-07 | 42 | 41 |  |  | 42954 | 59 | 59
2017-08-07 00:30 | 38 | 36 |  |  | 42954.0208 | 53 | 53
2017-08-07 01:00 | 37 | 35 |  |  | 42954.0417 | 52 | 52
2017-08-07 01:30 | 37 | 35 |  |  | 42954.0625 | 52 | 51
2017-08-07 02:00 | 38 | 36 |  |  | 42954.0833 | 54 | 54
2017-08-07 02:30 | 39 | 37 |  |  | 42954.1042 | 55 | 54
2017-08-07 03:00 | 40 | 38 |  |  | 42954.125 | 55 | 55
2017-08-07 03:30 | 41 | 39 |  |  | 42954.1458 | 55 | 55
2017-08-07 04:00 | 41 | 39 |  |  | 42954.1667 | 55 | 55
2017-08-07 04:30 | 41 | 39 |  |  | 42954.1875 | 54 | 54
2017-08-07 05:00 | 38 | 37 |  |  | 42954.2083 | 54 | 54
2017-08-07 05:30 | 40 | 40 |  |  | 42954.2292 | 57 | 57
2017-08-07 06:00 | 48 | 48 |  |  | 42954.25 | 64 | 64
2017-08-07 06:30 | 53 | 53 |  |  | 42954.2708 | 73 | 73
2017-08-07 07:00 | 58 | 58 |  |  | 42954.2917 | 82 | 82
2017-08-07 07:30 | 64 | 64 |  |  | 42954.3125 | 93 | 92
2017-08-07 08:00 | 66 | 66 |  |  | 42954.3333 | 95 | 95
2017-08-07 08:30 | 63 | 63 |  |  | 42954.3542 | 91 | 90
2017-08-07 09:00 | 59 | 58 |  |  | 42954.375 | 86 | 85
2017-08-07 09:30 | 58 | 57 |  |  | 42954.3958 | 84 | 83
2017-08-07 10:00 | 59 | 59 |  |  | 42954.4167 | 86 | 85
2017-08-07 10:30 | 59 | 59 |  |  | 42954.4375 | 86 | 85
2017-08-07 11:00 | 58 | 57 |  |  | 42954.4583 | 83 | 82
2017-08-07 11:30 | 55 | 55 |  |  | 42954.4792 | 81 | 80
2017-08-07 12:00 | 54 | 54 |  |  | 42954.5 | 80 | 79
2017-08-07 12:30 | 55 | 55 |  |  | 42954.5208 | 80 | 79
2017-08-07 13:00 | 54 | 54 |  |  | 42954.5417 | 80 | 79
2017-08-07 13:30 | 53 | 53 |  |  | 42954.5625 | 80 | 79
2017-08-07 14:00 | 55 | 55 |  |  | 42954.5833 | 80 | 79
2017-08-07 14:30 | 55 | 55 |  |  | 42954.6042 | 80 | 79
2017-08-07 15:00 | 56 | 56 |  |  | 42954.625 | 81 | 80
2017-08-07 15:30 | 58 | 57 |  |  | 42954.6458 | 84 | 83
2017-08-07 16:00 | 61 | 61 |  |  | 42954.6667 | 87 | 86
2017-08-07 16:30 | 64 | 63 |  |  | 42954.6875 | 90 | 88
2017-08-07 17:00 | 69 | 68 |  |  | 42954.7083 | 95 | 92
2017-08-07 17:30 | 70 | 69 |  |  | 42954.7292 | 96 | 93
2017-08-07 18:00 | 71 | 69 |  |  | 42954.75 | 97 | 92
2017-08-07 18:30 | 70 | 67 |  |  | 42954.7708 | 96 | 89
2017-08-07 19:00 | 72 | 69 |  |  | 42954.7917 | 98 | 91
2017-08-07 19:30 | 70 | 68 |  |  | 42954.8125 | 96 | 89
2017-08-07 20:00 | 68 | 65 |  |  | 42954.8333 | 93 | 86
2017-08-07 20:30 | 67 | 65 |  |  | 42954.8542 | 93 | 86
2017-08-07 21:00 | 63 | 63 |  |  | 42954.875 | 83 | 82
2017-08-07 21:30 | 56 | 56 |  |  | 42954.8958 | 75 | 75
2017-08-07 22:00 | 53 | 53 |  |  | 42954.9167 | 74 | 73
2017-08-07 22:30 | 55 | 55 |  |  | 42954.9375 | 76 | 75
2017-08-07 23:00 | 54 | 54 |  |  | 42954.9583 | 74 | 73
2017-08-07 23:30 | 49 | 49 |  |  | 42954.9792 | 68 | 67
2017-08-08 | 44 | 43 |  |  | 42955 | 62 | 61
2017-08-08 00:30 | 41 | 40 |  |  | 42955.0208 | 57 | 56
2017-08-08 01:00 | 40 | 38 |  |  | 42955.0417 | 53 | 53
2017-08-08 01:30 | 39 | 37 |  |  | 42955.0625 | 53 | 52
2017-08-08 02:00 | 39 | 37 |  |  | 42955.0833 | 51 | 51
2017-08-08 02:30 | 38 | 36 |  |  | 42955.1042 | 51 | 50
2017-08-08 03:00 | 37 | 35 |  |  | 42955.125 | 51 | 50
2017-08-08 03:30 | 38 | 36 |  |  | 42955.1458 | 52 | 51
2017-08-08 04:00 | 38 | 37 |  |  | 42955.1667 | 52 | 51
2017-08-08 04:30 | 38 | 37 |  |  | 42955.1875 | 51 | 51
2017-08-08 05:00 | 38 | 37 |  |  | 42955.2083 | 52 | 52
2017-08-08 05:30 | 41 | 41 |  |  | 42955.2292 | 55 | 55
2017-08-08 06:00 | 46 | 46 |  |  | 42955.25 | 60 | 60
2017-08-08 06:30 | 53 | 53 |  |  | 42955.2708 | 73 | 73
2017-08-08 07:00 | 57 | 57 |  |  | 42955.2917 | 81 | 81
2017-08-08 07:30 | 63 | 63 |  |  | 42955.3125 | 89 | 89
2017-08-08 08:00 | 60 | 60 |  |  | 42955.3333 | 88 | 88
2017-08-08 08:30 | 57 | 57 |  |  | 42955.3542 | 86 | 86
2017-08-08 09:00 | 52 | 52 |  |  | 42955.375 | 81 | 81
2017-08-08 09:30 | 50 | 50 |  |  | 42955.3958 | 78 | 77
2017-08-08 10:00 | 47 | 47 |  |  | 42955.4167 | 75 | 74
2017-08-08 10:30 | 46 | 46 |  |  | 42955.4375 | 72 | 72
2017-08-08 11:00 | 46 | 46 |  |  | 42955.4583 | 71 | 71
2017-08-08 11:30 | 46 | 46 |  |  | 42955.4792 | 72 | 71
2017-08-08 12:00 | 45 | 45 |  |  | 42955.5 | 71 | 71
2017-08-08 12:30 | 44 | 44 |  |  | 42955.5208 | 70 | 70
2017-08-08 13:00 | 45 | 45 |  |  | 42955.5417 | 71 | 70
2017-08-08 13:30 | 46 | 46 |  |  | 42955.5625 | 72 | 72
2017-08-08 14:00 | 49 | 49 |  |  | 42955.5833 | 73 | 73
2017-08-08 14:30 | 49 | 49 |  |  | 42955.6042 | 75 | 74
2017-08-08 15:00 | 49 | 49 |  |  | 42955.625 | 76 | 75
2017-08-08 15:30 | 51 | 51 |  |  | 42955.6458 | 76 | 76
2017-08-08 16:00 | 54 | 54 |  |  | 42955.6667 | 79 | 79
2017-08-08 16:30 | 58 | 58 |  |  | 42955.6875 | 84 | 84
2017-08-08 17:00 | 64 | 64 |  |  | 42955.7083 | 89 | 89
2017-08-08 17:30 | 65 | 65 |  |  | 42955.7292 | 89 | 88
2017-08-08 18:00 | 68 | 67 |  |  | 42955.75 | 91 | 91
2017-08-08 18:30 | 69 | 68 |  |  | 42955.7708 | 91 | 90
2017-08-08 19:00 | 71 | 70 |  |  | 42955.7917 | 94 | 93
2017-08-08 19:30 | 70 | 69 |  |  | 42955.8125 | 91 | 91
2017-08-08 20:00 | 67 | 67 |  |  | 42955.8333 | 88 | 88
2017-08-08 20:30 | 67 | 66 |  |  | 42955.8542 | 87 | 87
2017-08-08 21:00 | 64 | 64 |  |  | 42955.875 | 83 | 83
2017-08-08 21:30 | 60 | 60 |  |  | 42955.8958 | 80 | 80
2017-08-08 22:00 | 57 | 56 |  |  | 42955.9167 | 78 | 78
2017-08-08 22:30 | 55 | 55 |  |  | 42955.9375 | 77 | 77
2017-08-08 23:00 | 54 | 53 |  |  | 42955.9583 | 74 | 73
2017-08-08 23:30 | 49 | 48 |  |  | 42955.9792 | 68 | 68
2017-08-09 | 45 | 43 |  |  | 42956 | 63 | 63
2017-08-09 00:30 | 40 | 39 |  |  | 42956.0208 | 56 | 55
2017-08-09 01:00 | 37 | 36 |  |  | 42956.0417 | 53 | 52
2017-08-09 01:30 | 37 | 35 |  |  | 42956.0625 | 51 | 50
2017-08-09 02:00 | 35 | 33 |  |  | 42956.0833 | 49 | 48
2017-08-09 02:30 | 36 | 33 |  |  | 42956.1042 | 48 | 48
2017-08-09 03:00 | 35 | 33 |  |  | 42956.125 | 49 | 48
2017-08-09 03:30 | 36 | 33 |  |  | 42956.1458 | 50 | 49
2017-08-09 04:00 | 36 | 34 |  |  | 42956.1667 | 50 | 49
2017-08-09 04:30 | 36 | 34 |  |  | 42956.1875 | 49 | 48
2017-08-09 05:00 | 38 | 36 |  |  | 42956.2083 | 52 | 51
2017-08-09 05:30 | 41 | 41 |  |  | 42956.2292 | 56 | 56
2017-08-09 06:00 | 47 | 47 |  |  | 42956.25 | 63 | 62
2017-08-09 06:30 | 57 | 57 |  |  | 42956.2708 | 76 | 76
2017-08-09 07:00 | 65 | 65 |  |  | 42956.2917 | 89 | 89
2017-08-09 07:30 | 70 | 70 |  |  | 42956.3125 | 97 | 97
2017-08-09 08:00 | 68 | 68 |  |  | 42956.3333 | 96 | 96
2017-08-09 08:30 | 63 | 63 |  |  | 42956.3542 | 90 | 90
2017-08-09 09:00 | 58 | 58 |  |  | 42956.375 | 84 | 84
2017-08-09 09:30 | 54 | 54 |  |  | 42956.3958 | 80 | 79
2017-08-09 10:00 | 52 | 52 |  |  | 42956.4167 | 77 | 77
2017-08-09 10:30 | 51 | 51 |  |  | 42956.4375 | 75 | 74
2017-08-09 11:00 | 50 | 50 |  |  | 42956.4583 | 74 | 74
2017-08-09 11:30 | 49 | 48 |  |  | 42956.4792 | 74 | 73
2017-08-09 12:00 | 49 | 49 |  |  | 42956.5 | 74 | 74
2017-08-09 12:30 | 49 | 48 |  |  | 42956.5208 | 74 | 74
2017-08-09 13:00 | 50 | 49 |  |  | 42956.5417 | 75 | 74
2017-08-09 13:30 | 49 | 49 |  |  | 42956.5625 | 74 | 73
2017-08-09 14:00 | 51 | 51 |  |  | 42956.5833 | 75 | 75
2017-08-09 14:30 | 55 | 55 |  |  | 42956.6042 | 79 | 79
2017-08-09 15:00 | 56 | 56 |  |  | 42956.625 | 81 | 81
2017-08-09 15:30 | 57 | 57 |  |  | 42956.6458 | 82 | 82
2017-08-09 16:00 | 58 | 58 |  |  | 42956.6667 | 83 | 82
2017-08-09 16:30 | 63 | 63 |  |  | 42956.6875 | 88 | 88
2017-08-09 17:00 | 69 | 69 |  |  | 42956.7083 | 93 | 93
2017-08-09 17:30 | 71 | 71 |  |  | 42956.7292 | 94 | 94
2017-08-09 18:00 | 75 | 74 |  |  | 42956.75 | 95 | 95
2017-08-09 18:30 | 76 | 76 |  |  | 42956.7708 | 96 | 96
2017-08-09 19:00 | 78 | 77 |  |  | 42956.7917 | 98 | 98
2017-08-09 19:30 | 76 | 75 |  |  | 42956.8125 | 96 | 96
2017-08-09 20:00 | 75 | 75 |  |  | 42956.8333 | 95 | 94
2017-08-09 20:30 | 73 | 73 |  |  | 42956.8542 | 93 | 93
2017-08-09 21:00 | 68 | 68 |  |  | 42956.875 | 86 | 86
2017-08-09 21:30 | 65 | 64 |  |  | 42956.8958 | 81 | 81
2017-08-09 22:00 | 60 | 59 |  |  | 42956.9167 | 78 | 78
2017-08-09 22:30 | 56 | 56 |  |  | 42956.9375 | 75 | 74
2017-08-09 23:00 | 53 | 53 |  |  | 42956.9583 | 71 | 70
2017-08-09 23:30 | 48 | 47 |  |  | 42956.9792 | 65 | 65
2017-08-10 | 44 | 44 |  |  | 42957 | 61 | 60
2017-08-10 00:30 | 40 | 40 |  |  | 42957.0208 | 56 | 55
2017-08-10 01:00 | 38 | 37 |  |  | 42957.0417 | 51 | 51
2017-08-10 01:30 | 35 | 34 |  |  | 42957.0625 | 49 | 48
2017-08-10 02:00 | 35 | 34 |  |  | 42957.0833 | 47 | 46
2017-08-10 02:30 | 33 | 32 |  |  | 42957.1042 | 45 | 44
2017-08-10 03:00 | 32 | 31 |  |  | 42957.125 | 44 | 43
2017-08-10 03:30 | 34 | 33 |  |  | 42957.1458 | 44 | 43
2017-08-10 04:00 | 34 | 33 |  |  | 42957.1667 | 44 | 43
2017-08-10 04:30 | 37 | 36 |  |  | 42957.1875 | 47 | 47
2017-08-10 05:00 | 38 | 37 |  |  | 42957.2083 | 49 | 49
2017-08-10 05:30 | 41 | 41 |  |  | 42957.2292 | 54 | 53
2017-08-10 06:00 | 49 | 49 |  |  | 42957.25 | 65 | 64
2017-08-10 06:30 | 58 | 58 |  |  | 42957.2708 | 77 | 77
2017-08-10 07:00 | 67 | 66 |  |  | 42957.2917 | 89 | 89
2017-08-10 07:30 | 72 | 72 |  |  | 42957.3125 | 99 | 99
2017-08-10 08:00 | 70 | 70 |  |  | 42957.3333 | 97 | 97
2017-08-10 08:30 | 64 | 63 |  |  | 42957.3542 | 92 | 92
2017-08-10 09:00 | 59 | 59 |  |  | 42957.375 | 85 | 85
2017-08-10 09:30 | 57 | 57 |  |  | 42957.3958 | 82 | 82
2017-08-10 10:00 | 52 | 52 |  |  | 42957.4167 | 77 | 77
2017-08-10 10:30 | 51 | 51 |  |  | 42957.4375 | 74 | 74
2017-08-10 11:00 | 49 | 49 |  |  | 42957.4583 | 73 | 73
2017-08-10 11:30 | 49 | 49 |  |  | 42957.4792 | 71 | 71
2017-08-10 12:00 | 49 | 49 |  |  | 42957.5 | 71 | 71
2017-08-10 12:30 | 50 | 50 |  |  | 42957.5208 | 72 | 72
2017-08-10 13:00 | 51 | 51 |  |  | 42957.5417 | 74 | 74
2017-08-10 13:30 | 55 | 55 |  |  | 42957.5625 | 77 | 77
2017-08-10 14:00 | 58 | 58 |  |  | 42957.5833 | 80 | 80
2017-08-10 14:30 | 57 | 57 |  |  | 42957.6042 | 78 | 78
2017-08-10 15:00 | 56 | 56 |  |  | 42957.625 | 78 | 78
2017-08-10 15:30 | 58 | 58 |  |  | 42957.6458 | 80 | 80
2017-08-10 16:00 | 58 | 58 |  |  | 42957.6667 | 81 | 81
2017-08-10 16:30 | 62 | 62 |  |  | 42957.6875 | 85 | 84
2017-08-10 17:00 | 65 | 65 |  |  | 42957.7083 | 88 | 88
2017-08-10 17:30 | 68 | 67 |  |  | 42957.7292 | 90 | 89
2017-08-10 18:00 | 70 | 69 |  |  | 42957.75 | 92 | 92
2017-08-10 18:30 | 72 | 71 |  |  | 42957.7708 | 93 | 93
2017-08-10 19:00 | 74 | 73 |  |  | 42957.7917 | 95 | 95
2017-08-10 19:30 | 72 | 71 |  |  | 42957.8125 | 93 | 93
2017-08-10 20:00 | 70 | 69 |  |  | 42957.8333 | 89 | 89
2017-08-10 20:30 | 68 | 67 |  |  | 42957.8542 | 88 | 88
2017-08-10 21:00 | 66 | 65 |  |  | 42957.875 | 85 | 85
2017-08-10 21:30 | 62 | 60 |  |  | 42957.8958 | 79 | 79
2017-08-10 22:00 | 58 | 56 |  |  | 42957.9167 | 77 | 77
2017-08-10 22:30 | 57 | 57 |  |  | 42957.9375 | 78 | 78
2017-08-10 23:00 | 55 | 54 |  |  | 42957.9583 | 73 | 72
2017-08-10 23:30 | 49 | 49 |  |  | 42957.9792 | 68 | 68
2017-08-11 | 44 | 44 |  |  | 42958 | 62 | 62
2017-08-11 00:30 | 39 | 39 |  |  | 42958.0208 | 55 | 55
2017-08-11 01:00 | 35 | 35 |  |  | 42958.0417 | 50 | 50
2017-08-11 01:30 | 34 | 34 |  |  | 42958.0625 | 48 | 48
2017-08-11 02:00 | 34 | 34 |  |  | 42958.0833 | 47 | 47
2017-08-11 02:30 | 34 | 34 |  |  | 42958.1042 | 46 | 46
2017-08-11 03:00 | 32 | 32 |  |  | 42958.125 | 45 | 44
2017-08-11 03:30 | 33 | 33 |  |  | 42958.1458 | 46 | 46
2017-08-11 04:00 | 36 | 36 |  |  | 42958.1667 | 47 | 47
2017-08-11 04:30 | 38 | 38 |  |  | 42958.1875 | 50 | 50
2017-08-11 05:00 | 41 | 41 |  |  | 42958.2083 | 54 | 53
2017-08-11 05:30 | 43 | 43 |  |  | 42958.2292 | 57 | 57
2017-08-11 06:00 | 49 | 48 |  |  | 42958.25 | 64 | 63
2017-08-11 06:30 | 57 | 56 |  |  | 42958.2708 | 76 | 75
2017-08-11 07:00 | 56 | 55 |  |  | 42958.2917 | 83 | 82
2017-08-11 07:30 | 57 | 56 |  |  | 42958.3125 | 88 | 88
2017-08-11 08:00 | 55 | 54 |  |  | 42958.3333 | 87 | 87
2017-08-11 08:30 | 52 | 52 |  |  | 42958.3542 | 84 | 84
2017-08-11 09:00 | 50 | 50 |  |  | 42958.375 | 79 | 79
2017-08-11 09:30 | 48 | 47 |  |  | 42958.3958 | 77 | 77
2017-08-11 10:00 | 46 | 46 |  |  | 42958.4167 | 74 | 74
2017-08-11 10:30 | 47 | 47 |  |  | 42958.4375 | 73 | 73
2017-08-11 11:00 | 47 | 47 |  |  | 42958.4583 | 73 | 73
2017-08-11 11:30 | 47 | 46 |  |  | 42958.4792 | 73 | 73
2017-08-11 12:00 | 47 | 47 |  |  | 42958.5 | 73 | 73
2017-08-11 12:30 | 47 | 46 |  |  | 42958.5208 | 73 | 73
2017-08-11 13:00 | 47 | 47 |  |  | 42958.5417 | 73 | 73
2017-08-11 13:30 | 47 | 46 |  |  | 42958.5625 | 73 | 73
2017-08-11 14:00 | 48 | 48 |  |  | 42958.5833 | 74 | 74
2017-08-11 14:30 | 51 | 51 |  |  | 42958.6042 | 76 | 76
2017-08-11 15:00 | 53 | 53 |  |  | 42958.625 | 77 | 77
2017-08-11 15:30 | 54 | 54 |  |  | 42958.6458 | 78 | 78
2017-08-11 16:00 | 56 | 56 |  |  | 42958.6667 | 80 | 80
2017-08-11 16:30 | 59 | 59 |  |  | 42958.6875 | 84 | 84
2017-08-11 17:00 | 61 | 61 |  |  | 42958.7083 | 86 | 86
2017-08-11 17:30 | 62 | 61 |  |  | 42958.7292 | 86 | 86
2017-08-11 18:00 | 63 | 63 |  |  | 42958.75 | 85 | 85
2017-08-11 18:30 | 63 | 63 |  |  | 42958.7708 | 83 | 83
2017-08-11 19:00 | 63 | 63 |  |  | 42958.7917 | 85 | 84
2017-08-11 19:30 | 61 | 61 |  |  | 42958.8125 | 82 | 81
2017-08-11 20:00 | 60 | 60 |  |  | 42958.8333 | 81 | 81
2017-08-11 20:30 | 58 | 58 |  |  | 42958.8542 | 78 | 78
2017-08-11 21:00 | 55 | 55 |  |  | 42958.875 | 75 | 75
2017-08-11 21:30 | 52 | 52 |  |  | 42958.8958 | 72 | 72
2017-08-11 22:00 | 50 | 50 |  |  | 42958.9167 | 71 | 71
2017-08-11 22:30 | 54 | 54 |  |  | 42958.9375 | 74 | 74
2017-08-11 23:00 | 54 | 54 |  |  | 42958.9583 | 74 | 74
2017-08-11 23:30 | 50 | 50 |  |  | 42958.9792 | 69 | 69
2017-08-12 | 46 | 46 |  |  | 42959 | 64 | 64
2017-08-12 00:30 | 42 | 42 |  |  | 42959.0208 | 58 | 58
2017-08-12 01:00 | 38 | 38 |  |  | 42959.0417 | 53 | 53
2017-08-12 01:30 | 34 | 34 |  |  | 42959.0625 | 49 | 49
2017-08-12 02:00 | 35 | 34 |  |  | 42959.0833 | 49 | 49
2017-08-12 02:30 | 38 | 36 |  |  | 42959.1042 | 51 | 49
2017-08-12 03:00 | 39 | 37 |  |  | 42959.125 | 51 | 50
2017-08-12 03:30 | 38 | 36 |  |  | 42959.1458 | 52 | 50
2017-08-12 04:00 | 39 | 38 |  |  | 42959.1667 | 53 | 51
2017-08-12 04:30 | 39 | 38 |  |  | 42959.1875 | 53 | 51
2017-08-12 05:00 | 40 | 38 |  |  | 42959.2083 | 53 | 51
2017-08-12 05:30 | 40 | 39 |  |  | 42959.2292 | 53 | 51
2017-08-12 06:00 | 41 | 39 |  |  | 42959.25 | 54 | 52
2017-08-12 06:30 | 39 | 36 |  |  | 42959.2708 | 53 | 52
2017-08-12 07:00 | 40 | 38 |  |  | 42959.2917 | 55 | 54
2017-08-12 07:30 | 42 | 39 |  |  | 42959.3125 | 57 | 56
2017-08-12 08:00 | 42 | 39 |  |  | 42959.3333 | 58 | 57
2017-08-12 08:30 | 44 | 40 |  |  | 42959.3542 | 59 | 59
2017-08-12 09:00 | 42 | 38 |  |  | 42959.375 | 58 | 58
2017-08-12 09:30 | 41 | 36 |  |  | 42959.3958 | 56 | 56
2017-08-12 10:00 | 39 | 34 |  |  | 42959.4167 | 51 | 51
2017-08-12 10:30 | 45 | 41 |  |  | 42959.4375 | 55 | 55
2017-08-12 11:00 | 48 | 44 |  |  | 42959.4583 | 62 | 62
2017-08-12 11:30 | 45 | 40 |  |  | 42959.4792 | 62 | 62
2017-08-12 12:00 | 42 | 37 |  |  | 42959.5 | 52 | 52
2017-08-12 12:30 | 44 | 39 |  |  | 42959.5208 | 56 | 56
2017-08-12 13:00 | 46 | 43 |  |  | 42959.5417 | 61 | 61
2017-08-12 13:30 | 45 | 41 |  |  | 42959.5625 | 59 | 58
2017-08-12 14:00 | 46 | 43 |  |  | 42959.5833 | 61 | 61
2017-08-12 14:30 | 43 | 40 |  |  | 42959.6042 | 58 | 58
2017-08-12 15:00 | 44 | 40 |  |  | 42959.625 | 58 | 58
2017-08-12 15:30 | 44 | 41 |  |  | 42959.6458 | 60 | 60
2017-08-12 16:00 | 45 | 41 |  |  | 42959.6667 | 61 | 60
2017-08-12 16:30 | 46 | 42 |  |  | 42959.6875 | 63 | 63
2017-08-12 17:00 | 49 | 45 |  |  | 42959.7083 | 66 | 66
2017-08-12 17:30 | 49 | 46 |  |  | 42959.7292 | 67 | 67
2017-08-12 18:00 | 50 | 47 |  |  | 42959.75 | 68 | 68
2017-08-12 18:30 | 51 | 49 |  |  | 42959.7708 | 70 | 69
2017-08-12 19:00 | 52 | 50 |  |  | 42959.7917 | 71 | 71
2017-08-12 19:30 | 50 | 48 |  |  | 42959.8125 | 69 | 69
2017-08-12 20:00 | 49 | 47 |  |  | 42959.8333 | 68 | 68
2017-08-12 20:30 | 49 | 47 |  |  | 42959.8542 | 68 | 68
2017-08-12 21:00 | 49 | 47 |  |  | 42959.875 | 67 | 67
2017-08-12 21:30 | 46 | 43 |  |  | 42959.8958 | 64 | 64
2017-08-12 22:00 | 46 | 44 |  |  | 42959.9167 | 64 | 64
2017-08-12 22:30 | 46 | 44 |  |  | 42959.9375 | 65 | 64
2017-08-12 23:00 | 46 | 45 |  |  | 42959.9583 | 63 | 62
2017-08-12 23:30 | 44 | 42 |  |  | 42959.9792 | 60 | 60
2017-08-13 | 40 | 38 |  |  | 42960 | 57 | 56
2017-08-13 00:30 | 36 | 33 |  |  | 42960.0208 | 51 | 49
2017-08-13 01:00 | 32 | 30 |  |  | 42960.0417 | 47 | 45
2017-08-13 01:30 | 32 | 29 |  |  | 42960.0625 | 45 | 44
2017-08-13 02:00 | 31 | 29 |  |  | 42960.0833 | 43 | 42
2017-08-13 02:30 | 31 | 29 |  |  | 42960.1042 | 42 | 41
2017-08-13 03:00 | 30 | 27 |  |  | 42960.125 | 41 | 41
2017-08-13 03:30 | 32 | 27 |  |  | 42960.1458 | 41 | 41
2017-08-13 04:00 | 32 | 27 |  |  | 42960.1667 | 41 | 41
2017-08-13 04:30 | 32 | 27 |  |  | 42960.1875 | 41 | 41
2017-08-13 05:00 | 33 | 28 |  |  | 42960.2083 | 41 | 41
2017-08-13 05:30 | 32 | 27 |  |  | 42960.2292 | 42 | 42
2017-08-13 06:00 | 32 | 27 |  |  | 42960.25 | 43 | 43
2017-08-13 06:30 | 33 | 28 |  |  | 42960.2708 | 45 | 45
2017-08-13 07:00 | 35 | 30 |  |  | 42960.2917 | 46 | 46
2017-08-13 07:30 | 40 | 36 |  |  | 42960.3125 | 55 | 55
2017-08-13 08:00 | 41 | 38 |  |  | 42960.3333 | 57 | 57
2017-08-13 08:30 | 43 | 39 |  |  | 42960.3542 | 59 | 58
2017-08-13 09:00 | 44 | 40 |  |  | 42960.375 | 59 | 59
2017-08-13 09:30 | 45 | 41 |  |  | 42960.3958 | 59 | 59
2017-08-13 10:00 | 46 | 42 |  |  | 42960.4167 | 61 | 61
2017-08-13 10:30 | 47 | 42 |  |  | 42960.4375 | 59 | 59
2017-08-13 11:00 | 46 | 42 |  |  | 42960.4583 | 60 | 60
2017-08-13 11:30 | 47 | 42 |  |  | 42960.4792 | 59 | 59
2017-08-13 12:00 | 47 | 42 |  |  | 42960.5 | 60 | 60
2017-08-13 12:30 | 41 | 34 |  |  | 42960.5208 | 52 | 52
2017-08-13 13:00 | 40 | 33 |  |  | 42960.5417 | 50 | 50
2017-08-13 13:30 | 40 | 34 |  |  | 42960.5625 | 52 | 51
2017-08-13 14:00 | 43 | 36 |  |  | 42960.5833 | 53 | 52
2017-08-13 14:30 | 44 | 38 |  |  | 42960.6042 | 55 | 54
2017-08-13 15:00 | 46 | 40 |  |  | 42960.625 | 57 | 57
2017-08-13 15:30 | 46 | 40 |  |  | 42960.6458 | 58 | 58
2017-08-13 16:00 | 46 | 41 |  |  | 42960.6667 | 59 | 59
2017-08-13 16:30 | 48 | 43 |  |  | 42960.6875 | 62 | 61
2017-08-13 17:00 | 52 | 47 |  |  | 42960.7083 | 67 | 66
2017-08-13 17:30 | 55 | 51 |  |  | 42960.7292 | 69 | 69
2017-08-13 18:00 | 60 | 56 |  |  | 42960.75 | 73 | 73
2017-08-13 18:30 | 62 | 59 |  |  | 42960.7708 | 77 | 77
2017-08-13 19:00 | 62 | 60 |  |  | 42960.7917 | 78 | 78
2017-08-13 19:30 | 60 | 58 |  |  | 42960.8125 | 75 | 75
2017-08-13 20:00 | 58 | 55 |  |  | 42960.8333 | 75 | 75
2017-08-13 20:30 | 60 | 57 |  |  | 42960.8542 | 75 | 75
2017-08-13 21:00 | 56 | 52 |  |  | 42960.875 | 71 | 71
2017-08-13 21:30 | 52 | 49 |  |  | 42960.8958 | 67 | 67
2017-08-13 22:00 | 50 | 47 |  |  | 42960.9167 | 66 | 66
2017-08-13 22:30 | 51 | 48 |  |  | 42960.9375 | 68 | 68
2017-08-13 23:00 | 50 | 46 |  |  | 42960.9583 | 66 | 66
2017-08-13 23:30 | 45 | 42 |  |  | 42960.9792 | 59 | 59
2017-08-14 | 40 | 37 |  |  | 42961 | 54 | 54
2017-08-14 00:30 | 36 | 33 |  |  | 42961.0208 | 49 | 49
2017-08-14 01:00 | 35 | 32 |  |  | 42961.0417 | 47 | 47
2017-08-14 01:30 | 34 | 31 |  |  | 42961.0625 | 46 | 46
2017-08-14 02:00 | 35 | 30 |  |  | 42961.0833 | 45 | 45
2017-08-14 02:30 | 35 | 30 |  |  | 42961.1042 | 44 | 44
2017-08-14 03:00 | 35 | 30 |  |  | 42961.125 | 44 | 44
2017-08-14 03:30 | 35 | 31 |  |  | 42961.1458 | 44 | 44
2017-08-14 04:00 | 35 | 30 |  |  | 42961.1667 | 43 | 43
2017-08-14 04:30 | 35 | 31 |  |  | 42961.1875 | 43 | 43
2017-08-14 05:00 | 37 | 32 |  |  | 42961.2083 | 46 | 46
2017-08-14 05:30 | 40 | 35 |  |  | 42961.2292 | 49 | 49
2017-08-14 06:00 | 46 | 41 |  |  | 42961.25 | 55 | 55
2017-08-14 06:30 | 55 | 50 |  |  | 42961.2708 | 67 | 66
2017-08-14 07:00 | 56 | 49 |  |  | 42961.2917 | 72 | 72
2017-08-14 07:30 | 57 | 54 |  |  | 42961.3125 | 80 | 80
2017-08-14 08:00 | 56 | 55 |  |  | 42961.3333 | 85 | 85
2017-08-14 08:30 | 54 | 53 |  |  | 42961.3542 | 82 | 82
2017-08-14 09:00 | 52 | 51 |  |  | 42961.375 | 80 | 80
2017-08-14 09:30 | 51 | 51 |  |  | 42961.3958 | 77 | 77
2017-08-14 10:00 | 50 | 50 |  |  | 42961.4167 | 77 | 77
2017-08-14 10:30 | 47 | 47 |  |  | 42961.4375 | 75 | 74
2017-08-14 11:00 | 48 | 48 |  |  | 42961.4583 | 77 | 75
2017-08-14 11:30 | 48 | 48 |  |  | 42961.4792 | 76 | 74
2017-08-14 12:00 | 47 | 47 |  |  | 42961.5 | 74 | 72
2017-08-14 12:30 | 47 | 47 |  |  | 42961.5208 | 75 | 73
2017-08-14 13:00 | 44 | 44 |  |  | 42961.5417 | 73 | 70
2017-08-14 13:30 | 50 | 50 |  |  | 42961.5625 | 75 | 72
2017-08-14 14:00 | 51 | 51 |  |  | 42961.5833 | 76 | 74
2017-08-14 14:30 | 51 | 51 |  |  | 42961.6042 | 81 | 79
2017-08-14 15:00 | 53 | 53 |  |  | 42961.625 | 79 | 77
2017-08-14 15:30 | 52 | 52 |  |  | 42961.6458 | 77 | 75
2017-08-14 16:00 | 59 | 59 |  |  | 42961.6667 | 83 | 81
2017-08-14 16:30 | 61 | 61 |  |  | 42961.6875 | 85 | 84
2017-08-14 17:00 | 68 | 67 |  |  | 42961.7083 | 91 | 90
2017-08-14 17:30 | 72 | 71 |  |  | 42961.7292 | 93 | 92
2017-08-14 18:00 | 73 | 73 |  |  | 42961.75 | 93 | 93
2017-08-14 18:30 | 73 | 72 |  |  | 42961.7708 | 91 | 91
2017-08-14 19:00 | 74 | 73 |  |  | 42961.7917 | 93 | 93
2017-08-14 19:30 | 71 | 71 |  |  | 42961.8125 | 91 | 90
2017-08-14 20:00 | 69 | 69 |  |  | 42961.8333 | 89 | 88
2017-08-14 20:30 | 68 | 67 |  |  | 42961.8542 | 88 | 87
2017-08-14 21:00 | 65 | 64 |  |  | 42961.875 | 83 | 82
2017-08-14 21:30 | 61 | 61 |  |  | 42961.8958 | 80 | 78
2017-08-14 22:00 | 60 | 60 |  |  | 42961.9167 | 79 | 78
2017-08-14 22:30 | 56 | 56 |  |  | 42961.9375 | 75 | 74
2017-08-14 23:00 | 50 | 50 |  |  | 42961.9583 | 68 | 67
2017-08-14 23:30 | 46 | 46 |  |  | 42961.9792 | 64 | 63
2017-08-15 | 41 | 41 |  |  | 42962 | 59 | 59
2017-08-15 00:30 | 38 | 38 |  |  | 42962.0208 | 54 | 54
2017-08-15 01:00 | 35 | 35 |  |  | 42962.0417 | 50 | 50
2017-08-15 01:30 | 32 | 31 |  |  | 42962.0625 | 46 | 46
2017-08-15 02:00 | 31 | 30 |  |  | 42962.0833 | 45 | 44
2017-08-15 02:30 | 33 | 32 |  |  | 42962.1042 | 46 | 46
2017-08-15 03:00 | 34 | 34 |  |  | 42962.125 | 48 | 48
2017-08-15 03:30 | 36 | 35 |  |  | 42962.1458 | 49 | 49
2017-08-15 04:00 | 36 | 36 |  |  | 42962.1667 | 49 | 49
2017-08-15 04:30 | 38 | 37 |  |  | 42962.1875 | 51 | 51
2017-08-15 05:00 | 36 | 36 |  |  | 42962.2083 | 51 | 51
2017-08-15 05:30 | 39 | 39 |  |  | 42962.2292 | 54 | 54
2017-08-15 06:00 | 45 | 45 |  |  | 42962.25 | 61 | 60
2017-08-15 06:30 | 50 | 50 |  |  | 42962.2708 | 71 | 70
2017-08-15 07:00 | 51 | 51 |  |  | 42962.2917 | 79 | 78
2017-08-15 07:30 | 57 | 55 |  |  | 42962.3125 | 88 | 86
2017-08-15 08:00 | 57 | 54 |  |  | 42962.3333 | 88 | 85
2017-08-15 08:30 | 54 | 52 |  |  | 42962.3542 | 86 | 83
2017-08-15 09:00 | 52 | 49 |  |  | 42962.375 | 82 | 79
2017-08-15 09:30 | 52 | 49 |  |  | 42962.3958 | 80 | 77
2017-08-15 10:00 | 51 | 48 |  |  | 42962.4167 | 80 | 76
2017-08-15 10:30 | 50 | 47 |  |  | 42962.4375 | 77 | 73
2017-08-15 11:00 | 50 | 47 |  |  | 42962.4583 | 77 | 73
2017-08-15 11:30 | 51 | 47 |  |  | 42962.4792 | 77 | 72
2017-08-15 12:00 | 51 | 48 |  |  | 42962.5 | 77 | 73
2017-08-15 12:30 | 51 | 47 |  |  | 42962.5208 | 78 | 73
2017-08-15 13:00 | 51 | 49 |  |  | 42962.5417 | 79 | 74
2017-08-15 13:30 | 52 | 50 |  |  | 42962.5625 | 81 | 76
2017-08-15 14:00 | 54 | 52 |  |  | 42962.5833 | 82 | 77
2017-08-15 14:30 | 54 | 53 |  |  | 42962.6042 | 81 | 79
2017-08-15 15:00 | 52 | 52 |  |  | 42962.625 | 79 | 79
2017-08-15 15:30 | 51 | 51 |  |  | 42962.6458 | 78 | 77
2017-08-15 16:00 | 55 | 55 |  |  | 42962.6667 | 80 | 79
2017-08-15 16:30 | 63 | 63 |  |  | 42962.6875 | 86 | 85
2017-08-15 17:00 | 67 | 67 |  |  | 42962.7083 | 88 | 88
2017-08-15 17:30 | 68 | 68 |  |  | 42962.7292 | 90 | 89
2017-08-15 18:00 | 71 | 71 |  |  | 42962.75 | 92 | 92
2017-08-15 18:30 | 71 | 71 |  |  | 42962.7708 | 91 | 91
2017-08-15 19:00 | 72 | 72 |  |  | 42962.7917 | 92 | 92
2017-08-15 19:30 | 70 | 70 |  |  | 42962.8125 | 89 | 89
2017-08-15 20:00 | 66 | 66 |  |  | 42962.8333 | 86 | 86
2017-08-15 20:30 | 67 | 66 |  |  | 42962.8542 | 86 | 86
2017-08-15 21:00 | 62 | 61 |  |  | 42962.875 | 80 | 80
2017-08-15 21:30 | 57 | 57 |  |  | 42962.8958 | 75 | 75
2017-08-15 22:00 | 56 | 56 |  |  | 42962.9167 | 73 | 73
2017-08-15 22:30 | 52 | 52 |  |  | 42962.9375 | 70 | 70
2017-08-15 23:00 | 51 | 50 |  |  | 42962.9583 | 67 | 67
2017-08-15 23:30 | 46 | 45 |  |  | 42962.9792 | 63 | 62
2017-08-16 | 42 | 40 |  |  | 42963 | 58 | 58
2017-08-16 00:30 | 37 | 36 |  |  | 42963.0208 | 52 | 51
2017-08-16 01:00 | 34 | 32 |  |  | 42963.0417 | 47 | 47
2017-08-16 01:30 | 34 | 32 |  |  | 42963.0625 | 45 | 44
2017-08-16 02:00 | 35 | 32 |  |  | 42963.0833 | 45 | 44
2017-08-16 02:30 | 38 | 36 |  |  | 42963.1042 | 49 | 48
2017-08-16 03:00 | 41 | 38 |  |  | 42963.125 | 52 | 51
2017-08-16 03:30 | 43 | 40 |  |  | 42963.1458 | 55 | 53
2017-08-16 04:00 | 43 | 40 |  |  | 42963.1667 | 55 | 53
2017-08-16 04:30 | 46 | 43 |  |  | 42963.1875 | 56 | 55
2017-08-16 05:00 | 46 | 44 |  |  | 42963.2083 | 57 | 56
2017-08-16 05:30 | 45 | 43 |  |  | 42963.2292 | 56 | 55
2017-08-16 06:00 | 46 | 45 |  |  | 42963.25 | 58 | 57
2017-08-16 06:30 | 46 | 45 |  |  | 42963.2708 | 59 | 59
2017-08-16 07:00 | 45 | 44 |  |  | 42963.2917 | 60 | 60
2017-08-16 07:30 | 46 | 45 |  |  | 42963.3125 | 62 | 62
2017-08-16 08:00 | 47 | 47 |  |  | 42963.3333 | 64 | 64
2017-08-16 08:30 | 48 | 47 |  |  | 42963.3542 | 64 | 64
2017-08-16 09:00 | 46 | 46 |  |  | 42963.375 | 64 | 64
2017-08-16 09:30 | 44 | 44 |  |  | 42963.3958 | 63 | 63
2017-08-16 10:00 | 44 | 43 |  |  | 42963.4167 | 62 | 62
2017-08-16 10:30 | 45 | 45 |  |  | 42963.4375 | 65 | 65
2017-08-16 11:00 | 44 | 44 |  |  | 42963.4583 | 63 | 63
2017-08-16 11:30 | 44 | 44 |  |  | 42963.4792 | 62 | 62
2017-08-16 12:00 | 44 | 44 |  |  | 42963.5 | 62 | 62
2017-08-16 12:30 | 47 | 47 |  |  | 42963.5208 | 65 | 65
2017-08-16 13:00 | 47 | 46 |  |  | 42963.5417 | 64 | 64
2017-08-16 13:30 | 47 | 46 |  |  | 42963.5625 | 64 | 63
2017-08-16 14:00 | 47 | 47 |  |  | 42963.5833 | 65 | 64
2017-08-16 14:30 | 50 | 50 |  |  | 42963.6042 | 67 | 67
2017-08-16 15:00 | 51 | 51 |  |  | 42963.625 | 69 | 69
2017-08-16 15:30 | 56 | 55 |  |  | 42963.6458 | 72 | 71
2017-08-16 16:00 | 58 | 56 |  |  | 42963.6667 | 73 | 72
2017-08-16 16:30 | 60 | 58 |  |  | 42963.6875 | 77 | 76
2017-08-16 17:00 | 65 | 63 |  |  | 42963.7083 | 82 | 81
2017-08-16 17:30 | 70 | 67 |  |  | 42963.7292 | 86 | 84
2017-08-16 18:00 | 72 | 70 |  |  | 42963.75 | 90 | 88
2017-08-16 18:30 | 74 | 74 |  |  | 42963.7708 | 92 | 91
2017-08-16 19:00 | 74 | 74 |  |  | 42963.7917 | 93 | 92
2017-08-16 19:30 | 73 | 72 |  |  | 42963.8125 | 90 | 89
2017-08-16 20:00 | 70 | 70 |  |  | 42963.8333 | 88 | 87
2017-08-16 20:30 | 69 | 69 |  |  | 42963.8542 | 87 | 86
2017-08-16 21:00 | 66 | 66 |  |  | 42963.875 | 82 | 81
2017-08-16 21:30 | 63 | 62 |  |  | 42963.8958 | 79 | 78
2017-08-16 22:00 | 60 | 58 |  |  | 42963.9167 | 77 | 75
2017-08-16 22:30 | 58 | 56 |  |  | 42963.9375 | 75 | 73
2017-08-16 23:00 | 58 | 55 |  |  | 42963.9583 | 75 | 73
2017-08-16 23:30 | 54 | 51 |  |  | 42963.9792 | 71 | 69
2017-08-17 | 48 | 45 |  |  | 42964 | 64 | 61
2017-08-17 00:30 | 44 | 41 |  |  | 42964.0208 | 59 | 56
2017-08-17 01:00 | 41 | 38 |  |  | 42964.0417 | 55 | 51
2017-08-17 01:30 | 39 | 35 |  |  | 42964.0625 | 52 | 49
2017-08-17 02:00 | 40 | 36 |  |  | 42964.0833 | 53 | 49
2017-08-17 02:30 | 42 | 38 |  |  | 42964.1042 | 54 | 50
2017-08-17 03:00 | 42 | 38 |  |  | 42964.125 | 54 | 51
2017-08-17 03:30 | 43 | 40 |  |  | 42964.1458 | 55 | 52
2017-08-17 04:00 | 44 | 41 |  |  | 42964.1667 | 55 | 52
2017-08-17 04:30 | 44 | 42 |  |  | 42964.1875 | 56 | 54
2017-08-17 05:00 | 46 | 44 |  |  | 42964.2083 | 59 | 56
2017-08-17 05:30 | 48 | 47 |  |  | 42964.2292 | 61 | 60
2017-08-17 06:00 | 49 | 49 |  |  | 42964.25 | 63 | 62
2017-08-17 06:30 | 53 | 53 |  |  | 42964.2708 | 71 | 71
2017-08-17 07:00 | 60 | 60 |  |  | 42964.2917 | 80 | 80
2017-08-17 07:30 | 65 | 65 |  |  | 42964.3125 | 88 | 88
2017-08-17 08:00 | 65 | 65 |  |  | 42964.3333 | 90 | 90
2017-08-17 08:30 | 62 | 62 |  |  | 42964.3542 | 88 | 87
2017-08-17 09:00 | 57 | 57 |  |  | 42964.375 | 84 | 84
2017-08-17 09:30 | 56 | 55 |  |  | 42964.3958 | 82 | 82
2017-08-17 10:00 | 53 | 53 |  |  | 42964.4167 | 80 | 80
2017-08-17 10:30 | 53 | 53 |  |  | 42964.4375 | 79 | 79
2017-08-17 11:00 | 53 | 53 |  |  | 42964.4583 | 78 | 78
2017-08-17 11:30 | 55 | 55 |  |  | 42964.4792 | 80 | 80
2017-08-17 12:00 | 55 | 55 |  |  | 42964.5 | 81 | 81
2017-08-17 12:30 | 55 | 55 |  |  | 42964.5208 | 82 | 82
2017-08-17 13:00 | 57 | 57 |  |  | 42964.5417 | 83 | 83
2017-08-17 13:30 | 59 | 59 |  |  | 42964.5625 | 85 | 85
2017-08-17 14:00 | 62 | 62 |  |  | 42964.5833 | 87 | 87
2017-08-17 14:30 | 64 | 64 |  |  | 42964.6042 | 91 | 91
2017-08-17 15:00 | 66 | 66 |  |  | 42964.625 | 93 | 93
2017-08-17 15:30 | 67 | 67 |  |  | 42964.6458 | 93 | 93
2017-08-17 16:00 | 67 | 67 |  |  | 42964.6667 | 96 | 94
2017-08-17 16:30 | 71 | 69 |  |  | 42964.6875 | 102 | 97
2017-08-17 17:00 | 71 | 68 |  |  | 42964.7083 | 101 | 96
2017-08-17 17:30 | 71 | 69 |  |  | 42964.7292 | 100 | 95
2017-08-17 18:00 | 76 | 74 |  |  | 42964.75 | 103 | 98
2017-08-17 18:30 | 76 | 74 |  |  | 42964.7708 | 103 | 98
2017-08-17 19:00 | 77 | 75 |  |  | 42964.7917 | 104 | 99
2017-08-17 19:30 | 74 | 71 |  |  | 42964.8125 | 100 | 94
2017-08-17 20:00 | 68 | 68 |  |  | 42964.8333 | 89 | 89
2017-08-17 20:30 | 65 | 65 |  |  | 42964.8542 | 86 | 86
2017-08-17 21:00 | 60 | 60 |  |  | 42964.875 | 80 | 80
2017-08-17 21:30 | 56 | 56 |  |  | 42964.8958 | 77 | 76
2017-08-17 22:00 | 53 | 53 |  |  | 42964.9167 | 74 | 73
2017-08-17 22:30 | 56 | 55 |  |  | 42964.9375 | 75 | 75
2017-08-17 23:00 | 54 | 53 |  |  | 42964.9583 | 73 | 73
2017-08-17 23:30 | 48 | 48 |  |  | 42964.9792 | 67 | 67
2017-08-18 | 44 | 43 |  |  | 42965 | 61 | 61
2017-08-18 00:30 | 40 | 39 |  |  | 42965.0208 | 56 | 56
2017-08-18 01:00 | 38 | 36 |  |  | 42965.0417 | 53 | 51
2017-08-18 01:30 | 37 | 35 |  |  | 42965.0625 | 50 | 48
2017-08-18 02:00 | 37 | 35 |  |  | 42965.0833 | 50 | 49
2017-08-18 02:30 | 38 | 35 |  |  | 42965.1042 | 50 | 49
2017-08-18 03:00 | 37 | 35 |  |  | 42965.125 | 50 | 49
2017-08-18 03:30 | 37 | 35 |  |  | 42965.1458 | 49 | 48
2017-08-18 04:00 | 38 | 36 |  |  | 42965.1667 | 51 | 50
2017-08-18 04:30 | 39 | 37 |  |  | 42965.1875 | 52 | 51
2017-08-18 05:00 | 39 | 37 |  |  | 42965.2083 | 53 | 52
2017-08-18 05:30 | 39 | 38 |  |  | 42965.2292 | 54 | 53
2017-08-18 06:00 | 43 | 43 |  |  | 42965.25 | 60 | 59
2017-08-18 06:30 | 49 | 49 |  |  | 42965.2708 | 69 | 69
2017-08-18 07:00 | 55 | 55 |  |  | 42965.2917 | 80 | 80
2017-08-18 07:30 | 57 | 57 |  |  | 42965.3125 | 83 | 83
2017-08-18 08:00 | 57 | 57 |  |  | 42965.3333 | 84 | 84
2017-08-18 08:30 | 56 | 56 |  |  | 42965.3542 | 84 | 83
2017-08-18 09:00 | 51 | 51 |  |  | 42965.375 | 77 | 77
2017-08-18 09:30 | 48 | 48 |  |  | 42965.3958 | 75 | 75
2017-08-18 10:00 | 47 | 47 |  |  | 42965.4167 | 74 | 73
2017-08-18 10:30 | 47 | 47 |  |  | 42965.4375 | 73 | 72
2017-08-18 11:00 | 49 | 49 |  |  | 42965.4583 | 75 | 74
2017-08-18 11:30 | 51 | 51 |  |  | 42965.4792 | 78 | 77
2017-08-18 12:00 | 50 | 50 |  |  | 42965.5 | 78 | 76
2017-08-18 12:30 | 51 | 51 |  |  | 42965.5208 | 76 | 75
2017-08-18 13:00 | 50 | 50 |  |  | 42965.5417 | 76 | 74
2017-08-18 13:30 | 50 | 50 |  |  | 42965.5625 | 76 | 75
2017-08-18 14:00 | 50 | 50 |  |  | 42965.5833 | 75 | 75
2017-08-18 14:30 | 52 | 52 |  |  | 42965.6042 | 76 | 76
2017-08-18 15:00 | 50 | 50 |  |  | 42965.625 | 76 | 76
2017-08-18 15:30 | 52 | 52 |  |  | 42965.6458 | 77 | 77
2017-08-18 16:00 | 54 | 54 |  |  | 42965.6667 | 78 | 78
2017-08-18 16:30 | 55 | 55 |  |  | 42965.6875 | 80 | 80
2017-08-18 17:00 | 59 | 59 |  |  | 42965.7083 | 82 | 82
2017-08-18 17:30 | 61 | 61 |  |  | 42965.7292 | 84 | 84
2017-08-18 18:00 | 58 | 58 |  |  | 42965.75 | 80 | 80
2017-08-18 18:30 | 58 | 58 |  |  | 42965.7708 | 79 | 79
2017-08-18 19:00 | 56 | 56 |  |  | 42965.7917 | 77 | 77
2017-08-18 19:30 | 54 | 53 |  |  | 42965.8125 | 75 | 74
2017-08-18 20:00 | 53 | 53 |  |  | 42965.8333 | 73 | 73
2017-08-18 20:30 | 53 | 52 |  |  | 42965.8542 | 72 | 72
2017-08-18 21:00 | 50 | 50 |  |  | 42965.875 | 70 | 70
2017-08-18 21:30 | 47 | 47 |  |  | 42965.8958 | 65 | 65
2017-08-18 22:00 | 47 | 46 |  |  | 42965.9167 | 66 | 65
2017-08-18 22:30 | 47 | 46 |  |  | 42965.9375 | 66 | 66
2017-08-18 23:00 | 47 | 47 |  |  | 42965.9583 | 65 | 65
2017-08-18 23:30 | 43 | 42 |  |  | 42965.9792 | 62 | 62
2017-08-19 | 41 | 40 |  |  | 42966 | 58 | 58
2017-08-19 00:30 | 38 | 37 |  |  | 42966.0208 | 53 | 53
2017-08-19 01:00 | 35 | 34 |  |  | 42966.0417 | 49 | 48
2017-08-19 01:30 | 33 | 31 |  |  | 42966.0625 | 47 | 46
2017-08-19 02:00 | 32 | 30 |  |  | 42966.0833 | 45 | 44
2017-08-19 02:30 | 32 | 30 |  |  | 42966.1042 | 43 | 43
2017-08-19 03:00 | 32 | 30 |  |  | 42966.125 | 44 | 43
2017-08-19 03:30 | 33 | 31 |  |  | 42966.1458 | 44 | 43
2017-08-19 04:00 | 33 | 31 |  |  | 42966.1667 | 45 | 45
2017-08-19 04:30 | 33 | 32 |  |  | 42966.1875 | 45 | 45
2017-08-19 05:00 | 34 | 32 |  |  | 42966.2083 | 46 | 46
2017-08-19 05:30 | 34 | 33 |  |  | 42966.2292 | 47 | 46
2017-08-19 06:00 | 34 | 33 |  |  | 42966.25 | 48 | 48
2017-08-19 06:30 | 36 | 35 |  |  | 42966.2708 | 51 | 51
2017-08-19 07:00 | 37 | 37 |  |  | 42966.2917 | 54 | 54
2017-08-19 07:30 | 38 | 38 |  |  | 42966.3125 | 55 | 55
2017-08-19 08:00 | 38 | 38 |  |  | 42966.3333 | 56 | 56
2017-08-19 08:30 | 41 | 41 |  |  | 42966.3542 | 59 | 59
2017-08-19 09:00 | 38 | 38 |  |  | 42966.375 | 54 | 54
2017-08-19 09:30 | 37 | 37 |  |  | 42966.3958 | 53 | 53
2017-08-19 10:00 | 37 | 36 |  |  | 42966.4167 | 52 | 52
2017-08-19 10:30 | 36 | 36 |  |  | 42966.4375 | 51 | 51
2017-08-19 11:00 | 36 | 35 |  |  | 42966.4583 | 51 | 51
2017-08-19 11:30 | 36 | 36 |  |  | 42966.4792 | 51 | 50
2017-08-19 12:00 | 36 | 36 |  |  | 42966.5 | 51 | 51
2017-08-19 12:30 | 35 | 35 |  |  | 42966.5208 | 51 | 51
2017-08-19 13:00 | 36 | 36 |  |  | 42966.5417 | 50 | 50
2017-08-19 13:30 | 36 | 36 |  |  | 42966.5625 | 51 | 51
2017-08-19 14:00 | 36 | 36 |  |  | 42966.5833 | 50 | 50
2017-08-19 14:30 | 36 | 36 |  |  | 42966.6042 | 50 | 50
2017-08-19 15:00 | 38 | 38 |  |  | 42966.625 | 52 | 52
2017-08-19 15:30 | 40 | 40 |  |  | 42966.6458 | 58 | 58
2017-08-19 16:00 | 42 | 42 |  |  | 42966.6667 | 60 | 60
2017-08-19 16:30 | 43 | 42 |  |  | 42966.6875 | 62 | 61
2017-08-19 17:00 | 44 | 44 |  |  | 42966.7083 | 64 | 64
2017-08-19 17:30 | 47 | 46 |  |  | 42966.7292 | 66 | 66
2017-08-19 18:00 | 49 | 49 |  |  | 42966.75 | 69 | 69
2017-08-19 18:30 | 51 | 51 |  |  | 42966.7708 | 72 | 72
2017-08-19 19:00 | 52 | 51 |  |  | 42966.7917 | 74 | 74
2017-08-19 19:30 | 52 | 51 |  |  | 42966.8125 | 74 | 74
2017-08-19 20:00 | 52 | 51 |  |  | 42966.8333 | 72 | 72
2017-08-19 20:30 | 51 | 50 |  |  | 42966.8542 | 71 | 71
2017-08-19 21:00 | 50 | 49 |  |  | 42966.875 | 68 | 68
2017-08-19 21:30 | 46 | 46 |  |  | 42966.8958 | 65 | 65
2017-08-19 22:00 | 47 | 46 |  |  | 42966.9167 | 66 | 65
2017-08-19 22:30 | 48 | 48 |  |  | 42966.9375 | 69 | 69
2017-08-19 23:00 | 46 | 45 |  |  | 42966.9583 | 64 | 64
2017-08-19 23:30 | 43 | 42 |  |  | 42966.9792 | 60 | 60
2017-08-20 | 42 | 41 |  |  | 42967 | 59 | 59
2017-08-20 00:30 | 39 | 38 |  |  | 42967.0208 | 54 | 54
2017-08-20 01:00 | 37 | 36 |  |  | 42967.0417 | 52 | 51
2017-08-20 01:30 | 35 | 34 |  |  | 42967.0625 | 49 | 48
2017-08-20 02:00 | 36 | 34 |  |  | 42967.0833 | 48 | 47
2017-08-20 02:30 | 35 | 33 |  |  | 42967.1042 | 48 | 46
2017-08-20 03:00 | 35 | 33 |  |  | 42967.125 | 46 | 45
2017-08-20 03:30 | 35 | 33 |  |  | 42967.1458 | 45 | 44
2017-08-20 04:00 | 35 | 32 |  |  | 42967.1667 | 46 | 45
2017-08-20 04:30 | 35 | 32 |  |  | 42967.1875 | 46 | 45
2017-08-20 05:00 | 34 | 32 |  |  | 42967.2083 | 46 | 44
2017-08-20 05:30 | 34 | 32 |  |  | 42967.2292 | 47 | 46
2017-08-20 06:00 | 34 | 32 |  |  | 42967.25 | 47 | 46
2017-08-20 06:30 | 34 | 32 |  |  | 42967.2708 | 48 | 47
2017-08-20 07:00 | 34 | 32 |  |  | 42967.2917 | 50 | 49
2017-08-20 07:30 | 36 | 34 |  |  | 42967.3125 | 53 | 53
2017-08-20 08:00 | 39 | 37 |  |  | 42967.3333 | 57 | 57
2017-08-20 08:30 | 41 | 40 |  |  | 42967.3542 | 60 | 60
2017-08-20 09:00 | 42 | 40 |  |  | 42967.375 | 61 | 61
2017-08-20 09:30 | 42 | 41 |  |  | 42967.3958 | 61 | 61
2017-08-20 10:00 | 42 | 41 |  |  | 42967.4167 | 60 | 60
2017-08-20 10:30 | 42 | 40 |  |  | 42967.4375 | 59 | 58
2017-08-20 11:00 | 41 | 39 |  |  | 42967.4583 | 57 | 56
2017-08-20 11:30 | 40 | 39 |  |  | 42967.4792 | 57 | 56
2017-08-20 12:00 | 41 | 40 |  |  | 42967.5 | 58 | 58
2017-08-20 12:30 | 41 | 39 |  |  | 42967.5208 | 60 | 60
2017-08-20 13:00 | 41 | 40 |  |  | 42967.5417 | 60 | 59
2017-08-20 13:30 | 42 | 40 |  |  | 42967.5625 | 61 | 60
2017-08-20 14:00 | 43 | 41 |  |  | 42967.5833 | 62 | 61
2017-08-20 14:30 | 44 | 42 |  |  | 42967.6042 | 63 | 62
2017-08-20 15:00 | 44 | 43 |  |  | 42967.625 | 64 | 63
2017-08-20 15:30 | 44 | 43 |  |  | 42967.6458 | 64 | 63
2017-08-20 16:00 | 45 | 43 |  |  | 42967.6667 | 65 | 65
2017-08-20 16:30 | 45 | 44 |  |  | 42967.6875 | 63 | 63
2017-08-20 17:00 | 46 | 46 |  |  | 42967.7083 | 65 | 65
2017-08-20 17:30 | 49 | 48 |  |  | 42967.7292 | 68 | 68
2017-08-20 18:00 | 53 | 52 |  |  | 42967.75 | 73 | 72
2017-08-20 18:30 | 57 | 55 |  |  | 42967.7708 | 78 | 75
2017-08-20 19:00 | 59 | 57 |  |  | 42967.7917 | 81 | 79
2017-08-20 19:30 | 59 | 57 |  |  | 42967.8125 | 80 | 77
2017-08-20 20:00 | 56 | 53 |  |  | 42967.8333 | 78 | 75
2017-08-20 20:30 | 55 | 53 |  |  | 42967.8542 | 77 | 74
2017-08-20 21:00 | 53 | 51 |  |  | 42967.875 | 74 | 71
2017-08-20 21:30 | 50 | 48 |  |  | 42967.8958 | 70 | 69
2017-08-20 22:00 | 49 | 48 |  |  | 42967.9167 | 69 | 68
2017-08-20 22:30 | 50 | 49 |  |  | 42967.9375 | 71 | 70
2017-08-20 23:00 | 49 | 47 |  |  | 42967.9583 | 68 | 67
2017-08-20 23:30 | 45 | 43 |  |  | 42967.9792 | 62 | 62
2017-08-21 | 42 | 40 |  |  | 42968 | 60 | 58
2017-08-21 00:30 | 39 | 36 |  |  | 42968.0208 | 54 | 53
2017-08-21 01:00 | 35 | 33 |  |  | 42968.0417 | 50 | 49
2017-08-21 01:30 | 35 | 32 |  |  | 42968.0625 | 48 | 47
2017-08-21 02:00 | 35 | 32 |  |  | 42968.0833 | 47 | 46
2017-08-21 02:30 | 34 | 31 |  |  | 42968.1042 | 48 | 46
2017-08-21 03:00 | 34 | 32 |  |  | 42968.125 | 47 | 46
2017-08-21 03:30 | 34 | 32 |  |  | 42968.1458 | 46 | 45
2017-08-21 04:00 | 34 | 32 |  |  | 42968.1667 | 46 | 46
2017-08-21 04:30 | 35 | 33 |  |  | 42968.1875 | 48 | 47
2017-08-21 05:00 | 36 | 35 |  |  | 42968.2083 | 49 | 49
2017-08-21 05:30 | 41 | 41 |  |  | 42968.2292 | 55 | 55
2017-08-21 06:00 | 49 | 49 |  |  | 42968.25 | 65 | 65
2017-08-21 06:30 | 57 | 57 |  |  | 42968.2708 | 75 | 75
2017-08-21 07:00 | 63 | 63 |  |  | 42968.2917 | 86 | 86
2017-08-21 07:30 | 69 | 69 |  |  | 42968.3125 | 94 | 94
2017-08-21 08:00 | 68 | 67 |  |  | 42968.3333 | 94 | 94
2017-08-21 08:30 | 64 | 64 |  |  | 42968.3542 | 92 | 92
2017-08-21 09:00 | 61 | 61 |  |  | 42968.375 | 86 | 86
2017-08-21 09:30 | 57 | 57 |  |  | 42968.3958 | 81 | 81
2017-08-21 10:00 | 55 | 55 |  |  | 42968.4167 | 78 | 78
2017-08-21 10:30 | 54 | 54 |  |  | 42968.4375 | 76 | 76
2017-08-21 11:00 | 53 | 53 |  |  | 42968.4583 | 75 | 75
2017-08-21 11:30 | 52 | 52 |  |  | 42968.4792 | 73 | 73
2017-08-21 12:00 | 53 | 53 |  |  | 42968.5 | 74 | 74
2017-08-21 12:30 | 52 | 52 |  |  | 42968.5208 | 75 | 75
2017-08-21 13:00 | 52 | 52 |  |  | 42968.5417 | 77 | 77
2017-08-21 13:30 | 54 | 54 |  |  | 42968.5625 | 80 | 80
2017-08-21 14:00 | 56 | 56 |  |  | 42968.5833 | 77 | 77
2017-08-21 14:30 | 54 | 54 |  |  | 42968.6042 | 75 | 75
2017-08-21 15:00 | 55 | 55 |  |  | 42968.625 | 76 | 76
2017-08-21 15:30 | 58 | 57 |  |  | 42968.6458 | 80 | 80
2017-08-21 16:00 | 59 | 59 |  |  | 42968.6667 | 81 | 80
2017-08-21 16:30 | 61 | 61 |  |  | 42968.6875 | 83 | 83
2017-08-21 17:00 | 67 | 67 |  |  | 42968.7083 | 88 | 88
2017-08-21 17:30 | 71 | 71 |  |  | 42968.7292 | 91 | 91
2017-08-21 18:00 | 73 | 73 |  |  | 42968.75 | 93 | 92
2017-08-21 18:30 | 73 | 73 |  |  | 42968.7708 | 93 | 92
2017-08-21 19:00 | 73 | 73 |  |  | 42968.7917 | 93 | 92
2017-08-21 19:30 | 72 | 72 |  |  | 42968.8125 | 91 | 90
2017-08-21 20:00 | 70 | 70 |  |  | 42968.8333 | 88 | 88
2017-08-21 20:30 | 69 | 69 |  |  | 42968.8542 | 87 | 87
2017-08-21 21:00 | 67 | 66 |  |  | 42968.875 | 84 | 84
2017-08-21 21:30 | 63 | 63 |  |  | 42968.8958 | 80 | 79
2017-08-21 22:00 | 60 | 59 |  |  | 42968.9167 | 77 | 76
2017-08-21 22:30 | 60 | 59 |  |  | 42968.9375 | 76 | 75
2017-08-21 23:00 | 59 | 57 |  |  | 42968.9583 | 73 | 73
2017-08-21 23:30 | 54 | 52 |  |  | 42968.9792 | 68 | 68
2017-08-22 | 47 | 44 |  |  | 42969 | 62 | 61
2017-08-22 00:30 | 44 | 41 |  |  | 42969.0208 | 57 | 56
2017-08-22 01:00 | 41 | 37 |  |  | 42969.0417 | 53 | 52
2017-08-22 01:30 | 39 | 34 |  |  | 42969.0625 | 49 | 48
2017-08-22 02:00 | 37 | 32 |  |  | 42969.0833 | 47 | 46
2017-08-22 02:30 | 37 | 32 |  |  | 42969.1042 | 46 | 44
2017-08-22 03:00 | 36 | 31 |  |  | 42969.125 | 45 | 43
2017-08-22 03:30 | 36 | 32 |  |  | 42969.1458 | 47 | 46
2017-08-22 04:00 | 38 | 34 |  |  | 42969.1667 | 47 | 46
2017-08-22 04:30 | 39 | 35 |  |  | 42969.1875 | 49 | 47
2017-08-22 05:00 | 39 | 35 |  |  | 42969.2083 | 49 | 48
2017-08-22 05:30 | 41 | 39 |  |  | 42969.2292 | 52 | 52
2017-08-22 06:00 | 47 | 46 |  |  | 42969.25 | 61 | 60
2017-08-22 06:30 | 53 | 52 |  |  | 42969.2708 | 71 | 71
2017-08-22 07:00 | 58 | 58 |  |  | 42969.2917 | 80 | 80
2017-08-22 07:30 | 64 | 63 |  |  | 42969.3125 | 88 | 88
2017-08-22 08:00 | 60 | 59 |  |  | 42969.3333 | 87 | 86
2017-08-22 08:30 | 57 | 56 |  |  | 42969.3542 | 84 | 84
2017-08-22 09:00 | 56 | 55 |  |  | 42969.375 | 82 | 82
2017-08-22 09:30 | 55 | 54 |  |  | 42969.3958 | 78 | 78
2017-08-22 10:00 | 53 | 53 |  |  | 42969.4167 | 76 | 76
2017-08-22 10:30 | 52 | 52 |  |  | 42969.4375 | 76 | 76
2017-08-22 11:00 | 53 | 53 |  |  | 42969.4583 | 79 | 79
2017-08-22 11:30 | 51 | 51 |  |  | 42969.4792 | 76 | 76
2017-08-22 12:00 | 51 | 51 |  |  | 42969.5 | 76 | 76
2017-08-22 12:30 | 49 | 49 |  |  | 42969.5208 | 75 | 75
2017-08-22 13:00 | 52 | 52 |  |  | 42969.5417 | 77 | 77
2017-08-22 13:30 | 53 | 53 |  |  | 42969.5625 | 80 | 80
2017-08-22 14:00 | 56 | 56 |  |  | 42969.5833 | 82 | 82
2017-08-22 14:30 | 55 | 55 |  |  | 42969.6042 | 81 | 81
2017-08-22 15:00 | 56 | 56 |  |  | 42969.625 | 82 | 82
2017-08-22 15:30 | 57 | 56 |  |  | 42969.6458 | 82 | 82
2017-08-22 16:00 | 58 | 57 |  |  | 42969.6667 | 83 | 83
2017-08-22 16:30 | 59 | 59 |  |  | 42969.6875 | 85 | 84
2017-08-22 17:00 | 65 | 65 |  |  | 42969.7083 | 89 | 88
2017-08-22 17:30 | 69 | 69 |  |  | 42969.7292 | 92 | 91
2017-08-22 18:00 | 71 | 71 |  |  | 42969.75 | 93 | 93
2017-08-22 18:30 | 72 | 71 |  |  | 42969.7708 | 93 | 93
2017-08-22 19:00 | 72 | 72 |  |  | 42969.7917 | 93 | 92
2017-08-22 19:30 | 69 | 69 |  |  | 42969.8125 | 91 | 90
2017-08-22 20:00 | 68 | 68 |  |  | 42969.8333 | 88 | 87
2017-08-22 20:30 | 65 | 65 |  |  | 42969.8542 | 86 | 84
2017-08-22 21:00 | 63 | 62 |  |  | 42969.875 | 81 | 80
2017-08-22 21:30 | 61 | 61 |  |  | 42969.8958 | 79 | 78
2017-08-22 22:00 | 59 | 59 |  |  | 42969.9167 | 77 | 76
2017-08-22 22:30 | 58 | 58 |  |  | 42969.9375 | 77 | 77
2017-08-22 23:00 | 56 | 55 |  |  | 42969.9583 | 73 | 72
2017-08-22 23:30 | 52 | 51 |  |  | 42969.9792 | 68 | 68
2017-08-23 | 45 | 44 |  |  | 42970 | 62 | 62
2017-08-23 00:30 | 40 | 39 |  |  | 42970.0208 | 57 | 57
2017-08-23 01:00 | 37 | 36 |  |  | 42970.0417 | 52 | 52
2017-08-23 01:30 | 34 | 33 |  |  | 42970.0625 | 49 | 49
2017-08-23 02:00 | 35 | 33 |  |  | 42970.0833 | 49 | 48
2017-08-23 02:30 | 36 | 34 |  |  | 42970.1042 | 50 | 49
2017-08-23 03:00 | 34 | 32 |  |  | 42970.125 | 48 | 47
2017-08-23 03:30 | 35 | 34 |  |  | 42970.1458 | 48 | 47
2017-08-23 04:00 | 35 | 33 |  |  | 42970.1667 | 48 | 47
2017-08-23 04:30 | 36 | 34 |  |  | 42970.1875 | 48 | 47
2017-08-23 05:00 | 35 | 34 |  |  | 42970.2083 | 50 | 49
2017-08-23 05:30 | 40 | 40 |  |  | 42970.2292 | 54 | 54
2017-08-23 06:00 | 47 | 45 |  |  | 42970.25 | 62 | 61
2017-08-23 06:30 | 55 | 50 |  |  | 42970.2708 | 79 | 71
2017-08-23 07:00 | 63 | 59 |  |  | 42970.2917 | 90 | 81
2017-08-23 07:30 | 68 | 64 |  |  | 42970.3125 | 97 | 90
2017-08-23 08:00 | 67 | 63 |  |  | 42970.3333 | 97 | 90
2017-08-23 08:30 | 64 | 61 |  |  | 42970.3542 | 98 | 91
2017-08-23 09:00 | 46 | 43 |  |  | 42970.375 | 86 | 81
2017-08-23 09:30 | 44 | 41 |  |  | 42970.3958 | 83 | 77
2017-08-23 10:00 | 41 | 38 |  |  | 42970.4167 | 82 | 76
2017-08-23 10:30 | 43 | 40 |  |  | 42970.4375 | 80 | 74
2017-08-23 11:00 | 43 | 40 |  |  | 42970.4583 | 77 | 72
2017-08-23 11:30 | 42 | 40 |  |  | 42970.4792 | 78 | 72
2017-08-23 12:00 | 44 | 41 |  |  | 42970.5 | 79 | 74
2017-08-23 12:30 | 58 | 55 |  |  | 42970.5208 | 86 | 79
2017-08-23 13:00 | 59 | 57 |  |  | 42970.5417 | 85 | 81
2017-08-23 13:30 | 62 | 60 |  |  | 42970.5625 | 89 | 86
2017-08-23 14:00 | 63 | 61 |  |  | 42970.5833 | 89 | 85
2017-08-23 14:30 | 62 | 60 |  |  | 42970.6042 | 88 | 85
2017-08-23 15:00 | 60 | 58 |  |  | 42970.625 | 88 | 84
2017-08-23 15:30 | 59 | 57 |  |  | 42970.6458 | 87 | 84
2017-08-23 16:00 | 63 | 59 |  |  | 42970.6667 | 91 | 85
2017-08-23 16:30 | 66 | 63 |  |  | 42970.6875 | 95 | 88
2017-08-23 17:00 | 70 | 67 |  |  | 42970.7083 | 99 | 93
2017-08-23 17:30 | 72 | 68 |  |  | 42970.7292 | 101 | 94
2017-08-23 18:00 | 75 | 70 |  |  | 42970.75 | 104 | 95
2017-08-23 18:30 | 76 | 70 |  |  | 42970.7708 | 105 | 94
2017-08-23 19:00 | 78 | 71 |  |  | 42970.7917 | 106 | 94
2017-08-23 19:30 | 74 | 70 |  |  | 42970.8125 | 99 | 92
2017-08-23 20:00 | 70 | 67 |  |  | 42970.8333 | 95 | 90
2017-08-23 20:30 | 69 | 66 |  |  | 42970.8542 | 93 | 88
2017-08-23 21:00 | 62 | 62 |  |  | 42970.875 | 83 | 83
2017-08-23 21:30 | 58 | 58 |  |  | 42970.8958 | 77 | 77
2017-08-23 22:00 | 57 | 57 |  |  | 42970.9167 | 78 | 78
2017-08-23 22:30 | 56 | 56 |  |  | 42970.9375 | 79 | 79
2017-08-23 23:00 | 56 | 56 |  |  | 42970.9583 | 76 | 75
2017-08-23 23:30 | 53 | 53 |  |  | 42970.9792 | 70 | 70
2017-08-24 | 47 | 47 |  |  | 42971 | 65 | 65
2017-08-24 00:30 | 43 | 43 |  |  | 42971.0208 | 60 | 60
2017-08-24 01:00 | 39 | 39 |  |  | 42971.0417 | 54 | 54
2017-08-24 01:30 | 35 | 35 |  |  | 42971.0625 | 50 | 50
2017-08-24 02:00 | 34 | 34 |  |  | 42971.0833 | 48 | 48
2017-08-24 02:30 | 34 | 33 |  |  | 42971.1042 | 48 | 48
2017-08-24 03:00 | 33 | 33 |  |  | 42971.125 | 48 | 47
2017-08-24 03:30 | 35 | 34 |  |  | 42971.1458 | 48 | 47
2017-08-24 04:00 | 36 | 35 |  |  | 42971.1667 | 49 | 49
2017-08-24 04:30 | 38 | 37 |  |  | 42971.1875 | 51 | 51
2017-08-24 05:00 | 38 | 38 |  |  | 42971.2083 | 52 | 51
2017-08-24 05:30 | 42 | 42 |  |  | 42971.2292 | 57 | 56
2017-08-24 06:00 | 48 | 48 |  |  | 42971.25 | 63 | 63
2017-08-24 06:30 | 53 | 53 |  |  | 42971.2708 | 73 | 73
2017-08-24 07:00 | 58 | 57 |  |  | 42971.2917 | 83 | 82
2017-08-24 07:30 | 66 | 65 |  |  | 42971.3125 | 93 | 92
2017-08-24 08:00 | 65 | 64 |  |  | 42971.3333 | 94 | 93
2017-08-24 08:30 | 68 | 68 |  |  | 42971.3542 | 96 | 95
2017-08-24 09:00 | 67 | 67 |  |  | 42971.375 | 97 | 97
2017-08-24 09:30 | 68 | 68 |  |  | 42971.3958 | 93 | 92
2017-08-24 10:00 | 72 | 72 |  |  | 42971.4167 | 99 | 99
2017-08-24 10:30 | 77 | 77 |  |  | 42971.4375 | 104 | 104
2017-08-24 11:00 | 75 | 75 |  |  | 42971.4583 | 101 | 101
2017-08-24 11:30 | 54 | 54 |  |  | 42971.4792 | 91 | 91
2017-08-24 12:00 | 42 | 42 |  |  | 42971.5 | 76 | 76
2017-08-24 12:30 | 38 | 38 |  |  | 42971.5208 | 71 | 71
2017-08-24 13:00 | 35 | 35 |  |  | 42971.5417 | 69 | 69
2017-08-24 13:30 | 35 | 34 |  |  | 42971.5625 | 68 | 67
2017-08-24 14:00 | 39 | 38 |  |  | 42971.5833 | 73 | 73
2017-08-24 14:30 | 46 | 46 |  |  | 42971.6042 | 75 | 75
2017-08-24 15:00 | 64 | 64 |  |  | 42971.625 | 84 | 84
2017-08-24 15:30 | 69 | 69 |  |  | 42971.6458 | 92 | 92
2017-08-24 16:00 | 69 | 69 |  |  | 42971.6667 | 92 | 92
2017-08-24 16:30 | 70 | 70 |  |  | 42971.6875 | 94 | 94
2017-08-24 17:00 | 69 | 69 |  |  | 42971.7083 | 93 | 93
2017-08-24 17:30 | 70 | 70 |  |  | 42971.7292 | 93 | 92
2017-08-24 18:00 | 72 | 72 |  |  | 42971.75 | 95 | 95
2017-08-24 18:30 | 73 | 72 |  |  | 42971.7708 | 95 | 94
2017-08-24 19:00 | 76 | 75 |  |  | 42971.7917 | 97 | 96
2017-08-24 19:30 | 74 | 74 |  |  | 42971.8125 | 95 | 94
2017-08-24 20:00 | 73 | 73 |  |  | 42971.8333 | 93 | 92
2017-08-24 20:30 | 71 | 71 |  |  | 42971.8542 | 91 | 90
2017-08-24 21:00 | 66 | 66 |  |  | 42971.875 | 86 | 85
2017-08-24 21:30 | 63 | 63 |  |  | 42971.8958 | 81 | 81
2017-08-24 22:00 | 59 | 59 |  |  | 42971.9167 | 78 | 77
2017-08-24 22:30 | 57 | 57 |  |  | 42971.9375 | 78 | 77
2017-08-24 23:00 | 55 | 54 |  |  | 42971.9583 | 74 | 73
2017-08-24 23:30 | 49 | 48 |  |  | 42971.9792 | 68 | 67
2017-08-25 | 44 | 43 |  |  | 42972 | 63 | 61
2017-08-25 00:30 | 41 | 39 |  |  | 42972.0208 | 57 | 55
2017-08-25 01:00 | 38 | 36 |  |  | 42972.0417 | 52 | 50
2017-08-25 01:30 | 35 | 33 |  |  | 42972.0625 | 49 | 48
2017-08-25 02:00 | 36 | 35 |  |  | 42972.0833 | 49 | 48
2017-08-25 02:30 | 36 | 35 |  |  | 42972.1042 | 49 | 48
2017-08-25 03:00 | 35 | 34 |  |  | 42972.125 | 48 | 47
2017-08-25 03:30 | 36 | 34 |  |  | 42972.1458 | 49 | 49
2017-08-25 04:00 | 36 | 35 |  |  | 42972.1667 | 48 | 47
2017-08-25 04:30 | 37 | 35 |  |  | 42972.1875 | 48 | 47
2017-08-25 05:00 | 38 | 37 |  |  | 42972.2083 | 51 | 50
2017-08-25 05:30 | 42 | 41 |  |  | 42972.2292 | 54 | 53
2017-08-25 06:00 | 46 | 46 |  |  | 42972.25 | 61 | 61
2017-08-25 06:30 | 54 | 53 |  |  | 42972.2708 | 72 | 72
2017-08-25 07:00 | 60 | 60 |  |  | 42972.2917 | 83 | 82
2017-08-25 07:30 | 65 | 65 |  |  | 42972.3125 | 89 | 89
2017-08-25 08:00 | 61 | 61 |  |  | 42972.3333 | 86 | 86
2017-08-25 08:30 | 74 | 74 |  |  | 42972.3542 | 62 | 62
2017-08-25 09:00 | 94 | 94 |  |  | 42972.375 | 36 | 35
2017-08-25 09:30 | 89 | 89 |  |  | 42972.3958 | 33 | 32
2017-08-25 10:00 | 88 | 88 |  |  | 42972.4167 | 34 | 33
2017-08-25 10:30 | 86 | 86 |  |  | 42972.4375 | 35 | 33
2017-08-25 11:00 | 78 | 78 |  |  | 42972.4583 | 42 | 41
2017-08-25 11:30 | 50 | 50 |  |  | 42972.4792 | 70 | 70
2017-08-25 12:00 | 49 | 49 |  |  | 42972.5 | 73 | 73
2017-08-25 12:30 | 49 | 48 |  |  | 42972.5208 | 74 | 74
2017-08-25 13:00 | 48 | 47 |  |  | 42972.5417 | 71 | 71
2017-08-25 13:30 | 49 | 49 |  |  | 42972.5625 | 74 | 74
2017-08-25 14:00 | 52 | 52 |  |  | 42972.5833 | 73 | 72
2017-08-25 14:30 | 52 | 52 |  |  | 42972.6042 | 74 | 73
2017-08-25 15:00 | 50 | 50 |  |  | 42972.625 | 74 | 73
2017-08-25 15:30 | 52 | 52 |  |  | 42972.6458 | 75 | 74
2017-08-25 16:00 | 57 | 56 |  |  | 42972.6667 | 77 | 76
2017-08-25 16:30 | 62 | 62 |  |  | 42972.6875 | 84 | 84
2017-08-25 17:00 | 65 | 65 |  |  | 42972.7083 | 88 | 88
2017-08-25 17:30 | 65 | 64 |  |  | 42972.7292 | 86 | 86
2017-08-25 18:00 | 65 | 65 |  |  | 42972.75 | 86 | 86
2017-08-25 18:30 | 67 | 66 |  |  | 42972.7708 | 87 | 86
2017-08-25 19:00 | 69 | 69 |  |  | 42972.7917 | 90 | 89
2017-08-25 19:30 | 68 | 67 |  |  | 42972.8125 | 88 | 88
2017-08-25 20:00 | 66 | 66 |  |  | 42972.8333 | 87 | 87
2017-08-25 20:30 | 67 | 66 |  |  | 42972.8542 | 87 | 87
2017-08-25 21:00 | 64 | 64 |  |  | 42972.875 | 83 | 83
2017-08-25 21:30 | 61 | 61 |  |  | 42972.8958 | 81 | 81
2017-08-25 22:00 | 61 | 61 |  |  | 42972.9167 | 80 | 80
2017-08-25 22:30 | 58 | 58 |  |  | 42972.9375 | 77 | 77
2017-08-25 23:00 | 58 | 58 |  |  | 42972.9583 | 76 | 75
2017-08-25 23:30 | 52 | 52 |  |  | 42972.9792 | 69 | 69
2017-08-26 | 45 | 45 |  |  | 42973 | 62 | 62
2017-08-26 00:30 | 40 | 39 |  |  | 42973.0208 | 55 | 54
2017-08-26 01:00 | 40 | 38 |  |  | 42973.0417 | 54 | 53
2017-08-26 01:30 | 37 | 35 |  |  | 42973.0625 | 50 | 49
2017-08-26 02:00 | 37 | 35 |  |  | 42973.0833 | 50 | 48
2017-08-26 02:30 | 35 | 33 |  |  | 42973.1042 | 48 | 47
2017-08-26 03:00 | 35 | 33 |  |  | 42973.125 | 46 | 46
2017-08-26 03:30 | 35 | 33 |  |  | 42973.1458 | 46 | 46
2017-08-26 04:00 | 34 | 33 |  |  | 42973.1667 | 45 | 45
2017-08-26 04:30 | 35 | 33 |  |  | 42973.1875 | 47 | 46
2017-08-26 05:00 | 36 | 35 |  |  | 42973.2083 | 48 | 48
2017-08-26 05:30 | 37 | 36 |  |  | 42973.2292 | 49 | 49
2017-08-26 06:00 | 39 | 38 |  |  | 42973.25 | 52 | 51
2017-08-26 06:30 | 38 | 37 |  |  | 42973.2708 | 53 | 52
2017-08-26 07:00 | 39 | 38 |  |  | 42973.2917 | 54 | 54
2017-08-26 07:30 | 40 | 39 |  |  | 42973.3125 | 57 | 57
2017-08-26 08:00 | 40 | 40 |  |  | 42973.3333 | 58 | 58
2017-08-26 08:30 | 40 | 40 |  |  | 42973.3542 | 59 | 59
2017-08-26 09:00 | 40 | 39 |  |  | 42973.375 | 58 | 58
2017-08-26 09:30 | 38 | 38 |  |  | 42973.3958 | 57 | 56
2017-08-26 10:00 | 38 | 38 |  |  | 42973.4167 | 55 | 55
2017-08-26 10:30 | 37 | 37 |  |  | 42973.4375 | 54 | 54
2017-08-26 11:00 | 37 | 37 |  |  | 42973.4583 | 54 | 54
2017-08-26 11:30 | 36 | 36 |  |  | 42973.4792 | 52 | 52
2017-08-26 12:00 | 36 | 36 |  |  | 42973.5 | 52 | 52
2017-08-26 12:30 | 36 | 35 |  |  | 42973.5208 | 51 | 51
2017-08-26 13:00 | 37 | 36 |  |  | 42973.5417 | 51 | 51
2017-08-26 13:30 | 38 | 38 |  |  | 42973.5625 | 52 | 52
2017-08-26 14:00 | 37 | 36 |  |  | 42973.5833 | 52 | 52
2017-08-26 14:30 | 36 | 36 |  |  | 42973.6042 | 52 | 52
2017-08-26 15:00 | 37 | 36 |  |  | 42973.625 | 53 | 53
2017-08-26 15:30 | 37 | 36 |  |  | 42973.6458 | 53 | 53
2017-08-26 16:00 | 38 | 38 |  |  | 42973.6667 | 55 | 55
2017-08-26 16:30 | 41 | 41 |  |  | 42973.6875 | 59 | 59
2017-08-26 17:00 | 47 | 46 |  |  | 42973.7083 | 65 | 65
2017-08-26 17:30 | 48 | 48 |  |  | 42973.7292 | 66 | 66
2017-08-26 18:00 | 53 | 51 |  |  | 42973.75 | 72 | 72
2017-08-26 18:30 | 57 | 54 |  |  | 42973.7708 | 75 | 75
2017-08-26 19:00 | 60 | 56 |  |  | 42973.7917 | 76 | 76
2017-08-26 19:30 | 58 | 54 |  |  | 42973.8125 | 74 | 74
2017-08-26 20:00 | 55 | 52 |  |  | 42973.8333 | 72 | 71
2017-08-26 20:30 | 54 | 50 |  |  | 42973.8542 | 70 | 69
2017-08-26 21:00 | 51 | 47 |  |  | 42973.875 | 65 | 65
2017-08-26 21:30 | 48 | 44 |  |  | 42973.8958 | 62 | 62
2017-08-26 22:00 | 48 | 44 |  |  | 42973.9167 | 64 | 63
2017-08-26 22:30 | 50 | 46 |  |  | 42973.9375 | 65 | 65
2017-08-26 23:00 | 53 | 48 |  |  | 42973.9583 | 65 | 65
2017-08-26 23:30 | 50 | 45 |  |  | 42973.9792 | 62 | 62
2017-08-27 | 48 | 42 |  |  | 42974 | 58 | 58
2017-08-27 00:30 | 44 | 37 |  |  | 42974.0208 | 52 | 52
2017-08-27 01:00 | 41 | 33 |  |  | 42974.0417 | 47 | 47
2017-08-27 01:30 | 39 | 31 |  |  | 42974.0625 | 45 | 45
2017-08-27 02:00 | 37 | 30 |  |  | 42974.0833 | 43 | 42
2017-08-27 02:30 | 45 | 30 |  |  | 42974.1042 | 41 | 41
2017-08-27 03:00 | 48 | 29 |  |  | 42974.125 | 42 | 41
2017-08-27 03:30 | 47 | 28 |  |  | 42974.1458 | 40 | 40
2017-08-27 04:00 | 47 | 28 |  |  | 42974.1667 | 40 | 39
2017-08-27 04:30 | 48 | 28 |  |  | 42974.1875 | 41 | 41
2017-08-27 05:00 | 49 | 30 |  |  | 42974.2083 | 43 | 43
2017-08-27 05:30 | 49 | 31 |  |  | 42974.2292 | 44 | 44
2017-08-27 06:00 | 49 | 31 |  |  | 42974.25 | 44 | 44
2017-08-27 06:30 | 49 | 30 |  |  | 42974.2708 | 44 | 44
2017-08-27 07:00 | 49 | 31 |  |  | 42974.2917 | 46 | 45
2017-08-27 07:30 | 49 | 32 |  |  | 42974.3125 | 47 | 47
2017-08-27 08:00 | 50 | 34 |  |  | 42974.3333 | 50 | 50
2017-08-27 08:30 | 49 | 33 |  |  | 42974.3542 | 49 | 49
2017-08-27 09:00 | 49 | 35 |  |  | 42974.375 | 51 | 51
2017-08-27 09:30 | 49 | 36 |  |  | 42974.3958 | 53 | 53
2017-08-27 10:00 | 50 | 37 |  |  | 42974.4167 | 56 | 56
2017-08-27 10:30 | 49 | 36 |  |  | 42974.4375 | 54 | 54
2017-08-27 11:00 | 48 | 34 |  |  | 42974.4583 | 48 | 48
2017-08-27 11:30 | 48 | 35 |  |  | 42974.4792 | 52 | 52
2017-08-27 12:00 | 46 | 32 |  |  | 42974.5 | 50 | 50
2017-08-27 12:30 | 48 | 34 |  |  | 42974.5208 | 52 | 52
2017-08-27 13:00 | 49 | 34 |  |  | 42974.5417 | 46 | 46
2017-08-27 13:30 | 48 | 34 |  |  | 42974.5625 | 47 | 47
2017-08-27 14:00 | 49 | 35 |  |  | 42974.5833 | 48 | 48
2017-08-27 14:30 | 48 | 33 |  |  | 42974.6042 | 50 | 49
2017-08-27 15:00 | 51 | 37 |  |  | 42974.625 | 52 | 51
2017-08-27 15:30 | 50 | 36 |  |  | 42974.6458 | 53 | 53
2017-08-27 16:00 | 52 | 38 |  |  | 42974.6667 | 55 | 55
2017-08-27 16:30 | 53 | 41 |  |  | 42974.6875 | 57 | 57
2017-08-27 17:00 | 57 | 45 |  |  | 42974.7083 | 61 | 61
2017-08-27 17:30 | 61 | 50 |  |  | 42974.7292 | 67 | 67
2017-08-27 18:00 | 70 | 53 |  |  | 42974.75 | 71 | 71
2017-08-27 18:30 | 76 | 56 |  |  | 42974.7708 | 74 | 74
2017-08-27 19:00 | 78 | 58 |  |  | 42974.7917 | 75 | 75
2017-08-27 19:30 | 77 | 57 |  |  | 42974.8125 | 74 | 74
2017-08-27 20:00 | 74 | 55 |  |  | 42974.8333 | 72 | 72
2017-08-27 20:30 | 71 | 53 |  |  | 42974.8542 | 70 | 70
2017-08-27 21:00 | 70 | 50 |  |  | 42974.875 | 68 | 67
2017-08-27 21:30 | 67 | 48 |  |  | 42974.8958 | 65 | 64
2017-08-27 22:00 | 67 | 48 |  |  | 42974.9167 | 66 | 65
2017-08-27 22:30 | 67 | 48 |  |  | 42974.9375 | 67 | 66
2017-08-27 23:00 | 68 | 48 |  |  | 42974.9583 | 65 | 65
2017-08-27 23:30 | 65 | 44 |  |  | 42974.9792 | 61 | 60
2017-08-28 | 64 | 40 |  |  | 42975 | 56 | 56
2017-08-28 00:30 | 62 | 35 |  |  | 42975.0208 | 51 | 50
2017-08-28 01:00 | 61 | 33 |  |  | 42975.0417 | 46 | 46
2017-08-28 01:30 | 60 | 30 |  |  | 42975.0625 | 44 | 44
2017-08-28 02:00 | 60 | 30 |  |  | 42975.0833 | 44 | 44
2017-08-28 02:30 | 58 | 32 |  |  | 42975.1042 | 46 | 45
2017-08-28 03:00 | 53 | 30 |  |  | 42975.125 | 46 | 43
2017-08-28 03:30 | 54 | 31 |  |  | 42975.1458 | 47 | 43
2017-08-28 04:00 | 53 | 30 |  |  | 42975.1667 | 47 | 43
2017-08-28 04:30 | 53 | 32 |  |  | 42975.1875 | 48 | 44
2017-08-28 05:00 | 54 | 35 |  |  | 42975.2083 | 51 | 48
2017-08-28 05:30 | 40 | 39 |  |  | 42975.2292 | 52 | 52
2017-08-28 06:00 | 45 | 45 |  |  | 42975.25 | 58 | 58
2017-08-28 06:30 | 53 | 52 |  |  | 42975.2708 | 69 | 69
2017-08-28 07:00 | 58 | 58 |  |  | 42975.2917 | 79 | 79
2017-08-28 07:30 | 63 | 63 |  |  | 42975.3125 | 88 | 87
2017-08-28 08:00 | 61 | 60 |  |  | 42975.3333 | 85 | 85
2017-08-28 08:30 | 43 | 42 |  |  | 42975.3542 | 74 | 73
2017-08-28 09:00 | 33 | 32 |  |  | 42975.375 | 66 | 66
2017-08-28 09:30 | 31 | 30 |  |  | 42975.3958 | 64 | 64
2017-08-28 10:00 | 31 | 30 |  |  | 42975.4167 | 62 | 62
2017-08-28 10:30 | 34 | 34 |  |  | 42975.4375 | 63 | 63
2017-08-28 11:00 | 47 | 46 |  |  | 42975.4583 | 69 | 69
2017-08-28 11:30 | 45 | 44 |  |  | 42975.4792 | 68 | 67
2017-08-28 12:00 | 43 | 43 |  |  | 42975.5 | 66 | 65
2017-08-28 12:30 | 44 | 44 |  |  | 42975.5208 | 68 | 67
2017-08-28 13:00 | 45 | 45 |  |  | 42975.5417 | 69 | 68
2017-08-28 13:30 | 47 | 46 |  |  | 42975.5625 | 71 | 70
2017-08-28 14:00 | 48 | 48 |  |  | 42975.5833 | 72 | 71
2017-08-28 14:30 | 48 | 48 |  |  | 42975.6042 | 71 | 71
2017-08-28 15:00 | 48 | 48 |  |  | 42975.625 | 72 | 71
2017-08-28 15:30 | 50 | 50 |  |  | 42975.6458 | 73 | 72
2017-08-28 16:00 | 51 | 51 |  |  | 42975.6667 | 75 | 74
2017-08-28 16:30 | 56 | 56 |  |  | 42975.6875 | 80 | 79
2017-08-28 17:00 | 61 | 60 |  |  | 42975.7083 | 85 | 85
2017-08-28 17:30 | 65 | 64 |  |  | 42975.7292 | 87 | 87
2017-08-28 18:00 | 68 | 66 |  |  | 42975.75 | 88 | 88
2017-08-28 18:30 | 68 | 66 |  |  | 42975.7708 | 87 | 87
2017-08-28 19:00 | 70 | 68 |  |  | 42975.7917 | 89 | 88
2017-08-28 19:30 | 67 | 65 |  |  | 42975.8125 | 86 | 86
2017-08-28 20:00 | 65 | 64 |  |  | 42975.8333 | 85 | 84
2017-08-28 20:30 | 64 | 64 |  |  | 42975.8542 | 84 | 84
2017-08-28 21:00 | 60 | 60 |  |  | 42975.875 | 80 | 79
2017-08-28 21:30 | 54 | 54 |  |  | 42975.8958 | 75 | 74
2017-08-28 22:00 | 53 | 53 |  |  | 42975.9167 | 74 | 73
2017-08-28 22:30 | 51 | 51 |  |  | 42975.9375 | 71 | 70
2017-08-28 23:00 | 49 | 49 |  |  | 42975.9583 | 67 | 66
2017-08-28 23:30 | 46 | 45 |  |  | 42975.9792 | 64 | 64
2017-08-29 | 42 | 42 |  |  | 42976 | 60 | 60
2017-08-29 00:30 | 39 | 39 |  |  | 42976.0208 | 55 | 55
2017-08-29 01:00 | 35 | 35 |  |  | 42976.0417 | 50 | 50
2017-08-29 01:30 | 31 | 31 |  |  | 42976.0625 | 46 | 46
2017-08-29 02:00 | 30 | 30 |  |  | 42976.0833 | 44 | 44
2017-08-29 02:30 | 31 | 31 |  |  | 42976.1042 | 45 | 44
2017-08-29 03:00 | 30 | 30 |  |  | 42976.125 | 45 | 44
2017-08-29 03:30 | 31 | 31 |  |  | 42976.1458 | 45 | 44
2017-08-29 04:00 | 30 | 30 |  |  | 42976.1667 | 44 | 43
2017-08-29 04:30 | 31 | 31 |  |  | 42976.1875 | 46 | 45
2017-08-29 05:00 | 33 | 32 |  |  | 42976.2083 | 46 | 46
2017-08-29 05:30 | 35 | 34 |  |  | 42976.2292 | 48 | 47
2017-08-29 06:00 | 41 | 40 |  |  | 42976.25 | 56 | 55
2017-08-29 06:30 | 52 | 52 |  |  | 42976.2708 | 71 | 70
2017-08-29 07:00 | 62 | 61 |  |  | 42976.2917 | 83 | 82
2017-08-29 07:30 | 67 | 67 |  |  | 42976.3125 | 90 | 90
2017-08-29 08:00 | 65 | 65 |  |  | 42976.3333 | 90 | 89
2017-08-29 08:30 | 61 | 61 |  |  | 42976.3542 | 85 | 84
2017-08-29 09:00 | 38 | 38 |  |  | 42976.375 | 72 | 71
2017-08-29 09:30 | 31 | 31 |  |  | 42976.3958 | 65 | 63
2017-08-29 10:00 | 32 | 31 |  |  | 42976.4167 | 63 | 62
2017-08-29 10:30 | 30 | 30 |  |  | 42976.4375 | 60 | 59
2017-08-29 11:00 | 29 | 28 |  |  | 42976.4583 | 58 | 58
2017-08-29 11:30 | 29 | 28 |  |  | 42976.4792 | 58 | 57
2017-08-29 12:00 | 29 | 28 |  |  | 42976.5 | 58 | 58
2017-08-29 12:30 | 39 | 38 |  |  | 42976.5208 | 65 | 65
2017-08-29 13:00 | 47 | 46 |  |  | 42976.5417 | 69 | 68
2017-08-29 13:30 | 46 | 46 |  |  | 42976.5625 | 70 | 70
2017-08-29 14:00 | 48 | 47 |  |  | 42976.5833 | 71 | 70
2017-08-29 14:30 | 50 | 49 |  |  | 42976.6042 | 73 | 72
2017-08-29 15:00 | 51 | 50 |  |  | 42976.625 | 74 | 74
2017-08-29 15:30 | 52 | 51 |  |  | 42976.6458 | 75 | 75
2017-08-29 16:00 | 54 | 53 |  |  | 42976.6667 | 77 | 77
2017-08-29 16:30 | 58 | 57 |  |  | 42976.6875 | 81 | 81
2017-08-29 17:00 | 61 | 60 |  |  | 42976.7083 | 83 | 83
2017-08-29 17:30 | 61 | 60 |  |  | 42976.7292 | 81 | 81
2017-08-29 18:00 | 65 | 62 |  |  | 42976.75 | 86 | 84
2017-08-29 18:30 | 65 | 61 |  |  | 42976.7708 | 84 | 82
2017-08-29 19:00 | 65 | 63 |  |  | 42976.7917 | 85 | 84
2017-08-29 19:30 | 64 | 61 |  |  | 42976.8125 | 83 | 82
2017-08-29 20:00 | 63 | 60 |  |  | 42976.8333 | 82 | 82
2017-08-29 20:30 | 61 | 60 |  |  | 42976.8542 | 82 | 82
2017-08-29 21:00 | 58 | 57 |  |  | 42976.875 | 78 | 78
2017-08-29 21:30 | 56 | 55 |  |  | 42976.8958 | 74 | 74
2017-08-29 22:00 | 55 | 53 |  |  | 42976.9167 | 72 | 72
2017-08-29 22:30 | 51 | 48 |  |  | 42976.9375 | 68 | 67
2017-08-29 23:00 | 51 | 48 |  |  | 42976.9583 | 66 | 65
2017-08-29 23:30 | 48 | 45 |  |  | 42976.9792 | 61 | 60
2017-08-30 | 45 | 41 |  |  | 42977 | 57 | 56
2017-08-30 00:30 | 42 | 37 |  |  | 42977.0208 | 53 | 51
2017-08-30 01:00 | 38 | 33 |  |  | 42977.0417 | 49 | 46
2017-08-30 01:30 | 36 | 31 |  |  | 42977.0625 | 44 | 42
2017-08-30 02:00 | 34 | 30 |  |  | 42977.0833 | 45 | 42
2017-08-30 02:30 | 34 | 29 |  |  | 42977.1042 | 43 | 41
2017-08-30 03:00 | 34 | 29 |  |  | 42977.125 | 42 | 40
2017-08-30 03:30 | 34 | 29 |  |  | 42977.1458 | 43 | 41
2017-08-30 04:00 | 35 | 30 |  |  | 42977.1667 | 44 | 41
2017-08-30 04:30 | 35 | 30 |  |  | 42977.1875 | 43 | 41
2017-08-30 05:00 | 37 | 33 |  |  | 42977.2083 | 46 | 44
2017-08-30 05:30 | 39 | 36 |  |  | 42977.2292 | 49 | 48
2017-08-30 06:00 | 43 | 41 |  |  | 42977.25 | 56 | 55
2017-08-30 06:30 | 50 | 48 |  |  | 42977.2708 | 67 | 67
2017-08-30 07:00 | 54 | 53 |  |  | 42977.2917 | 75 | 75
2017-08-30 07:30 | 60 | 60 |  |  | 42977.3125 | 84 | 84
2017-08-30 08:00 | 58 | 58 |  |  | 42977.3333 | 83 | 83
2017-08-30 08:30 | 54 | 54 |  |  | 42977.3542 | 81 | 81
2017-08-30 09:00 | 53 | 52 |  |  | 42977.375 | 79 | 79
2017-08-30 09:30 | 51 | 51 |  |  | 42977.3958 | 77 | 77
2017-08-30 10:00 | 50 | 50 |  |  | 42977.4167 | 76 | 76
2017-08-30 10:30 | 51 | 51 |  |  | 42977.4375 | 75 | 75
2017-08-30 11:00 | 51 | 51 |  |  | 42977.4583 | 74 | 74
2017-08-30 11:30 | 50 | 50 |  |  | 42977.4792 | 72 | 71
2017-08-30 12:00 | 48 | 48 |  |  | 42977.5 | 68 | 68
2017-08-30 12:30 | 47 | 46 |  |  | 42977.5208 | 65 | 65
2017-08-30 13:00 | 47 | 47 |  |  | 42977.5417 | 66 | 66
2017-08-30 13:30 | 48 | 48 |  |  | 42977.5625 | 69 | 68
2017-08-30 14:00 | 51 | 51 |  |  | 42977.5833 | 71 | 71
2017-08-30 14:30 | 50 | 50 |  |  | 42977.6042 | 71 | 71
2017-08-30 15:00 | 51 | 50 |  |  | 42977.625 | 72 | 72
2017-08-30 15:30 | 51 | 51 |  |  | 42977.6458 | 74 | 73
2017-08-30 16:00 | 55 | 55 |  |  | 42977.6667 | 77 | 77
2017-08-30 16:30 | 59 | 58 |  |  | 42977.6875 | 80 | 80
2017-08-30 17:00 | 62 | 62 |  |  | 42977.7083 | 84 | 84
2017-08-30 17:30 | 61 | 61 |  |  | 42977.7292 | 83 | 83
2017-08-30 18:00 | 64 | 63 |  |  | 42977.75 | 86 | 86
2017-08-30 18:30 | 67 | 66 |  |  | 42977.7708 | 86 | 85
2017-08-30 19:00 | 69 | 67 |  |  | 42977.7917 | 88 | 87
2017-08-30 19:30 | 68 | 66 |  |  | 42977.8125 | 86 | 84
2017-08-30 20:00 | 67 | 65 |  |  | 42977.8333 | 83 | 82
2017-08-30 20:30 | 66 | 64 |  |  | 42977.8542 | 83 | 82
2017-08-30 21:00 | 63 | 61 |  |  | 42977.875 | 78 | 77
2017-08-30 21:30 | 60 | 58 |  |  | 42977.8958 | 75 | 73
2017-08-30 22:00 | 56 | 54 |  |  | 42977.9167 | 73 | 72
2017-08-30 22:30 | 55 | 53 |  |  | 42977.9375 | 72 | 71
2017-08-30 23:00 | 55 | 53 |  |  | 42977.9583 | 70 | 69
2017-08-30 23:30 | 49 | 47 |  |  | 42977.9792 | 64 | 63
2017-08-31 | 46 | 43 |  |  | 42978 | 59 | 58
2017-08-31 00:30 | 43 | 39 |  |  | 42978.0208 | 54 | 52
2017-08-31 01:00 | 40 | 36 |  |  | 42978.0417 | 50 | 48
2017-08-31 01:30 | 38 | 33 |  |  | 42978.0625 | 46 | 44
2017-08-31 02:00 | 36 | 31 |  |  | 42978.0833 | 46 | 43
2017-08-31 02:30 | 37 | 31 |  |  | 42978.1042 | 45 | 43
2017-08-31 03:00 | 37 | 32 |  |  | 42978.125 | 46 | 43
2017-08-31 03:30 | 37 | 32 |  |  | 42978.1458 | 47 | 44
2017-08-31 04:00 | 36 | 31 |  |  | 42978.1667 | 46 | 43
2017-08-31 04:30 | 35 | 30 |  |  | 42978.1875 | 44 | 41
2017-08-31 05:00 | 36 | 32 |  |  | 42978.2083 | 46 | 44
2017-08-31 05:30 | 39 | 37 |  |  | 42978.2292 | 50 | 49
2017-08-31 06:00 | 44 | 43 |  |  | 42978.25 | 56 | 55
2017-08-31 06:30 | 51 | 50 |  |  | 42978.2708 | 66 | 66
2017-08-31 07:00 | 56 | 55 |  |  | 42978.2917 | 75 | 74
2017-08-31 07:30 | 61 | 60 |  |  | 42978.3125 | 82 | 82
2017-08-31 08:00 | 59 | 58 |  |  | 42978.3333 | 80 | 80
2017-08-31 08:30 | 56 | 55 |  |  | 42978.3542 | 79 | 79
2017-08-31 09:00 | 74 | 74 |  |  | 42978.375 | 54 | 54
2017-08-31 09:30 | 91 | 91 |  |  | 42978.3958 | 31 | 31
2017-08-31 10:00 | 88 | 88 |  |  | 42978.4167 | 32 | 31
2017-08-31 10:30 | 86 | 86 |  |  | 42978.4375 | 31 | 30
2017-08-31 11:00 | 89 | 89 |  |  | 42978.4583 | 35 | 34
2017-08-31 11:30 | 91 | 91 |  |  | 42978.4792 | 40 | 39
2017-08-31 12:00 | 91 | 91 |  |  | 42978.5 | 40 | 40
2017-08-31 12:30 | 89 | 89 |  |  | 42978.5208 | 43 | 43
2017-08-31 13:00 | 52 | 52 |  |  | 42978.5417 | 71 | 71
2017-08-31 13:30 | 51 | 50 |  |  | 42978.5625 | 70 | 70
2017-08-31 14:00 | 49 | 49 |  |  | 42978.5833 | 70 | 69
2017-08-31 14:30 | 51 | 51 |  |  | 42978.6042 | 70 | 70
2017-08-31 15:00 | 51 | 51 |  |  | 42978.625 | 70 | 70
2017-08-31 15:30 | 52 | 51 |  |  | 42978.6458 | 73 | 73
2017-08-31 16:00 | 53 | 53 |  |  | 42978.6667 | 75 | 75
2017-08-31 16:30 | 56 | 55 |  |  | 42978.6875 | 78 | 78
2017-08-31 17:00 | 58 | 58 |  |  | 42978.7083 | 81 | 81
2017-08-31 17:30 | 61 | 60 |  |  | 42978.7292 | 82 | 82
2017-08-31 18:00 | 65 | 65 |  |  | 42978.75 | 86 | 85
2017-08-31 18:30 | 69 | 67 |  |  | 42978.7708 | 89 | 87
2017-08-31 19:00 | 72 | 70 |  |  | 42978.7917 | 92 | 89
2017-08-31 19:30 | 71 | 69 |  |  | 42978.8125 | 90 | 87
2017-08-31 20:00 | 70 | 67 |  |  | 42978.8333 | 89 | 85
2017-08-31 20:30 | 68 | 65 |  |  | 42978.8542 | 87 | 83
2017-08-31 21:00 | 64 | 61 |  |  | 42978.875 | 81 | 78
2017-08-31 21:30 | 61 | 58 |  |  | 42978.8958 | 76 | 73
2017-08-31 22:00 | 56 | 54 |  |  | 42978.9167 | 74 | 72
2017-08-31 22:30 | 55 | 53 |  |  | 42978.9375 | 75 | 73
2017-08-31 23:00 | 56 | 53 |  |  | 42978.9583 | 74 | 71
2017-08-31 23:30 | 50 | 48 |  |  | 42978.9792 | 67 | 66
2017-09-01 | 47 | 43 |  |  | 42979 | 60 | 59
2017-09-01 00:30 | 42 | 37 |  |  | 42979.0208 | 53 | 52
2017-09-01 01:00 | 38 | 32 |  |  | 42979.0417 | 48 | 45
2017-09-01 01:30 | 37 | 31 |  |  | 42979.0625 | 46 | 43
2017-09-01 02:00 | 37 | 31 |  |  | 42979.0833 | 46 | 43
2017-09-01 02:30 | 37 | 32 |  |  | 42979.1042 | 45 | 43
2017-09-01 03:00 | 37 | 32 |  |  | 42979.125 | 45 | 43
2017-09-01 03:30 | 37 | 31 |  |  | 42979.1458 | 45 | 42
2017-09-01 04:00 | 36 | 30 |  |  | 42979.1667 | 43 | 41
2017-09-01 04:30 | 36 | 31 |  |  | 42979.1875 | 44 | 42
2017-09-01 05:00 | 38 | 33 |  |  | 42979.2083 | 48 | 45
2017-09-01 05:30 | 40 | 37 |  |  | 42979.2292 | 50 | 48
2017-09-01 06:00 | 43 | 41 |  |  | 42979.25 | 55 | 54
2017-09-01 06:30 | 54 | 53 |  |  | 42979.2708 | 70 | 70
2017-09-01 07:00 | 63 | 59 |  |  | 42979.2917 | 84 | 80
2017-09-01 07:30 | 69 | 65 |  |  | 42979.3125 | 92 | 88
2017-09-01 08:00 | 67 | 64 |  |  | 42979.3333 | 91 | 88
2017-09-01 08:30 | 62 | 59 |  |  | 42979.3542 | 87 | 84
2017-09-01 09:00 | 58 | 55 |  |  | 42979.375 | 85 | 82
2017-09-01 09:30 | 55 | 54 |  |  | 42979.3958 | 76 | 76
2017-09-01 10:00 | 53 | 53 |  |  | 42979.4167 | 75 | 75
2017-09-01 10:30 | 51 | 51 |  |  | 42979.4375 | 74 | 74
2017-09-01 11:00 | 51 | 51 |  |  | 42979.4583 | 71 | 71
2017-09-01 11:30 | 51 | 51 |  |  | 42979.4792 | 73 | 73
2017-09-01 12:00 | 51 | 51 |  |  | 42979.5 | 75 | 74
2017-09-01 12:30 | 52 | 52 |  |  | 42979.5208 | 71 | 70
2017-09-01 13:00 | 84 | 84 |  |  | 42979.5417 | 37 | 36
2017-09-01 13:30 | 83 | 83 |  |  | 42979.5625 | 34 | 33
2017-09-01 14:00 | 84 | 84 |  |  | 42979.5833 | 34 | 33
2017-09-01 14:30 | 83 | 83 |  |  | 42979.6042 | 33 | 32
2017-09-01 15:00 | 48 | 48 |  |  | 42979.625 | 67 | 67
2017-09-01 15:30 | 49 | 49 |  |  | 42979.6458 | 71 | 70
2017-09-01 16:00 | 53 | 53 |  |  | 42979.6667 | 74 | 73
2017-09-01 16:30 | 54 | 54 |  |  | 42979.6875 | 76 | 76
2017-09-01 17:00 | 59 | 58 |  |  | 42979.7083 | 81 | 80
2017-09-01 17:30 | 62 | 58 |  |  | 42979.7292 | 85 | 80
2017-09-01 18:00 | 63 | 59 |  |  | 42979.75 | 85 | 80
2017-09-01 18:30 | 67 | 62 |  |  | 42979.7708 | 87 | 81
2017-09-01 19:00 | 69 | 64 |  |  | 42979.7917 | 90 | 84
2017-09-01 19:30 | 69 | 64 |  |  | 42979.8125 | 90 | 83
2017-09-01 20:00 | 68 | 63 |  |  | 42979.8333 | 89 | 83
2017-09-01 20:30 | 67 | 62 |  |  | 42979.8542 | 87 | 81
2017-09-01 21:00 | 63 | 59 |  |  | 42979.875 | 79 | 76
2017-09-01 21:30 | 54 | 54 |  |  | 42979.8958 | 71 | 71
2017-09-01 22:00 | 52 | 51 |  |  | 42979.9167 | 70 | 70
2017-09-01 22:30 | 51 | 50 |  |  | 42979.9375 | 68 | 68
2017-09-01 23:00 | 51 | 49 |  |  | 42979.9583 | 66 | 66
2017-09-01 23:30 | 48 | 46 |  |  | 42979.9792 | 62 | 61
2017-09-02 | 44 | 41 |  |  | 42980 | 56 | 55
2017-09-02 00:30 | 40 | 36 |  |  | 42980.0208 | 50 | 49
2017-09-02 01:00 | 41 | 36 |  |  | 42980.0417 | 49 | 48
2017-09-02 01:30 | 39 | 34 |  |  | 42980.0625 | 47 | 46
2017-09-02 02:00 | 38 | 32 |  |  | 42980.0833 | 46 | 44
2017-09-02 02:30 | 36 | 32 |  |  | 42980.1042 | 45 | 44
2017-09-02 03:00 | 35 | 32 |  |  | 42980.125 | 43 | 43
2017-09-02 03:30 | 35 | 32 |  |  | 42980.1458 | 43 | 43
2017-09-02 04:00 | 35 | 33 |  |  | 42980.1667 | 42 | 42
2017-09-02 04:30 | 35 | 32 |  |  | 42980.1875 | 42 | 42
2017-09-02 05:00 | 34 | 33 |  |  | 42980.2083 | 44 | 44
2017-09-02 05:30 | 35 | 34 |  |  | 42980.2292 | 46 | 46
2017-09-02 06:00 | 36 | 35 |  |  | 42980.25 | 47 | 47
2017-09-02 06:30 | 35 | 33 |  |  | 42980.2708 | 48 | 48
2017-09-02 07:00 | 35 | 34 |  |  | 42980.2917 | 51 | 51
2017-09-02 07:30 | 38 | 37 |  |  | 42980.3125 | 54 | 53
2017-09-02 08:00 | 38 | 37 |  |  | 42980.3333 | 55 | 55
2017-09-02 08:30 | 39 | 39 |  |  | 42980.3542 | 56 | 55
2017-09-02 09:00 | 40 | 39 |  |  | 42980.375 | 57 | 56
2017-09-02 09:30 | 40 | 40 |  |  | 42980.3958 | 58 | 57
2017-09-02 10:00 | 37 | 37 |  |  | 42980.4167 | 55 | 54
2017-09-02 10:30 | 38 | 37 |  |  | 42980.4375 | 54 | 53
2017-09-02 11:00 | 36 | 36 |  |  | 42980.4583 | 53 | 51
2017-09-02 11:30 | 35 | 35 |  |  | 42980.4792 | 52 | 51
2017-09-02 12:00 | 36 | 36 |  |  | 42980.5 | 52 | 51
2017-09-02 12:30 | 35 | 35 |  |  | 42980.5208 | 51 | 50
2017-09-02 13:00 | 34 | 33 |  |  | 42980.5417 | 50 | 49
2017-09-02 13:30 | 34 | 33 |  |  | 42980.5625 | 49 | 48
2017-09-02 14:00 | 34 | 33 |  |  | 42980.5833 | 50 | 49
2017-09-02 14:30 | 34 | 33 |  |  | 42980.6042 | 50 | 48
2017-09-02 15:00 | 34 | 34 |  |  | 42980.625 | 50 | 49
2017-09-02 15:30 | 37 | 36 |  |  | 42980.6458 | 52 | 51
2017-09-02 16:00 | 37 | 36 |  |  | 42980.6667 | 55 | 54
2017-09-02 16:30 | 40 | 39 |  |  | 42980.6875 | 58 | 57
2017-09-02 17:00 | 43 | 42 |  |  | 42980.7083 | 61 | 61
2017-09-02 17:30 | 45 | 44 |  |  | 42980.7292 | 62 | 61
2017-09-02 18:00 | 47 | 46 |  |  | 42980.75 | 66 | 66
2017-09-02 18:30 | 52 | 52 |  |  | 42980.7708 | 70 | 70
2017-09-02 19:00 | 53 | 53 |  |  | 42980.7917 | 72 | 72
2017-09-02 19:30 | 54 | 54 |  |  | 42980.8125 | 72 | 71
2017-09-02 20:00 | 51 | 51 |  |  | 42980.8333 | 69 | 69
2017-09-02 20:30 | 52 | 51 |  |  | 42980.8542 | 70 | 69
2017-09-02 21:00 | 50 | 50 |  |  | 42980.875 | 67 | 66
2017-09-02 21:30 | 48 | 47 |  |  | 42980.8958 | 63 | 63
2017-09-02 22:00 | 47 | 45 |  |  | 42980.9167 | 63 | 63
2017-09-02 22:30 | 49 | 48 |  |  | 42980.9375 | 65 | 65
2017-09-02 23:00 | 51 | 49 |  |  | 42980.9583 | 64 | 64
2017-09-02 23:30 | 48 | 46 |  |  | 42980.9792 | 62 | 62
2017-09-03 | 45 | 43 |  |  | 42981 | 58 | 58
2017-09-03 00:30 | 39 | 37 |  |  | 42981.0208 | 51 | 51
2017-09-03 01:00 | 36 | 34 |  |  | 42981.0417 | 47 | 47
2017-09-03 01:30 | 34 | 31 |  |  | 42981.0625 | 44 | 44
2017-09-03 02:00 | 33 | 30 |  |  | 42981.0833 | 42 | 42
2017-09-03 02:30 | 34 | 31 |  |  | 42981.1042 | 43 | 43
2017-09-03 03:00 | 34 | 31 |  |  | 42981.125 | 43 | 43
2017-09-03 03:30 | 34 | 32 |  |  | 42981.1458 | 44 | 44
2017-09-03 04:00 | 34 | 32 |  |  | 42981.1667 | 43 | 43
2017-09-03 04:30 | 35 | 33 |  |  | 42981.1875 | 44 | 44
2017-09-03 05:00 | 36 | 34 |  |  | 42981.2083 | 46 | 46
2017-09-03 05:30 | 35 | 33 |  |  | 42981.2292 | 45 | 45
2017-09-03 06:00 | 35 | 33 |  |  | 42981.25 | 45 | 45
2017-09-03 06:30 | 31 | 29 |  |  | 42981.2708 | 42 | 42
2017-09-03 07:00 | 32 | 30 |  |  | 42981.2917 | 43 | 43
2017-09-03 07:30 | 31 | 29 |  |  | 42981.3125 | 44 | 44
2017-09-03 08:00 | 31 | 29 |  |  | 42981.3333 | 45 | 45
2017-09-03 08:30 | 32 | 31 |  |  | 42981.3542 | 47 | 47
2017-09-03 09:00 | 33 | 31 |  |  | 42981.375 | 49 | 48
2017-09-03 09:30 | 35 | 34 |  |  | 42981.3958 | 51 | 51
2017-09-03 10:00 | 35 | 35 |  |  | 42981.4167 | 51 | 50
2017-09-03 10:30 | 35 | 34 |  |  | 42981.4375 | 51 | 50
2017-09-03 11:00 | 36 | 36 |  |  | 42981.4583 | 52 | 51
2017-09-03 11:30 | 33 | 33 |  |  | 42981.4792 | 50 | 48
2017-09-03 12:00 | 36 | 35 |  |  | 42981.5 | 53 | 51
2017-09-03 12:30 | 37 | 36 |  |  | 42981.5208 | 54 | 52
2017-09-03 13:00 | 38 | 38 |  |  | 42981.5417 | 54 | 53
2017-09-03 13:30 | 38 | 37 |  |  | 42981.5625 | 54 | 53
2017-09-03 14:00 | 41 | 40 |  |  | 42981.5833 | 56 | 55
2017-09-03 14:30 | 40 | 39 |  |  | 42981.6042 | 56 | 55
2017-09-03 15:00 | 39 | 38 |  |  | 42981.625 | 56 | 55
2017-09-03 15:30 | 39 | 39 |  |  | 42981.6458 | 56 | 55
2017-09-03 16:00 | 43 | 43 |  |  | 42981.6667 | 59 | 59
2017-09-03 16:30 | 46 | 45 |  |  | 42981.6875 | 63 | 63
2017-09-03 17:00 | 50 | 49 |  |  | 42981.7083 | 68 | 67
2017-09-03 17:30 | 53 | 52 |  |  | 42981.7292 | 69 | 69
2017-09-03 18:00 | 54 | 53 |  |  | 42981.75 | 71 | 71
2017-09-03 18:30 | 58 | 57 |  |  | 42981.7708 | 73 | 73
2017-09-03 19:00 | 58 | 57 |  |  | 42981.7917 | 76 | 76
2017-09-03 19:30 | 56 | 55 |  |  | 42981.8125 | 73 | 73
2017-09-03 20:00 | 54 | 52 |  |  | 42981.8333 | 70 | 70
2017-09-03 20:30 | 53 | 52 |  |  | 42981.8542 | 70 | 70
2017-09-03 21:00 | 50 | 49 |  |  | 42981.875 | 66 | 66
2017-09-03 21:30 | 48 | 47 |  |  | 42981.8958 | 63 | 63
2017-09-03 22:00 | 47 | 46 |  |  | 42981.9167 | 63 | 63
2017-09-03 22:30 | 49 | 47 |  |  | 42981.9375 | 66 | 66
2017-09-03 23:00 | 49 | 47 |  |  | 42981.9583 | 63 | 63
2017-09-03 23:30 | 47 | 45 |  |  | 42981.9792 | 60 | 60
2017-09-04 | 44 | 41 |  |  | 42982 | 55 | 55
2017-09-04 00:30 | 41 | 38 |  |  | 42982.0208 | 51 | 51
2017-09-04 01:00 | 37 | 34 |  |  | 42982.0417 | 48 | 48
2017-09-04 01:30 | 35 | 31 |  |  | 42982.0625 | 45 | 45
2017-09-04 02:00 | 35 | 32 |  |  | 42982.0833 | 44 | 44
2017-09-04 02:30 | 37 | 34 |  |  | 42982.1042 | 45 | 45
2017-09-04 03:00 | 38 | 35 |  |  | 42982.125 | 48 | 48
2017-09-04 03:30 | 38 | 35 |  |  | 42982.1458 | 47 | 47
2017-09-04 04:00 | 38 | 35 |  |  | 42982.1667 | 48 | 48
2017-09-04 04:30 | 38 | 36 |  |  | 42982.1875 | 48 | 48
2017-09-04 05:00 | 39 | 38 |  |  | 42982.2083 | 49 | 49
2017-09-04 05:30 | 42 | 41 |  |  | 42982.2292 | 53 | 53
2017-09-04 06:00 | 52 | 51 |  |  | 42982.25 | 65 | 64
2017-09-04 06:30 | 54 | 54 |  |  | 42982.2708 | 71 | 71
2017-09-04 07:00 | 59 | 59 |  |  | 42982.2917 | 78 | 78
2017-09-04 07:30 | 59 | 59 |  |  | 42982.3125 | 81 | 81
2017-09-04 08:00 | 57 | 56 |  |  | 42982.3333 | 80 | 80
2017-09-04 08:30 | 56 | 56 |  |  | 42982.3542 | 79 | 79
2017-09-04 09:00 | 54 | 54 |  |  | 42982.375 | 76 | 76
2017-09-04 09:30 | 53 | 53 |  |  | 42982.3958 | 76 | 76
2017-09-04 10:00 | 54 | 54 |  |  | 42982.4167 | 76 | 75
2017-09-04 10:30 | 54 | 54 |  |  | 42982.4375 | 76 | 75
2017-09-04 11:00 | 53 | 53 |  |  | 42982.4583 | 75 | 74
2017-09-04 11:30 | 53 | 53 |  |  | 42982.4792 | 75 | 74
2017-09-04 12:00 | 53 | 53 |  |  | 42982.5 | 76 | 75
2017-09-04 12:30 | 53 | 53 |  |  | 42982.5208 | 76 | 75
2017-09-04 13:00 | 55 | 55 |  |  | 42982.5417 | 79 | 78
2017-09-04 13:30 | 59 | 59 |  |  | 42982.5625 | 84 | 83
2017-09-04 14:00 | 61 | 61 |  |  | 42982.5833 | 86 | 86
2017-09-04 14:30 | 62 | 62 |  |  | 42982.6042 | 86 | 86
2017-09-04 15:00 | 63 | 63 |  |  | 42982.625 | 86 | 86
2017-09-04 15:30 | 64 | 63 |  |  | 42982.6458 | 86 | 85
2017-09-04 16:00 | 65 | 64 |  |  | 42982.6667 | 88 | 87
2017-09-04 16:30 | 68 | 67 |  |  | 42982.6875 | 89 | 88
2017-09-04 17:00 | 70 | 69 |  |  | 42982.7083 | 92 | 91
2017-09-04 17:30 | 71 | 69 |  |  | 42982.7292 | 91 | 90
2017-09-04 18:00 | 73 | 71 |  |  | 42982.75 | 92 | 91
2017-09-04 18:30 | 74 | 72 |  |  | 42982.7708 | 93 | 90
2017-09-04 19:00 | 75 | 73 |  |  | 42982.7917 | 93 | 91
2017-09-04 19:30 | 72 | 70 |  |  | 42982.8125 | 90 | 86
2017-09-04 20:00 | 70 | 68 |  |  | 42982.8333 | 87 | 85
2017-09-04 20:30 | 69 | 67 |  |  | 42982.8542 | 85 | 83
2017-09-04 21:00 | 64 | 61 |  |  | 42982.875 | 79 | 76
2017-09-04 21:30 | 58 | 57 |  |  | 42982.8958 | 73 | 72
2017-09-04 22:00 | 56 | 54 |  |  | 42982.9167 | 71 | 69
2017-09-04 22:30 | 56 | 55 |  |  | 42982.9375 | 71 | 71
2017-09-04 23:00 | 54 | 53 |  |  | 42982.9583 | 68 | 68
2017-09-04 23:30 | 51 | 50 |  |  | 42982.9792 | 64 | 64
2017-09-05 | 46 | 45 |  |  | 42983 | 59 | 58
2017-09-05 00:30 | 43 | 41 |  |  | 42983.0208 | 55 | 54
2017-09-05 01:00 | 39 | 37 |  |  | 42983.0417 | 50 | 49
2017-09-05 01:30 | 37 | 32 |  |  | 42983.0625 | 46 | 44
2017-09-05 02:00 | 37 | 31 |  |  | 42983.0833 | 44 | 42
2017-09-05 02:30 | 38 | 32 |  |  | 42983.1042 | 46 | 44
2017-09-05 03:00 | 41 | 36 |  |  | 42983.125 | 49 | 47
2017-09-05 03:30 | 39 | 33 |  |  | 42983.1458 | 46 | 44
2017-09-05 04:00 | 36 | 30 |  |  | 42983.1667 | 42 | 40
2017-09-05 04:30 | 38 | 32 |  |  | 42983.1875 | 45 | 44
2017-09-05 05:00 | 37 | 33 |  |  | 42983.2083 | 46 | 44
2017-09-05 05:30 | 38 | 35 |  |  | 42983.2292 | 48 | 47
2017-09-05 06:00 | 41 | 40 |  |  | 42983.25 | 54 | 54
2017-09-05 06:30 | 49 | 48 |  |  | 42983.2708 | 65 | 65
2017-09-05 07:00 | 57 | 52 |  |  | 42983.2917 | 78 | 74
2017-09-05 07:30 | 67 | 61 |  |  | 42983.3125 | 83 | 78
2017-09-05 08:00 | 104 | 101 |  |  | 42983.3333 | 44 | 38
2017-09-05 08:30 | 100 | 97 |  |  | 42983.3542 | 42 | 37
2017-09-05 09:00 | 94 | 90 |  |  | 42983.375 | 40 | 35
2017-09-05 09:30 | 92 | 88 |  |  | 42983.3958 | 39 | 34
2017-09-05 10:00 | 60 | 56 |  |  | 42983.4167 | 70 | 67
2017-09-05 10:30 | 52 | 49 |  |  | 42983.4375 | 76 | 74
2017-09-05 11:00 | 51 | 48 |  |  | 42983.4583 | 74 | 72
2017-09-05 11:30 | 52 | 47 |  |  | 42983.4792 | 72 | 69
2017-09-05 12:00 | 51 | 45 |  |  | 42983.5 | 72 | 68
2017-09-05 12:30 | 53 | 47 |  |  | 42983.5208 | 74 | 71
2017-09-05 13:00 | 54 | 49 |  |  | 42983.5417 | 76 | 73
2017-09-05 13:30 | 56 | 50 |  |  | 42983.5625 | 77 | 73
2017-09-05 14:00 | 58 | 53 |  |  | 42983.5833 | 80 | 77
2017-09-05 14:30 | 58 | 53 |  |  | 42983.6042 | 81 | 78
2017-09-05 15:00 | 59 | 55 |  |  | 42983.625 | 82 | 79
2017-09-05 15:30 | 62 | 57 |  |  | 42983.6458 | 85 | 82
2017-09-05 16:00 | 63 | 59 |  |  | 42983.6667 | 87 | 84
2017-09-05 16:30 | 68 | 63 |  |  | 42983.6875 | 92 | 88
2017-09-05 17:00 | 70 | 65 |  |  | 42983.7083 | 93 | 90
2017-09-05 17:30 | 72 | 67 |  |  | 42983.7292 | 93 | 89
2017-09-05 18:00 | 71 | 66 |  |  | 42983.75 | 93 | 89
2017-09-05 18:30 | 74 | 66 |  |  | 42983.7708 | 96 | 87
2017-09-05 19:00 | 74 | 66 |  |  | 42983.7917 | 95 | 86
2017-09-05 19:30 | 71 | 65 |  |  | 42983.8125 | 89 | 85
2017-09-05 20:00 | 64 | 62 |  |  | 42983.8333 | 83 | 82
2017-09-05 20:30 | 63 | 61 |  |  | 42983.8542 | 82 | 81
2017-09-05 21:00 | 58 | 57 |  |  | 42983.875 | 74 | 74
2017-09-05 21:30 | 53 | 52 |  |  | 42983.8958 | 69 | 69
2017-09-05 22:00 | 51 | 51 |  |  | 42983.9167 | 68 | 67
2017-09-05 22:30 | 53 | 52 |  |  | 42983.9375 | 70 | 69
2017-09-05 23:00 | 52 | 52 |  |  | 42983.9583 | 70 | 68
2017-09-05 23:30 | 48 | 47 |  |  | 42983.9792 | 66 | 64
2017-09-06 | 41 | 41 |  |  | 42984 | 58 | 57
2017-09-06 00:30 | 36 | 35 |  |  | 42984.0208 | 52 | 50
2017-09-06 01:00 | 34 | 33 |  |  | 42984.0417 | 49 | 48
2017-09-06 01:30 | 32 | 31 |  |  | 42984.0625 | 46 | 44
2017-09-06 02:00 | 32 | 32 |  |  | 42984.0833 | 46 | 44
2017-09-06 02:30 | 34 | 34 |  |  | 42984.1042 | 47 | 46
2017-09-06 03:00 | 36 | 35 |  |  | 42984.125 | 49 | 48
2017-09-06 03:30 | 36 | 36 |  |  | 42984.1458 | 49 | 48
2017-09-06 04:00 | 37 | 36 |  |  | 42984.1667 | 48 | 47
2017-09-06 04:30 | 37 | 37 |  |  | 42984.1875 | 48 | 47
2017-09-06 05:00 | 38 | 37 |  |  | 42984.2083 | 50 | 50
2017-09-06 05:30 | 42 | 42 |  |  | 42984.2292 | 56 | 55
2017-09-06 06:00 | 46 | 46 |  |  | 42984.25 | 63 | 61
2017-09-06 06:30 | 54 | 54 |  |  | 42984.2708 | 72 | 72
2017-09-06 07:00 | 60 | 60 |  |  | 42984.2917 | 80 | 80
2017-09-06 07:30 | 64 | 64 |  |  | 42984.3125 | 87 | 86
2017-09-06 08:00 | 62 | 62 |  |  | 42984.3333 | 85 | 84
2017-09-06 08:30 | 58 | 58 |  |  | 42984.3542 | 82 | 81
2017-09-06 09:00 | 54 | 54 |  |  | 42984.375 | 78 | 77
2017-09-06 09:30 | 51 | 51 |  |  | 42984.3958 | 73 | 72
2017-09-06 10:00 | 49 | 49 |  |  | 42984.4167 | 71 | 70
2017-09-06 10:30 | 47 | 47 |  |  | 42984.4375 | 68 | 67
2017-09-06 11:00 | 47 | 47 |  |  | 42984.4583 | 69 | 68
2017-09-06 11:30 | 45 | 45 |  |  | 42984.4792 | 68 | 66
2017-09-06 12:00 | 46 | 46 |  |  | 42984.5 | 68 | 67
2017-09-06 12:30 | 45 | 45 |  |  | 42984.5208 | 69 | 67
2017-09-06 13:00 | 47 | 47 |  |  | 42984.5417 | 70 | 68
2017-09-06 13:30 | 48 | 48 |  |  | 42984.5625 | 72 | 71
2017-09-06 14:00 | 51 | 51 |  |  | 42984.5833 | 73 | 72
2017-09-06 14:30 | 52 | 52 |  |  | 42984.6042 | 74 | 74
2017-09-06 15:00 | 52 | 52 |  |  | 42984.625 | 76 | 75
2017-09-06 15:30 | 55 | 54 |  |  | 42984.6458 | 77 | 77
2017-09-06 16:00 | 57 | 57 |  |  | 42984.6667 | 79 | 79
2017-09-06 16:30 | 61 | 60 |  |  | 42984.6875 | 83 | 83
2017-09-06 17:00 | 64 | 63 |  |  | 42984.7083 | 87 | 86
2017-09-06 17:30 | 66 | 65 |  |  | 42984.7292 | 87 | 86
2017-09-06 18:00 | 68 | 67 |  |  | 42984.75 | 87 | 87
2017-09-06 18:30 | 71 | 69 |  |  | 42984.7708 | 88 | 87
2017-09-06 19:00 | 72 | 70 |  |  | 42984.7917 | 89 | 88
2017-09-06 19:30 | 69 | 67 |  |  | 42984.8125 | 85 | 84
2017-09-06 20:00 | 66 | 64 |  |  | 42984.8333 | 82 | 82
2017-09-06 20:30 | 65 | 64 |  |  | 42984.8542 | 81 | 80
2017-09-06 21:00 | 59 | 58 |  |  | 42984.875 | 75 | 74
2017-09-06 21:30 | 54 | 52 |  |  | 42984.8958 | 70 | 70
2017-09-06 22:00 | 52 | 51 |  |  | 42984.9167 | 69 | 68
2017-09-06 22:30 | 53 | 52 |  |  | 42984.9375 | 70 | 70
2017-09-06 23:00 | 53 | 52 |  |  | 42984.9583 | 69 | 68
2017-09-06 23:30 | 51 | 47 |  |  | 42984.9792 | 64 | 63
2017-09-07 | 45 | 41 |  |  | 42985 | 59 | 57
2017-09-07 00:30 | 43 | 38 |  |  | 42985.0208 | 55 | 53
2017-09-07 01:00 | 40 | 34 |  |  | 42985.0417 | 51 | 48
2017-09-07 01:30 | 39 | 33 |  |  | 42985.0625 | 48 | 45
2017-09-07 02:00 | 39 | 33 |  |  | 42985.0833 | 49 | 46
2017-09-07 02:30 | 41 | 34 |  |  | 42985.1042 | 50 | 46
2017-09-07 03:00 | 41 | 33 |  |  | 42985.125 | 50 | 46
2017-09-07 03:30 | 40 | 33 |  |  | 42985.1458 | 50 | 46
2017-09-07 04:00 | 40 | 33 |  |  | 42985.1667 | 50 | 46
2017-09-07 04:30 | 40 | 32 |  |  | 42985.1875 | 49 | 46
2017-09-07 05:00 | 42 | 36 |  |  | 42985.2083 | 53 | 50
2017-09-07 05:30 | 45 | 41 |  |  | 42985.2292 | 58 | 56
2017-09-07 06:00 | 51 | 48 |  |  | 42985.25 | 66 | 64
2017-09-07 06:30 | 55 | 53 |  |  | 42985.2708 | 72 | 72
2017-09-07 07:00 | 58 | 57 |  |  | 42985.2917 | 78 | 78
2017-09-07 07:30 | 63 | 59 |  |  | 42985.3125 | 82 | 82
2017-09-07 08:00 | 61 | 56 |  |  | 42985.3333 | 80 | 80
2017-09-07 08:30 | 57 | 52 |  |  | 42985.3542 | 77 | 77
2017-09-07 09:00 | 55 | 50 |  |  | 42985.375 | 74 | 74
2017-09-07 09:30 | 53 | 48 |  |  | 42985.3958 | 71 | 71
2017-09-07 10:00 | 52 | 48 |  |  | 42985.4167 | 71 | 71
2017-09-07 10:30 | 51 | 46 |  |  | 42985.4375 | 69 | 69
2017-09-07 11:00 | 50 | 45 |  |  | 42985.4583 | 68 | 68
2017-09-07 11:30 | 51 | 45 |  |  | 42985.4792 | 68 | 68
2017-09-07 12:00 | 50 | 45 |  |  | 42985.5 | 67 | 67
2017-09-07 12:30 | 50 | 45 |  |  | 42985.5208 | 68 | 67
2017-09-07 13:00 | 52 | 47 |  |  | 42985.5417 | 70 | 69
2017-09-07 13:30 | 52 | 47 |  |  | 42985.5625 | 72 | 71
2017-09-07 14:00 | 53 | 48 |  |  | 42985.5833 | 73 | 73
2017-09-07 14:30 | 54 | 50 |  |  | 42985.6042 | 75 | 74
2017-09-07 15:00 | 55 | 51 |  |  | 42985.625 | 77 | 76
2017-09-07 15:30 | 57 | 53 |  |  | 42985.6458 | 78 | 77
2017-09-07 16:00 | 61 | 57 |  |  | 42985.6667 | 81 | 81
2017-09-07 16:30 | 65 | 61 |  |  | 42985.6875 | 83 | 83
2017-09-07 17:00 | 70 | 64 |  |  | 42985.7083 | 86 | 86
2017-09-07 17:30 | 73 | 66 |  |  | 42985.7292 | 87 | 87
2017-09-07 18:00 | 75 | 68 |  |  | 42985.75 | 93 | 93
2017-09-07 18:30 | 77 | 70 |  |  | 42985.7708 | 94 | 93
2017-09-07 19:00 | 79 | 72 |  |  | 42985.7917 | 96 | 95
2017-09-07 19:30 | 78 | 70 |  |  | 42985.8125 | 92 | 91
2017-09-07 20:00 | 75 | 68 |  |  | 42985.8333 | 88 | 88
2017-09-07 20:30 | 70 | 65 |  |  | 42985.8542 | 82 | 82
2017-09-07 21:00 | 64 | 59 |  |  | 42985.875 | 74 | 74
2017-09-07 21:30 | 61 | 55 |  |  | 42985.8958 | 70 | 70
2017-09-07 22:00 | 59 | 53 |  |  | 42985.9167 | 69 | 69
2017-09-07 22:30 | 61 | 54 |  |  | 42985.9375 | 71 | 71
2017-09-07 23:00 | 60 | 52 |  |  | 42985.9583 | 68 | 68
2017-09-07 23:30 | 55 | 47 |  |  | 42985.9792 | 63 | 63
2017-09-08 | 51 | 43 |  |  | 42986 | 57 | 57
2017-09-08 00:30 | 48 | 39 |  |  | 42986.0208 | 53 | 53
2017-09-08 01:00 | 45 | 35 |  |  | 42986.0417 | 48 | 48
2017-09-08 01:30 | 44 | 33 |  |  | 42986.0625 | 46 | 46
2017-09-08 02:00 | 43 | 32 |  |  | 42986.0833 | 44 | 44
2017-09-08 02:30 | 43 | 32 |  |  | 42986.1042 | 46 | 46
2017-09-08 03:00 | 43 | 32 |  |  | 42986.125 | 45 | 45
2017-09-08 03:30 | 43 | 32 |  |  | 42986.1458 | 45 | 45
2017-09-08 04:00 | 43 | 33 |  |  | 42986.1667 | 45 | 44
2017-09-08 04:30 | 44 | 33 |  |  | 42986.1875 | 46 | 46
2017-09-08 05:00 | 45 | 36 |  |  | 42986.2083 | 49 | 49
2017-09-08 05:30 | 47 | 40 |  |  | 42986.2292 | 53 | 53
2017-09-08 06:00 | 53 | 48 |  |  | 42986.25 | 62 | 62
2017-09-08 06:30 | 56 | 52 |  |  | 42986.2708 | 69 | 69
2017-09-08 07:00 | 60 | 58 |  |  | 42986.2917 | 77 | 77
2017-09-08 07:30 | 61 | 60 |  |  | 42986.3125 | 82 | 81
2017-09-08 08:00 | 58 | 57 |  |  | 42986.3333 | 82 | 80
2017-09-08 08:30 | 57 | 56 |  |  | 42986.3542 | 82 | 80
2017-09-08 09:00 | 53 | 52 |  |  | 42986.375 | 78 | 75
2017-09-08 09:30 | 49 | 48 |  |  | 42986.3958 | 73 | 70
2017-09-08 10:00 | 48 | 47 |  |  | 42986.4167 | 71 | 68
2017-09-08 10:30 | 48 | 47 |  |  | 42986.4375 | 70 | 67
2017-09-08 11:00 | 47 | 47 |  |  | 42986.4583 | 71 | 68
2017-09-08 11:30 | 48 | 47 |  |  | 42986.4792 | 70 | 67
2017-09-08 12:00 | 48 | 47 |  |  | 42986.5 | 70 | 67
2017-09-08 12:30 | 48 | 47 |  |  | 42986.5208 | 71 | 68
2017-09-08 13:00 | 49 | 48 |  |  | 42986.5417 | 71 | 69
2017-09-08 13:30 | 50 | 48 |  |  | 42986.5625 | 71 | 70
2017-09-08 14:00 | 52 | 48 |  |  | 42986.5833 | 70 | 70
2017-09-08 14:30 | 52 | 48 |  |  | 42986.6042 | 72 | 71
2017-09-08 15:00 | 53 | 49 |  |  | 42986.625 | 72 | 72
2017-09-08 15:30 | 56 | 52 |  |  | 42986.6458 | 74 | 74
2017-09-08 16:00 | 59 | 55 |  |  | 42986.6667 | 78 | 78
2017-09-08 16:30 | 62 | 57 |  |  | 42986.6875 | 80 | 80
2017-09-08 17:00 | 63 | 59 |  |  | 42986.7083 | 82 | 82
2017-09-08 17:30 | 64 | 59 |  |  | 42986.7292 | 81 | 81
2017-09-08 18:00 | 63 | 58 |  |  | 42986.75 | 79 | 79
2017-09-08 18:30 | 63 | 57 |  |  | 42986.7708 | 78 | 78
2017-09-08 19:00 | 63 | 57 |  |  | 42986.7917 | 78 | 78
2017-09-08 19:30 | 60 | 54 |  |  | 42986.8125 | 75 | 74
2017-09-08 20:00 | 60 | 53 |  |  | 42986.8333 | 73 | 73
2017-09-08 20:30 | 61 | 54 |  |  | 42986.8542 | 79 | 78
2017-09-08 21:00 | 56 | 50 |  |  | 42986.875 | 74 | 73
2017-09-08 21:30 | 54 | 48 |  |  | 42986.8958 | 70 | 70
2017-09-08 22:00 | 54 | 47 |  |  | 42986.9167 | 69 | 69
2017-09-08 22:30 | 56 | 48 |  |  | 42986.9375 | 70 | 69
2017-09-08 23:00 | 56 | 48 |  |  | 42986.9583 | 69 | 69
2017-09-08 23:30 | 52 | 44 |  |  | 42986.9792 | 65 | 65
2017-09-09 | 51 | 41 |  |  | 42987 | 61 | 61
2017-09-09 00:30 | 51 | 41 |  |  | 42987.0208 | 59 | 59
2017-09-09 01:00 | 50 | 38 |  |  | 42987.0417 | 56 | 56
2017-09-09 01:30 | 48 | 35 |  |  | 42987.0625 | 52 | 51
2017-09-09 02:00 | 47 | 34 |  |  | 42987.0833 | 51 | 50
2017-09-09 02:30 | 47 | 34 |  |  | 42987.1042 | 51 | 50
2017-09-09 03:00 | 46 | 33 |  |  | 42987.125 | 49 | 49
2017-09-09 03:30 | 45 | 33 |  |  | 42987.1458 | 49 | 48
2017-09-09 04:00 | 45 | 32 |  |  | 42987.1667 | 47 | 47
2017-09-09 04:30 | 44 | 31 |  |  | 42987.1875 | 46 | 46
2017-09-09 05:00 | 43 | 31 |  |  | 42987.2083 | 46 | 46
2017-09-09 05:30 | 43 | 32 |  |  | 42987.2292 | 49 | 49
2017-09-09 06:00 | 45 | 34 |  |  | 42987.25 | 51 | 51
2017-09-09 06:30 | 46 | 36 |  |  | 42987.2708 | 53 | 53
2017-09-09 07:00 | 46 | 36 |  |  | 42987.2917 | 55 | 55
2017-09-09 07:30 | 45 | 36 |  |  | 42987.3125 | 56 | 56
2017-09-09 08:00 | 45 | 36 |  |  | 42987.3333 | 57 | 57
2017-09-09 08:30 | 45 | 37 |  |  | 42987.3542 | 59 | 59
2017-09-09 09:00 | 45 | 37 |  |  | 42987.375 | 58 | 57
2017-09-09 09:30 | 44 | 37 |  |  | 42987.3958 | 57 | 57
2017-09-09 10:00 | 44 | 37 |  |  | 42987.4167 | 58 | 58
2017-09-09 10:30 | 45 | 37 |  |  | 42987.4375 | 57 | 57
2017-09-09 11:00 | 44 | 36 |  |  | 42987.4583 | 56 | 55
2017-09-09 11:30 | 44 | 36 |  |  | 42987.4792 | 56 | 55
2017-09-09 12:00 | 44 | 35 |  |  | 42987.5 | 56 | 55
2017-09-09 12:30 | 43 | 35 |  |  | 42987.5208 | 56 | 56
2017-09-09 13:00 | 44 | 35 |  |  | 42987.5417 | 56 | 56
2017-09-09 13:30 | 46 | 37 |  |  | 42987.5625 | 58 | 57
2017-09-09 14:00 | 45 | 38 |  |  | 42987.5833 | 58 | 57
2017-09-09 14:30 | 47 | 39 |  |  | 42987.6042 | 59 | 59
2017-09-09 15:00 | 47 | 39 |  |  | 42987.625 | 59 | 59
2017-09-09 15:30 | 46 | 38 |  |  | 42987.6458 | 60 | 59
2017-09-09 16:00 | 49 | 41 |  |  | 42987.6667 | 63 | 63
2017-09-09 16:30 | 52 | 45 |  |  | 42987.6875 | 68 | 68
2017-09-09 17:00 | 55 | 48 |  |  | 42987.7083 | 70 | 70
2017-09-09 17:30 | 57 | 49 |  |  | 42987.7292 | 73 | 73
2017-09-09 18:00 | 58 | 50 |  |  | 42987.75 | 73 | 73
2017-09-09 18:30 | 61 | 53 |  |  | 42987.7708 | 76 | 76
2017-09-09 19:00 | 62 | 54 |  |  | 42987.7917 | 79 | 79
2017-09-09 19:30 | 60 | 51 |  |  | 42987.8125 | 74 | 74
2017-09-09 20:00 | 56 | 47 |  |  | 42987.8333 | 67 | 67
2017-09-09 20:30 | 55 | 46 |  |  | 42987.8542 | 67 | 67
2017-09-09 21:00 | 54 | 44 |  |  | 42987.875 | 63 | 63
2017-09-09 21:30 | 52 | 43 |  |  | 42987.8958 | 62 | 62
2017-09-09 22:00 | 51 | 43 |  |  | 42987.9167 | 62 | 62
2017-09-09 22:30 | 55 | 46 |  |  | 42987.9375 | 66 | 66
2017-09-09 23:00 | 56 | 48 |  |  | 42987.9583 | 65 | 65
2017-09-09 23:30 | 54 | 44 |  |  | 42987.9792 | 62 | 62
2017-09-10 | 50 | 39 |  |  | 42988 | 57 | 57
2017-09-10 00:30 | 48 | 36 |  |  | 42988.0208 | 51 | 51
2017-09-10 01:00 | 46 | 32 |  |  | 42988.0417 | 47 | 47
2017-09-10 01:30 | 44 | 29 |  |  | 42988.0625 | 43 | 42
2017-09-10 02:00 | 42 | 27 |  |  | 42988.0833 | 41 | 41
2017-09-10 02:30 | 42 | 27 |  |  | 42988.1042 | 42 | 42
2017-09-10 03:00 | 42 | 26 |  |  | 42988.125 | 42 | 42
2017-09-10 03:30 | 41 | 25 |  |  | 42988.1458 | 41 | 41
2017-09-10 04:00 | 40 | 24 |  |  | 42988.1667 | 39 | 39
2017-09-10 04:30 | 40 | 23 |  |  | 42988.1875 | 38 | 38
2017-09-10 05:00 | 40 | 24 |  |  | 42988.2083 | 39 | 39
2017-09-10 05:30 | 40 | 25 |  |  | 42988.2292 | 40 | 40
2017-09-10 06:00 | 40 | 25 |  |  | 42988.25 | 42 | 42
2017-09-10 06:30 | 41 | 27 |  |  | 42988.2708 | 43 | 43
2017-09-10 07:00 | 40 | 27 |  |  | 42988.2917 | 42 | 42
2017-09-10 07:30 | 39 | 25 |  |  | 42988.3125 | 41 | 41
2017-09-10 08:00 | 40 | 27 |  |  | 42988.3333 | 43 | 43
2017-09-10 08:30 | 40 | 28 |  |  | 42988.3542 | 45 | 45
2017-09-10 09:00 | 39 | 28 |  |  | 42988.375 | 46 | 46
2017-09-10 09:30 | 39 | 28 |  |  | 42988.3958 | 46 | 46
2017-09-10 10:00 | 39 | 29 |  |  | 42988.4167 | 46 | 46
2017-09-10 10:30 | 40 | 30 |  |  | 42988.4375 | 46 | 46
2017-09-10 11:00 | 39 | 30 |  |  | 42988.4583 | 46 | 46
2017-09-10 11:30 | 39 | 30 |  |  | 42988.4792 | 46 | 46
2017-09-10 12:00 | 39 | 29 |  |  | 42988.5 | 46 | 46
2017-09-10 12:30 | 39 | 29 |  |  | 42988.5208 | 47 | 46
2017-09-10 13:00 | 39 | 29 |  |  | 42988.5417 | 47 | 46
2017-09-10 13:30 | 40 | 30 |  |  | 42988.5625 | 47 | 47
2017-09-10 14:00 | 41 | 31 |  |  | 42988.5833 | 47 | 46
2017-09-10 14:30 | 41 | 32 |  |  | 42988.6042 | 46 | 46
2017-09-10 15:00 | 42 | 33 |  |  | 42988.625 | 48 | 47
2017-09-10 15:30 | 43 | 34 |  |  | 42988.6458 | 51 | 50
2017-09-10 16:00 | 47 | 39 |  |  | 42988.6667 | 55 | 55
2017-09-10 16:30 | 51 | 43 |  |  | 42988.6875 | 60 | 60
2017-09-10 17:00 | 56 | 47 |  |  | 42988.7083 | 65 | 65
2017-09-10 17:30 | 60 | 51 |  |  | 42988.7292 | 67 | 67
2017-09-10 18:00 | 63 | 54 |  |  | 42988.75 | 71 | 71
2017-09-10 18:30 | 67 | 58 |  |  | 42988.7708 | 75 | 75
2017-09-10 19:00 | 69 | 60 |  |  | 42988.7917 | 79 | 78
2017-09-10 19:30 | 70 | 59 |  |  | 42988.8125 | 78 | 78
2017-09-10 20:00 | 68 | 58 |  |  | 42988.8333 | 77 | 76
2017-09-10 20:30 | 67 | 57 |  |  | 42988.8542 | 75 | 75
2017-09-10 21:00 | 63 | 53 |  |  | 42988.875 | 71 | 71
2017-09-10 21:30 | 62 | 51 |  |  | 42988.8958 | 68 | 68
2017-09-10 22:00 | 59 | 50 |  |  | 42988.9167 | 67 | 66
2017-09-10 22:30 | 61 | 50 |  |  | 42988.9375 | 69 | 68
2017-09-10 23:00 | 61 | 50 |  |  | 42988.9583 | 68 | 67
2017-09-10 23:30 | 59 | 47 |  |  | 42988.9792 | 64 | 63
2017-09-11 | 55 | 42 |  |  | 42989 | 59 | 58
2017-09-11 00:30 | 49 | 36 |  |  | 42989.0208 | 52 | 52
2017-09-11 01:00 | 47 | 33 |  |  | 42989.0417 | 48 | 47
2017-09-11 01:30 | 46 | 31 |  |  | 42989.0625 | 46 | 45
2017-09-11 02:00 | 46 | 29 |  |  | 42989.0833 | 44 | 44
2017-09-11 02:30 | 47 | 30 |  |  | 42989.1042 | 45 | 44
2017-09-11 03:00 | 47 | 31 |  |  | 42989.125 | 45 | 45
2017-09-11 03:30 | 45 | 31 |  |  | 42989.1458 | 44 | 44
2017-09-11 04:00 | 45 | 31 |  |  | 42989.1667 | 44 | 43
2017-09-11 04:30 | 45 | 33 |  |  | 42989.1875 | 45 | 45
2017-09-11 05:00 | 45 | 34 |  |  | 42989.2083 | 47 | 47
2017-09-11 05:30 | 49 | 40 |  |  | 42989.2292 | 54 | 54
2017-09-11 06:00 | 53 | 46 |  |  | 42989.25 | 61 | 61
2017-09-11 06:30 | 58 | 52 |  |  | 42989.2708 | 70 | 70
2017-09-11 07:00 | 62 | 57 |  |  | 42989.2917 | 78 | 78
2017-09-11 07:30 | 65 | 61 |  |  | 42989.3125 | 85 | 84
2017-09-11 08:00 | 64 | 60 |  |  | 42989.3333 | 83 | 83
2017-09-11 08:30 | 62 | 57 |  |  | 42989.3542 | 81 | 81
2017-09-11 09:00 | 59 | 54 |  |  | 42989.375 | 79 | 79
2017-09-11 09:30 | 57 | 52 |  |  | 42989.3958 | 76 | 76
2017-09-11 10:00 | 55 | 50 |  |  | 42989.4167 | 75 | 75
2017-09-11 10:30 | 54 | 49 |  |  | 42989.4375 | 74 | 73
2017-09-11 11:00 | 53 | 48 |  |  | 42989.4583 | 73 | 72
2017-09-11 11:30 | 53 | 48 |  |  | 42989.4792 | 72 | 72
2017-09-11 12:00 | 52 | 48 |  |  | 42989.5 | 74 | 73
2017-09-11 12:30 | 52 | 48 |  |  | 42989.5208 | 74 | 73
2017-09-11 13:00 | 53 | 49 |  |  | 42989.5417 | 74 | 73
2017-09-11 13:30 | 55 | 51 |  |  | 42989.5625 | 76 | 75
2017-09-11 14:00 | 56 | 52 |  |  | 42989.5833 | 76 | 75
2017-09-11 14:30 | 58 | 54 |  |  | 42989.6042 | 77 | 76
2017-09-11 15:00 | 58 | 55 |  |  | 42989.625 | 76 | 76
2017-09-11 15:30 | 60 | 55 |  |  | 42989.6458 | 77 | 77
2017-09-11 16:00 | 64 | 59 |  |  | 42989.6667 | 80 | 80
2017-09-11 16:30 | 66 | 62 |  |  | 42989.6875 | 83 | 83
2017-09-11 17:00 | 69 | 64 |  |  | 42989.7083 | 86 | 86
2017-09-11 17:30 | 72 | 67 |  |  | 42989.7292 | 86 | 86
2017-09-11 18:00 | 72 | 67 |  |  | 42989.75 | 86 | 86
2017-09-11 18:30 | 73 | 69 |  |  | 42989.7708 | 87 | 87
2017-09-11 19:00 | 76 | 71 |  |  | 42989.7917 | 89 | 89
2017-09-11 19:30 | 75 | 69 |  |  | 42989.8125 | 88 | 88
2017-09-11 20:00 | 72 | 68 |  |  | 42989.8333 | 86 | 86
2017-09-11 20:30 | 71 | 67 |  |  | 42989.8542 | 84 | 84
2017-09-11 21:00 | 67 | 62 |  |  | 42989.875 | 80 | 80
2017-09-11 21:30 | 64 | 59 |  |  | 42989.8958 | 75 | 75
2017-09-11 22:00 | 61 | 57 |  |  | 42989.9167 | 73 | 73
2017-09-11 22:30 | 61 | 56 |  |  | 42989.9375 | 73 | 73
2017-09-11 23:00 | 62 | 56 |  |  | 42989.9583 | 72 | 72
2017-09-11 23:30 | 58 | 51 |  |  | 42989.9792 | 66 | 66
2017-09-12 | 55 | 46 |  |  | 42990 | 63 | 62
2017-09-12 00:30 | 52 | 42 |  |  | 42990.0208 | 57 | 56
2017-09-12 01:00 | 49 | 37 |  |  | 42990.0417 | 52 | 51
2017-09-12 01:30 | 48 | 36 |  |  | 42990.0625 | 48 | 48
2017-09-12 02:00 | 47 | 35 |  |  | 42990.0833 | 48 | 47
2017-09-12 02:30 | 47 | 35 |  |  | 42990.1042 | 46 | 46
2017-09-12 03:00 | 47 | 34 |  |  | 42990.125 | 47 | 46
2017-09-12 03:30 | 48 | 35 |  |  | 42990.1458 | 46 | 45
2017-09-12 04:00 | 47 | 34 |  |  | 42990.1667 | 46 | 45
2017-09-12 04:30 | 47 | 34 |  |  | 42990.1875 | 47 | 47
2017-09-12 05:00 | 48 | 36 |  |  | 42990.2083 | 48 | 48
2017-09-12 05:30 | 50 | 40 |  |  | 42990.2292 | 54 | 54
2017-09-12 06:00 | 54 | 46 |  |  | 42990.25 | 61 | 60
2017-09-12 06:30 | 56 | 50 |  |  | 42990.2708 | 67 | 67
2017-09-12 07:00 | 62 | 58 |  |  | 42990.2917 | 77 | 77
2017-09-12 07:30 | 63 | 58 |  |  | 42990.3125 | 81 | 81
2017-09-12 08:00 | 63 | 58 |  |  | 42990.3333 | 81 | 81
2017-09-12 08:30 | 59 | 54 |  |  | 42990.3542 | 79 | 79
2017-09-12 09:00 | 56 | 52 |  |  | 42990.375 | 76 | 76
2017-09-12 09:30 | 52 | 48 |  |  | 42990.3958 | 72 | 72
2017-09-12 10:00 | 51 | 46 |  |  | 42990.4167 | 71 | 71
2017-09-12 10:30 | 52 | 48 |  |  | 42990.4375 | 72 | 72
2017-09-12 11:00 | 53 | 48 |  |  | 42990.4583 | 72 | 72
2017-09-12 11:30 | 52 | 48 |  |  | 42990.4792 | 73 | 72
2017-09-12 12:00 | 49 | 48 |  |  | 42990.5 | 75 | 74
2017-09-12 12:30 | 49 | 48 |  |  | 42990.5208 | 77 | 75
2017-09-12 13:00 | 52 | 52 |  |  | 42990.5417 | 79 | 78
2017-09-12 13:30 | 55 | 55 |  |  | 42990.5625 | 82 | 80
2017-09-12 14:00 | 56 | 56 |  |  | 42990.5833 | 84 | 82
2017-09-12 14:30 | 56 | 56 |  |  | 42990.6042 | 84 | 83
2017-09-12 15:00 | 59 | 58 |  |  | 42990.625 | 86 | 85
2017-09-12 15:30 | 56 | 56 |  |  | 42990.6458 | 81 | 80
2017-09-12 16:00 | 62 | 61 |  |  | 42990.6667 | 86 | 85
2017-09-12 16:30 | 65 | 64 |  |  | 42990.6875 | 89 | 88
2017-09-12 17:00 | 67 | 66 |  |  | 42990.7083 | 91 | 91
2017-09-12 17:30 | 69 | 67 |  |  | 42990.7292 | 92 | 92
2017-09-12 18:00 | 69 | 67 |  |  | 42990.75 | 91 | 91
2017-09-12 18:30 | 71 | 69 |  |  | 42990.7708 | 91 | 91
2017-09-12 19:00 | 74 | 72 |  |  | 42990.7917 | 91 | 91
2017-09-12 19:30 | 70 | 68 |  |  | 42990.8125 | 88 | 88
2017-09-12 20:00 | 67 | 66 |  |  | 42990.8333 | 86 | 86
2017-09-12 20:30 | 66 | 64 |  |  | 42990.8542 | 84 | 83
2017-09-12 21:00 | 63 | 61 |  |  | 42990.875 | 80 | 79
2017-09-12 21:30 | 60 | 58 |  |  | 42990.8958 | 75 | 74
2017-09-12 22:00 | 57 | 55 |  |  | 42990.9167 | 73 | 73
2017-09-12 22:30 | 56 | 54 |  |  | 42990.9375 | 74 | 74
2017-09-12 23:00 | 56 | 53 |  |  | 42990.9583 | 71 | 71
2017-09-12 23:30 | 53 | 50 |  |  | 42990.9792 | 67 | 67
2017-09-13 | 48 | 44 |  |  | 42991 | 60 | 60
2017-09-13 00:30 | 43 | 39 |  |  | 42991.0208 | 54 | 54
2017-09-13 01:00 | 39 | 34 |  |  | 42991.0417 | 48 | 48
2017-09-13 01:30 | 37 | 32 |  |  | 42991.0625 | 46 | 46
2017-09-13 02:00 | 37 | 33 |  |  | 42991.0833 | 46 | 46
2017-09-13 02:30 | 38 | 34 |  |  | 42991.1042 | 46 | 46
2017-09-13 03:00 | 37 | 33 |  |  | 42991.125 | 46 | 46
2017-09-13 03:30 | 37 | 34 |  |  | 42991.1458 | 45 | 45
2017-09-13 04:00 | 37 | 33 |  |  | 42991.1667 | 46 | 46
2017-09-13 04:30 | 40 | 36 |  |  | 42991.1875 | 49 | 49
2017-09-13 05:00 | 42 | 38 |  |  | 42991.2083 | 51 | 51
2017-09-13 05:30 | 45 | 42 |  |  | 42991.2292 | 56 | 56
2017-09-13 06:00 | 49 | 48 |  |  | 42991.25 | 63 | 63
2017-09-13 06:30 | 53 | 53 |  |  | 42991.2708 | 70 | 70
2017-09-13 07:00 | 60 | 60 |  |  | 42991.2917 | 80 | 80
2017-09-13 07:30 | 66 | 66 |  |  | 42991.3125 | 89 | 88
2017-09-13 08:00 | 66 | 66 |  |  | 42991.3333 | 91 | 90
2017-09-13 08:30 | 64 | 64 |  |  | 42991.3542 | 90 | 89
2017-09-13 09:00 | 60 | 60 |  |  | 42991.375 | 86 | 85
2017-09-13 09:30 | 58 | 58 |  |  | 42991.3958 | 84 | 82
2017-09-13 10:00 | 57 | 57 |  |  | 42991.4167 | 83 | 81
2017-09-13 10:30 | 56 | 56 |  |  | 42991.4375 | 81 | 79
2017-09-13 11:00 | 55 | 55 |  |  | 42991.4583 | 81 | 79
2017-09-13 11:30 | 55 | 55 |  |  | 42991.4792 | 82 | 79
2017-09-13 12:00 | 52 | 51 |  |  | 42991.5 | 80 | 77
2017-09-13 12:30 | 52 | 52 |  |  | 42991.5208 | 81 | 77
2017-09-13 13:00 | 56 | 56 |  |  | 42991.5417 | 83 | 79
2017-09-13 13:30 | 56 | 56 |  |  | 42991.5625 | 84 | 80
2017-09-13 14:00 | 56 | 56 |  |  | 42991.5833 | 86 | 82
2017-09-13 14:30 | 55 | 55 |  |  | 42991.6042 | 84 | 82
2017-09-13 15:00 | 57 | 57 |  |  | 42991.625 | 85 | 83
2017-09-13 15:30 | 61 | 61 |  |  | 42991.6458 | 91 | 88
2017-09-13 16:00 | 67 | 67 |  |  | 42991.6667 | 95 | 93
2017-09-13 16:30 | 70 | 70 |  |  | 42991.6875 | 96 | 95
2017-09-13 17:00 | 73 | 73 |  |  | 42991.7083 | 98 | 97
2017-09-13 17:30 | 75 | 75 |  |  | 42991.7292 | 98 | 98
2017-09-13 18:00 | 75 | 74 |  |  | 42991.75 | 98 | 97
2017-09-13 18:30 | 78 | 77 |  |  | 42991.7708 | 97 | 96
2017-09-13 19:00 | 79 | 78 |  |  | 42991.7917 | 98 | 97
2017-09-13 19:30 | 76 | 75 |  |  | 42991.8125 | 95 | 94
2017-09-13 20:00 | 74 | 73 |  |  | 42991.8333 | 94 | 93
2017-09-13 20:30 | 74 | 74 |  |  | 42991.8542 | 93 | 92
2017-09-13 21:00 | 72 | 71 |  |  | 42991.875 | 90 | 89
2017-09-13 21:30 | 65 | 65 |  |  | 42991.8958 | 83 | 82
2017-09-13 22:00 | 63 | 63 |  |  | 42991.9167 | 82 | 81
2017-09-13 22:30 | 65 | 64 |  |  | 42991.9375 | 83 | 83
2017-09-13 23:00 | 63 | 62 |  |  | 42991.9583 | 81 | 81
2017-09-13 23:30 | 59 | 58 |  |  | 42991.9792 | 77 | 76
2017-09-14 | 53 | 52 |  |  | 42992 | 70 | 70
2017-09-14 00:30 | 49 | 47 |  |  | 42992.0208 | 63 | 63
2017-09-14 01:00 | 45 | 42 |  |  | 42992.0417 | 58 | 58
2017-09-14 01:30 | 40 | 37 |  |  | 42992.0625 | 52 | 52
2017-09-14 02:00 | 38 | 35 |  |  | 42992.0833 | 51 | 50
2017-09-14 02:30 | 39 | 37 |  |  | 42992.1042 | 52 | 51
2017-09-14 03:00 | 39 | 36 |  |  | 42992.125 | 52 | 51
2017-09-14 03:30 | 39 | 37 |  |  | 42992.1458 | 51 | 51
2017-09-14 04:00 | 38 | 35 |  |  | 42992.1667 | 49 | 49
2017-09-14 04:30 | 39 | 37 |  |  | 42992.1875 | 52 | 51
2017-09-14 05:00 | 41 | 40 |  |  | 42992.2083 | 55 | 54
2017-09-14 05:30 | 45 | 44 |  |  | 42992.2292 | 60 | 59
2017-09-14 06:00 | 48 | 48 |  |  | 42992.25 | 65 | 64
2017-09-14 06:30 | 52 | 51 |  |  | 42992.2708 | 72 | 71
2017-09-14 07:00 | 56 | 56 |  |  | 42992.2917 | 79 | 77
2017-09-14 07:30 | 62 | 62 |  |  | 42992.3125 | 88 | 86
2017-09-14 08:00 | 77 | 77 |  |  | 42992.3333 | 112 | 110
2017-09-14 08:30 | 83 | 83 |  |  | 42992.3542 | 119 | 118
2017-09-14 09:00 | 80 | 80 |  |  | 42992.375 | 115 | 115
2017-09-14 09:30 | 76 | 76 |  |  | 42992.3958 | 109 | 109
2017-09-14 10:00 | 70 | 70 |  |  | 42992.4167 | 104 | 104
2017-09-14 10:30 | 63 | 63 |  |  | 42992.4375 | 95 | 94
2017-09-14 11:00 | 60 | 60 |  |  | 42992.4583 | 94 | 93
2017-09-14 11:30 | 59 | 59 |  |  | 42992.4792 | 93 | 91
2017-09-14 12:00 | 58 | 58 |  |  | 42992.5 | 92 | 91
2017-09-14 12:30 | 59 | 59 |  |  | 42992.5208 | 93 | 92
2017-09-14 13:00 | 58 | 58 |  |  | 42992.5417 | 92 | 90
2017-09-14 13:30 | 48 | 47 |  |  | 42992.5625 | 75 | 74
2017-09-14 14:00 | 49 | 48 |  |  | 42992.5833 | 71 | 71
2017-09-14 14:30 | 55 | 54 |  |  | 42992.6042 | 77 | 77
2017-09-14 15:00 | 58 | 58 |  |  | 42992.625 | 79 | 79
2017-09-14 15:30 | 59 | 59 |  |  | 42992.6458 | 81 | 81
2017-09-14 16:00 | 62 | 62 |  |  | 42992.6667 | 86 | 85
2017-09-14 16:30 | 67 | 67 |  |  | 42992.6875 | 91 | 91
2017-09-14 17:00 | 75 | 75 |  |  | 42992.7083 | 97 | 97
2017-09-14 17:30 | 78 | 77 |  |  | 42992.7292 | 98 | 98
2017-09-14 18:00 | 79 | 78 |  |  | 42992.75 | 98 | 98
2017-09-14 18:30 | 80 | 79 |  |  | 42992.7708 | 98 | 98
2017-09-14 19:00 | 81 | 79 |  |  | 42992.7917 | 97 | 97
2017-09-14 19:30 | 76 | 75 |  |  | 42992.8125 | 94 | 94
2017-09-14 20:00 | 70 | 70 |  |  | 42992.8333 | 91 | 91
2017-09-14 20:30 | 66 | 66 |  |  | 42992.8542 | 87 | 86
2017-09-14 21:00 | 61 | 61 |  |  | 42992.875 | 82 | 81
2017-09-14 21:30 | 59 | 59 |  |  | 42992.8958 | 77 | 75
2017-09-14 22:00 | 58 | 58 |  |  | 42992.9167 | 76 | 75
2017-09-14 22:30 | 58 | 58 |  |  | 42992.9375 | 76 | 75
2017-09-14 23:00 | 56 | 56 |  |  | 42992.9583 | 73 | 72
2017-09-14 23:30 | 51 | 50 |  |  | 42992.9792 | 67 | 67
2017-09-15 | 45 | 45 |  |  | 42993 | 60 | 59
2017-09-15 00:30 | 43 | 42 |  |  | 42993.0208 | 55 | 55
2017-09-15 01:00 | 40 | 38 |  |  | 42993.0417 | 51 | 51
2017-09-15 01:30 | 36 | 34 |  |  | 42993.0625 | 46 | 46
2017-09-15 02:00 | 34 | 33 |  |  | 42993.0833 | 45 | 45
2017-09-15 02:30 | 39 | 33 |  |  | 42993.1042 | 46 | 45
2017-09-15 03:00 | 44 | 33 |  |  | 42993.125 | 45 | 45
2017-09-15 03:30 | 46 | 35 |  |  | 42993.1458 | 46 | 46
2017-09-15 04:00 | 46 | 36 |  |  | 42993.1667 | 47 | 47
2017-09-15 04:30 | 48 | 38 |  |  | 42993.1875 | 50 | 49
2017-09-15 05:00 | 47 | 39 |  |  | 42993.2083 | 50 | 50
2017-09-15 05:30 | 53 | 47 |  |  | 42993.2292 | 58 | 58
2017-09-15 06:00 | 57 | 51 |  |  | 42993.25 | 66 | 66
2017-09-15 06:30 | 62 | 58 |  |  | 42993.2708 | 76 | 76
2017-09-15 07:00 | 67 | 63 |  |  | 42993.2917 | 83 | 83
2017-09-15 07:30 | 68 | 65 |  |  | 42993.3125 | 88 | 87
2017-09-15 08:00 | 64 | 62 |  |  | 42993.3333 | 85 | 85
2017-09-15 08:30 | 61 | 59 |  |  | 42993.3542 | 84 | 83
2017-09-15 09:00 | 58 | 55 |  |  | 42993.375 | 79 | 78
2017-09-15 09:30 | 54 | 51 |  |  | 42993.3958 | 74 | 73
2017-09-15 10:00 | 52 | 49 |  |  | 42993.4167 | 72 | 71
2017-09-15 10:30 | 49 | 47 |  |  | 42993.4375 | 69 | 68
2017-09-15 11:00 | 48 | 46 |  |  | 42993.4583 | 68 | 67
2017-09-15 11:30 | 47 | 45 |  |  | 42993.4792 | 67 | 66
2017-09-15 12:00 | 46 | 44 |  |  | 42993.5 | 67 | 65
2017-09-15 12:30 | 47 | 45 |  |  | 42993.5208 | 68 | 67
2017-09-15 13:00 | 47 | 46 |  |  | 42993.5417 | 69 | 68
2017-09-15 13:30 | 47 | 45 |  |  | 42993.5625 | 69 | 67
2017-09-15 14:00 | 49 | 47 |  |  | 42993.5833 | 71 | 69
2017-09-15 14:30 | 49 | 47 |  |  | 42993.6042 | 69 | 68
2017-09-15 15:00 | 51 | 49 |  |  | 42993.625 | 72 | 70
2017-09-15 15:30 | 53 | 51 |  |  | 42993.6458 | 74 | 73
2017-09-15 16:00 | 56 | 53 |  |  | 42993.6667 | 78 | 77
2017-09-15 16:30 | 59 | 56 |  |  | 42993.6875 | 80 | 80
2017-09-15 17:00 | 63 | 60 |  |  | 42993.7083 | 82 | 82
2017-09-15 17:30 | 66 | 62 |  |  | 42993.7292 | 83 | 83
2017-09-15 18:00 | 66 | 62 |  |  | 42993.75 | 82 | 82
2017-09-15 18:30 | 67 | 63 |  |  | 42993.7708 | 83 | 83
2017-09-15 19:00 | 69 | 65 |  |  | 42993.7917 | 85 | 85
2017-09-15 19:30 | 68 | 64 |  |  | 42993.8125 | 83 | 83
2017-09-15 20:00 | 67 | 63 |  |  | 42993.8333 | 81 | 80
2017-09-15 20:30 | 65 | 61 |  |  | 42993.8542 | 80 | 80
2017-09-15 21:00 | 62 | 57 |  |  | 42993.875 | 75 | 75
2017-09-15 21:30 | 60 | 53 |  |  | 42993.8958 | 71 | 71
2017-09-15 22:00 | 58 | 51 |  |  | 42993.9167 | 69 | 69
2017-09-15 22:30 | 62 | 54 |  |  | 42993.9375 | 73 | 73
2017-09-15 23:00 | 63 | 54 |  |  | 42993.9583 | 73 | 72
2017-09-15 23:30 | 60 | 50 |  |  | 42993.9792 | 69 | 69
2017-09-16 | 56 | 45 |  |  | 42994 | 62 | 62
2017-09-16 00:30 | 49 | 39 |  |  | 42994.0208 | 57 | 56
2017-09-16 01:00 | 42 | 36 |  |  | 42994.0417 | 54 | 51
2017-09-16 01:30 | 40 | 34 |  |  | 42994.0625 | 51 | 49
2017-09-16 02:00 | 39 | 33 |  |  | 42994.0833 | 50 | 48
2017-09-16 02:30 | 37 | 30 |  |  | 42994.1042 | 46 | 44
2017-09-16 03:00 | 36 | 30 |  |  | 42994.125 | 45 | 43
2017-09-16 03:30 | 36 | 30 |  |  | 42994.1458 | 44 | 42
2017-09-16 04:00 | 36 | 30 |  |  | 42994.1667 | 44 | 42
2017-09-16 04:30 | 36 | 31 |  |  | 42994.1875 | 44 | 42
2017-09-16 05:00 | 39 | 34 |  |  | 42994.2083 | 48 | 46
2017-09-16 05:30 | 41 | 37 |  |  | 42994.2292 | 50 | 48
2017-09-16 06:00 | 42 | 39 |  |  | 42994.25 | 53 | 51
2017-09-16 06:30 | 42 | 39 |  |  | 42994.2708 | 53 | 52
2017-09-16 07:00 | 42 | 38 |  |  | 42994.2917 | 54 | 53
2017-09-16 07:30 | 40 | 38 |  |  | 42994.3125 | 54 | 53
2017-09-16 08:00 | 39 | 37 |  |  | 42994.3333 | 53 | 53
2017-09-16 08:30 | 39 | 37 |  |  | 42994.3542 | 53 | 53
2017-09-16 09:00 | 38 | 36 |  |  | 42994.375 | 53 | 53
2017-09-16 09:30 | 37 | 36 |  |  | 42994.3958 | 53 | 53
2017-09-16 10:00 | 36 | 35 |  |  | 42994.4167 | 51 | 51
2017-09-16 10:30 | 36 | 34 |  |  | 42994.4375 | 50 | 50
2017-09-16 11:00 | 34 | 33 |  |  | 42994.4583 | 49 | 49
2017-09-16 11:30 | 35 | 33 |  |  | 42994.4792 | 48 | 48
2017-09-16 12:00 | 34 | 32 |  |  | 42994.5 | 47 | 47
2017-09-16 12:30 | 34 | 32 |  |  | 42994.5208 | 47 | 47
2017-09-16 13:00 | 34 | 32 |  |  | 42994.5417 | 46 | 46
2017-09-16 13:30 | 35 | 33 |  |  | 42994.5625 | 48 | 48
2017-09-16 14:00 | 35 | 33 |  |  | 42994.5833 | 48 | 48
2017-09-16 14:30 | 36 | 34 |  |  | 42994.6042 | 48 | 48
2017-09-16 15:00 | 37 | 35 |  |  | 42994.625 | 52 | 52
2017-09-16 15:30 | 38 | 36 |  |  | 42994.6458 | 54 | 54
2017-09-16 16:00 | 41 | 39 |  |  | 42994.6667 | 57 | 57
2017-09-16 16:30 | 45 | 43 |  |  | 42994.6875 | 61 | 61
2017-09-16 17:00 | 50 | 48 |  |  | 42994.7083 | 66 | 66
2017-09-16 17:30 | 53 | 51 |  |  | 42994.7292 | 69 | 69
2017-09-16 18:00 | 52 | 50 |  |  | 42994.75 | 70 | 70
2017-09-16 18:30 | 58 | 56 |  |  | 42994.7708 | 75 | 75
2017-09-16 19:00 | 61 | 59 |  |  | 42994.7917 | 78 | 77
2017-09-16 19:30 | 60 | 57 |  |  | 42994.8125 | 76 | 75
2017-09-16 20:00 | 58 | 55 |  |  | 42994.8333 | 74 | 73
2017-09-16 20:30 | 57 | 54 |  |  | 42994.8542 | 73 | 72
2017-09-16 21:00 | 54 | 51 |  |  | 42994.875 | 69 | 68
2017-09-16 21:30 | 52 | 48 |  |  | 42994.8958 | 65 | 64
2017-09-16 22:00 | 49 | 46 |  |  | 42994.9167 | 65 | 64
2017-09-16 22:30 | 53 | 49 |  |  | 42994.9375 | 69 | 68
2017-09-16 23:00 | 53 | 49 |  |  | 42994.9583 | 68 | 67
2017-09-16 23:30 | 51 | 47 |  |  | 42994.9792 | 66 | 64
2017-09-17 | 46 | 41 |  |  | 42995 | 61 | 59
2017-09-17 00:30 | 41 | 35 |  |  | 42995.0208 | 54 | 52
2017-09-17 01:00 | 37 | 30 |  |  | 42995.0417 | 48 | 45
2017-09-17 01:30 | 35 | 28 |  |  | 42995.0625 | 46 | 44
2017-09-17 02:00 | 36 | 30 |  |  | 42995.0833 | 46 | 45
2017-09-17 02:30 | 36 | 30 |  |  | 42995.1042 | 46 | 44
2017-09-17 03:00 | 36 | 29 |  |  | 42995.125 | 45 | 44
2017-09-17 03:30 | 36 | 29 |  |  | 42995.1458 | 44 | 42
2017-09-17 04:00 | 35 | 29 |  |  | 42995.1667 | 42 | 41
2017-09-17 04:30 | 34 | 28 |  |  | 42995.1875 | 41 | 40
2017-09-17 05:00 | 35 | 29 |  |  | 42995.2083 | 43 | 41
2017-09-17 05:30 | 34 | 29 |  |  | 42995.2292 | 43 | 42
2017-09-17 06:00 | 34 | 28 |  |  | 42995.25 | 43 | 42
2017-09-17 06:30 | 32 | 25 |  |  | 42995.2708 | 40 | 39
2017-09-17 07:00 | 31 | 25 |  |  | 42995.2917 | 40 | 39
2017-09-17 07:30 | 30 | 25 |  |  | 42995.3125 | 41 | 40
2017-09-17 08:00 | 33 | 28 |  |  | 42995.3333 | 45 | 44
2017-09-17 08:30 | 33 | 29 |  |  | 42995.3542 | 45 | 44
2017-09-17 09:00 | 34 | 29 |  |  | 42995.375 | 46 | 45
2017-09-17 09:30 | 36 | 33 |  |  | 42995.3958 | 50 | 50
2017-09-17 10:00 | 35 | 31 |  |  | 42995.4167 | 51 | 51
2017-09-17 10:30 | 37 | 34 |  |  | 42995.4375 | 52 | 52
2017-09-17 11:00 | 40 | 37 |  |  | 42995.4583 | 54 | 54
2017-09-17 11:30 | 39 | 36 |  |  | 42995.4792 | 52 | 52
2017-09-17 12:00 | 36 | 32 |  |  | 42995.5 | 47 | 47
2017-09-17 12:30 | 36 | 33 |  |  | 42995.5208 | 49 | 49
2017-09-17 13:00 | 38 | 35 |  |  | 42995.5417 | 48 | 48
2017-09-17 13:30 | 39 | 37 |  |  | 42995.5625 | 51 | 51
2017-09-17 14:00 | 38 | 35 |  |  | 42995.5833 | 48 | 48
2017-09-17 14:30 | 38 | 34 |  |  | 42995.6042 | 49 | 49
2017-09-17 15:00 | 41 | 37 |  |  | 42995.625 | 51 | 51
2017-09-17 15:30 | 40 | 37 |  |  | 42995.6458 | 54 | 54
2017-09-17 16:00 | 40 | 37 |  |  | 42995.6667 | 56 | 56
2017-09-17 16:30 | 42 | 40 |  |  | 42995.6875 | 58 | 58
2017-09-17 17:00 | 47 | 44 |  |  | 42995.7083 | 63 | 63
2017-09-17 17:30 | 49 | 47 |  |  | 42995.7292 | 65 | 65
2017-09-17 18:00 | 51 | 49 |  |  | 42995.75 | 68 | 67
2017-09-17 18:30 | 56 | 53 |  |  | 42995.7708 | 73 | 72
2017-09-17 19:00 | 58 | 56 |  |  | 42995.7917 | 75 | 74
2017-09-17 19:30 | 56 | 53 |  |  | 42995.8125 | 74 | 73
2017-09-17 20:00 | 56 | 53 |  |  | 42995.8333 | 73 | 72
2017-09-17 20:30 | 55 | 53 |  |  | 42995.8542 | 73 | 73
2017-09-17 21:00 | 54 | 51 |  |  | 42995.875 | 70 | 70
2017-09-17 21:30 | 52 | 49 |  |  | 42995.8958 | 67 | 66
2017-09-17 22:00 | 49 | 46 |  |  | 42995.9167 | 66 | 66
2017-09-17 22:30 | 52 | 48 |  |  | 42995.9375 | 69 | 68
2017-09-17 23:00 | 54 | 50 |  |  | 42995.9583 | 69 | 68
2017-09-17 23:30 | 50 | 46 |  |  | 42995.9792 | 64 | 63
2017-09-18 | 46 | 41 |  |  | 42996 | 59 | 58
2017-09-18 00:30 | 42 | 37 |  |  | 42996.0208 | 54 | 52
2017-09-18 01:00 | 40 | 34 |  |  | 42996.0417 | 50 | 48
2017-09-18 01:30 | 37 | 31 |  |  | 42996.0625 | 46 | 45
2017-09-18 02:00 | 35 | 30 |  |  | 42996.0833 | 46 | 45
2017-09-18 02:30 | 36 | 30 |  |  | 42996.1042 | 46 | 45
2017-09-18 03:00 | 36 | 31 |  |  | 42996.125 | 46 | 45
2017-09-18 03:30 | 36 | 32 |  |  | 42996.1458 | 47 | 45
2017-09-18 04:00 | 37 | 33 |  |  | 42996.1667 | 46 | 45
2017-09-18 04:30 | 37 | 32 |  |  | 42996.1875 | 46 | 45
2017-09-18 05:00 | 39 | 34 |  |  | 42996.2083 | 49 | 48
2017-09-18 05:30 | 43 | 40 |  |  | 42996.2292 | 55 | 55
2017-09-18 06:00 | 46 | 44 |  |  | 42996.25 | 61 | 61
2017-09-18 06:30 | 52 | 51 |  |  | 42996.2708 | 69 | 69
2017-09-18 07:00 | 56 | 56 |  |  | 42996.2917 | 76 | 76
2017-09-18 07:30 | 57 | 57 |  |  | 42996.3125 | 79 | 79
2017-09-18 08:00 | 57 | 57 |  |  | 42996.3333 | 79 | 79
2017-09-18 08:30 | 57 | 56 |  |  | 42996.3542 | 79 | 79
2017-09-18 09:00 | 57 | 57 |  |  | 42996.375 | 81 | 81
2017-09-18 09:30 | 59 | 59 |  |  | 42996.3958 | 82 | 81
2017-09-18 10:00 | 60 | 58 |  |  | 42996.4167 | 80 | 79
2017-09-18 10:30 | 57 | 55 |  |  | 42996.4375 | 77 | 76
2017-09-18 11:00 | 55 | 53 |  |  | 42996.4583 | 76 | 75
2017-09-18 11:30 | 54 | 52 |  |  | 42996.4792 | 74 | 73
2017-09-18 12:00 | 53 | 51 |  |  | 42996.5 | 72 | 70
2017-09-18 12:30 | 53 | 50 |  |  | 42996.5208 | 72 | 71
2017-09-18 13:00 | 55 | 53 |  |  | 42996.5417 | 73 | 72
2017-09-18 13:30 | 55 | 53 |  |  | 42996.5625 | 75 | 74
2017-09-18 14:00 | 56 | 54 |  |  | 42996.5833 | 75 | 74
2017-09-18 14:30 | 56 | 53 |  |  | 42996.6042 | 75 | 74
2017-09-18 15:00 | 57 | 54 |  |  | 42996.625 | 76 | 74
2017-09-18 15:30 | 57 | 54 |  |  | 42996.6458 | 76 | 75
2017-09-18 16:00 | 61 | 59 |  |  | 42996.6667 | 81 | 81
2017-09-18 16:30 | 64 | 63 |  |  | 42996.6875 | 85 | 84
2017-09-18 17:00 | 67 | 66 |  |  | 42996.7083 | 88 | 87
2017-09-18 17:30 | 70 | 70 |  |  | 42996.7292 | 90 | 90
2017-09-18 18:00 | 70 | 70 |  |  | 42996.75 | 90 | 90
2017-09-18 18:30 | 70 | 70 |  |  | 42996.7708 | 89 | 89
2017-09-18 19:00 | 72 | 72 |  |  | 42996.7917 | 90 | 90
2017-09-18 19:30 | 69 | 69 |  |  | 42996.8125 | 86 | 86
2017-09-18 20:00 | 66 | 66 |  |  | 42996.8333 | 83 | 82
2017-09-18 20:30 | 66 | 65 |  |  | 42996.8542 | 83 | 83
2017-09-18 21:00 | 62 | 61 |  |  | 42996.875 | 78 | 78
2017-09-18 21:30 | 57 | 56 |  |  | 42996.8958 | 71 | 71
2017-09-18 22:00 | 53 | 52 |  |  | 42996.9167 | 69 | 69
2017-09-18 22:30 | 54 | 53 |  |  | 42996.9375 | 72 | 71
2017-09-18 23:00 | 55 | 54 |  |  | 42996.9583 | 70 | 70
2017-09-18 23:30 | 51 | 51 |  |  | 42996.9792 | 66 | 66
2017-09-19 | 47 | 47 |  |  | 42997 | 62 | 62
2017-09-19 00:30 | 42 | 41 |  |  | 42997.0208 | 55 | 55
2017-09-19 01:00 | 39 | 38 |  |  | 42997.0417 | 50 | 50
2017-09-19 01:30 | 36 | 35 |  |  | 42997.0625 | 48 | 48
2017-09-19 02:00 | 37 | 36 |  |  | 42997.0833 | 47 | 47
2017-09-19 02:30 | 39 | 35 |  |  | 42997.1042 | 47 | 47
2017-09-19 03:00 | 37 | 35 |  |  | 42997.125 | 46 | 45
2017-09-19 03:30 | 37 | 35 |  |  | 42997.1458 | 46 | 45
2017-09-19 04:00 | 36 | 34 |  |  | 42997.1667 | 45 | 45
2017-09-19 04:30 | 37 | 34 |  |  | 42997.1875 | 46 | 45
2017-09-19 05:00 | 38 | 35 |  |  | 42997.2083 | 47 | 47
2017-09-19 05:30 | 44 | 40 |  |  | 42997.2292 | 53 | 53
2017-09-19 06:00 | 48 | 45 |  |  | 42997.25 | 59 | 59
2017-09-19 06:30 | 52 | 48 |  |  | 42997.2708 | 65 | 65
2017-09-19 07:00 | 51 | 46 |  |  | 42997.2917 | 69 | 69
2017-09-19 07:30 | 48 | 45 |  |  | 42997.3125 | 74 | 74
2017-09-19 08:00 | 45 | 42 |  |  | 42997.3333 | 73 | 73
2017-09-19 08:30 | 23 | 16 |  |  | 42997.3542 | 62 | 62
2017-09-19 09:00 | 21 | 15 |  |  | 42997.375 | 61 | 61
2017-09-19 09:30 | 19 | 17 |  |  | 42997.3958 | 62 | 61
2017-09-19 10:00 | 15 | 14 |  |  | 42997.4167 | 60 | 59
2017-09-19 10:30 | 15 | 14 |  |  | 42997.4375 | 60 | 59
2017-09-19 11:00 | 17 | 16 |  |  | 42997.4583 | 61 | 60
2017-09-19 11:30 | 16 | 15 |  |  | 42997.4792 | 62 | 61
2017-09-19 12:00 | 16 | 15 |  |  | 42997.5 | 62 | 62
2017-09-19 12:30 | 16 | 15 |  |  | 42997.5208 | 62 | 62
2017-09-19 13:00 | 16 | 16 |  |  | 42997.5417 | 63 | 63
2017-09-19 13:30 | 16 | 16 |  |  | 42997.5625 | 63 | 63
2017-09-19 14:00 | 15 | 15 |  |  | 42997.5833 | 63 | 63
2017-09-19 14:30 | 15 | 15 |  |  | 42997.6042 | 63 | 63
2017-09-19 15:00 | 19 | 19 |  |  | 42997.625 | 63 | 63
2017-09-19 15:30 | 19 | 19 |  |  | 42997.6458 | 63 | 63
2017-09-19 16:00 | 18 | 18 |  |  | 42997.6667 | 64 | 64
2017-09-19 16:30 | 31 | 31 |  |  | 42997.6875 | 70 | 70
2017-09-19 17:00 | 35 | 35 |  |  | 42997.7083 | 74 | 74
2017-09-19 17:30 | 37 | 37 |  |  | 42997.7292 | 74 | 74
2017-09-19 18:00 | 38 | 37 |  |  | 42997.75 | 74 | 74
2017-09-19 18:30 | 37 | 37 |  |  | 42997.7708 | 73 | 72
2017-09-19 19:00 | 39 | 39 |  |  | 42997.7917 | 75 | 74
2017-09-19 19:30 | 38 | 37 |  |  | 42997.8125 | 73 | 73
2017-09-19 20:00 | 36 | 36 |  |  | 42997.8333 | 70 | 70
2017-09-19 20:30 | 35 | 35 |  |  | 42997.8542 | 70 | 70
2017-09-19 21:00 | 33 | 33 |  |  | 42997.875 | 65 | 65
2017-09-19 21:30 | 31 | 30 |  |  | 42997.8958 | 62 | 62
2017-09-19 22:00 | 29 | 29 |  |  | 42997.9167 | 61 | 61
2017-09-19 22:30 | 29 | 28 |  |  | 42997.9375 | 61 | 61
2017-09-19 23:00 | 29 | 29 |  |  | 42997.9583 | 60 | 60
2017-09-19 23:30 | 27 | 27 |  |  | 42997.9792 | 56 | 56
2017-09-20 | 25 | 25 |  |  | 42998 | 52 | 52
2017-09-20 00:30 | 20 | 20 |  |  | 42998.0208 | 45 | 45
2017-09-20 01:00 | 17 | 17 |  |  | 42998.0417 | 41 | 41
2017-09-20 01:30 | 15 | 15 |  |  | 42998.0625 | 38 | 38
2017-09-20 02:00 | 14 | 14 |  |  | 42998.0833 | 38 | 37
2017-09-20 02:30 | 14 | 14 |  |  | 42998.1042 | 37 | 37
2017-09-20 03:00 | 15 | 15 |  |  | 42998.125 | 37 | 37
2017-09-20 03:30 | 15 | 15 |  |  | 42998.1458 | 37 | 37
2017-09-20 04:00 | 15 | 15 |  |  | 42998.1667 | 37 | 37
2017-09-20 04:30 | 14 | 14 |  |  | 42998.1875 | 37 | 37
2017-09-20 05:00 | 15 | 15 |  |  | 42998.2083 | 40 | 40
2017-09-20 05:30 | 16 | 16 |  |  | 42998.2292 | 41 | 41
2017-09-20 06:00 | 21 | 21 |  |  | 42998.25 | 47 | 47
2017-09-20 06:30 | 26 | 25 |  |  | 42998.2708 | 56 | 55
2017-09-20 07:00 | 31 | 30 |  |  | 42998.2917 | 63 | 62
2017-09-20 07:30 | 31 | 31 |  |  | 42998.3125 | 66 | 66
2017-09-20 08:00 | 32 | 31 |  |  | 42998.3333 | 68 | 67
2017-09-20 08:30 | 34 | 33 |  |  | 42998.3542 | 70 | 69
2017-09-20 09:00 | 34 | 33 |  |  | 42998.375 | 70 | 68
2017-09-20 09:30 | 33 | 32 |  |  | 42998.3958 | 67 | 66
2017-09-20 10:00 | 34 | 32 |  |  | 42998.4167 | 67 | 66
2017-09-20 10:30 | 33 | 32 |  |  | 42998.4375 | 68 | 67
2017-09-20 11:00 | 33 | 32 |  |  | 42998.4583 | 67 | 66
2017-09-20 11:30 | 33 | 32 |  |  | 42998.4792 | 67 | 66
2017-09-20 12:00 | 33 | 31 |  |  | 42998.5 | 67 | 66
2017-09-20 12:30 | 33 | 31 |  |  | 42998.5208 | 66 | 65
2017-09-20 13:00 | 34 | 32 |  |  | 42998.5417 | 67 | 66
2017-09-20 13:30 | 34 | 33 |  |  | 42998.5625 | 68 | 66
2017-09-20 14:00 | 35 | 33 |  |  | 42998.5833 | 69 | 67
2017-09-20 14:30 | 34 | 32 |  |  | 42998.6042 | 68 | 66
2017-09-20 15:00 | 32 | 30 |  |  | 42998.625 | 67 | 66
2017-09-20 15:30 | 33 | 31 |  |  | 42998.6458 | 69 | 68
2017-09-20 16:00 | 33 | 32 |  |  | 42998.6667 | 71 | 70
2017-09-20 16:30 | 34 | 33 |  |  | 42998.6875 | 71 | 70
2017-09-20 17:00 | 36 | 35 |  |  | 42998.7083 | 73 | 72
2017-09-20 17:30 | 37 | 37 |  |  | 42998.7292 | 73 | 73
2017-09-20 18:00 | 37 | 36 |  |  | 42998.75 | 72 | 72
2017-09-20 18:30 | 36 | 35 |  |  | 42998.7708 | 70 | 70
2017-09-20 19:00 | 38 | 37 |  |  | 42998.7917 | 72 | 72
2017-09-20 19:30 | 36 | 36 |  |  | 42998.8125 | 70 | 70
2017-09-20 20:00 | 36 | 35 |  |  | 42998.8333 | 71 | 71
2017-09-20 20:30 | 36 | 35 |  |  | 42998.8542 | 70 | 69
2017-09-20 21:00 | 33 | 31 |  |  | 42998.875 | 64 | 64
2017-09-20 21:30 | 30 | 29 |  |  | 42998.8958 | 59 | 59
2017-09-20 22:00 | 29 | 28 |  |  | 42998.9167 | 60 | 60
2017-09-20 22:30 | 28 | 28 |  |  | 42998.9375 | 61 | 61
2017-09-20 23:00 | 28 | 28 |  |  | 42998.9583 | 58 | 58
2017-09-20 23:30 | 23 | 23 |  |  | 42998.9792 | 53 | 53
2017-09-21 | 20 | 20 |  |  | 42999 | 48 | 48
2017-09-21 00:30 | 15 | 15 |  |  | 42999.0208 | 41 | 41
2017-09-21 01:00 | 15 | 15 |  |  | 42999.0417 | 39 | 39
2017-09-21 01:30 | 13 | 13 |  |  | 42999.0625 | 36 | 36
2017-09-21 02:00 | 13 | 13 |  |  | 42999.0833 | 36 | 36
2017-09-21 02:30 | 14 | 14 |  |  | 42999.1042 | 38 | 38
2017-09-21 03:00 | 14 | 14 |  |  | 42999.125 | 36 | 36
2017-09-21 03:30 | 13 | 13 |  |  | 42999.1458 | 37 | 37
2017-09-21 04:00 | 13 | 13 |  |  | 42999.1667 | 36 | 36
2017-09-21 04:30 | 14 | 14 |  |  | 42999.1875 | 37 | 37
2017-09-21 05:00 | 16 | 16 |  |  | 42999.2083 | 39 | 39
2017-09-21 05:30 | 17 | 17 |  |  | 42999.2292 | 42 | 42
2017-09-21 06:00 | 21 | 21 |  |  | 42999.25 | 47 | 47
2017-09-21 06:30 | 25 | 25 |  |  | 42999.2708 | 56 | 56
2017-09-21 07:00 | 29 | 29 |  |  | 42999.2917 | 64 | 64
2017-09-21 07:30 | 32 | 31 |  |  | 42999.3125 | 68 | 68
2017-09-21 08:00 | 33 | 31 |  |  | 42999.3333 | 70 | 70
2017-09-21 08:30 | 33 | 31 |  |  | 42999.3542 | 70 | 69
2017-09-21 09:00 | 34 | 32 |  |  | 42999.375 | 72 | 72
2017-09-21 09:30 | 40 | 37 |  |  | 42999.3958 | 76 | 75
2017-09-21 10:00 | 38 | 36 |  |  | 42999.4167 | 75 | 74
2017-09-21 10:30 | 37 | 34 |  |  | 42999.4375 | 72 | 70
2017-09-21 11:00 | 35 | 32 |  |  | 42999.4583 | 70 | 68
2017-09-21 11:30 | 35 | 33 |  |  | 42999.4792 | 70 | 70
2017-09-21 12:00 | 34 | 32 |  |  | 42999.5 | 71 | 71
2017-09-21 12:30 | 34 | 33 |  |  | 42999.5208 | 70 | 70
2017-09-21 13:00 | 33 | 33 |  |  | 42999.5417 | 70 | 70
2017-09-21 13:30 | 34 | 33 |  |  | 42999.5625 | 72 | 72
2017-09-21 14:00 | 34 | 33 |  |  | 42999.5833 | 72 | 72
2017-09-21 14:30 | 34 | 33 |  |  | 42999.6042 | 71 | 71
2017-09-21 15:00 | 32 | 31 |  |  | 42999.625 | 70 | 70
2017-09-21 15:30 | 33 | 32 |  |  | 42999.6458 | 71 | 71
2017-09-21 16:00 | 35 | 35 |  |  | 42999.6667 | 73 | 73
2017-09-21 16:30 | 37 | 37 |  |  | 42999.6875 | 75 | 75
2017-09-21 17:00 | 39 | 39 |  |  | 42999.7083 | 77 | 77
2017-09-21 17:30 | 40 | 40 |  |  | 42999.7292 | 78 | 78
2017-09-21 18:00 | 40 | 40 |  |  | 42999.75 | 79 | 79
2017-09-21 18:30 | 41 | 41 |  |  | 42999.7708 | 78 | 78
2017-09-21 19:00 | 43 | 43 |  |  | 42999.7917 | 79 | 78
2017-09-21 19:30 | 42 | 42 |  |  | 42999.8125 | 77 | 77
2017-09-21 20:00 | 41 | 41 |  |  | 42999.8333 | 77 | 77
2017-09-21 20:30 | 40 | 40 |  |  | 42999.8542 | 74 | 74
2017-09-21 21:00 | 38 | 37 |  |  | 42999.875 | 70 | 69
2017-09-21 21:30 | 30 | 29 |  |  | 42999.8958 | 63 | 63
2017-09-21 22:00 | 27 | 26 |  |  | 42999.9167 | 61 | 61
2017-09-21 22:30 | 29 | 28 |  |  | 42999.9375 | 64 | 63
2017-09-21 23:00 | 29 | 28 |  |  | 42999.9583 | 61 | 61
2017-09-21 23:30 | 25 | 24 |  |  | 42999.9792 | 57 | 57
2017-09-22 | 21 | 21 |  |  | 43000 | 53 | 52
2017-09-22 00:30 | 19 | 19 |  |  | 43000.0208 | 47 | 47
2017-09-22 01:00 | 15 | 15 |  |  | 43000.0417 | 43 | 43
2017-09-22 01:30 | 13 | 13 |  |  | 43000.0625 | 40 | 40
2017-09-22 02:00 | 13 | 13 |  |  | 43000.0833 | 39 | 39
2017-09-22 02:30 | 14 | 14 |  |  | 43000.1042 | 40 | 40
2017-09-22 03:00 | 15 | 15 |  |  | 43000.125 | 41 | 41
2017-09-22 03:30 | 16 | 16 |  |  | 43000.1458 | 41 | 41
2017-09-22 04:00 | 16 | 15 |  |  | 43000.1667 | 40 | 40
2017-09-22 04:30 | 16 | 16 |  |  | 43000.1875 | 41 | 41
2017-09-22 05:00 | 17 | 17 |  |  | 43000.2083 | 42 | 41
2017-09-22 05:30 | 17 | 17 |  |  | 43000.2292 | 46 | 45
2017-09-22 06:00 | 21 | 20 |  |  | 43000.25 | 51 | 50
2017-09-22 06:30 | 24 | 23 |  |  | 43000.2708 | 57 | 56
2017-09-22 07:00 | 30 | 29 |  |  | 43000.2917 | 66 | 65
2017-09-22 07:30 | 31 | 30 |  |  | 43000.3125 | 69 | 68
2017-09-22 08:00 | 30 | 29 |  |  | 43000.3333 | 70 | 69
2017-09-22 08:30 | 33 | 32 |  |  | 43000.3542 | 72 | 71
2017-09-22 09:00 | 33 | 32 |  |  | 43000.375 | 71 | 71
2017-09-22 09:30 | 35 | 35 |  |  | 43000.3958 | 71 | 71
2017-09-22 10:00 | 35 | 35 |  |  | 43000.4167 | 71 | 71
2017-09-22 10:30 | 33 | 32 |  |  | 43000.4375 | 69 | 69
2017-09-22 11:00 | 33 | 32 |  |  | 43000.4583 | 69 | 68
2017-09-22 11:30 | 33 | 32 |  |  | 43000.4792 | 70 | 69
2017-09-22 12:00 | 32 | 31 |  |  | 43000.5 | 69 | 69
2017-09-22 12:30 | 31 | 30 |  |  | 43000.5208 | 68 | 68
2017-09-22 13:00 | 31 | 31 |  |  | 43000.5417 | 68 | 68
2017-09-22 13:30 | 49 | 49 |  |  | 43000.5625 | 76 | 76
2017-09-22 14:00 | 59 | 59 |  |  | 43000.5833 | 83 | 82
2017-09-22 14:30 | 59 | 58 |  |  | 43000.6042 | 82 | 82
2017-09-22 15:00 | 65 | 65 |  |  | 43000.625 | 90 | 89
2017-09-22 15:30 | 72 | 72 |  |  | 43000.6458 | 95 | 95
2017-09-22 16:00 | 75 | 75 |  |  | 43000.6667 | 98 | 98
2017-09-22 16:30 | 73 | 73 |  |  | 43000.6875 | 95 | 95
2017-09-22 17:00 | 70 | 70 |  |  | 43000.7083 | 93 | 93
2017-09-22 17:30 | 70 | 70 |  |  | 43000.7292 | 91 | 91
2017-09-22 18:00 | 67 | 67 |  |  | 43000.75 | 87 | 86
2017-09-22 18:30 | 66 | 66 |  |  | 43000.7708 | 84 | 84
2017-09-22 19:00 | 67 | 67 |  |  | 43000.7917 | 84 | 84
2017-09-22 19:30 | 67 | 67 |  |  | 43000.8125 | 84 | 84
2017-09-22 20:00 | 66 | 66 |  |  | 43000.8333 | 83 | 83
2017-09-22 20:30 | 62 | 62 |  |  | 43000.8542 | 78 | 78
2017-09-22 21:00 | 58 | 58 |  |  | 43000.875 | 73 | 73
2017-09-22 21:30 | 53 | 53 |  |  | 43000.8958 | 68 | 68
2017-09-22 22:00 | 49 | 49 |  |  | 43000.9167 | 66 | 66
2017-09-22 22:30 | 51 | 51 |  |  | 43000.9375 | 69 | 68
2017-09-22 23:00 | 53 | 53 |  |  | 43000.9583 | 69 | 69
2017-09-22 23:30 | 50 | 50 |  |  | 43000.9792 | 66 | 66
2017-09-23 | 45 | 45 |  |  | 43001 | 60 | 60
2017-09-23 00:30 | 40 | 40 |  |  | 43001.0208 | 54 | 54
2017-09-23 01:00 | 37 | 37 |  |  | 43001.0417 | 49 | 49
2017-09-23 01:30 | 34 | 34 |  |  | 43001.0625 | 46 | 46
2017-09-23 02:00 | 33 | 33 |  |  | 43001.0833 | 46 | 46
2017-09-23 02:30 | 34 | 34 |  |  | 43001.1042 | 45 | 45
2017-09-23 03:00 | 33 | 33 |  |  | 43001.125 | 44 | 44
2017-09-23 03:30 | 31 | 31 |  |  | 43001.1458 | 43 | 43
2017-09-23 04:00 | 30 | 30 |  |  | 43001.1667 | 42 | 42
2017-09-23 04:30 | 31 | 31 |  |  | 43001.1875 | 43 | 43
2017-09-23 05:00 | 33 | 33 |  |  | 43001.2083 | 44 | 44
2017-09-23 05:30 | 33 | 33 |  |  | 43001.2292 | 44 | 44
2017-09-23 06:00 | 32 | 32 |  |  | 43001.25 | 45 | 45
2017-09-23 06:30 | 32 | 31 |  |  | 43001.2708 | 44 | 44
2017-09-23 07:00 | 33 | 32 |  |  | 43001.2917 | 46 | 46
2017-09-23 07:30 | 32 | 32 |  |  | 43001.3125 | 48 | 48
2017-09-23 08:00 | 34 | 34 |  |  | 43001.3333 | 50 | 50
2017-09-23 08:30 | 35 | 35 |  |  | 43001.3542 | 53 | 53
2017-09-23 09:00 | 37 | 37 |  |  | 43001.375 | 55 | 55
2017-09-23 09:30 | 37 | 37 |  |  | 43001.3958 | 56 | 55
2017-09-23 10:00 | 37 | 37 |  |  | 43001.4167 | 55 | 55
2017-09-23 10:30 | 36 | 36 |  |  | 43001.4375 | 53 | 53
2017-09-23 11:00 | 33 | 33 |  |  | 43001.4583 | 49 | 49
2017-09-23 11:30 | 32 | 32 |  |  | 43001.4792 | 48 | 48
2017-09-23 12:00 | 34 | 34 |  |  | 43001.5 | 48 | 48
2017-09-23 12:30 | 33 | 33 |  |  | 43001.5208 | 48 | 48
2017-09-23 13:00 | 35 | 35 |  |  | 43001.5417 | 51 | 51
2017-09-23 13:30 | 39 | 39 |  |  | 43001.5625 | 54 | 53
2017-09-23 14:00 | 38 | 38 |  |  | 43001.5833 | 52 | 52
2017-09-23 14:30 | 42 | 41 |  |  | 43001.6042 | 55 | 55
2017-09-23 15:00 | 41 | 41 |  |  | 43001.625 | 53 | 53
2017-09-23 15:30 | 39 | 39 |  |  | 43001.6458 | 52 | 52
2017-09-23 16:00 | 40 | 40 |  |  | 43001.6667 | 54 | 54
2017-09-23 16:30 | 44 | 43 |  |  | 43001.6875 | 58 | 58
2017-09-23 17:00 | 49 | 48 |  |  | 43001.7083 | 64 | 64
2017-09-23 17:30 | 51 | 51 |  |  | 43001.7292 | 67 | 66
2017-09-23 18:00 | 50 | 50 |  |  | 43001.75 | 67 | 67
2017-09-23 18:30 | 53 | 53 |  |  | 43001.7708 | 71 | 71
2017-09-23 19:00 | 56 | 56 |  |  | 43001.7917 | 72 | 72
2017-09-23 19:30 | 57 | 56 |  |  | 43001.8125 | 73 | 73
2017-09-23 20:00 | 57 | 57 |  |  | 43001.8333 | 73 | 73
2017-09-23 20:30 | 55 | 55 |  |  | 43001.8542 | 72 | 72
2017-09-23 21:00 | 53 | 53 |  |  | 43001.875 | 68 | 68
2017-09-23 21:30 | 49 | 49 |  |  | 43001.8958 | 63 | 63
2017-09-23 22:00 | 46 | 46 |  |  | 43001.9167 | 62 | 62
2017-09-23 22:30 | 46 | 45 |  |  | 43001.9375 | 63 | 63
2017-09-23 23:00 | 45 | 44 |  |  | 43001.9583 | 60 | 60
2017-09-23 23:30 | 41 | 41 |  |  | 43001.9792 | 56 | 56
2017-09-24 | 38 | 37 |  |  | 43002 | 52 | 52
2017-09-24 00:30 | 33 | 32 |  |  | 43002.0208 | 47 | 47
2017-09-24 01:00 | 30 | 29 |  |  | 43002.0417 | 43 | 43
2017-09-24 01:30 | 30 | 29 |  |  | 43002.0625 | 42 | 42
2017-09-24 02:00 | 30 | 29 |  |  | 43002.0833 | 42 | 42
2017-09-24 02:30 | 32 | 31 |  |  | 43002.1042 | 43 | 43
2017-09-24 03:00 | 31 | 30 |  |  | 43002.125 | 42 | 42
2017-09-24 03:30 | 31 | 31 |  |  | 43002.1458 | 43 | 43
2017-09-24 04:00 | 33 | 33 |  |  | 43002.1667 | 44 | 44
2017-09-24 04:30 | 32 | 32 |  |  | 43002.1875 | 45 | 45
2017-09-24 05:00 | 31 | 31 |  |  | 43002.2083 | 45 | 45
2017-09-24 05:30 | 32 | 31 |  |  | 43002.2292 | 45 | 45
2017-09-24 06:00 | 30 | 30 |  |  | 43002.25 | 44 | 44
2017-09-24 06:30 | 31 | 31 |  |  | 43002.2708 | 46 | 46
2017-09-24 07:00 | 31 | 31 |  |  | 43002.2917 | 46 | 45
2017-09-24 07:30 | 31 | 30 |  |  | 43002.3125 | 46 | 46
2017-09-24 08:00 | 29 | 29 |  |  | 43002.3333 | 46 | 45
2017-09-24 08:30 | 30 | 30 |  |  | 43002.3542 | 47 | 47
2017-09-24 09:00 | 31 | 31 |  |  | 43002.375 | 49 | 48
2017-09-24 09:30 | 32 | 32 |  |  | 43002.3958 | 51 | 50
2017-09-24 10:00 | 31 | 31 |  |  | 43002.4167 | 50 | 49
2017-09-24 10:30 | 32 | 32 |  |  | 43002.4375 | 50 | 48
2017-09-24 11:00 | 32 | 31 |  |  | 43002.4583 | 49 | 47
2017-09-24 11:30 | 34 | 33 |  |  | 43002.4792 | 49 | 47
2017-09-24 12:00 | 33 | 32 |  |  | 43002.5 | 49 | 47
2017-09-24 12:30 | 32 | 32 |  |  | 43002.5208 | 48 | 46
2017-09-24 13:00 | 34 | 33 |  |  | 43002.5417 | 49 | 47
2017-09-24 13:30 | 36 | 36 |  |  | 43002.5625 | 51 | 49
2017-09-24 14:00 | 38 | 37 |  |  | 43002.5833 | 52 | 51
2017-09-24 14:30 | 39 | 39 |  |  | 43002.6042 | 52 | 51
2017-09-24 15:00 | 39 | 39 |  |  | 43002.625 | 54 | 53
2017-09-24 15:30 | 40 | 40 |  |  | 43002.6458 | 56 | 55
2017-09-24 16:00 | 44 | 44 |  |  | 43002.6667 | 59 | 59
2017-09-24 16:30 | 49 | 48 |  |  | 43002.6875 | 64 | 64
2017-09-24 17:00 | 52 | 52 |  |  | 43002.7083 | 68 | 68
2017-09-24 17:30 | 55 | 55 |  |  | 43002.7292 | 70 | 70
2017-09-24 18:00 | 57 | 57 |  |  | 43002.75 | 74 | 74
2017-09-24 18:30 | 59 | 59 |  |  | 43002.7708 | 77 | 77
2017-09-24 19:00 | 62 | 61 |  |  | 43002.7917 | 80 | 80
2017-09-24 19:30 | 60 | 60 |  |  | 43002.8125 | 79 | 79
2017-09-24 20:00 | 59 | 59 |  |  | 43002.8333 | 77 | 77
2017-09-24 20:30 | 59 | 59 |  |  | 43002.8542 | 77 | 77
2017-09-24 21:00 | 55 | 55 |  |  | 43002.875 | 72 | 72
2017-09-24 21:30 | 52 | 51 |  |  | 43002.8958 | 70 | 70
2017-09-24 22:00 | 49 | 48 |  |  | 43002.9167 | 69 | 69
2017-09-24 22:30 | 50 | 49 |  |  | 43002.9375 | 69 | 69
2017-09-24 23:00 | 49 | 48 |  |  | 43002.9583 | 67 | 67
2017-09-24 23:30 | 46 | 45 |  |  | 43002.9792 | 62 | 62
2017-09-25 | 41 | 41 |  |  | 43003 | 57 | 57
2017-09-25 00:30 | 37 | 36 |  |  | 43003.0208 | 53 | 53
2017-09-25 01:00 | 34 | 33 |  |  | 43003.0417 | 48 | 48
2017-09-25 01:30 | 33 | 33 |  |  | 43003.0625 | 47 | 47
2017-09-25 02:00 | 34 | 33 |  |  | 43003.0833 | 48 | 48
2017-09-25 02:30 | 36 | 35 |  |  | 43003.1042 | 50 | 50
2017-09-25 03:00 | 38 | 37 |  |  | 43003.125 | 52 | 52
2017-09-25 03:30 | 38 | 37 |  |  | 43003.1458 | 51 | 51
2017-09-25 04:00 | 39 | 38 |  |  | 43003.1667 | 52 | 52
2017-09-25 04:30 | 38 | 37 |  |  | 43003.1875 | 50 | 50
2017-09-25 05:00 | 36 | 36 |  |  | 43003.2083 | 50 | 50
2017-09-25 05:30 | 38 | 38 |  |  | 43003.2292 | 52 | 52
2017-09-25 06:00 | 43 | 43 |  |  | 43003.25 | 59 | 59
2017-09-25 06:30 | 51 | 51 |  |  | 43003.2708 | 70 | 69
2017-09-25 07:00 | 60 | 60 |  |  | 43003.2917 | 85 | 84
2017-09-25 07:30 | 75 | 74 |  |  | 43003.3125 | 109 | 107
2017-09-25 08:00 | 77 | 75 |  |  | 43003.3333 | 111 | 110
2017-09-25 08:30 | 79 | 77 |  |  | 43003.3542 | 114 | 113
2017-09-25 09:00 | 78 | 76 |  |  | 43003.375 | 113 | 113
2017-09-25 09:30 | 79 | 77 |  |  | 43003.3958 | 114 | 113
2017-09-25 10:00 | 80 | 78 |  |  | 43003.4167 | 114 | 114
2017-09-25 10:30 | 78 | 78 |  |  | 43003.4375 | 113 | 113
2017-09-25 11:00 | 76 | 76 |  |  | 43003.4583 | 112 | 112
2017-09-25 11:30 | 77 | 76 |  |  | 43003.4792 | 113 | 113
2017-09-25 12:00 | 77 | 77 |  |  | 43003.5 | 114 | 114
2017-09-25 12:30 | 77 | 77 |  |  | 43003.5208 | 115 | 115
2017-09-25 13:00 | 79 | 79 |  |  | 43003.5417 | 115 | 115
2017-09-25 13:30 | 84 | 84 |  |  | 43003.5625 | 116 | 116
2017-09-25 14:00 | 87 | 86 |  |  | 43003.5833 | 119 | 119
2017-09-25 14:30 | 87 | 87 |  |  | 43003.6042 | 122 | 122
2017-09-25 15:00 | 90 | 90 |  |  | 43003.625 | 124 | 124
2017-09-25 15:30 | 91 | 91 |  |  | 43003.6458 | 125 | 125
2017-09-25 16:00 | 91 | 91 |  |  | 43003.6667 | 126 | 126
2017-09-25 16:30 | 92 | 92 |  |  | 43003.6875 | 128 | 128
2017-09-25 17:00 | 93 | 93 |  |  | 43003.7083 | 131 | 128
2017-09-25 17:30 | 82 | 82 |  |  | 43003.7292 | 123 | 121
2017-09-25 18:00 | 81 | 81 |  |  | 43003.75 | 120 | 118
2017-09-25 18:30 | 80 | 80 |  |  | 43003.7708 | 118 | 116
2017-09-25 19:00 | 80 | 80 |  |  | 43003.7917 | 118 | 116
2017-09-25 19:30 | 78 | 78 |  |  | 43003.8125 | 112 | 112
2017-09-25 20:00 | 76 | 76 |  |  | 43003.8333 | 109 | 109
2017-09-25 20:30 | 80 | 80 |  |  | 43003.8542 | 110 | 110
2017-09-25 21:00 | 77 | 77 |  |  | 43003.875 | 104 | 104
2017-09-25 21:30 | 74 | 74 |  |  | 43003.8958 | 102 | 101
2017-09-25 22:00 | 74 | 73 |  |  | 43003.9167 | 101 | 100
2017-09-25 22:30 | 71 | 70 |  |  | 43003.9375 | 97 | 96
2017-09-25 23:00 | 67 | 67 |  |  | 43003.9583 | 92 | 91
2017-09-25 23:30 | 63 | 63 |  |  | 43003.9792 | 86 | 86
2017-09-26 | 57 | 57 |  |  | 43004 | 79 | 79
2017-09-26 00:30 | 52 | 52 |  |  | 43004.0208 | 72 | 72
2017-09-26 01:00 | 49 | 49 |  |  | 43004.0417 | 68 | 68
2017-09-26 01:30 | 47 | 47 |  |  | 43004.0625 | 65 | 65
2017-09-26 02:00 | 45 | 45 |  |  | 43004.0833 | 63 | 63
2017-09-26 02:30 | 46 | 46 |  |  | 43004.1042 | 64 | 64
2017-09-26 03:00 | 46 | 46 |  |  | 43004.125 | 64 | 64
2017-09-26 03:30 | 45 | 45 |  |  | 43004.1458 | 64 | 63
2017-09-26 04:00 | 45 | 45 |  |  | 43004.1667 | 64 | 63
2017-09-26 04:30 | 46 | 46 |  |  | 43004.1875 | 65 | 65
2017-09-26 05:00 | 49 | 49 |  |  | 43004.2083 | 69 | 69
2017-09-26 05:30 | 53 | 53 |  |  | 43004.2292 | 75 | 74
2017-09-26 06:00 | 56 | 56 |  |  | 43004.25 | 81 | 80
2017-09-26 06:30 | 64 | 64 |  |  | 43004.2708 | 93 | 92
2017-09-26 07:00 | 71 | 71 |  |  | 43004.2917 | 101 | 101
2017-09-26 07:30 | 76 | 76 |  |  | 43004.3125 | 110 | 110
2017-09-26 08:00 | 81 | 81 |  |  | 43004.3333 | 117 | 117
2017-09-26 08:30 | 85 | 85 |  |  | 43004.3542 | 121 | 121
2017-09-26 09:00 | 83 | 83 |  |  | 43004.375 | 120 | 120
2017-09-26 09:30 | 82 | 82 |  |  | 43004.3958 | 117 | 116
2017-09-26 10:00 | 86 | 86 |  |  | 43004.4167 | 120 | 120
2017-09-26 10:30 | 94 | 94 |  |  | 43004.4375 | 130 | 130
2017-09-26 11:00 | 92 | 92 |  |  | 43004.4583 | 130 | 130
2017-09-26 11:30 | 81 | 81 |  |  | 43004.4792 | 119 | 119
2017-09-26 12:00 | 91 | 91 |  |  | 43004.5 | 127 | 127
2017-09-26 12:30 | 80 | 80 |  |  | 43004.5208 | 116 | 116
2017-09-26 13:00 | 79 | 79 |  |  | 43004.5417 | 114 | 114
2017-09-26 13:30 | 81 | 81 |  |  | 43004.5625 | 115 | 115
2017-09-26 14:00 | 81 | 81 |  |  | 43004.5833 | 114 | 114
2017-09-26 14:30 | 82 | 82 |  |  | 43004.6042 | 115 | 115
2017-09-26 15:00 | 83 | 83 |  |  | 43004.625 | 118 | 118
2017-09-26 15:30 | 87 | 87 |  |  | 43004.6458 | 122 | 122
2017-09-26 16:00 | 88 | 88 |  |  | 43004.6667 | 122 | 122
2017-09-26 16:30 | 90 | 89 |  |  | 43004.6875 | 125 | 124
2017-09-26 17:00 | 91 | 91 |  |  | 43004.7083 | 126 | 125
2017-09-26 17:30 | 92 | 92 |  |  | 43004.7292 | 123 | 122
2017-09-26 18:00 | 92 | 92 |  |  | 43004.75 | 123 | 123
2017-09-26 18:30 | 84 | 84 |  |  | 43004.7708 | 118 | 118
2017-09-26 19:00 | 83 | 83 |  |  | 43004.7917 | 118 | 117
2017-09-26 19:30 | 81 | 81 |  |  | 43004.8125 | 113 | 113
2017-09-26 20:00 | 86 | 85 |  |  | 43004.8333 | 113 | 113
2017-09-26 20:30 | 85 | 84 |  |  | 43004.8542 | 111 | 111
2017-09-26 21:00 | 78 | 77 |  |  | 43004.875 | 103 | 103
2017-09-26 21:30 | 75 | 74 |  |  | 43004.8958 | 99 | 99
2017-09-26 22:00 | 74 | 73 |  |  | 43004.9167 | 99 | 99
2017-09-26 22:30 | 71 | 71 |  |  | 43004.9375 | 96 | 96
2017-09-26 23:00 | 69 | 69 |  |  | 43004.9583 | 92 | 92
2017-09-26 23:30 | 67 | 67 |  |  | 43004.9792 | 89 | 89
2017-09-27 | 63 | 63 |  |  | 43005 | 85 | 85
2017-09-27 00:30 | 58 | 58 |  |  | 43005.0208 | 78 | 78
2017-09-27 01:00 | 54 | 53 |  |  | 43005.0417 | 72 | 72
2017-09-27 01:30 | 52 | 51 |  |  | 43005.0625 | 71 | 70
2017-09-27 02:00 | 51 | 50 |  |  | 43005.0833 | 68 | 68
2017-09-27 02:30 | 51 | 50 |  |  | 43005.1042 | 68 | 68
2017-09-27 03:00 | 53 | 52 |  |  | 43005.125 | 68 | 68
2017-09-27 03:30 | 52 | 51 |  |  | 43005.1458 | 68 | 68
2017-09-27 04:00 | 52 | 51 |  |  | 43005.1667 | 68 | 67
2017-09-27 04:30 | 52 | 51 |  |  | 43005.1875 | 68 | 68
2017-09-27 05:00 | 53 | 52 |  |  | 43005.2083 | 70 | 70
2017-09-27 05:30 | 58 | 57 |  |  | 43005.2292 | 77 | 76
2017-09-27 06:00 | 61 | 61 |  |  | 43005.25 | 83 | 83
2017-09-27 06:30 | 67 | 67 |  |  | 43005.2708 | 93 | 93
2017-09-27 07:00 | 75 | 75 |  |  | 43005.2917 | 103 | 103
2017-09-27 07:30 | 78 | 78 |  |  | 43005.3125 | 112 | 112
2017-09-27 08:00 | 79 | 79 |  |  | 43005.3333 | 115 | 115
2017-09-27 08:30 | 84 | 83 |  |  | 43005.3542 | 121 | 119
2017-09-27 09:00 | 86 | 85 |  |  | 43005.375 | 123 | 121
2017-09-27 09:30 | 85 | 84 |  |  | 43005.3958 | 120 | 118
2017-09-27 10:00 | 86 | 86 |  |  | 43005.4167 | 121 | 119
2017-09-27 10:30 | 82 | 82 |  |  | 43005.4375 | 117 | 116
2017-09-27 11:00 | 85 | 84 |  |  | 43005.4583 | 121 | 120
2017-09-27 11:30 | 87 | 86 |  |  | 43005.4792 | 121 | 120
2017-09-27 12:00 | 88 | 88 |  |  | 43005.5 | 125 | 123
2017-09-27 12:30 | 87 | 86 |  |  | 43005.5208 | 126 | 123
2017-09-27 13:00 | 88 | 87 |  |  | 43005.5417 | 127 | 124
2017-09-27 13:30 | 89 | 88 |  |  | 43005.5625 | 126 | 123
2017-09-27 14:00 | 90 | 89 |  |  | 43005.5833 | 127 | 124
2017-09-27 14:30 | 94 | 93 |  |  | 43005.6042 | 128 | 126
2017-09-27 15:00 | 95 | 95 |  |  | 43005.625 | 129 | 127
2017-09-27 15:30 | 93 | 92 |  |  | 43005.6458 | 128 | 126
2017-09-27 16:00 | 93 | 92 |  |  | 43005.6667 | 128 | 126
2017-09-27 16:30 | 92 | 90 |  |  | 43005.6875 | 128 | 125
2017-09-27 17:00 | 92 | 90 |  |  | 43005.7083 | 127 | 124
2017-09-27 17:30 | 92 | 90 |  |  | 43005.7292 | 127 | 123
2017-09-27 18:00 | 91 | 89 |  |  | 43005.75 | 125 | 121
2017-09-27 18:30 | 91 | 87 |  |  | 43005.7708 | 125 | 117
2017-09-27 19:00 | 92 | 88 |  |  | 43005.7917 | 126 | 118
2017-09-27 19:30 | 89 | 86 |  |  | 43005.8125 | 121 | 114
2017-09-27 20:00 | 88 | 85 |  |  | 43005.8333 | 120 | 113
2017-09-27 20:30 | 86 | 83 |  |  | 43005.8542 | 118 | 111
2017-09-27 21:00 | 82 | 80 |  |  | 43005.875 | 112 | 106
2017-09-27 21:30 | 78 | 75 |  |  | 43005.8958 | 108 | 101
2017-09-27 22:00 | 75 | 72 |  |  | 43005.9167 | 107 | 100
2017-09-27 22:30 | 74 | 71 |  |  | 43005.9375 | 104 | 97
2017-09-27 23:00 | 70 | 67 |  |  | 43005.9583 | 99 | 93
2017-09-27 23:30 | 63 | 63 |  |  | 43005.9792 | 87 | 87
2017-09-28 | 57 | 57 |  |  | 43006 | 80 | 79
2017-09-28 00:30 | 53 | 53 |  |  | 43006.0208 | 74 | 74
2017-09-28 01:00 | 49 | 49 |  |  | 43006.0417 | 69 | 69
2017-09-28 01:30 | 46 | 46 |  |  | 43006.0625 | 66 | 66
2017-09-28 02:00 | 45 | 45 |  |  | 43006.0833 | 65 | 65
2017-09-28 02:30 | 47 | 47 |  |  | 43006.1042 | 66 | 66
2017-09-28 03:00 | 47 | 47 |  |  | 43006.125 | 65 | 65
2017-09-28 03:30 | 48 | 47 |  |  | 43006.1458 | 65 | 65
2017-09-28 04:00 | 48 | 47 |  |  | 43006.1667 | 65 | 65
2017-09-28 04:30 | 48 | 47 |  |  | 43006.1875 | 66 | 66
2017-09-28 05:00 | 50 | 50 |  |  | 43006.2083 | 68 | 68
2017-09-28 05:30 | 53 | 53 |  |  | 43006.2292 | 72 | 72
2017-09-28 06:00 | 58 | 58 |  |  | 43006.25 | 79 | 79
2017-09-28 06:30 | 65 | 65 |  |  | 43006.2708 | 90 | 90
2017-09-28 07:00 | 68 | 68 |  |  | 43006.2917 | 96 | 96
2017-09-28 07:30 | 73 | 73 |  |  | 43006.3125 | 105 | 105
2017-09-28 08:00 | 75 | 75 |  |  | 43006.3333 | 109 | 109
2017-09-28 08:30 | 77 | 77 |  |  | 43006.3542 | 111 | 111
2017-09-28 09:00 | 76 | 76 |  |  | 43006.375 | 112 | 112
2017-09-28 09:30 | 75 | 75 |  |  | 43006.3958 | 110 | 110
2017-09-28 10:00 | 75 | 75 |  |  | 43006.4167 | 111 | 111
2017-09-28 10:30 | 76 | 76 |  |  | 43006.4375 | 111 | 111
2017-09-28 11:00 | 77 | 76 |  |  | 43006.4583 | 113 | 113
2017-09-28 11:30 | 78 | 78 |  |  | 43006.4792 | 115 | 115
2017-09-28 12:00 | 80 | 79 |  |  | 43006.5 | 117 | 117
2017-09-28 12:30 | 82 | 82 |  |  | 43006.5208 | 120 | 120
2017-09-28 13:00 | 85 | 85 |  |  | 43006.5417 | 122 | 122
2017-09-28 13:30 | 88 | 87 |  |  | 43006.5625 | 125 | 123
2017-09-28 14:00 | 91 | 91 |  |  | 43006.5833 | 126 | 124
2017-09-28 14:30 | 94 | 94 |  |  | 43006.6042 | 129 | 127
2017-09-28 15:00 | 92 | 92 |  |  | 43006.625 | 131 | 129
2017-09-28 15:30 | 90 | 89 |  |  | 43006.6458 | 134 | 129
2017-09-28 16:00 | 93 | 92 |  |  | 43006.6667 | 137 | 132
2017-09-28 16:30 | 100 | 99 |  |  | 43006.6875 | 137 | 131
2017-09-28 17:00 | 109 | 109 |  |  | 43006.7083 | 136 | 129
2017-09-28 17:30 | 97 | 97 |  |  | 43006.7292 | 130 | 126
2017-09-28 18:00 | 88 | 88 |  |  | 43006.75 | 126 | 124
2017-09-28 18:30 | 88 | 87 |  |  | 43006.7708 | 126 | 121
2017-09-28 19:00 | 86 | 85 |  |  | 43006.7917 | 123 | 122
2017-09-28 19:30 | 79 | 79 |  |  | 43006.8125 | 113 | 113
2017-09-28 20:00 | 79 | 79 |  |  | 43006.8333 | 112 | 111
2017-09-28 20:30 | 77 | 77 |  |  | 43006.8542 | 110 | 110
2017-09-28 21:00 | 72 | 72 |  |  | 43006.875 | 104 | 104
2017-09-28 21:30 | 70 | 70 |  |  | 43006.8958 | 101 | 101
2017-09-28 22:00 | 72 | 71 |  |  | 43006.9167 | 102 | 101
2017-09-28 22:30 | 78 | 78 |  |  | 43006.9375 | 102 | 102
2017-09-28 23:00 | 75 | 75 |  |  | 43006.9583 | 97 | 97
2017-09-28 23:30 | 67 | 67 |  |  | 43006.9792 | 91 | 91
2017-09-29 | 61 | 60 |  |  | 43007 | 83 | 83
2017-09-29 00:30 | 54 | 54 |  |  | 43007.0208 | 76 | 76
2017-09-29 01:00 | 52 | 52 |  |  | 43007.0417 | 72 | 72
2017-09-29 01:30 | 49 | 48 |  |  | 43007.0625 | 69 | 69
2017-09-29 02:00 | 48 | 47 |  |  | 43007.0833 | 67 | 67
2017-09-29 02:30 | 48 | 48 |  |  | 43007.1042 | 67 | 67
2017-09-29 03:00 | 47 | 47 |  |  | 43007.125 | 66 | 66
2017-09-29 03:30 | 48 | 47 |  |  | 43007.1458 | 66 | 66
2017-09-29 04:00 | 46 | 45 |  |  | 43007.1667 | 66 | 66
2017-09-29 04:30 | 46 | 46 |  |  | 43007.1875 | 66 | 66
2017-09-29 05:00 | 47 | 47 |  |  | 43007.2083 | 68 | 68
2017-09-29 05:30 | 51 | 51 |  |  | 43007.2292 | 72 | 72
2017-09-29 06:00 | 55 | 55 |  |  | 43007.25 | 79 | 78
2017-09-29 06:30 | 61 | 61 |  |  | 43007.2708 | 90 | 90
2017-09-29 07:00 | 68 | 68 |  |  | 43007.2917 | 100 | 99
2017-09-29 07:30 | 76 | 76 |  |  | 43007.3125 | 110 | 110
2017-09-29 08:00 | 79 | 79 |  |  | 43007.3333 | 115 | 115
2017-09-29 08:30 | 80 | 80 |  |  | 43007.3542 | 118 | 118
2017-09-29 09:00 | 79 | 79 |  |  | 43007.375 | 117 | 117
2017-09-29 09:30 | 79 | 79 |  |  | 43007.3958 | 117 | 117
2017-09-29 10:00 | 78 | 77 |  |  | 43007.4167 | 116 | 116
2017-09-29 10:30 | 79 | 79 |  |  | 43007.4375 | 117 | 117
2017-09-29 11:00 | 81 | 81 |  |  | 43007.4583 | 119 | 119
2017-09-29 11:30 | 82 | 82 |  |  | 43007.4792 | 122 | 120
2017-09-29 12:00 | 85 | 84 |  |  | 43007.5 | 125 | 123
2017-09-29 12:30 | 86 | 86 |  |  | 43007.5208 | 126 | 124
2017-09-29 13:00 | 90 | 89 |  |  | 43007.5417 | 132 | 128
2017-09-29 13:30 | 96 | 94 |  |  | 43007.5625 | 136 | 132
2017-09-29 14:00 | 92 | 92 |  |  | 43007.5833 | 137 | 133
2017-09-29 14:30 | 92 | 91 |  |  | 43007.6042 | 138 | 133
2017-09-29 15:00 | 82 | 81 |  |  | 43007.625 | 117 | 112
2017-09-29 15:30 | 79 | 78 |  |  | 43007.6458 | 113 | 108
2017-09-29 16:00 | 79 | 78 |  |  | 43007.6667 | 112 | 106
2017-09-29 16:30 | 78 | 77 |  |  | 43007.6875 | 112 | 105
2017-09-29 17:00 | 77 | 76 |  |  | 43007.7083 | 106 | 101
2017-09-29 17:30 | 73 | 73 |  |  | 43007.7292 | 98 | 97
2017-09-29 18:00 | 68 | 68 |  |  | 43007.75 | 94 | 93
2017-09-29 18:30 | 67 | 67 |  |  | 43007.7708 | 91 | 91
2017-09-29 19:00 | 67 | 67 |  |  | 43007.7917 | 92 | 92
2017-09-29 19:30 | 66 | 66 |  |  | 43007.8125 | 90 | 90
2017-09-29 20:00 | 64 | 64 |  |  | 43007.8333 | 86 | 86
2017-09-29 20:30 | 62 | 62 |  |  | 43007.8542 | 84 | 84
2017-09-29 21:00 | 59 | 59 |  |  | 43007.875 | 81 | 81
2017-09-29 21:30 | 56 | 56 |  |  | 43007.8958 | 78 | 78
2017-09-29 22:00 | 54 | 54 |  |  | 43007.9167 | 76 | 76
2017-09-29 22:30 | 52 | 52 |  |  | 43007.9375 | 74 | 74
2017-09-29 23:00 | 50 | 50 |  |  | 43007.9583 | 71 | 71
2017-09-29 23:30 | 47 | 47 |  |  | 43007.9792 | 68 | 68
2017-09-30 | 43 | 43 |  |  | 43008 | 63 | 62
2017-09-30 00:30 | 37 | 37 |  |  | 43008.0208 | 56 | 55
2017-09-30 01:00 | 35 | 35 |  |  | 43008.0417 | 51 | 50
2017-09-30 01:30 | 33 | 33 |  |  | 43008.0625 | 49 | 49
2017-09-30 02:00 | 33 | 33 |  |  | 43008.0833 | 49 | 48
2017-09-30 02:30 | 34 | 34 |  |  | 43008.1042 | 50 | 50
2017-09-30 03:00 | 35 | 35 |  |  | 43008.125 | 52 | 52
2017-09-30 03:30 | 35 | 35 |  |  | 43008.1458 | 52 | 52
2017-09-30 04:00 | 35 | 35 |  |  | 43008.1667 | 51 | 51
2017-09-30 04:30 | 34 | 34 |  |  | 43008.1875 | 51 | 50
2017-09-30 05:00 | 36 | 35 |  |  | 43008.2083 | 51 | 51
2017-09-30 05:30 | 37 | 37 |  |  | 43008.2292 | 52 | 52
2017-09-30 06:00 | 38 | 38 |  |  | 43008.25 | 54 | 54
2017-09-30 06:30 | 39 | 39 |  |  | 43008.2708 | 56 | 55
2017-09-30 07:00 | 39 | 39 |  |  | 43008.2917 | 56 | 55
2017-09-30 07:30 | 38 | 38 |  |  | 43008.3125 | 56 | 55
2017-09-30 08:00 | 37 | 37 |  |  | 43008.3333 | 57 | 56
2017-09-30 08:30 | 39 | 39 |  |  | 43008.3542 | 60 | 59
2017-09-30 09:00 | 41 | 41 |  |  | 43008.375 | 59 | 59
2017-09-30 09:30 | 44 | 44 |  |  | 43008.3958 | 61 | 60
2017-09-30 10:00 | 43 | 43 |  |  | 43008.4167 | 61 | 60
2017-09-30 10:30 | 44 | 43 |  |  | 43008.4375 | 62 | 61
2017-09-30 11:00 | 47 | 47 |  |  | 43008.4583 | 64 | 63
2017-09-30 11:30 | 48 | 47 |  |  | 43008.4792 | 67 | 66
2017-09-30 12:00 | 47 | 46 |  |  | 43008.5 | 66 | 65
2017-09-30 12:30 | 49 | 49 |  |  | 43008.5208 | 66 | 66
2017-09-30 13:00 | 52 | 51 |  |  | 43008.5417 | 70 | 70
2017-09-30 13:30 | 54 | 53 |  |  | 43008.5625 | 71 | 71
2017-09-30 14:00 | 59 | 58 |  |  | 43008.5833 | 75 | 75
2017-09-30 14:30 | 61 | 60 |  |  | 43008.6042 | 76 | 76
2017-09-30 15:00 | 62 | 62 |  |  | 43008.625 | 78 | 78
2017-09-30 15:30 | 66 | 64 |  |  | 43008.6458 | 82 | 81
2017-09-30 16:00 | 68 | 66 |  |  | 43008.6667 | 83 | 82
2017-09-30 16:30 | 68 | 65 |  |  | 43008.6875 | 83 | 81
2017-09-30 17:00 | 65 | 61 |  |  | 43008.7083 | 82 | 81
2017-09-30 17:30 | 64 | 60 |  |  | 43008.7292 | 80 | 78
2017-09-30 18:00 | 62 | 58 |  |  | 43008.75 | 79 | 78
2017-09-30 18:30 | 63 | 59 |  |  | 43008.7708 | 80 | 78
2017-09-30 19:00 | 64 | 60 |  |  | 43008.7917 | 82 | 80
2017-09-30 19:30 | 62 | 59 |  |  | 43008.8125 | 78 | 77
2017-09-30 20:00 | 60 | 57 |  |  | 43008.8333 | 78 | 77
2017-09-30 20:30 | 60 | 57 |  |  | 43008.8542 | 78 | 77
2017-09-30 21:00 | 57 | 55 |  |  | 43008.875 | 73 | 73
2017-09-30 21:30 | 54 | 52 |  |  | 43008.8958 | 70 | 69
2017-09-30 22:00 | 53 | 50 |  |  | 43008.9167 | 69 | 69
2017-09-30 22:30 | 54 | 51 |  |  | 43008.9375 | 70 | 69
2017-09-30 23:00 | 56 | 52 |  |  | 43008.9583 | 69 | 68
2017-09-30 23:30 | 52 | 48 |  |  | 43008.9792 | 65 | 64
2017-10-01 | 48 | 44 |  |  | 43009 | 59 | 58
2017-10-01 00:30 | 44 | 38 |  |  | 43009.0208 | 53 | 52
2017-10-01 01:00 | 42 | 33 |  |  | 43009.0417 | 49 | 47
2017-10-01 01:30 | 40 | 31 |  |  | 43009.0625 | 47 | 44
2017-10-01 02:00 | 40 | 31 |  |  | 43009.0833 | 47 | 45
2017-10-01 02:30 | 40 | 31 |  |  | 43009.1042 | 48 | 46
2017-10-01 03:00 | 41 | 32 |  |  | 43009.125 | 47 | 45
2017-10-01 03:30 | 42 | 33 |  |  | 43009.1458 | 48 | 45
2017-10-01 04:00 | 41 | 32 |  |  | 43009.1667 | 47 | 45
2017-10-01 04:30 | 40 | 31 |  |  | 43009.1875 | 46 | 44
2017-10-01 05:00 | 40 | 31 |  |  | 43009.2083 | 46 | 44
2017-10-01 05:30 | 41 | 32 |  |  | 43009.2292 | 48 | 46
2017-10-01 06:00 | 41 | 32 |  |  | 43009.25 | 48 | 46
2017-10-01 06:30 | 40 | 31 |  |  | 43009.2708 | 47 | 45
2017-10-01 07:00 | 41 | 32 |  |  | 43009.2917 | 49 | 47
2017-10-01 07:30 | 41 | 33 |  |  | 43009.3125 | 50 | 48
2017-10-01 08:00 | 38 | 31 |  |  | 43009.3333 | 45 | 44
2017-10-01 08:30 | 44 | 39 |  |  | 43009.3542 | 53 | 52
2017-10-01 09:00 | 45 | 39 |  |  | 43009.375 | 54 | 53
2017-10-01 09:30 | 46 | 41 |  |  | 43009.3958 | 58 | 58
2017-10-01 10:00 | 45 | 40 |  |  | 43009.4167 | 56 | 56
2017-10-01 10:30 | 46 | 42 |  |  | 43009.4375 | 57 | 57
2017-10-01 11:00 | 47 | 43 |  |  | 43009.4583 | 57 | 57
2017-10-01 11:30 | 47 | 43 |  |  | 43009.4792 | 59 | 58
2017-10-01 12:00 | 46 | 42 |  |  | 43009.5 | 52 | 51
2017-10-01 12:30 | 46 | 42 |  |  | 43009.5208 | 52 | 52
2017-10-01 13:00 | 46 | 42 |  |  | 43009.5417 | 53 | 53
2017-10-01 13:30 | 46 | 42 |  |  | 43009.5625 | 56 | 56
2017-10-01 14:00 | 47 | 43 |  |  | 43009.5833 | 56 | 56
2017-10-01 14:30 | 46 | 42 |  |  | 43009.6042 | 56 | 56
2017-10-01 15:00 | 47 | 43 |  |  | 43009.625 | 56 | 56
2017-10-01 15:30 | 50 | 46 |  |  | 43009.6458 | 60 | 59
2017-10-01 16:00 | 54 | 50 |  |  | 43009.6667 | 68 | 67
2017-10-01 16:30 | 53 | 49 |  |  | 43009.6875 | 67 | 67
2017-10-01 17:00 | 56 | 51 |  |  | 43009.7083 | 70 | 69
2017-10-01 17:30 | 57 | 52 |  |  | 43009.7292 | 71 | 70
2017-10-01 18:00 | 58 | 54 |  |  | 43009.75 | 71 | 71
2017-10-01 18:30 | 58 | 54 |  |  | 43009.7708 | 72 | 71
2017-10-01 19:00 | 56 | 52 |  |  | 43009.7917 | 71 | 71
2017-10-01 19:30 | 55 | 51 |  |  | 43009.8125 | 69 | 69
2017-10-01 20:00 | 55 | 51 |  |  | 43009.8333 | 69 | 68
2017-10-01 20:30 | 56 | 52 |  |  | 43009.8542 | 69 | 69
2017-10-01 21:00 | 53 | 49 |  |  | 43009.875 | 66 | 66
2017-10-01 21:30 | 51 | 46 |  |  | 43009.8958 | 64 | 63
2017-10-01 22:00 | 50 | 45 |  |  | 43009.9167 | 63 | 62
2017-10-01 22:30 | 52 | 47 |  |  | 43009.9375 | 65 | 65
2017-10-01 23:00 | 55 | 49 |  |  | 43009.9583 | 65 | 64
2017-10-01 23:30 | 52 | 46 |  |  | 43009.9792 | 63 | 62
2017-10-02 | 50 | 42 |  |  | 43010 | 58 | 57
2017-10-02 00:30 | 46 | 39 |  |  | 43010.0208 | 52 | 51
2017-10-02 01:00 | 42 | 35 |  |  | 43010.0417 | 47 | 46
2017-10-02 01:30 | 39 | 31 |  |  | 43010.0625 | 45 | 44
2017-10-02 02:00 | 39 | 32 |  |  | 43010.0833 | 45 | 44
2017-10-02 02:30 | 40 | 32 |  |  | 43010.1042 | 45 | 44
2017-10-02 03:00 | 50 | 32 |  |  | 43010.125 | 47 | 43
2017-10-02 03:30 | 51 | 31 |  |  | 43010.1458 | 46 | 42
2017-10-02 04:00 | 51 | 32 |  |  | 43010.1667 | 46 | 42
2017-10-02 04:30 | 50 | 30 |  |  | 43010.1875 | 45 | 40
2017-10-02 05:00 | 49 | 29 |  |  | 43010.2083 | 45 | 40
2017-10-02 05:30 | 49 | 29 |  |  | 43010.2292 | 46 | 42
2017-10-02 06:00 | 50 | 30 |  |  | 43010.25 | 46 | 42
2017-10-02 06:30 | 50 | 32 |  |  | 43010.2708 | 50 | 47
2017-10-02 07:00 | 50 | 32 |  |  | 43010.2917 | 51 | 48
2017-10-02 07:30 | 50 | 34 |  |  | 43010.3125 | 54 | 53
2017-10-02 08:00 | 52 | 38 |  |  | 43010.3333 | 58 | 57
2017-10-02 08:30 | 56 | 44 |  |  | 43010.3542 | 66 | 65
2017-10-02 09:00 | 60 | 49 |  |  | 43010.375 | 72 | 70
2017-10-02 09:30 | 63 | 50 |  |  | 43010.3958 | 73 | 70
2017-10-02 10:00 | 65 | 53 |  |  | 43010.4167 | 74 | 71
2017-10-02 10:30 | 65 | 53 |  |  | 43010.4375 | 73 | 71
2017-10-02 11:00 | 62 | 51 |  |  | 43010.4583 | 72 | 71
2017-10-02 11:30 | 61 | 51 |  |  | 43010.4792 | 70 | 69
2017-10-02 12:00 | 63 | 51 |  |  | 43010.5 | 72 | 69
2017-10-02 12:30 | 63 | 50 |  |  | 43010.5208 | 71 | 67
2017-10-02 13:00 | 62 | 48 |  |  | 43010.5417 | 69 | 66
2017-10-02 13:30 | 61 | 48 |  |  | 43010.5625 | 70 | 66
2017-10-02 14:00 | 62 | 49 |  |  | 43010.5833 | 70 | 66
2017-10-02 14:30 | 62 | 49 |  |  | 43010.6042 | 67 | 63
2017-10-02 15:00 | 60 | 49 |  |  | 43010.625 | 67 | 65
2017-10-02 15:30 | 61 | 50 |  |  | 43010.6458 | 70 | 68
2017-10-02 16:00 | 63 | 53 |  |  | 43010.6667 | 73 | 71
2017-10-02 16:30 | 66 | 55 |  |  | 43010.6875 | 75 | 72
2017-10-02 17:00 | 70 | 59 |  |  | 43010.7083 | 80 | 77
2017-10-02 17:30 | 73 | 61 |  |  | 43010.7292 | 82 | 79
2017-10-02 18:00 | 74 | 63 |  |  | 43010.75 | 84 | 80
2017-10-02 18:30 | 78 | 65 |  |  | 43010.7708 | 87 | 81
2017-10-02 19:00 | 78 | 66 |  |  | 43010.7917 | 87 | 83
2017-10-02 19:30 | 76 | 63 |  |  | 43010.8125 | 85 | 80
2017-10-02 20:00 | 73 | 61 |  |  | 43010.8333 | 80 | 76
2017-10-02 20:30 | 71 | 59 |  |  | 43010.8542 | 77 | 74
2017-10-02 21:00 | 68 | 55 |  |  | 43010.875 | 74 | 70
2017-10-02 21:30 | 66 | 53 |  |  | 43010.8958 | 70 | 67
2017-10-02 22:00 | 63 | 50 |  |  | 43010.9167 | 69 | 66
2017-10-02 22:30 | 63 | 49 |  |  | 43010.9375 | 69 | 65
2017-10-02 23:00 | 62 | 47 |  |  | 43010.9583 | 65 | 61
2017-10-02 23:30 | 58 | 43 |  |  | 43010.9792 | 62 | 58
2017-10-03 | 56 | 40 |  |  | 43011 | 58 | 54
2017-10-03 00:30 | 55 | 39 |  |  | 43011.0208 | 56 | 52
2017-10-03 01:00 | 52 | 34 |  |  | 43011.0417 | 52 | 48
2017-10-03 01:30 | 48 | 30 |  |  | 43011.0625 | 45 | 42
2017-10-03 02:00 | 49 | 29 |  |  | 43011.0833 | 44 | 40
2017-10-03 02:30 | 48 | 29 |  |  | 43011.1042 | 43 | 40
2017-10-03 03:00 | 49 | 28 |  |  | 43011.125 | 43 | 40
2017-10-03 03:30 | 49 | 28 |  |  | 43011.1458 | 43 | 40
2017-10-03 04:00 | 48 | 27 |  |  | 43011.1667 | 42 | 38
2017-10-03 04:30 | 47 | 28 |  |  | 43011.1875 | 42 | 39
2017-10-03 05:00 | 48 | 29 |  |  | 43011.2083 | 44 | 41
2017-10-03 05:30 | 48 | 34 |  |  | 43011.2292 | 49 | 47
2017-10-03 06:00 | 53 | 41 |  |  | 43011.25 | 57 | 55
2017-10-03 06:30 | 60 | 52 |  |  | 43011.2708 | 70 | 69
2017-10-03 07:00 | 70 | 61 |  |  | 43011.2917 | 83 | 81
2017-10-03 07:30 | 76 | 66 |  |  | 43011.3125 | 93 | 90
2017-10-03 08:00 | 79 | 67 |  |  | 43011.3333 | 95 | 91
2017-10-03 08:30 | 79 | 68 |  |  | 43011.3542 | 96 | 92
2017-10-03 09:00 | 80 | 68 |  |  | 43011.375 | 96 | 92
2017-10-03 09:30 | 78 | 67 |  |  | 43011.3958 | 93 | 88
2017-10-03 10:00 | 79 | 68 |  |  | 43011.4167 | 92 | 87
2017-10-03 10:30 | 76 | 64 |  |  | 43011.4375 | 88 | 83
2017-10-03 11:00 | 74 | 63 |  |  | 43011.4583 | 86 | 82
2017-10-03 11:30 | 75 | 64 |  |  | 43011.4792 | 87 | 83
2017-10-03 12:00 | 77 | 66 |  |  | 43011.5 | 91 | 87
2017-10-03 12:30 | 76 | 66 |  |  | 43011.5208 | 94 | 90
2017-10-03 13:00 | 74 | 61 |  |  | 43011.5417 | 88 | 83
2017-10-03 13:30 | 75 | 62 |  |  | 43011.5625 | 91 | 86
2017-10-03 14:00 | 77 | 65 |  |  | 43011.5833 | 93 | 88
2017-10-03 14:30 | 79 | 69 |  |  | 43011.6042 | 97 | 92
2017-10-03 15:00 | 81 | 71 |  |  | 43011.625 | 99 | 94
2017-10-03 15:30 | 83 | 72 |  |  | 43011.6458 | 99 | 92
2017-10-03 16:00 | 84 | 72 |  |  | 43011.6667 | 100 | 93
2017-10-03 16:30 | 85 | 73 |  |  | 43011.6875 | 102 | 94
2017-10-03 17:00 | 87 | 75 |  |  | 43011.7083 | 103 | 94
2017-10-03 17:30 | 88 | 75 |  |  | 43011.7292 | 103 | 93
2017-10-03 18:00 | 97 | 77 |  |  | 43011.75 | 114 | 95
2017-10-03 18:30 | 98 | 78 |  |  | 43011.7708 | 115 | 93
2017-10-03 19:00 | 100 | 80 |  |  | 43011.7917 | 116 | 95
2017-10-03 19:30 | 95 | 78 |  |  | 43011.8125 | 108 | 92
2017-10-03 20:00 | 88 | 77 |  |  | 43011.8333 | 98 | 91
2017-10-03 20:30 | 83 | 77 |  |  | 43011.8542 | 91 | 89
2017-10-03 21:00 | 79 | 72 |  |  | 43011.875 | 86 | 84
2017-10-03 21:30 | 75 | 66 |  |  | 43011.8958 | 82 | 79
2017-10-03 22:00 | 72 | 62 |  |  | 43011.9167 | 80 | 77
2017-10-03 22:30 | 68 | 60 |  |  | 43011.9375 | 75 | 73
2017-10-03 23:00 | 66 | 58 |  |  | 43011.9583 | 71 | 70
2017-10-03 23:30 | 60 | 51 |  |  | 43011.9792 | 66 | 65
2017-10-04 | 56 | 47 |  |  | 43012 | 60 | 59
2017-10-04 00:30 | 52 | 42 |  |  | 43012.0208 | 53 | 52
2017-10-04 01:00 | 49 | 38 |  |  | 43012.0417 | 50 | 48
2017-10-04 01:30 | 48 | 36 |  |  | 43012.0625 | 48 | 46
2017-10-04 02:00 | 49 | 36 |  |  | 43012.0833 | 48 | 46
2017-10-04 02:30 | 50 | 37 |  |  | 43012.1042 | 48 | 46
2017-10-04 03:00 | 50 | 37 |  |  | 43012.125 | 48 | 46
2017-10-04 03:30 | 48 | 35 |  |  | 43012.1458 | 46 | 43
2017-10-04 04:00 | 46 | 32 |  |  | 43012.1667 | 43 | 41
2017-10-04 04:30 | 46 | 33 |  |  | 43012.1875 | 45 | 43
2017-10-04 05:00 | 49 | 36 |  |  | 43012.2083 | 48 | 46
2017-10-04 05:30 | 51 | 41 |  |  | 43012.2292 | 53 | 51
2017-10-04 06:00 | 56 | 47 |  |  | 43012.25 | 61 | 60
2017-10-04 06:30 | 62 | 56 |  |  | 43012.2708 | 72 | 71
2017-10-04 07:00 | 66 | 62 |  |  | 43012.2917 | 81 | 81
2017-10-04 07:30 | 70 | 66 |  |  | 43012.3125 | 88 | 88
2017-10-04 08:00 | 70 | 66 |  |  | 43012.3333 | 91 | 91
2017-10-04 08:30 | 70 | 65 |  |  | 43012.3542 | 92 | 91
2017-10-04 09:00 | 68 | 64 |  |  | 43012.375 | 88 | 88
2017-10-04 09:30 | 69 | 63 |  |  | 43012.3958 | 88 | 87
2017-10-04 10:00 | 71 | 65 |  |  | 43012.4167 | 90 | 88
2017-10-04 10:30 | 76 | 69 |  |  | 43012.4375 | 95 | 91
2017-10-04 11:00 | 80 | 73 |  |  | 43012.4583 | 99 | 95
2017-10-04 11:30 | 80 | 72 |  |  | 43012.4792 | 96 | 92
2017-10-04 12:00 | 78 | 70 |  |  | 43012.5 | 94 | 90
2017-10-04 12:30 | 77 | 68 |  |  | 43012.5208 | 96 | 92
2017-10-04 13:00 | 78 | 69 |  |  | 43012.5417 | 99 | 95
2017-10-04 13:30 | 81 | 73 |  |  | 43012.5625 | 103 | 98
2017-10-04 14:00 | 84 | 76 |  |  | 43012.5833 | 102 | 98
2017-10-04 14:30 | 85 | 77 |  |  | 43012.6042 | 101 | 97
2017-10-04 15:00 | 82 | 73 |  |  | 43012.625 | 101 | 97
2017-10-04 15:30 | 80 | 72 |  |  | 43012.6458 | 99 | 94
2017-10-04 16:00 | 82 | 73 |  |  | 43012.6667 | 101 | 96
2017-10-04 16:30 | 84 | 75 |  |  | 43012.6875 | 102 | 97
2017-10-04 17:00 | 86 | 76 |  |  | 43012.7083 | 103 | 97
2017-10-04 17:30 | 84 | 74 |  |  | 43012.7292 | 100 | 94
2017-10-04 18:00 | 82 | 73 |  |  | 43012.75 | 96 | 91
2017-10-04 18:30 | 83 | 75 |  |  | 43012.7708 | 97 | 92
2017-10-04 19:00 | 87 | 79 |  |  | 43012.7917 | 100 | 95
2017-10-04 19:30 | 85 | 77 |  |  | 43012.8125 | 97 | 91
2017-10-04 20:00 | 83 | 74 |  |  | 43012.8333 | 94 | 89
2017-10-04 20:30 | 77 | 70 |  |  | 43012.8542 | 89 | 85
2017-10-04 21:00 | 72 | 66 |  |  | 43012.875 | 83 | 80
2017-10-04 21:30 | 69 | 63 |  |  | 43012.8958 | 78 | 76
2017-10-04 22:00 | 68 | 61 |  |  | 43012.9167 | 77 | 75
2017-10-04 22:30 | 66 | 59 |  |  | 43012.9375 | 74 | 72
2017-10-04 23:00 | 65 | 57 |  |  | 43012.9583 | 71 | 69
2017-10-04 23:30 | 61 | 51 |  |  | 43012.9792 | 66 | 64
2017-10-05 | 59 | 47 |  |  | 43013 | 61 | 58
2017-10-05 00:30 | 55 | 41 |  |  | 43013.0208 | 54 | 50
2017-10-05 01:00 | 52 | 37 |  |  | 43013.0417 | 49 | 45
2017-10-05 01:30 | 50 | 34 |  |  | 43013.0625 | 47 | 42
2017-10-05 02:00 | 52 | 36 |  |  | 43013.0833 | 48 | 43
2017-10-05 02:30 | 52 | 35 |  |  | 43013.1042 | 48 | 42
2017-10-05 03:00 | 52 | 34 |  |  | 43013.125 | 48 | 43
2017-10-05 03:30 | 50 | 33 |  |  | 43013.1458 | 46 | 40
2017-10-05 04:00 | 49 | 32 |  |  | 43013.1667 | 46 | 40
2017-10-05 04:30 | 50 | 33 |  |  | 43013.1875 | 46 | 41
2017-10-05 05:00 | 51 | 35 |  |  | 43013.2083 | 49 | 43
2017-10-05 05:30 | 46 | 38 |  |  | 43013.2292 | 50 | 48
2017-10-05 06:00 | 47 | 45 |  |  | 43013.25 | 57 | 56
2017-10-05 06:30 | 54 | 54 |  |  | 43013.2708 | 70 | 69
2017-10-05 07:00 | 60 | 60 |  |  | 43013.2917 | 77 | 77
2017-10-05 07:30 | 62 | 62 |  |  | 43013.3125 | 83 | 83
2017-10-05 08:00 | 62 | 62 |  |  | 43013.3333 | 83 | 83
2017-10-05 08:30 | 63 | 63 |  |  | 43013.3542 | 85 | 85
2017-10-05 09:00 | 64 | 64 |  |  | 43013.375 | 87 | 86
2017-10-05 09:30 | 65 | 65 |  |  | 43013.3958 | 87 | 86
2017-10-05 10:00 | 64 | 63 |  |  | 43013.4167 | 87 | 87
2017-10-05 10:30 | 65 | 64 |  |  | 43013.4375 | 87 | 87
2017-10-05 11:00 | 67 | 67 |  |  | 43013.4583 | 88 | 88
2017-10-05 11:30 | 66 | 66 |  |  | 43013.4792 | 88 | 88
2017-10-05 12:00 | 66 | 65 |  |  | 43013.5 | 89 | 89
2017-10-05 12:30 | 65 | 64 |  |  | 43013.5208 | 89 | 89
2017-10-05 13:00 | 65 | 64 |  |  | 43013.5417 | 89 | 89
2017-10-05 13:30 | 67 | 66 |  |  | 43013.5625 | 90 | 90
2017-10-05 14:00 | 70 | 70 |  |  | 43013.5833 | 94 | 94
2017-10-05 14:30 | 72 | 72 |  |  | 43013.6042 | 96 | 96
2017-10-05 15:00 | 76 | 76 |  |  | 43013.625 | 99 | 99
2017-10-05 15:30 | 78 | 78 |  |  | 43013.6458 | 101 | 101
2017-10-05 16:00 | 79 | 79 |  |  | 43013.6667 | 101 | 101
2017-10-05 16:30 | 78 | 78 |  |  | 43013.6875 | 100 | 100
2017-10-05 17:00 | 78 | 78 |  |  | 43013.7083 | 101 | 101
2017-10-05 17:30 | 79 | 79 |  |  | 43013.7292 | 99 | 99
2017-10-05 18:00 | 81 | 81 |  |  | 43013.75 | 99 | 99
2017-10-05 18:30 | 81 | 81 |  |  | 43013.7708 | 98 | 98
2017-10-05 19:00 | 82 | 82 |  |  | 43013.7917 | 100 | 100
2017-10-05 19:30 | 81 | 81 |  |  | 43013.8125 | 98 | 98
2017-10-05 20:00 | 81 | 81 |  |  | 43013.8333 | 97 | 97
2017-10-05 20:30 | 76 | 76 |  |  | 43013.8542 | 93 | 92
2017-10-05 21:00 | 72 | 71 |  |  | 43013.875 | 86 | 85
2017-10-05 21:30 | 66 | 66 |  |  | 43013.8958 | 79 | 79
2017-10-05 22:00 | 62 | 62 |  |  | 43013.9167 | 77 | 77
2017-10-05 22:30 | 60 | 60 |  |  | 43013.9375 | 75 | 75
2017-10-05 23:00 | 59 | 59 |  |  | 43013.9583 | 72 | 72
2017-10-05 23:30 | 54 | 54 |  |  | 43013.9792 | 67 | 67
2017-10-06 | 49 | 49 |  |  | 43014 | 62 | 62
2017-10-06 00:30 | 45 | 45 |  |  | 43014.0208 | 56 | 56
2017-10-06 01:00 | 42 | 41 |  |  | 43014.0417 | 51 | 51
2017-10-06 01:30 | 38 | 38 |  |  | 43014.0625 | 48 | 47
2017-10-06 02:00 | 37 | 37 |  |  | 43014.0833 | 46 | 46
2017-10-06 02:30 | 40 | 38 |  |  | 43014.1042 | 47 | 46
2017-10-06 03:00 | 39 | 37 |  |  | 43014.125 | 47 | 46
2017-10-06 03:30 | 40 | 38 |  |  | 43014.1458 | 47 | 46
2017-10-06 04:00 | 39 | 37 |  |  | 43014.1667 | 46 | 45
2017-10-06 04:30 | 40 | 38 |  |  | 43014.1875 | 47 | 46
2017-10-06 05:00 | 41 | 39 |  |  | 43014.2083 | 48 | 47
2017-10-06 05:30 | 45 | 42 |  |  | 43014.2292 | 53 | 53
2017-10-06 06:00 | 49 | 47 |  |  | 43014.25 | 58 | 58
2017-10-06 06:30 | 58 | 54 |  |  | 43014.2708 | 69 | 69
2017-10-06 07:00 | 61 | 56 |  |  | 43014.2917 | 75 | 75
2017-10-06 07:30 | 65 | 61 |  |  | 43014.3125 | 82 | 82
2017-10-06 08:00 | 65 | 62 |  |  | 43014.3333 | 85 | 85
2017-10-06 08:30 | 66 | 62 |  |  | 43014.3542 | 87 | 87
2017-10-06 09:00 | 66 | 63 |  |  | 43014.375 | 89 | 89
2017-10-06 09:30 | 68 | 65 |  |  | 43014.3958 | 91 | 91
2017-10-06 10:00 | 69 | 66 |  |  | 43014.4167 | 91 | 91
2017-10-06 10:30 | 72 | 68 |  |  | 43014.4375 | 94 | 94
2017-10-06 11:00 | 73 | 70 |  |  | 43014.4583 | 96 | 96
2017-10-06 11:30 | 72 | 70 |  |  | 43014.4792 | 95 | 95
2017-10-06 12:00 | 73 | 69 |  |  | 43014.5 | 95 | 95
2017-10-06 12:30 | 75 | 71 |  |  | 43014.5208 | 97 | 97
2017-10-06 13:00 | 76 | 72 |  |  | 43014.5417 | 99 | 99
2017-10-06 13:30 | 77 | 73 |  |  | 43014.5625 | 100 | 99
2017-10-06 14:00 | 78 | 76 |  |  | 43014.5833 | 100 | 100
2017-10-06 14:30 | 83 | 81 |  |  | 43014.6042 | 101 | 101
2017-10-06 15:00 | 91 | 90 |  |  | 43014.625 | 112 | 112
2017-10-06 15:30 | 90 | 88 |  |  | 43014.6458 | 114 | 113
2017-10-06 16:00 | 85 | 83 |  |  | 43014.6667 | 107 | 107
2017-10-06 16:30 | 78 | 76 |  |  | 43014.6875 | 99 | 98
2017-10-06 17:00 | 79 | 77 |  |  | 43014.7083 | 102 | 101
2017-10-06 17:30 | 80 | 78 |  |  | 43014.7292 | 101 | 101
2017-10-06 18:00 | 79 | 77 |  |  | 43014.75 | 98 | 98
2017-10-06 18:30 | 78 | 76 |  |  | 43014.7708 | 95 | 94
2017-10-06 19:00 | 77 | 75 |  |  | 43014.7917 | 95 | 94
2017-10-06 19:30 | 78 | 75 |  |  | 43014.8125 | 94 | 93
2017-10-06 20:00 | 77 | 75 |  |  | 43014.8333 | 95 | 94
2017-10-06 20:30 | 77 | 74 |  |  | 43014.8542 | 91 | 91
2017-10-06 21:00 | 74 | 68 |  |  | 43014.875 | 84 | 84
2017-10-06 21:30 | 70 | 64 |  |  | 43014.8958 | 80 | 80
2017-10-06 22:00 | 69 | 62 |  |  | 43014.9167 | 78 | 78
2017-10-06 22:30 | 66 | 60 |  |  | 43014.9375 | 76 | 76
2017-10-06 23:00 | 63 | 57 |  |  | 43014.9583 | 71 | 71
2017-10-06 23:30 | 59 | 53 |  |  | 43014.9792 | 67 | 67
2017-10-07 | 57 | 49 |  |  | 43015 | 62 | 62
2017-10-07 00:30 | 53 | 44 |  |  | 43015.0208 | 56 | 55
2017-10-07 01:00 | 46 | 42 |  |  | 43015.0417 | 52 | 51
2017-10-07 01:30 | 44 | 40 |  |  | 43015.0625 | 49 | 49
2017-10-07 02:00 | 43 | 39 |  |  | 43015.0833 | 48 | 48
2017-10-07 02:30 | 42 | 38 |  |  | 43015.1042 | 46 | 46
2017-10-07 03:00 | 39 | 33 |  |  | 43015.125 | 42 | 42
2017-10-07 03:30 | 38 | 32 |  |  | 43015.1458 | 40 | 40
2017-10-07 04:00 | 36 | 30 |  |  | 43015.1667 | 38 | 38
2017-10-07 04:30 | 35 | 29 |  |  | 43015.1875 | 37 | 37
2017-10-07 05:00 | 36 | 29 |  |  | 43015.2083 | 38 | 38
2017-10-07 05:30 | 38 | 31 |  |  | 43015.2292 | 39 | 39
2017-10-07 06:00 | 38 | 32 |  |  | 43015.25 | 42 | 42
2017-10-07 06:30 | 39 | 34 |  |  | 43015.2708 | 44 | 44
2017-10-07 07:00 | 41 | 35 |  |  | 43015.2917 | 47 | 47
2017-10-07 07:30 | 43 | 38 |  |  | 43015.3125 | 52 | 52
2017-10-07 08:00 | 45 | 40 |  |  | 43015.3333 | 54 | 54
2017-10-07 08:30 | 54 | 49 |  |  | 43015.3542 | 65 | 65
2017-10-07 09:00 | 58 | 54 |  |  | 43015.375 | 71 | 71
2017-10-07 09:30 | 59 | 55 |  |  | 43015.3958 | 72 | 72
2017-10-07 10:00 | 56 | 51 |  |  | 43015.4167 | 67 | 66
2017-10-07 10:30 | 57 | 52 |  |  | 43015.4375 | 68 | 67
2017-10-07 11:00 | 60 | 56 |  |  | 43015.4583 | 72 | 72
2017-10-07 11:30 | 60 | 55 |  |  | 43015.4792 | 71 | 70
2017-10-07 12:00 | 58 | 54 |  |  | 43015.5 | 69 | 69
2017-10-07 12:30 | 54 | 49 |  |  | 43015.5208 | 66 | 65
2017-10-07 13:00 | 49 | 43 |  |  | 43015.5417 | 59 | 58
2017-10-07 13:30 | 50 | 43 |  |  | 43015.5625 | 59 | 59
2017-10-07 14:00 | 56 | 51 |  |  | 43015.5833 | 64 | 64
2017-10-07 14:30 | 60 | 55 |  |  | 43015.6042 | 69 | 69
2017-10-07 15:00 | 59 | 54 |  |  | 43015.625 | 68 | 68
2017-10-07 15:30 | 56 | 52 |  |  | 43015.6458 | 65 | 65
2017-10-07 16:00 | 58 | 55 |  |  | 43015.6667 | 70 | 70
2017-10-07 16:30 | 57 | 54 |  |  | 43015.6875 | 69 | 69
2017-10-07 17:00 | 58 | 54 |  |  | 43015.7083 | 69 | 69
2017-10-07 17:30 | 59 | 55 |  |  | 43015.7292 | 70 | 70
2017-10-07 18:00 | 59 | 55 |  |  | 43015.75 | 72 | 72
2017-10-07 18:30 | 59 | 55 |  |  | 43015.7708 | 71 | 71
2017-10-07 19:00 | 59 | 55 |  |  | 43015.7917 | 72 | 72
2017-10-07 19:30 | 58 | 54 |  |  | 43015.8125 | 69 | 69
2017-10-07 20:00 | 56 | 52 |  |  | 43015.8333 | 67 | 67
2017-10-07 20:30 | 57 | 51 |  |  | 43015.8542 | 66 | 65
2017-10-07 21:00 | 54 | 48 |  |  | 43015.875 | 61 | 60
2017-10-07 21:30 | 52 | 46 |  |  | 43015.8958 | 60 | 59
2017-10-07 22:00 | 51 | 45 |  |  | 43015.9167 | 59 | 59
2017-10-07 22:30 | 52 | 47 |  |  | 43015.9375 | 61 | 61
2017-10-07 23:00 | 52 | 48 |  |  | 43015.9583 | 60 | 60
2017-10-07 23:30 | 51 | 46 |  |  | 43015.9792 | 58 | 58
2017-10-08 | 47 | 42 |  |  | 43016 | 53 | 53
2017-10-08 00:30 | 42 | 36 |  |  | 43016.0208 | 47 | 47
2017-10-08 01:00 | 39 | 33 |  |  | 43016.0417 | 43 | 43
2017-10-08 01:30 | 40 | 34 |  |  | 43016.0625 | 43 | 43
2017-10-08 02:00 | 38 | 32 |  |  | 43016.0833 | 44 | 44
2017-10-08 02:30 | 36 | 31 |  |  | 43016.1042 | 41 | 41
2017-10-08 03:00 | 36 | 31 |  |  | 43016.125 | 40 | 40
2017-10-08 03:30 | 36 | 31 |  |  | 43016.1458 | 40 | 40
2017-10-08 04:00 | 35 | 29 |  |  | 43016.1667 | 40 | 40
2017-10-08 04:30 | 35 | 30 |  |  | 43016.1875 | 40 | 40
2017-10-08 05:00 | 35 | 30 |  |  | 43016.2083 | 40 | 40
2017-10-08 05:30 | 34 | 29 |  |  | 43016.2292 | 40 | 40
2017-10-08 06:00 | 32 | 27 |  |  | 43016.25 | 37 | 37
2017-10-08 06:30 | 31 | 26 |  |  | 43016.2708 | 36 | 36
2017-10-08 07:00 | 32 | 25 |  |  | 43016.2917 | 36 | 36
2017-10-08 07:30 | 32 | 25 |  |  | 43016.3125 | 38 | 38
2017-10-08 08:00 | 30 | 23 |  |  | 43016.3333 | 37 | 37
2017-10-08 08:30 | 36 | 28 |  |  | 43016.3542 | 44 | 44
2017-10-08 09:00 | 39 | 31 |  |  | 43016.375 | 47 | 47
2017-10-08 09:30 | 39 | 32 |  |  | 43016.3958 | 49 | 49
2017-10-08 10:00 | 45 | 39 |  |  | 43016.4167 | 55 | 55
2017-10-08 10:30 | 46 | 39 |  |  | 43016.4375 | 53 | 52
2017-10-08 11:00 | 46 | 39 |  |  | 43016.4583 | 53 | 52
2017-10-08 11:30 | 45 | 38 |  |  | 43016.4792 | 54 | 53
2017-10-08 12:00 | 42 | 34 |  |  | 43016.5 | 49 | 47
2017-10-08 12:30 | 47 | 40 |  |  | 43016.5208 | 54 | 53
2017-10-08 13:00 | 50 | 44 |  |  | 43016.5417 | 57 | 56
2017-10-08 13:30 | 51 | 44 |  |  | 43016.5625 | 58 | 58
2017-10-08 14:00 | 52 | 46 |  |  | 43016.5833 | 60 | 60
2017-10-08 14:30 | 51 | 46 |  |  | 43016.6042 | 59 | 59
2017-10-08 15:00 | 49 | 43 |  |  | 43016.625 | 58 | 58
2017-10-08 15:30 | 50 | 44 |  |  | 43016.6458 | 57 | 57
2017-10-08 16:00 | 49 | 44 |  |  | 43016.6667 | 58 | 58
2017-10-08 16:30 | 49 | 44 |  |  | 43016.6875 | 60 | 60
2017-10-08 17:00 | 52 | 48 |  |  | 43016.7083 | 64 | 64
2017-10-08 17:30 | 54 | 51 |  |  | 43016.7292 | 66 | 65
2017-10-08 18:00 | 58 | 54 |  |  | 43016.75 | 69 | 69
2017-10-08 18:30 | 63 | 60 |  |  | 43016.7708 | 76 | 76
2017-10-08 19:00 | 67 | 64 |  |  | 43016.7917 | 79 | 79
2017-10-08 19:30 | 65 | 62 |  |  | 43016.8125 | 78 | 78
2017-10-08 20:00 | 63 | 60 |  |  | 43016.8333 | 76 | 76
2017-10-08 20:30 | 61 | 58 |  |  | 43016.8542 | 74 | 74
2017-10-08 21:00 | 57 | 54 |  |  | 43016.875 | 69 | 69
2017-10-08 21:30 | 55 | 52 |  |  | 43016.8958 | 66 | 66
2017-10-08 22:00 | 53 | 49 |  |  | 43016.9167 | 66 | 66
2017-10-08 22:30 | 53 | 48 |  |  | 43016.9375 | 65 | 65
2017-10-08 23:00 | 52 | 48 |  |  | 43016.9583 | 63 | 63
2017-10-08 23:30 | 47 | 43 |  |  | 43016.9792 | 58 | 58
2017-10-09 | 41 | 36 |  |  | 43017 | 52 | 52
2017-10-09 00:30 | 38 | 33 |  |  | 43017.0208 | 47 | 47
2017-10-09 01:00 | 36 | 31 |  |  | 43017.0417 | 46 | 46
2017-10-09 01:30 | 36 | 32 |  |  | 43017.0625 | 44 | 44
2017-10-09 02:00 | 38 | 34 |  |  | 43017.0833 | 45 | 45
2017-10-09 02:30 | 37 | 33 |  |  | 43017.1042 | 44 | 44
2017-10-09 03:00 | 38 | 34 |  |  | 43017.125 | 45 | 45
2017-10-09 03:30 | 38 | 33 |  |  | 43017.1458 | 43 | 43
2017-10-09 04:00 | 37 | 32 |  |  | 43017.1667 | 42 | 42
2017-10-09 04:30 | 38 | 33 |  |  | 43017.1875 | 43 | 43
2017-10-09 05:00 | 38 | 33 |  |  | 43017.2083 | 44 | 44
2017-10-09 05:30 | 42 | 37 |  |  | 43017.2292 | 47 | 47
2017-10-09 06:00 | 46 | 39 |  |  | 43017.25 | 52 | 51
2017-10-09 06:30 | 58 | 52 |  |  | 43017.2708 | 67 | 67
2017-10-09 07:00 | 63 | 58 |  |  | 43017.2917 | 76 | 76
2017-10-09 07:30 | 82 | 77 |  |  | 43017.3125 | 109 | 109
2017-10-09 08:00 | 85 | 81 |  |  | 43017.3333 | 115 | 115
2017-10-09 08:30 | 89 | 85 |  |  | 43017.3542 | 120 | 120
2017-10-09 09:00 | 89 | 85 |  |  | 43017.375 | 118 | 118
2017-10-09 09:30 | 84 | 80 |  |  | 43017.3958 | 112 | 112
2017-10-09 10:00 | 80 | 75 |  |  | 43017.4167 | 106 | 106
2017-10-09 10:30 | 83 | 78 |  |  | 43017.4375 | 111 | 111
2017-10-09 11:00 | 87 | 84 |  |  | 43017.4583 | 120 | 120
2017-10-09 11:30 | 84 | 82 |  |  | 43017.4792 | 118 | 117
2017-10-09 12:00 | 84 | 83 |  |  | 43017.5 | 121 | 120
2017-10-09 12:30 | 86 | 85 |  |  | 43017.5208 | 124 | 124
2017-10-09 13:00 | 91 | 90 |  |  | 43017.5417 | 129 | 129
2017-10-09 13:30 | 90 | 89 |  |  | 43017.5625 | 131 | 131
2017-10-09 14:00 | 88 | 87 |  |  | 43017.5833 | 125 | 124
2017-10-09 14:30 | 92 | 91 |  |  | 43017.6042 | 130 | 129
2017-10-09 15:00 | 90 | 90 |  |  | 43017.625 | 130 | 129
2017-10-09 15:30 | 94 | 94 |  |  | 43017.6458 | 131 | 130
2017-10-09 16:00 | 103 | 102 |  |  | 43017.6667 | 140 | 139
2017-10-09 16:30 | 99 | 98 |  |  | 43017.6875 | 137 | 135
2017-10-09 17:00 | 96 | 96 |  |  | 43017.7083 | 133 | 131
2017-10-09 17:30 | 93 | 93 |  |  | 43017.7292 | 129 | 127
2017-10-09 18:00 | 93 | 93 |  |  | 43017.75 | 127 | 126
2017-10-09 18:30 | 95 | 94 |  |  | 43017.7708 | 128 | 125
2017-10-09 19:00 | 97 | 97 |  |  | 43017.7917 | 129 | 126
2017-10-09 19:30 | 94 | 93 |  |  | 43017.8125 | 124 | 123
2017-10-09 20:00 | 93 | 92 |  |  | 43017.8333 | 122 | 121
2017-10-09 20:30 | 89 | 89 |  |  | 43017.8542 | 119 | 117
2017-10-09 21:00 | 84 | 84 |  |  | 43017.875 | 113 | 111
2017-10-09 21:30 | 81 | 81 |  |  | 43017.8958 | 108 | 106
2017-10-09 22:00 | 76 | 75 |  |  | 43017.9167 | 104 | 102
2017-10-09 22:30 | 75 | 73 |  |  | 43017.9375 | 100 | 99
2017-10-09 23:00 | 71 | 69 |  |  | 43017.9583 | 93 | 92
2017-10-09 23:30 | 66 | 64 |  |  | 43017.9792 | 87 | 87
2017-10-10 | 60 | 59 |  |  | 43018 | 82 | 81
2017-10-10 00:30 | 54 | 53 |  |  | 43018.0208 | 74 | 73
2017-10-10 01:00 | 51 | 50 |  |  | 43018.0417 | 70 | 69
2017-10-10 01:30 | 50 | 48 |  |  | 43018.0625 | 68 | 66
2017-10-10 02:00 | 48 | 46 |  |  | 43018.0833 | 67 | 65
2017-10-10 02:30 | 48 | 46 |  |  | 43018.1042 | 67 | 65
2017-10-10 03:00 | 49 | 48 |  |  | 43018.125 | 66 | 64
2017-10-10 03:30 | 50 | 49 |  |  | 43018.1458 | 66 | 64
2017-10-10 04:00 | 47 | 46 |  |  | 43018.1667 | 66 | 64
2017-10-10 04:30 | 48 | 47 |  |  | 43018.1875 | 68 | 67
2017-10-10 05:00 | 50 | 49 |  |  | 43018.2083 | 69 | 68
2017-10-10 05:30 | 54 | 52 |  |  | 43018.2292 | 75 | 74
2017-10-10 06:00 | 58 | 56 |  |  | 43018.25 | 81 | 80
2017-10-10 06:30 | 66 | 65 |  |  | 43018.2708 | 95 | 94
2017-10-10 07:00 | 73 | 72 |  |  | 43018.2917 | 105 | 104
2017-10-10 07:30 | 81 | 80 |  |  | 43018.3125 | 116 | 116
2017-10-10 08:00 | 71 | 70 |  |  | 43018.3333 | 99 | 99
2017-10-10 08:30 | 63 | 62 |  |  | 43018.3542 | 87 | 87
2017-10-10 09:00 | 65 | 64 |  |  | 43018.375 | 89 | 89
2017-10-10 09:30 | 67 | 66 |  |  | 43018.3958 | 91 | 91
2017-10-10 10:00 | 68 | 67 |  |  | 43018.4167 | 91 | 91
2017-10-10 10:30 | 71 | 69 |  |  | 43018.4375 | 94 | 92
2017-10-10 11:00 | 74 | 73 |  |  | 43018.4583 | 98 | 95
2017-10-10 11:30 | 76 | 75 |  |  | 43018.4792 | 100 | 97
2017-10-10 12:00 | 75 | 74 |  |  | 43018.5 | 99 | 97
2017-10-10 12:30 | 75 | 74 |  |  | 43018.5208 | 99 | 96
2017-10-10 13:00 | 77 | 76 |  |  | 43018.5417 | 100 | 97
2017-10-10 13:30 | 79 | 77 |  |  | 43018.5625 | 102 | 98
2017-10-10 14:00 | 76 | 74 |  |  | 43018.5833 | 101 | 97
2017-10-10 14:30 | 77 | 75 |  |  | 43018.6042 | 103 | 99
2017-10-10 15:00 | 78 | 76 |  |  | 43018.625 | 104 | 100
2017-10-10 15:30 | 79 | 76 |  |  | 43018.6458 | 104 | 100
2017-10-10 16:00 | 80 | 77 |  |  | 43018.6667 | 106 | 100
2017-10-10 16:30 | 76 | 72 |  |  | 43018.6875 | 100 | 93
2017-10-10 17:00 | 75 | 71 |  |  | 43018.7083 | 97 | 91
2017-10-10 17:30 | 71 | 69 |  |  | 43018.7292 | 90 | 88
2017-10-10 18:00 | 68 | 68 |  |  | 43018.75 | 88 | 87
2017-10-10 18:30 | 70 | 68 |  |  | 43018.7708 | 86 | 85
2017-10-10 19:00 | 70 | 68 |  |  | 43018.7917 | 86 | 84
2017-10-10 19:30 | 68 | 67 |  |  | 43018.8125 | 82 | 80
2017-10-10 20:00 | 67 | 66 |  |  | 43018.8333 | 81 | 80
2017-10-10 20:30 | 65 | 64 |  |  | 43018.8542 | 78 | 77
2017-10-10 21:00 | 60 | 60 |  |  | 43018.875 | 74 | 74
2017-10-10 21:30 | 56 | 56 |  |  | 43018.8958 | 70 | 70
2017-10-10 22:00 | 53 | 53 |  |  | 43018.9167 | 68 | 68
2017-10-10 22:30 | 52 | 52 |  |  | 43018.9375 | 66 | 66
2017-10-10 23:00 | 51 | 51 |  |  | 43018.9583 | 62 | 62
2017-10-10 23:30 | 47 | 46 |  |  | 43018.9792 | 57 | 57
2017-10-11 | 44 | 42 |  |  | 43019 | 53 | 53
2017-10-11 00:30 | 39 | 37 |  |  | 43019.0208 | 47 | 47
2017-10-11 01:00 | 38 | 36 |  |  | 43019.0417 | 44 | 44
2017-10-11 01:30 | 37 | 34 |  |  | 43019.0625 | 43 | 43
2017-10-11 02:00 | 39 | 37 |  |  | 43019.0833 | 44 | 44
2017-10-11 02:30 | 38 | 35 |  |  | 43019.1042 | 43 | 43
2017-10-11 03:00 | 38 | 35 |  |  | 43019.125 | 43 | 43
2017-10-11 03:30 | 38 | 35 |  |  | 43019.1458 | 43 | 43
2017-10-11 04:00 | 38 | 35 |  |  | 43019.1667 | 42 | 42
2017-10-11 04:30 | 38 | 35 |  |  | 43019.1875 | 42 | 42
2017-10-11 05:00 | 39 | 36 |  |  | 43019.2083 | 44 | 44
2017-10-11 05:30 | 39 | 37 |  |  | 43019.2292 | 46 | 46
2017-10-11 06:00 | 40 | 39 |  |  | 43019.25 | 49 | 49
2017-10-11 06:30 | 45 | 45 |  |  | 43019.2708 | 60 | 60
2017-10-11 07:00 | 50 | 50 |  |  | 43019.2917 | 68 | 68
2017-10-11 07:30 | 56 | 56 |  |  | 43019.3125 | 77 | 77
2017-10-11 08:00 | 60 | 59 |  |  | 43019.3333 | 82 | 82
2017-10-11 08:30 | 63 | 62 |  |  | 43019.3542 | 87 | 86
2017-10-11 09:00 | 65 | 61 |  |  | 43019.375 | 90 | 85
2017-10-11 09:30 | 66 | 62 |  |  | 43019.3958 | 90 | 85
2017-10-11 10:00 | 67 | 63 |  |  | 43019.4167 | 91 | 85
2017-10-11 10:30 | 68 | 64 |  |  | 43019.4375 | 92 | 88
2017-10-11 11:00 | 70 | 66 |  |  | 43019.4583 | 96 | 92
2017-10-11 11:30 | 71 | 68 |  |  | 43019.4792 | 98 | 94
2017-10-11 12:00 | 73 | 69 |  |  | 43019.5 | 98 | 94
2017-10-11 12:30 | 71 | 67 |  |  | 43019.5208 | 93 | 89
2017-10-11 13:00 | 70 | 67 |  |  | 43019.5417 | 97 | 93
2017-10-11 13:30 | 72 | 71 |  |  | 43019.5625 | 97 | 94
2017-10-11 14:00 | 85 | 84 |  |  | 43019.5833 | 120 | 117
2017-10-11 14:30 | 93 | 92 |  |  | 43019.6042 | 135 | 132
2017-10-11 15:00 | 93 | 92 |  |  | 43019.625 | 135 | 132
2017-10-11 15:30 | 92 | 91 |  |  | 43019.6458 | 133 | 131
2017-10-11 16:00 | 93 | 91 |  |  | 43019.6667 | 136 | 133
2017-10-11 16:30 | 95 | 93 |  |  | 43019.6875 | 135 | 131
2017-10-11 17:00 | 96 | 94 |  |  | 43019.7083 | 135 | 132
2017-10-11 17:30 | 91 | 90 |  |  | 43019.7292 | 125 | 124
2017-10-11 18:00 | 89 | 89 |  |  | 43019.75 | 121 | 121
2017-10-11 18:30 | 90 | 90 |  |  | 43019.7708 | 120 | 120
2017-10-11 19:00 | 91 | 91 |  |  | 43019.7917 | 120 | 120
2017-10-11 19:30 | 87 | 86 |  |  | 43019.8125 | 116 | 116
2017-10-11 20:00 | 85 | 85 |  |  | 43019.8333 | 114 | 114
2017-10-11 20:30 | 85 | 85 |  |  | 43019.8542 | 113 | 113
2017-10-11 21:00 | 78 | 78 |  |  | 43019.875 | 105 | 105
2017-10-11 21:30 | 76 | 75 |  |  | 43019.8958 | 102 | 101
2017-10-11 22:00 | 73 | 72 |  |  | 43019.9167 | 100 | 99
2017-10-11 22:30 | 69 | 69 |  |  | 43019.9375 | 97 | 96
2017-10-11 23:00 | 67 | 67 |  |  | 43019.9583 | 92 | 92
2017-10-11 23:30 | 62 | 62 |  |  | 43019.9792 | 87 | 87
2017-10-12 | 61 | 60 |  |  | 43020 | 85 | 85
2017-10-12 00:30 | 57 | 56 |  |  | 43020.0208 | 79 | 78
2017-10-12 01:00 | 52 | 51 |  |  | 43020.0417 | 72 | 72
2017-10-12 01:30 | 51 | 50 |  |  | 43020.0625 | 69 | 69
2017-10-12 02:00 | 51 | 50 |  |  | 43020.0833 | 69 | 69
2017-10-12 02:30 | 51 | 51 |  |  | 43020.1042 | 69 | 69
2017-10-12 03:00 | 51 | 50 |  |  | 43020.125 | 69 | 69
2017-10-12 03:30 | 51 | 50 |  |  | 43020.1458 | 68 | 68
2017-10-12 04:00 | 50 | 48 |  |  | 43020.1667 | 66 | 66
2017-10-12 04:30 | 51 | 50 |  |  | 43020.1875 | 68 | 68
2017-10-12 05:00 | 52 | 51 |  |  | 43020.2083 | 70 | 70
2017-10-12 05:30 | 55 | 54 |  |  | 43020.2292 | 76 | 76
2017-10-12 06:00 | 58 | 58 |  |  | 43020.25 | 83 | 83
2017-10-12 06:30 | 67 | 67 |  |  | 43020.2708 | 95 | 95
2017-10-12 07:00 | 72 | 72 |  |  | 43020.2917 | 103 | 103
2017-10-12 07:30 | 83 | 83 |  |  | 43020.3125 | 117 | 117
2017-10-12 08:00 | 86 | 86 |  |  | 43020.3333 | 123 | 123
2017-10-12 08:30 | 87 | 87 |  |  | 43020.3542 | 127 | 127
2017-10-12 09:00 | 89 | 89 |  |  | 43020.375 | 129 | 129
2017-10-12 09:30 | 90 | 89 |  |  | 43020.3958 | 129 | 128
2017-10-12 10:00 | 89 | 88 |  |  | 43020.4167 | 128 | 127
2017-10-12 10:30 | 90 | 89 |  |  | 43020.4375 | 127 | 126
2017-10-12 11:00 | 90 | 90 |  |  | 43020.4583 | 128 | 128
2017-10-12 11:30 | 89 | 88 |  |  | 43020.4792 | 126 | 126
2017-10-12 12:00 | 89 | 89 |  |  | 43020.5 | 127 | 126
2017-10-12 12:30 | 89 | 89 |  |  | 43020.5208 | 127 | 126
2017-10-12 13:00 | 90 | 89 |  |  | 43020.5417 | 127 | 126
2017-10-12 13:30 | 92 | 91 |  |  | 43020.5625 | 130 | 129
2017-10-12 14:00 | 91 | 91 |  |  | 43020.5833 | 129 | 128
2017-10-12 14:30 | 92 | 92 |  |  | 43020.6042 | 129 | 129
2017-10-12 15:00 | 88 | 88 |  |  | 43020.625 | 124 | 124
2017-10-12 15:30 | 90 | 90 |  |  | 43020.6458 | 126 | 125
2017-10-12 16:00 | 91 | 90 |  |  | 43020.6667 | 127 | 126
2017-10-12 16:30 | 91 | 91 |  |  | 43020.6875 | 126 | 125
2017-10-12 17:00 | 93 | 92 |  |  | 43020.7083 | 127 | 126
2017-10-12 17:30 | 91 | 90 |  |  | 43020.7292 | 124 | 123
2017-10-12 18:00 | 89 | 89 |  |  | 43020.75 | 122 | 121
2017-10-12 18:30 | 91 | 90 |  |  | 43020.7708 | 120 | 119
2017-10-12 19:00 | 93 | 92 |  |  | 43020.7917 | 122 | 120
2017-10-12 19:30 | 91 | 90 |  |  | 43020.8125 | 120 | 118
2017-10-12 20:00 | 91 | 90 |  |  | 43020.8333 | 117 | 116
2017-10-12 20:30 | 88 | 87 |  |  | 43020.8542 | 114 | 113
2017-10-12 21:00 | 82 | 81 |  |  | 43020.875 | 107 | 107
2017-10-12 21:30 | 78 | 76 |  |  | 43020.8958 | 101 | 100
2017-10-12 22:00 | 74 | 73 |  |  | 43020.9167 | 100 | 98
2017-10-12 22:30 | 72 | 71 |  |  | 43020.9375 | 97 | 96
2017-10-12 23:00 | 70 | 68 |  |  | 43020.9583 | 92 | 91
2017-10-12 23:30 | 65 | 64 |  |  | 43020.9792 | 87 | 85
2017-10-13 | 61 | 59 |  |  | 43021 | 83 | 81
2017-10-13 00:30 | 56 | 55 |  |  | 43021.0208 | 76 | 74
2017-10-13 01:00 | 54 | 52 |  |  | 43021.0417 | 71 | 69
2017-10-13 01:30 | 50 | 48 |  |  | 43021.0625 | 68 | 65
2017-10-13 02:00 | 48 | 46 |  |  | 43021.0833 | 67 | 64
2017-10-13 02:30 | 49 | 46 |  |  | 43021.1042 | 66 | 63
2017-10-13 03:00 | 47 | 44 |  |  | 43021.125 | 65 | 62
2017-10-13 03:30 | 48 | 45 |  |  | 43021.1458 | 65 | 62
2017-10-13 04:00 | 49 | 46 |  |  | 43021.1667 | 65 | 62
2017-10-13 04:30 | 51 | 49 |  |  | 43021.1875 | 68 | 65
2017-10-13 05:00 | 53 | 51 |  |  | 43021.2083 | 71 | 68
2017-10-13 05:30 | 55 | 53 |  |  | 43021.2292 | 75 | 73
2017-10-13 06:00 | 57 | 56 |  |  | 43021.25 | 80 | 79
2017-10-13 06:30 | 65 | 65 |  |  | 43021.2708 | 93 | 92
2017-10-13 07:00 | 70 | 68 |  |  | 43021.2917 | 103 | 100
2017-10-13 07:30 | 76 | 73 |  |  | 43021.3125 | 112 | 109
2017-10-13 08:00 | 77 | 75 |  |  | 43021.3333 | 114 | 113
2017-10-13 08:30 | 64 | 62 |  |  | 43021.3542 | 95 | 94
2017-10-13 09:00 | 63 | 62 |  |  | 43021.375 | 94 | 92
2017-10-13 09:30 | 65 | 63 |  |  | 43021.3958 | 96 | 93
2017-10-13 10:00 | 66 | 64 |  |  | 43021.4167 | 97 | 94
2017-10-13 10:30 | 65 | 65 |  |  | 43021.4375 | 98 | 97
2017-10-13 11:00 | 68 | 68 |  |  | 43021.4583 | 100 | 99
2017-10-13 11:30 | 69 | 69 |  |  | 43021.4792 | 102 | 101
2017-10-13 12:00 | 75 | 75 |  |  | 43021.5 | 108 | 107
2017-10-13 12:30 | 85 | 85 |  |  | 43021.5208 | 124 | 123
2017-10-13 13:00 | 88 | 88 |  |  | 43021.5417 | 127 | 126
2017-10-13 13:30 | 82 | 82 |  |  | 43021.5625 | 113 | 113
2017-10-13 14:00 | 77 | 77 |  |  | 43021.5833 | 101 | 101
2017-10-13 14:30 | 76 | 75 |  |  | 43021.6042 | 102 | 101
2017-10-13 15:00 | 74 | 74 |  |  | 43021.625 | 103 | 102
2017-10-13 15:30 | 71 | 71 |  |  | 43021.6458 | 102 | 102
2017-10-13 16:00 | 73 | 73 |  |  | 43021.6667 | 101 | 100
2017-10-13 16:30 | 74 | 74 |  |  | 43021.6875 | 100 | 100
2017-10-13 17:00 | 73 | 73 |  |  | 43021.7083 | 98 | 97
2017-10-13 17:30 | 71 | 71 |  |  | 43021.7292 | 95 | 95
2017-10-13 18:00 | 70 | 70 |  |  | 43021.75 | 92 | 92
2017-10-13 18:30 | 68 | 68 |  |  | 43021.7708 | 88 | 88
2017-10-13 19:00 | 68 | 68 |  |  | 43021.7917 | 88 | 88
2017-10-13 19:30 | 67 | 66 |  |  | 43021.8125 | 86 | 86
2017-10-13 20:00 | 66 | 65 |  |  | 43021.8333 | 84 | 84
2017-10-13 20:30 | 65 | 64 |  |  | 43021.8542 | 83 | 83
2017-10-13 21:00 | 62 | 62 |  |  | 43021.875 | 80 | 80
2017-10-13 21:30 | 60 | 60 |  |  | 43021.8958 | 77 | 77
2017-10-13 22:00 | 57 | 57 |  |  | 43021.9167 | 76 | 76
2017-10-13 22:30 | 57 | 56 |  |  | 43021.9375 | 75 | 75
2017-10-13 23:00 | 56 | 55 |  |  | 43021.9583 | 72 | 72
2017-10-13 23:30 | 52 | 51 |  |  | 43021.9792 | 68 | 67
2017-10-14 | 49 | 44 |  |  | 43022 | 61 | 59
2017-10-14 00:30 | 47 | 41 |  |  | 43022.0208 | 56 | 54
2017-10-14 01:00 | 44 | 38 |  |  | 43022.0417 | 52 | 50
2017-10-14 01:30 | 41 | 35 |  |  | 43022.0625 | 49 | 46
2017-10-14 02:00 | 41 | 34 |  |  | 43022.0833 | 48 | 45
2017-10-14 02:30 | 41 | 34 |  |  | 43022.1042 | 48 | 46
2017-10-14 03:00 | 42 | 34 |  |  | 43022.125 | 49 | 46
2017-10-14 03:30 | 43 | 35 |  |  | 43022.1458 | 49 | 46
2017-10-14 04:00 | 43 | 35 |  |  | 43022.1667 | 49 | 46
2017-10-14 04:30 | 41 | 34 |  |  | 43022.1875 | 48 | 45
2017-10-14 05:00 | 41 | 33 |  |  | 43022.2083 | 47 | 44
2017-10-14 05:30 | 41 | 33 |  |  | 43022.2292 | 47 | 44
2017-10-14 06:00 | 40 | 32 |  |  | 43022.25 | 47 | 45
2017-10-14 06:30 | 41 | 33 |  |  | 43022.2708 | 51 | 48
2017-10-14 07:00 | 43 | 37 |  |  | 43022.2917 | 54 | 52
2017-10-14 07:30 | 44 | 39 |  |  | 43022.3125 | 56 | 55
2017-10-14 08:00 | 45 | 40 |  |  | 43022.3333 | 59 | 58
2017-10-14 08:30 | 46 | 42 |  |  | 43022.3542 | 62 | 61
2017-10-14 09:00 | 49 | 46 |  |  | 43022.375 | 64 | 63
2017-10-14 09:30 | 48 | 45 |  |  | 43022.3958 | 65 | 65
2017-10-14 10:00 | 52 | 48 |  |  | 43022.4167 | 71 | 70
2017-10-14 10:30 | 51 | 47 |  |  | 43022.4375 | 70 | 68
2017-10-14 11:00 | 52 | 48 |  |  | 43022.4583 | 69 | 68
2017-10-14 11:30 | 52 | 47 |  |  | 43022.4792 | 66 | 65
2017-10-14 12:00 | 50 | 45 |  |  | 43022.5 | 67 | 65
2017-10-14 12:30 | 54 | 49 |  |  | 43022.5208 | 71 | 70
2017-10-14 13:00 | 55 | 50 |  |  | 43022.5417 | 71 | 70
2017-10-14 13:30 | 52 | 47 |  |  | 43022.5625 | 67 | 66
2017-10-14 14:00 | 49 | 43 |  |  | 43022.5833 | 61 | 60
2017-10-14 14:30 | 49 | 43 |  |  | 43022.6042 | 60 | 58
2017-10-14 15:00 | 48 | 42 |  |  | 43022.625 | 60 | 58
2017-10-14 15:30 | 46 | 41 |  |  | 43022.6458 | 61 | 59
2017-10-14 16:00 | 48 | 43 |  |  | 43022.6667 | 63 | 61
2017-10-14 16:30 | 54 | 49 |  |  | 43022.6875 | 69 | 68
2017-10-14 17:00 | 56 | 50 |  |  | 43022.7083 | 70 | 68
2017-10-14 17:30 | 57 | 51 |  |  | 43022.7292 | 71 | 69
2017-10-14 18:00 | 58 | 53 |  |  | 43022.75 | 73 | 71
2017-10-14 18:30 | 59 | 54 |  |  | 43022.7708 | 75 | 73
2017-10-14 19:00 | 60 | 55 |  |  | 43022.7917 | 76 | 74
2017-10-14 19:30 | 58 | 53 |  |  | 43022.8125 | 74 | 73
2017-10-14 20:00 | 59 | 55 |  |  | 43022.8333 | 73 | 72
2017-10-14 20:30 | 58 | 53 |  |  | 43022.8542 | 72 | 71
2017-10-14 21:00 | 56 | 51 |  |  | 43022.875 | 69 | 68
2017-10-14 21:30 | 53 | 48 |  |  | 43022.8958 | 66 | 64
2017-10-14 22:00 | 52 | 46 |  |  | 43022.9167 | 66 | 64
2017-10-14 22:30 | 54 | 48 |  |  | 43022.9375 | 68 | 66
2017-10-14 23:00 | 55 | 49 |  |  | 43022.9583 | 68 | 65
2017-10-14 23:30 | 53 | 46 |  |  | 43022.9792 | 64 | 62
2017-10-15 | 49 | 41 |  |  | 43023 | 59 | 57
2017-10-15 00:30 | 44 | 36 |  |  | 43023.0208 | 53 | 50
2017-10-15 01:00 | 44 | 34 |  |  | 43023.0417 | 50 | 46
2017-10-15 01:30 | 42 | 32 |  |  | 43023.0625 | 48 | 44
2017-10-15 02:00 | 42 | 32 |  |  | 43023.0833 | 48 | 44
2017-10-15 02:30 | 41 | 31 |  |  | 43023.1042 | 47 | 42
2017-10-15 03:00 | 37 | 30 |  |  | 43023.125 | 42 | 41
2017-10-15 03:30 | 37 | 30 |  |  | 43023.1458 | 42 | 40
2017-10-15 04:00 | 36 | 29 |  |  | 43023.1667 | 41 | 40
2017-10-15 04:30 | 36 | 29 |  |  | 43023.1875 | 41 | 40
2017-10-15 05:00 | 35 | 28 |  |  | 43023.2083 | 39 | 38
2017-10-15 05:30 | 33 | 26 |  |  | 43023.2292 | 39 | 37
2017-10-15 06:00 | 37 | 29 |  |  | 43023.25 | 43 | 42
2017-10-15 06:30 | 39 | 32 |  |  | 43023.2708 | 48 | 47
2017-10-15 07:00 | 39 | 32 |  |  | 43023.2917 | 48 | 47
2017-10-15 07:30 | 39 | 33 |  |  | 43023.3125 | 51 | 51
2017-10-15 08:00 | 38 | 33 |  |  | 43023.3333 | 50 | 50
2017-10-15 08:30 | 40 | 36 |  |  | 43023.3542 | 52 | 52
2017-10-15 09:00 | 42 | 39 |  |  | 43023.375 | 56 | 56
2017-10-15 09:30 | 42 | 38 |  |  | 43023.3958 | 56 | 56
2017-10-15 10:00 | 41 | 37 |  |  | 43023.4167 | 51 | 51
2017-10-15 10:30 | 44 | 41 |  |  | 43023.4375 | 55 | 55
2017-10-15 11:00 | 45 | 42 |  |  | 43023.4583 | 57 | 57
2017-10-15 11:30 | 45 | 42 |  |  | 43023.4792 | 62 | 62
2017-10-15 12:00 | 47 | 44 |  |  | 43023.5 | 58 | 58
2017-10-15 12:30 | 48 | 44 |  |  | 43023.5208 | 59 | 59
2017-10-15 13:00 | 46 | 41 |  |  | 43023.5417 | 58 | 57
2017-10-15 13:30 | 45 | 40 |  |  | 43023.5625 | 60 | 59
2017-10-15 14:00 | 45 | 40 |  |  | 43023.5833 | 57 | 57
2017-10-15 14:30 | 47 | 42 |  |  | 43023.6042 | 57 | 56
2017-10-15 15:00 | 49 | 45 |  |  | 43023.625 | 62 | 61
2017-10-15 15:30 | 49 | 45 |  |  | 43023.6458 | 62 | 61
2017-10-15 16:00 | 50 | 45 |  |  | 43023.6667 | 63 | 63
2017-10-15 16:30 | 51 | 47 |  |  | 43023.6875 | 66 | 65
2017-10-15 17:00 | 52 | 48 |  |  | 43023.7083 | 66 | 65
2017-10-15 17:30 | 51 | 47 |  |  | 43023.7292 | 65 | 64
2017-10-15 18:00 | 53 | 50 |  |  | 43023.75 | 67 | 66
2017-10-15 18:30 | 56 | 53 |  |  | 43023.7708 | 71 | 70
2017-10-15 19:00 | 57 | 53 |  |  | 43023.7917 | 73 | 72
2017-10-15 19:30 | 58 | 54 |  |  | 43023.8125 | 73 | 72
2017-10-15 20:00 | 55 | 52 |  |  | 43023.8333 | 69 | 69
2017-10-15 20:30 | 51 | 48 |  |  | 43023.8542 | 66 | 66
2017-10-15 21:00 | 47 | 45 |  |  | 43023.875 | 62 | 62
2017-10-15 21:30 | 46 | 44 |  |  | 43023.8958 | 61 | 60
2017-10-15 22:00 | 46 | 44 |  |  | 43023.9167 | 62 | 61
2017-10-15 22:30 | 48 | 45 |  |  | 43023.9375 | 64 | 64
2017-10-15 23:00 | 50 | 46 |  |  | 43023.9583 | 63 | 62
2017-10-15 23:30 | 45 | 41 |  |  | 43023.9792 | 58 | 57
2017-10-16 | 43 | 39 |  |  | 43024 | 55 | 54
2017-10-16 00:30 | 42 | 37 |  |  | 43024.0208 | 51 | 50
2017-10-16 01:00 | 41 | 34 |  |  | 43024.0417 | 49 | 49
2017-10-16 01:30 | 39 | 33 |  |  | 43024.0625 | 48 | 47
2017-10-16 02:00 | 39 | 32 |  |  | 43024.0833 | 47 | 46
2017-10-16 02:30 | 40 | 33 |  |  | 43024.1042 | 46 | 45
2017-10-16 03:00 | 40 | 34 |  |  | 43024.125 | 46 | 45
2017-10-16 03:30 | 39 | 32 |  |  | 43024.1458 | 45 | 44
2017-10-16 04:00 | 39 | 32 |  |  | 43024.1667 | 44 | 43
2017-10-16 04:30 | 41 | 35 |  |  | 43024.1875 | 48 | 47
2017-10-16 05:00 | 42 | 37 |  |  | 43024.2083 | 50 | 49
2017-10-16 05:30 | 42 | 39 |  |  | 43024.2292 | 51 | 51
2017-10-16 06:00 | 50 | 47 |  |  | 43024.25 | 63 | 63
2017-10-16 06:30 | 59 | 57 |  |  | 43024.2708 | 76 | 76
2017-10-16 07:00 | 61 | 60 |  |  | 43024.2917 | 81 | 81
2017-10-16 07:30 | 64 | 64 |  |  | 43024.3125 | 88 | 88
2017-10-16 08:00 | 66 | 66 |  |  | 43024.3333 | 93 | 93
2017-10-16 08:30 | 70 | 70 |  |  | 43024.3542 | 96 | 96
2017-10-16 09:00 | 72 | 72 |  |  | 43024.375 | 97 | 97
2017-10-16 09:30 | 71 | 71 |  |  | 43024.3958 | 99 | 99
2017-10-16 10:00 | 74 | 73 |  |  | 43024.4167 | 101 | 101
2017-10-16 10:30 | 75 | 74 |  |  | 43024.4375 | 102 | 101
2017-10-16 11:00 | 73 | 73 |  |  | 43024.4583 | 100 | 100
2017-10-16 11:30 | 70 | 70 |  |  | 43024.4792 | 97 | 97
2017-10-16 12:00 | 69 | 69 |  |  | 43024.5 | 96 | 96
2017-10-16 12:30 | 69 | 69 |  |  | 43024.5208 | 95 | 95
2017-10-16 13:00 | 67 | 67 |  |  | 43024.5417 | 92 | 92
2017-10-16 13:30 | 66 | 66 |  |  | 43024.5625 | 93 | 92
2017-10-16 14:00 | 69 | 69 |  |  | 43024.5833 | 94 | 94
2017-10-16 14:30 | 69 | 69 |  |  | 43024.6042 | 93 | 93
2017-10-16 15:00 | 67 | 67 |  |  | 43024.625 | 91 | 91
2017-10-16 15:30 | 65 | 65 |  |  | 43024.6458 | 87 | 86
2017-10-16 16:00 | 63 | 63 |  |  | 43024.6667 | 88 | 87
2017-10-16 16:30 | 66 | 66 |  |  | 43024.6875 | 90 | 90
2017-10-16 17:00 | 69 | 69 |  |  | 43024.7083 | 94 | 93
2017-10-16 17:30 | 68 | 68 |  |  | 43024.7292 | 92 | 91
2017-10-16 18:00 | 70 | 70 |  |  | 43024.75 | 95 | 94
2017-10-16 18:30 | 71 | 70 |  |  | 43024.7708 | 94 | 93
2017-10-16 19:00 | 71 | 70 |  |  | 43024.7917 | 94 | 92
2017-10-16 19:30 | 69 | 67 |  |  | 43024.8125 | 90 | 88
2017-10-16 20:00 | 66 | 63 |  |  | 43024.8333 | 84 | 83
2017-10-16 20:30 | 65 | 62 |  |  | 43024.8542 | 81 | 80
2017-10-16 21:00 | 60 | 57 |  |  | 43024.875 | 74 | 73
2017-10-16 21:30 | 56 | 53 |  |  | 43024.8958 | 69 | 68
2017-10-16 22:00 | 56 | 53 |  |  | 43024.9167 | 70 | 69
2017-10-16 22:30 | 60 | 55 |  |  | 43024.9375 | 77 | 75
2017-10-16 23:00 | 61 | 56 |  |  | 43024.9583 | 76 | 73
2017-10-16 23:30 | 58 | 51 |  |  | 43024.9792 | 71 | 69
2017-10-17 | 55 | 47 |  |  | 43025 | 66 | 63
2017-10-17 00:30 | 52 | 43 |  |  | 43025.0208 | 62 | 58
2017-10-17 01:00 | 51 | 40 |  |  | 43025.0417 | 60 | 55
2017-10-17 01:30 | 51 | 39 |  |  | 43025.0625 | 58 | 54
2017-10-17 02:00 | 51 | 40 |  |  | 43025.0833 | 60 | 56
2017-10-17 02:30 | 53 | 42 |  |  | 43025.1042 | 62 | 57
2017-10-17 03:00 | 53 | 41 |  |  | 43025.125 | 63 | 57
2017-10-17 03:30 | 52 | 40 |  |  | 43025.1458 | 60 | 55
2017-10-17 04:00 | 52 | 39 |  |  | 43025.1667 | 59 | 54
2017-10-17 04:30 | 54 | 42 |  |  | 43025.1875 | 64 | 59
2017-10-17 05:00 | 55 | 45 |  |  | 43025.2083 | 68 | 63
2017-10-17 05:30 | 58 | 49 |  |  | 43025.2292 | 72 | 68
2017-10-17 06:00 | 61 | 53 |  |  | 43025.25 | 77 | 74
2017-10-17 06:30 | 63 | 58 |  |  | 43025.2708 | 84 | 82
2017-10-17 07:00 | 65 | 61 |  |  | 43025.2917 | 88 | 86
2017-10-17 07:30 | 70 | 68 |  |  | 43025.3125 | 97 | 96
2017-10-17 08:00 | 72 | 70 |  |  | 43025.3333 | 100 | 99
2017-10-17 08:30 | 73 | 71 |  |  | 43025.3542 | 104 | 102
2017-10-17 09:00 | 73 | 71 |  |  | 43025.375 | 103 | 102
2017-10-17 09:30 | 73 | 71 |  |  | 43025.3958 | 102 | 101
2017-10-17 10:00 | 73 | 70 |  |  | 43025.4167 | 102 | 101
2017-10-17 10:30 | 73 | 70 |  |  | 43025.4375 | 101 | 100
2017-10-17 11:00 | 75 | 73 |  |  | 43025.4583 | 103 | 102
2017-10-17 11:30 | 78 | 75 |  |  | 43025.4792 | 106 | 105
2017-10-17 12:00 | 75 | 72 |  |  | 43025.5 | 104 | 103
2017-10-17 12:30 | 75 | 72 |  |  | 43025.5208 | 103 | 102
2017-10-17 13:00 | 74 | 71 |  |  | 43025.5417 | 101 | 100
2017-10-17 13:30 | 75 | 72 |  |  | 43025.5625 | 102 | 101
2017-10-17 14:00 | 75 | 72 |  |  | 43025.5833 | 102 | 101
2017-10-17 14:30 | 75 | 73 |  |  | 43025.6042 | 102 | 100
2017-10-17 15:00 | 74 | 71 |  |  | 43025.625 | 101 | 99
2017-10-17 15:30 | 74 | 71 |  |  | 43025.6458 | 98 | 97
2017-10-17 16:00 | 74 | 72 |  |  | 43025.6667 | 100 | 99
2017-10-17 16:30 | 77 | 75 |  |  | 43025.6875 | 104 | 102
2017-10-17 17:00 | 76 | 73 |  |  | 43025.7083 | 102 | 101
2017-10-17 17:30 | 78 | 75 |  |  | 43025.7292 | 104 | 103
2017-10-17 18:00 | 77 | 74 |  |  | 43025.75 | 102 | 100
2017-10-17 18:30 | 77 | 74 |  |  | 43025.7708 | 101 | 99
2017-10-17 19:00 | 78 | 74 |  |  | 43025.7917 | 103 | 100
2017-10-17 19:30 | 75 | 71 |  |  | 43025.8125 | 97 | 94
2017-10-17 20:00 | 71 | 69 |  |  | 43025.8333 | 93 | 92
2017-10-17 20:30 | 71 | 69 |  |  | 43025.8542 | 93 | 92
2017-10-17 21:00 | 69 | 66 |  |  | 43025.875 | 88 | 87
2017-10-17 21:30 | 64 | 62 |  |  | 43025.8958 | 84 | 83
2017-10-17 22:00 | 62 | 60 |  |  | 43025.9167 | 82 | 81
2017-10-17 22:30 | 64 | 62 |  |  | 43025.9375 | 87 | 86
2017-10-17 23:00 | 64 | 62 |  |  | 43025.9583 | 86 | 85
2017-10-17 23:30 | 60 | 57 |  |  | 43025.9792 | 79 | 78
2017-10-18 | 56 | 52 |  |  | 43026 | 73 | 72
2017-10-18 00:30 | 53 | 48 |  |  | 43026.0208 | 68 | 66
2017-10-18 01:00 | 49 | 45 |  |  | 43026.0417 | 65 | 63
2017-10-18 01:30 | 46 | 43 |  |  | 43026.0625 | 63 | 61
2017-10-18 02:00 | 46 | 43 |  |  | 43026.0833 | 63 | 61
2017-10-18 02:30 | 47 | 44 |  |  | 43026.1042 | 64 | 62
2017-10-18 03:00 | 46 | 43 |  |  | 43026.125 | 62 | 60
2017-10-18 03:30 | 47 | 44 |  |  | 43026.1458 | 64 | 61
2017-10-18 04:00 | 46 | 43 |  |  | 43026.1667 | 62 | 60
2017-10-18 04:30 | 47 | 44 |  |  | 43026.1875 | 64 | 62
2017-10-18 05:00 | 47 | 44 |  |  | 43026.2083 | 66 | 64
2017-10-18 05:30 | 51 | 49 |  |  | 43026.2292 | 70 | 68
2017-10-18 06:00 | 55 | 53 |  |  | 43026.25 | 75 | 74
2017-10-18 06:30 | 64 | 59 |  |  | 43026.2708 | 88 | 83
2017-10-18 07:00 | 67 | 63 |  |  | 43026.2917 | 95 | 90
2017-10-18 07:30 | 71 | 68 |  |  | 43026.3125 | 102 | 97
2017-10-18 08:00 | 73 | 71 |  |  | 43026.3333 | 106 | 101
2017-10-18 08:30 | 72 | 70 |  |  | 43026.3542 | 106 | 102
2017-10-18 09:00 | 72 | 70 |  |  | 43026.375 | 106 | 103
2017-10-18 09:30 | 69 | 68 |  |  | 43026.3958 | 104 | 101
2017-10-18 10:00 | 67 | 66 |  |  | 43026.4167 | 100 | 97
2017-10-18 10:30 | 67 | 64 |  |  | 43026.4375 | 98 | 94
2017-10-18 11:00 | 67 | 64 |  |  | 43026.4583 | 94 | 89
2017-10-18 11:30 | 70 | 67 |  |  | 43026.4792 | 99 | 94
2017-10-18 12:00 | 71 | 67 |  |  | 43026.5 | 103 | 98
2017-10-18 12:30 | 70 | 66 |  |  | 43026.5208 | 102 | 97
2017-10-18 13:00 | 73 | 70 |  |  | 43026.5417 | 100 | 96
2017-10-18 13:30 | 70 | 67 |  |  | 43026.5625 | 100 | 97
2017-10-18 14:00 | 75 | 72 |  |  | 43026.5833 | 108 | 104
2017-10-18 14:30 | 70 | 66 |  |  | 43026.6042 | 101 | 97
2017-10-18 15:00 | 67 | 63 |  |  | 43026.625 | 96 | 92
2017-10-18 15:30 | 67 | 63 |  |  | 43026.6458 | 93 | 89
2017-10-18 16:00 | 71 | 68 |  |  | 43026.6667 | 99 | 95
2017-10-18 16:30 | 74 | 70 |  |  | 43026.6875 | 102 | 97
2017-10-18 17:00 | 75 | 71 |  |  | 43026.7083 | 105 | 99
2017-10-18 17:30 | 74 | 70 |  |  | 43026.7292 | 103 | 98
2017-10-18 18:00 | 75 | 70 |  |  | 43026.75 | 102 | 96
2017-10-18 18:30 | 76 | 71 |  |  | 43026.7708 | 102 | 96
2017-10-18 19:00 | 75 | 69 |  |  | 43026.7917 | 100 | 95
2017-10-18 19:30 | 73 | 67 |  |  | 43026.8125 | 96 | 90
2017-10-18 20:00 | 71 | 66 |  |  | 43026.8333 | 95 | 89
2017-10-18 20:30 | 72 | 67 |  |  | 43026.8542 | 96 | 90
2017-10-18 21:00 | 69 | 63 |  |  | 43026.875 | 92 | 85
2017-10-18 21:30 | 61 | 59 |  |  | 43026.8958 | 79 | 78
2017-10-18 22:00 | 58 | 56 |  |  | 43026.9167 | 76 | 75
2017-10-18 22:30 | 60 | 57 |  |  | 43026.9375 | 81 | 80
2017-10-18 23:00 | 59 | 56 |  |  | 43026.9583 | 78 | 77
2017-10-18 23:30 | 53 | 50 |  |  | 43026.9792 | 72 | 71
2017-10-19 | 52 | 49 |  |  | 43027 | 71 | 69
2017-10-19 00:30 | 49 | 46 |  |  | 43027.0208 | 66 | 64
2017-10-19 01:00 | 45 | 41 |  |  | 43027.0417 | 61 | 59
2017-10-19 01:30 | 44 | 39 |  |  | 43027.0625 | 58 | 55
2017-10-19 02:00 | 43 | 38 |  |  | 43027.0833 | 57 | 54
2017-10-19 02:30 | 41 | 36 |  |  | 43027.1042 | 56 | 53
2017-10-19 03:00 | 43 | 38 |  |  | 43027.125 | 57 | 54
2017-10-19 03:30 | 42 | 37 |  |  | 43027.1458 | 56 | 53
2017-10-19 04:00 | 41 | 37 |  |  | 43027.1667 | 55 | 52
2017-10-19 04:30 | 42 | 38 |  |  | 43027.1875 | 56 | 54
2017-10-19 05:00 | 42 | 38 |  |  | 43027.2083 | 57 | 54
2017-10-19 05:30 | 45 | 41 |  |  | 43027.2292 | 61 | 59
2017-10-19 06:00 | 50 | 47 |  |  | 43027.25 | 68 | 66
2017-10-19 06:30 | 53 | 50 |  |  | 43027.2708 | 74 | 72
2017-10-19 07:00 | 56 | 53 |  |  | 43027.2917 | 79 | 76
2017-10-19 07:30 | 60 | 59 |  |  | 43027.3125 | 85 | 83
2017-10-19 08:00 | 63 | 62 |  |  | 43027.3333 | 92 | 90
2017-10-19 08:30 | 67 | 65 |  |  | 43027.3542 | 98 | 95
2017-10-19 09:00 | 63 | 61 |  |  | 43027.375 | 91 | 87
2017-10-19 09:30 | 63 | 61 |  |  | 43027.3958 | 88 | 85
2017-10-19 10:00 | 60 | 57 |  |  | 43027.4167 | 86 | 82
2017-10-19 10:30 | 60 | 57 |  |  | 43027.4375 | 84 | 80
2017-10-19 11:00 | 63 | 61 |  |  | 43027.4583 | 92 | 89
2017-10-19 11:30 | 62 | 59 |  |  | 43027.4792 | 85 | 81
2017-10-19 12:00 | 61 | 58 |  |  | 43027.5 | 87 | 84
2017-10-19 12:30 | 63 | 60 |  |  | 43027.5208 | 88 | 85
2017-10-19 13:00 | 61 | 58 |  |  | 43027.5417 | 83 | 80
2017-10-19 13:30 | 62 | 59 |  |  | 43027.5625 | 81 | 78
2017-10-19 14:00 | 61 | 58 |  |  | 43027.5833 | 81 | 78
2017-10-19 14:30 | 60 | 58 |  |  | 43027.6042 | 80 | 77
2017-10-19 15:00 | 62 | 60 |  |  | 43027.625 | 85 | 82
2017-10-19 15:30 | 62 | 60 |  |  | 43027.6458 | 87 | 84
2017-10-19 16:00 | 62 | 59 |  |  | 43027.6667 | 84 | 81
2017-10-19 16:30 | 62 | 59 |  |  | 43027.6875 | 86 | 82
2017-10-19 17:00 | 63 | 60 |  |  | 43027.7083 | 86 | 82
2017-10-19 17:30 | 64 | 61 |  |  | 43027.7292 | 87 | 84
2017-10-19 18:00 | 62 | 60 |  |  | 43027.75 | 86 | 82
2017-10-19 18:30 | 65 | 62 |  |  | 43027.7708 | 88 | 83
2017-10-19 19:00 | 66 | 62 |  |  | 43027.7917 | 89 | 84
2017-10-19 19:30 | 65 | 61 |  |  | 43027.8125 | 86 | 81
2017-10-19 20:00 | 65 | 64 |  |  | 43027.8333 | 86 | 84
2017-10-19 20:30 | 68 | 66 |  |  | 43027.8542 | 89 | 87
2017-10-19 21:00 | 65 | 63 |  |  | 43027.875 | 84 | 82
2017-10-19 21:30 | 60 | 59 |  |  | 43027.8958 | 78 | 77
2017-10-19 22:00 | 59 | 57 |  |  | 43027.9167 | 78 | 77
2017-10-19 22:30 | 57 | 55 |  |  | 43027.9375 | 78 | 77
2017-10-19 23:00 | 60 | 58 |  |  | 43027.9583 | 81 | 80
2017-10-19 23:30 | 57 | 55 |  |  | 43027.9792 | 77 | 75
2017-10-20 | 51 | 48 |  |  | 43028 | 69 | 68
2017-10-20 00:30 | 48 | 44 |  |  | 43028.0208 | 64 | 62
2017-10-20 01:00 | 45 | 42 |  |  | 43028.0417 | 60 | 57
2017-10-20 01:30 | 43 | 40 |  |  | 43028.0625 | 56 | 54
2017-10-20 02:00 | 41 | 37 |  |  | 43028.0833 | 53 | 51
2017-10-20 02:30 | 42 | 38 |  |  | 43028.1042 | 54 | 51
2017-10-20 03:00 | 43 | 39 |  |  | 43028.125 | 56 | 53
2017-10-20 03:30 | 41 | 37 |  |  | 43028.1458 | 54 | 52
2017-10-20 04:00 | 39 | 35 |  |  | 43028.1667 | 51 | 48
2017-10-20 04:30 | 41 | 37 |  |  | 43028.1875 | 54 | 52
2017-10-20 05:00 | 44 | 41 |  |  | 43028.2083 | 59 | 56
2017-10-20 05:30 | 47 | 44 |  |  | 43028.2292 | 64 | 62
2017-10-20 06:00 | 54 | 52 |  |  | 43028.25 | 74 | 73
2017-10-20 06:30 | 59 | 58 |  |  | 43028.2708 | 83 | 82
2017-10-20 07:00 | 61 | 60 |  |  | 43028.2917 | 87 | 87
2017-10-20 07:30 | 64 | 63 |  |  | 43028.3125 | 92 | 91
2017-10-20 08:00 | 66 | 66 |  |  | 43028.3333 | 97 | 97
2017-10-20 08:30 | 69 | 68 |  |  | 43028.3542 | 102 | 101
2017-10-20 09:00 | 68 | 67 |  |  | 43028.375 | 99 | 99
2017-10-20 09:30 | 67 | 67 |  |  | 43028.3958 | 97 | 96
2017-10-20 10:00 | 68 | 67 |  |  | 43028.4167 | 96 | 96
2017-10-20 10:30 | 67 | 66 |  |  | 43028.4375 | 94 | 94
2017-10-20 11:00 | 69 | 69 |  |  | 43028.4583 | 95 | 94
2017-10-20 11:30 | 70 | 69 |  |  | 43028.4792 | 97 | 97
2017-10-20 12:00 | 70 | 69 |  |  | 43028.5 | 102 | 101
2017-10-20 12:30 | 69 | 68 |  |  | 43028.5208 | 98 | 98
2017-10-20 13:00 | 72 | 71 |  |  | 43028.5417 | 100 | 99
2017-10-20 13:30 | 70 | 69 |  |  | 43028.5625 | 97 | 97
2017-10-20 14:00 | 68 | 67 |  |  | 43028.5833 | 91 | 90
2017-10-20 14:30 | 67 | 66 |  |  | 43028.6042 | 93 | 93
2017-10-20 15:00 | 64 | 63 |  |  | 43028.625 | 89 | 89
2017-10-20 15:30 | 63 | 62 |  |  | 43028.6458 | 87 | 86
2017-10-20 16:00 | 66 | 65 |  |  | 43028.6667 | 89 | 89
2017-10-20 16:30 | 68 | 67 |  |  | 43028.6875 | 91 | 90
2017-10-20 17:00 | 70 | 68 |  |  | 43028.7083 | 93 | 92
2017-10-20 17:30 | 66 | 65 |  |  | 43028.7292 | 87 | 87
2017-10-20 18:00 | 63 | 62 |  |  | 43028.75 | 83 | 82
2017-10-20 18:30 | 61 | 60 |  |  | 43028.7708 | 80 | 79
2017-10-20 19:00 | 66 | 61 |  |  | 43028.7917 | 86 | 81
2017-10-20 19:30 | 68 | 59 |  |  | 43028.8125 | 88 | 79
2017-10-20 20:00 | 65 | 57 |  |  | 43028.8333 | 85 | 77
2017-10-20 20:30 | 60 | 56 |  |  | 43028.8542 | 79 | 73
2017-10-20 21:00 | 55 | 52 |  |  | 43028.875 | 73 | 71
2017-10-20 21:30 | 53 | 49 |  |  | 43028.8958 | 69 | 67
2017-10-20 22:00 | 54 | 50 |  |  | 43028.9167 | 71 | 69
2017-10-20 22:30 | 56 | 52 |  |  | 43028.9375 | 72 | 70
2017-10-20 23:00 | 56 | 51 |  |  | 43028.9583 | 71 | 68
2017-10-20 23:30 | 51 | 47 |  |  | 43028.9792 | 66 | 63
2017-10-21 | 47 | 42 |  |  | 43029 | 61 | 58
2017-10-21 00:30 | 43 | 37 |  |  | 43029.0208 | 55 | 53
2017-10-21 01:00 | 42 | 36 |  |  | 43029.0417 | 53 | 50
2017-10-21 01:30 | 41 | 34 |  |  | 43029.0625 | 50 | 47
2017-10-21 02:00 | 41 | 33 |  |  | 43029.0833 | 49 | 46
2017-10-21 02:30 | 40 | 32 |  |  | 43029.1042 | 49 | 45
2017-10-21 03:00 | 42 | 35 |  |  | 43029.125 | 52 | 48
2017-10-21 03:30 | 44 | 36 |  |  | 43029.1458 | 53 | 49
2017-10-21 04:00 | 44 | 35 |  |  | 43029.1667 | 53 | 48
2017-10-21 04:30 | 42 | 33 |  |  | 43029.1875 | 51 | 47
2017-10-21 05:00 | 41 | 33 |  |  | 43029.2083 | 51 | 46
2017-10-21 05:30 | 42 | 34 |  |  | 43029.2292 | 51 | 47
2017-10-21 06:00 | 43 | 35 |  |  | 43029.25 | 53 | 49
2017-10-21 06:30 | 44 | 37 |  |  | 43029.2708 | 54 | 51
2017-10-21 07:00 | 44 | 38 |  |  | 43029.2917 | 56 | 53
2017-10-21 07:30 | 44 | 39 |  |  | 43029.3125 | 58 | 55
2017-10-21 08:00 | 52 | 41 |  |  | 43029.3333 | 70 | 59
2017-10-21 08:30 | 58 | 46 |  |  | 43029.3542 | 77 | 65
2017-10-21 09:00 | 58 | 49 |  |  | 43029.375 | 79 | 70
2017-10-21 09:30 | 59 | 50 |  |  | 43029.3958 | 79 | 71
2017-10-21 10:00 | 62 | 55 |  |  | 43029.4167 | 83 | 76
2017-10-21 10:30 | 65 | 57 |  |  | 43029.4375 | 84 | 77
2017-10-21 11:00 | 64 | 55 |  |  | 43029.4583 | 85 | 75
2017-10-21 11:30 | 61 | 53 |  |  | 43029.4792 | 82 | 73
2017-10-21 12:00 | 60 | 51 |  |  | 43029.5 | 79 | 71
2017-10-21 12:30 | 61 | 52 |  |  | 43029.5208 | 80 | 72
2017-10-21 13:00 | 61 | 52 |  |  | 43029.5417 | 80 | 71
2017-10-21 13:30 | 62 | 53 |  |  | 43029.5625 | 80 | 72
2017-10-21 14:00 | 63 | 55 |  |  | 43029.5833 | 79 | 72
2017-10-21 14:30 | 61 | 53 |  |  | 43029.6042 | 78 | 71
2017-10-21 15:00 | 60 | 51 |  |  | 43029.625 | 76 | 69
2017-10-21 15:30 | 61 | 52 |  |  | 43029.6458 | 78 | 71
2017-10-21 16:00 | 61 | 52 |  |  | 43029.6667 | 78 | 71
2017-10-21 16:30 | 63 | 54 |  |  | 43029.6875 | 80 | 73
2017-10-21 17:00 | 63 | 54 |  |  | 43029.7083 | 81 | 74
2017-10-21 17:30 | 62 | 53 |  |  | 43029.7292 | 81 | 74
2017-10-21 18:00 | 62 | 53 |  |  | 43029.75 | 80 | 73
2017-10-21 18:30 | 63 | 54 |  |  | 43029.7708 | 83 | 74
2017-10-21 19:00 | 62 | 50 |  |  | 43029.7917 | 81 | 70
2017-10-21 19:30 | 60 | 50 |  |  | 43029.8125 | 79 | 70
2017-10-21 20:00 | 61 | 50 |  |  | 43029.8333 | 78 | 69
2017-10-21 20:30 | 60 | 50 |  |  | 43029.8542 | 77 | 69
2017-10-21 21:00 | 58 | 49 |  |  | 43029.875 | 75 | 67
2017-10-21 21:30 | 51 | 47 |  |  | 43029.8958 | 65 | 64
2017-10-21 22:00 | 51 | 47 |  |  | 43029.9167 | 66 | 65
2017-10-21 22:30 | 52 | 48 |  |  | 43029.9375 | 69 | 68
2017-10-21 23:00 | 53 | 48 |  |  | 43029.9583 | 67 | 66
2017-10-21 23:30 | 50 | 46 |  |  | 43029.9792 | 64 | 62
2017-10-22 | 47 | 42 |  |  | 43030 | 59 | 57
2017-10-22 00:30 | 45 | 40 |  |  | 43030.0208 | 57 | 55
2017-10-22 01:00 | 44 | 38 |  |  | 43030.0417 | 53 | 51
2017-10-22 01:30 | 40 | 34 |  |  | 43030.0625 | 49 | 46
2017-10-22 02:00 | 39 | 33 |  |  | 43030.0833 | 47 | 45
2017-10-22 02:30 | 38 | 32 |  |  | 43030.1042 | 46 | 45
2017-10-22 03:00 | 39 | 33 |  |  | 43030.125 | 47 | 45
2017-10-22 03:30 | 38 | 32 |  |  | 43030.1458 | 45 | 44
2017-10-22 04:00 | 39 | 32 |  |  | 43030.1667 | 47 | 45
2017-10-22 04:30 | 38 | 31 |  |  | 43030.1875 | 46 | 44
2017-10-22 05:00 | 39 | 32 |  |  | 43030.2083 | 47 | 45
2017-10-22 05:30 | 38 | 30 |  |  | 43030.2292 | 46 | 44
2017-10-22 06:00 | 38 | 30 |  |  | 43030.25 | 46 | 44
2017-10-22 06:30 | 38 | 30 |  |  | 43030.2708 | 46 | 44
2017-10-22 07:00 | 37 | 29 |  |  | 43030.2917 | 46 | 44
2017-10-22 07:30 | 36 | 28 |  |  | 43030.3125 | 46 | 45
2017-10-22 08:00 | 38 | 31 |  |  | 43030.3333 | 49 | 48
2017-10-22 08:30 | 39 | 34 |  |  | 43030.3542 | 51 | 50
2017-10-22 09:00 | 38 | 32 |  |  | 43030.375 | 49 | 47
2017-10-22 09:30 | 37 | 31 |  |  | 43030.3958 | 48 | 47
2017-10-22 10:00 | 37 | 32 |  |  | 43030.4167 | 49 | 48
2017-10-22 10:30 | 38 | 33 |  |  | 43030.4375 | 48 | 47
2017-10-22 11:00 | 41 | 36 |  |  | 43030.4583 | 50 | 49
2017-10-22 11:30 | 42 | 37 |  |  | 43030.4792 | 52 | 52
2017-10-22 12:00 | 44 | 39 |  |  | 43030.5 | 55 | 54
2017-10-22 12:30 | 42 | 38 |  |  | 43030.5208 | 54 | 53
2017-10-22 13:00 | 42 | 38 |  |  | 43030.5417 | 54 | 53
2017-10-22 13:30 | 44 | 40 |  |  | 43030.5625 | 55 | 54
2017-10-22 14:00 | 44 | 40 |  |  | 43030.5833 | 54 | 53
2017-10-22 14:30 | 46 | 42 |  |  | 43030.6042 | 55 | 54
2017-10-22 15:00 | 46 | 41 |  |  | 43030.625 | 57 | 55
2017-10-22 15:30 | 46 | 41 |  |  | 43030.6458 | 58 | 57
2017-10-22 16:00 | 46 | 41 |  |  | 43030.6667 | 58 | 56
2017-10-22 16:30 | 46 | 40 |  |  | 43030.6875 | 58 | 55
2017-10-22 17:00 | 45 | 40 |  |  | 43030.7083 | 58 | 56
2017-10-22 17:30 | 45 | 40 |  |  | 43030.7292 | 59 | 56
2017-10-22 18:00 | 46 | 41 |  |  | 43030.75 | 60 | 57
2017-10-22 18:30 | 50 | 44 |  |  | 43030.7708 | 66 | 62
2017-10-22 19:00 | 53 | 46 |  |  | 43030.7917 | 69 | 64
2017-10-22 19:30 | 53 | 46 |  |  | 43030.8125 | 68 | 64
2017-10-22 20:00 | 52 | 47 |  |  | 43030.8333 | 67 | 64
2017-10-22 20:30 | 51 | 46 |  |  | 43030.8542 | 67 | 64
2017-10-22 21:00 | 49 | 43 |  |  | 43030.875 | 64 | 61
2017-10-22 21:30 | 48 | 42 |  |  | 43030.8958 | 61 | 59
2017-10-22 22:00 | 47 | 41 |  |  | 43030.9167 | 61 | 58
2017-10-22 22:30 | 48 | 41 |  |  | 43030.9375 | 61 | 59
2017-10-22 23:00 | 48 | 41 |  |  | 43030.9583 | 60 | 57
2017-10-22 23:30 | 45 | 38 |  |  | 43030.9792 | 56 | 53
2017-10-23 | 43 | 34 |  |  | 43031 | 52 | 49
2017-10-23 00:30 | 42 | 32 |  |  | 43031.0208 | 49 | 45
2017-10-23 01:00 | 43 | 32 |  |  | 43031.0417 | 48 | 44
2017-10-23 01:30 | 41 | 30 |  |  | 43031.0625 | 47 | 42
2017-10-23 02:00 | 41 | 29 |  |  | 43031.0833 | 45 | 40
2017-10-23 02:30 | 40 | 29 |  |  | 43031.1042 | 44 | 39
2017-10-23 03:00 | 40 | 29 |  |  | 43031.125 | 45 | 39
2017-10-23 03:30 | 38 | 27 |  |  | 43031.1458 | 44 | 39
2017-10-23 04:00 | 41 | 31 |  |  | 43031.1667 | 47 | 43
2017-10-23 04:30 | 40 | 31 |  |  | 43031.1875 | 48 | 43
2017-10-23 05:00 | 41 | 33 |  |  | 43031.2083 | 49 | 45
2017-10-23 05:30 | 42 | 35 |  |  | 43031.2292 | 52 | 49
2017-10-23 06:00 | 50 | 45 |  |  | 43031.25 | 60 | 58
2017-10-23 06:30 | 56 | 53 |  |  | 43031.2708 | 70 | 68
2017-10-23 07:00 | 60 | 58 |  |  | 43031.2917 | 77 | 76
2017-10-23 07:30 | 61 | 59 |  |  | 43031.3125 | 85 | 85
2017-10-23 08:00 | 62 | 60 |  |  | 43031.3333 | 86 | 86
2017-10-23 08:30 | 64 | 63 |  |  | 43031.3542 | 87 | 86
2017-10-23 09:00 | 66 | 66 |  |  | 43031.375 | 85 | 85
2017-10-23 09:30 | 69 | 69 |  |  | 43031.3958 | 91 | 91
2017-10-23 10:00 | 69 | 69 |  |  | 43031.4167 | 89 | 89
2017-10-23 10:30 | 67 | 66 |  |  | 43031.4375 | 86 | 86
2017-10-23 11:00 | 67 | 66 |  |  | 43031.4583 | 89 | 89
2017-10-23 11:30 | 68 | 67 |  |  | 43031.4792 | 88 | 88
2017-10-23 12:00 | 69 | 68 |  |  | 43031.5 | 90 | 90
2017-10-23 12:30 | 64 | 63 |  |  | 43031.5208 | 93 | 93
2017-10-23 13:00 | 59 | 58 |  |  | 43031.5417 | 86 | 86
2017-10-23 13:30 | 62 | 60 |  |  | 43031.5625 | 88 | 88
2017-10-23 14:00 | 68 | 67 |  |  | 43031.5833 | 93 | 93
2017-10-23 14:30 | 69 | 68 |  |  | 43031.6042 | 96 | 96
2017-10-23 15:00 | 68 | 67 |  |  | 43031.625 | 92 | 92
2017-10-23 15:30 | 71 | 69 |  |  | 43031.6458 | 94 | 94
2017-10-23 16:00 | 69 | 68 |  |  | 43031.6667 | 92 | 92
2017-10-23 16:30 | 69 | 67 |  |  | 43031.6875 | 91 | 91
2017-10-23 17:00 | 68 | 66 |  |  | 43031.7083 | 90 | 89
2017-10-23 17:30 | 64 | 62 |  |  | 43031.7292 | 85 | 84
2017-10-23 18:00 | 60 | 58 |  |  | 43031.75 | 76 | 75
2017-10-23 18:30 | 60 | 58 |  |  | 43031.7708 | 76 | 74
2017-10-23 19:00 | 61 | 59 |  |  | 43031.7917 | 78 | 76
2017-10-23 19:30 | 60 | 57 |  |  | 43031.8125 | 77 | 75
2017-10-23 20:00 | 56 | 54 |  |  | 43031.8333 | 72 | 71
2017-10-23 20:30 | 54 | 53 |  |  | 43031.8542 | 69 | 68
2017-10-23 21:00 | 53 | 50 |  |  | 43031.875 | 67 | 66
2017-10-23 21:30 | 50 | 48 |  |  | 43031.8958 | 63 | 62
2017-10-23 22:00 | 49 | 46 |  |  | 43031.9167 | 62 | 61
2017-10-23 22:30 | 51 | 48 |  |  | 43031.9375 | 67 | 65
2017-10-23 23:00 | 53 | 49 |  |  | 43031.9583 | 68 | 66
2017-10-23 23:30 | 51 | 47 |  |  | 43031.9792 | 66 | 64
2017-10-24 | 48 | 44 |  |  | 43032 | 62 | 59
2017-10-24 00:30 | 44 | 39 |  |  | 43032.0208 | 55 | 52
2017-10-24 01:00 | 42 | 36 |  |  | 43032.0417 | 51 | 47
2017-10-24 01:30 | 42 | 34 |  |  | 43032.0625 | 50 | 46
2017-10-24 02:00 | 43 | 35 |  |  | 43032.0833 | 50 | 46
2017-10-24 02:30 | 43 | 35 |  |  | 43032.1042 | 51 | 46
2017-10-24 03:00 | 43 | 34 |  |  | 43032.125 | 50 | 46
2017-10-24 03:30 | 42 | 34 |  |  | 43032.1458 | 50 | 45
2017-10-24 04:00 | 42 | 34 |  |  | 43032.1667 | 50 | 45
2017-10-24 04:30 | 43 | 35 |  |  | 43032.1875 | 52 | 47
2017-10-24 05:00 | 44 | 37 |  |  | 43032.2083 | 53 | 50
2017-10-24 05:30 | 44 | 38 |  |  | 43032.2292 | 55 | 52
2017-10-24 06:00 | 54 | 49 |  |  | 43032.25 | 68 | 65
2017-10-24 06:30 | 60 | 56 |  |  | 43032.2708 | 77 | 76
2017-10-24 07:00 | 60 | 58 |  |  | 43032.2917 | 81 | 80
2017-10-24 07:30 | 61 | 59 |  |  | 43032.3125 | 85 | 84
2017-10-24 08:00 | 65 | 62 |  |  | 43032.3333 | 89 | 88
2017-10-24 08:30 | 81 | 79 |  |  | 43032.3542 | 125 | 124
2017-10-24 09:00 | 81 | 80 |  |  | 43032.375 | 124 | 124
2017-10-24 09:30 | 83 | 82 |  |  | 43032.3958 | 125 | 125
2017-10-24 10:00 | 83 | 81 |  |  | 43032.4167 | 123 | 123
2017-10-24 10:30 | 82 | 81 |  |  | 43032.4375 | 125 | 125
2017-10-24 11:00 | 83 | 82 |  |  | 43032.4583 | 127 | 127
2017-10-24 11:30 | 83 | 81 |  |  | 43032.4792 | 125 | 125
2017-10-24 12:00 | 83 | 82 |  |  | 43032.5 | 126 | 125
2017-10-24 12:30 | 82 | 80 |  |  | 43032.5208 | 126 | 125
2017-10-24 13:00 | 80 | 79 |  |  | 43032.5417 | 123 | 122
2017-10-24 13:30 | 83 | 82 |  |  | 43032.5625 | 127 | 127
2017-10-24 14:00 | 86 | 86 |  |  | 43032.5833 | 127 | 127
2017-10-24 14:30 | 87 | 86 |  |  | 43032.6042 | 126 | 126
2017-10-24 15:00 | 67 | 65 |  |  | 43032.625 | 89 | 88
2017-10-24 15:30 | 68 | 66 |  |  | 43032.6458 | 90 | 90
2017-10-24 16:00 | 69 | 68 |  |  | 43032.6667 | 93 | 92
2017-10-24 16:30 | 68 | 64 |  |  | 43032.6875 | 92 | 89
2017-10-24 17:00 | 70 | 65 |  |  | 43032.7083 | 94 | 90
2017-10-24 17:30 | 67 | 62 |  |  | 43032.7292 | 89 | 85
2017-10-24 18:00 | 65 | 61 |  |  | 43032.75 | 85 | 83
2017-10-24 18:30 | 65 | 61 |  |  | 43032.7708 | 84 | 82
2017-10-24 19:00 | 66 | 63 |  |  | 43032.7917 | 85 | 82
2017-10-24 19:30 | 62 | 59 |  |  | 43032.8125 | 79 | 77
2017-10-24 20:00 | 60 | 56 |  |  | 43032.8333 | 75 | 72
2017-10-24 20:30 | 58 | 55 |  |  | 43032.8542 | 73 | 71
2017-10-24 21:00 | 55 | 52 |  |  | 43032.875 | 69 | 67
2017-10-24 21:30 | 51 | 49 |  |  | 43032.8958 | 64 | 63
2017-10-24 22:00 | 50 | 48 |  |  | 43032.9167 | 63 | 63
2017-10-24 22:30 | 51 | 49 |  |  | 43032.9375 | 68 | 68
2017-10-24 23:00 | 56 | 52 |  |  | 43032.9583 | 73 | 72
2017-10-24 23:30 | 52 | 47 |  |  | 43032.9792 | 68 | 66
2017-10-25 | 49 | 43 |  |  | 43033 | 63 | 60
2017-10-25 00:30 | 45 | 39 |  |  | 43033.0208 | 56 | 54
2017-10-25 01:00 | 42 | 34 |  |  | 43033.0417 | 50 | 47
2017-10-25 01:30 | 42 | 33 |  |  | 43033.0625 | 50 | 47
2017-10-25 02:00 | 41 | 33 |  |  | 43033.0833 | 50 | 48
2017-10-25 02:30 | 41 | 33 |  |  | 43033.1042 | 51 | 49
2017-10-25 03:00 | 41 | 33 |  |  | 43033.125 | 48 | 46
2017-10-25 03:30 | 41 | 33 |  |  | 43033.1458 | 48 | 46
2017-10-25 04:00 | 40 | 32 |  |  | 43033.1667 | 47 | 44
2017-10-25 04:30 | 40 | 32 |  |  | 43033.1875 | 48 | 46
2017-10-25 05:00 | 43 | 36 |  |  | 43033.2083 | 53 | 51
2017-10-25 05:30 | 50 | 44 |  |  | 43033.2292 | 63 | 62
2017-10-25 06:00 | 54 | 49 |  |  | 43033.25 | 70 | 69
2017-10-25 06:30 | 55 | 52 |  |  | 43033.2708 | 74 | 73
2017-10-25 07:00 | 58 | 55 |  |  | 43033.2917 | 79 | 78
2017-10-25 07:30 | 60 | 59 |  |  | 43033.3125 | 84 | 84
2017-10-25 08:00 | 61 | 59 |  |  | 43033.3333 | 84 | 84
2017-10-25 08:30 | 61 | 60 |  |  | 43033.3542 | 86 | 86
2017-10-25 09:00 | 61 | 60 |  |  | 43033.375 | 85 | 85
2017-10-25 09:30 | 60 | 60 |  |  | 43033.3958 | 84 | 84
2017-10-25 10:00 | 60 | 59 |  |  | 43033.4167 | 84 | 84
2017-10-25 10:30 | 61 | 60 |  |  | 43033.4375 | 85 | 85
2017-10-25 11:00 | 62 | 61 |  |  | 43033.4583 | 87 | 87
2017-10-25 11:30 | 62 | 62 |  |  | 43033.4792 | 88 | 88
2017-10-25 12:00 | 61 | 61 |  |  | 43033.5 | 87 | 87
2017-10-25 12:30 | 61 | 61 |  |  | 43033.5208 | 86 | 86
2017-10-25 13:00 | 63 | 63 |  |  | 43033.5417 | 89 | 89
2017-10-25 13:30 | 66 | 66 |  |  | 43033.5625 | 93 | 93
2017-10-25 14:00 | 67 | 67 |  |  | 43033.5833 | 92 | 92
2017-10-25 14:30 | 69 | 69 |  |  | 43033.6042 | 95 | 95
2017-10-25 15:00 | 67 | 67 |  |  | 43033.625 | 94 | 94
2017-10-25 15:30 | 69 | 69 |  |  | 43033.6458 | 94 | 94
2017-10-25 16:00 | 69 | 69 |  |  | 43033.6667 | 96 | 96
2017-10-25 16:30 | 71 | 71 |  |  | 43033.6875 | 99 | 99
2017-10-25 17:00 | 70 | 70 |  |  | 43033.7083 | 97 | 97
2017-10-25 17:30 | 67 | 67 |  |  | 43033.7292 | 92 | 92
2017-10-25 18:00 | 66 | 66 |  |  | 43033.75 | 89 | 89
2017-10-25 18:30 | 65 | 65 |  |  | 43033.7708 | 88 | 87
2017-10-25 19:00 | 65 | 65 |  |  | 43033.7917 | 89 | 87
2017-10-25 19:30 | 62 | 62 |  |  | 43033.8125 | 84 | 82
2017-10-25 20:00 | 61 | 61 |  |  | 43033.8333 | 78 | 78
2017-10-25 20:30 | 59 | 58 |  |  | 43033.8542 | 74 | 74
2017-10-25 21:00 | 56 | 56 |  |  | 43033.875 | 71 | 71
2017-10-25 21:30 | 52 | 50 |  |  | 43033.8958 | 67 | 67
2017-10-25 22:00 | 52 | 51 |  |  | 43033.9167 | 68 | 67
2017-10-25 22:30 | 53 | 52 |  |  | 43033.9375 | 72 | 72
2017-10-25 23:00 | 54 | 54 |  |  | 43033.9583 | 76 | 76
2017-10-25 23:30 | 50 | 50 |  |  | 43033.9792 | 70 | 70
2017-10-26 | 46 | 46 |  |  | 43034 | 65 | 65
2017-10-26 00:30 | 42 | 42 |  |  | 43034.0208 | 57 | 57
2017-10-26 01:00 | 38 | 37 |  |  | 43034.0417 | 51 | 51
2017-10-26 01:30 | 36 | 36 |  |  | 43034.0625 | 50 | 50
2017-10-26 02:00 | 36 | 36 |  |  | 43034.0833 | 49 | 49
2017-10-26 02:30 | 35 | 34 |  |  | 43034.1042 | 49 | 48
2017-10-26 03:00 | 34 | 34 |  |  | 43034.125 | 48 | 48
2017-10-26 03:30 | 34 | 34 |  |  | 43034.1458 | 48 | 48
2017-10-26 04:00 | 36 | 35 |  |  | 43034.1667 | 49 | 49
2017-10-26 04:30 | 37 | 37 |  |  | 43034.1875 | 51 | 51
2017-10-26 05:00 | 39 | 39 |  |  | 43034.2083 | 53 | 53
2017-10-26 05:30 | 40 | 40 |  |  | 43034.2292 | 56 | 56
2017-10-26 06:00 | 43 | 43 |  |  | 43034.25 | 59 | 59
2017-10-26 06:30 | 46 | 46 |  |  | 43034.2708 | 64 | 64
2017-10-26 07:00 | 50 | 50 |  |  | 43034.2917 | 70 | 70
2017-10-26 07:30 | 53 | 52 |  |  | 43034.3125 | 75 | 74
2017-10-26 08:00 | 57 | 55 |  |  | 43034.3333 | 80 | 79
2017-10-26 08:30 | 59 | 58 |  |  | 43034.3542 | 86 | 85
2017-10-26 09:00 | 60 | 58 |  |  | 43034.375 | 85 | 84
2017-10-26 09:30 | 59 | 57 |  |  | 43034.3958 | 84 | 82
2017-10-26 10:00 | 59 | 57 |  |  | 43034.4167 | 84 | 83
2017-10-26 10:30 | 61 | 59 |  |  | 43034.4375 | 85 | 83
2017-10-26 11:00 | 60 | 58 |  |  | 43034.4583 | 84 | 83
2017-10-26 11:30 | 62 | 61 |  |  | 43034.4792 | 87 | 86
2017-10-26 12:00 | 63 | 61 |  |  | 43034.5 | 88 | 87
2017-10-26 12:30 | 64 | 63 |  |  | 43034.5208 | 89 | 88
2017-10-26 13:00 | 64 | 63 |  |  | 43034.5417 | 88 | 88
2017-10-26 13:30 | 63 | 63 |  |  | 43034.5625 | 86 | 86
2017-10-26 14:00 | 65 | 64 |  |  | 43034.5833 | 88 | 88
2017-10-26 14:30 | 68 | 68 |  |  | 43034.6042 | 88 | 88
2017-10-26 15:00 | 71 | 70 |  |  | 43034.625 | 92 | 92
2017-10-26 15:30 | 67 | 66 |  |  | 43034.6458 | 93 | 92
2017-10-26 16:00 | 68 | 67 |  |  | 43034.6667 | 92 | 92
2017-10-26 16:30 | 70 | 69 |  |  | 43034.6875 | 95 | 95
2017-10-26 17:00 | 72 | 72 |  |  | 43034.7083 | 96 | 96
2017-10-26 17:30 | 72 | 72 |  |  | 43034.7292 | 95 | 95
2017-10-26 18:00 | 73 | 73 |  |  | 43034.75 | 96 | 96
2017-10-26 18:30 | 73 | 73 |  |  | 43034.7708 | 94 | 94
2017-10-26 19:00 | 72 | 72 |  |  | 43034.7917 | 95 | 95
2017-10-26 19:30 | 69 | 69 |  |  | 43034.8125 | 91 | 91
2017-10-26 20:00 | 65 | 65 |  |  | 43034.8333 | 85 | 85
2017-10-26 20:30 | 62 | 62 |  |  | 43034.8542 | 81 | 81
2017-10-26 21:00 | 60 | 60 |  |  | 43034.875 | 78 | 78
2017-10-26 21:30 | 54 | 53 |  |  | 43034.8958 | 69 | 69
2017-10-26 22:00 | 54 | 53 |  |  | 43034.9167 | 71 | 71
2017-10-26 22:30 | 56 | 55 |  |  | 43034.9375 | 77 | 77
2017-10-26 23:00 | 58 | 58 |  |  | 43034.9583 | 79 | 79
2017-10-26 23:30 | 56 | 56 |  |  | 43034.9792 | 77 | 77
2017-10-27 | 51 | 51 |  |  | 43035 | 71 | 70
2017-10-27 00:30 | 44 | 44 |  |  | 43035.0208 | 63 | 62
2017-10-27 01:00 | 42 | 41 |  |  | 43035.0417 | 58 | 56
2017-10-27 01:30 | 42 | 41 |  |  | 43035.0625 | 59 | 57
2017-10-27 02:00 | 43 | 42 |  |  | 43035.0833 | 60 | 58
2017-10-27 02:30 | 42 | 41 |  |  | 43035.1042 | 60 | 58
2017-10-27 03:00 | 41 | 40 |  |  | 43035.125 | 58 | 57
2017-10-27 03:30 | 41 | 40 |  |  | 43035.1458 | 58 | 56
2017-10-27 04:00 | 40 | 39 |  |  | 43035.1667 | 57 | 55
2017-10-27 04:30 | 41 | 39 |  |  | 43035.1875 | 58 | 56
2017-10-27 05:00 | 42 | 41 |  |  | 43035.2083 | 59 | 57
2017-10-27 05:30 | 43 | 42 |  |  | 43035.2292 | 60 | 59
2017-10-27 06:00 | 50 | 49 |  |  | 43035.25 | 69 | 68
2017-10-27 06:30 | 56 | 55 |  |  | 43035.2708 | 76 | 76
2017-10-27 07:00 | 59 | 58 |  |  | 43035.2917 | 82 | 81
2017-10-27 07:30 | 62 | 62 |  |  | 43035.3125 | 88 | 88
2017-10-27 08:00 | 63 | 63 |  |  | 43035.3333 | 91 | 91
2017-10-27 08:30 | 64 | 64 |  |  | 43035.3542 | 92 | 92
2017-10-27 09:00 | 63 | 63 |  |  | 43035.375 | 91 | 91
2017-10-27 09:30 | 63 | 63 |  |  | 43035.3958 | 89 | 89
2017-10-27 10:00 | 62 | 62 |  |  | 43035.4167 | 87 | 87
2017-10-27 10:30 | 61 | 61 |  |  | 43035.4375 | 85 | 85
2017-10-27 11:00 | 63 | 62 |  |  | 43035.4583 | 87 | 87
2017-10-27 11:30 | 63 | 62 |  |  | 43035.4792 | 88 | 88
2017-10-27 12:00 | 63 | 63 |  |  | 43035.5 | 91 | 90
2017-10-27 12:30 | 64 | 64 |  |  | 43035.5208 | 92 | 92
2017-10-27 13:00 | 65 | 65 |  |  | 43035.5417 | 93 | 93
2017-10-27 13:30 | 65 | 65 |  |  | 43035.5625 | 93 | 93
2017-10-27 14:00 | 66 | 65 |  |  | 43035.5833 | 94 | 94
2017-10-27 14:30 | 66 | 66 |  |  | 43035.6042 | 93 | 93
2017-10-27 15:00 | 67 | 66 |  |  | 43035.625 | 93 | 93
2017-10-27 15:30 | 68 | 68 |  |  | 43035.6458 | 94 | 94
2017-10-27 16:00 | 69 | 69 |  |  | 43035.6667 | 95 | 95
2017-10-27 16:30 | 69 | 68 |  |  | 43035.6875 | 94 | 94
2017-10-27 17:00 | 72 | 70 |  |  | 43035.7083 | 97 | 97
2017-10-27 17:30 | 72 | 71 |  |  | 43035.7292 | 97 | 97
2017-10-27 18:00 | 68 | 67 |  |  | 43035.75 | 93 | 92
2017-10-27 18:30 | 64 | 62 |  |  | 43035.7708 | 87 | 86
2017-10-27 19:00 | 66 | 65 |  |  | 43035.7917 | 91 | 90
2017-10-27 19:30 | 65 | 64 |  |  | 43035.8125 | 89 | 89
2017-10-27 20:00 | 63 | 62 |  |  | 43035.8333 | 86 | 85
2017-10-27 20:30 | 62 | 61 |  |  | 43035.8542 | 84 | 84
2017-10-27 21:00 | 56 | 55 |  |  | 43035.875 | 77 | 77
2017-10-27 21:30 | 54 | 53 |  |  | 43035.8958 | 72 | 71
2017-10-27 22:00 | 52 | 50 |  |  | 43035.9167 | 69 | 68
2017-10-27 22:30 | 51 | 49 |  |  | 43035.9375 | 67 | 65
2017-10-27 23:00 | 52 | 50 |  |  | 43035.9583 | 68 | 67
2017-10-27 23:30 | 48 | 46 |  |  | 43035.9792 | 62 | 61
2017-10-28 | 43 | 41 |  |  | 43036 | 56 | 55
2017-10-28 00:30 | 41 | 38 |  |  | 43036.0208 | 52 | 51
2017-10-28 01:00 | 40 | 36 |  |  | 43036.0417 | 48 | 46
2017-10-28 01:30 | 37 | 33 |  |  | 43036.0625 | 46 | 44
2017-10-28 02:00 | 37 | 33 |  |  | 43036.0833 | 46 | 44
2017-10-28 02:30 | 37 | 33 |  |  | 43036.1042 | 45 | 44
2017-10-28 03:00 | 36 | 32 |  |  | 43036.125 | 44 | 42
2017-10-28 03:30 | 35 | 31 |  |  | 43036.1458 | 43 | 42
2017-10-28 04:00 | 36 | 32 |  |  | 43036.1667 | 44 | 43
2017-10-28 04:30 | 35 | 30 |  |  | 43036.1875 | 42 | 40
2017-10-28 05:00 | 37 | 33 |  |  | 43036.2083 | 46 | 44
2017-10-28 05:30 | 35 | 30 |  |  | 43036.2292 | 42 | 41
2017-10-28 06:00 | 37 | 33 |  |  | 43036.25 | 47 | 45
2017-10-28 06:30 | 41 | 38 |  |  | 43036.2708 | 53 | 52
2017-10-28 07:00 | 42 | 39 |  |  | 43036.2917 | 55 | 54
2017-10-28 07:30 | 44 | 42 |  |  | 43036.3125 | 58 | 57
2017-10-28 08:00 | 46 | 44 |  |  | 43036.3333 | 61 | 60
2017-10-28 08:30 | 48 | 46 |  |  | 43036.3542 | 64 | 64
2017-10-28 09:00 | 48 | 47 |  |  | 43036.375 | 64 | 64
2017-10-28 09:30 | 48 | 47 |  |  | 43036.3958 | 64 | 64
2017-10-28 10:00 | 49 | 48 |  |  | 43036.4167 | 64 | 64
2017-10-28 10:30 | 50 | 49 |  |  | 43036.4375 | 65 | 65
2017-10-28 11:00 | 50 | 49 |  |  | 43036.4583 | 65 | 65
2017-10-28 11:30 | 50 | 49 |  |  | 43036.4792 | 65 | 65
2017-10-28 12:00 | 48 | 47 |  |  | 43036.5 | 64 | 64
2017-10-28 12:30 | 52 | 51 |  |  | 43036.5208 | 66 | 66
2017-10-28 13:00 | 49 | 48 |  |  | 43036.5417 | 64 | 64
2017-10-28 13:30 | 51 | 50 |  |  | 43036.5625 | 65 | 65
2017-10-28 14:00 | 52 | 51 |  |  | 43036.5833 | 63 | 63
2017-10-28 14:30 | 51 | 50 |  |  | 43036.6042 | 60 | 60
2017-10-28 15:00 | 50 | 49 |  |  | 43036.625 | 61 | 61
2017-10-28 15:30 | 51 | 49 |  |  | 43036.6458 | 64 | 64
2017-10-28 16:00 | 51 | 50 |  |  | 43036.6667 | 64 | 64
2017-10-28 16:30 | 50 | 49 |  |  | 43036.6875 | 64 | 64
2017-10-28 17:00 | 50 | 49 |  |  | 43036.7083 | 65 | 65
2017-10-28 17:30 | 49 | 48 |  |  | 43036.7292 | 66 | 65
2017-10-28 18:00 | 49 | 47 |  |  | 43036.75 | 65 | 65
2017-10-28 18:30 | 50 | 48 |  |  | 43036.7708 | 67 | 67
2017-10-28 19:00 | 53 | 51 |  |  | 43036.7917 | 71 | 70
2017-10-28 19:30 | 52 | 50 |  |  | 43036.8125 | 69 | 68
2017-10-28 20:00 | 51 | 49 |  |  | 43036.8333 | 67 | 66
2017-10-28 20:30 | 51 | 49 |  |  | 43036.8542 | 66 | 66
2017-10-28 21:00 | 48 | 47 |  |  | 43036.875 | 63 | 63
2017-10-28 21:30 | 48 | 47 |  |  | 43036.8958 | 62 | 62
2017-10-28 22:00 | 49 | 47 |  |  | 43036.9167 | 62 | 62
2017-10-28 22:30 | 48 | 47 |  |  | 43036.9375 | 64 | 63
2017-10-28 23:00 | 49 | 47 |  |  | 43036.9583 | 65 | 64
2017-10-28 23:30 | 45 | 42 |  |  | 43036.9792 | 58 | 57
2017-10-29 | 42 | 39 |  |  | 43037 | 54 | 53
2017-10-29 00:30 | 39 | 36 |  |  | 43037.0208 | 49 | 48
2017-10-29 01:00 | 37 | 34 |  |  | 43037.0417 | 47 | 46
2017-10-29 01:30 | 39 | 35 |  |  | 43037.0625 | 47 | 46
2017-10-29 02:00 | 38 | 35 |  |  | 43037.0833 | 48 | 47
2017-10-29 02:30 | 38 | 35 |  |  | 43037.1042 | 47 | 46
2017-10-29 03:00 | 37 | 33 |  |  | 43037.125 | 46 | 44
2017-10-29 03:30 | 37 | 33 |  |  | 43037.1458 | 44 | 43
2017-10-29 04:00 | 37 | 33 |  |  | 43037.1667 | 46 | 44
2017-10-29 04:30 | 38 | 34 |  |  | 43037.1875 | 48 | 47
2017-10-29 05:00 | 39 | 35 |  |  | 43037.2083 | 48 | 47
2017-10-29 05:30 | 38 | 33 |  |  | 43037.2292 | 47 | 45
2017-10-29 06:00 | 36 | 31 |  |  | 43037.25 | 47 | 45
2017-10-29 06:30 | 40 | 36 |  |  | 43037.2708 | 52 | 50
2017-10-29 07:00 | 40 | 36 |  |  | 43037.2917 | 52 | 50
2017-10-29 07:30 | 40 | 36 |  |  | 43037.3125 | 53 | 52
2017-10-29 08:00 | 41 | 38 |  |  | 43037.3333 | 55 | 54
2017-10-29 08:30 | 44 | 41 |  |  | 43037.3542 | 60 | 59
2017-10-29 09:00 | 46 | 44 |  |  | 43037.375 | 62 | 62
2017-10-29 09:30 | 48 | 46 |  |  | 43037.3958 | 63 | 63
2017-10-29 10:00 | 48 | 47 |  |  | 43037.4167 | 64 | 63
2017-10-29 10:30 | 48 | 47 |  |  | 43037.4375 | 63 | 63
2017-10-29 11:00 | 49 | 48 |  |  | 43037.4583 | 64 | 64
2017-10-29 11:30 | 50 | 48 |  |  | 43037.4792 | 63 | 63
2017-10-29 12:00 | 51 | 49 |  |  | 43037.5 | 64 | 64
2017-10-29 12:30 | 52 | 51 |  |  | 43037.5208 | 64 | 64
2017-10-29 13:00 | 53 | 52 |  |  | 43037.5417 | 66 | 66
2017-10-29 13:30 | 54 | 53 |  |  | 43037.5625 | 68 | 67
2017-10-29 14:00 | 55 | 54 |  |  | 43037.5833 | 66 | 65
2017-10-29 14:30 | 57 | 55 |  |  | 43037.6042 | 67 | 66
2017-10-29 15:00 | 57 | 55 |  |  | 43037.625 | 68 | 67
2017-10-29 15:30 | 58 | 56 |  |  | 43037.6458 | 70 | 69
2017-10-29 16:00 | 59 | 59 |  |  | 43037.6667 | 73 | 73
2017-10-29 16:30 | 64 | 64 |  |  | 43037.6875 | 79 | 79
2017-10-29 17:00 | 66 | 66 |  |  | 43037.7083 | 82 | 82
2017-10-29 17:30 | 65 | 65 |  |  | 43037.7292 | 81 | 81
2017-10-29 18:00 | 66 | 65 |  |  | 43037.75 | 81 | 81
2017-10-29 18:30 | 68 | 67 |  |  | 43037.7708 | 83 | 83
2017-10-29 19:00 | 69 | 69 |  |  | 43037.7917 | 88 | 88
2017-10-29 19:30 | 69 | 69 |  |  | 43037.8125 | 85 | 85
2017-10-29 20:00 | 63 | 63 |  |  | 43037.8333 | 79 | 79
2017-10-29 20:30 | 61 | 60 |  |  | 43037.8542 | 78 | 78
2017-10-29 21:00 | 57 | 56 |  |  | 43037.875 | 74 | 74
2017-10-29 21:30 | 55 | 53 |  |  | 43037.8958 | 71 | 70
2017-10-29 22:00 | 55 | 52 |  |  | 43037.9167 | 71 | 71
2017-10-29 22:30 | 56 | 54 |  |  | 43037.9375 | 72 | 71
2017-10-29 23:00 | 54 | 51 |  |  | 43037.9583 | 68 | 67
2017-10-29 23:30 | 51 | 48 |  |  | 43037.9792 | 64 | 63
2017-10-30 | 46 | 43 |  |  | 43038 | 59 | 58
2017-10-30 00:30 | 44 | 41 |  |  | 43038.0208 | 56 | 56
2017-10-30 01:00 | 41 | 38 |  |  | 43038.0417 | 52 | 52
2017-10-30 01:30 | 39 | 36 |  |  | 43038.0625 | 50 | 49
2017-10-30 02:00 | 39 | 36 |  |  | 43038.0833 | 49 | 48
2017-10-30 02:30 | 39 | 36 |  |  | 43038.1042 | 50 | 48
2017-10-30 03:00 | 37 | 33 |  |  | 43038.125 | 49 | 47
2017-10-30 03:30 | 38 | 34 |  |  | 43038.1458 | 48 | 47
2017-10-30 04:00 | 38 | 34 |  |  | 43038.1667 | 47 | 46
2017-10-30 04:30 | 38 | 35 |  |  | 43038.1875 | 48 | 47
2017-10-30 05:00 | 40 | 37 |  |  | 43038.2083 | 50 | 49
2017-10-30 05:30 | 40 | 38 |  |  | 43038.2292 | 52 | 52
2017-10-30 06:00 | 42 | 41 |  |  | 43038.25 | 56 | 56
2017-10-30 06:30 | 51 | 51 |  |  | 43038.2708 | 70 | 70
2017-10-30 07:00 | 57 | 57 |  |  | 43038.2917 | 79 | 79
2017-10-30 07:30 | 61 | 61 |  |  | 43038.3125 | 86 | 85
2017-10-30 08:00 | 61 | 60 |  |  | 43038.3333 | 86 | 86
2017-10-30 08:30 | 63 | 63 |  |  | 43038.3542 | 89 | 89
2017-10-30 09:00 | 66 | 66 |  |  | 43038.375 | 92 | 92
2017-10-30 09:30 | 71 | 71 |  |  | 43038.3958 | 99 | 99
2017-10-30 10:00 | 77 | 77 |  |  | 43038.4167 | 102 | 102
2017-10-30 10:30 | 75 | 75 |  |  | 43038.4375 | 101 | 101
2017-10-30 11:00 | 72 | 72 |  |  | 43038.4583 | 101 | 101
2017-10-30 11:30 | 79 | 79 |  |  | 43038.4792 | 105 | 105
2017-10-30 12:00 | 79 | 79 |  |  | 43038.5 | 108 | 108
2017-10-30 12:30 | 77 | 77 |  |  | 43038.5208 | 105 | 105
2017-10-30 13:00 | 82 | 82 |  |  | 43038.5417 | 109 | 109
2017-10-30 13:30 | 85 | 84 |  |  | 43038.5625 | 110 | 110
2017-10-30 14:00 | 84 | 84 |  |  | 43038.5833 | 110 | 110
2017-10-30 14:30 | 92 | 89 |  |  | 43038.6042 | 116 | 115
2017-10-30 15:00 | 100 | 97 |  |  | 43038.625 | 124 | 123
2017-10-30 15:30 | 105 | 101 |  |  | 43038.6458 | 124 | 123
2017-10-30 16:00 | 100 | 95 |  |  | 43038.6667 | 122 | 121
2017-10-30 16:30 | 95 | 91 |  |  | 43038.6875 | 112 | 111
2017-10-30 17:00 | 91 | 87 |  |  | 43038.7083 | 113 | 112
2017-10-30 17:30 | 84 | 82 |  |  | 43038.7292 | 107 | 106
2017-10-30 18:00 | 79 | 78 |  |  | 43038.75 | 102 | 101
2017-10-30 18:30 | 76 | 75 |  |  | 43038.7708 | 98 | 97
2017-10-30 19:00 | 76 | 76 |  |  | 43038.7917 | 100 | 99
2017-10-30 19:30 | 73 | 73 |  |  | 43038.8125 | 97 | 96
2017-10-30 20:00 | 72 | 72 |  |  | 43038.8333 | 94 | 94
2017-10-30 20:30 | 71 | 71 |  |  | 43038.8542 | 92 | 92
2017-10-30 21:00 | 66 | 66 |  |  | 43038.875 | 87 | 86
2017-10-30 21:30 | 63 | 63 |  |  | 43038.8958 | 81 | 81
2017-10-30 22:00 | 65 | 65 |  |  | 43038.9167 | 82 | 82
2017-10-30 22:30 | 64 | 64 |  |  | 43038.9375 | 81 | 81
2017-10-30 23:00 | 61 | 61 |  |  | 43038.9583 | 77 | 77
2017-10-30 23:30 | 56 | 56 |  |  | 43038.9792 | 70 | 70
2017-10-31 | 52 | 51 |  |  | 43039 | 65 | 65
2017-10-31 00:30 | 49 | 48 |  |  | 43039.0208 | 60 | 60
2017-10-31 01:00 | 43 | 42 |  |  | 43039.0417 | 53 | 53
2017-10-31 01:30 | 44 | 42 |  |  | 43039.0625 | 52 | 52
2017-10-31 02:00 | 43 | 42 |  |  | 43039.0833 | 52 | 52
2017-10-31 02:30 | 43 | 41 |  |  | 43039.1042 | 53 | 53
2017-10-31 03:00 | 41 | 39 |  |  | 43039.125 | 50 | 50
2017-10-31 03:30 | 39 | 37 |  |  | 43039.1458 | 48 | 48
2017-10-31 04:00 | 39 | 36 |  |  | 43039.1667 | 48 | 48
2017-10-31 04:30 | 40 | 37 |  |  | 43039.1875 | 49 | 48
2017-10-31 05:00 | 43 | 41 |  |  | 43039.2083 | 52 | 52
2017-10-31 05:30 | 44 | 41 |  |  | 43039.2292 | 56 | 55
2017-10-31 06:00 | 46 | 45 |  |  | 43039.25 | 59 | 59
2017-10-31 06:30 | 54 | 54 |  |  | 43039.2708 | 69 | 69
2017-10-31 07:00 | 60 | 60 |  |  | 43039.2917 | 80 | 80
2017-10-31 07:30 | 61 | 60 |  |  | 43039.3125 | 83 | 83
2017-10-31 08:00 | 61 | 61 |  |  | 43039.3333 | 82 | 82
2017-10-31 08:30 | 65 | 65 |  |  | 43039.3542 | 87 | 87
2017-10-31 09:00 | 65 | 65 |  |  | 43039.375 | 89 | 89
2017-10-31 09:30 | 64 | 63 |  |  | 43039.3958 | 86 | 86
2017-10-31 10:00 | 65 | 64 |  |  | 43039.4167 | 86 | 86
2017-10-31 10:30 | 65 | 65 |  |  | 43039.4375 | 87 | 87
2017-10-31 11:00 | 65 | 65 |  |  | 43039.4583 | 86 | 86
2017-10-31 11:30 | 66 | 66 |  |  | 43039.4792 | 87 | 87
2017-10-31 12:00 | 67 | 66 |  |  | 43039.5 | 89 | 89
2017-10-31 12:30 | 71 | 70 |  |  | 43039.5208 | 92 | 92
2017-10-31 13:00 | 69 | 68 |  |  | 43039.5417 | 90 | 90
2017-10-31 13:30 | 70 | 70 |  |  | 43039.5625 | 93 | 92
2017-10-31 14:00 | 72 | 71 |  |  | 43039.5833 | 93 | 93
2017-10-31 14:30 | 72 | 72 |  |  | 43039.6042 | 94 | 94
2017-10-31 15:00 | 73 | 73 |  |  | 43039.625 | 94 | 94
2017-10-31 15:30 | 71 | 71 |  |  | 43039.6458 | 93 | 93
2017-10-31 16:00 | 76 | 76 |  |  | 43039.6667 | 98 | 98
2017-10-31 16:30 | 78 | 78 |  |  | 43039.6875 | 99 | 98
2017-10-31 17:00 | 79 | 78 |  |  | 43039.7083 | 99 | 99
2017-10-31 17:30 | 75 | 74 |  |  | 43039.7292 | 94 | 93
2017-10-31 18:00 | 70 | 69 |  |  | 43039.75 | 88 | 87
2017-10-31 18:30 | 68 | 67 |  |  | 43039.7708 | 85 | 84
2017-10-31 19:00 | 71 | 70 |  |  | 43039.7917 | 88 | 88
2017-10-31 19:30 | 69 | 68 |  |  | 43039.8125 | 85 | 85
2017-10-31 20:00 | 66 | 66 |  |  | 43039.8333 | 84 | 83
2017-10-31 20:30 | 66 | 66 |  |  | 43039.8542 | 83 | 83
2017-10-31 21:00 | 63 | 62 |  |  | 43039.875 | 77 | 77
2017-10-31 21:30 | 57 | 57 |  |  | 43039.8958 | 71 | 71
2017-10-31 22:00 | 53 | 53 |  |  | 43039.9167 | 67 | 67
2017-10-31 22:30 | 53 | 52 |  |  | 43039.9375 | 66 | 66
2017-10-31 23:00 | 52 | 50 |  |  | 43039.9583 | 64 | 63
2017-10-31 23:30 | 49 | 47 |  |  | 43039.9792 | 61 | 60
2017-11-01 | 44 | 42 |  |  | 43040 | 55 | 55
2017-11-01 00:30 | 39 | 37 |  |  | 43040.0208 | 48 | 48
2017-11-01 01:00 | 35 | 33 |  |  | 43040.0417 | 45 | 44
2017-11-01 01:30 | 34 | 30 |  |  | 43040.0625 | 42 | 42
2017-11-01 02:00 | 33 | 30 |  |  | 43040.0833 | 43 | 43
2017-11-01 02:30 | 33 | 30 |  |  | 43040.1042 | 42 | 42
2017-11-01 03:00 | 33 | 30 |  |  | 43040.125 | 42 | 42
2017-11-01 03:30 | 32 | 29 |  |  | 43040.1458 | 41 | 41
2017-11-01 04:00 | 30 | 26 |  |  | 43040.1667 | 38 | 37
2017-11-01 04:30 | 31 | 27 |  |  | 43040.1875 | 40 | 39
2017-11-01 05:00 | 34 | 31 |  |  | 43040.2083 | 45 | 44
2017-11-01 05:30 | 37 | 34 |  |  | 43040.2292 | 48 | 48
2017-11-01 06:00 | 42 | 40 |  |  | 43040.25 | 56 | 55
2017-11-01 06:30 | 46 | 45 |  |  | 43040.2708 | 63 | 63
2017-11-01 07:00 | 51 | 50 |  |  | 43040.2917 | 71 | 71
2017-11-01 07:30 | 56 | 55 |  |  | 43040.3125 | 78 | 78
2017-11-01 08:00 | 55 | 55 |  |  | 43040.3333 | 78 | 78
2017-11-01 08:30 | 57 | 57 |  |  | 43040.3542 | 84 | 84
2017-11-01 09:00 | 60 | 60 |  |  | 43040.375 | 88 | 87
2017-11-01 09:30 | 60 | 60 |  |  | 43040.3958 | 86 | 86
2017-11-01 10:00 | 60 | 60 |  |  | 43040.4167 | 86 | 86
2017-11-01 10:30 | 60 | 60 |  |  | 43040.4375 | 87 | 87
2017-11-01 11:00 | 61 | 61 |  |  | 43040.4583 | 87 | 87
2017-11-01 11:30 | 59 | 59 |  |  | 43040.4792 | 85 | 85
2017-11-01 12:00 | 62 | 62 |  |  | 43040.5 | 86 | 86
2017-11-01 12:30 | 64 | 64 |  |  | 43040.5208 | 89 | 89
2017-11-01 13:00 | 64 | 64 |  |  | 43040.5417 | 89 | 89
2017-11-01 13:30 | 65 | 65 |  |  | 43040.5625 | 89 | 88
2017-11-01 14:00 | 65 | 65 |  |  | 43040.5833 | 90 | 90
2017-11-01 14:30 | 66 | 66 |  |  | 43040.6042 | 91 | 90
2017-11-01 15:00 | 65 | 65 |  |  | 43040.625 | 90 | 90
2017-11-01 15:30 | 65 | 65 |  |  | 43040.6458 | 90 | 90
2017-11-01 16:00 | 67 | 67 |  |  | 43040.6667 | 92 | 92
2017-11-01 16:30 | 69 | 69 |  |  | 43040.6875 | 94 | 94
2017-11-01 17:00 | 71 | 71 |  |  | 43040.7083 | 95 | 95
2017-11-01 17:30 | 70 | 70 |  |  | 43040.7292 | 92 | 91
2017-11-01 18:00 | 68 | 68 |  |  | 43040.75 | 87 | 87
2017-11-01 18:30 | 66 | 66 |  |  | 43040.7708 | 86 | 84
2017-11-01 19:00 | 71 | 71 |  |  | 43040.7917 | 89 | 88
2017-11-01 19:30 | 71 | 71 |  |  | 43040.8125 | 88 | 87
2017-11-01 20:00 | 69 | 69 |  |  | 43040.8333 | 86 | 85
2017-11-01 20:30 | 66 | 66 |  |  | 43040.8542 | 83 | 82
2017-11-01 21:00 | 62 | 62 |  |  | 43040.875 | 76 | 76
2017-11-01 21:30 | 55 | 55 |  |  | 43040.8958 | 70 | 69
2017-11-01 22:00 | 52 | 52 |  |  | 43040.9167 | 67 | 67
2017-11-01 22:30 | 54 | 53 |  |  | 43040.9375 | 67 | 67
2017-11-01 23:00 | 54 | 53 |  |  | 43040.9583 | 67 | 67
2017-11-01 23:30 | 51 | 49 |  |  | 43040.9792 | 63 | 62
2017-11-02 | 47 | 44 |  |  | 43041 | 57 | 57
2017-11-02 00:30 | 41 | 39 |  |  | 43041.0208 | 51 | 50
2017-11-02 01:00 | 35 | 32 |  |  | 43041.0417 | 44 | 44
2017-11-02 01:30 | 34 | 31 |  |  | 43041.0625 | 43 | 43
2017-11-02 02:00 | 35 | 32 |  |  | 43041.0833 | 43 | 43
2017-11-02 02:30 | 34 | 30 |  |  | 43041.1042 | 41 | 41
2017-11-02 03:00 | 34 | 30 |  |  | 43041.125 | 41 | 40
2017-11-02 03:30 | 34 | 30 |  |  | 43041.1458 | 41 | 40
2017-11-02 04:00 | 34 | 29 |  |  | 43041.1667 | 41 | 40
2017-11-02 04:30 | 37 | 33 |  |  | 43041.1875 | 46 | 46
2017-11-02 05:00 | 42 | 39 |  |  | 43041.2083 | 53 | 53
2017-11-02 05:30 | 44 | 41 |  |  | 43041.2292 | 56 | 56
2017-11-02 06:00 | 47 | 45 |  |  | 43041.25 | 61 | 61
2017-11-02 06:30 | 51 | 50 |  |  | 43041.2708 | 67 | 67
2017-11-02 07:00 | 51 | 51 |  |  | 43041.2917 | 71 | 71
2017-11-02 07:30 | 53 | 53 |  |  | 43041.3125 | 76 | 76
2017-11-02 08:00 | 53 | 53 |  |  | 43041.3333 | 77 | 77
2017-11-02 08:30 | 55 | 54 |  |  | 43041.3542 | 80 | 80
2017-11-02 09:00 | 56 | 55 |  |  | 43041.375 | 82 | 82
2017-11-02 09:30 | 57 | 57 |  |  | 43041.3958 | 82 | 82
2017-11-02 10:00 | 57 | 57 |  |  | 43041.4167 | 82 | 82
2017-11-02 10:30 | 58 | 58 |  |  | 43041.4375 | 82 | 82
2017-11-02 11:00 | 60 | 60 |  |  | 43041.4583 | 85 | 85
2017-11-02 11:30 | 62 | 62 |  |  | 43041.4792 | 86 | 86
2017-11-02 12:00 | 63 | 63 |  |  | 43041.5 | 89 | 88
2017-11-02 12:30 | 63 | 63 |  |  | 43041.5208 | 91 | 90
2017-11-02 13:00 | 66 | 66 |  |  | 43041.5417 | 94 | 93
2017-11-02 13:30 | 67 | 67 |  |  | 43041.5625 | 96 | 96
2017-11-02 14:00 | 68 | 68 |  |  | 43041.5833 | 94 | 94
2017-11-02 14:30 | 69 | 68 |  |  | 43041.6042 | 92 | 91
2017-11-02 15:00 | 68 | 67 |  |  | 43041.625 | 88 | 87
2017-11-02 15:30 | 68 | 67 |  |  | 43041.6458 | 90 | 89
2017-11-02 16:00 | 69 | 68 |  |  | 43041.6667 | 91 | 91
2017-11-02 16:30 | 71 | 70 |  |  | 43041.6875 | 93 | 92
2017-11-02 17:00 | 72 | 71 |  |  | 43041.7083 | 94 | 93
2017-11-02 17:30 | 73 | 71 |  |  | 43041.7292 | 93 | 91
2017-11-02 18:00 | 73 | 71 |  |  | 43041.75 | 92 | 91
2017-11-02 18:30 | 72 | 71 |  |  | 43041.7708 | 90 | 89
2017-11-02 19:00 | 77 | 76 |  |  | 43041.7917 | 96 | 94
2017-11-02 19:30 | 76 | 75 |  |  | 43041.8125 | 94 | 92
2017-11-02 20:00 | 74 | 73 |  |  | 43041.8333 | 91 | 89
2017-11-02 20:30 | 73 | 72 |  |  | 43041.8542 | 91 | 89
2017-11-02 21:00 | 71 | 70 |  |  | 43041.875 | 87 | 86
2017-11-02 21:30 | 65 | 64 |  |  | 43041.8958 | 80 | 79
2017-11-02 22:00 | 62 | 60 |  |  | 43041.9167 | 78 | 78
2017-11-02 22:30 | 63 | 61 |  |  | 43041.9375 | 79 | 79
2017-11-02 23:00 | 63 | 61 |  |  | 43041.9583 | 77 | 76
2017-11-02 23:30 | 59 | 57 |  |  | 43041.9792 | 73 | 73
2017-11-03 | 53 | 51 |  |  | 43042 | 66 | 66
2017-11-03 00:30 | 49 | 47 |  |  | 43042.0208 | 61 | 60
2017-11-03 01:00 | 45 | 42 |  |  | 43042.0417 | 56 | 55
2017-11-03 01:30 | 44 | 41 |  |  | 43042.0625 | 53 | 53
2017-11-03 02:00 | 43 | 40 |  |  | 43042.0833 | 53 | 53
2017-11-03 02:30 | 43 | 40 |  |  | 43042.1042 | 53 | 52
2017-11-03 03:00 | 42 | 39 |  |  | 43042.125 | 51 | 51
2017-11-03 03:30 | 43 | 39 |  |  | 43042.1458 | 52 | 51
2017-11-03 04:00 | 40 | 37 |  |  | 43042.1667 | 50 | 49
2017-11-03 04:30 | 41 | 38 |  |  | 43042.1875 | 51 | 50
2017-11-03 05:00 | 48 | 46 |  |  | 43042.2083 | 58 | 58
2017-11-03 05:30 | 53 | 51 |  |  | 43042.2292 | 65 | 65
2017-11-03 06:00 | 54 | 53 |  |  | 43042.25 | 69 | 68
2017-11-03 06:30 | 59 | 58 |  |  | 43042.2708 | 77 | 77
2017-11-03 07:00 | 60 | 60 |  |  | 43042.2917 | 81 | 81
2017-11-03 07:30 | 60 | 60 |  |  | 43042.3125 | 84 | 84
2017-11-03 08:00 | 62 | 62 |  |  | 43042.3333 | 89 | 88
2017-11-03 08:30 | 65 | 65 |  |  | 43042.3542 | 92 | 92
2017-11-03 09:00 | 64 | 64 |  |  | 43042.375 | 92 | 92
2017-11-03 09:30 | 63 | 63 |  |  | 43042.3958 | 91 | 90
2017-11-03 10:00 | 65 | 65 |  |  | 43042.4167 | 92 | 91
2017-11-03 10:30 | 62 | 62 |  |  | 43042.4375 | 87 | 86
2017-11-03 11:00 | 62 | 62 |  |  | 43042.4583 | 86 | 86
2017-11-03 11:30 | 64 | 64 |  |  | 43042.4792 | 91 | 91
2017-11-03 12:00 | 67 | 67 |  |  | 43042.5 | 96 | 96
2017-11-03 12:30 | 68 | 68 |  |  | 43042.5208 | 97 | 97
2017-11-03 13:00 | 71 | 71 |  |  | 43042.5417 | 99 | 99
2017-11-03 13:30 | 70 | 70 |  |  | 43042.5625 | 96 | 96
2017-11-03 14:00 | 69 | 69 |  |  | 43042.5833 | 92 | 92
2017-11-03 14:30 | 68 | 68 |  |  | 43042.6042 | 91 | 91
2017-11-03 15:00 | 68 | 68 |  |  | 43042.625 | 91 | 91
2017-11-03 15:30 | 69 | 69 |  |  | 43042.6458 | 93 | 93
2017-11-03 16:00 | 70 | 70 |  |  | 43042.6667 | 96 | 95
2017-11-03 16:30 | 71 | 71 |  |  | 43042.6875 | 96 | 96
2017-11-03 17:00 | 73 | 73 |  |  | 43042.7083 | 97 | 97
2017-11-03 17:30 | 72 | 71 |  |  | 43042.7292 | 94 | 93
2017-11-03 18:00 | 69 | 68 |  |  | 43042.75 | 89 | 88
2017-11-03 18:30 | 66 | 65 |  |  | 43042.7708 | 86 | 85
2017-11-03 19:00 | 68 | 68 |  |  | 43042.7917 | 88 | 87
2017-11-03 19:30 | 68 | 67 |  |  | 43042.8125 | 86 | 85
2017-11-03 20:00 | 66 | 65 |  |  | 43042.8333 | 85 | 84
2017-11-03 20:30 | 65 | 64 |  |  | 43042.8542 | 83 | 82
2017-11-03 21:00 | 61 | 60 |  |  | 43042.875 | 78 | 77
2017-11-03 21:30 | 58 | 57 |  |  | 43042.8958 | 76 | 74
2017-11-03 22:00 | 60 | 56 |  |  | 43042.9167 | 77 | 74
2017-11-03 22:30 | 63 | 58 |  |  | 43042.9375 | 80 | 77
2017-11-03 23:00 | 66 | 61 |  |  | 43042.9583 | 81 | 78
2017-11-03 23:30 | 63 | 59 |  |  | 43042.9792 | 78 | 76
2017-11-04 | 58 | 53 |  |  | 43043 | 72 | 69
2017-11-04 00:30 | 53 | 48 |  |  | 43043.0208 | 65 | 62
2017-11-04 01:00 | 50 | 44 |  |  | 43043.0417 | 61 | 57
2017-11-04 01:30 | 48 | 43 |  |  | 43043.0625 | 58 | 56
2017-11-04 02:00 | 47 | 43 |  |  | 43043.0833 | 56 | 55
2017-11-04 02:30 | 47 | 43 |  |  | 43043.1042 | 56 | 55
2017-11-04 03:00 | 46 | 42 |  |  | 43043.125 | 55 | 54
2017-11-04 03:30 | 43 | 40 |  |  | 43043.1458 | 53 | 53
2017-11-04 04:00 | 42 | 38 |  |  | 43043.1667 | 53 | 52
2017-11-04 04:30 | 42 | 38 |  |  | 43043.1875 | 52 | 51
2017-11-04 05:00 | 42 | 38 |  |  | 43043.2083 | 52 | 51
2017-11-04 05:30 | 42 | 37 |  |  | 43043.2292 | 51 | 51
2017-11-04 06:00 | 42 | 38 |  |  | 43043.25 | 53 | 53
2017-11-04 06:30 | 44 | 41 |  |  | 43043.2708 | 56 | 55
2017-11-04 07:00 | 44 | 41 |  |  | 43043.2917 | 57 | 57
2017-11-04 07:30 | 46 | 44 |  |  | 43043.3125 | 61 | 61
2017-11-04 08:00 | 46 | 44 |  |  | 43043.3333 | 62 | 62
2017-11-04 08:30 | 47 | 46 |  |  | 43043.3542 | 65 | 65
2017-11-04 09:00 | 49 | 48 |  |  | 43043.375 | 67 | 67
2017-11-04 09:30 | 50 | 49 |  |  | 43043.3958 | 67 | 67
2017-11-04 10:00 | 51 | 51 |  |  | 43043.4167 | 69 | 68
2017-11-04 10:30 | 51 | 50 |  |  | 43043.4375 | 69 | 69
2017-11-04 11:00 | 51 | 50 |  |  | 43043.4583 | 69 | 69
2017-11-04 11:30 | 52 | 51 |  |  | 43043.4792 | 69 | 69
2017-11-04 12:00 | 55 | 54 |  |  | 43043.5 | 72 | 72
2017-11-04 12:30 | 54 | 53 |  |  | 43043.5208 | 70 | 70
2017-11-04 13:00 | 55 | 55 |  |  | 43043.5417 | 71 | 71
2017-11-04 13:30 | 58 | 57 |  |  | 43043.5625 | 72 | 72
2017-11-04 14:00 | 61 | 60 |  |  | 43043.5833 | 72 | 72
2017-11-04 14:30 | 62 | 61 |  |  | 43043.6042 | 74 | 74
2017-11-04 15:00 | 62 | 61 |  |  | 43043.625 | 74 | 73
2017-11-04 15:30 | 62 | 61 |  |  | 43043.6458 | 78 | 78
2017-11-04 16:00 | 64 | 63 |  |  | 43043.6667 | 81 | 81
2017-11-04 16:30 | 67 | 65 |  |  | 43043.6875 | 83 | 83
2017-11-04 17:00 | 66 | 64 |  |  | 43043.7083 | 83 | 82
2017-11-04 17:30 | 65 | 63 |  |  | 43043.7292 | 82 | 80
2017-11-04 18:00 | 64 | 62 |  |  | 43043.75 | 80 | 79
2017-11-04 18:30 | 65 | 62 |  |  | 43043.7708 | 82 | 81
2017-11-04 19:00 | 68 | 66 |  |  | 43043.7917 | 86 | 85
2017-11-04 19:30 | 67 | 65 |  |  | 43043.8125 | 84 | 83
2017-11-04 20:00 | 66 | 64 |  |  | 43043.8333 | 83 | 82
2017-11-04 20:30 | 66 | 64 |  |  | 43043.8542 | 82 | 82
2017-11-04 21:00 | 65 | 63 |  |  | 43043.875 | 80 | 79
2017-11-04 21:30 | 61 | 59 |  |  | 43043.8958 | 77 | 76
2017-11-04 22:00 | 60 | 57 |  |  | 43043.9167 | 76 | 76
2017-11-04 22:30 | 61 | 59 |  |  | 43043.9375 | 79 | 78
2017-11-04 23:00 | 63 | 60 |  |  | 43043.9583 | 78 | 78
2017-11-04 23:30 | 59 | 57 |  |  | 43043.9792 | 74 | 74
2017-11-05 | 54 | 52 |  |  | 43044 | 68 | 67
2017-11-05 00:30 | 51 | 48 |  |  | 43044.0208 | 63 | 62
2017-11-05 01:00 | 48 | 44 |  |  | 43044.0417 | 59 | 58
2017-11-05 01:30 | 45 | 42 |  |  | 43044.0625 | 56 | 55
2017-11-05 02:00 | 45 | 41 |  |  | 43044.0833 | 55 | 55
2017-11-05 02:30 | 45 | 41 |  |  | 43044.1042 | 55 | 54
2017-11-05 03:00 | 43 | 39 |  |  | 43044.125 | 53 | 52
2017-11-05 03:30 | 42 | 38 |  |  | 43044.1458 | 52 | 51
2017-11-05 04:00 | 41 | 37 |  |  | 43044.1667 | 50 | 49
2017-11-05 04:30 | 41 | 36 |  |  | 43044.1875 | 49 | 49
2017-11-05 05:00 | 40 | 36 |  |  | 43044.2083 | 49 | 49
2017-11-05 05:30 | 37 | 34 |  |  | 43044.2292 | 48 | 48
2017-11-05 06:00 | 37 | 34 |  |  | 43044.25 | 48 | 48
2017-11-05 06:30 | 38 | 36 |  |  | 43044.2708 | 51 | 51
2017-11-05 07:00 | 39 | 37 |  |  | 43044.2917 | 53 | 53
2017-11-05 07:30 | 39 | 37 |  |  | 43044.3125 | 55 | 55
2017-11-05 08:00 | 42 | 41 |  |  | 43044.3333 | 60 | 60
2017-11-05 08:30 | 47 | 46 |  |  | 43044.3542 | 63 | 62
2017-11-05 09:00 | 50 | 49 |  |  | 43044.375 | 66 | 66
2017-11-05 09:30 | 47 | 46 |  |  | 43044.3958 | 67 | 66
2017-11-05 10:00 | 46 | 45 |  |  | 43044.4167 | 68 | 67
2017-11-05 10:30 | 47 | 46 |  |  | 43044.4375 | 71 | 70
2017-11-05 11:00 | 46 | 46 |  |  | 43044.4583 | 68 | 66
2017-11-05 11:30 | 46 | 46 |  |  | 43044.4792 | 65 | 64
2017-11-05 12:00 | 47 | 47 |  |  | 43044.5 | 65 | 64
2017-11-05 12:30 | 47 | 47 |  |  | 43044.5208 | 64 | 63
2017-11-05 13:00 | 48 | 48 |  |  | 43044.5417 | 65 | 64
2017-11-05 13:30 | 50 | 50 |  |  | 43044.5625 | 66 | 65
2017-11-05 14:00 | 52 | 52 |  |  | 43044.5833 | 67 | 67
2017-11-05 14:30 | 55 | 54 |  |  | 43044.6042 | 69 | 69
2017-11-05 15:00 | 56 | 55 |  |  | 43044.625 | 71 | 71
2017-11-05 15:30 | 57 | 57 |  |  | 43044.6458 | 74 | 73
2017-11-05 16:00 | 63 | 63 |  |  | 43044.6667 | 78 | 78
2017-11-05 16:30 | 61 | 61 |  |  | 43044.6875 | 76 | 76
2017-11-05 17:00 | 63 | 63 |  |  | 43044.7083 | 79 | 79
2017-11-05 17:30 | 64 | 64 |  |  | 43044.7292 | 80 | 79
2017-11-05 18:00 | 65 | 64 |  |  | 43044.75 | 79 | 79
2017-11-05 18:30 | 65 | 65 |  |  | 43044.7708 | 82 | 82
2017-11-05 19:00 | 69 | 69 |  |  | 43044.7917 | 87 | 87
2017-11-05 19:30 | 66 | 66 |  |  | 43044.8125 | 84 | 83
2017-11-05 20:00 | 65 | 65 |  |  | 43044.8333 | 82 | 82
2017-11-05 20:30 | 65 | 65 |  |  | 43044.8542 | 82 | 82
2017-11-05 21:00 | 64 | 64 |  |  | 43044.875 | 80 | 80
2017-11-05 21:30 | 61 | 61 |  |  | 43044.8958 | 76 | 76
2017-11-05 22:00 | 59 | 59 |  |  | 43044.9167 | 76 | 76
2017-11-05 22:30 | 59 | 59 |  |  | 43044.9375 | 76 | 76
2017-11-05 23:00 | 58 | 58 |  |  | 43044.9583 | 73 | 73
2017-11-05 23:30 | 56 | 55 |  |  | 43044.9792 | 70 | 70
2017-11-06 | 51 | 50 |  |  | 43045 | 64 | 64
2017-11-06 00:30 | 48 | 46 |  |  | 43045.0208 | 60 | 59
2017-11-06 01:00 | 45 | 44 |  |  | 43045.0417 | 56 | 56
2017-11-06 01:30 | 44 | 42 |  |  | 43045.0625 | 54 | 54
2017-11-06 02:00 | 45 | 44 |  |  | 43045.0833 | 56 | 56
2017-11-06 02:30 | 44 | 43 |  |  | 43045.1042 | 55 | 55
2017-11-06 03:00 | 44 | 42 |  |  | 43045.125 | 55 | 55
2017-11-06 03:30 | 43 | 41 |  |  | 43045.1458 | 53 | 53
2017-11-06 04:00 | 42 | 40 |  |  | 43045.1667 | 51 | 51
2017-11-06 04:30 | 41 | 40 |  |  | 43045.1875 | 52 | 52
2017-11-06 05:00 | 45 | 44 |  |  | 43045.2083 | 56 | 55
2017-11-06 05:30 | 47 | 46 |  |  | 43045.2292 | 59 | 58
2017-11-06 06:00 | 50 | 50 |  |  | 43045.25 | 64 | 64
2017-11-06 06:30 | 57 | 56 |  |  | 43045.2708 | 74 | 73
2017-11-06 07:00 | 57 | 57 |  |  | 43045.2917 | 78 | 77
2017-11-06 07:30 | 63 | 63 |  |  | 43045.3125 | 88 | 86
2017-11-06 08:00 | 63 | 62 |  |  | 43045.3333 | 87 | 85
2017-11-06 08:30 | 65 | 65 |  |  | 43045.3542 | 90 | 90
2017-11-06 09:00 | 68 | 68 |  |  | 43045.375 | 93 | 93
2017-11-06 09:30 | 71 | 71 |  |  | 43045.3958 | 95 | 95
2017-11-06 10:00 | 71 | 71 |  |  | 43045.4167 | 98 | 97
2017-11-06 10:30 | 68 | 68 |  |  | 43045.4375 | 92 | 92
2017-11-06 11:00 | 64 | 64 |  |  | 43045.4583 | 91 | 90
2017-11-06 11:30 | 72 | 72 |  |  | 43045.4792 | 97 | 97
2017-11-06 12:00 | 76 | 76 |  |  | 43045.5 | 102 | 102
2017-11-06 12:30 | 73 | 73 |  |  | 43045.5208 | 96 | 96
2017-11-06 13:00 | 78 | 78 |  |  | 43045.5417 | 100 | 99
2017-11-06 13:30 | 80 | 80 |  |  | 43045.5625 | 106 | 106
2017-11-06 14:00 | 75 | 75 |  |  | 43045.5833 | 101 | 100
2017-11-06 14:30 | 77 | 77 |  |  | 43045.6042 | 101 | 101
2017-11-06 15:00 | 73 | 73 |  |  | 43045.625 | 97 | 97
2017-11-06 15:30 | 75 | 75 |  |  | 43045.6458 | 99 | 99
2017-11-06 16:00 | 78 | 78 |  |  | 43045.6667 | 100 | 100
2017-11-06 16:30 | 80 | 80 |  |  | 43045.6875 | 103 | 103
2017-11-06 17:00 | 81 | 81 |  |  | 43045.7083 | 104 | 104
2017-11-06 17:30 | 82 | 81 |  |  | 43045.7292 | 101 | 101
2017-11-06 18:00 | 80 | 80 |  |  | 43045.75 | 99 | 99
2017-11-06 18:30 | 80 | 80 |  |  | 43045.7708 | 97 | 97
2017-11-06 19:00 | 84 | 84 |  |  | 43045.7917 | 101 | 101
2017-11-06 19:30 | 82 | 82 |  |  | 43045.8125 | 98 | 98
2017-11-06 20:00 | 79 | 78 |  |  | 43045.8333 | 95 | 95
2017-11-06 20:30 | 76 | 76 |  |  | 43045.8542 | 93 | 93
2017-11-06 21:00 | 74 | 73 |  |  | 43045.875 | 89 | 89
2017-11-06 21:30 | 69 | 69 |  |  | 43045.8958 | 82 | 82
2017-11-06 22:00 | 68 | 68 |  |  | 43045.9167 | 83 | 83
2017-11-06 22:30 | 66 | 65 |  |  | 43045.9375 | 83 | 83
2017-11-06 23:00 | 64 | 63 |  |  | 43045.9583 | 77 | 76
2017-11-06 23:30 | 59 | 57 |  |  | 43045.9792 | 72 | 71
2017-11-07 | 54 | 52 |  |  | 43046 | 66 | 66
2017-11-07 00:30 | 51 | 49 |  |  | 43046.0208 | 62 | 61
2017-11-07 01:00 | 48 | 45 |  |  | 43046.0417 | 57 | 56
2017-11-07 01:30 | 47 | 44 |  |  | 43046.0625 | 58 | 57
2017-11-07 02:00 | 49 | 45 |  |  | 43046.0833 | 58 | 57
2017-11-07 02:30 | 47 | 44 |  |  | 43046.1042 | 57 | 56
2017-11-07 03:00 | 48 | 44 |  |  | 43046.125 | 57 | 56
2017-11-07 03:30 | 46 | 43 |  |  | 43046.1458 | 56 | 55
2017-11-07 04:00 | 43 | 40 |  |  | 43046.1667 | 53 | 52
2017-11-07 04:30 | 44 | 40 |  |  | 43046.1875 | 54 | 54
2017-11-07 05:00 | 44 | 41 |  |  | 43046.2083 | 56 | 55
2017-11-07 05:30 | 46 | 43 |  |  | 43046.2292 | 58 | 57
2017-11-07 06:00 | 49 | 47 |  |  | 43046.25 | 61 | 61
2017-11-07 06:30 | 55 | 54 |  |  | 43046.2708 | 73 | 73
2017-11-07 07:00 | 58 | 57 |  |  | 43046.2917 | 79 | 79
2017-11-07 07:30 | 58 | 58 |  |  | 43046.3125 | 83 | 83
2017-11-07 08:00 | 60 | 59 |  |  | 43046.3333 | 85 | 85
2017-11-07 08:30 | 62 | 62 |  |  | 43046.3542 | 90 | 90
2017-11-07 09:00 | 61 | 61 |  |  | 43046.375 | 89 | 89
2017-11-07 09:30 | 63 | 63 |  |  | 43046.3958 | 89 | 89
2017-11-07 10:00 | 63 | 63 |  |  | 43046.4167 | 88 | 88
2017-11-07 10:30 | 64 | 64 |  |  | 43046.4375 | 89 | 89
2017-11-07 11:00 | 67 | 67 |  |  | 43046.4583 | 92 | 92
2017-11-07 11:30 | 69 | 69 |  |  | 43046.4792 | 96 | 96
2017-11-07 12:00 | 71 | 71 |  |  | 43046.5 | 99 | 99
2017-11-07 12:30 | 70 | 70 |  |  | 43046.5208 | 94 | 94
2017-11-07 13:00 | 70 | 69 |  |  | 43046.5417 | 97 | 97
2017-11-07 13:30 | 66 | 66 |  |  | 43046.5625 | 93 | 93
2017-11-07 14:00 | 72 | 72 |  |  | 43046.5833 | 94 | 94
2017-11-07 14:30 | 71 | 71 |  |  | 43046.6042 | 99 | 99
2017-11-07 15:00 | 75 | 75 |  |  | 43046.625 | 99 | 99
2017-11-07 15:30 | 73 | 72 |  |  | 43046.6458 | 103 | 103
2017-11-07 16:00 | 74 | 73 |  |  | 43046.6667 | 101 | 101
2017-11-07 16:30 | 72 | 71 |  |  | 43046.6875 | 98 | 98
2017-11-07 17:00 | 74 | 73 |  |  | 43046.7083 | 97 | 97
2017-11-07 17:30 | 72 | 72 |  |  | 43046.7292 | 95 | 95
2017-11-07 18:00 | 70 | 69 |  |  | 43046.75 | 90 | 89
2017-11-07 18:30 | 68 | 67 |  |  | 43046.7708 | 87 | 87
2017-11-07 19:00 | 71 | 70 |  |  | 43046.7917 | 89 | 88
2017-11-07 19:30 | 68 | 68 |  |  | 43046.8125 | 86 | 85
2017-11-07 20:00 | 67 | 67 |  |  | 43046.8333 | 85 | 84
2017-11-07 20:30 | 70 | 70 |  |  | 43046.8542 | 87 | 87
2017-11-07 21:00 | 69 | 67 |  |  | 43046.875 | 82 | 82
2017-11-07 21:30 | 63 | 62 |  |  | 43046.8958 | 76 | 76
2017-11-07 22:00 | 60 | 59 |  |  | 43046.9167 | 75 | 74
2017-11-07 22:30 | 63 | 61 |  |  | 43046.9375 | 78 | 77
2017-11-07 23:00 | 62 | 61 |  |  | 43046.9583 | 75 | 75
2017-11-07 23:30 | 56 | 54 |  |  | 43046.9792 | 70 | 69
2017-11-08 | 54 | 51 |  |  | 43047 | 66 | 65
2017-11-08 00:30 | 49 | 47 |  |  | 43047.0208 | 61 | 60
2017-11-08 01:00 | 46 | 44 |  |  | 43047.0417 | 56 | 56
2017-11-08 01:30 | 45 | 43 |  |  | 43047.0625 | 54 | 54
2017-11-08 02:00 | 45 | 43 |  |  | 43047.0833 | 54 | 54
2017-11-08 02:30 | 47 | 44 |  |  | 43047.1042 | 54 | 54
2017-11-08 03:00 | 47 | 43 |  |  | 43047.125 | 55 | 54
2017-11-08 03:30 | 46 | 43 |  |  | 43047.1458 | 55 | 54
2017-11-08 04:00 | 45 | 42 |  |  | 43047.1667 | 53 | 53
2017-11-08 04:30 | 46 | 43 |  |  | 43047.1875 | 55 | 54
2017-11-08 05:00 | 49 | 47 |  |  | 43047.2083 | 59 | 58
2017-11-08 05:30 | 52 | 50 |  |  | 43047.2292 | 63 | 63
2017-11-08 06:00 | 55 | 53 |  |  | 43047.25 | 67 | 67
2017-11-08 06:30 | 61 | 60 |  |  | 43047.2708 | 79 | 79
2017-11-08 07:00 | 65 | 64 |  |  | 43047.2917 | 83 | 83
2017-11-08 07:30 | 68 | 66 |  |  | 43047.3125 | 89 | 89
2017-11-08 08:00 | 69 | 68 |  |  | 43047.3333 | 91 | 91
2017-11-08 08:30 | 70 | 69 |  |  | 43047.3542 | 94 | 94
2017-11-08 09:00 | 70 | 70 |  |  | 43047.375 | 95 | 95
2017-11-08 09:30 | 71 | 70 |  |  | 43047.3958 | 93 | 93
2017-11-08 10:00 | 75 | 74 |  |  | 43047.4167 | 97 | 97
2017-11-08 10:30 | 75 | 74 |  |  | 43047.4375 | 95 | 95
2017-11-08 11:00 | 74 | 73 |  |  | 43047.4583 | 96 | 96
2017-11-08 11:30 | 77 | 77 |  |  | 43047.4792 | 99 | 99
2017-11-08 12:00 | 79 | 79 |  |  | 43047.5 | 102 | 102
2017-11-08 12:30 | 78 | 78 |  |  | 43047.5208 | 100 | 100
2017-11-08 13:00 | 79 | 79 |  |  | 43047.5417 | 96 | 96
2017-11-08 13:30 | 81 | 81 |  |  | 43047.5625 | 100 | 100
2017-11-08 14:00 | 80 | 80 |  |  | 43047.5833 | 101 | 101
2017-11-08 14:30 | 80 | 79 |  |  | 43047.6042 | 98 | 98
2017-11-08 15:00 | 77 | 76 |  |  | 43047.625 | 94 | 94
2017-11-08 15:30 | 76 | 75 |  |  | 43047.6458 | 94 | 94
2017-11-08 16:00 | 75 | 74 |  |  | 43047.6667 | 96 | 96
2017-11-08 16:30 | 74 | 73 |  |  | 43047.6875 | 93 | 93
2017-11-08 17:00 | 73 | 72 |  |  | 43047.7083 | 92 | 92
2017-11-08 17:30 | 76 | 75 |  |  | 43047.7292 | 93 | 93
2017-11-08 18:00 | 76 | 75 |  |  | 43047.75 | 93 | 93
2017-11-08 18:30 | 74 | 74 |  |  | 43047.7708 | 92 | 92
2017-11-08 19:00 | 77 | 77 |  |  | 43047.7917 | 93 | 93
2017-11-08 19:30 | 75 | 75 |  |  | 43047.8125 | 91 | 91
2017-11-08 20:00 | 75 | 74 |  |  | 43047.8333 | 90 | 89
2017-11-08 20:30 | 74 | 73 |  |  | 43047.8542 | 88 | 87
2017-11-08 21:00 | 70 | 70 |  |  | 43047.875 | 83 | 83
2017-11-08 21:30 | 65 | 65 |  |  | 43047.8958 | 78 | 78
2017-11-08 22:00 | 65 | 64 |  |  | 43047.9167 | 79 | 79
2017-11-08 22:30 | 65 | 64 |  |  | 43047.9375 | 80 | 80
2017-11-08 23:00 | 65 | 64 |  |  | 43047.9583 | 77 | 77
2017-11-08 23:30 | 61 | 59 |  |  | 43047.9792 | 72 | 72
2017-11-09 | 56 | 53 |  |  | 43048 | 66 | 65
2017-11-09 00:30 | 51 | 48 |  |  | 43048.0208 | 60 | 60
2017-11-09 01:00 | 48 | 45 |  |  | 43048.0417 | 56 | 56
2017-11-09 01:30 | 45 | 42 |  |  | 43048.0625 | 54 | 54
2017-11-09 02:00 | 45 | 42 |  |  | 43048.0833 | 54 | 54
2017-11-09 02:30 | 46 | 43 |  |  | 43048.1042 | 53 | 53
2017-11-09 03:00 | 45 | 43 |  |  | 43048.125 | 54 | 54
2017-11-09 03:30 | 44 | 42 |  |  | 43048.1458 | 52 | 52
2017-11-09 04:00 | 43 | 41 |  |  | 43048.1667 | 51 | 51
2017-11-09 04:30 | 42 | 40 |  |  | 43048.1875 | 50 | 50
2017-11-09 05:00 | 44 | 42 |  |  | 43048.2083 | 54 | 54
2017-11-09 05:30 | 48 | 46 |  |  | 43048.2292 | 58 | 58
2017-11-09 06:00 | 46 | 45 |  |  | 43048.25 | 58 | 58
2017-11-09 06:30 | 49 | 48 |  |  | 43048.2708 | 66 | 65
2017-11-09 07:00 | 50 | 50 |  |  | 43048.2917 | 69 | 69
2017-11-09 07:30 | 53 | 53 |  |  | 43048.3125 | 75 | 75
2017-11-09 08:00 | 54 | 54 |  |  | 43048.3333 | 77 | 77
2017-11-09 08:30 | 56 | 56 |  |  | 43048.3542 | 79 | 78
2017-11-09 09:00 | 53 | 53 |  |  | 43048.375 | 76 | 75
2017-11-09 09:30 | 53 | 53 |  |  | 43048.3958 | 78 | 77
2017-11-09 10:00 | 59 | 59 |  |  | 43048.4167 | 80 | 79
2017-11-09 10:30 | 59 | 59 |  |  | 43048.4375 | 78 | 78
2017-11-09 11:00 | 59 | 59 |  |  | 43048.4583 | 80 | 79
2017-11-09 11:30 | 59 | 59 |  |  | 43048.4792 | 82 | 82
2017-11-09 12:00 | 66 | 66 |  |  | 43048.5 | 84 | 83
2017-11-09 12:30 | 57 | 57 |  |  | 43048.5208 | 81 | 81
2017-11-09 13:00 | 63 | 63 |  |  | 43048.5417 | 89 | 88
2017-11-09 13:30 | 60 | 60 |  |  | 43048.5625 | 81 | 81
2017-11-09 14:00 | 62 | 62 |  |  | 43048.5833 | 76 | 76
2017-11-09 14:30 | 68 | 68 |  |  | 43048.6042 | 84 | 84
2017-11-09 15:00 | 70 | 70 |  |  | 43048.625 | 92 | 92
2017-11-09 15:30 | 72 | 71 |  |  | 43048.6458 | 87 | 87
2017-11-09 16:00 | 70 | 70 |  |  | 43048.6667 | 89 | 89
2017-11-09 16:30 | 73 | 73 |  |  | 43048.6875 | 92 | 91
2017-11-09 17:00 | 73 | 73 |  |  | 43048.7083 | 93 | 92
2017-11-09 17:30 | 73 | 73 |  |  | 43048.7292 | 92 | 92
2017-11-09 18:00 | 75 | 75 |  |  | 43048.75 | 92 | 92
2017-11-09 18:30 | 75 | 75 |  |  | 43048.7708 | 92 | 92
2017-11-09 19:00 | 78 | 78 |  |  | 43048.7917 | 94 | 94
2017-11-09 19:30 | 75 | 74 |  |  | 43048.8125 | 91 | 91
2017-11-09 20:00 | 74 | 73 |  |  | 43048.8333 | 88 | 88
2017-11-09 20:30 | 69 | 69 |  |  | 43048.8542 | 83 | 83
2017-11-09 21:00 | 64 | 64 |  |  | 43048.875 | 77 | 77
2017-11-09 21:30 | 59 | 59 |  |  | 43048.8958 | 72 | 72
2017-11-09 22:00 | 58 | 57 |  |  | 43048.9167 | 72 | 72
2017-11-09 22:30 | 57 | 56 |  |  | 43048.9375 | 71 | 71
2017-11-09 23:00 | 61 | 60 |  |  | 43048.9583 | 75 | 75
2017-11-09 23:30 | 59 | 57 |  |  | 43048.9792 | 72 | 72
2017-11-10 | 54 | 53 |  |  | 43049 | 66 | 66
2017-11-10 00:30 | 51 | 49 |  |  | 43049.0208 | 62 | 62
2017-11-10 01:00 | 49 | 47 |  |  | 43049.0417 | 59 | 58
2017-11-10 01:30 | 47 | 44 |  |  | 43049.0625 | 55 | 55
2017-11-10 02:00 | 47 | 44 |  |  | 43049.0833 | 55 | 54
2017-11-10 02:30 | 44 | 41 |  |  | 43049.1042 | 52 | 52
2017-11-10 03:00 | 43 | 40 |  |  | 43049.125 | 52 | 51
2017-11-10 03:30 | 43 | 40 |  |  | 43049.1458 | 51 | 50
2017-11-10 04:00 | 41 | 38 |  |  | 43049.1667 | 47 | 47
2017-11-10 04:30 | 40 | 37 |  |  | 43049.1875 | 48 | 47
2017-11-10 05:00 | 42 | 39 |  |  | 43049.2083 | 50 | 50
2017-11-10 05:30 | 45 | 42 |  |  | 43049.2292 | 55 | 55
2017-11-10 06:00 | 49 | 47 |  |  | 43049.25 | 61 | 61
2017-11-10 06:30 | 53 | 52 |  |  | 43049.2708 | 69 | 69
2017-11-10 07:00 | 55 | 55 |  |  | 43049.2917 | 77 | 76
2017-11-10 07:30 | 56 | 56 |  |  | 43049.3125 | 84 | 83
2017-11-10 08:00 | 61 | 61 |  |  | 43049.3333 | 91 | 90
2017-11-10 08:30 | 62 | 62 |  |  | 43049.3542 | 93 | 92
2017-11-10 09:00 | 60 | 60 |  |  | 43049.375 | 89 | 88
2017-11-10 09:30 | 62 | 62 |  |  | 43049.3958 | 91 | 90
2017-11-10 10:00 | 60 | 60 |  |  | 43049.4167 | 88 | 87
2017-11-10 10:30 | 59 | 59 |  |  | 43049.4375 | 87 | 85
2017-11-10 11:00 | 53 | 53 |  |  | 43049.4583 | 84 | 82
2017-11-10 11:30 | 52 | 52 |  |  | 43049.4792 | 82 | 81
2017-11-10 12:00 | 58 | 58 |  |  | 43049.5 | 85 | 84
2017-11-10 12:30 | 55 | 55 |  |  | 43049.5208 | 87 | 85
2017-11-10 13:00 | 49 | 49 |  |  | 43049.5417 | 80 | 79
2017-11-10 13:30 | 51 | 51 |  |  | 43049.5625 | 78 | 77
2017-11-10 14:00 | 45 | 45 |  |  | 43049.5833 | 79 | 78
2017-11-10 14:30 | 53 | 53 |  |  | 43049.6042 | 79 | 78
2017-11-10 15:00 | 55 | 55 |  |  | 43049.625 | 78 | 77
2017-11-10 15:30 | 56 | 56 |  |  | 43049.6458 | 76 | 75
2017-11-10 16:00 | 57 | 57 |  |  | 43049.6667 | 79 | 78
2017-11-10 16:30 | 59 | 59 |  |  | 43049.6875 | 83 | 82
2017-11-10 17:00 | 60 | 59 |  |  | 43049.7083 | 82 | 82
2017-11-10 17:30 | 61 | 61 |  |  | 43049.7292 | 82 | 82
2017-11-10 18:00 | 60 | 60 |  |  | 43049.75 | 79 | 79
2017-11-10 18:30 | 60 | 59 |  |  | 43049.7708 | 77 | 77
2017-11-10 19:00 | 61 | 60 |  |  | 43049.7917 | 77 | 77
2017-11-10 19:30 | 59 | 59 |  |  | 43049.8125 | 75 | 74
2017-11-10 20:00 | 59 | 59 |  |  | 43049.8333 | 75 | 75
2017-11-10 20:30 | 59 | 59 |  |  | 43049.8542 | 75 | 75
2017-11-10 21:00 | 58 | 58 |  |  | 43049.875 | 72 | 72
2017-11-10 21:30 | 55 | 54 |  |  | 43049.8958 | 68 | 68
2017-11-10 22:00 | 54 | 53 |  |  | 43049.9167 | 69 | 69
2017-11-10 22:30 | 54 | 52 |  |  | 43049.9375 | 68 | 68
2017-11-10 23:00 | 54 | 53 |  |  | 43049.9583 | 68 | 68
2017-11-10 23:30 | 51 | 49 |  |  | 43049.9792 | 64 | 64
2017-11-11 | 48 | 46 |  |  | 43050 | 60 | 60
2017-11-11 00:30 | 45 | 42 |  |  | 43050.0208 | 55 | 55
2017-11-11 01:00 | 41 | 38 |  |  | 43050.0417 | 50 | 50
2017-11-11 01:30 | 41 | 37 |  |  | 43050.0625 | 48 | 48
2017-11-11 02:00 | 40 | 36 |  |  | 43050.0833 | 47 | 47
2017-11-11 02:30 | 39 | 35 |  |  | 43050.1042 | 46 | 46
2017-11-11 03:00 | 38 | 34 |  |  | 43050.125 | 46 | 45
2017-11-11 03:30 | 37 | 33 |  |  | 43050.1458 | 45 | 45
2017-11-11 04:00 | 36 | 32 |  |  | 43050.1667 | 43 | 43
2017-11-11 04:30 | 36 | 32 |  |  | 43050.1875 | 44 | 43
2017-11-11 05:00 | 37 | 33 |  |  | 43050.2083 | 45 | 44
2017-11-11 05:30 | 38 | 34 |  |  | 43050.2292 | 46 | 45
2017-11-11 06:00 | 39 | 35 |  |  | 43050.25 | 49 | 48
2017-11-11 06:30 | 41 | 38 |  |  | 43050.2708 | 52 | 52
2017-11-11 07:00 | 43 | 40 |  |  | 43050.2917 | 55 | 55
2017-11-11 07:30 | 44 | 41 |  |  | 43050.3125 | 55 | 55
2017-11-11 08:00 | 44 | 42 |  |  | 43050.3333 | 57 | 57
2017-11-11 08:30 | 48 | 47 |  |  | 43050.3542 | 60 | 60
2017-11-11 09:00 | 48 | 46 |  |  | 43050.375 | 60 | 60
2017-11-11 09:30 | 45 | 42 |  |  | 43050.3958 | 62 | 62
2017-11-11 10:00 | 46 | 44 |  |  | 43050.4167 | 60 | 60
2017-11-11 10:30 | 50 | 48 |  |  | 43050.4375 | 63 | 63
2017-11-11 11:00 | 48 | 46 |  |  | 43050.4583 | 67 | 67
2017-11-11 11:30 | 49 | 47 |  |  | 43050.4792 | 65 | 65
2017-11-11 12:00 | 45 | 42 |  |  | 43050.5 | 59 | 59
2017-11-11 12:30 | 49 | 46 |  |  | 43050.5208 | 62 | 62
2017-11-11 13:00 | 49 | 46 |  |  | 43050.5417 | 59 | 59
2017-11-11 13:30 | 46 | 43 |  |  | 43050.5625 | 58 | 58
2017-11-11 14:00 | 46 | 43 |  |  | 43050.5833 | 57 | 57
2017-11-11 14:30 | 50 | 47 |  |  | 43050.6042 | 60 | 60
2017-11-11 15:00 | 52 | 49 |  |  | 43050.625 | 64 | 64
2017-11-11 15:30 | 50 | 47 |  |  | 43050.6458 | 63 | 63
2017-11-11 16:00 | 51 | 48 |  |  | 43050.6667 | 66 | 65
2017-11-11 16:30 | 54 | 51 |  |  | 43050.6875 | 67 | 67
2017-11-11 17:00 | 57 | 55 |  |  | 43050.7083 | 69 | 69
2017-11-11 17:30 | 55 | 52 |  |  | 43050.7292 | 69 | 69
2017-11-11 18:00 | 55 | 52 |  |  | 43050.75 | 69 | 68
2017-11-11 18:30 | 56 | 53 |  |  | 43050.7708 | 70 | 70
2017-11-11 19:00 | 58 | 55 |  |  | 43050.7917 | 73 | 72
2017-11-11 19:30 | 57 | 54 |  |  | 43050.8125 | 71 | 71
2017-11-11 20:00 | 57 | 55 |  |  | 43050.8333 | 72 | 72
2017-11-11 20:30 | 57 | 54 |  |  | 43050.8542 | 72 | 72
2017-11-11 21:00 | 56 | 54 |  |  | 43050.875 | 70 | 70
2017-11-11 21:30 | 55 | 53 |  |  | 43050.8958 | 69 | 68
2017-11-11 22:00 | 55 | 53 |  |  | 43050.9167 | 70 | 69
2017-11-11 22:30 | 56 | 54 |  |  | 43050.9375 | 71 | 71
2017-11-11 23:00 | 57 | 54 |  |  | 43050.9583 | 70 | 70
2017-11-11 23:30 | 54 | 51 |  |  | 43050.9792 | 66 | 66
2017-11-12 | 51 | 48 |  |  | 43051 | 63 | 62
2017-11-12 00:30 | 47 | 43 |  |  | 43051.0208 | 58 | 57
2017-11-12 01:00 | 43 | 38 |  |  | 43051.0417 | 53 | 52
2017-11-12 01:30 | 41 | 38 |  |  | 43051.0625 | 51 | 51
2017-11-12 02:00 | 40 | 37 |  |  | 43051.0833 | 50 | 50
2017-11-12 02:30 | 39 | 36 |  |  | 43051.1042 | 48 | 48
2017-11-12 03:00 | 38 | 35 |  |  | 43051.125 | 47 | 47
2017-11-12 03:30 | 36 | 32 |  |  | 43051.1458 | 45 | 45
2017-11-12 04:00 | 33 | 30 |  |  | 43051.1667 | 42 | 42
2017-11-12 04:30 | 32 | 29 |  |  | 43051.1875 | 43 | 42
2017-11-12 05:00 | 34 | 30 |  |  | 43051.2083 | 43 | 43
2017-11-12 05:30 | 34 | 29 |  |  | 43051.2292 | 43 | 43
2017-11-12 06:00 | 33 | 29 |  |  | 43051.25 | 42 | 42
2017-11-12 06:30 | 33 | 29 |  |  | 43051.2708 | 43 | 43
2017-11-12 07:00 | 33 | 29 |  |  | 43051.2917 | 43 | 43
2017-11-12 07:30 | 33 | 29 |  |  | 43051.3125 | 44 | 44
2017-11-12 08:00 | 33 | 29 |  |  | 43051.3333 | 45 | 45
2017-11-12 08:30 | 35 | 33 |  |  | 43051.3542 | 51 | 51
2017-11-12 09:00 | 38 | 36 |  |  | 43051.375 | 54 | 54
2017-11-12 09:30 | 41 | 40 |  |  | 43051.3958 | 56 | 56
2017-11-12 10:00 | 40 | 39 |  |  | 43051.4167 | 56 | 56
2017-11-12 10:30 | 38 | 37 |  |  | 43051.4375 | 55 | 54
2017-11-12 11:00 | 38 | 36 |  |  | 43051.4583 | 54 | 54
2017-11-12 11:30 | 36 | 35 |  |  | 43051.4792 | 52 | 52
2017-11-12 12:00 | 37 | 36 |  |  | 43051.5 | 51 | 51
2017-11-12 12:30 | 35 | 34 |  |  | 43051.5208 | 50 | 50
2017-11-12 13:00 | 35 | 34 |  |  | 43051.5417 | 50 | 50
2017-11-12 13:30 | 36 | 34 |  |  | 43051.5625 | 52 | 51
2017-11-12 14:00 | 37 | 36 |  |  | 43051.5833 | 53 | 52
2017-11-12 14:30 | 37 | 36 |  |  | 43051.6042 | 52 | 51
2017-11-12 15:00 | 40 | 39 |  |  | 43051.625 | 53 | 53
2017-11-12 15:30 | 42 | 41 |  |  | 43051.6458 | 56 | 56
2017-11-12 16:00 | 44 | 43 |  |  | 43051.6667 | 59 | 58
2017-11-12 16:30 | 46 | 45 |  |  | 43051.6875 | 61 | 61
2017-11-12 17:00 | 50 | 48 |  |  | 43051.7083 | 66 | 66
2017-11-12 17:30 | 51 | 49 |  |  | 43051.7292 | 66 | 66
2017-11-12 18:00 | 54 | 52 |  |  | 43051.75 | 70 | 70
2017-11-12 18:30 | 56 | 54 |  |  | 43051.7708 | 72 | 72
2017-11-12 19:00 | 58 | 57 |  |  | 43051.7917 | 76 | 76
2017-11-12 19:30 | 57 | 56 |  |  | 43051.8125 | 74 | 74
2017-11-12 20:00 | 57 | 56 |  |  | 43051.8333 | 73 | 73
2017-11-12 20:30 | 58 | 57 |  |  | 43051.8542 | 74 | 74
2017-11-12 21:00 | 55 | 55 |  |  | 43051.875 | 73 | 72
2017-11-12 21:30 | 53 | 52 |  |  | 43051.8958 | 69 | 69
2017-11-12 22:00 | 52 | 51 |  |  | 43051.9167 | 69 | 69
2017-11-12 22:30 | 51 | 49 |  |  | 43051.9375 | 69 | 68
2017-11-12 23:00 | 50 | 49 |  |  | 43051.9583 | 66 | 65
2017-11-12 23:30 | 47 | 45 |  |  | 43051.9792 | 62 | 62
2017-11-13 | 45 | 44 |  |  | 43052 | 59 | 59
2017-11-13 00:30 | 38 | 36 |  |  | 43052.0208 | 51 | 51
2017-11-13 01:00 | 35 | 33 |  |  | 43052.0417 | 48 | 48
2017-11-13 01:30 | 34 | 32 |  |  | 43052.0625 | 45 | 45
2017-11-13 02:00 | 34 | 32 |  |  | 43052.0833 | 44 | 44
2017-11-13 02:30 | 34 | 31 |  |  | 43052.1042 | 44 | 44
2017-11-13 03:00 | 32 | 30 |  |  | 43052.125 | 44 | 44
2017-11-13 03:30 | 32 | 29 |  |  | 43052.1458 | 43 | 43
2017-11-13 04:00 | 32 | 30 |  |  | 43052.1667 | 42 | 42
2017-11-13 04:30 | 35 | 33 |  |  | 43052.1875 | 45 | 45
2017-11-13 05:00 | 37 | 35 |  |  | 43052.2083 | 49 | 48
2017-11-13 05:30 | 38 | 37 |  |  | 43052.2292 | 51 | 51
2017-11-13 06:00 | 41 | 40 |  |  | 43052.25 | 55 | 55
2017-11-13 06:30 | 48 | 47 |  |  | 43052.2708 | 65 | 64
2017-11-13 07:00 | 51 | 51 |  |  | 43052.2917 | 71 | 70
2017-11-13 07:30 | 56 | 55 |  |  | 43052.3125 | 79 | 79
2017-11-13 08:00 | 57 | 57 |  |  | 43052.3333 | 81 | 81
2017-11-13 08:30 | 58 | 58 |  |  | 43052.3542 | 84 | 84
2017-11-13 09:00 | 60 | 60 |  |  | 43052.375 | 83 | 83
2017-11-13 09:30 | 58 | 58 |  |  | 43052.3958 | 83 | 82
2017-11-13 10:00 | 57 | 57 |  |  | 43052.4167 | 82 | 81
2017-11-13 10:30 | 55 | 55 |  |  | 43052.4375 | 80 | 80
2017-11-13 11:00 | 54 | 54 |  |  | 43052.4583 | 77 | 77
2017-11-13 11:30 | 56 | 56 |  |  | 43052.4792 | 77 | 77
2017-11-13 12:00 | 54 | 54 |  |  | 43052.5 | 76 | 76
2017-11-13 12:30 | 53 | 53 |  |  | 43052.5208 | 73 | 73
2017-11-13 13:00 | 51 | 51 |  |  | 43052.5417 | 74 | 74
2017-11-13 13:30 | 52 | 52 |  |  | 43052.5625 | 74 | 74
2017-11-13 14:00 | 53 | 53 |  |  | 43052.5833 | 75 | 75
2017-11-13 14:30 | 55 | 55 |  |  | 43052.6042 | 76 | 75
2017-11-13 15:00 | 54 | 54 |  |  | 43052.625 | 76 | 76
2017-11-13 15:30 | 53 | 53 |  |  | 43052.6458 | 75 | 75
2017-11-13 16:00 | 55 | 54 |  |  | 43052.6667 | 76 | 76
2017-11-13 16:30 | 55 | 55 |  |  | 43052.6875 | 77 | 77
2017-11-13 17:00 | 59 | 58 |  |  | 43052.7083 | 81 | 80
2017-11-13 17:30 | 61 | 61 |  |  | 43052.7292 | 81 | 81
2017-11-13 18:00 | 61 | 60 |  |  | 43052.75 | 80 | 80
2017-11-13 18:30 | 60 | 60 |  |  | 43052.7708 | 79 | 79
2017-11-13 19:00 | 64 | 64 |  |  | 43052.7917 | 82 | 82
2017-11-13 19:30 | 63 | 63 |  |  | 43052.8125 | 80 | 80
2017-11-13 20:00 | 61 | 61 |  |  | 43052.8333 | 78 | 78
2017-11-13 20:30 | 60 | 60 |  |  | 43052.8542 | 79 | 78
2017-11-13 21:00 | 60 | 60 |  |  | 43052.875 | 76 | 76
2017-11-13 21:30 | 58 | 58 |  |  | 43052.8958 | 74 | 73
2017-11-13 22:00 | 55 | 55 |  |  | 43052.9167 | 72 | 72
2017-11-13 22:30 | 55 | 54 |  |  | 43052.9375 | 71 | 71
2017-11-13 23:00 | 53 | 52 |  |  | 43052.9583 | 66 | 66
2017-11-13 23:30 | 50 | 48 |  |  | 43052.9792 | 61 | 61
2017-11-14 | 45 | 43 |  |  | 43053 | 56 | 56
2017-11-14 00:30 | 43 | 40 |  |  | 43053.0208 | 52 | 52
2017-11-14 01:00 | 43 | 40 |  |  | 43053.0417 | 50 | 50
2017-11-14 01:30 | 41 | 38 |  |  | 43053.0625 | 48 | 48
2017-11-14 02:00 | 39 | 36 |  |  | 43053.0833 | 48 | 47
2017-11-14 02:30 | 38 | 35 |  |  | 43053.1042 | 46 | 46
2017-11-14 03:00 | 39 | 36 |  |  | 43053.125 | 46 | 46
2017-11-14 03:30 | 39 | 36 |  |  | 43053.1458 | 46 | 45
2017-11-14 04:00 | 39 | 36 |  |  | 43053.1667 | 45 | 45
2017-11-14 04:30 | 38 | 35 |  |  | 43053.1875 | 45 | 45
2017-11-14 05:00 | 39 | 36 |  |  | 43053.2083 | 47 | 47
2017-11-14 05:30 | 42 | 39 |  |  | 43053.2292 | 50 | 50
2017-11-14 06:00 | 44 | 42 |  |  | 43053.25 | 53 | 53
2017-11-14 06:30 | 47 | 47 |  |  | 43053.2708 | 61 | 61
2017-11-14 07:00 | 49 | 49 |  |  | 43053.2917 | 67 | 66
2017-11-14 07:30 | 52 | 52 |  |  | 43053.3125 | 74 | 72
2017-11-14 08:00 | 53 | 53 |  |  | 43053.3333 | 77 | 75
2017-11-14 08:30 | 54 | 54 |  |  | 43053.3542 | 78 | 77
2017-11-14 09:00 | 61 | 61 |  |  | 43053.375 | 88 | 88
2017-11-14 09:30 | 60 | 60 |  |  | 43053.3958 | 86 | 86
2017-11-14 10:00 | 60 | 60 |  |  | 43053.4167 | 86 | 86
2017-11-14 10:30 | 60 | 60 |  |  | 43053.4375 | 86 | 85
2017-11-14 11:00 | 61 | 61 |  |  | 43053.4583 | 85 | 85
2017-11-14 11:30 | 61 | 60 |  |  | 43053.4792 | 86 | 86
2017-11-14 12:00 | 59 | 59 |  |  | 43053.5 | 85 | 85
2017-11-14 12:30 | 58 | 58 |  |  | 43053.5208 | 82 | 82
2017-11-14 13:00 | 60 | 60 |  |  | 43053.5417 | 86 | 86
2017-11-14 13:30 | 60 | 59 |  |  | 43053.5625 | 84 | 84
2017-11-14 14:00 | 58 | 57 |  |  | 43053.5833 | 81 | 81
2017-11-14 14:30 | 53 | 53 |  |  | 43053.6042 | 71 | 71
2017-11-14 15:00 | 49 | 49 |  |  | 43053.625 | 70 | 70
2017-11-14 15:30 | 53 | 53 |  |  | 43053.6458 | 73 | 73
2017-11-14 16:00 | 54 | 54 |  |  | 43053.6667 | 75 | 75
2017-11-14 16:30 | 56 | 56 |  |  | 43053.6875 | 77 | 77
2017-11-14 17:00 | 59 | 59 |  |  | 43053.7083 | 79 | 79
2017-11-14 17:30 | 60 | 59 |  |  | 43053.7292 | 78 | 78
2017-11-14 18:00 | 59 | 58 |  |  | 43053.75 | 76 | 75
2017-11-14 18:30 | 58 | 57 |  |  | 43053.7708 | 73 | 73
2017-11-14 19:00 | 62 | 61 |  |  | 43053.7917 | 77 | 77
2017-11-14 19:30 | 61 | 60 |  |  | 43053.8125 | 75 | 74
2017-11-14 20:00 | 60 | 59 |  |  | 43053.8333 | 74 | 74
2017-11-14 20:30 | 60 | 59 |  |  | 43053.8542 | 75 | 74
2017-11-14 21:00 | 57 | 56 |  |  | 43053.875 | 70 | 70
2017-11-14 21:30 | 53 | 52 |  |  | 43053.8958 | 65 | 65
2017-11-14 22:00 | 50 | 49 |  |  | 43053.9167 | 63 | 63
2017-11-14 22:30 | 50 | 48 |  |  | 43053.9375 | 63 | 62
2017-11-14 23:00 | 50 | 47 |  |  | 43053.9583 | 62 | 61
2017-11-14 23:30 | 48 | 45 |  |  | 43053.9792 | 59 | 58
2017-11-15 | 43 | 40 |  |  | 43054 | 55 | 54
2017-11-15 00:30 | 42 | 38 |  |  | 43054.0208 | 51 | 49
2017-11-15 01:00 | 37 | 33 |  |  | 43054.0417 | 44 | 42
2017-11-15 01:30 | 36 | 31 |  |  | 43054.0625 | 42 | 41
2017-11-15 02:00 | 37 | 32 |  |  | 43054.0833 | 43 | 41
2017-11-15 02:30 | 36 | 30 |  |  | 43054.1042 | 42 | 40
2017-11-15 03:00 | 36 | 30 |  |  | 43054.125 | 42 | 40
2017-11-15 03:30 | 35 | 29 |  |  | 43054.1458 | 41 | 39
2017-11-15 04:00 | 35 | 29 |  |  | 43054.1667 | 42 | 39
2017-11-15 04:30 | 35 | 30 |  |  | 43054.1875 | 42 | 40
2017-11-15 05:00 | 36 | 31 |  |  | 43054.2083 | 43 | 41
2017-11-15 05:30 | 38 | 34 |  |  | 43054.2292 | 46 | 44
2017-11-15 06:00 | 41 | 38 |  |  | 43054.25 | 51 | 50
2017-11-15 06:30 | 45 | 43 |  |  | 43054.2708 | 58 | 58
2017-11-15 07:00 | 49 | 48 |  |  | 43054.2917 | 65 | 65
2017-11-15 07:30 | 47 | 46 |  |  | 43054.3125 | 67 | 67
2017-11-15 08:00 | 46 | 46 |  |  | 43054.3333 | 68 | 68
2017-11-15 08:30 | 48 | 48 |  |  | 43054.3542 | 68 | 68
2017-11-15 09:00 | 48 | 48 |  |  | 43054.375 | 69 | 69
2017-11-15 09:30 | 48 | 48 |  |  | 43054.3958 | 66 | 66
2017-11-15 10:00 | 51 | 51 |  |  | 43054.4167 | 71 | 71
2017-11-15 10:30 | 51 | 51 |  |  | 43054.4375 | 70 | 70
2017-11-15 11:00 | 54 | 54 |  |  | 43054.4583 | 73 | 73
2017-11-15 11:30 | 56 | 56 |  |  | 43054.4792 | 75 | 75
2017-11-15 12:00 | 55 | 55 |  |  | 43054.5 | 70 | 70
2017-11-15 12:30 | 55 | 54 |  |  | 43054.5208 | 72 | 72
2017-11-15 13:00 | 56 | 55 |  |  | 43054.5417 | 76 | 76
2017-11-15 13:30 | 60 | 60 |  |  | 43054.5625 | 85 | 85
2017-11-15 14:00 | 60 | 59 |  |  | 43054.5833 | 81 | 81
2017-11-15 14:30 | 66 | 65 |  |  | 43054.6042 | 83 | 83
2017-11-15 15:00 | 66 | 65 |  |  | 43054.625 | 84 | 84
2017-11-15 15:30 | 61 | 59 |  |  | 43054.6458 | 82 | 82
2017-11-15 16:00 | 61 | 59 |  |  | 43054.6667 | 84 | 84
2017-11-15 16:30 | 60 | 58 |  |  | 43054.6875 | 80 | 80
2017-11-15 17:00 | 62 | 60 |  |  | 43054.7083 | 82 | 82
2017-11-15 17:30 | 62 | 60 |  |  | 43054.7292 | 80 | 80
2017-11-15 18:00 | 61 | 60 |  |  | 43054.75 | 78 | 78
2017-11-15 18:30 | 61 | 60 |  |  | 43054.7708 | 77 | 77
2017-11-15 19:00 | 64 | 62 |  |  | 43054.7917 | 80 | 79
2017-11-15 19:30 | 63 | 62 |  |  | 43054.8125 | 77 | 77
2017-11-15 20:00 | 62 | 61 |  |  | 43054.8333 | 77 | 77
2017-11-15 20:30 | 62 | 61 |  |  | 43054.8542 | 76 | 76
2017-11-15 21:00 | 57 | 57 |  |  | 43054.875 | 71 | 71
2017-11-15 21:30 | 54 | 53 |  |  | 43054.8958 | 67 | 67
2017-11-15 22:00 | 53 | 51 |  |  | 43054.9167 | 67 | 67
2017-11-15 22:30 | 54 | 52 |  |  | 43054.9375 | 67 | 67
2017-11-15 23:00 | 53 | 52 |  |  | 43054.9583 | 66 | 66
2017-11-15 23:30 | 50 | 49 |  |  | 43054.9792 | 63 | 62
2017-11-16 | 46 | 43 |  |  | 43055 | 56 | 55
2017-11-16 00:30 | 42 | 39 |  |  | 43055.0208 | 53 | 51
2017-11-16 01:00 | 39 | 35 |  |  | 43055.0417 | 48 | 46
2017-11-16 01:30 | 39 | 33 |  |  | 43055.0625 | 46 | 44
2017-11-16 02:00 | 40 | 34 |  |  | 43055.0833 | 47 | 45
2017-11-16 02:30 | 40 | 34 |  |  | 43055.1042 | 48 | 46
2017-11-16 03:00 | 39 | 33 |  |  | 43055.125 | 47 | 46
2017-11-16 03:30 | 37 | 32 |  |  | 43055.1458 | 46 | 45
2017-11-16 04:00 | 37 | 32 |  |  | 43055.1667 | 46 | 45
2017-11-16 04:30 | 39 | 35 |  |  | 43055.1875 | 49 | 48
2017-11-16 05:00 | 43 | 39 |  |  | 43055.2083 | 53 | 52
2017-11-16 05:30 | 45 | 41 |  |  | 43055.2292 | 57 | 57
2017-11-16 06:00 | 47 | 45 |  |  | 43055.25 | 62 | 61
2017-11-16 06:30 | 51 | 50 |  |  | 43055.2708 | 69 | 69
2017-11-16 07:00 | 54 | 53 |  |  | 43055.2917 | 75 | 75
2017-11-16 07:30 | 56 | 55 |  |  | 43055.3125 | 80 | 80
2017-11-16 08:00 | 57 | 57 |  |  | 43055.3333 | 83 | 83
2017-11-16 08:30 | 56 | 56 |  |  | 43055.3542 | 84 | 84
2017-11-16 09:00 | 53 | 53 |  |  | 43055.375 | 84 | 84
2017-11-16 09:30 | 55 | 55 |  |  | 43055.3958 | 86 | 86
2017-11-16 10:00 | 59 | 59 |  |  | 43055.4167 | 89 | 88
2017-11-16 10:30 | 58 | 58 |  |  | 43055.4375 | 86 | 86
2017-11-16 11:00 | 59 | 59 |  |  | 43055.4583 | 84 | 83
2017-11-16 11:30 | 60 | 59 |  |  | 43055.4792 | 90 | 89
2017-11-16 12:00 | 59 | 59 |  |  | 43055.5 | 88 | 88
2017-11-16 12:30 | 57 | 57 |  |  | 43055.5208 | 83 | 83
2017-11-16 13:00 | 62 | 59 |  |  | 43055.5417 | 88 | 84
2017-11-16 13:30 | 62 | 58 |  |  | 43055.5625 | 89 | 84
2017-11-16 14:00 | 63 | 59 |  |  | 43055.5833 | 87 | 82
2017-11-16 14:30 | 63 | 59 |  |  | 43055.6042 | 88 | 84
2017-11-16 15:00 | 64 | 60 |  |  | 43055.625 | 91 | 86
2017-11-16 15:30 | 67 | 63 |  |  | 43055.6458 | 97 | 92
2017-11-16 16:00 | 69 | 64 |  |  | 43055.6667 | 98 | 93
2017-11-16 16:30 | 69 | 63 |  |  | 43055.6875 | 99 | 94
2017-11-16 17:00 | 73 | 68 |  |  | 43055.7083 | 102 | 97
2017-11-16 17:30 | 73 | 67 |  |  | 43055.7292 | 102 | 95
2017-11-16 18:00 | 73 | 67 |  |  | 43055.75 | 100 | 93
2017-11-16 18:30 | 72 | 67 |  |  | 43055.7708 | 97 | 91
2017-11-16 19:00 | 75 | 71 |  |  | 43055.7917 | 99 | 93
2017-11-16 19:30 | 77 | 72 |  |  | 43055.8125 | 100 | 93
2017-11-16 20:00 | 77 | 72 |  |  | 43055.8333 | 101 | 94
2017-11-16 20:30 | 77 | 72 |  |  | 43055.8542 | 99 | 92
2017-11-16 21:00 | 69 | 68 |  |  | 43055.875 | 88 | 86
2017-11-16 21:30 | 63 | 61 |  |  | 43055.8958 | 82 | 80
2017-11-16 22:00 | 62 | 59 |  |  | 43055.9167 | 81 | 79
2017-11-16 22:30 | 61 | 58 |  |  | 43055.9375 | 81 | 78
2017-11-16 23:00 | 61 | 58 |  |  | 43055.9583 | 80 | 77
2017-11-16 23:30 | 60 | 57 |  |  | 43055.9792 | 78 | 75
2017-11-17 | 54 | 49 |  |  | 43056 | 71 | 67
2017-11-17 00:30 | 49 | 44 |  |  | 43056.0208 | 64 | 60
2017-11-17 01:00 | 46 | 40 |  |  | 43056.0417 | 61 | 56
2017-11-17 01:30 | 43 | 36 |  |  | 43056.0625 | 57 | 52
2017-11-17 02:00 | 43 | 37 |  |  | 43056.0833 | 56 | 52
2017-11-17 02:30 | 42 | 38 |  |  | 43056.1042 | 54 | 52
2017-11-17 03:00 | 41 | 37 |  |  | 43056.125 | 53 | 51
2017-11-17 03:30 | 41 | 37 |  |  | 43056.1458 | 53 | 50
2017-11-17 04:00 | 41 | 36 |  |  | 43056.1667 | 53 | 50
2017-11-17 04:30 | 42 | 38 |  |  | 43056.1875 | 54 | 51
2017-11-17 05:00 | 46 | 42 |  |  | 43056.2083 | 58 | 56
2017-11-17 05:30 | 48 | 44 |  |  | 43056.2292 | 61 | 59
2017-11-17 06:00 | 49 | 46 |  |  | 43056.25 | 65 | 64
2017-11-17 06:30 | 53 | 51 |  |  | 43056.2708 | 73 | 73
2017-11-17 07:00 | 55 | 54 |  |  | 43056.2917 | 77 | 77
2017-11-17 07:30 | 55 | 55 |  |  | 43056.3125 | 81 | 81
2017-11-17 08:00 | 55 | 55 |  |  | 43056.3333 | 84 | 84
2017-11-17 08:30 | 52 | 52 |  |  | 43056.3542 | 83 | 83
2017-11-17 09:00 | 51 | 50 |  |  | 43056.375 | 80 | 80
2017-11-17 09:30 | 51 | 51 |  |  | 43056.3958 | 80 | 80
2017-11-17 10:00 | 53 | 53 |  |  | 43056.4167 | 82 | 82
2017-11-17 10:30 | 52 | 52 |  |  | 43056.4375 | 84 | 84
2017-11-17 11:00 | 54 | 54 |  |  | 43056.4583 | 83 | 83
2017-11-17 11:30 | 51 | 51 |  |  | 43056.4792 | 81 | 81
2017-11-17 12:00 | 48 | 48 |  |  | 43056.5 | 79 | 79
2017-11-17 12:30 | 51 | 50 |  |  | 43056.5208 | 79 | 79
2017-11-17 13:00 | 53 | 52 |  |  | 43056.5417 | 82 | 82
2017-11-17 13:30 | 54 | 54 |  |  | 43056.5625 | 80 | 80
2017-11-17 14:00 | 56 | 56 |  |  | 43056.5833 | 81 | 81
2017-11-17 14:30 | 56 | 55 |  |  | 43056.6042 | 80 | 80
2017-11-17 15:00 | 56 | 55 |  |  | 43056.625 | 80 | 80
2017-11-17 15:30 | 56 | 56 |  |  | 43056.6458 | 82 | 82
2017-11-17 16:00 | 61 | 60 |  |  | 43056.6667 | 85 | 85
2017-11-17 16:30 | 62 | 61 |  |  | 43056.6875 | 86 | 85
2017-11-17 17:00 | 63 | 62 |  |  | 43056.7083 | 87 | 87
2017-11-17 17:30 | 61 | 60 |  |  | 43056.7292 | 85 | 84
2017-11-17 18:00 | 59 | 58 |  |  | 43056.75 | 81 | 80
2017-11-17 18:30 | 56 | 55 |  |  | 43056.7708 | 76 | 76
2017-11-17 19:00 | 59 | 58 |  |  | 43056.7917 | 81 | 80
2017-11-17 19:30 | 59 | 58 |  |  | 43056.8125 | 80 | 80
2017-11-17 20:00 | 58 | 57 |  |  | 43056.8333 | 78 | 78
2017-11-17 20:30 | 57 | 55 |  |  | 43056.8542 | 76 | 76
2017-11-17 21:00 | 54 | 52 |  |  | 43056.875 | 73 | 72
2017-11-17 21:30 | 51 | 48 |  |  | 43056.8958 | 68 | 68
2017-11-17 22:00 | 50 | 47 |  |  | 43056.9167 | 68 | 67
2017-11-17 22:30 | 48 | 46 |  |  | 43056.9375 | 66 | 65
2017-11-17 23:00 | 51 | 48 |  |  | 43056.9583 | 67 | 66
2017-11-17 23:30 | 49 | 46 |  |  | 43056.9792 | 66 | 65
2017-11-18 | 46 | 42 |  |  | 43057 | 61 | 60
2017-11-18 00:30 | 41 | 37 |  |  | 43057.0208 | 56 | 54
2017-11-18 01:00 | 40 | 35 |  |  | 43057.0417 | 52 | 50
2017-11-18 01:30 | 38 | 33 |  |  | 43057.0625 | 50 | 48
2017-11-18 02:00 | 38 | 33 |  |  | 43057.0833 | 50 | 47
2017-11-18 02:30 | 38 | 32 |  |  | 43057.1042 | 49 | 47
2017-11-18 03:00 | 36 | 31 |  |  | 43057.125 | 48 | 45
2017-11-18 03:30 | 36 | 31 |  |  | 43057.1458 | 47 | 45
2017-11-18 04:00 | 36 | 31 |  |  | 43057.1667 | 46 | 44
2017-11-18 04:30 | 36 | 30 |  |  | 43057.1875 | 47 | 45
2017-11-18 05:00 | 38 | 33 |  |  | 43057.2083 | 49 | 45
2017-11-18 05:30 | 37 | 31 |  |  | 43057.2292 | 49 | 46
2017-11-18 06:00 | 36 | 31 |  |  | 43057.25 | 49 | 46
2017-11-18 06:30 | 37 | 32 |  |  | 43057.2708 | 50 | 48
2017-11-18 07:00 | 37 | 32 |  |  | 43057.2917 | 52 | 51
2017-11-18 07:30 | 38 | 34 |  |  | 43057.3125 | 56 | 54
2017-11-18 08:00 | 42 | 39 |  |  | 43057.3333 | 61 | 60
2017-11-18 08:30 | 44 | 42 |  |  | 43057.3542 | 65 | 65
2017-11-18 09:00 | 46 | 45 |  |  | 43057.375 | 67 | 67
2017-11-18 09:30 | 50 | 49 |  |  | 43057.3958 | 68 | 68
2017-11-18 10:00 | 51 | 50 |  |  | 43057.4167 | 68 | 68
2017-11-18 10:30 | 50 | 48 |  |  | 43057.4375 | 68 | 68
2017-11-18 11:00 | 49 | 48 |  |  | 43057.4583 | 69 | 69
2017-11-18 11:30 | 45 | 43 |  |  | 43057.4792 | 65 | 65
2017-11-18 12:00 | 45 | 43 |  |  | 43057.5 | 66 | 66
2017-11-18 12:30 | 49 | 47 |  |  | 43057.5208 | 68 | 68
2017-11-18 13:00 | 50 | 48 |  |  | 43057.5417 | 68 | 67
2017-11-18 13:30 | 49 | 47 |  |  | 43057.5625 | 69 | 69
2017-11-18 14:00 | 48 | 46 |  |  | 43057.5833 | 68 | 68
2017-11-18 14:30 | 47 | 44 |  |  | 43057.6042 | 67 | 67
2017-11-18 15:00 | 46 | 44 |  |  | 43057.625 | 66 | 65
2017-11-18 15:30 | 47 | 45 |  |  | 43057.6458 | 67 | 66
2017-11-18 16:00 | 49 | 47 |  |  | 43057.6667 | 67 | 67
2017-11-18 16:30 | 48 | 45 |  |  | 43057.6875 | 68 | 67
2017-11-18 17:00 | 49 | 47 |  |  | 43057.7083 | 69 | 69
2017-11-18 17:30 | 50 | 47 |  |  | 43057.7292 | 69 | 69
2017-11-18 18:00 | 51 | 49 |  |  | 43057.75 | 71 | 70
2017-11-18 18:30 | 52 | 49 |  |  | 43057.7708 | 72 | 71
2017-11-18 19:00 | 52 | 50 |  |  | 43057.7917 | 74 | 73
2017-11-18 19:30 | 52 | 50 |  |  | 43057.8125 | 73 | 72
2017-11-18 20:00 | 52 | 49 |  |  | 43057.8333 | 71 | 70
2017-11-18 20:30 | 51 | 48 |  |  | 43057.8542 | 70 | 69
2017-11-18 21:00 | 50 | 47 |  |  | 43057.875 | 69 | 68
2017-11-18 21:30 | 49 | 45 |  |  | 43057.8958 | 66 | 65
2017-11-18 22:00 | 47 | 44 |  |  | 43057.9167 | 65 | 64
2017-11-18 22:30 | 47 | 44 |  |  | 43057.9375 | 65 | 64
2017-11-18 23:00 | 49 | 45 |  |  | 43057.9583 | 65 | 64
2017-11-18 23:30 | 47 | 42 |  |  | 43057.9792 | 62 | 60
2017-11-19 | 43 | 38 |  |  | 43058 | 58 | 56
2017-11-19 00:30 | 40 | 34 |  |  | 43058.0208 | 53 | 51
2017-11-19 01:00 | 36 | 31 |  |  | 43058.0417 | 48 | 47
2017-11-19 01:30 | 35 | 29 |  |  | 43058.0625 | 46 | 45
2017-11-19 02:00 | 35 | 29 |  |  | 43058.0833 | 46 | 44
2017-11-19 02:30 | 34 | 28 |  |  | 43058.1042 | 45 | 43
2017-11-19 03:00 | 34 | 28 |  |  | 43058.125 | 44 | 42
2017-11-19 03:30 | 33 | 27 |  |  | 43058.1458 | 44 | 42
2017-11-19 04:00 | 33 | 27 |  |  | 43058.1667 | 44 | 42
2017-11-19 04:30 | 29 | 26 |  |  | 43058.1875 | 43 | 40
2017-11-19 05:00 | 26 | 25 |  |  | 43058.2083 | 44 | 39
2017-11-19 05:30 | 26 | 25 |  |  | 43058.2292 | 44 | 39
2017-11-19 06:00 | 26 | 25 |  |  | 43058.25 | 45 | 40
2017-11-19 06:30 | 24 | 23 |  |  | 43058.2708 | 45 | 40
2017-11-19 07:00 | 23 | 22 |  |  | 43058.2917 | 44 | 40
2017-11-19 07:30 | 24 | 24 |  |  | 43058.3125 | 45 | 41
2017-11-19 08:00 | 26 | 26 |  |  | 43058.3333 | 48 | 45
2017-11-19 08:30 | 33 | 32 |  |  | 43058.3542 | 51 | 49
2017-11-19 09:00 | 39 | 39 |  |  | 43058.375 | 57 | 55
2017-11-19 09:30 | 36 | 36 |  |  | 43058.3958 | 60 | 59
2017-11-19 10:00 | 37 | 37 |  |  | 43058.4167 | 61 | 58
2017-11-19 10:30 | 40 | 40 |  |  | 43058.4375 | 64 | 61
2017-11-19 11:00 | 40 | 40 |  |  | 43058.4583 | 64 | 62
2017-11-19 11:30 | 41 | 41 |  |  | 43058.4792 | 64 | 61
2017-11-19 12:00 | 40 | 40 |  |  | 43058.5 | 61 | 59
2017-11-19 12:30 | 41 | 41 |  |  | 43058.5208 | 59 | 56
2017-11-19 13:00 | 42 | 42 |  |  | 43058.5417 | 60 | 58
2017-11-19 13:30 | 42 | 42 |  |  | 43058.5625 | 61 | 60
2017-11-19 14:00 | 38 | 38 |  |  | 43058.5833 | 59 | 57
2017-11-19 14:30 | 36 | 36 |  |  | 43058.6042 | 59 | 57
2017-11-19 15:00 | 36 | 36 |  |  | 43058.625 | 59 | 56
2017-11-19 15:30 | 40 | 40 |  |  | 43058.6458 | 59 | 56
2017-11-19 16:00 | 37 | 36 |  |  | 43058.6667 | 57 | 55
2017-11-19 16:30 | 40 | 40 |  |  | 43058.6875 | 63 | 61
2017-11-19 17:00 | 44 | 44 |  |  | 43058.7083 | 66 | 64
2017-11-19 17:30 | 47 | 46 |  |  | 43058.7292 | 67 | 65
2017-11-19 18:00 | 47 | 47 |  |  | 43058.75 | 69 | 67
2017-11-19 18:30 | 48 | 48 |  |  | 43058.7708 | 70 | 68
2017-11-19 19:00 | 50 | 50 |  |  | 43058.7917 | 74 | 71
2017-11-19 19:30 | 50 | 50 |  |  | 43058.8125 | 74 | 71
2017-11-19 20:00 | 49 | 49 |  |  | 43058.8333 | 73 | 70
2017-11-19 20:30 | 49 | 49 |  |  | 43058.8542 | 74 | 71
2017-11-19 21:00 | 47 | 47 |  |  | 43058.875 | 70 | 67
2017-11-19 21:30 | 44 | 43 |  |  | 43058.8958 | 67 | 63
2017-11-19 22:00 | 43 | 43 |  |  | 43058.9167 | 67 | 63
2017-11-19 22:30 | 43 | 42 |  |  | 43058.9375 | 67 | 62
2017-11-19 23:00 | 45 | 44 |  |  | 43058.9583 | 67 | 62
2017-11-19 23:30 | 42 | 41 |  |  | 43058.9792 | 64 | 59
2017-11-20 | 37 | 36 |  |  | 43059 | 60 | 54
2017-11-20 00:30 | 34 | 33 |  |  | 43059.0208 | 55 | 48
2017-11-20 01:00 | 30 | 28 |  |  | 43059.0417 | 51 | 44
2017-11-20 01:30 | 29 | 28 |  |  | 43059.0625 | 48 | 42
2017-11-20 02:00 | 29 | 27 |  |  | 43059.0833 | 48 | 42
2017-11-20 02:30 | 28 | 26 |  |  | 43059.1042 | 47 | 41
2017-11-20 03:00 | 29 | 28 |  |  | 43059.125 | 48 | 42
2017-11-20 03:30 | 30 | 29 |  |  | 43059.1458 | 47 | 41
2017-11-20 04:00 | 28 | 27 |  |  | 43059.1667 | 48 | 41
2017-11-20 04:30 | 29 | 28 |  |  | 43059.1875 | 48 | 42
2017-11-20 05:00 | 31 | 30 |  |  | 43059.2083 | 50 | 44
2017-11-20 05:30 | 35 | 35 |  |  | 43059.2292 | 55 | 50
2017-11-20 06:00 | 39 | 39 |  |  | 43059.25 | 58 | 54
2017-11-20 06:30 | 44 | 44 |  |  | 43059.2708 | 64 | 62
2017-11-20 07:00 | 47 | 47 |  |  | 43059.2917 | 70 | 68
2017-11-20 07:30 | 51 | 51 |  |  | 43059.3125 | 78 | 77
2017-11-20 08:00 | 53 | 53 |  |  | 43059.3333 | 80 | 79
2017-11-20 08:30 | 54 | 53 |  |  | 43059.3542 | 79 | 79
2017-11-20 09:00 | 52 | 52 |  |  | 43059.375 | 78 | 78
2017-11-20 09:30 | 53 | 53 |  |  | 43059.3958 | 79 | 79
2017-11-20 10:00 | 54 | 53 |  |  | 43059.4167 | 78 | 77
2017-11-20 10:30 | 53 | 53 |  |  | 43059.4375 | 77 | 77
2017-11-20 11:00 | 52 | 52 |  |  | 43059.4583 | 79 | 79
2017-11-20 11:30 | 52 | 52 |  |  | 43059.4792 | 75 | 75
2017-11-20 12:00 | 52 | 52 |  |  | 43059.5 | 74 | 74
2017-11-20 12:30 | 54 | 54 |  |  | 43059.5208 | 74 | 74
2017-11-20 13:00 | 55 | 55 |  |  | 43059.5417 | 75 | 75
2017-11-20 13:30 | 55 | 55 |  |  | 43059.5625 | 76 | 76
2017-11-20 14:00 | 57 | 57 |  |  | 43059.5833 | 80 | 80
2017-11-20 14:30 | 62 | 62 |  |  | 43059.6042 | 82 | 82
2017-11-20 15:00 | 63 | 63 |  |  | 43059.625 | 84 | 84
2017-11-20 15:30 | 60 | 60 |  |  | 43059.6458 | 83 | 82
2017-11-20 16:00 | 60 | 60 |  |  | 43059.6667 | 83 | 83
2017-11-20 16:30 | 61 | 61 |  |  | 43059.6875 | 85 | 85
2017-11-20 17:00 | 62 | 61 |  |  | 43059.7083 | 83 | 83
2017-11-20 17:30 | 60 | 60 |  |  | 43059.7292 | 80 | 80
2017-11-20 18:00 | 60 | 59 |  |  | 43059.75 | 79 | 79
2017-11-20 18:30 | 60 | 59 |  |  | 43059.7708 | 78 | 78
2017-11-20 19:00 | 63 | 62 |  |  | 43059.7917 | 81 | 81
2017-11-20 19:30 | 62 | 60 |  |  | 43059.8125 | 79 | 79
2017-11-20 20:00 | 60 | 59 |  |  | 43059.8333 | 76 | 76
2017-11-20 20:30 | 58 | 58 |  |  | 43059.8542 | 74 | 74
2017-11-20 21:00 | 56 | 55 |  |  | 43059.875 | 71 | 71
2017-11-20 21:30 | 54 | 53 |  |  | 43059.8958 | 69 | 69
2017-11-20 22:00 | 53 | 52 |  |  | 43059.9167 | 69 | 69
2017-11-20 22:30 | 52 | 51 |  |  | 43059.9375 | 67 | 67
2017-11-20 23:00 | 53 | 50 |  |  | 43059.9583 | 67 | 66
2017-11-20 23:30 | 52 | 49 |  |  | 43059.9792 | 65 | 64
2017-11-21 | 49 | 45 |  |  | 43060 | 62 | 61
2017-11-21 00:30 | 46 | 42 |  |  | 43060.0208 | 57 | 56
2017-11-21 01:00 | 39 | 38 |  |  | 43060.0417 | 55 | 50
2017-11-21 01:30 | 37 | 36 |  |  | 43060.0625 | 54 | 48
2017-11-21 02:00 | 36 | 35 |  |  | 43060.0833 | 54 | 48
2017-11-21 02:30 | 37 | 36 |  |  | 43060.1042 | 54 | 48
2017-11-21 03:00 | 35 | 34 |  |  | 43060.125 | 52 | 45
2017-11-21 03:30 | 36 | 35 |  |  | 43060.1458 | 54 | 47
2017-11-21 04:00 | 35 | 34 |  |  | 43060.1667 | 53 | 47
2017-11-21 04:30 | 36 | 35 |  |  | 43060.1875 | 54 | 48
2017-11-21 05:00 | 38 | 37 |  |  | 43060.2083 | 57 | 51
2017-11-21 05:30 | 40 | 40 |  |  | 43060.2292 | 60 | 56
2017-11-21 06:00 | 44 | 43 |  |  | 43060.25 | 63 | 59
2017-11-21 06:30 | 46 | 46 |  |  | 43060.2708 | 67 | 65
2017-11-21 07:00 | 51 | 49 |  |  | 43060.2917 | 80 | 72
2017-11-21 07:30 | 54 | 53 |  |  | 43060.3125 | 87 | 79
2017-11-21 08:00 | 56 | 55 |  |  | 43060.3333 | 89 | 82
2017-11-21 08:30 | 58 | 56 |  |  | 43060.3542 | 92 | 84
2017-11-21 09:00 | 59 | 58 |  |  | 43060.375 | 94 | 87
2017-11-21 09:30 | 58 | 57 |  |  | 43060.3958 | 92 | 86
2017-11-21 10:00 | 57 | 56 |  |  | 43060.4167 | 91 | 85
2017-11-21 10:30 | 55 | 54 |  |  | 43060.4375 | 87 | 81
2017-11-21 11:00 | 54 | 53 |  |  | 43060.4583 | 87 | 81
2017-11-21 11:30 | 56 | 55 |  |  | 43060.4792 | 86 | 81
2017-11-21 12:00 | 57 | 56 |  |  | 43060.5 | 87 | 81
2017-11-21 12:30 | 59 | 58 |  |  | 43060.5208 | 84 | 78
2017-11-21 13:00 | 55 | 55 |  |  | 43060.5417 | 82 | 76
2017-11-21 13:30 | 51 | 50 |  |  | 43060.5625 | 86 | 80
2017-11-21 14:00 | 59 | 59 |  |  | 43060.5833 | 91 | 85
2017-11-21 14:30 | 58 | 58 |  |  | 43060.6042 | 93 | 87
2017-11-21 15:00 | 55 | 55 |  |  | 43060.625 | 89 | 82
2017-11-21 15:30 | 56 | 55 |  |  | 43060.6458 | 88 | 81
2017-11-21 16:00 | 57 | 56 |  |  | 43060.6667 | 89 | 82
2017-11-21 16:30 | 57 | 56 |  |  | 43060.6875 | 89 | 81
2017-11-21 17:00 | 57 | 56 |  |  | 43060.7083 | 87 | 81
2017-11-21 17:30 | 57 | 56 |  |  | 43060.7292 | 86 | 80
2017-11-21 18:00 | 56 | 55 |  |  | 43060.75 | 86 | 79
2017-11-21 18:30 | 56 | 55 |  |  | 43060.7708 | 85 | 76
2017-11-21 19:00 | 58 | 57 |  |  | 43060.7917 | 88 | 80
2017-11-21 19:30 | 57 | 56 |  |  | 43060.8125 | 86 | 77
2017-11-21 20:00 | 57 | 56 |  |  | 43060.8333 | 86 | 77
2017-11-21 20:30 | 57 | 56 |  |  | 43060.8542 | 85 | 78
2017-11-21 21:00 | 56 | 56 |  |  | 43060.875 | 78 | 76
2017-11-21 21:30 | 52 | 52 |  |  | 43060.8958 | 74 | 72
2017-11-21 22:00 | 52 | 52 |  |  | 43060.9167 | 73 | 71
2017-11-21 22:30 | 51 | 50 |  |  | 43060.9375 | 71 | 69
2017-11-21 23:00 | 54 | 53 |  |  | 43060.9583 | 72 | 70
2017-11-21 23:30 | 51 | 51 |  |  | 43060.9792 | 70 | 67
2017-11-22 | 46 | 45 |  |  | 43061 | 66 | 62
2017-11-22 00:30 | 40 | 39 |  |  | 43061.0208 | 59 | 55
2017-11-22 01:00 | 37 | 37 |  |  | 43061.0417 | 55 | 50
2017-11-22 01:30 | 35 | 34 |  |  | 43061.0625 | 53 | 47
2017-11-22 02:00 | 36 | 35 |  |  | 43061.0833 | 54 | 49
2017-11-22 02:30 | 35 | 34 |  |  | 43061.1042 | 53 | 48
2017-11-22 03:00 | 35 | 34 |  |  | 43061.125 | 53 | 47
2017-11-22 03:30 | 35 | 35 |  |  | 43061.1458 | 52 | 47
2017-11-22 04:00 | 36 | 35 |  |  | 43061.1667 | 53 | 47
2017-11-22 04:30 | 36 | 36 |  |  | 43061.1875 | 54 | 48
2017-11-22 05:00 | 38 | 37 |  |  | 43061.2083 | 56 | 51
2017-11-22 05:30 | 42 | 42 |  |  | 43061.2292 | 60 | 55
2017-11-22 06:00 | 44 | 44 |  |  | 43061.25 | 63 | 59
2017-11-22 06:30 | 48 | 48 |  |  | 43061.2708 | 68 | 66
2017-11-22 07:00 | 52 | 52 |  |  | 43061.2917 | 74 | 73
2017-11-22 07:30 | 56 | 56 |  |  | 43061.3125 | 82 | 81
2017-11-22 08:00 | 56 | 56 |  |  | 43061.3333 | 83 | 82
2017-11-22 08:30 | 55 | 55 |  |  | 43061.3542 | 83 | 82
2017-11-22 09:00 | 54 | 54 |  |  | 43061.375 | 78 | 78
2017-11-22 09:30 | 53 | 53 |  |  | 43061.3958 | 80 | 79
2017-11-22 10:00 | 52 | 52 |  |  | 43061.4167 | 81 | 79
2017-11-22 10:30 | 52 | 52 |  |  | 43061.4375 | 80 | 78
2017-11-22 11:00 | 51 | 51 |  |  | 43061.4583 | 77 | 75
2017-11-22 11:30 | 52 | 52 |  |  | 43061.4792 | 80 | 78
2017-11-22 12:00 | 53 | 53 |  |  | 43061.5 | 81 | 79
2017-11-22 12:30 | 53 | 53 |  |  | 43061.5208 | 81 | 79
2017-11-22 13:00 | 52 | 52 |  |  | 43061.5417 | 80 | 77
2017-11-22 13:30 | 53 | 53 |  |  | 43061.5625 | 81 | 79
2017-11-22 14:00 | 54 | 54 |  |  | 43061.5833 | 84 | 82
2017-11-22 14:30 | 58 | 58 |  |  | 43061.6042 | 87 | 84
2017-11-22 15:00 | 57 | 57 |  |  | 43061.625 | 82 | 79
2017-11-22 15:30 | 59 | 59 |  |  | 43061.6458 | 87 | 84
2017-11-22 16:00 | 61 | 61 |  |  | 43061.6667 | 91 | 88
2017-11-22 16:30 | 63 | 63 |  |  | 43061.6875 | 92 | 88
2017-11-22 17:00 | 66 | 66 |  |  | 43061.7083 | 92 | 88
2017-11-22 17:30 | 67 | 67 |  |  | 43061.7292 | 92 | 88
2017-11-22 18:00 | 66 | 65 |  |  | 43061.75 | 90 | 85
2017-11-22 18:30 | 66 | 65 |  |  | 43061.7708 | 89 | 84
2017-11-22 19:00 | 67 | 67 |  |  | 43061.7917 | 90 | 85
2017-11-22 19:30 | 65 | 65 |  |  | 43061.8125 | 88 | 83
2017-11-22 20:00 | 63 | 63 |  |  | 43061.8333 | 86 | 81
2017-11-22 20:30 | 60 | 60 |  |  | 43061.8542 | 83 | 78
2017-11-22 21:00 | 58 | 58 |  |  | 43061.875 | 76 | 74
2017-11-22 21:30 | 55 | 55 |  |  | 43061.8958 | 73 | 71
2017-11-22 22:00 | 53 | 53 |  |  | 43061.9167 | 71 | 69
2017-11-22 22:30 | 52 | 52 |  |  | 43061.9375 | 71 | 69
2017-11-22 23:00 | 55 | 55 |  |  | 43061.9583 | 73 | 71
2017-11-22 23:30 | 52 | 52 |  |  | 43061.9792 | 70 | 67
2017-11-23 | 47 | 47 |  |  | 43062 | 65 | 62
2017-11-23 00:30 | 42 | 42 |  |  | 43062.0208 | 60 | 56
2017-11-23 01:00 | 39 | 38 |  |  | 43062.0417 | 55 | 50
2017-11-23 01:30 | 38 | 38 |  |  | 43062.0625 | 54 | 49
2017-11-23 02:00 | 38 | 38 |  |  | 43062.0833 | 53 | 48
2017-11-23 02:30 | 36 | 35 |  |  | 43062.1042 | 54 | 48
2017-11-23 03:00 | 36 | 35 |  |  | 43062.125 | 53 | 47
2017-11-23 03:30 | 36 | 35 |  |  | 43062.1458 | 53 | 47
2017-11-23 04:00 | 36 | 36 |  |  | 43062.1667 | 54 | 48
2017-11-23 04:30 | 37 | 36 |  |  | 43062.1875 | 54 | 49
2017-11-23 05:00 | 38 | 38 |  |  | 43062.2083 | 57 | 51
2017-11-23 05:30 | 41 | 40 |  |  | 43062.2292 | 59 | 55
2017-11-23 06:00 | 44 | 44 |  |  | 43062.25 | 63 | 59
2017-11-23 06:30 | 47 | 47 |  |  | 43062.2708 | 67 | 65
2017-11-23 07:00 | 50 | 50 |  |  | 43062.2917 | 73 | 71
2017-11-23 07:30 | 54 | 54 |  |  | 43062.3125 | 79 | 78
2017-11-23 08:00 | 57 | 56 |  |  | 43062.3333 | 83 | 82
2017-11-23 08:30 | 59 | 59 |  |  | 43062.3542 | 88 | 86
2017-11-23 09:00 | 60 | 60 |  |  | 43062.375 | 89 | 87
2017-11-23 09:30 | 60 | 60 |  |  | 43062.3958 | 90 | 88
2017-11-23 10:00 | 61 | 60 |  |  | 43062.4167 | 89 | 88
2017-11-23 10:30 | 60 | 60 |  |  | 43062.4375 | 87 | 85
2017-11-23 11:00 | 58 | 58 |  |  | 43062.4583 | 86 | 84
2017-11-23 11:30 | 58 | 58 |  |  | 43062.4792 | 85 | 84
2017-11-23 12:00 | 57 | 57 |  |  | 43062.5 | 83 | 81
2017-11-23 12:30 | 58 | 57 |  |  | 43062.5208 | 82 | 80
2017-11-23 13:00 | 57 | 56 |  |  | 43062.5417 | 82 | 79
2017-11-23 13:30 | 55 | 55 |  |  | 43062.5625 | 81 | 79
2017-11-23 14:00 | 56 | 56 |  |  | 43062.5833 | 83 | 81
2017-11-23 14:30 | 57 | 57 |  |  | 43062.6042 | 82 | 80
2017-11-23 15:00 | 54 | 54 |  |  | 43062.625 | 82 | 78
2017-11-23 15:30 | 49 | 49 |  |  | 43062.6458 | 82 | 78
2017-11-23 16:00 | 54 | 54 |  |  | 43062.6667 | 84 | 80
2017-11-23 16:30 | 54 | 54 |  |  | 43062.6875 | 85 | 81
2017-11-23 17:00 | 55 | 55 |  |  | 43062.7083 | 86 | 81
2017-11-23 17:30 | 55 | 55 |  |  | 43062.7292 | 84 | 80
2017-11-23 18:00 | 56 | 56 |  |  | 43062.75 | 84 | 79
2017-11-23 18:30 | 56 | 55 |  |  | 43062.7708 | 83 | 77
2017-11-23 19:00 | 58 | 57 |  |  | 43062.7917 | 86 | 80
2017-11-23 19:30 | 58 | 58 |  |  | 43062.8125 | 84 | 79
2017-11-23 20:00 | 59 | 59 |  |  | 43062.8333 | 83 | 79
2017-11-23 20:30 | 57 | 57 |  |  | 43062.8542 | 82 | 78
2017-11-23 21:00 | 56 | 56 |  |  | 43062.875 | 77 | 75
2017-11-23 21:30 | 51 | 51 |  |  | 43062.8958 | 71 | 69
2017-11-23 22:00 | 47 | 47 |  |  | 43062.9167 | 68 | 65
2017-11-23 22:30 | 45 | 45 |  |  | 43062.9375 | 67 | 65
2017-11-23 23:00 | 47 | 47 |  |  | 43062.9583 | 68 | 65
2017-11-23 23:30 | 48 | 47 |  |  | 43062.9792 | 69 | 65
2017-11-24 | 44 | 44 |  |  | 43063 | 65 | 61
2017-11-24 00:30 | 37 | 37 |  |  | 43063.0208 | 58 | 53
2017-11-24 01:00 | 33 | 32 |  |  | 43063.0417 | 54 | 47
2017-11-24 01:30 | 31 | 31 |  |  | 43063.0625 | 53 | 45
2017-11-24 02:00 | 32 | 32 |  |  | 43063.0833 | 53 | 46
2017-11-24 02:30 | 34 | 32 |  |  | 43063.1042 | 49 | 46
2017-11-24 03:00 | 35 | 32 |  |  | 43063.125 | 47 | 45
2017-11-24 03:30 | 35 | 32 |  |  | 43063.1458 | 47 | 46
2017-11-24 04:00 | 35 | 31 |  |  | 43063.1667 | 48 | 47
2017-11-24 04:30 | 36 | 33 |  |  | 43063.1875 | 49 | 48
2017-11-24 05:00 | 38 | 34 |  |  | 43063.2083 | 51 | 50
2017-11-24 05:30 | 39 | 36 |  |  | 43063.2292 | 54 | 53
2017-11-24 06:00 | 42 | 40 |  |  | 43063.25 | 58 | 57
2017-11-24 06:30 | 45 | 44 |  |  | 43063.2708 | 64 | 64
2017-11-24 07:00 | 47 | 46 |  |  | 43063.2917 | 71 | 71
2017-11-24 07:30 | 48 | 47 |  |  | 43063.3125 | 75 | 75
2017-11-24 08:00 | 49 | 49 |  |  | 43063.3333 | 77 | 76
2017-11-24 08:30 | 53 | 51 |  |  | 43063.3542 | 81 | 80
2017-11-24 09:00 | 54 | 53 |  |  | 43063.375 | 84 | 83
2017-11-24 09:30 | 55 | 54 |  |  | 43063.3958 | 84 | 82
2017-11-24 10:00 | 57 | 55 |  |  | 43063.4167 | 87 | 84
2017-11-24 10:30 | 60 | 56 |  |  | 43063.4375 | 89 | 85
2017-11-24 11:00 | 59 | 55 |  |  | 43063.4583 | 88 | 84
2017-11-24 11:30 | 69 | 55 |  |  | 43063.4792 | 98 | 85
2017-11-24 12:00 | 71 | 56 |  |  | 43063.5 | 98 | 86
2017-11-24 12:30 | 71 | 57 |  |  | 43063.5208 | 97 | 84
2017-11-24 13:00 | 70 | 55 |  |  | 43063.5417 | 97 | 84
2017-11-24 13:30 | 71 | 54 |  |  | 43063.5625 | 98 | 84
2017-11-24 14:00 | 72 | 56 |  |  | 43063.5833 | 97 | 84
2017-11-24 14:30 | 73 | 56 |  |  | 43063.6042 | 98 | 85
2017-11-24 15:00 | 72 | 55 |  |  | 43063.625 | 98 | 86
2017-11-24 15:30 | 74 | 58 |  |  | 43063.6458 | 99 | 87
2017-11-24 16:00 | 76 | 59 |  |  | 43063.6667 | 100 | 88
2017-11-24 16:30 | 78 | 60 |  |  | 43063.6875 | 100 | 90
2017-11-24 17:00 | 82 | 63 |  |  | 43063.7083 | 101 | 92
2017-11-24 17:30 | 82 | 63 |  |  | 43063.7292 | 98 | 90
2017-11-24 18:00 | 86 | 59 |  |  | 43063.75 | 90 | 83
2017-11-24 18:30 | 90 | 56 |  |  | 43063.7708 | 83 | 79
2017-11-24 19:00 | 90 | 57 |  |  | 43063.7917 | 86 | 81
2017-11-24 19:30 | 91 | 57 |  |  | 43063.8125 | 85 | 80
2017-11-24 20:00 | 91 | 56 |  |  | 43063.8333 | 83 | 79
2017-11-24 20:30 | 91 | 57 |  |  | 43063.8542 | 83 | 79
2017-11-24 21:00 | 89 | 55 |  |  | 43063.875 | 81 | 77
2017-11-24 21:30 | 85 | 48 |  |  | 43063.8958 | 73 | 68
2017-11-24 22:00 | 85 | 46 |  |  | 43063.9167 | 72 | 68
2017-11-24 22:30 | 87 | 45 |  |  | 43063.9375 | 70 | 66
2017-11-24 23:00 | 86 | 42 |  |  | 43063.9583 | 65 | 62
2017-11-24 23:30 | 80 | 38 |  |  | 43063.9792 | 60 | 58
2017-11-25 | 65 | 37 |  |  | 43064 | 54 | 54
2017-11-25 00:30 | 64 | 33 |  |  | 43064.0208 | 49 | 49
2017-11-25 01:00 | 65 | 31 |  |  | 43064.0417 | 48 | 48
2017-11-25 01:30 | 66 | 32 |  |  | 43064.0625 | 48 | 48
2017-11-25 02:00 | 66 | 33 |  |  | 43064.0833 | 49 | 48
2017-11-25 02:30 | 65 | 32 |  |  | 43064.1042 | 47 | 47
2017-11-25 03:00 | 66 | 30 |  |  | 43064.125 | 46 | 46
2017-11-25 03:30 | 66 | 30 |  |  | 43064.1458 | 46 | 45
2017-11-25 04:00 | 64 | 30 |  |  | 43064.1667 | 46 | 46
2017-11-25 04:30 | 64 | 30 |  |  | 43064.1875 | 47 | 47
2017-11-25 05:00 | 64 | 31 |  |  | 43064.2083 | 47 | 47
2017-11-25 05:30 | 64 | 31 |  |  | 43064.2292 | 46 | 46
2017-11-25 06:00 | 63 | 29 |  |  | 43064.25 | 46 | 46
2017-11-25 06:30 | 63 | 30 |  |  | 43064.2708 | 49 | 49
2017-11-25 07:00 | 62 | 31 |  |  | 43064.2917 | 51 | 51
2017-11-25 07:30 | 62 | 34 |  |  | 43064.3125 | 54 | 54
2017-11-25 08:00 | 38 | 34 |  |  | 43064.3333 | 55 | 54
2017-11-25 08:30 | 40 | 38 |  |  | 43064.3542 | 60 | 60
2017-11-25 09:00 | 41 | 40 |  |  | 43064.375 | 61 | 61
2017-11-25 09:30 | 42 | 40 |  |  | 43064.3958 | 62 | 61
2017-11-25 10:00 | 44 | 42 |  |  | 43064.4167 | 63 | 62
2017-11-25 10:30 | 42 | 40 |  |  | 43064.4375 | 60 | 59
2017-11-25 11:00 | 43 | 41 |  |  | 43064.4583 | 60 | 59
2017-11-25 11:30 | 44 | 42 |  |  | 43064.4792 | 60 | 60
2017-11-25 12:00 | 44 | 42 |  |  | 43064.5 | 60 | 59
2017-11-25 12:30 | 43 | 40 |  |  | 43064.5208 | 59 | 58
2017-11-25 13:00 | 45 | 43 |  |  | 43064.5417 | 60 | 59
2017-11-25 13:30 | 44 | 42 |  |  | 43064.5625 | 59 | 59
2017-11-25 14:00 | 44 | 42 |  |  | 43064.5833 | 60 | 59
2017-11-25 14:30 | 45 | 43 |  |  | 43064.6042 | 61 | 61
2017-11-25 15:00 | 45 | 43 |  |  | 43064.625 | 63 | 62
2017-11-25 15:30 | 44 | 43 |  |  | 43064.6458 | 61 | 61
2017-11-25 16:00 | 44 | 43 |  |  | 43064.6667 | 60 | 59
2017-11-25 16:30 | 48 | 46 |  |  | 43064.6875 | 65 | 64
2017-11-25 17:00 | 48 | 46 |  |  | 43064.7083 | 66 | 65
2017-11-25 17:30 | 51 | 48 |  |  | 43064.7292 | 68 | 67
2017-11-25 18:00 | 50 | 47 |  |  | 43064.75 | 68 | 67
2017-11-25 18:30 | 50 | 47 |  |  | 43064.7708 | 69 | 68
2017-11-25 19:00 | 52 | 50 |  |  | 43064.7917 | 72 | 71
2017-11-25 19:30 | 53 | 51 |  |  | 43064.8125 | 73 | 72
2017-11-25 20:00 | 52 | 49 |  |  | 43064.8333 | 71 | 69
2017-11-25 20:30 | 50 | 48 |  |  | 43064.8542 | 70 | 68
2017-11-25 21:00 | 49 | 47 |  |  | 43064.875 | 68 | 68
2017-11-25 21:30 | 47 | 45 |  |  | 43064.8958 | 65 | 64
2017-11-25 22:00 | 45 | 43 |  |  | 43064.9167 | 63 | 63
2017-11-25 22:30 | 44 | 41 |  |  | 43064.9375 | 62 | 62
2017-11-25 23:00 | 48 | 45 |  |  | 43064.9583 | 65 | 64
2017-11-25 23:30 | 48 | 45 |  |  | 43064.9792 | 65 | 64
2017-11-26 | 44 | 40 |  |  | 43065 | 61 | 60
2017-11-26 00:30 | 40 | 35 |  |  | 43065.0208 | 56 | 54
2017-11-26 01:00 | 38 | 33 |  |  | 43065.0417 | 53 | 51
2017-11-26 01:30 | 37 | 31 |  |  | 43065.0625 | 50 | 47
2017-11-26 02:00 | 36 | 31 |  |  | 43065.0833 | 49 | 46
2017-11-26 02:30 | 35 | 29 |  |  | 43065.1042 | 48 | 45
2017-11-26 03:00 | 35 | 29 |  |  | 43065.125 | 47 | 44
2017-11-26 03:30 | 35 | 29 |  |  | 43065.1458 | 48 | 44
2017-11-26 04:00 | 34 | 28 |  |  | 43065.1667 | 46 | 43
2017-11-26 04:30 | 34 | 28 |  |  | 43065.1875 | 47 | 43
2017-11-26 05:00 | 34 | 27 |  |  | 43065.2083 | 45 | 41
2017-11-26 05:30 | 31 | 27 |  |  | 43065.2292 | 47 | 41
2017-11-26 06:00 | 27 | 26 |  |  | 43065.25 | 50 | 40
2017-11-26 06:30 | 28 | 26 |  |  | 43065.2708 | 50 | 41
2017-11-26 07:00 | 27 | 26 |  |  | 43065.2917 | 51 | 43
2017-11-26 07:30 | 28 | 27 |  |  | 43065.3125 | 51 | 44
2017-11-26 08:00 | 31 | 30 |  |  | 43065.3333 | 55 | 49
2017-11-26 08:30 | 35 | 34 |  |  | 43065.3542 | 56 | 51
2017-11-26 09:00 | 37 | 37 |  |  | 43065.375 | 57 | 53
2017-11-26 09:30 | 36 | 36 |  |  | 43065.3958 | 58 | 54
2017-11-26 10:00 | 36 | 36 |  |  | 43065.4167 | 59 | 55
2017-11-26 10:30 | 38 | 38 |  |  | 43065.4375 | 60 | 56
2017-11-26 11:00 | 38 | 38 |  |  | 43065.4583 | 58 | 55
2017-11-26 11:30 | 40 | 39 |  |  | 43065.4792 | 58 | 56
2017-11-26 12:00 | 40 | 40 |  |  | 43065.5 | 57 | 54
2017-11-26 12:30 | 40 | 40 |  |  | 43065.5208 | 55 | 52
2017-11-26 13:00 | 37 | 37 |  |  | 43065.5417 | 56 | 53
2017-11-26 13:30 | 39 | 39 |  |  | 43065.5625 | 57 | 54
2017-11-26 14:00 | 40 | 40 |  |  | 43065.5833 | 56 | 53
2017-11-26 14:30 | 39 | 39 |  |  | 43065.6042 | 56 | 53
2017-11-26 15:00 | 41 | 41 |  |  | 43065.625 | 61 | 59
2017-11-26 15:30 | 40 | 40 |  |  | 43065.6458 | 64 | 62
2017-11-26 16:00 | 41 | 41 |  |  | 43065.6667 | 64 | 62
2017-11-26 16:30 | 44 | 44 |  |  | 43065.6875 | 68 | 65
2017-11-26 17:00 | 47 | 47 |  |  | 43065.7083 | 69 | 67
2017-11-26 17:30 | 53 | 53 |  |  | 43065.7292 | 75 | 72
2017-11-26 18:00 | 56 | 56 |  |  | 43065.75 | 78 | 75
2017-11-26 18:30 | 57 | 57 |  |  | 43065.7708 | 82 | 79
2017-11-26 19:00 | 62 | 62 |  |  | 43065.7917 | 86 | 83
2017-11-26 19:30 | 62 | 62 |  |  | 43065.8125 | 85 | 82
2017-11-26 20:00 | 61 | 61 |  |  | 43065.8333 | 83 | 81
2017-11-26 20:30 | 63 | 62 |  |  | 43065.8542 | 86 | 83
2017-11-26 21:00 | 59 | 59 |  |  | 43065.875 | 81 | 79
2017-11-26 21:30 | 57 | 57 |  |  | 43065.8958 | 80 | 77
2017-11-26 22:00 | 56 | 55 |  |  | 43065.9167 | 78 | 75
2017-11-26 22:30 | 53 | 53 |  |  | 43065.9375 | 76 | 73
2017-11-26 23:00 | 54 | 53 |  |  | 43065.9583 | 76 | 71
2017-11-26 23:30 | 52 | 51 |  |  | 43065.9792 | 74 | 69
2017-11-27 | 46 | 46 |  |  | 43066 | 67 | 62
2017-11-27 00:30 | 41 | 41 |  |  | 43066.0208 | 62 | 57
2017-11-27 01:00 | 38 | 37 |  |  | 43066.0417 | 58 | 52
2017-11-27 01:30 | 38 | 37 |  |  | 43066.0625 | 58 | 51
2017-11-27 02:00 | 37 | 36 |  |  | 43066.0833 | 58 | 51
2017-11-27 02:30 | 37 | 35 |  |  | 43066.1042 | 58 | 51
2017-11-27 03:00 | 35 | 34 |  |  | 43066.125 | 57 | 50
2017-11-27 03:30 | 35 | 34 |  |  | 43066.1458 | 56 | 49
2017-11-27 04:00 | 35 | 33 |  |  | 43066.1667 | 55 | 48
2017-11-27 04:30 | 34 | 33 |  |  | 43066.1875 | 56 | 49
2017-11-27 05:00 | 37 | 37 |  |  | 43066.2083 | 57 | 51
2017-11-27 05:30 | 38 | 38 |  |  | 43066.2292 | 60 | 54
2017-11-27 06:00 | 41 | 41 |  |  | 43066.25 | 63 | 58
2017-11-27 06:30 | 46 | 46 |  |  | 43066.2708 | 69 | 66
2017-11-27 07:00 | 50 | 50 |  |  | 43066.2917 | 75 | 74
2017-11-27 07:30 | 55 | 55 |  |  | 43066.3125 | 84 | 83
2017-11-27 08:00 | 58 | 58 |  |  | 43066.3333 | 88 | 87
2017-11-27 08:30 | 63 | 61 |  |  | 43066.3542 | 91 | 90
2017-11-27 09:00 | 64 | 61 |  |  | 43066.375 | 93 | 92
2017-11-27 09:30 | 65 | 62 |  |  | 43066.3958 | 92 | 92
2017-11-27 10:00 | 65 | 62 |  |  | 43066.4167 | 93 | 92
2017-11-27 10:30 | 66 | 63 |  |  | 43066.4375 | 93 | 93
2017-11-27 11:00 | 70 | 67 |  |  | 43066.4583 | 97 | 96
2017-11-27 11:30 | 71 | 68 |  |  | 43066.4792 | 98 | 97
2017-11-27 12:00 | 71 | 68 |  |  | 43066.5 | 98 | 97
2017-11-27 12:30 | 71 | 68 |  |  | 43066.5208 | 98 | 97
2017-11-27 13:00 | 72 | 69 |  |  | 43066.5417 | 98 | 97
2017-11-27 13:30 | 74 | 71 |  |  | 43066.5625 | 98 | 98
2017-11-27 14:00 | 75 | 72 |  |  | 43066.5833 | 97 | 97
2017-11-27 14:30 | 76 | 73 |  |  | 43066.6042 | 99 | 99
2017-11-27 15:00 | 76 | 74 |  |  | 43066.625 | 100 | 100
2017-11-27 15:30 | 74 | 73 |  |  | 43066.6458 | 102 | 99
2017-11-27 16:00 | 75 | 74 |  |  | 43066.6667 | 104 | 100
2017-11-27 16:30 | 76 | 76 |  |  | 43066.6875 | 104 | 101
2017-11-27 17:00 | 77 | 76 |  |  | 43066.7083 | 104 | 100
2017-11-27 17:30 | 76 | 76 |  |  | 43066.7292 | 104 | 99
2017-11-27 18:00 | 75 | 75 |  |  | 43066.75 | 101 | 95
2017-11-27 18:30 | 76 | 75 |  |  | 43066.7708 | 95 | 94
2017-11-27 19:00 | 79 | 77 |  |  | 43066.7917 | 97 | 96
2017-11-27 19:30 | 77 | 75 |  |  | 43066.8125 | 94 | 94
2017-11-27 20:00 | 74 | 73 |  |  | 43066.8333 | 91 | 91
2017-11-27 20:30 | 76 | 73 |  |  | 43066.8542 | 92 | 92
2017-11-27 21:00 | 75 | 71 |  |  | 43066.875 | 88 | 88
2017-11-27 21:30 | 70 | 67 |  |  | 43066.8958 | 83 | 83
2017-11-27 22:00 | 67 | 65 |  |  | 43066.9167 | 82 | 81
2017-11-27 22:30 | 63 | 60 |  |  | 43066.9375 | 77 | 77
2017-11-27 23:00 | 65 | 63 |  |  | 43066.9583 | 78 | 77
2017-11-27 23:30 | 64 | 63 |  |  | 43066.9792 | 78 | 77
2017-11-28 | 59 | 58 |  |  | 43067 | 74 | 73
2017-11-28 00:30 | 55 | 55 |  |  | 43067.0208 | 70 | 69
2017-11-28 01:00 | 52 | 51 |  |  | 43067.0417 | 66 | 65
2017-11-28 01:30 | 50 | 49 |  |  | 43067.0625 | 63 | 62
2017-11-28 02:00 | 49 | 48 |  |  | 43067.0833 | 63 | 61
2017-11-28 02:30 | 51 | 50 |  |  | 43067.1042 | 64 | 62
2017-11-28 03:00 | 50 | 49 |  |  | 43067.125 | 64 | 62
2017-11-28 03:30 | 49 | 48 |  |  | 43067.1458 | 62 | 60
2017-11-28 04:00 | 50 | 49 |  |  | 43067.1667 | 64 | 62
2017-11-28 04:30 | 53 | 52 |  |  | 43067.1875 | 66 | 64
2017-11-28 05:00 | 56 | 55 |  |  | 43067.2083 | 70 | 68
2017-11-28 05:30 | 58 | 57 |  |  | 43067.2292 | 73 | 72
2017-11-28 06:00 | 61 | 60 |  |  | 43067.25 | 77 | 76
2017-11-28 06:30 | 65 | 63 |  |  | 43067.2708 | 83 | 82
2017-11-28 07:00 | 68 | 65 |  |  | 43067.2917 | 88 | 88
2017-11-28 07:30 | 71 | 69 |  |  | 43067.3125 | 97 | 96
2017-11-28 08:00 | 76 | 73 |  |  | 43067.3333 | 101 | 101
2017-11-28 08:30 | 77 | 75 |  |  | 43067.3542 | 104 | 103
2017-11-28 09:00 | 76 | 74 |  |  | 43067.375 | 103 | 103
2017-11-28 09:30 | 77 | 75 |  |  | 43067.3958 | 104 | 103
2017-11-28 10:00 | 77 | 76 |  |  | 43067.4167 | 106 | 105
2017-11-28 10:30 | 79 | 77 |  |  | 43067.4375 | 106 | 104
2017-11-28 11:00 | 80 | 79 |  |  | 43067.4583 | 107 | 106
2017-11-28 11:30 | 78 | 78 |  |  | 43067.4792 | 108 | 107
2017-11-28 12:00 | 81 | 80 |  |  | 43067.5 | 108 | 107
2017-11-28 12:30 | 80 | 79 |  |  | 43067.5208 | 106 | 105
2017-11-28 13:00 | 80 | 79 |  |  | 43067.5417 | 107 | 106
2017-11-28 13:30 | 80 | 79 |  |  | 43067.5625 | 106 | 105
2017-11-28 14:00 | 82 | 81 |  |  | 43067.5833 | 110 | 109
2017-11-28 14:30 | 86 | 85 |  |  | 43067.6042 | 113 | 112
2017-11-28 15:00 | 86 | 85 |  |  | 43067.625 | 113 | 112
2017-11-28 15:30 | 82 | 82 |  |  | 43067.6458 | 108 | 107
2017-11-28 16:00 | 86 | 85 |  |  | 43067.6667 | 110 | 109
2017-11-28 16:30 | 87 | 86 |  |  | 43067.6875 | 113 | 111
2017-11-28 17:00 | 86 | 86 |  |  | 43067.7083 | 112 | 110
2017-11-28 17:30 | 87 | 87 |  |  | 43067.7292 | 111 | 108
2017-11-28 18:00 | 85 | 85 |  |  | 43067.75 | 108 | 105
2017-11-28 18:30 | 83 | 83 |  |  | 43067.7708 | 106 | 104
2017-11-28 19:00 | 86 | 86 |  |  | 43067.7917 | 107 | 106
2017-11-28 19:30 | 84 | 83 |  |  | 43067.8125 | 102 | 102
2017-11-28 20:00 | 82 | 81 |  |  | 43067.8333 | 101 | 101
2017-11-28 20:30 | 80 | 79 |  |  | 43067.8542 | 98 | 98
2017-11-28 21:00 | 76 | 75 |  |  | 43067.875 | 93 | 93
2017-11-28 21:30 | 70 | 68 |  |  | 43067.8958 | 87 | 87
2017-11-28 22:00 | 68 | 67 |  |  | 43067.9167 | 86 | 86
2017-11-28 22:30 | 67 | 65 |  |  | 43067.9375 | 84 | 84
2017-11-28 23:00 | 64 | 63 |  |  | 43067.9583 | 81 | 81
2017-11-28 23:30 | 65 | 64 |  |  | 43067.9792 | 83 | 82
2017-11-29 | 61 | 61 |  |  | 43068 | 78 | 77
2017-11-29 00:30 | 57 | 56 |  |  | 43068.0208 | 73 | 72
2017-11-29 01:00 | 54 | 53 |  |  | 43068.0417 | 70 | 68
2017-11-29 01:30 | 50 | 49 |  |  | 43068.0625 | 65 | 63
2017-11-29 02:00 | 48 | 48 |  |  | 43068.0833 | 63 | 61
2017-11-29 02:30 | 47 | 46 |  |  | 43068.1042 | 62 | 60
2017-11-29 03:00 | 46 | 45 |  |  | 43068.125 | 61 | 59
2017-11-29 03:30 | 46 | 45 |  |  | 43068.1458 | 61 | 59
2017-11-29 04:00 | 44 | 43 |  |  | 43068.1667 | 59 | 57
2017-11-29 04:30 | 45 | 44 |  |  | 43068.1875 | 59 | 57
2017-11-29 05:00 | 48 | 47 |  |  | 43068.2083 | 63 | 61
2017-11-29 05:30 | 52 | 51 |  |  | 43068.2292 | 68 | 66
2017-11-29 06:00 | 58 | 56 |  |  | 43068.25 | 74 | 73
2017-11-29 06:30 | 64 | 62 |  |  | 43068.2708 | 84 | 83
2017-11-29 07:00 | 67 | 65 |  |  | 43068.2917 | 89 | 89
2017-11-29 07:30 | 74 | 71 |  |  | 43068.3125 | 99 | 98
2017-11-29 08:00 | 77 | 76 |  |  | 43068.3333 | 105 | 103
2017-11-29 08:30 | 77 | 76 |  |  | 43068.3542 | 107 | 105
2017-11-29 09:00 | 77 | 75 |  |  | 43068.375 | 105 | 104
2017-11-29 09:30 | 78 | 77 |  |  | 43068.3958 | 106 | 105
2017-11-29 10:00 | 80 | 78 |  |  | 43068.4167 | 106 | 106
2017-11-29 10:30 | 83 | 82 |  |  | 43068.4375 | 110 | 109
2017-11-29 11:00 | 87 | 86 |  |  | 43068.4583 | 114 | 113
2017-11-29 11:30 | 89 | 88 |  |  | 43068.4792 | 116 | 115
2017-11-29 12:00 | 88 | 87 |  |  | 43068.5 | 114 | 113
2017-11-29 12:30 | 87 | 86 |  |  | 43068.5208 | 113 | 112
2017-11-29 13:00 | 87 | 86 |  |  | 43068.5417 | 114 | 112
2017-11-29 13:30 | 86 | 85 |  |  | 43068.5625 | 112 | 111
2017-11-29 14:00 | 83 | 82 |  |  | 43068.5833 | 110 | 109
2017-11-29 14:30 | 84 | 82 |  |  | 43068.6042 | 109 | 108
2017-11-29 15:00 | 82 | 80 |  |  | 43068.625 | 105 | 105
2017-11-29 15:30 | 83 | 81 |  |  | 43068.6458 | 107 | 107
2017-11-29 16:00 | 88 | 86 |  |  | 43068.6667 | 108 | 107
2017-11-29 16:30 | 84 | 82 |  |  | 43068.6875 | 107 | 107
2017-11-29 17:00 | 85 | 83 |  |  | 43068.7083 | 109 | 108
2017-11-29 17:30 | 86 | 84 |  |  | 43068.7292 | 107 | 107
2017-11-29 18:00 | 82 | 80 |  |  | 43068.75 | 102 | 101
2017-11-29 18:30 | 78 | 77 |  |  | 43068.7708 | 97 | 97
2017-11-29 19:00 | 82 | 81 |  |  | 43068.7917 | 101 | 100
2017-11-29 19:30 | 80 | 78 |  |  | 43068.8125 | 98 | 97
2017-11-29 20:00 | 78 | 76 |  |  | 43068.8333 | 95 | 94
2017-11-29 20:30 | 75 | 73 |  |  | 43068.8542 | 90 | 89
2017-11-29 21:00 | 73 | 71 |  |  | 43068.875 | 88 | 87
2017-11-29 21:30 | 68 | 67 |  |  | 43068.8958 | 84 | 82
2017-11-29 22:00 | 65 | 63 |  |  | 43068.9167 | 81 | 79
2017-11-29 22:30 | 61 | 60 |  |  | 43068.9375 | 78 | 76
2017-11-29 23:00 | 61 | 60 |  |  | 43068.9583 | 78 | 75
2017-11-29 23:30 | 59 | 59 |  |  | 43068.9792 | 77 | 74
2017-11-30 | 56 | 56 |  |  | 43069 | 73 | 70
2017-11-30 00:30 | 50 | 49 |  |  | 43069.0208 | 66 | 63
2017-11-30 01:00 | 46 | 45 |  |  | 43069.0417 | 63 | 59
2017-11-30 01:30 | 44 | 44 |  |  | 43069.0625 | 60 | 57
2017-11-30 02:00 | 45 | 45 |  |  | 43069.0833 | 61 | 57
2017-11-30 02:30 | 44 | 43 |  |  | 43069.1042 | 58 | 54
2017-11-30 03:00 | 42 | 41 |  |  | 43069.125 | 58 | 54
2017-11-30 03:30 | 42 | 41 |  |  | 43069.1458 | 57 | 53
2017-11-30 04:00 | 47 | 46 |  |  | 43069.1667 | 63 | 59
2017-11-30 04:30 | 49 | 49 |  |  | 43069.1875 | 65 | 61
2017-11-30 05:00 | 51 | 51 |  |  | 43069.2083 | 67 | 63
2017-11-30 05:30 | 53 | 52 |  |  | 43069.2292 | 69 | 66
2017-11-30 06:00 | 56 | 56 |  |  | 43069.25 | 74 | 71
2017-11-30 06:30 | 61 | 60 |  |  | 43069.2708 | 80 | 79
2017-11-30 07:00 | 65 | 63 |  |  | 43069.2917 | 87 | 87
2017-11-30 07:30 | 69 | 69 |  |  | 43069.3125 | 96 | 96
2017-11-30 08:00 | 74 | 74 |  |  | 43069.3333 | 101 | 100
2017-11-30 08:30 | 75 | 74 |  |  | 43069.3542 | 101 | 101
2017-11-30 09:00 | 75 | 74 |  |  | 43069.375 | 101 | 101
2017-11-30 09:30 | 77 | 77 |  |  | 43069.3958 | 104 | 103
2017-11-30 10:00 | 73 | 73 |  |  | 43069.4167 | 105 | 104
2017-11-30 10:30 | 73 | 72 |  |  | 43069.4375 | 101 | 101
2017-11-30 11:00 | 76 | 75 |  |  | 43069.4583 | 102 | 102
2017-11-30 11:30 | 75 | 74 |  |  | 43069.4792 | 104 | 104
2017-11-30 12:00 | 76 | 75 |  |  | 43069.5 | 104 | 103
2017-11-30 12:30 | 82 | 81 |  |  | 43069.5208 | 106 | 106
2017-11-30 13:00 | 75 | 74 |  |  | 43069.5417 | 101 | 101
2017-11-30 13:30 | 72 | 72 |  |  | 43069.5625 | 101 | 101
2017-11-30 14:00 | 77 | 77 |  |  | 43069.5833 | 102 | 102
2017-11-30 14:30 | 75 | 75 |  |  | 43069.6042 | 100 | 99
2017-11-30 15:00 | 75 | 74 |  |  | 43069.625 | 102 | 101
2017-11-30 15:30 | 76 | 75 |  |  | 43069.6458 | 102 | 101
2017-11-30 16:00 | 77 | 76 |  |  | 43069.6667 | 101 | 101
2017-11-30 16:30 | 79 | 78 |  |  | 43069.6875 | 103 | 102
2017-11-30 17:00 | 80 | 79 |  |  | 43069.7083 | 103 | 102
2017-11-30 17:30 | 80 | 79 |  |  | 43069.7292 | 101 | 100
2017-11-30 18:00 | 79 | 78 |  |  | 43069.75 | 99 | 98
2017-11-30 18:30 | 80 | 79 |  |  | 43069.7708 | 97 | 96
2017-11-30 19:00 | 82 | 81 |  |  | 43069.7917 | 99 | 98
2017-11-30 19:30 | 81 | 80 |  |  | 43069.8125 | 98 | 97
2017-11-30 20:00 | 81 | 79 |  |  | 43069.8333 | 97 | 96
2017-11-30 20:30 | 80 | 79 |  |  | 43069.8542 | 97 | 96
2017-11-30 21:00 | 77 | 76 |  |  | 43069.875 | 92 | 91
2017-11-30 21:30 | 68 | 67 |  |  | 43069.8958 | 82 | 82
2017-11-30 22:00 | 63 | 62 |  |  | 43069.9167 | 79 | 79
2017-11-30 22:30 | 62 | 61 |  |  | 43069.9375 | 77 | 77
2017-11-30 23:00 | 62 | 61 |  |  | 43069.9583 | 76 | 76
2017-11-30 23:30 | 59 | 57 |  |  | 43069.9792 | 73 | 72
2017-12-01 | 53 | 50 |  |  | 43070 | 66 | 65
2017-12-01 00:30 | 50 | 47 |  |  | 43070.0208 | 61 | 60
2017-12-01 01:00 | 48 | 44 |  |  | 43070.0417 | 58 | 57
2017-12-01 01:30 | 47 | 43 |  |  | 43070.0625 | 58 | 56
2017-12-01 02:00 | 47 | 42 |  |  | 43070.0833 | 57 | 55
2017-12-01 02:30 | 44 | 40 |  |  | 43070.1042 | 53 | 51
2017-12-01 03:00 | 44 | 40 |  |  | 43070.125 | 54 | 52
2017-12-01 03:30 | 45 | 40 |  |  | 43070.1458 | 55 | 53
2017-12-01 04:00 | 44 | 40 |  |  | 43070.1667 | 54 | 52
2017-12-01 04:30 | 43 | 39 |  |  | 43070.1875 | 54 | 52
2017-12-01 05:00 | 45 | 41 |  |  | 43070.2083 | 57 | 55
2017-12-01 05:30 | 48 | 45 |  |  | 43070.2292 | 61 | 60
2017-12-01 06:00 | 50 | 48 |  |  | 43070.25 | 65 | 64
2017-12-01 06:30 | 53 | 52 |  |  | 43070.2708 | 73 | 72
2017-12-01 07:00 | 57 | 57 |  |  | 43070.2917 | 81 | 81
2017-12-01 07:30 | 61 | 61 |  |  | 43070.3125 | 89 | 89
2017-12-01 08:00 | 63 | 63 |  |  | 43070.3333 | 92 | 92
2017-12-01 08:30 | 63 | 63 |  |  | 43070.3542 | 91 | 91
2017-12-01 09:00 | 66 | 65 |  |  | 43070.375 | 95 | 95
2017-12-01 09:30 | 67 | 66 |  |  | 43070.3958 | 95 | 95
2017-12-01 10:00 | 69 | 69 |  |  | 43070.4167 | 97 | 97
2017-12-01 10:30 | 68 | 67 |  |  | 43070.4375 | 93 | 92
2017-12-01 11:00 | 69 | 68 |  |  | 43070.4583 | 95 | 95
2017-12-01 11:30 | 72 | 71 |  |  | 43070.4792 | 97 | 96
2017-12-01 12:00 | 76 | 75 |  |  | 43070.5 | 100 | 99
2017-12-01 12:30 | 77 | 77 |  |  | 43070.5208 | 102 | 101
2017-12-01 13:00 | 79 | 78 |  |  | 43070.5417 | 102 | 101
2017-12-01 13:30 | 79 | 78 |  |  | 43070.5625 | 101 | 100
2017-12-01 14:00 | 77 | 76 |  |  | 43070.5833 | 100 | 100
2017-12-01 14:30 | 78 | 77 |  |  | 43070.6042 | 99 | 98
2017-12-01 15:00 | 77 | 76 |  |  | 43070.625 | 99 | 99
2017-12-01 15:30 | 75 | 74 |  |  | 43070.6458 | 99 | 98
2017-12-01 16:00 | 75 | 74 |  |  | 43070.6667 | 99 | 98
2017-12-01 16:30 | 73 | 72 |  |  | 43070.6875 | 98 | 97
2017-12-01 17:00 | 74 | 73 |  |  | 43070.7083 | 99 | 97
2017-12-01 17:30 | 74 | 72 |  |  | 43070.7292 | 98 | 97
2017-12-01 18:00 | 70 | 68 |  |  | 43070.75 | 92 | 91
2017-12-01 18:30 | 68 | 66 |  |  | 43070.7708 | 88 | 87
2017-12-01 19:00 | 69 | 68 |  |  | 43070.7917 | 90 | 89
2017-12-01 19:30 | 67 | 67 |  |  | 43070.8125 | 87 | 87
2017-12-01 20:00 | 66 | 66 |  |  | 43070.8333 | 86 | 86
2017-12-01 20:30 | 67 | 67 |  |  | 43070.8542 | 86 | 86
2017-12-01 21:00 | 66 | 65 |  |  | 43070.875 | 84 | 84
2017-12-01 21:30 | 64 | 63 |  |  | 43070.8958 | 81 | 80
2017-12-01 22:00 | 61 | 60 |  |  | 43070.9167 | 79 | 79
2017-12-01 22:30 | 59 | 58 |  |  | 43070.9375 | 77 | 76
2017-12-01 23:00 | 57 | 56 |  |  | 43070.9583 | 73 | 72
2017-12-01 23:30 | 52 | 50 |  |  | 43070.9792 | 69 | 68
2017-12-02 | 50 | 48 |  |  | 43071 | 66 | 65
2017-12-02 00:30 | 46 | 42 |  |  | 43071.0208 | 59 | 57
2017-12-02 01:00 | 42 | 38 |  |  | 43071.0417 | 55 | 53
2017-12-02 01:30 | 41 | 37 |  |  | 43071.0625 | 53 | 52
2017-12-02 02:00 | 43 | 39 |  |  | 43071.0833 | 54 | 52
2017-12-02 02:30 | 43 | 39 |  |  | 43071.1042 | 54 | 52
2017-12-02 03:00 | 42 | 40 |  |  | 43071.125 | 57 | 53
2017-12-02 03:30 | 42 | 42 |  |  | 43071.1458 | 60 | 53
2017-12-02 04:00 | 42 | 41 |  |  | 43071.1667 | 59 | 53
2017-12-02 04:30 | 41 | 40 |  |  | 43071.1875 | 59 | 53
2017-12-02 05:00 | 39 | 39 |  |  | 43071.2083 | 58 | 51
2017-12-02 05:30 | 38 | 37 |  |  | 43071.2292 | 57 | 50
2017-12-02 06:00 | 37 | 36 |  |  | 43071.25 | 56 | 49
2017-12-02 06:30 | 39 | 38 |  |  | 43071.2708 | 57 | 52
2017-12-02 07:00 | 40 | 40 |  |  | 43071.2917 | 59 | 55
2017-12-02 07:30 | 43 | 43 |  |  | 43071.3125 | 61 | 58
2017-12-02 08:00 | 44 | 44 |  |  | 43071.3333 | 63 | 60
2017-12-02 08:30 | 47 | 47 |  |  | 43071.3542 | 67 | 65
2017-12-02 09:00 | 47 | 47 |  |  | 43071.375 | 72 | 70
2017-12-02 09:30 | 48 | 48 |  |  | 43071.3958 | 69 | 68
2017-12-02 10:00 | 48 | 48 |  |  | 43071.4167 | 69 | 68
2017-12-02 10:30 | 54 | 54 |  |  | 43071.4375 | 74 | 72
2017-12-02 11:00 | 56 | 56 |  |  | 43071.4583 | 75 | 74
2017-12-02 11:30 | 54 | 54 |  |  | 43071.4792 | 74 | 73
2017-12-02 12:00 | 51 | 51 |  |  | 43071.5 | 74 | 73
2017-12-02 12:30 | 50 | 50 |  |  | 43071.5208 | 72 | 70
2017-12-02 13:00 | 50 | 50 |  |  | 43071.5417 | 71 | 70
2017-12-02 13:30 | 50 | 50 |  |  | 43071.5625 | 73 | 71
2017-12-02 14:00 | 56 | 56 |  |  | 43071.5833 | 76 | 74
2017-12-02 14:30 | 64 | 64 |  |  | 43071.6042 | 83 | 81
2017-12-02 15:00 | 61 | 61 |  |  | 43071.625 | 83 | 81
2017-12-02 15:30 | 58 | 57 |  |  | 43071.6458 | 81 | 79
2017-12-02 16:00 | 60 | 60 |  |  | 43071.6667 | 82 | 80
2017-12-02 16:30 | 63 | 63 |  |  | 43071.6875 | 86 | 84
2017-12-02 17:00 | 63 | 63 |  |  | 43071.7083 | 87 | 85
2017-12-02 17:30 | 64 | 64 |  |  | 43071.7292 | 87 | 85
2017-12-02 18:00 | 63 | 63 |  |  | 43071.75 | 86 | 84
2017-12-02 18:30 | 62 | 62 |  |  | 43071.7708 | 85 | 82
2017-12-02 19:00 | 66 | 66 |  |  | 43071.7917 | 89 | 87
2017-12-02 19:30 | 66 | 66 |  |  | 43071.8125 | 89 | 86
2017-12-02 20:00 | 65 | 65 |  |  | 43071.8333 | 88 | 85
2017-12-02 20:30 | 63 | 63 |  |  | 43071.8542 | 87 | 84
2017-12-02 21:00 | 61 | 61 |  |  | 43071.875 | 82 | 80
2017-12-02 21:30 | 59 | 59 |  |  | 43071.8958 | 81 | 78
2017-12-02 22:00 | 59 | 59 |  |  | 43071.9167 | 81 | 78
2017-12-02 22:30 | 57 | 56 |  |  | 43071.9375 | 79 | 76
2017-12-02 23:00 | 59 | 58 |  |  | 43071.9583 | 81 | 77
2017-12-02 23:30 | 56 | 56 |  |  | 43071.9792 | 78 | 74
2017-12-03 | 52 | 51 |  |  | 43072 | 73 | 69
2017-12-03 00:30 | 46 | 46 |  |  | 43072.0208 | 67 | 62
2017-12-03 01:00 | 44 | 43 |  |  | 43072.0417 | 63 | 58
2017-12-03 01:30 | 42 | 42 |  |  | 43072.0625 | 61 | 56
2017-12-03 02:00 | 41 | 40 |  |  | 43072.0833 | 61 | 56
2017-12-03 02:30 | 41 | 40 |  |  | 43072.1042 | 61 | 55
2017-12-03 03:00 | 41 | 41 |  |  | 43072.125 | 60 | 54
2017-12-03 03:30 | 40 | 40 |  |  | 43072.1458 | 59 | 54
2017-12-03 04:00 | 41 | 40 |  |  | 43072.1667 | 60 | 54
2017-12-03 04:30 | 41 | 40 |  |  | 43072.1875 | 61 | 54
2017-12-03 05:00 | 43 | 42 |  |  | 43072.2083 | 62 | 55
2017-12-03 05:30 | 41 | 40 |  |  | 43072.2292 | 62 | 55
2017-12-03 06:00 | 40 | 39 |  |  | 43072.25 | 60 | 55
2017-12-03 06:30 | 38 | 37 |  |  | 43072.2708 | 58 | 53
2017-12-03 07:00 | 36 | 35 |  |  | 43072.2917 | 58 | 53
2017-12-03 07:30 | 40 | 40 |  |  | 43072.3125 | 61 | 57
2017-12-03 08:00 | 42 | 41 |  |  | 43072.3333 | 64 | 61
2017-12-03 08:30 | 43 | 43 |  |  | 43072.3542 | 66 | 64
2017-12-03 09:00 | 46 | 46 |  |  | 43072.375 | 67 | 64
2017-12-03 09:30 | 49 | 49 |  |  | 43072.3958 | 69 | 67
2017-12-03 10:00 | 50 | 49 |  |  | 43072.4167 | 70 | 68
2017-12-03 10:30 | 51 | 51 |  |  | 43072.4375 | 68 | 66
2017-12-03 11:00 | 56 | 56 |  |  | 43072.4583 | 73 | 71
2017-12-03 11:30 | 56 | 56 |  |  | 43072.4792 | 77 | 75
2017-12-03 12:00 | 59 | 59 |  |  | 43072.5 | 77 | 75
2017-12-03 12:30 | 62 | 62 |  |  | 43072.5208 | 83 | 81
2017-12-03 13:00 | 68 | 68 |  |  | 43072.5417 | 89 | 87
2017-12-03 13:30 | 70 | 70 |  |  | 43072.5625 | 90 | 89
2017-12-03 14:00 | 68 | 68 |  |  | 43072.5833 | 90 | 88
2017-12-03 14:30 | 67 | 67 |  |  | 43072.6042 | 86 | 84
2017-12-03 15:00 | 66 | 66 |  |  | 43072.625 | 87 | 86
2017-12-03 15:30 | 66 | 66 |  |  | 43072.6458 | 86 | 84
2017-12-03 16:00 | 69 | 69 |  |  | 43072.6667 | 87 | 85
2017-12-03 16:30 | 71 | 71 |  |  | 43072.6875 | 91 | 88
2017-12-03 17:00 | 72 | 71 |  |  | 43072.7083 | 99 | 92
2017-12-03 17:30 | 72 | 70 |  |  | 43072.7292 | 101 | 89
2017-12-03 18:00 | 68 | 66 |  |  | 43072.75 | 97 | 85
2017-12-03 18:30 | 66 | 64 |  |  | 43072.7708 | 95 | 83
2017-12-03 19:00 | 66 | 64 |  |  | 43072.7917 | 97 | 84
2017-12-03 19:30 | 66 | 64 |  |  | 43072.8125 | 96 | 84
2017-12-03 20:00 | 65 | 62 |  |  | 43072.8333 | 95 | 82
2017-12-03 20:30 | 64 | 62 |  |  | 43072.8542 | 93 | 82
2017-12-03 21:00 | 62 | 60 |  |  | 43072.875 | 90 | 79
2017-12-03 21:30 | 59 | 58 |  |  | 43072.8958 | 87 | 76
2017-12-03 22:00 | 55 | 55 |  |  | 43072.9167 | 77 | 74
2017-12-03 22:30 | 54 | 54 |  |  | 43072.9375 | 76 | 73
2017-12-03 23:00 | 55 | 55 |  |  | 43072.9583 | 77 | 73
2017-12-03 23:30 | 53 | 53 |  |  | 43072.9792 | 73 | 70
2017-12-04 | 48 | 48 |  |  | 43073 | 67 | 63
2017-12-04 00:30 | 42 | 42 |  |  | 43073.0208 | 61 | 57
2017-12-04 01:00 | 39 | 39 |  |  | 43073.0417 | 57 | 52
2017-12-04 01:30 | 38 | 37 |  |  | 43073.0625 | 57 | 52
2017-12-04 02:00 | 37 | 36 |  |  | 43073.0833 | 56 | 51
2017-12-04 02:30 | 35 | 34 |  |  | 43073.1042 | 54 | 48
2017-12-04 03:00 | 33 | 32 |  |  | 43073.125 | 53 | 47
2017-12-04 03:30 | 33 | 33 |  |  | 43073.1458 | 53 | 47
2017-12-04 04:00 | 33 | 32 |  |  | 43073.1667 | 52 | 46
2017-12-04 04:30 | 35 | 34 |  |  | 43073.1875 | 54 | 48
2017-12-04 05:00 | 38 | 38 |  |  | 43073.2083 | 57 | 51
2017-12-04 05:30 | 40 | 40 |  |  | 43073.2292 | 60 | 55
2017-12-04 06:00 | 44 | 44 |  |  | 43073.25 | 65 | 61
2017-12-04 06:30 | 49 | 49 |  |  | 43073.2708 | 72 | 69
2017-12-04 07:00 | 54 | 54 |  |  | 43073.2917 | 77 | 76
2017-12-04 07:30 | 59 | 59 |  |  | 43073.3125 | 85 | 84
2017-12-04 08:00 | 64 | 64 |  |  | 43073.3333 | 93 | 91
2017-12-04 08:30 | 64 | 64 |  |  | 43073.3542 | 93 | 92
2017-12-04 09:00 | 67 | 67 |  |  | 43073.375 | 98 | 97
2017-12-04 09:30 | 71 | 71 |  |  | 43073.3958 | 98 | 97
2017-12-04 10:00 | 72 | 72 |  |  | 43073.4167 | 103 | 101
2017-12-04 10:30 | 76 | 76 |  |  | 43073.4375 | 105 | 103
2017-12-04 11:00 | 81 | 81 |  |  | 43073.4583 | 109 | 107
2017-12-04 11:30 | 84 | 84 |  |  | 43073.4792 | 113 | 111
2017-12-04 12:00 | 85 | 84 |  |  | 43073.5 | 116 | 111
2017-12-04 12:30 | 82 | 81 |  |  | 43073.5208 | 114 | 107
2017-12-04 13:00 | 79 | 79 |  |  | 43073.5417 | 110 | 104
2017-12-04 13:30 | 79 | 79 |  |  | 43073.5625 | 107 | 103
2017-12-04 14:00 | 78 | 78 |  |  | 43073.5833 | 105 | 102
2017-12-04 14:30 | 76 | 76 |  |  | 43073.6042 | 105 | 101
2017-12-04 15:00 | 72 | 72 |  |  | 43073.625 | 102 | 98
2017-12-04 15:30 | 71 | 70 |  |  | 43073.6458 | 100 | 94
2017-12-04 16:00 | 71 | 71 |  |  | 43073.6667 | 101 | 95
2017-12-04 16:30 | 73 | 72 |  |  | 43073.6875 | 101 | 95
2017-12-04 17:00 | 73 | 73 |  |  | 43073.7083 | 100 | 96
2017-12-04 17:30 | 70 | 70 |  |  | 43073.7292 | 95 | 92
2017-12-04 18:00 | 68 | 68 |  |  | 43073.75 | 92 | 87
2017-12-04 18:30 | 65 | 65 |  |  | 43073.7708 | 88 | 82
2017-12-04 19:00 | 67 | 67 |  |  | 43073.7917 | 90 | 85
2017-12-04 19:30 | 69 | 68 |  |  | 43073.8125 | 90 | 85
2017-12-04 20:00 | 68 | 68 |  |  | 43073.8333 | 88 | 83
2017-12-04 20:30 | 66 | 66 |  |  | 43073.8542 | 85 | 83
2017-12-04 21:00 | 63 | 63 |  |  | 43073.875 | 80 | 78
2017-12-04 21:30 | 57 | 57 |  |  | 43073.8958 | 74 | 72
2017-12-04 22:00 | 55 | 55 |  |  | 43073.9167 | 73 | 71
2017-12-04 22:30 | 54 | 53 |  |  | 43073.9375 | 71 | 69
2017-12-04 23:00 | 53 | 53 |  |  | 43073.9583 | 70 | 67
2017-12-04 23:30 | 50 | 50 |  |  | 43073.9792 | 67 | 64
2017-12-05 | 45 | 45 |  |  | 43074 | 62 | 58
2017-12-05 00:30 | 40 | 40 |  |  | 43074.0208 | 57 | 52
2017-12-05 01:00 | 37 | 37 |  |  | 43074.0417 | 53 | 47
2017-12-05 01:30 | 34 | 34 |  |  | 43074.0625 | 50 | 44
2017-12-05 02:00 | 36 | 35 |  |  | 43074.0833 | 51 | 44
2017-12-05 02:30 | 37 | 37 |  |  | 43074.1042 | 54 | 47
2017-12-05 03:00 | 37 | 37 |  |  | 43074.125 | 54 | 47
2017-12-05 03:30 | 36 | 35 |  |  | 43074.1458 | 52 | 45
2017-12-05 04:00 | 34 | 34 |  |  | 43074.1667 | 52 | 44
2017-12-05 04:30 | 35 | 35 |  |  | 43074.1875 | 53 | 46
2017-12-05 05:00 | 37 | 36 |  |  | 43074.2083 | 55 | 48
2017-12-05 05:30 | 39 | 38 |  |  | 43074.2292 | 57 | 51
2017-12-05 06:00 | 41 | 41 |  |  | 43074.25 | 58 | 54
2017-12-05 06:30 | 43 | 43 |  |  | 43074.2708 | 63 | 61
2017-12-05 07:00 | 51 | 50 |  |  | 43074.2917 | 69 | 69
2017-12-05 07:30 | 56 | 54 |  |  | 43074.3125 | 78 | 77
2017-12-05 08:00 | 61 | 60 |  |  | 43074.3333 | 84 | 84
2017-12-05 08:30 | 66 | 65 |  |  | 43074.3542 | 94 | 93
2017-12-05 09:00 | 68 | 67 |  |  | 43074.375 | 94 | 93
2017-12-05 09:30 | 59 | 59 |  |  | 43074.3958 | 85 | 84
2017-12-05 10:00 | 58 | 58 |  |  | 43074.4167 | 87 | 87
2017-12-05 10:30 | 63 | 62 |  |  | 43074.4375 | 89 | 89
2017-12-05 11:00 | 60 | 59 |  |  | 43074.4583 | 85 | 84
2017-12-05 11:30 | 52 | 52 |  |  | 43074.4792 | 78 | 77
2017-12-05 12:00 | 57 | 56 |  |  | 43074.5 | 84 | 84
2017-12-05 12:30 | 61 | 60 |  |  | 43074.5208 | 87 | 86
2017-12-05 13:00 | 62 | 61 |  |  | 43074.5417 | 87 | 86
2017-12-05 13:30 | 64 | 64 |  |  | 43074.5625 | 90 | 90
2017-12-05 14:00 | 67 | 67 |  |  | 43074.5833 | 94 | 93
2017-12-05 14:30 | 69 | 68 |  |  | 43074.6042 | 95 | 95
2017-12-05 15:00 | 73 | 73 |  |  | 43074.625 | 103 | 102
2017-12-05 15:30 | 78 | 78 |  |  | 43074.6458 | 105 | 103
2017-12-05 16:00 | 77 | 77 |  |  | 43074.6667 | 103 | 102
2017-12-05 16:30 | 72 | 72 |  |  | 43074.6875 | 98 | 96
2017-12-05 17:00 | 69 | 69 |  |  | 43074.7083 | 95 | 93
2017-12-05 17:30 | 72 | 72 |  |  | 43074.7292 | 97 | 94
2017-12-05 18:00 | 72 | 72 |  |  | 43074.75 | 94 | 91
2017-12-05 18:30 | 71 | 71 |  |  | 43074.7708 | 89 | 88
2017-12-05 19:00 | 72 | 71 |  |  | 43074.7917 | 91 | 90
2017-12-05 19:30 | 73 | 73 |  |  | 43074.8125 | 92 | 90
2017-12-05 20:00 | 71 | 70 |  |  | 43074.8333 | 90 | 87
2017-12-05 20:30 | 70 | 69 |  |  | 43074.8542 | 86 | 86
2017-12-05 21:00 | 66 | 65 |  |  | 43074.875 | 82 | 81
2017-12-05 21:30 | 61 | 60 |  |  | 43074.8958 | 77 | 77
2017-12-05 22:00 | 59 | 58 |  |  | 43074.9167 | 75 | 74
2017-12-05 22:30 | 54 | 54 |  |  | 43074.9375 | 72 | 71
2017-12-05 23:00 | 55 | 55 |  |  | 43074.9583 | 72 | 71
2017-12-05 23:30 | 55 | 55 |  |  | 43074.9792 | 73 | 70
2017-12-06 | 50 | 50 |  |  | 43075 | 68 | 64
2017-12-06 00:30 | 45 | 45 |  |  | 43075.0208 | 62 | 58
2017-12-06 01:00 | 40 | 40 |  |  | 43075.0417 | 57 | 52
2017-12-06 01:30 | 39 | 38 |  |  | 43075.0625 | 55 | 49
2017-12-06 02:00 | 37 | 37 |  |  | 43075.0833 | 53 | 47
2017-12-06 02:30 | 36 | 36 |  |  | 43075.1042 | 53 | 47
2017-12-06 03:00 | 34 | 34 |  |  | 43075.125 | 51 | 44
2017-12-06 03:30 | 34 | 34 |  |  | 43075.1458 | 50 | 44
2017-12-06 04:00 | 35 | 34 |  |  | 43075.1667 | 52 | 47
2017-12-06 04:30 | 37 | 37 |  |  | 43075.1875 | 54 | 49
2017-12-06 05:00 | 39 | 39 |  |  | 43075.2083 | 56 | 52
2017-12-06 05:30 | 40 | 40 |  |  | 43075.2292 | 58 | 55
2017-12-06 06:00 | 44 | 44 |  |  | 43075.25 | 62 | 59
2017-12-06 06:30 | 47 | 47 |  |  | 43075.2708 | 68 | 66
2017-12-06 07:00 | 48 | 48 |  |  | 43075.2917 | 72 | 68
2017-12-06 07:30 | 51 | 51 |  |  | 43075.3125 | 77 | 74
2017-12-06 08:00 | 52 | 52 |  |  | 43075.3333 | 78 | 77
2017-12-06 08:30 | 52 | 51 |  |  | 43075.3542 | 78 | 77
2017-12-06 09:00 | 51 | 51 |  |  | 43075.375 | 78 | 76
2017-12-06 09:30 | 51 | 51 |  |  | 43075.3958 | 77 | 76
2017-12-06 10:00 | 54 | 54 |  |  | 43075.4167 | 79 | 77
2017-12-06 10:30 | 59 | 59 |  |  | 43075.4375 | 85 | 83
2017-12-06 11:00 | 58 | 57 |  |  | 43075.4583 | 84 | 83
2017-12-06 11:30 | 58 | 58 |  |  | 43075.4792 | 83 | 83
2017-12-06 12:00 | 59 | 59 |  |  | 43075.5 | 84 | 83
2017-12-06 12:30 | 62 | 62 |  |  | 43075.5208 | 88 | 87
2017-12-06 13:00 | 62 | 62 |  |  | 43075.5417 | 90 | 89
2017-12-06 13:30 | 66 | 66 |  |  | 43075.5625 | 92 | 90
2017-12-06 14:00 | 68 | 68 |  |  | 43075.5833 | 95 | 93
2017-12-06 14:30 | 70 | 70 |  |  | 43075.6042 | 97 | 96
2017-12-06 15:00 | 72 | 72 |  |  | 43075.625 | 100 | 99
2017-12-06 15:30 | 74 | 74 |  |  | 43075.6458 | 104 | 100
2017-12-06 16:00 | 78 | 78 |  |  | 43075.6667 | 107 | 103
2017-12-06 16:30 | 81 | 81 |  |  | 43075.6875 | 109 | 106
2017-12-06 17:00 | 84 | 83 |  |  | 43075.7083 | 112 | 108
2017-12-06 17:30 | 82 | 82 |  |  | 43075.7292 | 110 | 105
2017-12-06 18:00 | 77 | 77 |  |  | 43075.75 | 104 | 97
2017-12-06 18:30 | 74 | 73 |  |  | 43075.7708 | 96 | 92
2017-12-06 19:00 | 77 | 77 |  |  | 43075.7917 | 97 | 95
2017-12-06 19:30 | 77 | 77 |  |  | 43075.8125 | 98 | 95
2017-12-06 20:00 | 77 | 76 |  |  | 43075.8333 | 97 | 93
2017-12-06 20:30 | 74 | 74 |  |  | 43075.8542 | 95 | 91
2017-12-06 21:00 | 72 | 72 |  |  | 43075.875 | 91 | 88
2017-12-06 21:30 | 68 | 68 |  |  | 43075.8958 | 86 | 82
2017-12-06 22:00 | 65 | 65 |  |  | 43075.9167 | 84 | 81
2017-12-06 22:30 | 63 | 63 |  |  | 43075.9375 | 81 | 79
2017-12-06 23:00 | 64 | 64 |  |  | 43075.9583 | 81 | 80
2017-12-06 23:30 | 61 | 61 |  |  | 43075.9792 | 78 | 76
2017-12-07 | 55 | 55 |  |  | 43076 | 72 | 70
2017-12-07 00:30 | 48 | 48 |  |  | 43076.0208 | 64 | 61
2017-12-07 01:00 | 43 | 43 |  |  | 43076.0417 | 57 | 54
2017-12-07 01:30 | 41 | 41 |  |  | 43076.0625 | 54 | 51
2017-12-07 02:00 | 40 | 39 |  |  | 43076.0833 | 54 | 50
2017-12-07 02:30 | 38 | 38 |  |  | 43076.1042 | 53 | 49
2017-12-07 03:00 | 37 | 36 |  |  | 43076.125 | 52 | 47
2017-12-07 03:30 | 35 | 35 |  |  | 43076.1458 | 51 | 46
2017-12-07 04:00 | 35 | 34 |  |  | 43076.1667 | 51 | 46
2017-12-07 04:30 | 36 | 36 |  |  | 43076.1875 | 51 | 46
2017-12-07 05:00 | 37 | 37 |  |  | 43076.2083 | 53 | 48
2017-12-07 05:30 | 41 | 41 |  |  | 43076.2292 | 58 | 53
2017-12-07 06:00 | 45 | 45 |  |  | 43076.25 | 61 | 58
2017-12-07 06:30 | 48 | 48 |  |  | 43076.2708 | 66 | 64
2017-12-07 07:00 | 52 | 51 |  |  | 43076.2917 | 72 | 70
2017-12-07 07:30 | 56 | 56 |  |  | 43076.3125 | 79 | 78
2017-12-07 08:00 | 59 | 59 |  |  | 43076.3333 | 84 | 83
2017-12-07 08:30 | 60 | 60 |  |  | 43076.3542 | 88 | 86
2017-12-07 09:00 | 61 | 60 |  |  | 43076.375 | 89 | 86
2017-12-07 09:30 | 59 | 59 |  |  | 43076.3958 | 87 | 84
2017-12-07 10:00 | 60 | 60 |  |  | 43076.4167 | 87 | 85
2017-12-07 10:30 | 60 | 60 |  |  | 43076.4375 | 87 | 85
2017-12-07 11:00 | 59 | 59 |  |  | 43076.4583 | 85 | 83
2017-12-07 11:30 | 57 | 57 |  |  | 43076.4792 | 85 | 83
2017-12-07 12:00 | 58 | 58 |  |  | 43076.5 | 85 | 83
2017-12-07 12:30 | 59 | 58 |  |  | 43076.5208 | 85 | 84
2017-12-07 13:00 | 61 | 61 |  |  | 43076.5417 | 87 | 86
2017-12-07 13:30 | 64 | 64 |  |  | 43076.5625 | 90 | 89
2017-12-07 14:00 | 66 | 65 |  |  | 43076.5833 | 92 | 91
2017-12-07 14:30 | 69 | 68 |  |  | 43076.6042 | 94 | 93
2017-12-07 15:00 | 70 | 69 |  |  | 43076.625 | 96 | 94
2017-12-07 15:30 | 70 | 70 |  |  | 43076.6458 | 98 | 95
2017-12-07 16:00 | 72 | 72 |  |  | 43076.6667 | 108 | 97
2017-12-07 16:30 | 74 | 73 |  |  | 43076.6875 | 109 | 98
2017-12-07 17:00 | 75 | 74 |  |  | 43076.7083 | 111 | 100
2017-12-07 17:30 | 72 | 71 |  |  | 43076.7292 | 107 | 95
2017-12-07 18:00 | 69 | 69 |  |  | 43076.75 | 107 | 91
2017-12-07 18:30 | 67 | 66 |  |  | 43076.7708 | 105 | 86
2017-12-07 19:00 | 68 | 68 |  |  | 43076.7917 | 106 | 89
2017-12-07 19:30 | 71 | 71 |  |  | 43076.8125 | 107 | 91
2017-12-07 20:00 | 72 | 70 |  |  | 43076.8333 | 93 | 88
2017-12-07 20:30 | 71 | 68 |  |  | 43076.8542 | 91 | 88
2017-12-07 21:00 | 72 | 67 |  |  | 43076.875 | 86 | 85
2017-12-07 21:30 | 67 | 62 |  |  | 43076.8958 | 80 | 79
2017-12-07 22:00 | 64 | 59 |  |  | 43076.9167 | 78 | 77
2017-12-07 22:30 | 62 | 57 |  |  | 43076.9375 | 78 | 76
2017-12-07 23:00 | 61 | 58 |  |  | 43076.9583 | 78 | 75
2017-12-07 23:30 | 55 | 51 |  |  | 43076.9792 | 71 | 68
2017-12-08 | 53 | 47 |  |  | 43077 | 67 | 64
2017-12-08 00:30 | 52 | 45 |  |  | 43077.0208 | 64 | 62
2017-12-08 01:00 | 51 | 44 |  |  | 43077.0417 | 61 | 58
2017-12-08 01:30 | 49 | 42 |  |  | 43077.0625 | 58 | 54
2017-12-08 02:00 | 49 | 41 |  |  | 43077.0833 | 59 | 55
2017-12-08 02:30 | 50 | 42 |  |  | 43077.1042 | 59 | 55
2017-12-08 03:00 | 48 | 40 |  |  | 43077.125 | 56 | 52
2017-12-08 03:30 | 48 | 39 |  |  | 43077.1458 | 56 | 52
2017-12-08 04:00 | 48 | 39 |  |  | 43077.1667 | 56 | 52
2017-12-08 04:30 | 50 | 42 |  |  | 43077.1875 | 58 | 54
2017-12-08 05:00 | 51 | 43 |  |  | 43077.2083 | 60 | 56
2017-12-08 05:30 | 53 | 45 |  |  | 43077.2292 | 63 | 59
2017-12-08 06:00 | 55 | 47 |  |  | 43077.25 | 66 | 63
2017-12-08 06:30 | 60 | 50 |  |  | 43077.2708 | 71 | 69
2017-12-08 07:00 | 60 | 51 |  |  | 43077.2917 | 76 | 74
2017-12-08 07:30 | 67 | 57 |  |  | 43077.3125 | 84 | 83
2017-12-08 08:00 | 70 | 61 |  |  | 43077.3333 | 91 | 89
2017-12-08 08:30 | 70 | 62 |  |  | 43077.3542 | 93 | 90
2017-12-08 09:00 | 73 | 66 |  |  | 43077.375 | 96 | 94
2017-12-08 09:30 | 72 | 66 |  |  | 43077.3958 | 97 | 95
2017-12-08 10:00 | 71 | 66 |  |  | 43077.4167 | 99 | 95
2017-12-08 10:30 | 71 | 66 |  |  | 43077.4375 | 100 | 95
2017-12-08 11:00 | 73 | 68 |  |  | 43077.4583 | 99 | 95
2017-12-08 11:30 | 81 | 73 |  |  | 43077.4792 | 103 | 101
2017-12-08 12:00 | 82 | 77 |  |  | 43077.5 | 114 | 109
2017-12-08 12:30 | 88 | 84 |  |  | 43077.5208 | 119 | 114
2017-12-08 13:00 | 85 | 81 |  |  | 43077.5417 | 117 | 111
2017-12-08 13:30 | 83 | 78 |  |  | 43077.5625 | 109 | 106
2017-12-08 14:00 | 80 | 75 |  |  | 43077.5833 | 109 | 104
2017-12-08 14:30 | 77 | 73 |  |  | 43077.6042 | 107 | 101
2017-12-08 15:00 | 78 | 73 |  |  | 43077.625 | 105 | 100
2017-12-08 15:30 | 75 | 71 |  |  | 43077.6458 | 103 | 97
2017-12-08 16:00 | 75 | 70 |  |  | 43077.6667 | 102 | 97
2017-12-08 16:30 | 76 | 70 |  |  | 43077.6875 | 100 | 97
2017-12-08 17:00 | 76 | 69 |  |  | 43077.7083 | 99 | 96
2017-12-08 17:30 | 73 | 67 |  |  | 43077.7292 | 96 | 93
2017-12-08 18:00 | 69 | 63 |  |  | 43077.75 | 90 | 87
2017-12-08 18:30 | 64 | 57 |  |  | 43077.7708 | 84 | 80
2017-12-08 19:00 | 67 | 62 |  |  | 43077.7917 | 89 | 84
2017-12-08 19:30 | 66 | 61 |  |  | 43077.8125 | 88 | 83
2017-12-08 20:00 | 66 | 60 |  |  | 43077.8333 | 85 | 80
2017-12-08 20:30 | 65 | 59 |  |  | 43077.8542 | 84 | 79
2017-12-08 21:00 | 64 | 58 |  |  | 43077.875 | 83 | 77
2017-12-08 21:30 | 61 | 55 |  |  | 43077.8958 | 77 | 71
2017-12-08 22:00 | 60 | 54 |  |  | 43077.9167 | 76 | 71
2017-12-08 22:30 | 62 | 53 |  |  | 43077.9375 | 72 | 69
2017-12-08 23:00 | 60 | 53 |  |  | 43077.9583 | 72 | 68
2017-12-08 23:30 | 57 | 50 |  |  | 43077.9792 | 70 | 66
2017-12-09 | 54 | 48 |  |  | 43078 | 67 | 63
2017-12-09 00:30 | 51 | 44 |  |  | 43078.0208 | 63 | 59
2017-12-09 01:00 | 49 | 42 |  |  | 43078.0417 | 60 | 55
2017-12-09 01:30 | 49 | 43 |  |  | 43078.0625 | 60 | 55
2017-12-09 02:00 | 48 | 41 |  |  | 43078.0833 | 59 | 54
2017-12-09 02:30 | 47 | 40 |  |  | 43078.1042 | 59 | 53
2017-12-09 03:00 | 46 | 39 |  |  | 43078.125 | 58 | 52
2017-12-09 03:30 | 44 | 38 |  |  | 43078.1458 | 57 | 51
2017-12-09 04:00 | 43 | 36 |  |  | 43078.1667 | 55 | 48
2017-12-09 04:30 | 43 | 36 |  |  | 43078.1875 | 54 | 48
2017-12-09 05:00 | 42 | 36 |  |  | 43078.2083 | 54 | 47
2017-12-09 05:30 | 44 | 37 |  |  | 43078.2292 | 55 | 48
2017-12-09 06:00 | 45 | 37 |  |  | 43078.25 | 56 | 49
2017-12-09 06:30 | 47 | 39 |  |  | 43078.2708 | 55 | 50
2017-12-09 07:00 | 48 | 39 |  |  | 43078.2917 | 57 | 53
2017-12-09 07:30 | 50 | 42 |  |  | 43078.3125 | 60 | 56
2017-12-09 08:00 | 53 | 45 |  |  | 43078.3333 | 62 | 60
2017-12-09 08:30 | 55 | 46 |  |  | 43078.3542 | 64 | 62
2017-12-09 09:00 | 52 | 42 |  |  | 43078.375 | 64 | 62
2017-12-09 09:30 | 42 | 29 |  |  | 43078.3958 | 57 | 55
2017-12-09 10:00 | 44 | 32 |  |  | 43078.4167 | 59 | 57
2017-12-09 10:30 | 48 | 35 |  |  | 43078.4375 | 62 | 60
2017-12-09 11:00 | 49 | 37 |  |  | 43078.4583 | 63 | 61
2017-12-09 11:30 | 53 | 44 |  |  | 43078.4792 | 68 | 67
2017-12-09 12:00 | 67 | 60 |  |  | 43078.5 | 79 | 77
2017-12-09 12:30 | 69 | 62 |  |  | 43078.5208 | 79 | 77
2017-12-09 13:00 | 70 | 64 |  |  | 43078.5417 | 81 | 78
2017-12-09 13:30 | 71 | 65 |  |  | 43078.5625 | 82 | 80
2017-12-09 14:00 | 73 | 67 |  |  | 43078.5833 | 83 | 81
2017-12-09 14:30 | 71 | 66 |  |  | 43078.6042 | 83 | 80
2017-12-09 15:00 | 69 | 66 |  |  | 43078.625 | 86 | 82
2017-12-09 15:30 | 70 | 68 |  |  | 43078.6458 | 92 | 86
2017-12-09 16:00 | 70 | 68 |  |  | 43078.6667 | 92 | 86
2017-12-09 16:30 | 71 | 69 |  |  | 43078.6875 | 94 | 88
2017-12-09 17:00 | 71 | 68 |  |  | 43078.7083 | 94 | 88
2017-12-09 17:30 | 70 | 68 |  |  | 43078.7292 | 95 | 88
2017-12-09 18:00 | 69 | 66 |  |  | 43078.75 | 91 | 86
2017-12-09 18:30 | 66 | 63 |  |  | 43078.7708 | 89 | 83
2017-12-09 19:00 | 67 | 64 |  |  | 43078.7917 | 90 | 84
2017-12-09 19:30 | 65 | 63 |  |  | 43078.8125 | 87 | 81
2017-12-09 20:00 | 64 | 61 |  |  | 43078.8333 | 85 | 79
2017-12-09 20:30 | 64 | 60 |  |  | 43078.8542 | 82 | 78
2017-12-09 21:00 | 62 | 57 |  |  | 43078.875 | 77 | 74
2017-12-09 21:30 | 62 | 56 |  |  | 43078.8958 | 76 | 73
2017-12-09 22:00 | 61 | 55 |  |  | 43078.9167 | 75 | 72
2017-12-09 22:30 | 60 | 54 |  |  | 43078.9375 | 75 | 72
2017-12-09 23:00 | 62 | 57 |  |  | 43078.9583 | 76 | 73
2017-12-09 23:30 | 60 | 56 |  |  | 43078.9792 | 76 | 72
2017-12-10 | 54 | 49 |  |  | 43079 | 70 | 66
2017-12-10 00:30 | 44 | 43 |  |  | 43079.0208 | 59 | 57
2017-12-10 01:00 | 42 | 39 |  |  | 43079.0417 | 55 | 54
2017-12-10 01:30 | 43 | 39 |  |  | 43079.0625 | 54 | 53
2017-12-10 02:00 | 42 | 37 |  |  | 43079.0833 | 53 | 51
2017-12-10 02:30 | 40 | 36 |  |  | 43079.1042 | 51 | 49
2017-12-10 03:00 | 40 | 36 |  |  | 43079.125 | 52 | 50
2017-12-10 03:30 | 41 | 37 |  |  | 43079.1458 | 51 | 49
2017-12-10 04:00 | 40 | 36 |  |  | 43079.1667 | 50 | 49
2017-12-10 04:30 | 40 | 36 |  |  | 43079.1875 | 51 | 50
2017-12-10 05:00 | 42 | 38 |  |  | 43079.2083 | 52 | 51
2017-12-10 05:30 | 41 | 36 |  |  | 43079.2292 | 52 | 49
2017-12-10 06:00 | 39 | 34 |  |  | 43079.25 | 50 | 48
2017-12-10 06:30 | 39 | 35 |  |  | 43079.2708 | 51 | 49
2017-12-10 07:00 | 40 | 36 |  |  | 43079.2917 | 52 | 51
2017-12-10 07:30 | 41 | 37 |  |  | 43079.3125 | 53 | 52
2017-12-10 08:00 | 41 | 38 |  |  | 43079.3333 | 54 | 54
2017-12-10 08:30 | 44 | 42 |  |  | 43079.3542 | 59 | 58
2017-12-10 09:00 | 43 | 41 |  |  | 43079.375 | 59 | 59
2017-12-10 09:30 | 41 | 40 |  |  | 43079.3958 | 59 | 59
2017-12-10 10:00 | 42 | 40 |  |  | 43079.4167 | 60 | 60
2017-12-10 10:30 | 41 | 40 |  |  | 43079.4375 | 59 | 59
2017-12-10 11:00 | 41 | 40 |  |  | 43079.4583 | 58 | 58
2017-12-10 11:30 | 42 | 41 |  |  | 43079.4792 | 59 | 59
2017-12-10 12:00 | 43 | 42 |  |  | 43079.5 | 60 | 60
2017-12-10 12:30 | 43 | 43 |  |  | 43079.5208 | 61 | 61
2017-12-10 13:00 | 45 | 44 |  |  | 43079.5417 | 61 | 61
2017-12-10 13:30 | 53 | 53 |  |  | 43079.5625 | 65 | 65
2017-12-10 14:00 | 56 | 55 |  |  | 43079.5833 | 67 | 67
2017-12-10 14:30 | 59 | 58 |  |  | 43079.6042 | 72 | 72
2017-12-10 15:00 | 64 | 62 |  |  | 43079.625 | 74 | 74
2017-12-10 15:30 | 67 | 63 |  |  | 43079.6458 | 78 | 78
2017-12-10 16:00 | 65 | 60 |  |  | 43079.6667 | 81 | 81
2017-12-10 16:30 | 62 | 56 |  |  | 43079.6875 | 75 | 75
2017-12-10 17:00 | 65 | 59 |  |  | 43079.7083 | 76 | 76
2017-12-10 17:30 | 65 | 59 |  |  | 43079.7292 | 76 | 76
2017-12-10 18:00 | 66 | 60 |  |  | 43079.75 | 77 | 77
2017-12-10 18:30 | 66 | 60 |  |  | 43079.7708 | 77 | 77
2017-12-10 19:00 | 69 | 64 |  |  | 43079.7917 | 82 | 82
2017-12-10 19:30 | 70 | 65 |  |  | 43079.8125 | 84 | 84
2017-12-10 20:00 | 68 | 63 |  |  | 43079.8333 | 82 | 82
2017-12-10 20:30 | 68 | 62 |  |  | 43079.8542 | 82 | 82
2017-12-10 21:00 | 67 | 62 |  |  | 43079.875 | 79 | 79
2017-12-10 21:30 | 65 | 59 |  |  | 43079.8958 | 77 | 77
2017-12-10 22:00 | 64 | 58 |  |  | 43079.9167 | 76 | 76
2017-12-10 22:30 | 62 | 56 |  |  | 43079.9375 | 72 | 72
2017-12-10 23:00 | 61 | 54 |  |  | 43079.9583 | 69 | 69
2017-12-10 23:30 | 58 | 51 |  |  | 43079.9792 | 66 | 66
2017-12-11 | 54 | 47 |  |  | 43080 | 62 | 62
2017-12-11 00:30 | 51 | 42 |  |  | 43080.0208 | 57 | 57
2017-12-11 01:00 | 48 | 38 |  |  | 43080.0417 | 54 | 54
2017-12-11 01:30 | 49 | 38 |  |  | 43080.0625 | 53 | 53
2017-12-11 02:00 | 50 | 39 |  |  | 43080.0833 | 53 | 53
2017-12-11 02:30 | 51 | 40 |  |  | 43080.1042 | 51 | 51
2017-12-11 03:00 | 49 | 38 |  |  | 43080.125 | 51 | 50
2017-12-11 03:30 | 49 | 37 |  |  | 43080.1458 | 50 | 50
2017-12-11 04:00 | 49 | 38 |  |  | 43080.1667 | 50 | 50
2017-12-11 04:30 | 49 | 39 |  |  | 43080.1875 | 51 | 51
2017-12-11 05:00 | 51 | 40 |  |  | 43080.2083 | 54 | 54
2017-12-11 05:30 | 53 | 44 |  |  | 43080.2292 | 59 | 59
2017-12-11 06:00 | 56 | 49 |  |  | 43080.25 | 65 | 65
2017-12-11 06:30 | 58 | 53 |  |  | 43080.2708 | 73 | 73
2017-12-11 07:00 | 62 | 58 |  |  | 43080.2917 | 81 | 80
2017-12-11 07:30 | 64 | 61 |  |  | 43080.3125 | 88 | 87
2017-12-11 08:00 | 67 | 65 |  |  | 43080.3333 | 91 | 91
2017-12-11 08:30 | 69 | 68 |  |  | 43080.3542 | 97 | 96
2017-12-11 09:00 | 70 | 69 |  |  | 43080.375 | 98 | 97
2017-12-11 09:30 | 71 | 70 |  |  | 43080.3958 | 98 | 98
2017-12-11 10:00 | 74 | 73 |  |  | 43080.4167 | 101 | 100
2017-12-11 10:30 | 76 | 73 |  |  | 43080.4375 | 102 | 101
2017-12-11 11:00 | 83 | 73 |  |  | 43080.4583 | 105 | 103
2017-12-11 11:30 | 80 | 70 |  |  | 43080.4792 | 99 | 97
2017-12-11 12:00 | 80 | 70 |  |  | 43080.5 | 97 | 95
2017-12-11 12:30 | 80 | 71 |  |  | 43080.5208 | 98 | 95
2017-12-11 13:00 | 83 | 73 |  |  | 43080.5417 | 101 | 99
2017-12-11 13:30 | 86 | 77 |  |  | 43080.5625 | 104 | 101
2017-12-11 14:00 | 84 | 74 |  |  | 43080.5833 | 102 | 99
2017-12-11 14:30 | 84 | 74 |  |  | 43080.6042 | 100 | 98
2017-12-11 15:00 | 87 | 78 |  |  | 43080.625 | 104 | 101
2017-12-11 15:30 | 91 | 81 |  |  | 43080.6458 | 106 | 104
2017-12-11 16:00 | 95 | 85 |  |  | 43080.6667 | 109 | 107
2017-12-11 16:30 | 97 | 86 |  |  | 43080.6875 | 110 | 109
2017-12-11 17:00 | 99 | 88 |  |  | 43080.7083 | 110 | 109
2017-12-11 17:30 | 99 | 87 |  |  | 43080.7292 | 107 | 106
2017-12-11 18:00 | 91 | 85 |  |  | 43080.75 | 104 | 103
2017-12-11 18:30 | 87 | 83 |  |  | 43080.7708 | 103 | 100
2017-12-11 19:00 | 90 | 88 |  |  | 43080.7917 | 107 | 104
2017-12-11 19:30 | 90 | 88 |  |  | 43080.8125 | 108 | 105
2017-12-11 20:00 | 89 | 86 |  |  | 43080.8333 | 105 | 102
2017-12-11 20:30 | 85 | 82 |  |  | 43080.8542 | 101 | 98
2017-12-11 21:00 | 80 | 77 |  |  | 43080.875 | 97 | 93
2017-12-11 21:30 | 72 | 71 |  |  | 43080.8958 | 88 | 87
2017-12-11 22:00 | 69 | 69 |  |  | 43080.9167 | 83 | 83
2017-12-11 22:30 | 64 | 64 |  |  | 43080.9375 | 79 | 79
2017-12-11 23:00 | 64 | 63 |  |  | 43080.9583 | 77 | 77
2017-12-11 23:30 | 60 | 58 |  |  | 43080.9792 | 72 | 72
2017-12-12 | 55 | 53 |  |  | 43081 | 65 | 65
2017-12-12 00:30 | 50 | 48 |  |  | 43081.0208 | 60 | 60
2017-12-12 01:00 | 47 | 46 |  |  | 43081.0417 | 56 | 56
2017-12-12 01:30 | 46 | 44 |  |  | 43081.0625 | 54 | 54
2017-12-12 02:00 | 46 | 45 |  |  | 43081.0833 | 54 | 54
2017-12-12 02:30 | 44 | 43 |  |  | 43081.1042 | 54 | 54
2017-12-12 03:00 | 42 | 40 |  |  | 43081.125 | 51 | 51
2017-12-12 03:30 | 43 | 41 |  |  | 43081.1458 | 52 | 51
2017-12-12 04:00 | 43 | 41 |  |  | 43081.1667 | 51 | 51
2017-12-12 04:30 | 43 | 42 |  |  | 43081.1875 | 52 | 52
2017-12-12 05:00 | 44 | 42 |  |  | 43081.2083 | 53 | 53
2017-12-12 05:30 | 46 | 45 |  |  | 43081.2292 | 56 | 56
2017-12-12 06:00 | 50 | 49 |  |  | 43081.25 | 61 | 61
2017-12-12 06:30 | 56 | 54 |  |  | 43081.2708 | 72 | 70
2017-12-12 07:00 | 60 | 59 |  |  | 43081.2917 | 80 | 77
2017-12-12 07:30 | 61 | 59 |  |  | 43081.3125 | 84 | 83
2017-12-12 08:00 | 62 | 61 |  |  | 43081.3333 | 87 | 85
2017-12-12 08:30 | 64 | 64 |  |  | 43081.3542 | 90 | 88
2017-12-12 09:00 | 68 | 68 |  |  | 43081.375 | 95 | 93
2017-12-12 09:30 | 72 | 72 |  |  | 43081.3958 | 99 | 98
2017-12-12 10:00 | 75 | 74 |  |  | 43081.4167 | 100 | 100
2017-12-12 10:30 | 73 | 71 |  |  | 43081.4375 | 95 | 94
2017-12-12 11:00 | 72 | 70 |  |  | 43081.4583 | 93 | 93
2017-12-12 11:30 | 72 | 70 |  |  | 43081.4792 | 93 | 93
2017-12-12 12:00 | 70 | 68 |  |  | 43081.5 | 91 | 91
2017-12-12 12:30 | 68 | 66 |  |  | 43081.5208 | 91 | 90
2017-12-12 13:00 | 66 | 65 |  |  | 43081.5417 | 89 | 88
2017-12-12 13:30 | 68 | 67 |  |  | 43081.5625 | 91 | 90
2017-12-12 14:00 | 67 | 65 |  |  | 43081.5833 | 87 | 86
2017-12-12 14:30 | 67 | 66 |  |  | 43081.6042 | 86 | 85
2017-12-12 15:00 | 71 | 69 |  |  | 43081.625 | 90 | 89
2017-12-12 15:30 | 75 | 73 |  |  | 43081.6458 | 94 | 93
2017-12-12 16:00 | 78 | 77 |  |  | 43081.6667 | 97 | 97
2017-12-12 16:30 | 79 | 77 |  |  | 43081.6875 | 99 | 98
2017-12-12 17:00 | 80 | 79 |  |  | 43081.7083 | 99 | 99
2017-12-12 17:30 | 82 | 79 |  |  | 43081.7292 | 98 | 98
2017-12-12 18:00 | 80 | 77 |  |  | 43081.75 | 95 | 95
2017-12-12 18:30 | 77 | 75 |  |  | 43081.7708 | 93 | 92
2017-12-12 19:00 | 79 | 77 |  |  | 43081.7917 | 96 | 95
2017-12-12 19:30 | 80 | 78 |  |  | 43081.8125 | 95 | 95
2017-12-12 20:00 | 79 | 76 |  |  | 43081.8333 | 92 | 92
2017-12-12 20:30 | 74 | 71 |  |  | 43081.8542 | 87 | 87
2017-12-12 21:00 | 69 | 65 |  |  | 43081.875 | 81 | 81
2017-12-12 21:30 | 66 | 62 |  |  | 43081.8958 | 78 | 77
2017-12-12 22:00 | 64 | 61 |  |  | 43081.9167 | 77 | 77
2017-12-12 22:30 | 66 | 62 |  |  | 43081.9375 | 77 | 77
2017-12-12 23:00 | 67 | 63 |  |  | 43081.9583 | 77 | 77
2017-12-12 23:30 | 64 | 59 |  |  | 43081.9792 | 74 | 74
2017-12-13 | 59 | 54 |  |  | 43082 | 68 | 68
2017-12-13 00:30 | 54 | 49 |  |  | 43082.0208 | 61 | 61
2017-12-13 01:00 | 51 | 45 |  |  | 43082.0417 | 57 | 57
2017-12-13 01:30 | 52 | 43 |  |  | 43082.0625 | 55 | 55
2017-12-13 02:00 | 52 | 43 |  |  | 43082.0833 | 55 | 54
2017-12-13 02:30 | 50 | 40 |  |  | 43082.1042 | 52 | 52
2017-12-13 03:00 | 50 | 39 |  |  | 43082.125 | 51 | 51
2017-12-13 03:30 | 49 | 39 |  |  | 43082.1458 | 51 | 51
2017-12-13 04:00 | 49 | 39 |  |  | 43082.1667 | 52 | 51
2017-12-13 04:30 | 50 | 40 |  |  | 43082.1875 | 54 | 53
2017-12-13 05:00 | 49 | 39 |  |  | 43082.2083 | 50 | 50
2017-12-13 05:30 | 47 | 38 |  |  | 43082.2292 | 50 | 50
2017-12-13 06:00 | 47 | 41 |  |  | 43082.25 | 54 | 54
2017-12-13 06:30 | 50 | 47 |  |  | 43082.2708 | 63 | 63
2017-12-13 07:00 | 50 | 48 |  |  | 43082.2917 | 69 | 68
2017-12-13 07:30 | 54 | 53 |  |  | 43082.3125 | 76 | 75
2017-12-13 08:00 | 56 | 55 |  |  | 43082.3333 | 79 | 79
2017-12-13 08:30 | 60 | 59 |  |  | 43082.3542 | 85 | 84
2017-12-13 09:00 | 63 | 63 |  |  | 43082.375 | 89 | 88
2017-12-13 09:30 | 63 | 62 |  |  | 43082.3958 | 89 | 87
2017-12-13 10:00 | 64 | 64 |  |  | 43082.4167 | 90 | 89
2017-12-13 10:30 | 63 | 63 |  |  | 43082.4375 | 89 | 87
2017-12-13 11:00 | 62 | 62 |  |  | 43082.4583 | 88 | 86
2017-12-13 11:30 | 64 | 64 |  |  | 43082.4792 | 91 | 90
2017-12-13 12:00 | 68 | 68 |  |  | 43082.5 | 92 | 91
2017-12-13 12:30 | 69 | 69 |  |  | 43082.5208 | 93 | 92
2017-12-13 13:00 | 69 | 68 |  |  | 43082.5417 | 91 | 91
2017-12-13 13:30 | 71 | 69 |  |  | 43082.5625 | 91 | 91
2017-12-13 14:00 | 72 | 71 |  |  | 43082.5833 | 93 | 93
2017-12-13 14:30 | 73 | 71 |  |  | 43082.6042 | 93 | 93
2017-12-13 15:00 | 74 | 73 |  |  | 43082.625 | 94 | 94
2017-12-13 15:30 | 78 | 76 |  |  | 43082.6458 | 97 | 97
2017-12-13 16:00 | 79 | 77 |  |  | 43082.6667 | 101 | 101
2017-12-13 16:30 | 78 | 76 |  |  | 43082.6875 | 99 | 99
2017-12-13 17:00 | 79 | 77 |  |  | 43082.7083 | 99 | 99
2017-12-13 17:30 | 79 | 77 |  |  | 43082.7292 | 97 | 97
2017-12-13 18:00 | 78 | 75 |  |  | 43082.75 | 94 | 94
2017-12-13 18:30 | 78 | 76 |  |  | 43082.7708 | 94 | 94
2017-12-13 19:00 | 81 | 79 |  |  | 43082.7917 | 98 | 98
2017-12-13 19:30 | 83 | 81 |  |  | 43082.8125 | 98 | 97
2017-12-13 20:00 | 76 | 75 |  |  | 43082.8333 | 92 | 92
2017-12-13 20:30 | 70 | 69 |  |  | 43082.8542 | 87 | 87
2017-12-13 21:00 | 69 | 67 |  |  | 43082.875 | 83 | 83
2017-12-13 21:30 | 67 | 63 |  |  | 43082.8958 | 78 | 78
2017-12-13 22:00 | 67 | 60 |  |  | 43082.9167 | 77 | 77
2017-12-13 22:30 | 66 | 59 |  |  | 43082.9375 | 76 | 76
2017-12-13 23:00 | 64 | 55 |  |  | 43082.9583 | 72 | 72
2017-12-13 23:30 | 64 | 54 |  |  | 43082.9792 | 70 | 70
2017-12-14 | 63 | 53 |  |  | 43083 | 67 | 67
2017-12-14 00:30 | 57 | 49 |  |  | 43083.0208 | 62 | 62
2017-12-14 01:00 | 53 | 44 |  |  | 43083.0417 | 57 | 57
2017-12-14 01:30 | 51 | 43 |  |  | 43083.0625 | 55 | 55
2017-12-14 02:00 | 51 | 42 |  |  | 43083.0833 | 53 | 53
2017-12-14 02:30 | 52 | 42 |  |  | 43083.1042 | 54 | 53
2017-12-14 03:00 | 52 | 41 |  |  | 43083.125 | 53 | 53
2017-12-14 03:30 | 51 | 41 |  |  | 43083.1458 | 53 | 52
2017-12-14 04:00 | 51 | 41 |  |  | 43083.1667 | 53 | 53
2017-12-14 04:30 | 52 | 43 |  |  | 43083.1875 | 54 | 54
2017-12-14 05:00 | 52 | 43 |  |  | 43083.2083 | 56 | 55
2017-12-14 05:30 | 54 | 46 |  |  | 43083.2292 | 59 | 59
2017-12-14 06:00 | 56 | 50 |  |  | 43083.25 | 64 | 64
2017-12-14 06:30 | 58 | 55 |  |  | 43083.2708 | 71 | 71
2017-12-14 07:00 | 56 | 54 |  |  | 43083.2917 | 75 | 74
2017-12-14 07:30 | 58 | 57 |  |  | 43083.3125 | 81 | 80
2017-12-14 08:00 | 60 | 59 |  |  | 43083.3333 | 82 | 81
2017-12-14 08:30 | 60 | 59 |  |  | 43083.3542 | 83 | 82
2017-12-14 09:00 | 60 | 59 |  |  | 43083.375 | 82 | 82
2017-12-14 09:30 | 59 | 57 |  |  | 43083.3958 | 80 | 80
2017-12-14 10:00 | 61 | 59 |  |  | 43083.4167 | 81 | 81
2017-12-14 10:30 | 61 | 59 |  |  | 43083.4375 | 81 | 81
2017-12-14 11:00 | 62 | 59 |  |  | 43083.4583 | 80 | 80
2017-12-14 11:30 | 67 | 65 |  |  | 43083.4792 | 85 | 85
2017-12-14 12:00 | 69 | 67 |  |  | 43083.5 | 86 | 86
2017-12-14 12:30 | 69 | 67 |  |  | 43083.5208 | 87 | 87
2017-12-14 13:00 | 72 | 70 |  |  | 43083.5417 | 91 | 90
2017-12-14 13:30 | 74 | 73 |  |  | 43083.5625 | 93 | 93
2017-12-14 14:00 | 76 | 74 |  |  | 43083.5833 | 92 | 92
2017-12-14 14:30 | 77 | 76 |  |  | 43083.6042 | 94 | 94
2017-12-14 15:00 | 78 | 78 |  |  | 43083.625 | 99 | 98
2017-12-14 15:30 | 74 | 74 |  |  | 43083.6458 | 96 | 95
2017-12-14 16:00 | 72 | 71 |  |  | 43083.6667 | 94 | 93
2017-12-14 16:30 | 75 | 73 |  |  | 43083.6875 | 97 | 96
2017-12-14 17:00 | 77 | 75 |  |  | 43083.7083 | 98 | 97
2017-12-14 17:30 | 77 | 74 |  |  | 43083.7292 | 95 | 95
2017-12-14 18:00 | 77 | 74 |  |  | 43083.75 | 92 | 92
2017-12-14 18:30 | 75 | 71 |  |  | 43083.7708 | 87 | 87
2017-12-14 19:00 | 76 | 72 |  |  | 43083.7917 | 89 | 89
2017-12-14 19:30 | 74 | 72 |  |  | 43083.8125 | 90 | 89
2017-12-14 20:00 | 73 | 71 |  |  | 43083.8333 | 88 | 88
2017-12-14 20:30 | 71 | 69 |  |  | 43083.8542 | 86 | 86
2017-12-14 21:00 | 67 | 66 |  |  | 43083.875 | 81 | 81
2017-12-14 21:30 | 63 | 62 |  |  | 43083.8958 | 78 | 77
2017-12-14 22:00 | 61 | 60 |  |  | 43083.9167 | 76 | 75
2017-12-14 22:30 | 58 | 57 |  |  | 43083.9375 | 74 | 73
2017-12-14 23:00 | 59 | 58 |  |  | 43083.9583 | 74 | 74
2017-12-14 23:30 | 59 | 58 |  |  | 43083.9792 | 75 | 74
2017-12-15 | 54 | 52 |  |  | 43084 | 68 | 67
2017-12-15 00:30 | 49 | 47 |  |  | 43084.0208 | 60 | 60
2017-12-15 01:00 | 45 | 43 |  |  | 43084.0417 | 56 | 56
2017-12-15 01:30 | 47 | 40 |  |  | 43084.0625 | 52 | 52
2017-12-15 02:00 | 47 | 39 |  |  | 43084.0833 | 53 | 53
2017-12-15 02:30 | 46 | 38 |  |  | 43084.1042 | 51 | 51
2017-12-15 03:00 | 46 | 38 |  |  | 43084.125 | 50 | 50
2017-12-15 03:30 | 45 | 37 |  |  | 43084.1458 | 49 | 49
2017-12-15 04:00 | 44 | 36 |  |  | 43084.1667 | 49 | 49
2017-12-15 04:30 | 46 | 38 |  |  | 43084.1875 | 50 | 50
2017-12-15 05:00 | 47 | 40 |  |  | 43084.2083 | 53 | 53
2017-12-15 05:30 | 48 | 42 |  |  | 43084.2292 | 57 | 57
2017-12-15 06:00 | 49 | 44 |  |  | 43084.25 | 61 | 60
2017-12-15 06:30 | 54 | 50 |  |  | 43084.2708 | 71 | 70
2017-12-15 07:00 | 54 | 51 |  |  | 43084.2917 | 75 | 74
2017-12-15 07:30 | 57 | 53 |  |  | 43084.3125 | 80 | 80
2017-12-15 08:00 | 60 | 57 |  |  | 43084.3333 | 84 | 83
2017-12-15 08:30 | 60 | 58 |  |  | 43084.3542 | 86 | 85
2017-12-15 09:00 | 58 | 56 |  |  | 43084.375 | 85 | 85
2017-12-15 09:30 | 60 | 58 |  |  | 43084.3958 | 86 | 86
2017-12-15 10:00 | 61 | 59 |  |  | 43084.4167 | 88 | 87
2017-12-15 10:30 | 61 | 59 |  |  | 43084.4375 | 88 | 87
2017-12-15 11:00 | 66 | 60 |  |  | 43084.4583 | 92 | 89
2017-12-15 11:30 | 73 | 62 |  |  | 43084.4792 | 96 | 89
2017-12-15 12:00 | 72 | 61 |  |  | 43084.5 | 94 | 87
2017-12-15 12:30 | 73 | 61 |  |  | 43084.5208 | 93 | 87
2017-12-15 13:00 | 74 | 62 |  |  | 43084.5417 | 93 | 87
2017-12-15 13:30 | 76 | 65 |  |  | 43084.5625 | 96 | 91
2017-12-15 14:00 | 77 | 66 |  |  | 43084.5833 | 97 | 93
2017-12-15 14:30 | 77 | 65 |  |  | 43084.6042 | 97 | 92
2017-12-15 15:00 | 80 | 66 |  |  | 43084.625 | 98 | 94
2017-12-15 15:30 | 81 | 68 |  |  | 43084.6458 | 100 | 96
2017-12-15 16:00 | 85 | 73 |  |  | 43084.6667 | 103 | 100
2017-12-15 16:30 | 88 | 75 |  |  | 43084.6875 | 106 | 103
2017-12-15 17:00 | 89 | 77 |  |  | 43084.7083 | 108 | 105
2017-12-15 17:30 | 92 | 78 |  |  | 43084.7292 | 105 | 104
2017-12-15 18:00 | 92 | 76 |  |  | 43084.75 | 101 | 100
2017-12-15 18:30 | 85 | 71 |  |  | 43084.7708 | 96 | 94
2017-12-15 19:00 | 86 | 74 |  |  | 43084.7917 | 100 | 98
2017-12-15 19:30 | 86 | 72 |  |  | 43084.8125 | 95 | 95
2017-12-15 20:00 | 87 | 72 |  |  | 43084.8333 | 94 | 94
2017-12-15 20:30 | 87 | 71 |  |  | 43084.8542 | 92 | 92
2017-12-15 21:00 | 75 | 68 |  |  | 43084.875 | 91 | 89
2017-12-15 21:30 | 67 | 64 |  |  | 43084.8958 | 84 | 83
2017-12-15 22:00 | 65 | 62 |  |  | 43084.9167 | 82 | 82
2017-12-15 22:30 | 64 | 61 |  |  | 43084.9375 | 81 | 81
2017-12-15 23:00 | 66 | 63 |  |  | 43084.9583 | 82 | 82
2017-12-15 23:30 | 63 | 60 |  |  | 43084.9792 | 79 | 79
2017-12-16 | 59 | 54 |  |  | 43085 | 73 | 73
2017-12-16 00:30 | 56 | 50 |  |  | 43085.0208 | 66 | 66
2017-12-16 01:00 | 52 | 45 |  |  | 43085.0417 | 61 | 61
2017-12-16 01:30 | 51 | 44 |  |  | 43085.0625 | 60 | 60
2017-12-16 02:00 | 49 | 42 |  |  | 43085.0833 | 58 | 58
2017-12-16 02:30 | 50 | 42 |  |  | 43085.1042 | 57 | 57
2017-12-16 03:00 | 49 | 41 |  |  | 43085.125 | 57 | 57
2017-12-16 03:30 | 49 | 41 |  |  | 43085.1458 | 56 | 56
2017-12-16 04:00 | 49 | 41 |  |  | 43085.1667 | 56 | 56
2017-12-16 04:30 | 47 | 39 |  |  | 43085.1875 | 55 | 55
2017-12-16 05:00 | 50 | 42 |  |  | 43085.2083 | 56 | 56
2017-12-16 05:30 | 49 | 41 |  |  | 43085.2292 | 55 | 55
2017-12-16 06:00 | 49 | 41 |  |  | 43085.25 | 56 | 55
2017-12-16 06:30 | 49 | 42 |  |  | 43085.2708 | 58 | 58
2017-12-16 07:00 | 48 | 42 |  |  | 43085.2917 | 60 | 60
2017-12-16 07:30 | 50 | 43 |  |  | 43085.3125 | 62 | 62
2017-12-16 08:00 | 52 | 47 |  |  | 43085.3333 | 66 | 66
2017-12-16 08:30 | 54 | 49 |  |  | 43085.3542 | 71 | 71
2017-12-16 09:00 | 55 | 51 |  |  | 43085.375 | 71 | 71
2017-12-16 09:30 | 54 | 50 |  |  | 43085.3958 | 69 | 69
2017-12-16 10:00 | 53 | 48 |  |  | 43085.4167 | 67 | 67
2017-12-16 10:30 | 53 | 48 |  |  | 43085.4375 | 67 | 67
2017-12-16 11:00 | 52 | 48 |  |  | 43085.4583 | 66 | 66
2017-12-16 11:30 | 54 | 49 |  |  | 43085.4792 | 68 | 68
2017-12-16 12:00 | 53 | 49 |  |  | 43085.5 | 67 | 67
2017-12-16 12:30 | 54 | 50 |  |  | 43085.5208 | 66 | 65
2017-12-16 13:00 | 58 | 54 |  |  | 43085.5417 | 68 | 68
2017-12-16 13:30 | 58 | 55 |  |  | 43085.5625 | 69 | 69
2017-12-16 14:00 | 58 | 53 |  |  | 43085.5833 | 70 | 70
2017-12-16 14:30 | 60 | 53 |  |  | 43085.6042 | 69 | 69
2017-12-16 15:00 | 61 | 55 |  |  | 43085.625 | 72 | 72
2017-12-16 15:30 | 62 | 55 |  |  | 43085.6458 | 72 | 72
2017-12-16 16:00 | 64 | 58 |  |  | 43085.6667 | 77 | 76
2017-12-16 16:30 | 65 | 58 |  |  | 43085.6875 | 78 | 77
2017-12-16 17:00 | 68 | 62 |  |  | 43085.7083 | 82 | 81
2017-12-16 17:30 | 71 | 64 |  |  | 43085.7292 | 84 | 83
2017-12-16 18:00 | 67 | 59 |  |  | 43085.75 | 82 | 81
2017-12-16 18:30 | 67 | 58 |  |  | 43085.7708 | 80 | 80
2017-12-16 19:00 | 66 | 59 |  |  | 43085.7917 | 81 | 80
2017-12-16 19:30 | 67 | 61 |  |  | 43085.8125 | 83 | 83
2017-12-16 20:00 | 67 | 61 |  |  | 43085.8333 | 82 | 82
2017-12-16 20:30 | 67 | 61 |  |  | 43085.8542 | 82 | 81
2017-12-16 21:00 | 65 | 60 |  |  | 43085.875 | 79 | 79
2017-12-16 21:30 | 64 | 60 |  |  | 43085.8958 | 79 | 79
2017-12-16 22:00 | 68 | 63 |  |  | 43085.9167 | 84 | 84
2017-12-16 22:30 | 69 | 65 |  |  | 43085.9375 | 84 | 84
2017-12-16 23:00 | 69 | 64 |  |  | 43085.9583 | 82 | 82
2017-12-16 23:30 | 65 | 59 |  |  | 43085.9792 | 78 | 78
2017-12-17 | 61 | 54 |  |  | 43086 | 72 | 72
2017-12-17 00:30 | 57 | 50 |  |  | 43086.0208 | 66 | 66
2017-12-17 01:00 | 53 | 45 |  |  | 43086.0417 | 61 | 61
2017-12-17 01:30 | 52 | 44 |  |  | 43086.0625 | 58 | 58
2017-12-17 02:00 | 50 | 43 |  |  | 43086.0833 | 58 | 58
2017-12-17 02:30 | 50 | 42 |  |  | 43086.1042 | 58 | 58
2017-12-17 03:00 | 50 | 42 |  |  | 43086.125 | 57 | 57
2017-12-17 03:30 | 48 | 40 |  |  | 43086.1458 | 55 | 55
2017-12-17 04:00 | 49 | 40 |  |  | 43086.1667 | 54 | 54
2017-12-17 04:30 | 48 | 39 |  |  | 43086.1875 | 53 | 53
2017-12-17 05:00 | 48 | 38 |  |  | 43086.2083 | 52 | 52
2017-12-17 05:30 | 46 | 36 |  |  | 43086.2292 | 51 | 51
2017-12-17 06:00 | 45 | 34 |  |  | 43086.25 | 51 | 51
2017-12-17 06:30 | 44 | 35 |  |  | 43086.2708 | 51 | 51
2017-12-17 07:00 | 44 | 35 |  |  | 43086.2917 | 53 | 53
2017-12-17 07:30 | 44 | 37 |  |  | 43086.3125 | 55 | 55
2017-12-17 08:00 | 44 | 38 |  |  | 43086.3333 | 58 | 58
2017-12-17 08:30 | 47 | 41 |  |  | 43086.3542 | 60 | 60
2017-12-17 09:00 | 48 | 42 |  |  | 43086.375 | 61 | 61
2017-12-17 09:30 | 50 | 44 |  |  | 43086.3958 | 63 | 63
2017-12-17 10:00 | 52 | 47 |  |  | 43086.4167 | 64 | 64
2017-12-17 10:30 | 54 | 49 |  |  | 43086.4375 | 67 | 67
2017-12-17 11:00 | 54 | 50 |  |  | 43086.4583 | 66 | 66
2017-12-17 11:30 | 55 | 50 |  |  | 43086.4792 | 67 | 66
2017-12-17 12:00 | 56 | 52 |  |  | 43086.5 | 68 | 67
2017-12-17 12:30 | 58 | 54 |  |  | 43086.5208 | 70 | 70
2017-12-17 13:00 | 59 | 55 |  |  | 43086.5417 | 73 | 73
2017-12-17 13:30 | 60 | 56 |  |  | 43086.5625 | 72 | 72
2017-12-17 14:00 | 58 | 55 |  |  | 43086.5833 | 68 | 68
2017-12-17 14:30 | 58 | 54 |  |  | 43086.6042 | 69 | 69
2017-12-17 15:00 | 66 | 56 |  |  | 43086.625 | 75 | 73
2017-12-17 15:30 | 68 | 58 |  |  | 43086.6458 | 78 | 75
2017-12-17 16:00 | 69 | 60 |  |  | 43086.6667 | 81 | 79
2017-12-17 16:30 | 71 | 62 |  |  | 43086.6875 | 82 | 80
2017-12-17 17:00 | 74 | 65 |  |  | 43086.7083 | 86 | 84
2017-12-17 17:30 | 76 | 67 |  |  | 43086.7292 | 88 | 86
2017-12-17 18:00 | 75 | 65 |  |  | 43086.75 | 87 | 85
2017-12-17 18:30 | 76 | 65 |  |  | 43086.7708 | 88 | 84
2017-12-17 19:00 | 79 | 68 |  |  | 43086.7917 | 92 | 89
2017-12-17 19:30 | 78 | 68 |  |  | 43086.8125 | 91 | 88
2017-12-17 20:00 | 78 | 67 |  |  | 43086.8333 | 91 | 88
2017-12-17 20:30 | 70 | 65 |  |  | 43086.8542 | 84 | 84
2017-12-17 21:00 | 68 | 63 |  |  | 43086.875 | 82 | 82
2017-12-17 21:30 | 66 | 60 |  |  | 43086.8958 | 80 | 80
2017-12-17 22:00 | 66 | 60 |  |  | 43086.9167 | 80 | 80
2017-12-17 22:30 | 65 | 59 |  |  | 43086.9375 | 79 | 79
2017-12-17 23:00 | 61 | 55 |  |  | 43086.9583 | 74 | 74
2017-12-17 23:30 | 57 | 49 |  |  | 43086.9792 | 67 | 67
2017-12-18 | 54 | 47 |  |  | 43087 | 65 | 65
2017-12-18 00:30 | 53 | 45 |  |  | 43087.0208 | 63 | 63
2017-12-18 01:00 | 52 | 44 |  |  | 43087.0417 | 62 | 62
2017-12-18 01:30 | 50 | 42 |  |  | 43087.0625 | 59 | 59
2017-12-18 02:00 | 49 | 41 |  |  | 43087.0833 | 57 | 57
2017-12-18 02:30 | 48 | 39 |  |  | 43087.1042 | 55 | 55
2017-12-18 03:00 | 48 | 38 |  |  | 43087.125 | 54 | 54
2017-12-18 03:30 | 47 | 37 |  |  | 43087.1458 | 52 | 52
2017-12-18 04:00 | 49 | 40 |  |  | 43087.1667 | 54 | 54
2017-12-18 04:30 | 49 | 40 |  |  | 43087.1875 | 54 | 54
2017-12-18 05:00 | 49 | 40 |  |  | 43087.2083 | 55 | 55
2017-12-18 05:30 | 50 | 42 |  |  | 43087.2292 | 59 | 59
2017-12-18 06:00 | 53 | 47 |  |  | 43087.25 | 64 | 64
2017-12-18 06:30 | 56 | 53 |  |  | 43087.2708 | 74 | 73
2017-12-18 07:00 | 58 | 57 |  |  | 43087.2917 | 82 | 81
2017-12-18 07:30 | 61 | 60 |  |  | 43087.3125 | 90 | 88
2017-12-18 08:00 | 63 | 62 |  |  | 43087.3333 | 96 | 93
2017-12-18 08:30 | 65 | 65 |  |  | 43087.3542 | 99 | 96
2017-12-18 09:00 | 66 | 65 |  |  | 43087.375 | 98 | 96
2017-12-18 09:30 | 68 | 68 |  |  | 43087.3958 | 99 | 97
2017-12-18 10:00 | 69 | 69 |  |  | 43087.4167 | 100 | 98
2017-12-18 10:30 | 69 | 69 |  |  | 43087.4375 | 99 | 96
2017-12-18 11:00 | 70 | 70 |  |  | 43087.4583 | 99 | 96
2017-12-18 11:30 | 70 | 70 |  |  | 43087.4792 | 100 | 97
2017-12-18 12:00 | 70 | 70 |  |  | 43087.5 | 99 | 96
2017-12-18 12:30 | 70 | 70 |  |  | 43087.5208 | 98 | 95
2017-12-18 13:00 | 70 | 70 |  |  | 43087.5417 | 100 | 97
2017-12-18 13:30 | 71 | 71 |  |  | 43087.5625 | 102 | 99
2017-12-18 14:00 | 73 | 73 |  |  | 43087.5833 | 102 | 99
2017-12-18 14:30 | 77 | 75 |  |  | 43087.6042 | 107 | 102
2017-12-18 15:00 | 83 | 77 |  |  | 43087.625 | 110 | 105
2017-12-18 15:30 | 86 | 79 |  |  | 43087.6458 | 110 | 106
2017-12-18 16:00 | 88 | 81 |  |  | 43087.6667 | 112 | 108
2017-12-18 16:30 | 86 | 78 |  |  | 43087.6875 | 109 | 105
2017-12-18 17:00 | 87 | 78 |  |  | 43087.7083 | 107 | 104
2017-12-18 17:30 | 88 | 78 |  |  | 43087.7292 | 105 | 102
2017-12-18 18:00 | 84 | 72 |  |  | 43087.75 | 97 | 94
2017-12-18 18:30 | 79 | 72 |  |  | 43087.7708 | 93 | 92
2017-12-18 19:00 | 78 | 73 |  |  | 43087.7917 | 96 | 95
2017-12-18 19:30 | 79 | 74 |  |  | 43087.8125 | 97 | 97
2017-12-18 20:00 | 78 | 72 |  |  | 43087.8333 | 95 | 94
2017-12-18 20:30 | 74 | 69 |  |  | 43087.8542 | 91 | 90
2017-12-18 21:00 | 68 | 67 |  |  | 43087.875 | 86 | 86
2017-12-18 21:30 | 64 | 61 |  |  | 43087.8958 | 83 | 81
2017-12-18 22:00 | 61 | 59 |  |  | 43087.9167 | 81 | 79
2017-12-18 22:30 | 60 | 59 |  |  | 43087.9375 | 78 | 77
2017-12-18 23:00 | 64 | 62 |  |  | 43087.9583 | 80 | 79
2017-12-18 23:30 | 57 | 56 |  |  | 43087.9792 | 74 | 73
2017-12-19 | 55 | 53 |  |  | 43088 | 71 | 70
2017-12-19 00:30 | 51 | 48 |  |  | 43088.0208 | 65 | 64
2017-12-19 01:00 | 46 | 43 |  |  | 43088.0417 | 60 | 59
2017-12-19 01:30 | 44 | 41 |  |  | 43088.0625 | 58 | 56
2017-12-19 02:00 | 45 | 42 |  |  | 43088.0833 | 58 | 56
2017-12-19 02:30 | 45 | 42 |  |  | 43088.1042 | 57 | 55
2017-12-19 03:00 | 45 | 41 |  |  | 43088.125 | 57 | 55
2017-12-19 03:30 | 44 | 40 |  |  | 43088.1458 | 57 | 54
2017-12-19 04:00 | 44 | 40 |  |  | 43088.1667 | 57 | 54
2017-12-19 04:30 | 44 | 40 |  |  | 43088.1875 | 56 | 54
2017-12-19 05:00 | 43 | 39 |  |  | 43088.2083 | 56 | 54
2017-12-19 05:30 | 41 | 38 |  |  | 43088.2292 | 55 | 53
2017-12-19 06:00 | 45 | 42 |  |  | 43088.25 | 60 | 59
2017-12-19 06:30 | 49 | 47 |  |  | 43088.2708 | 69 | 68
2017-12-19 07:00 | 52 | 51 |  |  | 43088.2917 | 77 | 77
2017-12-19 07:30 | 56 | 55 |  |  | 43088.3125 | 84 | 83
2017-12-19 08:00 | 56 | 55 |  |  | 43088.3333 | 87 | 86
2017-12-19 08:30 | 59 | 56 |  |  | 43088.3542 | 89 | 89
2017-12-19 09:00 | 62 | 58 |  |  | 43088.375 | 91 | 91
2017-12-19 09:30 | 63 | 59 |  |  | 43088.3958 | 92 | 92
2017-12-19 10:00 | 63 | 60 |  |  | 43088.4167 | 92 | 92
2017-12-19 10:30 | 67 | 62 |  |  | 43088.4375 | 93 | 92
2017-12-19 11:00 | 69 | 63 |  |  | 43088.4583 | 94 | 93
2017-12-19 11:30 | 70 | 64 |  |  | 43088.4792 | 94 | 92
2017-12-19 12:00 | 70 | 64 |  |  | 43088.5 | 94 | 93
2017-12-19 12:30 | 71 | 65 |  |  | 43088.5208 | 95 | 94
2017-12-19 13:00 | 74 | 67 |  |  | 43088.5417 | 98 | 96
2017-12-19 13:30 | 74 | 68 |  |  | 43088.5625 | 99 | 97
2017-12-19 14:00 | 78 | 69 |  |  | 43088.5833 | 99 | 96
2017-12-19 14:30 | 89 | 71 |  |  | 43088.6042 | 104 | 99
2017-12-19 15:00 | 91 | 73 |  |  | 43088.625 | 106 | 101
2017-12-19 15:30 | 94 | 76 |  |  | 43088.6458 | 109 | 105
2017-12-19 16:00 | 96 | 74 |  |  | 43088.6667 | 106 | 103
2017-12-19 16:30 | 95 | 69 |  |  | 43088.6875 | 100 | 98
2017-12-19 17:00 | 99 | 71 |  |  | 43088.7083 | 100 | 98
2017-12-19 17:30 | 100 | 71 |  |  | 43088.7292 | 98 | 97
2017-12-19 18:00 | 99 | 67 |  |  | 43088.75 | 94 | 92
2017-12-19 18:30 | 95 | 64 |  |  | 43088.7708 | 90 | 87
2017-12-19 19:00 | 91 | 65 |  |  | 43088.7917 | 92 | 89
2017-12-19 19:30 | 92 | 66 |  |  | 43088.8125 | 91 | 89
2017-12-19 20:00 | 94 | 67 |  |  | 43088.8333 | 92 | 90
2017-12-19 20:30 | 92 | 68 |  |  | 43088.8542 | 93 | 90
2017-12-19 21:00 | 88 | 67 |  |  | 43088.875 | 93 | 88
2017-12-19 21:30 | 87 | 65 |  |  | 43088.8958 | 91 | 86
2017-12-19 22:00 | 85 | 61 |  |  | 43088.9167 | 88 | 83
2017-12-19 22:30 | 78 | 61 |  |  | 43088.9375 | 85 | 82
2017-12-19 23:00 | 66 | 61 |  |  | 43088.9583 | 79 | 79
2017-12-19 23:30 | 63 | 57 |  |  | 43088.9792 | 76 | 76
2017-12-20 | 59 | 54 |  |  | 43089 | 72 | 72
2017-12-20 00:30 | 55 | 48 |  |  | 43089.0208 | 65 | 65
2017-12-20 01:00 | 53 | 45 |  |  | 43089.0417 | 60 | 60
2017-12-20 01:30 | 51 | 43 |  |  | 43089.0625 | 58 | 58
2017-12-20 02:00 | 51 | 42 |  |  | 43089.0833 | 57 | 57
2017-12-20 02:30 | 50 | 41 |  |  | 43089.1042 | 58 | 57
2017-12-20 03:00 | 49 | 40 |  |  | 43089.125 | 55 | 55
2017-12-20 03:30 | 48 | 39 |  |  | 43089.1458 | 54 | 54
2017-12-20 04:00 | 47 | 37 |  |  | 43089.1667 | 54 | 53
2017-12-20 04:30 | 48 | 38 |  |  | 43089.1875 | 55 | 54
2017-12-20 05:00 | 49 | 40 |  |  | 43089.2083 | 56 | 56
2017-12-20 05:30 | 51 | 43 |  |  | 43089.2292 | 60 | 60
2017-12-20 06:00 | 53 | 45 |  |  | 43089.25 | 64 | 63
2017-12-20 06:30 | 56 | 49 |  |  | 43089.2708 | 70 | 70
2017-12-20 07:00 | 72 | 53 |  |  | 43089.2917 | 80 | 78
2017-12-20 07:30 | 80 | 56 |  |  | 43089.3125 | 91 | 87
2017-12-20 08:00 | 82 | 60 |  |  | 43089.3333 | 96 | 91
2017-12-20 08:30 | 87 | 67 |  |  | 43089.3542 | 101 | 97
2017-12-20 09:00 | 87 | 68 |  |  | 43089.375 | 103 | 99
2017-12-20 09:30 | 86 | 67 |  |  | 43089.3958 | 102 | 98
2017-12-20 10:00 | 86 | 65 |  |  | 43089.4167 | 103 | 98
2017-12-20 10:30 | 88 | 68 |  |  | 43089.4375 | 105 | 100
2017-12-20 11:00 | 87 | 68 |  |  | 43089.4583 | 106 | 100
2017-12-20 11:30 | 90 | 71 |  |  | 43089.4792 | 107 | 102
2017-12-20 12:00 | 93 | 74 |  |  | 43089.5 | 108 | 104
2017-12-20 12:30 | 95 | 74 |  |  | 43089.5208 | 108 | 105
2017-12-20 13:00 | 103 | 79 |  |  | 43089.5417 | 110 | 110
2017-12-20 13:30 | 98 | 79 |  |  | 43089.5625 | 113 | 112
2017-12-20 14:00 | 101 | 82 |  |  | 43089.5833 | 114 | 114
2017-12-20 14:30 | 104 | 85 |  |  | 43089.6042 | 117 | 117
2017-12-20 15:00 | 108 | 89 |  |  | 43089.625 | 121 | 120
2017-12-20 15:30 | 110 | 92 |  |  | 43089.6458 | 124 | 123
2017-12-20 16:00 | 112 | 93 |  |  | 43089.6667 | 124 | 124
2017-12-20 16:30 | 114 | 94 |  |  | 43089.6875 | 124 | 124
2017-12-20 17:00 | 115 | 94 |  |  | 43089.7083 | 122 | 122
2017-12-20 17:30 | 113 | 85 |  |  | 43089.7292 | 114 | 114
2017-12-20 18:00 | 115 | 76 |  |  | 43089.75 | 106 | 106
2017-12-20 18:30 | 116 | 71 |  |  | 43089.7708 | 99 | 99
2017-12-20 19:00 | 111 | 71 |  |  | 43089.7917 | 99 | 98
2017-12-20 19:30 | 110 | 71 |  |  | 43089.8125 | 98 | 98
2017-12-20 20:00 | 110 | 72 |  |  | 43089.8333 | 100 | 99
2017-12-20 20:30 | 101 | 71 |  |  | 43089.8542 | 100 | 96
2017-12-20 21:00 | 97 | 70 |  |  | 43089.875 | 101 | 95
2017-12-20 21:30 | 93 | 65 |  |  | 43089.8958 | 95 | 90
2017-12-20 22:00 | 97 | 68 |  |  | 43089.9167 | 94 | 89
2017-12-20 22:30 | 97 | 69 |  |  | 43089.9375 | 94 | 90
2017-12-20 23:00 | 99 | 70 |  |  | 43089.9583 | 96 | 91
2017-12-20 23:30 | 87 | 67 |  |  | 43089.9792 | 88 | 87
2017-12-21 | 79 | 61 |  |  | 43090 | 79 | 79
2017-12-21 00:30 | 81 | 55 |  |  | 43090.0208 | 75 | 73
2017-12-21 01:00 | 78 | 51 |  |  | 43090.0417 | 68 | 67
2017-12-21 01:30 | 78 | 50 |  |  | 43090.0625 | 67 | 65
2017-12-21 02:00 | 78 | 48 |  |  | 43090.0833 | 67 | 65
2017-12-21 02:30 | 77 | 47 |  |  | 43090.1042 | 64 | 63
2017-12-21 03:00 | 75 | 44 |  |  | 43090.125 | 63 | 61
2017-12-21 03:30 | 74 | 44 |  |  | 43090.1458 | 61 | 60
2017-12-21 04:00 | 74 | 44 |  |  | 43090.1667 | 60 | 59
2017-12-21 04:30 | 73 | 43 |  |  | 43090.1875 | 61 | 59
2017-12-21 05:00 | 75 | 45 |  |  | 43090.2083 | 62 | 60
2017-12-21 05:30 | 75 | 47 |  |  | 43090.2292 | 64 | 63
2017-12-21 06:00 | 81 | 50 |  |  | 43090.25 | 71 | 68
2017-12-21 06:30 | 95 | 58 |  |  | 43090.2708 | 89 | 79
2017-12-21 07:00 | 95 | 62 |  |  | 43090.2917 | 96 | 86
2017-12-21 07:30 | 97 | 66 |  |  | 43090.3125 | 104 | 93
2017-12-21 08:00 | 99 | 68 |  |  | 43090.3333 | 107 | 99
2017-12-21 08:30 | 100 | 72 |  |  | 43090.3542 | 113 | 105
2017-12-21 09:00 | 102 | 74 |  |  | 43090.375 | 115 | 106
2017-12-21 09:30 | 112 | 76 |  |  | 43090.3958 | 113 | 109
2017-12-21 10:00 | 116 | 80 |  |  | 43090.4167 | 115 | 113
2017-12-21 10:30 | 117 | 83 |  |  | 43090.4375 | 117 | 115
2017-12-21 11:00 | 120 | 89 |  |  | 43090.4583 | 120 | 118
2017-12-21 11:30 | 121 | 91 |  |  | 43090.4792 | 120 | 117
2017-12-21 12:00 | 123 | 93 |  |  | 43090.5 | 122 | 120
2017-12-21 12:30 | 123 | 96 |  |  | 43090.5208 | 126 | 125
2017-12-21 13:00 | 120 | 94 |  |  | 43090.5417 | 124 | 122
2017-12-21 13:30 | 119 | 94 |  |  | 43090.5625 | 125 | 123
2017-12-21 14:00 | 122 | 98 |  |  | 43090.5833 | 128 | 125
2017-12-21 14:30 | 123 | 101 |  |  | 43090.6042 | 130 | 128
2017-12-21 15:00 | 124 | 101 |  |  | 43090.625 | 133 | 131
2017-12-21 15:30 | 125 | 100 |  |  | 43090.6458 | 133 | 131
2017-12-21 16:00 | 126 | 100 |  |  | 43090.6667 | 134 | 132
2017-12-21 16:30 | 126 | 96 |  |  | 43090.6875 | 129 | 128
2017-12-21 17:00 | 127 | 99 |  |  | 43090.7083 | 129 | 128
2017-12-21 17:30 | 109 | 95 |  |  | 43090.7292 | 123 | 123
2017-12-21 18:00 | 92 | 86 |  |  | 43090.75 | 117 | 117
2017-12-21 18:30 | 91 | 79 |  |  | 43090.7708 | 111 | 111
2017-12-21 19:00 | 92 | 81 |  |  | 43090.7917 | 113 | 112
2017-12-21 19:30 | 91 | 80 |  |  | 43090.8125 | 111 | 111
2017-12-21 20:00 | 93 | 81 |  |  | 43090.8333 | 113 | 113
2017-12-21 20:30 | 92 | 80 |  |  | 43090.8542 | 111 | 110
2017-12-21 21:00 | 87 | 76 |  |  | 43090.875 | 105 | 105
2017-12-21 21:30 | 79 | 71 |  |  | 43090.8958 | 101 | 101
2017-12-21 22:00 | 69 | 69 |  |  | 43090.9167 | 97 | 97
2017-12-21 22:30 | 68 | 68 |  |  | 43090.9375 | 96 | 96
2017-12-21 23:00 | 67 | 67 |  |  | 43090.9583 | 93 | 93
2017-12-21 23:30 | 67 | 66 |  |  | 43090.9792 | 92 | 92
2017-12-22 | 66 | 66 |  |  | 43091 | 88 | 88
2017-12-22 00:30 | 59 | 59 |  |  | 43091.0208 | 78 | 78
2017-12-22 01:00 | 52 | 52 |  |  | 43091.0417 | 72 | 72
2017-12-22 01:30 | 50 | 50 |  |  | 43091.0625 | 69 | 69
2017-12-22 02:00 | 48 | 48 |  |  | 43091.0833 | 66 | 66
2017-12-22 02:30 | 47 | 46 |  |  | 43091.1042 | 65 | 65
2017-12-22 03:00 | 45 | 45 |  |  | 43091.125 | 64 | 64
2017-12-22 03:30 | 45 | 45 |  |  | 43091.1458 | 63 | 63
2017-12-22 04:00 | 44 | 44 |  |  | 43091.1667 | 62 | 62
2017-12-22 04:30 | 45 | 45 |  |  | 43091.1875 | 63 | 63
2017-12-22 05:00 | 45 | 45 |  |  | 43091.2083 | 64 | 64
2017-12-22 05:30 | 48 | 48 |  |  | 43091.2292 | 66 | 66
2017-12-22 06:00 | 50 | 50 |  |  | 43091.25 | 71 | 71
2017-12-22 06:30 | 53 | 53 |  |  | 43091.2708 | 77 | 77
2017-12-22 07:00 | 56 | 56 |  |  | 43091.2917 | 81 | 81
2017-12-22 07:30 | 59 | 59 |  |  | 43091.3125 | 87 | 87
2017-12-22 08:00 | 67 | 65 |  |  | 43091.3333 | 97 | 96
2017-12-22 08:30 | 69 | 67 |  |  | 43091.3542 | 100 | 99
2017-12-22 09:00 | 73 | 69 |  |  | 43091.375 | 104 | 102
2017-12-22 09:30 | 76 | 72 |  |  | 43091.3958 | 107 | 105
2017-12-22 10:00 | 75 | 71 |  |  | 43091.4167 | 107 | 105
2017-12-22 10:30 | 74 | 70 |  |  | 43091.4375 | 104 | 102
2017-12-22 11:00 | 74 | 70 |  |  | 43091.4583 | 105 | 102
2017-12-22 11:30 | 73 | 68 |  |  | 43091.4792 | 105 | 102
2017-12-22 12:00 | 76 | 73 |  |  | 43091.5 | 106 | 104
2017-12-22 12:30 | 76 | 73 |  |  | 43091.5208 | 105 | 104
2017-12-22 13:00 | 66 | 63 |  |  | 43091.5417 | 95 | 94
2017-12-22 13:30 | 67 | 65 |  |  | 43091.5625 | 97 | 96
2017-12-22 14:00 | 72 | 70 |  |  | 43091.5833 | 98 | 98
2017-12-22 14:30 | 75 | 73 |  |  | 43091.6042 | 101 | 100
2017-12-22 15:00 | 78 | 75 |  |  | 43091.625 | 105 | 105
2017-12-22 15:30 | 77 | 75 |  |  | 43091.6458 | 103 | 102
2017-12-22 16:00 | 80 | 78 |  |  | 43091.6667 | 106 | 106
2017-12-22 16:30 | 82 | 79 |  |  | 43091.6875 | 107 | 107
2017-12-22 17:00 | 82 | 80 |  |  | 43091.7083 | 108 | 108
2017-12-22 17:30 | 81 | 80 |  |  | 43091.7292 | 107 | 107
2017-12-22 18:00 | 79 | 77 |  |  | 43091.75 | 104 | 104
2017-12-22 18:30 | 77 | 74 |  |  | 43091.7708 | 100 | 100
2017-12-22 19:00 | 80 | 77 |  |  | 43091.7917 | 102 | 101
2017-12-22 19:30 | 80 | 76 |  |  | 43091.8125 | 100 | 99
2017-12-22 20:00 | 77 | 74 |  |  | 43091.8333 | 98 | 97
2017-12-22 20:30 | 76 | 72 |  |  | 43091.8542 | 95 | 94
2017-12-22 21:00 | 75 | 69 |  |  | 43091.875 | 91 | 91
2017-12-22 21:30 | 74 | 67 |  |  | 43091.8958 | 89 | 88
2017-12-22 22:00 | 73 | 66 |  |  | 43091.9167 | 89 | 89
2017-12-22 22:30 | 72 | 66 |  |  | 43091.9375 | 88 | 88
2017-12-22 23:00 | 70 | 64 |  |  | 43091.9583 | 85 | 85
2017-12-22 23:30 | 67 | 61 |  |  | 43091.9792 | 81 | 81
2017-12-23 | 65 | 58 |  |  | 43092 | 78 | 77
2017-12-23 00:30 | 60 | 53 |  |  | 43092.0208 | 71 | 71
2017-12-23 01:00 | 57 | 51 |  |  | 43092.0417 | 69 | 69
2017-12-23 01:30 | 55 | 50 |  |  | 43092.0625 | 67 | 67
2017-12-23 02:00 | 54 | 49 |  |  | 43092.0833 | 67 | 66
2017-12-23 02:30 | 53 | 48 |  |  | 43092.1042 | 66 | 66
2017-12-23 03:00 | 52 | 47 |  |  | 43092.125 | 64 | 63
2017-12-23 03:30 | 51 | 45 |  |  | 43092.1458 | 62 | 62
2017-12-23 04:00 | 51 | 45 |  |  | 43092.1667 | 62 | 61
2017-12-23 04:30 | 49 | 44 |  |  | 43092.1875 | 63 | 62
2017-12-23 05:00 | 49 | 44 |  |  | 43092.2083 | 62 | 62
2017-12-23 05:30 | 47 | 43 |  |  | 43092.2292 | 62 | 61
2017-12-23 06:00 | 45 | 40 |  |  | 43092.25 | 61 | 60
2017-12-23 06:30 | 45 | 40 |  |  | 43092.2708 | 60 | 60
2017-12-23 07:00 | 47 | 41 |  |  | 43092.2917 | 62 | 62
2017-12-23 07:30 | 51 | 45 |  |  | 43092.3125 | 67 | 67
2017-12-23 08:00 | 54 | 48 |  |  | 43092.3333 | 70 | 70
2017-12-23 08:30 | 58 | 52 |  |  | 43092.3542 | 75 | 75
2017-12-23 09:00 | 61 | 56 |  |  | 43092.375 | 79 | 79
2017-12-23 09:30 | 61 | 56 |  |  | 43092.3958 | 80 | 80
2017-12-23 10:00 | 62 | 58 |  |  | 43092.4167 | 80 | 80
2017-12-23 10:30 | 62 | 58 |  |  | 43092.4375 | 81 | 81
2017-12-23 11:00 | 61 | 59 |  |  | 43092.4583 | 82 | 81
2017-12-23 11:30 | 62 | 61 |  |  | 43092.4792 | 83 | 82
2017-12-23 12:00 | 63 | 62 |  |  | 43092.5 | 84 | 84
2017-12-23 12:30 | 66 | 65 |  |  | 43092.5208 | 87 | 87
2017-12-23 13:00 | 65 | 64 |  |  | 43092.5417 | 86 | 86
2017-12-23 13:30 | 70 | 69 |  |  | 43092.5625 | 88 | 88
2017-12-23 14:00 | 67 | 66 |  |  | 43092.5833 | 81 | 81
2017-12-23 14:30 | 61 | 60 |  |  | 43092.6042 | 78 | 78
2017-12-23 15:00 | 67 | 66 |  |  | 43092.625 | 84 | 84
2017-12-23 15:30 | 66 | 65 |  |  | 43092.6458 | 85 | 85
2017-12-23 16:00 | 67 | 66 |  |  | 43092.6667 | 85 | 85
2017-12-23 16:30 | 69 | 68 |  |  | 43092.6875 | 86 | 86
2017-12-23 17:00 | 69 | 68 |  |  | 43092.7083 | 88 | 88
2017-12-23 17:30 | 70 | 69 |  |  | 43092.7292 | 88 | 88
2017-12-23 18:00 | 69 | 68 |  |  | 43092.75 | 88 | 88
2017-12-23 18:30 | 69 | 68 |  |  | 43092.7708 | 88 | 88
2017-12-23 19:00 | 71 | 70 |  |  | 43092.7917 | 89 | 89
2017-12-23 19:30 | 71 | 71 |  |  | 43092.8125 | 90 | 90
2017-12-23 20:00 | 71 | 71 |  |  | 43092.8333 | 91 | 91
2017-12-23 20:30 | 69 | 69 |  |  | 43092.8542 | 89 | 89
2017-12-23 21:00 | 68 | 68 |  |  | 43092.875 | 88 | 88
2017-12-23 21:30 | 65 | 65 |  |  | 43092.8958 | 85 | 85
2017-12-23 22:00 | 67 | 67 |  |  | 43092.9167 | 87 | 87
2017-12-23 22:30 | 67 | 67 |  |  | 43092.9375 | 86 | 86
2017-12-23 23:00 | 64 | 64 |  |  | 43092.9583 | 82 | 82
2017-12-23 23:30 | 60 | 60 |  |  | 43092.9792 | 78 | 77
2017-12-24 | 55 | 55 |  |  | 43093 | 71 | 71
2017-12-24 00:30 | 50 | 50 |  |  | 43093.0208 | 66 | 66
2017-12-24 01:00 | 48 | 47 |  |  | 43093.0417 | 63 | 63
2017-12-24 01:30 | 46 | 46 |  |  | 43093.0625 | 60 | 60
2017-12-24 02:00 | 46 | 46 |  |  | 43093.0833 | 61 | 61
2017-12-24 02:30 | 44 | 44 |  |  | 43093.1042 | 59 | 59
2017-12-24 03:00 | 44 | 44 |  |  | 43093.125 | 59 | 59
2017-12-24 03:30 | 44 | 44 |  |  | 43093.1458 | 58 | 58
2017-12-24 04:00 | 42 | 42 |  |  | 43093.1667 | 57 | 57
2017-12-24 04:30 | 40 | 40 |  |  | 43093.1875 | 54 | 54
2017-12-24 05:00 | 38 | 38 |  |  | 43093.2083 | 53 | 53
2017-12-24 05:30 | 35 | 34 |  |  | 43093.2292 | 50 | 50
2017-12-24 06:00 | 35 | 35 |  |  | 43093.25 | 51 | 51
2017-12-24 06:30 | 35 | 35 |  |  | 43093.2708 | 53 | 52
2017-12-24 07:00 | 37 | 37 |  |  | 43093.2917 | 55 | 55
2017-12-24 07:30 | 39 | 39 |  |  | 43093.3125 | 59 | 59
2017-12-24 08:00 | 41 | 41 |  |  | 43093.3333 | 60 | 60
2017-12-24 08:30 | 44 | 44 |  |  | 43093.3542 | 62 | 62
2017-12-24 09:00 | 44 | 44 |  |  | 43093.375 | 63 | 63
2017-12-24 09:30 | 45 | 45 |  |  | 43093.3958 | 64 | 64
2017-12-24 10:00 | 47 | 47 |  |  | 43093.4167 | 66 | 66
2017-12-24 10:30 | 50 | 49 |  |  | 43093.4375 | 68 | 68
2017-12-24 11:00 | 52 | 51 |  |  | 43093.4583 | 68 | 68
2017-12-24 11:30 | 50 | 50 |  |  | 43093.4792 | 68 | 68
2017-12-24 12:00 | 52 | 52 |  |  | 43093.5 | 70 | 69
2017-12-24 12:30 | 57 | 55 |  |  | 43093.5208 | 73 | 73
2017-12-24 13:00 | 60 | 58 |  |  | 43093.5417 | 76 | 75
2017-12-24 13:30 | 61 | 59 |  |  | 43093.5625 | 77 | 76
2017-12-24 14:00 | 62 | 61 |  |  | 43093.5833 | 79 | 77
2017-12-24 14:30 | 65 | 65 |  |  | 43093.6042 | 84 | 81
2017-12-24 15:00 | 74 | 70 |  |  | 43093.625 | 93 | 87
2017-12-24 15:30 | 77 | 72 |  |  | 43093.6458 | 95 | 90
2017-12-24 16:00 | 78 | 74 |  |  | 43093.6667 | 97 | 91
2017-12-24 16:30 | 78 | 74 |  |  | 43093.6875 | 98 | 93
2017-12-24 17:00 | 81 | 75 |  |  | 43093.7083 | 98 | 93
2017-12-24 17:30 | 82 | 75 |  |  | 43093.7292 | 97 | 93
2017-12-24 18:00 | 84 | 76 |  |  | 43093.75 | 96 | 93
2017-12-24 18:30 | 81 | 72 |  |  | 43093.7708 | 92 | 90
2017-12-24 19:00 | 81 | 72 |  |  | 43093.7917 | 94 | 91
2017-12-24 19:30 | 82 | 72 |  |  | 43093.8125 | 95 | 93
2017-12-24 20:00 | 82 | 72 |  |  | 43093.8333 | 95 | 92
2017-12-24 20:30 | 81 | 71 |  |  | 43093.8542 | 94 | 91
2017-12-24 21:00 | 78 | 67 |  |  | 43093.875 | 90 | 87
2017-12-24 21:30 | 75 | 65 |  |  | 43093.8958 | 88 | 85
2017-12-24 22:00 | 77 | 65 |  |  | 43093.9167 | 88 | 85
2017-12-24 22:30 | 67 | 64 |  |  | 43093.9375 | 82 | 82
2017-12-24 23:00 | 66 | 62 |  |  | 43093.9583 | 79 | 79
2017-12-24 23:30 | 62 | 58 |  |  | 43093.9792 | 74 | 74
2017-12-25 | 58 | 52 |  |  | 43094 | 68 | 68
2017-12-25 00:30 | 54 | 46 |  |  | 43094.0208 | 61 | 61
2017-12-25 01:00 | 51 | 43 |  |  | 43094.0417 | 56 | 56
2017-12-25 01:30 | 50 | 42 |  |  | 43094.0625 | 56 | 56
2017-12-25 02:00 | 51 | 41 |  |  | 43094.0833 | 54 | 54
2017-12-25 02:30 | 49 | 39 |  |  | 43094.1042 | 53 | 53
2017-12-25 03:00 | 48 | 38 |  |  | 43094.125 | 51 | 51
2017-12-25 03:30 | 48 | 38 |  |  | 43094.1458 | 51 | 51
2017-12-25 04:00 | 49 | 39 |  |  | 43094.1667 | 52 | 52
2017-12-25 04:30 | 47 | 36 |  |  | 43094.1875 | 49 | 49
2017-12-25 05:00 | 45 | 34 |  |  | 43094.2083 | 48 | 48
2017-12-25 05:30 | 45 | 32 |  |  | 43094.2292 | 47 | 47
2017-12-25 06:00 | 44 | 31 |  |  | 43094.25 | 47 | 47
2017-12-25 06:30 | 46 | 35 |  |  | 43094.2708 | 53 | 53
2017-12-25 07:00 | 47 | 37 |  |  | 43094.2917 | 56 | 56
2017-12-25 07:30 | 49 | 41 |  |  | 43094.3125 | 60 | 60
2017-12-25 08:00 | 51 | 43 |  |  | 43094.3333 | 61 | 61
2017-12-25 08:30 | 52 | 44 |  |  | 43094.3542 | 62 | 62
2017-12-25 09:00 | 52 | 45 |  |  | 43094.375 | 62 | 62
2017-12-25 09:30 | 52 | 45 |  |  | 43094.3958 | 63 | 62
2017-12-25 10:00 | 51 | 46 |  |  | 43094.4167 | 64 | 64
2017-12-25 10:30 | 53 | 48 |  |  | 43094.4375 | 65 | 64
2017-12-25 11:00 | 55 | 51 |  |  | 43094.4583 | 66 | 66
2017-12-25 11:30 | 56 | 53 |  |  | 43094.4792 | 69 | 68
2017-12-25 12:00 | 58 | 54 |  |  | 43094.5 | 70 | 70
2017-12-25 12:30 | 60 | 56 |  |  | 43094.5208 | 72 | 72
2017-12-25 13:00 | 59 | 55 |  |  | 43094.5417 | 71 | 70
2017-12-25 13:30 | 71 | 59 |  |  | 43094.5625 | 81 | 77
2017-12-25 14:00 | 72 | 60 |  |  | 43094.5833 | 83 | 78
2017-12-25 14:30 | 75 | 62 |  |  | 43094.6042 | 85 | 80
2017-12-25 15:00 | 77 | 64 |  |  | 43094.625 | 87 | 82
2017-12-25 15:30 | 77 | 65 |  |  | 43094.6458 | 87 | 82
2017-12-25 16:00 | 77 | 67 |  |  | 43094.6667 | 90 | 85
2017-12-25 16:30 | 78 | 68 |  |  | 43094.6875 | 91 | 86
2017-12-25 17:00 | 77 | 65 |  |  | 43094.7083 | 90 | 85
2017-12-25 17:30 | 78 | 64 |  |  | 43094.7292 | 87 | 83
2017-12-25 18:00 | 79 | 63 |  |  | 43094.75 | 85 | 82
2017-12-25 18:30 | 79 | 64 |  |  | 43094.7708 | 85 | 82
2017-12-25 19:00 | 81 | 66 |  |  | 43094.7917 | 91 | 88
2017-12-25 19:30 | 80 | 66 |  |  | 43094.8125 | 89 | 86
2017-12-25 20:00 | 77 | 63 |  |  | 43094.8333 | 86 | 82
2017-12-25 20:30 | 69 | 61 |  |  | 43094.8542 | 80 | 79
2017-12-25 21:00 | 61 | 57 |  |  | 43094.875 | 75 | 75
2017-12-25 21:30 | 59 | 55 |  |  | 43094.8958 | 72 | 72
2017-12-25 22:00 | 58 | 54 |  |  | 43094.9167 | 72 | 72
2017-12-25 22:30 | 58 | 53 |  |  | 43094.9375 | 71 | 71
2017-12-25 23:00 | 53 | 48 |  |  | 43094.9583 | 68 | 68
2017-12-25 23:30 | 50 | 43 |  |  | 43094.9792 | 62 | 62
2017-12-26 | 48 | 41 |  |  | 43095 | 59 | 59
2017-12-26 00:30 | 46 | 38 |  |  | 43095.0208 | 56 | 56
2017-12-26 01:00 | 45 | 36 |  |  | 43095.0417 | 52 | 52
2017-12-26 01:30 | 45 | 35 |  |  | 43095.0625 | 51 | 51
2017-12-26 02:00 | 46 | 36 |  |  | 43095.0833 | 53 | 52
2017-12-26 02:30 | 47 | 37 |  |  | 43095.1042 | 52 | 52
2017-12-26 03:00 | 45 | 35 |  |  | 43095.125 | 50 | 50
2017-12-26 03:30 | 46 | 35 |  |  | 43095.1458 | 50 | 50
2017-12-26 04:00 | 46 | 35 |  |  | 43095.1667 | 50 | 50
2017-12-26 04:30 | 46 | 36 |  |  | 43095.1875 | 50 | 50
2017-12-26 05:00 | 47 | 36 |  |  | 43095.2083 | 50 | 50
2017-12-26 05:30 | 46 | 34 |  |  | 43095.2292 | 50 | 50
2017-12-26 06:00 | 46 | 34 |  |  | 43095.25 | 50 | 50
2017-12-26 06:30 | 46 | 35 |  |  | 43095.2708 | 54 | 54
2017-12-26 07:00 | 45 | 34 |  |  | 43095.2917 | 53 | 53
2017-12-26 07:30 | 45 | 36 |  |  | 43095.3125 | 56 | 56
2017-12-26 08:00 | 45 | 37 |  |  | 43095.3333 | 58 | 58
2017-12-26 08:30 | 46 | 38 |  |  | 43095.3542 | 60 | 59
2017-12-26 09:00 | 49 | 42 |  |  | 43095.375 | 62 | 61
2017-12-26 09:30 | 50 | 44 |  |  | 43095.3958 | 64 | 63
2017-12-26 10:00 | 52 | 45 |  |  | 43095.4167 | 68 | 68
2017-12-26 10:30 | 53 | 46 |  |  | 43095.4375 | 67 | 67
2017-12-26 11:00 | 56 | 51 |  |  | 43095.4583 | 69 | 68
2017-12-26 11:30 | 57 | 51 |  |  | 43095.4792 | 67 | 67
2017-12-26 12:00 | 57 | 50 |  |  | 43095.5 | 66 | 66
2017-12-26 12:30 | 55 | 47 |  |  | 43095.5208 | 64 | 64
2017-12-26 13:00 | 54 | 47 |  |  | 43095.5417 | 64 | 64
2017-12-26 13:30 | 53 | 47 |  |  | 43095.5625 | 64 | 63
2017-12-26 14:00 | 54 | 48 |  |  | 43095.5833 | 65 | 65
2017-12-26 14:30 | 55 | 49 |  |  | 43095.6042 | 66 | 65
2017-12-26 15:00 | 56 | 51 |  |  | 43095.625 | 66 | 65
2017-12-26 15:30 | 76 | 61 |  |  | 43095.6458 | 83 | 79
2017-12-26 16:00 | 85 | 63 |  |  | 43095.6667 | 91 | 85
2017-12-26 16:30 | 87 | 64 |  |  | 43095.6875 | 91 | 85
2017-12-26 17:00 | 90 | 67 |  |  | 43095.7083 | 94 | 88
2017-12-26 17:30 | 91 | 68 |  |  | 43095.7292 | 96 | 90
2017-12-26 18:00 | 91 | 68 |  |  | 43095.75 | 96 | 91
2017-12-26 18:30 | 92 | 68 |  |  | 43095.7708 | 94 | 89
2017-12-26 19:00 | 93 | 69 |  |  | 43095.7917 | 95 | 90
2017-12-26 19:30 | 85 | 68 |  |  | 43095.8125 | 90 | 88
2017-12-26 20:00 | 77 | 65 |  |  | 43095.8333 | 85 | 84
2017-12-26 20:30 | 76 | 63 |  |  | 43095.8542 | 83 | 83
2017-12-26 21:00 | 64 | 61 |  |  | 43095.875 | 78 | 78
2017-12-26 21:30 | 61 | 58 |  |  | 43095.8958 | 77 | 77
2017-12-26 22:00 | 61 | 58 |  |  | 43095.9167 | 78 | 77
2017-12-26 22:30 | 61 | 57 |  |  | 43095.9375 | 76 | 75
2017-12-26 23:00 | 58 | 54 |  |  | 43095.9583 | 72 | 70
2017-12-26 23:30 | 55 | 50 |  |  | 43095.9792 | 68 | 67
2017-12-27 | 51 | 47 |  |  | 43096 | 63 | 62
2017-12-27 00:30 | 46 | 41 |  |  | 43096.0208 | 59 | 57
2017-12-27 01:00 | 43 | 39 |  |  | 43096.0417 | 53 | 52
2017-12-27 01:30 | 42 | 37 |  |  | 43096.0625 | 53 | 52
2017-12-27 02:00 | 42 | 37 |  |  | 43096.0833 | 53 | 52
2017-12-27 02:30 | 43 | 38 |  |  | 43096.1042 | 55 | 53
2017-12-27 03:00 | 43 | 38 |  |  | 43096.125 | 53 | 52
2017-12-27 03:30 | 43 | 38 |  |  | 43096.1458 | 53 | 52
2017-12-27 04:00 | 43 | 38 |  |  | 43096.1667 | 53 | 52
2017-12-27 04:30 | 43 | 38 |  |  | 43096.1875 | 53 | 52
2017-12-27 05:00 | 42 | 38 |  |  | 43096.2083 | 53 | 52
2017-12-27 05:30 | 43 | 38 |  |  | 43096.2292 | 54 | 54
2017-12-27 06:00 | 43 | 39 |  |  | 43096.25 | 55 | 55
2017-12-27 06:30 | 46 | 43 |  |  | 43096.2708 | 62 | 62
2017-12-27 07:00 | 48 | 46 |  |  | 43096.2917 | 66 | 66
2017-12-27 07:30 | 52 | 49 |  |  | 43096.3125 | 72 | 72
2017-12-27 08:00 | 58 | 53 |  |  | 43096.3333 | 77 | 77
2017-12-27 08:30 | 60 | 55 |  |  | 43096.3542 | 80 | 80
2017-12-27 09:00 | 61 | 58 |  |  | 43096.375 | 84 | 84
2017-12-27 09:30 | 65 | 62 |  |  | 43096.3958 | 85 | 85
2017-12-27 10:00 | 65 | 62 |  |  | 43096.4167 | 86 | 85
2017-12-27 10:30 | 65 | 62 |  |  | 43096.4375 | 83 | 83
2017-12-27 11:00 | 63 | 60 |  |  | 43096.4583 | 82 | 82
2017-12-27 11:30 | 62 | 60 |  |  | 43096.4792 | 81 | 81
2017-12-27 12:00 | 63 | 61 |  |  | 43096.5 | 82 | 81
2017-12-27 12:30 | 67 | 65 |  |  | 43096.5208 | 85 | 85
2017-12-27 13:00 | 72 | 70 |  |  | 43096.5417 | 87 | 87
2017-12-27 13:30 | 75 | 73 |  |  | 43096.5625 | 90 | 90
2017-12-27 14:00 | 77 | 75 |  |  | 43096.5833 | 94 | 94
2017-12-27 14:30 | 79 | 76 |  |  | 43096.6042 | 91 | 91
2017-12-27 15:00 | 74 | 72 |  |  | 43096.625 | 89 | 89
2017-12-27 15:30 | 77 | 75 |  |  | 43096.6458 | 95 | 95
2017-12-27 16:00 | 80 | 77 |  |  | 43096.6667 | 98 | 98
2017-12-27 16:30 | 84 | 81 |  |  | 43096.6875 | 99 | 99
2017-12-27 17:00 | 84 | 82 |  |  | 43096.7083 | 101 | 101
2017-12-27 17:30 | 84 | 81 |  |  | 43096.7292 | 102 | 102
2017-12-27 18:00 | 84 | 81 |  |  | 43096.75 | 100 | 100
2017-12-27 18:30 | 80 | 77 |  |  | 43096.7708 | 94 | 94
2017-12-27 19:00 | 77 | 74 |  |  | 43096.7917 | 93 | 92
2017-12-27 19:30 | 75 | 73 |  |  | 43096.8125 | 90 | 90
2017-12-27 20:00 | 75 | 72 |  |  | 43096.8333 | 90 | 90
2017-12-27 20:30 | 75 | 72 |  |  | 43096.8542 | 89 | 89
2017-12-27 21:00 | 72 | 69 |  |  | 43096.875 | 86 | 86
2017-12-27 21:30 | 69 | 66 |  |  | 43096.8958 | 82 | 82
2017-12-27 22:00 | 69 | 64 |  |  | 43096.9167 | 80 | 80
2017-12-27 22:30 | 69 | 63 |  |  | 43096.9375 | 78 | 78
2017-12-27 23:00 | 67 | 61 |  |  | 43096.9583 | 75 | 75
2017-12-27 23:30 | 63 | 57 |  |  | 43096.9792 | 72 | 72
2017-12-28 | 59 | 52 |  |  | 43097 | 66 | 66
2017-12-28 00:30 | 55 | 47 |  |  | 43097.0208 | 61 | 61
2017-12-28 01:00 | 48 | 43 |  |  | 43097.0417 | 56 | 56
2017-12-28 01:30 | 49 | 45 |  |  | 43097.0625 | 59 | 58
2017-12-28 02:00 | 50 | 45 |  |  | 43097.0833 | 59 | 57
2017-12-28 02:30 | 49 | 43 |  |  | 43097.1042 | 57 | 55
2017-12-28 03:00 | 47 | 42 |  |  | 43097.125 | 56 | 54
2017-12-28 03:30 | 46 | 40 |  |  | 43097.1458 | 54 | 52
2017-12-28 04:00 | 45 | 39 |  |  | 43097.1667 | 53 | 50
2017-12-28 04:30 | 44 | 38 |  |  | 43097.1875 | 51 | 49
2017-12-28 05:00 | 44 | 38 |  |  | 43097.2083 | 51 | 49
2017-12-28 05:30 | 44 | 39 |  |  | 43097.2292 | 53 | 51
2017-12-28 06:00 | 46 | 41 |  |  | 43097.25 | 56 | 54
2017-12-28 06:30 | 49 | 45 |  |  | 43097.2708 | 62 | 61
2017-12-28 07:00 | 51 | 49 |  |  | 43097.2917 | 66 | 66
2017-12-28 07:30 | 53 | 51 |  |  | 43097.3125 | 71 | 71
2017-12-28 08:00 | 56 | 55 |  |  | 43097.3333 | 76 | 76
2017-12-28 08:30 | 58 | 57 |  |  | 43097.3542 | 83 | 83
2017-12-28 09:00 | 57 | 57 |  |  | 43097.375 | 84 | 84
2017-12-28 09:30 | 59 | 59 |  |  | 43097.3958 | 86 | 86
2017-12-28 10:00 | 60 | 60 |  |  | 43097.4167 | 85 | 85
2017-12-28 10:30 | 62 | 62 |  |  | 43097.4375 | 89 | 89
2017-12-28 11:00 | 65 | 65 |  |  | 43097.4583 | 92 | 92
2017-12-28 11:30 | 64 | 64 |  |  | 43097.4792 | 91 | 91
2017-12-28 12:00 | 62 | 62 |  |  | 43097.5 | 90 | 90
2017-12-28 12:30 | 63 | 63 |  |  | 43097.5208 | 88 | 88
2017-12-28 13:00 | 59 | 59 |  |  | 43097.5417 | 82 | 82
2017-12-28 13:30 | 56 | 56 |  |  | 43097.5625 | 81 | 81
2017-12-28 14:00 | 58 | 58 |  |  | 43097.5833 | 84 | 84
2017-12-28 14:30 | 66 | 66 |  |  | 43097.6042 | 89 | 89
2017-12-28 15:00 | 73 | 73 |  |  | 43097.625 | 91 | 91
2017-12-28 15:30 | 74 | 74 |  |  | 43097.6458 | 93 | 93
2017-12-28 16:00 | 76 | 76 |  |  | 43097.6667 | 97 | 97
2017-12-28 16:30 | 72 | 72 |  |  | 43097.6875 | 96 | 96
2017-12-28 17:00 | 72 | 72 |  |  | 43097.7083 | 95 | 95
2017-12-28 17:30 | 75 | 75 |  |  | 43097.7292 | 95 | 95
2017-12-28 18:00 | 76 | 76 |  |  | 43097.75 | 95 | 95
2017-12-28 18:30 | 74 | 74 |  |  | 43097.7708 | 92 | 92
2017-12-28 19:00 | 77 | 76 |  |  | 43097.7917 | 94 | 94
2017-12-28 19:30 | 78 | 78 |  |  | 43097.8125 | 94 | 94
2017-12-28 20:00 | 77 | 77 |  |  | 43097.8333 | 93 | 93
2017-12-28 20:30 | 77 | 77 |  |  | 43097.8542 | 93 | 93
2017-12-28 21:00 | 70 | 70 |  |  | 43097.875 | 87 | 86
2017-12-28 21:30 | 64 | 63 |  |  | 43097.8958 | 80 | 80
2017-12-28 22:00 | 61 | 61 |  |  | 43097.9167 | 78 | 78
2017-12-28 22:30 | 61 | 58 |  |  | 43097.9375 | 75 | 75
2017-12-28 23:00 | 59 | 56 |  |  | 43097.9583 | 71 | 71
2017-12-28 23:30 | 55 | 53 |  |  | 43097.9792 | 68 | 67
2017-12-29 | 53 | 50 |  |  | 43098 | 64 | 63
2017-12-29 00:30 | 48 | 45 |  |  | 43098.0208 | 60 | 59
2017-12-29 01:00 | 44 | 41 |  |  | 43098.0417 | 54 | 53
2017-12-29 01:30 | 44 | 40 |  |  | 43098.0625 | 54 | 53
2017-12-29 02:00 | 46 | 42 |  |  | 43098.0833 | 55 | 54
2017-12-29 02:30 | 45 | 41 |  |  | 43098.1042 | 54 | 52
2017-12-29 03:00 | 44 | 40 |  |  | 43098.125 | 53 | 52
2017-12-29 03:30 | 44 | 40 |  |  | 43098.1458 | 53 | 52
2017-12-29 04:00 | 44 | 40 |  |  | 43098.1667 | 53 | 52
2017-12-29 04:30 | 42 | 38 |  |  | 43098.1875 | 51 | 49
2017-12-29 05:00 | 43 | 38 |  |  | 43098.2083 | 52 | 50
2017-12-29 05:30 | 44 | 40 |  |  | 43098.2292 | 55 | 53
2017-12-29 06:00 | 48 | 44 |  |  | 43098.25 | 59 | 58
2017-12-29 06:30 | 49 | 46 |  |  | 43098.2708 | 63 | 62
2017-12-29 07:00 | 51 | 49 |  |  | 43098.2917 | 68 | 68
2017-12-29 07:30 | 52 | 50 |  |  | 43098.3125 | 73 | 72
2017-12-29 08:00 | 50 | 48 |  |  | 43098.3333 | 71 | 71
2017-12-29 08:30 | 42 | 40 |  |  | 43098.3542 | 86 | 86
2017-12-29 09:00 | 45 | 41 |  |  | 43098.375 | 89 | 88
2017-12-29 09:30 | 44 | 41 |  |  | 43098.3958 | 91 | 89
2017-12-29 10:00 | 44 | 41 |  |  | 43098.4167 | 91 | 89
2017-12-29 10:30 | 48 | 45 |  |  | 43098.4375 | 92 | 91
2017-12-29 11:00 | 50 | 47 |  |  | 43098.4583 | 93 | 92
2017-12-29 11:30 | 50 | 48 |  |  | 43098.4792 | 93 | 91
2017-12-29 12:00 | 50 | 47 |  |  | 43098.5 | 89 | 87
2017-12-29 12:30 | 57 | 55 |  |  | 43098.5208 | 76 | 75
2017-12-29 13:00 | 59 | 57 |  |  | 43098.5417 | 77 | 75
2017-12-29 13:30 | 67 | 65 |  |  | 43098.5625 | 84 | 83
2017-12-29 14:00 | 74 | 73 |  |  | 43098.5833 | 86 | 85
2017-12-29 14:30 | 76 | 74 |  |  | 43098.6042 | 92 | 91
2017-12-29 15:00 | 73 | 71 |  |  | 43098.625 | 88 | 87
2017-12-29 15:30 | 74 | 72 |  |  | 43098.6458 | 91 | 89
2017-12-29 16:00 | 81 | 77 |  |  | 43098.6667 | 95 | 95
2017-12-29 16:30 | 87 | 83 |  |  | 43098.6875 | 102 | 102
2017-12-29 17:00 | 88 | 84 |  |  | 43098.7083 | 102 | 102
2017-12-29 17:30 | 86 | 81 |  |  | 43098.7292 | 100 | 100
2017-12-29 18:00 | 81 | 75 |  |  | 43098.75 | 94 | 93
2017-12-29 18:30 | 79 | 73 |  |  | 43098.7708 | 90 | 89
2017-12-29 19:00 | 78 | 72 |  |  | 43098.7917 | 89 | 89
2017-12-29 19:30 | 78 | 73 |  |  | 43098.8125 | 89 | 89
2017-12-29 20:00 | 78 | 73 |  |  | 43098.8333 | 89 | 89
2017-12-29 20:30 | 79 | 73 |  |  | 43098.8542 | 89 | 88
2017-12-29 21:00 | 75 | 71 |  |  | 43098.875 | 85 | 85
2017-12-29 21:30 | 74 | 70 |  |  | 43098.8958 | 85 | 85
2017-12-29 22:00 | 72 | 67 |  |  | 43098.9167 | 84 | 84
2017-12-29 22:30 | 71 | 66 |  |  | 43098.9375 | 83 | 83
2017-12-29 23:00 | 70 | 64 |  |  | 43098.9583 | 78 | 78
2017-12-29 23:30 | 64 | 58 |  |  | 43098.9792 | 73 | 73
2017-12-30 | 59 | 52 |  |  | 43099 | 67 | 67
2017-12-30 00:30 | 59 | 51 |  |  | 43099.0208 | 66 | 66
2017-12-30 01:00 | 57 | 49 |  |  | 43099.0417 | 63 | 63
2017-12-30 01:30 | 57 | 48 |  |  | 43099.0625 | 62 | 62
2017-12-30 02:00 | 60 | 50 |  |  | 43099.0833 | 64 | 64
2017-12-30 02:30 | 60 | 50 |  |  | 43099.1042 | 64 | 63
2017-12-30 03:00 | 59 | 49 |  |  | 43099.125 | 62 | 62
2017-12-30 03:30 | 57 | 47 |  |  | 43099.1458 | 60 | 60
2017-12-30 04:00 | 56 | 46 |  |  | 43099.1667 | 60 | 60
2017-12-30 04:30 | 57 | 46 |  |  | 43099.1875 | 61 | 61
2017-12-30 05:00 | 59 | 48 |  |  | 43099.2083 | 62 | 61
2017-12-30 05:30 | 60 | 49 |  |  | 43099.2292 | 63 | 62
2017-12-30 06:00 | 59 | 47 |  |  | 43099.25 | 62 | 61
2017-12-30 06:30 | 58 | 47 |  |  | 43099.2708 | 63 | 62
2017-12-30 07:00 | 57 | 47 |  |  | 43099.2917 | 63 | 63
2017-12-30 07:30 | 57 | 48 |  |  | 43099.3125 | 63 | 63
2017-12-30 08:00 | 58 | 51 |  |  | 43099.3333 | 68 | 68
2017-12-30 08:30 | 59 | 53 |  |  | 43099.3542 | 70 | 70
2017-12-30 09:00 | 63 | 58 |  |  | 43099.375 | 76 | 76
2017-12-30 09:30 | 63 | 58 |  |  | 43099.3958 | 74 | 74
2017-12-30 10:00 | 64 | 59 |  |  | 43099.4167 | 75 | 75
2017-12-30 10:30 | 71 | 67 |  |  | 43099.4375 | 82 | 82
2017-12-30 11:00 | 71 | 68 |  |  | 43099.4583 | 83 | 83
2017-12-30 11:30 | 69 | 65 |  |  | 43099.4792 | 80 | 80
2017-12-30 12:00 | 73 | 69 |  |  | 43099.5 | 85 | 85
2017-12-30 12:30 | 77 | 73 |  |  | 43099.5208 | 86 | 86
2017-12-30 13:00 | 79 | 75 |  |  | 43099.5417 | 90 | 90
2017-12-30 13:30 | 78 | 74 |  |  | 43099.5625 | 92 | 92
2017-12-30 14:00 | 76 | 72 |  |  | 43099.5833 | 86 | 86
2017-12-30 14:30 | 79 | 76 |  |  | 43099.6042 | 92 | 92
2017-12-30 15:00 | 78 | 75 |  |  | 43099.625 | 91 | 91
2017-12-30 15:30 | 79 | 75 |  |  | 43099.6458 | 90 | 90
2017-12-30 16:00 | 80 | 76 |  |  | 43099.6667 | 92 | 92
2017-12-30 16:30 | 83 | 80 |  |  | 43099.6875 | 96 | 96
2017-12-30 17:00 | 84 | 82 |  |  | 43099.7083 | 97 | 97
2017-12-30 17:30 | 85 | 83 |  |  | 43099.7292 | 99 | 99
2017-12-30 18:00 | 84 | 81 |  |  | 43099.75 | 97 | 97
2017-12-30 18:30 | 83 | 80 |  |  | 43099.7708 | 96 | 96
2017-12-30 19:00 | 85 | 81 |  |  | 43099.7917 | 100 | 100
2017-12-30 19:30 | 84 | 82 |  |  | 43099.8125 | 99 | 99
2017-12-30 20:00 | 84 | 82 |  |  | 43099.8333 | 100 | 100
2017-12-30 20:30 | 82 | 79 |  |  | 43099.8542 | 98 | 98
2017-12-30 21:00 | 80 | 76 |  |  | 43099.875 | 94 | 94
2017-12-30 21:30 | 78 | 74 |  |  | 43099.8958 | 92 | 92
2017-12-30 22:00 | 76 | 72 |  |  | 43099.9167 | 90 | 89
2017-12-30 22:30 | 75 | 70 |  |  | 43099.9375 | 87 | 87
2017-12-30 23:00 | 72 | 67 |  |  | 43099.9583 | 83 | 83
2017-12-30 23:30 | 66 | 61 |  |  | 43099.9792 | 78 | 78
2017-12-31 | 62 | 57 |  |  | 43100 | 73 | 73
2017-12-31 00:30 | 63 | 56 |  |  | 43100.0208 | 71 | 71
2017-12-31 01:00 | 59 | 52 |  |  | 43100.0417 | 66 | 66
2017-12-31 01:30 | 58 | 50 |  |  | 43100.0625 | 64 | 64
2017-12-31 02:00 | 57 | 49 |  |  | 43100.0833 | 64 | 64
2017-12-31 02:30 | 57 | 49 |  |  | 43100.1042 | 62 | 62
2017-12-31 03:00 | 56 | 48 |  |  | 43100.125 | 61 | 61
2017-12-31 03:30 | 55 | 46 |  |  | 43100.1458 | 61 | 61
2017-12-31 04:00 | 55 | 46 |  |  | 43100.1667 | 59 | 59
2017-12-31 04:30 | 56 | 46 |  |  | 43100.1875 | 61 | 61
2017-12-31 05:00 | 57 | 46 |  |  | 43100.2083 | 62 | 62
2017-12-31 05:30 | 55 | 44 |  |  | 43100.2292 | 58 | 58
2017-12-31 06:00 | 53 | 42 |  |  | 43100.25 | 57 | 57
2017-12-31 06:30 | 51 | 42 |  |  | 43100.2708 | 59 | 59
2017-12-31 07:00 | 48 | 43 |  |  | 43100.2917 | 61 | 60
2017-12-31 07:30 | 50 | 46 |  |  | 43100.3125 | 64 | 62
2017-12-31 08:00 | 52 | 48 |  |  | 43100.3333 | 65 | 64
2017-12-31 08:30 | 55 | 52 |  |  | 43100.3542 | 70 | 69
2017-12-31 09:00 | 58 | 56 |  |  | 43100.375 | 74 | 74
2017-12-31 09:30 | 60 | 59 |  |  | 43100.3958 | 77 | 77
2017-12-31 10:00 | 66 | 65 |  |  | 43100.4167 | 80 | 80
2017-12-31 10:30 | 70 | 69 |  |  | 43100.4375 | 84 | 83
2017-12-31 11:00 | 78 | 77 |  |  | 43100.4583 | 90 | 90
2017-12-31 11:30 | 80 | 80 |  |  | 43100.4792 | 92 | 92
2017-12-31 12:00 | 85 | 83 |  |  | 43100.5 | 96 | 96
2017-12-31 12:30 | 84 | 82 |  |  | 43100.5208 | 100 | 100
2017-12-31 13:00 | 88 | 86 |  |  | 43100.5417 | 99 | 99
2017-12-31 13:30 | 88 | 86 |  |  | 43100.5625 | 98 | 98
2017-12-31 14:00 | 89 | 87 |  |  | 43100.5833 | 102 | 102
2017-12-31 14:30 | 92 | 90 |  |  | 43100.6042 | 105 | 105
2017-12-31 15:00 | 95 | 92 |  |  | 43100.625 | 101 | 101
2017-12-31 15:30 | 91 | 88 |  |  | 43100.6458 | 102 | 102
2017-12-31 16:00 | 89 | 85 |  |  | 43100.6667 | 104 | 104
2017-12-31 16:30 | 85 | 81 |  |  | 43100.6875 | 100 | 100
2017-12-31 17:00 | 84 | 80 |  |  | 43100.7083 | 99 | 99
2017-12-31 17:30 | 83 | 79 |  |  | 43100.7292 | 97 | 97
2017-12-31 18:00 | 79 | 75 |  |  | 43100.75 | 93 | 93
2017-12-31 18:30 | 78 | 74 |  |  | 43100.7708 | 92 | 92
2017-12-31 19:00 | 77 | 73 |  |  | 43100.7917 | 93 | 93
2017-12-31 19:30 | 76 | 73 |  |  | 43100.8125 | 92 | 92
2017-12-31 20:00 | 75 | 72 |  |  | 43100.8333 | 91 | 91
2017-12-31 20:30 | 73 | 69 |  |  | 43100.8542 | 89 | 89
2017-12-31 21:00 | 68 | 65 |  |  | 43100.875 | 85 | 85
2017-12-31 21:30 | 65 | 61 |  |  | 43100.8958 | 82 | 82
2017-12-31 22:00 | 66 | 62 |  |  | 43100.9167 | 82 | 82
2017-12-31 22:30 | 65 | 61 |  |  | 43100.9375 | 79 | 79
2017-12-31 23:00 | 63 | 58 |  |  | 43100.9583 | 76 | 76
2017-12-31 23:30 | 59 | 54 |  |  | 43100.9792 | 71 | 71
2018-01-01 | 57 | 51 |  |  | 43101 | 67 | 67
2018-01-01 00:30 | 52 | 46 |  |  | 43101.0208 | 61 | 61
2018-01-01 01:00 | 51 | 44 |  |  | 43101.0417 | 60 | 60
2018-01-01 01:30 | 51 | 43 |  |  | 43101.0625 | 59 | 58
2018-01-01 02:00 | 52 | 43 |  |  | 43101.0833 | 59 | 59
2018-01-01 02:30 | 52 | 43 |  |  | 43101.1042 | 58 | 58
2018-01-01 03:00 | 52 | 42 |  |  | 43101.125 | 57 | 57
2018-01-01 03:30 | 51 | 41 |  |  | 43101.1458 | 56 | 55
2018-01-01 04:00 | 51 | 41 |  |  | 43101.1667 | 55 | 54
2018-01-01 04:30 | 50 | 39 |  |  | 43101.1875 | 55 | 54
2018-01-01 05:00 | 49 | 38 |  |  | 43101.2083 | 53 | 53
2018-01-01 05:30 | 50 | 36 |  |  | 43101.2292 | 52 | 52
2018-01-01 06:00 | 49 | 36 |  |  | 43101.25 | 53 | 52
2018-01-01 06:30 | 50 | 37 |  |  | 43101.2708 | 56 | 55
2018-01-01 07:00 | 50 | 39 |  |  | 43101.2917 | 58 | 58
2018-01-01 07:30 | 51 | 42 |  |  | 43101.3125 | 63 | 63
2018-01-01 08:00 | 53 | 44 |  |  | 43101.3333 | 65 | 65
2018-01-01 08:30 | 56 | 50 |  |  | 43101.3542 | 71 | 71
2018-01-01 09:00 | 56 | 49 |  |  | 43101.375 | 72 | 72
2018-01-01 09:30 | 56 | 52 |  |  | 43101.3958 | 73 | 73
2018-01-01 10:00 | 56 | 52 |  |  | 43101.4167 | 74 | 74
2018-01-01 10:30 | 62 | 59 |  |  | 43101.4375 | 76 | 76
2018-01-01 11:00 | 71 | 70 |  |  | 43101.4583 | 88 | 88
2018-01-01 11:30 | 74 | 73 |  |  | 43101.4792 | 94 | 94
2018-01-01 12:00 | 75 | 74 |  |  | 43101.5 | 96 | 96
2018-01-01 12:30 | 76 | 75 |  |  | 43101.5208 | 93 | 93
2018-01-01 13:00 | 80 | 79 |  |  | 43101.5417 | 99 | 99
2018-01-01 13:30 | 83 | 82 |  |  | 43101.5625 | 100 | 100
2018-01-01 14:00 | 81 | 80 |  |  | 43101.5833 | 98 | 98
2018-01-01 14:30 | 84 | 82 |  |  | 43101.6042 | 101 | 101
2018-01-01 15:00 | 86 | 84 |  |  | 43101.625 | 106 | 105
2018-01-01 15:30 | 86 | 84 |  |  | 43101.6458 | 103 | 103
2018-01-01 16:00 | 93 | 88 |  |  | 43101.6667 | 113 | 109
2018-01-01 16:30 | 93 | 86 |  |  | 43101.6875 | 111 | 107
2018-01-01 17:00 | 94 | 87 |  |  | 43101.7083 | 111 | 106
2018-01-01 17:30 | 94 | 88 |  |  | 43101.7292 | 112 | 107
2018-01-01 18:00 | 93 | 86 |  |  | 43101.75 | 109 | 104
2018-01-01 18:30 | 85 | 79 |  |  | 43101.7708 | 98 | 98
2018-01-01 19:00 | 83 | 78 |  |  | 43101.7917 | 98 | 98
2018-01-01 19:30 | 84 | 79 |  |  | 43101.8125 | 99 | 99
2018-01-01 20:00 | 83 | 77 |  |  | 43101.8333 | 99 | 99
2018-01-01 20:30 | 81 | 74 |  |  | 43101.8542 | 96 | 96
2018-01-01 21:00 | 79 | 71 |  |  | 43101.875 | 92 | 92
2018-01-01 21:30 | 77 | 68 |  |  | 43101.8958 | 89 | 88
2018-01-01 22:00 | 74 | 64 |  |  | 43101.9167 | 86 | 85
2018-01-01 22:30 | 70 | 65 |  |  | 43101.9375 | 86 | 86
2018-01-01 23:00 | 70 | 64 |  |  | 43101.9583 | 82 | 82
2018-01-01 23:30 | 68 | 61 |  |  | 43101.9792 | 82 | 81
2018-01-02 | 68 | 56 |  |  | 43102 | 75 | 75
2018-01-02 00:30 | 65 | 52 |  |  | 43102.0208 | 69 | 69
2018-01-02 01:00 | 63 | 49 |  |  | 43102.0417 | 65 | 65
2018-01-02 01:30 | 62 | 46 |  |  | 43102.0625 | 63 | 63
2018-01-02 02:00 | 61 | 46 |  |  | 43102.0833 | 62 | 62
2018-01-02 02:30 | 61 | 45 |  |  | 43102.1042 | 62 | 62
2018-01-02 03:00 | 62 | 45 |  |  | 43102.125 | 62 | 62
2018-01-02 03:30 | 61 | 45 |  |  | 43102.1458 | 61 | 61
2018-01-02 04:00 | 60 | 44 |  |  | 43102.1667 | 60 | 60
2018-01-02 04:30 | 61 | 45 |  |  | 43102.1875 | 61 | 61
2018-01-02 05:00 | 62 | 46 |  |  | 43102.2083 | 62 | 62
2018-01-02 05:30 | 63 | 47 |  |  | 43102.2292 | 65 | 65
2018-01-02 06:00 | 64 | 50 |  |  | 43102.25 | 68 | 68
2018-01-02 06:30 | 67 | 55 |  |  | 43102.2708 | 76 | 76
2018-01-02 07:00 | 69 | 62 |  |  | 43102.2917 | 85 | 85
2018-01-02 07:30 | 67 | 67 |  |  | 43102.3125 | 95 | 93
2018-01-02 08:00 | 74 | 74 |  |  | 43102.3333 | 101 | 100
2018-01-02 08:30 | 80 | 79 |  |  | 43102.3542 | 108 | 107
2018-01-02 09:00 | 80 | 79 |  |  | 43102.375 | 107 | 107
2018-01-02 09:30 | 84 | 83 |  |  | 43102.3958 | 113 | 112
2018-01-02 10:00 | 87 | 86 |  |  | 43102.4167 | 115 | 115
2018-01-02 10:30 | 90 | 89 |  |  | 43102.4375 | 116 | 116
2018-01-02 11:00 | 93 | 92 |  |  | 43102.4583 | 117 | 117
2018-01-02 11:30 | 94 | 93 |  |  | 43102.4792 | 117 | 117
2018-01-02 12:00 | 95 | 93 |  |  | 43102.5 | 119 | 119
2018-01-02 12:30 | 94 | 93 |  |  | 43102.5208 | 117 | 117
2018-01-02 13:00 | 94 | 92 |  |  | 43102.5417 | 114 | 114
2018-01-02 13:30 | 97 | 95 |  |  | 43102.5625 | 118 | 118
2018-01-02 14:00 | 98 | 96 |  |  | 43102.5833 | 119 | 119
2018-01-02 14:30 | 101 | 100 |  |  | 43102.6042 | 120 | 120
2018-01-02 15:00 | 106 | 104 |  |  | 43102.625 | 127 | 127
2018-01-02 15:30 | 109 | 108 |  |  | 43102.6458 | 131 | 131
2018-01-02 16:00 | 104 | 103 |  |  | 43102.6667 | 130 | 130
2018-01-02 16:30 | 100 | 98 |  |  | 43102.6875 | 125 | 125
2018-01-02 17:00 | 98 | 96 |  |  | 43102.7083 | 121 | 121
2018-01-02 17:30 | 96 | 93 |  |  | 43102.7292 | 115 | 115
2018-01-02 18:00 | 96 | 93 |  |  | 43102.75 | 113 | 113
2018-01-02 18:30 | 93 | 91 |  |  | 43102.7708 | 109 | 109
2018-01-02 19:00 | 93 | 91 |  |  | 43102.7917 | 110 | 110
2018-01-02 19:30 | 93 | 91 |  |  | 43102.8125 | 109 | 109
2018-01-02 20:00 | 88 | 86 |  |  | 43102.8333 | 103 | 103
2018-01-02 20:30 | 86 | 83 |  |  | 43102.8542 | 100 | 100
2018-01-02 21:00 | 83 | 80 |  |  | 43102.875 | 96 | 96
2018-01-02 21:30 | 81 | 77 |  |  | 43102.8958 | 92 | 92
2018-01-02 22:00 | 78 | 75 |  |  | 43102.9167 | 90 | 90
2018-01-02 22:30 | 74 | 70 |  |  | 43102.9375 | 84 | 84
2018-01-02 23:00 | 73 | 68 |  |  | 43102.9583 | 83 | 83
2018-01-02 23:30 | 71 | 65 |  |  | 43102.9792 | 79 | 79
2018-01-03 | 66 | 60 |  |  | 43103 | 73 | 73
2018-01-03 00:30 | 61 | 55 |  |  | 43103.0208 | 68 | 68
2018-01-03 01:00 | 58 | 51 |  |  | 43103.0417 | 65 | 64
2018-01-03 01:30 | 58 | 50 |  |  | 43103.0625 | 62 | 62
2018-01-03 02:00 | 57 | 49 |  |  | 43103.0833 | 61 | 61
2018-01-03 02:30 | 57 | 49 |  |  | 43103.1042 | 61 | 60
2018-01-03 03:00 | 55 | 47 |  |  | 43103.125 | 59 | 59
2018-01-03 03:30 | 55 | 47 |  |  | 43103.1458 | 58 | 58
2018-01-03 04:00 | 55 | 47 |  |  | 43103.1667 | 58 | 58
2018-01-03 04:30 | 56 | 48 |  |  | 43103.1875 | 59 | 59
2018-01-03 05:00 | 56 | 48 |  |  | 43103.2083 | 61 | 60
2018-01-03 05:30 | 57 | 48 |  |  | 43103.2292 | 62 | 62
2018-01-03 06:00 | 57 | 50 |  |  | 43103.25 | 64 | 64
2018-01-03 06:30 | 61 | 55 |  |  | 43103.2708 | 73 | 73
2018-01-03 07:00 | 63 | 58 |  |  | 43103.2917 | 78 | 78
2018-01-03 07:30 | 69 | 64 |  |  | 43103.3125 | 86 | 86
2018-01-03 08:00 | 72 | 69 |  |  | 43103.3333 | 92 | 91
2018-01-03 08:30 | 75 | 72 |  |  | 43103.3542 | 96 | 96
2018-01-03 09:00 | 78 | 73 |  |  | 43103.375 | 97 | 97
2018-01-03 09:30 | 80 | 74 |  |  | 43103.3958 | 98 | 98
2018-01-03 10:00 | 80 | 76 |  |  | 43103.4167 | 99 | 99
2018-01-03 10:30 | 83 | 78 |  |  | 43103.4375 | 101 | 101
2018-01-03 11:00 | 84 | 80 |  |  | 43103.4583 | 101 | 101
2018-01-03 11:30 | 85 | 81 |  |  | 43103.4792 | 103 | 103
2018-01-03 12:00 | 88 | 85 |  |  | 43103.5 | 106 | 106
2018-01-03 12:30 | 90 | 88 |  |  | 43103.5208 | 109 | 109
2018-01-03 13:00 | 92 | 89 |  |  | 43103.5417 | 110 | 110
2018-01-03 13:30 | 96 | 94 |  |  | 43103.5625 | 112 | 112
2018-01-03 14:00 | 108 | 106 |  |  | 43103.5833 | 125 | 125
2018-01-03 14:30 | 108 | 106 |  |  | 43103.6042 | 126 | 126
2018-01-03 15:00 | 105 | 103 |  |  | 43103.625 | 125 | 125
2018-01-03 15:30 | 99 | 96 |  |  | 43103.6458 | 120 | 119
2018-01-03 16:00 | 93 | 90 |  |  | 43103.6667 | 112 | 112
2018-01-03 16:30 | 96 | 93 |  |  | 43103.6875 | 114 | 113
2018-01-03 17:00 | 96 | 93 |  |  | 43103.7083 | 116 | 115
2018-01-03 17:30 | 98 | 95 |  |  | 43103.7292 | 114 | 113
2018-01-03 18:00 | 97 | 94 |  |  | 43103.75 | 110 | 109
2018-01-03 18:30 | 91 | 89 |  |  | 43103.7708 | 103 | 103
2018-01-03 19:00 | 91 | 90 |  |  | 43103.7917 | 106 | 105
2018-01-03 19:30 | 91 | 90 |  |  | 43103.8125 | 105 | 104
2018-01-03 20:00 | 91 | 90 |  |  | 43103.8333 | 104 | 104
2018-01-03 20:30 | 88 | 87 |  |  | 43103.8542 | 102 | 101
2018-01-03 21:00 | 85 | 84 |  |  | 43103.875 | 97 | 97
2018-01-03 21:30 | 80 | 79 |  |  | 43103.8958 | 93 | 92
2018-01-03 22:00 | 78 | 77 |  |  | 43103.9167 | 91 | 90
2018-01-03 22:30 | 73 | 71 |  |  | 43103.9375 | 85 | 85
2018-01-03 23:00 | 71 | 70 |  |  | 43103.9583 | 83 | 82
2018-01-03 23:30 | 67 | 65 |  |  | 43103.9792 | 79 | 78
2018-01-04 | 62 | 60 |  |  | 43104 | 73 | 72
2018-01-04 00:30 | 59 | 57 |  |  | 43104.0208 | 69 | 68
2018-01-04 01:00 | 54 | 52 |  |  | 43104.0417 | 64 | 64
2018-01-04 01:30 | 52 | 50 |  |  | 43104.0625 | 62 | 61
2018-01-04 02:00 | 52 | 50 |  |  | 43104.0833 | 61 | 60
2018-01-04 02:30 | 52 | 48 |  |  | 43104.1042 | 60 | 59
2018-01-04 03:00 | 53 | 49 |  |  | 43104.125 | 60 | 59
2018-01-04 03:30 | 51 | 47 |  |  | 43104.1458 | 59 | 59
2018-01-04 04:00 | 49 | 45 |  |  | 43104.1667 | 57 | 56
2018-01-04 04:30 | 50 | 46 |  |  | 43104.1875 | 57 | 56
2018-01-04 05:00 | 51 | 47 |  |  | 43104.2083 | 59 | 58
2018-01-04 05:30 | 51 | 47 |  |  | 43104.2292 | 61 | 60
2018-01-04 06:00 | 53 | 50 |  |  | 43104.25 | 65 | 64
2018-01-04 06:30 | 55 | 54 |  |  | 43104.2708 | 72 | 70
2018-01-04 07:00 | 58 | 58 |  |  | 43104.2917 | 78 | 76
2018-01-04 07:30 | 66 | 65 |  |  | 43104.3125 | 88 | 85
2018-01-04 08:00 | 70 | 70 |  |  | 43104.3333 | 93 | 90
2018-01-04 08:30 | 71 | 71 |  |  | 43104.3542 | 95 | 92
2018-01-04 09:00 | 73 | 73 |  |  | 43104.375 | 96 | 93
2018-01-04 09:30 | 74 | 74 |  |  | 43104.3958 | 97 | 95
2018-01-04 10:00 | 80 | 79 |  |  | 43104.4167 | 98 | 96
2018-01-04 10:30 | 85 | 84 |  |  | 43104.4375 | 99 | 98
2018-01-04 11:00 | 83 | 83 |  |  | 43104.4583 | 99 | 98
2018-01-04 11:30 | 86 | 85 |  |  | 43104.4792 | 101 | 100
2018-01-04 12:00 | 87 | 87 |  |  | 43104.5 | 102 | 101
2018-01-04 12:30 | 89 | 89 |  |  | 43104.5208 | 104 | 103
2018-01-04 13:00 | 91 | 90 |  |  | 43104.5417 | 106 | 105
2018-01-04 13:30 | 94 | 93 |  |  | 43104.5625 | 106 | 105
2018-01-04 14:00 | 94 | 93 |  |  | 43104.5833 | 104 | 104
2018-01-04 14:30 | 92 | 92 |  |  | 43104.6042 | 102 | 102
2018-01-04 15:00 | 90 | 89 |  |  | 43104.625 | 100 | 100
2018-01-04 15:30 | 89 | 88 |  |  | 43104.6458 | 99 | 99
2018-01-04 16:00 | 88 | 87 |  |  | 43104.6667 | 99 | 99
2018-01-04 16:30 | 90 | 89 |  |  | 43104.6875 | 102 | 102
2018-01-04 17:00 | 95 | 94 |  |  | 43104.7083 | 106 | 106
2018-01-04 17:30 | 96 | 95 |  |  | 43104.7292 | 106 | 106
2018-01-04 18:00 | 96 | 94 |  |  | 43104.75 | 104 | 104
2018-01-04 18:30 | 93 | 91 |  |  | 43104.7708 | 99 | 99
2018-01-04 19:00 | 95 | 93 |  |  | 43104.7917 | 101 | 101
2018-01-04 19:30 | 94 | 92 |  |  | 43104.8125 | 101 | 101
2018-01-04 20:00 | 92 | 90 |  |  | 43104.8333 | 101 | 101
2018-01-04 20:30 | 89 | 87 |  |  | 43104.8542 | 101 | 101
2018-01-04 21:00 | 86 | 85 |  |  | 43104.875 | 97 | 97
2018-01-04 21:30 | 82 | 81 |  |  | 43104.8958 | 93 | 92
2018-01-04 22:00 | 82 | 81 |  |  | 43104.9167 | 94 | 94
2018-01-04 22:30 | 75 | 74 |  |  | 43104.9375 | 87 | 87
2018-01-04 23:00 | 74 | 73 |  |  | 43104.9583 | 85 | 85
2018-01-04 23:30 | 73 | 71 |  |  | 43104.9792 | 83 | 83
2018-01-05 | 67 | 65 |  |  | 43105 | 78 | 77
2018-01-05 00:30 | 63 | 61 |  |  | 43105.0208 | 71 | 71
2018-01-05 01:00 | 60 | 57 |  |  | 43105.0417 | 67 | 67
2018-01-05 01:30 | 58 | 54 |  |  | 43105.0625 | 64 | 64
2018-01-05 02:00 | 58 | 54 |  |  | 43105.0833 | 64 | 64
2018-01-05 02:30 | 57 | 53 |  |  | 43105.1042 | 63 | 63
2018-01-05 03:00 | 57 | 53 |  |  | 43105.125 | 63 | 63
2018-01-05 03:30 | 57 | 52 |  |  | 43105.1458 | 62 | 62
2018-01-05 04:00 | 56 | 51 |  |  | 43105.1667 | 62 | 62
2018-01-05 04:30 | 56 | 51 |  |  | 43105.1875 | 61 | 61
2018-01-05 05:00 | 56 | 51 |  |  | 43105.2083 | 62 | 62
2018-01-05 05:30 | 56 | 52 |  |  | 43105.2292 | 64 | 64
2018-01-05 06:00 | 57 | 54 |  |  | 43105.25 | 67 | 67
2018-01-05 06:30 | 59 | 57 |  |  | 43105.2708 | 74 | 74
2018-01-05 07:00 | 62 | 60 |  |  | 43105.2917 | 79 | 78
2018-01-05 07:30 | 69 | 68 |  |  | 43105.3125 | 89 | 88
2018-01-05 08:00 | 73 | 72 |  |  | 43105.3333 | 94 | 93
2018-01-05 08:30 | 74 | 74 |  |  | 43105.3542 | 97 | 96
2018-01-05 09:00 | 78 | 78 |  |  | 43105.375 | 101 | 99
2018-01-05 09:30 | 81 | 81 |  |  | 43105.3958 | 104 | 103
2018-01-05 10:00 | 84 | 83 |  |  | 43105.4167 | 108 | 107
2018-01-05 10:30 | 79 | 78 |  |  | 43105.4375 | 106 | 106
2018-01-05 11:00 | 79 | 78 |  |  | 43105.4583 | 100 | 100
2018-01-05 11:30 | 81 | 80 |  |  | 43105.4792 | 104 | 104
2018-01-05 12:00 | 78 | 77 |  |  | 43105.5 | 101 | 100
2018-01-05 12:30 | 77 | 76 |  |  | 43105.5208 | 98 | 98
2018-01-05 13:00 | 82 | 81 |  |  | 43105.5417 | 100 | 100
2018-01-05 13:30 | 84 | 83 |  |  | 43105.5625 | 101 | 101
2018-01-05 14:00 | 82 | 81 |  |  | 43105.5833 | 97 | 97
2018-01-05 14:30 | 81 | 80 |  |  | 43105.6042 | 98 | 98
2018-01-05 15:00 | 80 | 79 |  |  | 43105.625 | 100 | 100
2018-01-05 15:30 | 81 | 80 |  |  | 43105.6458 | 100 | 100
2018-01-05 16:00 | 83 | 82 |  |  | 43105.6667 | 102 | 102
2018-01-05 16:30 | 83 | 82 |  |  | 43105.6875 | 101 | 101
2018-01-05 17:00 | 84 | 83 |  |  | 43105.7083 | 102 | 102
2018-01-05 17:30 | 84 | 83 |  |  | 43105.7292 | 102 | 102
2018-01-05 18:00 | 82 | 80 |  |  | 43105.75 | 98 | 98
2018-01-05 18:30 | 80 | 77 |  |  | 43105.7708 | 93 | 93
2018-01-05 19:00 | 82 | 79 |  |  | 43105.7917 | 95 | 95
2018-01-05 19:30 | 83 | 80 |  |  | 43105.8125 | 96 | 96
2018-01-05 20:00 | 81 | 79 |  |  | 43105.8333 | 94 | 94
2018-01-05 20:30 | 78 | 77 |  |  | 43105.8542 | 92 | 91
2018-01-05 21:00 | 74 | 73 |  |  | 43105.875 | 87 | 87
2018-01-05 21:30 | 74 | 72 |  |  | 43105.8958 | 86 | 85
2018-01-05 22:00 | 76 | 74 |  |  | 43105.9167 | 87 | 87
2018-01-05 22:30 | 71 | 69 |  |  | 43105.9375 | 83 | 83
2018-01-05 23:00 | 71 | 68 |  |  | 43105.9583 | 82 | 82
2018-01-05 23:30 | 67 | 64 |  |  | 43105.9792 | 78 | 78
2018-01-06 | 62 | 58 |  |  | 43106 | 72 | 72
2018-01-06 00:30 | 56 | 53 |  |  | 43106.0208 | 66 | 66
2018-01-06 01:00 | 52 | 49 |  |  | 43106.0417 | 62 | 61
2018-01-06 01:30 | 51 | 48 |  |  | 43106.0625 | 61 | 59
2018-01-06 02:00 | 50 | 47 |  |  | 43106.0833 | 61 | 59
2018-01-06 02:30 | 50 | 46 |  |  | 43106.1042 | 61 | 59
2018-01-06 03:00 | 50 | 46 |  |  | 43106.125 | 61 | 58
2018-01-06 03:30 | 49 | 44 |  |  | 43106.1458 | 58 | 56
2018-01-06 04:00 | 48 | 44 |  |  | 43106.1667 | 58 | 56
2018-01-06 04:30 | 49 | 44 |  |  | 43106.1875 | 58 | 56
2018-01-06 05:00 | 49 | 44 |  |  | 43106.2083 | 58 | 56
2018-01-06 05:30 | 48 | 42 |  |  | 43106.2292 | 57 | 54
2018-01-06 06:00 | 46 | 40 |  |  | 43106.25 | 56 | 53
2018-01-06 06:30 | 43 | 39 |  |  | 43106.2708 | 55 | 53
2018-01-06 07:00 | 44 | 40 |  |  | 43106.2917 | 56 | 55
2018-01-06 07:30 | 45 | 42 |  |  | 43106.3125 | 58 | 57
2018-01-06 08:00 | 45 | 43 |  |  | 43106.3333 | 60 | 59
2018-01-06 08:30 | 48 | 47 |  |  | 43106.3542 | 63 | 63
2018-01-06 09:00 | 51 | 50 |  |  | 43106.375 | 67 | 66
2018-01-06 09:30 | 53 | 52 |  |  | 43106.3958 | 69 | 69
2018-01-06 10:00 | 51 | 50 |  |  | 43106.4167 | 66 | 66
2018-01-06 10:30 | 54 | 53 |  |  | 43106.4375 | 68 | 68
2018-01-06 11:00 | 59 | 58 |  |  | 43106.4583 | 73 | 73
2018-01-06 11:30 | 60 | 59 |  |  | 43106.4792 | 73 | 73
2018-01-06 12:00 | 60 | 59 |  |  | 43106.5 | 74 | 74
2018-01-06 12:30 | 58 | 58 |  |  | 43106.5208 | 71 | 71
2018-01-06 13:00 | 60 | 57 |  |  | 43106.5417 | 70 | 70
2018-01-06 13:30 | 62 | 60 |  |  | 43106.5625 | 73 | 73
2018-01-06 14:00 | 63 | 62 |  |  | 43106.5833 | 75 | 75
2018-01-06 14:30 | 68 | 67 |  |  | 43106.6042 | 81 | 80
2018-01-06 15:00 | 69 | 68 |  |  | 43106.625 | 81 | 80
2018-01-06 15:30 | 65 | 65 |  |  | 43106.6458 | 78 | 77
2018-01-06 16:00 | 66 | 65 |  |  | 43106.6667 | 77 | 77
2018-01-06 16:30 | 74 | 73 |  |  | 43106.6875 | 84 | 84
2018-01-06 17:00 | 77 | 76 |  |  | 43106.7083 | 89 | 89
2018-01-06 17:30 | 77 | 76 |  |  | 43106.7292 | 89 | 89
2018-01-06 18:00 | 75 | 74 |  |  | 43106.75 | 87 | 87
2018-01-06 18:30 | 74 | 72 |  |  | 43106.7708 | 85 | 85
2018-01-06 19:00 | 74 | 72 |  |  | 43106.7917 | 88 | 88
2018-01-06 19:30 | 74 | 73 |  |  | 43106.8125 | 89 | 88
2018-01-06 20:00 | 70 | 69 |  |  | 43106.8333 | 85 | 85
2018-01-06 20:30 | 69 | 67 |  |  | 43106.8542 | 84 | 83
2018-01-06 21:00 | 66 | 64 |  |  | 43106.875 | 80 | 80
2018-01-06 21:30 | 64 | 62 |  |  | 43106.8958 | 77 | 77
2018-01-06 22:00 | 65 | 62 |  |  | 43106.9167 | 79 | 79
2018-01-06 22:30 | 65 | 62 |  |  | 43106.9375 | 78 | 78
2018-01-06 23:00 | 65 | 62 |  |  | 43106.9583 | 77 | 77
2018-01-06 23:30 | 64 | 61 |  |  | 43106.9792 | 76 | 76
2018-01-07 | 60 | 56 |  |  | 43107 | 71 | 71
2018-01-07 00:30 | 55 | 50 |  |  | 43107.0208 | 63 | 63
2018-01-07 01:00 | 52 | 46 |  |  | 43107.0417 | 59 | 59
2018-01-07 01:30 | 50 | 44 |  |  | 43107.0625 | 58 | 58
2018-01-07 02:00 | 49 | 42 |  |  | 43107.0833 | 56 | 56
2018-01-07 02:30 | 49 | 42 |  |  | 43107.1042 | 55 | 55
2018-01-07 03:00 | 48 | 40 |  |  | 43107.125 | 54 | 54
2018-01-07 03:30 | 49 | 41 |  |  | 43107.1458 | 53 | 53
2018-01-07 04:00 | 48 | 40 |  |  | 43107.1667 | 52 | 52
2018-01-07 04:30 | 48 | 40 |  |  | 43107.1875 | 53 | 52
2018-01-07 05:00 | 48 | 39 |  |  | 43107.2083 | 52 | 52
2018-01-07 05:30 | 43 | 36 |  |  | 43107.2292 | 53 | 49
2018-01-07 06:00 | 42 | 35 |  |  | 43107.25 | 52 | 48
2018-01-07 06:30 | 41 | 35 |  |  | 43107.2708 | 51 | 48
2018-01-07 07:00 | 40 | 35 |  |  | 43107.2917 | 52 | 49
2018-01-07 07:30 | 40 | 35 |  |  | 43107.3125 | 52 | 50
2018-01-07 08:00 | 40 | 36 |  |  | 43107.3333 | 53 | 52
2018-01-07 08:30 | 42 | 39 |  |  | 43107.3542 | 56 | 55
2018-01-07 09:00 | 47 | 42 |  |  | 43107.375 | 59 | 59
2018-01-07 09:30 | 49 | 44 |  |  | 43107.3958 | 62 | 62
2018-01-07 10:00 | 52 | 42 |  |  | 43107.4167 | 60 | 59
2018-01-07 10:30 | 53 | 42 |  |  | 43107.4375 | 60 | 59
2018-01-07 11:00 | 52 | 43 |  |  | 43107.4583 | 61 | 59
2018-01-07 11:30 | 55 | 47 |  |  | 43107.4792 | 64 | 62
2018-01-07 12:00 | 54 | 47 |  |  | 43107.5 | 64 | 61
2018-01-07 12:30 | 55 | 49 |  |  | 43107.5208 | 66 | 64
2018-01-07 13:00 | 65 | 51 |  |  | 43107.5417 | 73 | 66
2018-01-07 13:30 | 72 | 54 |  |  | 43107.5625 | 78 | 68
2018-01-07 14:00 | 73 | 57 |  |  | 43107.5833 | 79 | 69
2018-01-07 14:30 | 71 | 57 |  |  | 43107.6042 | 81 | 70
2018-01-07 15:00 | 69 | 59 |  |  | 43107.625 | 84 | 73
2018-01-07 15:30 | 71 | 62 |  |  | 43107.6458 | 86 | 76
2018-01-07 16:00 | 75 | 65 |  |  | 43107.6667 | 88 | 79
2018-01-07 16:30 | 80 | 68 |  |  | 43107.6875 | 87 | 81
2018-01-07 17:00 | 79 | 70 |  |  | 43107.7083 | 87 | 84
2018-01-07 17:30 | 74 | 71 |  |  | 43107.7292 | 86 | 84
2018-01-07 18:00 | 74 | 70 |  |  | 43107.75 | 87 | 85
2018-01-07 18:30 | 75 | 72 |  |  | 43107.7708 | 88 | 86
2018-01-07 19:00 | 74 | 71 |  |  | 43107.7917 | 90 | 88
2018-01-07 19:30 | 75 | 72 |  |  | 43107.8125 | 92 | 91
2018-01-07 20:00 | 74 | 70 |  |  | 43107.8333 | 91 | 90
2018-01-07 20:30 | 69 | 68 |  |  | 43107.8542 | 87 | 87
2018-01-07 21:00 | 68 | 68 |  |  | 43107.875 | 85 | 85
2018-01-07 21:30 | 66 | 66 |  |  | 43107.8958 | 82 | 82
2018-01-07 22:00 | 65 | 64 |  |  | 43107.9167 | 81 | 81
2018-01-07 22:30 | 62 | 61 |  |  | 43107.9375 | 78 | 78
2018-01-07 23:00 | 63 | 62 |  |  | 43107.9583 | 77 | 77
2018-01-07 23:30 | 60 | 60 |  |  | 43107.9792 | 75 | 75
2018-01-08 | 57 | 56 |  |  | 43108 | 70 | 70
2018-01-08 00:30 | 51 | 49 |  |  | 43108.0208 | 64 | 63
2018-01-08 01:00 | 46 | 45 |  |  | 43108.0417 | 60 | 59
2018-01-08 01:30 | 48 | 45 |  |  | 43108.0625 | 59 | 58
2018-01-08 02:00 | 47 | 44 |  |  | 43108.0833 | 59 | 58
2018-01-08 02:30 | 46 | 43 |  |  | 43108.1042 | 58 | 56
2018-01-08 03:00 | 46 | 43 |  |  | 43108.125 | 57 | 55
2018-01-08 03:30 | 46 | 43 |  |  | 43108.1458 | 57 | 55
2018-01-08 04:00 | 45 | 42 |  |  | 43108.1667 | 57 | 56
2018-01-08 04:30 | 47 | 43 |  |  | 43108.1875 | 58 | 57
2018-01-08 05:00 | 48 | 45 |  |  | 43108.2083 | 59 | 58
2018-01-08 05:30 | 50 | 47 |  |  | 43108.2292 | 62 | 61
2018-01-08 06:00 | 52 | 50 |  |  | 43108.25 | 66 | 65
2018-01-08 06:30 | 56 | 55 |  |  | 43108.2708 | 73 | 73
2018-01-08 07:00 | 58 | 57 |  |  | 43108.2917 | 80 | 79
2018-01-08 07:30 | 64 | 63 |  |  | 43108.3125 | 88 | 87
2018-01-08 08:00 | 66 | 66 |  |  | 43108.3333 | 91 | 91
2018-01-08 08:30 | 71 | 70 |  |  | 43108.3542 | 95 | 95
2018-01-08 09:00 | 72 | 72 |  |  | 43108.375 | 97 | 97
2018-01-08 09:30 | 74 | 74 |  |  | 43108.3958 | 99 | 99
2018-01-08 10:00 | 75 | 75 |  |  | 43108.4167 | 100 | 100
2018-01-08 10:30 | 77 | 77 |  |  | 43108.4375 | 101 | 101
2018-01-08 11:00 | 76 | 76 |  |  | 43108.4583 | 101 | 101
2018-01-08 11:30 | 79 | 79 |  |  | 43108.4792 | 103 | 103
2018-01-08 12:00 | 80 | 80 |  |  | 43108.5 | 103 | 103
2018-01-08 12:30 | 79 | 78 |  |  | 43108.5208 | 102 | 102
2018-01-08 13:00 | 81 | 80 |  |  | 43108.5417 | 105 | 104
2018-01-08 13:30 | 82 | 81 |  |  | 43108.5625 | 106 | 105
2018-01-08 14:00 | 85 | 84 |  |  | 43108.5833 | 109 | 107
2018-01-08 14:30 | 88 | 88 |  |  | 43108.6042 | 112 | 111
2018-01-08 15:00 | 91 | 91 |  |  | 43108.625 | 116 | 113
2018-01-08 15:30 | 93 | 93 |  |  | 43108.6458 | 118 | 115
2018-01-08 16:00 | 94 | 93 |  |  | 43108.6667 | 118 | 115
2018-01-08 16:30 | 95 | 94 |  |  | 43108.6875 | 118 | 115
2018-01-08 17:00 | 96 | 95 |  |  | 43108.7083 | 120 | 116
2018-01-08 17:30 | 95 | 93 |  |  | 43108.7292 | 118 | 113
2018-01-08 18:00 | 90 | 90 |  |  | 43108.75 | 109 | 108
2018-01-08 18:30 | 88 | 88 |  |  | 43108.7708 | 105 | 105
2018-01-08 19:00 | 87 | 87 |  |  | 43108.7917 | 106 | 105
2018-01-08 19:30 | 88 | 88 |  |  | 43108.8125 | 105 | 105
2018-01-08 20:00 | 89 | 89 |  |  | 43108.8333 | 105 | 105
2018-01-08 20:30 | 88 | 88 |  |  | 43108.8542 | 104 | 104
2018-01-08 21:00 | 84 | 84 |  |  | 43108.875 | 99 | 99
2018-01-08 21:30 | 80 | 80 |  |  | 43108.8958 | 95 | 95
2018-01-08 22:00 | 78 | 77 |  |  | 43108.9167 | 94 | 93
2018-01-08 22:30 | 72 | 72 |  |  | 43108.9375 | 88 | 88
2018-01-08 23:00 | 70 | 70 |  |  | 43108.9583 | 83 | 83
2018-01-08 23:30 | 66 | 66 |  |  | 43108.9792 | 80 | 80
2018-01-09 | 60 | 60 |  |  | 43109 | 74 | 74
2018-01-09 00:30 | 57 | 56 |  |  | 43109.0208 | 68 | 68
2018-01-09 01:00 | 53 | 52 |  |  | 43109.0417 | 64 | 64
2018-01-09 01:30 | 51 | 50 |  |  | 43109.0625 | 62 | 62
2018-01-09 02:00 | 52 | 50 |  |  | 43109.0833 | 63 | 63
2018-01-09 02:30 | 53 | 52 |  |  | 43109.1042 | 64 | 64
2018-01-09 03:00 | 53 | 51 |  |  | 43109.125 | 64 | 64
2018-01-09 03:30 | 52 | 51 |  |  | 43109.1458 | 62 | 62
2018-01-09 04:00 | 51 | 50 |  |  | 43109.1667 | 61 | 61
2018-01-09 04:30 | 52 | 51 |  |  | 43109.1875 | 62 | 62
2018-01-09 05:00 | 53 | 52 |  |  | 43109.2083 | 63 | 63
2018-01-09 05:30 | 55 | 54 |  |  | 43109.2292 | 66 | 66
2018-01-09 06:00 | 57 | 56 |  |  | 43109.25 | 71 | 71
2018-01-09 06:30 | 59 | 59 |  |  | 43109.2708 | 79 | 79
2018-01-09 07:00 | 63 | 63 |  |  | 43109.2917 | 85 | 85
2018-01-09 07:30 | 70 | 70 |  |  | 43109.3125 | 95 | 95
2018-01-09 08:00 | 75 | 75 |  |  | 43109.3333 | 100 | 100
2018-01-09 08:30 | 78 | 77 |  |  | 43109.3542 | 104 | 104
2018-01-09 09:00 | 79 | 78 |  |  | 43109.375 | 105 | 105
2018-01-09 09:30 | 81 | 81 |  |  | 43109.3958 | 107 | 107
2018-01-09 10:00 | 80 | 79 |  |  | 43109.4167 | 104 | 103
2018-01-09 10:30 | 78 | 78 |  |  | 43109.4375 | 102 | 102
2018-01-09 11:00 | 78 | 77 |  |  | 43109.4583 | 102 | 101
2018-01-09 11:30 | 81 | 81 |  |  | 43109.4792 | 106 | 106
2018-01-09 12:00 | 86 | 85 |  |  | 43109.5 | 106 | 106
2018-01-09 12:30 | 87 | 87 |  |  | 43109.5208 | 110 | 109
2018-01-09 13:00 | 90 | 89 |  |  | 43109.5417 | 112 | 112
2018-01-09 13:30 | 93 | 92 |  |  | 43109.5625 | 116 | 115
2018-01-09 14:00 | 95 | 94 |  |  | 43109.5833 | 117 | 117
2018-01-09 14:30 | 98 | 97 |  |  | 43109.6042 | 119 | 119
2018-01-09 15:00 | 101 | 100 |  |  | 43109.625 | 122 | 121
2018-01-09 15:30 | 101 | 100 |  |  | 43109.6458 | 122 | 121
2018-01-09 16:00 | 99 | 98 |  |  | 43109.6667 | 121 | 119
2018-01-09 16:30 | 98 | 98 |  |  | 43109.6875 | 121 | 120
2018-01-09 17:00 | 99 | 99 |  |  | 43109.7083 | 121 | 119
2018-01-09 17:30 | 98 | 98 |  |  | 43109.7292 | 118 | 116
2018-01-09 18:00 | 95 | 93 |  |  | 43109.75 | 114 | 111
2018-01-09 18:30 | 93 | 91 |  |  | 43109.7708 | 111 | 107
2018-01-09 19:00 | 94 | 92 |  |  | 43109.7917 | 112 | 108
2018-01-09 19:30 | 94 | 92 |  |  | 43109.8125 | 111 | 108
2018-01-09 20:00 | 92 | 91 |  |  | 43109.8333 | 109 | 108
2018-01-09 20:30 | 92 | 91 |  |  | 43109.8542 | 108 | 107
2018-01-09 21:00 | 88 | 88 |  |  | 43109.875 | 102 | 102
2018-01-09 21:30 | 82 | 82 |  |  | 43109.8958 | 97 | 96
2018-01-09 22:00 | 78 | 78 |  |  | 43109.9167 | 93 | 93
2018-01-09 22:30 | 74 | 73 |  |  | 43109.9375 | 88 | 88
2018-01-09 23:00 | 72 | 72 |  |  | 43109.9583 | 85 | 85
2018-01-09 23:30 | 66 | 66 |  |  | 43109.9792 | 81 | 81
2018-01-10 | 63 | 63 |  |  | 43110 | 76 | 76
2018-01-10 00:30 | 59 | 58 |  |  | 43110.0208 | 71 | 71
2018-01-10 01:00 | 56 | 55 |  |  | 43110.0417 | 67 | 67
2018-01-10 01:30 | 55 | 53 |  |  | 43110.0625 | 66 | 66
2018-01-10 02:00 | 55 | 53 |  |  | 43110.0833 | 65 | 65
2018-01-10 02:30 | 55 | 53 |  |  | 43110.1042 | 65 | 65
2018-01-10 03:00 | 52 | 50 |  |  | 43110.125 | 63 | 62
2018-01-10 03:30 | 52 | 50 |  |  | 43110.1458 | 63 | 62
2018-01-10 04:00 | 52 | 50 |  |  | 43110.1667 | 63 | 62
2018-01-10 04:30 | 53 | 50 |  |  | 43110.1875 | 64 | 63
2018-01-10 05:00 | 54 | 52 |  |  | 43110.2083 | 65 | 64
2018-01-10 05:30 | 55 | 53 |  |  | 43110.2292 | 68 | 67
2018-01-10 06:00 | 58 | 56 |  |  | 43110.25 | 72 | 71
2018-01-10 06:30 | 60 | 59 |  |  | 43110.2708 | 79 | 78
2018-01-10 07:00 | 65 | 64 |  |  | 43110.2917 | 87 | 85
2018-01-10 07:30 | 71 | 71 |  |  | 43110.3125 | 94 | 94
2018-01-10 08:00 | 74 | 74 |  |  | 43110.3333 | 100 | 100
2018-01-10 08:30 | 77 | 77 |  |  | 43110.3542 | 103 | 102
2018-01-10 09:00 | 80 | 80 |  |  | 43110.375 | 106 | 106
2018-01-10 09:30 | 81 | 80 |  |  | 43110.3958 | 106 | 106
2018-01-10 10:00 | 82 | 82 |  |  | 43110.4167 | 106 | 106
2018-01-10 10:30 | 85 | 85 |  |  | 43110.4375 | 108 | 107
2018-01-10 11:00 | 88 | 88 |  |  | 43110.4583 | 112 | 111
2018-01-10 11:30 | 87 | 87 |  |  | 43110.4792 | 110 | 109
2018-01-10 12:00 | 88 | 87 |  |  | 43110.5 | 111 | 111
2018-01-10 12:30 | 88 | 87 |  |  | 43110.5208 | 111 | 111
2018-01-10 13:00 | 89 | 89 |  |  | 43110.5417 | 110 | 110
2018-01-10 13:30 | 92 | 91 |  |  | 43110.5625 | 112 | 112
2018-01-10 14:00 | 94 | 94 |  |  | 43110.5833 | 116 | 115
2018-01-10 14:30 | 96 | 95 |  |  | 43110.6042 | 119 | 118
2018-01-10 15:00 | 97 | 97 |  |  | 43110.625 | 118 | 118
2018-01-10 15:30 | 100 | 99 |  |  | 43110.6458 | 122 | 121
2018-01-10 16:00 | 102 | 101 |  |  | 43110.6667 | 126 | 122
2018-01-10 16:30 | 103 | 102 |  |  | 43110.6875 | 128 | 123
2018-01-10 17:00 | 105 | 103 |  |  | 43110.7083 | 130 | 124
2018-01-10 17:30 | 104 | 102 |  |  | 43110.7292 | 127 | 120
2018-01-10 18:00 | 102 | 100 |  |  | 43110.75 | 123 | 117
2018-01-10 18:30 | 98 | 97 |  |  | 43110.7708 | 114 | 113
2018-01-10 19:00 | 99 | 98 |  |  | 43110.7917 | 115 | 114
2018-01-10 19:30 | 98 | 98 |  |  | 43110.8125 | 116 | 115
2018-01-10 20:00 | 99 | 98 |  |  | 43110.8333 | 117 | 116
2018-01-10 20:30 | 96 | 96 |  |  | 43110.8542 | 113 | 113
2018-01-10 21:00 | 94 | 93 |  |  | 43110.875 | 109 | 109
2018-01-10 21:30 | 89 | 89 |  |  | 43110.8958 | 105 | 104
2018-01-10 22:00 | 86 | 86 |  |  | 43110.9167 | 102 | 102
2018-01-10 22:30 | 77 | 77 |  |  | 43110.9375 | 94 | 94
2018-01-10 23:00 | 73 | 73 |  |  | 43110.9583 | 88 | 88
2018-01-10 23:30 | 72 | 72 |  |  | 43110.9792 | 87 | 87
2018-01-11 | 68 | 67 |  |  | 43111 | 83 | 83
2018-01-11 00:30 | 62 | 61 |  |  | 43111.0208 | 74 | 74
2018-01-11 01:00 | 59 | 57 |  |  | 43111.0417 | 71 | 71
2018-01-11 01:30 | 57 | 55 |  |  | 43111.0625 | 68 | 68
2018-01-11 02:00 | 56 | 54 |  |  | 43111.0833 | 68 | 68
2018-01-11 02:30 | 55 | 54 |  |  | 43111.1042 | 67 | 67
2018-01-11 03:00 | 55 | 53 |  |  | 43111.125 | 67 | 67
2018-01-11 03:30 | 55 | 53 |  |  | 43111.1458 | 66 | 66
2018-01-11 04:00 | 54 | 52 |  |  | 43111.1667 | 65 | 65
2018-01-11 04:30 | 53 | 51 |  |  | 43111.1875 | 63 | 63
2018-01-11 05:00 | 55 | 53 |  |  | 43111.2083 | 65 | 65
2018-01-11 05:30 | 55 | 53 |  |  | 43111.2292 | 68 | 68
2018-01-11 06:00 | 55 | 54 |  |  | 43111.25 | 69 | 69
2018-01-11 06:30 | 60 | 59 |  |  | 43111.2708 | 76 | 76
2018-01-11 07:00 | 66 | 65 |  |  | 43111.2917 | 85 | 85
2018-01-11 07:30 | 76 | 76 |  |  | 43111.3125 | 98 | 98
2018-01-11 08:00 | 79 | 79 |  |  | 43111.3333 | 101 | 101
2018-01-11 08:30 | 78 | 78 |  |  | 43111.3542 | 102 | 102
2018-01-11 09:00 | 81 | 81 |  |  | 43111.375 | 104 | 104
2018-01-11 09:30 | 82 | 82 |  |  | 43111.3958 | 105 | 105
2018-01-11 10:00 | 82 | 82 |  |  | 43111.4167 | 106 | 105
2018-01-11 10:30 | 84 | 84 |  |  | 43111.4375 | 107 | 107
2018-01-11 11:00 | 85 | 85 |  |  | 43111.4583 | 108 | 108
2018-01-11 11:30 | 90 | 87 |  |  | 43111.4792 | 115 | 111
2018-01-11 12:00 | 99 | 93 |  |  | 43111.5 | 129 | 117
2018-01-11 12:30 | 94 | 88 |  |  | 43111.5208 | 127 | 115
2018-01-11 13:00 | 94 | 87 |  |  | 43111.5417 | 125 | 113
2018-01-11 13:30 | 97 | 91 |  |  | 43111.5625 | 128 | 116
2018-01-11 14:00 | 98 | 92 |  |  | 43111.5833 | 128 | 116
2018-01-11 14:30 | 103 | 97 |  |  | 43111.6042 | 132 | 120
2018-01-11 15:00 | 103 | 99 |  |  | 43111.625 | 135 | 124
2018-01-11 15:30 | 102 | 98 |  |  | 43111.6458 | 133 | 122
2018-01-11 16:00 | 104 | 100 |  |  | 43111.6667 | 134 | 123
2018-01-11 16:30 | 104 | 101 |  |  | 43111.6875 | 133 | 125
2018-01-11 17:00 | 99 | 96 |  |  | 43111.7083 | 128 | 119
2018-01-11 17:30 | 101 | 98 |  |  | 43111.7292 | 126 | 117
2018-01-11 18:00 | 101 | 99 |  |  | 43111.75 | 126 | 117
2018-01-11 18:30 | 94 | 93 |  |  | 43111.7708 | 126 | 111
2018-01-11 19:00 | 94 | 93 |  |  | 43111.7917 | 123 | 112
2018-01-11 19:30 | 96 | 96 |  |  | 43111.8125 | 122 | 113
2018-01-11 20:00 | 95 | 95 |  |  | 43111.8333 | 121 | 112
2018-01-11 20:30 | 94 | 94 |  |  | 43111.8542 | 115 | 110
2018-01-11 21:00 | 91 | 91 |  |  | 43111.875 | 112 | 106
2018-01-11 21:30 | 86 | 86 |  |  | 43111.8958 | 106 | 100
2018-01-11 22:00 | 83 | 82 |  |  | 43111.9167 | 97 | 97
2018-01-11 22:30 | 77 | 76 |  |  | 43111.9375 | 91 | 91
2018-01-11 23:00 | 71 | 71 |  |  | 43111.9583 | 83 | 83
2018-01-11 23:30 | 67 | 67 |  |  | 43111.9792 | 79 | 78
2018-01-12 | 60 | 60 |  |  | 43112 | 72 | 71
2018-01-12 00:30 | 54 | 54 |  |  | 43112.0208 | 66 | 66
2018-01-12 01:00 | 52 | 52 |  |  | 43112.0417 | 63 | 63
2018-01-12 01:30 | 51 | 51 |  |  | 43112.0625 | 61 | 61
2018-01-12 02:00 | 51 | 51 |  |  | 43112.0833 | 62 | 61
2018-01-12 02:30 | 51 | 51 |  |  | 43112.1042 | 61 | 60
2018-01-12 03:00 | 50 | 49 |  |  | 43112.125 | 59 | 58
2018-01-12 03:30 | 49 | 49 |  |  | 43112.1458 | 58 | 57
2018-01-12 04:00 | 49 | 49 |  |  | 43112.1667 | 59 | 57
2018-01-12 04:30 | 48 | 47 |  |  | 43112.1875 | 58 | 57
2018-01-12 05:00 | 47 | 46 |  |  | 43112.2083 | 58 | 57
2018-01-12 05:30 | 50 | 49 |  |  | 43112.2292 | 62 | 61
2018-01-12 06:00 | 54 | 53 |  |  | 43112.25 | 66 | 66
2018-01-12 06:30 | 61 | 60 |  |  | 43112.2708 | 77 | 77
2018-01-12 07:00 | 65 | 65 |  |  | 43112.2917 | 86 | 84
2018-01-12 07:30 | 72 | 71 |  |  | 43112.3125 | 95 | 93
2018-01-12 08:00 | 78 | 78 |  |  | 43112.3333 | 100 | 98
2018-01-12 08:30 | 81 | 80 |  |  | 43112.3542 | 102 | 101
2018-01-12 09:00 | 79 | 79 |  |  | 43112.375 | 102 | 99
2018-01-12 09:30 | 78 | 78 |  |  | 43112.3958 | 102 | 99
2018-01-12 10:00 | 81 | 81 |  |  | 43112.4167 | 106 | 103
2018-01-12 10:30 | 83 | 83 |  |  | 43112.4375 | 105 | 103
2018-01-12 11:00 | 84 | 83 |  |  | 43112.4583 | 106 | 104
2018-01-12 11:30 | 85 | 84 |  |  | 43112.4792 | 108 | 106
2018-01-12 12:00 | 87 | 87 |  |  | 43112.5 | 112 | 110
2018-01-12 12:30 | 89 | 89 |  |  | 43112.5208 | 113 | 111
2018-01-12 13:00 | 92 | 92 |  |  | 43112.5417 | 116 | 114
2018-01-12 13:30 | 93 | 93 |  |  | 43112.5625 | 115 | 114
2018-01-12 14:00 | 94 | 93 |  |  | 43112.5833 | 117 | 115
2018-01-12 14:30 | 95 | 95 |  |  | 43112.6042 | 120 | 116
2018-01-12 15:00 | 100 | 99 |  |  | 43112.625 | 122 | 119
2018-01-12 15:30 | 101 | 100 |  |  | 43112.6458 | 123 | 121
2018-01-12 16:00 | 101 | 100 |  |  | 43112.6667 | 126 | 122
2018-01-12 16:30 | 101 | 101 |  |  | 43112.6875 | 134 | 122
2018-01-12 17:00 | 100 | 100 |  |  | 43112.7083 | 139 | 121
2018-01-12 17:30 | 99 | 99 |  |  | 43112.7292 | 134 | 118
2018-01-12 18:00 | 95 | 94 |  |  | 43112.75 | 127 | 113
2018-01-12 18:30 | 90 | 90 |  |  | 43112.7708 | 114 | 108
2018-01-12 19:00 | 90 | 90 |  |  | 43112.7917 | 114 | 108
2018-01-12 19:30 | 92 | 92 |  |  | 43112.8125 | 115 | 109
2018-01-12 20:00 | 91 | 91 |  |  | 43112.8333 | 113 | 108
2018-01-12 20:30 | 89 | 88 |  |  | 43112.8542 | 105 | 105
2018-01-12 21:00 | 87 | 85 |  |  | 43112.875 | 102 | 101
2018-01-12 21:30 | 83 | 82 |  |  | 43112.8958 | 98 | 97
2018-01-12 22:00 | 79 | 79 |  |  | 43112.9167 | 97 | 94
2018-01-12 22:30 | 72 | 72 |  |  | 43112.9375 | 90 | 86
2018-01-12 23:00 | 68 | 67 |  |  | 43112.9583 | 81 | 81
2018-01-12 23:30 | 65 | 63 |  |  | 43112.9792 | 78 | 78
2018-01-13 | 60 | 58 |  |  | 43113 | 72 | 71
2018-01-13 00:30 | 55 | 52 |  |  | 43113.0208 | 65 | 64
2018-01-13 01:00 | 53 | 50 |  |  | 43113.0417 | 60 | 60
2018-01-13 01:30 | 50 | 48 |  |  | 43113.0625 | 58 | 58
2018-01-13 02:00 | 49 | 47 |  |  | 43113.0833 | 57 | 56
2018-01-13 02:30 | 49 | 47 |  |  | 43113.1042 | 58 | 57
2018-01-13 03:00 | 47 | 45 |  |  | 43113.125 | 56 | 56
2018-01-13 03:30 | 46 | 45 |  |  | 43113.1458 | 56 | 55
2018-01-13 04:00 | 46 | 45 |  |  | 43113.1667 | 56 | 55
2018-01-13 04:30 | 47 | 45 |  |  | 43113.1875 | 56 | 56
2018-01-13 05:00 | 47 | 46 |  |  | 43113.2083 | 56 | 55
2018-01-13 05:30 | 45 | 43 |  |  | 43113.2292 | 54 | 53
2018-01-13 06:00 | 46 | 44 |  |  | 43113.25 | 56 | 55
2018-01-13 06:30 | 48 | 45 |  |  | 43113.2708 | 56 | 56
2018-01-13 07:00 | 49 | 45 |  |  | 43113.2917 | 57 | 57
2018-01-13 07:30 | 53 | 50 |  |  | 43113.3125 | 64 | 64
2018-01-13 08:00 | 52 | 51 |  |  | 43113.3333 | 65 | 65
2018-01-13 08:30 | 54 | 53 |  |  | 43113.3542 | 69 | 68
2018-01-13 09:00 | 55 | 55 |  |  | 43113.375 | 71 | 71
2018-01-13 09:30 | 58 | 58 |  |  | 43113.3958 | 73 | 73
2018-01-13 10:00 | 59 | 59 |  |  | 43113.4167 | 75 | 75
2018-01-13 10:30 | 62 | 62 |  |  | 43113.4375 | 78 | 77
2018-01-13 11:00 | 66 | 66 |  |  | 43113.4583 | 83 | 83
2018-01-13 11:30 | 70 | 70 |  |  | 43113.4792 | 86 | 86
2018-01-13 12:00 | 78 | 78 |  |  | 43113.5 | 93 | 93
2018-01-13 12:30 | 84 | 83 |  |  | 43113.5208 | 99 | 99
2018-01-13 13:00 | 90 | 89 |  |  | 43113.5417 | 105 | 104
2018-01-13 13:30 | 93 | 92 |  |  | 43113.5625 | 107 | 107
2018-01-13 14:00 | 97 | 96 |  |  | 43113.5833 | 111 | 111
2018-01-13 14:30 | 99 | 98 |  |  | 43113.6042 | 112 | 111
2018-01-13 15:00 | 89 | 88 |  |  | 43113.625 | 109 | 109
2018-01-13 15:30 | 91 | 90 |  |  | 43113.6458 | 111 | 110
2018-01-13 16:00 | 94 | 93 |  |  | 43113.6667 | 115 | 114
2018-01-13 16:30 | 95 | 94 |  |  | 43113.6875 | 120 | 119
2018-01-13 17:00 | 98 | 98 |  |  | 43113.7083 | 120 | 119
2018-01-13 17:30 | 98 | 98 |  |  | 43113.7292 | 121 | 120
2018-01-13 18:00 | 95 | 94 |  |  | 43113.75 | 118 | 116
2018-01-13 18:30 | 91 | 90 |  |  | 43113.7708 | 113 | 110
2018-01-13 19:00 | 89 | 87 |  |  | 43113.7917 | 112 | 110
2018-01-13 19:30 | 90 | 90 |  |  | 43113.8125 | 112 | 111
2018-01-13 20:00 | 89 | 89 |  |  | 43113.8333 | 111 | 110
2018-01-13 20:30 | 87 | 87 |  |  | 43113.8542 | 108 | 107
2018-01-13 21:00 | 84 | 84 |  |  | 43113.875 | 104 | 104
2018-01-13 21:30 | 82 | 82 |  |  | 43113.8958 | 102 | 102
2018-01-13 22:00 | 81 | 81 |  |  | 43113.9167 | 100 | 100
2018-01-13 22:30 | 77 | 77 |  |  | 43113.9375 | 96 | 96
2018-01-13 23:00 | 71 | 71 |  |  | 43113.9583 | 90 | 90
2018-01-13 23:30 | 66 | 65 |  |  | 43113.9792 | 82 | 82
2018-01-14 | 63 | 60 |  |  | 43114 | 78 | 77
2018-01-14 00:30 | 61 | 59 |  |  | 43114.0208 | 75 | 74
2018-01-14 01:00 | 59 | 55 |  |  | 43114.0417 | 72 | 70
2018-01-14 01:30 | 59 | 54 |  |  | 43114.0625 | 71 | 70
2018-01-14 02:00 | 57 | 53 |  |  | 43114.0833 | 69 | 68
2018-01-14 02:30 | 61 | 56 |  |  | 43114.1042 | 69 | 67
2018-01-14 03:00 | 61 | 55 |  |  | 43114.125 | 69 | 67
2018-01-14 03:30 | 60 | 54 |  |  | 43114.1458 | 66 | 64
2018-01-14 04:00 | 61 | 55 |  |  | 43114.1667 | 66 | 65
2018-01-14 04:30 | 62 | 56 |  |  | 43114.1875 | 69 | 67
2018-01-14 05:00 | 63 | 56 |  |  | 43114.2083 | 69 | 67
2018-01-14 05:30 | 61 | 54 |  |  | 43114.2292 | 66 | 64
2018-01-14 06:00 | 59 | 51 |  |  | 43114.25 | 65 | 63
2018-01-14 06:30 | 58 | 52 |  |  | 43114.2708 | 65 | 64
2018-01-14 07:00 | 60 | 54 |  |  | 43114.2917 | 69 | 67
2018-01-14 07:30 | 63 | 58 |  |  | 43114.3125 | 73 | 72
2018-01-14 08:00 | 68 | 63 |  |  | 43114.3333 | 80 | 79
2018-01-14 08:30 | 75 | 70 |  |  | 43114.3542 | 87 | 84
2018-01-14 09:00 | 77 | 72 |  |  | 43114.375 | 89 | 86
2018-01-14 09:30 | 79 | 77 |  |  | 43114.3958 | 94 | 92
2018-01-14 10:00 | 81 | 78 |  |  | 43114.4167 | 96 | 93
2018-01-14 10:30 | 85 | 82 |  |  | 43114.4375 | 99 | 95
2018-01-14 11:00 | 89 | 86 |  |  | 43114.4583 | 103 | 98
2018-01-14 11:30 | 92 | 89 |  |  | 43114.4792 | 107 | 102
2018-01-14 12:00 | 93 | 90 |  |  | 43114.5 | 107 | 102
2018-01-14 12:30 | 96 | 93 |  |  | 43114.5208 | 107 | 103
2018-01-14 13:00 | 99 | 96 |  |  | 43114.5417 | 111 | 107
2018-01-14 13:30 | 102 | 98 |  |  | 43114.5625 | 116 | 112
2018-01-14 14:00 | 106 | 102 |  |  | 43114.5833 | 119 | 115
2018-01-14 14:30 | 101 | 98 |  |  | 43114.6042 | 117 | 113
2018-01-14 15:00 | 99 | 97 |  |  | 43114.625 | 116 | 112
2018-01-14 15:30 | 100 | 98 |  |  | 43114.6458 | 118 | 115
2018-01-14 16:00 | 100 | 98 |  |  | 43114.6667 | 120 | 116
2018-01-14 16:30 | 101 | 100 |  |  | 43114.6875 | 120 | 116
2018-01-14 17:00 | 101 | 99 |  |  | 43114.7083 | 119 | 114
2018-01-14 17:30 | 94 | 91 |  |  | 43114.7292 | 112 | 107
2018-01-14 18:00 | 90 | 86 |  |  | 43114.75 | 108 | 102
2018-01-14 18:30 | 85 | 82 |  |  | 43114.7708 | 99 | 97
2018-01-14 19:00 | 87 | 85 |  |  | 43114.7917 | 100 | 99
2018-01-14 19:30 | 84 | 82 |  |  | 43114.8125 | 98 | 98
2018-01-14 20:00 | 82 | 80 |  |  | 43114.8333 | 95 | 95
2018-01-14 20:30 | 81 | 80 |  |  | 43114.8542 | 95 | 95
2018-01-14 21:00 | 79 | 77 |  |  | 43114.875 | 91 | 91
2018-01-14 21:30 | 76 | 73 |  |  | 43114.8958 | 86 | 86
2018-01-14 22:00 | 75 | 72 |  |  | 43114.9167 | 84 | 84
2018-01-14 22:30 | 72 | 68 |  |  | 43114.9375 | 80 | 80
2018-01-14 23:00 | 69 | 64 |  |  | 43114.9583 | 75 | 74
2018-01-14 23:30 | 66 | 60 |  |  | 43114.9792 | 72 | 71
2018-01-15 | 60 | 53 |  |  | 43115 | 64 | 64
2018-01-15 00:30 | 56 | 47 |  |  | 43115.0208 | 59 | 58
2018-01-15 01:00 | 53 | 44 |  |  | 43115.0417 | 56 | 55
2018-01-15 01:30 | 54 | 45 |  |  | 43115.0625 | 58 | 57
2018-01-15 02:00 | 55 | 44 |  |  | 43115.0833 | 57 | 56
2018-01-15 02:30 | 53 | 43 |  |  | 43115.1042 | 54 | 53
2018-01-15 03:00 | 51 | 40 |  |  | 43115.125 | 52 | 51
2018-01-15 03:30 | 50 | 39 |  |  | 43115.1458 | 50 | 49
2018-01-15 04:00 | 49 | 38 |  |  | 43115.1667 | 48 | 46
2018-01-15 04:30 | 50 | 41 |  |  | 43115.1875 | 52 | 50
2018-01-15 05:00 | 55 | 46 |  |  | 43115.2083 | 57 | 56
2018-01-15 05:30 | 56 | 48 |  |  | 43115.2292 | 60 | 59
2018-01-15 06:00 | 57 | 50 |  |  | 43115.25 | 63 | 63
2018-01-15 06:30 | 61 | 58 |  |  | 43115.2708 | 74 | 74
2018-01-15 07:00 | 63 | 61 |  |  | 43115.2917 | 81 | 81
2018-01-15 07:30 | 71 | 69 |  |  | 43115.3125 | 90 | 90
2018-01-15 08:00 | 74 | 72 |  |  | 43115.3333 | 94 | 94
2018-01-15 08:30 | 76 | 74 |  |  | 43115.3542 | 97 | 96
2018-01-15 09:00 | 76 | 74 |  |  | 43115.375 | 98 | 97
2018-01-15 09:30 | 77 | 75 |  |  | 43115.3958 | 98 | 97
2018-01-15 10:00 | 79 | 77 |  |  | 43115.4167 | 100 | 99
2018-01-15 10:30 | 80 | 78 |  |  | 43115.4375 | 100 | 99
2018-01-15 11:00 | 79 | 76 |  |  | 43115.4583 | 100 | 98
2018-01-15 11:30 | 78 | 76 |  |  | 43115.4792 | 100 | 98
2018-01-15 12:00 | 79 | 77 |  |  | 43115.5 | 100 | 99
2018-01-15 12:30 | 81 | 79 |  |  | 43115.5208 | 101 | 100
2018-01-15 13:00 | 84 | 82 |  |  | 43115.5417 | 105 | 104
2018-01-15 13:30 | 85 | 83 |  |  | 43115.5625 | 106 | 105
2018-01-15 14:00 | 88 | 86 |  |  | 43115.5833 | 108 | 107
2018-01-15 14:30 | 89 | 87 |  |  | 43115.6042 | 108 | 107
2018-01-15 15:00 | 93 | 89 |  |  | 43115.625 | 107 | 107
2018-01-15 15:30 | 93 | 87 |  |  | 43115.6458 | 106 | 106
2018-01-15 16:00 | 93 | 87 |  |  | 43115.6667 | 105 | 105
2018-01-15 16:30 | 93 | 87 |  |  | 43115.6875 | 106 | 105
2018-01-15 17:00 | 93 | 87 |  |  | 43115.7083 | 105 | 104
2018-01-15 17:30 | 93 | 86 |  |  | 43115.7292 | 103 | 102
2018-01-15 18:00 | 92 | 85 |  |  | 43115.75 | 99 | 98
2018-01-15 18:30 | 89 | 81 |  |  | 43115.7708 | 94 | 92
2018-01-15 19:00 | 90 | 81 |  |  | 43115.7917 | 95 | 93
2018-01-15 19:30 | 90 | 82 |  |  | 43115.8125 | 95 | 93
2018-01-15 20:00 | 89 | 81 |  |  | 43115.8333 | 95 | 93
2018-01-15 20:30 | 89 | 81 |  |  | 43115.8542 | 93 | 91
2018-01-15 21:00 | 85 | 77 |  |  | 43115.875 | 88 | 87
2018-01-15 21:30 | 79 | 72 |  |  | 43115.8958 | 83 | 83
2018-01-15 22:00 | 76 | 68 |  |  | 43115.9167 | 80 | 80
2018-01-15 22:30 | 71 | 62 |  |  | 43115.9375 | 74 | 73
2018-01-15 23:00 | 67 | 56 |  |  | 43115.9583 | 67 | 66
2018-01-15 23:30 | 65 | 53 |  |  | 43115.9792 | 65 | 64
2018-01-16 | 65 | 51 |  |  | 43116 | 62 | 61
2018-01-16 00:30 | 63 | 47 |  |  | 43116.0208 | 57 | 56
2018-01-16 01:00 | 61 | 44 |  |  | 43116.0417 | 55 | 53
2018-01-16 01:30 | 62 | 44 |  |  | 43116.0625 | 54 | 52
2018-01-16 02:00 | 62 | 44 |  |  | 43116.0833 | 54 | 53
2018-01-16 02:30 | 61 | 43 |  |  | 43116.1042 | 53 | 51
2018-01-16 03:00 | 61 | 43 |  |  | 43116.125 | 52 | 50
2018-01-16 03:30 | 60 | 41 |  |  | 43116.1458 | 51 | 49
2018-01-16 04:00 | 60 | 41 |  |  | 43116.1667 | 51 | 49
2018-01-16 04:30 | 60 | 40 |  |  | 43116.1875 | 51 | 49
2018-01-16 05:00 | 58 | 41 |  |  | 43116.2083 | 52 | 51
2018-01-16 05:30 | 62 | 46 |  |  | 43116.2292 | 57 | 56
2018-01-16 06:00 | 63 | 49 |  |  | 43116.25 | 62 | 61
2018-01-16 06:30 | 64 | 53 |  |  | 43116.2708 | 68 | 68
2018-01-16 07:00 | 65 | 59 |  |  | 43116.2917 | 76 | 76
2018-01-16 07:30 | 71 | 65 |  |  | 43116.3125 | 84 | 84
2018-01-16 08:00 | 73 | 67 |  |  | 43116.3333 | 87 | 87
2018-01-16 08:30 | 75 | 68 |  |  | 43116.3542 | 89 | 89
2018-01-16 09:00 | 77 | 71 |  |  | 43116.375 | 92 | 92
2018-01-16 09:30 | 78 | 71 |  |  | 43116.3958 | 92 | 92
2018-01-16 10:00 | 81 | 74 |  |  | 43116.4167 | 94 | 94
2018-01-16 10:30 | 81 | 74 |  |  | 43116.4375 | 97 | 97
2018-01-16 11:00 | 81 | 75 |  |  | 43116.4583 | 100 | 99
2018-01-16 11:30 | 85 | 79 |  |  | 43116.4792 | 104 | 104
2018-01-16 12:00 | 89 | 83 |  |  | 43116.5 | 109 | 109
2018-01-16 12:30 | 96 | 85 |  |  | 43116.5208 | 112 | 111
2018-01-16 13:00 | 98 | 83 |  |  | 43116.5417 | 110 | 108
2018-01-16 13:30 | 95 | 80 |  |  | 43116.5625 | 106 | 103
2018-01-16 14:00 | 96 | 81 |  |  | 43116.5833 | 106 | 104
2018-01-16 14:30 | 98 | 84 |  |  | 43116.6042 | 108 | 106
2018-01-16 15:00 | 98 | 84 |  |  | 43116.625 | 108 | 106
2018-01-16 15:30 | 100 | 86 |  |  | 43116.6458 | 110 | 108
2018-01-16 16:00 | 103 | 88 |  |  | 43116.6667 | 112 | 110
2018-01-16 16:30 | 106 | 92 |  |  | 43116.6875 | 112 | 111
2018-01-16 17:00 | 108 | 93 |  |  | 43116.7083 | 112 | 111
2018-01-16 17:30 | 108 | 92 |  |  | 43116.7292 | 108 | 108
2018-01-16 18:00 | 108 | 89 |  |  | 43116.75 | 105 | 104
2018-01-16 18:30 | 106 | 87 |  |  | 43116.7708 | 100 | 100
2018-01-16 19:00 | 105 | 88 |  |  | 43116.7917 | 103 | 103
2018-01-16 19:30 | 105 | 89 |  |  | 43116.8125 | 104 | 103
2018-01-16 20:00 | 105 | 88 |  |  | 43116.8333 | 101 | 101
2018-01-16 20:30 | 101 | 85 |  |  | 43116.8542 | 98 | 97
2018-01-16 21:00 | 98 | 80 |  |  | 43116.875 | 92 | 91
2018-01-16 21:30 | 98 | 78 |  |  | 43116.8958 | 90 | 89
2018-01-16 22:00 | 94 | 75 |  |  | 43116.9167 | 88 | 88
2018-01-16 22:30 | 81 | 67 |  |  | 43116.9375 | 79 | 79
2018-01-16 23:00 | 68 | 61 |  |  | 43116.9583 | 74 | 70
2018-01-16 23:30 | 66 | 59 |  |  | 43116.9792 | 73 | 68
2018-01-17 | 62 | 54 |  |  | 43117 | 69 | 65
2018-01-17 00:30 | 56 | 48 |  |  | 43117.0208 | 62 | 57
2018-01-17 01:00 | 53 | 45 |  |  | 43117.0417 | 57 | 54
2018-01-17 01:30 | 53 | 44 |  |  | 43117.0625 | 55 | 52
2018-01-17 02:00 | 52 | 42 |  |  | 43117.0833 | 54 | 50
2018-01-17 02:30 | 50 | 40 |  |  | 43117.1042 | 52 | 48
2018-01-17 03:00 | 50 | 40 |  |  | 43117.125 | 52 | 48
2018-01-17 03:30 | 48 | 38 |  |  | 43117.1458 | 49 | 45
2018-01-17 04:00 | 47 | 36 |  |  | 43117.1667 | 48 | 44
2018-01-17 04:30 | 47 | 37 |  |  | 43117.1875 | 50 | 46
2018-01-17 05:00 | 49 | 39 |  |  | 43117.2083 | 52 | 48
2018-01-17 05:30 | 52 | 43 |  |  | 43117.2292 | 55 | 52
2018-01-17 06:00 | 55 | 47 |  |  | 43117.25 | 61 | 58
2018-01-17 06:30 | 58 | 52 |  |  | 43117.2708 | 67 | 66
2018-01-17 07:00 | 60 | 56 |  |  | 43117.2917 | 75 | 74
2018-01-17 07:30 | 64 | 62 |  |  | 43117.3125 | 81 | 81
2018-01-17 08:00 | 61 | 61 |  |  | 43117.3333 | 83 | 83
2018-01-17 08:30 | 56 | 55 |  |  | 43117.3542 | 80 | 80
2018-01-17 09:00 | 56 | 55 |  |  | 43117.375 | 82 | 82
2018-01-17 09:30 | 56 | 55 |  |  | 43117.3958 | 81 | 81
2018-01-17 10:00 | 54 | 53 |  |  | 43117.4167 | 79 | 79
2018-01-17 10:30 | 54 | 53 |  |  | 43117.4375 | 79 | 78
2018-01-17 11:00 | 54 | 52 |  |  | 43117.4583 | 78 | 78
2018-01-17 11:30 | 54 | 52 |  |  | 43117.4792 | 79 | 78
2018-01-17 12:00 | 56 | 55 |  |  | 43117.5 | 80 | 80
2018-01-17 12:30 | 57 | 55 |  |  | 43117.5208 | 82 | 81
2018-01-17 13:00 | 59 | 57 |  |  | 43117.5417 | 83 | 82
2018-01-17 13:30 | 60 | 59 |  |  | 43117.5625 | 85 | 85
2018-01-17 14:00 | 61 | 60 |  |  | 43117.5833 | 85 | 84
2018-01-17 14:30 | 61 | 60 |  |  | 43117.6042 | 86 | 85
2018-01-17 15:00 | 62 | 61 |  |  | 43117.625 | 86 | 86
2018-01-17 15:30 | 65 | 63 |  |  | 43117.6458 | 88 | 88
2018-01-17 16:00 | 67 | 67 |  |  | 43117.6667 | 92 | 92
2018-01-17 16:30 | 78 | 78 |  |  | 43117.6875 | 98 | 98
2018-01-17 17:00 | 83 | 83 |  |  | 43117.7083 | 102 | 101
2018-01-17 17:30 | 82 | 82 |  |  | 43117.7292 | 99 | 99
2018-01-17 18:00 | 81 | 81 |  |  | 43117.75 | 97 | 96
2018-01-17 18:30 | 77 | 75 |  |  | 43117.7708 | 91 | 90
2018-01-17 19:00 | 80 | 79 |  |  | 43117.7917 | 94 | 93
2018-01-17 19:30 | 82 | 81 |  |  | 43117.8125 | 95 | 94
2018-01-17 20:00 | 80 | 77 |  |  | 43117.8333 | 93 | 91
2018-01-17 20:30 | 79 | 75 |  |  | 43117.8542 | 90 | 88
2018-01-17 21:00 | 75 | 73 |  |  | 43117.875 | 86 | 86
2018-01-17 21:30 | 72 | 68 |  |  | 43117.8958 | 80 | 79
2018-01-17 22:00 | 72 | 68 |  |  | 43117.9167 | 81 | 80
2018-01-17 22:30 | 66 | 61 |  |  | 43117.9375 | 76 | 75
2018-01-17 23:00 | 62 | 57 |  |  | 43117.9583 | 71 | 69
2018-01-17 23:30 | 59 | 53 |  |  | 43117.9792 | 67 | 66
2018-01-18 | 57 | 50 |  |  | 43118 | 64 | 62
2018-01-18 00:30 | 54 | 46 |  |  | 43118.0208 | 59 | 56
2018-01-18 01:00 | 54 | 44 |  |  | 43118.0417 | 57 | 54
2018-01-18 01:30 | 54 | 43 |  |  | 43118.0625 | 56 | 53
2018-01-18 02:00 | 53 | 41 |  |  | 43118.0833 | 54 | 51
2018-01-18 02:30 | 52 | 39 |  |  | 43118.1042 | 53 | 49
2018-01-18 03:00 | 52 | 39 |  |  | 43118.125 | 52 | 48
2018-01-18 03:30 | 52 | 39 |  |  | 43118.1458 | 52 | 48
2018-01-18 04:00 | 51 | 38 |  |  | 43118.1667 | 51 | 47
2018-01-18 04:30 | 52 | 39 |  |  | 43118.1875 | 52 | 48
2018-01-18 05:00 | 51 | 40 |  |  | 43118.2083 | 53 | 49
2018-01-18 05:30 | 51 | 41 |  |  | 43118.2292 | 54 | 51
2018-01-18 06:00 | 57 | 48 |  |  | 43118.25 | 62 | 60
2018-01-18 06:30 | 61 | 55 |  |  | 43118.2708 | 72 | 71
2018-01-18 07:00 | 64 | 60 |  |  | 43118.2917 | 80 | 79
2018-01-18 07:30 | 70 | 69 |  |  | 43118.3125 | 89 | 88
2018-01-18 08:00 | 65 | 65 |  |  | 43118.3333 | 86 | 86
2018-01-18 08:30 | 67 | 66 |  |  | 43118.3542 | 87 | 87
2018-01-18 09:00 | 69 | 68 |  |  | 43118.375 | 88 | 88
2018-01-18 09:30 | 72 | 72 |  |  | 43118.3958 | 93 | 93
2018-01-18 10:00 | 72 | 71 |  |  | 43118.4167 | 93 | 93
2018-01-18 10:30 | 73 | 73 |  |  | 43118.4375 | 93 | 93
2018-01-18 11:00 | 72 | 72 |  |  | 43118.4583 | 92 | 92
2018-01-18 11:30 | 74 | 74 |  |  | 43118.4792 | 94 | 93
2018-01-18 12:00 | 75 | 75 |  |  | 43118.5 | 95 | 94
2018-01-18 12:30 | 75 | 75 |  |  | 43118.5208 | 94 | 94
2018-01-18 13:00 | 76 | 76 |  |  | 43118.5417 | 94 | 94
2018-01-18 13:30 | 78 | 78 |  |  | 43118.5625 | 98 | 98
2018-01-18 14:00 | 80 | 80 |  |  | 43118.5833 | 99 | 98
2018-01-18 14:30 | 73 | 73 |  |  | 43118.6042 | 95 | 95
2018-01-18 15:00 | 72 | 72 |  |  | 43118.625 | 93 | 93
2018-01-18 15:30 | 74 | 74 |  |  | 43118.6458 | 95 | 94
2018-01-18 16:00 | 72 | 72 |  |  | 43118.6667 | 93 | 93
2018-01-18 16:30 | 72 | 72 |  |  | 43118.6875 | 93 | 92
2018-01-18 17:00 | 72 | 72 |  |  | 43118.7083 | 92 | 91
2018-01-18 17:30 | 73 | 73 |  |  | 43118.7292 | 91 | 90
2018-01-18 18:00 | 73 | 73 |  |  | 43118.75 | 90 | 89
2018-01-18 18:30 | 70 | 70 |  |  | 43118.7708 | 86 | 85
2018-01-18 19:00 | 72 | 72 |  |  | 43118.7917 | 89 | 88
2018-01-18 19:30 | 73 | 72 |  |  | 43118.8125 | 90 | 89
2018-01-18 20:00 | 72 | 72 |  |  | 43118.8333 | 89 | 88
2018-01-18 20:30 | 72 | 71 |  |  | 43118.8542 | 86 | 86
2018-01-18 21:00 | 70 | 70 |  |  | 43118.875 | 82 | 82
2018-01-18 21:30 | 65 | 65 |  |  | 43118.8958 | 79 | 79
2018-01-18 22:00 | 65 | 63 |  |  | 43118.9167 | 80 | 79
2018-01-18 22:30 | 65 | 61 |  |  | 43118.9375 | 76 | 74
2018-01-18 23:00 | 63 | 59 |  |  | 43118.9583 | 71 | 70
2018-01-18 23:30 | 62 | 57 |  |  | 43118.9792 | 70 | 68
2018-01-19 | 60 | 52 |  |  | 43119 | 65 | 63
2018-01-19 00:30 | 58 | 45 |  |  | 43119.0208 | 59 | 54
2018-01-19 01:00 | 56 | 42 |  |  | 43119.0417 | 56 | 50
2018-01-19 01:30 | 55 | 40 |  |  | 43119.0625 | 55 | 48
2018-01-19 02:00 | 54 | 38 |  |  | 43119.0833 | 55 | 48
2018-01-19 02:30 | 53 | 37 |  |  | 43119.1042 | 53 | 45
2018-01-19 03:00 | 51 | 36 |  |  | 43119.125 | 51 | 44
2018-01-19 03:30 | 50 | 35 |  |  | 43119.1458 | 48 | 42
2018-01-19 04:00 | 49 | 33 |  |  | 43119.1667 | 47 | 40
2018-01-19 04:30 | 48 | 33 |  |  | 43119.1875 | 48 | 41
2018-01-19 05:00 | 48 | 34 |  |  | 43119.2083 | 49 | 44
2018-01-19 05:30 | 52 | 39 |  |  | 43119.2292 | 54 | 50
2018-01-19 06:00 | 50 | 40 |  |  | 43119.25 | 55 | 51
2018-01-19 06:30 | 53 | 46 |  |  | 43119.2708 | 62 | 60
2018-01-19 07:00 | 55 | 51 |  |  | 43119.2917 | 68 | 68
2018-01-19 07:30 | 66 | 60 |  |  | 43119.3125 | 84 | 80
2018-01-19 08:00 | 71 | 60 |  |  | 43119.3333 | 90 | 81
2018-01-19 08:30 | 71 | 61 |  |  | 43119.3542 | 90 | 82
2018-01-19 09:00 | 71 | 61 |  |  | 43119.375 | 91 | 82
2018-01-19 09:30 | 70 | 60 |  |  | 43119.3958 | 89 | 80
2018-01-19 10:00 | 71 | 61 |  |  | 43119.4167 | 89 | 81
2018-01-19 10:30 | 71 | 60 |  |  | 43119.4375 | 88 | 81
2018-01-19 11:00 | 70 | 60 |  |  | 43119.4583 | 88 | 82
2018-01-19 11:30 | 70 | 61 |  |  | 43119.4792 | 88 | 82
2018-01-19 12:00 | 69 | 61 |  |  | 43119.5 | 89 | 82
2018-01-19 12:30 | 68 | 61 |  |  | 43119.5208 | 90 | 83
2018-01-19 13:00 | 69 | 62 |  |  | 43119.5417 | 90 | 84
2018-01-19 13:30 | 69 | 62 |  |  | 43119.5625 | 90 | 84
2018-01-19 14:00 | 70 | 64 |  |  | 43119.5833 | 90 | 84
2018-01-19 14:30 | 72 | 65 |  |  | 43119.6042 | 92 | 85
2018-01-19 15:00 | 75 | 69 |  |  | 43119.625 | 97 | 90
2018-01-19 15:30 | 77 | 71 |  |  | 43119.6458 | 98 | 91
2018-01-19 16:00 | 81 | 74 |  |  | 43119.6667 | 102 | 94
2018-01-19 16:30 | 82 | 75 |  |  | 43119.6875 | 104 | 95
2018-01-19 17:00 | 85 | 77 |  |  | 43119.7083 | 106 | 97
2018-01-19 17:30 | 85 | 77 |  |  | 43119.7292 | 105 | 95
2018-01-19 18:00 | 82 | 73 |  |  | 43119.75 | 100 | 91
2018-01-19 18:30 | 77 | 68 |  |  | 43119.7708 | 94 | 84
2018-01-19 19:00 | 78 | 70 |  |  | 43119.7917 | 94 | 86
2018-01-19 19:30 | 78 | 70 |  |  | 43119.8125 | 95 | 87
2018-01-19 20:00 | 78 | 69 |  |  | 43119.8333 | 95 | 86
2018-01-19 20:30 | 77 | 69 |  |  | 43119.8542 | 93 | 84
2018-01-19 21:00 | 75 | 72 |  |  | 43119.875 | 87 | 85
2018-01-19 21:30 | 74 | 70 |  |  | 43119.8958 | 84 | 81
2018-01-19 22:00 | 72 | 66 |  |  | 43119.9167 | 82 | 79
2018-01-19 22:30 | 66 | 60 |  |  | 43119.9375 | 76 | 74
2018-01-19 23:00 | 65 | 58 |  |  | 43119.9583 | 73 | 70
2018-01-19 23:30 | 63 | 54 |  |  | 43119.9792 | 70 | 66
2018-01-20 | 58 | 47 |  |  | 43120 | 63 | 59
2018-01-20 00:30 | 52 | 40 |  |  | 43120.0208 | 56 | 51
2018-01-20 01:00 | 51 | 39 |  |  | 43120.0417 | 54 | 50
2018-01-20 01:30 | 54 | 41 |  |  | 43120.0625 | 57 | 53
2018-01-20 02:00 | 56 | 43 |  |  | 43120.0833 | 59 | 54
2018-01-20 02:30 | 54 | 40 |  |  | 43120.1042 | 57 | 51
2018-01-20 03:00 | 54 | 40 |  |  | 43120.125 | 57 | 52
2018-01-20 03:30 | 55 | 41 |  |  | 43120.1458 | 58 | 52
2018-01-20 04:00 | 57 | 44 |  |  | 43120.1667 | 60 | 54
2018-01-20 04:30 | 58 | 44 |  |  | 43120.1875 | 61 | 54
2018-01-20 05:00 | 58 | 44 |  |  | 43120.2083 | 61 | 55
2018-01-20 05:30 | 58 | 44 |  |  | 43120.2292 | 62 | 55
2018-01-20 06:00 | 58 | 44 |  |  | 43120.25 | 61 | 55
2018-01-20 06:30 | 57 | 44 |  |  | 43120.2708 | 63 | 57
2018-01-20 07:00 | 58 | 46 |  |  | 43120.2917 | 64 | 59
2018-01-20 07:30 | 59 | 49 |  |  | 43120.3125 | 66 | 63
2018-01-20 08:00 | 60 | 52 |  |  | 43120.3333 | 68 | 66
2018-01-20 08:30 | 62 | 54 |  |  | 43120.3542 | 72 | 70
2018-01-20 09:00 | 62 | 56 |  |  | 43120.375 | 73 | 71
2018-01-20 09:30 | 60 | 53 |  |  | 43120.3958 | 70 | 68
2018-01-20 10:00 | 57 | 51 |  |  | 43120.4167 | 67 | 65
2018-01-20 10:30 | 55 | 49 |  |  | 43120.4375 | 64 | 63
2018-01-20 11:00 | 54 | 49 |  |  | 43120.4583 | 64 | 63
2018-01-20 11:30 | 54 | 49 |  |  | 43120.4792 | 64 | 64
2018-01-20 12:00 | 55 | 49 |  |  | 43120.5 | 64 | 63
2018-01-20 12:30 | 54 | 49 |  |  | 43120.5208 | 64 | 63
2018-01-20 13:00 | 54 | 49 |  |  | 43120.5417 | 62 | 62
2018-01-20 13:30 | 57 | 52 |  |  | 43120.5625 | 65 | 64
2018-01-20 14:00 | 59 | 57 |  |  | 43120.5833 | 67 | 67
2018-01-20 14:30 | 61 | 59 |  |  | 43120.6042 | 70 | 69
2018-01-20 15:00 | 63 | 61 |  |  | 43120.625 | 72 | 72
2018-01-20 15:30 | 65 | 64 |  |  | 43120.6458 | 75 | 75
2018-01-20 16:00 | 67 | 67 |  |  | 43120.6667 | 78 | 78
2018-01-20 16:30 | 71 | 70 |  |  | 43120.6875 | 82 | 82
2018-01-20 17:00 | 72 | 72 |  |  | 43120.7083 | 84 | 84
2018-01-20 17:30 | 72 | 72 |  |  | 43120.7292 | 84 | 84
2018-01-20 18:00 | 70 | 70 |  |  | 43120.75 | 83 | 82
2018-01-20 18:30 | 70 | 69 |  |  | 43120.7708 | 82 | 82
2018-01-20 19:00 | 70 | 69 |  |  | 43120.7917 | 85 | 85
2018-01-20 19:30 | 72 | 72 |  |  | 43120.8125 | 86 | 85
2018-01-20 20:00 | 70 | 69 |  |  | 43120.8333 | 85 | 84
2018-01-20 20:30 | 71 | 69 |  |  | 43120.8542 | 83 | 83
2018-01-20 21:00 | 68 | 67 |  |  | 43120.875 | 81 | 80
2018-01-20 21:30 | 65 | 64 |  |  | 43120.8958 | 77 | 76
2018-01-20 22:00 | 64 | 62 |  |  | 43120.9167 | 76 | 75
2018-01-20 22:30 | 63 | 57 |  |  | 43120.9375 | 73 | 72
2018-01-20 23:00 | 61 | 55 |  |  | 43120.9583 | 71 | 69
2018-01-20 23:30 | 59 | 53 |  |  | 43120.9792 | 68 | 66
2018-01-21 | 55 | 47 |  |  | 43121 | 62 | 60
2018-01-21 00:30 | 51 | 42 |  |  | 43121.0208 | 57 | 54
2018-01-21 01:00 | 50 | 37 |  |  | 43121.0417 | 53 | 49
2018-01-21 01:30 | 49 | 35 |  |  | 43121.0625 | 52 | 47
2018-01-21 02:00 | 50 | 36 |  |  | 43121.0833 | 52 | 48
2018-01-21 02:30 | 50 | 36 |  |  | 43121.1042 | 52 | 47
2018-01-21 03:00 | 49 | 34 |  |  | 43121.125 | 50 | 44
2018-01-21 03:30 | 49 | 34 |  |  | 43121.1458 | 50 | 45
2018-01-21 04:00 | 48 | 33 |  |  | 43121.1667 | 49 | 44
2018-01-21 04:30 | 49 | 33 |  |  | 43121.1875 | 50 | 44
2018-01-21 05:00 | 49 | 33 |  |  | 43121.2083 | 50 | 44
2018-01-21 05:30 | 50 | 32 |  |  | 43121.2292 | 49 | 42
2018-01-21 06:00 | 48 | 30 |  |  | 43121.25 | 47 | 41
2018-01-21 06:30 | 48 | 30 |  |  | 43121.2708 | 48 | 42
2018-01-21 07:00 | 47 | 30 |  |  | 43121.2917 | 49 | 44
2018-01-21 07:30 | 48 | 34 |  |  | 43121.3125 | 52 | 47
2018-01-21 08:00 | 50 | 39 |  |  | 43121.3333 | 55 | 52
2018-01-21 08:30 | 49 | 39 |  |  | 43121.3542 | 57 | 54
2018-01-21 09:00 | 52 | 44 |  |  | 43121.375 | 61 | 59
2018-01-21 09:30 | 55 | 49 |  |  | 43121.3958 | 66 | 64
2018-01-21 10:00 | 55 | 48 |  |  | 43121.4167 | 66 | 65
2018-01-21 10:30 | 53 | 45 |  |  | 43121.4375 | 58 | 56
2018-01-21 11:00 | 52 | 45 |  |  | 43121.4583 | 58 | 56
2018-01-21 11:30 | 56 | 50 |  |  | 43121.4792 | 62 | 60
2018-01-21 12:00 | 55 | 49 |  |  | 43121.5 | 61 | 60
2018-01-21 12:30 | 55 | 49 |  |  | 43121.5208 | 59 | 57
2018-01-21 13:00 | 58 | 52 |  |  | 43121.5417 | 64 | 63
2018-01-21 13:30 | 60 | 54 |  |  | 43121.5625 | 67 | 66
2018-01-21 14:00 | 60 | 54 |  |  | 43121.5833 | 65 | 63
2018-01-21 14:30 | 62 | 57 |  |  | 43121.6042 | 67 | 65
2018-01-21 15:00 | 63 | 59 |  |  | 43121.625 | 72 | 70
2018-01-21 15:30 | 66 | 63 |  |  | 43121.6458 | 74 | 73
2018-01-21 16:00 | 66 | 62 |  |  | 43121.6667 | 76 | 74
2018-01-21 16:30 | 67 | 62 |  |  | 43121.6875 | 76 | 74
2018-01-21 17:00 | 68 | 63 |  |  | 43121.7083 | 78 | 76
2018-01-21 17:30 | 69 | 64 |  |  | 43121.7292 | 80 | 78
2018-01-21 18:00 | 68 | 63 |  |  | 43121.75 | 79 | 77
2018-01-21 18:30 | 70 | 65 |  |  | 43121.7708 | 81 | 79
2018-01-21 19:00 | 73 | 68 |  |  | 43121.7917 | 85 | 83
2018-01-21 19:30 | 76 | 72 |  |  | 43121.8125 | 90 | 88
2018-01-21 20:00 | 77 | 73 |  |  | 43121.8333 | 90 | 89
2018-01-21 20:30 | 76 | 72 |  |  | 43121.8542 | 89 | 87
2018-01-21 21:00 | 75 | 70 |  |  | 43121.875 | 86 | 84
2018-01-21 21:30 | 71 | 66 |  |  | 43121.8958 | 82 | 80
2018-01-21 22:00 | 69 | 64 |  |  | 43121.9167 | 81 | 79
2018-01-21 22:30 | 66 | 62 |  |  | 43121.9375 | 78 | 76
2018-01-21 23:00 | 63 | 58 |  |  | 43121.9583 | 74 | 72
2018-01-21 23:30 | 61 | 54 |  |  | 43121.9792 | 71 | 69
2018-01-22 | 59 | 49 |  |  | 43122 | 66 | 64
2018-01-22 00:30 | 54 | 43 |  |  | 43122.0208 | 59 | 56
2018-01-22 01:00 | 53 | 41 |  |  | 43122.0417 | 57 | 54
2018-01-22 01:30 | 53 | 40 |  |  | 43122.0625 | 56 | 52
2018-01-22 02:00 | 51 | 37 |  |  | 43122.0833 | 53 | 49
2018-01-22 02:30 | 48 | 34 |  |  | 43122.1042 | 50 | 46
2018-01-22 03:00 | 48 | 34 |  |  | 43122.125 | 49 | 45
2018-01-22 03:30 | 49 | 35 |  |  | 43122.1458 | 50 | 45
2018-01-22 04:00 | 50 | 36 |  |  | 43122.1667 | 51 | 47
2018-01-22 04:30 | 50 | 36 |  |  | 43122.1875 | 52 | 48
2018-01-22 05:00 | 49 | 36 |  |  | 43122.2083 | 52 | 48
2018-01-22 05:30 | 51 | 40 |  |  | 43122.2292 | 55 | 52
2018-01-22 06:00 | 52 | 44 |  |  | 43122.25 | 58 | 56
2018-01-22 06:30 | 59 | 52 |  |  | 43122.2708 | 70 | 69
2018-01-22 07:00 | 65 | 59 |  |  | 43122.2917 | 79 | 78
2018-01-22 07:30 | 72 | 65 |  |  | 43122.3125 | 89 | 87
2018-01-22 08:00 | 73 | 67 |  |  | 43122.3333 | 93 | 91
2018-01-22 08:30 | 75 | 71 |  |  | 43122.3542 | 98 | 97
2018-01-22 09:00 | 76 | 72 |  |  | 43122.375 | 101 | 99
2018-01-22 09:30 | 79 | 74 |  |  | 43122.3958 | 102 | 100
2018-01-22 10:00 | 81 | 75 |  |  | 43122.4167 | 104 | 101
2018-01-22 10:30 | 81 | 75 |  |  | 43122.4375 | 104 | 100
2018-01-22 11:00 | 83 | 77 |  |  | 43122.4583 | 103 | 100
2018-01-22 11:30 | 83 | 78 |  |  | 43122.4792 | 104 | 101
2018-01-22 12:00 | 83 | 78 |  |  | 43122.5 | 106 | 102
2018-01-22 12:30 | 83 | 78 |  |  | 43122.5208 | 105 | 102
2018-01-22 13:00 | 84 | 80 |  |  | 43122.5417 | 106 | 103
2018-01-22 13:30 | 85 | 81 |  |  | 43122.5625 | 108 | 104
2018-01-22 14:00 | 85 | 80 |  |  | 43122.5833 | 110 | 104
2018-01-22 14:30 | 87 | 82 |  |  | 43122.6042 | 112 | 106
2018-01-22 15:00 | 88 | 82 |  |  | 43122.625 | 112 | 106
2018-01-22 15:30 | 90 | 82 |  |  | 43122.6458 | 110 | 106
2018-01-22 16:00 | 99 | 84 |  |  | 43122.6667 | 111 | 109
2018-01-22 16:30 | 107 | 86 |  |  | 43122.6875 | 116 | 112
2018-01-22 17:00 | 109 | 89 |  |  | 43122.7083 | 119 | 115
2018-01-22 17:30 | 105 | 90 |  |  | 43122.7292 | 119 | 113
2018-01-22 18:00 | 93 | 88 |  |  | 43122.75 | 123 | 108
2018-01-22 18:30 | 88 | 83 |  |  | 43122.7708 | 117 | 100
2018-01-22 19:00 | 87 | 83 |  |  | 43122.7917 | 117 | 102
2018-01-22 19:30 | 88 | 84 |  |  | 43122.8125 | 117 | 103
2018-01-22 20:00 | 88 | 85 |  |  | 43122.8333 | 117 | 103
2018-01-22 20:30 | 88 | 84 |  |  | 43122.8542 | 116 | 102
2018-01-22 21:00 | 83 | 81 |  |  | 43122.875 | 106 | 97
2018-01-22 21:30 | 77 | 75 |  |  | 43122.8958 | 100 | 91
2018-01-22 22:00 | 74 | 72 |  |  | 43122.9167 | 96 | 88
2018-01-22 22:30 | 68 | 67 |  |  | 43122.9375 | 85 | 83
2018-01-22 23:00 | 67 | 67 |  |  | 43122.9583 | 85 | 81
2018-01-22 23:30 | 65 | 64 |  |  | 43122.9792 | 82 | 78
2018-01-23 | 57 | 56 |  |  | 43123 | 74 | 71
2018-01-23 00:30 | 53 | 52 |  |  | 43123.0208 | 68 | 64
2018-01-23 01:00 | 49 | 48 |  |  | 43123.0417 | 64 | 59
2018-01-23 01:30 | 47 | 46 |  |  | 43123.0625 | 63 | 59
2018-01-23 02:00 | 47 | 47 |  |  | 43123.0833 | 63 | 58
2018-01-23 02:30 | 47 | 46 |  |  | 43123.1042 | 61 | 57
2018-01-23 03:00 | 46 | 45 |  |  | 43123.125 | 61 | 56
2018-01-23 03:30 | 45 | 44 |  |  | 43123.1458 | 61 | 56
2018-01-23 04:00 | 45 | 44 |  |  | 43123.1667 | 61 | 55
2018-01-23 04:30 | 46 | 45 |  |  | 43123.1875 | 62 | 57
2018-01-23 05:00 | 48 | 47 |  |  | 43123.2083 | 64 | 60
2018-01-23 05:30 | 50 | 49 |  |  | 43123.2292 | 67 | 63
2018-01-23 06:00 | 53 | 53 |  |  | 43123.25 | 71 | 68
2018-01-23 06:30 | 58 | 57 |  |  | 43123.2708 | 80 | 77
2018-01-23 07:00 | 61 | 61 |  |  | 43123.2917 | 84 | 82
2018-01-23 07:30 | 67 | 67 |  |  | 43123.3125 | 95 | 92
2018-01-23 08:00 | 71 | 70 |  |  | 43123.3333 | 100 | 95
2018-01-23 08:30 | 74 | 73 |  |  | 43123.3542 | 104 | 99
2018-01-23 09:00 | 75 | 73 |  |  | 43123.375 | 108 | 100
2018-01-23 09:30 | 64 | 61 |  |  | 43123.3958 | 89 | 77
2018-01-23 10:00 | 74 | 72 |  |  | 43123.4167 | 104 | 94
2018-01-23 10:30 | 77 | 74 |  |  | 43123.4375 | 110 | 99
2018-01-23 11:00 | 80 | 77 |  |  | 43123.4583 | 114 | 104
2018-01-23 11:30 | 80 | 78 |  |  | 43123.4792 | 114 | 104
2018-01-23 12:00 | 80 | 78 |  |  | 43123.5 | 114 | 104
2018-01-23 12:30 | 83 | 81 |  |  | 43123.5208 | 116 | 106
2018-01-23 13:00 | 84 | 82 |  |  | 43123.5417 | 117 | 107
2018-01-23 13:30 | 87 | 85 |  |  | 43123.5625 | 121 | 110
2018-01-23 14:00 | 90 | 86 |  |  | 43123.5833 | 124 | 111
2018-01-23 14:30 | 91 | 87 |  |  | 43123.6042 | 126 | 112
2018-01-23 15:00 | 90 | 86 |  |  | 43123.625 | 126 | 112
2018-01-23 15:30 | 90 | 86 |  |  | 43123.6458 | 128 | 114
2018-01-23 16:00 | 92 | 88 |  |  | 43123.6667 | 130 | 114
2018-01-23 16:30 | 94 | 91 |  |  | 43123.6875 | 130 | 117
2018-01-23 17:00 | 96 | 93 |  |  | 43123.7083 | 132 | 119
2018-01-23 17:30 | 97 | 93 |  |  | 43123.7292 | 131 | 116
2018-01-23 18:00 | 93 | 89 |  |  | 43123.75 | 126 | 111
2018-01-23 18:30 | 88 | 84 |  |  | 43123.7708 | 117 | 105
2018-01-23 19:00 | 89 | 87 |  |  | 43123.7917 | 118 | 107
2018-01-23 19:30 | 89 | 87 |  |  | 43123.8125 | 118 | 108
2018-01-23 20:00 | 90 | 87 |  |  | 43123.8333 | 118 | 107
2018-01-23 20:30 | 88 | 86 |  |  | 43123.8542 | 113 | 105
2018-01-23 21:00 | 85 | 84 |  |  | 43123.875 | 105 | 101
2018-01-23 21:30 | 79 | 78 |  |  | 43123.8958 | 100 | 95
2018-01-23 22:00 | 74 | 73 |  |  | 43123.9167 | 97 | 91
2018-01-23 22:30 | 71 | 68 |  |  | 43123.9375 | 92 | 85
2018-01-23 23:00 | 70 | 66 |  |  | 43123.9583 | 89 | 81
2018-01-23 23:30 | 66 | 63 |  |  | 43123.9792 | 85 | 79
2018-01-24 | 62 | 58 |  |  | 43124 | 81 | 73
2018-01-24 00:30 | 58 | 52 |  |  | 43124.0208 | 75 | 67
2018-01-24 01:00 | 55 | 48 |  |  | 43124.0417 | 72 | 62
2018-01-24 01:30 | 54 | 46 |  |  | 43124.0625 | 70 | 59
2018-01-24 02:00 | 54 | 45 |  |  | 43124.0833 | 70 | 59
2018-01-24 02:30 | 53 | 45 |  |  | 43124.1042 | 69 | 57
2018-01-24 03:00 | 52 | 44 |  |  | 43124.125 | 68 | 57
2018-01-24 03:30 | 51 | 43 |  |  | 43124.1458 | 68 | 56
2018-01-24 04:00 | 50 | 42 |  |  | 43124.1667 | 68 | 56
2018-01-24 04:30 | 51 | 44 |  |  | 43124.1875 | 69 | 57
2018-01-24 05:00 | 53 | 46 |  |  | 43124.2083 | 70 | 59
2018-01-24 05:30 | 55 | 49 |  |  | 43124.2292 | 73 | 63
2018-01-24 06:00 | 60 | 53 |  |  | 43124.25 | 81 | 68
2018-01-24 06:30 | 63 | 57 |  |  | 43124.2708 | 87 | 75
2018-01-24 07:00 | 67 | 62 |  |  | 43124.2917 | 94 | 84
2018-01-24 07:30 | 73 | 70 |  |  | 43124.3125 | 102 | 96
2018-01-24 08:00 | 81 | 75 |  |  | 43124.3333 | 106 | 101
2018-01-24 08:30 | 85 | 77 |  |  | 43124.3542 | 112 | 105
2018-01-24 09:00 | 84 | 74 |  |  | 43124.375 | 112 | 103
2018-01-24 09:30 | 88 | 79 |  |  | 43124.3958 | 113 | 105
2018-01-24 10:00 | 89 | 80 |  |  | 43124.4167 | 116 | 109
2018-01-24 10:30 | 77 | 67 |  |  | 43124.4375 | 109 | 101
2018-01-24 11:00 | 61 | 49 |  |  | 43124.4583 | 96 | 88
2018-01-24 11:30 | 60 | 49 |  |  | 43124.4792 | 94 | 87
2018-01-24 12:00 | 73 | 63 |  |  | 43124.5 | 105 | 97
2018-01-24 12:30 | 87 | 77 |  |  | 43124.5208 | 113 | 106
2018-01-24 13:00 | 88 | 78 |  |  | 43124.5417 | 114 | 107
2018-01-24 13:30 | 89 | 80 |  |  | 43124.5625 | 112 | 106
2018-01-24 14:00 | 92 | 82 |  |  | 43124.5833 | 114 | 107
2018-01-24 14:30 | 90 | 83 |  |  | 43124.6042 | 117 | 111
2018-01-24 15:00 | 89 | 82 |  |  | 43124.625 | 118 | 111
2018-01-24 15:30 | 93 | 86 |  |  | 43124.6458 | 121 | 115
2018-01-24 16:00 | 95 | 88 |  |  | 43124.6667 | 123 | 116
2018-01-24 16:30 | 98 | 92 |  |  | 43124.6875 | 126 | 119
2018-01-24 17:00 | 100 | 93 |  |  | 43124.7083 | 127 | 119
2018-01-24 17:30 | 100 | 93 |  |  | 43124.7292 | 125 | 117
2018-01-24 18:00 | 97 | 88 |  |  | 43124.75 | 120 | 111
2018-01-24 18:30 | 96 | 86 |  |  | 43124.7708 | 116 | 106
2018-01-24 19:00 | 97 | 88 |  |  | 43124.7917 | 117 | 108
2018-01-24 19:30 | 98 | 90 |  |  | 43124.8125 | 118 | 110
2018-01-24 20:00 | 99 | 90 |  |  | 43124.8333 | 119 | 110
2018-01-24 20:30 | 99 | 90 |  |  | 43124.8542 | 117 | 108
2018-01-24 21:00 | 95 | 87 |  |  | 43124.875 | 114 | 106
2018-01-24 21:30 | 91 | 82 |  |  | 43124.8958 | 108 | 99
2018-01-24 22:00 | 88 | 79 |  |  | 43124.9167 | 104 | 98
2018-01-24 22:30 | 82 | 74 |  |  | 43124.9375 | 97 | 92
2018-01-24 23:00 | 79 | 72 |  |  | 43124.9583 | 93 | 89
2018-01-24 23:30 | 76 | 69 |  |  | 43124.9792 | 90 | 86
2018-01-25 | 73 | 65 |  |  | 43125 | 85 | 81
2018-01-25 00:30 | 69 | 59 |  |  | 43125.0208 | 79 | 75
2018-01-25 01:00 | 70 | 57 |  |  | 43125.0417 | 77 | 72
2018-01-25 01:30 | 67 | 55 |  |  | 43125.0625 | 75 | 70
2018-01-25 02:00 | 68 | 55 |  |  | 43125.0833 | 75 | 70
2018-01-25 02:30 | 67 | 54 |  |  | 43125.1042 | 75 | 70
2018-01-25 03:00 | 66 | 53 |  |  | 43125.125 | 73 | 68
2018-01-25 03:30 | 65 | 52 |  |  | 43125.1458 | 72 | 67
2018-01-25 04:00 | 64 | 50 |  |  | 43125.1667 | 70 | 65
2018-01-25 04:30 | 65 | 51 |  |  | 43125.1875 | 72 | 66
2018-01-25 05:00 | 64 | 52 |  |  | 43125.2083 | 72 | 67
2018-01-25 05:30 | 70 | 55 |  |  | 43125.2292 | 80 | 72
2018-01-25 06:00 | 73 | 59 |  |  | 43125.25 | 85 | 78
2018-01-25 06:30 | 76 | 64 |  |  | 43125.2708 | 92 | 86
2018-01-25 07:00 | 76 | 68 |  |  | 43125.2917 | 96 | 92
2018-01-25 07:30 | 79 | 73 |  |  | 43125.3125 | 103 | 100
2018-01-25 08:00 | 85 | 77 |  |  | 43125.3333 | 110 | 105
2018-01-25 08:30 | 91 | 83 |  |  | 43125.3542 | 118 | 113
2018-01-25 09:00 | 93 | 85 |  |  | 43125.375 | 122 | 116
2018-01-25 09:30 | 93 | 84 |  |  | 43125.3958 | 120 | 115
2018-01-25 10:00 | 94 | 85 |  |  | 43125.4167 | 119 | 114
2018-01-25 10:30 | 93 | 86 |  |  | 43125.4375 | 121 | 115
2018-01-25 11:00 | 93 | 87 |  |  | 43125.4583 | 120 | 115
2018-01-25 11:30 | 93 | 87 |  |  | 43125.4792 | 120 | 115
2018-01-25 12:00 | 92 | 86 |  |  | 43125.5 | 119 | 115
2018-01-25 12:30 | 94 | 88 |  |  | 43125.5208 | 121 | 116
2018-01-25 13:00 | 92 | 86 |  |  | 43125.5417 | 119 | 114
2018-01-25 13:30 | 94 | 88 |  |  | 43125.5625 | 121 | 116
2018-01-25 14:00 | 97 | 90 |  |  | 43125.5833 | 125 | 119
2018-01-25 14:30 | 95 | 88 |  |  | 43125.6042 | 124 | 118
2018-01-25 15:00 | 97 | 90 |  |  | 43125.625 | 125 | 119
2018-01-25 15:30 | 99 | 92 |  |  | 43125.6458 | 126 | 119
2018-01-25 16:00 | 101 | 94 |  |  | 43125.6667 | 127 | 120
2018-01-25 16:30 | 109 | 102 |  |  | 43125.6875 | 135 | 127
2018-01-25 17:00 | 110 | 102 |  |  | 43125.7083 | 135 | 127
2018-01-25 17:30 | 105 | 98 |  |  | 43125.7292 | 127 | 122
2018-01-25 18:00 | 100 | 96 |  |  | 43125.75 | 121 | 119
2018-01-25 18:30 | 98 | 94 |  |  | 43125.7708 | 116 | 114
2018-01-25 19:00 | 96 | 94 |  |  | 43125.7917 | 115 | 115
2018-01-25 19:30 | 97 | 95 |  |  | 43125.8125 | 115 | 115
2018-01-25 20:00 | 97 | 95 |  |  | 43125.8333 | 114 | 114
2018-01-25 20:30 | 96 | 93 |  |  | 43125.8542 | 112 | 111
2018-01-25 21:00 | 94 | 92 |  |  | 43125.875 | 108 | 108
2018-01-25 21:30 | 87 | 85 |  |  | 43125.8958 | 100 | 100
2018-01-25 22:00 | 83 | 80 |  |  | 43125.9167 | 97 | 96
2018-01-25 22:30 | 77 | 74 |  |  | 43125.9375 | 92 | 92
2018-01-25 23:00 | 75 | 72 |  |  | 43125.9583 | 89 | 88
2018-01-25 23:30 | 70 | 69 |  |  | 43125.9792 | 86 | 85
2018-01-26 | 63 | 62 |  |  | 43126 | 79 | 78
2018-01-26 00:30 | 62 | 57 |  |  | 43126.0208 | 73 | 72
2018-01-26 01:00 | 59 | 52 |  |  | 43126.0417 | 68 | 67
2018-01-26 01:30 | 57 | 50 |  |  | 43126.0625 | 66 | 65
2018-01-26 02:00 | 57 | 49 |  |  | 43126.0833 | 65 | 64
2018-01-26 02:30 | 56 | 48 |  |  | 43126.1042 | 64 | 63
2018-01-26 03:00 | 54 | 46 |  |  | 43126.125 | 62 | 61
2018-01-26 03:30 | 54 | 46 |  |  | 43126.1458 | 61 | 60
2018-01-26 04:00 | 53 | 44 |  |  | 43126.1667 | 60 | 59
2018-01-26 04:30 | 53 | 45 |  |  | 43126.1875 | 60 | 59
2018-01-26 05:00 | 52 | 44 |  |  | 43126.2083 | 60 | 59
2018-01-26 05:30 | 53 | 44 |  |  | 43126.2292 | 61 | 60
2018-01-26 06:00 | 51 | 43 |  |  | 43126.25 | 61 | 59
2018-01-26 06:30 | 51 | 43 |  |  | 43126.2708 | 62 | 62
2018-01-26 07:00 | 53 | 45 |  |  | 43126.2917 | 66 | 66
2018-01-26 07:30 | 56 | 49 |  |  | 43126.3125 | 72 | 72
2018-01-26 08:00 | 62 | 55 |  |  | 43126.3333 | 78 | 77
2018-01-26 08:30 | 67 | 61 |  |  | 43126.3542 | 82 | 82
2018-01-26 09:00 | 68 | 63 |  |  | 43126.375 | 84 | 84
2018-01-26 09:30 | 70 | 65 |  |  | 43126.3958 | 85 | 84
2018-01-26 10:00 | 68 | 63 |  |  | 43126.4167 | 84 | 84
2018-01-26 10:30 | 67 | 62 |  |  | 43126.4375 | 82 | 82
2018-01-26 11:00 | 68 | 63 |  |  | 43126.4583 | 83 | 82
2018-01-26 11:30 | 72 | 67 |  |  | 43126.4792 | 86 | 85
2018-01-26 12:00 | 80 | 67 |  |  | 43126.5 | 87 | 87
2018-01-26 12:30 | 90 | 70 |  |  | 43126.5208 | 90 | 88
2018-01-26 13:00 | 90 | 70 |  |  | 43126.5417 | 90 | 88
2018-01-26 13:30 | 87 | 66 |  |  | 43126.5625 | 90 | 88
2018-01-26 14:00 | 84 | 62 |  |  | 43126.5833 | 86 | 83
2018-01-26 14:30 | 84 | 63 |  |  | 43126.6042 | 86 | 83
2018-01-26 15:00 | 86 | 66 |  |  | 43126.625 | 89 | 86
2018-01-26 15:30 | 89 | 68 |  |  | 43126.6458 | 91 | 89
2018-01-26 16:00 | 93 | 73 |  |  | 43126.6667 | 93 | 92
2018-01-26 16:30 | 95 | 74 |  |  | 43126.6875 | 96 | 95
2018-01-26 17:00 | 97 | 76 |  |  | 43126.7083 | 98 | 97
2018-01-26 17:30 | 99 | 78 |  |  | 43126.7292 | 98 | 97
2018-01-26 18:00 | 99 | 77 |  |  | 43126.75 | 97 | 96
2018-01-26 18:30 | 97 | 74 |  |  | 43126.7708 | 95 | 94
2018-01-26 19:00 | 97 | 74 |  |  | 43126.7917 | 98 | 96
2018-01-26 19:30 | 98 | 78 |  |  | 43126.8125 | 101 | 99
2018-01-26 20:00 | 97 | 77 |  |  | 43126.8333 | 100 | 97
2018-01-26 20:30 | 97 | 77 |  |  | 43126.8542 | 100 | 97
2018-01-26 21:00 | 94 | 75 |  |  | 43126.875 | 97 | 94
2018-01-26 21:30 | 90 | 71 |  |  | 43126.8958 | 93 | 90
2018-01-26 22:00 | 90 | 69 |  |  | 43126.9167 | 91 | 88
2018-01-26 22:30 | 85 | 63 |  |  | 43126.9375 | 85 | 82
2018-01-26 23:00 | 84 | 61 |  |  | 43126.9583 | 82 | 79
2018-01-26 23:30 | 81 | 57 |  |  | 43126.9792 | 78 | 75
2018-01-27 | 81 | 56 |  |  | 43127 | 77 | 74
2018-01-27 00:30 | 81 | 56 |  |  | 43127.0208 | 77 | 73
2018-01-27 01:00 | 80 | 54 |  |  | 43127.0417 | 74 | 70
2018-01-27 01:30 | 79 | 51 |  |  | 43127.0625 | 72 | 69
2018-01-27 02:00 | 72 | 51 |  |  | 43127.0833 | 69 | 68
2018-01-27 02:30 | 63 | 49 |  |  | 43127.1042 | 65 | 65
2018-01-27 03:00 | 63 | 49 |  |  | 43127.125 | 64 | 64
2018-01-27 03:30 | 63 | 49 |  |  | 43127.1458 | 63 | 63
2018-01-27 04:00 | 62 | 47 |  |  | 43127.1667 | 63 | 63
2018-01-27 04:30 | 61 | 47 |  |  | 43127.1875 | 63 | 63
2018-01-27 05:00 | 62 | 47 |  |  | 43127.2083 | 62 | 62
2018-01-27 05:30 | 61 | 47 |  |  | 43127.2292 | 63 | 63
2018-01-27 06:00 | 60 | 46 |  |  | 43127.25 | 62 | 62
2018-01-27 06:30 | 59 | 46 |  |  | 43127.2708 | 63 | 63
2018-01-27 07:00 | 60 | 48 |  |  | 43127.2917 | 66 | 66
2018-01-27 07:30 | 64 | 54 |  |  | 43127.3125 | 72 | 72
2018-01-27 08:00 | 66 | 56 |  |  | 43127.3333 | 76 | 76
2018-01-27 08:30 | 71 | 62 |  |  | 43127.3542 | 82 | 82
2018-01-27 09:00 | 80 | 64 |  |  | 43127.375 | 84 | 83
2018-01-27 09:30 | 80 | 60 |  |  | 43127.3958 | 83 | 80
2018-01-27 10:00 | 78 | 60 |  |  | 43127.4167 | 84 | 80
2018-01-27 10:30 | 78 | 61 |  |  | 43127.4375 | 84 | 79
2018-01-27 11:00 | 79 | 63 |  |  | 43127.4583 | 84 | 80
2018-01-27 11:30 | 80 | 65 |  |  | 43127.4792 | 85 | 81
2018-01-27 12:00 | 79 | 63 |  |  | 43127.5 | 85 | 81
2018-01-27 12:30 | 79 | 64 |  |  | 43127.5208 | 85 | 81
2018-01-27 13:00 | 79 | 64 |  |  | 43127.5417 | 86 | 82
2018-01-27 13:30 | 80 | 65 |  |  | 43127.5625 | 87 | 83
2018-01-27 14:00 | 81 | 67 |  |  | 43127.5833 | 87 | 84
2018-01-27 14:30 | 83 | 70 |  |  | 43127.6042 | 90 | 87
2018-01-27 15:00 | 84 | 72 |  |  | 43127.625 | 91 | 88
2018-01-27 15:30 | 85 | 73 |  |  | 43127.6458 | 93 | 90
2018-01-27 16:00 | 86 | 75 |  |  | 43127.6667 | 94 | 92
2018-01-27 16:30 | 94 | 76 |  |  | 43127.6875 | 95 | 95
2018-01-27 17:00 | 95 | 78 |  |  | 43127.7083 | 96 | 96
2018-01-27 17:30 | 94 | 77 |  |  | 43127.7292 | 99 | 96
2018-01-27 18:00 | 88 | 76 |  |  | 43127.75 | 98 | 95
2018-01-27 18:30 | 85 | 76 |  |  | 43127.7708 | 98 | 96
2018-01-27 19:00 | 88 | 77 |  |  | 43127.7917 | 100 | 97
2018-01-27 19:30 | 88 | 78 |  |  | 43127.8125 | 101 | 98
2018-01-27 20:00 | 85 | 79 |  |  | 43127.8333 | 100 | 100
2018-01-27 20:30 | 84 | 79 |  |  | 43127.8542 | 99 | 99
2018-01-27 21:00 | 81 | 78 |  |  | 43127.875 | 96 | 96
2018-01-27 21:30 | 81 | 78 |  |  | 43127.8958 | 96 | 95
2018-01-27 22:00 | 79 | 77 |  |  | 43127.9167 | 95 | 94
2018-01-27 22:30 | 73 | 69 |  |  | 43127.9375 | 88 | 87
2018-01-27 23:00 | 70 | 67 |  |  | 43127.9583 | 84 | 83
2018-01-27 23:30 | 69 | 66 |  |  | 43127.9792 | 83 | 82
2018-01-28 | 66 | 60 |  |  | 43128 | 78 | 77
2018-01-28 00:30 | 61 | 54 |  |  | 43128.0208 | 71 | 70
2018-01-28 01:00 | 59 | 52 |  |  | 43128.0417 | 67 | 66
2018-01-28 01:30 | 57 | 50 |  |  | 43128.0625 | 66 | 65
2018-01-28 02:00 | 58 | 50 |  |  | 43128.0833 | 65 | 63
2018-01-28 02:30 | 58 | 49 |  |  | 43128.1042 | 64 | 62
2018-01-28 03:00 | 56 | 47 |  |  | 43128.125 | 64 | 62
2018-01-28 03:30 | 56 | 47 |  |  | 43128.1458 | 63 | 61
2018-01-28 04:00 | 56 | 46 |  |  | 43128.1667 | 62 | 60
2018-01-28 04:30 | 55 | 44 |  |  | 43128.1875 | 62 | 59
2018-01-28 05:00 | 54 | 44 |  |  | 43128.2083 | 62 | 59
2018-01-28 05:30 | 54 | 44 |  |  | 43128.2292 | 61 | 59
2018-01-28 06:00 | 53 | 42 |  |  | 43128.25 | 60 | 57
2018-01-28 06:30 | 52 | 41 |  |  | 43128.2708 | 58 | 56
2018-01-28 07:00 | 52 | 42 |  |  | 43128.2917 | 59 | 57
2018-01-28 07:30 | 53 | 46 |  |  | 43128.3125 | 63 | 62
2018-01-28 08:00 | 56 | 49 |  |  | 43128.3333 | 68 | 67
2018-01-28 08:30 | 57 | 52 |  |  | 43128.3542 | 68 | 67
2018-01-28 09:00 | 60 | 55 |  |  | 43128.375 | 72 | 72
2018-01-28 09:30 | 62 | 58 |  |  | 43128.3958 | 72 | 71
2018-01-28 10:00 | 61 | 58 |  |  | 43128.4167 | 77 | 76
2018-01-28 10:30 | 62 | 59 |  |  | 43128.4375 | 78 | 77
2018-01-28 11:00 | 61 | 58 |  |  | 43128.4583 | 74 | 74
2018-01-28 11:30 | 58 | 54 |  |  | 43128.4792 | 74 | 73
2018-01-28 12:00 | 59 | 55 |  |  | 43128.5 | 71 | 70
2018-01-28 12:30 | 59 | 56 |  |  | 43128.5208 | 69 | 68
2018-01-28 13:00 | 58 | 56 |  |  | 43128.5417 | 69 | 68
2018-01-28 13:30 | 59 | 56 |  |  | 43128.5625 | 70 | 70
2018-01-28 14:00 | 61 | 58 |  |  | 43128.5833 | 72 | 72
2018-01-28 14:30 | 63 | 60 |  |  | 43128.6042 | 80 | 80
2018-01-28 15:00 | 65 | 63 |  |  | 43128.625 | 78 | 77
2018-01-28 15:30 | 69 | 67 |  |  | 43128.6458 | 84 | 83
2018-01-28 16:00 | 70 | 68 |  |  | 43128.6667 | 83 | 83
2018-01-28 16:30 | 69 | 67 |  |  | 43128.6875 | 81 | 80
2018-01-28 17:00 | 69 | 67 |  |  | 43128.7083 | 82 | 81
2018-01-28 17:30 | 71 | 69 |  |  | 43128.7292 | 84 | 84
2018-01-28 18:00 | 74 | 72 |  |  | 43128.75 | 87 | 87
2018-01-28 18:30 | 72 | 69 |  |  | 43128.7708 | 86 | 85
2018-01-28 19:00 | 75 | 73 |  |  | 43128.7917 | 91 | 90
2018-01-28 19:30 | 79 | 77 |  |  | 43128.8125 | 95 | 94
2018-01-28 20:00 | 79 | 75 |  |  | 43128.8333 | 95 | 92
2018-01-28 20:30 | 79 | 74 |  |  | 43128.8542 | 94 | 92
2018-01-28 21:00 | 77 | 73 |  |  | 43128.875 | 92 | 89
2018-01-28 21:30 | 73 | 69 |  |  | 43128.8958 | 87 | 86
2018-01-28 22:00 | 69 | 65 |  |  | 43128.9167 | 82 | 82
2018-01-28 22:30 | 66 | 62 |  |  | 43128.9375 | 79 | 78
2018-01-28 23:00 | 68 | 63 |  |  | 43128.9583 | 80 | 79
2018-01-28 23:30 | 65 | 60 |  |  | 43128.9792 | 77 | 76
2018-01-29 | 61 | 55 |  |  | 43129 | 71 | 70
2018-01-29 00:30 | 58 | 49 |  |  | 43129.0208 | 66 | 64
2018-01-29 01:00 | 56 | 46 |  |  | 43129.0417 | 63 | 60
2018-01-29 01:30 | 55 | 44 |  |  | 43129.0625 | 60 | 57
2018-01-29 02:00 | 54 | 44 |  |  | 43129.0833 | 59 | 56
2018-01-29 02:30 | 54 | 44 |  |  | 43129.1042 | 59 | 56
2018-01-29 03:00 | 54 | 43 |  |  | 43129.125 | 59 | 56
2018-01-29 03:30 | 55 | 44 |  |  | 43129.1458 | 59 | 56
2018-01-29 04:00 | 54 | 44 |  |  | 43129.1667 | 60 | 57
2018-01-29 04:30 | 54 | 44 |  |  | 43129.1875 | 60 | 57
2018-01-29 05:00 | 55 | 46 |  |  | 43129.2083 | 62 | 59
2018-01-29 05:30 | 58 | 50 |  |  | 43129.2292 | 66 | 64
2018-01-29 06:00 | 61 | 55 |  |  | 43129.25 | 71 | 70
2018-01-29 06:30 | 65 | 63 |  |  | 43129.2708 | 82 | 82
2018-01-29 07:00 | 68 | 66 |  |  | 43129.2917 | 89 | 89
2018-01-29 07:30 | 79 | 73 |  |  | 43129.3125 | 98 | 97
2018-01-29 08:00 | 82 | 74 |  |  | 43129.3333 | 102 | 102
2018-01-29 08:30 | 83 | 76 |  |  | 43129.3542 | 101 | 101
2018-01-29 09:00 | 82 | 75 |  |  | 43129.375 | 102 | 101
2018-01-29 09:30 | 85 | 78 |  |  | 43129.3958 | 107 | 107
2018-01-29 10:00 | 91 | 85 |  |  | 43129.4167 | 113 | 113
2018-01-29 10:30 | 97 | 90 |  |  | 43129.4375 | 119 | 119
2018-01-29 11:00 | 105 | 87 |  |  | 43129.4583 | 122 | 122
2018-01-29 11:30 | 105 | 84 |  |  | 43129.4792 | 119 | 119
2018-01-29 12:00 | 101 | 78 |  |  | 43129.5 | 109 | 109
2018-01-29 12:30 | 100 | 78 |  |  | 43129.5208 | 106 | 106
2018-01-29 13:00 | 102 | 82 |  |  | 43129.5417 | 109 | 109
2018-01-29 13:30 | 104 | 84 |  |  | 43129.5625 | 112 | 112
2018-01-29 14:00 | 108 | 89 |  |  | 43129.5833 | 116 | 116
2018-01-29 14:30 | 110 | 91 |  |  | 43129.6042 | 118 | 118
2018-01-29 15:00 | 111 | 90 |  |  | 43129.625 | 118 | 118
2018-01-29 15:30 | 110 | 88 |  |  | 43129.6458 | 114 | 114
2018-01-29 16:00 | 116 | 95 |  |  | 43129.6667 | 119 | 119
2018-01-29 16:30 | 119 | 98 |  |  | 43129.6875 | 122 | 122
2018-01-29 17:00 | 121 | 100 |  |  | 43129.7083 | 123 | 123
2018-01-29 17:30 | 122 | 100 |  |  | 43129.7292 | 122 | 122
2018-01-29 18:00 | 119 | 96 |  |  | 43129.75 | 116 | 116
2018-01-29 18:30 | 108 | 90 |  |  | 43129.7708 | 110 | 109
2018-01-29 19:00 | 111 | 93 |  |  | 43129.7917 | 114 | 113
2018-01-29 19:30 | 111 | 93 |  |  | 43129.8125 | 113 | 112
2018-01-29 20:00 | 109 | 93 |  |  | 43129.8333 | 113 | 112
2018-01-29 20:30 | 106 | 93 |  |  | 43129.8542 | 112 | 110
2018-01-29 21:00 | 95 | 91 |  |  | 43129.875 | 108 | 104
2018-01-29 21:30 | 89 | 84 |  |  | 43129.8958 | 101 | 98
2018-01-29 22:00 | 86 | 81 |  |  | 43129.9167 | 100 | 97
2018-01-29 22:30 | 82 | 75 |  |  | 43129.9375 | 95 | 91
2018-01-29 23:00 | 80 | 73 |  |  | 43129.9583 | 92 | 87
2018-01-29 23:30 | 76 | 68 |  |  | 43129.9792 | 87 | 82
2018-01-30 | 72 | 63 |  |  | 43130 | 81 | 76
2018-01-30 00:30 | 69 | 57 |  |  | 43130.0208 | 75 | 70
2018-01-30 01:00 | 66 | 53 |  |  | 43130.0417 | 71 | 65
2018-01-30 01:30 | 64 | 50 |  |  | 43130.0625 | 69 | 62
2018-01-30 02:00 | 64 | 50 |  |  | 43130.0833 | 70 | 62
2018-01-30 02:30 | 64 | 49 |  |  | 43130.1042 | 69 | 61
2018-01-30 03:00 | 64 | 49 |  |  | 43130.125 | 69 | 61
2018-01-30 03:30 | 64 | 49 |  |  | 43130.1458 | 69 | 60
2018-01-30 04:00 | 62 | 47 |  |  | 43130.1667 | 67 | 58
2018-01-30 04:30 | 61 | 46 |  |  | 43130.1875 | 67 | 58
2018-01-30 05:00 | 62 | 48 |  |  | 43130.2083 | 69 | 62
2018-01-30 05:30 | 64 | 51 |  |  | 43130.2292 | 73 | 66
2018-01-30 06:00 | 65 | 54 |  |  | 43130.25 | 77 | 70
2018-01-30 06:30 | 67 | 60 |  |  | 43130.2708 | 84 | 81
2018-01-30 07:00 | 70 | 66 |  |  | 43130.2917 | 90 | 89
2018-01-30 07:30 | 75 | 70 |  |  | 43130.3125 | 99 | 97
2018-01-30 08:00 | 77 | 73 |  |  | 43130.3333 | 102 | 101
2018-01-30 08:30 | 77 | 73 |  |  | 43130.3542 | 105 | 104
2018-01-30 09:00 | 87 | 82 |  |  | 43130.375 | 115 | 115
2018-01-30 09:30 | 91 | 85 |  |  | 43130.3958 | 119 | 119
2018-01-30 10:00 | 92 | 85 |  |  | 43130.4167 | 118 | 118
2018-01-30 10:30 | 95 | 88 |  |  | 43130.4375 | 118 | 118
2018-01-30 11:00 | 91 | 84 |  |  | 43130.4583 | 115 | 115
2018-01-30 11:30 | 87 | 84 |  |  | 43130.4792 | 113 | 113
2018-01-30 12:00 | 90 | 88 |  |  | 43130.5 | 117 | 117
2018-01-30 12:30 | 91 | 90 |  |  | 43130.5208 | 119 | 119
2018-01-30 13:00 | 94 | 93 |  |  | 43130.5417 | 122 | 122
2018-01-30 13:30 | 94 | 92 |  |  | 43130.5625 | 124 | 124
2018-01-30 14:00 | 96 | 95 |  |  | 43130.5833 | 124 | 124
2018-01-30 14:30 | 94 | 93 |  |  | 43130.6042 | 122 | 122
2018-01-30 15:00 | 94 | 92 |  |  | 43130.625 | 123 | 123
2018-01-30 15:30 | 95 | 94 |  |  | 43130.6458 | 121 | 121
2018-01-30 16:00 | 101 | 95 |  |  | 43130.6667 | 131 | 131
2018-01-30 16:30 | 104 | 97 |  |  | 43130.6875 | 131 | 131
2018-01-30 17:00 | 107 | 100 |  |  | 43130.7083 | 128 | 127
2018-01-30 17:30 | 103 | 98 |  |  | 43130.7292 | 123 | 123
2018-01-30 18:00 | 102 | 98 |  |  | 43130.75 | 121 | 120
2018-01-30 18:30 | 100 | 95 |  |  | 43130.7708 | 115 | 115
2018-01-30 19:00 | 99 | 95 |  |  | 43130.7917 | 116 | 116
2018-01-30 19:30 | 99 | 95 |  |  | 43130.8125 | 116 | 116
2018-01-30 20:00 | 98 | 94 |  |  | 43130.8333 | 116 | 115
2018-01-30 20:30 | 96 | 93 |  |  | 43130.8542 | 114 | 113
2018-01-30 21:00 | 92 | 89 |  |  | 43130.875 | 112 | 109
2018-01-30 21:30 | 88 | 84 |  |  | 43130.8958 | 106 | 103
2018-01-30 22:00 | 88 | 83 |  |  | 43130.9167 | 105 | 102
2018-01-30 22:30 | 84 | 78 |  |  | 43130.9375 | 99 | 97
2018-01-30 23:00 | 76 | 75 |  |  | 43130.9583 | 92 | 92
2018-01-30 23:30 | 69 | 69 |  |  | 43130.9792 | 86 | 86
2018-01-31 | 64 | 64 |  |  | 43131 | 81 | 81
2018-01-31 00:30 | 61 | 61 |  |  | 43131.0208 | 77 | 77
2018-01-31 01:00 | 59 | 58 |  |  | 43131.0417 | 74 | 74
2018-01-31 01:30 | 57 | 57 |  |  | 43131.0625 | 71 | 71
2018-01-31 02:00 | 56 | 55 |  |  | 43131.0833 | 70 | 70
2018-01-31 02:30 | 52 | 51 |  |  | 43131.1042 | 66 | 66
2018-01-31 03:00 | 51 | 50 |  |  | 43131.125 | 64 | 64
2018-01-31 03:30 | 51 | 50 |  |  | 43131.1458 | 64 | 64
2018-01-31 04:00 | 52 | 51 |  |  | 43131.1667 | 65 | 65
2018-01-31 04:30 | 53 | 52 |  |  | 43131.1875 | 67 | 67
2018-01-31 05:00 | 56 | 55 |  |  | 43131.2083 | 69 | 69
2018-01-31 05:30 | 58 | 57 |  |  | 43131.2292 | 73 | 73
2018-01-31 06:00 | 61 | 61 |  |  | 43131.25 | 78 | 78
2018-01-31 06:30 | 63 | 63 |  |  | 43131.2708 | 84 | 84
2018-01-31 07:00 | 67 | 67 |  |  | 43131.2917 | 92 | 92
2018-01-31 07:30 | 74 | 74 |  |  | 43131.3125 | 101 | 100
2018-01-31 08:00 | 81 | 81 |  |  | 43131.3333 | 109 | 108
2018-01-31 08:30 | 82 | 82 |  |  | 43131.3542 | 111 | 110
2018-01-31 09:00 | 85 | 84 |  |  | 43131.375 | 114 | 113
2018-01-31 09:30 | 84 | 84 |  |  | 43131.3958 | 115 | 114
2018-01-31 10:00 | 85 | 85 |  |  | 43131.4167 | 116 | 115
2018-01-31 10:30 | 89 | 89 |  |  | 43131.4375 | 119 | 119
2018-01-31 11:00 | 92 | 92 |  |  | 43131.4583 | 122 | 122
2018-01-31 11:30 | 96 | 96 |  |  | 43131.4792 | 125 | 125
2018-01-31 12:00 | 98 | 97 |  |  | 43131.5 | 130 | 128
2018-01-31 12:30 | 103 | 102 |  |  | 43131.5208 | 135 | 132
2018-01-31 13:00 | 105 | 104 |  |  | 43131.5417 | 139 | 136
2018-01-31 13:30 | 110 | 109 |  |  | 43131.5625 | 141 | 138
2018-01-31 14:00 | 111 | 110 |  |  | 43131.5833 | 144 | 141
2018-01-31 14:30 | 114 | 114 |  |  | 43131.6042 | 147 | 145
2018-01-31 15:00 | 112 | 112 |  |  | 43131.625 | 146 | 144
2018-01-31 15:30 | 113 | 113 |  |  | 43131.6458 | 145 | 142
2018-01-31 16:00 | 120 | 119 |  |  | 43131.6667 | 156 | 150
2018-01-31 16:30 | 119 | 118 |  |  | 43131.6875 | 159 | 151
2018-01-31 17:00 | 110 | 109 |  |  | 43131.7083 | 154 | 146
2018-01-31 17:30 | 105 | 105 |  |  | 43131.7292 | 144 | 138
2018-01-31 18:00 | 106 | 105 |  |  | 43131.75 | 140 | 136
2018-01-31 18:30 | 103 | 103 |  |  | 43131.7708 | 134 | 132
2018-01-31 19:00 | 102 | 102 |  |  | 43131.7917 | 134 | 132
2018-01-31 19:30 | 104 | 103 |  |  | 43131.8125 | 134 | 131
2018-01-31 20:00 | 102 | 100 |  |  | 43131.8333 | 130 | 126
2018-01-31 20:30 | 107 | 102 |  |  | 43131.8542 | 129 | 124
2018-01-31 21:00 | 103 | 99 |  |  | 43131.875 | 121 | 118
2018-01-31 21:30 | 96 | 94 |  |  | 43131.8958 | 112 | 112
2018-01-31 22:00 | 93 | 90 |  |  | 43131.9167 | 108 | 107
2018-01-31 22:30 | 85 | 84 |  |  | 43131.9375 | 102 | 102
2018-01-31 23:00 | 80 | 79 |  |  | 43131.9583 | 96 | 96
2018-01-31 23:30 | 75 | 74 |  |  | 43131.9792 | 91 | 91
2018-02-01 | 69 | 69 |  |  | 43132 | 85 | 85
2018-02-01 00:30 | 66 | 65 |  |  | 43132.0208 | 82 | 81
2018-02-01 01:00 | 63 | 62 |  |  | 43132.0417 | 78 | 78
2018-02-01 01:30 | 61 | 60 |  |  | 43132.0625 | 76 | 76
2018-02-01 02:00 | 60 | 59 |  |  | 43132.0833 | 75 | 75
2018-02-01 02:30 | 61 | 60 |  |  | 43132.1042 | 75 | 75
2018-02-01 03:00 | 58 | 58 |  |  | 43132.125 | 73 | 73
2018-02-01 03:30 | 58 | 57 |  |  | 43132.1458 | 70 | 70
2018-02-01 04:00 | 57 | 56 |  |  | 43132.1667 | 71 | 71
2018-02-01 04:30 | 57 | 57 |  |  | 43132.1875 | 71 | 71
2018-02-01 05:00 | 58 | 58 |  |  | 43132.2083 | 73 | 73
2018-02-01 05:30 | 60 | 60 |  |  | 43132.2292 | 75 | 75
2018-02-01 06:00 | 62 | 62 |  |  | 43132.25 | 80 | 80
2018-02-01 06:30 | 67 | 67 |  |  | 43132.2708 | 87 | 87
2018-02-01 07:00 | 71 | 71 |  |  | 43132.2917 | 94 | 94
2018-02-01 07:30 | 78 | 77 |  |  | 43132.3125 | 103 | 102
2018-02-01 08:00 | 84 | 83 |  |  | 43132.3333 | 111 | 110
2018-02-01 08:30 | 86 | 85 |  |  | 43132.3542 | 113 | 112
2018-02-01 09:00 | 88 | 87 |  |  | 43132.375 | 115 | 113
2018-02-01 09:30 | 90 | 89 |  |  | 43132.3958 | 117 | 115
2018-02-01 10:00 | 87 | 86 |  |  | 43132.4167 | 114 | 113
2018-02-01 10:30 | 82 | 81 |  |  | 43132.4375 | 110 | 109
2018-02-01 11:00 | 83 | 82 |  |  | 43132.4583 | 109 | 109
2018-02-01 11:30 | 88 | 88 |  |  | 43132.4792 | 117 | 116
2018-02-01 12:00 | 89 | 89 |  |  | 43132.5 | 117 | 116
2018-02-01 12:30 | 91 | 90 |  |  | 43132.5208 | 116 | 115
2018-02-01 13:00 | 87 | 86 |  |  | 43132.5417 | 113 | 112
2018-02-01 13:30 | 83 | 82 |  |  | 43132.5625 | 110 | 109
2018-02-01 14:00 | 87 | 86 |  |  | 43132.5833 | 115 | 114
2018-02-01 14:30 | 87 | 86 |  |  | 43132.6042 | 114 | 113
2018-02-01 15:00 | 89 | 88 |  |  | 43132.625 | 117 | 115
2018-02-01 15:30 | 87 | 86 |  |  | 43132.6458 | 114 | 113
2018-02-01 16:00 | 91 | 90 |  |  | 43132.6667 | 117 | 115
2018-02-01 16:30 | 91 | 89 |  |  | 43132.6875 | 116 | 115
2018-02-01 17:00 | 90 | 89 |  |  | 43132.7083 | 114 | 112
2018-02-01 17:30 | 86 | 85 |  |  | 43132.7292 | 109 | 107
2018-02-01 18:00 | 85 | 84 |  |  | 43132.75 | 107 | 106
2018-02-01 18:30 | 85 | 84 |  |  | 43132.7708 | 105 | 102
2018-02-01 19:00 | 87 | 86 |  |  | 43132.7917 | 108 | 106
2018-02-01 19:30 | 85 | 84 |  |  | 43132.8125 | 104 | 102
2018-02-01 20:00 | 81 | 81 |  |  | 43132.8333 | 101 | 99
2018-02-01 20:30 | 80 | 79 |  |  | 43132.8542 | 98 | 98
2018-02-01 21:00 | 80 | 80 |  |  | 43132.875 | 97 | 96
2018-02-01 21:30 | 78 | 77 |  |  | 43132.8958 | 95 | 94
2018-02-01 22:00 | 74 | 72 |  |  | 43132.9167 | 90 | 89
2018-02-01 22:30 | 68 | 66 |  |  | 43132.9375 | 84 | 83
2018-02-01 23:00 | 68 | 66 |  |  | 43132.9583 | 83 | 81
2018-02-01 23:30 | 64 | 61 |  |  | 43132.9792 | 78 | 77
2018-02-02 | 58 | 56 |  |  | 43133 | 73 | 72
2018-02-02 00:30 | 52 | 50 |  |  | 43133.0208 | 66 | 65
2018-02-02 01:00 | 49 | 45 |  |  | 43133.0417 | 60 | 59
2018-02-02 01:30 | 49 | 45 |  |  | 43133.0625 | 60 | 58
2018-02-02 02:00 | 52 | 48 |  |  | 43133.0833 | 63 | 62
2018-02-02 02:30 | 53 | 48 |  |  | 43133.1042 | 63 | 61
2018-02-02 03:00 | 50 | 46 |  |  | 43133.125 | 59 | 57
2018-02-02 03:30 | 50 | 46 |  |  | 43133.1458 | 59 | 58
2018-02-02 04:00 | 50 | 46 |  |  | 43133.1667 | 59 | 57
2018-02-02 04:30 | 50 | 47 |  |  | 43133.1875 | 60 | 58
2018-02-02 05:00 | 52 | 48 |  |  | 43133.2083 | 61 | 59
2018-02-02 05:30 | 54 | 52 |  |  | 43133.2292 | 65 | 64
2018-02-02 06:00 | 55 | 53 |  |  | 43133.25 | 69 | 68
2018-02-02 06:30 | 59 | 59 |  |  | 43133.2708 | 78 | 78
2018-02-02 07:00 | 64 | 64 |  |  | 43133.2917 | 86 | 86
2018-02-02 07:30 | 73 | 73 |  |  | 43133.3125 | 96 | 95
2018-02-02 08:00 | 76 | 75 |  |  | 43133.3333 | 99 | 99
2018-02-02 08:30 | 76 | 75 |  |  | 43133.3542 | 100 | 99
2018-02-02 09:00 | 76 | 75 |  |  | 43133.375 | 99 | 99
2018-02-02 09:30 | 76 | 75 |  |  | 43133.3958 | 99 | 99
2018-02-02 10:00 | 78 | 77 |  |  | 43133.4167 | 101 | 101
2018-02-02 10:30 | 78 | 77 |  |  | 43133.4375 | 101 | 101
2018-02-02 11:00 | 79 | 78 |  |  | 43133.4583 | 102 | 102
2018-02-02 11:30 | 78 | 78 |  |  | 43133.4792 | 102 | 102
2018-02-02 12:00 | 74 | 73 |  |  | 43133.5 | 97 | 97
2018-02-02 12:30 | 78 | 77 |  |  | 43133.5208 | 102 | 101
2018-02-02 13:00 | 79 | 78 |  |  | 43133.5417 | 101 | 101
2018-02-02 13:30 | 77 | 76 |  |  | 43133.5625 | 99 | 98
2018-02-02 14:00 | 76 | 75 |  |  | 43133.5833 | 98 | 97
2018-02-02 14:30 | 80 | 79 |  |  | 43133.6042 | 101 | 100
2018-02-02 15:00 | 81 | 80 |  |  | 43133.625 | 102 | 102
2018-02-02 15:30 | 80 | 79 |  |  | 43133.6458 | 101 | 100
2018-02-02 16:00 | 79 | 78 |  |  | 43133.6667 | 100 | 99
2018-02-02 16:30 | 81 | 79 |  |  | 43133.6875 | 101 | 100
2018-02-02 17:00 | 81 | 79 |  |  | 43133.7083 | 100 | 98
2018-02-02 17:30 | 80 | 79 |  |  | 43133.7292 | 97 | 96
2018-02-02 18:00 | 79 | 77 |  |  | 43133.75 | 95 | 94
2018-02-02 18:30 | 78 | 75 |  |  | 43133.7708 | 93 | 91
2018-02-02 19:00 | 79 | 78 |  |  | 43133.7917 | 95 | 94
2018-02-02 19:30 | 77 | 76 |  |  | 43133.8125 | 92 | 92
2018-02-02 20:00 | 77 | 75 |  |  | 43133.8333 | 91 | 90
2018-02-02 20:30 | 75 | 74 |  |  | 43133.8542 | 90 | 89
2018-02-02 21:00 | 74 | 73 |  |  | 43133.875 | 88 | 87
2018-02-02 21:30 | 68 | 67 |  |  | 43133.8958 | 80 | 80
2018-02-02 22:00 | 66 | 65 |  |  | 43133.9167 | 79 | 79
2018-02-02 22:30 | 63 | 61 |  |  | 43133.9375 | 75 | 74
2018-02-02 23:00 | 62 | 60 |  |  | 43133.9583 | 72 | 71
2018-02-02 23:30 | 60 | 57 |  |  | 43133.9792 | 71 | 70
2018-02-03 | 55 | 52 |  |  | 43134 | 66 | 64
2018-02-03 00:30 | 53 | 49 |  |  | 43134.0208 | 61 | 60
2018-02-03 01:00 | 49 | 46 |  |  | 43134.0417 | 57 | 56
2018-02-03 01:30 | 49 | 45 |  |  | 43134.0625 | 57 | 55
2018-02-03 02:00 | 49 | 44 |  |  | 43134.0833 | 56 | 54
2018-02-03 02:30 | 48 | 44 |  |  | 43134.1042 | 55 | 53
2018-02-03 03:00 | 48 | 43 |  |  | 43134.125 | 55 | 53
2018-02-03 03:30 | 48 | 44 |  |  | 43134.1458 | 55 | 53
2018-02-03 04:00 | 46 | 42 |  |  | 43134.1667 | 55 | 52
2018-02-03 04:30 | 45 | 40 |  |  | 43134.1875 | 54 | 51
2018-02-03 05:00 | 45 | 41 |  |  | 43134.2083 | 53 | 51
2018-02-03 05:30 | 46 | 43 |  |  | 43134.2292 | 55 | 53
2018-02-03 06:00 | 47 | 43 |  |  | 43134.25 | 56 | 55
2018-02-03 06:30 | 50 | 46 |  |  | 43134.2708 | 60 | 59
2018-02-03 07:00 | 52 | 48 |  |  | 43134.2917 | 63 | 62
2018-02-03 07:30 | 52 | 50 |  |  | 43134.3125 | 65 | 64
2018-02-03 08:00 | 53 | 51 |  |  | 43134.3333 | 66 | 66
2018-02-03 08:30 | 57 | 55 |  |  | 43134.3542 | 70 | 70
2018-02-03 09:00 | 58 | 58 |  |  | 43134.375 | 72 | 72
2018-02-03 09:30 | 59 | 58 |  |  | 43134.3958 | 73 | 73
2018-02-03 10:00 | 60 | 59 |  |  | 43134.4167 | 73 | 72
2018-02-03 10:30 | 59 | 58 |  |  | 43134.4375 | 72 | 72
2018-02-03 11:00 | 59 | 58 |  |  | 43134.4583 | 72 | 71
2018-02-03 11:30 | 58 | 57 |  |  | 43134.4792 | 72 | 71
2018-02-03 12:00 | 61 | 60 |  |  | 43134.5 | 76 | 75
2018-02-03 12:30 | 61 | 60 |  |  | 43134.5208 | 74 | 74
2018-02-03 13:00 | 61 | 59 |  |  | 43134.5417 | 74 | 74
2018-02-03 13:30 | 63 | 61 |  |  | 43134.5625 | 75 | 75
2018-02-03 14:00 | 61 | 59 |  |  | 43134.5833 | 74 | 73
2018-02-03 14:30 | 62 | 61 |  |  | 43134.6042 | 76 | 75
2018-02-03 15:00 | 63 | 61 |  |  | 43134.625 | 77 | 76
2018-02-03 15:30 | 62 | 60 |  |  | 43134.6458 | 76 | 75
2018-02-03 16:00 | 62 | 60 |  |  | 43134.6667 | 77 | 76
2018-02-03 16:30 | 63 | 62 |  |  | 43134.6875 | 77 | 77
2018-02-03 17:00 | 64 | 62 |  |  | 43134.7083 | 78 | 78
2018-02-03 17:30 | 62 | 60 |  |  | 43134.7292 | 76 | 76
2018-02-03 18:00 | 61 | 59 |  |  | 43134.75 | 75 | 75
2018-02-03 18:30 | 61 | 59 |  |  | 43134.7708 | 76 | 75
2018-02-03 19:00 | 63 | 61 |  |  | 43134.7917 | 79 | 78
2018-02-03 19:30 | 64 | 63 |  |  | 43134.8125 | 78 | 78
2018-02-03 20:00 | 63 | 61 |  |  | 43134.8333 | 78 | 77
2018-02-03 20:30 | 63 | 61 |  |  | 43134.8542 | 77 | 76
2018-02-03 21:00 | 61 | 59 |  |  | 43134.875 | 74 | 73
2018-02-03 21:30 | 58 | 56 |  |  | 43134.8958 | 71 | 70
2018-02-03 22:00 | 55 | 53 |  |  | 43134.9167 | 69 | 68
2018-02-03 22:30 | 55 | 53 |  |  | 43134.9375 | 69 | 68
2018-02-03 23:00 | 59 | 57 |  |  | 43134.9583 | 70 | 69
2018-02-03 23:30 | 57 | 53 |  |  | 43134.9792 | 69 | 67
2018-02-04 | 55 | 51 |  |  | 43135 | 66 | 64
2018-02-04 00:30 | 50 | 46 |  |  | 43135.0208 | 59 | 57
2018-02-04 01:00 | 47 | 42 |  |  | 43135.0417 | 55 | 53
2018-02-04 01:30 | 46 | 41 |  |  | 43135.0625 | 53 | 51
2018-02-04 02:00 | 44 | 39 |  |  | 43135.0833 | 52 | 50
2018-02-04 02:30 | 44 | 38 |  |  | 43135.1042 | 51 | 48
2018-02-04 03:00 | 44 | 38 |  |  | 43135.125 | 51 | 48
2018-02-04 03:30 | 43 | 37 |  |  | 43135.1458 | 50 | 47
2018-02-04 04:00 | 40 | 36 |  |  | 43135.1667 | 46 | 46
2018-02-04 04:30 | 40 | 37 |  |  | 43135.1875 | 47 | 46
2018-02-04 05:00 | 39 | 36 |  |  | 43135.2083 | 47 | 46
2018-02-04 05:30 | 39 | 36 |  |  | 43135.2292 | 46 | 46
2018-02-04 06:00 | 40 | 36 |  |  | 43135.25 | 47 | 46
2018-02-04 06:30 | 41 | 37 |  |  | 43135.2708 | 50 | 49
2018-02-04 07:00 | 43 | 40 |  |  | 43135.2917 | 52 | 51
2018-02-04 07:30 | 42 | 39 |  |  | 43135.3125 | 52 | 52
2018-02-04 08:00 | 44 | 42 |  |  | 43135.3333 | 57 | 57
2018-02-04 08:30 | 46 | 44 |  |  | 43135.3542 | 59 | 59
2018-02-04 09:00 | 48 | 47 |  |  | 43135.375 | 63 | 63
2018-02-04 09:30 | 49 | 48 |  |  | 43135.3958 | 64 | 64
2018-02-04 10:00 | 50 | 49 |  |  | 43135.4167 | 64 | 64
2018-02-04 10:30 | 48 | 47 |  |  | 43135.4375 | 63 | 62
2018-02-04 11:00 | 48 | 48 |  |  | 43135.4583 | 61 | 61
2018-02-04 11:30 | 48 | 47 |  |  | 43135.4792 | 62 | 62
2018-02-04 12:00 | 49 | 48 |  |  | 43135.5 | 62 | 62
2018-02-04 12:30 | 49 | 49 |  |  | 43135.5208 | 60 | 60
2018-02-04 13:00 | 47 | 46 |  |  | 43135.5417 | 60 | 60
2018-02-04 13:30 | 48 | 48 |  |  | 43135.5625 | 62 | 62
2018-02-04 14:00 | 51 | 50 |  |  | 43135.5833 | 63 | 62
2018-02-04 14:30 | 47 | 47 |  |  | 43135.6042 | 61 | 61
2018-02-04 15:00 | 46 | 45 |  |  | 43135.625 | 58 | 57
2018-02-04 15:30 | 45 | 44 |  |  | 43135.6458 | 59 | 58
2018-02-04 16:00 | 48 | 47 |  |  | 43135.6667 | 61 | 61
2018-02-04 16:30 | 49 | 48 |  |  | 43135.6875 | 62 | 62
2018-02-04 17:00 | 50 | 49 |  |  | 43135.7083 | 64 | 64
2018-02-04 17:30 | 52 | 51 |  |  | 43135.7292 | 65 | 65
2018-02-04 18:00 | 53 | 53 |  |  | 43135.75 | 67 | 67
2018-02-04 18:30 | 56 | 55 |  |  | 43135.7708 | 69 | 69
2018-02-04 19:00 | 60 | 59 |  |  | 43135.7917 | 74 | 74
2018-02-04 19:30 | 63 | 62 |  |  | 43135.8125 | 77 | 77
2018-02-04 20:00 | 59 | 59 |  |  | 43135.8333 | 75 | 75
2018-02-04 20:30 | 59 | 59 |  |  | 43135.8542 | 74 | 74
2018-02-04 21:00 | 56 | 56 |  |  | 43135.875 | 71 | 71
2018-02-04 21:30 | 55 | 54 |  |  | 43135.8958 | 68 | 68
2018-02-04 22:00 | 54 | 53 |  |  | 43135.9167 | 69 | 68
2018-02-04 22:30 | 55 | 54 |  |  | 43135.9375 | 69 | 69
2018-02-04 23:00 | 57 | 56 |  |  | 43135.9583 | 69 | 69
2018-02-04 23:30 | 55 | 53 |  |  | 43135.9792 | 68 | 68
2018-02-05 | 52 | 50 |  |  | 43136 | 64 | 64
2018-02-05 00:30 | 47 | 44 |  |  | 43136.0208 | 57 | 57
2018-02-05 01:00 | 44 | 41 |  |  | 43136.0417 | 53 | 53
2018-02-05 01:30 | 42 | 39 |  |  | 43136.0625 | 50 | 50
2018-02-05 02:00 | 41 | 38 |  |  | 43136.0833 | 50 | 49
2018-02-05 02:30 | 43 | 40 |  |  | 43136.1042 | 51 | 50
2018-02-05 03:00 | 41 | 38 |  |  | 43136.125 | 50 | 50
2018-02-05 03:30 | 41 | 38 |  |  | 43136.1458 | 49 | 49
2018-02-05 04:00 | 40 | 37 |  |  | 43136.1667 | 48 | 48
2018-02-05 04:30 | 40 | 37 |  |  | 43136.1875 | 48 | 48
2018-02-05 05:00 | 41 | 39 |  |  | 43136.2083 | 49 | 49
2018-02-05 05:30 | 42 | 40 |  |  | 43136.2292 | 51 | 51
2018-02-05 06:00 | 44 | 43 |  |  | 43136.25 | 56 | 56
2018-02-05 06:30 | 52 | 52 |  |  | 43136.2708 | 68 | 67
2018-02-05 07:00 | 56 | 56 |  |  | 43136.2917 | 76 | 76
2018-02-05 07:30 | 62 | 62 |  |  | 43136.3125 | 85 | 84
2018-02-05 08:00 | 66 | 66 |  |  | 43136.3333 | 90 | 90
2018-02-05 08:30 | 65 | 65 |  |  | 43136.3542 | 90 | 90
2018-02-05 09:00 | 65 | 65 |  |  | 43136.375 | 90 | 90
2018-02-05 09:30 | 65 | 65 |  |  | 43136.3958 | 90 | 90
2018-02-05 10:00 | 65 | 65 |  |  | 43136.4167 | 90 | 90
2018-02-05 10:30 | 64 | 64 |  |  | 43136.4375 | 88 | 88
2018-02-05 11:00 | 64 | 64 |  |  | 43136.4583 | 87 | 87
2018-02-05 11:30 | 64 | 64 |  |  | 43136.4792 | 87 | 87
2018-02-05 12:00 | 65 | 65 |  |  | 43136.5 | 87 | 87
2018-02-05 12:30 | 64 | 64 |  |  | 43136.5208 | 85 | 85
2018-02-05 13:00 | 66 | 65 |  |  | 43136.5417 | 85 | 85
2018-02-05 13:30 | 66 | 66 |  |  | 43136.5625 | 87 | 87
2018-02-05 14:00 | 70 | 70 |  |  | 43136.5833 | 90 | 90
2018-02-05 14:30 | 71 | 70 |  |  | 43136.6042 | 91 | 91
2018-02-05 15:00 | 70 | 70 |  |  | 43136.625 | 94 | 94
2018-02-05 15:30 | 71 | 71 |  |  | 43136.6458 | 95 | 95
2018-02-05 16:00 | 75 | 75 |  |  | 43136.6667 | 96 | 96
2018-02-05 16:30 | 79 | 79 |  |  | 43136.6875 | 100 | 100
2018-02-05 17:00 | 81 | 81 |  |  | 43136.7083 | 100 | 100
2018-02-05 17:30 | 81 | 81 |  |  | 43136.7292 | 99 | 98
2018-02-05 18:00 | 79 | 78 |  |  | 43136.75 | 95 | 94
2018-02-05 18:30 | 79 | 77 |  |  | 43136.7708 | 93 | 92
2018-02-05 19:00 | 81 | 79 |  |  | 43136.7917 | 95 | 94
2018-02-05 19:30 | 80 | 79 |  |  | 43136.8125 | 93 | 92
2018-02-05 20:00 | 80 | 79 |  |  | 43136.8333 | 94 | 92
2018-02-05 20:30 | 81 | 79 |  |  | 43136.8542 | 94 | 93
2018-02-05 21:00 | 79 | 77 |  |  | 43136.875 | 90 | 89
2018-02-05 21:30 | 75 | 73 |  |  | 43136.8958 | 87 | 85
2018-02-05 22:00 | 74 | 72 |  |  | 43136.9167 | 86 | 84
2018-02-05 22:30 | 67 | 65 |  |  | 43136.9375 | 80 | 78
2018-02-05 23:00 | 66 | 63 |  |  | 43136.9583 | 77 | 74
2018-02-05 23:30 | 60 | 59 |  |  | 43136.9792 | 71 | 71
2018-02-06 | 56 | 54 |  |  | 43137 | 66 | 65
2018-02-06 00:30 | 50 | 47 |  |  | 43137.0208 | 59 | 58
2018-02-06 01:00 | 47 | 43 |  |  | 43137.0417 | 56 | 54
2018-02-06 01:30 | 46 | 42 |  |  | 43137.0625 | 54 | 52
2018-02-06 02:00 | 45 | 41 |  |  | 43137.0833 | 54 | 52
2018-02-06 02:30 | 44 | 40 |  |  | 43137.1042 | 53 | 51
2018-02-06 03:00 | 44 | 40 |  |  | 43137.125 | 53 | 51
2018-02-06 03:30 | 45 | 41 |  |  | 43137.1458 | 52 | 50
2018-02-06 04:00 | 45 | 41 |  |  | 43137.1667 | 53 | 51
2018-02-06 04:30 | 44 | 40 |  |  | 43137.1875 | 53 | 52
2018-02-06 05:00 | 47 | 43 |  |  | 43137.2083 | 56 | 55
2018-02-06 05:30 | 51 | 48 |  |  | 43137.2292 | 61 | 60
2018-02-06 06:00 | 57 | 54 |  |  | 43137.25 | 68 | 67
2018-02-06 06:30 | 61 | 59 |  |  | 43137.2708 | 76 | 76
2018-02-06 07:00 | 64 | 63 |  |  | 43137.2917 | 82 | 82
2018-02-06 07:30 | 73 | 72 |  |  | 43137.3125 | 93 | 93
2018-02-06 08:00 | 76 | 75 |  |  | 43137.3333 | 97 | 97
2018-02-06 08:30 | 76 | 76 |  |  | 43137.3542 | 98 | 98
2018-02-06 09:00 | 75 | 75 |  |  | 43137.375 | 98 | 98
2018-02-06 09:30 | 77 | 76 |  |  | 43137.3958 | 100 | 100
2018-02-06 10:00 | 77 | 77 |  |  | 43137.4167 | 101 | 101
2018-02-06 10:30 | 76 | 75 |  |  | 43137.4375 | 98 | 98
2018-02-06 11:00 | 72 | 71 |  |  | 43137.4583 | 95 | 95
2018-02-06 11:30 | 72 | 71 |  |  | 43137.4792 | 94 | 94
2018-02-06 12:00 | 73 | 72 |  |  | 43137.5 | 96 | 96
2018-02-06 12:30 | 74 | 74 |  |  | 43137.5208 | 96 | 96
2018-02-06 13:00 | 73 | 72 |  |  | 43137.5417 | 92 | 92
2018-02-06 13:30 | 74 | 73 |  |  | 43137.5625 | 93 | 93
2018-02-06 14:00 | 78 | 78 |  |  | 43137.5833 | 96 | 96
2018-02-06 14:30 | 76 | 75 |  |  | 43137.6042 | 96 | 96
2018-02-06 15:00 | 75 | 74 |  |  | 43137.625 | 93 | 93
2018-02-06 15:30 | 74 | 73 |  |  | 43137.6458 | 95 | 95
2018-02-06 16:00 | 77 | 76 |  |  | 43137.6667 | 98 | 98
2018-02-06 16:30 | 77 | 77 |  |  | 43137.6875 | 100 | 100
2018-02-06 17:00 | 81 | 80 |  |  | 43137.7083 | 98 | 98
2018-02-06 17:30 | 81 | 80 |  |  | 43137.7292 | 98 | 97
2018-02-06 18:00 | 82 | 80 |  |  | 43137.75 | 97 | 96
2018-02-06 18:30 | 82 | 81 |  |  | 43137.7708 | 96 | 96
2018-02-06 19:00 | 86 | 84 |  |  | 43137.7917 | 101 | 100
2018-02-06 19:30 | 85 | 84 |  |  | 43137.8125 | 100 | 100
2018-02-06 20:00 | 84 | 83 |  |  | 43137.8333 | 98 | 97
2018-02-06 20:30 | 83 | 83 |  |  | 43137.8542 | 96 | 96
2018-02-06 21:00 | 78 | 78 |  |  | 43137.875 | 92 | 92
2018-02-06 21:30 | 75 | 74 |  |  | 43137.8958 | 87 | 87
2018-02-06 22:00 | 72 | 71 |  |  | 43137.9167 | 84 | 84
2018-02-06 22:30 | 67 | 65 |  |  | 43137.9375 | 77 | 77
2018-02-06 23:00 | 64 | 62 |  |  | 43137.9583 | 74 | 74
2018-02-06 23:30 | 59 | 57 |  |  | 43137.9792 | 70 | 70
2018-02-07 | 52 | 50 |  |  | 43138 | 63 | 63
2018-02-07 00:30 | 47 | 45 |  |  | 43138.0208 | 57 | 57
2018-02-07 01:00 | 44 | 42 |  |  | 43138.0417 | 53 | 53
2018-02-07 01:30 | 43 | 41 |  |  | 43138.0625 | 53 | 53
2018-02-07 02:00 | 44 | 42 |  |  | 43138.0833 | 51 | 51
2018-02-07 02:30 | 45 | 43 |  |  | 43138.1042 | 53 | 53
2018-02-07 03:00 | 45 | 43 |  |  | 43138.125 | 53 | 53
2018-02-07 03:30 | 44 | 42 |  |  | 43138.1458 | 52 | 52
2018-02-07 04:00 | 43 | 41 |  |  | 43138.1667 | 52 | 52
2018-02-07 04:30 | 43 | 41 |  |  | 43138.1875 | 51 | 51
2018-02-07 05:00 | 43 | 42 |  |  | 43138.2083 | 53 | 53
2018-02-07 05:30 | 47 | 46 |  |  | 43138.2292 | 57 | 57
2018-02-07 06:00 | 50 | 49 |  |  | 43138.25 | 62 | 62
2018-02-07 06:30 | 57 | 56 |  |  | 43138.2708 | 72 | 72
2018-02-07 07:00 | 66 | 62 |  |  | 43138.2917 | 81 | 81
2018-02-07 07:30 | 79 | 71 |  |  | 43138.3125 | 93 | 92
2018-02-07 08:00 | 82 | 74 |  |  | 43138.3333 | 98 | 96
2018-02-07 08:30 | 78 | 71 |  |  | 43138.3542 | 95 | 94
2018-02-07 09:00 | 76 | 70 |  |  | 43138.375 | 94 | 93
2018-02-07 09:30 | 81 | 73 |  |  | 43138.3958 | 96 | 96
2018-02-07 10:00 | 78 | 70 |  |  | 43138.4167 | 95 | 94
2018-02-07 10:30 | 78 | 70 |  |  | 43138.4375 | 94 | 94
2018-02-07 11:00 | 78 | 70 |  |  | 43138.4583 | 94 | 94
2018-02-07 11:30 | 76 | 68 |  |  | 43138.4792 | 92 | 92
2018-02-07 12:00 | 77 | 69 |  |  | 43138.5 | 93 | 93
2018-02-07 12:30 | 76 | 68 |  |  | 43138.5208 | 92 | 91
2018-02-07 13:00 | 73 | 64 |  |  | 43138.5417 | 86 | 86
2018-02-07 13:30 | 72 | 65 |  |  | 43138.5625 | 86 | 86
2018-02-07 14:00 | 75 | 68 |  |  | 43138.5833 | 89 | 89
2018-02-07 14:30 | 75 | 68 |  |  | 43138.6042 | 89 | 88
2018-02-07 15:00 | 75 | 68 |  |  | 43138.625 | 89 | 89
2018-02-07 15:30 | 77 | 70 |  |  | 43138.6458 | 91 | 91
2018-02-07 16:00 | 80 | 73 |  |  | 43138.6667 | 94 | 93
2018-02-07 16:30 | 80 | 72 |  |  | 43138.6875 | 92 | 92
2018-02-07 17:00 | 84 | 76 |  |  | 43138.7083 | 96 | 96
2018-02-07 17:30 | 86 | 79 |  |  | 43138.7292 | 97 | 96
2018-02-07 18:00 | 86 | 78 |  |  | 43138.75 | 96 | 95
2018-02-07 18:30 | 85 | 76 |  |  | 43138.7708 | 92 | 91
2018-02-07 19:00 | 89 | 81 |  |  | 43138.7917 | 97 | 95
2018-02-07 19:30 | 90 | 81 |  |  | 43138.8125 | 98 | 96
2018-02-07 20:00 | 92 | 83 |  |  | 43138.8333 | 98 | 97
2018-02-07 20:30 | 92 | 84 |  |  | 43138.8542 | 99 | 98
2018-02-07 21:00 | 85 | 80 |  |  | 43138.875 | 93 | 93
2018-02-07 21:30 | 81 | 77 |  |  | 43138.8958 | 90 | 90
2018-02-07 22:00 | 78 | 74 |  |  | 43138.9167 | 88 | 88
2018-02-07 22:30 | 70 | 66 |  |  | 43138.9375 | 81 | 81
2018-02-07 23:00 | 70 | 65 |  |  | 43138.9583 | 78 | 78
2018-02-07 23:30 | 67 | 60 |  |  | 43138.9792 | 72 | 72
2018-02-08 | 62 | 54 |  |  | 43139 | 67 | 67
2018-02-08 00:30 | 58 | 48 |  |  | 43139.0208 | 60 | 60
2018-02-08 01:00 | 55 | 44 |  |  | 43139.0417 | 55 | 55
2018-02-08 01:30 | 53 | 42 |  |  | 43139.0625 | 53 | 53
2018-02-08 02:00 | 53 | 41 |  |  | 43139.0833 | 52 | 52
2018-02-08 02:30 | 53 | 41 |  |  | 43139.1042 | 52 | 52
2018-02-08 03:00 | 53 | 42 |  |  | 43139.125 | 52 | 52
2018-02-08 03:30 | 52 | 42 |  |  | 43139.1458 | 52 | 52
2018-02-08 04:00 | 52 | 41 |  |  | 43139.1667 | 52 | 51
2018-02-08 04:30 | 52 | 41 |  |  | 43139.1875 | 53 | 52
2018-02-08 05:00 | 54 | 44 |  |  | 43139.2083 | 55 | 55
2018-02-08 05:30 | 56 | 48 |  |  | 43139.2292 | 60 | 60
2018-02-08 06:00 | 59 | 51 |  |  | 43139.25 | 64 | 64
2018-02-08 06:30 | 65 | 60 |  |  | 43139.2708 | 76 | 76
2018-02-08 07:00 | 69 | 66 |  |  | 43139.2917 | 85 | 85
2018-02-08 07:30 | 77 | 75 |  |  | 43139.3125 | 96 | 96
2018-02-08 08:00 | 79 | 78 |  |  | 43139.3333 | 101 | 100
2018-02-08 08:30 | 79 | 77 |  |  | 43139.3542 | 101 | 100
2018-02-08 09:00 | 75 | 73 |  |  | 43139.375 | 99 | 98
2018-02-08 09:30 | 77 | 75 |  |  | 43139.3958 | 99 | 98
2018-02-08 10:00 | 77 | 76 |  |  | 43139.4167 | 100 | 99
2018-02-08 10:30 | 78 | 77 |  |  | 43139.4375 | 103 | 102
2018-02-08 11:00 | 79 | 77 |  |  | 43139.4583 | 103 | 102
2018-02-08 11:30 | 75 | 73 |  |  | 43139.4792 | 98 | 97
2018-02-08 12:00 | 78 | 75 |  |  | 43139.5 | 98 | 97
2018-02-08 12:30 | 74 | 71 |  |  | 43139.5208 | 95 | 95
2018-02-08 13:00 | 69 | 67 |  |  | 43139.5417 | 90 | 90
2018-02-08 13:30 | 69 | 67 |  |  | 43139.5625 | 92 | 91
2018-02-08 14:00 | 71 | 70 |  |  | 43139.5833 | 91 | 90
2018-02-08 14:30 | 66 | 64 |  |  | 43139.6042 | 85 | 84
2018-02-08 15:00 | 61 | 59 |  |  | 43139.625 | 80 | 78
2018-02-08 15:30 | 56 | 55 |  |  | 43139.6458 | 79 | 78
2018-02-08 16:00 | 59 | 58 |  |  | 43139.6667 | 80 | 79
2018-02-08 16:30 | 64 | 62 |  |  | 43139.6875 | 84 | 84
2018-02-08 17:00 | 65 | 63 |  |  | 43139.7083 | 85 | 85
2018-02-08 17:30 | 67 | 64 |  |  | 43139.7292 | 83 | 83
2018-02-08 18:00 | 65 | 62 |  |  | 43139.75 | 80 | 80
2018-02-08 18:30 | 65 | 61 |  |  | 43139.7708 | 78 | 78
2018-02-08 19:00 | 70 | 66 |  |  | 43139.7917 | 85 | 85
2018-02-08 19:30 | 72 | 69 |  |  | 43139.8125 | 87 | 87
2018-02-08 20:00 | 71 | 68 |  |  | 43139.8333 | 84 | 84
2018-02-08 20:30 | 67 | 63 |  |  | 43139.8542 | 78 | 78
2018-02-08 21:00 | 65 | 61 |  |  | 43139.875 | 76 | 76
2018-02-08 21:30 | 63 | 58 |  |  | 43139.8958 | 73 | 73
2018-02-08 22:00 | 65 | 60 |  |  | 43139.9167 | 76 | 76
2018-02-08 22:30 | 63 | 58 |  |  | 43139.9375 | 73 | 73
2018-02-08 23:00 | 63 | 57 |  |  | 43139.9583 | 70 | 70
2018-02-08 23:30 | 61 | 54 |  |  | 43139.9792 | 67 | 67
2018-02-09 | 56 | 48 |  |  | 43140 | 61 | 61
2018-02-09 00:30 | 50 | 41 |  |  | 43140.0208 | 54 | 54
2018-02-09 01:00 | 47 | 37 |  |  | 43140.0417 | 49 | 49
2018-02-09 01:30 | 46 | 36 |  |  | 43140.0625 | 48 | 48
2018-02-09 02:00 | 44 | 34 |  |  | 43140.0833 | 46 | 46
2018-02-09 02:30 | 43 | 33 |  |  | 43140.1042 | 43 | 43
2018-02-09 03:00 | 41 | 29 |  |  | 43140.125 | 40 | 40
2018-02-09 03:30 | 41 | 30 |  |  | 43140.1458 | 40 | 40
2018-02-09 04:00 | 41 | 29 |  |  | 43140.1667 | 40 | 40
2018-02-09 04:30 | 42 | 30 |  |  | 43140.1875 | 42 | 42
2018-02-09 05:00 | 45 | 35 |  |  | 43140.2083 | 47 | 47
2018-02-09 05:30 | 45 | 37 |  |  | 43140.2292 | 51 | 51
2018-02-09 06:00 | 46 | 39 |  |  | 43140.25 | 54 | 54
2018-02-09 06:30 | 51 | 47 |  |  | 43140.2708 | 65 | 64
2018-02-09 07:00 | 53 | 51 |  |  | 43140.2917 | 72 | 71
2018-02-09 07:30 | 56 | 54 |  |  | 43140.3125 | 79 | 78
2018-02-09 08:00 | 55 | 54 |  |  | 43140.3333 | 78 | 78
2018-02-09 08:30 | 53 | 53 |  |  | 43140.3542 | 77 | 77
2018-02-09 09:00 | 52 | 52 |  |  | 43140.375 | 76 | 76
2018-02-09 09:30 | 54 | 54 |  |  | 43140.3958 | 78 | 78
2018-02-09 10:00 | 56 | 56 |  |  | 43140.4167 | 80 | 80
2018-02-09 10:30 | 55 | 55 |  |  | 43140.4375 | 82 | 82
2018-02-09 11:00 | 56 | 56 |  |  | 43140.4583 | 84 | 84
2018-02-09 11:30 | 58 | 58 |  |  | 43140.4792 | 86 | 86
2018-02-09 12:00 | 57 | 57 |  |  | 43140.5 | 85 | 85
2018-02-09 12:30 | 57 | 57 |  |  | 43140.5208 | 84 | 84
2018-02-09 13:00 | 58 | 58 |  |  | 43140.5417 | 84 | 84
2018-02-09 13:30 | 58 | 58 |  |  | 43140.5625 | 84 | 84
2018-02-09 14:00 | 61 | 61 |  |  | 43140.5833 | 87 | 87
2018-02-09 14:30 | 64 | 64 |  |  | 43140.6042 | 90 | 90
2018-02-09 15:00 | 66 | 66 |  |  | 43140.625 | 93 | 93
2018-02-09 15:30 | 68 | 68 |  |  | 43140.6458 | 94 | 94
2018-02-09 16:00 | 70 | 70 |  |  | 43140.6667 | 97 | 97
2018-02-09 16:30 | 74 | 74 |  |  | 43140.6875 | 100 | 98
2018-02-09 17:00 | 77 | 77 |  |  | 43140.7083 | 102 | 101
2018-02-09 17:30 | 77 | 76 |  |  | 43140.7292 | 101 | 98
2018-02-09 18:00 | 76 | 76 |  |  | 43140.75 | 98 | 97
2018-02-09 18:30 | 73 | 73 |  |  | 43140.7708 | 93 | 93
2018-02-09 19:00 | 75 | 75 |  |  | 43140.7917 | 94 | 94
2018-02-09 19:30 | 77 | 77 |  |  | 43140.8125 | 96 | 96
2018-02-09 20:00 | 80 | 80 |  |  | 43140.8333 | 97 | 97
2018-02-09 20:30 | 78 | 78 |  |  | 43140.8542 | 94 | 94
2018-02-09 21:00 | 76 | 76 |  |  | 43140.875 | 92 | 92
2018-02-09 21:30 | 72 | 72 |  |  | 43140.8958 | 88 | 88
2018-02-09 22:00 | 69 | 69 |  |  | 43140.9167 | 85 | 85
2018-02-09 22:30 | 64 | 64 |  |  | 43140.9375 | 80 | 80
2018-02-09 23:00 | 62 | 62 |  |  | 43140.9583 | 78 | 77
2018-02-09 23:30 | 61 | 60 |  |  | 43140.9792 | 74 | 74
2018-02-10 | 55 | 54 |  |  | 43141 | 68 | 68
2018-02-10 00:30 | 46 | 45 |  |  | 43141.0208 | 58 | 58
2018-02-10 01:00 | 44 | 42 |  |  | 43141.0417 | 54 | 54
2018-02-10 01:30 | 44 | 42 |  |  | 43141.0625 | 55 | 55
2018-02-10 02:00 | 43 | 41 |  |  | 43141.0833 | 54 | 54
2018-02-10 02:30 | 41 | 39 |  |  | 43141.1042 | 51 | 51
2018-02-10 03:00 | 39 | 36 |  |  | 43141.125 | 49 | 49
2018-02-10 03:30 | 38 | 36 |  |  | 43141.1458 | 48 | 48
2018-02-10 04:00 | 38 | 36 |  |  | 43141.1667 | 48 | 48
2018-02-10 04:30 | 40 | 38 |  |  | 43141.1875 | 50 | 50
2018-02-10 05:00 | 40 | 39 |  |  | 43141.2083 | 51 | 51
2018-02-10 05:30 | 42 | 40 |  |  | 43141.2292 | 52 | 52
2018-02-10 06:00 | 39 | 38 |  |  | 43141.25 | 51 | 51
2018-02-10 06:30 | 40 | 38 |  |  | 43141.2708 | 53 | 52
2018-02-10 07:00 | 41 | 40 |  |  | 43141.2917 | 55 | 55
2018-02-10 07:30 | 44 | 43 |  |  | 43141.3125 | 60 | 60
2018-02-10 08:00 | 45 | 45 |  |  | 43141.3333 | 61 | 61
2018-02-10 08:30 | 47 | 47 |  |  | 43141.3542 | 65 | 64
2018-02-10 09:00 | 50 | 49 |  |  | 43141.375 | 67 | 67
2018-02-10 09:30 | 51 | 51 |  |  | 43141.3958 | 68 | 68
2018-02-10 10:00 | 51 | 51 |  |  | 43141.4167 | 69 | 68
2018-02-10 10:30 | 52 | 52 |  |  | 43141.4375 | 70 | 69
2018-02-10 11:00 | 54 | 54 |  |  | 43141.4583 | 71 | 71
2018-02-10 11:30 | 55 | 55 |  |  | 43141.4792 | 71 | 71
2018-02-10 12:00 | 57 | 57 |  |  | 43141.5 | 73 | 73
2018-02-10 12:30 | 58 | 57 |  |  | 43141.5208 | 74 | 73
2018-02-10 13:00 | 59 | 58 |  |  | 43141.5417 | 74 | 74
2018-02-10 13:30 | 65 | 64 |  |  | 43141.5625 | 79 | 79
2018-02-10 14:00 | 70 | 68 |  |  | 43141.5833 | 82 | 81
2018-02-10 14:30 | 70 | 69 |  |  | 43141.6042 | 82 | 81
2018-02-10 15:00 | 70 | 70 |  |  | 43141.625 | 84 | 84
2018-02-10 15:30 | 74 | 74 |  |  | 43141.6458 | 88 | 87
2018-02-10 16:00 | 77 | 76 |  |  | 43141.6667 | 90 | 89
2018-02-10 16:30 | 76 | 76 |  |  | 43141.6875 | 90 | 89
2018-02-10 17:00 | 78 | 77 |  |  | 43141.7083 | 90 | 89
2018-02-10 17:30 | 76 | 76 |  |  | 43141.7292 | 88 | 88
2018-02-10 18:00 | 76 | 75 |  |  | 43141.75 | 88 | 87
2018-02-10 18:30 | 74 | 73 |  |  | 43141.7708 | 91 | 90
2018-02-10 19:00 | 76 | 75 |  |  | 43141.7917 | 96 | 94
2018-02-10 19:30 | 77 | 77 |  |  | 43141.8125 | 96 | 94
2018-02-10 20:00 | 76 | 75 |  |  | 43141.8333 | 94 | 93
2018-02-10 20:30 | 74 | 73 |  |  | 43141.8542 | 92 | 91
2018-02-10 21:00 | 71 | 70 |  |  | 43141.875 | 88 | 86
2018-02-10 21:30 | 68 | 67 |  |  | 43141.8958 | 86 | 84
2018-02-10 22:00 | 67 | 65 |  |  | 43141.9167 | 86 | 84
2018-02-10 22:30 | 66 | 65 |  |  | 43141.9375 | 84 | 83
2018-02-10 23:00 | 66 | 64 |  |  | 43141.9583 | 81 | 80
2018-02-10 23:30 | 62 | 60 |  |  | 43141.9792 | 77 | 76
2018-02-11 | 59 | 56 |  |  | 43142 | 74 | 72
2018-02-11 00:30 | 54 | 50 |  |  | 43142.0208 | 67 | 65
2018-02-11 01:00 | 51 | 47 |  |  | 43142.0417 | 62 | 61
2018-02-11 01:30 | 50 | 45 |  |  | 43142.0625 | 60 | 59
2018-02-11 02:00 | 50 | 44 |  |  | 43142.0833 | 58 | 58
2018-02-11 02:30 | 50 | 45 |  |  | 43142.1042 | 57 | 57
2018-02-11 03:00 | 51 | 45 |  |  | 43142.125 | 58 | 57
2018-02-11 03:30 | 49 | 43 |  |  | 43142.1458 | 56 | 56
2018-02-11 04:00 | 50 | 43 |  |  | 43142.1667 | 56 | 56
2018-02-11 04:30 | 49 | 42 |  |  | 43142.1875 | 55 | 55
2018-02-11 05:00 | 50 | 43 |  |  | 43142.2083 | 55 | 55
2018-02-11 05:30 | 48 | 41 |  |  | 43142.2292 | 55 | 55
2018-02-11 06:00 | 47 | 39 |  |  | 43142.25 | 53 | 53
2018-02-11 06:30 | 47 | 39 |  |  | 43142.2708 | 55 | 54
2018-02-11 07:00 | 47 | 40 |  |  | 43142.2917 | 57 | 56
2018-02-11 07:30 | 49 | 43 |  |  | 43142.3125 | 61 | 60
2018-02-11 08:00 | 52 | 48 |  |  | 43142.3333 | 65 | 64
2018-02-11 08:30 | 54 | 51 |  |  | 43142.3542 | 69 | 68
2018-02-11 09:00 | 55 | 52 |  |  | 43142.375 | 71 | 70
2018-02-11 09:30 | 59 | 55 |  |  | 43142.3958 | 71 | 71
2018-02-11 10:00 | 62 | 59 |  |  | 43142.4167 | 75 | 75
2018-02-11 10:30 | 64 | 61 |  |  | 43142.4375 | 78 | 78
2018-02-11 11:00 | 66 | 64 |  |  | 43142.4583 | 80 | 80
2018-02-11 11:30 | 69 | 67 |  |  | 43142.4792 | 83 | 83
2018-02-11 12:00 | 72 | 71 |  |  | 43142.5 | 88 | 87
2018-02-11 12:30 | 75 | 75 |  |  | 43142.5208 | 90 | 89
2018-02-11 13:00 | 78 | 78 |  |  | 43142.5417 | 93 | 92
2018-02-11 13:30 | 82 | 82 |  |  | 43142.5625 | 97 | 97
2018-02-11 14:00 | 86 | 86 |  |  | 43142.5833 | 101 | 100
2018-02-11 14:30 | 92 | 90 |  |  | 43142.6042 | 108 | 106
2018-02-11 15:00 | 99 | 94 |  |  | 43142.625 | 112 | 109
2018-02-11 15:30 | 102 | 96 |  |  | 43142.6458 | 114 | 111
2018-02-11 16:00 | 100 | 95 |  |  | 43142.6667 | 114 | 112
2018-02-11 16:30 | 94 | 90 |  |  | 43142.6875 | 115 | 112
2018-02-11 17:00 | 97 | 92 |  |  | 43142.7083 | 117 | 113
2018-02-11 17:30 | 97 | 93 |  |  | 43142.7292 | 115 | 113
2018-02-11 18:00 | 100 | 94 |  |  | 43142.75 | 116 | 114
2018-02-11 18:30 | 105 | 99 |  |  | 43142.7708 | 115 | 115
2018-02-11 19:00 | 96 | 90 |  |  | 43142.7917 | 107 | 107
2018-02-11 19:30 | 82 | 80 |  |  | 43142.8125 | 100 | 100
2018-02-11 20:00 | 78 | 77 |  |  | 43142.8333 | 95 | 95
2018-02-11 20:30 | 75 | 74 |  |  | 43142.8542 | 94 | 94
2018-02-11 21:00 | 73 | 72 |  |  | 43142.875 | 90 | 90
2018-02-11 21:30 | 69 | 68 |  |  | 43142.8958 | 84 | 84
2018-02-11 22:00 | 69 | 66 |  |  | 43142.9167 | 82 | 82
2018-02-11 22:30 | 68 | 65 |  |  | 43142.9375 | 79 | 78
2018-02-11 23:00 | 67 | 63 |  |  | 43142.9583 | 75 | 74
2018-02-11 23:30 | 61 | 55 |  |  | 43142.9792 | 69 | 68
2018-02-12 | 58 | 52 |  |  | 43143 | 64 | 63
2018-02-12 00:30 | 55 | 48 |  |  | 43143.0208 | 61 | 60
2018-02-12 01:00 | 53 | 45 |  |  | 43143.0417 | 58 | 56
2018-02-12 01:30 | 52 | 44 |  |  | 43143.0625 | 57 | 55
2018-02-12 02:00 | 52 | 43 |  |  | 43143.0833 | 57 | 55
2018-02-12 02:30 | 51 | 43 |  |  | 43143.1042 | 56 | 55
2018-02-12 03:00 | 52 | 43 |  |  | 43143.125 | 56 | 54
2018-02-12 03:30 | 51 | 42 |  |  | 43143.1458 | 55 | 54
2018-02-12 04:00 | 50 | 41 |  |  | 43143.1667 | 54 | 53
2018-02-12 04:30 | 51 | 43 |  |  | 43143.1875 | 56 | 55
2018-02-12 05:00 | 53 | 45 |  |  | 43143.2083 | 59 | 57
2018-02-12 05:30 | 57 | 52 |  |  | 43143.2292 | 64 | 63
2018-02-12 06:00 | 61 | 56 |  |  | 43143.25 | 71 | 70
2018-02-12 06:30 | 64 | 63 |  |  | 43143.2708 | 82 | 82
2018-02-12 07:00 | 68 | 68 |  |  | 43143.2917 | 91 | 90
2018-02-12 07:30 | 77 | 77 |  |  | 43143.3125 | 102 | 102
2018-02-12 08:00 | 81 | 81 |  |  | 43143.3333 | 106 | 106
2018-02-12 08:30 | 81 | 81 |  |  | 43143.3542 | 109 | 109
2018-02-12 09:00 | 83 | 83 |  |  | 43143.375 | 111 | 111
2018-02-12 09:30 | 85 | 85 |  |  | 43143.3958 | 114 | 113
2018-02-12 10:00 | 87 | 87 |  |  | 43143.4167 | 115 | 115
2018-02-12 10:30 | 90 | 90 |  |  | 43143.4375 | 118 | 118
2018-02-12 11:00 | 92 | 92 |  |  | 43143.4583 | 120 | 120
2018-02-12 11:30 | 95 | 95 |  |  | 43143.4792 | 123 | 122
2018-02-12 12:00 | 94 | 94 |  |  | 43143.5 | 122 | 121
2018-02-12 12:30 | 96 | 95 |  |  | 43143.5208 | 123 | 122
2018-02-12 13:00 | 96 | 96 |  |  | 43143.5417 | 124 | 123
2018-02-12 13:30 | 100 | 99 |  |  | 43143.5625 | 129 | 126
2018-02-12 14:00 | 104 | 103 |  |  | 43143.5833 | 133 | 130
2018-02-12 14:30 | 107 | 106 |  |  | 43143.6042 | 138 | 134
2018-02-12 15:00 | 108 | 107 |  |  | 43143.625 | 139 | 135
2018-02-12 15:30 | 111 | 110 |  |  | 43143.6458 | 140 | 136
2018-02-12 16:00 | 111 | 110 |  |  | 43143.6667 | 145 | 141
2018-02-12 16:30 | 110 | 108 |  |  | 43143.6875 | 148 | 142
2018-02-12 17:00 | 112 | 110 |  |  | 43143.7083 | 149 | 143
2018-02-12 17:30 | 110 | 108 |  |  | 43143.7292 | 145 | 139
2018-02-12 18:00 | 107 | 106 |  |  | 43143.75 | 138 | 135
2018-02-12 18:30 | 105 | 104 |  |  | 43143.7708 | 132 | 131
2018-02-12 19:00 | 108 | 108 |  |  | 43143.7917 | 135 | 134
2018-02-12 19:30 | 108 | 108 |  |  | 43143.8125 | 135 | 135
2018-02-12 20:00 | 108 | 108 |  |  | 43143.8333 | 135 | 135
2018-02-12 20:30 | 105 | 105 |  |  | 43143.8542 | 131 | 131
2018-02-12 21:00 | 101 | 101 |  |  | 43143.875 | 127 | 126
2018-02-12 21:30 | 96 | 95 |  |  | 43143.8958 | 119 | 119
2018-02-12 22:00 | 93 | 91 |  |  | 43143.9167 | 114 | 114
2018-02-12 22:30 | 88 | 84 |  |  | 43143.9375 | 108 | 107
2018-02-12 23:00 | 91 | 87 |  |  | 43143.9583 | 104 | 104
2018-02-12 23:30 | 88 | 83 |  |  | 43143.9792 | 101 | 101
2018-02-13 | 83 | 78 |  |  | 43144 | 96 | 95
2018-02-13 00:30 | 78 | 72 |  |  | 43144.0208 | 88 | 88
2018-02-13 01:00 | 75 | 69 |  |  | 43144.0417 | 86 | 86
2018-02-13 01:30 | 73 | 66 |  |  | 43144.0625 | 83 | 83
2018-02-13 02:00 | 73 | 66 |  |  | 43144.0833 | 82 | 82
2018-02-13 02:30 | 72 | 65 |  |  | 43144.1042 | 81 | 81
2018-02-13 03:00 | 71 | 64 |  |  | 43144.125 | 80 | 80
2018-02-13 03:30 | 70 | 63 |  |  | 43144.1458 | 78 | 78
2018-02-13 04:00 | 69 | 62 |  |  | 43144.1667 | 78 | 78
2018-02-13 04:30 | 69 | 63 |  |  | 43144.1875 | 80 | 80
2018-02-13 05:00 | 72 | 66 |  |  | 43144.2083 | 83 | 83
2018-02-13 05:30 | 75 | 71 |  |  | 43144.2292 | 89 | 89
2018-02-13 06:00 | 78 | 74 |  |  | 43144.25 | 94 | 93
2018-02-13 06:30 | 83 | 80 |  |  | 43144.2708 | 105 | 105
2018-02-13 07:00 | 90 | 86 |  |  | 43144.2917 | 113 | 113
2018-02-13 07:30 | 100 | 95 |  |  | 43144.3125 | 125 | 125
2018-02-13 08:00 | 104 | 100 |  |  | 43144.3333 | 129 | 129
2018-02-13 08:30 | 109 | 106 |  |  | 43144.3542 | 136 | 136
2018-02-13 09:00 | 111 | 108 |  |  | 43144.375 | 141 | 141
2018-02-13 09:30 | 107 | 105 |  |  | 43144.3958 | 139 | 138
2018-02-13 10:00 | 104 | 101 |  |  | 43144.4167 | 132 | 132
2018-02-13 10:30 | 103 | 100 |  |  | 43144.4375 | 131 | 131
2018-02-13 11:00 | 105 | 103 |  |  | 43144.4583 | 134 | 134
2018-02-13 11:30 | 106 | 104 |  |  | 43144.4792 | 135 | 135
2018-02-13 12:00 | 107 | 106 |  |  | 43144.5 | 138 | 138
2018-02-13 12:30 | 109 | 107 |  |  | 43144.5208 | 139 | 139
2018-02-13 13:00 | 112 | 109 |  |  | 43144.5417 | 142 | 141
2018-02-13 13:30 | 115 | 112 |  |  | 43144.5625 | 145 | 144
2018-02-13 14:00 | 117 | 114 |  |  | 43144.5833 | 147 | 146
2018-02-13 14:30 | 116 | 113 |  |  | 43144.6042 | 148 | 147
2018-02-13 15:00 | 110 | 108 |  |  | 43144.625 | 146 | 145
2018-02-13 15:30 | 110 | 107 |  |  | 43144.6458 | 146 | 144
2018-02-13 16:00 | 116 | 110 |  |  | 43144.6667 | 152 | 148
2018-02-13 16:30 | 120 | 115 |  |  | 43144.6875 | 155 | 150
2018-02-13 17:00 | 119 | 113 |  |  | 43144.7083 | 153 | 148
2018-02-13 17:30 | 112 | 110 |  |  | 43144.7292 | 141 | 140
2018-02-13 18:00 | 110 | 109 |  |  | 43144.75 | 139 | 139
2018-02-13 18:30 | 108 | 108 |  |  | 43144.7708 | 136 | 135
2018-02-13 19:00 | 113 | 110 |  |  | 43144.7917 | 140 | 138
2018-02-13 19:30 | 111 | 109 |  |  | 43144.8125 | 138 | 135
2018-02-13 20:00 | 106 | 105 |  |  | 43144.8333 | 136 | 134
2018-02-13 20:30 | 97 | 96 |  |  | 43144.8542 | 126 | 123
2018-02-13 21:00 | 92 | 91 |  |  | 43144.875 | 117 | 115
2018-02-13 21:30 | 84 | 84 |  |  | 43144.8958 | 106 | 106
2018-02-13 22:00 | 81 | 81 |  |  | 43144.9167 | 103 | 103
2018-02-13 22:30 | 74 | 74 |  |  | 43144.9375 | 97 | 97
2018-02-13 23:00 | 71 | 70 |  |  | 43144.9583 | 91 | 91
2018-02-13 23:30 | 66 | 66 |  |  | 43144.9792 | 86 | 86
2018-02-14 | 65 | 65 |  |  | 43145 | 82 | 82
2018-02-14 00:30 | 63 | 62 |  |  | 43145.0208 | 77 | 77
2018-02-14 01:00 | 59 | 58 |  |  | 43145.0417 | 72 | 72
2018-02-14 01:30 | 59 | 58 |  |  | 43145.0625 | 71 | 71
2018-02-14 02:00 | 58 | 58 |  |  | 43145.0833 | 72 | 72
2018-02-14 02:30 | 57 | 56 |  |  | 43145.1042 | 70 | 70
2018-02-14 03:00 | 56 | 56 |  |  | 43145.125 | 70 | 70
2018-02-14 03:30 | 56 | 56 |  |  | 43145.1458 | 69 | 69
2018-02-14 04:00 | 57 | 56 |  |  | 43145.1667 | 68 | 68
2018-02-14 04:30 | 57 | 56 |  |  | 43145.1875 | 69 | 69
2018-02-14 05:00 | 57 | 57 |  |  | 43145.2083 | 71 | 71
2018-02-14 05:30 | 58 | 58 |  |  | 43145.2292 | 73 | 73
2018-02-14 06:00 | 60 | 59 |  |  | 43145.25 | 77 | 77
2018-02-14 06:30 | 66 | 66 |  |  | 43145.2708 | 88 | 88
2018-02-14 07:00 | 73 | 73 |  |  | 43145.2917 | 98 | 97
2018-02-14 07:30 | 82 | 82 |  |  | 43145.3125 | 108 | 108
2018-02-14 08:00 | 87 | 87 |  |  | 43145.3333 | 115 | 114
2018-02-14 08:30 | 89 | 88 |  |  | 43145.3542 | 117 | 117
2018-02-14 09:00 | 91 | 90 |  |  | 43145.375 | 120 | 120
2018-02-14 09:30 | 94 | 93 |  |  | 43145.3958 | 122 | 122
2018-02-14 10:00 | 96 | 95 |  |  | 43145.4167 | 124 | 124
2018-02-14 10:30 | 97 | 96 |  |  | 43145.4375 | 126 | 126
2018-02-14 11:00 | 99 | 98 |  |  | 43145.4583 | 128 | 128
2018-02-14 11:30 | 99 | 97 |  |  | 43145.4792 | 130 | 130
2018-02-14 12:00 | 102 | 100 |  |  | 43145.5 | 133 | 133
2018-02-14 12:30 | 104 | 102 |  |  | 43145.5208 | 133 | 133
2018-02-14 13:00 | 110 | 107 |  |  | 43145.5417 | 139 | 139
2018-02-14 13:30 | 113 | 111 |  |  | 43145.5625 | 143 | 143
2018-02-14 14:00 | 112 | 109 |  |  | 43145.5833 | 145 | 145
2018-02-14 14:30 | 110 | 107 |  |  | 43145.6042 | 145 | 145
2018-02-14 15:00 | 110 | 106 |  |  | 43145.625 | 145 | 144
2018-02-14 15:30 | 111 | 107 |  |  | 43145.6458 | 145 | 144
2018-02-14 16:00 | 111 | 109 |  |  | 43145.6667 | 147 | 146
2018-02-14 16:30 | 115 | 112 |  |  | 43145.6875 | 149 | 148
2018-02-14 17:00 | 115 | 113 |  |  | 43145.7083 | 152 | 151
2018-02-14 17:30 | 114 | 110 |  |  | 43145.7292 | 150 | 149
2018-02-14 18:00 | 111 | 107 |  |  | 43145.75 | 144 | 143
2018-02-14 18:30 | 108 | 105 |  |  | 43145.7708 | 136 | 136
2018-02-14 19:00 | 112 | 107 |  |  | 43145.7917 | 138 | 138
2018-02-14 19:30 | 112 | 105 |  |  | 43145.8125 | 138 | 138
2018-02-14 20:00 | 108 | 104 |  |  | 43145.8333 | 137 | 136
2018-02-14 20:30 | 108 | 105 |  |  | 43145.8542 | 136 | 135
2018-02-14 21:00 | 109 | 106 |  |  | 43145.875 | 138 | 138
2018-02-14 21:30 | 104 | 101 |  |  | 43145.8958 | 131 | 130
2018-02-14 22:00 | 100 | 98 |  |  | 43145.9167 | 128 | 126
2018-02-14 22:30 | 89 | 87 |  |  | 43145.9375 | 115 | 114
2018-02-14 23:00 | 79 | 79 |  |  | 43145.9583 | 102 | 102
2018-02-14 23:30 | 75 | 75 |  |  | 43145.9792 | 98 | 98
2018-02-15 | 73 | 73 |  |  | 43146 | 96 | 96
2018-02-15 00:30 | 69 | 69 |  |  | 43146.0208 | 90 | 90
2018-02-15 01:00 | 68 | 68 |  |  | 43146.0417 | 85 | 85
2018-02-15 01:30 | 65 | 65 |  |  | 43146.0625 | 82 | 82
2018-02-15 02:00 | 68 | 67 |  |  | 43146.0833 | 86 | 86
2018-02-15 02:30 | 67 | 66 |  |  | 43146.1042 | 83 | 83
2018-02-15 03:00 | 64 | 63 |  |  | 43146.125 | 79 | 79
2018-02-15 03:30 | 61 | 60 |  |  | 43146.1458 | 75 | 75
2018-02-15 04:00 | 60 | 58 |  |  | 43146.1667 | 72 | 72
2018-02-15 04:30 | 59 | 58 |  |  | 43146.1875 | 73 | 73
2018-02-15 05:00 | 62 | 61 |  |  | 43146.2083 | 76 | 76
2018-02-15 05:30 | 64 | 63 |  |  | 43146.2292 | 79 | 79
2018-02-15 06:00 | 66 | 66 |  |  | 43146.25 | 84 | 84
2018-02-15 06:30 | 73 | 72 |  |  | 43146.2708 | 94 | 94
2018-02-15 07:00 | 79 | 79 |  |  | 43146.2917 | 106 | 106
2018-02-15 07:30 | 89 | 89 |  |  | 43146.3125 | 119 | 119
2018-02-15 08:00 | 95 | 95 |  |  | 43146.3333 | 126 | 126
2018-02-15 08:30 | 97 | 96 |  |  | 43146.3542 | 129 | 129
2018-02-15 09:00 | 101 | 100 |  |  | 43146.375 | 133 | 132
2018-02-15 09:30 | 105 | 105 |  |  | 43146.3958 | 138 | 137
2018-02-15 10:00 | 106 | 106 |  |  | 43146.4167 | 140 | 139
2018-02-15 10:30 | 107 | 107 |  |  | 43146.4375 | 141 | 140
2018-02-15 11:00 | 108 | 107 |  |  | 43146.4583 | 145 | 143
2018-02-15 11:30 | 101 | 99 |  |  | 43146.4792 | 148 | 142
2018-02-15 12:00 | 106 | 102 |  |  | 43146.5 | 157 | 146
2018-02-15 12:30 | 110 | 104 |  |  | 43146.5208 | 163 | 149
2018-02-15 13:00 | 115 | 110 |  |  | 43146.5417 | 166 | 152
2018-02-15 13:30 | 119 | 114 |  |  | 43146.5625 | 172 | 157
2018-02-15 14:00 | 124 | 119 |  |  | 43146.5833 | 175 | 161
2018-02-15 14:30 | 124 | 120 |  |  | 43146.6042 | 175 | 161
2018-02-15 15:00 | 121 | 118 |  |  | 43146.625 | 172 | 158
2018-02-15 15:30 | 127 | 121 |  |  | 43146.6458 | 189 | 163
2018-02-15 16:00 | 126 | 122 |  |  | 43146.6667 | 194 | 164
2018-02-15 16:30 | 128 | 127 |  |  | 43146.6875 | 184 | 163
2018-02-15 17:00 | 127 | 125 |  |  | 43146.7083 | 175 | 162
2018-02-15 17:30 | 121 | 120 |  |  | 43146.7292 | 168 | 157
2018-02-15 18:00 | 122 | 120 |  |  | 43146.75 | 169 | 156
2018-02-15 18:30 | 118 | 115 |  |  | 43146.7708 | 161 | 144
2018-02-15 19:00 | 117 | 114 |  |  | 43146.7917 | 159 | 146
2018-02-15 19:30 | 116 | 114 |  |  | 43146.8125 | 159 | 144
2018-02-15 20:00 | 114 | 112 |  |  | 43146.8333 | 154 | 141
2018-02-15 20:30 | 115 | 112 |  |  | 43146.8542 | 155 | 142
2018-02-15 21:00 | 113 | 111 |  |  | 43146.875 | 156 | 141
2018-02-15 21:30 | 107 | 103 |  |  | 43146.8958 | 148 | 131
2018-02-15 22:00 | 104 | 103 |  |  | 43146.9167 | 135 | 126
2018-02-15 22:30 | 95 | 94 |  |  | 43146.9375 | 121 | 113
2018-02-15 23:00 | 91 | 89 |  |  | 43146.9583 | 109 | 107
2018-02-15 23:30 | 90 | 87 |  |  | 43146.9792 | 106 | 104
2018-02-16 | 88 | 85 |  |  | 43147 | 106 | 104
2018-02-16 00:30 | 82 | 79 |  |  | 43147.0208 | 99 | 97
2018-02-16 01:00 | 76 | 74 |  |  | 43147.0417 | 92 | 91
2018-02-16 01:30 | 73 | 70 |  |  | 43147.0625 | 89 | 88
2018-02-16 02:00 | 75 | 72 |  |  | 43147.0833 | 92 | 90
2018-02-16 02:30 | 73 | 71 |  |  | 43147.1042 | 89 | 88
2018-02-16 03:00 | 69 | 67 |  |  | 43147.125 | 84 | 83
2018-02-16 03:30 | 68 | 66 |  |  | 43147.1458 | 84 | 82
2018-02-16 04:00 | 67 | 64 |  |  | 43147.1667 | 82 | 81
2018-02-16 04:30 | 68 | 66 |  |  | 43147.1875 | 83 | 82
2018-02-16 05:00 | 71 | 69 |  |  | 43147.2083 | 86 | 85
2018-02-16 05:30 | 76 | 72 |  |  | 43147.2292 | 90 | 90
2018-02-16 06:00 | 80 | 74 |  |  | 43147.25 | 93 | 93
2018-02-16 06:30 | 85 | 81 |  |  | 43147.2708 | 104 | 103
2018-02-16 07:00 | 95 | 89 |  |  | 43147.2917 | 116 | 115
2018-02-16 07:30 | 104 | 100 |  |  | 43147.3125 | 129 | 129
2018-02-16 08:00 | 111 | 106 |  |  | 43147.3333 | 138 | 137
2018-02-16 08:30 | 114 | 109 |  |  | 43147.3542 | 143 | 142
2018-02-16 09:00 | 119 | 111 |  |  | 43147.375 | 147 | 144
2018-02-16 09:30 | 116 | 108 |  |  | 43147.3958 | 144 | 141
2018-02-16 10:00 | 115 | 108 |  |  | 43147.4167 | 144 | 142
2018-02-16 10:30 | 115 | 109 |  |  | 43147.4375 | 145 | 143
2018-02-16 11:00 | 116 | 112 |  |  | 43147.4583 | 146 | 145
2018-02-16 11:30 | 120 | 115 |  |  | 43147.4792 | 150 | 149
2018-02-16 12:00 | 121 | 117 |  |  | 43147.5 | 152 | 151
2018-02-16 12:30 | 121 | 117 |  |  | 43147.5208 | 150 | 149
2018-02-16 13:00 | 122 | 118 |  |  | 43147.5417 | 150 | 149
2018-02-16 13:30 | 115 | 112 |  |  | 43147.5625 | 146 | 145
2018-02-16 14:00 | 115 | 112 |  |  | 43147.5833 | 146 | 143
2018-02-16 14:30 | 114 | 109 |  |  | 43147.6042 | 148 | 145
2018-02-16 15:00 | 120 | 114 |  |  | 43147.625 | 155 | 150
2018-02-16 15:30 | 122 | 115 |  |  | 43147.6458 | 154 | 148
2018-02-16 16:00 | 123 | 116 |  |  | 43147.6667 | 156 | 149
2018-02-16 16:30 | 122 | 114 |  |  | 43147.6875 | 153 | 146
2018-02-16 17:00 | 120 | 114 |  |  | 43147.7083 | 150 | 145
2018-02-16 17:30 | 111 | 106 |  |  | 43147.7292 | 147 | 145
2018-02-16 18:00 | 107 | 101 |  |  | 43147.75 | 144 | 141
2018-02-16 18:30 | 105 | 97 |  |  | 43147.7708 | 137 | 134
2018-02-16 19:00 | 105 | 96 |  |  | 43147.7917 | 134 | 131
2018-02-16 19:30 | 102 | 94 |  |  | 43147.8125 | 128 | 124
2018-02-16 20:00 | 101 | 95 |  |  | 43147.8333 | 125 | 123
2018-02-16 20:30 | 98 | 91 |  |  | 43147.8542 | 120 | 117
2018-02-16 21:00 | 93 | 87 |  |  | 43147.875 | 114 | 112
2018-02-16 21:30 | 85 | 78 |  |  | 43147.8958 | 104 | 101
2018-02-16 22:00 | 82 | 76 |  |  | 43147.9167 | 100 | 99
2018-02-16 22:30 | 83 | 73 |  |  | 43147.9375 | 99 | 97
2018-02-16 23:00 | 84 | 74 |  |  | 43147.9583 | 100 | 98
2018-02-16 23:30 | 78 | 68 |  |  | 43147.9792 | 89 | 88
2018-02-17 | 75 | 61 |  |  | 43148 | 82 | 81
2018-02-17 00:30 | 76 | 57 |  |  | 43148.0208 | 78 | 76
2018-02-17 01:00 | 75 | 55 |  |  | 43148.0417 | 76 | 74
2018-02-17 01:30 | 75 | 55 |  |  | 43148.0625 | 74 | 72
2018-02-17 02:00 | 68 | 56 |  |  | 43148.0833 | 71 | 71
2018-02-17 02:30 | 65 | 54 |  |  | 43148.1042 | 71 | 70
2018-02-17 03:00 | 64 | 54 |  |  | 43148.125 | 70 | 70
2018-02-17 03:30 | 65 | 54 |  |  | 43148.1458 | 71 | 70
2018-02-17 04:00 | 66 | 54 |  |  | 43148.1667 | 69 | 69
2018-02-17 04:30 | 65 | 54 |  |  | 43148.1875 | 70 | 70
2018-02-17 05:00 | 65 | 54 |  |  | 43148.2083 | 69 | 69
2018-02-17 05:30 | 65 | 54 |  |  | 43148.2292 | 68 | 68
2018-02-17 06:00 | 62 | 52 |  |  | 43148.25 | 67 | 67
2018-02-17 06:30 | 64 | 54 |  |  | 43148.2708 | 72 | 72
2018-02-17 07:00 | 65 | 57 |  |  | 43148.2917 | 76 | 76
2018-02-17 07:30 | 67 | 60 |  |  | 43148.3125 | 79 | 79
2018-02-17 08:00 | 67 | 64 |  |  | 43148.3333 | 85 | 85
2018-02-17 08:30 | 68 | 67 |  |  | 43148.3542 | 88 | 87
2018-02-17 09:00 | 70 | 69 |  |  | 43148.375 | 92 | 90
2018-02-17 09:30 | 71 | 71 |  |  | 43148.3958 | 94 | 93
2018-02-17 10:00 | 72 | 71 |  |  | 43148.4167 | 94 | 91
2018-02-17 10:30 | 72 | 71 |  |  | 43148.4375 | 95 | 92
2018-02-17 11:00 | 76 | 75 |  |  | 43148.4583 | 96 | 93
2018-02-17 11:30 | 76 | 75 |  |  | 43148.4792 | 97 | 93
2018-02-17 12:00 | 74 | 73 |  |  | 43148.5 | 96 | 92
2018-02-17 12:30 | 73 | 72 |  |  | 43148.5208 | 95 | 90
2018-02-17 13:00 | 75 | 74 |  |  | 43148.5417 | 97 | 93
2018-02-17 13:30 | 77 | 76 |  |  | 43148.5625 | 97 | 93
2018-02-17 14:00 | 77 | 76 |  |  | 43148.5833 | 97 | 93
2018-02-17 14:30 | 78 | 76 |  |  | 43148.6042 | 99 | 94
2018-02-17 15:00 | 80 | 78 |  |  | 43148.625 | 101 | 96
2018-02-17 15:30 | 86 | 85 |  |  | 43148.6458 | 106 | 102
2018-02-17 16:00 | 90 | 89 |  |  | 43148.6667 | 111 | 107
2018-02-17 16:30 | 92 | 91 |  |  | 43148.6875 | 113 | 108
2018-02-17 17:00 | 91 | 89 |  |  | 43148.7083 | 113 | 108
2018-02-17 17:30 | 92 | 91 |  |  | 43148.7292 | 112 | 107
2018-02-17 18:00 | 92 | 90 |  |  | 43148.75 | 113 | 107
2018-02-17 18:30 | 93 | 90 |  |  | 43148.7708 | 114 | 107
2018-02-17 19:00 | 94 | 91 |  |  | 43148.7917 | 117 | 111
2018-02-17 19:30 | 89 | 87 |  |  | 43148.8125 | 112 | 106
2018-02-17 20:00 | 86 | 84 |  |  | 43148.8333 | 110 | 103
2018-02-17 20:30 | 83 | 82 |  |  | 43148.8542 | 109 | 101
2018-02-17 21:00 | 77 | 77 |  |  | 43148.875 | 105 | 96
2018-02-17 21:30 | 73 | 73 |  |  | 43148.8958 | 102 | 91
2018-02-17 22:00 | 71 | 71 |  |  | 43148.9167 | 100 | 88
2018-02-17 22:30 | 74 | 73 |  |  | 43148.9375 | 103 | 91
2018-02-17 23:00 | 74 | 74 |  |  | 43148.9583 | 100 | 91
2018-02-17 23:30 | 68 | 68 |  |  | 43148.9792 | 93 | 83
2018-02-18 | 63 | 62 |  |  | 43149 | 88 | 77
2018-02-18 00:30 | 59 | 58 |  |  | 43149.0208 | 85 | 73
2018-02-18 01:00 | 56 | 56 |  |  | 43149.0417 | 81 | 71
2018-02-18 01:30 | 54 | 53 |  |  | 43149.0625 | 76 | 68
2018-02-18 02:00 | 53 | 53 |  |  | 43149.0833 | 74 | 67
2018-02-18 02:30 | 53 | 50 |  |  | 43149.1042 | 75 | 65
2018-02-18 03:00 | 52 | 49 |  |  | 43149.125 | 74 | 63
2018-02-18 03:30 | 52 | 49 |  |  | 43149.1458 | 74 | 63
2018-02-18 04:00 | 51 | 48 |  |  | 43149.1667 | 73 | 62
2018-02-18 04:30 | 51 | 48 |  |  | 43149.1875 | 72 | 61
2018-02-18 05:00 | 50 | 47 |  |  | 43149.2083 | 72 | 61
2018-02-18 05:30 | 49 | 46 |  |  | 43149.2292 | 72 | 60
2018-02-18 06:00 | 48 | 45 |  |  | 43149.25 | 71 | 60
2018-02-18 06:30 | 49 | 45 |  |  | 43149.2708 | 71 | 60
2018-02-18 07:00 | 48 | 46 |  |  | 43149.2917 | 72 | 62
2018-02-18 07:30 | 48 | 47 |  |  | 43149.3125 | 72 | 63
2018-02-18 08:00 | 49 | 48 |  |  | 43149.3333 | 73 | 66
2018-02-18 08:30 | 52 | 51 |  |  | 43149.3542 | 75 | 69
2018-02-18 09:00 | 56 | 55 |  |  | 43149.375 | 81 | 74
2018-02-18 09:30 | 59 | 58 |  |  | 43149.3958 | 86 | 76
2018-02-18 10:00 | 63 | 61 |  |  | 43149.4167 | 89 | 77
2018-02-18 10:30 | 62 | 60 |  |  | 43149.4375 | 89 | 78
2018-02-18 11:00 | 62 | 60 |  |  | 43149.4583 | 90 | 78
2018-02-18 11:30 | 64 | 62 |  |  | 43149.4792 | 90 | 79
2018-02-18 12:00 | 67 | 66 |  |  | 43149.5 | 92 | 80
2018-02-18 12:30 | 66 | 65 |  |  | 43149.5208 | 92 | 81
2018-02-18 13:00 | 66 | 66 |  |  | 43149.5417 | 94 | 83
2018-02-18 13:30 | 69 | 68 |  |  | 43149.5625 | 99 | 86
2018-02-18 14:00 | 72 | 71 |  |  | 43149.5833 | 102 | 89
2018-02-18 14:30 | 73 | 73 |  |  | 43149.6042 | 102 | 90
2018-02-18 15:00 | 77 | 75 |  |  | 43149.625 | 101 | 91
2018-02-18 15:30 | 83 | 80 |  |  | 43149.6458 | 104 | 95
2018-02-18 16:00 | 89 | 86 |  |  | 43149.6667 | 109 | 101
2018-02-18 16:30 | 91 | 88 |  |  | 43149.6875 | 112 | 104
2018-02-18 17:00 | 94 | 91 |  |  | 43149.7083 | 115 | 107
2018-02-18 17:30 | 93 | 90 |  |  | 43149.7292 | 115 | 106
2018-02-18 18:00 | 92 | 89 |  |  | 43149.75 | 114 | 105
2018-02-18 18:30 | 92 | 89 |  |  | 43149.7708 | 113 | 106
2018-02-18 19:00 | 93 | 91 |  |  | 43149.7917 | 115 | 111
2018-02-18 19:30 | 90 | 88 |  |  | 43149.8125 | 111 | 107
2018-02-18 20:00 | 88 | 86 |  |  | 43149.8333 | 110 | 106
2018-02-18 20:30 | 86 | 84 |  |  | 43149.8542 | 108 | 104
2018-02-18 21:00 | 80 | 79 |  |  | 43149.875 | 102 | 98
2018-02-18 21:30 | 73 | 72 |  |  | 43149.8958 | 92 | 90
2018-02-18 22:00 | 71 | 70 |  |  | 43149.9167 | 91 | 89
2018-02-18 22:30 | 70 | 70 |  |  | 43149.9375 | 90 | 89
2018-02-18 23:00 | 70 | 70 |  |  | 43149.9583 | 91 | 90
2018-02-18 23:30 | 66 | 64 |  |  | 43149.9792 | 83 | 82
2018-02-19 | 60 | 58 |  |  | 43150 | 77 | 75
2018-02-19 00:30 | 57 | 54 |  |  | 43150.0208 | 72 | 70
2018-02-19 01:00 | 53 | 50 |  |  | 43150.0417 | 67 | 66
2018-02-19 01:30 | 53 | 48 |  |  | 43150.0625 | 66 | 64
2018-02-19 02:00 | 51 | 47 |  |  | 43150.0833 | 64 | 62
2018-02-19 02:30 | 51 | 46 |  |  | 43150.1042 | 63 | 61
2018-02-19 03:00 | 51 | 46 |  |  | 43150.125 | 64 | 61
2018-02-19 03:30 | 51 | 47 |  |  | 43150.1458 | 64 | 62
2018-02-19 04:00 | 52 | 47 |  |  | 43150.1667 | 64 | 62
2018-02-19 04:30 | 52 | 47 |  |  | 43150.1875 | 64 | 62
2018-02-19 05:00 | 53 | 49 |  |  | 43150.2083 | 66 | 64
2018-02-19 05:30 | 56 | 53 |  |  | 43150.2292 | 69 | 68
2018-02-19 06:00 | 62 | 59 |  |  | 43150.25 | 77 | 76
2018-02-19 06:30 | 67 | 66 |  |  | 43150.2708 | 87 | 87
2018-02-19 07:00 | 74 | 74 |  |  | 43150.2917 | 99 | 99
2018-02-19 07:30 | 79 | 79 |  |  | 43150.3125 | 107 | 106
2018-02-19 08:00 | 81 | 81 |  |  | 43150.3333 | 110 | 110
2018-02-19 08:30 | 82 | 82 |  |  | 43150.3542 | 112 | 111
2018-02-19 09:00 | 82 | 82 |  |  | 43150.375 | 112 | 112
2018-02-19 09:30 | 84 | 84 |  |  | 43150.3958 | 113 | 113
2018-02-19 10:00 | 85 | 85 |  |  | 43150.4167 | 116 | 116
2018-02-19 10:30 | 85 | 85 |  |  | 43150.4375 | 116 | 116
2018-02-19 11:00 | 86 | 86 |  |  | 43150.4583 | 116 | 115
2018-02-19 11:30 | 86 | 86 |  |  | 43150.4792 | 117 | 116
2018-02-19 12:00 | 86 | 86 |  |  | 43150.5 | 116 | 116
2018-02-19 12:30 | 86 | 86 |  |  | 43150.5208 | 116 | 116
2018-02-19 13:00 | 87 | 87 |  |  | 43150.5417 | 116 | 116
2018-02-19 13:30 | 91 | 91 |  |  | 43150.5625 | 120 | 120
2018-02-19 14:00 | 95 | 95 |  |  | 43150.5833 | 123 | 122
2018-02-19 14:30 | 98 | 98 |  |  | 43150.6042 | 126 | 126
2018-02-19 15:00 | 101 | 101 |  |  | 43150.625 | 129 | 128
2018-02-19 15:30 | 102 | 102 |  |  | 43150.6458 | 129 | 129
2018-02-19 16:00 | 104 | 104 |  |  | 43150.6667 | 131 | 130
2018-02-19 16:30 | 106 | 106 |  |  | 43150.6875 | 134 | 131
2018-02-19 17:00 | 109 | 109 |  |  | 43150.7083 | 136 | 133
2018-02-19 17:30 | 110 | 110 |  |  | 43150.7292 | 135 | 133
2018-02-19 18:00 | 107 | 107 |  |  | 43150.75 | 130 | 129
2018-02-19 18:30 | 104 | 104 |  |  | 43150.7708 | 125 | 124
2018-02-19 19:00 | 104 | 104 |  |  | 43150.7917 | 126 | 125
2018-02-19 19:30 | 102 | 102 |  |  | 43150.8125 | 124 | 123
2018-02-19 20:00 | 100 | 100 |  |  | 43150.8333 | 120 | 120
2018-02-19 20:30 | 99 | 99 |  |  | 43150.8542 | 118 | 117
2018-02-19 21:00 | 96 | 96 |  |  | 43150.875 | 113 | 113
2018-02-19 21:30 | 92 | 92 |  |  | 43150.8958 | 110 | 110
2018-02-19 22:00 | 90 | 90 |  |  | 43150.9167 | 108 | 107
2018-02-19 22:30 | 85 | 84 |  |  | 43150.9375 | 101 | 101
2018-02-19 23:00 | 79 | 79 |  |  | 43150.9583 | 95 | 95
2018-02-19 23:30 | 71 | 71 |  |  | 43150.9792 | 88 | 88
2018-02-20 | 64 | 64 |  |  | 43151 | 80 | 80
2018-02-20 00:30 | 61 | 61 |  |  | 43151.0208 | 75 | 75
2018-02-20 01:00 | 57 | 57 |  |  | 43151.0417 | 72 | 72
2018-02-20 01:30 | 56 | 55 |  |  | 43151.0625 | 70 | 70
2018-02-20 02:00 | 54 | 54 |  |  | 43151.0833 | 68 | 68
2018-02-20 02:30 | 52 | 52 |  |  | 43151.1042 | 67 | 66
2018-02-20 03:00 | 53 | 53 |  |  | 43151.125 | 66 | 66
2018-02-20 03:30 | 52 | 52 |  |  | 43151.1458 | 66 | 66
2018-02-20 04:00 | 53 | 52 |  |  | 43151.1667 | 66 | 66
2018-02-20 04:30 | 53 | 53 |  |  | 43151.1875 | 68 | 68
2018-02-20 05:00 | 56 | 56 |  |  | 43151.2083 | 71 | 70
2018-02-20 05:30 | 59 | 58 |  |  | 43151.2292 | 76 | 76
2018-02-20 06:00 | 62 | 62 |  |  | 43151.25 | 81 | 81
2018-02-20 06:30 | 69 | 69 |  |  | 43151.2708 | 93 | 92
2018-02-20 07:00 | 75 | 75 |  |  | 43151.2917 | 101 | 101
2018-02-20 07:30 | 81 | 81 |  |  | 43151.3125 | 113 | 112
2018-02-20 08:00 | 87 | 87 |  |  | 43151.3333 | 119 | 118
2018-02-20 08:30 | 87 | 86 |  |  | 43151.3542 | 122 | 118
2018-02-20 09:00 | 90 | 89 |  |  | 43151.375 | 125 | 122
2018-02-20 09:30 | 90 | 89 |  |  | 43151.3958 | 124 | 121
2018-02-20 10:00 | 92 | 91 |  |  | 43151.4167 | 124 | 121
2018-02-20 10:30 | 93 | 93 |  |  | 43151.4375 | 124 | 121
2018-02-20 11:00 | 93 | 93 |  |  | 43151.4583 | 124 | 121
2018-02-20 11:30 | 95 | 95 |  |  | 43151.4792 | 127 | 124
2018-02-20 12:00 | 93 | 93 |  |  | 43151.5 | 121 | 118
2018-02-20 12:30 | 90 | 90 |  |  | 43151.5208 | 119 | 116
2018-02-20 13:00 | 93 | 92 |  |  | 43151.5417 | 120 | 116
2018-02-20 13:30 | 91 | 91 |  |  | 43151.5625 | 120 | 117
2018-02-20 14:00 | 93 | 93 |  |  | 43151.5833 | 122 | 119
2018-02-20 14:30 | 92 | 92 |  |  | 43151.6042 | 121 | 118
2018-02-20 15:00 | 90 | 90 |  |  | 43151.625 | 120 | 116
2018-02-20 15:30 | 93 | 93 |  |  | 43151.6458 | 120 | 116
2018-02-20 16:00 | 93 | 93 |  |  | 43151.6667 | 123 | 118
2018-02-20 16:30 | 94 | 93 |  |  | 43151.6875 | 123 | 118
2018-02-20 17:00 | 97 | 97 |  |  | 43151.7083 | 124 | 119
2018-02-20 17:30 | 96 | 96 |  |  | 43151.7292 | 121 | 117
2018-02-20 18:00 | 92 | 92 |  |  | 43151.75 | 116 | 113
2018-02-20 18:30 | 91 | 91 |  |  | 43151.7708 | 111 | 110
2018-02-20 19:00 | 96 | 96 |  |  | 43151.7917 | 116 | 115
2018-02-20 19:30 | 94 | 94 |  |  | 43151.8125 | 113 | 112
2018-02-20 20:00 | 92 | 92 |  |  | 43151.8333 | 110 | 109
2018-02-20 20:30 | 90 | 90 |  |  | 43151.8542 | 107 | 106
2018-02-20 21:00 | 84 | 84 |  |  | 43151.875 | 99 | 98
2018-02-20 21:30 | 78 | 78 |  |  | 43151.8958 | 94 | 92
2018-02-20 22:00 | 77 | 77 |  |  | 43151.9167 | 94 | 92
2018-02-20 22:30 | 70 | 69 |  |  | 43151.9375 | 88 | 86
2018-02-20 23:00 | 68 | 67 |  |  | 43151.9583 | 84 | 82
2018-02-20 23:30 | 65 | 64 |  |  | 43151.9792 | 80 | 80
2018-02-21 | 61 | 61 |  |  | 43152 | 76 | 75
2018-02-21 00:30 | 56 | 56 |  |  | 43152.0208 | 70 | 70
2018-02-21 01:00 | 53 | 53 |  |  | 43152.0417 | 66 | 66
2018-02-21 01:30 | 51 | 51 |  |  | 43152.0625 | 64 | 64
2018-02-21 02:00 | 50 | 50 |  |  | 43152.0833 | 63 | 62
2018-02-21 02:30 | 49 | 49 |  |  | 43152.1042 | 63 | 62
2018-02-21 03:00 | 50 | 50 |  |  | 43152.125 | 64 | 64
2018-02-21 03:30 | 51 | 51 |  |  | 43152.1458 | 65 | 64
2018-02-21 04:00 | 52 | 52 |  |  | 43152.1667 | 66 | 65
2018-02-21 04:30 | 53 | 53 |  |  | 43152.1875 | 66 | 65
2018-02-21 05:00 | 53 | 53 |  |  | 43152.2083 | 66 | 66
2018-02-21 05:30 | 57 | 57 |  |  | 43152.2292 | 70 | 70
2018-02-21 06:00 | 62 | 62 |  |  | 43152.25 | 78 | 78
2018-02-21 06:30 | 69 | 69 |  |  | 43152.2708 | 89 | 88
2018-02-21 07:00 | 75 | 75 |  |  | 43152.2917 | 98 | 97
2018-02-21 07:30 | 83 | 83 |  |  | 43152.3125 | 108 | 108
2018-02-21 08:00 | 87 | 87 |  |  | 43152.3333 | 116 | 115
2018-02-21 08:30 | 89 | 89 |  |  | 43152.3542 | 116 | 115
2018-02-21 09:00 | 89 | 89 |  |  | 43152.375 | 120 | 118
2018-02-21 09:30 | 91 | 90 |  |  | 43152.3958 | 120 | 118
2018-02-21 10:00 | 88 | 88 |  |  | 43152.4167 | 117 | 115
2018-02-21 10:30 | 88 | 87 |  |  | 43152.4375 | 117 | 115
2018-02-21 11:00 | 86 | 86 |  |  | 43152.4583 | 116 | 114
2018-02-21 11:30 | 86 | 85 |  |  | 43152.4792 | 115 | 113
2018-02-21 12:00 | 87 | 87 |  |  | 43152.5 | 114 | 112
2018-02-21 12:30 | 88 | 87 |  |  | 43152.5208 | 116 | 114
2018-02-21 13:00 | 87 | 86 |  |  | 43152.5417 | 114 | 112
2018-02-21 13:30 | 83 | 82 |  |  | 43152.5625 | 114 | 112
2018-02-21 14:00 | 87 | 86 |  |  | 43152.5833 | 113 | 110
2018-02-21 14:30 | 85 | 85 |  |  | 43152.6042 | 111 | 109
2018-02-21 15:00 | 83 | 82 |  |  | 43152.625 | 108 | 105
2018-02-21 15:30 | 80 | 79 |  |  | 43152.6458 | 105 | 102
2018-02-21 16:00 | 83 | 82 |  |  | 43152.6667 | 107 | 104
2018-02-21 16:30 | 85 | 84 |  |  | 43152.6875 | 109 | 106
2018-02-21 17:00 | 86 | 86 |  |  | 43152.7083 | 107 | 105
2018-02-21 17:30 | 85 | 85 |  |  | 43152.7292 | 104 | 102
2018-02-21 18:00 | 84 | 83 |  |  | 43152.75 | 102 | 100
2018-02-21 18:30 | 81 | 81 |  |  | 43152.7708 | 98 | 97
2018-02-21 19:00 | 84 | 84 |  |  | 43152.7917 | 101 | 100
2018-02-21 19:30 | 83 | 83 |  |  | 43152.8125 | 100 | 99
2018-02-21 20:00 | 83 | 83 |  |  | 43152.8333 | 98 | 98
2018-02-21 20:30 | 81 | 81 |  |  | 43152.8542 | 95 | 95
2018-02-21 21:00 | 78 | 78 |  |  | 43152.875 | 90 | 90
2018-02-21 21:30 | 74 | 74 |  |  | 43152.8958 | 87 | 87
2018-02-21 22:00 | 73 | 73 |  |  | 43152.9167 | 88 | 88
2018-02-21 22:30 | 68 | 68 |  |  | 43152.9375 | 82 | 82
2018-02-21 23:00 | 64 | 64 |  |  | 43152.9583 | 76 | 76
2018-02-21 23:30 | 58 | 58 |  |  | 43152.9792 | 72 | 72
2018-02-22 | 53 | 53 |  |  | 43153 | 67 | 67
2018-02-22 00:30 | 50 | 50 |  |  | 43153.0208 | 63 | 63
2018-02-22 01:00 | 45 | 45 |  |  | 43153.0417 | 57 | 57
2018-02-22 01:30 | 44 | 44 |  |  | 43153.0625 | 56 | 56
2018-02-22 02:00 | 42 | 42 |  |  | 43153.0833 | 54 | 54
2018-02-22 02:30 | 43 | 43 |  |  | 43153.1042 | 55 | 55
2018-02-22 03:00 | 44 | 44 |  |  | 43153.125 | 56 | 56
2018-02-22 03:30 | 45 | 44 |  |  | 43153.1458 | 56 | 56
2018-02-22 04:00 | 45 | 45 |  |  | 43153.1667 | 57 | 57
2018-02-22 04:30 | 46 | 46 |  |  | 43153.1875 | 58 | 58
2018-02-22 05:00 | 48 | 48 |  |  | 43153.2083 | 60 | 60
2018-02-22 05:30 | 52 | 52 |  |  | 43153.2292 | 65 | 65
2018-02-22 06:00 | 56 | 56 |  |  | 43153.25 | 72 | 72
2018-02-22 06:30 | 63 | 63 |  |  | 43153.2708 | 82 | 82
2018-02-22 07:00 | 70 | 70 |  |  | 43153.2917 | 90 | 90
2018-02-22 07:30 | 77 | 77 |  |  | 43153.3125 | 101 | 100
2018-02-22 08:00 | 77 | 77 |  |  | 43153.3333 | 102 | 102
2018-02-22 08:30 | 77 | 77 |  |  | 43153.3542 | 103 | 103
2018-02-22 09:00 | 80 | 80 |  |  | 43153.375 | 107 | 107
2018-02-22 09:30 | 83 | 83 |  |  | 43153.3958 | 108 | 108
2018-02-22 10:00 | 82 | 82 |  |  | 43153.4167 | 110 | 110
2018-02-22 10:30 | 83 | 83 |  |  | 43153.4375 | 109 | 109
2018-02-22 11:00 | 86 | 86 |  |  | 43153.4583 | 111 | 111
2018-02-22 11:30 | 83 | 83 |  |  | 43153.4792 | 107 | 107
2018-02-22 12:00 | 83 | 83 |  |  | 43153.5 | 107 | 106
2018-02-22 12:30 | 80 | 80 |  |  | 43153.5208 | 107 | 107
2018-02-22 13:00 | 79 | 79 |  |  | 43153.5417 | 106 | 105
2018-02-22 13:30 | 80 | 80 |  |  | 43153.5625 | 106 | 106
2018-02-22 14:00 | 80 | 80 |  |  | 43153.5833 | 104 | 104
2018-02-22 14:30 | 80 | 80 |  |  | 43153.6042 | 103 | 102
2018-02-22 15:00 | 77 | 77 |  |  | 43153.625 | 99 | 98
2018-02-22 15:30 | 78 | 78 |  |  | 43153.6458 | 101 | 100
2018-02-22 16:00 | 81 | 81 |  |  | 43153.6667 | 103 | 102
2018-02-22 16:30 | 82 | 82 |  |  | 43153.6875 | 102 | 101
2018-02-22 17:00 | 83 | 83 |  |  | 43153.7083 | 104 | 102
2018-02-22 17:30 | 83 | 83 |  |  | 43153.7292 | 102 | 100
2018-02-22 18:00 | 81 | 81 |  |  | 43153.75 | 99 | 99
2018-02-22 18:30 | 81 | 81 |  |  | 43153.7708 | 98 | 98
2018-02-22 19:00 | 84 | 84 |  |  | 43153.7917 | 101 | 100
2018-02-22 19:30 | 84 | 84 |  |  | 43153.8125 | 99 | 98
2018-02-22 20:00 | 85 | 85 |  |  | 43153.8333 | 100 | 99
2018-02-22 20:30 | 86 | 86 |  |  | 43153.8542 | 101 | 100
2018-02-22 21:00 | 82 | 82 |  |  | 43153.875 | 96 | 96
2018-02-22 21:30 | 76 | 76 |  |  | 43153.8958 | 90 | 89
2018-02-22 22:00 | 75 | 75 |  |  | 43153.9167 | 89 | 89
2018-02-22 22:30 | 70 | 70 |  |  | 43153.9375 | 85 | 85
2018-02-22 23:00 | 67 | 67 |  |  | 43153.9583 | 79 | 79
2018-02-22 23:30 | 63 | 63 |  |  | 43153.9792 | 75 | 75
2018-02-23 | 59 | 59 |  |  | 43154 | 70 | 70
2018-02-23 00:30 | 55 | 55 |  |  | 43154.0208 | 68 | 68
2018-02-23 01:00 | 54 | 54 |  |  | 43154.0417 | 66 | 66
2018-02-23 01:30 | 52 | 52 |  |  | 43154.0625 | 63 | 63
2018-02-23 02:00 | 50 | 50 |  |  | 43154.0833 | 62 | 62
2018-02-23 02:30 | 49 | 49 |  |  | 43154.1042 | 61 | 61
2018-02-23 03:00 | 47 | 47 |  |  | 43154.125 | 59 | 58
2018-02-23 03:30 | 49 | 49 |  |  | 43154.1458 | 60 | 59
2018-02-23 04:00 | 50 | 50 |  |  | 43154.1667 | 61 | 60
2018-02-23 04:30 | 50 | 50 |  |  | 43154.1875 | 62 | 61
2018-02-23 05:00 | 53 | 53 |  |  | 43154.2083 | 66 | 65
2018-02-23 05:30 | 58 | 58 |  |  | 43154.2292 | 70 | 70
2018-02-23 06:00 | 62 | 62 |  |  | 43154.25 | 76 | 76
2018-02-23 06:30 | 69 | 69 |  |  | 43154.2708 | 87 | 87
2018-02-23 07:00 | 76 | 76 |  |  | 43154.2917 | 96 | 96
2018-02-23 07:30 | 84 | 84 |  |  | 43154.3125 | 108 | 108
2018-02-23 08:00 | 90 | 90 |  |  | 43154.3333 | 114 | 114
2018-02-23 08:30 | 90 | 90 |  |  | 43154.3542 | 116 | 116
2018-02-23 09:00 | 89 | 89 |  |  | 43154.375 | 117 | 117
2018-02-23 09:30 | 90 | 89 |  |  | 43154.3958 | 116 | 116
2018-02-23 10:00 | 93 | 93 |  |  | 43154.4167 | 119 | 119
2018-02-23 10:30 | 94 | 94 |  |  | 43154.4375 | 121 | 121
2018-02-23 11:00 | 94 | 94 |  |  | 43154.4583 | 120 | 120
2018-02-23 11:30 | 94 | 94 |  |  | 43154.4792 | 122 | 122
2018-02-23 12:00 | 93 | 93 |  |  | 43154.5 | 121 | 121
2018-02-23 12:30 | 94 | 94 |  |  | 43154.5208 | 121 | 121
2018-02-23 13:00 | 93 | 93 |  |  | 43154.5417 | 117 | 117
2018-02-23 13:30 | 93 | 93 |  |  | 43154.5625 | 115 | 115
2018-02-23 14:00 | 92 | 92 |  |  | 43154.5833 | 116 | 115
2018-02-23 14:30 | 92 | 92 |  |  | 43154.6042 | 116 | 116
2018-02-23 15:00 | 92 | 92 |  |  | 43154.625 | 116 | 116
2018-02-23 15:30 | 90 | 90 |  |  | 43154.6458 | 112 | 112
2018-02-23 16:00 | 89 | 89 |  |  | 43154.6667 | 111 | 111
2018-02-23 16:30 | 88 | 88 |  |  | 43154.6875 | 111 | 110
2018-02-23 17:00 | 89 | 89 |  |  | 43154.7083 | 112 | 112
2018-02-23 17:30 | 89 | 89 |  |  | 43154.7292 | 110 | 110
2018-02-23 18:00 | 87 | 87 |  |  | 43154.75 | 106 | 106
2018-02-23 18:30 | 84 | 84 |  |  | 43154.7708 | 103 | 103
2018-02-23 19:00 | 86 | 86 |  |  | 43154.7917 | 105 | 104
2018-02-23 19:30 | 83 | 83 |  |  | 43154.8125 | 100 | 99
2018-02-23 20:00 | 81 | 80 |  |  | 43154.8333 | 98 | 98
2018-02-23 20:30 | 81 | 80 |  |  | 43154.8542 | 98 | 97
2018-02-23 21:00 | 77 | 77 |  |  | 43154.875 | 94 | 93
2018-02-23 21:30 | 72 | 72 |  |  | 43154.8958 | 89 | 88
2018-02-23 22:00 | 70 | 70 |  |  | 43154.9167 | 87 | 86
2018-02-23 22:30 | 67 | 67 |  |  | 43154.9375 | 83 | 83
2018-02-23 23:00 | 65 | 65 |  |  | 43154.9583 | 80 | 80
2018-02-23 23:30 | 62 | 62 |  |  | 43154.9792 | 78 | 78
2018-02-24 | 58 | 58 |  |  | 43155 | 73 | 73
2018-02-24 00:30 | 54 | 54 |  |  | 43155.0208 | 69 | 69
2018-02-24 01:00 | 53 | 53 |  |  | 43155.0417 | 67 | 67
2018-02-24 01:30 | 52 | 52 |  |  | 43155.0625 | 67 | 67
2018-02-24 02:00 | 53 | 53 |  |  | 43155.0833 | 67 | 66
2018-02-24 02:30 | 52 | 51 |  |  | 43155.1042 | 65 | 65
2018-02-24 03:00 | 50 | 49 |  |  | 43155.125 | 64 | 64
2018-02-24 03:30 | 50 | 49 |  |  | 43155.1458 | 65 | 64
2018-02-24 04:00 | 52 | 51 |  |  | 43155.1667 | 66 | 66
2018-02-24 04:30 | 52 | 51 |  |  | 43155.1875 | 67 | 66
2018-02-24 05:00 | 53 | 52 |  |  | 43155.2083 | 69 | 68
2018-02-24 05:30 | 53 | 53 |  |  | 43155.2292 | 69 | 68
2018-02-24 06:00 | 52 | 52 |  |  | 43155.25 | 69 | 68
2018-02-24 06:30 | 54 | 54 |  |  | 43155.2708 | 71 | 70
2018-02-24 07:00 | 54 | 53 |  |  | 43155.2917 | 71 | 70
2018-02-24 07:30 | 55 | 55 |  |  | 43155.3125 | 73 | 73
2018-02-24 08:00 | 72 | 72 |  |  | 43155.3333 | 107 | 107
2018-02-24 08:30 | 77 | 77 |  |  | 43155.3542 | 114 | 114
2018-02-24 09:00 | 82 | 82 |  |  | 43155.375 | 118 | 118
2018-02-24 09:30 | 87 | 87 |  |  | 43155.3958 | 126 | 126
2018-02-24 10:00 | 88 | 88 |  |  | 43155.4167 | 130 | 129
2018-02-24 10:30 | 90 | 90 |  |  | 43155.4375 | 133 | 133
2018-02-24 11:00 | 93 | 93 |  |  | 43155.4583 | 132 | 132
2018-02-24 11:30 | 92 | 92 |  |  | 43155.4792 | 125 | 125
2018-02-24 12:00 | 87 | 87 |  |  | 43155.5 | 118 | 118
2018-02-24 12:30 | 80 | 80 |  |  | 43155.5208 | 111 | 111
2018-02-24 13:00 | 69 | 69 |  |  | 43155.5417 | 94 | 94
2018-02-24 13:30 | 72 | 72 |  |  | 43155.5625 | 94 | 94
2018-02-24 14:00 | 70 | 70 |  |  | 43155.5833 | 84 | 84
2018-02-24 14:30 | 68 | 68 |  |  | 43155.6042 | 84 | 84
2018-02-24 15:00 | 71 | 71 |  |  | 43155.625 | 90 | 90
2018-02-24 15:30 | 70 | 70 |  |  | 43155.6458 | 90 | 90
2018-02-24 16:00 | 73 | 73 |  |  | 43155.6667 | 91 | 91
2018-02-24 16:30 | 73 | 73 |  |  | 43155.6875 | 92 | 92
2018-02-24 17:00 | 74 | 74 |  |  | 43155.7083 | 91 | 91
2018-02-24 17:30 | 74 | 74 |  |  | 43155.7292 | 91 | 91
2018-02-24 18:00 | 73 | 73 |  |  | 43155.75 | 91 | 91
2018-02-24 18:30 | 74 | 74 |  |  | 43155.7708 | 92 | 92
2018-02-24 19:00 | 75 | 75 |  |  | 43155.7917 | 94 | 94
2018-02-24 19:30 | 73 | 73 |  |  | 43155.8125 | 93 | 93
2018-02-24 20:00 | 73 | 73 |  |  | 43155.8333 | 92 | 92
2018-02-24 20:30 | 71 | 71 |  |  | 43155.8542 | 89 | 89
2018-02-24 21:00 | 69 | 69 |  |  | 43155.875 | 87 | 87
2018-02-24 21:30 | 69 | 69 |  |  | 43155.8958 | 87 | 87
2018-02-24 22:00 | 69 | 69 |  |  | 43155.9167 | 87 | 87
2018-02-24 22:30 | 69 | 69 |  |  | 43155.9375 | 86 | 86
2018-02-24 23:00 | 70 | 69 |  |  | 43155.9583 | 85 | 85
2018-02-24 23:30 | 67 | 67 |  |  | 43155.9792 | 82 | 82
2018-02-25 | 61 | 61 |  |  | 43156 | 77 | 77
2018-02-25 00:30 | 56 | 56 |  |  | 43156.0208 | 70 | 69
2018-02-25 01:00 | 53 | 53 |  |  | 43156.0417 | 67 | 67
2018-02-25 01:30 | 51 | 51 |  |  | 43156.0625 | 64 | 64
2018-02-25 02:00 | 52 | 52 |  |  | 43156.0833 | 64 | 64
2018-02-25 02:30 | 49 | 48 |  |  | 43156.1042 | 62 | 62
2018-02-25 03:00 | 47 | 47 |  |  | 43156.125 | 60 | 60
2018-02-25 03:30 | 46 | 46 |  |  | 43156.1458 | 59 | 58
2018-02-25 04:00 | 45 | 45 |  |  | 43156.1667 | 59 | 58
2018-02-25 04:30 | 46 | 45 |  |  | 43156.1875 | 59 | 58
2018-02-25 05:00 | 46 | 45 |  |  | 43156.2083 | 59 | 58
2018-02-25 05:30 | 47 | 46 |  |  | 43156.2292 | 60 | 59
2018-02-25 06:00 | 46 | 45 |  |  | 43156.25 | 60 | 59
2018-02-25 06:30 | 48 | 47 |  |  | 43156.2708 | 63 | 62
2018-02-25 07:00 | 49 | 48 |  |  | 43156.2917 | 63 | 63
2018-02-25 07:30 | 49 | 49 |  |  | 43156.3125 | 66 | 66
2018-02-25 08:00 | 52 | 52 |  |  | 43156.3333 | 70 | 69
2018-02-25 08:30 | 57 | 57 |  |  | 43156.3542 | 76 | 76
2018-02-25 09:00 | 60 | 60 |  |  | 43156.375 | 79 | 79
2018-02-25 09:30 | 62 | 62 |  |  | 43156.3958 | 80 | 80
2018-02-25 10:00 | 64 | 64 |  |  | 43156.4167 | 83 | 83
2018-02-25 10:30 | 65 | 65 |  |  | 43156.4375 | 82 | 82
2018-02-25 11:00 | 68 | 68 |  |  | 43156.4583 | 86 | 86
2018-02-25 11:30 | 73 | 73 |  |  | 43156.4792 | 89 | 89
2018-02-25 12:00 | 75 | 75 |  |  | 43156.5 | 94 | 94
2018-02-25 12:30 | 76 | 76 |  |  | 43156.5208 | 95 | 95
2018-02-25 13:00 | 78 | 78 |  |  | 43156.5417 | 97 | 97
2018-02-25 13:30 | 83 | 82 |  |  | 43156.5625 | 100 | 100
2018-02-25 14:00 | 88 | 87 |  |  | 43156.5833 | 103 | 103
2018-02-25 14:30 | 87 | 86 |  |  | 43156.6042 | 99 | 99
2018-02-25 15:00 | 83 | 82 |  |  | 43156.625 | 98 | 98
2018-02-25 15:30 | 87 | 86 |  |  | 43156.6458 | 96 | 96
2018-02-25 16:00 | 93 | 92 |  |  | 43156.6667 | 104 | 104
2018-02-25 16:30 | 98 | 97 |  |  | 43156.6875 | 111 | 111
2018-02-25 17:00 | 99 | 98 |  |  | 43156.7083 | 115 | 115
2018-02-25 17:30 | 98 | 97 |  |  | 43156.7292 | 115 | 115
2018-02-25 18:00 | 98 | 96 |  |  | 43156.75 | 115 | 114
2018-02-25 18:30 | 99 | 98 |  |  | 43156.7708 | 116 | 116
2018-02-25 19:00 | 100 | 99 |  |  | 43156.7917 | 119 | 119
2018-02-25 19:30 | 100 | 99 |  |  | 43156.8125 | 118 | 118
2018-02-25 20:00 | 99 | 99 |  |  | 43156.8333 | 117 | 117
2018-02-25 20:30 | 97 | 96 |  |  | 43156.8542 | 114 | 114
2018-02-25 21:00 | 88 | 87 |  |  | 43156.875 | 105 | 105
2018-02-25 21:30 | 83 | 83 |  |  | 43156.8958 | 101 | 100
2018-02-25 22:00 | 81 | 80 |  |  | 43156.9167 | 98 | 98
2018-02-25 22:30 | 78 | 78 |  |  | 43156.9375 | 96 | 95
2018-02-25 23:00 | 77 | 76 |  |  | 43156.9583 | 93 | 92
2018-02-25 23:30 | 72 | 72 |  |  | 43156.9792 | 89 | 89
2018-02-26 | 67 | 66 |  |  | 43157 | 81 | 81
2018-02-26 00:30 | 62 | 61 |  |  | 43157.0208 | 75 | 75
2018-02-26 01:00 | 59 | 58 |  |  | 43157.0417 | 72 | 72
2018-02-26 01:30 | 60 | 58 |  |  | 43157.0625 | 73 | 73
2018-02-26 02:00 | 60 | 57 |  |  | 43157.0833 | 73 | 73
2018-02-26 02:30 | 58 | 56 |  |  | 43157.1042 | 71 | 71
2018-02-26 03:00 | 57 | 54 |  |  | 43157.125 | 69 | 69
2018-02-26 03:30 | 59 | 57 |  |  | 43157.1458 | 70 | 70
2018-02-26 04:00 | 58 | 55 |  |  | 43157.1667 | 70 | 70
2018-02-26 04:30 | 55 | 52 |  |  | 43157.1875 | 67 | 67
2018-02-26 05:00 | 56 | 54 |  |  | 43157.2083 | 68 | 68
2018-02-26 05:30 | 59 | 58 |  |  | 43157.2292 | 73 | 73
2018-02-26 06:00 | 62 | 61 |  |  | 43157.25 | 79 | 79
2018-02-26 06:30 | 69 | 69 |  |  | 43157.2708 | 91 | 91
2018-02-26 07:00 | 78 | 78 |  |  | 43157.2917 | 103 | 102
2018-02-26 07:30 | 88 | 88 |  |  | 43157.3125 | 116 | 115
2018-02-26 08:00 | 92 | 92 |  |  | 43157.3333 | 122 | 122
2018-02-26 08:30 | 94 | 94 |  |  | 43157.3542 | 126 | 125
2018-02-26 09:00 | 97 | 97 |  |  | 43157.375 | 129 | 129
2018-02-26 09:30 | 99 | 99 |  |  | 43157.3958 | 130 | 129
2018-02-26 10:00 | 102 | 102 |  |  | 43157.4167 | 132 | 132
2018-02-26 10:30 | 106 | 106 |  |  | 43157.4375 | 136 | 135
2018-02-26 11:00 | 109 | 109 |  |  | 43157.4583 | 142 | 141
2018-02-26 11:30 | 113 | 110 |  |  | 43157.4792 | 145 | 142
2018-02-26 12:00 | 113 | 110 |  |  | 43157.5 | 147 | 144
2018-02-26 12:30 | 114 | 111 |  |  | 43157.5208 | 148 | 145
2018-02-26 13:00 | 115 | 112 |  |  | 43157.5417 | 148 | 145
2018-02-26 13:30 | 118 | 116 |  |  | 43157.5625 | 151 | 148
2018-02-26 14:00 | 122 | 119 |  |  | 43157.5833 | 153 | 152
2018-02-26 14:30 | 125 | 121 |  |  | 43157.6042 | 154 | 153
2018-02-26 15:00 | 125 | 122 |  |  | 43157.625 | 155 | 154
2018-02-26 15:30 | 117 | 115 |  |  | 43157.6458 | 150 | 149
2018-02-26 16:00 | 117 | 115 |  |  | 43157.6667 | 149 | 148
2018-02-26 16:30 | 118 | 116 |  |  | 43157.6875 | 150 | 149
2018-02-26 17:00 | 121 | 118 |  |  | 43157.7083 | 150 | 149
2018-02-26 17:30 | 121 | 117 |  |  | 43157.7292 | 147 | 146
2018-02-26 18:00 | 120 | 115 |  |  | 43157.75 | 142 | 142
2018-02-26 18:30 | 113 | 112 |  |  | 43157.7708 | 137 | 137
2018-02-26 19:00 | 114 | 114 |  |  | 43157.7917 | 143 | 142
2018-02-26 19:30 | 113 | 113 |  |  | 43157.8125 | 146 | 144
2018-02-26 20:00 | 107 | 106 |  |  | 43157.8333 | 138 | 135
2018-02-26 20:30 | 101 | 101 |  |  | 43157.8542 | 126 | 124
2018-02-26 21:00 | 94 | 93 |  |  | 43157.875 | 114 | 114
2018-02-26 21:30 | 95 | 94 |  |  | 43157.8958 | 111 | 111
2018-02-26 22:00 | 93 | 92 |  |  | 43157.9167 | 110 | 110
2018-02-26 22:30 | 87 | 86 |  |  | 43157.9375 | 104 | 103
2018-02-26 23:00 | 82 | 81 |  |  | 43157.9583 | 97 | 97
2018-02-26 23:30 | 75 | 74 |  |  | 43157.9792 | 90 | 90
2018-02-27 | 67 | 67 |  |  | 43158 | 82 | 82
2018-02-27 00:30 | 63 | 62 |  |  | 43158.0208 | 76 | 76
2018-02-27 01:00 | 57 | 57 |  |  | 43158.0417 | 70 | 70
2018-02-27 01:30 | 55 | 55 |  |  | 43158.0625 | 66 | 66
2018-02-27 02:00 | 52 | 52 |  |  | 43158.0833 | 64 | 64
2018-02-27 02:30 | 52 | 52 |  |  | 43158.1042 | 65 | 65
2018-02-27 03:00 | 53 | 53 |  |  | 43158.125 | 65 | 65
2018-02-27 03:30 | 52 | 52 |  |  | 43158.1458 | 65 | 64
2018-02-27 04:00 | 51 | 51 |  |  | 43158.1667 | 65 | 64
2018-02-27 04:30 | 50 | 50 |  |  | 43158.1875 | 64 | 63
2018-02-27 05:00 | 54 | 54 |  |  | 43158.2083 | 67 | 67
2018-02-27 05:30 | 59 | 58 |  |  | 43158.2292 | 72 | 72
2018-02-27 06:00 | 64 | 63 |  |  | 43158.25 | 79 | 79
2018-02-27 06:30 | 70 | 69 |  |  | 43158.2708 | 90 | 90
2018-02-27 07:00 | 78 | 78 |  |  | 43158.2917 | 102 | 102
2018-02-27 07:30 | 84 | 84 |  |  | 43158.3125 | 113 | 110
2018-02-27 08:00 | 86 | 86 |  |  | 43158.3333 | 118 | 114
2018-02-27 08:30 | 89 | 89 |  |  | 43158.3542 | 121 | 117
2018-02-27 09:00 | 90 | 90 |  |  | 43158.375 | 121 | 118
2018-02-27 09:30 | 89 | 89 |  |  | 43158.3958 | 120 | 117
2018-02-27 10:00 | 90 | 90 |  |  | 43158.4167 | 122 | 119
2018-02-27 10:30 | 89 | 89 |  |  | 43158.4375 | 121 | 118
2018-02-27 11:00 | 91 | 91 |  |  | 43158.4583 | 123 | 120
2018-02-27 11:30 | 94 | 94 |  |  | 43158.4792 | 125 | 123
2018-02-27 12:00 | 92 | 91 |  |  | 43158.5 | 125 | 122
2018-02-27 12:30 | 88 | 88 |  |  | 43158.5208 | 119 | 116
2018-02-27 13:00 | 86 | 86 |  |  | 43158.5417 | 113 | 110
2018-02-27 13:30 | 87 | 87 |  |  | 43158.5625 | 116 | 113
2018-02-27 14:00 | 90 | 90 |  |  | 43158.5833 | 122 | 119
2018-02-27 14:30 | 96 | 96 |  |  | 43158.6042 | 123 | 121
2018-02-27 15:00 | 94 | 94 |  |  | 43158.625 | 124 | 122
2018-02-27 15:30 | 95 | 95 |  |  | 43158.6458 | 124 | 121
2018-02-27 16:00 | 96 | 96 |  |  | 43158.6667 | 122 | 121
2018-02-27 16:30 | 96 | 96 |  |  | 43158.6875 | 122 | 120
2018-02-27 17:00 | 95 | 94 |  |  | 43158.7083 | 118 | 117
2018-02-27 17:30 | 94 | 94 |  |  | 43158.7292 | 116 | 115
2018-02-27 18:00 | 92 | 91 |  |  | 43158.75 | 112 | 111
2018-02-27 18:30 | 91 | 90 |  |  | 43158.7708 | 110 | 109
2018-02-27 19:00 | 91 | 91 |  |  | 43158.7917 | 110 | 109
2018-02-27 19:30 | 91 | 90 |  |  | 43158.8125 | 109 | 109
2018-02-27 20:00 | 92 | 91 |  |  | 43158.8333 | 108 | 108
2018-02-27 20:30 | 91 | 90 |  |  | 43158.8542 | 106 | 105
2018-02-27 21:00 | 86 | 86 |  |  | 43158.875 | 102 | 101
2018-02-27 21:30 | 81 | 81 |  |  | 43158.8958 | 97 | 96
2018-02-27 22:00 | 79 | 79 |  |  | 43158.9167 | 96 | 95
2018-02-27 22:30 | 74 | 74 |  |  | 43158.9375 | 91 | 89
2018-02-27 23:00 | 71 | 70 |  |  | 43158.9583 | 87 | 85
2018-02-27 23:30 | 66 | 65 |  |  | 43158.9792 | 82 | 80
2018-02-28 | 61 | 60 |  |  | 43159 | 77 | 74
2018-02-28 00:30 | 58 | 57 |  |  | 43159.0208 | 72 | 70
2018-02-28 01:00 | 55 | 53 |  |  | 43159.0417 | 68 | 66
2018-02-28 01:30 | 50 | 50 |  |  | 43159.0625 | 62 | 62
2018-02-28 02:00 | 49 | 49 |  |  | 43159.0833 | 61 | 61
2018-02-28 02:30 | 50 | 50 |  |  | 43159.1042 | 61 | 61
2018-02-28 03:00 | 50 | 50 |  |  | 43159.125 | 61 | 61
2018-02-28 03:30 | 51 | 50 |  |  | 43159.1458 | 61 | 61
2018-02-28 04:00 | 50 | 50 |  |  | 43159.1667 | 61 | 61
2018-02-28 04:30 | 52 | 52 |  |  | 43159.1875 | 63 | 63
2018-02-28 05:00 | 53 | 53 |  |  | 43159.2083 | 65 | 65
2018-02-28 05:30 | 54 | 54 |  |  | 43159.2292 | 66 | 65
2018-02-28 06:00 | 56 | 56 |  |  | 43159.25 | 70 | 69
2018-02-28 06:30 | 60 | 60 |  |  | 43159.2708 | 78 | 77
2018-02-28 07:00 | 70 | 70 |  |  | 43159.2917 | 90 | 89
2018-02-28 07:30 | 77 | 77 |  |  | 43159.3125 | 99 | 98
2018-02-28 08:00 | 77 | 76 |  |  | 43159.3333 | 102 | 100
2018-02-28 08:30 | 81 | 80 |  |  | 43159.3542 | 107 | 105
2018-02-28 09:00 | 85 | 80 |  |  | 43159.375 | 108 | 106
2018-02-28 09:30 | 85 | 81 |  |  | 43159.3958 | 108 | 106
2018-02-28 10:00 | 87 | 83 |  |  | 43159.4167 | 111 | 109
2018-02-28 10:30 | 88 | 84 |  |  | 43159.4375 | 111 | 108
2018-02-28 11:00 | 89 | 85 |  |  | 43159.4583 | 111 | 110
2018-02-28 11:30 | 89 | 84 |  |  | 43159.4792 | 110 | 109
2018-02-28 12:00 | 90 | 86 |  |  | 43159.5 | 112 | 111
2018-02-28 12:30 | 91 | 87 |  |  | 43159.5208 | 114 | 113
2018-02-28 13:00 | 92 | 88 |  |  | 43159.5417 | 114 | 113
2018-02-28 13:30 | 93 | 89 |  |  | 43159.5625 | 116 | 115
2018-02-28 14:00 | 93 | 89 |  |  | 43159.5833 | 116 | 115
2018-02-28 14:30 | 94 | 91 |  |  | 43159.6042 | 115 | 114
2018-02-28 15:00 | 93 | 90 |  |  | 43159.625 | 114 | 114
2018-02-28 15:30 | 94 | 90 |  |  | 43159.6458 | 115 | 114
2018-02-28 16:00 | 96 | 93 |  |  | 43159.6667 | 117 | 116
2018-02-28 16:30 | 98 | 95 |  |  | 43159.6875 | 118 | 117
2018-02-28 17:00 | 100 | 97 |  |  | 43159.7083 | 118 | 117
2018-02-28 17:30 | 100 | 98 |  |  | 43159.7292 | 117 | 117
2018-02-28 18:00 | 98 | 96 |  |  | 43159.75 | 113 | 113
2018-02-28 18:30 | 94 | 93 |  |  | 43159.7708 | 109 | 109
2018-02-28 19:00 | 98 | 96 |  |  | 43159.7917 | 114 | 113
2018-02-28 19:30 | 97 | 95 |  |  | 43159.8125 | 112 | 112
2018-02-28 20:00 | 95 | 93 |  |  | 43159.8333 | 110 | 110
2018-02-28 20:30 | 92 | 89 |  |  | 43159.8542 | 106 | 105
2018-02-28 21:00 | 89 | 85 |  |  | 43159.875 | 102 | 101
2018-02-28 21:30 | 86 | 83 |  |  | 43159.8958 | 98 | 97
2018-02-28 22:00 | 83 | 80 |  |  | 43159.9167 | 96 | 96
2018-02-28 22:30 | 75 | 73 |  |  | 43159.9375 | 90 | 90
2018-02-28 23:00 | 72 | 70 |  |  | 43159.9583 | 84 | 84
2018-02-28 23:30 | 66 | 64 |  |  | 43159.9792 | 79 | 79
2018-03-01 | 60 | 58 |  |  | 43160 | 74 | 73
2018-03-01 00:30 | 56 | 55 |  |  | 43160.0208 | 68 | 68
2018-03-01 01:00 | 51 | 50 |  |  | 43160.0417 | 63 | 63
2018-03-01 01:30 | 51 | 50 |  |  | 43160.0625 | 63 | 62
2018-03-01 02:00 | 50 | 50 |  |  | 43160.0833 | 62 | 61
2018-03-01 02:30 | 50 | 49 |  |  | 43160.1042 | 61 | 61
2018-03-01 03:00 | 50 | 48 |  |  | 43160.125 | 61 | 61
2018-03-01 03:30 | 50 | 48 |  |  | 43160.1458 | 61 | 61
2018-03-01 04:00 | 49 | 48 |  |  | 43160.1667 | 60 | 60
2018-03-01 04:30 | 50 | 48 |  |  | 43160.1875 | 61 | 60
2018-03-01 05:00 | 52 | 51 |  |  | 43160.2083 | 64 | 64
2018-03-01 05:30 | 57 | 56 |  |  | 43160.2292 | 69 | 68
2018-03-01 06:00 | 61 | 59 |  |  | 43160.25 | 74 | 73
2018-03-01 06:30 | 66 | 64 |  |  | 43160.2708 | 83 | 82
2018-03-01 07:00 | 71 | 71 |  |  | 43160.2917 | 90 | 90
2018-03-01 07:30 | 78 | 77 |  |  | 43160.3125 | 99 | 98
2018-03-01 08:00 | 79 | 78 |  |  | 43160.3333 | 101 | 100
2018-03-01 08:30 | 81 | 80 |  |  | 43160.3542 | 105 | 104
2018-03-01 09:00 | 82 | 81 |  |  | 43160.375 | 106 | 105
2018-03-01 09:30 | 81 | 80 |  |  | 43160.3958 | 107 | 106
2018-03-01 10:00 | 82 | 81 |  |  | 43160.4167 | 107 | 106
2018-03-01 10:30 | 83 | 82 |  |  | 43160.4375 | 108 | 108
2018-03-01 11:00 | 85 | 85 |  |  | 43160.4583 | 112 | 111
2018-03-01 11:30 | 86 | 85 |  |  | 43160.4792 | 113 | 112
2018-03-01 12:00 | 88 | 88 |  |  | 43160.5 | 115 | 115
2018-03-01 12:30 | 90 | 89 |  |  | 43160.5208 | 117 | 116
2018-03-01 13:00 | 94 | 93 |  |  | 43160.5417 | 122 | 121
2018-03-01 13:30 | 100 | 98 |  |  | 43160.5625 | 129 | 127
2018-03-01 14:00 | 106 | 102 |  |  | 43160.5833 | 139 | 131
2018-03-01 14:30 | 108 | 106 |  |  | 43160.6042 | 141 | 136
2018-03-01 15:00 | 111 | 109 |  |  | 43160.625 | 144 | 139
2018-03-01 15:30 | 115 | 113 |  |  | 43160.6458 | 146 | 141
2018-03-01 16:00 | 118 | 116 |  |  | 43160.6667 | 151 | 146
2018-03-01 16:30 | 121 | 119 |  |  | 43160.6875 | 152 | 148
2018-03-01 17:00 | 117 | 115 |  |  | 43160.7083 | 149 | 144
2018-03-01 17:30 | 114 | 112 |  |  | 43160.7292 | 146 | 140
2018-03-01 18:00 | 114 | 110 |  |  | 43160.75 | 144 | 136
2018-03-01 18:30 | 112 | 108 |  |  | 43160.7708 | 139 | 132
2018-03-01 19:00 | 113 | 109 |  |  | 43160.7917 | 141 | 133
2018-03-01 19:30 | 112 | 106 |  |  | 43160.8125 | 140 | 131
2018-03-01 20:00 | 113 | 106 |  |  | 43160.8333 | 138 | 129
2018-03-01 20:30 | 108 | 105 |  |  | 43160.8542 | 135 | 128
2018-03-01 21:00 | 112 | 106 |  |  | 43160.875 | 134 | 126
2018-03-01 21:30 | 111 | 102 |  |  | 43160.8958 | 129 | 119
2018-03-01 22:00 | 105 | 99 |  |  | 43160.9167 | 121 | 116
2018-03-01 22:30 | 102 | 93 |  |  | 43160.9375 | 112 | 109
2018-03-01 23:00 | 99 | 87 |  |  | 43160.9583 | 102 | 100
2018-03-01 23:30 | 94 | 82 |  |  | 43160.9792 | 97 | 96
2018-03-02 | 89 | 74 |  |  | 43161 | 89 | 89
2018-03-02 00:30 | 85 | 70 |  |  | 43161.0208 | 84 | 83
2018-03-02 01:00 | 81 | 64 |  |  | 43161.0417 | 79 | 78
2018-03-02 01:30 | 79 | 60 |  |  | 43161.0625 | 74 | 73
2018-03-02 02:00 | 76 | 57 |  |  | 43161.0833 | 71 | 70
2018-03-02 02:30 | 77 | 57 |  |  | 43161.1042 | 70 | 69
2018-03-02 03:00 | 72 | 54 |  |  | 43161.125 | 67 | 66
2018-03-02 03:30 | 72 | 54 |  |  | 43161.1458 | 66 | 65
2018-03-02 04:00 | 71 | 53 |  |  | 43161.1667 | 67 | 66
2018-03-02 04:30 | 73 | 57 |  |  | 43161.1875 | 69 | 69
2018-03-02 05:00 | 75 | 59 |  |  | 43161.2083 | 73 | 73
2018-03-02 05:30 | 76 | 63 |  |  | 43161.2292 | 77 | 77
2018-03-02 06:00 | 83 | 67 |  |  | 43161.25 | 85 | 82
2018-03-02 06:30 | 86 | 72 |  |  | 43161.2708 | 93 | 91
2018-03-02 07:00 | 89 | 79 |  |  | 43161.2917 | 103 | 102
2018-03-02 07:30 | 92 | 84 |  |  | 43161.3125 | 111 | 109
2018-03-02 08:00 | 94 | 86 |  |  | 43161.3333 | 114 | 114
2018-03-02 08:30 | 95 | 88 |  |  | 43161.3542 | 116 | 116
2018-03-02 09:00 | 99 | 92 |  |  | 43161.375 | 122 | 122
2018-03-02 09:30 | 103 | 96 |  |  | 43161.3958 | 126 | 125
2018-03-02 10:00 | 104 | 96 |  |  | 43161.4167 | 125 | 123
2018-03-02 10:30 | 105 | 97 |  |  | 43161.4375 | 124 | 122
2018-03-02 11:00 | 107 | 99 |  |  | 43161.4583 | 128 | 126
2018-03-02 11:30 | 110 | 102 |  |  | 43161.4792 | 127 | 125
2018-03-02 12:00 | 114 | 100 |  |  | 43161.5 | 135 | 127
2018-03-02 12:30 | 113 | 97 |  |  | 43161.5208 | 137 | 129
2018-03-02 13:00 | 115 | 98 |  |  | 43161.5417 | 138 | 129
2018-03-02 13:30 | 117 | 101 |  |  | 43161.5625 | 136 | 127
2018-03-02 14:00 | 120 | 105 |  |  | 43161.5833 | 136 | 128
2018-03-02 14:30 | 121 | 105 |  |  | 43161.6042 | 138 | 129
2018-03-02 15:00 | 114 | 98 |  |  | 43161.625 | 136 | 129
2018-03-02 15:30 | 106 | 93 |  |  | 43161.6458 | 125 | 121
2018-03-02 16:00 | 113 | 102 |  |  | 43161.6667 | 130 | 127
2018-03-02 16:30 | 113 | 101 |  |  | 43161.6875 | 129 | 125
2018-03-02 17:00 | 111 | 99 |  |  | 43161.7083 | 126 | 122
2018-03-02 17:30 | 109 | 96 |  |  | 43161.7292 | 123 | 119
2018-03-02 18:00 | 106 | 95 |  |  | 43161.75 | 121 | 118
2018-03-02 18:30 | 105 | 94 |  |  | 43161.7708 | 118 | 115
2018-03-02 19:00 | 105 | 94 |  |  | 43161.7917 | 118 | 114
2018-03-02 19:30 | 105 | 95 |  |  | 43161.8125 | 117 | 114
2018-03-02 20:00 | 104 | 93 |  |  | 43161.8333 | 116 | 112
2018-03-02 20:30 | 103 | 92 |  |  | 43161.8542 | 114 | 110
2018-03-02 21:00 | 99 | 88 |  |  | 43161.875 | 108 | 104
2018-03-02 21:30 | 89 | 83 |  |  | 43161.8958 | 99 | 98
2018-03-02 22:00 | 88 | 82 |  |  | 43161.9167 | 98 | 98
2018-03-02 22:30 | 85 | 76 |  |  | 43161.9375 | 94 | 92
2018-03-02 23:00 | 83 | 73 |  |  | 43161.9583 | 89 | 88
2018-03-02 23:30 | 82 | 71 |  |  | 43161.9792 | 87 | 86
2018-03-03 | 80 | 65 |  |  | 43162 | 82 | 80
2018-03-03 00:30 | 78 | 61 |  |  | 43162.0208 | 76 | 74
2018-03-03 01:00 | 74 | 56 |  |  | 43162.0417 | 71 | 69
2018-03-03 01:30 | 73 | 54 |  |  | 43162.0625 | 69 | 67
2018-03-03 02:00 | 72 | 52 |  |  | 43162.0833 | 67 | 65
2018-03-03 02:30 | 71 | 51 |  |  | 43162.1042 | 66 | 64
2018-03-03 03:00 | 70 | 50 |  |  | 43162.125 | 66 | 64
2018-03-03 03:30 | 70 | 50 |  |  | 43162.1458 | 65 | 62
2018-03-03 04:00 | 70 | 49 |  |  | 43162.1667 | 64 | 62
2018-03-03 04:30 | 70 | 50 |  |  | 43162.1875 | 65 | 62
2018-03-03 05:00 | 73 | 53 |  |  | 43162.2083 | 68 | 65
2018-03-03 05:30 | 73 | 54 |  |  | 43162.2292 | 69 | 66
2018-03-03 06:00 | 72 | 53 |  |  | 43162.25 | 69 | 67
2018-03-03 06:30 | 73 | 54 |  |  | 43162.2708 | 71 | 69
2018-03-03 07:00 | 72 | 54 |  |  | 43162.2917 | 72 | 70
2018-03-03 07:30 | 70 | 55 |  |  | 43162.3125 | 72 | 72
2018-03-03 08:00 | 68 | 54 |  |  | 43162.3333 | 72 | 71
2018-03-03 08:30 | 70 | 58 |  |  | 43162.3542 | 77 | 76
2018-03-03 09:00 | 73 | 63 |  |  | 43162.375 | 82 | 82
2018-03-03 09:30 | 76 | 68 |  |  | 43162.3958 | 86 | 86
2018-03-03 10:00 | 79 | 69 |  |  | 43162.4167 | 90 | 89
2018-03-03 10:30 | 83 | 74 |  |  | 43162.4375 | 93 | 92
2018-03-03 11:00 | 85 | 76 |  |  | 43162.4583 | 94 | 94
2018-03-03 11:30 | 84 | 75 |  |  | 43162.4792 | 95 | 94
2018-03-03 12:00 | 81 | 72 |  |  | 43162.5 | 92 | 91
2018-03-03 12:30 | 81 | 71 |  |  | 43162.5208 | 88 | 87
2018-03-03 13:00 | 80 | 70 |  |  | 43162.5417 | 85 | 83
2018-03-03 13:30 | 83 | 73 |  |  | 43162.5625 | 89 | 88
2018-03-03 14:00 | 84 | 75 |  |  | 43162.5833 | 93 | 92
2018-03-03 14:30 | 83 | 75 |  |  | 43162.6042 | 90 | 89
2018-03-03 15:00 | 88 | 81 |  |  | 43162.625 | 97 | 96
2018-03-03 15:30 | 90 | 82 |  |  | 43162.6458 | 99 | 98
2018-03-03 16:00 | 90 | 82 |  |  | 43162.6667 | 101 | 100
2018-03-03 16:30 | 92 | 85 |  |  | 43162.6875 | 103 | 102
2018-03-03 17:00 | 91 | 85 |  |  | 43162.7083 | 103 | 102
2018-03-03 17:30 | 88 | 87 |  |  | 43162.7292 | 103 | 103
2018-03-03 18:00 | 89 | 88 |  |  | 43162.75 | 107 | 107
2018-03-03 18:30 | 89 | 88 |  |  | 43162.7708 | 108 | 108
2018-03-03 19:00 | 92 | 91 |  |  | 43162.7917 | 112 | 112
2018-03-03 19:30 | 91 | 90 |  |  | 43162.8125 | 109 | 109
2018-03-03 20:00 | 89 | 88 |  |  | 43162.8333 | 108 | 108
2018-03-03 20:30 | 87 | 85 |  |  | 43162.8542 | 106 | 105
2018-03-03 21:00 | 83 | 81 |  |  | 43162.875 | 100 | 100
2018-03-03 21:30 | 80 | 77 |  |  | 43162.8958 | 96 | 96
2018-03-03 22:00 | 79 | 76 |  |  | 43162.9167 | 96 | 96
2018-03-03 22:30 | 81 | 77 |  |  | 43162.9375 | 95 | 95
2018-03-03 23:00 | 80 | 76 |  |  | 43162.9583 | 93 | 93
2018-03-03 23:30 | 77 | 72 |  |  | 43162.9792 | 90 | 90
2018-03-04 | 71 | 67 |  |  | 43163 | 85 | 85
2018-03-04 00:30 | 67 | 62 |  |  | 43163.0208 | 79 | 78
2018-03-04 01:00 | 65 | 59 |  |  | 43163.0417 | 74 | 74
2018-03-04 01:30 | 62 | 56 |  |  | 43163.0625 | 71 | 71
2018-03-04 02:00 | 62 | 54 |  |  | 43163.0833 | 70 | 70
2018-03-04 02:30 | 61 | 53 |  |  | 43163.1042 | 69 | 68
2018-03-04 03:00 | 60 | 52 |  |  | 43163.125 | 67 | 67
2018-03-04 03:30 | 60 | 51 |  |  | 43163.1458 | 65 | 65
2018-03-04 04:00 | 59 | 51 |  |  | 43163.1667 | 65 | 64
2018-03-04 04:30 | 59 | 50 |  |  | 43163.1875 | 64 | 64
2018-03-04 05:00 | 58 | 50 |  |  | 43163.2083 | 64 | 64
2018-03-04 05:30 | 59 | 50 |  |  | 43163.2292 | 65 | 65
2018-03-04 06:00 | 59 | 49 |  |  | 43163.25 | 65 | 64
2018-03-04 06:30 | 59 | 49 |  |  | 43163.2708 | 64 | 64
2018-03-04 07:00 | 59 | 50 |  |  | 43163.2917 | 67 | 67
2018-03-04 07:30 | 58 | 51 |  |  | 43163.3125 | 69 | 69
2018-03-04 08:00 | 59 | 53 |  |  | 43163.3333 | 72 | 72
2018-03-04 08:30 | 61 | 57 |  |  | 43163.3542 | 76 | 75
2018-03-04 09:00 | 61 | 57 |  |  | 43163.375 | 75 | 75
2018-03-04 09:30 | 62 | 58 |  |  | 43163.3958 | 80 | 80
2018-03-04 10:00 | 65 | 62 |  |  | 43163.4167 | 82 | 82
2018-03-04 10:30 | 69 | 66 |  |  | 43163.4375 | 84 | 84
2018-03-04 11:00 | 70 | 67 |  |  | 43163.4583 | 87 | 86
2018-03-04 11:30 | 71 | 69 |  |  | 43163.4792 | 87 | 87
2018-03-04 12:00 | 74 | 72 |  |  | 43163.5 | 90 | 90
2018-03-04 12:30 | 78 | 76 |  |  | 43163.5208 | 94 | 94
2018-03-04 13:00 | 80 | 79 |  |  | 43163.5417 | 97 | 97
2018-03-04 13:30 | 85 | 83 |  |  | 43163.5625 | 100 | 100
2018-03-04 14:00 | 92 | 91 |  |  | 43163.5833 | 104 | 103
2018-03-04 14:30 | 96 | 95 |  |  | 43163.6042 | 110 | 110
2018-03-04 15:00 | 100 | 99 |  |  | 43163.625 | 118 | 118
2018-03-04 15:30 | 101 | 100 |  |  | 43163.6458 | 121 | 121
2018-03-04 16:00 | 105 | 103 |  |  | 43163.6667 | 122 | 121
2018-03-04 16:30 | 106 | 104 |  |  | 43163.6875 | 125 | 123
2018-03-04 17:00 | 109 | 107 |  |  | 43163.7083 | 128 | 126
2018-03-04 17:30 | 109 | 107 |  |  | 43163.7292 | 127 | 125
2018-03-04 18:00 | 107 | 105 |  |  | 43163.75 | 125 | 124
2018-03-04 18:30 | 107 | 105 |  |  | 43163.7708 | 122 | 121
2018-03-04 19:00 | 107 | 104 |  |  | 43163.7917 | 123 | 122
2018-03-04 19:30 | 105 | 103 |  |  | 43163.8125 | 121 | 120
2018-03-04 20:00 | 103 | 100 |  |  | 43163.8333 | 118 | 116
2018-03-04 20:30 | 96 | 94 |  |  | 43163.8542 | 114 | 112
2018-03-04 21:00 | 91 | 91 |  |  | 43163.875 | 107 | 106
2018-03-04 21:30 | 87 | 87 |  |  | 43163.8958 | 103 | 102
2018-03-04 22:00 | 85 | 85 |  |  | 43163.9167 | 103 | 102
2018-03-04 22:30 | 85 | 84 |  |  | 43163.9375 | 102 | 101
2018-03-04 23:00 | 82 | 81 |  |  | 43163.9583 | 97 | 96
2018-03-04 23:30 | 74 | 73 |  |  | 43163.9792 | 88 | 87
2018-03-05 | 69 | 67 |  |  | 43164 | 83 | 81
2018-03-05 00:30 | 65 | 63 |  |  | 43164.0208 | 78 | 76
2018-03-05 01:00 | 64 | 61 |  |  | 43164.0417 | 76 | 73
2018-03-05 01:30 | 61 | 59 |  |  | 43164.0625 | 75 | 72
2018-03-05 02:00 | 60 | 57 |  |  | 43164.0833 | 72 | 70
2018-03-05 02:30 | 58 | 56 |  |  | 43164.1042 | 69 | 68
2018-03-05 03:00 | 56 | 54 |  |  | 43164.125 | 68 | 67
2018-03-05 03:30 | 56 | 54 |  |  | 43164.1458 | 68 | 67
2018-03-05 04:00 | 57 | 55 |  |  | 43164.1667 | 70 | 69
2018-03-05 04:30 | 59 | 56 |  |  | 43164.1875 | 71 | 70
2018-03-05 05:00 | 60 | 58 |  |  | 43164.2083 | 72 | 71
2018-03-05 05:30 | 62 | 60 |  |  | 43164.2292 | 75 | 74
2018-03-05 06:00 | 67 | 66 |  |  | 43164.25 | 83 | 83
2018-03-05 06:30 | 74 | 73 |  |  | 43164.2708 | 94 | 94
2018-03-05 07:00 | 84 | 84 |  |  | 43164.2917 | 105 | 105
2018-03-05 07:30 | 91 | 91 |  |  | 43164.3125 | 118 | 118
2018-03-05 08:00 | 97 | 97 |  |  | 43164.3333 | 127 | 126
2018-03-05 08:30 | 84 | 84 |  |  | 43164.3542 | 105 | 104
2018-03-05 09:00 | 85 | 85 |  |  | 43164.375 | 105 | 104
2018-03-05 09:30 | 85 | 85 |  |  | 43164.3958 | 105 | 104
2018-03-05 10:00 | 85 | 85 |  |  | 43164.4167 | 104 | 104
2018-03-05 10:30 | 86 | 86 |  |  | 43164.4375 | 105 | 104
2018-03-05 11:00 | 99 | 99 |  |  | 43164.4583 | 126 | 125
2018-03-05 11:30 | 100 | 100 |  |  | 43164.4792 | 131 | 129
2018-03-05 12:00 | 99 | 98 |  |  | 43164.5 | 128 | 126
2018-03-05 12:30 | 98 | 98 |  |  | 43164.5208 | 127 | 126
2018-03-05 13:00 | 95 | 95 |  |  | 43164.5417 | 128 | 127
2018-03-05 13:30 | 98 | 98 |  |  | 43164.5625 | 128 | 127
2018-03-05 14:00 | 103 | 103 |  |  | 43164.5833 | 132 | 131
2018-03-05 14:30 | 102 | 102 |  |  | 43164.6042 | 130 | 129
2018-03-05 15:00 | 103 | 103 |  |  | 43164.625 | 133 | 132
2018-03-05 15:30 | 105 | 105 |  |  | 43164.6458 | 134 | 133
2018-03-05 16:00 | 107 | 107 |  |  | 43164.6667 | 134 | 132
2018-03-05 16:30 | 108 | 108 |  |  | 43164.6875 | 134 | 132
2018-03-05 17:00 | 108 | 108 |  |  | 43164.7083 | 132 | 131
2018-03-05 17:30 | 107 | 107 |  |  | 43164.7292 | 130 | 128
2018-03-05 18:00 | 106 | 105 |  |  | 43164.75 | 125 | 124
2018-03-05 18:30 | 105 | 105 |  |  | 43164.7708 | 123 | 122
2018-03-05 19:00 | 107 | 107 |  |  | 43164.7917 | 126 | 125
2018-03-05 19:30 | 106 | 106 |  |  | 43164.8125 | 124 | 124
2018-03-05 20:00 | 107 | 106 |  |  | 43164.8333 | 122 | 121
2018-03-05 20:30 | 102 | 102 |  |  | 43164.8542 | 118 | 118
2018-03-05 21:00 | 98 | 97 |  |  | 43164.875 | 113 | 112
2018-03-05 21:30 | 92 | 91 |  |  | 43164.8958 | 105 | 105
2018-03-05 22:00 | 89 | 88 |  |  | 43164.9167 | 104 | 104
2018-03-05 22:30 | 83 | 83 |  |  | 43164.9375 | 98 | 98
2018-03-05 23:00 | 77 | 77 |  |  | 43164.9583 | 92 | 92
2018-03-05 23:30 | 72 | 72 |  |  | 43164.9792 | 86 | 86
2018-03-06 | 67 | 67 |  |  | 43165 | 81 | 81
2018-03-06 00:30 | 63 | 63 |  |  | 43165.0208 | 77 | 77
2018-03-06 01:00 | 59 | 59 |  |  | 43165.0417 | 73 | 73
2018-03-06 01:30 | 57 | 57 |  |  | 43165.0625 | 69 | 69
2018-03-06 02:00 | 57 | 57 |  |  | 43165.0833 | 70 | 70
2018-03-06 02:30 | 57 | 57 |  |  | 43165.1042 | 71 | 71
2018-03-06 03:00 | 60 | 60 |  |  | 43165.125 | 73 | 73
2018-03-06 03:30 | 58 | 58 |  |  | 43165.1458 | 72 | 72
2018-03-06 04:00 | 58 | 58 |  |  | 43165.1667 | 72 | 71
2018-03-06 04:30 | 57 | 57 |  |  | 43165.1875 | 70 | 70
2018-03-06 05:00 | 57 | 57 |  |  | 43165.2083 | 71 | 71
2018-03-06 05:30 | 60 | 60 |  |  | 43165.2292 | 74 | 74
2018-03-06 06:00 | 64 | 64 |  |  | 43165.25 | 80 | 80
2018-03-06 06:30 | 69 | 69 |  |  | 43165.2708 | 89 | 89
2018-03-06 07:00 | 81 | 81 |  |  | 43165.2917 | 103 | 103
2018-03-06 07:30 | 85 | 84 |  |  | 43165.3125 | 110 | 109
2018-03-06 08:00 | 89 | 88 |  |  | 43165.3333 | 115 | 115
2018-03-06 08:30 | 89 | 88 |  |  | 43165.3542 | 118 | 118
2018-03-06 09:00 | 91 | 91 |  |  | 43165.375 | 118 | 118
2018-03-06 09:30 | 94 | 93 |  |  | 43165.3958 | 121 | 120
2018-03-06 10:00 | 93 | 92 |  |  | 43165.4167 | 121 | 120
2018-03-06 10:30 | 92 | 91 |  |  | 43165.4375 | 119 | 118
2018-03-06 11:00 | 93 | 92 |  |  | 43165.4583 | 119 | 118
2018-03-06 11:30 | 92 | 91 |  |  | 43165.4792 | 115 | 114
2018-03-06 12:00 | 93 | 91 |  |  | 43165.5 | 116 | 114
2018-03-06 12:30 | 93 | 91 |  |  | 43165.5208 | 116 | 114
2018-03-06 13:00 | 94 | 92 |  |  | 43165.5417 | 118 | 116
2018-03-06 13:30 | 94 | 92 |  |  | 43165.5625 | 119 | 117
2018-03-06 14:00 | 96 | 95 |  |  | 43165.5833 | 118 | 116
2018-03-06 14:30 | 93 | 91 |  |  | 43165.6042 | 114 | 112
2018-03-06 15:00 | 91 | 89 |  |  | 43165.625 | 112 | 110
2018-03-06 15:30 | 89 | 87 |  |  | 43165.6458 | 110 | 107
2018-03-06 16:00 | 86 | 85 |  |  | 43165.6667 | 107 | 106
2018-03-06 16:30 | 88 | 86 |  |  | 43165.6875 | 106 | 105
2018-03-06 17:00 | 88 | 86 |  |  | 43165.7083 | 107 | 106
2018-03-06 17:30 | 86 | 84 |  |  | 43165.7292 | 104 | 103
2018-03-06 18:00 | 83 | 82 |  |  | 43165.75 | 101 | 100
2018-03-06 18:30 | 84 | 83 |  |  | 43165.7708 | 100 | 99
2018-03-06 19:00 | 83 | 82 |  |  | 43165.7917 | 100 | 99
2018-03-06 19:30 | 82 | 81 |  |  | 43165.8125 | 98 | 97
2018-03-06 20:00 | 82 | 81 |  |  | 43165.8333 | 97 | 96
2018-03-06 20:30 | 81 | 79 |  |  | 43165.8542 | 96 | 95
2018-03-06 21:00 | 76 | 74 |  |  | 43165.875 | 89 | 88
2018-03-06 21:30 | 73 | 71 |  |  | 43165.8958 | 85 | 84
2018-03-06 22:00 | 72 | 70 |  |  | 43165.9167 | 86 | 85
2018-03-06 22:30 | 71 | 69 |  |  | 43165.9375 | 84 | 83
2018-03-06 23:00 | 66 | 63 |  |  | 43165.9583 | 78 | 76
2018-03-06 23:30 | 61 | 59 |  |  | 43165.9792 | 73 | 72
2018-03-07 | 55 | 52 |  |  | 43166 | 67 | 66
2018-03-07 00:30 | 52 | 48 |  |  | 43166.0208 | 62 | 60
2018-03-07 01:00 | 50 | 46 |  |  | 43166.0417 | 59 | 57
2018-03-07 01:30 | 49 | 44 |  |  | 43166.0625 | 58 | 55
2018-03-07 02:00 | 50 | 45 |  |  | 43166.0833 | 59 | 56
2018-03-07 02:30 | 50 | 46 |  |  | 43166.1042 | 59 | 56
2018-03-07 03:00 | 52 | 47 |  |  | 43166.125 | 61 | 58
2018-03-07 03:30 | 51 | 46 |  |  | 43166.1458 | 59 | 56
2018-03-07 04:00 | 51 | 46 |  |  | 43166.1667 | 58 | 55
2018-03-07 04:30 | 49 | 45 |  |  | 43166.1875 | 58 | 55
2018-03-07 05:00 | 52 | 48 |  |  | 43166.2083 | 60 | 57
2018-03-07 05:30 | 55 | 52 |  |  | 43166.2292 | 65 | 63
2018-03-07 06:00 | 58 | 55 |  |  | 43166.25 | 68 | 67
2018-03-07 06:30 | 58 | 56 |  |  | 43166.2708 | 71 | 70
2018-03-07 07:00 | 67 | 66 |  |  | 43166.2917 | 82 | 82
2018-03-07 07:30 | 72 | 71 |  |  | 43166.3125 | 91 | 91
2018-03-07 08:00 | 76 | 75 |  |  | 43166.3333 | 96 | 96
2018-03-07 08:30 | 84 | 84 |  |  | 43166.3542 | 106 | 106
2018-03-07 09:00 | 84 | 84 |  |  | 43166.375 | 109 | 109
2018-03-07 09:30 | 85 | 85 |  |  | 43166.3958 | 109 | 109
2018-03-07 10:00 | 87 | 87 |  |  | 43166.4167 | 107 | 107
2018-03-07 10:30 | 87 | 87 |  |  | 43166.4375 | 107 | 107
2018-03-07 11:00 | 85 | 85 |  |  | 43166.4583 | 106 | 106
2018-03-07 11:30 | 86 | 86 |  |  | 43166.4792 | 105 | 105
2018-03-07 12:00 | 90 | 90 |  |  | 43166.5 | 110 | 110
2018-03-07 12:30 | 86 | 86 |  |  | 43166.5208 | 109 | 109
2018-03-07 13:00 | 81 | 80 |  |  | 43166.5417 | 104 | 104
2018-03-07 13:30 | 83 | 82 |  |  | 43166.5625 | 107 | 107
2018-03-07 14:00 | 79 | 79 |  |  | 43166.5833 | 103 | 103
2018-03-07 14:30 | 82 | 82 |  |  | 43166.6042 | 105 | 105
2018-03-07 15:00 | 82 | 82 |  |  | 43166.625 | 106 | 106
2018-03-07 15:30 | 84 | 83 |  |  | 43166.6458 | 104 | 104
2018-03-07 16:00 | 84 | 83 |  |  | 43166.6667 | 104 | 104
2018-03-07 16:30 | 88 | 87 |  |  | 43166.6875 | 106 | 106
2018-03-07 17:00 | 89 | 88 |  |  | 43166.7083 | 107 | 107
2018-03-07 17:30 | 88 | 87 |  |  | 43166.7292 | 104 | 104
2018-03-07 18:00 | 87 | 86 |  |  | 43166.75 | 104 | 103
2018-03-07 18:30 | 87 | 86 |  |  | 43166.7708 | 102 | 102
2018-03-07 19:00 | 88 | 87 |  |  | 43166.7917 | 101 | 101
2018-03-07 19:30 | 86 | 85 |  |  | 43166.8125 | 98 | 98
2018-03-07 20:00 | 83 | 82 |  |  | 43166.8333 | 96 | 95
2018-03-07 20:30 | 83 | 82 |  |  | 43166.8542 | 94 | 94
2018-03-07 21:00 | 79 | 78 |  |  | 43166.875 | 89 | 89
2018-03-07 21:30 | 76 | 74 |  |  | 43166.8958 | 85 | 85
2018-03-07 22:00 | 75 | 73 |  |  | 43166.9167 | 86 | 86
2018-03-07 22:30 | 70 | 68 |  |  | 43166.9375 | 81 | 80
2018-03-07 23:00 | 66 | 63 |  |  | 43166.9583 | 74 | 74
2018-03-07 23:30 | 62 | 60 |  |  | 43166.9792 | 71 | 71
2018-03-08 | 56 | 54 |  |  | 43167 | 64 | 64
2018-03-08 00:30 | 51 | 50 |  |  | 43167.0208 | 58 | 58
2018-03-08 01:00 | 47 | 45 |  |  | 43167.0417 | 55 | 55
2018-03-08 01:30 | 45 | 43 |  |  | 43167.0625 | 52 | 52
2018-03-08 02:00 | 45 | 43 |  |  | 43167.0833 | 51 | 51
2018-03-08 02:30 | 45 | 42 |  |  | 43167.1042 | 52 | 52
2018-03-08 03:00 | 45 | 43 |  |  | 43167.125 | 51 | 51
2018-03-08 03:30 | 44 | 41 |  |  | 43167.1458 | 51 | 50
2018-03-08 04:00 | 44 | 41 |  |  | 43167.1667 | 50 | 50
2018-03-08 04:30 | 45 | 42 |  |  | 43167.1875 | 52 | 52
2018-03-08 05:00 | 45 | 42 |  |  | 43167.2083 | 51 | 51
2018-03-08 05:30 | 49 | 47 |  |  | 43167.2292 | 57 | 57
2018-03-08 06:00 | 54 | 53 |  |  | 43167.25 | 64 | 64
2018-03-08 06:30 | 62 | 62 |  |  | 43167.2708 | 76 | 76
2018-03-08 07:00 | 71 | 71 |  |  | 43167.2917 | 88 | 88
2018-03-08 07:30 | 80 | 80 |  |  | 43167.3125 | 99 | 99
2018-03-08 08:00 | 80 | 80 |  |  | 43167.3333 | 101 | 101
2018-03-08 08:30 | 79 | 79 |  |  | 43167.3542 | 102 | 102
2018-03-08 09:00 | 83 | 83 |  |  | 43167.375 | 106 | 106
2018-03-08 09:30 | 84 | 84 |  |  | 43167.3958 | 105 | 104
2018-03-08 10:00 | 84 | 84 |  |  | 43167.4167 | 101 | 101
2018-03-08 10:30 | 77 | 77 |  |  | 43167.4375 | 102 | 101
2018-03-08 11:00 | 82 | 81 |  |  | 43167.4583 | 105 | 104
2018-03-08 11:30 | 79 | 79 |  |  | 43167.4792 | 99 | 98
2018-03-08 12:00 | 76 | 76 |  |  | 43167.5 | 99 | 98
2018-03-08 12:30 | 81 | 81 |  |  | 43167.5208 | 104 | 103
2018-03-08 13:00 | 80 | 80 |  |  | 43167.5417 | 100 | 100
2018-03-08 13:30 | 74 | 74 |  |  | 43167.5625 | 96 | 96
2018-03-08 14:00 | 75 | 75 |  |  | 43167.5833 | 95 | 94
2018-03-08 14:30 | 75 | 74 |  |  | 43167.6042 | 97 | 97
2018-03-08 15:00 | 77 | 77 |  |  | 43167.625 | 99 | 98
2018-03-08 15:30 | 78 | 78 |  |  | 43167.6458 | 100 | 100
2018-03-08 16:00 | 79 | 78 |  |  | 43167.6667 | 101 | 101
2018-03-08 16:30 | 79 | 79 |  |  | 43167.6875 | 99 | 98
2018-03-08 17:00 | 83 | 82 |  |  | 43167.7083 | 100 | 100
2018-03-08 17:30 | 84 | 84 |  |  | 43167.7292 | 100 | 100
2018-03-08 18:00 | 80 | 79 |  |  | 43167.75 | 94 | 94
2018-03-08 18:30 | 79 | 78 |  |  | 43167.7708 | 93 | 93
2018-03-08 19:00 | 83 | 83 |  |  | 43167.7917 | 96 | 96
2018-03-08 19:30 | 82 | 81 |  |  | 43167.8125 | 94 | 94
2018-03-08 20:00 | 82 | 81 |  |  | 43167.8333 | 94 | 94
2018-03-08 20:30 | 82 | 81 |  |  | 43167.8542 | 94 | 94
2018-03-08 21:00 | 79 | 79 |  |  | 43167.875 | 90 | 90
2018-03-08 21:30 | 74 | 73 |  |  | 43167.8958 | 84 | 84
2018-03-08 22:00 | 71 | 70 |  |  | 43167.9167 | 81 | 81
2018-03-08 22:30 | 64 | 64 |  |  | 43167.9375 | 75 | 75
2018-03-08 23:00 | 62 | 61 |  |  | 43167.9583 | 72 | 72
2018-03-08 23:30 | 59 | 58 |  |  | 43167.9792 | 68 | 68
2018-03-09 | 52 | 51 |  |  | 43168 | 61 | 61
2018-03-09 00:30 | 49 | 46 |  |  | 43168.0208 | 56 | 56
2018-03-09 01:00 | 46 | 42 |  |  | 43168.0417 | 53 | 51
2018-03-09 01:30 | 44 | 40 |  |  | 43168.0625 | 51 | 48
2018-03-09 02:00 | 43 | 38 |  |  | 43168.0833 | 49 | 47
2018-03-09 02:30 | 43 | 38 |  |  | 43168.1042 | 49 | 46
2018-03-09 03:00 | 44 | 39 |  |  | 43168.125 | 50 | 47
2018-03-09 03:30 | 43 | 38 |  |  | 43168.1458 | 50 | 47
2018-03-09 04:00 | 43 | 38 |  |  | 43168.1667 | 49 | 46
2018-03-09 04:30 | 43 | 38 |  |  | 43168.1875 | 50 | 47
2018-03-09 05:00 | 46 | 42 |  |  | 43168.2083 | 54 | 51
2018-03-09 05:30 | 49 | 46 |  |  | 43168.2292 | 58 | 55
2018-03-09 06:00 | 53 | 50 |  |  | 43168.25 | 63 | 61
2018-03-09 06:30 | 60 | 58 |  |  | 43168.2708 | 75 | 74
2018-03-09 07:00 | 67 | 67 |  |  | 43168.2917 | 84 | 84
2018-03-09 07:30 | 77 | 75 |  |  | 43168.3125 | 96 | 95
2018-03-09 08:00 | 80 | 78 |  |  | 43168.3333 | 101 | 100
2018-03-09 08:30 | 77 | 76 |  |  | 43168.3542 | 100 | 99
2018-03-09 09:00 | 73 | 71 |  |  | 43168.375 | 93 | 93
2018-03-09 09:30 | 75 | 74 |  |  | 43168.3958 | 95 | 95
2018-03-09 10:00 | 75 | 74 |  |  | 43168.4167 | 99 | 99
2018-03-09 10:30 | 74 | 73 |  |  | 43168.4375 | 98 | 98
2018-03-09 11:00 | 69 | 68 |  |  | 43168.4583 | 92 | 92
2018-03-09 11:30 | 68 | 67 |  |  | 43168.4792 | 94 | 94
2018-03-09 12:00 | 72 | 71 |  |  | 43168.5 | 95 | 95
2018-03-09 12:30 | 72 | 71 |  |  | 43168.5208 | 92 | 92
2018-03-09 13:00 | 71 | 69 |  |  | 43168.5417 | 88 | 88
2018-03-09 13:30 | 69 | 68 |  |  | 43168.5625 | 89 | 89
2018-03-09 14:00 | 73 | 72 |  |  | 43168.5833 | 94 | 94
2018-03-09 14:30 | 71 | 70 |  |  | 43168.6042 | 91 | 91
2018-03-09 15:00 | 71 | 70 |  |  | 43168.625 | 91 | 90
2018-03-09 15:30 | 72 | 71 |  |  | 43168.6458 | 93 | 93
2018-03-09 16:00 | 78 | 76 |  |  | 43168.6667 | 100 | 99
2018-03-09 16:30 | 79 | 77 |  |  | 43168.6875 | 98 | 97
2018-03-09 17:00 | 82 | 80 |  |  | 43168.7083 | 100 | 99
2018-03-09 17:30 | 83 | 80 |  |  | 43168.7292 | 98 | 97
2018-03-09 18:00 | 82 | 79 |  |  | 43168.75 | 96 | 94
2018-03-09 18:30 | 81 | 78 |  |  | 43168.7708 | 95 | 93
2018-03-09 19:00 | 83 | 80 |  |  | 43168.7917 | 97 | 95
2018-03-09 19:30 | 83 | 80 |  |  | 43168.8125 | 97 | 95
2018-03-09 20:00 | 79 | 77 |  |  | 43168.8333 | 92 | 91
2018-03-09 20:30 | 77 | 75 |  |  | 43168.8542 | 89 | 89
2018-03-09 21:00 | 73 | 71 |  |  | 43168.875 | 85 | 84
2018-03-09 21:30 | 70 | 67 |  |  | 43168.8958 | 81 | 80
2018-03-09 22:00 | 70 | 67 |  |  | 43168.9167 | 81 | 80
2018-03-09 22:30 | 67 | 64 |  |  | 43168.9375 | 78 | 76
2018-03-09 23:00 | 63 | 60 |  |  | 43168.9583 | 72 | 71
2018-03-09 23:30 | 59 | 55 |  |  | 43168.9792 | 70 | 68
2018-03-10 | 57 | 52 |  |  | 43169 | 67 | 64
2018-03-10 00:30 | 53 | 48 |  |  | 43169.0208 | 62 | 59
2018-03-10 01:00 | 50 | 45 |  |  | 43169.0417 | 57 | 54
2018-03-10 01:30 | 48 | 43 |  |  | 43169.0625 | 55 | 51
2018-03-10 02:00 | 48 | 42 |  |  | 43169.0833 | 54 | 51
2018-03-10 02:30 | 48 | 42 |  |  | 43169.1042 | 54 | 50
2018-03-10 03:00 | 48 | 41 |  |  | 43169.125 | 54 | 50
2018-03-10 03:30 | 47 | 40 |  |  | 43169.1458 | 53 | 49
2018-03-10 04:00 | 47 | 41 |  |  | 43169.1667 | 53 | 49
2018-03-10 04:30 | 48 | 42 |  |  | 43169.1875 | 55 | 51
2018-03-10 05:00 | 49 | 42 |  |  | 43169.2083 | 56 | 52
2018-03-10 05:30 | 51 | 45 |  |  | 43169.2292 | 57 | 53
2018-03-10 06:00 | 49 | 44 |  |  | 43169.25 | 58 | 54
2018-03-10 06:30 | 51 | 46 |  |  | 43169.2708 | 60 | 56
2018-03-10 07:00 | 52 | 47 |  |  | 43169.2917 | 62 | 59
2018-03-10 07:30 | 55 | 51 |  |  | 43169.3125 | 67 | 65
2018-03-10 08:00 | 54 | 51 |  |  | 43169.3333 | 69 | 68
2018-03-10 08:30 | 51 | 49 |  |  | 43169.3542 | 66 | 65
2018-03-10 09:00 | 53 | 51 |  |  | 43169.375 | 66 | 66
2018-03-10 09:30 | 55 | 54 |  |  | 43169.3958 | 67 | 67
2018-03-10 10:00 | 59 | 58 |  |  | 43169.4167 | 71 | 70
2018-03-10 10:30 | 61 | 60 |  |  | 43169.4375 | 75 | 75
2018-03-10 11:00 | 54 | 53 |  |  | 43169.4583 | 73 | 73
2018-03-10 11:30 | 52 | 51 |  |  | 43169.4792 | 70 | 70
2018-03-10 12:00 | 53 | 52 |  |  | 43169.5 | 69 | 69
2018-03-10 12:30 | 52 | 51 |  |  | 43169.5208 | 64 | 64
2018-03-10 13:00 | 48 | 46 |  |  | 43169.5417 | 58 | 58
2018-03-10 13:30 | 53 | 52 |  |  | 43169.5625 | 70 | 70
2018-03-10 14:00 | 59 | 58 |  |  | 43169.5833 | 72 | 72
2018-03-10 14:30 | 58 | 56 |  |  | 43169.6042 | 68 | 67
2018-03-10 15:00 | 58 | 56 |  |  | 43169.625 | 72 | 71
2018-03-10 15:30 | 60 | 59 |  |  | 43169.6458 | 77 | 77
2018-03-10 16:00 | 66 | 64 |  |  | 43169.6667 | 83 | 82
2018-03-10 16:30 | 66 | 65 |  |  | 43169.6875 | 81 | 80
2018-03-10 17:00 | 66 | 65 |  |  | 43169.7083 | 81 | 81
2018-03-10 17:30 | 66 | 65 |  |  | 43169.7292 | 81 | 81
2018-03-10 18:00 | 65 | 64 |  |  | 43169.75 | 82 | 81
2018-03-10 18:30 | 67 | 65 |  |  | 43169.7708 | 83 | 82
2018-03-10 19:00 | 68 | 67 |  |  | 43169.7917 | 84 | 84
2018-03-10 19:30 | 67 | 65 |  |  | 43169.8125 | 82 | 81
2018-03-10 20:00 | 67 | 65 |  |  | 43169.8333 | 82 | 81
2018-03-10 20:30 | 67 | 65 |  |  | 43169.8542 | 82 | 81
2018-03-10 21:00 | 66 | 64 |  |  | 43169.875 | 79 | 78
2018-03-10 21:30 | 63 | 59 |  |  | 43169.8958 | 75 | 74
2018-03-10 22:00 | 62 | 58 |  |  | 43169.9167 | 75 | 73
2018-03-10 22:30 | 62 | 57 |  |  | 43169.9375 | 73 | 71
2018-03-10 23:00 | 60 | 56 |  |  | 43169.9583 | 71 | 69
2018-03-10 23:30 | 59 | 54 |  |  | 43169.9792 | 70 | 67
2018-03-11 | 56 | 50 |  |  | 43170 | 66 | 64
2018-03-11 00:30 | 53 | 47 |  |  | 43170.0208 | 62 | 59
2018-03-11 01:00 | 49 | 42 |  |  | 43170.0417 | 57 | 54
2018-03-11 01:30 | 48 | 42 |  |  | 43170.0625 | 56 | 52
2018-03-11 02:00 | 47 | 41 |  |  | 43170.0833 | 55 | 52
2018-03-11 02:30 | 45 | 39 |  |  | 43170.1042 | 53 | 51
2018-03-11 03:00 | 46 | 40 |  |  | 43170.125 | 53 | 50
2018-03-11 03:30 | 45 | 39 |  |  | 43170.1458 | 53 | 50
2018-03-11 04:00 | 45 | 39 |  |  | 43170.1667 | 52 | 50
2018-03-11 04:30 | 46 | 40 |  |  | 43170.1875 | 53 | 50
2018-03-11 05:00 | 46 | 41 |  |  | 43170.2083 | 54 | 52
2018-03-11 05:30 | 46 | 41 |  |  | 43170.2292 | 54 | 52
2018-03-11 06:00 | 46 | 41 |  |  | 43170.25 | 54 | 52
2018-03-11 06:30 | 45 | 40 |  |  | 43170.2708 | 54 | 52
2018-03-11 07:00 | 47 | 42 |  |  | 43170.2917 | 58 | 56
2018-03-11 07:30 | 48 | 44 |  |  | 43170.3125 | 59 | 57
2018-03-11 08:00 | 50 | 46 |  |  | 43170.3333 | 63 | 61
2018-03-11 08:30 | 49 | 46 |  |  | 43170.3542 | 62 | 60
2018-03-11 09:00 | 50 | 47 |  |  | 43170.375 | 64 | 63
2018-03-11 09:30 | 53 | 51 |  |  | 43170.3958 | 71 | 71
2018-03-11 10:00 | 57 | 55 |  |  | 43170.4167 | 73 | 72
2018-03-11 10:30 | 57 | 55 |  |  | 43170.4375 | 71 | 70
2018-03-11 11:00 | 54 | 52 |  |  | 43170.4583 | 66 | 65
2018-03-11 11:30 | 55 | 54 |  |  | 43170.4792 | 66 | 66
2018-03-11 12:00 | 53 | 51 |  |  | 43170.5 | 68 | 68
2018-03-11 12:30 | 49 | 47 |  |  | 43170.5208 | 66 | 66
2018-03-11 13:00 | 56 | 55 |  |  | 43170.5417 | 67 | 67
2018-03-11 13:30 | 56 | 54 |  |  | 43170.5625 | 70 | 70
2018-03-11 14:00 | 54 | 53 |  |  | 43170.5833 | 69 | 69
2018-03-11 14:30 | 60 | 58 |  |  | 43170.6042 | 74 | 74
2018-03-11 15:00 | 60 | 59 |  |  | 43170.625 | 68 | 68
2018-03-11 15:30 | 56 | 55 |  |  | 43170.6458 | 68 | 67
2018-03-11 16:00 | 59 | 57 |  |  | 43170.6667 | 72 | 71
2018-03-11 16:30 | 62 | 60 |  |  | 43170.6875 | 78 | 78
2018-03-11 17:00 | 64 | 63 |  |  | 43170.7083 | 79 | 78
2018-03-11 17:30 | 63 | 62 |  |  | 43170.7292 | 76 | 76
2018-03-11 18:00 | 64 | 63 |  |  | 43170.75 | 78 | 78
2018-03-11 18:30 | 66 | 65 |  |  | 43170.7708 | 81 | 80
2018-03-11 19:00 | 69 | 68 |  |  | 43170.7917 | 84 | 83
2018-03-11 19:30 | 70 | 68 |  |  | 43170.8125 | 83 | 82
2018-03-11 20:00 | 69 | 66 |  |  | 43170.8333 | 83 | 82
2018-03-11 20:30 | 68 | 67 |  |  | 43170.8542 | 83 | 82
2018-03-11 21:00 | 65 | 63 |  |  | 43170.875 | 78 | 77
2018-03-11 21:30 | 65 | 62 |  |  | 43170.8958 | 77 | 76
2018-03-11 22:00 | 64 | 62 |  |  | 43170.9167 | 77 | 76
2018-03-11 22:30 | 64 | 61 |  |  | 43170.9375 | 77 | 76
2018-03-11 23:00 | 64 | 61 |  |  | 43170.9583 | 76 | 75
2018-03-11 23:30 | 63 | 59 |  |  | 43170.9792 | 74 | 72
2018-03-12 | 59 | 55 |  |  | 43171 | 69 | 67
2018-03-12 00:30 | 54 | 50 |  |  | 43171.0208 | 64 | 61
2018-03-12 01:00 | 52 | 46 |  |  | 43171.0417 | 60 | 57
2018-03-12 01:30 | 50 | 45 |  |  | 43171.0625 | 58 | 55
2018-03-12 02:00 | 50 | 45 |  |  | 43171.0833 | 58 | 56
2018-03-12 02:30 | 51 | 46 |  |  | 43171.1042 | 58 | 55
2018-03-12 03:00 | 49 | 44 |  |  | 43171.125 | 57 | 54
2018-03-12 03:30 | 49 | 44 |  |  | 43171.1458 | 57 | 55
2018-03-12 04:00 | 51 | 46 |  |  | 43171.1667 | 58 | 56
2018-03-12 04:30 | 51 | 46 |  |  | 43171.1875 | 59 | 57
2018-03-12 05:00 | 53 | 48 |  |  | 43171.2083 | 60 | 58
2018-03-12 05:30 | 52 | 49 |  |  | 43171.2292 | 62 | 61
2018-03-12 06:00 | 57 | 55 |  |  | 43171.25 | 67 | 67
2018-03-12 06:30 | 62 | 61 |  |  | 43171.2708 | 77 | 77
2018-03-12 07:00 | 71 | 70 |  |  | 43171.2917 | 88 | 88
2018-03-12 07:30 | 76 | 76 |  |  | 43171.3125 | 98 | 98
2018-03-12 08:00 | 75 | 75 |  |  | 43171.3333 | 96 | 96
2018-03-12 08:30 | 75 | 75 |  |  | 43171.3542 | 97 | 97
2018-03-12 09:00 | 75 | 75 |  |  | 43171.375 | 97 | 97
2018-03-12 09:30 | 76 | 76 |  |  | 43171.3958 | 98 | 97
2018-03-12 10:00 | 79 | 79 |  |  | 43171.4167 | 105 | 104
2018-03-12 10:30 | 81 | 81 |  |  | 43171.4375 | 105 | 105
2018-03-12 11:00 | 80 | 80 |  |  | 43171.4583 | 106 | 106
2018-03-12 11:30 | 77 | 77 |  |  | 43171.4792 | 104 | 103
2018-03-12 12:00 | 74 | 73 |  |  | 43171.5 | 98 | 98
2018-03-12 12:30 | 85 | 85 |  |  | 43171.5208 | 105 | 105
2018-03-12 13:00 | 78 | 78 |  |  | 43171.5417 | 106 | 106
2018-03-12 13:30 | 82 | 82 |  |  | 43171.5625 | 108 | 108
2018-03-12 14:00 | 83 | 83 |  |  | 43171.5833 | 109 | 109
2018-03-12 14:30 | 85 | 85 |  |  | 43171.6042 | 109 | 109
2018-03-12 15:00 | 82 | 82 |  |  | 43171.625 | 103 | 103
2018-03-12 15:30 | 83 | 83 |  |  | 43171.6458 | 104 | 104
2018-03-12 16:00 | 86 | 86 |  |  | 43171.6667 | 108 | 108
2018-03-12 16:30 | 88 | 88 |  |  | 43171.6875 | 108 | 107
2018-03-12 17:00 | 90 | 90 |  |  | 43171.7083 | 107 | 107
2018-03-12 17:30 | 90 | 90 |  |  | 43171.7292 | 106 | 105
2018-03-12 18:00 | 90 | 90 |  |  | 43171.75 | 105 | 104
2018-03-12 18:30 | 90 | 90 |  |  | 43171.7708 | 104 | 104
2018-03-12 19:00 | 92 | 92 |  |  | 43171.7917 | 107 | 107
2018-03-12 19:30 | 90 | 90 |  |  | 43171.8125 | 104 | 104
2018-03-12 20:00 | 87 | 87 |  |  | 43171.8333 | 100 | 100
2018-03-12 20:30 | 85 | 85 |  |  | 43171.8542 | 99 | 99
2018-03-12 21:00 | 82 | 82 |  |  | 43171.875 | 95 | 95
2018-03-12 21:30 | 77 | 77 |  |  | 43171.8958 | 89 | 89
2018-03-12 22:00 | 74 | 74 |  |  | 43171.9167 | 88 | 88
2018-03-12 22:30 | 72 | 72 |  |  | 43171.9375 | 84 | 84
2018-03-12 23:00 | 69 | 68 |  |  | 43171.9583 | 79 | 79
2018-03-12 23:30 | 64 | 62 |  |  | 43171.9792 | 73 | 72
2018-03-13 | 60 | 58 |  |  | 43172 | 69 | 69
2018-03-13 00:30 | 56 | 54 |  |  | 43172.0208 | 66 | 65
2018-03-13 01:00 | 53 | 50 |  |  | 43172.0417 | 61 | 60
2018-03-13 01:30 | 50 | 47 |  |  | 43172.0625 | 59 | 57
2018-03-13 02:00 | 50 | 47 |  |  | 43172.0833 | 58 | 57
2018-03-13 02:30 | 50 | 46 |  |  | 43172.1042 | 58 | 56
2018-03-13 03:00 | 50 | 46 |  |  | 43172.125 | 57 | 56
2018-03-13 03:30 | 49 | 45 |  |  | 43172.1458 | 57 | 55
2018-03-13 04:00 | 49 | 45 |  |  | 43172.1667 | 57 | 55
2018-03-13 04:30 | 50 | 46 |  |  | 43172.1875 | 58 | 56
2018-03-13 05:00 | 52 | 49 |  |  | 43172.2083 | 60 | 59
2018-03-13 05:30 | 54 | 51 |  |  | 43172.2292 | 63 | 62
2018-03-13 06:00 | 57 | 55 |  |  | 43172.25 | 69 | 68
2018-03-13 06:30 | 62 | 61 |  |  | 43172.2708 | 79 | 79
2018-03-13 07:00 | 70 | 69 |  |  | 43172.2917 | 89 | 88
2018-03-13 07:30 | 76 | 75 |  |  | 43172.3125 | 97 | 97
2018-03-13 08:00 | 76 | 75 |  |  | 43172.3333 | 98 | 98
2018-03-13 08:30 | 80 | 79 |  |  | 43172.3542 | 107 | 106
2018-03-13 09:00 | 81 | 79 |  |  | 43172.375 | 109 | 108
2018-03-13 09:30 | 85 | 83 |  |  | 43172.3958 | 113 | 113
2018-03-13 10:00 | 87 | 85 |  |  | 43172.4167 | 116 | 115
2018-03-13 10:30 | 87 | 86 |  |  | 43172.4375 | 116 | 115
2018-03-13 11:00 | 89 | 88 |  |  | 43172.4583 | 115 | 114
2018-03-13 11:30 | 87 | 85 |  |  | 43172.4792 | 114 | 113
2018-03-13 12:00 | 84 | 83 |  |  | 43172.5 | 112 | 111
2018-03-13 12:30 | 82 | 80 |  |  | 43172.5208 | 107 | 106
2018-03-13 13:00 | 85 | 84 |  |  | 43172.5417 | 111 | 110
2018-03-13 13:30 | 84 | 82 |  |  | 43172.5625 | 110 | 109
2018-03-13 14:00 | 84 | 82 |  |  | 43172.5833 | 109 | 108
2018-03-13 14:30 | 84 | 81 |  |  | 43172.6042 | 109 | 108
2018-03-13 15:00 | 84 | 82 |  |  | 43172.625 | 111 | 110
2018-03-13 15:30 | 87 | 85 |  |  | 43172.6458 | 112 | 111
2018-03-13 16:00 | 89 | 86 |  |  | 43172.6667 | 114 | 112
2018-03-13 16:30 | 89 | 87 |  |  | 43172.6875 | 113 | 112
2018-03-13 17:00 | 90 | 88 |  |  | 43172.7083 | 113 | 112
2018-03-13 17:30 | 88 | 86 |  |  | 43172.7292 | 108 | 107
2018-03-13 18:00 | 86 | 84 |  |  | 43172.75 | 105 | 104
2018-03-13 18:30 | 87 | 85 |  |  | 43172.7708 | 105 | 103
2018-03-13 19:00 | 89 | 86 |  |  | 43172.7917 | 109 | 106
2018-03-13 19:30 | 87 | 85 |  |  | 43172.8125 | 106 | 103
2018-03-13 20:00 | 87 | 84 |  |  | 43172.8333 | 104 | 101
2018-03-13 20:30 | 87 | 85 |  |  | 43172.8542 | 104 | 101
2018-03-13 21:00 | 84 | 83 |  |  | 43172.875 | 100 | 99
2018-03-13 21:30 | 79 | 77 |  |  | 43172.8958 | 94 | 93
2018-03-13 22:00 | 78 | 76 |  |  | 43172.9167 | 94 | 92
2018-03-13 22:30 | 72 | 71 |  |  | 43172.9375 | 88 | 87
2018-03-13 23:00 | 69 | 68 |  |  | 43172.9583 | 84 | 83
2018-03-13 23:30 | 66 | 64 |  |  | 43172.9792 | 80 | 79
2018-03-14 | 61 | 58 |  |  | 43173 | 75 | 73
2018-03-14 00:30 | 56 | 53 |  |  | 43173.0208 | 68 | 66
2018-03-14 01:00 | 52 | 48 |  |  | 43173.0417 | 63 | 60
2018-03-14 01:30 | 50 | 46 |  |  | 43173.0625 | 61 | 58
2018-03-14 02:00 | 50 | 45 |  |  | 43173.0833 | 61 | 58
2018-03-14 02:30 | 52 | 48 |  |  | 43173.1042 | 62 | 59
2018-03-14 03:00 | 53 | 49 |  |  | 43173.125 | 64 | 61
2018-03-14 03:30 | 53 | 48 |  |  | 43173.1458 | 63 | 60
2018-03-14 04:00 | 53 | 48 |  |  | 43173.1667 | 63 | 60
2018-03-14 04:30 | 53 | 48 |  |  | 43173.1875 | 63 | 60
2018-03-14 05:00 | 56 | 52 |  |  | 43173.2083 | 66 | 63
2018-03-14 05:30 | 60 | 57 |  |  | 43173.2292 | 71 | 70
2018-03-14 06:00 | 65 | 63 |  |  | 43173.25 | 79 | 78
2018-03-14 06:30 | 69 | 68 |  |  | 43173.2708 | 89 | 88
2018-03-14 07:00 | 77 | 76 |  |  | 43173.2917 | 98 | 97
2018-03-14 07:30 | 83 | 83 |  |  | 43173.3125 | 109 | 108
2018-03-14 08:00 | 85 | 85 |  |  | 43173.3333 | 109 | 109
2018-03-14 08:30 | 87 | 86 |  |  | 43173.3542 | 112 | 112
2018-03-14 09:00 | 85 | 85 |  |  | 43173.375 | 109 | 109
2018-03-14 09:30 | 85 | 84 |  |  | 43173.3958 | 111 | 111
2018-03-14 10:00 | 84 | 84 |  |  | 43173.4167 | 111 | 111
2018-03-14 10:30 | 81 | 81 |  |  | 43173.4375 | 105 | 105
2018-03-14 11:00 | 82 | 82 |  |  | 43173.4583 | 107 | 107
2018-03-14 11:30 | 88 | 88 |  |  | 43173.4792 | 113 | 113
2018-03-14 12:00 | 83 | 83 |  |  | 43173.5 | 108 | 108
2018-03-14 12:30 | 78 | 78 |  |  | 43173.5208 | 100 | 100
2018-03-14 13:00 | 79 | 79 |  |  | 43173.5417 | 101 | 101
2018-03-14 13:30 | 81 | 81 |  |  | 43173.5625 | 102 | 102
2018-03-14 14:00 | 78 | 78 |  |  | 43173.5833 | 99 | 99
2018-03-14 14:30 | 77 | 77 |  |  | 43173.6042 | 97 | 97
2018-03-14 15:00 | 78 | 78 |  |  | 43173.625 | 99 | 99
2018-03-14 15:30 | 78 | 78 |  |  | 43173.6458 | 100 | 100
2018-03-14 16:00 | 79 | 79 |  |  | 43173.6667 | 102 | 101
2018-03-14 16:30 | 84 | 83 |  |  | 43173.6875 | 104 | 104
2018-03-14 17:00 | 87 | 86 |  |  | 43173.7083 | 106 | 106
2018-03-14 17:30 | 88 | 87 |  |  | 43173.7292 | 105 | 105
2018-03-14 18:00 | 86 | 86 |  |  | 43173.75 | 102 | 102
2018-03-14 18:30 | 87 | 86 |  |  | 43173.7708 | 102 | 102
2018-03-14 19:00 | 88 | 88 |  |  | 43173.7917 | 102 | 102
2018-03-14 19:30 | 87 | 87 |  |  | 43173.8125 | 101 | 100
2018-03-14 20:00 | 87 | 86 |  |  | 43173.8333 | 100 | 99
2018-03-14 20:30 | 86 | 85 |  |  | 43173.8542 | 98 | 97
2018-03-14 21:00 | 82 | 82 |  |  | 43173.875 | 93 | 93
2018-03-14 21:30 | 78 | 78 |  |  | 43173.8958 | 90 | 89
2018-03-14 22:00 | 78 | 78 |  |  | 43173.9167 | 89 | 89
2018-03-14 22:30 | 73 | 72 |  |  | 43173.9375 | 84 | 84
2018-03-14 23:00 | 70 | 68 |  |  | 43173.9583 | 80 | 79
2018-03-14 23:30 | 65 | 63 |  |  | 43173.9792 | 75 | 74
2018-03-15 | 59 | 57 |  |  | 43174 | 69 | 68
2018-03-15 00:30 | 56 | 53 |  |  | 43174.0208 | 65 | 63
2018-03-15 01:00 | 53 | 49 |  |  | 43174.0417 | 61 | 59
2018-03-15 01:30 | 53 | 49 |  |  | 43174.0625 | 61 | 59
2018-03-15 02:00 | 53 | 49 |  |  | 43174.0833 | 61 | 58
2018-03-15 02:30 | 54 | 49 |  |  | 43174.1042 | 60 | 57
2018-03-15 03:00 | 53 | 48 |  |  | 43174.125 | 59 | 56
2018-03-15 03:30 | 52 | 47 |  |  | 43174.1458 | 59 | 56
2018-03-15 04:00 | 52 | 47 |  |  | 43174.1667 | 58 | 55
2018-03-15 04:30 | 52 | 47 |  |  | 43174.1875 | 59 | 56
2018-03-15 05:00 | 54 | 50 |  |  | 43174.2083 | 60 | 58
2018-03-15 05:30 | 57 | 54 |  |  | 43174.2292 | 65 | 63
2018-03-15 06:00 | 60 | 58 |  |  | 43174.25 | 71 | 70
2018-03-15 06:30 | 64 | 63 |  |  | 43174.2708 | 79 | 79
2018-03-15 07:00 | 72 | 71 |  |  | 43174.2917 | 89 | 89
2018-03-15 07:30 | 75 | 75 |  |  | 43174.3125 | 94 | 94
2018-03-15 08:00 | 76 | 76 |  |  | 43174.3333 | 96 | 96
2018-03-15 08:30 | 75 | 75 |  |  | 43174.3542 | 96 | 96
2018-03-15 09:00 | 75 | 75 |  |  | 43174.375 | 94 | 94
2018-03-15 09:30 | 78 | 77 |  |  | 43174.3958 | 101 | 101
2018-03-15 10:00 | 75 | 75 |  |  | 43174.4167 | 98 | 98
2018-03-15 10:30 | 73 | 73 |  |  | 43174.4375 | 92 | 92
2018-03-15 11:00 | 74 | 73 |  |  | 43174.4583 | 93 | 93
2018-03-15 11:30 | 77 | 76 |  |  | 43174.4792 | 97 | 97
2018-03-15 12:00 | 77 | 77 |  |  | 43174.5 | 95 | 95
2018-03-15 12:30 | 76 | 75 |  |  | 43174.5208 | 97 | 97
2018-03-15 13:00 | 75 | 74 |  |  | 43174.5417 | 96 | 96
2018-03-15 13:30 | 76 | 74 |  |  | 43174.5625 | 98 | 97
2018-03-15 14:00 | 77 | 74 |  |  | 43174.5833 | 99 | 97
2018-03-15 14:30 | 77 | 75 |  |  | 43174.6042 | 98 | 96
2018-03-15 15:00 | 77 | 75 |  |  | 43174.625 | 99 | 97
2018-03-15 15:30 | 79 | 76 |  |  | 43174.6458 | 99 | 97
2018-03-15 16:00 | 82 | 80 |  |  | 43174.6667 | 101 | 99
2018-03-15 16:30 | 85 | 83 |  |  | 43174.6875 | 105 | 103
2018-03-15 17:00 | 87 | 85 |  |  | 43174.7083 | 107 | 104
2018-03-15 17:30 | 88 | 85 |  |  | 43174.7292 | 107 | 103
2018-03-15 18:00 | 88 | 84 |  |  | 43174.75 | 105 | 101
2018-03-15 18:30 | 87 | 82 |  |  | 43174.7708 | 102 | 98
2018-03-15 19:00 | 87 | 84 |  |  | 43174.7917 | 102 | 98
2018-03-15 19:30 | 85 | 82 |  |  | 43174.8125 | 100 | 96
2018-03-15 20:00 | 86 | 82 |  |  | 43174.8333 | 99 | 95
2018-03-15 20:30 | 84 | 81 |  |  | 43174.8542 | 97 | 94
2018-03-15 21:00 | 83 | 78 |  |  | 43174.875 | 94 | 90
2018-03-15 21:30 | 81 | 75 |  |  | 43174.8958 | 92 | 87
2018-03-15 22:00 | 78 | 73 |  |  | 43174.9167 | 89 | 85
2018-03-15 22:30 | 71 | 68 |  |  | 43174.9375 | 81 | 80
2018-03-15 23:00 | 68 | 65 |  |  | 43174.9583 | 77 | 75
2018-03-15 23:30 | 66 | 63 |  |  | 43174.9792 | 74 | 73
2018-03-16 | 60 | 57 |  |  | 43175 | 69 | 68
2018-03-16 00:30 | 55 | 51 |  |  | 43175.0208 | 63 | 61
2018-03-16 01:00 | 52 | 47 |  |  | 43175.0417 | 59 | 56
2018-03-16 01:30 | 52 | 47 |  |  | 43175.0625 | 58 | 55
2018-03-16 02:00 | 50 | 46 |  |  | 43175.0833 | 57 | 54
2018-03-16 02:30 | 49 | 45 |  |  | 43175.1042 | 57 | 54
2018-03-16 03:00 | 49 | 45 |  |  | 43175.125 | 56 | 53
2018-03-16 03:30 | 49 | 45 |  |  | 43175.1458 | 55 | 52
2018-03-16 04:00 | 49 | 45 |  |  | 43175.1667 | 56 | 53
2018-03-16 04:30 | 50 | 46 |  |  | 43175.1875 | 58 | 55
2018-03-16 05:00 | 54 | 51 |  |  | 43175.2083 | 62 | 59
2018-03-16 05:30 | 57 | 54 |  |  | 43175.2292 | 66 | 64
2018-03-16 06:00 | 58 | 56 |  |  | 43175.25 | 68 | 67
2018-03-16 06:30 | 62 | 60 |  |  | 43175.2708 | 75 | 75
2018-03-16 07:00 | 66 | 65 |  |  | 43175.2917 | 83 | 83
2018-03-16 07:30 | 71 | 70 |  |  | 43175.3125 | 90 | 90
2018-03-16 08:00 | 70 | 69 |  |  | 43175.3333 | 90 | 90
2018-03-16 08:30 | 69 | 69 |  |  | 43175.3542 | 89 | 89
2018-03-16 09:00 | 70 | 69 |  |  | 43175.375 | 91 | 90
2018-03-16 09:30 | 68 | 67 |  |  | 43175.3958 | 89 | 89
2018-03-16 10:00 | 66 | 65 |  |  | 43175.4167 | 87 | 87
2018-03-16 10:30 | 66 | 65 |  |  | 43175.4375 | 86 | 86
2018-03-16 11:00 | 67 | 66 |  |  | 43175.4583 | 86 | 85
2018-03-16 11:30 | 69 | 68 |  |  | 43175.4792 | 89 | 88
2018-03-16 12:00 | 70 | 69 |  |  | 43175.5 | 89 | 89
2018-03-16 12:30 | 71 | 70 |  |  | 43175.5208 | 91 | 91
2018-03-16 13:00 | 70 | 69 |  |  | 43175.5417 | 90 | 90
2018-03-16 13:30 | 70 | 70 |  |  | 43175.5625 | 92 | 92
2018-03-16 14:00 | 74 | 74 |  |  | 43175.5833 | 96 | 96
2018-03-16 14:30 | 78 | 78 |  |  | 43175.6042 | 98 | 98
2018-03-16 15:00 | 80 | 80 |  |  | 43175.625 | 101 | 101
2018-03-16 15:30 | 83 | 83 |  |  | 43175.6458 | 103 | 103
2018-03-16 16:00 | 86 | 86 |  |  | 43175.6667 | 106 | 106
2018-03-16 16:30 | 88 | 88 |  |  | 43175.6875 | 108 | 108
2018-03-16 17:00 | 91 | 91 |  |  | 43175.7083 | 111 | 110
2018-03-16 17:30 | 90 | 90 |  |  | 43175.7292 | 108 | 107
2018-03-16 18:00 | 87 | 86 |  |  | 43175.75 | 104 | 102
2018-03-16 18:30 | 84 | 83 |  |  | 43175.7708 | 100 | 98
2018-03-16 19:00 | 86 | 85 |  |  | 43175.7917 | 102 | 100
2018-03-16 19:30 | 84 | 82 |  |  | 43175.8125 | 99 | 97
2018-03-16 20:00 | 82 | 80 |  |  | 43175.8333 | 96 | 94
2018-03-16 20:30 | 80 | 78 |  |  | 43175.8542 | 93 | 91
2018-03-16 21:00 | 77 | 75 |  |  | 43175.875 | 90 | 88
2018-03-16 21:30 | 74 | 71 |  |  | 43175.8958 | 87 | 84
2018-03-16 22:00 | 72 | 70 |  |  | 43175.9167 | 86 | 84
2018-03-16 22:30 | 71 | 69 |  |  | 43175.9375 | 84 | 83
2018-03-16 23:00 | 68 | 66 |  |  | 43175.9583 | 79 | 79
2018-03-16 23:30 | 63 | 60 |  |  | 43175.9792 | 74 | 73
2018-03-17 | 60 | 58 |  |  | 43176 | 70 | 70
2018-03-17 00:30 | 58 | 54 |  |  | 43176.0208 | 67 | 65
2018-03-17 01:00 | 55 | 51 |  |  | 43176.0417 | 62 | 61
2018-03-17 01:30 | 51 | 47 |  |  | 43176.0625 | 59 | 57
2018-03-17 02:00 | 52 | 47 |  |  | 43176.0833 | 59 | 57
2018-03-17 02:30 | 52 | 47 |  |  | 43176.1042 | 59 | 56
2018-03-17 03:00 | 51 | 47 |  |  | 43176.125 | 59 | 57
2018-03-17 03:30 | 50 | 45 |  |  | 43176.1458 | 59 | 56
2018-03-17 04:00 | 50 | 45 |  |  | 43176.1667 | 58 | 55
2018-03-17 04:30 | 49 | 45 |  |  | 43176.1875 | 57 | 54
2018-03-17 05:00 | 50 | 45 |  |  | 43176.2083 | 57 | 55
2018-03-17 05:30 | 50 | 45 |  |  | 43176.2292 | 57 | 55
2018-03-17 06:00 | 49 | 44 |  |  | 43176.25 | 57 | 55
2018-03-17 06:30 | 51 | 46 |  |  | 43176.2708 | 60 | 58
2018-03-17 07:00 | 52 | 48 |  |  | 43176.2917 | 64 | 62
2018-03-17 07:30 | 52 | 50 |  |  | 43176.3125 | 65 | 64
2018-03-17 08:00 | 57 | 55 |  |  | 43176.3333 | 73 | 72
2018-03-17 08:30 | 58 | 56 |  |  | 43176.3542 | 74 | 74
2018-03-17 09:00 | 59 | 58 |  |  | 43176.375 | 76 | 76
2018-03-17 09:30 | 59 | 58 |  |  | 43176.3958 | 77 | 77
2018-03-17 10:00 | 61 | 60 |  |  | 43176.4167 | 78 | 78
2018-03-17 10:30 | 61 | 59 |  |  | 43176.4375 | 77 | 76
2018-03-17 11:00 | 61 | 59 |  |  | 43176.4583 | 77 | 77
2018-03-17 11:30 | 61 | 60 |  |  | 43176.4792 | 77 | 76
2018-03-17 12:00 | 62 | 60 |  |  | 43176.5 | 78 | 77
2018-03-17 12:30 | 62 | 61 |  |  | 43176.5208 | 79 | 78
2018-03-17 13:00 | 63 | 62 |  |  | 43176.5417 | 79 | 78
2018-03-17 13:30 | 63 | 62 |  |  | 43176.5625 | 78 | 77
2018-03-17 14:00 | 66 | 64 |  |  | 43176.5833 | 80 | 79
2018-03-17 14:30 | 67 | 66 |  |  | 43176.6042 | 80 | 80
2018-03-17 15:00 | 68 | 67 |  |  | 43176.625 | 83 | 82
2018-03-17 15:30 | 71 | 70 |  |  | 43176.6458 | 85 | 85
2018-03-17 16:00 | 75 | 74 |  |  | 43176.6667 | 90 | 89
2018-03-17 16:30 | 78 | 76 |  |  | 43176.6875 | 91 | 90
2018-03-17 17:00 | 78 | 76 |  |  | 43176.7083 | 89 | 89
2018-03-17 17:30 | 79 | 77 |  |  | 43176.7292 | 88 | 87
2018-03-17 18:00 | 79 | 76 |  |  | 43176.75 | 89 | 88
2018-03-17 18:30 | 80 | 78 |  |  | 43176.7708 | 92 | 92
2018-03-17 19:00 | 79 | 77 |  |  | 43176.7917 | 93 | 93
2018-03-17 19:30 | 79 | 77 |  |  | 43176.8125 | 92 | 92
2018-03-17 20:00 | 77 | 76 |  |  | 43176.8333 | 90 | 90
2018-03-17 20:30 | 75 | 74 |  |  | 43176.8542 | 89 | 88
2018-03-17 21:00 | 72 | 71 |  |  | 43176.875 | 85 | 85
2018-03-17 21:30 | 69 | 68 |  |  | 43176.8958 | 82 | 82
2018-03-17 22:00 | 71 | 70 |  |  | 43176.9167 | 86 | 85
2018-03-17 22:30 | 67 | 65 |  |  | 43176.9375 | 81 | 80
2018-03-17 23:00 | 64 | 62 |  |  | 43176.9583 | 76 | 75
2018-03-17 23:30 | 63 | 61 |  |  | 43176.9792 | 76 | 75
2018-03-18 | 60 | 57 |  |  | 43177 | 71 | 70
2018-03-18 00:30 | 59 | 55 |  |  | 43177.0208 | 67 | 65
2018-03-18 01:00 | 55 | 51 |  |  | 43177.0417 | 63 | 61
2018-03-18 01:30 | 54 | 48 |  |  | 43177.0625 | 62 | 59
2018-03-18 02:00 | 54 | 49 |  |  | 43177.0833 | 61 | 59
2018-03-18 02:30 | 54 | 48 |  |  | 43177.1042 | 61 | 58
2018-03-18 03:00 | 53 | 47 |  |  | 43177.125 | 59 | 56
2018-03-18 03:30 | 52 | 46 |  |  | 43177.1458 | 59 | 56
2018-03-18 04:00 | 51 | 45 |  |  | 43177.1667 | 59 | 55
2018-03-18 04:30 | 51 | 45 |  |  | 43177.1875 | 56 | 53
2018-03-18 05:00 | 50 | 44 |  |  | 43177.2083 | 57 | 54
2018-03-18 05:30 | 53 | 48 |  |  | 43177.2292 | 60 | 57
2018-03-18 06:00 | 52 | 46 |  |  | 43177.25 | 60 | 56
2018-03-18 06:30 | 51 | 45 |  |  | 43177.2708 | 60 | 56
2018-03-18 07:00 | 52 | 46 |  |  | 43177.2917 | 60 | 57
2018-03-18 07:30 | 61 | 56 |  |  | 43177.3125 | 72 | 69
2018-03-18 08:00 | 66 | 61 |  |  | 43177.3333 | 75 | 73
2018-03-18 08:30 | 67 | 63 |  |  | 43177.3542 | 77 | 75
2018-03-18 09:00 | 65 | 62 |  |  | 43177.375 | 75 | 74
2018-03-18 09:30 | 65 | 63 |  |  | 43177.3958 | 78 | 77
2018-03-18 10:00 | 71 | 69 |  |  | 43177.4167 | 82 | 81
2018-03-18 10:30 | 72 | 70 |  |  | 43177.4375 | 83 | 82
2018-03-18 11:00 | 69 | 67 |  |  | 43177.4583 | 81 | 81
2018-03-18 11:30 | 69 | 68 |  |  | 43177.4792 | 81 | 81
2018-03-18 12:00 | 70 | 69 |  |  | 43177.5 | 83 | 83
2018-03-18 12:30 | 72 | 71 |  |  | 43177.5208 | 85 | 85
2018-03-18 13:00 | 71 | 69 |  |  | 43177.5417 | 82 | 80
2018-03-18 13:30 | 72 | 70 |  |  | 43177.5625 | 83 | 82
2018-03-18 14:00 | 72 | 70 |  |  | 43177.5833 | 81 | 80
2018-03-18 14:30 | 75 | 73 |  |  | 43177.6042 | 84 | 82
2018-03-18 15:00 | 76 | 74 |  |  | 43177.625 | 86 | 84
2018-03-18 15:30 | 79 | 77 |  |  | 43177.6458 | 88 | 87
2018-03-18 16:00 | 79 | 77 |  |  | 43177.6667 | 88 | 87
2018-03-18 16:30 | 85 | 83 |  |  | 43177.6875 | 94 | 93
2018-03-18 17:00 | 87 | 85 |  |  | 43177.7083 | 98 | 96
2018-03-18 17:30 | 87 | 85 |  |  | 43177.7292 | 98 | 94
2018-03-18 18:00 | 87 | 85 |  |  | 43177.75 | 99 | 96
2018-03-18 18:30 | 88 | 85 |  |  | 43177.7708 | 99 | 97
2018-03-18 19:00 | 90 | 88 |  |  | 43177.7917 | 104 | 101
2018-03-18 19:30 | 89 | 87 |  |  | 43177.8125 | 101 | 100
2018-03-18 20:00 | 86 | 85 |  |  | 43177.8333 | 98 | 98
2018-03-18 20:30 | 83 | 82 |  |  | 43177.8542 | 96 | 95
2018-03-18 21:00 | 79 | 77 |  |  | 43177.875 | 92 | 91
2018-03-18 21:30 | 77 | 76 |  |  | 43177.8958 | 90 | 90
2018-03-18 22:00 | 78 | 76 |  |  | 43177.9167 | 91 | 90
2018-03-18 22:30 | 75 | 72 |  |  | 43177.9375 | 89 | 88
2018-03-18 23:00 | 73 | 71 |  |  | 43177.9583 | 85 | 85
2018-03-18 23:30 | 67 | 64 |  |  | 43177.9792 | 79 | 78
2018-03-19 | 63 | 60 |  |  | 43178 | 73 | 73
2018-03-19 00:30 | 59 | 56 |  |  | 43178.0208 | 69 | 69
2018-03-19 01:00 | 57 | 54 |  |  | 43178.0417 | 67 | 66
2018-03-19 01:30 | 55 | 52 |  |  | 43178.0625 | 64 | 63
2018-03-19 02:00 | 55 | 51 |  |  | 43178.0833 | 63 | 62
2018-03-19 02:30 | 54 | 50 |  |  | 43178.1042 | 62 | 60
2018-03-19 03:00 | 53 | 48 |  |  | 43178.125 | 61 | 60
2018-03-19 03:30 | 52 | 48 |  |  | 43178.1458 | 60 | 59
2018-03-19 04:00 | 52 | 47 |  |  | 43178.1667 | 59 | 58
2018-03-19 04:30 | 50 | 46 |  |  | 43178.1875 | 59 | 58
2018-03-19 05:00 | 52 | 49 |  |  | 43178.2083 | 60 | 60
2018-03-19 05:30 | 55 | 52 |  |  | 43178.2292 | 64 | 64
2018-03-19 06:00 | 59 | 58 |  |  | 43178.25 | 71 | 70
2018-03-19 06:30 | 65 | 64 |  |  | 43178.2708 | 81 | 81
2018-03-19 07:00 | 71 | 69 |  |  | 43178.2917 | 89 | 88
2018-03-19 07:30 | 79 | 78 |  |  | 43178.3125 | 99 | 99
2018-03-19 08:00 | 82 | 80 |  |  | 43178.3333 | 104 | 104
2018-03-19 08:30 | 84 | 82 |  |  | 43178.3542 | 106 | 105
2018-03-19 09:00 | 84 | 83 |  |  | 43178.375 | 107 | 106
2018-03-19 09:30 | 87 | 87 |  |  | 43178.3958 | 110 | 109
2018-03-19 10:00 | 89 | 88 |  |  | 43178.4167 | 111 | 110
2018-03-19 10:30 | 90 | 90 |  |  | 43178.4375 | 113 | 112
2018-03-19 11:00 | 93 | 92 |  |  | 43178.4583 | 115 | 114
2018-03-19 11:30 | 94 | 94 |  |  | 43178.4792 | 115 | 115
2018-03-19 12:00 | 92 | 92 |  |  | 43178.5 | 114 | 113
2018-03-19 12:30 | 91 | 91 |  |  | 43178.5208 | 113 | 112
2018-03-19 13:00 | 94 | 93 |  |  | 43178.5417 | 114 | 114
2018-03-19 13:30 | 95 | 95 |  |  | 43178.5625 | 116 | 116
2018-03-19 14:00 | 98 | 98 |  |  | 43178.5833 | 119 | 119
2018-03-19 14:30 | 100 | 100 |  |  | 43178.6042 | 120 | 120
2018-03-19 15:00 | 101 | 100 |  |  | 43178.625 | 122 | 122
2018-03-19 15:30 | 103 | 103 |  |  | 43178.6458 | 124 | 124
2018-03-19 16:00 | 106 | 105 |  |  | 43178.6667 | 127 | 127
2018-03-19 16:30 | 107 | 106 |  |  | 43178.6875 | 126 | 126
2018-03-19 17:00 | 108 | 108 |  |  | 43178.7083 | 127 | 126
2018-03-19 17:30 | 106 | 106 |  |  | 43178.7292 | 125 | 123
2018-03-19 18:00 | 104 | 102 |  |  | 43178.75 | 121 | 120
2018-03-19 18:30 | 102 | 101 |  |  | 43178.7708 | 120 | 119
2018-03-19 19:00 | 107 | 106 |  |  | 43178.7917 | 123 | 122
2018-03-19 19:30 | 105 | 104 |  |  | 43178.8125 | 120 | 118
2018-03-19 20:00 | 103 | 102 |  |  | 43178.8333 | 118 | 117
2018-03-19 20:30 | 100 | 99 |  |  | 43178.8542 | 115 | 114
2018-03-19 21:00 | 94 | 93 |  |  | 43178.875 | 107 | 106
2018-03-19 21:30 | 89 | 89 |  |  | 43178.8958 | 101 | 101
2018-03-19 22:00 | 88 | 88 |  |  | 43178.9167 | 102 | 101
2018-03-19 22:30 | 84 | 84 |  |  | 43178.9375 | 98 | 98
2018-03-19 23:00 | 79 | 79 |  |  | 43178.9583 | 93 | 93
2018-03-19 23:30 | 74 | 74 |  |  | 43178.9792 | 88 | 88
2018-03-20 | 69 | 69 |  |  | 43179 | 82 | 82
2018-03-20 00:30 | 64 | 62 |  |  | 43179.0208 | 75 | 75
2018-03-20 01:00 | 62 | 59 |  |  | 43179.0417 | 71 | 71
2018-03-20 01:30 | 59 | 57 |  |  | 43179.0625 | 68 | 68
2018-03-20 02:00 | 58 | 55 |  |  | 43179.0833 | 66 | 66
2018-03-20 02:30 | 56 | 53 |  |  | 43179.1042 | 64 | 64
2018-03-20 03:00 | 55 | 52 |  |  | 43179.125 | 64 | 64
2018-03-20 03:30 | 56 | 53 |  |  | 43179.1458 | 64 | 63
2018-03-20 04:00 | 54 | 52 |  |  | 43179.1667 | 62 | 62
2018-03-20 04:30 | 55 | 52 |  |  | 43179.1875 | 64 | 64
2018-03-20 05:00 | 56 | 54 |  |  | 43179.2083 | 66 | 65
2018-03-20 05:30 | 62 | 61 |  |  | 43179.2292 | 73 | 73
2018-03-20 06:00 | 64 | 63 |  |  | 43179.25 | 77 | 77
2018-03-20 06:30 | 65 | 64 |  |  | 43179.2708 | 82 | 82
2018-03-20 07:00 | 70 | 70 |  |  | 43179.2917 | 89 | 89
2018-03-20 07:30 | 75 | 74 |  |  | 43179.3125 | 96 | 96
2018-03-20 08:00 | 79 | 77 |  |  | 43179.3333 | 101 | 101
2018-03-20 08:30 | 81 | 80 |  |  | 43179.3542 | 106 | 106
2018-03-20 09:00 | 87 | 86 |  |  | 43179.375 | 114 | 113
2018-03-20 09:30 | 88 | 88 |  |  | 43179.3958 | 114 | 114
2018-03-20 10:00 | 90 | 90 |  |  | 43179.4167 | 115 | 115
2018-03-20 10:30 | 81 | 81 |  |  | 43179.4375 | 110 | 109
2018-03-20 11:00 | 72 | 71 |  |  | 43179.4583 | 103 | 102
2018-03-20 11:30 | 72 | 71 |  |  | 43179.4792 | 102 | 101
2018-03-20 12:00 | 69 | 68 |  |  | 43179.5 | 99 | 99
2018-03-20 12:30 | 67 | 66 |  |  | 43179.5208 | 96 | 96
2018-03-20 13:00 | 68 | 67 |  |  | 43179.5417 | 97 | 97
2018-03-20 13:30 | 70 | 69 |  |  | 43179.5625 | 99 | 99
2018-03-20 14:00 | 71 | 70 |  |  | 43179.5833 | 102 | 102
2018-03-20 14:30 | 82 | 82 |  |  | 43179.6042 | 107 | 107
2018-03-20 15:00 | 89 | 89 |  |  | 43179.625 | 112 | 112
2018-03-20 15:30 | 91 | 91 |  |  | 43179.6458 | 115 | 115
2018-03-20 16:00 | 95 | 94 |  |  | 43179.6667 | 118 | 117
2018-03-20 16:30 | 96 | 96 |  |  | 43179.6875 | 118 | 118
2018-03-20 17:00 | 99 | 99 |  |  | 43179.7083 | 120 | 119
2018-03-20 17:30 | 98 | 97 |  |  | 43179.7292 | 118 | 117
2018-03-20 18:00 | 96 | 95 |  |  | 43179.75 | 115 | 113
2018-03-20 18:30 | 94 | 94 |  |  | 43179.7708 | 112 | 111
2018-03-20 19:00 | 97 | 97 |  |  | 43179.7917 | 115 | 114
2018-03-20 19:30 | 96 | 96 |  |  | 43179.8125 | 113 | 112
2018-03-20 20:00 | 95 | 94 |  |  | 43179.8333 | 111 | 109
2018-03-20 20:30 | 92 | 91 |  |  | 43179.8542 | 109 | 108
2018-03-20 21:00 | 87 | 86 |  |  | 43179.875 | 102 | 101
2018-03-20 21:30 | 83 | 83 |  |  | 43179.8958 | 97 | 96
2018-03-20 22:00 | 81 | 81 |  |  | 43179.9167 | 96 | 95
2018-03-20 22:30 | 76 | 75 |  |  | 43179.9375 | 90 | 90
2018-03-20 23:00 | 73 | 72 |  |  | 43179.9583 | 86 | 85
2018-03-20 23:30 | 70 | 68 |  |  | 43179.9792 | 83 | 82
2018-03-21 | 67 | 63 |  |  | 43180 | 79 | 78
2018-03-21 00:30 | 62 | 59 |  |  | 43180.0208 | 75 | 73
2018-03-21 01:00 | 61 | 56 |  |  | 43180.0417 | 71 | 68
2018-03-21 01:30 | 61 | 57 |  |  | 43180.0625 | 70 | 68
2018-03-21 02:00 | 62 | 57 |  |  | 43180.0833 | 70 | 68
2018-03-21 02:30 | 59 | 55 |  |  | 43180.1042 | 69 | 67
2018-03-21 03:00 | 58 | 54 |  |  | 43180.125 | 68 | 66
2018-03-21 03:30 | 59 | 54 |  |  | 43180.1458 | 68 | 66
2018-03-21 04:00 | 57 | 52 |  |  | 43180.1667 | 64 | 62
2018-03-21 04:30 | 54 | 51 |  |  | 43180.1875 | 63 | 62
2018-03-21 05:00 | 54 | 51 |  |  | 43180.2083 | 63 | 62
2018-03-21 05:30 | 57 | 55 |  |  | 43180.2292 | 67 | 66
2018-03-21 06:00 | 60 | 59 |  |  | 43180.25 | 72 | 72
2018-03-21 06:30 | 67 | 66 |  |  | 43180.2708 | 85 | 85
2018-03-21 07:00 | 77 | 75 |  |  | 43180.2917 | 97 | 95
2018-03-21 07:30 | 84 | 82 |  |  | 43180.3125 | 106 | 105
2018-03-21 08:00 | 86 | 85 |  |  | 43180.3333 | 111 | 110
2018-03-21 08:30 | 88 | 86 |  |  | 43180.3542 | 114 | 113
2018-03-21 09:00 | 80 | 78 |  |  | 43180.375 | 113 | 112
2018-03-21 09:30 | 76 | 72 |  |  | 43180.3958 | 109 | 106
2018-03-21 10:00 | 76 | 73 |  |  | 43180.4167 | 110 | 108
2018-03-21 10:30 | 77 | 73 |  |  | 43180.4375 | 107 | 105
2018-03-21 11:00 | 70 | 66 |  |  | 43180.4583 | 100 | 97
2018-03-21 11:30 | 74 | 71 |  |  | 43180.4792 | 107 | 104
2018-03-21 12:00 | 77 | 73 |  |  | 43180.5 | 105 | 102
2018-03-21 12:30 | 73 | 69 |  |  | 43180.5208 | 104 | 101
2018-03-21 13:00 | 72 | 68 |  |  | 43180.5417 | 106 | 103
2018-03-21 13:30 | 76 | 72 |  |  | 43180.5625 | 105 | 102
2018-03-21 14:00 | 89 | 85 |  |  | 43180.5833 | 112 | 108
2018-03-21 14:30 | 90 | 86 |  |  | 43180.6042 | 113 | 110
2018-03-21 15:00 | 92 | 88 |  |  | 43180.625 | 114 | 111
2018-03-21 15:30 | 93 | 89 |  |  | 43180.6458 | 117 | 113
2018-03-21 16:00 | 93 | 88 |  |  | 43180.6667 | 116 | 111
2018-03-21 16:30 | 93 | 89 |  |  | 43180.6875 | 115 | 110
2018-03-21 17:00 | 94 | 89 |  |  | 43180.7083 | 116 | 111
2018-03-21 17:30 | 93 | 90 |  |  | 43180.7292 | 113 | 110
2018-03-21 18:00 | 91 | 89 |  |  | 43180.75 | 109 | 108
2018-03-21 18:30 | 90 | 88 |  |  | 43180.7708 | 106 | 105
2018-03-21 19:00 | 92 | 90 |  |  | 43180.7917 | 108 | 107
2018-03-21 19:30 | 92 | 89 |  |  | 43180.8125 | 107 | 105
2018-03-21 20:00 | 89 | 87 |  |  | 43180.8333 | 104 | 103
2018-03-21 20:30 | 85 | 85 |  |  | 43180.8542 | 100 | 100
2018-03-21 21:00 | 81 | 81 |  |  | 43180.875 | 96 | 96
2018-03-21 21:30 | 78 | 78 |  |  | 43180.8958 | 92 | 92
2018-03-21 22:00 | 78 | 77 |  |  | 43180.9167 | 92 | 92
2018-03-21 22:30 | 72 | 71 |  |  | 43180.9375 | 87 | 86
2018-03-21 23:00 | 69 | 68 |  |  | 43180.9583 | 82 | 82
2018-03-21 23:30 | 66 | 65 |  |  | 43180.9792 | 79 | 78
2018-03-22 | 60 | 59 |  |  | 43181 | 73 | 73
2018-03-22 00:30 | 57 | 55 |  |  | 43181.0208 | 68 | 68
2018-03-22 01:00 | 54 | 53 |  |  | 43181.0417 | 65 | 65
2018-03-22 01:30 | 55 | 53 |  |  | 43181.0625 | 65 | 65
2018-03-22 02:00 | 54 | 53 |  |  | 43181.0833 | 63 | 63
2018-03-22 02:30 | 53 | 51 |  |  | 43181.1042 | 61 | 61
2018-03-22 03:00 | 48 | 46 |  |  | 43181.125 | 57 | 57
2018-03-22 03:30 | 46 | 44 |  |  | 43181.1458 | 54 | 54
2018-03-22 04:00 | 45 | 43 |  |  | 43181.1667 | 54 | 54
2018-03-22 04:30 | 47 | 46 |  |  | 43181.1875 | 57 | 57
2018-03-22 05:00 | 50 | 49 |  |  | 43181.2083 | 60 | 60
2018-03-22 05:30 | 54 | 54 |  |  | 43181.2292 | 66 | 65
2018-03-22 06:00 | 58 | 58 |  |  | 43181.25 | 71 | 71
2018-03-22 06:30 | 65 | 64 |  |  | 43181.2708 | 82 | 82
2018-03-22 07:00 | 71 | 70 |  |  | 43181.2917 | 90 | 90
2018-03-22 07:30 | 76 | 74 |  |  | 43181.3125 | 96 | 96
2018-03-22 08:00 | 76 | 75 |  |  | 43181.3333 | 99 | 99
2018-03-22 08:30 | 79 | 77 |  |  | 43181.3542 | 102 | 102
2018-03-22 09:00 | 82 | 81 |  |  | 43181.375 | 108 | 108
2018-03-22 09:30 | 80 | 80 |  |  | 43181.3958 | 106 | 105
2018-03-22 10:00 | 78 | 78 |  |  | 43181.4167 | 108 | 108
2018-03-22 10:30 | 79 | 78 |  |  | 43181.4375 | 106 | 106
2018-03-22 11:00 | 84 | 83 |  |  | 43181.4583 | 108 | 108
2018-03-22 11:30 | 80 | 80 |  |  | 43181.4792 | 101 | 100
2018-03-22 12:00 | 79 | 79 |  |  | 43181.5 | 102 | 102
2018-03-22 12:30 | 77 | 77 |  |  | 43181.5208 | 100 | 100
2018-03-22 13:00 | 80 | 80 |  |  | 43181.5417 | 107 | 107
2018-03-22 13:30 | 79 | 79 |  |  | 43181.5625 | 104 | 104
2018-03-22 14:00 | 81 | 81 |  |  | 43181.5833 | 106 | 106
2018-03-22 14:30 | 81 | 81 |  |  | 43181.6042 | 107 | 107
2018-03-22 15:00 | 82 | 82 |  |  | 43181.625 | 109 | 109
2018-03-22 15:30 | 83 | 83 |  |  | 43181.6458 | 109 | 109
2018-03-22 16:00 | 87 | 87 |  |  | 43181.6667 | 110 | 110
2018-03-22 16:30 | 88 | 87 |  |  | 43181.6875 | 112 | 112
2018-03-22 17:00 | 89 | 89 |  |  | 43181.7083 | 112 | 112
2018-03-22 17:30 | 86 | 86 |  |  | 43181.7292 | 107 | 107
2018-03-22 18:00 | 85 | 85 |  |  | 43181.75 | 107 | 106
2018-03-22 18:30 | 88 | 88 |  |  | 43181.7708 | 108 | 108
2018-03-22 19:00 | 93 | 92 |  |  | 43181.7917 | 111 | 111
2018-03-22 19:30 | 91 | 91 |  |  | 43181.8125 | 108 | 108
2018-03-22 20:00 | 90 | 90 |  |  | 43181.8333 | 107 | 107
2018-03-22 20:30 | 88 | 87 |  |  | 43181.8542 | 105 | 104
2018-03-22 21:00 | 84 | 84 |  |  | 43181.875 | 99 | 99
2018-03-22 21:30 | 80 | 80 |  |  | 43181.8958 | 93 | 93
2018-03-22 22:00 | 78 | 76 |  |  | 43181.9167 | 92 | 91
2018-03-22 22:30 | 74 | 72 |  |  | 43181.9375 | 87 | 87
2018-03-22 23:00 | 68 | 67 |  |  | 43181.9583 | 80 | 80
2018-03-22 23:30 | 63 | 61 |  |  | 43181.9792 | 75 | 75
2018-03-23 | 59 | 57 |  |  | 43182 | 71 | 71
2018-03-23 00:30 | 55 | 52 |  |  | 43182.0208 | 65 | 65
2018-03-23 01:00 | 52 | 49 |  |  | 43182.0417 | 61 | 60
2018-03-23 01:30 | 51 | 49 |  |  | 43182.0625 | 61 | 60
2018-03-23 02:00 | 52 | 49 |  |  | 43182.0833 | 61 | 60
2018-03-23 02:30 | 51 | 48 |  |  | 43182.1042 | 59 | 58
2018-03-23 03:00 | 50 | 47 |  |  | 43182.125 | 59 | 58
2018-03-23 03:30 | 48 | 45 |  |  | 43182.1458 | 57 | 56
2018-03-23 04:00 | 49 | 46 |  |  | 43182.1667 | 58 | 57
2018-03-23 04:30 | 50 | 47 |  |  | 43182.1875 | 59 | 58
2018-03-23 05:00 | 54 | 51 |  |  | 43182.2083 | 63 | 62
2018-03-23 05:30 | 56 | 54 |  |  | 43182.2292 | 66 | 66
2018-03-23 06:00 | 60 | 58 |  |  | 43182.25 | 72 | 72
2018-03-23 06:30 | 64 | 63 |  |  | 43182.2708 | 82 | 82
2018-03-23 07:00 | 69 | 68 |  |  | 43182.2917 | 90 | 90
2018-03-23 07:30 | 75 | 75 |  |  | 43182.3125 | 97 | 97
2018-03-23 08:00 | 78 | 77 |  |  | 43182.3333 | 102 | 102
2018-03-23 08:30 | 80 | 79 |  |  | 43182.3542 | 104 | 104
2018-03-23 09:00 | 80 | 79 |  |  | 43182.375 | 107 | 107
2018-03-23 09:30 | 82 | 81 |  |  | 43182.3958 | 109 | 109
2018-03-23 10:00 | 86 | 85 |  |  | 43182.4167 | 110 | 110
2018-03-23 10:30 | 84 | 83 |  |  | 43182.4375 | 107 | 107
2018-03-23 11:00 | 82 | 82 |  |  | 43182.4583 | 107 | 107
2018-03-23 11:30 | 81 | 80 |  |  | 43182.4792 | 106 | 106
2018-03-23 12:00 | 80 | 79 |  |  | 43182.5 | 109 | 109
2018-03-23 12:30 | 78 | 77 |  |  | 43182.5208 | 102 | 102
2018-03-23 13:00 | 77 | 76 |  |  | 43182.5417 | 101 | 100
2018-03-23 13:30 | 75 | 74 |  |  | 43182.5625 | 101 | 101
2018-03-23 14:00 | 74 | 73 |  |  | 43182.5833 | 96 | 96
2018-03-23 14:30 | 74 | 73 |  |  | 43182.6042 | 97 | 96
2018-03-23 15:00 | 76 | 75 |  |  | 43182.625 | 102 | 102
2018-03-23 15:30 | 80 | 80 |  |  | 43182.6458 | 102 | 102
2018-03-23 16:00 | 85 | 84 |  |  | 43182.6667 | 108 | 108
2018-03-23 16:30 | 87 | 86 |  |  | 43182.6875 | 108 | 108
2018-03-23 17:00 | 89 | 88 |  |  | 43182.7083 | 111 | 110
2018-03-23 17:30 | 88 | 87 |  |  | 43182.7292 | 108 | 107
2018-03-23 18:00 | 86 | 85 |  |  | 43182.75 | 105 | 104
2018-03-23 18:30 | 86 | 85 |  |  | 43182.7708 | 103 | 103
2018-03-23 19:00 | 87 | 86 |  |  | 43182.7917 | 104 | 104
2018-03-23 19:30 | 85 | 84 |  |  | 43182.8125 | 101 | 100
2018-03-23 20:00 | 84 | 82 |  |  | 43182.8333 | 100 | 99
2018-03-23 20:30 | 82 | 80 |  |  | 43182.8542 | 97 | 96
2018-03-23 21:00 | 79 | 76 |  |  | 43182.875 | 92 | 91
2018-03-23 21:30 | 75 | 71 |  |  | 43182.8958 | 88 | 87
2018-03-23 22:00 | 74 | 70 |  |  | 43182.9167 | 88 | 86
2018-03-23 22:30 | 72 | 68 |  |  | 43182.9375 | 85 | 84
2018-03-23 23:00 | 70 | 66 |  |  | 43182.9583 | 82 | 80
2018-03-23 23:30 | 68 | 63 |  |  | 43182.9792 | 79 | 77
2018-03-24 | 64 | 59 |  |  | 43183 | 74 | 72
2018-03-24 00:30 | 59 | 54 |  |  | 43183.0208 | 69 | 66
2018-03-24 01:00 | 56 | 53 |  |  | 43183.0417 | 65 | 64
2018-03-24 01:30 | 53 | 50 |  |  | 43183.0625 | 63 | 62
2018-03-24 02:00 | 53 | 50 |  |  | 43183.0833 | 62 | 61
2018-03-24 02:30 | 52 | 49 |  |  | 43183.1042 | 62 | 61
2018-03-24 03:00 | 52 | 49 |  |  | 43183.125 | 60 | 60
2018-03-24 03:30 | 51 | 47 |  |  | 43183.1458 | 60 | 59
2018-03-24 04:00 | 51 | 47 |  |  | 43183.1667 | 59 | 58
2018-03-24 04:30 | 50 | 46 |  |  | 43183.1875 | 58 | 58
2018-03-24 05:00 | 51 | 48 |  |  | 43183.2083 | 60 | 59
2018-03-24 05:30 | 51 | 48 |  |  | 43183.2292 | 60 | 59
2018-03-24 06:00 | 52 | 48 |  |  | 43183.25 | 60 | 60
2018-03-24 06:30 | 52 | 49 |  |  | 43183.2708 | 63 | 62
2018-03-24 07:00 | 52 | 50 |  |  | 43183.2917 | 64 | 63
2018-03-24 07:30 | 54 | 52 |  |  | 43183.3125 | 68 | 68
2018-03-24 08:00 | 55 | 53 |  |  | 43183.3333 | 68 | 68
2018-03-24 08:30 | 54 | 52 |  |  | 43183.3542 | 70 | 70
2018-03-24 09:00 | 60 | 58 |  |  | 43183.375 | 78 | 78
2018-03-24 09:30 | 61 | 59 |  |  | 43183.3958 | 78 | 78
2018-03-24 10:00 | 60 | 59 |  |  | 43183.4167 | 76 | 76
2018-03-24 10:30 | 62 | 61 |  |  | 43183.4375 | 78 | 78
2018-03-24 11:00 | 64 | 63 |  |  | 43183.4583 | 81 | 81
2018-03-24 11:30 | 64 | 64 |  |  | 43183.4792 | 80 | 80
2018-03-24 12:00 | 64 | 63 |  |  | 43183.5 | 80 | 80
2018-03-24 12:30 | 64 | 63 |  |  | 43183.5208 | 78 | 78
2018-03-24 13:00 | 61 | 60 |  |  | 43183.5417 | 74 | 74
2018-03-24 13:30 | 58 | 57 |  |  | 43183.5625 | 74 | 74
2018-03-24 14:00 | 58 | 57 |  |  | 43183.5833 | 71 | 71
2018-03-24 14:30 | 59 | 58 |  |  | 43183.6042 | 72 | 72
2018-03-24 15:00 | 62 | 61 |  |  | 43183.625 | 76 | 75
2018-03-24 15:30 | 64 | 63 |  |  | 43183.6458 | 77 | 77
2018-03-24 16:00 | 65 | 64 |  |  | 43183.6667 | 78 | 78
2018-03-24 16:30 | 67 | 67 |  |  | 43183.6875 | 84 | 84
2018-03-24 17:00 | 68 | 67 |  |  | 43183.7083 | 85 | 85
2018-03-24 17:30 | 68 | 67 |  |  | 43183.7292 | 84 | 83
2018-03-24 18:00 | 69 | 67 |  |  | 43183.75 | 84 | 84
2018-03-24 18:30 | 71 | 69 |  |  | 43183.7708 | 86 | 85
2018-03-24 19:00 | 74 | 72 |  |  | 43183.7917 | 89 | 88
2018-03-24 19:30 | 73 | 71 |  |  | 43183.8125 | 88 | 87
2018-03-24 20:00 | 72 | 70 |  |  | 43183.8333 | 87 | 86
2018-03-24 20:30 | 71 | 69 |  |  | 43183.8542 | 85 | 84
2018-03-24 21:00 | 68 | 65 |  |  | 43183.875 | 81 | 80
2018-03-24 21:30 | 66 | 63 |  |  | 43183.8958 | 79 | 78
2018-03-24 22:00 | 65 | 62 |  |  | 43183.9167 | 79 | 78
2018-03-24 22:30 | 65 | 61 |  |  | 43183.9375 | 79 | 77
2018-03-24 23:00 | 64 | 61 |  |  | 43183.9583 | 76 | 75
2018-03-24 23:30 | 64 | 61 |  |  | 43183.9792 | 76 | 75
2018-03-25 | 62 | 58 |  |  | 43184 | 73 | 72
2018-03-25 00:30 | 58 | 53 |  |  | 43184.0208 | 67 | 66
2018-03-25 01:00 | 57 | 52 |  |  | 43184.0417 | 65 | 64
2018-03-25 01:30 | 55 | 50 |  |  | 43184.0625 | 64 | 62
2018-03-25 02:00 | 56 | 50 |  |  | 43184.0833 | 64 | 62
2018-03-25 02:30 | 54 | 48 |  |  | 43184.1042 | 63 | 60
2018-03-25 03:00 | 54 | 48 |  |  | 43184.125 | 62 | 60
2018-03-25 03:30 | 53 | 47 |  |  | 43184.1458 | 60 | 58
2018-03-25 04:00 | 55 | 49 |  |  | 43184.1667 | 61 | 58
2018-03-25 04:30 | 54 | 48 |  |  | 43184.1875 | 61 | 59
2018-03-25 05:00 | 52 | 47 |  |  | 43184.2083 | 61 | 59
2018-03-25 05:30 | 51 | 46 |  |  | 43184.2292 | 59 | 57
2018-03-25 06:00 | 50 | 45 |  |  | 43184.25 | 59 | 57
2018-03-25 06:30 | 50 | 45 |  |  | 43184.2708 | 59 | 58
2018-03-25 07:00 | 51 | 46 |  |  | 43184.2917 | 61 | 60
2018-03-25 07:30 | 50 | 46 |  |  | 43184.3125 | 64 | 63
2018-03-25 08:00 | 54 | 50 |  |  | 43184.3333 | 68 | 67
2018-03-25 08:30 | 56 | 53 |  |  | 43184.3542 | 72 | 71
2018-03-25 09:00 | 58 | 56 |  |  | 43184.375 | 73 | 73
2018-03-25 09:30 | 63 | 62 |  |  | 43184.3958 | 78 | 78
2018-03-25 10:00 | 66 | 64 |  |  | 43184.4167 | 82 | 82
2018-03-25 10:30 | 69 | 67 |  |  | 43184.4375 | 87 | 86
2018-03-25 11:00 | 72 | 70 |  |  | 43184.4583 | 88 | 88
2018-03-25 11:30 | 70 | 69 |  |  | 43184.4792 | 83 | 83
2018-03-25 12:00 | 69 | 68 |  |  | 43184.5 | 83 | 83
2018-03-25 12:30 | 68 | 67 |  |  | 43184.5208 | 83 | 83
2018-03-25 13:00 | 66 | 65 |  |  | 43184.5417 | 83 | 83
2018-03-25 13:30 | 70 | 69 |  |  | 43184.5625 | 82 | 82
2018-03-25 14:00 | 74 | 73 |  |  | 43184.5833 | 85 | 85
2018-03-25 14:30 | 68 | 67 |  |  | 43184.6042 | 83 | 83
2018-03-25 15:00 | 66 | 65 |  |  | 43184.625 | 81 | 81
2018-03-25 15:30 | 69 | 68 |  |  | 43184.6458 | 82 | 82
2018-03-25 16:00 | 68 | 67 |  |  | 43184.6667 | 82 | 82
2018-03-25 16:30 | 70 | 69 |  |  | 43184.6875 | 82 | 81
2018-03-25 17:00 | 70 | 69 |  |  | 43184.7083 | 84 | 84
2018-03-25 17:30 | 71 | 69 |  |  | 43184.7292 | 85 | 84
2018-03-25 18:00 | 73 | 72 |  |  | 43184.75 | 87 | 86
2018-03-25 18:30 | 75 | 73 |  |  | 43184.7708 | 89 | 88
2018-03-25 19:00 | 78 | 77 |  |  | 43184.7917 | 94 | 93
2018-03-25 19:30 | 77 | 76 |  |  | 43184.8125 | 93 | 91
2018-03-25 20:00 | 78 | 77 |  |  | 43184.8333 | 94 | 93
2018-03-25 20:30 | 78 | 76 |  |  | 43184.8542 | 94 | 93
2018-03-25 21:00 | 75 | 74 |  |  | 43184.875 | 91 | 90
2018-03-25 21:30 | 76 | 74 |  |  | 43184.8958 | 90 | 90
2018-03-25 22:00 | 75 | 73 |  |  | 43184.9167 | 92 | 91
2018-03-25 22:30 | 73 | 71 |  |  | 43184.9375 | 89 | 89
2018-03-25 23:00 | 71 | 69 |  |  | 43184.9583 | 85 | 85
2018-03-25 23:30 | 68 | 66 |  |  | 43184.9792 | 82 | 82
2018-03-26 | 65 | 62 |  |  | 43185 | 77 | 76
2018-03-26 00:30 | 61 | 57 |  |  | 43185.0208 | 71 | 70
2018-03-26 01:00 | 58 | 54 |  |  | 43185.0417 | 68 | 66
2018-03-26 01:30 | 56 | 52 |  |  | 43185.0625 | 65 | 64
2018-03-26 02:00 | 56 | 52 |  |  | 43185.0833 | 66 | 64
2018-03-26 02:30 | 56 | 52 |  |  | 43185.1042 | 65 | 63
2018-03-26 03:00 | 56 | 52 |  |  | 43185.125 | 65 | 63
2018-03-26 03:30 | 56 | 51 |  |  | 43185.1458 | 64 | 63
2018-03-26 04:00 | 55 | 51 |  |  | 43185.1667 | 64 | 62
2018-03-26 04:30 | 52 | 49 |  |  | 43185.1875 | 62 | 61
2018-03-26 05:00 | 55 | 51 |  |  | 43185.2083 | 64 | 63
2018-03-26 05:30 | 56 | 54 |  |  | 43185.2292 | 67 | 67
2018-03-26 06:00 | 57 | 56 |  |  | 43185.25 | 69 | 68
2018-03-26 06:30 | 64 | 63 |  |  | 43185.2708 | 80 | 79
2018-03-26 07:00 | 71 | 70 |  |  | 43185.2917 | 90 | 90
2018-03-26 07:30 | 78 | 76 |  |  | 43185.3125 | 100 | 100
2018-03-26 08:00 | 82 | 79 |  |  | 43185.3333 | 104 | 102
2018-03-26 08:30 | 86 | 80 |  |  | 43185.3542 | 106 | 105
2018-03-26 09:00 | 87 | 81 |  |  | 43185.375 | 108 | 106
2018-03-26 09:30 | 90 | 84 |  |  | 43185.3958 | 110 | 108
2018-03-26 10:00 | 93 | 87 |  |  | 43185.4167 | 113 | 112
2018-03-26 10:30 | 97 | 92 |  |  | 43185.4375 | 118 | 117
2018-03-26 11:00 | 96 | 91 |  |  | 43185.4583 | 119 | 119
2018-03-26 11:30 | 97 | 92 |  |  | 43185.4792 | 120 | 119
2018-03-26 12:00 | 98 | 93 |  |  | 43185.5 | 121 | 120
2018-03-26 12:30 | 102 | 96 |  |  | 43185.5208 | 122 | 121
2018-03-26 13:00 | 105 | 97 |  |  | 43185.5417 | 127 | 124
2018-03-26 13:30 | 109 | 101 |  |  | 43185.5625 | 131 | 128
2018-03-26 14:00 | 110 | 102 |  |  | 43185.5833 | 131 | 127
2018-03-26 14:30 | 112 | 105 |  |  | 43185.6042 | 133 | 130
2018-03-26 15:00 | 111 | 104 |  |  | 43185.625 | 130 | 127
2018-03-26 15:30 | 111 | 104 |  |  | 43185.6458 | 130 | 127
2018-03-26 16:00 | 112 | 104 |  |  | 43185.6667 | 129 | 126
2018-03-26 16:30 | 111 | 103 |  |  | 43185.6875 | 127 | 123
2018-03-26 17:00 | 113 | 105 |  |  | 43185.7083 | 130 | 125
2018-03-26 17:30 | 111 | 104 |  |  | 43185.7292 | 126 | 122
2018-03-26 18:00 | 109 | 101 |  |  | 43185.75 | 123 | 120
2018-03-26 18:30 | 107 | 100 |  |  | 43185.7708 | 120 | 116
2018-03-26 19:00 | 108 | 101 |  |  | 43185.7917 | 121 | 118
2018-03-26 19:30 | 104 | 99 |  |  | 43185.8125 | 116 | 115
2018-03-26 20:00 | 100 | 97 |  |  | 43185.8333 | 112 | 112
2018-03-26 20:30 | 96 | 94 |  |  | 43185.8542 | 110 | 109
2018-03-26 21:00 | 92 | 91 |  |  | 43185.875 | 105 | 105
2018-03-26 21:30 | 87 | 86 |  |  | 43185.8958 | 99 | 98
2018-03-26 22:00 | 87 | 84 |  |  | 43185.9167 | 100 | 99
2018-03-26 22:30 | 83 | 79 |  |  | 43185.9375 | 95 | 95
2018-03-26 23:00 | 77 | 73 |  |  | 43185.9583 | 88 | 88
2018-03-26 23:30 | 78 | 68 |  |  | 43185.9792 | 81 | 81
2018-03-27 | 74 | 62 |  |  | 43186 | 75 | 74
2018-03-27 00:30 | 69 | 57 |  |  | 43186.0208 | 69 | 69
2018-03-27 01:00 | 68 | 54 |  |  | 43186.0417 | 65 | 64
2018-03-27 01:30 | 68 | 53 |  |  | 43186.0625 | 64 | 63
2018-03-27 02:00 | 68 | 53 |  |  | 43186.0833 | 64 | 63
2018-03-27 02:30 | 67 | 51 |  |  | 43186.1042 | 64 | 64
2018-03-27 03:00 | 66 | 50 |  |  | 43186.125 | 63 | 62
2018-03-27 03:30 | 65 | 49 |  |  | 43186.1458 | 63 | 62
2018-03-27 04:00 | 65 | 49 |  |  | 43186.1667 | 62 | 61
2018-03-27 04:30 | 66 | 49 |  |  | 43186.1875 | 63 | 62
2018-03-27 05:00 | 67 | 52 |  |  | 43186.2083 | 66 | 65
2018-03-27 05:30 | 69 | 55 |  |  | 43186.2292 | 69 | 68
2018-03-27 06:00 | 73 | 61 |  |  | 43186.25 | 76 | 76
2018-03-27 06:30 | 81 | 69 |  |  | 43186.2708 | 88 | 87
2018-03-27 07:00 | 91 | 79 |  |  | 43186.2917 | 101 | 99
2018-03-27 07:30 | 99 | 90 |  |  | 43186.3125 | 115 | 114
2018-03-27 08:00 | 103 | 93 |  |  | 43186.3333 | 122 | 120
2018-03-27 08:30 | 106 | 96 |  |  | 43186.3542 | 126 | 124
2018-03-27 09:00 | 109 | 98 |  |  | 43186.375 | 127 | 125
2018-03-27 09:30 | 110 | 100 |  |  | 43186.3958 | 131 | 129
2018-03-27 10:00 | 111 | 101 |  |  | 43186.4167 | 132 | 130
2018-03-27 10:30 | 112 | 102 |  |  | 43186.4375 | 132 | 129
2018-03-27 11:00 | 113 | 103 |  |  | 43186.4583 | 136 | 134
2018-03-27 11:30 | 111 | 100 |  |  | 43186.4792 | 131 | 129
2018-03-27 12:00 | 114 | 103 |  |  | 43186.5 | 131 | 128
2018-03-27 12:30 | 112 | 101 |  |  | 43186.5208 | 129 | 126
2018-03-27 13:00 | 108 | 97 |  |  | 43186.5417 | 124 | 121
2018-03-27 13:30 | 101 | 90 |  |  | 43186.5625 | 115 | 112
2018-03-27 14:00 | 100 | 89 |  |  | 43186.5833 | 115 | 113
2018-03-27 14:30 | 101 | 89 |  |  | 43186.6042 | 114 | 112
2018-03-27 15:00 | 102 | 91 |  |  | 43186.625 | 118 | 117
2018-03-27 15:30 | 106 | 95 |  |  | 43186.6458 | 119 | 117
2018-03-27 16:00 | 107 | 97 |  |  | 43186.6667 | 121 | 118
2018-03-27 16:30 | 110 | 100 |  |  | 43186.6875 | 122 | 120
2018-03-27 17:00 | 110 | 100 |  |  | 43186.7083 | 124 | 121
2018-03-27 17:30 | 111 | 99 |  |  | 43186.7292 | 121 | 117
2018-03-27 18:00 | 109 | 96 |  |  | 43186.75 | 118 | 114
2018-03-27 18:30 | 110 | 96 |  |  | 43186.7708 | 116 | 111
2018-03-27 19:00 | 111 | 97 |  |  | 43186.7917 | 116 | 111
2018-03-27 19:30 | 105 | 94 |  |  | 43186.8125 | 110 | 108
2018-03-27 20:00 | 101 | 92 |  |  | 43186.8333 | 107 | 106
2018-03-27 20:30 | 95 | 90 |  |  | 43186.8542 | 104 | 104
2018-03-27 21:00 | 90 | 85 |  |  | 43186.875 | 98 | 98
2018-03-27 21:30 | 84 | 79 |  |  | 43186.8958 | 91 | 91
2018-03-27 22:00 | 82 | 77 |  |  | 43186.9167 | 90 | 90
2018-03-27 22:30 | 81 | 76 |  |  | 43186.9375 | 91 | 91
2018-03-27 23:00 | 79 | 74 |  |  | 43186.9583 | 87 | 87
2018-03-27 23:30 | 76 | 71 |  |  | 43186.9792 | 84 | 84
2018-03-28 | 73 | 67 |  |  | 43187 | 80 | 80
2018-03-28 00:30 | 69 | 62 |  |  | 43187.0208 | 75 | 75
2018-03-28 01:00 | 66 | 58 |  |  | 43187.0417 | 70 | 70
2018-03-28 01:30 | 64 | 57 |  |  | 43187.0625 | 67 | 67
2018-03-28 02:00 | 66 | 57 |  |  | 43187.0833 | 68 | 67
2018-03-28 02:30 | 66 | 57 |  |  | 43187.1042 | 68 | 68
2018-03-28 03:00 | 65 | 57 |  |  | 43187.125 | 68 | 67
2018-03-28 03:30 | 65 | 56 |  |  | 43187.1458 | 68 | 67
2018-03-28 04:00 | 64 | 55 |  |  | 43187.1667 | 67 | 67
2018-03-28 04:30 | 64 | 55 |  |  | 43187.1875 | 67 | 67
2018-03-28 05:00 | 63 | 55 |  |  | 43187.2083 | 67 | 66
2018-03-28 05:30 | 67 | 60 |  |  | 43187.2292 | 72 | 72
2018-03-28 06:00 | 69 | 63 |  |  | 43187.25 | 77 | 77
2018-03-28 06:30 | 70 | 67 |  |  | 43187.2708 | 84 | 84
2018-03-28 07:00 | 76 | 75 |  |  | 43187.2917 | 96 | 95
2018-03-28 07:30 | 80 | 80 |  |  | 43187.3125 | 103 | 102
2018-03-28 08:00 | 82 | 82 |  |  | 43187.3333 | 106 | 106
2018-03-28 08:30 | 84 | 84 |  |  | 43187.3542 | 111 | 110
2018-03-28 09:00 | 85 | 85 |  |  | 43187.375 | 112 | 112
2018-03-28 09:30 | 84 | 84 |  |  | 43187.3958 | 112 | 112
2018-03-28 10:00 | 87 | 86 |  |  | 43187.4167 | 113 | 113
2018-03-28 10:30 | 87 | 87 |  |  | 43187.4375 | 113 | 113
2018-03-28 11:00 | 86 | 86 |  |  | 43187.4583 | 111 | 111
2018-03-28 11:30 | 86 | 86 |  |  | 43187.4792 | 112 | 112
2018-03-28 12:00 | 88 | 88 |  |  | 43187.5 | 111 | 111
2018-03-28 12:30 | 86 | 85 |  |  | 43187.5208 | 111 | 111
2018-03-28 13:00 | 88 | 88 |  |  | 43187.5417 | 112 | 112
2018-03-28 13:30 | 87 | 87 |  |  | 43187.5625 | 111 | 111
2018-03-28 14:00 | 90 | 89 |  |  | 43187.5833 | 112 | 112
2018-03-28 14:30 | 91 | 91 |  |  | 43187.6042 | 113 | 113
2018-03-28 15:00 | 91 | 90 |  |  | 43187.625 | 113 | 113
2018-03-28 15:30 | 92 | 91 |  |  | 43187.6458 | 114 | 114
2018-03-28 16:00 | 95 | 94 |  |  | 43187.6667 | 115 | 115
2018-03-28 16:30 | 95 | 95 |  |  | 43187.6875 | 117 | 117
2018-03-28 17:00 | 97 | 96 |  |  | 43187.7083 | 118 | 118
2018-03-28 17:30 | 96 | 96 |  |  | 43187.7292 | 117 | 117
2018-03-28 18:00 | 93 | 92 |  |  | 43187.75 | 112 | 112
2018-03-28 18:30 | 92 | 91 |  |  | 43187.7708 | 110 | 110
2018-03-28 19:00 | 94 | 93 |  |  | 43187.7917 | 111 | 111
2018-03-28 19:30 | 89 | 89 |  |  | 43187.8125 | 107 | 106
2018-03-28 20:00 | 87 | 86 |  |  | 43187.8333 | 105 | 103
2018-03-28 20:30 | 85 | 84 |  |  | 43187.8542 | 102 | 100
2018-03-28 21:00 | 81 | 79 |  |  | 43187.875 | 96 | 94
2018-03-28 21:30 | 76 | 75 |  |  | 43187.8958 | 93 | 90
2018-03-28 22:00 | 74 | 74 |  |  | 43187.9167 | 92 | 89
2018-03-28 22:30 | 69 | 69 |  |  | 43187.9375 | 88 | 85
2018-03-28 23:00 | 66 | 66 |  |  | 43187.9583 | 82 | 80
2018-03-28 23:30 | 64 | 63 |  |  | 43187.9792 | 78 | 77
2018-03-29 | 57 | 57 |  |  | 43188 | 71 | 70
2018-03-29 00:30 | 51 | 50 |  |  | 43188.0208 | 65 | 63
2018-03-29 01:00 | 48 | 48 |  |  | 43188.0417 | 62 | 59
2018-03-29 01:30 | 46 | 45 |  |  | 43188.0625 | 60 | 57
2018-03-29 02:00 | 47 | 46 |  |  | 43188.0833 | 59 | 56
2018-03-29 02:30 | 46 | 45 |  |  | 43188.1042 | 59 | 55
2018-03-29 03:00 | 45 | 44 |  |  | 43188.125 | 58 | 54
2018-03-29 03:30 | 43 | 42 |  |  | 43188.1458 | 57 | 53
2018-03-29 04:00 | 42 | 42 |  |  | 43188.1667 | 56 | 52
2018-03-29 04:30 | 43 | 42 |  |  | 43188.1875 | 57 | 54
2018-03-29 05:00 | 47 | 46 |  |  | 43188.2083 | 61 | 58
2018-03-29 05:30 | 51 | 50 |  |  | 43188.2292 | 65 | 62
2018-03-29 06:00 | 55 | 54 |  |  | 43188.25 | 71 | 68
2018-03-29 06:30 | 62 | 61 |  |  | 43188.2708 | 81 | 79
2018-03-29 07:00 | 73 | 71 |  |  | 43188.2917 | 92 | 91
2018-03-29 07:30 | 77 | 75 |  |  | 43188.3125 | 100 | 99
2018-03-29 08:00 | 80 | 78 |  |  | 43188.3333 | 103 | 102
2018-03-29 08:30 | 81 | 78 |  |  | 43188.3542 | 105 | 105
2018-03-29 09:00 | 81 | 80 |  |  | 43188.375 | 107 | 106
2018-03-29 09:30 | 81 | 79 |  |  | 43188.3958 | 107 | 107
2018-03-29 10:00 | 80 | 78 |  |  | 43188.4167 | 106 | 105
2018-03-29 10:30 | 83 | 81 |  |  | 43188.4375 | 107 | 107
2018-03-29 11:00 | 81 | 80 |  |  | 43188.4583 | 106 | 106
2018-03-29 11:30 | 81 | 79 |  |  | 43188.4792 | 107 | 107
2018-03-29 12:00 | 84 | 83 |  |  | 43188.5 | 108 | 107
2018-03-29 12:30 | 82 | 80 |  |  | 43188.5208 | 106 | 105
2018-03-29 13:00 | 82 | 81 |  |  | 43188.5417 | 105 | 104
2018-03-29 13:30 | 81 | 80 |  |  | 43188.5625 | 105 | 104
2018-03-29 14:00 | 80 | 78 |  |  | 43188.5833 | 106 | 106
2018-03-29 14:30 | 81 | 80 |  |  | 43188.6042 | 105 | 105
2018-03-29 15:00 | 81 | 80 |  |  | 43188.625 | 104 | 104
2018-03-29 15:30 | 81 | 80 |  |  | 43188.6458 | 104 | 103
2018-03-29 16:00 | 79 | 78 |  |  | 43188.6667 | 104 | 102
2018-03-29 16:30 | 80 | 80 |  |  | 43188.6875 | 105 | 103
2018-03-29 17:00 | 82 | 81 |  |  | 43188.7083 | 105 | 104
2018-03-29 17:30 | 83 | 83 |  |  | 43188.7292 | 106 | 104
2018-03-29 18:00 | 82 | 81 |  |  | 43188.75 | 104 | 102
2018-03-29 18:30 | 82 | 82 |  |  | 43188.7708 | 103 | 100
2018-03-29 19:00 | 82 | 82 |  |  | 43188.7917 | 103 | 100
2018-03-29 19:30 | 80 | 79 |  |  | 43188.8125 | 100 | 98
2018-03-29 20:00 | 80 | 79 |  |  | 43188.8333 | 99 | 97
2018-03-29 20:30 | 79 | 79 |  |  | 43188.8542 | 98 | 96
2018-03-29 21:00 | 76 | 75 |  |  | 43188.875 | 92 | 91
2018-03-29 21:30 | 72 | 70 |  |  | 43188.8958 | 86 | 85
2018-03-29 22:00 | 69 | 69 |  |  | 43188.9167 | 86 | 84
2018-03-29 22:30 | 66 | 65 |  |  | 43188.9375 | 84 | 81
2018-03-29 23:00 | 62 | 62 |  |  | 43188.9583 | 80 | 76
2018-03-29 23:30 | 58 | 57 |  |  | 43188.9792 | 75 | 71
2018-03-30 | 52 | 52 |  |  | 43189 | 69 | 64
2018-03-30 00:30 | 46 | 46 |  |  | 43189.0208 | 62 | 58
2018-03-30 01:00 | 43 | 43 |  |  | 43189.0417 | 59 | 54
2018-03-30 01:30 | 41 | 41 |  |  | 43189.0625 | 56 | 51
2018-03-30 02:00 | 39 | 39 |  |  | 43189.0833 | 55 | 49
2018-03-30 02:30 | 37 | 37 |  |  | 43189.1042 | 53 | 46
2018-03-30 03:00 | 36 | 36 |  |  | 43189.125 | 53 | 47
2018-03-30 03:30 | 36 | 36 |  |  | 43189.1458 | 53 | 46
2018-03-30 04:00 | 36 | 36 |  |  | 43189.1667 | 53 | 46
2018-03-30 04:30 | 36 | 36 |  |  | 43189.1875 | 53 | 46
2018-03-30 05:00 | 37 | 37 |  |  | 43189.2083 | 54 | 47
2018-03-30 05:30 | 37 | 37 |  |  | 43189.2292 | 55 | 48
2018-03-30 06:00 | 38 | 38 |  |  | 43189.25 | 56 | 50
2018-03-30 06:30 | 39 | 39 |  |  | 43189.2708 | 57 | 51
2018-03-30 07:00 | 41 | 41 |  |  | 43189.2917 | 59 | 54
2018-03-30 07:30 | 44 | 44 |  |  | 43189.3125 | 62 | 58
2018-03-30 08:00 | 44 | 44 |  |  | 43189.3333 | 62 | 58
2018-03-30 08:30 | 47 | 46 |  |  | 43189.3542 | 64 | 61
2018-03-30 09:00 | 51 | 50 |  |  | 43189.375 | 71 | 69
2018-03-30 09:30 | 53 | 52 |  |  | 43189.3958 | 72 | 70
2018-03-30 10:00 | 53 | 52 |  |  | 43189.4167 | 72 | 71
2018-03-30 10:30 | 50 | 49 |  |  | 43189.4375 | 68 | 67
2018-03-30 11:00 | 54 | 52 |  |  | 43189.4583 | 68 | 67
2018-03-30 11:30 | 55 | 53 |  |  | 43189.4792 | 65 | 63
2018-03-30 12:00 | 53 | 51 |  |  | 43189.5 | 68 | 66
2018-03-30 12:30 | 57 | 56 |  |  | 43189.5208 | 70 | 69
2018-03-30 13:00 | 55 | 54 |  |  | 43189.5417 | 71 | 69
2018-03-30 13:30 | 59 | 57 |  |  | 43189.5625 | 74 | 72
2018-03-30 14:00 | 58 | 56 |  |  | 43189.5833 | 73 | 71
2018-03-30 14:30 | 61 | 59 |  |  | 43189.6042 | 75 | 74
2018-03-30 15:00 | 61 | 60 |  |  | 43189.625 | 76 | 74
2018-03-30 15:30 | 62 | 60 |  |  | 43189.6458 | 76 | 74
2018-03-30 16:00 | 61 | 60 |  |  | 43189.6667 | 77 | 75
2018-03-30 16:30 | 63 | 62 |  |  | 43189.6875 | 77 | 76
2018-03-30 17:00 | 63 | 62 |  |  | 43189.7083 | 79 | 77
2018-03-30 17:30 | 65 | 64 |  |  | 43189.7292 | 81 | 79
2018-03-30 18:00 | 65 | 64 |  |  | 43189.75 | 82 | 80
2018-03-30 18:30 | 66 | 65 |  |  | 43189.7708 | 84 | 81
2018-03-30 19:00 | 68 | 67 |  |  | 43189.7917 | 86 | 84
2018-03-30 19:30 | 68 | 67 |  |  | 43189.8125 | 85 | 83
2018-03-30 20:00 | 65 | 65 |  |  | 43189.8333 | 84 | 81
2018-03-30 20:30 | 65 | 65 |  |  | 43189.8542 | 84 | 81
2018-03-30 21:00 | 63 | 63 |  |  | 43189.875 | 79 | 77
2018-03-30 21:30 | 60 | 60 |  |  | 43189.8958 | 77 | 74
2018-03-30 22:00 | 61 | 61 |  |  | 43189.9167 | 78 | 75
2018-03-30 22:30 | 59 | 59 |  |  | 43189.9375 | 78 | 75
2018-03-30 23:00 | 57 | 57 |  |  | 43189.9583 | 74 | 71
2018-03-30 23:30 | 55 | 54 |  |  | 43189.9792 | 72 | 68
2018-03-31 | 49 | 49 |  |  | 43190 | 67 | 62
2018-03-31 00:30 | 45 | 45 |  |  | 43190.0208 | 62 | 56
2018-03-31 01:00 | 41 | 41 |  |  | 43190.0417 | 59 | 53
2018-03-31 01:30 | 42 | 42 |  |  | 43190.0625 | 59 | 53
2018-03-31 02:00 | 41 | 41 |  |  | 43190.0833 | 59 | 52
2018-03-31 02:30 | 41 | 41 |  |  | 43190.1042 | 58 | 52
2018-03-31 03:00 | 41 | 40 |  |  | 43190.125 | 58 | 51
2018-03-31 03:30 | 40 | 40 |  |  | 43190.1458 | 58 | 50
2018-03-31 04:00 | 40 | 39 |  |  | 43190.1667 | 58 | 50
2018-03-31 04:30 | 39 | 39 |  |  | 43190.1875 | 57 | 50
2018-03-31 05:00 | 40 | 40 |  |  | 43190.2083 | 58 | 51
2018-03-31 05:30 | 41 | 41 |  |  | 43190.2292 | 60 | 54
2018-03-31 06:00 | 41 | 41 |  |  | 43190.25 | 60 | 54
2018-03-31 06:30 | 41 | 41 |  |  | 43190.2708 | 60 | 53
2018-03-31 07:00 | 40 | 40 |  |  | 43190.2917 | 58 | 52
2018-03-31 07:30 | 41 | 41 |  |  | 43190.3125 | 59 | 54
2018-03-31 08:00 | 43 | 43 |  |  | 43190.3333 | 61 | 57
2018-03-31 08:30 | 46 | 45 |  |  | 43190.3542 | 63 | 60
2018-03-31 09:00 | 48 | 47 |  |  | 43190.375 | 66 | 63
2018-03-31 09:30 | 51 | 50 |  |  | 43190.3958 | 71 | 68
2018-03-31 10:00 | 50 | 49 |  |  | 43190.4167 | 67 | 65
2018-03-31 10:30 | 47 | 45 |  |  | 43190.4375 | 65 | 62
2018-03-31 11:00 | 48 | 47 |  |  | 43190.4583 | 65 | 62
2018-03-31 11:30 | 48 | 47 |  |  | 43190.4792 | 63 | 62
2018-03-31 12:00 | 48 | 47 |  |  | 43190.5 | 63 | 61
2018-03-31 12:30 | 48 | 47 |  |  | 43190.5208 | 62 | 60
2018-03-31 13:00 | 47 | 46 |  |  | 43190.5417 | 62 | 59
2018-03-31 13:30 | 48 | 47 |  |  | 43190.5625 | 63 | 61
2018-03-31 14:00 | 50 | 49 |  |  | 43190.5833 | 65 | 62
2018-03-31 14:30 | 53 | 51 |  |  | 43190.6042 | 67 | 65
2018-03-31 15:00 | 54 | 53 |  |  | 43190.625 | 69 | 66
2018-03-31 15:30 | 55 | 54 |  |  | 43190.6458 | 69 | 67
2018-03-31 16:00 | 55 | 54 |  |  | 43190.6667 | 71 | 69
2018-03-31 16:30 | 55 | 54 |  |  | 43190.6875 | 69 | 67
2018-03-31 17:00 | 57 | 56 |  |  | 43190.7083 | 72 | 69
2018-03-31 17:30 | 55 | 54 |  |  | 43190.7292 | 72 | 69
2018-03-31 18:00 | 55 | 54 |  |  | 43190.75 | 73 | 70
2018-03-31 18:30 | 55 | 54 |  |  | 43190.7708 | 73 | 70
2018-03-31 19:00 | 55 | 55 |  |  | 43190.7917 | 74 | 71
2018-03-31 19:30 | 55 | 55 |  |  | 43190.8125 | 74 | 71
2018-03-31 20:00 | 55 | 54 |  |  | 43190.8333 | 73 | 70
2018-03-31 20:30 | 56 | 55 |  |  | 43190.8542 | 74 | 72
2018-03-31 21:00 | 55 | 54 |  |  | 43190.875 | 73 | 70
2018-03-31 21:30 | 53 | 52 |  |  | 43190.8958 | 70 | 68
2018-03-31 22:00 | 52 | 51 |  |  | 43190.9167 | 70 | 68
2018-03-31 22:30 | 54 | 53 |  |  | 43190.9375 | 70 | 67
2018-03-31 23:00 | 51 | 50 |  |  | 43190.9583 | 66 | 63
2018-03-31 23:30 | 47 | 46 |  |  | 43190.9792 | 63 | 60
2018-04-01 | 43 | 43 |  |  | 43191 | 60 | 56
2018-04-01 00:30 | 39 | 39 |  |  | 43191.0208 | 55 | 51
2018-04-01 01:00 | 39 | 39 |  |  | 43191.0417 | 56 | 51
2018-04-01 01:30 | 39 | 39 |  |  | 43191.0625 | 55 | 49
2018-04-01 02:00 | 39 | 38 |  |  | 43191.0833 | 54 | 48
2018-04-01 02:30 | 38 | 38 |  |  | 43191.1042 | 54 | 48
2018-04-01 03:00 | 37 | 37 |  |  | 43191.125 | 53 | 47
2018-04-01 03:30 | 36 | 36 |  |  | 43191.1458 | 51 | 45
2018-04-01 04:00 | 35 | 34 |  |  | 43191.1667 | 51 | 45
2018-04-01 04:30 | 36 | 36 |  |  | 43191.1875 | 52 | 45
2018-04-01 05:00 | 37 | 36 |  |  | 43191.2083 | 53 | 47
2018-04-01 05:30 | 38 | 38 |  |  | 43191.2292 | 54 | 48
2018-04-01 06:00 | 36 | 36 |  |  | 43191.25 | 54 | 47
2018-04-01 06:30 | 37 | 36 |  |  | 43191.2708 | 55 | 49
2018-04-01 07:00 | 37 | 37 |  |  | 43191.2917 | 56 | 50
2018-04-01 07:30 | 38 | 38 |  |  | 43191.3125 | 57 | 51
2018-04-01 08:00 | 39 | 39 |  |  | 43191.3333 | 57 | 52
2018-04-01 08:30 | 42 | 42 |  |  | 43191.3542 | 61 | 57
2018-04-01 09:00 | 44 | 44 |  |  | 43191.375 | 63 | 60
2018-04-01 09:30 | 48 | 47 |  |  | 43191.3958 | 66 | 64
2018-04-01 10:00 | 51 | 51 |  |  | 43191.4167 | 71 | 68
2018-04-01 10:30 | 52 | 51 |  |  | 43191.4375 | 71 | 68
2018-04-01 11:00 | 51 | 51 |  |  | 43191.4583 | 67 | 64
2018-04-01 11:30 | 51 | 50 |  |  | 43191.4792 | 68 | 65
2018-04-01 12:00 | 49 | 49 |  |  | 43191.5 | 66 | 63
2018-04-01 12:30 | 49 | 49 |  |  | 43191.5208 | 67 | 64
2018-04-01 13:00 | 53 | 53 |  |  | 43191.5417 | 68 | 65
2018-04-01 13:30 | 52 | 51 |  |  | 43191.5625 | 66 | 63
2018-04-01 14:00 | 51 | 50 |  |  | 43191.5833 | 63 | 60
2018-04-01 14:30 | 51 | 51 |  |  | 43191.6042 | 65 | 62
2018-04-01 15:00 | 50 | 50 |  |  | 43191.625 | 66 | 63
2018-04-01 15:30 | 51 | 50 |  |  | 43191.6458 | 68 | 65
2018-04-01 16:00 | 53 | 52 |  |  | 43191.6667 | 69 | 67
2018-04-01 16:30 | 55 | 54 |  |  | 43191.6875 | 71 | 69
2018-04-01 17:00 | 56 | 55 |  |  | 43191.7083 | 72 | 70
2018-04-01 17:30 | 55 | 55 |  |  | 43191.7292 | 72 | 70
2018-04-01 18:00 | 56 | 55 |  |  | 43191.75 | 74 | 71
2018-04-01 18:30 | 57 | 57 |  |  | 43191.7708 | 76 | 74
2018-04-01 19:00 | 57 | 57 |  |  | 43191.7917 | 77 | 74
2018-04-01 19:30 | 58 | 57 |  |  | 43191.8125 | 77 | 75
2018-04-01 20:00 | 58 | 58 |  |  | 43191.8333 | 76 | 74
2018-04-01 20:30 | 59 | 59 |  |  | 43191.8542 | 77 | 75
2018-04-01 21:00 | 57 | 57 |  |  | 43191.875 | 74 | 72
2018-04-01 21:30 | 56 | 55 |  |  | 43191.8958 | 72 | 70
2018-04-01 22:00 | 57 | 56 |  |  | 43191.9167 | 75 | 73
2018-04-01 22:30 | 58 | 57 |  |  | 43191.9375 | 77 | 74
2018-04-01 23:00 | 58 | 58 |  |  | 43191.9583 | 75 | 72
2018-04-01 23:30 | 54 | 54 |  |  | 43191.9792 | 71 | 68
2018-04-02 | 49 | 49 |  |  | 43192 | 66 | 62
2018-04-02 00:30 | 45 | 45 |  |  | 43192.0208 | 61 | 56
2018-04-02 01:00 | 44 | 43 |  |  | 43192.0417 | 60 | 55
2018-04-02 01:30 | 41 | 41 |  |  | 43192.0625 | 58 | 52
2018-04-02 02:00 | 40 | 40 |  |  | 43192.0833 | 57 | 51
2018-04-02 02:30 | 39 | 38 |  |  | 43192.1042 | 55 | 49
2018-04-02 03:00 | 39 | 39 |  |  | 43192.125 | 55 | 49
2018-04-02 03:30 | 38 | 38 |  |  | 43192.1458 | 54 | 48
2018-04-02 04:00 | 37 | 36 |  |  | 43192.1667 | 53 | 47
2018-04-02 04:30 | 37 | 36 |  |  | 43192.1875 | 53 | 47
2018-04-02 05:00 | 39 | 38 |  |  | 43192.2083 | 54 | 48
2018-04-02 05:30 | 39 | 39 |  |  | 43192.2292 | 56 | 50
2018-04-02 06:00 | 39 | 39 |  |  | 43192.25 | 56 | 51
2018-04-02 06:30 | 39 | 39 |  |  | 43192.2708 | 58 | 54
2018-04-02 07:00 | 40 | 40 |  |  | 43192.2917 | 61 | 56
2018-04-02 07:30 | 42 | 41 |  |  | 43192.3125 | 62 | 59
2018-04-02 08:00 | 43 | 42 |  |  | 43192.3333 | 63 | 60
2018-04-02 08:30 | 46 | 44 |  |  | 43192.3542 | 65 | 63
2018-04-02 09:00 | 49 | 47 |  |  | 43192.375 | 67 | 66
2018-04-02 09:30 | 54 | 51 |  |  | 43192.3958 | 71 | 70
2018-04-02 10:00 | 55 | 52 |  |  | 43192.4167 | 73 | 72
2018-04-02 10:30 | 56 | 53 |  |  | 43192.4375 | 70 | 70
2018-04-02 11:00 | 56 | 54 |  |  | 43192.4583 | 68 | 68
2018-04-02 11:30 | 54 | 52 |  |  | 43192.4792 | 68 | 68
2018-04-02 12:00 | 57 | 55 |  |  | 43192.5 | 68 | 68
2018-04-02 12:30 | 57 | 54 |  |  | 43192.5208 | 66 | 66
2018-04-02 13:00 | 55 | 52 |  |  | 43192.5417 | 68 | 68
2018-04-02 13:30 | 55 | 53 |  |  | 43192.5625 | 70 | 70
2018-04-02 14:00 | 54 | 52 |  |  | 43192.5833 | 67 | 66
2018-04-02 14:30 | 57 | 55 |  |  | 43192.6042 | 68 | 68
2018-04-02 15:00 | 57 | 55 |  |  | 43192.625 | 69 | 68
2018-04-02 15:30 | 59 | 57 |  |  | 43192.6458 | 73 | 72
2018-04-02 16:00 | 61 | 59 |  |  | 43192.6667 | 77 | 76
2018-04-02 16:30 | 64 | 61 |  |  | 43192.6875 | 79 | 78
2018-04-02 17:00 | 64 | 63 |  |  | 43192.7083 | 82 | 80
2018-04-02 17:30 | 64 | 62 |  |  | 43192.7292 | 81 | 79
2018-04-02 18:00 | 63 | 60 |  |  | 43192.75 | 80 | 79
2018-04-02 18:30 | 65 | 62 |  |  | 43192.7708 | 83 | 80
2018-04-02 19:00 | 68 | 64 |  |  | 43192.7917 | 86 | 81
2018-04-02 19:30 | 67 | 63 |  |  | 43192.8125 | 84 | 79
2018-04-02 20:00 | 71 | 60 |  |  | 43192.8333 | 83 | 77
2018-04-02 20:30 | 70 | 60 |  |  | 43192.8542 | 82 | 76
2018-04-02 21:00 | 66 | 57 |  |  | 43192.875 | 77 | 73
2018-04-02 21:30 | 64 | 56 |  |  | 43192.8958 | 73 | 71
2018-04-02 22:00 | 65 | 57 |  |  | 43192.9167 | 77 | 74
2018-04-02 22:30 | 65 | 55 |  |  | 43192.9375 | 75 | 72
2018-04-02 23:00 | 63 | 54 |  |  | 43192.9583 | 70 | 68
2018-04-02 23:30 | 59 | 49 |  |  | 43192.9792 | 65 | 63
2018-04-03 | 56 | 44 |  |  | 43193 | 61 | 58
2018-04-03 00:30 | 53 | 40 |  |  | 43193.0208 | 57 | 53
2018-04-03 01:00 | 52 | 38 |  |  | 43193.0417 | 54 | 50
2018-04-03 01:30 | 50 | 36 |  |  | 43193.0625 | 52 | 48
2018-04-03 02:00 | 50 | 36 |  |  | 43193.0833 | 51 | 47
2018-04-03 02:30 | 50 | 35 |  |  | 43193.1042 | 50 | 46
2018-04-03 03:00 | 49 | 34 |  |  | 43193.125 | 51 | 46
2018-04-03 03:30 | 51 | 36 |  |  | 43193.1458 | 52 | 48
2018-04-03 04:00 | 51 | 36 |  |  | 43193.1667 | 52 | 48
2018-04-03 04:30 | 51 | 37 |  |  | 43193.1875 | 53 | 49
2018-04-03 05:00 | 52 | 39 |  |  | 43193.2083 | 55 | 51
2018-04-03 05:30 | 54 | 42 |  |  | 43193.2292 | 58 | 55
2018-04-03 06:00 | 56 | 47 |  |  | 43193.25 | 64 | 62
2018-04-03 06:30 | 62 | 54 |  |  | 43193.2708 | 75 | 74
2018-04-03 07:00 | 62 | 58 |  |  | 43193.2917 | 81 | 81
2018-04-03 07:30 | 64 | 62 |  |  | 43193.3125 | 89 | 88
2018-04-03 08:00 | 64 | 62 |  |  | 43193.3333 | 88 | 88
2018-04-03 08:30 | 64 | 62 |  |  | 43193.3542 | 94 | 93
2018-04-03 09:00 | 68 | 66 |  |  | 43193.375 | 92 | 92
2018-04-03 09:30 | 67 | 65 |  |  | 43193.3958 | 91 | 91
2018-04-03 10:00 | 64 | 62 |  |  | 43193.4167 | 89 | 89
2018-04-03 10:30 | 59 | 58 |  |  | 43193.4375 | 87 | 87
2018-04-03 11:00 | 60 | 58 |  |  | 43193.4583 | 91 | 91
2018-04-03 11:30 | 64 | 63 |  |  | 43193.4792 | 90 | 90
2018-04-03 12:00 | 63 | 61 |  |  | 43193.5 | 89 | 88
2018-04-03 12:30 | 62 | 60 |  |  | 43193.5208 | 90 | 90
2018-04-03 13:00 | 64 | 63 |  |  | 43193.5417 | 91 | 91
2018-04-03 13:30 | 65 | 64 |  |  | 43193.5625 | 91 | 91
2018-04-03 14:00 | 66 | 65 |  |  | 43193.5833 | 91 | 91
2018-04-03 14:30 | 69 | 68 |  |  | 43193.6042 | 91 | 91
2018-04-03 15:00 | 69 | 68 |  |  | 43193.625 | 94 | 93
2018-04-03 15:30 | 70 | 68 |  |  | 43193.6458 | 95 | 94
2018-04-03 16:00 | 72 | 70 |  |  | 43193.6667 | 96 | 95
2018-04-03 16:30 | 72 | 70 |  |  | 43193.6875 | 96 | 94
2018-04-03 17:00 | 75 | 72 |  |  | 43193.7083 | 97 | 96
2018-04-03 17:30 | 74 | 70 |  |  | 43193.7292 | 95 | 93
2018-04-03 18:00 | 72 | 69 |  |  | 43193.75 | 93 | 91
2018-04-03 18:30 | 72 | 69 |  |  | 43193.7708 | 92 | 90
2018-04-03 19:00 | 75 | 72 |  |  | 43193.7917 | 93 | 91
2018-04-03 19:30 | 75 | 71 |  |  | 43193.8125 | 92 | 90
2018-04-03 20:00 | 73 | 70 |  |  | 43193.8333 | 89 | 88
2018-04-03 20:30 | 71 | 69 |  |  | 43193.8542 | 88 | 86
2018-04-03 21:00 | 65 | 63 |  |  | 43193.875 | 80 | 80
2018-04-03 21:30 | 61 | 58 |  |  | 43193.8958 | 76 | 74
2018-04-03 22:00 | 61 | 58 |  |  | 43193.9167 | 76 | 75
2018-04-03 22:30 | 61 | 58 |  |  | 43193.9375 | 75 | 75
2018-04-03 23:00 | 60 | 57 |  |  | 43193.9583 | 73 | 71
2018-04-03 23:30 | 56 | 53 |  |  | 43193.9792 | 69 | 68
2018-04-04 | 51 | 48 |  |  | 43194 | 63 | 62
2018-04-04 00:30 | 47 | 43 |  |  | 43194.0208 | 58 | 57
2018-04-04 01:00 | 47 | 43 |  |  | 43194.0417 | 57 | 56
2018-04-04 01:30 | 45 | 41 |  |  | 43194.0625 | 55 | 54
2018-04-04 02:00 | 44 | 40 |  |  | 43194.0833 | 53 | 52
2018-04-04 02:30 | 44 | 40 |  |  | 43194.1042 | 53 | 51
2018-04-04 03:00 | 43 | 39 |  |  | 43194.125 | 52 | 51
2018-04-04 03:30 | 43 | 38 |  |  | 43194.1458 | 52 | 50
2018-04-04 04:00 | 41 | 37 |  |  | 43194.1667 | 50 | 49
2018-04-04 04:30 | 41 | 37 |  |  | 43194.1875 | 50 | 49
2018-04-04 05:00 | 43 | 40 |  |  | 43194.2083 | 53 | 52
2018-04-04 05:30 | 47 | 45 |  |  | 43194.2292 | 59 | 58
2018-04-04 06:00 | 52 | 50 |  |  | 43194.25 | 66 | 66
2018-04-04 06:30 | 57 | 56 |  |  | 43194.2708 | 76 | 76
2018-04-04 07:00 | 61 | 61 |  |  | 43194.2917 | 83 | 83
2018-04-04 07:30 | 68 | 68 |  |  | 43194.3125 | 93 | 92
2018-04-04 08:00 | 69 | 69 |  |  | 43194.3333 | 96 | 96
2018-04-04 08:30 | 72 | 72 |  |  | 43194.3542 | 98 | 98
2018-04-04 09:00 | 74 | 74 |  |  | 43194.375 | 102 | 102
2018-04-04 09:30 | 75 | 75 |  |  | 43194.3958 | 100 | 100
2018-04-04 10:00 | 73 | 73 |  |  | 43194.4167 | 100 | 100
2018-04-04 10:30 | 70 | 69 |  |  | 43194.4375 | 97 | 97
2018-04-04 11:00 | 71 | 71 |  |  | 43194.4583 | 100 | 100
2018-04-04 11:30 | 73 | 73 |  |  | 43194.4792 | 101 | 101
2018-04-04 12:00 | 76 | 76 |  |  | 43194.5 | 106 | 106
2018-04-04 12:30 | 74 | 73 |  |  | 43194.5208 | 96 | 96
2018-04-04 13:00 | 71 | 70 |  |  | 43194.5417 | 93 | 93
2018-04-04 13:30 | 69 | 69 |  |  | 43194.5625 | 95 | 95
2018-04-04 14:00 | 70 | 69 |  |  | 43194.5833 | 94 | 94
2018-04-04 14:30 | 70 | 70 |  |  | 43194.6042 | 94 | 94
2018-04-04 15:00 | 73 | 72 |  |  | 43194.625 | 96 | 96
2018-04-04 15:30 | 72 | 71 |  |  | 43194.6458 | 96 | 96
2018-04-04 16:00 | 72 | 72 |  |  | 43194.6667 | 95 | 95
2018-04-04 16:30 | 73 | 72 |  |  | 43194.6875 | 95 | 95
2018-04-04 17:00 | 72 | 71 |  |  | 43194.7083 | 95 | 94
2018-04-04 17:30 | 66 | 65 |  |  | 43194.7292 | 88 | 87
2018-04-04 18:00 | 66 | 64 |  |  | 43194.75 | 86 | 85
2018-04-04 18:30 | 67 | 66 |  |  | 43194.7708 | 86 | 85
2018-04-04 19:00 | 69 | 67 |  |  | 43194.7917 | 87 | 86
2018-04-04 19:30 | 68 | 66 |  |  | 43194.8125 | 84 | 83
2018-04-04 20:00 | 65 | 64 |  |  | 43194.8333 | 81 | 81
2018-04-04 20:30 | 63 | 63 |  |  | 43194.8542 | 80 | 80
2018-04-04 21:00 | 59 | 59 |  |  | 43194.875 | 74 | 74
2018-04-04 21:30 | 56 | 56 |  |  | 43194.8958 | 70 | 70
2018-04-04 22:00 | 55 | 54 |  |  | 43194.9167 | 69 | 69
2018-04-04 22:30 | 54 | 52 |  |  | 43194.9375 | 68 | 68
2018-04-04 23:00 | 53 | 52 |  |  | 43194.9583 | 66 | 66
2018-04-04 23:30 | 50 | 49 |  |  | 43194.9792 | 63 | 63
2018-04-05 | 45 | 44 |  |  | 43195 | 58 | 58
2018-04-05 00:30 | 44 | 42 |  |  | 43195.0208 | 55 | 55
2018-04-05 01:00 | 44 | 42 |  |  | 43195.0417 | 54 | 54
2018-04-05 01:30 | 41 | 38 |  |  | 43195.0625 | 50 | 49
2018-04-05 02:00 | 42 | 38 |  |  | 43195.0833 | 49 | 49
2018-04-05 02:30 | 38 | 34 |  |  | 43195.1042 | 46 | 45
2018-04-05 03:00 | 38 | 33 |  |  | 43195.125 | 45 | 44
2018-04-05 03:30 | 37 | 33 |  |  | 43195.1458 | 45 | 44
2018-04-05 04:00 | 37 | 33 |  |  | 43195.1667 | 45 | 44
2018-04-05 04:30 | 37 | 34 |  |  | 43195.1875 | 46 | 45
2018-04-05 05:00 | 39 | 36 |  |  | 43195.2083 | 48 | 48
2018-04-05 05:30 | 43 | 41 |  |  | 43195.2292 | 53 | 52
2018-04-05 06:00 | 49 | 47 |  |  | 43195.25 | 60 | 60
2018-04-05 06:30 | 59 | 57 |  |  | 43195.2708 | 74 | 74
2018-04-05 07:00 | 61 | 60 |  |  | 43195.2917 | 80 | 80
2018-04-05 07:30 | 65 | 64 |  |  | 43195.3125 | 87 | 87
2018-04-05 08:00 | 69 | 67 |  |  | 43195.3333 | 91 | 91
2018-04-05 08:30 | 70 | 69 |  |  | 43195.3542 | 93 | 93
2018-04-05 09:00 | 67 | 66 |  |  | 43195.375 | 93 | 93
2018-04-05 09:30 | 68 | 68 |  |  | 43195.3958 | 93 | 93
2018-04-05 10:00 | 69 | 68 |  |  | 43195.4167 | 94 | 94
2018-04-05 10:30 | 68 | 68 |  |  | 43195.4375 | 93 | 93
2018-04-05 11:00 | 68 | 68 |  |  | 43195.4583 | 92 | 92
2018-04-05 11:30 | 69 | 69 |  |  | 43195.4792 | 91 | 91
2018-04-05 12:00 | 70 | 70 |  |  | 43195.5 | 95 | 95
2018-04-05 12:30 | 70 | 70 |  |  | 43195.5208 | 94 | 94
2018-04-05 13:00 | 66 | 65 |  |  | 43195.5417 | 90 | 90
2018-04-05 13:30 | 70 | 70 |  |  | 43195.5625 | 90 | 90
2018-04-05 14:00 | 71 | 70 |  |  | 43195.5833 | 91 | 91
2018-04-05 14:30 | 73 | 73 |  |  | 43195.6042 | 96 | 96
2018-04-05 15:00 | 72 | 71 |  |  | 43195.625 | 93 | 93
2018-04-05 15:30 | 70 | 69 |  |  | 43195.6458 | 93 | 93
2018-04-05 16:00 | 72 | 71 |  |  | 43195.6667 | 95 | 95
2018-04-05 16:30 | 72 | 71 |  |  | 43195.6875 | 95 | 95
2018-04-05 17:00 | 73 | 72 |  |  | 43195.7083 | 92 | 92
2018-04-05 17:30 | 72 | 71 |  |  | 43195.7292 | 91 | 91
2018-04-05 18:00 | 73 | 72 |  |  | 43195.75 | 93 | 92
2018-04-05 18:30 | 73 | 72 |  |  | 43195.7708 | 91 | 91
2018-04-05 19:00 | 72 | 71 |  |  | 43195.7917 | 90 | 89
2018-04-05 19:30 | 70 | 69 |  |  | 43195.8125 | 86 | 86
2018-04-05 20:00 | 68 | 67 |  |  | 43195.8333 | 83 | 83
2018-04-05 20:30 | 65 | 64 |  |  | 43195.8542 | 82 | 82
2018-04-05 21:00 | 62 | 61 |  |  | 43195.875 | 77 | 77
2018-04-05 21:30 | 59 | 59 |  |  | 43195.8958 | 73 | 73
2018-04-05 22:00 | 59 | 58 |  |  | 43195.9167 | 73 | 73
2018-04-05 22:30 | 55 | 54 |  |  | 43195.9375 | 69 | 69
2018-04-05 23:00 | 54 | 52 |  |  | 43195.9583 | 66 | 66
2018-04-05 23:30 | 50 | 48 |  |  | 43195.9792 | 61 | 61
2018-04-06 | 44 | 41 |  |  | 43196 | 55 | 54
2018-04-06 00:30 | 42 | 39 |  |  | 43196.0208 | 52 | 51
2018-04-06 01:00 | 43 | 40 |  |  | 43196.0417 | 53 | 51
2018-04-06 01:30 | 43 | 39 |  |  | 43196.0625 | 52 | 50
2018-04-06 02:00 | 41 | 37 |  |  | 43196.0833 | 49 | 47
2018-04-06 02:30 | 41 | 37 |  |  | 43196.1042 | 50 | 48
2018-04-06 03:00 | 41 | 37 |  |  | 43196.125 | 50 | 48
2018-04-06 03:30 | 41 | 36 |  |  | 43196.1458 | 50 | 48
2018-04-06 04:00 | 41 | 37 |  |  | 43196.1667 | 50 | 49
2018-04-06 04:30 | 41 | 37 |  |  | 43196.1875 | 50 | 49
2018-04-06 05:00 | 44 | 40 |  |  | 43196.2083 | 53 | 52
2018-04-06 05:30 | 46 | 43 |  |  | 43196.2292 | 56 | 55
2018-04-06 06:00 | 52 | 50 |  |  | 43196.25 | 64 | 63
2018-04-06 06:30 | 60 | 58 |  |  | 43196.2708 | 74 | 74
2018-04-06 07:00 | 66 | 62 |  |  | 43196.2917 | 83 | 81
2018-04-06 07:30 | 64 | 59 |  |  | 43196.3125 | 89 | 84
2018-04-06 08:00 | 65 | 61 |  |  | 43196.3333 | 90 | 87
2018-04-06 08:30 | 64 | 61 |  |  | 43196.3542 | 91 | 88
2018-04-06 09:00 | 64 | 61 |  |  | 43196.375 | 92 | 89
2018-04-06 09:30 | 65 | 61 |  |  | 43196.3958 | 94 | 90
2018-04-06 10:00 | 65 | 63 |  |  | 43196.4167 | 96 | 93
2018-04-06 10:30 | 64 | 62 |  |  | 43196.4375 | 93 | 90
2018-04-06 11:00 | 64 | 62 |  |  | 43196.4583 | 92 | 89
2018-04-06 11:30 | 64 | 62 |  |  | 43196.4792 | 92 | 89
2018-04-06 12:00 | 64 | 62 |  |  | 43196.5 | 90 | 88
2018-04-06 12:30 | 63 | 60 |  |  | 43196.5208 | 88 | 85
2018-04-06 13:00 | 64 | 61 |  |  | 43196.5417 | 89 | 86
2018-04-06 13:30 | 64 | 62 |  |  | 43196.5625 | 90 | 87
2018-04-06 14:00 | 64 | 61 |  |  | 43196.5833 | 89 | 86
2018-04-06 14:30 | 65 | 63 |  |  | 43196.6042 | 91 | 88
2018-04-06 15:00 | 68 | 66 |  |  | 43196.625 | 96 | 93
2018-04-06 15:30 | 72 | 69 |  |  | 43196.6458 | 98 | 95
2018-04-06 16:00 | 72 | 69 |  |  | 43196.6667 | 98 | 95
2018-04-06 16:30 | 72 | 69 |  |  | 43196.6875 | 97 | 94
2018-04-06 17:00 | 73 | 69 |  |  | 43196.7083 | 98 | 94
2018-04-06 17:30 | 71 | 67 |  |  | 43196.7292 | 95 | 91
2018-04-06 18:00 | 69 | 65 |  |  | 43196.75 | 93 | 87
2018-04-06 18:30 | 69 | 64 |  |  | 43196.7708 | 92 | 86
2018-04-06 19:00 | 69 | 64 |  |  | 43196.7917 | 93 | 86
2018-04-06 19:30 | 68 | 62 |  |  | 43196.8125 | 92 | 84
2018-04-06 20:00 | 67 | 60 |  |  | 43196.8333 | 88 | 80
2018-04-06 20:30 | 66 | 59 |  |  | 43196.8542 | 86 | 78
2018-04-06 21:00 | 59 | 57 |  |  | 43196.875 | 75 | 74
2018-04-06 21:30 | 56 | 54 |  |  | 43196.8958 | 72 | 71
2018-04-06 22:00 | 56 | 53 |  |  | 43196.9167 | 71 | 69
2018-04-06 22:30 | 54 | 51 |  |  | 43196.9375 | 69 | 68
2018-04-06 23:00 | 54 | 50 |  |  | 43196.9583 | 68 | 66
2018-04-06 23:30 | 51 | 46 |  |  | 43196.9792 | 64 | 61
2018-04-07 | 47 | 43 |  |  | 43197 | 59 | 57
2018-04-07 00:30 | 44 | 39 |  |  | 43197.0208 | 54 | 52
2018-04-07 01:00 | 43 | 38 |  |  | 43197.0417 | 53 | 50
2018-04-07 01:30 | 42 | 37 |  |  | 43197.0625 | 52 | 49
2018-04-07 02:00 | 41 | 36 |  |  | 43197.0833 | 51 | 48
2018-04-07 02:30 | 41 | 35 |  |  | 43197.1042 | 50 | 47
2018-04-07 03:00 | 40 | 34 |  |  | 43197.125 | 50 | 46
2018-04-07 03:30 | 39 | 34 |  |  | 43197.1458 | 50 | 46
2018-04-07 04:00 | 36 | 34 |  |  | 43197.1667 | 55 | 47
2018-04-07 04:30 | 37 | 36 |  |  | 43197.1875 | 57 | 49
2018-04-07 05:00 | 36 | 35 |  |  | 43197.2083 | 57 | 49
2018-04-07 05:30 | 38 | 36 |  |  | 43197.2292 | 58 | 49
2018-04-07 06:00 | 39 | 38 |  |  | 43197.25 | 58 | 51
2018-04-07 06:30 | 40 | 38 |  |  | 43197.2708 | 60 | 53
2018-04-07 07:00 | 39 | 38 |  |  | 43197.2917 | 60 | 54
2018-04-07 07:30 | 40 | 40 |  |  | 43197.3125 | 62 | 56
2018-04-07 08:00 | 42 | 41 |  |  | 43197.3333 | 63 | 58
2018-04-07 08:30 | 43 | 43 |  |  | 43197.3542 | 65 | 61
2018-04-07 09:00 | 44 | 44 |  |  | 43197.375 | 67 | 62
2018-04-07 09:30 | 45 | 44 |  |  | 43197.3958 | 69 | 64
2018-04-07 10:00 | 45 | 44 |  |  | 43197.4167 | 68 | 62
2018-04-07 10:30 | 44 | 43 |  |  | 43197.4375 | 66 | 60
2018-04-07 11:00 | 44 | 43 |  |  | 43197.4583 | 68 | 63
2018-04-07 11:30 | 43 | 43 |  |  | 43197.4792 | 64 | 59
2018-04-07 12:00 | 42 | 42 |  |  | 43197.5 | 60 | 56
2018-04-07 12:30 | 40 | 39 |  |  | 43197.5208 | 60 | 56
2018-04-07 13:00 | 41 | 40 |  |  | 43197.5417 | 60 | 55
2018-04-07 13:30 | 42 | 42 |  |  | 43197.5625 | 62 | 57
2018-04-07 14:00 | 43 | 42 |  |  | 43197.5833 | 61 | 57
2018-04-07 14:30 | 44 | 44 |  |  | 43197.6042 | 63 | 58
2018-04-07 15:00 | 45 | 45 |  |  | 43197.625 | 63 | 59
2018-04-07 15:30 | 47 | 47 |  |  | 43197.6458 | 67 | 62
2018-04-07 16:00 | 48 | 48 |  |  | 43197.6667 | 67 | 63
2018-04-07 16:30 | 48 | 48 |  |  | 43197.6875 | 69 | 65
2018-04-07 17:00 | 50 | 50 |  |  | 43197.7083 | 71 | 67
2018-04-07 17:30 | 51 | 51 |  |  | 43197.7292 | 72 | 67
2018-04-07 18:00 | 51 | 50 |  |  | 43197.75 | 73 | 68
2018-04-07 18:30 | 52 | 52 |  |  | 43197.7708 | 76 | 71
2018-04-07 19:00 | 54 | 53 |  |  | 43197.7917 | 77 | 73
2018-04-07 19:30 | 53 | 53 |  |  | 43197.8125 | 76 | 72
2018-04-07 20:00 | 53 | 53 |  |  | 43197.8333 | 75 | 71
2018-04-07 20:30 | 53 | 53 |  |  | 43197.8542 | 75 | 71
2018-04-07 21:00 | 51 | 50 |  |  | 43197.875 | 71 | 67
2018-04-07 21:30 | 47 | 47 |  |  | 43197.8958 | 68 | 64
2018-04-07 22:00 | 47 | 46 |  |  | 43197.9167 | 68 | 63
2018-04-07 22:30 | 48 | 48 |  |  | 43197.9375 | 68 | 64
2018-04-07 23:00 | 48 | 47 |  |  | 43197.9583 | 67 | 62
2018-04-07 23:30 | 45 | 44 |  |  | 43197.9792 | 63 | 58
2018-04-08 | 42 | 41 |  |  | 43198 | 61 | 55
2018-04-08 00:30 | 41 | 40 |  |  | 43198.0208 | 60 | 53
2018-04-08 01:00 | 40 | 39 |  |  | 43198.0417 | 58 | 50
2018-04-08 01:30 | 36 | 34 |  |  | 43198.0625 | 54 | 46
2018-04-08 02:00 | 38 | 37 |  |  | 43198.0833 | 56 | 47
2018-04-08 02:30 | 37 | 35 |  |  | 43198.1042 | 55 | 46
2018-04-08 03:00 | 37 | 35 |  |  | 43198.125 | 55 | 46
2018-04-08 03:30 | 38 | 37 |  |  | 43198.1458 | 55 | 47
2018-04-08 04:00 | 38 | 37 |  |  | 43198.1667 | 56 | 48
2018-04-08 04:30 | 38 | 37 |  |  | 43198.1875 | 56 | 49
2018-04-08 05:00 | 39 | 38 |  |  | 43198.2083 | 56 | 49
2018-04-08 05:30 | 40 | 39 |  |  | 43198.2292 | 58 | 51
2018-04-08 06:00 | 42 | 41 |  |  | 43198.25 | 61 | 54
2018-04-08 06:30 | 45 | 44 |  |  | 43198.2708 | 64 | 57
2018-04-08 07:00 | 44 | 43 |  |  | 43198.2917 | 64 | 58
2018-04-08 07:30 | 43 | 42 |  |  | 43198.3125 | 62 | 56
2018-04-08 08:00 | 42 | 41 |  |  | 43198.3333 | 60 | 56
2018-04-08 08:30 | 43 | 43 |  |  | 43198.3542 | 61 | 58
2018-04-08 09:00 | 42 | 42 |  |  | 43198.375 | 60 | 56
2018-04-08 09:30 | 39 | 39 |  |  | 43198.3958 | 56 | 53
2018-04-08 10:00 | 39 | 39 |  |  | 43198.4167 | 60 | 57
2018-04-08 10:30 | 45 | 45 |  |  | 43198.4375 | 64 | 61
2018-04-08 11:00 | 48 | 48 |  |  | 43198.4583 | 68 | 65
2018-04-08 11:30 | 50 | 50 |  |  | 43198.4792 | 70 | 67
2018-04-08 12:00 | 47 | 47 |  |  | 43198.5 | 68 | 65
2018-04-08 12:30 | 47 | 47 |  |  | 43198.5208 | 67 | 63
2018-04-08 13:00 | 46 | 46 |  |  | 43198.5417 | 65 | 62
2018-04-08 13:30 | 46 | 46 |  |  | 43198.5625 | 66 | 62
2018-04-08 14:00 | 46 | 46 |  |  | 43198.5833 | 66 | 62
2018-04-08 14:30 | 48 | 48 |  |  | 43198.6042 | 66 | 63
2018-04-08 15:00 | 49 | 49 |  |  | 43198.625 | 67 | 64
2018-04-08 15:30 | 50 | 50 |  |  | 43198.6458 | 67 | 64
2018-04-08 16:00 | 51 | 51 |  |  | 43198.6667 | 69 | 66
2018-04-08 16:30 | 53 | 52 |  |  | 43198.6875 | 71 | 68
2018-04-08 17:00 | 56 | 56 |  |  | 43198.7083 | 75 | 72
2018-04-08 17:30 | 58 | 57 |  |  | 43198.7292 | 76 | 73
2018-04-08 18:00 | 60 | 59 |  |  | 43198.75 | 79 | 75
2018-04-08 18:30 | 61 | 61 |  |  | 43198.7708 | 82 | 78
2018-04-08 19:00 | 62 | 61 |  |  | 43198.7917 | 83 | 78
2018-04-08 19:30 | 60 | 60 |  |  | 43198.8125 | 80 | 77
2018-04-08 20:00 | 59 | 58 |  |  | 43198.8333 | 79 | 75
2018-04-08 20:30 | 57 | 57 |  |  | 43198.8542 | 77 | 74
2018-04-08 21:00 | 54 | 53 |  |  | 43198.875 | 73 | 70
2018-04-08 21:30 | 51 | 50 |  |  | 43198.8958 | 70 | 65
2018-04-08 22:00 | 51 | 51 |  |  | 43198.9167 | 72 | 67
2018-04-08 22:30 | 53 | 52 |  |  | 43198.9375 | 74 | 69
2018-04-08 23:00 | 53 | 52 |  |  | 43198.9583 | 71 | 66
2018-04-08 23:30 | 49 | 48 |  |  | 43198.9792 | 69 | 63
2018-04-09 | 46 | 46 |  |  | 43199 | 65 | 59
2018-04-09 00:30 | 45 | 44 |  |  | 43199.0208 | 62 | 56
2018-04-09 01:00 | 42 | 41 |  |  | 43199.0417 | 60 | 53
2018-04-09 01:30 | 41 | 39 |  |  | 43199.0625 | 57 | 49
2018-04-09 02:00 | 41 | 40 |  |  | 43199.0833 | 57 | 50
2018-04-09 02:30 | 41 | 40 |  |  | 43199.1042 | 57 | 49
2018-04-09 03:00 | 40 | 39 |  |  | 43199.125 | 57 | 49
2018-04-09 03:30 | 39 | 38 |  |  | 43199.1458 | 56 | 48
2018-04-09 04:00 | 41 | 40 |  |  | 43199.1667 | 58 | 50
2018-04-09 04:30 | 42 | 41 |  |  | 43199.1875 | 59 | 51
2018-04-09 05:00 | 44 | 43 |  |  | 43199.2083 | 60 | 53
2018-04-09 05:30 | 47 | 46 |  |  | 43199.2292 | 62 | 56
2018-04-09 06:00 | 51 | 51 |  |  | 43199.25 | 68 | 63
2018-04-09 06:30 | 58 | 57 |  |  | 43199.2708 | 75 | 73
2018-04-09 07:00 | 62 | 62 |  |  | 43199.2917 | 83 | 81
2018-04-09 07:30 | 65 | 65 |  |  | 43199.3125 | 88 | 86
2018-04-09 08:00 | 63 | 63 |  |  | 43199.3333 | 90 | 87
2018-04-09 08:30 | 62 | 61 |  |  | 43199.3542 | 90 | 88
2018-04-09 09:00 | 62 | 61 |  |  | 43199.375 | 89 | 87
2018-04-09 09:30 | 61 | 61 |  |  | 43199.3958 | 89 | 86
2018-04-09 10:00 | 62 | 62 |  |  | 43199.4167 | 91 | 87
2018-04-09 10:30 | 63 | 63 |  |  | 43199.4375 | 92 | 88
2018-04-09 11:00 | 64 | 64 |  |  | 43199.4583 | 92 | 88
2018-04-09 11:30 | 63 | 63 |  |  | 43199.4792 | 92 | 88
2018-04-09 12:00 | 63 | 63 |  |  | 43199.5 | 91 | 87
2018-04-09 12:30 | 62 | 62 |  |  | 43199.5208 | 91 | 87
2018-04-09 13:00 | 62 | 62 |  |  | 43199.5417 | 91 | 87
2018-04-09 13:30 | 64 | 64 |  |  | 43199.5625 | 93 | 89
2018-04-09 14:00 | 65 | 65 |  |  | 43199.5833 | 93 | 90
2018-04-09 14:30 | 67 | 67 |  |  | 43199.6042 | 95 | 91
2018-04-09 15:00 | 73 | 73 |  |  | 43199.625 | 99 | 95
2018-04-09 15:30 | 73 | 73 |  |  | 43199.6458 | 99 | 95
2018-04-09 16:00 | 74 | 74 |  |  | 43199.6667 | 101 | 97
2018-04-09 16:30 | 74 | 74 |  |  | 43199.6875 | 101 | 96
2018-04-09 17:00 | 75 | 75 |  |  | 43199.7083 | 101 | 96
2018-04-09 17:30 | 73 | 72 |  |  | 43199.7292 | 98 | 92
2018-04-09 18:00 | 71 | 70 |  |  | 43199.75 | 95 | 90
2018-04-09 18:30 | 69 | 69 |  |  | 43199.7708 | 93 | 87
2018-04-09 19:00 | 71 | 70 |  |  | 43199.7917 | 94 | 87
2018-04-09 19:30 | 69 | 68 |  |  | 43199.8125 | 90 | 85
2018-04-09 20:00 | 68 | 67 |  |  | 43199.8333 | 88 | 81
2018-04-09 20:30 | 66 | 66 |  |  | 43199.8542 | 86 | 80
2018-04-09 21:00 | 61 | 61 |  |  | 43199.875 | 80 | 76
2018-04-09 21:30 | 58 | 57 |  |  | 43199.8958 | 76 | 72
2018-04-09 22:00 | 59 | 58 |  |  | 43199.9167 | 77 | 73
2018-04-09 22:30 | 55 | 55 |  |  | 43199.9375 | 74 | 70
2018-04-09 23:00 | 53 | 53 |  |  | 43199.9583 | 71 | 66
2018-04-09 23:30 | 47 | 47 |  |  | 43199.9792 | 66 | 60
2018-04-10 | 42 | 42 |  |  | 43200 | 62 | 55
2018-04-10 00:30 | 43 | 42 |  |  | 43200.0208 | 60 | 52
2018-04-10 01:00 | 42 | 41 |  |  | 43200.0417 | 59 | 50
2018-04-10 01:30 | 42 | 41 |  |  | 43200.0625 | 59 | 50
2018-04-10 02:00 | 44 | 43 |  |  | 43200.0833 | 61 | 52
2018-04-10 02:30 | 43 | 42 |  |  | 43200.1042 | 60 | 51
2018-04-10 03:00 | 41 | 40 |  |  | 43200.125 | 58 | 49
2018-04-10 03:30 | 42 | 41 |  |  | 43200.1458 | 59 | 50
2018-04-10 04:00 | 42 | 41 |  |  | 43200.1667 | 61 | 51
2018-04-10 04:30 | 42 | 41 |  |  | 43200.1875 | 60 | 51
2018-04-10 05:00 | 43 | 41 |  |  | 43200.2083 | 61 | 52
2018-04-10 05:30 | 44 | 43 |  |  | 43200.2292 | 61 | 54
2018-04-10 06:00 | 49 | 49 |  |  | 43200.25 | 67 | 61
2018-04-10 06:30 | 55 | 55 |  |  | 43200.2708 | 75 | 71
2018-04-10 07:00 | 57 | 57 |  |  | 43200.2917 | 79 | 76
2018-04-10 07:30 | 61 | 61 |  |  | 43200.3125 | 85 | 83
2018-04-10 08:00 | 63 | 63 |  |  | 43200.3333 | 87 | 87
2018-04-10 08:30 | 65 | 64 |  |  | 43200.3542 | 91 | 90
2018-04-10 09:00 | 66 | 66 |  |  | 43200.375 | 92 | 91
2018-04-10 09:30 | 65 | 65 |  |  | 43200.3958 | 91 | 90
2018-04-10 10:00 | 65 | 65 |  |  | 43200.4167 | 91 | 90
2018-04-10 10:30 | 65 | 65 |  |  | 43200.4375 | 92 | 91
2018-04-10 11:00 | 67 | 67 |  |  | 43200.4583 | 94 | 93
2018-04-10 11:30 | 68 | 68 |  |  | 43200.4792 | 95 | 94
2018-04-10 12:00 | 69 | 69 |  |  | 43200.5 | 98 | 96
2018-04-10 12:30 | 70 | 70 |  |  | 43200.5208 | 98 | 96
2018-04-10 13:00 | 70 | 70 |  |  | 43200.5417 | 97 | 95
2018-04-10 13:30 | 71 | 71 |  |  | 43200.5625 | 97 | 95
2018-04-10 14:00 | 73 | 72 |  |  | 43200.5833 | 98 | 97
2018-04-10 14:30 | 75 | 75 |  |  | 43200.6042 | 98 | 97
2018-04-10 15:00 | 78 | 78 |  |  | 43200.625 | 99 | 98
2018-04-10 15:30 | 77 | 77 |  |  | 43200.6458 | 100 | 98
2018-04-10 16:00 | 73 | 73 |  |  | 43200.6667 | 101 | 98
2018-04-10 16:30 | 72 | 72 |  |  | 43200.6875 | 100 | 98
2018-04-10 17:00 | 72 | 72 |  |  | 43200.7083 | 100 | 97
2018-04-10 17:30 | 73 | 73 |  |  | 43200.7292 | 98 | 94
2018-04-10 18:00 | 72 | 72 |  |  | 43200.75 | 97 | 94
2018-04-10 18:30 | 71 | 71 |  |  | 43200.7708 | 95 | 92
2018-04-10 19:00 | 73 | 73 |  |  | 43200.7917 | 95 | 92
2018-04-10 19:30 | 71 | 71 |  |  | 43200.8125 | 92 | 88
2018-04-10 20:00 | 68 | 68 |  |  | 43200.8333 | 88 | 85
2018-04-10 20:30 | 66 | 66 |  |  | 43200.8542 | 86 | 83
2018-04-10 21:00 | 63 | 63 |  |  | 43200.875 | 82 | 78
2018-04-10 21:30 | 59 | 59 |  |  | 43200.8958 | 78 | 74
2018-04-10 22:00 | 59 | 59 |  |  | 43200.9167 | 78 | 74
2018-04-10 22:30 | 55 | 55 |  |  | 43200.9375 | 73 | 71
2018-04-10 23:00 | 54 | 54 |  |  | 43200.9583 | 72 | 68
2018-04-10 23:30 | 50 | 49 |  |  | 43200.9792 | 68 | 64
2018-04-11 | 45 | 44 |  |  | 43201 | 63 | 59
2018-04-11 00:30 | 42 | 42 |  |  | 43201.0208 | 60 | 55
2018-04-11 01:00 | 38 | 37 |  |  | 43201.0417 | 54 | 49
2018-04-11 01:30 | 37 | 36 |  |  | 43201.0625 | 54 | 48
2018-04-11 02:00 | 37 | 36 |  |  | 43201.0833 | 53 | 47
2018-04-11 02:30 | 38 | 37 |  |  | 43201.1042 | 55 | 48
2018-04-11 03:00 | 39 | 37 |  |  | 43201.125 | 56 | 49
2018-04-11 03:30 | 39 | 38 |  |  | 43201.1458 | 56 | 49
2018-04-11 04:00 | 40 | 39 |  |  | 43201.1667 | 57 | 50
2018-04-11 04:30 | 42 | 41 |  |  | 43201.1875 | 58 | 52
2018-04-11 05:00 | 45 | 44 |  |  | 43201.2083 | 62 | 56
2018-04-11 05:30 | 48 | 47 |  |  | 43201.2292 | 64 | 59
2018-04-11 06:00 | 51 | 51 |  |  | 43201.25 | 68 | 64
2018-04-11 06:30 | 56 | 56 |  |  | 43201.2708 | 76 | 72
2018-04-11 07:00 | 55 | 55 |  |  | 43201.2917 | 77 | 74
2018-04-11 07:30 | 60 | 60 |  |  | 43201.3125 | 85 | 84
2018-04-11 08:00 | 59 | 59 |  |  | 43201.3333 | 85 | 84
2018-04-11 08:30 | 61 | 61 |  |  | 43201.3542 | 89 | 88
2018-04-11 09:00 | 63 | 63 |  |  | 43201.375 | 89 | 89
2018-04-11 09:30 | 60 | 60 |  |  | 43201.3958 | 86 | 86
2018-04-11 10:00 | 58 | 58 |  |  | 43201.4167 | 84 | 84
2018-04-11 10:30 | 57 | 57 |  |  | 43201.4375 | 84 | 84
2018-04-11 11:00 | 58 | 57 |  |  | 43201.4583 | 82 | 82
2018-04-11 11:30 | 55 | 55 |  |  | 43201.4792 | 80 | 79
2018-04-11 12:00 | 58 | 58 |  |  | 43201.5 | 81 | 81
2018-04-11 12:30 | 57 | 57 |  |  | 43201.5208 | 80 | 80
2018-04-11 13:00 | 56 | 56 |  |  | 43201.5417 | 82 | 81
2018-04-11 13:30 | 56 | 56 |  |  | 43201.5625 | 82 | 82
2018-04-11 14:00 | 54 | 54 |  |  | 43201.5833 | 79 | 78
2018-04-11 14:30 | 55 | 55 |  |  | 43201.6042 | 79 | 79
2018-04-11 15:00 | 56 | 56 |  |  | 43201.625 | 81 | 80
2018-04-11 15:30 | 58 | 58 |  |  | 43201.6458 | 82 | 81
2018-04-11 16:00 | 60 | 60 |  |  | 43201.6667 | 85 | 83
2018-04-11 16:30 | 60 | 60 |  |  | 43201.6875 | 84 | 83
2018-04-11 17:00 | 61 | 61 |  |  | 43201.7083 | 84 | 83
2018-04-11 17:30 | 61 | 61 |  |  | 43201.7292 | 83 | 82
2018-04-11 18:00 | 62 | 62 |  |  | 43201.75 | 83 | 82
2018-04-11 18:30 | 64 | 64 |  |  | 43201.7708 | 83 | 82
2018-04-11 19:00 | 64 | 64 |  |  | 43201.7917 | 83 | 82
2018-04-11 19:30 | 64 | 64 |  |  | 43201.8125 | 83 | 81
2018-04-11 20:00 | 62 | 62 |  |  | 43201.8333 | 81 | 80
2018-04-11 20:30 | 62 | 62 |  |  | 43201.8542 | 80 | 78
2018-04-11 21:00 | 59 | 59 |  |  | 43201.875 | 75 | 74
2018-04-11 21:30 | 55 | 55 |  |  | 43201.8958 | 71 | 69
2018-04-11 22:00 | 55 | 55 |  |  | 43201.9167 | 73 | 71
2018-04-11 22:30 | 54 | 54 |  |  | 43201.9375 | 72 | 69
2018-04-11 23:00 | 52 | 52 |  |  | 43201.9583 | 68 | 66
2018-04-11 23:30 | 46 | 46 |  |  | 43201.9792 | 62 | 59
2018-04-12 | 42 | 41 |  |  | 43202 | 59 | 55
2018-04-12 00:30 | 41 | 40 |  |  | 43202.0208 | 59 | 54
2018-04-12 01:00 | 43 | 42 |  |  | 43202.0417 | 60 | 55
2018-04-12 01:30 | 41 | 40 |  |  | 43202.0625 | 58 | 52
2018-04-12 02:00 | 37 | 36 |  |  | 43202.0833 | 55 | 48
2018-04-12 02:30 | 34 | 33 |  |  | 43202.1042 | 54 | 46
2018-04-12 03:00 | 36 | 35 |  |  | 43202.125 | 54 | 46
2018-04-12 03:30 | 36 | 35 |  |  | 43202.1458 | 55 | 48
2018-04-12 04:00 | 36 | 35 |  |  | 43202.1667 | 54 | 47
2018-04-12 04:30 | 38 | 37 |  |  | 43202.1875 | 56 | 49
2018-04-12 05:00 | 41 | 40 |  |  | 43202.2083 | 59 | 52
2018-04-12 05:30 | 45 | 45 |  |  | 43202.2292 | 63 | 58
2018-04-12 06:00 | 51 | 51 |  |  | 43202.25 | 69 | 65
2018-04-12 06:30 | 57 | 57 |  |  | 43202.2708 | 76 | 74
2018-04-12 07:00 | 59 | 59 |  |  | 43202.2917 | 81 | 79
2018-04-12 07:30 | 60 | 60 |  |  | 43202.3125 | 85 | 83
2018-04-12 08:00 | 64 | 64 |  |  | 43202.3333 | 89 | 87
2018-04-12 08:30 | 66 | 65 |  |  | 43202.3542 | 91 | 90
2018-04-12 09:00 | 67 | 67 |  |  | 43202.375 | 94 | 93
2018-04-12 09:30 | 66 | 66 |  |  | 43202.3958 | 93 | 92
2018-04-12 10:00 | 70 | 70 |  |  | 43202.4167 | 97 | 96
2018-04-12 10:30 | 69 | 69 |  |  | 43202.4375 | 95 | 94
2018-04-12 11:00 | 69 | 69 |  |  | 43202.4583 | 95 | 93
2018-04-12 11:30 | 70 | 70 |  |  | 43202.4792 | 92 | 90
2018-04-12 12:00 | 66 | 66 |  |  | 43202.5 | 87 | 86
2018-04-12 12:30 | 64 | 64 |  |  | 43202.5208 | 91 | 90
2018-04-12 13:00 | 65 | 65 |  |  | 43202.5417 | 91 | 90
2018-04-12 13:30 | 68 | 68 |  |  | 43202.5625 | 91 | 90
2018-04-12 14:00 | 68 | 68 |  |  | 43202.5833 | 90 | 90
2018-04-12 14:30 | 69 | 69 |  |  | 43202.6042 | 91 | 90
2018-04-12 15:00 | 68 | 68 |  |  | 43202.625 | 92 | 91
2018-04-12 15:30 | 68 | 68 |  |  | 43202.6458 | 93 | 92
2018-04-12 16:00 | 69 | 69 |  |  | 43202.6667 | 92 | 91
2018-04-12 16:30 | 66 | 66 |  |  | 43202.6875 | 89 | 88
2018-04-12 17:00 | 66 | 66 |  |  | 43202.7083 | 89 | 88
2018-04-12 17:30 | 64 | 64 |  |  | 43202.7292 | 87 | 85
2018-04-12 18:00 | 64 | 64 |  |  | 43202.75 | 86 | 84
2018-04-12 18:30 | 63 | 63 |  |  | 43202.7708 | 85 | 83
2018-04-12 19:00 | 65 | 65 |  |  | 43202.7917 | 86 | 84
2018-04-12 19:30 | 65 | 65 |  |  | 43202.8125 | 85 | 82
2018-04-12 20:00 | 63 | 62 |  |  | 43202.8333 | 82 | 80
2018-04-12 20:30 | 62 | 62 |  |  | 43202.8542 | 80 | 78
2018-04-12 21:00 | 58 | 58 |  |  | 43202.875 | 76 | 74
2018-04-12 21:30 | 56 | 56 |  |  | 43202.8958 | 74 | 72
2018-04-12 22:00 | 55 | 55 |  |  | 43202.9167 | 75 | 73
2018-04-12 22:30 | 51 | 51 |  |  | 43202.9375 | 71 | 69
2018-04-12 23:00 | 51 | 51 |  |  | 43202.9583 | 69 | 66
2018-04-12 23:30 | 48 | 48 |  |  | 43202.9792 | 66 | 63
2018-04-13 | 45 | 45 |  |  | 43203 | 63 | 59
2018-04-13 00:30 | 41 | 41 |  |  | 43203.0208 | 59 | 55
2018-04-13 01:00 | 41 | 40 |  |  | 43203.0417 | 59 | 53
2018-04-13 01:30 | 37 | 37 |  |  | 43203.0625 | 55 | 49
2018-04-13 02:00 | 36 | 35 |  |  | 43203.0833 | 54 | 47
2018-04-13 02:30 | 34 | 33 |  |  | 43203.1042 | 52 | 45
2018-04-13 03:00 | 34 | 33 |  |  | 43203.125 | 52 | 45
2018-04-13 03:30 | 36 | 35 |  |  | 43203.1458 | 53 | 47
2018-04-13 04:00 | 36 | 36 |  |  | 43203.1667 | 55 | 48
2018-04-13 04:30 | 38 | 37 |  |  | 43203.1875 | 56 | 49
2018-04-13 05:00 | 40 | 40 |  |  | 43203.2083 | 58 | 52
2018-04-13 05:30 | 42 | 42 |  |  | 43203.2292 | 60 | 55
2018-04-13 06:00 | 49 | 48 |  |  | 43203.25 | 67 | 64
2018-04-13 06:30 | 56 | 56 |  |  | 43203.2708 | 76 | 74
2018-04-13 07:00 | 58 | 58 |  |  | 43203.2917 | 82 | 81
2018-04-13 07:30 | 64 | 63 |  |  | 43203.3125 | 89 | 89
2018-04-13 08:00 | 59 | 58 |  |  | 43203.3333 | 88 | 87
2018-04-13 08:30 | 54 | 54 |  |  | 43203.3542 | 86 | 85
2018-04-13 09:00 | 52 | 51 |  |  | 43203.375 | 85 | 84
2018-04-13 09:30 | 53 | 53 |  |  | 43203.3958 | 87 | 86
2018-04-13 10:00 | 57 | 57 |  |  | 43203.4167 | 89 | 88
2018-04-13 10:30 | 67 | 66 |  |  | 43203.4375 | 94 | 93
2018-04-13 11:00 | 67 | 67 |  |  | 43203.4583 | 96 | 95
2018-04-13 11:30 | 66 | 66 |  |  | 43203.4792 | 93 | 92
2018-04-13 12:00 | 69 | 68 |  |  | 43203.5 | 90 | 89
2018-04-13 12:30 | 65 | 65 |  |  | 43203.5208 | 93 | 91
2018-04-13 13:00 | 69 | 69 |  |  | 43203.5417 | 97 | 96
2018-04-13 13:30 | 69 | 69 |  |  | 43203.5625 | 97 | 96
2018-04-13 14:00 | 67 | 67 |  |  | 43203.5833 | 95 | 93
2018-04-13 14:30 | 69 | 69 |  |  | 43203.6042 | 93 | 92
2018-04-13 15:00 | 68 | 68 |  |  | 43203.625 | 94 | 92
2018-04-13 15:30 | 69 | 69 |  |  | 43203.6458 | 96 | 94
2018-04-13 16:00 | 68 | 68 |  |  | 43203.6667 | 95 | 93
2018-04-13 16:30 | 67 | 67 |  |  | 43203.6875 | 93 | 92
2018-04-13 17:00 | 69 | 69 |  |  | 43203.7083 | 94 | 92
2018-04-13 17:30 | 68 | 68 |  |  | 43203.7292 | 92 | 89
2018-04-13 18:00 | 66 | 66 |  |  | 43203.75 | 89 | 86
2018-04-13 18:30 | 64 | 64 |  |  | 43203.7708 | 87 | 83
2018-04-13 19:00 | 63 | 63 |  |  | 43203.7917 | 86 | 82
2018-04-13 19:30 | 62 | 62 |  |  | 43203.8125 | 84 | 81
2018-04-13 20:00 | 62 | 62 |  |  | 43203.8333 | 83 | 80
2018-04-13 20:30 | 60 | 60 |  |  | 43203.8542 | 80 | 78
2018-04-13 21:00 | 58 | 58 |  |  | 43203.875 | 78 | 75
2018-04-13 21:30 | 54 | 54 |  |  | 43203.8958 | 75 | 71
2018-04-13 22:00 | 54 | 54 |  |  | 43203.9167 | 75 | 72
2018-04-13 22:30 | 52 | 52 |  |  | 43203.9375 | 73 | 69
2018-04-13 23:00 | 51 | 51 |  |  | 43203.9583 | 70 | 67
2018-04-13 23:30 | 50 | 50 |  |  | 43203.9792 | 69 | 65
2018-04-14 | 48 | 48 |  |  | 43204 | 67 | 62
2018-04-14 00:30 | 46 | 45 |  |  | 43204.0208 | 65 | 59
2018-04-14 01:00 | 43 | 41 |  |  | 43204.0417 | 62 | 55
2018-04-14 01:30 | 42 | 41 |  |  | 43204.0625 | 60 | 54
2018-04-14 02:00 | 42 | 40 |  |  | 43204.0833 | 60 | 53
2018-04-14 02:30 | 42 | 41 |  |  | 43204.1042 | 60 | 52
2018-04-14 03:00 | 41 | 40 |  |  | 43204.125 | 60 | 52
2018-04-14 03:30 | 41 | 40 |  |  | 43204.1458 | 60 | 52
2018-04-14 04:00 | 42 | 41 |  |  | 43204.1667 | 61 | 53
2018-04-14 04:30 | 43 | 42 |  |  | 43204.1875 | 61 | 54
2018-04-14 05:00 | 44 | 43 |  |  | 43204.2083 | 62 | 55
2018-04-14 05:30 | 45 | 44 |  |  | 43204.2292 | 64 | 57
2018-04-14 06:00 | 44 | 43 |  |  | 43204.25 | 62 | 56
2018-04-14 06:30 | 44 | 43 |  |  | 43204.2708 | 63 | 57
2018-04-14 07:00 | 44 | 43 |  |  | 43204.2917 | 64 | 58
2018-04-14 07:30 | 43 | 42 |  |  | 43204.3125 | 64 | 59
2018-04-14 08:00 | 44 | 43 |  |  | 43204.3333 | 66 | 62
2018-04-14 08:30 | 47 | 46 |  |  | 43204.3542 | 68 | 65
2018-04-14 09:00 | 50 | 50 |  |  | 43204.375 | 71 | 69
2018-04-14 09:30 | 54 | 54 |  |  | 43204.3958 | 77 | 74
2018-04-14 10:00 | 55 | 55 |  |  | 43204.4167 | 79 | 75
2018-04-14 10:30 | 55 | 55 |  |  | 43204.4375 | 77 | 73
2018-04-14 11:00 | 55 | 55 |  |  | 43204.4583 | 77 | 73
2018-04-14 11:30 | 56 | 56 |  |  | 43204.4792 | 78 | 74
2018-04-14 12:00 | 54 | 54 |  |  | 43204.5 | 77 | 73
2018-04-14 12:30 | 48 | 48 |  |  | 43204.5208 | 70 | 66
2018-04-14 13:00 | 52 | 52 |  |  | 43204.5417 | 72 | 68
2018-04-14 13:30 | 54 | 54 |  |  | 43204.5625 | 75 | 71
2018-04-14 14:00 | 51 | 50 |  |  | 43204.5833 | 72 | 68
2018-04-14 14:30 | 49 | 48 |  |  | 43204.6042 | 72 | 67
2018-04-14 15:00 | 52 | 51 |  |  | 43204.625 | 74 | 69
2018-04-14 15:30 | 52 | 51 |  |  | 43204.6458 | 73 | 68
2018-04-14 16:00 | 54 | 54 |  |  | 43204.6667 | 76 | 72
2018-04-14 16:30 | 57 | 56 |  |  | 43204.6875 | 78 | 74
2018-04-14 17:00 | 59 | 58 |  |  | 43204.7083 | 81 | 76
2018-04-14 17:30 | 62 | 61 |  |  | 43204.7292 | 83 | 78
2018-04-14 18:00 | 61 | 61 |  |  | 43204.75 | 82 | 78
2018-04-14 18:30 | 63 | 63 |  |  | 43204.7708 | 84 | 81
2018-04-14 19:00 | 65 | 65 |  |  | 43204.7917 | 86 | 82
2018-04-14 19:30 | 64 | 64 |  |  | 43204.8125 | 84 | 80
2018-04-14 20:00 | 63 | 62 |  |  | 43204.8333 | 82 | 79
2018-04-14 20:30 | 61 | 61 |  |  | 43204.8542 | 81 | 78
2018-04-14 21:00 | 59 | 59 |  |  | 43204.875 | 77 | 74
2018-04-14 21:30 | 56 | 56 |  |  | 43204.8958 | 74 | 71
2018-04-14 22:00 | 57 | 56 |  |  | 43204.9167 | 76 | 72
2018-04-14 22:30 | 57 | 57 |  |  | 43204.9375 | 77 | 73
2018-04-14 23:00 | 57 | 56 |  |  | 43204.9583 | 74 | 70
2018-04-14 23:30 | 55 | 54 |  |  | 43204.9792 | 71 | 67
2018-04-15 | 50 | 50 |  |  | 43205 | 69 | 63
2018-04-15 00:30 | 48 | 48 |  |  | 43205.0208 | 66 | 60
2018-04-15 01:00 | 47 | 46 |  |  | 43205.0417 | 64 | 56
2018-04-15 01:30 | 46 | 45 |  |  | 43205.0625 | 65 | 57
2018-04-15 02:00 | 46 | 45 |  |  | 43205.0833 | 63 | 55
2018-04-15 02:30 | 44 | 42 |  |  | 43205.1042 | 61 | 53
2018-04-15 03:00 | 43 | 42 |  |  | 43205.125 | 60 | 51
2018-04-15 03:30 | 43 | 42 |  |  | 43205.1458 | 60 | 51
2018-04-15 04:00 | 44 | 42 |  |  | 43205.1667 | 60 | 52
2018-04-15 04:30 | 44 | 43 |  |  | 43205.1875 | 61 | 53
2018-04-15 05:00 | 45 | 43 |  |  | 43205.2083 | 61 | 53
2018-04-15 05:30 | 45 | 44 |  |  | 43205.2292 | 62 | 54
2018-04-15 06:00 | 46 | 44 |  |  | 43205.25 | 63 | 55
2018-04-15 06:30 | 45 | 44 |  |  | 43205.2708 | 65 | 57
2018-04-15 07:00 | 45 | 43 |  |  | 43205.2917 | 65 | 57
2018-04-15 07:30 | 44 | 42 |  |  | 43205.3125 | 65 | 58
2018-04-15 08:00 | 42 | 41 |  |  | 43205.3333 | 63 | 57
2018-04-15 08:30 | 42 | 41 |  |  | 43205.3542 | 64 | 59
2018-04-15 09:00 | 44 | 43 |  |  | 43205.375 | 65 | 61
2018-04-15 09:30 | 44 | 44 |  |  | 43205.3958 | 66 | 62
2018-04-15 10:00 | 47 | 46 |  |  | 43205.4167 | 67 | 64
2018-04-15 10:30 | 47 | 47 |  |  | 43205.4375 | 68 | 65
2018-04-15 11:00 | 47 | 47 |  |  | 43205.4583 | 67 | 64
2018-04-15 11:30 | 48 | 48 |  |  | 43205.4792 | 68 | 66
2018-04-15 12:00 | 51 | 51 |  |  | 43205.5 | 71 | 68
2018-04-15 12:30 | 53 | 52 |  |  | 43205.5208 | 72 | 70
2018-04-15 13:00 | 56 | 56 |  |  | 43205.5417 | 75 | 72
2018-04-15 13:30 | 59 | 59 |  |  | 43205.5625 | 78 | 75
2018-04-15 14:00 | 61 | 61 |  |  | 43205.5833 | 78 | 74
2018-04-15 14:30 | 67 | 66 |  |  | 43205.6042 | 83 | 79
2018-04-15 15:00 | 68 | 67 |  |  | 43205.625 | 83 | 81
2018-04-15 15:30 | 69 | 68 |  |  | 43205.6458 | 83 | 82
2018-04-15 16:00 | 71 | 69 |  |  | 43205.6667 | 85 | 84
2018-04-15 16:30 | 72 | 70 |  |  | 43205.6875 | 87 | 86
2018-04-15 17:00 | 74 | 73 |  |  | 43205.7083 | 89 | 88
2018-04-15 17:30 | 75 | 74 |  |  | 43205.7292 | 91 | 90
2018-04-15 18:00 | 76 | 75 |  |  | 43205.75 | 93 | 92
2018-04-15 18:30 | 79 | 77 |  |  | 43205.7708 | 96 | 95
2018-04-15 19:00 | 82 | 81 |  |  | 43205.7917 | 100 | 99
2018-04-15 19:30 | 80 | 78 |  |  | 43205.8125 | 97 | 96
2018-04-15 20:00 | 78 | 77 |  |  | 43205.8333 | 95 | 94
2018-04-15 20:30 | 76 | 75 |  |  | 43205.8542 | 94 | 93
2018-04-15 21:00 | 71 | 70 |  |  | 43205.875 | 87 | 86
2018-04-15 21:30 | 66 | 64 |  |  | 43205.8958 | 81 | 81
2018-04-15 22:00 | 65 | 63 |  |  | 43205.9167 | 81 | 80
2018-04-15 22:30 | 63 | 61 |  |  | 43205.9375 | 79 | 78
2018-04-15 23:00 | 61 | 59 |  |  | 43205.9583 | 75 | 74
2018-04-15 23:30 | 56 | 52 |  |  | 43205.9792 | 70 | 69
2018-04-16 | 52 | 48 |  |  | 43206 | 66 | 63
2018-04-16 00:30 | 47 | 46 |  |  | 43206.0208 | 66 | 60
2018-04-16 01:00 | 47 | 45 |  |  | 43206.0417 | 65 | 59
2018-04-16 01:30 | 47 | 46 |  |  | 43206.0625 | 65 | 59
2018-04-16 02:00 | 47 | 46 |  |  | 43206.0833 | 64 | 59
2018-04-16 02:30 | 48 | 47 |  |  | 43206.1042 | 64 | 59
2018-04-16 03:00 | 46 | 44 |  |  | 43206.125 | 63 | 56
2018-04-16 03:30 | 45 | 44 |  |  | 43206.1458 | 63 | 55
2018-04-16 04:00 | 45 | 44 |  |  | 43206.1667 | 63 | 55
2018-04-16 04:30 | 45 | 44 |  |  | 43206.1875 | 63 | 56
2018-04-16 05:00 | 46 | 45 |  |  | 43206.2083 | 65 | 57
2018-04-16 05:30 | 48 | 48 |  |  | 43206.2292 | 66 | 60
2018-04-16 06:00 | 51 | 51 |  |  | 43206.25 | 69 | 65
2018-04-16 06:30 | 54 | 53 |  |  | 43206.2708 | 74 | 70
2018-04-16 07:00 | 55 | 55 |  |  | 43206.2917 | 78 | 75
2018-04-16 07:30 | 57 | 57 |  |  | 43206.3125 | 85 | 81
2018-04-16 08:00 | 58 | 58 |  |  | 43206.3333 | 86 | 82
2018-04-16 08:30 | 59 | 59 |  |  | 43206.3542 | 87 | 84
2018-04-16 09:00 | 60 | 60 |  |  | 43206.375 | 88 | 86
2018-04-16 09:30 | 58 | 58 |  |  | 43206.3958 | 87 | 84
2018-04-16 10:00 | 60 | 60 |  |  | 43206.4167 | 89 | 86
2018-04-16 10:30 | 58 | 58 |  |  | 43206.4375 | 86 | 84
2018-04-16 11:00 | 59 | 58 |  |  | 43206.4583 | 87 | 85
2018-04-16 11:30 | 59 | 59 |  |  | 43206.4792 | 88 | 85
2018-04-16 12:00 | 61 | 61 |  |  | 43206.5 | 90 | 88
2018-04-16 12:30 | 63 | 63 |  |  | 43206.5208 | 92 | 90
2018-04-16 13:00 | 66 | 66 |  |  | 43206.5417 | 94 | 92
2018-04-16 13:30 | 68 | 68 |  |  | 43206.5625 | 97 | 95
2018-04-16 14:00 | 69 | 69 |  |  | 43206.5833 | 97 | 95
2018-04-16 14:30 | 74 | 74 |  |  | 43206.6042 | 101 | 99
2018-04-16 15:00 | 78 | 78 |  |  | 43206.625 | 104 | 102
2018-04-16 15:30 | 81 | 81 |  |  | 43206.6458 | 109 | 106
2018-04-16 16:00 | 82 | 82 |  |  | 43206.6667 | 109 | 105
2018-04-16 16:30 | 83 | 83 |  |  | 43206.6875 | 109 | 106
2018-04-16 17:00 | 82 | 82 |  |  | 43206.7083 | 111 | 105
2018-04-16 17:30 | 80 | 80 |  |  | 43206.7292 | 111 | 102
2018-04-16 18:00 | 78 | 78 |  |  | 43206.75 | 107 | 98
2018-04-16 18:30 | 78 | 77 |  |  | 43206.7708 | 104 | 96
2018-04-16 19:00 | 78 | 77 |  |  | 43206.7917 | 105 | 96
2018-04-16 19:30 | 79 | 78 |  |  | 43206.8125 | 105 | 98
2018-04-16 20:00 | 78 | 77 |  |  | 43206.8333 | 103 | 96
2018-04-16 20:30 | 75 | 74 |  |  | 43206.8542 | 99 | 92
2018-04-16 21:00 | 70 | 70 |  |  | 43206.875 | 90 | 87
2018-04-16 21:30 | 67 | 67 |  |  | 43206.8958 | 86 | 83
2018-04-16 22:00 | 66 | 66 |  |  | 43206.9167 | 86 | 83
2018-04-16 22:30 | 58 | 58 |  |  | 43206.9375 | 78 | 75
2018-04-16 23:00 | 54 | 54 |  |  | 43206.9583 | 72 | 68
2018-04-16 23:30 | 48 | 48 |  |  | 43206.9792 | 68 | 63
2018-04-17 | 47 | 46 |  |  | 43207 | 65 | 59
2018-04-17 00:30 | 44 | 43 |  |  | 43207.0208 | 62 | 55
2018-04-17 01:00 | 41 | 40 |  |  | 43207.0417 | 58 | 50
2018-04-17 01:30 | 42 | 40 |  |  | 43207.0625 | 57 | 49
2018-04-17 02:00 | 40 | 39 |  |  | 43207.0833 | 56 | 47
2018-04-17 02:30 | 38 | 37 |  |  | 43207.1042 | 54 | 45
2018-04-17 03:00 | 38 | 37 |  |  | 43207.125 | 54 | 45
2018-04-17 03:30 | 38 | 36 |  |  | 43207.1458 | 54 | 45
2018-04-17 04:00 | 39 | 38 |  |  | 43207.1667 | 55 | 46
2018-04-17 04:30 | 40 | 39 |  |  | 43207.1875 | 56 | 48
2018-04-17 05:00 | 41 | 40 |  |  | 43207.2083 | 58 | 50
2018-04-17 05:30 | 46 | 45 |  |  | 43207.2292 | 62 | 55
2018-04-17 06:00 | 52 | 52 |  |  | 43207.25 | 67 | 63
2018-04-17 06:30 | 57 | 57 |  |  | 43207.2708 | 75 | 72
2018-04-17 07:00 | 61 | 61 |  |  | 43207.2917 | 82 | 80
2018-04-17 07:30 | 64 | 64 |  |  | 43207.3125 | 87 | 85
2018-04-17 08:00 | 65 | 65 |  |  | 43207.3333 | 90 | 88
2018-04-17 08:30 | 67 | 67 |  |  | 43207.3542 | 92 | 91
2018-04-17 09:00 | 67 | 67 |  |  | 43207.375 | 92 | 90
2018-04-17 09:30 | 68 | 68 |  |  | 43207.3958 | 93 | 92
2018-04-17 10:00 | 69 | 69 |  |  | 43207.4167 | 94 | 93
2018-04-17 10:30 | 68 | 67 |  |  | 43207.4375 | 92 | 90
2018-04-17 11:00 | 68 | 68 |  |  | 43207.4583 | 94 | 93
2018-04-17 11:30 | 69 | 69 |  |  | 43207.4792 | 94 | 93
2018-04-17 12:00 | 69 | 69 |  |  | 43207.5 | 98 | 93
2018-04-17 12:30 | 71 | 70 |  |  | 43207.5208 | 99 | 93
2018-04-17 13:00 | 71 | 70 |  |  | 43207.5417 | 101 | 95
2018-04-17 13:30 | 71 | 71 |  |  | 43207.5625 | 101 | 95
2018-04-17 14:00 | 70 | 69 |  |  | 43207.5833 | 99 | 93
2018-04-17 14:30 | 73 | 72 |  |  | 43207.6042 | 101 | 95
2018-04-17 15:00 | 76 | 75 |  |  | 43207.625 | 104 | 98
2018-04-17 15:30 | 78 | 76 |  |  | 43207.6458 | 111 | 101
2018-04-17 16:00 | 80 | 78 |  |  | 43207.6667 | 113 | 103
2018-04-17 16:30 | 86 | 83 |  |  | 43207.6875 | 117 | 105
2018-04-17 17:00 | 89 | 86 |  |  | 43207.7083 | 120 | 107
2018-04-17 17:30 | 87 | 84 |  |  | 43207.7292 | 114 | 104
2018-04-17 18:00 | 83 | 81 |  |  | 43207.75 | 110 | 100
2018-04-17 18:30 | 82 | 79 |  |  | 43207.7708 | 107 | 97
2018-04-17 19:00 | 82 | 79 |  |  | 43207.7917 | 107 | 98
2018-04-17 19:30 | 80 | 79 |  |  | 43207.8125 | 101 | 96
2018-04-17 20:00 | 78 | 77 |  |  | 43207.8333 | 98 | 93
2018-04-17 20:30 | 75 | 75 |  |  | 43207.8542 | 95 | 90
2018-04-17 21:00 | 71 | 70 |  |  | 43207.875 | 90 | 85
2018-04-17 21:30 | 67 | 67 |  |  | 43207.8958 | 84 | 81
2018-04-17 22:00 | 66 | 66 |  |  | 43207.9167 | 84 | 82
2018-04-17 22:30 | 60 | 60 |  |  | 43207.9375 | 79 | 76
2018-04-17 23:00 | 57 | 57 |  |  | 43207.9583 | 75 | 71
2018-04-17 23:30 | 52 | 52 |  |  | 43207.9792 | 70 | 65
2018-04-18 | 47 | 47 |  |  | 43208 | 65 | 60
2018-04-18 00:30 | 44 | 44 |  |  | 43208.0208 | 61 | 56
2018-04-18 01:00 | 43 | 42 |  |  | 43208.0417 | 60 | 54
2018-04-18 01:30 | 41 | 41 |  |  | 43208.0625 | 57 | 50
2018-04-18 02:00 | 40 | 39 |  |  | 43208.0833 | 58 | 50
2018-04-18 02:30 | 40 | 39 |  |  | 43208.1042 | 57 | 50
2018-04-18 03:00 | 41 | 39 |  |  | 43208.125 | 57 | 50
2018-04-18 03:30 | 41 | 40 |  |  | 43208.1458 | 57 | 49
2018-04-18 04:00 | 41 | 40 |  |  | 43208.1667 | 58 | 51
2018-04-18 04:30 | 42 | 42 |  |  | 43208.1875 | 58 | 51
2018-04-18 05:00 | 44 | 43 |  |  | 43208.2083 | 60 | 53
2018-04-18 05:30 | 47 | 47 |  |  | 43208.2292 | 63 | 57
2018-04-18 06:00 | 54 | 54 |  |  | 43208.25 | 71 | 66
2018-04-18 06:30 | 63 | 63 |  |  | 43208.2708 | 82 | 79
2018-04-18 07:00 | 69 | 69 |  |  | 43208.2917 | 90 | 88
2018-04-18 07:30 | 74 | 74 |  |  | 43208.3125 | 98 | 96
2018-04-18 08:00 | 76 | 76 |  |  | 43208.3333 | 101 | 100
2018-04-18 08:30 | 79 | 79 |  |  | 43208.3542 | 103 | 102
2018-04-18 09:00 | 79 | 79 |  |  | 43208.375 | 107 | 105
2018-04-18 09:30 | 78 | 78 |  |  | 43208.3958 | 109 | 103
2018-04-18 10:00 | 79 | 79 |  |  | 43208.4167 | 108 | 102
2018-04-18 10:30 | 79 | 79 |  |  | 43208.4375 | 106 | 101
2018-04-18 11:00 | 78 | 78 |  |  | 43208.4583 | 107 | 102
2018-04-18 11:30 | 76 | 76 |  |  | 43208.4792 | 111 | 105
2018-04-18 12:00 | 79 | 79 |  |  | 43208.5 | 108 | 103
2018-04-18 12:30 | 75 | 75 |  |  | 43208.5208 | 107 | 101
2018-04-18 13:00 | 75 | 75 |  |  | 43208.5417 | 103 | 97
2018-04-18 13:30 | 77 | 77 |  |  | 43208.5625 | 104 | 98
2018-04-18 14:00 | 74 | 74 |  |  | 43208.5833 | 102 | 96
2018-04-18 14:30 | 74 | 73 |  |  | 43208.6042 | 104 | 97
2018-04-18 15:00 | 75 | 74 |  |  | 43208.625 | 105 | 98
2018-04-18 15:30 | 75 | 74 |  |  | 43208.6458 | 103 | 96
2018-04-18 16:00 | 74 | 74 |  |  | 43208.6667 | 103 | 95
2018-04-18 16:30 | 79 | 78 |  |  | 43208.6875 | 107 | 99
2018-04-18 17:00 | 79 | 78 |  |  | 43208.7083 | 106 | 98
2018-04-18 17:30 | 77 | 77 |  |  | 43208.7292 | 104 | 95
2018-04-18 18:00 | 75 | 74 |  |  | 43208.75 | 101 | 92
2018-04-18 18:30 | 75 | 74 |  |  | 43208.7708 | 101 | 91
2018-04-18 19:00 | 78 | 77 |  |  | 43208.7917 | 102 | 92
2018-04-18 19:30 | 73 | 73 |  |  | 43208.8125 | 95 | 88
2018-04-18 20:00 | 71 | 71 |  |  | 43208.8333 | 91 | 85
2018-04-18 20:30 | 69 | 69 |  |  | 43208.8542 | 88 | 83
2018-04-18 21:00 | 66 | 66 |  |  | 43208.875 | 82 | 79
2018-04-18 21:30 | 63 | 63 |  |  | 43208.8958 | 77 | 74
2018-04-18 22:00 | 60 | 60 |  |  | 43208.9167 | 76 | 73
2018-04-18 22:30 | 55 | 55 |  |  | 43208.9375 | 72 | 68
2018-04-18 23:00 | 51 | 51 |  |  | 43208.9583 | 66 | 61
2018-04-18 23:30 | 47 | 46 |  |  | 43208.9792 | 63 | 58
2018-04-19 | 42 | 42 |  |  | 43209 | 58 | 52
2018-04-19 00:30 | 39 | 39 |  |  | 43209.0208 | 54 | 47
2018-04-19 01:00 | 38 | 37 |  |  | 43209.0417 | 53 | 45
2018-04-19 01:30 | 35 | 34 |  |  | 43209.0625 | 50 | 41
2018-04-19 02:00 | 34 | 32 |  |  | 43209.0833 | 49 | 41
2018-04-19 02:30 | 33 | 32 |  |  | 43209.1042 | 49 | 40
2018-04-19 03:00 | 32 | 31 |  |  | 43209.125 | 49 | 40
2018-04-19 03:30 | 33 | 32 |  |  | 43209.1458 | 49 | 41
2018-04-19 04:00 | 35 | 33 |  |  | 43209.1667 | 50 | 42
2018-04-19 04:30 | 36 | 35 |  |  | 43209.1875 | 51 | 44
2018-04-19 05:00 | 39 | 37 |  |  | 43209.2083 | 54 | 47
2018-04-19 05:30 | 43 | 42 |  |  | 43209.2292 | 58 | 52
2018-04-19 06:00 | 46 | 46 |  |  | 43209.25 | 62 | 57
2018-04-19 06:30 | 55 | 55 |  |  | 43209.2708 | 74 | 71
2018-04-19 07:00 | 60 | 59 |  |  | 43209.2917 | 83 | 79
2018-04-19 07:30 | 62 | 62 |  |  | 43209.3125 | 88 | 85
2018-04-19 08:00 | 63 | 63 |  |  | 43209.3333 | 90 | 88
2018-04-19 08:30 | 64 | 64 |  |  | 43209.3542 | 91 | 90
2018-04-19 09:00 | 66 | 66 |  |  | 43209.375 | 92 | 91
2018-04-19 09:30 | 65 | 65 |  |  | 43209.3958 | 92 | 91
2018-04-19 10:00 | 65 | 65 |  |  | 43209.4167 | 94 | 92
2018-04-19 10:30 | 67 | 67 |  |  | 43209.4375 | 96 | 94
2018-04-19 11:00 | 70 | 70 |  |  | 43209.4583 | 96 | 95
2018-04-19 11:30 | 66 | 66 |  |  | 43209.4792 | 93 | 92
2018-04-19 12:00 | 66 | 66 |  |  | 43209.5 | 93 | 91
2018-04-19 12:30 | 67 | 67 |  |  | 43209.5208 | 94 | 93
2018-04-19 13:00 | 68 | 68 |  |  | 43209.5417 | 94 | 93
2018-04-19 13:30 | 67 | 67 |  |  | 43209.5625 | 95 | 92
2018-04-19 14:00 | 65 | 65 |  |  | 43209.5833 | 93 | 89
2018-04-19 14:30 | 65 | 65 |  |  | 43209.6042 | 91 | 87
2018-04-19 15:00 | 65 | 64 |  |  | 43209.625 | 92 | 89
2018-04-19 15:30 | 63 | 63 |  |  | 43209.6458 | 93 | 90
2018-04-19 16:00 | 63 | 63 |  |  | 43209.6667 | 93 | 89
2018-04-19 16:30 | 66 | 65 |  |  | 43209.6875 | 93 | 89
2018-04-19 17:00 | 63 | 63 |  |  | 43209.7083 | 92 | 86
2018-04-19 17:30 | 63 | 62 |  |  | 43209.7292 | 94 | 84
2018-04-19 18:00 | 66 | 65 |  |  | 43209.75 | 95 | 86
2018-04-19 18:30 | 65 | 64 |  |  | 43209.7708 | 93 | 84
2018-04-19 19:00 | 69 | 67 |  |  | 43209.7917 | 98 | 87
2018-04-19 19:30 | 71 | 70 |  |  | 43209.8125 | 99 | 89
2018-04-19 20:00 | 68 | 67 |  |  | 43209.8333 | 90 | 85
2018-04-19 20:30 | 64 | 64 |  |  | 43209.8542 | 84 | 81
2018-04-19 21:00 | 59 | 59 |  |  | 43209.875 | 78 | 75
2018-04-19 21:30 | 56 | 56 |  |  | 43209.8958 | 73 | 70
2018-04-19 22:00 | 52 | 52 |  |  | 43209.9167 | 72 | 68
2018-04-19 22:30 | 50 | 49 |  |  | 43209.9375 | 69 | 65
2018-04-19 23:00 | 50 | 50 |  |  | 43209.9583 | 68 | 64
2018-04-19 23:30 | 50 | 49 |  |  | 43209.9792 | 67 | 63
2018-04-20 | 47 | 46 |  |  | 43210 | 65 | 60
2018-04-20 00:30 | 42 | 42 |  |  | 43210.0208 | 59 | 53
2018-04-20 01:00 | 39 | 38 |  |  | 43210.0417 | 54 | 47
2018-04-20 01:30 | 37 | 36 |  |  | 43210.0625 | 52 | 44
2018-04-20 02:00 | 37 | 36 |  |  | 43210.0833 | 52 | 44
2018-04-20 02:30 | 37 | 36 |  |  | 43210.1042 | 52 | 43
2018-04-20 03:00 | 36 | 35 |  |  | 43210.125 | 51 | 42
2018-04-20 03:30 | 37 | 36 |  |  | 43210.1458 | 52 | 43
2018-04-20 04:00 | 38 | 36 |  |  | 43210.1667 | 53 | 45
2018-04-20 04:30 | 40 | 39 |  |  | 43210.1875 | 56 | 48
2018-04-20 05:00 | 42 | 41 |  |  | 43210.2083 | 57 | 50
2018-04-20 05:30 | 46 | 46 |  |  | 43210.2292 | 61 | 55
2018-04-20 06:00 | 51 | 51 |  |  | 43210.25 | 65 | 61
2018-04-20 06:30 | 58 | 58 |  |  | 43210.2708 | 75 | 73
2018-04-20 07:00 | 63 | 62 |  |  | 43210.2917 | 83 | 82
2018-04-20 07:30 | 67 | 67 |  |  | 43210.3125 | 90 | 89
2018-04-20 08:00 | 63 | 63 |  |  | 43210.3333 | 88 | 87
2018-04-20 08:30 | 63 | 63 |  |  | 43210.3542 | 87 | 86
2018-04-20 09:00 | 63 | 63 |  |  | 43210.375 | 89 | 88
2018-04-20 09:30 | 64 | 64 |  |  | 43210.3958 | 89 | 89
2018-04-20 10:00 | 67 | 67 |  |  | 43210.4167 | 93 | 92
2018-04-20 10:30 | 66 | 66 |  |  | 43210.4375 | 92 | 91
2018-04-20 11:00 | 67 | 67 |  |  | 43210.4583 | 90 | 90
2018-04-20 11:30 | 69 | 69 |  |  | 43210.4792 | 92 | 90
2018-04-20 12:00 | 70 | 70 |  |  | 43210.5 | 98 | 93
2018-04-20 12:30 | 75 | 75 |  |  | 43210.5208 | 105 | 100
2018-04-20 13:00 | 75 | 74 |  |  | 43210.5417 | 106 | 99
2018-04-20 13:30 | 73 | 72 |  |  | 43210.5625 | 102 | 95
2018-04-20 14:00 | 72 | 71 |  |  | 43210.5833 | 100 | 92
2018-04-20 14:30 | 74 | 74 |  |  | 43210.6042 | 100 | 93
2018-04-20 15:00 | 74 | 73 |  |  | 43210.625 | 101 | 94
2018-04-20 15:30 | 75 | 74 |  |  | 43210.6458 | 102 | 94
2018-04-20 16:00 | 76 | 75 |  |  | 43210.6667 | 103 | 96
2018-04-20 16:30 | 76 | 75 |  |  | 43210.6875 | 103 | 96
2018-04-20 17:00 | 72 | 71 |  |  | 43210.7083 | 100 | 91
2018-04-20 17:30 | 70 | 69 |  |  | 43210.7292 | 97 | 89
2018-04-20 18:00 | 69 | 68 |  |  | 43210.75 | 96 | 86
2018-04-20 18:30 | 66 | 66 |  |  | 43210.7708 | 89 | 83
2018-04-20 19:00 | 68 | 68 |  |  | 43210.7917 | 92 | 86
2018-04-20 19:30 | 69 | 68 |  |  | 43210.8125 | 91 | 85
2018-04-20 20:00 | 67 | 67 |  |  | 43210.8333 | 87 | 83
2018-04-20 20:30 | 64 | 64 |  |  | 43210.8542 | 86 | 81
2018-04-20 21:00 | 60 | 59 |  |  | 43210.875 | 80 | 74
2018-04-20 21:30 | 52 | 52 |  |  | 43210.8958 | 70 | 67
2018-04-20 22:00 | 53 | 53 |  |  | 43210.9167 | 72 | 69
2018-04-20 22:30 | 53 | 53 |  |  | 43210.9375 | 71 | 68
2018-04-20 23:00 | 53 | 52 |  |  | 43210.9583 | 69 | 65
2018-04-20 23:30 | 49 | 49 |  |  | 43210.9792 | 66 | 62
2018-04-21 | 44 | 44 |  |  | 43211 | 62 | 56
2018-04-21 00:30 | 43 | 42 |  |  | 43211.0208 | 59 | 52
2018-04-21 01:00 | 40 | 39 |  |  | 43211.0417 | 56 | 49
2018-04-21 01:30 | 39 | 37 |  |  | 43211.0625 | 55 | 47
2018-04-21 02:00 | 39 | 38 |  |  | 43211.0833 | 54 | 46
2018-04-21 02:30 | 37 | 36 |  |  | 43211.1042 | 53 | 45
2018-04-21 03:00 | 36 | 35 |  |  | 43211.125 | 52 | 43
2018-04-21 03:30 | 36 | 35 |  |  | 43211.1458 | 51 | 42
2018-04-21 04:00 | 36 | 35 |  |  | 43211.1667 | 51 | 42
2018-04-21 04:30 | 37 | 35 |  |  | 43211.1875 | 52 | 43
2018-04-21 05:00 | 35 | 34 |  |  | 43211.2083 | 49 | 42
2018-04-21 05:30 | 37 | 36 |  |  | 43211.2292 | 51 | 44
2018-04-21 06:00 | 37 | 36 |  |  | 43211.25 | 52 | 46
2018-04-21 06:30 | 38 | 38 |  |  | 43211.2708 | 54 | 49
2018-04-21 07:00 | 40 | 40 |  |  | 43211.2917 | 57 | 52
2018-04-21 07:30 | 40 | 39 |  |  | 43211.3125 | 57 | 53
2018-04-21 08:00 | 40 | 39 |  |  | 43211.3333 | 58 | 54
2018-04-21 08:30 | 41 | 41 |  |  | 43211.3542 | 60 | 57
2018-04-21 09:00 | 42 | 42 |  |  | 43211.375 | 60 | 58
2018-04-21 09:30 | 40 | 40 |  |  | 43211.3958 | 58 | 56
2018-04-21 10:00 | 41 | 41 |  |  | 43211.4167 | 58 | 56
2018-04-21 10:30 | 41 | 41 |  |  | 43211.4375 | 58 | 56
2018-04-21 11:00 | 44 | 43 |  |  | 43211.4583 | 59 | 57
2018-04-21 11:30 | 44 | 44 |  |  | 43211.4792 | 61 | 60
2018-04-21 12:00 | 46 | 46 |  |  | 43211.5 | 63 | 61
2018-04-21 12:30 | 44 | 44 |  |  | 43211.5208 | 63 | 60
2018-04-21 13:00 | 43 | 43 |  |  | 43211.5417 | 63 | 59
2018-04-21 13:30 | 46 | 46 |  |  | 43211.5625 | 60 | 56
2018-04-21 14:00 | 48 | 48 |  |  | 43211.5833 | 64 | 60
2018-04-21 14:30 | 51 | 51 |  |  | 43211.6042 | 70 | 66
2018-04-21 15:00 | 52 | 52 |  |  | 43211.625 | 73 | 70
2018-04-21 15:30 | 50 | 50 |  |  | 43211.6458 | 71 | 67
2018-04-21 16:00 | 51 | 50 |  |  | 43211.6667 | 68 | 64
2018-04-21 16:30 | 54 | 54 |  |  | 43211.6875 | 72 | 68
2018-04-21 17:00 | 55 | 55 |  |  | 43211.7083 | 74 | 70
2018-04-21 17:30 | 58 | 57 |  |  | 43211.7292 | 76 | 72
2018-04-21 18:00 | 59 | 58 |  |  | 43211.75 | 78 | 74
2018-04-21 18:30 | 60 | 60 |  |  | 43211.7708 | 79 | 76
2018-04-21 19:00 | 61 | 61 |  |  | 43211.7917 | 80 | 76
2018-04-21 19:30 | 58 | 58 |  |  | 43211.8125 | 77 | 73
2018-04-21 20:00 | 56 | 56 |  |  | 43211.8333 | 74 | 71
2018-04-21 20:30 | 55 | 54 |  |  | 43211.8542 | 72 | 69
2018-04-21 21:00 | 51 | 51 |  |  | 43211.875 | 68 | 64
2018-04-21 21:30 | 48 | 48 |  |  | 43211.8958 | 66 | 62
2018-04-21 22:00 | 47 | 47 |  |  | 43211.9167 | 66 | 62
2018-04-21 22:30 | 48 | 47 |  |  | 43211.9375 | 65 | 61
2018-04-21 23:00 | 47 | 47 |  |  | 43211.9583 | 64 | 59
2018-04-21 23:30 | 45 | 44 |  |  | 43211.9792 | 61 | 56
2018-04-22 | 42 | 41 |  |  | 43212 | 59 | 53
2018-04-22 00:30 | 38 | 37 |  |  | 43212.0208 | 55 | 47
2018-04-22 01:00 | 35 | 33 |  |  | 43212.0417 | 51 | 43
2018-04-22 01:30 | 33 | 31 |  |  | 43212.0625 | 49 | 40
2018-04-22 02:00 | 33 | 31 |  |  | 43212.0833 | 49 | 40
2018-04-22 02:30 | 33 | 32 |  |  | 43212.1042 | 47 | 41
2018-04-22 03:00 | 32 | 31 |  |  | 43212.125 | 45 | 39
2018-04-22 03:30 | 30 | 29 |  |  | 43212.1458 | 44 | 38
2018-04-22 04:00 | 30 | 30 |  |  | 43212.1667 | 43 | 37
2018-04-22 04:30 | 30 | 30 |  |  | 43212.1875 | 45 | 39
2018-04-22 05:00 | 31 | 30 |  |  | 43212.2083 | 45 | 39
2018-04-22 05:30 | 33 | 33 |  |  | 43212.2292 | 47 | 41
2018-04-22 06:00 | 33 | 32 |  |  | 43212.25 | 46 | 41
2018-04-22 06:30 | 32 | 32 |  |  | 43212.2708 | 46 | 41
2018-04-22 07:00 | 32 | 31 |  |  | 43212.2917 | 47 | 42
2018-04-22 07:30 | 32 | 32 |  |  | 43212.3125 | 48 | 44
2018-04-22 08:00 | 32 | 32 |  |  | 43212.3333 | 48 | 44
2018-04-22 08:30 | 34 | 34 |  |  | 43212.3542 | 50 | 46
2018-04-22 09:00 | 35 | 35 |  |  | 43212.375 | 51 | 48
2018-04-22 09:30 | 37 | 37 |  |  | 43212.3958 | 54 | 52
2018-04-22 10:00 | 42 | 42 |  |  | 43212.4167 | 59 | 58
2018-04-22 10:30 | 41 | 41 |  |  | 43212.4375 | 60 | 59
2018-04-22 11:00 | 39 | 39 |  |  | 43212.4583 | 53 | 52
2018-04-22 11:30 | 40 | 40 |  |  | 43212.4792 | 55 | 54
2018-04-22 12:00 | 45 | 45 |  |  | 43212.5 | 56 | 55
2018-04-22 12:30 | 37 | 37 |  |  | 43212.5208 | 49 | 48
2018-04-22 13:00 | 39 | 39 |  |  | 43212.5417 | 53 | 52
2018-04-22 13:30 | 39 | 39 |  |  | 43212.5625 | 51 | 50
2018-04-22 14:00 | 41 | 41 |  |  | 43212.5833 | 54 | 53
2018-04-22 14:30 | 45 | 45 |  |  | 43212.6042 | 55 | 54
2018-04-22 15:00 | 41 | 41 |  |  | 43212.625 | 54 | 53
2018-04-22 15:30 | 44 | 44 |  |  | 43212.6458 | 56 | 55
2018-04-22 16:00 | 44 | 44 |  |  | 43212.6667 | 59 | 58
2018-04-22 16:30 | 48 | 48 |  |  | 43212.6875 | 63 | 62
2018-04-22 17:00 | 54 | 54 |  |  | 43212.7083 | 68 | 67
2018-04-22 17:30 | 56 | 56 |  |  | 43212.7292 | 72 | 70
2018-04-22 18:00 | 57 | 57 |  |  | 43212.75 | 75 | 73
2018-04-22 18:30 | 57 | 57 |  |  | 43212.7708 | 77 | 73
2018-04-22 19:00 | 60 | 60 |  |  | 43212.7917 | 78 | 75
2018-04-22 19:30 | 59 | 59 |  |  | 43212.8125 | 76 | 73
2018-04-22 20:00 | 56 | 56 |  |  | 43212.8333 | 74 | 72
2018-04-22 20:30 | 55 | 54 |  |  | 43212.8542 | 72 | 70
2018-04-22 21:00 | 51 | 51 |  |  | 43212.875 | 68 | 65
2018-04-22 21:30 | 48 | 48 |  |  | 43212.8958 | 64 | 62
2018-04-22 22:00 | 46 | 46 |  |  | 43212.9167 | 64 | 61
2018-04-22 22:30 | 46 | 46 |  |  | 43212.9375 | 64 | 61
2018-04-22 23:00 | 46 | 46 |  |  | 43212.9583 | 61 | 58
2018-04-22 23:30 | 43 | 43 |  |  | 43212.9792 | 58 | 54
2018-04-23 | 39 | 39 |  |  | 43213 | 54 | 50
2018-04-23 00:30 | 36 | 36 |  |  | 43213.0208 | 50 | 45
2018-04-23 01:00 | 34 | 33 |  |  | 43213.0417 | 48 | 42
2018-04-23 01:30 | 32 | 31 |  |  | 43213.0625 | 45 | 40
2018-04-23 02:00 | 32 | 31 |  |  | 43213.0833 | 45 | 40
2018-04-23 02:30 | 33 | 32 |  |  | 43213.1042 | 46 | 41
2018-04-23 03:00 | 33 | 32 |  |  | 43213.125 | 45 | 40
2018-04-23 03:30 | 32 | 31 |  |  | 43213.1458 | 45 | 40
2018-04-23 04:00 | 31 | 30 |  |  | 43213.1667 | 44 | 39
2018-04-23 04:30 | 34 | 33 |  |  | 43213.1875 | 47 | 42
2018-04-23 05:00 | 38 | 37 |  |  | 43213.2083 | 50 | 46
2018-04-23 05:30 | 39 | 39 |  |  | 43213.2292 | 52 | 49
2018-04-23 06:00 | 44 | 44 |  |  | 43213.25 | 57 | 55
2018-04-23 06:30 | 50 | 50 |  |  | 43213.2708 | 66 | 66
2018-04-23 07:00 | 55 | 55 |  |  | 43213.2917 | 74 | 73
2018-04-23 07:30 | 59 | 59 |  |  | 43213.3125 | 81 | 81
2018-04-23 08:00 | 59 | 58 |  |  | 43213.3333 | 81 | 80
2018-04-23 08:30 | 60 | 60 |  |  | 43213.3542 | 83 | 82
2018-04-23 09:00 | 59 | 59 |  |  | 43213.375 | 81 | 81
2018-04-23 09:30 | 58 | 57 |  |  | 43213.3958 | 80 | 79
2018-04-23 10:00 | 57 | 56 |  |  | 43213.4167 | 78 | 78
2018-04-23 10:30 | 57 | 56 |  |  | 43213.4375 | 78 | 78
2018-04-23 11:00 | 58 | 57 |  |  | 43213.4583 | 80 | 80
2018-04-23 11:30 | 59 | 58 |  |  | 43213.4792 | 79 | 79
2018-04-23 12:00 | 60 | 59 |  |  | 43213.5 | 81 | 81
2018-04-23 12:30 | 61 | 60 |  |  | 43213.5208 | 82 | 82
2018-04-23 13:00 | 60 | 59 |  |  | 43213.5417 | 83 | 83
2018-04-23 13:30 | 61 | 61 |  |  | 43213.5625 | 85 | 84
2018-04-23 14:00 | 65 | 65 |  |  | 43213.5833 | 89 | 87
2018-04-23 14:30 | 68 | 68 |  |  | 43213.6042 | 94 | 92
2018-04-23 15:00 | 68 | 67 |  |  | 43213.625 | 92 | 90
2018-04-23 15:30 | 66 | 66 |  |  | 43213.6458 | 90 | 88
2018-04-23 16:00 | 68 | 68 |  |  | 43213.6667 | 91 | 88
2018-04-23 16:30 | 69 | 69 |  |  | 43213.6875 | 92 | 89
2018-04-23 17:00 | 70 | 70 |  |  | 43213.7083 | 95 | 91
2018-04-23 17:30 | 70 | 70 |  |  | 43213.7292 | 94 | 90
2018-04-23 18:00 | 71 | 71 |  |  | 43213.75 | 95 | 91
2018-04-23 18:30 | 68 | 68 |  |  | 43213.7708 | 92 | 87
2018-04-23 19:00 | 72 | 72 |  |  | 43213.7917 | 94 | 89
2018-04-23 19:30 | 70 | 70 |  |  | 43213.8125 | 91 | 87
2018-04-23 20:00 | 68 | 68 |  |  | 43213.8333 | 88 | 84
2018-04-23 20:30 | 65 | 65 |  |  | 43213.8542 | 84 | 81
2018-04-23 21:00 | 61 | 61 |  |  | 43213.875 | 77 | 76
2018-04-23 21:30 | 57 | 57 |  |  | 43213.8958 | 72 | 71
2018-04-23 22:00 | 56 | 56 |  |  | 43213.9167 | 72 | 71
2018-04-23 22:30 | 53 | 53 |  |  | 43213.9375 | 68 | 67
2018-04-23 23:00 | 51 | 51 |  |  | 43213.9583 | 66 | 63
2018-04-23 23:30 | 46 | 46 |  |  | 43213.9792 | 62 | 58
2018-04-24 | 41 | 41 |  |  | 43214 | 57 | 52
2018-04-24 00:30 | 38 | 38 |  |  | 43214.0208 | 53 | 47
2018-04-24 01:00 | 37 | 36 |  |  | 43214.0417 | 51 | 45
2018-04-24 01:30 | 35 | 34 |  |  | 43214.0625 | 49 | 42
2018-04-24 02:00 | 35 | 34 |  |  | 43214.0833 | 48 | 41
2018-04-24 02:30 | 34 | 34 |  |  | 43214.1042 | 47 | 40
2018-04-24 03:00 | 34 | 34 |  |  | 43214.125 | 47 | 41
2018-04-24 03:30 | 35 | 35 |  |  | 43214.1458 | 47 | 41
2018-04-24 04:00 | 35 | 35 |  |  | 43214.1667 | 47 | 41
2018-04-24 04:30 | 37 | 37 |  |  | 43214.1875 | 50 | 44
2018-04-24 05:00 | 39 | 39 |  |  | 43214.2083 | 52 | 47
2018-04-24 05:30 | 43 | 43 |  |  | 43214.2292 | 56 | 52
2018-04-24 06:00 | 48 | 47 |  |  | 43214.25 | 61 | 58
2018-04-24 06:30 | 52 | 52 |  |  | 43214.2708 | 69 | 67
2018-04-24 07:00 | 57 | 57 |  |  | 43214.2917 | 76 | 75
2018-04-24 07:30 | 61 | 61 |  |  | 43214.3125 | 81 | 80
2018-04-24 08:00 | 61 | 61 |  |  | 43214.3333 | 84 | 83
2018-04-24 08:30 | 61 | 60 |  |  | 43214.3542 | 83 | 83
2018-04-24 09:00 | 60 | 59 |  |  | 43214.375 | 81 | 81
2018-04-24 09:30 | 58 | 57 |  |  | 43214.3958 | 79 | 79
2018-04-24 10:00 | 56 | 55 |  |  | 43214.4167 | 77 | 77
2018-04-24 10:30 | 56 | 55 |  |  | 43214.4375 | 76 | 76
2018-04-24 11:00 | 55 | 54 |  |  | 43214.4583 | 76 | 76
2018-04-24 11:30 | 53 | 53 |  |  | 43214.4792 | 74 | 74
2018-04-24 12:00 | 54 | 53 |  |  | 43214.5 | 74 | 74
2018-04-24 12:30 | 86 | 86 |  |  | 43214.5208 | 49 | 49
2018-04-24 13:00 | 91 | 91 |  |  | 43214.5417 | 49 | 49
2018-04-24 13:30 | 91 | 91 |  |  | 43214.5625 | 46 | 46
2018-04-24 14:00 | 89 | 89 |  |  | 43214.5833 | 45 | 45
2018-04-24 14:30 | 92 | 92 |  |  | 43214.6042 | 47 | 47
2018-04-24 15:00 | 70 | 69 |  |  | 43214.625 | 73 | 73
2018-04-24 15:30 | 63 | 62 |  |  | 43214.6458 | 83 | 83
2018-04-24 16:00 | 63 | 63 |  |  | 43214.6667 | 84 | 84
2018-04-24 16:30 | 63 | 63 |  |  | 43214.6875 | 85 | 85
2018-04-24 17:00 | 66 | 66 |  |  | 43214.7083 | 89 | 88
2018-04-24 17:30 | 66 | 66 |  |  | 43214.7292 | 87 | 87
2018-04-24 18:00 | 65 | 65 |  |  | 43214.75 | 85 | 85
2018-04-24 18:30 | 62 | 62 |  |  | 43214.7708 | 82 | 81
2018-04-24 19:00 | 62 | 62 |  |  | 43214.7917 | 83 | 82
2018-04-24 19:30 | 63 | 63 |  |  | 43214.8125 | 82 | 80
2018-04-24 20:00 | 62 | 62 |  |  | 43214.8333 | 80 | 78
2018-04-24 20:30 | 60 | 60 |  |  | 43214.8542 | 78 | 76
2018-04-24 21:00 | 58 | 58 |  |  | 43214.875 | 75 | 72
2018-04-24 21:30 | 54 | 54 |  |  | 43214.8958 | 70 | 67
2018-04-24 22:00 | 52 | 51 |  |  | 43214.9167 | 68 | 65
2018-04-24 22:30 | 50 | 50 |  |  | 43214.9375 | 67 | 63
2018-04-24 23:00 | 49 | 48 |  |  | 43214.9583 | 63 | 58
2018-04-24 23:30 | 45 | 45 |  |  | 43214.9792 | 59 | 55
2018-04-25 | 38 | 38 |  |  | 43215 | 53 | 48
2018-04-25 00:30 | 35 | 34 |  |  | 43215.0208 | 49 | 44
2018-04-25 01:00 | 32 | 31 |  |  | 43215.0417 | 46 | 39
2018-04-25 01:30 | 32 | 31 |  |  | 43215.0625 | 46 | 38
2018-04-25 02:00 | 30 | 29 |  |  | 43215.0833 | 44 | 37
2018-04-25 02:30 | 30 | 29 |  |  | 43215.1042 | 43 | 37
2018-04-25 03:00 | 30 | 29 |  |  | 43215.125 | 44 | 37
2018-04-25 03:30 | 30 | 29 |  |  | 43215.1458 | 43 | 37
2018-04-25 04:00 | 28 | 27 |  |  | 43215.1667 | 43 | 36
2018-04-25 04:30 | 28 | 27 |  |  | 43215.1875 | 43 | 37
2018-04-25 05:00 | 29 | 28 |  |  | 43215.2083 | 43 | 36
2018-04-25 05:30 | 30 | 29 |  |  | 43215.2292 | 44 | 38
2018-04-25 06:00 | 30 | 30 |  |  | 43215.25 | 46 | 40
2018-04-25 06:30 | 32 | 32 |  |  | 43215.2708 | 48 | 43
2018-04-25 07:00 | 32 | 32 |  |  | 43215.2917 | 50 | 45
2018-04-25 07:30 | 32 | 32 |  |  | 43215.3125 | 51 | 47
2018-04-25 08:00 | 32 | 31 |  |  | 43215.3333 | 50 | 47
2018-04-25 08:30 | 32 | 32 |  |  | 43215.3542 | 51 | 47
2018-04-25 09:00 | 32 | 31 |  |  | 43215.375 | 49 | 47
2018-04-25 09:30 | 31 | 31 |  |  | 43215.3958 | 48 | 46
2018-04-25 10:00 | 30 | 30 |  |  | 43215.4167 | 46 | 44
2018-04-25 10:30 | 29 | 29 |  |  | 43215.4375 | 44 | 42
2018-04-25 11:00 | 30 | 30 |  |  | 43215.4583 | 47 | 45
2018-04-25 11:30 | 32 | 32 |  |  | 43215.4792 | 48 | 46
2018-04-25 12:00 | 35 | 35 |  |  | 43215.5 | 50 | 48
2018-04-25 12:30 | 35 | 35 |  |  | 43215.5208 | 52 | 50
2018-04-25 13:00 | 38 | 38 |  |  | 43215.5417 | 53 | 51
2018-04-25 13:30 | 36 | 36 |  |  | 43215.5625 | 51 | 50
2018-04-25 14:00 | 37 | 37 |  |  | 43215.5833 | 54 | 53
2018-04-25 14:30 | 40 | 39 |  |  | 43215.6042 | 59 | 57
2018-04-25 15:00 | 40 | 40 |  |  | 43215.625 | 58 | 57
2018-04-25 15:30 | 42 | 42 |  |  | 43215.6458 | 58 | 57
2018-04-25 16:00 | 46 | 46 |  |  | 43215.6667 | 64 | 63
2018-04-25 16:30 | 51 | 51 |  |  | 43215.6875 | 68 | 67
2018-04-25 17:00 | 54 | 54 |  |  | 43215.7083 | 72 | 70
2018-04-25 17:30 | 54 | 54 |  |  | 43215.7292 | 73 | 70
2018-04-25 18:00 | 56 | 56 |  |  | 43215.75 | 75 | 72
2018-04-25 18:30 | 56 | 56 |  |  | 43215.7708 | 75 | 72
2018-04-25 19:00 | 58 | 58 |  |  | 43215.7917 | 77 | 74
2018-04-25 19:30 | 58 | 57 |  |  | 43215.8125 | 76 | 73
2018-04-25 20:00 | 56 | 55 |  |  | 43215.8333 | 74 | 70
2018-04-25 20:30 | 53 | 53 |  |  | 43215.8542 | 72 | 68
2018-04-25 21:00 | 51 | 50 |  |  | 43215.875 | 67 | 63
2018-04-25 21:30 | 48 | 48 |  |  | 43215.8958 | 65 | 61
2018-04-25 22:00 | 47 | 47 |  |  | 43215.9167 | 64 | 60
2018-04-25 22:30 | 47 | 46 |  |  | 43215.9375 | 64 | 60
2018-04-25 23:00 | 45 | 45 |  |  | 43215.9583 | 61 | 56
2018-04-25 23:30 | 42 | 42 |  |  | 43215.9792 | 59 | 54
2018-04-26 | 38 | 37 |  |  | 43216 | 54 | 48
2018-04-26 00:30 | 35 | 34 |  |  | 43216.0208 | 51 | 45
2018-04-26 01:00 | 32 | 31 |  |  | 43216.0417 | 48 | 40
2018-04-26 01:30 | 30 | 29 |  |  | 43216.0625 | 46 | 38
2018-04-26 02:00 | 30 | 28 |  |  | 43216.0833 | 45 | 37
2018-04-26 02:30 | 29 | 28 |  |  | 43216.1042 | 44 | 37
2018-04-26 03:00 | 29 | 28 |  |  | 43216.125 | 44 | 38
2018-04-26 03:30 | 30 | 30 |  |  | 43216.1458 | 44 | 38
2018-04-26 04:00 | 30 | 29 |  |  | 43216.1667 | 44 | 38
2018-04-26 04:30 | 30 | 30 |  |  | 43216.1875 | 44 | 39
2018-04-26 05:00 | 35 | 34 |  |  | 43216.2083 | 49 | 43
2018-04-26 05:30 | 38 | 38 |  |  | 43216.2292 | 52 | 48
2018-04-26 06:00 | 43 | 43 |  |  | 43216.25 | 57 | 54
2018-04-26 06:30 | 50 | 50 |  |  | 43216.2708 | 67 | 66
2018-04-26 07:00 | 54 | 54 |  |  | 43216.2917 | 73 | 72
2018-04-26 07:30 | 57 | 57 |  |  | 43216.3125 | 80 | 79
2018-04-26 08:00 | 56 | 56 |  |  | 43216.3333 | 82 | 81
2018-04-26 08:30 | 50 | 50 |  |  | 43216.3542 | 74 | 74
2018-04-26 09:00 | 53 | 51 |  |  | 43216.375 | 78 | 78
2018-04-26 09:30 | 51 | 50 |  |  | 43216.3958 | 77 | 76
2018-04-26 10:00 | 61 | 60 |  |  | 43216.4167 | 94 | 93
2018-04-26 10:30 | 68 | 67 |  |  | 43216.4375 | 104 | 104
2018-04-26 11:00 | 69 | 68 |  |  | 43216.4583 | 105 | 104
2018-04-26 11:30 | 69 | 68 |  |  | 43216.4792 | 105 | 104
2018-04-26 12:00 | 68 | 68 |  |  | 43216.5 | 105 | 104
2018-04-26 12:30 | 68 | 68 |  |  | 43216.5208 | 104 | 104
2018-04-26 13:00 | 66 | 66 |  |  | 43216.5417 | 96 | 95
2018-04-26 13:30 | 61 | 61 |  |  | 43216.5625 | 87 | 85
2018-04-26 14:00 | 64 | 64 |  |  | 43216.5833 | 90 | 89
2018-04-26 14:30 | 66 | 66 |  |  | 43216.6042 | 94 | 92
2018-04-26 15:00 | 67 | 67 |  |  | 43216.625 | 95 | 93
2018-04-26 15:30 | 67 | 67 |  |  | 43216.6458 | 96 | 94
2018-04-26 16:00 | 67 | 67 |  |  | 43216.6667 | 98 | 97
2018-04-26 16:30 | 68 | 68 |  |  | 43216.6875 | 97 | 94
2018-04-26 17:00 | 70 | 70 |  |  | 43216.7083 | 98 | 95
2018-04-26 17:30 | 68 | 67 |  |  | 43216.7292 | 95 | 92
2018-04-26 18:00 | 67 | 67 |  |  | 43216.75 | 97 | 92
2018-04-26 18:30 | 66 | 66 |  |  | 43216.7708 | 94 | 90
2018-04-26 19:00 | 67 | 67 |  |  | 43216.7917 | 94 | 91
2018-04-26 19:30 | 68 | 68 |  |  | 43216.8125 | 92 | 89
2018-04-26 20:00 | 66 | 66 |  |  | 43216.8333 | 90 | 87
2018-04-26 20:30 | 65 | 64 |  |  | 43216.8542 | 88 | 85
2018-04-26 21:00 | 61 | 61 |  |  | 43216.875 | 82 | 81
2018-04-26 21:30 | 58 | 58 |  |  | 43216.8958 | 77 | 76
2018-04-26 22:00 | 54 | 54 |  |  | 43216.9167 | 76 | 75
2018-04-26 22:30 | 52 | 52 |  |  | 43216.9375 | 72 | 72
2018-04-26 23:00 | 51 | 51 |  |  | 43216.9583 | 69 | 68
2018-04-26 23:30 | 46 | 46 |  |  | 43216.9792 | 64 | 63
2018-04-27 | 42 | 42 |  |  | 43217 | 58 | 57
2018-04-27 00:30 | 40 | 40 |  |  | 43217.0208 | 54 | 53
2018-04-27 01:00 | 38 | 38 |  |  | 43217.0417 | 51 | 49
2018-04-27 01:30 | 36 | 36 |  |  | 43217.0625 | 50 | 47
2018-04-27 02:00 | 35 | 35 |  |  | 43217.0833 | 48 | 45
2018-04-27 02:30 | 36 | 36 |  |  | 43217.1042 | 48 | 45
2018-04-27 03:00 | 35 | 35 |  |  | 43217.125 | 48 | 45
2018-04-27 03:30 | 34 | 34 |  |  | 43217.1458 | 47 | 44
2018-04-27 04:00 | 34 | 34 |  |  | 43217.1667 | 46 | 43
2018-04-27 04:30 | 36 | 36 |  |  | 43217.1875 | 49 | 46
2018-04-27 05:00 | 39 | 39 |  |  | 43217.2083 | 52 | 49
2018-04-27 05:30 | 42 | 42 |  |  | 43217.2292 | 55 | 53
2018-04-27 06:00 | 45 | 45 |  |  | 43217.25 | 59 | 58
2018-04-27 06:30 | 52 | 52 |  |  | 43217.2708 | 69 | 69
2018-04-27 07:00 | 56 | 56 |  |  | 43217.2917 | 77 | 76
2018-04-27 07:30 | 59 | 59 |  |  | 43217.3125 | 82 | 81
2018-04-27 08:00 | 58 | 58 |  |  | 43217.3333 | 82 | 82
2018-04-27 08:30 | 57 | 57 |  |  | 43217.3542 | 82 | 82
2018-04-27 09:00 | 55 | 55 |  |  | 43217.375 | 80 | 80
2018-04-27 09:30 | 54 | 53 |  |  | 43217.3958 | 78 | 78
2018-04-27 10:00 | 52 | 52 |  |  | 43217.4167 | 76 | 76
2018-04-27 10:30 | 52 | 52 |  |  | 43217.4375 | 76 | 76
2018-04-27 11:00 | 53 | 52 |  |  | 43217.4583 | 78 | 77
2018-04-27 11:30 | 52 | 51 |  |  | 43217.4792 | 78 | 77
2018-04-27 12:00 | 53 | 52 |  |  | 43217.5 | 77 | 77
2018-04-27 12:30 | 53 | 53 |  |  | 43217.5208 | 78 | 78
2018-04-27 13:00 | 54 | 54 |  |  | 43217.5417 | 79 | 79
2018-04-27 13:30 | 55 | 55 |  |  | 43217.5625 | 80 | 79
2018-04-27 14:00 | 59 | 58 |  |  | 43217.5833 | 83 | 83
2018-04-27 14:30 | 62 | 61 |  |  | 43217.6042 | 85 | 85
2018-04-27 15:00 | 63 | 62 |  |  | 43217.625 | 86 | 86
2018-04-27 15:30 | 64 | 64 |  |  | 43217.6458 | 88 | 88
2018-04-27 16:00 | 66 | 65 |  |  | 43217.6667 | 90 | 89
2018-04-27 16:30 | 65 | 65 |  |  | 43217.6875 | 88 | 87
2018-04-27 17:00 | 67 | 66 |  |  | 43217.7083 | 89 | 88
2018-04-27 17:30 | 66 | 66 |  |  | 43217.7292 | 89 | 87
2018-04-27 18:00 | 64 | 64 |  |  | 43217.75 | 87 | 85
2018-04-27 18:30 | 62 | 62 |  |  | 43217.7708 | 84 | 81
2018-04-27 19:00 | 64 | 64 |  |  | 43217.7917 | 85 | 82
2018-04-27 19:30 | 63 | 63 |  |  | 43217.8125 | 81 | 80
2018-04-27 20:00 | 61 | 61 |  |  | 43217.8333 | 80 | 79
2018-04-27 20:30 | 60 | 59 |  |  | 43217.8542 | 78 | 77
2018-04-27 21:00 | 57 | 57 |  |  | 43217.875 | 74 | 73
2018-04-27 21:30 | 55 | 55 |  |  | 43217.8958 | 72 | 70
2018-04-27 22:00 | 52 | 52 |  |  | 43217.9167 | 71 | 69
2018-04-27 22:30 | 51 | 51 |  |  | 43217.9375 | 68 | 66
2018-04-27 23:00 | 51 | 51 |  |  | 43217.9583 | 67 | 64
2018-04-27 23:30 | 48 | 48 |  |  | 43217.9792 | 63 | 60
2018-04-28 | 43 | 43 |  |  | 43218 | 58 | 55
2018-04-28 00:30 | 38 | 38 |  |  | 43218.0208 | 51 | 49
2018-04-28 01:00 | 34 | 34 |  |  | 43218.0417 | 48 | 45
2018-04-28 01:30 | 36 | 36 |  |  | 43218.0625 | 48 | 45
2018-04-28 02:00 | 35 | 35 |  |  | 43218.0833 | 46 | 44
2018-04-28 02:30 | 35 | 35 |  |  | 43218.1042 | 47 | 43
2018-04-28 03:00 | 36 | 35 |  |  | 43218.125 | 46 | 43
2018-04-28 03:30 | 35 | 35 |  |  | 43218.1458 | 47 | 44
2018-04-28 04:00 | 35 | 35 |  |  | 43218.1667 | 47 | 44
2018-04-28 04:30 | 36 | 35 |  |  | 43218.1875 | 48 | 45
2018-04-28 05:00 | 37 | 37 |  |  | 43218.2083 | 49 | 46
2018-04-28 05:30 | 37 | 37 |  |  | 43218.2292 | 50 | 47
2018-04-28 06:00 | 37 | 37 |  |  | 43218.25 | 50 | 47
2018-04-28 06:30 | 38 | 38 |  |  | 43218.2708 | 52 | 50
2018-04-28 07:00 | 40 | 40 |  |  | 43218.2917 | 54 | 52
2018-04-28 07:30 | 39 | 39 |  |  | 43218.3125 | 54 | 52
2018-04-28 08:00 | 36 | 36 |  |  | 43218.3333 | 53 | 52
2018-04-28 08:30 | 36 | 36 |  |  | 43218.3542 | 54 | 53
2018-04-28 09:00 | 35 | 35 |  |  | 43218.375 | 54 | 53
2018-04-28 09:30 | 33 | 33 |  |  | 43218.3958 | 53 | 53
2018-04-28 10:00 | 31 | 31 |  |  | 43218.4167 | 54 | 53
2018-04-28 10:30 | 37 | 37 |  |  | 43218.4375 | 61 | 61
2018-04-28 11:00 | 37 | 37 |  |  | 43218.4583 | 60 | 60
2018-04-28 11:30 | 31 | 31 |  |  | 43218.4792 | 53 | 52
2018-04-28 12:00 | 30 | 30 |  |  | 43218.5 | 51 | 51
2018-04-28 12:30 | 32 | 32 |  |  | 43218.5208 | 50 | 50
2018-04-28 13:00 | 34 | 34 |  |  | 43218.5417 | 55 | 55
2018-04-28 13:30 | 34 | 34 |  |  | 43218.5625 | 56 | 55
2018-04-28 14:00 | 41 | 41 |  |  | 43218.5833 | 59 | 59
2018-04-28 14:30 | 50 | 50 |  |  | 43218.6042 | 66 | 66
2018-04-28 15:00 | 49 | 49 |  |  | 43218.625 | 69 | 69
2018-04-28 15:30 | 51 | 50 |  |  | 43218.6458 | 69 | 69
2018-04-28 16:00 | 54 | 54 |  |  | 43218.6667 | 69 | 68
2018-04-28 16:30 | 54 | 54 |  |  | 43218.6875 | 69 | 69
2018-04-28 17:00 | 55 | 55 |  |  | 43218.7083 | 71 | 71
2018-04-28 17:30 | 55 | 55 |  |  | 43218.7292 | 73 | 72
2018-04-28 18:00 | 57 | 57 |  |  | 43218.75 | 75 | 74
2018-04-28 18:30 | 58 | 58 |  |  | 43218.7708 | 76 | 75
2018-04-28 19:00 | 59 | 59 |  |  | 43218.7917 | 77 | 76
2018-04-28 19:30 | 58 | 58 |  |  | 43218.8125 | 76 | 75
2018-04-28 20:00 | 57 | 57 |  |  | 43218.8333 | 74 | 73
2018-04-28 20:30 | 55 | 55 |  |  | 43218.8542 | 73 | 72
2018-04-28 21:00 | 52 | 52 |  |  | 43218.875 | 69 | 68
2018-04-28 21:30 | 51 | 51 |  |  | 43218.8958 | 67 | 66
2018-04-28 22:00 | 50 | 50 |  |  | 43218.9167 | 67 | 66
2018-04-28 22:30 | 51 | 51 |  |  | 43218.9375 | 68 | 67
2018-04-28 23:00 | 50 | 50 |  |  | 43218.9583 | 66 | 65
2018-04-28 23:30 | 48 | 48 |  |  | 43218.9792 | 63 | 62
2018-04-29 | 44 | 44 |  |  | 43219 | 58 | 56
2018-04-29 00:30 | 40 | 40 |  |  | 43219.0208 | 54 | 52
2018-04-29 01:00 | 37 | 37 |  |  | 43219.0417 | 51 | 48
2018-04-29 01:30 | 35 | 35 |  |  | 43219.0625 | 49 | 46
2018-04-29 02:00 | 34 | 34 |  |  | 43219.0833 | 47 | 44
2018-04-29 02:30 | 33 | 33 |  |  | 43219.1042 | 45 | 42
2018-04-29 03:00 | 34 | 33 |  |  | 43219.125 | 44 | 42
2018-04-29 03:30 | 34 | 33 |  |  | 43219.1458 | 44 | 42
2018-04-29 04:00 | 33 | 33 |  |  | 43219.1667 | 45 | 43
2018-04-29 04:30 | 34 | 32 |  |  | 43219.1875 | 47 | 44
2018-04-29 05:00 | 37 | 32 |  |  | 43219.2083 | 48 | 44
2018-04-29 05:30 | 38 | 33 |  |  | 43219.2292 | 48 | 43
2018-04-29 06:00 | 39 | 34 |  |  | 43219.25 | 49 | 45
2018-04-29 06:30 | 39 | 35 |  |  | 43219.2708 | 51 | 47
2018-04-29 07:00 | 41 | 37 |  |  | 43219.2917 | 52 | 48
2018-04-29 07:30 | 40 | 35 |  |  | 43219.3125 | 52 | 48
2018-04-29 08:00 | 38 | 34 |  |  | 43219.3333 | 52 | 48
2018-04-29 08:30 | 35 | 32 |  |  | 43219.3542 | 49 | 47
2018-04-29 09:00 | 35 | 32 |  |  | 43219.375 | 49 | 46
2018-04-29 09:30 | 34 | 32 |  |  | 43219.3958 | 48 | 46
2018-04-29 10:00 | 34 | 32 |  |  | 43219.4167 | 46 | 44
2018-04-29 10:30 | 33 | 31 |  |  | 43219.4375 | 46 | 44
2018-04-29 11:00 | 33 | 32 |  |  | 43219.4583 | 47 | 45
2018-04-29 11:30 | 39 | 37 |  |  | 43219.4792 | 51 | 49
2018-04-29 12:00 | 40 | 39 |  |  | 43219.5 | 54 | 53
2018-04-29 12:30 | 39 | 38 |  |  | 43219.5208 | 54 | 52
2018-04-29 13:00 | 35 | 34 |  |  | 43219.5417 | 48 | 47
2018-04-29 13:30 | 34 | 33 |  |  | 43219.5625 | 47 | 46
2018-04-29 14:00 | 37 | 35 |  |  | 43219.5833 | 48 | 47
2018-04-29 14:30 | 41 | 39 |  |  | 43219.6042 | 54 | 53
2018-04-29 15:00 | 44 | 42 |  |  | 43219.625 | 57 | 56
2018-04-29 15:30 | 45 | 44 |  |  | 43219.6458 | 60 | 59
2018-04-29 16:00 | 48 | 46 |  |  | 43219.6667 | 62 | 61
2018-04-29 16:30 | 51 | 50 |  |  | 43219.6875 | 66 | 65
2018-04-29 17:00 | 54 | 52 |  |  | 43219.7083 | 70 | 68
2018-04-29 17:30 | 57 | 55 |  |  | 43219.7292 | 73 | 70
2018-04-29 18:00 | 60 | 58 |  |  | 43219.75 | 77 | 74
2018-04-29 18:30 | 61 | 59 |  |  | 43219.7708 | 79 | 76
2018-04-29 19:00 | 61 | 59 |  |  | 43219.7917 | 79 | 76
2018-04-29 19:30 | 61 | 59 |  |  | 43219.8125 | 78 | 76
2018-04-29 20:00 | 60 | 58 |  |  | 43219.8333 | 76 | 73
2018-04-29 20:30 | 58 | 56 |  |  | 43219.8542 | 75 | 72
2018-04-29 21:00 | 57 | 54 |  |  | 43219.875 | 73 | 70
2018-04-29 21:30 | 55 | 52 |  |  | 43219.8958 | 71 | 68
2018-04-29 22:00 | 57 | 54 |  |  | 43219.9167 | 73 | 70
2018-04-29 22:30 | 60 | 56 |  |  | 43219.9375 | 77 | 73
2018-04-29 23:00 | 61 | 57 |  |  | 43219.9583 | 75 | 70
2018-04-29 23:30 | 55 | 51 |  |  | 43219.9792 | 69 | 64
2018-04-30 | 49 | 45 |  |  | 43220 | 63 | 57
2018-04-30 00:30 | 46 | 40 |  |  | 43220.0208 | 59 | 52
2018-04-30 01:00 | 43 | 37 |  |  | 43220.0417 | 54 | 48
2018-04-30 01:30 | 42 | 36 |  |  | 43220.0625 | 53 | 48
2018-04-30 02:00 | 41 | 35 |  |  | 43220.0833 | 51 | 46
2018-04-30 02:30 | 41 | 35 |  |  | 43220.1042 | 51 | 45
2018-04-30 03:00 | 41 | 35 |  |  | 43220.125 | 51 | 46
2018-04-30 03:30 | 41 | 36 |  |  | 43220.1458 | 51 | 46
2018-04-30 04:00 | 41 | 36 |  |  | 43220.1667 | 52 | 46
2018-04-30 04:30 | 42 | 38 |  |  | 43220.1875 | 52 | 47
2018-04-30 05:00 | 43 | 39 |  |  | 43220.2083 | 54 | 49
2018-04-30 05:30 | 46 | 43 |  |  | 43220.2292 | 57 | 53
2018-04-30 06:00 | 49 | 48 |  |  | 43220.25 | 63 | 61
2018-04-30 06:30 | 55 | 54 |  |  | 43220.2708 | 73 | 72
2018-04-30 07:00 | 60 | 59 |  |  | 43220.2917 | 80 | 79
2018-04-30 07:30 | 64 | 64 |  |  | 43220.3125 | 85 | 84
2018-04-30 08:00 | 63 | 63 |  |  | 43220.3333 | 84 | 83
2018-04-30 08:30 | 60 | 59 |  |  | 43220.3542 | 83 | 81
2018-04-30 09:00 | 57 | 56 |  |  | 43220.375 | 79 | 78
2018-04-30 09:30 | 55 | 54 |  |  | 43220.3958 | 76 | 75
2018-04-30 10:00 | 55 | 55 |  |  | 43220.4167 | 76 | 75
2018-04-30 10:30 | 57 | 57 |  |  | 43220.4375 | 78 | 76
2018-04-30 11:00 | 57 | 57 |  |  | 43220.4583 | 78 | 77
2018-04-30 11:30 | 57 | 57 |  |  | 43220.4792 | 78 | 77
2018-04-30 12:00 | 61 | 60 |  |  | 43220.5 | 83 | 82
2018-04-30 12:30 | 60 | 60 |  |  | 43220.5208 | 82 | 81
2018-04-30 13:00 | 62 | 61 |  |  | 43220.5417 | 83 | 82
2018-04-30 13:30 | 65 | 62 |  |  | 43220.5625 | 86 | 86
2018-04-30 14:00 | 66 | 64 |  |  | 43220.5833 | 86 | 86
2018-04-30 14:30 | 68 | 66 |  |  | 43220.6042 | 89 | 89
2018-04-30 15:00 | 71 | 68 |  |  | 43220.625 | 92 | 92
2018-04-30 15:30 | 70 | 67 |  |  | 43220.6458 | 89 | 89
2018-04-30 16:00 | 72 | 69 |  |  | 43220.6667 | 90 | 90
2018-04-30 16:30 | 73 | 70 |  |  | 43220.6875 | 92 | 91
2018-04-30 17:00 | 76 | 73 |  |  | 43220.7083 | 94 | 94
2018-04-30 17:30 | 78 | 75 |  |  | 43220.7292 | 95 | 94
2018-04-30 18:00 | 78 | 74 |  |  | 43220.75 | 96 | 95
2018-04-30 18:30 | 78 | 74 |  |  | 43220.7708 | 94 | 93
2018-04-30 19:00 | 77 | 73 |  |  | 43220.7917 | 93 | 92
2018-04-30 19:30 | 75 | 71 |  |  | 43220.8125 | 90 | 89
2018-04-30 20:00 | 73 | 69 |  |  | 43220.8333 | 88 | 86
2018-04-30 20:30 | 70 | 66 |  |  | 43220.8542 | 84 | 83
2018-04-30 21:00 | 69 | 64 |  |  | 43220.875 | 82 | 81
2018-04-30 21:30 | 66 | 61 |  |  | 43220.8958 | 78 | 77
2018-04-30 22:00 | 64 | 58 |  |  | 43220.9167 | 76 | 75
2018-04-30 22:30 | 61 | 55 |  |  | 43220.9375 | 74 | 72
2018-04-30 23:00 | 62 | 55 |  |  | 43220.9583 | 72 | 69
2018-04-30 23:30 | 58 | 50 |  |  | 43220.9792 | 67 | 64
2018-05-01 | 56 | 46 |  |  | 43221 | 62 | 58
2018-05-01 00:30 | 54 | 41 |  |  | 43221.0208 | 56 | 52
2018-05-01 01:00 | 52 | 38 |  |  | 43221.0417 | 53 | 49
2018-05-01 01:30 | 52 | 37 |  |  | 43221.0625 | 52 | 46
2018-05-01 02:00 | 50 | 35 |  |  | 43221.0833 | 51 | 45
2018-05-01 02:30 | 50 | 35 |  |  | 43221.1042 | 50 | 44
2018-05-01 03:00 | 50 | 34 |  |  | 43221.125 | 50 | 44
2018-05-01 03:30 | 50 | 35 |  |  | 43221.1458 | 50 | 45
2018-05-01 04:00 | 51 | 36 |  |  | 43221.1667 | 52 | 46
2018-05-01 04:30 | 52 | 38 |  |  | 43221.1875 | 53 | 48
2018-05-01 05:00 | 54 | 41 |  |  | 43221.2083 | 55 | 50
2018-05-01 05:30 | 55 | 43 |  |  | 43221.2292 | 59 | 55
2018-05-01 06:00 | 56 | 48 |  |  | 43221.25 | 64 | 61
2018-05-01 06:30 | 61 | 54 |  |  | 43221.2708 | 72 | 70
2018-05-01 07:00 | 64 | 59 |  |  | 43221.2917 | 79 | 78
2018-05-01 07:30 | 66 | 62 |  |  | 43221.3125 | 84 | 83
2018-05-01 08:00 | 64 | 60 |  |  | 43221.3333 | 84 | 83
2018-05-01 08:30 | 63 | 58 |  |  | 43221.3542 | 83 | 82
2018-05-01 09:00 | 63 | 59 |  |  | 43221.375 | 85 | 84
2018-05-01 09:30 | 63 | 59 |  |  | 43221.3958 | 83 | 82
2018-05-01 10:00 | 62 | 58 |  |  | 43221.4167 | 81 | 80
2018-05-01 10:30 | 58 | 54 |  |  | 43221.4375 | 78 | 77
2018-05-01 11:00 | 62 | 59 |  |  | 43221.4583 | 81 | 81
2018-05-01 11:30 | 68 | 65 |  |  | 43221.4792 | 86 | 86
2018-05-01 12:00 | 68 | 65 |  |  | 43221.5 | 86 | 85
2018-05-01 12:30 | 61 | 58 |  |  | 43221.5208 | 81 | 81
2018-05-01 13:00 | 58 | 53 |  |  | 43221.5417 | 80 | 80
2018-05-01 13:30 | 59 | 54 |  |  | 43221.5625 | 79 | 78
2018-05-01 14:00 | 63 | 59 |  |  | 43221.5833 | 84 | 83
2018-05-01 14:30 | 69 | 65 |  |  | 43221.6042 | 88 | 87
2018-05-01 15:00 | 70 | 65 |  |  | 43221.625 | 89 | 87
2018-05-01 15:30 | 70 | 66 |  |  | 43221.6458 | 92 | 91
2018-05-01 16:00 | 73 | 69 |  |  | 43221.6667 | 96 | 94
2018-05-01 16:30 | 75 | 71 |  |  | 43221.6875 | 96 | 95
2018-05-01 17:00 | 80 | 75 |  |  | 43221.7083 | 100 | 98
2018-05-01 17:30 | 80 | 76 |  |  | 43221.7292 | 101 | 99
2018-05-01 18:00 | 81 | 76 |  |  | 43221.75 | 101 | 100
2018-05-01 18:30 | 79 | 74 |  |  | 43221.7708 | 99 | 96
2018-05-01 19:00 | 80 | 74 |  |  | 43221.7917 | 100 | 97
2018-05-01 19:30 | 79 | 74 |  |  | 43221.8125 | 97 | 95
2018-05-01 20:00 | 77 | 73 |  |  | 43221.8333 | 94 | 93
2018-05-01 20:30 | 76 | 72 |  |  | 43221.8542 | 93 | 92
2018-05-01 21:00 | 72 | 68 |  |  | 43221.875 | 88 | 87
2018-05-01 21:30 | 68 | 63 |  |  | 43221.8958 | 83 | 82
2018-05-01 22:00 | 69 | 63 |  |  | 43221.9167 | 85 | 83
2018-05-01 22:30 | 66 | 60 |  |  | 43221.9375 | 82 | 80
2018-05-01 23:00 | 65 | 57 |  |  | 43221.9583 | 77 | 74
2018-05-01 23:30 | 61 | 52 |  |  | 43221.9792 | 72 | 69
2018-05-02 | 57 | 46 |  |  | 43222 | 66 | 63
2018-05-02 00:30 | 54 | 42 |  |  | 43222.0208 | 61 | 57
2018-05-02 01:00 | 54 | 41 |  |  | 43222.0417 | 59 | 54
2018-05-02 01:30 | 54 | 41 |  |  | 43222.0625 | 58 | 53
2018-05-02 02:00 | 55 | 41 |  |  | 43222.0833 | 59 | 53
2018-05-02 02:30 | 54 | 39 |  |  | 43222.1042 | 59 | 53
2018-05-02 03:00 | 53 | 39 |  |  | 43222.125 | 58 | 52
2018-05-02 03:30 | 53 | 39 |  |  | 43222.1458 | 58 | 52
2018-05-02 04:00 | 53 | 39 |  |  | 43222.1667 | 57 | 51
2018-05-02 04:30 | 54 | 40 |  |  | 43222.1875 | 59 | 54
2018-05-02 05:00 | 56 | 43 |  |  | 43222.2083 | 61 | 56
2018-05-02 05:30 | 60 | 49 |  |  | 43222.2292 | 66 | 62
2018-05-02 06:00 | 62 | 54 |  |  | 43222.25 | 71 | 69
2018-05-02 06:30 | 65 | 58 |  |  | 43222.2708 | 80 | 79
2018-05-02 07:00 | 67 | 62 |  |  | 43222.2917 | 87 | 86
2018-05-02 07:30 | 69 | 66 |  |  | 43222.3125 | 93 | 93
2018-05-02 08:00 | 73 | 71 |  |  | 43222.3333 | 97 | 97
2018-05-02 08:30 | 72 | 70 |  |  | 43222.3542 | 95 | 95
2018-05-02 09:00 | 67 | 64 |  |  | 43222.375 | 91 | 91
2018-05-02 09:30 | 63 | 61 |  |  | 43222.3958 | 89 | 89
2018-05-02 10:00 | 64 | 63 |  |  | 43222.4167 | 87 | 87
2018-05-02 10:30 | 70 | 68 |  |  | 43222.4375 | 94 | 94
2018-05-02 11:00 | 68 | 65 |  |  | 43222.4583 | 93 | 93
2018-05-02 11:30 | 71 | 68 |  |  | 43222.4792 | 94 | 94
2018-05-02 12:00 | 73 | 71 |  |  | 43222.5 | 98 | 98
2018-05-02 12:30 | 69 | 67 |  |  | 43222.5208 | 95 | 94
2018-05-02 13:00 | 71 | 69 |  |  | 43222.5417 | 94 | 94
2018-05-02 13:30 | 70 | 67 |  |  | 43222.5625 | 93 | 93
2018-05-02 14:00 | 70 | 68 |  |  | 43222.5833 | 93 | 92
2018-05-02 14:30 | 71 | 68 |  |  | 43222.6042 | 94 | 93
2018-05-02 15:00 | 74 | 71 |  |  | 43222.625 | 96 | 96
2018-05-02 15:30 | 73 | 71 |  |  | 43222.6458 | 96 | 96
2018-05-02 16:00 | 75 | 73 |  |  | 43222.6667 | 97 | 97
2018-05-02 16:30 | 76 | 73 |  |  | 43222.6875 | 99 | 98
2018-05-02 17:00 | 78 | 75 |  |  | 43222.7083 | 101 | 100
2018-05-02 17:30 | 79 | 75 |  |  | 43222.7292 | 101 | 100
2018-05-02 18:00 | 78 | 74 |  |  | 43222.75 | 102 | 100
2018-05-02 18:30 | 79 | 74 |  |  | 43222.7708 | 99 | 97
2018-05-02 19:00 | 79 | 75 |  |  | 43222.7917 | 98 | 97
2018-05-02 19:30 | 78 | 74 |  |  | 43222.8125 | 97 | 95
2018-05-02 20:00 | 77 | 73 |  |  | 43222.8333 | 95 | 94
2018-05-02 20:30 | 75 | 72 |  |  | 43222.8542 | 94 | 93
2018-05-02 21:00 | 74 | 70 |  |  | 43222.875 | 91 | 90
2018-05-02 21:30 | 71 | 68 |  |  | 43222.8958 | 88 | 87
2018-05-02 22:00 | 69 | 65 |  |  | 43222.9167 | 86 | 85
2018-05-02 22:30 | 67 | 63 |  |  | 43222.9375 | 84 | 82
2018-05-02 23:00 | 65 | 60 |  |  | 43222.9583 | 80 | 77
2018-05-02 23:30 | 62 | 56 |  |  | 43222.9792 | 75 | 72
2018-05-03 | 62 | 53 |  |  | 43223 | 72 | 70
2018-05-03 00:30 | 60 | 51 |  |  | 43223.0208 | 69 | 66
2018-05-03 01:00 | 58 | 47 |  |  | 43223.0417 | 65 | 61
2018-05-03 01:30 | 56 | 45 |  |  | 43223.0625 | 64 | 59
2018-05-03 02:00 | 56 | 44 |  |  | 43223.0833 | 63 | 58
2018-05-03 02:30 | 56 | 44 |  |  | 43223.1042 | 63 | 58
2018-05-03 03:00 | 56 | 43 |  |  | 43223.125 | 62 | 57
2018-05-03 03:30 | 56 | 43 |  |  | 43223.1458 | 61 | 56
2018-05-03 04:00 | 56 | 43 |  |  | 43223.1667 | 61 | 56
2018-05-03 04:30 | 57 | 44 |  |  | 43223.1875 | 61 | 56
2018-05-03 05:00 | 57 | 45 |  |  | 43223.2083 | 64 | 59
2018-05-03 05:30 | 59 | 50 |  |  | 43223.2292 | 68 | 64
2018-05-03 06:00 | 61 | 53 |  |  | 43223.25 | 73 | 71
2018-05-03 06:30 | 66 | 60 |  |  | 43223.2708 | 82 | 81
2018-05-03 07:00 | 69 | 64 |  |  | 43223.2917 | 88 | 87
2018-05-03 07:30 | 71 | 66 |  |  | 43223.3125 | 92 | 91
2018-05-03 08:00 | 71 | 66 |  |  | 43223.3333 | 92 | 91
2018-05-03 08:30 | 70 | 65 |  |  | 43223.3542 | 91 | 90
2018-05-03 09:00 | 69 | 65 |  |  | 43223.375 | 90 | 90
2018-05-03 09:30 | 69 | 65 |  |  | 43223.3958 | 91 | 91
2018-05-03 10:00 | 68 | 65 |  |  | 43223.4167 | 92 | 92
2018-05-03 10:30 | 68 | 65 |  |  | 43223.4375 | 92 | 92
2018-05-03 11:00 | 70 | 67 |  |  | 43223.4583 | 91 | 91
2018-05-03 11:30 | 69 | 66 |  |  | 43223.4792 | 92 | 92
2018-05-03 12:00 | 67 | 65 |  |  | 43223.5 | 92 | 91
2018-05-03 12:30 | 68 | 65 |  |  | 43223.5208 | 92 | 92
2018-05-03 13:00 | 68 | 66 |  |  | 43223.5417 | 91 | 91
2018-05-03 13:30 | 69 | 67 |  |  | 43223.5625 | 92 | 92
2018-05-03 14:00 | 70 | 68 |  |  | 43223.5833 | 92 | 92
2018-05-03 14:30 | 71 | 68 |  |  | 43223.6042 | 94 | 93
2018-05-03 15:00 | 72 | 69 |  |  | 43223.625 | 96 | 96
2018-05-03 15:30 | 71 | 67 |  |  | 43223.6458 | 94 | 93
2018-05-03 16:00 | 72 | 67 |  |  | 43223.6667 | 96 | 95
2018-05-03 16:30 | 74 | 70 |  |  | 43223.6875 | 98 | 97
2018-05-03 17:00 | 77 | 73 |  |  | 43223.7083 | 102 | 100
2018-05-03 17:30 | 78 | 74 |  |  | 43223.7292 | 102 | 100
2018-05-03 18:00 | 78 | 74 |  |  | 43223.75 | 101 | 99
2018-05-03 18:30 | 78 | 74 |  |  | 43223.7708 | 99 | 97
2018-05-03 19:00 | 79 | 74 |  |  | 43223.7917 | 100 | 97
2018-05-03 19:30 | 78 | 73 |  |  | 43223.8125 | 98 | 95
2018-05-03 20:00 | 77 | 71 |  |  | 43223.8333 | 96 | 93
2018-05-03 20:30 | 75 | 70 |  |  | 43223.8542 | 94 | 91
2018-05-03 21:00 | 72 | 69 |  |  | 43223.875 | 90 | 90
2018-05-03 21:30 | 69 | 65 |  |  | 43223.8958 | 86 | 86
2018-05-03 22:00 | 68 | 65 |  |  | 43223.9167 | 85 | 85
2018-05-03 22:30 | 69 | 63 |  |  | 43223.9375 | 84 | 83
2018-05-03 23:00 | 68 | 62 |  |  | 43223.9583 | 81 | 80
2018-05-03 23:30 | 64 | 57 |  |  | 43223.9792 | 75 | 74
2018-05-04 | 59 | 52 |  |  | 43224 | 71 | 70
2018-05-04 00:30 | 57 | 49 |  |  | 43224.0208 | 66 | 65
2018-05-04 01:00 | 54 | 45 |  |  | 43224.0417 | 61 | 59
2018-05-04 01:30 | 54 | 43 |  |  | 43224.0625 | 60 | 57
2018-05-04 02:00 | 53 | 43 |  |  | 43224.0833 | 60 | 57
2018-05-04 02:30 | 54 | 43 |  |  | 43224.1042 | 59 | 57
2018-05-04 03:00 | 53 | 42 |  |  | 43224.125 | 58 | 56
2018-05-04 03:30 | 53 | 43 |  |  | 43224.1458 | 58 | 56
2018-05-04 04:00 | 54 | 45 |  |  | 43224.1667 | 59 | 57
2018-05-04 04:30 | 56 | 46 |  |  | 43224.1875 | 61 | 59
2018-05-04 05:00 | 58 | 50 |  |  | 43224.2083 | 65 | 63
2018-05-04 05:30 | 60 | 53 |  |  | 43224.2292 | 70 | 68
2018-05-04 06:00 | 63 | 57 |  |  | 43224.25 | 75 | 74
2018-05-04 06:30 | 67 | 62 |  |  | 43224.2708 | 83 | 82
2018-05-04 07:00 | 69 | 65 |  |  | 43224.2917 | 89 | 89
2018-05-04 07:30 | 72 | 68 |  |  | 43224.3125 | 95 | 95
2018-05-04 08:00 | 73 | 69 |  |  | 43224.3333 | 99 | 99
2018-05-04 08:30 | 74 | 70 |  |  | 43224.3542 | 102 | 102
2018-05-04 09:00 | 73 | 69 |  |  | 43224.375 | 100 | 100
2018-05-04 09:30 | 69 | 65 |  |  | 43224.3958 | 95 | 95
2018-05-04 10:00 | 64 | 60 |  |  | 43224.4167 | 88 | 88
2018-05-04 10:30 | 64 | 60 |  |  | 43224.4375 | 88 | 88
2018-05-04 11:00 | 64 | 61 |  |  | 43224.4583 | 87 | 87
2018-05-04 11:30 | 64 | 61 |  |  | 43224.4792 | 89 | 88
2018-05-04 12:00 | 65 | 62 |  |  | 43224.5 | 90 | 90
2018-05-04 12:30 | 65 | 62 |  |  | 43224.5208 | 89 | 89
2018-05-04 13:00 | 67 | 64 |  |  | 43224.5417 | 93 | 93
2018-05-04 13:30 | 69 | 65 |  |  | 43224.5625 | 96 | 96
2018-05-04 14:00 | 73 | 69 |  |  | 43224.5833 | 97 | 96
2018-05-04 14:30 | 73 | 68 |  |  | 43224.6042 | 97 | 96
2018-05-04 15:00 | 76 | 71 |  |  | 43224.625 | 99 | 98
2018-05-04 15:30 | 78 | 74 |  |  | 43224.6458 | 102 | 101
2018-05-04 16:00 | 80 | 75 |  |  | 43224.6667 | 102 | 101
2018-05-04 16:30 | 82 | 77 |  |  | 43224.6875 | 103 | 102
2018-05-04 17:00 | 82 | 77 |  |  | 43224.7083 | 105 | 104
2018-05-04 17:30 | 82 | 77 |  |  | 43224.7292 | 103 | 101
2018-05-04 18:00 | 81 | 75 |  |  | 43224.75 | 101 | 99
2018-05-04 18:30 | 79 | 72 |  |  | 43224.7708 | 97 | 94
2018-05-04 19:00 | 79 | 73 |  |  | 43224.7917 | 98 | 95
2018-05-04 19:30 | 77 | 70 |  |  | 43224.8125 | 94 | 91
2018-05-04 20:00 | 74 | 68 |  |  | 43224.8333 | 91 | 89
2018-05-04 20:30 | 75 | 68 |  |  | 43224.8542 | 90 | 88
2018-05-04 21:00 | 71 | 64 |  |  | 43224.875 | 86 | 83
2018-05-04 21:30 | 68 | 60 |  |  | 43224.8958 | 83 | 80
2018-05-04 22:00 | 68 | 59 |  |  | 43224.9167 | 81 | 78
2018-05-04 22:30 | 66 | 58 |  |  | 43224.9375 | 79 | 77
2018-05-04 23:00 | 66 | 57 |  |  | 43224.9583 | 76 | 74
2018-05-04 23:30 | 63 | 54 |  |  | 43224.9792 | 72 | 69
2018-05-05 | 60 | 50 |  |  | 43225 | 69 | 66
2018-05-05 00:30 | 57 | 46 |  |  | 43225.0208 | 65 | 61
2018-05-05 01:00 | 56 | 45 |  |  | 43225.0417 | 62 | 58
2018-05-05 01:30 | 55 | 43 |  |  | 43225.0625 | 60 | 56
2018-05-05 02:00 | 52 | 40 |  |  | 43225.0833 | 58 | 53
2018-05-05 02:30 | 53 | 39 |  |  | 43225.1042 | 57 | 52
2018-05-05 03:00 | 52 | 40 |  |  | 43225.125 | 56 | 53
2018-05-05 03:30 | 51 | 39 |  |  | 43225.1458 | 56 | 53
2018-05-05 04:00 | 51 | 39 |  |  | 43225.1667 | 56 | 53
2018-05-05 04:30 | 51 | 39 |  |  | 43225.1875 | 56 | 53
2018-05-05 05:00 | 51 | 39 |  |  | 43225.2083 | 56 | 53
2018-05-05 05:30 | 52 | 42 |  |  | 43225.2292 | 57 | 54
2018-05-05 06:00 | 52 | 43 |  |  | 43225.25 | 59 | 56
2018-05-05 06:30 | 53 | 43 |  |  | 43225.2708 | 61 | 59
2018-05-05 07:00 | 54 | 45 |  |  | 43225.2917 | 62 | 60
2018-05-05 07:30 | 54 | 45 |  |  | 43225.3125 | 64 | 63
2018-05-05 08:00 | 52 | 45 |  |  | 43225.3333 | 64 | 63
2018-05-05 08:30 | 53 | 46 |  |  | 43225.3542 | 66 | 65
2018-05-05 09:00 | 53 | 47 |  |  | 43225.375 | 67 | 66
2018-05-05 09:30 | 52 | 47 |  |  | 43225.3958 | 66 | 66
2018-05-05 10:00 | 53 | 47 |  |  | 43225.4167 | 67 | 66
2018-05-05 10:30 | 52 | 46 |  |  | 43225.4375 | 65 | 65
2018-05-05 11:00 | 52 | 46 |  |  | 43225.4583 | 64 | 63
2018-05-05 11:30 | 52 | 46 |  |  | 43225.4792 | 64 | 64
2018-05-05 12:00 | 54 | 48 |  |  | 43225.5 | 66 | 65
2018-05-05 12:30 | 55 | 49 |  |  | 43225.5208 | 65 | 64
2018-05-05 13:00 | 54 | 48 |  |  | 43225.5417 | 63 | 63
2018-05-05 13:30 | 55 | 49 |  |  | 43225.5625 | 66 | 65
2018-05-05 14:00 | 57 | 51 |  |  | 43225.5833 | 68 | 67
2018-05-05 14:30 | 59 | 53 |  |  | 43225.6042 | 69 | 68
2018-05-05 15:00 | 60 | 54 |  |  | 43225.625 | 72 | 71
2018-05-05 15:30 | 60 | 55 |  |  | 43225.6458 | 72 | 72
2018-05-05 16:00 | 61 | 56 |  |  | 43225.6667 | 75 | 75
2018-05-05 16:30 | 63 | 58 |  |  | 43225.6875 | 78 | 77
2018-05-05 17:00 | 66 | 61 |  |  | 43225.7083 | 81 | 81
2018-05-05 17:30 | 65 | 60 |  |  | 43225.7292 | 81 | 81
2018-05-05 18:00 | 65 | 60 |  |  | 43225.75 | 82 | 81
2018-05-05 18:30 | 64 | 59 |  |  | 43225.7708 | 80 | 79
2018-05-05 19:00 | 65 | 59 |  |  | 43225.7917 | 80 | 80
2018-05-05 19:30 | 64 | 57 |  |  | 43225.8125 | 79 | 79
2018-05-05 20:00 | 63 | 57 |  |  | 43225.8333 | 78 | 77
2018-05-05 20:30 | 63 | 57 |  |  | 43225.8542 | 79 | 78
2018-05-05 21:00 | 63 | 56 |  |  | 43225.875 | 76 | 75
2018-05-05 21:30 | 60 | 52 |  |  | 43225.8958 | 72 | 71
2018-05-05 22:00 | 60 | 52 |  |  | 43225.9167 | 73 | 71
2018-05-05 22:30 | 60 | 53 |  |  | 43225.9375 | 72 | 71
2018-05-05 23:00 | 59 | 51 |  |  | 43225.9583 | 69 | 68
2018-05-05 23:30 | 57 | 48 |  |  | 43225.9792 | 67 | 65
2018-05-06 | 55 | 46 |  |  | 43226 | 63 | 61
2018-05-06 00:30 | 51 | 41 |  |  | 43226.0208 | 58 | 56
2018-05-06 01:00 | 48 | 37 |  |  | 43226.0417 | 55 | 52
2018-05-06 01:30 | 48 | 36 |  |  | 43226.0625 | 53 | 50
2018-05-06 02:00 | 47 | 35 |  |  | 43226.0833 | 52 | 50
2018-05-06 02:30 | 47 | 36 |  |  | 43226.1042 | 51 | 49
2018-05-06 03:00 | 47 | 36 |  |  | 43226.125 | 50 | 48
2018-05-06 03:30 | 47 | 34 |  |  | 43226.1458 | 50 | 48
2018-05-06 04:00 | 47 | 34 |  |  | 43226.1667 | 50 | 47
2018-05-06 04:30 | 47 | 34 |  |  | 43226.1875 | 50 | 48
2018-05-06 05:00 | 48 | 36 |  |  | 43226.2083 | 51 | 49
2018-05-06 05:30 | 50 | 38 |  |  | 43226.2292 | 53 | 51
2018-05-06 06:00 | 50 | 39 |  |  | 43226.25 | 54 | 52
2018-05-06 06:30 | 51 | 40 |  |  | 43226.2708 | 56 | 54
2018-05-06 07:00 | 51 | 39 |  |  | 43226.2917 | 56 | 54
2018-05-06 07:30 | 51 | 39 |  |  | 43226.3125 | 57 | 55
2018-05-06 08:00 | 49 | 38 |  |  | 43226.3333 | 57 | 56
2018-05-06 08:30 | 48 | 38 |  |  | 43226.3542 | 57 | 56
2018-05-06 09:00 | 48 | 38 |  |  | 43226.375 | 57 | 55
2018-05-06 09:30 | 47 | 37 |  |  | 43226.3958 | 55 | 54
2018-05-06 10:00 | 45 | 35 |  |  | 43226.4167 | 53 | 53
2018-05-06 10:30 | 46 | 37 |  |  | 43226.4375 | 54 | 53
2018-05-06 11:00 | 47 | 38 |  |  | 43226.4583 | 56 | 55
2018-05-06 11:30 | 47 | 38 |  |  | 43226.4792 | 55 | 54
2018-05-06 12:00 | 47 | 38 |  |  | 43226.5 | 55 | 55
2018-05-06 12:30 | 50 | 41 |  |  | 43226.5208 | 59 | 59
2018-05-06 13:00 | 50 | 42 |  |  | 43226.5417 | 60 | 60
2018-05-06 13:30 | 50 | 42 |  |  | 43226.5625 | 60 | 59
2018-05-06 14:00 | 47 | 39 |  |  | 43226.5833 | 55 | 54
2018-05-06 14:30 | 49 | 42 |  |  | 43226.6042 | 58 | 58
2018-05-06 15:00 | 52 | 45 |  |  | 43226.625 | 60 | 60
2018-05-06 15:30 | 52 | 46 |  |  | 43226.6458 | 61 | 60
2018-05-06 16:00 | 54 | 48 |  |  | 43226.6667 | 64 | 64
2018-05-06 16:30 | 55 | 49 |  |  | 43226.6875 | 68 | 67
2018-05-06 17:00 | 58 | 52 |  |  | 43226.7083 | 70 | 70
2018-05-06 17:30 | 61 | 54 |  |  | 43226.7292 | 73 | 72
2018-05-06 18:00 | 60 | 53 |  |  | 43226.75 | 73 | 72
2018-05-06 18:30 | 62 | 54 |  |  | 43226.7708 | 72 | 72
2018-05-06 19:00 | 64 | 56 |  |  | 43226.7917 | 75 | 74
2018-05-06 19:30 | 63 | 56 |  |  | 43226.8125 | 74 | 73
2018-05-06 20:00 | 63 | 56 |  |  | 43226.8333 | 73 | 72
2018-05-06 20:30 | 61 | 54 |  |  | 43226.8542 | 72 | 71
2018-05-06 21:00 | 59 | 51 |  |  | 43226.875 | 68 | 67
2018-05-06 21:30 | 57 | 49 |  |  | 43226.8958 | 66 | 65
2018-05-06 22:00 | 58 | 49 |  |  | 43226.9167 | 68 | 67
2018-05-06 22:30 | 61 | 52 |  |  | 43226.9375 | 70 | 69
2018-05-06 23:00 | 61 | 52 |  |  | 43226.9583 | 69 | 67
2018-05-06 23:30 | 58 | 49 |  |  | 43226.9792 | 65 | 63
2018-05-07 | 55 | 45 |  |  | 43227 | 61 | 59
2018-05-07 00:30 | 52 | 41 |  |  | 43227.0208 | 56 | 54
2018-05-07 01:00 | 53 | 41 |  |  | 43227.0417 | 55 | 52
2018-05-07 01:30 | 51 | 40 |  |  | 43227.0625 | 53 | 51
2018-05-07 02:00 | 51 | 40 |  |  | 43227.0833 | 54 | 53
2018-05-07 02:30 | 54 | 43 |  |  | 43227.1042 | 60 | 58
2018-05-07 03:00 | 56 | 45 |  |  | 43227.125 | 60 | 58
2018-05-07 03:30 | 56 | 44 |  |  | 43227.1458 | 60 | 58
2018-05-07 04:00 | 55 | 43 |  |  | 43227.1667 | 60 | 58
2018-05-07 04:30 | 55 | 44 |  |  | 43227.1875 | 60 | 57
2018-05-07 05:00 | 54 | 43 |  |  | 43227.2083 | 58 | 56
2018-05-07 05:30 | 54 | 43 |  |  | 43227.2292 | 60 | 57
2018-05-07 06:00 | 53 | 42 |  |  | 43227.25 | 59 | 58
2018-05-07 06:30 | 51 | 41 |  |  | 43227.2708 | 59 | 58
2018-05-07 07:00 | 50 | 39 |  |  | 43227.2917 | 59 | 57
2018-05-07 07:30 | 48 | 38 |  |  | 43227.3125 | 57 | 56
2018-05-07 08:00 | 48 | 38 |  |  | 43227.3333 | 57 | 57
2018-05-07 08:30 | 50 | 42 |  |  | 43227.3542 | 60 | 60
2018-05-07 09:00 | 51 | 42 |  |  | 43227.375 | 62 | 62
2018-05-07 09:30 | 51 | 43 |  |  | 43227.3958 | 63 | 63
2018-05-07 10:00 | 56 | 48 |  |  | 43227.4167 | 67 | 67
2018-05-07 10:30 | 56 | 46 |  |  | 43227.4375 | 68 | 66
2018-05-07 11:00 | 60 | 51 |  |  | 43227.4583 | 74 | 73
2018-05-07 11:30 | 60 | 50 |  |  | 43227.4792 | 72 | 70
2018-05-07 12:00 | 61 | 53 |  |  | 43227.5 | 74 | 72
2018-05-07 12:30 | 61 | 52 |  |  | 43227.5208 | 71 | 69
2018-05-07 13:00 | 61 | 53 |  |  | 43227.5417 | 71 | 69
2018-05-07 13:30 | 65 | 57 |  |  | 43227.5625 | 78 | 76
2018-05-07 14:00 | 67 | 59 |  |  | 43227.5833 | 78 | 77
2018-05-07 14:30 | 67 | 59 |  |  | 43227.6042 | 78 | 77
2018-05-07 15:00 | 66 | 58 |  |  | 43227.625 | 77 | 75
2018-05-07 15:30 | 66 | 58 |  |  | 43227.6458 | 77 | 75
2018-05-07 16:00 | 70 | 62 |  |  | 43227.6667 | 81 | 79
2018-05-07 16:30 | 72 | 65 |  |  | 43227.6875 | 84 | 83
2018-05-07 17:00 | 74 | 68 |  |  | 43227.7083 | 87 | 85
2018-05-07 17:30 | 78 | 71 |  |  | 43227.7292 | 90 | 88
2018-05-07 18:00 | 79 | 72 |  |  | 43227.75 | 91 | 89
2018-05-07 18:30 | 78 | 71 |  |  | 43227.7708 | 90 | 88
2018-05-07 19:00 | 78 | 71 |  |  | 43227.7917 | 89 | 87
2018-05-07 19:30 | 76 | 69 |  |  | 43227.8125 | 86 | 84
2018-05-07 20:00 | 74 | 68 |  |  | 43227.8333 | 85 | 83
2018-05-07 20:30 | 73 | 67 |  |  | 43227.8542 | 84 | 83
2018-05-07 21:00 | 71 | 64 |  |  | 43227.875 | 80 | 79
2018-05-07 21:30 | 67 | 60 |  |  | 43227.8958 | 76 | 75
2018-05-07 22:00 | 67 | 60 |  |  | 43227.9167 | 76 | 75
2018-05-07 22:30 | 64 | 56 |  |  | 43227.9375 | 73 | 72
2018-05-07 23:00 | 65 | 56 |  |  | 43227.9583 | 72 | 71
2018-05-07 23:30 | 64 | 55 |  |  | 43227.9792 | 70 | 68
2018-05-08 | 59 | 49 |  |  | 43228 | 65 | 63
2018-05-08 00:30 | 56 | 44 |  |  | 43228.0208 | 60 | 57
2018-05-08 01:00 | 54 | 41 |  |  | 43228.0417 | 56 | 53
2018-05-08 01:30 | 54 | 40 |  |  | 43228.0625 | 54 | 51
2018-05-08 02:00 | 53 | 40 |  |  | 43228.0833 | 54 | 51
2018-05-08 02:30 | 54 | 41 |  |  | 43228.1042 | 55 | 51
2018-05-08 03:00 | 53 | 39 |  |  | 43228.125 | 54 | 50
2018-05-08 03:30 | 53 | 39 |  |  | 43228.1458 | 54 | 51
2018-05-08 04:00 | 54 | 41 |  |  | 43228.1667 | 55 | 51
2018-05-08 04:30 | 54 | 42 |  |  | 43228.1875 | 56 | 52
2018-05-08 05:00 | 56 | 44 |  |  | 43228.2083 | 58 | 55
2018-05-08 05:30 | 60 | 50 |  |  | 43228.2292 | 64 | 61
2018-05-08 06:00 | 63 | 56 |  |  | 43228.25 | 70 | 68
2018-05-08 06:30 | 66 | 61 |  |  | 43228.2708 | 79 | 79
2018-05-08 07:00 | 72 | 68 |  |  | 43228.2917 | 89 | 89
2018-05-08 07:30 | 80 | 76 |  |  | 43228.3125 | 98 | 98
2018-05-08 08:00 | 80 | 76 |  |  | 43228.3333 | 99 | 99
2018-05-08 08:30 | 82 | 79 |  |  | 43228.3542 | 105 | 105
2018-05-08 09:00 | 82 | 79 |  |  | 43228.375 | 106 | 106
2018-05-08 09:30 | 78 | 74 |  |  | 43228.3958 | 102 | 101
2018-05-08 10:00 | 75 | 71 |  |  | 43228.4167 | 99 | 99
2018-05-08 10:30 | 76 | 73 |  |  | 43228.4375 | 101 | 101
2018-05-08 11:00 | 80 | 77 |  |  | 43228.4583 | 105 | 105
2018-05-08 11:30 | 78 | 74 |  |  | 43228.4792 | 101 | 100
2018-05-08 12:00 | 75 | 71 |  |  | 43228.5 | 97 | 97
2018-05-08 12:30 | 76 | 72 |  |  | 43228.5208 | 98 | 98
2018-05-08 13:00 | 76 | 72 |  |  | 43228.5417 | 100 | 100
2018-05-08 13:30 | 78 | 74 |  |  | 43228.5625 | 102 | 102
2018-05-08 14:00 | 76 | 73 |  |  | 43228.5833 | 101 | 100
2018-05-08 14:30 | 80 | 77 |  |  | 43228.6042 | 104 | 103
2018-05-08 15:00 | 81 | 77 |  |  | 43228.625 | 103 | 103
2018-05-08 15:30 | 83 | 79 |  |  | 43228.6458 | 101 | 101
2018-05-08 16:00 | 82 | 77 |  |  | 43228.6667 | 98 | 97
2018-05-08 16:30 | 81 | 76 |  |  | 43228.6875 | 100 | 99
2018-05-08 17:00 | 85 | 80 |  |  | 43228.7083 | 103 | 102
2018-05-08 17:30 | 88 | 84 |  |  | 43228.7292 | 106 | 105
2018-05-08 18:00 | 85 | 81 |  |  | 43228.75 | 103 | 102
2018-05-08 18:30 | 87 | 83 |  |  | 43228.7708 | 102 | 100
2018-05-08 19:00 | 87 | 83 |  |  | 43228.7917 | 102 | 101
2018-05-08 19:30 | 86 | 82 |  |  | 43228.8125 | 100 | 99
2018-05-08 20:00 | 83 | 80 |  |  | 43228.8333 | 98 | 97
2018-05-08 20:30 | 82 | 79 |  |  | 43228.8542 | 96 | 96
2018-05-08 21:00 | 78 | 76 |  |  | 43228.875 | 91 | 91
2018-05-08 21:30 | 74 | 71 |  |  | 43228.8958 | 85 | 85
2018-05-08 22:00 | 73 | 69 |  |  | 43228.9167 | 84 | 84
2018-05-08 22:30 | 68 | 64 |  |  | 43228.9375 | 80 | 79
2018-05-08 23:00 | 65 | 61 |  |  | 43228.9583 | 75 | 74
2018-05-08 23:30 | 62 | 56 |  |  | 43228.9792 | 71 | 70
2018-05-09 | 59 | 53 |  |  | 43229 | 67 | 66
2018-05-09 00:30 | 57 | 49 |  |  | 43229.0208 | 61 | 60
2018-05-09 01:00 | 54 | 45 |  |  | 43229.0417 | 56 | 55
2018-05-09 01:30 | 53 | 43 |  |  | 43229.0625 | 54 | 53
2018-05-09 02:00 | 54 | 44 |  |  | 43229.0833 | 55 | 54
2018-05-09 02:30 | 53 | 42 |  |  | 43229.1042 | 55 | 53
2018-05-09 03:00 | 54 | 43 |  |  | 43229.125 | 55 | 53
2018-05-09 03:30 | 53 | 43 |  |  | 43229.1458 | 54 | 52
2018-05-09 04:00 | 52 | 41 |  |  | 43229.1667 | 53 | 52
2018-05-09 04:30 | 53 | 43 |  |  | 43229.1875 | 55 | 53
2018-05-09 05:00 | 56 | 47 |  |  | 43229.2083 | 58 | 57
2018-05-09 05:30 | 58 | 50 |  |  | 43229.2292 | 62 | 62
2018-05-09 06:00 | 61 | 55 |  |  | 43229.25 | 68 | 68
2018-05-09 06:30 | 66 | 60 |  |  | 43229.2708 | 78 | 78
2018-05-09 07:00 | 72 | 68 |  |  | 43229.2917 | 88 | 87
2018-05-09 07:30 | 81 | 75 |  |  | 43229.3125 | 97 | 96
2018-05-09 08:00 | 82 | 77 |  |  | 43229.3333 | 100 | 98
2018-05-09 08:30 | 80 | 75 |  |  | 43229.3542 | 97 | 96
2018-05-09 09:00 | 80 | 75 |  |  | 43229.375 | 96 | 95
2018-05-09 09:30 | 77 | 71 |  |  | 43229.3958 | 93 | 92
2018-05-09 10:00 | 73 | 68 |  |  | 43229.4167 | 91 | 90
2018-05-09 10:30 | 72 | 67 |  |  | 43229.4375 | 90 | 89
2018-05-09 11:00 | 73 | 69 |  |  | 43229.4583 | 90 | 90
2018-05-09 11:30 | 74 | 69 |  |  | 43229.4792 | 90 | 90
2018-05-09 12:00 | 73 | 69 |  |  | 43229.5 | 92 | 91
2018-05-09 12:30 | 73 | 69 |  |  | 43229.5208 | 92 | 92
2018-05-09 13:00 | 74 | 69 |  |  | 43229.5417 | 92 | 92
2018-05-09 13:30 | 76 | 71 |  |  | 43229.5625 | 94 | 94
2018-05-09 14:00 | 75 | 72 |  |  | 43229.5833 | 95 | 94
2018-05-09 14:30 | 75 | 71 |  |  | 43229.6042 | 94 | 92
2018-05-09 15:00 | 75 | 71 |  |  | 43229.625 | 94 | 92
2018-05-09 15:30 | 79 | 75 |  |  | 43229.6458 | 98 | 96
2018-05-09 16:00 | 83 | 79 |  |  | 43229.6667 | 101 | 99
2018-05-09 16:30 | 87 | 84 |  |  | 43229.6875 | 105 | 103
2018-05-09 17:00 | 91 | 87 |  |  | 43229.7083 | 108 | 106
2018-05-09 17:30 | 90 | 85 |  |  | 43229.7292 | 107 | 104
2018-05-09 18:00 | 90 | 85 |  |  | 43229.75 | 107 | 103
2018-05-09 18:30 | 92 | 87 |  |  | 43229.7708 | 107 | 103
2018-05-09 19:00 | 91 | 85 |  |  | 43229.7917 | 106 | 102
2018-05-09 19:30 | 87 | 82 |  |  | 43229.8125 | 101 | 98
2018-05-09 20:00 | 85 | 81 |  |  | 43229.8333 | 100 | 98
2018-05-09 20:30 | 86 | 82 |  |  | 43229.8542 | 100 | 98
2018-05-09 21:00 | 82 | 79 |  |  | 43229.875 | 96 | 94
2018-05-09 21:30 | 77 | 74 |  |  | 43229.8958 | 90 | 89
2018-05-09 22:00 | 76 | 72 |  |  | 43229.9167 | 88 | 87
2018-05-09 22:30 | 74 | 69 |  |  | 43229.9375 | 84 | 83
2018-05-09 23:00 | 70 | 64 |  |  | 43229.9583 | 77 | 76
2018-05-09 23:30 | 66 | 59 |  |  | 43229.9792 | 72 | 71
2018-05-10 | 62 | 54 |  |  | 43230 | 68 | 67
2018-05-10 00:30 | 58 | 49 |  |  | 43230.0208 | 62 | 61
2018-05-10 01:00 | 58 | 48 |  |  | 43230.0417 | 61 | 59
2018-05-10 01:30 | 58 | 48 |  |  | 43230.0625 | 60 | 58
2018-05-10 02:00 | 58 | 48 |  |  | 43230.0833 | 59 | 57
2018-05-10 02:30 | 58 | 48 |  |  | 43230.1042 | 59 | 57
2018-05-10 03:00 | 58 | 47 |  |  | 43230.125 | 59 | 57
2018-05-10 03:30 | 59 | 48 |  |  | 43230.1458 | 59 | 57
2018-05-10 04:00 | 58 | 48 |  |  | 43230.1667 | 59 | 56
2018-05-10 04:30 | 59 | 49 |  |  | 43230.1875 | 60 | 58
2018-05-10 05:00 | 61 | 51 |  |  | 43230.2083 | 63 | 61
2018-05-10 05:30 | 63 | 55 |  |  | 43230.2292 | 67 | 65
2018-05-10 06:00 | 65 | 59 |  |  | 43230.25 | 72 | 70
2018-05-10 06:30 | 68 | 63 |  |  | 43230.2708 | 79 | 78
2018-05-10 07:00 | 69 | 65 |  |  | 43230.2917 | 85 | 84
2018-05-10 07:30 | 73 | 69 |  |  | 43230.3125 | 90 | 90
2018-05-10 08:00 | 81 | 78 |  |  | 43230.3333 | 96 | 95
2018-05-10 08:30 | 82 | 78 |  |  | 43230.3542 | 96 | 95
2018-05-10 09:00 | 81 | 77 |  |  | 43230.375 | 95 | 94
2018-05-10 09:30 | 81 | 77 |  |  | 43230.3958 | 94 | 94
2018-05-10 10:00 | 79 | 76 |  |  | 43230.4167 | 94 | 93
2018-05-10 10:30 | 81 | 77 |  |  | 43230.4375 | 94 | 94
2018-05-10 11:00 | 82 | 78 |  |  | 43230.4583 | 94 | 93
2018-05-10 11:30 | 83 | 78 |  |  | 43230.4792 | 96 | 95
2018-05-10 12:00 | 84 | 79 |  |  | 43230.5 | 97 | 96
2018-05-10 12:30 | 85 | 81 |  |  | 43230.5208 | 98 | 97
2018-05-10 13:00 | 85 | 80 |  |  | 43230.5417 | 97 | 96
2018-05-10 13:30 | 85 | 81 |  |  | 43230.5625 | 97 | 96
2018-05-10 14:00 | 85 | 81 |  |  | 43230.5833 | 98 | 97
2018-05-10 14:30 | 88 | 84 |  |  | 43230.6042 | 100 | 99
2018-05-10 15:00 | 77 | 73 |  |  | 43230.625 | 94 | 93
2018-05-10 15:30 | 77 | 72 |  |  | 43230.6458 | 94 | 93
2018-05-10 16:00 | 80 | 74 |  |  | 43230.6667 | 98 | 96
2018-05-10 16:30 | 83 | 77 |  |  | 43230.6875 | 101 | 99
2018-05-10 17:00 | 86 | 80 |  |  | 43230.7083 | 104 | 101
2018-05-10 17:30 | 87 | 81 |  |  | 43230.7292 | 105 | 102
2018-05-10 18:00 | 87 | 82 |  |  | 43230.75 | 106 | 103
2018-05-10 18:30 | 87 | 82 |  |  | 43230.7708 | 104 | 101
2018-05-10 19:00 | 87 | 82 |  |  | 43230.7917 | 104 | 101
2018-05-10 19:30 | 86 | 81 |  |  | 43230.8125 | 101 | 99
2018-05-10 20:00 | 87 | 81 |  |  | 43230.8333 | 100 | 97
2018-05-10 20:30 | 86 | 80 |  |  | 43230.8542 | 99 | 96
2018-05-10 21:00 | 82 | 77 |  |  | 43230.875 | 94 | 93
2018-05-10 21:30 | 77 | 71 |  |  | 43230.8958 | 87 | 86
2018-05-10 22:00 | 76 | 69 |  |  | 43230.9167 | 86 | 84
2018-05-10 22:30 | 74 | 67 |  |  | 43230.9375 | 82 | 80
2018-05-10 23:00 | 72 | 64 |  |  | 43230.9583 | 79 | 77
2018-05-10 23:30 | 70 | 61 |  |  | 43230.9792 | 76 | 74
2018-05-11 | 66 | 57 |  |  | 43231 | 71 | 69
2018-05-11 00:30 | 61 | 50 |  |  | 43231.0208 | 64 | 61
2018-05-11 01:00 | 59 | 48 |  |  | 43231.0417 | 61 | 58
2018-05-11 01:30 | 57 | 45 |  |  | 43231.0625 | 57 | 54
2018-05-11 02:00 | 57 | 44 |  |  | 43231.0833 | 57 | 53
2018-05-11 02:30 | 57 | 44 |  |  | 43231.1042 | 57 | 53
2018-05-11 03:00 | 58 | 45 |  |  | 43231.125 | 58 | 54
2018-05-11 03:30 | 60 | 47 |  |  | 43231.1458 | 60 | 57
2018-05-11 04:00 | 59 | 47 |  |  | 43231.1667 | 60 | 57
2018-05-11 04:30 | 60 | 48 |  |  | 43231.1875 | 61 | 58
2018-05-11 05:00 | 61 | 50 |  |  | 43231.2083 | 63 | 59
2018-05-11 05:30 | 62 | 53 |  |  | 43231.2292 | 66 | 63
2018-05-11 06:00 | 62 | 55 |  |  | 43231.25 | 68 | 66
2018-05-11 06:30 | 66 | 61 |  |  | 43231.2708 | 76 | 76
2018-05-11 07:00 | 69 | 66 |  |  | 43231.2917 | 84 | 84
2018-05-11 07:30 | 71 | 68 |  |  | 43231.3125 | 88 | 88
2018-05-11 08:00 | 68 | 65 |  |  | 43231.3333 | 86 | 86
2018-05-11 08:30 | 69 | 67 |  |  | 43231.3542 | 87 | 87
2018-05-11 09:00 | 76 | 73 |  |  | 43231.375 | 97 | 97
2018-05-11 09:30 | 72 | 70 |  |  | 43231.3958 | 93 | 92
2018-05-11 10:00 | 72 | 69 |  |  | 43231.4167 | 93 | 92
2018-05-11 10:30 | 71 | 68 |  |  | 43231.4375 | 91 | 90
2018-05-11 11:00 | 71 | 67 |  |  | 43231.4583 | 90 | 88
2018-05-11 11:30 | 71 | 68 |  |  | 43231.4792 | 90 | 89
2018-05-11 12:00 | 70 | 66 |  |  | 43231.5 | 89 | 87
2018-05-11 12:30 | 70 | 65 |  |  | 43231.5208 | 88 | 86
2018-05-11 13:00 | 70 | 65 |  |  | 43231.5417 | 90 | 87
2018-05-11 13:30 | 66 | 60 |  |  | 43231.5625 | 87 | 85
2018-05-11 14:00 | 69 | 62 |  |  | 43231.5833 | 89 | 87
2018-05-11 14:30 | 72 | 66 |  |  | 43231.6042 | 92 | 89
2018-05-11 15:00 | 74 | 67 |  |  | 43231.625 | 94 | 92
2018-05-11 15:30 | 77 | 71 |  |  | 43231.6458 | 96 | 94
2018-05-11 16:00 | 80 | 74 |  |  | 43231.6667 | 100 | 97
2018-05-11 16:30 | 84 | 78 |  |  | 43231.6875 | 105 | 102
2018-05-11 17:00 | 82 | 81 |  |  | 43231.7083 | 107 | 105
2018-05-11 17:30 | 82 | 81 |  |  | 43231.7292 | 108 | 106
2018-05-11 18:00 | 82 | 81 |  |  | 43231.75 | 107 | 105
2018-05-11 18:30 | 81 | 80 |  |  | 43231.7708 | 104 | 102
2018-05-11 19:00 | 83 | 82 |  |  | 43231.7917 | 106 | 105
2018-05-11 19:30 | 86 | 85 |  |  | 43231.8125 | 109 | 108
2018-05-11 20:00 | 83 | 82 |  |  | 43231.8333 | 108 | 108
2018-05-11 20:30 | 83 | 82 |  |  | 43231.8542 | 106 | 106
2018-05-11 21:00 | 80 | 79 |  |  | 43231.875 | 102 | 102
2018-05-11 21:30 | 76 | 75 |  |  | 43231.8958 | 98 | 97
2018-05-11 22:00 | 76 | 75 |  |  | 43231.9167 | 97 | 97
2018-05-11 22:30 | 72 | 71 |  |  | 43231.9375 | 94 | 94
2018-05-11 23:00 | 68 | 67 |  |  | 43231.9583 | 86 | 86
2018-05-11 23:30 | 64 | 62 |  |  | 43231.9792 | 80 | 80
2018-05-12 | 60 | 58 |  |  | 43232 | 76 | 75
2018-05-12 00:30 | 57 | 54 |  |  | 43232.0208 | 71 | 70
2018-05-12 01:00 | 56 | 53 |  |  | 43232.0417 | 69 | 68
2018-05-12 01:30 | 53 | 50 |  |  | 43232.0625 | 62 | 60
2018-05-12 02:00 | 52 | 47 |  |  | 43232.0833 | 57 | 55
2018-05-12 02:30 | 50 | 45 |  |  | 43232.1042 | 57 | 55
2018-05-12 03:00 | 50 | 45 |  |  | 43232.125 | 57 | 55
2018-05-12 03:30 | 51 | 45 |  |  | 43232.1458 | 58 | 56
2018-05-12 04:00 | 53 | 47 |  |  | 43232.1667 | 59 | 57
2018-05-12 04:30 | 53 | 47 |  |  | 43232.1875 | 60 | 58
2018-05-12 05:00 | 55 | 49 |  |  | 43232.2083 | 62 | 60
2018-05-12 05:30 | 55 | 49 |  |  | 43232.2292 | 63 | 61
2018-05-12 06:00 | 54 | 49 |  |  | 43232.25 | 63 | 61
2018-05-12 06:30 | 55 | 50 |  |  | 43232.2708 | 65 | 63
2018-05-12 07:00 | 54 | 50 |  |  | 43232.2917 | 65 | 64
2018-05-12 07:30 | 56 | 52 |  |  | 43232.3125 | 68 | 67
2018-05-12 08:00 | 56 | 54 |  |  | 43232.3333 | 68 | 68
2018-05-12 08:30 | 56 | 53 |  |  | 43232.3542 | 68 | 67
2018-05-12 09:00 | 54 | 52 |  |  | 43232.375 | 67 | 67
2018-05-12 09:30 | 51 | 49 |  |  | 43232.3958 | 65 | 65
2018-05-12 10:00 | 50 | 48 |  |  | 43232.4167 | 63 | 63
2018-05-12 10:30 | 51 | 49 |  |  | 43232.4375 | 63 | 63
2018-05-12 11:00 | 52 | 50 |  |  | 43232.4583 | 64 | 64
2018-05-12 11:30 | 51 | 49 |  |  | 43232.4792 | 63 | 62
2018-05-12 12:00 | 49 | 47 |  |  | 43232.5 | 62 | 61
2018-05-12 12:30 | 46 | 44 |  |  | 43232.5208 | 57 | 56
2018-05-12 13:00 | 47 | 45 |  |  | 43232.5417 | 57 | 56
2018-05-12 13:30 | 46 | 44 |  |  | 43232.5625 | 57 | 57
2018-05-12 14:00 | 49 | 46 |  |  | 43232.5833 | 58 | 58
2018-05-12 14:30 | 50 | 48 |  |  | 43232.6042 | 61 | 60
2018-05-12 15:00 | 50 | 49 |  |  | 43232.625 | 62 | 62
2018-05-12 15:30 | 51 | 50 |  |  | 43232.6458 | 64 | 64
2018-05-12 16:00 | 52 | 51 |  |  | 43232.6667 | 65 | 65
2018-05-12 16:30 | 53 | 52 |  |  | 43232.6875 | 69 | 68
2018-05-12 17:00 | 55 | 54 |  |  | 43232.7083 | 72 | 72
2018-05-12 17:30 | 57 | 56 |  |  | 43232.7292 | 74 | 74
2018-05-12 18:00 | 57 | 57 |  |  | 43232.75 | 76 | 76
2018-05-12 18:30 | 57 | 56 |  |  | 43232.7708 | 76 | 76
2018-05-12 19:00 | 60 | 60 |  |  | 43232.7917 | 78 | 78
2018-05-12 19:30 | 59 | 59 |  |  | 43232.8125 | 76 | 76
2018-05-12 20:00 | 57 | 56 |  |  | 43232.8333 | 74 | 74
2018-05-12 20:30 | 55 | 55 |  |  | 43232.8542 | 73 | 73
2018-05-12 21:00 | 55 | 54 |  |  | 43232.875 | 71 | 71
2018-05-12 21:30 | 52 | 51 |  |  | 43232.8958 | 68 | 67
2018-05-12 22:00 | 53 | 52 |  |  | 43232.9167 | 69 | 68
2018-05-12 22:30 | 53 | 52 |  |  | 43232.9375 | 69 | 69
2018-05-12 23:00 | 52 | 51 |  |  | 43232.9583 | 66 | 65
2018-05-12 23:30 | 50 | 48 |  |  | 43232.9792 | 62 | 62
2018-05-13 | 46 | 43 |  |  | 43233 | 57 | 57
2018-05-13 00:30 | 44 | 40 |  |  | 43233.0208 | 55 | 54
2018-05-13 01:00 | 44 | 40 |  |  | 43233.0417 | 54 | 52
2018-05-13 01:30 | 43 | 38 |  |  | 43233.0625 | 52 | 50
2018-05-13 02:00 | 39 | 38 |  |  | 43233.0833 | 53 | 49
2018-05-13 02:30 | 37 | 37 |  |  | 43233.1042 | 51 | 48
2018-05-13 03:00 | 37 | 36 |  |  | 43233.125 | 51 | 47
2018-05-13 03:30 | 36 | 36 |  |  | 43233.1458 | 50 | 46
2018-05-13 04:00 | 36 | 36 |  |  | 43233.1667 | 51 | 47
2018-05-13 04:30 | 37 | 37 |  |  | 43233.1875 | 51 | 47
2018-05-13 05:00 | 38 | 37 |  |  | 43233.2083 | 51 | 47
2018-05-13 05:30 | 39 | 38 |  |  | 43233.2292 | 53 | 49
2018-05-13 06:00 | 39 | 39 |  |  | 43233.25 | 53 | 50
2018-05-13 06:30 | 41 | 40 |  |  | 43233.2708 | 55 | 51
2018-05-13 07:00 | 42 | 41 |  |  | 43233.2917 | 57 | 54
2018-05-13 07:30 | 43 | 43 |  |  | 43233.3125 | 59 | 56
2018-05-13 08:00 | 40 | 40 |  |  | 43233.3333 | 58 | 55
2018-05-13 08:30 | 37 | 37 |  |  | 43233.3542 | 55 | 52
2018-05-13 09:00 | 37 | 36 |  |  | 43233.375 | 55 | 52
2018-05-13 09:30 | 37 | 37 |  |  | 43233.3958 | 55 | 52
2018-05-13 10:00 | 36 | 35 |  |  | 43233.4167 | 54 | 51
2018-05-13 10:30 | 34 | 34 |  |  | 43233.4375 | 51 | 49
2018-05-13 11:00 | 34 | 34 |  |  | 43233.4583 | 52 | 49
2018-05-13 11:30 | 34 | 34 |  |  | 43233.4792 | 51 | 49
2018-05-13 12:00 | 32 | 32 |  |  | 43233.5 | 50 | 48
2018-05-13 12:30 | 32 | 32 |  |  | 43233.5208 | 49 | 47
2018-05-13 13:00 | 33 | 33 |  |  | 43233.5417 | 50 | 47
2018-05-13 13:30 | 35 | 35 |  |  | 43233.5625 | 52 | 49
2018-05-13 14:00 | 36 | 36 |  |  | 43233.5833 | 53 | 50
2018-05-13 14:30 | 38 | 38 |  |  | 43233.6042 | 55 | 52
2018-05-13 15:00 | 40 | 40 |  |  | 43233.625 | 57 | 55
2018-05-13 15:30 | 41 | 41 |  |  | 43233.6458 | 59 | 57
2018-05-13 16:00 | 44 | 44 |  |  | 43233.6667 | 63 | 62
2018-05-13 16:30 | 48 | 48 |  |  | 43233.6875 | 68 | 66
2018-05-13 17:00 | 52 | 52 |  |  | 43233.7083 | 72 | 70
2018-05-13 17:30 | 54 | 54 |  |  | 43233.7292 | 72 | 71
2018-05-13 18:00 | 53 | 53 |  |  | 43233.75 | 73 | 71
2018-05-13 18:30 | 52 | 52 |  |  | 43233.7708 | 72 | 71
2018-05-13 19:00 | 54 | 54 |  |  | 43233.7917 | 74 | 72
2018-05-13 19:30 | 53 | 53 |  |  | 43233.8125 | 73 | 71
2018-05-13 20:00 | 52 | 52 |  |  | 43233.8333 | 70 | 69
2018-05-13 20:30 | 50 | 50 |  |  | 43233.8542 | 70 | 68
2018-05-13 21:00 | 49 | 49 |  |  | 43233.875 | 68 | 66
2018-05-13 21:30 | 51 | 51 |  |  | 43233.8958 | 66 | 64
2018-05-13 22:00 | 50 | 50 |  |  | 43233.9167 | 68 | 66
2018-05-13 22:30 | 50 | 50 |  |  | 43233.9375 | 67 | 65
2018-05-13 23:00 | 50 | 50 |  |  | 43233.9583 | 66 | 64
2018-05-13 23:30 | 48 | 47 |  |  | 43233.9792 | 64 | 62
2018-05-14 | 44 | 44 |  |  | 43234 | 61 | 58
2018-05-14 00:30 | 42 | 42 |  |  | 43234.0208 | 58 | 54
2018-05-14 01:00 | 41 | 40 |  |  | 43234.0417 | 55 | 51
2018-05-14 01:30 | 39 | 39 |  |  | 43234.0625 | 54 | 50
2018-05-14 02:00 | 38 | 37 |  |  | 43234.0833 | 52 | 49
2018-05-14 02:30 | 37 | 36 |  |  | 43234.1042 | 51 | 47
2018-05-14 03:00 | 36 | 36 |  |  | 43234.125 | 51 | 48
2018-05-14 03:30 | 36 | 36 |  |  | 43234.1458 | 51 | 47
2018-05-14 04:00 | 37 | 37 |  |  | 43234.1667 | 51 | 48
2018-05-14 04:30 | 36 | 36 |  |  | 43234.1875 | 52 | 48
2018-05-14 05:00 | 40 | 39 |  |  | 43234.2083 | 54 | 51
2018-05-14 05:30 | 42 | 42 |  |  | 43234.2292 | 56 | 54
2018-05-14 06:00 | 50 | 50 |  |  | 43234.25 | 64 | 63
2018-05-14 06:30 | 55 | 55 |  |  | 43234.2708 | 75 | 73
2018-05-14 07:00 | 59 | 58 |  |  | 43234.2917 | 88 | 81
2018-05-14 07:30 | 61 | 60 |  |  | 43234.3125 | 93 | 86
2018-05-14 08:00 | 59 | 58 |  |  | 43234.3333 | 91 | 84
2018-05-14 08:30 | 57 | 55 |  |  | 43234.3542 | 89 | 82
2018-05-14 09:00 | 53 | 52 |  |  | 43234.375 | 84 | 77
2018-05-14 09:30 | 53 | 51 |  |  | 43234.3958 | 82 | 74
2018-05-14 10:00 | 53 | 52 |  |  | 43234.4167 | 81 | 73
2018-05-14 10:30 | 52 | 51 |  |  | 43234.4375 | 79 | 72
2018-05-14 11:00 | 51 | 50 |  |  | 43234.4583 | 76 | 70
2018-05-14 11:30 | 49 | 48 |  |  | 43234.4792 | 75 | 68
2018-05-14 12:00 | 51 | 50 |  |  | 43234.5 | 78 | 72
2018-05-14 12:30 | 52 | 51 |  |  | 43234.5208 | 78 | 72
2018-05-14 13:00 | 52 | 52 |  |  | 43234.5417 | 76 | 71
2018-05-14 13:30 | 54 | 53 |  |  | 43234.5625 | 79 | 73
2018-05-14 14:00 | 55 | 55 |  |  | 43234.5833 | 80 | 74
2018-05-14 14:30 | 57 | 56 |  |  | 43234.6042 | 82 | 75
2018-05-14 15:00 | 55 | 55 |  |  | 43234.625 | 83 | 76
2018-05-14 15:30 | 56 | 55 |  |  | 43234.6458 | 88 | 78
2018-05-14 16:00 | 59 | 56 |  |  | 43234.6667 | 93 | 80
2018-05-14 16:30 | 63 | 60 |  |  | 43234.6875 | 98 | 84
2018-05-14 17:00 | 68 | 66 |  |  | 43234.7083 | 102 | 88
2018-05-14 17:30 | 70 | 67 |  |  | 43234.7292 | 105 | 90
2018-05-14 18:00 | 69 | 66 |  |  | 43234.75 | 105 | 89
2018-05-14 18:30 | 67 | 64 |  |  | 43234.7708 | 101 | 86
2018-05-14 19:00 | 65 | 62 |  |  | 43234.7917 | 99 | 85
2018-05-14 19:30 | 65 | 62 |  |  | 43234.8125 | 98 | 83
2018-05-14 20:00 | 64 | 61 |  |  | 43234.8333 | 96 | 81
2018-05-14 20:30 | 62 | 59 |  |  | 43234.8542 | 94 | 79
2018-05-14 21:00 | 56 | 56 |  |  | 43234.875 | 78 | 73
2018-05-14 21:30 | 51 | 51 |  |  | 43234.8958 | 73 | 68
2018-05-14 22:00 | 49 | 49 |  |  | 43234.9167 | 71 | 67
2018-05-14 22:30 | 48 | 48 |  |  | 43234.9375 | 68 | 66
2018-05-14 23:00 | 48 | 48 |  |  | 43234.9583 | 65 | 64
2018-05-14 23:30 | 44 | 44 |  |  | 43234.9792 | 63 | 61
2018-05-15 | 41 | 41 |  |  | 43235 | 58 | 56
2018-05-15 00:30 | 37 | 37 |  |  | 43235.0208 | 53 | 50
2018-05-15 01:00 | 34 | 34 |  |  | 43235.0417 | 50 | 47
2018-05-15 01:30 | 34 | 34 |  |  | 43235.0625 | 50 | 46
2018-05-15 02:00 | 34 | 34 |  |  | 43235.0833 | 49 | 45
2018-05-15 02:30 | 34 | 34 |  |  | 43235.1042 | 49 | 44
2018-05-15 03:00 | 34 | 34 |  |  | 43235.125 | 49 | 44
2018-05-15 03:30 | 33 | 33 |  |  | 43235.1458 | 47 | 43
2018-05-15 04:00 | 34 | 34 |  |  | 43235.1667 | 48 | 44
2018-05-15 04:30 | 37 | 37 |  |  | 43235.1875 | 52 | 48
2018-05-15 05:00 | 40 | 40 |  |  | 43235.2083 | 56 | 52
2018-05-15 05:30 | 44 | 44 |  |  | 43235.2292 | 60 | 57
2018-05-15 06:00 | 48 | 48 |  |  | 43235.25 | 64 | 62
2018-05-15 06:30 | 51 | 51 |  |  | 43235.2708 | 72 | 71
2018-05-15 07:00 | 55 | 55 |  |  | 43235.2917 | 78 | 77
2018-05-15 07:30 | 58 | 58 |  |  | 43235.3125 | 86 | 83
2018-05-15 08:00 | 57 | 56 |  |  | 43235.3333 | 84 | 82
2018-05-15 08:30 | 53 | 52 |  |  | 43235.3542 | 81 | 78
2018-05-15 09:00 | 54 | 53 |  |  | 43235.375 | 80 | 77
2018-05-15 09:30 | 56 | 56 |  |  | 43235.3958 | 80 | 77
2018-05-15 10:00 | 55 | 55 |  |  | 43235.4167 | 77 | 75
2018-05-15 10:30 | 53 | 53 |  |  | 43235.4375 | 74 | 71
2018-05-15 11:00 | 53 | 53 |  |  | 43235.4583 | 73 | 71
2018-05-15 11:30 | 53 | 53 |  |  | 43235.4792 | 72 | 70
2018-05-15 12:00 | 52 | 52 |  |  | 43235.5 | 72 | 69
2018-05-15 12:30 | 52 | 52 |  |  | 43235.5208 | 72 | 71
2018-05-15 13:00 | 54 | 54 |  |  | 43235.5417 | 73 | 71
2018-05-15 13:30 | 57 | 56 |  |  | 43235.5625 | 75 | 74
2018-05-15 14:00 | 58 | 58 |  |  | 43235.5833 | 77 | 76
2018-05-15 14:30 | 59 | 59 |  |  | 43235.6042 | 78 | 77
2018-05-15 15:00 | 57 | 57 |  |  | 43235.625 | 79 | 77
2018-05-15 15:30 | 56 | 56 |  |  | 43235.6458 | 79 | 76
2018-05-15 16:00 | 58 | 57 |  |  | 43235.6667 | 83 | 79
2018-05-15 16:30 | 61 | 61 |  |  | 43235.6875 | 87 | 82
2018-05-15 17:00 | 66 | 65 |  |  | 43235.7083 | 91 | 86
2018-05-15 17:30 | 68 | 67 |  |  | 43235.7292 | 94 | 89
2018-05-15 18:00 | 67 | 67 |  |  | 43235.75 | 94 | 89
2018-05-15 18:30 | 66 | 65 |  |  | 43235.7708 | 91 | 84
2018-05-15 19:00 | 67 | 66 |  |  | 43235.7917 | 93 | 85
2018-05-15 19:30 | 66 | 65 |  |  | 43235.8125 | 91 | 83
2018-05-15 20:00 | 64 | 63 |  |  | 43235.8333 | 89 | 81
2018-05-15 20:30 | 63 | 62 |  |  | 43235.8542 | 87 | 80
2018-05-15 21:00 | 56 | 56 |  |  | 43235.875 | 78 | 73
2018-05-15 21:30 | 52 | 51 |  |  | 43235.8958 | 72 | 68
2018-05-15 22:00 | 48 | 48 |  |  | 43235.9167 | 71 | 66
2018-05-15 22:30 | 47 | 47 |  |  | 43235.9375 | 68 | 66
2018-05-15 23:00 | 46 | 46 |  |  | 43235.9583 | 65 | 62
2018-05-15 23:30 | 43 | 43 |  |  | 43235.9792 | 62 | 59
2018-05-16 | 38 | 38 |  |  | 43236 | 57 | 53
2018-05-16 00:30 | 35 | 34 |  |  | 43236.0208 | 52 | 47
2018-05-16 01:00 | 33 | 32 |  |  | 43236.0417 | 50 | 44
2018-05-16 01:30 | 32 | 31 |  |  | 43236.0625 | 48 | 42
2018-05-16 02:00 | 32 | 32 |  |  | 43236.0833 | 50 | 43
2018-05-16 02:30 | 32 | 31 |  |  | 43236.1042 | 50 | 43
2018-05-16 03:00 | 34 | 33 |  |  | 43236.125 | 51 | 44
2018-05-16 03:30 | 35 | 34 |  |  | 43236.1458 | 52 | 45
2018-05-16 04:00 | 34 | 33 |  |  | 43236.1667 | 51 | 44
2018-05-16 04:30 | 34 | 33 |  |  | 43236.1875 | 51 | 44
2018-05-16 05:00 | 36 | 36 |  |  | 43236.2083 | 53 | 47
2018-05-16 05:30 | 42 | 42 |  |  | 43236.2292 | 60 | 55
2018-05-16 06:00 | 46 | 46 |  |  | 43236.25 | 64 | 61
2018-05-16 06:30 | 53 | 51 |  |  | 43236.2708 | 81 | 71
2018-05-16 07:00 | 61 | 59 |  |  | 43236.2917 | 91 | 83
2018-05-16 07:30 | 66 | 65 |  |  | 43236.3125 | 96 | 89
2018-05-16 08:00 | 65 | 64 |  |  | 43236.3333 | 95 | 89
2018-05-16 08:30 | 63 | 63 |  |  | 43236.3542 | 92 | 87
2018-05-16 09:00 | 61 | 60 |  |  | 43236.375 | 90 | 84
2018-05-16 09:30 | 59 | 59 |  |  | 43236.3958 | 87 | 81
2018-05-16 10:00 | 59 | 57 |  |  | 43236.4167 | 78 | 78
2018-05-16 10:30 | 58 | 56 |  |  | 43236.4375 | 76 | 76
2018-05-16 11:00 | 57 | 55 |  |  | 43236.4583 | 76 | 76
2018-05-16 11:30 | 58 | 57 |  |  | 43236.4792 | 78 | 78
2018-05-16 12:00 | 60 | 59 |  |  | 43236.5 | 78 | 78
2018-05-16 12:30 | 60 | 59 |  |  | 43236.5208 | 79 | 79
2018-05-16 13:00 | 58 | 56 |  |  | 43236.5417 | 75 | 75
2018-05-16 13:30 | 59 | 58 |  |  | 43236.5625 | 76 | 76
2018-05-16 14:00 | 61 | 59 |  |  | 43236.5833 | 78 | 78
2018-05-16 14:30 | 61 | 59 |  |  | 43236.6042 | 80 | 80
2018-05-16 15:00 | 62 | 61 |  |  | 43236.625 | 82 | 82
2018-05-16 15:30 | 63 | 62 |  |  | 43236.6458 | 82 | 82
2018-05-16 16:00 | 63 | 62 |  |  | 43236.6667 | 83 | 83
2018-05-16 16:30 | 63 | 62 |  |  | 43236.6875 | 85 | 84
2018-05-16 17:00 | 66 | 66 |  |  | 43236.7083 | 87 | 87
2018-05-16 17:30 | 69 | 68 |  |  | 43236.7292 | 89 | 88
2018-05-16 18:00 | 70 | 69 |  |  | 43236.75 | 90 | 90
2018-05-16 18:30 | 69 | 68 |  |  | 43236.7708 | 89 | 88
2018-05-16 19:00 | 70 | 69 |  |  | 43236.7917 | 90 | 89
2018-05-16 19:30 | 69 | 69 |  |  | 43236.8125 | 88 | 86
2018-05-16 20:00 | 67 | 67 |  |  | 43236.8333 | 86 | 85
2018-05-16 20:30 | 67 | 66 |  |  | 43236.8542 | 86 | 85
2018-05-16 21:00 | 64 | 64 |  |  | 43236.875 | 81 | 80
2018-05-16 21:30 | 61 | 61 |  |  | 43236.8958 | 78 | 77
2018-05-16 22:00 | 63 | 60 |  |  | 43236.9167 | 78 | 78
2018-05-16 22:30 | 60 | 58 |  |  | 43236.9375 | 74 | 74
2018-05-16 23:00 | 57 | 55 |  |  | 43236.9583 | 71 | 70
2018-05-16 23:30 | 55 | 53 |  |  | 43236.9792 | 68 | 67
2018-05-17 | 51 | 49 |  |  | 43237 | 64 | 62
2018-05-17 00:30 | 47 | 45 |  |  | 43237.0208 | 59 | 58
2018-05-17 01:00 | 44 | 42 |  |  | 43237.0417 | 56 | 54
2018-05-17 01:30 | 43 | 41 |  |  | 43237.0625 | 54 | 52
2018-05-17 02:00 | 42 | 42 |  |  | 43237.0833 | 55 | 53
2018-05-17 02:30 | 41 | 40 |  |  | 43237.1042 | 55 | 51
2018-05-17 03:00 | 40 | 39 |  |  | 43237.125 | 54 | 50
2018-05-17 03:30 | 41 | 40 |  |  | 43237.1458 | 55 | 51
2018-05-17 04:00 | 40 | 40 |  |  | 43237.1667 | 54 | 50
2018-05-17 04:30 | 41 | 41 |  |  | 43237.1875 | 56 | 51
2018-05-17 05:00 | 44 | 44 |  |  | 43237.2083 | 58 | 54
2018-05-17 05:30 | 47 | 47 |  |  | 43237.2292 | 60 | 58
2018-05-17 06:00 | 51 | 51 |  |  | 43237.25 | 65 | 64
2018-05-17 06:30 | 57 | 57 |  |  | 43237.2708 | 74 | 73
2018-05-17 07:00 | 62 | 62 |  |  | 43237.2917 | 83 | 82
2018-05-17 07:30 | 66 | 66 |  |  | 43237.3125 | 88 | 87
2018-05-17 08:00 | 64 | 63 |  |  | 43237.3333 | 86 | 85
2018-05-17 08:30 | 63 | 62 |  |  | 43237.3542 | 86 | 85
2018-05-17 09:00 | 61 | 61 |  |  | 43237.375 | 83 | 82
2018-05-17 09:30 | 60 | 59 |  |  | 43237.3958 | 81 | 81
2018-05-17 10:00 | 61 | 60 |  |  | 43237.4167 | 80 | 80
2018-05-17 10:30 | 59 | 58 |  |  | 43237.4375 | 77 | 77
2018-05-17 11:00 | 60 | 59 |  |  | 43237.4583 | 79 | 79
2018-05-17 11:30 | 63 | 62 |  |  | 43237.4792 | 82 | 82
2018-05-17 12:00 | 65 | 64 |  |  | 43237.5 | 84 | 84
2018-05-17 12:30 | 66 | 65 |  |  | 43237.5208 | 87 | 87
2018-05-17 13:00 | 66 | 66 |  |  | 43237.5417 | 88 | 87
2018-05-17 13:30 | 69 | 68 |  |  | 43237.5625 | 92 | 92
2018-05-17 14:00 | 66 | 66 |  |  | 43237.5833 | 89 | 88
2018-05-17 14:30 | 65 | 64 |  |  | 43237.6042 | 84 | 84
2018-05-17 15:00 | 64 | 63 |  |  | 43237.625 | 84 | 83
2018-05-17 15:30 | 63 | 62 |  |  | 43237.6458 | 84 | 83
2018-05-17 16:00 | 65 | 65 |  |  | 43237.6667 | 87 | 86
2018-05-17 16:30 | 68 | 68 |  |  | 43237.6875 | 89 | 88
2018-05-17 17:00 | 71 | 71 |  |  | 43237.7083 | 91 | 90
2018-05-17 17:30 | 73 | 73 |  |  | 43237.7292 | 95 | 93
2018-05-17 18:00 | 74 | 74 |  |  | 43237.75 | 95 | 94
2018-05-17 18:30 | 69 | 69 |  |  | 43237.7708 | 92 | 90
2018-05-17 19:00 | 70 | 70 |  |  | 43237.7917 | 92 | 90
2018-05-17 19:30 | 67 | 67 |  |  | 43237.8125 | 89 | 87
2018-05-17 20:00 | 66 | 66 |  |  | 43237.8333 | 86 | 85
2018-05-17 20:30 | 65 | 64 |  |  | 43237.8542 | 86 | 85
2018-05-17 21:00 | 63 | 63 |  |  | 43237.875 | 81 | 81
2018-05-17 21:30 | 58 | 57 |  |  | 43237.8958 | 74 | 73
2018-05-17 22:00 | 55 | 55 |  |  | 43237.9167 | 74 | 73
2018-05-17 22:30 | 53 | 53 |  |  | 43237.9375 | 71 | 70
2018-05-17 23:00 | 52 | 51 |  |  | 43237.9583 | 69 | 67
2018-05-17 23:30 | 48 | 48 |  |  | 43237.9792 | 65 | 63
2018-05-18 | 43 | 43 |  |  | 43238 | 59 | 58
2018-05-18 00:30 | 39 | 39 |  |  | 43238.0208 | 55 | 52
2018-05-18 01:00 | 36 | 36 |  |  | 43238.0417 | 51 | 48
2018-05-18 01:30 | 35 | 35 |  |  | 43238.0625 | 49 | 45
2018-05-18 02:00 | 34 | 34 |  |  | 43238.0833 | 49 | 45
2018-05-18 02:30 | 35 | 35 |  |  | 43238.1042 | 49 | 45
2018-05-18 03:00 | 35 | 35 |  |  | 43238.125 | 50 | 45
2018-05-18 03:30 | 35 | 35 |  |  | 43238.1458 | 50 | 45
2018-05-18 04:00 | 35 | 35 |  |  | 43238.1667 | 49 | 45
2018-05-18 04:30 | 36 | 35 |  |  | 43238.1875 | 50 | 45
2018-05-18 05:00 | 36 | 36 |  |  | 43238.2083 | 50 | 46
2018-05-18 05:30 | 40 | 40 |  |  | 43238.2292 | 55 | 52
2018-05-18 06:00 | 46 | 46 |  |  | 43238.25 | 63 | 60
2018-05-18 06:30 | 54 | 54 |  |  | 43238.2708 | 75 | 72
2018-05-18 07:00 | 57 | 57 |  |  | 43238.2917 | 82 | 79
2018-05-18 07:30 | 63 | 63 |  |  | 43238.3125 | 90 | 88
2018-05-18 08:00 | 61 | 61 |  |  | 43238.3333 | 87 | 86
2018-05-18 08:30 | 58 | 58 |  |  | 43238.3542 | 85 | 83
2018-05-18 09:00 | 56 | 56 |  |  | 43238.375 | 81 | 79
2018-05-18 09:30 | 54 | 54 |  |  | 43238.3958 | 78 | 77
2018-05-18 10:00 | 52 | 52 |  |  | 43238.4167 | 75 | 74
2018-05-18 10:30 | 51 | 51 |  |  | 43238.4375 | 73 | 72
2018-05-18 11:00 | 51 | 51 |  |  | 43238.4583 | 72 | 71
2018-05-18 11:30 | 53 | 51 |  |  | 43238.4792 | 70 | 70
2018-05-18 12:00 | 52 | 50 |  |  | 43238.5 | 70 | 70
2018-05-18 12:30 | 53 | 51 |  |  | 43238.5208 | 72 | 72
2018-05-18 13:00 | 53 | 52 |  |  | 43238.5417 | 72 | 72
2018-05-18 13:30 | 55 | 54 |  |  | 43238.5625 | 73 | 73
2018-05-18 14:00 | 57 | 56 |  |  | 43238.5833 | 74 | 74
2018-05-18 14:30 | 57 | 56 |  |  | 43238.6042 | 75 | 75
2018-05-18 15:00 | 59 | 57 |  |  | 43238.625 | 77 | 77
2018-05-18 15:30 | 59 | 58 |  |  | 43238.6458 | 78 | 78
2018-05-18 16:00 | 63 | 62 |  |  | 43238.6667 | 83 | 83
2018-05-18 16:30 | 65 | 64 |  |  | 43238.6875 | 85 | 85
2018-05-18 17:00 | 67 | 66 |  |  | 43238.7083 | 87 | 87
2018-05-18 17:30 | 67 | 67 |  |  | 43238.7292 | 88 | 88
2018-05-18 18:00 | 66 | 66 |  |  | 43238.75 | 88 | 87
2018-05-18 18:30 | 63 | 63 |  |  | 43238.7708 | 84 | 83
2018-05-18 19:00 | 63 | 63 |  |  | 43238.7917 | 85 | 84
2018-05-18 19:30 | 62 | 62 |  |  | 43238.8125 | 83 | 82
2018-05-18 20:00 | 61 | 60 |  |  | 43238.8333 | 81 | 80
2018-05-18 20:30 | 56 | 56 |  |  | 43238.8542 | 78 | 77
2018-05-18 21:00 | 52 | 51 |  |  | 43238.875 | 73 | 72
2018-05-18 21:30 | 51 | 51 |  |  | 43238.8958 | 70 | 68
2018-05-18 22:00 | 50 | 50 |  |  | 43238.9167 | 70 | 68
2018-05-18 22:30 | 48 | 48 |  |  | 43238.9375 | 68 | 66
2018-05-18 23:00 | 49 | 49 |  |  | 43238.9583 | 67 | 64
2018-05-18 23:30 | 45 | 45 |  |  | 43238.9792 | 64 | 61
2018-05-19 | 41 | 41 |  |  | 43239 | 60 | 57
2018-05-19 00:30 | 37 | 36 |  |  | 43239.0208 | 55 | 51
2018-05-19 01:00 | 33 | 33 |  |  | 43239.0417 | 49 | 45
2018-05-19 01:30 | 31 | 31 |  |  | 43239.0625 | 47 | 43
2018-05-19 02:00 | 31 | 31 |  |  | 43239.0833 | 46 | 42
2018-05-19 02:30 | 31 | 31 |  |  | 43239.1042 | 45 | 41
2018-05-19 03:00 | 31 | 30 |  |  | 43239.125 | 45 | 42
2018-05-19 03:30 | 30 | 30 |  |  | 43239.1458 | 44 | 42
2018-05-19 04:00 | 30 | 30 |  |  | 43239.1667 | 44 | 42
2018-05-19 04:30 | 30 | 30 |  |  | 43239.1875 | 44 | 42
2018-05-19 05:00 | 32 | 32 |  |  | 43239.2083 | 46 | 44
2018-05-19 05:30 | 32 | 32 |  |  | 43239.2292 | 46 | 44
2018-05-19 06:00 | 33 | 33 |  |  | 43239.25 | 48 | 46
2018-05-19 06:30 | 35 | 35 |  |  | 43239.2708 | 50 | 49
2018-05-19 07:00 | 38 | 38 |  |  | 43239.2917 | 54 | 52
2018-05-19 07:30 | 38 | 37 |  |  | 43239.3125 | 55 | 54
2018-05-19 08:00 | 37 | 37 |  |  | 43239.3333 | 55 | 54
2018-05-19 08:30 | 38 | 38 |  |  | 43239.3542 | 56 | 55
2018-05-19 09:00 | 37 | 37 |  |  | 43239.375 | 55 | 54
2018-05-19 09:30 | 36 | 36 |  |  | 43239.3958 | 54 | 53
2018-05-19 10:00 | 35 | 35 |  |  | 43239.4167 | 53 | 51
2018-05-19 10:30 | 35 | 35 |  |  | 43239.4375 | 52 | 50
2018-05-19 11:00 | 35 | 35 |  |  | 43239.4583 | 50 | 49
2018-05-19 11:30 | 34 | 34 |  |  | 43239.4792 | 50 | 48
2018-05-19 12:00 | 33 | 33 |  |  | 43239.5 | 49 | 48
2018-05-19 12:30 | 34 | 34 |  |  | 43239.5208 | 50 | 48
2018-05-19 13:00 | 34 | 34 |  |  | 43239.5417 | 50 | 49
2018-05-19 13:30 | 36 | 36 |  |  | 43239.5625 | 52 | 50
2018-05-19 14:00 | 37 | 37 |  |  | 43239.5833 | 52 | 51
2018-05-19 14:30 | 38 | 38 |  |  | 43239.6042 | 54 | 53
2018-05-19 15:00 | 41 | 41 |  |  | 43239.625 | 58 | 56
2018-05-19 15:30 | 43 | 43 |  |  | 43239.6458 | 60 | 58
2018-05-19 16:00 | 44 | 44 |  |  | 43239.6667 | 62 | 61
2018-05-19 16:30 | 47 | 47 |  |  | 43239.6875 | 65 | 64
2018-05-19 17:00 | 51 | 50 |  |  | 43239.7083 | 69 | 68
2018-05-19 17:30 | 53 | 53 |  |  | 43239.7292 | 72 | 71
2018-05-19 18:00 | 52 | 52 |  |  | 43239.75 | 73 | 72
2018-05-19 18:30 | 53 | 53 |  |  | 43239.7708 | 73 | 72
2018-05-19 19:00 | 53 | 53 |  |  | 43239.7917 | 74 | 73
2018-05-19 19:30 | 53 | 53 |  |  | 43239.8125 | 73 | 71
2018-05-19 20:00 | 51 | 51 |  |  | 43239.8333 | 71 | 70
2018-05-19 20:30 | 51 | 51 |  |  | 43239.8542 | 70 | 69
2018-05-19 21:00 | 47 | 47 |  |  | 43239.875 | 65 | 64
2018-05-19 21:30 | 42 | 42 |  |  | 43239.8958 | 62 | 60
2018-05-19 22:00 | 42 | 42 |  |  | 43239.9167 | 61 | 59
2018-05-19 22:30 | 44 | 44 |  |  | 43239.9375 | 64 | 63
2018-05-19 23:00 | 47 | 47 |  |  | 43239.9583 | 64 | 62
2018-05-19 23:30 | 44 | 44 |  |  | 43239.9792 | 63 | 60
2018-05-20 | 40 | 40 |  |  | 43240 | 58 | 56
2018-05-20 00:30 | 37 | 37 |  |  | 43240.0208 | 54 | 51
2018-05-20 01:00 | 37 | 37 |  |  | 43240.0417 | 53 | 50
2018-05-20 01:30 | 35 | 34 |  |  | 43240.0625 | 51 | 46
2018-05-20 02:00 | 35 | 34 |  |  | 43240.0833 | 50 | 45
2018-05-20 02:30 | 34 | 34 |  |  | 43240.1042 | 49 | 45
2018-05-20 03:00 | 34 | 34 |  |  | 43240.125 | 49 | 44
2018-05-20 03:30 | 34 | 34 |  |  | 43240.1458 | 48 | 43
2018-05-20 04:00 | 34 | 33 |  |  | 43240.1667 | 48 | 43
2018-05-20 04:30 | 35 | 34 |  |  | 43240.1875 | 50 | 45
2018-05-20 05:00 | 37 | 37 |  |  | 43240.2083 | 52 | 48
2018-05-20 05:30 | 39 | 38 |  |  | 43240.2292 | 53 | 49
2018-05-20 06:00 | 39 | 39 |  |  | 43240.25 | 54 | 49
2018-05-20 06:30 | 38 | 37 |  |  | 43240.2708 | 54 | 50
2018-05-20 07:00 | 39 | 38 |  |  | 43240.2917 | 56 | 51
2018-05-20 07:30 | 38 | 37 |  |  | 43240.3125 | 55 | 50
2018-05-20 08:00 | 36 | 35 |  |  | 43240.3333 | 54 | 49
2018-05-20 08:30 | 35 | 35 |  |  | 43240.3542 | 53 | 49
2018-05-20 09:00 | 34 | 34 |  |  | 43240.375 | 53 | 49
2018-05-20 09:30 | 34 | 34 |  |  | 43240.3958 | 52 | 49
2018-05-20 10:00 | 34 | 34 |  |  | 43240.4167 | 51 | 48
2018-05-20 10:30 | 33 | 33 |  |  | 43240.4375 | 51 | 48
2018-05-20 11:00 | 34 | 34 |  |  | 43240.4583 | 51 | 48
2018-05-20 11:30 | 34 | 34 |  |  | 43240.4792 | 50 | 48
2018-05-20 12:00 | 35 | 35 |  |  | 43240.5 | 51 | 48
2018-05-20 12:30 | 35 | 35 |  |  | 43240.5208 | 50 | 47
2018-05-20 13:00 | 33 | 32 |  |  | 43240.5417 | 48 | 46
2018-05-20 13:30 | 33 | 33 |  |  | 43240.5625 | 49 | 46
2018-05-20 14:00 | 34 | 34 |  |  | 43240.5833 | 49 | 47
2018-05-20 14:30 | 37 | 37 |  |  | 43240.6042 | 52 | 50
2018-05-20 15:00 | 41 | 41 |  |  | 43240.625 | 55 | 53
2018-05-20 15:30 | 43 | 43 |  |  | 43240.6458 | 59 | 56
2018-05-20 16:00 | 44 | 44 |  |  | 43240.6667 | 61 | 59
2018-05-20 16:30 | 45 | 45 |  |  | 43240.6875 | 63 | 61
2018-05-20 17:00 | 48 | 48 |  |  | 43240.7083 | 66 | 65
2018-05-20 17:30 | 51 | 51 |  |  | 43240.7292 | 70 | 69
2018-05-20 18:00 | 55 | 55 |  |  | 43240.75 | 74 | 72
2018-05-20 18:30 | 53 | 53 |  |  | 43240.7708 | 73 | 71
2018-05-20 19:00 | 53 | 53 |  |  | 43240.7917 | 73 | 71
2018-05-20 19:30 | 53 | 53 |  |  | 43240.8125 | 72 | 71
2018-05-20 20:00 | 51 | 51 |  |  | 43240.8333 | 70 | 69
2018-05-20 20:30 | 50 | 50 |  |  | 43240.8542 | 69 | 68
2018-05-20 21:00 | 48 | 47 |  |  | 43240.875 | 67 | 66
2018-05-20 21:30 | 45 | 45 |  |  | 43240.8958 | 64 | 62
2018-05-20 22:00 | 45 | 45 |  |  | 43240.9167 | 65 | 63
2018-05-20 22:30 | 49 | 49 |  |  | 43240.9375 | 67 | 65
2018-05-20 23:00 | 49 | 49 |  |  | 43240.9583 | 66 | 64
2018-05-20 23:30 | 47 | 47 |  |  | 43240.9792 | 63 | 61
2018-05-21 | 42 | 42 |  |  | 43241 | 58 | 55
2018-05-21 00:30 | 38 | 38 |  |  | 43241.0208 | 53 | 50
2018-05-21 01:00 | 35 | 35 |  |  | 43241.0417 | 51 | 47
2018-05-21 01:30 | 35 | 34 |  |  | 43241.0625 | 50 | 45
2018-05-21 02:00 | 33 | 32 |  |  | 43241.0833 | 48 | 43
2018-05-21 02:30 | 33 | 33 |  |  | 43241.1042 | 48 | 43
2018-05-21 03:00 | 34 | 34 |  |  | 43241.125 | 52 | 45
2018-05-21 03:30 | 35 | 35 |  |  | 43241.1458 | 56 | 46
2018-05-21 04:00 | 37 | 37 |  |  | 43241.1667 | 57 | 47
2018-05-21 04:30 | 42 | 41 |  |  | 43241.1875 | 60 | 51
2018-05-21 05:00 | 44 | 44 |  |  | 43241.2083 | 62 | 53
2018-05-21 05:30 | 46 | 45 |  |  | 43241.2292 | 64 | 56
2018-05-21 06:00 | 50 | 48 |  |  | 43241.25 | 66 | 60
2018-05-21 06:30 | 53 | 51 |  |  | 43241.2708 | 71 | 68
2018-05-21 07:00 | 55 | 54 |  |  | 43241.2917 | 79 | 74
2018-05-21 07:30 | 59 | 58 |  |  | 43241.3125 | 86 | 81
2018-05-21 08:00 | 56 | 56 |  |  | 43241.3333 | 84 | 79
2018-05-21 08:30 | 52 | 51 |  |  | 43241.3542 | 80 | 76
2018-05-21 09:00 | 48 | 47 |  |  | 43241.375 | 75 | 71
2018-05-21 09:30 | 46 | 45 |  |  | 43241.3958 | 71 | 66
2018-05-21 10:00 | 46 | 44 |  |  | 43241.4167 | 70 | 65
2018-05-21 10:30 | 46 | 44 |  |  | 43241.4375 | 69 | 64
2018-05-21 11:00 | 46 | 44 |  |  | 43241.4583 | 69 | 64
2018-05-21 11:30 | 46 | 45 |  |  | 43241.4792 | 69 | 65
2018-05-21 12:00 | 49 | 47 |  |  | 43241.5 | 71 | 67
2018-05-21 12:30 | 50 | 47 |  |  | 43241.5208 | 72 | 68
2018-05-21 13:00 | 51 | 48 |  |  | 43241.5417 | 71 | 68
2018-05-21 13:30 | 54 | 51 |  |  | 43241.5625 | 73 | 70
2018-05-21 14:00 | 56 | 53 |  |  | 43241.5833 | 74 | 71
2018-05-21 14:30 | 57 | 54 |  |  | 43241.6042 | 75 | 72
2018-05-21 15:00 | 58 | 55 |  |  | 43241.625 | 77 | 75
2018-05-21 15:30 | 57 | 55 |  |  | 43241.6458 | 80 | 76
2018-05-21 16:00 | 59 | 57 |  |  | 43241.6667 | 83 | 80
2018-05-21 16:30 | 60 | 58 |  |  | 43241.6875 | 84 | 81
2018-05-21 17:00 | 61 | 59 |  |  | 43241.7083 | 87 | 83
2018-05-21 17:30 | 61 | 60 |  |  | 43241.7292 | 88 | 84
2018-05-21 18:00 | 61 | 60 |  |  | 43241.75 | 88 | 84
2018-05-21 18:30 | 58 | 57 |  |  | 43241.7708 | 86 | 81
2018-05-21 19:00 | 60 | 59 |  |  | 43241.7917 | 86 | 81
2018-05-21 19:30 | 62 | 60 |  |  | 43241.8125 | 82 | 81
2018-05-21 20:00 | 59 | 58 |  |  | 43241.8333 | 80 | 80
2018-05-21 20:30 | 58 | 57 |  |  | 43241.8542 | 78 | 78
2018-05-21 21:00 | 54 | 53 |  |  | 43241.875 | 74 | 74
2018-05-21 21:30 | 52 | 50 |  |  | 43241.8958 | 70 | 70
2018-05-21 22:00 | 49 | 48 |  |  | 43241.9167 | 68 | 68
2018-05-21 22:30 | 50 | 49 |  |  | 43241.9375 | 68 | 68
2018-05-21 23:00 | 49 | 47 |  |  | 43241.9583 | 64 | 64
2018-05-21 23:30 | 48 | 46 |  |  | 43241.9792 | 62 | 62
2018-05-22 | 43 | 41 |  |  | 43242 | 56 | 56
2018-05-22 00:30 | 41 | 38 |  |  | 43242.0208 | 52 | 52
2018-05-22 01:00 | 38 | 35 |  |  | 43242.0417 | 49 | 48
2018-05-22 01:30 | 38 | 35 |  |  | 43242.0625 | 48 | 47
2018-05-22 02:00 | 41 | 37 |  |  | 43242.0833 | 50 | 49
2018-05-22 02:30 | 47 | 37 |  |  | 43242.1042 | 51 | 49
2018-05-22 03:00 | 50 | 37 |  |  | 43242.125 | 52 | 48
2018-05-22 03:30 | 50 | 37 |  |  | 43242.1458 | 51 | 48
2018-05-22 04:00 | 50 | 37 |  |  | 43242.1667 | 51 | 48
2018-05-22 04:30 | 52 | 39 |  |  | 43242.1875 | 53 | 50
2018-05-22 05:00 | 52 | 40 |  |  | 43242.2083 | 55 | 52
2018-05-22 05:30 | 55 | 46 |  |  | 43242.2292 | 60 | 58
2018-05-22 06:00 | 58 | 51 |  |  | 43242.25 | 65 | 64
2018-05-22 06:30 | 63 | 57 |  |  | 43242.2708 | 74 | 74
2018-05-22 07:00 | 64 | 61 |  |  | 43242.2917 | 81 | 81
2018-05-22 07:30 | 66 | 62 |  |  | 43242.3125 | 86 | 85
2018-05-22 08:00 | 63 | 58 |  |  | 43242.3333 | 84 | 83
2018-05-22 08:30 | 57 | 52 |  |  | 43242.3542 | 79 | 78
2018-05-22 09:00 | 56 | 49 |  |  | 43242.375 | 77 | 76
2018-05-22 09:30 | 53 | 46 |  |  | 43242.3958 | 73 | 72
2018-05-22 10:00 | 51 | 43 |  |  | 43242.4167 | 71 | 70
2018-05-22 10:30 | 51 | 41 |  |  | 43242.4375 | 69 | 68
2018-05-22 11:00 | 50 | 41 |  |  | 43242.4583 | 67 | 66
2018-05-22 11:30 | 50 | 40 |  |  | 43242.4792 | 67 | 65
2018-05-22 12:00 | 50 | 41 |  |  | 43242.5 | 67 | 66
2018-05-22 12:30 | 50 | 41 |  |  | 43242.5208 | 68 | 66
2018-05-22 13:00 | 50 | 42 |  |  | 43242.5417 | 69 | 67
2018-05-22 13:30 | 52 | 44 |  |  | 43242.5625 | 70 | 69
2018-05-22 14:00 | 52 | 48 |  |  | 43242.5833 | 73 | 72
2018-05-22 14:30 | 52 | 50 |  |  | 43242.6042 | 76 | 76
2018-05-22 15:00 | 53 | 51 |  |  | 43242.625 | 77 | 77
2018-05-22 15:30 | 54 | 52 |  |  | 43242.6458 | 79 | 79
2018-05-22 16:00 | 56 | 54 |  |  | 43242.6667 | 82 | 81
2018-05-22 16:30 | 55 | 55 |  |  | 43242.6875 | 83 | 83
2018-05-22 17:00 | 59 | 59 |  |  | 43242.7083 | 88 | 88
2018-05-22 17:30 | 61 | 61 |  |  | 43242.7292 | 89 | 89
2018-05-22 18:00 | 62 | 62 |  |  | 43242.75 | 89 | 89
2018-05-22 18:30 | 60 | 60 |  |  | 43242.7708 | 85 | 85
2018-05-22 19:00 | 62 | 62 |  |  | 43242.7917 | 87 | 87
2018-05-22 19:30 | 61 | 61 |  |  | 43242.8125 | 83 | 83
2018-05-22 20:00 | 60 | 60 |  |  | 43242.8333 | 81 | 81
2018-05-22 20:30 | 59 | 59 |  |  | 43242.8542 | 81 | 81
2018-05-22 21:00 | 57 | 57 |  |  | 43242.875 | 77 | 77
2018-05-22 21:30 | 53 | 53 |  |  | 43242.8958 | 73 | 73
2018-05-22 22:00 | 52 | 52 |  |  | 43242.9167 | 72 | 72
2018-05-22 22:30 | 50 | 50 |  |  | 43242.9375 | 71 | 71
2018-05-22 23:00 | 48 | 48 |  |  | 43242.9583 | 66 | 66
2018-05-22 23:30 | 44 | 44 |  |  | 43242.9792 | 63 | 63
2018-05-23 | 42 | 41 |  |  | 43243 | 58 | 58
2018-05-23 00:30 | 39 | 37 |  |  | 43243.0208 | 52 | 51
2018-05-23 01:00 | 38 | 34 |  |  | 43243.0417 | 48 | 47
2018-05-23 01:30 | 36 | 32 |  |  | 43243.0625 | 46 | 45
2018-05-23 02:00 | 35 | 31 |  |  | 43243.0833 | 44 | 43
2018-05-23 02:30 | 36 | 32 |  |  | 43243.1042 | 45 | 44
2018-05-23 03:00 | 34 | 30 |  |  | 43243.125 | 43 | 42
2018-05-23 03:30 | 35 | 31 |  |  | 43243.1458 | 44 | 43
2018-05-23 04:00 | 36 | 32 |  |  | 43243.1667 | 45 | 44
2018-05-23 04:30 | 38 | 35 |  |  | 43243.1875 | 48 | 47
2018-05-23 05:00 | 42 | 40 |  |  | 43243.2083 | 52 | 51
2018-05-23 05:30 | 46 | 43 |  |  | 43243.2292 | 56 | 56
2018-05-23 06:00 | 52 | 50 |  |  | 43243.25 | 65 | 64
2018-05-23 06:30 | 60 | 58 |  |  | 43243.2708 | 78 | 77
2018-05-23 07:00 | 64 | 62 |  |  | 43243.2917 | 84 | 84
2018-05-23 07:30 | 69 | 67 |  |  | 43243.3125 | 91 | 91
2018-05-23 08:00 | 66 | 63 |  |  | 43243.3333 | 90 | 89
2018-05-23 08:30 | 65 | 64 |  |  | 43243.3542 | 88 | 87
2018-05-23 09:00 | 63 | 61 |  |  | 43243.375 | 85 | 84
2018-05-23 09:30 | 61 | 60 |  |  | 43243.3958 | 82 | 81
2018-05-23 10:00 | 59 | 58 |  |  | 43243.4167 | 80 | 79
2018-05-23 10:30 | 59 | 58 |  |  | 43243.4375 | 79 | 78
2018-05-23 11:00 | 58 | 57 |  |  | 43243.4583 | 79 | 78
2018-05-23 11:30 | 60 | 59 |  |  | 43243.4792 | 80 | 80
2018-05-23 12:00 | 60 | 59 |  |  | 43243.5 | 80 | 79
2018-05-23 12:30 | 63 | 62 |  |  | 43243.5208 | 83 | 82
2018-05-23 13:00 | 62 | 61 |  |  | 43243.5417 | 83 | 83
2018-05-23 13:30 | 62 | 62 |  |  | 43243.5625 | 85 | 85
2018-05-23 14:00 | 61 | 61 |  |  | 43243.5833 | 83 | 83
2018-05-23 14:30 | 63 | 62 |  |  | 43243.6042 | 82 | 82
2018-05-23 15:00 | 60 | 60 |  |  | 43243.625 | 81 | 81
2018-05-23 15:30 | 57 | 56 |  |  | 43243.6458 | 79 | 79
2018-05-23 16:00 | 59 | 59 |  |  | 43243.6667 | 83 | 83
2018-05-23 16:30 | 61 | 60 |  |  | 43243.6875 | 85 | 85
2018-05-23 17:00 | 64 | 63 |  |  | 43243.7083 | 87 | 86
2018-05-23 17:30 | 66 | 65 |  |  | 43243.7292 | 89 | 88
2018-05-23 18:00 | 67 | 66 |  |  | 43243.75 | 90 | 88
2018-05-23 18:30 | 65 | 63 |  |  | 43243.7708 | 87 | 85
2018-05-23 19:00 | 67 | 65 |  |  | 43243.7917 | 88 | 86
2018-05-23 19:30 | 65 | 64 |  |  | 43243.8125 | 86 | 85
2018-05-23 20:00 | 65 | 64 |  |  | 43243.8333 | 84 | 82
2018-05-23 20:30 | 64 | 62 |  |  | 43243.8542 | 82 | 81
2018-05-23 21:00 | 59 | 58 |  |  | 43243.875 | 78 | 77
2018-05-23 21:30 | 54 | 53 |  |  | 43243.8958 | 72 | 71
2018-05-23 22:00 | 53 | 52 |  |  | 43243.9167 | 71 | 70
2018-05-23 22:30 | 49 | 48 |  |  | 43243.9375 | 68 | 68
2018-05-23 23:00 | 49 | 49 |  |  | 43243.9583 | 66 | 65
2018-05-23 23:30 | 46 | 45 |  |  | 43243.9792 | 62 | 61
2018-05-24 | 42 | 41 |  |  | 43244 | 57 | 57
2018-05-24 00:30 | 38 | 37 |  |  | 43244.0208 | 51 | 51
2018-05-24 01:00 | 35 | 34 |  |  | 43244.0417 | 48 | 47
2018-05-24 01:30 | 34 | 33 |  |  | 43244.0625 | 46 | 45
2018-05-24 02:00 | 34 | 32 |  |  | 43244.0833 | 46 | 45
2018-05-24 02:30 | 34 | 32 |  |  | 43244.1042 | 45 | 45
2018-05-24 03:00 | 37 | 33 |  |  | 43244.125 | 46 | 45
2018-05-24 03:30 | 39 | 35 |  |  | 43244.1458 | 47 | 45
2018-05-24 04:00 | 38 | 35 |  |  | 43244.1667 | 47 | 45
2018-05-24 04:30 | 41 | 37 |  |  | 43244.1875 | 50 | 49
2018-05-24 05:00 | 43 | 41 |  |  | 43244.2083 | 53 | 52
2018-05-24 05:30 | 47 | 45 |  |  | 43244.2292 | 58 | 57
2018-05-24 06:00 | 50 | 48 |  |  | 43244.25 | 62 | 62
2018-05-24 06:30 | 59 | 55 |  |  | 43244.2708 | 79 | 74
2018-05-24 07:00 | 64 | 59 |  |  | 43244.2917 | 88 | 83
2018-05-24 07:30 | 68 | 64 |  |  | 43244.3125 | 95 | 90
2018-05-24 08:00 | 66 | 62 |  |  | 43244.3333 | 93 | 89
2018-05-24 08:30 | 61 | 57 |  |  | 43244.3542 | 89 | 85
2018-05-24 09:00 | 57 | 54 |  |  | 43244.375 | 85 | 81
2018-05-24 09:30 | 53 | 50 |  |  | 43244.3958 | 82 | 78
2018-05-24 10:00 | 52 | 51 |  |  | 43244.4167 | 77 | 76
2018-05-24 10:30 | 51 | 51 |  |  | 43244.4375 | 75 | 75
2018-05-24 11:00 | 50 | 50 |  |  | 43244.4583 | 73 | 73
2018-05-24 11:30 | 50 | 50 |  |  | 43244.4792 | 74 | 74
2018-05-24 12:00 | 53 | 52 |  |  | 43244.5 | 76 | 75
2018-05-24 12:30 | 50 | 50 |  |  | 43244.5208 | 78 | 77
2018-05-24 13:00 | 56 | 56 |  |  | 43244.5417 | 81 | 81
2018-05-24 13:30 | 56 | 56 |  |  | 43244.5625 | 83 | 83
2018-05-24 14:00 | 59 | 58 |  |  | 43244.5833 | 82 | 82
2018-05-24 14:30 | 59 | 59 |  |  | 43244.6042 | 82 | 82
2018-05-24 15:00 | 54 | 54 |  |  | 43244.625 | 80 | 79
2018-05-24 15:30 | 55 | 54 |  |  | 43244.6458 | 79 | 79
2018-05-24 16:00 | 57 | 56 |  |  | 43244.6667 | 83 | 82
2018-05-24 16:30 | 61 | 60 |  |  | 43244.6875 | 86 | 85
2018-05-24 17:00 | 62 | 61 |  |  | 43244.7083 | 87 | 86
2018-05-24 17:30 | 63 | 62 |  |  | 43244.7292 | 88 | 86
2018-05-24 18:00 | 64 | 63 |  |  | 43244.75 | 88 | 87
2018-05-24 18:30 | 64 | 63 |  |  | 43244.7708 | 88 | 86
2018-05-24 19:00 | 67 | 65 |  |  | 43244.7917 | 89 | 87
2018-05-24 19:30 | 67 | 66 |  |  | 43244.8125 | 88 | 87
2018-05-24 20:00 | 66 | 65 |  |  | 43244.8333 | 85 | 84
2018-05-24 20:30 | 65 | 64 |  |  | 43244.8542 | 84 | 83
2018-05-24 21:00 | 62 | 61 |  |  | 43244.875 | 80 | 79
2018-05-24 21:30 | 59 | 57 |  |  | 43244.8958 | 76 | 74
2018-05-24 22:00 | 54 | 52 |  |  | 43244.9167 | 73 | 73
2018-05-24 22:30 | 53 | 52 |  |  | 43244.9375 | 73 | 73
2018-05-24 23:00 | 54 | 53 |  |  | 43244.9583 | 69 | 69
2018-05-24 23:30 | 49 | 47 |  |  | 43244.9792 | 65 | 64
2018-05-25 | 45 | 43 |  |  | 43245 | 59 | 59
2018-05-25 00:30 | 40 | 38 |  |  | 43245.0208 | 53 | 53
2018-05-25 01:00 | 39 | 37 |  |  | 43245.0417 | 50 | 50
2018-05-25 01:30 | 38 | 36 |  |  | 43245.0625 | 48 | 47
2018-05-25 02:00 | 38 | 35 |  |  | 43245.0833 | 48 | 47
2018-05-25 02:30 | 38 | 35 |  |  | 43245.1042 | 48 | 47
2018-05-25 03:00 | 39 | 35 |  |  | 43245.125 | 48 | 47
2018-05-25 03:30 | 40 | 37 |  |  | 43245.1458 | 49 | 48
2018-05-25 04:00 | 40 | 36 |  |  | 43245.1667 | 49 | 48
2018-05-25 04:30 | 41 | 38 |  |  | 43245.1875 | 51 | 50
2018-05-25 05:00 | 44 | 41 |  |  | 43245.2083 | 54 | 53
2018-05-25 05:30 | 48 | 46 |  |  | 43245.2292 | 58 | 58
2018-05-25 06:00 | 51 | 50 |  |  | 43245.25 | 64 | 64
2018-05-25 06:30 | 56 | 55 |  |  | 43245.2708 | 73 | 72
2018-05-25 07:00 | 61 | 60 |  |  | 43245.2917 | 80 | 80
2018-05-25 07:30 | 63 | 62 |  |  | 43245.3125 | 84 | 84
2018-05-25 08:00 | 63 | 62 |  |  | 43245.3333 | 86 | 86
2018-05-25 08:30 | 62 | 61 |  |  | 43245.3542 | 87 | 87
2018-05-25 09:00 | 60 | 59 |  |  | 43245.375 | 85 | 85
2018-05-25 09:30 | 58 | 57 |  |  | 43245.3958 | 82 | 82
2018-05-25 10:00 | 55 | 54 |  |  | 43245.4167 | 80 | 80
2018-05-25 10:30 | 58 | 57 |  |  | 43245.4375 | 79 | 79
2018-05-25 11:00 | 57 | 56 |  |  | 43245.4583 | 80 | 80
2018-05-25 11:30 | 53 | 52 |  |  | 43245.4792 | 77 | 77
2018-05-25 12:00 | 56 | 55 |  |  | 43245.5 | 79 | 79
2018-05-25 12:30 | 54 | 53 |  |  | 43245.5208 | 77 | 77
2018-05-25 13:00 | 52 | 52 |  |  | 43245.5417 | 75 | 75
2018-05-25 13:30 | 51 | 50 |  |  | 43245.5625 | 75 | 75
2018-05-25 14:00 | 54 | 53 |  |  | 43245.5833 | 77 | 77
2018-05-25 14:30 | 54 | 54 |  |  | 43245.6042 | 76 | 76
2018-05-25 15:00 | 56 | 55 |  |  | 43245.625 | 77 | 77
2018-05-25 15:30 | 57 | 56 |  |  | 43245.6458 | 77 | 77
2018-05-25 16:00 | 58 | 57 |  |  | 43245.6667 | 80 | 80
2018-05-25 16:30 | 60 | 59 |  |  | 43245.6875 | 83 | 83
2018-05-25 17:00 | 62 | 61 |  |  | 43245.7083 | 84 | 84
2018-05-25 17:30 | 65 | 63 |  |  | 43245.7292 | 87 | 87
2018-05-25 18:00 | 63 | 62 |  |  | 43245.75 | 86 | 85
2018-05-25 18:30 | 63 | 61 |  |  | 43245.7708 | 83 | 83
2018-05-25 19:00 | 64 | 62 |  |  | 43245.7917 | 84 | 83
2018-05-25 19:30 | 63 | 62 |  |  | 43245.8125 | 82 | 82
2018-05-25 20:00 | 60 | 58 |  |  | 43245.8333 | 78 | 78
2018-05-25 20:30 | 58 | 56 |  |  | 43245.8542 | 77 | 77
2018-05-25 21:00 | 57 | 55 |  |  | 43245.875 | 74 | 74
2018-05-25 21:30 | 54 | 52 |  |  | 43245.8958 | 71 | 71
2018-05-25 22:00 | 53 | 52 |  |  | 43245.9167 | 70 | 69
2018-05-25 22:30 | 51 | 49 |  |  | 43245.9375 | 69 | 69
2018-05-25 23:00 | 53 | 51 |  |  | 43245.9583 | 69 | 68
2018-05-25 23:30 | 51 | 48 |  |  | 43245.9792 | 66 | 65
2018-05-26 | 47 | 44 |  |  | 43246 | 61 | 59
2018-05-26 00:30 | 43 | 39 |  |  | 43246.0208 | 54 | 53
2018-05-26 01:00 | 39 | 34 |  |  | 43246.0417 | 50 | 48
2018-05-26 01:30 | 39 | 35 |  |  | 43246.0625 | 50 | 48
2018-05-26 02:00 | 38 | 36 |  |  | 43246.0833 | 50 | 48
2018-05-26 02:30 | 37 | 36 |  |  | 43246.1042 | 51 | 47
2018-05-26 03:00 | 37 | 36 |  |  | 43246.125 | 51 | 47
2018-05-26 03:30 | 37 | 36 |  |  | 43246.1458 | 51 | 47
2018-05-26 04:00 | 37 | 36 |  |  | 43246.1667 | 51 | 48
2018-05-26 04:30 | 37 | 36 |  |  | 43246.1875 | 51 | 48
2018-05-26 05:00 | 37 | 36 |  |  | 43246.2083 | 52 | 48
2018-05-26 05:30 | 40 | 39 |  |  | 43246.2292 | 53 | 49
2018-05-26 06:00 | 40 | 39 |  |  | 43246.25 | 55 | 51
2018-05-26 06:30 | 42 | 41 |  |  | 43246.2708 | 57 | 55
2018-05-26 07:00 | 40 | 40 |  |  | 43246.2917 | 57 | 55
2018-05-26 07:30 | 40 | 39 |  |  | 43246.3125 | 60 | 58
2018-05-26 08:00 | 46 | 42 |  |  | 43246.3333 | 72 | 67
2018-05-26 08:30 | 47 | 40 |  |  | 43246.3542 | 72 | 65
2018-05-26 09:00 | 47 | 40 |  |  | 43246.375 | 72 | 66
2018-05-26 09:30 | 48 | 41 |  |  | 43246.3958 | 73 | 66
2018-05-26 10:00 | 53 | 47 |  |  | 43246.4167 | 75 | 68
2018-05-26 10:30 | 52 | 46 |  |  | 43246.4375 | 71 | 65
2018-05-26 11:00 | 48 | 42 |  |  | 43246.4583 | 67 | 61
2018-05-26 11:30 | 48 | 41 |  |  | 43246.4792 | 67 | 61
2018-05-26 12:00 | 46 | 39 |  |  | 43246.5 | 66 | 59
2018-05-26 12:30 | 48 | 41 |  |  | 43246.5208 | 68 | 61
2018-05-26 13:00 | 47 | 39 |  |  | 43246.5417 | 70 | 63
2018-05-26 13:30 | 51 | 44 |  |  | 43246.5625 | 76 | 70
2018-05-26 14:00 | 59 | 54 |  |  | 43246.5833 | 83 | 77
2018-05-26 14:30 | 60 | 55 |  |  | 43246.6042 | 83 | 78
2018-05-26 15:00 | 60 | 55 |  |  | 43246.625 | 84 | 78
2018-05-26 15:30 | 61 | 55 |  |  | 43246.6458 | 82 | 77
2018-05-26 16:00 | 61 | 55 |  |  | 43246.6667 | 84 | 78
2018-05-26 16:30 | 62 | 56 |  |  | 43246.6875 | 87 | 82
2018-05-26 17:00 | 63 | 58 |  |  | 43246.7083 | 89 | 84
2018-05-26 17:30 | 66 | 59 |  |  | 43246.7292 | 93 | 86
2018-05-26 18:00 | 67 | 59 |  |  | 43246.75 | 93 | 86
2018-05-26 18:30 | 68 | 60 |  |  | 43246.7708 | 93 | 85
2018-05-26 19:00 | 67 | 60 |  |  | 43246.7917 | 92 | 85
2018-05-26 19:30 | 65 | 59 |  |  | 43246.8125 | 90 | 84
2018-05-26 20:00 | 64 | 57 |  |  | 43246.8333 | 90 | 83
2018-05-26 20:30 | 64 | 59 |  |  | 43246.8542 | 89 | 83
2018-05-26 21:00 | 64 | 58 |  |  | 43246.875 | 88 | 82
2018-05-26 21:30 | 62 | 56 |  |  | 43246.8958 | 85 | 79
2018-05-26 22:00 | 61 | 55 |  |  | 43246.9167 | 85 | 78
2018-05-26 22:30 | 63 | 56 |  |  | 43246.9375 | 84 | 78
2018-05-26 23:00 | 62 | 55 |  |  | 43246.9583 | 83 | 76
2018-05-26 23:30 | 60 | 53 |  |  | 43246.9792 | 80 | 72
2018-05-27 | 56 | 48 |  |  | 43247 | 76 | 67
2018-05-27 00:30 | 54 | 44 |  |  | 43247.0208 | 72 | 62
2018-05-27 01:00 | 52 | 41 |  |  | 43247.0417 | 69 | 58
2018-05-27 01:30 | 51 | 40 |  |  | 43247.0625 | 67 | 56
2018-05-27 02:00 | 50 | 39 |  |  | 43247.0833 | 65 | 54
2018-05-27 02:30 | 50 | 39 |  |  | 43247.1042 | 65 | 53
2018-05-27 03:00 | 49 | 38 |  |  | 43247.125 | 64 | 52
2018-05-27 03:30 | 47 | 36 |  |  | 43247.1458 | 61 | 51
2018-05-27 04:00 | 47 | 36 |  |  | 43247.1667 | 60 | 50
2018-05-27 04:30 | 47 | 36 |  |  | 43247.1875 | 60 | 50
2018-05-27 05:00 | 47 | 37 |  |  | 43247.2083 | 61 | 51
2018-05-27 05:30 | 47 | 38 |  |  | 43247.2292 | 61 | 51
2018-05-27 06:00 | 47 | 38 |  |  | 43247.25 | 63 | 53
2018-05-27 06:30 | 49 | 40 |  |  | 43247.2708 | 65 | 56
2018-05-27 07:00 | 50 | 41 |  |  | 43247.2917 | 67 | 58
2018-05-27 07:30 | 50 | 42 |  |  | 43247.3125 | 69 | 61
2018-05-27 08:00 | 51 | 43 |  |  | 43247.3333 | 70 | 63
2018-05-27 08:30 | 52 | 45 |  |  | 43247.3542 | 72 | 65
2018-05-27 09:00 | 53 | 47 |  |  | 43247.375 | 72 | 66
2018-05-27 09:30 | 51 | 46 |  |  | 43247.3958 | 69 | 64
2018-05-27 10:00 | 49 | 43 |  |  | 43247.4167 | 69 | 64
2018-05-27 10:30 | 49 | 43 |  |  | 43247.4375 | 66 | 60
2018-05-27 11:00 | 52 | 47 |  |  | 43247.4583 | 74 | 70
2018-05-27 11:30 | 56 | 51 |  |  | 43247.4792 | 78 | 74
2018-05-27 12:00 | 55 | 50 |  |  | 43247.5 | 75 | 71
2018-05-27 12:30 | 50 | 45 |  |  | 43247.5208 | 73 | 69
2018-05-27 13:00 | 50 | 45 |  |  | 43247.5417 | 74 | 70
2018-05-27 13:30 | 50 | 45 |  |  | 43247.5625 | 71 | 67
2018-05-27 14:00 | 53 | 48 |  |  | 43247.5833 | 74 | 70
2018-05-27 14:30 | 56 | 52 |  |  | 43247.6042 | 76 | 72
2018-05-27 15:00 | 56 | 51 |  |  | 43247.625 | 75 | 71
2018-05-27 15:30 | 54 | 49 |  |  | 43247.6458 | 73 | 69
2018-05-27 16:00 | 57 | 52 |  |  | 43247.6667 | 77 | 72
2018-05-27 16:30 | 59 | 54 |  |  | 43247.6875 | 81 | 76
2018-05-27 17:00 | 61 | 56 |  |  | 43247.7083 | 85 | 81
2018-05-27 17:30 | 66 | 60 |  |  | 43247.7292 | 91 | 84
2018-05-27 18:00 | 69 | 63 |  |  | 43247.75 | 94 | 87
2018-05-27 18:30 | 70 | 63 |  |  | 43247.7708 | 93 | 87
2018-05-27 19:00 | 69 | 63 |  |  | 43247.7917 | 94 | 87
2018-05-27 19:30 | 67 | 62 |  |  | 43247.8125 | 91 | 86
2018-05-27 20:00 | 66 | 61 |  |  | 43247.8333 | 91 | 85
2018-05-27 20:30 | 65 | 60 |  |  | 43247.8542 | 90 | 84
2018-05-27 21:00 | 62 | 57 |  |  | 43247.875 | 86 | 80
2018-05-27 21:30 | 61 | 55 |  |  | 43247.8958 | 85 | 77
2018-05-27 22:00 | 63 | 56 |  |  | 43247.9167 | 86 | 79
2018-05-27 22:30 | 63 | 56 |  |  | 43247.9375 | 86 | 78
2018-05-27 23:00 | 62 | 55 |  |  | 43247.9583 | 84 | 75
2018-05-27 23:30 | 58 | 51 |  |  | 43247.9792 | 80 | 71
2018-05-28 | 56 | 47 |  |  | 43248 | 76 | 66
2018-05-28 00:30 | 54 | 44 |  |  | 43248.0208 | 72 | 61
2018-05-28 01:00 | 51 | 41 |  |  | 43248.0417 | 68 | 57
2018-05-28 01:30 | 51 | 40 |  |  | 43248.0625 | 67 | 56
2018-05-28 02:00 | 50 | 40 |  |  | 43248.0833 | 65 | 54
2018-05-28 02:30 | 49 | 39 |  |  | 43248.1042 | 63 | 52
2018-05-28 03:00 | 49 | 38 |  |  | 43248.125 | 63 | 52
2018-05-28 03:30 | 49 | 38 |  |  | 43248.1458 | 63 | 52
2018-05-28 04:00 | 49 | 38 |  |  | 43248.1667 | 63 | 52
2018-05-28 04:30 | 50 | 40 |  |  | 43248.1875 | 64 | 54
2018-05-28 05:00 | 52 | 43 |  |  | 43248.2083 | 67 | 57
2018-05-28 05:30 | 54 | 46 |  |  | 43248.2292 | 71 | 62
2018-05-28 06:00 | 58 | 53 |  |  | 43248.25 | 77 | 70
2018-05-28 06:30 | 65 | 61 |  |  | 43248.2708 | 86 | 82
2018-05-28 07:00 | 72 | 65 |  |  | 43248.2917 | 101 | 92
2018-05-28 07:30 | 81 | 69 |  |  | 43248.3125 | 118 | 101
2018-05-28 08:00 | 80 | 68 |  |  | 43248.3333 | 118 | 102
2018-05-28 08:30 | 78 | 67 |  |  | 43248.3542 | 117 | 102
2018-05-28 09:00 | 76 | 65 |  |  | 43248.375 | 114 | 99
2018-05-28 09:30 | 73 | 62 |  |  | 43248.3958 | 109 | 93
2018-05-28 10:00 | 70 | 57 |  |  | 43248.4167 | 105 | 89
2018-05-28 10:30 | 70 | 58 |  |  | 43248.4375 | 106 | 90
2018-05-28 11:00 | 76 | 65 |  |  | 43248.4583 | 108 | 94
2018-05-28 11:30 | 76 | 66 |  |  | 43248.4792 | 109 | 94
2018-05-28 12:00 | 77 | 68 |  |  | 43248.5 | 110 | 95
2018-05-28 12:30 | 78 | 67 |  |  | 43248.5208 | 109 | 94
2018-05-28 13:00 | 77 | 67 |  |  | 43248.5417 | 109 | 95
2018-05-28 13:30 | 81 | 71 |  |  | 43248.5625 | 111 | 96
2018-05-28 14:00 | 82 | 72 |  |  | 43248.5833 | 111 | 97
2018-05-28 14:30 | 82 | 72 |  |  | 43248.6042 | 113 | 99
2018-05-28 15:00 | 81 | 71 |  |  | 43248.625 | 113 | 98
2018-05-28 15:30 | 83 | 73 |  |  | 43248.6458 | 114 | 99
2018-05-28 16:00 | 84 | 74 |  |  | 43248.6667 | 115 | 100
2018-05-28 16:30 | 86 | 75 |  |  | 43248.6875 | 118 | 103
2018-05-28 17:00 | 90 | 79 |  |  | 43248.7083 | 125 | 107
2018-05-28 17:30 | 94 | 83 |  |  | 43248.7292 | 127 | 110
2018-05-28 18:00 | 95 | 83 |  |  | 43248.75 | 129 | 110
2018-05-28 18:30 | 94 | 80 |  |  | 43248.7708 | 127 | 107
2018-05-28 19:00 | 92 | 79 |  |  | 43248.7917 | 124 | 106
2018-05-28 19:30 | 91 | 79 |  |  | 43248.8125 | 123 | 104
2018-05-28 20:00 | 87 | 75 |  |  | 43248.8333 | 120 | 101
2018-05-28 20:30 | 84 | 75 |  |  | 43248.8542 | 112 | 99
2018-05-28 21:00 | 76 | 72 |  |  | 43248.875 | 98 | 94
2018-05-28 21:30 | 73 | 69 |  |  | 43248.8958 | 94 | 90
2018-05-28 22:00 | 73 | 69 |  |  | 43248.9167 | 94 | 90
2018-05-28 22:30 | 69 | 64 |  |  | 43248.9375 | 90 | 85
2018-05-28 23:00 | 68 | 62 |  |  | 43248.9583 | 87 | 81
2018-05-28 23:30 | 64 | 58 |  |  | 43248.9792 | 83 | 76
2018-05-29 | 61 | 54 |  |  | 43249 | 78 | 72
2018-05-29 00:30 | 57 | 50 |  |  | 43249.0208 | 73 | 65
2018-05-29 01:00 | 53 | 45 |  |  | 43249.0417 | 68 | 60
2018-05-29 01:30 | 52 | 43 |  |  | 43249.0625 | 66 | 57
2018-05-29 02:00 | 51 | 42 |  |  | 43249.0833 | 65 | 55
2018-05-29 02:30 | 51 | 41 |  |  | 43249.1042 | 65 | 55
2018-05-29 03:00 | 52 | 41 |  |  | 43249.125 | 65 | 55
2018-05-29 03:30 | 52 | 42 |  |  | 43249.1458 | 66 | 55
2018-05-29 04:00 | 54 | 44 |  |  | 43249.1667 | 67 | 57
2018-05-29 04:30 | 56 | 47 |  |  | 43249.1875 | 70 | 59
2018-05-29 05:00 | 59 | 51 |  |  | 43249.2083 | 73 | 64
2018-05-29 05:30 | 61 | 55 |  |  | 43249.2292 | 75 | 68
2018-05-29 06:00 | 63 | 59 |  |  | 43249.25 | 80 | 74
2018-05-29 06:30 | 69 | 66 |  |  | 43249.2708 | 89 | 85
2018-05-29 07:00 | 72 | 67 |  |  | 43249.2917 | 96 | 94
2018-05-29 07:30 | 79 | 73 |  |  | 43249.3125 | 104 | 102
2018-05-29 08:00 | 78 | 73 |  |  | 43249.3333 | 106 | 104
2018-05-29 08:30 | 78 | 72 |  |  | 43249.3542 | 106 | 105
2018-05-29 09:00 | 75 | 69 |  |  | 43249.375 | 102 | 100
2018-05-29 09:30 | 74 | 67 |  |  | 43249.3958 | 101 | 99
2018-05-29 10:00 | 75 | 69 |  |  | 43249.4167 | 101 | 99
2018-05-29 10:30 | 74 | 68 |  |  | 43249.4375 | 98 | 96
2018-05-29 11:00 | 74 | 69 |  |  | 43249.4583 | 97 | 95
2018-05-29 11:30 | 76 | 70 |  |  | 43249.4792 | 99 | 98
2018-05-29 12:00 | 77 | 72 |  |  | 43249.5 | 100 | 98
2018-05-29 12:30 | 81 | 76 |  |  | 43249.5208 | 103 | 102
2018-05-29 13:00 | 83 | 79 |  |  | 43249.5417 | 109 | 107
2018-05-29 13:30 | 88 | 81 |  |  | 43249.5625 | 113 | 110
2018-05-29 14:00 | 86 | 78 |  |  | 43249.5833 | 113 | 109
2018-05-29 14:30 | 83 | 75 |  |  | 43249.6042 | 109 | 105
2018-05-29 15:00 | 83 | 75 |  |  | 43249.625 | 109 | 105
2018-05-29 15:30 | 85 | 77 |  |  | 43249.6458 | 111 | 106
2018-05-29 16:00 | 87 | 78 |  |  | 43249.6667 | 111 | 107
2018-05-29 16:30 | 88 | 79 |  |  | 43249.6875 | 114 | 109
2018-05-29 17:00 | 92 | 84 |  |  | 43249.7083 | 119 | 115
2018-05-29 17:30 | 96 | 89 |  |  | 43249.7292 | 124 | 119
2018-05-29 18:00 | 97 | 90 |  |  | 43249.75 | 124 | 119
2018-05-29 18:30 | 96 | 88 |  |  | 43249.7708 | 122 | 115
2018-05-29 19:00 | 95 | 87 |  |  | 43249.7917 | 122 | 115
2018-05-29 19:30 | 95 | 87 |  |  | 43249.8125 | 119 | 113
2018-05-29 20:00 | 94 | 85 |  |  | 43249.8333 | 118 | 111
2018-05-29 20:30 | 91 | 82 |  |  | 43249.8542 | 116 | 109
2018-05-29 21:00 | 84 | 75 |  |  | 43249.875 | 106 | 102
2018-05-29 21:30 | 79 | 69 |  |  | 43249.8958 | 100 | 95
2018-05-29 22:00 | 77 | 67 |  |  | 43249.9167 | 99 | 93
2018-05-29 22:30 | 76 | 64 |  |  | 43249.9375 | 96 | 90
2018-05-29 23:00 | 75 | 63 |  |  | 43249.9583 | 94 | 86
2018-05-29 23:30 | 71 | 59 |  |  | 43249.9792 | 87 | 81
2018-05-30 | 66 | 54 |  |  | 43250 | 81 | 75
2018-05-30 00:30 | 63 | 50 |  |  | 43250.0208 | 75 | 69
2018-05-30 01:00 | 61 | 47 |  |  | 43250.0417 | 70 | 64
2018-05-30 01:30 | 59 | 44 |  |  | 43250.0625 | 68 | 62
2018-05-30 02:00 | 60 | 45 |  |  | 43250.0833 | 68 | 62
2018-05-30 02:30 | 59 | 45 |  |  | 43250.1042 | 66 | 60
2018-05-30 03:00 | 58 | 44 |  |  | 43250.125 | 65 | 59
2018-05-30 03:30 | 58 | 43 |  |  | 43250.1458 | 65 | 59
2018-05-30 04:00 | 56 | 42 |  |  | 43250.1667 | 64 | 58
2018-05-30 04:30 | 58 | 44 |  |  | 43250.1875 | 66 | 60
2018-05-30 05:00 | 60 | 48 |  |  | 43250.2083 | 68 | 63
2018-05-30 05:30 | 63 | 54 |  |  | 43250.2292 | 75 | 71
2018-05-30 06:00 | 68 | 61 |  |  | 43250.25 | 83 | 81
2018-05-30 06:30 | 75 | 70 |  |  | 43250.2708 | 95 | 94
2018-05-30 07:00 | 79 | 76 |  |  | 43250.2917 | 105 | 104
2018-05-30 07:30 | 82 | 79 |  |  | 43250.3125 | 111 | 110
2018-05-30 08:00 | 81 | 78 |  |  | 43250.3333 | 110 | 110
2018-05-30 08:30 | 78 | 75 |  |  | 43250.3542 | 107 | 106
2018-05-30 09:00 | 73 | 70 |  |  | 43250.375 | 102 | 101
2018-05-30 09:30 | 69 | 67 |  |  | 43250.3958 | 98 | 98
2018-05-30 10:00 | 65 | 62 |  |  | 43250.4167 | 94 | 93
2018-05-30 10:30 | 64 | 61 |  |  | 43250.4375 | 91 | 91
2018-05-30 11:00 | 62 | 60 |  |  | 43250.4583 | 89 | 89
2018-05-30 11:30 | 63 | 61 |  |  | 43250.4792 | 90 | 90
2018-05-30 12:00 | 62 | 60 |  |  | 43250.5 | 90 | 90
2018-05-30 12:30 | 62 | 60 |  |  | 43250.5208 | 91 | 91
2018-05-30 13:00 | 62 | 60 |  |  | 43250.5417 | 91 | 91
2018-05-30 13:30 | 62 | 60 |  |  | 43250.5625 | 92 | 92
2018-05-30 14:00 | 63 | 62 |  |  | 43250.5833 | 92 | 92
2018-05-30 14:30 | 67 | 66 |  |  | 43250.6042 | 95 | 95
2018-05-30 15:00 | 70 | 68 |  |  | 43250.625 | 99 | 99
2018-05-30 15:30 | 71 | 69 |  |  | 43250.6458 | 103 | 102
2018-05-30 16:00 | 75 | 72 |  |  | 43250.6667 | 105 | 104
2018-05-30 16:30 | 80 | 77 |  |  | 43250.6875 | 110 | 109
2018-05-30 17:00 | 82 | 79 |  |  | 43250.7083 | 113 | 112
2018-05-30 17:30 | 86 | 83 |  |  | 43250.7292 | 118 | 115
2018-05-30 18:00 | 90 | 86 |  |  | 43250.75 | 118 | 115
2018-05-30 18:30 | 89 | 84 |  |  | 43250.7708 | 116 | 112
2018-05-30 19:00 | 90 | 84 |  |  | 43250.7917 | 117 | 113
2018-05-30 19:30 | 89 | 85 |  |  | 43250.8125 | 114 | 111
2018-05-30 20:00 | 87 | 84 |  |  | 43250.8333 | 111 | 109
2018-05-30 20:30 | 84 | 80 |  |  | 43250.8542 | 109 | 107
2018-05-30 21:00 | 79 | 76 |  |  | 43250.875 | 102 | 101
2018-05-30 21:30 | 75 | 72 |  |  | 43250.8958 | 98 | 96
2018-05-30 22:00 | 73 | 69 |  |  | 43250.9167 | 96 | 94
2018-05-30 22:30 | 75 | 68 |  |  | 43250.9375 | 95 | 92
2018-05-30 23:00 | 75 | 68 |  |  | 43250.9583 | 92 | 89
2018-05-30 23:30 | 71 | 63 |  |  | 43250.9792 | 86 | 84
2018-05-31 | 66 | 56 |  |  | 43251 | 80 | 78
2018-05-31 00:30 | 63 | 52 |  |  | 43251.0208 | 74 | 71
2018-05-31 01:00 | 59 | 48 |  |  | 43251.0417 | 69 | 66
2018-05-31 01:30 | 59 | 47 |  |  | 43251.0625 | 67 | 63
2018-05-31 02:00 | 57 | 44 |  |  | 43251.0833 | 65 | 61
2018-05-31 02:30 | 57 | 44 |  |  | 43251.1042 | 65 | 61
2018-05-31 03:00 | 57 | 45 |  |  | 43251.125 | 65 | 61
2018-05-31 03:30 | 58 | 45 |  |  | 43251.1458 | 65 | 61
2018-05-31 04:00 | 58 | 46 |  |  | 43251.1667 | 65 | 61
2018-05-31 04:30 | 59 | 47 |  |  | 43251.1875 | 67 | 63
2018-05-31 05:00 | 61 | 50 |  |  | 43251.2083 | 70 | 66
2018-05-31 05:30 | 65 | 57 |  |  | 43251.2292 | 76 | 74
2018-05-31 06:00 | 69 | 63 |  |  | 43251.25 | 84 | 83
2018-05-31 06:30 | 74 | 70 |  |  | 43251.2708 | 96 | 95
2018-05-31 07:00 | 75 | 72 |  |  | 43251.2917 | 106 | 105
2018-05-31 07:30 | 77 | 75 |  |  | 43251.3125 | 111 | 111
2018-05-31 08:00 | 76 | 74 |  |  | 43251.3333 | 110 | 110
2018-05-31 08:30 | 73 | 71 |  |  | 43251.3542 | 106 | 106
2018-05-31 09:00 | 69 | 66 |  |  | 43251.375 | 100 | 100
2018-05-31 09:30 | 67 | 65 |  |  | 43251.3958 | 97 | 97
2018-05-31 10:00 | 65 | 62 |  |  | 43251.4167 | 93 | 93
2018-05-31 10:30 | 63 | 60 |  |  | 43251.4375 | 90 | 90
2018-05-31 11:00 | 62 | 59 |  |  | 43251.4583 | 88 | 88
2018-05-31 11:30 | 60 | 57 |  |  | 43251.4792 | 85 | 85
2018-05-31 12:00 | 59 | 56 |  |  | 43251.5 | 85 | 85
2018-05-31 12:30 | 59 | 56 |  |  | 43251.5208 | 85 | 85
2018-05-31 13:00 | 59 | 56 |  |  | 43251.5417 | 84 | 83
2018-05-31 13:30 | 60 | 56 |  |  | 43251.5625 | 85 | 85
2018-05-31 14:00 | 62 | 59 |  |  | 43251.5833 | 88 | 87
2018-05-31 14:30 | 64 | 60 |  |  | 43251.6042 | 89 | 89
2018-05-31 15:00 | 64 | 61 |  |  | 43251.625 | 91 | 91
2018-05-31 15:30 | 66 | 63 |  |  | 43251.6458 | 95 | 94
2018-05-31 16:00 | 73 | 70 |  |  | 43251.6667 | 100 | 99
2018-05-31 16:30 | 77 | 74 |  |  | 43251.6875 | 105 | 104
2018-05-31 17:00 | 80 | 77 |  |  | 43251.7083 | 109 | 107
2018-05-31 17:30 | 85 | 81 |  |  | 43251.7292 | 114 | 112
2018-05-31 18:00 | 87 | 83 |  |  | 43251.75 | 116 | 114
2018-05-31 18:30 | 88 | 84 |  |  | 43251.7708 | 116 | 113
2018-05-31 19:00 | 90 | 86 |  |  | 43251.7917 | 117 | 115
2018-05-31 19:30 | 88 | 84 |  |  | 43251.8125 | 115 | 113
2018-05-31 20:00 | 86 | 81 |  |  | 43251.8333 | 111 | 109
2018-05-31 20:30 | 85 | 81 |  |  | 43251.8542 | 111 | 109
2018-05-31 21:00 | 82 | 77 |  |  | 43251.875 | 106 | 104
2018-05-31 21:30 | 81 | 76 |  |  | 43251.8958 | 103 | 100
2018-05-31 22:00 | 79 | 75 |  |  | 43251.9167 | 102 | 100
2018-05-31 22:30 | 74 | 69 |  |  | 43251.9375 | 97 | 95
2018-05-31 23:00 | 74 | 68 |  |  | 43251.9583 | 93 | 90
2018-05-31 23:30 | 71 | 64 |  |  | 43251.9792 | 88 | 85
2018-06-01 | 66 | 57 |  |  | 43252 | 82 | 78
2018-06-01 00:30 | 61 | 52 |  |  | 43252.0208 | 74 | 70
2018-06-01 01:00 | 58 | 47 |  |  | 43252.0417 | 69 | 65
2018-06-01 01:30 | 58 | 46 |  |  | 43252.0625 | 67 | 62
2018-06-01 02:00 | 58 | 46 |  |  | 43252.0833 | 67 | 62
2018-06-01 02:30 | 59 | 46 |  |  | 43252.1042 | 67 | 62
2018-06-01 03:00 | 58 | 45 |  |  | 43252.125 | 66 | 62
2018-06-01 03:30 | 59 | 45 |  |  | 43252.1458 | 66 | 61
2018-06-01 04:00 | 59 | 46 |  |  | 43252.1667 | 66 | 61
2018-06-01 04:30 | 59 | 47 |  |  | 43252.1875 | 68 | 63
2018-06-01 05:00 | 61 | 51 |  |  | 43252.2083 | 71 | 67
2018-06-01 05:30 | 63 | 55 |  |  | 43252.2292 | 75 | 72
2018-06-01 06:00 | 68 | 62 |  |  | 43252.25 | 84 | 82
2018-06-01 06:30 | 76 | 72 |  |  | 43252.2708 | 98 | 97
2018-06-01 07:00 | 78 | 75 |  |  | 43252.2917 | 108 | 108
2018-06-01 07:30 | 88 | 81 |  |  | 43252.3125 | 117 | 116
2018-06-01 08:00 | 90 | 81 |  |  | 43252.3333 | 116 | 115
2018-06-01 08:30 | 87 | 76 |  |  | 43252.3542 | 110 | 109
2018-06-01 09:00 | 84 | 72 |  |  | 43252.375 | 105 | 104
2018-06-01 09:30 | 82 | 68 |  |  | 43252.3958 | 99 | 98
2018-06-01 10:00 | 80 | 66 |  |  | 43252.4167 | 96 | 95
2018-06-01 10:30 | 78 | 64 |  |  | 43252.4375 | 92 | 91
2018-06-01 11:00 | 77 | 62 |  |  | 43252.4583 | 90 | 89
2018-06-01 11:30 | 76 | 61 |  |  | 43252.4792 | 87 | 86
2018-06-01 12:00 | 75 | 60 |  |  | 43252.5 | 86 | 85
2018-06-01 12:30 | 72 | 57 |  |  | 43252.5208 | 79 | 78
2018-06-01 13:00 | 71 | 56 |  |  | 43252.5417 | 75 | 75
2018-06-01 13:30 | 69 | 57 |  |  | 43252.5625 | 75 | 75
2018-06-01 14:00 | 71 | 59 |  |  | 43252.5833 | 78 | 78
2018-06-01 14:30 | 72 | 60 |  |  | 43252.6042 | 79 | 79
2018-06-01 15:00 | 74 | 63 |  |  | 43252.625 | 82 | 82
2018-06-01 15:30 | 76 | 65 |  |  | 43252.6458 | 84 | 84
2018-06-01 16:00 | 76 | 67 |  |  | 43252.6667 | 87 | 87
2018-06-01 16:30 | 81 | 70 |  |  | 43252.6875 | 91 | 91
2018-06-01 17:00 | 85 | 74 |  |  | 43252.7083 | 96 | 95
2018-06-01 17:30 | 86 | 75 |  |  | 43252.7292 | 97 | 97
2018-06-01 18:00 | 88 | 75 |  |  | 43252.75 | 96 | 96
2018-06-01 18:30 | 88 | 75 |  |  | 43252.7708 | 96 | 95
2018-06-01 19:00 | 89 | 77 |  |  | 43252.7917 | 98 | 97
2018-06-01 19:30 | 86 | 74 |  |  | 43252.8125 | 95 | 94
2018-06-01 20:00 | 83 | 70 |  |  | 43252.8333 | 92 | 90
2018-06-01 20:30 | 82 | 69 |  |  | 43252.8542 | 90 | 88
2018-06-01 21:00 | 77 | 66 |  |  | 43252.875 | 86 | 85
2018-06-01 21:30 | 73 | 61 |  |  | 43252.8958 | 81 | 80
2018-06-01 22:00 | 72 | 59 |  |  | 43252.9167 | 81 | 80
2018-06-01 22:30 | 71 | 58 |  |  | 43252.9375 | 79 | 78
2018-06-01 23:00 | 71 | 58 |  |  | 43252.9583 | 77 | 76
2018-06-01 23:30 | 69 | 54 |  |  | 43252.9792 | 72 | 71
2018-06-02 | 65 | 49 |  |  | 43253 | 66 | 66
2018-06-02 00:30 | 61 | 43 |  |  | 43253.0208 | 59 | 59
2018-06-02 01:00 | 60 | 41 |  |  | 43253.0417 | 56 | 56
2018-06-02 01:30 | 59 | 39 |  |  | 43253.0625 | 53 | 53
2018-06-02 02:00 | 58 | 39 |  |  | 43253.0833 | 52 | 51
2018-06-02 02:30 | 58 | 39 |  |  | 43253.1042 | 52 | 52
2018-06-02 03:00 | 57 | 37 |  |  | 43253.125 | 50 | 50
2018-06-02 03:30 | 57 | 38 |  |  | 43253.1458 | 51 | 50
2018-06-02 04:00 | 56 | 36 |  |  | 43253.1667 | 51 | 50
2018-06-02 04:30 | 57 | 38 |  |  | 43253.1875 | 51 | 51
2018-06-02 05:00 | 57 | 38 |  |  | 43253.2083 | 52 | 52
2018-06-02 05:30 | 56 | 39 |  |  | 43253.2292 | 54 | 54
2018-06-02 06:00 | 59 | 43 |  |  | 43253.25 | 57 | 57
2018-06-02 06:30 | 61 | 47 |  |  | 43253.2708 | 63 | 63
2018-06-02 07:00 | 61 | 48 |  |  | 43253.2917 | 65 | 65
2018-06-02 07:30 | 61 | 48 |  |  | 43253.3125 | 68 | 68
2018-06-02 08:00 | 60 | 48 |  |  | 43253.3333 | 66 | 66
2018-06-02 08:30 | 68 | 46 |  |  | 43253.3542 | 69 | 67
2018-06-02 09:00 | 75 | 45 |  |  | 43253.375 | 70 | 67
2018-06-02 09:30 | 77 | 42 |  |  | 43253.3958 | 66 | 63
2018-06-02 10:00 | 87 | 39 |  |  | 43253.4167 | 60 | 59
2018-06-02 10:30 | 81 | 37 |  |  | 43253.4375 | 56 | 56
2018-06-02 11:00 | 65 | 36 |  |  | 43253.4583 | 53 | 53
2018-06-02 11:30 | 64 | 35 |  |  | 43253.4792 | 52 | 51
2018-06-02 12:00 | 64 | 35 |  |  | 43253.5 | 50 | 50
2018-06-02 12:30 | 65 | 33 |  |  | 43253.5208 | 49 | 49
2018-06-02 13:00 | 66 | 33 |  |  | 43253.5417 | 49 | 49
2018-06-02 13:30 | 66 | 35 |  |  | 43253.5625 | 50 | 50
2018-06-02 14:00 | 66 | 34 |  |  | 43253.5833 | 50 | 50
2018-06-02 14:30 | 68 | 37 |  |  | 43253.6042 | 53 | 53
2018-06-02 15:00 | 69 | 40 |  |  | 43253.625 | 57 | 57
2018-06-02 15:30 | 70 | 42 |  |  | 43253.6458 | 60 | 60
2018-06-02 16:00 | 72 | 44 |  |  | 43253.6667 | 63 | 62
2018-06-02 16:30 | 74 | 47 |  |  | 43253.6875 | 67 | 66
2018-06-02 17:00 | 82 | 51 |  |  | 43253.7083 | 72 | 72
2018-06-02 17:30 | 101 | 56 |  |  | 43253.7292 | 79 | 79
2018-06-02 18:00 | 101 | 58 |  |  | 43253.75 | 81 | 81
2018-06-02 18:30 | 101 | 58 |  |  | 43253.7708 | 81 | 81
2018-06-02 19:00 | 102 | 59 |  |  | 43253.7917 | 83 | 83
2018-06-02 19:30 | 102 | 60 |  |  | 43253.8125 | 82 | 81
2018-06-02 20:00 | 101 | 58 |  |  | 43253.8333 | 80 | 80
2018-06-02 20:30 | 100 | 56 |  |  | 43253.8542 | 78 | 78
2018-06-02 21:00 | 99 | 54 |  |  | 43253.875 | 75 | 75
2018-06-02 21:30 | 94 | 53 |  |  | 43253.8958 | 72 | 72
2018-06-02 22:00 | 77 | 51 |  |  | 43253.9167 | 72 | 70
2018-06-02 22:30 | 79 | 53 |  |  | 43253.9375 | 74 | 72
2018-06-02 23:00 | 80 | 53 |  |  | 43253.9583 | 72 | 70
2018-06-02 23:30 | 80 | 51 |  |  | 43253.9792 | 69 | 67
2018-06-03 | 78 | 47 |  |  | 43254 | 65 | 63
2018-06-03 00:30 | 76 | 42 |  |  | 43254.0208 | 60 | 56
2018-06-03 01:00 | 75 | 38 |  |  | 43254.0417 | 55 | 52
2018-06-03 01:30 | 74 | 36 |  |  | 43254.0625 | 53 | 49
2018-06-03 02:00 | 72 | 34 |  |  | 43254.0833 | 51 | 47
2018-06-03 02:30 | 71 | 33 |  |  | 43254.1042 | 48 | 45
2018-06-03 03:00 | 72 | 33 |  |  | 43254.125 | 48 | 45
2018-06-03 03:30 | 71 | 33 |  |  | 43254.1458 | 48 | 45
2018-06-03 04:00 | 72 | 34 |  |  | 43254.1667 | 49 | 46
2018-06-03 04:30 | 73 | 35 |  |  | 43254.1875 | 50 | 47
2018-06-03 05:00 | 73 | 36 |  |  | 43254.2083 | 52 | 48
2018-06-03 05:30 | 73 | 37 |  |  | 43254.2292 | 52 | 48
2018-06-03 06:00 | 73 | 37 |  |  | 43254.25 | 53 | 50
2018-06-03 06:30 | 73 | 38 |  |  | 43254.2708 | 55 | 52
2018-06-03 07:00 | 74 | 40 |  |  | 43254.2917 | 58 | 55
2018-06-03 07:30 | 74 | 41 |  |  | 43254.3125 | 59 | 57
2018-06-03 08:00 | 73 | 41 |  |  | 43254.3333 | 60 | 58
2018-06-03 08:30 | 73 | 42 |  |  | 43254.3542 | 61 | 59
2018-06-03 09:00 | 71 | 39 |  |  | 43254.375 | 59 | 58
2018-06-03 09:30 | 70 | 38 |  |  | 43254.3958 | 57 | 56
2018-06-03 10:00 | 69 | 38 |  |  | 43254.4167 | 56 | 55
2018-06-03 10:30 | 69 | 37 |  |  | 43254.4375 | 54 | 52
2018-06-03 11:00 | 68 | 35 |  |  | 43254.4583 | 52 | 51
2018-06-03 11:30 | 67 | 34 |  |  | 43254.4792 | 48 | 47
2018-06-03 12:00 | 66 | 33 |  |  | 43254.5 | 47 | 46
2018-06-03 12:30 | 67 | 34 |  |  | 43254.5208 | 48 | 47
2018-06-03 13:00 | 67 | 34 |  |  | 43254.5417 | 48 | 47
2018-06-03 13:30 | 68 | 35 |  |  | 43254.5625 | 49 | 48
2018-06-03 14:00 | 68 | 35 |  |  | 43254.5833 | 49 | 48
2018-06-03 14:30 | 69 | 38 |  |  | 43254.6042 | 53 | 52
2018-06-03 15:00 | 71 | 42 |  |  | 43254.625 | 57 | 56
2018-06-03 15:30 | 71 | 43 |  |  | 43254.6458 | 58 | 57
2018-06-03 16:00 | 72 | 45 |  |  | 43254.6667 | 60 | 59
2018-06-03 16:30 | 74 | 47 |  |  | 43254.6875 | 63 | 62
2018-06-03 17:00 | 78 | 50 |  |  | 43254.7083 | 68 | 67
2018-06-03 17:30 | 81 | 55 |  |  | 43254.7292 | 74 | 73
2018-06-03 18:00 | 82 | 57 |  |  | 43254.75 | 76 | 75
2018-06-03 18:30 | 82 | 57 |  |  | 43254.7708 | 76 | 75
2018-06-03 19:00 | 83 | 58 |  |  | 43254.7917 | 77 | 76
2018-06-03 19:30 | 82 | 56 |  |  | 43254.8125 | 74 | 73
2018-06-03 20:00 | 81 | 55 |  |  | 43254.8333 | 73 | 72
2018-06-03 20:30 | 79 | 53 |  |  | 43254.8542 | 73 | 71
2018-06-03 21:00 | 77 | 51 |  |  | 43254.875 | 69 | 68
2018-06-03 21:30 | 75 | 49 |  |  | 43254.8958 | 66 | 65
2018-06-03 22:00 | 75 | 48 |  |  | 43254.9167 | 67 | 65
2018-06-03 22:30 | 77 | 50 |  |  | 43254.9375 | 69 | 67
2018-06-03 23:00 | 77 | 48 |  |  | 43254.9583 | 66 | 64
2018-06-03 23:30 | 76 | 45 |  |  | 43254.9792 | 62 | 60
2018-06-04 | 74 | 41 |  |  | 43255 | 59 | 56
2018-06-04 00:30 | 74 | 38 |  |  | 43255.0208 | 55 | 52
2018-06-04 01:00 | 73 | 36 |  |  | 43255.0417 | 51 | 47
2018-06-04 01:30 | 71 | 32 |  |  | 43255.0625 | 48 | 44
2018-06-04 02:00 | 70 | 29 |  |  | 43255.0833 | 45 | 42
2018-06-04 02:30 | 70 | 31 |  |  | 43255.1042 | 45 | 43
2018-06-04 03:00 | 70 | 31 |  |  | 43255.125 | 45 | 42
2018-06-04 03:30 | 70 | 31 |  |  | 43255.1458 | 45 | 42
2018-06-04 04:00 | 71 | 33 |  |  | 43255.1667 | 46 | 43
2018-06-04 04:30 | 71 | 35 |  |  | 43255.1875 | 48 | 45
2018-06-04 05:00 | 72 | 39 |  |  | 43255.2083 | 51 | 49
2018-06-04 05:30 | 71 | 43 |  |  | 43255.2292 | 55 | 53
2018-06-04 06:00 | 77 | 48 |  |  | 43255.25 | 60 | 60
2018-06-04 06:30 | 91 | 54 |  |  | 43255.2708 | 74 | 72
2018-06-04 07:00 | 88 | 60 |  |  | 43255.2917 | 84 | 83
2018-06-04 07:30 | 95 | 65 |  |  | 43255.3125 | 90 | 90
2018-06-04 08:00 | 94 | 64 |  |  | 43255.3333 | 89 | 89
2018-06-04 08:30 | 90 | 59 |  |  | 43255.3542 | 85 | 84
2018-06-04 09:00 | 88 | 55 |  |  | 43255.375 | 80 | 79
2018-06-04 09:30 | 85 | 50 |  |  | 43255.3958 | 74 | 73
2018-06-04 10:00 | 84 | 49 |  |  | 43255.4167 | 71 | 70
2018-06-04 10:30 | 85 | 46 |  |  | 43255.4375 | 68 | 66
2018-06-04 11:00 | 84 | 45 |  |  | 43255.4583 | 68 | 66
2018-06-04 11:30 | 84 | 45 |  |  | 43255.4792 | 68 | 66
2018-06-04 12:00 | 86 | 48 |  |  | 43255.5 | 69 | 67
2018-06-04 12:30 | 86 | 48 |  |  | 43255.5208 | 72 | 70
2018-06-04 13:00 | 87 | 51 |  |  | 43255.5417 | 76 | 74
2018-06-04 13:30 | 90 | 55 |  |  | 43255.5625 | 80 | 79
2018-06-04 14:00 | 93 | 57 |  |  | 43255.5833 | 82 | 81
2018-06-04 14:30 | 94 | 59 |  |  | 43255.6042 | 84 | 83
2018-06-04 15:00 | 95 | 59 |  |  | 43255.625 | 84 | 83
2018-06-04 15:30 | 96 | 59 |  |  | 43255.6458 | 86 | 86
2018-06-04 16:00 | 99 | 63 |  |  | 43255.6667 | 89 | 89
2018-06-04 16:30 | 107 | 67 |  |  | 43255.6875 | 95 | 94
2018-06-04 17:00 | 106 | 65 |  |  | 43255.7083 | 90 | 88
2018-06-04 17:30 | 108 | 66 |  |  | 43255.7292 | 91 | 88
2018-06-04 18:00 | 107 | 64 |  |  | 43255.75 | 87 | 85
2018-06-04 18:30 | 102 | 63 |  |  | 43255.7708 | 86 | 83
2018-06-04 19:00 | 96 | 62 |  |  | 43255.7917 | 86 | 83
2018-06-04 19:30 | 95 | 62 |  |  | 43255.8125 | 84 | 81
2018-06-04 20:00 | 84 | 59 |  |  | 43255.8333 | 77 | 77
2018-06-04 20:30 | 76 | 57 |  |  | 43255.8542 | 75 | 74
2018-06-04 21:00 | 66 | 56 |  |  | 43255.875 | 72 | 71
2018-06-04 21:30 | 68 | 55 |  |  | 43255.8958 | 69 | 67
2018-06-04 22:00 | 67 | 53 |  |  | 43255.9167 | 70 | 68
2018-06-04 22:30 | 66 | 51 |  |  | 43255.9375 | 69 | 67
2018-06-04 23:00 | 66 | 51 |  |  | 43255.9583 | 67 | 63
2018-06-04 23:30 | 63 | 46 |  |  | 43255.9792 | 63 | 59
2018-06-05 | 60 | 40 |  |  | 43256 | 57 | 52
2018-06-05 00:30 | 57 | 36 |  |  | 43256.0208 | 52 | 46
2018-06-05 01:00 | 57 | 33 |  |  | 43256.0417 | 50 | 43
2018-06-05 01:30 | 57 | 32 |  |  | 43256.0625 | 48 | 41
2018-06-05 02:00 | 56 | 31 |  |  | 43256.0833 | 47 | 39
2018-06-05 02:30 | 55 | 29 |  |  | 43256.1042 | 46 | 38
2018-06-05 03:00 | 56 | 31 |  |  | 43256.125 | 48 | 40
2018-06-05 03:30 | 55 | 32 |  |  | 43256.1458 | 46 | 40
2018-06-05 04:00 | 56 | 34 |  |  | 43256.1667 | 48 | 42
2018-06-05 04:30 | 58 | 37 |  |  | 43256.1875 | 51 | 46
2018-06-05 05:00 | 61 | 42 |  |  | 43256.2083 | 56 | 51
2018-06-05 05:30 | 61 | 45 |  |  | 43256.2292 | 58 | 54
2018-06-05 06:00 | 61 | 48 |  |  | 43256.25 | 59 | 57
2018-06-05 06:30 | 67 | 51 |  |  | 43256.2708 | 66 | 66
2018-06-05 07:00 | 67 | 55 |  |  | 43256.2917 | 75 | 75
2018-06-05 07:30 | 69 | 59 |  |  | 43256.3125 | 81 | 81
2018-06-05 08:00 | 70 | 57 |  |  | 43256.3333 | 82 | 81
2018-06-05 08:30 | 71 | 52 |  |  | 43256.3542 | 78 | 76
2018-06-05 09:00 | 70 | 48 |  |  | 43256.375 | 74 | 71
2018-06-05 09:30 | 68 | 44 |  |  | 43256.3958 | 68 | 66
2018-06-05 10:00 | 61 | 42 |  |  | 43256.4167 | 64 | 64
2018-06-05 10:30 | 58 | 41 |  |  | 43256.4375 | 61 | 61
2018-06-05 11:00 | 58 | 41 |  |  | 43256.4583 | 60 | 60
2018-06-05 11:30 | 57 | 41 |  |  | 43256.4792 | 60 | 60
2018-06-05 12:00 | 58 | 41 |  |  | 43256.5 | 61 | 61
2018-06-05 12:30 | 58 | 43 |  |  | 43256.5208 | 63 | 63
2018-06-05 13:00 | 57 | 44 |  |  | 43256.5417 | 65 | 64
2018-06-05 13:30 | 58 | 46 |  |  | 43256.5625 | 65 | 65
2018-06-05 14:00 | 58 | 45 |  |  | 43256.5833 | 63 | 63
2018-06-05 14:30 | 58 | 45 |  |  | 43256.6042 | 61 | 61
2018-06-05 15:00 | 61 | 49 |  |  | 43256.625 | 63 | 63
2018-06-05 15:30 | 64 | 51 |  |  | 43256.6458 | 65 | 65
2018-06-05 16:00 | 65 | 51 |  |  | 43256.6667 | 69 | 69
2018-06-05 16:30 | 68 | 54 |  |  | 43256.6875 | 70 | 70
2018-06-05 17:00 | 74 | 59 |  |  | 43256.7083 | 75 | 74
2018-06-05 17:30 | 78 | 63 |  |  | 43256.7292 | 79 | 79
2018-06-05 18:00 | 84 | 70 |  |  | 43256.75 | 85 | 85
2018-06-05 18:30 | 81 | 66 |  |  | 43256.7708 | 81 | 81
2018-06-05 19:00 | 77 | 65 |  |  | 43256.7917 | 79 | 79
2018-06-05 19:30 | 75 | 62 |  |  | 43256.8125 | 76 | 76
2018-06-05 20:00 | 73 | 60 |  |  | 43256.8333 | 75 | 75
2018-06-05 20:30 | 74 | 61 |  |  | 43256.8542 | 76 | 76
2018-06-05 21:00 | 71 | 59 |  |  | 43256.875 | 72 | 72
2018-06-05 21:30 | 69 | 56 |  |  | 43256.8958 | 68 | 68
2018-06-05 22:00 | 68 | 55 |  |  | 43256.9167 | 67 | 67
2018-06-05 22:30 | 67 | 52 |  |  | 43256.9375 | 64 | 64
2018-06-05 23:00 | 66 | 50 |  |  | 43256.9583 | 60 | 60
2018-06-05 23:30 | 63 | 45 |  |  | 43256.9792 | 55 | 55
2018-06-06 | 60 | 41 |  |  | 43257 | 51 | 51
2018-06-06 00:30 | 61 | 37 |  |  | 43257.0208 | 45 | 45
2018-06-06 01:00 | 61 | 33 |  |  | 43257.0417 | 41 | 40
2018-06-06 01:30 | 61 | 33 |  |  | 43257.0625 | 39 | 38
2018-06-06 02:00 | 61 | 32 |  |  | 43257.0833 | 39 | 37
2018-06-06 02:30 | 61 | 30 |  |  | 43257.1042 | 37 | 35
2018-06-06 03:00 | 61 | 29 |  |  | 43257.125 | 36 | 35
2018-06-06 03:30 | 62 | 30 |  |  | 43257.1458 | 37 | 36
2018-06-06 04:00 | 62 | 32 |  |  | 43257.1667 | 39 | 38
2018-06-06 04:30 | 63 | 34 |  |  | 43257.1875 | 41 | 39
2018-06-06 05:00 | 65 | 40 |  |  | 43257.2083 | 45 | 44
2018-06-06 05:30 | 66 | 44 |  |  | 43257.2292 | 50 | 49
2018-06-06 06:00 | 69 | 49 |  |  | 43257.25 | 55 | 55
2018-06-06 06:30 | 83 | 51 |  |  | 43257.2708 | 68 | 66
2018-06-06 07:00 | 85 | 55 |  |  | 43257.2917 | 76 | 73
2018-06-06 07:30 | 88 | 59 |  |  | 43257.3125 | 84 | 81
2018-06-06 08:00 | 86 | 56 |  |  | 43257.3333 | 82 | 78
2018-06-06 08:30 | 84 | 53 |  |  | 43257.3542 | 80 | 75
2018-06-06 09:00 | 80 | 48 |  |  | 43257.375 | 74 | 69
2018-06-06 09:30 | 77 | 44 |  |  | 43257.3958 | 70 | 65
2018-06-06 10:00 | 75 | 42 |  |  | 43257.4167 | 67 | 61
2018-06-06 10:30 | 71 | 38 |  |  | 43257.4375 | 61 | 54
2018-06-06 11:00 | 69 | 37 |  |  | 43257.4583 | 61 | 53
2018-06-06 11:30 | 69 | 35 |  |  | 43257.4792 | 61 | 53
2018-06-06 12:00 | 72 | 40 |  |  | 43257.5 | 66 | 59
2018-06-06 12:30 | 73 | 42 |  |  | 43257.5208 | 68 | 61
2018-06-06 13:00 | 76 | 48 |  |  | 43257.5417 | 75 | 69
2018-06-06 13:30 | 77 | 51 |  |  | 43257.5625 | 76 | 70
2018-06-06 14:00 | 74 | 48 |  |  | 43257.5833 | 70 | 64
2018-06-06 14:30 | 74 | 46 |  |  | 43257.6042 | 74 | 68
2018-06-06 15:00 | 77 | 46 |  |  | 43257.625 | 79 | 73
2018-06-06 15:30 | 80 | 48 |  |  | 43257.6458 | 81 | 75
2018-06-06 16:00 | 82 | 49 |  |  | 43257.6667 | 81 | 76
2018-06-06 16:30 | 88 | 53 |  |  | 43257.6875 | 79 | 77
2018-06-06 17:00 | 91 | 58 |  |  | 43257.7083 | 84 | 82
2018-06-06 17:30 | 95 | 62 |  |  | 43257.7292 | 88 | 86
2018-06-06 18:00 | 97 | 64 |  |  | 43257.75 | 89 | 88
2018-06-06 18:30 | 96 | 62 |  |  | 43257.7708 | 87 | 85
2018-06-06 19:00 | 94 | 62 |  |  | 43257.7917 | 88 | 86
2018-06-06 19:30 | 93 | 61 |  |  | 43257.8125 | 86 | 83
2018-06-06 20:00 | 91 | 59 |  |  | 43257.8333 | 84 | 81
2018-06-06 20:30 | 89 | 58 |  |  | 43257.8542 | 82 | 80
2018-06-06 21:00 | 86 | 53 |  |  | 43257.875 | 76 | 73
2018-06-06 21:30 | 87 | 51 |  |  | 43257.8958 | 72 | 70
2018-06-06 22:00 | 86 | 49 |  |  | 43257.9167 | 71 | 69
2018-06-06 22:30 | 83 | 49 |  |  | 43257.9375 | 68 | 67
2018-06-06 23:00 | 70 | 48 |  |  | 43257.9583 | 65 | 64
2018-06-06 23:30 | 69 | 45 |  |  | 43257.9792 | 61 | 60
2018-06-07 | 67 | 39 |  |  | 43258 | 55 | 55
2018-06-07 00:30 | 65 | 36 |  |  | 43258.0208 | 51 | 50
2018-06-07 01:00 | 67 | 35 |  |  | 43258.0417 | 48 | 48
2018-06-07 01:30 | 67 | 35 |  |  | 43258.0625 | 48 | 47
2018-06-07 02:00 | 68 | 36 |  |  | 43258.0833 | 49 | 48
2018-06-07 02:30 | 69 | 37 |  |  | 43258.1042 | 49 | 48
2018-06-07 03:00 | 68 | 37 |  |  | 43258.125 | 50 | 49
2018-06-07 03:30 | 68 | 36 |  |  | 43258.1458 | 49 | 48
2018-06-07 04:00 | 69 | 38 |  |  | 43258.1667 | 51 | 50
2018-06-07 04:30 | 71 | 41 |  |  | 43258.1875 | 53 | 52
2018-06-07 05:00 | 72 | 44 |  |  | 43258.2083 | 56 | 56
2018-06-07 05:30 | 74 | 49 |  |  | 43258.2292 | 62 | 61
2018-06-07 06:00 | 75 | 53 |  |  | 43258.25 | 67 | 66
2018-06-07 06:30 | 70 | 51 |  |  | 43258.2708 | 70 | 70
2018-06-07 07:00 | 62 | 55 |  |  | 43258.2917 | 79 | 79
2018-06-07 07:30 | 65 | 59 |  |  | 43258.3125 | 87 | 87
2018-06-07 08:00 | 66 | 62 |  |  | 43258.3333 | 91 | 90
2018-06-07 08:30 | 64 | 60 |  |  | 43258.3542 | 90 | 89
2018-06-07 09:00 | 64 | 60 |  |  | 43258.375 | 89 | 88
2018-06-07 09:30 | 64 | 61 |  |  | 43258.3958 | 88 | 86
2018-06-07 10:00 | 63 | 59 |  |  | 43258.4167 | 86 | 85
2018-06-07 10:30 | 61 | 57 |  |  | 43258.4375 | 85 | 83
2018-06-07 11:00 | 57 | 52 |  |  | 43258.4583 | 79 | 78
2018-06-07 11:30 | 57 | 48 |  |  | 43258.4792 | 77 | 77
2018-06-07 12:00 | 59 | 50 |  |  | 43258.5 | 79 | 78
2018-06-07 12:30 | 59 | 50 |  |  | 43258.5208 | 76 | 75
2018-06-07 13:00 | 60 | 52 |  |  | 43258.5417 | 76 | 75
2018-06-07 13:30 | 62 | 54 |  |  | 43258.5625 | 78 | 78
2018-06-07 14:00 | 63 | 54 |  |  | 43258.5833 | 78 | 78
2018-06-07 14:30 | 60 | 49 |  |  | 43258.6042 | 74 | 74
2018-06-07 15:00 | 61 | 51 |  |  | 43258.625 | 76 | 76
2018-06-07 15:30 | 66 | 55 |  |  | 43258.6458 | 78 | 78
2018-06-07 16:00 | 70 | 60 |  |  | 43258.6667 | 81 | 81
2018-06-07 16:30 | 73 | 62 |  |  | 43258.6875 | 83 | 83
2018-06-07 17:00 | 74 | 63 |  |  | 43258.7083 | 86 | 86
2018-06-07 17:30 | 78 | 67 |  |  | 43258.7292 | 88 | 88
2018-06-07 18:00 | 80 | 69 |  |  | 43258.75 | 89 | 89
2018-06-07 18:30 | 80 | 68 |  |  | 43258.7708 | 87 | 87
2018-06-07 19:00 | 82 | 69 |  |  | 43258.7917 | 88 | 88
2018-06-07 19:30 | 80 | 67 |  |  | 43258.8125 | 87 | 87
2018-06-07 20:00 | 77 | 65 |  |  | 43258.8333 | 85 | 85
2018-06-07 20:30 | 77 | 65 |  |  | 43258.8542 | 85 | 85
2018-06-07 21:00 | 74 | 60 |  |  | 43258.875 | 79 | 79
2018-06-07 21:30 | 70 | 55 |  |  | 43258.8958 | 72 | 72
2018-06-07 22:00 | 67 | 50 |  |  | 43258.9167 | 68 | 67
2018-06-07 22:30 | 71 | 49 |  |  | 43258.9375 | 66 | 66
2018-06-07 23:00 | 73 | 48 |  |  | 43258.9583 | 65 | 65
2018-06-07 23:30 | 70 | 45 |  |  | 43258.9792 | 59 | 58
2018-06-08 | 66 | 40 |  |  | 43259 | 52 | 51
2018-06-08 00:30 | 64 | 35 |  |  | 43259.0208 | 47 | 46
2018-06-08 01:00 | 63 | 32 |  |  | 43259.0417 | 43 | 42
2018-06-08 01:30 | 65 | 33 |  |  | 43259.0625 | 44 | 43
2018-06-08 02:00 | 65 | 32 |  |  | 43259.0833 | 42 | 41
2018-06-08 02:30 | 67 | 33 |  |  | 43259.1042 | 43 | 40
2018-06-08 03:00 | 66 | 30 |  |  | 43259.125 | 40 | 38
2018-06-08 03:30 | 67 | 30 |  |  | 43259.1458 | 42 | 39
2018-06-08 04:00 | 68 | 34 |  |  | 43259.1667 | 44 | 42
2018-06-08 04:30 | 69 | 37 |  |  | 43259.1875 | 47 | 45
2018-06-08 05:00 | 71 | 40 |  |  | 43259.2083 | 50 | 49
2018-06-08 05:30 | 71 | 44 |  |  | 43259.2292 | 53 | 52
2018-06-08 06:00 | 69 | 47 |  |  | 43259.25 | 57 | 57
2018-06-08 06:30 | 81 | 51 |  |  | 43259.2708 | 69 | 68
2018-06-08 07:00 | 88 | 54 |  |  | 43259.2917 | 76 | 75
2018-06-08 07:30 | 91 | 56 |  |  | 43259.3125 | 82 | 81
2018-06-08 08:00 | 92 | 56 |  |  | 43259.3333 | 82 | 81
2018-06-08 08:30 | 90 | 56 |  |  | 43259.3542 | 83 | 81
2018-06-08 09:00 | 87 | 55 |  |  | 43259.375 | 82 | 79
2018-06-08 09:30 | 85 | 55 |  |  | 43259.3958 | 81 | 78
2018-06-08 10:00 | 83 | 54 |  |  | 43259.4167 | 79 | 75
2018-06-08 10:30 | 85 | 56 |  |  | 43259.4375 | 81 | 78
2018-06-08 11:00 | 84 | 55 |  |  | 43259.4583 | 78 | 74
2018-06-08 11:30 | 81 | 49 |  |  | 43259.4792 | 70 | 66
2018-06-08 12:00 | 82 | 52 |  |  | 43259.5 | 74 | 70
2018-06-08 12:30 | 81 | 51 |  |  | 43259.5208 | 75 | 71
2018-06-08 13:00 | 81 | 50 |  |  | 43259.5417 | 76 | 72
2018-06-08 13:30 | 82 | 50 |  |  | 43259.5625 | 79 | 75
2018-06-08 14:00 | 81 | 47 |  |  | 43259.5833 | 73 | 69
2018-06-08 14:30 | 81 | 44 |  |  | 43259.6042 | 71 | 67
2018-06-08 15:00 | 84 | 50 |  |  | 43259.625 | 72 | 69
2018-06-08 15:30 | 82 | 47 |  |  | 43259.6458 | 71 | 67
2018-06-08 16:00 | 84 | 50 |  |  | 43259.6667 | 73 | 70
2018-06-08 16:30 | 87 | 54 |  |  | 43259.6875 | 77 | 74
2018-06-08 17:00 | 87 | 59 |  |  | 43259.7083 | 82 | 79
2018-06-08 17:30 | 88 | 66 |  |  | 43259.7292 | 89 | 85
2018-06-08 18:00 | 85 | 62 |  |  | 43259.75 | 84 | 81
2018-06-08 18:30 | 85 | 61 |  |  | 43259.7708 | 82 | 79
2018-06-08 19:00 | 84 | 59 |  |  | 43259.7917 | 80 | 77
2018-06-08 19:30 | 82 | 56 |  |  | 43259.8125 | 78 | 75
2018-06-08 20:00 | 84 | 57 |  |  | 43259.8333 | 77 | 74
2018-06-08 20:30 | 92 | 54 |  |  | 43259.8542 | 73 | 72
2018-06-08 21:00 | 89 | 51 |  |  | 43259.875 | 68 | 67
2018-06-08 21:30 | 86 | 48 |  |  | 43259.8958 | 65 | 63
2018-06-08 22:00 | 87 | 46 |  |  | 43259.9167 | 65 | 63
2018-06-08 22:30 | 88 | 46 |  |  | 43259.9375 | 64 | 62
2018-06-08 23:00 | 86 | 46 |  |  | 43259.9583 | 64 | 61
2018-06-08 23:30 | 82 | 43 |  |  | 43259.9792 | 60 | 58
2018-06-09 | 64 | 37 |  |  | 43260 | 50 | 50
2018-06-09 00:30 | 63 | 33 |  |  | 43260.0208 | 45 | 44
2018-06-09 01:00 | 61 | 29 |  |  | 43260.0417 | 39 | 39
2018-06-09 01:30 | 61 | 28 |  |  | 43260.0625 | 38 | 38
2018-06-09 02:00 | 62 | 28 |  |  | 43260.0833 | 39 | 38
2018-06-09 02:30 | 62 | 27 |  |  | 43260.1042 | 37 | 36
2018-06-09 03:00 | 62 | 26 |  |  | 43260.125 | 36 | 34
2018-06-09 03:30 | 62 | 25 |  |  | 43260.1458 | 35 | 34
2018-06-09 04:00 | 62 | 26 |  |  | 43260.1667 | 36 | 35
2018-06-09 04:30 | 62 | 28 |  |  | 43260.1875 | 39 | 38
2018-06-09 05:00 | 63 | 28 |  |  | 43260.2083 | 40 | 39
2018-06-09 05:30 | 64 | 30 |  |  | 43260.2292 | 42 | 41
2018-06-09 06:00 | 64 | 33 |  |  | 43260.25 | 45 | 44
2018-06-09 06:30 | 65 | 35 |  |  | 43260.2708 | 48 | 47
2018-06-09 07:00 | 67 | 38 |  |  | 43260.2917 | 53 | 53
2018-06-09 07:30 | 66 | 39 |  |  | 43260.3125 | 54 | 54
2018-06-09 08:00 | 70 | 40 |  |  | 43260.3333 | 59 | 57
2018-06-09 08:30 | 68 | 41 |  |  | 43260.3542 | 61 | 59
2018-06-09 09:00 | 63 | 41 |  |  | 43260.375 | 60 | 59
2018-06-09 09:30 | 60 | 36 |  |  | 43260.3958 | 57 | 56
2018-06-09 10:00 | 59 | 35 |  |  | 43260.4167 | 52 | 51
2018-06-09 10:30 | 58 | 36 |  |  | 43260.4375 | 52 | 51
2018-06-09 11:00 | 58 | 37 |  |  | 43260.4583 | 54 | 53
2018-06-09 11:30 | 58 | 36 |  |  | 43260.4792 | 51 | 50
2018-06-09 12:00 | 60 | 37 |  |  | 43260.5 | 51 | 50
2018-06-09 12:30 | 60 | 36 |  |  | 43260.5208 | 55 | 54
2018-06-09 13:00 | 63 | 33 |  |  | 43260.5417 | 51 | 49
2018-06-09 13:30 | 64 | 34 |  |  | 43260.5625 | 49 | 48
2018-06-09 14:00 | 63 | 33 |  |  | 43260.5833 | 49 | 47
2018-06-09 14:30 | 64 | 34 |  |  | 43260.6042 | 50 | 48
2018-06-09 15:00 | 65 | 35 |  |  | 43260.625 | 51 | 49
2018-06-09 15:30 | 64 | 33 |  |  | 43260.6458 | 51 | 49
2018-06-09 16:00 | 66 | 36 |  |  | 43260.6667 | 55 | 53
2018-06-09 16:30 | 68 | 41 |  |  | 43260.6875 | 60 | 58
2018-06-09 17:00 | 69 | 43 |  |  | 43260.7083 | 63 | 61
2018-06-09 17:30 | 70 | 46 |  |  | 43260.7292 | 65 | 63
2018-06-09 18:00 | 73 | 49 |  |  | 43260.75 | 67 | 65
2018-06-09 18:30 | 81 | 47 |  |  | 43260.7708 | 66 | 63
2018-06-09 19:00 | 80 | 48 |  |  | 43260.7917 | 67 | 64
2018-06-09 19:30 | 80 | 46 |  |  | 43260.8125 | 65 | 62
2018-06-09 20:00 | 79 | 46 |  |  | 43260.8333 | 65 | 61
2018-06-09 20:30 | 78 | 45 |  |  | 43260.8542 | 64 | 61
2018-06-09 21:00 | 77 | 43 |  |  | 43260.875 | 60 | 57
2018-06-09 21:30 | 76 | 41 |  |  | 43260.8958 | 58 | 54
2018-06-09 22:00 | 76 | 40 |  |  | 43260.9167 | 58 | 54
2018-06-09 22:30 | 77 | 41 |  |  | 43260.9375 | 59 | 56
2018-06-09 23:00 | 79 | 42 |  |  | 43260.9583 | 60 | 56
2018-06-09 23:30 | 78 | 40 |  |  | 43260.9792 | 57 | 52
2018-06-10 | 77 | 37 |  |  | 43261 | 55 | 50
2018-06-10 00:30 | 77 | 33 |  |  | 43261.0208 | 51 | 45
2018-06-10 01:00 | 76 | 31 |  |  | 43261.0417 | 48 | 41
2018-06-10 01:30 | 77 | 31 |  |  | 43261.0625 | 49 | 41
2018-06-10 02:00 | 78 | 30 |  |  | 43261.0833 | 49 | 41
2018-06-10 02:30 | 77 | 28 |  |  | 43261.1042 | 47 | 38
2018-06-10 03:00 | 77 | 28 |  |  | 43261.125 | 45 | 38
2018-06-10 03:30 | 77 | 27 |  |  | 43261.1458 | 44 | 37
2018-06-10 04:00 | 77 | 27 |  |  | 43261.1667 | 44 | 37
2018-06-10 04:30 | 77 | 28 |  |  | 43261.1875 | 45 | 38
2018-06-10 05:00 | 76 | 29 |  |  | 43261.2083 | 45 | 38
2018-06-10 05:30 | 75 | 29 |  |  | 43261.2292 | 46 | 39
2018-06-10 06:00 | 77 | 33 |  |  | 43261.25 | 49 | 43
2018-06-10 06:30 | 76 | 31 |  |  | 43261.2708 | 48 | 42
2018-06-10 07:00 | 76 | 31 |  |  | 43261.2917 | 49 | 44
2018-06-10 07:30 | 76 | 31 |  |  | 43261.3125 | 50 | 46
2018-06-10 08:00 | 75 | 33 |  |  | 43261.3333 | 50 | 46
2018-06-10 08:30 | 74 | 33 |  |  | 43261.3542 | 51 | 48
2018-06-10 09:00 | 73 | 32 |  |  | 43261.375 | 51 | 48
2018-06-10 09:30 | 72 | 31 |  |  | 43261.3958 | 50 | 47
2018-06-10 10:00 | 72 | 30 |  |  | 43261.4167 | 49 | 46
2018-06-10 10:30 | 72 | 32 |  |  | 43261.4375 | 50 | 47
2018-06-10 11:00 | 73 | 33 |  |  | 43261.4583 | 49 | 46
2018-06-10 11:30 | 72 | 32 |  |  | 43261.4792 | 51 | 47
2018-06-10 12:00 | 73 | 32 |  |  | 43261.5 | 52 | 48
2018-06-10 12:30 | 74 | 33 |  |  | 43261.5208 | 52 | 48
2018-06-10 13:00 | 74 | 32 |  |  | 43261.5417 | 51 | 48
2018-06-10 13:30 | 73 | 30 |  |  | 43261.5625 | 49 | 45
2018-06-10 14:00 | 76 | 37 |  |  | 43261.5833 | 52 | 49
2018-06-10 14:30 | 78 | 42 |  |  | 43261.6042 | 59 | 55
2018-06-10 15:00 | 79 | 44 |  |  | 43261.625 | 61 | 58
2018-06-10 15:30 | 79 | 44 |  |  | 43261.6458 | 63 | 59
2018-06-10 16:00 | 80 | 46 |  |  | 43261.6667 | 64 | 61
2018-06-10 16:30 | 80 | 46 |  |  | 43261.6875 | 64 | 61
2018-06-10 17:00 | 83 | 50 |  |  | 43261.7083 | 69 | 66
2018-06-10 17:30 | 85 | 55 |  |  | 43261.7292 | 73 | 70
2018-06-10 18:00 | 83 | 56 |  |  | 43261.75 | 75 | 73
2018-06-10 18:30 | 83 | 56 |  |  | 43261.7708 | 76 | 73
2018-06-10 19:00 | 84 | 58 |  |  | 43261.7917 | 77 | 75
2018-06-10 19:30 | 85 | 58 |  |  | 43261.8125 | 77 | 75
2018-06-10 20:00 | 84 | 57 |  |  | 43261.8333 | 75 | 73
2018-06-10 20:30 | 83 | 57 |  |  | 43261.8542 | 75 | 73
2018-06-10 21:00 | 80 | 54 |  |  | 43261.875 | 72 | 70
2018-06-10 21:30 | 79 | 51 |  |  | 43261.8958 | 70 | 67
2018-06-10 22:00 | 77 | 48 |  |  | 43261.9167 | 68 | 65
2018-06-10 22:30 | 78 | 49 |  |  | 43261.9375 | 69 | 66
2018-06-10 23:00 | 80 | 49 |  |  | 43261.9583 | 68 | 64
2018-06-10 23:30 | 78 | 47 |  |  | 43261.9792 | 64 | 61
2018-06-11 | 76 | 42 |  |  | 43262 | 60 | 56
2018-06-11 00:30 | 73 | 37 |  |  | 43262.0208 | 54 | 51
2018-06-11 01:00 | 72 | 34 |  |  | 43262.0417 | 49 | 46
2018-06-11 01:30 | 71 | 32 |  |  | 43262.0625 | 46 | 43
2018-06-11 02:00 | 71 | 29 |  |  | 43262.0833 | 45 | 41
2018-06-11 02:30 | 70 | 29 |  |  | 43262.1042 | 45 | 41
2018-06-11 03:00 | 71 | 31 |  |  | 43262.125 | 46 | 42
2018-06-11 03:30 | 71 | 31 |  |  | 43262.1458 | 47 | 43
2018-06-11 04:00 | 70 | 33 |  |  | 43262.1667 | 48 | 44
2018-06-11 04:30 | 71 | 36 |  |  | 43262.1875 | 50 | 47
2018-06-11 05:00 | 72 | 40 |  |  | 43262.2083 | 52 | 49
2018-06-11 05:30 | 73 | 45 |  |  | 43262.2292 | 56 | 55
2018-06-11 06:00 | 55 | 51 |  |  | 43262.25 | 64 | 63
2018-06-11 06:30 | 61 | 60 |  |  | 43262.2708 | 75 | 75
2018-06-11 07:00 | 68 | 67 |  |  | 43262.2917 | 86 | 86
2018-06-11 07:30 | 72 | 72 |  |  | 43262.3125 | 93 | 93
2018-06-11 08:00 | 69 | 68 |  |  | 43262.3333 | 91 | 91
2018-06-11 08:30 | 63 | 62 |  |  | 43262.3542 | 86 | 86
2018-06-11 09:00 | 59 | 58 |  |  | 43262.375 | 81 | 81
2018-06-11 09:30 | 57 | 56 |  |  | 43262.3958 | 79 | 79
2018-06-11 10:00 | 56 | 55 |  |  | 43262.4167 | 77 | 77
2018-06-11 10:30 | 54 | 54 |  |  | 43262.4375 | 74 | 74
2018-06-11 11:00 | 53 | 52 |  |  | 43262.4583 | 72 | 72
2018-06-11 11:30 | 54 | 54 |  |  | 43262.4792 | 74 | 74
2018-06-11 12:00 | 56 | 55 |  |  | 43262.5 | 77 | 77
2018-06-11 12:30 | 57 | 56 |  |  | 43262.5208 | 77 | 77
2018-06-11 13:00 | 57 | 56 |  |  | 43262.5417 | 77 | 77
2018-06-11 13:30 | 60 | 60 |  |  | 43262.5625 | 79 | 79
2018-06-11 14:00 | 61 | 60 |  |  | 43262.5833 | 81 | 81
2018-06-11 14:30 | 61 | 60 |  |  | 43262.6042 | 82 | 82
2018-06-11 15:00 | 62 | 62 |  |  | 43262.625 | 82 | 82
2018-06-11 15:30 | 64 | 64 |  |  | 43262.6458 | 84 | 84
2018-06-11 16:00 | 68 | 68 |  |  | 43262.6667 | 87 | 87
2018-06-11 16:30 | 67 | 67 |  |  | 43262.6875 | 85 | 85
2018-06-11 17:00 | 68 | 68 |  |  | 43262.7083 | 87 | 87
2018-06-11 17:30 | 69 | 69 |  |  | 43262.7292 | 89 | 89
2018-06-11 18:00 | 70 | 70 |  |  | 43262.75 | 89 | 89
2018-06-11 18:30 | 69 | 69 |  |  | 43262.7708 | 86 | 86
2018-06-11 19:00 | 70 | 69 |  |  | 43262.7917 | 86 | 86
2018-06-11 19:30 | 68 | 67 |  |  | 43262.8125 | 84 | 84
2018-06-11 20:00 | 69 | 67 |  |  | 43262.8333 | 83 | 83
2018-06-11 20:30 | 71 | 69 |  |  | 43262.8542 | 85 | 84
2018-06-11 21:00 | 67 | 65 |  |  | 43262.875 | 80 | 79
2018-06-11 21:30 | 64 | 61 |  |  | 43262.8958 | 75 | 74
2018-06-11 22:00 | 66 | 63 |  |  | 43262.9167 | 78 | 77
2018-06-11 22:30 | 63 | 60 |  |  | 43262.9375 | 75 | 74
2018-06-11 23:00 | 62 | 59 |  |  | 43262.9583 | 72 | 70
2018-06-11 23:30 | 58 | 54 |  |  | 43262.9792 | 68 | 66
2018-06-12 | 53 | 49 |  |  | 43263 | 63 | 61
2018-06-12 00:30 | 51 | 47 |  |  | 43263.0208 | 59 | 57
2018-06-12 01:00 | 48 | 43 |  |  | 43263.0417 | 56 | 53
2018-06-12 01:30 | 46 | 39 |  |  | 43263.0625 | 52 | 49
2018-06-12 02:00 | 46 | 39 |  |  | 43263.0833 | 51 | 48
2018-06-12 02:30 | 45 | 38 |  |  | 43263.1042 | 50 | 48
2018-06-12 03:00 | 44 | 38 |  |  | 43263.125 | 50 | 48
2018-06-12 03:30 | 44 | 38 |  |  | 43263.1458 | 50 | 48
2018-06-12 04:00 | 44 | 38 |  |  | 43263.1667 | 51 | 48
2018-06-12 04:30 | 45 | 40 |  |  | 43263.1875 | 51 | 49
2018-06-12 05:00 | 50 | 46 |  |  | 43263.2083 | 56 | 54
2018-06-12 05:30 | 53 | 50 |  |  | 43263.2292 | 61 | 60
2018-06-12 06:00 | 59 | 57 |  |  | 43263.25 | 69 | 68
2018-06-12 06:30 | 64 | 62 |  |  | 43263.2708 | 76 | 76
2018-06-12 07:00 | 68 | 66 |  |  | 43263.2917 | 85 | 85
2018-06-12 07:30 | 72 | 72 |  |  | 43263.3125 | 93 | 93
2018-06-12 08:00 | 70 | 69 |  |  | 43263.3333 | 93 | 93
2018-06-12 08:30 | 63 | 63 |  |  | 43263.3542 | 87 | 87
2018-06-12 09:00 | 57 | 57 |  |  | 43263.375 | 80 | 80
2018-06-12 09:30 | 58 | 58 |  |  | 43263.3958 | 82 | 81
2018-06-12 10:00 | 55 | 55 |  |  | 43263.4167 | 79 | 78
2018-06-12 10:30 | 54 | 54 |  |  | 43263.4375 | 76 | 76
2018-06-12 11:00 | 52 | 52 |  |  | 43263.4583 | 73 | 73
2018-06-12 11:30 | 50 | 50 |  |  | 43263.4792 | 70 | 70
2018-06-12 12:00 | 49 | 49 |  |  | 43263.5 | 70 | 70
2018-06-12 12:30 | 50 | 50 |  |  | 43263.5208 | 72 | 72
2018-06-12 13:00 | 50 | 50 |  |  | 43263.5417 | 72 | 71
2018-06-12 13:30 | 53 | 53 |  |  | 43263.5625 | 73 | 73
2018-06-12 14:00 | 54 | 54 |  |  | 43263.5833 | 70 | 70
2018-06-12 14:30 | 58 | 58 |  |  | 43263.6042 | 74 | 74
2018-06-12 15:00 | 59 | 59 |  |  | 43263.625 | 79 | 78
2018-06-12 15:30 | 63 | 63 |  |  | 43263.6458 | 80 | 80
2018-06-12 16:00 | 66 | 66 |  |  | 43263.6667 | 85 | 85
2018-06-12 16:30 | 69 | 69 |  |  | 43263.6875 | 87 | 87
2018-06-12 17:00 | 71 | 71 |  |  | 43263.7083 | 90 | 90
2018-06-12 17:30 | 73 | 73 |  |  | 43263.7292 | 92 | 92
2018-06-12 18:00 | 74 | 73 |  |  | 43263.75 | 93 | 92
2018-06-12 18:30 | 72 | 70 |  |  | 43263.7708 | 90 | 88
2018-06-12 19:00 | 74 | 73 |  |  | 43263.7917 | 92 | 90
2018-06-12 19:30 | 73 | 72 |  |  | 43263.8125 | 90 | 89
2018-06-12 20:00 | 70 | 70 |  |  | 43263.8333 | 86 | 86
2018-06-12 20:30 | 68 | 68 |  |  | 43263.8542 | 85 | 85
2018-06-12 21:00 | 66 | 65 |  |  | 43263.875 | 80 | 80
2018-06-12 21:30 | 63 | 62 |  |  | 43263.8958 | 75 | 75
2018-06-12 22:00 | 62 | 61 |  |  | 43263.9167 | 77 | 77
2018-06-12 22:30 | 62 | 61 |  |  | 43263.9375 | 75 | 74
2018-06-12 23:00 | 59 | 58 |  |  | 43263.9583 | 71 | 70
2018-06-12 23:30 | 56 | 55 |  |  | 43263.9792 | 67 | 67
2018-06-13 | 52 | 50 |  |  | 43264 | 62 | 62
2018-06-13 00:30 | 47 | 45 |  |  | 43264.0208 | 56 | 55
2018-06-13 01:00 | 42 | 40 |  |  | 43264.0417 | 51 | 50
2018-06-13 01:30 | 41 | 39 |  |  | 43264.0625 | 49 | 48
2018-06-13 02:00 | 40 | 39 |  |  | 43264.0833 | 47 | 46
2018-06-13 02:30 | 41 | 39 |  |  | 43264.1042 | 48 | 48
2018-06-13 03:00 | 42 | 40 |  |  | 43264.125 | 50 | 50
2018-06-13 03:30 | 42 | 40 |  |  | 43264.1458 | 51 | 50
2018-06-13 04:00 | 42 | 40 |  |  | 43264.1667 | 50 | 49
2018-06-13 04:30 | 44 | 42 |  |  | 43264.1875 | 51 | 51
2018-06-13 05:00 | 47 | 46 |  |  | 43264.2083 | 55 | 55
2018-06-13 05:30 | 52 | 51 |  |  | 43264.2292 | 61 | 60
2018-06-13 06:00 | 57 | 57 |  |  | 43264.25 | 67 | 67
2018-06-13 06:30 | 63 | 62 |  |  | 43264.2708 | 77 | 77
2018-06-13 07:00 | 67 | 67 |  |  | 43264.2917 | 85 | 85
2018-06-13 07:30 | 70 | 70 |  |  | 43264.3125 | 91 | 91
2018-06-13 08:00 | 70 | 70 |  |  | 43264.3333 | 91 | 91
2018-06-13 08:30 | 66 | 66 |  |  | 43264.3542 | 89 | 88
2018-06-13 09:00 | 63 | 63 |  |  | 43264.375 | 85 | 85
2018-06-13 09:30 | 61 | 61 |  |  | 43264.3958 | 84 | 83
2018-06-13 10:00 | 58 | 58 |  |  | 43264.4167 | 81 | 80
2018-06-13 10:30 | 60 | 60 |  |  | 43264.4375 | 76 | 76
2018-06-13 11:00 | 60 | 60 |  |  | 43264.4583 | 80 | 79
2018-06-13 11:30 | 61 | 61 |  |  | 43264.4792 | 82 | 82
2018-06-13 12:00 | 62 | 62 |  |  | 43264.5 | 83 | 83
2018-06-13 12:30 | 63 | 63 |  |  | 43264.5208 | 83 | 83
2018-06-13 13:00 | 64 | 64 |  |  | 43264.5417 | 86 | 85
2018-06-13 13:30 | 63 | 63 |  |  | 43264.5625 | 82 | 82
2018-06-13 14:00 | 63 | 63 |  |  | 43264.5833 | 84 | 83
2018-06-13 14:30 | 66 | 66 |  |  | 43264.6042 | 87 | 87
2018-06-13 15:00 | 64 | 64 |  |  | 43264.625 | 85 | 85
2018-06-13 15:30 | 67 | 67 |  |  | 43264.6458 | 89 | 88
2018-06-13 16:00 | 70 | 69 |  |  | 43264.6667 | 91 | 91
2018-06-13 16:30 | 70 | 69 |  |  | 43264.6875 | 92 | 91
2018-06-13 17:00 | 72 | 71 |  |  | 43264.7083 | 93 | 93
2018-06-13 17:30 | 73 | 73 |  |  | 43264.7292 | 93 | 93
2018-06-13 18:00 | 68 | 68 |  |  | 43264.75 | 88 | 88
2018-06-13 18:30 | 67 | 67 |  |  | 43264.7708 | 85 | 85
2018-06-13 19:00 | 68 | 68 |  |  | 43264.7917 | 87 | 86
2018-06-13 19:30 | 67 | 66 |  |  | 43264.8125 | 85 | 84
2018-06-13 20:00 | 66 | 65 |  |  | 43264.8333 | 83 | 83
2018-06-13 20:30 | 64 | 64 |  |  | 43264.8542 | 82 | 82
2018-06-13 21:00 | 63 | 62 |  |  | 43264.875 | 77 | 77
2018-06-13 21:30 | 59 | 58 |  |  | 43264.8958 | 73 | 73
2018-06-13 22:00 | 57 | 56 |  |  | 43264.9167 | 71 | 71
2018-06-13 22:30 | 56 | 55 |  |  | 43264.9375 | 70 | 70
2018-06-13 23:00 | 55 | 55 |  |  | 43264.9583 | 68 | 68
2018-06-13 23:30 | 53 | 53 |  |  | 43264.9792 | 65 | 65
2018-06-14 | 48 | 48 |  |  | 43265 | 60 | 60
2018-06-14 00:30 | 42 | 42 |  |  | 43265.0208 | 54 | 53
2018-06-14 01:00 | 40 | 39 |  |  | 43265.0417 | 50 | 50
2018-06-14 01:30 | 39 | 38 |  |  | 43265.0625 | 50 | 49
2018-06-14 02:00 | 40 | 39 |  |  | 43265.0833 | 49 | 48
2018-06-14 02:30 | 38 | 38 |  |  | 43265.1042 | 48 | 47
2018-06-14 03:00 | 38 | 37 |  |  | 43265.125 | 49 | 48
2018-06-14 03:30 | 40 | 39 |  |  | 43265.1458 | 51 | 50
2018-06-14 04:00 | 42 | 41 |  |  | 43265.1667 | 51 | 50
2018-06-14 04:30 | 44 | 43 |  |  | 43265.1875 | 54 | 53
2018-06-14 05:00 | 46 | 45 |  |  | 43265.2083 | 56 | 55
2018-06-14 05:30 | 49 | 49 |  |  | 43265.2292 | 60 | 59
2018-06-14 06:00 | 53 | 53 |  |  | 43265.25 | 65 | 65
2018-06-14 06:30 | 59 | 58 |  |  | 43265.2708 | 72 | 72
2018-06-14 07:00 | 61 | 61 |  |  | 43265.2917 | 78 | 78
2018-06-14 07:30 | 68 | 68 |  |  | 43265.3125 | 89 | 89
2018-06-14 08:00 | 69 | 68 |  |  | 43265.3333 | 90 | 89
2018-06-14 08:30 | 66 | 65 |  |  | 43265.3542 | 89 | 89
2018-06-14 09:00 | 65 | 64 |  |  | 43265.375 | 87 | 86
2018-06-14 09:30 | 60 | 59 |  |  | 43265.3958 | 84 | 84
2018-06-14 10:00 | 56 | 56 |  |  | 43265.4167 | 83 | 82
2018-06-14 10:30 | 62 | 61 |  |  | 43265.4375 | 87 | 86
2018-06-14 11:00 | 66 | 65 |  |  | 43265.4583 | 88 | 88
2018-06-14 11:30 | 63 | 62 |  |  | 43265.4792 | 85 | 85
2018-06-14 12:00 | 69 | 68 |  |  | 43265.5 | 89 | 89
2018-06-14 12:30 | 67 | 67 |  |  | 43265.5208 | 89 | 88
2018-06-14 13:00 | 63 | 62 |  |  | 43265.5417 | 87 | 86
2018-06-14 13:30 | 67 | 67 |  |  | 43265.5625 | 91 | 91
2018-06-14 14:00 | 69 | 68 |  |  | 43265.5833 | 92 | 92
2018-06-14 14:30 | 68 | 68 |  |  | 43265.6042 | 93 | 92
2018-06-14 15:00 | 67 | 66 |  |  | 43265.625 | 89 | 89
2018-06-14 15:30 | 66 | 66 |  |  | 43265.6458 | 87 | 87
2018-06-14 16:00 | 67 | 67 |  |  | 43265.6667 | 88 | 87
2018-06-14 16:30 | 67 | 67 |  |  | 43265.6875 | 87 | 87
2018-06-14 17:00 | 68 | 68 |  |  | 43265.7083 | 88 | 88
2018-06-14 17:30 | 70 | 70 |  |  | 43265.7292 | 90 | 90
2018-06-14 18:00 | 69 | 68 |  |  | 43265.75 | 89 | 88
2018-06-14 18:30 | 69 | 68 |  |  | 43265.7708 | 88 | 88
2018-06-14 19:00 | 69 | 69 |  |  | 43265.7917 | 88 | 88
2018-06-14 19:30 | 68 | 68 |  |  | 43265.8125 | 87 | 86
2018-06-14 20:00 | 66 | 66 |  |  | 43265.8333 | 85 | 84
2018-06-14 20:30 | 66 | 66 |  |  | 43265.8542 | 83 | 83
2018-06-14 21:00 | 62 | 62 |  |  | 43265.875 | 78 | 78
2018-06-14 21:30 | 59 | 59 |  |  | 43265.8958 | 74 | 74
2018-06-14 22:00 | 57 | 57 |  |  | 43265.9167 | 72 | 72
2018-06-14 22:30 | 56 | 56 |  |  | 43265.9375 | 70 | 70
2018-06-14 23:00 | 55 | 55 |  |  | 43265.9583 | 68 | 68
2018-06-14 23:30 | 51 | 51 |  |  | 43265.9792 | 63 | 63
2018-06-15 | 45 | 45 |  |  | 43266 | 59 | 58
2018-06-15 00:30 | 43 | 43 |  |  | 43266.0208 | 55 | 55
2018-06-15 01:00 | 41 | 41 |  |  | 43266.0417 | 52 | 51
2018-06-15 01:30 | 41 | 41 |  |  | 43266.0625 | 51 | 51
2018-06-15 02:00 | 39 | 39 |  |  | 43266.0833 | 48 | 48
2018-06-15 02:30 | 39 | 38 |  |  | 43266.1042 | 50 | 50
2018-06-15 03:00 | 39 | 39 |  |  | 43266.125 | 51 | 50
2018-06-15 03:30 | 41 | 41 |  |  | 43266.1458 | 52 | 51
2018-06-15 04:00 | 43 | 42 |  |  | 43266.1667 | 53 | 53
2018-06-15 04:30 | 45 | 45 |  |  | 43266.1875 | 55 | 55
2018-06-15 05:00 | 48 | 48 |  |  | 43266.2083 | 58 | 58
2018-06-15 05:30 | 51 | 51 |  |  | 43266.2292 | 62 | 62
2018-06-15 06:00 | 55 | 55 |  |  | 43266.25 | 67 | 66
2018-06-15 06:30 | 59 | 59 |  |  | 43266.2708 | 73 | 73
2018-06-15 07:00 | 60 | 59 |  |  | 43266.2917 | 78 | 78
2018-06-15 07:30 | 64 | 64 |  |  | 43266.3125 | 86 | 86
2018-06-15 08:00 | 64 | 64 |  |  | 43266.3333 | 86 | 86
2018-06-15 08:30 | 63 | 62 |  |  | 43266.3542 | 88 | 88
2018-06-15 09:00 | 60 | 60 |  |  | 43266.375 | 85 | 85
2018-06-15 09:30 | 58 | 58 |  |  | 43266.3958 | 81 | 81
2018-06-15 10:00 | 57 | 56 |  |  | 43266.4167 | 80 | 80
2018-06-15 10:30 | 55 | 54 |  |  | 43266.4375 | 78 | 78
2018-06-15 11:00 | 56 | 55 |  |  | 43266.4583 | 79 | 78
2018-06-15 11:30 | 56 | 55 |  |  | 43266.4792 | 79 | 78
2018-06-15 12:00 | 56 | 56 |  |  | 43266.5 | 79 | 79
2018-06-15 12:30 | 56 | 55 |  |  | 43266.5208 | 79 | 78
2018-06-15 13:00 | 55 | 55 |  |  | 43266.5417 | 77 | 77
2018-06-15 13:30 | 55 | 55 |  |  | 43266.5625 | 75 | 75
2018-06-15 14:00 | 57 | 57 |  |  | 43266.5833 | 78 | 77
2018-06-15 14:30 | 60 | 59 |  |  | 43266.6042 | 81 | 80
2018-06-15 15:00 | 61 | 61 |  |  | 43266.625 | 83 | 82
2018-06-15 15:30 | 63 | 62 |  |  | 43266.6458 | 85 | 84
2018-06-15 16:00 | 64 | 64 |  |  | 43266.6667 | 86 | 86
2018-06-15 16:30 | 64 | 63 |  |  | 43266.6875 | 85 | 85
2018-06-15 17:00 | 66 | 65 |  |  | 43266.7083 | 87 | 87
2018-06-15 17:30 | 62 | 61 |  |  | 43266.7292 | 84 | 84
2018-06-15 18:00 | 60 | 59 |  |  | 43266.75 | 82 | 82
2018-06-15 18:30 | 62 | 61 |  |  | 43266.7708 | 82 | 82
2018-06-15 19:00 | 62 | 62 |  |  | 43266.7917 | 82 | 82
2018-06-15 19:30 | 62 | 62 |  |  | 43266.8125 | 82 | 82
2018-06-15 20:00 | 62 | 62 |  |  | 43266.8333 | 80 | 80
2018-06-15 20:30 | 60 | 60 |  |  | 43266.8542 | 78 | 78
2018-06-15 21:00 | 58 | 58 |  |  | 43266.875 | 74 | 74
2018-06-15 21:30 | 55 | 55 |  |  | 43266.8958 | 69 | 69
2018-06-15 22:00 | 55 | 55 |  |  | 43266.9167 | 71 | 71
2018-06-15 22:30 | 55 | 54 |  |  | 43266.9375 | 70 | 70
2018-06-15 23:00 | 55 | 55 |  |  | 43266.9583 | 69 | 68
2018-06-15 23:30 | 52 | 52 |  |  | 43266.9792 | 66 | 65
2018-06-16 | 47 | 47 |  |  | 43267 | 61 | 60
2018-06-16 00:30 | 42 | 42 |  |  | 43267.0208 | 54 | 54
2018-06-16 01:00 | 40 | 40 |  |  | 43267.0417 | 51 | 50
2018-06-16 01:30 | 39 | 39 |  |  | 43267.0625 | 50 | 50
2018-06-16 02:00 | 38 | 38 |  |  | 43267.0833 | 49 | 49
2018-06-16 02:30 | 38 | 38 |  |  | 43267.1042 | 49 | 49
2018-06-16 03:00 | 41 | 41 |  |  | 43267.125 | 52 | 51
2018-06-16 03:30 | 42 | 42 |  |  | 43267.1458 | 53 | 53
2018-06-16 04:00 | 43 | 43 |  |  | 43267.1667 | 54 | 54
2018-06-16 04:30 | 44 | 44 |  |  | 43267.1875 | 55 | 55
2018-06-16 05:00 | 47 | 47 |  |  | 43267.2083 | 57 | 57
2018-06-16 05:30 | 49 | 49 |  |  | 43267.2292 | 58 | 58
2018-06-16 06:00 | 47 | 47 |  |  | 43267.25 | 57 | 56
2018-06-16 06:30 | 47 | 47 |  |  | 43267.2708 | 59 | 58
2018-06-16 07:00 | 48 | 48 |  |  | 43267.2917 | 62 | 61
2018-06-16 07:30 | 49 | 49 |  |  | 43267.3125 | 63 | 63
2018-06-16 08:00 | 48 | 48 |  |  | 43267.3333 | 63 | 63
2018-06-16 08:30 | 47 | 47 |  |  | 43267.3542 | 64 | 64
2018-06-16 09:00 | 46 | 46 |  |  | 43267.375 | 63 | 63
2018-06-16 09:30 | 43 | 43 |  |  | 43267.3958 | 61 | 61
2018-06-16 10:00 | 43 | 43 |  |  | 43267.4167 | 60 | 59
2018-06-16 10:30 | 44 | 43 |  |  | 43267.4375 | 58 | 58
2018-06-16 11:00 | 41 | 41 |  |  | 43267.4583 | 56 | 56
2018-06-16 11:30 | 41 | 41 |  |  | 43267.4792 | 56 | 56
2018-06-16 12:00 | 41 | 41 |  |  | 43267.5 | 55 | 55
2018-06-16 12:30 | 41 | 41 |  |  | 43267.5208 | 55 | 55
2018-06-16 13:00 | 40 | 40 |  |  | 43267.5417 | 53 | 53
2018-06-16 13:30 | 41 | 41 |  |  | 43267.5625 | 54 | 54
2018-06-16 14:00 | 42 | 42 |  |  | 43267.5833 | 54 | 54
2018-06-16 14:30 | 42 | 42 |  |  | 43267.6042 | 54 | 54
2018-06-16 15:00 | 42 | 42 |  |  | 43267.625 | 55 | 55
2018-06-16 15:30 | 42 | 42 |  |  | 43267.6458 | 56 | 56
2018-06-16 16:00 | 45 | 45 |  |  | 43267.6667 | 59 | 59
2018-06-16 16:30 | 48 | 47 |  |  | 43267.6875 | 63 | 63
2018-06-16 17:00 | 50 | 50 |  |  | 43267.7083 | 68 | 68
2018-06-16 17:30 | 55 | 55 |  |  | 43267.7292 | 74 | 74
2018-06-16 18:00 | 56 | 56 |  |  | 43267.75 | 75 | 75
2018-06-16 18:30 | 57 | 57 |  |  | 43267.7708 | 75 | 75
2018-06-16 19:00 | 58 | 58 |  |  | 43267.7917 | 76 | 76
2018-06-16 19:30 | 58 | 57 |  |  | 43267.8125 | 75 | 75
2018-06-16 20:00 | 56 | 56 |  |  | 43267.8333 | 74 | 73
2018-06-16 20:30 | 54 | 54 |  |  | 43267.8542 | 71 | 71
2018-06-16 21:00 | 52 | 52 |  |  | 43267.875 | 68 | 68
2018-06-16 21:30 | 50 | 50 |  |  | 43267.8958 | 66 | 66
2018-06-16 22:00 | 49 | 48 |  |  | 43267.9167 | 65 | 65
2018-06-16 22:30 | 52 | 51 |  |  | 43267.9375 | 67 | 67
2018-06-16 23:00 | 52 | 52 |  |  | 43267.9583 | 66 | 65
2018-06-16 23:30 | 51 | 50 |  |  | 43267.9792 | 64 | 63
2018-06-17 | 46 | 45 |  |  | 43268 | 59 | 58
2018-06-17 00:30 | 43 | 42 |  |  | 43268.0208 | 55 | 53
2018-06-17 01:00 | 39 | 38 |  |  | 43268.0417 | 51 | 50
2018-06-17 01:30 | 40 | 38 |  |  | 43268.0625 | 51 | 50
2018-06-17 02:00 | 39 | 37 |  |  | 43268.0833 | 50 | 49
2018-06-17 02:30 | 38 | 37 |  |  | 43268.1042 | 49 | 48
2018-06-17 03:00 | 38 | 37 |  |  | 43268.125 | 48 | 47
2018-06-17 03:30 | 39 | 37 |  |  | 43268.1458 | 48 | 48
2018-06-17 04:00 | 39 | 38 |  |  | 43268.1667 | 50 | 49
2018-06-17 04:30 | 42 | 41 |  |  | 43268.1875 | 51 | 51
2018-06-17 05:00 | 43 | 42 |  |  | 43268.2083 | 51 | 51
2018-06-17 05:30 | 42 | 42 |  |  | 43268.2292 | 52 | 51
2018-06-17 06:00 | 42 | 41 |  |  | 43268.25 | 52 | 51
2018-06-17 06:30 | 44 | 43 |  |  | 43268.2708 | 55 | 55
2018-06-17 07:00 | 46 | 45 |  |  | 43268.2917 | 57 | 57
2018-06-17 07:30 | 48 | 48 |  |  | 43268.3125 | 61 | 61
2018-06-17 08:00 | 50 | 50 |  |  | 43268.3333 | 62 | 62
2018-06-17 08:30 | 48 | 48 |  |  | 43268.3542 | 61 | 61
2018-06-17 09:00 | 47 | 47 |  |  | 43268.375 | 62 | 61
2018-06-17 09:30 | 46 | 46 |  |  | 43268.3958 | 61 | 61
2018-06-17 10:00 | 44 | 44 |  |  | 43268.4167 | 59 | 59
2018-06-17 10:30 | 41 | 41 |  |  | 43268.4375 | 56 | 56
2018-06-17 11:00 | 39 | 39 |  |  | 43268.4583 | 54 | 54
2018-06-17 11:30 | 36 | 36 |  |  | 43268.4792 | 50 | 50
2018-06-17 12:00 | 35 | 34 |  |  | 43268.5 | 49 | 49
2018-06-17 12:30 | 34 | 33 |  |  | 43268.5208 | 48 | 48
2018-06-17 13:00 | 35 | 35 |  |  | 43268.5417 | 50 | 50
2018-06-17 13:30 | 36 | 36 |  |  | 43268.5625 | 51 | 50
2018-06-17 14:00 | 38 | 38 |  |  | 43268.5833 | 53 | 53
2018-06-17 14:30 | 40 | 39 |  |  | 43268.6042 | 54 | 54
2018-06-17 15:00 | 40 | 40 |  |  | 43268.625 | 56 | 56
2018-06-17 15:30 | 44 | 44 |  |  | 43268.6458 | 60 | 60
2018-06-17 16:00 | 46 | 46 |  |  | 43268.6667 | 63 | 63
2018-06-17 16:30 | 51 | 50 |  |  | 43268.6875 | 68 | 68
2018-06-17 17:00 | 54 | 54 |  |  | 43268.7083 | 72 | 72
2018-06-17 17:30 | 59 | 59 |  |  | 43268.7292 | 77 | 77
2018-06-17 18:00 | 62 | 61 |  |  | 43268.75 | 80 | 80
2018-06-17 18:30 | 63 | 62 |  |  | 43268.7708 | 80 | 80
2018-06-17 19:00 | 65 | 64 |  |  | 43268.7917 | 81 | 81
2018-06-17 19:30 | 64 | 64 |  |  | 43268.8125 | 82 | 82
2018-06-17 20:00 | 64 | 64 |  |  | 43268.8333 | 81 | 81
2018-06-17 20:30 | 64 | 64 |  |  | 43268.8542 | 81 | 81
2018-06-17 21:00 | 62 | 62 |  |  | 43268.875 | 77 | 77
2018-06-17 21:30 | 59 | 59 |  |  | 43268.8958 | 73 | 73
2018-06-17 22:00 | 58 | 58 |  |  | 43268.9167 | 74 | 74
2018-06-17 22:30 | 58 | 57 |  |  | 43268.9375 | 73 | 73
2018-06-17 23:00 | 57 | 57 |  |  | 43268.9583 | 72 | 71
2018-06-17 23:30 | 53 | 52 |  |  | 43268.9792 | 67 | 66
2018-06-18 | 47 | 47 |  |  | 43269 | 60 | 60
2018-06-18 00:30 | 45 | 44 |  |  | 43269.0208 | 57 | 56
2018-06-18 01:00 | 43 | 42 |  |  | 43269.0417 | 56 | 54
2018-06-18 01:30 | 42 | 41 |  |  | 43269.0625 | 54 | 52
2018-06-18 02:00 | 42 | 40 |  |  | 43269.0833 | 53 | 52
2018-06-18 02:30 | 40 | 39 |  |  | 43269.1042 | 52 | 50
2018-06-18 03:00 | 39 | 37 |  |  | 43269.125 | 50 | 48
2018-06-18 03:30 | 40 | 39 |  |  | 43269.1458 | 50 | 49
2018-06-18 04:00 | 40 | 39 |  |  | 43269.1667 | 51 | 50
2018-06-18 04:30 | 43 | 42 |  |  | 43269.1875 | 53 | 51
2018-06-18 05:00 | 46 | 45 |  |  | 43269.2083 | 55 | 54
2018-06-18 05:30 | 51 | 50 |  |  | 43269.2292 | 60 | 59
2018-06-18 06:00 | 56 | 56 |  |  | 43269.25 | 66 | 66
2018-06-18 06:30 | 64 | 64 |  |  | 43269.2708 | 77 | 77
2018-06-18 07:00 | 74 | 74 |  |  | 43269.2917 | 91 | 91
2018-06-18 07:30 | 78 | 78 |  |  | 43269.3125 | 100 | 100
2018-06-18 08:00 | 79 | 79 |  |  | 43269.3333 | 88 | 87
2018-06-18 08:30 | 77 | 77 |  |  | 43269.3542 | 78 | 78
2018-06-18 09:00 | 73 | 73 |  |  | 43269.375 | 80 | 79
2018-06-18 09:30 | 63 | 63 |  |  | 43269.3958 | 84 | 83
2018-06-18 10:00 | 61 | 61 |  |  | 43269.4167 | 85 | 84
2018-06-18 10:30 | 59 | 59 |  |  | 43269.4375 | 82 | 82
2018-06-18 11:00 | 58 | 58 |  |  | 43269.4583 | 81 | 81
2018-06-18 11:30 | 59 | 59 |  |  | 43269.4792 | 82 | 81
2018-06-18 12:00 | 62 | 61 |  |  | 43269.5 | 84 | 83
2018-06-18 12:30 | 60 | 59 |  |  | 43269.5208 | 83 | 82
2018-06-18 13:00 | 59 | 57 |  |  | 43269.5417 | 82 | 80
2018-06-18 13:30 | 59 | 58 |  |  | 43269.5625 | 83 | 81
2018-06-18 14:00 | 60 | 59 |  |  | 43269.5833 | 83 | 82
2018-06-18 14:30 | 61 | 60 |  |  | 43269.6042 | 84 | 83
2018-06-18 15:00 | 61 | 60 |  |  | 43269.625 | 84 | 83
2018-06-18 15:30 | 61 | 60 |  |  | 43269.6458 | 84 | 84
2018-06-18 16:00 | 63 | 62 |  |  | 43269.6667 | 86 | 86
2018-06-18 16:30 | 69 | 68 |  |  | 43269.6875 | 92 | 91
2018-06-18 17:00 | 77 | 76 |  |  | 43269.7083 | 99 | 99
2018-06-18 17:30 | 82 | 82 |  |  | 43269.7292 | 106 | 106
2018-06-18 18:00 | 78 | 78 |  |  | 43269.75 | 103 | 102
2018-06-18 18:30 | 79 | 79 |  |  | 43269.7708 | 102 | 101
2018-06-18 19:00 | 81 | 81 |  |  | 43269.7917 | 104 | 103
2018-06-18 19:30 | 81 | 81 |  |  | 43269.8125 | 102 | 102
2018-06-18 20:00 | 80 | 80 |  |  | 43269.8333 | 100 | 100
2018-06-18 20:30 | 79 | 79 |  |  | 43269.8542 | 99 | 99
2018-06-18 21:00 | 78 | 78 |  |  | 43269.875 | 96 | 96
2018-06-18 21:30 | 74 | 73 |  |  | 43269.8958 | 90 | 90
2018-06-18 22:00 | 71 | 71 |  |  | 43269.9167 | 89 | 89
2018-06-18 22:30 | 66 | 65 |  |  | 43269.9375 | 83 | 83
2018-06-18 23:00 | 62 | 60 |  |  | 43269.9583 | 76 | 76
2018-06-18 23:30 | 54 | 54 |  |  | 43269.9792 | 69 | 69
2018-06-19 | 51 | 50 |  |  | 43270 | 64 | 64
2018-06-19 00:30 | 48 | 47 |  |  | 43270.0208 | 60 | 60
2018-06-19 01:00 | 43 | 43 |  |  | 43270.0417 | 55 | 55
2018-06-19 01:30 | 40 | 40 |  |  | 43270.0625 | 52 | 52
2018-06-19 02:00 | 40 | 39 |  |  | 43270.0833 | 51 | 51
2018-06-19 02:30 | 39 | 39 |  |  | 43270.1042 | 50 | 50
2018-06-19 03:00 | 39 | 38 |  |  | 43270.125 | 49 | 49
2018-06-19 03:30 | 39 | 38 |  |  | 43270.1458 | 49 | 49
2018-06-19 04:00 | 39 | 38 |  |  | 43270.1667 | 50 | 50
2018-06-19 04:30 | 41 | 40 |  |  | 43270.1875 | 52 | 52
2018-06-19 05:00 | 44 | 44 |  |  | 43270.2083 | 56 | 56
2018-06-19 05:30 | 50 | 49 |  |  | 43270.2292 | 63 | 63
2018-06-19 06:00 | 57 | 56 |  |  | 43270.25 | 69 | 69
2018-06-19 06:30 | 62 | 61 |  |  | 43270.2708 | 83 | 82
2018-06-19 07:00 | 65 | 64 |  |  | 43270.2917 | 92 | 92
2018-06-19 07:30 | 69 | 68 |  |  | 43270.3125 | 101 | 101
2018-06-19 08:00 | 67 | 65 |  |  | 43270.3333 | 99 | 99
2018-06-19 08:30 | 62 | 61 |  |  | 43270.3542 | 94 | 94
2018-06-19 09:00 | 59 | 57 |  |  | 43270.375 | 90 | 89
2018-06-19 09:30 | 60 | 56 |  |  | 43270.3958 | 88 | 86
2018-06-19 10:00 | 61 | 57 |  |  | 43270.4167 | 89 | 86
2018-06-19 10:30 | 61 | 56 |  |  | 43270.4375 | 87 | 85
2018-06-19 11:00 | 61 | 56 |  |  | 43270.4583 | 87 | 84
2018-06-19 11:30 | 60 | 55 |  |  | 43270.4792 | 85 | 83
2018-06-19 12:00 | 59 | 55 |  |  | 43270.5 | 84 | 81
2018-06-19 12:30 | 59 | 54 |  |  | 43270.5208 | 83 | 81
2018-06-19 13:00 | 58 | 53 |  |  | 43270.5417 | 84 | 81
2018-06-19 13:30 | 59 | 54 |  |  | 43270.5625 | 85 | 82
2018-06-19 14:00 | 61 | 55 |  |  | 43270.5833 | 85 | 82
2018-06-19 14:30 | 61 | 55 |  |  | 43270.6042 | 85 | 83
2018-06-19 15:00 | 62 | 57 |  |  | 43270.625 | 85 | 83
2018-06-19 15:30 | 62 | 58 |  |  | 43270.6458 | 86 | 84
2018-06-19 16:00 | 64 | 60 |  |  | 43270.6667 | 88 | 86
2018-06-19 16:30 | 65 | 61 |  |  | 43270.6875 | 89 | 87
2018-06-19 17:00 | 67 | 64 |  |  | 43270.7083 | 91 | 90
2018-06-19 17:30 | 71 | 68 |  |  | 43270.7292 | 96 | 95
2018-06-19 18:00 | 71 | 71 |  |  | 43270.75 | 97 | 97
2018-06-19 18:30 | 71 | 70 |  |  | 43270.7708 | 95 | 95
2018-06-19 19:00 | 73 | 72 |  |  | 43270.7917 | 97 | 97
2018-06-19 19:30 | 71 | 71 |  |  | 43270.8125 | 95 | 95
2018-06-19 20:00 | 70 | 70 |  |  | 43270.8333 | 94 | 93
2018-06-19 20:30 | 71 | 70 |  |  | 43270.8542 | 93 | 93
2018-06-19 21:00 | 68 | 68 |  |  | 43270.875 | 90 | 89
2018-06-19 21:30 | 65 | 65 |  |  | 43270.8958 | 86 | 85
2018-06-19 22:00 | 63 | 63 |  |  | 43270.9167 | 84 | 83
2018-06-19 22:30 | 61 | 59 |  |  | 43270.9375 | 79 | 79
2018-06-19 23:00 | 60 | 58 |  |  | 43270.9583 | 76 | 76
2018-06-19 23:30 | 55 | 54 |  |  | 43270.9792 | 72 | 72
2018-06-20 | 49 | 49 |  |  | 43271 | 65 | 65
2018-06-20 00:30 | 47 | 47 |  |  | 43271.0208 | 62 | 62
2018-06-20 01:00 | 43 | 43 |  |  | 43271.0417 | 57 | 57
2018-06-20 01:30 | 39 | 38 |  |  | 43271.0625 | 52 | 52
2018-06-20 02:00 | 37 | 37 |  |  | 43271.0833 | 50 | 50
2018-06-20 02:30 | 39 | 39 |  |  | 43271.1042 | 52 | 52
2018-06-20 03:00 | 40 | 40 |  |  | 43271.125 | 53 | 53
2018-06-20 03:30 | 41 | 41 |  |  | 43271.1458 | 53 | 53
2018-06-20 04:00 | 41 | 41 |  |  | 43271.1667 | 53 | 53
2018-06-20 04:30 | 42 | 42 |  |  | 43271.1875 | 54 | 53
2018-06-20 05:00 | 45 | 44 |  |  | 43271.2083 | 56 | 56
2018-06-20 05:30 | 51 | 51 |  |  | 43271.2292 | 63 | 63
2018-06-20 06:00 | 58 | 57 |  |  | 43271.25 | 72 | 72
2018-06-20 06:30 | 60 | 58 |  |  | 43271.2708 | 81 | 81
2018-06-20 07:00 | 65 | 63 |  |  | 43271.2917 | 92 | 92
2018-06-20 07:30 | 72 | 70 |  |  | 43271.3125 | 102 | 101
2018-06-20 08:00 | 72 | 69 |  |  | 43271.3333 | 102 | 101
2018-06-20 08:30 | 69 | 67 |  |  | 43271.3542 | 98 | 97
2018-06-20 09:00 | 65 | 63 |  |  | 43271.375 | 94 | 93
2018-06-20 09:30 | 64 | 61 |  |  | 43271.3958 | 91 | 90
2018-06-20 10:00 | 61 | 58 |  |  | 43271.4167 | 86 | 84
2018-06-20 10:30 | 60 | 55 |  |  | 43271.4375 | 85 | 83
2018-06-20 11:00 | 60 | 56 |  |  | 43271.4583 | 85 | 83
2018-06-20 11:30 | 60 | 56 |  |  | 43271.4792 | 84 | 82
2018-06-20 12:00 | 61 | 57 |  |  | 43271.5 | 85 | 84
2018-06-20 12:30 | 60 | 57 |  |  | 43271.5208 | 85 | 84
2018-06-20 13:00 | 60 | 56 |  |  | 43271.5417 | 85 | 84
2018-06-20 13:30 | 63 | 59 |  |  | 43271.5625 | 85 | 83
2018-06-20 14:00 | 62 | 58 |  |  | 43271.5833 | 86 | 84
2018-06-20 14:30 | 61 | 57 |  |  | 43271.6042 | 82 | 81
2018-06-20 15:00 | 62 | 59 |  |  | 43271.625 | 82 | 81
2018-06-20 15:30 | 62 | 60 |  |  | 43271.6458 | 81 | 81
2018-06-20 16:00 | 62 | 60 |  |  | 43271.6667 | 81 | 80
2018-06-20 16:30 | 60 | 58 |  |  | 43271.6875 | 79 | 78
2018-06-20 17:00 | 63 | 61 |  |  | 43271.7083 | 81 | 80
2018-06-20 17:30 | 66 | 64 |  |  | 43271.7292 | 85 | 85
2018-06-20 18:00 | 65 | 64 |  |  | 43271.75 | 85 | 85
2018-06-20 18:30 | 65 | 65 |  |  | 43271.7708 | 83 | 83
2018-06-20 19:00 | 69 | 68 |  |  | 43271.7917 | 85 | 85
2018-06-20 19:30 | 68 | 67 |  |  | 43271.8125 | 84 | 84
2018-06-20 20:00 | 67 | 65 |  |  | 43271.8333 | 83 | 82
2018-06-20 20:30 | 64 | 62 |  |  | 43271.8542 | 79 | 79
2018-06-20 21:00 | 63 | 61 |  |  | 43271.875 | 77 | 77
2018-06-20 21:30 | 59 | 58 |  |  | 43271.8958 | 73 | 73
2018-06-20 22:00 | 58 | 57 |  |  | 43271.9167 | 74 | 73
2018-06-20 22:30 | 57 | 55 |  |  | 43271.9375 | 72 | 72
2018-06-20 23:00 | 57 | 55 |  |  | 43271.9583 | 70 | 70
2018-06-20 23:30 | 52 | 51 |  |  | 43271.9792 | 64 | 64
2018-06-21 | 48 | 47 |  |  | 43272 | 61 | 61
2018-06-21 00:30 | 47 | 46 |  |  | 43272.0208 | 58 | 58
2018-06-21 01:00 | 43 | 43 |  |  | 43272.0417 | 54 | 54
2018-06-21 01:30 | 39 | 39 |  |  | 43272.0625 | 50 | 50
2018-06-21 02:00 | 38 | 38 |  |  | 43272.0833 | 48 | 48
2018-06-21 02:30 | 39 | 38 |  |  | 43272.1042 | 48 | 48
2018-06-21 03:00 | 37 | 37 |  |  | 43272.125 | 47 | 47
2018-06-21 03:30 | 39 | 39 |  |  | 43272.1458 | 48 | 48
2018-06-21 04:00 | 40 | 40 |  |  | 43272.1667 | 48 | 48
2018-06-21 04:30 | 41 | 41 |  |  | 43272.1875 | 49 | 49
2018-06-21 05:00 | 44 | 43 |  |  | 43272.2083 | 51 | 51
2018-06-21 05:30 | 49 | 47 |  |  | 43272.2292 | 56 | 56
2018-06-21 06:00 | 54 | 51 |  |  | 43272.25 | 63 | 63
2018-06-21 06:30 | 64 | 60 |  |  | 43272.2708 | 76 | 75
2018-06-21 07:00 | 67 | 65 |  |  | 43272.2917 | 85 | 85
2018-06-21 07:30 | 71 | 70 |  |  | 43272.3125 | 93 | 93
2018-06-21 08:00 | 66 | 65 |  |  | 43272.3333 | 89 | 89
2018-06-21 08:30 | 58 | 56 |  |  | 43272.3542 | 82 | 82
2018-06-21 09:00 | 54 | 52 |  |  | 43272.375 | 78 | 78
2018-06-21 09:30 | 52 | 50 |  |  | 43272.3958 | 73 | 73
2018-06-21 10:00 | 50 | 47 |  |  | 43272.4167 | 70 | 70
2018-06-21 10:30 | 48 | 45 |  |  | 43272.4375 | 67 | 67
2018-06-21 11:00 | 48 | 45 |  |  | 43272.4583 | 66 | 65
2018-06-21 11:30 | 48 | 45 |  |  | 43272.4792 | 65 | 65
2018-06-21 12:00 | 48 | 45 |  |  | 43272.5 | 64 | 64
2018-06-21 12:30 | 49 | 47 |  |  | 43272.5208 | 66 | 66
2018-06-21 13:00 | 51 | 48 |  |  | 43272.5417 | 70 | 70
2018-06-21 13:30 | 51 | 49 |  |  | 43272.5625 | 71 | 71
2018-06-21 14:00 | 56 | 54 |  |  | 43272.5833 | 75 | 75
2018-06-21 14:30 | 57 | 55 |  |  | 43272.6042 | 76 | 76
2018-06-21 15:00 | 51 | 49 |  |  | 43272.625 | 69 | 68
2018-06-21 15:30 | 49 | 47 |  |  | 43272.6458 | 66 | 66
2018-06-21 16:00 | 53 | 50 |  |  | 43272.6667 | 70 | 70
2018-06-21 16:30 | 59 | 57 |  |  | 43272.6875 | 75 | 75
2018-06-21 17:00 | 64 | 62 |  |  | 43272.7083 | 80 | 80
2018-06-21 17:30 | 66 | 64 |  |  | 43272.7292 | 83 | 83
2018-06-21 18:00 | 65 | 64 |  |  | 43272.75 | 83 | 83
2018-06-21 18:30 | 64 | 64 |  |  | 43272.7708 | 81 | 81
2018-06-21 19:00 | 62 | 61 |  |  | 43272.7917 | 80 | 80
2018-06-21 19:30 | 59 | 59 |  |  | 43272.8125 | 77 | 76
2018-06-21 20:00 | 59 | 59 |  |  | 43272.8333 | 76 | 76
2018-06-21 20:30 | 58 | 58 |  |  | 43272.8542 | 75 | 74
2018-06-21 21:00 | 56 | 55 |  |  | 43272.875 | 71 | 70
2018-06-21 21:30 | 53 | 53 |  |  | 43272.8958 | 67 | 66
2018-06-21 22:00 | 53 | 53 |  |  | 43272.9167 | 68 | 68
2018-06-21 22:30 | 50 | 50 |  |  | 43272.9375 | 64 | 63
2018-06-21 23:00 | 50 | 49 |  |  | 43272.9583 | 63 | 62
2018-06-21 23:30 | 48 | 46 |  |  | 43272.9792 | 58 | 58
2018-06-22 | 42 | 41 |  |  | 43273 | 53 | 53
2018-06-22 00:30 | 39 | 37 |  |  | 43273.0208 | 48 | 47
2018-06-22 01:00 | 37 | 34 |  |  | 43273.0417 | 45 | 43
2018-06-22 01:30 | 37 | 32 |  |  | 43273.0625 | 44 | 41
2018-06-22 02:00 | 36 | 32 |  |  | 43273.0833 | 42 | 40
2018-06-22 02:30 | 35 | 31 |  |  | 43273.1042 | 41 | 39
2018-06-22 03:00 | 35 | 31 |  |  | 43273.125 | 42 | 40
2018-06-22 03:30 | 37 | 33 |  |  | 43273.1458 | 44 | 42
2018-06-22 04:00 | 39 | 35 |  |  | 43273.1667 | 45 | 43
2018-06-22 04:30 | 41 | 37 |  |  | 43273.1875 | 47 | 45
2018-06-22 05:00 | 46 | 43 |  |  | 43273.2083 | 51 | 49
2018-06-22 05:30 | 46 | 44 |  |  | 43273.2292 | 53 | 52
2018-06-22 06:00 | 51 | 51 |  |  | 43273.25 | 59 | 59
2018-06-22 06:30 | 58 | 57 |  |  | 43273.2708 | 71 | 70
2018-06-22 07:00 | 62 | 61 |  |  | 43273.2917 | 79 | 79
2018-06-22 07:30 | 67 | 67 |  |  | 43273.3125 | 87 | 87
2018-06-22 08:00 | 66 | 66 |  |  | 43273.3333 | 87 | 87
2018-06-22 08:30 | 60 | 60 |  |  | 43273.3542 | 83 | 83
2018-06-22 09:00 | 54 | 54 |  |  | 43273.375 | 77 | 77
2018-06-22 09:30 | 51 | 51 |  |  | 43273.3958 | 73 | 73
2018-06-22 10:00 | 47 | 47 |  |  | 43273.4167 | 68 | 68
2018-06-22 10:30 | 42 | 42 |  |  | 43273.4375 | 63 | 63
2018-06-22 11:00 | 42 | 42 |  |  | 43273.4583 | 64 | 64
2018-06-22 11:30 | 42 | 41 |  |  | 43273.4792 | 64 | 63
2018-06-22 12:00 | 44 | 44 |  |  | 43273.5 | 65 | 65
2018-06-22 12:30 | 44 | 44 |  |  | 43273.5208 | 64 | 64
2018-06-22 13:00 | 43 | 43 |  |  | 43273.5417 | 65 | 65
2018-06-22 13:30 | 44 | 43 |  |  | 43273.5625 | 66 | 66
2018-06-22 14:00 | 45 | 44 |  |  | 43273.5833 | 66 | 66
2018-06-22 14:30 | 46 | 46 |  |  | 43273.6042 | 65 | 65
2018-06-22 15:00 | 44 | 43 |  |  | 43273.625 | 63 | 63
2018-06-22 15:30 | 44 | 44 |  |  | 43273.6458 | 64 | 64
2018-06-22 16:00 | 44 | 44 |  |  | 43273.6667 | 65 | 65
2018-06-22 16:30 | 46 | 45 |  |  | 43273.6875 | 66 | 66
2018-06-22 17:00 | 51 | 51 |  |  | 43273.7083 | 71 | 71
2018-06-22 17:30 | 52 | 52 |  |  | 43273.7292 | 73 | 73
2018-06-22 18:00 | 52 | 51 |  |  | 43273.75 | 73 | 73
2018-06-22 18:30 | 50 | 50 |  |  | 43273.7708 | 71 | 71
2018-06-22 19:00 | 51 | 50 |  |  | 43273.7917 | 71 | 71
2018-06-22 19:30 | 49 | 49 |  |  | 43273.8125 | 70 | 69
2018-06-22 20:00 | 50 | 50 |  |  | 43273.8333 | 69 | 69
2018-06-22 20:30 | 50 | 50 |  |  | 43273.8542 | 68 | 68
2018-06-22 21:00 | 47 | 47 |  |  | 43273.875 | 64 | 64
2018-06-22 21:30 | 43 | 43 |  |  | 43273.8958 | 60 | 60
2018-06-22 22:00 | 41 | 41 |  |  | 43273.9167 | 59 | 59
2018-06-22 22:30 | 42 | 42 |  |  | 43273.9375 | 59 | 59
2018-06-22 23:00 | 43 | 42 |  |  | 43273.9583 | 58 | 57
2018-06-22 23:30 | 39 | 38 |  |  | 43273.9792 | 54 | 53
2018-06-23 | 36 | 34 |  |  | 43274 | 49 | 48
2018-06-23 00:30 | 34 | 32 |  |  | 43274.0208 | 45 | 44
2018-06-23 01:00 | 33 | 30 |  |  | 43274.0417 | 44 | 42
2018-06-23 01:30 | 33 | 30 |  |  | 43274.0625 | 42 | 40
2018-06-23 02:00 | 30 | 26 |  |  | 43274.0833 | 39 | 37
2018-06-23 02:30 | 31 | 27 |  |  | 43274.1042 | 40 | 38
2018-06-23 03:00 | 33 | 26 |  |  | 43274.125 | 41 | 38
2018-06-23 03:30 | 34 | 29 |  |  | 43274.1458 | 40 | 38
2018-06-23 04:00 | 34 | 29 |  |  | 43274.1667 | 41 | 39
2018-06-23 04:30 | 36 | 31 |  |  | 43274.1875 | 43 | 41
2018-06-23 05:00 | 38 | 33 |  |  | 43274.2083 | 46 | 45
2018-06-23 05:30 | 40 | 36 |  |  | 43274.2292 | 49 | 47
2018-06-23 06:00 | 43 | 39 |  |  | 43274.25 | 51 | 50
2018-06-23 06:30 | 42 | 39 |  |  | 43274.2708 | 53 | 52
2018-06-23 07:00 | 42 | 40 |  |  | 43274.2917 | 54 | 53
2018-06-23 07:30 | 43 | 41 |  |  | 43274.3125 | 57 | 56
2018-06-23 08:00 | 40 | 38 |  |  | 43274.3333 | 56 | 56
2018-06-23 08:30 | 39 | 37 |  |  | 43274.3542 | 54 | 54
2018-06-23 09:00 | 38 | 36 |  |  | 43274.375 | 54 | 54
2018-06-23 09:30 | 37 | 34 |  |  | 43274.3958 | 53 | 52
2018-06-23 10:00 | 36 | 33 |  |  | 43274.4167 | 51 | 50
2018-06-23 10:30 | 35 | 32 |  |  | 43274.4375 | 48 | 48
2018-06-23 11:00 | 35 | 32 |  |  | 43274.4583 | 48 | 48
2018-06-23 11:30 | 36 | 33 |  |  | 43274.4792 | 47 | 47
2018-06-23 12:00 | 37 | 35 |  |  | 43274.5 | 50 | 49
2018-06-23 12:30 | 39 | 36 |  |  | 43274.5208 | 51 | 51
2018-06-23 13:00 | 38 | 35 |  |  | 43274.5417 | 52 | 52
2018-06-23 13:30 | 40 | 37 |  |  | 43274.5625 | 53 | 53
2018-06-23 14:00 | 41 | 38 |  |  | 43274.5833 | 53 | 53
2018-06-23 14:30 | 42 | 39 |  |  | 43274.6042 | 54 | 53
2018-06-23 15:00 | 42 | 39 |  |  | 43274.625 | 54 | 54
2018-06-23 15:30 | 44 | 41 |  |  | 43274.6458 | 58 | 58
2018-06-23 16:00 | 45 | 42 |  |  | 43274.6667 | 60 | 59
2018-06-23 16:30 | 46 | 43 |  |  | 43274.6875 | 61 | 61
2018-06-23 17:00 | 45 | 43 |  |  | 43274.7083 | 61 | 61
2018-06-23 17:30 | 48 | 45 |  |  | 43274.7292 | 65 | 65
2018-06-23 18:00 | 50 | 48 |  |  | 43274.75 | 66 | 65
2018-06-23 18:30 | 49 | 46 |  |  | 43274.7708 | 66 | 65
2018-06-23 19:00 | 52 | 49 |  |  | 43274.7917 | 68 | 67
2018-06-23 19:30 | 52 | 49 |  |  | 43274.8125 | 68 | 67
2018-06-23 20:00 | 50 | 47 |  |  | 43274.8333 | 66 | 65
2018-06-23 20:30 | 48 | 45 |  |  | 43274.8542 | 63 | 62
2018-06-23 21:00 | 45 | 42 |  |  | 43274.875 | 60 | 59
2018-06-23 21:30 | 45 | 41 |  |  | 43274.8958 | 58 | 58
2018-06-23 22:00 | 43 | 41 |  |  | 43274.9167 | 58 | 58
2018-06-23 22:30 | 44 | 42 |  |  | 43274.9375 | 58 | 58
2018-06-23 23:00 | 44 | 42 |  |  | 43274.9583 | 57 | 56
2018-06-23 23:30 | 42 | 39 |  |  | 43274.9792 | 55 | 54
2018-06-24 | 39 | 36 |  |  | 43275 | 51 | 50
2018-06-24 00:30 | 40 | 36 |  |  | 43275.0208 | 50 | 49
2018-06-24 01:00 | 40 | 36 |  |  | 43275.0417 | 49 | 48
2018-06-24 01:30 | 37 | 33 |  |  | 43275.0625 | 47 | 46
2018-06-24 02:00 | 37 | 33 |  |  | 43275.0833 | 45 | 44
2018-06-24 02:30 | 37 | 32 |  |  | 43275.1042 | 45 | 43
2018-06-24 03:00 | 35 | 31 |  |  | 43275.125 | 43 | 41
2018-06-24 03:30 | 35 | 30 |  |  | 43275.1458 | 42 | 40
2018-06-24 04:00 | 33 | 28 |  |  | 43275.1667 | 41 | 39
2018-06-24 04:30 | 35 | 30 |  |  | 43275.1875 | 43 | 41
2018-06-24 05:00 | 38 | 33 |  |  | 43275.2083 | 46 | 44
2018-06-24 05:30 | 40 | 35 |  |  | 43275.2292 | 50 | 47
2018-06-24 06:00 | 41 | 36 |  |  | 43275.25 | 51 | 49
2018-06-24 06:30 | 41 | 37 |  |  | 43275.2708 | 51 | 49
2018-06-24 07:00 | 42 | 37 |  |  | 43275.2917 | 53 | 52
2018-06-24 07:30 | 44 | 39 |  |  | 43275.3125 | 56 | 55
2018-06-24 08:00 | 43 | 40 |  |  | 43275.3333 | 56 | 55
2018-06-24 08:30 | 41 | 38 |  |  | 43275.3542 | 55 | 54
2018-06-24 09:00 | 38 | 35 |  |  | 43275.375 | 54 | 53
2018-06-24 09:30 | 37 | 35 |  |  | 43275.3958 | 52 | 51
2018-06-24 10:00 | 38 | 35 |  |  | 43275.4167 | 51 | 51
2018-06-24 10:30 | 39 | 36 |  |  | 43275.4375 | 53 | 52
2018-06-24 11:00 | 40 | 37 |  |  | 43275.4583 | 52 | 51
2018-06-24 11:30 | 39 | 36 |  |  | 43275.4792 | 50 | 49
2018-06-24 12:00 | 38 | 35 |  |  | 43275.5 | 50 | 49
2018-06-24 12:30 | 40 | 36 |  |  | 43275.5208 | 50 | 50
2018-06-24 13:00 | 40 | 36 |  |  | 43275.5417 | 50 | 49
2018-06-24 13:30 | 39 | 35 |  |  | 43275.5625 | 51 | 50
2018-06-24 14:00 | 38 | 34 |  |  | 43275.5833 | 50 | 49
2018-06-24 14:30 | 40 | 36 |  |  | 43275.6042 | 52 | 51
2018-06-24 15:00 | 41 | 38 |  |  | 43275.625 | 53 | 52
2018-06-24 15:30 | 42 | 38 |  |  | 43275.6458 | 55 | 54
2018-06-24 16:00 | 45 | 42 |  |  | 43275.6667 | 59 | 59
2018-06-24 16:30 | 46 | 43 |  |  | 43275.6875 | 61 | 60
2018-06-24 17:00 | 46 | 43 |  |  | 43275.7083 | 63 | 62
2018-06-24 17:30 | 51 | 49 |  |  | 43275.7292 | 69 | 69
2018-06-24 18:00 | 52 | 51 |  |  | 43275.75 | 71 | 70
2018-06-24 18:30 | 53 | 52 |  |  | 43275.7708 | 71 | 71
2018-06-24 19:00 | 54 | 52 |  |  | 43275.7917 | 73 | 73
2018-06-24 19:30 | 54 | 52 |  |  | 43275.8125 | 72 | 72
2018-06-24 20:00 | 52 | 50 |  |  | 43275.8333 | 71 | 70
2018-06-24 20:30 | 53 | 51 |  |  | 43275.8542 | 72 | 71
2018-06-24 21:00 | 51 | 49 |  |  | 43275.875 | 68 | 67
2018-06-24 21:30 | 50 | 49 |  |  | 43275.8958 | 67 | 66
2018-06-24 22:00 | 50 | 49 |  |  | 43275.9167 | 67 | 67
2018-06-24 22:30 | 50 | 48 |  |  | 43275.9375 | 66 | 66
2018-06-24 23:00 | 50 | 48 |  |  | 43275.9583 | 64 | 63
2018-06-24 23:30 | 48 | 45 |  |  | 43275.9792 | 61 | 60
2018-06-25 | 44 | 41 |  |  | 43276 | 57 | 57
2018-06-25 00:30 | 42 | 39 |  |  | 43276.0208 | 53 | 52
2018-06-25 01:00 | 41 | 38 |  |  | 43276.0417 | 51 | 51
2018-06-25 01:30 | 41 | 38 |  |  | 43276.0625 | 50 | 50
2018-06-25 02:00 | 39 | 36 |  |  | 43276.0833 | 48 | 48
2018-06-25 02:30 | 37 | 34 |  |  | 43276.1042 | 47 | 46
2018-06-25 03:00 | 36 | 32 |  |  | 43276.125 | 45 | 44
2018-06-25 03:30 | 36 | 32 |  |  | 43276.1458 | 44 | 44
2018-06-25 04:00 | 36 | 32 |  |  | 43276.1667 | 45 | 44
2018-06-25 04:30 | 38 | 35 |  |  | 43276.1875 | 47 | 46
2018-06-25 05:00 | 41 | 38 |  |  | 43276.2083 | 49 | 49
2018-06-25 05:30 | 46 | 45 |  |  | 43276.2292 | 56 | 55
2018-06-25 06:00 | 49 | 48 |  |  | 43276.25 | 60 | 60
2018-06-25 06:30 | 53 | 51 |  |  | 43276.2708 | 68 | 67
2018-06-25 07:00 | 56 | 53 |  |  | 43276.2917 | 75 | 74
2018-06-25 07:30 | 64 | 63 |  |  | 43276.3125 | 89 | 88
2018-06-25 08:00 | 63 | 63 |  |  | 43276.3333 | 90 | 88
2018-06-25 08:30 | 61 | 61 |  |  | 43276.3542 | 88 | 85
2018-06-25 09:00 | 59 | 59 |  |  | 43276.375 | 87 | 84
2018-06-25 09:30 | 58 | 58 |  |  | 43276.3958 | 89 | 86
2018-06-25 10:00 | 56 | 56 |  |  | 43276.4167 | 82 | 79
2018-06-25 10:30 | 51 | 50 |  |  | 43276.4375 | 75 | 73
2018-06-25 11:00 | 51 | 51 |  |  | 43276.4583 | 74 | 72
2018-06-25 11:30 | 54 | 54 |  |  | 43276.4792 | 78 | 75
2018-06-25 12:00 | 53 | 53 |  |  | 43276.5 | 78 | 75
2018-06-25 12:30 | 56 | 56 |  |  | 43276.5208 | 81 | 78
2018-06-25 13:00 | 57 | 57 |  |  | 43276.5417 | 77 | 75
2018-06-25 13:30 | 58 | 58 |  |  | 43276.5625 | 81 | 79
2018-06-25 14:00 | 59 | 59 |  |  | 43276.5833 | 79 | 76
2018-06-25 14:30 | 55 | 55 |  |  | 43276.6042 | 78 | 76
2018-06-25 15:00 | 53 | 52 |  |  | 43276.625 | 79 | 77
2018-06-25 15:30 | 56 | 56 |  |  | 43276.6458 | 78 | 76
2018-06-25 16:00 | 59 | 59 |  |  | 43276.6667 | 80 | 78
2018-06-25 16:30 | 65 | 61 |  |  | 43276.6875 | 87 | 82
2018-06-25 17:00 | 69 | 62 |  |  | 43276.7083 | 91 | 85
2018-06-25 17:30 | 74 | 65 |  |  | 43276.7292 | 94 | 89
2018-06-25 18:00 | 73 | 63 |  |  | 43276.75 | 90 | 87
2018-06-25 18:30 | 71 | 60 |  |  | 43276.7708 | 87 | 83
2018-06-25 19:00 | 69 | 60 |  |  | 43276.7917 | 86 | 83
2018-06-25 19:30 | 65 | 60 |  |  | 43276.8125 | 81 | 80
2018-06-25 20:00 | 64 | 59 |  |  | 43276.8333 | 80 | 79
2018-06-25 20:30 | 63 | 59 |  |  | 43276.8542 | 81 | 78
2018-06-25 21:00 | 60 | 55 |  |  | 43276.875 | 72 | 72
2018-06-25 21:30 | 52 | 51 |  |  | 43276.8958 | 66 | 65
2018-06-25 22:00 | 51 | 48 |  |  | 43276.9167 | 65 | 65
2018-06-25 22:30 | 45 | 43 |  |  | 43276.9375 | 60 | 60
2018-06-25 23:00 | 47 | 44 |  |  | 43276.9583 | 59 | 59
2018-06-25 23:30 | 44 | 41 |  |  | 43276.9792 | 57 | 56
2018-06-26 | 45 | 42 |  |  | 43277 | 55 | 54
2018-06-26 00:30 | 42 | 39 |  |  | 43277.0208 | 52 | 51
2018-06-26 01:00 | 40 | 37 |  |  | 43277.0417 | 49 | 48
2018-06-26 01:30 | 40 | 36 |  |  | 43277.0625 | 49 | 47
2018-06-26 02:00 | 40 | 37 |  |  | 43277.0833 | 49 | 48
2018-06-26 02:30 | 41 | 37 |  |  | 43277.1042 | 50 | 49
2018-06-26 03:00 | 40 | 36 |  |  | 43277.125 | 50 | 48
2018-06-26 03:30 | 40 | 36 |  |  | 43277.1458 | 49 | 47
2018-06-26 04:00 | 41 | 38 |  |  | 43277.1667 | 51 | 50
2018-06-26 04:30 | 42 | 39 |  |  | 43277.1875 | 51 | 49
2018-06-26 05:00 | 46 | 43 |  |  | 43277.2083 | 55 | 53
2018-06-26 05:30 | 48 | 46 |  |  | 43277.2292 | 58 | 57
2018-06-26 06:00 | 50 | 48 |  |  | 43277.25 | 61 | 61
2018-06-26 06:30 | 52 | 51 |  |  | 43277.2708 | 66 | 66
2018-06-26 07:00 | 54 | 53 |  |  | 43277.2917 | 73 | 73
2018-06-26 07:30 | 55 | 55 |  |  | 43277.3125 | 81 | 81
2018-06-26 08:00 | 52 | 52 |  |  | 43277.3333 | 80 | 80
2018-06-26 08:30 | 49 | 49 |  |  | 43277.3542 | 77 | 77
2018-06-26 09:00 | 50 | 50 |  |  | 43277.375 | 78 | 78
2018-06-26 09:30 | 49 | 49 |  |  | 43277.3958 | 74 | 74
2018-06-26 10:00 | 48 | 48 |  |  | 43277.4167 | 73 | 73
2018-06-26 10:30 | 48 | 48 |  |  | 43277.4375 | 70 | 69
2018-06-26 11:00 | 46 | 46 |  |  | 43277.4583 | 72 | 72
2018-06-26 11:30 | 49 | 49 |  |  | 43277.4792 | 73 | 73
2018-06-26 12:00 | 48 | 48 |  |  | 43277.5 | 71 | 71
2018-06-26 12:30 | 44 | 44 |  |  | 43277.5208 | 69 | 69
2018-06-26 13:00 | 45 | 45 |  |  | 43277.5417 | 69 | 69
2018-06-26 13:30 | 49 | 49 |  |  | 43277.5625 | 71 | 70
2018-06-26 14:00 | 48 | 48 |  |  | 43277.5833 | 71 | 71
2018-06-26 14:30 | 51 | 51 |  |  | 43277.6042 | 75 | 74
2018-06-26 15:00 | 52 | 52 |  |  | 43277.625 | 74 | 74
2018-06-26 15:30 | 53 | 53 |  |  | 43277.6458 | 76 | 76
2018-06-26 16:00 | 58 | 57 |  |  | 43277.6667 | 79 | 79
2018-06-26 16:30 | 58 | 58 |  |  | 43277.6875 | 79 | 79
2018-06-26 17:00 | 61 | 60 |  |  | 43277.7083 | 82 | 82
2018-06-26 17:30 | 64 | 64 |  |  | 43277.7292 | 85 | 85
2018-06-26 18:00 | 63 | 62 |  |  | 43277.75 | 83 | 83
2018-06-26 18:30 | 61 | 60 |  |  | 43277.7708 | 80 | 79
2018-06-26 19:00 | 62 | 62 |  |  | 43277.7917 | 81 | 81
2018-06-26 19:30 | 61 | 60 |  |  | 43277.8125 | 78 | 78
2018-06-26 20:00 | 60 | 59 |  |  | 43277.8333 | 77 | 77
2018-06-26 20:30 | 59 | 59 |  |  | 43277.8542 | 77 | 77
2018-06-26 21:00 | 57 | 56 |  |  | 43277.875 | 72 | 72
2018-06-26 21:30 | 54 | 53 |  |  | 43277.8958 | 69 | 68
2018-06-26 22:00 | 52 | 51 |  |  | 43277.9167 | 68 | 67
2018-06-26 22:30 | 48 | 48 |  |  | 43277.9375 | 65 | 64
2018-06-26 23:00 | 49 | 48 |  |  | 43277.9583 | 62 | 62
2018-06-26 23:30 | 46 | 45 |  |  | 43277.9792 | 59 | 58
2018-06-27 | 45 | 44 |  |  | 43278 | 57 | 56
2018-06-27 00:30 | 43 | 42 |  |  | 43278.0208 | 55 | 54
2018-06-27 01:00 | 41 | 39 |  |  | 43278.0417 | 52 | 51
2018-06-27 01:30 | 41 | 39 |  |  | 43278.0625 | 51 | 50
2018-06-27 02:00 | 41 | 40 |  |  | 43278.0833 | 51 | 51
2018-06-27 02:30 | 41 | 38 |  |  | 43278.1042 | 51 | 50
2018-06-27 03:00 | 40 | 38 |  |  | 43278.125 | 49 | 48
2018-06-27 03:30 | 39 | 36 |  |  | 43278.1458 | 48 | 47
2018-06-27 04:00 | 39 | 36 |  |  | 43278.1667 | 48 | 47
2018-06-27 04:30 | 40 | 38 |  |  | 43278.1875 | 49 | 48
2018-06-27 05:00 | 42 | 40 |  |  | 43278.2083 | 50 | 50
2018-06-27 05:30 | 46 | 45 |  |  | 43278.2292 | 56 | 55
2018-06-27 06:00 | 51 | 50 |  |  | 43278.25 | 62 | 61
2018-06-27 06:30 | 52 | 51 |  |  | 43278.2708 | 66 | 65
2018-06-27 07:00 | 51 | 50 |  |  | 43278.2917 | 72 | 72
2018-06-27 07:30 | 55 | 54 |  |  | 43278.3125 | 80 | 80
2018-06-27 08:00 | 54 | 54 |  |  | 43278.3333 | 81 | 81
2018-06-27 08:30 | 53 | 53 |  |  | 43278.3542 | 80 | 80
2018-06-27 09:00 | 54 | 54 |  |  | 43278.375 | 82 | 82
2018-06-27 09:30 | 53 | 53 |  |  | 43278.3958 | 79 | 78
2018-06-27 10:00 | 52 | 51 |  |  | 43278.4167 | 77 | 77
2018-06-27 10:30 | 53 | 53 |  |  | 43278.4375 | 79 | 78
2018-06-27 11:00 | 54 | 54 |  |  | 43278.4583 | 80 | 79
2018-06-27 11:30 | 56 | 56 |  |  | 43278.4792 | 81 | 80
2018-06-27 12:00 | 56 | 56 |  |  | 43278.5 | 81 | 80
2018-06-27 12:30 | 54 | 54 |  |  | 43278.5208 | 80 | 79
2018-06-27 13:00 | 54 | 54 |  |  | 43278.5417 | 79 | 79
2018-06-27 13:30 | 54 | 54 |  |  | 43278.5625 | 79 | 78
2018-06-27 14:00 | 54 | 54 |  |  | 43278.5833 | 78 | 78
2018-06-27 14:30 | 54 | 54 |  |  | 43278.6042 | 78 | 77
2018-06-27 15:00 | 55 | 55 |  |  | 43278.625 | 78 | 77
2018-06-27 15:30 | 58 | 58 |  |  | 43278.6458 | 80 | 79
2018-06-27 16:00 | 60 | 60 |  |  | 43278.6667 | 81 | 81
2018-06-27 16:30 | 60 | 60 |  |  | 43278.6875 | 82 | 82
2018-06-27 17:00 | 62 | 62 |  |  | 43278.7083 | 86 | 86
2018-06-27 17:30 | 67 | 66 |  |  | 43278.7292 | 90 | 90
2018-06-27 18:00 | 64 | 62 |  |  | 43278.75 | 86 | 85
2018-06-27 18:30 | 63 | 61 |  |  | 43278.7708 | 83 | 81
2018-06-27 19:00 | 64 | 62 |  |  | 43278.7917 | 84 | 83
2018-06-27 19:30 | 64 | 63 |  |  | 43278.8125 | 83 | 81
2018-06-27 20:00 | 62 | 61 |  |  | 43278.8333 | 81 | 79
2018-06-27 20:30 | 60 | 58 |  |  | 43278.8542 | 80 | 77
2018-06-27 21:00 | 58 | 57 |  |  | 43278.875 | 75 | 74
2018-06-27 21:30 | 54 | 53 |  |  | 43278.8958 | 69 | 68
2018-06-27 22:00 | 55 | 54 |  |  | 43278.9167 | 71 | 70
2018-06-27 22:30 | 50 | 48 |  |  | 43278.9375 | 65 | 65
2018-06-27 23:00 | 48 | 47 |  |  | 43278.9583 | 61 | 60
2018-06-27 23:30 | 49 | 48 |  |  | 43278.9792 | 62 | 61
2018-06-28 | 44 | 41 |  |  | 43279 | 57 | 55
2018-06-28 00:30 | 42 | 40 |  |  | 43279.0208 | 55 | 54
2018-06-28 01:00 | 43 | 40 |  |  | 43279.0417 | 53 | 51
2018-06-28 01:30 | 41 | 38 |  |  | 43279.0625 | 51 | 49
2018-06-28 02:00 | 39 | 36 |  |  | 43279.0833 | 50 | 48
2018-06-28 02:30 | 39 | 36 |  |  | 43279.1042 | 48 | 47
2018-06-28 03:00 | 38 | 35 |  |  | 43279.125 | 48 | 46
2018-06-28 03:30 | 37 | 34 |  |  | 43279.1458 | 47 | 45
2018-06-28 04:00 | 38 | 35 |  |  | 43279.1667 | 47 | 46
2018-06-28 04:30 | 40 | 37 |  |  | 43279.1875 | 49 | 47
2018-06-28 05:00 | 42 | 39 |  |  | 43279.2083 | 52 | 51
2018-06-28 05:30 | 46 | 44 |  |  | 43279.2292 | 57 | 56
2018-06-28 06:00 | 52 | 50 |  |  | 43279.25 | 64 | 63
2018-06-28 06:30 | 56 | 55 |  |  | 43279.2708 | 73 | 72
2018-06-28 07:00 | 54 | 53 |  |  | 43279.2917 | 77 | 77
2018-06-28 07:30 | 57 | 56 |  |  | 43279.3125 | 85 | 84
2018-06-28 08:00 | 56 | 54 |  |  | 43279.3333 | 83 | 82
2018-06-28 08:30 | 55 | 54 |  |  | 43279.3542 | 82 | 81
2018-06-28 09:00 | 53 | 52 |  |  | 43279.375 | 77 | 77
2018-06-28 09:30 | 51 | 50 |  |  | 43279.3958 | 74 | 73
2018-06-28 10:00 | 50 | 49 |  |  | 43279.4167 | 74 | 73
2018-06-28 10:30 | 49 | 48 |  |  | 43279.4375 | 72 | 72
2018-06-28 11:00 | 49 | 48 |  |  | 43279.4583 | 72 | 72
2018-06-28 11:30 | 47 | 47 |  |  | 43279.4792 | 71 | 71
2018-06-28 12:00 | 49 | 48 |  |  | 43279.5 | 72 | 72
2018-06-28 12:30 | 52 | 52 |  |  | 43279.5208 | 74 | 74
2018-06-28 13:00 | 52 | 52 |  |  | 43279.5417 | 73 | 73
2018-06-28 13:30 | 50 | 50 |  |  | 43279.5625 | 75 | 74
2018-06-28 14:00 | 53 | 53 |  |  | 43279.5833 | 76 | 76
2018-06-28 14:30 | 52 | 52 |  |  | 43279.6042 | 73 | 73
2018-06-28 15:00 | 53 | 53 |  |  | 43279.625 | 74 | 74
2018-06-28 15:30 | 52 | 51 |  |  | 43279.6458 | 74 | 74
2018-06-28 16:00 | 54 | 54 |  |  | 43279.6667 | 76 | 76
2018-06-28 16:30 | 56 | 55 |  |  | 43279.6875 | 79 | 79
2018-06-28 17:00 | 59 | 58 |  |  | 43279.7083 | 81 | 81
2018-06-28 17:30 | 61 | 60 |  |  | 43279.7292 | 82 | 82
2018-06-28 18:00 | 61 | 60 |  |  | 43279.75 | 82 | 82
2018-06-28 18:30 | 60 | 59 |  |  | 43279.7708 | 80 | 79
2018-06-28 19:00 | 63 | 62 |  |  | 43279.7917 | 83 | 82
2018-06-28 19:30 | 63 | 62 |  |  | 43279.8125 | 81 | 81
2018-06-28 20:00 | 61 | 60 |  |  | 43279.8333 | 79 | 78
2018-06-28 20:30 | 61 | 60 |  |  | 43279.8542 | 78 | 77
2018-06-28 21:00 | 62 | 61 |  |  | 43279.875 | 78 | 77
2018-06-28 21:30 | 61 | 60 |  |  | 43279.8958 | 75 | 73
2018-06-28 22:00 | 59 | 58 |  |  | 43279.9167 | 74 | 73
2018-06-28 22:30 | 57 | 56 |  |  | 43279.9375 | 72 | 70
2018-06-28 23:00 | 56 | 54 |  |  | 43279.9583 | 69 | 66
2018-06-28 23:30 | 52 | 49 |  |  | 43279.9792 | 64 | 62
2018-06-29 | 47 | 44 |  |  | 43280 | 58 | 56
2018-06-29 00:30 | 44 | 41 |  |  | 43280.0208 | 54 | 52
2018-06-29 01:00 | 44 | 41 |  |  | 43280.0417 | 53 | 51
2018-06-29 01:30 | 44 | 40 |  |  | 43280.0625 | 53 | 51
2018-06-29 02:00 | 44 | 40 |  |  | 43280.0833 | 53 | 51
2018-06-29 02:30 | 45 | 41 |  |  | 43280.1042 | 54 | 51
2018-06-29 03:00 | 45 | 41 |  |  | 43280.125 | 54 | 51
2018-06-29 03:30 | 45 | 41 |  |  | 43280.1458 | 54 | 51
2018-06-29 04:00 | 45 | 42 |  |  | 43280.1667 | 55 | 52
2018-06-29 04:30 | 47 | 43 |  |  | 43280.1875 | 56 | 53
2018-06-29 05:00 | 50 | 46 |  |  | 43280.2083 | 59 | 57
2018-06-29 05:30 | 53 | 50 |  |  | 43280.2292 | 64 | 63
2018-06-29 06:00 | 56 | 54 |  |  | 43280.25 | 69 | 67
2018-06-29 06:30 | 61 | 60 |  |  | 43280.2708 | 77 | 77
2018-06-29 07:00 | 58 | 57 |  |  | 43280.2917 | 83 | 83
2018-06-29 07:30 | 63 | 62 |  |  | 43280.3125 | 90 | 90
2018-06-29 08:00 | 63 | 61 |  |  | 43280.3333 | 91 | 91
2018-06-29 08:30 | 62 | 60 |  |  | 43280.3542 | 91 | 90
2018-06-29 09:00 | 61 | 59 |  |  | 43280.375 | 87 | 87
2018-06-29 09:30 | 57 | 56 |  |  | 43280.3958 | 81 | 81
2018-06-29 10:00 | 54 | 54 |  |  | 43280.4167 | 79 | 78
2018-06-29 10:30 | 52 | 51 |  |  | 43280.4375 | 73 | 73
2018-06-29 11:00 | 50 | 50 |  |  | 43280.4583 | 71 | 71
2018-06-29 11:30 | 49 | 49 |  |  | 43280.4792 | 71 | 71
2018-06-29 12:00 | 50 | 49 |  |  | 43280.5 | 73 | 73
2018-06-29 12:30 | 50 | 50 |  |  | 43280.5208 | 74 | 73
2018-06-29 13:00 | 51 | 50 |  |  | 43280.5417 | 75 | 75
2018-06-29 13:30 | 53 | 52 |  |  | 43280.5625 | 76 | 76
2018-06-29 14:00 | 56 | 56 |  |  | 43280.5833 | 78 | 78
2018-06-29 14:30 | 57 | 56 |  |  | 43280.6042 | 79 | 79
2018-06-29 15:00 | 58 | 57 |  |  | 43280.625 | 80 | 80
2018-06-29 15:30 | 59 | 59 |  |  | 43280.6458 | 80 | 80
2018-06-29 16:00 | 59 | 59 |  |  | 43280.6667 | 80 | 79
2018-06-29 16:30 | 60 | 59 |  |  | 43280.6875 | 79 | 79
2018-06-29 17:00 | 61 | 60 |  |  | 43280.7083 | 82 | 82
2018-06-29 17:30 | 64 | 63 |  |  | 43280.7292 | 85 | 85
2018-06-29 18:00 | 65 | 63 |  |  | 43280.75 | 85 | 84
2018-06-29 18:30 | 60 | 59 |  |  | 43280.7708 | 79 | 78
2018-06-29 19:00 | 61 | 59 |  |  | 43280.7917 | 79 | 78
2018-06-29 19:30 | 62 | 60 |  |  | 43280.8125 | 79 | 79
2018-06-29 20:00 | 62 | 60 |  |  | 43280.8333 | 79 | 79
2018-06-29 20:30 | 60 | 58 |  |  | 43280.8542 | 77 | 76
2018-06-29 21:00 | 58 | 56 |  |  | 43280.875 | 74 | 73
2018-06-29 21:30 | 54 | 53 |  |  | 43280.8958 | 70 | 69
2018-06-29 22:00 | 54 | 52 |  |  | 43280.9167 | 69 | 68
2018-06-29 22:30 | 52 | 50 |  |  | 43280.9375 | 67 | 66
2018-06-29 23:00 | 51 | 50 |  |  | 43280.9583 | 64 | 63
2018-06-29 23:30 | 48 | 45 |  |  | 43280.9792 | 59 | 58
2018-06-30 | 44 | 42 |  |  | 43281 | 56 | 55
2018-06-30 00:30 | 43 | 40 |  |  | 43281.0208 | 54 | 53
2018-06-30 01:00 | 45 | 42 |  |  | 43281.0417 | 55 | 54
2018-06-30 01:30 | 47 | 43 |  |  | 43281.0625 | 56 | 54
2018-06-30 02:00 | 46 | 42 |  |  | 43281.0833 | 55 | 54
2018-06-30 02:30 | 46 | 41 |  |  | 43281.1042 | 54 | 52
2018-06-30 03:00 | 45 | 40 |  |  | 43281.125 | 54 | 52
2018-06-30 03:30 | 44 | 40 |  |  | 43281.1458 | 53 | 51
2018-06-30 04:00 | 44 | 40 |  |  | 43281.1667 | 53 | 51
2018-06-30 04:30 | 44 | 39 |  |  | 43281.1875 | 52 | 51
2018-06-30 05:00 | 44 | 40 |  |  | 43281.2083 | 53 | 52
2018-06-30 05:30 | 45 | 41 |  |  | 43281.2292 | 55 | 53
2018-06-30 06:00 | 46 | 43 |  |  | 43281.25 | 57 | 55
2018-06-30 06:30 | 49 | 46 |  |  | 43281.2708 | 60 | 59
2018-06-30 07:00 | 46 | 43 |  |  | 43281.2917 | 59 | 58
2018-06-30 07:30 | 46 | 43 |  |  | 43281.3125 | 60 | 59
2018-06-30 08:00 | 40 | 38 |  |  | 43281.3333 | 55 | 55
2018-06-30 08:30 | 39 | 37 |  |  | 43281.3542 | 55 | 55
2018-06-30 09:00 | 41 | 39 |  |  | 43281.375 | 56 | 56
2018-06-30 09:30 | 41 | 39 |  |  | 43281.3958 | 59 | 59
2018-06-30 10:00 | 41 | 40 |  |  | 43281.4167 | 57 | 57
2018-06-30 10:30 | 45 | 43 |  |  | 43281.4375 | 60 | 60
2018-06-30 11:00 | 46 | 44 |  |  | 43281.4583 | 60 | 59
2018-06-30 11:30 | 46 | 44 |  |  | 43281.4792 | 58 | 58
2018-06-30 12:00 | 46 | 44 |  |  | 43281.5 | 58 | 57
2018-06-30 12:30 | 43 | 41 |  |  | 43281.5208 | 57 | 57
2018-06-30 13:00 | 44 | 42 |  |  | 43281.5417 | 59 | 59
2018-06-30 13:30 | 45 | 42 |  |  | 43281.5625 | 60 | 59
2018-06-30 14:00 | 48 | 46 |  |  | 43281.5833 | 61 | 61
2018-06-30 14:30 | 49 | 47 |  |  | 43281.6042 | 62 | 61
2018-06-30 15:00 | 52 | 50 |  |  | 43281.625 | 65 | 65
2018-06-30 15:30 | 52 | 50 |  |  | 43281.6458 | 67 | 67
2018-06-30 16:00 | 50 | 48 |  |  | 43281.6667 | 65 | 64
2018-06-30 16:30 | 52 | 49 |  |  | 43281.6875 | 66 | 66
2018-06-30 17:00 | 50 | 48 |  |  | 43281.7083 | 66 | 66
2018-06-30 17:30 | 52 | 50 |  |  | 43281.7292 | 69 | 69
2018-06-30 18:00 | 53 | 52 |  |  | 43281.75 | 71 | 71
2018-06-30 18:30 | 53 | 52 |  |  | 43281.7708 | 69 | 69
2018-06-30 19:00 | 53 | 52 |  |  | 43281.7917 | 69 | 69
2018-06-30 19:30 | 52 | 51 |  |  | 43281.8125 | 68 | 68
2018-06-30 20:00 | 51 | 49 |  |  | 43281.8333 | 66 | 66
2018-06-30 20:30 | 48 | 46 |  |  | 43281.8542 | 63 | 63
2018-06-30 21:00 | 45 | 43 |  |  | 43281.875 | 58 | 58
2018-06-30 21:30 | 44 | 42 |  |  | 43281.8958 | 59 | 59
2018-06-30 22:00 | 45 | 43 |  |  | 43281.9167 | 60 | 60
2018-06-30 22:30 | 44 | 42 |  |  | 43281.9375 | 59 | 59
2018-06-30 23:00 | 45 | 43 |  |  | 43281.9583 | 58 | 57
2018-06-30 23:30 | 43 | 41 |  |  | 43281.9792 | 55 | 54
2018-07-01 | 40 | 38 |  |  | 43282 | 52 | 52
2018-07-01 00:30 | 40 | 37 |  |  | 43282.0208 | 51 | 50
2018-07-01 01:00 | 41 | 38 |  |  | 43282.0417 | 50 | 49
2018-07-01 01:30 | 41 | 37 |  |  | 43282.0625 | 51 | 49
2018-07-01 02:00 | 41 | 37 |  |  | 43282.0833 | 50 | 48
2018-07-01 02:30 | 41 | 36 |  |  | 43282.1042 | 49 | 47
2018-07-01 03:00 | 40 | 35 |  |  | 43282.125 | 48 | 46
2018-07-01 03:30 | 39 | 34 |  |  | 43282.1458 | 47 | 45
2018-07-01 04:00 | 40 | 34 |  |  | 43282.1667 | 48 | 46
2018-07-01 04:30 | 40 | 36 |  |  | 43282.1875 | 49 | 47
2018-07-01 05:00 | 41 | 36 |  |  | 43282.2083 | 49 | 47
2018-07-01 05:30 | 41 | 37 |  |  | 43282.2292 | 51 | 49
2018-07-01 06:00 | 42 | 37 |  |  | 43282.25 | 51 | 49
2018-07-01 06:30 | 42 | 38 |  |  | 43282.2708 | 52 | 50
2018-07-01 07:00 | 41 | 37 |  |  | 43282.2917 | 52 | 50
2018-07-01 07:30 | 43 | 39 |  |  | 43282.3125 | 55 | 54
2018-07-01 08:00 | 39 | 35 |  |  | 43282.3333 | 52 | 51
2018-07-01 08:30 | 39 | 35 |  |  | 43282.3542 | 51 | 51
2018-07-01 09:00 | 40 | 37 |  |  | 43282.375 | 54 | 54
2018-07-01 09:30 | 41 | 39 |  |  | 43282.3958 | 56 | 56
2018-07-01 10:00 | 41 | 38 |  |  | 43282.4167 | 56 | 56
2018-07-01 10:30 | 43 | 41 |  |  | 43282.4375 | 59 | 58
2018-07-01 11:00 | 44 | 42 |  |  | 43282.4583 | 59 | 58
2018-07-01 11:30 | 52 | 50 |  |  | 43282.4792 | 64 | 64
2018-07-01 12:00 | 56 | 54 |  |  | 43282.5 | 69 | 68
2018-07-01 12:30 | 56 | 54 |  |  | 43282.5208 | 71 | 70
2018-07-01 13:00 | 54 | 52 |  |  | 43282.5417 | 67 | 67
2018-07-01 13:30 | 56 | 54 |  |  | 43282.5625 | 70 | 69
2018-07-01 14:00 | 57 | 55 |  |  | 43282.5833 | 71 | 71
2018-07-01 14:30 | 60 | 58 |  |  | 43282.6042 | 73 | 72
2018-07-01 15:00 | 58 | 56 |  |  | 43282.625 | 72 | 71
2018-07-01 15:30 | 57 | 55 |  |  | 43282.6458 | 70 | 70
2018-07-01 16:00 | 56 | 53 |  |  | 43282.6667 | 68 | 67
2018-07-01 16:30 | 50 | 48 |  |  | 43282.6875 | 65 | 64
2018-07-01 17:00 | 53 | 51 |  |  | 43282.7083 | 68 | 68
2018-07-01 17:30 | 53 | 52 |  |  | 43282.7292 | 69 | 69
2018-07-01 18:00 | 55 | 53 |  |  | 43282.75 | 70 | 70
2018-07-01 18:30 | 55 | 53 |  |  | 43282.7708 | 71 | 70
2018-07-01 19:00 | 57 | 55 |  |  | 43282.7917 | 72 | 72
2018-07-01 19:30 | 58 | 56 |  |  | 43282.8125 | 73 | 73
2018-07-01 20:00 | 57 | 56 |  |  | 43282.8333 | 72 | 72
2018-07-01 20:30 | 57 | 56 |  |  | 43282.8542 | 72 | 72
2018-07-01 21:00 | 54 | 53 |  |  | 43282.875 | 68 | 68
2018-07-01 21:30 | 52 | 50 |  |  | 43282.8958 | 65 | 65
2018-07-01 22:00 | 51 | 49 |  |  | 43282.9167 | 66 | 65
2018-07-01 22:30 | 51 | 49 |  |  | 43282.9375 | 65 | 65
2018-07-01 23:00 | 50 | 48 |  |  | 43282.9583 | 63 | 62
2018-07-01 23:30 | 50 | 47 |  |  | 43282.9792 | 61 | 61
2018-07-02 | 51 | 48 |  |  | 43283 | 63 | 62
2018-07-02 00:30 | 49 | 45 |  |  | 43283.0208 | 60 | 58
2018-07-02 01:00 | 46 | 42 |  |  | 43283.0417 | 55 | 54
2018-07-02 01:30 | 45 | 40 |  |  | 43283.0625 | 54 | 53
2018-07-02 02:00 | 45 | 41 |  |  | 43283.0833 | 54 | 52
2018-07-02 02:30 | 45 | 40 |  |  | 43283.1042 | 54 | 53
2018-07-02 03:00 | 44 | 39 |  |  | 43283.125 | 52 | 50
2018-07-02 03:30 | 43 | 38 |  |  | 43283.1458 | 51 | 49
2018-07-02 04:00 | 43 | 38 |  |  | 43283.1667 | 52 | 50
2018-07-02 04:30 | 45 | 39 |  |  | 43283.1875 | 53 | 51
2018-07-02 05:00 | 47 | 43 |  |  | 43283.2083 | 55 | 53
2018-07-02 05:30 | 52 | 48 |  |  | 43283.2292 | 61 | 60
2018-07-02 06:00 | 54 | 51 |  |  | 43283.25 | 64 | 63
2018-07-02 06:30 | 55 | 54 |  |  | 43283.2708 | 70 | 69
2018-07-02 07:00 | 55 | 54 |  |  | 43283.2917 | 73 | 73
2018-07-02 07:30 | 60 | 59 |  |  | 43283.3125 | 81 | 81
2018-07-02 08:00 | 71 | 70 |  |  | 43283.3333 | 104 | 103
2018-07-02 08:30 | 66 | 64 |  |  | 43283.3542 | 103 | 102
2018-07-02 09:00 | 58 | 56 |  |  | 43283.375 | 97 | 96
2018-07-02 09:30 | 55 | 53 |  |  | 43283.3958 | 93 | 92
2018-07-02 10:00 | 55 | 52 |  |  | 43283.4167 | 89 | 88
2018-07-02 10:30 | 53 | 51 |  |  | 43283.4375 | 88 | 87
2018-07-02 11:00 | 51 | 49 |  |  | 43283.4583 | 87 | 86
2018-07-02 11:30 | 57 | 55 |  |  | 43283.4792 | 89 | 89
2018-07-02 12:00 | 56 | 53 |  |  | 43283.5 | 88 | 87
2018-07-02 12:30 | 57 | 54 |  |  | 43283.5208 | 91 | 90
2018-07-02 13:00 | 59 | 56 |  |  | 43283.5417 | 89 | 88
2018-07-02 13:30 | 61 | 59 |  |  | 43283.5625 | 93 | 92
2018-07-02 14:00 | 73 | 71 |  |  | 43283.5833 | 101 | 100
2018-07-02 14:30 | 75 | 73 |  |  | 43283.6042 | 103 | 102
2018-07-02 15:00 | 69 | 67 |  |  | 43283.625 | 98 | 97
2018-07-02 15:30 | 70 | 69 |  |  | 43283.6458 | 98 | 97
2018-07-02 16:00 | 75 | 73 |  |  | 43283.6667 | 104 | 103
2018-07-02 16:30 | 73 | 71 |  |  | 43283.6875 | 104 | 102
2018-07-02 17:00 | 75 | 73 |  |  | 43283.7083 | 106 | 104
2018-07-02 17:30 | 79 | 77 |  |  | 43283.7292 | 109 | 106
2018-07-02 18:00 | 79 | 76 |  |  | 43283.75 | 109 | 106
2018-07-02 18:30 | 78 | 75 |  |  | 43283.7708 | 106 | 102
2018-07-02 19:00 | 80 | 76 |  |  | 43283.7917 | 106 | 103
2018-07-02 19:30 | 79 | 76 |  |  | 43283.8125 | 105 | 101
2018-07-02 20:00 | 78 | 75 |  |  | 43283.8333 | 103 | 100
2018-07-02 20:30 | 77 | 74 |  |  | 43283.8542 | 102 | 99
2018-07-02 21:00 | 76 | 72 |  |  | 43283.875 | 99 | 96
2018-07-02 21:30 | 73 | 69 |  |  | 43283.8958 | 96 | 92
2018-07-02 22:00 | 71 | 67 |  |  | 43283.9167 | 94 | 89
2018-07-02 22:30 | 70 | 65 |  |  | 43283.9375 | 92 | 87
2018-07-02 23:00 | 68 | 64 |  |  | 43283.9583 | 88 | 83
2018-07-02 23:30 | 65 | 63 |  |  | 43283.9792 | 83 | 82
2018-07-03 | 61 | 59 |  |  | 43284 | 78 | 77
2018-07-03 00:30 | 57 | 55 |  |  | 43284.0208 | 72 | 71
2018-07-03 01:00 | 55 | 53 |  |  | 43284.0417 | 69 | 68
2018-07-03 01:30 | 54 | 51 |  |  | 43284.0625 | 67 | 66
2018-07-03 02:00 | 54 | 50 |  |  | 43284.0833 | 65 | 64
2018-07-03 02:30 | 54 | 50 |  |  | 43284.1042 | 65 | 63
2018-07-03 03:00 | 52 | 49 |  |  | 43284.125 | 65 | 63
2018-07-03 03:30 | 52 | 48 |  |  | 43284.1458 | 64 | 63
2018-07-03 04:00 | 51 | 48 |  |  | 43284.1667 | 64 | 62
2018-07-03 04:30 | 52 | 49 |  |  | 43284.1875 | 65 | 63
2018-07-03 05:00 | 55 | 53 |  |  | 43284.2083 | 69 | 68
2018-07-03 05:30 | 58 | 57 |  |  | 43284.2292 | 73 | 73
2018-07-03 06:00 | 63 | 63 |  |  | 43284.25 | 80 | 80
2018-07-03 06:30 | 68 | 68 |  |  | 43284.2708 | 91 | 91
2018-07-03 07:00 | 73 | 73 |  |  | 43284.2917 | 99 | 99
2018-07-03 07:30 | 77 | 75 |  |  | 43284.3125 | 108 | 106
2018-07-03 08:00 | 76 | 74 |  |  | 43284.3333 | 108 | 107
2018-07-03 08:30 | 73 | 72 |  |  | 43284.3542 | 107 | 106
2018-07-03 09:00 | 71 | 70 |  |  | 43284.375 | 104 | 103
2018-07-03 09:30 | 61 | 60 |  |  | 43284.3958 | 96 | 95
2018-07-03 10:00 | 55 | 53 |  |  | 43284.4167 | 90 | 89
2018-07-03 10:30 | 54 | 52 |  |  | 43284.4375 | 87 | 86
2018-07-03 11:00 | 54 | 52 |  |  | 43284.4583 | 87 | 86
2018-07-03 11:30 | 54 | 51 |  |  | 43284.4792 | 86 | 85
2018-07-03 12:00 | 52 | 50 |  |  | 43284.5 | 86 | 85
2018-07-03 12:30 | 54 | 51 |  |  | 43284.5208 | 86 | 85
2018-07-03 13:00 | 55 | 53 |  |  | 43284.5417 | 87 | 86
2018-07-03 13:30 | 59 | 58 |  |  | 43284.5625 | 92 | 91
2018-07-03 14:00 | 72 | 71 |  |  | 43284.5833 | 102 | 101
2018-07-03 14:30 | 74 | 72 |  |  | 43284.6042 | 102 | 101
2018-07-03 15:00 | 73 | 71 |  |  | 43284.625 | 100 | 99
2018-07-03 15:30 | 75 | 73 |  |  | 43284.6458 | 103 | 102
2018-07-03 16:00 | 77 | 75 |  |  | 43284.6667 | 104 | 103
2018-07-03 16:30 | 78 | 76 |  |  | 43284.6875 | 106 | 105
2018-07-03 17:00 | 78 | 77 |  |  | 43284.7083 | 107 | 106
2018-07-03 17:30 | 79 | 78 |  |  | 43284.7292 | 109 | 107
2018-07-03 18:00 | 82 | 80 |  |  | 43284.75 | 110 | 109
2018-07-03 18:30 | 80 | 79 |  |  | 43284.7708 | 108 | 106
2018-07-03 19:00 | 83 | 81 |  |  | 43284.7917 | 109 | 106
2018-07-03 19:30 | 79 | 77 |  |  | 43284.8125 | 107 | 104
2018-07-03 20:00 | 78 | 75 |  |  | 43284.8333 | 105 | 102
2018-07-03 20:30 | 78 | 76 |  |  | 43284.8542 | 105 | 102
2018-07-03 21:00 | 77 | 75 |  |  | 43284.875 | 102 | 99
2018-07-03 21:30 | 74 | 71 |  |  | 43284.8958 | 98 | 94
2018-07-03 22:00 | 72 | 70 |  |  | 43284.9167 | 96 | 93
2018-07-03 22:30 | 71 | 70 |  |  | 43284.9375 | 93 | 92
2018-07-03 23:00 | 70 | 69 |  |  | 43284.9583 | 90 | 89
2018-07-03 23:30 | 66 | 64 |  |  | 43284.9792 | 85 | 84
2018-07-04 | 64 | 61 |  |  | 43285 | 82 | 80
2018-07-04 00:30 | 60 | 57 |  |  | 43285.0208 | 77 | 74
2018-07-04 01:00 | 56 | 52 |  |  | 43285.0417 | 72 | 69
2018-07-04 01:30 | 54 | 49 |  |  | 43285.0625 | 68 | 64
2018-07-04 02:00 | 52 | 47 |  |  | 43285.0833 | 66 | 62
2018-07-04 02:30 | 52 | 47 |  |  | 43285.1042 | 66 | 62
2018-07-04 03:00 | 50 | 44 |  |  | 43285.125 | 63 | 59
2018-07-04 03:30 | 51 | 45 |  |  | 43285.1458 | 63 | 59
2018-07-04 04:00 | 51 | 46 |  |  | 43285.1667 | 63 | 59
2018-07-04 04:30 | 52 | 47 |  |  | 43285.1875 | 64 | 61
2018-07-04 05:00 | 57 | 52 |  |  | 43285.2083 | 69 | 66
2018-07-04 05:30 | 59 | 56 |  |  | 43285.2292 | 74 | 72
2018-07-04 06:00 | 64 | 61 |  |  | 43285.25 | 80 | 79
2018-07-04 06:30 | 69 | 65 |  |  | 43285.2708 | 91 | 88
2018-07-04 07:00 | 70 | 67 |  |  | 43285.2917 | 97 | 95
2018-07-04 07:30 | 75 | 72 |  |  | 43285.3125 | 105 | 103
2018-07-04 08:00 | 74 | 71 |  |  | 43285.3333 | 107 | 105
2018-07-04 08:30 | 74 | 71 |  |  | 43285.3542 | 105 | 104
2018-07-04 09:00 | 71 | 69 |  |  | 43285.375 | 102 | 101
2018-07-04 09:30 | 68 | 66 |  |  | 43285.3958 | 101 | 99
2018-07-04 10:00 | 68 | 66 |  |  | 43285.4167 | 99 | 98
2018-07-04 10:30 | 70 | 67 |  |  | 43285.4375 | 99 | 98
2018-07-04 11:00 | 73 | 70 |  |  | 43285.4583 | 101 | 100
2018-07-04 11:30 | 71 | 69 |  |  | 43285.4792 | 98 | 97
2018-07-04 12:00 | 70 | 68 |  |  | 43285.5 | 97 | 96
2018-07-04 12:30 | 67 | 65 |  |  | 43285.5208 | 95 | 94
2018-07-04 13:00 | 66 | 64 |  |  | 43285.5417 | 93 | 93
2018-07-04 13:30 | 66 | 65 |  |  | 43285.5625 | 94 | 94
2018-07-04 14:00 | 69 | 67 |  |  | 43285.5833 | 96 | 95
2018-07-04 14:30 | 72 | 70 |  |  | 43285.6042 | 99 | 98
2018-07-04 15:00 | 74 | 71 |  |  | 43285.625 | 102 | 100
2018-07-04 15:30 | 76 | 73 |  |  | 43285.6458 | 104 | 102
2018-07-04 16:00 | 77 | 74 |  |  | 43285.6667 | 105 | 103
2018-07-04 16:30 | 78 | 75 |  |  | 43285.6875 | 107 | 105
2018-07-04 17:00 | 78 | 75 |  |  | 43285.7083 | 108 | 106
2018-07-04 17:30 | 78 | 75 |  |  | 43285.7292 | 108 | 106
2018-07-04 18:00 | 78 | 75 |  |  | 43285.75 | 108 | 105
2018-07-04 18:30 | 76 | 73 |  |  | 43285.7708 | 105 | 102
2018-07-04 19:00 | 77 | 74 |  |  | 43285.7917 | 105 | 101
2018-07-04 19:30 | 77 | 74 |  |  | 43285.8125 | 104 | 100
2018-07-04 20:00 | 76 | 73 |  |  | 43285.8333 | 103 | 99
2018-07-04 20:30 | 76 | 73 |  |  | 43285.8542 | 103 | 98
2018-07-04 21:00 | 74 | 70 |  |  | 43285.875 | 99 | 94
2018-07-04 21:30 | 74 | 69 |  |  | 43285.8958 | 97 | 91
2018-07-04 22:00 | 74 | 69 |  |  | 43285.9167 | 98 | 92
2018-07-04 22:30 | 72 | 67 |  |  | 43285.9375 | 93 | 89
2018-07-04 23:00 | 68 | 67 |  |  | 43285.9583 | 86 | 85
2018-07-04 23:30 | 64 | 62 |  |  | 43285.9792 | 82 | 81
2018-07-05 | 58 | 56 |  |  | 43286 | 77 | 76
2018-07-05 00:30 | 55 | 53 |  |  | 43286.0208 | 71 | 70
2018-07-05 01:00 | 52 | 49 |  |  | 43286.0417 | 67 | 66
2018-07-05 01:30 | 50 | 47 |  |  | 43286.0625 | 65 | 63
2018-07-05 02:00 | 50 | 46 |  |  | 43286.0833 | 65 | 63
2018-07-05 02:30 | 50 | 46 |  |  | 43286.1042 | 63 | 62
2018-07-05 03:00 | 50 | 46 |  |  | 43286.125 | 63 | 62
2018-07-05 03:30 | 50 | 46 |  |  | 43286.1458 | 62 | 61
2018-07-05 04:00 | 50 | 46 |  |  | 43286.1667 | 63 | 62
2018-07-05 04:30 | 51 | 48 |  |  | 43286.1875 | 64 | 62
2018-07-05 05:00 | 54 | 51 |  |  | 43286.2083 | 68 | 66
2018-07-05 05:30 | 59 | 57 |  |  | 43286.2292 | 74 | 73
2018-07-05 06:00 | 62 | 61 |  |  | 43286.25 | 80 | 79
2018-07-05 06:30 | 67 | 67 |  |  | 43286.2708 | 89 | 89
2018-07-05 07:00 | 70 | 69 |  |  | 43286.2917 | 96 | 96
2018-07-05 07:30 | 72 | 72 |  |  | 43286.3125 | 104 | 104
2018-07-05 08:00 | 72 | 71 |  |  | 43286.3333 | 105 | 105
2018-07-05 08:30 | 72 | 71 |  |  | 43286.3542 | 106 | 106
2018-07-05 09:00 | 71 | 70 |  |  | 43286.375 | 104 | 104
2018-07-05 09:30 | 71 | 71 |  |  | 43286.3958 | 103 | 103
2018-07-05 10:00 | 76 | 75 |  |  | 43286.4167 | 111 | 111
2018-07-05 10:30 | 76 | 76 |  |  | 43286.4375 | 105 | 105
2018-07-05 11:00 | 75 | 75 |  |  | 43286.4583 | 100 | 100
2018-07-05 11:30 | 78 | 77 |  |  | 43286.4792 | 108 | 108
2018-07-05 12:00 | 79 | 78 |  |  | 43286.5 | 104 | 104
2018-07-05 12:30 | 76 | 75 |  |  | 43286.5208 | 106 | 106
2018-07-05 13:00 | 79 | 78 |  |  | 43286.5417 | 109 | 108
2018-07-05 13:30 | 76 | 75 |  |  | 43286.5625 | 100 | 100
2018-07-05 14:00 | 74 | 73 |  |  | 43286.5833 | 102 | 101
2018-07-05 14:30 | 79 | 77 |  |  | 43286.6042 | 106 | 106
2018-07-05 15:00 | 79 | 78 |  |  | 43286.625 | 106 | 105
2018-07-05 15:30 | 76 | 75 |  |  | 43286.6458 | 104 | 103
2018-07-05 16:00 | 79 | 77 |  |  | 43286.6667 | 106 | 105
2018-07-05 16:30 | 80 | 78 |  |  | 43286.6875 | 109 | 109
2018-07-05 17:00 | 83 | 81 |  |  | 43286.7083 | 112 | 110
2018-07-05 17:30 | 85 | 82 |  |  | 43286.7292 | 112 | 109
2018-07-05 18:00 | 85 | 81 |  |  | 43286.75 | 115 | 110
2018-07-05 18:30 | 85 | 81 |  |  | 43286.7708 | 114 | 108
2018-07-05 19:00 | 86 | 82 |  |  | 43286.7917 | 115 | 109
2018-07-05 19:30 | 84 | 80 |  |  | 43286.8125 | 110 | 107
2018-07-05 20:00 | 84 | 81 |  |  | 43286.8333 | 108 | 105
2018-07-05 20:30 | 84 | 82 |  |  | 43286.8542 | 108 | 105
2018-07-05 21:00 | 81 | 78 |  |  | 43286.875 | 103 | 99
2018-07-05 21:30 | 77 | 74 |  |  | 43286.8958 | 99 | 95
2018-07-05 22:00 | 76 | 72 |  |  | 43286.9167 | 98 | 94
2018-07-05 22:30 | 73 | 69 |  |  | 43286.9375 | 96 | 91
2018-07-05 23:00 | 74 | 69 |  |  | 43286.9583 | 93 | 88
2018-07-05 23:30 | 66 | 65 |  |  | 43286.9792 | 84 | 84
2018-07-06 | 62 | 60 |  |  | 43287 | 79 | 78
2018-07-06 00:30 | 58 | 56 |  |  | 43287.0208 | 74 | 73
2018-07-06 01:00 | 56 | 53 |  |  | 43287.0417 | 70 | 69
2018-07-06 01:30 | 53 | 50 |  |  | 43287.0625 | 67 | 66
2018-07-06 02:00 | 52 | 48 |  |  | 43287.0833 | 65 | 64
2018-07-06 02:30 | 50 | 47 |  |  | 43287.1042 | 65 | 64
2018-07-06 03:00 | 50 | 47 |  |  | 43287.125 | 65 | 63
2018-07-06 03:30 | 50 | 47 |  |  | 43287.1458 | 64 | 62
2018-07-06 04:00 | 50 | 47 |  |  | 43287.1667 | 64 | 62
2018-07-06 04:30 | 51 | 48 |  |  | 43287.1875 | 65 | 64
2018-07-06 05:00 | 54 | 51 |  |  | 43287.2083 | 68 | 67
2018-07-06 05:30 | 56 | 55 |  |  | 43287.2292 | 72 | 71
2018-07-06 06:00 | 61 | 60 |  |  | 43287.25 | 79 | 79
2018-07-06 06:30 | 66 | 65 |  |  | 43287.2708 | 89 | 88
2018-07-06 07:00 | 70 | 68 |  |  | 43287.2917 | 96 | 95
2018-07-06 07:30 | 72 | 70 |  |  | 43287.3125 | 102 | 101
2018-07-06 08:00 | 72 | 70 |  |  | 43287.3333 | 105 | 104
2018-07-06 08:30 | 72 | 71 |  |  | 43287.3542 | 107 | 106
2018-07-06 09:00 | 72 | 70 |  |  | 43287.375 | 106 | 105
2018-07-06 09:30 | 73 | 71 |  |  | 43287.3958 | 105 | 104
2018-07-06 10:00 | 77 | 76 |  |  | 43287.4167 | 108 | 107
2018-07-06 10:30 | 79 | 78 |  |  | 43287.4375 | 107 | 106
2018-07-06 11:00 | 74 | 72 |  |  | 43287.4583 | 102 | 100
2018-07-06 11:30 | 75 | 73 |  |  | 43287.4792 | 104 | 103
2018-07-06 12:00 | 75 | 73 |  |  | 43287.5 | 108 | 107
2018-07-06 12:30 | 77 | 74 |  |  | 43287.5208 | 111 | 109
2018-07-06 13:00 | 73 | 70 |  |  | 43287.5417 | 103 | 102
2018-07-06 13:30 | 71 | 68 |  |  | 43287.5625 | 96 | 94
2018-07-06 14:00 | 76 | 74 |  |  | 43287.5833 | 101 | 100
2018-07-06 14:30 | 76 | 74 |  |  | 43287.6042 | 102 | 101
2018-07-06 15:00 | 76 | 74 |  |  | 43287.625 | 101 | 100
2018-07-06 15:30 | 76 | 74 |  |  | 43287.6458 | 104 | 103
2018-07-06 16:00 | 79 | 77 |  |  | 43287.6667 | 107 | 105
2018-07-06 16:30 | 78 | 76 |  |  | 43287.6875 | 107 | 105
2018-07-06 17:00 | 80 | 78 |  |  | 43287.7083 | 109 | 108
2018-07-06 17:30 | 80 | 78 |  |  | 43287.7292 | 110 | 108
2018-07-06 18:00 | 78 | 76 |  |  | 43287.75 | 107 | 105
2018-07-06 18:30 | 77 | 73 |  |  | 43287.7708 | 104 | 101
2018-07-06 19:00 | 78 | 74 |  |  | 43287.7917 | 105 | 101
2018-07-06 19:30 | 77 | 74 |  |  | 43287.8125 | 102 | 99
2018-07-06 20:00 | 76 | 73 |  |  | 43287.8333 | 101 | 98
2018-07-06 20:30 | 77 | 74 |  |  | 43287.8542 | 102 | 99
2018-07-06 21:00 | 75 | 72 |  |  | 43287.875 | 98 | 95
2018-07-06 21:30 | 71 | 70 |  |  | 43287.8958 | 93 | 92
2018-07-06 22:00 | 69 | 68 |  |  | 43287.9167 | 92 | 91
2018-07-06 22:30 | 69 | 68 |  |  | 43287.9375 | 92 | 91
2018-07-06 23:00 | 69 | 67 |  |  | 43287.9583 | 87 | 86
2018-07-06 23:30 | 66 | 64 |  |  | 43287.9792 | 85 | 84
2018-07-07 | 61 | 58 |  |  | 43288 | 80 | 78
2018-07-07 00:30 | 59 | 55 |  |  | 43288.0208 | 75 | 74
2018-07-07 01:00 | 55 | 52 |  |  | 43288.0417 | 70 | 69
2018-07-07 01:30 | 53 | 49 |  |  | 43288.0625 | 67 | 66
2018-07-07 02:00 | 51 | 47 |  |  | 43288.0833 | 65 | 64
2018-07-07 02:30 | 51 | 47 |  |  | 43288.1042 | 65 | 64
2018-07-07 03:00 | 50 | 46 |  |  | 43288.125 | 64 | 63
2018-07-07 03:30 | 49 | 45 |  |  | 43288.1458 | 63 | 62
2018-07-07 04:00 | 49 | 45 |  |  | 43288.1667 | 62 | 61
2018-07-07 04:30 | 49 | 45 |  |  | 43288.1875 | 62 | 61
2018-07-07 05:00 | 50 | 46 |  |  | 43288.2083 | 63 | 62
2018-07-07 05:30 | 51 | 47 |  |  | 43288.2292 | 65 | 64
2018-07-07 06:00 | 52 | 49 |  |  | 43288.25 | 68 | 67
2018-07-07 06:30 | 56 | 53 |  |  | 43288.2708 | 72 | 72
2018-07-07 07:00 | 57 | 55 |  |  | 43288.2917 | 75 | 75
2018-07-07 07:30 | 58 | 56 |  |  | 43288.3125 | 79 | 78
2018-07-07 08:00 | 59 | 57 |  |  | 43288.3333 | 81 | 81
2018-07-07 08:30 | 62 | 60 |  |  | 43288.3542 | 84 | 84
2018-07-07 09:00 | 63 | 62 |  |  | 43288.375 | 88 | 88
2018-07-07 09:30 | 61 | 60 |  |  | 43288.3958 | 87 | 87
2018-07-07 10:00 | 64 | 63 |  |  | 43288.4167 | 91 | 91
2018-07-07 10:30 | 65 | 64 |  |  | 43288.4375 | 91 | 91
2018-07-07 11:00 | 65 | 64 |  |  | 43288.4583 | 91 | 91
2018-07-07 11:30 | 66 | 64 |  |  | 43288.4792 | 90 | 90
2018-07-07 12:00 | 64 | 63 |  |  | 43288.5 | 84 | 84
2018-07-07 12:30 | 65 | 63 |  |  | 43288.5208 | 82 | 82
2018-07-07 13:00 | 68 | 67 |  |  | 43288.5417 | 90 | 90
2018-07-07 13:30 | 71 | 70 |  |  | 43288.5625 | 94 | 94
2018-07-07 14:00 | 69 | 68 |  |  | 43288.5833 | 92 | 92
2018-07-07 14:30 | 65 | 63 |  |  | 43288.6042 | 87 | 86
2018-07-07 15:00 | 63 | 61 |  |  | 43288.625 | 82 | 81
2018-07-07 15:30 | 66 | 64 |  |  | 43288.6458 | 84 | 83
2018-07-07 16:00 | 65 | 64 |  |  | 43288.6667 | 87 | 86
2018-07-07 16:30 | 65 | 64 |  |  | 43288.6875 | 86 | 86
2018-07-07 17:00 | 66 | 65 |  |  | 43288.7083 | 89 | 89
2018-07-07 17:30 | 66 | 64 |  |  | 43288.7292 | 90 | 90
2018-07-07 18:00 | 66 | 65 |  |  | 43288.75 | 91 | 91
2018-07-07 18:30 | 66 | 65 |  |  | 43288.7708 | 89 | 89
2018-07-07 19:00 | 67 | 66 |  |  | 43288.7917 | 90 | 89
2018-07-07 19:30 | 67 | 65 |  |  | 43288.8125 | 88 | 88
2018-07-07 20:00 | 66 | 65 |  |  | 43288.8333 | 88 | 88
2018-07-07 20:30 | 67 | 65 |  |  | 43288.8542 | 88 | 88
2018-07-07 21:00 | 66 | 64 |  |  | 43288.875 | 86 | 85
2018-07-07 21:30 | 64 | 62 |  |  | 43288.8958 | 83 | 83
2018-07-07 22:00 | 64 | 62 |  |  | 43288.9167 | 86 | 85
2018-07-07 22:30 | 65 | 62 |  |  | 43288.9375 | 85 | 85
2018-07-07 23:00 | 65 | 63 |  |  | 43288.9583 | 84 | 83
2018-07-07 23:30 | 64 | 61 |  |  | 43288.9792 | 82 | 81
2018-07-08 | 60 | 57 |  |  | 43289 | 77 | 76
2018-07-08 00:30 | 57 | 54 |  |  | 43289.0208 | 73 | 72
2018-07-08 01:00 | 55 | 52 |  |  | 43289.0417 | 70 | 69
2018-07-08 01:30 | 54 | 50 |  |  | 43289.0625 | 67 | 66
2018-07-08 02:00 | 52 | 49 |  |  | 43289.0833 | 66 | 65
2018-07-08 02:30 | 51 | 48 |  |  | 43289.1042 | 64 | 63
2018-07-08 03:00 | 51 | 48 |  |  | 43289.125 | 64 | 63
2018-07-08 03:30 | 51 | 48 |  |  | 43289.1458 | 63 | 63
2018-07-08 04:00 | 50 | 47 |  |  | 43289.1667 | 62 | 62
2018-07-08 04:30 | 50 | 47 |  |  | 43289.1875 | 62 | 62
2018-07-08 05:00 | 50 | 47 |  |  | 43289.2083 | 62 | 62
2018-07-08 05:30 | 51 | 48 |  |  | 43289.2292 | 64 | 64
2018-07-08 06:00 | 51 | 48 |  |  | 43289.25 | 66 | 66
2018-07-08 06:30 | 53 | 51 |  |  | 43289.2708 | 69 | 68
2018-07-08 07:00 | 55 | 53 |  |  | 43289.2917 | 73 | 73
2018-07-08 07:30 | 57 | 55 |  |  | 43289.3125 | 77 | 76
2018-07-08 08:00 | 56 | 54 |  |  | 43289.3333 | 77 | 77
2018-07-08 08:30 | 55 | 54 |  |  | 43289.3542 | 77 | 77
2018-07-08 09:00 | 56 | 54 |  |  | 43289.375 | 78 | 78
2018-07-08 09:30 | 56 | 54 |  |  | 43289.3958 | 78 | 78
2018-07-08 10:00 | 55 | 53 |  |  | 43289.4167 | 75 | 75
2018-07-08 10:30 | 52 | 50 |  |  | 43289.4375 | 72 | 72
2018-07-08 11:00 | 49 | 48 |  |  | 43289.4583 | 69 | 68
2018-07-08 11:30 | 46 | 45 |  |  | 43289.4792 | 65 | 65
2018-07-08 12:00 | 45 | 43 |  |  | 43289.5 | 63 | 63
2018-07-08 12:30 | 43 | 41 |  |  | 43289.5208 | 62 | 62
2018-07-08 13:00 | 44 | 42 |  |  | 43289.5417 | 62 | 62
2018-07-08 13:30 | 44 | 43 |  |  | 43289.5625 | 63 | 63
2018-07-08 14:00 | 46 | 45 |  |  | 43289.5833 | 64 | 64
2018-07-08 14:30 | 48 | 46 |  |  | 43289.6042 | 66 | 66
2018-07-08 15:00 | 50 | 49 |  |  | 43289.625 | 69 | 69
2018-07-08 15:30 | 54 | 53 |  |  | 43289.6458 | 75 | 75
2018-07-08 16:00 | 59 | 58 |  |  | 43289.6667 | 80 | 80
2018-07-08 16:30 | 62 | 61 |  |  | 43289.6875 | 85 | 85
2018-07-08 17:00 | 65 | 63 |  |  | 43289.7083 | 89 | 89
2018-07-08 17:30 | 68 | 67 |  |  | 43289.7292 | 94 | 94
2018-07-08 18:00 | 72 | 71 |  |  | 43289.75 | 98 | 98
2018-07-08 18:30 | 74 | 72 |  |  | 43289.7708 | 100 | 100
2018-07-08 19:00 | 75 | 74 |  |  | 43289.7917 | 102 | 102
2018-07-08 19:30 | 73 | 72 |  |  | 43289.8125 | 101 | 101
2018-07-08 20:00 | 74 | 73 |  |  | 43289.8333 | 100 | 100
2018-07-08 20:30 | 75 | 74 |  |  | 43289.8542 | 101 | 101
2018-07-08 21:00 | 72 | 71 |  |  | 43289.875 | 97 | 97
2018-07-08 21:30 | 70 | 69 |  |  | 43289.8958 | 95 | 95
2018-07-08 22:00 | 70 | 69 |  |  | 43289.9167 | 95 | 94
2018-07-08 22:30 | 70 | 68 |  |  | 43289.9375 | 93 | 93
2018-07-08 23:00 | 70 | 68 |  |  | 43289.9583 | 90 | 90
2018-07-08 23:30 | 68 | 66 |  |  | 43289.9792 | 88 | 87
2018-07-09 | 65 | 63 |  |  | 43290 | 83 | 83
2018-07-09 00:30 | 61 | 58 |  |  | 43290.0208 | 77 | 77
2018-07-09 01:00 | 57 | 55 |  |  | 43290.0417 | 73 | 73
2018-07-09 01:30 | 55 | 52 |  |  | 43290.0625 | 70 | 70
2018-07-09 02:00 | 53 | 50 |  |  | 43290.0833 | 69 | 68
2018-07-09 02:30 | 52 | 49 |  |  | 43290.1042 | 67 | 67
2018-07-09 03:00 | 52 | 49 |  |  | 43290.125 | 67 | 66
2018-07-09 03:30 | 52 | 49 |  |  | 43290.1458 | 67 | 66
2018-07-09 04:00 | 52 | 49 |  |  | 43290.1667 | 67 | 67
2018-07-09 04:30 | 53 | 51 |  |  | 43290.1875 | 68 | 68
2018-07-09 05:00 | 58 | 56 |  |  | 43290.2083 | 72 | 72
2018-07-09 05:30 | 62 | 61 |  |  | 43290.2292 | 78 | 78
2018-07-09 06:00 | 68 | 68 |  |  | 43290.25 | 87 | 87
2018-07-09 06:30 | 75 | 74 |  |  | 43290.2708 | 96 | 96
2018-07-09 07:00 | 78 | 77 |  |  | 43290.2917 | 105 | 105
2018-07-09 07:30 | 84 | 83 |  |  | 43290.3125 | 117 | 116
2018-07-09 08:00 | 84 | 82 |  |  | 43290.3333 | 118 | 117
2018-07-09 08:30 | 81 | 80 |  |  | 43290.3542 | 116 | 115
2018-07-09 09:00 | 77 | 75 |  |  | 43290.375 | 111 | 110
2018-07-09 09:30 | 73 | 71 |  |  | 43290.3958 | 106 | 104
2018-07-09 10:00 | 71 | 68 |  |  | 43290.4167 | 102 | 100
2018-07-09 10:30 | 68 | 65 |  |  | 43290.4375 | 97 | 95
2018-07-09 11:00 | 67 | 64 |  |  | 43290.4583 | 95 | 93
2018-07-09 11:30 | 65 | 63 |  |  | 43290.4792 | 93 | 92
2018-07-09 12:00 | 64 | 61 |  |  | 43290.5 | 91 | 90
2018-07-09 12:30 | 63 | 61 |  |  | 43290.5208 | 91 | 90
2018-07-09 13:00 | 64 | 61 |  |  | 43290.5417 | 91 | 90
2018-07-09 13:30 | 65 | 63 |  |  | 43290.5625 | 92 | 91
2018-07-09 14:00 | 66 | 64 |  |  | 43290.5833 | 94 | 93
2018-07-09 14:30 | 71 | 69 |  |  | 43290.6042 | 98 | 97
2018-07-09 15:00 | 72 | 69 |  |  | 43290.625 | 100 | 98
2018-07-09 15:30 | 75 | 72 |  |  | 43290.6458 | 103 | 100
2018-07-09 16:00 | 74 | 71 |  |  | 43290.6667 | 103 | 100
2018-07-09 16:30 | 74 | 71 |  |  | 43290.6875 | 103 | 101
2018-07-09 17:00 | 77 | 74 |  |  | 43290.7083 | 107 | 103
2018-07-09 17:30 | 81 | 78 |  |  | 43290.7292 | 112 | 108
2018-07-09 18:00 | 83 | 81 |  |  | 43290.75 | 114 | 110
2018-07-09 18:30 | 84 | 81 |  |  | 43290.7708 | 114 | 110
2018-07-09 19:00 | 85 | 82 |  |  | 43290.7917 | 115 | 111
2018-07-09 19:30 | 87 | 84 |  |  | 43290.8125 | 115 | 111
2018-07-09 20:00 | 89 | 86 |  |  | 43290.8333 | 117 | 113
2018-07-09 20:30 | 84 | 81 |  |  | 43290.8542 | 113 | 108
2018-07-09 21:00 | 80 | 77 |  |  | 43290.875 | 107 | 102
2018-07-09 21:30 | 77 | 74 |  |  | 43290.8958 | 103 | 98
2018-07-09 22:00 | 76 | 73 |  |  | 43290.9167 | 101 | 96
2018-07-09 22:30 | 76 | 73 |  |  | 43290.9375 | 98 | 95
2018-07-09 23:00 | 74 | 70 |  |  | 43290.9583 | 94 | 90
2018-07-09 23:30 | 66 | 63 |  |  | 43290.9792 | 86 | 85
2018-07-10 | 62 | 60 |  |  | 43291 | 81 | 80
2018-07-10 00:30 | 59 | 56 |  |  | 43291.0208 | 75 | 74
2018-07-10 01:00 | 58 | 55 |  |  | 43291.0417 | 71 | 70
2018-07-10 01:30 | 54 | 51 |  |  | 43291.0625 | 68 | 66
2018-07-10 02:00 | 53 | 49 |  |  | 43291.0833 | 67 | 65
2018-07-10 02:30 | 52 | 49 |  |  | 43291.1042 | 66 | 65
2018-07-10 03:00 | 52 | 49 |  |  | 43291.125 | 64 | 63
2018-07-10 03:30 | 51 | 48 |  |  | 43291.1458 | 64 | 63
2018-07-10 04:00 | 52 | 49 |  |  | 43291.1667 | 65 | 64
2018-07-10 04:30 | 53 | 50 |  |  | 43291.1875 | 66 | 65
2018-07-10 05:00 | 57 | 55 |  |  | 43291.2083 | 71 | 70
2018-07-10 05:30 | 63 | 61 |  |  | 43291.2292 | 78 | 77
2018-07-10 06:00 | 68 | 67 |  |  | 43291.25 | 85 | 85
2018-07-10 06:30 | 74 | 74 |  |  | 43291.2708 | 97 | 97
2018-07-10 07:00 | 78 | 77 |  |  | 43291.2917 | 107 | 106
2018-07-10 07:30 | 86 | 82 |  |  | 43291.3125 | 121 | 117
2018-07-10 08:00 | 90 | 83 |  |  | 43291.3333 | 130 | 122
2018-07-10 08:30 | 88 | 83 |  |  | 43291.3542 | 129 | 122
2018-07-10 09:00 | 88 | 82 |  |  | 43291.375 | 128 | 121
2018-07-10 09:30 | 83 | 76 |  |  | 43291.3958 | 122 | 113
2018-07-10 10:00 | 78 | 71 |  |  | 43291.4167 | 113 | 104
2018-07-10 10:30 | 70 | 67 |  |  | 43291.4375 | 101 | 98
2018-07-10 11:00 | 65 | 62 |  |  | 43291.4583 | 95 | 94
2018-07-10 11:30 | 63 | 62 |  |  | 43291.4792 | 91 | 90
2018-07-10 12:00 | 63 | 62 |  |  | 43291.5 | 90 | 90
2018-07-10 12:30 | 65 | 65 |  |  | 43291.5208 | 93 | 93
2018-07-10 13:00 | 66 | 65 |  |  | 43291.5417 | 94 | 94
2018-07-10 13:30 | 68 | 68 |  |  | 43291.5625 | 96 | 96
2018-07-10 14:00 | 69 | 68 |  |  | 43291.5833 | 97 | 97
2018-07-10 14:30 | 73 | 73 |  |  | 43291.6042 | 101 | 101
2018-07-10 15:00 | 74 | 73 |  |  | 43291.625 | 102 | 102
2018-07-10 15:30 | 73 | 72 |  |  | 43291.6458 | 99 | 98
2018-07-10 16:00 | 75 | 75 |  |  | 43291.6667 | 100 | 100
2018-07-10 16:30 | 78 | 76 |  |  | 43291.6875 | 105 | 103
2018-07-10 17:00 | 81 | 78 |  |  | 43291.7083 | 111 | 107
2018-07-10 17:30 | 84 | 81 |  |  | 43291.7292 | 116 | 110
2018-07-10 18:00 | 87 | 84 |  |  | 43291.75 | 119 | 113
2018-07-10 18:30 | 86 | 83 |  |  | 43291.7708 | 118 | 111
2018-07-10 19:00 | 88 | 84 |  |  | 43291.7917 | 120 | 113
2018-07-10 19:30 | 87 | 84 |  |  | 43291.8125 | 117 | 111
2018-07-10 20:00 | 86 | 83 |  |  | 43291.8333 | 115 | 110
2018-07-10 20:30 | 86 | 83 |  |  | 43291.8542 | 116 | 111
2018-07-10 21:00 | 83 | 79 |  |  | 43291.875 | 112 | 106
2018-07-10 21:30 | 80 | 75 |  |  | 43291.8958 | 107 | 100
2018-07-10 22:00 | 78 | 73 |  |  | 43291.9167 | 105 | 97
2018-07-10 22:30 | 73 | 69 |  |  | 43291.9375 | 98 | 92
2018-07-10 23:00 | 71 | 67 |  |  | 43291.9583 | 94 | 88
2018-07-10 23:30 | 67 | 63 |  |  | 43291.9792 | 87 | 85
2018-07-11 | 61 | 58 |  |  | 43292 | 80 | 79
2018-07-11 00:30 | 58 | 56 |  |  | 43292.0208 | 76 | 75
2018-07-11 01:00 | 55 | 53 |  |  | 43292.0417 | 71 | 71
2018-07-11 01:30 | 53 | 50 |  |  | 43292.0625 | 67 | 67
2018-07-11 02:00 | 52 | 50 |  |  | 43292.0833 | 66 | 66
2018-07-11 02:30 | 50 | 48 |  |  | 43292.1042 | 64 | 64
2018-07-11 03:00 | 50 | 48 |  |  | 43292.125 | 64 | 64
2018-07-11 03:30 | 50 | 47 |  |  | 43292.1458 | 64 | 64
2018-07-11 04:00 | 51 | 48 |  |  | 43292.1667 | 64 | 64
2018-07-11 04:30 | 52 | 49 |  |  | 43292.1875 | 65 | 65
2018-07-11 05:00 | 57 | 55 |  |  | 43292.2083 | 70 | 70
2018-07-11 05:30 | 62 | 61 |  |  | 43292.2292 | 77 | 77
2018-07-11 06:00 | 67 | 66 |  |  | 43292.25 | 84 | 84
2018-07-11 06:30 | 72 | 71 |  |  | 43292.2708 | 96 | 96
2018-07-11 07:00 | 77 | 76 |  |  | 43292.2917 | 106 | 106
2018-07-11 07:30 | 83 | 82 |  |  | 43292.3125 | 117 | 117
2018-07-11 08:00 | 82 | 82 |  |  | 43292.3333 | 119 | 119
2018-07-11 08:30 | 80 | 80 |  |  | 43292.3542 | 120 | 120
2018-07-11 09:00 | 78 | 77 |  |  | 43292.375 | 116 | 115
2018-07-11 09:30 | 75 | 74 |  |  | 43292.3958 | 112 | 111
2018-07-11 10:00 | 70 | 68 |  |  | 43292.4167 | 105 | 105
2018-07-11 10:30 | 67 | 64 |  |  | 43292.4375 | 99 | 98
2018-07-11 11:00 | 67 | 65 |  |  | 43292.4583 | 99 | 98
2018-07-11 11:30 | 69 | 67 |  |  | 43292.4792 | 99 | 98
2018-07-11 12:00 | 68 | 67 |  |  | 43292.5 | 101 | 101
2018-07-11 12:30 | 71 | 70 |  |  | 43292.5208 | 105 | 105
2018-07-11 13:00 | 76 | 75 |  |  | 43292.5417 | 109 | 109
2018-07-11 13:30 | 80 | 79 |  |  | 43292.5625 | 113 | 113
2018-07-11 14:00 | 81 | 81 |  |  | 43292.5833 | 113 | 113
2018-07-11 14:30 | 81 | 80 |  |  | 43292.6042 | 112 | 112
2018-07-11 15:00 | 80 | 80 |  |  | 43292.625 | 112 | 112
2018-07-11 15:30 | 80 | 80 |  |  | 43292.6458 | 112 | 112
2018-07-11 16:00 | 82 | 80 |  |  | 43292.6667 | 114 | 113
2018-07-11 16:30 | 82 | 79 |  |  | 43292.6875 | 115 | 113
2018-07-11 17:00 | 86 | 84 |  |  | 43292.7083 | 119 | 116
2018-07-11 17:30 | 90 | 84 |  |  | 43292.7292 | 124 | 117
2018-07-11 18:00 | 88 | 83 |  |  | 43292.75 | 124 | 117
2018-07-11 18:30 | 88 | 82 |  |  | 43292.7708 | 122 | 115
2018-07-11 19:00 | 91 | 87 |  |  | 43292.7917 | 123 | 118
2018-07-11 19:30 | 90 | 86 |  |  | 43292.8125 | 120 | 116
2018-07-11 20:00 | 89 | 85 |  |  | 43292.8333 | 119 | 115
2018-07-11 20:30 | 87 | 84 |  |  | 43292.8542 | 115 | 113
2018-07-11 21:00 | 82 | 80 |  |  | 43292.875 | 108 | 107
2018-07-11 21:30 | 77 | 76 |  |  | 43292.8958 | 102 | 102
2018-07-11 22:00 | 76 | 75 |  |  | 43292.9167 | 102 | 102
2018-07-11 22:30 | 72 | 72 |  |  | 43292.9375 | 99 | 98
2018-07-11 23:00 | 72 | 71 |  |  | 43292.9583 | 94 | 94
2018-07-11 23:30 | 66 | 65 |  |  | 43292.9792 | 89 | 88
2018-07-12 | 59 | 57 |  |  | 43293 | 81 | 81
2018-07-12 00:30 | 57 | 54 |  |  | 43293.0208 | 76 | 75
2018-07-12 01:00 | 56 | 54 |  |  | 43293.0417 | 73 | 72
2018-07-12 01:30 | 53 | 50 |  |  | 43293.0625 | 70 | 69
2018-07-12 02:00 | 53 | 50 |  |  | 43293.0833 | 69 | 67
2018-07-12 02:30 | 53 | 50 |  |  | 43293.1042 | 68 | 67
2018-07-12 03:00 | 51 | 48 |  |  | 43293.125 | 67 | 65
2018-07-12 03:30 | 51 | 47 |  |  | 43293.1458 | 67 | 65
2018-07-12 04:00 | 52 | 48 |  |  | 43293.1667 | 67 | 65
2018-07-12 04:30 | 53 | 50 |  |  | 43293.1875 | 69 | 67
2018-07-12 05:00 | 57 | 54 |  |  | 43293.2083 | 72 | 71
2018-07-12 05:30 | 61 | 59 |  |  | 43293.2292 | 78 | 77
2018-07-12 06:00 | 66 | 64 |  |  | 43293.25 | 86 | 85
2018-07-12 06:30 | 70 | 69 |  |  | 43293.2708 | 95 | 94
2018-07-12 07:00 | 72 | 71 |  |  | 43293.2917 | 102 | 102
2018-07-12 07:30 | 79 | 78 |  |  | 43293.3125 | 114 | 113
2018-07-12 08:00 | 82 | 78 |  |  | 43293.3333 | 120 | 117
2018-07-12 08:30 | 79 | 75 |  |  | 43293.3542 | 120 | 117
2018-07-12 09:00 | 76 | 74 |  |  | 43293.375 | 117 | 115
2018-07-12 09:30 | 75 | 72 |  |  | 43293.3958 | 113 | 110
2018-07-12 10:00 | 70 | 67 |  |  | 43293.4167 | 105 | 102
2018-07-12 10:30 | 65 | 62 |  |  | 43293.4375 | 99 | 95
2018-07-12 11:00 | 64 | 61 |  |  | 43293.4583 | 97 | 93
2018-07-12 11:30 | 63 | 59 |  |  | 43293.4792 | 96 | 92
2018-07-12 12:00 | 62 | 59 |  |  | 43293.5 | 97 | 93
2018-07-12 12:30 | 63 | 60 |  |  | 43293.5208 | 98 | 95
2018-07-12 13:00 | 64 | 61 |  |  | 43293.5417 | 98 | 96
2018-07-12 13:30 | 69 | 66 |  |  | 43293.5625 | 102 | 101
2018-07-12 14:00 | 72 | 69 |  |  | 43293.5833 | 103 | 101
2018-07-12 14:30 | 73 | 70 |  |  | 43293.6042 | 104 | 102
2018-07-12 15:00 | 72 | 70 |  |  | 43293.625 | 103 | 101
2018-07-12 15:30 | 73 | 71 |  |  | 43293.6458 | 105 | 103
2018-07-12 16:00 | 74 | 71 |  |  | 43293.6667 | 104 | 102
2018-07-12 16:30 | 74 | 71 |  |  | 43293.6875 | 106 | 103
2018-07-12 17:00 | 76 | 74 |  |  | 43293.7083 | 109 | 107
2018-07-12 17:30 | 79 | 77 |  |  | 43293.7292 | 112 | 110
2018-07-12 18:00 | 79 | 77 |  |  | 43293.75 | 112 | 110
2018-07-12 18:30 | 79 | 76 |  |  | 43293.7708 | 111 | 108
2018-07-12 19:00 | 82 | 79 |  |  | 43293.7917 | 114 | 111
2018-07-12 19:30 | 81 | 78 |  |  | 43293.8125 | 113 | 109
2018-07-12 20:00 | 79 | 76 |  |  | 43293.8333 | 110 | 107
2018-07-12 20:30 | 80 | 77 |  |  | 43293.8542 | 111 | 108
2018-07-12 21:00 | 76 | 73 |  |  | 43293.875 | 106 | 103
2018-07-12 21:30 | 73 | 70 |  |  | 43293.8958 | 102 | 98
2018-07-12 22:00 | 72 | 69 |  |  | 43293.9167 | 101 | 97
2018-07-12 22:30 | 70 | 66 |  |  | 43293.9375 | 96 | 92
2018-07-12 23:00 | 65 | 61 |  |  | 43293.9583 | 90 | 86
2018-07-12 23:30 | 60 | 58 |  |  | 43293.9792 | 82 | 81
2018-07-13 | 55 | 53 |  |  | 43294 | 76 | 76
2018-07-13 00:30 | 53 | 52 |  |  | 43294.0208 | 73 | 73
2018-07-13 01:00 | 52 | 51 |  |  | 43294.0417 | 71 | 71
2018-07-13 01:30 | 53 | 51 |  |  | 43294.0625 | 69 | 69
2018-07-13 02:00 | 53 | 51 |  |  | 43294.0833 | 68 | 68
2018-07-13 02:30 | 52 | 50 |  |  | 43294.1042 | 67 | 67
2018-07-13 03:00 | 50 | 47 |  |  | 43294.125 | 66 | 65
2018-07-13 03:30 | 50 | 48 |  |  | 43294.1458 | 66 | 65
2018-07-13 04:00 | 51 | 49 |  |  | 43294.1667 | 67 | 66
2018-07-13 04:30 | 52 | 51 |  |  | 43294.1875 | 70 | 69
2018-07-13 05:00 | 56 | 55 |  |  | 43294.2083 | 73 | 73
2018-07-13 05:30 | 62 | 61 |  |  | 43294.2292 | 81 | 81
2018-07-13 06:00 | 67 | 67 |  |  | 43294.25 | 89 | 89
2018-07-13 06:30 | 71 | 71 |  |  | 43294.2708 | 99 | 99
2018-07-13 07:00 | 75 | 74 |  |  | 43294.2917 | 107 | 106
2018-07-13 07:30 | 80 | 79 |  |  | 43294.3125 | 116 | 115
2018-07-13 08:00 | 77 | 75 |  |  | 43294.3333 | 116 | 114
2018-07-13 08:30 | 74 | 72 |  |  | 43294.3542 | 114 | 113
2018-07-13 09:00 | 71 | 69 |  |  | 43294.375 | 110 | 108
2018-07-13 09:30 | 67 | 66 |  |  | 43294.3958 | 104 | 102
2018-07-13 10:00 | 64 | 62 |  |  | 43294.4167 | 98 | 97
2018-07-13 10:30 | 63 | 61 |  |  | 43294.4375 | 95 | 94
2018-07-13 11:00 | 62 | 61 |  |  | 43294.4583 | 92 | 91
2018-07-13 11:30 | 63 | 62 |  |  | 43294.4792 | 92 | 92
2018-07-13 12:00 | 63 | 62 |  |  | 43294.5 | 93 | 93
2018-07-13 12:30 | 62 | 61 |  |  | 43294.5208 | 91 | 91
2018-07-13 13:00 | 64 | 62 |  |  | 43294.5417 | 93 | 92
2018-07-13 13:30 | 64 | 63 |  |  | 43294.5625 | 94 | 94
2018-07-13 14:00 | 65 | 64 |  |  | 43294.5833 | 94 | 93
2018-07-13 14:30 | 67 | 65 |  |  | 43294.6042 | 95 | 94
2018-07-13 15:00 | 69 | 67 |  |  | 43294.625 | 97 | 96
2018-07-13 15:30 | 73 | 71 |  |  | 43294.6458 | 100 | 99
2018-07-13 16:00 | 76 | 73 |  |  | 43294.6667 | 104 | 103
2018-07-13 16:30 | 77 | 75 |  |  | 43294.6875 | 108 | 106
2018-07-13 17:00 | 81 | 78 |  |  | 43294.7083 | 113 | 111
2018-07-13 17:30 | 85 | 81 |  |  | 43294.7292 | 117 | 114
2018-07-13 18:00 | 85 | 82 |  |  | 43294.75 | 119 | 116
2018-07-13 18:30 | 84 | 81 |  |  | 43294.7708 | 116 | 114
2018-07-13 19:00 | 82 | 79 |  |  | 43294.7917 | 115 | 112
2018-07-13 19:30 | 83 | 80 |  |  | 43294.8125 | 114 | 111
2018-07-13 20:00 | 84 | 81 |  |  | 43294.8333 | 114 | 112
2018-07-13 20:30 | 84 | 81 |  |  | 43294.8542 | 114 | 112
2018-07-13 21:00 | 78 | 75 |  |  | 43294.875 | 108 | 105
2018-07-13 21:30 | 74 | 71 |  |  | 43294.8958 | 103 | 100
2018-07-13 22:00 | 74 | 71 |  |  | 43294.9167 | 103 | 100
2018-07-13 22:30 | 72 | 68 |  |  | 43294.9375 | 100 | 97
2018-07-13 23:00 | 70 | 66 |  |  | 43294.9583 | 96 | 92
2018-07-13 23:30 | 66 | 63 |  |  | 43294.9792 | 90 | 88
2018-07-14 | 61 | 60 |  |  | 43295 | 83 | 83
2018-07-14 00:30 | 56 | 56 |  |  | 43295.0208 | 77 | 77
2018-07-14 01:00 | 53 | 52 |  |  | 43295.0417 | 72 | 72
2018-07-14 01:30 | 52 | 51 |  |  | 43295.0625 | 70 | 70
2018-07-14 02:00 | 52 | 50 |  |  | 43295.0833 | 68 | 68
2018-07-14 02:30 | 52 | 51 |  |  | 43295.1042 | 68 | 67
2018-07-14 03:00 | 50 | 48 |  |  | 43295.125 | 67 | 67
2018-07-14 03:30 | 50 | 47 |  |  | 43295.1458 | 67 | 66
2018-07-14 04:00 | 50 | 47 |  |  | 43295.1667 | 67 | 66
2018-07-14 04:30 | 51 | 48 |  |  | 43295.1875 | 67 | 66
2018-07-14 05:00 | 53 | 51 |  |  | 43295.2083 | 69 | 69
2018-07-14 05:30 | 57 | 55 |  |  | 43295.2292 | 74 | 73
2018-07-14 06:00 | 59 | 57 |  |  | 43295.25 | 78 | 77
2018-07-14 06:30 | 60 | 59 |  |  | 43295.2708 | 82 | 82
2018-07-14 07:00 | 62 | 60 |  |  | 43295.2917 | 85 | 85
2018-07-14 07:30 | 64 | 62 |  |  | 43295.3125 | 89 | 88
2018-07-14 08:00 | 63 | 61 |  |  | 43295.3333 | 89 | 89
2018-07-14 08:30 | 61 | 60 |  |  | 43295.3542 | 90 | 90
2018-07-14 09:00 | 59 | 58 |  |  | 43295.375 | 87 | 87
2018-07-14 09:30 | 57 | 56 |  |  | 43295.3958 | 84 | 84
2018-07-14 10:00 | 53 | 51 |  |  | 43295.4167 | 79 | 79
2018-07-14 10:30 | 52 | 50 |  |  | 43295.4375 | 77 | 76
2018-07-14 11:00 | 52 | 50 |  |  | 43295.4583 | 74 | 74
2018-07-14 11:30 | 50 | 48 |  |  | 43295.4792 | 71 | 71
2018-07-14 12:00 | 49 | 47 |  |  | 43295.5 | 69 | 69
2018-07-14 12:30 | 48 | 45 |  |  | 43295.5208 | 67 | 66
2018-07-14 13:00 | 47 | 44 |  |  | 43295.5417 | 66 | 65
2018-07-14 13:30 | 46 | 43 |  |  | 43295.5625 | 66 | 66
2018-07-14 14:00 | 47 | 44 |  |  | 43295.5833 | 66 | 66
2018-07-14 14:30 | 48 | 45 |  |  | 43295.6042 | 68 | 67
2018-07-14 15:00 | 50 | 47 |  |  | 43295.625 | 71 | 70
2018-07-14 15:30 | 54 | 51 |  |  | 43295.6458 | 75 | 75
2018-07-14 16:00 | 58 | 55 |  |  | 43295.6667 | 80 | 79
2018-07-14 16:30 | 61 | 59 |  |  | 43295.6875 | 84 | 84
2018-07-14 17:00 | 62 | 60 |  |  | 43295.7083 | 88 | 88
2018-07-14 17:30 | 64 | 63 |  |  | 43295.7292 | 92 | 92
2018-07-14 18:00 | 68 | 67 |  |  | 43295.75 | 97 | 97
2018-07-14 18:30 | 68 | 68 |  |  | 43295.7708 | 98 | 98
2018-07-14 19:00 | 71 | 71 |  |  | 43295.7917 | 101 | 101
2018-07-14 19:30 | 72 | 71 |  |  | 43295.8125 | 101 | 101
2018-07-14 20:00 | 72 | 71 |  |  | 43295.8333 | 101 | 101
2018-07-14 20:30 | 72 | 71 |  |  | 43295.8542 | 101 | 100
2018-07-14 21:00 | 71 | 70 |  |  | 43295.875 | 98 | 97
2018-07-14 21:30 | 70 | 69 |  |  | 43295.8958 | 94 | 94
2018-07-14 22:00 | 70 | 69 |  |  | 43295.9167 | 95 | 94
2018-07-14 22:30 | 70 | 69 |  |  | 43295.9375 | 93 | 93
2018-07-14 23:00 | 67 | 67 |  |  | 43295.9583 | 90 | 89
2018-07-14 23:30 | 64 | 63 |  |  | 43295.9792 | 86 | 85
2018-07-15 | 59 | 57 |  |  | 43296 | 80 | 79
2018-07-15 00:30 | 57 | 56 |  |  | 43296.0208 | 76 | 76
2018-07-15 01:00 | 57 | 55 |  |  | 43296.0417 | 74 | 74
2018-07-15 01:30 | 56 | 54 |  |  | 43296.0625 | 72 | 71
2018-07-15 02:00 | 55 | 52 |  |  | 43296.0833 | 70 | 68
2018-07-15 02:30 | 60 | 50 |  |  | 43296.1042 | 69 | 65
2018-07-15 03:00 | 62 | 50 |  |  | 43296.125 | 69 | 65
2018-07-15 03:30 | 61 | 49 |  |  | 43296.1458 | 69 | 64
2018-07-15 04:00 | 61 | 48 |  |  | 43296.1667 | 68 | 63
2018-07-15 04:30 | 60 | 48 |  |  | 43296.1875 | 68 | 63
2018-07-15 05:00 | 60 | 48 |  |  | 43296.2083 | 70 | 66
2018-07-15 05:30 | 61 | 49 |  |  | 43296.2292 | 70 | 66
2018-07-15 06:00 | 62 | 51 |  |  | 43296.25 | 72 | 68
2018-07-15 06:30 | 62 | 52 |  |  | 43296.2708 | 75 | 72
2018-07-15 07:00 | 63 | 54 |  |  | 43296.2917 | 79 | 76
2018-07-15 07:30 | 65 | 57 |  |  | 43296.3125 | 82 | 80
2018-07-15 08:00 | 66 | 58 |  |  | 43296.3333 | 84 | 82
2018-07-15 08:30 | 66 | 58 |  |  | 43296.3542 | 84 | 83
2018-07-15 09:00 | 65 | 57 |  |  | 43296.375 | 83 | 82
2018-07-15 09:30 | 62 | 54 |  |  | 43296.3958 | 81 | 79
2018-07-15 10:00 | 61 | 52 |  |  | 43296.4167 | 78 | 77
2018-07-15 10:30 | 59 | 50 |  |  | 43296.4375 | 75 | 73
2018-07-15 11:00 | 57 | 49 |  |  | 43296.4583 | 72 | 71
2018-07-15 11:30 | 55 | 47 |  |  | 43296.4792 | 69 | 68
2018-07-15 12:00 | 54 | 45 |  |  | 43296.5 | 67 | 66
2018-07-15 12:30 | 53 | 44 |  |  | 43296.5208 | 65 | 64
2018-07-15 13:00 | 53 | 44 |  |  | 43296.5417 | 64 | 63
2018-07-15 13:30 | 54 | 44 |  |  | 43296.5625 | 66 | 65
2018-07-15 14:00 | 55 | 46 |  |  | 43296.5833 | 67 | 66
2018-07-15 14:30 | 57 | 49 |  |  | 43296.6042 | 69 | 68
2018-07-15 15:00 | 58 | 50 |  |  | 43296.625 | 72 | 71
2018-07-15 15:30 | 61 | 54 |  |  | 43296.6458 | 76 | 75
2018-07-15 16:00 | 66 | 58 |  |  | 43296.6667 | 81 | 80
2018-07-15 16:30 | 68 | 61 |  |  | 43296.6875 | 85 | 84
2018-07-15 17:00 | 71 | 66 |  |  | 43296.7083 | 92 | 91
2018-07-15 17:30 | 75 | 71 |  |  | 43296.7292 | 99 | 98
2018-07-15 18:00 | 78 | 74 |  |  | 43296.75 | 104 | 102
2018-07-15 18:30 | 79 | 74 |  |  | 43296.7708 | 105 | 103
2018-07-15 19:00 | 79 | 75 |  |  | 43296.7917 | 105 | 104
2018-07-15 19:30 | 80 | 76 |  |  | 43296.8125 | 106 | 104
2018-07-15 20:00 | 80 | 76 |  |  | 43296.8333 | 105 | 103
2018-07-15 20:30 | 81 | 77 |  |  | 43296.8542 | 107 | 104
2018-07-15 21:00 | 78 | 74 |  |  | 43296.875 | 101 | 100
2018-07-15 21:30 | 74 | 69 |  |  | 43296.8958 | 96 | 94
2018-07-15 22:00 | 73 | 68 |  |  | 43296.9167 | 95 | 93
2018-07-15 22:30 | 71 | 65 |  |  | 43296.9375 | 91 | 89
2018-07-15 23:00 | 70 | 63 |  |  | 43296.9583 | 87 | 85
2018-07-15 23:30 | 67 | 60 |  |  | 43296.9792 | 83 | 81
2018-07-16 | 62 | 55 |  |  | 43297 | 78 | 76
2018-07-16 00:30 | 63 | 54 |  |  | 43297.0208 | 76 | 73
2018-07-16 01:00 | 61 | 51 |  |  | 43297.0417 | 72 | 69
2018-07-16 01:30 | 60 | 50 |  |  | 43297.0625 | 71 | 68
2018-07-16 02:00 | 60 | 49 |  |  | 43297.0833 | 69 | 66
2018-07-16 02:30 | 59 | 48 |  |  | 43297.1042 | 67 | 64
2018-07-16 03:00 | 59 | 48 |  |  | 43297.125 | 67 | 64
2018-07-16 03:30 | 58 | 47 |  |  | 43297.1458 | 66 | 62
2018-07-16 04:00 | 58 | 47 |  |  | 43297.1667 | 67 | 63
2018-07-16 04:30 | 58 | 48 |  |  | 43297.1875 | 67 | 64
2018-07-16 05:00 | 61 | 52 |  |  | 43297.2083 | 71 | 69
2018-07-16 05:30 | 67 | 60 |  |  | 43297.2292 | 79 | 77
2018-07-16 06:00 | 73 | 67 |  |  | 43297.25 | 86 | 85
2018-07-16 06:30 | 83 | 77 |  |  | 43297.2708 | 102 | 102
2018-07-16 07:00 | 87 | 85 |  |  | 43297.2917 | 118 | 118
2018-07-16 07:30 | 91 | 88 |  |  | 43297.3125 | 128 | 128
2018-07-16 08:00 | 82 | 78 |  |  | 43297.3333 | 121 | 120
2018-07-16 08:30 | 75 | 69 |  |  | 43297.3542 | 114 | 113
2018-07-16 09:00 | 68 | 62 |  |  | 43297.375 | 107 | 102
2018-07-16 09:30 | 117 | 113 |  |  | 43297.3958 | 53 | 47
2018-07-16 10:00 | 113 | 109 |  |  | 43297.4167 | 50 | 45
2018-07-16 10:30 | 112 | 109 |  |  | 43297.4375 | 51 | 46
2018-07-16 11:00 | 72 | 71 |  |  | 43297.4583 | 85 | 76
2018-07-16 11:30 | 57 | 56 |  |  | 43297.4792 | 91 | 85
2018-07-16 12:00 | 56 | 54 |  |  | 43297.5 | 88 | 83
2018-07-16 12:30 | 55 | 53 |  |  | 43297.5208 | 88 | 83
2018-07-16 13:00 | 57 | 54 |  |  | 43297.5417 | 89 | 83
2018-07-16 13:30 | 58 | 55 |  |  | 43297.5625 | 90 | 84
2018-07-16 14:00 | 58 | 55 |  |  | 43297.5833 | 90 | 84
2018-07-16 14:30 | 59 | 57 |  |  | 43297.6042 | 90 | 85
2018-07-16 15:00 | 62 | 60 |  |  | 43297.625 | 95 | 88
2018-07-16 15:30 | 64 | 61 |  |  | 43297.6458 | 98 | 90
2018-07-16 16:00 | 67 | 64 |  |  | 43297.6667 | 99 | 92
2018-07-16 16:30 | 71 | 68 |  |  | 43297.6875 | 105 | 96
2018-07-16 17:00 | 74 | 71 |  |  | 43297.7083 | 110 | 100
2018-07-16 17:30 | 79 | 75 |  |  | 43297.7292 | 118 | 106
2018-07-16 18:00 | 82 | 79 |  |  | 43297.75 | 122 | 110
2018-07-16 18:30 | 83 | 79 |  |  | 43297.7708 | 122 | 108
2018-07-16 19:00 | 85 | 81 |  |  | 43297.7917 | 123 | 110
2018-07-16 19:30 | 85 | 81 |  |  | 43297.8125 | 120 | 110
2018-07-16 20:00 | 83 | 80 |  |  | 43297.8333 | 119 | 109
2018-07-16 20:30 | 84 | 81 |  |  | 43297.8542 | 119 | 109
2018-07-16 21:00 | 82 | 79 |  |  | 43297.875 | 115 | 104
2018-07-16 21:30 | 77 | 74 |  |  | 43297.8958 | 110 | 97
2018-07-16 22:00 | 76 | 70 |  |  | 43297.9167 | 108 | 95
2018-07-16 22:30 | 73 | 67 |  |  | 43297.9375 | 103 | 90
2018-07-16 23:00 | 71 | 65 |  |  | 43297.9583 | 98 | 85
2018-07-16 23:30 | 67 | 61 |  |  | 43297.9792 | 93 | 81
2018-07-17 | 61 | 57 |  |  | 43298 | 84 | 77
2018-07-17 00:30 | 58 | 54 |  |  | 43298.0208 | 78 | 72
2018-07-17 01:00 | 55 | 50 |  |  | 43298.0417 | 75 | 68
2018-07-17 01:30 | 54 | 49 |  |  | 43298.0625 | 73 | 65
2018-07-17 02:00 | 55 | 49 |  |  | 43298.0833 | 73 | 64
2018-07-17 02:30 | 54 | 48 |  |  | 43298.1042 | 72 | 63
2018-07-17 03:00 | 54 | 49 |  |  | 43298.125 | 72 | 64
2018-07-17 03:30 | 54 | 49 |  |  | 43298.1458 | 73 | 64
2018-07-17 04:00 | 55 | 49 |  |  | 43298.1667 | 73 | 64
2018-07-17 04:30 | 56 | 51 |  |  | 43298.1875 | 75 | 67
2018-07-17 05:00 | 60 | 56 |  |  | 43298.2083 | 79 | 72
2018-07-17 05:30 | 69 | 64 |  |  | 43298.2292 | 84 | 81
2018-07-17 06:00 | 79 | 72 |  |  | 43298.25 | 95 | 91
2018-07-17 06:30 | 87 | 82 |  |  | 43298.2708 | 110 | 107
2018-07-17 07:00 | 92 | 89 |  |  | 43298.2917 | 124 | 122
2018-07-17 07:30 | 90 | 86 |  |  | 43298.3125 | 128 | 123
2018-07-17 08:00 | 86 | 82 |  |  | 43298.3333 | 124 | 121
2018-07-17 08:30 | 78 | 73 |  |  | 43298.3542 | 118 | 114
2018-07-17 09:00 | 42 | 39 |  |  | 43298.375 | 93 | 92
2018-07-17 09:30 | 44 | 40 |  |  | 43298.3958 | 90 | 88
2018-07-17 10:00 | 43 | 41 |  |  | 43298.4167 | 86 | 85
2018-07-17 10:30 | 41 | 40 |  |  | 43298.4375 | 84 | 84
2018-07-17 11:00 | 41 | 40 |  |  | 43298.4583 | 81 | 81
2018-07-17 11:30 | 40 | 40 |  |  | 43298.4792 | 80 | 80
2018-07-17 12:00 | 41 | 40 |  |  | 43298.5 | 80 | 80
2018-07-17 12:30 | 59 | 57 |  |  | 43298.5208 | 88 | 88
2018-07-17 13:00 | 64 | 59 |  |  | 43298.5417 | 89 | 89
2018-07-17 13:30 | 66 | 61 |  |  | 43298.5625 | 90 | 90
2018-07-17 14:00 | 66 | 61 |  |  | 43298.5833 | 89 | 88
2018-07-17 14:30 | 66 | 62 |  |  | 43298.6042 | 90 | 90
2018-07-17 15:00 | 67 | 63 |  |  | 43298.625 | 90 | 90
2018-07-17 15:30 | 69 | 64 |  |  | 43298.6458 | 92 | 92
2018-07-17 16:00 | 72 | 67 |  |  | 43298.6667 | 95 | 94
2018-07-17 16:30 | 74 | 70 |  |  | 43298.6875 | 98 | 98
2018-07-17 17:00 | 76 | 72 |  |  | 43298.7083 | 101 | 100
2018-07-17 17:30 | 77 | 73 |  |  | 43298.7292 | 104 | 103
2018-07-17 18:00 | 82 | 77 |  |  | 43298.75 | 108 | 106
2018-07-17 18:30 | 82 | 78 |  |  | 43298.7708 | 108 | 106
2018-07-17 19:00 | 85 | 81 |  |  | 43298.7917 | 111 | 109
2018-07-17 19:30 | 85 | 80 |  |  | 43298.8125 | 110 | 108
2018-07-17 20:00 | 85 | 80 |  |  | 43298.8333 | 108 | 107
2018-07-17 20:30 | 85 | 82 |  |  | 43298.8542 | 110 | 110
2018-07-17 21:00 | 87 | 82 |  |  | 43298.875 | 108 | 108
2018-07-17 21:30 | 85 | 78 |  |  | 43298.8958 | 102 | 102
2018-07-17 22:00 | 83 | 75 |  |  | 43298.9167 | 99 | 99
2018-07-17 22:30 | 78 | 69 |  |  | 43298.9375 | 94 | 94
2018-07-17 23:00 | 77 | 66 |  |  | 43298.9583 | 88 | 88
2018-07-17 23:30 | 72 | 61 |  |  | 43298.9792 | 83 | 83
2018-07-18 | 67 | 57 |  |  | 43299 | 77 | 77
2018-07-18 00:30 | 66 | 55 |  |  | 43299.0208 | 74 | 74
2018-07-18 01:00 | 63 | 52 |  |  | 43299.0417 | 70 | 70
2018-07-18 01:30 | 62 | 51 |  |  | 43299.0625 | 67 | 67
2018-07-18 02:00 | 62 | 50 |  |  | 43299.0833 | 65 | 65
2018-07-18 02:30 | 62 | 49 |  |  | 43299.1042 | 65 | 65
2018-07-18 03:00 | 63 | 50 |  |  | 43299.125 | 66 | 66
2018-07-18 03:30 | 64 | 52 |  |  | 43299.1458 | 67 | 67
2018-07-18 04:00 | 65 | 53 |  |  | 43299.1667 | 67 | 67
2018-07-18 04:30 | 67 | 55 |  |  | 43299.1875 | 69 | 69
2018-07-18 05:00 | 68 | 58 |  |  | 43299.2083 | 73 | 73
2018-07-18 05:30 | 72 | 63 |  |  | 43299.2292 | 80 | 80
2018-07-18 06:00 | 80 | 70 |  |  | 43299.25 | 89 | 89
2018-07-18 06:30 | 89 | 78 |  |  | 43299.2708 | 103 | 102
2018-07-18 07:00 | 91 | 82 |  |  | 43299.2917 | 116 | 115
2018-07-18 07:30 | 96 | 87 |  |  | 43299.3125 | 125 | 124
2018-07-18 08:00 | 92 | 84 |  |  | 43299.3333 | 124 | 124
2018-07-18 08:30 | 88 | 78 |  |  | 43299.3542 | 119 | 119
2018-07-18 09:00 | 86 | 75 |  |  | 43299.375 | 117 | 117
2018-07-18 09:30 | 64 | 54 |  |  | 43299.3958 | 104 | 103
2018-07-18 10:00 | 56 | 47 |  |  | 43299.4167 | 96 | 96
2018-07-18 10:30 | 54 | 45 |  |  | 43299.4375 | 92 | 91
2018-07-18 11:00 | 54 | 44 |  |  | 43299.4583 | 89 | 89
2018-07-18 11:30 | 53 | 44 |  |  | 43299.4792 | 86 | 86
2018-07-18 12:00 | 55 | 45 |  |  | 43299.5 | 87 | 87
2018-07-18 12:30 | 72 | 63 |  |  | 43299.5208 | 93 | 93
2018-07-18 13:00 | 68 | 62 |  |  | 43299.5417 | 93 | 93
2018-07-18 13:30 | 70 | 64 |  |  | 43299.5625 | 95 | 94
2018-07-18 14:00 | 72 | 66 |  |  | 43299.5833 | 95 | 94
2018-07-18 14:30 | 73 | 68 |  |  | 43299.6042 | 96 | 95
2018-07-18 15:00 | 74 | 68 |  |  | 43299.625 | 97 | 96
2018-07-18 15:30 | 76 | 71 |  |  | 43299.6458 | 98 | 98
2018-07-18 16:00 | 80 | 70 |  |  | 43299.6667 | 99 | 98
2018-07-18 16:30 | 83 | 72 |  |  | 43299.6875 | 102 | 101
2018-07-18 17:00 | 84 | 74 |  |  | 43299.7083 | 104 | 103
2018-07-18 17:30 | 86 | 74 |  |  | 43299.7292 | 107 | 106
2018-07-18 18:00 | 87 | 76 |  |  | 43299.75 | 109 | 108
2018-07-18 18:30 | 89 | 77 |  |  | 43299.7708 | 108 | 107
2018-07-18 19:00 | 90 | 78 |  |  | 43299.7917 | 109 | 107
2018-07-18 19:30 | 89 | 77 |  |  | 43299.8125 | 108 | 106
2018-07-18 20:00 | 89 | 77 |  |  | 43299.8333 | 108 | 106
2018-07-18 20:30 | 92 | 79 |  |  | 43299.8542 | 108 | 106
2018-07-18 21:00 | 89 | 76 |  |  | 43299.875 | 104 | 102
2018-07-18 21:30 | 86 | 73 |  |  | 43299.8958 | 100 | 98
2018-07-18 22:00 | 83 | 70 |  |  | 43299.9167 | 100 | 98
2018-07-18 22:30 | 80 | 66 |  |  | 43299.9375 | 96 | 95
2018-07-18 23:00 | 79 | 65 |  |  | 43299.9583 | 92 | 90
2018-07-18 23:30 | 73 | 62 |  |  | 43299.9792 | 85 | 84
2018-07-19 | 67 | 56 |  |  | 43300 | 78 | 78
2018-07-19 00:30 | 67 | 55 |  |  | 43300.0208 | 75 | 74
2018-07-19 01:00 | 66 | 53 |  |  | 43300.0417 | 72 | 71
2018-07-19 01:30 | 66 | 52 |  |  | 43300.0625 | 70 | 70
2018-07-19 02:00 | 74 | 51 |  |  | 43300.0833 | 68 | 66
2018-07-19 02:30 | 77 | 50 |  |  | 43300.1042 | 68 | 65
2018-07-19 03:00 | 81 | 50 |  |  | 43300.125 | 67 | 64
2018-07-19 03:30 | 81 | 50 |  |  | 43300.1458 | 67 | 64
2018-07-19 04:00 | 82 | 51 |  |  | 43300.1667 | 68 | 64
2018-07-19 04:30 | 82 | 52 |  |  | 43300.1875 | 70 | 66
2018-07-19 05:00 | 84 | 57 |  |  | 43300.2083 | 74 | 71
2018-07-19 05:30 | 86 | 63 |  |  | 43300.2292 | 81 | 79
2018-07-19 06:00 | 95 | 67 |  |  | 43300.25 | 91 | 87
2018-07-19 06:30 | 93 | 75 |  |  | 43300.2708 | 103 | 101
2018-07-19 07:00 | 93 | 81 |  |  | 43300.2917 | 114 | 113
2018-07-19 07:30 | 109 | 89 |  |  | 43300.3125 | 126 | 126
2018-07-19 08:00 | 109 | 85 |  |  | 43300.3333 | 124 | 124
2018-07-19 08:30 | 115 | 78 |  |  | 43300.3542 | 117 | 117
2018-07-19 09:00 | 143 | 120 |  |  | 43300.375 | 77 | 76
2018-07-19 09:30 | 138 | 126 |  |  | 43300.3958 | 61 | 53
2018-07-19 10:00 | 123 | 115 |  |  | 43300.4167 | 62 | 49
2018-07-19 10:30 | 115 | 111 |  |  | 43300.4375 | 55 | 48
2018-07-19 11:00 | 112 | 108 |  |  | 43300.4583 | 54 | 48
2018-07-19 11:30 | 82 | 73 |  |  | 43300.4792 | 82 | 79
2018-07-19 12:00 | 73 | 61 |  |  | 43300.5 | 94 | 92
2018-07-19 12:30 | 71 | 59 |  |  | 43300.5208 | 91 | 89
2018-07-19 13:00 | 70 | 57 |  |  | 43300.5417 | 86 | 84
2018-07-19 13:30 | 71 | 58 |  |  | 43300.5625 | 87 | 85
2018-07-19 14:00 | 73 | 60 |  |  | 43300.5833 | 89 | 87
2018-07-19 14:30 | 73 | 63 |  |  | 43300.6042 | 89 | 88
2018-07-19 15:00 | 72 | 63 |  |  | 43300.625 | 89 | 88
2018-07-19 15:30 | 72 | 62 |  |  | 43300.6458 | 90 | 89
2018-07-19 16:00 | 73 | 65 |  |  | 43300.6667 | 93 | 92
2018-07-19 16:30 | 70 | 68 |  |  | 43300.6875 | 97 | 97
2018-07-19 17:00 | 72 | 68 |  |  | 43300.7083 | 99 | 99
2018-07-19 17:30 | 79 | 68 |  |  | 43300.7292 | 105 | 100
2018-07-19 18:00 | 82 | 72 |  |  | 43300.75 | 108 | 103
2018-07-19 18:30 | 72 | 72 |  |  | 43300.7708 | 108 | 104
2018-07-19 19:00 | 74 | 74 |  |  | 43300.7917 | 111 | 107
2018-07-19 19:30 | 74 | 74 |  |  | 43300.8125 | 109 | 106
2018-07-19 20:00 | 73 | 73 |  |  | 43300.8333 | 108 | 105
2018-07-19 20:30 | 73 | 73 |  |  | 43300.8542 | 108 | 105
2018-07-19 21:00 | 70 | 70 |  |  | 43300.875 | 104 | 100
2018-07-19 21:30 | 64 | 64 |  |  | 43300.8958 | 98 | 93
2018-07-19 22:00 | 62 | 62 |  |  | 43300.9167 | 95 | 90
2018-07-19 22:30 | 60 | 60 |  |  | 43300.9375 | 90 | 87
2018-07-19 23:00 | 57 | 57 |  |  | 43300.9583 | 86 | 82
2018-07-19 23:30 | 54 | 53 |  |  | 43300.9792 | 79 | 78
2018-07-20 | 49 | 48 |  |  | 43301 | 72 | 72
2018-07-20 00:30 | 48 | 46 |  |  | 43301.0208 | 67 | 67
2018-07-20 01:00 | 46 | 43 |  |  | 43301.0417 | 64 | 64
2018-07-20 01:30 | 45 | 44 |  |  | 43301.0625 | 62 | 61
2018-07-20 02:00 | 47 | 45 |  |  | 43301.0833 | 62 | 62
2018-07-20 02:30 | 46 | 44 |  |  | 43301.1042 | 61 | 61
2018-07-20 03:00 | 45 | 44 |  |  | 43301.125 | 62 | 61
2018-07-20 03:30 | 47 | 45 |  |  | 43301.1458 | 62 | 61
2018-07-20 04:00 | 47 | 45 |  |  | 43301.1667 | 62 | 61
2018-07-20 04:30 | 49 | 48 |  |  | 43301.1875 | 64 | 63
2018-07-20 05:00 | 51 | 50 |  |  | 43301.2083 | 67 | 67
2018-07-20 05:30 | 55 | 54 |  |  | 43301.2292 | 73 | 73
2018-07-20 06:00 | 63 | 62 |  |  | 43301.25 | 83 | 83
2018-07-20 06:30 | 70 | 70 |  |  | 43301.2708 | 94 | 94
2018-07-20 07:00 | 75 | 75 |  |  | 43301.2917 | 105 | 105
2018-07-20 07:30 | 79 | 79 |  |  | 43301.3125 | 115 | 115
2018-07-20 08:00 | 102 | 102 |  |  | 43301.3333 | 95 | 95
2018-07-20 08:30 | 133 | 132 |  |  | 43301.3542 | 55 | 54
2018-07-20 09:00 | 122 | 121 |  |  | 43301.375 | 51 | 50
2018-07-20 09:30 | 105 | 104 |  |  | 43301.3958 | 40 | 39
2018-07-20 10:00 | 84 | 82 |  |  | 43301.4167 | 39 | 38
2018-07-20 10:30 | 47 | 39 |  |  | 43301.4375 | 83 | 82
2018-07-20 11:00 | 46 | 38 |  |  | 43301.4583 | 81 | 80
2018-07-20 11:30 | 48 | 41 |  |  | 43301.4792 | 82 | 82
2018-07-20 12:00 | 44 | 37 |  |  | 43301.5 | 80 | 79
2018-07-20 12:30 | 46 | 39 |  |  | 43301.5208 | 82 | 82
2018-07-20 13:00 | 71 | 64 |  |  | 43301.5417 | 97 | 96
2018-07-20 13:30 | 63 | 55 |  |  | 43301.5625 | 84 | 83
2018-07-20 14:00 | 66 | 63 |  |  | 43301.5833 | 89 | 89
2018-07-20 14:30 | 72 | 71 |  |  | 43301.6042 | 99 | 99
2018-07-20 15:00 | 72 | 72 |  |  | 43301.625 | 103 | 103
2018-07-20 15:30 | 69 | 68 |  |  | 43301.6458 | 101 | 101
2018-07-20 16:00 | 69 | 68 |  |  | 43301.6667 | 100 | 100
2018-07-20 16:30 | 69 | 69 |  |  | 43301.6875 | 100 | 100
2018-07-20 17:00 | 67 | 65 |  |  | 43301.7083 | 99 | 98
2018-07-20 17:30 | 67 | 64 |  |  | 43301.7292 | 99 | 98
2018-07-20 18:00 | 69 | 65 |  |  | 43301.75 | 100 | 98
2018-07-20 18:30 | 69 | 65 |  |  | 43301.7708 | 98 | 96
2018-07-20 19:00 | 70 | 66 |  |  | 43301.7917 | 99 | 96
2018-07-20 19:30 | 67 | 65 |  |  | 43301.8125 | 95 | 94
2018-07-20 20:00 | 66 | 63 |  |  | 43301.8333 | 94 | 92
2018-07-20 20:30 | 65 | 63 |  |  | 43301.8542 | 92 | 90
2018-07-20 21:00 | 62 | 59 |  |  | 43301.875 | 88 | 86
2018-07-20 21:30 | 60 | 57 |  |  | 43301.8958 | 86 | 84
2018-07-20 22:00 | 62 | 58 |  |  | 43301.9167 | 86 | 84
2018-07-20 22:30 | 60 | 56 |  |  | 43301.9375 | 85 | 82
2018-07-20 23:00 | 57 | 52 |  |  | 43301.9583 | 81 | 78
2018-07-20 23:30 | 53 | 51 |  |  | 43301.9792 | 75 | 75
2018-07-21 | 50 | 47 |  |  | 43302 | 70 | 70
2018-07-21 00:30 | 49 | 45 |  |  | 43302.0208 | 65 | 65
2018-07-21 01:00 | 49 | 44 |  |  | 43302.0417 | 63 | 62
2018-07-21 01:30 | 47 | 42 |  |  | 43302.0625 | 61 | 61
2018-07-21 02:00 | 47 | 42 |  |  | 43302.0833 | 60 | 59
2018-07-21 02:30 | 47 | 41 |  |  | 43302.1042 | 60 | 59
2018-07-21 03:00 | 47 | 41 |  |  | 43302.125 | 60 | 59
2018-07-21 03:30 | 47 | 41 |  |  | 43302.1458 | 59 | 58
2018-07-21 04:00 | 47 | 41 |  |  | 43302.1667 | 59 | 58
2018-07-21 04:30 | 47 | 41 |  |  | 43302.1875 | 60 | 59
2018-07-21 05:00 | 48 | 42 |  |  | 43302.2083 | 60 | 59
2018-07-21 05:30 | 49 | 43 |  |  | 43302.2292 | 62 | 62
2018-07-21 06:00 | 50 | 45 |  |  | 43302.25 | 66 | 65
2018-07-21 06:30 | 53 | 48 |  |  | 43302.2708 | 69 | 68
2018-07-21 07:00 | 53 | 48 |  |  | 43302.2917 | 71 | 69
2018-07-21 07:30 | 54 | 49 |  |  | 43302.3125 | 74 | 72
2018-07-21 08:00 | 54 | 48 |  |  | 43302.3333 | 75 | 74
2018-07-21 08:30 | 53 | 48 |  |  | 43302.3542 | 75 | 74
2018-07-21 09:00 | 50 | 46 |  |  | 43302.375 | 74 | 73
2018-07-21 09:30 | 49 | 44 |  |  | 43302.3958 | 71 | 71
2018-07-21 10:00 | 49 | 43 |  |  | 43302.4167 | 69 | 68
2018-07-21 10:30 | 46 | 42 |  |  | 43302.4375 | 66 | 66
2018-07-21 11:00 | 44 | 39 |  |  | 43302.4583 | 64 | 63
2018-07-21 11:30 | 44 | 38 |  |  | 43302.4792 | 62 | 62
2018-07-21 12:00 | 44 | 39 |  |  | 43302.5 | 61 | 60
2018-07-21 12:30 | 42 | 37 |  |  | 43302.5208 | 60 | 59
2018-07-21 13:00 | 42 | 36 |  |  | 43302.5417 | 58 | 58
2018-07-21 13:30 | 42 | 36 |  |  | 43302.5625 | 59 | 58
2018-07-21 14:00 | 43 | 37 |  |  | 43302.5833 | 59 | 59
2018-07-21 14:30 | 43 | 37 |  |  | 43302.6042 | 60 | 60
2018-07-21 15:00 | 45 | 39 |  |  | 43302.625 | 62 | 62
2018-07-21 15:30 | 48 | 42 |  |  | 43302.6458 | 67 | 66
2018-07-21 16:00 | 51 | 46 |  |  | 43302.6667 | 71 | 70
2018-07-21 16:30 | 52 | 47 |  |  | 43302.6875 | 73 | 72
2018-07-21 17:00 | 55 | 50 |  |  | 43302.7083 | 78 | 77
2018-07-21 17:30 | 57 | 53 |  |  | 43302.7292 | 83 | 82
2018-07-21 18:00 | 60 | 56 |  |  | 43302.75 | 87 | 86
2018-07-21 18:30 | 61 | 57 |  |  | 43302.7708 | 88 | 87
2018-07-21 19:00 | 62 | 59 |  |  | 43302.7917 | 90 | 89
2018-07-21 19:30 | 62 | 60 |  |  | 43302.8125 | 90 | 89
2018-07-21 20:00 | 62 | 59 |  |  | 43302.8333 | 89 | 89
2018-07-21 20:30 | 62 | 60 |  |  | 43302.8542 | 89 | 89
2018-07-21 21:00 | 60 | 58 |  |  | 43302.875 | 86 | 85
2018-07-21 21:30 | 59 | 57 |  |  | 43302.8958 | 84 | 83
2018-07-21 22:00 | 58 | 56 |  |  | 43302.9167 | 84 | 84
2018-07-21 22:30 | 58 | 55 |  |  | 43302.9375 | 83 | 83
2018-07-21 23:00 | 57 | 54 |  |  | 43302.9583 | 79 | 79
2018-07-21 23:30 | 53 | 51 |  |  | 43302.9792 | 75 | 75
2018-07-22 | 50 | 48 |  |  | 43303 | 72 | 72
2018-07-22 00:30 | 50 | 47 |  |  | 43303.0208 | 69 | 68
2018-07-22 01:00 | 49 | 45 |  |  | 43303.0417 | 66 | 65
2018-07-22 01:30 | 47 | 43 |  |  | 43303.0625 | 63 | 62
2018-07-22 02:00 | 46 | 41 |  |  | 43303.0833 | 61 | 60
2018-07-22 02:30 | 45 | 40 |  |  | 43303.1042 | 60 | 59
2018-07-22 03:00 | 44 | 39 |  |  | 43303.125 | 58 | 57
2018-07-22 03:30 | 43 | 38 |  |  | 43303.1458 | 58 | 56
2018-07-22 04:00 | 42 | 37 |  |  | 43303.1667 | 57 | 55
2018-07-22 04:30 | 42 | 37 |  |  | 43303.1875 | 56 | 55
2018-07-22 05:00 | 42 | 38 |  |  | 43303.2083 | 57 | 57
2018-07-22 05:30 | 43 | 40 |  |  | 43303.2292 | 59 | 59
2018-07-22 06:00 | 46 | 43 |  |  | 43303.25 | 62 | 61
2018-07-22 06:30 | 48 | 45 |  |  | 43303.2708 | 64 | 64
2018-07-22 07:00 | 47 | 44 |  |  | 43303.2917 | 67 | 66
2018-07-22 07:30 | 49 | 47 |  |  | 43303.3125 | 71 | 70
2018-07-22 08:00 | 50 | 47 |  |  | 43303.3333 | 71 | 71
2018-07-22 08:30 | 48 | 45 |  |  | 43303.3542 | 70 | 70
2018-07-22 09:00 | 45 | 43 |  |  | 43303.375 | 67 | 67
2018-07-22 09:30 | 43 | 41 |  |  | 43303.3958 | 64 | 64
2018-07-22 10:00 | 43 | 40 |  |  | 43303.4167 | 63 | 62
2018-07-22 10:30 | 42 | 39 |  |  | 43303.4375 | 62 | 62
2018-07-22 11:00 | 43 | 41 |  |  | 43303.4583 | 63 | 63
2018-07-22 11:30 | 41 | 39 |  |  | 43303.4792 | 59 | 59
2018-07-22 12:00 | 40 | 38 |  |  | 43303.5 | 59 | 59
2018-07-22 12:30 | 41 | 39 |  |  | 43303.5208 | 60 | 60
2018-07-22 13:00 | 43 | 41 |  |  | 43303.5417 | 61 | 61
2018-07-22 13:30 | 42 | 40 |  |  | 43303.5625 | 59 | 59
2018-07-22 14:00 | 43 | 40 |  |  | 43303.5833 | 58 | 58
2018-07-22 14:30 | 44 | 41 |  |  | 43303.6042 | 58 | 58
2018-07-22 15:00 | 46 | 43 |  |  | 43303.625 | 62 | 62
2018-07-22 15:30 | 49 | 47 |  |  | 43303.6458 | 70 | 69
2018-07-22 16:00 | 53 | 51 |  |  | 43303.6667 | 74 | 74
2018-07-22 16:30 | 54 | 52 |  |  | 43303.6875 | 77 | 77
2018-07-22 17:00 | 58 | 55 |  |  | 43303.7083 | 82 | 81
2018-07-22 17:30 | 61 | 58 |  |  | 43303.7292 | 87 | 86
2018-07-22 18:00 | 65 | 63 |  |  | 43303.75 | 92 | 92
2018-07-22 18:30 | 66 | 64 |  |  | 43303.7708 | 94 | 93
2018-07-22 19:00 | 67 | 65 |  |  | 43303.7917 | 96 | 96
2018-07-22 19:30 | 67 | 66 |  |  | 43303.8125 | 95 | 95
2018-07-22 20:00 | 67 | 65 |  |  | 43303.8333 | 94 | 94
2018-07-22 20:30 | 66 | 65 |  |  | 43303.8542 | 94 | 94
2018-07-22 21:00 | 64 | 62 |  |  | 43303.875 | 91 | 90
2018-07-22 21:30 | 61 | 58 |  |  | 43303.8958 | 87 | 86
2018-07-22 22:00 | 61 | 59 |  |  | 43303.9167 | 86 | 85
2018-07-22 22:30 | 61 | 58 |  |  | 43303.9375 | 85 | 84
2018-07-22 23:00 | 59 | 56 |  |  | 43303.9583 | 81 | 80
2018-07-22 23:30 | 56 | 53 |  |  | 43303.9792 | 77 | 76
2018-07-23 | 52 | 48 |  |  | 43304 | 72 | 71
2018-07-23 00:30 | 52 | 48 |  |  | 43304.0208 | 69 | 68
2018-07-23 01:00 | 48 | 45 |  |  | 43304.0417 | 65 | 64
2018-07-23 01:30 | 46 | 42 |  |  | 43304.0625 | 63 | 62
2018-07-23 02:00 | 46 | 42 |  |  | 43304.0833 | 61 | 60
2018-07-23 02:30 | 46 | 42 |  |  | 43304.1042 | 61 | 60
2018-07-23 03:00 | 46 | 42 |  |  | 43304.125 | 61 | 60
2018-07-23 03:30 | 46 | 41 |  |  | 43304.1458 | 60 | 59
2018-07-23 04:00 | 46 | 41 |  |  | 43304.1667 | 60 | 59
2018-07-23 04:30 | 47 | 43 |  |  | 43304.1875 | 62 | 60
2018-07-23 05:00 | 51 | 48 |  |  | 43304.2083 | 67 | 66
2018-07-23 05:30 | 58 | 56 |  |  | 43304.2292 | 74 | 73
2018-07-23 06:00 | 63 | 61 |  |  | 43304.25 | 82 | 81
2018-07-23 06:30 | 71 | 70 |  |  | 43304.2708 | 96 | 96
2018-07-23 07:00 | 78 | 77 |  |  | 43304.2917 | 110 | 110
2018-07-23 07:30 | 83 | 81 |  |  | 43304.3125 | 121 | 119
2018-07-23 08:00 | 81 | 77 |  |  | 43304.3333 | 121 | 117
2018-07-23 08:30 | 76 | 72 |  |  | 43304.3542 | 115 | 111
2018-07-23 09:00 | 71 | 67 |  |  | 43304.375 | 109 | 106
2018-07-23 09:30 | 67 | 64 |  |  | 43304.3958 | 102 | 100
2018-07-23 10:00 | 62 | 60 |  |  | 43304.4167 | 95 | 95
2018-07-23 10:30 | 60 | 58 |  |  | 43304.4375 | 91 | 91
2018-07-23 11:00 | 58 | 55 |  |  | 43304.4583 | 87 | 87
2018-07-23 11:30 | 56 | 54 |  |  | 43304.4792 | 86 | 86
2018-07-23 12:00 | 57 | 56 |  |  | 43304.5 | 87 | 87
2018-07-23 12:30 | 56 | 56 |  |  | 43304.5208 | 89 | 89
2018-07-23 13:00 | 59 | 58 |  |  | 43304.5417 | 90 | 90
2018-07-23 13:30 | 61 | 61 |  |  | 43304.5625 | 91 | 91
2018-07-23 14:00 | 62 | 61 |  |  | 43304.5833 | 91 | 91
2018-07-23 14:30 | 63 | 62 |  |  | 43304.6042 | 92 | 92
2018-07-23 15:00 | 63 | 63 |  |  | 43304.625 | 91 | 91
2018-07-23 15:30 | 63 | 62 |  |  | 43304.6458 | 91 | 91
2018-07-23 16:00 | 65 | 65 |  |  | 43304.6667 | 95 | 95
2018-07-23 16:30 | 68 | 66 |  |  | 43304.6875 | 97 | 96
2018-07-23 17:00 | 70 | 67 |  |  | 43304.7083 | 99 | 98
2018-07-23 17:30 | 73 | 69 |  |  | 43304.7292 | 104 | 100
2018-07-23 18:00 | 77 | 72 |  |  | 43304.75 | 109 | 104
2018-07-23 18:30 | 78 | 73 |  |  | 43304.7708 | 109 | 104
2018-07-23 19:00 | 79 | 74 |  |  | 43304.7917 | 111 | 106
2018-07-23 19:30 | 78 | 74 |  |  | 43304.8125 | 109 | 105
2018-07-23 20:00 | 77 | 73 |  |  | 43304.8333 | 107 | 103
2018-07-23 20:30 | 76 | 73 |  |  | 43304.8542 | 106 | 103
2018-07-23 21:00 | 75 | 70 |  |  | 43304.875 | 102 | 98
2018-07-23 21:30 | 72 | 66 |  |  | 43304.8958 | 97 | 92
2018-07-23 22:00 | 71 | 64 |  |  | 43304.9167 | 96 | 91
2018-07-23 22:30 | 68 | 60 |  |  | 43304.9375 | 93 | 87
2018-07-23 23:00 | 66 | 58 |  |  | 43304.9583 | 88 | 81
2018-07-23 23:30 | 63 | 54 |  |  | 43304.9792 | 83 | 77
2018-07-24 | 57 | 52 |  |  | 43305 | 74 | 72
2018-07-24 00:30 | 54 | 49 |  |  | 43305.0208 | 69 | 68
2018-07-24 01:00 | 52 | 47 |  |  | 43305.0417 | 66 | 65
2018-07-24 01:30 | 51 | 47 |  |  | 43305.0625 | 63 | 63
2018-07-24 02:00 | 50 | 45 |  |  | 43305.0833 | 63 | 62
2018-07-24 02:30 | 50 | 45 |  |  | 43305.1042 | 62 | 61
2018-07-24 03:00 | 50 | 45 |  |  | 43305.125 | 61 | 60
2018-07-24 03:30 | 50 | 45 |  |  | 43305.1458 | 61 | 60
2018-07-24 04:00 | 50 | 45 |  |  | 43305.1667 | 60 | 60
2018-07-24 04:30 | 51 | 47 |  |  | 43305.1875 | 62 | 62
2018-07-24 05:00 | 56 | 53 |  |  | 43305.2083 | 69 | 68
2018-07-24 05:30 | 61 | 58 |  |  | 43305.2292 | 75 | 75
2018-07-24 06:00 | 65 | 63 |  |  | 43305.25 | 84 | 84
2018-07-24 06:30 | 77 | 71 |  |  | 43305.2708 | 104 | 99
2018-07-24 07:00 | 85 | 77 |  |  | 43305.2917 | 120 | 112
2018-07-24 07:30 | 85 | 79 |  |  | 43305.3125 | 128 | 122
2018-07-24 08:00 | 81 | 75 |  |  | 43305.3333 | 129 | 120
2018-07-24 08:30 | 63 | 55 |  |  | 43305.3542 | 115 | 107
2018-07-24 09:00 | 44 | 37 |  |  | 43305.375 | 105 | 93
2018-07-24 09:30 | 42 | 36 |  |  | 43305.3958 | 102 | 88
2018-07-24 10:00 | 36 | 35 |  |  | 43305.4167 | 86 | 85
2018-07-24 10:30 | 37 | 36 |  |  | 43305.4375 | 82 | 82
2018-07-24 11:00 | 39 | 36 |  |  | 43305.4583 | 82 | 82
2018-07-24 11:30 | 39 | 36 |  |  | 43305.4792 | 80 | 80
2018-07-24 12:00 | 62 | 57 |  |  | 43305.5 | 92 | 92
2018-07-24 12:30 | 61 | 57 |  |  | 43305.5208 | 92 | 92
2018-07-24 13:00 | 60 | 56 |  |  | 43305.5417 | 90 | 90
2018-07-24 13:30 | 62 | 58 |  |  | 43305.5625 | 93 | 92
2018-07-24 14:00 | 64 | 59 |  |  | 43305.5833 | 95 | 94
2018-07-24 14:30 | 65 | 61 |  |  | 43305.6042 | 96 | 95
2018-07-24 15:00 | 66 | 62 |  |  | 43305.625 | 96 | 96
2018-07-24 15:30 | 66 | 64 |  |  | 43305.6458 | 96 | 96
2018-07-24 16:00 | 66 | 65 |  |  | 43305.6667 | 98 | 98
2018-07-24 16:30 | 66 | 66 |  |  | 43305.6875 | 103 | 100
2018-07-24 17:00 | 71 | 71 |  |  | 43305.7083 | 107 | 104
2018-07-24 17:30 | 72 | 72 |  |  | 43305.7292 | 110 | 106
2018-07-24 18:00 | 75 | 75 |  |  | 43305.75 | 112 | 109
2018-07-24 18:30 | 74 | 74 |  |  | 43305.7708 | 111 | 107
2018-07-24 19:00 | 76 | 76 |  |  | 43305.7917 | 112 | 108
2018-07-24 19:30 | 75 | 75 |  |  | 43305.8125 | 110 | 105
2018-07-24 20:00 | 74 | 74 |  |  | 43305.8333 | 109 | 103
2018-07-24 20:30 | 74 | 74 |  |  | 43305.8542 | 108 | 102
2018-07-24 21:00 | 71 | 71 |  |  | 43305.875 | 100 | 98
2018-07-24 21:30 | 69 | 68 |  |  | 43305.8958 | 97 | 94
2018-07-24 22:00 | 67 | 67 |  |  | 43305.9167 | 96 | 93
2018-07-24 22:30 | 64 | 64 |  |  | 43305.9375 | 93 | 90
2018-07-24 23:00 | 63 | 62 |  |  | 43305.9583 | 89 | 86
2018-07-24 23:30 | 59 | 59 |  |  | 43305.9792 | 85 | 82
2018-07-25 | 55 | 55 |  |  | 43306 | 80 | 78
2018-07-25 00:30 | 52 | 52 |  |  | 43306.0208 | 76 | 72
2018-07-25 01:00 | 49 | 49 |  |  | 43306.0417 | 72 | 68
2018-07-25 01:30 | 47 | 47 |  |  | 43306.0625 | 68 | 65
2018-07-25 02:00 | 46 | 46 |  |  | 43306.0833 | 67 | 64
2018-07-25 02:30 | 46 | 46 |  |  | 43306.1042 | 65 | 62
2018-07-25 03:00 | 45 | 45 |  |  | 43306.125 | 65 | 61
2018-07-25 03:30 | 45 | 45 |  |  | 43306.1458 | 64 | 61
2018-07-25 04:00 | 45 | 45 |  |  | 43306.1667 | 65 | 62
2018-07-25 04:30 | 47 | 47 |  |  | 43306.1875 | 67 | 64
2018-07-25 05:00 | 51 | 51 |  |  | 43306.2083 | 71 | 68
2018-07-25 05:30 | 58 | 57 |  |  | 43306.2292 | 77 | 75
2018-07-25 06:00 | 63 | 62 |  |  | 43306.25 | 85 | 83
2018-07-25 06:30 | 69 | 68 |  |  | 43306.2708 | 95 | 94
2018-07-25 07:00 | 69 | 68 |  |  | 43306.2917 | 107 | 103
2018-07-25 07:30 | 71 | 71 |  |  | 43306.3125 | 114 | 111
2018-07-25 08:00 | 72 | 72 |  |  | 43306.3333 | 118 | 114
2018-07-25 08:30 | 60 | 60 |  |  | 43306.3542 | 113 | 109
2018-07-25 09:00 | 42 | 42 |  |  | 43306.375 | 104 | 99
2018-07-25 09:30 | 41 | 41 |  |  | 43306.3958 | 101 | 96
2018-07-25 10:00 | 41 | 41 |  |  | 43306.4167 | 98 | 94
2018-07-25 10:30 | 38 | 38 |  |  | 43306.4375 | 91 | 87
2018-07-25 11:00 | 51 | 49 |  |  | 43306.4583 | 92 | 92
2018-07-25 11:30 | 69 | 67 |  |  | 43306.4792 | 97 | 97
2018-07-25 12:00 | 64 | 60 |  |  | 43306.5 | 96 | 96
2018-07-25 12:30 | 63 | 58 |  |  | 43306.5208 | 95 | 95
2018-07-25 13:00 | 66 | 61 |  |  | 43306.5417 | 98 | 98
2018-07-25 13:30 | 73 | 68 |  |  | 43306.5625 | 105 | 105
2018-07-25 14:00 | 75 | 70 |  |  | 43306.5833 | 100 | 100
2018-07-25 14:30 | 71 | 65 |  |  | 43306.6042 | 99 | 99
2018-07-25 15:00 | 71 | 66 |  |  | 43306.625 | 101 | 100
2018-07-25 15:30 | 71 | 67 |  |  | 43306.6458 | 101 | 101
2018-07-25 16:00 | 74 | 70 |  |  | 43306.6667 | 103 | 103
2018-07-25 16:30 | 75 | 73 |  |  | 43306.6875 | 104 | 104
2018-07-25 17:00 | 76 | 73 |  |  | 43306.7083 | 106 | 106
2018-07-25 17:30 | 78 | 76 |  |  | 43306.7292 | 109 | 109
2018-07-25 18:00 | 78 | 76 |  |  | 43306.75 | 109 | 109
2018-07-25 18:30 | 77 | 76 |  |  | 43306.7708 | 107 | 106
2018-07-25 19:00 | 78 | 76 |  |  | 43306.7917 | 107 | 107
2018-07-25 19:30 | 76 | 75 |  |  | 43306.8125 | 105 | 105
2018-07-25 20:00 | 76 | 74 |  |  | 43306.8333 | 104 | 103
2018-07-25 20:30 | 76 | 74 |  |  | 43306.8542 | 104 | 104
2018-07-25 21:00 | 74 | 72 |  |  | 43306.875 | 99 | 99
2018-07-25 21:30 | 71 | 69 |  |  | 43306.8958 | 95 | 95
2018-07-25 22:00 | 70 | 68 |  |  | 43306.9167 | 95 | 94
2018-07-25 22:30 | 66 | 64 |  |  | 43306.9375 | 91 | 91
2018-07-25 23:00 | 64 | 62 |  |  | 43306.9583 | 87 | 86
2018-07-25 23:30 | 61 | 59 |  |  | 43306.9792 | 84 | 82
2018-07-26 | 56 | 55 |  |  | 43307 | 77 | 76
2018-07-26 00:30 | 52 | 51 |  |  | 43307.0208 | 73 | 71
2018-07-26 01:00 | 47 | 47 |  |  | 43307.0417 | 69 | 66
2018-07-26 01:30 | 46 | 46 |  |  | 43307.0625 | 67 | 64
2018-07-26 02:00 | 46 | 46 |  |  | 43307.0833 | 66 | 62
2018-07-26 02:30 | 45 | 45 |  |  | 43307.1042 | 65 | 61
2018-07-26 03:00 | 44 | 44 |  |  | 43307.125 | 64 | 61
2018-07-26 03:30 | 44 | 44 |  |  | 43307.1458 | 63 | 60
2018-07-26 04:00 | 44 | 44 |  |  | 43307.1667 | 64 | 61
2018-07-26 04:30 | 46 | 46 |  |  | 43307.1875 | 66 | 63
2018-07-26 05:00 | 50 | 50 |  |  | 43307.2083 | 69 | 67
2018-07-26 05:30 | 55 | 54 |  |  | 43307.2292 | 76 | 74
2018-07-26 06:00 | 62 | 61 |  |  | 43307.25 | 83 | 82
2018-07-26 06:30 | 68 | 66 |  |  | 43307.2708 | 94 | 93
2018-07-26 07:00 | 72 | 70 |  |  | 43307.2917 | 103 | 103
2018-07-26 07:30 | 72 | 71 |  |  | 43307.3125 | 113 | 112
2018-07-26 08:00 | 71 | 71 |  |  | 43307.3333 | 116 | 113
2018-07-26 08:30 | 66 | 66 |  |  | 43307.3542 | 112 | 109
2018-07-26 09:00 | 94 | 93 |  |  | 43307.375 | 36 | 35
2018-07-26 09:30 | 93 | 91 |  |  | 43307.3958 | 31 | 29
2018-07-26 10:00 | 89 | 87 |  |  | 43307.4167 | 31 | 29
2018-07-26 10:30 | 84 | 82 |  |  | 43307.4375 | 35 | 32
2018-07-26 11:00 | 37 | 37 |  |  | 43307.4583 | 87 | 83
2018-07-26 11:30 | 51 | 50 |  |  | 43307.4792 | 91 | 89
2018-07-26 12:00 | 56 | 56 |  |  | 43307.5 | 91 | 89
2018-07-26 12:30 | 56 | 55 |  |  | 43307.5208 | 92 | 89
2018-07-26 13:00 | 57 | 56 |  |  | 43307.5417 | 93 | 91
2018-07-26 13:30 | 59 | 58 |  |  | 43307.5625 | 95 | 94
2018-07-26 14:00 | 61 | 60 |  |  | 43307.5833 | 96 | 95
2018-07-26 14:30 | 61 | 61 |  |  | 43307.6042 | 97 | 95
2018-07-26 15:00 | 66 | 66 |  |  | 43307.625 | 101 | 99
2018-07-26 15:30 | 65 | 65 |  |  | 43307.6458 | 99 | 96
2018-07-26 16:00 | 68 | 68 |  |  | 43307.6667 | 102 | 100
2018-07-26 16:30 | 70 | 70 |  |  | 43307.6875 | 105 | 103
2018-07-26 17:00 | 72 | 72 |  |  | 43307.7083 | 109 | 106
2018-07-26 17:30 | 71 | 71 |  |  | 43307.7292 | 108 | 105
2018-07-26 18:00 | 69 | 69 |  |  | 43307.75 | 109 | 105
2018-07-26 18:30 | 69 | 69 |  |  | 43307.7708 | 108 | 102
2018-07-26 19:00 | 71 | 71 |  |  | 43307.7917 | 109 | 104
2018-07-26 19:30 | 71 | 71 |  |  | 43307.8125 | 108 | 103
2018-07-26 20:00 | 70 | 70 |  |  | 43307.8333 | 104 | 102
2018-07-26 20:30 | 69 | 69 |  |  | 43307.8542 | 103 | 100
2018-07-26 21:00 | 68 | 68 |  |  | 43307.875 | 100 | 97
2018-07-26 21:30 | 64 | 64 |  |  | 43307.8958 | 96 | 92
2018-07-26 22:00 | 62 | 62 |  |  | 43307.9167 | 96 | 91
2018-07-26 22:30 | 59 | 59 |  |  | 43307.9375 | 91 | 87
2018-07-26 23:00 | 56 | 56 |  |  | 43307.9583 | 88 | 83
2018-07-26 23:30 | 53 | 53 |  |  | 43307.9792 | 83 | 79
2018-07-27 | 51 | 50 |  |  | 43308 | 75 | 74
2018-07-27 00:30 | 50 | 49 |  |  | 43308.0208 | 71 | 70
2018-07-27 01:00 | 49 | 48 |  |  | 43308.0417 | 67 | 66
2018-07-27 01:30 | 47 | 47 |  |  | 43308.0625 | 65 | 65
2018-07-27 02:00 | 47 | 46 |  |  | 43308.0833 | 64 | 64
2018-07-27 02:30 | 47 | 46 |  |  | 43308.1042 | 64 | 63
2018-07-27 03:00 | 47 | 46 |  |  | 43308.125 | 63 | 63
2018-07-27 03:30 | 46 | 45 |  |  | 43308.1458 | 63 | 63
2018-07-27 04:00 | 45 | 44 |  |  | 43308.1667 | 63 | 62
2018-07-27 04:30 | 47 | 46 |  |  | 43308.1875 | 65 | 65
2018-07-27 05:00 | 52 | 51 |  |  | 43308.2083 | 69 | 68
2018-07-27 05:30 | 57 | 55 |  |  | 43308.2292 | 75 | 75
2018-07-27 06:00 | 63 | 61 |  |  | 43308.25 | 82 | 82
2018-07-27 06:30 | 68 | 67 |  |  | 43308.2708 | 94 | 94
2018-07-27 07:00 | 71 | 70 |  |  | 43308.2917 | 104 | 104
2018-07-27 07:30 | 71 | 71 |  |  | 43308.3125 | 113 | 110
2018-07-27 08:00 | 69 | 69 |  |  | 43308.3333 | 114 | 110
2018-07-27 08:30 | 110 | 109 |  |  | 43308.3542 | 78 | 76
2018-07-27 09:00 | 121 | 120 |  |  | 43308.375 | 59 | 58
2018-07-27 09:30 | 115 | 113 |  |  | 43308.3958 | 56 | 55
2018-07-27 10:00 | 112 | 110 |  |  | 43308.4167 | 55 | 53
2018-07-27 10:30 | 110 | 107 |  |  | 43308.4375 | 55 | 52
2018-07-27 11:00 | 63 | 63 |  |  | 43308.4583 | 92 | 87
2018-07-27 11:30 | 54 | 53 |  |  | 43308.4792 | 91 | 85
2018-07-27 12:00 | 53 | 52 |  |  | 43308.5 | 91 | 86
2018-07-27 12:30 | 54 | 54 |  |  | 43308.5208 | 87 | 85
2018-07-27 13:00 | 54 | 54 |  |  | 43308.5417 | 88 | 87
2018-07-27 13:30 | 47 | 46 |  |  | 43308.5625 | 72 | 72
2018-07-27 14:00 | 48 | 47 |  |  | 43308.5833 | 67 | 67
2018-07-27 14:30 | 48 | 47 |  |  | 43308.6042 | 68 | 68
2018-07-27 15:00 | 48 | 47 |  |  | 43308.625 | 69 | 69
2018-07-27 15:30 | 49 | 48 |  |  | 43308.6458 | 70 | 70
2018-07-27 16:00 | 50 | 49 |  |  | 43308.6667 | 72 | 71
2018-07-27 16:30 | 51 | 50 |  |  | 43308.6875 | 73 | 73
2018-07-27 17:00 | 52 | 52 |  |  | 43308.7083 | 73 | 73
2018-07-27 17:30 | 54 | 54 |  |  | 43308.7292 | 76 | 76
2018-07-27 18:00 | 57 | 53 |  |  | 43308.75 | 75 | 75
2018-07-27 18:30 | 54 | 50 |  |  | 43308.7708 | 72 | 72
2018-07-27 19:00 | 56 | 52 |  |  | 43308.7917 | 72 | 72
2018-07-27 19:30 | 53 | 50 |  |  | 43308.8125 | 70 | 70
2018-07-27 20:00 | 51 | 48 |  |  | 43308.8333 | 68 | 68
2018-07-27 20:30 | 52 | 48 |  |  | 43308.8542 | 68 | 68
2018-07-27 21:00 | 50 | 46 |  |  | 43308.875 | 66 | 66
2018-07-27 21:30 | 48 | 44 |  |  | 43308.8958 | 62 | 61
2018-07-27 22:00 | 45 | 41 |  |  | 43308.9167 | 61 | 61
2018-07-27 22:30 | 43 | 39 |  |  | 43308.9375 | 58 | 58
2018-07-27 23:00 | 42 | 38 |  |  | 43308.9583 | 56 | 55
2018-07-27 23:30 | 39 | 35 |  |  | 43308.9792 | 53 | 53
2018-07-28 | 37 | 33 |  |  | 43309 | 49 | 48
2018-07-28 00:30 | 36 | 32 |  |  | 43309.0208 | 47 | 46
2018-07-28 01:00 | 35 | 31 |  |  | 43309.0417 | 45 | 44
2018-07-28 01:30 | 35 | 31 |  |  | 43309.0625 | 43 | 42
2018-07-28 02:00 | 34 | 30 |  |  | 43309.0833 | 44 | 43
2018-07-28 02:30 | 34 | 31 |  |  | 43309.1042 | 45 | 44
2018-07-28 03:00 | 35 | 32 |  |  | 43309.125 | 45 | 44
2018-07-28 03:30 | 35 | 31 |  |  | 43309.1458 | 45 | 44
2018-07-28 04:00 | 36 | 32 |  |  | 43309.1667 | 44 | 44
2018-07-28 04:30 | 37 | 34 |  |  | 43309.1875 | 46 | 46
2018-07-28 05:00 | 39 | 35 |  |  | 43309.2083 | 47 | 47
2018-07-28 05:30 | 39 | 36 |  |  | 43309.2292 | 50 | 50
2018-07-28 06:00 | 42 | 38 |  |  | 43309.25 | 52 | 52
2018-07-28 06:30 | 44 | 40 |  |  | 43309.2708 | 55 | 55
2018-07-28 07:00 | 45 | 41 |  |  | 43309.2917 | 57 | 57
2018-07-28 07:30 | 48 | 44 |  |  | 43309.3125 | 57 | 57
2018-07-28 08:00 | 46 | 41 |  |  | 43309.3333 | 52 | 52
2018-07-28 08:30 | 44 | 39 |  |  | 43309.3542 | 51 | 51
2018-07-28 09:00 | 44 | 39 |  |  | 43309.375 | 50 | 50
2018-07-28 09:30 | 42 | 37 |  |  | 43309.3958 | 49 | 49
2018-07-28 10:00 | 41 | 35 |  |  | 43309.4167 | 46 | 46
2018-07-28 10:30 | 40 | 34 |  |  | 43309.4375 | 44 | 44
2018-07-28 11:00 | 40 | 35 |  |  | 43309.4583 | 46 | 46
2018-07-28 11:30 | 41 | 36 |  |  | 43309.4792 | 47 | 47
2018-07-28 12:00 | 42 | 37 |  |  | 43309.5 | 49 | 49
2018-07-28 12:30 | 42 | 37 |  |  | 43309.5208 | 49 | 49
2018-07-28 13:00 | 42 | 38 |  |  | 43309.5417 | 51 | 51
2018-07-28 13:30 | 43 | 38 |  |  | 43309.5625 | 52 | 52
2018-07-28 14:00 | 44 | 40 |  |  | 43309.5833 | 53 | 53
2018-07-28 14:30 | 45 | 41 |  |  | 43309.6042 | 54 | 54
2018-07-28 15:00 | 47 | 43 |  |  | 43309.625 | 56 | 56
2018-07-28 15:30 | 49 | 45 |  |  | 43309.6458 | 59 | 59
2018-07-28 16:00 | 50 | 47 |  |  | 43309.6667 | 60 | 60
2018-07-28 16:30 | 50 | 48 |  |  | 43309.6875 | 61 | 61
2018-07-28 17:00 | 49 | 47 |  |  | 43309.7083 | 59 | 58
2018-07-28 17:30 | 48 | 46 |  |  | 43309.7292 | 59 | 58
2018-07-28 18:00 | 50 | 48 |  |  | 43309.75 | 63 | 62
2018-07-28 18:30 | 45 | 43 |  |  | 43309.7708 | 65 | 64
2018-07-28 19:00 | 46 | 44 |  |  | 43309.7917 | 66 | 65
2018-07-28 19:30 | 46 | 44 |  |  | 43309.8125 | 65 | 65
2018-07-28 20:00 | 46 | 44 |  |  | 43309.8333 | 65 | 64
2018-07-28 20:30 | 47 | 44 |  |  | 43309.8542 | 65 | 64
2018-07-28 21:00 | 45 | 43 |  |  | 43309.875 | 62 | 61
2018-07-28 21:30 | 46 | 44 |  |  | 43309.8958 | 62 | 61
2018-07-28 22:00 | 47 | 45 |  |  | 43309.9167 | 64 | 63
2018-07-28 22:30 | 47 | 45 |  |  | 43309.9375 | 65 | 64
2018-07-28 23:00 | 47 | 45 |  |  | 43309.9583 | 63 | 61
2018-07-28 23:30 | 44 | 43 |  |  | 43309.9792 | 60 | 59
2018-07-29 | 43 | 41 |  |  | 43310 | 57 | 56
2018-07-29 00:30 | 40 | 38 |  |  | 43310.0208 | 55 | 53
2018-07-29 01:00 | 39 | 37 |  |  | 43310.0417 | 51 | 50
2018-07-29 01:30 | 37 | 35 |  |  | 43310.0625 | 50 | 48
2018-07-29 02:00 | 37 | 35 |  |  | 43310.0833 | 49 | 47
2018-07-29 02:30 | 35 | 33 |  |  | 43310.1042 | 47 | 45
2018-07-29 03:00 | 33 | 32 |  |  | 43310.125 | 45 | 43
2018-07-29 03:30 | 34 | 32 |  |  | 43310.1458 | 45 | 44
2018-07-29 04:00 | 36 | 33 |  |  | 43310.1667 | 45 | 44
2018-07-29 04:30 | 36 | 34 |  |  | 43310.1875 | 46 | 45
2018-07-29 05:00 | 37 | 34 |  |  | 43310.2083 | 47 | 46
2018-07-29 05:30 | 37 | 34 |  |  | 43310.2292 | 47 | 46
2018-07-29 06:00 | 36 | 33 |  |  | 43310.25 | 47 | 46
2018-07-29 06:30 | 36 | 33 |  |  | 43310.2708 | 49 | 48
2018-07-29 07:00 | 37 | 35 |  |  | 43310.2917 | 51 | 50
2018-07-29 07:30 | 44 | 42 |  |  | 43310.3125 | 63 | 62
2018-07-29 08:00 | 45 | 43 |  |  | 43310.3333 | 64 | 63
2018-07-29 08:30 | 45 | 42 |  |  | 43310.3542 | 64 | 63
2018-07-29 09:00 | 44 | 42 |  |  | 43310.375 | 62 | 62
2018-07-29 09:30 | 44 | 41 |  |  | 43310.3958 | 61 | 61
2018-07-29 10:00 | 43 | 40 |  |  | 43310.4167 | 60 | 59
2018-07-29 10:30 | 41 | 38 |  |  | 43310.4375 | 57 | 57
2018-07-29 11:00 | 40 | 36 |  |  | 43310.4583 | 55 | 55
2018-07-29 11:30 | 38 | 34 |  |  | 43310.4792 | 52 | 52
2018-07-29 12:00 | 36 | 32 |  |  | 43310.5 | 47 | 47
2018-07-29 12:30 | 35 | 30 |  |  | 43310.5208 | 44 | 44
2018-07-29 13:00 | 35 | 31 |  |  | 43310.5417 | 46 | 46
2018-07-29 13:30 | 36 | 31 |  |  | 43310.5625 | 47 | 47
2018-07-29 14:00 | 37 | 32 |  |  | 43310.5833 | 48 | 48
2018-07-29 14:30 | 39 | 35 |  |  | 43310.6042 | 53 | 53
2018-07-29 15:00 | 42 | 38 |  |  | 43310.625 | 57 | 57
2018-07-29 15:30 | 46 | 43 |  |  | 43310.6458 | 62 | 62
2018-07-29 16:00 | 50 | 48 |  |  | 43310.6667 | 69 | 69
2018-07-29 16:30 | 53 | 51 |  |  | 43310.6875 | 71 | 71
2018-07-29 17:00 | 55 | 53 |  |  | 43310.7083 | 74 | 74
2018-07-29 17:30 | 55 | 53 |  |  | 43310.7292 | 74 | 74
2018-07-29 18:00 | 53 | 51 |  |  | 43310.75 | 70 | 70
2018-07-29 18:30 | 54 | 52 |  |  | 43310.7708 | 71 | 71
2018-07-29 19:00 | 54 | 52 |  |  | 43310.7917 | 73 | 72
2018-07-29 19:30 | 53 | 51 |  |  | 43310.8125 | 70 | 70
2018-07-29 20:00 | 53 | 51 |  |  | 43310.8333 | 70 | 69
2018-07-29 20:30 | 52 | 50 |  |  | 43310.8542 | 70 | 69
2018-07-29 21:00 | 50 | 47 |  |  | 43310.875 | 67 | 66
2018-07-29 21:30 | 48 | 46 |  |  | 43310.8958 | 65 | 64
2018-07-29 22:00 | 47 | 46 |  |  | 43310.9167 | 65 | 64
2018-07-29 22:30 | 46 | 44 |  |  | 43310.9375 | 63 | 62
2018-07-29 23:00 | 45 | 44 |  |  | 43310.9583 | 62 | 61
2018-07-29 23:30 | 44 | 42 |  |  | 43310.9792 | 59 | 57
2018-07-30 | 42 | 40 |  |  | 43311 | 56 | 55
2018-07-30 00:30 | 42 | 39 |  |  | 43311.0208 | 54 | 53
2018-07-30 01:00 | 37 | 34 |  |  | 43311.0417 | 50 | 49
2018-07-30 01:30 | 36 | 33 |  |  | 43311.0625 | 46 | 45
2018-07-30 02:00 | 36 | 33 |  |  | 43311.0833 | 45 | 45
2018-07-30 02:30 | 37 | 33 |  |  | 43311.1042 | 47 | 46
2018-07-30 03:00 | 38 | 34 |  |  | 43311.125 | 47 | 46
2018-07-30 03:30 | 38 | 35 |  |  | 43311.1458 | 47 | 46
2018-07-30 04:00 | 39 | 36 |  |  | 43311.1667 | 48 | 47
2018-07-30 04:30 | 40 | 37 |  |  | 43311.1875 | 49 | 49
2018-07-30 05:00 | 42 | 38 |  |  | 43311.2083 | 50 | 50
2018-07-30 05:30 | 44 | 40 |  |  | 43311.2292 | 52 | 52
2018-07-30 06:00 | 48 | 43 |  |  | 43311.25 | 57 | 57
2018-07-30 06:30 | 52 | 48 |  |  | 43311.2708 | 64 | 63
2018-07-30 07:00 | 55 | 50 |  |  | 43311.2917 | 70 | 70
2018-07-30 07:30 | 59 | 53 |  |  | 43311.3125 | 76 | 76
2018-07-30 08:00 | 55 | 49 |  |  | 43311.3333 | 73 | 73
2018-07-30 08:30 | 69 | 65 |  |  | 43311.3542 | 52 | 50
2018-07-30 09:00 | 87 | 86 |  |  | 43311.375 | 35 | 27
2018-07-30 09:30 | 84 | 82 |  |  | 43311.3958 | 34 | 26
2018-07-30 10:00 | 80 | 79 |  |  | 43311.4167 | 34 | 26
2018-07-30 10:30 | 79 | 78 |  |  | 43311.4375 | 32 | 25
2018-07-30 11:00 | 77 | 77 |  |  | 43311.4583 | 33 | 26
2018-07-30 11:30 | 51 | 45 |  |  | 43311.4792 | 55 | 54
2018-07-30 12:00 | 50 | 43 |  |  | 43311.5 | 62 | 62
2018-07-30 12:30 | 50 | 43 |  |  | 43311.5208 | 63 | 63
2018-07-30 13:00 | 48 | 40 |  |  | 43311.5417 | 58 | 57
2018-07-30 13:30 | 51 | 44 |  |  | 43311.5625 | 64 | 64
2018-07-30 14:00 | 53 | 47 |  |  | 43311.5833 | 66 | 66
2018-07-30 14:30 | 54 | 48 |  |  | 43311.6042 | 68 | 68
2018-07-30 15:00 | 57 | 51 |  |  | 43311.625 | 72 | 72
2018-07-30 15:30 | 59 | 53 |  |  | 43311.6458 | 75 | 75
2018-07-30 16:00 | 61 | 57 |  |  | 43311.6667 | 79 | 79
2018-07-30 16:30 | 60 | 56 |  |  | 43311.6875 | 77 | 77
2018-07-30 17:00 | 60 | 55 |  |  | 43311.7083 | 78 | 78
2018-07-30 17:30 | 61 | 57 |  |  | 43311.7292 | 78 | 78
2018-07-30 18:00 | 61 | 57 |  |  | 43311.75 | 81 | 81
2018-07-30 18:30 | 61 | 57 |  |  | 43311.7708 | 80 | 80
2018-07-30 19:00 | 60 | 57 |  |  | 43311.7917 | 81 | 81
2018-07-30 19:30 | 59 | 55 |  |  | 43311.8125 | 78 | 78
2018-07-30 20:00 | 58 | 55 |  |  | 43311.8333 | 76 | 76
2018-07-30 20:30 | 58 | 55 |  |  | 43311.8542 | 75 | 75
2018-07-30 21:00 | 56 | 52 |  |  | 43311.875 | 71 | 71
2018-07-30 21:30 | 53 | 49 |  |  | 43311.8958 | 66 | 66
2018-07-30 22:00 | 52 | 48 |  |  | 43311.9167 | 67 | 67
2018-07-30 22:30 | 50 | 46 |  |  | 43311.9375 | 64 | 64
2018-07-30 23:00 | 48 | 44 |  |  | 43311.9583 | 60 | 59
2018-07-30 23:30 | 44 | 40 |  |  | 43311.9792 | 56 | 56
2018-07-31 | 41 | 37 |  |  | 43312 | 53 | 52
2018-07-31 00:30 | 41 | 36 |  |  | 43312.0208 | 51 | 50
2018-07-31 01:00 | 41 | 36 |  |  | 43312.0417 | 49 | 49
2018-07-31 01:30 | 40 | 36 |  |  | 43312.0625 | 49 | 48
2018-07-31 02:00 | 41 | 37 |  |  | 43312.0833 | 51 | 51
2018-07-31 02:30 | 41 | 37 |  |  | 43312.1042 | 51 | 51
2018-07-31 03:00 | 42 | 38 |  |  | 43312.125 | 52 | 52
2018-07-31 03:30 | 42 | 38 |  |  | 43312.1458 | 54 | 53
2018-07-31 04:00 | 41 | 37 |  |  | 43312.1667 | 51 | 50
2018-07-31 04:30 | 42 | 38 |  |  | 43312.1875 | 53 | 53
2018-07-31 05:00 | 44 | 41 |  |  | 43312.2083 | 56 | 55
2018-07-31 05:30 | 49 | 45 |  |  | 43312.2292 | 61 | 61
2018-07-31 06:00 | 49 | 46 |  |  | 43312.25 | 63 | 62
2018-07-31 06:30 | 51 | 50 |  |  | 43312.2708 | 72 | 70
2018-07-31 07:00 | 55 | 53 |  |  | 43312.2917 | 80 | 79
2018-07-31 07:30 | 53 | 49 |  |  | 43312.3125 | 80 | 80
2018-07-31 08:00 | 50 | 46 |  |  | 43312.3333 | 76 | 76
2018-07-31 08:30 | 47 | 43 |  |  | 43312.3542 | 71 | 71
2018-07-31 09:00 | 44 | 39 |  |  | 43312.375 | 64 | 64
2018-07-31 09:30 | 43 | 37 |  |  | 43312.3958 | 60 | 60
2018-07-31 10:00 | 42 | 36 |  |  | 43312.4167 | 57 | 57
2018-07-31 10:30 | 41 | 35 |  |  | 43312.4375 | 54 | 53
2018-07-31 11:00 | 39 | 34 |  |  | 43312.4583 | 52 | 52
2018-07-31 11:30 | 39 | 34 |  |  | 43312.4792 | 55 | 54
2018-07-31 12:00 | 43 | 36 |  |  | 43312.5 | 57 | 57
2018-07-31 12:30 | 46 | 38 |  |  | 43312.5208 | 61 | 60
2018-07-31 13:00 | 45 | 38 |  |  | 43312.5417 | 59 | 59
2018-07-31 13:30 | 46 | 40 |  |  | 43312.5625 | 64 | 64
2018-07-31 14:00 | 48 | 41 |  |  | 43312.5833 | 66 | 66
2018-07-31 14:30 | 50 | 44 |  |  | 43312.6042 | 68 | 68
2018-07-31 15:00 | 53 | 48 |  |  | 43312.625 | 72 | 72
2018-07-31 15:30 | 56 | 51 |  |  | 43312.6458 | 76 | 76
2018-07-31 16:00 | 57 | 52 |  |  | 43312.6667 | 77 | 77
2018-07-31 16:30 | 54 | 51 |  |  | 43312.6875 | 73 | 73
2018-07-31 17:00 | 54 | 54 |  |  | 43312.7083 | 80 | 76
2018-07-31 17:30 | 55 | 55 |  |  | 43312.7292 | 84 | 78
2018-07-31 18:00 | 54 | 54 |  |  | 43312.75 | 85 | 79
2018-07-31 18:30 | 55 | 55 |  |  | 43312.7708 | 84 | 80
2018-07-31 19:00 | 56 | 56 |  |  | 43312.7917 | 86 | 81
2018-07-31 19:30 | 57 | 56 |  |  | 43312.8125 | 85 | 80
2018-07-31 20:00 | 54 | 54 |  |  | 43312.8333 | 82 | 76
2018-07-31 20:30 | 54 | 54 |  |  | 43312.8542 | 80 | 75
2018-07-31 21:00 | 50 | 50 |  |  | 43312.875 | 75 | 70
2018-07-31 21:30 | 48 | 48 |  |  | 43312.8958 | 72 | 67
2018-07-31 22:00 | 49 | 49 |  |  | 43312.9167 | 74 | 68
2018-07-31 22:30 | 49 | 47 |  |  | 43312.9375 | 67 | 66
2018-07-31 23:00 | 48 | 45 |  |  | 43312.9583 | 63 | 63
2018-07-31 23:30 | 47 | 44 |  |  | 43312.9792 | 60 | 60
2018-08-01 | 45 | 40 |  |  | 43313 | 55 | 55
2018-08-01 00:30 | 43 | 39 |  |  | 43313.0208 | 55 | 54
2018-08-01 01:00 | 37 | 33 |  |  | 43313.0417 | 45 | 45
2018-08-01 01:30 | 34 | 29 |  |  | 43313.0625 | 39 | 38
2018-08-01 02:00 | 34 | 29 |  |  | 43313.0833 | 38 | 38
2018-08-01 02:30 | 34 | 30 |  |  | 43313.1042 | 41 | 40
2018-08-01 03:00 | 35 | 31 |  |  | 43313.125 | 44 | 43
2018-08-01 03:30 | 37 | 33 |  |  | 43313.1458 | 48 | 47
2018-08-01 04:00 | 38 | 35 |  |  | 43313.1667 | 49 | 48
2018-08-01 04:30 | 41 | 38 |  |  | 43313.1875 | 53 | 52
2018-08-01 05:00 | 43 | 40 |  |  | 43313.2083 | 54 | 53
2018-08-01 05:30 | 46 | 43 |  |  | 43313.2292 | 58 | 57
2018-08-01 06:00 | 49 | 45 |  |  | 43313.25 | 61 | 60
2018-08-01 06:30 | 53 | 49 |  |  | 43313.2708 | 67 | 66
2018-08-01 07:00 | 56 | 49 |  |  | 43313.2917 | 74 | 74
2018-08-01 07:30 | 51 | 48 |  |  | 43313.3125 | 78 | 78
2018-08-01 08:00 | 46 | 45 |  |  | 43313.3333 | 72 | 72
2018-08-01 08:30 | 41 | 41 |  |  | 43313.3542 | 66 | 66
2018-08-01 09:00 | 38 | 37 |  |  | 43313.375 | 60 | 60
2018-08-01 09:30 | 39 | 38 |  |  | 43313.3958 | 59 | 58
2018-08-01 10:00 | 39 | 37 |  |  | 43313.4167 | 59 | 58
2018-08-01 10:30 | 38 | 36 |  |  | 43313.4375 | 57 | 56
2018-08-01 11:00 | 42 | 38 |  |  | 43313.4583 | 61 | 57
2018-08-01 11:30 | 42 | 37 |  |  | 43313.4792 | 60 | 56
2018-08-01 12:00 | 42 | 37 |  |  | 43313.5 | 61 | 56
2018-08-01 12:30 | 42 | 37 |  |  | 43313.5208 | 61 | 57
2018-08-01 13:00 | 42 | 38 |  |  | 43313.5417 | 61 | 57
2018-08-01 13:30 | 43 | 39 |  |  | 43313.5625 | 62 | 58
2018-08-01 14:00 | 45 | 41 |  |  | 43313.5833 | 63 | 60
2018-08-01 14:30 | 47 | 44 |  |  | 43313.6042 | 64 | 62
2018-08-01 15:00 | 47 | 44 |  |  | 43313.625 | 64 | 62
2018-08-01 15:30 | 47 | 44 |  |  | 43313.6458 | 64 | 62
2018-08-01 16:00 | 49 | 47 |  |  | 43313.6667 | 67 | 65
2018-08-01 16:30 | 49 | 48 |  |  | 43313.6875 | 66 | 65
2018-08-01 17:00 | 49 | 48 |  |  | 43313.7083 | 66 | 66
2018-08-01 17:30 | 50 | 49 |  |  | 43313.7292 | 67 | 67
2018-08-01 18:00 | 52 | 51 |  |  | 43313.75 | 74 | 72
2018-08-01 18:30 | 52 | 52 |  |  | 43313.7708 | 74 | 71
2018-08-01 19:00 | 53 | 52 |  |  | 43313.7917 | 74 | 71
2018-08-01 19:30 | 53 | 52 |  |  | 43313.8125 | 75 | 71
2018-08-01 20:00 | 53 | 52 |  |  | 43313.8333 | 72 | 69
2018-08-01 20:30 | 54 | 54 |  |  | 43313.8542 | 73 | 71
2018-08-01 21:00 | 51 | 51 |  |  | 43313.875 | 70 | 67
2018-08-01 21:30 | 48 | 48 |  |  | 43313.8958 | 65 | 61
2018-08-01 22:00 | 46 | 45 |  |  | 43313.9167 | 64 | 59
2018-08-01 22:30 | 44 | 43 |  |  | 43313.9375 | 62 | 58
2018-08-01 23:00 | 44 | 42 |  |  | 43313.9583 | 61 | 55
2018-08-01 23:30 | 39 | 37 |  |  | 43313.9792 | 52 | 48
2018-08-02 | 37 | 34 |  |  | 43314 | 44 | 43
2018-08-02 00:30 | 36 | 32 |  |  | 43314.0208 | 44 | 42
2018-08-02 01:00 | 36 | 32 |  |  | 43314.0417 | 42 | 41
2018-08-02 01:30 | 35 | 32 |  |  | 43314.0625 | 42 | 41
2018-08-02 02:00 | 36 | 32 |  |  | 43314.0833 | 42 | 41
2018-08-02 02:30 | 38 | 34 |  |  | 43314.1042 | 45 | 44
2018-08-02 03:00 | 39 | 35 |  |  | 43314.125 | 47 | 46
2018-08-02 03:30 | 40 | 36 |  |  | 43314.1458 | 49 | 48
2018-08-02 04:00 | 41 | 37 |  |  | 43314.1667 | 50 | 48
2018-08-02 04:30 | 43 | 39 |  |  | 43314.1875 | 51 | 50
2018-08-02 05:00 | 46 | 43 |  |  | 43314.2083 | 55 | 54
2018-08-02 05:30 | 49 | 46 |  |  | 43314.2292 | 59 | 59
2018-08-02 06:00 | 53 | 52 |  |  | 43314.25 | 67 | 66
2018-08-02 06:30 | 58 | 57 |  |  | 43314.2708 | 76 | 76
2018-08-02 07:00 | 56 | 55 |  |  | 43314.2917 | 80 | 80
2018-08-02 07:30 | 57 | 57 |  |  | 43314.3125 | 87 | 87
2018-08-02 08:00 | 56 | 55 |  |  | 43314.3333 | 85 | 84
2018-08-02 08:30 | 52 | 52 |  |  | 43314.3542 | 79 | 78
2018-08-02 09:00 | 48 | 48 |  |  | 43314.375 | 74 | 74
2018-08-02 09:30 | 45 | 44 |  |  | 43314.3958 | 67 | 67
2018-08-02 10:00 | 44 | 43 |  |  | 43314.4167 | 67 | 66
2018-08-02 10:30 | 44 | 44 |  |  | 43314.4375 | 66 | 66
2018-08-02 11:00 | 45 | 45 |  |  | 43314.4583 | 67 | 66
2018-08-02 11:30 | 44 | 44 |  |  | 43314.4792 | 67 | 66
2018-08-02 12:00 | 45 | 44 |  |  | 43314.5 | 67 | 67
2018-08-02 12:30 | 45 | 44 |  |  | 43314.5208 | 67 | 67
2018-08-02 13:00 | 47 | 47 |  |  | 43314.5417 | 67 | 67
2018-08-02 13:30 | 50 | 49 |  |  | 43314.5625 | 70 | 70
2018-08-02 14:00 | 51 | 50 |  |  | 43314.5833 | 70 | 70
2018-08-02 14:30 | 51 | 50 |  |  | 43314.6042 | 70 | 70
2018-08-02 15:00 | 52 | 51 |  |  | 43314.625 | 72 | 72
2018-08-02 15:30 | 53 | 52 |  |  | 43314.6458 | 74 | 74
2018-08-02 16:00 | 55 | 53 |  |  | 43314.6667 | 76 | 75
2018-08-02 16:30 | 55 | 54 |  |  | 43314.6875 | 74 | 74
2018-08-02 17:00 | 56 | 54 |  |  | 43314.7083 | 73 | 73
2018-08-02 17:30 | 54 | 53 |  |  | 43314.7292 | 74 | 73
2018-08-02 18:00 | 58 | 57 |  |  | 43314.75 | 78 | 78
2018-08-02 18:30 | 58 | 57 |  |  | 43314.7708 | 80 | 79
2018-08-02 19:00 | 59 | 59 |  |  | 43314.7917 | 81 | 80
2018-08-02 19:30 | 58 | 57 |  |  | 43314.8125 | 78 | 77
2018-08-02 20:00 | 56 | 56 |  |  | 43314.8333 | 76 | 75
2018-08-02 20:30 | 57 | 56 |  |  | 43314.8542 | 76 | 76
2018-08-02 21:00 | 54 | 54 |  |  | 43314.875 | 71 | 70
2018-08-02 21:30 | 50 | 49 |  |  | 43314.8958 | 65 | 65
2018-08-02 22:00 | 48 | 48 |  |  | 43314.9167 | 64 | 64
2018-08-02 22:30 | 46 | 46 |  |  | 43314.9375 | 62 | 62
2018-08-02 23:00 | 45 | 45 |  |  | 43314.9583 | 58 | 58
2018-08-02 23:30 | 40 | 39 |  |  | 43314.9792 | 52 | 52
2018-08-03 | 34 | 33 |  |  | 43315 | 45 | 45
2018-08-03 00:30 | 33 | 32 |  |  | 43315.0208 | 43 | 43
2018-08-03 01:00 | 31 | 30 |  |  | 43315.0417 | 38 | 38
2018-08-03 01:30 | 29 | 28 |  |  | 43315.0625 | 37 | 36
2018-08-03 02:00 | 30 | 28 |  |  | 43315.0833 | 38 | 37
2018-08-03 02:30 | 33 | 31 |  |  | 43315.1042 | 42 | 42
2018-08-03 03:00 | 35 | 33 |  |  | 43315.125 | 44 | 44
2018-08-03 03:30 | 35 | 33 |  |  | 43315.1458 | 43 | 43
2018-08-03 04:00 | 36 | 34 |  |  | 43315.1667 | 46 | 46
2018-08-03 04:30 | 38 | 36 |  |  | 43315.1875 | 48 | 48
2018-08-03 05:00 | 40 | 38 |  |  | 43315.2083 | 51 | 50
2018-08-03 05:30 | 43 | 42 |  |  | 43315.2292 | 55 | 55
2018-08-03 06:00 | 47 | 46 |  |  | 43315.25 | 60 | 60
2018-08-03 06:30 | 53 | 52 |  |  | 43315.2708 | 71 | 71
2018-08-03 07:00 | 54 | 54 |  |  | 43315.2917 | 76 | 76
2018-08-03 07:30 | 58 | 58 |  |  | 43315.3125 | 83 | 82
2018-08-03 08:00 | 54 | 54 |  |  | 43315.3333 | 77 | 77
2018-08-03 08:30 | 50 | 50 |  |  | 43315.3542 | 72 | 72
2018-08-03 09:00 | 46 | 46 |  |  | 43315.375 | 68 | 68
2018-08-03 09:30 | 43 | 43 |  |  | 43315.3958 | 63 | 62
2018-08-03 10:00 | 44 | 44 |  |  | 43315.4167 | 64 | 64
2018-08-03 10:30 | 44 | 44 |  |  | 43315.4375 | 64 | 64
2018-08-03 11:00 | 45 | 45 |  |  | 43315.4583 | 66 | 65
2018-08-03 11:30 | 47 | 47 |  |  | 43315.4792 | 70 | 70
2018-08-03 12:00 | 48 | 48 |  |  | 43315.5 | 70 | 70
2018-08-03 12:30 | 48 | 48 |  |  | 43315.5208 | 69 | 69
2018-08-03 13:00 | 47 | 47 |  |  | 43315.5417 | 67 | 66
2018-08-03 13:30 | 47 | 47 |  |  | 43315.5625 | 67 | 67
2018-08-03 14:00 | 48 | 48 |  |  | 43315.5833 | 68 | 67
2018-08-03 14:30 | 49 | 49 |  |  | 43315.6042 | 67 | 67
2018-08-03 15:00 | 46 | 46 |  |  | 43315.625 | 67 | 66
2018-08-03 15:30 | 45 | 45 |  |  | 43315.6458 | 65 | 65
2018-08-03 16:00 | 47 | 47 |  |  | 43315.6667 | 67 | 66
2018-08-03 16:30 | 46 | 46 |  |  | 43315.6875 | 67 | 67
2018-08-03 17:00 | 47 | 46 |  |  | 43315.7083 | 69 | 69
2018-08-03 17:30 | 52 | 51 |  |  | 43315.7292 | 72 | 72
2018-08-03 18:00 | 53 | 52 |  |  | 43315.75 | 73 | 73
2018-08-03 18:30 | 53 | 52 |  |  | 43315.7708 | 72 | 72
2018-08-03 19:00 | 52 | 51 |  |  | 43315.7917 | 71 | 71
2018-08-03 19:30 | 52 | 51 |  |  | 43315.8125 | 71 | 71
2018-08-03 20:00 | 52 | 51 |  |  | 43315.8333 | 69 | 69
2018-08-03 20:30 | 52 | 51 |  |  | 43315.8542 | 70 | 70
2018-08-03 21:00 | 49 | 48 |  |  | 43315.875 | 66 | 66
2018-08-03 21:30 | 48 | 47 |  |  | 43315.8958 | 64 | 64
2018-08-03 22:00 | 48 | 47 |  |  | 43315.9167 | 65 | 64
2018-08-03 22:30 | 46 | 45 |  |  | 43315.9375 | 62 | 62
2018-08-03 23:00 | 46 | 44 |  |  | 43315.9583 | 59 | 59
2018-08-03 23:30 | 42 | 40 |  |  | 43315.9792 | 56 | 55
2018-08-04 | 38 | 35 |  |  | 43316 | 50 | 49
2018-08-04 00:30 | 38 | 35 |  |  | 43316.0208 | 49 | 48
2018-08-04 01:00 | 37 | 34 |  |  | 43316.0417 | 46 | 45
2018-08-04 01:30 | 36 | 32 |  |  | 43316.0625 | 45 | 44
2018-08-04 02:00 | 36 | 33 |  |  | 43316.0833 | 46 | 45
2018-08-04 02:30 | 36 | 33 |  |  | 43316.1042 | 45 | 44
2018-08-04 03:00 | 36 | 33 |  |  | 43316.125 | 45 | 45
2018-08-04 03:30 | 38 | 35 |  |  | 43316.1458 | 47 | 46
2018-08-04 04:00 | 37 | 34 |  |  | 43316.1667 | 46 | 46
2018-08-04 04:30 | 37 | 34 |  |  | 43316.1875 | 46 | 46
2018-08-04 05:00 | 39 | 37 |  |  | 43316.2083 | 48 | 47
2018-08-04 05:30 | 40 | 37 |  |  | 43316.2292 | 49 | 49
2018-08-04 06:00 | 39 | 36 |  |  | 43316.25 | 47 | 47
2018-08-04 06:30 | 38 | 36 |  |  | 43316.2708 | 49 | 48
2018-08-04 07:00 | 39 | 36 |  |  | 43316.2917 | 51 | 51
2018-08-04 07:30 | 40 | 38 |  |  | 43316.3125 | 52 | 52
2018-08-04 08:00 | 39 | 37 |  |  | 43316.3333 | 52 | 52
2018-08-04 08:30 | 37 | 35 |  |  | 43316.3542 | 51 | 51
2018-08-04 09:00 | 36 | 34 |  |  | 43316.375 | 50 | 50
2018-08-04 09:30 | 37 | 35 |  |  | 43316.3958 | 51 | 51
2018-08-04 10:00 | 37 | 35 |  |  | 43316.4167 | 51 | 51
2018-08-04 10:30 | 35 | 34 |  |  | 43316.4375 | 49 | 49
2018-08-04 11:00 | 35 | 33 |  |  | 43316.4583 | 49 | 49
2018-08-04 11:30 | 35 | 33 |  |  | 43316.4792 | 48 | 48
2018-08-04 12:00 | 34 | 32 |  |  | 43316.5 | 47 | 47
2018-08-04 12:30 | 32 | 30 |  |  | 43316.5208 | 44 | 44
2018-08-04 13:00 | 31 | 29 |  |  | 43316.5417 | 43 | 43
2018-08-04 13:30 | 31 | 29 |  |  | 43316.5625 | 44 | 44
2018-08-04 14:00 | 33 | 31 |  |  | 43316.5833 | 45 | 45
2018-08-04 14:30 | 34 | 32 |  |  | 43316.6042 | 47 | 47
2018-08-04 15:00 | 36 | 34 |  |  | 43316.625 | 49 | 49
2018-08-04 15:30 | 39 | 37 |  |  | 43316.6458 | 52 | 52
2018-08-04 16:00 | 39 | 38 |  |  | 43316.6667 | 53 | 53
2018-08-04 16:30 | 40 | 38 |  |  | 43316.6875 | 54 | 54
2018-08-04 17:00 | 43 | 41 |  |  | 43316.7083 | 57 | 57
2018-08-04 17:30 | 44 | 42 |  |  | 43316.7292 | 59 | 59
2018-08-04 18:00 | 44 | 40 |  |  | 43316.75 | 58 | 57
2018-08-04 18:30 | 44 | 39 |  |  | 43316.7708 | 58 | 56
2018-08-04 19:00 | 45 | 41 |  |  | 43316.7917 | 60 | 58
2018-08-04 19:30 | 45 | 41 |  |  | 43316.8125 | 59 | 57
2018-08-04 20:00 | 44 | 40 |  |  | 43316.8333 | 57 | 57
2018-08-04 20:30 | 42 | 40 |  |  | 43316.8542 | 57 | 57
2018-08-04 21:00 | 41 | 39 |  |  | 43316.875 | 55 | 55
2018-08-04 21:30 | 41 | 39 |  |  | 43316.8958 | 53 | 53
2018-08-04 22:00 | 42 | 40 |  |  | 43316.9167 | 55 | 54
2018-08-04 22:30 | 41 | 38 |  |  | 43316.9375 | 53 | 53
2018-08-04 23:00 | 39 | 37 |  |  | 43316.9583 | 51 | 51
2018-08-04 23:30 | 38 | 35 |  |  | 43316.9792 | 49 | 49
2018-08-05 | 36 | 34 |  |  | 43317 | 48 | 47
2018-08-05 00:30 | 35 | 31 |  |  | 43317.0208 | 45 | 44
2018-08-05 01:00 | 34 | 31 |  |  | 43317.0417 | 42 | 41
2018-08-05 01:30 | 35 | 31 |  |  | 43317.0625 | 43 | 42
2018-08-05 02:00 | 36 | 32 |  |  | 43317.0833 | 43 | 43
2018-08-05 02:30 | 34 | 33 |  |  | 43317.1042 | 45 | 44
2018-08-05 03:00 | 33 | 33 |  |  | 43317.125 | 45 | 43
2018-08-05 03:30 | 32 | 32 |  |  | 43317.1458 | 45 | 43
2018-08-05 04:00 | 32 | 32 |  |  | 43317.1667 | 45 | 43
2018-08-05 04:30 | 32 | 32 |  |  | 43317.1875 | 44 | 42
2018-08-05 05:00 | 31 | 31 |  |  | 43317.2083 | 44 | 42
2018-08-05 05:30 | 31 | 31 |  |  | 43317.2292 | 45 | 43
2018-08-05 06:00 | 31 | 30 |  |  | 43317.25 | 44 | 42
2018-08-05 06:30 | 31 | 31 |  |  | 43317.2708 | 46 | 44
2018-08-05 07:00 | 32 | 32 |  |  | 43317.2917 | 47 | 45
2018-08-05 07:30 | 32 | 31 |  |  | 43317.3125 | 48 | 46
2018-08-05 08:00 | 30 | 30 |  |  | 43317.3333 | 46 | 44
2018-08-05 08:30 | 30 | 30 |  |  | 43317.3542 | 46 | 44
2018-08-05 09:00 | 30 | 30 |  |  | 43317.375 | 45 | 44
2018-08-05 09:30 | 30 | 30 |  |  | 43317.3958 | 46 | 45
2018-08-05 10:00 | 30 | 30 |  |  | 43317.4167 | 46 | 45
2018-08-05 10:30 | 29 | 29 |  |  | 43317.4375 | 45 | 44
2018-08-05 11:00 | 28 | 28 |  |  | 43317.4583 | 44 | 43
2018-08-05 11:30 | 28 | 28 |  |  | 43317.4792 | 43 | 42
2018-08-05 12:00 | 28 | 28 |  |  | 43317.5 | 42 | 42
2018-08-05 12:30 | 26 | 26 |  |  | 43317.5208 | 41 | 41
2018-08-05 13:00 | 27 | 27 |  |  | 43317.5417 | 41 | 41
2018-08-05 13:30 | 28 | 28 |  |  | 43317.5625 | 43 | 42
2018-08-05 14:00 | 29 | 29 |  |  | 43317.5833 | 43 | 42
2018-08-05 14:30 | 29 | 29 |  |  | 43317.6042 | 44 | 44
2018-08-05 15:00 | 31 | 30 |  |  | 43317.625 | 46 | 45
2018-08-05 15:30 | 33 | 33 |  |  | 43317.6458 | 49 | 49
2018-08-05 16:00 | 36 | 36 |  |  | 43317.6667 | 52 | 51
2018-08-05 16:30 | 36 | 36 |  |  | 43317.6875 | 53 | 51
2018-08-05 17:00 | 39 | 39 |  |  | 43317.7083 | 56 | 55
2018-08-05 17:30 | 45 | 45 |  |  | 43317.7292 | 62 | 61
2018-08-05 18:00 | 46 | 45 |  |  | 43317.75 | 65 | 63
2018-08-05 18:30 | 45 | 45 |  |  | 43317.7708 | 65 | 62
2018-08-05 19:00 | 45 | 44 |  |  | 43317.7917 | 65 | 62
2018-08-05 19:30 | 44 | 44 |  |  | 43317.8125 | 65 | 62
2018-08-05 20:00 | 44 | 43 |  |  | 43317.8333 | 63 | 60
2018-08-05 20:30 | 44 | 44 |  |  | 43317.8542 | 62 | 60
2018-08-05 21:00 | 41 | 41 |  |  | 43317.875 | 58 | 56
2018-08-05 21:30 | 40 | 40 |  |  | 43317.8958 | 58 | 56
2018-08-05 22:00 | 41 | 41 |  |  | 43317.9167 | 60 | 58
2018-08-05 22:30 | 41 | 41 |  |  | 43317.9375 | 60 | 58
2018-08-05 23:00 | 41 | 41 |  |  | 43317.9583 | 58 | 55
2018-08-05 23:30 | 38 | 38 |  |  | 43317.9792 | 55 | 52
2018-08-06 | 35 | 35 |  |  | 43318 | 51 | 48
2018-08-06 00:30 | 34 | 34 |  |  | 43318.0208 | 50 | 46
2018-08-06 01:00 | 34 | 34 |  |  | 43318.0417 | 50 | 46
2018-08-06 01:30 | 34 | 34 |  |  | 43318.0625 | 48 | 45
2018-08-06 02:00 | 33 | 33 |  |  | 43318.0833 | 48 | 45
2018-08-06 02:30 | 33 | 33 |  |  | 43318.1042 | 48 | 45
2018-08-06 03:00 | 33 | 33 |  |  | 43318.125 | 48 | 45
2018-08-06 03:30 | 34 | 33 |  |  | 43318.1458 | 48 | 45
2018-08-06 04:00 | 34 | 34 |  |  | 43318.1667 | 48 | 45
2018-08-06 04:30 | 35 | 35 |  |  | 43318.1875 | 49 | 46
2018-08-06 05:00 | 37 | 37 |  |  | 43318.2083 | 51 | 49
2018-08-06 05:30 | 41 | 41 |  |  | 43318.2292 | 54 | 52
2018-08-06 06:00 | 45 | 45 |  |  | 43318.25 | 57 | 56
2018-08-06 06:30 | 46 | 46 |  |  | 43318.2708 | 64 | 63
2018-08-06 07:00 | 47 | 47 |  |  | 43318.2917 | 72 | 72
2018-08-06 07:30 | 49 | 49 |  |  | 43318.3125 | 76 | 76
2018-08-06 08:00 | 44 | 44 |  |  | 43318.3333 | 72 | 72
2018-08-06 08:30 | 39 | 39 |  |  | 43318.3542 | 68 | 68
2018-08-06 09:00 | 36 | 36 |  |  | 43318.375 | 64 | 64
2018-08-06 09:30 | 35 | 34 |  |  | 43318.3958 | 62 | 62
2018-08-06 10:00 | 33 | 32 |  |  | 43318.4167 | 58 | 58
2018-08-06 10:30 | 32 | 30 |  |  | 43318.4375 | 57 | 57
2018-08-06 11:00 | 33 | 32 |  |  | 43318.4583 | 58 | 58
2018-08-06 11:30 | 33 | 32 |  |  | 43318.4792 | 57 | 57
2018-08-06 12:00 | 32 | 31 |  |  | 43318.5 | 57 | 57
2018-08-06 12:30 | 33 | 32 |  |  | 43318.5208 | 58 | 58
2018-08-06 13:00 | 35 | 34 |  |  | 43318.5417 | 60 | 60
2018-08-06 13:30 | 38 | 37 |  |  | 43318.5625 | 63 | 63
2018-08-06 14:00 | 42 | 41 |  |  | 43318.5833 | 67 | 67
2018-08-06 14:30 | 42 | 41 |  |  | 43318.6042 | 67 | 67
2018-08-06 15:00 | 42 | 41 |  |  | 43318.625 | 69 | 69
2018-08-06 15:30 | 45 | 45 |  |  | 43318.6458 | 70 | 69
2018-08-06 16:00 | 51 | 50 |  |  | 43318.6667 | 71 | 70
2018-08-06 16:30 | 49 | 49 |  |  | 43318.6875 | 70 | 69
2018-08-06 17:00 | 51 | 51 |  |  | 43318.7083 | 71 | 70
2018-08-06 17:30 | 53 | 53 |  |  | 43318.7292 | 73 | 72
2018-08-06 18:00 | 53 | 53 |  |  | 43318.75 | 74 | 72
2018-08-06 18:30 | 49 | 48 |  |  | 43318.7708 | 71 | 66
2018-08-06 19:00 | 47 | 47 |  |  | 43318.7917 | 69 | 66
2018-08-06 19:30 | 48 | 48 |  |  | 43318.8125 | 69 | 66
2018-08-06 20:00 | 47 | 47 |  |  | 43318.8333 | 66 | 64
2018-08-06 20:30 | 46 | 46 |  |  | 43318.8542 | 64 | 62
2018-08-06 21:00 | 44 | 44 |  |  | 43318.875 | 61 | 59
2018-08-06 21:30 | 42 | 42 |  |  | 43318.8958 | 59 | 57
2018-08-06 22:00 | 41 | 41 |  |  | 43318.9167 | 58 | 56
2018-08-06 22:30 | 38 | 38 |  |  | 43318.9375 | 55 | 53
2018-08-06 23:00 | 38 | 38 |  |  | 43318.9583 | 53 | 50
2018-08-06 23:30 | 34 | 33 |  |  | 43318.9792 | 50 | 46
2018-08-07 | 30 | 30 |  |  | 43319 | 46 | 42
2018-08-07 00:30 | 29 | 29 |  |  | 43319.0208 | 44 | 39
2018-08-07 01:00 | 27 | 27 |  |  | 43319.0417 | 43 | 36
2018-08-07 01:30 | 27 | 26 |  |  | 43319.0625 | 42 | 35
2018-08-07 02:00 | 29 | 28 |  |  | 43319.0833 | 42 | 36
2018-08-07 02:30 | 30 | 30 |  |  | 43319.1042 | 43 | 40
2018-08-07 03:00 | 32 | 31 |  |  | 43319.125 | 44 | 41
2018-08-07 03:30 | 34 | 34 |  |  | 43319.1458 | 46 | 43
2018-08-07 04:00 | 36 | 36 |  |  | 43319.1667 | 48 | 44
2018-08-07 04:30 | 36 | 36 |  |  | 43319.1875 | 48 | 45
2018-08-07 05:00 | 39 | 39 |  |  | 43319.2083 | 51 | 48
2018-08-07 05:30 | 39 | 39 |  |  | 43319.2292 | 50 | 48
2018-08-07 06:00 | 41 | 41 |  |  | 43319.25 | 53 | 52
2018-08-07 06:30 | 46 | 45 |  |  | 43319.2708 | 62 | 59
2018-08-07 07:00 | 47 | 47 |  |  | 43319.2917 | 70 | 65
2018-08-07 07:30 | 48 | 48 |  |  | 43319.3125 | 74 | 71
2018-08-07 08:00 | 49 | 49 |  |  | 43319.3333 | 79 | 75
2018-08-07 08:30 | 47 | 47 |  |  | 43319.3542 | 77 | 74
2018-08-07 09:00 | 44 | 44 |  |  | 43319.375 | 74 | 70
2018-08-07 09:30 | 46 | 46 |  |  | 43319.3958 | 69 | 65
2018-08-07 10:00 | 48 | 48 |  |  | 43319.4167 | 70 | 67
2018-08-07 10:30 | 45 | 45 |  |  | 43319.4375 | 62 | 58
2018-08-07 11:00 | 48 | 48 |  |  | 43319.4583 | 66 | 63
2018-08-07 11:30 | 48 | 48 |  |  | 43319.4792 | 70 | 67
2018-08-07 12:00 | 49 | 49 |  |  | 43319.5 | 66 | 63
2018-08-07 12:30 | 46 | 46 |  |  | 43319.5208 | 65 | 62
2018-08-07 13:00 | 52 | 52 |  |  | 43319.5417 | 71 | 68
2018-08-07 13:30 | 53 | 53 |  |  | 43319.5625 | 75 | 72
2018-08-07 14:00 | 54 | 53 |  |  | 43319.5833 | 75 | 72
2018-08-07 14:30 | 53 | 53 |  |  | 43319.6042 | 79 | 76
2018-08-07 15:00 | 53 | 53 |  |  | 43319.625 | 77 | 73
2018-08-07 15:30 | 54 | 54 |  |  | 43319.6458 | 75 | 72
2018-08-07 16:00 | 53 | 53 |  |  | 43319.6667 | 75 | 71
2018-08-07 16:30 | 50 | 50 |  |  | 43319.6875 | 74 | 69
2018-08-07 17:00 | 49 | 48 |  |  | 43319.7083 | 72 | 67
2018-08-07 17:30 | 49 | 48 |  |  | 43319.7292 | 72 | 67
2018-08-07 18:00 | 50 | 49 |  |  | 43319.75 | 74 | 69
2018-08-07 18:30 | 49 | 49 |  |  | 43319.7708 | 74 | 68
2018-08-07 19:00 | 51 | 50 |  |  | 43319.7917 | 75 | 68
2018-08-07 19:30 | 50 | 49 |  |  | 43319.8125 | 74 | 67
2018-08-07 20:00 | 48 | 47 |  |  | 43319.8333 | 71 | 65
2018-08-07 20:30 | 47 | 47 |  |  | 43319.8542 | 71 | 65
2018-08-07 21:00 | 47 | 46 |  |  | 43319.875 | 68 | 61
2018-08-07 21:30 | 43 | 42 |  |  | 43319.8958 | 66 | 58
2018-08-07 22:00 | 42 | 41 |  |  | 43319.9167 | 65 | 57
2018-08-07 22:30 | 41 | 40 |  |  | 43319.9375 | 61 | 54
2018-08-07 23:00 | 38 | 37 |  |  | 43319.9583 | 58 | 51
2018-08-07 23:30 | 31 | 31 |  |  | 43319.9792 | 48 | 44
2018-08-08 | 28 | 28 |  |  | 43320 | 44 | 42
2018-08-08 00:30 | 28 | 28 |  |  | 43320.0208 | 42 | 40
2018-08-08 01:00 | 27 | 27 |  |  | 43320.0417 | 41 | 38
2018-08-08 01:30 | 28 | 28 |  |  | 43320.0625 | 42 | 39
2018-08-08 02:00 | 28 | 28 |  |  | 43320.0833 | 43 | 40
2018-08-08 02:30 | 31 | 31 |  |  | 43320.1042 | 44 | 40
2018-08-08 03:00 | 32 | 32 |  |  | 43320.125 | 44 | 41
2018-08-08 03:30 | 32 | 32 |  |  | 43320.1458 | 45 | 41
2018-08-08 04:00 | 32 | 32 |  |  | 43320.1667 | 44 | 40
2018-08-08 04:30 | 32 | 32 |  |  | 43320.1875 | 46 | 42
2018-08-08 05:00 | 35 | 35 |  |  | 43320.2083 | 46 | 43
2018-08-08 05:30 | 37 | 37 |  |  | 43320.2292 | 50 | 48
2018-08-08 06:00 | 40 | 40 |  |  | 43320.25 | 55 | 53
2018-08-08 06:30 | 45 | 44 |  |  | 43320.2708 | 65 | 62
2018-08-08 07:00 | 52 | 50 |  |  | 43320.2917 | 74 | 73
2018-08-08 07:30 | 51 | 50 |  |  | 43320.3125 | 79 | 77
2018-08-08 08:00 | 48 | 48 |  |  | 43320.3333 | 78 | 75
2018-08-08 08:30 | 43 | 41 |  |  | 43320.3542 | 73 | 70
2018-08-08 09:00 | 39 | 37 |  |  | 43320.375 | 66 | 64
2018-08-08 09:30 | 37 | 35 |  |  | 43320.3958 | 59 | 58
2018-08-08 10:00 | 37 | 34 |  |  | 43320.4167 | 55 | 55
2018-08-08 10:30 | 40 | 34 |  |  | 43320.4375 | 56 | 56
2018-08-08 11:00 | 41 | 36 |  |  | 43320.4583 | 58 | 57
2018-08-08 11:30 | 42 | 37 |  |  | 43320.4792 | 58 | 57
2018-08-08 12:00 | 36 | 35 |  |  | 43320.5 | 55 | 55
2018-08-08 12:30 | 37 | 36 |  |  | 43320.5208 | 57 | 57
2018-08-08 13:00 | 38 | 37 |  |  | 43320.5417 | 58 | 58
2018-08-08 13:30 | 40 | 39 |  |  | 43320.5625 | 60 | 60
2018-08-08 14:00 | 43 | 42 |  |  | 43320.5833 | 62 | 62
2018-08-08 14:30 | 43 | 43 |  |  | 43320.6042 | 62 | 62
2018-08-08 15:00 | 43 | 42 |  |  | 43320.625 | 63 | 62
2018-08-08 15:30 | 43 | 43 |  |  | 43320.6458 | 64 | 63
2018-08-08 16:00 | 43 | 43 |  |  | 43320.6667 | 65 | 63
2018-08-08 16:30 | 42 | 42 |  |  | 43320.6875 | 68 | 62
2018-08-08 17:00 | 43 | 42 |  |  | 43320.7083 | 69 | 62
2018-08-08 17:30 | 46 | 45 |  |  | 43320.7292 | 72 | 65
2018-08-08 18:00 | 48 | 46 |  |  | 43320.75 | 75 | 67
2018-08-08 18:30 | 47 | 44 |  |  | 43320.7708 | 77 | 65
2018-08-08 19:00 | 49 | 46 |  |  | 43320.7917 | 79 | 66
2018-08-08 19:30 | 48 | 47 |  |  | 43320.8125 | 74 | 67
2018-08-08 20:00 | 47 | 47 |  |  | 43320.8333 | 69 | 67
2018-08-08 20:30 | 47 | 47 |  |  | 43320.8542 | 69 | 67
2018-08-08 21:00 | 44 | 44 |  |  | 43320.875 | 65 | 63
2018-08-08 21:30 | 43 | 43 |  |  | 43320.8958 | 61 | 59
2018-08-08 22:00 | 41 | 41 |  |  | 43320.9167 | 60 | 58
2018-08-08 22:30 | 40 | 40 |  |  | 43320.9375 | 58 | 56
2018-08-08 23:00 | 39 | 38 |  |  | 43320.9583 | 55 | 52
2018-08-08 23:30 | 33 | 33 |  |  | 43320.9792 | 51 | 47
2018-08-09 | 29 | 29 |  |  | 43321 | 47 | 43
2018-08-09 00:30 | 28 | 27 |  |  | 43321.0208 | 44 | 40
2018-08-09 01:00 | 26 | 25 |  |  | 43321.0417 | 41 | 37
2018-08-09 01:30 | 25 | 25 |  |  | 43321.0625 | 39 | 35
2018-08-09 02:00 | 27 | 26 |  |  | 43321.0833 | 39 | 36
2018-08-09 02:30 | 28 | 28 |  |  | 43321.1042 | 40 | 37
2018-08-09 03:00 | 28 | 28 |  |  | 43321.125 | 39 | 36
2018-08-09 03:30 | 28 | 28 |  |  | 43321.1458 | 40 | 37
2018-08-09 04:00 | 29 | 29 |  |  | 43321.1667 | 41 | 38
2018-08-09 04:30 | 31 | 31 |  |  | 43321.1875 | 42 | 40
2018-08-09 05:00 | 35 | 35 |  |  | 43321.2083 | 46 | 44
2018-08-09 05:30 | 39 | 39 |  |  | 43321.2292 | 51 | 50
2018-08-09 06:00 | 42 | 42 |  |  | 43321.25 | 57 | 56
2018-08-09 06:30 | 45 | 45 |  |  | 43321.2708 | 67 | 65
2018-08-09 07:00 | 53 | 52 |  |  | 43321.2917 | 77 | 76
2018-08-09 07:30 | 53 | 51 |  |  | 43321.3125 | 79 | 79
2018-08-09 08:00 | 49 | 47 |  |  | 43321.3333 | 75 | 75
2018-08-09 08:30 | 45 | 44 |  |  | 43321.3542 | 72 | 72
2018-08-09 09:00 | 41 | 40 |  |  | 43321.375 | 65 | 65
2018-08-09 09:30 | 37 | 37 |  |  | 43321.3958 | 59 | 59
2018-08-09 10:00 | 35 | 35 |  |  | 43321.4167 | 56 | 56
2018-08-09 10:30 | 34 | 33 |  |  | 43321.4375 | 56 | 54
2018-08-09 11:00 | 33 | 33 |  |  | 43321.4583 | 55 | 53
2018-08-09 11:30 | 36 | 36 |  |  | 43321.4792 | 57 | 54
2018-08-09 12:00 | 35 | 35 |  |  | 43321.5 | 56 | 53
2018-08-09 12:30 | 35 | 35 |  |  | 43321.5208 | 57 | 54
2018-08-09 13:00 | 37 | 37 |  |  | 43321.5417 | 58 | 56
2018-08-09 13:30 | 38 | 37 |  |  | 43321.5625 | 58 | 56
2018-08-09 14:00 | 40 | 39 |  |  | 43321.5833 | 60 | 58
2018-08-09 14:30 | 41 | 41 |  |  | 43321.6042 | 60 | 58
2018-08-09 15:00 | 40 | 40 |  |  | 43321.625 | 60 | 59
2018-08-09 15:30 | 42 | 42 |  |  | 43321.6458 | 62 | 61
2018-08-09 16:00 | 45 | 45 |  |  | 43321.6667 | 65 | 64
2018-08-09 16:30 | 44 | 44 |  |  | 43321.6875 | 65 | 65
2018-08-09 17:00 | 44 | 44 |  |  | 43321.7083 | 64 | 64
2018-08-09 17:30 | 46 | 45 |  |  | 43321.7292 | 66 | 66
2018-08-09 18:00 | 50 | 50 |  |  | 43321.75 | 70 | 70
2018-08-09 18:30 | 51 | 50 |  |  | 43321.7708 | 70 | 69
2018-08-09 19:00 | 52 | 52 |  |  | 43321.7917 | 71 | 71
2018-08-09 19:30 | 52 | 51 |  |  | 43321.8125 | 70 | 70
2018-08-09 20:00 | 51 | 50 |  |  | 43321.8333 | 68 | 67
2018-08-09 20:30 | 51 | 50 |  |  | 43321.8542 | 67 | 66
2018-08-09 21:00 | 46 | 45 |  |  | 43321.875 | 62 | 62
2018-08-09 21:30 | 44 | 43 |  |  | 43321.8958 | 58 | 58
2018-08-09 22:00 | 43 | 42 |  |  | 43321.9167 | 58 | 58
2018-08-09 22:30 | 39 | 39 |  |  | 43321.9375 | 55 | 55
2018-08-09 23:00 | 38 | 37 |  |  | 43321.9583 | 52 | 52
2018-08-09 23:30 | 35 | 35 |  |  | 43321.9792 | 49 | 49
2018-08-10 | 31 | 30 |  |  | 43322 | 44 | 44
2018-08-10 00:30 | 31 | 30 |  |  | 43322.0208 | 42 | 42
2018-08-10 01:00 | 33 | 30 |  |  | 43322.0417 | 42 | 42
2018-08-10 01:30 | 31 | 28 |  |  | 43322.0625 | 40 | 40
2018-08-10 02:00 | 31 | 28 |  |  | 43322.0833 | 40 | 40
2018-08-10 02:30 | 31 | 28 |  |  | 43322.1042 | 39 | 39
2018-08-10 03:00 | 30 | 27 |  |  | 43322.125 | 37 | 37
2018-08-10 03:30 | 31 | 28 |  |  | 43322.1458 | 39 | 38
2018-08-10 04:00 | 31 | 28 |  |  | 43322.1667 | 38 | 38
2018-08-10 04:30 | 32 | 30 |  |  | 43322.1875 | 40 | 40
2018-08-10 05:00 | 35 | 33 |  |  | 43322.2083 | 43 | 43
2018-08-10 05:30 | 35 | 34 |  |  | 43322.2292 | 45 | 45
2018-08-10 06:00 | 39 | 38 |  |  | 43322.25 | 51 | 51
2018-08-10 06:30 | 43 | 43 |  |  | 43322.2708 | 60 | 59
2018-08-10 07:00 | 43 | 42 |  |  | 43322.2917 | 64 | 63
2018-08-10 07:30 | 45 | 45 |  |  | 43322.3125 | 71 | 70
2018-08-10 08:00 | 46 | 46 |  |  | 43322.3333 | 72 | 71
2018-08-10 08:30 | 43 | 43 |  |  | 43322.3542 | 68 | 67
2018-08-10 09:00 | 40 | 40 |  |  | 43322.375 | 64 | 62
2018-08-10 09:30 | 38 | 38 |  |  | 43322.3958 | 59 | 57
2018-08-10 10:00 | 36 | 36 |  |  | 43322.4167 | 58 | 56
2018-08-10 10:30 | 37 | 37 |  |  | 43322.4375 | 59 | 57
2018-08-10 11:00 | 39 | 39 |  |  | 43322.4583 | 62 | 60
2018-08-10 11:30 | 41 | 40 |  |  | 43322.4792 | 63 | 61
2018-08-10 12:00 | 43 | 43 |  |  | 43322.5 | 63 | 61
2018-08-10 12:30 | 43 | 43 |  |  | 43322.5208 | 62 | 60
2018-08-10 13:00 | 42 | 42 |  |  | 43322.5417 | 61 | 59
2018-08-10 13:30 | 41 | 41 |  |  | 43322.5625 | 61 | 59
2018-08-10 14:00 | 41 | 41 |  |  | 43322.5833 | 61 | 59
2018-08-10 14:30 | 41 | 41 |  |  | 43322.6042 | 62 | 61
2018-08-10 15:00 | 41 | 41 |  |  | 43322.625 | 63 | 61
2018-08-10 15:30 | 43 | 43 |  |  | 43322.6458 | 65 | 64
2018-08-10 16:00 | 45 | 45 |  |  | 43322.6667 | 67 | 66
2018-08-10 16:30 | 45 | 45 |  |  | 43322.6875 | 67 | 66
2018-08-10 17:00 | 46 | 46 |  |  | 43322.7083 | 68 | 68
2018-08-10 17:30 | 46 | 46 |  |  | 43322.7292 | 68 | 68
2018-08-10 18:00 | 47 | 47 |  |  | 43322.75 | 68 | 68
2018-08-10 18:30 | 48 | 47 |  |  | 43322.7708 | 67 | 67
2018-08-10 19:00 | 49 | 48 |  |  | 43322.7917 | 68 | 68
2018-08-10 19:30 | 49 | 48 |  |  | 43322.8125 | 67 | 66
2018-08-10 20:00 | 47 | 46 |  |  | 43322.8333 | 65 | 65
2018-08-10 20:30 | 45 | 45 |  |  | 43322.8542 | 64 | 64
2018-08-10 21:00 | 45 | 44 |  |  | 43322.875 | 61 | 61
2018-08-10 21:30 | 42 | 41 |  |  | 43322.8958 | 58 | 58
2018-08-10 22:00 | 41 | 40 |  |  | 43322.9167 | 58 | 58
2018-08-10 22:30 | 42 | 41 |  |  | 43322.9375 | 57 | 57
2018-08-10 23:00 | 39 | 38 |  |  | 43322.9583 | 54 | 54
2018-08-10 23:30 | 34 | 33 |  |  | 43322.9792 | 50 | 49
2018-08-11 | 31 | 30 |  |  | 43323 | 45 | 45
2018-08-11 00:30 | 30 | 28 |  |  | 43323.0208 | 42 | 42
2018-08-11 01:00 | 32 | 29 |  |  | 43323.0417 | 42 | 42
2018-08-11 01:30 | 32 | 29 |  |  | 43323.0625 | 42 | 41
2018-08-11 02:00 | 32 | 30 |  |  | 43323.0833 | 42 | 42
2018-08-11 02:30 | 32 | 29 |  |  | 43323.1042 | 41 | 41
2018-08-11 03:00 | 32 | 29 |  |  | 43323.125 | 42 | 41
2018-08-11 03:30 | 32 | 29 |  |  | 43323.1458 | 41 | 41
2018-08-11 04:00 | 34 | 31 |  |  | 43323.1667 | 42 | 42
2018-08-11 04:30 | 33 | 30 |  |  | 43323.1875 | 42 | 42
2018-08-11 05:00 | 34 | 31 |  |  | 43323.2083 | 43 | 42
2018-08-11 05:30 | 36 | 33 |  |  | 43323.2292 | 44 | 44
2018-08-11 06:00 | 35 | 33 |  |  | 43323.25 | 45 | 44
2018-08-11 06:30 | 36 | 33 |  |  | 43323.2708 | 47 | 46
2018-08-11 07:00 | 35 | 33 |  |  | 43323.2917 | 51 | 51
2018-08-11 07:30 | 34 | 32 |  |  | 43323.3125 | 52 | 52
2018-08-11 08:00 | 32 | 29 |  |  | 43323.3333 | 52 | 52
2018-08-11 08:30 | 33 | 30 |  |  | 43323.3542 | 54 | 54
2018-08-11 09:00 | 33 | 30 |  |  | 43323.375 | 54 | 53
2018-08-11 09:30 | 31 | 28 |  |  | 43323.3958 | 51 | 50
2018-08-11 10:00 | 28 | 25 |  |  | 43323.4167 | 46 | 46
2018-08-11 10:30 | 28 | 24 |  |  | 43323.4375 | 45 | 44
2018-08-11 11:00 | 28 | 25 |  |  | 43323.4583 | 45 | 45
2018-08-11 11:30 | 25 | 21 |  |  | 43323.4792 | 41 | 41
2018-08-11 12:00 | 26 | 22 |  |  | 43323.5 | 44 | 44
2018-08-11 12:30 | 29 | 26 |  |  | 43323.5208 | 49 | 49
2018-08-11 13:00 | 29 | 27 |  |  | 43323.5417 | 45 | 44
2018-08-11 13:30 | 31 | 28 |  |  | 43323.5625 | 46 | 46
2018-08-11 14:00 | 32 | 30 |  |  | 43323.5833 | 46 | 46
2018-08-11 14:30 | 33 | 30 |  |  | 43323.6042 | 47 | 46
2018-08-11 15:00 | 32 | 29 |  |  | 43323.625 | 45 | 45
2018-08-11 15:30 | 33 | 31 |  |  | 43323.6458 | 47 | 46
2018-08-11 16:00 | 34 | 32 |  |  | 43323.6667 | 48 | 48
2018-08-11 16:30 | 35 | 33 |  |  | 43323.6875 | 50 | 50
2018-08-11 17:00 | 37 | 35 |  |  | 43323.7083 | 54 | 53
2018-08-11 17:30 | 40 | 36 |  |  | 43323.7292 | 56 | 55
2018-08-11 18:00 | 44 | 40 |  |  | 43323.75 | 60 | 59
2018-08-11 18:30 | 46 | 40 |  |  | 43323.7708 | 63 | 60
2018-08-11 19:00 | 47 | 42 |  |  | 43323.7917 | 63 | 61
2018-08-11 19:30 | 46 | 41 |  |  | 43323.8125 | 62 | 60
2018-08-11 20:00 | 45 | 41 |  |  | 43323.8333 | 60 | 59
2018-08-11 20:30 | 44 | 40 |  |  | 43323.8542 | 60 | 60
2018-08-11 21:00 | 41 | 38 |  |  | 43323.875 | 56 | 56
2018-08-11 21:30 | 39 | 36 |  |  | 43323.8958 | 53 | 53
2018-08-11 22:00 | 38 | 35 |  |  | 43323.9167 | 53 | 52
2018-08-11 22:30 | 39 | 36 |  |  | 43323.9375 | 55 | 54
2018-08-11 23:00 | 38 | 35 |  |  | 43323.9583 | 52 | 51
2018-08-11 23:30 | 36 | 32 |  |  | 43323.9792 | 48 | 48
2018-08-12 | 34 | 29 |  |  | 43324 | 46 | 44
2018-08-12 00:30 | 35 | 31 |  |  | 43324.0208 | 47 | 45
2018-08-12 01:00 | 34 | 29 |  |  | 43324.0417 | 44 | 42
2018-08-12 01:30 | 32 | 26 |  |  | 43324.0625 | 41 | 38
2018-08-12 02:00 | 31 | 24 |  |  | 43324.0833 | 39 | 36
2018-08-12 02:30 | 27 | 23 |  |  | 43324.1042 | 39 | 36
2018-08-12 03:00 | 23 | 23 |  |  | 43324.125 | 41 | 35
2018-08-12 03:30 | 25 | 25 |  |  | 43324.1458 | 43 | 37
2018-08-12 04:00 | 26 | 26 |  |  | 43324.1667 | 44 | 38
2018-08-12 04:30 | 26 | 26 |  |  | 43324.1875 | 44 | 38
2018-08-12 05:00 | 28 | 27 |  |  | 43324.2083 | 43 | 38
2018-08-12 05:30 | 28 | 28 |  |  | 43324.2292 | 45 | 40
2018-08-12 06:00 | 27 | 26 |  |  | 43324.25 | 45 | 39
2018-08-12 06:30 | 28 | 27 |  |  | 43324.2708 | 47 | 42
2018-08-12 07:00 | 28 | 27 |  |  | 43324.2917 | 47 | 42
2018-08-12 07:30 | 27 | 27 |  |  | 43324.3125 | 48 | 43
2018-08-12 08:00 | 25 | 25 |  |  | 43324.3333 | 47 | 42
2018-08-12 08:30 | 25 | 24 |  |  | 43324.3542 | 45 | 41
2018-08-12 09:00 | 23 | 23 |  |  | 43324.375 | 44 | 41
2018-08-12 09:30 | 23 | 23 |  |  | 43324.3958 | 44 | 41
2018-08-12 10:00 | 23 | 23 |  |  | 43324.4167 | 43 | 40
2018-08-12 10:30 | 22 | 21 |  |  | 43324.4375 | 41 | 38
2018-08-12 11:00 | 22 | 21 |  |  | 43324.4583 | 40 | 37
2018-08-12 11:30 | 20 | 20 |  |  | 43324.4792 | 38 | 35
2018-08-12 12:00 | 21 | 21 |  |  | 43324.5 | 38 | 35
2018-08-12 12:30 | 20 | 20 |  |  | 43324.5208 | 38 | 35
2018-08-12 13:00 | 21 | 20 |  |  | 43324.5417 | 38 | 34
2018-08-12 13:30 | 20 | 20 |  |  | 43324.5625 | 38 | 35
2018-08-12 14:00 | 22 | 22 |  |  | 43324.5833 | 39 | 36
2018-08-12 14:30 | 24 | 24 |  |  | 43324.6042 | 42 | 39
2018-08-12 15:00 | 29 | 29 |  |  | 43324.625 | 47 | 44
2018-08-12 15:30 | 33 | 33 |  |  | 43324.6458 | 51 | 48
2018-08-12 16:00 | 38 | 38 |  |  | 43324.6667 | 57 | 54
2018-08-12 16:30 | 41 | 41 |  |  | 43324.6875 | 61 | 58
2018-08-12 17:00 | 40 | 40 |  |  | 43324.7083 | 59 | 57
2018-08-12 17:30 | 40 | 40 |  |  | 43324.7292 | 61 | 58
2018-08-12 18:00 | 41 | 41 |  |  | 43324.75 | 65 | 60
2018-08-12 18:30 | 45 | 43 |  |  | 43324.7708 | 73 | 63
2018-08-12 19:00 | 49 | 44 |  |  | 43324.7917 | 81 | 65
2018-08-12 19:30 | 49 | 44 |  |  | 43324.8125 | 80 | 65
2018-08-12 20:00 | 47 | 44 |  |  | 43324.8333 | 77 | 66
2018-08-12 20:30 | 48 | 44 |  |  | 43324.8542 | 77 | 66
2018-08-12 21:00 | 43 | 42 |  |  | 43324.875 | 69 | 62
2018-08-12 21:30 | 41 | 41 |  |  | 43324.8958 | 62 | 60
2018-08-12 22:00 | 41 | 41 |  |  | 43324.9167 | 62 | 60
2018-08-12 22:30 | 39 | 39 |  |  | 43324.9375 | 61 | 59
2018-08-12 23:00 | 39 | 39 |  |  | 43324.9583 | 59 | 57
2018-08-12 23:30 | 36 | 36 |  |  | 43324.9792 | 55 | 52
2018-08-13 | 32 | 32 |  |  | 43325 | 52 | 49
2018-08-13 00:30 | 31 | 31 |  |  | 43325.0208 | 49 | 46
2018-08-13 01:00 | 30 | 30 |  |  | 43325.0417 | 49 | 44
2018-08-13 01:30 | 29 | 28 |  |  | 43325.0625 | 47 | 43
2018-08-13 02:00 | 27 | 27 |  |  | 43325.0833 | 45 | 41
2018-08-13 02:30 | 28 | 27 |  |  | 43325.1042 | 46 | 41
2018-08-13 03:00 | 28 | 27 |  |  | 43325.125 | 47 | 42
2018-08-13 03:30 | 29 | 29 |  |  | 43325.1458 | 48 | 45
2018-08-13 04:00 | 30 | 30 |  |  | 43325.1667 | 47 | 44
2018-08-13 04:30 | 30 | 29 |  |  | 43325.1875 | 46 | 43
2018-08-13 05:00 | 29 | 29 |  |  | 43325.2083 | 45 | 42
2018-08-13 05:30 | 32 | 32 |  |  | 43325.2292 | 47 | 45
2018-08-13 06:00 | 36 | 36 |  |  | 43325.25 | 51 | 50
2018-08-13 06:30 | 42 | 42 |  |  | 43325.2708 | 61 | 60
2018-08-13 07:00 | 47 | 45 |  |  | 43325.2917 | 69 | 69
2018-08-13 07:30 | 48 | 46 |  |  | 43325.3125 | 73 | 73
2018-08-13 08:00 | 43 | 41 |  |  | 43325.3333 | 65 | 65
2018-08-13 08:30 | 38 | 35 |  |  | 43325.3542 | 58 | 58
2018-08-13 09:00 | 32 | 31 |  |  | 43325.375 | 52 | 51
2018-08-13 09:30 | 27 | 27 |  |  | 43325.3958 | 46 | 45
2018-08-13 10:00 | 26 | 26 |  |  | 43325.4167 | 43 | 42
2018-08-13 10:30 | 26 | 26 |  |  | 43325.4375 | 43 | 42
2018-08-13 11:00 | 27 | 27 |  |  | 43325.4583 | 42 | 42
2018-08-13 11:30 | 28 | 28 |  |  | 43325.4792 | 44 | 43
2018-08-13 12:00 | 30 | 30 |  |  | 43325.5 | 48 | 47
2018-08-13 12:30 | 30 | 29 |  |  | 43325.5208 | 46 | 45
2018-08-13 13:00 | 32 | 31 |  |  | 43325.5417 | 49 | 48
2018-08-13 13:30 | 32 | 31 |  |  | 43325.5625 | 48 | 47
2018-08-13 14:00 | 34 | 34 |  |  | 43325.5833 | 51 | 50
2018-08-13 14:30 | 34 | 34 |  |  | 43325.6042 | 50 | 50
2018-08-13 15:00 | 35 | 34 |  |  | 43325.625 | 52 | 52
2018-08-13 15:30 | 36 | 36 |  |  | 43325.6458 | 54 | 53
2018-08-13 16:00 | 38 | 38 |  |  | 43325.6667 | 57 | 56
2018-08-13 16:30 | 36 | 36 |  |  | 43325.6875 | 55 | 52
2018-08-13 17:00 | 37 | 37 |  |  | 43325.7083 | 56 | 53
2018-08-13 17:30 | 42 | 42 |  |  | 43325.7292 | 63 | 61
2018-08-13 18:00 | 45 | 45 |  |  | 43325.75 | 67 | 65
2018-08-13 18:30 | 44 | 44 |  |  | 43325.7708 | 67 | 65
2018-08-13 19:00 | 45 | 45 |  |  | 43325.7917 | 68 | 65
2018-08-13 19:30 | 47 | 47 |  |  | 43325.8125 | 71 | 69
2018-08-13 20:00 | 48 | 48 |  |  | 43325.8333 | 70 | 68
2018-08-13 20:30 | 47 | 47 |  |  | 43325.8542 | 70 | 67
2018-08-13 21:00 | 43 | 43 |  |  | 43325.875 | 65 | 63
2018-08-13 21:30 | 41 | 41 |  |  | 43325.8958 | 61 | 58
2018-08-13 22:00 | 38 | 37 |  |  | 43325.9167 | 57 | 55
2018-08-13 22:30 | 36 | 36 |  |  | 43325.9375 | 56 | 54
2018-08-13 23:00 | 36 | 36 |  |  | 43325.9583 | 55 | 51
2018-08-13 23:30 | 31 | 31 |  |  | 43325.9792 | 50 | 46
2018-08-14 | 26 | 25 |  |  | 43326 | 43 | 38
2018-08-14 00:30 | 24 | 24 |  |  | 43326.0208 | 40 | 37
2018-08-14 01:00 | 23 | 23 |  |  | 43326.0417 | 37 | 33
2018-08-14 01:30 | 22 | 21 |  |  | 43326.0625 | 36 | 31
2018-08-14 02:00 | 22 | 21 |  |  | 43326.0833 | 36 | 31
2018-08-14 02:30 | 23 | 23 |  |  | 43326.1042 | 36 | 33
2018-08-14 03:00 | 25 | 25 |  |  | 43326.125 | 38 | 35
2018-08-14 03:30 | 27 | 27 |  |  | 43326.1458 | 40 | 37
2018-08-14 04:00 | 30 | 30 |  |  | 43326.1667 | 45 | 41
2018-08-14 04:30 | 32 | 32 |  |  | 43326.1875 | 48 | 44
2018-08-14 05:00 | 34 | 34 |  |  | 43326.2083 | 51 | 47
2018-08-14 05:30 | 38 | 38 |  |  | 43326.2292 | 54 | 52
2018-08-14 06:00 | 42 | 42 |  |  | 43326.25 | 60 | 56
2018-08-14 06:30 | 43 | 43 |  |  | 43326.2708 | 67 | 62
2018-08-14 07:00 | 51 | 48 |  |  | 43326.2917 | 74 | 72
2018-08-14 07:30 | 51 | 51 |  |  | 43326.3125 | 79 | 79
2018-08-14 08:00 | 49 | 49 |  |  | 43326.3333 | 76 | 76
2018-08-14 08:30 | 45 | 45 |  |  | 43326.3542 | 71 | 71
2018-08-14 09:00 | 40 | 40 |  |  | 43326.375 | 64 | 63
2018-08-14 09:30 | 38 | 38 |  |  | 43326.3958 | 60 | 60
2018-08-14 10:00 | 34 | 34 |  |  | 43326.4167 | 53 | 53
2018-08-14 10:30 | 34 | 34 |  |  | 43326.4375 | 52 | 51
2018-08-14 11:00 | 38 | 38 |  |  | 43326.4583 | 59 | 58
2018-08-14 11:30 | 41 | 41 |  |  | 43326.4792 | 63 | 62
2018-08-14 12:00 | 41 | 41 |  |  | 43326.5 | 64 | 63
2018-08-14 12:30 | 41 | 41 |  |  | 43326.5208 | 63 | 63
2018-08-14 13:00 | 40 | 40 |  |  | 43326.5417 | 62 | 61
2018-08-14 13:30 | 42 | 42 |  |  | 43326.5625 | 64 | 64
2018-08-14 14:00 | 42 | 42 |  |  | 43326.5833 | 63 | 63
2018-08-14 14:30 | 43 | 43 |  |  | 43326.6042 | 64 | 64
2018-08-14 15:00 | 44 | 44 |  |  | 43326.625 | 67 | 66
2018-08-14 15:30 | 45 | 45 |  |  | 43326.6458 | 67 | 67
2018-08-14 16:00 | 45 | 44 |  |  | 43326.6667 | 65 | 65
2018-08-14 16:30 | 43 | 43 |  |  | 43326.6875 | 63 | 63
2018-08-14 17:00 | 43 | 41 |  |  | 43326.7083 | 60 | 59
2018-08-14 17:30 | 46 | 44 |  |  | 43326.7292 | 66 | 64
2018-08-14 18:00 | 49 | 47 |  |  | 43326.75 | 71 | 69
2018-08-14 18:30 | 49 | 48 |  |  | 43326.7708 | 72 | 70
2018-08-14 19:00 | 51 | 50 |  |  | 43326.7917 | 74 | 72
2018-08-14 19:30 | 49 | 48 |  |  | 43326.8125 | 75 | 70
2018-08-14 20:00 | 49 | 49 |  |  | 43326.8333 | 72 | 68
2018-08-14 20:30 | 46 | 46 |  |  | 43326.8542 | 70 | 65
2018-08-14 21:00 | 43 | 43 |  |  | 43326.875 | 66 | 61
2018-08-14 21:30 | 41 | 41 |  |  | 43326.8958 | 63 | 57
2018-08-14 22:00 | 40 | 40 |  |  | 43326.9167 | 62 | 55
2018-08-14 22:30 | 38 | 38 |  |  | 43326.9375 | 61 | 54
2018-08-14 23:00 | 37 | 37 |  |  | 43326.9583 | 55 | 51
2018-08-14 23:30 | 33 | 33 |  |  | 43326.9792 | 49 | 44
2018-08-15 | 27 | 27 |  |  | 43327 | 42 | 37
2018-08-15 00:30 | 26 | 25 |  |  | 43327.0208 | 42 | 36
2018-08-15 01:00 | 27 | 27 |  |  | 43327.0417 | 42 | 36
2018-08-15 01:30 | 26 | 26 |  |  | 43327.0625 | 42 | 35
2018-08-15 02:00 | 28 | 27 |  |  | 43327.0833 | 43 | 38
2018-08-15 02:30 | 27 | 26 |  |  | 43327.1042 | 42 | 37
2018-08-15 03:00 | 27 | 26 |  |  | 43327.125 | 42 | 37
2018-08-15 03:30 | 27 | 27 |  |  | 43327.1458 | 43 | 38
2018-08-15 04:00 | 27 | 27 |  |  | 43327.1667 | 43 | 38
2018-08-15 04:30 | 29 | 29 |  |  | 43327.1875 | 45 | 40
2018-08-15 05:00 | 30 | 30 |  |  | 43327.2083 | 46 | 41
2018-08-15 05:30 | 30 | 29 |  |  | 43327.2292 | 45 | 40
2018-08-15 06:00 | 29 | 29 |  |  | 43327.25 | 44 | 40
2018-08-15 06:30 | 29 | 29 |  |  | 43327.2708 | 45 | 41
2018-08-15 07:00 | 28 | 27 |  |  | 43327.2917 | 48 | 43
2018-08-15 07:30 | 27 | 26 |  |  | 43327.3125 | 49 | 44
2018-08-15 08:00 | 25 | 25 |  |  | 43327.3333 | 48 | 42
2018-08-15 08:30 | 26 | 26 |  |  | 43327.3542 | 46 | 40
2018-08-15 09:00 | 27 | 27 |  |  | 43327.375 | 45 | 40
2018-08-15 09:30 | 24 | 24 |  |  | 43327.3958 | 42 | 37
2018-08-15 10:00 | 22 | 22 |  |  | 43327.4167 | 37 | 34
2018-08-15 10:30 | 24 | 24 |  |  | 43327.4375 | 38 | 36
2018-08-15 11:00 | 27 | 26 |  |  | 43327.4583 | 40 | 39
2018-08-15 11:30 | 27 | 27 |  |  | 43327.4792 | 41 | 39
2018-08-15 12:00 | 32 | 31 |  |  | 43327.5 | 46 | 45
2018-08-15 12:30 | 31 | 30 |  |  | 43327.5208 | 45 | 44
2018-08-15 13:00 | 29 | 28 |  |  | 43327.5417 | 42 | 41
2018-08-15 13:30 | 30 | 29 |  |  | 43327.5625 | 44 | 43
2018-08-15 14:00 | 32 | 32 |  |  | 43327.5833 | 47 | 45
2018-08-15 14:30 | 33 | 33 |  |  | 43327.6042 | 48 | 47
2018-08-15 15:00 | 35 | 34 |  |  | 43327.625 | 51 | 49
2018-08-15 15:30 | 35 | 34 |  |  | 43327.6458 | 51 | 49
2018-08-15 16:00 | 36 | 36 |  |  | 43327.6667 | 54 | 51
2018-08-15 16:30 | 39 | 39 |  |  | 43327.6875 | 58 | 55
2018-08-15 17:00 | 39 | 39 |  |  | 43327.7083 | 57 | 53
2018-08-15 17:30 | 41 | 41 |  |  | 43327.7292 | 61 | 56
2018-08-15 18:00 | 43 | 43 |  |  | 43327.75 | 65 | 59
2018-08-15 18:30 | 44 | 44 |  |  | 43327.7708 | 66 | 60
2018-08-15 19:00 | 45 | 44 |  |  | 43327.7917 | 68 | 62
2018-08-15 19:30 | 43 | 43 |  |  | 43327.8125 | 65 | 60
2018-08-15 20:00 | 43 | 43 |  |  | 43327.8333 | 64 | 60
2018-08-15 20:30 | 43 | 43 |  |  | 43327.8542 | 61 | 58
2018-08-15 21:00 | 43 | 43 |  |  | 43327.875 | 60 | 57
2018-08-15 21:30 | 40 | 40 |  |  | 43327.8958 | 57 | 54
2018-08-15 22:00 | 39 | 39 |  |  | 43327.9167 | 57 | 54
2018-08-15 22:30 | 37 | 37 |  |  | 43327.9375 | 55 | 51
2018-08-15 23:00 | 35 | 35 |  |  | 43327.9583 | 50 | 47
2018-08-15 23:30 | 31 | 31 |  |  | 43327.9792 | 46 | 42
2018-08-16 | 27 | 27 |  |  | 43328 | 41 | 37
2018-08-16 00:30 | 28 | 28 |  |  | 43328.0208 | 44 | 39
2018-08-16 01:00 | 30 | 29 |  |  | 43328.0417 | 45 | 41
2018-08-16 01:30 | 31 | 30 |  |  | 43328.0625 | 48 | 43
2018-08-16 02:00 | 31 | 31 |  |  | 43328.0833 | 48 | 43
2018-08-16 02:30 | 32 | 31 |  |  | 43328.1042 | 50 | 45
2018-08-16 03:00 | 31 | 31 |  |  | 43328.125 | 50 | 45
2018-08-16 03:30 | 32 | 32 |  |  | 43328.1458 | 49 | 46
2018-08-16 04:00 | 32 | 32 |  |  | 43328.1667 | 48 | 45
2018-08-16 04:30 | 34 | 34 |  |  | 43328.1875 | 51 | 49
2018-08-16 05:00 | 37 | 37 |  |  | 43328.2083 | 53 | 50
2018-08-16 05:30 | 39 | 39 |  |  | 43328.2292 | 56 | 53
2018-08-16 06:00 | 40 | 40 |  |  | 43328.25 | 53 | 51
2018-08-16 06:30 | 43 | 42 |  |  | 43328.2708 | 59 | 58
2018-08-16 07:00 | 49 | 48 |  |  | 43328.2917 | 70 | 70
2018-08-16 07:30 | 50 | 47 |  |  | 43328.3125 | 71 | 71
2018-08-16 08:00 | 47 | 44 |  |  | 43328.3333 | 67 | 66
2018-08-16 08:30 | 41 | 38 |  |  | 43328.3542 | 60 | 59
2018-08-16 09:00 | 37 | 33 |  |  | 43328.375 | 53 | 52
2018-08-16 09:30 | 34 | 30 |  |  | 43328.3958 | 47 | 46
2018-08-16 10:00 | 34 | 30 |  |  | 43328.4167 | 46 | 45
2018-08-16 10:30 | 36 | 31 |  |  | 43328.4375 | 47 | 46
2018-08-16 11:00 | 37 | 32 |  |  | 43328.4583 | 50 | 49
2018-08-16 11:30 | 36 | 32 |  |  | 43328.4792 | 49 | 48
2018-08-16 12:00 | 35 | 30 |  |  | 43328.5 | 47 | 46
2018-08-16 12:30 | 36 | 32 |  |  | 43328.5208 | 48 | 48
2018-08-16 13:00 | 37 | 33 |  |  | 43328.5417 | 50 | 50
2018-08-16 13:30 | 38 | 34 |  |  | 43328.5625 | 50 | 50
2018-08-16 14:00 | 39 | 36 |  |  | 43328.5833 | 53 | 53
2018-08-16 14:30 | 40 | 37 |  |  | 43328.6042 | 54 | 54
2018-08-16 15:00 | 41 | 38 |  |  | 43328.625 | 57 | 56
2018-08-16 15:30 | 43 | 40 |  |  | 43328.6458 | 58 | 58
2018-08-16 16:00 | 44 | 42 |  |  | 43328.6667 | 59 | 59
2018-08-16 16:30 | 42 | 40 |  |  | 43328.6875 | 58 | 58
2018-08-16 17:00 | 42 | 40 |  |  | 43328.7083 | 57 | 57
2018-08-16 17:30 | 44 | 43 |  |  | 43328.7292 | 63 | 63
2018-08-16 18:00 | 43 | 42 |  |  | 43328.75 | 62 | 62
2018-08-16 18:30 | 43 | 43 |  |  | 43328.7708 | 62 | 62
2018-08-16 19:00 | 44 | 44 |  |  | 43328.7917 | 63 | 63
2018-08-16 19:30 | 43 | 43 |  |  | 43328.8125 | 61 | 61
2018-08-16 20:00 | 40 | 39 |  |  | 43328.8333 | 58 | 58
2018-08-16 20:30 | 39 | 38 |  |  | 43328.8542 | 56 | 56
2018-08-16 21:00 | 37 | 36 |  |  | 43328.875 | 51 | 51
2018-08-16 21:30 | 34 | 33 |  |  | 43328.8958 | 47 | 47
2018-08-16 22:00 | 32 | 31 |  |  | 43328.9167 | 46 | 46
2018-08-16 22:30 | 31 | 30 |  |  | 43328.9375 | 45 | 44
2018-08-16 23:00 | 32 | 31 |  |  | 43328.9583 | 43 | 43
2018-08-16 23:30 | 29 | 27 |  |  | 43328.9792 | 40 | 40
2018-08-17 | 25 | 23 |  |  | 43329 | 35 | 34
2018-08-17 00:30 | 27 | 23 |  |  | 43329.0208 | 34 | 34
2018-08-17 01:00 | 26 | 22 |  |  | 43329.0417 | 31 | 30
2018-08-17 01:30 | 25 | 21 |  |  | 43329.0625 | 29 | 29
2018-08-17 02:00 | 26 | 22 |  |  | 43329.0833 | 31 | 30
2018-08-17 02:30 | 27 | 23 |  |  | 43329.1042 | 33 | 33
2018-08-17 03:00 | 28 | 24 |  |  | 43329.125 | 33 | 33
2018-08-17 03:30 | 30 | 26 |  |  | 43329.1458 | 37 | 36
2018-08-17 04:00 | 31 | 26 |  |  | 43329.1667 | 37 | 36
2018-08-17 04:30 | 32 | 27 |  |  | 43329.1875 | 40 | 38
2018-08-17 05:00 | 35 | 30 |  |  | 43329.2083 | 41 | 40
2018-08-17 05:30 | 39 | 34 |  |  | 43329.2292 | 46 | 45
2018-08-17 06:00 | 41 | 35 |  |  | 43329.25 | 50 | 48
2018-08-17 06:30 | 45 | 40 |  |  | 43329.2708 | 60 | 57
2018-08-17 07:00 | 48 | 43 |  |  | 43329.2917 | 68 | 65
2018-08-17 07:30 | 46 | 42 |  |  | 43329.3125 | 68 | 66
2018-08-17 08:00 | 52 | 41 |  |  | 43329.3333 | 68 | 64
2018-08-17 08:30 | 47 | 33 |  |  | 43329.3542 | 58 | 53
2018-08-17 09:00 | 38 | 17 |  |  | 43329.375 | 38 | 24
2018-08-17 09:30 | 36 | 17 |  |  | 43329.3958 | 37 | 22
2018-08-17 10:00 | 26 | 16 |  |  | 43329.4167 | 31 | 20
2018-08-17 10:30 | 25 | 17 |  |  | 43329.4375 | 31 | 22
2018-08-17 11:00 | 26 | 18 |  |  | 43329.4583 | 29 | 23
2018-08-17 11:30 | 30 | 23 |  |  | 43329.4792 | 36 | 31
2018-08-17 12:00 | 33 | 28 |  |  | 43329.5 | 43 | 40
2018-08-17 12:30 | 35 | 30 |  |  | 43329.5208 | 46 | 43
2018-08-17 13:00 | 45 | 42 |  |  | 43329.5417 | 67 | 64
2018-08-17 13:30 | 48 | 45 |  |  | 43329.5625 | 71 | 69
2018-08-17 14:00 | 49 | 46 |  |  | 43329.5833 | 72 | 71
2018-08-17 14:30 | 48 | 45 |  |  | 43329.6042 | 70 | 68
2018-08-17 15:00 | 47 | 44 |  |  | 43329.625 | 68 | 66
2018-08-17 15:30 | 48 | 45 |  |  | 43329.6458 | 68 | 66
2018-08-17 16:00 | 49 | 47 |  |  | 43329.6667 | 70 | 69
2018-08-17 16:30 | 46 | 44 |  |  | 43329.6875 | 66 | 66
2018-08-17 17:00 | 46 | 45 |  |  | 43329.7083 | 67 | 67
2018-08-17 17:30 | 43 | 43 |  |  | 43329.7292 | 66 | 65
2018-08-17 18:00 | 41 | 41 |  |  | 43329.75 | 64 | 64
2018-08-17 18:30 | 40 | 40 |  |  | 43329.7708 | 61 | 61
2018-08-17 19:00 | 40 | 40 |  |  | 43329.7917 | 60 | 59
2018-08-17 19:30 | 41 | 40 |  |  | 43329.8125 | 60 | 60
2018-08-17 20:00 | 38 | 38 |  |  | 43329.8333 | 56 | 56
2018-08-17 20:30 | 36 | 35 |  |  | 43329.8542 | 53 | 53
2018-08-17 21:00 | 35 | 34 |  |  | 43329.875 | 52 | 51
2018-08-17 21:30 | 34 | 32 |  |  | 43329.8958 | 49 | 49
2018-08-17 22:00 | 33 | 32 |  |  | 43329.9167 | 49 | 49
2018-08-17 22:30 | 32 | 30 |  |  | 43329.9375 | 48 | 48
2018-08-17 23:00 | 34 | 32 |  |  | 43329.9583 | 49 | 49
2018-08-17 23:30 | 33 | 31 |  |  | 43329.9792 | 48 | 48
2018-08-18 | 30 | 29 |  |  | 43330 | 45 | 45
2018-08-18 00:30 | 29 | 28 |  |  | 43330.0208 | 42 | 42
2018-08-18 01:00 | 26 | 25 |  |  | 43330.0417 | 38 | 38
2018-08-18 01:30 | 27 | 26 |  |  | 43330.0625 | 40 | 40
2018-08-18 02:00 | 27 | 26 |  |  | 43330.0833 | 37 | 37
2018-08-18 02:30 | 26 | 25 |  |  | 43330.1042 | 37 | 37
2018-08-18 03:00 | 27 | 25 |  |  | 43330.125 | 38 | 38
2018-08-18 03:30 | 29 | 28 |  |  | 43330.1458 | 40 | 40
2018-08-18 04:00 | 29 | 28 |  |  | 43330.1667 | 42 | 42
2018-08-18 04:30 | 30 | 30 |  |  | 43330.1875 | 44 | 44
2018-08-18 05:00 | 31 | 31 |  |  | 43330.2083 | 45 | 44
2018-08-18 05:30 | 31 | 31 |  |  | 43330.2292 | 45 | 45
2018-08-18 06:00 | 31 | 31 |  |  | 43330.25 | 45 | 45
2018-08-18 06:30 | 27 | 27 |  |  | 43330.2708 | 38 | 38
2018-08-18 07:00 | 29 | 29 |  |  | 43330.2917 | 40 | 40
2018-08-18 07:30 | 28 | 27 |  |  | 43330.3125 | 40 | 40
2018-08-18 08:00 | 23 | 22 |  |  | 43330.3333 | 34 | 33
2018-08-18 08:30 | 22 | 21 |  |  | 43330.3542 | 33 | 32
2018-08-18 09:00 | 23 | 22 |  |  | 43330.375 | 35 | 34
2018-08-18 09:30 | 28 | 27 |  |  | 43330.3958 | 43 | 43
2018-08-18 10:00 | 30 | 29 |  |  | 43330.4167 | 44 | 44
2018-08-18 10:30 | 30 | 29 |  |  | 43330.4375 | 47 | 46
2018-08-18 11:00 | 30 | 29 |  |  | 43330.4583 | 46 | 45
2018-08-18 11:30 | 30 | 29 |  |  | 43330.4792 | 45 | 45
2018-08-18 12:00 | 30 | 29 |  |  | 43330.5 | 47 | 46
2018-08-18 12:30 | 30 | 29 |  |  | 43330.5208 | 45 | 45
2018-08-18 13:00 | 29 | 28 |  |  | 43330.5417 | 45 | 44
2018-08-18 13:30 | 30 | 29 |  |  | 43330.5625 | 46 | 45
2018-08-18 14:00 | 29 | 28 |  |  | 43330.5833 | 43 | 42
2018-08-18 14:30 | 32 | 31 |  |  | 43330.6042 | 46 | 46
2018-08-18 15:00 | 33 | 32 |  |  | 43330.625 | 48 | 47
2018-08-18 15:30 | 35 | 34 |  |  | 43330.6458 | 52 | 51
2018-08-18 16:00 | 36 | 36 |  |  | 43330.6667 | 54 | 53
2018-08-18 16:30 | 36 | 36 |  |  | 43330.6875 | 54 | 54
2018-08-18 17:00 | 34 | 34 |  |  | 43330.7083 | 51 | 51
2018-08-18 17:30 | 34 | 34 |  |  | 43330.7292 | 50 | 50
2018-08-18 18:00 | 33 | 33 |  |  | 43330.75 | 52 | 52
2018-08-18 18:30 | 34 | 34 |  |  | 43330.7708 | 53 | 52
2018-08-18 19:00 | 35 | 35 |  |  | 43330.7917 | 54 | 52
2018-08-18 19:30 | 33 | 33 |  |  | 43330.8125 | 53 | 51
2018-08-18 20:00 | 32 | 32 |  |  | 43330.8333 | 50 | 49
2018-08-18 20:30 | 32 | 31 |  |  | 43330.8542 | 50 | 48
2018-08-18 21:00 | 30 | 30 |  |  | 43330.875 | 46 | 45
2018-08-18 21:30 | 28 | 28 |  |  | 43330.8958 | 44 | 43
2018-08-18 22:00 | 30 | 29 |  |  | 43330.9167 | 45 | 44
2018-08-18 22:30 | 29 | 29 |  |  | 43330.9375 | 45 | 44
2018-08-18 23:00 | 28 | 28 |  |  | 43330.9583 | 43 | 42
2018-08-18 23:30 | 26 | 25 |  |  | 43330.9792 | 41 | 39
2018-08-19 | 29 | 28 |  |  | 43331 | 44 | 42
2018-08-19 00:30 | 30 | 29 |  |  | 43331.0208 | 44 | 43
2018-08-19 01:00 | 29 | 29 |  |  | 43331.0417 | 42 | 41
2018-08-19 01:30 | 27 | 27 |  |  | 43331.0625 | 41 | 39
2018-08-19 02:00 | 28 | 28 |  |  | 43331.0833 | 43 | 41
2018-08-19 02:30 | 28 | 28 |  |  | 43331.1042 | 43 | 41
2018-08-19 03:00 | 27 | 26 |  |  | 43331.125 | 40 | 38
2018-08-19 03:30 | 26 | 25 |  |  | 43331.1458 | 40 | 37
2018-08-19 04:00 | 25 | 25 |  |  | 43331.1667 | 39 | 37
2018-08-19 04:30 | 26 | 26 |  |  | 43331.1875 | 39 | 37
2018-08-19 05:00 | 27 | 26 |  |  | 43331.2083 | 39 | 38
2018-08-19 05:30 | 28 | 28 |  |  | 43331.2292 | 42 | 41
2018-08-19 06:00 | 28 | 28 |  |  | 43331.25 | 41 | 40
2018-08-19 06:30 | 26 | 26 |  |  | 43331.2708 | 41 | 40
2018-08-19 07:00 | 26 | 26 |  |  | 43331.2917 | 41 | 40
2018-08-19 07:30 | 25 | 25 |  |  | 43331.3125 | 39 | 38
2018-08-19 08:00 | 22 | 22 |  |  | 43331.3333 | 34 | 34
2018-08-19 08:30 | 22 | 22 |  |  | 43331.3542 | 36 | 36
2018-08-19 09:00 | 23 | 23 |  |  | 43331.375 | 36 | 36
2018-08-19 09:30 | 22 | 22 |  |  | 43331.3958 | 34 | 34
2018-08-19 10:00 | 22 | 22 |  |  | 43331.4167 | 34 | 34
2018-08-19 10:30 | 22 | 22 |  |  | 43331.4375 | 33 | 33
2018-08-19 11:00 | 23 | 22 |  |  | 43331.4583 | 34 | 34
2018-08-19 11:30 | 21 | 21 |  |  | 43331.4792 | 32 | 32
2018-08-19 12:00 | 22 | 21 |  |  | 43331.5 | 32 | 32
2018-08-19 12:30 | 21 | 21 |  |  | 43331.5208 | 33 | 33
2018-08-19 13:00 | 21 | 21 |  |  | 43331.5417 | 33 | 33
2018-08-19 13:30 | 21 | 20 |  |  | 43331.5625 | 33 | 33
2018-08-19 14:00 | 23 | 23 |  |  | 43331.5833 | 35 | 34
2018-08-19 14:30 | 24 | 24 |  |  | 43331.6042 | 37 | 37
2018-08-19 15:00 | 24 | 24 |  |  | 43331.625 | 37 | 37
2018-08-19 15:30 | 27 | 27 |  |  | 43331.6458 | 40 | 40
2018-08-19 16:00 | 27 | 27 |  |  | 43331.6667 | 41 | 41
2018-08-19 16:30 | 31 | 31 |  |  | 43331.6875 | 45 | 45
2018-08-19 17:00 | 29 | 29 |  |  | 43331.7083 | 44 | 43
2018-08-19 17:30 | 30 | 30 |  |  | 43331.7292 | 46 | 45
2018-08-19 18:00 | 35 | 35 |  |  | 43331.75 | 54 | 53
2018-08-19 18:30 | 39 | 39 |  |  | 43331.7708 | 58 | 57
2018-08-19 19:00 | 40 | 40 |  |  | 43331.7917 | 61 | 61
2018-08-19 19:30 | 39 | 39 |  |  | 43331.8125 | 60 | 59
2018-08-19 20:00 | 37 | 36 |  |  | 43331.8333 | 57 | 56
2018-08-19 20:30 | 37 | 37 |  |  | 43331.8542 | 56 | 55
2018-08-19 21:00 | 34 | 33 |  |  | 43331.875 | 51 | 50
2018-08-19 21:30 | 32 | 32 |  |  | 43331.8958 | 49 | 48
2018-08-19 22:00 | 33 | 32 |  |  | 43331.9167 | 50 | 49
2018-08-19 22:30 | 31 | 31 |  |  | 43331.9375 | 48 | 47
2018-08-19 23:00 | 30 | 30 |  |  | 43331.9583 | 46 | 45
2018-08-19 23:30 | 27 | 27 |  |  | 43331.9792 | 42 | 41
2018-08-20 | 25 | 25 |  |  | 43332 | 40 | 38
2018-08-20 00:30 | 23 | 23 |  |  | 43332.0208 | 38 | 36
2018-08-20 01:00 | 25 | 24 |  |  | 43332.0417 | 39 | 37
2018-08-20 01:30 | 25 | 24 |  |  | 43332.0625 | 37 | 34
2018-08-20 02:00 | 25 | 24 |  |  | 43332.0833 | 38 | 35
2018-08-20 02:30 | 26 | 26 |  |  | 43332.1042 | 40 | 38
2018-08-20 03:00 | 24 | 24 |  |  | 43332.125 | 39 | 37
2018-08-20 03:30 | 25 | 24 |  |  | 43332.1458 | 38 | 36
2018-08-20 04:00 | 26 | 25 |  |  | 43332.1667 | 40 | 37
2018-08-20 04:30 | 29 | 28 |  |  | 43332.1875 | 43 | 41
2018-08-20 05:00 | 33 | 33 |  |  | 43332.2083 | 49 | 47
2018-08-20 05:30 | 37 | 37 |  |  | 43332.2292 | 51 | 50
2018-08-20 06:00 | 38 | 38 |  |  | 43332.25 | 52 | 50
2018-08-20 06:30 | 41 | 40 |  |  | 43332.2708 | 59 | 58
2018-08-20 07:00 | 45 | 45 |  |  | 43332.2917 | 68 | 67
2018-08-20 07:30 | 45 | 45 |  |  | 43332.3125 | 70 | 70
2018-08-20 08:00 | 42 | 42 |  |  | 43332.3333 | 66 | 65
2018-08-20 08:30 | 41 | 41 |  |  | 43332.3542 | 65 | 65
2018-08-20 09:00 | 37 | 36 |  |  | 43332.375 | 57 | 57
2018-08-20 09:30 | 36 | 34 |  |  | 43332.3958 | 51 | 50
2018-08-20 10:00 | 35 | 32 |  |  | 43332.4167 | 49 | 49
2018-08-20 10:30 | 34 | 31 |  |  | 43332.4375 | 47 | 46
2018-08-20 11:00 | 35 | 32 |  |  | 43332.4583 | 48 | 47
2018-08-20 11:30 | 35 | 33 |  |  | 43332.4792 | 48 | 48
2018-08-20 12:00 | 34 | 31 |  |  | 43332.5 | 47 | 47
2018-08-20 12:30 | 36 | 33 |  |  | 43332.5208 | 51 | 51
2018-08-20 13:00 | 37 | 34 |  |  | 43332.5417 | 53 | 53
2018-08-20 13:30 | 40 | 37 |  |  | 43332.5625 | 57 | 57
2018-08-20 14:00 | 41 | 39 |  |  | 43332.5833 | 59 | 58
2018-08-20 14:30 | 42 | 40 |  |  | 43332.6042 | 60 | 59
2018-08-20 15:00 | 43 | 41 |  |  | 43332.625 | 61 | 61
2018-08-20 15:30 | 45 | 43 |  |  | 43332.6458 | 63 | 63
2018-08-20 16:00 | 44 | 42 |  |  | 43332.6667 | 61 | 61
2018-08-20 16:30 | 43 | 42 |  |  | 43332.6875 | 60 | 60
2018-08-20 17:00 | 44 | 43 |  |  | 43332.7083 | 62 | 62
2018-08-20 17:30 | 46 | 46 |  |  | 43332.7292 | 66 | 66
2018-08-20 18:00 | 51 | 49 |  |  | 43332.75 | 71 | 71
2018-08-20 18:30 | 55 | 49 |  |  | 43332.7708 | 72 | 72
2018-08-20 19:00 | 57 | 51 |  |  | 43332.7917 | 74 | 73
2018-08-20 19:30 | 55 | 50 |  |  | 43332.8125 | 72 | 72
2018-08-20 20:00 | 53 | 49 |  |  | 43332.8333 | 71 | 71
2018-08-20 20:30 | 52 | 49 |  |  | 43332.8542 | 70 | 69
2018-08-20 21:00 | 50 | 46 |  |  | 43332.875 | 65 | 65
2018-08-20 21:30 | 49 | 45 |  |  | 43332.8958 | 63 | 62
2018-08-20 22:00 | 49 | 44 |  |  | 43332.9167 | 61 | 61
2018-08-20 22:30 | 47 | 41 |  |  | 43332.9375 | 58 | 58
2018-08-20 23:00 | 44 | 39 |  |  | 43332.9583 | 54 | 54
2018-08-20 23:30 | 43 | 35 |  |  | 43332.9792 | 48 | 47
2018-08-21 | 38 | 29 |  |  | 43333 | 41 | 41
2018-08-21 00:30 | 37 | 29 |  |  | 43333.0208 | 40 | 40
2018-08-21 01:00 | 36 | 28 |  |  | 43333.0417 | 39 | 38
2018-08-21 01:30 | 35 | 26 |  |  | 43333.0625 | 36 | 36
2018-08-21 02:00 | 36 | 28 |  |  | 43333.0833 | 37 | 37
2018-08-21 02:30 | 38 | 30 |  |  | 43333.1042 | 40 | 40
2018-08-21 03:00 | 37 | 30 |  |  | 43333.125 | 41 | 41
2018-08-21 03:30 | 38 | 33 |  |  | 43333.1458 | 43 | 43
2018-08-21 04:00 | 39 | 33 |  |  | 43333.1667 | 43 | 43
2018-08-21 04:30 | 41 | 35 |  |  | 43333.1875 | 46 | 46
2018-08-21 05:00 | 46 | 41 |  |  | 43333.2083 | 52 | 52
2018-08-21 05:30 | 50 | 44 |  |  | 43333.2292 | 58 | 58
2018-08-21 06:00 | 53 | 47 |  |  | 43333.25 | 61 | 61
2018-08-21 06:30 | 62 | 55 |  |  | 43333.2708 | 74 | 73
2018-08-21 07:00 | 67 | 59 |  |  | 43333.2917 | 83 | 83
2018-08-21 07:30 | 63 | 56 |  |  | 43333.3125 | 82 | 82
2018-08-21 08:00 | 54 | 49 |  |  | 43333.3333 | 74 | 74
2018-08-21 08:30 | 52 | 45 |  |  | 43333.3542 | 67 | 67
2018-08-21 09:00 | 47 | 40 |  |  | 43333.375 | 59 | 59
2018-08-21 09:30 | 44 | 36 |  |  | 43333.3958 | 54 | 54
2018-08-21 10:00 | 36 | 32 |  |  | 43333.4167 | 49 | 48
2018-08-21 10:30 | 36 | 33 |  |  | 43333.4375 | 48 | 48
2018-08-21 11:00 | 37 | 34 |  |  | 43333.4583 | 51 | 51
2018-08-21 11:30 | 39 | 36 |  |  | 43333.4792 | 54 | 54
2018-08-21 12:00 | 40 | 38 |  |  | 43333.5 | 57 | 57
2018-08-21 12:30 | 42 | 39 |  |  | 43333.5208 | 58 | 58
2018-08-21 13:00 | 42 | 39 |  |  | 43333.5417 | 59 | 59
2018-08-21 13:30 | 43 | 40 |  |  | 43333.5625 | 60 | 60
2018-08-21 14:00 | 43 | 41 |  |  | 43333.5833 | 60 | 60
2018-08-21 14:30 | 43 | 41 |  |  | 43333.6042 | 59 | 59
2018-08-21 15:00 | 43 | 41 |  |  | 43333.625 | 59 | 59
2018-08-21 15:30 | 42 | 40 |  |  | 43333.6458 | 58 | 58
2018-08-21 16:00 | 44 | 42 |  |  | 43333.6667 | 61 | 61
2018-08-21 16:30 | 45 | 44 |  |  | 43333.6875 | 63 | 63
2018-08-21 17:00 | 46 | 45 |  |  | 43333.7083 | 64 | 63
2018-08-21 17:30 | 49 | 48 |  |  | 43333.7292 | 68 | 68
2018-08-21 18:00 | 51 | 50 |  |  | 43333.75 | 72 | 70
2018-08-21 18:30 | 51 | 50 |  |  | 43333.7708 | 72 | 71
2018-08-21 19:00 | 53 | 52 |  |  | 43333.7917 | 76 | 74
2018-08-21 19:30 | 51 | 51 |  |  | 43333.8125 | 73 | 71
2018-08-21 20:00 | 49 | 49 |  |  | 43333.8333 | 68 | 67
2018-08-21 20:30 | 49 | 48 |  |  | 43333.8542 | 67 | 65
2018-08-21 21:00 | 46 | 46 |  |  | 43333.875 | 64 | 62
2018-08-21 21:30 | 47 | 46 |  |  | 43333.8958 | 63 | 60
2018-08-21 22:00 | 44 | 43 |  |  | 43333.9167 | 62 | 59
2018-08-21 22:30 | 42 | 42 |  |  | 43333.9375 | 60 | 58
2018-08-21 23:00 | 39 | 38 |  |  | 43333.9583 | 55 | 52
2018-08-21 23:30 | 34 | 33 |  |  | 43333.9792 | 49 | 46
2018-08-22 | 28 | 27 |  |  | 43334 | 42 | 38
2018-08-22 00:30 | 28 | 27 |  |  | 43334.0208 | 41 | 38
2018-08-22 01:00 | 27 | 27 |  |  | 43334.0417 | 40 | 37
2018-08-22 01:30 | 25 | 25 |  |  | 43334.0625 | 39 | 35
2018-08-22 02:00 | 26 | 26 |  |  | 43334.0833 | 38 | 34
2018-08-22 02:30 | 27 | 27 |  |  | 43334.1042 | 39 | 35
2018-08-22 03:00 | 29 | 28 |  |  | 43334.125 | 40 | 36
2018-08-22 03:30 | 29 | 29 |  |  | 43334.1458 | 40 | 36
2018-08-22 04:00 | 29 | 29 |  |  | 43334.1667 | 41 | 37
2018-08-22 04:30 | 32 | 32 |  |  | 43334.1875 | 47 | 43
2018-08-22 05:00 | 38 | 38 |  |  | 43334.2083 | 52 | 49
2018-08-22 05:30 | 41 | 41 |  |  | 43334.2292 | 55 | 52
2018-08-22 06:00 | 45 | 45 |  |  | 43334.25 | 62 | 58
2018-08-22 06:30 | 53 | 53 |  |  | 43334.2708 | 72 | 70
2018-08-22 07:00 | 59 | 58 |  |  | 43334.2917 | 83 | 81
2018-08-22 07:30 | 57 | 56 |  |  | 43334.3125 | 84 | 82
2018-08-22 08:00 | 51 | 51 |  |  | 43334.3333 | 79 | 76
2018-08-22 08:30 | 46 | 46 |  |  | 43334.3542 | 73 | 69
2018-08-22 09:00 | 45 | 44 |  |  | 43334.375 | 66 | 64
2018-08-22 09:30 | 41 | 39 |  |  | 43334.3958 | 57 | 56
2018-08-22 10:00 | 38 | 35 |  |  | 43334.4167 | 51 | 51
2018-08-22 10:30 | 37 | 34 |  |  | 43334.4375 | 49 | 49
2018-08-22 11:00 | 36 | 34 |  |  | 43334.4583 | 49 | 49
2018-08-22 11:30 | 40 | 37 |  |  | 43334.4792 | 53 | 53
2018-08-22 12:00 | 39 | 36 |  |  | 43334.5 | 53 | 53
2018-08-22 12:30 | 37 | 34 |  |  | 43334.5208 | 50 | 50
2018-08-22 13:00 | 36 | 33 |  |  | 43334.5417 | 48 | 48
2018-08-22 13:30 | 35 | 32 |  |  | 43334.5625 | 47 | 47
2018-08-22 14:00 | 38 | 34 |  |  | 43334.5833 | 49 | 49
2018-08-22 14:30 | 40 | 37 |  |  | 43334.6042 | 53 | 53
2018-08-22 15:00 | 40 | 38 |  |  | 43334.625 | 55 | 55
2018-08-22 15:30 | 41 | 39 |  |  | 43334.6458 | 56 | 55
2018-08-22 16:00 | 44 | 43 |  |  | 43334.6667 | 60 | 60
2018-08-22 16:30 | 47 | 45 |  |  | 43334.6875 | 64 | 64
2018-08-22 17:00 | 48 | 47 |  |  | 43334.7083 | 66 | 66
2018-08-22 17:30 | 50 | 50 |  |  | 43334.7292 | 70 | 69
2018-08-22 18:00 | 51 | 51 |  |  | 43334.75 | 72 | 71
2018-08-22 18:30 | 52 | 51 |  |  | 43334.7708 | 72 | 70
2018-08-22 19:00 | 53 | 53 |  |  | 43334.7917 | 75 | 73
2018-08-22 19:30 | 53 | 53 |  |  | 43334.8125 | 74 | 71
2018-08-22 20:00 | 53 | 52 |  |  | 43334.8333 | 72 | 70
2018-08-22 20:30 | 52 | 52 |  |  | 43334.8542 | 71 | 69
2018-08-22 21:00 | 47 | 47 |  |  | 43334.875 | 65 | 62
2018-08-22 21:30 | 44 | 44 |  |  | 43334.8958 | 62 | 59
2018-08-22 22:00 | 43 | 43 |  |  | 43334.9167 | 62 | 59
2018-08-22 22:30 | 43 | 43 |  |  | 43334.9375 | 62 | 59
2018-08-22 23:00 | 42 | 42 |  |  | 43334.9583 | 60 | 57
2018-08-22 23:30 | 36 | 36 |  |  | 43334.9792 | 54 | 50
2018-08-23 | 31 | 31 |  |  | 43335 | 49 | 45
2018-08-23 00:30 | 33 | 33 |  |  | 43335.0208 | 49 | 46
2018-08-23 01:00 | 30 | 30 |  |  | 43335.0417 | 46 | 42
2018-08-23 01:30 | 31 | 30 |  |  | 43335.0625 | 47 | 43
2018-08-23 02:00 | 29 | 29 |  |  | 43335.0833 | 44 | 40
2018-08-23 02:30 | 28 | 28 |  |  | 43335.1042 | 42 | 37
2018-08-23 03:00 | 27 | 27 |  |  | 43335.125 | 40 | 36
2018-08-23 03:30 | 26 | 26 |  |  | 43335.1458 | 40 | 35
2018-08-23 04:00 | 27 | 27 |  |  | 43335.1667 | 41 | 36
2018-08-23 04:30 | 31 | 31 |  |  | 43335.1875 | 46 | 42
2018-08-23 05:00 | 35 | 35 |  |  | 43335.2083 | 51 | 47
2018-08-23 05:30 | 39 | 39 |  |  | 43335.2292 | 55 | 52
2018-08-23 06:00 | 43 | 43 |  |  | 43335.25 | 58 | 56
2018-08-23 06:30 | 47 | 47 |  |  | 43335.2708 | 68 | 66
2018-08-23 07:00 | 54 | 53 |  |  | 43335.2917 | 77 | 76
2018-08-23 07:30 | 55 | 52 |  |  | 43335.3125 | 78 | 78
2018-08-23 08:00 | 51 | 48 |  |  | 43335.3333 | 74 | 73
2018-08-23 08:30 | 47 | 44 |  |  | 43335.3542 | 69 | 69
2018-08-23 09:00 | 43 | 40 |  |  | 43335.375 | 64 | 64
2018-08-23 09:30 | 42 | 38 |  |  | 43335.3958 | 58 | 58
2018-08-23 10:00 | 41 | 37 |  |  | 43335.4167 | 56 | 56
2018-08-23 10:30 | 40 | 35 |  |  | 43335.4375 | 54 | 54
2018-08-23 11:00 | 42 | 38 |  |  | 43335.4583 | 57 | 57
2018-08-23 11:30 | 44 | 40 |  |  | 43335.4792 | 60 | 60
2018-08-23 12:00 | 46 | 41 |  |  | 43335.5 | 62 | 62
2018-08-23 12:30 | 45 | 40 |  |  | 43335.5208 | 59 | 59
2018-08-23 13:00 | 44 | 40 |  |  | 43335.5417 | 59 | 59
2018-08-23 13:30 | 45 | 40 |  |  | 43335.5625 | 59 | 59
2018-08-23 14:00 | 45 | 41 |  |  | 43335.5833 | 59 | 59
2018-08-23 14:30 | 45 | 40 |  |  | 43335.6042 | 58 | 58
2018-08-23 15:00 | 46 | 42 |  |  | 43335.625 | 59 | 58
2018-08-23 15:30 | 47 | 42 |  |  | 43335.6458 | 60 | 60
2018-08-23 16:00 | 45 | 41 |  |  | 43335.6667 | 59 | 59
2018-08-23 16:30 | 46 | 41 |  |  | 43335.6875 | 59 | 59
2018-08-23 17:00 | 46 | 42 |  |  | 43335.7083 | 60 | 60
2018-08-23 17:30 | 45 | 43 |  |  | 43335.7292 | 61 | 60
2018-08-23 18:00 | 49 | 48 |  |  | 43335.75 | 68 | 66
2018-08-23 18:30 | 49 | 49 |  |  | 43335.7708 | 67 | 64
2018-08-23 19:00 | 51 | 51 |  |  | 43335.7917 | 70 | 67
2018-08-23 19:30 | 49 | 48 |  |  | 43335.8125 | 68 | 65
2018-08-23 20:00 | 49 | 48 |  |  | 43335.8333 | 66 | 64
2018-08-23 20:30 | 49 | 48 |  |  | 43335.8542 | 64 | 62
2018-08-23 21:00 | 47 | 45 |  |  | 43335.875 | 59 | 58
2018-08-23 21:30 | 46 | 44 |  |  | 43335.8958 | 57 | 56
2018-08-23 22:00 | 45 | 43 |  |  | 43335.9167 | 58 | 57
2018-08-23 22:30 | 43 | 42 |  |  | 43335.9375 | 59 | 57
2018-08-23 23:00 | 40 | 39 |  |  | 43335.9583 | 54 | 52
2018-08-23 23:30 | 38 | 36 |  |  | 43335.9792 | 51 | 49
2018-08-24 | 33 | 31 |  |  | 43336 | 45 | 43
2018-08-24 00:30 | 30 | 29 |  |  | 43336.0208 | 42 | 39
2018-08-24 01:00 | 28 | 28 |  |  | 43336.0417 | 42 | 38
2018-08-24 01:30 | 26 | 25 |  |  | 43336.0625 | 40 | 35
2018-08-24 02:00 | 26 | 25 |  |  | 43336.0833 | 38 | 33
2018-08-24 02:30 | 27 | 27 |  |  | 43336.1042 | 39 | 35
2018-08-24 03:00 | 26 | 26 |  |  | 43336.125 | 37 | 34
2018-08-24 03:30 | 25 | 24 |  |  | 43336.1458 | 35 | 32
2018-08-24 04:00 | 27 | 26 |  |  | 43336.1667 | 37 | 34
2018-08-24 04:30 | 29 | 28 |  |  | 43336.1875 | 41 | 38
2018-08-24 05:00 | 33 | 32 |  |  | 43336.2083 | 44 | 41
2018-08-24 05:30 | 37 | 36 |  |  | 43336.2292 | 49 | 47
2018-08-24 06:00 | 40 | 40 |  |  | 43336.25 | 54 | 52
2018-08-24 06:30 | 47 | 46 |  |  | 43336.2708 | 66 | 64
2018-08-24 07:00 | 50 | 50 |  |  | 43336.2917 | 72 | 71
2018-08-24 07:30 | 50 | 49 |  |  | 43336.3125 | 74 | 74
2018-08-24 08:00 | 46 | 46 |  |  | 43336.3333 | 70 | 70
2018-08-24 08:30 | 42 | 41 |  |  | 43336.3542 | 66 | 65
2018-08-24 09:00 | 39 | 38 |  |  | 43336.375 | 60 | 59
2018-08-24 09:30 | 37 | 36 |  |  | 43336.3958 | 56 | 55
2018-08-24 10:00 | 36 | 35 |  |  | 43336.4167 | 55 | 54
2018-08-24 10:30 | 38 | 37 |  |  | 43336.4375 | 56 | 55
2018-08-24 11:00 | 39 | 38 |  |  | 43336.4583 | 57 | 57
2018-08-24 11:30 | 41 | 40 |  |  | 43336.4792 | 60 | 60
2018-08-24 12:00 | 44 | 42 |  |  | 43336.5 | 63 | 63
2018-08-24 12:30 | 47 | 44 |  |  | 43336.5208 | 65 | 65
2018-08-24 13:00 | 47 | 44 |  |  | 43336.5417 | 62 | 62
2018-08-24 13:30 | 39 | 37 |  |  | 43336.5625 | 57 | 57
2018-08-24 14:00 | 42 | 40 |  |  | 43336.5833 | 60 | 60
2018-08-24 14:30 | 43 | 41 |  |  | 43336.6042 | 60 | 60
2018-08-24 15:00 | 45 | 43 |  |  | 43336.625 | 61 | 61
2018-08-24 15:30 | 46 | 44 |  |  | 43336.6458 | 63 | 63
2018-08-24 16:00 | 49 | 47 |  |  | 43336.6667 | 66 | 66
2018-08-24 16:30 | 48 | 47 |  |  | 43336.6875 | 67 | 67
2018-08-24 17:00 | 48 | 47 |  |  | 43336.7083 | 66 | 66
2018-08-24 17:30 | 50 | 50 |  |  | 43336.7292 | 69 | 69
2018-08-24 18:00 | 51 | 51 |  |  | 43336.75 | 71 | 69
2018-08-24 18:30 | 49 | 49 |  |  | 43336.7708 | 69 | 66
2018-08-24 19:00 | 50 | 50 |  |  | 43336.7917 | 70 | 68
2018-08-24 19:30 | 48 | 48 |  |  | 43336.8125 | 68 | 66
2018-08-24 20:00 | 49 | 47 |  |  | 43336.8333 | 64 | 63
2018-08-24 20:30 | 48 | 46 |  |  | 43336.8542 | 63 | 62
2018-08-24 21:00 | 46 | 44 |  |  | 43336.875 | 59 | 59
2018-08-24 21:30 | 43 | 42 |  |  | 43336.8958 | 56 | 56
2018-08-24 22:00 | 42 | 40 |  |  | 43336.9167 | 54 | 54
2018-08-24 22:30 | 41 | 39 |  |  | 43336.9375 | 53 | 53
2018-08-24 23:00 | 41 | 39 |  |  | 43336.9583 | 51 | 50
2018-08-24 23:30 | 36 | 33 |  |  | 43336.9792 | 45 | 44
2018-08-25 | 32 | 28 |  |  | 43337 | 39 | 37
2018-08-25 00:30 | 31 | 27 |  |  | 43337.0208 | 37 | 35
2018-08-25 01:00 | 31 | 27 |  |  | 43337.0417 | 37 | 35
2018-08-25 01:30 | 32 | 25 |  |  | 43337.0625 | 34 | 32
2018-08-25 02:00 | 35 | 22 |  |  | 43337.0833 | 30 | 29
2018-08-25 02:30 | 34 | 20 |  |  | 43337.1042 | 28 | 26
2018-08-25 03:00 | 33 | 19 |  |  | 43337.125 | 27 | 25
2018-08-25 03:30 | 33 | 18 |  |  | 43337.1458 | 26 | 24
2018-08-25 04:00 | 32 | 16 |  |  | 43337.1667 | 25 | 23
2018-08-25 04:30 | 33 | 18 |  |  | 43337.1875 | 27 | 25
2018-08-25 05:00 | 34 | 19 |  |  | 43337.2083 | 27 | 25
2018-08-25 05:30 | 33 | 20 |  |  | 43337.2292 | 29 | 27
2018-08-25 06:00 | 33 | 21 |  |  | 43337.25 | 30 | 28
2018-08-25 06:30 | 33 | 21 |  |  | 43337.2708 | 29 | 28
2018-08-25 07:00 | 33 | 21 |  |  | 43337.2917 | 31 | 30
2018-08-25 07:30 | 33 | 22 |  |  | 43337.3125 | 31 | 30
2018-08-25 08:00 | 33 | 21 |  |  | 43337.3333 | 30 | 29
2018-08-25 08:30 | 35 | 21 |  |  | 43337.3542 | 33 | 31
2018-08-25 09:00 | 34 | 19 |  |  | 43337.375 | 31 | 29
2018-08-25 09:30 | 34 | 19 |  |  | 43337.3958 | 31 | 29
2018-08-25 10:00 | 33 | 18 |  |  | 43337.4167 | 29 | 28
2018-08-25 10:30 | 29 | 19 |  |  | 43337.4375 | 30 | 30
2018-08-25 11:00 | 31 | 22 |  |  | 43337.4583 | 30 | 30
2018-08-25 11:30 | 31 | 23 |  |  | 43337.4792 | 31 | 31
2018-08-25 12:00 | 30 | 22 |  |  | 43337.5 | 30 | 30
2018-08-25 12:30 | 31 | 23 |  |  | 43337.5208 | 28 | 28
2018-08-25 13:00 | 32 | 23 |  |  | 43337.5417 | 28 | 28
2018-08-25 13:30 | 40 | 31 |  |  | 43337.5625 | 41 | 41
2018-08-25 14:00 | 50 | 39 |  |  | 43337.5833 | 53 | 53
2018-08-25 14:30 | 57 | 47 |  |  | 43337.6042 | 57 | 56
2018-08-25 15:00 | 48 | 38 |  |  | 43337.625 | 50 | 50
2018-08-25 15:30 | 39 | 29 |  |  | 43337.6458 | 41 | 41
2018-08-25 16:00 | 39 | 29 |  |  | 43337.6667 | 40 | 40
2018-08-25 16:30 | 43 | 31 |  |  | 43337.6875 | 46 | 45
2018-08-25 17:00 | 49 | 34 |  |  | 43337.7083 | 52 | 50
2018-08-25 17:30 | 50 | 36 |  |  | 43337.7292 | 53 | 52
2018-08-25 18:00 | 69 | 38 |  |  | 43337.75 | 56 | 55
2018-08-25 18:30 | 77 | 39 |  |  | 43337.7708 | 58 | 56
2018-08-25 19:00 | 78 | 41 |  |  | 43337.7917 | 60 | 58
2018-08-25 19:30 | 79 | 40 |  |  | 43337.8125 | 59 | 57
2018-08-25 20:00 | 80 | 40 |  |  | 43337.8333 | 58 | 56
2018-08-25 20:30 | 79 | 41 |  |  | 43337.8542 | 59 | 57
2018-08-25 21:00 | 73 | 39 |  |  | 43337.875 | 58 | 53
2018-08-25 21:30 | 73 | 37 |  |  | 43337.8958 | 57 | 51
2018-08-25 22:00 | 74 | 36 |  |  | 43337.9167 | 57 | 52
2018-08-25 22:30 | 58 | 36 |  |  | 43337.9375 | 50 | 50
2018-08-25 23:00 | 55 | 35 |  |  | 43337.9583 | 47 | 47
2018-08-25 23:30 | 54 | 33 |  |  | 43337.9792 | 45 | 45
2018-08-26 | 53 | 31 |  |  | 43338 | 43 | 43
2018-08-26 00:30 | 53 | 28 |  |  | 43338.0208 | 39 | 39
2018-08-26 01:00 | 52 | 26 |  |  | 43338.0417 | 36 | 35
2018-08-26 01:30 | 52 | 25 |  |  | 43338.0625 | 35 | 35
2018-08-26 02:00 | 52 | 23 |  |  | 43338.0833 | 31 | 31
2018-08-26 02:30 | 52 | 21 |  |  | 43338.1042 | 29 | 28
2018-08-26 03:00 | 51 | 21 |  |  | 43338.125 | 28 | 28
2018-08-26 03:30 | 52 | 21 |  |  | 43338.1458 | 29 | 29
2018-08-26 04:00 | 52 | 21 |  |  | 43338.1667 | 29 | 29
2018-08-26 04:30 | 52 | 24 |  |  | 43338.1875 | 32 | 32
2018-08-26 05:00 | 50 | 24 |  |  | 43338.2083 | 34 | 34
2018-08-26 05:30 | 50 | 26 |  |  | 43338.2292 | 37 | 37
2018-08-26 06:00 | 49 | 26 |  |  | 43338.25 | 38 | 37
2018-08-26 06:30 | 49 | 26 |  |  | 43338.2708 | 38 | 38
2018-08-26 07:00 | 49 | 25 |  |  | 43338.2917 | 38 | 38
2018-08-26 07:30 | 50 | 27 |  |  | 43338.3125 | 41 | 41
2018-08-26 08:00 | 51 | 29 |  |  | 43338.3333 | 43 | 42
2018-08-26 08:30 | 51 | 30 |  |  | 43338.3542 | 45 | 44
2018-08-26 09:00 | 51 | 32 |  |  | 43338.375 | 46 | 45
2018-08-26 09:30 | 51 | 33 |  |  | 43338.3958 | 48 | 47
2018-08-26 10:00 | 50 | 33 |  |  | 43338.4167 | 48 | 46
2018-08-26 10:30 | 51 | 35 |  |  | 43338.4375 | 51 | 50
2018-08-26 11:00 | 54 | 38 |  |  | 43338.4583 | 49 | 49
2018-08-26 11:30 | 54 | 37 |  |  | 43338.4792 | 46 | 46
2018-08-26 12:00 | 53 | 35 |  |  | 43338.5 | 46 | 45
2018-08-26 12:30 | 55 | 37 |  |  | 43338.5208 | 47 | 47
2018-08-26 13:00 | 56 | 38 |  |  | 43338.5417 | 51 | 50
2018-08-26 13:30 | 55 | 37 |  |  | 43338.5625 | 45 | 44
2018-08-26 14:00 | 57 | 37 |  |  | 43338.5833 | 47 | 47
2018-08-26 14:30 | 58 | 38 |  |  | 43338.6042 | 53 | 53
2018-08-26 15:00 | 57 | 36 |  |  | 43338.625 | 49 | 49
2018-08-26 15:30 | 58 | 39 |  |  | 43338.6458 | 51 | 51
2018-08-26 16:00 | 56 | 36 |  |  | 43338.6667 | 48 | 48
2018-08-26 16:30 | 55 | 34 |  |  | 43338.6875 | 48 | 48
2018-08-26 17:00 | 56 | 37 |  |  | 43338.7083 | 51 | 51
2018-08-26 17:30 | 56 | 38 |  |  | 43338.7292 | 52 | 52
2018-08-26 18:00 | 59 | 43 |  |  | 43338.75 | 57 | 57
2018-08-26 18:30 | 64 | 44 |  |  | 43338.7708 | 60 | 60
2018-08-26 19:00 | 65 | 45 |  |  | 43338.7917 | 61 | 61
2018-08-26 19:30 | 64 | 44 |  |  | 43338.8125 | 60 | 60
2018-08-26 20:00 | 64 | 43 |  |  | 43338.8333 | 59 | 58
2018-08-26 20:30 | 60 | 43 |  |  | 43338.8542 | 58 | 58
2018-08-26 21:00 | 57 | 40 |  |  | 43338.875 | 53 | 53
2018-08-26 21:30 | 56 | 38 |  |  | 43338.8958 | 50 | 50
2018-08-26 22:00 | 56 | 37 |  |  | 43338.9167 | 51 | 50
2018-08-26 22:30 | 54 | 36 |  |  | 43338.9375 | 51 | 51
2018-08-26 23:00 | 54 | 35 |  |  | 43338.9583 | 48 | 48
2018-08-26 23:30 | 52 | 30 |  |  | 43338.9792 | 42 | 42
2018-08-27 | 51 | 26 |  |  | 43339 | 37 | 37
2018-08-27 00:30 | 51 | 26 |  |  | 43339.0208 | 35 | 35
2018-08-27 01:00 | 50 | 25 |  |  | 43339.0417 | 33 | 33
2018-08-27 01:30 | 47 | 22 |  |  | 43339.0625 | 30 | 30
2018-08-27 02:00 | 46 | 20 |  |  | 43339.0833 | 29 | 28
2018-08-27 02:30 | 47 | 22 |  |  | 43339.1042 | 30 | 29
2018-08-27 03:00 | 47 | 22 |  |  | 43339.125 | 30 | 30
2018-08-27 03:30 | 49 | 25 |  |  | 43339.1458 | 35 | 34
2018-08-27 04:00 | 49 | 26 |  |  | 43339.1667 | 36 | 35
2018-08-27 04:30 | 50 | 29 |  |  | 43339.1875 | 38 | 38
2018-08-27 05:00 | 52 | 32 |  |  | 43339.2083 | 41 | 41
2018-08-27 05:30 | 50 | 35 |  |  | 43339.2292 | 44 | 43
2018-08-27 06:00 | 40 | 40 |  |  | 43339.25 | 50 | 50
2018-08-27 06:30 | 45 | 44 |  |  | 43339.2708 | 60 | 60
2018-08-27 07:00 | 46 | 46 |  |  | 43339.2917 | 64 | 63
2018-08-27 07:30 | 50 | 46 |  |  | 43339.3125 | 69 | 68
2018-08-27 08:00 | 68 | 65 |  |  | 43339.3333 | 47 | 45
2018-08-27 08:30 | 86 | 83 |  |  | 43339.3542 | 23 | 18
2018-08-27 09:00 | 78 | 75 |  |  | 43339.375 | 20 | 16
2018-08-27 09:30 | 74 | 71 |  |  | 43339.3958 | 19 | 16
2018-08-27 10:00 | 69 | 67 |  |  | 43339.4167 | 17 | 14
2018-08-27 10:30 | 66 | 66 |  |  | 43339.4375 | 17 | 15
2018-08-27 11:00 | 63 | 63 |  |  | 43339.4583 | 17 | 13
2018-08-27 11:30 | 61 | 61 |  |  | 43339.4792 | 17 | 13
2018-08-27 12:00 | 61 | 61 |  |  | 43339.5 | 17 | 13
2018-08-27 12:30 | 61 | 61 |  |  | 43339.5208 | 17 | 13
2018-08-27 13:00 | 63 | 63 |  |  | 43339.5417 | 19 | 15
2018-08-27 13:30 | 65 | 65 |  |  | 43339.5625 | 20 | 16
2018-08-27 14:00 | 65 | 65 |  |  | 43339.5833 | 18 | 15
2018-08-27 14:30 | 69 | 69 |  |  | 43339.6042 | 19 | 17
2018-08-27 15:00 | 71 | 71 |  |  | 43339.625 | 18 | 17
2018-08-27 15:30 | 75 | 75 |  |  | 43339.6458 | 17 | 16
2018-08-27 16:00 | 82 | 82 |  |  | 43339.6667 | 19 | 18
2018-08-27 16:30 | 83 | 83 |  |  | 43339.6875 | 18 | 17
2018-08-27 17:00 | 90 | 89 |  |  | 43339.7083 | 18 | 17
2018-08-27 17:30 | 95 | 95 |  |  | 43339.7292 | 18 | 17
2018-08-27 18:00 | 100 | 99 |  |  | 43339.75 | 17 | 17
2018-08-27 18:30 | 102 | 102 |  |  | 43339.7708 | 15 | 15
2018-08-27 19:00 | 104 | 104 |  |  | 43339.7917 | 16 | 16
2018-08-27 19:30 | 102 | 102 |  |  | 43339.8125 | 15 | 15
2018-08-27 20:00 | 101 | 101 |  |  | 43339.8333 | 15 | 15
2018-08-27 20:30 | 101 | 101 |  |  | 43339.8542 | 15 | 14
2018-08-27 21:00 | 95 | 95 |  |  | 43339.875 | 12 | 12
2018-08-27 21:30 | 92 | 92 |  |  | 43339.8958 | 12 | 12
2018-08-27 22:00 | 88 | 88 |  |  | 43339.9167 | 12 | 12
2018-08-27 22:30 | 85 | 85 |  |  | 43339.9375 | 11 | 11
2018-08-27 23:00 | 81 | 81 |  |  | 43339.9583 | 9 | 9
2018-08-27 23:30 | 73 | 72 |  |  | 43339.9792 | 5 | 5
2018-08-28 | 65 | 64 |  |  | 43340 | 3 | 3
2018-08-28 00:30 | 61 | 60 |  |  | 43340.0208 | 4 | 2
2018-08-28 01:00 | 58 | 57 |  |  | 43340.0417 | 3 | 2
2018-08-28 01:30 | 56 | 54 |  |  | 43340.0625 | 3 | 1
2018-08-28 02:00 | 55 | 53 |  |  | 43340.0833 | 2 | 1
2018-08-28 02:30 | 55 | 52 |  |  | 43340.1042 | 2 | 1
2018-08-28 03:00 | 59 | 57 |  |  | 43340.125 | 6 | 6
2018-08-28 03:30 | 63 | 61 |  |  | 43340.1458 | 10 | 9
2018-08-28 04:00 | 64 | 62 |  |  | 43340.1667 | 12 | 11
2018-08-28 04:30 | 62 | 61 |  |  | 43340.1875 | 9 | 8
2018-08-28 05:00 | 66 | 65 |  |  | 43340.2083 | 10 | 9
2018-08-28 05:30 | 69 | 68 |  |  | 43340.2292 | 9 | 7
2018-08-28 06:00 | 72 | 72 |  |  | 43340.25 | 10 | 5
2018-08-28 06:30 | 84 | 84 |  |  | 43340.2708 | 15 | 12
2018-08-28 07:00 | 89 | 88 |  |  | 43340.2917 | 13 | 12
2018-08-28 07:30 | 92 | 90 |  |  | 43340.3125 | 19 | 15
2018-08-28 08:00 | 86 | 85 |  |  | 43340.3333 | 17 | 14
2018-08-28 08:30 | 79 | 77 |  |  | 43340.3542 | 16 | 14
2018-08-28 09:00 | 73 | 71 |  |  | 43340.375 | 15 | 13
2018-08-28 09:30 | 68 | 66 |  |  | 43340.3958 | 13 | 12
2018-08-28 10:00 | 65 | 63 |  |  | 43340.4167 | 13 | 12
2018-08-28 10:30 | 65 | 63 |  |  | 43340.4375 | 15 | 14
2018-08-28 11:00 | 67 | 65 |  |  | 43340.4583 | 18 | 17
2018-08-28 11:30 | 68 | 67 |  |  | 43340.4792 | 19 | 19
2018-08-28 12:00 | 70 | 69 |  |  | 43340.5 | 20 | 20
2018-08-28 12:30 | 69 | 68 |  |  | 43340.5208 | 20 | 20
2018-08-28 13:00 | 70 | 69 |  |  | 43340.5417 | 20 | 20
2018-08-28 13:30 | 70 | 68 |  |  | 43340.5625 | 20 | 20
2018-08-28 14:00 | 70 | 69 |  |  | 43340.5833 | 20 | 19
2018-08-28 14:30 | 71 | 70 |  |  | 43340.6042 | 20 | 19
2018-08-28 15:00 | 72 | 70 |  |  | 43340.625 | 18 | 16
2018-08-28 15:30 | 76 | 74 |  |  | 43340.6458 | 19 | 17
2018-08-28 16:00 | 81 | 79 |  |  | 43340.6667 | 19 | 17
2018-08-28 16:30 | 86 | 84 |  |  | 43340.6875 | 19 | 17
2018-08-28 17:00 | 88 | 85 |  |  | 43340.7083 | 20 | 14
2018-08-28 17:30 | 93 | 90 |  |  | 43340.7292 | 22 | 14
2018-08-28 18:00 | 100 | 97 |  |  | 43340.75 | 24 | 15
2018-08-28 18:30 | 103 | 100 |  |  | 43340.7708 | 27 | 14
2018-08-28 19:00 | 106 | 102 |  |  | 43340.7917 | 29 | 15
2018-08-28 19:30 | 102 | 98 |  |  | 43340.8125 | 28 | 12
2018-08-28 20:00 | 102 | 98 |  |  | 43340.8333 | 27 | 13
2018-08-28 20:30 | 101 | 98 |  |  | 43340.8542 | 24 | 12
2018-08-28 21:00 | 93 | 91 |  |  | 43340.875 | 15 | 8
2018-08-28 21:30 | 88 | 86 |  |  | 43340.8958 | 12 | 6
2018-08-28 22:00 | 84 | 82 |  |  | 43340.9167 | 14 | 6
2018-08-28 22:30 | 84 | 81 |  |  | 43340.9375 | 15 | 7
2018-08-28 23:00 | 83 | 80 |  |  | 43340.9583 | 16 | 7
2018-08-28 23:30 | 76 | 72 |  |  | 43340.9792 | 14 | 4
2018-08-29 | 69 | 64 |  |  | 43341 | 13 | 1
2018-08-29 00:30 | 67 | 62 |  |  | 43341.0208 | 13 | 3
2018-08-29 01:00 | 64 | 58 |  |  | 43341.0417 | 13 | 2
2018-08-29 01:30 | 61 | 54 |  |  | 43341.0625 | 13 | 1
2018-08-29 02:00 | 60 | 54 |  |  | 43341.0833 | 10 | 0
2018-08-29 02:30 | 60 | 54 |  |  | 43341.1042 | 10 | 1
2018-08-29 03:00 | 58 | 53 |  |  | 43341.125 | 10 | 0
2018-08-29 03:30 | 59 | 53 |  |  | 43341.1458 | 10 | 1
2018-08-29 04:00 | 60 | 55 |  |  | 43341.1667 | 10 | 1
2018-08-29 04:30 | 63 | 58 |  |  | 43341.1875 | 10 | 3
2018-08-29 05:00 | 69 | 65 |  |  | 43341.2083 | 11 | 6
2018-08-29 05:30 | 72 | 69 |  |  | 43341.2292 | 11 | 5
2018-08-29 06:00 | 80 | 78 |  |  | 43341.25 | 12 | 8
2018-08-29 06:30 | 88 | 86 |  |  | 43341.2708 | 17 | 13
2018-08-29 07:00 | 95 | 94 |  |  | 43341.2917 | 19 | 16
2018-08-29 07:30 | 98 | 95 |  |  | 43341.3125 | 25 | 16
2018-08-29 08:00 | 90 | 87 |  |  | 43341.3333 | 23 | 12
2018-08-29 08:30 | 82 | 78 |  |  | 43341.3542 | 21 | 11
2018-08-29 09:00 | 74 | 69 |  |  | 43341.375 | 19 | 8
2018-08-29 09:30 | 71 | 67 |  |  | 43341.3958 | 18 | 10
2018-08-29 10:00 | 67 | 64 |  |  | 43341.4167 | 16 | 11
2018-08-29 10:30 | 68 | 65 |  |  | 43341.4375 | 19 | 14
2018-08-29 11:00 | 68 | 66 |  |  | 43341.4583 | 19 | 17
2018-08-29 11:30 | 69 | 67 |  |  | 43341.4792 | 21 | 19
2018-08-29 12:00 | 69 | 68 |  |  | 43341.5 | 22 | 21
2018-08-29 12:30 | 69 | 67 |  |  | 43341.5208 | 22 | 21
2018-08-29 13:00 | 70 | 69 |  |  | 43341.5417 | 23 | 22
2018-08-29 13:30 | 71 | 69 |  |  | 43341.5625 | 23 | 22
2018-08-29 14:00 | 74 | 72 |  |  | 43341.5833 | 24 | 22
2018-08-29 14:30 | 76 | 74 |  |  | 43341.6042 | 24 | 22
2018-08-29 15:00 | 81 | 78 |  |  | 43341.625 | 27 | 24
2018-08-29 15:30 | 82 | 79 |  |  | 43341.6458 | 26 | 23
2018-08-29 16:00 | 86 | 83 |  |  | 43341.6667 | 26 | 21
2018-08-29 16:30 | 88 | 85 |  |  | 43341.6875 | 24 | 19
2018-08-29 17:00 | 92 | 89 |  |  | 43341.7083 | 24 | 17
2018-08-29 17:30 | 99 | 96 |  |  | 43341.7292 | 27 | 19
2018-08-29 18:00 | 103 | 100 |  |  | 43341.75 | 29 | 19
2018-08-29 18:30 | 106 | 101 |  |  | 43341.7708 | 32 | 16
2018-08-29 19:00 | 107 | 102 |  |  | 43341.7917 | 33 | 16
2018-08-29 19:30 | 106 | 102 |  |  | 43341.8125 | 33 | 15
2018-08-29 20:00 | 107 | 102 |  |  | 43341.8333 | 32 | 14
2018-08-29 20:30 | 107 | 102 |  |  | 43341.8542 | 32 | 16
2018-08-29 21:00 | 103 | 97 |  |  | 43341.875 | 31 | 12
2018-08-29 21:30 | 95 | 90 |  |  | 43341.8958 | 27 | 8
2018-08-29 22:00 | 89 | 87 |  |  | 43341.9167 | 17 | 8
2018-08-29 22:30 | 85 | 83 |  |  | 43341.9375 | 12 | 8
2018-08-29 23:00 | 81 | 79 |  |  | 43341.9583 | 10 | 4
2018-08-29 23:30 | 76 | 74 |  |  | 43341.9792 | 8 | 2
2018-08-30 | 67 | 65 |  |  | 43342 | 3 | 0
2018-08-30 00:30 | 64 | 62 |  |  | 43342.0208 | 4 | 1
2018-08-30 01:00 | 63 | 61 |  |  | 43342.0417 | 4 | 2
2018-08-30 01:30 | 60 | 57 |  |  | 43342.0625 | 4 | 1
2018-08-30 02:00 | 59 | 56 |  |  | 43342.0833 | 4 | 1
2018-08-30 02:30 | 57 | 55 |  |  | 43342.1042 | 1 | 1
2018-08-30 03:00 | 55 | 52 |  |  | 43342.125 | 2 | 2
2018-08-30 03:30 | 55 | 53 |  |  | 43342.1458 | 1 | 1
2018-08-30 04:00 | 56 | 54 |  |  | 43342.1667 | 2 | 1
2018-08-30 04:30 | 58 | 56 |  |  | 43342.1875 | 1 | 1
2018-08-30 05:00 | 63 | 62 |  |  | 43342.2083 | 2 | 2
2018-08-30 05:30 | 70 | 69 |  |  | 43342.2292 | 3 | 3
2018-08-30 06:00 | 78 | 77 |  |  | 43342.25 | 7 | 4
2018-08-30 06:30 | 94 | 91 |  |  | 43342.2708 | 20 | 11
2018-08-30 07:00 | 99 | 98 |  |  | 43342.2917 | 18 | 13
2018-08-30 07:30 | 102 | 100 |  |  | 43342.3125 | 22 | 16
2018-08-30 08:00 | 96 | 94 |  |  | 43342.3333 | 23 | 16
2018-08-30 08:30 | 85 | 83 |  |  | 43342.3542 | 19 | 14
2018-08-30 09:00 | 77 | 75 |  |  | 43342.375 | 18 | 13
2018-08-30 09:30 | 72 | 68 |  |  | 43342.3958 | 18 | 12
2018-08-30 10:00 | 75 | 67 |  |  | 43342.4167 | 28 | 14
2018-08-30 10:30 | 71 | 64 |  |  | 43342.4375 | 24 | 11
2018-08-30 11:00 | 72 | 66 |  |  | 43342.4583 | 26 | 16
2018-08-30 11:30 | 71 | 65 |  |  | 43342.4792 | 26 | 15
2018-08-30 12:00 | 71 | 64 |  |  | 43342.5 | 27 | 17
2018-08-30 12:30 | 71 | 65 |  |  | 43342.5208 | 27 | 18
2018-08-30 13:00 | 71 | 64 |  |  | 43342.5417 | 26 | 16
2018-08-30 13:30 | 72 | 66 |  |  | 43342.5625 | 27 | 17
2018-08-30 14:00 | 75 | 68 |  |  | 43342.5833 | 29 | 17
2018-08-30 14:30 | 77 | 70 |  |  | 43342.6042 | 29 | 17
2018-08-30 15:00 | 79 | 69 |  |  | 43342.625 | 33 | 15
2018-08-30 15:30 | 81 | 72 |  |  | 43342.6458 | 34 | 14
2018-08-30 16:00 | 87 | 77 |  |  | 43342.6667 | 36 | 15
2018-08-30 16:30 | 91 | 81 |  |  | 43342.6875 | 36 | 15
2018-08-30 17:00 | 96 | 87 |  |  | 43342.7083 | 37 | 17
2018-08-30 17:30 | 102 | 93 |  |  | 43342.7292 | 40 | 17
2018-08-30 18:00 | 110 | 101 |  |  | 43342.75 | 43 | 20
2018-08-30 18:30 | 113 | 105 |  |  | 43342.7708 | 44 | 20
2018-08-30 19:00 | 116 | 108 |  |  | 43342.7917 | 45 | 21
2018-08-30 19:30 | 108 | 105 |  |  | 43342.8125 | 31 | 20
2018-08-30 20:00 | 106 | 104 |  |  | 43342.8333 | 25 | 18
2018-08-30 20:30 | 104 | 102 |  |  | 43342.8542 | 24 | 16
2018-08-30 21:00 | 96 | 94 |  |  | 43342.875 | 18 | 12
2018-08-30 21:30 | 92 | 91 |  |  | 43342.8958 | 17 | 10
2018-08-30 22:00 | 90 | 88 |  |  | 43342.9167 | 17 | 12
2018-08-30 22:30 | 88 | 86 |  |  | 43342.9375 | 17 | 13
2018-08-30 23:00 | 85 | 83 |  |  | 43342.9583 | 16 | 11
2018-08-30 23:30 | 80 | 77 |  |  | 43342.9792 | 14 | 9
2018-08-31 | 70 | 66 |  |  | 43343 | 12 | 4
2018-08-31 00:30 | 70 | 65 |  |  | 43343.0208 | 14 | 8
2018-08-31 01:00 | 66 | 60 |  |  | 43343.0417 | 12 | 5
2018-08-31 01:30 | 65 | 59 |  |  | 43343.0625 | 13 | 6
2018-08-31 02:00 | 62 | 55 |  |  | 43343.0833 | 14 | 3
2018-08-31 02:30 | 62 | 55 |  |  | 43343.1042 | 14 | 4
2018-08-31 03:00 | 63 | 56 |  |  | 43343.125 | 14 | 5
2018-08-31 03:30 | 63 | 55 |  |  | 43343.1458 | 14 | 4
2018-08-31 04:00 | 63 | 55 |  |  | 43343.1667 | 14 | 4
2018-08-31 04:30 | 67 | 60 |  |  | 43343.1875 | 15 | 6
2018-08-31 05:00 | 71 | 66 |  |  | 43343.2083 | 16 | 9
2018-08-31 05:30 | 77 | 73 |  |  | 43343.2292 | 17 | 11
2018-08-31 06:00 | 86 | 83 |  |  | 43343.25 | 20 | 16
2018-08-31 06:30 | 94 | 89 |  |  | 43343.2708 | 27 | 16
2018-08-31 07:00 | 97 | 91 |  |  | 43343.2917 | 30 | 16
2018-08-31 07:30 | 96 | 90 |  |  | 43343.3125 | 31 | 15
2018-08-31 08:00 | 91 | 85 |  |  | 43343.3333 | 30 | 15
2018-08-31 08:30 | 85 | 78 |  |  | 43343.3542 | 29 | 14
2018-08-31 09:00 | 76 | 69 |  |  | 43343.375 | 25 | 11
2018-08-31 09:30 | 73 | 66 |  |  | 43343.3958 | 24 | 12
2018-08-31 10:00 | 71 | 63 |  |  | 43343.4167 | 24 | 13
2018-08-31 10:30 | 71 | 64 |  |  | 43343.4375 | 25 | 14
2018-08-31 11:00 | 71 | 63 |  |  | 43343.4583 | 26 | 15
2018-08-31 11:30 | 71 | 64 |  |  | 43343.4792 | 26 | 16
2018-08-31 12:00 | 69 | 62 |  |  | 43343.5 | 25 | 16
2018-08-31 12:30 | 63 | 61 |  |  | 43343.5208 | 16 | 15
2018-08-31 13:00 | 61 | 59 |  |  | 43343.5417 | 14 | 13
2018-08-31 13:30 | 62 | 60 |  |  | 43343.5625 | 14 | 13
2018-08-31 14:00 | 64 | 61 |  |  | 43343.5833 | 15 | 11
2018-08-31 14:30 | 65 | 63 |  |  | 43343.6042 | 15 | 11
2018-08-31 15:00 | 44 | 38 |  |  | 43343.625 | 36 | 34
2018-08-31 15:30 | 42 | 30 |  |  | 43343.6458 | 49 | 43
2018-08-31 16:00 | 44 | 33 |  |  | 43343.6667 | 52 | 47
2018-08-31 16:30 | 46 | 35 |  |  | 43343.6875 | 56 | 50
2018-08-31 17:00 | 50 | 38 |  |  | 43343.7083 | 60 | 54
2018-08-31 17:30 | 52 | 40 |  |  | 43343.7292 | 63 | 56
2018-08-31 18:00 | 55 | 43 |  |  | 43343.75 | 66 | 58
2018-08-31 18:30 | 54 | 43 |  |  | 43343.7708 | 67 | 59
2018-08-31 19:00 | 56 | 44 |  |  | 43343.7917 | 67 | 59
2018-08-31 19:30 | 55 | 41 |  |  | 43343.8125 | 65 | 56
2018-08-31 20:00 | 54 | 40 |  |  | 43343.8333 | 64 | 54
2018-08-31 20:30 | 53 | 39 |  |  | 43343.8542 | 63 | 54
2018-08-31 21:00 | 51 | 36 |  |  | 43343.875 | 58 | 50
2018-08-31 21:30 | 50 | 35 |  |  | 43343.8958 | 55 | 46
2018-08-31 22:00 | 51 | 33 |  |  | 43343.9167 | 54 | 44
2018-08-31 22:30 | 51 | 31 |  |  | 43343.9375 | 54 | 43
2018-08-31 23:00 | 50 | 29 |  |  | 43343.9583 | 51 | 40
2018-08-31 23:30 | 43 | 27 |  |  | 43343.9792 | 42 | 36
2018-09-01 | 41 | 23 |  |  | 43344 | 38 | 32
2018-09-01 00:30 | 37 | 23 |  |  | 43344.0208 | 41 | 31
2018-09-01 01:00 | 32 | 22 |  |  | 43344.0417 | 44 | 29
2018-09-01 01:30 | 34 | 23 |  |  | 43344.0625 | 46 | 31
2018-09-01 02:00 | 32 | 22 |  |  | 43344.0833 | 44 | 28
2018-09-01 02:30 | 33 | 24 |  |  | 43344.1042 | 44 | 32
2018-09-01 03:00 | 34 | 25 |  |  | 43344.125 | 44 | 32
2018-09-01 03:30 | 36 | 26 |  |  | 43344.1458 | 48 | 36
2018-09-01 04:00 | 37 | 28 |  |  | 43344.1667 | 52 | 41
2018-09-01 04:30 | 36 | 27 |  |  | 43344.1875 | 51 | 39
2018-09-01 05:00 | 36 | 27 |  |  | 43344.2083 | 51 | 40
2018-09-01 05:30 | 35 | 26 |  |  | 43344.2292 | 48 | 37
2018-09-01 06:00 | 32 | 24 |  |  | 43344.25 | 45 | 34
2018-09-01 06:30 | 31 | 22 |  |  | 43344.2708 | 44 | 33
2018-09-01 07:00 | 29 | 21 |  |  | 43344.2917 | 41 | 31
2018-09-01 07:30 | 28 | 18 |  |  | 43344.3125 | 39 | 29
2018-09-01 08:00 | 26 | 16 |  |  | 43344.3333 | 37 | 26
2018-09-01 08:30 | 26 | 16 |  |  | 43344.3542 | 37 | 28
2018-09-01 09:00 | 27 | 19 |  |  | 43344.375 | 40 | 31
2018-09-01 09:30 | 25 | 16 |  |  | 43344.3958 | 36 | 26
2018-09-01 10:00 | 24 | 15 |  |  | 43344.4167 | 36 | 25
2018-09-01 10:30 | 27 | 19 |  |  | 43344.4375 | 40 | 32
2018-09-01 11:00 | 33 | 27 |  |  | 43344.4583 | 45 | 39
2018-09-01 11:30 | 31 | 24 |  |  | 43344.4792 | 44 | 37
2018-09-01 12:00 | 29 | 22 |  |  | 43344.5 | 43 | 34
2018-09-01 12:30 | 31 | 23 |  |  | 43344.5208 | 44 | 36
2018-09-01 13:00 | 30 | 20 |  |  | 43344.5417 | 41 | 32
2018-09-01 13:30 | 30 | 22 |  |  | 43344.5625 | 43 | 34
2018-09-01 14:00 | 31 | 22 |  |  | 43344.5833 | 43 | 35
2018-09-01 14:30 | 32 | 24 |  |  | 43344.6042 | 44 | 36
2018-09-01 15:00 | 32 | 24 |  |  | 43344.625 | 45 | 37
2018-09-01 15:30 | 36 | 28 |  |  | 43344.6458 | 51 | 44
2018-09-01 16:00 | 37 | 30 |  |  | 43344.6667 | 52 | 45
2018-09-01 16:30 | 36 | 29 |  |  | 43344.6875 | 54 | 45
2018-09-01 17:00 | 38 | 31 |  |  | 43344.7083 | 58 | 49
2018-09-01 17:30 | 41 | 35 |  |  | 43344.7292 | 61 | 53
2018-09-01 18:00 | 42 | 36 |  |  | 43344.75 | 65 | 56
2018-09-01 18:30 | 45 | 38 |  |  | 43344.7708 | 69 | 59
2018-09-01 19:00 | 46 | 39 |  |  | 43344.7917 | 70 | 60
2018-09-01 19:30 | 45 | 37 |  |  | 43344.8125 | 68 | 57
2018-09-01 20:00 | 45 | 38 |  |  | 43344.8333 | 68 | 58
2018-09-01 20:30 | 44 | 36 |  |  | 43344.8542 | 66 | 55
2018-09-01 21:00 | 41 | 33 |  |  | 43344.875 | 62 | 50
2018-09-01 21:30 | 39 | 30 |  |  | 43344.8958 | 59 | 46
2018-09-01 22:00 | 39 | 30 |  |  | 43344.9167 | 58 | 46
2018-09-01 22:30 | 40 | 31 |  |  | 43344.9375 | 60 | 47
2018-09-01 23:00 | 39 | 30 |  |  | 43344.9583 | 59 | 44
2018-09-01 23:30 | 38 | 27 |  |  | 43344.9792 | 56 | 40
2018-09-02 | 35 | 23 |  |  | 43345 | 52 | 36
2018-09-02 00:30 | 35 | 24 |  |  | 43345.0208 | 51 | 36
2018-09-02 01:00 | 38 | 26 |  |  | 43345.0417 | 54 | 39
2018-09-02 01:30 | 37 | 25 |  |  | 43345.0625 | 53 | 37
2018-09-02 02:00 | 35 | 24 |  |  | 43345.0833 | 51 | 36
2018-09-02 02:30 | 28 | 25 |  |  | 43345.1042 | 58 | 36
2018-09-02 03:00 | 27 | 24 |  |  | 43345.125 | 58 | 35
2018-09-02 03:30 | 26 | 23 |  |  | 43345.1458 | 57 | 33
2018-09-02 04:00 | 24 | 21 |  |  | 43345.1667 | 55 | 31
2018-09-02 04:30 | 24 | 21 |  |  | 43345.1875 | 55 | 30
2018-09-02 05:00 | 25 | 22 |  |  | 43345.2083 | 56 | 32
2018-09-02 05:30 | 25 | 22 |  |  | 43345.2292 | 56 | 31
2018-09-02 06:00 | 25 | 22 |  |  | 43345.25 | 56 | 31
2018-09-02 06:30 | 26 | 23 |  |  | 43345.2708 | 57 | 34
2018-09-02 07:00 | 26 | 23 |  |  | 43345.2917 | 57 | 33
2018-09-02 07:30 | 24 | 21 |  |  | 43345.3125 | 55 | 31
2018-09-02 08:00 | 21 | 17 |  |  | 43345.3333 | 51 | 28
2018-09-02 08:30 | 19 | 16 |  |  | 43345.3542 | 50 | 25
2018-09-02 09:00 | 17 | 14 |  |  | 43345.375 | 47 | 23
2018-09-02 09:30 | 16 | 13 |  |  | 43345.3958 | 46 | 21
2018-09-02 10:00 | 17 | 14 |  |  | 43345.4167 | 45 | 22
2018-09-02 10:30 | 16 | 14 |  |  | 43345.4375 | 45 | 22
2018-09-02 11:00 | 17 | 14 |  |  | 43345.4583 | 45 | 22
2018-09-02 11:30 | 18 | 15 |  |  | 43345.4792 | 46 | 24
2018-09-02 12:00 | 18 | 15 |  |  | 43345.5 | 46 | 23
2018-09-02 12:30 | 18 | 15 |  |  | 43345.5208 | 46 | 23
2018-09-02 13:00 | 18 | 16 |  |  | 43345.5417 | 46 | 24
2018-09-02 13:30 | 19 | 16 |  |  | 43345.5625 | 47 | 25
2018-09-02 14:00 | 20 | 17 |  |  | 43345.5833 | 47 | 26
2018-09-02 14:30 | 23 | 21 |  |  | 43345.6042 | 51 | 32
2018-09-02 15:00 | 23 | 22 |  |  | 43345.625 | 50 | 32
2018-09-02 15:30 | 22 | 20 |  |  | 43345.6458 | 50 | 31
2018-09-02 16:00 | 23 | 21 |  |  | 43345.6667 | 50 | 32
2018-09-02 16:30 | 25 | 23 |  |  | 43345.6875 | 51 | 33
2018-09-02 17:00 | 30 | 29 |  |  | 43345.7083 | 56 | 41
2018-09-02 17:30 | 35 | 34 |  |  | 43345.7292 | 62 | 48
2018-09-02 18:00 | 41 | 40 |  |  | 43345.75 | 70 | 56
2018-09-02 18:30 | 42 | 42 |  |  | 43345.7708 | 67 | 59
2018-09-02 19:00 | 44 | 42 |  |  | 43345.7917 | 68 | 61
2018-09-02 19:30 | 45 | 44 |  |  | 43345.8125 | 69 | 62
2018-09-02 20:00 | 43 | 42 |  |  | 43345.8333 | 66 | 59
2018-09-02 20:30 | 40 | 39 |  |  | 43345.8542 | 63 | 56
2018-09-02 21:00 | 37 | 36 |  |  | 43345.875 | 61 | 53
2018-09-02 21:30 | 35 | 34 |  |  | 43345.8958 | 57 | 49
2018-09-02 22:00 | 33 | 32 |  |  | 43345.9167 | 56 | 48
2018-09-02 22:30 | 34 | 32 |  |  | 43345.9375 | 57 | 49
2018-09-02 23:00 | 33 | 32 |  |  | 43345.9583 | 54 | 46
2018-09-02 23:30 | 30 | 29 |  |  | 43345.9792 | 51 | 41
2018-09-03 | 28 | 26 |  |  | 43346 | 49 | 38
2018-09-03 00:30 | 28 | 25 |  |  | 43346.0208 | 49 | 36
2018-09-03 01:00 | 27 | 24 |  |  | 43346.0417 | 48 | 34
2018-09-03 01:30 | 25 | 24 |  |  | 43346.0625 | 49 | 34
2018-09-03 02:00 | 25 | 25 |  |  | 43346.0833 | 55 | 35
2018-09-03 02:30 | 26 | 26 |  |  | 43346.1042 | 54 | 34
2018-09-03 03:00 | 24 | 24 |  |  | 43346.125 | 53 | 31
2018-09-03 03:30 | 22 | 22 |  |  | 43346.1458 | 51 | 28
2018-09-03 04:00 | 24 | 23 |  |  | 43346.1667 | 51 | 28
2018-09-03 04:30 | 25 | 24 |  |  | 43346.1875 | 53 | 32
2018-09-03 05:00 | 29 | 29 |  |  | 43346.2083 | 56 | 37
2018-09-03 05:30 | 33 | 32 |  |  | 43346.2292 | 57 | 41
2018-09-03 06:00 | 37 | 36 |  |  | 43346.25 | 58 | 44
2018-09-03 06:30 | 38 | 37 |  |  | 43346.2708 | 62 | 48
2018-09-03 07:00 | 38 | 37 |  |  | 43346.2917 | 68 | 52
2018-09-03 07:30 | 38 | 38 |  |  | 43346.3125 | 71 | 54
2018-09-03 08:00 | 35 | 35 |  |  | 43346.3333 | 67 | 51
2018-09-03 08:30 | 34 | 34 |  |  | 43346.3542 | 66 | 51
2018-09-03 09:00 | 34 | 34 |  |  | 43346.375 | 64 | 49
2018-09-03 09:30 | 33 | 33 |  |  | 43346.3958 | 61 | 47
2018-09-03 10:00 | 33 | 32 |  |  | 43346.4167 | 59 | 45
2018-09-03 10:30 | 36 | 35 |  |  | 43346.4375 | 61 | 47
2018-09-03 11:00 | 40 | 40 |  |  | 43346.4583 | 65 | 52
2018-09-03 11:30 | 42 | 41 |  |  | 43346.4792 | 65 | 52
2018-09-03 12:00 | 42 | 42 |  |  | 43346.5 | 65 | 53
2018-09-03 12:30 | 44 | 43 |  |  | 43346.5208 | 67 | 54
2018-09-03 13:00 | 42 | 41 |  |  | 43346.5417 | 67 | 54
2018-09-03 13:30 | 39 | 38 |  |  | 43346.5625 | 63 | 49
2018-09-03 14:00 | 39 | 39 |  |  | 43346.5833 | 63 | 49
2018-09-03 14:30 | 45 | 45 |  |  | 43346.6042 | 67 | 54
2018-09-03 15:00 | 42 | 42 |  |  | 43346.625 | 67 | 53
2018-09-03 15:30 | 45 | 44 |  |  | 43346.6458 | 69 | 55
2018-09-03 16:00 | 42 | 42 |  |  | 43346.6667 | 71 | 57
2018-09-03 16:30 | 42 | 41 |  |  | 43346.6875 | 71 | 56
2018-09-03 17:00 | 48 | 48 |  |  | 43346.7083 | 76 | 62
2018-09-03 17:30 | 50 | 50 |  |  | 43346.7292 | 80 | 65
2018-09-03 18:00 | 52 | 52 |  |  | 43346.75 | 83 | 67
2018-09-03 18:30 | 53 | 53 |  |  | 43346.7708 | 87 | 69
2018-09-03 19:00 | 55 | 55 |  |  | 43346.7917 | 88 | 71
2018-09-03 19:30 | 52 | 52 |  |  | 43346.8125 | 83 | 67
2018-09-03 20:00 | 52 | 52 |  |  | 43346.8333 | 83 | 67
2018-09-03 20:30 | 49 | 49 |  |  | 43346.8542 | 78 | 63
2018-09-03 21:00 | 48 | 47 |  |  | 43346.875 | 77 | 60
2018-09-03 21:30 | 42 | 42 |  |  | 43346.8958 | 73 | 54
2018-09-03 22:00 | 40 | 40 |  |  | 43346.9167 | 70 | 51
2018-09-03 22:30 | 38 | 37 |  |  | 43346.9375 | 65 | 49
2018-09-03 23:00 | 39 | 37 |  |  | 43346.9583 | 61 | 48
2018-09-03 23:30 | 36 | 34 |  |  | 43346.9792 | 59 | 44
2018-09-04 | 31 | 29 |  |  | 43347 | 54 | 38
2018-09-04 00:30 | 29 | 27 |  |  | 43347.0208 | 53 | 34
2018-09-04 01:00 | 26 | 25 |  |  | 43347.0417 | 52 | 30
2018-09-04 01:30 | 24 | 23 |  |  | 43347.0625 | 52 | 28
2018-09-04 02:00 | 25 | 24 |  |  | 43347.0833 | 51 | 30
2018-09-04 02:30 | 26 | 26 |  |  | 43347.1042 | 51 | 31
2018-09-04 03:00 | 25 | 25 |  |  | 43347.125 | 51 | 29
2018-09-04 03:30 | 25 | 25 |  |  | 43347.1458 | 51 | 30
2018-09-04 04:00 | 27 | 26 |  |  | 43347.1667 | 52 | 32
2018-09-04 04:30 | 30 | 30 |  |  | 43347.1875 | 55 | 36
2018-09-04 05:00 | 33 | 32 |  |  | 43347.2083 | 57 | 40
2018-09-04 05:30 | 35 | 34 |  |  | 43347.2292 | 56 | 41
2018-09-04 06:00 | 38 | 36 |  |  | 43347.25 | 58 | 46
2018-09-04 06:30 | 42 | 41 |  |  | 43347.2708 | 71 | 55
2018-09-04 07:00 | 43 | 43 |  |  | 43347.2917 | 77 | 60
2018-09-04 07:30 | 46 | 45 |  |  | 43347.3125 | 82 | 69
2018-09-04 08:00 | 46 | 46 |  |  | 43347.3333 | 81 | 68
2018-09-04 08:30 | 44 | 43 |  |  | 43347.3542 | 76 | 63
2018-09-04 09:00 | 41 | 40 |  |  | 43347.375 | 72 | 58
2018-09-04 09:30 | 42 | 41 |  |  | 43347.3958 | 70 | 57
2018-09-04 10:00 | 37 | 37 |  |  | 43347.4167 | 67 | 53
2018-09-04 10:30 | 35 | 34 |  |  | 43347.4375 | 64 | 50
2018-09-04 11:00 | 37 | 36 |  |  | 43347.4583 | 66 | 53
2018-09-04 11:30 | 36 | 35 |  |  | 43347.4792 | 64 | 49
2018-09-04 12:00 | 35 | 34 |  |  | 43347.5 | 65 | 50
2018-09-04 12:30 | 36 | 35 |  |  | 43347.5208 | 64 | 48
2018-09-04 13:00 | 38 | 37 |  |  | 43347.5417 | 68 | 54
2018-09-04 13:30 | 32 | 31 |  |  | 43347.5625 | 64 | 48
2018-09-04 14:00 | 33 | 32 |  |  | 43347.5833 | 65 | 49
2018-09-04 14:30 | 32 | 32 |  |  | 43347.6042 | 68 | 54
2018-09-04 15:00 | 31 | 31 |  |  | 43347.625 | 67 | 51
2018-09-04 15:30 | 36 | 35 |  |  | 43347.6458 | 71 | 57
2018-09-04 16:00 | 37 | 37 |  |  | 43347.6667 | 72 | 57
2018-09-04 16:30 | 38 | 38 |  |  | 43347.6875 | 75 | 60
2018-09-04 17:00 | 41 | 40 |  |  | 43347.7083 | 79 | 64
2018-09-04 17:30 | 43 | 43 |  |  | 43347.7292 | 83 | 67
2018-09-04 18:00 | 46 | 46 |  |  | 43347.75 | 86 | 70
2018-09-04 18:30 | 47 | 47 |  |  | 43347.7708 | 86 | 70
2018-09-04 19:00 | 48 | 47 |  |  | 43347.7917 | 87 | 70
2018-09-04 19:30 | 53 | 52 |  |  | 43347.8125 | 88 | 71
2018-09-04 20:00 | 53 | 53 |  |  | 43347.8333 | 89 | 71
2018-09-04 20:30 | 52 | 52 |  |  | 43347.8542 | 88 | 70
2018-09-04 21:00 | 47 | 47 |  |  | 43347.875 | 83 | 62
2018-09-04 21:30 | 41 | 41 |  |  | 43347.8958 | 78 | 55
2018-09-04 22:00 | 38 | 38 |  |  | 43347.9167 | 77 | 52
2018-09-04 22:30 | 36 | 36 |  |  | 43347.9375 | 75 | 50
2018-09-04 23:00 | 36 | 36 |  |  | 43347.9583 | 76 | 49
2018-09-04 23:30 | 33 | 32 |  |  | 43347.9792 | 63 | 43
2018-09-05 | 28 | 27 |  |  | 43348 | 60 | 38
2018-09-05 00:30 | 26 | 25 |  |  | 43348.0208 | 56 | 34
2018-09-05 01:00 | 25 | 24 |  |  | 43348.0417 | 53 | 31
2018-09-05 01:30 | 24 | 23 |  |  | 43348.0625 | 53 | 29
2018-09-05 02:00 | 25 | 24 |  |  | 43348.0833 | 54 | 30
2018-09-05 02:30 | 27 | 26 |  |  | 43348.1042 | 55 | 32
2018-09-05 03:00 | 29 | 28 |  |  | 43348.125 | 54 | 36
2018-09-05 03:30 | 29 | 28 |  |  | 43348.1458 | 55 | 37
2018-09-05 04:00 | 30 | 29 |  |  | 43348.1667 | 56 | 37
2018-09-05 04:30 | 31 | 30 |  |  | 43348.1875 | 56 | 38
2018-09-05 05:00 | 34 | 33 |  |  | 43348.2083 | 58 | 40
2018-09-05 05:30 | 37 | 36 |  |  | 43348.2292 | 61 | 45
2018-09-05 06:00 | 41 | 39 |  |  | 43348.25 | 61 | 48
2018-09-05 06:30 | 44 | 42 |  |  | 43348.2708 | 71 | 57
2018-09-05 07:00 | 45 | 43 |  |  | 43348.2917 | 67 | 61
2018-09-05 07:30 | 47 | 46 |  |  | 43348.3125 | 70 | 68
2018-09-05 08:00 | 46 | 46 |  |  | 43348.3333 | 70 | 69
2018-09-05 08:30 | 34 | 33 |  |  | 43348.3542 | 62 | 61
2018-09-05 09:00 | 13 | 9 |  |  | 43348.375 | 50 | 50
2018-09-05 09:30 | 16 | 11 |  |  | 43348.3958 | 49 | 49
2018-09-05 10:00 | 15 | 10 |  |  | 43348.4167 | 50 | 50
2018-09-05 10:30 | 21 | 17 |  |  | 43348.4375 | 54 | 54
2018-09-05 11:00 | 22 | 18 |  |  | 43348.4583 | 49 | 49
2018-09-05 11:30 | 22 | 18 |  |  | 43348.4792 | 52 | 52
2018-09-05 12:00 | 20 | 16 |  |  | 43348.5 | 50 | 50
2018-09-05 12:30 | 17 | 12 |  |  | 43348.5208 | 49 | 49
2018-09-05 13:00 | 15 | 10 |  |  | 43348.5417 | 50 | 50
2018-09-05 13:30 | 14 | 9 |  |  | 43348.5625 | 45 | 45
2018-09-05 14:00 | 20 | 16 |  |  | 43348.5833 | 46 | 46
2018-09-05 14:30 | 26 | 22 |  |  | 43348.6042 | 53 | 53
2018-09-05 15:00 | 23 | 20 |  |  | 43348.625 | 54 | 54
2018-09-05 15:30 | 20 | 17 |  |  | 43348.6458 | 52 | 52
2018-09-05 16:00 | 22 | 19 |  |  | 43348.6667 | 58 | 57
2018-09-05 16:30 | 20 | 17 |  |  | 43348.6875 | 55 | 55
2018-09-05 17:00 | 22 | 20 |  |  | 43348.7083 | 60 | 60
2018-09-05 17:30 | 24 | 21 |  |  | 43348.7292 | 61 | 61
2018-09-05 18:00 | 32 | 25 |  |  | 43348.75 | 65 | 65
2018-09-05 18:30 | 30 | 24 |  |  | 43348.7708 | 65 | 65
2018-09-05 19:00 | 31 | 25 |  |  | 43348.7917 | 66 | 66
2018-09-05 19:30 | 33 | 27 |  |  | 43348.8125 | 66 | 65
2018-09-05 20:00 | 34 | 28 |  |  | 43348.8333 | 65 | 65
2018-09-05 20:30 | 32 | 25 |  |  | 43348.8542 | 63 | 63
2018-09-05 21:00 | 28 | 19 |  |  | 43348.875 | 57 | 56
2018-09-05 21:30 | 19 | 15 |  |  | 43348.8958 | 52 | 51
2018-09-05 22:00 | 19 | 16 |  |  | 43348.9167 | 52 | 50
2018-09-05 22:30 | 19 | 16 |  |  | 43348.9375 | 51 | 50
2018-09-05 23:00 | 19 | 15 |  |  | 43348.9583 | 48 | 46
2018-09-05 23:30 | 13 | 10 |  |  | 43348.9792 | 41 | 39
2018-09-06 | 8 | 4 |  |  | 43349 | 34 | 32
2018-09-06 00:30 | 6 | 3 |  |  | 43349.0208 | 32 | 29
2018-09-06 01:00 | 6 | 4 |  |  | 43349.0417 | 31 | 27
2018-09-06 01:30 | 5 | 2 |  |  | 43349.0625 | 28 | 25
2018-09-06 02:00 | 11 | 8 |  |  | 43349.0833 | 33 | 30
2018-09-06 02:30 | 8 | 6 |  |  | 43349.1042 | 30 | 28
2018-09-06 03:00 | 5 | 2 |  |  | 43349.125 | 27 | 24
2018-09-06 03:30 | 4 | 1 |  |  | 43349.1458 | 26 | 23
2018-09-06 04:00 | 4 | 1 |  |  | 43349.1667 | 24 | 21
2018-09-06 04:30 | 7 | 4 |  |  | 43349.1875 | 29 | 26
2018-09-06 05:00 | 10 | 7 |  |  | 43349.2083 | 31 | 29
2018-09-06 05:30 | 16 | 12 |  |  | 43349.2292 | 36 | 34
2018-09-06 06:00 | 14 | 10 |  |  | 43349.25 | 37 | 35
2018-09-06 06:30 | 17 | 11 |  |  | 43349.2708 | 45 | 44
2018-09-06 07:00 | 24 | 14 |  |  | 43349.2917 | 51 | 51
2018-09-06 07:30 | 23 | 17 |  |  | 43349.3125 | 59 | 58
2018-09-06 08:00 | 23 | 17 |  |  | 43349.3333 | 58 | 58
2018-09-06 08:30 | 17 | 12 |  |  | 43349.3542 | 54 | 54
2018-09-06 09:00 | 11 | 6 |  |  | 43349.375 | 48 | 47
2018-09-06 09:30 | 15 | 11 |  |  | 43349.3958 | 51 | 50
2018-09-06 10:00 | 19 | 16 |  |  | 43349.4167 | 54 | 54
2018-09-06 10:30 | 21 | 20 |  |  | 43349.4375 | 54 | 54
2018-09-06 11:00 | 19 | 18 |  |  | 43349.4583 | 47 | 47
2018-09-06 11:30 | 22 | 22 |  |  | 43349.4792 | 52 | 52
2018-09-06 12:00 | 14 | 14 |  |  | 43349.5 | 54 | 54
2018-09-06 12:30 | 14 | 13 |  |  | 43349.5208 | 51 | 50
2018-09-06 13:00 | 17 | 16 |  |  | 43349.5417 | 51 | 51
2018-09-06 13:30 | 18 | 18 |  |  | 43349.5625 | 51 | 51
2018-09-06 14:00 | 14 | 12 |  |  | 43349.5833 | 49 | 49
2018-09-06 14:30 | 14 | 13 |  |  | 43349.6042 | 50 | 50
2018-09-06 15:00 | 15 | 13 |  |  | 43349.625 | 51 | 51
2018-09-06 15:30 | 21 | 19 |  |  | 43349.6458 | 56 | 56
2018-09-06 16:00 | 22 | 18 |  |  | 43349.6667 | 57 | 56
2018-09-06 16:30 | 22 | 19 |  |  | 43349.6875 | 58 | 57
2018-09-06 17:00 | 23 | 20 |  |  | 43349.7083 | 60 | 59
2018-09-06 17:30 | 31 | 27 |  |  | 43349.7292 | 66 | 64
2018-09-06 18:00 | 36 | 31 |  |  | 43349.75 | 70 | 67
2018-09-06 18:30 | 38 | 34 |  |  | 43349.7708 | 71 | 69
2018-09-06 19:00 | 41 | 36 |  |  | 43349.7917 | 73 | 71
2018-09-06 19:30 | 38 | 35 |  |  | 43349.8125 | 71 | 69
2018-09-06 20:00 | 39 | 36 |  |  | 43349.8333 | 70 | 69
2018-09-06 20:30 | 38 | 36 |  |  | 43349.8542 | 69 | 68
2018-09-06 21:00 | 35 | 31 |  |  | 43349.875 | 65 | 64
2018-09-06 21:30 | 32 | 28 |  |  | 43349.8958 | 61 | 59
2018-09-06 22:00 | 30 | 26 |  |  | 43349.9167 | 59 | 57
2018-09-06 22:30 | 28 | 24 |  |  | 43349.9375 | 58 | 56
2018-09-06 23:00 | 30 | 25 |  |  | 43349.9583 | 57 | 54
2018-09-06 23:30 | 26 | 20 |  |  | 43349.9792 | 51 | 48
2018-09-07 | 21 | 13 |  |  | 43350 | 44 | 41
2018-09-07 00:30 | 15 | 8 |  |  | 43350.0208 | 36 | 35
2018-09-07 01:00 | 14 | 6 |  |  | 43350.0417 | 31 | 31
2018-09-07 01:30 | 13 | 2 |  |  | 43350.0625 | 27 | 26
2018-09-07 02:00 | 14 | 5 |  |  | 43350.0833 | 29 | 28
2018-09-07 02:30 | 14 | 6 |  |  | 43350.1042 | 28 | 27
2018-09-07 03:00 | 16 | 8 |  |  | 43350.125 | 29 | 28
2018-09-07 03:30 | 16 | 8 |  |  | 43350.1458 | 29 | 27
2018-09-07 04:00 | 15 | 7 |  |  | 43350.1667 | 28 | 27
2018-09-07 04:30 | 15 | 9 |  |  | 43350.1875 | 30 | 29
2018-09-07 05:00 | 18 | 13 |  |  | 43350.2083 | 34 | 33
2018-09-07 05:30 | 22 | 19 |  |  | 43350.2292 | 40 | 40
2018-09-07 06:00 | 23 | 21 |  |  | 43350.25 | 45 | 45
2018-09-07 06:30 | 24 | 22 |  |  | 43350.2708 | 51 | 51
2018-09-07 07:00 | 24 | 23 |  |  | 43350.2917 | 57 | 57
2018-09-07 07:30 | 24 | 21 |  |  | 43350.3125 | 59 | 58
2018-09-07 08:00 | 26 | 18 |  |  | 43350.3333 | 61 | 57
2018-09-07 08:30 | 26 | 18 |  |  | 43350.3542 | 61 | 58
2018-09-07 09:00 | 28 | 19 |  |  | 43350.375 | 61 | 58
2018-09-07 09:30 | 28 | 20 |  |  | 43350.3958 | 63 | 61
2018-09-07 10:00 | 29 | 23 |  |  | 43350.4167 | 64 | 62
2018-09-07 10:30 | 21 | 13 |  |  | 43350.4375 | 52 | 50
2018-09-07 11:00 | 19 | 9 |  |  | 43350.4583 | 50 | 47
2018-09-07 11:30 | 20 | 10 |  |  | 43350.4792 | 50 | 47
2018-09-07 12:00 | 20 | 10 |  |  | 43350.5 | 49 | 46
2018-09-07 12:30 | 19 | 8 |  |  | 43350.5208 | 48 | 46
2018-09-07 13:00 | 20 | 5 |  |  | 43350.5417 | 46 | 43
2018-09-07 13:30 | 20 | 2 |  |  | 43350.5625 | 39 | 36
2018-09-07 14:00 | 19 | 2 |  |  | 43350.5833 | 42 | 40
2018-09-07 14:30 | 20 | 2 |  |  | 43350.6042 | 45 | 42
2018-09-07 15:00 | 20 | 7 |  |  | 43350.625 | 50 | 47
2018-09-07 15:30 | 23 | 11 |  |  | 43350.6458 | 54 | 51
2018-09-07 16:00 | 26 | 18 |  |  | 43350.6667 | 59 | 56
2018-09-07 16:30 | 24 | 13 |  |  | 43350.6875 | 56 | 52
2018-09-07 17:00 | 27 | 18 |  |  | 43350.7083 | 60 | 58
2018-09-07 17:30 | 29 | 20 |  |  | 43350.7292 | 63 | 60
2018-09-07 18:00 | 30 | 18 |  |  | 43350.75 | 62 | 59
2018-09-07 18:30 | 29 | 17 |  |  | 43350.7708 | 61 | 57
2018-09-07 19:00 | 31 | 19 |  |  | 43350.7917 | 63 | 58
2018-09-07 19:30 | 30 | 17 |  |  | 43350.8125 | 61 | 56
2018-09-07 20:00 | 28 | 16 |  |  | 43350.8333 | 58 | 54
2018-09-07 20:30 | 27 | 11 |  |  | 43350.8542 | 55 | 50
2018-09-07 21:00 | 26 | 8 |  |  | 43350.875 | 53 | 47
2018-09-07 21:30 | 26 | 7 |  |  | 43350.8958 | 51 | 44
2018-09-07 22:00 | 24 | 7 |  |  | 43350.9167 | 50 | 44
2018-09-07 22:30 | 20 | 14 |  |  | 43350.9375 | 49 | 48
2018-09-07 23:00 | 23 | 17 |  |  | 43350.9583 | 48 | 47
2018-09-07 23:30 | 23 | 15 |  |  | 43350.9792 | 47 | 46
2018-09-08 | 24 | 15 |  |  | 43351 | 46 | 44
2018-09-08 00:30 | 24 | 13 |  |  | 43351.0208 | 42 | 40
2018-09-08 01:00 | 24 | 12 |  |  | 43351.0417 | 40 | 37
2018-09-08 01:30 | 26 | 14 |  |  | 43351.0625 | 41 | 38
2018-09-08 02:00 | 24 | 14 |  |  | 43351.0833 | 39 | 37
2018-09-08 02:30 | 24 | 13 |  |  | 43351.1042 | 38 | 36
2018-09-08 03:00 | 24 | 14 |  |  | 43351.125 | 39 | 37
2018-09-08 03:30 | 25 | 15 |  |  | 43351.1458 | 38 | 37
2018-09-08 04:00 | 24 | 14 |  |  | 43351.1667 | 39 | 37
2018-09-08 04:30 | 25 | 15 |  |  | 43351.1875 | 39 | 37
2018-09-08 05:00 | 26 | 17 |  |  | 43351.2083 | 41 | 39
2018-09-08 05:30 | 25 | 16 |  |  | 43351.2292 | 40 | 39
2018-09-08 06:00 | 24 | 15 |  |  | 43351.25 | 41 | 40
2018-09-08 06:30 | 23 | 15 |  |  | 43351.2708 | 42 | 40
2018-09-08 07:00 | 23 | 14 |  |  | 43351.2917 | 43 | 42
2018-09-08 07:30 | 21 | 13 |  |  | 43351.3125 | 43 | 42
2018-09-08 08:00 | 20 | 12 |  |  | 43351.3333 | 44 | 43
2018-09-08 08:30 | 20 | 14 |  |  | 43351.3542 | 46 | 46
2018-09-08 09:00 | 21 | 17 |  |  | 43351.375 | 48 | 48
2018-09-08 09:30 | 13 | 5 |  |  | 43351.3958 | 39 | 39
2018-09-08 10:00 | 10 | 4 |  |  | 43351.4167 | 40 | 40
2018-09-08 10:30 | 14 | 11 |  |  | 43351.4375 | 44 | 44
2018-09-08 11:00 | 18 | 15 |  |  | 43351.4583 | 48 | 48
2018-09-08 11:30 | 14 | 7 |  |  | 43351.4792 | 43 | 43
2018-09-08 12:00 | 14 | 6 |  |  | 43351.5 | 41 | 41
2018-09-08 12:30 | 13 | 3 |  |  | 43351.5208 | 37 | 37
2018-09-08 13:00 | 17 | 12 |  |  | 43351.5417 | 39 | 39
2018-09-08 13:30 | 39 | 36 |  |  | 43351.5625 | 49 | 49
2018-09-08 14:00 | 43 | 40 |  |  | 43351.5833 | 52 | 52
2018-09-08 14:30 | 45 | 42 |  |  | 43351.6042 | 54 | 54
2018-09-08 15:00 | 46 | 43 |  |  | 43351.625 | 58 | 58
2018-09-08 15:30 | 43 | 40 |  |  | 43351.6458 | 53 | 53
2018-09-08 16:00 | 44 | 41 |  |  | 43351.6667 | 55 | 55
2018-09-08 16:30 | 45 | 42 |  |  | 43351.6875 | 60 | 60
2018-09-08 17:00 | 46 | 43 |  |  | 43351.7083 | 61 | 61
2018-09-08 17:30 | 46 | 44 |  |  | 43351.7292 | 61 | 61
2018-09-08 18:00 | 47 | 44 |  |  | 43351.75 | 63 | 63
2018-09-08 18:30 | 52 | 48 |  |  | 43351.7708 | 67 | 66
2018-09-08 19:00 | 54 | 50 |  |  | 43351.7917 | 69 | 68
2018-09-08 19:30 | 51 | 47 |  |  | 43351.8125 | 66 | 65
2018-09-08 20:00 | 50 | 46 |  |  | 43351.8333 | 65 | 63
2018-09-08 20:30 | 49 | 45 |  |  | 43351.8542 | 63 | 62
2018-09-08 21:00 | 46 | 42 |  |  | 43351.875 | 59 | 58
2018-09-08 21:30 | 44 | 40 |  |  | 43351.8958 | 55 | 55
2018-09-08 22:00 | 43 | 39 |  |  | 43351.9167 | 56 | 55
2018-09-08 22:30 | 44 | 39 |  |  | 43351.9375 | 57 | 55
2018-09-08 23:00 | 42 | 37 |  |  | 43351.9583 | 53 | 52
2018-09-08 23:30 | 40 | 34 |  |  | 43351.9792 | 50 | 48
2018-09-09 | 36 | 29 |  |  | 43352 | 46 | 44
2018-09-09 00:30 | 35 | 26 |  |  | 43352.0208 | 42 | 39
2018-09-09 01:00 | 34 | 25 |  |  | 43352.0417 | 39 | 37
2018-09-09 01:30 | 35 | 28 |  |  | 43352.0625 | 42 | 40
2018-09-09 02:00 | 37 | 29 |  |  | 43352.0833 | 43 | 41
2018-09-09 02:30 | 40 | 32 |  |  | 43352.1042 | 47 | 45
2018-09-09 03:00 | 40 | 32 |  |  | 43352.125 | 46 | 44
2018-09-09 03:30 | 40 | 32 |  |  | 43352.1458 | 47 | 45
2018-09-09 04:00 | 39 | 31 |  |  | 43352.1667 | 45 | 43
2018-09-09 04:30 | 39 | 31 |  |  | 43352.1875 | 45 | 42
2018-09-09 05:00 | 38 | 29 |  |  | 43352.2083 | 44 | 41
2018-09-09 05:30 | 38 | 30 |  |  | 43352.2292 | 45 | 43
2018-09-09 06:00 | 37 | 29 |  |  | 43352.25 | 45 | 43
2018-09-09 06:30 | 37 | 30 |  |  | 43352.2708 | 46 | 44
2018-09-09 07:00 | 37 | 30 |  |  | 43352.2917 | 46 | 45
2018-09-09 07:30 | 35 | 28 |  |  | 43352.3125 | 43 | 42
2018-09-09 08:00 | 33 | 25 |  |  | 43352.3333 | 41 | 40
2018-09-09 08:30 | 35 | 28 |  |  | 43352.3542 | 44 | 43
2018-09-09 09:00 | 34 | 27 |  |  | 43352.375 | 44 | 44
2018-09-09 09:30 | 33 | 27 |  |  | 43352.3958 | 43 | 43
2018-09-09 10:00 | 32 | 26 |  |  | 43352.4167 | 42 | 41
2018-09-09 10:30 | 32 | 26 |  |  | 43352.4375 | 41 | 41
2018-09-09 11:00 | 31 | 25 |  |  | 43352.4583 | 40 | 40
2018-09-09 11:30 | 30 | 24 |  |  | 43352.4792 | 38 | 38
2018-09-09 12:00 | 32 | 25 |  |  | 43352.5 | 40 | 40
2018-09-09 12:30 | 32 | 26 |  |  | 43352.5208 | 40 | 40
2018-09-09 13:00 | 32 | 26 |  |  | 43352.5417 | 41 | 40
2018-09-09 13:30 | 33 | 27 |  |  | 43352.5625 | 42 | 41
2018-09-09 14:00 | 34 | 29 |  |  | 43352.5833 | 43 | 43
2018-09-09 14:30 | 35 | 30 |  |  | 43352.6042 | 44 | 44
2018-09-09 15:00 | 38 | 34 |  |  | 43352.625 | 49 | 49
2018-09-09 15:30 | 41 | 37 |  |  | 43352.6458 | 52 | 52
2018-09-09 16:00 | 44 | 40 |  |  | 43352.6667 | 56 | 56
2018-09-09 16:30 | 48 | 44 |  |  | 43352.6875 | 61 | 61
2018-09-09 17:00 | 52 | 49 |  |  | 43352.7083 | 65 | 65
2018-09-09 17:30 | 50 | 46 |  |  | 43352.7292 | 63 | 63
2018-09-09 18:00 | 52 | 49 |  |  | 43352.75 | 66 | 65
2018-09-09 18:30 | 53 | 51 |  |  | 43352.7708 | 69 | 68
2018-09-09 19:00 | 55 | 52 |  |  | 43352.7917 | 71 | 71
2018-09-09 19:30 | 54 | 51 |  |  | 43352.8125 | 70 | 70
2018-09-09 20:00 | 52 | 49 |  |  | 43352.8333 | 68 | 67
2018-09-09 20:30 | 53 | 50 |  |  | 43352.8542 | 68 | 68
2018-09-09 21:00 | 51 | 48 |  |  | 43352.875 | 65 | 65
2018-09-09 21:30 | 49 | 44 |  |  | 43352.8958 | 62 | 61
2018-09-09 22:00 | 48 | 44 |  |  | 43352.9167 | 62 | 61
2018-09-09 22:30 | 46 | 42 |  |  | 43352.9375 | 61 | 60
2018-09-09 23:00 | 46 | 41 |  |  | 43352.9583 | 58 | 57
2018-09-09 23:30 | 43 | 38 |  |  | 43352.9792 | 55 | 53
2018-09-10 | 39 | 32 |  |  | 43353 | 48 | 47
2018-09-10 00:30 | 39 | 32 |  |  | 43353.0208 | 48 | 46
2018-09-10 01:00 | 38 | 30 |  |  | 43353.0417 | 46 | 44
2018-09-10 01:30 | 38 | 30 |  |  | 43353.0625 | 45 | 42
2018-09-10 02:00 | 37 | 27 |  |  | 43353.0833 | 42 | 39
2018-09-10 02:30 | 37 | 28 |  |  | 43353.1042 | 42 | 39
2018-09-10 03:00 | 36 | 26 |  |  | 43353.125 | 40 | 37
2018-09-10 03:30 | 35 | 26 |  |  | 43353.1458 | 40 | 37
2018-09-10 04:00 | 36 | 27 |  |  | 43353.1667 | 41 | 38
2018-09-10 04:30 | 37 | 30 |  |  | 43353.1875 | 43 | 41
2018-09-10 05:00 | 38 | 32 |  |  | 43353.2083 | 43 | 41
2018-09-10 05:30 | 40 | 36 |  |  | 43353.2292 | 48 | 47
2018-09-10 06:00 | 43 | 39 |  |  | 43353.25 | 53 | 52
2018-09-10 06:30 | 47 | 44 |  |  | 43353.2708 | 60 | 59
2018-09-10 07:00 | 49 | 47 |  |  | 43353.2917 | 66 | 66
2018-09-10 07:30 | 49 | 48 |  |  | 43353.3125 | 69 | 69
2018-09-10 08:00 | 46 | 44 |  |  | 43353.3333 | 68 | 68
2018-09-10 08:30 | 43 | 41 |  |  | 43353.3542 | 66 | 66
2018-09-10 09:00 | 41 | 39 |  |  | 43353.375 | 63 | 63
2018-09-10 09:30 | 39 | 38 |  |  | 43353.3958 | 62 | 61
2018-09-10 10:00 | 39 | 38 |  |  | 43353.4167 | 61 | 60
2018-09-10 10:30 | 39 | 38 |  |  | 43353.4375 | 60 | 60
2018-09-10 11:00 | 40 | 39 |  |  | 43353.4583 | 61 | 60
2018-09-10 11:30 | 41 | 41 |  |  | 43353.4792 | 62 | 62
2018-09-10 12:00 | 44 | 43 |  |  | 43353.5 | 65 | 65
2018-09-10 12:30 | 43 | 43 |  |  | 43353.5208 | 64 | 64
2018-09-10 13:00 | 43 | 43 |  |  | 43353.5417 | 64 | 64
2018-09-10 13:30 | 43 | 43 |  |  | 43353.5625 | 64 | 63
2018-09-10 14:00 | 42 | 41 |  |  | 43353.5833 | 62 | 62
2018-09-10 14:30 | 42 | 42 |  |  | 43353.6042 | 63 | 62
2018-09-10 15:00 | 44 | 43 |  |  | 43353.625 | 65 | 65
2018-09-10 15:30 | 44 | 43 |  |  | 43353.6458 | 64 | 64
2018-09-10 16:00 | 47 | 46 |  |  | 43353.6667 | 67 | 67
2018-09-10 16:30 | 48 | 47 |  |  | 43353.6875 | 67 | 67
2018-09-10 17:00 | 52 | 51 |  |  | 43353.7083 | 71 | 71
2018-09-10 17:30 | 57 | 55 |  |  | 43353.7292 | 74 | 74
2018-09-10 18:00 | 61 | 58 |  |  | 43353.75 | 76 | 75
2018-09-10 18:30 | 63 | 57 |  |  | 43353.7708 | 76 | 73
2018-09-10 19:00 | 63 | 57 |  |  | 43353.7917 | 77 | 73
2018-09-10 19:30 | 62 | 56 |  |  | 43353.8125 | 75 | 71
2018-09-10 20:00 | 57 | 55 |  |  | 43353.8333 | 70 | 70
2018-09-10 20:30 | 55 | 53 |  |  | 43353.8542 | 68 | 68
2018-09-10 21:00 | 51 | 49 |  |  | 43353.875 | 63 | 63
2018-09-10 21:30 | 48 | 46 |  |  | 43353.8958 | 60 | 59
2018-09-10 22:00 | 45 | 42 |  |  | 43353.9167 | 56 | 56
2018-09-10 22:30 | 44 | 41 |  |  | 43353.9375 | 57 | 56
2018-09-10 23:00 | 41 | 38 |  |  | 43353.9583 | 52 | 51
2018-09-10 23:30 | 37 | 33 |  |  | 43353.9792 | 47 | 46
2018-09-11 | 33 | 28 |  |  | 43354 | 42 | 42
2018-09-11 00:30 | 35 | 28 |  |  | 43354.0208 | 42 | 41
2018-09-11 01:00 | 35 | 28 |  |  | 43354.0417 | 41 | 39
2018-09-11 01:30 | 37 | 30 |  |  | 43354.0625 | 42 | 40
2018-09-11 02:00 | 36 | 29 |  |  | 43354.0833 | 41 | 39
2018-09-11 02:30 | 35 | 27 |  |  | 43354.1042 | 40 | 38
2018-09-11 03:00 | 34 | 26 |  |  | 43354.125 | 39 | 36
2018-09-11 03:30 | 37 | 30 |  |  | 43354.1458 | 43 | 40
2018-09-11 04:00 | 36 | 29 |  |  | 43354.1667 | 40 | 38
2018-09-11 04:30 | 38 | 32 |  |  | 43354.1875 | 44 | 42
2018-09-11 05:00 | 40 | 34 |  |  | 43354.2083 | 46 | 45
2018-09-11 05:30 | 42 | 38 |  |  | 43354.2292 | 50 | 48
2018-09-11 06:00 | 47 | 44 |  |  | 43354.25 | 57 | 56
2018-09-11 06:30 | 49 | 47 |  |  | 43354.2708 | 62 | 62
2018-09-11 07:00 | 47 | 45 |  |  | 43354.2917 | 64 | 64
2018-09-11 07:30 | 49 | 47 |  |  | 43354.3125 | 68 | 68
2018-09-11 08:00 | 47 | 45 |  |  | 43354.3333 | 67 | 67
2018-09-11 08:30 | 44 | 42 |  |  | 43354.3542 | 65 | 65
2018-09-11 09:00 | 44 | 42 |  |  | 43354.375 | 66 | 66
2018-09-11 09:30 | 43 | 42 |  |  | 43354.3958 | 64 | 64
2018-09-11 10:00 | 42 | 41 |  |  | 43354.4167 | 64 | 63
2018-09-11 10:30 | 39 | 38 |  |  | 43354.4375 | 62 | 62
2018-09-11 11:00 | 41 | 40 |  |  | 43354.4583 | 63 | 62
2018-09-11 11:30 | 44 | 43 |  |  | 43354.4792 | 64 | 64
2018-09-11 12:00 | 45 | 45 |  |  | 43354.5 | 66 | 66
2018-09-11 12:30 | 43 | 42 |  |  | 43354.5208 | 64 | 64
2018-09-11 13:00 | 45 | 44 |  |  | 43354.5417 | 65 | 65
2018-09-11 13:30 | 49 | 48 |  |  | 43354.5625 | 69 | 68
2018-09-11 14:00 | 50 | 49 |  |  | 43354.5833 | 70 | 70
2018-09-11 14:30 | 50 | 49 |  |  | 43354.6042 | 72 | 71
2018-09-11 15:00 | 48 | 47 |  |  | 43354.625 | 70 | 70
2018-09-11 15:30 | 47 | 46 |  |  | 43354.6458 | 67 | 67
2018-09-11 16:00 | 49 | 46 |  |  | 43354.6667 | 67 | 67
2018-09-11 16:30 | 53 | 49 |  |  | 43354.6875 | 71 | 69
2018-09-11 17:00 | 55 | 50 |  |  | 43354.7083 | 71 | 69
2018-09-11 17:30 | 56 | 51 |  |  | 43354.7292 | 73 | 70
2018-09-11 18:00 | 59 | 54 |  |  | 43354.75 | 75 | 73
2018-09-11 18:30 | 60 | 55 |  |  | 43354.7708 | 76 | 73
2018-09-11 19:00 | 61 | 57 |  |  | 43354.7917 | 78 | 74
2018-09-11 19:30 | 60 | 55 |  |  | 43354.8125 | 76 | 72
2018-09-11 20:00 | 58 | 55 |  |  | 43354.8333 | 72 | 71
2018-09-11 20:30 | 56 | 54 |  |  | 43354.8542 | 70 | 69
2018-09-11 21:00 | 52 | 50 |  |  | 43354.875 | 65 | 64
2018-09-11 21:30 | 50 | 47 |  |  | 43354.8958 | 61 | 60
2018-09-11 22:00 | 51 | 47 |  |  | 43354.9167 | 63 | 62
2018-09-11 22:30 | 49 | 45 |  |  | 43354.9375 | 62 | 60
2018-09-11 23:00 | 48 | 43 |  |  | 43354.9583 | 58 | 57
2018-09-11 23:30 | 45 | 40 |  |  | 43354.9792 | 56 | 54
2018-09-12 | 41 | 34 |  |  | 43355 | 50 | 48
2018-09-12 00:30 | 39 | 32 |  |  | 43355.0208 | 47 | 44
2018-09-12 01:00 | 39 | 31 |  |  | 43355.0417 | 45 | 42
2018-09-12 01:30 | 40 | 31 |  |  | 43355.0625 | 46 | 42
2018-09-12 02:00 | 39 | 30 |  |  | 43355.0833 | 44 | 40
2018-09-12 02:30 | 39 | 29 |  |  | 43355.1042 | 44 | 40
2018-09-12 03:00 | 37 | 27 |  |  | 43355.125 | 42 | 37
2018-09-12 03:30 | 37 | 28 |  |  | 43355.1458 | 41 | 37
2018-09-12 04:00 | 37 | 29 |  |  | 43355.1667 | 41 | 39
2018-09-12 04:30 | 39 | 32 |  |  | 43355.1875 | 45 | 42
2018-09-12 05:00 | 42 | 35 |  |  | 43355.2083 | 47 | 45
2018-09-12 05:30 | 43 | 38 |  |  | 43355.2292 | 51 | 49
2018-09-12 06:00 | 46 | 42 |  |  | 43355.25 | 55 | 54
2018-09-12 06:30 | 48 | 45 |  |  | 43355.2708 | 61 | 61
2018-09-12 07:00 | 45 | 43 |  |  | 43355.2917 | 62 | 62
2018-09-12 07:30 | 51 | 49 |  |  | 43355.3125 | 68 | 68
2018-09-12 08:00 | 53 | 52 |  |  | 43355.3333 | 69 | 69
2018-09-12 08:30 | 49 | 48 |  |  | 43355.3542 | 67 | 67
2018-09-12 09:00 | 50 | 49 |  |  | 43355.375 | 67 | 67
2018-09-12 09:30 | 50 | 49 |  |  | 43355.3958 | 69 | 68
2018-09-12 10:00 | 52 | 50 |  |  | 43355.4167 | 72 | 72
2018-09-12 10:30 | 57 | 56 |  |  | 43355.4375 | 73 | 73
2018-09-12 11:00 | 55 | 55 |  |  | 43355.4583 | 72 | 72
2018-09-12 11:30 | 54 | 53 |  |  | 43355.4792 | 69 | 69
2018-09-12 12:00 | 53 | 52 |  |  | 43355.5 | 68 | 68
2018-09-12 12:30 | 55 | 55 |  |  | 43355.5208 | 71 | 70
2018-09-12 13:00 | 54 | 53 |  |  | 43355.5417 | 67 | 67
2018-09-12 13:30 | 54 | 53 |  |  | 43355.5625 | 71 | 71
2018-09-12 14:00 | 55 | 54 |  |  | 43355.5833 | 71 | 71
2018-09-12 14:30 | 56 | 55 |  |  | 43355.6042 | 72 | 71
2018-09-12 15:00 | 57 | 56 |  |  | 43355.625 | 73 | 73
2018-09-12 15:30 | 57 | 56 |  |  | 43355.6458 | 74 | 74
2018-09-12 16:00 | 58 | 57 |  |  | 43355.6667 | 74 | 74
2018-09-12 16:30 | 58 | 57 |  |  | 43355.6875 | 75 | 75
2018-09-12 17:00 | 63 | 61 |  |  | 43355.7083 | 78 | 78
2018-09-12 17:30 | 65 | 63 |  |  | 43355.7292 | 79 | 79
2018-09-12 18:00 | 67 | 64 |  |  | 43355.75 | 80 | 80
2018-09-12 18:30 | 69 | 66 |  |  | 43355.7708 | 81 | 81
2018-09-12 19:00 | 69 | 67 |  |  | 43355.7917 | 81 | 80
2018-09-12 19:30 | 68 | 65 |  |  | 43355.8125 | 79 | 78
2018-09-12 20:00 | 66 | 64 |  |  | 43355.8333 | 76 | 76
2018-09-12 20:30 | 64 | 62 |  |  | 43355.8542 | 75 | 75
2018-09-12 21:00 | 61 | 59 |  |  | 43355.875 | 70 | 70
2018-09-12 21:30 | 57 | 54 |  |  | 43355.8958 | 65 | 64
2018-09-12 22:00 | 54 | 51 |  |  | 43355.9167 | 64 | 63
2018-09-12 22:30 | 51 | 48 |  |  | 43355.9375 | 61 | 60
2018-09-12 23:00 | 48 | 46 |  |  | 43355.9583 | 57 | 57
2018-09-12 23:30 | 43 | 40 |  |  | 43355.9792 | 53 | 52
2018-09-13 | 41 | 37 |  |  | 43356 | 49 | 48
2018-09-13 00:30 | 40 | 35 |  |  | 43356.0208 | 46 | 44
2018-09-13 01:00 | 38 | 32 |  |  | 43356.0417 | 42 | 41
2018-09-13 01:30 | 37 | 29 |  |  | 43356.0625 | 40 | 38
2018-09-13 02:00 | 37 | 30 |  |  | 43356.0833 | 40 | 38
2018-09-13 02:30 | 39 | 32 |  |  | 43356.1042 | 42 | 40
2018-09-13 03:00 | 39 | 32 |  |  | 43356.125 | 42 | 40
2018-09-13 03:30 | 43 | 36 |  |  | 43356.1458 | 47 | 44
2018-09-13 04:00 | 43 | 36 |  |  | 43356.1667 | 46 | 44
2018-09-13 04:30 | 43 | 37 |  |  | 43356.1875 | 47 | 45
2018-09-13 05:00 | 44 | 39 |  |  | 43356.2083 | 49 | 47
2018-09-13 05:30 | 49 | 45 |  |  | 43356.2292 | 54 | 52
2018-09-13 06:00 | 52 | 49 |  |  | 43356.25 | 60 | 59
2018-09-13 06:30 | 54 | 52 |  |  | 43356.2708 | 65 | 65
2018-09-13 07:00 | 56 | 54 |  |  | 43356.2917 | 69 | 69
2018-09-13 07:30 | 59 | 57 |  |  | 43356.3125 | 75 | 75
2018-09-13 08:00 | 55 | 53 |  |  | 43356.3333 | 73 | 73
2018-09-13 08:30 | 52 | 50 |  |  | 43356.3542 | 69 | 69
2018-09-13 09:00 | 51 | 49 |  |  | 43356.375 | 69 | 69
2018-09-13 09:30 | 51 | 50 |  |  | 43356.3958 | 70 | 70
2018-09-13 10:00 | 52 | 51 |  |  | 43356.4167 | 71 | 71
2018-09-13 10:30 | 51 | 51 |  |  | 43356.4375 | 70 | 70
2018-09-13 11:00 | 54 | 53 |  |  | 43356.4583 | 72 | 72
2018-09-13 11:30 | 53 | 53 |  |  | 43356.4792 | 73 | 72
2018-09-13 12:00 | 50 | 50 |  |  | 43356.5 | 71 | 71
2018-09-13 12:30 | 53 | 53 |  |  | 43356.5208 | 74 | 73
2018-09-13 13:00 | 54 | 54 |  |  | 43356.5417 | 74 | 74
2018-09-13 13:30 | 55 | 54 |  |  | 43356.5625 | 76 | 75
2018-09-13 14:00 | 56 | 56 |  |  | 43356.5833 | 77 | 76
2018-09-13 14:30 | 58 | 58 |  |  | 43356.6042 | 78 | 78
2018-09-13 15:00 | 59 | 58 |  |  | 43356.625 | 79 | 78
2018-09-13 15:30 | 58 | 57 |  |  | 43356.6458 | 77 | 76
2018-09-13 16:00 | 61 | 60 |  |  | 43356.6667 | 80 | 80
2018-09-13 16:30 | 65 | 61 |  |  | 43356.6875 | 82 | 80
2018-09-13 17:00 | 69 | 65 |  |  | 43356.7083 | 85 | 82
2018-09-13 17:30 | 71 | 67 |  |  | 43356.7292 | 87 | 84
2018-09-13 18:00 | 74 | 69 |  |  | 43356.75 | 88 | 85
2018-09-13 18:30 | 76 | 71 |  |  | 43356.7708 | 89 | 85
2018-09-13 19:00 | 75 | 70 |  |  | 43356.7917 | 88 | 84
2018-09-13 19:30 | 72 | 70 |  |  | 43356.8125 | 84 | 83
2018-09-13 20:00 | 70 | 69 |  |  | 43356.8333 | 83 | 83
2018-09-13 20:30 | 69 | 68 |  |  | 43356.8542 | 81 | 81
2018-09-13 21:00 | 65 | 64 |  |  | 43356.875 | 75 | 75
2018-09-13 21:30 | 61 | 59 |  |  | 43356.8958 | 70 | 69
2018-09-13 22:00 | 59 | 55 |  |  | 43356.9167 | 68 | 67
2018-09-13 22:30 | 56 | 54 |  |  | 43356.9375 | 66 | 66
2018-09-13 23:00 | 53 | 51 |  |  | 43356.9583 | 62 | 62
2018-09-13 23:30 | 49 | 47 |  |  | 43356.9792 | 59 | 59
2018-09-14 | 46 | 42 |  |  | 43357 | 56 | 55
2018-09-14 00:30 | 46 | 42 |  |  | 43357.0208 | 55 | 54
2018-09-14 01:00 | 47 | 42 |  |  | 43357.0417 | 54 | 52
2018-09-14 01:30 | 47 | 41 |  |  | 43357.0625 | 52 | 50
2018-09-14 02:00 | 45 | 39 |  |  | 43357.0833 | 50 | 48
2018-09-14 02:30 | 44 | 39 |  |  | 43357.1042 | 50 | 48
2018-09-14 03:00 | 44 | 39 |  |  | 43357.125 | 50 | 48
2018-09-14 03:30 | 44 | 38 |  |  | 43357.1458 | 51 | 48
2018-09-14 04:00 | 45 | 40 |  |  | 43357.1667 | 51 | 49
2018-09-14 04:30 | 45 | 40 |  |  | 43357.1875 | 51 | 50
2018-09-14 05:00 | 48 | 43 |  |  | 43357.2083 | 55 | 53
2018-09-14 05:30 | 52 | 49 |  |  | 43357.2292 | 59 | 59
2018-09-14 06:00 | 57 | 55 |  |  | 43357.25 | 66 | 66
2018-09-14 06:30 | 62 | 61 |  |  | 43357.2708 | 75 | 75
2018-09-14 07:00 | 62 | 61 |  |  | 43357.2917 | 77 | 77
2018-09-14 07:30 | 63 | 62 |  |  | 43357.3125 | 80 | 80
2018-09-14 08:00 | 61 | 60 |  |  | 43357.3333 | 80 | 80
2018-09-14 08:30 | 56 | 55 |  |  | 43357.3542 | 78 | 78
2018-09-14 09:00 | 48 | 47 |  |  | 43357.375 | 74 | 74
2018-09-14 09:30 | 50 | 48 |  |  | 43357.3958 | 76 | 76
2018-09-14 10:00 | 51 | 50 |  |  | 43357.4167 | 76 | 76
2018-09-14 10:30 | 48 | 47 |  |  | 43357.4375 | 74 | 73
2018-09-14 11:00 | 47 | 47 |  |  | 43357.4583 | 74 | 73
2018-09-14 11:30 | 46 | 45 |  |  | 43357.4792 | 72 | 72
2018-09-14 12:00 | 47 | 46 |  |  | 43357.5 | 71 | 71
2018-09-14 12:30 | 43 | 42 |  |  | 43357.5208 | 68 | 68
2018-09-14 13:00 | 42 | 41 |  |  | 43357.5417 | 67 | 66
2018-09-14 13:30 | 43 | 42 |  |  | 43357.5625 | 67 | 66
2018-09-14 14:00 | 44 | 43 |  |  | 43357.5833 | 67 | 67
2018-09-14 14:30 | 45 | 44 |  |  | 43357.6042 | 67 | 66
2018-09-14 15:00 | 44 | 43 |  |  | 43357.625 | 66 | 65
2018-09-14 15:30 | 46 | 45 |  |  | 43357.6458 | 67 | 67
2018-09-14 16:00 | 49 | 48 |  |  | 43357.6667 | 71 | 71
2018-09-14 16:30 | 52 | 50 |  |  | 43357.6875 | 74 | 73
2018-09-14 17:00 | 54 | 52 |  |  | 43357.7083 | 75 | 75
2018-09-14 17:30 | 56 | 54 |  |  | 43357.7292 | 76 | 76
2018-09-14 18:00 | 54 | 52 |  |  | 43357.75 | 73 | 73
2018-09-14 18:30 | 54 | 52 |  |  | 43357.7708 | 72 | 72
2018-09-14 19:00 | 55 | 52 |  |  | 43357.7917 | 73 | 73
2018-09-14 19:30 | 54 | 52 |  |  | 43357.8125 | 72 | 72
2018-09-14 20:00 | 54 | 52 |  |  | 43357.8333 | 71 | 71
2018-09-14 20:30 | 55 | 52 |  |  | 43357.8542 | 71 | 71
2018-09-14 21:00 | 52 | 50 |  |  | 43357.875 | 67 | 67
2018-09-14 21:30 | 49 | 47 |  |  | 43357.8958 | 64 | 64
2018-09-14 22:00 | 49 | 47 |  |  | 43357.9167 | 64 | 64
2018-09-14 22:30 | 47 | 44 |  |  | 43357.9375 | 62 | 62
2018-09-14 23:00 | 48 | 44 |  |  | 43357.9583 | 61 | 61
2018-09-14 23:30 | 46 | 42 |  |  | 43357.9792 | 60 | 59
2018-09-15 | 44 | 38 |  |  | 43358 | 56 | 55
2018-09-15 00:30 | 41 | 35 |  |  | 43358.0208 | 51 | 50
2018-09-15 01:00 | 38 | 31 |  |  | 43358.0417 | 47 | 46
2018-09-15 01:30 | 38 | 30 |  |  | 43358.0625 | 45 | 43
2018-09-15 02:00 | 37 | 29 |  |  | 43358.0833 | 44 | 42
2018-09-15 02:30 | 36 | 27 |  |  | 43358.1042 | 42 | 40
2018-09-15 03:00 | 35 | 26 |  |  | 43358.125 | 42 | 40
2018-09-15 03:30 | 35 | 26 |  |  | 43358.1458 | 41 | 39
2018-09-15 04:00 | 28 | 27 |  |  | 43358.1667 | 41 | 40
2018-09-15 04:30 | 29 | 29 |  |  | 43358.1875 | 42 | 41
2018-09-15 05:00 | 30 | 30 |  |  | 43358.2083 | 43 | 42
2018-09-15 05:30 | 32 | 31 |  |  | 43358.2292 | 45 | 44
2018-09-15 06:00 | 31 | 30 |  |  | 43358.25 | 44 | 43
2018-09-15 06:30 | 32 | 31 |  |  | 43358.2708 | 46 | 46
2018-09-15 07:00 | 31 | 31 |  |  | 43358.2917 | 47 | 46
2018-09-15 07:30 | 30 | 30 |  |  | 43358.3125 | 47 | 47
2018-09-15 08:00 | 29 | 29 |  |  | 43358.3333 | 46 | 46
2018-09-15 08:30 | 31 | 31 |  |  | 43358.3542 | 48 | 48
2018-09-15 09:00 | 31 | 31 |  |  | 43358.375 | 48 | 47
2018-09-15 09:30 | 31 | 31 |  |  | 43358.3958 | 47 | 47
2018-09-15 10:00 | 28 | 27 |  |  | 43358.4167 | 43 | 43
2018-09-15 10:30 | 30 | 29 |  |  | 43358.4375 | 45 | 45
2018-09-15 11:00 | 30 | 30 |  |  | 43358.4583 | 45 | 45
2018-09-15 11:30 | 28 | 28 |  |  | 43358.4792 | 43 | 43
2018-09-15 12:00 | 27 | 27 |  |  | 43358.5 | 41 | 41
2018-09-15 12:30 | 26 | 26 |  |  | 43358.5208 | 42 | 41
2018-09-15 13:00 | 26 | 26 |  |  | 43358.5417 | 41 | 41
2018-09-15 13:30 | 28 | 28 |  |  | 43358.5625 | 42 | 42
2018-09-15 14:00 | 27 | 27 |  |  | 43358.5833 | 41 | 41
2018-09-15 14:30 | 30 | 30 |  |  | 43358.6042 | 44 | 44
2018-09-15 15:00 | 32 | 32 |  |  | 43358.625 | 46 | 46
2018-09-15 15:30 | 31 | 31 |  |  | 43358.6458 | 47 | 47
2018-09-15 16:00 | 34 | 34 |  |  | 43358.6667 | 51 | 51
2018-09-15 16:30 | 36 | 36 |  |  | 43358.6875 | 53 | 52
2018-09-15 17:00 | 39 | 39 |  |  | 43358.7083 | 56 | 56
2018-09-15 17:30 | 41 | 41 |  |  | 43358.7292 | 57 | 57
2018-09-15 18:00 | 41 | 41 |  |  | 43358.75 | 59 | 59
2018-09-15 18:30 | 45 | 45 |  |  | 43358.7708 | 63 | 63
2018-09-15 19:00 | 46 | 46 |  |  | 43358.7917 | 65 | 65
2018-09-15 19:30 | 45 | 45 |  |  | 43358.8125 | 63 | 62
2018-09-15 20:00 | 46 | 46 |  |  | 43358.8333 | 64 | 63
2018-09-15 20:30 | 46 | 46 |  |  | 43358.8542 | 64 | 63
2018-09-15 21:00 | 42 | 42 |  |  | 43358.875 | 59 | 58
2018-09-15 21:30 | 42 | 42 |  |  | 43358.8958 | 57 | 56
2018-09-15 22:00 | 39 | 39 |  |  | 43358.9167 | 55 | 55
2018-09-15 22:30 | 41 | 41 |  |  | 43358.9375 | 58 | 58
2018-09-15 23:00 | 41 | 41 |  |  | 43358.9583 | 57 | 56
2018-09-15 23:30 | 38 | 38 |  |  | 43358.9792 | 53 | 52
2018-09-16 | 34 | 34 |  |  | 43359 | 49 | 48
2018-09-16 00:30 | 32 | 32 |  |  | 43359.0208 | 46 | 45
2018-09-16 01:00 | 31 | 30 |  |  | 43359.0417 | 45 | 43
2018-09-16 01:30 | 31 | 31 |  |  | 43359.0625 | 44 | 42
2018-09-16 02:00 | 29 | 29 |  |  | 43359.0833 | 42 | 40
2018-09-16 02:30 | 28 | 27 |  |  | 43359.1042 | 41 | 39
2018-09-16 03:00 | 28 | 27 |  |  | 43359.125 | 41 | 39
2018-09-16 03:30 | 26 | 25 |  |  | 43359.1458 | 38 | 36
2018-09-16 04:00 | 27 | 26 |  |  | 43359.1667 | 40 | 38
2018-09-16 04:30 | 26 | 26 |  |  | 43359.1875 | 41 | 38
2018-09-16 05:00 | 26 | 26 |  |  | 43359.2083 | 40 | 37
2018-09-16 05:30 | 28 | 28 |  |  | 43359.2292 | 42 | 40
2018-09-16 06:00 | 29 | 28 |  |  | 43359.25 | 43 | 41
2018-09-16 06:30 | 28 | 27 |  |  | 43359.2708 | 43 | 41
2018-09-16 07:00 | 26 | 25 |  |  | 43359.2917 | 42 | 40
2018-09-16 07:30 | 24 | 23 |  |  | 43359.3125 | 41 | 39
2018-09-16 08:00 | 24 | 23 |  |  | 43359.3333 | 41 | 39
2018-09-16 08:30 | 24 | 24 |  |  | 43359.3542 | 41 | 40
2018-09-16 09:00 | 25 | 25 |  |  | 43359.375 | 42 | 41
2018-09-16 09:30 | 25 | 25 |  |  | 43359.3958 | 42 | 41
2018-09-16 10:00 | 32 | 32 |  |  | 43359.4167 | 44 | 44
2018-09-16 10:30 | 32 | 32 |  |  | 43359.4375 | 46 | 46
2018-09-16 11:00 | 26 | 26 |  |  | 43359.4583 | 40 | 39
2018-09-16 11:30 | 26 | 25 |  |  | 43359.4792 | 39 | 39
2018-09-16 12:00 | 25 | 25 |  |  | 43359.5 | 39 | 38
2018-09-16 12:30 | 24 | 24 |  |  | 43359.5208 | 38 | 38
2018-09-16 13:00 | 27 | 27 |  |  | 43359.5417 | 40 | 39
2018-09-16 13:30 | 32 | 32 |  |  | 43359.5625 | 43 | 43
2018-09-16 14:00 | 34 | 34 |  |  | 43359.5833 | 47 | 47
2018-09-16 14:30 | 33 | 33 |  |  | 43359.6042 | 46 | 46
2018-09-16 15:00 | 33 | 33 |  |  | 43359.625 | 46 | 45
2018-09-16 15:30 | 31 | 31 |  |  | 43359.6458 | 46 | 45
2018-09-16 16:00 | 33 | 33 |  |  | 43359.6667 | 48 | 48
2018-09-16 16:30 | 34 | 34 |  |  | 43359.6875 | 50 | 49
2018-09-16 17:00 | 35 | 35 |  |  | 43359.7083 | 51 | 51
2018-09-16 17:30 | 37 | 37 |  |  | 43359.7292 | 54 | 54
2018-09-16 18:00 | 42 | 42 |  |  | 43359.75 | 60 | 59
2018-09-16 18:30 | 47 | 47 |  |  | 43359.7708 | 65 | 64
2018-09-16 19:00 | 48 | 47 |  |  | 43359.7917 | 67 | 67
2018-09-16 19:30 | 45 | 45 |  |  | 43359.8125 | 64 | 64
2018-09-16 20:00 | 43 | 43 |  |  | 43359.8333 | 62 | 62
2018-09-16 20:30 | 44 | 43 |  |  | 43359.8542 | 62 | 62
2018-09-16 21:00 | 41 | 41 |  |  | 43359.875 | 59 | 58
2018-09-16 21:30 | 37 | 37 |  |  | 43359.8958 | 55 | 54
2018-09-16 22:00 | 36 | 36 |  |  | 43359.9167 | 55 | 54
2018-09-16 22:30 | 35 | 35 |  |  | 43359.9375 | 53 | 52
2018-09-16 23:00 | 34 | 33 |  |  | 43359.9583 | 49 | 48
2018-09-16 23:30 | 30 | 30 |  |  | 43359.9792 | 46 | 45
2018-09-17 | 29 | 29 |  |  | 43360 | 45 | 43
2018-09-17 00:30 | 27 | 26 |  |  | 43360.0208 | 42 | 39
2018-09-17 01:00 | 25 | 24 |  |  | 43360.0417 | 38 | 36
2018-09-17 01:30 | 25 | 24 |  |  | 43360.0625 | 38 | 36
2018-09-17 02:00 | 25 | 24 |  |  | 43360.0833 | 38 | 35
2018-09-17 02:30 | 25 | 24 |  |  | 43360.1042 | 39 | 36
2018-09-17 03:00 | 27 | 26 |  |  | 43360.125 | 40 | 37
2018-09-17 03:30 | 27 | 26 |  |  | 43360.1458 | 39 | 36
2018-09-17 04:00 | 27 | 26 |  |  | 43360.1667 | 39 | 36
2018-09-17 04:30 | 24 | 23 |  |  | 43360.1875 | 37 | 34
2018-09-17 05:00 | 29 | 28 |  |  | 43360.2083 | 41 | 38
2018-09-17 05:30 | 31 | 31 |  |  | 43360.2292 | 43 | 41
2018-09-17 06:00 | 35 | 35 |  |  | 43360.25 | 48 | 47
2018-09-17 06:30 | 39 | 39 |  |  | 43360.2708 | 54 | 54
2018-09-17 07:00 | 43 | 42 |  |  | 43360.2917 | 61 | 61
2018-09-17 07:30 | 47 | 47 |  |  | 43360.3125 | 67 | 67
2018-09-17 08:00 | 45 | 44 |  |  | 43360.3333 | 66 | 66
2018-09-17 08:30 | 41 | 41 |  |  | 43360.3542 | 63 | 63
2018-09-17 09:00 | 37 | 37 |  |  | 43360.375 | 59 | 59
2018-09-17 09:30 | 37 | 37 |  |  | 43360.3958 | 59 | 58
2018-09-17 10:00 | 39 | 38 |  |  | 43360.4167 | 59 | 59
2018-09-17 10:30 | 41 | 40 |  |  | 43360.4375 | 61 | 60
2018-09-17 11:00 | 42 | 42 |  |  | 43360.4583 | 61 | 60
2018-09-17 11:30 | 45 | 44 |  |  | 43360.4792 | 62 | 62
2018-09-17 12:00 | 42 | 42 |  |  | 43360.5 | 59 | 58
2018-09-17 12:30 | 43 | 42 |  |  | 43360.5208 | 61 | 61
2018-09-17 13:00 | 46 | 45 |  |  | 43360.5417 | 61 | 61
2018-09-17 13:30 | 48 | 48 |  |  | 43360.5625 | 64 | 64
2018-09-17 14:00 | 48 | 47 |  |  | 43360.5833 | 65 | 65
2018-09-17 14:30 | 53 | 53 |  |  | 43360.6042 | 69 | 69
2018-09-17 15:00 | 53 | 52 |  |  | 43360.625 | 70 | 69
2018-09-17 15:30 | 50 | 50 |  |  | 43360.6458 | 69 | 69
2018-09-17 16:00 | 51 | 51 |  |  | 43360.6667 | 71 | 71
2018-09-17 16:30 | 56 | 56 |  |  | 43360.6875 | 77 | 76
2018-09-17 17:00 | 61 | 60 |  |  | 43360.7083 | 80 | 80
2018-09-17 17:30 | 59 | 59 |  |  | 43360.7292 | 77 | 77
2018-09-17 18:00 | 61 | 61 |  |  | 43360.75 | 79 | 79
2018-09-17 18:30 | 62 | 62 |  |  | 43360.7708 | 79 | 79
2018-09-17 19:00 | 64 | 64 |  |  | 43360.7917 | 80 | 80
2018-09-17 19:30 | 63 | 63 |  |  | 43360.8125 | 79 | 78
2018-09-17 20:00 | 61 | 61 |  |  | 43360.8333 | 78 | 78
2018-09-17 20:30 | 58 | 57 |  |  | 43360.8542 | 74 | 74
2018-09-17 21:00 | 55 | 55 |  |  | 43360.875 | 70 | 69
2018-09-17 21:30 | 53 | 53 |  |  | 43360.8958 | 67 | 67
2018-09-17 22:00 | 53 | 53 |  |  | 43360.9167 | 68 | 67
2018-09-17 22:30 | 52 | 52 |  |  | 43360.9375 | 68 | 67
2018-09-17 23:00 | 49 | 49 |  |  | 43360.9583 | 63 | 63
2018-09-17 23:30 | 46 | 46 |  |  | 43360.9792 | 61 | 59
2018-09-18 | 41 | 41 |  |  | 43361 | 57 | 55
2018-09-18 00:30 | 41 | 41 |  |  | 43361.0208 | 55 | 53
2018-09-18 01:00 | 38 | 38 |  |  | 43361.0417 | 51 | 49
2018-09-18 01:30 | 36 | 35 |  |  | 43361.0625 | 47 | 46
2018-09-18 02:00 | 35 | 34 |  |  | 43361.0833 | 46 | 44
2018-09-18 02:30 | 33 | 33 |  |  | 43361.1042 | 45 | 43
2018-09-18 03:00 | 34 | 33 |  |  | 43361.125 | 44 | 42
2018-09-18 03:30 | 35 | 34 |  |  | 43361.1458 | 45 | 43
2018-09-18 04:00 | 36 | 35 |  |  | 43361.1667 | 46 | 44
2018-09-18 04:30 | 37 | 36 |  |  | 43361.1875 | 47 | 46
2018-09-18 05:00 | 40 | 40 |  |  | 43361.2083 | 51 | 50
2018-09-18 05:30 | 43 | 43 |  |  | 43361.2292 | 54 | 53
2018-09-18 06:00 | 48 | 48 |  |  | 43361.25 | 59 | 59
2018-09-18 06:30 | 51 | 51 |  |  | 43361.2708 | 64 | 64
2018-09-18 07:00 | 51 | 50 |  |  | 43361.2917 | 67 | 67
2018-09-18 07:30 | 51 | 51 |  |  | 43361.3125 | 72 | 72
2018-09-18 08:00 | 48 | 48 |  |  | 43361.3333 | 70 | 69
2018-09-18 08:30 | 48 | 48 |  |  | 43361.3542 | 70 | 70
2018-09-18 09:00 | 53 | 53 |  |  | 43361.375 | 74 | 74
2018-09-18 09:30 | 54 | 54 |  |  | 43361.3958 | 73 | 73
2018-09-18 10:00 | 51 | 51 |  |  | 43361.4167 | 69 | 68
2018-09-18 10:30 | 48 | 48 |  |  | 43361.4375 | 66 | 66
2018-09-18 11:00 | 43 | 43 |  |  | 43361.4583 | 65 | 65
2018-09-18 11:30 | 42 | 41 |  |  | 43361.4792 | 62 | 61
2018-09-18 12:00 | 39 | 39 |  |  | 43361.5 | 60 | 60
2018-09-18 12:30 | 40 | 39 |  |  | 43361.5208 | 63 | 63
2018-09-18 13:00 | 40 | 39 |  |  | 43361.5417 | 61 | 61
2018-09-18 13:30 | 38 | 38 |  |  | 43361.5625 | 59 | 59
2018-09-18 14:00 | 41 | 40 |  |  | 43361.5833 | 62 | 61
2018-09-18 14:30 | 41 | 41 |  |  | 43361.6042 | 61 | 61
2018-09-18 15:00 | 38 | 38 |  |  | 43361.625 | 60 | 60
2018-09-18 15:30 | 44 | 44 |  |  | 43361.6458 | 65 | 65
2018-09-18 16:00 | 48 | 48 |  |  | 43361.6667 | 69 | 68
2018-09-18 16:30 | 50 | 50 |  |  | 43361.6875 | 71 | 70
2018-09-18 17:00 | 55 | 55 |  |  | 43361.7083 | 75 | 74
2018-09-18 17:30 | 56 | 56 |  |  | 43361.7292 | 75 | 74
2018-09-18 18:00 | 55 | 55 |  |  | 43361.75 | 74 | 73
2018-09-18 18:30 | 56 | 55 |  |  | 43361.7708 | 76 | 72
2018-09-18 19:00 | 56 | 55 |  |  | 43361.7917 | 76 | 72
2018-09-18 19:30 | 56 | 55 |  |  | 43361.8125 | 76 | 71
2018-09-18 20:00 | 55 | 54 |  |  | 43361.8333 | 75 | 69
2018-09-18 20:30 | 55 | 55 |  |  | 43361.8542 | 72 | 69
2018-09-18 21:00 | 51 | 51 |  |  | 43361.875 | 67 | 65
2018-09-18 21:30 | 49 | 49 |  |  | 43361.8958 | 63 | 61
2018-09-18 22:00 | 47 | 47 |  |  | 43361.9167 | 63 | 60
2018-09-18 22:30 | 42 | 42 |  |  | 43361.9375 | 59 | 57
2018-09-18 23:00 | 42 | 41 |  |  | 43361.9583 | 57 | 54
2018-09-18 23:30 | 40 | 39 |  |  | 43361.9792 | 56 | 53
2018-09-19 | 35 | 33 |  |  | 43362 | 52 | 47
2018-09-19 00:30 | 35 | 34 |  |  | 43362.0208 | 51 | 45
2018-09-19 01:00 | 34 | 33 |  |  | 43362.0417 | 48 | 43
2018-09-19 01:30 | 31 | 29 |  |  | 43362.0625 | 44 | 39
2018-09-19 02:00 | 29 | 27 |  |  | 43362.0833 | 43 | 38
2018-09-19 02:30 | 30 | 29 |  |  | 43362.1042 | 44 | 39
2018-09-19 03:00 | 32 | 31 |  |  | 43362.125 | 45 | 40
2018-09-19 03:30 | 32 | 31 |  |  | 43362.1458 | 46 | 42
2018-09-19 04:00 | 33 | 32 |  |  | 43362.1667 | 47 | 42
2018-09-19 04:30 | 33 | 31 |  |  | 43362.1875 | 46 | 42
2018-09-19 05:00 | 35 | 34 |  |  | 43362.2083 | 48 | 43
2018-09-19 05:30 | 41 | 40 |  |  | 43362.2292 | 54 | 51
2018-09-19 06:00 | 43 | 43 |  |  | 43362.25 | 56 | 54
2018-09-19 06:30 | 43 | 43 |  |  | 43362.2708 | 58 | 57
2018-09-19 07:00 | 44 | 44 |  |  | 43362.2917 | 61 | 60
2018-09-19 07:30 | 46 | 46 |  |  | 43362.3125 | 65 | 65
2018-09-19 08:00 | 44 | 43 |  |  | 43362.3333 | 63 | 63
2018-09-19 08:30 | 44 | 43 |  |  | 43362.3542 | 64 | 64
2018-09-19 09:00 | 43 | 42 |  |  | 43362.375 | 63 | 63
2018-09-19 09:30 | 44 | 44 |  |  | 43362.3958 | 63 | 63
2018-09-19 10:00 | 46 | 45 |  |  | 43362.4167 | 63 | 63
2018-09-19 10:30 | 45 | 44 |  |  | 43362.4375 | 63 | 63
2018-09-19 11:00 | 47 | 47 |  |  | 43362.4583 | 65 | 65
2018-09-19 11:30 | 46 | 46 |  |  | 43362.4792 | 66 | 66
2018-09-19 12:00 | 44 | 43 |  |  | 43362.5 | 64 | 64
2018-09-19 12:30 | 43 | 43 |  |  | 43362.5208 | 64 | 64
2018-09-19 13:00 | 43 | 43 |  |  | 43362.5417 | 63 | 63
2018-09-19 13:30 | 45 | 44 |  |  | 43362.5625 | 65 | 65
2018-09-19 14:00 | 43 | 42 |  |  | 43362.5833 | 63 | 63
2018-09-19 14:30 | 46 | 45 |  |  | 43362.6042 | 64 | 64
2018-09-19 15:00 | 47 | 46 |  |  | 43362.625 | 67 | 67
2018-09-19 15:30 | 47 | 47 |  |  | 43362.6458 | 68 | 67
2018-09-19 16:00 | 46 | 46 |  |  | 43362.6667 | 69 | 66
2018-09-19 16:30 | 46 | 46 |  |  | 43362.6875 | 70 | 67
2018-09-19 17:00 | 49 | 49 |  |  | 43362.7083 | 73 | 70
2018-09-19 17:30 | 51 | 51 |  |  | 43362.7292 | 73 | 70
2018-09-19 18:00 | 53 | 52 |  |  | 43362.75 | 74 | 70
2018-09-19 18:30 | 55 | 54 |  |  | 43362.7708 | 76 | 71
2018-09-19 19:00 | 56 | 55 |  |  | 43362.7917 | 76 | 71
2018-09-19 19:30 | 55 | 54 |  |  | 43362.8125 | 74 | 69
2018-09-19 20:00 | 52 | 51 |  |  | 43362.8333 | 71 | 67
2018-09-19 20:30 | 51 | 51 |  |  | 43362.8542 | 69 | 67
2018-09-19 21:00 | 48 | 48 |  |  | 43362.875 | 65 | 63
2018-09-19 21:30 | 43 | 43 |  |  | 43362.8958 | 59 | 57
2018-09-19 22:00 | 41 | 41 |  |  | 43362.9167 | 58 | 56
2018-09-19 22:30 | 37 | 37 |  |  | 43362.9375 | 55 | 53
2018-09-19 23:00 | 32 | 32 |  |  | 43362.9583 | 49 | 46
2018-09-19 23:30 | 27 | 26 |  |  | 43362.9792 | 44 | 40
2018-09-20 | 22 | 21 |  |  | 43363 | 39 | 36
2018-09-20 00:30 | 21 | 20 |  |  | 43363.0208 | 37 | 33
2018-09-20 01:00 | 19 | 18 |  |  | 43363.0417 | 33 | 29
2018-09-20 01:30 | 17 | 15 |  |  | 43363.0625 | 31 | 27
2018-09-20 02:00 | 16 | 15 |  |  | 43363.0833 | 31 | 25
2018-09-20 02:30 | 19 | 18 |  |  | 43363.1042 | 33 | 28
2018-09-20 03:00 | 18 | 17 |  |  | 43363.125 | 32 | 27
2018-09-20 03:30 | 19 | 18 |  |  | 43363.1458 | 33 | 28
2018-09-20 04:00 | 19 | 18 |  |  | 43363.1667 | 34 | 28
2018-09-20 04:30 | 20 | 19 |  |  | 43363.1875 | 35 | 30
2018-09-20 05:00 | 24 | 23 |  |  | 43363.2083 | 38 | 34
2018-09-20 05:30 | 26 | 26 |  |  | 43363.2292 | 40 | 37
2018-09-20 06:00 | 29 | 28 |  |  | 43363.25 | 44 | 42
2018-09-20 06:30 | 33 | 33 |  |  | 43363.2708 | 51 | 49
2018-09-20 07:00 | 36 | 36 |  |  | 43363.2917 | 58 | 55
2018-09-20 07:30 | 37 | 36 |  |  | 43363.3125 | 60 | 57
2018-09-20 08:00 | 35 | 35 |  |  | 43363.3333 | 59 | 57
2018-09-20 08:30 | 35 | 35 |  |  | 43363.3542 | 60 | 58
2018-09-20 09:00 | 34 | 34 |  |  | 43363.375 | 58 | 57
2018-09-20 09:30 | 36 | 36 |  |  | 43363.3958 | 60 | 59
2018-09-20 10:00 | 36 | 36 |  |  | 43363.4167 | 56 | 56
2018-09-20 10:30 | 38 | 38 |  |  | 43363.4375 | 57 | 57
2018-09-20 11:00 | 38 | 38 |  |  | 43363.4583 | 59 | 58
2018-09-20 11:30 | 40 | 40 |  |  | 43363.4792 | 62 | 61
2018-09-20 12:00 | 39 | 39 |  |  | 43363.5 | 61 | 61
2018-09-20 12:30 | 37 | 37 |  |  | 43363.5208 | 56 | 55
2018-09-20 13:00 | 43 | 43 |  |  | 43363.5417 | 62 | 62
2018-09-20 13:30 | 46 | 46 |  |  | 43363.5625 | 66 | 66
2018-09-20 14:00 | 49 | 49 |  |  | 43363.5833 | 67 | 67
2018-09-20 14:30 | 52 | 52 |  |  | 43363.6042 | 74 | 73
2018-09-20 15:00 | 50 | 50 |  |  | 43363.625 | 72 | 72
2018-09-20 15:30 | 49 | 49 |  |  | 43363.6458 | 71 | 70
2018-09-20 16:00 | 50 | 50 |  |  | 43363.6667 | 73 | 71
2018-09-20 16:30 | 51 | 50 |  |  | 43363.6875 | 73 | 72
2018-09-20 17:00 | 53 | 53 |  |  | 43363.7083 | 75 | 74
2018-09-20 17:30 | 54 | 54 |  |  | 43363.7292 | 76 | 74
2018-09-20 18:00 | 54 | 54 |  |  | 43363.75 | 75 | 73
2018-09-20 18:30 | 52 | 52 |  |  | 43363.7708 | 73 | 71
2018-09-20 19:00 | 54 | 53 |  |  | 43363.7917 | 75 | 71
2018-09-20 19:30 | 53 | 52 |  |  | 43363.8125 | 73 | 70
2018-09-20 20:00 | 51 | 50 |  |  | 43363.8333 | 70 | 67
2018-09-20 20:30 | 49 | 49 |  |  | 43363.8542 | 67 | 66
2018-09-20 21:00 | 45 | 45 |  |  | 43363.875 | 62 | 61
2018-09-20 21:30 | 41 | 41 |  |  | 43363.8958 | 58 | 56
2018-09-20 22:00 | 44 | 43 |  |  | 43363.9167 | 60 | 58
2018-09-20 22:30 | 42 | 42 |  |  | 43363.9375 | 60 | 58
2018-09-20 23:00 | 41 | 41 |  |  | 43363.9583 | 58 | 56
2018-09-20 23:30 | 37 | 37 |  |  | 43363.9792 | 55 | 52
2018-09-21 | 31 | 31 |  |  | 43364 | 49 | 46
2018-09-21 00:30 | 28 | 26 |  |  | 43364.0208 | 44 | 40
2018-09-21 01:00 | 22 | 21 |  |  | 43364.0417 | 38 | 33
2018-09-21 01:30 | 20 | 18 |  |  | 43364.0625 | 36 | 30
2018-09-21 02:00 | 20 | 18 |  |  | 43364.0833 | 36 | 30
2018-09-21 02:30 | 20 | 18 |  |  | 43364.1042 | 36 | 29
2018-09-21 03:00 | 20 | 18 |  |  | 43364.125 | 36 | 29
2018-09-21 03:30 | 22 | 20 |  |  | 43364.1458 | 39 | 32
2018-09-21 04:00 | 21 | 19 |  |  | 43364.1667 | 38 | 31
2018-09-21 04:30 | 20 | 18 |  |  | 43364.1875 | 37 | 30
2018-09-21 05:00 | 22 | 20 |  |  | 43364.2083 | 39 | 32
2018-09-21 05:30 | 27 | 26 |  |  | 43364.2292 | 44 | 39
2018-09-21 06:00 | 29 | 29 |  |  | 43364.25 | 47 | 44
2018-09-21 06:30 | 33 | 33 |  |  | 43364.2708 | 52 | 50
2018-09-21 07:00 | 33 | 33 |  |  | 43364.2917 | 56 | 55
2018-09-21 07:30 | 36 | 36 |  |  | 43364.3125 | 61 | 60
2018-09-21 08:00 | 37 | 37 |  |  | 43364.3333 | 62 | 62
2018-09-21 08:30 | 35 | 35 |  |  | 43364.3542 | 60 | 60
2018-09-21 09:00 | 34 | 34 |  |  | 43364.375 | 58 | 58
2018-09-21 09:30 | 33 | 33 |  |  | 43364.3958 | 57 | 57
2018-09-21 10:00 | 33 | 33 |  |  | 43364.4167 | 56 | 56
2018-09-21 10:30 | 33 | 33 |  |  | 43364.4375 | 55 | 55
2018-09-21 11:00 | 34 | 34 |  |  | 43364.4583 | 56 | 56
2018-09-21 11:30 | 35 | 34 |  |  | 43364.4792 | 58 | 58
2018-09-21 12:00 | 37 | 37 |  |  | 43364.5 | 60 | 60
2018-09-21 12:30 | 38 | 37 |  |  | 43364.5208 | 60 | 60
2018-09-21 13:00 | 40 | 40 |  |  | 43364.5417 | 63 | 63
2018-09-21 13:30 | 41 | 41 |  |  | 43364.5625 | 64 | 64
2018-09-21 14:00 | 40 | 39 |  |  | 43364.5833 | 61 | 61
2018-09-21 14:30 | 40 | 40 |  |  | 43364.6042 | 60 | 60
2018-09-21 15:00 | 39 | 39 |  |  | 43364.625 | 60 | 60
2018-09-21 15:30 | 39 | 38 |  |  | 43364.6458 | 61 | 61
2018-09-21 16:00 | 44 | 44 |  |  | 43364.6667 | 68 | 67
2018-09-21 16:30 | 48 | 48 |  |  | 43364.6875 | 72 | 71
2018-09-21 17:00 | 48 | 48 |  |  | 43364.7083 | 71 | 70
2018-09-21 17:30 | 48 | 47 |  |  | 43364.7292 | 70 | 68
2018-09-21 18:00 | 48 | 48 |  |  | 43364.75 | 70 | 68
2018-09-21 18:30 | 48 | 48 |  |  | 43364.7708 | 69 | 67
2018-09-21 19:00 | 49 | 48 |  |  | 43364.7917 | 70 | 69
2018-09-21 19:30 | 48 | 48 |  |  | 43364.8125 | 69 | 68
2018-09-21 20:00 | 47 | 47 |  |  | 43364.8333 | 67 | 66
2018-09-21 20:30 | 46 | 46 |  |  | 43364.8542 | 65 | 64
2018-09-21 21:00 | 43 | 42 |  |  | 43364.875 | 61 | 59
2018-09-21 21:30 | 38 | 38 |  |  | 43364.8958 | 57 | 55
2018-09-21 22:00 | 36 | 36 |  |  | 43364.9167 | 55 | 53
2018-09-21 22:30 | 35 | 34 |  |  | 43364.9375 | 55 | 52
2018-09-21 23:00 | 35 | 34 |  |  | 43364.9583 | 54 | 51
2018-09-21 23:30 | 33 | 33 |  |  | 43364.9792 | 53 | 49
2018-09-22 | 31 | 30 |  |  | 43365 | 51 | 47
2018-09-22 00:30 | 30 | 28 |  |  | 43365.0208 | 49 | 43
2018-09-22 01:00 | 28 | 25 |  |  | 43365.0417 | 44 | 38
2018-09-22 01:30 | 27 | 24 |  |  | 43365.0625 | 43 | 37
2018-09-22 02:00 | 26 | 23 |  |  | 43365.0833 | 42 | 35
2018-09-22 02:30 | 26 | 23 |  |  | 43365.1042 | 42 | 35
2018-09-22 03:00 | 24 | 22 |  |  | 43365.125 | 40 | 33
2018-09-22 03:30 | 25 | 22 |  |  | 43365.1458 | 40 | 34
2018-09-22 04:00 | 25 | 23 |  |  | 43365.1667 | 41 | 35
2018-09-22 04:30 | 25 | 23 |  |  | 43365.1875 | 41 | 36
2018-09-22 05:00 | 28 | 25 |  |  | 43365.2083 | 43 | 38
2018-09-22 05:30 | 28 | 26 |  |  | 43365.2292 | 44 | 39
2018-09-22 06:00 | 28 | 26 |  |  | 43365.25 | 44 | 39
2018-09-22 06:30 | 29 | 27 |  |  | 43365.2708 | 46 | 41
2018-09-22 07:00 | 30 | 28 |  |  | 43365.2917 | 48 | 44
2018-09-22 07:30 | 30 | 29 |  |  | 43365.3125 | 49 | 45
2018-09-22 08:00 | 27 | 26 |  |  | 43365.3333 | 46 | 44
2018-09-22 08:30 | 27 | 26 |  |  | 43365.3542 | 47 | 44
2018-09-22 09:00 | 27 | 26 |  |  | 43365.375 | 46 | 42
2018-09-22 09:30 | 27 | 26 |  |  | 43365.3958 | 45 | 42
2018-09-22 10:00 | 26 | 26 |  |  | 43365.4167 | 44 | 41
2018-09-22 10:30 | 29 | 29 |  |  | 43365.4375 | 47 | 44
2018-09-22 11:00 | 31 | 31 |  |  | 43365.4583 | 48 | 45
2018-09-22 11:30 | 33 | 33 |  |  | 43365.4792 | 49 | 47
2018-09-22 12:00 | 34 | 33 |  |  | 43365.5 | 51 | 48
2018-09-22 12:30 | 33 | 32 |  |  | 43365.5208 | 49 | 47
2018-09-22 13:00 | 32 | 31 |  |  | 43365.5417 | 49 | 46
2018-09-22 13:30 | 33 | 32 |  |  | 43365.5625 | 50 | 47
2018-09-22 14:00 | 32 | 31 |  |  | 43365.5833 | 48 | 45
2018-09-22 14:30 | 31 | 30 |  |  | 43365.6042 | 48 | 44
2018-09-22 15:00 | 32 | 31 |  |  | 43365.625 | 47 | 44
2018-09-22 15:30 | 34 | 33 |  |  | 43365.6458 | 50 | 47
2018-09-22 16:00 | 36 | 35 |  |  | 43365.6667 | 54 | 50
2018-09-22 16:30 | 36 | 35 |  |  | 43365.6875 | 55 | 51
2018-09-22 17:00 | 39 | 38 |  |  | 43365.7083 | 57 | 54
2018-09-22 17:30 | 41 | 40 |  |  | 43365.7292 | 59 | 56
2018-09-22 18:00 | 40 | 39 |  |  | 43365.75 | 59 | 55
2018-09-22 18:30 | 41 | 40 |  |  | 43365.7708 | 60 | 56
2018-09-22 19:00 | 44 | 43 |  |  | 43365.7917 | 63 | 59
2018-09-22 19:30 | 43 | 41 |  |  | 43365.8125 | 62 | 58
2018-09-22 20:00 | 42 | 41 |  |  | 43365.8333 | 61 | 56
2018-09-22 20:30 | 42 | 41 |  |  | 43365.8542 | 61 | 57
2018-09-22 21:00 | 40 | 38 |  |  | 43365.875 | 58 | 54
2018-09-22 21:30 | 38 | 37 |  |  | 43365.8958 | 56 | 52
2018-09-22 22:00 | 38 | 37 |  |  | 43365.9167 | 57 | 53
2018-09-22 22:30 | 38 | 37 |  |  | 43365.9375 | 56 | 52
2018-09-22 23:00 | 35 | 33 |  |  | 43365.9583 | 52 | 48
2018-09-22 23:30 | 31 | 29 |  |  | 43365.9792 | 48 | 43
2018-09-23 | 30 | 28 |  |  | 43366 | 47 | 42
2018-09-23 00:30 | 33 | 30 |  |  | 43366.0208 | 50 | 44
2018-09-23 01:00 | 33 | 31 |  |  | 43366.0417 | 50 | 43
2018-09-23 01:30 | 33 | 30 |  |  | 43366.0625 | 49 | 42
2018-09-23 02:00 | 32 | 29 |  |  | 43366.0833 | 49 | 41
2018-09-23 02:30 | 31 | 28 |  |  | 43366.1042 | 48 | 41
2018-09-23 03:00 | 29 | 26 |  |  | 43366.125 | 46 | 38
2018-09-23 03:30 | 27 | 24 |  |  | 43366.1458 | 44 | 35
2018-09-23 04:00 | 27 | 24 |  |  | 43366.1667 | 43 | 35
2018-09-23 04:30 | 27 | 23 |  |  | 43366.1875 | 43 | 35
2018-09-23 05:00 | 30 | 26 |  |  | 43366.2083 | 46 | 39
2018-09-23 05:30 | 31 | 28 |  |  | 43366.2292 | 48 | 41
2018-09-23 06:00 | 31 | 28 |  |  | 43366.25 | 49 | 41
2018-09-23 06:30 | 32 | 29 |  |  | 43366.2708 | 50 | 43
2018-09-23 07:00 | 30 | 27 |  |  | 43366.2917 | 49 | 41
2018-09-23 07:30 | 28 | 25 |  |  | 43366.3125 | 47 | 40
2018-09-23 08:00 | 27 | 24 |  |  | 43366.3333 | 46 | 39
2018-09-23 08:30 | 26 | 24 |  |  | 43366.3542 | 45 | 38
2018-09-23 09:00 | 26 | 24 |  |  | 43366.375 | 45 | 40
2018-09-23 09:30 | 27 | 25 |  |  | 43366.3958 | 45 | 40
2018-09-23 10:00 | 25 | 24 |  |  | 43366.4167 | 42 | 38
2018-09-23 10:30 | 25 | 23 |  |  | 43366.4375 | 41 | 37
2018-09-23 11:00 | 24 | 22 |  |  | 43366.4583 | 41 | 36
2018-09-23 11:30 | 25 | 23 |  |  | 43366.4792 | 41 | 37
2018-09-23 12:00 | 26 | 24 |  |  | 43366.5 | 41 | 38
2018-09-23 12:30 | 26 | 24 |  |  | 43366.5208 | 42 | 38
2018-09-23 13:00 | 28 | 26 |  |  | 43366.5417 | 43 | 40
2018-09-23 13:30 | 28 | 26 |  |  | 43366.5625 | 44 | 40
2018-09-23 14:00 | 31 | 30 |  |  | 43366.5833 | 46 | 42
2018-09-23 14:30 | 32 | 31 |  |  | 43366.6042 | 47 | 43
2018-09-23 15:00 | 33 | 32 |  |  | 43366.625 | 48 | 44
2018-09-23 15:30 | 31 | 30 |  |  | 43366.6458 | 47 | 43
2018-09-23 16:00 | 33 | 32 |  |  | 43366.6667 | 50 | 46
2018-09-23 16:30 | 36 | 35 |  |  | 43366.6875 | 54 | 50
2018-09-23 17:00 | 36 | 35 |  |  | 43366.7083 | 54 | 51
2018-09-23 17:30 | 40 | 39 |  |  | 43366.7292 | 57 | 54
2018-09-23 18:00 | 42 | 41 |  |  | 43366.75 | 60 | 57
2018-09-23 18:30 | 44 | 43 |  |  | 43366.7708 | 63 | 60
2018-09-23 19:00 | 46 | 45 |  |  | 43366.7917 | 65 | 62
2018-09-23 19:30 | 43 | 42 |  |  | 43366.8125 | 61 | 58
2018-09-23 20:00 | 41 | 40 |  |  | 43366.8333 | 59 | 56
2018-09-23 20:30 | 40 | 39 |  |  | 43366.8542 | 59 | 56
2018-09-23 21:00 | 40 | 39 |  |  | 43366.875 | 57 | 54
2018-09-23 21:30 | 38 | 37 |  |  | 43366.8958 | 55 | 52
2018-09-23 22:00 | 38 | 37 |  |  | 43366.9167 | 57 | 53
2018-09-23 22:30 | 36 | 35 |  |  | 43366.9375 | 56 | 52
2018-09-23 23:00 | 37 | 36 |  |  | 43366.9583 | 55 | 51
2018-09-23 23:30 | 33 | 32 |  |  | 43366.9792 | 52 | 47
2018-09-24 | 28 | 26 |  |  | 43367 | 46 | 40
2018-09-24 00:30 | 28 | 26 |  |  | 43367.0208 | 46 | 40
2018-09-24 01:00 | 28 | 26 |  |  | 43367.0417 | 44 | 37
2018-09-24 01:30 | 29 | 26 |  |  | 43367.0625 | 45 | 37
2018-09-24 02:00 | 29 | 27 |  |  | 43367.0833 | 45 | 38
2018-09-24 02:30 | 30 | 28 |  |  | 43367.1042 | 45 | 39
2018-09-24 03:00 | 29 | 27 |  |  | 43367.125 | 44 | 39
2018-09-24 03:30 | 30 | 28 |  |  | 43367.1458 | 44 | 39
2018-09-24 04:00 | 30 | 28 |  |  | 43367.1667 | 45 | 39
2018-09-24 04:30 | 31 | 29 |  |  | 43367.1875 | 46 | 41
2018-09-24 05:00 | 36 | 34 |  |  | 43367.2083 | 50 | 45
2018-09-24 05:30 | 40 | 39 |  |  | 43367.2292 | 55 | 51
2018-09-24 06:00 | 40 | 39 |  |  | 43367.25 | 55 | 52
2018-09-24 06:30 | 43 | 42 |  |  | 43367.2708 | 59 | 58
2018-09-24 07:00 | 42 | 42 |  |  | 43367.2917 | 62 | 60
2018-09-24 07:30 | 42 | 42 |  |  | 43367.3125 | 64 | 62
2018-09-24 08:00 | 38 | 37 |  |  | 43367.3333 | 61 | 59
2018-09-24 08:30 | 36 | 36 |  |  | 43367.3542 | 60 | 59
2018-09-24 09:00 | 38 | 38 |  |  | 43367.375 | 63 | 62
2018-09-24 09:30 | 40 | 40 |  |  | 43367.3958 | 64 | 64
2018-09-24 10:00 | 39 | 39 |  |  | 43367.4167 | 63 | 62
2018-09-24 10:30 | 40 | 40 |  |  | 43367.4375 | 62 | 62
2018-09-24 11:00 | 42 | 41 |  |  | 43367.4583 | 63 | 62
2018-09-24 11:30 | 42 | 41 |  |  | 43367.4792 | 64 | 63
2018-09-24 12:00 | 45 | 44 |  |  | 43367.5 | 66 | 66
2018-09-24 12:30 | 47 | 47 |  |  | 43367.5208 | 69 | 68
2018-09-24 13:00 | 51 | 51 |  |  | 43367.5417 | 70 | 70
2018-09-24 13:30 | 52 | 51 |  |  | 43367.5625 | 74 | 74
2018-09-24 14:00 | 56 | 56 |  |  | 43367.5833 | 75 | 74
2018-09-24 14:30 | 57 | 56 |  |  | 43367.6042 | 79 | 79
2018-09-24 15:00 | 51 | 50 |  |  | 43367.625 | 74 | 74
2018-09-24 15:30 | 50 | 49 |  |  | 43367.6458 | 69 | 69
2018-09-24 16:00 | 51 | 49 |  |  | 43367.6667 | 69 | 69
2018-09-24 16:30 | 53 | 52 |  |  | 43367.6875 | 71 | 71
2018-09-24 17:00 | 55 | 53 |  |  | 43367.7083 | 73 | 73
2018-09-24 17:30 | 54 | 52 |  |  | 43367.7292 | 71 | 71
2018-09-24 18:00 | 55 | 52 |  |  | 43367.75 | 70 | 70
2018-09-24 18:30 | 55 | 53 |  |  | 43367.7708 | 71 | 70
2018-09-24 19:00 | 56 | 54 |  |  | 43367.7917 | 72 | 71
2018-09-24 19:30 | 54 | 52 |  |  | 43367.8125 | 70 | 69
2018-09-24 20:00 | 52 | 50 |  |  | 43367.8333 | 67 | 67
2018-09-24 20:30 | 50 | 48 |  |  | 43367.8542 | 65 | 65
2018-09-24 21:00 | 46 | 44 |  |  | 43367.875 | 61 | 61
2018-09-24 21:30 | 44 | 41 |  |  | 43367.8958 | 57 | 57
2018-09-24 22:00 | 44 | 40 |  |  | 43367.9167 | 58 | 57
2018-09-24 22:30 | 40 | 36 |  |  | 43367.9375 | 55 | 54
2018-09-24 23:00 | 39 | 35 |  |  | 43367.9583 | 52 | 52
2018-09-24 23:30 | 39 | 34 |  |  | 43367.9792 | 52 | 52
2018-09-25 | 37 | 31 |  |  | 43368 | 50 | 49
2018-09-25 00:30 | 35 | 29 |  |  | 43368.0208 | 46 | 45
2018-09-25 01:00 | 34 | 28 |  |  | 43368.0417 | 43 | 42
2018-09-25 01:30 | 32 | 25 |  |  | 43368.0625 | 40 | 39
2018-09-25 02:00 | 33 | 25 |  |  | 43368.0833 | 39 | 38
2018-09-25 02:30 | 33 | 25 |  |  | 43368.1042 | 41 | 39
2018-09-25 03:00 | 33 | 25 |  |  | 43368.125 | 40 | 38
2018-09-25 03:30 | 33 | 25 |  |  | 43368.1458 | 39 | 37
2018-09-25 04:00 | 33 | 25 |  |  | 43368.1667 | 40 | 38
2018-09-25 04:30 | 33 | 25 |  |  | 43368.1875 | 41 | 39
2018-09-25 05:00 | 34 | 27 |  |  | 43368.2083 | 42 | 41
2018-09-25 05:30 | 37 | 31 |  |  | 43368.2292 | 47 | 46
2018-09-25 06:00 | 41 | 37 |  |  | 43368.25 | 54 | 53
2018-09-25 06:30 | 42 | 38 |  |  | 43368.2708 | 58 | 57
2018-09-25 07:00 | 43 | 41 |  |  | 43368.2917 | 63 | 63
2018-09-25 07:30 | 46 | 44 |  |  | 43368.3125 | 67 | 67
2018-09-25 08:00 | 47 | 46 |  |  | 43368.3333 | 71 | 70
2018-09-25 08:30 | 50 | 49 |  |  | 43368.3542 | 76 | 76
2018-09-25 09:00 | 49 | 47 |  |  | 43368.375 | 75 | 75
2018-09-25 09:30 | 46 | 45 |  |  | 43368.3958 | 69 | 69
2018-09-25 10:00 | 42 | 40 |  |  | 43368.4167 | 66 | 66
2018-09-25 10:30 | 43 | 41 |  |  | 43368.4375 | 64 | 64
2018-09-25 11:00 | 52 | 51 |  |  | 43368.4583 | 74 | 73
2018-09-25 11:30 | 53 | 52 |  |  | 43368.4792 | 74 | 74
2018-09-25 12:00 | 52 | 51 |  |  | 43368.5 | 74 | 74
2018-09-25 12:30 | 53 | 52 |  |  | 43368.5208 | 76 | 75
2018-09-25 13:00 | 52 | 51 |  |  | 43368.5417 | 74 | 73
2018-09-25 13:30 | 50 | 48 |  |  | 43368.5625 | 71 | 71
2018-09-25 14:00 | 48 | 47 |  |  | 43368.5833 | 70 | 70
2018-09-25 14:30 | 54 | 52 |  |  | 43368.6042 | 74 | 74
2018-09-25 15:00 | 51 | 49 |  |  | 43368.625 | 71 | 71
2018-09-25 15:30 | 51 | 50 |  |  | 43368.6458 | 73 | 73
2018-09-25 16:00 | 53 | 52 |  |  | 43368.6667 | 75 | 75
2018-09-25 16:30 | 51 | 49 |  |  | 43368.6875 | 72 | 72
2018-09-25 17:00 | 52 | 50 |  |  | 43368.7083 | 73 | 73
2018-09-25 17:30 | 54 | 52 |  |  | 43368.7292 | 74 | 74
2018-09-25 18:00 | 56 | 53 |  |  | 43368.75 | 75 | 75
2018-09-25 18:30 | 55 | 52 |  |  | 43368.7708 | 74 | 74
2018-09-25 19:00 | 56 | 53 |  |  | 43368.7917 | 73 | 73
2018-09-25 19:30 | 54 | 52 |  |  | 43368.8125 | 72 | 72
2018-09-25 20:00 | 54 | 52 |  |  | 43368.8333 | 71 | 71
2018-09-25 20:30 | 53 | 51 |  |  | 43368.8542 | 70 | 70
2018-09-25 21:00 | 49 | 47 |  |  | 43368.875 | 66 | 66
2018-09-25 21:30 | 46 | 43 |  |  | 43368.8958 | 61 | 60
2018-09-25 22:00 | 47 | 44 |  |  | 43368.9167 | 62 | 62
2018-09-25 22:30 | 44 | 41 |  |  | 43368.9375 | 59 | 59
2018-09-25 23:00 | 43 | 40 |  |  | 43368.9583 | 56 | 56
2018-09-25 23:30 | 40 | 36 |  |  | 43368.9792 | 52 | 51
2018-09-26 | 38 | 32 |  |  | 43369 | 49 | 48
2018-09-26 00:30 | 36 | 30 |  |  | 43369.0208 | 46 | 44
2018-09-26 01:00 | 33 | 26 |  |  | 43369.0417 | 41 | 39
2018-09-26 01:30 | 34 | 27 |  |  | 43369.0625 | 40 | 39
2018-09-26 02:00 | 39 | 32 |  |  | 43369.0833 | 47 | 46
2018-09-26 02:30 | 39 | 32 |  |  | 43369.1042 | 46 | 45
2018-09-26 03:00 | 37 | 31 |  |  | 43369.125 | 45 | 44
2018-09-26 03:30 | 33 | 26 |  |  | 43369.1458 | 40 | 39
2018-09-26 04:00 | 32 | 25 |  |  | 43369.1667 | 40 | 39
2018-09-26 04:30 | 35 | 29 |  |  | 43369.1875 | 43 | 42
2018-09-26 05:00 | 37 | 31 |  |  | 43369.2083 | 46 | 45
2018-09-26 05:30 | 40 | 36 |  |  | 43369.2292 | 51 | 50
2018-09-26 06:00 | 44 | 40 |  |  | 43369.25 | 56 | 56
2018-09-26 06:30 | 47 | 43 |  |  | 43369.2708 | 62 | 61
2018-09-26 07:00 | 47 | 45 |  |  | 43369.2917 | 66 | 65
2018-09-26 07:30 | 46 | 44 |  |  | 43369.3125 | 69 | 69
2018-09-26 08:00 | 41 | 39 |  |  | 43369.3333 | 64 | 64
2018-09-26 08:30 | 39 | 38 |  |  | 43369.3542 | 63 | 63
2018-09-26 09:00 | 39 | 38 |  |  | 43369.375 | 62 | 61
2018-09-26 09:30 | 43 | 42 |  |  | 43369.3958 | 64 | 64
2018-09-26 10:00 | 45 | 44 |  |  | 43369.4167 | 67 | 67
2018-09-26 10:30 | 43 | 42 |  |  | 43369.4375 | 67 | 66
2018-09-26 11:00 | 43 | 43 |  |  | 43369.4583 | 66 | 66
2018-09-26 11:30 | 42 | 41 |  |  | 43369.4792 | 64 | 64
2018-09-26 12:00 | 44 | 43 |  |  | 43369.5 | 68 | 67
2018-09-26 12:30 | 47 | 46 |  |  | 43369.5208 | 67 | 67
2018-09-26 13:00 | 47 | 46 |  |  | 43369.5417 | 66 | 66
2018-09-26 13:30 | 45 | 44 |  |  | 43369.5625 | 63 | 63
2018-09-26 14:00 | 49 | 48 |  |  | 43369.5833 | 65 | 65
2018-09-26 14:30 | 50 | 49 |  |  | 43369.6042 | 66 | 65
2018-09-26 15:00 | 51 | 50 |  |  | 43369.625 | 69 | 68
2018-09-26 15:30 | 43 | 41 |  |  | 43369.6458 | 63 | 63
2018-09-26 16:00 | 45 | 44 |  |  | 43369.6667 | 66 | 66
2018-09-26 16:30 | 46 | 45 |  |  | 43369.6875 | 67 | 67
2018-09-26 17:00 | 49 | 47 |  |  | 43369.7083 | 68 | 68
2018-09-26 17:30 | 51 | 46 |  |  | 43369.7292 | 68 | 67
2018-09-26 18:00 | 54 | 50 |  |  | 43369.75 | 71 | 70
2018-09-26 18:30 | 55 | 50 |  |  | 43369.7708 | 70 | 69
2018-09-26 19:00 | 57 | 52 |  |  | 43369.7917 | 73 | 71
2018-09-26 19:30 | 53 | 50 |  |  | 43369.8125 | 69 | 68
2018-09-26 20:00 | 51 | 48 |  |  | 43369.8333 | 67 | 66
2018-09-26 20:30 | 51 | 48 |  |  | 43369.8542 | 65 | 65
2018-09-26 21:00 | 45 | 42 |  |  | 43369.875 | 60 | 59
2018-09-26 21:30 | 43 | 41 |  |  | 43369.8958 | 56 | 55
2018-09-26 22:00 | 41 | 39 |  |  | 43369.9167 | 55 | 54
2018-09-26 22:30 | 42 | 38 |  |  | 43369.9375 | 56 | 55
2018-09-26 23:00 | 42 | 37 |  |  | 43369.9583 | 53 | 52
2018-09-26 23:30 | 38 | 32 |  |  | 43369.9792 | 49 | 47
2018-09-27 | 36 | 29 |  |  | 43370 | 46 | 44
2018-09-27 00:30 | 36 | 28 |  |  | 43370.0208 | 44 | 42
2018-09-27 01:00 | 35 | 26 |  |  | 43370.0417 | 42 | 39
2018-09-27 01:30 | 35 | 26 |  |  | 43370.0625 | 41 | 38
2018-09-27 02:00 | 35 | 25 |  |  | 43370.0833 | 40 | 37
2018-09-27 02:30 | 34 | 24 |  |  | 43370.1042 | 39 | 36
2018-09-27 03:00 | 35 | 26 |  |  | 43370.125 | 42 | 38
2018-09-27 03:30 | 34 | 24 |  |  | 43370.1458 | 39 | 35
2018-09-27 04:00 | 36 | 27 |  |  | 43370.1667 | 41 | 38
2018-09-27 04:30 | 36 | 27 |  |  | 43370.1875 | 43 | 40
2018-09-27 05:00 | 38 | 30 |  |  | 43370.2083 | 46 | 42
2018-09-27 05:30 | 37 | 31 |  |  | 43370.2292 | 47 | 44
2018-09-27 06:00 | 38 | 33 |  |  | 43370.25 | 49 | 47
2018-09-27 06:30 | 41 | 37 |  |  | 43370.2708 | 54 | 53
2018-09-27 07:00 | 42 | 39 |  |  | 43370.2917 | 59 | 58
2018-09-27 07:30 | 43 | 41 |  |  | 43370.3125 | 63 | 63
2018-09-27 08:00 | 44 | 41 |  |  | 43370.3333 | 66 | 65
2018-09-27 08:30 | 47 | 44 |  |  | 43370.3542 | 68 | 68
2018-09-27 09:00 | 46 | 43 |  |  | 43370.375 | 67 | 66
2018-09-27 09:30 | 49 | 46 |  |  | 43370.3958 | 68 | 67
2018-09-27 10:00 | 51 | 48 |  |  | 43370.4167 | 71 | 71
2018-09-27 10:30 | 52 | 50 |  |  | 43370.4375 | 72 | 72
2018-09-27 11:00 | 52 | 51 |  |  | 43370.4583 | 72 | 72
2018-09-27 11:30 | 52 | 51 |  |  | 43370.4792 | 73 | 73
2018-09-27 12:00 | 55 | 54 |  |  | 43370.5 | 75 | 75
2018-09-27 12:30 | 54 | 52 |  |  | 43370.5208 | 75 | 75
2018-09-27 13:00 | 52 | 51 |  |  | 43370.5417 | 72 | 72
2018-09-27 13:30 | 52 | 51 |  |  | 43370.5625 | 72 | 72
2018-09-27 14:00 | 50 | 48 |  |  | 43370.5833 | 68 | 68
2018-09-27 14:30 | 49 | 47 |  |  | 43370.6042 | 68 | 68
2018-09-27 15:00 | 50 | 49 |  |  | 43370.625 | 71 | 71
2018-09-27 15:30 | 51 | 49 |  |  | 43370.6458 | 71 | 71
2018-09-27 16:00 | 52 | 50 |  |  | 43370.6667 | 73 | 73
2018-09-27 16:30 | 54 | 51 |  |  | 43370.6875 | 74 | 73
2018-09-27 17:00 | 58 | 56 |  |  | 43370.7083 | 77 | 76
2018-09-27 17:30 | 59 | 57 |  |  | 43370.7292 | 77 | 77
2018-09-27 18:00 | 60 | 57 |  |  | 43370.75 | 77 | 77
2018-09-27 18:30 | 63 | 59 |  |  | 43370.7708 | 80 | 78
2018-09-27 19:00 | 64 | 59 |  |  | 43370.7917 | 81 | 77
2018-09-27 19:30 | 64 | 59 |  |  | 43370.8125 | 79 | 75
2018-09-27 20:00 | 60 | 57 |  |  | 43370.8333 | 75 | 74
2018-09-27 20:30 | 60 | 57 |  |  | 43370.8542 | 73 | 72
2018-09-27 21:00 | 53 | 52 |  |  | 43370.875 | 67 | 67
2018-09-27 21:30 | 49 | 47 |  |  | 43370.8958 | 62 | 62
2018-09-27 22:00 | 45 | 43 |  |  | 43370.9167 | 58 | 58
2018-09-27 22:30 | 43 | 40 |  |  | 43370.9375 | 56 | 56
2018-09-27 23:00 | 42 | 39 |  |  | 43370.9583 | 54 | 54
2018-09-27 23:30 | 40 | 36 |  |  | 43370.9792 | 51 | 51
2018-09-28 | 35 | 31 |  |  | 43371 | 46 | 46
2018-09-28 00:30 | 35 | 30 |  |  | 43371.0208 | 44 | 44
2018-09-28 01:00 | 35 | 29 |  |  | 43371.0417 | 43 | 42
2018-09-28 01:30 | 34 | 26 |  |  | 43371.0625 | 39 | 37
2018-09-28 02:00 | 33 | 24 |  |  | 43371.0833 | 38 | 36
2018-09-28 02:30 | 33 | 25 |  |  | 43371.1042 | 38 | 35
2018-09-28 03:00 | 31 | 22 |  |  | 43371.125 | 35 | 32
2018-09-28 03:30 | 31 | 22 |  |  | 43371.1458 | 36 | 33
2018-09-28 04:00 | 31 | 22 |  |  | 43371.1667 | 35 | 33
2018-09-28 04:30 | 32 | 24 |  |  | 43371.1875 | 38 | 36
2018-09-28 05:00 | 35 | 28 |  |  | 43371.2083 | 42 | 40
2018-09-28 05:30 | 37 | 32 |  |  | 43371.2292 | 46 | 45
2018-09-28 06:00 | 40 | 36 |  |  | 43371.25 | 51 | 50
2018-09-28 06:30 | 46 | 42 |  |  | 43371.2708 | 60 | 59
2018-09-28 07:00 | 44 | 42 |  |  | 43371.2917 | 63 | 62
2018-09-28 07:30 | 45 | 42 |  |  | 43371.3125 | 65 | 65
2018-09-28 08:00 | 43 | 41 |  |  | 43371.3333 | 64 | 64
2018-09-28 08:30 | 43 | 41 |  |  | 43371.3542 | 65 | 65
2018-09-28 09:00 | 46 | 45 |  |  | 43371.375 | 68 | 68
2018-09-28 09:30 | 51 | 50 |  |  | 43371.3958 | 73 | 73
2018-09-28 10:00 | 50 | 49 |  |  | 43371.4167 | 72 | 72
2018-09-28 10:30 | 50 | 49 |  |  | 43371.4375 | 70 | 69
2018-09-28 11:00 | 48 | 46 |  |  | 43371.4583 | 68 | 68
2018-09-28 11:30 | 48 | 46 |  |  | 43371.4792 | 70 | 70
2018-09-28 12:00 | 49 | 48 |  |  | 43371.5 | 71 | 71
2018-09-28 12:30 | 49 | 48 |  |  | 43371.5208 | 72 | 72
2018-09-28 13:00 | 47 | 46 |  |  | 43371.5417 | 70 | 70
2018-09-28 13:30 | 48 | 47 |  |  | 43371.5625 | 69 | 69
2018-09-28 14:00 | 48 | 47 |  |  | 43371.5833 | 68 | 68
2018-09-28 14:30 | 51 | 49 |  |  | 43371.6042 | 73 | 73
2018-09-28 15:00 | 55 | 53 |  |  | 43371.625 | 76 | 76
2018-09-28 15:30 | 56 | 54 |  |  | 43371.6458 | 76 | 76
2018-09-28 16:00 | 55 | 53 |  |  | 43371.6667 | 76 | 76
2018-09-28 16:30 | 58 | 55 |  |  | 43371.6875 | 78 | 77
2018-09-28 17:00 | 59 | 56 |  |  | 43371.7083 | 77 | 76
2018-09-28 17:30 | 60 | 56 |  |  | 43371.7292 | 77 | 76
2018-09-28 18:00 | 59 | 55 |  |  | 43371.75 | 76 | 75
2018-09-28 18:30 | 60 | 56 |  |  | 43371.7708 | 76 | 74
2018-09-28 19:00 | 62 | 58 |  |  | 43371.7917 | 78 | 76
2018-09-28 19:30 | 61 | 56 |  |  | 43371.8125 | 77 | 75
2018-09-28 20:00 | 59 | 55 |  |  | 43371.8333 | 74 | 73
2018-09-28 20:30 | 59 | 56 |  |  | 43371.8542 | 74 | 72
2018-09-28 21:00 | 57 | 53 |  |  | 43371.875 | 71 | 70
2018-09-28 21:30 | 54 | 50 |  |  | 43371.8958 | 67 | 66
2018-09-28 22:00 | 54 | 51 |  |  | 43371.9167 | 68 | 67
2018-09-28 22:30 | 53 | 48 |  |  | 43371.9375 | 66 | 65
2018-09-28 23:00 | 52 | 47 |  |  | 43371.9583 | 62 | 60
2018-09-28 23:30 | 48 | 42 |  |  | 43371.9792 | 58 | 56
2018-09-29 | 47 | 41 |  |  | 43372 | 57 | 55
2018-09-29 00:30 | 44 | 36 |  |  | 43372.0208 | 52 | 49
2018-09-29 01:00 | 44 | 36 |  |  | 43372.0417 | 51 | 48
2018-09-29 01:30 | 42 | 34 |  |  | 43372.0625 | 49 | 46
2018-09-29 02:00 | 41 | 33 |  |  | 43372.0833 | 47 | 44
2018-09-29 02:30 | 40 | 31 |  |  | 43372.1042 | 45 | 42
2018-09-29 03:00 | 40 | 31 |  |  | 43372.125 | 45 | 43
2018-09-29 03:30 | 40 | 31 |  |  | 43372.1458 | 45 | 43
2018-09-29 04:00 | 42 | 34 |  |  | 43372.1667 | 47 | 45
2018-09-29 04:30 | 42 | 33 |  |  | 43372.1875 | 47 | 45
2018-09-29 05:00 | 40 | 32 |  |  | 43372.2083 | 47 | 44
2018-09-29 05:30 | 42 | 33 |  |  | 43372.2292 | 49 | 46
2018-09-29 06:00 | 42 | 33 |  |  | 43372.25 | 50 | 47
2018-09-29 06:30 | 43 | 35 |  |  | 43372.2708 | 51 | 48
2018-09-29 07:00 | 41 | 32 |  |  | 43372.2917 | 50 | 48
2018-09-29 07:30 | 39 | 32 |  |  | 43372.3125 | 49 | 48
2018-09-29 08:00 | 38 | 31 |  |  | 43372.3333 | 48 | 47
2018-09-29 08:30 | 37 | 30 |  |  | 43372.3542 | 48 | 47
2018-09-29 09:00 | 39 | 33 |  |  | 43372.375 | 51 | 51
2018-09-29 09:30 | 40 | 35 |  |  | 43372.3958 | 54 | 53
2018-09-29 10:00 | 39 | 34 |  |  | 43372.4167 | 52 | 52
2018-09-29 10:30 | 39 | 34 |  |  | 43372.4375 | 52 | 51
2018-09-29 11:00 | 42 | 36 |  |  | 43372.4583 | 54 | 54
2018-09-29 11:30 | 41 | 36 |  |  | 43372.4792 | 53 | 53
2018-09-29 12:00 | 42 | 37 |  |  | 43372.5 | 54 | 54
2018-09-29 12:30 | 41 | 36 |  |  | 43372.5208 | 53 | 53
2018-09-29 13:00 | 42 | 37 |  |  | 43372.5417 | 54 | 54
2018-09-29 13:30 | 43 | 38 |  |  | 43372.5625 | 56 | 56
2018-09-29 14:00 | 41 | 36 |  |  | 43372.5833 | 53 | 52
2018-09-29 14:30 | 44 | 40 |  |  | 43372.6042 | 54 | 54
2018-09-29 15:00 | 51 | 48 |  |  | 43372.625 | 64 | 64
2018-09-29 15:30 | 52 | 48 |  |  | 43372.6458 | 66 | 66
2018-09-29 16:00 | 55 | 50 |  |  | 43372.6667 | 67 | 66
2018-09-29 16:30 | 54 | 48 |  |  | 43372.6875 | 66 | 64
2018-09-29 17:00 | 52 | 46 |  |  | 43372.7083 | 64 | 62
2018-09-29 17:30 | 51 | 45 |  |  | 43372.7292 | 62 | 60
2018-09-29 18:00 | 48 | 41 |  |  | 43372.75 | 59 | 57
2018-09-29 18:30 | 50 | 45 |  |  | 43372.7708 | 62 | 61
2018-09-29 19:00 | 52 | 47 |  |  | 43372.7917 | 64 | 63
2018-09-29 19:30 | 51 | 46 |  |  | 43372.8125 | 63 | 62
2018-09-29 20:00 | 51 | 45 |  |  | 43372.8333 | 63 | 62
2018-09-29 20:30 | 50 | 46 |  |  | 43372.8542 | 63 | 63
2018-09-29 21:00 | 47 | 43 |  |  | 43372.875 | 60 | 59
2018-09-29 21:30 | 46 | 41 |  |  | 43372.8958 | 58 | 58
2018-09-29 22:00 | 45 | 41 |  |  | 43372.9167 | 57 | 57
2018-09-29 22:30 | 44 | 40 |  |  | 43372.9375 | 56 | 56
2018-09-29 23:00 | 43 | 38 |  |  | 43372.9583 | 53 | 52
2018-09-29 23:30 | 40 | 34 |  |  | 43372.9792 | 49 | 48
2018-09-30 | 39 | 33 |  |  | 43373 | 47 | 46
2018-09-30 00:30 | 38 | 31 |  |  | 43373.0208 | 44 | 43
2018-09-30 01:00 | 40 | 32 |  |  | 43373.0417 | 45 | 44
2018-09-30 01:30 | 40 | 32 |  |  | 43373.0625 | 47 | 45
2018-09-30 02:00 | 41 | 32 |  |  | 43373.0833 | 45 | 43
2018-09-30 02:30 | 39 | 30 |  |  | 43373.1042 | 44 | 42
2018-09-30 03:00 | 39 | 30 |  |  | 43373.125 | 43 | 41
2018-09-30 03:30 | 38 | 30 |  |  | 43373.1458 | 43 | 42
2018-09-30 04:00 | 41 | 33 |  |  | 43373.1667 | 47 | 46
2018-09-30 04:30 | 41 | 34 |  |  | 43373.1875 | 47 | 46
2018-09-30 05:00 | 39 | 31 |  |  | 43373.2083 | 44 | 43
2018-09-30 05:30 | 39 | 32 |  |  | 43373.2292 | 44 | 43
2018-09-30 06:00 | 37 | 29 |  |  | 43373.25 | 43 | 42
2018-09-30 06:30 | 36 | 28 |  |  | 43373.2708 | 42 | 42
2018-09-30 07:00 | 37 | 30 |  |  | 43373.2917 | 45 | 45
2018-09-30 07:30 | 38 | 32 |  |  | 43373.3125 | 48 | 47
2018-09-30 08:00 | 39 | 31 |  |  | 43373.3333 | 47 | 46
2018-09-30 08:30 | 42 | 34 |  |  | 43373.3542 | 51 | 50
2018-09-30 09:00 | 47 | 41 |  |  | 43373.375 | 58 | 57
2018-09-30 09:30 | 49 | 44 |  |  | 43373.3958 | 60 | 59
2018-09-30 10:00 | 51 | 46 |  |  | 43373.4167 | 63 | 63
2018-09-30 10:30 | 50 | 46 |  |  | 43373.4375 | 63 | 63
2018-09-30 11:00 | 51 | 46 |  |  | 43373.4583 | 63 | 63
2018-09-30 11:30 | 54 | 50 |  |  | 43373.4792 | 65 | 65
2018-09-30 12:00 | 55 | 51 |  |  | 43373.5 | 66 | 65
2018-09-30 12:30 | 56 | 52 |  |  | 43373.5208 | 67 | 67
2018-09-30 13:00 | 54 | 49 |  |  | 43373.5417 | 67 | 66
2018-09-30 13:30 | 48 | 42 |  |  | 43373.5625 | 64 | 63
2018-09-30 14:00 | 45 | 38 |  |  | 43373.5833 | 58 | 56
2018-09-30 14:30 | 42 | 34 |  |  | 43373.6042 | 50 | 48
2018-09-30 15:00 | 45 | 38 |  |  | 43373.625 | 53 | 51
2018-09-30 15:30 | 43 | 36 |  |  | 43373.6458 | 55 | 54
2018-09-30 16:00 | 44 | 37 |  |  | 43373.6667 | 55 | 53
2018-09-30 16:30 | 47 | 41 |  |  | 43373.6875 | 57 | 56
2018-09-30 17:00 | 49 | 43 |  |  | 43373.7083 | 60 | 59
2018-09-30 17:30 | 51 | 45 |  |  | 43373.7292 | 62 | 61
2018-09-30 18:00 | 50 | 45 |  |  | 43373.75 | 62 | 61
2018-09-30 18:30 | 55 | 49 |  |  | 43373.7708 | 67 | 65
2018-09-30 19:00 | 56 | 50 |  |  | 43373.7917 | 68 | 67
2018-09-30 19:30 | 55 | 50 |  |  | 43373.8125 | 67 | 66
2018-09-30 20:00 | 55 | 49 |  |  | 43373.8333 | 66 | 65
2018-09-30 20:30 | 54 | 48 |  |  | 43373.8542 | 65 | 64
2018-09-30 21:00 | 53 | 48 |  |  | 43373.875 | 64 | 63
2018-09-30 21:30 | 53 | 47 |  |  | 43373.8958 | 64 | 63
2018-09-30 22:00 | 53 | 47 |  |  | 43373.9167 | 64 | 63
2018-09-30 22:30 | 53 | 48 |  |  | 43373.9375 | 65 | 63
2018-09-30 23:00 | 53 | 47 |  |  | 43373.9583 | 63 | 62
2018-09-30 23:30 | 51 | 45 |  |  | 43373.9792 | 60 | 59
2018-10-01 | 48 | 40 |  |  | 43374 | 57 | 55
2018-10-01 00:30 | 45 | 36 |  |  | 43374.0208 | 52 | 50
2018-10-01 01:00 | 43 | 34 |  |  | 43374.0417 | 48 | 46
2018-10-01 01:30 | 43 | 33 |  |  | 43374.0625 | 47 | 45
2018-10-01 02:00 | 41 | 30 |  |  | 43374.0833 | 44 | 41
2018-10-01 02:30 | 38 | 30 |  |  | 43374.1042 | 42 | 41
2018-10-01 03:00 | 37 | 30 |  |  | 43374.125 | 42 | 41
2018-10-01 03:30 | 37 | 31 |  |  | 43374.1458 | 42 | 41
2018-10-01 04:00 | 38 | 31 |  |  | 43374.1667 | 41 | 41
2018-10-01 04:30 | 38 | 31 |  |  | 43374.1875 | 42 | 41
2018-10-01 05:00 | 39 | 32 |  |  | 43374.2083 | 43 | 42
2018-10-01 05:30 | 38 | 32 |  |  | 43374.2292 | 44 | 44
2018-10-01 06:00 | 38 | 31 |  |  | 43374.25 | 45 | 44
2018-10-01 06:30 | 39 | 32 |  |  | 43374.2708 | 48 | 47
2018-10-01 07:00 | 38 | 31 |  |  | 43374.2917 | 47 | 47
2018-10-01 07:30 | 38 | 32 |  |  | 43374.3125 | 48 | 48
2018-10-01 08:00 | 38 | 31 |  |  | 43374.3333 | 49 | 49
2018-10-01 08:30 | 36 | 31 |  |  | 43374.3542 | 48 | 48
2018-10-01 09:00 | 34 | 28 |  |  | 43374.375 | 46 | 46
2018-10-01 09:30 | 34 | 29 |  |  | 43374.3958 | 46 | 46
2018-10-01 10:00 | 34 | 30 |  |  | 43374.4167 | 47 | 47
2018-10-01 10:30 | 34 | 30 |  |  | 43374.4375 | 47 | 47
2018-10-01 11:00 | 36 | 32 |  |  | 43374.4583 | 47 | 47
2018-10-01 11:30 | 36 | 32 |  |  | 43374.4792 | 45 | 45
2018-10-01 12:00 | 36 | 32 |  |  | 43374.5 | 45 | 45
2018-10-01 12:30 | 35 | 32 |  |  | 43374.5208 | 47 | 47
2018-10-01 13:00 | 38 | 35 |  |  | 43374.5417 | 50 | 50
2018-10-01 13:30 | 39 | 36 |  |  | 43374.5625 | 49 | 49
2018-10-01 14:00 | 39 | 36 |  |  | 43374.5833 | 49 | 49
2018-10-01 14:30 | 40 | 36 |  |  | 43374.6042 | 48 | 48
2018-10-01 15:00 | 44 | 41 |  |  | 43374.625 | 54 | 54
2018-10-01 15:30 | 44 | 41 |  |  | 43374.6458 | 56 | 56
2018-10-01 16:00 | 47 | 44 |  |  | 43374.6667 | 58 | 58
2018-10-01 16:30 | 46 | 43 |  |  | 43374.6875 | 59 | 59
2018-10-01 17:00 | 48 | 45 |  |  | 43374.7083 | 62 | 62
2018-10-01 17:30 | 51 | 49 |  |  | 43374.7292 | 65 | 65
2018-10-01 18:00 | 54 | 51 |  |  | 43374.75 | 67 | 67
2018-10-01 18:30 | 54 | 51 |  |  | 43374.7708 | 69 | 68
2018-10-01 19:00 | 54 | 51 |  |  | 43374.7917 | 69 | 69
2018-10-01 19:30 | 54 | 51 |  |  | 43374.8125 | 67 | 67
2018-10-01 20:00 | 54 | 51 |  |  | 43374.8333 | 67 | 67
2018-10-01 20:30 | 55 | 52 |  |  | 43374.8542 | 68 | 68
2018-10-01 21:00 | 52 | 48 |  |  | 43374.875 | 64 | 64
2018-10-01 21:30 | 50 | 46 |  |  | 43374.8958 | 62 | 62
2018-10-01 22:00 | 49 | 45 |  |  | 43374.9167 | 61 | 61
2018-10-01 22:30 | 47 | 42 |  |  | 43374.9375 | 59 | 59
2018-10-01 23:00 | 47 | 42 |  |  | 43374.9583 | 58 | 57
2018-10-01 23:30 | 45 | 40 |  |  | 43374.9792 | 55 | 55
2018-10-02 | 42 | 36 |  |  | 43375 | 51 | 50
2018-10-02 00:30 | 40 | 32 |  |  | 43375.0208 | 46 | 46
2018-10-02 01:00 | 38 | 31 |  |  | 43375.0417 | 45 | 44
2018-10-02 01:30 | 38 | 30 |  |  | 43375.0625 | 43 | 43
2018-10-02 02:00 | 38 | 30 |  |  | 43375.0833 | 43 | 43
2018-10-02 02:30 | 36 | 28 |  |  | 43375.1042 | 43 | 42
2018-10-02 03:00 | 36 | 28 |  |  | 43375.125 | 42 | 41
2018-10-02 03:30 | 36 | 28 |  |  | 43375.1458 | 40 | 40
2018-10-02 04:00 | 36 | 29 |  |  | 43375.1667 | 42 | 41
2018-10-02 04:30 | 37 | 30 |  |  | 43375.1875 | 43 | 42
2018-10-02 05:00 | 39 | 33 |  |  | 43375.2083 | 45 | 45
2018-10-02 05:30 | 40 | 34 |  |  | 43375.2292 | 47 | 46
2018-10-02 06:00 | 41 | 37 |  |  | 43375.25 | 51 | 51
2018-10-02 06:30 | 43 | 40 |  |  | 43375.2708 | 58 | 58
2018-10-02 07:00 | 43 | 42 |  |  | 43375.2917 | 61 | 61
2018-10-02 07:30 | 45 | 44 |  |  | 43375.3125 | 67 | 67
2018-10-02 08:00 | 43 | 42 |  |  | 43375.3333 | 67 | 66
2018-10-02 08:30 | 42 | 42 |  |  | 43375.3542 | 67 | 66
2018-10-02 09:00 | 41 | 40 |  |  | 43375.375 | 65 | 63
2018-10-02 09:30 | 42 | 41 |  |  | 43375.3958 | 66 | 65
2018-10-02 10:00 | 44 | 44 |  |  | 43375.4167 | 68 | 67
2018-10-02 10:30 | 48 | 48 |  |  | 43375.4375 | 70 | 69
2018-10-02 11:00 | 51 | 51 |  |  | 43375.4583 | 71 | 70
2018-10-02 11:30 | 48 | 47 |  |  | 43375.4792 | 67 | 66
2018-10-02 12:00 | 47 | 47 |  |  | 43375.5 | 67 | 66
2018-10-02 12:30 | 46 | 45 |  |  | 43375.5208 | 66 | 65
2018-10-02 13:00 | 47 | 46 |  |  | 43375.5417 | 65 | 64
2018-10-02 13:30 | 45 | 44 |  |  | 43375.5625 | 64 | 63
2018-10-02 14:00 | 42 | 42 |  |  | 43375.5833 | 60 | 59
2018-10-02 14:30 | 45 | 45 |  |  | 43375.6042 | 65 | 64
2018-10-02 15:00 | 45 | 44 |  |  | 43375.625 | 65 | 64
2018-10-02 15:30 | 42 | 41 |  |  | 43375.6458 | 62 | 61
2018-10-02 16:00 | 42 | 41 |  |  | 43375.6667 | 62 | 62
2018-10-02 16:30 | 46 | 44 |  |  | 43375.6875 | 64 | 64
2018-10-02 17:00 | 49 | 48 |  |  | 43375.7083 | 67 | 67
2018-10-02 17:30 | 49 | 48 |  |  | 43375.7292 | 65 | 65
2018-10-02 18:00 | 50 | 48 |  |  | 43375.75 | 66 | 66
2018-10-02 18:30 | 52 | 51 |  |  | 43375.7708 | 68 | 68
2018-10-02 19:00 | 55 | 53 |  |  | 43375.7917 | 70 | 70
2018-10-02 19:30 | 55 | 53 |  |  | 43375.8125 | 69 | 69
2018-10-02 20:00 | 54 | 52 |  |  | 43375.8333 | 69 | 69
2018-10-02 20:30 | 51 | 50 |  |  | 43375.8542 | 65 | 65
2018-10-02 21:00 | 49 | 48 |  |  | 43375.875 | 61 | 61
2018-10-02 21:30 | 45 | 44 |  |  | 43375.8958 | 57 | 57
2018-10-02 22:00 | 45 | 43 |  |  | 43375.9167 | 58 | 58
2018-10-02 22:30 | 45 | 43 |  |  | 43375.9375 | 58 | 58
2018-10-02 23:00 | 43 | 40 |  |  | 43375.9583 | 53 | 53
2018-10-02 23:30 | 37 | 34 |  |  | 43375.9792 | 48 | 48
2018-10-03 | 36 | 32 |  |  | 43376 | 46 | 46
2018-10-03 00:30 | 35 | 30 |  |  | 43376.0208 | 43 | 43
2018-10-03 01:00 | 35 | 30 |  |  | 43376.0417 | 41 | 41
2018-10-03 01:30 | 34 | 28 |  |  | 43376.0625 | 40 | 39
2018-10-03 02:00 | 33 | 27 |  |  | 43376.0833 | 38 | 38
2018-10-03 02:30 | 33 | 27 |  |  | 43376.1042 | 38 | 37
2018-10-03 03:00 | 35 | 30 |  |  | 43376.125 | 40 | 40
2018-10-03 03:30 | 34 | 30 |  |  | 43376.1458 | 40 | 40
2018-10-03 04:00 | 35 | 30 |  |  | 43376.1667 | 42 | 42
2018-10-03 04:30 | 36 | 32 |  |  | 43376.1875 | 44 | 44
2018-10-03 05:00 | 39 | 35 |  |  | 43376.2083 | 47 | 47
2018-10-03 05:30 | 42 | 39 |  |  | 43376.2292 | 51 | 51
2018-10-03 06:00 | 46 | 43 |  |  | 43376.25 | 57 | 57
2018-10-03 06:30 | 52 | 50 |  |  | 43376.2708 | 66 | 66
2018-10-03 07:00 | 50 | 49 |  |  | 43376.2917 | 69 | 69
2018-10-03 07:30 | 50 | 49 |  |  | 43376.3125 | 72 | 72
2018-10-03 08:00 | 47 | 46 |  |  | 43376.3333 | 72 | 71
2018-10-03 08:30 | 46 | 46 |  |  | 43376.3542 | 71 | 70
2018-10-03 09:00 | 44 | 44 |  |  | 43376.375 | 69 | 68
2018-10-03 09:30 | 41 | 41 |  |  | 43376.3958 | 65 | 63
2018-10-03 10:00 | 40 | 40 |  |  | 43376.4167 | 64 | 62
2018-10-03 10:30 | 41 | 41 |  |  | 43376.4375 | 65 | 63
2018-10-03 11:00 | 43 | 43 |  |  | 43376.4583 | 69 | 67
2018-10-03 11:30 | 43 | 43 |  |  | 43376.4792 | 68 | 66
2018-10-03 12:00 | 38 | 38 |  |  | 43376.5 | 63 | 61
2018-10-03 12:30 | 35 | 35 |  |  | 43376.5208 | 60 | 58
2018-10-03 13:00 | 36 | 35 |  |  | 43376.5417 | 59 | 57
2018-10-03 13:30 | 35 | 35 |  |  | 43376.5625 | 59 | 56
2018-10-03 14:00 | 38 | 37 |  |  | 43376.5833 | 58 | 57
2018-10-03 14:30 | 41 | 39 |  |  | 43376.6042 | 59 | 59
2018-10-03 15:00 | 41 | 39 |  |  | 43376.625 | 59 | 59
2018-10-03 15:30 | 40 | 38 |  |  | 43376.6458 | 59 | 59
2018-10-03 16:00 | 43 | 41 |  |  | 43376.6667 | 63 | 63
2018-10-03 16:30 | 49 | 47 |  |  | 43376.6875 | 70 | 70
2018-10-03 17:00 | 53 | 50 |  |  | 43376.7083 | 73 | 73
2018-10-03 17:30 | 53 | 50 |  |  | 43376.7292 | 72 | 71
2018-10-03 18:00 | 55 | 52 |  |  | 43376.75 | 73 | 72
2018-10-03 18:30 | 57 | 54 |  |  | 43376.7708 | 74 | 73
2018-10-03 19:00 | 59 | 56 |  |  | 43376.7917 | 76 | 75
2018-10-03 19:30 | 57 | 53 |  |  | 43376.8125 | 74 | 72
2018-10-03 20:00 | 57 | 54 |  |  | 43376.8333 | 73 | 71
2018-10-03 20:30 | 58 | 55 |  |  | 43376.8542 | 72 | 71
2018-10-03 21:00 | 53 | 49 |  |  | 43376.875 | 67 | 66
2018-10-03 21:30 | 52 | 48 |  |  | 43376.8958 | 65 | 63
2018-10-03 22:00 | 51 | 47 |  |  | 43376.9167 | 64 | 63
2018-10-03 22:30 | 46 | 41 |  |  | 43376.9375 | 59 | 58
2018-10-03 23:00 | 44 | 40 |  |  | 43376.9583 | 55 | 53
2018-10-03 23:30 | 40 | 34 |  |  | 43376.9792 | 51 | 49
2018-10-04 | 37 | 30 |  |  | 43377 | 47 | 44
2018-10-04 00:30 | 37 | 30 |  |  | 43377.0208 | 46 | 44
2018-10-04 01:00 | 36 | 28 |  |  | 43377.0417 | 44 | 40
2018-10-04 01:30 | 35 | 27 |  |  | 43377.0625 | 41 | 38
2018-10-04 02:00 | 38 | 28 |  |  | 43377.0833 | 44 | 40
2018-10-04 02:30 | 39 | 29 |  |  | 43377.1042 | 45 | 41
2018-10-04 03:00 | 39 | 29 |  |  | 43377.125 | 45 | 41
2018-10-04 03:30 | 39 | 29 |  |  | 43377.1458 | 46 | 42
2018-10-04 04:00 | 38 | 28 |  |  | 43377.1667 | 44 | 40
2018-10-04 04:30 | 40 | 31 |  |  | 43377.1875 | 46 | 42
2018-10-04 05:00 | 40 | 31 |  |  | 43377.2083 | 46 | 43
2018-10-04 05:30 | 41 | 33 |  |  | 43377.2292 | 49 | 46
2018-10-04 06:00 | 45 | 39 |  |  | 43377.25 | 55 | 53
2018-10-04 06:30 | 46 | 42 |  |  | 43377.2708 | 60 | 58
2018-10-04 07:00 | 38 | 35 |  |  | 43377.2917 | 56 | 55
2018-10-04 07:30 | 42 | 40 |  |  | 43377.3125 | 61 | 61
2018-10-04 08:00 | 37 | 36 |  |  | 43377.3333 | 58 | 58
2018-10-04 08:30 | 36 | 35 |  |  | 43377.3542 | 59 | 59
2018-10-04 09:00 | 36 | 36 |  |  | 43377.375 | 62 | 62
2018-10-04 09:30 | 37 | 36 |  |  | 43377.3958 | 61 | 60
2018-10-04 10:00 | 36 | 35 |  |  | 43377.4167 | 60 | 60
2018-10-04 10:30 | 36 | 35 |  |  | 43377.4375 | 58 | 58
2018-10-04 11:00 | 36 | 35 |  |  | 43377.4583 | 59 | 59
2018-10-04 11:30 | 37 | 36 |  |  | 43377.4792 | 59 | 59
2018-10-04 12:00 | 37 | 36 |  |  | 43377.5 | 58 | 58
2018-10-04 12:30 | 38 | 37 |  |  | 43377.5208 | 60 | 60
2018-10-04 13:00 | 36 | 35 |  |  | 43377.5417 | 58 | 58
2018-10-04 13:30 | 36 | 35 |  |  | 43377.5625 | 57 | 57
2018-10-04 14:00 | 35 | 35 |  |  | 43377.5833 | 59 | 59
2018-10-04 14:30 | 37 | 37 |  |  | 43377.6042 | 56 | 56
2018-10-04 15:00 | 39 | 38 |  |  | 43377.625 | 61 | 60
2018-10-04 15:30 | 41 | 40 |  |  | 43377.6458 | 63 | 63
2018-10-04 16:00 | 46 | 45 |  |  | 43377.6667 | 65 | 65
2018-10-04 16:30 | 49 | 48 |  |  | 43377.6875 | 71 | 71
2018-10-04 17:00 | 53 | 52 |  |  | 43377.7083 | 73 | 73
2018-10-04 17:30 | 59 | 56 |  |  | 43377.7292 | 76 | 75
2018-10-04 18:00 | 59 | 56 |  |  | 43377.75 | 77 | 75
2018-10-04 18:30 | 62 | 58 |  |  | 43377.7708 | 79 | 77
2018-10-04 19:00 | 63 | 59 |  |  | 43377.7917 | 80 | 78
2018-10-04 19:30 | 61 | 57 |  |  | 43377.8125 | 77 | 75
2018-10-04 20:00 | 60 | 56 |  |  | 43377.8333 | 75 | 72
2018-10-04 20:30 | 56 | 52 |  |  | 43377.8542 | 71 | 68
2018-10-04 21:00 | 52 | 49 |  |  | 43377.875 | 64 | 63
2018-10-04 21:30 | 50 | 47 |  |  | 43377.8958 | 62 | 61
2018-10-04 22:00 | 50 | 46 |  |  | 43377.9167 | 62 | 61
2018-10-04 22:30 | 49 | 45 |  |  | 43377.9375 | 62 | 61
2018-10-04 23:00 | 49 | 45 |  |  | 43377.9583 | 60 | 59
2018-10-04 23:30 | 46 | 42 |  |  | 43377.9792 | 57 | 56
2018-10-05 | 43 | 38 |  |  | 43378 | 54 | 52
2018-10-05 00:30 | 43 | 36 |  |  | 43378.0208 | 51 | 49
2018-10-05 01:00 | 41 | 33 |  |  | 43378.0417 | 48 | 45
2018-10-05 01:30 | 39 | 32 |  |  | 43378.0625 | 47 | 43
2018-10-05 02:00 | 38 | 30 |  |  | 43378.0833 | 46 | 42
2018-10-05 02:30 | 38 | 29 |  |  | 43378.1042 | 45 | 41
2018-10-05 03:00 | 38 | 30 |  |  | 43378.125 | 45 | 43
2018-10-05 03:30 | 39 | 32 |  |  | 43378.1458 | 45 | 43
2018-10-05 04:00 | 38 | 31 |  |  | 43378.1667 | 44 | 42
2018-10-05 04:30 | 40 | 33 |  |  | 43378.1875 | 46 | 44
2018-10-05 05:00 | 42 | 35 |  |  | 43378.2083 | 48 | 46
2018-10-05 05:30 | 46 | 40 |  |  | 43378.2292 | 53 | 52
2018-10-05 06:00 | 47 | 43 |  |  | 43378.25 | 58 | 57
2018-10-05 06:30 | 47 | 45 |  |  | 43378.2708 | 62 | 61
2018-10-05 07:00 | 47 | 46 |  |  | 43378.2917 | 65 | 65
2018-10-05 07:30 | 47 | 47 |  |  | 43378.3125 | 71 | 71
2018-10-05 08:00 | 44 | 44 |  |  | 43378.3333 | 68 | 68
2018-10-05 08:30 | 43 | 42 |  |  | 43378.3542 | 67 | 67
2018-10-05 09:00 | 47 | 47 |  |  | 43378.375 | 71 | 71
2018-10-05 09:30 | 49 | 49 |  |  | 43378.3958 | 72 | 72
2018-10-05 10:00 | 51 | 51 |  |  | 43378.4167 | 76 | 76
2018-10-05 10:30 | 52 | 52 |  |  | 43378.4375 | 73 | 73
2018-10-05 11:00 | 52 | 51 |  |  | 43378.4583 | 71 | 71
2018-10-05 11:30 | 51 | 50 |  |  | 43378.4792 | 72 | 71
2018-10-05 12:00 | 51 | 48 |  |  | 43378.5 | 72 | 70
2018-10-05 12:30 | 50 | 47 |  |  | 43378.5208 | 73 | 71
2018-10-05 13:00 | 51 | 49 |  |  | 43378.5417 | 77 | 76
2018-10-05 13:30 | 52 | 50 |  |  | 43378.5625 | 74 | 73
2018-10-05 14:00 | 56 | 53 |  |  | 43378.5833 | 74 | 73
2018-10-05 14:30 | 58 | 56 |  |  | 43378.6042 | 78 | 77
2018-10-05 15:00 | 58 | 56 |  |  | 43378.625 | 78 | 76
2018-10-05 15:30 | 61 | 59 |  |  | 43378.6458 | 81 | 79
2018-10-05 16:00 | 62 | 59 |  |  | 43378.6667 | 82 | 79
2018-10-05 16:30 | 61 | 58 |  |  | 43378.6875 | 79 | 77
2018-10-05 17:00 | 64 | 60 |  |  | 43378.7083 | 83 | 80
2018-10-05 17:30 | 62 | 58 |  |  | 43378.7292 | 81 | 78
2018-10-05 18:00 | 60 | 56 |  |  | 43378.75 | 79 | 75
2018-10-05 18:30 | 62 | 58 |  |  | 43378.7708 | 79 | 75
2018-10-05 19:00 | 63 | 59 |  |  | 43378.7917 | 80 | 76
2018-10-05 19:30 | 60 | 55 |  |  | 43378.8125 | 76 | 72
2018-10-05 20:00 | 58 | 53 |  |  | 43378.8333 | 73 | 69
2018-10-05 20:30 | 56 | 52 |  |  | 43378.8542 | 71 | 68
2018-10-05 21:00 | 51 | 49 |  |  | 43378.875 | 65 | 64
2018-10-05 21:30 | 50 | 47 |  |  | 43378.8958 | 63 | 62
2018-10-05 22:00 | 49 | 46 |  |  | 43378.9167 | 62 | 61
2018-10-05 22:30 | 47 | 44 |  |  | 43378.9375 | 61 | 59
2018-10-05 23:00 | 48 | 44 |  |  | 43378.9583 | 60 | 58
2018-10-05 23:30 | 44 | 40 |  |  | 43378.9792 | 56 | 54
2018-10-06 | 39 | 34 |  |  | 43379 | 50 | 48
2018-10-06 00:30 | 38 | 32 |  |  | 43379.0208 | 46 | 43
2018-10-06 01:00 | 39 | 34 |  |  | 43379.0417 | 46 | 44
2018-10-06 01:30 | 39 | 33 |  |  | 43379.0625 | 46 | 43
2018-10-06 02:00 | 37 | 31 |  |  | 43379.0833 | 43 | 40
2018-10-06 02:30 | 36 | 30 |  |  | 43379.1042 | 43 | 40
2018-10-06 03:00 | 36 | 29 |  |  | 43379.125 | 42 | 39
2018-10-06 03:30 | 36 | 29 |  |  | 43379.1458 | 42 | 39
2018-10-06 04:00 | 36 | 30 |  |  | 43379.1667 | 42 | 39
2018-10-06 04:30 | 37 | 31 |  |  | 43379.1875 | 44 | 41
2018-10-06 05:00 | 37 | 31 |  |  | 43379.2083 | 43 | 40
2018-10-06 05:30 | 37 | 31 |  |  | 43379.2292 | 44 | 41
2018-10-06 06:00 | 40 | 34 |  |  | 43379.25 | 47 | 45
2018-10-06 06:30 | 43 | 37 |  |  | 43379.2708 | 51 | 48
2018-10-06 07:00 | 43 | 37 |  |  | 43379.2917 | 54 | 51
2018-10-06 07:30 | 43 | 38 |  |  | 43379.3125 | 54 | 52
2018-10-06 08:00 | 41 | 37 |  |  | 43379.3333 | 54 | 52
2018-10-06 08:30 | 42 | 39 |  |  | 43379.3542 | 57 | 56
2018-10-06 09:00 | 43 | 40 |  |  | 43379.375 | 56 | 55
2018-10-06 09:30 | 37 | 35 |  |  | 43379.3958 | 49 | 49
2018-10-06 10:00 | 38 | 36 |  |  | 43379.4167 | 51 | 50
2018-10-06 10:30 | 37 | 35 |  |  | 43379.4375 | 50 | 49
2018-10-06 11:00 | 45 | 44 |  |  | 43379.4583 | 56 | 55
2018-10-06 11:30 | 47 | 45 |  |  | 43379.4792 | 59 | 59
2018-10-06 12:00 | 45 | 43 |  |  | 43379.5 | 59 | 59
2018-10-06 12:30 | 50 | 48 |  |  | 43379.5208 | 63 | 62
2018-10-06 13:00 | 50 | 48 |  |  | 43379.5417 | 68 | 67
2018-10-06 13:30 | 48 | 45 |  |  | 43379.5625 | 66 | 65
2018-10-06 14:00 | 45 | 42 |  |  | 43379.5833 | 57 | 57
2018-10-06 14:30 | 46 | 43 |  |  | 43379.6042 | 56 | 56
2018-10-06 15:00 | 43 | 39 |  |  | 43379.625 | 57 | 57
2018-10-06 15:30 | 49 | 46 |  |  | 43379.6458 | 61 | 60
2018-10-06 16:00 | 53 | 51 |  |  | 43379.6667 | 65 | 64
2018-10-06 16:30 | 55 | 52 |  |  | 43379.6875 | 67 | 66
2018-10-06 17:00 | 57 | 55 |  |  | 43379.7083 | 70 | 69
2018-10-06 17:30 | 57 | 55 |  |  | 43379.7292 | 69 | 69
2018-10-06 18:00 | 56 | 54 |  |  | 43379.75 | 69 | 68
2018-10-06 18:30 | 53 | 52 |  |  | 43379.7708 | 66 | 66
2018-10-06 19:00 | 55 | 53 |  |  | 43379.7917 | 68 | 68
2018-10-06 19:30 | 55 | 53 |  |  | 43379.8125 | 68 | 68
2018-10-06 20:00 | 53 | 51 |  |  | 43379.8333 | 65 | 65
2018-10-06 20:30 | 52 | 50 |  |  | 43379.8542 | 64 | 63
2018-10-06 21:00 | 47 | 45 |  |  | 43379.875 | 59 | 59
2018-10-06 21:30 | 45 | 43 |  |  | 43379.8958 | 56 | 56
2018-10-06 22:00 | 46 | 43 |  |  | 43379.9167 | 57 | 56
2018-10-06 22:30 | 46 | 43 |  |  | 43379.9375 | 58 | 58
2018-10-06 23:00 | 49 | 46 |  |  | 43379.9583 | 60 | 59
2018-10-06 23:30 | 50 | 47 |  |  | 43379.9792 | 62 | 60
2018-10-07 | 49 | 45 |  |  | 43380 | 60 | 58
2018-10-07 00:30 | 46 | 41 |  |  | 43380.0208 | 54 | 52
2018-10-07 01:00 | 43 | 37 |  |  | 43380.0417 | 50 | 48
2018-10-07 01:30 | 39 | 35 |  |  | 43380.0625 | 49 | 45
2018-10-07 02:00 | 35 | 34 |  |  | 43380.0833 | 51 | 42
2018-10-07 02:30 | 32 | 31 |  |  | 43380.1042 | 45 | 40
2018-10-07 03:00 | 31 | 31 |  |  | 43380.125 | 44 | 40
2018-10-07 03:30 | 30 | 30 |  |  | 43380.1458 | 43 | 39
2018-10-07 04:00 | 30 | 30 |  |  | 43380.1667 | 42 | 39
2018-10-07 04:30 | 32 | 32 |  |  | 43380.1875 | 44 | 41
2018-10-07 05:00 | 33 | 33 |  |  | 43380.2083 | 44 | 41
2018-10-07 05:30 | 33 | 33 |  |  | 43380.2292 | 46 | 43
2018-10-07 06:00 | 33 | 33 |  |  | 43380.25 | 46 | 44
2018-10-07 06:30 | 34 | 33 |  |  | 43380.2708 | 49 | 46
2018-10-07 07:00 | 33 | 33 |  |  | 43380.2917 | 48 | 45
2018-10-07 07:30 | 32 | 32 |  |  | 43380.3125 | 48 | 46
2018-10-07 08:00 | 31 | 31 |  |  | 43380.3333 | 45 | 44
2018-10-07 08:30 | 33 | 33 |  |  | 43380.3542 | 48 | 47
2018-10-07 09:00 | 31 | 31 |  |  | 43380.375 | 49 | 48
2018-10-07 09:30 | 34 | 34 |  |  | 43380.3958 | 52 | 51
2018-10-07 10:00 | 35 | 35 |  |  | 43380.4167 | 51 | 51
2018-10-07 10:30 | 37 | 37 |  |  | 43380.4375 | 53 | 53
2018-10-07 11:00 | 42 | 42 |  |  | 43380.4583 | 56 | 56
2018-10-07 11:30 | 45 | 45 |  |  | 43380.4792 | 57 | 57
2018-10-07 12:00 | 45 | 45 |  |  | 43380.5 | 57 | 57
2018-10-07 12:30 | 46 | 46 |  |  | 43380.5208 | 57 | 56
2018-10-07 13:00 | 42 | 42 |  |  | 43380.5417 | 54 | 54
2018-10-07 13:30 | 40 | 39 |  |  | 43380.5625 | 55 | 55
2018-10-07 14:00 | 41 | 41 |  |  | 43380.5833 | 53 | 53
2018-10-07 14:30 | 44 | 44 |  |  | 43380.6042 | 54 | 54
2018-10-07 15:00 | 41 | 40 |  |  | 43380.625 | 51 | 50
2018-10-07 15:30 | 41 | 40 |  |  | 43380.6458 | 52 | 51
2018-10-07 16:00 | 44 | 44 |  |  | 43380.6667 | 57 | 56
2018-10-07 16:30 | 47 | 47 |  |  | 43380.6875 | 59 | 59
2018-10-07 17:00 | 48 | 48 |  |  | 43380.7083 | 61 | 61
2018-10-07 17:30 | 47 | 46 |  |  | 43380.7292 | 61 | 60
2018-10-07 18:00 | 47 | 47 |  |  | 43380.75 | 62 | 61
2018-10-07 18:30 | 52 | 52 |  |  | 43380.7708 | 67 | 66
2018-10-07 19:00 | 55 | 55 |  |  | 43380.7917 | 73 | 72
2018-10-07 19:30 | 54 | 54 |  |  | 43380.8125 | 71 | 70
2018-10-07 20:00 | 55 | 55 |  |  | 43380.8333 | 71 | 70
2018-10-07 20:30 | 55 | 54 |  |  | 43380.8542 | 70 | 69
2018-10-07 21:00 | 53 | 53 |  |  | 43380.875 | 68 | 67
2018-10-07 21:30 | 51 | 51 |  |  | 43380.8958 | 65 | 64
2018-10-07 22:00 | 52 | 52 |  |  | 43380.9167 | 68 | 66
2018-10-07 22:30 | 52 | 52 |  |  | 43380.9375 | 69 | 67
2018-10-07 23:00 | 50 | 50 |  |  | 43380.9583 | 65 | 64
2018-10-07 23:30 | 49 | 49 |  |  | 43380.9792 | 64 | 62
2018-10-08 | 43 | 43 |  |  | 43381 | 59 | 56
2018-10-08 00:30 | 38 | 38 |  |  | 43381.0208 | 52 | 49
2018-10-08 01:00 | 33 | 32 |  |  | 43381.0417 | 47 | 44
2018-10-08 01:30 | 32 | 31 |  |  | 43381.0625 | 45 | 42
2018-10-08 02:00 | 31 | 31 |  |  | 43381.0833 | 44 | 40
2018-10-08 02:30 | 30 | 30 |  |  | 43381.1042 | 43 | 39
2018-10-08 03:00 | 29 | 29 |  |  | 43381.125 | 41 | 37
2018-10-08 03:30 | 30 | 29 |  |  | 43381.1458 | 42 | 38
2018-10-08 04:00 | 29 | 28 |  |  | 43381.1667 | 41 | 36
2018-10-08 04:30 | 29 | 29 |  |  | 43381.1875 | 42 | 38
2018-10-08 05:00 | 32 | 32 |  |  | 43381.2083 | 44 | 41
2018-10-08 05:30 | 34 | 34 |  |  | 43381.2292 | 46 | 43
2018-10-08 06:00 | 38 | 38 |  |  | 43381.25 | 50 | 49
2018-10-08 06:30 | 47 | 46 |  |  | 43381.2708 | 60 | 60
2018-10-08 07:00 | 51 | 50 |  |  | 43381.2917 | 67 | 66
2018-10-08 07:30 | 52 | 52 |  |  | 43381.3125 | 74 | 73
2018-10-08 08:00 | 52 | 51 |  |  | 43381.3333 | 74 | 73
2018-10-08 08:30 | 48 | 48 |  |  | 43381.3542 | 72 | 71
2018-10-08 09:00 | 49 | 48 |  |  | 43381.375 | 71 | 70
2018-10-08 09:30 | 53 | 52 |  |  | 43381.3958 | 74 | 73
2018-10-08 10:00 | 48 | 48 |  |  | 43381.4167 | 71 | 70
2018-10-08 10:30 | 48 | 48 |  |  | 43381.4375 | 71 | 71
2018-10-08 11:00 | 56 | 55 |  |  | 43381.4583 | 75 | 75
2018-10-08 11:30 | 54 | 54 |  |  | 43381.4792 | 76 | 76
2018-10-08 12:00 | 52 | 52 |  |  | 43381.5 | 76 | 76
2018-10-08 12:30 | 53 | 52 |  |  | 43381.5208 | 77 | 77
2018-10-08 13:00 | 56 | 56 |  |  | 43381.5417 | 77 | 76
2018-10-08 13:30 | 60 | 60 |  |  | 43381.5625 | 72 | 72
2018-10-08 14:00 | 63 | 62 |  |  | 43381.5833 | 80 | 80
2018-10-08 14:30 | 56 | 55 |  |  | 43381.6042 | 82 | 82
2018-10-08 15:00 | 53 | 53 |  |  | 43381.625 | 73 | 73
2018-10-08 15:30 | 53 | 53 |  |  | 43381.6458 | 74 | 74
2018-10-08 16:00 | 56 | 56 |  |  | 43381.6667 | 75 | 75
2018-10-08 16:30 | 55 | 54 |  |  | 43381.6875 | 74 | 74
2018-10-08 17:00 | 60 | 59 |  |  | 43381.7083 | 76 | 75
2018-10-08 17:30 | 62 | 61 |  |  | 43381.7292 | 77 | 76
2018-10-08 18:00 | 64 | 64 |  |  | 43381.75 | 79 | 79
2018-10-08 18:30 | 66 | 65 |  |  | 43381.7708 | 80 | 80
2018-10-08 19:00 | 66 | 65 |  |  | 43381.7917 | 80 | 80
2018-10-08 19:30 | 64 | 63 |  |  | 43381.8125 | 77 | 76
2018-10-08 20:00 | 61 | 60 |  |  | 43381.8333 | 74 | 73
2018-10-08 20:30 | 60 | 58 |  |  | 43381.8542 | 72 | 72
2018-10-08 21:00 | 57 | 56 |  |  | 43381.875 | 68 | 68
2018-10-08 21:30 | 53 | 53 |  |  | 43381.8958 | 64 | 63
2018-10-08 22:00 | 49 | 48 |  |  | 43381.9167 | 61 | 60
2018-10-08 22:30 | 48 | 47 |  |  | 43381.9375 | 60 | 60
2018-10-08 23:00 | 46 | 44 |  |  | 43381.9583 | 57 | 57
2018-10-08 23:30 | 43 | 41 |  |  | 43381.9792 | 53 | 52
2018-10-09 | 40 | 37 |  |  | 43382 | 51 | 50
2018-10-09 00:30 | 38 | 35 |  |  | 43382.0208 | 48 | 46
2018-10-09 01:00 | 32 | 31 |  |  | 43382.0417 | 44 | 40
2018-10-09 01:30 | 26 | 26 |  |  | 43382.0625 | 42 | 35
2018-10-09 02:00 | 27 | 27 |  |  | 43382.0833 | 42 | 35
2018-10-09 02:30 | 29 | 29 |  |  | 43382.1042 | 44 | 37
2018-10-09 03:00 | 29 | 29 |  |  | 43382.125 | 44 | 36
2018-10-09 03:30 | 28 | 27 |  |  | 43382.1458 | 42 | 35
2018-10-09 04:00 | 25 | 25 |  |  | 43382.1667 | 41 | 33
2018-10-09 04:30 | 26 | 26 |  |  | 43382.1875 | 42 | 35
2018-10-09 05:00 | 29 | 29 |  |  | 43382.2083 | 45 | 39
2018-10-09 05:30 | 33 | 33 |  |  | 43382.2292 | 49 | 44
2018-10-09 06:00 | 40 | 40 |  |  | 43382.25 | 55 | 51
2018-10-09 06:30 | 44 | 44 |  |  | 43382.2708 | 61 | 58
2018-10-09 07:00 | 44 | 43 |  |  | 43382.2917 | 61 | 60
2018-10-09 07:30 | 46 | 45 |  |  | 43382.3125 | 64 | 64
2018-10-09 08:00 | 49 | 47 |  |  | 43382.3333 | 68 | 67
2018-10-09 08:30 | 48 | 47 |  |  | 43382.3542 | 70 | 69
2018-10-09 09:00 | 45 | 44 |  |  | 43382.375 | 68 | 67
2018-10-09 09:30 | 41 | 40 |  |  | 43382.3958 | 63 | 63
2018-10-09 10:00 | 46 | 44 |  |  | 43382.4167 | 65 | 64
2018-10-09 10:30 | 48 | 47 |  |  | 43382.4375 | 70 | 69
2018-10-09 11:00 | 52 | 51 |  |  | 43382.4583 | 73 | 72
2018-10-09 11:30 | 52 | 50 |  |  | 43382.4792 | 73 | 73
2018-10-09 12:00 | 49 | 48 |  |  | 43382.5 | 74 | 74
2018-10-09 12:30 | 46 | 45 |  |  | 43382.5208 | 69 | 69
2018-10-09 13:00 | 49 | 48 |  |  | 43382.5417 | 75 | 75
2018-10-09 13:30 | 47 | 47 |  |  | 43382.5625 | 74 | 74
2018-10-09 14:00 | 52 | 51 |  |  | 43382.5833 | 77 | 77
2018-10-09 14:30 | 52 | 51 |  |  | 43382.6042 | 74 | 74
2018-10-09 15:00 | 54 | 54 |  |  | 43382.625 | 76 | 76
2018-10-09 15:30 | 61 | 60 |  |  | 43382.6458 | 81 | 81
2018-10-09 16:00 | 65 | 64 |  |  | 43382.6667 | 87 | 87
2018-10-09 16:30 | 66 | 63 |  |  | 43382.6875 | 85 | 85
2018-10-09 17:00 | 65 | 63 |  |  | 43382.7083 | 84 | 83
2018-10-09 17:30 | 69 | 66 |  |  | 43382.7292 | 86 | 85
2018-10-09 18:00 | 68 | 65 |  |  | 43382.75 | 84 | 83
2018-10-09 18:30 | 66 | 64 |  |  | 43382.7708 | 81 | 80
2018-10-09 19:00 | 67 | 65 |  |  | 43382.7917 | 83 | 81
2018-10-09 19:30 | 65 | 62 |  |  | 43382.8125 | 79 | 77
2018-10-09 20:00 | 63 | 62 |  |  | 43382.8333 | 76 | 76
2018-10-09 20:30 | 61 | 61 |  |  | 43382.8542 | 75 | 75
2018-10-09 21:00 | 56 | 55 |  |  | 43382.875 | 69 | 69
2018-10-09 21:30 | 54 | 53 |  |  | 43382.8958 | 66 | 66
2018-10-09 22:00 | 54 | 53 |  |  | 43382.9167 | 68 | 67
2018-10-09 22:30 | 55 | 53 |  |  | 43382.9375 | 69 | 68
2018-10-09 23:00 | 53 | 51 |  |  | 43382.9583 | 66 | 65
2018-10-09 23:30 | 51 | 49 |  |  | 43382.9792 | 62 | 61
2018-10-10 | 46 | 44 |  |  | 43383 | 58 | 56
2018-10-10 00:30 | 44 | 41 |  |  | 43383.0208 | 54 | 53
2018-10-10 01:00 | 40 | 37 |  |  | 43383.0417 | 49 | 47
2018-10-10 01:30 | 39 | 35 |  |  | 43383.0625 | 47 | 45
2018-10-10 02:00 | 40 | 36 |  |  | 43383.0833 | 48 | 45
2018-10-10 02:30 | 40 | 36 |  |  | 43383.1042 | 48 | 45
2018-10-10 03:00 | 41 | 37 |  |  | 43383.125 | 49 | 47
2018-10-10 03:30 | 43 | 38 |  |  | 43383.1458 | 50 | 47
2018-10-10 04:00 | 43 | 39 |  |  | 43383.1667 | 51 | 48
2018-10-10 04:30 | 44 | 40 |  |  | 43383.1875 | 52 | 50
2018-10-10 05:00 | 45 | 41 |  |  | 43383.2083 | 53 | 51
2018-10-10 05:30 | 42 | 39 |  |  | 43383.2292 | 52 | 50
2018-10-10 06:00 | 44 | 42 |  |  | 43383.25 | 54 | 53
2018-10-10 06:30 | 46 | 45 |  |  | 43383.2708 | 60 | 60
2018-10-10 07:00 | 45 | 44 |  |  | 43383.2917 | 62 | 62
2018-10-10 07:30 | 47 | 46 |  |  | 43383.3125 | 66 | 66
2018-10-10 08:00 | 39 | 37 |  |  | 43383.3333 | 52 | 52
2018-10-10 08:30 | 32 | 31 |  |  | 43383.3542 | 40 | 40
2018-10-10 09:00 | 33 | 32 |  |  | 43383.375 | 42 | 42
2018-10-10 09:30 | 36 | 35 |  |  | 43383.3958 | 45 | 45
2018-10-10 10:00 | 35 | 35 |  |  | 43383.4167 | 44 | 44
2018-10-10 10:30 | 33 | 32 |  |  | 43383.4375 | 42 | 42
2018-10-10 11:00 | 37 | 37 |  |  | 43383.4583 | 50 | 50
2018-10-10 11:30 | 49 | 49 |  |  | 43383.4792 | 71 | 71
2018-10-10 12:00 | 51 | 50 |  |  | 43383.5 | 74 | 74
2018-10-10 12:30 | 51 | 50 |  |  | 43383.5208 | 75 | 74
2018-10-10 13:00 | 54 | 52 |  |  | 43383.5417 | 78 | 76
2018-10-10 13:30 | 57 | 55 |  |  | 43383.5625 | 81 | 79
2018-10-10 14:00 | 59 | 57 |  |  | 43383.5833 | 83 | 81
2018-10-10 14:30 | 60 | 58 |  |  | 43383.6042 | 83 | 81
2018-10-10 15:00 | 60 | 59 |  |  | 43383.625 | 83 | 82
2018-10-10 15:30 | 64 | 62 |  |  | 43383.6458 | 85 | 84
2018-10-10 16:00 | 69 | 66 |  |  | 43383.6667 | 86 | 86
2018-10-10 16:30 | 70 | 67 |  |  | 43383.6875 | 87 | 87
2018-10-10 17:00 | 72 | 69 |  |  | 43383.7083 | 90 | 90
2018-10-10 17:30 | 74 | 71 |  |  | 43383.7292 | 90 | 90
2018-10-10 18:00 | 74 | 69 |  |  | 43383.75 | 87 | 87
2018-10-10 18:30 | 74 | 70 |  |  | 43383.7708 | 86 | 86
2018-10-10 19:00 | 75 | 72 |  |  | 43383.7917 | 86 | 86
2018-10-10 19:30 | 72 | 68 |  |  | 43383.8125 | 83 | 83
2018-10-10 20:00 | 70 | 67 |  |  | 43383.8333 | 81 | 81
2018-10-10 20:30 | 69 | 65 |  |  | 43383.8542 | 80 | 80
2018-10-10 21:00 | 68 | 64 |  |  | 43383.875 | 79 | 79
2018-10-10 21:30 | 64 | 60 |  |  | 43383.8958 | 74 | 74
2018-10-10 22:00 | 64 | 60 |  |  | 43383.9167 | 74 | 74
2018-10-10 22:30 | 63 | 58 |  |  | 43383.9375 | 72 | 72
2018-10-10 23:00 | 61 | 56 |  |  | 43383.9583 | 69 | 69
2018-10-10 23:30 | 56 | 51 |  |  | 43383.9792 | 63 | 63
2018-10-11 | 52 | 46 |  |  | 43384 | 60 | 59
2018-10-11 00:30 | 49 | 43 |  |  | 43384.0208 | 55 | 55
2018-10-11 01:00 | 47 | 41 |  |  | 43384.0417 | 52 | 52
2018-10-11 01:30 | 46 | 39 |  |  | 43384.0625 | 50 | 50
2018-10-11 02:00 | 48 | 40 |  |  | 43384.0833 | 51 | 51
2018-10-11 02:30 | 45 | 41 |  |  | 43384.1042 | 53 | 52
2018-10-11 03:00 | 45 | 42 |  |  | 43384.125 | 55 | 53
2018-10-11 03:30 | 45 | 43 |  |  | 43384.1458 | 55 | 53
2018-10-11 04:00 | 44 | 42 |  |  | 43384.1667 | 52 | 51
2018-10-11 04:30 | 41 | 38 |  |  | 43384.1875 | 48 | 47
2018-10-11 05:00 | 41 | 39 |  |  | 43384.2083 | 49 | 48
2018-10-11 05:30 | 40 | 38 |  |  | 43384.2292 | 51 | 50
2018-10-11 06:00 | 41 | 39 |  |  | 43384.25 | 53 | 52
2018-10-11 06:30 | 44 | 43 |  |  | 43384.2708 | 59 | 59
2018-10-11 07:00 | 47 | 46 |  |  | 43384.2917 | 66 | 66
2018-10-11 07:30 | 52 | 51 |  |  | 43384.3125 | 74 | 74
2018-10-11 08:00 | 52 | 52 |  |  | 43384.3333 | 74 | 74
2018-10-11 08:30 | 52 | 52 |  |  | 43384.3542 | 75 | 74
2018-10-11 09:00 | 51 | 50 |  |  | 43384.375 | 75 | 75
2018-10-11 09:30 | 51 | 51 |  |  | 43384.3958 | 73 | 73
2018-10-11 10:00 | 48 | 48 |  |  | 43384.4167 | 73 | 72
2018-10-11 10:30 | 51 | 51 |  |  | 43384.4375 | 76 | 76
2018-10-11 11:00 | 54 | 54 |  |  | 43384.4583 | 78 | 78
2018-10-11 11:30 | 56 | 55 |  |  | 43384.4792 | 77 | 77
2018-10-11 12:00 | 58 | 57 |  |  | 43384.5 | 79 | 79
2018-10-11 12:30 | 63 | 62 |  |  | 43384.5208 | 83 | 82
2018-10-11 13:00 | 68 | 68 |  |  | 43384.5417 | 86 | 86
2018-10-11 13:30 | 72 | 71 |  |  | 43384.5625 | 90 | 90
2018-10-11 14:00 | 63 | 61 |  |  | 43384.5833 | 88 | 87
2018-10-11 14:30 | 63 | 62 |  |  | 43384.6042 | 85 | 84
2018-10-11 15:00 | 67 | 66 |  |  | 43384.625 | 88 | 87
2018-10-11 15:30 | 69 | 67 |  |  | 43384.6458 | 89 | 89
2018-10-11 16:00 | 66 | 65 |  |  | 43384.6667 | 85 | 85
2018-10-11 16:30 | 65 | 62 |  |  | 43384.6875 | 83 | 82
2018-10-11 17:00 | 64 | 62 |  |  | 43384.7083 | 84 | 83
2018-10-11 17:30 | 65 | 63 |  |  | 43384.7292 | 84 | 83
2018-10-11 18:00 | 66 | 63 |  |  | 43384.75 | 83 | 81
2018-10-11 18:30 | 67 | 64 |  |  | 43384.7708 | 84 | 82
2018-10-11 19:00 | 68 | 66 |  |  | 43384.7917 | 85 | 83
2018-10-11 19:30 | 66 | 64 |  |  | 43384.8125 | 82 | 80
2018-10-11 20:00 | 66 | 63 |  |  | 43384.8333 | 81 | 79
2018-10-11 20:30 | 64 | 62 |  |  | 43384.8542 | 80 | 77
2018-10-11 21:00 | 60 | 60 |  |  | 43384.875 | 74 | 74
2018-10-11 21:30 | 55 | 55 |  |  | 43384.8958 | 69 | 69
2018-10-11 22:00 | 57 | 57 |  |  | 43384.9167 | 71 | 71
2018-10-11 22:30 | 58 | 58 |  |  | 43384.9375 | 72 | 72
2018-10-11 23:00 | 56 | 55 |  |  | 43384.9583 | 68 | 68
2018-10-11 23:30 | 51 | 50 |  |  | 43384.9792 | 64 | 64
2018-10-12 | 45 | 44 |  |  | 43385 | 57 | 57
2018-10-12 00:30 | 43 | 42 |  |  | 43385.0208 | 54 | 54
2018-10-12 01:00 | 41 | 40 |  |  | 43385.0417 | 50 | 50
2018-10-12 01:30 | 40 | 39 |  |  | 43385.0625 | 48 | 48
2018-10-12 02:00 | 40 | 39 |  |  | 43385.0833 | 49 | 48
2018-10-12 02:30 | 38 | 36 |  |  | 43385.1042 | 47 | 47
2018-10-12 03:00 | 39 | 37 |  |  | 43385.125 | 48 | 48
2018-10-12 03:30 | 40 | 38 |  |  | 43385.1458 | 49 | 49
2018-10-12 04:00 | 40 | 39 |  |  | 43385.1667 | 49 | 49
2018-10-12 04:30 | 41 | 40 |  |  | 43385.1875 | 50 | 50
2018-10-12 05:00 | 42 | 41 |  |  | 43385.2083 | 52 | 52
2018-10-12 05:30 | 42 | 41 |  |  | 43385.2292 | 53 | 53
2018-10-12 06:00 | 41 | 41 |  |  | 43385.25 | 54 | 54
2018-10-12 06:30 | 48 | 47 |  |  | 43385.2708 | 63 | 63
2018-10-12 07:00 | 50 | 50 |  |  | 43385.2917 | 71 | 70
2018-10-12 07:30 | 54 | 54 |  |  | 43385.3125 | 76 | 75
2018-10-12 08:00 | 56 | 56 |  |  | 43385.3333 | 79 | 79
2018-10-12 08:30 | 60 | 60 |  |  | 43385.3542 | 85 | 84
2018-10-12 09:00 | 61 | 61 |  |  | 43385.375 | 87 | 86
2018-10-12 09:30 | 59 | 59 |  |  | 43385.3958 | 85 | 84
2018-10-12 10:00 | 59 | 59 |  |  | 43385.4167 | 83 | 82
2018-10-12 10:30 | 53 | 53 |  |  | 43385.4375 | 79 | 78
2018-10-12 11:00 | 53 | 53 |  |  | 43385.4583 | 78 | 77
2018-10-12 11:30 | 54 | 54 |  |  | 43385.4792 | 80 | 79
2018-10-12 12:00 | 59 | 59 |  |  | 43385.5 | 83 | 82
2018-10-12 12:30 | 60 | 60 |  |  | 43385.5208 | 84 | 83
2018-10-12 13:00 | 58 | 58 |  |  | 43385.5417 | 83 | 83
2018-10-12 13:30 | 58 | 57 |  |  | 43385.5625 | 82 | 81
2018-10-12 14:00 | 59 | 59 |  |  | 43385.5833 | 79 | 79
2018-10-12 14:30 | 61 | 60 |  |  | 43385.6042 | 81 | 80
2018-10-12 15:00 | 60 | 59 |  |  | 43385.625 | 80 | 80
2018-10-12 15:30 | 59 | 59 |  |  | 43385.6458 | 80 | 80
2018-10-12 16:00 | 58 | 58 |  |  | 43385.6667 | 80 | 79
2018-10-12 16:30 | 60 | 59 |  |  | 43385.6875 | 80 | 80
2018-10-12 17:00 | 61 | 61 |  |  | 43385.7083 | 81 | 81
2018-10-12 17:30 | 62 | 61 |  |  | 43385.7292 | 81 | 81
2018-10-12 18:00 | 60 | 59 |  |  | 43385.75 | 78 | 78
2018-10-12 18:30 | 61 | 60 |  |  | 43385.7708 | 78 | 78
2018-10-12 19:00 | 61 | 61 |  |  | 43385.7917 | 78 | 78
2018-10-12 19:30 | 59 | 58 |  |  | 43385.8125 | 76 | 76
2018-10-12 20:00 | 59 | 59 |  |  | 43385.8333 | 75 | 75
2018-10-12 20:30 | 61 | 60 |  |  | 43385.8542 | 76 | 76
2018-10-12 21:00 | 57 | 57 |  |  | 43385.875 | 71 | 71
2018-10-12 21:30 | 53 | 53 |  |  | 43385.8958 | 68 | 68
2018-10-12 22:00 | 51 | 50 |  |  | 43385.9167 | 66 | 66
2018-10-12 22:30 | 51 | 49 |  |  | 43385.9375 | 66 | 66
2018-10-12 23:00 | 49 | 47 |  |  | 43385.9583 | 62 | 62
2018-10-12 23:30 | 46 | 45 |  |  | 43385.9792 | 59 | 59
2018-10-13 | 43 | 42 |  |  | 43386 | 56 | 55
2018-10-13 00:30 | 41 | 39 |  |  | 43386.0208 | 52 | 51
2018-10-13 01:00 | 39 | 37 |  |  | 43386.0417 | 49 | 49
2018-10-13 01:30 | 41 | 38 |  |  | 43386.0625 | 50 | 49
2018-10-13 02:00 | 43 | 36 |  |  | 43386.0833 | 55 | 47
2018-10-13 02:30 | 42 | 33 |  |  | 43386.1042 | 56 | 43
2018-10-13 03:00 | 41 | 32 |  |  | 43386.125 | 56 | 43
2018-10-13 03:30 | 41 | 32 |  |  | 43386.1458 | 56 | 42
2018-10-13 04:00 | 43 | 34 |  |  | 43386.1667 | 58 | 45
2018-10-13 04:30 | 42 | 33 |  |  | 43386.1875 | 57 | 44
2018-10-13 05:00 | 44 | 35 |  |  | 43386.2083 | 58 | 45
2018-10-13 05:30 | 44 | 36 |  |  | 43386.2292 | 59 | 46
2018-10-13 06:00 | 42 | 35 |  |  | 43386.25 | 56 | 46
2018-10-13 06:30 | 42 | 35 |  |  | 43386.2708 | 56 | 46
2018-10-13 07:00 | 43 | 37 |  |  | 43386.2917 | 59 | 50
2018-10-13 07:30 | 43 | 38 |  |  | 43386.3125 | 61 | 53
2018-10-13 08:00 | 42 | 37 |  |  | 43386.3333 | 60 | 53
2018-10-13 08:30 | 47 | 43 |  |  | 43386.3542 | 66 | 60
2018-10-13 09:00 | 55 | 52 |  |  | 43386.375 | 75 | 69
2018-10-13 09:30 | 59 | 55 |  |  | 43386.3958 | 79 | 71
2018-10-13 10:00 | 58 | 53 |  |  | 43386.4167 | 77 | 68
2018-10-13 10:30 | 55 | 50 |  |  | 43386.4375 | 76 | 67
2018-10-13 11:00 | 56 | 51 |  |  | 43386.4583 | 77 | 68
2018-10-13 11:30 | 57 | 52 |  |  | 43386.4792 | 77 | 68
2018-10-13 12:00 | 53 | 47 |  |  | 43386.5 | 73 | 62
2018-10-13 12:30 | 52 | 46 |  |  | 43386.5208 | 72 | 60
2018-10-13 13:00 | 52 | 45 |  |  | 43386.5417 | 72 | 60
2018-10-13 13:30 | 54 | 47 |  |  | 43386.5625 | 75 | 64
2018-10-13 14:00 | 55 | 48 |  |  | 43386.5833 | 75 | 64
2018-10-13 14:30 | 56 | 50 |  |  | 43386.6042 | 75 | 64
2018-10-13 15:00 | 55 | 49 |  |  | 43386.625 | 75 | 65
2018-10-13 15:30 | 57 | 50 |  |  | 43386.6458 | 77 | 66
2018-10-13 16:00 | 55 | 49 |  |  | 43386.6667 | 76 | 65
2018-10-13 16:30 | 56 | 50 |  |  | 43386.6875 | 76 | 65
2018-10-13 17:00 | 60 | 54 |  |  | 43386.7083 | 81 | 71
2018-10-13 17:30 | 58 | 52 |  |  | 43386.7292 | 79 | 68
2018-10-13 18:00 | 56 | 50 |  |  | 43386.75 | 77 | 67
2018-10-13 18:30 | 59 | 53 |  |  | 43386.7708 | 79 | 70
2018-10-13 19:00 | 59 | 54 |  |  | 43386.7917 | 79 | 70
2018-10-13 19:30 | 58 | 53 |  |  | 43386.8125 | 79 | 70
2018-10-13 20:00 | 59 | 54 |  |  | 43386.8333 | 80 | 70
2018-10-13 20:30 | 57 | 51 |  |  | 43386.8542 | 76 | 66
2018-10-13 21:00 | 52 | 46 |  |  | 43386.875 | 72 | 60
2018-10-13 21:30 | 51 | 44 |  |  | 43386.8958 | 70 | 58
2018-10-13 22:00 | 51 | 44 |  |  | 43386.9167 | 71 | 59
2018-10-13 22:30 | 52 | 45 |  |  | 43386.9375 | 73 | 61
2018-10-13 23:00 | 55 | 47 |  |  | 43386.9583 | 73 | 61
2018-10-13 23:30 | 54 | 47 |  |  | 43386.9792 | 74 | 60
2018-10-14 | 49 | 40 |  |  | 43387 | 69 | 54
2018-10-14 00:30 | 49 | 39 |  |  | 43387.0208 | 69 | 52
2018-10-14 01:00 | 47 | 35 |  |  | 43387.0417 | 65 | 47
2018-10-14 01:30 | 47 | 35 |  |  | 43387.0625 | 65 | 46
2018-10-14 02:00 | 48 | 36 |  |  | 43387.0833 | 66 | 46
2018-10-14 02:30 | 48 | 35 |  |  | 43387.1042 | 66 | 46
2018-10-14 03:00 | 50 | 36 |  |  | 43387.125 | 66 | 46
2018-10-14 03:30 | 48 | 34 |  |  | 43387.1458 | 65 | 44
2018-10-14 04:00 | 48 | 35 |  |  | 43387.1667 | 65 | 44
2018-10-14 04:30 | 50 | 36 |  |  | 43387.1875 | 67 | 45
2018-10-14 05:00 | 50 | 37 |  |  | 43387.2083 | 68 | 46
2018-10-14 05:30 | 49 | 35 |  |  | 43387.2292 | 66 | 45
2018-10-14 06:00 | 45 | 31 |  |  | 43387.25 | 62 | 43
2018-10-14 06:30 | 46 | 33 |  |  | 43387.2708 | 64 | 46
2018-10-14 07:00 | 46 | 33 |  |  | 43387.2917 | 64 | 46
2018-10-14 07:30 | 45 | 33 |  |  | 43387.3125 | 63 | 47
2018-10-14 08:00 | 46 | 36 |  |  | 43387.3333 | 66 | 51
2018-10-14 08:30 | 50 | 41 |  |  | 43387.3542 | 69 | 56
2018-10-14 09:00 | 53 | 46 |  |  | 43387.375 | 74 | 63
2018-10-14 09:30 | 55 | 50 |  |  | 43387.3958 | 75 | 67
2018-10-14 10:00 | 57 | 52 |  |  | 43387.4167 | 77 | 67
2018-10-14 10:30 | 58 | 53 |  |  | 43387.4375 | 78 | 69
2018-10-14 11:00 | 56 | 51 |  |  | 43387.4583 | 77 | 68
2018-10-14 11:30 | 58 | 53 |  |  | 43387.4792 | 75 | 66
2018-10-14 12:00 | 59 | 54 |  |  | 43387.5 | 75 | 66
2018-10-14 12:30 | 58 | 53 |  |  | 43387.5208 | 73 | 64
2018-10-14 13:00 | 57 | 51 |  |  | 43387.5417 | 72 | 63
2018-10-14 13:30 | 56 | 51 |  |  | 43387.5625 | 72 | 63
2018-10-14 14:00 | 55 | 50 |  |  | 43387.5833 | 70 | 60
2018-10-14 14:30 | 58 | 52 |  |  | 43387.6042 | 73 | 63
2018-10-14 15:00 | 57 | 51 |  |  | 43387.625 | 74 | 65
2018-10-14 15:30 | 58 | 52 |  |  | 43387.6458 | 76 | 66
2018-10-14 16:00 | 59 | 53 |  |  | 43387.6667 | 77 | 67
2018-10-14 16:30 | 59 | 53 |  |  | 43387.6875 | 77 | 67
2018-10-14 17:00 | 56 | 50 |  |  | 43387.7083 | 75 | 66
2018-10-14 17:30 | 57 | 52 |  |  | 43387.7292 | 76 | 67
2018-10-14 18:00 | 59 | 54 |  |  | 43387.75 | 77 | 69
2018-10-14 18:30 | 60 | 54 |  |  | 43387.7708 | 80 | 70
2018-10-14 19:00 | 62 | 56 |  |  | 43387.7917 | 82 | 71
2018-10-14 19:30 | 60 | 54 |  |  | 43387.8125 | 81 | 70
2018-10-14 20:00 | 61 | 55 |  |  | 43387.8333 | 81 | 70
2018-10-14 20:30 | 65 | 59 |  |  | 43387.8542 | 84 | 74
2018-10-14 21:00 | 65 | 59 |  |  | 43387.875 | 84 | 74
2018-10-14 21:30 | 62 | 56 |  |  | 43387.8958 | 80 | 70
2018-10-14 22:00 | 59 | 52 |  |  | 43387.9167 | 80 | 68
2018-10-14 22:30 | 60 | 53 |  |  | 43387.9375 | 80 | 69
2018-10-14 23:00 | 57 | 49 |  |  | 43387.9583 | 76 | 64
2018-10-14 23:30 | 54 | 45 |  |  | 43387.9792 | 73 | 59
2018-10-15 | 51 | 42 |  |  | 43388 | 69 | 55
2018-10-15 00:30 | 51 | 42 |  |  | 43388.0208 | 68 | 55
2018-10-15 01:00 | 50 | 40 |  |  | 43388.0417 | 66 | 51
2018-10-15 01:30 | 48 | 38 |  |  | 43388.0625 | 64 | 49
2018-10-15 02:00 | 48 | 38 |  |  | 43388.0833 | 65 | 48
2018-10-15 02:30 | 48 | 38 |  |  | 43388.1042 | 62 | 49
2018-10-15 03:00 | 48 | 38 |  |  | 43388.125 | 63 | 50
2018-10-15 03:30 | 48 | 39 |  |  | 43388.1458 | 63 | 50
2018-10-15 04:00 | 47 | 38 |  |  | 43388.1667 | 62 | 48
2018-10-15 04:30 | 49 | 41 |  |  | 43388.1875 | 65 | 52
2018-10-15 05:00 | 50 | 43 |  |  | 43388.2083 | 66 | 55
2018-10-15 05:30 | 49 | 43 |  |  | 43388.2292 | 64 | 53
2018-10-15 06:00 | 46 | 41 |  |  | 43388.25 | 63 | 54
2018-10-15 06:30 | 52 | 49 |  |  | 43388.2708 | 70 | 64
2018-10-15 07:00 | 58 | 54 |  |  | 43388.2917 | 81 | 73
2018-10-15 07:30 | 67 | 63 |  |  | 43388.3125 | 90 | 83
2018-10-15 08:00 | 70 | 66 |  |  | 43388.3333 | 96 | 88
2018-10-15 08:30 | 70 | 67 |  |  | 43388.3542 | 96 | 88
2018-10-15 09:00 | 68 | 65 |  |  | 43388.375 | 93 | 85
2018-10-15 09:30 | 67 | 64 |  |  | 43388.3958 | 93 | 85
2018-10-15 10:00 | 69 | 66 |  |  | 43388.4167 | 93 | 86
2018-10-15 10:30 | 69 | 66 |  |  | 43388.4375 | 93 | 85
2018-10-15 11:00 | 67 | 64 |  |  | 43388.4583 | 92 | 85
2018-10-15 11:30 | 68 | 65 |  |  | 43388.4792 | 92 | 85
2018-10-15 12:00 | 71 | 68 |  |  | 43388.5 | 94 | 87
2018-10-15 12:30 | 66 | 63 |  |  | 43388.5208 | 90 | 82
2018-10-15 13:00 | 64 | 61 |  |  | 43388.5417 | 90 | 83
2018-10-15 13:30 | 61 | 57 |  |  | 43388.5625 | 85 | 77
2018-10-15 14:00 | 64 | 61 |  |  | 43388.5833 | 86 | 78
2018-10-15 14:30 | 65 | 62 |  |  | 43388.6042 | 90 | 82
2018-10-15 15:00 | 68 | 65 |  |  | 43388.625 | 92 | 84
2018-10-15 15:30 | 68 | 65 |  |  | 43388.6458 | 94 | 85
2018-10-15 16:00 | 70 | 66 |  |  | 43388.6667 | 95 | 87
2018-10-15 16:30 | 71 | 67 |  |  | 43388.6875 | 95 | 86
2018-10-15 17:00 | 70 | 66 |  |  | 43388.7083 | 95 | 86
2018-10-15 17:30 | 73 | 69 |  |  | 43388.7292 | 98 | 88
2018-10-15 18:00 | 74 | 69 |  |  | 43388.75 | 97 | 86
2018-10-15 18:30 | 77 | 73 |  |  | 43388.7708 | 99 | 87
2018-10-15 19:00 | 79 | 75 |  |  | 43388.7917 | 102 | 90
2018-10-15 19:30 | 76 | 72 |  |  | 43388.8125 | 98 | 86
2018-10-15 20:00 | 73 | 70 |  |  | 43388.8333 | 92 | 83
2018-10-15 20:30 | 72 | 69 |  |  | 43388.8542 | 91 | 83
2018-10-15 21:00 | 69 | 65 |  |  | 43388.875 | 87 | 78
2018-10-15 21:30 | 67 | 63 |  |  | 43388.8958 | 85 | 75
2018-10-15 22:00 | 64 | 59 |  |  | 43388.9167 | 83 | 71
2018-10-15 22:30 | 62 | 56 |  |  | 43388.9375 | 81 | 70
2018-10-15 23:00 | 58 | 55 |  |  | 43388.9583 | 74 | 67
2018-10-15 23:30 | 58 | 54 |  |  | 43388.9792 | 74 | 66
2018-10-16 | 52 | 48 |  |  | 43389 | 68 | 59
2018-10-16 00:30 | 50 | 45 |  |  | 43389.0208 | 65 | 55
2018-10-16 01:00 | 50 | 44 |  |  | 43389.0417 | 65 | 54
2018-10-16 01:30 | 50 | 45 |  |  | 43389.0625 | 63 | 54
2018-10-16 02:00 | 49 | 43 |  |  | 43389.0833 | 61 | 51
2018-10-16 02:30 | 48 | 42 |  |  | 43389.1042 | 60 | 51
2018-10-16 03:00 | 48 | 43 |  |  | 43389.125 | 61 | 51
2018-10-16 03:30 | 49 | 43 |  |  | 43389.1458 | 61 | 52
2018-10-16 04:00 | 47 | 41 |  |  | 43389.1667 | 61 | 52
2018-10-16 04:30 | 47 | 42 |  |  | 43389.1875 | 62 | 52
2018-10-16 05:00 | 49 | 44 |  |  | 43389.2083 | 63 | 54
2018-10-16 05:30 | 47 | 43 |  |  | 43389.2292 | 61 | 54
2018-10-16 06:00 | 45 | 42 |  |  | 43389.25 | 60 | 54
2018-10-16 06:30 | 51 | 49 |  |  | 43389.2708 | 68 | 65
2018-10-16 07:00 | 53 | 52 |  |  | 43389.2917 | 73 | 71
2018-10-16 07:30 | 61 | 57 |  |  | 43389.3125 | 80 | 79
2018-10-16 08:00 | 59 | 56 |  |  | 43389.3333 | 79 | 79
2018-10-16 08:30 | 59 | 55 |  |  | 43389.3542 | 79 | 79
2018-10-16 09:00 | 57 | 54 |  |  | 43389.375 | 78 | 78
2018-10-16 09:30 | 57 | 54 |  |  | 43389.3958 | 79 | 79
2018-10-16 10:00 | 59 | 56 |  |  | 43389.4167 | 79 | 79
2018-10-16 10:30 | 60 | 55 |  |  | 43389.4375 | 79 | 79
2018-10-16 11:00 | 61 | 55 |  |  | 43389.4583 | 80 | 79
2018-10-16 11:30 | 62 | 57 |  |  | 43389.4792 | 81 | 80
2018-10-16 12:00 | 60 | 54 |  |  | 43389.5 | 79 | 78
2018-10-16 12:30 | 58 | 51 |  |  | 43389.5208 | 76 | 75
2018-10-16 13:00 | 56 | 49 |  |  | 43389.5417 | 74 | 73
2018-10-16 13:30 | 60 | 54 |  |  | 43389.5625 | 79 | 78
2018-10-16 14:00 | 59 | 54 |  |  | 43389.5833 | 79 | 78
2018-10-16 14:30 | 62 | 56 |  |  | 43389.6042 | 81 | 80
2018-10-16 15:00 | 63 | 57 |  |  | 43389.625 | 81 | 80
2018-10-16 15:30 | 67 | 59 |  |  | 43389.6458 | 83 | 83
2018-10-16 16:00 | 70 | 64 |  |  | 43389.6667 | 86 | 85
2018-10-16 16:30 | 72 | 65 |  |  | 43389.6875 | 87 | 87
2018-10-16 17:00 | 75 | 67 |  |  | 43389.7083 | 89 | 89
2018-10-16 17:30 | 76 | 69 |  |  | 43389.7292 | 88 | 88
2018-10-16 18:00 | 78 | 70 |  |  | 43389.75 | 88 | 88
2018-10-16 18:30 | 81 | 74 |  |  | 43389.7708 | 90 | 90
2018-10-16 19:00 | 84 | 76 |  |  | 43389.7917 | 92 | 91
2018-10-16 19:30 | 82 | 74 |  |  | 43389.8125 | 89 | 89
2018-10-16 20:00 | 80 | 71 |  |  | 43389.8333 | 86 | 86
2018-10-16 20:30 | 79 | 70 |  |  | 43389.8542 | 84 | 83
2018-10-16 21:00 | 76 | 66 |  |  | 43389.875 | 79 | 78
2018-10-16 21:30 | 75 | 63 |  |  | 43389.8958 | 75 | 75
2018-10-16 22:00 | 73 | 61 |  |  | 43389.9167 | 74 | 72
2018-10-16 22:30 | 71 | 59 |  |  | 43389.9375 | 71 | 70
2018-10-16 23:00 | 68 | 54 |  |  | 43389.9583 | 65 | 65
2018-10-16 23:30 | 63 | 50 |  |  | 43389.9792 | 61 | 61
2018-10-17 | 58 | 43 |  |  | 43390 | 55 | 54
2018-10-17 00:30 | 58 | 41 |  |  | 43390.0208 | 52 | 52
2018-10-17 01:00 | 58 | 40 |  |  | 43390.0417 | 51 | 50
2018-10-17 01:30 | 58 | 40 |  |  | 43390.0625 | 49 | 49
2018-10-17 02:00 | 58 | 40 |  |  | 43390.0833 | 50 | 49
2018-10-17 02:30 | 59 | 41 |  |  | 43390.1042 | 51 | 51
2018-10-17 03:00 | 60 | 43 |  |  | 43390.125 | 52 | 52
2018-10-17 03:30 | 57 | 39 |  |  | 43390.1458 | 48 | 48
2018-10-17 04:00 | 56 | 37 |  |  | 43390.1667 | 47 | 47
2018-10-17 04:30 | 56 | 37 |  |  | 43390.1875 | 48 | 48
2018-10-17 05:00 | 56 | 40 |  |  | 43390.2083 | 51 | 51
2018-10-17 05:30 | 57 | 41 |  |  | 43390.2292 | 52 | 52
2018-10-17 06:00 | 58 | 44 |  |  | 43390.25 | 56 | 56
2018-10-17 06:30 | 59 | 46 |  |  | 43390.2708 | 62 | 61
2018-10-17 07:00 | 58 | 50 |  |  | 43390.2917 | 69 | 69
2018-10-17 07:30 | 56 | 55 |  |  | 43390.3125 | 78 | 78
2018-10-17 08:00 | 57 | 57 |  |  | 43390.3333 | 79 | 79
2018-10-17 08:30 | 59 | 58 |  |  | 43390.3542 | 80 | 80
2018-10-17 09:00 | 58 | 57 |  |  | 43390.375 | 80 | 80
2018-10-17 09:30 | 53 | 53 |  |  | 43390.3958 | 77 | 77
2018-10-17 10:00 | 53 | 53 |  |  | 43390.4167 | 78 | 77
2018-10-17 10:30 | 55 | 55 |  |  | 43390.4375 | 81 | 81
2018-10-17 11:00 | 57 | 57 |  |  | 43390.4583 | 83 | 83
2018-10-17 11:30 | 58 | 58 |  |  | 43390.4792 | 83 | 83
2018-10-17 12:00 | 56 | 56 |  |  | 43390.5 | 80 | 79
2018-10-17 12:30 | 56 | 55 |  |  | 43390.5208 | 80 | 79
2018-10-17 13:00 | 56 | 56 |  |  | 43390.5417 | 78 | 78
2018-10-17 13:30 | 56 | 56 |  |  | 43390.5625 | 79 | 79
2018-10-17 14:00 | 60 | 59 |  |  | 43390.5833 | 82 | 81
2018-10-17 14:30 | 62 | 62 |  |  | 43390.6042 | 83 | 83
2018-10-17 15:00 | 62 | 62 |  |  | 43390.625 | 83 | 83
2018-10-17 15:30 | 59 | 59 |  |  | 43390.6458 | 79 | 79
2018-10-17 16:00 | 60 | 60 |  |  | 43390.6667 | 80 | 80
2018-10-17 16:30 | 61 | 60 |  |  | 43390.6875 | 82 | 82
2018-10-17 17:00 | 64 | 63 |  |  | 43390.7083 | 85 | 85
2018-10-17 17:30 | 66 | 65 |  |  | 43390.7292 | 84 | 84
2018-10-17 18:00 | 66 | 64 |  |  | 43390.75 | 83 | 83
2018-10-17 18:30 | 67 | 66 |  |  | 43390.7708 | 84 | 83
2018-10-17 19:00 | 69 | 68 |  |  | 43390.7917 | 85 | 85
2018-10-17 19:30 | 68 | 67 |  |  | 43390.8125 | 84 | 84
2018-10-17 20:00 | 68 | 67 |  |  | 43390.8333 | 82 | 82
2018-10-17 20:30 | 66 | 65 |  |  | 43390.8542 | 81 | 81
2018-10-17 21:00 | 62 | 61 |  |  | 43390.875 | 77 | 77
2018-10-17 21:30 | 57 | 56 |  |  | 43390.8958 | 72 | 72
2018-10-17 22:00 | 56 | 55 |  |  | 43390.9167 | 70 | 70
2018-10-17 22:30 | 54 | 53 |  |  | 43390.9375 | 68 | 67
2018-10-17 23:00 | 51 | 50 |  |  | 43390.9583 | 64 | 63
2018-10-17 23:30 | 47 | 45 |  |  | 43390.9792 | 60 | 59
2018-10-18 | 45 | 42 |  |  | 43391 | 57 | 56
2018-10-18 00:30 | 41 | 38 |  |  | 43391.0208 | 52 | 51
2018-10-18 01:00 | 38 | 35 |  |  | 43391.0417 | 47 | 46
2018-10-18 01:30 | 37 | 34 |  |  | 43391.0625 | 46 | 45
2018-10-18 02:00 | 38 | 34 |  |  | 43391.0833 | 47 | 45
2018-10-18 02:30 | 41 | 40 |  |  | 43391.1042 | 53 | 50
2018-10-18 03:00 | 40 | 40 |  |  | 43391.125 | 56 | 50
2018-10-18 03:30 | 38 | 37 |  |  | 43391.1458 | 54 | 48
2018-10-18 04:00 | 39 | 39 |  |  | 43391.1667 | 54 | 49
2018-10-18 04:30 | 39 | 38 |  |  | 43391.1875 | 55 | 49
2018-10-18 05:00 | 40 | 40 |  |  | 43391.2083 | 55 | 50
2018-10-18 05:30 | 35 | 35 |  |  | 43391.2292 | 50 | 46
2018-10-18 06:00 | 39 | 38 |  |  | 43391.25 | 51 | 49
2018-10-18 06:30 | 46 | 45 |  |  | 43391.2708 | 62 | 61
2018-10-18 07:00 | 52 | 50 |  |  | 43391.2917 | 69 | 69
2018-10-18 07:30 | 57 | 55 |  |  | 43391.3125 | 76 | 76
2018-10-18 08:00 | 56 | 54 |  |  | 43391.3333 | 75 | 75
2018-10-18 08:30 | 54 | 53 |  |  | 43391.3542 | 78 | 78
2018-10-18 09:00 | 57 | 56 |  |  | 43391.375 | 78 | 78
2018-10-18 09:30 | 55 | 54 |  |  | 43391.3958 | 80 | 80
2018-10-18 10:00 | 53 | 52 |  |  | 43391.4167 | 78 | 78
2018-10-18 10:30 | 56 | 54 |  |  | 43391.4375 | 75 | 75
2018-10-18 11:00 | 57 | 56 |  |  | 43391.4583 | 77 | 77
2018-10-18 11:30 | 56 | 54 |  |  | 43391.4792 | 76 | 76
2018-10-18 12:00 | 65 | 64 |  |  | 43391.5 | 83 | 83
2018-10-18 12:30 | 65 | 64 |  |  | 43391.5208 | 91 | 90
2018-10-18 13:00 | 53 | 53 |  |  | 43391.5417 | 85 | 84
2018-10-18 13:30 | 58 | 58 |  |  | 43391.5625 | 83 | 83
2018-10-18 14:00 | 63 | 63 |  |  | 43391.5833 | 86 | 85
2018-10-18 14:30 | 67 | 67 |  |  | 43391.6042 | 87 | 86
2018-10-18 15:00 | 65 | 65 |  |  | 43391.625 | 90 | 89
2018-10-18 15:30 | 63 | 63 |  |  | 43391.6458 | 88 | 87
2018-10-18 16:00 | 60 | 60 |  |  | 43391.6667 | 86 | 84
2018-10-18 16:30 | 60 | 60 |  |  | 43391.6875 | 84 | 83
2018-10-18 17:00 | 61 | 61 |  |  | 43391.7083 | 83 | 81
2018-10-18 17:30 | 62 | 62 |  |  | 43391.7292 | 84 | 82
2018-10-18 18:00 | 68 | 68 |  |  | 43391.75 | 88 | 86
2018-10-18 18:30 | 69 | 69 |  |  | 43391.7708 | 88 | 85
2018-10-18 19:00 | 71 | 71 |  |  | 43391.7917 | 90 | 88
2018-10-18 19:30 | 69 | 69 |  |  | 43391.8125 | 87 | 85
2018-10-18 20:00 | 64 | 64 |  |  | 43391.8333 | 81 | 79
2018-10-18 20:30 | 61 | 61 |  |  | 43391.8542 | 78 | 76
2018-10-18 21:00 | 59 | 59 |  |  | 43391.875 | 74 | 72
2018-10-18 21:30 | 54 | 54 |  |  | 43391.8958 | 69 | 67
2018-10-18 22:00 | 52 | 52 |  |  | 43391.9167 | 68 | 66
2018-10-18 22:30 | 49 | 49 |  |  | 43391.9375 | 67 | 64
2018-10-18 23:00 | 47 | 47 |  |  | 43391.9583 | 64 | 61
2018-10-18 23:30 | 43 | 43 |  |  | 43391.9792 | 60 | 55
2018-10-19 | 40 | 39 |  |  | 43392 | 57 | 52
2018-10-19 00:30 | 36 | 36 |  |  | 43392.0208 | 52 | 47
2018-10-19 01:00 | 32 | 32 |  |  | 43392.0417 | 48 | 41
2018-10-19 01:30 | 32 | 31 |  |  | 43392.0625 | 48 | 40
2018-10-19 02:00 | 32 | 31 |  |  | 43392.0833 | 47 | 39
2018-10-19 02:30 | 31 | 31 |  |  | 43392.1042 | 48 | 40
2018-10-19 03:00 | 31 | 31 |  |  | 43392.125 | 47 | 39
2018-10-19 03:30 | 32 | 31 |  |  | 43392.1458 | 48 | 40
2018-10-19 04:00 | 30 | 30 |  |  | 43392.1667 | 48 | 40
2018-10-19 04:30 | 32 | 31 |  |  | 43392.1875 | 49 | 41
2018-10-19 05:00 | 33 | 32 |  |  | 43392.2083 | 49 | 41
2018-10-19 05:30 | 33 | 33 |  |  | 43392.2292 | 50 | 43
2018-10-19 06:00 | 38 | 38 |  |  | 43392.25 | 54 | 49
2018-10-19 06:30 | 45 | 45 |  |  | 43392.2708 | 62 | 59
2018-10-19 07:00 | 48 | 48 |  |  | 43392.2917 | 71 | 67
2018-10-19 07:30 | 51 | 51 |  |  | 43392.3125 | 75 | 73
2018-10-19 08:00 | 54 | 54 |  |  | 43392.3333 | 78 | 76
2018-10-19 08:30 | 55 | 55 |  |  | 43392.3542 | 80 | 78
2018-10-19 09:00 | 54 | 54 |  |  | 43392.375 | 79 | 78
2018-10-19 09:30 | 54 | 54 |  |  | 43392.3958 | 78 | 77
2018-10-19 10:00 | 54 | 54 |  |  | 43392.4167 | 78 | 76
2018-10-19 10:30 | 57 | 57 |  |  | 43392.4375 | 81 | 80
2018-10-19 11:00 | 56 | 55 |  |  | 43392.4583 | 79 | 77
2018-10-19 11:30 | 59 | 59 |  |  | 43392.4792 | 79 | 78
2018-10-19 12:00 | 59 | 59 |  |  | 43392.5 | 83 | 81
2018-10-19 12:30 | 55 | 55 |  |  | 43392.5208 | 76 | 74
2018-10-19 13:00 | 51 | 51 |  |  | 43392.5417 | 70 | 68
2018-10-19 13:30 | 48 | 48 |  |  | 43392.5625 | 71 | 69
2018-10-19 14:00 | 52 | 52 |  |  | 43392.5833 | 72 | 71
2018-10-19 14:30 | 52 | 52 |  |  | 43392.6042 | 76 | 74
2018-10-19 15:00 | 48 | 48 |  |  | 43392.625 | 70 | 68
2018-10-19 15:30 | 48 | 48 |  |  | 43392.6458 | 70 | 68
2018-10-19 16:00 | 51 | 51 |  |  | 43392.6667 | 74 | 71
2018-10-19 16:30 | 58 | 58 |  |  | 43392.6875 | 82 | 78
2018-10-19 17:00 | 59 | 59 |  |  | 43392.7083 | 82 | 79
2018-10-19 17:30 | 58 | 58 |  |  | 43392.7292 | 79 | 76
2018-10-19 18:00 | 56 | 56 |  |  | 43392.75 | 78 | 73
2018-10-19 18:30 | 58 | 57 |  |  | 43392.7708 | 78 | 73
2018-10-19 19:00 | 59 | 59 |  |  | 43392.7917 | 79 | 74
2018-10-19 19:30 | 58 | 57 |  |  | 43392.8125 | 77 | 72
2018-10-19 20:00 | 57 | 57 |  |  | 43392.8333 | 74 | 71
2018-10-19 20:30 | 57 | 57 |  |  | 43392.8542 | 73 | 70
2018-10-19 21:00 | 54 | 54 |  |  | 43392.875 | 70 | 67
2018-10-19 21:30 | 50 | 50 |  |  | 43392.8958 | 66 | 63
2018-10-19 22:00 | 48 | 48 |  |  | 43392.9167 | 65 | 62
2018-10-19 22:30 | 48 | 48 |  |  | 43392.9375 | 65 | 62
2018-10-19 23:00 | 48 | 48 |  |  | 43392.9583 | 63 | 59
2018-10-19 23:30 | 45 | 44 |  |  | 43392.9792 | 61 | 57
2018-10-20 | 40 | 39 |  |  | 43393 | 57 | 52
2018-10-20 00:30 | 40 | 40 |  |  | 43393.0208 | 57 | 51
2018-10-20 01:00 | 38 | 37 |  |  | 43393.0417 | 54 | 47
2018-10-20 01:30 | 38 | 37 |  |  | 43393.0625 | 54 | 46
2018-10-20 02:00 | 39 | 38 |  |  | 43393.0833 | 55 | 47
2018-10-20 02:30 | 39 | 38 |  |  | 43393.1042 | 55 | 47
2018-10-20 03:00 | 40 | 39 |  |  | 43393.125 | 55 | 48
2018-10-20 03:30 | 40 | 39 |  |  | 43393.1458 | 56 | 48
2018-10-20 04:00 | 40 | 39 |  |  | 43393.1667 | 57 | 49
2018-10-20 04:30 | 39 | 37 |  |  | 43393.1875 | 56 | 48
2018-10-20 05:00 | 37 | 36 |  |  | 43393.2083 | 54 | 46
2018-10-20 05:30 | 37 | 36 |  |  | 43393.2292 | 55 | 47
2018-10-20 06:00 | 34 | 34 |  |  | 43393.25 | 58 | 45
2018-10-20 06:30 | 31 | 30 |  |  | 43393.2708 | 56 | 41
2018-10-20 07:00 | 26 | 25 |  |  | 43393.2917 | 52 | 37
2018-10-20 07:30 | 25 | 23 |  |  | 43393.3125 | 49 | 36
2018-10-20 08:00 | 29 | 26 |  |  | 43393.3333 | 49 | 37
2018-10-20 08:30 | 35 | 32 |  |  | 43393.3542 | 55 | 46
2018-10-20 09:00 | 35 | 33 |  |  | 43393.375 | 56 | 46
2018-10-20 09:30 | 35 | 33 |  |  | 43393.3958 | 56 | 46
2018-10-20 10:00 | 34 | 31 |  |  | 43393.4167 | 52 | 43
2018-10-20 10:30 | 31 | 28 |  |  | 43393.4375 | 49 | 41
2018-10-20 11:00 | 31 | 27 |  |  | 43393.4583 | 48 | 40
2018-10-20 11:30 | 33 | 29 |  |  | 43393.4792 | 50 | 42
2018-10-20 12:00 | 36 | 33 |  |  | 43393.5 | 53 | 45
2018-10-20 12:30 | 36 | 33 |  |  | 43393.5208 | 54 | 47
2018-10-20 13:00 | 36 | 34 |  |  | 43393.5417 | 53 | 45
2018-10-20 13:30 | 36 | 34 |  |  | 43393.5625 | 52 | 45
2018-10-20 14:00 | 37 | 35 |  |  | 43393.5833 | 53 | 46
2018-10-20 14:30 | 38 | 35 |  |  | 43393.6042 | 54 | 46
2018-10-20 15:00 | 38 | 36 |  |  | 43393.625 | 55 | 47
2018-10-20 15:30 | 41 | 39 |  |  | 43393.6458 | 59 | 51
2018-10-20 16:00 | 41 | 39 |  |  | 43393.6667 | 60 | 53
2018-10-20 16:30 | 44 | 42 |  |  | 43393.6875 | 62 | 55
2018-10-20 17:00 | 47 | 46 |  |  | 43393.7083 | 67 | 60
2018-10-20 17:30 | 49 | 47 |  |  | 43393.7292 | 69 | 62
2018-10-20 18:00 | 52 | 51 |  |  | 43393.75 | 72 | 66
2018-10-20 18:30 | 54 | 53 |  |  | 43393.7708 | 75 | 69
2018-10-20 19:00 | 56 | 55 |  |  | 43393.7917 | 79 | 73
2018-10-20 19:30 | 57 | 56 |  |  | 43393.8125 | 79 | 73
2018-10-20 20:00 | 53 | 52 |  |  | 43393.8333 | 74 | 68
2018-10-20 20:30 | 52 | 50 |  |  | 43393.8542 | 73 | 66
2018-10-20 21:00 | 49 | 47 |  |  | 43393.875 | 69 | 61
2018-10-20 21:30 | 44 | 43 |  |  | 43393.8958 | 64 | 55
2018-10-20 22:00 | 46 | 45 |  |  | 43393.9167 | 68 | 59
2018-10-20 22:30 | 43 | 42 |  |  | 43393.9375 | 64 | 55
2018-10-20 23:00 | 40 | 39 |  |  | 43393.9583 | 61 | 51
2018-10-20 23:30 | 39 | 38 |  |  | 43393.9792 | 60 | 50
2018-10-21 | 38 | 37 |  |  | 43394 | 61 | 49
2018-10-21 00:30 | 37 | 37 |  |  | 43394.0208 | 59 | 47
2018-10-21 01:00 | 35 | 34 |  |  | 43394.0417 | 56 | 45
2018-10-21 01:30 | 34 | 33 |  |  | 43394.0625 | 54 | 43
2018-10-21 02:00 | 33 | 32 |  |  | 43394.0833 | 53 | 41
2018-10-21 02:30 | 34 | 33 |  |  | 43394.1042 | 55 | 43
2018-10-21 03:00 | 33 | 32 |  |  | 43394.125 | 53 | 41
2018-10-21 03:30 | 34 | 32 |  |  | 43394.1458 | 51 | 42
2018-10-21 04:00 | 34 | 32 |  |  | 43394.1667 | 51 | 41
2018-10-21 04:30 | 35 | 33 |  |  | 43394.1875 | 52 | 43
2018-10-21 05:00 | 34 | 33 |  |  | 43394.2083 | 52 | 42
2018-10-21 05:30 | 32 | 30 |  |  | 43394.2292 | 50 | 40
2018-10-21 06:00 | 30 | 28 |  |  | 43394.25 | 49 | 38
2018-10-21 06:30 | 31 | 30 |  |  | 43394.2708 | 50 | 40
2018-10-21 07:00 | 29 | 27 |  |  | 43394.2917 | 49 | 39
2018-10-21 07:30 | 30 | 28 |  |  | 43394.3125 | 48 | 39
2018-10-21 08:00 | 33 | 31 |  |  | 43394.3333 | 51 | 43
2018-10-21 08:30 | 34 | 32 |  |  | 43394.3542 | 51 | 44
2018-10-21 09:00 | 35 | 32 |  |  | 43394.375 | 52 | 46
2018-10-21 09:30 | 37 | 34 |  |  | 43394.3958 | 54 | 49
2018-10-21 10:00 | 37 | 34 |  |  | 43394.4167 | 53 | 49
2018-10-21 10:30 | 34 | 30 |  |  | 43394.4375 | 48 | 43
2018-10-21 11:00 | 38 | 35 |  |  | 43394.4583 | 52 | 48
2018-10-21 11:30 | 41 | 38 |  |  | 43394.4792 | 60 | 55
2018-10-21 12:00 | 42 | 39 |  |  | 43394.5 | 57 | 52
2018-10-21 12:30 | 42 | 39 |  |  | 43394.5208 | 58 | 53
2018-10-21 13:00 | 40 | 37 |  |  | 43394.5417 | 55 | 50
2018-10-21 13:30 | 41 | 38 |  |  | 43394.5625 | 55 | 49
2018-10-21 14:00 | 49 | 47 |  |  | 43394.5833 | 64 | 59
2018-10-21 14:30 | 51 | 48 |  |  | 43394.6042 | 64 | 59
2018-10-21 15:00 | 52 | 49 |  |  | 43394.625 | 66 | 60
2018-10-21 15:30 | 51 | 48 |  |  | 43394.6458 | 68 | 63
2018-10-21 16:00 | 48 | 45 |  |  | 43394.6667 | 65 | 60
2018-10-21 16:30 | 50 | 48 |  |  | 43394.6875 | 68 | 63
2018-10-21 17:00 | 48 | 46 |  |  | 43394.7083 | 68 | 62
2018-10-21 17:30 | 44 | 42 |  |  | 43394.7292 | 63 | 57
2018-10-21 18:00 | 46 | 44 |  |  | 43394.75 | 66 | 59
2018-10-21 18:30 | 50 | 49 |  |  | 43394.7708 | 70 | 64
2018-10-21 19:00 | 53 | 51 |  |  | 43394.7917 | 72 | 66
2018-10-21 19:30 | 50 | 49 |  |  | 43394.8125 | 70 | 64
2018-10-21 20:00 | 48 | 46 |  |  | 43394.8333 | 67 | 61
2018-10-21 20:30 | 48 | 46 |  |  | 43394.8542 | 67 | 60
2018-10-21 21:00 | 46 | 44 |  |  | 43394.875 | 64 | 57
2018-10-21 21:30 | 45 | 43 |  |  | 43394.8958 | 64 | 56
2018-10-21 22:00 | 46 | 44 |  |  | 43394.9167 | 66 | 58
2018-10-21 22:30 | 47 | 46 |  |  | 43394.9375 | 68 | 59
2018-10-21 23:00 | 47 | 46 |  |  | 43394.9583 | 67 | 58
2018-10-21 23:30 | 45 | 44 |  |  | 43394.9792 | 65 | 55
2018-10-22 | 39 | 38 |  |  | 43395 | 60 | 48
2018-10-22 00:30 | 35 | 34 |  |  | 43395.0208 | 57 | 44
2018-10-22 01:00 | 30 | 29 |  |  | 43395.0417 | 51 | 38
2018-10-22 01:30 | 30 | 28 |  |  | 43395.0625 | 49 | 37
2018-10-22 02:00 | 30 | 28 |  |  | 43395.0833 | 50 | 38
2018-10-22 02:30 | 31 | 30 |  |  | 43395.1042 | 51 | 39
2018-10-22 03:00 | 35 | 33 |  |  | 43395.125 | 52 | 42
2018-10-22 03:30 | 39 | 37 |  |  | 43395.1458 | 55 | 46
2018-10-22 04:00 | 38 | 37 |  |  | 43395.1667 | 55 | 46
2018-10-22 04:30 | 39 | 38 |  |  | 43395.1875 | 55 | 46
2018-10-22 05:00 | 39 | 37 |  |  | 43395.2083 | 54 | 45
2018-10-22 05:30 | 41 | 39 |  |  | 43395.2292 | 57 | 49
2018-10-22 06:00 | 43 | 41 |  |  | 43395.25 | 60 | 52
2018-10-22 06:30 | 45 | 43 |  |  | 43395.2708 | 64 | 57
2018-10-22 07:00 | 45 | 43 |  |  | 43395.2917 | 69 | 60
2018-10-22 07:30 | 48 | 46 |  |  | 43395.3125 | 74 | 65
2018-10-22 08:00 | 49 | 47 |  |  | 43395.3333 | 77 | 69
2018-10-22 08:30 | 51 | 49 |  |  | 43395.3542 | 80 | 73
2018-10-22 09:00 | 52 | 50 |  |  | 43395.375 | 81 | 73
2018-10-22 09:30 | 50 | 48 |  |  | 43395.3958 | 80 | 72
2018-10-22 10:00 | 49 | 47 |  |  | 43395.4167 | 77 | 69
2018-10-22 10:30 | 50 | 47 |  |  | 43395.4375 | 74 | 67
2018-10-22 11:00 | 51 | 48 |  |  | 43395.4583 | 73 | 68
2018-10-22 11:30 | 51 | 48 |  |  | 43395.4792 | 74 | 68
2018-10-22 12:00 | 51 | 48 |  |  | 43395.5 | 74 | 68
2018-10-22 12:30 | 55 | 52 |  |  | 43395.5208 | 78 | 72
2018-10-22 13:00 | 57 | 54 |  |  | 43395.5417 | 79 | 74
2018-10-22 13:30 | 56 | 53 |  |  | 43395.5625 | 80 | 75
2018-10-22 14:00 | 57 | 55 |  |  | 43395.5833 | 83 | 78
2018-10-22 14:30 | 63 | 61 |  |  | 43395.6042 | 87 | 82
2018-10-22 15:00 | 67 | 65 |  |  | 43395.625 | 89 | 84
2018-10-22 15:30 | 66 | 64 |  |  | 43395.6458 | 87 | 81
2018-10-22 16:00 | 61 | 60 |  |  | 43395.6667 | 86 | 80
2018-10-22 16:30 | 62 | 62 |  |  | 43395.6875 | 87 | 81
2018-10-22 17:00 | 64 | 63 |  |  | 43395.7083 | 89 | 82
2018-10-22 17:30 | 67 | 66 |  |  | 43395.7292 | 91 | 83
2018-10-22 18:00 | 67 | 66 |  |  | 43395.75 | 91 | 82
2018-10-22 18:30 | 66 | 65 |  |  | 43395.7708 | 90 | 80
2018-10-22 19:00 | 70 | 70 |  |  | 43395.7917 | 94 | 84
2018-10-22 19:30 | 66 | 66 |  |  | 43395.8125 | 90 | 79
2018-10-22 20:00 | 63 | 62 |  |  | 43395.8333 | 84 | 74
2018-10-22 20:30 | 60 | 59 |  |  | 43395.8542 | 82 | 71
2018-10-22 21:00 | 56 | 55 |  |  | 43395.875 | 78 | 67
2018-10-22 21:30 | 54 | 52 |  |  | 43395.8958 | 70 | 63
2018-10-22 22:00 | 54 | 52 |  |  | 43395.9167 | 71 | 63
2018-10-22 22:30 | 54 | 52 |  |  | 43395.9375 | 71 | 65
2018-10-22 23:00 | 51 | 49 |  |  | 43395.9583 | 67 | 59
2018-10-22 23:30 | 49 | 47 |  |  | 43395.9792 | 67 | 58
2018-10-23 | 44 | 43 |  |  | 43396 | 64 | 54
2018-10-23 00:30 | 41 | 39 |  |  | 43396.0208 | 59 | 48
2018-10-23 01:00 | 37 | 35 |  |  | 43396.0417 | 56 | 43
2018-10-23 01:30 | 34 | 33 |  |  | 43396.0625 | 55 | 42
2018-10-23 02:00 | 33 | 32 |  |  | 43396.0833 | 53 | 40
2018-10-23 02:30 | 34 | 33 |  |  | 43396.1042 | 53 | 41
2018-10-23 03:00 | 34 | 32 |  |  | 43396.125 | 53 | 40
2018-10-23 03:30 | 35 | 33 |  |  | 43396.1458 | 53 | 41
2018-10-23 04:00 | 35 | 33 |  |  | 43396.1667 | 53 | 40
2018-10-23 04:30 | 36 | 34 |  |  | 43396.1875 | 54 | 42
2018-10-23 05:00 | 40 | 38 |  |  | 43396.2083 | 57 | 46
2018-10-23 05:30 | 40 | 39 |  |  | 43396.2292 | 57 | 48
2018-10-23 06:00 | 43 | 41 |  |  | 43396.25 | 59 | 51
2018-10-23 06:30 | 47 | 44 |  |  | 43396.2708 | 62 | 57
2018-10-23 07:00 | 48 | 45 |  |  | 43396.2917 | 65 | 61
2018-10-23 07:30 | 51 | 47 |  |  | 43396.3125 | 71 | 69
2018-10-23 08:00 | 56 | 51 |  |  | 43396.3333 | 77 | 75
2018-10-23 08:30 | 57 | 53 |  |  | 43396.3542 | 79 | 77
2018-10-23 09:00 | 57 | 52 |  |  | 43396.375 | 79 | 77
2018-10-23 09:30 | 56 | 52 |  |  | 43396.3958 | 78 | 76
2018-10-23 10:00 | 56 | 51 |  |  | 43396.4167 | 77 | 76
2018-10-23 10:30 | 57 | 52 |  |  | 43396.4375 | 77 | 76
2018-10-23 11:00 | 59 | 54 |  |  | 43396.4583 | 80 | 79
2018-10-23 11:30 | 56 | 54 |  |  | 43396.4792 | 82 | 77
2018-10-23 12:00 | 56 | 54 |  |  | 43396.5 | 84 | 78
2018-10-23 12:30 | 57 | 55 |  |  | 43396.5208 | 83 | 78
2018-10-23 13:00 | 58 | 56 |  |  | 43396.5417 | 83 | 78
2018-10-23 13:30 | 60 | 58 |  |  | 43396.5625 | 84 | 79
2018-10-23 14:00 | 60 | 58 |  |  | 43396.5833 | 86 | 81
2018-10-23 14:30 | 64 | 62 |  |  | 43396.6042 | 85 | 81
2018-10-23 15:00 | 66 | 65 |  |  | 43396.625 | 89 | 85
2018-10-23 15:30 | 65 | 61 |  |  | 43396.6458 | 85 | 82
2018-10-23 16:00 | 67 | 61 |  |  | 43396.6667 | 85 | 83
2018-10-23 16:30 | 69 | 64 |  |  | 43396.6875 | 87 | 85
2018-10-23 17:00 | 75 | 69 |  |  | 43396.7083 | 80 | 76
2018-10-23 17:30 | 74 | 70 |  |  | 43396.7292 | 80 | 76
2018-10-23 18:00 | 76 | 71 |  |  | 43396.75 | 79 | 76
2018-10-23 18:30 | 75 | 70 |  |  | 43396.7708 | 78 | 74
2018-10-23 19:00 | 77 | 72 |  |  | 43396.7917 | 79 | 75
2018-10-23 19:30 | 73 | 65 |  |  | 43396.8125 | 73 | 69
2018-10-23 20:00 | 73 | 66 |  |  | 43396.8333 | 72 | 68
2018-10-23 20:30 | 72 | 65 |  |  | 43396.8542 | 69 | 66
2018-10-23 21:00 | 72 | 62 |  |  | 43396.875 | 64 | 63
2018-10-23 21:30 | 68 | 57 |  |  | 43396.8958 | 59 | 58
2018-10-23 22:00 | 67 | 56 |  |  | 43396.9167 | 59 | 57
2018-10-23 22:30 | 66 | 56 |  |  | 43396.9375 | 59 | 57
2018-10-23 23:00 | 63 | 53 |  |  | 43396.9583 | 54 | 52
2018-10-23 23:30 | 61 | 51 |  |  | 43396.9792 | 53 | 51
2018-10-24 | 57 | 47 |  |  | 43397 | 52 | 49
2018-10-24 00:30 | 52 | 41 |  |  | 43397.0208 | 45 | 41
2018-10-24 01:00 | 49 | 38 |  |  | 43397.0417 | 44 | 39
2018-10-24 01:30 | 49 | 39 |  |  | 43397.0625 | 44 | 39
2018-10-24 02:00 | 48 | 37 |  |  | 43397.0833 | 43 | 38
2018-10-24 02:30 | 47 | 36 |  |  | 43397.1042 | 42 | 37
2018-10-24 03:00 | 47 | 37 |  |  | 43397.125 | 42 | 37
2018-10-24 03:30 | 48 | 38 |  |  | 43397.1458 | 43 | 38
2018-10-24 04:00 | 47 | 37 |  |  | 43397.1667 | 43 | 37
2018-10-24 04:30 | 48 | 38 |  |  | 43397.1875 | 43 | 38
2018-10-24 05:00 | 47 | 36 |  |  | 43397.2083 | 42 | 37
2018-10-24 05:30 | 48 | 38 |  |  | 43397.2292 | 43 | 38
2018-10-24 06:00 | 48 | 34 |  |  | 43397.25 | 39 | 35
2018-10-24 06:30 | 53 | 37 |  |  | 43397.2708 | 42 | 41
2018-10-24 07:00 | 54 | 41 |  |  | 43397.2917 | 49 | 46
2018-10-24 07:30 | 56 | 46 |  |  | 43397.3125 | 58 | 53
2018-10-24 08:00 | 59 | 49 |  |  | 43397.3333 | 64 | 59
2018-10-24 08:30 | 60 | 50 |  |  | 43397.3542 | 65 | 62
2018-10-24 09:00 | 59 | 49 |  |  | 43397.375 | 65 | 62
2018-10-24 09:30 | 62 | 51 |  |  | 43397.3958 | 68 | 66
2018-10-24 10:00 | 62 | 51 |  |  | 43397.4167 | 68 | 65
2018-10-24 10:30 | 63 | 51 |  |  | 43397.4375 | 67 | 65
2018-10-24 11:00 | 65 | 52 |  |  | 43397.4583 | 69 | 67
2018-10-24 11:30 | 67 | 54 |  |  | 43397.4792 | 70 | 68
2018-10-24 12:00 | 67 | 55 |  |  | 43397.5 | 72 | 70
2018-10-24 12:30 | 68 | 56 |  |  | 43397.5208 | 74 | 73
2018-10-24 13:00 | 68 | 58 |  |  | 43397.5417 | 76 | 73
2018-10-24 13:30 | 68 | 60 |  |  | 43397.5625 | 78 | 73
2018-10-24 14:00 | 71 | 63 |  |  | 43397.5833 | 79 | 74
2018-10-24 14:30 | 73 | 65 |  |  | 43397.6042 | 85 | 79
2018-10-24 15:00 | 73 | 67 |  |  | 43397.625 | 87 | 81
2018-10-24 15:30 | 72 | 66 |  |  | 43397.6458 | 86 | 80
2018-10-24 16:00 | 76 | 70 |  |  | 43397.6667 | 89 | 82
2018-10-24 16:30 | 79 | 74 |  |  | 43397.6875 | 91 | 83
2018-10-24 17:00 | 82 | 78 |  |  | 43397.7083 | 95 | 86
2018-10-24 17:30 | 78 | 75 |  |  | 43397.7292 | 92 | 82
2018-10-24 18:00 | 75 | 71 |  |  | 43397.75 | 87 | 77
2018-10-24 18:30 | 75 | 71 |  |  | 43397.7708 | 85 | 75
2018-10-24 19:00 | 75 | 72 |  |  | 43397.7917 | 85 | 75
2018-10-24 19:30 | 77 | 74 |  |  | 43397.8125 | 88 | 77
2018-10-24 20:00 | 80 | 77 |  |  | 43397.8333 | 90 | 79
2018-10-24 20:30 | 78 | 74 |  |  | 43397.8542 | 85 | 76
2018-10-24 21:00 | 78 | 71 |  |  | 43397.875 | 75 | 71
2018-10-24 21:30 | 77 | 68 |  |  | 43397.8958 | 70 | 68
2018-10-24 22:00 | 75 | 66 |  |  | 43397.9167 | 68 | 67
2018-10-24 22:30 | 74 | 64 |  |  | 43397.9375 | 67 | 66
2018-10-24 23:00 | 71 | 61 |  |  | 43397.9583 | 63 | 61
2018-10-24 23:30 | 66 | 56 |  |  | 43397.9792 | 59 | 57
2018-10-25 | 61 | 50 |  |  | 43398 | 55 | 52
2018-10-25 00:30 | 55 | 42 |  |  | 43398.0208 | 46 | 43
2018-10-25 01:00 | 53 | 42 |  |  | 43398.0417 | 45 | 41
2018-10-25 01:30 | 52 | 42 |  |  | 43398.0625 | 45 | 41
2018-10-25 02:00 | 51 | 39 |  |  | 43398.0833 | 44 | 40
2018-10-25 02:30 | 49 | 37 |  |  | 43398.1042 | 42 | 38
2018-10-25 03:00 | 48 | 36 |  |  | 43398.125 | 40 | 35
2018-10-25 03:30 | 47 | 35 |  |  | 43398.1458 | 40 | 36
2018-10-25 04:00 | 46 | 34 |  |  | 43398.1667 | 39 | 34
2018-10-25 04:30 | 45 | 32 |  |  | 43398.1875 | 38 | 33
2018-10-25 05:00 | 47 | 35 |  |  | 43398.2083 | 40 | 36
2018-10-25 05:30 | 47 | 34 |  |  | 43398.2292 | 39 | 35
2018-10-25 06:00 | 49 | 34 |  |  | 43398.25 | 40 | 36
2018-10-25 06:30 | 56 | 42 |  |  | 43398.2708 | 50 | 49
2018-10-25 07:00 | 64 | 50 |  |  | 43398.2917 | 59 | 59
2018-10-25 07:30 | 65 | 49 |  |  | 43398.3125 | 59 | 59
2018-10-25 08:00 | 66 | 51 |  |  | 43398.3333 | 64 | 64
2018-10-25 08:30 | 69 | 54 |  |  | 43398.3542 | 71 | 70
2018-10-25 09:00 | 73 | 59 |  |  | 43398.375 | 72 | 72
2018-10-25 09:30 | 70 | 59 |  |  | 43398.3958 | 75 | 74
2018-10-25 10:00 | 63 | 55 |  |  | 43398.4167 | 72 | 69
2018-10-25 10:30 | 59 | 53 |  |  | 43398.4375 | 71 | 63
2018-10-25 11:00 | 62 | 57 |  |  | 43398.4583 | 77 | 70
2018-10-25 11:30 | 60 | 54 |  |  | 43398.4792 | 76 | 68
2018-10-25 12:00 | 58 | 52 |  |  | 43398.5 | 74 | 65
2018-10-25 12:30 | 59 | 53 |  |  | 43398.5208 | 77 | 68
2018-10-25 13:00 | 60 | 55 |  |  | 43398.5417 | 76 | 68
2018-10-25 13:30 | 59 | 53 |  |  | 43398.5625 | 73 | 65
2018-10-25 14:00 | 62 | 57 |  |  | 43398.5833 | 77 | 68
2018-10-25 14:30 | 64 | 59 |  |  | 43398.6042 | 79 | 70
2018-10-25 15:00 | 65 | 61 |  |  | 43398.625 | 81 | 73
2018-10-25 15:30 | 68 | 64 |  |  | 43398.6458 | 85 | 76
2018-10-25 16:00 | 70 | 67 |  |  | 43398.6667 | 87 | 78
2018-10-25 16:30 | 73 | 70 |  |  | 43398.6875 | 90 | 80
2018-10-25 17:00 | 76 | 74 |  |  | 43398.7083 | 94 | 83
2018-10-25 17:30 | 76 | 74 |  |  | 43398.7292 | 91 | 81
2018-10-25 18:00 | 75 | 73 |  |  | 43398.75 | 88 | 79
2018-10-25 18:30 | 76 | 74 |  |  | 43398.7708 | 88 | 78
2018-10-25 19:00 | 80 | 77 |  |  | 43398.7917 | 92 | 82
2018-10-25 19:30 | 76 | 73 |  |  | 43398.8125 | 87 | 78
2018-10-25 20:00 | 73 | 70 |  |  | 43398.8333 | 84 | 74
2018-10-25 20:30 | 71 | 67 |  |  | 43398.8542 | 81 | 71
2018-10-25 21:00 | 70 | 64 |  |  | 43398.875 | 74 | 68
2018-10-25 21:30 | 66 | 60 |  |  | 43398.8958 | 69 | 63
2018-10-25 22:00 | 66 | 57 |  |  | 43398.9167 | 64 | 60
2018-10-25 22:30 | 65 | 55 |  |  | 43398.9375 | 61 | 58
2018-10-25 23:00 | 61 | 51 |  |  | 43398.9583 | 55 | 51
2018-10-25 23:30 | 57 | 47 |  |  | 43398.9792 | 52 | 48
2018-10-26 | 55 | 46 |  |  | 43399 | 52 | 47
2018-10-26 00:30 | 54 | 44 |  |  | 43399.0208 | 50 | 45
2018-10-26 01:00 | 52 | 43 |  |  | 43399.0417 | 48 | 44
2018-10-26 01:30 | 52 | 44 |  |  | 43399.0625 | 50 | 45
2018-10-26 02:00 | 51 | 42 |  |  | 43399.0833 | 49 | 44
2018-10-26 02:30 | 50 | 41 |  |  | 43399.1042 | 48 | 42
2018-10-26 03:00 | 51 | 42 |  |  | 43399.125 | 49 | 44
2018-10-26 03:30 | 51 | 43 |  |  | 43399.1458 | 51 | 46
2018-10-26 04:00 | 50 | 41 |  |  | 43399.1667 | 49 | 44
2018-10-26 04:30 | 50 | 41 |  |  | 43399.1875 | 49 | 44
2018-10-26 05:00 | 51 | 41 |  |  | 43399.2083 | 49 | 43
2018-10-26 05:30 | 49 | 41 |  |  | 43399.2292 | 49 | 42
2018-10-26 06:00 | 48 | 37 |  |  | 43399.25 | 46 | 40
2018-10-26 06:30 | 51 | 41 |  |  | 43399.2708 | 50 | 45
2018-10-26 07:00 | 57 | 46 |  |  | 43399.2917 | 55 | 52
2018-10-26 07:30 | 61 | 50 |  |  | 43399.3125 | 62 | 60
2018-10-26 08:00 | 63 | 52 |  |  | 43399.3333 | 66 | 64
2018-10-26 08:30 | 64 | 54 |  |  | 43399.3542 | 69 | 67
2018-10-26 09:00 | 66 | 56 |  |  | 43399.375 | 69 | 68
2018-10-26 09:30 | 67 | 55 |  |  | 43399.3958 | 70 | 69
2018-10-26 10:00 | 66 | 55 |  |  | 43399.4167 | 70 | 69
2018-10-26 10:30 | 65 | 57 |  |  | 43399.4375 | 73 | 71
2018-10-26 11:00 | 70 | 62 |  |  | 43399.4583 | 78 | 76
2018-10-26 11:30 | 70 | 62 |  |  | 43399.4792 | 79 | 77
2018-10-26 12:00 | 74 | 65 |  |  | 43399.5 | 81 | 79
2018-10-26 12:30 | 79 | 66 |  |  | 43399.5208 | 83 | 82
2018-10-26 13:00 | 81 | 68 |  |  | 43399.5417 | 85 | 84
2018-10-26 13:30 | 81 | 69 |  |  | 43399.5625 | 85 | 84
2018-10-26 14:00 | 84 | 72 |  |  | 43399.5833 | 88 | 87
2018-10-26 14:30 | 87 | 77 |  |  | 43399.6042 | 91 | 89
2018-10-26 15:00 | 88 | 80 |  |  | 43399.625 | 95 | 93
2018-10-26 15:30 | 92 | 84 |  |  | 43399.6458 | 97 | 95
2018-10-26 16:00 | 94 | 87 |  |  | 43399.6667 | 102 | 98
2018-10-26 16:30 | 94 | 89 |  |  | 43399.6875 | 105 | 99
2018-10-26 17:00 | 96 | 90 |  |  | 43399.7083 | 106 | 100
2018-10-26 17:30 | 91 | 86 |  |  | 43399.7292 | 103 | 95
2018-10-26 18:00 | 85 | 80 |  |  | 43399.75 | 96 | 90
2018-10-26 18:30 | 86 | 78 |  |  | 43399.7708 | 88 | 86
2018-10-26 19:00 | 88 | 79 |  |  | 43399.7917 | 89 | 87
2018-10-26 19:30 | 87 | 77 |  |  | 43399.8125 | 86 | 85
2018-10-26 20:00 | 87 | 76 |  |  | 43399.8333 | 84 | 83
2018-10-26 20:30 | 86 | 73 |  |  | 43399.8542 | 80 | 80
2018-10-26 21:00 | 82 | 68 |  |  | 43399.875 | 76 | 75
2018-10-26 21:30 | 77 | 64 |  |  | 43399.8958 | 70 | 70
2018-10-26 22:00 | 75 | 61 |  |  | 43399.9167 | 68 | 67
2018-10-26 22:30 | 74 | 60 |  |  | 43399.9375 | 67 | 66
2018-10-26 23:00 | 72 | 58 |  |  | 43399.9583 | 63 | 62
2018-10-26 23:30 | 69 | 54 |  |  | 43399.9792 | 60 | 59
2018-10-27 | 68 | 54 |  |  | 43400 | 61 | 60
2018-10-27 00:30 | 63 | 52 |  |  | 43400.0208 | 60 | 57
2018-10-27 01:00 | 61 | 50 |  |  | 43400.0417 | 60 | 58
2018-10-27 01:30 | 53 | 45 |  |  | 43400.0625 | 59 | 57
2018-10-27 02:00 | 52 | 45 |  |  | 43400.0833 | 58 | 57
2018-10-27 02:30 | 50 | 43 |  |  | 43400.1042 | 56 | 55
2018-10-27 03:00 | 49 | 41 |  |  | 43400.125 | 55 | 53
2018-10-27 03:30 | 49 | 42 |  |  | 43400.1458 | 55 | 54
2018-10-27 04:00 | 50 | 43 |  |  | 43400.1667 | 56 | 54
2018-10-27 04:30 | 49 | 41 |  |  | 43400.1875 | 56 | 54
2018-10-27 05:00 | 49 | 42 |  |  | 43400.2083 | 55 | 53
2018-10-27 05:30 | 47 | 40 |  |  | 43400.2292 | 54 | 53
2018-10-27 06:00 | 47 | 40 |  |  | 43400.25 | 54 | 53
2018-10-27 06:30 | 48 | 41 |  |  | 43400.2708 | 56 | 54
2018-10-27 07:00 | 47 | 40 |  |  | 43400.2917 | 56 | 54
2018-10-27 07:30 | 40 | 39 |  |  | 43400.3125 | 56 | 56
2018-10-27 08:00 | 44 | 42 |  |  | 43400.3333 | 58 | 58
2018-10-27 08:30 | 46 | 44 |  |  | 43400.3542 | 62 | 61
2018-10-27 09:00 | 47 | 46 |  |  | 43400.375 | 64 | 64
2018-10-27 09:30 | 47 | 46 |  |  | 43400.3958 | 63 | 63
2018-10-27 10:00 | 47 | 46 |  |  | 43400.4167 | 61 | 61
2018-10-27 10:30 | 47 | 45 |  |  | 43400.4375 | 60 | 60
2018-10-27 11:00 | 47 | 46 |  |  | 43400.4583 | 60 | 60
2018-10-27 11:30 | 48 | 47 |  |  | 43400.4792 | 61 | 61
2018-10-27 12:00 | 49 | 48 |  |  | 43400.5 | 62 | 62
2018-10-27 12:30 | 50 | 49 |  |  | 43400.5208 | 63 | 63
2018-10-27 13:00 | 50 | 49 |  |  | 43400.5417 | 60 | 60
2018-10-27 13:30 | 52 | 51 |  |  | 43400.5625 | 61 | 61
2018-10-27 14:00 | 52 | 51 |  |  | 43400.5833 | 61 | 61
2018-10-27 14:30 | 52 | 51 |  |  | 43400.6042 | 63 | 63
2018-10-27 15:00 | 54 | 53 |  |  | 43400.625 | 67 | 67
2018-10-27 15:30 | 55 | 54 |  |  | 43400.6458 | 67 | 67
2018-10-27 16:00 | 55 | 54 |  |  | 43400.6667 | 67 | 67
2018-10-27 16:30 | 57 | 55 |  |  | 43400.6875 | 69 | 69
2018-10-27 17:00 | 57 | 56 |  |  | 43400.7083 | 70 | 70
2018-10-27 17:30 | 56 | 55 |  |  | 43400.7292 | 69 | 69
2018-10-27 18:00 | 56 | 55 |  |  | 43400.75 | 70 | 70
2018-10-27 18:30 | 58 | 56 |  |  | 43400.7708 | 73 | 73
2018-10-27 19:00 | 60 | 59 |  |  | 43400.7917 | 76 | 76
2018-10-27 19:30 | 57 | 56 |  |  | 43400.8125 | 73 | 73
2018-10-27 20:00 | 56 | 55 |  |  | 43400.8333 | 71 | 71
2018-10-27 20:30 | 55 | 54 |  |  | 43400.8542 | 70 | 70
2018-10-27 21:00 | 52 | 51 |  |  | 43400.875 | 66 | 66
2018-10-27 21:30 | 51 | 49 |  |  | 43400.8958 | 64 | 64
2018-10-27 22:00 | 51 | 50 |  |  | 43400.9167 | 65 | 65
2018-10-27 22:30 | 51 | 50 |  |  | 43400.9375 | 65 | 65
2018-10-27 23:00 | 51 | 48 |  |  | 43400.9583 | 62 | 62
2018-10-27 23:30 | 52 | 50 |  |  | 43400.9792 | 63 | 63
2018-10-28 | 52 | 50 |  |  | 43401 | 63 | 63
2018-10-28 00:30 | 49 | 46 |  |  | 43401.0208 | 59 | 58
2018-10-28 01:00 | 48 | 44 |  |  | 43401.0417 | 57 | 56
2018-10-28 01:30 | 46 | 41 |  |  | 43401.0625 | 54 | 52
2018-10-28 02:00 | 45 | 41 |  |  | 43401.0833 | 54 | 53
2018-10-28 02:30 | 44 | 40 |  |  | 43401.1042 | 52 | 51
2018-10-28 03:00 | 43 | 38 |  |  | 43401.125 | 51 | 49
2018-10-28 03:30 | 43 | 38 |  |  | 43401.1458 | 51 | 50
2018-10-28 04:00 | 41 | 37 |  |  | 43401.1667 | 49 | 48
2018-10-28 04:30 | 43 | 38 |  |  | 43401.1875 | 50 | 50
2018-10-28 05:00 | 42 | 38 |  |  | 43401.2083 | 50 | 49
2018-10-28 05:30 | 39 | 35 |  |  | 43401.2292 | 47 | 47
2018-10-28 06:00 | 40 | 36 |  |  | 43401.25 | 49 | 49
2018-10-28 06:30 | 36 | 32 |  |  | 43401.2708 | 46 | 46
2018-10-28 07:00 | 36 | 33 |  |  | 43401.2917 | 47 | 47
2018-10-28 07:30 | 37 | 34 |  |  | 43401.3125 | 49 | 49
2018-10-28 08:00 | 36 | 33 |  |  | 43401.3333 | 48 | 48
2018-10-28 08:30 | 37 | 36 |  |  | 43401.3542 | 51 | 51
2018-10-28 09:00 | 43 | 42 |  |  | 43401.375 | 59 | 59
2018-10-28 09:30 | 39 | 38 |  |  | 43401.3958 | 54 | 54
2018-10-28 10:00 | 51 | 50 |  |  | 43401.4167 | 66 | 66
2018-10-28 10:30 | 46 | 44 |  |  | 43401.4375 | 64 | 64
2018-10-28 11:00 | 36 | 33 |  |  | 43401.4583 | 50 | 50
2018-10-28 11:30 | 36 | 34 |  |  | 43401.4792 | 49 | 49
2018-10-28 12:00 | 39 | 37 |  |  | 43401.5 | 52 | 52
2018-10-28 12:30 | 39 | 38 |  |  | 43401.5208 | 52 | 52
2018-10-28 13:00 | 41 | 40 |  |  | 43401.5417 | 55 | 55
2018-10-28 13:30 | 42 | 41 |  |  | 43401.5625 | 56 | 56
2018-10-28 14:00 | 44 | 43 |  |  | 43401.5833 | 57 | 57
2018-10-28 14:30 | 47 | 45 |  |  | 43401.6042 | 60 | 60
2018-10-28 15:00 | 49 | 48 |  |  | 43401.625 | 63 | 63
2018-10-28 15:30 | 49 | 48 |  |  | 43401.6458 | 64 | 64
2018-10-28 16:00 | 51 | 50 |  |  | 43401.6667 | 65 | 65
2018-10-28 16:30 | 51 | 51 |  |  | 43401.6875 | 67 | 67
2018-10-28 17:00 | 56 | 55 |  |  | 43401.7083 | 73 | 73
2018-10-28 17:30 | 56 | 55 |  |  | 43401.7292 | 71 | 71
2018-10-28 18:00 | 58 | 57 |  |  | 43401.75 | 73 | 73
2018-10-28 18:30 | 61 | 60 |  |  | 43401.7708 | 77 | 77
2018-10-28 19:00 | 63 | 63 |  |  | 43401.7917 | 79 | 79
2018-10-28 19:30 | 60 | 59 |  |  | 43401.8125 | 76 | 76
2018-10-28 20:00 | 59 | 57 |  |  | 43401.8333 | 75 | 74
2018-10-28 20:30 | 59 | 57 |  |  | 43401.8542 | 74 | 73
2018-10-28 21:00 | 59 | 57 |  |  | 43401.875 | 73 | 72
2018-10-28 21:30 | 57 | 55 |  |  | 43401.8958 | 71 | 70
2018-10-28 22:00 | 55 | 52 |  |  | 43401.9167 | 68 | 68
2018-10-28 22:30 | 54 | 52 |  |  | 43401.9375 | 68 | 67
2018-10-28 23:00 | 54 | 52 |  |  | 43401.9583 | 66 | 65
2018-10-28 23:30 | 51 | 48 |  |  | 43401.9792 | 63 | 62
2018-10-29 | 47 | 43 |  |  | 43402 | 59 | 57
2018-10-29 00:30 | 44 | 40 |  |  | 43402.0208 | 54 | 53
2018-10-29 01:00 | 42 | 38 |  |  | 43402.0417 | 51 | 50
2018-10-29 01:30 | 41 | 37 |  |  | 43402.0625 | 50 | 49
2018-10-29 02:00 | 41 | 37 |  |  | 43402.0833 | 49 | 48
2018-10-29 02:30 | 40 | 36 |  |  | 43402.1042 | 48 | 47
2018-10-29 03:00 | 40 | 36 |  |  | 43402.125 | 48 | 47
2018-10-29 03:30 | 41 | 36 |  |  | 43402.1458 | 49 | 48
2018-10-29 04:00 | 41 | 37 |  |  | 43402.1667 | 49 | 48
2018-10-29 04:30 | 43 | 39 |  |  | 43402.1875 | 51 | 49
2018-10-29 05:00 | 42 | 39 |  |  | 43402.2083 | 50 | 49
2018-10-29 05:30 | 43 | 41 |  |  | 43402.2292 | 52 | 51
2018-10-29 06:00 | 47 | 45 |  |  | 43402.25 | 58 | 58
2018-10-29 06:30 | 53 | 52 |  |  | 43402.2708 | 68 | 68
2018-10-29 07:00 | 55 | 55 |  |  | 43402.2917 | 76 | 76
2018-10-29 07:30 | 59 | 59 |  |  | 43402.3125 | 84 | 84
2018-10-29 08:00 | 63 | 63 |  |  | 43402.3333 | 89 | 89
2018-10-29 08:30 | 61 | 61 |  |  | 43402.3542 | 90 | 90
2018-10-29 09:00 | 62 | 62 |  |  | 43402.375 | 90 | 90
2018-10-29 09:30 | 62 | 61 |  |  | 43402.3958 | 89 | 89
2018-10-29 10:00 | 62 | 61 |  |  | 43402.4167 | 88 | 87
2018-10-29 10:30 | 61 | 60 |  |  | 43402.4375 | 85 | 85
2018-10-29 11:00 | 63 | 62 |  |  | 43402.4583 | 88 | 87
2018-10-29 11:30 | 66 | 65 |  |  | 43402.4792 | 90 | 90
2018-10-29 12:00 | 67 | 66 |  |  | 43402.5 | 91 | 90
2018-10-29 12:30 | 68 | 67 |  |  | 43402.5208 | 91 | 91
2018-10-29 13:00 | 69 | 68 |  |  | 43402.5417 | 92 | 91
2018-10-29 13:30 | 70 | 69 |  |  | 43402.5625 | 92 | 91
2018-10-29 14:00 | 68 | 67 |  |  | 43402.5833 | 90 | 90
2018-10-29 14:30 | 69 | 67 |  |  | 43402.6042 | 88 | 87
2018-10-29 15:00 | 67 | 65 |  |  | 43402.625 | 86 | 85
2018-10-29 15:30 | 68 | 66 |  |  | 43402.6458 | 87 | 86
2018-10-29 16:00 | 69 | 67 |  |  | 43402.6667 | 88 | 87
2018-10-29 16:30 | 70 | 68 |  |  | 43402.6875 | 90 | 88
2018-10-29 17:00 | 71 | 69 |  |  | 43402.7083 | 91 | 90
2018-10-29 17:30 | 71 | 69 |  |  | 43402.7292 | 89 | 88
2018-10-29 18:00 | 70 | 68 |  |  | 43402.75 | 88 | 87
2018-10-29 18:30 | 70 | 68 |  |  | 43402.7708 | 88 | 86
2018-10-29 19:00 | 71 | 70 |  |  | 43402.7917 | 88 | 86
2018-10-29 19:30 | 69 | 67 |  |  | 43402.8125 | 86 | 84
2018-10-29 20:00 | 70 | 68 |  |  | 43402.8333 | 85 | 82
2018-10-29 20:30 | 71 | 69 |  |  | 43402.8542 | 84 | 83
2018-10-29 21:00 | 67 | 67 |  |  | 43402.875 | 79 | 79
2018-10-29 21:30 | 65 | 64 |  |  | 43402.8958 | 77 | 76
2018-10-29 22:00 | 63 | 62 |  |  | 43402.9167 | 76 | 75
2018-10-29 22:30 | 60 | 59 |  |  | 43402.9375 | 74 | 73
2018-10-29 23:00 | 61 | 59 |  |  | 43402.9583 | 72 | 71
2018-10-29 23:30 | 57 | 55 |  |  | 43402.9792 | 67 | 66
2018-10-30 | 54 | 51 |  |  | 43403 | 64 | 62
2018-10-30 00:30 | 51 | 47 |  |  | 43403.0208 | 59 | 57
2018-10-30 01:00 | 48 | 43 |  |  | 43403.0417 | 56 | 53
2018-10-30 01:30 | 47 | 43 |  |  | 43403.0625 | 53 | 51
2018-10-30 02:00 | 44 | 41 |  |  | 43403.0833 | 50 | 50
2018-10-30 02:30 | 44 | 41 |  |  | 43403.1042 | 50 | 49
2018-10-30 03:00 | 42 | 39 |  |  | 43403.125 | 49 | 48
2018-10-30 03:30 | 41 | 38 |  |  | 43403.1458 | 50 | 49
2018-10-30 04:00 | 43 | 39 |  |  | 43403.1667 | 50 | 50
2018-10-30 04:30 | 45 | 43 |  |  | 43403.1875 | 53 | 52
2018-10-30 05:00 | 47 | 45 |  |  | 43403.2083 | 55 | 54
2018-10-30 05:30 | 49 | 46 |  |  | 43403.2292 | 57 | 57
2018-10-30 06:00 | 48 | 46 |  |  | 43403.25 | 59 | 59
2018-10-30 06:30 | 49 | 48 |  |  | 43403.2708 | 64 | 64
2018-10-30 07:00 | 50 | 50 |  |  | 43403.2917 | 69 | 69
2018-10-30 07:30 | 50 | 49 |  |  | 43403.3125 | 72 | 72
2018-10-30 08:00 | 50 | 50 |  |  | 43403.3333 | 75 | 74
2018-10-30 08:30 | 54 | 53 |  |  | 43403.3542 | 80 | 79
2018-10-30 09:00 | 56 | 56 |  |  | 43403.375 | 83 | 83
2018-10-30 09:30 | 56 | 56 |  |  | 43403.3958 | 82 | 82
2018-10-30 10:00 | 56 | 56 |  |  | 43403.4167 | 80 | 80
2018-10-30 10:30 | 55 | 55 |  |  | 43403.4375 | 78 | 78
2018-10-30 11:00 | 54 | 54 |  |  | 43403.4583 | 80 | 80
2018-10-30 11:30 | 53 | 53 |  |  | 43403.4792 | 82 | 82
2018-10-30 12:00 | 56 | 56 |  |  | 43403.5 | 80 | 80
2018-10-30 12:30 | 56 | 56 |  |  | 43403.5208 | 78 | 78
2018-10-30 13:00 | 56 | 56 |  |  | 43403.5417 | 79 | 78
2018-10-30 13:30 | 57 | 57 |  |  | 43403.5625 | 79 | 78
2018-10-30 14:00 | 60 | 60 |  |  | 43403.5833 | 81 | 81
2018-10-30 14:30 | 61 | 61 |  |  | 43403.6042 | 81 | 81
2018-10-30 15:00 | 56 | 55 |  |  | 43403.625 | 76 | 76
2018-10-30 15:30 | 55 | 55 |  |  | 43403.6458 | 75 | 75
2018-10-30 16:00 | 59 | 58 |  |  | 43403.6667 | 80 | 80
2018-10-30 16:30 | 61 | 60 |  |  | 43403.6875 | 83 | 83
2018-10-30 17:00 | 65 | 64 |  |  | 43403.7083 | 85 | 85
2018-10-30 17:30 | 66 | 65 |  |  | 43403.7292 | 85 | 85
2018-10-30 18:00 | 66 | 65 |  |  | 43403.75 | 83 | 83
2018-10-30 18:30 | 68 | 67 |  |  | 43403.7708 | 82 | 82
2018-10-30 19:00 | 69 | 69 |  |  | 43403.7917 | 84 | 84
2018-10-30 19:30 | 67 | 67 |  |  | 43403.8125 | 82 | 82
2018-10-30 20:00 | 66 | 65 |  |  | 43403.8333 | 80 | 80
2018-10-30 20:30 | 64 | 64 |  |  | 43403.8542 | 78 | 78
2018-10-30 21:00 | 61 | 60 |  |  | 43403.875 | 73 | 73
2018-10-30 21:30 | 57 | 56 |  |  | 43403.8958 | 69 | 69
2018-10-30 22:00 | 55 | 54 |  |  | 43403.9167 | 67 | 67
2018-10-30 22:30 | 53 | 52 |  |  | 43403.9375 | 66 | 66
2018-10-30 23:00 | 52 | 50 |  |  | 43403.9583 | 63 | 62
2018-10-30 23:30 | 49 | 47 |  |  | 43403.9792 | 59 | 59
2018-10-31 | 45 | 43 |  |  | 43404 | 56 | 56
2018-10-31 00:30 | 44 | 42 |  |  | 43404.0208 | 53 | 52
2018-10-31 01:00 | 42 | 39 |  |  | 43404.0417 | 49 | 48
2018-10-31 01:30 | 41 | 38 |  |  | 43404.0625 | 47 | 46
2018-10-31 02:00 | 40 | 37 |  |  | 43404.0833 | 46 | 45
2018-10-31 02:30 | 38 | 35 |  |  | 43404.1042 | 45 | 45
2018-10-31 03:00 | 37 | 34 |  |  | 43404.125 | 44 | 43
2018-10-31 03:30 | 38 | 35 |  |  | 43404.1458 | 45 | 44
2018-10-31 04:00 | 36 | 33 |  |  | 43404.1667 | 43 | 43
2018-10-31 04:30 | 37 | 35 |  |  | 43404.1875 | 45 | 44
2018-10-31 05:00 | 40 | 38 |  |  | 43404.2083 | 48 | 47
2018-10-31 05:30 | 43 | 41 |  |  | 43404.2292 | 51 | 51
2018-10-31 06:00 | 43 | 42 |  |  | 43404.25 | 53 | 53
2018-10-31 06:30 | 45 | 45 |  |  | 43404.2708 | 61 | 61
2018-10-31 07:00 | 52 | 52 |  |  | 43404.2917 | 74 | 74
2018-10-31 07:30 | 53 | 53 |  |  | 43404.3125 | 75 | 75
2018-10-31 08:00 | 51 | 51 |  |  | 43404.3333 | 74 | 74
2018-10-31 08:30 | 50 | 50 |  |  | 43404.3542 | 75 | 75
2018-10-31 09:00 | 48 | 48 |  |  | 43404.375 | 75 | 74
2018-10-31 09:30 | 51 | 51 |  |  | 43404.3958 | 78 | 78
2018-10-31 10:00 | 49 | 49 |  |  | 43404.4167 | 75 | 75
2018-10-31 10:30 | 46 | 46 |  |  | 43404.4375 | 73 | 73
2018-10-31 11:00 | 45 | 45 |  |  | 43404.4583 | 72 | 72
2018-10-31 11:30 | 48 | 47 |  |  | 43404.4792 | 73 | 73
2018-10-31 12:00 | 48 | 48 |  |  | 43404.5 | 71 | 71
2018-10-31 12:30 | 49 | 49 |  |  | 43404.5208 | 73 | 73
2018-10-31 13:00 | 52 | 52 |  |  | 43404.5417 | 77 | 76
2018-10-31 13:30 | 51 | 51 |  |  | 43404.5625 | 75 | 74
2018-10-31 14:00 | 51 | 51 |  |  | 43404.5833 | 74 | 73
2018-10-31 14:30 | 52 | 52 |  |  | 43404.6042 | 74 | 74
2018-10-31 15:00 | 55 | 55 |  |  | 43404.625 | 78 | 77
2018-10-31 15:30 | 58 | 57 |  |  | 43404.6458 | 80 | 80
2018-10-31 16:00 | 59 | 58 |  |  | 43404.6667 | 83 | 82
2018-10-31 16:30 | 67 | 66 |  |  | 43404.6875 | 88 | 87
2018-10-31 17:00 | 71 | 69 |  |  | 43404.7083 | 91 | 90
2018-10-31 17:30 | 72 | 70 |  |  | 43404.7292 | 91 | 90
2018-10-31 18:00 | 70 | 68 |  |  | 43404.75 | 90 | 87
2018-10-31 18:30 | 70 | 68 |  |  | 43404.7708 | 88 | 85
2018-10-31 19:00 | 75 | 73 |  |  | 43404.7917 | 93 | 90
2018-10-31 19:30 | 72 | 70 |  |  | 43404.8125 | 90 | 87
2018-10-31 20:00 | 73 | 71 |  |  | 43404.8333 | 90 | 87
2018-10-31 20:30 | 72 | 70 |  |  | 43404.8542 | 88 | 86
2018-10-31 21:00 | 69 | 68 |  |  | 43404.875 | 83 | 83
2018-10-31 21:30 | 67 | 66 |  |  | 43404.8958 | 80 | 79
2018-10-31 22:00 | 66 | 64 |  |  | 43404.9167 | 79 | 78
2018-10-31 22:30 | 65 | 63 |  |  | 43404.9375 | 78 | 77
2018-10-31 23:00 | 64 | 61 |  |  | 43404.9583 | 74 | 73
2018-10-31 23:30 | 60 | 57 |  |  | 43404.9792 | 71 | 69
2018-11-01 | 56 | 52 |  |  | 43405 | 65 | 63
2018-11-01 00:30 | 53 | 49 |  |  | 43405.0208 | 61 | 59
2018-11-01 01:00 | 50 | 45 |  |  | 43405.0417 | 57 | 54
2018-11-01 01:30 | 47 | 42 |  |  | 43405.0625 | 53 | 51
2018-11-01 02:00 | 45 | 40 |  |  | 43405.0833 | 51 | 49
2018-11-01 02:30 | 45 | 39 |  |  | 43405.1042 | 50 | 48
2018-11-01 03:00 | 45 | 39 |  |  | 43405.125 | 50 | 48
2018-11-01 03:30 | 44 | 38 |  |  | 43405.1458 | 49 | 46
2018-11-01 04:00 | 44 | 37 |  |  | 43405.1667 | 48 | 46
2018-11-01 04:30 | 42 | 37 |  |  | 43405.1875 | 49 | 47
2018-11-01 05:00 | 44 | 39 |  |  | 43405.2083 | 51 | 48
2018-11-01 05:30 | 44 | 40 |  |  | 43405.2292 | 54 | 51
2018-11-01 06:00 | 46 | 42 |  |  | 43405.25 | 57 | 55
2018-11-01 06:30 | 48 | 47 |  |  | 43405.2708 | 63 | 63
2018-11-01 07:00 | 48 | 46 |  |  | 43405.2917 | 67 | 66
2018-11-01 07:30 | 52 | 50 |  |  | 43405.3125 | 73 | 72
2018-11-01 08:00 | 52 | 51 |  |  | 43405.3333 | 75 | 75
2018-11-01 08:30 | 53 | 51 |  |  | 43405.3542 | 78 | 77
2018-11-01 09:00 | 52 | 51 |  |  | 43405.375 | 78 | 78
2018-11-01 09:30 | 54 | 53 |  |  | 43405.3958 | 81 | 80
2018-11-01 10:00 | 53 | 52 |  |  | 43405.4167 | 78 | 77
2018-11-01 10:30 | 52 | 51 |  |  | 43405.4375 | 75 | 74
2018-11-01 11:00 | 51 | 49 |  |  | 43405.4583 | 73 | 72
2018-11-01 11:30 | 50 | 49 |  |  | 43405.4792 | 72 | 71
2018-11-01 12:00 | 50 | 49 |  |  | 43405.5 | 73 | 72
2018-11-01 12:30 | 51 | 49 |  |  | 43405.5208 | 74 | 73
2018-11-01 13:00 | 49 | 47 |  |  | 43405.5417 | 71 | 71
2018-11-01 13:30 | 49 | 48 |  |  | 43405.5625 | 71 | 70
2018-11-01 14:00 | 52 | 50 |  |  | 43405.5833 | 73 | 72
2018-11-01 14:30 | 56 | 54 |  |  | 43405.6042 | 77 | 77
2018-11-01 15:00 | 58 | 56 |  |  | 43405.625 | 80 | 79
2018-11-01 15:30 | 59 | 57 |  |  | 43405.6458 | 81 | 80
2018-11-01 16:00 | 63 | 61 |  |  | 43405.6667 | 85 | 84
2018-11-01 16:30 | 65 | 62 |  |  | 43405.6875 | 86 | 85
2018-11-01 17:00 | 69 | 65 |  |  | 43405.7083 | 90 | 87
2018-11-01 17:30 | 69 | 65 |  |  | 43405.7292 | 90 | 85
2018-11-01 18:00 | 68 | 64 |  |  | 43405.75 | 87 | 83
2018-11-01 18:30 | 68 | 65 |  |  | 43405.7708 | 85 | 82
2018-11-01 19:00 | 72 | 69 |  |  | 43405.7917 | 88 | 85
2018-11-01 19:30 | 69 | 65 |  |  | 43405.8125 | 85 | 82
2018-11-01 20:00 | 66 | 63 |  |  | 43405.8333 | 83 | 79
2018-11-01 20:30 | 67 | 64 |  |  | 43405.8542 | 82 | 78
2018-11-01 21:00 | 64 | 62 |  |  | 43405.875 | 77 | 76
2018-11-01 21:30 | 62 | 60 |  |  | 43405.8958 | 74 | 73
2018-11-01 22:00 | 58 | 57 |  |  | 43405.9167 | 73 | 73
2018-11-01 22:30 | 58 | 57 |  |  | 43405.9375 | 72 | 72
2018-11-01 23:00 | 60 | 58 |  |  | 43405.9583 | 71 | 70
2018-11-01 23:30 | 56 | 54 |  |  | 43405.9792 | 68 | 67
2018-11-02 | 51 | 48 |  |  | 43406 | 62 | 61
2018-11-02 00:30 | 45 | 43 |  |  | 43406.0208 | 54 | 53
2018-11-02 01:00 | 42 | 39 |  |  | 43406.0417 | 50 | 49
2018-11-02 01:30 | 41 | 37 |  |  | 43406.0625 | 48 | 46
2018-11-02 02:00 | 41 | 38 |  |  | 43406.0833 | 48 | 47
2018-11-02 02:30 | 42 | 39 |  |  | 43406.1042 | 49 | 49
2018-11-02 03:00 | 40 | 38 |  |  | 43406.125 | 48 | 48
2018-11-02 03:30 | 39 | 37 |  |  | 43406.1458 | 48 | 48
2018-11-02 04:00 | 40 | 37 |  |  | 43406.1667 | 49 | 48
2018-11-02 04:30 | 39 | 37 |  |  | 43406.1875 | 48 | 48
2018-11-02 05:00 | 42 | 40 |  |  | 43406.2083 | 52 | 52
2018-11-02 05:30 | 45 | 43 |  |  | 43406.2292 | 56 | 56
2018-11-02 06:00 | 44 | 43 |  |  | 43406.25 | 57 | 57
2018-11-02 06:30 | 48 | 48 |  |  | 43406.2708 | 64 | 64
2018-11-02 07:00 | 50 | 49 |  |  | 43406.2917 | 68 | 68
2018-11-02 07:30 | 51 | 49 |  |  | 43406.3125 | 71 | 71
2018-11-02 08:00 | 53 | 52 |  |  | 43406.3333 | 76 | 75
2018-11-02 08:30 | 52 | 52 |  |  | 43406.3542 | 78 | 78
2018-11-02 09:00 | 56 | 55 |  |  | 43406.375 | 80 | 79
2018-11-02 09:30 | 54 | 53 |  |  | 43406.3958 | 77 | 77
2018-11-02 10:00 | 50 | 49 |  |  | 43406.4167 | 74 | 74
2018-11-02 10:30 | 48 | 47 |  |  | 43406.4375 | 72 | 72
2018-11-02 11:00 | 46 | 45 |  |  | 43406.4583 | 71 | 71
2018-11-02 11:30 | 47 | 47 |  |  | 43406.4792 | 71 | 71
2018-11-02 12:00 | 46 | 45 |  |  | 43406.5 | 70 | 70
2018-11-02 12:30 | 45 | 44 |  |  | 43406.5208 | 69 | 69
2018-11-02 13:00 | 46 | 45 |  |  | 43406.5417 | 70 | 70
2018-11-02 13:30 | 44 | 43 |  |  | 43406.5625 | 66 | 66
2018-11-02 14:00 | 46 | 45 |  |  | 43406.5833 | 68 | 67
2018-11-02 14:30 | 50 | 48 |  |  | 43406.6042 | 72 | 72
2018-11-02 15:00 | 48 | 47 |  |  | 43406.625 | 71 | 71
2018-11-02 15:30 | 50 | 48 |  |  | 43406.6458 | 71 | 71
2018-11-02 16:00 | 54 | 53 |  |  | 43406.6667 | 75 | 75
2018-11-02 16:30 | 59 | 58 |  |  | 43406.6875 | 81 | 81
2018-11-02 17:00 | 61 | 59 |  |  | 43406.7083 | 82 | 81
2018-11-02 17:30 | 63 | 61 |  |  | 43406.7292 | 81 | 80
2018-11-02 18:00 | 63 | 61 |  |  | 43406.75 | 81 | 80
2018-11-02 18:30 | 65 | 63 |  |  | 43406.7708 | 82 | 82
2018-11-02 19:00 | 67 | 65 |  |  | 43406.7917 | 84 | 83
2018-11-02 19:30 | 65 | 64 |  |  | 43406.8125 | 82 | 81
2018-11-02 20:00 | 65 | 64 |  |  | 43406.8333 | 82 | 81
2018-11-02 20:30 | 65 | 64 |  |  | 43406.8542 | 80 | 79
2018-11-02 21:00 | 62 | 62 |  |  | 43406.875 | 77 | 77
2018-11-02 21:30 | 61 | 60 |  |  | 43406.8958 | 75 | 75
2018-11-02 22:00 | 62 | 61 |  |  | 43406.9167 | 78 | 78
2018-11-02 22:30 | 62 | 60 |  |  | 43406.9375 | 79 | 79
2018-11-02 23:00 | 62 | 61 |  |  | 43406.9583 | 76 | 76
2018-11-02 23:30 | 58 | 56 |  |  | 43406.9792 | 72 | 72
2018-11-03 | 53 | 51 |  |  | 43407 | 67 | 67
2018-11-03 00:30 | 53 | 50 |  |  | 43407.0208 | 64 | 64
2018-11-03 01:00 | 52 | 48 |  |  | 43407.0417 | 60 | 59
2018-11-03 01:30 | 51 | 48 |  |  | 43407.0625 | 57 | 56
2018-11-03 02:00 | 50 | 46 |  |  | 43407.0833 | 56 | 55
2018-11-03 02:30 | 49 | 44 |  |  | 43407.1042 | 55 | 54
2018-11-03 03:00 | 49 | 44 |  |  | 43407.125 | 55 | 54
2018-11-03 03:30 | 47 | 42 |  |  | 43407.1458 | 53 | 52
2018-11-03 04:00 | 48 | 43 |  |  | 43407.1667 | 54 | 53
2018-11-03 04:30 | 47 | 42 |  |  | 43407.1875 | 53 | 52
2018-11-03 05:00 | 48 | 43 |  |  | 43407.2083 | 54 | 53
2018-11-03 05:30 | 49 | 44 |  |  | 43407.2292 | 54 | 53
2018-11-03 06:00 | 49 | 44 |  |  | 43407.25 | 55 | 54
2018-11-03 06:30 | 47 | 43 |  |  | 43407.2708 | 54 | 54
2018-11-03 07:00 | 45 | 41 |  |  | 43407.2917 | 53 | 53
2018-11-03 07:30 | 44 | 40 |  |  | 43407.3125 | 53 | 53
2018-11-03 08:00 | 44 | 41 |  |  | 43407.3333 | 53 | 53
2018-11-03 08:30 | 43 | 41 |  |  | 43407.3542 | 55 | 55
2018-11-03 09:00 | 43 | 41 |  |  | 43407.375 | 55 | 55
2018-11-03 09:30 | 44 | 42 |  |  | 43407.3958 | 56 | 55
2018-11-03 10:00 | 47 | 46 |  |  | 43407.4167 | 58 | 58
2018-11-03 10:30 | 47 | 46 |  |  | 43407.4375 | 58 | 58
2018-11-03 11:00 | 49 | 48 |  |  | 43407.4583 | 59 | 59
2018-11-03 11:30 | 49 | 48 |  |  | 43407.4792 | 60 | 60
2018-11-03 12:00 | 51 | 50 |  |  | 43407.5 | 60 | 60
2018-11-03 12:30 | 52 | 51 |  |  | 43407.5208 | 63 | 63
2018-11-03 13:00 | 51 | 50 |  |  | 43407.5417 | 59 | 59
2018-11-03 13:30 | 54 | 53 |  |  | 43407.5625 | 62 | 62
2018-11-03 14:00 | 56 | 55 |  |  | 43407.5833 | 63 | 63
2018-11-03 14:30 | 60 | 60 |  |  | 43407.6042 | 68 | 67
2018-11-03 15:00 | 62 | 61 |  |  | 43407.625 | 69 | 69
2018-11-03 15:30 | 64 | 64 |  |  | 43407.6458 | 70 | 70
2018-11-03 16:00 | 66 | 66 |  |  | 43407.6667 | 70 | 70
2018-11-03 16:30 | 67 | 67 |  |  | 43407.6875 | 70 | 70
2018-11-03 17:00 | 69 | 69 |  |  | 43407.7083 | 73 | 73
2018-11-03 17:30 | 70 | 70 |  |  | 43407.7292 | 75 | 75
2018-11-03 18:00 | 70 | 70 |  |  | 43407.75 | 75 | 75
2018-11-03 18:30 | 70 | 70 |  |  | 43407.7708 | 77 | 77
2018-11-03 19:00 | 74 | 74 |  |  | 43407.7917 | 81 | 81
2018-11-03 19:30 | 73 | 73 |  |  | 43407.8125 | 80 | 80
2018-11-03 20:00 | 72 | 72 |  |  | 43407.8333 | 78 | 78
2018-11-03 20:30 | 70 | 70 |  |  | 43407.8542 | 77 | 77
2018-11-03 21:00 | 67 | 67 |  |  | 43407.875 | 75 | 75
2018-11-03 21:30 | 64 | 64 |  |  | 43407.8958 | 73 | 73
2018-11-03 22:00 | 63 | 63 |  |  | 43407.9167 | 72 | 72
2018-11-03 22:30 | 62 | 62 |  |  | 43407.9375 | 72 | 72
2018-11-03 23:00 | 62 | 62 |  |  | 43407.9583 | 69 | 69
2018-11-03 23:30 | 60 | 60 |  |  | 43407.9792 | 67 | 67
2018-11-04 | 56 | 56 |  |  | 43408 | 64 | 64
2018-11-04 00:30 | 52 | 52 |  |  | 43408.0208 | 60 | 60
2018-11-04 01:00 | 49 | 49 |  |  | 43408.0417 | 57 | 57
2018-11-04 01:30 | 47 | 47 |  |  | 43408.0625 | 54 | 54
2018-11-04 02:00 | 44 | 44 |  |  | 43408.0833 | 52 | 52
2018-11-04 02:30 | 42 | 42 |  |  | 43408.1042 | 50 | 49
2018-11-04 03:00 | 43 | 43 |  |  | 43408.125 | 51 | 51
2018-11-04 03:30 | 42 | 42 |  |  | 43408.1458 | 51 | 51
2018-11-04 04:00 | 40 | 40 |  |  | 43408.1667 | 48 | 48
2018-11-04 04:30 | 42 | 42 |  |  | 43408.1875 | 50 | 50
2018-11-04 05:00 | 40 | 40 |  |  | 43408.2083 | 49 | 49
2018-11-04 05:30 | 40 | 40 |  |  | 43408.2292 | 50 | 49
2018-11-04 06:00 | 40 | 40 |  |  | 43408.25 | 52 | 49
2018-11-04 06:30 | 37 | 37 |  |  | 43408.2708 | 50 | 47
2018-11-04 07:00 | 37 | 37 |  |  | 43408.2917 | 49 | 47
2018-11-04 07:30 | 34 | 34 |  |  | 43408.3125 | 48 | 46
2018-11-04 08:00 | 33 | 33 |  |  | 43408.3333 | 47 | 46
2018-11-04 08:30 | 36 | 35 |  |  | 43408.3542 | 49 | 48
2018-11-04 09:00 | 37 | 37 |  |  | 43408.375 | 52 | 51
2018-11-04 09:30 | 41 | 40 |  |  | 43408.3958 | 55 | 54
2018-11-04 10:00 | 44 | 43 |  |  | 43408.4167 | 57 | 57
2018-11-04 10:30 | 45 | 44 |  |  | 43408.4375 | 57 | 56
2018-11-04 11:00 | 45 | 45 |  |  | 43408.4583 | 56 | 55
2018-11-04 11:30 | 50 | 50 |  |  | 43408.4792 | 59 | 59
2018-11-04 12:00 | 51 | 51 |  |  | 43408.5 | 60 | 60
2018-11-04 12:30 | 56 | 56 |  |  | 43408.5208 | 63 | 62
2018-11-04 13:00 | 58 | 58 |  |  | 43408.5417 | 64 | 63
2018-11-04 13:30 | 59 | 59 |  |  | 43408.5625 | 64 | 63
2018-11-04 14:00 | 58 | 58 |  |  | 43408.5833 | 64 | 63
2018-11-04 14:30 | 62 | 62 |  |  | 43408.6042 | 67 | 66
2018-11-04 15:00 | 64 | 64 |  |  | 43408.625 | 68 | 68
2018-11-04 15:30 | 66 | 66 |  |  | 43408.6458 | 71 | 71
2018-11-04 16:00 | 69 | 69 |  |  | 43408.6667 | 72 | 72
2018-11-04 16:30 | 71 | 71 |  |  | 43408.6875 | 76 | 76
2018-11-04 17:00 | 74 | 73 |  |  | 43408.7083 | 80 | 79
2018-11-04 17:30 | 74 | 74 |  |  | 43408.7292 | 81 | 81
2018-11-04 18:00 | 75 | 75 |  |  | 43408.75 | 82 | 82
2018-11-04 18:30 | 77 | 77 |  |  | 43408.7708 | 86 | 86
2018-11-04 19:00 | 81 | 81 |  |  | 43408.7917 | 91 | 91
2018-11-04 19:30 | 80 | 80 |  |  | 43408.8125 | 90 | 90
2018-11-04 20:00 | 80 | 80 |  |  | 43408.8333 | 90 | 90
2018-11-04 20:30 | 80 | 80 |  |  | 43408.8542 | 91 | 90
2018-11-04 21:00 | 75 | 74 |  |  | 43408.875 | 85 | 85
2018-11-04 21:30 | 70 | 70 |  |  | 43408.8958 | 82 | 82
2018-11-04 22:00 | 69 | 69 |  |  | 43408.9167 | 81 | 81
2018-11-04 22:30 | 67 | 67 |  |  | 43408.9375 | 79 | 79
2018-11-04 23:00 | 64 | 64 |  |  | 43408.9583 | 74 | 74
2018-11-04 23:30 | 61 | 61 |  |  | 43408.9792 | 73 | 73
2018-11-05 | 57 | 57 |  |  | 43409 | 67 | 67
2018-11-05 00:30 | 53 | 53 |  |  | 43409.0208 | 65 | 65
2018-11-05 01:00 | 50 | 49 |  |  | 43409.0417 | 61 | 61
2018-11-05 01:30 | 46 | 45 |  |  | 43409.0625 | 57 | 56
2018-11-05 02:00 | 44 | 43 |  |  | 43409.0833 | 55 | 55
2018-11-05 02:30 | 42 | 41 |  |  | 43409.1042 | 54 | 54
2018-11-05 03:00 | 39 | 39 |  |  | 43409.125 | 53 | 52
2018-11-05 03:30 | 39 | 39 |  |  | 43409.1458 | 51 | 51
2018-11-05 04:00 | 39 | 39 |  |  | 43409.1667 | 52 | 52
2018-11-05 04:30 | 45 | 45 |  |  | 43409.1875 | 54 | 54
2018-11-05 05:00 | 50 | 49 |  |  | 43409.2083 | 59 | 58
2018-11-05 05:30 | 53 | 53 |  |  | 43409.2292 | 63 | 62
2018-11-05 06:00 | 55 | 55 |  |  | 43409.25 | 65 | 65
2018-11-05 06:30 | 61 | 61 |  |  | 43409.2708 | 74 | 74
2018-11-05 07:00 | 63 | 63 |  |  | 43409.2917 | 78 | 78
2018-11-05 07:30 | 68 | 68 |  |  | 43409.3125 | 86 | 86
2018-11-05 08:00 | 74 | 73 |  |  | 43409.3333 | 94 | 92
2018-11-05 08:30 | 75 | 75 |  |  | 43409.3542 | 96 | 96
2018-11-05 09:00 | 74 | 74 |  |  | 43409.375 | 96 | 96
2018-11-05 09:30 | 75 | 74 |  |  | 43409.3958 | 97 | 97
2018-11-05 10:00 | 76 | 75 |  |  | 43409.4167 | 97 | 97
2018-11-05 10:30 | 78 | 77 |  |  | 43409.4375 | 100 | 100
2018-11-05 11:00 | 80 | 79 |  |  | 43409.4583 | 101 | 101
2018-11-05 11:30 | 82 | 82 |  |  | 43409.4792 | 103 | 103
2018-11-05 12:00 | 84 | 84 |  |  | 43409.5 | 105 | 105
2018-11-05 12:30 | 86 | 86 |  |  | 43409.5208 | 107 | 107
2018-11-05 13:00 | 87 | 87 |  |  | 43409.5417 | 107 | 107
2018-11-05 13:30 | 90 | 90 |  |  | 43409.5625 | 109 | 109
2018-11-05 14:00 | 90 | 90 |  |  | 43409.5833 | 107 | 107
2018-11-05 14:30 | 92 | 92 |  |  | 43409.6042 | 110 | 109
2018-11-05 15:00 | 94 | 93 |  |  | 43409.625 | 112 | 111
2018-11-05 15:30 | 95 | 95 |  |  | 43409.6458 | 113 | 111
2018-11-05 16:00 | 98 | 98 |  |  | 43409.6667 | 115 | 113
2018-11-05 16:30 | 100 | 99 |  |  | 43409.6875 | 115 | 113
2018-11-05 17:00 | 93 | 93 |  |  | 43409.7083 | 112 | 110
2018-11-05 17:30 | 91 | 91 |  |  | 43409.7292 | 107 | 105
2018-11-05 18:00 | 89 | 89 |  |  | 43409.75 | 103 | 102
2018-11-05 18:30 | 90 | 90 |  |  | 43409.7708 | 102 | 101
2018-11-05 19:00 | 89 | 89 |  |  | 43409.7917 | 103 | 102
2018-11-05 19:30 | 87 | 87 |  |  | 43409.8125 | 102 | 101
2018-11-05 20:00 | 86 | 86 |  |  | 43409.8333 | 101 | 99
2018-11-05 20:30 | 82 | 82 |  |  | 43409.8542 | 97 | 96
2018-11-05 21:00 | 81 | 81 |  |  | 43409.875 | 95 | 95
2018-11-05 21:30 | 77 | 77 |  |  | 43409.8958 | 90 | 89
2018-11-05 22:00 | 73 | 73 |  |  | 43409.9167 | 87 | 87
2018-11-05 22:30 | 72 | 71 |  |  | 43409.9375 | 85 | 85
2018-11-05 23:00 | 67 | 67 |  |  | 43409.9583 | 79 | 79
2018-11-05 23:30 | 65 | 64 |  |  | 43409.9792 | 77 | 77
2018-11-06 | 63 | 63 |  |  | 43410 | 74 | 74
2018-11-06 00:30 | 61 | 61 |  |  | 43410.0208 | 71 | 71
2018-11-06 01:00 | 55 | 55 |  |  | 43410.0417 | 66 | 66
2018-11-06 01:30 | 54 | 54 |  |  | 43410.0625 | 64 | 64
2018-11-06 02:00 | 52 | 52 |  |  | 43410.0833 | 64 | 64
2018-11-06 02:30 | 51 | 51 |  |  | 43410.1042 | 62 | 62
2018-11-06 03:00 | 50 | 50 |  |  | 43410.125 | 62 | 62
2018-11-06 03:30 | 50 | 50 |  |  | 43410.1458 | 62 | 62
2018-11-06 04:00 | 49 | 49 |  |  | 43410.1667 | 61 | 61
2018-11-06 04:30 | 49 | 49 |  |  | 43410.1875 | 62 | 62
2018-11-06 05:00 | 53 | 53 |  |  | 43410.2083 | 65 | 65
2018-11-06 05:30 | 49 | 49 |  |  | 43410.2292 | 63 | 63
2018-11-06 06:00 | 51 | 51 |  |  | 43410.25 | 68 | 68
2018-11-06 06:30 | 58 | 57 |  |  | 43410.2708 | 77 | 77
2018-11-06 07:00 | 63 | 62 |  |  | 43410.2917 | 84 | 83
2018-11-06 07:30 | 67 | 67 |  |  | 43410.3125 | 93 | 93
2018-11-06 08:00 | 67 | 67 |  |  | 43410.3333 | 96 | 96
2018-11-06 08:30 | 66 | 65 |  |  | 43410.3542 | 96 | 96
2018-11-06 09:00 | 64 | 63 |  |  | 43410.375 | 94 | 94
2018-11-06 09:30 | 67 | 66 |  |  | 43410.3958 | 97 | 97
2018-11-06 10:00 | 69 | 68 |  |  | 43410.4167 | 100 | 99
2018-11-06 10:30 | 72 | 72 |  |  | 43410.4375 | 103 | 103
2018-11-06 11:00 | 75 | 74 |  |  | 43410.4583 | 105 | 105
2018-11-06 11:30 | 79 | 76 |  |  | 43410.4792 | 105 | 104
2018-11-06 12:00 | 83 | 80 |  |  | 43410.5 | 109 | 109
2018-11-06 12:30 | 85 | 82 |  |  | 43410.5208 | 112 | 112
2018-11-06 13:00 | 85 | 83 |  |  | 43410.5417 | 112 | 112
2018-11-06 13:30 | 85 | 82 |  |  | 43410.5625 | 111 | 111
2018-11-06 14:00 | 88 | 87 |  |  | 43410.5833 | 117 | 117
2018-11-06 14:30 | 85 | 85 |  |  | 43410.6042 | 118 | 117
2018-11-06 15:00 | 87 | 87 |  |  | 43410.625 | 118 | 117
2018-11-06 15:30 | 98 | 98 |  |  | 43410.6458 | 126 | 125
2018-11-06 16:00 | 102 | 101 |  |  | 43410.6667 | 127 | 126
2018-11-06 16:30 | 101 | 101 |  |  | 43410.6875 | 126 | 125
2018-11-06 17:00 | 98 | 98 |  |  | 43410.7083 | 121 | 120
2018-11-06 17:30 | 98 | 98 |  |  | 43410.7292 | 120 | 119
2018-11-06 18:00 | 95 | 95 |  |  | 43410.75 | 117 | 116
2018-11-06 18:30 | 95 | 95 |  |  | 43410.7708 | 116 | 114
2018-11-06 19:00 | 97 | 97 |  |  | 43410.7917 | 116 | 115
2018-11-06 19:30 | 95 | 94 |  |  | 43410.8125 | 112 | 110
2018-11-06 20:00 | 91 | 90 |  |  | 43410.8333 | 109 | 106
2018-11-06 20:30 | 92 | 91 |  |  | 43410.8542 | 111 | 108
2018-11-06 21:00 | 91 | 91 |  |  | 43410.875 | 109 | 108
2018-11-06 21:30 | 83 | 83 |  |  | 43410.8958 | 99 | 98
2018-11-06 22:00 | 81 | 81 |  |  | 43410.9167 | 98 | 97
2018-11-06 22:30 | 74 | 73 |  |  | 43410.9375 | 88 | 88
2018-11-06 23:00 | 69 | 69 |  |  | 43410.9583 | 85 | 83
2018-11-06 23:30 | 65 | 65 |  |  | 43410.9792 | 80 | 79
2018-11-07 | 63 | 63 |  |  | 43411 | 81 | 79
2018-11-07 00:30 | 62 | 62 |  |  | 43411.0208 | 80 | 78
2018-11-07 01:00 | 63 | 62 |  |  | 43411.0417 | 78 | 77
2018-11-07 01:30 | 63 | 59 |  |  | 43411.0625 | 72 | 72
2018-11-07 02:00 | 60 | 56 |  |  | 43411.0833 | 68 | 68
2018-11-07 02:30 | 59 | 55 |  |  | 43411.1042 | 67 | 67
2018-11-07 03:00 | 57 | 53 |  |  | 43411.125 | 65 | 65
2018-11-07 03:30 | 56 | 52 |  |  | 43411.1458 | 64 | 64
2018-11-07 04:00 | 58 | 54 |  |  | 43411.1667 | 64 | 64
2018-11-07 04:30 | 58 | 55 |  |  | 43411.1875 | 66 | 66
2018-11-07 05:00 | 60 | 56 |  |  | 43411.2083 | 67 | 67
2018-11-07 05:30 | 62 | 58 |  |  | 43411.2292 | 70 | 70
2018-11-07 06:00 | 64 | 62 |  |  | 43411.25 | 74 | 74
2018-11-07 06:30 | 69 | 68 |  |  | 43411.2708 | 83 | 82
2018-11-07 07:00 | 71 | 71 |  |  | 43411.2917 | 90 | 89
2018-11-07 07:30 | 78 | 77 |  |  | 43411.3125 | 99 | 96
2018-11-07 08:00 | 87 | 81 |  |  | 43411.3333 | 108 | 102
2018-11-07 08:30 | 84 | 78 |  |  | 43411.3542 | 103 | 97
2018-11-07 09:00 | 82 | 76 |  |  | 43411.375 | 100 | 95
2018-11-07 09:30 | 84 | 78 |  |  | 43411.3958 | 102 | 97
2018-11-07 10:00 | 84 | 78 |  |  | 43411.4167 | 102 | 96
2018-11-07 10:30 | 83 | 79 |  |  | 43411.4375 | 104 | 98
2018-11-07 11:00 | 83 | 80 |  |  | 43411.4583 | 105 | 98
2018-11-07 11:30 | 86 | 83 |  |  | 43411.4792 | 106 | 99
2018-11-07 12:00 | 87 | 85 |  |  | 43411.5 | 108 | 101
2018-11-07 12:30 | 89 | 87 |  |  | 43411.5208 | 109 | 103
2018-11-07 13:00 | 90 | 87 |  |  | 43411.5417 | 106 | 102
2018-11-07 13:30 | 95 | 89 |  |  | 43411.5625 | 108 | 106
2018-11-07 14:00 | 102 | 97 |  |  | 43411.5833 | 113 | 111
2018-11-07 14:30 | 98 | 94 |  |  | 43411.6042 | 114 | 112
2018-11-07 15:00 | 97 | 95 |  |  | 43411.625 | 112 | 111
2018-11-07 15:30 | 99 | 96 |  |  | 43411.6458 | 110 | 110
2018-11-07 16:00 | 102 | 100 |  |  | 43411.6667 | 113 | 112
2018-11-07 16:30 | 96 | 95 |  |  | 43411.6875 | 113 | 112
2018-11-07 17:00 | 96 | 95 |  |  | 43411.7083 | 113 | 112
2018-11-07 17:30 | 94 | 92 |  |  | 43411.7292 | 109 | 108
2018-11-07 18:00 | 91 | 90 |  |  | 43411.75 | 105 | 104
2018-11-07 18:30 | 86 | 86 |  |  | 43411.7708 | 100 | 100
2018-11-07 19:00 | 88 | 87 |  |  | 43411.7917 | 101 | 100
2018-11-07 19:30 | 86 | 86 |  |  | 43411.8125 | 99 | 99
2018-11-07 20:00 | 85 | 83 |  |  | 43411.8333 | 99 | 97
2018-11-07 20:30 | 83 | 82 |  |  | 43411.8542 | 98 | 96
2018-11-07 21:00 | 81 | 79 |  |  | 43411.875 | 95 | 93
2018-11-07 21:30 | 78 | 76 |  |  | 43411.8958 | 92 | 88
2018-11-07 22:00 | 75 | 73 |  |  | 43411.9167 | 90 | 87
2018-11-07 22:30 | 75 | 73 |  |  | 43411.9375 | 89 | 86
2018-11-07 23:00 | 76 | 75 |  |  | 43411.9583 | 85 | 83
2018-11-07 23:30 | 73 | 71 |  |  | 43411.9792 | 80 | 79
2018-11-08 | 68 | 66 |  |  | 43412 | 76 | 74
2018-11-08 00:30 | 61 | 59 |  |  | 43412.0208 | 70 | 68
2018-11-08 01:00 | 56 | 55 |  |  | 43412.0417 | 68 | 65
2018-11-08 01:30 | 55 | 55 |  |  | 43412.0625 | 67 | 63
2018-11-08 02:00 | 52 | 52 |  |  | 43412.0833 | 65 | 61
2018-11-08 02:30 | 51 | 51 |  |  | 43412.1042 | 65 | 61
2018-11-08 03:00 | 51 | 50 |  |  | 43412.125 | 65 | 61
2018-11-08 03:30 | 51 | 50 |  |  | 43412.1458 | 64 | 60
2018-11-08 04:00 | 51 | 50 |  |  | 43412.1667 | 64 | 60
2018-11-08 04:30 | 51 | 50 |  |  | 43412.1875 | 63 | 60
2018-11-08 05:00 | 54 | 53 |  |  | 43412.2083 | 67 | 64
2018-11-08 05:30 | 55 | 54 |  |  | 43412.2292 | 68 | 65
2018-11-08 06:00 | 59 | 58 |  |  | 43412.25 | 71 | 69
2018-11-08 06:30 | 67 | 67 |  |  | 43412.2708 | 81 | 81
2018-11-08 07:00 | 71 | 71 |  |  | 43412.2917 | 86 | 86
2018-11-08 07:30 | 77 | 77 |  |  | 43412.3125 | 94 | 94
2018-11-08 08:00 | 82 | 82 |  |  | 43412.3333 | 99 | 99
2018-11-08 08:30 | 84 | 84 |  |  | 43412.3542 | 101 | 101
2018-11-08 09:00 | 82 | 82 |  |  | 43412.375 | 98 | 98
2018-11-08 09:30 | 85 | 85 |  |  | 43412.3958 | 102 | 102
2018-11-08 10:00 | 85 | 85 |  |  | 43412.4167 | 100 | 100
2018-11-08 10:30 | 85 | 85 |  |  | 43412.4375 | 99 | 99
2018-11-08 11:00 | 83 | 83 |  |  | 43412.4583 | 96 | 96
2018-11-08 11:30 | 83 | 83 |  |  | 43412.4792 | 98 | 98
2018-11-08 12:00 | 79 | 79 |  |  | 43412.5 | 94 | 94
2018-11-08 12:30 | 73 | 73 |  |  | 43412.5208 | 88 | 88
2018-11-08 13:00 | 64 | 64 |  |  | 43412.5417 | 80 | 80
2018-11-08 13:30 | 68 | 68 |  |  | 43412.5625 | 81 | 81
2018-11-08 14:00 | 70 | 70 |  |  | 43412.5833 | 83 | 83
2018-11-08 14:30 | 70 | 70 |  |  | 43412.6042 | 86 | 86
2018-11-08 15:00 | 64 | 64 |  |  | 43412.625 | 77 | 77
2018-11-08 15:30 | 65 | 65 |  |  | 43412.6458 | 82 | 82
2018-11-08 16:00 | 68 | 67 |  |  | 43412.6667 | 86 | 86
2018-11-08 16:30 | 70 | 70 |  |  | 43412.6875 | 89 | 89
2018-11-08 17:00 | 74 | 74 |  |  | 43412.7083 | 92 | 92
2018-11-08 17:30 | 74 | 74 |  |  | 43412.7292 | 91 | 91
2018-11-08 18:00 | 74 | 74 |  |  | 43412.75 | 90 | 89
2018-11-08 18:30 | 73 | 73 |  |  | 43412.7708 | 89 | 88
2018-11-08 19:00 | 76 | 76 |  |  | 43412.7917 | 90 | 90
2018-11-08 19:30 | 74 | 74 |  |  | 43412.8125 | 89 | 89
2018-11-08 20:00 | 74 | 73 |  |  | 43412.8333 | 89 | 88
2018-11-08 20:30 | 74 | 73 |  |  | 43412.8542 | 88 | 88
2018-11-08 21:00 | 71 | 71 |  |  | 43412.875 | 84 | 84
2018-11-08 21:30 | 66 | 66 |  |  | 43412.8958 | 79 | 79
2018-11-08 22:00 | 62 | 62 |  |  | 43412.9167 | 76 | 76
2018-11-08 22:30 | 60 | 60 |  |  | 43412.9375 | 74 | 74
2018-11-08 23:00 | 57 | 57 |  |  | 43412.9583 | 70 | 70
2018-11-08 23:30 | 54 | 54 |  |  | 43412.9792 | 67 | 67
2018-11-09 | 51 | 51 |  |  | 43413 | 64 | 64
2018-11-09 00:30 | 49 | 49 |  |  | 43413.0208 | 61 | 61
2018-11-09 01:00 | 45 | 45 |  |  | 43413.0417 | 57 | 56
2018-11-09 01:30 | 42 | 42 |  |  | 43413.0625 | 53 | 53
2018-11-09 02:00 | 41 | 41 |  |  | 43413.0833 | 52 | 52
2018-11-09 02:30 | 39 | 39 |  |  | 43413.1042 | 50 | 50
2018-11-09 03:00 | 38 | 38 |  |  | 43413.125 | 49 | 49
2018-11-09 03:30 | 38 | 38 |  |  | 43413.1458 | 49 | 49
2018-11-09 04:00 | 37 | 37 |  |  | 43413.1667 | 48 | 48
2018-11-09 04:30 | 39 | 39 |  |  | 43413.1875 | 50 | 50
2018-11-09 05:00 | 39 | 39 |  |  | 43413.2083 | 50 | 50
2018-11-09 05:30 | 40 | 40 |  |  | 43413.2292 | 53 | 52
2018-11-09 06:00 | 44 | 44 |  |  | 43413.25 | 58 | 58
2018-11-09 06:30 | 50 | 49 |  |  | 43413.2708 | 67 | 66
2018-11-09 07:00 | 53 | 53 |  |  | 43413.2917 | 74 | 73
2018-11-09 07:30 | 56 | 55 |  |  | 43413.3125 | 78 | 78
2018-11-09 08:00 | 56 | 55 |  |  | 43413.3333 | 80 | 79
2018-11-09 08:30 | 54 | 53 |  |  | 43413.3542 | 79 | 78
2018-11-09 09:00 | 54 | 53 |  |  | 43413.375 | 78 | 77
2018-11-09 09:30 | 54 | 53 |  |  | 43413.3958 | 79 | 78
2018-11-09 10:00 | 53 | 51 |  |  | 43413.4167 | 77 | 76
2018-11-09 10:30 | 56 | 55 |  |  | 43413.4375 | 79 | 77
2018-11-09 11:00 | 57 | 56 |  |  | 43413.4583 | 80 | 78
2018-11-09 11:30 | 58 | 57 |  |  | 43413.4792 | 78 | 76
2018-11-09 12:00 | 60 | 59 |  |  | 43413.5 | 77 | 75
2018-11-09 12:30 | 55 | 54 |  |  | 43413.5208 | 77 | 75
2018-11-09 13:00 | 49 | 48 |  |  | 43413.5417 | 77 | 75
2018-11-09 13:30 | 55 | 54 |  |  | 43413.5625 | 72 | 71
2018-11-09 14:00 | 58 | 57 |  |  | 43413.5833 | 78 | 76
2018-11-09 14:30 | 57 | 56 |  |  | 43413.6042 | 79 | 78
2018-11-09 15:00 | 56 | 55 |  |  | 43413.625 | 78 | 76
2018-11-09 15:30 | 57 | 56 |  |  | 43413.6458 | 77 | 76
2018-11-09 16:00 | 60 | 59 |  |  | 43413.6667 | 81 | 80
2018-11-09 16:30 | 60 | 59 |  |  | 43413.6875 | 82 | 81
2018-11-09 17:00 | 63 | 63 |  |  | 43413.7083 | 83 | 83
2018-11-09 17:30 | 64 | 63 |  |  | 43413.7292 | 81 | 81
2018-11-09 18:00 | 63 | 63 |  |  | 43413.75 | 81 | 81
2018-11-09 18:30 | 63 | 63 |  |  | 43413.7708 | 81 | 81
2018-11-09 19:00 | 67 | 66 |  |  | 43413.7917 | 86 | 85
2018-11-09 19:30 | 67 | 65 |  |  | 43413.8125 | 87 | 84
2018-11-09 20:00 | 66 | 64 |  |  | 43413.8333 | 85 | 82
2018-11-09 20:30 | 65 | 64 |  |  | 43413.8542 | 83 | 81
2018-11-09 21:00 | 63 | 63 |  |  | 43413.875 | 77 | 77
2018-11-09 21:30 | 60 | 60 |  |  | 43413.8958 | 73 | 73
2018-11-09 22:00 | 58 | 58 |  |  | 43413.9167 | 72 | 72
2018-11-09 22:30 | 57 | 57 |  |  | 43413.9375 | 72 | 72
2018-11-09 23:00 | 55 | 55 |  |  | 43413.9583 | 69 | 69
2018-11-09 23:30 | 51 | 51 |  |  | 43413.9792 | 65 | 65
2018-11-10 | 49 | 49 |  |  | 43414 | 62 | 62
2018-11-10 00:30 | 47 | 47 |  |  | 43414.0208 | 59 | 59
2018-11-10 01:00 | 45 | 45 |  |  | 43414.0417 | 57 | 57
2018-11-10 01:30 | 45 | 45 |  |  | 43414.0625 | 55 | 55
2018-11-10 02:00 | 41 | 41 |  |  | 43414.0833 | 53 | 53
2018-11-10 02:30 | 41 | 41 |  |  | 43414.1042 | 53 | 53
2018-11-10 03:00 | 41 | 41 |  |  | 43414.125 | 52 | 52
2018-11-10 03:30 | 40 | 39 |  |  | 43414.1458 | 51 | 51
2018-11-10 04:00 | 39 | 39 |  |  | 43414.1667 | 49 | 49
2018-11-10 04:30 | 39 | 38 |  |  | 43414.1875 | 50 | 50
2018-11-10 05:00 | 39 | 39 |  |  | 43414.2083 | 50 | 50
2018-11-10 05:30 | 38 | 38 |  |  | 43414.2292 | 50 | 50
2018-11-10 06:00 | 39 | 38 |  |  | 43414.25 | 52 | 52
2018-11-10 06:30 | 37 | 37 |  |  | 43414.2708 | 51 | 51
2018-11-10 07:00 | 36 | 36 |  |  | 43414.2917 | 51 | 51
2018-11-10 07:30 | 36 | 36 |  |  | 43414.3125 | 52 | 52
2018-11-10 08:00 | 37 | 37 |  |  | 43414.3333 | 52 | 52
2018-11-10 08:30 | 37 | 37 |  |  | 43414.3542 | 54 | 54
2018-11-10 09:00 | 40 | 40 |  |  | 43414.375 | 58 | 58
2018-11-10 09:30 | 44 | 44 |  |  | 43414.3958 | 61 | 61
2018-11-10 10:00 | 47 | 47 |  |  | 43414.4167 | 62 | 62
2018-11-10 10:30 | 49 | 49 |  |  | 43414.4375 | 60 | 60
2018-11-10 11:00 | 47 | 47 |  |  | 43414.4583 | 62 | 62
2018-11-10 11:30 | 46 | 46 |  |  | 43414.4792 | 58 | 58
2018-11-10 12:00 | 46 | 46 |  |  | 43414.5 | 60 | 60
2018-11-10 12:30 | 45 | 45 |  |  | 43414.5208 | 56 | 56
2018-11-10 13:00 | 46 | 46 |  |  | 43414.5417 | 58 | 58
2018-11-10 13:30 | 46 | 46 |  |  | 43414.5625 | 58 | 58
2018-11-10 14:00 | 47 | 46 |  |  | 43414.5833 | 61 | 61
2018-11-10 14:30 | 47 | 46 |  |  | 43414.6042 | 61 | 61
2018-11-10 15:00 | 49 | 49 |  |  | 43414.625 | 64 | 64
2018-11-10 15:30 | 50 | 50 |  |  | 43414.6458 | 64 | 64
2018-11-10 16:00 | 52 | 52 |  |  | 43414.6667 | 67 | 67
2018-11-10 16:30 | 53 | 53 |  |  | 43414.6875 | 70 | 70
2018-11-10 17:00 | 55 | 55 |  |  | 43414.7083 | 70 | 70
2018-11-10 17:30 | 56 | 56 |  |  | 43414.7292 | 71 | 71
2018-11-10 18:00 | 55 | 55 |  |  | 43414.75 | 70 | 70
2018-11-10 18:30 | 56 | 56 |  |  | 43414.7708 | 71 | 71
2018-11-10 19:00 | 59 | 59 |  |  | 43414.7917 | 76 | 76
2018-11-10 19:30 | 59 | 59 |  |  | 43414.8125 | 76 | 76
2018-11-10 20:00 | 58 | 58 |  |  | 43414.8333 | 74 | 74
2018-11-10 20:30 | 58 | 58 |  |  | 43414.8542 | 73 | 73
2018-11-10 21:00 | 57 | 57 |  |  | 43414.875 | 72 | 72
2018-11-10 21:30 | 57 | 57 |  |  | 43414.8958 | 72 | 72
2018-11-10 22:00 | 57 | 56 |  |  | 43414.9167 | 72 | 71
2018-11-10 22:30 | 56 | 56 |  |  | 43414.9375 | 71 | 71
2018-11-10 23:00 | 54 | 54 |  |  | 43414.9583 | 67 | 67
2018-11-10 23:30 | 51 | 51 |  |  | 43414.9792 | 65 | 65
2018-11-11 | 50 | 49 |  |  | 43415 | 63 | 62
2018-11-11 00:30 | 46 | 46 |  |  | 43415.0208 | 58 | 57
2018-11-11 01:00 | 44 | 43 |  |  | 43415.0417 | 55 | 54
2018-11-11 01:30 | 43 | 42 |  |  | 43415.0625 | 53 | 51
2018-11-11 02:00 | 42 | 41 |  |  | 43415.0833 | 52 | 51
2018-11-11 02:30 | 42 | 41 |  |  | 43415.1042 | 51 | 49
2018-11-11 03:00 | 42 | 41 |  |  | 43415.125 | 51 | 49
2018-11-11 03:30 | 41 | 40 |  |  | 43415.1458 | 51 | 49
2018-11-11 04:00 | 39 | 39 |  |  | 43415.1667 | 51 | 49
2018-11-11 04:30 | 40 | 39 |  |  | 43415.1875 | 50 | 49
2018-11-11 05:00 | 39 | 39 |  |  | 43415.2083 | 54 | 50
2018-11-11 05:30 | 41 | 41 |  |  | 43415.2292 | 54 | 51
2018-11-11 06:00 | 40 | 40 |  |  | 43415.25 | 54 | 51
2018-11-11 06:30 | 38 | 37 |  |  | 43415.2708 | 53 | 49
2018-11-11 07:00 | 35 | 35 |  |  | 43415.2917 | 51 | 48
2018-11-11 07:30 | 35 | 33 |  |  | 43415.3125 | 50 | 48
2018-11-11 08:00 | 35 | 34 |  |  | 43415.3333 | 50 | 48
2018-11-11 08:30 | 37 | 35 |  |  | 43415.3542 | 53 | 51
2018-11-11 09:00 | 38 | 36 |  |  | 43415.375 | 53 | 52
2018-11-11 09:30 | 39 | 36 |  |  | 43415.3958 | 53 | 52
2018-11-11 10:00 | 41 | 39 |  |  | 43415.4167 | 53 | 52
2018-11-11 10:30 | 42 | 40 |  |  | 43415.4375 | 55 | 54
2018-11-11 11:00 | 44 | 42 |  |  | 43415.4583 | 58 | 57
2018-11-11 11:30 | 45 | 43 |  |  | 43415.4792 | 56 | 56
2018-11-11 12:00 | 43 | 41 |  |  | 43415.5 | 53 | 52
2018-11-11 12:30 | 39 | 36 |  |  | 43415.5208 | 49 | 49
2018-11-11 13:00 | 38 | 35 |  |  | 43415.5417 | 48 | 48
2018-11-11 13:30 | 37 | 34 |  |  | 43415.5625 | 49 | 49
2018-11-11 14:00 | 42 | 40 |  |  | 43415.5833 | 50 | 50
2018-11-11 14:30 | 44 | 42 |  |  | 43415.6042 | 55 | 55
2018-11-11 15:00 | 49 | 46 |  |  | 43415.625 | 60 | 59
2018-11-11 15:30 | 52 | 49 |  |  | 43415.6458 | 63 | 62
2018-11-11 16:00 | 54 | 52 |  |  | 43415.6667 | 66 | 65
2018-11-11 16:30 | 54 | 53 |  |  | 43415.6875 | 67 | 66
2018-11-11 17:00 | 57 | 55 |  |  | 43415.7083 | 70 | 70
2018-11-11 17:30 | 58 | 56 |  |  | 43415.7292 | 71 | 70
2018-11-11 18:00 | 59 | 58 |  |  | 43415.75 | 72 | 72
2018-11-11 18:30 | 61 | 59 |  |  | 43415.7708 | 75 | 75
2018-11-11 19:00 | 65 | 64 |  |  | 43415.7917 | 80 | 79
2018-11-11 19:30 | 64 | 63 |  |  | 43415.8125 | 80 | 79
2018-11-11 20:00 | 63 | 62 |  |  | 43415.8333 | 79 | 78
2018-11-11 20:30 | 64 | 64 |  |  | 43415.8542 | 80 | 78
2018-11-11 21:00 | 62 | 61 |  |  | 43415.875 | 77 | 75
2018-11-11 21:30 | 59 | 59 |  |  | 43415.8958 | 76 | 74
2018-11-11 22:00 | 59 | 58 |  |  | 43415.9167 | 75 | 73
2018-11-11 22:30 | 57 | 56 |  |  | 43415.9375 | 73 | 71
2018-11-11 23:00 | 55 | 54 |  |  | 43415.9583 | 69 | 67
2018-11-11 23:30 | 52 | 51 |  |  | 43415.9792 | 67 | 65
2018-11-12 | 47 | 47 |  |  | 43416 | 63 | 60
2018-11-12 00:30 | 45 | 45 |  |  | 43416.0208 | 60 | 57
2018-11-12 01:00 | 42 | 41 |  |  | 43416.0417 | 57 | 54
2018-11-12 01:30 | 40 | 40 |  |  | 43416.0625 | 56 | 52
2018-11-12 02:00 | 40 | 39 |  |  | 43416.0833 | 55 | 51
2018-11-12 02:30 | 40 | 40 |  |  | 43416.1042 | 55 | 51
2018-11-12 03:00 | 40 | 39 |  |  | 43416.125 | 54 | 50
2018-11-12 03:30 | 39 | 38 |  |  | 43416.1458 | 54 | 49
2018-11-12 04:00 | 39 | 38 |  |  | 43416.1667 | 53 | 48
2018-11-12 04:30 | 41 | 40 |  |  | 43416.1875 | 55 | 51
2018-11-12 05:00 | 43 | 43 |  |  | 43416.2083 | 57 | 53
2018-11-12 05:30 | 47 | 46 |  |  | 43416.2292 | 60 | 57
2018-11-12 06:00 | 48 | 47 |  |  | 43416.25 | 62 | 60
2018-11-12 06:30 | 51 | 50 |  |  | 43416.2708 | 67 | 66
2018-11-12 07:00 | 54 | 52 |  |  | 43416.2917 | 71 | 70
2018-11-12 07:30 | 58 | 56 |  |  | 43416.3125 | 76 | 76
2018-11-12 08:00 | 59 | 56 |  |  | 43416.3333 | 78 | 78
2018-11-12 08:30 | 59 | 56 |  |  | 43416.3542 | 80 | 80
2018-11-12 09:00 | 58 | 57 |  |  | 43416.375 | 81 | 81
2018-11-12 09:30 | 56 | 56 |  |  | 43416.3958 | 79 | 78
2018-11-12 10:00 | 56 | 56 |  |  | 43416.4167 | 78 | 77
2018-11-12 10:30 | 56 | 56 |  |  | 43416.4375 | 80 | 79
2018-11-12 11:00 | 57 | 57 |  |  | 43416.4583 | 82 | 81
2018-11-12 11:30 | 60 | 59 |  |  | 43416.4792 | 83 | 82
2018-11-12 12:00 | 62 | 61 |  |  | 43416.5 | 83 | 82
2018-11-12 12:30 | 58 | 57 |  |  | 43416.5208 | 79 | 79
2018-11-12 13:00 | 57 | 57 |  |  | 43416.5417 | 78 | 77
2018-11-12 13:30 | 57 | 56 |  |  | 43416.5625 | 79 | 78
2018-11-12 14:00 | 58 | 57 |  |  | 43416.5833 | 79 | 78
2018-11-12 14:30 | 59 | 59 |  |  | 43416.6042 | 80 | 80
2018-11-12 15:00 | 57 | 57 |  |  | 43416.625 | 78 | 78
2018-11-12 15:30 | 55 | 55 |  |  | 43416.6458 | 77 | 77
2018-11-12 16:00 | 61 | 61 |  |  | 43416.6667 | 82 | 82
2018-11-12 16:30 | 63 | 63 |  |  | 43416.6875 | 84 | 84
2018-11-12 17:00 | 66 | 66 |  |  | 43416.7083 | 87 | 87
2018-11-12 17:30 | 67 | 67 |  |  | 43416.7292 | 87 | 87
2018-11-12 18:00 | 68 | 68 |  |  | 43416.75 | 87 | 87
2018-11-12 18:30 | 70 | 70 |  |  | 43416.7708 | 87 | 86
2018-11-12 19:00 | 74 | 74 |  |  | 43416.7917 | 90 | 89
2018-11-12 19:30 | 72 | 72 |  |  | 43416.8125 | 88 | 88
2018-11-12 20:00 | 71 | 71 |  |  | 43416.8333 | 86 | 85
2018-11-12 20:30 | 70 | 69 |  |  | 43416.8542 | 84 | 83
2018-11-12 21:00 | 66 | 65 |  |  | 43416.875 | 80 | 80
2018-11-12 21:30 | 63 | 63 |  |  | 43416.8958 | 77 | 76
2018-11-12 22:00 | 61 | 61 |  |  | 43416.9167 | 75 | 75
2018-11-12 22:30 | 59 | 58 |  |  | 43416.9375 | 74 | 74
2018-11-12 23:00 | 56 | 55 |  |  | 43416.9583 | 70 | 70
2018-11-12 23:30 | 56 | 55 |  |  | 43416.9792 | 69 | 68
2018-11-13 | 50 | 50 |  |  | 43417 | 64 | 63
2018-11-13 00:30 | 46 | 46 |  |  | 43417.0208 | 59 | 58
2018-11-13 01:00 | 44 | 44 |  |  | 43417.0417 | 56 | 55
2018-11-13 01:30 | 43 | 43 |  |  | 43417.0625 | 54 | 53
2018-11-13 02:00 | 42 | 41 |  |  | 43417.0833 | 53 | 52
2018-11-13 02:30 | 42 | 41 |  |  | 43417.1042 | 51 | 50
2018-11-13 03:00 | 41 | 41 |  |  | 43417.125 | 51 | 50
2018-11-13 03:30 | 40 | 40 |  |  | 43417.1458 | 50 | 49
2018-11-13 04:00 | 39 | 38 |  |  | 43417.1667 | 49 | 48
2018-11-13 04:30 | 38 | 37 |  |  | 43417.1875 | 49 | 48
2018-11-13 05:00 | 40 | 40 |  |  | 43417.2083 | 52 | 52
2018-11-13 05:30 | 43 | 43 |  |  | 43417.2292 | 55 | 54
2018-11-13 06:00 | 45 | 45 |  |  | 43417.25 | 59 | 58
2018-11-13 06:30 | 51 | 51 |  |  | 43417.2708 | 68 | 67
2018-11-13 07:00 | 54 | 54 |  |  | 43417.2917 | 73 | 73
2018-11-13 07:30 | 53 | 52 |  |  | 43417.3125 | 75 | 74
2018-11-13 08:00 | 54 | 53 |  |  | 43417.3333 | 77 | 77
2018-11-13 08:30 | 56 | 55 |  |  | 43417.3542 | 80 | 80
2018-11-13 09:00 | 61 | 60 |  |  | 43417.375 | 84 | 83
2018-11-13 09:30 | 60 | 59 |  |  | 43417.3958 | 83 | 83
2018-11-13 10:00 | 59 | 58 |  |  | 43417.4167 | 79 | 79
2018-11-13 10:30 | 55 | 55 |  |  | 43417.4375 | 77 | 77
2018-11-13 11:00 | 56 | 55 |  |  | 43417.4583 | 80 | 80
2018-11-13 11:30 | 58 | 58 |  |  | 43417.4792 | 82 | 82
2018-11-13 12:00 | 59 | 58 |  |  | 43417.5 | 80 | 79
2018-11-13 12:30 | 57 | 57 |  |  | 43417.5208 | 80 | 80
2018-11-13 13:00 | 58 | 57 |  |  | 43417.5417 | 81 | 81
2018-11-13 13:30 | 60 | 59 |  |  | 43417.5625 | 81 | 81
2018-11-13 14:00 | 60 | 60 |  |  | 43417.5833 | 82 | 82
2018-11-13 14:30 | 62 | 62 |  |  | 43417.6042 | 83 | 83
2018-11-13 15:00 | 64 | 63 |  |  | 43417.625 | 84 | 84
2018-11-13 15:30 | 63 | 63 |  |  | 43417.6458 | 84 | 84
2018-11-13 16:00 | 69 | 69 |  |  | 43417.6667 | 89 | 89
2018-11-13 16:30 | 66 | 66 |  |  | 43417.6875 | 86 | 86
2018-11-13 17:00 | 69 | 69 |  |  | 43417.7083 | 90 | 90
2018-11-13 17:30 | 73 | 73 |  |  | 43417.7292 | 92 | 92
2018-11-13 18:00 | 74 | 74 |  |  | 43417.75 | 91 | 91
2018-11-13 18:30 | 73 | 73 |  |  | 43417.7708 | 89 | 89
2018-11-13 19:00 | 77 | 77 |  |  | 43417.7917 | 92 | 92
2018-11-13 19:30 | 75 | 75 |  |  | 43417.8125 | 90 | 90
2018-11-13 20:00 | 73 | 73 |  |  | 43417.8333 | 88 | 87
2018-11-13 20:30 | 72 | 72 |  |  | 43417.8542 | 87 | 87
2018-11-13 21:00 | 70 | 70 |  |  | 43417.875 | 83 | 83
2018-11-13 21:30 | 66 | 66 |  |  | 43417.8958 | 79 | 79
2018-11-13 22:00 | 64 | 64 |  |  | 43417.9167 | 78 | 78
2018-11-13 22:30 | 61 | 61 |  |  | 43417.9375 | 76 | 76
2018-11-13 23:00 | 61 | 61 |  |  | 43417.9583 | 73 | 73
2018-11-13 23:30 | 55 | 55 |  |  | 43417.9792 | 69 | 69
2018-11-14 | 52 | 52 |  |  | 43418 | 65 | 65
2018-11-14 00:30 | 48 | 48 |  |  | 43418.0208 | 60 | 60
2018-11-14 01:00 | 47 | 47 |  |  | 43418.0417 | 58 | 58
2018-11-14 01:30 | 46 | 46 |  |  | 43418.0625 | 56 | 56
2018-11-14 02:00 | 43 | 43 |  |  | 43418.0833 | 54 | 53
2018-11-14 02:30 | 41 | 40 |  |  | 43418.1042 | 51 | 50
2018-11-14 03:00 | 38 | 38 |  |  | 43418.125 | 49 | 49
2018-11-14 03:30 | 38 | 38 |  |  | 43418.1458 | 49 | 48
2018-11-14 04:00 | 38 | 37 |  |  | 43418.1667 | 48 | 47
2018-11-14 04:30 | 36 | 36 |  |  | 43418.1875 | 48 | 47
2018-11-14 05:00 | 37 | 37 |  |  | 43418.2083 | 49 | 48
2018-11-14 05:30 | 40 | 39 |  |  | 43418.2292 | 53 | 53
2018-11-14 06:00 | 41 | 41 |  |  | 43418.25 | 56 | 56
2018-11-14 06:30 | 46 | 46 |  |  | 43418.2708 | 63 | 63
2018-11-14 07:00 | 49 | 49 |  |  | 43418.2917 | 69 | 69
2018-11-14 07:30 | 53 | 53 |  |  | 43418.3125 | 75 | 74
2018-11-14 08:00 | 53 | 52 |  |  | 43418.3333 | 76 | 75
2018-11-14 08:30 | 54 | 53 |  |  | 43418.3542 | 77 | 77
2018-11-14 09:00 | 59 | 58 |  |  | 43418.375 | 83 | 83
2018-11-14 09:30 | 64 | 63 |  |  | 43418.3958 | 88 | 87
2018-11-14 10:00 | 67 | 66 |  |  | 43418.4167 | 90 | 89
2018-11-14 10:30 | 65 | 64 |  |  | 43418.4375 | 87 | 87
2018-11-14 11:00 | 66 | 65 |  |  | 43418.4583 | 87 | 86
2018-11-14 11:30 | 65 | 63 |  |  | 43418.4792 | 87 | 86
2018-11-14 12:00 | 67 | 66 |  |  | 43418.5 | 90 | 89
2018-11-14 12:30 | 67 | 66 |  |  | 43418.5208 | 89 | 88
2018-11-14 13:00 | 66 | 65 |  |  | 43418.5417 | 89 | 88
2018-11-14 13:30 | 70 | 69 |  |  | 43418.5625 | 91 | 90
2018-11-14 14:00 | 70 | 69 |  |  | 43418.5833 | 88 | 87
2018-11-14 14:30 | 70 | 69 |  |  | 43418.6042 | 93 | 92
2018-11-14 15:00 | 65 | 64 |  |  | 43418.625 | 89 | 89
2018-11-14 15:30 | 71 | 70 |  |  | 43418.6458 | 93 | 93
2018-11-14 16:00 | 70 | 69 |  |  | 43418.6667 | 91 | 91
2018-11-14 16:30 | 73 | 72 |  |  | 43418.6875 | 94 | 94
2018-11-14 17:00 | 75 | 75 |  |  | 43418.7083 | 96 | 96
2018-11-14 17:30 | 74 | 74 |  |  | 43418.7292 | 93 | 93
2018-11-14 18:00 | 76 | 76 |  |  | 43418.75 | 93 | 93
2018-11-14 18:30 | 74 | 74 |  |  | 43418.7708 | 91 | 91
2018-11-14 19:00 | 79 | 79 |  |  | 43418.7917 | 94 | 94
2018-11-14 19:30 | 78 | 78 |  |  | 43418.8125 | 93 | 93
2018-11-14 20:00 | 76 | 76 |  |  | 43418.8333 | 91 | 91
2018-11-14 20:30 | 74 | 73 |  |  | 43418.8542 | 88 | 88
2018-11-14 21:00 | 71 | 70 |  |  | 43418.875 | 85 | 85
2018-11-14 21:30 | 68 | 68 |  |  | 43418.8958 | 81 | 81
2018-11-14 22:00 | 65 | 65 |  |  | 43418.9167 | 78 | 78
2018-11-14 22:30 | 64 | 63 |  |  | 43418.9375 | 77 | 77
2018-11-14 23:00 | 61 | 61 |  |  | 43418.9583 | 73 | 73
2018-11-14 23:30 | 56 | 56 |  |  | 43418.9792 | 69 | 69
2018-11-15 | 51 | 51 |  |  | 43419 | 64 | 64
2018-11-15 00:30 | 49 | 49 |  |  | 43419.0208 | 62 | 62
2018-11-15 01:00 | 48 | 48 |  |  | 43419.0417 | 59 | 59
2018-11-15 01:30 | 46 | 46 |  |  | 43419.0625 | 57 | 57
2018-11-15 02:00 | 46 | 46 |  |  | 43419.0833 | 57 | 57
2018-11-15 02:30 | 45 | 45 |  |  | 43419.1042 | 55 | 55
2018-11-15 03:00 | 44 | 44 |  |  | 43419.125 | 55 | 55
2018-11-15 03:30 | 45 | 45 |  |  | 43419.1458 | 55 | 55
2018-11-15 04:00 | 46 | 46 |  |  | 43419.1667 | 55 | 55
2018-11-15 04:30 | 45 | 44 |  |  | 43419.1875 | 54 | 54
2018-11-15 05:00 | 45 | 45 |  |  | 43419.2083 | 55 | 55
2018-11-15 05:30 | 48 | 48 |  |  | 43419.2292 | 59 | 59
2018-11-15 06:00 | 51 | 51 |  |  | 43419.25 | 64 | 64
2018-11-15 06:30 | 55 | 55 |  |  | 43419.2708 | 71 | 71
2018-11-15 07:00 | 59 | 59 |  |  | 43419.2917 | 77 | 77
2018-11-15 07:30 | 62 | 62 |  |  | 43419.3125 | 85 | 84
2018-11-15 08:00 | 63 | 63 |  |  | 43419.3333 | 87 | 86
2018-11-15 08:30 | 62 | 61 |  |  | 43419.3542 | 86 | 86
2018-11-15 09:00 | 60 | 59 |  |  | 43419.375 | 85 | 85
2018-11-15 09:30 | 61 | 61 |  |  | 43419.3958 | 86 | 85
2018-11-15 10:00 | 62 | 62 |  |  | 43419.4167 | 87 | 87
2018-11-15 10:30 | 61 | 61 |  |  | 43419.4375 | 85 | 85
2018-11-15 11:00 | 62 | 62 |  |  | 43419.4583 | 85 | 85
2018-11-15 11:30 | 59 | 59 |  |  | 43419.4792 | 85 | 85
2018-11-15 12:00 | 60 | 59 |  |  | 43419.5 | 85 | 85
2018-11-15 12:30 | 59 | 59 |  |  | 43419.5208 | 84 | 84
2018-11-15 13:00 | 63 | 63 |  |  | 43419.5417 | 84 | 84
2018-11-15 13:30 | 66 | 66 |  |  | 43419.5625 | 85 | 85
2018-11-15 14:00 | 73 | 73 |  |  | 43419.5833 | 96 | 95
2018-11-15 14:30 | 77 | 77 |  |  | 43419.6042 | 97 | 96
2018-11-15 15:00 | 76 | 75 |  |  | 43419.625 | 96 | 95
2018-11-15 15:30 | 72 | 72 |  |  | 43419.6458 | 94 | 93
2018-11-15 16:00 | 77 | 76 |  |  | 43419.6667 | 99 | 98
2018-11-15 16:30 | 79 | 78 |  |  | 43419.6875 | 98 | 98
2018-11-15 17:00 | 84 | 83 |  |  | 43419.7083 | 102 | 101
2018-11-15 17:30 | 83 | 82 |  |  | 43419.7292 | 101 | 100
2018-11-15 18:00 | 80 | 79 |  |  | 43419.75 | 96 | 96
2018-11-15 18:30 | 80 | 78 |  |  | 43419.7708 | 94 | 94
2018-11-15 19:00 | 83 | 82 |  |  | 43419.7917 | 97 | 97
2018-11-15 19:30 | 83 | 81 |  |  | 43419.8125 | 97 | 97
2018-11-15 20:00 | 81 | 79 |  |  | 43419.8333 | 95 | 95
2018-11-15 20:30 | 80 | 77 |  |  | 43419.8542 | 93 | 92
2018-11-15 21:00 | 77 | 75 |  |  | 43419.875 | 89 | 89
2018-11-15 21:30 | 76 | 72 |  |  | 43419.8958 | 84 | 84
2018-11-15 22:00 | 76 | 70 |  |  | 43419.9167 | 83 | 83
2018-11-15 22:30 | 74 | 67 |  |  | 43419.9375 | 81 | 81
2018-11-15 23:00 | 70 | 64 |  |  | 43419.9583 | 76 | 76
2018-11-15 23:30 | 65 | 58 |  |  | 43419.9792 | 71 | 71
2018-11-16 | 60 | 51 |  |  | 43420 | 65 | 65
2018-11-16 00:30 | 57 | 49 |  |  | 43420.0208 | 62 | 62
2018-11-16 01:00 | 56 | 46 |  |  | 43420.0417 | 58 | 58
2018-11-16 01:30 | 54 | 44 |  |  | 43420.0625 | 55 | 54
2018-11-16 02:00 | 53 | 43 |  |  | 43420.0833 | 54 | 54
2018-11-16 02:30 | 53 | 43 |  |  | 43420.1042 | 54 | 54
2018-11-16 03:00 | 52 | 42 |  |  | 43420.125 | 52 | 52
2018-11-16 03:30 | 51 | 42 |  |  | 43420.1458 | 52 | 52
2018-11-16 04:00 | 50 | 40 |  |  | 43420.1667 | 52 | 52
2018-11-16 04:30 | 50 | 41 |  |  | 43420.1875 | 52 | 52
2018-11-16 05:00 | 52 | 42 |  |  | 43420.2083 | 54 | 54
2018-11-16 05:30 | 54 | 45 |  |  | 43420.2292 | 58 | 58
2018-11-16 06:00 | 54 | 46 |  |  | 43420.25 | 61 | 61
2018-11-16 06:30 | 55 | 50 |  |  | 43420.2708 | 67 | 67
2018-11-16 07:00 | 57 | 54 |  |  | 43420.2917 | 74 | 73
2018-11-16 07:30 | 53 | 49 |  |  | 43420.3125 | 76 | 76
2018-11-16 08:00 | 57 | 51 |  |  | 43420.3333 | 78 | 78
2018-11-16 08:30 | 58 | 52 |  |  | 43420.3542 | 81 | 81
2018-11-16 09:00 | 57 | 52 |  |  | 43420.375 | 81 | 81
2018-11-16 09:30 | 57 | 53 |  |  | 43420.3958 | 83 | 83
2018-11-16 10:00 | 56 | 53 |  |  | 43420.4167 | 83 | 82
2018-11-16 10:30 | 54 | 51 |  |  | 43420.4375 | 81 | 80
2018-11-16 11:00 | 56 | 52 |  |  | 43420.4583 | 81 | 80
2018-11-16 11:30 | 57 | 53 |  |  | 43420.4792 | 81 | 81
2018-11-16 12:00 | 56 | 53 |  |  | 43420.5 | 81 | 80
2018-11-16 12:30 | 57 | 53 |  |  | 43420.5208 | 80 | 80
2018-11-16 13:00 | 57 | 53 |  |  | 43420.5417 | 79 | 78
2018-11-16 13:30 | 59 | 56 |  |  | 43420.5625 | 80 | 80
2018-11-16 14:00 | 66 | 63 |  |  | 43420.5833 | 85 | 85
2018-11-16 14:30 | 69 | 65 |  |  | 43420.6042 | 87 | 87
2018-11-16 15:00 | 70 | 67 |  |  | 43420.625 | 89 | 89
2018-11-16 15:30 | 74 | 68 |  |  | 43420.6458 | 90 | 89
2018-11-16 16:00 | 91 | 72 |  |  | 43420.6667 | 99 | 95
2018-11-16 16:30 | 95 | 76 |  |  | 43420.6875 | 101 | 98
2018-11-16 17:00 | 99 | 79 |  |  | 43420.7083 | 103 | 100
2018-11-16 17:30 | 103 | 79 |  |  | 43420.7292 | 100 | 98
2018-11-16 18:00 | 110 | 76 |  |  | 43420.75 | 93 | 93
2018-11-16 18:30 | 109 | 75 |  |  | 43420.7708 | 92 | 91
2018-11-16 19:00 | 111 | 78 |  |  | 43420.7917 | 94 | 94
2018-11-16 19:30 | 110 | 76 |  |  | 43420.8125 | 92 | 92
2018-11-16 20:00 | 105 | 75 |  |  | 43420.8333 | 92 | 90
2018-11-16 20:30 | 88 | 72 |  |  | 43420.8542 | 86 | 86
2018-11-16 21:00 | 86 | 69 |  |  | 43420.875 | 82 | 82
2018-11-16 21:30 | 83 | 65 |  |  | 43420.8958 | 78 | 78
2018-11-16 22:00 | 81 | 64 |  |  | 43420.9167 | 77 | 77
2018-11-16 22:30 | 80 | 61 |  |  | 43420.9375 | 75 | 75
2018-11-16 23:00 | 78 | 58 |  |  | 43420.9583 | 71 | 71
2018-11-16 23:30 | 77 | 56 |  |  | 43420.9792 | 69 | 69
2018-11-17 | 73 | 49 |  |  | 43421 | 63 | 63
2018-11-17 00:30 | 70 | 46 |  |  | 43421.0208 | 60 | 60
2018-11-17 01:00 | 69 | 45 |  |  | 43421.0417 | 58 | 58
2018-11-17 01:30 | 68 | 43 |  |  | 43421.0625 | 55 | 55
2018-11-17 02:00 | 66 | 41 |  |  | 43421.0833 | 53 | 53
2018-11-17 02:30 | 66 | 39 |  |  | 43421.1042 | 51 | 51
2018-11-17 03:00 | 65 | 38 |  |  | 43421.125 | 50 | 50
2018-11-17 03:30 | 65 | 38 |  |  | 43421.1458 | 50 | 50
2018-11-17 04:00 | 56 | 38 |  |  | 43421.1667 | 50 | 49
2018-11-17 04:30 | 58 | 40 |  |  | 43421.1875 | 53 | 52
2018-11-17 05:00 | 60 | 41 |  |  | 43421.2083 | 53 | 53
2018-11-17 05:30 | 61 | 42 |  |  | 43421.2292 | 54 | 53
2018-11-17 06:00 | 62 | 43 |  |  | 43421.25 | 55 | 54
2018-11-17 06:30 | 61 | 42 |  |  | 43421.2708 | 56 | 56
2018-11-17 07:00 | 60 | 43 |  |  | 43421.2917 | 57 | 56
2018-11-17 07:30 | 58 | 42 |  |  | 43421.3125 | 56 | 56
2018-11-17 08:00 | 56 | 41 |  |  | 43421.3333 | 58 | 58
2018-11-17 08:30 | 61 | 47 |  |  | 43421.3542 | 63 | 63
2018-11-17 09:00 | 59 | 45 |  |  | 43421.375 | 62 | 62
2018-11-17 09:30 | 67 | 41 |  |  | 43421.3958 | 66 | 65
2018-11-17 10:00 | 75 | 44 |  |  | 43421.4167 | 67 | 65
2018-11-17 10:30 | 76 | 46 |  |  | 43421.4375 | 68 | 65
2018-11-17 11:00 | 76 | 47 |  |  | 43421.4583 | 68 | 65
2018-11-17 11:30 | 76 | 48 |  |  | 43421.4792 | 67 | 64
2018-11-17 12:00 | 76 | 48 |  |  | 43421.5 | 66 | 63
2018-11-17 12:30 | 79 | 53 |  |  | 43421.5208 | 69 | 66
2018-11-17 13:00 | 83 | 54 |  |  | 43421.5417 | 70 | 69
2018-11-17 13:30 | 82 | 51 |  |  | 43421.5625 | 65 | 64
2018-11-17 14:00 | 84 | 54 |  |  | 43421.5833 | 68 | 67
2018-11-17 14:30 | 83 | 52 |  |  | 43421.6042 | 64 | 63
2018-11-17 15:00 | 88 | 60 |  |  | 43421.625 | 73 | 72
2018-11-17 15:30 | 91 | 64 |  |  | 43421.6458 | 79 | 79
2018-11-17 16:00 | 94 | 66 |  |  | 43421.6667 | 82 | 81
2018-11-17 16:30 | 98 | 69 |  |  | 43421.6875 | 85 | 85
2018-11-17 17:00 | 98 | 68 |  |  | 43421.7083 | 84 | 84
2018-11-17 17:30 | 100 | 69 |  |  | 43421.7292 | 85 | 85
2018-11-17 18:00 | 99 | 71 |  |  | 43421.75 | 85 | 85
2018-11-17 18:30 | 97 | 69 |  |  | 43421.7708 | 85 | 84
2018-11-17 19:00 | 97 | 70 |  |  | 43421.7917 | 86 | 85
2018-11-17 19:30 | 95 | 69 |  |  | 43421.8125 | 84 | 84
2018-11-17 20:00 | 86 | 65 |  |  | 43421.8333 | 79 | 79
2018-11-17 20:30 | 78 | 64 |  |  | 43421.8542 | 77 | 77
2018-11-17 21:00 | 67 | 59 |  |  | 43421.875 | 73 | 72
2018-11-17 21:30 | 65 | 58 |  |  | 43421.8958 | 71 | 70
2018-11-17 22:00 | 64 | 56 |  |  | 43421.9167 | 70 | 69
2018-11-17 22:30 | 63 | 55 |  |  | 43421.9375 | 69 | 68
2018-11-17 23:00 | 63 | 54 |  |  | 43421.9583 | 67 | 65
2018-11-17 23:30 | 59 | 50 |  |  | 43421.9792 | 63 | 61
2018-11-18 | 56 | 46 |  |  | 43422 | 59 | 57
2018-11-18 00:30 | 55 | 43 |  |  | 43422.0208 | 57 | 54
2018-11-18 01:00 | 56 | 43 |  |  | 43422.0417 | 57 | 52
2018-11-18 01:30 | 57 | 43 |  |  | 43422.0625 | 57 | 52
2018-11-18 02:00 | 55 | 41 |  |  | 43422.0833 | 55 | 50
2018-11-18 02:30 | 53 | 40 |  |  | 43422.1042 | 53 | 49
2018-11-18 03:00 | 52 | 39 |  |  | 43422.125 | 51 | 48
2018-11-18 03:30 | 52 | 39 |  |  | 43422.1458 | 51 | 48
2018-11-18 04:00 | 52 | 39 |  |  | 43422.1667 | 51 | 48
2018-11-18 04:30 | 52 | 39 |  |  | 43422.1875 | 52 | 48
2018-11-18 05:00 | 53 | 39 |  |  | 43422.2083 | 52 | 48
2018-11-18 05:30 | 53 | 38 |  |  | 43422.2292 | 51 | 48
2018-11-18 06:00 | 52 | 38 |  |  | 43422.25 | 52 | 49
2018-11-18 06:30 | 51 | 36 |  |  | 43422.2708 | 51 | 49
2018-11-18 07:00 | 50 | 36 |  |  | 43422.2917 | 51 | 49
2018-11-18 07:30 | 49 | 36 |  |  | 43422.3125 | 51 | 50
2018-11-18 08:00 | 51 | 39 |  |  | 43422.3333 | 56 | 55
2018-11-18 08:30 | 53 | 43 |  |  | 43422.3542 | 58 | 57
2018-11-18 09:00 | 55 | 46 |  |  | 43422.375 | 60 | 59
2018-11-18 09:30 | 52 | 43 |  |  | 43422.3958 | 60 | 60
2018-11-18 10:00 | 51 | 43 |  |  | 43422.4167 | 60 | 59
2018-11-18 10:30 | 55 | 46 |  |  | 43422.4375 | 55 | 54
2018-11-18 11:00 | 52 | 42 |  |  | 43422.4583 | 57 | 55
2018-11-18 11:30 | 51 | 40 |  |  | 43422.4792 | 57 | 56
2018-11-18 12:00 | 53 | 44 |  |  | 43422.5 | 58 | 56
2018-11-18 12:30 | 53 | 43 |  |  | 43422.5208 | 56 | 54
2018-11-18 13:00 | 48 | 37 |  |  | 43422.5417 | 49 | 47
2018-11-18 13:30 | 50 | 40 |  |  | 43422.5625 | 53 | 52
2018-11-18 14:00 | 54 | 45 |  |  | 43422.5833 | 59 | 57
2018-11-18 14:30 | 52 | 42 |  |  | 43422.6042 | 56 | 54
2018-11-18 15:00 | 53 | 44 |  |  | 43422.625 | 57 | 56
2018-11-18 15:30 | 54 | 45 |  |  | 43422.6458 | 58 | 56
2018-11-18 16:00 | 57 | 48 |  |  | 43422.6667 | 62 | 61
2018-11-18 16:30 | 58 | 49 |  |  | 43422.6875 | 66 | 64
2018-11-18 17:00 | 61 | 51 |  |  | 43422.7083 | 68 | 65
2018-11-18 17:30 | 66 | 54 |  |  | 43422.7292 | 72 | 67
2018-11-18 18:00 | 68 | 56 |  |  | 43422.75 | 75 | 70
2018-11-18 18:30 | 71 | 59 |  |  | 43422.7708 | 78 | 73
2018-11-18 19:00 | 74 | 63 |  |  | 43422.7917 | 83 | 78
2018-11-18 19:30 | 73 | 63 |  |  | 43422.8125 | 81 | 77
2018-11-18 20:00 | 72 | 61 |  |  | 43422.8333 | 79 | 75
2018-11-18 20:30 | 70 | 59 |  |  | 43422.8542 | 78 | 74
2018-11-18 21:00 | 64 | 57 |  |  | 43422.875 | 72 | 71
2018-11-18 21:30 | 64 | 56 |  |  | 43422.8958 | 70 | 69
2018-11-18 22:00 | 62 | 54 |  |  | 43422.9167 | 68 | 67
2018-11-18 22:30 | 61 | 52 |  |  | 43422.9375 | 67 | 65
2018-11-18 23:00 | 60 | 50 |  |  | 43422.9583 | 63 | 61
2018-11-18 23:30 | 58 | 48 |  |  | 43422.9792 | 61 | 59
2018-11-19 | 55 | 45 |  |  | 43423 | 58 | 56
2018-11-19 00:30 | 53 | 42 |  |  | 43423.0208 | 55 | 52
2018-11-19 01:00 | 53 | 40 |  |  | 43423.0417 | 53 | 50
2018-11-19 01:30 | 53 | 40 |  |  | 43423.0625 | 52 | 48
2018-11-19 02:00 | 53 | 40 |  |  | 43423.0833 | 51 | 48
2018-11-19 02:30 | 53 | 40 |  |  | 43423.1042 | 52 | 49
2018-11-19 03:00 | 53 | 40 |  |  | 43423.125 | 51 | 48
2018-11-19 03:30 | 53 | 40 |  |  | 43423.1458 | 52 | 49
2018-11-19 04:00 | 53 | 40 |  |  | 43423.1667 | 51 | 48
2018-11-19 04:30 | 53 | 40 |  |  | 43423.1875 | 51 | 47
2018-11-19 05:00 | 54 | 41 |  |  | 43423.2083 | 53 | 49
2018-11-19 05:30 | 56 | 44 |  |  | 43423.2292 | 56 | 53
2018-11-19 06:00 | 55 | 46 |  |  | 43423.25 | 58 | 56
2018-11-19 06:30 | 56 | 49 |  |  | 43423.2708 | 63 | 62
2018-11-19 07:00 | 55 | 49 |  |  | 43423.2917 | 67 | 66
2018-11-19 07:30 | 52 | 47 |  |  | 43423.3125 | 70 | 70
2018-11-19 08:00 | 53 | 47 |  |  | 43423.3333 | 72 | 71
2018-11-19 08:30 | 52 | 46 |  |  | 43423.3542 | 72 | 71
2018-11-19 09:00 | 58 | 47 |  |  | 43423.375 | 72 | 72
2018-11-19 09:30 | 61 | 50 |  |  | 43423.3958 | 79 | 79
2018-11-19 10:00 | 63 | 53 |  |  | 43423.4167 | 80 | 80
2018-11-19 10:30 | 58 | 47 |  |  | 43423.4375 | 69 | 69
2018-11-19 11:00 | 61 | 49 |  |  | 43423.4583 | 71 | 71
2018-11-19 11:30 | 60 | 49 |  |  | 43423.4792 | 70 | 70
2018-11-19 12:00 | 58 | 48 |  |  | 43423.5 | 70 | 70
2018-11-19 12:30 | 58 | 48 |  |  | 43423.5208 | 70 | 70
2018-11-19 13:00 | 58 | 47 |  |  | 43423.5417 | 69 | 69
2018-11-19 13:30 | 57 | 45 |  |  | 43423.5625 | 69 | 69
2018-11-19 14:00 | 66 | 56 |  |  | 43423.5833 | 73 | 73
2018-11-19 14:30 | 67 | 57 |  |  | 43423.6042 | 74 | 74
2018-11-19 15:00 | 66 | 56 |  |  | 43423.625 | 74 | 74
2018-11-19 15:30 | 67 | 57 |  |  | 43423.6458 | 75 | 75
2018-11-19 16:00 | 70 | 60 |  |  | 43423.6667 | 79 | 79
2018-11-19 16:30 | 78 | 69 |  |  | 43423.6875 | 91 | 91
2018-11-19 17:00 | 83 | 74 |  |  | 43423.7083 | 97 | 97
2018-11-19 17:30 | 85 | 75 |  |  | 43423.7292 | 96 | 96
2018-11-19 18:00 | 87 | 77 |  |  | 43423.75 | 95 | 95
2018-11-19 18:30 | 88 | 76 |  |  | 43423.7708 | 93 | 92
2018-11-19 19:00 | 92 | 82 |  |  | 43423.7917 | 97 | 96
2018-11-19 19:30 | 91 | 81 |  |  | 43423.8125 | 97 | 96
2018-11-19 20:00 | 91 | 79 |  |  | 43423.8333 | 95 | 94
2018-11-19 20:30 | 89 | 78 |  |  | 43423.8542 | 93 | 93
2018-11-19 21:00 | 84 | 75 |  |  | 43423.875 | 90 | 90
2018-11-19 21:30 | 82 | 73 |  |  | 43423.8958 | 86 | 86
2018-11-19 22:00 | 80 | 69 |  |  | 43423.9167 | 84 | 84
2018-11-19 22:30 | 77 | 65 |  |  | 43423.9375 | 81 | 81
2018-11-19 23:00 | 76 | 63 |  |  | 43423.9583 | 77 | 77
2018-11-19 23:30 | 73 | 58 |  |  | 43423.9792 | 73 | 73
2018-11-20 | 70 | 54 |  |  | 43424 | 68 | 68
2018-11-20 00:30 | 68 | 50 |  |  | 43424.0208 | 64 | 63
2018-11-20 01:00 | 67 | 48 |  |  | 43424.0417 | 62 | 60
2018-11-20 01:30 | 67 | 47 |  |  | 43424.0625 | 59 | 58
2018-11-20 02:00 | 67 | 46 |  |  | 43424.0833 | 59 | 57
2018-11-20 02:30 | 68 | 47 |  |  | 43424.1042 | 59 | 57
2018-11-20 03:00 | 66 | 45 |  |  | 43424.125 | 58 | 57
2018-11-20 03:30 | 64 | 45 |  |  | 43424.1458 | 58 | 57
2018-11-20 04:00 | 63 | 44 |  |  | 43424.1667 | 58 | 57
2018-11-20 04:30 | 64 | 46 |  |  | 43424.1875 | 60 | 59
2018-11-20 05:00 | 64 | 47 |  |  | 43424.2083 | 61 | 61
2018-11-20 05:30 | 65 | 48 |  |  | 43424.2292 | 64 | 64
2018-11-20 06:00 | 65 | 50 |  |  | 43424.25 | 67 | 67
2018-11-20 06:30 | 67 | 54 |  |  | 43424.2708 | 74 | 74
2018-11-20 07:00 | 69 | 55 |  |  | 43424.2917 | 79 | 79
2018-11-20 07:30 | 66 | 52 |  |  | 43424.3125 | 81 | 81
2018-11-20 08:00 | 66 | 52 |  |  | 43424.3333 | 81 | 81
2018-11-20 08:30 | 62 | 47 |  |  | 43424.3542 | 74 | 74
2018-11-20 09:00 | 59 | 45 |  |  | 43424.375 | 71 | 71
2018-11-20 09:30 | 62 | 46 |  |  | 43424.3958 | 72 | 72
2018-11-20 10:00 | 62 | 45 |  |  | 43424.4167 | 71 | 71
2018-11-20 10:30 | 61 | 45 |  |  | 43424.4375 | 70 | 70
2018-11-20 11:00 | 61 | 46 |  |  | 43424.4583 | 69 | 69
2018-11-20 11:30 | 61 | 46 |  |  | 43424.4792 | 69 | 69
2018-11-20 12:00 | 61 | 46 |  |  | 43424.5 | 69 | 69
2018-11-20 12:30 | 60 | 45 |  |  | 43424.5208 | 67 | 67
2018-11-20 13:00 | 61 | 47 |  |  | 43424.5417 | 68 | 67
2018-11-20 13:30 | 61 | 47 |  |  | 43424.5625 | 70 | 70
2018-11-20 14:00 | 61 | 46 |  |  | 43424.5833 | 70 | 69
2018-11-20 14:30 | 61 | 47 |  |  | 43424.6042 | 71 | 70
2018-11-20 15:00 | 67 | 53 |  |  | 43424.625 | 81 | 81
2018-11-20 15:30 | 79 | 67 |  |  | 43424.6458 | 92 | 91
2018-11-20 16:00 | 84 | 73 |  |  | 43424.6667 | 96 | 96
2018-11-20 16:30 | 89 | 78 |  |  | 43424.6875 | 103 | 102
2018-11-20 17:00 | 91 | 79 |  |  | 43424.7083 | 102 | 101
2018-11-20 17:30 | 94 | 81 |  |  | 43424.7292 | 103 | 101
2018-11-20 18:00 | 95 | 81 |  |  | 43424.75 | 102 | 100
2018-11-20 18:30 | 94 | 81 |  |  | 43424.7708 | 100 | 98
2018-11-20 19:00 | 96 | 85 |  |  | 43424.7917 | 104 | 102
2018-11-20 19:30 | 96 | 85 |  |  | 43424.8125 | 103 | 102
2018-11-20 20:00 | 94 | 84 |  |  | 43424.8333 | 102 | 100
2018-11-20 20:30 | 91 | 81 |  |  | 43424.8542 | 99 | 98
2018-11-20 21:00 | 87 | 78 |  |  | 43424.875 | 94 | 94
2018-11-20 21:30 | 85 | 76 |  |  | 43424.8958 | 90 | 90
2018-11-20 22:00 | 82 | 72 |  |  | 43424.9167 | 87 | 87
2018-11-20 22:30 | 81 | 69 |  |  | 43424.9375 | 84 | 84
2018-11-20 23:00 | 79 | 67 |  |  | 43424.9583 | 80 | 79
2018-11-20 23:30 | 76 | 62 |  |  | 43424.9792 | 76 | 75
2018-11-21 | 73 | 57 |  |  | 43425 | 71 | 70
2018-11-21 00:30 | 71 | 54 |  |  | 43425.0208 | 68 | 67
2018-11-21 01:00 | 71 | 53 |  |  | 43425.0417 | 65 | 64
2018-11-21 01:30 | 70 | 52 |  |  | 43425.0625 | 63 | 61
2018-11-21 02:00 | 69 | 51 |  |  | 43425.0833 | 62 | 60
2018-11-21 02:30 | 68 | 49 |  |  | 43425.1042 | 61 | 59
2018-11-21 03:00 | 68 | 48 |  |  | 43425.125 | 60 | 58
2018-11-21 03:30 | 68 | 48 |  |  | 43425.1458 | 60 | 58
2018-11-21 04:00 | 69 | 49 |  |  | 43425.1667 | 62 | 60
2018-11-21 04:30 | 70 | 50 |  |  | 43425.1875 | 63 | 60
2018-11-21 05:00 | 69 | 50 |  |  | 43425.2083 | 64 | 62
2018-11-21 05:30 | 71 | 54 |  |  | 43425.2292 | 69 | 67
2018-11-21 06:00 | 73 | 58 |  |  | 43425.25 | 73 | 72
2018-11-21 06:30 | 75 | 62 |  |  | 43425.2708 | 81 | 80
2018-11-21 07:00 | 76 | 66 |  |  | 43425.2917 | 86 | 86
2018-11-21 07:30 | 77 | 66 |  |  | 43425.3125 | 90 | 89
2018-11-21 08:00 | 72 | 61 |  |  | 43425.3333 | 88 | 88
2018-11-21 08:30 | 62 | 53 |  |  | 43425.3542 | 86 | 86
2018-11-21 09:00 | 56 | 47 |  |  | 43425.375 | 83 | 83
2018-11-21 09:30 | 56 | 47 |  |  | 43425.3958 | 83 | 83
2018-11-21 10:00 | 57 | 48 |  |  | 43425.4167 | 84 | 84
2018-11-21 10:30 | 57 | 48 |  |  | 43425.4375 | 84 | 84
2018-11-21 11:00 | 59 | 50 |  |  | 43425.4583 | 86 | 86
2018-11-21 11:30 | 59 | 53 |  |  | 43425.4792 | 88 | 88
2018-11-21 12:00 | 58 | 54 |  |  | 43425.5 | 91 | 90
2018-11-21 12:30 | 59 | 56 |  |  | 43425.5208 | 92 | 91
2018-11-21 13:00 | 62 | 58 |  |  | 43425.5417 | 92 | 91
2018-11-21 13:30 | 63 | 59 |  |  | 43425.5625 | 94 | 94
2018-11-21 14:00 | 73 | 69 |  |  | 43425.5833 | 99 | 99
2018-11-21 14:30 | 80 | 78 |  |  | 43425.6042 | 106 | 106
2018-11-21 15:00 | 92 | 90 |  |  | 43425.625 | 113 | 113
2018-11-21 15:30 | 94 | 93 |  |  | 43425.6458 | 115 | 115
2018-11-21 16:00 | 98 | 96 |  |  | 43425.6667 | 119 | 119
2018-11-21 16:30 | 98 | 97 |  |  | 43425.6875 | 118 | 118
2018-11-21 17:00 | 100 | 99 |  |  | 43425.7083 | 117 | 117
2018-11-21 17:30 | 99 | 97 |  |  | 43425.7292 | 117 | 117
2018-11-21 18:00 | 98 | 95 |  |  | 43425.75 | 115 | 115
2018-11-21 18:30 | 98 | 95 |  |  | 43425.7708 | 113 | 113
2018-11-21 19:00 | 99 | 97 |  |  | 43425.7917 | 115 | 115
2018-11-21 19:30 | 100 | 97 |  |  | 43425.8125 | 114 | 114
2018-11-21 20:00 | 96 | 94 |  |  | 43425.8333 | 111 | 111
2018-11-21 20:30 | 95 | 92 |  |  | 43425.8542 | 110 | 110
2018-11-21 21:00 | 91 | 90 |  |  | 43425.875 | 107 | 107
2018-11-21 21:30 | 88 | 86 |  |  | 43425.8958 | 103 | 103
2018-11-21 22:00 | 84 | 82 |  |  | 43425.9167 | 100 | 100
2018-11-21 22:30 | 81 | 78 |  |  | 43425.9375 | 96 | 96
2018-11-21 23:00 | 78 | 75 |  |  | 43425.9583 | 92 | 92
2018-11-21 23:30 | 75 | 70 |  |  | 43425.9792 | 87 | 87
2018-11-22 | 72 | 66 |  |  | 43426 | 82 | 82
2018-11-22 00:30 | 69 | 62 |  |  | 43426.0208 | 77 | 77
2018-11-22 01:00 | 67 | 59 |  |  | 43426.0417 | 74 | 74
2018-11-22 01:30 | 66 | 58 |  |  | 43426.0625 | 71 | 71
2018-11-22 02:00 | 66 | 57 |  |  | 43426.0833 | 70 | 70
2018-11-22 02:30 | 65 | 56 |  |  | 43426.1042 | 68 | 68
2018-11-22 03:00 | 64 | 55 |  |  | 43426.125 | 67 | 67
2018-11-22 03:30 | 64 | 55 |  |  | 43426.1458 | 67 | 67
2018-11-22 04:00 | 64 | 55 |  |  | 43426.1667 | 67 | 67
2018-11-22 04:30 | 64 | 55 |  |  | 43426.1875 | 67 | 67
2018-11-22 05:00 | 65 | 57 |  |  | 43426.2083 | 70 | 70
2018-11-22 05:30 | 66 | 59 |  |  | 43426.2292 | 74 | 74
2018-11-22 06:00 | 68 | 62 |  |  | 43426.25 | 79 | 79
2018-11-22 06:30 | 76 | 70 |  |  | 43426.2708 | 90 | 90
2018-11-22 07:00 | 78 | 73 |  |  | 43426.2917 | 96 | 96
2018-11-22 07:30 | 78 | 75 |  |  | 43426.3125 | 105 | 105
2018-11-22 08:00 | 79 | 76 |  |  | 43426.3333 | 113 | 112
2018-11-22 08:30 | 68 | 66 |  |  | 43426.3542 | 107 | 106
2018-11-22 09:00 | 63 | 60 |  |  | 43426.375 | 102 | 101
2018-11-22 09:30 | 65 | 62 |  |  | 43426.3958 | 107 | 106
2018-11-22 10:00 | 62 | 60 |  |  | 43426.4167 | 106 | 105
2018-11-22 10:30 | 63 | 61 |  |  | 43426.4375 | 105 | 104
2018-11-22 11:00 | 71 | 69 |  |  | 43426.4583 | 109 | 109
2018-11-22 11:30 | 78 | 77 |  |  | 43426.4792 | 121 | 120
2018-11-22 12:00 | 78 | 77 |  |  | 43426.5 | 121 | 120
2018-11-22 12:30 | 72 | 71 |  |  | 43426.5208 | 116 | 114
2018-11-22 13:00 | 68 | 65 |  |  | 43426.5417 | 108 | 106
2018-11-22 13:30 | 74 | 70 |  |  | 43426.5625 | 105 | 104
2018-11-22 14:00 | 72 | 68 |  |  | 43426.5833 | 102 | 100
2018-11-22 14:30 | 74 | 71 |  |  | 43426.6042 | 105 | 104
2018-11-22 15:00 | 74 | 70 |  |  | 43426.625 | 104 | 103
2018-11-22 15:30 | 91 | 86 |  |  | 43426.6458 | 111 | 111
2018-11-22 16:00 | 92 | 88 |  |  | 43426.6667 | 111 | 111
2018-11-22 16:30 | 99 | 93 |  |  | 43426.6875 | 117 | 117
2018-11-22 17:00 | 101 | 96 |  |  | 43426.7083 | 120 | 120
2018-11-22 17:30 | 101 | 96 |  |  | 43426.7292 | 118 | 118
2018-11-22 18:00 | 100 | 94 |  |  | 43426.75 | 116 | 116
2018-11-22 18:30 | 100 | 93 |  |  | 43426.7708 | 113 | 113
2018-11-22 19:00 | 103 | 97 |  |  | 43426.7917 | 116 | 116
2018-11-22 19:30 | 103 | 97 |  |  | 43426.8125 | 115 | 115
2018-11-22 20:00 | 102 | 96 |  |  | 43426.8333 | 113 | 113
2018-11-22 20:30 | 99 | 94 |  |  | 43426.8542 | 111 | 111
2018-11-22 21:00 | 95 | 90 |  |  | 43426.875 | 106 | 106
2018-11-22 21:30 | 90 | 84 |  |  | 43426.8958 | 100 | 100
2018-11-22 22:00 | 89 | 82 |  |  | 43426.9167 | 97 | 97
2018-11-22 22:30 | 86 | 78 |  |  | 43426.9375 | 93 | 93
2018-11-22 23:00 | 84 | 75 |  |  | 43426.9583 | 89 | 89
2018-11-22 23:30 | 80 | 70 |  |  | 43426.9792 | 84 | 84
2018-11-23 | 76 | 65 |  |  | 43427 | 79 | 79
2018-11-23 00:30 | 72 | 61 |  |  | 43427.0208 | 72 | 72
2018-11-23 01:00 | 71 | 58 |  |  | 43427.0417 | 70 | 70
2018-11-23 01:30 | 72 | 57 |  |  | 43427.0625 | 67 | 67
2018-11-23 02:00 | 70 | 54 |  |  | 43427.0833 | 65 | 65
2018-11-23 02:30 | 71 | 54 |  |  | 43427.1042 | 65 | 65
2018-11-23 03:00 | 71 | 54 |  |  | 43427.125 | 66 | 65
2018-11-23 03:30 | 71 | 54 |  |  | 43427.1458 | 65 | 65
2018-11-23 04:00 | 71 | 53 |  |  | 43427.1667 | 64 | 64
2018-11-23 04:30 | 70 | 52 |  |  | 43427.1875 | 63 | 63
2018-11-23 05:00 | 70 | 53 |  |  | 43427.2083 | 64 | 64
2018-11-23 05:30 | 71 | 55 |  |  | 43427.2292 | 68 | 67
2018-11-23 06:00 | 70 | 56 |  |  | 43427.25 | 71 | 71
2018-11-23 06:30 | 72 | 60 |  |  | 43427.2708 | 79 | 79
2018-11-23 07:00 | 73 | 63 |  |  | 43427.2917 | 84 | 84
2018-11-23 07:30 | 74 | 64 |  |  | 43427.3125 | 87 | 87
2018-11-23 08:00 | 77 | 67 |  |  | 43427.3333 | 90 | 90
2018-11-23 08:30 | 76 | 66 |  |  | 43427.3542 | 90 | 90
2018-11-23 09:00 | 75 | 65 |  |  | 43427.375 | 89 | 89
2018-11-23 09:30 | 74 | 63 |  |  | 43427.3958 | 85 | 85
2018-11-23 10:00 | 72 | 62 |  |  | 43427.4167 | 84 | 84
2018-11-23 10:30 | 70 | 60 |  |  | 43427.4375 | 82 | 82
2018-11-23 11:00 | 70 | 61 |  |  | 43427.4583 | 84 | 84
2018-11-23 11:30 | 70 | 60 |  |  | 43427.4792 | 84 | 84
2018-11-23 12:00 | 70 | 60 |  |  | 43427.5 | 84 | 84
2018-11-23 12:30 | 71 | 60 |  |  | 43427.5208 | 84 | 84
2018-11-23 13:00 | 71 | 61 |  |  | 43427.5417 | 85 | 85
2018-11-23 13:30 | 73 | 63 |  |  | 43427.5625 | 89 | 89
2018-11-23 14:00 | 77 | 67 |  |  | 43427.5833 | 92 | 92
2018-11-23 14:30 | 79 | 70 |  |  | 43427.6042 | 94 | 94
2018-11-23 15:00 | 81 | 71 |  |  | 43427.625 | 95 | 95
2018-11-23 15:30 | 83 | 73 |  |  | 43427.6458 | 97 | 96
2018-11-23 16:00 | 87 | 76 |  |  | 43427.6667 | 100 | 100
2018-11-23 16:30 | 91 | 80 |  |  | 43427.6875 | 103 | 103
2018-11-23 17:00 | 93 | 83 |  |  | 43427.7083 | 106 | 105
2018-11-23 17:30 | 93 | 82 |  |  | 43427.7292 | 104 | 104
2018-11-23 18:00 | 93 | 80 |  |  | 43427.75 | 101 | 100
2018-11-23 18:30 | 90 | 78 |  |  | 43427.7708 | 99 | 99
2018-11-23 19:00 | 91 | 81 |  |  | 43427.7917 | 102 | 101
2018-11-23 19:30 | 91 | 80 |  |  | 43427.8125 | 100 | 100
2018-11-23 20:00 | 91 | 80 |  |  | 43427.8333 | 99 | 99
2018-11-23 20:30 | 89 | 78 |  |  | 43427.8542 | 96 | 96
2018-11-23 21:00 | 85 | 73 |  |  | 43427.875 | 91 | 90
2018-11-23 21:30 | 81 | 71 |  |  | 43427.8958 | 88 | 87
2018-11-23 22:00 | 79 | 69 |  |  | 43427.9167 | 86 | 86
2018-11-23 22:30 | 78 | 67 |  |  | 43427.9375 | 84 | 84
2018-11-23 23:00 | 78 | 66 |  |  | 43427.9583 | 81 | 80
2018-11-23 23:30 | 74 | 61 |  |  | 43427.9792 | 77 | 76
2018-11-24 | 70 | 57 |  |  | 43428 | 73 | 72
2018-11-24 00:30 | 69 | 55 |  |  | 43428.0208 | 68 | 67
2018-11-24 01:00 | 68 | 52 |  |  | 43428.0417 | 66 | 65
2018-11-24 01:30 | 67 | 50 |  |  | 43428.0625 | 64 | 62
2018-11-24 02:00 | 66 | 49 |  |  | 43428.0833 | 63 | 61
2018-11-24 02:30 | 66 | 48 |  |  | 43428.1042 | 63 | 61
2018-11-24 03:00 | 65 | 47 |  |  | 43428.125 | 63 | 61
2018-11-24 03:30 | 64 | 47 |  |  | 43428.1458 | 61 | 61
2018-11-24 04:00 | 64 | 47 |  |  | 43428.1667 | 61 | 61
2018-11-24 04:30 | 64 | 47 |  |  | 43428.1875 | 61 | 61
2018-11-24 05:00 | 63 | 46 |  |  | 43428.2083 | 59 | 59
2018-11-24 05:30 | 60 | 45 |  |  | 43428.2292 | 60 | 59
2018-11-24 06:00 | 55 | 45 |  |  | 43428.25 | 62 | 59
2018-11-24 06:30 | 52 | 44 |  |  | 43428.2708 | 61 | 60
2018-11-24 07:00 | 51 | 43 |  |  | 43428.2917 | 61 | 59
2018-11-24 07:30 | 49 | 42 |  |  | 43428.3125 | 60 | 59
2018-11-24 08:00 | 48 | 42 |  |  | 43428.3333 | 59 | 58
2018-11-24 08:30 | 49 | 44 |  |  | 43428.3542 | 60 | 59
2018-11-24 09:00 | 49 | 45 |  |  | 43428.375 | 61 | 61
2018-11-24 09:30 | 49 | 44 |  |  | 43428.3958 | 61 | 61
2018-11-24 10:00 | 49 | 44 |  |  | 43428.4167 | 61 | 61
2018-11-24 10:30 | 49 | 44 |  |  | 43428.4375 | 60 | 59
2018-11-24 11:00 | 49 | 44 |  |  | 43428.4583 | 59 | 59
2018-11-24 11:30 | 47 | 43 |  |  | 43428.4792 | 59 | 59
2018-11-24 12:00 | 47 | 43 |  |  | 43428.5 | 59 | 59
2018-11-24 12:30 | 47 | 43 |  |  | 43428.5208 | 59 | 59
2018-11-24 13:00 | 47 | 42 |  |  | 43428.5417 | 60 | 60
2018-11-24 13:30 | 49 | 44 |  |  | 43428.5625 | 60 | 60
2018-11-24 14:00 | 50 | 46 |  |  | 43428.5833 | 64 | 64
2018-11-24 14:30 | 54 | 50 |  |  | 43428.6042 | 67 | 67
2018-11-24 15:00 | 58 | 55 |  |  | 43428.625 | 71 | 70
2018-11-24 15:30 | 61 | 58 |  |  | 43428.6458 | 74 | 74
2018-11-24 16:00 | 64 | 61 |  |  | 43428.6667 | 78 | 78
2018-11-24 16:30 | 66 | 63 |  |  | 43428.6875 | 81 | 81
2018-11-24 17:00 | 70 | 66 |  |  | 43428.7083 | 84 | 83
2018-11-24 17:30 | 72 | 67 |  |  | 43428.7292 | 86 | 85
2018-11-24 18:00 | 72 | 67 |  |  | 43428.75 | 87 | 86
2018-11-24 18:30 | 73 | 68 |  |  | 43428.7708 | 87 | 86
2018-11-24 19:00 | 77 | 72 |  |  | 43428.7917 | 92 | 90
2018-11-24 19:30 | 77 | 72 |  |  | 43428.8125 | 92 | 91
2018-11-24 20:00 | 76 | 71 |  |  | 43428.8333 | 90 | 88
2018-11-24 20:30 | 73 | 69 |  |  | 43428.8542 | 88 | 87
2018-11-24 21:00 | 69 | 65 |  |  | 43428.875 | 84 | 83
2018-11-24 21:30 | 67 | 63 |  |  | 43428.8958 | 81 | 80
2018-11-24 22:00 | 66 | 61 |  |  | 43428.9167 | 80 | 79
2018-11-24 22:30 | 67 | 61 |  |  | 43428.9375 | 79 | 78
2018-11-24 23:00 | 65 | 59 |  |  | 43428.9583 | 75 | 74
2018-11-24 23:30 | 63 | 55 |  |  | 43428.9792 | 73 | 72
2018-11-25 | 61 | 52 |  |  | 43429 | 70 | 68
2018-11-25 00:30 | 58 | 48 |  |  | 43429.0208 | 66 | 63
2018-11-25 01:00 | 54 | 46 |  |  | 43429.0417 | 61 | 60
2018-11-25 01:30 | 53 | 44 |  |  | 43429.0625 | 59 | 57
2018-11-25 02:00 | 51 | 42 |  |  | 43429.0833 | 58 | 56
2018-11-25 02:30 | 51 | 41 |  |  | 43429.1042 | 57 | 55
2018-11-25 03:00 | 51 | 41 |  |  | 43429.125 | 57 | 55
2018-11-25 03:30 | 50 | 40 |  |  | 43429.1458 | 57 | 54
2018-11-25 04:00 | 49 | 40 |  |  | 43429.1667 | 56 | 54
2018-11-25 04:30 | 50 | 40 |  |  | 43429.1875 | 56 | 54
2018-11-25 05:00 | 52 | 42 |  |  | 43429.2083 | 57 | 55
2018-11-25 05:30 | 52 | 43 |  |  | 43429.2292 | 59 | 58
2018-11-25 06:00 | 52 | 43 |  |  | 43429.25 | 59 | 58
2018-11-25 06:30 | 50 | 41 |  |  | 43429.2708 | 58 | 57
2018-11-25 07:00 | 48 | 38 |  |  | 43429.2917 | 57 | 56
2018-11-25 07:30 | 46 | 38 |  |  | 43429.3125 | 56 | 56
2018-11-25 08:00 | 46 | 39 |  |  | 43429.3333 | 58 | 58
2018-11-25 08:30 | 47 | 41 |  |  | 43429.3542 | 61 | 61
2018-11-25 09:00 | 47 | 42 |  |  | 43429.375 | 62 | 62
2018-11-25 09:30 | 58 | 53 |  |  | 43429.3958 | 76 | 76
2018-11-25 10:00 | 52 | 47 |  |  | 43429.4167 | 69 | 69
2018-11-25 10:30 | 53 | 47 |  |  | 43429.4375 | 69 | 69
2018-11-25 11:00 | 58 | 53 |  |  | 43429.4583 | 67 | 67
2018-11-25 11:30 | 60 | 56 |  |  | 43429.4792 | 74 | 74
2018-11-25 12:00 | 55 | 50 |  |  | 43429.5 | 69 | 69
2018-11-25 12:30 | 58 | 54 |  |  | 43429.5208 | 70 | 70
2018-11-25 13:00 | 66 | 63 |  |  | 43429.5417 | 77 | 77
2018-11-25 13:30 | 73 | 66 |  |  | 43429.5625 | 86 | 86
2018-11-25 14:00 | 81 | 70 |  |  | 43429.5833 | 91 | 91
2018-11-25 14:30 | 81 | 68 |  |  | 43429.6042 | 86 | 86
2018-11-25 15:00 | 85 | 74 |  |  | 43429.625 | 94 | 93
2018-11-25 15:30 | 94 | 84 |  |  | 43429.6458 | 102 | 101
2018-11-25 16:00 | 91 | 78 |  |  | 43429.6667 | 97 | 95
2018-11-25 16:30 | 92 | 80 |  |  | 43429.6875 | 99 | 98
2018-11-25 17:00 | 95 | 85 |  |  | 43429.7083 | 106 | 105
2018-11-25 17:30 | 97 | 86 |  |  | 43429.7292 | 107 | 106
2018-11-25 18:00 | 98 | 86 |  |  | 43429.75 | 107 | 105
2018-11-25 18:30 | 97 | 84 |  |  | 43429.7708 | 107 | 105
2018-11-25 19:00 | 97 | 85 |  |  | 43429.7917 | 109 | 107
2018-11-25 19:30 | 97 | 85 |  |  | 43429.8125 | 110 | 108
2018-11-25 20:00 | 96 | 83 |  |  | 43429.8333 | 108 | 106
2018-11-25 20:30 | 96 | 83 |  |  | 43429.8542 | 107 | 105
2018-11-25 21:00 | 92 | 79 |  |  | 43429.875 | 102 | 100
2018-11-25 21:30 | 88 | 76 |  |  | 43429.8958 | 98 | 97
2018-11-25 22:00 | 86 | 72 |  |  | 43429.9167 | 96 | 95
2018-11-25 22:30 | 82 | 71 |  |  | 43429.9375 | 93 | 93
2018-11-25 23:00 | 79 | 67 |  |  | 43429.9583 | 88 | 88
2018-11-25 23:30 | 77 | 63 |  |  | 43429.9792 | 85 | 84
2018-11-26 | 76 | 60 |  |  | 43430 | 81 | 79
2018-11-26 00:30 | 73 | 56 |  |  | 43430.0208 | 75 | 73
2018-11-26 01:00 | 70 | 52 |  |  | 43430.0417 | 71 | 69
2018-11-26 01:30 | 68 | 50 |  |  | 43430.0625 | 67 | 65
2018-11-26 02:00 | 67 | 48 |  |  | 43430.0833 | 65 | 64
2018-11-26 02:30 | 66 | 48 |  |  | 43430.1042 | 65 | 63
2018-11-26 03:00 | 66 | 47 |  |  | 43430.125 | 64 | 62
2018-11-26 03:30 | 66 | 47 |  |  | 43430.1458 | 63 | 61
2018-11-26 04:00 | 65 | 46 |  |  | 43430.1667 | 63 | 61
2018-11-26 04:30 | 65 | 47 |  |  | 43430.1875 | 63 | 61
2018-11-26 05:00 | 67 | 49 |  |  | 43430.2083 | 66 | 64
2018-11-26 05:30 | 67 | 51 |  |  | 43430.2292 | 68 | 67
2018-11-26 06:00 | 68 | 55 |  |  | 43430.25 | 74 | 73
2018-11-26 06:30 | 69 | 59 |  |  | 43430.2708 | 81 | 81
2018-11-26 07:00 | 69 | 61 |  |  | 43430.2917 | 88 | 88
2018-11-26 07:30 | 72 | 64 |  |  | 43430.3125 | 94 | 94
2018-11-26 08:00 | 75 | 67 |  |  | 43430.3333 | 97 | 97
2018-11-26 08:30 | 73 | 68 |  |  | 43430.3542 | 98 | 98
2018-11-26 09:00 | 71 | 66 |  |  | 43430.375 | 98 | 97
2018-11-26 09:30 | 72 | 68 |  |  | 43430.3958 | 100 | 100
2018-11-26 10:00 | 74 | 70 |  |  | 43430.4167 | 101 | 101
2018-11-26 10:30 | 74 | 71 |  |  | 43430.4375 | 102 | 101
2018-11-26 11:00 | 77 | 74 |  |  | 43430.4583 | 104 | 103
2018-11-26 11:30 | 77 | 74 |  |  | 43430.4792 | 105 | 105
2018-11-26 12:00 | 79 | 76 |  |  | 43430.5 | 107 | 106
2018-11-26 12:30 | 82 | 79 |  |  | 43430.5208 | 109 | 108
2018-11-26 13:00 | 84 | 81 |  |  | 43430.5417 | 110 | 110
2018-11-26 13:30 | 89 | 85 |  |  | 43430.5625 | 115 | 115
2018-11-26 14:00 | 96 | 90 |  |  | 43430.5833 | 119 | 118
2018-11-26 14:30 | 99 | 94 |  |  | 43430.6042 | 122 | 122
2018-11-26 15:00 | 101 | 97 |  |  | 43430.625 | 124 | 124
2018-11-26 15:30 | 104 | 99 |  |  | 43430.6458 | 127 | 126
2018-11-26 16:00 | 116 | 104 |  |  | 43430.6667 | 133 | 132
2018-11-26 16:30 | 122 | 105 |  |  | 43430.6875 | 135 | 134
2018-11-26 17:00 | 124 | 105 |  |  | 43430.7083 | 136 | 135
2018-11-26 17:30 | 123 | 104 |  |  | 43430.7292 | 133 | 132
2018-11-26 18:00 | 115 | 97 |  |  | 43430.75 | 126 | 126
2018-11-26 18:30 | 114 | 94 |  |  | 43430.7708 | 121 | 120
2018-11-26 19:00 | 104 | 87 |  |  | 43430.7917 | 121 | 119
2018-11-26 19:30 | 97 | 85 |  |  | 43430.8125 | 130 | 118
2018-11-26 20:00 | 84 | 81 |  |  | 43430.8333 | 123 | 111
2018-11-26 20:30 | 79 | 79 |  |  | 43430.8542 | 113 | 108
2018-11-26 21:00 | 76 | 75 |  |  | 43430.875 | 106 | 102
2018-11-26 21:30 | 73 | 73 |  |  | 43430.8958 | 99 | 97
2018-11-26 22:00 | 71 | 71 |  |  | 43430.9167 | 98 | 95
2018-11-26 22:30 | 72 | 72 |  |  | 43430.9375 | 95 | 93
2018-11-26 23:00 | 68 | 68 |  |  | 43430.9583 | 89 | 88
2018-11-26 23:30 | 63 | 63 |  |  | 43430.9792 | 85 | 82
2018-11-27 | 59 | 57 |  |  | 43431 | 80 | 76
2018-11-27 00:30 | 55 | 53 |  |  | 43431.0208 | 74 | 69
2018-11-27 01:00 | 51 | 49 |  |  | 43431.0417 | 71 | 65
2018-11-27 01:30 | 50 | 47 |  |  | 43431.0625 | 69 | 63
2018-11-27 02:00 | 49 | 46 |  |  | 43431.0833 | 67 | 62
2018-11-27 02:30 | 47 | 44 |  |  | 43431.1042 | 65 | 59
2018-11-27 03:00 | 47 | 44 |  |  | 43431.125 | 63 | 57
2018-11-27 03:30 | 47 | 43 |  |  | 43431.1458 | 63 | 57
2018-11-27 04:00 | 47 | 44 |  |  | 43431.1667 | 64 | 58
2018-11-27 04:30 | 47 | 45 |  |  | 43431.1875 | 65 | 60
2018-11-27 05:00 | 50 | 48 |  |  | 43431.2083 | 68 | 62
2018-11-27 05:30 | 52 | 50 |  |  | 43431.2292 | 71 | 66
2018-11-27 06:00 | 57 | 55 |  |  | 43431.25 | 76 | 73
2018-11-27 06:30 | 60 | 57 |  |  | 43431.2708 | 81 | 80
2018-11-27 07:00 | 66 | 63 |  |  | 43431.2917 | 88 | 88
2018-11-27 07:30 | 72 | 68 |  |  | 43431.3125 | 93 | 93
2018-11-27 08:00 | 76 | 70 |  |  | 43431.3333 | 97 | 97
2018-11-27 08:30 | 79 | 73 |  |  | 43431.3542 | 104 | 103
2018-11-27 09:00 | 81 | 76 |  |  | 43431.375 | 106 | 106
2018-11-27 09:30 | 85 | 80 |  |  | 43431.3958 | 109 | 109
2018-11-27 10:00 | 81 | 76 |  |  | 43431.4167 | 106 | 106
2018-11-27 10:30 | 82 | 78 |  |  | 43431.4375 | 108 | 108
2018-11-27 11:00 | 82 | 78 |  |  | 43431.4583 | 105 | 105
2018-11-27 11:30 | 86 | 82 |  |  | 43431.4792 | 108 | 108
2018-11-27 12:00 | 88 | 84 |  |  | 43431.5 | 112 | 111
2018-11-27 12:30 | 91 | 86 |  |  | 43431.5208 | 112 | 112
2018-11-27 13:00 | 90 | 85 |  |  | 43431.5417 | 112 | 112
2018-11-27 13:30 | 82 | 76 |  |  | 43431.5625 | 101 | 101
2018-11-27 14:00 | 88 | 83 |  |  | 43431.5833 | 109 | 109
2018-11-27 14:30 | 91 | 86 |  |  | 43431.6042 | 112 | 112
2018-11-27 15:00 | 83 | 77 |  |  | 43431.625 | 103 | 103
2018-11-27 15:30 | 86 | 81 |  |  | 43431.6458 | 107 | 106
2018-11-27 16:00 | 91 | 86 |  |  | 43431.6667 | 111 | 111
2018-11-27 16:30 | 95 | 90 |  |  | 43431.6875 | 115 | 115
2018-11-27 17:00 | 98 | 94 |  |  | 43431.7083 | 118 | 118
2018-11-27 17:30 | 100 | 94 |  |  | 43431.7292 | 117 | 117
2018-11-27 18:00 | 99 | 92 |  |  | 43431.75 | 115 | 115
2018-11-27 18:30 | 100 | 90 |  |  | 43431.7708 | 113 | 111
2018-11-27 19:00 | 103 | 94 |  |  | 43431.7917 | 118 | 116
2018-11-27 19:30 | 103 | 94 |  |  | 43431.8125 | 117 | 115
2018-11-27 20:00 | 101 | 92 |  |  | 43431.8333 | 115 | 113
2018-11-27 20:30 | 99 | 91 |  |  | 43431.8542 | 112 | 112
2018-11-27 21:00 | 95 | 89 |  |  | 43431.875 | 109 | 109
2018-11-27 21:30 | 93 | 86 |  |  | 43431.8958 | 105 | 105
2018-11-27 22:00 | 91 | 83 |  |  | 43431.9167 | 103 | 102
2018-11-27 22:30 | 88 | 80 |  |  | 43431.9375 | 100 | 99
2018-11-27 23:00 | 85 | 78 |  |  | 43431.9583 | 95 | 95
2018-11-27 23:30 | 81 | 73 |  |  | 43431.9792 | 90 | 89
2018-11-28 | 75 | 66 |  |  | 43432 | 83 | 82
2018-11-28 00:30 | 72 | 62 |  |  | 43432.0208 | 77 | 77
2018-11-28 01:00 | 71 | 60 |  |  | 43432.0417 | 75 | 74
2018-11-28 01:30 | 69 | 56 |  |  | 43432.0625 | 72 | 72
2018-11-28 02:00 | 68 | 55 |  |  | 43432.0833 | 70 | 70
2018-11-28 02:30 | 67 | 54 |  |  | 43432.1042 | 69 | 68
2018-11-28 03:00 | 67 | 53 |  |  | 43432.125 | 67 | 67
2018-11-28 03:30 | 66 | 53 |  |  | 43432.1458 | 67 | 67
2018-11-28 04:00 | 66 | 52 |  |  | 43432.1667 | 67 | 67
2018-11-28 04:30 | 66 | 53 |  |  | 43432.1875 | 68 | 67
2018-11-28 05:00 | 67 | 54 |  |  | 43432.2083 | 70 | 70
2018-11-28 05:30 | 69 | 57 |  |  | 43432.2292 | 74 | 73
2018-11-28 06:00 | 69 | 60 |  |  | 43432.25 | 80 | 80
2018-11-28 06:30 | 73 | 67 |  |  | 43432.2708 | 91 | 91
2018-11-28 07:00 | 78 | 73 |  |  | 43432.2917 | 101 | 100
2018-11-28 07:30 | 84 | 80 |  |  | 43432.3125 | 111 | 111
2018-11-28 08:00 | 89 | 82 |  |  | 43432.3333 | 117 | 116
2018-11-28 08:30 | 91 | 82 |  |  | 43432.3542 | 119 | 118
2018-11-28 09:00 | 89 | 81 |  |  | 43432.375 | 118 | 117
2018-11-28 09:30 | 91 | 82 |  |  | 43432.3958 | 120 | 119
2018-11-28 10:00 | 92 | 83 |  |  | 43432.4167 | 120 | 119
2018-11-28 10:30 | 97 | 87 |  |  | 43432.4375 | 123 | 121
2018-11-28 11:00 | 102 | 93 |  |  | 43432.4583 | 129 | 127
2018-11-28 11:30 | 104 | 98 |  |  | 43432.4792 | 135 | 132
2018-11-28 12:00 | 107 | 100 |  |  | 43432.5 | 139 | 136
2018-11-28 12:30 | 116 | 111 |  |  | 43432.5208 | 145 | 143
2018-11-28 13:00 | 104 | 98 |  |  | 43432.5417 | 139 | 137
2018-11-28 13:30 | 104 | 98 |  |  | 43432.5625 | 138 | 136
2018-11-28 14:00 | 107 | 102 |  |  | 43432.5833 | 140 | 139
2018-11-28 14:30 | 106 | 102 |  |  | 43432.6042 | 141 | 139
2018-11-28 15:00 | 118 | 111 |  |  | 43432.625 | 146 | 142
2018-11-28 15:30 | 121 | 114 |  |  | 43432.6458 | 148 | 144
2018-11-28 16:00 | 117 | 111 |  |  | 43432.6667 | 150 | 147
2018-11-28 16:30 | 118 | 113 |  |  | 43432.6875 | 154 | 151
2018-11-28 17:00 | 121 | 116 |  |  | 43432.7083 | 158 | 155
2018-11-28 17:30 | 121 | 116 |  |  | 43432.7292 | 156 | 152
2018-11-28 18:00 | 116 | 109 |  |  | 43432.75 | 149 | 144
2018-11-28 18:30 | 113 | 106 |  |  | 43432.7708 | 144 | 140
2018-11-28 19:00 | 116 | 109 |  |  | 43432.7917 | 147 | 143
2018-11-28 19:30 | 115 | 107 |  |  | 43432.8125 | 146 | 141
2018-11-28 20:00 | 111 | 103 |  |  | 43432.8333 | 142 | 138
2018-11-28 20:30 | 109 | 99 |  |  | 43432.8542 | 138 | 133
2018-11-28 21:00 | 100 | 94 |  |  | 43432.875 | 125 | 124
2018-11-28 21:30 | 93 | 88 |  |  | 43432.8958 | 116 | 116
2018-11-28 22:00 | 90 | 85 |  |  | 43432.9167 | 111 | 111
2018-11-28 22:30 | 86 | 80 |  |  | 43432.9375 | 107 | 106
2018-11-28 23:00 | 81 | 75 |  |  | 43432.9583 | 99 | 98
2018-11-28 23:30 | 83 | 75 |  |  | 43432.9792 | 93 | 93
2018-11-29 | 78 | 68 |  |  | 43433 | 86 | 86
2018-11-29 00:30 | 74 | 62 |  |  | 43433.0208 | 79 | 79
2018-11-29 01:00 | 73 | 59 |  |  | 43433.0417 | 74 | 74
2018-11-29 01:30 | 72 | 57 |  |  | 43433.0625 | 72 | 72
2018-11-29 02:00 | 71 | 55 |  |  | 43433.0833 | 71 | 70
2018-11-29 02:30 | 72 | 55 |  |  | 43433.1042 | 69 | 68
2018-11-29 03:00 | 70 | 52 |  |  | 43433.125 | 68 | 67
2018-11-29 03:30 | 69 | 51 |  |  | 43433.1458 | 68 | 67
2018-11-29 04:00 | 68 | 50 |  |  | 43433.1667 | 68 | 67
2018-11-29 04:30 | 68 | 49 |  |  | 43433.1875 | 68 | 67
2018-11-29 05:00 | 68 | 49 |  |  | 43433.2083 | 70 | 69
2018-11-29 05:30 | 70 | 52 |  |  | 43433.2292 | 72 | 71
2018-11-29 06:00 | 69 | 53 |  |  | 43433.25 | 77 | 76
2018-11-29 06:30 | 72 | 60 |  |  | 43433.2708 | 87 | 87
2018-11-29 07:00 | 76 | 66 |  |  | 43433.2917 | 95 | 95
2018-11-29 07:30 | 78 | 69 |  |  | 43433.3125 | 98 | 98
2018-11-29 08:00 | 78 | 70 |  |  | 43433.3333 | 99 | 99
2018-11-29 08:30 | 75 | 68 |  |  | 43433.3542 | 98 | 98
2018-11-29 09:00 | 76 | 68 |  |  | 43433.375 | 99 | 99
2018-11-29 09:30 | 77 | 67 |  |  | 43433.3958 | 99 | 99
2018-11-29 10:00 | 74 | 68 |  |  | 43433.4167 | 101 | 101
2018-11-29 10:30 | 76 | 70 |  |  | 43433.4375 | 101 | 101
2018-11-29 11:00 | 77 | 72 |  |  | 43433.4583 | 103 | 103
2018-11-29 11:30 | 80 | 76 |  |  | 43433.4792 | 106 | 106
2018-11-29 12:00 | 84 | 79 |  |  | 43433.5 | 108 | 108
2018-11-29 12:30 | 87 | 82 |  |  | 43433.5208 | 110 | 110
2018-11-29 13:00 | 91 | 86 |  |  | 43433.5417 | 114 | 114
2018-11-29 13:30 | 97 | 91 |  |  | 43433.5625 | 120 | 119
2018-11-29 14:00 | 100 | 94 |  |  | 43433.5833 | 123 | 123
2018-11-29 14:30 | 103 | 97 |  |  | 43433.6042 | 128 | 128
2018-11-29 15:00 | 105 | 99 |  |  | 43433.625 | 129 | 129
2018-11-29 15:30 | 107 | 101 |  |  | 43433.6458 | 131 | 131
2018-11-29 16:00 | 107 | 101 |  |  | 43433.6667 | 132 | 131
2018-11-29 16:30 | 107 | 100 |  |  | 43433.6875 | 131 | 130
2018-11-29 17:00 | 107 | 100 |  |  | 43433.7083 | 130 | 129
2018-11-29 17:30 | 108 | 100 |  |  | 43433.7292 | 130 | 129
2018-11-29 18:00 | 107 | 97 |  |  | 43433.75 | 126 | 124
2018-11-29 18:30 | 104 | 94 |  |  | 43433.7708 | 123 | 120
2018-11-29 19:00 | 106 | 95 |  |  | 43433.7917 | 125 | 123
2018-11-29 19:30 | 106 | 95 |  |  | 43433.8125 | 123 | 121
2018-11-29 20:00 | 101 | 93 |  |  | 43433.8333 | 120 | 119
2018-11-29 20:30 | 101 | 91 |  |  | 43433.8542 | 118 | 117
2018-11-29 21:00 | 98 | 89 |  |  | 43433.875 | 113 | 112
2018-11-29 21:30 | 93 | 83 |  |  | 43433.8958 | 107 | 105
2018-11-29 22:00 | 89 | 79 |  |  | 43433.9167 | 102 | 102
2018-11-29 22:30 | 84 | 76 |  |  | 43433.9375 | 100 | 100
2018-11-29 23:00 | 82 | 72 |  |  | 43433.9583 | 94 | 93
2018-11-29 23:30 | 79 | 67 |  |  | 43433.9792 | 88 | 87
2018-11-30 | 74 | 59 |  |  | 43434 | 82 | 81
2018-11-30 00:30 | 73 | 56 |  |  | 43434.0208 | 76 | 76
2018-11-30 01:00 | 72 | 53 |  |  | 43434.0417 | 72 | 71
2018-11-30 01:30 | 72 | 51 |  |  | 43434.0625 | 70 | 69
2018-11-30 02:00 | 70 | 49 |  |  | 43434.0833 | 68 | 67
2018-11-30 02:30 | 69 | 49 |  |  | 43434.1042 | 68 | 67
2018-11-30 03:00 | 69 | 49 |  |  | 43434.125 | 68 | 66
2018-11-30 03:30 | 69 | 49 |  |  | 43434.1458 | 68 | 66
2018-11-30 04:00 | 68 | 47 |  |  | 43434.1667 | 67 | 65
2018-11-30 04:30 | 68 | 47 |  |  | 43434.1875 | 67 | 66
2018-11-30 05:00 | 68 | 48 |  |  | 43434.2083 | 69 | 67
2018-11-30 05:30 | 71 | 53 |  |  | 43434.2292 | 73 | 72
2018-11-30 06:00 | 71 | 54 |  |  | 43434.25 | 76 | 76
2018-11-30 06:30 | 71 | 60 |  |  | 43434.2708 | 85 | 85
2018-11-30 07:00 | 70 | 64 |  |  | 43434.2917 | 93 | 93
2018-11-30 07:30 | 65 | 63 |  |  | 43434.3125 | 97 | 96
2018-11-30 08:00 | 64 | 62 |  |  | 43434.3333 | 99 | 98
2018-11-30 08:30 | 65 | 63 |  |  | 43434.3542 | 100 | 100
2018-11-30 09:00 | 67 | 64 |  |  | 43434.375 | 100 | 100
2018-11-30 09:30 | 68 | 65 |  |  | 43434.3958 | 101 | 101
2018-11-30 10:00 | 68 | 65 |  |  | 43434.4167 | 102 | 102
2018-11-30 10:30 | 69 | 67 |  |  | 43434.4375 | 103 | 103
2018-11-30 11:00 | 71 | 69 |  |  | 43434.4583 | 106 | 105
2018-11-30 11:30 | 79 | 78 |  |  | 43434.4792 | 113 | 112
2018-11-30 12:00 | 81 | 80 |  |  | 43434.5 | 118 | 118
2018-11-30 12:30 | 81 | 79 |  |  | 43434.5208 | 117 | 117
2018-11-30 13:00 | 80 | 78 |  |  | 43434.5417 | 112 | 111
2018-11-30 13:30 | 89 | 87 |  |  | 43434.5625 | 118 | 118
2018-11-30 14:00 | 90 | 87 |  |  | 43434.5833 | 113 | 113
2018-11-30 14:30 | 93 | 92 |  |  | 43434.6042 | 118 | 118
2018-11-30 15:00 | 94 | 94 |  |  | 43434.625 | 119 | 119
2018-11-30 15:30 | 91 | 91 |  |  | 43434.6458 | 121 | 121
2018-11-30 16:00 | 96 | 93 |  |  | 43434.6667 | 129 | 127
2018-11-30 16:30 | 98 | 96 |  |  | 43434.6875 | 130 | 128
2018-11-30 17:00 | 102 | 100 |  |  | 43434.7083 | 134 | 132
2018-11-30 17:30 | 95 | 94 |  |  | 43434.7292 | 132 | 127
2018-11-30 18:00 | 81 | 81 |  |  | 43434.75 | 125 | 118
2018-11-30 18:30 | 77 | 77 |  |  | 43434.7708 | 122 | 114
2018-11-30 19:00 | 79 | 79 |  |  | 43434.7917 | 121 | 116
2018-11-30 19:30 | 79 | 79 |  |  | 43434.8125 | 122 | 115
2018-11-30 20:00 | 77 | 77 |  |  | 43434.8333 | 121 | 114
2018-11-30 20:30 | 88 | 88 |  |  | 43434.8542 | 124 | 116
2018-11-30 21:00 | 85 | 85 |  |  | 43434.875 | 118 | 112
2018-11-30 21:30 | 81 | 81 |  |  | 43434.8958 | 114 | 108
2018-11-30 22:00 | 78 | 78 |  |  | 43434.9167 | 112 | 105
2018-11-30 22:30 | 76 | 76 |  |  | 43434.9375 | 111 | 103
2018-11-30 23:00 | 74 | 73 |  |  | 43434.9583 | 107 | 98
2018-11-30 23:30 | 68 | 68 |  |  | 43434.9792 | 102 | 93
2018-12-01 | 62 | 61 |  |  | 43435 | 86 | 84
2018-12-01 00:30 | 59 | 58 |  |  | 43435.0208 | 80 | 79
2018-12-01 01:00 | 55 | 54 |  |  | 43435.0417 | 76 | 75
2018-12-01 01:30 | 53 | 53 |  |  | 43435.0625 | 73 | 72
2018-12-01 02:00 | 53 | 52 |  |  | 43435.0833 | 72 | 70
2018-12-01 02:30 | 52 | 51 |  |  | 43435.1042 | 71 | 69
2018-12-01 03:00 | 51 | 50 |  |  | 43435.125 | 70 | 68
2018-12-01 03:30 | 51 | 50 |  |  | 43435.1458 | 70 | 68
2018-12-01 04:00 | 51 | 50 |  |  | 43435.1667 | 69 | 67
2018-12-01 04:30 | 51 | 50 |  |  | 43435.1875 | 68 | 66
2018-12-01 05:00 | 50 | 49 |  |  | 43435.2083 | 67 | 65
2018-12-01 05:30 | 50 | 50 |  |  | 43435.2292 | 68 | 65
2018-12-01 06:00 | 51 | 50 |  |  | 43435.25 | 70 | 68
2018-12-01 06:30 | 52 | 51 |  |  | 43435.2708 | 72 | 70
2018-12-01 07:00 | 51 | 50 |  |  | 43435.2917 | 73 | 72
2018-12-01 07:30 | 54 | 53 |  |  | 43435.3125 | 75 | 75
2018-12-01 08:00 | 58 | 56 |  |  | 43435.3333 | 79 | 78
2018-12-01 08:30 | 61 | 59 |  |  | 43435.3542 | 83 | 82
2018-12-01 09:00 | 64 | 62 |  |  | 43435.375 | 86 | 86
2018-12-01 09:30 | 66 | 64 |  |  | 43435.3958 | 87 | 87
2018-12-01 10:00 | 68 | 67 |  |  | 43435.4167 | 89 | 89
2018-12-01 10:30 | 70 | 69 |  |  | 43435.4375 | 90 | 90
2018-12-01 11:00 | 73 | 72 |  |  | 43435.4583 | 94 | 93
2018-12-01 11:30 | 75 | 75 |  |  | 43435.4792 | 98 | 95
2018-12-01 12:00 | 76 | 76 |  |  | 43435.5 | 100 | 98
2018-12-01 12:30 | 77 | 77 |  |  | 43435.5208 | 99 | 98
2018-12-01 13:00 | 79 | 79 |  |  | 43435.5417 | 101 | 100
2018-12-01 13:30 | 82 | 82 |  |  | 43435.5625 | 106 | 103
2018-12-01 14:00 | 85 | 84 |  |  | 43435.5833 | 107 | 106
2018-12-01 14:30 | 86 | 86 |  |  | 43435.6042 | 110 | 109
2018-12-01 15:00 | 87 | 87 |  |  | 43435.625 | 110 | 110
2018-12-01 15:30 | 92 | 92 |  |  | 43435.6458 | 114 | 113
2018-12-01 16:00 | 93 | 93 |  |  | 43435.6667 | 118 | 117
2018-12-01 16:30 | 96 | 96 |  |  | 43435.6875 | 121 | 120
2018-12-01 17:00 | 99 | 99 |  |  | 43435.7083 | 125 | 124
2018-12-01 17:30 | 97 | 97 |  |  | 43435.7292 | 124 | 122
2018-12-01 18:00 | 94 | 94 |  |  | 43435.75 | 120 | 120
2018-12-01 18:30 | 93 | 93 |  |  | 43435.7708 | 119 | 119
2018-12-01 19:00 | 95 | 95 |  |  | 43435.7917 | 123 | 122
2018-12-01 19:30 | 94 | 94 |  |  | 43435.8125 | 122 | 121
2018-12-01 20:00 | 94 | 94 |  |  | 43435.8333 | 122 | 121
2018-12-01 20:30 | 92 | 91 |  |  | 43435.8542 | 119 | 118
2018-12-01 21:00 | 87 | 87 |  |  | 43435.875 | 113 | 113
2018-12-01 21:30 | 84 | 84 |  |  | 43435.8958 | 108 | 108
2018-12-01 22:00 | 82 | 82 |  |  | 43435.9167 | 107 | 107
2018-12-01 22:30 | 81 | 81 |  |  | 43435.9375 | 106 | 106
2018-12-01 23:00 | 78 | 78 |  |  | 43435.9583 | 101 | 101
2018-12-01 23:30 | 74 | 74 |  |  | 43435.9792 | 95 | 95
2018-12-02 | 68 | 68 |  |  | 43436 | 90 | 90
2018-12-02 00:30 | 63 | 63 |  |  | 43436.0208 | 83 | 83
2018-12-02 01:00 | 61 | 61 |  |  | 43436.0417 | 80 | 80
2018-12-02 01:30 | 59 | 59 |  |  | 43436.0625 | 78 | 77
2018-12-02 02:00 | 57 | 57 |  |  | 43436.0833 | 75 | 75
2018-12-02 02:30 | 57 | 57 |  |  | 43436.1042 | 73 | 73
2018-12-02 03:00 | 55 | 55 |  |  | 43436.125 | 72 | 71
2018-12-02 03:30 | 54 | 54 |  |  | 43436.1458 | 70 | 70
2018-12-02 04:00 | 52 | 52 |  |  | 43436.1667 | 70 | 70
2018-12-02 04:30 | 52 | 51 |  |  | 43436.1875 | 70 | 70
2018-12-02 05:00 | 50 | 50 |  |  | 43436.2083 | 68 | 66
2018-12-02 05:30 | 50 | 49 |  |  | 43436.2292 | 68 | 66
2018-12-02 06:00 | 49 | 49 |  |  | 43436.25 | 69 | 66
2018-12-02 06:30 | 49 | 48 |  |  | 43436.2708 | 69 | 67
2018-12-02 07:00 | 49 | 48 |  |  | 43436.2917 | 70 | 69
2018-12-02 07:30 | 51 | 50 |  |  | 43436.3125 | 73 | 72
2018-12-02 08:00 | 53 | 52 |  |  | 43436.3333 | 74 | 74
2018-12-02 08:30 | 56 | 54 |  |  | 43436.3542 | 78 | 78
2018-12-02 09:00 | 59 | 57 |  |  | 43436.375 | 81 | 81
2018-12-02 09:30 | 64 | 63 |  |  | 43436.3958 | 89 | 89
2018-12-02 10:00 | 66 | 65 |  |  | 43436.4167 | 88 | 88
2018-12-02 10:30 | 70 | 69 |  |  | 43436.4375 | 92 | 91
2018-12-02 11:00 | 72 | 72 |  |  | 43436.4583 | 99 | 96
2018-12-02 11:30 | 76 | 75 |  |  | 43436.4792 | 102 | 98
2018-12-02 12:00 | 81 | 81 |  |  | 43436.5 | 109 | 103
2018-12-02 12:30 | 86 | 85 |  |  | 43436.5208 | 125 | 112
2018-12-02 13:00 | 88 | 87 |  |  | 43436.5417 | 125 | 112
2018-12-02 13:30 | 93 | 92 |  |  | 43436.5625 | 130 | 119
2018-12-02 14:00 | 91 | 91 |  |  | 43436.5833 | 130 | 118
2018-12-02 14:30 | 96 | 95 |  |  | 43436.6042 | 132 | 121
2018-12-02 15:00 | 101 | 101 |  |  | 43436.625 | 137 | 125
2018-12-02 15:30 | 102 | 102 |  |  | 43436.6458 | 141 | 130
2018-12-02 16:00 | 98 | 98 |  |  | 43436.6667 | 144 | 131
2018-12-02 16:30 | 91 | 91 |  |  | 43436.6875 | 142 | 129
2018-12-02 17:00 | 93 | 93 |  |  | 43436.7083 | 145 | 134
2018-12-02 17:30 | 94 | 94 |  |  | 43436.7292 | 146 | 134
2018-12-02 18:00 | 93 | 93 |  |  | 43436.75 | 145 | 133
2018-12-02 18:30 | 92 | 92 |  |  | 43436.7708 | 145 | 132
2018-12-02 19:00 | 93 | 93 |  |  | 43436.7917 | 142 | 134
2018-12-02 19:30 | 93 | 93 |  |  | 43436.8125 | 143 | 135
2018-12-02 20:00 | 92 | 92 |  |  | 43436.8333 | 141 | 132
2018-12-02 20:30 | 91 | 91 |  |  | 43436.8542 | 138 | 130
2018-12-02 21:00 | 86 | 86 |  |  | 43436.875 | 132 | 125
2018-12-02 21:30 | 83 | 83 |  |  | 43436.8958 | 122 | 119
2018-12-02 22:00 | 85 | 82 |  |  | 43436.9167 | 116 | 115
2018-12-02 22:30 | 87 | 85 |  |  | 43436.9375 | 115 | 114
2018-12-02 23:00 | 83 | 81 |  |  | 43436.9583 | 108 | 107
2018-12-02 23:30 | 77 | 75 |  |  | 43436.9792 | 102 | 101
2018-12-03 | 68 | 68 |  |  | 43437 | 95 | 93
2018-12-03 00:30 | 63 | 63 |  |  | 43437.0208 | 88 | 86
2018-12-03 01:00 | 61 | 61 |  |  | 43437.0417 | 84 | 82
2018-12-03 01:30 | 59 | 59 |  |  | 43437.0625 | 80 | 79
2018-12-03 02:00 | 58 | 58 |  |  | 43437.0833 | 78 | 76
2018-12-03 02:30 | 57 | 56 |  |  | 43437.1042 | 76 | 74
2018-12-03 03:00 | 56 | 55 |  |  | 43437.125 | 76 | 74
2018-12-03 03:30 | 56 | 55 |  |  | 43437.1458 | 76 | 74
2018-12-03 04:00 | 56 | 55 |  |  | 43437.1667 | 76 | 75
2018-12-03 04:30 | 55 | 54 |  |  | 43437.1875 | 76 | 75
2018-12-03 05:00 | 57 | 56 |  |  | 43437.2083 | 78 | 77
2018-12-03 05:30 | 57 | 56 |  |  | 43437.2292 | 79 | 79
2018-12-03 06:00 | 61 | 60 |  |  | 43437.25 | 84 | 83
2018-12-03 06:30 | 67 | 66 |  |  | 43437.2708 | 95 | 94
2018-12-03 07:00 | 73 | 71 |  |  | 43437.2917 | 103 | 103
2018-12-03 07:30 | 76 | 75 |  |  | 43437.3125 | 109 | 109
2018-12-03 08:00 | 79 | 78 |  |  | 43437.3333 | 114 | 113
2018-12-03 08:30 | 82 | 80 |  |  | 43437.3542 | 116 | 115
2018-12-03 09:00 | 82 | 80 |  |  | 43437.375 | 116 | 116
2018-12-03 09:30 | 82 | 81 |  |  | 43437.3958 | 117 | 116
2018-12-03 10:00 | 82 | 81 |  |  | 43437.4167 | 117 | 116
2018-12-03 10:30 | 81 | 80 |  |  | 43437.4375 | 115 | 115
2018-12-03 11:00 | 83 | 82 |  |  | 43437.4583 | 117 | 117
2018-12-03 11:30 | 85 | 84 |  |  | 43437.4792 | 120 | 120
2018-12-03 12:00 | 86 | 86 |  |  | 43437.5 | 120 | 120
2018-12-03 12:30 | 91 | 91 |  |  | 43437.5208 | 124 | 124
2018-12-03 13:00 | 91 | 91 |  |  | 43437.5417 | 128 | 128
2018-12-03 13:30 | 91 | 91 |  |  | 43437.5625 | 126 | 126
2018-12-03 14:00 | 89 | 89 |  |  | 43437.5833 | 124 | 124
2018-12-03 14:30 | 91 | 91 |  |  | 43437.6042 | 126 | 126
2018-12-03 15:00 | 91 | 91 |  |  | 43437.625 | 129 | 129
2018-12-03 15:30 | 96 | 96 |  |  | 43437.6458 | 132 | 132
2018-12-03 16:00 | 98 | 98 |  |  | 43437.6667 | 133 | 133
2018-12-03 16:30 | 98 | 98 |  |  | 43437.6875 | 133 | 133
2018-12-03 17:00 | 100 | 100 |  |  | 43437.7083 | 135 | 135
2018-12-03 17:30 | 99 | 99 |  |  | 43437.7292 | 133 | 132
2018-12-03 18:00 | 97 | 96 |  |  | 43437.75 | 128 | 127
2018-12-03 18:30 | 94 | 94 |  |  | 43437.7708 | 123 | 123
2018-12-03 19:00 | 97 | 97 |  |  | 43437.7917 | 126 | 125
2018-12-03 19:30 | 95 | 95 |  |  | 43437.8125 | 124 | 124
2018-12-03 20:00 | 93 | 93 |  |  | 43437.8333 | 120 | 120
2018-12-03 20:30 | 91 | 91 |  |  | 43437.8542 | 117 | 117
2018-12-03 21:00 | 87 | 87 |  |  | 43437.875 | 112 | 112
2018-12-03 21:30 | 82 | 82 |  |  | 43437.8958 | 106 | 106
2018-12-03 22:00 | 79 | 79 |  |  | 43437.9167 | 103 | 103
2018-12-03 22:30 | 76 | 76 |  |  | 43437.9375 | 100 | 100
2018-12-03 23:00 | 73 | 73 |  |  | 43437.9583 | 94 | 94
2018-12-03 23:30 | 65 | 65 |  |  | 43437.9792 | 87 | 87
2018-12-04 | 58 | 58 |  |  | 43438 | 81 | 81
2018-12-04 00:30 | 55 | 55 |  |  | 43438.0208 | 75 | 75
2018-12-04 01:00 | 52 | 52 |  |  | 43438.0417 | 72 | 72
2018-12-04 01:30 | 52 | 52 |  |  | 43438.0625 | 70 | 70
2018-12-04 02:00 | 51 | 51 |  |  | 43438.0833 | 70 | 70
2018-12-04 02:30 | 51 | 51 |  |  | 43438.1042 | 69 | 69
2018-12-04 03:00 | 52 | 51 |  |  | 43438.125 | 69 | 69
2018-12-04 03:30 | 52 | 51 |  |  | 43438.1458 | 69 | 69
2018-12-04 04:00 | 51 | 51 |  |  | 43438.1667 | 68 | 68
2018-12-04 04:30 | 50 | 50 |  |  | 43438.1875 | 69 | 69
2018-12-04 05:00 | 49 | 49 |  |  | 43438.2083 | 69 | 69
2018-12-04 05:30 | 50 | 50 |  |  | 43438.2292 | 72 | 72
2018-12-04 06:00 | 54 | 54 |  |  | 43438.25 | 77 | 77
2018-12-04 06:30 | 61 | 61 |  |  | 43438.2708 | 88 | 88
2018-12-04 07:00 | 64 | 64 |  |  | 43438.2917 | 94 | 94
2018-12-04 07:30 | 67 | 66 |  |  | 43438.3125 | 100 | 100
2018-12-04 08:00 | 71 | 70 |  |  | 43438.3333 | 105 | 105
2018-12-04 08:30 | 76 | 75 |  |  | 43438.3542 | 111 | 111
2018-12-04 09:00 | 77 | 77 |  |  | 43438.375 | 113 | 113
2018-12-04 09:30 | 76 | 75 |  |  | 43438.3958 | 114 | 114
2018-12-04 10:00 | 77 | 76 |  |  | 43438.4167 | 110 | 110
2018-12-04 10:30 | 81 | 79 |  |  | 43438.4375 | 117 | 117
2018-12-04 11:00 | 79 | 78 |  |  | 43438.4583 | 112 | 112
2018-12-04 11:30 | 84 | 83 |  |  | 43438.4792 | 116 | 116
2018-12-04 12:00 | 85 | 83 |  |  | 43438.5 | 118 | 118
2018-12-04 12:30 | 82 | 80 |  |  | 43438.5208 | 116 | 116
2018-12-04 13:00 | 87 | 85 |  |  | 43438.5417 | 121 | 121
2018-12-04 13:30 | 90 | 89 |  |  | 43438.5625 | 125 | 125
2018-12-04 14:00 | 91 | 90 |  |  | 43438.5833 | 125 | 125
2018-12-04 14:30 | 94 | 93 |  |  | 43438.6042 | 128 | 128
2018-12-04 15:00 | 92 | 91 |  |  | 43438.625 | 126 | 126
2018-12-04 15:30 | 90 | 90 |  |  | 43438.6458 | 124 | 124
2018-12-04 16:00 | 91 | 90 |  |  | 43438.6667 | 124 | 124
2018-12-04 16:30 | 89 | 89 |  |  | 43438.6875 | 123 | 123
2018-12-04 17:00 | 91 | 91 |  |  | 43438.7083 | 123 | 123
2018-12-04 17:30 | 92 | 92 |  |  | 43438.7292 | 123 | 123
2018-12-04 18:00 | 90 | 90 |  |  | 43438.75 | 120 | 120
2018-12-04 18:30 | 88 | 88 |  |  | 43438.7708 | 117 | 117
2018-12-04 19:00 | 91 | 90 |  |  | 43438.7917 | 119 | 119
2018-12-04 19:30 | 89 | 89 |  |  | 43438.8125 | 117 | 117
2018-12-04 20:00 | 88 | 88 |  |  | 43438.8333 | 114 | 114
2018-12-04 20:30 | 87 | 87 |  |  | 43438.8542 | 113 | 113
2018-12-04 21:00 | 83 | 83 |  |  | 43438.875 | 108 | 108
2018-12-04 21:30 | 77 | 77 |  |  | 43438.8958 | 101 | 101
2018-12-04 22:00 | 74 | 74 |  |  | 43438.9167 | 99 | 98
2018-12-04 22:30 | 72 | 72 |  |  | 43438.9375 | 96 | 96
2018-12-04 23:00 | 67 | 67 |  |  | 43438.9583 | 89 | 89
2018-12-04 23:30 | 63 | 63 |  |  | 43438.9792 | 85 | 84
2018-12-05 | 59 | 59 |  |  | 43439 | 80 | 80
2018-12-05 00:30 | 55 | 55 |  |  | 43439.0208 | 74 | 74
2018-12-05 01:00 | 53 | 53 |  |  | 43439.0417 | 71 | 71
2018-12-05 01:30 | 53 | 53 |  |  | 43439.0625 | 70 | 69
2018-12-05 02:00 | 53 | 53 |  |  | 43439.0833 | 70 | 69
2018-12-05 02:30 | 54 | 54 |  |  | 43439.1042 | 69 | 69
2018-12-05 03:00 | 53 | 53 |  |  | 43439.125 | 68 | 67
2018-12-05 03:30 | 52 | 52 |  |  | 43439.1458 | 68 | 67
2018-12-05 04:00 | 52 | 52 |  |  | 43439.1667 | 68 | 67
2018-12-05 04:30 | 51 | 51 |  |  | 43439.1875 | 68 | 67
2018-12-05 05:00 | 52 | 52 |  |  | 43439.2083 | 69 | 69
2018-12-05 05:30 | 54 | 54 |  |  | 43439.2292 | 72 | 72
2018-12-05 06:00 | 56 | 56 |  |  | 43439.25 | 76 | 76
2018-12-05 06:30 | 60 | 60 |  |  | 43439.2708 | 84 | 84
2018-12-05 07:00 | 63 | 63 |  |  | 43439.2917 | 89 | 89
2018-12-05 07:30 | 68 | 68 |  |  | 43439.3125 | 97 | 97
2018-12-05 08:00 | 71 | 70 |  |  | 43439.3333 | 102 | 102
2018-12-05 08:30 | 73 | 73 |  |  | 43439.3542 | 102 | 102
2018-12-05 09:00 | 69 | 69 |  |  | 43439.375 | 98 | 98
2018-12-05 09:30 | 72 | 72 |  |  | 43439.3958 | 101 | 101
2018-12-05 10:00 | 76 | 75 |  |  | 43439.4167 | 106 | 106
2018-12-05 10:30 | 75 | 75 |  |  | 43439.4375 | 106 | 106
2018-12-05 11:00 | 77 | 76 |  |  | 43439.4583 | 108 | 107
2018-12-05 11:30 | 78 | 77 |  |  | 43439.4792 | 104 | 104
2018-12-05 12:00 | 75 | 74 |  |  | 43439.5 | 99 | 99
2018-12-05 12:30 | 74 | 74 |  |  | 43439.5208 | 99 | 99
2018-12-05 13:00 | 78 | 77 |  |  | 43439.5417 | 107 | 106
2018-12-05 13:30 | 80 | 80 |  |  | 43439.5625 | 107 | 107
2018-12-05 14:00 | 81 | 81 |  |  | 43439.5833 | 103 | 103
2018-12-05 14:30 | 82 | 82 |  |  | 43439.6042 | 111 | 111
2018-12-05 15:00 | 81 | 81 |  |  | 43439.625 | 110 | 110
2018-12-05 15:30 | 80 | 80 |  |  | 43439.6458 | 104 | 104
2018-12-05 16:00 | 81 | 81 |  |  | 43439.6667 | 106 | 106
2018-12-05 16:30 | 80 | 80 |  |  | 43439.6875 | 104 | 104
2018-12-05 17:00 | 80 | 80 |  |  | 43439.7083 | 106 | 106
2018-12-05 17:30 | 81 | 81 |  |  | 43439.7292 | 106 | 106
2018-12-05 18:00 | 81 | 81 |  |  | 43439.75 | 105 | 105
2018-12-05 18:30 | 82 | 82 |  |  | 43439.7708 | 103 | 103
2018-12-05 19:00 | 85 | 85 |  |  | 43439.7917 | 107 | 107
2018-12-05 19:30 | 86 | 86 |  |  | 43439.8125 | 107 | 107
2018-12-05 20:00 | 85 | 85 |  |  | 43439.8333 | 105 | 105
2018-12-05 20:30 | 82 | 82 |  |  | 43439.8542 | 104 | 104
2018-12-05 21:00 | 77 | 77 |  |  | 43439.875 | 98 | 98
2018-12-05 21:30 | 74 | 74 |  |  | 43439.8958 | 93 | 93
2018-12-05 22:00 | 70 | 70 |  |  | 43439.9167 | 90 | 90
2018-12-05 22:30 | 69 | 69 |  |  | 43439.9375 | 89 | 89
2018-12-05 23:00 | 65 | 65 |  |  | 43439.9583 | 84 | 84
2018-12-05 23:30 | 59 | 59 |  |  | 43439.9792 | 80 | 80
2018-12-06 | 54 | 54 |  |  | 43440 | 73 | 73
2018-12-06 00:30 | 52 | 52 |  |  | 43440.0208 | 68 | 68
2018-12-06 01:00 | 49 | 49 |  |  | 43440.0417 | 64 | 64
2018-12-06 01:30 | 49 | 48 |  |  | 43440.0625 | 64 | 63
2018-12-06 02:00 | 49 | 49 |  |  | 43440.0833 | 63 | 63
2018-12-06 02:30 | 50 | 50 |  |  | 43440.1042 | 63 | 63
2018-12-06 03:00 | 50 | 50 |  |  | 43440.125 | 63 | 63
2018-12-06 03:30 | 50 | 50 |  |  | 43440.1458 | 64 | 64
2018-12-06 04:00 | 51 | 50 |  |  | 43440.1667 | 64 | 64
2018-12-06 04:30 | 52 | 52 |  |  | 43440.1875 | 66 | 65
2018-12-06 05:00 | 52 | 52 |  |  | 43440.2083 | 68 | 68
2018-12-06 05:30 | 55 | 55 |  |  | 43440.2292 | 71 | 70
2018-12-06 06:00 | 59 | 59 |  |  | 43440.25 | 76 | 76
2018-12-06 06:30 | 65 | 65 |  |  | 43440.2708 | 84 | 84
2018-12-06 07:00 | 70 | 70 |  |  | 43440.2917 | 95 | 94
2018-12-06 07:30 | 69 | 68 |  |  | 43440.3125 | 99 | 99
2018-12-06 08:00 | 68 | 68 |  |  | 43440.3333 | 101 | 101
2018-12-06 08:30 | 69 | 69 |  |  | 43440.3542 | 101 | 101
2018-12-06 09:00 | 67 | 67 |  |  | 43440.375 | 100 | 100
2018-12-06 09:30 | 66 | 66 |  |  | 43440.3958 | 102 | 102
2018-12-06 10:00 | 68 | 67 |  |  | 43440.4167 | 102 | 101
2018-12-06 10:30 | 66 | 65 |  |  | 43440.4375 | 100 | 99
2018-12-06 11:00 | 65 | 64 |  |  | 43440.4583 | 95 | 95
2018-12-06 11:30 | 63 | 62 |  |  | 43440.4792 | 93 | 92
2018-12-06 12:00 | 63 | 62 |  |  | 43440.5 | 95 | 95
2018-12-06 12:30 | 71 | 70 |  |  | 43440.5208 | 99 | 99
2018-12-06 13:00 | 69 | 68 |  |  | 43440.5417 | 95 | 95
2018-12-06 13:30 | 68 | 67 |  |  | 43440.5625 | 92 | 92
2018-12-06 14:00 | 68 | 67 |  |  | 43440.5833 | 93 | 92
2018-12-06 14:30 | 71 | 70 |  |  | 43440.6042 | 96 | 96
2018-12-06 15:00 | 72 | 71 |  |  | 43440.625 | 98 | 98
2018-12-06 15:30 | 73 | 72 |  |  | 43440.6458 | 101 | 101
2018-12-06 16:00 | 75 | 75 |  |  | 43440.6667 | 104 | 104
2018-12-06 16:30 | 78 | 77 |  |  | 43440.6875 | 105 | 105
2018-12-06 17:00 | 80 | 80 |  |  | 43440.7083 | 108 | 108
2018-12-06 17:30 | 81 | 81 |  |  | 43440.7292 | 107 | 107
2018-12-06 18:00 | 80 | 79 |  |  | 43440.75 | 104 | 104
2018-12-06 18:30 | 77 | 77 |  |  | 43440.7708 | 101 | 101
2018-12-06 19:00 | 81 | 81 |  |  | 43440.7917 | 105 | 105
2018-12-06 19:30 | 84 | 84 |  |  | 43440.8125 | 107 | 107
2018-12-06 20:00 | 84 | 84 |  |  | 43440.8333 | 106 | 106
2018-12-06 20:30 | 83 | 83 |  |  | 43440.8542 | 106 | 106
2018-12-06 21:00 | 81 | 81 |  |  | 43440.875 | 102 | 102
2018-12-06 21:30 | 76 | 75 |  |  | 43440.8958 | 96 | 96
2018-12-06 22:00 | 73 | 72 |  |  | 43440.9167 | 94 | 94
2018-12-06 22:30 | 72 | 72 |  |  | 43440.9375 | 92 | 92
2018-12-06 23:00 | 69 | 69 |  |  | 43440.9583 | 88 | 88
2018-12-06 23:30 | 66 | 66 |  |  | 43440.9792 | 85 | 85
2018-12-07 | 61 | 61 |  |  | 43441 | 80 | 80
2018-12-07 00:30 | 56 | 56 |  |  | 43441.0208 | 72 | 72
2018-12-07 01:00 | 52 | 52 |  |  | 43441.0417 | 68 | 68
2018-12-07 01:30 | 49 | 48 |  |  | 43441.0625 | 65 | 65
2018-12-07 02:00 | 50 | 50 |  |  | 43441.0833 | 65 | 65
2018-12-07 02:30 | 51 | 51 |  |  | 43441.1042 | 66 | 66
2018-12-07 03:00 | 51 | 51 |  |  | 43441.125 | 66 | 65
2018-12-07 03:30 | 52 | 52 |  |  | 43441.1458 | 66 | 66
2018-12-07 04:00 | 52 | 52 |  |  | 43441.1667 | 66 | 66
2018-12-07 04:30 | 53 | 52 |  |  | 43441.1875 | 68 | 67
2018-12-07 05:00 | 54 | 54 |  |  | 43441.2083 | 71 | 69
2018-12-07 05:30 | 54 | 53 |  |  | 43441.2292 | 72 | 70
2018-12-07 06:00 | 57 | 56 |  |  | 43441.25 | 76 | 74
2018-12-07 06:30 | 61 | 59 |  |  | 43441.2708 | 82 | 81
2018-12-07 07:00 | 67 | 64 |  |  | 43441.2917 | 88 | 88
2018-12-07 07:30 | 71 | 68 |  |  | 43441.3125 | 93 | 93
2018-12-07 08:00 | 74 | 71 |  |  | 43441.3333 | 99 | 99
2018-12-07 08:30 | 75 | 72 |  |  | 43441.3542 | 101 | 101
2018-12-07 09:00 | 75 | 72 |  |  | 43441.375 | 101 | 101
2018-12-07 09:30 | 74 | 71 |  |  | 43441.3958 | 102 | 102
2018-12-07 10:00 | 72 | 69 |  |  | 43441.4167 | 99 | 99
2018-12-07 10:30 | 73 | 70 |  |  | 43441.4375 | 101 | 101
2018-12-07 11:00 | 74 | 71 |  |  | 43441.4583 | 98 | 98
2018-12-07 11:30 | 72 | 68 |  |  | 43441.4792 | 95 | 95
2018-12-07 12:00 | 72 | 68 |  |  | 43441.5 | 96 | 96
2018-12-07 12:30 | 67 | 63 |  |  | 43441.5208 | 93 | 93
2018-12-07 13:00 | 69 | 66 |  |  | 43441.5417 | 94 | 94
2018-12-07 13:30 | 73 | 69 |  |  | 43441.5625 | 101 | 100
2018-12-07 14:00 | 76 | 73 |  |  | 43441.5833 | 100 | 100
2018-12-07 14:30 | 74 | 71 |  |  | 43441.6042 | 99 | 99
2018-12-07 15:00 | 72 | 69 |  |  | 43441.625 | 100 | 100
2018-12-07 15:30 | 71 | 69 |  |  | 43441.6458 | 97 | 97
2018-12-07 16:00 | 72 | 70 |  |  | 43441.6667 | 95 | 95
2018-12-07 16:30 | 71 | 68 |  |  | 43441.6875 | 94 | 94
2018-12-07 17:00 | 71 | 70 |  |  | 43441.7083 | 97 | 96
2018-12-07 17:30 | 73 | 72 |  |  | 43441.7292 | 97 | 97
2018-12-07 18:00 | 70 | 68 |  |  | 43441.75 | 95 | 94
2018-12-07 18:30 | 68 | 67 |  |  | 43441.7708 | 94 | 93
2018-12-07 19:00 | 73 | 71 |  |  | 43441.7917 | 98 | 97
2018-12-07 19:30 | 73 | 72 |  |  | 43441.8125 | 96 | 96
2018-12-07 20:00 | 73 | 72 |  |  | 43441.8333 | 96 | 95
2018-12-07 20:30 | 74 | 73 |  |  | 43441.8542 | 96 | 95
2018-12-07 21:00 | 72 | 70 |  |  | 43441.875 | 93 | 92
2018-12-07 21:30 | 68 | 67 |  |  | 43441.8958 | 89 | 89
2018-12-07 22:00 | 68 | 66 |  |  | 43441.9167 | 89 | 89
2018-12-07 22:30 | 67 | 65 |  |  | 43441.9375 | 88 | 87
2018-12-07 23:00 | 66 | 64 |  |  | 43441.9583 | 85 | 84
2018-12-07 23:30 | 62 | 61 |  |  | 43441.9792 | 82 | 81
2018-12-08 | 58 | 57 |  |  | 43442 | 78 | 76
2018-12-08 00:30 | 55 | 54 |  |  | 43442.0208 | 73 | 71
2018-12-08 01:00 | 51 | 50 |  |  | 43442.0417 | 68 | 65
2018-12-08 01:30 | 49 | 48 |  |  | 43442.0625 | 65 | 62
2018-12-08 02:00 | 47 | 46 |  |  | 43442.0833 | 64 | 61
2018-12-08 02:30 | 47 | 46 |  |  | 43442.1042 | 64 | 60
2018-12-08 03:00 | 47 | 46 |  |  | 43442.125 | 63 | 60
2018-12-08 03:30 | 47 | 46 |  |  | 43442.1458 | 63 | 60
2018-12-08 04:00 | 47 | 46 |  |  | 43442.1667 | 63 | 60
2018-12-08 04:30 | 48 | 48 |  |  | 43442.1875 | 63 | 60
2018-12-08 05:00 | 51 | 50 |  |  | 43442.2083 | 66 | 62
2018-12-08 05:30 | 49 | 49 |  |  | 43442.2292 | 66 | 61
2018-12-08 06:00 | 50 | 49 |  |  | 43442.25 | 67 | 64
2018-12-08 06:30 | 53 | 52 |  |  | 43442.2708 | 71 | 68
2018-12-08 07:00 | 54 | 53 |  |  | 43442.2917 | 74 | 72
2018-12-08 07:30 | 54 | 53 |  |  | 43442.3125 | 76 | 73
2018-12-08 08:00 | 60 | 59 |  |  | 43442.3333 | 87 | 85
2018-12-08 08:30 | 62 | 61 |  |  | 43442.3542 | 85 | 84
2018-12-08 09:00 | 60 | 59 |  |  | 43442.375 | 85 | 84
2018-12-08 09:30 | 61 | 59 |  |  | 43442.3958 | 87 | 86
2018-12-08 10:00 | 59 | 58 |  |  | 43442.4167 | 86 | 86
2018-12-08 10:30 | 58 | 56 |  |  | 43442.4375 | 84 | 83
2018-12-08 11:00 | 56 | 54 |  |  | 43442.4583 | 77 | 76
2018-12-08 11:30 | 57 | 55 |  |  | 43442.4792 | 78 | 77
2018-12-08 12:00 | 54 | 52 |  |  | 43442.5 | 79 | 79
2018-12-08 12:30 | 57 | 55 |  |  | 43442.5208 | 83 | 83
2018-12-08 13:00 | 60 | 58 |  |  | 43442.5417 | 81 | 81
2018-12-08 13:30 | 61 | 59 |  |  | 43442.5625 | 81 | 81
2018-12-08 14:00 | 59 | 57 |  |  | 43442.5833 | 80 | 79
2018-12-08 14:30 | 58 | 56 |  |  | 43442.6042 | 79 | 78
2018-12-08 15:00 | 58 | 56 |  |  | 43442.625 | 78 | 77
2018-12-08 15:30 | 61 | 59 |  |  | 43442.6458 | 79 | 78
2018-12-08 16:00 | 59 | 57 |  |  | 43442.6667 | 78 | 78
2018-12-08 16:30 | 57 | 56 |  |  | 43442.6875 | 79 | 78
2018-12-08 17:00 | 60 | 59 |  |  | 43442.7083 | 82 | 81
2018-12-08 17:30 | 61 | 59 |  |  | 43442.7292 | 82 | 81
2018-12-08 18:00 | 60 | 59 |  |  | 43442.75 | 81 | 80
2018-12-08 18:30 | 62 | 61 |  |  | 43442.7708 | 84 | 83
2018-12-08 19:00 | 65 | 64 |  |  | 43442.7917 | 88 | 88
2018-12-08 19:30 | 66 | 65 |  |  | 43442.8125 | 90 | 89
2018-12-08 20:00 | 67 | 66 |  |  | 43442.8333 | 89 | 88
2018-12-08 20:30 | 66 | 65 |  |  | 43442.8542 | 90 | 88
2018-12-08 21:00 | 63 | 63 |  |  | 43442.875 | 86 | 84
2018-12-08 21:30 | 61 | 60 |  |  | 43442.8958 | 82 | 81
2018-12-08 22:00 | 63 | 62 |  |  | 43442.9167 | 84 | 83
2018-12-08 22:30 | 64 | 63 |  |  | 43442.9375 | 86 | 84
2018-12-08 23:00 | 62 | 61 |  |  | 43442.9583 | 83 | 81
2018-12-08 23:30 | 59 | 58 |  |  | 43442.9792 | 79 | 77
2018-12-09 | 56 | 55 |  |  | 43443 | 77 | 75
2018-12-09 00:30 | 52 | 52 |  |  | 43443.0208 | 72 | 69
2018-12-09 01:00 | 49 | 48 |  |  | 43443.0417 | 67 | 64
2018-12-09 01:30 | 46 | 46 |  |  | 43443.0625 | 66 | 62
2018-12-09 02:00 | 47 | 47 |  |  | 43443.0833 | 66 | 62
2018-12-09 02:30 | 47 | 46 |  |  | 43443.1042 | 65 | 61
2018-12-09 03:00 | 46 | 46 |  |  | 43443.125 | 64 | 60
2018-12-09 03:30 | 46 | 46 |  |  | 43443.1458 | 64 | 60
2018-12-09 04:00 | 46 | 45 |  |  | 43443.1667 | 63 | 59
2018-12-09 04:30 | 45 | 45 |  |  | 43443.1875 | 63 | 59
2018-12-09 05:00 | 44 | 44 |  |  | 43443.2083 | 62 | 59
2018-12-09 05:30 | 45 | 45 |  |  | 43443.2292 | 63 | 60
2018-12-09 06:00 | 44 | 43 |  |  | 43443.25 | 62 | 59
2018-12-09 06:30 | 43 | 43 |  |  | 43443.2708 | 63 | 60
2018-12-09 07:00 | 45 | 44 |  |  | 43443.2917 | 62 | 60
2018-12-09 07:30 | 46 | 45 |  |  | 43443.3125 | 63 | 62
2018-12-09 08:00 | 48 | 46 |  |  | 43443.3333 | 64 | 63
2018-12-09 08:30 | 50 | 48 |  |  | 43443.3542 | 69 | 68
2018-12-09 09:00 | 50 | 48 |  |  | 43443.375 | 72 | 72
2018-12-09 09:30 | 53 | 50 |  |  | 43443.3958 | 71 | 71
2018-12-09 10:00 | 50 | 48 |  |  | 43443.4167 | 68 | 68
2018-12-09 10:30 | 51 | 49 |  |  | 43443.4375 | 67 | 66
2018-12-09 11:00 | 52 | 50 |  |  | 43443.4583 | 69 | 68
2018-12-09 11:30 | 51 | 49 |  |  | 43443.4792 | 68 | 67
2018-12-09 12:00 | 54 | 51 |  |  | 43443.5 | 71 | 70
2018-12-09 12:30 | 60 | 58 |  |  | 43443.5208 | 77 | 76
2018-12-09 13:00 | 55 | 53 |  |  | 43443.5417 | 71 | 70
2018-12-09 13:30 | 52 | 50 |  |  | 43443.5625 | 70 | 69
2018-12-09 14:00 | 55 | 53 |  |  | 43443.5833 | 74 | 73
2018-12-09 14:30 | 56 | 54 |  |  | 43443.6042 | 73 | 73
2018-12-09 15:00 | 55 | 54 |  |  | 43443.625 | 71 | 71
2018-12-09 15:30 | 57 | 55 |  |  | 43443.6458 | 72 | 71
2018-12-09 16:00 | 61 | 59 |  |  | 43443.6667 | 77 | 76
2018-12-09 16:30 | 63 | 61 |  |  | 43443.6875 | 80 | 80
2018-12-09 17:00 | 62 | 61 |  |  | 43443.7083 | 81 | 80
2018-12-09 17:30 | 64 | 63 |  |  | 43443.7292 | 83 | 82
2018-12-09 18:00 | 65 | 64 |  |  | 43443.75 | 85 | 84
2018-12-09 18:30 | 66 | 65 |  |  | 43443.7708 | 87 | 86
2018-12-09 19:00 | 69 | 68 |  |  | 43443.7917 | 92 | 90
2018-12-09 19:30 | 70 | 70 |  |  | 43443.8125 | 97 | 94
2018-12-09 20:00 | 69 | 69 |  |  | 43443.8333 | 96 | 92
2018-12-09 20:30 | 68 | 68 |  |  | 43443.8542 | 97 | 93
2018-12-09 21:00 | 65 | 65 |  |  | 43443.875 | 91 | 88
2018-12-09 21:30 | 64 | 63 |  |  | 43443.8958 | 87 | 86
2018-12-09 22:00 | 63 | 62 |  |  | 43443.9167 | 86 | 85
2018-12-09 22:30 | 63 | 62 |  |  | 43443.9375 | 86 | 86
2018-12-09 23:00 | 62 | 61 |  |  | 43443.9583 | 83 | 82
2018-12-09 23:30 | 58 | 57 |  |  | 43443.9792 | 79 | 78
2018-12-10 | 53 | 52 |  |  | 43444 | 74 | 73
2018-12-10 00:30 | 50 | 49 |  |  | 43444.0208 | 69 | 67
2018-12-10 01:00 | 47 | 46 |  |  | 43444.0417 | 66 | 64
2018-12-10 01:30 | 44 | 44 |  |  | 43444.0625 | 63 | 60
2018-12-10 02:00 | 44 | 44 |  |  | 43444.0833 | 63 | 60
2018-12-10 02:30 | 46 | 45 |  |  | 43444.1042 | 64 | 61
2018-12-10 03:00 | 46 | 45 |  |  | 43444.125 | 65 | 62
2018-12-10 03:30 | 46 | 46 |  |  | 43444.1458 | 65 | 62
2018-12-10 04:00 | 46 | 46 |  |  | 43444.1667 | 65 | 62
2018-12-10 04:30 | 47 | 46 |  |  | 43444.1875 | 65 | 62
2018-12-10 05:00 | 47 | 47 |  |  | 43444.2083 | 66 | 64
2018-12-10 05:30 | 50 | 50 |  |  | 43444.2292 | 70 | 67
2018-12-10 06:00 | 53 | 52 |  |  | 43444.25 | 73 | 71
2018-12-10 06:30 | 60 | 58 |  |  | 43444.2708 | 82 | 81
2018-12-10 07:00 | 62 | 60 |  |  | 43444.2917 | 87 | 87
2018-12-10 07:30 | 67 | 64 |  |  | 43444.3125 | 94 | 93
2018-12-10 08:00 | 71 | 68 |  |  | 43444.3333 | 101 | 100
2018-12-10 08:30 | 75 | 71 |  |  | 43444.3542 | 103 | 103
2018-12-10 09:00 | 76 | 72 |  |  | 43444.375 | 103 | 103
2018-12-10 09:30 | 76 | 72 |  |  | 43444.3958 | 101 | 101
2018-12-10 10:00 | 75 | 69 |  |  | 43444.4167 | 102 | 102
2018-12-10 10:30 | 74 | 73 |  |  | 43444.4375 | 103 | 103
2018-12-10 11:00 | 72 | 71 |  |  | 43444.4583 | 101 | 101
2018-12-10 11:30 | 73 | 72 |  |  | 43444.4792 | 102 | 102
2018-12-10 12:00 | 73 | 73 |  |  | 43444.5 | 102 | 101
2018-12-10 12:30 | 73 | 73 |  |  | 43444.5208 | 104 | 103
2018-12-10 13:00 | 73 | 73 |  |  | 43444.5417 | 102 | 102
2018-12-10 13:30 | 76 | 75 |  |  | 43444.5625 | 102 | 102
2018-12-10 14:00 | 78 | 78 |  |  | 43444.5833 | 105 | 105
2018-12-10 14:30 | 81 | 81 |  |  | 43444.6042 | 113 | 112
2018-12-10 15:00 | 79 | 79 |  |  | 43444.625 | 110 | 110
2018-12-10 15:30 | 86 | 86 |  |  | 43444.6458 | 116 | 116
2018-12-10 16:00 | 89 | 89 |  |  | 43444.6667 | 122 | 121
2018-12-10 16:30 | 89 | 89 |  |  | 43444.6875 | 118 | 117
2018-12-10 17:00 | 90 | 90 |  |  | 43444.7083 | 120 | 118
2018-12-10 17:30 | 91 | 91 |  |  | 43444.7292 | 120 | 118
2018-12-10 18:00 | 88 | 88 |  |  | 43444.75 | 116 | 115
2018-12-10 18:30 | 87 | 87 |  |  | 43444.7708 | 113 | 112
2018-12-10 19:00 | 90 | 90 |  |  | 43444.7917 | 116 | 115
2018-12-10 19:30 | 90 | 90 |  |  | 43444.8125 | 115 | 114
2018-12-10 20:00 | 88 | 88 |  |  | 43444.8333 | 114 | 112
2018-12-10 20:30 | 86 | 86 |  |  | 43444.8542 | 112 | 110
2018-12-10 21:00 | 81 | 81 |  |  | 43444.875 | 107 | 106
2018-12-10 21:30 | 77 | 77 |  |  | 43444.8958 | 102 | 100
2018-12-10 22:00 | 75 | 75 |  |  | 43444.9167 | 98 | 98
2018-12-10 22:30 | 72 | 72 |  |  | 43444.9375 | 95 | 95
2018-12-10 23:00 | 68 | 68 |  |  | 43444.9583 | 90 | 90
2018-12-10 23:30 | 64 | 64 |  |  | 43444.9792 | 85 | 85
2018-12-11 | 58 | 58 |  |  | 43445 | 79 | 79
2018-12-11 00:30 | 54 | 54 |  |  | 43445.0208 | 73 | 73
2018-12-11 01:00 | 51 | 51 |  |  | 43445.0417 | 69 | 68
2018-12-11 01:30 | 49 | 49 |  |  | 43445.0625 | 67 | 67
2018-12-11 02:00 | 50 | 49 |  |  | 43445.0833 | 67 | 67
2018-12-11 02:30 | 48 | 48 |  |  | 43445.1042 | 66 | 66
2018-12-11 03:00 | 47 | 47 |  |  | 43445.125 | 65 | 65
2018-12-11 03:30 | 47 | 47 |  |  | 43445.1458 | 65 | 65
2018-12-11 04:00 | 46 | 45 |  |  | 43445.1667 | 65 | 64
2018-12-11 04:30 | 45 | 45 |  |  | 43445.1875 | 64 | 64
2018-12-11 05:00 | 48 | 48 |  |  | 43445.2083 | 67 | 67
2018-12-11 05:30 | 51 | 51 |  |  | 43445.2292 | 71 | 71
2018-12-11 06:00 | 53 | 53 |  |  | 43445.25 | 75 | 75
2018-12-11 06:30 | 57 | 57 |  |  | 43445.2708 | 82 | 82
2018-12-11 07:00 | 60 | 60 |  |  | 43445.2917 | 89 | 89
2018-12-11 07:30 | 64 | 63 |  |  | 43445.3125 | 98 | 97
2018-12-11 08:00 | 68 | 67 |  |  | 43445.3333 | 103 | 103
2018-12-11 08:30 | 68 | 68 |  |  | 43445.3542 | 104 | 104
2018-12-11 09:00 | 68 | 68 |  |  | 43445.375 | 105 | 105
2018-12-11 09:30 | 70 | 70 |  |  | 43445.3958 | 104 | 104
2018-12-11 10:00 | 70 | 70 |  |  | 43445.4167 | 105 | 105
2018-12-11 10:30 | 69 | 69 |  |  | 43445.4375 | 103 | 103
2018-12-11 11:00 | 70 | 69 |  |  | 43445.4583 | 102 | 102
2018-12-11 11:30 | 72 | 72 |  |  | 43445.4792 | 105 | 105
2018-12-11 12:00 | 73 | 73 |  |  | 43445.5 | 105 | 105
2018-12-11 12:30 | 77 | 77 |  |  | 43445.5208 | 109 | 109
2018-12-11 13:00 | 76 | 76 |  |  | 43445.5417 | 111 | 111
2018-12-11 13:30 | 78 | 77 |  |  | 43445.5625 | 118 | 113
2018-12-11 14:00 | 79 | 78 |  |  | 43445.5833 | 119 | 114
2018-12-11 14:30 | 83 | 82 |  |  | 43445.6042 | 123 | 119
2018-12-11 15:00 | 80 | 79 |  |  | 43445.625 | 121 | 116
2018-12-11 15:30 | 80 | 79 |  |  | 43445.6458 | 121 | 116
2018-12-11 16:00 | 85 | 83 |  |  | 43445.6667 | 126 | 121
2018-12-11 16:30 | 94 | 93 |  |  | 43445.6875 | 131 | 126
2018-12-11 17:00 | 94 | 93 |  |  | 43445.7083 | 131 | 126
2018-12-11 17:30 | 91 | 89 |  |  | 43445.7292 | 127 | 121
2018-12-11 18:00 | 92 | 90 |  |  | 43445.75 | 126 | 119
2018-12-11 18:30 | 89 | 88 |  |  | 43445.7708 | 124 | 115
2018-12-11 19:00 | 91 | 90 |  |  | 43445.7917 | 128 | 118
2018-12-11 19:30 | 91 | 91 |  |  | 43445.8125 | 126 | 118
2018-12-11 20:00 | 90 | 90 |  |  | 43445.8333 | 120 | 116
2018-12-11 20:30 | 90 | 87 |  |  | 43445.8542 | 112 | 112
2018-12-11 21:00 | 86 | 83 |  |  | 43445.875 | 106 | 106
2018-12-11 21:30 | 82 | 80 |  |  | 43445.8958 | 101 | 101
2018-12-11 22:00 | 79 | 77 |  |  | 43445.9167 | 99 | 98
2018-12-11 22:30 | 76 | 73 |  |  | 43445.9375 | 96 | 96
2018-12-11 23:00 | 72 | 70 |  |  | 43445.9583 | 91 | 91
2018-12-11 23:30 | 69 | 67 |  |  | 43445.9792 | 87 | 86
2018-12-12 | 63 | 60 |  |  | 43446 | 81 | 81
2018-12-12 00:30 | 58 | 55 |  |  | 43446.0208 | 74 | 73
2018-12-12 01:00 | 53 | 51 |  |  | 43446.0417 | 69 | 68
2018-12-12 01:30 | 50 | 48 |  |  | 43446.0625 | 65 | 64
2018-12-12 02:00 | 49 | 46 |  |  | 43446.0833 | 64 | 63
2018-12-12 02:30 | 48 | 46 |  |  | 43446.1042 | 63 | 62
2018-12-12 03:00 | 48 | 45 |  |  | 43446.125 | 63 | 62
2018-12-12 03:30 | 46 | 43 |  |  | 43446.1458 | 63 | 62
2018-12-12 04:00 | 46 | 43 |  |  | 43446.1667 | 63 | 62
2018-12-12 04:30 | 49 | 46 |  |  | 43446.1875 | 64 | 63
2018-12-12 05:00 | 52 | 49 |  |  | 43446.2083 | 68 | 67
2018-12-12 05:30 | 54 | 51 |  |  | 43446.2292 | 72 | 71
2018-12-12 06:00 | 58 | 55 |  |  | 43446.25 | 77 | 76
2018-12-12 06:30 | 63 | 60 |  |  | 43446.2708 | 86 | 85
2018-12-12 07:00 | 62 | 62 |  |  | 43446.2917 | 97 | 92
2018-12-12 07:30 | 66 | 65 |  |  | 43446.3125 | 103 | 99
2018-12-12 08:00 | 70 | 69 |  |  | 43446.3333 | 108 | 104
2018-12-12 08:30 | 72 | 71 |  |  | 43446.3542 | 111 | 106
2018-12-12 09:00 | 72 | 71 |  |  | 43446.375 | 110 | 106
2018-12-12 09:30 | 68 | 68 |  |  | 43446.3958 | 107 | 103
2018-12-12 10:00 | 68 | 67 |  |  | 43446.4167 | 106 | 101
2018-12-12 10:30 | 67 | 66 |  |  | 43446.4375 | 106 | 101
2018-12-12 11:00 | 70 | 69 |  |  | 43446.4583 | 106 | 102
2018-12-12 11:30 | 69 | 68 |  |  | 43446.4792 | 105 | 101
2018-12-12 12:00 | 69 | 68 |  |  | 43446.5 | 103 | 100
2018-12-12 12:30 | 69 | 68 |  |  | 43446.5208 | 104 | 100
2018-12-12 13:00 | 69 | 68 |  |  | 43446.5417 | 106 | 101
2018-12-12 13:30 | 71 | 71 |  |  | 43446.5625 | 107 | 102
2018-12-12 14:00 | 71 | 71 |  |  | 43446.5833 | 107 | 102
2018-12-12 14:30 | 72 | 69 |  |  | 43446.6042 | 102 | 102
2018-12-12 15:00 | 73 | 70 |  |  | 43446.625 | 104 | 104
2018-12-12 15:30 | 75 | 72 |  |  | 43446.6458 | 107 | 107
2018-12-12 16:00 | 80 | 78 |  |  | 43446.6667 | 112 | 112
2018-12-12 16:30 | 88 | 87 |  |  | 43446.6875 | 118 | 118
2018-12-12 17:00 | 89 | 88 |  |  | 43446.7083 | 120 | 119
2018-12-12 17:30 | 91 | 90 |  |  | 43446.7292 | 120 | 119
2018-12-12 18:00 | 90 | 89 |  |  | 43446.75 | 116 | 115
2018-12-12 18:30 | 87 | 85 |  |  | 43446.7708 | 111 | 111
2018-12-12 19:00 | 89 | 87 |  |  | 43446.7917 | 114 | 114
2018-12-12 19:30 | 90 | 88 |  |  | 43446.8125 | 114 | 114
2018-12-12 20:00 | 91 | 89 |  |  | 43446.8333 | 113 | 113
2018-12-12 20:30 | 91 | 89 |  |  | 43446.8542 | 113 | 113
2018-12-12 21:00 | 87 | 86 |  |  | 43446.875 | 108 | 107
2018-12-12 21:30 | 83 | 81 |  |  | 43446.8958 | 103 | 102
2018-12-12 22:00 | 79 | 78 |  |  | 43446.9167 | 99 | 99
2018-12-12 22:30 | 75 | 73 |  |  | 43446.9375 | 96 | 95
2018-12-12 23:00 | 72 | 71 |  |  | 43446.9583 | 91 | 91
2018-12-12 23:30 | 70 | 68 |  |  | 43446.9792 | 88 | 88
2018-12-13 | 63 | 62 |  |  | 43447 | 82 | 81
2018-12-13 00:30 | 58 | 57 |  |  | 43447.0208 | 75 | 75
2018-12-13 01:00 | 53 | 52 |  |  | 43447.0417 | 69 | 68
2018-12-13 01:30 | 51 | 50 |  |  | 43447.0625 | 68 | 67
2018-12-13 02:00 | 51 | 50 |  |  | 43447.0833 | 68 | 67
2018-12-13 02:30 | 50 | 49 |  |  | 43447.1042 | 66 | 64
2018-12-13 03:00 | 50 | 49 |  |  | 43447.125 | 66 | 65
2018-12-13 03:30 | 50 | 49 |  |  | 43447.1458 | 67 | 65
2018-12-13 04:00 | 50 | 49 |  |  | 43447.1667 | 66 | 64
2018-12-13 04:30 | 51 | 50 |  |  | 43447.1875 | 66 | 65
2018-12-13 05:00 | 52 | 51 |  |  | 43447.2083 | 69 | 67
2018-12-13 05:30 | 55 | 54 |  |  | 43447.2292 | 72 | 71
2018-12-13 06:00 | 58 | 57 |  |  | 43447.25 | 76 | 76
2018-12-13 06:30 | 65 | 62 |  |  | 43447.2708 | 86 | 86
2018-12-13 07:00 | 66 | 63 |  |  | 43447.2917 | 92 | 92
2018-12-13 07:30 | 68 | 65 |  |  | 43447.3125 | 96 | 96
2018-12-13 08:00 | 68 | 65 |  |  | 43447.3333 | 98 | 98
2018-12-13 08:30 | 70 | 67 |  |  | 43447.3542 | 101 | 101
2018-12-13 09:00 | 69 | 67 |  |  | 43447.375 | 100 | 100
2018-12-13 09:30 | 70 | 68 |  |  | 43447.3958 | 102 | 101
2018-12-13 10:00 | 74 | 70 |  |  | 43447.4167 | 104 | 104
2018-12-13 10:30 | 76 | 72 |  |  | 43447.4375 | 105 | 105
2018-12-13 11:00 | 76 | 71 |  |  | 43447.4583 | 103 | 103
2018-12-13 11:30 | 72 | 67 |  |  | 43447.4792 | 101 | 101
2018-12-13 12:00 | 76 | 70 |  |  | 43447.5 | 102 | 102
2018-12-13 12:30 | 76 | 73 |  |  | 43447.5208 | 107 | 106
2018-12-13 13:00 | 78 | 77 |  |  | 43447.5417 | 109 | 109
2018-12-13 13:30 | 81 | 80 |  |  | 43447.5625 | 110 | 110
2018-12-13 14:00 | 85 | 84 |  |  | 43447.5833 | 114 | 114
2018-12-13 14:30 | 88 | 87 |  |  | 43447.6042 | 119 | 119
2018-12-13 15:00 | 86 | 85 |  |  | 43447.625 | 113 | 113
2018-12-13 15:30 | 87 | 86 |  |  | 43447.6458 | 114 | 114
2018-12-13 16:00 | 90 | 89 |  |  | 43447.6667 | 119 | 119
2018-12-13 16:30 | 93 | 93 |  |  | 43447.6875 | 122 | 122
2018-12-13 17:00 | 96 | 96 |  |  | 43447.7083 | 124 | 124
2018-12-13 17:30 | 93 | 93 |  |  | 43447.7292 | 121 | 121
2018-12-13 18:00 | 93 | 93 |  |  | 43447.75 | 119 | 119
2018-12-13 18:30 | 92 | 92 |  |  | 43447.7708 | 117 | 117
2018-12-13 19:00 | 95 | 95 |  |  | 43447.7917 | 120 | 120
2018-12-13 19:30 | 96 | 95 |  |  | 43447.8125 | 120 | 120
2018-12-13 20:00 | 95 | 95 |  |  | 43447.8333 | 118 | 118
2018-12-13 20:30 | 95 | 94 |  |  | 43447.8542 | 116 | 116
2018-12-13 21:00 | 90 | 90 |  |  | 43447.875 | 112 | 112
2018-12-13 21:30 | 84 | 84 |  |  | 43447.8958 | 105 | 105
2018-12-13 22:00 | 82 | 82 |  |  | 43447.9167 | 102 | 102
2018-12-13 22:30 | 81 | 80 |  |  | 43447.9375 | 100 | 100
2018-12-13 23:00 | 78 | 78 |  |  | 43447.9583 | 97 | 97
2018-12-13 23:30 | 73 | 73 |  |  | 43447.9792 | 92 | 92
2018-12-14 | 66 | 65 |  |  | 43448 | 85 | 84
2018-12-14 00:30 | 62 | 62 |  |  | 43448.0208 | 79 | 79
2018-12-14 01:00 | 60 | 60 |  |  | 43448.0417 | 76 | 76
2018-12-14 01:30 | 60 | 60 |  |  | 43448.0625 | 75 | 75
2018-12-14 02:00 | 60 | 60 |  |  | 43448.0833 | 74 | 74
2018-12-14 02:30 | 58 | 58 |  |  | 43448.1042 | 73 | 73
2018-12-14 03:00 | 58 | 58 |  |  | 43448.125 | 72 | 72
2018-12-14 03:30 | 58 | 58 |  |  | 43448.1458 | 74 | 74
2018-12-14 04:00 | 57 | 57 |  |  | 43448.1667 | 72 | 72
2018-12-14 04:30 | 55 | 55 |  |  | 43448.1875 | 72 | 72
2018-12-14 05:00 | 58 | 58 |  |  | 43448.2083 | 74 | 74
2018-12-14 05:30 | 59 | 59 |  |  | 43448.2292 | 77 | 77
2018-12-14 06:00 | 61 | 61 |  |  | 43448.25 | 80 | 80
2018-12-14 06:30 | 65 | 65 |  |  | 43448.2708 | 89 | 89
2018-12-14 07:00 | 74 | 74 |  |  | 43448.2917 | 100 | 100
2018-12-14 07:30 | 82 | 81 |  |  | 43448.3125 | 110 | 110
2018-12-14 08:00 | 84 | 84 |  |  | 43448.3333 | 115 | 115
2018-12-14 08:30 | 87 | 87 |  |  | 43448.3542 | 119 | 119
2018-12-14 09:00 | 86 | 86 |  |  | 43448.375 | 119 | 119
2018-12-14 09:30 | 82 | 82 |  |  | 43448.3958 | 114 | 114
2018-12-14 10:00 | 81 | 81 |  |  | 43448.4167 | 112 | 112
2018-12-14 10:30 | 79 | 79 |  |  | 43448.4375 | 107 | 107
2018-12-14 11:00 | 75 | 74 |  |  | 43448.4583 | 105 | 105
2018-12-14 11:30 | 73 | 73 |  |  | 43448.4792 | 102 | 102
2018-12-14 12:00 | 72 | 72 |  |  | 43448.5 | 102 | 102
2018-12-14 12:30 | 75 | 75 |  |  | 43448.5208 | 106 | 105
2018-12-14 13:00 | 78 | 78 |  |  | 43448.5417 | 108 | 108
2018-12-14 13:30 | 87 | 86 |  |  | 43448.5625 | 118 | 118
2018-12-14 14:00 | 91 | 90 |  |  | 43448.5833 | 119 | 119
2018-12-14 14:30 | 86 | 85 |  |  | 43448.6042 | 110 | 110
2018-12-14 15:00 | 84 | 84 |  |  | 43448.625 | 105 | 105
2018-12-14 15:30 | 84 | 84 |  |  | 43448.6458 | 105 | 105
2018-12-14 16:00 | 87 | 87 |  |  | 43448.6667 | 109 | 109
2018-12-14 16:30 | 84 | 83 |  |  | 43448.6875 | 109 | 109
2018-12-14 17:00 | 83 | 82 |  |  | 43448.7083 | 108 | 108
2018-12-14 17:30 | 83 | 83 |  |  | 43448.7292 | 105 | 105
2018-12-14 18:00 | 87 | 86 |  |  | 43448.75 | 106 | 105
2018-12-14 18:30 | 86 | 85 |  |  | 43448.7708 | 103 | 102
2018-12-14 19:00 | 87 | 86 |  |  | 43448.7917 | 105 | 104
2018-12-14 19:30 | 87 | 86 |  |  | 43448.8125 | 104 | 103
2018-12-14 20:00 | 86 | 85 |  |  | 43448.8333 | 103 | 102
2018-12-14 20:30 | 86 | 84 |  |  | 43448.8542 | 102 | 101
2018-12-14 21:00 | 83 | 81 |  |  | 43448.875 | 97 | 96
2018-12-14 21:30 | 78 | 76 |  |  | 43448.8958 | 93 | 92
2018-12-14 22:00 | 74 | 73 |  |  | 43448.9167 | 90 | 90
2018-12-14 22:30 | 71 | 69 |  |  | 43448.9375 | 87 | 87
2018-12-14 23:00 | 68 | 67 |  |  | 43448.9583 | 83 | 82
2018-12-14 23:30 | 63 | 62 |  |  | 43448.9792 | 77 | 77
2018-12-15 | 58 | 56 |  |  | 43449 | 72 | 72
2018-12-15 00:30 | 54 | 52 |  |  | 43449.0208 | 66 | 66
2018-12-15 01:00 | 50 | 49 |  |  | 43449.0417 | 63 | 63
2018-12-15 01:30 | 48 | 48 |  |  | 43449.0625 | 62 | 61
2018-12-15 02:00 | 47 | 46 |  |  | 43449.0833 | 59 | 59
2018-12-15 02:30 | 44 | 44 |  |  | 43449.1042 | 56 | 56
2018-12-15 03:00 | 43 | 43 |  |  | 43449.125 | 56 | 56
2018-12-15 03:30 | 42 | 42 |  |  | 43449.1458 | 54 | 54
2018-12-15 04:00 | 41 | 41 |  |  | 43449.1667 | 54 | 54
2018-12-15 04:30 | 42 | 42 |  |  | 43449.1875 | 54 | 54
2018-12-15 05:00 | 44 | 44 |  |  | 43449.2083 | 57 | 56
2018-12-15 05:30 | 44 | 44 |  |  | 43449.2292 | 56 | 56
2018-12-15 06:00 | 44 | 44 |  |  | 43449.25 | 58 | 58
2018-12-15 06:30 | 44 | 44 |  |  | 43449.2708 | 60 | 60
2018-12-15 07:00 | 45 | 45 |  |  | 43449.2917 | 61 | 60
2018-12-15 07:30 | 48 | 47 |  |  | 43449.3125 | 64 | 63
2018-12-15 08:00 | 51 | 51 |  |  | 43449.3333 | 68 | 67
2018-12-15 08:30 | 53 | 52 |  |  | 43449.3542 | 71 | 70
2018-12-15 09:00 | 52 | 51 |  |  | 43449.375 | 70 | 69
2018-12-15 09:30 | 51 | 50 |  |  | 43449.3958 | 70 | 69
2018-12-15 10:00 | 52 | 51 |  |  | 43449.4167 | 73 | 72
2018-12-15 10:30 | 55 | 55 |  |  | 43449.4375 | 75 | 73
2018-12-15 11:00 | 56 | 55 |  |  | 43449.4583 | 74 | 73
2018-12-15 11:30 | 64 | 63 |  |  | 43449.4792 | 77 | 77
2018-12-15 12:00 | 66 | 65 |  |  | 43449.5 | 77 | 76
2018-12-15 12:30 | 63 | 62 |  |  | 43449.5208 | 76 | 75
2018-12-15 13:00 | 61 | 60 |  |  | 43449.5417 | 78 | 77
2018-12-15 13:30 | 61 | 60 |  |  | 43449.5625 | 78 | 77
2018-12-15 14:00 | 61 | 60 |  |  | 43449.5833 | 79 | 78
2018-12-15 14:30 | 62 | 62 |  |  | 43449.6042 | 81 | 80
2018-12-15 15:00 | 66 | 66 |  |  | 43449.625 | 81 | 81
2018-12-15 15:30 | 65 | 64 |  |  | 43449.6458 | 79 | 79
2018-12-15 16:00 | 66 | 66 |  |  | 43449.6667 | 81 | 81
2018-12-15 16:30 | 69 | 69 |  |  | 43449.6875 | 85 | 85
2018-12-15 17:00 | 73 | 73 |  |  | 43449.7083 | 89 | 89
2018-12-15 17:30 | 73 | 73 |  |  | 43449.7292 | 89 | 89
2018-12-15 18:00 | 74 | 74 |  |  | 43449.75 | 89 | 89
2018-12-15 18:30 | 74 | 74 |  |  | 43449.7708 | 89 | 89
2018-12-15 19:00 | 76 | 76 |  |  | 43449.7917 | 92 | 91
2018-12-15 19:30 | 75 | 75 |  |  | 43449.8125 | 91 | 91
2018-12-15 20:00 | 74 | 74 |  |  | 43449.8333 | 91 | 90
2018-12-15 20:30 | 71 | 71 |  |  | 43449.8542 | 88 | 88
2018-12-15 21:00 | 67 | 67 |  |  | 43449.875 | 85 | 84
2018-12-15 21:30 | 65 | 65 |  |  | 43449.8958 | 82 | 81
2018-12-15 22:00 | 63 | 63 |  |  | 43449.9167 | 80 | 80
2018-12-15 22:30 | 64 | 64 |  |  | 43449.9375 | 81 | 80
2018-12-15 23:00 | 63 | 63 |  |  | 43449.9583 | 77 | 77
2018-12-15 23:30 | 59 | 58 |  |  | 43449.9792 | 74 | 74
2018-12-16 | 54 | 54 |  |  | 43450 | 69 | 69
2018-12-16 00:30 | 48 | 48 |  |  | 43450.0208 | 63 | 63
2018-12-16 01:00 | 45 | 45 |  |  | 43450.0417 | 58 | 58
2018-12-16 01:30 | 43 | 43 |  |  | 43450.0625 | 57 | 57
2018-12-16 02:00 | 43 | 43 |  |  | 43450.0833 | 56 | 56
2018-12-16 02:30 | 42 | 42 |  |  | 43450.1042 | 54 | 54
2018-12-16 03:00 | 42 | 42 |  |  | 43450.125 | 54 | 54
2018-12-16 03:30 | 41 | 41 |  |  | 43450.1458 | 54 | 54
2018-12-16 04:00 | 42 | 42 |  |  | 43450.1667 | 53 | 53
2018-12-16 04:30 | 42 | 42 |  |  | 43450.1875 | 55 | 55
2018-12-16 05:00 | 42 | 42 |  |  | 43450.2083 | 56 | 56
2018-12-16 05:30 | 43 | 43 |  |  | 43450.2292 | 57 | 57
2018-12-16 06:00 | 43 | 42 |  |  | 43450.25 | 57 | 57
2018-12-16 06:30 | 42 | 42 |  |  | 43450.2708 | 58 | 58
2018-12-16 07:00 | 43 | 43 |  |  | 43450.2917 | 60 | 60
2018-12-16 07:30 | 47 | 47 |  |  | 43450.3125 | 64 | 64
2018-12-16 08:00 | 51 | 50 |  |  | 43450.3333 | 68 | 67
2018-12-16 08:30 | 54 | 54 |  |  | 43450.3542 | 73 | 72
2018-12-16 09:00 | 57 | 56 |  |  | 43450.375 | 76 | 75
2018-12-16 09:30 | 62 | 61 |  |  | 43450.3958 | 80 | 80
2018-12-16 10:00 | 65 | 64 |  |  | 43450.4167 | 83 | 83
2018-12-16 10:30 | 62 | 61 |  |  | 43450.4375 | 80 | 80
2018-12-16 11:00 | 60 | 60 |  |  | 43450.4583 | 78 | 78
2018-12-16 11:30 | 60 | 59 |  |  | 43450.4792 | 78 | 78
2018-12-16 12:00 | 58 | 57 |  |  | 43450.5 | 75 | 75
2018-12-16 12:30 | 56 | 56 |  |  | 43450.5208 | 75 | 75
2018-12-16 13:00 | 56 | 56 |  |  | 43450.5417 | 74 | 74
2018-12-16 13:30 | 57 | 56 |  |  | 43450.5625 | 74 | 73
2018-12-16 14:00 | 55 | 55 |  |  | 43450.5833 | 71 | 71
2018-12-16 14:30 | 57 | 57 |  |  | 43450.6042 | 72 | 72
2018-12-16 15:00 | 56 | 56 |  |  | 43450.625 | 72 | 72
2018-12-16 15:30 | 56 | 55 |  |  | 43450.6458 | 72 | 72
2018-12-16 16:00 | 57 | 57 |  |  | 43450.6667 | 75 | 75
2018-12-16 16:30 | 60 | 59 |  |  | 43450.6875 | 77 | 77
2018-12-16 17:00 | 60 | 60 |  |  | 43450.7083 | 78 | 78
2018-12-16 17:30 | 61 | 61 |  |  | 43450.7292 | 79 | 79
2018-12-16 18:00 | 61 | 61 |  |  | 43450.75 | 80 | 80
2018-12-16 18:30 | 62 | 62 |  |  | 43450.7708 | 80 | 80
2018-12-16 19:00 | 64 | 64 |  |  | 43450.7917 | 82 | 82
2018-12-16 19:30 | 63 | 63 |  |  | 43450.8125 | 81 | 81
2018-12-16 20:00 | 63 | 63 |  |  | 43450.8333 | 80 | 80
2018-12-16 20:30 | 62 | 62 |  |  | 43450.8542 | 79 | 79
2018-12-16 21:00 | 59 | 58 |  |  | 43450.875 | 75 | 75
2018-12-16 21:30 | 56 | 56 |  |  | 43450.8958 | 72 | 72
2018-12-16 22:00 | 54 | 54 |  |  | 43450.9167 | 72 | 72
2018-12-16 22:30 | 54 | 54 |  |  | 43450.9375 | 72 | 72
2018-12-16 23:00 | 53 | 53 |  |  | 43450.9583 | 70 | 70
2018-12-16 23:30 | 50 | 50 |  |  | 43450.9792 | 66 | 66
2018-12-17 | 45 | 45 |  |  | 43451 | 61 | 61
2018-12-17 00:30 | 41 | 41 |  |  | 43451.0208 | 55 | 55
2018-12-17 01:00 | 38 | 38 |  |  | 43451.0417 | 53 | 52
2018-12-17 01:30 | 38 | 38 |  |  | 43451.0625 | 52 | 52
2018-12-17 02:00 | 38 | 38 |  |  | 43451.0833 | 52 | 52
2018-12-17 02:30 | 37 | 37 |  |  | 43451.1042 | 50 | 50
2018-12-17 03:00 | 37 | 37 |  |  | 43451.125 | 49 | 49
2018-12-17 03:30 | 35 | 35 |  |  | 43451.1458 | 49 | 49
2018-12-17 04:00 | 35 | 35 |  |  | 43451.1667 | 49 | 49
2018-12-17 04:30 | 36 | 36 |  |  | 43451.1875 | 50 | 50
2018-12-17 05:00 | 40 | 40 |  |  | 43451.2083 | 54 | 54
2018-12-17 05:30 | 42 | 42 |  |  | 43451.2292 | 57 | 57
2018-12-17 06:00 | 47 | 46 |  |  | 43451.25 | 63 | 63
2018-12-17 06:30 | 52 | 51 |  |  | 43451.2708 | 71 | 70
2018-12-17 07:00 | 54 | 54 |  |  | 43451.2917 | 79 | 77
2018-12-17 07:30 | 59 | 57 |  |  | 43451.3125 | 87 | 85
2018-12-17 08:00 | 64 | 62 |  |  | 43451.3333 | 93 | 92
2018-12-17 08:30 | 69 | 68 |  |  | 43451.3542 | 99 | 98
2018-12-17 09:00 | 69 | 69 |  |  | 43451.375 | 98 | 98
2018-12-17 09:30 | 68 | 68 |  |  | 43451.3958 | 94 | 94
2018-12-17 10:00 | 67 | 66 |  |  | 43451.4167 | 94 | 94
2018-12-17 10:30 | 66 | 65 |  |  | 43451.4375 | 91 | 91
2018-12-17 11:00 | 64 | 64 |  |  | 43451.4583 | 91 | 91
2018-12-17 11:30 | 66 | 65 |  |  | 43451.4792 | 95 | 95
2018-12-17 12:00 | 69 | 68 |  |  | 43451.5 | 92 | 92
2018-12-17 12:30 | 68 | 67 |  |  | 43451.5208 | 93 | 93
2018-12-17 13:00 | 65 | 64 |  |  | 43451.5417 | 96 | 96
2018-12-17 13:30 | 65 | 64 |  |  | 43451.5625 | 96 | 96
2018-12-17 14:00 | 67 | 66 |  |  | 43451.5833 | 92 | 92
2018-12-17 14:30 | 70 | 69 |  |  | 43451.6042 | 93 | 93
2018-12-17 15:00 | 73 | 73 |  |  | 43451.625 | 96 | 96
2018-12-17 15:30 | 73 | 72 |  |  | 43451.6458 | 98 | 98
2018-12-17 16:00 | 72 | 71 |  |  | 43451.6667 | 99 | 99
2018-12-17 16:30 | 73 | 73 |  |  | 43451.6875 | 99 | 99
2018-12-17 17:00 | 74 | 74 |  |  | 43451.7083 | 100 | 99
2018-12-17 17:30 | 73 | 73 |  |  | 43451.7292 | 96 | 95
2018-12-17 18:00 | 74 | 74 |  |  | 43451.75 | 95 | 94
2018-12-17 18:30 | 75 | 75 |  |  | 43451.7708 | 94 | 93
2018-12-17 19:00 | 78 | 78 |  |  | 43451.7917 | 98 | 97
2018-12-17 19:30 | 80 | 80 |  |  | 43451.8125 | 98 | 98
2018-12-17 20:00 | 79 | 79 |  |  | 43451.8333 | 96 | 96
2018-12-17 20:30 | 77 | 77 |  |  | 43451.8542 | 94 | 94
2018-12-17 21:00 | 72 | 72 |  |  | 43451.875 | 88 | 88
2018-12-17 21:30 | 69 | 68 |  |  | 43451.8958 | 84 | 84
2018-12-17 22:00 | 64 | 64 |  |  | 43451.9167 | 80 | 80
2018-12-17 22:30 | 63 | 63 |  |  | 43451.9375 | 78 | 78
2018-12-17 23:00 | 60 | 60 |  |  | 43451.9583 | 74 | 74
2018-12-17 23:30 | 55 | 55 |  |  | 43451.9792 | 69 | 69
2018-12-18 | 49 | 49 |  |  | 43452 | 64 | 64
2018-12-18 00:30 | 47 | 45 |  |  | 43452.0208 | 60 | 58
2018-12-18 01:00 | 45 | 43 |  |  | 43452.0417 | 55 | 55
2018-12-18 01:30 | 43 | 41 |  |  | 43452.0625 | 53 | 53
2018-12-18 02:00 | 43 | 41 |  |  | 43452.0833 | 54 | 53
2018-12-18 02:30 | 42 | 40 |  |  | 43452.1042 | 53 | 53
2018-12-18 03:00 | 43 | 41 |  |  | 43452.125 | 54 | 53
2018-12-18 03:30 | 43 | 41 |  |  | 43452.1458 | 53 | 53
2018-12-18 04:00 | 42 | 40 |  |  | 43452.1667 | 52 | 52
2018-12-18 04:30 | 42 | 40 |  |  | 43452.1875 | 53 | 53
2018-12-18 05:00 | 43 | 42 |  |  | 43452.2083 | 55 | 55
2018-12-18 05:30 | 44 | 43 |  |  | 43452.2292 | 56 | 56
2018-12-18 06:00 | 47 | 46 |  |  | 43452.25 | 61 | 61
2018-12-18 06:30 | 52 | 51 |  |  | 43452.2708 | 70 | 70
2018-12-18 07:00 | 56 | 55 |  |  | 43452.2917 | 76 | 76
2018-12-18 07:30 | 59 | 59 |  |  | 43452.3125 | 83 | 83
2018-12-18 08:00 | 61 | 61 |  |  | 43452.3333 | 88 | 88
2018-12-18 08:30 | 66 | 65 |  |  | 43452.3542 | 93 | 93
2018-12-18 09:00 | 66 | 65 |  |  | 43452.375 | 91 | 90
2018-12-18 09:30 | 66 | 65 |  |  | 43452.3958 | 93 | 93
2018-12-18 10:00 | 64 | 62 |  |  | 43452.4167 | 87 | 86
2018-12-18 10:30 | 62 | 60 |  |  | 43452.4375 | 84 | 82
2018-12-18 11:00 | 62 | 60 |  |  | 43452.4583 | 87 | 85
2018-12-18 11:30 | 63 | 61 |  |  | 43452.4792 | 86 | 85
2018-12-18 12:00 | 65 | 63 |  |  | 43452.5 | 90 | 88
2018-12-18 12:30 | 69 | 68 |  |  | 43452.5208 | 92 | 91
2018-12-18 13:00 | 71 | 69 |  |  | 43452.5417 | 94 | 92
2018-12-18 13:30 | 70 | 68 |  |  | 43452.5625 | 92 | 90
2018-12-18 14:00 | 72 | 70 |  |  | 43452.5833 | 94 | 92
2018-12-18 14:30 | 74 | 72 |  |  | 43452.6042 | 99 | 96
2018-12-18 15:00 | 75 | 72 |  |  | 43452.625 | 101 | 99
2018-12-18 15:30 | 78 | 76 |  |  | 43452.6458 | 103 | 101
2018-12-18 16:00 | 82 | 80 |  |  | 43452.6667 | 106 | 103
2018-12-18 16:30 | 84 | 81 |  |  | 43452.6875 | 106 | 103
2018-12-18 17:00 | 88 | 85 |  |  | 43452.7083 | 108 | 105
2018-12-18 17:30 | 88 | 86 |  |  | 43452.7292 | 106 | 104
2018-12-18 18:00 | 88 | 86 |  |  | 43452.75 | 105 | 103
2018-12-18 18:30 | 87 | 84 |  |  | 43452.7708 | 102 | 100
2018-12-18 19:00 | 89 | 87 |  |  | 43452.7917 | 105 | 103
2018-12-18 19:30 | 90 | 88 |  |  | 43452.8125 | 105 | 103
2018-12-18 20:00 | 89 | 86 |  |  | 43452.8333 | 103 | 101
2018-12-18 20:30 | 84 | 82 |  |  | 43452.8542 | 99 | 98
2018-12-18 21:00 | 80 | 79 |  |  | 43452.875 | 95 | 94
2018-12-18 21:30 | 75 | 73 |  |  | 43452.8958 | 91 | 89
2018-12-18 22:00 | 73 | 71 |  |  | 43452.9167 | 88 | 86
2018-12-18 22:30 | 70 | 68 |  |  | 43452.9375 | 85 | 83
2018-12-18 23:00 | 65 | 64 |  |  | 43452.9583 | 78 | 77
2018-12-18 23:30 | 60 | 59 |  |  | 43452.9792 | 74 | 73
2018-12-19 | 56 | 54 |  |  | 43453 | 68 | 68
2018-12-19 00:30 | 52 | 50 |  |  | 43453.0208 | 63 | 62
2018-12-19 01:00 | 49 | 46 |  |  | 43453.0417 | 60 | 58
2018-12-19 01:30 | 48 | 45 |  |  | 43453.0625 | 58 | 56
2018-12-19 02:00 | 48 | 45 |  |  | 43453.0833 | 58 | 56
2018-12-19 02:30 | 47 | 44 |  |  | 43453.1042 | 58 | 56
2018-12-19 03:00 | 47 | 43 |  |  | 43453.125 | 58 | 56
2018-12-19 03:30 | 46 | 43 |  |  | 43453.1458 | 57 | 55
2018-12-19 04:00 | 46 | 42 |  |  | 43453.1667 | 57 | 55
2018-12-19 04:30 | 46 | 42 |  |  | 43453.1875 | 57 | 55
2018-12-19 05:00 | 46 | 42 |  |  | 43453.2083 | 58 | 56
2018-12-19 05:30 | 46 | 43 |  |  | 43453.2292 | 59 | 57
2018-12-19 06:00 | 49 | 47 |  |  | 43453.25 | 63 | 62
2018-12-19 06:30 | 52 | 50 |  |  | 43453.2708 | 70 | 70
2018-12-19 07:00 | 53 | 52 |  |  | 43453.2917 | 75 | 75
2018-12-19 07:30 | 58 | 58 |  |  | 43453.3125 | 85 | 85
2018-12-19 08:00 | 60 | 60 |  |  | 43453.3333 | 88 | 88
2018-12-19 08:30 | 64 | 64 |  |  | 43453.3542 | 92 | 92
2018-12-19 09:00 | 66 | 66 |  |  | 43453.375 | 95 | 95
2018-12-19 09:30 | 66 | 66 |  |  | 43453.3958 | 95 | 95
2018-12-19 10:00 | 66 | 66 |  |  | 43453.4167 | 94 | 94
2018-12-19 10:30 | 68 | 68 |  |  | 43453.4375 | 93 | 93
2018-12-19 11:00 | 68 | 68 |  |  | 43453.4583 | 91 | 91
2018-12-19 11:30 | 72 | 71 |  |  | 43453.4792 | 95 | 95
2018-12-19 12:00 | 74 | 73 |  |  | 43453.5 | 99 | 98
2018-12-19 12:30 | 76 | 75 |  |  | 43453.5208 | 98 | 98
2018-12-19 13:00 | 77 | 77 |  |  | 43453.5417 | 100 | 100
2018-12-19 13:30 | 78 | 77 |  |  | 43453.5625 | 101 | 101
2018-12-19 14:00 | 79 | 78 |  |  | 43453.5833 | 105 | 105
2018-12-19 14:30 | 79 | 79 |  |  | 43453.6042 | 104 | 104
2018-12-19 15:00 | 79 | 79 |  |  | 43453.625 | 106 | 106
2018-12-19 15:30 | 83 | 82 |  |  | 43453.6458 | 114 | 111
2018-12-19 16:00 | 87 | 86 |  |  | 43453.6667 | 119 | 116
2018-12-19 16:30 | 90 | 90 |  |  | 43453.6875 | 120 | 117
2018-12-19 17:00 | 95 | 94 |  |  | 43453.7083 | 124 | 120
2018-12-19 17:30 | 96 | 95 |  |  | 43453.7292 | 123 | 118
2018-12-19 18:00 | 96 | 96 |  |  | 43453.75 | 119 | 115
2018-12-19 18:30 | 93 | 93 |  |  | 43453.7708 | 118 | 111
2018-12-19 19:00 | 95 | 94 |  |  | 43453.7917 | 111 | 110
2018-12-19 19:30 | 95 | 93 |  |  | 43453.8125 | 111 | 110
2018-12-19 20:00 | 95 | 93 |  |  | 43453.8333 | 110 | 109
2018-12-19 20:30 | 94 | 92 |  |  | 43453.8542 | 109 | 108
2018-12-19 21:00 | 90 | 88 |  |  | 43453.875 | 104 | 103
2018-12-19 21:30 | 87 | 84 |  |  | 43453.8958 | 99 | 98
2018-12-19 22:00 | 85 | 82 |  |  | 43453.9167 | 97 | 97
2018-12-19 22:30 | 82 | 79 |  |  | 43453.9375 | 94 | 94
2018-12-19 23:00 | 80 | 77 |  |  | 43453.9583 | 91 | 90
2018-12-19 23:30 | 74 | 72 |  |  | 43453.9792 | 85 | 85
2018-12-20 | 68 | 67 |  |  | 43454 | 80 | 79
2018-12-20 00:30 | 61 | 60 |  |  | 43454.0208 | 73 | 72
2018-12-20 01:00 | 57 | 56 |  |  | 43454.0417 | 69 | 68
2018-12-20 01:30 | 57 | 56 |  |  | 43454.0625 | 69 | 67
2018-12-20 02:00 | 58 | 57 |  |  | 43454.0833 | 70 | 67
2018-12-20 02:30 | 56 | 55 |  |  | 43454.1042 | 68 | 65
2018-12-20 03:00 | 55 | 54 |  |  | 43454.125 | 68 | 65
2018-12-20 03:30 | 54 | 54 |  |  | 43454.1458 | 66 | 64
2018-12-20 04:00 | 55 | 54 |  |  | 43454.1667 | 67 | 65
2018-12-20 04:30 | 55 | 54 |  |  | 43454.1875 | 68 | 66
2018-12-20 05:00 | 56 | 56 |  |  | 43454.2083 | 70 | 68
2018-12-20 05:30 | 57 | 56 |  |  | 43454.2292 | 71 | 69
2018-12-20 06:00 | 59 | 57 |  |  | 43454.25 | 73 | 72
2018-12-20 06:30 | 63 | 60 |  |  | 43454.2708 | 79 | 79
2018-12-20 07:00 | 67 | 65 |  |  | 43454.2917 | 86 | 86
2018-12-20 07:30 | 73 | 71 |  |  | 43454.3125 | 94 | 94
2018-12-20 08:00 | 74 | 73 |  |  | 43454.3333 | 97 | 97
2018-12-20 08:30 | 72 | 71 |  |  | 43454.3542 | 99 | 99
2018-12-20 09:00 | 75 | 73 |  |  | 43454.375 | 100 | 100
2018-12-20 09:30 | 77 | 75 |  |  | 43454.3958 | 102 | 102
2018-12-20 10:00 | 76 | 75 |  |  | 43454.4167 | 102 | 101
2018-12-20 10:30 | 75 | 75 |  |  | 43454.4375 | 102 | 101
2018-12-20 11:00 | 75 | 75 |  |  | 43454.4583 | 109 | 102
2018-12-20 11:30 | 78 | 78 |  |  | 43454.4792 | 111 | 105
2018-12-20 12:00 | 82 | 82 |  |  | 43454.5 | 115 | 108
2018-12-20 12:30 | 84 | 84 |  |  | 43454.5208 | 118 | 111
2018-12-20 13:00 | 88 | 88 |  |  | 43454.5417 | 120 | 114
2018-12-20 13:30 | 91 | 91 |  |  | 43454.5625 | 122 | 116
2018-12-20 14:00 | 89 | 88 |  |  | 43454.5833 | 122 | 116
2018-12-20 14:30 | 88 | 88 |  |  | 43454.6042 | 122 | 116
2018-12-20 15:00 | 87 | 87 |  |  | 43454.625 | 123 | 116
2018-12-20 15:30 | 87 | 87 |  |  | 43454.6458 | 125 | 117
2018-12-20 16:00 | 93 | 93 |  |  | 43454.6667 | 129 | 121
2018-12-20 16:30 | 95 | 95 |  |  | 43454.6875 | 131 | 123
2018-12-20 17:00 | 89 | 89 |  |  | 43454.7083 | 129 | 121
2018-12-20 17:30 | 88 | 88 |  |  | 43454.7292 | 130 | 119
2018-12-20 18:00 | 88 | 88 |  |  | 43454.75 | 128 | 116
2018-12-20 18:30 | 85 | 85 |  |  | 43454.7708 | 127 | 112
2018-12-20 19:00 | 87 | 87 |  |  | 43454.7917 | 126 | 115
2018-12-20 19:30 | 87 | 87 |  |  | 43454.8125 | 125 | 115
2018-12-20 20:00 | 90 | 90 |  |  | 43454.8333 | 127 | 116
2018-12-20 20:30 | 94 | 94 |  |  | 43454.8542 | 128 | 117
2018-12-20 21:00 | 91 | 91 |  |  | 43454.875 | 122 | 113
2018-12-20 21:30 | 89 | 88 |  |  | 43454.8958 | 115 | 108
2018-12-20 22:00 | 93 | 91 |  |  | 43454.9167 | 109 | 107
2018-12-20 22:30 | 89 | 87 |  |  | 43454.9375 | 105 | 104
2018-12-20 23:00 | 83 | 80 |  |  | 43454.9583 | 98 | 97
2018-12-20 23:30 | 77 | 75 |  |  | 43454.9792 | 92 | 90
2018-12-21 | 70 | 69 |  |  | 43455 | 86 | 84
2018-12-21 00:30 | 66 | 65 |  |  | 43455.0208 | 79 | 77
2018-12-21 01:00 | 61 | 60 |  |  | 43455.0417 | 74 | 72
2018-12-21 01:30 | 61 | 60 |  |  | 43455.0625 | 73 | 71
2018-12-21 02:00 | 61 | 60 |  |  | 43455.0833 | 73 | 72
2018-12-21 02:30 | 61 | 60 |  |  | 43455.1042 | 73 | 71
2018-12-21 03:00 | 59 | 58 |  |  | 43455.125 | 72 | 70
2018-12-21 03:30 | 59 | 57 |  |  | 43455.1458 | 71 | 69
2018-12-21 04:00 | 58 | 56 |  |  | 43455.1667 | 69 | 67
2018-12-21 04:30 | 57 | 56 |  |  | 43455.1875 | 69 | 67
2018-12-21 05:00 | 58 | 57 |  |  | 43455.2083 | 71 | 69
2018-12-21 05:30 | 58 | 57 |  |  | 43455.2292 | 72 | 70
2018-12-21 06:00 | 59 | 58 |  |  | 43455.25 | 73 | 72
2018-12-21 06:30 | 66 | 64 |  |  | 43455.2708 | 83 | 83
2018-12-21 07:00 | 70 | 67 |  |  | 43455.2917 | 91 | 91
2018-12-21 07:30 | 81 | 78 |  |  | 43455.3125 | 102 | 102
2018-12-21 08:00 | 90 | 88 |  |  | 43455.3333 | 115 | 115
2018-12-21 08:30 | 94 | 91 |  |  | 43455.3542 | 120 | 120
2018-12-21 09:00 | 100 | 96 |  |  | 43455.375 | 124 | 124
2018-12-21 09:30 | 99 | 96 |  |  | 43455.3958 | 124 | 124
2018-12-21 10:00 | 98 | 94 |  |  | 43455.4167 | 122 | 122
2018-12-21 10:30 | 96 | 95 |  |  | 43455.4375 | 127 | 125
2018-12-21 11:00 | 93 | 92 |  |  | 43455.4583 | 125 | 122
2018-12-21 11:30 | 98 | 98 |  |  | 43455.4792 | 129 | 126
2018-12-21 12:00 | 101 | 100 |  |  | 43455.5 | 131 | 128
2018-12-21 12:30 | 102 | 102 |  |  | 43455.5208 | 133 | 130
2018-12-21 13:00 | 104 | 104 |  |  | 43455.5417 | 141 | 131
2018-12-21 13:30 | 107 | 106 |  |  | 43455.5625 | 142 | 133
2018-12-21 14:00 | 109 | 109 |  |  | 43455.5833 | 144 | 136
2018-12-21 14:30 | 112 | 112 |  |  | 43455.6042 | 147 | 139
2018-12-21 15:00 | 106 | 106 |  |  | 43455.625 | 148 | 139
2018-12-21 15:30 | 107 | 107 |  |  | 43455.6458 | 150 | 140
2018-12-21 16:00 | 108 | 108 |  |  | 43455.6667 | 152 | 142
2018-12-21 16:30 | 111 | 110 |  |  | 43455.6875 | 152 | 144
2018-12-21 17:00 | 114 | 114 |  |  | 43455.7083 | 154 | 146
2018-12-21 17:30 | 118 | 118 |  |  | 43455.7292 | 155 | 147
2018-12-21 18:00 | 109 | 109 |  |  | 43455.75 | 148 | 142
2018-12-21 18:30 | 102 | 102 |  |  | 43455.7708 | 133 | 128
2018-12-21 19:00 | 100 | 99 |  |  | 43455.7917 | 124 | 123
2018-12-21 19:30 | 96 | 94 |  |  | 43455.8125 | 118 | 118
2018-12-21 20:00 | 92 | 90 |  |  | 43455.8333 | 113 | 113
2018-12-21 20:30 | 88 | 86 |  |  | 43455.8542 | 109 | 109
2018-12-21 21:00 | 85 | 84 |  |  | 43455.875 | 107 | 106
2018-12-21 21:30 | 84 | 84 |  |  | 43455.8958 | 102 | 101
2018-12-21 22:00 | 80 | 80 |  |  | 43455.9167 | 98 | 98
2018-12-21 22:30 | 73 | 73 |  |  | 43455.9375 | 90 | 90
2018-12-21 23:00 | 69 | 68 |  |  | 43455.9583 | 85 | 85
2018-12-21 23:30 | 64 | 63 |  |  | 43455.9792 | 80 | 80
2018-12-22 | 63 | 63 |  |  | 43456 | 80 | 79
2018-12-22 00:30 | 62 | 62 |  |  | 43456.0208 | 77 | 77
2018-12-22 01:00 | 58 | 58 |  |  | 43456.0417 | 75 | 74
2018-12-22 01:30 | 56 | 56 |  |  | 43456.0625 | 71 | 71
2018-12-22 02:00 | 54 | 54 |  |  | 43456.0833 | 70 | 69
2018-12-22 02:30 | 52 | 52 |  |  | 43456.1042 | 68 | 66
2018-12-22 03:00 | 48 | 48 |  |  | 43456.125 | 64 | 62
2018-12-22 03:30 | 48 | 48 |  |  | 43456.1458 | 63 | 62
2018-12-22 04:00 | 47 | 47 |  |  | 43456.1667 | 63 | 61
2018-12-22 04:30 | 47 | 47 |  |  | 43456.1875 | 63 | 61
2018-12-22 05:00 | 49 | 49 |  |  | 43456.2083 | 65 | 64
2018-12-22 05:30 | 48 | 48 |  |  | 43456.2292 | 64 | 63
2018-12-22 06:00 | 46 | 46 |  |  | 43456.25 | 63 | 62
2018-12-22 06:30 | 46 | 46 |  |  | 43456.2708 | 65 | 64
2018-12-22 07:00 | 49 | 49 |  |  | 43456.2917 | 68 | 67
2018-12-22 07:30 | 50 | 50 |  |  | 43456.3125 | 71 | 71
2018-12-22 08:00 | 53 | 53 |  |  | 43456.3333 | 74 | 74
2018-12-22 08:30 | 56 | 55 |  |  | 43456.3542 | 81 | 80
2018-12-22 09:00 | 60 | 59 |  |  | 43456.375 | 81 | 81
2018-12-22 09:30 | 61 | 59 |  |  | 43456.3958 | 82 | 81
2018-12-22 10:00 | 61 | 60 |  |  | 43456.4167 | 82 | 82
2018-12-22 10:30 | 61 | 60 |  |  | 43456.4375 | 82 | 82
2018-12-22 11:00 | 65 | 63 |  |  | 43456.4583 | 88 | 88
2018-12-22 11:30 | 65 | 63 |  |  | 43456.4792 | 85 | 85
2018-12-22 12:00 | 69 | 67 |  |  | 43456.5 | 86 | 86
2018-12-22 12:30 | 74 | 73 |  |  | 43456.5208 | 93 | 92
2018-12-22 13:00 | 80 | 79 |  |  | 43456.5417 | 98 | 97
2018-12-22 13:30 | 84 | 83 |  |  | 43456.5625 | 100 | 100
2018-12-22 14:00 | 88 | 88 |  |  | 43456.5833 | 103 | 103
2018-12-22 14:30 | 85 | 85 |  |  | 43456.6042 | 101 | 101
2018-12-22 15:00 | 86 | 86 |  |  | 43456.625 | 103 | 102
2018-12-22 15:30 | 91 | 89 |  |  | 43456.6458 | 114 | 107
2018-12-22 16:00 | 95 | 94 |  |  | 43456.6667 | 122 | 116
2018-12-22 16:30 | 94 | 93 |  |  | 43456.6875 | 120 | 114
2018-12-22 17:00 | 96 | 94 |  |  | 43456.7083 | 120 | 114
2018-12-22 17:30 | 89 | 87 |  |  | 43456.7292 | 111 | 107
2018-12-22 18:00 | 78 | 78 |  |  | 43456.75 | 106 | 98
2018-12-22 18:30 | 73 | 73 |  |  | 43456.7708 | 100 | 93
2018-12-22 19:00 | 73 | 73 |  |  | 43456.7917 | 98 | 93
2018-12-22 19:30 | 70 | 70 |  |  | 43456.8125 | 94 | 90
2018-12-22 20:00 | 68 | 68 |  |  | 43456.8333 | 92 | 87
2018-12-22 20:30 | 66 | 66 |  |  | 43456.8542 | 90 | 85
2018-12-22 21:00 | 66 | 63 |  |  | 43456.875 | 80 | 80
2018-12-22 21:30 | 63 | 60 |  |  | 43456.8958 | 77 | 77
2018-12-22 22:00 | 60 | 57 |  |  | 43456.9167 | 77 | 77
2018-12-22 22:30 | 63 | 60 |  |  | 43456.9375 | 78 | 78
2018-12-22 23:00 | 61 | 58 |  |  | 43456.9583 | 75 | 75
2018-12-22 23:30 | 56 | 53 |  |  | 43456.9792 | 71 | 71
2018-12-23 | 52 | 49 |  |  | 43457 | 66 | 66
2018-12-23 00:30 | 49 | 45 |  |  | 43457.0208 | 62 | 62
2018-12-23 01:00 | 48 | 45 |  |  | 43457.0417 | 61 | 60
2018-12-23 01:30 | 48 | 45 |  |  | 43457.0625 | 61 | 60
2018-12-23 02:00 | 47 | 44 |  |  | 43457.0833 | 61 | 60
2018-12-23 02:30 | 47 | 44 |  |  | 43457.1042 | 61 | 60
2018-12-23 03:00 | 46 | 44 |  |  | 43457.125 | 60 | 59
2018-12-23 03:30 | 46 | 44 |  |  | 43457.1458 | 59 | 58
2018-12-23 04:00 | 46 | 44 |  |  | 43457.1667 | 59 | 58
2018-12-23 04:30 | 46 | 44 |  |  | 43457.1875 | 59 | 58
2018-12-23 05:00 | 44 | 42 |  |  | 43457.2083 | 58 | 57
2018-12-23 05:30 | 42 | 41 |  |  | 43457.2292 | 57 | 55
2018-12-23 06:00 | 40 | 39 |  |  | 43457.25 | 56 | 55
2018-12-23 06:30 | 39 | 38 |  |  | 43457.2708 | 57 | 55
2018-12-23 07:00 | 38 | 36 |  |  | 43457.2917 | 54 | 53
2018-12-23 07:30 | 38 | 36 |  |  | 43457.3125 | 55 | 54
2018-12-23 08:00 | 38 | 36 |  |  | 43457.3333 | 55 | 54
2018-12-23 08:30 | 41 | 38 |  |  | 43457.3542 | 57 | 56
2018-12-23 09:00 | 43 | 40 |  |  | 43457.375 | 59 | 59
2018-12-23 09:30 | 44 | 42 |  |  | 43457.3958 | 60 | 59
2018-12-23 10:00 | 45 | 42 |  |  | 43457.4167 | 59 | 59
2018-12-23 10:30 | 46 | 43 |  |  | 43457.4375 | 59 | 59
2018-12-23 11:00 | 47 | 44 |  |  | 43457.4583 | 61 | 61
2018-12-23 11:30 | 49 | 46 |  |  | 43457.4792 | 62 | 62
2018-12-23 12:00 | 49 | 46 |  |  | 43457.5 | 61 | 60
2018-12-23 12:30 | 50 | 47 |  |  | 43457.5208 | 60 | 59
2018-12-23 13:00 | 47 | 45 |  |  | 43457.5417 | 58 | 58
2018-12-23 13:30 | 46 | 44 |  |  | 43457.5625 | 58 | 57
2018-12-23 14:00 | 47 | 44 |  |  | 43457.5833 | 56 | 56
2018-12-23 14:30 | 47 | 45 |  |  | 43457.6042 | 58 | 57
2018-12-23 15:00 | 50 | 48 |  |  | 43457.625 | 62 | 62
2018-12-23 15:30 | 52 | 50 |  |  | 43457.6458 | 65 | 65
2018-12-23 16:00 | 55 | 54 |  |  | 43457.6667 | 68 | 68
2018-12-23 16:30 | 54 | 53 |  |  | 43457.6875 | 69 | 68
2018-12-23 17:00 | 56 | 54 |  |  | 43457.7083 | 71 | 70
2018-12-23 17:30 | 55 | 54 |  |  | 43457.7292 | 70 | 70
2018-12-23 18:00 | 56 | 54 |  |  | 43457.75 | 72 | 71
2018-12-23 18:30 | 57 | 56 |  |  | 43457.7708 | 73 | 72
2018-12-23 19:00 | 59 | 57 |  |  | 43457.7917 | 76 | 75
2018-12-23 19:30 | 62 | 60 |  |  | 43457.8125 | 78 | 78
2018-12-23 20:00 | 60 | 58 |  |  | 43457.8333 | 77 | 77
2018-12-23 20:30 | 60 | 58 |  |  | 43457.8542 | 76 | 76
2018-12-23 21:00 | 58 | 56 |  |  | 43457.875 | 74 | 74
2018-12-23 21:30 | 54 | 52 |  |  | 43457.8958 | 71 | 71
2018-12-23 22:00 | 55 | 53 |  |  | 43457.9167 | 72 | 72
2018-12-23 22:30 | 56 | 54 |  |  | 43457.9375 | 74 | 74
2018-12-23 23:00 | 55 | 53 |  |  | 43457.9583 | 71 | 71
2018-12-23 23:30 | 54 | 52 |  |  | 43457.9792 | 69 | 69
2018-12-24 | 51 | 49 |  |  | 43458 | 66 | 65
2018-12-24 00:30 | 48 | 46 |  |  | 43458.0208 | 62 | 61
2018-12-24 01:00 | 45 | 44 |  |  | 43458.0417 | 58 | 58
2018-12-24 01:30 | 46 | 44 |  |  | 43458.0625 | 58 | 57
2018-12-24 02:00 | 45 | 44 |  |  | 43458.0833 | 59 | 58
2018-12-24 02:30 | 43 | 42 |  |  | 43458.1042 | 57 | 56
2018-12-24 03:00 | 42 | 41 |  |  | 43458.125 | 56 | 55
2018-12-24 03:30 | 42 | 41 |  |  | 43458.1458 | 56 | 55
2018-12-24 04:00 | 43 | 42 |  |  | 43458.1667 | 57 | 55
2018-12-24 04:30 | 42 | 41 |  |  | 43458.1875 | 56 | 55
2018-12-24 05:00 | 43 | 41 |  |  | 43458.2083 | 57 | 56
2018-12-24 05:30 | 42 | 41 |  |  | 43458.2292 | 58 | 58
2018-12-24 06:00 | 43 | 41 |  |  | 43458.25 | 59 | 59
2018-12-24 06:30 | 47 | 45 |  |  | 43458.2708 | 64 | 64
2018-12-24 07:00 | 46 | 43 |  |  | 43458.2917 | 65 | 65
2018-12-24 07:30 | 45 | 45 |  |  | 43458.3125 | 68 | 68
2018-12-24 08:00 | 47 | 46 |  |  | 43458.3333 | 71 | 71
2018-12-24 08:30 | 51 | 50 |  |  | 43458.3542 | 74 | 74
2018-12-24 09:00 | 51 | 50 |  |  | 43458.375 | 76 | 75
2018-12-24 09:30 | 54 | 52 |  |  | 43458.3958 | 77 | 77
2018-12-24 10:00 | 55 | 53 |  |  | 43458.4167 | 77 | 77
2018-12-24 10:30 | 54 | 52 |  |  | 43458.4375 | 75 | 75
2018-12-24 11:00 | 53 | 51 |  |  | 43458.4583 | 75 | 75
2018-12-24 11:30 | 55 | 53 |  |  | 43458.4792 | 79 | 79
2018-12-24 12:00 | 52 | 50 |  |  | 43458.5 | 69 | 69
2018-12-24 12:30 | 47 | 45 |  |  | 43458.5208 | 69 | 69
2018-12-24 13:00 | 48 | 46 |  |  | 43458.5417 | 68 | 68
2018-12-24 13:30 | 48 | 45 |  |  | 43458.5625 | 68 | 68
2018-12-24 14:00 | 46 | 44 |  |  | 43458.5833 | 67 | 67
2018-12-24 14:30 | 47 | 45 |  |  | 43458.6042 | 66 | 66
2018-12-24 15:00 | 48 | 46 |  |  | 43458.625 | 66 | 66
2018-12-24 15:30 | 48 | 46 |  |  | 43458.6458 | 69 | 69
2018-12-24 16:00 | 53 | 51 |  |  | 43458.6667 | 74 | 74
2018-12-24 16:30 | 54 | 52 |  |  | 43458.6875 | 75 | 75
2018-12-24 17:00 | 58 | 57 |  |  | 43458.7083 | 79 | 79
2018-12-24 17:30 | 59 | 58 |  |  | 43458.7292 | 79 | 79
2018-12-24 18:00 | 59 | 58 |  |  | 43458.75 | 78 | 78
2018-12-24 18:30 | 64 | 55 |  |  | 43458.7708 | 75 | 73
2018-12-24 19:00 | 67 | 56 |  |  | 43458.7917 | 77 | 74
2018-12-24 19:30 | 67 | 57 |  |  | 43458.8125 | 78 | 75
2018-12-24 20:00 | 67 | 56 |  |  | 43458.8333 | 77 | 74
2018-12-24 20:30 | 65 | 56 |  |  | 43458.8542 | 76 | 73
2018-12-24 21:00 | 64 | 54 |  |  | 43458.875 | 74 | 71
2018-12-24 21:30 | 64 | 52 |  |  | 43458.8958 | 73 | 69
2018-12-24 22:00 | 63 | 51 |  |  | 43458.9167 | 73 | 69
2018-12-24 22:30 | 63 | 51 |  |  | 43458.9375 | 73 | 70
2018-12-24 23:00 | 65 | 51 |  |  | 43458.9583 | 72 | 67
2018-12-24 23:30 | 63 | 48 |  |  | 43458.9792 | 68 | 63
2018-12-25 | 59 | 43 |  |  | 43459 | 64 | 58
2018-12-25 00:30 | 56 | 38 |  |  | 43459.0208 | 59 | 51
2018-12-25 01:00 | 53 | 33 |  |  | 43459.0417 | 55 | 47
2018-12-25 01:30 | 53 | 32 |  |  | 43459.0625 | 53 | 45
2018-12-25 02:00 | 53 | 30 |  |  | 43459.0833 | 52 | 43
2018-12-25 02:30 | 53 | 30 |  |  | 43459.1042 | 52 | 43
2018-12-25 03:00 | 51 | 29 |  |  | 43459.125 | 50 | 42
2018-12-25 03:30 | 51 | 28 |  |  | 43459.1458 | 49 | 41
2018-12-25 04:00 | 50 | 28 |  |  | 43459.1667 | 48 | 40
2018-12-25 04:30 | 48 | 28 |  |  | 43459.1875 | 47 | 41
2018-12-25 05:00 | 51 | 28 |  |  | 43459.2083 | 47 | 41
2018-12-25 05:30 | 63 | 25 |  |  | 43459.2292 | 50 | 38
2018-12-25 06:00 | 63 | 26 |  |  | 43459.25 | 51 | 40
2018-12-25 06:30 | 63 | 26 |  |  | 43459.2708 | 51 | 40
2018-12-25 07:00 | 61 | 25 |  |  | 43459.2917 | 50 | 40
2018-12-25 07:30 | 60 | 24 |  |  | 43459.3125 | 50 | 41
2018-12-25 08:00 | 58 | 24 |  |  | 43459.3333 | 48 | 40
2018-12-25 08:30 | 59 | 26 |  |  | 43459.3542 | 50 | 42
2018-12-25 09:00 | 59 | 26 |  |  | 43459.375 | 50 | 44
2018-12-25 09:30 | 59 | 28 |  |  | 43459.3958 | 53 | 47
2018-12-25 10:00 | 59 | 30 |  |  | 43459.4167 | 52 | 46
2018-12-25 10:30 | 60 | 32 |  |  | 43459.4375 | 52 | 47
2018-12-25 11:00 | 59 | 32 |  |  | 43459.4583 | 53 | 48
2018-12-25 11:30 | 59 | 31 |  |  | 43459.4792 | 51 | 46
2018-12-25 12:00 | 59 | 31 |  |  | 43459.5 | 51 | 46
2018-12-25 12:30 | 59 | 32 |  |  | 43459.5208 | 52 | 46
2018-12-25 13:00 | 58 | 30 |  |  | 43459.5417 | 50 | 44
2018-12-25 13:30 | 58 | 32 |  |  | 43459.5625 | 50 | 45
2018-12-25 14:00 | 59 | 33 |  |  | 43459.5833 | 50 | 45
2018-12-25 14:30 | 59 | 33 |  |  | 43459.6042 | 51 | 46
2018-12-25 15:00 | 60 | 34 |  |  | 43459.625 | 52 | 47
2018-12-25 15:30 | 60 | 35 |  |  | 43459.6458 | 53 | 48
2018-12-25 16:00 | 56 | 35 |  |  | 43459.6667 | 54 | 50
2018-12-25 16:30 | 56 | 38 |  |  | 43459.6875 | 56 | 53
2018-12-25 17:00 | 57 | 38 |  |  | 43459.7083 | 58 | 55
2018-12-25 17:30 | 58 | 39 |  |  | 43459.7292 | 58 | 55
2018-12-25 18:00 | 58 | 40 |  |  | 43459.75 | 60 | 57
2018-12-25 18:30 | 62 | 43 |  |  | 43459.7708 | 62 | 59
2018-12-25 19:00 | 64 | 46 |  |  | 43459.7917 | 66 | 62
2018-12-25 19:30 | 64 | 47 |  |  | 43459.8125 | 67 | 64
2018-12-25 20:00 | 65 | 49 |  |  | 43459.8333 | 68 | 65
2018-12-25 20:30 | 65 | 48 |  |  | 43459.8542 | 68 | 64
2018-12-25 21:00 | 65 | 47 |  |  | 43459.875 | 66 | 62
2018-12-25 21:30 | 65 | 46 |  |  | 43459.8958 | 66 | 62
2018-12-25 22:00 | 65 | 45 |  |  | 43459.9167 | 67 | 62
2018-12-25 22:30 | 67 | 47 |  |  | 43459.9375 | 68 | 64
2018-12-25 23:00 | 66 | 46 |  |  | 43459.9583 | 66 | 61
2018-12-25 23:30 | 66 | 44 |  |  | 43459.9792 | 64 | 59
2018-12-26 | 64 | 40 |  |  | 43460 | 61 | 55
2018-12-26 00:30 | 63 | 38 |  |  | 43460.0208 | 59 | 52
2018-12-26 01:00 | 62 | 35 |  |  | 43460.0417 | 55 | 47
2018-12-26 01:30 | 61 | 33 |  |  | 43460.0625 | 54 | 45
2018-12-26 02:00 | 61 | 32 |  |  | 43460.0833 | 54 | 45
2018-12-26 02:30 | 61 | 32 |  |  | 43460.1042 | 53 | 44
2018-12-26 03:00 | 61 | 32 |  |  | 43460.125 | 52 | 43
2018-12-26 03:30 | 61 | 32 |  |  | 43460.1458 | 52 | 43
2018-12-26 04:00 | 61 | 31 |  |  | 43460.1667 | 52 | 43
2018-12-26 04:30 | 60 | 30 |  |  | 43460.1875 | 52 | 43
2018-12-26 05:00 | 60 | 30 |  |  | 43460.2083 | 52 | 43
2018-12-26 05:30 | 60 | 30 |  |  | 43460.2292 | 52 | 43
2018-12-26 06:00 | 60 | 30 |  |  | 43460.25 | 53 | 43
2018-12-26 06:30 | 60 | 29 |  |  | 43460.2708 | 53 | 44
2018-12-26 07:00 | 59 | 28 |  |  | 43460.2917 | 52 | 44
2018-12-26 07:30 | 57 | 27 |  |  | 43460.3125 | 52 | 45
2018-12-26 08:00 | 55 | 27 |  |  | 43460.3333 | 51 | 44
2018-12-26 08:30 | 54 | 28 |  |  | 43460.3542 | 52 | 47
2018-12-26 09:00 | 55 | 31 |  |  | 43460.375 | 53 | 49
2018-12-26 09:30 | 55 | 31 |  |  | 43460.3958 | 53 | 49
2018-12-26 10:00 | 53 | 30 |  |  | 43460.4167 | 51 | 47
2018-12-26 10:30 | 53 | 31 |  |  | 43460.4375 | 49 | 46
2018-12-26 11:00 | 53 | 31 |  |  | 43460.4583 | 50 | 47
2018-12-26 11:30 | 52 | 31 |  |  | 43460.4792 | 49 | 46
2018-12-26 12:00 | 51 | 28 |  |  | 43460.5 | 47 | 43
2018-12-26 12:30 | 51 | 29 |  |  | 43460.5208 | 48 | 44
2018-12-26 13:00 | 50 | 28 |  |  | 43460.5417 | 48 | 44
2018-12-26 13:30 | 52 | 31 |  |  | 43460.5625 | 49 | 46
2018-12-26 14:00 | 53 | 32 |  |  | 43460.5833 | 49 | 46
2018-12-26 14:30 | 53 | 33 |  |  | 43460.6042 | 50 | 47
2018-12-26 15:00 | 54 | 35 |  |  | 43460.625 | 52 | 48
2018-12-26 15:30 | 55 | 36 |  |  | 43460.6458 | 54 | 51
2018-12-26 16:00 | 56 | 38 |  |  | 43460.6667 | 56 | 53
2018-12-26 16:30 | 57 | 40 |  |  | 43460.6875 | 58 | 55
2018-12-26 17:00 | 59 | 42 |  |  | 43460.7083 | 61 | 58
2018-12-26 17:30 | 59 | 43 |  |  | 43460.7292 | 62 | 59
2018-12-26 18:00 | 61 | 45 |  |  | 43460.75 | 64 | 61
2018-12-26 18:30 | 64 | 47 |  |  | 43460.7708 | 66 | 62
2018-12-26 19:00 | 66 | 49 |  |  | 43460.7917 | 69 | 66
2018-12-26 19:30 | 68 | 52 |  |  | 43460.8125 | 72 | 68
2018-12-26 20:00 | 68 | 52 |  |  | 43460.8333 | 72 | 68
2018-12-26 20:30 | 68 | 52 |  |  | 43460.8542 | 72 | 68
2018-12-26 21:00 | 69 | 51 |  |  | 43460.875 | 71 | 67
2018-12-26 21:30 | 67 | 49 |  |  | 43460.8958 | 69 | 64
2018-12-26 22:00 | 68 | 49 |  |  | 43460.9167 | 71 | 66
2018-12-26 22:30 | 69 | 50 |  |  | 43460.9375 | 72 | 67
2018-12-26 23:00 | 69 | 49 |  |  | 43460.9583 | 70 | 64
2018-12-26 23:30 | 67 | 45 |  |  | 43460.9792 | 66 | 60
2018-12-27 | 65 | 40 |  |  | 43461 | 62 | 55
2018-12-27 00:30 | 63 | 36 |  |  | 43461.0208 | 59 | 50
2018-12-27 01:00 | 62 | 33 |  |  | 43461.0417 | 56 | 46
2018-12-27 01:30 | 62 | 33 |  |  | 43461.0625 | 55 | 45
2018-12-27 02:00 | 62 | 32 |  |  | 43461.0833 | 55 | 45
2018-12-27 02:30 | 62 | 33 |  |  | 43461.1042 | 56 | 46
2018-12-27 03:00 | 63 | 34 |  |  | 43461.125 | 58 | 48
2018-12-27 03:30 | 63 | 34 |  |  | 43461.1458 | 58 | 48
2018-12-27 04:00 | 64 | 35 |  |  | 43461.1667 | 59 | 49
2018-12-27 04:30 | 64 | 36 |  |  | 43461.1875 | 60 | 50
2018-12-27 05:00 | 65 | 37 |  |  | 43461.2083 | 59 | 50
2018-12-27 05:30 | 66 | 37 |  |  | 43461.2292 | 61 | 51
2018-12-27 06:00 | 65 | 37 |  |  | 43461.25 | 62 | 52
2018-12-27 06:30 | 65 | 39 |  |  | 43461.2708 | 63 | 55
2018-12-27 07:00 | 63 | 39 |  |  | 43461.2917 | 64 | 58
2018-12-27 07:30 | 61 | 40 |  |  | 43461.3125 | 65 | 61
2018-12-27 08:00 | 58 | 39 |  |  | 43461.3333 | 64 | 61
2018-12-27 08:30 | 59 | 38 |  |  | 43461.3542 | 66 | 62
2018-12-27 09:00 | 59 | 38 |  |  | 43461.375 | 67 | 63
2018-12-27 09:30 | 60 | 41 |  |  | 43461.3958 | 69 | 66
2018-12-27 10:00 | 61 | 43 |  |  | 43461.4167 | 70 | 66
2018-12-27 10:30 | 61 | 43 |  |  | 43461.4375 | 69 | 65
2018-12-27 11:00 | 60 | 43 |  |  | 43461.4583 | 67 | 64
2018-12-27 11:30 | 60 | 42 |  |  | 43461.4792 | 67 | 63
2018-12-27 12:00 | 60 | 43 |  |  | 43461.5 | 67 | 63
2018-12-27 12:30 | 60 | 43 |  |  | 43461.5208 | 66 | 62
2018-12-27 13:00 | 63 | 43 |  |  | 43461.5417 | 65 | 62
2018-12-27 13:30 | 69 | 45 |  |  | 43461.5625 | 66 | 65
2018-12-27 14:00 | 70 | 45 |  |  | 43461.5833 | 67 | 66
2018-12-27 14:30 | 72 | 45 |  |  | 43461.6042 | 67 | 65
2018-12-27 15:00 | 72 | 46 |  |  | 43461.625 | 67 | 65
2018-12-27 15:30 | 73 | 48 |  |  | 43461.6458 | 69 | 67
2018-12-27 16:00 | 74 | 50 |  |  | 43461.6667 | 71 | 70
2018-12-27 16:30 | 76 | 52 |  |  | 43461.6875 | 74 | 72
2018-12-27 17:00 | 80 | 57 |  |  | 43461.7083 | 79 | 77
2018-12-27 17:30 | 81 | 58 |  |  | 43461.7292 | 80 | 78
2018-12-27 18:00 | 84 | 59 |  |  | 43461.75 | 82 | 79
2018-12-27 18:30 | 84 | 59 |  |  | 43461.7708 | 80 | 77
2018-12-27 19:00 | 85 | 62 |  |  | 43461.7917 | 81 | 79
2018-12-27 19:30 | 86 | 64 |  |  | 43461.8125 | 84 | 82
2018-12-27 20:00 | 86 | 64 |  |  | 43461.8333 | 84 | 82
2018-12-27 20:30 | 85 | 63 |  |  | 43461.8542 | 83 | 81
2018-12-27 21:00 | 82 | 61 |  |  | 43461.875 | 81 | 79
2018-12-27 21:30 | 81 | 58 |  |  | 43461.8958 | 77 | 75
2018-12-27 22:00 | 82 | 59 |  |  | 43461.9167 | 78 | 77
2018-12-27 22:30 | 80 | 56 |  |  | 43461.9375 | 76 | 75
2018-12-27 23:00 | 78 | 53 |  |  | 43461.9583 | 72 | 70
2018-12-27 23:30 | 76 | 49 |  |  | 43461.9792 | 69 | 67
2018-12-28 | 75 | 46 |  |  | 43462 | 65 | 62
2018-12-28 00:30 | 73 | 42 |  |  | 43462.0208 | 60 | 58
2018-12-28 01:00 | 71 | 38 |  |  | 43462.0417 | 56 | 53
2018-12-28 01:30 | 70 | 37 |  |  | 43462.0625 | 53 | 51
2018-12-28 02:00 | 70 | 35 |  |  | 43462.0833 | 53 | 50
2018-12-28 02:30 | 70 | 36 |  |  | 43462.1042 | 54 | 51
2018-12-28 03:00 | 71 | 36 |  |  | 43462.125 | 54 | 51
2018-12-28 03:30 | 71 | 38 |  |  | 43462.1458 | 55 | 52
2018-12-28 04:00 | 71 | 36 |  |  | 43462.1667 | 55 | 52
2018-12-28 04:30 | 71 | 37 |  |  | 43462.1875 | 55 | 52
2018-12-28 05:00 | 72 | 37 |  |  | 43462.2083 | 55 | 52
2018-12-28 05:30 | 73 | 36 |  |  | 43462.2292 | 55 | 52
2018-12-28 06:00 | 70 | 34 |  |  | 43462.25 | 54 | 51
2018-12-28 06:30 | 68 | 35 |  |  | 43462.2708 | 56 | 55
2018-12-28 07:00 | 42 | 37 |  |  | 43462.2917 | 59 | 59
2018-12-28 07:30 | 40 | 37 |  |  | 43462.3125 | 61 | 61
2018-12-28 08:00 | 41 | 39 |  |  | 43462.3333 | 64 | 63
2018-12-28 08:30 | 44 | 42 |  |  | 43462.3542 | 68 | 67
2018-12-28 09:00 | 46 | 43 |  |  | 43462.375 | 68 | 67
2018-12-28 09:30 | 46 | 42 |  |  | 43462.3958 | 67 | 66
2018-12-28 10:00 | 48 | 44 |  |  | 43462.4167 | 67 | 66
2018-12-28 10:30 | 48 | 44 |  |  | 43462.4375 | 66 | 65
2018-12-28 11:00 | 46 | 42 |  |  | 43462.4583 | 65 | 64
2018-12-28 11:30 | 47 | 44 |  |  | 43462.4792 | 65 | 64
2018-12-28 12:00 | 47 | 43 |  |  | 43462.5 | 64 | 63
2018-12-28 12:30 | 47 | 44 |  |  | 43462.5208 | 63 | 63
2018-12-28 13:00 | 47 | 44 |  |  | 43462.5417 | 64 | 64
2018-12-28 13:30 | 49 | 46 |  |  | 43462.5625 | 66 | 66
2018-12-28 14:00 | 49 | 47 |  |  | 43462.5833 | 66 | 65
2018-12-28 14:30 | 49 | 47 |  |  | 43462.6042 | 66 | 66
2018-12-28 15:00 | 49 | 47 |  |  | 43462.625 | 67 | 67
2018-12-28 15:30 | 51 | 49 |  |  | 43462.6458 | 69 | 69
2018-12-28 16:00 | 54 | 52 |  |  | 43462.6667 | 73 | 73
2018-12-28 16:30 | 56 | 54 |  |  | 43462.6875 | 76 | 76
2018-12-28 17:00 | 58 | 56 |  |  | 43462.7083 | 79 | 79
2018-12-28 17:30 | 59 | 57 |  |  | 43462.7292 | 79 | 79
2018-12-28 18:00 | 60 | 57 |  |  | 43462.75 | 79 | 78
2018-12-28 18:30 | 60 | 57 |  |  | 43462.7708 | 77 | 76
2018-12-28 19:00 | 62 | 58 |  |  | 43462.7917 | 79 | 78
2018-12-28 19:30 | 62 | 59 |  |  | 43462.8125 | 80 | 79
2018-12-28 20:00 | 65 | 61 |  |  | 43462.8333 | 81 | 80
2018-12-28 20:30 | 64 | 62 |  |  | 43462.8542 | 80 | 80
2018-12-28 21:00 | 60 | 58 |  |  | 43462.875 | 76 | 76
2018-12-28 21:30 | 58 | 55 |  |  | 43462.8958 | 73 | 73
2018-12-28 22:00 | 57 | 54 |  |  | 43462.9167 | 74 | 73
2018-12-28 22:30 | 59 | 55 |  |  | 43462.9375 | 76 | 75
2018-12-28 23:00 | 60 | 56 |  |  | 43462.9583 | 74 | 73
2018-12-28 23:30 | 57 | 52 |  |  | 43462.9792 | 71 | 70
2018-12-29 | 53 | 46 |  |  | 43463 | 65 | 63
2018-12-29 00:30 | 48 | 40 |  |  | 43463.0208 | 60 | 57
2018-12-29 01:00 | 47 | 38 |  |  | 43463.0417 | 57 | 54
2018-12-29 01:30 | 47 | 38 |  |  | 43463.0625 | 56 | 53
2018-12-29 02:00 | 47 | 38 |  |  | 43463.0833 | 57 | 54
2018-12-29 02:30 | 48 | 39 |  |  | 43463.1042 | 57 | 54
2018-12-29 03:00 | 48 | 39 |  |  | 43463.125 | 58 | 54
2018-12-29 03:30 | 48 | 39 |  |  | 43463.1458 | 57 | 53
2018-12-29 04:00 | 47 | 38 |  |  | 43463.1667 | 56 | 52
2018-12-29 04:30 | 47 | 39 |  |  | 43463.1875 | 55 | 53
2018-12-29 05:00 | 47 | 39 |  |  | 43463.2083 | 55 | 53
2018-12-29 05:30 | 46 | 38 |  |  | 43463.2292 | 53 | 51
2018-12-29 06:00 | 42 | 33 |  |  | 43463.25 | 51 | 49
2018-12-29 06:30 | 41 | 32 |  |  | 43463.2708 | 50 | 48
2018-12-29 07:00 | 41 | 32 |  |  | 43463.2917 | 52 | 50
2018-12-29 07:30 | 43 | 35 |  |  | 43463.3125 | 54 | 53
2018-12-29 08:00 | 41 | 34 |  |  | 43463.3333 | 53 | 52
2018-12-29 08:30 | 40 | 33 |  |  | 43463.3542 | 53 | 53
2018-12-29 09:00 | 39 | 33 |  |  | 43463.375 | 57 | 57
2018-12-29 09:30 | 38 | 33 |  |  | 43463.3958 | 53 | 52
2018-12-29 10:00 | 38 | 34 |  |  | 43463.4167 | 52 | 52
2018-12-29 10:30 | 38 | 33 |  |  | 43463.4375 | 51 | 51
2018-12-29 11:00 | 41 | 37 |  |  | 43463.4583 | 54 | 54
2018-12-29 11:30 | 40 | 36 |  |  | 43463.4792 | 50 | 50
2018-12-29 12:00 | 38 | 35 |  |  | 43463.5 | 51 | 51
2018-12-29 12:30 | 39 | 36 |  |  | 43463.5208 | 53 | 52
2018-12-29 13:00 | 40 | 36 |  |  | 43463.5417 | 54 | 54
2018-12-29 13:30 | 42 | 39 |  |  | 43463.5625 | 56 | 56
2018-12-29 14:00 | 45 | 42 |  |  | 43463.5833 | 58 | 58
2018-12-29 14:30 | 48 | 45 |  |  | 43463.6042 | 60 | 60
2018-12-29 15:00 | 50 | 48 |  |  | 43463.625 | 62 | 62
2018-12-29 15:30 | 54 | 50 |  |  | 43463.6458 | 67 | 67
2018-12-29 16:00 | 58 | 54 |  |  | 43463.6667 | 70 | 70
2018-12-29 16:30 | 58 | 55 |  |  | 43463.6875 | 71 | 70
2018-12-29 17:00 | 61 | 58 |  |  | 43463.7083 | 74 | 74
2018-12-29 17:30 | 63 | 60 |  |  | 43463.7292 | 76 | 76
2018-12-29 18:00 | 63 | 59 |  |  | 43463.75 | 77 | 76
2018-12-29 18:30 | 65 | 60 |  |  | 43463.7708 | 78 | 78
2018-12-29 19:00 | 68 | 63 |  |  | 43463.7917 | 82 | 81
2018-12-29 19:30 | 69 | 65 |  |  | 43463.8125 | 84 | 83
2018-12-29 20:00 | 70 | 65 |  |  | 43463.8333 | 84 | 84
2018-12-29 20:30 | 69 | 65 |  |  | 43463.8542 | 84 | 84
2018-12-29 21:00 | 65 | 62 |  |  | 43463.875 | 81 | 80
2018-12-29 21:30 | 63 | 60 |  |  | 43463.8958 | 78 | 78
2018-12-29 22:00 | 63 | 60 |  |  | 43463.9167 | 77 | 77
2018-12-29 22:30 | 60 | 57 |  |  | 43463.9375 | 75 | 74
2018-12-29 23:00 | 60 | 56 |  |  | 43463.9583 | 73 | 73
2018-12-29 23:30 | 60 | 56 |  |  | 43463.9792 | 72 | 72
2018-12-30 | 56 | 51 |  |  | 43464 | 68 | 67
2018-12-30 00:30 | 52 | 47 |  |  | 43464.0208 | 63 | 63
2018-12-30 01:00 | 49 | 43 |  |  | 43464.0417 | 59 | 58
2018-12-30 01:30 | 48 | 42 |  |  | 43464.0625 | 59 | 58
2018-12-30 02:00 | 48 | 41 |  |  | 43464.0833 | 57 | 56
2018-12-30 02:30 | 48 | 41 |  |  | 43464.1042 | 57 | 56
2018-12-30 03:00 | 47 | 40 |  |  | 43464.125 | 56 | 55
2018-12-30 03:30 | 48 | 41 |  |  | 43464.1458 | 57 | 55
2018-12-30 04:00 | 48 | 41 |  |  | 43464.1667 | 57 | 55
2018-12-30 04:30 | 49 | 41 |  |  | 43464.1875 | 58 | 56
2018-12-30 05:00 | 49 | 41 |  |  | 43464.2083 | 58 | 56
2018-12-30 05:30 | 48 | 39 |  |  | 43464.2292 | 56 | 54
2018-12-30 06:00 | 47 | 38 |  |  | 43464.25 | 56 | 54
2018-12-30 06:30 | 46 | 37 |  |  | 43464.2708 | 54 | 52
2018-12-30 07:00 | 45 | 36 |  |  | 43464.2917 | 56 | 54
2018-12-30 07:30 | 44 | 37 |  |  | 43464.3125 | 57 | 56
2018-12-30 08:00 | 45 | 38 |  |  | 43464.3333 | 56 | 55
2018-12-30 08:30 | 45 | 40 |  |  | 43464.3542 | 56 | 55
2018-12-30 09:00 | 43 | 38 |  |  | 43464.375 | 56 | 56
2018-12-30 09:30 | 41 | 37 |  |  | 43464.3958 | 55 | 55
2018-12-30 10:00 | 40 | 37 |  |  | 43464.4167 | 55 | 55
2018-12-30 10:30 | 41 | 38 |  |  | 43464.4375 | 55 | 55
2018-12-30 11:00 | 42 | 38 |  |  | 43464.4583 | 57 | 57
2018-12-30 11:30 | 43 | 40 |  |  | 43464.4792 | 55 | 55
2018-12-30 12:00 | 41 | 38 |  |  | 43464.5 | 55 | 55
2018-12-30 12:30 | 41 | 39 |  |  | 43464.5208 | 55 | 55
2018-12-30 13:00 | 43 | 39 |  |  | 43464.5417 | 54 | 54
2018-12-30 13:30 | 45 | 40 |  |  | 43464.5625 | 55 | 54
2018-12-30 14:00 | 45 | 40 |  |  | 43464.5833 | 55 | 54
2018-12-30 14:30 | 48 | 43 |  |  | 43464.6042 | 57 | 56
2018-12-30 15:00 | 49 | 44 |  |  | 43464.625 | 59 | 58
2018-12-30 15:30 | 51 | 47 |  |  | 43464.6458 | 61 | 60
2018-12-30 16:00 | 56 | 53 |  |  | 43464.6667 | 66 | 66
2018-12-30 16:30 | 59 | 56 |  |  | 43464.6875 | 70 | 69
2018-12-30 17:00 | 63 | 60 |  |  | 43464.7083 | 75 | 74
2018-12-30 17:30 | 66 | 62 |  |  | 43464.7292 | 77 | 76
2018-12-30 18:00 | 67 | 62 |  |  | 43464.75 | 78 | 77
2018-12-30 18:30 | 69 | 64 |  |  | 43464.7708 | 80 | 79
2018-12-30 19:00 | 70 | 65 |  |  | 43464.7917 | 81 | 81
2018-12-30 19:30 | 71 | 67 |  |  | 43464.8125 | 84 | 83
2018-12-30 20:00 | 70 | 66 |  |  | 43464.8333 | 83 | 83
2018-12-30 20:30 | 71 | 66 |  |  | 43464.8542 | 84 | 83
2018-12-30 21:00 | 68 | 63 |  |  | 43464.875 | 80 | 80
2018-12-30 21:30 | 63 | 60 |  |  | 43464.8958 | 77 | 77
2018-12-30 22:00 | 62 | 58 |  |  | 43464.9167 | 77 | 76
2018-12-30 22:30 | 61 | 57 |  |  | 43464.9375 | 76 | 76
2018-12-30 23:00 | 59 | 55 |  |  | 43464.9583 | 73 | 73
2018-12-30 23:30 | 56 | 51 |  |  | 43464.9792 | 69 | 69
2018-12-31 | 52 | 47 |  |  | 43465 | 64 | 64
2018-12-31 00:30 | 49 | 43 |  |  | 43465.0208 | 60 | 59
2018-12-31 01:00 | 48 | 41 |  |  | 43465.0417 | 57 | 56
2018-12-31 01:30 | 46 | 39 |  |  | 43465.0625 | 56 | 55
2018-12-31 02:00 | 46 | 39 |  |  | 43465.0833 | 56 | 55
2018-12-31 02:30 | 46 | 39 |  |  | 43465.1042 | 55 | 54
2018-12-31 03:00 | 47 | 39 |  |  | 43465.125 | 55 | 54
2018-12-31 03:30 | 47 | 39 |  |  | 43465.1458 | 55 | 53
2018-12-31 04:00 | 47 | 40 |  |  | 43465.1667 | 55 | 53
2018-12-31 04:30 | 47 | 40 |  |  | 43465.1875 | 55 | 54
2018-12-31 05:00 | 46 | 38 |  |  | 43465.2083 | 55 | 53
2018-12-31 05:30 | 46 | 38 |  |  | 43465.2292 | 54 | 53
2018-12-31 06:00 | 46 | 38 |  |  | 43465.25 | 56 | 55
2018-12-31 06:30 | 47 | 41 |  |  | 43465.2708 | 61 | 60
2018-12-31 07:00 | 47 | 42 |  |  | 43465.2917 | 64 | 64
2018-12-31 07:30 | 46 | 43 |  |  | 43465.3125 | 67 | 67
2018-12-31 08:00 | 50 | 46 |  |  | 43465.3333 | 72 | 72
2018-12-31 08:30 | 52 | 49 |  |  | 43465.3542 | 73 | 72
2018-12-31 09:00 | 52 | 49 |  |  | 43465.375 | 72 | 72
2018-12-31 09:30 | 51 | 47 |  |  | 43465.3958 | 72 | 71
2018-12-31 10:00 | 51 | 48 |  |  | 43465.4167 | 72 | 71
2018-12-31 10:30 | 55 | 51 |  |  | 43465.4375 | 74 | 73
2018-12-31 11:00 | 52 | 49 |  |  | 43465.4583 | 71 | 71
2018-12-31 11:30 | 51 | 49 |  |  | 43465.4792 | 68 | 68
2018-12-31 12:00 | 50 | 48 |  |  | 43465.5 | 70 | 69
2018-12-31 12:30 | 51 | 49 |  |  | 43465.5208 | 69 | 69
2018-12-31 13:00 | 53 | 52 |  |  | 43465.5417 | 70 | 70
2018-12-31 13:30 | 54 | 53 |  |  | 43465.5625 | 72 | 72
2018-12-31 14:00 | 57 | 56 |  |  | 43465.5833 | 74 | 73
2018-12-31 14:30 | 58 | 57 |  |  | 43465.6042 | 75 | 75
2018-12-31 15:00 | 62 | 60 |  |  | 43465.625 | 79 | 79
2018-12-31 15:30 | 65 | 64 |  |  | 43465.6458 | 83 | 83
2018-12-31 16:00 | 70 | 69 |  |  | 43465.6667 | 88 | 88
2018-12-31 16:30 | 75 | 74 |  |  | 43465.6875 | 93 | 93
2018-12-31 17:00 | 79 | 77 |  |  | 43465.7083 | 97 | 97
2018-12-31 17:30 | 80 | 79 |  |  | 43465.7292 | 99 | 98
2018-12-31 18:00 | 80 | 77 |  |  | 43465.75 | 97 | 96
2018-12-31 18:30 | 76 | 74 |  |  | 43465.7708 | 92 | 91
2018-12-31 19:00 | 75 | 73 |  |  | 43465.7917 | 92 | 92
2018-12-31 19:30 | 76 | 73 |  |  | 43465.8125 | 92 | 91
2018-12-31 20:00 | 74 | 71 |  |  | 43465.8333 | 89 | 89
2018-12-31 20:30 | 71 | 69 |  |  | 43465.8542 | 87 | 86
2018-12-31 21:00 | 66 | 64 |  |  | 43465.875 | 82 | 81
2018-12-31 21:30 | 62 | 59 |  |  | 43465.8958 | 79 | 78
2018-12-31 22:00 | 63 | 60 |  |  | 43465.9167 | 79 | 78
2018-12-31 22:30 | 63 | 60 |  |  | 43465.9375 | 80 | 79
2018-12-31 23:00 | 64 | 62 |  |  | 43465.9583 | 79 | 78
2018-12-31 23:30 | 62 | 59 |  |  | 43465.9792 | 77 | 76
2019-01-01 | 58 | 54 |  |  | 43466 | 73 | 71
2019-01-01 00:30 | 57 | 51 |  |  | 43466.0208 | 69 | 67
2019-01-01 01:00 | 56 | 50 |  |  | 43466.0417 | 67 | 64
2019-01-01 01:30 | 55 | 48 |  |  | 43466.0625 | 66 | 63
2019-01-01 02:00 | 54 | 47 |  |  | 43466.0833 | 65 | 62
2019-01-01 02:30 | 53 | 47 |  |  | 43466.1042 | 63 | 61
2019-01-01 03:00 | 51 | 45 |  |  | 43466.125 | 62 | 60
2019-01-01 03:30 | 51 | 45 |  |  | 43466.1458 | 62 | 60
2019-01-01 04:00 | 51 | 45 |  |  | 43466.1667 | 63 | 60
2019-01-01 04:30 | 52 | 45 |  |  | 43466.1875 | 63 | 61
2019-01-01 05:00 | 50 | 45 |  |  | 43466.2083 | 64 | 60
2019-01-01 05:30 | 45 | 43 |  |  | 43466.2292 | 64 | 58
2019-01-01 06:00 | 43 | 41 |  |  | 43466.25 | 63 | 56
2019-01-01 06:30 | 43 | 41 |  |  | 43466.2708 | 64 | 58
2019-01-01 07:00 | 43 | 40 |  |  | 43466.2917 | 63 | 58
2019-01-01 07:30 | 42 | 41 |  |  | 43466.3125 | 64 | 60
2019-01-01 08:00 | 43 | 42 |  |  | 43466.3333 | 64 | 61
2019-01-01 08:30 | 44 | 43 |  |  | 43466.3542 | 66 | 63
2019-01-01 09:00 | 43 | 42 |  |  | 43466.375 | 66 | 64
2019-01-01 09:30 | 44 | 44 |  |  | 43466.3958 | 64 | 62
2019-01-01 10:00 | 45 | 45 |  |  | 43466.4167 | 64 | 62
2019-01-01 10:30 | 46 | 46 |  |  | 43466.4375 | 64 | 62
2019-01-01 11:00 | 46 | 46 |  |  | 43466.4583 | 63 | 61
2019-01-01 11:30 | 46 | 46 |  |  | 43466.4792 | 63 | 61
2019-01-01 12:00 | 45 | 45 |  |  | 43466.5 | 62 | 60
2019-01-01 12:30 | 45 | 45 |  |  | 43466.5208 | 61 | 59
2019-01-01 13:00 | 45 | 45 |  |  | 43466.5417 | 62 | 60
2019-01-01 13:30 | 46 | 46 |  |  | 43466.5625 | 63 | 61
2019-01-01 14:00 | 48 | 48 |  |  | 43466.5833 | 64 | 62
2019-01-01 14:30 | 50 | 50 |  |  | 43466.6042 | 66 | 64
2019-01-01 15:00 | 53 | 53 |  |  | 43466.625 | 68 | 67
2019-01-01 15:30 | 56 | 56 |  |  | 43466.6458 | 72 | 70
2019-01-01 16:00 | 64 | 64 |  |  | 43466.6667 | 78 | 77
2019-01-01 16:30 | 61 | 61 |  |  | 43466.6875 | 79 | 78
2019-01-01 17:00 | 64 | 64 |  |  | 43466.7083 | 82 | 81
2019-01-01 17:30 | 69 | 69 |  |  | 43466.7292 | 87 | 86
2019-01-01 18:00 | 69 | 69 |  |  | 43466.75 | 89 | 87
2019-01-01 18:30 | 68 | 68 |  |  | 43466.7708 | 87 | 85
2019-01-01 19:00 | 69 | 69 |  |  | 43466.7917 | 88 | 86
2019-01-01 19:30 | 70 | 70 |  |  | 43466.8125 | 90 | 88
2019-01-01 20:00 | 70 | 70 |  |  | 43466.8333 | 90 | 88
2019-01-01 20:30 | 68 | 68 |  |  | 43466.8542 | 88 | 86
2019-01-01 21:00 | 65 | 65 |  |  | 43466.875 | 84 | 82
2019-01-01 21:30 | 62 | 61 |  |  | 43466.8958 | 81 | 79
2019-01-01 22:00 | 61 | 60 |  |  | 43466.9167 | 81 | 78
2019-01-01 22:30 | 61 | 60 |  |  | 43466.9375 | 82 | 78
2019-01-01 23:00 | 60 | 59 |  |  | 43466.9583 | 79 | 75
2019-01-01 23:30 | 58 | 56 |  |  | 43466.9792 | 77 | 73
2019-01-02 | 53 | 51 |  |  | 43467 | 71 | 67
2019-01-02 00:30 | 50 | 49 |  |  | 43467.0208 | 68 | 64
2019-01-02 01:00 | 48 | 47 |  |  | 43467.0417 | 66 | 60
2019-01-02 01:30 | 47 | 46 |  |  | 43467.0625 | 65 | 59
2019-01-02 02:00 | 48 | 46 |  |  | 43467.0833 | 65 | 59
2019-01-02 02:30 | 47 | 45 |  |  | 43467.1042 | 64 | 57
2019-01-02 03:00 | 45 | 43 |  |  | 43467.125 | 63 | 56
2019-01-02 03:30 | 45 | 43 |  |  | 43467.1458 | 63 | 56
2019-01-02 04:00 | 46 | 44 |  |  | 43467.1667 | 63 | 57
2019-01-02 04:30 | 47 | 45 |  |  | 43467.1875 | 64 | 57
2019-01-02 05:00 | 46 | 44 |  |  | 43467.2083 | 64 | 57
2019-01-02 05:30 | 45 | 43 |  |  | 43467.2292 | 63 | 57
2019-01-02 06:00 | 45 | 43 |  |  | 43467.25 | 64 | 58
2019-01-02 06:30 | 49 | 48 |  |  | 43467.2708 | 69 | 65
2019-01-02 07:00 | 51 | 51 |  |  | 43467.2917 | 73 | 71
2019-01-02 07:30 | 55 | 55 |  |  | 43467.3125 | 79 | 77
2019-01-02 08:00 | 58 | 58 |  |  | 43467.3333 | 84 | 81
2019-01-02 08:30 | 63 | 63 |  |  | 43467.3542 | 89 | 87
2019-01-02 09:00 | 62 | 62 |  |  | 43467.375 | 90 | 87
2019-01-02 09:30 | 64 | 63 |  |  | 43467.3958 | 90 | 87
2019-01-02 10:00 | 61 | 61 |  |  | 43467.4167 | 88 | 86
2019-01-02 10:30 | 61 | 61 |  |  | 43467.4375 | 86 | 85
2019-01-02 11:00 | 62 | 62 |  |  | 43467.4583 | 84 | 83
2019-01-02 11:30 | 64 | 64 |  |  | 43467.4792 | 85 | 83
2019-01-02 12:00 | 65 | 65 |  |  | 43467.5 | 86 | 84
2019-01-02 12:30 | 68 | 66 |  |  | 43467.5208 | 93 | 83
2019-01-02 13:00 | 67 | 65 |  |  | 43467.5417 | 95 | 85
2019-01-02 13:30 | 69 | 66 |  |  | 43467.5625 | 99 | 88
2019-01-02 14:00 | 72 | 69 |  |  | 43467.5833 | 101 | 89
2019-01-02 14:30 | 73 | 70 |  |  | 43467.6042 | 103 | 90
2019-01-02 15:00 | 76 | 73 |  |  | 43467.625 | 107 | 95
2019-01-02 15:30 | 79 | 76 |  |  | 43467.6458 | 110 | 98
2019-01-02 16:00 | 83 | 80 |  |  | 43467.6667 | 114 | 103
2019-01-02 16:30 | 85 | 83 |  |  | 43467.6875 | 115 | 104
2019-01-02 17:00 | 86 | 84 |  |  | 43467.7083 | 117 | 105
2019-01-02 17:30 | 89 | 86 |  |  | 43467.7292 | 119 | 104
2019-01-02 18:00 | 89 | 85 |  |  | 43467.75 | 117 | 102
2019-01-02 18:30 | 84 | 82 |  |  | 43467.7708 | 107 | 99
2019-01-02 19:00 | 85 | 83 |  |  | 43467.7917 | 108 | 100
2019-01-02 19:30 | 86 | 85 |  |  | 43467.8125 | 109 | 101
2019-01-02 20:00 | 83 | 83 |  |  | 43467.8333 | 99 | 98
2019-01-02 20:30 | 80 | 80 |  |  | 43467.8542 | 96 | 95
2019-01-02 21:00 | 77 | 77 |  |  | 43467.875 | 93 | 91
2019-01-02 21:30 | 73 | 73 |  |  | 43467.8958 | 88 | 87
2019-01-02 22:00 | 72 | 71 |  |  | 43467.9167 | 86 | 85
2019-01-02 22:30 | 69 | 68 |  |  | 43467.9375 | 85 | 83
2019-01-02 23:00 | 64 | 63 |  |  | 43467.9583 | 80 | 77
2019-01-02 23:30 | 60 | 60 |  |  | 43467.9792 | 77 | 75
2019-01-03 | 56 | 56 |  |  | 43468 | 73 | 70
2019-01-03 00:30 | 55 | 54 |  |  | 43468.0208 | 70 | 67
2019-01-03 01:00 | 51 | 51 |  |  | 43468.0417 | 67 | 63
2019-01-03 01:30 | 49 | 48 |  |  | 43468.0625 | 65 | 60
2019-01-03 02:00 | 49 | 48 |  |  | 43468.0833 | 64 | 60
2019-01-03 02:30 | 48 | 47 |  |  | 43468.1042 | 63 | 59
2019-01-03 03:00 | 48 | 47 |  |  | 43468.125 | 63 | 58
2019-01-03 03:30 | 48 | 47 |  |  | 43468.1458 | 63 | 58
2019-01-03 04:00 | 48 | 47 |  |  | 43468.1667 | 63 | 59
2019-01-03 04:30 | 50 | 49 |  |  | 43468.1875 | 65 | 60
2019-01-03 05:00 | 50 | 49 |  |  | 43468.2083 | 65 | 60
2019-01-03 05:30 | 51 | 50 |  |  | 43468.2292 | 66 | 62
2019-01-03 06:00 | 50 | 50 |  |  | 43468.25 | 66 | 63
2019-01-03 06:30 | 54 | 54 |  |  | 43468.2708 | 71 | 68
2019-01-03 07:00 | 54 | 54 |  |  | 43468.2917 | 75 | 73
2019-01-03 07:30 | 62 | 62 |  |  | 43468.3125 | 84 | 83
2019-01-03 08:00 | 64 | 64 |  |  | 43468.3333 | 85 | 84
2019-01-03 08:30 | 64 | 64 |  |  | 43468.3542 | 84 | 83
2019-01-03 09:00 | 63 | 63 |  |  | 43468.375 | 86 | 86
2019-01-03 09:30 | 66 | 66 |  |  | 43468.3958 | 92 | 90
2019-01-03 10:00 | 70 | 70 |  |  | 43468.4167 | 96 | 95
2019-01-03 10:30 | 71 | 71 |  |  | 43468.4375 | 97 | 96
2019-01-03 11:00 | 74 | 74 |  |  | 43468.4583 | 95 | 94
2019-01-03 11:30 | 75 | 75 |  |  | 43468.4792 | 96 | 94
2019-01-03 12:00 | 75 | 75 |  |  | 43468.5 | 94 | 93
2019-01-03 12:30 | 67 | 67 |  |  | 43468.5208 | 90 | 88
2019-01-03 13:00 | 65 | 65 |  |  | 43468.5417 | 87 | 85
2019-01-03 13:30 | 69 | 69 |  |  | 43468.5625 | 91 | 90
2019-01-03 14:00 | 69 | 69 |  |  | 43468.5833 | 87 | 86
2019-01-03 14:30 | 73 | 73 |  |  | 43468.6042 | 91 | 90
2019-01-03 15:00 | 76 | 75 |  |  | 43468.625 | 96 | 95
2019-01-03 15:30 | 77 | 76 |  |  | 43468.6458 | 94 | 93
2019-01-03 16:00 | 74 | 73 |  |  | 43468.6667 | 90 | 89
2019-01-03 16:30 | 76 | 76 |  |  | 43468.6875 | 94 | 91
2019-01-03 17:00 | 81 | 81 |  |  | 43468.7083 | 98 | 96
2019-01-03 17:30 | 84 | 84 |  |  | 43468.7292 | 99 | 97
2019-01-03 18:00 | 85 | 85 |  |  | 43468.75 | 101 | 98
2019-01-03 18:30 | 84 | 84 |  |  | 43468.7708 | 100 | 95
2019-01-03 19:00 | 87 | 87 |  |  | 43468.7917 | 103 | 98
2019-01-03 19:30 | 87 | 87 |  |  | 43468.8125 | 103 | 99
2019-01-03 20:00 | 87 | 87 |  |  | 43468.8333 | 102 | 98
2019-01-03 20:30 | 86 | 86 |  |  | 43468.8542 | 102 | 97
2019-01-03 21:00 | 86 | 86 |  |  | 43468.875 | 101 | 96
2019-01-03 21:30 | 80 | 80 |  |  | 43468.8958 | 95 | 90
2019-01-03 22:00 | 78 | 78 |  |  | 43468.9167 | 94 | 88
2019-01-03 22:30 | 73 | 73 |  |  | 43468.9375 | 89 | 86
2019-01-03 23:00 | 70 | 70 |  |  | 43468.9583 | 84 | 82
2019-01-03 23:30 | 67 | 66 |  |  | 43468.9792 | 82 | 79
2019-01-04 | 63 | 62 |  |  | 43469 | 78 | 75
2019-01-04 00:30 | 59 | 59 |  |  | 43469.0208 | 74 | 70
2019-01-04 01:00 | 55 | 54 |  |  | 43469.0417 | 69 | 65
2019-01-04 01:30 | 53 | 53 |  |  | 43469.0625 | 68 | 63
2019-01-04 02:00 | 53 | 52 |  |  | 43469.0833 | 68 | 63
2019-01-04 02:30 | 52 | 52 |  |  | 43469.1042 | 68 | 64
2019-01-04 03:00 | 53 | 52 |  |  | 43469.125 | 68 | 64
2019-01-04 03:30 | 52 | 52 |  |  | 43469.1458 | 67 | 63
2019-01-04 04:00 | 52 | 52 |  |  | 43469.1667 | 67 | 63
2019-01-04 04:30 | 53 | 52 |  |  | 43469.1875 | 67 | 63
2019-01-04 05:00 | 54 | 54 |  |  | 43469.2083 | 68 | 64
2019-01-04 05:30 | 52 | 51 |  |  | 43469.2292 | 68 | 63
2019-01-04 06:00 | 52 | 51 |  |  | 43469.25 | 70 | 66
2019-01-04 06:30 | 53 | 53 |  |  | 43469.2708 | 72 | 71
2019-01-04 07:00 | 57 | 57 |  |  | 43469.2917 | 78 | 77
2019-01-04 07:30 | 62 | 62 |  |  | 43469.3125 | 85 | 85
2019-01-04 08:00 | 64 | 64 |  |  | 43469.3333 | 88 | 87
2019-01-04 08:30 | 65 | 65 |  |  | 43469.3542 | 88 | 87
2019-01-04 09:00 | 66 | 66 |  |  | 43469.375 | 87 | 86
2019-01-04 09:30 | 64 | 64 |  |  | 43469.3958 | 83 | 82
2019-01-04 10:00 | 62 | 62 |  |  | 43469.4167 | 78 | 77
2019-01-04 10:30 | 60 | 60 |  |  | 43469.4375 | 76 | 75
2019-01-04 11:00 | 59 | 59 |  |  | 43469.4583 | 76 | 75
2019-01-04 11:30 | 58 | 58 |  |  | 43469.4792 | 76 | 75
2019-01-04 12:00 | 60 | 60 |  |  | 43469.5 | 79 | 78
2019-01-04 12:30 | 61 | 61 |  |  | 43469.5208 | 80 | 79
2019-01-04 13:00 | 65 | 65 |  |  | 43469.5417 | 82 | 81
2019-01-04 13:30 | 68 | 68 |  |  | 43469.5625 | 85 | 84
2019-01-04 14:00 | 69 | 69 |  |  | 43469.5833 | 85 | 85
2019-01-04 14:30 | 70 | 69 |  |  | 43469.6042 | 87 | 86
2019-01-04 15:00 | 72 | 72 |  |  | 43469.625 | 90 | 89
2019-01-04 15:30 | 74 | 74 |  |  | 43469.6458 | 91 | 91
2019-01-04 16:00 | 79 | 78 |  |  | 43469.6667 | 96 | 96
2019-01-04 16:30 | 82 | 82 |  |  | 43469.6875 | 100 | 99
2019-01-04 17:00 | 85 | 85 |  |  | 43469.7083 | 103 | 102
2019-01-04 17:30 | 87 | 87 |  |  | 43469.7292 | 103 | 102
2019-01-04 18:00 | 85 | 85 |  |  | 43469.75 | 102 | 100
2019-01-04 18:30 | 82 | 82 |  |  | 43469.7708 | 99 | 96
2019-01-04 19:00 | 81 | 81 |  |  | 43469.7917 | 98 | 95
2019-01-04 19:30 | 82 | 82 |  |  | 43469.8125 | 100 | 97
2019-01-04 20:00 | 82 | 82 |  |  | 43469.8333 | 99 | 96
2019-01-04 20:30 | 81 | 81 |  |  | 43469.8542 | 98 | 96
2019-01-04 21:00 | 79 | 79 |  |  | 43469.875 | 95 | 94
2019-01-04 21:30 | 76 | 76 |  |  | 43469.8958 | 92 | 91
2019-01-04 22:00 | 72 | 72 |  |  | 43469.9167 | 89 | 88
2019-01-04 22:30 | 68 | 68 |  |  | 43469.9375 | 87 | 86
2019-01-04 23:00 | 65 | 65 |  |  | 43469.9583 | 83 | 81
2019-01-04 23:30 | 60 | 60 |  |  | 43469.9792 | 78 | 76
2019-01-05 | 53 | 53 |  |  | 43470 | 72 | 70
2019-01-05 00:30 | 52 | 52 |  |  | 43470.0208 | 69 | 67
2019-01-05 01:00 | 51 | 51 |  |  | 43470.0417 | 69 | 66
2019-01-05 01:30 | 51 | 51 |  |  | 43470.0625 | 68 | 65
2019-01-05 02:00 | 49 | 49 |  |  | 43470.0833 | 67 | 63
2019-01-05 02:30 | 48 | 47 |  |  | 43470.1042 | 65 | 61
2019-01-05 03:00 | 48 | 47 |  |  | 43470.125 | 65 | 60
2019-01-05 03:30 | 47 | 46 |  |  | 43470.1458 | 63 | 59
2019-01-05 04:00 | 47 | 46 |  |  | 43470.1667 | 63 | 58
2019-01-05 04:30 | 48 | 47 |  |  | 43470.1875 | 62 | 58
2019-01-05 05:00 | 48 | 46 |  |  | 43470.2083 | 62 | 58
2019-01-05 05:30 | 44 | 43 |  |  | 43470.2292 | 60 | 56
2019-01-05 06:00 | 45 | 44 |  |  | 43470.25 | 60 | 56
2019-01-05 06:30 | 44 | 44 |  |  | 43470.2708 | 60 | 57
2019-01-05 07:00 | 44 | 44 |  |  | 43470.2917 | 60 | 58
2019-01-05 07:30 | 43 | 43 |  |  | 43470.3125 | 60 | 58
2019-01-05 08:00 | 43 | 43 |  |  | 43470.3333 | 60 | 59
2019-01-05 08:30 | 45 | 45 |  |  | 43470.3542 | 65 | 64
2019-01-05 09:00 | 45 | 45 |  |  | 43470.375 | 66 | 65
2019-01-05 09:30 | 47 | 47 |  |  | 43470.3958 | 67 | 66
2019-01-05 10:00 | 52 | 52 |  |  | 43470.4167 | 69 | 69
2019-01-05 10:30 | 52 | 52 |  |  | 43470.4375 | 69 | 69
2019-01-05 11:00 | 54 | 54 |  |  | 43470.4583 | 72 | 71
2019-01-05 11:30 | 53 | 53 |  |  | 43470.4792 | 70 | 70
2019-01-05 12:00 | 53 | 53 |  |  | 43470.5 | 66 | 65
2019-01-05 12:30 | 53 | 52 |  |  | 43470.5208 | 65 | 65
2019-01-05 13:00 | 53 | 53 |  |  | 43470.5417 | 71 | 70
2019-01-05 13:30 | 57 | 57 |  |  | 43470.5625 | 74 | 72
2019-01-05 14:00 | 59 | 59 |  |  | 43470.5833 | 76 | 74
2019-01-05 14:30 | 64 | 64 |  |  | 43470.6042 | 73 | 71
2019-01-05 15:00 | 63 | 63 |  |  | 43470.625 | 75 | 73
2019-01-05 15:30 | 65 | 65 |  |  | 43470.6458 | 79 | 77
2019-01-05 16:00 | 67 | 67 |  |  | 43470.6667 | 82 | 80
2019-01-05 16:30 | 72 | 72 |  |  | 43470.6875 | 86 | 84
2019-01-05 17:00 | 76 | 75 |  |  | 43470.7083 | 93 | 92
2019-01-05 17:30 | 76 | 76 |  |  | 43470.7292 | 92 | 91
2019-01-05 18:00 | 75 | 75 |  |  | 43470.75 | 92 | 90
2019-01-05 18:30 | 76 | 76 |  |  | 43470.7708 | 92 | 90
2019-01-05 19:00 | 76 | 76 |  |  | 43470.7917 | 92 | 90
2019-01-05 19:30 | 77 | 77 |  |  | 43470.8125 | 94 | 92
2019-01-05 20:00 | 78 | 78 |  |  | 43470.8333 | 95 | 93
2019-01-05 20:30 | 75 | 75 |  |  | 43470.8542 | 92 | 91
2019-01-05 21:00 | 73 | 73 |  |  | 43470.875 | 90 | 89
2019-01-05 21:30 | 70 | 70 |  |  | 43470.8958 | 87 | 85
2019-01-05 22:00 | 67 | 67 |  |  | 43470.9167 | 85 | 83
2019-01-05 22:30 | 67 | 67 |  |  | 43470.9375 | 86 | 83
2019-01-05 23:00 | 67 | 67 |  |  | 43470.9583 | 84 | 81
2019-01-05 23:30 | 65 | 65 |  |  | 43470.9792 | 81 | 79
2019-01-06 | 62 | 62 |  |  | 43471 | 77 | 75
2019-01-06 00:30 | 59 | 59 |  |  | 43471.0208 | 74 | 71
2019-01-06 01:00 | 57 | 57 |  |  | 43471.0417 | 71 | 68
2019-01-06 01:30 | 55 | 54 |  |  | 43471.0625 | 68 | 65
2019-01-06 02:00 | 54 | 53 |  |  | 43471.0833 | 68 | 64
2019-01-06 02:30 | 53 | 53 |  |  | 43471.1042 | 67 | 63
2019-01-06 03:00 | 52 | 51 |  |  | 43471.125 | 67 | 63
2019-01-06 03:30 | 52 | 51 |  |  | 43471.1458 | 67 | 63
2019-01-06 04:00 | 51 | 50 |  |  | 43471.1667 | 67 | 62
2019-01-06 04:30 | 49 | 48 |  |  | 43471.1875 | 65 | 61
2019-01-06 05:00 | 49 | 48 |  |  | 43471.2083 | 65 | 61
2019-01-06 05:30 | 49 | 48 |  |  | 43471.2292 | 65 | 61
2019-01-06 06:00 | 49 | 48 |  |  | 43471.25 | 67 | 62
2019-01-06 06:30 | 49 | 48 |  |  | 43471.2708 | 67 | 62
2019-01-06 07:00 | 48 | 47 |  |  | 43471.2917 | 67 | 63
2019-01-06 07:30 | 49 | 47 |  |  | 43471.3125 | 69 | 66
2019-01-06 08:00 | 50 | 49 |  |  | 43471.3333 | 69 | 66
2019-01-06 08:30 | 49 | 49 |  |  | 43471.3542 | 68 | 65
2019-01-06 09:00 | 53 | 53 |  |  | 43471.375 | 71 | 70
2019-01-06 09:30 | 55 | 55 |  |  | 43471.3958 | 72 | 71
2019-01-06 10:00 | 56 | 56 |  |  | 43471.4167 | 73 | 72
2019-01-06 10:30 | 60 | 60 |  |  | 43471.4375 | 77 | 76
2019-01-06 11:00 | 63 | 62 |  |  | 43471.4583 | 77 | 75
2019-01-06 11:30 | 60 | 60 |  |  | 43471.4792 | 75 | 72
2019-01-06 12:00 | 61 | 61 |  |  | 43471.5 | 78 | 75
2019-01-06 12:30 | 65 | 65 |  |  | 43471.5208 | 80 | 77
2019-01-06 13:00 | 65 | 65 |  |  | 43471.5417 | 81 | 78
2019-01-06 13:30 | 69 | 69 |  |  | 43471.5625 | 84 | 82
2019-01-06 14:00 | 71 | 71 |  |  | 43471.5833 | 84 | 81
2019-01-06 14:30 | 74 | 74 |  |  | 43471.6042 | 86 | 83
2019-01-06 15:00 | 76 | 76 |  |  | 43471.625 | 89 | 86
2019-01-06 15:30 | 79 | 79 |  |  | 43471.6458 | 92 | 90
2019-01-06 16:00 | 80 | 80 |  |  | 43471.6667 | 93 | 91
2019-01-06 16:30 | 79 | 79 |  |  | 43471.6875 | 92 | 90
2019-01-06 17:00 | 80 | 80 |  |  | 43471.7083 | 96 | 94
2019-01-06 17:30 | 82 | 82 |  |  | 43471.7292 | 98 | 96
2019-01-06 18:00 | 85 | 85 |  |  | 43471.75 | 100 | 97
2019-01-06 18:30 | 85 | 85 |  |  | 43471.7708 | 100 | 97
2019-01-06 19:00 | 84 | 84 |  |  | 43471.7917 | 101 | 98
2019-01-06 19:30 | 86 | 86 |  |  | 43471.8125 | 103 | 100
2019-01-06 20:00 | 86 | 86 |  |  | 43471.8333 | 104 | 101
2019-01-06 20:30 | 83 | 83 |  |  | 43471.8542 | 100 | 98
2019-01-06 21:00 | 80 | 80 |  |  | 43471.875 | 96 | 95
2019-01-06 21:30 | 77 | 77 |  |  | 43471.8958 | 94 | 92
2019-01-06 22:00 | 77 | 77 |  |  | 43471.9167 | 93 | 92
2019-01-06 22:30 | 75 | 75 |  |  | 43471.9375 | 93 | 91
2019-01-06 23:00 | 73 | 73 |  |  | 43471.9583 | 89 | 87
2019-01-06 23:30 | 70 | 69 |  |  | 43471.9792 | 86 | 84
2019-01-07 | 65 | 65 |  |  | 43472 | 81 | 78
2019-01-07 00:30 | 62 | 61 |  |  | 43472.0208 | 77 | 74
2019-01-07 01:00 | 59 | 59 |  |  | 43472.0417 | 74 | 70
2019-01-07 01:30 | 58 | 57 |  |  | 43472.0625 | 72 | 68
2019-01-07 02:00 | 57 | 57 |  |  | 43472.0833 | 73 | 69
2019-01-07 02:30 | 56 | 55 |  |  | 43472.1042 | 71 | 66
2019-01-07 03:00 | 56 | 55 |  |  | 43472.125 | 70 | 66
2019-01-07 03:30 | 57 | 56 |  |  | 43472.1458 | 70 | 66
2019-01-07 04:00 | 56 | 55 |  |  | 43472.1667 | 70 | 65
2019-01-07 04:30 | 54 | 54 |  |  | 43472.1875 | 70 | 66
2019-01-07 05:00 | 54 | 54 |  |  | 43472.2083 | 70 | 67
2019-01-07 05:30 | 56 | 56 |  |  | 43472.2292 | 73 | 70
2019-01-07 06:00 | 60 | 59 |  |  | 43472.25 | 77 | 75
2019-01-07 06:30 | 66 | 66 |  |  | 43472.2708 | 86 | 84
2019-01-07 07:00 | 73 | 73 |  |  | 43472.2917 | 95 | 94
2019-01-07 07:30 | 81 | 81 |  |  | 43472.3125 | 106 | 106
2019-01-07 08:00 | 86 | 85 |  |  | 43472.3333 | 110 | 110
2019-01-07 08:30 | 85 | 84 |  |  | 43472.3542 | 111 | 111
2019-01-07 09:00 | 84 | 84 |  |  | 43472.375 | 110 | 110
2019-01-07 09:30 | 83 | 82 |  |  | 43472.3958 | 108 | 108
2019-01-07 10:00 | 81 | 81 |  |  | 43472.4167 | 107 | 107
2019-01-07 10:30 | 84 | 83 |  |  | 43472.4375 | 107 | 106
2019-01-07 11:00 | 85 | 84 |  |  | 43472.4583 | 108 | 108
2019-01-07 11:30 | 84 | 83 |  |  | 43472.4792 | 108 | 107
2019-01-07 12:00 | 86 | 85 |  |  | 43472.5 | 110 | 109
2019-01-07 12:30 | 88 | 87 |  |  | 43472.5208 | 109 | 109
2019-01-07 13:00 | 89 | 88 |  |  | 43472.5417 | 111 | 111
2019-01-07 13:30 | 93 | 92 |  |  | 43472.5625 | 114 | 113
2019-01-07 14:00 | 96 | 96 |  |  | 43472.5833 | 117 | 116
2019-01-07 14:30 | 97 | 97 |  |  | 43472.6042 | 116 | 116
2019-01-07 15:00 | 94 | 94 |  |  | 43472.625 | 116 | 115
2019-01-07 15:30 | 95 | 95 |  |  | 43472.6458 | 116 | 116
2019-01-07 16:00 | 94 | 93 |  |  | 43472.6667 | 114 | 113
2019-01-07 16:30 | 94 | 92 |  |  | 43472.6875 | 113 | 112
2019-01-07 17:00 | 94 | 92 |  |  | 43472.7083 | 112 | 110
2019-01-07 17:30 | 93 | 92 |  |  | 43472.7292 | 110 | 108
2019-01-07 18:00 | 92 | 91 |  |  | 43472.75 | 108 | 106
2019-01-07 18:30 | 91 | 91 |  |  | 43472.7708 | 104 | 104
2019-01-07 19:00 | 94 | 93 |  |  | 43472.7917 | 107 | 106
2019-01-07 19:30 | 94 | 94 |  |  | 43472.8125 | 106 | 106
2019-01-07 20:00 | 92 | 92 |  |  | 43472.8333 | 104 | 104
2019-01-07 20:30 | 92 | 92 |  |  | 43472.8542 | 104 | 104
2019-01-07 21:00 | 90 | 89 |  |  | 43472.875 | 100 | 100
2019-01-07 21:30 | 86 | 85 |  |  | 43472.8958 | 97 | 97
2019-01-07 22:00 | 83 | 82 |  |  | 43472.9167 | 95 | 94
2019-01-07 22:30 | 80 | 79 |  |  | 43472.9375 | 93 | 92
2019-01-07 23:00 | 77 | 76 |  |  | 43472.9583 | 87 | 87
2019-01-07 23:30 | 72 | 71 |  |  | 43472.9792 | 83 | 83
2019-01-08 | 69 | 68 |  |  | 43473 | 79 | 79
2019-01-08 00:30 | 65 | 63 |  |  | 43473.0208 | 73 | 72
2019-01-08 01:00 | 61 | 58 |  |  | 43473.0417 | 68 | 67
2019-01-08 01:30 | 58 | 55 |  |  | 43473.0625 | 66 | 64
2019-01-08 02:00 | 59 | 55 |  |  | 43473.0833 | 66 | 65
2019-01-08 02:30 | 60 | 56 |  |  | 43473.1042 | 67 | 65
2019-01-08 03:00 | 58 | 55 |  |  | 43473.125 | 66 | 64
2019-01-08 03:30 | 58 | 55 |  |  | 43473.1458 | 65 | 64
2019-01-08 04:00 | 57 | 54 |  |  | 43473.1667 | 65 | 64
2019-01-08 04:30 | 57 | 54 |  |  | 43473.1875 | 65 | 64
2019-01-08 05:00 | 59 | 55 |  |  | 43473.2083 | 67 | 66
2019-01-08 05:30 | 61 | 58 |  |  | 43473.2292 | 71 | 70
2019-01-08 06:00 | 64 | 61 |  |  | 43473.25 | 75 | 75
2019-01-08 06:30 | 69 | 68 |  |  | 43473.2708 | 85 | 85
2019-01-08 07:00 | 72 | 71 |  |  | 43473.2917 | 91 | 91
2019-01-08 07:30 | 78 | 77 |  |  | 43473.3125 | 98 | 98
2019-01-08 08:00 | 80 | 79 |  |  | 43473.3333 | 100 | 100
2019-01-08 08:30 | 83 | 81 |  |  | 43473.3542 | 104 | 104
2019-01-08 09:00 | 81 | 79 |  |  | 43473.375 | 104 | 103
2019-01-08 09:30 | 80 | 78 |  |  | 43473.3958 | 102 | 102
2019-01-08 10:00 | 80 | 79 |  |  | 43473.4167 | 103 | 103
2019-01-08 10:30 | 83 | 81 |  |  | 43473.4375 | 104 | 103
2019-01-08 11:00 | 87 | 86 |  |  | 43473.4583 | 107 | 106
2019-01-08 11:30 | 85 | 84 |  |  | 43473.4792 | 106 | 105
2019-01-08 12:00 | 83 | 82 |  |  | 43473.5 | 104 | 104
2019-01-08 12:30 | 85 | 84 |  |  | 43473.5208 | 107 | 106
2019-01-08 13:00 | 81 | 81 |  |  | 43473.5417 | 102 | 102
2019-01-08 13:30 | 84 | 83 |  |  | 43473.5625 | 105 | 105
2019-01-08 14:00 | 86 | 86 |  |  | 43473.5833 | 105 | 105
2019-01-08 14:30 | 83 | 82 |  |  | 43473.6042 | 104 | 104
2019-01-08 15:00 | 84 | 84 |  |  | 43473.625 | 103 | 102
2019-01-08 15:30 | 85 | 84 |  |  | 43473.6458 | 107 | 107
2019-01-08 16:00 | 87 | 86 |  |  | 43473.6667 | 107 | 106
2019-01-08 16:30 | 90 | 89 |  |  | 43473.6875 | 107 | 107
2019-01-08 17:00 | 92 | 92 |  |  | 43473.7083 | 110 | 109
2019-01-08 17:30 | 92 | 91 |  |  | 43473.7292 | 110 | 109
2019-01-08 18:00 | 92 | 91 |  |  | 43473.75 | 109 | 108
2019-01-08 18:30 | 91 | 90 |  |  | 43473.7708 | 106 | 105
2019-01-08 19:00 | 92 | 91 |  |  | 43473.7917 | 106 | 106
2019-01-08 19:30 | 93 | 92 |  |  | 43473.8125 | 106 | 106
2019-01-08 20:00 | 92 | 92 |  |  | 43473.8333 | 106 | 105
2019-01-08 20:30 | 90 | 89 |  |  | 43473.8542 | 103 | 102
2019-01-08 21:00 | 88 | 88 |  |  | 43473.875 | 100 | 100
2019-01-08 21:30 | 85 | 85 |  |  | 43473.8958 | 96 | 96
2019-01-08 22:00 | 82 | 81 |  |  | 43473.9167 | 94 | 94
2019-01-08 22:30 | 78 | 78 |  |  | 43473.9375 | 92 | 92
2019-01-08 23:00 | 74 | 73 |  |  | 43473.9583 | 86 | 86
2019-01-08 23:30 | 70 | 70 |  |  | 43473.9792 | 84 | 83
2019-01-09 | 67 | 65 |  |  | 43474 | 79 | 79
2019-01-09 00:30 | 64 | 62 |  |  | 43474.0208 | 75 | 74
2019-01-09 01:00 | 62 | 60 |  |  | 43474.0417 | 72 | 71
2019-01-09 01:30 | 62 | 59 |  |  | 43474.0625 | 71 | 70
2019-01-09 02:00 | 62 | 59 |  |  | 43474.0833 | 71 | 70
2019-01-09 02:30 | 60 | 57 |  |  | 43474.1042 | 69 | 68
2019-01-09 03:00 | 60 | 57 |  |  | 43474.125 | 68 | 67
2019-01-09 03:30 | 60 | 57 |  |  | 43474.1458 | 68 | 67
2019-01-09 04:00 | 57 | 53 |  |  | 43474.1667 | 67 | 66
2019-01-09 04:30 | 57 | 53 |  |  | 43474.1875 | 67 | 66
2019-01-09 05:00 | 58 | 55 |  |  | 43474.2083 | 68 | 67
2019-01-09 05:30 | 60 | 57 |  |  | 43474.2292 | 70 | 70
2019-01-09 06:00 | 62 | 60 |  |  | 43474.25 | 74 | 73
2019-01-09 06:30 | 66 | 65 |  |  | 43474.2708 | 83 | 83
2019-01-09 07:00 | 67 | 67 |  |  | 43474.2917 | 86 | 86
2019-01-09 07:30 | 72 | 71 |  |  | 43474.3125 | 95 | 95
2019-01-09 08:00 | 80 | 80 |  |  | 43474.3333 | 106 | 106
2019-01-09 08:30 | 81 | 81 |  |  | 43474.3542 | 109 | 109
2019-01-09 09:00 | 79 | 79 |  |  | 43474.375 | 108 | 108
2019-01-09 09:30 | 81 | 81 |  |  | 43474.3958 | 106 | 106
2019-01-09 10:00 | 80 | 80 |  |  | 43474.4167 | 107 | 107
2019-01-09 10:30 | 81 | 81 |  |  | 43474.4375 | 109 | 109
2019-01-09 11:00 | 82 | 82 |  |  | 43474.4583 | 110 | 110
2019-01-09 11:30 | 80 | 80 |  |  | 43474.4792 | 111 | 111
2019-01-09 12:00 | 79 | 78 |  |  | 43474.5 | 105 | 105
2019-01-09 12:30 | 80 | 80 |  |  | 43474.5208 | 101 | 101
2019-01-09 13:00 | 81 | 81 |  |  | 43474.5417 | 102 | 102
2019-01-09 13:30 | 82 | 82 |  |  | 43474.5625 | 107 | 107
2019-01-09 14:00 | 83 | 83 |  |  | 43474.5833 | 107 | 107
2019-01-09 14:30 | 86 | 86 |  |  | 43474.6042 | 106 | 105
2019-01-09 15:00 | 86 | 86 |  |  | 43474.625 | 109 | 109
2019-01-09 15:30 | 89 | 89 |  |  | 43474.6458 | 111 | 110
2019-01-09 16:00 | 89 | 89 |  |  | 43474.6667 | 114 | 114
2019-01-09 16:30 | 92 | 92 |  |  | 43474.6875 | 115 | 114
2019-01-09 17:00 | 95 | 95 |  |  | 43474.7083 | 113 | 113
2019-01-09 17:30 | 96 | 96 |  |  | 43474.7292 | 112 | 111
2019-01-09 18:00 | 95 | 95 |  |  | 43474.75 | 110 | 109
2019-01-09 18:30 | 94 | 93 |  |  | 43474.7708 | 109 | 107
2019-01-09 19:00 | 94 | 94 |  |  | 43474.7917 | 108 | 107
2019-01-09 19:30 | 95 | 95 |  |  | 43474.8125 | 109 | 107
2019-01-09 20:00 | 96 | 95 |  |  | 43474.8333 | 108 | 107
2019-01-09 20:30 | 95 | 94 |  |  | 43474.8542 | 108 | 107
2019-01-09 21:00 | 91 | 91 |  |  | 43474.875 | 104 | 103
2019-01-09 21:30 | 89 | 89 |  |  | 43474.8958 | 102 | 101
2019-01-09 22:00 | 86 | 86 |  |  | 43474.9167 | 100 | 99
2019-01-09 22:30 | 82 | 81 |  |  | 43474.9375 | 96 | 96
2019-01-09 23:00 | 77 | 76 |  |  | 43474.9583 | 91 | 91
2019-01-09 23:30 | 71 | 71 |  |  | 43474.9792 | 87 | 87
2019-01-10 | 66 | 66 |  |  | 43475 | 82 | 81
2019-01-10 00:30 | 62 | 62 |  |  | 43475.0208 | 77 | 77
2019-01-10 01:00 | 61 | 60 |  |  | 43475.0417 | 74 | 74
2019-01-10 01:30 | 59 | 58 |  |  | 43475.0625 | 73 | 73
2019-01-10 02:00 | 60 | 58 |  |  | 43475.0833 | 72 | 72
2019-01-10 02:30 | 59 | 56 |  |  | 43475.1042 | 70 | 69
2019-01-10 03:00 | 59 | 55 |  |  | 43475.125 | 70 | 69
2019-01-10 03:30 | 59 | 55 |  |  | 43475.1458 | 70 | 69
2019-01-10 04:00 | 59 | 56 |  |  | 43475.1667 | 70 | 69
2019-01-10 04:30 | 61 | 57 |  |  | 43475.1875 | 72 | 71
2019-01-10 05:00 | 62 | 58 |  |  | 43475.2083 | 73 | 72
2019-01-10 05:30 | 66 | 63 |  |  | 43475.2292 | 77 | 76
2019-01-10 06:00 | 68 | 66 |  |  | 43475.25 | 81 | 80
2019-01-10 06:30 | 72 | 70 |  |  | 43475.2708 | 89 | 89
2019-01-10 07:00 | 75 | 73 |  |  | 43475.2917 | 95 | 94
2019-01-10 07:30 | 82 | 80 |  |  | 43475.3125 | 105 | 104
2019-01-10 08:00 | 84 | 82 |  |  | 43475.3333 | 110 | 108
2019-01-10 08:30 | 87 | 85 |  |  | 43475.3542 | 111 | 110
2019-01-10 09:00 | 92 | 87 |  |  | 43475.375 | 123 | 119
2019-01-10 09:30 | 92 | 85 |  |  | 43475.3958 | 126 | 119
2019-01-10 10:00 | 96 | 90 |  |  | 43475.4167 | 123 | 117
2019-01-10 10:30 | 96 | 90 |  |  | 43475.4375 | 123 | 116
2019-01-10 11:00 | 91 | 85 |  |  | 43475.4583 | 124 | 117
2019-01-10 11:30 | 95 | 90 |  |  | 43475.4792 | 123 | 117
2019-01-10 12:00 | 99 | 95 |  |  | 43475.5 | 126 | 120
2019-01-10 12:30 | 100 | 97 |  |  | 43475.5208 | 126 | 120
2019-01-10 13:00 | 101 | 98 |  |  | 43475.5417 | 125 | 119
2019-01-10 13:30 | 97 | 93 |  |  | 43475.5625 | 126 | 120
2019-01-10 14:00 | 95 | 91 |  |  | 43475.5833 | 120 | 113
2019-01-10 14:30 | 93 | 89 |  |  | 43475.6042 | 116 | 109
2019-01-10 15:00 | 94 | 90 |  |  | 43475.625 | 120 | 113
2019-01-10 15:30 | 97 | 93 |  |  | 43475.6458 | 123 | 116
2019-01-10 16:00 | 98 | 94 |  |  | 43475.6667 | 125 | 118
2019-01-10 16:30 | 100 | 97 |  |  | 43475.6875 | 126 | 119
2019-01-10 17:00 | 104 | 100 |  |  | 43475.7083 | 130 | 121
2019-01-10 17:30 | 105 | 99 |  |  | 43475.7292 | 131 | 119
2019-01-10 18:00 | 105 | 99 |  |  | 43475.75 | 131 | 117
2019-01-10 18:30 | 99 | 96 |  |  | 43475.7708 | 131 | 113
2019-01-10 19:00 | 100 | 97 |  |  | 43475.7917 | 132 | 114
2019-01-10 19:30 | 100 | 97 |  |  | 43475.8125 | 131 | 113
2019-01-10 20:00 | 99 | 96 |  |  | 43475.8333 | 131 | 113
2019-01-10 20:30 | 98 | 95 |  |  | 43475.8542 | 128 | 111
2019-01-10 21:00 | 95 | 91 |  |  | 43475.875 | 125 | 108
2019-01-10 21:30 | 90 | 87 |  |  | 43475.8958 | 121 | 103
2019-01-10 22:00 | 89 | 86 |  |  | 43475.9167 | 121 | 102
2019-01-10 22:30 | 82 | 80 |  |  | 43475.9375 | 109 | 96
2019-01-10 23:00 | 76 | 75 |  |  | 43475.9583 | 93 | 89
2019-01-10 23:30 | 71 | 71 |  |  | 43475.9792 | 90 | 86
2019-01-11 | 67 | 66 |  |  | 43476 | 84 | 81
2019-01-11 00:30 | 61 | 61 |  |  | 43476.0208 | 78 | 75
2019-01-11 01:00 | 58 | 58 |  |  | 43476.0417 | 73 | 69
2019-01-11 01:30 | 56 | 55 |  |  | 43476.0625 | 72 | 67
2019-01-11 02:00 | 55 | 54 |  |  | 43476.0833 | 70 | 65
2019-01-11 02:30 | 54 | 53 |  |  | 43476.1042 | 70 | 64
2019-01-11 03:00 | 53 | 52 |  |  | 43476.125 | 69 | 63
2019-01-11 03:30 | 53 | 52 |  |  | 43476.1458 | 68 | 63
2019-01-11 04:00 | 52 | 50 |  |  | 43476.1667 | 67 | 61
2019-01-11 04:30 | 52 | 51 |  |  | 43476.1875 | 68 | 62
2019-01-11 05:00 | 54 | 54 |  |  | 43476.2083 | 69 | 64
2019-01-11 05:30 | 56 | 55 |  |  | 43476.2292 | 72 | 67
2019-01-11 06:00 | 59 | 59 |  |  | 43476.25 | 75 | 71
2019-01-11 06:30 | 64 | 64 |  |  | 43476.2708 | 82 | 80
2019-01-11 07:00 | 70 | 70 |  |  | 43476.2917 | 88 | 87
2019-01-11 07:30 | 73 | 73 |  |  | 43476.3125 | 94 | 93
2019-01-11 08:00 | 77 | 77 |  |  | 43476.3333 | 102 | 102
2019-01-11 08:30 | 80 | 79 |  |  | 43476.3542 | 107 | 107
2019-01-11 09:00 | 80 | 80 |  |  | 43476.375 | 106 | 105
2019-01-11 09:30 | 79 | 79 |  |  | 43476.3958 | 104 | 103
2019-01-11 10:00 | 74 | 74 |  |  | 43476.4167 | 102 | 100
2019-01-11 10:30 | 73 | 73 |  |  | 43476.4375 | 101 | 99
2019-01-11 11:00 | 74 | 74 |  |  | 43476.4583 | 100 | 99
2019-01-11 11:30 | 73 | 73 |  |  | 43476.4792 | 98 | 96
2019-01-11 12:00 | 72 | 72 |  |  | 43476.5 | 97 | 95
2019-01-11 12:30 | 74 | 74 |  |  | 43476.5208 | 97 | 95
2019-01-11 13:00 | 75 | 75 |  |  | 43476.5417 | 97 | 95
2019-01-11 13:30 | 72 | 72 |  |  | 43476.5625 | 93 | 91
2019-01-11 14:00 | 74 | 74 |  |  | 43476.5833 | 95 | 94
2019-01-11 14:30 | 76 | 76 |  |  | 43476.6042 | 98 | 96
2019-01-11 15:00 | 77 | 77 |  |  | 43476.625 | 98 | 96
2019-01-11 15:30 | 80 | 80 |  |  | 43476.6458 | 102 | 100
2019-01-11 16:00 | 85 | 85 |  |  | 43476.6667 | 106 | 104
2019-01-11 16:30 | 90 | 90 |  |  | 43476.6875 | 110 | 108
2019-01-11 17:00 | 93 | 93 |  |  | 43476.7083 | 113 | 110
2019-01-11 17:30 | 93 | 93 |  |  | 43476.7292 | 112 | 109
2019-01-11 18:00 | 91 | 91 |  |  | 43476.75 | 109 | 105
2019-01-11 18:30 | 89 | 89 |  |  | 43476.7708 | 105 | 102
2019-01-11 19:00 | 88 | 88 |  |  | 43476.7917 | 106 | 102
2019-01-11 19:30 | 89 | 89 |  |  | 43476.8125 | 106 | 102
2019-01-11 20:00 | 89 | 89 |  |  | 43476.8333 | 105 | 103
2019-01-11 20:30 | 89 | 89 |  |  | 43476.8542 | 104 | 102
2019-01-11 21:00 | 85 | 85 |  |  | 43476.875 | 100 | 97
2019-01-11 21:30 | 79 | 79 |  |  | 43476.8958 | 94 | 91
2019-01-11 22:00 | 78 | 78 |  |  | 43476.9167 | 95 | 91
2019-01-11 22:30 | 77 | 77 |  |  | 43476.9375 | 95 | 90
2019-01-11 23:00 | 71 | 71 |  |  | 43476.9583 | 88 | 83
2019-01-11 23:30 | 67 | 67 |  |  | 43476.9792 | 85 | 80
2019-01-12 | 61 | 61 |  |  | 43477 | 79 | 74
2019-01-12 00:30 | 58 | 57 |  |  | 43477.0208 | 75 | 70
2019-01-12 01:00 | 54 | 53 |  |  | 43477.0417 | 71 | 65
2019-01-12 01:30 | 53 | 51 |  |  | 43477.0625 | 70 | 63
2019-01-12 02:00 | 50 | 48 |  |  | 43477.0833 | 66 | 60
2019-01-12 02:30 | 51 | 49 |  |  | 43477.1042 | 65 | 59
2019-01-12 03:00 | 49 | 47 |  |  | 43477.125 | 64 | 57
2019-01-12 03:30 | 45 | 44 |  |  | 43477.1458 | 60 | 53
2019-01-12 04:00 | 43 | 41 |  |  | 43477.1667 | 58 | 51
2019-01-12 04:30 | 43 | 41 |  |  | 43477.1875 | 57 | 50
2019-01-12 05:00 | 43 | 41 |  |  | 43477.2083 | 58 | 51
2019-01-12 05:30 | 43 | 41 |  |  | 43477.2292 | 57 | 51
2019-01-12 06:00 | 43 | 41 |  |  | 43477.25 | 58 | 52
2019-01-12 06:30 | 43 | 41 |  |  | 43477.2708 | 59 | 53
2019-01-12 07:00 | 41 | 40 |  |  | 43477.2917 | 57 | 51
2019-01-12 07:30 | 42 | 41 |  |  | 43477.3125 | 58 | 54
2019-01-12 08:00 | 42 | 42 |  |  | 43477.3333 | 60 | 57
2019-01-12 08:30 | 45 | 44 |  |  | 43477.3542 | 63 | 61
2019-01-12 09:00 | 49 | 49 |  |  | 43477.375 | 67 | 64
2019-01-12 09:30 | 49 | 49 |  |  | 43477.3958 | 66 | 63
2019-01-12 10:00 | 51 | 51 |  |  | 43477.4167 | 66 | 64
2019-01-12 10:30 | 49 | 49 |  |  | 43477.4375 | 64 | 62
2019-01-12 11:00 | 46 | 46 |  |  | 43477.4583 | 61 | 59
2019-01-12 11:30 | 46 | 46 |  |  | 43477.4792 | 60 | 59
2019-01-12 12:00 | 45 | 45 |  |  | 43477.5 | 61 | 59
2019-01-12 12:30 | 46 | 46 |  |  | 43477.5208 | 61 | 58
2019-01-12 13:00 | 46 | 46 |  |  | 43477.5417 | 59 | 57
2019-01-12 13:30 | 48 | 47 |  |  | 43477.5625 | 61 | 59
2019-01-12 14:00 | 51 | 51 |  |  | 43477.5833 | 63 | 61
2019-01-12 14:30 | 53 | 53 |  |  | 43477.6042 | 64 | 62
2019-01-12 15:00 | 56 | 56 |  |  | 43477.625 | 68 | 67
2019-01-12 15:30 | 59 | 58 |  |  | 43477.6458 | 71 | 70
2019-01-12 16:00 | 61 | 61 |  |  | 43477.6667 | 74 | 72
2019-01-12 16:30 | 63 | 63 |  |  | 43477.6875 | 77 | 75
2019-01-12 17:00 | 66 | 66 |  |  | 43477.7083 | 82 | 80
2019-01-12 17:30 | 69 | 69 |  |  | 43477.7292 | 84 | 81
2019-01-12 18:00 | 69 | 69 |  |  | 43477.75 | 84 | 82
2019-01-12 18:30 | 68 | 68 |  |  | 43477.7708 | 85 | 82
2019-01-12 19:00 | 68 | 68 |  |  | 43477.7917 | 86 | 83
2019-01-12 19:30 | 70 | 70 |  |  | 43477.8125 | 89 | 86
2019-01-12 20:00 | 69 | 69 |  |  | 43477.8333 | 89 | 85
2019-01-12 20:30 | 68 | 68 |  |  | 43477.8542 | 87 | 84
2019-01-12 21:00 | 66 | 66 |  |  | 43477.875 | 84 | 81
2019-01-12 21:30 | 64 | 64 |  |  | 43477.8958 | 82 | 80
2019-01-12 22:00 | 65 | 64 |  |  | 43477.9167 | 84 | 81
2019-01-12 22:30 | 67 | 66 |  |  | 43477.9375 | 86 | 82
2019-01-12 23:00 | 65 | 64 |  |  | 43477.9583 | 82 | 78
2019-01-12 23:30 | 62 | 61 |  |  | 43477.9792 | 79 | 75
2019-01-13 | 59 | 58 |  |  | 43478 | 76 | 72
2019-01-13 00:30 | 55 | 54 |  |  | 43478.0208 | 72 | 68
2019-01-13 01:00 | 52 | 51 |  |  | 43478.0417 | 69 | 64
2019-01-13 01:30 | 50 | 49 |  |  | 43478.0625 | 67 | 62
2019-01-13 02:00 | 48 | 47 |  |  | 43478.0833 | 65 | 60
2019-01-13 02:30 | 47 | 46 |  |  | 43478.1042 | 65 | 59
2019-01-13 03:00 | 47 | 46 |  |  | 43478.125 | 64 | 58
2019-01-13 03:30 | 46 | 44 |  |  | 43478.1458 | 63 | 57
2019-01-13 04:00 | 46 | 44 |  |  | 43478.1667 | 63 | 56
2019-01-13 04:30 | 48 | 46 |  |  | 43478.1875 | 64 | 57
2019-01-13 05:00 | 48 | 46 |  |  | 43478.2083 | 64 | 57
2019-01-13 05:30 | 45 | 43 |  |  | 43478.2292 | 63 | 55
2019-01-13 06:00 | 44 | 42 |  |  | 43478.25 | 62 | 54
2019-01-13 06:30 | 44 | 42 |  |  | 43478.2708 | 62 | 55
2019-01-13 07:00 | 43 | 41 |  |  | 43478.2917 | 61 | 55
2019-01-13 07:30 | 43 | 42 |  |  | 43478.3125 | 62 | 57
2019-01-13 08:00 | 43 | 42 |  |  | 43478.3333 | 63 | 58
2019-01-13 08:30 | 44 | 44 |  |  | 43478.3542 | 64 | 61
2019-01-13 09:00 | 46 | 45 |  |  | 43478.375 | 65 | 63
2019-01-13 09:30 | 49 | 49 |  |  | 43478.3958 | 67 | 64
2019-01-13 10:00 | 50 | 50 |  |  | 43478.4167 | 68 | 65
2019-01-13 10:30 | 54 | 54 |  |  | 43478.4375 | 70 | 68
2019-01-13 11:00 | 54 | 54 |  |  | 43478.4583 | 70 | 68
2019-01-13 11:30 | 56 | 56 |  |  | 43478.4792 | 70 | 68
2019-01-13 12:00 | 56 | 56 |  |  | 43478.5 | 72 | 70
2019-01-13 12:30 | 59 | 59 |  |  | 43478.5208 | 73 | 71
2019-01-13 13:00 | 58 | 58 |  |  | 43478.5417 | 73 | 72
2019-01-13 13:30 | 59 | 59 |  |  | 43478.5625 | 74 | 72
2019-01-13 14:00 | 60 | 60 |  |  | 43478.5833 | 73 | 72
2019-01-13 14:30 | 63 | 63 |  |  | 43478.6042 | 77 | 75
2019-01-13 15:00 | 66 | 66 |  |  | 43478.625 | 79 | 78
2019-01-13 15:30 | 65 | 65 |  |  | 43478.6458 | 79 | 78
2019-01-13 16:00 | 67 | 67 |  |  | 43478.6667 | 82 | 81
2019-01-13 16:30 | 70 | 69 |  |  | 43478.6875 | 84 | 83
2019-01-13 17:00 | 74 | 74 |  |  | 43478.7083 | 89 | 88
2019-01-13 17:30 | 76 | 76 |  |  | 43478.7292 | 93 | 91
2019-01-13 18:00 | 78 | 78 |  |  | 43478.75 | 95 | 93
2019-01-13 18:30 | 78 | 77 |  |  | 43478.7708 | 94 | 93
2019-01-13 19:00 | 78 | 78 |  |  | 43478.7917 | 98 | 96
2019-01-13 19:30 | 80 | 80 |  |  | 43478.8125 | 99 | 97
2019-01-13 20:00 | 77 | 77 |  |  | 43478.8333 | 97 | 96
2019-01-13 20:30 | 77 | 77 |  |  | 43478.8542 | 96 | 95
2019-01-13 21:00 | 76 | 76 |  |  | 43478.875 | 95 | 94
2019-01-13 21:30 | 74 | 74 |  |  | 43478.8958 | 93 | 91
2019-01-13 22:00 | 72 | 72 |  |  | 43478.9167 | 90 | 89
2019-01-13 22:30 | 72 | 72 |  |  | 43478.9375 | 90 | 89
2019-01-13 23:00 | 68 | 68 |  |  | 43478.9583 | 86 | 84
2019-01-13 23:30 | 64 | 64 |  |  | 43478.9792 | 82 | 80
2019-01-14 | 59 | 59 |  |  | 43479 | 76 | 75
2019-01-14 00:30 | 55 | 55 |  |  | 43479.0208 | 71 | 69
2019-01-14 01:00 | 52 | 52 |  |  | 43479.0417 | 69 | 67
2019-01-14 01:30 | 50 | 50 |  |  | 43479.0625 | 66 | 63
2019-01-14 02:00 | 49 | 49 |  |  | 43479.0833 | 65 | 62
2019-01-14 02:30 | 48 | 48 |  |  | 43479.1042 | 63 | 60
2019-01-14 03:00 | 46 | 45 |  |  | 43479.125 | 63 | 60
2019-01-14 03:30 | 45 | 45 |  |  | 43479.1458 | 63 | 60
2019-01-14 04:00 | 45 | 45 |  |  | 43479.1667 | 61 | 58
2019-01-14 04:30 | 45 | 44 |  |  | 43479.1875 | 62 | 59
2019-01-14 05:00 | 48 | 48 |  |  | 43479.2083 | 66 | 63
2019-01-14 05:30 | 52 | 52 |  |  | 43479.2292 | 70 | 68
2019-01-14 06:00 | 58 | 58 |  |  | 43479.25 | 75 | 73
2019-01-14 06:30 | 63 | 63 |  |  | 43479.2708 | 82 | 82
2019-01-14 07:00 | 65 | 64 |  |  | 43479.2917 | 87 | 87
2019-01-14 07:30 | 70 | 70 |  |  | 43479.3125 | 95 | 95
2019-01-14 08:00 | 73 | 73 |  |  | 43479.3333 | 100 | 100
2019-01-14 08:30 | 78 | 77 |  |  | 43479.3542 | 104 | 103
2019-01-14 09:00 | 78 | 77 |  |  | 43479.375 | 103 | 103
2019-01-14 09:30 | 82 | 81 |  |  | 43479.3958 | 113 | 112
2019-01-14 10:00 | 80 | 79 |  |  | 43479.4167 | 110 | 110
2019-01-14 10:30 | 77 | 76 |  |  | 43479.4375 | 108 | 108
2019-01-14 11:00 | 79 | 78 |  |  | 43479.4583 | 109 | 109
2019-01-14 11:30 | 79 | 77 |  |  | 43479.4792 | 109 | 109
2019-01-14 12:00 | 78 | 77 |  |  | 43479.5 | 109 | 108
2019-01-14 12:30 | 78 | 77 |  |  | 43479.5208 | 108 | 108
2019-01-14 13:00 | 81 | 80 |  |  | 43479.5417 | 111 | 110
2019-01-14 13:30 | 83 | 82 |  |  | 43479.5625 | 112 | 111
2019-01-14 14:00 | 85 | 85 |  |  | 43479.5833 | 115 | 115
2019-01-14 14:30 | 87 | 87 |  |  | 43479.6042 | 117 | 117
2019-01-14 15:00 | 91 | 91 |  |  | 43479.625 | 122 | 122
2019-01-14 15:30 | 88 | 88 |  |  | 43479.6458 | 116 | 115
2019-01-14 16:00 | 89 | 89 |  |  | 43479.6667 | 115 | 114
2019-01-14 16:30 | 91 | 91 |  |  | 43479.6875 | 116 | 115
2019-01-14 17:00 | 91 | 91 |  |  | 43479.7083 | 116 | 115
2019-01-14 17:30 | 93 | 93 |  |  | 43479.7292 | 115 | 114
2019-01-14 18:00 | 92 | 91 |  |  | 43479.75 | 112 | 111
2019-01-14 18:30 | 90 | 88 |  |  | 43479.7708 | 108 | 104
2019-01-14 19:00 | 91 | 88 |  |  | 43479.7917 | 110 | 105
2019-01-14 19:30 | 90 | 87 |  |  | 43479.8125 | 108 | 105
2019-01-14 20:00 | 89 | 87 |  |  | 43479.8333 | 108 | 104
2019-01-14 20:30 | 89 | 86 |  |  | 43479.8542 | 106 | 103
2019-01-14 21:00 | 88 | 86 |  |  | 43479.875 | 105 | 102
2019-01-14 21:30 | 85 | 83 |  |  | 43479.8958 | 101 | 98
2019-01-14 22:00 | 85 | 82 |  |  | 43479.9167 | 100 | 97
2019-01-14 22:30 | 80 | 77 |  |  | 43479.9375 | 96 | 92
2019-01-14 23:00 | 75 | 72 |  |  | 43479.9583 | 88 | 86
2019-01-14 23:30 | 68 | 65 |  |  | 43479.9792 | 83 | 80
2019-01-15 | 65 | 59 |  |  | 43480 | 77 | 74
2019-01-15 00:30 | 61 | 53 |  |  | 43480.0208 | 70 | 67
2019-01-15 01:00 | 59 | 49 |  |  | 43480.0417 | 67 | 63
2019-01-15 01:30 | 58 | 47 |  |  | 43480.0625 | 64 | 60
2019-01-15 02:00 | 60 | 50 |  |  | 43480.0833 | 67 | 62
2019-01-15 02:30 | 58 | 47 |  |  | 43480.1042 | 65 | 60
2019-01-15 03:00 | 58 | 47 |  |  | 43480.125 | 65 | 60
2019-01-15 03:30 | 58 | 47 |  |  | 43480.1458 | 65 | 59
2019-01-15 04:00 | 58 | 47 |  |  | 43480.1667 | 63 | 58
2019-01-15 04:30 | 58 | 47 |  |  | 43480.1875 | 64 | 60
2019-01-15 05:00 | 58 | 49 |  |  | 43480.2083 | 65 | 62
2019-01-15 05:30 | 60 | 51 |  |  | 43480.2292 | 67 | 64
2019-01-15 06:00 | 60 | 52 |  |  | 43480.25 | 71 | 68
2019-01-15 06:30 | 63 | 57 |  |  | 43480.2708 | 78 | 77
2019-01-15 07:00 | 64 | 61 |  |  | 43480.2917 | 84 | 84
2019-01-15 07:30 | 72 | 70 |  |  | 43480.3125 | 94 | 94
2019-01-15 08:00 | 76 | 75 |  |  | 43480.3333 | 99 | 99
2019-01-15 08:30 | 75 | 72 |  |  | 43480.3542 | 99 | 98
2019-01-15 09:00 | 78 | 76 |  |  | 43480.375 | 101 | 100
2019-01-15 09:30 | 77 | 75 |  |  | 43480.3958 | 101 | 100
2019-01-15 10:00 | 77 | 75 |  |  | 43480.4167 | 103 | 102
2019-01-15 10:30 | 77 | 75 |  |  | 43480.4375 | 102 | 101
2019-01-15 11:00 | 76 | 74 |  |  | 43480.4583 | 100 | 99
2019-01-15 11:30 | 77 | 75 |  |  | 43480.4792 | 100 | 99
2019-01-15 12:00 | 77 | 76 |  |  | 43480.5 | 102 | 101
2019-01-15 12:30 | 80 | 78 |  |  | 43480.5208 | 102 | 101
2019-01-15 13:00 | 78 | 77 |  |  | 43480.5417 | 102 | 101
2019-01-15 13:30 | 80 | 79 |  |  | 43480.5625 | 102 | 101
2019-01-15 14:00 | 86 | 83 |  |  | 43480.5833 | 111 | 105
2019-01-15 14:30 | 90 | 87 |  |  | 43480.6042 | 115 | 108
2019-01-15 15:00 | 90 | 87 |  |  | 43480.625 | 116 | 110
2019-01-15 15:30 | 90 | 86 |  |  | 43480.6458 | 117 | 110
2019-01-15 16:00 | 91 | 87 |  |  | 43480.6667 | 119 | 112
2019-01-15 16:30 | 99 | 94 |  |  | 43480.6875 | 124 | 116
2019-01-15 17:00 | 101 | 96 |  |  | 43480.7083 | 126 | 118
2019-01-15 17:30 | 100 | 95 |  |  | 43480.7292 | 123 | 114
2019-01-15 18:00 | 96 | 91 |  |  | 43480.75 | 118 | 111
2019-01-15 18:30 | 92 | 88 |  |  | 43480.7708 | 113 | 105
2019-01-15 19:00 | 94 | 89 |  |  | 43480.7917 | 116 | 106
2019-01-15 19:30 | 94 | 88 |  |  | 43480.8125 | 116 | 107
2019-01-15 20:00 | 93 | 87 |  |  | 43480.8333 | 114 | 105
2019-01-15 20:30 | 91 | 85 |  |  | 43480.8542 | 110 | 102
2019-01-15 21:00 | 89 | 85 |  |  | 43480.875 | 109 | 101
2019-01-15 21:30 | 85 | 80 |  |  | 43480.8958 | 105 | 96
2019-01-15 22:00 | 86 | 79 |  |  | 43480.9167 | 105 | 95
2019-01-15 22:30 | 80 | 75 |  |  | 43480.9375 | 99 | 92
2019-01-15 23:00 | 70 | 69 |  |  | 43480.9583 | 84 | 83
2019-01-15 23:30 | 67 | 63 |  |  | 43480.9792 | 79 | 78
2019-01-16 | 64 | 58 |  |  | 43481 | 75 | 73
2019-01-16 00:30 | 62 | 54 |  |  | 43481.0208 | 72 | 69
2019-01-16 01:00 | 59 | 51 |  |  | 43481.0417 | 68 | 65
2019-01-16 01:30 | 56 | 47 |  |  | 43481.0625 | 63 | 59
2019-01-16 02:00 | 55 | 46 |  |  | 43481.0833 | 62 | 58
2019-01-16 02:30 | 56 | 46 |  |  | 43481.1042 | 64 | 59
2019-01-16 03:00 | 57 | 47 |  |  | 43481.125 | 65 | 60
2019-01-16 03:30 | 57 | 47 |  |  | 43481.1458 | 64 | 59
2019-01-16 04:00 | 55 | 44 |  |  | 43481.1667 | 62 | 57
2019-01-16 04:30 | 55 | 45 |  |  | 43481.1875 | 63 | 59
2019-01-16 05:00 | 57 | 47 |  |  | 43481.2083 | 65 | 60
2019-01-16 05:30 | 58 | 49 |  |  | 43481.2292 | 67 | 63
2019-01-16 06:00 | 59 | 51 |  |  | 43481.25 | 71 | 68
2019-01-16 06:30 | 61 | 54 |  |  | 43481.2708 | 78 | 75
2019-01-16 07:00 | 64 | 59 |  |  | 43481.2917 | 83 | 82
2019-01-16 07:30 | 69 | 65 |  |  | 43481.3125 | 91 | 91
2019-01-16 08:00 | 74 | 70 |  |  | 43481.3333 | 98 | 96
2019-01-16 08:30 | 72 | 69 |  |  | 43481.3542 | 97 | 95
2019-01-16 09:00 | 75 | 70 |  |  | 43481.375 | 102 | 97
2019-01-16 09:30 | 80 | 71 |  |  | 43481.3958 | 108 | 99
2019-01-16 10:00 | 78 | 70 |  |  | 43481.4167 | 107 | 98
2019-01-16 10:30 | 78 | 70 |  |  | 43481.4375 | 106 | 97
2019-01-16 11:00 | 79 | 72 |  |  | 43481.4583 | 107 | 99
2019-01-16 11:30 | 82 | 76 |  |  | 43481.4792 | 110 | 103
2019-01-16 12:00 | 84 | 77 |  |  | 43481.5 | 112 | 104
2019-01-16 12:30 | 85 | 78 |  |  | 43481.5208 | 112 | 105
2019-01-16 13:00 | 87 | 80 |  |  | 43481.5417 | 114 | 106
2019-01-16 13:30 | 90 | 83 |  |  | 43481.5625 | 116 | 110
2019-01-16 14:00 | 93 | 85 |  |  | 43481.5833 | 117 | 111
2019-01-16 14:30 | 94 | 86 |  |  | 43481.6042 | 118 | 113
2019-01-16 15:00 | 94 | 86 |  |  | 43481.625 | 118 | 113
2019-01-16 15:30 | 94 | 85 |  |  | 43481.6458 | 119 | 113
2019-01-16 16:00 | 96 | 88 |  |  | 43481.6667 | 120 | 114
2019-01-16 16:30 | 102 | 93 |  |  | 43481.6875 | 125 | 118
2019-01-16 17:00 | 106 | 97 |  |  | 43481.7083 | 130 | 123
2019-01-16 17:30 | 108 | 98 |  |  | 43481.7292 | 130 | 121
2019-01-16 18:00 | 101 | 96 |  |  | 43481.75 | 123 | 116
2019-01-16 18:30 | 95 | 94 |  |  | 43481.7708 | 114 | 111
2019-01-16 19:00 | 96 | 95 |  |  | 43481.7917 | 114 | 113
2019-01-16 19:30 | 96 | 95 |  |  | 43481.8125 | 115 | 113
2019-01-16 20:00 | 94 | 93 |  |  | 43481.8333 | 112 | 111
2019-01-16 20:30 | 90 | 89 |  |  | 43481.8542 | 108 | 108
2019-01-16 21:00 | 89 | 88 |  |  | 43481.875 | 106 | 106
2019-01-16 21:30 | 89 | 89 |  |  | 43481.8958 | 105 | 105
2019-01-16 22:00 | 91 | 90 |  |  | 43481.9167 | 107 | 106
2019-01-16 22:30 | 85 | 84 |  |  | 43481.9375 | 104 | 103
2019-01-16 23:00 | 78 | 77 |  |  | 43481.9583 | 95 | 94
2019-01-16 23:30 | 70 | 70 |  |  | 43481.9792 | 88 | 87
2019-01-17 | 64 | 64 |  |  | 43482 | 81 | 80
2019-01-17 00:30 | 57 | 57 |  |  | 43482.0208 | 73 | 72
2019-01-17 01:00 | 55 | 54 |  |  | 43482.0417 | 70 | 68
2019-01-17 01:30 | 54 | 53 |  |  | 43482.0625 | 69 | 66
2019-01-17 02:00 | 53 | 51 |  |  | 43482.0833 | 67 | 64
2019-01-17 02:30 | 52 | 51 |  |  | 43482.1042 | 68 | 64
2019-01-17 03:00 | 52 | 51 |  |  | 43482.125 | 67 | 63
2019-01-17 03:30 | 51 | 50 |  |  | 43482.1458 | 65 | 62
2019-01-17 04:00 | 51 | 50 |  |  | 43482.1667 | 66 | 62
2019-01-17 04:30 | 51 | 50 |  |  | 43482.1875 | 66 | 63
2019-01-17 05:00 | 51 | 50 |  |  | 43482.2083 | 67 | 63
2019-01-17 05:30 | 51 | 51 |  |  | 43482.2292 | 68 | 64
2019-01-17 06:00 | 53 | 52 |  |  | 43482.25 | 69 | 67
2019-01-17 06:30 | 58 | 57 |  |  | 43482.2708 | 78 | 76
2019-01-17 07:00 | 62 | 60 |  |  | 43482.2917 | 82 | 82
2019-01-17 07:30 | 70 | 68 |  |  | 43482.3125 | 93 | 93
2019-01-17 08:00 | 75 | 73 |  |  | 43482.3333 | 98 | 98
2019-01-17 08:30 | 80 | 79 |  |  | 43482.3542 | 91 | 90
2019-01-17 09:00 | 78 | 78 |  |  | 43482.375 | 92 | 92
2019-01-17 09:30 | 81 | 81 |  |  | 43482.3958 | 94 | 93
2019-01-17 10:00 | 80 | 79 |  |  | 43482.4167 | 92 | 92
2019-01-17 10:30 | 76 | 75 |  |  | 43482.4375 | 101 | 101
2019-01-17 11:00 | 78 | 77 |  |  | 43482.4583 | 95 | 95
2019-01-17 11:30 | 80 | 80 |  |  | 43482.4792 | 93 | 92
2019-01-17 12:00 | 82 | 82 |  |  | 43482.5 | 95 | 94
2019-01-17 12:30 | 79 | 79 |  |  | 43482.5208 | 92 | 92
2019-01-17 13:00 | 79 | 79 |  |  | 43482.5417 | 92 | 92
2019-01-17 13:30 | 81 | 81 |  |  | 43482.5625 | 92 | 92
2019-01-17 14:00 | 83 | 83 |  |  | 43482.5833 | 94 | 93
2019-01-17 14:30 | 86 | 85 |  |  | 43482.6042 | 97 | 96
2019-01-17 15:00 | 87 | 85 |  |  | 43482.625 | 102 | 97
2019-01-17 15:30 | 91 | 86 |  |  | 43482.6458 | 110 | 98
2019-01-17 16:00 | 93 | 87 |  |  | 43482.6667 | 112 | 99
2019-01-17 16:30 | 97 | 93 |  |  | 43482.6875 | 114 | 102
2019-01-17 17:00 | 102 | 97 |  |  | 43482.7083 | 117 | 104
2019-01-17 17:30 | 103 | 98 |  |  | 43482.7292 | 118 | 104
2019-01-17 18:00 | 103 | 97 |  |  | 43482.75 | 117 | 102
2019-01-17 18:30 | 100 | 96 |  |  | 43482.7708 | 110 | 100
2019-01-17 19:00 | 103 | 99 |  |  | 43482.7917 | 112 | 102
2019-01-17 19:30 | 99 | 96 |  |  | 43482.8125 | 109 | 100
2019-01-17 20:00 | 99 | 96 |  |  | 43482.8333 | 109 | 99
2019-01-17 20:30 | 98 | 94 |  |  | 43482.8542 | 108 | 98
2019-01-17 21:00 | 91 | 90 |  |  | 43482.875 | 97 | 92
2019-01-17 21:30 | 86 | 85 |  |  | 43482.8958 | 93 | 90
2019-01-17 22:00 | 83 | 81 |  |  | 43482.9167 | 99 | 96
2019-01-17 22:30 | 81 | 79 |  |  | 43482.9375 | 96 | 93
2019-01-17 23:00 | 73 | 72 |  |  | 43482.9583 | 87 | 85
2019-01-17 23:30 | 68 | 66 |  |  | 43482.9792 | 82 | 80
2019-01-18 | 63 | 59 |  |  | 43483 | 74 | 72
2019-01-18 00:30 | 62 | 57 |  |  | 43483.0208 | 72 | 70
2019-01-18 01:00 | 58 | 53 |  |  | 43483.0417 | 68 | 65
2019-01-18 01:30 | 58 | 52 |  |  | 43483.0625 | 67 | 64
2019-01-18 02:00 | 56 | 49 |  |  | 43483.0833 | 64 | 61
2019-01-18 02:30 | 56 | 49 |  |  | 43483.1042 | 63 | 59
2019-01-18 03:00 | 54 | 46 |  |  | 43483.125 | 62 | 58
2019-01-18 03:30 | 52 | 44 |  |  | 43483.1458 | 60 | 56
2019-01-18 04:00 | 52 | 44 |  |  | 43483.1667 | 59 | 55
2019-01-18 04:30 | 53 | 45 |  |  | 43483.1875 | 61 | 57
2019-01-18 05:00 | 55 | 48 |  |  | 43483.2083 | 64 | 60
2019-01-18 05:30 | 57 | 50 |  |  | 43483.2292 | 66 | 63
2019-01-18 06:00 | 59 | 53 |  |  | 43483.25 | 70 | 67
2019-01-18 06:30 | 64 | 59 |  |  | 43483.2708 | 79 | 77
2019-01-18 07:00 | 67 | 65 |  |  | 43483.2917 | 85 | 84
2019-01-18 07:30 | 72 | 70 |  |  | 43483.3125 | 94 | 94
2019-01-18 08:00 | 76 | 73 |  |  | 43483.3333 | 100 | 99
2019-01-18 08:30 | 78 | 76 |  |  | 43483.3542 | 104 | 103
2019-01-18 09:00 | 83 | 80 |  |  | 43483.375 | 109 | 107
2019-01-18 09:30 | 83 | 81 |  |  | 43483.3958 | 106 | 104
2019-01-18 10:00 | 77 | 74 |  |  | 43483.4167 | 102 | 101
2019-01-18 10:30 | 78 | 75 |  |  | 43483.4375 | 103 | 102
2019-01-18 11:00 | 82 | 80 |  |  | 43483.4583 | 106 | 105
2019-01-18 11:30 | 80 | 77 |  |  | 43483.4792 | 102 | 101
2019-01-18 12:00 | 81 | 78 |  |  | 43483.5 | 104 | 103
2019-01-18 12:30 | 84 | 81 |  |  | 43483.5208 | 107 | 106
2019-01-18 13:00 | 86 | 83 |  |  | 43483.5417 | 109 | 108
2019-01-18 13:30 | 88 | 85 |  |  | 43483.5625 | 110 | 109
2019-01-18 14:00 | 89 | 87 |  |  | 43483.5833 | 110 | 109
2019-01-18 14:30 | 90 | 88 |  |  | 43483.6042 | 112 | 111
2019-01-18 15:00 | 90 | 89 |  |  | 43483.625 | 113 | 112
2019-01-18 15:30 | 90 | 89 |  |  | 43483.6458 | 113 | 112
2019-01-18 16:00 | 92 | 90 |  |  | 43483.6667 | 114 | 113
2019-01-18 16:30 | 96 | 95 |  |  | 43483.6875 | 118 | 116
2019-01-18 17:00 | 97 | 96 |  |  | 43483.7083 | 118 | 117
2019-01-18 17:30 | 98 | 96 |  |  | 43483.7292 | 118 | 116
2019-01-18 18:00 | 96 | 94 |  |  | 43483.75 | 114 | 112
2019-01-18 18:30 | 93 | 90 |  |  | 43483.7708 | 109 | 108
2019-01-18 19:00 | 92 | 91 |  |  | 43483.7917 | 109 | 108
2019-01-18 19:30 | 92 | 91 |  |  | 43483.8125 | 109 | 108
2019-01-18 20:00 | 90 | 89 |  |  | 43483.8333 | 107 | 106
2019-01-18 20:30 | 90 | 89 |  |  | 43483.8542 | 107 | 105
2019-01-18 21:00 | 85 | 83 |  |  | 43483.875 | 101 | 100
2019-01-18 21:30 | 83 | 81 |  |  | 43483.8958 | 99 | 97
2019-01-18 22:00 | 81 | 79 |  |  | 43483.9167 | 96 | 96
2019-01-18 22:30 | 82 | 79 |  |  | 43483.9375 | 97 | 96
2019-01-18 23:00 | 76 | 73 |  |  | 43483.9583 | 90 | 90
2019-01-18 23:30 | 71 | 66 |  |  | 43483.9792 | 84 | 83
2019-01-19 | 66 | 61 |  |  | 43484 | 79 | 78
2019-01-19 00:30 | 63 | 57 |  |  | 43484.0208 | 74 | 73
2019-01-19 01:00 | 61 | 55 |  |  | 43484.0417 | 71 | 70
2019-01-19 01:30 | 60 | 54 |  |  | 43484.0625 | 70 | 68
2019-01-19 02:00 | 59 | 52 |  |  | 43484.0833 | 68 | 66
2019-01-19 02:30 | 59 | 51 |  |  | 43484.1042 | 68 | 66
2019-01-19 03:00 | 58 | 50 |  |  | 43484.125 | 66 | 64
2019-01-19 03:30 | 58 | 49 |  |  | 43484.1458 | 66 | 63
2019-01-19 04:00 | 56 | 47 |  |  | 43484.1667 | 65 | 62
2019-01-19 04:30 | 56 | 47 |  |  | 43484.1875 | 66 | 63
2019-01-19 05:00 | 57 | 48 |  |  | 43484.2083 | 66 | 63
2019-01-19 05:30 | 56 | 47 |  |  | 43484.2292 | 64 | 61
2019-01-19 06:00 | 54 | 45 |  |  | 43484.25 | 64 | 61
2019-01-19 06:30 | 55 | 46 |  |  | 43484.2708 | 66 | 64
2019-01-19 07:00 | 54 | 46 |  |  | 43484.2917 | 66 | 65
2019-01-19 07:30 | 55 | 49 |  |  | 43484.3125 | 68 | 67
2019-01-19 08:00 | 56 | 51 |  |  | 43484.3333 | 72 | 71
2019-01-19 08:30 | 61 | 55 |  |  | 43484.3542 | 76 | 75
2019-01-19 09:00 | 59 | 55 |  |  | 43484.375 | 75 | 75
2019-01-19 09:30 | 57 | 53 |  |  | 43484.3958 | 73 | 73
2019-01-19 10:00 | 59 | 55 |  |  | 43484.4167 | 77 | 76
2019-01-19 10:30 | 56 | 51 |  |  | 43484.4375 | 72 | 72
2019-01-19 11:00 | 59 | 54 |  |  | 43484.4583 | 73 | 72
2019-01-19 11:30 | 66 | 63 |  |  | 43484.4792 | 79 | 79
2019-01-19 12:00 | 67 | 64 |  |  | 43484.5 | 83 | 83
2019-01-19 12:30 | 64 | 62 |  |  | 43484.5208 | 82 | 82
2019-01-19 13:00 | 65 | 63 |  |  | 43484.5417 | 82 | 81
2019-01-19 13:30 | 66 | 64 |  |  | 43484.5625 | 81 | 81
2019-01-19 14:00 | 68 | 66 |  |  | 43484.5833 | 83 | 82
2019-01-19 14:30 | 71 | 68 |  |  | 43484.6042 | 84 | 83
2019-01-19 15:00 | 75 | 71 |  |  | 43484.625 | 88 | 85
2019-01-19 15:30 | 77 | 74 |  |  | 43484.6458 | 89 | 87
2019-01-19 16:00 | 79 | 76 |  |  | 43484.6667 | 91 | 89
2019-01-19 16:30 | 81 | 81 |  |  | 43484.6875 | 96 | 95
2019-01-19 17:00 | 85 | 85 |  |  | 43484.7083 | 101 | 100
2019-01-19 17:30 | 85 | 84 |  |  | 43484.7292 | 101 | 101
2019-01-19 18:00 | 83 | 83 |  |  | 43484.75 | 100 | 100
2019-01-19 18:30 | 82 | 82 |  |  | 43484.7708 | 100 | 100
2019-01-19 19:00 | 82 | 82 |  |  | 43484.7917 | 103 | 102
2019-01-19 19:30 | 84 | 83 |  |  | 43484.8125 | 104 | 103
2019-01-19 20:00 | 85 | 85 |  |  | 43484.8333 | 105 | 104
2019-01-19 20:30 | 85 | 85 |  |  | 43484.8542 | 103 | 103
2019-01-19 21:00 | 81 | 81 |  |  | 43484.875 | 99 | 99
2019-01-19 21:30 | 78 | 78 |  |  | 43484.8958 | 96 | 96
2019-01-19 22:00 | 76 | 76 |  |  | 43484.9167 | 94 | 94
2019-01-19 22:30 | 77 | 76 |  |  | 43484.9375 | 93 | 93
2019-01-19 23:00 | 74 | 73 |  |  | 43484.9583 | 89 | 89
2019-01-19 23:30 | 68 | 68 |  |  | 43484.9792 | 84 | 84
2019-01-20 | 64 | 63 |  |  | 43485 | 80 | 80
2019-01-20 00:30 | 60 | 60 |  |  | 43485.0208 | 75 | 75
2019-01-20 01:00 | 59 | 59 |  |  | 43485.0417 | 73 | 73
2019-01-20 01:30 | 59 | 59 |  |  | 43485.0625 | 71 | 71
2019-01-20 02:00 | 60 | 59 |  |  | 43485.0833 | 71 | 70
2019-01-20 02:30 | 57 | 56 |  |  | 43485.1042 | 69 | 69
2019-01-20 03:00 | 55 | 55 |  |  | 43485.125 | 67 | 66
2019-01-20 03:30 | 54 | 54 |  |  | 43485.1458 | 66 | 66
2019-01-20 04:00 | 53 | 52 |  |  | 43485.1667 | 65 | 64
2019-01-20 04:30 | 53 | 52 |  |  | 43485.1875 | 65 | 64
2019-01-20 05:00 | 54 | 53 |  |  | 43485.2083 | 65 | 64
2019-01-20 05:30 | 53 | 53 |  |  | 43485.2292 | 65 | 64
2019-01-20 06:00 | 52 | 51 |  |  | 43485.25 | 64 | 63
2019-01-20 06:30 | 52 | 51 |  |  | 43485.2708 | 65 | 65
2019-01-20 07:00 | 51 | 50 |  |  | 43485.2917 | 64 | 63
2019-01-20 07:30 | 52 | 51 |  |  | 43485.3125 | 67 | 67
2019-01-20 08:00 | 53 | 53 |  |  | 43485.3333 | 71 | 70
2019-01-20 08:30 | 56 | 56 |  |  | 43485.3542 | 73 | 73
2019-01-20 09:00 | 58 | 58 |  |  | 43485.375 | 75 | 75
2019-01-20 09:30 | 60 | 59 |  |  | 43485.3958 | 77 | 76
2019-01-20 10:00 | 62 | 62 |  |  | 43485.4167 | 78 | 78
2019-01-20 10:30 | 61 | 60 |  |  | 43485.4375 | 75 | 74
2019-01-20 11:00 | 60 | 60 |  |  | 43485.4583 | 75 | 74
2019-01-20 11:30 | 60 | 60 |  |  | 43485.4792 | 74 | 74
2019-01-20 12:00 | 61 | 60 |  |  | 43485.5 | 73 | 73
2019-01-20 12:30 | 62 | 61 |  |  | 43485.5208 | 74 | 73
2019-01-20 13:00 | 65 | 64 |  |  | 43485.5417 | 76 | 76
2019-01-20 13:30 | 66 | 65 |  |  | 43485.5625 | 79 | 78
2019-01-20 14:00 | 68 | 68 |  |  | 43485.5833 | 81 | 80
2019-01-20 14:30 | 72 | 71 |  |  | 43485.6042 | 84 | 82
2019-01-20 15:00 | 74 | 74 |  |  | 43485.625 | 88 | 85
2019-01-20 15:30 | 77 | 77 |  |  | 43485.6458 | 91 | 89
2019-01-20 16:00 | 79 | 79 |  |  | 43485.6667 | 93 | 91
2019-01-20 16:30 | 80 | 80 |  |  | 43485.6875 | 95 | 93
2019-01-20 17:00 | 83 | 83 |  |  | 43485.7083 | 99 | 97
2019-01-20 17:30 | 85 | 84 |  |  | 43485.7292 | 100 | 98
2019-01-20 18:00 | 85 | 84 |  |  | 43485.75 | 100 | 98
2019-01-20 18:30 | 84 | 84 |  |  | 43485.7708 | 101 | 99
2019-01-20 19:00 | 85 | 85 |  |  | 43485.7917 | 103 | 102
2019-01-20 19:30 | 87 | 86 |  |  | 43485.8125 | 104 | 104
2019-01-20 20:00 | 86 | 86 |  |  | 43485.8333 | 105 | 105
2019-01-20 20:30 | 88 | 88 |  |  | 43485.8542 | 108 | 107
2019-01-20 21:00 | 87 | 86 |  |  | 43485.875 | 105 | 105
2019-01-20 21:30 | 83 | 83 |  |  | 43485.8958 | 101 | 101
2019-01-20 22:00 | 80 | 80 |  |  | 43485.9167 | 99 | 99
2019-01-20 22:30 | 76 | 76 |  |  | 43485.9375 | 95 | 95
2019-01-20 23:00 | 73 | 73 |  |  | 43485.9583 | 90 | 90
2019-01-20 23:30 | 68 | 68 |  |  | 43485.9792 | 85 | 85
2019-01-21 | 64 | 64 |  |  | 43486 | 80 | 79
2019-01-21 00:30 | 60 | 59 |  |  | 43486.0208 | 74 | 73
2019-01-21 01:00 | 57 | 55 |  |  | 43486.0417 | 71 | 70
2019-01-21 01:30 | 56 | 55 |  |  | 43486.0625 | 71 | 70
2019-01-21 02:00 | 56 | 55 |  |  | 43486.0833 | 69 | 68
2019-01-21 02:30 | 54 | 53 |  |  | 43486.1042 | 68 | 67
2019-01-21 03:00 | 53 | 52 |  |  | 43486.125 | 68 | 66
2019-01-21 03:30 | 54 | 52 |  |  | 43486.1458 | 67 | 65
2019-01-21 04:00 | 53 | 52 |  |  | 43486.1667 | 65 | 64
2019-01-21 04:30 | 54 | 52 |  |  | 43486.1875 | 66 | 65
2019-01-21 05:00 | 55 | 54 |  |  | 43486.2083 | 68 | 67
2019-01-21 05:30 | 57 | 56 |  |  | 43486.2292 | 72 | 70
2019-01-21 06:00 | 60 | 59 |  |  | 43486.25 | 76 | 75
2019-01-21 06:30 | 68 | 68 |  |  | 43486.2708 | 87 | 87
2019-01-21 07:00 | 72 | 72 |  |  | 43486.2917 | 95 | 95
2019-01-21 07:30 | 77 | 77 |  |  | 43486.3125 | 104 | 103
2019-01-21 08:00 | 83 | 82 |  |  | 43486.3333 | 116 | 115
2019-01-21 08:30 | 86 | 85 |  |  | 43486.3542 | 121 | 120
2019-01-21 09:00 | 88 | 86 |  |  | 43486.375 | 123 | 119
2019-01-21 09:30 | 92 | 89 |  |  | 43486.3958 | 133 | 124
2019-01-21 10:00 | 91 | 87 |  |  | 43486.4167 | 130 | 121
2019-01-21 10:30 | 92 | 88 |  |  | 43486.4375 | 128 | 118
2019-01-21 11:00 | 94 | 91 |  |  | 43486.4583 | 122 | 111
2019-01-21 11:30 | 92 | 88 |  |  | 43486.4792 | 125 | 114
2019-01-21 12:00 | 94 | 89 |  |  | 43486.5 | 132 | 121
2019-01-21 12:30 | 96 | 91 |  |  | 43486.5208 | 134 | 124
2019-01-21 13:00 | 97 | 93 |  |  | 43486.5417 | 137 | 127
2019-01-21 13:30 | 99 | 94 |  |  | 43486.5625 | 139 | 128
2019-01-21 14:00 | 102 | 98 |  |  | 43486.5833 | 141 | 131
2019-01-21 14:30 | 103 | 100 |  |  | 43486.6042 | 142 | 134
2019-01-21 15:00 | 103 | 100 |  |  | 43486.625 | 142 | 134
2019-01-21 15:30 | 106 | 103 |  |  | 43486.6458 | 145 | 137
2019-01-21 16:00 | 108 | 105 |  |  | 43486.6667 | 146 | 138
2019-01-21 16:30 | 110 | 106 |  |  | 43486.6875 | 149 | 138
2019-01-21 17:00 | 115 | 111 |  |  | 43486.7083 | 153 | 142
2019-01-21 17:30 | 114 | 110 |  |  | 43486.7292 | 149 | 138
2019-01-21 18:00 | 110 | 108 |  |  | 43486.75 | 143 | 135
2019-01-21 18:30 | 106 | 105 |  |  | 43486.7708 | 141 | 130
2019-01-21 19:00 | 104 | 103 |  |  | 43486.7917 | 138 | 128
2019-01-21 19:30 | 104 | 104 |  |  | 43486.8125 | 139 | 129
2019-01-21 20:00 | 104 | 104 |  |  | 43486.8333 | 134 | 127
2019-01-21 20:30 | 103 | 103 |  |  | 43486.8542 | 134 | 126
2019-01-21 21:00 | 101 | 101 |  |  | 43486.875 | 125 | 122
2019-01-21 21:30 | 96 | 95 |  |  | 43486.8958 | 116 | 114
2019-01-21 22:00 | 93 | 93 |  |  | 43486.9167 | 114 | 112
2019-01-21 22:30 | 89 | 89 |  |  | 43486.9375 | 111 | 108
2019-01-21 23:00 | 83 | 83 |  |  | 43486.9583 | 102 | 101
2019-01-21 23:30 | 76 | 76 |  |  | 43486.9792 | 96 | 95
2019-01-22 | 71 | 71 |  |  | 43487 | 91 | 89
2019-01-22 00:30 | 66 | 66 |  |  | 43487.0208 | 85 | 83
2019-01-22 01:00 | 62 | 62 |  |  | 43487.0417 | 80 | 78
2019-01-22 01:30 | 60 | 60 |  |  | 43487.0625 | 77 | 75
2019-01-22 02:00 | 58 | 58 |  |  | 43487.0833 | 77 | 74
2019-01-22 02:30 | 56 | 56 |  |  | 43487.1042 | 75 | 72
2019-01-22 03:00 | 54 | 54 |  |  | 43487.125 | 73 | 70
2019-01-22 03:30 | 54 | 54 |  |  | 43487.1458 | 73 | 70
2019-01-22 04:00 | 52 | 52 |  |  | 43487.1667 | 71 | 68
2019-01-22 04:30 | 53 | 53 |  |  | 43487.1875 | 73 | 69
2019-01-22 05:00 | 58 | 58 |  |  | 43487.2083 | 76 | 72
2019-01-22 05:30 | 59 | 59 |  |  | 43487.2292 | 78 | 75
2019-01-22 06:00 | 61 | 61 |  |  | 43487.25 | 81 | 79
2019-01-22 06:30 | 67 | 67 |  |  | 43487.2708 | 90 | 88
2019-01-22 07:00 | 74 | 74 |  |  | 43487.2917 | 99 | 98
2019-01-22 07:30 | 83 | 82 |  |  | 43487.3125 | 110 | 109
2019-01-22 08:00 | 87 | 86 |  |  | 43487.3333 | 116 | 116
2019-01-22 08:30 | 89 | 89 |  |  | 43487.3542 | 121 | 121
2019-01-22 09:00 | 90 | 90 |  |  | 43487.375 | 123 | 123
2019-01-22 09:30 | 90 | 89 |  |  | 43487.3958 | 121 | 121
2019-01-22 10:00 | 83 | 83 |  |  | 43487.4167 | 108 | 108
2019-01-22 10:30 | 82 | 82 |  |  | 43487.4375 | 106 | 106
2019-01-22 11:00 | 76 | 75 |  |  | 43487.4583 | 104 | 104
2019-01-22 11:30 | 72 | 72 |  |  | 43487.4792 | 104 | 104
2019-01-22 12:00 | 71 | 71 |  |  | 43487.5 | 102 | 102
2019-01-22 12:30 | 72 | 72 |  |  | 43487.5208 | 100 | 100
2019-01-22 13:00 | 75 | 74 |  |  | 43487.5417 | 101 | 101
2019-01-22 13:30 | 74 | 74 |  |  | 43487.5625 | 102 | 102
2019-01-22 14:00 | 88 | 88 |  |  | 43487.5833 | 110 | 110
2019-01-22 14:30 | 88 | 88 |  |  | 43487.6042 | 113 | 113
2019-01-22 15:00 | 90 | 90 |  |  | 43487.625 | 115 | 115
2019-01-22 15:30 | 91 | 91 |  |  | 43487.6458 | 117 | 117
2019-01-22 16:00 | 96 | 95 |  |  | 43487.6667 | 120 | 120
2019-01-22 16:30 | 106 | 98 |  |  | 43487.6875 | 125 | 124
2019-01-22 17:00 | 109 | 101 |  |  | 43487.7083 | 127 | 126
2019-01-22 17:30 | 112 | 102 |  |  | 43487.7292 | 123 | 123
2019-01-22 18:00 | 104 | 97 |  |  | 43487.75 | 112 | 112
2019-01-22 18:30 | 102 | 95 |  |  | 43487.7708 | 109 | 109
2019-01-22 19:00 | 101 | 96 |  |  | 43487.7917 | 111 | 111
2019-01-22 19:30 | 103 | 98 |  |  | 43487.8125 | 113 | 113
2019-01-22 20:00 | 101 | 96 |  |  | 43487.8333 | 112 | 112
2019-01-22 20:30 | 100 | 95 |  |  | 43487.8542 | 111 | 110
2019-01-22 21:00 | 96 | 92 |  |  | 43487.875 | 106 | 105
2019-01-22 21:30 | 92 | 87 |  |  | 43487.8958 | 102 | 101
2019-01-22 22:00 | 89 | 85 |  |  | 43487.9167 | 99 | 99
2019-01-22 22:30 | 86 | 83 |  |  | 43487.9375 | 95 | 95
2019-01-22 23:00 | 81 | 77 |  |  | 43487.9583 | 88 | 88
2019-01-22 23:30 | 73 | 70 |  |  | 43487.9792 | 83 | 82
2019-01-23 | 63 | 63 |  |  | 43488 | 76 | 74
2019-01-23 00:30 | 58 | 57 |  |  | 43488.0208 | 71 | 68
2019-01-23 01:00 | 57 | 56 |  |  | 43488.0417 | 70 | 66
2019-01-23 01:30 | 56 | 56 |  |  | 43488.0625 | 69 | 65
2019-01-23 02:00 | 54 | 54 |  |  | 43488.0833 | 67 | 63
2019-01-23 02:30 | 53 | 52 |  |  | 43488.1042 | 65 | 62
2019-01-23 03:00 | 51 | 50 |  |  | 43488.125 | 64 | 60
2019-01-23 03:30 | 50 | 49 |  |  | 43488.1458 | 63 | 59
2019-01-23 04:00 | 50 | 49 |  |  | 43488.1667 | 63 | 59
2019-01-23 04:30 | 50 | 50 |  |  | 43488.1875 | 64 | 59
2019-01-23 05:00 | 52 | 51 |  |  | 43488.2083 | 66 | 62
2019-01-23 05:30 | 52 | 51 |  |  | 43488.2292 | 67 | 63
2019-01-23 06:00 | 55 | 55 |  |  | 43488.25 | 71 | 68
2019-01-23 06:30 | 63 | 62 |  |  | 43488.2708 | 81 | 79
2019-01-23 07:00 | 67 | 67 |  |  | 43488.2917 | 87 | 86
2019-01-23 07:30 | 75 | 75 |  |  | 43488.3125 | 99 | 98
2019-01-23 08:00 | 77 | 77 |  |  | 43488.3333 | 104 | 104
2019-01-23 08:30 | 78 | 78 |  |  | 43488.3542 | 107 | 106
2019-01-23 09:00 | 80 | 80 |  |  | 43488.375 | 106 | 106
2019-01-23 09:30 | 79 | 79 |  |  | 43488.3958 | 107 | 106
2019-01-23 10:00 | 80 | 79 |  |  | 43488.4167 | 106 | 106
2019-01-23 10:30 | 78 | 77 |  |  | 43488.4375 | 103 | 103
2019-01-23 11:00 | 84 | 83 |  |  | 43488.4583 | 107 | 107
2019-01-23 11:30 | 77 | 76 |  |  | 43488.4792 | 105 | 105
2019-01-23 12:00 | 77 | 76 |  |  | 43488.5 | 104 | 103
2019-01-23 12:30 | 84 | 84 |  |  | 43488.5208 | 111 | 109
2019-01-23 13:00 | 82 | 82 |  |  | 43488.5417 | 109 | 107
2019-01-23 13:30 | 85 | 85 |  |  | 43488.5625 | 110 | 108
2019-01-23 14:00 | 86 | 85 |  |  | 43488.5833 | 111 | 109
2019-01-23 14:30 | 90 | 90 |  |  | 43488.6042 | 122 | 113
2019-01-23 15:00 | 92 | 92 |  |  | 43488.625 | 124 | 115
2019-01-23 15:30 | 92 | 92 |  |  | 43488.6458 | 124 | 114
2019-01-23 16:00 | 96 | 96 |  |  | 43488.6667 | 133 | 123
2019-01-23 16:30 | 93 | 93 |  |  | 43488.6875 | 132 | 121
2019-01-23 17:00 | 97 | 97 |  |  | 43488.7083 | 136 | 124
2019-01-23 17:30 | 95 | 95 |  |  | 43488.7292 | 134 | 120
2019-01-23 18:00 | 91 | 90 |  |  | 43488.75 | 127 | 112
2019-01-23 18:30 | 89 | 89 |  |  | 43488.7708 | 117 | 109
2019-01-23 19:00 | 91 | 91 |  |  | 43488.7917 | 116 | 110
2019-01-23 19:30 | 90 | 90 |  |  | 43488.8125 | 115 | 110
2019-01-23 20:00 | 89 | 89 |  |  | 43488.8333 | 113 | 107
2019-01-23 20:30 | 86 | 86 |  |  | 43488.8542 | 111 | 105
2019-01-23 21:00 | 92 | 92 |  |  | 43488.875 | 109 | 105
2019-01-23 21:30 | 88 | 88 |  |  | 43488.8958 | 100 | 99
2019-01-23 22:00 | 83 | 83 |  |  | 43488.9167 | 97 | 95
2019-01-23 22:30 | 81 | 81 |  |  | 43488.9375 | 94 | 93
2019-01-23 23:00 | 74 | 74 |  |  | 43488.9583 | 88 | 87
2019-01-23 23:30 | 71 | 70 |  |  | 43488.9792 | 84 | 83
2019-01-24 | 66 | 65 |  |  | 43489 | 80 | 79
2019-01-24 00:30 | 61 | 61 |  |  | 43489.0208 | 74 | 73
2019-01-24 01:00 | 59 | 59 |  |  | 43489.0417 | 71 | 69
2019-01-24 01:30 | 56 | 56 |  |  | 43489.0625 | 68 | 66
2019-01-24 02:00 | 54 | 54 |  |  | 43489.0833 | 67 | 65
2019-01-24 02:30 | 54 | 54 |  |  | 43489.1042 | 67 | 65
2019-01-24 03:00 | 52 | 52 |  |  | 43489.125 | 66 | 64
2019-01-24 03:30 | 51 | 51 |  |  | 43489.1458 | 65 | 62
2019-01-24 04:00 | 51 | 51 |  |  | 43489.1667 | 65 | 62
2019-01-24 04:30 | 51 | 51 |  |  | 43489.1875 | 66 | 63
2019-01-24 05:00 | 52 | 52 |  |  | 43489.2083 | 68 | 65
2019-01-24 05:30 | 55 | 55 |  |  | 43489.2292 | 70 | 68
2019-01-24 06:00 | 57 | 56 |  |  | 43489.25 | 73 | 72
2019-01-24 06:30 | 64 | 64 |  |  | 43489.2708 | 82 | 81
2019-01-24 07:00 | 68 | 68 |  |  | 43489.2917 | 89 | 89
2019-01-24 07:30 | 74 | 74 |  |  | 43489.3125 | 98 | 98
2019-01-24 08:00 | 74 | 74 |  |  | 43489.3333 | 102 | 102
2019-01-24 08:30 | 62 | 62 |  |  | 43489.3542 | 97 | 97
2019-01-24 09:00 | 62 | 61 |  |  | 43489.375 | 97 | 97
2019-01-24 09:30 | 63 | 62 |  |  | 43489.3958 | 97 | 97
2019-01-24 10:00 | 66 | 65 |  |  | 43489.4167 | 97 | 97
2019-01-24 10:30 | 66 | 65 |  |  | 43489.4375 | 97 | 97
2019-01-24 11:00 | 70 | 69 |  |  | 43489.4583 | 100 | 100
2019-01-24 11:30 | 73 | 73 |  |  | 43489.4792 | 103 | 103
2019-01-24 12:00 | 87 | 87 |  |  | 43489.5 | 112 | 111
2019-01-24 12:30 | 93 | 93 |  |  | 43489.5208 | 115 | 115
2019-01-24 13:00 | 92 | 92 |  |  | 43489.5417 | 112 | 111
2019-01-24 13:30 | 93 | 93 |  |  | 43489.5625 | 114 | 114
2019-01-24 14:00 | 89 | 89 |  |  | 43489.5833 | 111 | 111
2019-01-24 14:30 | 91 | 90 |  |  | 43489.6042 | 116 | 116
2019-01-24 15:00 | 95 | 94 |  |  | 43489.625 | 118 | 118
2019-01-24 15:30 | 98 | 98 |  |  | 43489.6458 | 122 | 122
2019-01-24 16:00 | 98 | 98 |  |  | 43489.6667 | 122 | 121
2019-01-24 16:30 | 102 | 101 |  |  | 43489.6875 | 128 | 123
2019-01-24 17:00 | 104 | 103 |  |  | 43489.7083 | 129 | 123
2019-01-24 17:30 | 97 | 96 |  |  | 43489.7292 | 127 | 120
2019-01-24 18:00 | 96 | 95 |  |  | 43489.75 | 126 | 118
2019-01-24 18:30 | 96 | 94 |  |  | 43489.7708 | 123 | 115
2019-01-24 19:00 | 95 | 93 |  |  | 43489.7917 | 122 | 114
2019-01-24 19:30 | 94 | 92 |  |  | 43489.8125 | 123 | 113
2019-01-24 20:00 | 94 | 91 |  |  | 43489.8333 | 122 | 113
2019-01-24 20:30 | 92 | 91 |  |  | 43489.8542 | 116 | 111
2019-01-24 21:00 | 88 | 87 |  |  | 43489.875 | 107 | 105
2019-01-24 21:30 | 81 | 81 |  |  | 43489.8958 | 100 | 98
2019-01-24 22:00 | 79 | 78 |  |  | 43489.9167 | 99 | 97
2019-01-24 22:30 | 83 | 83 |  |  | 43489.9375 | 97 | 97
2019-01-24 23:00 | 81 | 81 |  |  | 43489.9583 | 92 | 92
2019-01-24 23:30 | 76 | 75 |  |  | 43489.9792 | 88 | 87
2019-01-25 | 70 | 70 |  |  | 43490 | 83 | 83
2019-01-25 00:30 | 67 | 66 |  |  | 43490.0208 | 78 | 77
2019-01-25 01:00 | 63 | 62 |  |  | 43490.0417 | 73 | 73
2019-01-25 01:30 | 61 | 60 |  |  | 43490.0625 | 70 | 70
2019-01-25 02:00 | 60 | 58 |  |  | 43490.0833 | 70 | 69
2019-01-25 02:30 | 58 | 56 |  |  | 43490.1042 | 67 | 67
2019-01-25 03:00 | 57 | 55 |  |  | 43490.125 | 66 | 66
2019-01-25 03:30 | 54 | 52 |  |  | 43490.1458 | 65 | 64
2019-01-25 04:00 | 54 | 52 |  |  | 43490.1667 | 66 | 65
2019-01-25 04:30 | 57 | 55 |  |  | 43490.1875 | 67 | 66
2019-01-25 05:00 | 59 | 57 |  |  | 43490.2083 | 69 | 68
2019-01-25 05:30 | 61 | 59 |  |  | 43490.2292 | 73 | 73
2019-01-25 06:00 | 62 | 60 |  |  | 43490.25 | 77 | 76
2019-01-25 06:30 | 68 | 67 |  |  | 43490.2708 | 86 | 86
2019-01-25 07:00 | 70 | 70 |  |  | 43490.2917 | 92 | 91
2019-01-25 07:30 | 76 | 75 |  |  | 43490.3125 | 101 | 101
2019-01-25 08:00 | 81 | 81 |  |  | 43490.3333 | 107 | 107
2019-01-25 08:30 | 83 | 83 |  |  | 43490.3542 | 110 | 110
2019-01-25 09:00 | 83 | 83 |  |  | 43490.375 | 111 | 111
2019-01-25 09:30 | 84 | 84 |  |  | 43490.3958 | 114 | 114
2019-01-25 10:00 | 87 | 87 |  |  | 43490.4167 | 116 | 116
2019-01-25 10:30 | 88 | 88 |  |  | 43490.4375 | 117 | 117
2019-01-25 11:00 | 82 | 82 |  |  | 43490.4583 | 112 | 112
2019-01-25 11:30 | 75 | 75 |  |  | 43490.4792 | 103 | 102
2019-01-25 12:00 | 75 | 75 |  |  | 43490.5 | 101 | 101
2019-01-25 12:30 | 74 | 74 |  |  | 43490.5208 | 102 | 101
2019-01-25 13:00 | 80 | 80 |  |  | 43490.5417 | 106 | 105
2019-01-25 13:30 | 85 | 85 |  |  | 43490.5625 | 107 | 107
2019-01-25 14:00 | 84 | 84 |  |  | 43490.5833 | 107 | 107
2019-01-25 14:30 | 80 | 80 |  |  | 43490.6042 | 107 | 107
2019-01-25 15:00 | 82 | 82 |  |  | 43490.625 | 110 | 109
2019-01-25 15:30 | 85 | 85 |  |  | 43490.6458 | 111 | 110
2019-01-25 16:00 | 87 | 87 |  |  | 43490.6667 | 112 | 112
2019-01-25 16:30 | 89 | 89 |  |  | 43490.6875 | 113 | 113
2019-01-25 17:00 | 99 | 96 |  |  | 43490.7083 | 119 | 119
2019-01-25 17:30 | 101 | 96 |  |  | 43490.7292 | 118 | 118
2019-01-25 18:00 | 101 | 97 |  |  | 43490.75 | 115 | 115
2019-01-25 18:30 | 91 | 89 |  |  | 43490.7708 | 107 | 107
2019-01-25 19:00 | 89 | 88 |  |  | 43490.7917 | 107 | 107
2019-01-25 19:30 | 88 | 88 |  |  | 43490.8125 | 108 | 107
2019-01-25 20:00 | 85 | 85 |  |  | 43490.8333 | 107 | 103
2019-01-25 20:30 | 86 | 85 |  |  | 43490.8542 | 106 | 103
2019-01-25 21:00 | 84 | 82 |  |  | 43490.875 | 99 | 99
2019-01-25 21:30 | 82 | 81 |  |  | 43490.8958 | 99 | 98
2019-01-25 22:00 | 81 | 81 |  |  | 43490.9167 | 98 | 97
2019-01-25 22:30 | 78 | 78 |  |  | 43490.9375 | 95 | 94
2019-01-25 23:00 | 74 | 74 |  |  | 43490.9583 | 90 | 88
2019-01-25 23:30 | 68 | 68 |  |  | 43490.9792 | 86 | 83
2019-01-26 | 64 | 64 |  |  | 43491 | 81 | 78
2019-01-26 00:30 | 63 | 62 |  |  | 43491.0208 | 78 | 74
2019-01-26 01:00 | 58 | 57 |  |  | 43491.0417 | 73 | 70
2019-01-26 01:30 | 59 | 56 |  |  | 43491.0625 | 69 | 69
2019-01-26 02:00 | 58 | 54 |  |  | 43491.0833 | 68 | 67
2019-01-26 02:30 | 57 | 53 |  |  | 43491.1042 | 67 | 66
2019-01-26 03:00 | 55 | 51 |  |  | 43491.125 | 65 | 64
2019-01-26 03:30 | 54 | 50 |  |  | 43491.1458 | 65 | 64
2019-01-26 04:00 | 53 | 49 |  |  | 43491.1667 | 65 | 63
2019-01-26 04:30 | 53 | 48 |  |  | 43491.1875 | 64 | 63
2019-01-26 05:00 | 54 | 49 |  |  | 43491.2083 | 65 | 64
2019-01-26 05:30 | 54 | 49 |  |  | 43491.2292 | 65 | 64
2019-01-26 06:00 | 53 | 49 |  |  | 43491.25 | 65 | 63
2019-01-26 06:30 | 53 | 49 |  |  | 43491.2708 | 66 | 65
2019-01-26 07:00 | 53 | 49 |  |  | 43491.2917 | 67 | 66
2019-01-26 07:30 | 55 | 52 |  |  | 43491.3125 | 69 | 68
2019-01-26 08:00 | 54 | 52 |  |  | 43491.3333 | 70 | 70
2019-01-26 08:30 | 56 | 54 |  |  | 43491.3542 | 74 | 74
2019-01-26 09:00 | 58 | 57 |  |  | 43491.375 | 77 | 77
2019-01-26 09:30 | 57 | 55 |  |  | 43491.3958 | 75 | 75
2019-01-26 10:00 | 55 | 53 |  |  | 43491.4167 | 71 | 71
2019-01-26 10:30 | 51 | 50 |  |  | 43491.4375 | 67 | 67
2019-01-26 11:00 | 52 | 50 |  |  | 43491.4583 | 66 | 66
2019-01-26 11:30 | 52 | 51 |  |  | 43491.4792 | 68 | 67
2019-01-26 12:00 | 56 | 55 |  |  | 43491.5 | 68 | 68
2019-01-26 12:30 | 55 | 54 |  |  | 43491.5208 | 69 | 69
2019-01-26 13:00 | 54 | 54 |  |  | 43491.5417 | 69 | 69
2019-01-26 13:30 | 57 | 56 |  |  | 43491.5625 | 72 | 72
2019-01-26 14:00 | 60 | 59 |  |  | 43491.5833 | 74 | 74
2019-01-26 14:30 | 61 | 61 |  |  | 43491.6042 | 75 | 75
2019-01-26 15:00 | 64 | 62 |  |  | 43491.625 | 79 | 78
2019-01-26 15:30 | 68 | 64 |  |  | 43491.6458 | 86 | 81
2019-01-26 16:00 | 70 | 67 |  |  | 43491.6667 | 89 | 84
2019-01-26 16:30 | 73 | 70 |  |  | 43491.6875 | 92 | 87
2019-01-26 17:00 | 77 | 74 |  |  | 43491.7083 | 96 | 91
2019-01-26 17:30 | 78 | 75 |  |  | 43491.7292 | 96 | 91
2019-01-26 18:00 | 78 | 75 |  |  | 43491.75 | 98 | 92
2019-01-26 18:30 | 78 | 75 |  |  | 43491.7708 | 95 | 91
2019-01-26 19:00 | 74 | 74 |  |  | 43491.7917 | 91 | 91
2019-01-26 19:30 | 76 | 75 |  |  | 43491.8125 | 92 | 92
2019-01-26 20:00 | 75 | 75 |  |  | 43491.8333 | 92 | 92
2019-01-26 20:30 | 73 | 73 |  |  | 43491.8542 | 90 | 90
2019-01-26 21:00 | 74 | 73 |  |  | 43491.875 | 89 | 89
2019-01-26 21:30 | 73 | 72 |  |  | 43491.8958 | 88 | 88
2019-01-26 22:00 | 72 | 72 |  |  | 43491.9167 | 88 | 88
2019-01-26 22:30 | 74 | 73 |  |  | 43491.9375 | 87 | 86
2019-01-26 23:00 | 71 | 69 |  |  | 43491.9583 | 82 | 82
2019-01-26 23:30 | 68 | 67 |  |  | 43491.9792 | 80 | 79
2019-01-27 | 64 | 62 |  |  | 43492 | 75 | 74
2019-01-27 00:30 | 58 | 55 |  |  | 43492.0208 | 69 | 68
2019-01-27 01:00 | 54 | 51 |  |  | 43492.0417 | 64 | 63
2019-01-27 01:30 | 52 | 49 |  |  | 43492.0625 | 63 | 61
2019-01-27 02:00 | 52 | 48 |  |  | 43492.0833 | 62 | 60
2019-01-27 02:30 | 51 | 46 |  |  | 43492.1042 | 59 | 58
2019-01-27 03:00 | 50 | 45 |  |  | 43492.125 | 59 | 58
2019-01-27 03:30 | 50 | 45 |  |  | 43492.1458 | 58 | 56
2019-01-27 04:00 | 49 | 44 |  |  | 43492.1667 | 57 | 55
2019-01-27 04:30 | 49 | 43 |  |  | 43492.1875 | 57 | 55
2019-01-27 05:00 | 49 | 43 |  |  | 43492.2083 | 56 | 54
2019-01-27 05:30 | 48 | 42 |  |  | 43492.2292 | 55 | 53
2019-01-27 06:00 | 47 | 41 |  |  | 43492.25 | 56 | 54
2019-01-27 06:30 | 45 | 39 |  |  | 43492.2708 | 55 | 53
2019-01-27 07:00 | 43 | 38 |  |  | 43492.2917 | 55 | 53
2019-01-27 07:30 | 43 | 39 |  |  | 43492.3125 | 56 | 55
2019-01-27 08:00 | 45 | 41 |  |  | 43492.3333 | 58 | 57
2019-01-27 08:30 | 47 | 44 |  |  | 43492.3542 | 62 | 61
2019-01-27 09:00 | 47 | 45 |  |  | 43492.375 | 62 | 62
2019-01-27 09:30 | 49 | 47 |  |  | 43492.3958 | 64 | 64
2019-01-27 10:00 | 49 | 47 |  |  | 43492.4167 | 63 | 63
2019-01-27 10:30 | 48 | 47 |  |  | 43492.4375 | 62 | 62
2019-01-27 11:00 | 49 | 48 |  |  | 43492.4583 | 62 | 62
2019-01-27 11:30 | 49 | 48 |  |  | 43492.4792 | 61 | 61
2019-01-27 12:00 | 52 | 52 |  |  | 43492.5 | 65 | 65
2019-01-27 12:30 | 55 | 54 |  |  | 43492.5208 | 66 | 66
2019-01-27 13:00 | 57 | 56 |  |  | 43492.5417 | 67 | 67
2019-01-27 13:30 | 58 | 57 |  |  | 43492.5625 | 69 | 69
2019-01-27 14:00 | 60 | 59 |  |  | 43492.5833 | 71 | 71
2019-01-27 14:30 | 62 | 61 |  |  | 43492.6042 | 73 | 73
2019-01-27 15:00 | 64 | 63 |  |  | 43492.625 | 75 | 75
2019-01-27 15:30 | 64 | 63 |  |  | 43492.6458 | 77 | 77
2019-01-27 16:00 | 69 | 67 |  |  | 43492.6667 | 81 | 81
2019-01-27 16:30 | 73 | 72 |  |  | 43492.6875 | 85 | 85
2019-01-27 17:00 | 75 | 73 |  |  | 43492.7083 | 88 | 88
2019-01-27 17:30 | 76 | 76 |  |  | 43492.7292 | 90 | 89
2019-01-27 18:00 | 76 | 76 |  |  | 43492.75 | 90 | 90
2019-01-27 18:30 | 75 | 75 |  |  | 43492.7708 | 90 | 89
2019-01-27 19:00 | 75 | 75 |  |  | 43492.7917 | 91 | 91
2019-01-27 19:30 | 76 | 76 |  |  | 43492.8125 | 92 | 92
2019-01-27 20:00 | 75 | 75 |  |  | 43492.8333 | 92 | 92
2019-01-27 20:30 | 74 | 74 |  |  | 43492.8542 | 91 | 91
2019-01-27 21:00 | 73 | 73 |  |  | 43492.875 | 90 | 90
2019-01-27 21:30 | 72 | 72 |  |  | 43492.8958 | 89 | 89
2019-01-27 22:00 | 73 | 73 |  |  | 43492.9167 | 89 | 89
2019-01-27 22:30 | 69 | 69 |  |  | 43492.9375 | 86 | 86
2019-01-27 23:00 | 64 | 64 |  |  | 43492.9583 | 80 | 80
2019-01-27 23:30 | 61 | 60 |  |  | 43492.9792 | 76 | 75
2019-01-28 | 57 | 54 |  |  | 43493 | 70 | 69
2019-01-28 00:30 | 54 | 51 |  |  | 43493.0208 | 65 | 65
2019-01-28 01:00 | 53 | 49 |  |  | 43493.0417 | 63 | 62
2019-01-28 01:30 | 51 | 47 |  |  | 43493.0625 | 61 | 60
2019-01-28 02:00 | 51 | 46 |  |  | 43493.0833 | 61 | 60
2019-01-28 02:30 | 50 | 45 |  |  | 43493.1042 | 61 | 59
2019-01-28 03:00 | 50 | 44 |  |  | 43493.125 | 60 | 58
2019-01-28 03:30 | 50 | 44 |  |  | 43493.1458 | 59 | 57
2019-01-28 04:00 | 49 | 43 |  |  | 43493.1667 | 58 | 56
2019-01-28 04:30 | 48 | 42 |  |  | 43493.1875 | 57 | 55
2019-01-28 05:00 | 48 | 41 |  |  | 43493.2083 | 57 | 55
2019-01-28 05:30 | 48 | 41 |  |  | 43493.2292 | 58 | 56
2019-01-28 06:00 | 48 | 41 |  |  | 43493.25 | 59 | 57
2019-01-28 06:30 | 46 | 41 |  |  | 43493.2708 | 61 | 60
2019-01-28 07:00 | 48 | 43 |  |  | 43493.2917 | 64 | 63
2019-01-28 07:30 | 50 | 47 |  |  | 43493.3125 | 68 | 67
2019-01-28 08:00 | 53 | 50 |  |  | 43493.3333 | 71 | 70
2019-01-28 08:30 | 57 | 53 |  |  | 43493.3542 | 73 | 71
2019-01-28 09:00 | 58 | 54 |  |  | 43493.375 | 75 | 74
2019-01-28 09:30 | 59 | 56 |  |  | 43493.3958 | 76 | 75
2019-01-28 10:00 | 60 | 57 |  |  | 43493.4167 | 76 | 76
2019-01-28 10:30 | 58 | 55 |  |  | 43493.4375 | 74 | 74
2019-01-28 11:00 | 58 | 57 |  |  | 43493.4583 | 73 | 73
2019-01-28 11:30 | 55 | 54 |  |  | 43493.4792 | 71 | 71
2019-01-28 12:00 | 57 | 55 |  |  | 43493.5 | 72 | 72
2019-01-28 12:30 | 60 | 59 |  |  | 43493.5208 | 75 | 74
2019-01-28 13:00 | 60 | 59 |  |  | 43493.5417 | 76 | 75
2019-01-28 13:30 | 61 | 61 |  |  | 43493.5625 | 77 | 77
2019-01-28 14:00 | 63 | 63 |  |  | 43493.5833 | 80 | 80
2019-01-28 14:30 | 66 | 66 |  |  | 43493.6042 | 83 | 83
2019-01-28 15:00 | 68 | 67 |  |  | 43493.625 | 84 | 83
2019-01-28 15:30 | 70 | 69 |  |  | 43493.6458 | 86 | 86
2019-01-28 16:00 | 72 | 72 |  |  | 43493.6667 | 89 | 89
2019-01-28 16:30 | 77 | 77 |  |  | 43493.6875 | 94 | 94
2019-01-28 17:00 | 83 | 83 |  |  | 43493.7083 | 100 | 99
2019-01-28 17:30 | 85 | 85 |  |  | 43493.7292 | 103 | 102
2019-01-28 18:00 | 84 | 84 |  |  | 43493.75 | 101 | 100
2019-01-28 18:30 | 83 | 82 |  |  | 43493.7708 | 99 | 98
2019-01-28 19:00 | 84 | 83 |  |  | 43493.7917 | 102 | 101
2019-01-28 19:30 | 86 | 86 |  |  | 43493.8125 | 104 | 103
2019-01-28 20:00 | 88 | 88 |  |  | 43493.8333 | 105 | 105
2019-01-28 20:30 | 89 | 89 |  |  | 43493.8542 | 105 | 105
2019-01-28 21:00 | 87 | 87 |  |  | 43493.875 | 102 | 101
2019-01-28 21:30 | 81 | 81 |  |  | 43493.8958 | 97 | 96
2019-01-28 22:00 | 79 | 78 |  |  | 43493.9167 | 96 | 96
2019-01-28 22:30 | 75 | 75 |  |  | 43493.9375 | 93 | 93
2019-01-28 23:00 | 71 | 70 |  |  | 43493.9583 | 88 | 88
2019-01-28 23:30 | 67 | 67 |  |  | 43493.9792 | 83 | 83
2019-01-29 | 62 | 61 |  |  | 43494 | 78 | 78
2019-01-29 00:30 | 57 | 55 |  |  | 43494.0208 | 70 | 69
2019-01-29 01:00 | 55 | 52 |  |  | 43494.0417 | 66 | 66
2019-01-29 01:30 | 53 | 50 |  |  | 43494.0625 | 64 | 63
2019-01-29 02:00 | 54 | 50 |  |  | 43494.0833 | 63 | 62
2019-01-29 02:30 | 53 | 49 |  |  | 43494.1042 | 63 | 62
2019-01-29 03:00 | 51 | 48 |  |  | 43494.125 | 62 | 60
2019-01-29 03:30 | 51 | 47 |  |  | 43494.1458 | 62 | 61
2019-01-29 04:00 | 51 | 47 |  |  | 43494.1667 | 62 | 61
2019-01-29 04:30 | 51 | 47 |  |  | 43494.1875 | 62 | 61
2019-01-29 05:00 | 53 | 49 |  |  | 43494.2083 | 65 | 64
2019-01-29 05:30 | 55 | 52 |  |  | 43494.2292 | 68 | 67
2019-01-29 06:00 | 56 | 54 |  |  | 43494.25 | 72 | 71
2019-01-29 06:30 | 61 | 61 |  |  | 43494.2708 | 82 | 82
2019-01-29 07:00 | 65 | 65 |  |  | 43494.2917 | 89 | 89
2019-01-29 07:30 | 74 | 73 |  |  | 43494.3125 | 102 | 101
2019-01-29 08:00 | 79 | 79 |  |  | 43494.3333 | 108 | 107
2019-01-29 08:30 | 73 | 72 |  |  | 43494.3542 | 98 | 98
2019-01-29 09:00 | 70 | 70 |  |  | 43494.375 | 91 | 91
2019-01-29 09:30 | 73 | 72 |  |  | 43494.3958 | 93 | 92
2019-01-29 10:00 | 72 | 72 |  |  | 43494.4167 | 91 | 90
2019-01-29 10:30 | 73 | 72 |  |  | 43494.4375 | 89 | 89
2019-01-29 11:00 | 71 | 71 |  |  | 43494.4583 | 87 | 87
2019-01-29 11:30 | 62 | 62 |  |  | 43494.4792 | 87 | 87
2019-01-29 12:00 | 64 | 64 |  |  | 43494.5 | 88 | 88
2019-01-29 12:30 | 65 | 65 |  |  | 43494.5208 | 88 | 88
2019-01-29 13:00 | 64 | 64 |  |  | 43494.5417 | 88 | 88
2019-01-29 13:30 | 66 | 66 |  |  | 43494.5625 | 91 | 91
2019-01-29 14:00 | 73 | 73 |  |  | 43494.5833 | 100 | 99
2019-01-29 14:30 | 82 | 82 |  |  | 43494.6042 | 111 | 110
2019-01-29 15:00 | 85 | 85 |  |  | 43494.625 | 113 | 112
2019-01-29 15:30 | 86 | 86 |  |  | 43494.6458 | 113 | 112
2019-01-29 16:00 | 92 | 92 |  |  | 43494.6667 | 117 | 116
2019-01-29 16:30 | 93 | 93 |  |  | 43494.6875 | 119 | 117
2019-01-29 17:00 | 96 | 95 |  |  | 43494.7083 | 120 | 118
2019-01-29 17:30 | 94 | 93 |  |  | 43494.7292 | 117 | 115
2019-01-29 18:00 | 92 | 91 |  |  | 43494.75 | 114 | 112
2019-01-29 18:30 | 88 | 87 |  |  | 43494.7708 | 109 | 106
2019-01-29 19:00 | 89 | 88 |  |  | 43494.7917 | 110 | 107
2019-01-29 19:30 | 91 | 91 |  |  | 43494.8125 | 112 | 110
2019-01-29 20:00 | 93 | 92 |  |  | 43494.8333 | 112 | 109
2019-01-29 20:30 | 91 | 90 |  |  | 43494.8542 | 108 | 107
2019-01-29 21:00 | 88 | 87 |  |  | 43494.875 | 105 | 103
2019-01-29 21:30 | 86 | 85 |  |  | 43494.8958 | 103 | 99
2019-01-29 22:00 | 83 | 82 |  |  | 43494.9167 | 101 | 97
2019-01-29 22:30 | 78 | 77 |  |  | 43494.9375 | 94 | 92
2019-01-29 23:00 | 71 | 70 |  |  | 43494.9583 | 85 | 83
2019-01-29 23:30 | 65 | 63 |  |  | 43494.9792 | 80 | 78
2019-01-30 | 60 | 58 |  |  | 43495 | 76 | 74
2019-01-30 00:30 | 59 | 56 |  |  | 43495.0208 | 73 | 70
2019-01-30 01:00 | 55 | 53 |  |  | 43495.0417 | 68 | 66
2019-01-30 01:30 | 55 | 52 |  |  | 43495.0625 | 66 | 64
2019-01-30 02:00 | 54 | 51 |  |  | 43495.0833 | 65 | 63
2019-01-30 02:30 | 53 | 50 |  |  | 43495.1042 | 65 | 63
2019-01-30 03:00 | 52 | 50 |  |  | 43495.125 | 65 | 62
2019-01-30 03:30 | 52 | 49 |  |  | 43495.1458 | 64 | 62
2019-01-30 04:00 | 51 | 48 |  |  | 43495.1667 | 62 | 60
2019-01-30 04:30 | 53 | 50 |  |  | 43495.1875 | 65 | 62
2019-01-30 05:00 | 56 | 53 |  |  | 43495.2083 | 67 | 65
2019-01-30 05:30 | 58 | 56 |  |  | 43495.2292 | 71 | 69
2019-01-30 06:00 | 60 | 59 |  |  | 43495.25 | 75 | 74
2019-01-30 06:30 | 64 | 63 |  |  | 43495.2708 | 83 | 82
2019-01-30 07:00 | 70 | 69 |  |  | 43495.2917 | 93 | 91
2019-01-30 07:30 | 79 | 78 |  |  | 43495.3125 | 105 | 102
2019-01-30 08:00 | 75 | 73 |  |  | 43495.3333 | 104 | 102
2019-01-30 08:30 | 71 | 70 |  |  | 43495.3542 | 108 | 107
2019-01-30 09:00 | 71 | 70 |  |  | 43495.375 | 106 | 104
2019-01-30 09:30 | 71 | 69 |  |  | 43495.3958 | 103 | 101
2019-01-30 10:00 | 65 | 64 |  |  | 43495.4167 | 100 | 99
2019-01-30 10:30 | 63 | 62 |  |  | 43495.4375 | 97 | 97
2019-01-30 11:00 | 64 | 64 |  |  | 43495.4583 | 98 | 97
2019-01-30 11:30 | 65 | 65 |  |  | 43495.4792 | 100 | 99
2019-01-30 12:00 | 66 | 66 |  |  | 43495.5 | 101 | 101
2019-01-30 12:30 | 67 | 66 |  |  | 43495.5208 | 102 | 101
2019-01-30 13:00 | 68 | 68 |  |  | 43495.5417 | 103 | 102
2019-01-30 13:30 | 71 | 70 |  |  | 43495.5625 | 105 | 104
2019-01-30 14:00 | 72 | 72 |  |  | 43495.5833 | 105 | 104
2019-01-30 14:30 | 73 | 73 |  |  | 43495.6042 | 104 | 103
2019-01-30 15:00 | 84 | 84 |  |  | 43495.625 | 111 | 111
2019-01-30 15:30 | 90 | 90 |  |  | 43495.6458 | 116 | 115
2019-01-30 16:00 | 94 | 94 |  |  | 43495.6667 | 118 | 117
2019-01-30 16:30 | 96 | 96 |  |  | 43495.6875 | 120 | 119
2019-01-30 17:00 | 97 | 97 |  |  | 43495.7083 | 121 | 120
2019-01-30 17:30 | 94 | 94 |  |  | 43495.7292 | 115 | 114
2019-01-30 18:00 | 92 | 92 |  |  | 43495.75 | 113 | 111
2019-01-30 18:30 | 91 | 90 |  |  | 43495.7708 | 109 | 107
2019-01-30 19:00 | 91 | 91 |  |  | 43495.7917 | 109 | 108
2019-01-30 19:30 | 91 | 91 |  |  | 43495.8125 | 110 | 108
2019-01-30 20:00 | 93 | 93 |  |  | 43495.8333 | 112 | 110
2019-01-30 20:30 | 94 | 93 |  |  | 43495.8542 | 111 | 109
2019-01-30 21:00 | 91 | 90 |  |  | 43495.875 | 106 | 105
2019-01-30 21:30 | 87 | 86 |  |  | 43495.8958 | 100 | 100
2019-01-30 22:00 | 83 | 83 |  |  | 43495.9167 | 98 | 98
2019-01-30 22:30 | 80 | 80 |  |  | 43495.9375 | 94 | 94
2019-01-30 23:00 | 75 | 75 |  |  | 43495.9583 | 88 | 87
2019-01-30 23:30 | 71 | 70 |  |  | 43495.9792 | 84 | 83
2019-01-31 | 66 | 63 |  |  | 43496 | 78 | 76
2019-01-31 00:30 | 62 | 58 |  |  | 43496.0208 | 73 | 71
2019-01-31 01:00 | 59 | 56 |  |  | 43496.0417 | 69 | 67
2019-01-31 01:30 | 59 | 56 |  |  | 43496.0625 | 70 | 67
2019-01-31 02:00 | 58 | 54 |  |  | 43496.0833 | 68 | 65
2019-01-31 02:30 | 57 | 53 |  |  | 43496.1042 | 65 | 63
2019-01-31 03:00 | 55 | 51 |  |  | 43496.125 | 63 | 60
2019-01-31 03:30 | 53 | 48 |  |  | 43496.1458 | 63 | 60
2019-01-31 04:00 | 53 | 49 |  |  | 43496.1667 | 61 | 58
2019-01-31 04:30 | 52 | 49 |  |  | 43496.1875 | 62 | 59
2019-01-31 05:00 | 55 | 52 |  |  | 43496.2083 | 65 | 62
2019-01-31 05:30 | 57 | 54 |  |  | 43496.2292 | 68 | 66
2019-01-31 06:00 | 59 | 56 |  |  | 43496.25 | 70 | 69
2019-01-31 06:30 | 64 | 62 |  |  | 43496.2708 | 80 | 79
2019-01-31 07:00 | 66 | 65 |  |  | 43496.2917 | 86 | 86
2019-01-31 07:30 | 75 | 75 |  |  | 43496.3125 | 97 | 97
2019-01-31 08:00 | 68 | 66 |  |  | 43496.3333 | 97 | 96
2019-01-31 08:30 | 69 | 68 |  |  | 43496.3542 | 100 | 100
2019-01-31 09:00 | 71 | 69 |  |  | 43496.375 | 102 | 102
2019-01-31 09:30 | 71 | 69 |  |  | 43496.3958 | 110 | 110
2019-01-31 10:00 | 68 | 66 |  |  | 43496.4167 | 105 | 105
2019-01-31 10:30 | 69 | 69 |  |  | 43496.4375 | 100 | 100
2019-01-31 11:00 | 72 | 72 |  |  | 43496.4583 | 101 | 101
2019-01-31 11:30 | 72 | 71 |  |  | 43496.4792 | 102 | 102
2019-01-31 12:00 | 71 | 71 |  |  | 43496.5 | 102 | 102
2019-01-31 12:30 | 69 | 69 |  |  | 43496.5208 | 101 | 101
2019-01-31 13:00 | 72 | 71 |  |  | 43496.5417 | 104 | 103
2019-01-31 13:30 | 73 | 71 |  |  | 43496.5625 | 106 | 104
2019-01-31 14:00 | 75 | 73 |  |  | 43496.5833 | 107 | 106
2019-01-31 14:30 | 83 | 82 |  |  | 43496.6042 | 113 | 112
2019-01-31 15:00 | 89 | 88 |  |  | 43496.625 | 115 | 114
2019-01-31 15:30 | 90 | 90 |  |  | 43496.6458 | 115 | 115
2019-01-31 16:00 | 94 | 94 |  |  | 43496.6667 | 118 | 117
2019-01-31 16:30 | 97 | 97 |  |  | 43496.6875 | 118 | 118
2019-01-31 17:00 | 99 | 99 |  |  | 43496.7083 | 120 | 120
2019-01-31 17:30 | 102 | 101 |  |  | 43496.7292 | 118 | 118
2019-01-31 18:00 | 104 | 103 |  |  | 43496.75 | 118 | 118
2019-01-31 18:30 | 103 | 101 |  |  | 43496.7708 | 115 | 115
2019-01-31 19:00 | 103 | 102 |  |  | 43496.7917 | 116 | 116
2019-01-31 19:30 | 109 | 102 |  |  | 43496.8125 | 120 | 120
2019-01-31 20:00 | 107 | 100 |  |  | 43496.8333 | 120 | 119
2019-01-31 20:30 | 100 | 99 |  |  | 43496.8542 | 122 | 117
2019-01-31 21:00 | 96 | 96 |  |  | 43496.875 | 120 | 113
2019-01-31 21:30 | 90 | 90 |  |  | 43496.8958 | 114 | 105
2019-01-31 22:00 | 88 | 87 |  |  | 43496.9167 | 113 | 103
2019-01-31 22:30 | 86 | 86 |  |  | 43496.9375 | 110 | 101
2019-01-31 23:00 | 79 | 78 |  |  | 43496.9583 | 100 | 93
2019-01-31 23:30 | 71 | 71 |  |  | 43496.9792 | 88 | 86
2019-02-01 | 66 | 66 |  |  | 43497 | 80 | 79
2019-02-01 00:30 | 61 | 61 |  |  | 43497.0208 | 74 | 73
2019-02-01 01:00 | 58 | 58 |  |  | 43497.0417 | 71 | 70
2019-02-01 01:30 | 55 | 55 |  |  | 43497.0625 | 67 | 66
2019-02-01 02:00 | 53 | 53 |  |  | 43497.0833 | 66 | 65
2019-02-01 02:30 | 52 | 52 |  |  | 43497.1042 | 64 | 63
2019-02-01 03:00 | 51 | 51 |  |  | 43497.125 | 64 | 62
2019-02-01 03:30 | 49 | 49 |  |  | 43497.1458 | 62 | 61
2019-02-01 04:00 | 48 | 48 |  |  | 43497.1667 | 61 | 59
2019-02-01 04:30 | 48 | 48 |  |  | 43497.1875 | 61 | 60
2019-02-01 05:00 | 51 | 51 |  |  | 43497.2083 | 63 | 62
2019-02-01 05:30 | 53 | 53 |  |  | 43497.2292 | 66 | 66
2019-02-01 06:00 | 55 | 55 |  |  | 43497.25 | 70 | 69
2019-02-01 06:30 | 63 | 63 |  |  | 43497.2708 | 82 | 82
2019-02-01 07:00 | 68 | 68 |  |  | 43497.2917 | 91 | 91
2019-02-01 07:30 | 77 | 77 |  |  | 43497.3125 | 100 | 100
2019-02-01 08:00 | 84 | 84 |  |  | 43497.3333 | 109 | 109
2019-02-01 08:30 | 82 | 80 |  |  | 43497.3542 | 109 | 108
2019-02-01 09:00 | 83 | 82 |  |  | 43497.375 | 109 | 108
2019-02-01 09:30 | 85 | 84 |  |  | 43497.3958 | 110 | 109
2019-02-01 10:00 | 83 | 82 |  |  | 43497.4167 | 109 | 108
2019-02-01 10:30 | 83 | 82 |  |  | 43497.4375 | 106 | 105
2019-02-01 11:00 | 86 | 85 |  |  | 43497.4583 | 108 | 107
2019-02-01 11:30 | 85 | 84 |  |  | 43497.4792 | 109 | 108
2019-02-01 12:00 | 86 | 81 |  |  | 43497.5 | 115 | 108
2019-02-01 12:30 | 91 | 85 |  |  | 43497.5208 | 121 | 112
2019-02-01 13:00 | 93 | 87 |  |  | 43497.5417 | 121 | 111
2019-02-01 13:30 | 92 | 89 |  |  | 43497.5625 | 120 | 113
2019-02-01 14:00 | 90 | 88 |  |  | 43497.5833 | 120 | 113
2019-02-01 14:30 | 94 | 92 |  |  | 43497.6042 | 123 | 117
2019-02-01 15:00 | 95 | 92 |  |  | 43497.625 | 123 | 117
2019-02-01 15:30 | 98 | 94 |  |  | 43497.6458 | 124 | 116
2019-02-01 16:00 | 101 | 97 |  |  | 43497.6667 | 128 | 119
2019-02-01 16:30 | 106 | 103 |  |  | 43497.6875 | 132 | 123
2019-02-01 17:00 | 104 | 100 |  |  | 43497.7083 | 130 | 121
2019-02-01 17:30 | 102 | 99 |  |  | 43497.7292 | 125 | 118
2019-02-01 18:00 | 96 | 93 |  |  | 43497.75 | 118 | 112
2019-02-01 18:30 | 92 | 89 |  |  | 43497.7708 | 114 | 106
2019-02-01 19:00 | 90 | 89 |  |  | 43497.7917 | 117 | 107
2019-02-01 19:30 | 90 | 90 |  |  | 43497.8125 | 118 | 107
2019-02-01 20:00 | 91 | 90 |  |  | 43497.8333 | 117 | 106
2019-02-01 20:30 | 91 | 91 |  |  | 43497.8542 | 112 | 106
2019-02-01 21:00 | 90 | 90 |  |  | 43497.875 | 110 | 104
2019-02-01 21:30 | 87 | 86 |  |  | 43497.8958 | 108 | 102
2019-02-01 22:00 | 84 | 84 |  |  | 43497.9167 | 107 | 100
2019-02-01 22:30 | 81 | 80 |  |  | 43497.9375 | 104 | 96
2019-02-01 23:00 | 75 | 75 |  |  | 43497.9583 | 96 | 89
2019-02-01 23:30 | 67 | 67 |  |  | 43497.9792 | 81 | 81
2019-02-02 | 63 | 62 |  |  | 43498 | 78 | 77
2019-02-02 00:30 | 59 | 59 |  |  | 43498.0208 | 73 | 72
2019-02-02 01:00 | 55 | 55 |  |  | 43498.0417 | 69 | 67
2019-02-02 01:30 | 53 | 53 |  |  | 43498.0625 | 66 | 64
2019-02-02 02:00 | 51 | 51 |  |  | 43498.0833 | 64 | 62
2019-02-02 02:30 | 50 | 49 |  |  | 43498.1042 | 62 | 60
2019-02-02 03:00 | 48 | 47 |  |  | 43498.125 | 61 | 59
2019-02-02 03:30 | 47 | 47 |  |  | 43498.1458 | 61 | 59
2019-02-02 04:00 | 46 | 45 |  |  | 43498.1667 | 59 | 57
2019-02-02 04:30 | 47 | 47 |  |  | 43498.1875 | 59 | 57
2019-02-02 05:00 | 49 | 49 |  |  | 43498.2083 | 61 | 59
2019-02-02 05:30 | 49 | 49 |  |  | 43498.2292 | 63 | 61
2019-02-02 06:00 | 50 | 49 |  |  | 43498.25 | 63 | 61
2019-02-02 06:30 | 51 | 50 |  |  | 43498.2708 | 66 | 64
2019-02-02 07:00 | 52 | 51 |  |  | 43498.2917 | 67 | 65
2019-02-02 07:30 | 53 | 53 |  |  | 43498.3125 | 68 | 67
2019-02-02 08:00 | 55 | 55 |  |  | 43498.3333 | 70 | 69
2019-02-02 08:30 | 59 | 59 |  |  | 43498.3542 | 77 | 76
2019-02-02 09:00 | 59 | 59 |  |  | 43498.375 | 80 | 79
2019-02-02 09:30 | 57 | 57 |  |  | 43498.3958 | 75 | 74
2019-02-02 10:00 | 55 | 55 |  |  | 43498.4167 | 72 | 71
2019-02-02 10:30 | 56 | 56 |  |  | 43498.4375 | 73 | 73
2019-02-02 11:00 | 56 | 56 |  |  | 43498.4583 | 72 | 72
2019-02-02 11:30 | 56 | 56 |  |  | 43498.4792 | 71 | 71
2019-02-02 12:00 | 60 | 60 |  |  | 43498.5 | 73 | 72
2019-02-02 12:30 | 66 | 66 |  |  | 43498.5208 | 75 | 74
2019-02-02 13:00 | 63 | 63 |  |  | 43498.5417 | 77 | 76
2019-02-02 13:30 | 63 | 63 |  |  | 43498.5625 | 75 | 74
2019-02-02 14:00 | 69 | 69 |  |  | 43498.5833 | 79 | 78
2019-02-02 14:30 | 70 | 70 |  |  | 43498.6042 | 84 | 83
2019-02-02 15:00 | 71 | 71 |  |  | 43498.625 | 83 | 82
2019-02-02 15:30 | 72 | 72 |  |  | 43498.6458 | 84 | 82
2019-02-02 16:00 | 77 | 77 |  |  | 43498.6667 | 89 | 88
2019-02-02 16:30 | 78 | 78 |  |  | 43498.6875 | 91 | 89
2019-02-02 17:00 | 81 | 80 |  |  | 43498.7083 | 92 | 90
2019-02-02 17:30 | 81 | 80 |  |  | 43498.7292 | 94 | 92
2019-02-02 18:00 | 78 | 78 |  |  | 43498.75 | 91 | 88
2019-02-02 18:30 | 79 | 79 |  |  | 43498.7708 | 92 | 89
2019-02-02 19:00 | 82 | 81 |  |  | 43498.7917 | 97 | 94
2019-02-02 19:30 | 83 | 82 |  |  | 43498.8125 | 98 | 95
2019-02-02 20:00 | 81 | 80 |  |  | 43498.8333 | 96 | 93
2019-02-02 20:30 | 80 | 80 |  |  | 43498.8542 | 95 | 92
2019-02-02 21:00 | 80 | 80 |  |  | 43498.875 | 94 | 91
2019-02-02 21:30 | 74 | 74 |  |  | 43498.8958 | 88 | 86
2019-02-02 22:00 | 75 | 75 |  |  | 43498.9167 | 90 | 88
2019-02-02 22:30 | 73 | 73 |  |  | 43498.9375 | 88 | 85
2019-02-02 23:00 | 71 | 71 |  |  | 43498.9583 | 84 | 82
2019-02-02 23:30 | 67 | 67 |  |  | 43498.9792 | 81 | 79
2019-02-03 | 62 | 62 |  |  | 43499 | 76 | 74
2019-02-03 00:30 | 55 | 55 |  |  | 43499.0208 | 69 | 66
2019-02-03 01:00 | 52 | 51 |  |  | 43499.0417 | 65 | 61
2019-02-03 01:30 | 51 | 50 |  |  | 43499.0625 | 65 | 61
2019-02-03 02:00 | 51 | 50 |  |  | 43499.0833 | 64 | 60
2019-02-03 02:30 | 49 | 48 |  |  | 43499.1042 | 62 | 58
2019-02-03 03:00 | 46 | 46 |  |  | 43499.125 | 60 | 55
2019-02-03 03:30 | 46 | 45 |  |  | 43499.1458 | 59 | 54
2019-02-03 04:00 | 44 | 44 |  |  | 43499.1667 | 59 | 53
2019-02-03 04:30 | 45 | 44 |  |  | 43499.1875 | 60 | 55
2019-02-03 05:00 | 46 | 45 |  |  | 43499.2083 | 60 | 55
2019-02-03 05:30 | 46 | 45 |  |  | 43499.2292 | 60 | 55
2019-02-03 06:00 | 48 | 47 |  |  | 43499.25 | 61 | 56
2019-02-03 06:30 | 48 | 47 |  |  | 43499.2708 | 64 | 58
2019-02-03 07:00 | 47 | 46 |  |  | 43499.2917 | 63 | 58
2019-02-03 07:30 | 48 | 47 |  |  | 43499.3125 | 64 | 60
2019-02-03 08:00 | 47 | 47 |  |  | 43499.3333 | 66 | 62
2019-02-03 08:30 | 48 | 47 |  |  | 43499.3542 | 67 | 65
2019-02-03 09:00 | 52 | 52 |  |  | 43499.375 | 70 | 68
2019-02-03 09:30 | 56 | 56 |  |  | 43499.3958 | 75 | 73
2019-02-03 10:00 | 59 | 59 |  |  | 43499.4167 | 76 | 75
2019-02-03 10:30 | 62 | 62 |  |  | 43499.4375 | 76 | 74
2019-02-03 11:00 | 56 | 56 |  |  | 43499.4583 | 70 | 68
2019-02-03 11:30 | 54 | 54 |  |  | 43499.4792 | 66 | 64
2019-02-03 12:00 | 57 | 57 |  |  | 43499.5 | 72 | 71
2019-02-03 12:30 | 55 | 55 |  |  | 43499.5208 | 72 | 71
2019-02-03 13:00 | 53 | 53 |  |  | 43499.5417 | 69 | 68
2019-02-03 13:30 | 53 | 53 |  |  | 43499.5625 | 72 | 71
2019-02-03 14:00 | 53 | 53 |  |  | 43499.5833 | 71 | 69
2019-02-03 14:30 | 54 | 54 |  |  | 43499.6042 | 71 | 70
2019-02-03 15:00 | 58 | 58 |  |  | 43499.625 | 75 | 74
2019-02-03 15:30 | 61 | 61 |  |  | 43499.6458 | 76 | 75
2019-02-03 16:00 | 65 | 65 |  |  | 43499.6667 | 79 | 78
2019-02-03 16:30 | 68 | 68 |  |  | 43499.6875 | 82 | 81
2019-02-03 17:00 | 70 | 70 |  |  | 43499.7083 | 84 | 83
2019-02-03 17:30 | 71 | 71 |  |  | 43499.7292 | 86 | 83
2019-02-03 18:00 | 72 | 72 |  |  | 43499.75 | 88 | 84
2019-02-03 18:30 | 73 | 73 |  |  | 43499.7708 | 89 | 85
2019-02-03 19:00 | 72 | 71 |  |  | 43499.7917 | 90 | 86
2019-02-03 19:30 | 72 | 72 |  |  | 43499.8125 | 90 | 87
2019-02-03 20:00 | 72 | 72 |  |  | 43499.8333 | 90 | 87
2019-02-03 20:30 | 73 | 73 |  |  | 43499.8542 | 90 | 88
2019-02-03 21:00 | 71 | 71 |  |  | 43499.875 | 87 | 85
2019-02-03 21:30 | 67 | 66 |  |  | 43499.8958 | 83 | 81
2019-02-03 22:00 | 66 | 66 |  |  | 43499.9167 | 83 | 80
2019-02-03 22:30 | 66 | 66 |  |  | 43499.9375 | 82 | 80
2019-02-03 23:00 | 64 | 64 |  |  | 43499.9583 | 79 | 76
2019-02-03 23:30 | 61 | 60 |  |  | 43499.9792 | 76 | 73
2019-02-04 | 55 | 55 |  |  | 43500 | 71 | 68
2019-02-04 00:30 | 48 | 48 |  |  | 43500.0208 | 64 | 61
2019-02-04 01:00 | 45 | 44 |  |  | 43500.0417 | 61 | 57
2019-02-04 01:30 | 45 | 44 |  |  | 43500.0625 | 61 | 57
2019-02-04 02:00 | 44 | 43 |  |  | 43500.0833 | 60 | 55
2019-02-04 02:30 | 43 | 42 |  |  | 43500.1042 | 59 | 54
2019-02-04 03:00 | 43 | 42 |  |  | 43500.125 | 59 | 54
2019-02-04 03:30 | 42 | 41 |  |  | 43500.1458 | 57 | 52
2019-02-04 04:00 | 42 | 41 |  |  | 43500.1667 | 58 | 53
2019-02-04 04:30 | 43 | 42 |  |  | 43500.1875 | 59 | 54
2019-02-04 05:00 | 44 | 43 |  |  | 43500.2083 | 60 | 55
2019-02-04 05:30 | 47 | 46 |  |  | 43500.2292 | 63 | 59
2019-02-04 06:00 | 49 | 49 |  |  | 43500.25 | 67 | 64
2019-02-04 06:30 | 58 | 58 |  |  | 43500.2708 | 78 | 76
2019-02-04 07:00 | 63 | 63 |  |  | 43500.2917 | 86 | 85
2019-02-04 07:30 | 72 | 72 |  |  | 43500.3125 | 97 | 95
2019-02-04 08:00 | 76 | 75 |  |  | 43500.3333 | 102 | 98
2019-02-04 08:30 | 74 | 74 |  |  | 43500.3542 | 101 | 97
2019-02-04 09:00 | 75 | 75 |  |  | 43500.375 | 103 | 100
2019-02-04 09:30 | 79 | 79 |  |  | 43500.3958 | 103 | 100
2019-02-04 10:00 | 77 | 77 |  |  | 43500.4167 | 101 | 98
2019-02-04 10:30 | 74 | 74 |  |  | 43500.4375 | 100 | 97
2019-02-04 11:00 | 70 | 70 |  |  | 43500.4583 | 98 | 96
2019-02-04 11:30 | 72 | 72 |  |  | 43500.4792 | 98 | 96
2019-02-04 12:00 | 67 | 67 |  |  | 43500.5 | 97 | 95
2019-02-04 12:30 | 68 | 68 |  |  | 43500.5208 | 96 | 94
2019-02-04 13:00 | 71 | 71 |  |  | 43500.5417 | 100 | 97
2019-02-04 13:30 | 71 | 71 |  |  | 43500.5625 | 100 | 99
2019-02-04 14:00 | 74 | 74 |  |  | 43500.5833 | 101 | 99
2019-02-04 14:30 | 72 | 72 |  |  | 43500.6042 | 100 | 97
2019-02-04 15:00 | 72 | 71 |  |  | 43500.625 | 97 | 95
2019-02-04 15:30 | 74 | 74 |  |  | 43500.6458 | 98 | 96
2019-02-04 16:00 | 79 | 79 |  |  | 43500.6667 | 102 | 101
2019-02-04 16:30 | 84 | 84 |  |  | 43500.6875 | 105 | 104
2019-02-04 17:00 | 87 | 86 |  |  | 43500.7083 | 106 | 106
2019-02-04 17:30 | 86 | 86 |  |  | 43500.7292 | 104 | 103
2019-02-04 18:00 | 85 | 84 |  |  | 43500.75 | 102 | 100
2019-02-04 18:30 | 83 | 82 |  |  | 43500.7708 | 99 | 97
2019-02-04 19:00 | 88 | 86 |  |  | 43500.7917 | 102 | 100
2019-02-04 19:30 | 90 | 88 |  |  | 43500.8125 | 104 | 102
2019-02-04 20:00 | 87 | 86 |  |  | 43500.8333 | 103 | 100
2019-02-04 20:30 | 86 | 84 |  |  | 43500.8542 | 101 | 98
2019-02-04 21:00 | 84 | 83 |  |  | 43500.875 | 97 | 95
2019-02-04 21:30 | 80 | 79 |  |  | 43500.8958 | 93 | 91
2019-02-04 22:00 | 78 | 77 |  |  | 43500.9167 | 91 | 89
2019-02-04 22:30 | 75 | 74 |  |  | 43500.9375 | 89 | 87
2019-02-04 23:00 | 69 | 67 |  |  | 43500.9583 | 81 | 80
2019-02-04 23:30 | 64 | 61 |  |  | 43500.9792 | 77 | 74
2019-02-05 | 58 | 56 |  |  | 43501 | 70 | 69
2019-02-05 00:30 | 54 | 52 |  |  | 43501.0208 | 65 | 64
2019-02-05 01:00 | 53 | 50 |  |  | 43501.0417 | 62 | 61
2019-02-05 01:30 | 51 | 47 |  |  | 43501.0625 | 60 | 59
2019-02-05 02:00 | 52 | 48 |  |  | 43501.0833 | 60 | 58
2019-02-05 02:30 | 52 | 48 |  |  | 43501.1042 | 59 | 57
2019-02-05 03:00 | 52 | 47 |  |  | 43501.125 | 59 | 57
2019-02-05 03:30 | 51 | 47 |  |  | 43501.1458 | 59 | 57
2019-02-05 04:00 | 51 | 46 |  |  | 43501.1667 | 57 | 55
2019-02-05 04:30 | 50 | 46 |  |  | 43501.1875 | 58 | 56
2019-02-05 05:00 | 52 | 48 |  |  | 43501.2083 | 61 | 59
2019-02-05 05:30 | 53 | 50 |  |  | 43501.2292 | 65 | 64
2019-02-05 06:00 | 55 | 53 |  |  | 43501.25 | 68 | 68
2019-02-05 06:30 | 60 | 59 |  |  | 43501.2708 | 77 | 77
2019-02-05 07:00 | 67 | 66 |  |  | 43501.2917 | 87 | 87
2019-02-05 07:30 | 73 | 72 |  |  | 43501.3125 | 95 | 94
2019-02-05 08:00 | 75 | 74 |  |  | 43501.3333 | 100 | 100
2019-02-05 08:30 | 78 | 77 |  |  | 43501.3542 | 105 | 105
2019-02-05 09:00 | 79 | 78 |  |  | 43501.375 | 107 | 107
2019-02-05 09:30 | 81 | 80 |  |  | 43501.3958 | 105 | 105
2019-02-05 10:00 | 72 | 71 |  |  | 43501.4167 | 94 | 94
2019-02-05 10:30 | 71 | 71 |  |  | 43501.4375 | 96 | 95
2019-02-05 11:00 | 74 | 73 |  |  | 43501.4583 | 98 | 98
2019-02-05 11:30 | 74 | 73 |  |  | 43501.4792 | 98 | 98
2019-02-05 12:00 | 73 | 72 |  |  | 43501.5 | 97 | 97
2019-02-05 12:30 | 73 | 72 |  |  | 43501.5208 | 96 | 96
2019-02-05 13:00 | 76 | 76 |  |  | 43501.5417 | 100 | 100
2019-02-05 13:30 | 83 | 82 |  |  | 43501.5625 | 106 | 106
2019-02-05 14:00 | 88 | 87 |  |  | 43501.5833 | 110 | 110
2019-02-05 14:30 | 85 | 83 |  |  | 43501.6042 | 104 | 104
2019-02-05 15:00 | 88 | 86 |  |  | 43501.625 | 104 | 104
2019-02-05 15:30 | 90 | 86 |  |  | 43501.6458 | 104 | 103
2019-02-05 16:00 | 88 | 85 |  |  | 43501.6667 | 104 | 104
2019-02-05 16:30 | 91 | 87 |  |  | 43501.6875 | 105 | 105
2019-02-05 17:00 | 92 | 88 |  |  | 43501.7083 | 107 | 107
2019-02-05 17:30 | 93 | 88 |  |  | 43501.7292 | 105 | 105
2019-02-05 18:00 | 93 | 89 |  |  | 43501.75 | 105 | 104
2019-02-05 18:30 | 91 | 87 |  |  | 43501.7708 | 101 | 101
2019-02-05 19:00 | 91 | 87 |  |  | 43501.7917 | 101 | 101
2019-02-05 19:30 | 89 | 85 |  |  | 43501.8125 | 99 | 99
2019-02-05 20:00 | 90 | 85 |  |  | 43501.8333 | 99 | 99
2019-02-05 20:30 | 87 | 84 |  |  | 43501.8542 | 97 | 97
2019-02-05 21:00 | 85 | 81 |  |  | 43501.875 | 95 | 95
2019-02-05 21:30 | 82 | 78 |  |  | 43501.8958 | 90 | 90
2019-02-05 22:00 | 80 | 76 |  |  | 43501.9167 | 88 | 88
2019-02-05 22:30 | 77 | 72 |  |  | 43501.9375 | 86 | 86
2019-02-05 23:00 | 70 | 66 |  |  | 43501.9583 | 79 | 79
2019-02-05 23:30 | 64 | 60 |  |  | 43501.9792 | 73 | 73
2019-02-06 | 61 | 57 |  |  | 43502 | 69 | 69
2019-02-06 00:30 | 59 | 53 |  |  | 43502.0208 | 65 | 65
2019-02-06 01:00 | 57 | 51 |  |  | 43502.0417 | 61 | 61
2019-02-06 01:30 | 57 | 50 |  |  | 43502.0625 | 60 | 60
2019-02-06 02:00 | 56 | 49 |  |  | 43502.0833 | 59 | 59
2019-02-06 02:30 | 56 | 47 |  |  | 43502.1042 | 58 | 58
2019-02-06 03:00 | 54 | 46 |  |  | 43502.125 | 58 | 58
2019-02-06 03:30 | 54 | 45 |  |  | 43502.1458 | 57 | 57
2019-02-06 04:00 | 54 | 46 |  |  | 43502.1667 | 58 | 58
2019-02-06 04:30 | 55 | 47 |  |  | 43502.1875 | 60 | 60
2019-02-06 05:00 | 56 | 49 |  |  | 43502.2083 | 62 | 62
2019-02-06 05:30 | 58 | 52 |  |  | 43502.2292 | 66 | 66
2019-02-06 06:00 | 60 | 55 |  |  | 43502.25 | 73 | 72
2019-02-06 06:30 | 67 | 63 |  |  | 43502.2708 | 82 | 82
2019-02-06 07:00 | 72 | 69 |  |  | 43502.2917 | 90 | 90
2019-02-06 07:30 | 80 | 77 |  |  | 43502.3125 | 100 | 100
2019-02-06 08:00 | 84 | 81 |  |  | 43502.3333 | 103 | 103
2019-02-06 08:30 | 82 | 79 |  |  | 43502.3542 | 103 | 103
2019-02-06 09:00 | 81 | 79 |  |  | 43502.375 | 103 | 102
2019-02-06 09:30 | 81 | 79 |  |  | 43502.3958 | 106 | 106
2019-02-06 10:00 | 81 | 79 |  |  | 43502.4167 | 106 | 106
2019-02-06 10:30 | 80 | 78 |  |  | 43502.4375 | 106 | 106
2019-02-06 11:00 | 81 | 79 |  |  | 43502.4583 | 104 | 104
2019-02-06 11:30 | 78 | 76 |  |  | 43502.4792 | 103 | 103
2019-02-06 12:00 | 80 | 79 |  |  | 43502.5 | 104 | 104
2019-02-06 12:30 | 76 | 74 |  |  | 43502.5208 | 101 | 101
2019-02-06 13:00 | 75 | 74 |  |  | 43502.5417 | 101 | 100
2019-02-06 13:30 | 73 | 71 |  |  | 43502.5625 | 99 | 99
2019-02-06 14:00 | 77 | 75 |  |  | 43502.5833 | 99 | 99
2019-02-06 14:30 | 81 | 80 |  |  | 43502.6042 | 99 | 99
2019-02-06 15:00 | 78 | 76 |  |  | 43502.625 | 100 | 100
2019-02-06 15:30 | 80 | 79 |  |  | 43502.6458 | 101 | 101
2019-02-06 16:00 | 79 | 78 |  |  | 43502.6667 | 100 | 100
2019-02-06 16:30 | 84 | 82 |  |  | 43502.6875 | 104 | 104
2019-02-06 17:00 | 90 | 87 |  |  | 43502.7083 | 106 | 106
2019-02-06 17:30 | 93 | 90 |  |  | 43502.7292 | 106 | 106
2019-02-06 18:00 | 91 | 88 |  |  | 43502.75 | 104 | 104
2019-02-06 18:30 | 89 | 86 |  |  | 43502.7708 | 101 | 101
2019-02-06 19:00 | 92 | 89 |  |  | 43502.7917 | 103 | 103
2019-02-06 19:30 | 91 | 88 |  |  | 43502.8125 | 102 | 102
2019-02-06 20:00 | 90 | 86 |  |  | 43502.8333 | 100 | 100
2019-02-06 20:30 | 90 | 86 |  |  | 43502.8542 | 99 | 98
2019-02-06 21:00 | 86 | 83 |  |  | 43502.875 | 95 | 94
2019-02-06 21:30 | 83 | 79 |  |  | 43502.8958 | 91 | 91
2019-02-06 22:00 | 81 | 77 |  |  | 43502.9167 | 90 | 90
2019-02-06 22:30 | 77 | 73 |  |  | 43502.9375 | 86 | 86
2019-02-06 23:00 | 72 | 67 |  |  | 43502.9583 | 80 | 80
2019-02-06 23:30 | 68 | 62 |  |  | 43502.9792 | 76 | 76
2019-02-07 | 64 | 57 |  |  | 43503 | 71 | 71
2019-02-07 00:30 | 60 | 53 |  |  | 43503.0208 | 66 | 66
2019-02-07 01:00 | 59 | 52 |  |  | 43503.0417 | 63 | 63
2019-02-07 01:30 | 58 | 50 |  |  | 43503.0625 | 61 | 61
2019-02-07 02:00 | 57 | 49 |  |  | 43503.0833 | 60 | 60
2019-02-07 02:30 | 57 | 49 |  |  | 43503.1042 | 60 | 60
2019-02-07 03:00 | 56 | 47 |  |  | 43503.125 | 59 | 59
2019-02-07 03:30 | 56 | 47 |  |  | 43503.1458 | 57 | 57
2019-02-07 04:00 | 56 | 47 |  |  | 43503.1667 | 59 | 59
2019-02-07 04:30 | 56 | 47 |  |  | 43503.1875 | 58 | 58
2019-02-07 05:00 | 58 | 49 |  |  | 43503.2083 | 60 | 60
2019-02-07 05:30 | 59 | 52 |  |  | 43503.2292 | 63 | 63
2019-02-07 06:00 | 59 | 54 |  |  | 43503.25 | 66 | 66
2019-02-07 06:30 | 64 | 61 |  |  | 43503.2708 | 79 | 79
2019-02-07 07:00 | 66 | 64 |  |  | 43503.2917 | 85 | 84
2019-02-07 07:30 | 75 | 72 |  |  | 43503.3125 | 93 | 93
2019-02-07 08:00 | 80 | 77 |  |  | 43503.3333 | 99 | 99
2019-02-07 08:30 | 76 | 74 |  |  | 43503.3542 | 98 | 97
2019-02-07 09:00 | 75 | 74 |  |  | 43503.375 | 101 | 100
2019-02-07 09:30 | 76 | 74 |  |  | 43503.3958 | 102 | 102
2019-02-07 10:00 | 76 | 74 |  |  | 43503.4167 | 100 | 99
2019-02-07 10:30 | 73 | 71 |  |  | 43503.4375 | 95 | 94
2019-02-07 11:00 | 76 | 75 |  |  | 43503.4583 | 100 | 99
2019-02-07 11:30 | 77 | 76 |  |  | 43503.4792 | 102 | 101
2019-02-07 12:00 | 77 | 76 |  |  | 43503.5 | 102 | 101
2019-02-07 12:30 | 82 | 81 |  |  | 43503.5208 | 102 | 101
2019-02-07 13:00 | 77 | 75 |  |  | 43503.5417 | 99 | 99
2019-02-07 13:30 | 77 | 76 |  |  | 43503.5625 | 99 | 98
2019-02-07 14:00 | 84 | 82 |  |  | 43503.5833 | 105 | 104
2019-02-07 14:30 | 80 | 79 |  |  | 43503.6042 | 103 | 103
2019-02-07 15:00 | 83 | 81 |  |  | 43503.625 | 105 | 104
2019-02-07 15:30 | 84 | 83 |  |  | 43503.6458 | 107 | 106
2019-02-07 16:00 | 84 | 82 |  |  | 43503.6667 | 105 | 105
2019-02-07 16:30 | 88 | 86 |  |  | 43503.6875 | 107 | 106
2019-02-07 17:00 | 87 | 85 |  |  | 43503.7083 | 106 | 106
2019-02-07 17:30 | 88 | 86 |  |  | 43503.7292 | 104 | 104
2019-02-07 18:00 | 89 | 86 |  |  | 43503.75 | 102 | 102
2019-02-07 18:30 | 90 | 86 |  |  | 43503.7708 | 102 | 101
2019-02-07 19:00 | 92 | 89 |  |  | 43503.7917 | 104 | 103
2019-02-07 19:30 | 91 | 88 |  |  | 43503.8125 | 102 | 102
2019-02-07 20:00 | 90 | 87 |  |  | 43503.8333 | 101 | 101
2019-02-07 20:30 | 90 | 86 |  |  | 43503.8542 | 99 | 99
2019-02-07 21:00 | 88 | 84 |  |  | 43503.875 | 98 | 97
2019-02-07 21:30 | 83 | 80 |  |  | 43503.8958 | 93 | 93
2019-02-07 22:00 | 80 | 77 |  |  | 43503.9167 | 90 | 90
2019-02-07 22:30 | 78 | 74 |  |  | 43503.9375 | 89 | 88
2019-02-07 23:00 | 73 | 69 |  |  | 43503.9583 | 82 | 82
2019-02-07 23:30 | 67 | 62 |  |  | 43503.9792 | 77 | 77
2019-02-08 | 63 | 56 |  |  | 43504 | 71 | 71
2019-02-08 00:30 | 60 | 52 |  |  | 43504.0208 | 66 | 65
2019-02-08 01:00 | 60 | 51 |  |  | 43504.0417 | 63 | 62
2019-02-08 01:30 | 53 | 48 |  |  | 43504.0625 | 61 | 60
2019-02-08 02:00 | 50 | 46 |  |  | 43504.0833 | 60 | 58
2019-02-08 02:30 | 50 | 46 |  |  | 43504.1042 | 59 | 58
2019-02-08 03:00 | 49 | 46 |  |  | 43504.125 | 59 | 57
2019-02-08 03:30 | 49 | 45 |  |  | 43504.1458 | 59 | 57
2019-02-08 04:00 | 49 | 45 |  |  | 43504.1667 | 59 | 57
2019-02-08 04:30 | 50 | 46 |  |  | 43504.1875 | 60 | 59
2019-02-08 05:00 | 52 | 49 |  |  | 43504.2083 | 63 | 62
2019-02-08 05:30 | 55 | 53 |  |  | 43504.2292 | 68 | 67
2019-02-08 06:00 | 59 | 56 |  |  | 43504.25 | 72 | 71
2019-02-08 06:30 | 66 | 65 |  |  | 43504.2708 | 83 | 83
2019-02-08 07:00 | 72 | 71 |  |  | 43504.2917 | 93 | 93
2019-02-08 07:30 | 80 | 78 |  |  | 43504.3125 | 102 | 102
2019-02-08 08:00 | 82 | 82 |  |  | 43504.3333 | 106 | 106
2019-02-08 08:30 | 84 | 83 |  |  | 43504.3542 | 108 | 107
2019-02-08 09:00 | 85 | 84 |  |  | 43504.375 | 109 | 109
2019-02-08 09:30 | 84 | 83 |  |  | 43504.3958 | 108 | 107
2019-02-08 10:00 | 82 | 81 |  |  | 43504.4167 | 104 | 103
2019-02-08 10:30 | 75 | 74 |  |  | 43504.4375 | 101 | 100
2019-02-08 11:00 | 77 | 76 |  |  | 43504.4583 | 103 | 102
2019-02-08 11:30 | 77 | 76 |  |  | 43504.4792 | 103 | 102
2019-02-08 12:00 | 76 | 76 |  |  | 43504.5 | 100 | 99
2019-02-08 12:30 | 79 | 78 |  |  | 43504.5208 | 104 | 103
2019-02-08 13:00 | 78 | 77 |  |  | 43504.5417 | 104 | 103
2019-02-08 13:30 | 74 | 74 |  |  | 43504.5625 | 99 | 99
2019-02-08 14:00 | 75 | 75 |  |  | 43504.5833 | 101 | 100
2019-02-08 14:30 | 80 | 80 |  |  | 43504.6042 | 101 | 101
2019-02-08 15:00 | 82 | 81 |  |  | 43504.625 | 103 | 102
2019-02-08 15:30 | 83 | 83 |  |  | 43504.6458 | 105 | 104
2019-02-08 16:00 | 87 | 87 |  |  | 43504.6667 | 108 | 107
2019-02-08 16:30 | 93 | 92 |  |  | 43504.6875 | 114 | 113
2019-02-08 17:00 | 98 | 97 |  |  | 43504.7083 | 117 | 116
2019-02-08 17:30 | 100 | 99 |  |  | 43504.7292 | 118 | 116
2019-02-08 18:00 | 98 | 96 |  |  | 43504.75 | 115 | 112
2019-02-08 18:30 | 96 | 93 |  |  | 43504.7708 | 111 | 108
2019-02-08 19:00 | 95 | 94 |  |  | 43504.7917 | 110 | 109
2019-02-08 19:30 | 95 | 95 |  |  | 43504.8125 | 110 | 109
2019-02-08 20:00 | 94 | 93 |  |  | 43504.8333 | 109 | 108
2019-02-08 20:30 | 94 | 93 |  |  | 43504.8542 | 108 | 107
2019-02-08 21:00 | 89 | 88 |  |  | 43504.875 | 102 | 101
2019-02-08 21:30 | 84 | 83 |  |  | 43504.8958 | 97 | 96
2019-02-08 22:00 | 83 | 82 |  |  | 43504.9167 | 97 | 97
2019-02-08 22:30 | 80 | 79 |  |  | 43504.9375 | 95 | 94
2019-02-08 23:00 | 74 | 73 |  |  | 43504.9583 | 87 | 87
2019-02-08 23:30 | 68 | 67 |  |  | 43504.9792 | 82 | 82
2019-02-09 | 64 | 63 |  |  | 43505 | 77 | 77
2019-02-09 00:30 | 61 | 59 |  |  | 43505.0208 | 71 | 71
2019-02-09 01:00 | 57 | 56 |  |  | 43505.0417 | 67 | 67
2019-02-09 01:30 | 59 | 56 |  |  | 43505.0625 | 67 | 67
2019-02-09 02:00 | 58 | 55 |  |  | 43505.0833 | 66 | 65
2019-02-09 02:30 | 57 | 54 |  |  | 43505.1042 | 64 | 63
2019-02-09 03:00 | 57 | 53 |  |  | 43505.125 | 63 | 62
2019-02-09 03:30 | 55 | 51 |  |  | 43505.1458 | 62 | 62
2019-02-09 04:00 | 54 | 50 |  |  | 43505.1667 | 61 | 60
2019-02-09 04:30 | 54 | 50 |  |  | 43505.1875 | 61 | 60
2019-02-09 05:00 | 55 | 51 |  |  | 43505.2083 | 62 | 61
2019-02-09 05:30 | 55 | 51 |  |  | 43505.2292 | 63 | 62
2019-02-09 06:00 | 54 | 50 |  |  | 43505.25 | 61 | 60
2019-02-09 06:30 | 55 | 52 |  |  | 43505.2708 | 65 | 64
2019-02-09 07:00 | 56 | 53 |  |  | 43505.2917 | 66 | 66
2019-02-09 07:30 | 58 | 55 |  |  | 43505.3125 | 68 | 68
2019-02-09 08:00 | 59 | 58 |  |  | 43505.3333 | 71 | 71
2019-02-09 08:30 | 61 | 60 |  |  | 43505.3542 | 75 | 75
2019-02-09 09:00 | 64 | 62 |  |  | 43505.375 | 76 | 76
2019-02-09 09:30 | 65 | 63 |  |  | 43505.3958 | 80 | 80
2019-02-09 10:00 | 67 | 66 |  |  | 43505.4167 | 81 | 81
2019-02-09 10:30 | 68 | 67 |  |  | 43505.4375 | 82 | 82
2019-02-09 11:00 | 71 | 70 |  |  | 43505.4583 | 85 | 85
2019-02-09 11:30 | 72 | 70 |  |  | 43505.4792 | 84 | 84
2019-02-09 12:00 | 70 | 69 |  |  | 43505.5 | 83 | 83
2019-02-09 12:30 | 71 | 70 |  |  | 43505.5208 | 82 | 82
2019-02-09 13:00 | 74 | 72 |  |  | 43505.5417 | 84 | 83
2019-02-09 13:30 | 75 | 74 |  |  | 43505.5625 | 85 | 84
2019-02-09 14:00 | 76 | 75 |  |  | 43505.5833 | 87 | 86
2019-02-09 14:30 | 80 | 79 |  |  | 43505.6042 | 90 | 89
2019-02-09 15:00 | 80 | 79 |  |  | 43505.625 | 90 | 89
2019-02-09 15:30 | 82 | 80 |  |  | 43505.6458 | 91 | 91
2019-02-09 16:00 | 83 | 82 |  |  | 43505.6667 | 93 | 93
2019-02-09 16:30 | 88 | 87 |  |  | 43505.6875 | 97 | 96
2019-02-09 17:00 | 90 | 89 |  |  | 43505.7083 | 99 | 98
2019-02-09 17:30 | 93 | 92 |  |  | 43505.7292 | 102 | 102
2019-02-09 18:00 | 91 | 90 |  |  | 43505.75 | 101 | 100
2019-02-09 18:30 | 90 | 88 |  |  | 43505.7708 | 100 | 99
2019-02-09 19:00 | 78 | 77 |  |  | 43505.7917 | 96 | 95
2019-02-09 19:30 | 77 | 76 |  |  | 43505.8125 | 93 | 93
2019-02-09 20:00 | 78 | 77 |  |  | 43505.8333 | 94 | 94
2019-02-09 20:30 | 79 | 78 |  |  | 43505.8542 | 97 | 96
2019-02-09 21:00 | 85 | 84 |  |  | 43505.875 | 96 | 95
2019-02-09 21:30 | 83 | 82 |  |  | 43505.8958 | 94 | 93
2019-02-09 22:00 | 82 | 81 |  |  | 43505.9167 | 93 | 92
2019-02-09 22:30 | 80 | 79 |  |  | 43505.9375 | 91 | 90
2019-02-09 23:00 | 77 | 76 |  |  | 43505.9583 | 87 | 86
2019-02-09 23:30 | 72 | 70 |  |  | 43505.9792 | 81 | 80
2019-02-10 | 67 | 65 |  |  | 43506 | 76 | 75
2019-02-10 00:30 | 64 | 62 |  |  | 43506.0208 | 72 | 71
2019-02-10 01:00 | 63 | 61 |  |  | 43506.0417 | 70 | 70
2019-02-10 01:30 | 62 | 59 |  |  | 43506.0625 | 69 | 68
2019-02-10 02:00 | 60 | 57 |  |  | 43506.0833 | 68 | 67
2019-02-10 02:30 | 60 | 57 |  |  | 43506.1042 | 67 | 66
2019-02-10 03:00 | 59 | 55 |  |  | 43506.125 | 66 | 65
2019-02-10 03:30 | 59 | 55 |  |  | 43506.1458 | 65 | 63
2019-02-10 04:00 | 57 | 53 |  |  | 43506.1667 | 63 | 61
2019-02-10 04:30 | 57 | 53 |  |  | 43506.1875 | 63 | 62
2019-02-10 05:00 | 57 | 53 |  |  | 43506.2083 | 64 | 63
2019-02-10 05:30 | 57 | 52 |  |  | 43506.2292 | 64 | 62
2019-02-10 06:00 | 56 | 51 |  |  | 43506.25 | 63 | 62
2019-02-10 06:30 | 54 | 51 |  |  | 43506.2708 | 63 | 63
2019-02-10 07:00 | 53 | 49 |  |  | 43506.2917 | 63 | 63
2019-02-10 07:30 | 53 | 50 |  |  | 43506.3125 | 63 | 63
2019-02-10 08:00 | 52 | 51 |  |  | 43506.3333 | 64 | 64
2019-02-10 08:30 | 55 | 54 |  |  | 43506.3542 | 68 | 67
2019-02-10 09:00 | 57 | 56 |  |  | 43506.375 | 70 | 70
2019-02-10 09:30 | 61 | 60 |  |  | 43506.3958 | 74 | 73
2019-02-10 10:00 | 67 | 65 |  |  | 43506.4167 | 77 | 77
2019-02-10 10:30 | 71 | 69 |  |  | 43506.4375 | 82 | 82
2019-02-10 11:00 | 72 | 71 |  |  | 43506.4583 | 82 | 82
2019-02-10 11:30 | 75 | 73 |  |  | 43506.4792 | 82 | 82
2019-02-10 12:00 | 76 | 74 |  |  | 43506.5 | 82 | 82
2019-02-10 12:30 | 75 | 74 |  |  | 43506.5208 | 82 | 82
2019-02-10 13:00 | 76 | 75 |  |  | 43506.5417 | 83 | 83
2019-02-10 13:30 | 78 | 77 |  |  | 43506.5625 | 85 | 85
2019-02-10 14:00 | 79 | 78 |  |  | 43506.5833 | 87 | 87
2019-02-10 14:30 | 81 | 80 |  |  | 43506.6042 | 89 | 89
2019-02-10 15:00 | 84 | 83 |  |  | 43506.625 | 92 | 92
2019-02-10 15:30 | 85 | 84 |  |  | 43506.6458 | 94 | 93
2019-02-10 16:00 | 86 | 84 |  |  | 43506.6667 | 95 | 94
2019-02-10 16:30 | 88 | 88 |  |  | 43506.6875 | 98 | 98
2019-02-10 17:00 | 91 | 90 |  |  | 43506.7083 | 102 | 101
2019-02-10 17:30 | 91 | 91 |  |  | 43506.7292 | 103 | 103
2019-02-10 18:00 | 91 | 90 |  |  | 43506.75 | 101 | 100
2019-02-10 18:30 | 89 | 88 |  |  | 43506.7708 | 100 | 100
2019-02-10 19:00 | 88 | 88 |  |  | 43506.7917 | 103 | 103
2019-02-10 19:30 | 89 | 89 |  |  | 43506.8125 | 103 | 103
2019-02-10 20:00 | 90 | 90 |  |  | 43506.8333 | 103 | 103
2019-02-10 20:30 | 90 | 90 |  |  | 43506.8542 | 104 | 104
2019-02-10 21:00 | 86 | 86 |  |  | 43506.875 | 98 | 98
2019-02-10 21:30 | 84 | 84 |  |  | 43506.8958 | 96 | 96
2019-02-10 22:00 | 81 | 81 |  |  | 43506.9167 | 93 | 93
2019-02-10 22:30 | 79 | 78 |  |  | 43506.9375 | 92 | 92
2019-02-10 23:00 | 75 | 74 |  |  | 43506.9583 | 87 | 87
2019-02-10 23:30 | 70 | 68 |  |  | 43506.9792 | 82 | 82
2019-02-11 | 66 | 64 |  |  | 43507 | 77 | 77
2019-02-11 00:30 | 63 | 60 |  |  | 43507.0208 | 72 | 72
2019-02-11 01:00 | 59 | 57 |  |  | 43507.0417 | 68 | 68
2019-02-11 01:30 | 57 | 55 |  |  | 43507.0625 | 67 | 66
2019-02-11 02:00 | 54 | 52 |  |  | 43507.0833 | 64 | 64
2019-02-11 02:30 | 54 | 51 |  |  | 43507.1042 | 62 | 62
2019-02-11 03:00 | 54 | 52 |  |  | 43507.125 | 64 | 64
2019-02-11 03:30 | 53 | 51 |  |  | 43507.1458 | 63 | 63
2019-02-11 04:00 | 54 | 52 |  |  | 43507.1667 | 63 | 63
2019-02-11 04:30 | 56 | 53 |  |  | 43507.1875 | 65 | 65
2019-02-11 05:00 | 60 | 58 |  |  | 43507.2083 | 70 | 70
2019-02-11 05:30 | 64 | 62 |  |  | 43507.2292 | 75 | 75
2019-02-11 06:00 | 65 | 64 |  |  | 43507.25 | 78 | 78
2019-02-11 06:30 | 71 | 70 |  |  | 43507.2708 | 89 | 89
2019-02-11 07:00 | 78 | 77 |  |  | 43507.2917 | 99 | 99
2019-02-11 07:30 | 87 | 87 |  |  | 43507.3125 | 111 | 111
2019-02-11 08:00 | 88 | 88 |  |  | 43507.3333 | 115 | 115
2019-02-11 08:30 | 87 | 87 |  |  | 43507.3542 | 115 | 115
2019-02-11 09:00 | 95 | 95 |  |  | 43507.375 | 120 | 120
2019-02-11 09:30 | 96 | 96 |  |  | 43507.3958 | 124 | 124
2019-02-11 10:00 | 94 | 94 |  |  | 43507.4167 | 124 | 123
2019-02-11 10:30 | 94 | 94 |  |  | 43507.4375 | 123 | 122
2019-02-11 11:00 | 93 | 93 |  |  | 43507.4583 | 121 | 120
2019-02-11 11:30 | 95 | 95 |  |  | 43507.4792 | 123 | 123
2019-02-11 12:00 | 94 | 94 |  |  | 43507.5 | 120 | 120
2019-02-11 12:30 | 95 | 95 |  |  | 43507.5208 | 121 | 121
2019-02-11 13:00 | 97 | 97 |  |  | 43507.5417 | 121 | 121
2019-02-11 13:30 | 98 | 98 |  |  | 43507.5625 | 122 | 122
2019-02-11 14:00 | 98 | 98 |  |  | 43507.5833 | 121 | 121
2019-02-11 14:30 | 97 | 97 |  |  | 43507.6042 | 121 | 120
2019-02-11 15:00 | 97 | 97 |  |  | 43507.625 | 120 | 120
2019-02-11 15:30 | 98 | 98 |  |  | 43507.6458 | 121 | 121
2019-02-11 16:00 | 101 | 101 |  |  | 43507.6667 | 124 | 124
2019-02-11 16:30 | 105 | 105 |  |  | 43507.6875 | 127 | 127
2019-02-11 17:00 | 109 | 109 |  |  | 43507.7083 | 130 | 130
2019-02-11 17:30 | 109 | 109 |  |  | 43507.7292 | 128 | 128
2019-02-11 18:00 | 105 | 105 |  |  | 43507.75 | 124 | 124
2019-02-11 18:30 | 104 | 104 |  |  | 43507.7708 | 122 | 122
2019-02-11 19:00 | 103 | 103 |  |  | 43507.7917 | 123 | 123
2019-02-11 19:30 | 95 | 95 |  |  | 43507.8125 | 119 | 119
2019-02-11 20:00 | 94 | 94 |  |  | 43507.8333 | 118 | 118
2019-02-11 20:30 | 93 | 93 |  |  | 43507.8542 | 115 | 115
2019-02-11 21:00 | 97 | 97 |  |  | 43507.875 | 114 | 114
2019-02-11 21:30 | 95 | 94 |  |  | 43507.8958 | 109 | 109
2019-02-11 22:00 | 94 | 93 |  |  | 43507.9167 | 107 | 107
2019-02-11 22:30 | 93 | 91 |  |  | 43507.9375 | 107 | 106
2019-02-11 23:00 | 88 | 85 |  |  | 43507.9583 | 100 | 99
2019-02-11 23:30 | 83 | 80 |  |  | 43507.9792 | 95 | 95
2019-02-12 | 76 | 74 |  |  | 43508 | 90 | 90
2019-02-12 00:30 | 72 | 70 |  |  | 43508.0208 | 84 | 84
2019-02-12 01:00 | 69 | 67 |  |  | 43508.0417 | 80 | 80
2019-02-12 01:30 | 68 | 66 |  |  | 43508.0625 | 79 | 78
2019-02-12 02:00 | 66 | 64 |  |  | 43508.0833 | 76 | 76
2019-02-12 02:30 | 64 | 62 |  |  | 43508.1042 | 75 | 75
2019-02-12 03:00 | 65 | 62 |  |  | 43508.125 | 75 | 75
2019-02-12 03:30 | 65 | 63 |  |  | 43508.1458 | 76 | 76
2019-02-12 04:00 | 64 | 62 |  |  | 43508.1667 | 76 | 76
2019-02-12 04:30 | 63 | 61 |  |  | 43508.1875 | 77 | 77
2019-02-12 05:00 | 66 | 64 |  |  | 43508.2083 | 80 | 80
2019-02-12 05:30 | 68 | 66 |  |  | 43508.2292 | 84 | 84
2019-02-12 06:00 | 70 | 69 |  |  | 43508.25 | 88 | 88
2019-02-12 06:30 | 76 | 75 |  |  | 43508.2708 | 99 | 99
2019-02-12 07:00 | 81 | 80 |  |  | 43508.2917 | 109 | 109
2019-02-12 07:30 | 88 | 87 |  |  | 43508.3125 | 117 | 117
2019-02-12 08:00 | 91 | 91 |  |  | 43508.3333 | 122 | 122
2019-02-12 08:30 | 92 | 91 |  |  | 43508.3542 | 123 | 123
2019-02-12 09:00 | 92 | 91 |  |  | 43508.375 | 124 | 124
2019-02-12 09:30 | 94 | 93 |  |  | 43508.3958 | 126 | 126
2019-02-12 10:00 | 96 | 96 |  |  | 43508.4167 | 129 | 129
2019-02-12 10:30 | 99 | 99 |  |  | 43508.4375 | 131 | 130
2019-02-12 11:00 | 100 | 100 |  |  | 43508.4583 | 133 | 133
2019-02-12 11:30 | 103 | 102 |  |  | 43508.4792 | 136 | 136
2019-02-12 12:00 | 105 | 105 |  |  | 43508.5 | 141 | 141
2019-02-12 12:30 | 108 | 107 |  |  | 43508.5208 | 143 | 143
2019-02-12 13:00 | 101 | 101 |  |  | 43508.5417 | 140 | 139
2019-02-12 13:30 | 100 | 99 |  |  | 43508.5625 | 140 | 140
2019-02-12 14:00 | 103 | 102 |  |  | 43508.5833 | 140 | 140
2019-02-12 14:30 | 103 | 103 |  |  | 43508.6042 | 142 | 142
2019-02-12 15:00 | 105 | 105 |  |  | 43508.625 | 147 | 146
2019-02-12 15:30 | 104 | 103 |  |  | 43508.6458 | 147 | 141
2019-02-12 16:00 | 106 | 104 |  |  | 43508.6667 | 148 | 142
2019-02-12 16:30 | 110 | 107 |  |  | 43508.6875 | 150 | 143
2019-02-12 17:00 | 113 | 110 |  |  | 43508.7083 | 153 | 147
2019-02-12 17:30 | 113 | 111 |  |  | 43508.7292 | 153 | 147
2019-02-12 18:00 | 111 | 109 |  |  | 43508.75 | 148 | 143
2019-02-12 18:30 | 110 | 108 |  |  | 43508.7708 | 144 | 139
2019-02-12 19:00 | 110 | 108 |  |  | 43508.7917 | 144 | 140
2019-02-12 19:30 | 112 | 110 |  |  | 43508.8125 | 146 | 141
2019-02-12 20:00 | 112 | 111 |  |  | 43508.8333 | 147 | 142
2019-02-12 20:30 | 109 | 107 |  |  | 43508.8542 | 143 | 138
2019-02-12 21:00 | 105 | 103 |  |  | 43508.875 | 138 | 132
2019-02-12 21:30 | 101 | 101 |  |  | 43508.8958 | 127 | 127
2019-02-12 22:00 | 98 | 98 |  |  | 43508.9167 | 123 | 123
2019-02-12 22:30 | 92 | 92 |  |  | 43508.9375 | 118 | 118
2019-02-12 23:00 | 91 | 91 |  |  | 43508.9583 | 110 | 110
2019-02-12 23:30 | 85 | 85 |  |  | 43508.9792 | 104 | 104
2019-02-13 | 78 | 77 |  |  | 43509 | 97 | 97
2019-02-13 00:30 | 73 | 72 |  |  | 43509.0208 | 92 | 92
2019-02-13 01:00 | 70 | 69 |  |  | 43509.0417 | 87 | 87
2019-02-13 01:30 | 68 | 66 |  |  | 43509.0625 | 83 | 83
2019-02-13 02:00 | 65 | 63 |  |  | 43509.0833 | 79 | 79
2019-02-13 02:30 | 65 | 62 |  |  | 43509.1042 | 77 | 76
2019-02-13 03:00 | 65 | 62 |  |  | 43509.125 | 77 | 76
2019-02-13 03:30 | 63 | 60 |  |  | 43509.1458 | 75 | 75
2019-02-13 04:00 | 63 | 60 |  |  | 43509.1667 | 75 | 75
2019-02-13 04:30 | 63 | 61 |  |  | 43509.1875 | 76 | 76
2019-02-13 05:00 | 66 | 63 |  |  | 43509.2083 | 78 | 78
2019-02-13 05:30 | 67 | 64 |  |  | 43509.2292 | 81 | 81
2019-02-13 06:00 | 66 | 65 |  |  | 43509.25 | 84 | 84
2019-02-13 06:30 | 71 | 70 |  |  | 43509.2708 | 93 | 93
2019-02-13 07:00 | 78 | 77 |  |  | 43509.2917 | 103 | 103
2019-02-13 07:30 | 88 | 87 |  |  | 43509.3125 | 115 | 115
2019-02-13 08:00 | 90 | 89 |  |  | 43509.3333 | 119 | 119
2019-02-13 08:30 | 92 | 91 |  |  | 43509.3542 | 122 | 122
2019-02-13 09:00 | 93 | 93 |  |  | 43509.375 | 125 | 125
2019-02-13 09:30 | 99 | 96 |  |  | 43509.3958 | 131 | 130
2019-02-13 10:00 | 101 | 98 |  |  | 43509.4167 | 135 | 133
2019-02-13 10:30 | 104 | 100 |  |  | 43509.4375 | 136 | 133
2019-02-13 11:00 | 106 | 103 |  |  | 43509.4583 | 139 | 137
2019-02-13 11:30 | 108 | 107 |  |  | 43509.4792 | 142 | 140
2019-02-13 12:00 | 110 | 109 |  |  | 43509.5 | 145 | 143
2019-02-13 12:30 | 114 | 112 |  |  | 43509.5208 | 148 | 145
2019-02-13 13:00 | 109 | 107 |  |  | 43509.5417 | 147 | 143
2019-02-13 13:30 | 105 | 102 |  |  | 43509.5625 | 147 | 142
2019-02-13 14:00 | 107 | 104 |  |  | 43509.5833 | 149 | 143
2019-02-13 14:30 | 111 | 108 |  |  | 43509.6042 | 156 | 150
2019-02-13 15:00 | 111 | 110 |  |  | 43509.625 | 154 | 148
2019-02-13 15:30 | 114 | 113 |  |  | 43509.6458 | 155 | 149
2019-02-13 16:00 | 115 | 115 |  |  | 43509.6667 | 159 | 154
2019-02-13 16:30 | 117 | 116 |  |  | 43509.6875 | 161 | 155
2019-02-13 17:00 | 120 | 119 |  |  | 43509.7083 | 163 | 157
2019-02-13 17:30 | 119 | 118 |  |  | 43509.7292 | 160 | 153
2019-02-13 18:00 | 117 | 115 |  |  | 43509.75 | 158 | 151
2019-02-13 18:30 | 115 | 112 |  |  | 43509.7708 | 155 | 144
2019-02-13 19:00 | 115 | 111 |  |  | 43509.7917 | 155 | 144
2019-02-13 19:30 | 114 | 110 |  |  | 43509.8125 | 152 | 142
2019-02-13 20:00 | 111 | 108 |  |  | 43509.8333 | 149 | 139
2019-02-13 20:30 | 111 | 108 |  |  | 43509.8542 | 149 | 139
2019-02-13 21:00 | 110 | 106 |  |  | 43509.875 | 148 | 138
2019-02-13 21:30 | 105 | 99 |  |  | 43509.8958 | 136 | 127
2019-02-13 22:00 | 98 | 95 |  |  | 43509.9167 | 125 | 122
2019-02-13 22:30 | 90 | 88 |  |  | 43509.9375 | 114 | 113
2019-02-13 23:00 | 84 | 81 |  |  | 43509.9583 | 108 | 106
2019-02-13 23:30 | 80 | 77 |  |  | 43509.9792 | 104 | 103
2019-02-14 | 84 | 81 |  |  | 43510 | 105 | 105
2019-02-14 00:30 | 85 | 81 |  |  | 43510.0208 | 103 | 102
2019-02-14 01:00 | 84 | 80 |  |  | 43510.0417 | 100 | 99
2019-02-14 01:30 | 78 | 74 |  |  | 43510.0625 | 92 | 92
2019-02-14 02:00 | 73 | 68 |  |  | 43510.0833 | 87 | 86
2019-02-14 02:30 | 72 | 68 |  |  | 43510.1042 | 85 | 84
2019-02-14 03:00 | 70 | 66 |  |  | 43510.125 | 83 | 82
2019-02-14 03:30 | 69 | 65 |  |  | 43510.1458 | 81 | 81
2019-02-14 04:00 | 69 | 64 |  |  | 43510.1667 | 81 | 80
2019-02-14 04:30 | 69 | 64 |  |  | 43510.1875 | 81 | 80
2019-02-14 05:00 | 70 | 65 |  |  | 43510.2083 | 84 | 83
2019-02-14 05:30 | 71 | 67 |  |  | 43510.2292 | 86 | 85
2019-02-14 06:00 | 72 | 68 |  |  | 43510.25 | 89 | 89
2019-02-14 06:30 | 80 | 75 |  |  | 43510.2708 | 101 | 100
2019-02-14 07:00 | 84 | 80 |  |  | 43510.2917 | 107 | 106
2019-02-14 07:30 | 90 | 86 |  |  | 43510.3125 | 116 | 115
2019-02-14 08:00 | 94 | 92 |  |  | 43510.3333 | 124 | 124
2019-02-14 08:30 | 96 | 94 |  |  | 43510.3542 | 126 | 126
2019-02-14 09:00 | 96 | 94 |  |  | 43510.375 | 128 | 127
2019-02-14 09:30 | 100 | 98 |  |  | 43510.3958 | 131 | 130
2019-02-14 10:00 | 101 | 99 |  |  | 43510.4167 | 128 | 127
2019-02-14 10:30 | 95 | 93 |  |  | 43510.4375 | 125 | 125
2019-02-14 11:00 | 95 | 93 |  |  | 43510.4583 | 126 | 125
2019-02-14 11:30 | 99 | 96 |  |  | 43510.4792 | 130 | 130
2019-02-14 12:00 | 102 | 100 |  |  | 43510.5 | 134 | 133
2019-02-14 12:30 | 102 | 99 |  |  | 43510.5208 | 131 | 131
2019-02-14 13:00 | 106 | 104 |  |  | 43510.5417 | 135 | 134
2019-02-14 13:30 | 110 | 109 |  |  | 43510.5625 | 137 | 136
2019-02-14 14:00 | 111 | 110 |  |  | 43510.5833 | 135 | 135
2019-02-14 14:30 | 111 | 110 |  |  | 43510.6042 | 136 | 135
2019-02-14 15:00 | 114 | 112 |  |  | 43510.625 | 138 | 137
2019-02-14 15:30 | 112 | 110 |  |  | 43510.6458 | 136 | 135
2019-02-14 16:00 | 111 | 109 |  |  | 43510.6667 | 137 | 135
2019-02-14 16:30 | 110 | 107 |  |  | 43510.6875 | 135 | 133
2019-02-14 17:00 | 110 | 107 |  |  | 43510.7083 | 134 | 131
2019-02-14 17:30 | 108 | 105 |  |  | 43510.7292 | 128 | 126
2019-02-14 18:00 | 106 | 103 |  |  | 43510.75 | 125 | 123
2019-02-14 18:30 | 105 | 102 |  |  | 43510.7708 | 122 | 120
2019-02-14 19:00 | 105 | 102 |  |  | 43510.7917 | 124 | 122
2019-02-14 19:30 | 105 | 102 |  |  | 43510.8125 | 124 | 120
2019-02-14 20:00 | 106 | 102 |  |  | 43510.8333 | 123 | 120
2019-02-14 20:30 | 105 | 101 |  |  | 43510.8542 | 121 | 119
2019-02-14 21:00 | 100 | 98 |  |  | 43510.875 | 115 | 114
2019-02-14 21:30 | 95 | 93 |  |  | 43510.8958 | 110 | 109
2019-02-14 22:00 | 92 | 90 |  |  | 43510.9167 | 107 | 107
2019-02-14 22:30 | 88 | 86 |  |  | 43510.9375 | 104 | 104
2019-02-14 23:00 | 82 | 80 |  |  | 43510.9583 | 96 | 95
2019-02-14 23:30 | 76 | 73 |  |  | 43510.9792 | 92 | 91
2019-02-15 | 73 | 70 |  |  | 43511 | 88 | 87
2019-02-15 00:30 | 68 | 65 |  |  | 43511.0208 | 82 | 81
2019-02-15 01:00 | 66 | 63 |  |  | 43511.0417 | 79 | 78
2019-02-15 01:30 | 64 | 60 |  |  | 43511.0625 | 76 | 75
2019-02-15 02:00 | 63 | 60 |  |  | 43511.0833 | 75 | 74
2019-02-15 02:30 | 62 | 59 |  |  | 43511.1042 | 74 | 72
2019-02-15 03:00 | 61 | 57 |  |  | 43511.125 | 73 | 72
2019-02-15 03:30 | 61 | 57 |  |  | 43511.1458 | 72 | 72
2019-02-15 04:00 | 62 | 57 |  |  | 43511.1667 | 74 | 72
2019-02-15 04:30 | 62 | 57 |  |  | 43511.1875 | 73 | 71
2019-02-15 05:00 | 64 | 59 |  |  | 43511.2083 | 76 | 74
2019-02-15 05:30 | 65 | 62 |  |  | 43511.2292 | 78 | 77
2019-02-15 06:00 | 69 | 66 |  |  | 43511.25 | 83 | 82
2019-02-15 06:30 | 75 | 73 |  |  | 43511.2708 | 94 | 94
2019-02-15 07:00 | 79 | 77 |  |  | 43511.2917 | 101 | 100
2019-02-15 07:30 | 85 | 82 |  |  | 43511.3125 | 109 | 107
2019-02-15 08:00 | 86 | 84 |  |  | 43511.3333 | 112 | 111
2019-02-15 08:30 | 86 | 85 |  |  | 43511.3542 | 114 | 113
2019-02-15 09:00 | 86 | 85 |  |  | 43511.375 | 115 | 115
2019-02-15 09:30 | 86 | 85 |  |  | 43511.3958 | 113 | 113
2019-02-15 10:00 | 84 | 83 |  |  | 43511.4167 | 112 | 112
2019-02-15 10:30 | 86 | 85 |  |  | 43511.4375 | 111 | 110
2019-02-15 11:00 | 84 | 83 |  |  | 43511.4583 | 109 | 109
2019-02-15 11:30 | 84 | 84 |  |  | 43511.4792 | 109 | 108
2019-02-15 12:00 | 84 | 83 |  |  | 43511.5 | 109 | 109
2019-02-15 12:30 | 84 | 82 |  |  | 43511.5208 | 109 | 108
2019-02-15 13:00 | 86 | 85 |  |  | 43511.5417 | 109 | 108
2019-02-15 13:30 | 86 | 84 |  |  | 43511.5625 | 108 | 107
2019-02-15 14:00 | 86 | 84 |  |  | 43511.5833 | 110 | 108
2019-02-15 14:30 | 88 | 86 |  |  | 43511.6042 | 112 | 110
2019-02-15 15:00 | 87 | 85 |  |  | 43511.625 | 111 | 109
2019-02-15 15:30 | 86 | 84 |  |  | 43511.6458 | 110 | 108
2019-02-15 16:00 | 90 | 88 |  |  | 43511.6667 | 113 | 111
2019-02-15 16:30 | 93 | 91 |  |  | 43511.6875 | 117 | 115
2019-02-15 17:00 | 100 | 98 |  |  | 43511.7083 | 122 | 119
2019-02-15 17:30 | 101 | 98 |  |  | 43511.7292 | 122 | 118
2019-02-15 18:00 | 98 | 95 |  |  | 43511.75 | 118 | 114
2019-02-15 18:30 | 95 | 92 |  |  | 43511.7708 | 114 | 110
2019-02-15 19:00 | 95 | 91 |  |  | 43511.7917 | 114 | 111
2019-02-15 19:30 | 95 | 92 |  |  | 43511.8125 | 114 | 111
2019-02-15 20:00 | 95 | 91 |  |  | 43511.8333 | 113 | 109
2019-02-15 20:30 | 94 | 92 |  |  | 43511.8542 | 112 | 110
2019-02-15 21:00 | 90 | 88 |  |  | 43511.875 | 108 | 106
2019-02-15 21:30 | 88 | 86 |  |  | 43511.8958 | 106 | 104
2019-02-15 22:00 | 85 | 83 |  |  | 43511.9167 | 103 | 102
2019-02-15 22:30 | 82 | 80 |  |  | 43511.9375 | 101 | 100
2019-02-15 23:00 | 77 | 75 |  |  | 43511.9583 | 93 | 92
2019-02-15 23:30 | 73 | 71 |  |  | 43511.9792 | 89 | 88
2019-02-16 | 68 | 65 |  |  | 43512 | 83 | 81
2019-02-16 00:30 | 64 | 59 |  |  | 43512.0208 | 77 | 75
2019-02-16 01:00 | 61 | 57 |  |  | 43512.0417 | 74 | 72
2019-02-16 01:30 | 61 | 56 |  |  | 43512.0625 | 73 | 71
2019-02-16 02:00 | 59 | 55 |  |  | 43512.0833 | 70 | 68
2019-02-16 02:30 | 58 | 54 |  |  | 43512.1042 | 70 | 68
2019-02-16 03:00 | 57 | 53 |  |  | 43512.125 | 69 | 68
2019-02-16 03:30 | 57 | 53 |  |  | 43512.1458 | 67 | 66
2019-02-16 04:00 | 58 | 53 |  |  | 43512.1667 | 69 | 67
2019-02-16 04:30 | 57 | 52 |  |  | 43512.1875 | 67 | 66
2019-02-16 05:00 | 58 | 53 |  |  | 43512.2083 | 68 | 66
2019-02-16 05:30 | 59 | 55 |  |  | 43512.2292 | 70 | 69
2019-02-16 06:00 | 58 | 54 |  |  | 43512.25 | 70 | 69
2019-02-16 06:30 | 59 | 54 |  |  | 43512.2708 | 72 | 70
2019-02-16 07:00 | 59 | 55 |  |  | 43512.2917 | 72 | 71
2019-02-16 07:30 | 58 | 55 |  |  | 43512.3125 | 73 | 72
2019-02-16 08:00 | 58 | 55 |  |  | 43512.3333 | 74 | 74
2019-02-16 08:30 | 60 | 58 |  |  | 43512.3542 | 78 | 78
2019-02-16 09:00 | 64 | 62 |  |  | 43512.375 | 82 | 82
2019-02-16 09:30 | 64 | 63 |  |  | 43512.3958 | 82 | 82
2019-02-16 10:00 | 62 | 61 |  |  | 43512.4167 | 82 | 82
2019-02-16 10:30 | 59 | 58 |  |  | 43512.4375 | 77 | 77
2019-02-16 11:00 | 57 | 56 |  |  | 43512.4583 | 72 | 72
2019-02-16 11:30 | 58 | 57 |  |  | 43512.4792 | 74 | 74
2019-02-16 12:00 | 62 | 61 |  |  | 43512.5 | 75 | 75
2019-02-16 12:30 | 62 | 61 |  |  | 43512.5208 | 77 | 77
2019-02-16 13:00 | 65 | 64 |  |  | 43512.5417 | 81 | 81
2019-02-16 13:30 | 62 | 61 |  |  | 43512.5625 | 80 | 80
2019-02-16 14:00 | 68 | 67 |  |  | 43512.5833 | 85 | 85
2019-02-16 14:30 | 66 | 65 |  |  | 43512.6042 | 80 | 80
2019-02-16 15:00 | 65 | 63 |  |  | 43512.625 | 86 | 85
2019-02-16 15:30 | 67 | 65 |  |  | 43512.6458 | 86 | 86
2019-02-16 16:00 | 69 | 68 |  |  | 43512.6667 | 88 | 88
2019-02-16 16:30 | 69 | 68 |  |  | 43512.6875 | 89 | 88
2019-02-16 17:00 | 72 | 71 |  |  | 43512.7083 | 92 | 92
2019-02-16 17:30 | 77 | 75 |  |  | 43512.7292 | 95 | 94
2019-02-16 18:00 | 78 | 76 |  |  | 43512.75 | 96 | 96
2019-02-16 18:30 | 80 | 77 |  |  | 43512.7708 | 98 | 98
2019-02-16 19:00 | 81 | 79 |  |  | 43512.7917 | 100 | 100
2019-02-16 19:30 | 81 | 79 |  |  | 43512.8125 | 101 | 100
2019-02-16 20:00 | 82 | 80 |  |  | 43512.8333 | 102 | 101
2019-02-16 20:30 | 81 | 79 |  |  | 43512.8542 | 101 | 100
2019-02-16 21:00 | 79 | 76 |  |  | 43512.875 | 98 | 97
2019-02-16 21:30 | 76 | 73 |  |  | 43512.8958 | 95 | 94
2019-02-16 22:00 | 75 | 72 |  |  | 43512.9167 | 94 | 94
2019-02-16 22:30 | 72 | 69 |  |  | 43512.9375 | 91 | 91
2019-02-16 23:00 | 72 | 68 |  |  | 43512.9583 | 88 | 87
2019-02-16 23:30 | 67 | 63 |  |  | 43512.9792 | 84 | 83
2019-02-17 | 64 | 60 |  |  | 43513 | 80 | 79
2019-02-17 00:30 | 60 | 56 |  |  | 43513.0208 | 74 | 73
2019-02-17 01:00 | 57 | 52 |  |  | 43513.0417 | 69 | 69
2019-02-17 01:30 | 55 | 50 |  |  | 43513.0625 | 68 | 67
2019-02-17 02:00 | 53 | 48 |  |  | 43513.0833 | 65 | 65
2019-02-17 02:30 | 52 | 47 |  |  | 43513.1042 | 64 | 63
2019-02-17 03:00 | 51 | 46 |  |  | 43513.125 | 62 | 61
2019-02-17 03:30 | 52 | 46 |  |  | 43513.1458 | 63 | 62
2019-02-17 04:00 | 53 | 48 |  |  | 43513.1667 | 64 | 63
2019-02-17 04:30 | 54 | 49 |  |  | 43513.1875 | 64 | 63
2019-02-17 05:00 | 55 | 50 |  |  | 43513.2083 | 65 | 64
2019-02-17 05:30 | 53 | 48 |  |  | 43513.2292 | 64 | 63
2019-02-17 06:00 | 52 | 46 |  |  | 43513.25 | 62 | 61
2019-02-17 06:30 | 52 | 46 |  |  | 43513.2708 | 62 | 61
2019-02-17 07:00 | 51 | 45 |  |  | 43513.2917 | 62 | 61
2019-02-17 07:30 | 50 | 45 |  |  | 43513.3125 | 62 | 61
2019-02-17 08:00 | 50 | 45 |  |  | 43513.3333 | 63 | 63
2019-02-17 08:30 | 49 | 45 |  |  | 43513.3542 | 64 | 63
2019-02-17 09:00 | 49 | 46 |  |  | 43513.375 | 64 | 64
2019-02-17 09:30 | 49 | 46 |  |  | 43513.3958 | 66 | 65
2019-02-17 10:00 | 50 | 48 |  |  | 43513.4167 | 69 | 69
2019-02-17 10:30 | 53 | 51 |  |  | 43513.4375 | 72 | 72
2019-02-17 11:00 | 56 | 54 |  |  | 43513.4583 | 71 | 71
2019-02-17 11:30 | 58 | 55 |  |  | 43513.4792 | 72 | 71
2019-02-17 12:00 | 56 | 54 |  |  | 43513.5 | 70 | 69
2019-02-17 12:30 | 57 | 54 |  |  | 43513.5208 | 71 | 70
2019-02-17 13:00 | 58 | 55 |  |  | 43513.5417 | 70 | 69
2019-02-17 13:30 | 58 | 56 |  |  | 43513.5625 | 72 | 72
2019-02-17 14:00 | 59 | 57 |  |  | 43513.5833 | 73 | 72
2019-02-17 14:30 | 61 | 59 |  |  | 43513.6042 | 74 | 74
2019-02-17 15:00 | 62 | 60 |  |  | 43513.625 | 75 | 74
2019-02-17 15:30 | 63 | 61 |  |  | 43513.6458 | 76 | 76
2019-02-17 16:00 | 65 | 63 |  |  | 43513.6667 | 80 | 80
2019-02-17 16:30 | 66 | 64 |  |  | 43513.6875 | 82 | 81
2019-02-17 17:00 | 67 | 66 |  |  | 43513.7083 | 85 | 84
2019-02-17 17:30 | 72 | 70 |  |  | 43513.7292 | 88 | 88
2019-02-17 18:00 | 74 | 72 |  |  | 43513.75 | 92 | 91
2019-02-17 18:30 | 75 | 73 |  |  | 43513.7708 | 94 | 93
2019-02-17 19:00 | 79 | 77 |  |  | 43513.7917 | 99 | 98
2019-02-17 19:30 | 79 | 77 |  |  | 43513.8125 | 100 | 99
2019-02-17 20:00 | 78 | 76 |  |  | 43513.8333 | 99 | 98
2019-02-17 20:30 | 81 | 78 |  |  | 43513.8542 | 101 | 100
2019-02-17 21:00 | 79 | 76 |  |  | 43513.875 | 98 | 97
2019-02-17 21:30 | 77 | 74 |  |  | 43513.8958 | 95 | 94
2019-02-17 22:00 | 74 | 71 |  |  | 43513.9167 | 93 | 93
2019-02-17 22:30 | 74 | 71 |  |  | 43513.9375 | 93 | 93
2019-02-17 23:00 | 71 | 68 |  |  | 43513.9583 | 87 | 87
2019-02-17 23:30 | 68 | 65 |  |  | 43513.9792 | 84 | 84
2019-02-18 | 63 | 59 |  |  | 43514 | 79 | 78
2019-02-18 00:30 | 61 | 56 |  |  | 43514.0208 | 75 | 73
2019-02-18 01:00 | 57 | 52 |  |  | 43514.0417 | 70 | 69
2019-02-18 01:30 | 56 | 51 |  |  | 43514.0625 | 68 | 67
2019-02-18 02:00 | 55 | 50 |  |  | 43514.0833 | 67 | 65
2019-02-18 02:30 | 54 | 49 |  |  | 43514.1042 | 66 | 65
2019-02-18 03:00 | 54 | 49 |  |  | 43514.125 | 65 | 64
2019-02-18 03:30 | 56 | 50 |  |  | 43514.1458 | 66 | 65
2019-02-18 04:00 | 56 | 51 |  |  | 43514.1667 | 67 | 65
2019-02-18 04:30 | 57 | 52 |  |  | 43514.1875 | 68 | 67
2019-02-18 05:00 | 59 | 55 |  |  | 43514.2083 | 72 | 70
2019-02-18 05:30 | 60 | 57 |  |  | 43514.2292 | 74 | 74
2019-02-18 06:00 | 63 | 60 |  |  | 43514.25 | 79 | 78
2019-02-18 06:30 | 69 | 68 |  |  | 43514.2708 | 90 | 89
2019-02-18 07:00 | 74 | 71 |  |  | 43514.2917 | 96 | 95
2019-02-18 07:30 | 77 | 75 |  |  | 43514.3125 | 102 | 101
2019-02-18 08:00 | 77 | 75 |  |  | 43514.3333 | 103 | 103
2019-02-18 08:30 | 76 | 75 |  |  | 43514.3542 | 105 | 105
2019-02-18 09:00 | 78 | 77 |  |  | 43514.375 | 109 | 109
2019-02-18 09:30 | 84 | 84 |  |  | 43514.3958 | 115 | 115
2019-02-18 10:00 | 85 | 85 |  |  | 43514.4167 | 114 | 113
2019-02-18 10:30 | 86 | 85 |  |  | 43514.4375 | 113 | 112
2019-02-18 11:00 | 82 | 82 |  |  | 43514.4583 | 108 | 107
2019-02-18 11:30 | 82 | 81 |  |  | 43514.4792 | 107 | 107
2019-02-18 12:00 | 84 | 83 |  |  | 43514.5 | 109 | 109
2019-02-18 12:30 | 84 | 83 |  |  | 43514.5208 | 109 | 109
2019-02-18 13:00 | 84 | 83 |  |  | 43514.5417 | 110 | 110
2019-02-18 13:30 | 85 | 84 |  |  | 43514.5625 | 112 | 112
2019-02-18 14:00 | 87 | 86 |  |  | 43514.5833 | 112 | 112
2019-02-18 14:30 | 87 | 87 |  |  | 43514.6042 | 113 | 113
2019-02-18 15:00 | 87 | 86 |  |  | 43514.625 | 114 | 114
2019-02-18 15:30 | 86 | 85 |  |  | 43514.6458 | 112 | 112
2019-02-18 16:00 | 90 | 89 |  |  | 43514.6667 | 116 | 115
2019-02-18 16:30 | 94 | 93 |  |  | 43514.6875 | 119 | 118
2019-02-18 17:00 | 98 | 96 |  |  | 43514.7083 | 123 | 121
2019-02-18 17:30 | 100 | 98 |  |  | 43514.7292 | 121 | 120
2019-02-18 18:00 | 99 | 97 |  |  | 43514.75 | 119 | 118
2019-02-18 18:30 | 98 | 96 |  |  | 43514.7708 | 117 | 116
2019-02-18 19:00 | 99 | 98 |  |  | 43514.7917 | 120 | 120
2019-02-18 19:30 | 100 | 99 |  |  | 43514.8125 | 120 | 120
2019-02-18 20:00 | 103 | 102 |  |  | 43514.8333 | 121 | 121
2019-02-18 20:30 | 99 | 98 |  |  | 43514.8542 | 117 | 117
2019-02-18 21:00 | 95 | 94 |  |  | 43514.875 | 111 | 111
2019-02-18 21:30 | 91 | 90 |  |  | 43514.8958 | 107 | 107
2019-02-18 22:00 | 87 | 86 |  |  | 43514.9167 | 105 | 105
2019-02-18 22:30 | 84 | 83 |  |  | 43514.9375 | 102 | 102
2019-02-18 23:00 | 78 | 76 |  |  | 43514.9583 | 94 | 94
2019-02-18 23:30 | 73 | 70 |  |  | 43514.9792 | 89 | 89
2019-02-19 | 68 | 65 |  |  | 43515 | 84 | 83
2019-02-19 00:30 | 63 | 59 |  |  | 43515.0208 | 78 | 76
2019-02-19 01:00 | 62 | 56 |  |  | 43515.0417 | 74 | 72
2019-02-19 01:30 | 60 | 54 |  |  | 43515.0625 | 72 | 70
2019-02-19 02:00 | 59 | 53 |  |  | 43515.0833 | 70 | 68
2019-02-19 02:30 | 57 | 51 |  |  | 43515.1042 | 69 | 67
2019-02-19 03:00 | 57 | 51 |  |  | 43515.125 | 69 | 67
2019-02-19 03:30 | 57 | 52 |  |  | 43515.1458 | 70 | 67
2019-02-19 04:00 | 57 | 52 |  |  | 43515.1667 | 70 | 67
2019-02-19 04:30 | 58 | 53 |  |  | 43515.1875 | 71 | 68
2019-02-19 05:00 | 60 | 56 |  |  | 43515.2083 | 73 | 71
2019-02-19 05:30 | 61 | 57 |  |  | 43515.2292 | 76 | 74
2019-02-19 06:00 | 61 | 57 |  |  | 43515.25 | 77 | 76
2019-02-19 06:30 | 65 | 63 |  |  | 43515.2708 | 87 | 86
2019-02-19 07:00 | 68 | 67 |  |  | 43515.2917 | 94 | 94
2019-02-19 07:30 | 72 | 71 |  |  | 43515.3125 | 101 | 101
2019-02-19 08:00 | 73 | 72 |  |  | 43515.3333 | 103 | 103
2019-02-19 08:30 | 73 | 71 |  |  | 43515.3542 | 104 | 104
2019-02-19 09:00 | 73 | 72 |  |  | 43515.375 | 105 | 105
2019-02-19 09:30 | 74 | 73 |  |  | 43515.3958 | 107 | 107
2019-02-19 10:00 | 76 | 76 |  |  | 43515.4167 | 108 | 108
2019-02-19 10:30 | 77 | 77 |  |  | 43515.4375 | 110 | 109
2019-02-19 11:00 | 78 | 78 |  |  | 43515.4583 | 111 | 111
2019-02-19 11:30 | 79 | 79 |  |  | 43515.4792 | 110 | 110
2019-02-19 12:00 | 80 | 80 |  |  | 43515.5 | 112 | 112
2019-02-19 12:30 | 85 | 84 |  |  | 43515.5208 | 116 | 116
2019-02-19 13:00 | 87 | 86 |  |  | 43515.5417 | 117 | 117
2019-02-19 13:30 | 87 | 86 |  |  | 43515.5625 | 117 | 117
2019-02-19 14:00 | 90 | 89 |  |  | 43515.5833 | 120 | 120
2019-02-19 14:30 | 94 | 93 |  |  | 43515.6042 | 124 | 124
2019-02-19 15:00 | 96 | 96 |  |  | 43515.625 | 127 | 126
2019-02-19 15:30 | 98 | 98 |  |  | 43515.6458 | 127 | 126
2019-02-19 16:00 | 101 | 101 |  |  | 43515.6667 | 128 | 128
2019-02-19 16:30 | 106 | 105 |  |  | 43515.6875 | 132 | 131
2019-02-19 17:00 | 108 | 107 |  |  | 43515.7083 | 135 | 133
2019-02-19 17:30 | 101 | 101 |  |  | 43515.7292 | 131 | 129
2019-02-19 18:00 | 99 | 98 |  |  | 43515.75 | 126 | 125
2019-02-19 18:30 | 96 | 96 |  |  | 43515.7708 | 123 | 122
2019-02-19 19:00 | 98 | 97 |  |  | 43515.7917 | 125 | 125
2019-02-19 19:30 | 98 | 98 |  |  | 43515.8125 | 125 | 124
2019-02-19 20:00 | 95 | 95 |  |  | 43515.8333 | 123 | 122
2019-02-19 20:30 | 93 | 93 |  |  | 43515.8542 | 120 | 119
2019-02-19 21:00 | 89 | 89 |  |  | 43515.875 | 113 | 112
2019-02-19 21:30 | 86 | 86 |  |  | 43515.8958 | 108 | 107
2019-02-19 22:00 | 90 | 90 |  |  | 43515.9167 | 109 | 108
2019-02-19 22:30 | 88 | 88 |  |  | 43515.9375 | 106 | 106
2019-02-19 23:00 | 79 | 79 |  |  | 43515.9583 | 97 | 97
2019-02-19 23:30 | 74 | 73 |  |  | 43515.9792 | 91 | 91
2019-02-20 | 70 | 68 |  |  | 43516 | 86 | 86
2019-02-20 00:30 | 66 | 64 |  |  | 43516.0208 | 81 | 80
2019-02-20 01:00 | 63 | 61 |  |  | 43516.0417 | 78 | 77
2019-02-20 01:30 | 64 | 61 |  |  | 43516.0625 | 77 | 76
2019-02-20 02:00 | 64 | 61 |  |  | 43516.0833 | 77 | 76
2019-02-20 02:30 | 64 | 61 |  |  | 43516.1042 | 75 | 74
2019-02-20 03:00 | 63 | 60 |  |  | 43516.125 | 75 | 74
2019-02-20 03:30 | 63 | 60 |  |  | 43516.1458 | 74 | 73
2019-02-20 04:00 | 64 | 61 |  |  | 43516.1667 | 75 | 74
2019-02-20 04:30 | 63 | 60 |  |  | 43516.1875 | 75 | 74
2019-02-20 05:00 | 65 | 63 |  |  | 43516.2083 | 79 | 78
2019-02-20 05:30 | 66 | 65 |  |  | 43516.2292 | 82 | 82
2019-02-20 06:00 | 68 | 66 |  |  | 43516.25 | 86 | 86
2019-02-20 06:30 | 70 | 69 |  |  | 43516.2708 | 92 | 92
2019-02-20 07:00 | 71 | 69 |  |  | 43516.2917 | 97 | 96
2019-02-20 07:30 | 76 | 74 |  |  | 43516.3125 | 104 | 103
2019-02-20 08:00 | 80 | 80 |  |  | 43516.3333 | 111 | 110
2019-02-20 08:30 | 84 | 83 |  |  | 43516.3542 | 115 | 115
2019-02-20 09:00 | 81 | 81 |  |  | 43516.375 | 113 | 113
2019-02-20 09:30 | 80 | 79 |  |  | 43516.3958 | 114 | 113
2019-02-20 10:00 | 80 | 80 |  |  | 43516.4167 | 112 | 112
2019-02-20 10:30 | 80 | 80 |  |  | 43516.4375 | 111 | 110
2019-02-20 11:00 | 83 | 82 |  |  | 43516.4583 | 113 | 112
2019-02-20 11:30 | 83 | 82 |  |  | 43516.4792 | 114 | 113
2019-02-20 12:00 | 85 | 85 |  |  | 43516.5 | 115 | 114
2019-02-20 12:30 | 86 | 86 |  |  | 43516.5208 | 115 | 114
2019-02-20 13:00 | 87 | 87 |  |  | 43516.5417 | 116 | 115
2019-02-20 13:30 | 90 | 90 |  |  | 43516.5625 | 120 | 119
2019-02-20 14:00 | 97 | 97 |  |  | 43516.5833 | 127 | 124
2019-02-20 14:30 | 103 | 101 |  |  | 43516.6042 | 136 | 130
2019-02-20 15:00 | 103 | 101 |  |  | 43516.625 | 136 | 131
2019-02-20 15:30 | 103 | 101 |  |  | 43516.6458 | 137 | 131
2019-02-20 16:00 | 108 | 106 |  |  | 43516.6667 | 142 | 135
2019-02-20 16:30 | 113 | 110 |  |  | 43516.6875 | 149 | 138
2019-02-20 17:00 | 108 | 105 |  |  | 43516.7083 | 150 | 140
2019-02-20 17:30 | 109 | 106 |  |  | 43516.7292 | 150 | 139
2019-02-20 18:00 | 105 | 102 |  |  | 43516.75 | 143 | 133
2019-02-20 18:30 | 100 | 99 |  |  | 43516.7708 | 133 | 129
2019-02-20 19:00 | 102 | 102 |  |  | 43516.7917 | 136 | 132
2019-02-20 19:30 | 103 | 102 |  |  | 43516.8125 | 135 | 132
2019-02-20 20:00 | 103 | 102 |  |  | 43516.8333 | 134 | 130
2019-02-20 20:30 | 101 | 100 |  |  | 43516.8542 | 132 | 128
2019-02-20 21:00 | 99 | 98 |  |  | 43516.875 | 128 | 125
2019-02-20 21:30 | 95 | 94 |  |  | 43516.8958 | 124 | 119
2019-02-20 22:00 | 100 | 99 |  |  | 43516.9167 | 124 | 121
2019-02-20 22:30 | 98 | 97 |  |  | 43516.9375 | 121 | 117
2019-02-20 23:00 | 92 | 90 |  |  | 43516.9583 | 114 | 109
2019-02-20 23:30 | 87 | 83 |  |  | 43516.9792 | 109 | 103
2019-02-21 | 83 | 78 |  |  | 43517 | 104 | 98
2019-02-21 00:30 | 76 | 73 |  |  | 43517.0208 | 95 | 91
2019-02-21 01:00 | 70 | 70 |  |  | 43517.0417 | 86 | 86
2019-02-21 01:30 | 68 | 67 |  |  | 43517.0625 | 82 | 82
2019-02-21 02:00 | 65 | 64 |  |  | 43517.0833 | 80 | 79
2019-02-21 02:30 | 65 | 63 |  |  | 43517.1042 | 79 | 78
2019-02-21 03:00 | 64 | 62 |  |  | 43517.125 | 78 | 78
2019-02-21 03:30 | 63 | 62 |  |  | 43517.1458 | 78 | 78
2019-02-21 04:00 | 64 | 63 |  |  | 43517.1667 | 78 | 78
2019-02-21 04:30 | 63 | 62 |  |  | 43517.1875 | 79 | 79
2019-02-21 05:00 | 66 | 65 |  |  | 43517.2083 | 82 | 82
2019-02-21 05:30 | 69 | 68 |  |  | 43517.2292 | 86 | 86
2019-02-21 06:00 | 72 | 72 |  |  | 43517.25 | 91 | 91
2019-02-21 06:30 | 76 | 76 |  |  | 43517.2708 | 100 | 100
2019-02-21 07:00 | 80 | 80 |  |  | 43517.2917 | 108 | 108
2019-02-21 07:30 | 85 | 85 |  |  | 43517.3125 | 115 | 115
2019-02-21 08:00 | 91 | 91 |  |  | 43517.3333 | 122 | 121
2019-02-21 08:30 | 94 | 94 |  |  | 43517.3542 | 124 | 124
2019-02-21 09:00 | 95 | 95 |  |  | 43517.375 | 124 | 124
2019-02-21 09:30 | 94 | 93 |  |  | 43517.3958 | 122 | 122
2019-02-21 10:00 | 91 | 91 |  |  | 43517.4167 | 122 | 121
2019-02-21 10:30 | 93 | 92 |  |  | 43517.4375 | 122 | 121
2019-02-21 11:00 | 98 | 97 |  |  | 43517.4583 | 126 | 126
2019-02-21 11:30 | 98 | 98 |  |  | 43517.4792 | 124 | 124
2019-02-21 12:00 | 97 | 96 |  |  | 43517.5 | 123 | 123
2019-02-21 12:30 | 92 | 92 |  |  | 43517.5208 | 117 | 117
2019-02-21 13:00 | 91 | 90 |  |  | 43517.5417 | 119 | 119
2019-02-21 13:30 | 97 | 97 |  |  | 43517.5625 | 121 | 121
2019-02-21 14:00 | 98 | 97 |  |  | 43517.5833 | 124 | 124
2019-02-21 14:30 | 98 | 98 |  |  | 43517.6042 | 125 | 125
2019-02-21 15:00 | 97 | 97 |  |  | 43517.625 | 123 | 123
2019-02-21 15:30 | 100 | 100 |  |  | 43517.6458 | 126 | 126
2019-02-21 16:00 | 104 | 104 |  |  | 43517.6667 | 129 | 128
2019-02-21 16:30 | 109 | 109 |  |  | 43517.6875 | 132 | 131
2019-02-21 17:00 | 112 | 112 |  |  | 43517.7083 | 136 | 134
2019-02-21 17:30 | 114 | 114 |  |  | 43517.7292 | 137 | 135
2019-02-21 18:00 | 114 | 113 |  |  | 43517.75 | 135 | 133
2019-02-21 18:30 | 104 | 104 |  |  | 43517.7708 | 127 | 126
2019-02-21 19:00 | 104 | 104 |  |  | 43517.7917 | 129 | 128
2019-02-21 19:30 | 103 | 103 |  |  | 43517.8125 | 128 | 126
2019-02-21 20:00 | 102 | 102 |  |  | 43517.8333 | 127 | 124
2019-02-21 20:30 | 101 | 101 |  |  | 43517.8542 | 125 | 123
2019-02-21 21:00 | 95 | 95 |  |  | 43517.875 | 118 | 117
2019-02-21 21:30 | 91 | 91 |  |  | 43517.8958 | 113 | 111
2019-02-21 22:00 | 89 | 88 |  |  | 43517.9167 | 111 | 108
2019-02-21 22:30 | 95 | 93 |  |  | 43517.9375 | 114 | 110
2019-02-21 23:00 | 88 | 86 |  |  | 43517.9583 | 105 | 102
2019-02-21 23:30 | 81 | 80 |  |  | 43517.9792 | 98 | 96
2019-02-22 | 76 | 76 |  |  | 43518 | 92 | 91
2019-02-22 00:30 | 71 | 69 |  |  | 43518.0208 | 84 | 83
2019-02-22 01:00 | 67 | 66 |  |  | 43518.0417 | 80 | 79
2019-02-22 01:30 | 68 | 66 |  |  | 43518.0625 | 80 | 79
2019-02-22 02:00 | 68 | 66 |  |  | 43518.0833 | 79 | 78
2019-02-22 02:30 | 67 | 65 |  |  | 43518.1042 | 78 | 76
2019-02-22 03:00 | 66 | 63 |  |  | 43518.125 | 77 | 76
2019-02-22 03:30 | 66 | 63 |  |  | 43518.1458 | 77 | 76
2019-02-22 04:00 | 66 | 63 |  |  | 43518.1667 | 77 | 76
2019-02-22 04:30 | 67 | 64 |  |  | 43518.1875 | 78 | 77
2019-02-22 05:00 | 68 | 66 |  |  | 43518.2083 | 81 | 79
2019-02-22 05:30 | 70 | 68 |  |  | 43518.2292 | 82 | 81
2019-02-22 06:00 | 72 | 71 |  |  | 43518.25 | 86 | 86
2019-02-22 06:30 | 75 | 74 |  |  | 43518.2708 | 94 | 93
2019-02-22 07:00 | 77 | 76 |  |  | 43518.2917 | 99 | 99
2019-02-22 07:30 | 84 | 82 |  |  | 43518.3125 | 108 | 107
2019-02-22 08:00 | 86 | 84 |  |  | 43518.3333 | 110 | 109
2019-02-22 08:30 | 86 | 85 |  |  | 43518.3542 | 111 | 110
2019-02-22 09:00 | 86 | 85 |  |  | 43518.375 | 114 | 113
2019-02-22 09:30 | 90 | 89 |  |  | 43518.3958 | 115 | 114
2019-02-22 10:00 | 87 | 86 |  |  | 43518.4167 | 113 | 113
2019-02-22 10:30 | 85 | 85 |  |  | 43518.4375 | 115 | 114
2019-02-22 11:00 | 86 | 85 |  |  | 43518.4583 | 110 | 110
2019-02-22 11:30 | 87 | 87 |  |  | 43518.4792 | 113 | 113
2019-02-22 12:00 | 87 | 87 |  |  | 43518.5 | 109 | 108
2019-02-22 12:30 | 99 | 99 |  |  | 43518.5208 | 119 | 119
2019-02-22 13:00 | 100 | 100 |  |  | 43518.5417 | 125 | 125
2019-02-22 13:30 | 94 | 94 |  |  | 43518.5625 | 122 | 122
2019-02-22 14:00 | 85 | 85 |  |  | 43518.5833 | 111 | 111
2019-02-22 14:30 | 83 | 83 |  |  | 43518.6042 | 105 | 105
2019-02-22 15:00 | 85 | 85 |  |  | 43518.625 | 106 | 106
2019-02-22 15:30 | 89 | 88 |  |  | 43518.6458 | 108 | 107
2019-02-22 16:00 | 96 | 95 |  |  | 43518.6667 | 112 | 112
2019-02-22 16:30 | 94 | 93 |  |  | 43518.6875 | 113 | 113
2019-02-22 17:00 | 94 | 94 |  |  | 43518.7083 | 112 | 112
2019-02-22 17:30 | 94 | 93 |  |  | 43518.7292 | 110 | 109
2019-02-22 18:00 | 93 | 92 |  |  | 43518.75 | 109 | 108
2019-02-22 18:30 | 92 | 91 |  |  | 43518.7708 | 106 | 104
2019-02-22 19:00 | 93 | 92 |  |  | 43518.7917 | 107 | 105
2019-02-22 19:30 | 92 | 90 |  |  | 43518.8125 | 105 | 104
2019-02-22 20:00 | 90 | 88 |  |  | 43518.8333 | 103 | 101
2019-02-22 20:30 | 87 | 86 |  |  | 43518.8542 | 99 | 99
2019-02-22 21:00 | 83 | 82 |  |  | 43518.875 | 96 | 95
2019-02-22 21:30 | 79 | 78 |  |  | 43518.8958 | 91 | 91
2019-02-22 22:00 | 76 | 75 |  |  | 43518.9167 | 89 | 88
2019-02-22 22:30 | 73 | 72 |  |  | 43518.9375 | 86 | 86
2019-02-22 23:00 | 70 | 68 |  |  | 43518.9583 | 81 | 80
2019-02-22 23:30 | 65 | 63 |  |  | 43518.9792 | 77 | 76
2019-02-23 | 60 | 57 |  |  | 43519 | 71 | 70
2019-02-23 00:30 | 55 | 52 |  |  | 43519.0208 | 66 | 64
2019-02-23 01:00 | 54 | 51 |  |  | 43519.0417 | 63 | 62
2019-02-23 01:30 | 52 | 49 |  |  | 43519.0625 | 61 | 59
2019-02-23 02:00 | 51 | 48 |  |  | 43519.0833 | 59 | 58
2019-02-23 02:30 | 51 | 48 |  |  | 43519.1042 | 59 | 58
2019-02-23 03:00 | 50 | 47 |  |  | 43519.125 | 58 | 56
2019-02-23 03:30 | 50 | 47 |  |  | 43519.1458 | 57 | 56
2019-02-23 04:00 | 51 | 47 |  |  | 43519.1667 | 58 | 57
2019-02-23 04:30 | 51 | 47 |  |  | 43519.1875 | 58 | 57
2019-02-23 05:00 | 51 | 48 |  |  | 43519.2083 | 59 | 58
2019-02-23 05:30 | 50 | 46 |  |  | 43519.2292 | 58 | 57
2019-02-23 06:00 | 49 | 45 |  |  | 43519.25 | 57 | 56
2019-02-23 06:30 | 48 | 45 |  |  | 43519.2708 | 58 | 57
2019-02-23 07:00 | 47 | 44 |  |  | 43519.2917 | 58 | 57
2019-02-23 07:30 | 46 | 44 |  |  | 43519.3125 | 57 | 57
2019-02-23 08:00 | 46 | 44 |  |  | 43519.3333 | 61 | 60
2019-02-23 08:30 | 49 | 48 |  |  | 43519.3542 | 66 | 66
2019-02-23 09:00 | 51 | 50 |  |  | 43519.375 | 67 | 67
2019-02-23 09:30 | 51 | 50 |  |  | 43519.3958 | 66 | 66
2019-02-23 10:00 | 52 | 51 |  |  | 43519.4167 | 70 | 70
2019-02-23 10:30 | 56 | 55 |  |  | 43519.4375 | 71 | 71
2019-02-23 11:00 | 53 | 52 |  |  | 43519.4583 | 68 | 68
2019-02-23 11:30 | 56 | 55 |  |  | 43519.4792 | 69 | 69
2019-02-23 12:00 | 54 | 53 |  |  | 43519.5 | 71 | 71
2019-02-23 12:30 | 53 | 52 |  |  | 43519.5208 | 69 | 69
2019-02-23 13:00 | 56 | 55 |  |  | 43519.5417 | 71 | 71
2019-02-23 13:30 | 62 | 61 |  |  | 43519.5625 | 75 | 75
2019-02-23 14:00 | 62 | 61 |  |  | 43519.5833 | 72 | 72
2019-02-23 14:30 | 62 | 61 |  |  | 43519.6042 | 76 | 76
2019-02-23 15:00 | 65 | 64 |  |  | 43519.625 | 76 | 76
2019-02-23 15:30 | 68 | 67 |  |  | 43519.6458 | 80 | 80
2019-02-23 16:00 | 69 | 68 |  |  | 43519.6667 | 80 | 80
2019-02-23 16:30 | 72 | 71 |  |  | 43519.6875 | 83 | 82
2019-02-23 17:00 | 68 | 67 |  |  | 43519.7083 | 82 | 82
2019-02-23 17:30 | 70 | 69 |  |  | 43519.7292 | 82 | 82
2019-02-23 18:00 | 69 | 68 |  |  | 43519.75 | 83 | 83
2019-02-23 18:30 | 70 | 68 |  |  | 43519.7708 | 83 | 83
2019-02-23 19:00 | 72 | 71 |  |  | 43519.7917 | 87 | 87
2019-02-23 19:30 | 70 | 69 |  |  | 43519.8125 | 85 | 85
2019-02-23 20:00 | 71 | 69 |  |  | 43519.8333 | 86 | 85
2019-02-23 20:30 | 69 | 68 |  |  | 43519.8542 | 84 | 84
2019-02-23 21:00 | 67 | 66 |  |  | 43519.875 | 80 | 80
2019-02-23 21:30 | 66 | 64 |  |  | 43519.8958 | 78 | 78
2019-02-23 22:00 | 65 | 63 |  |  | 43519.9167 | 77 | 77
2019-02-23 22:30 | 65 | 63 |  |  | 43519.9375 | 77 | 77
2019-02-23 23:00 | 65 | 62 |  |  | 43519.9583 | 74 | 73
2019-02-23 23:30 | 61 | 58 |  |  | 43519.9792 | 73 | 72
2019-02-24 | 58 | 54 |  |  | 43520 | 68 | 67
2019-02-24 00:30 | 54 | 50 |  |  | 43520.0208 | 63 | 61
2019-02-24 01:00 | 51 | 46 |  |  | 43520.0417 | 60 | 58
2019-02-24 01:30 | 50 | 45 |  |  | 43520.0625 | 58 | 56
2019-02-24 02:00 | 49 | 45 |  |  | 43520.0833 | 58 | 57
2019-02-24 02:30 | 49 | 45 |  |  | 43520.1042 | 57 | 56
2019-02-24 03:00 | 48 | 44 |  |  | 43520.125 | 56 | 55
2019-02-24 03:30 | 48 | 44 |  |  | 43520.1458 | 55 | 53
2019-02-24 04:00 | 48 | 44 |  |  | 43520.1667 | 54 | 53
2019-02-24 04:30 | 47 | 43 |  |  | 43520.1875 | 54 | 53
2019-02-24 05:00 | 48 | 44 |  |  | 43520.2083 | 55 | 54
2019-02-24 05:30 | 49 | 46 |  |  | 43520.2292 | 56 | 56
2019-02-24 06:00 | 48 | 43 |  |  | 43520.25 | 55 | 55
2019-02-24 06:30 | 47 | 43 |  |  | 43520.2708 | 56 | 55
2019-02-24 07:00 | 47 | 42 |  |  | 43520.2917 | 56 | 55
2019-02-24 07:30 | 47 | 43 |  |  | 43520.3125 | 56 | 56
2019-02-24 08:00 | 45 | 42 |  |  | 43520.3333 | 55 | 55
2019-02-24 08:30 | 46 | 43 |  |  | 43520.3542 | 58 | 58
2019-02-24 09:00 | 52 | 50 |  |  | 43520.375 | 62 | 62
2019-02-24 09:30 | 54 | 52 |  |  | 43520.3958 | 64 | 64
2019-02-24 10:00 | 56 | 55 |  |  | 43520.4167 | 68 | 68
2019-02-24 10:30 | 58 | 57 |  |  | 43520.4375 | 69 | 69
2019-02-24 11:00 | 55 | 54 |  |  | 43520.4583 | 65 | 65
2019-02-24 11:30 | 53 | 52 |  |  | 43520.4792 | 67 | 67
2019-02-24 12:00 | 52 | 51 |  |  | 43520.5 | 67 | 67
2019-02-24 12:30 | 49 | 47 |  |  | 43520.5208 | 62 | 62
2019-02-24 13:00 | 51 | 49 |  |  | 43520.5417 | 60 | 60
2019-02-24 13:30 | 50 | 48 |  |  | 43520.5625 | 56 | 56
2019-02-24 14:00 | 49 | 47 |  |  | 43520.5833 | 59 | 59
2019-02-24 14:30 | 54 | 53 |  |  | 43520.6042 | 63 | 63
2019-02-24 15:00 | 61 | 60 |  |  | 43520.625 | 67 | 67
2019-02-24 15:30 | 61 | 60 |  |  | 43520.6458 | 73 | 73
2019-02-24 16:00 | 63 | 61 |  |  | 43520.6667 | 73 | 72
2019-02-24 16:30 | 65 | 63 |  |  | 43520.6875 | 75 | 75
2019-02-24 17:00 | 67 | 65 |  |  | 43520.7083 | 79 | 78
2019-02-24 17:30 | 71 | 69 |  |  | 43520.7292 | 82 | 81
2019-02-24 18:00 | 74 | 71 |  |  | 43520.75 | 84 | 83
2019-02-24 18:30 | 74 | 72 |  |  | 43520.7708 | 85 | 84
2019-02-24 19:00 | 77 | 75 |  |  | 43520.7917 | 90 | 89
2019-02-24 19:30 | 75 | 74 |  |  | 43520.8125 | 89 | 88
2019-02-24 20:00 | 74 | 72 |  |  | 43520.8333 | 87 | 86
2019-02-24 20:30 | 74 | 72 |  |  | 43520.8542 | 87 | 86
2019-02-24 21:00 | 72 | 69 |  |  | 43520.875 | 83 | 81
2019-02-24 21:30 | 68 | 65 |  |  | 43520.8958 | 78 | 77
2019-02-24 22:00 | 66 | 63 |  |  | 43520.9167 | 77 | 76
2019-02-24 22:30 | 64 | 62 |  |  | 43520.9375 | 77 | 76
2019-02-24 23:00 | 63 | 60 |  |  | 43520.9583 | 73 | 72
2019-02-24 23:30 | 60 | 56 |  |  | 43520.9792 | 69 | 68
2019-02-25 | 55 | 49 |  |  | 43521 | 63 | 61
2019-02-25 00:30 | 51 | 45 |  |  | 43521.0208 | 60 | 57
2019-02-25 01:00 | 48 | 42 |  |  | 43521.0417 | 55 | 53
2019-02-25 01:30 | 47 | 42 |  |  | 43521.0625 | 54 | 53
2019-02-25 02:00 | 47 | 42 |  |  | 43521.0833 | 54 | 53
2019-02-25 02:30 | 47 | 42 |  |  | 43521.1042 | 53 | 51
2019-02-25 03:00 | 47 | 42 |  |  | 43521.125 | 53 | 51
2019-02-25 03:30 | 47 | 42 |  |  | 43521.1458 | 54 | 52
2019-02-25 04:00 | 47 | 42 |  |  | 43521.1667 | 55 | 53
2019-02-25 04:30 | 49 | 44 |  |  | 43521.1875 | 55 | 53
2019-02-25 05:00 | 50 | 46 |  |  | 43521.2083 | 57 | 56
2019-02-25 05:30 | 52 | 50 |  |  | 43521.2292 | 62 | 61
2019-02-25 06:00 | 53 | 52 |  |  | 43521.25 | 65 | 65
2019-02-25 06:30 | 60 | 59 |  |  | 43521.2708 | 75 | 75
2019-02-25 07:00 | 63 | 62 |  |  | 43521.2917 | 82 | 81
2019-02-25 07:30 | 68 | 67 |  |  | 43521.3125 | 87 | 87
2019-02-25 08:00 | 63 | 62 |  |  | 43521.3333 | 87 | 87
2019-02-25 08:30 | 64 | 63 |  |  | 43521.3542 | 90 | 90
2019-02-25 09:00 | 64 | 64 |  |  | 43521.375 | 88 | 88
2019-02-25 09:30 | 64 | 63 |  |  | 43521.3958 | 84 | 84
2019-02-25 10:00 | 61 | 61 |  |  | 43521.4167 | 87 | 87
2019-02-25 10:30 | 65 | 64 |  |  | 43521.4375 | 85 | 85
2019-02-25 11:00 | 59 | 58 |  |  | 43521.4583 | 83 | 83
2019-02-25 11:30 | 59 | 58 |  |  | 43521.4792 | 80 | 80
2019-02-25 12:00 | 63 | 62 |  |  | 43521.5 | 83 | 83
2019-02-25 12:30 | 58 | 56 |  |  | 43521.5208 | 83 | 83
2019-02-25 13:00 | 66 | 65 |  |  | 43521.5417 | 86 | 86
2019-02-25 13:30 | 66 | 65 |  |  | 43521.5625 | 85 | 85
2019-02-25 14:00 | 69 | 68 |  |  | 43521.5833 | 88 | 88
2019-02-25 14:30 | 69 | 69 |  |  | 43521.6042 | 88 | 88
2019-02-25 15:00 | 70 | 69 |  |  | 43521.625 | 89 | 88
2019-02-25 15:30 | 73 | 72 |  |  | 43521.6458 | 91 | 91
2019-02-25 16:00 | 74 | 73 |  |  | 43521.6667 | 91 | 91
2019-02-25 16:30 | 74 | 72 |  |  | 43521.6875 | 90 | 90
2019-02-25 17:00 | 77 | 76 |  |  | 43521.7083 | 94 | 94
2019-02-25 17:30 | 78 | 76 |  |  | 43521.7292 | 92 | 91
2019-02-25 18:00 | 80 | 78 |  |  | 43521.75 | 92 | 91
2019-02-25 18:30 | 78 | 76 |  |  | 43521.7708 | 89 | 88
2019-02-25 19:00 | 79 | 78 |  |  | 43521.7917 | 90 | 89
2019-02-25 19:30 | 82 | 81 |  |  | 43521.8125 | 92 | 92
2019-02-25 20:00 | 80 | 79 |  |  | 43521.8333 | 91 | 90
2019-02-25 20:30 | 79 | 78 |  |  | 43521.8542 | 89 | 88
2019-02-25 21:00 | 78 | 77 |  |  | 43521.875 | 89 | 88
2019-02-25 21:30 | 75 | 74 |  |  | 43521.8958 | 85 | 84
2019-02-25 22:00 | 71 | 69 |  |  | 43521.9167 | 82 | 81
2019-02-25 22:30 | 70 | 68 |  |  | 43521.9375 | 80 | 78
2019-02-25 23:00 | 64 | 62 |  |  | 43521.9583 | 73 | 71
2019-02-25 23:30 | 60 | 56 |  |  | 43521.9792 | 69 | 67
2019-02-26 | 55 | 51 |  |  | 43522 | 64 | 61
2019-02-26 00:30 | 53 | 48 |  |  | 43522.0208 | 59 | 57
2019-02-26 01:00 | 50 | 45 |  |  | 43522.0417 | 56 | 53
2019-02-26 01:30 | 50 | 45 |  |  | 43522.0625 | 55 | 52
2019-02-26 02:00 | 49 | 44 |  |  | 43522.0833 | 55 | 51
2019-02-26 02:30 | 49 | 43 |  |  | 43522.1042 | 54 | 51
2019-02-26 03:00 | 49 | 43 |  |  | 43522.125 | 55 | 51
2019-02-26 03:30 | 49 | 43 |  |  | 43522.1458 | 54 | 51
2019-02-26 04:00 | 50 | 45 |  |  | 43522.1667 | 56 | 53
2019-02-26 04:30 | 51 | 46 |  |  | 43522.1875 | 57 | 54
2019-02-26 05:00 | 53 | 49 |  |  | 43522.2083 | 60 | 57
2019-02-26 05:30 | 53 | 49 |  |  | 43522.2292 | 61 | 59
2019-02-26 06:00 | 53 | 50 |  |  | 43522.25 | 63 | 62
2019-02-26 06:30 | 58 | 55 |  |  | 43522.2708 | 71 | 70
2019-02-26 07:00 | 60 | 58 |  |  | 43522.2917 | 76 | 76
2019-02-26 07:30 | 66 | 64 |  |  | 43522.3125 | 84 | 84
2019-02-26 08:00 | 70 | 68 |  |  | 43522.3333 | 88 | 88
2019-02-26 08:30 | 69 | 68 |  |  | 43522.3542 | 88 | 87
2019-02-26 09:00 | 69 | 68 |  |  | 43522.375 | 91 | 91
2019-02-26 09:30 | 67 | 66 |  |  | 43522.3958 | 90 | 89
2019-02-26 10:00 | 66 | 66 |  |  | 43522.4167 | 91 | 91
2019-02-26 10:30 | 70 | 70 |  |  | 43522.4375 | 92 | 92
2019-02-26 11:00 | 69 | 69 |  |  | 43522.4583 | 92 | 92
2019-02-26 11:30 | 71 | 71 |  |  | 43522.4792 | 90 | 90
2019-02-26 12:00 | 70 | 70 |  |  | 43522.5 | 91 | 91
2019-02-26 12:30 | 73 | 73 |  |  | 43522.5208 | 91 | 91
2019-02-26 13:00 | 70 | 70 |  |  | 43522.5417 | 91 | 91
2019-02-26 13:30 | 70 | 69 |  |  | 43522.5625 | 89 | 89
2019-02-26 14:00 | 70 | 69 |  |  | 43522.5833 | 85 | 85
2019-02-26 14:30 | 72 | 72 |  |  | 43522.6042 | 90 | 90
2019-02-26 15:00 | 70 | 69 |  |  | 43522.625 | 90 | 90
2019-02-26 15:30 | 69 | 68 |  |  | 43522.6458 | 89 | 89
2019-02-26 16:00 | 68 | 68 |  |  | 43522.6667 | 87 | 87
2019-02-26 16:30 | 69 | 69 |  |  | 43522.6875 | 88 | 88
2019-02-26 17:00 | 74 | 73 |  |  | 43522.7083 | 91 | 91
2019-02-26 17:30 | 78 | 78 |  |  | 43522.7292 | 93 | 93
2019-02-26 18:00 | 78 | 77 |  |  | 43522.75 | 92 | 92
2019-02-26 18:30 | 80 | 79 |  |  | 43522.7708 | 92 | 91
2019-02-26 19:00 | 85 | 84 |  |  | 43522.7917 | 96 | 96
2019-02-26 19:30 | 83 | 82 |  |  | 43522.8125 | 96 | 95
2019-02-26 20:00 | 82 | 81 |  |  | 43522.8333 | 94 | 93
2019-02-26 20:30 | 81 | 80 |  |  | 43522.8542 | 94 | 93
2019-02-26 21:00 | 77 | 76 |  |  | 43522.875 | 89 | 88
2019-02-26 21:30 | 76 | 75 |  |  | 43522.8958 | 86 | 85
2019-02-26 22:00 | 75 | 73 |  |  | 43522.9167 | 85 | 84
2019-02-26 22:30 | 71 | 70 |  |  | 43522.9375 | 83 | 81
2019-02-26 23:00 | 66 | 64 |  |  | 43522.9583 | 75 | 74
2019-02-26 23:30 | 60 | 57 |  |  | 43522.9792 | 71 | 69
2019-02-27 | 56 | 53 |  |  | 43523 | 66 | 64
2019-02-27 00:30 | 56 | 51 |  |  | 43523.0208 | 64 | 61
2019-02-27 01:00 | 54 | 49 |  |  | 43523.0417 | 60 | 58
2019-02-27 01:30 | 52 | 47 |  |  | 43523.0625 | 57 | 55
2019-02-27 02:00 | 51 | 46 |  |  | 43523.0833 | 57 | 55
2019-02-27 02:30 | 51 | 46 |  |  | 43523.1042 | 57 | 55
2019-02-27 03:00 | 52 | 47 |  |  | 43523.125 | 57 | 55
2019-02-27 03:30 | 52 | 47 |  |  | 43523.1458 | 57 | 55
2019-02-27 04:00 | 51 | 46 |  |  | 43523.1667 | 56 | 53
2019-02-27 04:30 | 50 | 45 |  |  | 43523.1875 | 56 | 54
2019-02-27 05:00 | 54 | 49 |  |  | 43523.2083 | 60 | 58
2019-02-27 05:30 | 55 | 52 |  |  | 43523.2292 | 64 | 62
2019-02-27 06:00 | 57 | 54 |  |  | 43523.25 | 66 | 65
2019-02-27 06:30 | 61 | 60 |  |  | 43523.2708 | 74 | 74
2019-02-27 07:00 | 63 | 62 |  |  | 43523.2917 | 80 | 80
2019-02-27 07:30 | 67 | 66 |  |  | 43523.3125 | 85 | 85
2019-02-27 08:00 | 69 | 69 |  |  | 43523.3333 | 89 | 89
2019-02-27 08:30 | 68 | 68 |  |  | 43523.3542 | 89 | 89
2019-02-27 09:00 | 70 | 70 |  |  | 43523.375 | 94 | 94
2019-02-27 09:30 | 74 | 74 |  |  | 43523.3958 | 94 | 93
2019-02-27 10:00 | 69 | 69 |  |  | 43523.4167 | 91 | 90
2019-02-27 10:30 | 68 | 68 |  |  | 43523.4375 | 89 | 89
2019-02-27 11:00 | 71 | 71 |  |  | 43523.4583 | 89 | 89
2019-02-27 11:30 | 70 | 69 |  |  | 43523.4792 | 93 | 93
2019-02-27 12:00 | 74 | 74 |  |  | 43523.5 | 93 | 93
2019-02-27 12:30 | 73 | 72 |  |  | 43523.5208 | 91 | 91
2019-02-27 13:00 | 71 | 70 |  |  | 43523.5417 | 93 | 93
2019-02-27 13:30 | 73 | 72 |  |  | 43523.5625 | 93 | 92
2019-02-27 14:00 | 74 | 73 |  |  | 43523.5833 | 92 | 91
2019-02-27 14:30 | 72 | 71 |  |  | 43523.6042 | 92 | 92
2019-02-27 15:00 | 71 | 70 |  |  | 43523.625 | 90 | 90
2019-02-27 15:30 | 73 | 71 |  |  | 43523.6458 | 90 | 90
2019-02-27 16:00 | 72 | 71 |  |  | 43523.6667 | 89 | 89
2019-02-27 16:30 | 76 | 74 |  |  | 43523.6875 | 93 | 92
2019-02-27 17:00 | 76 | 75 |  |  | 43523.7083 | 92 | 91
2019-02-27 17:30 | 76 | 75 |  |  | 43523.7292 | 90 | 89
2019-02-27 18:00 | 76 | 74 |  |  | 43523.75 | 88 | 86
2019-02-27 18:30 | 79 | 76 |  |  | 43523.7708 | 90 | 87
2019-02-27 19:00 | 82 | 80 |  |  | 43523.7917 | 92 | 90
2019-02-27 19:30 | 80 | 78 |  |  | 43523.8125 | 91 | 89
2019-02-27 20:00 | 81 | 79 |  |  | 43523.8333 | 91 | 90
2019-02-27 20:30 | 80 | 78 |  |  | 43523.8542 | 89 | 88
2019-02-27 21:00 | 76 | 75 |  |  | 43523.875 | 85 | 85
2019-02-27 21:30 | 72 | 71 |  |  | 43523.8958 | 81 | 81
2019-02-27 22:00 | 70 | 68 |  |  | 43523.9167 | 79 | 78
2019-02-27 22:30 | 68 | 66 |  |  | 43523.9375 | 79 | 78
2019-02-27 23:00 | 65 | 62 |  |  | 43523.9583 | 73 | 72
2019-02-27 23:30 | 60 | 56 |  |  | 43523.9792 | 68 | 66
2019-02-28 | 56 | 50 |  |  | 43524 | 63 | 61
2019-02-28 00:30 | 53 | 46 |  |  | 43524.0208 | 58 | 56
2019-02-28 01:00 | 51 | 44 |  |  | 43524.0417 | 54 | 52
2019-02-28 01:30 | 48 | 41 |  |  | 43524.0625 | 52 | 49
2019-02-28 02:00 | 47 | 40 |  |  | 43524.0833 | 51 | 48
2019-02-28 02:30 | 43 | 40 |  |  | 43524.1042 | 52 | 47
2019-02-28 03:00 | 42 | 39 |  |  | 43524.125 | 54 | 47
2019-02-28 03:30 | 41 | 39 |  |  | 43524.1458 | 56 | 48
2019-02-28 04:00 | 41 | 40 |  |  | 43524.1667 | 57 | 49
2019-02-28 04:30 | 42 | 41 |  |  | 43524.1875 | 58 | 50
2019-02-28 05:00 | 45 | 44 |  |  | 43524.2083 | 61 | 55
2019-02-28 05:30 | 46 | 45 |  |  | 43524.2292 | 62 | 57
2019-02-28 06:00 | 49 | 48 |  |  | 43524.25 | 65 | 61
2019-02-28 06:30 | 52 | 52 |  |  | 43524.2708 | 68 | 66
2019-02-28 07:00 | 53 | 53 |  |  | 43524.2917 | 73 | 72
2019-02-28 07:30 | 64 | 64 |  |  | 43524.3125 | 86 | 85
2019-02-28 08:00 | 68 | 67 |  |  | 43524.3333 | 91 | 90
2019-02-28 08:30 | 69 | 69 |  |  | 43524.3542 | 89 | 89
2019-02-28 09:00 | 69 | 68 |  |  | 43524.375 | 87 | 87
2019-02-28 09:30 | 66 | 66 |  |  | 43524.3958 | 85 | 85
2019-02-28 10:00 | 57 | 57 |  |  | 43524.4167 | 81 | 81
2019-02-28 10:30 | 66 | 65 |  |  | 43524.4375 | 83 | 83
2019-02-28 11:00 | 64 | 63 |  |  | 43524.4583 | 78 | 78
2019-02-28 11:30 | 61 | 60 |  |  | 43524.4792 | 82 | 82
2019-02-28 12:00 | 66 | 65 |  |  | 43524.5 | 87 | 87
2019-02-28 12:30 | 63 | 62 |  |  | 43524.5208 | 80 | 80
2019-02-28 13:00 | 61 | 61 |  |  | 43524.5417 | 79 | 78
2019-02-28 13:30 | 67 | 66 |  |  | 43524.5625 | 80 | 80
2019-02-28 14:00 | 67 | 66 |  |  | 43524.5833 | 85 | 85
2019-02-28 14:30 | 69 | 68 |  |  | 43524.6042 | 84 | 84
2019-02-28 15:00 | 66 | 65 |  |  | 43524.625 | 82 | 82
2019-02-28 15:30 | 66 | 65 |  |  | 43524.6458 | 83 | 83
2019-02-28 16:00 | 67 | 67 |  |  | 43524.6667 | 85 | 84
2019-02-28 16:30 | 69 | 69 |  |  | 43524.6875 | 87 | 86
2019-02-28 17:00 | 74 | 74 |  |  | 43524.7083 | 91 | 90
2019-02-28 17:30 | 74 | 74 |  |  | 43524.7292 | 92 | 91
2019-02-28 18:00 | 76 | 76 |  |  | 43524.75 | 92 | 91
2019-02-28 18:30 | 78 | 78 |  |  | 43524.7708 | 93 | 91
2019-02-28 19:00 | 82 | 82 |  |  | 43524.7917 | 96 | 95
2019-02-28 19:30 | 81 | 81 |  |  | 43524.8125 | 95 | 94
2019-02-28 20:00 | 81 | 81 |  |  | 43524.8333 | 94 | 92
2019-02-28 20:30 | 80 | 80 |  |  | 43524.8542 | 93 | 91
2019-02-28 21:00 | 78 | 78 |  |  | 43524.875 | 90 | 88
2019-02-28 21:30 | 73 | 73 |  |  | 43524.8958 | 84 | 82
2019-02-28 22:00 | 70 | 70 |  |  | 43524.9167 | 82 | 79
2019-02-28 22:30 | 66 | 66 |  |  | 43524.9375 | 79 | 76
2019-02-28 23:00 | 60 | 60 |  |  | 43524.9583 | 73 | 69
2019-02-28 23:30 | 51 | 51 |  |  | 43524.9792 | 67 | 62
2019-03-01 | 46 | 45 |  |  | 43525 | 62 | 57
2019-03-01 00:30 | 41 | 41 |  |  | 43525.0208 | 57 | 52
2019-03-01 01:00 | 40 | 39 |  |  | 43525.0417 | 55 | 48
2019-03-01 01:30 | 39 | 38 |  |  | 43525.0625 | 54 | 47
2019-03-01 02:00 | 39 | 38 |  |  | 43525.0833 | 54 | 47
2019-03-01 02:30 | 39 | 38 |  |  | 43525.1042 | 54 | 47
2019-03-01 03:00 | 40 | 39 |  |  | 43525.125 | 54 | 47
2019-03-01 03:30 | 42 | 41 |  |  | 43525.1458 | 57 | 50
2019-03-01 04:00 | 42 | 41 |  |  | 43525.1667 | 55 | 50
2019-03-01 04:30 | 44 | 43 |  |  | 43525.1875 | 57 | 52
2019-03-01 05:00 | 46 | 45 |  |  | 43525.2083 | 59 | 54
2019-03-01 05:30 | 47 | 46 |  |  | 43525.2292 | 59 | 55
2019-03-01 06:00 | 46 | 46 |  |  | 43525.25 | 60 | 57
2019-03-01 06:30 | 51 | 51 |  |  | 43525.2708 | 68 | 67
2019-03-01 07:00 | 54 | 54 |  |  | 43525.2917 | 74 | 73
2019-03-01 07:30 | 61 | 61 |  |  | 43525.3125 | 83 | 82
2019-03-01 08:00 | 64 | 63 |  |  | 43525.3333 | 86 | 85
2019-03-01 08:30 | 64 | 64 |  |  | 43525.3542 | 87 | 87
2019-03-01 09:00 | 63 | 62 |  |  | 43525.375 | 86 | 85
2019-03-01 09:30 | 66 | 66 |  |  | 43525.3958 | 91 | 90
2019-03-01 10:00 | 66 | 66 |  |  | 43525.4167 | 89 | 88
2019-03-01 10:30 | 65 | 64 |  |  | 43525.4375 | 88 | 87
2019-03-01 11:00 | 65 | 65 |  |  | 43525.4583 | 85 | 84
2019-03-01 11:30 | 64 | 64 |  |  | 43525.4792 | 85 | 84
2019-03-01 12:00 | 64 | 63 |  |  | 43525.5 | 85 | 84
2019-03-01 12:30 | 62 | 62 |  |  | 43525.5208 | 83 | 82
2019-03-01 13:00 | 66 | 65 |  |  | 43525.5417 | 80 | 79
2019-03-01 13:30 | 63 | 63 |  |  | 43525.5625 | 82 | 81
2019-03-01 14:00 | 64 | 63 |  |  | 43525.5833 | 84 | 83
2019-03-01 14:30 | 63 | 63 |  |  | 43525.6042 | 81 | 79
2019-03-01 15:00 | 64 | 63 |  |  | 43525.625 | 79 | 77
2019-03-01 15:30 | 66 | 66 |  |  | 43525.6458 | 86 | 84
2019-03-01 16:00 | 67 | 67 |  |  | 43525.6667 | 87 | 85
2019-03-01 16:30 | 71 | 71 |  |  | 43525.6875 | 93 | 91
2019-03-01 17:00 | 73 | 73 |  |  | 43525.7083 | 93 | 91
2019-03-01 17:30 | 73 | 73 |  |  | 43525.7292 | 92 | 88
2019-03-01 18:00 | 72 | 71 |  |  | 43525.75 | 89 | 85
2019-03-01 18:30 | 71 | 71 |  |  | 43525.7708 | 89 | 84
2019-03-01 19:00 | 72 | 72 |  |  | 43525.7917 | 89 | 85
2019-03-01 19:30 | 70 | 70 |  |  | 43525.8125 | 88 | 83
2019-03-01 20:00 | 70 | 70 |  |  | 43525.8333 | 87 | 83
2019-03-01 20:30 | 69 | 69 |  |  | 43525.8542 | 85 | 80
2019-03-01 21:00 | 66 | 66 |  |  | 43525.875 | 83 | 77
2019-03-01 21:30 | 61 | 61 |  |  | 43525.8958 | 76 | 71
2019-03-01 22:00 | 60 | 60 |  |  | 43525.9167 | 74 | 70
2019-03-01 22:30 | 57 | 57 |  |  | 43525.9375 | 72 | 68
2019-03-01 23:00 | 54 | 54 |  |  | 43525.9583 | 67 | 63
2019-03-01 23:30 | 51 | 51 |  |  | 43525.9792 | 66 | 61
2019-03-02 | 49 | 48 |  |  | 43526 | 63 | 57
2019-03-02 00:30 | 44 | 43 |  |  | 43526.0208 | 59 | 52
2019-03-02 01:00 | 42 | 41 |  |  | 43526.0417 | 56 | 49
2019-03-02 01:30 | 41 | 40 |  |  | 43526.0625 | 55 | 48
2019-03-02 02:00 | 42 | 41 |  |  | 43526.0833 | 54 | 48
2019-03-02 02:30 | 40 | 38 |  |  | 43526.1042 | 52 | 47
2019-03-02 03:00 | 39 | 37 |  |  | 43526.125 | 52 | 47
2019-03-02 03:30 | 38 | 37 |  |  | 43526.1458 | 52 | 46
2019-03-02 04:00 | 38 | 37 |  |  | 43526.1667 | 52 | 47
2019-03-02 04:30 | 38 | 37 |  |  | 43526.1875 | 52 | 47
2019-03-02 05:00 | 39 | 38 |  |  | 43526.2083 | 52 | 47
2019-03-02 05:30 | 41 | 39 |  |  | 43526.2292 | 54 | 49
2019-03-02 06:00 | 40 | 39 |  |  | 43526.25 | 55 | 50
2019-03-02 06:30 | 42 | 41 |  |  | 43526.2708 | 58 | 53
2019-03-02 07:00 | 42 | 41 |  |  | 43526.2917 | 58 | 54
2019-03-02 07:30 | 42 | 41 |  |  | 43526.3125 | 58 | 55
2019-03-02 08:00 | 45 | 45 |  |  | 43526.3333 | 62 | 59
2019-03-02 08:30 | 44 | 44 |  |  | 43526.3542 | 60 | 57
2019-03-02 09:00 | 45 | 45 |  |  | 43526.375 | 59 | 57
2019-03-02 09:30 | 40 | 40 |  |  | 43526.3958 | 58 | 56
2019-03-02 10:00 | 42 | 42 |  |  | 43526.4167 | 61 | 59
2019-03-02 10:30 | 39 | 38 |  |  | 43526.4375 | 58 | 56
2019-03-02 11:00 | 44 | 43 |  |  | 43526.4583 | 62 | 60
2019-03-02 11:30 | 40 | 40 |  |  | 43526.4792 | 56 | 53
2019-03-02 12:00 | 41 | 40 |  |  | 43526.5 | 53 | 49
2019-03-02 12:30 | 41 | 41 |  |  | 43526.5208 | 57 | 54
2019-03-02 13:00 | 38 | 38 |  |  | 43526.5417 | 55 | 52
2019-03-02 13:30 | 39 | 39 |  |  | 43526.5625 | 56 | 53
2019-03-02 14:00 | 41 | 41 |  |  | 43526.5833 | 57 | 54
2019-03-02 14:30 | 43 | 43 |  |  | 43526.6042 | 61 | 58
2019-03-02 15:00 | 47 | 47 |  |  | 43526.625 | 64 | 61
2019-03-02 15:30 | 46 | 46 |  |  | 43526.6458 | 62 | 58
2019-03-02 16:00 | 51 | 50 |  |  | 43526.6667 | 66 | 63
2019-03-02 16:30 | 52 | 52 |  |  | 43526.6875 | 65 | 61
2019-03-02 17:00 | 54 | 54 |  |  | 43526.7083 | 70 | 66
2019-03-02 17:30 | 56 | 55 |  |  | 43526.7292 | 72 | 68
2019-03-02 18:00 | 62 | 62 |  |  | 43526.75 | 77 | 73
2019-03-02 18:30 | 65 | 65 |  |  | 43526.7708 | 80 | 76
2019-03-02 19:00 | 69 | 69 |  |  | 43526.7917 | 85 | 81
2019-03-02 19:30 | 66 | 65 |  |  | 43526.8125 | 81 | 77
2019-03-02 20:00 | 67 | 66 |  |  | 43526.8333 | 82 | 78
2019-03-02 20:30 | 65 | 64 |  |  | 43526.8542 | 80 | 76
2019-03-02 21:00 | 61 | 61 |  |  | 43526.875 | 76 | 72
2019-03-02 21:30 | 60 | 59 |  |  | 43526.8958 | 74 | 70
2019-03-02 22:00 | 57 | 57 |  |  | 43526.9167 | 72 | 68
2019-03-02 22:30 | 56 | 55 |  |  | 43526.9375 | 71 | 67
2019-03-02 23:00 | 54 | 53 |  |  | 43526.9583 | 68 | 63
2019-03-02 23:30 | 53 | 52 |  |  | 43526.9792 | 67 | 62
2019-03-03 | 49 | 48 |  |  | 43527 | 65 | 59
2019-03-03 00:30 | 45 | 43 |  |  | 43527.0208 | 60 | 53
2019-03-03 01:00 | 42 | 41 |  |  | 43527.0417 | 57 | 50
2019-03-03 01:30 | 41 | 39 |  |  | 43527.0625 | 56 | 48
2019-03-03 02:00 | 41 | 39 |  |  | 43527.0833 | 55 | 47
2019-03-03 02:30 | 40 | 37 |  |  | 43527.1042 | 54 | 45
2019-03-03 03:00 | 40 | 38 |  |  | 43527.125 | 54 | 45
2019-03-03 03:30 | 39 | 36 |  |  | 43527.1458 | 53 | 44
2019-03-03 04:00 | 39 | 37 |  |  | 43527.1667 | 53 | 44
2019-03-03 04:30 | 38 | 36 |  |  | 43527.1875 | 53 | 44
2019-03-03 05:00 | 39 | 37 |  |  | 43527.2083 | 54 | 45
2019-03-03 05:30 | 39 | 37 |  |  | 43527.2292 | 53 | 44
2019-03-03 06:00 | 37 | 35 |  |  | 43527.25 | 52 | 43
2019-03-03 06:30 | 37 | 35 |  |  | 43527.2708 | 53 | 44
2019-03-03 07:00 | 36 | 34 |  |  | 43527.2917 | 52 | 43
2019-03-03 07:30 | 37 | 35 |  |  | 43527.3125 | 53 | 46
2019-03-03 08:00 | 39 | 38 |  |  | 43527.3333 | 57 | 51
2019-03-03 08:30 | 42 | 42 |  |  | 43527.3542 | 58 | 53
2019-03-03 09:00 | 40 | 39 |  |  | 43527.375 | 56 | 51
2019-03-03 09:30 | 42 | 42 |  |  | 43527.3958 | 61 | 57
2019-03-03 10:00 | 40 | 40 |  |  | 43527.4167 | 52 | 48
2019-03-03 10:30 | 39 | 39 |  |  | 43527.4375 | 56 | 53
2019-03-03 11:00 | 43 | 43 |  |  | 43527.4583 | 58 | 55
2019-03-03 11:30 | 43 | 43 |  |  | 43527.4792 | 52 | 49
2019-03-03 12:00 | 42 | 42 |  |  | 43527.5 | 55 | 52
2019-03-03 12:30 | 41 | 41 |  |  | 43527.5208 | 51 | 48
2019-03-03 13:00 | 36 | 36 |  |  | 43527.5417 | 50 | 47
2019-03-03 13:30 | 38 | 38 |  |  | 43527.5625 | 53 | 50
2019-03-03 14:00 | 41 | 41 |  |  | 43527.5833 | 55 | 52
2019-03-03 14:30 | 42 | 42 |  |  | 43527.6042 | 56 | 53
2019-03-03 15:00 | 41 | 40 |  |  | 43527.625 | 54 | 52
2019-03-03 15:30 | 43 | 43 |  |  | 43527.6458 | 57 | 55
2019-03-03 16:00 | 43 | 43 |  |  | 43527.6667 | 57 | 55
2019-03-03 16:30 | 48 | 48 |  |  | 43527.6875 | 62 | 59
2019-03-03 17:00 | 50 | 50 |  |  | 43527.7083 | 65 | 62
2019-03-03 17:30 | 52 | 52 |  |  | 43527.7292 | 66 | 63
2019-03-03 18:00 | 59 | 59 |  |  | 43527.75 | 73 | 70
2019-03-03 18:30 | 62 | 62 |  |  | 43527.7708 | 78 | 75
2019-03-03 19:00 | 67 | 67 |  |  | 43527.7917 | 83 | 80
2019-03-03 19:30 | 67 | 67 |  |  | 43527.8125 | 82 | 80
2019-03-03 20:00 | 66 | 66 |  |  | 43527.8333 | 83 | 80
2019-03-03 20:30 | 67 | 66 |  |  | 43527.8542 | 83 | 80
2019-03-03 21:00 | 67 | 66 |  |  | 43527.875 | 84 | 81
2019-03-03 21:30 | 64 | 64 |  |  | 43527.8958 | 80 | 77
2019-03-03 22:00 | 63 | 62 |  |  | 43527.9167 | 80 | 76
2019-03-03 22:30 | 58 | 58 |  |  | 43527.9375 | 76 | 72
2019-03-03 23:00 | 55 | 54 |  |  | 43527.9583 | 71 | 66
2019-03-03 23:30 | 51 | 50 |  |  | 43527.9792 | 67 | 62
2019-03-04 | 47 | 46 |  |  | 43528 | 64 | 59
2019-03-04 00:30 | 44 | 42 |  |  | 43528.0208 | 60 | 53
2019-03-04 01:00 | 40 | 38 |  |  | 43528.0417 | 57 | 49
2019-03-04 01:30 | 43 | 38 |  |  | 43528.0625 | 52 | 48
2019-03-04 02:00 | 44 | 37 |  |  | 43528.0833 | 51 | 48
2019-03-04 02:30 | 43 | 36 |  |  | 43528.1042 | 49 | 46
2019-03-04 03:00 | 43 | 36 |  |  | 43528.125 | 49 | 46
2019-03-04 03:30 | 44 | 37 |  |  | 43528.1458 | 50 | 47
2019-03-04 04:00 | 45 | 38 |  |  | 43528.1667 | 50 | 47
2019-03-04 04:30 | 44 | 38 |  |  | 43528.1875 | 51 | 48
2019-03-04 05:00 | 46 | 40 |  |  | 43528.2083 | 54 | 51
2019-03-04 05:30 | 50 | 45 |  |  | 43528.2292 | 58 | 56
2019-03-04 06:00 | 51 | 48 |  |  | 43528.25 | 60 | 59
2019-03-04 06:30 | 54 | 52 |  |  | 43528.2708 | 68 | 68
2019-03-04 07:00 | 56 | 55 |  |  | 43528.2917 | 73 | 73
2019-03-04 07:30 | 62 | 61 |  |  | 43528.3125 | 82 | 82
2019-03-04 08:00 | 66 | 66 |  |  | 43528.3333 | 89 | 89
2019-03-04 08:30 | 70 | 68 |  |  | 43528.3542 | 94 | 93
2019-03-04 09:00 | 72 | 71 |  |  | 43528.375 | 99 | 97
2019-03-04 09:30 | 76 | 72 |  |  | 43528.3958 | 101 | 97
2019-03-04 10:00 | 72 | 68 |  |  | 43528.4167 | 95 | 91
2019-03-04 10:30 | 72 | 69 |  |  | 43528.4375 | 97 | 93
2019-03-04 11:00 | 72 | 69 |  |  | 43528.4583 | 96 | 93
2019-03-04 11:30 | 72 | 69 |  |  | 43528.4792 | 93 | 90
2019-03-04 12:00 | 72 | 69 |  |  | 43528.5 | 92 | 89
2019-03-04 12:30 | 69 | 66 |  |  | 43528.5208 | 90 | 86
2019-03-04 13:00 | 68 | 64 |  |  | 43528.5417 | 89 | 86
2019-03-04 13:30 | 69 | 65 |  |  | 43528.5625 | 90 | 86
2019-03-04 14:00 | 68 | 64 |  |  | 43528.5833 | 90 | 87
2019-03-04 14:30 | 70 | 67 |  |  | 43528.6042 | 93 | 90
2019-03-04 15:00 | 71 | 68 |  |  | 43528.625 | 93 | 90
2019-03-04 15:30 | 71 | 67 |  |  | 43528.6458 | 90 | 87
2019-03-04 16:00 | 74 | 70 |  |  | 43528.6667 | 91 | 89
2019-03-04 16:30 | 79 | 75 |  |  | 43528.6875 | 97 | 95
2019-03-04 17:00 | 82 | 78 |  |  | 43528.7083 | 98 | 96
2019-03-04 17:30 | 86 | 81 |  |  | 43528.7292 | 98 | 97
2019-03-04 18:00 | 87 | 82 |  |  | 43528.75 | 97 | 96
2019-03-04 18:30 | 89 | 84 |  |  | 43528.7708 | 98 | 97
2019-03-04 19:00 | 92 | 87 |  |  | 43528.7917 | 101 | 100
2019-03-04 19:30 | 90 | 85 |  |  | 43528.8125 | 100 | 99
2019-03-04 20:00 | 89 | 83 |  |  | 43528.8333 | 97 | 97
2019-03-04 20:30 | 87 | 81 |  |  | 43528.8542 | 95 | 94
2019-03-04 21:00 | 85 | 79 |  |  | 43528.875 | 92 | 91
2019-03-04 21:30 | 84 | 77 |  |  | 43528.8958 | 89 | 89
2019-03-04 22:00 | 82 | 74 |  |  | 43528.9167 | 87 | 87
2019-03-04 22:30 | 79 | 70 |  |  | 43528.9375 | 83 | 83
2019-03-04 23:00 | 75 | 64 |  |  | 43528.9583 | 76 | 76
2019-03-04 23:30 | 71 | 59 |  |  | 43528.9792 | 72 | 72
2019-03-05 | 68 | 54 |  |  | 43529 | 66 | 66
2019-03-05 00:30 | 69 | 49 |  |  | 43529.0208 | 60 | 60
2019-03-05 01:00 | 74 | 46 |  |  | 43529.0417 | 54 | 54
2019-03-05 01:30 | 74 | 44 |  |  | 43529.0625 | 52 | 52
2019-03-05 02:00 | 74 | 44 |  |  | 43529.0833 | 53 | 52
2019-03-05 02:30 | 73 | 44 |  |  | 43529.1042 | 52 | 51
2019-03-05 03:00 | 72 | 43 |  |  | 43529.125 | 51 | 51
2019-03-05 03:30 | 72 | 41 |  |  | 43529.1458 | 51 | 50
2019-03-05 04:00 | 73 | 43 |  |  | 43529.1667 | 52 | 51
2019-03-05 04:30 | 75 | 45 |  |  | 43529.1875 | 54 | 54
2019-03-05 05:00 | 76 | 48 |  |  | 43529.2083 | 57 | 56
2019-03-05 05:30 | 76 | 50 |  |  | 43529.2292 | 60 | 59
2019-03-05 06:00 | 64 | 50 |  |  | 43529.25 | 62 | 61
2019-03-05 06:30 | 63 | 56 |  |  | 43529.2708 | 74 | 72
2019-03-05 07:00 | 68 | 59 |  |  | 43529.2917 | 81 | 78
2019-03-05 07:30 | 71 | 64 |  |  | 43529.3125 | 88 | 87
2019-03-05 08:00 | 71 | 65 |  |  | 43529.3333 | 88 | 88
2019-03-05 08:30 | 69 | 64 |  |  | 43529.3542 | 89 | 89
2019-03-05 09:00 | 69 | 65 |  |  | 43529.375 | 90 | 89
2019-03-05 09:30 | 69 | 64 |  |  | 43529.3958 | 88 | 88
2019-03-05 10:00 | 68 | 64 |  |  | 43529.4167 | 89 | 88
2019-03-05 10:30 | 70 | 65 |  |  | 43529.4375 | 87 | 87
2019-03-05 11:00 | 70 | 65 |  |  | 43529.4583 | 89 | 88
2019-03-05 11:30 | 71 | 67 |  |  | 43529.4792 | 91 | 91
2019-03-05 12:00 | 74 | 71 |  |  | 43529.5 | 91 | 91
2019-03-05 12:30 | 72 | 69 |  |  | 43529.5208 | 90 | 90
2019-03-05 13:00 | 69 | 66 |  |  | 43529.5417 | 91 | 91
2019-03-05 13:30 | 71 | 68 |  |  | 43529.5625 | 93 | 93
2019-03-05 14:00 | 75 | 72 |  |  | 43529.5833 | 96 | 96
2019-03-05 14:30 | 76 | 73 |  |  | 43529.6042 | 96 | 95
2019-03-05 15:00 | 77 | 73 |  |  | 43529.625 | 96 | 94
2019-03-05 15:30 | 78 | 72 |  |  | 43529.6458 | 94 | 92
2019-03-05 16:00 | 82 | 76 |  |  | 43529.6667 | 97 | 94
2019-03-05 16:30 | 86 | 81 |  |  | 43529.6875 | 102 | 98
2019-03-05 17:00 | 88 | 83 |  |  | 43529.7083 | 102 | 98
2019-03-05 17:30 | 87 | 81 |  |  | 43529.7292 | 99 | 95
2019-03-05 18:00 | 86 | 80 |  |  | 43529.75 | 96 | 92
2019-03-05 18:30 | 89 | 82 |  |  | 43529.7708 | 98 | 94
2019-03-05 19:00 | 91 | 86 |  |  | 43529.7917 | 102 | 99
2019-03-05 19:30 | 92 | 86 |  |  | 43529.8125 | 102 | 98
2019-03-05 20:00 | 89 | 83 |  |  | 43529.8333 | 100 | 96
2019-03-05 20:30 | 90 | 83 |  |  | 43529.8542 | 100 | 96
2019-03-05 21:00 | 86 | 80 |  |  | 43529.875 | 97 | 92
2019-03-05 21:30 | 80 | 74 |  |  | 43529.8958 | 90 | 85
2019-03-05 22:00 | 79 | 73 |  |  | 43529.9167 | 91 | 86
2019-03-05 22:30 | 80 | 72 |  |  | 43529.9375 | 91 | 85
2019-03-05 23:00 | 76 | 67 |  |  | 43529.9583 | 85 | 78
2019-03-05 23:30 | 68 | 60 |  |  | 43529.9792 | 75 | 72
2019-03-06 | 65 | 54 |  |  | 43530 | 70 | 66
2019-03-06 00:30 | 64 | 51 |  |  | 43530.0208 | 67 | 62
2019-03-06 01:00 | 64 | 51 |  |  | 43530.0417 | 66 | 60
2019-03-06 01:30 | 63 | 49 |  |  | 43530.0625 | 65 | 58
2019-03-06 02:00 | 63 | 49 |  |  | 43530.0833 | 64 | 58
2019-03-06 02:30 | 61 | 47 |  |  | 43530.1042 | 62 | 56
2019-03-06 03:00 | 62 | 47 |  |  | 43530.125 | 63 | 56
2019-03-06 03:30 | 63 | 49 |  |  | 43530.1458 | 65 | 59
2019-03-06 04:00 | 62 | 48 |  |  | 43530.1667 | 64 | 58
2019-03-06 04:30 | 64 | 50 |  |  | 43530.1875 | 66 | 60
2019-03-06 05:00 | 66 | 53 |  |  | 43530.2083 | 69 | 63
2019-03-06 05:30 | 67 | 56 |  |  | 43530.2292 | 72 | 68
2019-03-06 06:00 | 66 | 56 |  |  | 43530.25 | 73 | 69
2019-03-06 06:30 | 67 | 59 |  |  | 43530.2708 | 78 | 76
2019-03-06 07:00 | 71 | 64 |  |  | 43530.2917 | 86 | 84
2019-03-06 07:30 | 75 | 71 |  |  | 43530.3125 | 94 | 94
2019-03-06 08:00 | 79 | 75 |  |  | 43530.3333 | 103 | 102
2019-03-06 08:30 | 82 | 77 |  |  | 43530.3542 | 110 | 108
2019-03-06 09:00 | 83 | 78 |  |  | 43530.375 | 109 | 107
2019-03-06 09:30 | 84 | 80 |  |  | 43530.3958 | 109 | 108
2019-03-06 10:00 | 83 | 78 |  |  | 43530.4167 | 109 | 108
2019-03-06 10:30 | 83 | 78 |  |  | 43530.4375 | 110 | 109
2019-03-06 11:00 | 85 | 81 |  |  | 43530.4583 | 113 | 112
2019-03-06 11:30 | 85 | 82 |  |  | 43530.4792 | 111 | 110
2019-03-06 12:00 | 83 | 79 |  |  | 43530.5 | 107 | 106
2019-03-06 12:30 | 78 | 77 |  |  | 43530.5208 | 105 | 105
2019-03-06 13:00 | 80 | 80 |  |  | 43530.5417 | 108 | 108
2019-03-06 13:30 | 82 | 82 |  |  | 43530.5625 | 109 | 109
2019-03-06 14:00 | 88 | 86 |  |  | 43530.5833 | 115 | 113
2019-03-06 14:30 | 91 | 90 |  |  | 43530.6042 | 117 | 116
2019-03-06 15:00 | 93 | 92 |  |  | 43530.625 | 123 | 120
2019-03-06 15:30 | 94 | 93 |  |  | 43530.6458 | 120 | 118
2019-03-06 16:00 | 99 | 98 |  |  | 43530.6667 | 125 | 122
2019-03-06 16:30 | 101 | 100 |  |  | 43530.6875 | 124 | 121
2019-03-06 17:00 | 99 | 98 |  |  | 43530.7083 | 118 | 115
2019-03-06 17:30 | 98 | 97 |  |  | 43530.7292 | 115 | 112
2019-03-06 18:00 | 94 | 93 |  |  | 43530.75 | 111 | 108
2019-03-06 18:30 | 90 | 90 |  |  | 43530.7708 | 106 | 104
2019-03-06 19:00 | 92 | 92 |  |  | 43530.7917 | 108 | 107
2019-03-06 19:30 | 91 | 91 |  |  | 43530.8125 | 106 | 106
2019-03-06 20:00 | 91 | 90 |  |  | 43530.8333 | 105 | 104
2019-03-06 20:30 | 89 | 89 |  |  | 43530.8542 | 103 | 103
2019-03-06 21:00 | 86 | 86 |  |  | 43530.875 | 100 | 100
2019-03-06 21:30 | 83 | 83 |  |  | 43530.8958 | 97 | 97
2019-03-06 22:00 | 81 | 81 |  |  | 43530.9167 | 96 | 96
2019-03-06 22:30 | 77 | 77 |  |  | 43530.9375 | 91 | 91
2019-03-06 23:00 | 70 | 70 |  |  | 43530.9583 | 83 | 83
2019-03-06 23:30 | 63 | 63 |  |  | 43530.9792 | 76 | 76
2019-03-07 | 57 | 57 |  |  | 43531 | 71 | 71
2019-03-07 00:30 | 55 | 54 |  |  | 43531.0208 | 67 | 67
2019-03-07 01:00 | 55 | 54 |  |  | 43531.0417 | 66 | 66
2019-03-07 01:30 | 55 | 54 |  |  | 43531.0625 | 65 | 65
2019-03-07 02:00 | 55 | 53 |  |  | 43531.0833 | 65 | 65
2019-03-07 02:30 | 53 | 51 |  |  | 43531.1042 | 63 | 62
2019-03-07 03:00 | 51 | 49 |  |  | 43531.125 | 61 | 60
2019-03-07 03:30 | 51 | 48 |  |  | 43531.1458 | 60 | 60
2019-03-07 04:00 | 50 | 48 |  |  | 43531.1667 | 60 | 59
2019-03-07 04:30 | 49 | 47 |  |  | 43531.1875 | 59 | 59
2019-03-07 05:00 | 51 | 49 |  |  | 43531.2083 | 60 | 60
2019-03-07 05:30 | 51 | 50 |  |  | 43531.2292 | 62 | 62
2019-03-07 06:00 | 52 | 51 |  |  | 43531.25 | 66 | 66
2019-03-07 06:30 | 60 | 59 |  |  | 43531.2708 | 77 | 77
2019-03-07 07:00 | 67 | 67 |  |  | 43531.2917 | 90 | 89
2019-03-07 07:30 | 74 | 74 |  |  | 43531.3125 | 101 | 101
2019-03-07 08:00 | 73 | 73 |  |  | 43531.3333 | 106 | 106
2019-03-07 08:30 | 68 | 67 |  |  | 43531.3542 | 103 | 103
2019-03-07 09:00 | 69 | 68 |  |  | 43531.375 | 104 | 104
2019-03-07 09:30 | 69 | 67 |  |  | 43531.3958 | 102 | 102
2019-03-07 10:00 | 67 | 66 |  |  | 43531.4167 | 100 | 100
2019-03-07 10:30 | 69 | 67 |  |  | 43531.4375 | 103 | 103
2019-03-07 11:00 | 71 | 70 |  |  | 43531.4583 | 103 | 103
2019-03-07 11:30 | 74 | 73 |  |  | 43531.4792 | 105 | 105
2019-03-07 12:00 | 75 | 74 |  |  | 43531.5 | 105 | 105
2019-03-07 12:30 | 72 | 71 |  |  | 43531.5208 | 101 | 101
2019-03-07 13:00 | 73 | 72 |  |  | 43531.5417 | 103 | 103
2019-03-07 13:30 | 78 | 77 |  |  | 43531.5625 | 106 | 106
2019-03-07 14:00 | 79 | 77 |  |  | 43531.5833 | 109 | 108
2019-03-07 14:30 | 77 | 76 |  |  | 43531.6042 | 116 | 115
2019-03-07 15:00 | 80 | 79 |  |  | 43531.625 | 115 | 115
2019-03-07 15:30 | 83 | 82 |  |  | 43531.6458 | 112 | 112
2019-03-07 16:00 | 99 | 99 |  |  | 43531.6667 | 122 | 121
2019-03-07 16:30 | 103 | 103 |  |  | 43531.6875 | 127 | 126
2019-03-07 17:00 | 105 | 105 |  |  | 43531.7083 | 130 | 128
2019-03-07 17:30 | 103 | 102 |  |  | 43531.7292 | 124 | 122
2019-03-07 18:00 | 101 | 99 |  |  | 43531.75 | 121 | 117
2019-03-07 18:30 | 100 | 99 |  |  | 43531.7708 | 120 | 117
2019-03-07 19:00 | 101 | 100 |  |  | 43531.7917 | 120 | 118
2019-03-07 19:30 | 102 | 101 |  |  | 43531.8125 | 120 | 118
2019-03-07 20:00 | 101 | 99 |  |  | 43531.8333 | 120 | 117
2019-03-07 20:30 | 102 | 99 |  |  | 43531.8542 | 120 | 117
2019-03-07 21:00 | 99 | 97 |  |  | 43531.875 | 116 | 114
2019-03-07 21:30 | 93 | 91 |  |  | 43531.8958 | 110 | 107
2019-03-07 22:00 | 89 | 87 |  |  | 43531.9167 | 106 | 104
2019-03-07 22:30 | 83 | 81 |  |  | 43531.9375 | 99 | 98
2019-03-07 23:00 | 75 | 72 |  |  | 43531.9583 | 90 | 88
2019-03-07 23:30 | 69 | 67 |  |  | 43531.9792 | 84 | 83
2019-03-08 | 64 | 61 |  |  | 43532 | 79 | 78
2019-03-08 00:30 | 61 | 58 |  |  | 43532.0208 | 74 | 73
2019-03-08 01:00 | 57 | 53 |  |  | 43532.0417 | 69 | 67
2019-03-08 01:30 | 56 | 52 |  |  | 43532.0625 | 67 | 66
2019-03-08 02:00 | 55 | 50 |  |  | 43532.0833 | 66 | 65
2019-03-08 02:30 | 53 | 48 |  |  | 43532.1042 | 65 | 63
2019-03-08 03:00 | 55 | 50 |  |  | 43532.125 | 66 | 64
2019-03-08 03:30 | 55 | 50 |  |  | 43532.1458 | 65 | 63
2019-03-08 04:00 | 55 | 51 |  |  | 43532.1667 | 66 | 64
2019-03-08 04:30 | 56 | 52 |  |  | 43532.1875 | 66 | 64
2019-03-08 05:00 | 58 | 54 |  |  | 43532.2083 | 70 | 68
2019-03-08 05:30 | 60 | 57 |  |  | 43532.2292 | 72 | 71
2019-03-08 06:00 | 61 | 59 |  |  | 43532.25 | 75 | 74
2019-03-08 06:30 | 67 | 65 |  |  | 43532.2708 | 84 | 83
2019-03-08 07:00 | 69 | 67 |  |  | 43532.2917 | 90 | 89
2019-03-08 07:30 | 76 | 73 |  |  | 43532.3125 | 100 | 98
2019-03-08 08:00 | 81 | 80 |  |  | 43532.3333 | 108 | 107
2019-03-08 08:30 | 83 | 82 |  |  | 43532.3542 | 112 | 111
2019-03-08 09:00 | 82 | 81 |  |  | 43532.375 | 110 | 109
2019-03-08 09:30 | 82 | 81 |  |  | 43532.3958 | 108 | 108
2019-03-08 10:00 | 79 | 78 |  |  | 43532.4167 | 107 | 107
2019-03-08 10:30 | 81 | 80 |  |  | 43532.4375 | 107 | 107
2019-03-08 11:00 | 81 | 81 |  |  | 43532.4583 | 107 | 106
2019-03-08 11:30 | 78 | 77 |  |  | 43532.4792 | 103 | 102
2019-03-08 12:00 | 80 | 79 |  |  | 43532.5 | 105 | 105
2019-03-08 12:30 | 78 | 77 |  |  | 43532.5208 | 103 | 102
2019-03-08 13:00 | 80 | 78 |  |  | 43532.5417 | 109 | 108
2019-03-08 13:30 | 83 | 82 |  |  | 43532.5625 | 109 | 109
2019-03-08 14:00 | 85 | 84 |  |  | 43532.5833 | 108 | 107
2019-03-08 14:30 | 81 | 80 |  |  | 43532.6042 | 106 | 105
2019-03-08 15:00 | 84 | 82 |  |  | 43532.625 | 106 | 105
2019-03-08 15:30 | 82 | 80 |  |  | 43532.6458 | 103 | 102
2019-03-08 16:00 | 84 | 82 |  |  | 43532.6667 | 103 | 102
2019-03-08 16:30 | 85 | 83 |  |  | 43532.6875 | 104 | 102
2019-03-08 17:00 | 86 | 85 |  |  | 43532.7083 | 105 | 103
2019-03-08 17:30 | 87 | 85 |  |  | 43532.7292 | 104 | 102
2019-03-08 18:00 | 86 | 84 |  |  | 43532.75 | 104 | 100
2019-03-08 18:30 | 83 | 82 |  |  | 43532.7708 | 105 | 97
2019-03-08 19:00 | 84 | 83 |  |  | 43532.7917 | 105 | 98
2019-03-08 19:30 | 83 | 82 |  |  | 43532.8125 | 103 | 96
2019-03-08 20:00 | 81 | 80 |  |  | 43532.8333 | 101 | 93
2019-03-08 20:30 | 78 | 77 |  |  | 43532.8542 | 96 | 90
2019-03-08 21:00 | 75 | 74 |  |  | 43532.875 | 90 | 87
2019-03-08 21:30 | 73 | 72 |  |  | 43532.8958 | 89 | 85
2019-03-08 22:00 | 72 | 72 |  |  | 43532.9167 | 90 | 85
2019-03-08 22:30 | 68 | 67 |  |  | 43532.9375 | 86 | 81
2019-03-08 23:00 | 63 | 63 |  |  | 43532.9583 | 81 | 76
2019-03-08 23:30 | 59 | 58 |  |  | 43532.9792 | 77 | 71
2019-03-09 | 56 | 56 |  |  | 43533 | 73 | 68
2019-03-09 00:30 | 50 | 49 |  |  | 43533.0208 | 67 | 61
2019-03-09 01:00 | 47 | 46 |  |  | 43533.0417 | 62 | 56
2019-03-09 01:30 | 46 | 45 |  |  | 43533.0625 | 61 | 55
2019-03-09 02:00 | 44 | 43 |  |  | 43533.0833 | 60 | 53
2019-03-09 02:30 | 42 | 41 |  |  | 43533.1042 | 58 | 52
2019-03-09 03:00 | 42 | 41 |  |  | 43533.125 | 58 | 51
2019-03-09 03:30 | 41 | 40 |  |  | 43533.1458 | 57 | 51
2019-03-09 04:00 | 41 | 40 |  |  | 43533.1667 | 57 | 51
2019-03-09 04:30 | 42 | 41 |  |  | 43533.1875 | 58 | 51
2019-03-09 05:00 | 42 | 41 |  |  | 43533.2083 | 58 | 52
2019-03-09 05:30 | 42 | 40 |  |  | 43533.2292 | 59 | 53
2019-03-09 06:00 | 42 | 40 |  |  | 43533.25 | 60 | 53
2019-03-09 06:30 | 41 | 40 |  |  | 43533.2708 | 61 | 55
2019-03-09 07:00 | 42 | 41 |  |  | 43533.2917 | 62 | 57
2019-03-09 07:30 | 42 | 41 |  |  | 43533.3125 | 63 | 59
2019-03-09 08:00 | 39 | 38 |  |  | 43533.3333 | 63 | 60
2019-03-09 08:30 | 40 | 39 |  |  | 43533.3542 | 65 | 63
2019-03-09 09:00 | 42 | 42 |  |  | 43533.375 | 69 | 67
2019-03-09 09:30 | 43 | 43 |  |  | 43533.3958 | 69 | 67
2019-03-09 10:00 | 44 | 44 |  |  | 43533.4167 | 70 | 69
2019-03-09 10:30 | 48 | 48 |  |  | 43533.4375 | 73 | 72
2019-03-09 11:00 | 50 | 50 |  |  | 43533.4583 | 74 | 73
2019-03-09 11:30 | 54 | 53 |  |  | 43533.4792 | 75 | 74
2019-03-09 12:00 | 50 | 50 |  |  | 43533.5 | 73 | 72
2019-03-09 12:30 | 52 | 52 |  |  | 43533.5208 | 70 | 69
2019-03-09 13:00 | 56 | 56 |  |  | 43533.5417 | 70 | 68
2019-03-09 13:30 | 59 | 59 |  |  | 43533.5625 | 73 | 72
2019-03-09 14:00 | 61 | 60 |  |  | 43533.5833 | 75 | 73
2019-03-09 14:30 | 62 | 62 |  |  | 43533.6042 | 77 | 75
2019-03-09 15:00 | 63 | 63 |  |  | 43533.625 | 77 | 76
2019-03-09 15:30 | 65 | 65 |  |  | 43533.6458 | 80 | 78
2019-03-09 16:00 | 69 | 69 |  |  | 43533.6667 | 83 | 82
2019-03-09 16:30 | 74 | 73 |  |  | 43533.6875 | 88 | 85
2019-03-09 17:00 | 77 | 77 |  |  | 43533.7083 | 92 | 88
2019-03-09 17:30 | 79 | 78 |  |  | 43533.7292 | 94 | 90
2019-03-09 18:00 | 79 | 78 |  |  | 43533.75 | 95 | 90
2019-03-09 18:30 | 78 | 77 |  |  | 43533.7708 | 96 | 90
2019-03-09 19:00 | 77 | 76 |  |  | 43533.7917 | 96 | 91
2019-03-09 19:30 | 79 | 78 |  |  | 43533.8125 | 98 | 92
2019-03-09 20:00 | 78 | 77 |  |  | 43533.8333 | 97 | 91
2019-03-09 20:30 | 79 | 78 |  |  | 43533.8542 | 98 | 93
2019-03-09 21:00 | 78 | 77 |  |  | 43533.875 | 94 | 91
2019-03-09 21:30 | 73 | 72 |  |  | 43533.8958 | 89 | 86
2019-03-09 22:00 | 69 | 69 |  |  | 43533.9167 | 86 | 83
2019-03-09 22:30 | 68 | 67 |  |  | 43533.9375 | 85 | 81
2019-03-09 23:00 | 64 | 64 |  |  | 43533.9583 | 79 | 75
2019-03-09 23:30 | 61 | 60 |  |  | 43533.9792 | 76 | 72
2019-03-10 | 57 | 56 |  |  | 43534 | 71 | 67
2019-03-10 00:30 | 53 | 52 |  |  | 43534.0208 | 67 | 62
2019-03-10 01:00 | 49 | 48 |  |  | 43534.0417 | 64 | 59
2019-03-10 01:30 | 48 | 47 |  |  | 43534.0625 | 63 | 57
2019-03-10 02:00 | 47 | 46 |  |  | 43534.0833 | 62 | 55
2019-03-10 02:30 | 46 | 45 |  |  | 43534.1042 | 61 | 55
2019-03-10 03:00 | 46 | 44 |  |  | 43534.125 | 61 | 54
2019-03-10 03:30 | 45 | 43 |  |  | 43534.1458 | 61 | 54
2019-03-10 04:00 | 45 | 44 |  |  | 43534.1667 | 60 | 54
2019-03-10 04:30 | 45 | 44 |  |  | 43534.1875 | 61 | 54
2019-03-10 05:00 | 45 | 43 |  |  | 43534.2083 | 60 | 53
2019-03-10 05:30 | 45 | 44 |  |  | 43534.2292 | 61 | 54
2019-03-10 06:00 | 45 | 43 |  |  | 43534.25 | 61 | 55
2019-03-10 06:30 | 44 | 43 |  |  | 43534.2708 | 61 | 55
2019-03-10 07:00 | 44 | 43 |  |  | 43534.2917 | 62 | 56
2019-03-10 07:30 | 43 | 42 |  |  | 43534.3125 | 60 | 55
2019-03-10 08:00 | 40 | 39 |  |  | 43534.3333 | 57 | 54
2019-03-10 08:30 | 41 | 41 |  |  | 43534.3542 | 58 | 55
2019-03-10 09:00 | 46 | 46 |  |  | 43534.375 | 61 | 59
2019-03-10 09:30 | 47 | 47 |  |  | 43534.3958 | 63 | 61
2019-03-10 10:00 | 48 | 48 |  |  | 43534.4167 | 62 | 61
2019-03-10 10:30 | 51 | 51 |  |  | 43534.4375 | 65 | 63
2019-03-10 11:00 | 52 | 52 |  |  | 43534.4583 | 66 | 64
2019-03-10 11:30 | 54 | 54 |  |  | 43534.4792 | 68 | 66
2019-03-10 12:00 | 54 | 54 |  |  | 43534.5 | 67 | 66
2019-03-10 12:30 | 55 | 55 |  |  | 43534.5208 | 67 | 65
2019-03-10 13:00 | 61 | 61 |  |  | 43534.5417 | 72 | 70
2019-03-10 13:30 | 64 | 64 |  |  | 43534.5625 | 74 | 73
2019-03-10 14:00 | 68 | 67 |  |  | 43534.5833 | 77 | 76
2019-03-10 14:30 | 70 | 70 |  |  | 43534.6042 | 79 | 78
2019-03-10 15:00 | 69 | 69 |  |  | 43534.625 | 78 | 77
2019-03-10 15:30 | 70 | 70 |  |  | 43534.6458 | 79 | 77
2019-03-10 16:00 | 74 | 74 |  |  | 43534.6667 | 84 | 83
2019-03-10 16:30 | 76 | 76 |  |  | 43534.6875 | 87 | 83
2019-03-10 17:00 | 78 | 78 |  |  | 43534.7083 | 90 | 87
2019-03-10 17:30 | 77 | 77 |  |  | 43534.7292 | 91 | 87
2019-03-10 18:00 | 79 | 79 |  |  | 43534.75 | 94 | 89
2019-03-10 18:30 | 80 | 80 |  |  | 43534.7708 | 98 | 93
2019-03-10 19:00 | 82 | 82 |  |  | 43534.7917 | 100 | 96
2019-03-10 19:30 | 81 | 81 |  |  | 43534.8125 | 99 | 95
2019-03-10 20:00 | 80 | 80 |  |  | 43534.8333 | 98 | 94
2019-03-10 20:30 | 79 | 78 |  |  | 43534.8542 | 97 | 93
2019-03-10 21:00 | 75 | 75 |  |  | 43534.875 | 91 | 89
2019-03-10 21:30 | 70 | 70 |  |  | 43534.8958 | 86 | 84
2019-03-10 22:00 | 66 | 66 |  |  | 43534.9167 | 83 | 81
2019-03-10 22:30 | 64 | 64 |  |  | 43534.9375 | 81 | 79
2019-03-10 23:00 | 62 | 62 |  |  | 43534.9583 | 77 | 74
2019-03-10 23:30 | 57 | 57 |  |  | 43534.9792 | 73 | 70
2019-03-11 | 53 | 52 |  |  | 43535 | 68 | 65
2019-03-11 00:30 | 51 | 51 |  |  | 43535.0208 | 66 | 62
2019-03-11 01:00 | 50 | 49 |  |  | 43535.0417 | 64 | 60
2019-03-11 01:30 | 49 | 48 |  |  | 43535.0625 | 62 | 58
2019-03-11 02:00 | 49 | 48 |  |  | 43535.0833 | 62 | 57
2019-03-11 02:30 | 48 | 47 |  |  | 43535.1042 | 62 | 57
2019-03-11 03:00 | 46 | 45 |  |  | 43535.125 | 60 | 54
2019-03-11 03:30 | 45 | 44 |  |  | 43535.1458 | 59 | 54
2019-03-11 04:00 | 45 | 44 |  |  | 43535.1667 | 59 | 53
2019-03-11 04:30 | 43 | 42 |  |  | 43535.1875 | 57 | 52
2019-03-11 05:00 | 45 | 44 |  |  | 43535.2083 | 58 | 53
2019-03-11 05:30 | 48 | 47 |  |  | 43535.2292 | 61 | 57
2019-03-11 06:00 | 52 | 52 |  |  | 43535.25 | 65 | 63
2019-03-11 06:30 | 58 | 58 |  |  | 43535.2708 | 76 | 74
2019-03-11 07:00 | 63 | 63 |  |  | 43535.2917 | 83 | 82
2019-03-11 07:30 | 68 | 68 |  |  | 43535.3125 | 92 | 91
2019-03-11 08:00 | 72 | 72 |  |  | 43535.3333 | 97 | 96
2019-03-11 08:30 | 73 | 73 |  |  | 43535.3542 | 98 | 98
2019-03-11 09:00 | 73 | 73 |  |  | 43535.375 | 100 | 100
2019-03-11 09:30 | 76 | 76 |  |  | 43535.3958 | 103 | 102
2019-03-11 10:00 | 75 | 75 |  |  | 43535.4167 | 102 | 101
2019-03-11 10:30 | 76 | 76 |  |  | 43535.4375 | 102 | 100
2019-03-11 11:00 | 82 | 81 |  |  | 43535.4583 | 104 | 103
2019-03-11 11:30 | 82 | 82 |  |  | 43535.4792 | 109 | 108
2019-03-11 12:00 | 85 | 85 |  |  | 43535.5 | 110 | 109
2019-03-11 12:30 | 89 | 88 |  |  | 43535.5208 | 114 | 113
2019-03-11 13:00 | 92 | 92 |  |  | 43535.5417 | 116 | 113
2019-03-11 13:30 | 98 | 98 |  |  | 43535.5625 | 120 | 114
2019-03-11 14:00 | 101 | 101 |  |  | 43535.5833 | 135 | 128
2019-03-11 14:30 | 95 | 95 |  |  | 43535.6042 | 134 | 125
2019-03-11 15:00 | 90 | 90 |  |  | 43535.625 | 130 | 117
2019-03-11 15:30 | 90 | 89 |  |  | 43535.6458 | 128 | 115
2019-03-11 16:00 | 83 | 83 |  |  | 43535.6667 | 121 | 109
2019-03-11 16:30 | 88 | 87 |  |  | 43535.6875 | 122 | 113
2019-03-11 17:00 | 89 | 89 |  |  | 43535.7083 | 124 | 115
2019-03-11 17:30 | 87 | 86 |  |  | 43535.7292 | 123 | 110
2019-03-11 18:00 | 84 | 84 |  |  | 43535.75 | 117 | 106
2019-03-11 18:30 | 84 | 84 |  |  | 43535.7708 | 113 | 104
2019-03-11 19:00 | 86 | 86 |  |  | 43535.7917 | 114 | 105
2019-03-11 19:30 | 85 | 85 |  |  | 43535.8125 | 110 | 104
2019-03-11 20:00 | 82 | 82 |  |  | 43535.8333 | 106 | 101
2019-03-11 20:30 | 81 | 81 |  |  | 43535.8542 | 105 | 100
2019-03-11 21:00 | 83 | 83 |  |  | 43535.875 | 103 | 97
2019-03-11 21:30 | 82 | 82 |  |  | 43535.8958 | 101 | 96
2019-03-11 22:00 | 80 | 80 |  |  | 43535.9167 | 95 | 93
2019-03-11 22:30 | 73 | 73 |  |  | 43535.9375 | 86 | 86
2019-03-11 23:00 | 65 | 65 |  |  | 43535.9583 | 78 | 77
2019-03-11 23:30 | 60 | 59 |  |  | 43535.9792 | 73 | 73
2019-03-12 | 54 | 53 |  |  | 43536 | 67 | 66
2019-03-12 00:30 | 51 | 51 |  |  | 43536.0208 | 63 | 62
2019-03-12 01:00 | 52 | 52 |  |  | 43536.0417 | 63 | 62
2019-03-12 01:30 | 51 | 51 |  |  | 43536.0625 | 63 | 61
2019-03-12 02:00 | 52 | 52 |  |  | 43536.0833 | 63 | 61
2019-03-12 02:30 | 52 | 51 |  |  | 43536.1042 | 62 | 60
2019-03-12 03:00 | 51 | 51 |  |  | 43536.125 | 61 | 59
2019-03-12 03:30 | 52 | 52 |  |  | 43536.1458 | 61 | 59
2019-03-12 04:00 | 48 | 48 |  |  | 43536.1667 | 58 | 56
2019-03-12 04:30 | 48 | 48 |  |  | 43536.1875 | 58 | 56
2019-03-12 05:00 | 52 | 52 |  |  | 43536.2083 | 63 | 61
2019-03-12 05:30 | 54 | 54 |  |  | 43536.2292 | 66 | 65
2019-03-12 06:00 | 54 | 54 |  |  | 43536.25 | 67 | 67
2019-03-12 06:30 | 59 | 59 |  |  | 43536.2708 | 75 | 75
2019-03-12 07:00 | 65 | 65 |  |  | 43536.2917 | 83 | 83
2019-03-12 07:30 | 75 | 75 |  |  | 43536.3125 | 100 | 96
2019-03-12 08:00 | 76 | 76 |  |  | 43536.3333 | 106 | 99
2019-03-12 08:30 | 76 | 76 |  |  | 43536.3542 | 109 | 103
2019-03-12 09:00 | 78 | 78 |  |  | 43536.375 | 110 | 106
2019-03-12 09:30 | 81 | 81 |  |  | 43536.3958 | 115 | 112
2019-03-12 10:00 | 80 | 79 |  |  | 43536.4167 | 114 | 111
2019-03-12 10:30 | 82 | 82 |  |  | 43536.4375 | 117 | 113
2019-03-12 11:00 | 87 | 87 |  |  | 43536.4583 | 126 | 118
2019-03-12 11:30 | 89 | 88 |  |  | 43536.4792 | 131 | 118
2019-03-12 12:00 | 92 | 91 |  |  | 43536.5 | 134 | 122
2019-03-12 12:30 | 96 | 96 |  |  | 43536.5208 | 135 | 126
2019-03-12 13:00 | 95 | 95 |  |  | 43536.5417 | 130 | 121
2019-03-12 13:30 | 99 | 99 |  |  | 43536.5625 | 133 | 124
2019-03-12 14:00 | 98 | 98 |  |  | 43536.5833 | 132 | 122
2019-03-12 14:30 | 98 | 97 |  |  | 43536.6042 | 132 | 122
2019-03-12 15:00 | 99 | 99 |  |  | 43536.625 | 132 | 121
2019-03-12 15:30 | 107 | 107 |  |  | 43536.6458 | 137 | 127
2019-03-12 16:00 | 99 | 99 |  |  | 43536.6667 | 134 | 123
2019-03-12 16:30 | 97 | 96 |  |  | 43536.6875 | 133 | 121
2019-03-12 17:00 | 100 | 100 |  |  | 43536.7083 | 135 | 124
2019-03-12 17:30 | 100 | 100 |  |  | 43536.7292 | 136 | 123
2019-03-12 18:00 | 101 | 101 |  |  | 43536.75 | 138 | 124
2019-03-12 18:30 | 100 | 100 |  |  | 43536.7708 | 131 | 122
2019-03-12 19:00 | 102 | 102 |  |  | 43536.7917 | 130 | 123
2019-03-12 19:30 | 101 | 101 |  |  | 43536.8125 | 128 | 120
2019-03-12 20:00 | 95 | 95 |  |  | 43536.8333 | 122 | 113
2019-03-12 20:30 | 96 | 96 |  |  | 43536.8542 | 122 | 114
2019-03-12 21:00 | 95 | 95 |  |  | 43536.875 | 121 | 115
2019-03-12 21:30 | 87 | 87 |  |  | 43536.8958 | 110 | 105
2019-03-12 22:00 | 81 | 80 |  |  | 43536.9167 | 98 | 97
2019-03-12 22:30 | 78 | 77 |  |  | 43536.9375 | 93 | 92
2019-03-12 23:00 | 77 | 76 |  |  | 43536.9583 | 88 | 88
2019-03-12 23:30 | 69 | 69 |  |  | 43536.9792 | 81 | 80
2019-03-13 | 65 | 65 |  |  | 43537 | 78 | 77
2019-03-13 00:30 | 59 | 59 |  |  | 43537.0208 | 71 | 70
2019-03-13 01:00 | 56 | 56 |  |  | 43537.0417 | 68 | 66
2019-03-13 01:30 | 53 | 53 |  |  | 43537.0625 | 65 | 63
2019-03-13 02:00 | 52 | 51 |  |  | 43537.0833 | 63 | 60
2019-03-13 02:30 | 48 | 47 |  |  | 43537.1042 | 60 | 56
2019-03-13 03:00 | 46 | 45 |  |  | 43537.125 | 58 | 54
2019-03-13 03:30 | 44 | 44 |  |  | 43537.1458 | 57 | 54
2019-03-13 04:00 | 44 | 44 |  |  | 43537.1667 | 56 | 53
2019-03-13 04:30 | 45 | 44 |  |  | 43537.1875 | 57 | 53
2019-03-13 05:00 | 48 | 47 |  |  | 43537.2083 | 61 | 57
2019-03-13 05:30 | 48 | 48 |  |  | 43537.2292 | 61 | 58
2019-03-13 06:00 | 51 | 50 |  |  | 43537.25 | 65 | 61
2019-03-13 06:30 | 58 | 57 |  |  | 43537.2708 | 76 | 73
2019-03-13 07:00 | 62 | 62 |  |  | 43537.2917 | 86 | 80
2019-03-13 07:30 | 72 | 71 |  |  | 43537.3125 | 96 | 93
2019-03-13 08:00 | 78 | 77 |  |  | 43537.3333 | 103 | 100
2019-03-13 08:30 | 75 | 74 |  |  | 43537.3542 | 103 | 97
2019-03-13 09:00 | 75 | 74 |  |  | 43537.375 | 105 | 98
2019-03-13 09:30 | 76 | 75 |  |  | 43537.3958 | 105 | 99
2019-03-13 10:00 | 77 | 76 |  |  | 43537.4167 | 105 | 98
2019-03-13 10:30 | 77 | 76 |  |  | 43537.4375 | 104 | 97
2019-03-13 11:00 | 79 | 78 |  |  | 43537.4583 | 106 | 100
2019-03-13 11:30 | 80 | 80 |  |  | 43537.4792 | 109 | 102
2019-03-13 12:00 | 83 | 83 |  |  | 43537.5 | 110 | 105
2019-03-13 12:30 | 88 | 88 |  |  | 43537.5208 | 112 | 108
2019-03-13 13:00 | 91 | 91 |  |  | 43537.5417 | 114 | 110
2019-03-13 13:30 | 92 | 92 |  |  | 43537.5625 | 117 | 113
2019-03-13 14:00 | 94 | 94 |  |  | 43537.5833 | 120 | 116
2019-03-13 14:30 | 95 | 95 |  |  | 43537.6042 | 121 | 117
2019-03-13 15:00 | 96 | 96 |  |  | 43537.625 | 121 | 117
2019-03-13 15:30 | 97 | 97 |  |  | 43537.6458 | 121 | 117
2019-03-13 16:00 | 98 | 98 |  |  | 43537.6667 | 122 | 117
2019-03-13 16:30 | 92 | 92 |  |  | 43537.6875 | 120 | 115
2019-03-13 17:00 | 92 | 92 |  |  | 43537.7083 | 121 | 115
2019-03-13 17:30 | 91 | 91 |  |  | 43537.7292 | 119 | 112
2019-03-13 18:00 | 90 | 90 |  |  | 43537.75 | 116 | 109
2019-03-13 18:30 | 88 | 88 |  |  | 43537.7708 | 115 | 107
2019-03-13 19:00 | 89 | 89 |  |  | 43537.7917 | 116 | 108
2019-03-13 19:30 | 90 | 90 |  |  | 43537.8125 | 116 | 109
2019-03-13 20:00 | 89 | 89 |  |  | 43537.8333 | 114 | 108
2019-03-13 20:30 | 87 | 87 |  |  | 43537.8542 | 111 | 104
2019-03-13 21:00 | 88 | 88 |  |  | 43537.875 | 108 | 103
2019-03-13 21:30 | 88 | 88 |  |  | 43537.8958 | 106 | 100
2019-03-13 22:00 | 84 | 84 |  |  | 43537.9167 | 103 | 96
2019-03-13 22:30 | 80 | 80 |  |  | 43537.9375 | 101 | 93
2019-03-13 23:00 | 72 | 72 |  |  | 43537.9583 | 92 | 83
2019-03-13 23:30 | 69 | 68 |  |  | 43537.9792 | 88 | 79
2019-03-14 | 66 | 66 |  |  | 43538 | 82 | 78
2019-03-14 00:30 | 62 | 62 |  |  | 43538.0208 | 77 | 72
2019-03-14 01:00 | 60 | 59 |  |  | 43538.0417 | 73 | 69
2019-03-14 01:30 | 58 | 58 |  |  | 43538.0625 | 71 | 67
2019-03-14 02:00 | 53 | 53 |  |  | 43538.0833 | 67 | 61
2019-03-14 02:30 | 52 | 51 |  |  | 43538.1042 | 65 | 59
2019-03-14 03:00 | 51 | 50 |  |  | 43538.125 | 64 | 58
2019-03-14 03:30 | 47 | 46 |  |  | 43538.1458 | 60 | 53
2019-03-14 04:00 | 46 | 45 |  |  | 43538.1667 | 58 | 51
2019-03-14 04:30 | 48 | 47 |  |  | 43538.1875 | 61 | 54
2019-03-14 05:00 | 51 | 50 |  |  | 43538.2083 | 63 | 57
2019-03-14 05:30 | 53 | 53 |  |  | 43538.2292 | 66 | 62
2019-03-14 06:00 | 55 | 54 |  |  | 43538.25 | 68 | 65
2019-03-14 06:30 | 61 | 61 |  |  | 43538.2708 | 78 | 76
2019-03-14 07:00 | 64 | 64 |  |  | 43538.2917 | 83 | 82
2019-03-14 07:30 | 71 | 71 |  |  | 43538.3125 | 92 | 92
2019-03-14 08:00 | 73 | 73 |  |  | 43538.3333 | 97 | 95
2019-03-14 08:30 | 76 | 76 |  |  | 43538.3542 | 101 | 100
2019-03-14 09:00 | 78 | 78 |  |  | 43538.375 | 102 | 102
2019-03-14 09:30 | 80 | 80 |  |  | 43538.3958 | 104 | 104
2019-03-14 10:00 | 80 | 80 |  |  | 43538.4167 | 104 | 104
2019-03-14 10:30 | 79 | 79 |  |  | 43538.4375 | 103 | 103
2019-03-14 11:00 | 80 | 80 |  |  | 43538.4583 | 105 | 105
2019-03-14 11:30 | 81 | 81 |  |  | 43538.4792 | 105 | 105
2019-03-14 12:00 | 85 | 84 |  |  | 43538.5 | 107 | 107
2019-03-14 12:30 | 83 | 83 |  |  | 43538.5208 | 105 | 104
2019-03-14 13:00 | 85 | 85 |  |  | 43538.5417 | 106 | 106
2019-03-14 13:30 | 86 | 86 |  |  | 43538.5625 | 107 | 106
2019-03-14 14:00 | 88 | 88 |  |  | 43538.5833 | 107 | 107
2019-03-14 14:30 | 88 | 88 |  |  | 43538.6042 | 110 | 110
2019-03-14 15:00 | 90 | 90 |  |  | 43538.625 | 110 | 110
2019-03-14 15:30 | 88 | 87 |  |  | 43538.6458 | 109 | 109
2019-03-14 16:00 | 94 | 94 |  |  | 43538.6667 | 114 | 113
2019-03-14 16:30 | 96 | 96 |  |  | 43538.6875 | 112 | 111
2019-03-14 17:00 | 96 | 96 |  |  | 43538.7083 | 113 | 112
2019-03-14 17:30 | 92 | 91 |  |  | 43538.7292 | 109 | 108
2019-03-14 18:00 | 92 | 91 |  |  | 43538.75 | 108 | 107
2019-03-14 18:30 | 94 | 94 |  |  | 43538.7708 | 109 | 108
2019-03-14 19:00 | 97 | 97 |  |  | 43538.7917 | 112 | 111
2019-03-14 19:30 | 97 | 97 |  |  | 43538.8125 | 111 | 109
2019-03-14 20:00 | 95 | 95 |  |  | 43538.8333 | 108 | 108
2019-03-14 20:30 | 93 | 93 |  |  | 43538.8542 | 105 | 104
2019-03-14 21:00 | 89 | 89 |  |  | 43538.875 | 102 | 101
2019-03-14 21:30 | 82 | 82 |  |  | 43538.8958 | 94 | 94
2019-03-14 22:00 | 76 | 76 |  |  | 43538.9167 | 89 | 88
2019-03-14 22:30 | 70 | 69 |  |  | 43538.9375 | 81 | 81
2019-03-14 23:00 | 63 | 62 |  |  | 43538.9583 | 73 | 72
2019-03-14 23:30 | 58 | 56 |  |  | 43538.9792 | 68 | 67
2019-03-15 | 54 | 51 |  |  | 43539 | 63 | 62
2019-03-15 00:30 | 51 | 48 |  |  | 43539.0208 | 59 | 58
2019-03-15 01:00 | 48 | 45 |  |  | 43539.0417 | 55 | 53
2019-03-15 01:30 | 46 | 42 |  |  | 43539.0625 | 52 | 50
2019-03-15 02:00 | 44 | 42 |  |  | 43539.0833 | 53 | 49
2019-03-15 02:30 | 43 | 42 |  |  | 43539.1042 | 54 | 49
2019-03-15 03:00 | 44 | 44 |  |  | 43539.125 | 55 | 50
2019-03-15 03:30 | 46 | 45 |  |  | 43539.1458 | 56 | 52
2019-03-15 04:00 | 46 | 46 |  |  | 43539.1667 | 56 | 52
2019-03-15 04:30 | 47 | 47 |  |  | 43539.1875 | 58 | 54
2019-03-15 05:00 | 51 | 50 |  |  | 43539.2083 | 61 | 57
2019-03-15 05:30 | 51 | 50 |  |  | 43539.2292 | 61 | 58
2019-03-15 06:00 | 50 | 50 |  |  | 43539.25 | 63 | 60
2019-03-15 06:30 | 55 | 55 |  |  | 43539.2708 | 70 | 69
2019-03-15 07:00 | 56 | 56 |  |  | 43539.2917 | 76 | 74
2019-03-15 07:30 | 62 | 62 |  |  | 43539.3125 | 83 | 83
2019-03-15 08:00 | 66 | 66 |  |  | 43539.3333 | 88 | 87
2019-03-15 08:30 | 67 | 66 |  |  | 43539.3542 | 90 | 89
2019-03-15 09:00 | 66 | 66 |  |  | 43539.375 | 93 | 89
2019-03-15 09:30 | 68 | 68 |  |  | 43539.3958 | 96 | 91
2019-03-15 10:00 | 69 | 68 |  |  | 43539.4167 | 96 | 92
2019-03-15 10:30 | 69 | 69 |  |  | 43539.4375 | 98 | 93
2019-03-15 11:00 | 72 | 70 |  |  | 43539.4583 | 104 | 94
2019-03-15 11:30 | 72 | 71 |  |  | 43539.4792 | 104 | 94
2019-03-15 12:00 | 77 | 76 |  |  | 43539.5 | 109 | 100
2019-03-15 12:30 | 85 | 84 |  |  | 43539.5208 | 115 | 106
2019-03-15 13:00 | 87 | 86 |  |  | 43539.5417 | 115 | 107
2019-03-15 13:30 | 88 | 87 |  |  | 43539.5625 | 118 | 109
2019-03-15 14:00 | 98 | 96 |  |  | 43539.5833 | 127 | 117
2019-03-15 14:30 | 99 | 97 |  |  | 43539.6042 | 131 | 119
2019-03-15 15:00 | 99 | 96 |  |  | 43539.625 | 131 | 118
2019-03-15 15:30 | 98 | 96 |  |  | 43539.6458 | 126 | 116
2019-03-15 16:00 | 100 | 98 |  |  | 43539.6667 | 125 | 117
2019-03-15 16:30 | 102 | 101 |  |  | 43539.6875 | 124 | 117
2019-03-15 17:00 | 93 | 91 |  |  | 43539.7083 | 116 | 112
2019-03-15 17:30 | 87 | 86 |  |  | 43539.7292 | 108 | 104
2019-03-15 18:00 | 81 | 80 |  |  | 43539.75 | 102 | 96
2019-03-15 18:30 | 80 | 79 |  |  | 43539.7708 | 101 | 93
2019-03-15 19:00 | 82 | 81 |  |  | 43539.7917 | 102 | 95
2019-03-15 19:30 | 78 | 77 |  |  | 43539.8125 | 97 | 90
2019-03-15 20:00 | 76 | 75 |  |  | 43539.8333 | 93 | 86
2019-03-15 20:30 | 75 | 74 |  |  | 43539.8542 | 89 | 85
2019-03-15 21:00 | 72 | 71 |  |  | 43539.875 | 87 | 82
2019-03-15 21:30 | 68 | 68 |  |  | 43539.8958 | 83 | 78
2019-03-15 22:00 | 69 | 69 |  |  | 43539.9167 | 85 | 80
2019-03-15 22:30 | 71 | 70 |  |  | 43539.9375 | 86 | 81
2019-03-15 23:00 | 66 | 65 |  |  | 43539.9583 | 79 | 74
2019-03-15 23:30 | 55 | 54 |  |  | 43539.9792 | 69 | 63
2019-03-16 | 46 | 45 |  |  | 43540 | 61 | 54
2019-03-16 00:30 | 45 | 44 |  |  | 43540.0208 | 61 | 52
2019-03-16 01:00 | 43 | 41 |  |  | 43540.0417 | 58 | 49
2019-03-16 01:30 | 46 | 44 |  |  | 43540.0625 | 58 | 49
2019-03-16 02:00 | 45 | 43 |  |  | 43540.0833 | 59 | 49
2019-03-16 02:30 | 44 | 41 |  |  | 43540.1042 | 58 | 47
2019-03-16 03:00 | 44 | 42 |  |  | 43540.125 | 58 | 47
2019-03-16 03:30 | 43 | 41 |  |  | 43540.1458 | 57 | 46
2019-03-16 04:00 | 42 | 40 |  |  | 43540.1667 | 56 | 45
2019-03-16 04:30 | 41 | 39 |  |  | 43540.1875 | 54 | 44
2019-03-16 05:00 | 44 | 42 |  |  | 43540.2083 | 57 | 47
2019-03-16 05:30 | 45 | 43 |  |  | 43540.2292 | 59 | 50
2019-03-16 06:00 | 43 | 40 |  |  | 43540.25 | 57 | 48
2019-03-16 06:30 | 40 | 38 |  |  | 43540.2708 | 56 | 46
2019-03-16 07:00 | 38 | 37 |  |  | 43540.2917 | 53 | 46
2019-03-16 07:30 | 37 | 37 |  |  | 43540.3125 | 51 | 47
2019-03-16 08:00 | 38 | 38 |  |  | 43540.3333 | 53 | 49
2019-03-16 08:30 | 43 | 43 |  |  | 43540.3542 | 59 | 54
2019-03-16 09:00 | 41 | 41 |  |  | 43540.375 | 59 | 54
2019-03-16 09:30 | 42 | 41 |  |  | 43540.3958 | 57 | 52
2019-03-16 10:00 | 46 | 45 |  |  | 43540.4167 | 60 | 56
2019-03-16 10:30 | 47 | 47 |  |  | 43540.4375 | 61 | 58
2019-03-16 11:00 | 44 | 44 |  |  | 43540.4583 | 62 | 58
2019-03-16 11:30 | 45 | 45 |  |  | 43540.4792 | 61 | 57
2019-03-16 12:00 | 47 | 47 |  |  | 43540.5 | 58 | 56
2019-03-16 12:30 | 49 | 49 |  |  | 43540.5208 | 60 | 58
2019-03-16 13:00 | 46 | 46 |  |  | 43540.5417 | 58 | 56
2019-03-16 13:30 | 48 | 48 |  |  | 43540.5625 | 62 | 60
2019-03-16 14:00 | 41 | 41 |  |  | 43540.5833 | 59 | 56
2019-03-16 14:30 | 42 | 42 |  |  | 43540.6042 | 54 | 51
2019-03-16 15:00 | 47 | 47 |  |  | 43540.625 | 60 | 57
2019-03-16 15:30 | 50 | 50 |  |  | 43540.6458 | 64 | 62
2019-03-16 16:00 | 53 | 53 |  |  | 43540.6667 | 67 | 64
2019-03-16 16:30 | 57 | 57 |  |  | 43540.6875 | 70 | 67
2019-03-16 17:00 | 56 | 56 |  |  | 43540.7083 | 70 | 68
2019-03-16 17:30 | 56 | 56 |  |  | 43540.7292 | 69 | 66
2019-03-16 18:00 | 54 | 54 |  |  | 43540.75 | 69 | 66
2019-03-16 18:30 | 57 | 56 |  |  | 43540.7708 | 70 | 67
2019-03-16 19:00 | 60 | 60 |  |  | 43540.7917 | 73 | 70
2019-03-16 19:30 | 61 | 61 |  |  | 43540.8125 | 74 | 72
2019-03-16 20:00 | 61 | 61 |  |  | 43540.8333 | 74 | 72
2019-03-16 20:30 | 60 | 60 |  |  | 43540.8542 | 73 | 71
2019-03-16 21:00 | 55 | 55 |  |  | 43540.875 | 67 | 64
2019-03-16 21:30 | 54 | 53 |  |  | 43540.8958 | 66 | 63
2019-03-16 22:00 | 54 | 54 |  |  | 43540.9167 | 67 | 64
2019-03-16 22:30 | 54 | 53 |  |  | 43540.9375 | 68 | 64
2019-03-16 23:00 | 53 | 52 |  |  | 43540.9583 | 65 | 60
2019-03-16 23:30 | 51 | 50 |  |  | 43540.9792 | 63 | 59
2019-03-17 | 48 | 47 |  |  | 43541 | 60 | 55
2019-03-17 00:30 | 43 | 42 |  |  | 43541.0208 | 56 | 49
2019-03-17 01:00 | 39 | 37 |  |  | 43541.0417 | 52 | 45
2019-03-17 01:30 | 39 | 38 |  |  | 43541.0625 | 51 | 45
2019-03-17 02:00 | 39 | 38 |  |  | 43541.0833 | 49 | 44
2019-03-17 02:30 | 35 | 34 |  |  | 43541.1042 | 45 | 39
2019-03-17 03:00 | 33 | 32 |  |  | 43541.125 | 43 | 38
2019-03-17 03:30 | 33 | 32 |  |  | 43541.1458 | 43 | 38
2019-03-17 04:00 | 33 | 32 |  |  | 43541.1667 | 44 | 38
2019-03-17 04:30 | 35 | 33 |  |  | 43541.1875 | 46 | 40
2019-03-17 05:00 | 37 | 35 |  |  | 43541.2083 | 48 | 41
2019-03-17 05:30 | 41 | 39 |  |  | 43541.2292 | 52 | 46
2019-03-17 06:00 | 41 | 39 |  |  | 43541.25 | 53 | 47
2019-03-17 06:30 | 37 | 34 |  |  | 43541.2708 | 49 | 42
2019-03-17 07:00 | 35 | 32 |  |  | 43541.2917 | 47 | 41
2019-03-17 07:30 | 33 | 31 |  |  | 43541.3125 | 46 | 40
2019-03-17 08:00 | 34 | 32 |  |  | 43541.3333 | 47 | 42
2019-03-17 08:30 | 36 | 34 |  |  | 43541.3542 | 48 | 44
2019-03-17 09:00 | 39 | 38 |  |  | 43541.375 | 52 | 49
2019-03-17 09:30 | 43 | 42 |  |  | 43541.3958 | 58 | 53
2019-03-17 10:00 | 41 | 40 |  |  | 43541.4167 | 56 | 52
2019-03-17 10:30 | 42 | 41 |  |  | 43541.4375 | 55 | 51
2019-03-17 11:00 | 46 | 45 |  |  | 43541.4583 | 60 | 56
2019-03-17 11:30 | 42 | 41 |  |  | 43541.4792 | 58 | 53
2019-03-17 12:00 | 44 | 42 |  |  | 43541.5 | 60 | 55
2019-03-17 12:30 | 49 | 48 |  |  | 43541.5208 | 66 | 61
2019-03-17 13:00 | 49 | 48 |  |  | 43541.5417 | 67 | 61
2019-03-17 13:30 | 50 | 47 |  |  | 43541.5625 | 69 | 58
2019-03-17 14:00 | 49 | 46 |  |  | 43541.5833 | 64 | 52
2019-03-17 14:30 | 49 | 46 |  |  | 43541.6042 | 61 | 49
2019-03-17 15:00 | 54 | 52 |  |  | 43541.625 | 69 | 59
2019-03-17 15:30 | 62 | 60 |  |  | 43541.6458 | 75 | 66
2019-03-17 16:00 | 62 | 60 |  |  | 43541.6667 | 75 | 65
2019-03-17 16:30 | 60 | 57 |  |  | 43541.6875 | 74 | 64
2019-03-17 17:00 | 63 | 61 |  |  | 43541.7083 | 78 | 70
2019-03-17 17:30 | 64 | 62 |  |  | 43541.7292 | 80 | 72
2019-03-17 18:00 | 63 | 60 |  |  | 43541.75 | 79 | 72
2019-03-17 18:30 | 64 | 62 |  |  | 43541.7708 | 81 | 73
2019-03-17 19:00 | 63 | 61 |  |  | 43541.7917 | 81 | 73
2019-03-17 19:30 | 62 | 60 |  |  | 43541.8125 | 78 | 72
2019-03-17 20:00 | 61 | 60 |  |  | 43541.8333 | 74 | 71
2019-03-17 20:30 | 62 | 61 |  |  | 43541.8542 | 76 | 73
2019-03-17 21:00 | 63 | 63 |  |  | 43541.875 | 77 | 74
2019-03-17 21:30 | 63 | 62 |  |  | 43541.8958 | 75 | 71
2019-03-17 22:00 | 62 | 60 |  |  | 43541.9167 | 75 | 71
2019-03-17 22:30 | 61 | 59 |  |  | 43541.9375 | 74 | 70
2019-03-17 23:00 | 60 | 59 |  |  | 43541.9583 | 71 | 67
2019-03-17 23:30 | 60 | 58 |  |  | 43541.9792 | 70 | 66
2019-03-18 | 54 | 53 |  |  | 43542 | 66 | 61
2019-03-18 00:30 | 53 | 51 |  |  | 43542.0208 | 63 | 58
2019-03-18 01:00 | 50 | 48 |  |  | 43542.0417 | 60 | 55
2019-03-18 01:30 | 49 | 47 |  |  | 43542.0625 | 59 | 52
2019-03-18 02:00 | 48 | 45 |  |  | 43542.0833 | 58 | 51
2019-03-18 02:30 | 48 | 45 |  |  | 43542.1042 | 58 | 51
2019-03-18 03:00 | 48 | 45 |  |  | 43542.125 | 58 | 51
2019-03-18 03:30 | 50 | 47 |  |  | 43542.1458 | 58 | 52
2019-03-18 04:00 | 49 | 47 |  |  | 43542.1667 | 59 | 52
2019-03-18 04:30 | 51 | 48 |  |  | 43542.1875 | 60 | 53
2019-03-18 05:00 | 52 | 50 |  |  | 43542.2083 | 62 | 55
2019-03-18 05:30 | 51 | 49 |  |  | 43542.2292 | 61 | 55
2019-03-18 06:00 | 52 | 51 |  |  | 43542.25 | 63 | 59
2019-03-18 06:30 | 58 | 57 |  |  | 43542.2708 | 72 | 70
2019-03-18 07:00 | 62 | 61 |  |  | 43542.2917 | 79 | 77
2019-03-18 07:30 | 68 | 68 |  |  | 43542.3125 | 88 | 87
2019-03-18 08:00 | 72 | 72 |  |  | 43542.3333 | 92 | 91
2019-03-18 08:30 | 71 | 71 |  |  | 43542.3542 | 92 | 90
2019-03-18 09:00 | 72 | 71 |  |  | 43542.375 | 96 | 92
2019-03-18 09:30 | 74 | 73 |  |  | 43542.3958 | 96 | 91
2019-03-18 10:00 | 74 | 72 |  |  | 43542.4167 | 98 | 91
2019-03-18 10:30 | 73 | 72 |  |  | 43542.4375 | 101 | 93
2019-03-18 11:00 | 75 | 74 |  |  | 43542.4583 | 102 | 95
2019-03-18 11:30 | 77 | 76 |  |  | 43542.4792 | 105 | 98
2019-03-18 12:00 | 76 | 75 |  |  | 43542.5 | 103 | 97
2019-03-18 12:30 | 75 | 74 |  |  | 43542.5208 | 102 | 95
2019-03-18 13:00 | 77 | 76 |  |  | 43542.5417 | 103 | 96
2019-03-18 13:30 | 93 | 93 |  |  | 43542.5625 | 115 | 110
2019-03-18 14:00 | 107 | 107 |  |  | 43542.5833 | 126 | 123
2019-03-18 14:30 | 97 | 97 |  |  | 43542.6042 | 124 | 118
2019-03-18 15:00 | 84 | 81 |  |  | 43542.625 | 108 | 99
2019-03-18 15:30 | 76 | 73 |  |  | 43542.6458 | 96 | 86
2019-03-18 16:00 | 78 | 76 |  |  | 43542.6667 | 98 | 89
2019-03-18 16:30 | 81 | 78 |  |  | 43542.6875 | 99 | 89
2019-03-18 17:00 | 80 | 78 |  |  | 43542.7083 | 97 | 87
2019-03-18 17:30 | 81 | 79 |  |  | 43542.7292 | 98 | 88
2019-03-18 18:00 | 80 | 79 |  |  | 43542.75 | 91 | 86
2019-03-18 18:30 | 80 | 80 |  |  | 43542.7708 | 88 | 87
2019-03-18 19:00 | 83 | 83 |  |  | 43542.7917 | 91 | 90
2019-03-18 19:30 | 81 | 81 |  |  | 43542.8125 | 90 | 88
2019-03-18 20:00 | 81 | 81 |  |  | 43542.8333 | 88 | 86
2019-03-18 20:30 | 79 | 79 |  |  | 43542.8542 | 86 | 84
2019-03-18 21:00 | 77 | 76 |  |  | 43542.875 | 83 | 81
2019-03-18 21:30 | 73 | 73 |  |  | 43542.8958 | 80 | 78
2019-03-18 22:00 | 71 | 71 |  |  | 43542.9167 | 79 | 77
2019-03-18 22:30 | 67 | 67 |  |  | 43542.9375 | 76 | 74
2019-03-18 23:00 | 63 | 62 |  |  | 43542.9583 | 71 | 68
2019-03-18 23:30 | 57 | 56 |  |  | 43542.9792 | 65 | 62
2019-03-19 | 53 | 52 |  |  | 43543 | 62 | 58
2019-03-19 00:30 | 50 | 49 |  |  | 43543.0208 | 58 | 54
2019-03-19 01:00 | 47 | 46 |  |  | 43543.0417 | 55 | 50
2019-03-19 01:30 | 45 | 44 |  |  | 43543.0625 | 52 | 47
2019-03-19 02:00 | 44 | 43 |  |  | 43543.0833 | 51 | 46
2019-03-19 02:30 | 43 | 42 |  |  | 43543.1042 | 51 | 45
2019-03-19 03:00 | 43 | 42 |  |  | 43543.125 | 51 | 45
2019-03-19 03:30 | 41 | 40 |  |  | 43543.1458 | 49 | 43
2019-03-19 04:00 | 41 | 40 |  |  | 43543.1667 | 49 | 43
2019-03-19 04:30 | 42 | 41 |  |  | 43543.1875 | 50 | 44
2019-03-19 05:00 | 46 | 45 |  |  | 43543.2083 | 53 | 48
2019-03-19 05:30 | 49 | 49 |  |  | 43543.2292 | 57 | 53
2019-03-19 06:00 | 51 | 51 |  |  | 43543.25 | 59 | 57
2019-03-19 06:30 | 55 | 54 |  |  | 43543.2708 | 67 | 65
2019-03-19 07:00 | 59 | 58 |  |  | 43543.2917 | 73 | 72
2019-03-19 07:30 | 65 | 65 |  |  | 43543.3125 | 82 | 81
2019-03-19 08:00 | 67 | 67 |  |  | 43543.3333 | 85 | 84
2019-03-19 08:30 | 66 | 65 |  |  | 43543.3542 | 86 | 84
2019-03-19 09:00 | 66 | 66 |  |  | 43543.375 | 86 | 84
2019-03-19 09:30 | 66 | 66 |  |  | 43543.3958 | 87 | 86
2019-03-19 10:00 | 67 | 67 |  |  | 43543.4167 | 87 | 86
2019-03-19 10:30 | 67 | 67 |  |  | 43543.4375 | 86 | 85
2019-03-19 11:00 | 68 | 68 |  |  | 43543.4583 | 87 | 86
2019-03-19 11:30 | 70 | 69 |  |  | 43543.4792 | 88 | 88
2019-03-19 12:00 | 72 | 71 |  |  | 43543.5 | 92 | 91
2019-03-19 12:30 | 73 | 72 |  |  | 43543.5208 | 92 | 91
2019-03-19 13:00 | 74 | 74 |  |  | 43543.5417 | 93 | 92
2019-03-19 13:30 | 77 | 76 |  |  | 43543.5625 | 96 | 95
2019-03-19 14:00 | 79 | 79 |  |  | 43543.5833 | 98 | 97
2019-03-19 14:30 | 85 | 84 |  |  | 43543.6042 | 104 | 103
2019-03-19 15:00 | 88 | 88 |  |  | 43543.625 | 110 | 107
2019-03-19 15:30 | 93 | 92 |  |  | 43543.6458 | 113 | 110
2019-03-19 16:00 | 97 | 97 |  |  | 43543.6667 | 117 | 114
2019-03-19 16:30 | 100 | 100 |  |  | 43543.6875 | 118 | 115
2019-03-19 17:00 | 103 | 103 |  |  | 43543.7083 | 120 | 117
2019-03-19 17:30 | 103 | 103 |  |  | 43543.7292 | 119 | 115
2019-03-19 18:00 | 100 | 100 |  |  | 43543.75 | 117 | 111
2019-03-19 18:30 | 98 | 97 |  |  | 43543.7708 | 114 | 108
2019-03-19 19:00 | 101 | 101 |  |  | 43543.7917 | 118 | 111
2019-03-19 19:30 | 98 | 98 |  |  | 43543.8125 | 114 | 109
2019-03-19 20:00 | 97 | 97 |  |  | 43543.8333 | 110 | 106
2019-03-19 20:30 | 94 | 94 |  |  | 43543.8542 | 107 | 102
2019-03-19 21:00 | 89 | 89 |  |  | 43543.875 | 101 | 97
2019-03-19 21:30 | 84 | 84 |  |  | 43543.8958 | 93 | 91
2019-03-19 22:00 | 80 | 80 |  |  | 43543.9167 | 90 | 89
2019-03-19 22:30 | 76 | 76 |  |  | 43543.9375 | 85 | 83
2019-03-19 23:00 | 68 | 68 |  |  | 43543.9583 | 78 | 76
2019-03-19 23:30 | 64 | 64 |  |  | 43543.9792 | 74 | 72
2019-03-20 | 60 | 60 |  |  | 43544 | 71 | 68
2019-03-20 00:30 | 55 | 55 |  |  | 43544.0208 | 65 | 62
2019-03-20 01:00 | 52 | 51 |  |  | 43544.0417 | 62 | 56
2019-03-20 01:30 | 51 | 49 |  |  | 43544.0625 | 62 | 56
2019-03-20 02:00 | 50 | 48 |  |  | 43544.0833 | 62 | 55
2019-03-20 02:30 | 49 | 47 |  |  | 43544.1042 | 60 | 53
2019-03-20 03:00 | 48 | 46 |  |  | 43544.125 | 59 | 52
2019-03-20 03:30 | 46 | 44 |  |  | 43544.1458 | 57 | 50
2019-03-20 04:00 | 45 | 43 |  |  | 43544.1667 | 57 | 50
2019-03-20 04:30 | 46 | 44 |  |  | 43544.1875 | 58 | 50
2019-03-20 05:00 | 50 | 48 |  |  | 43544.2083 | 62 | 55
2019-03-20 05:30 | 54 | 53 |  |  | 43544.2292 | 66 | 61
2019-03-20 06:00 | 56 | 55 |  |  | 43544.25 | 69 | 65
2019-03-20 06:30 | 60 | 59 |  |  | 43544.2708 | 77 | 74
2019-03-20 07:00 | 63 | 63 |  |  | 43544.2917 | 83 | 80
2019-03-20 07:30 | 70 | 69 |  |  | 43544.3125 | 91 | 89
2019-03-20 08:00 | 72 | 72 |  |  | 43544.3333 | 94 | 93
2019-03-20 08:30 | 74 | 73 |  |  | 43544.3542 | 99 | 95
2019-03-20 09:00 | 74 | 74 |  |  | 43544.375 | 101 | 97
2019-03-20 09:30 | 76 | 75 |  |  | 43544.3958 | 102 | 97
2019-03-20 10:00 | 79 | 78 |  |  | 43544.4167 | 103 | 98
2019-03-20 10:30 | 77 | 77 |  |  | 43544.4375 | 103 | 98
2019-03-20 11:00 | 77 | 76 |  |  | 43544.4583 | 105 | 99
2019-03-20 11:30 | 77 | 75 |  |  | 43544.4792 | 106 | 97
2019-03-20 12:00 | 76 | 74 |  |  | 43544.5 | 105 | 96
2019-03-20 12:30 | 87 | 86 |  |  | 43544.5208 | 113 | 105
2019-03-20 13:00 | 82 | 82 |  |  | 43544.5417 | 112 | 104
2019-03-20 13:30 | 85 | 85 |  |  | 43544.5625 | 108 | 101
2019-03-20 14:00 | 84 | 83 |  |  | 43544.5833 | 114 | 107
2019-03-20 14:30 | 89 | 89 |  |  | 43544.6042 | 118 | 111
2019-03-20 15:00 | 94 | 93 |  |  | 43544.625 | 117 | 110
2019-03-20 15:30 | 97 | 97 |  |  | 43544.6458 | 120 | 114
2019-03-20 16:00 | 98 | 98 |  |  | 43544.6667 | 123 | 117
2019-03-20 16:30 | 91 | 91 |  |  | 43544.6875 | 118 | 110
2019-03-20 17:00 | 90 | 90 |  |  | 43544.7083 | 117 | 108
2019-03-20 17:30 | 91 | 91 |  |  | 43544.7292 | 112 | 105
2019-03-20 18:00 | 89 | 89 |  |  | 43544.75 | 110 | 103
2019-03-20 18:30 | 90 | 90 |  |  | 43544.7708 | 112 | 104
2019-03-20 19:00 | 93 | 93 |  |  | 43544.7917 | 115 | 107
2019-03-20 19:30 | 90 | 90 |  |  | 43544.8125 | 112 | 104
2019-03-20 20:00 | 90 | 90 |  |  | 43544.8333 | 108 | 103
2019-03-20 20:30 | 87 | 87 |  |  | 43544.8542 | 104 | 100
2019-03-20 21:00 | 83 | 83 |  |  | 43544.875 | 99 | 95
2019-03-20 21:30 | 81 | 81 |  |  | 43544.8958 | 97 | 92
2019-03-20 22:00 | 78 | 78 |  |  | 43544.9167 | 96 | 91
2019-03-20 22:30 | 74 | 74 |  |  | 43544.9375 | 90 | 87
2019-03-20 23:00 | 71 | 71 |  |  | 43544.9583 | 85 | 82
2019-03-20 23:30 | 68 | 67 |  |  | 43544.9792 | 79 | 77
2019-03-21 | 62 | 62 |  |  | 43545 | 74 | 72
2019-03-21 00:30 | 57 | 57 |  |  | 43545.0208 | 70 | 66
2019-03-21 01:00 | 55 | 55 |  |  | 43545.0417 | 67 | 62
2019-03-21 01:30 | 55 | 55 |  |  | 43545.0625 | 66 | 61
2019-03-21 02:00 | 53 | 53 |  |  | 43545.0833 | 65 | 60
2019-03-21 02:30 | 51 | 51 |  |  | 43545.1042 | 63 | 57
2019-03-21 03:00 | 50 | 49 |  |  | 43545.125 | 62 | 57
2019-03-21 03:30 | 51 | 50 |  |  | 43545.1458 | 63 | 57
2019-03-21 04:00 | 52 | 52 |  |  | 43545.1667 | 63 | 58
2019-03-21 04:30 | 54 | 53 |  |  | 43545.1875 | 66 | 61
2019-03-21 05:00 | 55 | 55 |  |  | 43545.2083 | 69 | 64
2019-03-21 05:30 | 59 | 58 |  |  | 43545.2292 | 72 | 68
2019-03-21 06:00 | 62 | 62 |  |  | 43545.25 | 74 | 72
2019-03-21 06:30 | 64 | 64 |  |  | 43545.2708 | 81 | 79
2019-03-21 07:00 | 69 | 69 |  |  | 43545.2917 | 89 | 88
2019-03-21 07:30 | 80 | 80 |  |  | 43545.3125 | 101 | 100
2019-03-21 08:00 | 82 | 82 |  |  | 43545.3333 | 104 | 102
2019-03-21 08:30 | 81 | 81 |  |  | 43545.3542 | 106 | 103
2019-03-21 09:00 | 80 | 80 |  |  | 43545.375 | 110 | 105
2019-03-21 09:30 | 82 | 82 |  |  | 43545.3958 | 109 | 105
2019-03-21 10:00 | 80 | 79 |  |  | 43545.4167 | 106 | 101
2019-03-21 10:30 | 79 | 79 |  |  | 43545.4375 | 103 | 99
2019-03-21 11:00 | 79 | 79 |  |  | 43545.4583 | 103 | 100
2019-03-21 11:30 | 79 | 79 |  |  | 43545.4792 | 105 | 102
2019-03-21 12:00 | 82 | 81 |  |  | 43545.5 | 106 | 104
2019-03-21 12:30 | 83 | 82 |  |  | 43545.5208 | 107 | 104
2019-03-21 13:00 | 83 | 82 |  |  | 43545.5417 | 108 | 106
2019-03-21 13:30 | 85 | 84 |  |  | 43545.5625 | 110 | 107
2019-03-21 14:00 | 88 | 88 |  |  | 43545.5833 | 112 | 110
2019-03-21 14:30 | 92 | 91 |  |  | 43545.6042 | 117 | 115
2019-03-21 15:00 | 95 | 95 |  |  | 43545.625 | 120 | 117
2019-03-21 15:30 | 98 | 98 |  |  | 43545.6458 | 123 | 119
2019-03-21 16:00 | 97 | 97 |  |  | 43545.6667 | 123 | 120
2019-03-21 16:30 | 99 | 99 |  |  | 43545.6875 | 119 | 115
2019-03-21 17:00 | 101 | 101 |  |  | 43545.7083 | 124 | 120
2019-03-21 17:30 | 97 | 97 |  |  | 43545.7292 | 120 | 114
2019-03-21 18:00 | 96 | 96 |  |  | 43545.75 | 118 | 112
2019-03-21 18:30 | 97 | 97 |  |  | 43545.7708 | 117 | 111
2019-03-21 19:00 | 98 | 98 |  |  | 43545.7917 | 119 | 112
2019-03-21 19:30 | 96 | 96 |  |  | 43545.8125 | 116 | 109
2019-03-21 20:00 | 93 | 93 |  |  | 43545.8333 | 112 | 106
2019-03-21 20:30 | 92 | 92 |  |  | 43545.8542 | 110 | 105
2019-03-21 21:00 | 89 | 89 |  |  | 43545.875 | 106 | 102
2019-03-21 21:30 | 83 | 82 |  |  | 43545.8958 | 97 | 95
2019-03-21 22:00 | 78 | 77 |  |  | 43545.9167 | 93 | 92
2019-03-21 22:30 | 75 | 74 |  |  | 43545.9375 | 90 | 88
2019-03-21 23:00 | 71 | 70 |  |  | 43545.9583 | 83 | 81
2019-03-21 23:30 | 65 | 64 |  |  | 43545.9792 | 77 | 75
2019-03-22 | 60 | 60 |  |  | 43546 | 73 | 70
2019-03-22 00:30 | 57 | 57 |  |  | 43546.0208 | 70 | 67
2019-03-22 01:00 | 55 | 55 |  |  | 43546.0417 | 68 | 64
2019-03-22 01:30 | 54 | 54 |  |  | 43546.0625 | 67 | 63
2019-03-22 02:00 | 52 | 52 |  |  | 43546.0833 | 65 | 60
2019-03-22 02:30 | 51 | 51 |  |  | 43546.1042 | 63 | 59
2019-03-22 03:00 | 49 | 49 |  |  | 43546.125 | 63 | 58
2019-03-22 03:30 | 50 | 49 |  |  | 43546.1458 | 63 | 59
2019-03-22 04:00 | 49 | 48 |  |  | 43546.1667 | 62 | 57
2019-03-22 04:30 | 48 | 48 |  |  | 43546.1875 | 62 | 57
2019-03-22 05:00 | 50 | 50 |  |  | 43546.2083 | 65 | 61
2019-03-22 05:30 | 55 | 55 |  |  | 43546.2292 | 68 | 65
2019-03-22 06:00 | 57 | 57 |  |  | 43546.25 | 72 | 69
2019-03-22 06:30 | 62 | 62 |  |  | 43546.2708 | 80 | 77
2019-03-22 07:00 | 67 | 67 |  |  | 43546.2917 | 88 | 86
2019-03-22 07:30 | 77 | 77 |  |  | 43546.3125 | 100 | 99
2019-03-22 08:00 | 79 | 79 |  |  | 43546.3333 | 104 | 102
2019-03-22 08:30 | 79 | 79 |  |  | 43546.3542 | 106 | 104
2019-03-22 09:00 | 81 | 81 |  |  | 43546.375 | 105 | 104
2019-03-22 09:30 | 80 | 80 |  |  | 43546.3958 | 107 | 105
2019-03-22 10:00 | 82 | 81 |  |  | 43546.4167 | 105 | 105
2019-03-22 10:30 | 81 | 80 |  |  | 43546.4375 | 104 | 103
2019-03-22 11:00 | 83 | 82 |  |  | 43546.4583 | 107 | 106
2019-03-22 11:30 | 80 | 80 |  |  | 43546.4792 | 106 | 104
2019-03-22 12:00 | 80 | 79 |  |  | 43546.5 | 104 | 102
2019-03-22 12:30 | 83 | 83 |  |  | 43546.5208 | 109 | 100
2019-03-22 13:00 | 77 | 76 |  |  | 43546.5417 | 109 | 95
2019-03-22 13:30 | 72 | 71 |  |  | 43546.5625 | 110 | 96
2019-03-22 14:00 | 72 | 70 |  |  | 43546.5833 | 110 | 96
2019-03-22 14:30 | 76 | 76 |  |  | 43546.6042 | 110 | 101
2019-03-22 15:00 | 84 | 84 |  |  | 43546.625 | 110 | 102
2019-03-22 15:30 | 84 | 83 |  |  | 43546.6458 | 113 | 105
2019-03-22 16:00 | 91 | 91 |  |  | 43546.6667 | 118 | 110
2019-03-22 16:30 | 93 | 93 |  |  | 43546.6875 | 122 | 112
2019-03-22 17:00 | 93 | 92 |  |  | 43546.7083 | 124 | 113
2019-03-22 17:30 | 91 | 90 |  |  | 43546.7292 | 121 | 108
2019-03-22 18:00 | 88 | 87 |  |  | 43546.75 | 118 | 105
2019-03-22 18:30 | 89 | 87 |  |  | 43546.7708 | 117 | 103
2019-03-22 19:00 | 89 | 88 |  |  | 43546.7917 | 118 | 104
2019-03-22 19:30 | 86 | 86 |  |  | 43546.8125 | 113 | 101
2019-03-22 20:00 | 85 | 85 |  |  | 43546.8333 | 106 | 99
2019-03-22 20:30 | 84 | 84 |  |  | 43546.8542 | 99 | 97
2019-03-22 21:00 | 80 | 79 |  |  | 43546.875 | 92 | 91
2019-03-22 21:30 | 76 | 76 |  |  | 43546.8958 | 89 | 88
2019-03-22 22:00 | 74 | 74 |  |  | 43546.9167 | 87 | 86
2019-03-22 22:30 | 73 | 73 |  |  | 43546.9375 | 87 | 86
2019-03-22 23:00 | 68 | 67 |  |  | 43546.9583 | 81 | 79
2019-03-22 23:30 | 62 | 62 |  |  | 43546.9792 | 75 | 73
2019-03-23 | 58 | 58 |  |  | 43547 | 71 | 69
2019-03-23 00:30 | 56 | 55 |  |  | 43547.0208 | 67 | 66
2019-03-23 01:00 | 52 | 52 |  |  | 43547.0417 | 64 | 63
2019-03-23 01:30 | 51 | 51 |  |  | 43547.0625 | 62 | 60
2019-03-23 02:00 | 50 | 50 |  |  | 43547.0833 | 61 | 59
2019-03-23 02:30 | 49 | 49 |  |  | 43547.1042 | 60 | 58
2019-03-23 03:00 | 49 | 49 |  |  | 43547.125 | 60 | 58
2019-03-23 03:30 | 49 | 48 |  |  | 43547.1458 | 60 | 57
2019-03-23 04:00 | 46 | 46 |  |  | 43547.1667 | 57 | 55
2019-03-23 04:30 | 45 | 45 |  |  | 43547.1875 | 57 | 54
2019-03-23 05:00 | 46 | 46 |  |  | 43547.2083 | 58 | 55
2019-03-23 05:30 | 47 | 47 |  |  | 43547.2292 | 60 | 58
2019-03-23 06:00 | 48 | 48 |  |  | 43547.25 | 61 | 59
2019-03-23 06:30 | 47 | 47 |  |  | 43547.2708 | 62 | 60
2019-03-23 07:00 | 47 | 47 |  |  | 43547.2917 | 62 | 60
2019-03-23 07:30 | 48 | 48 |  |  | 43547.3125 | 64 | 63
2019-03-23 08:00 | 49 | 49 |  |  | 43547.3333 | 64 | 64
2019-03-23 08:30 | 48 | 48 |  |  | 43547.3542 | 66 | 65
2019-03-23 09:00 | 50 | 49 |  |  | 43547.375 | 68 | 68
2019-03-23 09:30 | 51 | 51 |  |  | 43547.3958 | 71 | 70
2019-03-23 10:00 | 52 | 52 |  |  | 43547.4167 | 70 | 69
2019-03-23 10:30 | 53 | 53 |  |  | 43547.4375 | 71 | 70
2019-03-23 11:00 | 55 | 55 |  |  | 43547.4583 | 73 | 71
2019-03-23 11:30 | 59 | 59 |  |  | 43547.4792 | 76 | 75
2019-03-23 12:00 | 59 | 59 |  |  | 43547.5 | 77 | 76
2019-03-23 12:30 | 60 | 60 |  |  | 43547.5208 | 78 | 77
2019-03-23 13:00 | 61 | 61 |  |  | 43547.5417 | 79 | 78
2019-03-23 13:30 | 64 | 64 |  |  | 43547.5625 | 82 | 80
2019-03-23 14:00 | 65 | 65 |  |  | 43547.5833 | 82 | 79
2019-03-23 14:30 | 66 | 66 |  |  | 43547.6042 | 85 | 81
2019-03-23 15:00 | 70 | 70 |  |  | 43547.625 | 87 | 83
2019-03-23 15:30 | 73 | 73 |  |  | 43547.6458 | 91 | 86
2019-03-23 16:00 | 78 | 77 |  |  | 43547.6667 | 94 | 90
2019-03-23 16:30 | 78 | 78 |  |  | 43547.6875 | 94 | 90
2019-03-23 17:00 | 80 | 80 |  |  | 43547.7083 | 95 | 90
2019-03-23 17:30 | 80 | 79 |  |  | 43547.7292 | 95 | 90
2019-03-23 18:00 | 79 | 79 |  |  | 43547.75 | 94 | 91
2019-03-23 18:30 | 80 | 79 |  |  | 43547.7708 | 94 | 91
2019-03-23 19:00 | 82 | 81 |  |  | 43547.7917 | 95 | 93
2019-03-23 19:30 | 78 | 78 |  |  | 43547.8125 | 92 | 89
2019-03-23 20:00 | 72 | 72 |  |  | 43547.8333 | 90 | 84
2019-03-23 20:30 | 70 | 70 |  |  | 43547.8542 | 89 | 83
2019-03-23 21:00 | 67 | 67 |  |  | 43547.875 | 85 | 80
2019-03-23 21:30 | 66 | 66 |  |  | 43547.8958 | 83 | 77
2019-03-23 22:00 | 65 | 65 |  |  | 43547.9167 | 83 | 77
2019-03-23 22:30 | 63 | 63 |  |  | 43547.9375 | 81 | 76
2019-03-23 23:00 | 61 | 61 |  |  | 43547.9583 | 76 | 73
2019-03-23 23:30 | 58 | 58 |  |  | 43547.9792 | 72 | 69
2019-03-24 | 54 | 54 |  |  | 43548 | 68 | 64
2019-03-24 00:30 | 48 | 48 |  |  | 43548.0208 | 62 | 58
2019-03-24 01:00 | 45 | 44 |  |  | 43548.0417 | 58 | 54
2019-03-24 01:30 | 47 | 45 |  |  | 43548.0625 | 60 | 54
2019-03-24 02:00 | 47 | 45 |  |  | 43548.0833 | 60 | 53
2019-03-24 02:30 | 44 | 42 |  |  | 43548.1042 | 58 | 51
2019-03-24 03:00 | 41 | 39 |  |  | 43548.125 | 55 | 47
2019-03-24 03:30 | 36 | 33 |  |  | 43548.1458 | 50 | 41
2019-03-24 04:00 | 35 | 32 |  |  | 43548.1667 | 48 | 40
2019-03-24 04:30 | 35 | 32 |  |  | 43548.1875 | 50 | 42
2019-03-24 05:00 | 40 | 37 |  |  | 43548.2083 | 55 | 48
2019-03-24 05:30 | 43 | 40 |  |  | 43548.2292 | 57 | 50
2019-03-24 06:00 | 42 | 39 |  |  | 43548.25 | 56 | 49
2019-03-24 06:30 | 41 | 38 |  |  | 43548.2708 | 56 | 49
2019-03-24 07:00 | 40 | 37 |  |  | 43548.2917 | 57 | 50
2019-03-24 07:30 | 41 | 39 |  |  | 43548.3125 | 58 | 52
2019-03-24 08:00 | 43 | 41 |  |  | 43548.3333 | 59 | 54
2019-03-24 08:30 | 44 | 42 |  |  | 43548.3542 | 61 | 57
2019-03-24 09:00 | 45 | 44 |  |  | 43548.375 | 61 | 58
2019-03-24 09:30 | 44 | 44 |  |  | 43548.3958 | 61 | 59
2019-03-24 10:00 | 48 | 48 |  |  | 43548.4167 | 64 | 62
2019-03-24 10:30 | 51 | 51 |  |  | 43548.4375 | 66 | 64
2019-03-24 11:00 | 53 | 53 |  |  | 43548.4583 | 68 | 66
2019-03-24 11:30 | 56 | 56 |  |  | 43548.4792 | 70 | 68
2019-03-24 12:00 | 59 | 58 |  |  | 43548.5 | 73 | 71
2019-03-24 12:30 | 62 | 61 |  |  | 43548.5208 | 74 | 72
2019-03-24 13:00 | 62 | 62 |  |  | 43548.5417 | 75 | 73
2019-03-24 13:30 | 63 | 63 |  |  | 43548.5625 | 77 | 75
2019-03-24 14:00 | 67 | 66 |  |  | 43548.5833 | 79 | 77
2019-03-24 14:30 | 70 | 70 |  |  | 43548.6042 | 85 | 81
2019-03-24 15:00 | 73 | 73 |  |  | 43548.625 | 89 | 85
2019-03-24 15:30 | 77 | 77 |  |  | 43548.6458 | 93 | 88
2019-03-24 16:00 | 81 | 81 |  |  | 43548.6667 | 96 | 91
2019-03-24 16:30 | 86 | 86 |  |  | 43548.6875 | 99 | 95
2019-03-24 17:00 | 85 | 85 |  |  | 43548.7083 | 100 | 95
2019-03-24 17:30 | 81 | 81 |  |  | 43548.7292 | 100 | 94
2019-03-24 18:00 | 79 | 78 |  |  | 43548.75 | 100 | 94
2019-03-24 18:30 | 80 | 80 |  |  | 43548.7708 | 103 | 97
2019-03-24 19:00 | 80 | 80 |  |  | 43548.7917 | 104 | 98
2019-03-24 19:30 | 78 | 78 |  |  | 43548.8125 | 103 | 96
2019-03-24 20:00 | 76 | 76 |  |  | 43548.8333 | 98 | 93
2019-03-24 20:30 | 75 | 75 |  |  | 43548.8542 | 95 | 91
2019-03-24 21:00 | 80 | 80 |  |  | 43548.875 | 97 | 92
2019-03-24 21:30 | 79 | 79 |  |  | 43548.8958 | 95 | 90
2019-03-24 22:00 | 76 | 76 |  |  | 43548.9167 | 95 | 89
2019-03-24 22:30 | 76 | 76 |  |  | 43548.9375 | 94 | 90
2019-03-24 23:00 | 73 | 73 |  |  | 43548.9583 | 90 | 85
2019-03-24 23:30 | 68 | 68 |  |  | 43548.9792 | 85 | 82
2019-03-25 | 64 | 64 |  |  | 43549 | 79 | 77
2019-03-25 00:30 | 58 | 57 |  |  | 43549.0208 | 73 | 69
2019-03-25 01:00 | 57 | 56 |  |  | 43549.0417 | 71 | 66
2019-03-25 01:30 | 56 | 55 |  |  | 43549.0625 | 69 | 65
2019-03-25 02:00 | 55 | 54 |  |  | 43549.0833 | 69 | 65
2019-03-25 02:30 | 54 | 53 |  |  | 43549.1042 | 67 | 63
2019-03-25 03:00 | 54 | 53 |  |  | 43549.125 | 67 | 62
2019-03-25 03:30 | 52 | 52 |  |  | 43549.1458 | 66 | 61
2019-03-25 04:00 | 53 | 52 |  |  | 43549.1667 | 66 | 61
2019-03-25 04:30 | 53 | 52 |  |  | 43549.1875 | 67 | 62
2019-03-25 05:00 | 56 | 56 |  |  | 43549.2083 | 71 | 66
2019-03-25 05:30 | 59 | 59 |  |  | 43549.2292 | 74 | 71
2019-03-25 06:00 | 63 | 62 |  |  | 43549.25 | 78 | 75
2019-03-25 06:30 | 62 | 62 |  |  | 43549.2708 | 80 | 77
2019-03-25 07:00 | 67 | 67 |  |  | 43549.2917 | 88 | 86
2019-03-25 07:30 | 73 | 73 |  |  | 43549.3125 | 95 | 95
2019-03-25 08:00 | 76 | 76 |  |  | 43549.3333 | 100 | 99
2019-03-25 08:30 | 75 | 75 |  |  | 43549.3542 | 102 | 100
2019-03-25 09:00 | 75 | 74 |  |  | 43549.375 | 99 | 99
2019-03-25 09:30 | 77 | 76 |  |  | 43549.3958 | 101 | 100
2019-03-25 10:00 | 76 | 75 |  |  | 43549.4167 | 100 | 100
2019-03-25 10:30 | 76 | 75 |  |  | 43549.4375 | 101 | 101
2019-03-25 11:00 | 78 | 77 |  |  | 43549.4583 | 104 | 103
2019-03-25 11:30 | 81 | 81 |  |  | 43549.4792 | 108 | 108
2019-03-25 12:00 | 82 | 82 |  |  | 43549.5 | 107 | 106
2019-03-25 12:30 | 89 | 89 |  |  | 43549.5208 | 114 | 114
2019-03-25 13:00 | 87 | 86 |  |  | 43549.5417 | 112 | 112
2019-03-25 13:30 | 93 | 93 |  |  | 43549.5625 | 116 | 116
2019-03-25 14:00 | 90 | 90 |  |  | 43549.5833 | 110 | 109
2019-03-25 14:30 | 94 | 94 |  |  | 43549.6042 | 114 | 113
2019-03-25 15:00 | 91 | 91 |  |  | 43549.625 | 115 | 114
2019-03-25 15:30 | 90 | 90 |  |  | 43549.6458 | 115 | 114
2019-03-25 16:00 | 91 | 90 |  |  | 43549.6667 | 116 | 115
2019-03-25 16:30 | 86 | 85 |  |  | 43549.6875 | 112 | 110
2019-03-25 17:00 | 88 | 87 |  |  | 43549.7083 | 112 | 110
2019-03-25 17:30 | 87 | 86 |  |  | 43549.7292 | 110 | 107
2019-03-25 18:00 | 85 | 84 |  |  | 43549.75 | 107 | 105
2019-03-25 18:30 | 84 | 83 |  |  | 43549.7708 | 105 | 102
2019-03-25 19:00 | 85 | 84 |  |  | 43549.7917 | 105 | 101
2019-03-25 19:30 | 82 | 82 |  |  | 43549.8125 | 102 | 99
2019-03-25 20:00 | 85 | 85 |  |  | 43549.8333 | 101 | 99
2019-03-25 20:30 | 90 | 88 |  |  | 43549.8542 | 104 | 100
2019-03-25 21:00 | 87 | 85 |  |  | 43549.875 | 101 | 96
2019-03-25 21:30 | 84 | 81 |  |  | 43549.8958 | 98 | 92
2019-03-25 22:00 | 82 | 79 |  |  | 43549.9167 | 97 | 91
2019-03-25 22:30 | 79 | 76 |  |  | 43549.9375 | 93 | 88
2019-03-25 23:00 | 74 | 71 |  |  | 43549.9583 | 85 | 81
2019-03-25 23:30 | 66 | 63 |  |  | 43549.9792 | 76 | 74
2019-03-26 | 61 | 59 |  |  | 43550 | 71 | 70
2019-03-26 00:30 | 60 | 58 |  |  | 43550.0208 | 68 | 67
2019-03-26 01:00 | 60 | 57 |  |  | 43550.0417 | 67 | 65
2019-03-26 01:30 | 61 | 57 |  |  | 43550.0625 | 67 | 65
2019-03-26 02:00 | 62 | 58 |  |  | 43550.0833 | 68 | 66
2019-03-26 02:30 | 60 | 56 |  |  | 43550.1042 | 67 | 65
2019-03-26 03:00 | 58 | 54 |  |  | 43550.125 | 65 | 62
2019-03-26 03:30 | 58 | 54 |  |  | 43550.1458 | 64 | 61
2019-03-26 04:00 | 58 | 54 |  |  | 43550.1667 | 65 | 62
2019-03-26 04:30 | 58 | 54 |  |  | 43550.1875 | 65 | 62
2019-03-26 05:00 | 60 | 56 |  |  | 43550.2083 | 68 | 65
2019-03-26 05:30 | 59 | 57 |  |  | 43550.2292 | 69 | 68
2019-03-26 06:00 | 58 | 56 |  |  | 43550.25 | 69 | 69
2019-03-26 06:30 | 62 | 60 |  |  | 43550.2708 | 76 | 76
2019-03-26 07:00 | 66 | 64 |  |  | 43550.2917 | 83 | 82
2019-03-26 07:30 | 73 | 72 |  |  | 43550.3125 | 93 | 93
2019-03-26 08:00 | 75 | 74 |  |  | 43550.3333 | 96 | 96
2019-03-26 08:30 | 75 | 74 |  |  | 43550.3542 | 97 | 96
2019-03-26 09:00 | 75 | 75 |  |  | 43550.375 | 97 | 96
2019-03-26 09:30 | 81 | 81 |  |  | 43550.3958 | 103 | 103
2019-03-26 10:00 | 79 | 78 |  |  | 43550.4167 | 103 | 103
2019-03-26 10:30 | 79 | 79 |  |  | 43550.4375 | 103 | 103
2019-03-26 11:00 | 81 | 81 |  |  | 43550.4583 | 107 | 107
2019-03-26 11:30 | 88 | 87 |  |  | 43550.4792 | 113 | 111
2019-03-26 12:00 | 86 | 85 |  |  | 43550.5 | 111 | 110
2019-03-26 12:30 | 84 | 84 |  |  | 43550.5208 | 109 | 107
2019-03-26 13:00 | 84 | 83 |  |  | 43550.5417 | 106 | 104
2019-03-26 13:30 | 88 | 87 |  |  | 43550.5625 | 112 | 111
2019-03-26 14:00 | 87 | 86 |  |  | 43550.5833 | 117 | 116
2019-03-26 14:30 | 90 | 89 |  |  | 43550.6042 | 116 | 115
2019-03-26 15:00 | 90 | 90 |  |  | 43550.625 | 115 | 113
2019-03-26 15:30 | 92 | 91 |  |  | 43550.6458 | 116 | 114
2019-03-26 16:00 | 93 | 92 |  |  | 43550.6667 | 117 | 115
2019-03-26 16:30 | 94 | 93 |  |  | 43550.6875 | 118 | 115
2019-03-26 17:00 | 95 | 94 |  |  | 43550.7083 | 118 | 115
2019-03-26 17:30 | 96 | 94 |  |  | 43550.7292 | 118 | 113
2019-03-26 18:00 | 94 | 93 |  |  | 43550.75 | 112 | 110
2019-03-26 18:30 | 94 | 93 |  |  | 43550.7708 | 109 | 108
2019-03-26 19:00 | 94 | 94 |  |  | 43550.7917 | 109 | 108
2019-03-26 19:30 | 93 | 92 |  |  | 43550.8125 | 107 | 105
2019-03-26 20:00 | 92 | 91 |  |  | 43550.8333 | 105 | 104
2019-03-26 20:30 | 90 | 89 |  |  | 43550.8542 | 103 | 101
2019-03-26 21:00 | 86 | 85 |  |  | 43550.875 | 99 | 97
2019-03-26 21:30 | 82 | 81 |  |  | 43550.8958 | 94 | 92
2019-03-26 22:00 | 78 | 77 |  |  | 43550.9167 | 91 | 89
2019-03-26 22:30 | 76 | 76 |  |  | 43550.9375 | 87 | 87
2019-03-26 23:00 | 72 | 71 |  |  | 43550.9583 | 81 | 81
2019-03-26 23:30 | 65 | 65 |  |  | 43550.9792 | 77 | 76
2019-03-27 | 61 | 60 |  |  | 43551 | 71 | 70
2019-03-27 00:30 | 57 | 55 |  |  | 43551.0208 | 66 | 66
2019-03-27 01:00 | 55 | 53 |  |  | 43551.0417 | 63 | 62
2019-03-27 01:30 | 54 | 52 |  |  | 43551.0625 | 60 | 59
2019-03-27 02:00 | 52 | 49 |  |  | 43551.0833 | 58 | 57
2019-03-27 02:30 | 50 | 47 |  |  | 43551.1042 | 57 | 55
2019-03-27 03:00 | 49 | 45 |  |  | 43551.125 | 56 | 55
2019-03-27 03:30 | 49 | 45 |  |  | 43551.1458 | 57 | 55
2019-03-27 04:00 | 48 | 44 |  |  | 43551.1667 | 55 | 53
2019-03-27 04:30 | 49 | 45 |  |  | 43551.1875 | 56 | 55
2019-03-27 05:00 | 54 | 50 |  |  | 43551.2083 | 61 | 59
2019-03-27 05:30 | 56 | 53 |  |  | 43551.2292 | 65 | 64
2019-03-27 06:00 | 60 | 57 |  |  | 43551.25 | 70 | 69
2019-03-27 06:30 | 62 | 59 |  |  | 43551.2708 | 75 | 74
2019-03-27 07:00 | 69 | 66 |  |  | 43551.2917 | 85 | 84
2019-03-27 07:30 | 76 | 74 |  |  | 43551.3125 | 95 | 94
2019-03-27 08:00 | 80 | 79 |  |  | 43551.3333 | 100 | 100
2019-03-27 08:30 | 81 | 80 |  |  | 43551.3542 | 102 | 102
2019-03-27 09:00 | 81 | 80 |  |  | 43551.375 | 103 | 103
2019-03-27 09:30 | 81 | 80 |  |  | 43551.3958 | 103 | 103
2019-03-27 10:00 | 79 | 78 |  |  | 43551.4167 | 99 | 99
2019-03-27 10:30 | 80 | 79 |  |  | 43551.4375 | 100 | 100
2019-03-27 11:00 | 79 | 78 |  |  | 43551.4583 | 98 | 97
2019-03-27 11:30 | 80 | 79 |  |  | 43551.4792 | 100 | 99
2019-03-27 12:00 | 80 | 79 |  |  | 43551.5 | 99 | 99
2019-03-27 12:30 | 79 | 77 |  |  | 43551.5208 | 97 | 97
2019-03-27 13:00 | 78 | 77 |  |  | 43551.5417 | 97 | 97
2019-03-27 13:30 | 78 | 76 |  |  | 43551.5625 | 96 | 96
2019-03-27 14:00 | 78 | 77 |  |  | 43551.5833 | 98 | 97
2019-03-27 14:30 | 78 | 77 |  |  | 43551.6042 | 98 | 97
2019-03-27 15:00 | 78 | 77 |  |  | 43551.625 | 97 | 97
2019-03-27 15:30 | 76 | 75 |  |  | 43551.6458 | 95 | 94
2019-03-27 16:00 | 78 | 76 |  |  | 43551.6667 | 95 | 95
2019-03-27 16:30 | 80 | 78 |  |  | 43551.6875 | 97 | 97
2019-03-27 17:00 | 81 | 79 |  |  | 43551.7083 | 98 | 97
2019-03-27 17:30 | 79 | 77 |  |  | 43551.7292 | 94 | 93
2019-03-27 18:00 | 77 | 75 |  |  | 43551.75 | 91 | 89
2019-03-27 18:30 | 76 | 74 |  |  | 43551.7708 | 87 | 85
2019-03-27 19:00 | 77 | 74 |  |  | 43551.7917 | 88 | 86
2019-03-27 19:30 | 77 | 74 |  |  | 43551.8125 | 86 | 84
2019-03-27 20:00 | 75 | 71 |  |  | 43551.8333 | 84 | 82
2019-03-27 20:30 | 75 | 72 |  |  | 43551.8542 | 84 | 82
2019-03-27 21:00 | 73 | 70 |  |  | 43551.875 | 82 | 80
2019-03-27 21:30 | 70 | 67 |  |  | 43551.8958 | 77 | 75
2019-03-27 22:00 | 67 | 63 |  |  | 43551.9167 | 76 | 73
2019-03-27 22:30 | 64 | 59 |  |  | 43551.9375 | 72 | 69
2019-03-27 23:00 | 58 | 54 |  |  | 43551.9583 | 65 | 64
2019-03-27 23:30 | 56 | 51 |  |  | 43551.9792 | 64 | 62
2019-03-28 | 55 | 48 |  |  | 43552 | 61 | 58
2019-03-28 00:30 | 51 | 44 |  |  | 43552.0208 | 56 | 53
2019-03-28 01:00 | 49 | 41 |  |  | 43552.0417 | 52 | 48
2019-03-28 01:30 | 47 | 39 |  |  | 43552.0625 | 51 | 47
2019-03-28 02:00 | 46 | 40 |  |  | 43552.0833 | 51 | 48
2019-03-28 02:30 | 44 | 39 |  |  | 43552.1042 | 48 | 46
2019-03-28 03:00 | 42 | 37 |  |  | 43552.125 | 46 | 44
2019-03-28 03:30 | 43 | 38 |  |  | 43552.1458 | 48 | 46
2019-03-28 04:00 | 43 | 38 |  |  | 43552.1667 | 48 | 46
2019-03-28 04:30 | 43 | 39 |  |  | 43552.1875 | 48 | 46
2019-03-28 05:00 | 46 | 42 |  |  | 43552.2083 | 51 | 49
2019-03-28 05:30 | 48 | 45 |  |  | 43552.2292 | 54 | 53
2019-03-28 06:00 | 50 | 48 |  |  | 43552.25 | 58 | 57
2019-03-28 06:30 | 56 | 54 |  |  | 43552.2708 | 67 | 67
2019-03-28 07:00 | 61 | 61 |  |  | 43552.2917 | 76 | 76
2019-03-28 07:30 | 68 | 67 |  |  | 43552.3125 | 84 | 84
2019-03-28 08:00 | 72 | 71 |  |  | 43552.3333 | 89 | 89
2019-03-28 08:30 | 72 | 72 |  |  | 43552.3542 | 91 | 91
2019-03-28 09:00 | 75 | 75 |  |  | 43552.375 | 97 | 97
2019-03-28 09:30 | 77 | 76 |  |  | 43552.3958 | 99 | 99
2019-03-28 10:00 | 80 | 79 |  |  | 43552.4167 | 101 | 101
2019-03-28 10:30 | 75 | 74 |  |  | 43552.4375 | 99 | 98
2019-03-28 11:00 | 76 | 74 |  |  | 43552.4583 | 102 | 100
2019-03-28 11:30 | 75 | 73 |  |  | 43552.4792 | 101 | 99
2019-03-28 12:00 | 78 | 76 |  |  | 43552.5 | 95 | 92
2019-03-28 12:30 | 71 | 70 |  |  | 43552.5208 | 90 | 87
2019-03-28 13:00 | 73 | 71 |  |  | 43552.5417 | 94 | 92
2019-03-28 13:30 | 77 | 75 |  |  | 43552.5625 | 97 | 95
2019-03-28 14:00 | 78 | 76 |  |  | 43552.5833 | 97 | 95
2019-03-28 14:30 | 76 | 74 |  |  | 43552.6042 | 99 | 96
2019-03-28 15:00 | 74 | 71 |  |  | 43552.625 | 96 | 93
2019-03-28 15:30 | 72 | 70 |  |  | 43552.6458 | 91 | 88
2019-03-28 16:00 | 72 | 70 |  |  | 43552.6667 | 90 | 87
2019-03-28 16:30 | 73 | 71 |  |  | 43552.6875 | 93 | 90
2019-03-28 17:00 | 75 | 73 |  |  | 43552.7083 | 94 | 91
2019-03-28 17:30 | 75 | 73 |  |  | 43552.7292 | 93 | 89
2019-03-28 18:00 | 76 | 73 |  |  | 43552.75 | 92 | 88
2019-03-28 18:30 | 77 | 73 |  |  | 43552.7708 | 92 | 87
2019-03-28 19:00 | 76 | 72 |  |  | 43552.7917 | 90 | 85
2019-03-28 19:30 | 78 | 73 |  |  | 43552.8125 | 90 | 84
2019-03-28 20:00 | 81 | 72 |  |  | 43552.8333 | 91 | 82
2019-03-28 20:30 | 81 | 72 |  |  | 43552.8542 | 91 | 81
2019-03-28 21:00 | 80 | 71 |  |  | 43552.875 | 89 | 79
2019-03-28 21:30 | 74 | 68 |  |  | 43552.8958 | 81 | 76
2019-03-28 22:00 | 70 | 64 |  |  | 43552.9167 | 78 | 74
2019-03-28 22:30 | 69 | 61 |  |  | 43552.9375 | 76 | 71
2019-03-28 23:00 | 65 | 57 |  |  | 43552.9583 | 70 | 64
2019-03-28 23:30 | 61 | 52 |  |  | 43552.9792 | 66 | 60
2019-03-29 | 62 | 51 |  |  | 43553 | 66 | 59
2019-03-29 00:30 | 57 | 46 |  |  | 43553.0208 | 61 | 54
2019-03-29 01:00 | 53 | 42 |  |  | 43553.0417 | 56 | 49
2019-03-29 01:30 | 53 | 41 |  |  | 43553.0625 | 54 | 46
2019-03-29 02:00 | 54 | 41 |  |  | 43553.0833 | 55 | 47
2019-03-29 02:30 | 54 | 41 |  |  | 43553.1042 | 55 | 46
2019-03-29 03:00 | 55 | 41 |  |  | 43553.125 | 56 | 48
2019-03-29 03:30 | 54 | 40 |  |  | 43553.1458 | 55 | 47
2019-03-29 04:00 | 53 | 39 |  |  | 43553.1667 | 54 | 46
2019-03-29 04:30 | 54 | 40 |  |  | 43553.1875 | 55 | 48
2019-03-29 05:00 | 56 | 43 |  |  | 43553.2083 | 57 | 51
2019-03-29 05:30 | 55 | 45 |  |  | 43553.2292 | 59 | 53
2019-03-29 06:00 | 58 | 49 |  |  | 43553.25 | 63 | 59
2019-03-29 06:30 | 61 | 53 |  |  | 43553.2708 | 70 | 67
2019-03-29 07:00 | 63 | 56 |  |  | 43553.2917 | 78 | 73
2019-03-29 07:30 | 71 | 64 |  |  | 43553.3125 | 86 | 82
2019-03-29 08:00 | 75 | 68 |  |  | 43553.3333 | 91 | 87
2019-03-29 08:30 | 79 | 72 |  |  | 43553.3542 | 100 | 96
2019-03-29 09:00 | 75 | 69 |  |  | 43553.375 | 95 | 91
2019-03-29 09:30 | 74 | 69 |  |  | 43553.3958 | 96 | 94
2019-03-29 10:00 | 71 | 69 |  |  | 43553.4167 | 94 | 92
2019-03-29 10:30 | 70 | 68 |  |  | 43553.4375 | 93 | 91
2019-03-29 11:00 | 69 | 67 |  |  | 43553.4583 | 93 | 91
2019-03-29 11:30 | 72 | 70 |  |  | 43553.4792 | 95 | 93
2019-03-29 12:00 | 69 | 67 |  |  | 43553.5 | 93 | 91
2019-03-29 12:30 | 69 | 67 |  |  | 43553.5208 | 92 | 91
2019-03-29 13:00 | 67 | 65 |  |  | 43553.5417 | 89 | 88
2019-03-29 13:30 | 67 | 65 |  |  | 43553.5625 | 89 | 88
2019-03-29 14:00 | 67 | 67 |  |  | 43553.5833 | 90 | 89
2019-03-29 14:30 | 71 | 71 |  |  | 43553.6042 | 92 | 92
2019-03-29 15:00 | 69 | 69 |  |  | 43553.625 | 94 | 93
2019-03-29 15:30 | 72 | 71 |  |  | 43553.6458 | 95 | 94
2019-03-29 16:00 | 74 | 73 |  |  | 43553.6667 | 96 | 95
2019-03-29 16:30 | 77 | 76 |  |  | 43553.6875 | 97 | 96
2019-03-29 17:00 | 79 | 78 |  |  | 43553.7083 | 97 | 95
2019-03-29 17:30 | 80 | 79 |  |  | 43553.7292 | 96 | 93
2019-03-29 18:00 | 79 | 78 |  |  | 43553.75 | 94 | 91
2019-03-29 18:30 | 77 | 76 |  |  | 43553.7708 | 90 | 88
2019-03-29 19:00 | 77 | 75 |  |  | 43553.7917 | 90 | 88
2019-03-29 19:30 | 77 | 75 |  |  | 43553.8125 | 89 | 87
2019-03-29 20:00 | 76 | 75 |  |  | 43553.8333 | 88 | 86
2019-03-29 20:30 | 77 | 75 |  |  | 43553.8542 | 89 | 87
2019-03-29 21:00 | 78 | 73 |  |  | 43553.875 | 88 | 85
2019-03-29 21:30 | 76 | 69 |  |  | 43553.8958 | 85 | 81
2019-03-29 22:00 | 77 | 70 |  |  | 43553.9167 | 84 | 81
2019-03-29 22:30 | 76 | 70 |  |  | 43553.9375 | 83 | 81
2019-03-29 23:00 | 74 | 67 |  |  | 43553.9583 | 79 | 77
2019-03-29 23:30 | 68 | 61 |  |  | 43553.9792 | 74 | 72
2019-03-30 | 65 | 58 |  |  | 43554 | 70 | 68
2019-03-30 00:30 | 63 | 55 |  |  | 43554.0208 | 68 | 66
2019-03-30 01:00 | 63 | 55 |  |  | 43554.0417 | 67 | 63
2019-03-30 01:30 | 63 | 54 |  |  | 43554.0625 | 66 | 62
2019-03-30 02:00 | 62 | 53 |  |  | 43554.0833 | 64 | 60
2019-03-30 02:30 | 63 | 53 |  |  | 43554.1042 | 64 | 60
2019-03-30 03:00 | 61 | 51 |  |  | 43554.125 | 63 | 59
2019-03-30 03:30 | 60 | 49 |  |  | 43554.1458 | 63 | 58
2019-03-30 04:00 | 59 | 49 |  |  | 43554.1667 | 61 | 57
2019-03-30 04:30 | 60 | 50 |  |  | 43554.1875 | 61 | 57
2019-03-30 05:00 | 61 | 51 |  |  | 43554.2083 | 64 | 60
2019-03-30 05:30 | 62 | 53 |  |  | 43554.2292 | 66 | 62
2019-03-30 06:00 | 62 | 53 |  |  | 43554.25 | 66 | 62
2019-03-30 06:30 | 63 | 53 |  |  | 43554.2708 | 68 | 64
2019-03-30 07:00 | 61 | 52 |  |  | 43554.2917 | 66 | 63
2019-03-30 07:30 | 58 | 49 |  |  | 43554.3125 | 64 | 62
2019-03-30 08:00 | 52 | 46 |  |  | 43554.3333 | 64 | 62
2019-03-30 08:30 | 54 | 47 |  |  | 43554.3542 | 65 | 63
2019-03-30 09:00 | 56 | 50 |  |  | 43554.375 | 67 | 66
2019-03-30 09:30 | 57 | 52 |  |  | 43554.3958 | 69 | 68
2019-03-30 10:00 | 61 | 57 |  |  | 43554.4167 | 73 | 72
2019-03-30 10:30 | 66 | 61 |  |  | 43554.4375 | 77 | 76
2019-03-30 11:00 | 62 | 57 |  |  | 43554.4583 | 75 | 74
2019-03-30 11:30 | 66 | 60 |  |  | 43554.4792 | 77 | 76
2019-03-30 12:00 | 70 | 65 |  |  | 43554.5 | 81 | 81
2019-03-30 12:30 | 70 | 67 |  |  | 43554.5208 | 83 | 82
2019-03-30 13:00 | 71 | 67 |  |  | 43554.5417 | 85 | 84
2019-03-30 13:30 | 75 | 72 |  |  | 43554.5625 | 87 | 87
2019-03-30 14:00 | 76 | 74 |  |  | 43554.5833 | 90 | 90
2019-03-30 14:30 | 75 | 71 |  |  | 43554.6042 | 88 | 87
2019-03-30 15:00 | 76 | 73 |  |  | 43554.625 | 90 | 89
2019-03-30 15:30 | 76 | 73 |  |  | 43554.6458 | 90 | 89
2019-03-30 16:00 | 73 | 69 |  |  | 43554.6667 | 86 | 85
2019-03-30 16:30 | 71 | 67 |  |  | 43554.6875 | 82 | 82
2019-03-30 17:00 | 71 | 67 |  |  | 43554.7083 | 82 | 81
2019-03-30 17:30 | 69 | 66 |  |  | 43554.7292 | 80 | 79
2019-03-30 18:00 | 67 | 63 |  |  | 43554.75 | 78 | 77
2019-03-30 18:30 | 67 | 64 |  |  | 43554.7708 | 80 | 79
2019-03-30 19:00 | 68 | 66 |  |  | 43554.7917 | 81 | 80
2019-03-30 19:30 | 64 | 61 |  |  | 43554.8125 | 76 | 75
2019-03-30 20:00 | 64 | 61 |  |  | 43554.8333 | 75 | 74
2019-03-30 20:30 | 63 | 60 |  |  | 43554.8542 | 75 | 74
2019-03-30 21:00 | 59 | 56 |  |  | 43554.875 | 70 | 69
2019-03-30 21:30 | 60 | 57 |  |  | 43554.8958 | 70 | 69
2019-03-30 22:00 | 61 | 58 |  |  | 43554.9167 | 71 | 70
2019-03-30 22:30 | 60 | 57 |  |  | 43554.9375 | 71 | 70
2019-03-30 23:00 | 62 | 58 |  |  | 43554.9583 | 71 | 70
2019-03-30 23:30 | 59 | 55 |  |  | 43554.9792 | 68 | 66
2019-03-31 | 56 | 52 |  |  | 43555 | 65 | 63
2019-03-31 00:30 | 53 | 48 |  |  | 43555.0208 | 60 | 58
2019-03-31 01:00 | 49 | 44 |  |  | 43555.0417 | 56 | 54
2019-03-31 01:30 | 48 | 42 |  |  | 43555.0625 | 54 | 51
2019-03-31 02:00 | 48 | 42 |  |  | 43555.0833 | 53 | 50
2019-03-31 02:30 | 47 | 41 |  |  | 43555.1042 | 52 | 49
2019-03-31 03:00 | 46 | 40 |  |  | 43555.125 | 51 | 48
2019-03-31 03:30 | 44 | 38 |  |  | 43555.1458 | 48 | 46
2019-03-31 04:00 | 43 | 36 |  |  | 43555.1667 | 47 | 44
2019-03-31 04:30 | 52 | 36 |  |  | 43555.1875 | 50 | 45
2019-03-31 05:00 | 52 | 36 |  |  | 43555.2083 | 49 | 44
2019-03-31 05:30 | 50 | 34 |  |  | 43555.2292 | 48 | 42
2019-03-31 06:00 | 50 | 34 |  |  | 43555.25 | 49 | 44
2019-03-31 06:30 | 50 | 33 |  |  | 43555.2708 | 49 | 44
2019-03-31 07:00 | 48 | 30 |  |  | 43555.2917 | 48 | 42
2019-03-31 07:30 | 47 | 29 |  |  | 43555.3125 | 46 | 41
2019-03-31 08:00 | 47 | 28 |  |  | 43555.3333 | 44 | 40
2019-03-31 08:30 | 45 | 28 |  |  | 43555.3542 | 44 | 40
2019-03-31 09:00 | 44 | 27 |  |  | 43555.375 | 43 | 39
2019-03-31 09:30 | 42 | 24 |  |  | 43555.3958 | 40 | 37
2019-03-31 10:00 | 41 | 25 |  |  | 43555.4167 | 40 | 37
2019-03-31 10:30 | 41 | 25 |  |  | 43555.4375 | 38 | 35
2019-03-31 11:00 | 41 | 25 |  |  | 43555.4583 | 39 | 36
2019-03-31 11:30 | 41 | 25 |  |  | 43555.4792 | 39 | 36
2019-03-31 12:00 | 41 | 26 |  |  | 43555.5 | 39 | 36
2019-03-31 12:30 | 41 | 26 |  |  | 43555.5208 | 40 | 37
2019-03-31 13:00 | 42 | 27 |  |  | 43555.5417 | 41 | 39
2019-03-31 13:30 | 42 | 27 |  |  | 43555.5625 | 41 | 38
2019-03-31 14:00 | 43 | 29 |  |  | 43555.5833 | 43 | 40
2019-03-31 14:30 | 45 | 33 |  |  | 43555.6042 | 45 | 43
2019-03-31 15:00 | 48 | 36 |  |  | 43555.625 | 48 | 47
2019-03-31 15:30 | 49 | 38 |  |  | 43555.6458 | 50 | 49
2019-03-31 16:00 | 52 | 41 |  |  | 43555.6667 | 53 | 52
2019-03-31 16:30 | 53 | 43 |  |  | 43555.6875 | 55 | 54
2019-03-31 17:00 | 54 | 45 |  |  | 43555.7083 | 58 | 56
2019-03-31 17:30 | 55 | 45 |  |  | 43555.7292 | 58 | 56
2019-03-31 18:00 | 57 | 47 |  |  | 43555.75 | 60 | 58
2019-03-31 18:30 | 59 | 50 |  |  | 43555.7708 | 64 | 62
2019-03-31 19:00 | 60 | 51 |  |  | 43555.7917 | 66 | 64
2019-03-31 19:30 | 58 | 48 |  |  | 43555.8125 | 63 | 61
2019-03-31 20:00 | 56 | 46 |  |  | 43555.8333 | 61 | 59
2019-03-31 20:30 | 55 | 46 |  |  | 43555.8542 | 60 | 59
2019-03-31 21:00 | 54 | 44 |  |  | 43555.875 | 58 | 56
2019-03-31 21:30 | 54 | 43 |  |  | 43555.8958 | 57 | 54
2019-03-31 22:00 | 52 | 41 |  |  | 43555.9167 | 55 | 53
2019-03-31 22:30 | 52 | 40 |  |  | 43555.9375 | 56 | 54
2019-03-31 23:00 | 53 | 40 |  |  | 43555.9583 | 55 | 52
2019-03-31 23:30 | 50 | 37 |  |  | 43555.9792 | 52 | 49
2019-04-01 | 51 | 37 |  |  | 43556 | 52 | 48
2019-04-01 00:30 | 50 | 34 |  |  | 43556.0208 | 49 | 44
2019-04-01 01:00 | 48 | 31 |  |  | 43556.0417 | 46 | 41
2019-04-01 01:30 | 47 | 29 |  |  | 43556.0625 | 44 | 40
2019-04-01 02:00 | 47 | 30 |  |  | 43556.0833 | 45 | 40
2019-04-01 02:30 | 48 | 31 |  |  | 43556.1042 | 45 | 41
2019-04-01 03:00 | 49 | 33 |  |  | 43556.125 | 46 | 42
2019-04-01 03:30 | 49 | 33 |  |  | 43556.1458 | 46 | 41
2019-04-01 04:00 | 49 | 32 |  |  | 43556.1667 | 45 | 40
2019-04-01 04:30 | 48 | 31 |  |  | 43556.1875 | 44 | 40
2019-04-01 05:00 | 48 | 32 |  |  | 43556.2083 | 47 | 42
2019-04-01 05:30 | 49 | 36 |  |  | 43556.2292 | 49 | 46
2019-04-01 06:00 | 49 | 37 |  |  | 43556.25 | 50 | 48
2019-04-01 06:30 | 50 | 41 |  |  | 43556.2708 | 57 | 55
2019-04-01 07:00 | 49 | 42 |  |  | 43556.2917 | 60 | 59
2019-04-01 07:30 | 51 | 46 |  |  | 43556.3125 | 66 | 65
2019-04-01 08:00 | 53 | 47 |  |  | 43556.3333 | 69 | 68
2019-04-01 08:30 | 53 | 47 |  |  | 43556.3542 | 69 | 68
2019-04-01 09:00 | 53 | 47 |  |  | 43556.375 | 70 | 69
2019-04-01 09:30 | 57 | 48 |  |  | 43556.3958 | 73 | 69
2019-04-01 10:00 | 55 | 46 |  |  | 43556.4167 | 72 | 68
2019-04-01 10:30 | 55 | 47 |  |  | 43556.4375 | 72 | 69
2019-04-01 11:00 | 56 | 48 |  |  | 43556.4583 | 74 | 71
2019-04-01 11:30 | 54 | 46 |  |  | 43556.4792 | 71 | 68
2019-04-01 12:00 | 55 | 46 |  |  | 43556.5 | 71 | 68
2019-04-01 12:30 | 53 | 45 |  |  | 43556.5208 | 70 | 67
2019-04-01 13:00 | 55 | 47 |  |  | 43556.5417 | 68 | 66
2019-04-01 13:30 | 55 | 47 |  |  | 43556.5625 | 71 | 68
2019-04-01 14:00 | 59 | 52 |  |  | 43556.5833 | 73 | 71
2019-04-01 14:30 | 58 | 52 |  |  | 43556.6042 | 74 | 72
2019-04-01 15:00 | 64 | 53 |  |  | 43556.625 | 82 | 75
2019-04-01 15:30 | 64 | 53 |  |  | 43556.6458 | 80 | 73
2019-04-01 16:00 | 67 | 57 |  |  | 43556.6667 | 83 | 75
2019-04-01 16:30 | 68 | 57 |  |  | 43556.6875 | 85 | 76
2019-04-01 17:00 | 68 | 57 |  |  | 43556.7083 | 82 | 74
2019-04-01 17:30 | 68 | 57 |  |  | 43556.7292 | 81 | 72
2019-04-01 18:00 | 69 | 57 |  |  | 43556.75 | 82 | 71
2019-04-01 18:30 | 71 | 58 |  |  | 43556.7708 | 83 | 72
2019-04-01 19:00 | 72 | 59 |  |  | 43556.7917 | 85 | 73
2019-04-01 19:30 | 68 | 59 |  |  | 43556.8125 | 78 | 71
2019-04-01 20:00 | 61 | 57 |  |  | 43556.8333 | 68 | 67
2019-04-01 20:30 | 57 | 53 |  |  | 43556.8542 | 64 | 63
2019-04-01 21:00 | 54 | 51 |  |  | 43556.875 | 60 | 60
2019-04-01 21:30 | 53 | 49 |  |  | 43556.8958 | 59 | 58
2019-04-01 22:00 | 53 | 47 |  |  | 43556.9167 | 59 | 57
2019-04-01 22:30 | 52 | 44 |  |  | 43556.9375 | 57 | 55
2019-04-01 23:00 | 52 | 43 |  |  | 43556.9583 | 55 | 53
2019-04-01 23:30 | 48 | 39 |  |  | 43556.9792 | 51 | 48
2019-04-02 | 49 | 39 |  |  | 43557 | 52 | 49
2019-04-02 00:30 | 49 | 38 |  |  | 43557.0208 | 49 | 46
2019-04-02 01:00 | 46 | 34 |  |  | 43557.0417 | 46 | 42
2019-04-02 01:30 | 47 | 33 |  |  | 43557.0625 | 45 | 41
2019-04-02 02:00 | 47 | 33 |  |  | 43557.0833 | 45 | 40
2019-04-02 02:30 | 47 | 34 |  |  | 43557.1042 | 45 | 40
2019-04-02 03:00 | 46 | 33 |  |  | 43557.125 | 45 | 40
2019-04-02 03:30 | 47 | 33 |  |  | 43557.1458 | 44 | 40
2019-04-02 04:00 | 46 | 32 |  |  | 43557.1667 | 43 | 39
2019-04-02 04:30 | 46 | 33 |  |  | 43557.1875 | 44 | 39
2019-04-02 05:00 | 49 | 37 |  |  | 43557.2083 | 47 | 43
2019-04-02 05:30 | 49 | 38 |  |  | 43557.2292 | 49 | 46
2019-04-02 06:00 | 48 | 38 |  |  | 43557.25 | 49 | 46
2019-04-02 06:30 | 50 | 42 |  |  | 43557.2708 | 55 | 54
2019-04-02 07:00 | 49 | 43 |  |  | 43557.2917 | 58 | 57
2019-04-02 07:30 | 52 | 48 |  |  | 43557.3125 | 64 | 63
2019-04-02 08:00 | 54 | 50 |  |  | 43557.3333 | 70 | 70
2019-04-02 08:30 | 56 | 48 |  |  | 43557.3542 | 70 | 69
2019-04-02 09:00 | 58 | 50 |  |  | 43557.375 | 68 | 67
2019-04-02 09:30 | 58 | 49 |  |  | 43557.3958 | 70 | 70
2019-04-02 10:00 | 58 | 51 |  |  | 43557.4167 | 72 | 72
2019-04-02 10:30 | 58 | 52 |  |  | 43557.4375 | 77 | 76
2019-04-02 11:00 | 61 | 55 |  |  | 43557.4583 | 78 | 77
2019-04-02 11:30 | 60 | 54 |  |  | 43557.4792 | 74 | 73
2019-04-02 12:00 | 61 | 55 |  |  | 43557.5 | 78 | 77
2019-04-02 12:30 | 62 | 56 |  |  | 43557.5208 | 74 | 73
2019-04-02 13:00 | 60 | 54 |  |  | 43557.5417 | 68 | 67
2019-04-02 13:30 | 58 | 52 |  |  | 43557.5625 | 71 | 71
2019-04-02 14:00 | 60 | 54 |  |  | 43557.5833 | 76 | 76
2019-04-02 14:30 | 67 | 62 |  |  | 43557.6042 | 77 | 77
2019-04-02 15:00 | 64 | 59 |  |  | 43557.625 | 82 | 81
2019-04-02 15:30 | 67 | 61 |  |  | 43557.6458 | 82 | 82
2019-04-02 16:00 | 67 | 61 |  |  | 43557.6667 | 79 | 78
2019-04-02 16:30 | 68 | 62 |  |  | 43557.6875 | 78 | 78
2019-04-02 17:00 | 68 | 61 |  |  | 43557.7083 | 77 | 77
2019-04-02 17:30 | 68 | 61 |  |  | 43557.7292 | 76 | 76
2019-04-02 18:00 | 69 | 62 |  |  | 43557.75 | 76 | 76
2019-04-02 18:30 | 70 | 63 |  |  | 43557.7708 | 76 | 76
2019-04-02 19:00 | 71 | 63 |  |  | 43557.7917 | 77 | 77
2019-04-02 19:30 | 69 | 60 |  |  | 43557.8125 | 74 | 74
2019-04-02 20:00 | 68 | 59 |  |  | 43557.8333 | 71 | 71
2019-04-02 20:30 | 68 | 59 |  |  | 43557.8542 | 70 | 70
2019-04-02 21:00 | 68 | 57 |  |  | 43557.875 | 69 | 69
2019-04-02 21:30 | 68 | 56 |  |  | 43557.8958 | 67 | 67
2019-04-02 22:00 | 66 | 53 |  |  | 43557.9167 | 65 | 65
2019-04-02 22:30 | 63 | 49 |  |  | 43557.9375 | 61 | 60
2019-04-02 23:00 | 65 | 48 |  |  | 43557.9583 | 59 | 58
2019-04-02 23:30 | 62 | 43 |  |  | 43557.9792 | 57 | 56
2019-04-03 | 59 | 38 |  |  | 43558 | 52 | 52
2019-04-03 00:30 | 56 | 35 |  |  | 43558.0208 | 47 | 47
2019-04-03 01:00 | 55 | 33 |  |  | 43558.0417 | 44 | 43
2019-04-03 01:30 | 55 | 31 |  |  | 43558.0625 | 42 | 42
2019-04-03 02:00 | 55 | 31 |  |  | 43558.0833 | 42 | 41
2019-04-03 02:30 | 54 | 31 |  |  | 43558.1042 | 41 | 40
2019-04-03 03:00 | 55 | 31 |  |  | 43558.125 | 41 | 40
2019-04-03 03:30 | 54 | 32 |  |  | 43558.1458 | 41 | 40
2019-04-03 04:00 | 55 | 32 |  |  | 43558.1667 | 41 | 41
2019-04-03 04:30 | 54 | 32 |  |  | 43558.1875 | 41 | 40
2019-04-03 05:00 | 55 | 34 |  |  | 43558.2083 | 44 | 43
2019-04-03 05:30 | 58 | 39 |  |  | 43558.2292 | 50 | 49
2019-04-03 06:00 | 58 | 42 |  |  | 43558.25 | 53 | 53
2019-04-03 06:30 | 59 | 45 |  |  | 43558.2708 | 59 | 59
2019-04-03 07:00 | 62 | 50 |  |  | 43558.2917 | 66 | 66
2019-04-03 07:30 | 59 | 50 |  |  | 43558.3125 | 68 | 68
2019-04-03 08:00 | 60 | 51 |  |  | 43558.3333 | 71 | 71
2019-04-03 08:30 | 64 | 55 |  |  | 43558.3542 | 75 | 75
2019-04-03 09:00 | 60 | 51 |  |  | 43558.375 | 71 | 71
2019-04-03 09:30 | 58 | 48 |  |  | 43558.3958 | 72 | 72
2019-04-03 10:00 | 65 | 57 |  |  | 43558.4167 | 83 | 83
2019-04-03 10:30 | 66 | 59 |  |  | 43558.4375 | 77 | 77
2019-04-03 11:00 | 67 | 59 |  |  | 43558.4583 | 75 | 75
2019-04-03 11:30 | 60 | 51 |  |  | 43558.4792 | 76 | 75
2019-04-03 12:00 | 59 | 51 |  |  | 43558.5 | 75 | 75
2019-04-03 12:30 | 59 | 51 |  |  | 43558.5208 | 75 | 75
2019-04-03 13:00 | 62 | 54 |  |  | 43558.5417 | 78 | 77
2019-04-03 13:30 | 60 | 53 |  |  | 43558.5625 | 75 | 75
2019-04-03 14:00 | 64 | 55 |  |  | 43558.5833 | 71 | 71
2019-04-03 14:30 | 65 | 56 |  |  | 43558.6042 | 77 | 77
2019-04-03 15:00 | 67 | 58 |  |  | 43558.625 | 78 | 78
2019-04-03 15:30 | 65 | 55 |  |  | 43558.6458 | 74 | 74
2019-04-03 16:00 | 68 | 58 |  |  | 43558.6667 | 76 | 76
2019-04-03 16:30 | 67 | 57 |  |  | 43558.6875 | 74 | 73
2019-04-03 17:00 | 67 | 58 |  |  | 43558.7083 | 73 | 73
2019-04-03 17:30 | 69 | 59 |  |  | 43558.7292 | 72 | 72
2019-04-03 18:00 | 72 | 61 |  |  | 43558.75 | 75 | 74
2019-04-03 18:30 | 71 | 60 |  |  | 43558.7708 | 73 | 73
2019-04-03 19:00 | 72 | 62 |  |  | 43558.7917 | 73 | 73
2019-04-03 19:30 | 70 | 59 |  |  | 43558.8125 | 70 | 69
2019-04-03 20:00 | 66 | 56 |  |  | 43558.8333 | 65 | 65
2019-04-03 20:30 | 67 | 56 |  |  | 43558.8542 | 66 | 65
2019-04-03 21:00 | 67 | 56 |  |  | 43558.875 | 66 | 65
2019-04-03 21:30 | 67 | 55 |  |  | 43558.8958 | 64 | 64
2019-04-03 22:00 | 68 | 54 |  |  | 43558.9167 | 64 | 63
2019-04-03 22:30 | 66 | 50 |  |  | 43558.9375 | 61 | 60
2019-04-03 23:00 | 63 | 47 |  |  | 43558.9583 | 56 | 55
2019-04-03 23:30 | 61 | 43 |  |  | 43558.9792 | 53 | 52
2019-04-04 | 60 | 40 |  |  | 43559 | 51 | 50
2019-04-04 00:30 | 58 | 37 |  |  | 43559.0208 | 47 | 46
2019-04-04 01:00 | 58 | 35 |  |  | 43559.0417 | 45 | 44
2019-04-04 01:30 | 57 | 34 |  |  | 43559.0625 | 43 | 41
2019-04-04 02:00 | 57 | 33 |  |  | 43559.0833 | 43 | 41
2019-04-04 02:30 | 57 | 33 |  |  | 43559.1042 | 42 | 40
2019-04-04 03:00 | 57 | 32 |  |  | 43559.125 | 43 | 41
2019-04-04 03:30 | 56 | 31 |  |  | 43559.1458 | 42 | 40
2019-04-04 04:00 | 57 | 32 |  |  | 43559.1667 | 43 | 40
2019-04-04 04:30 | 58 | 33 |  |  | 43559.1875 | 44 | 42
2019-04-04 05:00 | 59 | 37 |  |  | 43559.2083 | 48 | 46
2019-04-04 05:30 | 61 | 41 |  |  | 43559.2292 | 52 | 51
2019-04-04 06:00 | 62 | 44 |  |  | 43559.25 | 56 | 55
2019-04-04 06:30 | 62 | 45 |  |  | 43559.2708 | 60 | 60
2019-04-04 07:00 | 62 | 47 |  |  | 43559.2917 | 65 | 65
2019-04-04 07:30 | 60 | 47 |  |  | 43559.3125 | 67 | 67
2019-04-04 08:00 | 60 | 48 |  |  | 43559.3333 | 70 | 70
2019-04-04 08:30 | 60 | 50 |  |  | 43559.3542 | 74 | 73
2019-04-04 09:00 | 60 | 49 |  |  | 43559.375 | 72 | 72
2019-04-04 09:30 | 61 | 50 |  |  | 43559.3958 | 75 | 75
2019-04-04 10:00 | 60 | 47 |  |  | 43559.4167 | 74 | 74
2019-04-04 10:30 | 58 | 45 |  |  | 43559.4375 | 70 | 70
2019-04-04 11:00 | 59 | 46 |  |  | 43559.4583 | 70 | 70
2019-04-04 11:30 | 57 | 44 |  |  | 43559.4792 | 68 | 68
2019-04-04 12:00 | 56 | 43 |  |  | 43559.5 | 68 | 68
2019-04-04 12:30 | 56 | 44 |  |  | 43559.5208 | 69 | 69
2019-04-04 13:00 | 56 | 44 |  |  | 43559.5417 | 68 | 68
2019-04-04 13:30 | 58 | 47 |  |  | 43559.5625 | 69 | 69
2019-04-04 14:00 | 60 | 47 |  |  | 43559.5833 | 69 | 68
2019-04-04 14:30 | 62 | 49 |  |  | 43559.6042 | 70 | 70
2019-04-04 15:00 | 62 | 49 |  |  | 43559.625 | 70 | 70
2019-04-04 15:30 | 63 | 50 |  |  | 43559.6458 | 71 | 71
2019-04-04 16:00 | 66 | 54 |  |  | 43559.6667 | 74 | 74
2019-04-04 16:30 | 71 | 56 |  |  | 43559.6875 | 75 | 75
2019-04-04 17:00 | 72 | 57 |  |  | 43559.7083 | 74 | 74
2019-04-04 17:30 | 72 | 57 |  |  | 43559.7292 | 74 | 73
2019-04-04 18:00 | 71 | 56 |  |  | 43559.75 | 72 | 72
2019-04-04 18:30 | 71 | 57 |  |  | 43559.7708 | 71 | 70
2019-04-04 19:00 | 73 | 58 |  |  | 43559.7917 | 72 | 71
2019-04-04 19:30 | 69 | 56 |  |  | 43559.8125 | 69 | 68
2019-04-04 20:00 | 69 | 56 |  |  | 43559.8333 | 67 | 66
2019-04-04 20:30 | 70 | 58 |  |  | 43559.8542 | 69 | 69
2019-04-04 21:00 | 67 | 57 |  |  | 43559.875 | 69 | 69
2019-04-04 21:30 | 67 | 55 |  |  | 43559.8958 | 66 | 66
2019-04-04 22:00 | 64 | 52 |  |  | 43559.9167 | 65 | 65
2019-04-04 22:30 | 61 | 46 |  |  | 43559.9375 | 60 | 60
2019-04-04 23:00 | 59 | 44 |  |  | 43559.9583 | 56 | 56
2019-04-04 23:30 | 58 | 42 |  |  | 43559.9792 | 54 | 54
2019-04-05 | 56 | 38 |  |  | 43560 | 50 | 50
2019-04-05 00:30 | 54 | 34 |  |  | 43560.0208 | 45 | 44
2019-04-05 01:00 | 54 | 32 |  |  | 43560.0417 | 42 | 41
2019-04-05 01:30 | 55 | 34 |  |  | 43560.0625 | 42 | 42
2019-04-05 02:00 | 55 | 35 |  |  | 43560.0833 | 43 | 42
2019-04-05 02:30 | 55 | 34 |  |  | 43560.1042 | 43 | 43
2019-04-05 03:00 | 55 | 33 |  |  | 43560.125 | 42 | 41
2019-04-05 03:30 | 55 | 34 |  |  | 43560.1458 | 43 | 42
2019-04-05 04:00 | 55 | 34 |  |  | 43560.1667 | 43 | 42
2019-04-05 04:30 | 55 | 34 |  |  | 43560.1875 | 44 | 44
2019-04-05 05:00 | 57 | 37 |  |  | 43560.2083 | 46 | 46
2019-04-05 05:30 | 59 | 41 |  |  | 43560.2292 | 51 | 51
2019-04-05 06:00 | 61 | 46 |  |  | 43560.25 | 57 | 56
2019-04-05 06:30 | 60 | 47 |  |  | 43560.2708 | 61 | 61
2019-04-05 07:00 | 59 | 47 |  |  | 43560.2917 | 65 | 65
2019-04-05 07:30 | 60 | 50 |  |  | 43560.3125 | 69 | 69
2019-04-05 08:00 | 60 | 50 |  |  | 43560.3333 | 72 | 71
2019-04-05 08:30 | 57 | 47 |  |  | 43560.3542 | 70 | 70
2019-04-05 09:00 | 56 | 47 |  |  | 43560.375 | 70 | 70
2019-04-05 09:30 | 56 | 48 |  |  | 43560.3958 | 71 | 70
2019-04-05 10:00 | 54 | 46 |  |  | 43560.4167 | 70 | 69
2019-04-05 10:30 | 55 | 47 |  |  | 43560.4375 | 70 | 69
2019-04-05 11:00 | 55 | 46 |  |  | 43560.4583 | 67 | 66
2019-04-05 11:30 | 55 | 46 |  |  | 43560.4792 | 65 | 65
2019-04-05 12:00 | 54 | 45 |  |  | 43560.5 | 68 | 67
2019-04-05 12:30 | 54 | 45 |  |  | 43560.5208 | 69 | 68
2019-04-05 13:00 | 54 | 45 |  |  | 43560.5417 | 67 | 66
2019-04-05 13:30 | 53 | 43 |  |  | 43560.5625 | 64 | 64
2019-04-05 14:00 | 53 | 44 |  |  | 43560.5833 | 65 | 64
2019-04-05 14:30 | 53 | 45 |  |  | 43560.6042 | 64 | 63
2019-04-05 15:00 | 53 | 45 |  |  | 43560.625 | 65 | 64
2019-04-05 15:30 | 59 | 50 |  |  | 43560.6458 | 69 | 68
2019-04-05 16:00 | 61 | 51 |  |  | 43560.6667 | 67 | 67
2019-04-05 16:30 | 66 | 53 |  |  | 43560.6875 | 70 | 70
2019-04-05 17:00 | 69 | 56 |  |  | 43560.7083 | 72 | 71
2019-04-05 17:30 | 70 | 57 |  |  | 43560.7292 | 73 | 73
2019-04-05 18:00 | 70 | 58 |  |  | 43560.75 | 72 | 72
2019-04-05 18:30 | 70 | 58 |  |  | 43560.7708 | 71 | 71
2019-04-05 19:00 | 71 | 59 |  |  | 43560.7917 | 72 | 71
2019-04-05 19:30 | 68 | 56 |  |  | 43560.8125 | 70 | 69
2019-04-05 20:00 | 66 | 56 |  |  | 43560.8333 | 68 | 68
2019-04-05 20:30 | 64 | 54 |  |  | 43560.8542 | 66 | 66
2019-04-05 21:00 | 62 | 52 |  |  | 43560.875 | 64 | 64
2019-04-05 21:30 | 62 | 50 |  |  | 43560.8958 | 62 | 61
2019-04-05 22:00 | 63 | 51 |  |  | 43560.9167 | 63 | 63
2019-04-05 22:30 | 64 | 51 |  |  | 43560.9375 | 64 | 64
2019-04-05 23:00 | 63 | 48 |  |  | 43560.9583 | 60 | 60
2019-04-05 23:30 | 59 | 43 |  |  | 43560.9792 | 55 | 55
2019-04-06 | 58 | 40 |  |  | 43561 | 53 | 52
2019-04-06 00:30 | 58 | 38 |  |  | 43561.0208 | 50 | 49
2019-04-06 01:00 | 58 | 36 |  |  | 43561.0417 | 47 | 45
2019-04-06 01:30 | 59 | 37 |  |  | 43561.0625 | 48 | 47
2019-04-06 02:00 | 59 | 36 |  |  | 43561.0833 | 46 | 44
2019-04-06 02:30 | 60 | 37 |  |  | 43561.1042 | 48 | 46
2019-04-06 03:00 | 63 | 39 |  |  | 43561.125 | 50 | 48
2019-04-06 03:30 | 63 | 40 |  |  | 43561.1458 | 51 | 49
2019-04-06 04:00 | 59 | 40 |  |  | 43561.1667 | 49 | 49
2019-04-06 04:30 | 60 | 40 |  |  | 43561.1875 | 50 | 49
2019-04-06 05:00 | 61 | 41 |  |  | 43561.2083 | 50 | 50
2019-04-06 05:30 | 58 | 38 |  |  | 43561.2292 | 48 | 47
2019-04-06 06:00 | 54 | 36 |  |  | 43561.25 | 48 | 47
2019-04-06 06:30 | 49 | 35 |  |  | 43561.2708 | 51 | 48
2019-04-06 07:00 | 50 | 36 |  |  | 43561.2917 | 52 | 48
2019-04-06 07:30 | 48 | 34 |  |  | 43561.3125 | 51 | 48
2019-04-06 08:00 | 46 | 34 |  |  | 43561.3333 | 50 | 47
2019-04-06 08:30 | 45 | 33 |  |  | 43561.3542 | 51 | 49
2019-04-06 09:00 | 46 | 35 |  |  | 43561.375 | 53 | 50
2019-04-06 09:30 | 46 | 35 |  |  | 43561.3958 | 54 | 51
2019-04-06 10:00 | 48 | 37 |  |  | 43561.4167 | 57 | 55
2019-04-06 10:30 | 49 | 39 |  |  | 43561.4375 | 57 | 55
2019-04-06 11:00 | 53 | 41 |  |  | 43561.4583 | 59 | 55
2019-04-06 11:30 | 54 | 41 |  |  | 43561.4792 | 58 | 54
2019-04-06 12:00 | 52 | 40 |  |  | 43561.5 | 56 | 53
2019-04-06 12:30 | 52 | 42 |  |  | 43561.5208 | 57 | 54
2019-04-06 13:00 | 53 | 42 |  |  | 43561.5417 | 58 | 55
2019-04-06 13:30 | 55 | 45 |  |  | 43561.5625 | 59 | 56
2019-04-06 14:00 | 55 | 44 |  |  | 43561.5833 | 58 | 56
2019-04-06 14:30 | 55 | 44 |  |  | 43561.6042 | 57 | 55
2019-04-06 15:00 | 56 | 46 |  |  | 43561.625 | 59 | 57
2019-04-06 15:30 | 53 | 42 |  |  | 43561.6458 | 55 | 52
2019-04-06 16:00 | 54 | 41 |  |  | 43561.6667 | 54 | 52
2019-04-06 16:30 | 59 | 42 |  |  | 43561.6875 | 54 | 54
2019-04-06 17:00 | 62 | 45 |  |  | 43561.7083 | 57 | 56
2019-04-06 17:30 | 64 | 48 |  |  | 43561.7292 | 61 | 61
2019-04-06 18:00 | 66 | 50 |  |  | 43561.75 | 64 | 63
2019-04-06 18:30 | 69 | 54 |  |  | 43561.7708 | 68 | 67
2019-04-06 19:00 | 69 | 54 |  |  | 43561.7917 | 68 | 67
2019-04-06 19:30 | 68 | 53 |  |  | 43561.8125 | 66 | 65
2019-04-06 20:00 | 67 | 51 |  |  | 43561.8333 | 65 | 64
2019-04-06 20:30 | 66 | 51 |  |  | 43561.8542 | 65 | 64
2019-04-06 21:00 | 66 | 50 |  |  | 43561.875 | 63 | 62
2019-04-06 21:30 | 65 | 48 |  |  | 43561.8958 | 62 | 61
2019-04-06 22:00 | 65 | 46 |  |  | 43561.9167 | 60 | 60
2019-04-06 22:30 | 63 | 44 |  |  | 43561.9375 | 58 | 57
2019-04-06 23:00 | 56 | 43 |  |  | 43561.9583 | 57 | 54
2019-04-06 23:30 | 56 | 43 |  |  | 43561.9792 | 59 | 55
2019-04-07 | 56 | 43 |  |  | 43562 | 59 | 54
2019-04-07 00:30 | 54 | 40 |  |  | 43562.0208 | 56 | 51
2019-04-07 01:00 | 50 | 35 |  |  | 43562.0417 | 50 | 44
2019-04-07 01:30 | 43 | 33 |  |  | 43562.0625 | 52 | 41
2019-04-07 02:00 | 40 | 31 |  |  | 43562.0833 | 52 | 39
2019-04-07 02:30 | 40 | 32 |  |  | 43562.1042 | 52 | 40
2019-04-07 03:00 | 39 | 32 |  |  | 43562.125 | 50 | 40
2019-04-07 03:30 | 37 | 30 |  |  | 43562.1458 | 49 | 38
2019-04-07 04:00 | 37 | 29 |  |  | 43562.1667 | 49 | 38
2019-04-07 04:30 | 38 | 30 |  |  | 43562.1875 | 49 | 39
2019-04-07 05:00 | 39 | 32 |  |  | 43562.2083 | 50 | 39
2019-04-07 05:30 | 39 | 32 |  |  | 43562.2292 | 51 | 40
2019-04-07 06:00 | 39 | 32 |  |  | 43562.25 | 51 | 40
2019-04-07 06:30 | 40 | 32 |  |  | 43562.2708 | 51 | 41
2019-04-07 07:00 | 39 | 31 |  |  | 43562.2917 | 52 | 42
2019-04-07 07:30 | 38 | 30 |  |  | 43562.3125 | 52 | 42
2019-04-07 08:00 | 36 | 27 |  |  | 43562.3333 | 51 | 39
2019-04-07 08:30 | 36 | 27 |  |  | 43562.3542 | 50 | 39
2019-04-07 09:00 | 35 | 27 |  |  | 43562.375 | 50 | 40
2019-04-07 09:30 | 32 | 25 |  |  | 43562.3958 | 47 | 37
2019-04-07 10:00 | 34 | 27 |  |  | 43562.4167 | 47 | 39
2019-04-07 10:30 | 36 | 30 |  |  | 43562.4375 | 49 | 42
2019-04-07 11:00 | 37 | 31 |  |  | 43562.4583 | 50 | 43
2019-04-07 11:30 | 38 | 33 |  |  | 43562.4792 | 51 | 43
2019-04-07 12:00 | 38 | 33 |  |  | 43562.5 | 51 | 43
2019-04-07 12:30 | 40 | 35 |  |  | 43562.5208 | 51 | 44
2019-04-07 13:00 | 39 | 35 |  |  | 43562.5417 | 51 | 43
2019-04-07 13:30 | 43 | 39 |  |  | 43562.5625 | 52 | 45
2019-04-07 14:00 | 42 | 38 |  |  | 43562.5833 | 51 | 44
2019-04-07 14:30 | 45 | 42 |  |  | 43562.6042 | 52 | 45
2019-04-07 15:00 | 47 | 43 |  |  | 43562.625 | 54 | 47
2019-04-07 15:30 | 48 | 44 |  |  | 43562.6458 | 58 | 51
2019-04-07 16:00 | 49 | 44 |  |  | 43562.6667 | 59 | 52
2019-04-07 16:30 | 49 | 45 |  |  | 43562.6875 | 61 | 53
2019-04-07 17:00 | 51 | 47 |  |  | 43562.7083 | 62 | 55
2019-04-07 17:30 | 53 | 49 |  |  | 43562.7292 | 65 | 58
2019-04-07 18:00 | 52 | 48 |  |  | 43562.75 | 65 | 58
2019-04-07 18:30 | 54 | 50 |  |  | 43562.7708 | 66 | 60
2019-04-07 19:00 | 52 | 48 |  |  | 43562.7917 | 66 | 59
2019-04-07 19:30 | 51 | 47 |  |  | 43562.8125 | 64 | 57
2019-04-07 20:00 | 50 | 46 |  |  | 43562.8333 | 63 | 56
2019-04-07 20:30 | 49 | 45 |  |  | 43562.8542 | 62 | 55
2019-04-07 21:00 | 47 | 43 |  |  | 43562.875 | 59 | 51
2019-04-07 21:30 | 45 | 40 |  |  | 43562.8958 | 57 | 50
2019-04-07 22:00 | 46 | 41 |  |  | 43562.9167 | 59 | 51
2019-04-07 22:30 | 47 | 42 |  |  | 43562.9375 | 60 | 52
2019-04-07 23:00 | 49 | 43 |  |  | 43562.9583 | 60 | 52
2019-04-07 23:30 | 48 | 42 |  |  | 43562.9792 | 59 | 50
2019-04-08 | 46 | 40 |  |  | 43563 | 58 | 48
2019-04-08 00:30 | 44 | 36 |  |  | 43563.0208 | 56 | 44
2019-04-08 01:00 | 42 | 34 |  |  | 43563.0417 | 53 | 41
2019-04-08 01:30 | 40 | 31 |  |  | 43563.0625 | 51 | 38
2019-04-08 02:00 | 39 | 30 |  |  | 43563.0833 | 50 | 37
2019-04-08 02:30 | 40 | 31 |  |  | 43563.1042 | 50 | 37
2019-04-08 03:00 | 40 | 32 |  |  | 43563.125 | 51 | 39
2019-04-08 03:30 | 39 | 30 |  |  | 43563.1458 | 50 | 38
2019-04-08 04:00 | 37 | 28 |  |  | 43563.1667 | 49 | 35
2019-04-08 04:30 | 39 | 31 |  |  | 43563.1875 | 51 | 38
2019-04-08 05:00 | 43 | 36 |  |  | 43563.2083 | 54 | 43
2019-04-08 05:30 | 47 | 41 |  |  | 43563.2292 | 57 | 48
2019-04-08 06:00 | 48 | 44 |  |  | 43563.25 | 59 | 51
2019-04-08 06:30 | 49 | 46 |  |  | 43563.2708 | 62 | 57
2019-04-08 07:00 | 47 | 45 |  |  | 43563.2917 | 62 | 59
2019-04-08 07:30 | 48 | 47 |  |  | 43563.3125 | 67 | 64
2019-04-08 08:00 | 48 | 46 |  |  | 43563.3333 | 68 | 65
2019-04-08 08:30 | 50 | 48 |  |  | 43563.3542 | 72 | 70
2019-04-08 09:00 | 52 | 50 |  |  | 43563.375 | 74 | 72
2019-04-08 09:30 | 53 | 52 |  |  | 43563.3958 | 77 | 75
2019-04-08 10:00 | 52 | 51 |  |  | 43563.4167 | 78 | 75
2019-04-08 10:30 | 54 | 51 |  |  | 43563.4375 | 79 | 74
2019-04-08 11:00 | 54 | 52 |  |  | 43563.4583 | 77 | 72
2019-04-08 11:30 | 53 | 51 |  |  | 43563.4792 | 75 | 70
2019-04-08 12:00 | 51 | 49 |  |  | 43563.5 | 73 | 69
2019-04-08 12:30 | 52 | 50 |  |  | 43563.5208 | 75 | 69
2019-04-08 13:00 | 54 | 51 |  |  | 43563.5417 | 75 | 69
2019-04-08 13:30 | 55 | 53 |  |  | 43563.5625 | 75 | 70
2019-04-08 14:00 | 57 | 55 |  |  | 43563.5833 | 77 | 72
2019-04-08 14:30 | 59 | 57 |  |  | 43563.6042 | 79 | 74
2019-04-08 15:00 | 62 | 59 |  |  | 43563.625 | 84 | 76
2019-04-08 15:30 | 64 | 61 |  |  | 43563.6458 | 85 | 77
2019-04-08 16:00 | 67 | 63 |  |  | 43563.6667 | 87 | 78
2019-04-08 16:30 | 68 | 64 |  |  | 43563.6875 | 88 | 78
2019-04-08 17:00 | 72 | 67 |  |  | 43563.7083 | 91 | 80
2019-04-08 17:30 | 72 | 67 |  |  | 43563.7292 | 90 | 78
2019-04-08 18:00 | 69 | 64 |  |  | 43563.75 | 86 | 76
2019-04-08 18:30 | 67 | 63 |  |  | 43563.7708 | 84 | 72
2019-04-08 19:00 | 68 | 63 |  |  | 43563.7917 | 84 | 73
2019-04-08 19:30 | 63 | 60 |  |  | 43563.8125 | 77 | 70
2019-04-08 20:00 | 61 | 59 |  |  | 43563.8333 | 72 | 69
2019-04-08 20:30 | 61 | 59 |  |  | 43563.8542 | 71 | 69
2019-04-08 21:00 | 57 | 56 |  |  | 43563.875 | 66 | 65
2019-04-08 21:30 | 53 | 53 |  |  | 43563.8958 | 62 | 61
2019-04-08 22:00 | 51 | 50 |  |  | 43563.9167 | 61 | 60
2019-04-08 22:30 | 47 | 46 |  |  | 43563.9375 | 58 | 57
2019-04-08 23:00 | 47 | 46 |  |  | 43563.9583 | 56 | 55
2019-04-08 23:30 | 44 | 42 |  |  | 43563.9792 | 53 | 51
2019-04-09 | 41 | 39 |  |  | 43564 | 50 | 48
2019-04-09 00:30 | 40 | 38 |  |  | 43564.0208 | 46 | 44
2019-04-09 01:00 | 38 | 35 |  |  | 43564.0417 | 43 | 41
2019-04-09 01:30 | 36 | 33 |  |  | 43564.0625 | 42 | 39
2019-04-09 02:00 | 36 | 33 |  |  | 43564.0833 | 42 | 39
2019-04-09 02:30 | 37 | 35 |  |  | 43564.1042 | 43 | 40
2019-04-09 03:00 | 39 | 36 |  |  | 43564.125 | 44 | 40
2019-04-09 03:30 | 37 | 34 |  |  | 43564.1458 | 42 | 39
2019-04-09 04:00 | 37 | 34 |  |  | 43564.1667 | 42 | 38
2019-04-09 04:30 | 37 | 34 |  |  | 43564.1875 | 43 | 39
2019-04-09 05:00 | 41 | 38 |  |  | 43564.2083 | 46 | 43
2019-04-09 05:30 | 44 | 42 |  |  | 43564.2292 | 50 | 48
2019-04-09 06:00 | 46 | 45 |  |  | 43564.25 | 54 | 52
2019-04-09 06:30 | 50 | 49 |  |  | 43564.2708 | 62 | 61
2019-04-09 07:00 | 51 | 50 |  |  | 43564.2917 | 66 | 66
2019-04-09 07:30 | 54 | 53 |  |  | 43564.3125 | 73 | 72
2019-04-09 08:00 | 58 | 57 |  |  | 43564.3333 | 79 | 77
2019-04-09 08:30 | 56 | 56 |  |  | 43564.3542 | 77 | 76
2019-04-09 09:00 | 55 | 52 |  |  | 43564.375 | 81 | 73
2019-04-09 09:30 | 50 | 46 |  |  | 43564.3958 | 77 | 68
2019-04-09 10:00 | 52 | 49 |  |  | 43564.4167 | 76 | 69
2019-04-09 10:30 | 49 | 48 |  |  | 43564.4375 | 71 | 69
2019-04-09 11:00 | 50 | 50 |  |  | 43564.4583 | 71 | 70
2019-04-09 11:30 | 47 | 47 |  |  | 43564.4792 | 69 | 68
2019-04-09 12:00 | 48 | 48 |  |  | 43564.5 | 69 | 69
2019-04-09 12:30 | 50 | 49 |  |  | 43564.5208 | 71 | 71
2019-04-09 13:00 | 49 | 49 |  |  | 43564.5417 | 70 | 70
2019-04-09 13:30 | 53 | 53 |  |  | 43564.5625 | 74 | 74
2019-04-09 14:00 | 56 | 55 |  |  | 43564.5833 | 76 | 75
2019-04-09 14:30 | 58 | 58 |  |  | 43564.6042 | 83 | 82
2019-04-09 15:00 | 61 | 60 |  |  | 43564.625 | 82 | 80
2019-04-09 15:30 | 63 | 63 |  |  | 43564.6458 | 87 | 84
2019-04-09 16:00 | 64 | 64 |  |  | 43564.6667 | 86 | 83
2019-04-09 16:30 | 62 | 62 |  |  | 43564.6875 | 84 | 81
2019-04-09 17:00 | 66 | 66 |  |  | 43564.7083 | 87 | 83
2019-04-09 17:30 | 68 | 68 |  |  | 43564.7292 | 89 | 84
2019-04-09 18:00 | 66 | 66 |  |  | 43564.75 | 87 | 81
2019-04-09 18:30 | 67 | 67 |  |  | 43564.7708 | 87 | 81
2019-04-09 19:00 | 68 | 68 |  |  | 43564.7917 | 86 | 81
2019-04-09 19:30 | 65 | 65 |  |  | 43564.8125 | 82 | 77
2019-04-09 20:00 | 64 | 63 |  |  | 43564.8333 | 80 | 75
2019-04-09 20:30 | 61 | 61 |  |  | 43564.8542 | 78 | 74
2019-04-09 21:00 | 60 | 60 |  |  | 43564.875 | 73 | 72
2019-04-09 21:30 | 60 | 60 |  |  | 43564.8958 | 72 | 71
2019-04-09 22:00 | 60 | 60 |  |  | 43564.9167 | 72 | 71
2019-04-09 22:30 | 54 | 54 |  |  | 43564.9375 | 69 | 67
2019-04-09 23:00 | 54 | 54 |  |  | 43564.9583 | 67 | 65
2019-04-09 23:30 | 50 | 50 |  |  | 43564.9792 | 64 | 62
2019-04-10 | 46 | 46 |  |  | 43565 | 60 | 58
2019-04-10 00:30 | 43 | 43 |  |  | 43565.0208 | 56 | 53
2019-04-10 01:00 | 40 | 40 |  |  | 43565.0417 | 53 | 50
2019-04-10 01:30 | 38 | 38 |  |  | 43565.0625 | 50 | 46
2019-04-10 02:00 | 35 | 35 |  |  | 43565.0833 | 47 | 44
2019-04-10 02:30 | 36 | 36 |  |  | 43565.1042 | 47 | 44
2019-04-10 03:00 | 34 | 34 |  |  | 43565.125 | 46 | 42
2019-04-10 03:30 | 32 | 32 |  |  | 43565.1458 | 44 | 40
2019-04-10 04:00 | 32 | 32 |  |  | 43565.1667 | 44 | 40
2019-04-10 04:30 | 36 | 36 |  |  | 43565.1875 | 48 | 44
2019-04-10 05:00 | 41 | 41 |  |  | 43565.2083 | 53 | 49
2019-04-10 05:30 | 45 | 45 |  |  | 43565.2292 | 57 | 54
2019-04-10 06:00 | 50 | 50 |  |  | 43565.25 | 62 | 60
2019-04-10 06:30 | 55 | 55 |  |  | 43565.2708 | 69 | 68
2019-04-10 07:00 | 54 | 54 |  |  | 43565.2917 | 72 | 71
2019-04-10 07:30 | 56 | 56 |  |  | 43565.3125 | 75 | 74
2019-04-10 08:00 | 58 | 58 |  |  | 43565.3333 | 78 | 77
2019-04-10 08:30 | 57 | 56 |  |  | 43565.3542 | 77 | 76
2019-04-10 09:00 | 57 | 56 |  |  | 43565.375 | 76 | 76
2019-04-10 09:30 | 55 | 54 |  |  | 43565.3958 | 76 | 76
2019-04-10 10:00 | 56 | 56 |  |  | 43565.4167 | 81 | 78
2019-04-10 10:30 | 60 | 60 |  |  | 43565.4375 | 84 | 79
2019-04-10 11:00 | 61 | 61 |  |  | 43565.4583 | 85 | 81
2019-04-10 11:30 | 59 | 59 |  |  | 43565.4792 | 81 | 76
2019-04-10 12:00 | 57 | 57 |  |  | 43565.5 | 77 | 72
2019-04-10 12:30 | 56 | 56 |  |  | 43565.5208 | 81 | 76
2019-04-10 13:00 | 61 | 61 |  |  | 43565.5417 | 79 | 74
2019-04-10 13:30 | 67 | 67 |  |  | 43565.5625 | 85 | 80
2019-04-10 14:00 | 66 | 65 |  |  | 43565.5833 | 87 | 82
2019-04-10 14:30 | 68 | 68 |  |  | 43565.6042 | 85 | 80
2019-04-10 15:00 | 67 | 67 |  |  | 43565.625 | 89 | 84
2019-04-10 15:30 | 60 | 60 |  |  | 43565.6458 | 85 | 80
2019-04-10 16:00 | 61 | 61 |  |  | 43565.6667 | 87 | 82
2019-04-10 16:30 | 61 | 61 |  |  | 43565.6875 | 86 | 80
2019-04-10 17:00 | 61 | 61 |  |  | 43565.7083 | 86 | 79
2019-04-10 17:30 | 62 | 62 |  |  | 43565.7292 | 87 | 78
2019-04-10 18:00 | 61 | 61 |  |  | 43565.75 | 85 | 76
2019-04-10 18:30 | 59 | 59 |  |  | 43565.7708 | 79 | 73
2019-04-10 19:00 | 61 | 61 |  |  | 43565.7917 | 80 | 74
2019-04-10 19:30 | 61 | 60 |  |  | 43565.8125 | 80 | 74
2019-04-10 20:00 | 59 | 59 |  |  | 43565.8333 | 76 | 71
2019-04-10 20:30 | 59 | 59 |  |  | 43565.8542 | 76 | 71
2019-04-10 21:00 | 59 | 59 |  |  | 43565.875 | 76 | 71
2019-04-10 21:30 | 59 | 59 |  |  | 43565.8958 | 75 | 69
2019-04-10 22:00 | 58 | 58 |  |  | 43565.9167 | 71 | 68
2019-04-10 22:30 | 53 | 53 |  |  | 43565.9375 | 66 | 64
2019-04-10 23:00 | 52 | 52 |  |  | 43565.9583 | 64 | 62
2019-04-10 23:30 | 51 | 51 |  |  | 43565.9792 | 64 | 61
2019-04-11 | 47 | 47 |  |  | 43566 | 61 | 57
2019-04-11 00:30 | 45 | 44 |  |  | 43566.0208 | 57 | 54
2019-04-11 01:00 | 43 | 42 |  |  | 43566.0417 | 54 | 50
2019-04-11 01:30 | 40 | 40 |  |  | 43566.0625 | 52 | 49
2019-04-11 02:00 | 39 | 39 |  |  | 43566.0833 | 51 | 47
2019-04-11 02:30 | 38 | 37 |  |  | 43566.1042 | 50 | 46
2019-04-11 03:00 | 37 | 36 |  |  | 43566.125 | 48 | 44
2019-04-11 03:30 | 37 | 36 |  |  | 43566.1458 | 48 | 44
2019-04-11 04:00 | 36 | 36 |  |  | 43566.1667 | 47 | 43
2019-04-11 04:30 | 38 | 38 |  |  | 43566.1875 | 50 | 46
2019-04-11 05:00 | 41 | 40 |  |  | 43566.2083 | 51 | 48
2019-04-11 05:30 | 45 | 45 |  |  | 43566.2292 | 55 | 52
2019-04-11 06:00 | 48 | 48 |  |  | 43566.25 | 59 | 57
2019-04-11 06:30 | 54 | 54 |  |  | 43566.2708 | 67 | 66
2019-04-11 07:00 | 57 | 57 |  |  | 43566.2917 | 73 | 72
2019-04-11 07:30 | 59 | 59 |  |  | 43566.3125 | 77 | 76
2019-04-11 08:00 | 57 | 57 |  |  | 43566.3333 | 77 | 77
2019-04-11 08:30 | 59 | 58 |  |  | 43566.3542 | 79 | 79
2019-04-11 09:00 | 55 | 54 |  |  | 43566.375 | 76 | 76
2019-04-11 09:30 | 54 | 53 |  |  | 43566.3958 | 76 | 76
2019-04-11 10:00 | 58 | 57 |  |  | 43566.4167 | 82 | 81
2019-04-11 10:30 | 63 | 63 |  |  | 43566.4375 | 87 | 85
2019-04-11 11:00 | 67 | 67 |  |  | 43566.4583 | 81 | 80
2019-04-11 11:30 | 54 | 54 |  |  | 43566.4792 | 73 | 71
2019-04-11 12:00 | 54 | 54 |  |  | 43566.5 | 77 | 76
2019-04-11 12:30 | 56 | 56 |  |  | 43566.5208 | 75 | 73
2019-04-11 13:00 | 55 | 55 |  |  | 43566.5417 | 74 | 72
2019-04-11 13:30 | 55 | 55 |  |  | 43566.5625 | 79 | 77
2019-04-11 14:00 | 57 | 56 |  |  | 43566.5833 | 76 | 74
2019-04-11 14:30 | 52 | 52 |  |  | 43566.6042 | 72 | 71
2019-04-11 15:00 | 55 | 55 |  |  | 43566.625 | 77 | 76
2019-04-11 15:30 | 55 | 55 |  |  | 43566.6458 | 76 | 74
2019-04-11 16:00 | 59 | 59 |  |  | 43566.6667 | 77 | 75
2019-04-11 16:30 | 60 | 60 |  |  | 43566.6875 | 78 | 76
2019-04-11 17:00 | 62 | 62 |  |  | 43566.7083 | 82 | 80
2019-04-11 17:30 | 62 | 62 |  |  | 43566.7292 | 81 | 78
2019-04-11 18:00 | 62 | 62 |  |  | 43566.75 | 81 | 77
2019-04-11 18:30 | 61 | 61 |  |  | 43566.7708 | 81 | 74
2019-04-11 19:00 | 61 | 61 |  |  | 43566.7917 | 82 | 75
2019-04-11 19:30 | 61 | 61 |  |  | 43566.8125 | 80 | 74
2019-04-11 20:00 | 62 | 62 |  |  | 43566.8333 | 75 | 74
2019-04-11 20:30 | 60 | 59 |  |  | 43566.8542 | 72 | 71
2019-04-11 21:00 | 57 | 56 |  |  | 43566.875 | 69 | 69
2019-04-11 21:30 | 55 | 54 |  |  | 43566.8958 | 66 | 65
2019-04-11 22:00 | 50 | 49 |  |  | 43566.9167 | 61 | 61
2019-04-11 22:30 | 48 | 46 |  |  | 43566.9375 | 60 | 59
2019-04-11 23:00 | 45 | 44 |  |  | 43566.9583 | 56 | 56
2019-04-11 23:30 | 41 | 40 |  |  | 43566.9792 | 52 | 52
2019-04-12 | 40 | 39 |  |  | 43567 | 52 | 51
2019-04-12 00:30 | 39 | 38 |  |  | 43567.0208 | 49 | 48
2019-04-12 01:00 | 37 | 36 |  |  | 43567.0417 | 46 | 45
2019-04-12 01:30 | 36 | 35 |  |  | 43567.0625 | 44 | 44
2019-04-12 02:00 | 36 | 35 |  |  | 43567.0833 | 44 | 44
2019-04-12 02:30 | 35 | 34 |  |  | 43567.1042 | 43 | 42
2019-04-12 03:00 | 34 | 33 |  |  | 43567.125 | 42 | 41
2019-04-12 03:30 | 34 | 33 |  |  | 43567.1458 | 43 | 42
2019-04-12 04:00 | 34 | 33 |  |  | 43567.1667 | 41 | 41
2019-04-12 04:30 | 35 | 34 |  |  | 43567.1875 | 42 | 42
2019-04-12 05:00 | 39 | 39 |  |  | 43567.2083 | 46 | 45
2019-04-12 05:30 | 42 | 42 |  |  | 43567.2292 | 50 | 49
2019-04-12 06:00 | 46 | 44 |  |  | 43567.25 | 54 | 54
2019-04-12 06:30 | 48 | 47 |  |  | 43567.2708 | 59 | 59
2019-04-12 07:00 | 50 | 49 |  |  | 43567.2917 | 65 | 65
2019-04-12 07:30 | 50 | 49 |  |  | 43567.3125 | 67 | 67
2019-04-12 08:00 | 48 | 48 |  |  | 43567.3333 | 72 | 68
2019-04-12 08:30 | 49 | 49 |  |  | 43567.3542 | 72 | 70
2019-04-12 09:00 | 50 | 50 |  |  | 43567.375 | 71 | 69
2019-04-12 09:30 | 45 | 45 |  |  | 43567.3958 | 68 | 66
2019-04-12 10:00 | 45 | 45 |  |  | 43567.4167 | 69 | 67
2019-04-12 10:30 | 49 | 49 |  |  | 43567.4375 | 72 | 70
2019-04-12 11:00 | 51 | 50 |  |  | 43567.4583 | 73 | 71
2019-04-12 11:30 | 54 | 53 |  |  | 43567.4792 | 72 | 70
2019-04-12 12:00 | 45 | 45 |  |  | 43567.5 | 68 | 65
2019-04-12 12:30 | 45 | 45 |  |  | 43567.5208 | 68 | 65
2019-04-12 13:00 | 46 | 46 |  |  | 43567.5417 | 65 | 62
2019-04-12 13:30 | 48 | 48 |  |  | 43567.5625 | 67 | 64
2019-04-12 14:00 | 48 | 48 |  |  | 43567.5833 | 71 | 69
2019-04-12 14:30 | 53 | 53 |  |  | 43567.6042 | 73 | 71
2019-04-12 15:00 | 52 | 52 |  |  | 43567.625 | 73 | 70
2019-04-12 15:30 | 51 | 51 |  |  | 43567.6458 | 71 | 68
2019-04-12 16:00 | 52 | 52 |  |  | 43567.6667 | 73 | 70
2019-04-12 16:30 | 52 | 52 |  |  | 43567.6875 | 73 | 70
2019-04-12 17:00 | 55 | 55 |  |  | 43567.7083 | 76 | 72
2019-04-12 17:30 | 58 | 58 |  |  | 43567.7292 | 78 | 74
2019-04-12 18:00 | 58 | 58 |  |  | 43567.75 | 78 | 74
2019-04-12 18:30 | 57 | 57 |  |  | 43567.7708 | 77 | 73
2019-04-12 19:00 | 57 | 57 |  |  | 43567.7917 | 77 | 71
2019-04-12 19:30 | 55 | 55 |  |  | 43567.8125 | 75 | 69
2019-04-12 20:00 | 53 | 52 |  |  | 43567.8333 | 72 | 65
2019-04-12 20:30 | 50 | 50 |  |  | 43567.8542 | 66 | 63
2019-04-12 21:00 | 49 | 48 |  |  | 43567.875 | 60 | 60
2019-04-12 21:30 | 47 | 46 |  |  | 43567.8958 | 59 | 58
2019-04-12 22:00 | 45 | 45 |  |  | 43567.9167 | 59 | 58
2019-04-12 22:30 | 44 | 44 |  |  | 43567.9375 | 58 | 57
2019-04-12 23:00 | 42 | 42 |  |  | 43567.9583 | 54 | 53
2019-04-12 23:30 | 39 | 38 |  |  | 43567.9792 | 50 | 49
2019-04-13 | 35 | 35 |  |  | 43568 | 49 | 47
2019-04-13 00:30 | 35 | 35 |  |  | 43568.0208 | 46 | 45
2019-04-13 01:00 | 35 | 35 |  |  | 43568.0417 | 45 | 44
2019-04-13 01:30 | 34 | 34 |  |  | 43568.0625 | 43 | 42
2019-04-13 02:00 | 32 | 32 |  |  | 43568.0833 | 41 | 40
2019-04-13 02:30 | 31 | 31 |  |  | 43568.1042 | 40 | 39
2019-04-13 03:00 | 29 | 29 |  |  | 43568.125 | 39 | 38
2019-04-13 03:30 | 29 | 29 |  |  | 43568.1458 | 40 | 39
2019-04-13 04:00 | 31 | 30 |  |  | 43568.1667 | 40 | 39
2019-04-13 04:30 | 32 | 32 |  |  | 43568.1875 | 42 | 40
2019-04-13 05:00 | 35 | 35 |  |  | 43568.2083 | 44 | 42
2019-04-13 05:30 | 34 | 34 |  |  | 43568.2292 | 44 | 43
2019-04-13 06:00 | 34 | 34 |  |  | 43568.25 | 44 | 43
2019-04-13 06:30 | 33 | 33 |  |  | 43568.2708 | 45 | 44
2019-04-13 07:00 | 32 | 32 |  |  | 43568.2917 | 45 | 44
2019-04-13 07:30 | 30 | 30 |  |  | 43568.3125 | 44 | 43
2019-04-13 08:00 | 32 | 31 |  |  | 43568.3333 | 45 | 44
2019-04-13 08:30 | 32 | 32 |  |  | 43568.3542 | 45 | 45
2019-04-13 09:00 | 33 | 32 |  |  | 43568.375 | 45 | 45
2019-04-13 09:30 | 33 | 33 |  |  | 43568.3958 | 46 | 46
2019-04-13 10:00 | 34 | 33 |  |  | 43568.4167 | 46 | 46
2019-04-13 10:30 | 35 | 34 |  |  | 43568.4375 | 48 | 48
2019-04-13 11:00 | 36 | 35 |  |  | 43568.4583 | 49 | 49
2019-04-13 11:30 | 38 | 37 |  |  | 43568.4792 | 48 | 48
2019-04-13 12:00 | 34 | 33 |  |  | 43568.5 | 45 | 45
2019-04-13 12:30 | 31 | 31 |  |  | 43568.5208 | 46 | 46
2019-04-13 13:00 | 32 | 31 |  |  | 43568.5417 | 45 | 45
2019-04-13 13:30 | 33 | 32 |  |  | 43568.5625 | 40 | 40
2019-04-13 14:00 | 36 | 35 |  |  | 43568.5833 | 41 | 41
2019-04-13 14:30 | 33 | 32 |  |  | 43568.6042 | 44 | 44
2019-04-13 15:00 | 35 | 34 |  |  | 43568.625 | 45 | 45
2019-04-13 15:30 | 39 | 38 |  |  | 43568.6458 | 47 | 47
2019-04-13 16:00 | 36 | 35 |  |  | 43568.6667 | 48 | 48
2019-04-13 16:30 | 39 | 38 |  |  | 43568.6875 | 53 | 53
2019-04-13 17:00 | 42 | 41 |  |  | 43568.7083 | 56 | 56
2019-04-13 17:30 | 45 | 45 |  |  | 43568.7292 | 59 | 59
2019-04-13 18:00 | 48 | 48 |  |  | 43568.75 | 62 | 62
2019-04-13 18:30 | 51 | 50 |  |  | 43568.7708 | 64 | 64
2019-04-13 19:00 | 50 | 50 |  |  | 43568.7917 | 64 | 64
2019-04-13 19:30 | 49 | 48 |  |  | 43568.8125 | 62 | 62
2019-04-13 20:00 | 46 | 46 |  |  | 43568.8333 | 60 | 60
2019-04-13 20:30 | 45 | 45 |  |  | 43568.8542 | 59 | 59
2019-04-13 21:00 | 42 | 42 |  |  | 43568.875 | 56 | 55
2019-04-13 21:30 | 41 | 41 |  |  | 43568.8958 | 54 | 53
2019-04-13 22:00 | 42 | 42 |  |  | 43568.9167 | 56 | 55
2019-04-13 22:30 | 42 | 42 |  |  | 43568.9375 | 57 | 56
2019-04-13 23:00 | 42 | 42 |  |  | 43568.9583 | 55 | 55
2019-04-13 23:30 | 41 | 41 |  |  | 43568.9792 | 54 | 53
2019-04-14 | 38 | 38 |  |  | 43569 | 58 | 50
2019-04-14 00:30 | 37 | 37 |  |  | 43569.0208 | 60 | 47
2019-04-14 01:00 | 35 | 35 |  |  | 43569.0417 | 57 | 44
2019-04-14 01:30 | 33 | 33 |  |  | 43569.0625 | 55 | 41
2019-04-14 02:00 | 31 | 31 |  |  | 43569.0833 | 55 | 39
2019-04-14 02:30 | 29 | 29 |  |  | 43569.1042 | 54 | 37
2019-04-14 03:00 | 29 | 29 |  |  | 43569.125 | 53 | 37
2019-04-14 03:30 | 30 | 29 |  |  | 43569.1458 | 51 | 38
2019-04-14 04:00 | 29 | 29 |  |  | 43569.1667 | 50 | 37
2019-04-14 04:30 | 28 | 28 |  |  | 43569.1875 | 49 | 36
2019-04-14 05:00 | 31 | 31 |  |  | 43569.2083 | 51 | 38
2019-04-14 05:30 | 33 | 32 |  |  | 43569.2292 | 52 | 40
2019-04-14 06:00 | 32 | 32 |  |  | 43569.25 | 52 | 40
2019-04-14 06:30 | 31 | 30 |  |  | 43569.2708 | 53 | 40
2019-04-14 07:00 | 29 | 29 |  |  | 43569.2917 | 52 | 39
2019-04-14 07:30 | 26 | 25 |  |  | 43569.3125 | 52 | 36
2019-04-14 08:00 | 22 | 22 |  |  | 43569.3333 | 49 | 33
2019-04-14 08:30 | 25 | 24 |  |  | 43569.3542 | 50 | 35
2019-04-14 09:00 | 30 | 29 |  |  | 43569.375 | 51 | 39
2019-04-14 09:30 | 29 | 28 |  |  | 43569.3958 | 52 | 39
2019-04-14 10:00 | 28 | 27 |  |  | 43569.4167 | 51 | 35
2019-04-14 10:30 | 28 | 28 |  |  | 43569.4375 | 52 | 36
2019-04-14 11:00 | 31 | 30 |  |  | 43569.4583 | 54 | 39
2019-04-14 11:30 | 29 | 28 |  |  | 43569.4792 | 51 | 36
2019-04-14 12:00 | 29 | 28 |  |  | 43569.5 | 52 | 39
2019-04-14 12:30 | 28 | 27 |  |  | 43569.5208 | 50 | 35
2019-04-14 13:00 | 29 | 29 |  |  | 43569.5417 | 52 | 38
2019-04-14 13:30 | 27 | 27 |  |  | 43569.5625 | 52 | 37
2019-04-14 14:00 | 28 | 28 |  |  | 43569.5833 | 51 | 35
2019-04-14 14:30 | 29 | 28 |  |  | 43569.6042 | 51 | 35
2019-04-14 15:00 | 27 | 27 |  |  | 43569.625 | 52 | 37
2019-04-14 15:30 | 31 | 30 |  |  | 43569.6458 | 55 | 41
2019-04-14 16:00 | 33 | 32 |  |  | 43569.6667 | 57 | 44
2019-04-14 16:30 | 37 | 36 |  |  | 43569.6875 | 61 | 49
2019-04-14 17:00 | 39 | 39 |  |  | 43569.7083 | 63 | 51
2019-04-14 17:30 | 43 | 42 |  |  | 43569.7292 | 66 | 54
2019-04-14 18:00 | 47 | 46 |  |  | 43569.75 | 69 | 59
2019-04-14 18:30 | 49 | 48 |  |  | 43569.7708 | 71 | 62
2019-04-14 19:00 | 49 | 49 |  |  | 43569.7917 | 71 | 63
2019-04-14 19:30 | 46 | 46 |  |  | 43569.8125 | 69 | 59
2019-04-14 20:00 | 44 | 44 |  |  | 43569.8333 | 66 | 57
2019-04-14 20:30 | 43 | 43 |  |  | 43569.8542 | 65 | 56
2019-04-14 21:00 | 42 | 41 |  |  | 43569.875 | 61 | 52
2019-04-14 21:30 | 39 | 38 |  |  | 43569.8958 | 59 | 50
2019-04-14 22:00 | 37 | 36 |  |  | 43569.9167 | 59 | 50
2019-04-14 22:30 | 38 | 37 |  |  | 43569.9375 | 60 | 51
2019-04-14 23:00 | 36 | 36 |  |  | 43569.9583 | 58 | 48
2019-04-14 23:30 | 35 | 34 |  |  | 43569.9792 | 58 | 47
2019-04-15 | 35 | 34 |  |  | 43570 | 58 | 47
2019-04-15 00:30 | 34 | 34 |  |  | 43570.0208 | 57 | 43
2019-04-15 01:00 | 33 | 32 |  |  | 43570.0417 | 55 | 41
2019-04-15 01:30 | 30 | 29 |  |  | 43570.0625 | 52 | 38
2019-04-15 02:00 | 29 | 28 |  |  | 43570.0833 | 52 | 38
2019-04-15 02:30 | 29 | 28 |  |  | 43570.1042 | 52 | 37
2019-04-15 03:00 | 29 | 28 |  |  | 43570.125 | 51 | 36
2019-04-15 03:30 | 26 | 26 |  |  | 43570.1458 | 51 | 35
2019-04-15 04:00 | 26 | 26 |  |  | 43570.1667 | 50 | 35
2019-04-15 04:30 | 27 | 26 |  |  | 43570.1875 | 51 | 36
2019-04-15 05:00 | 31 | 30 |  |  | 43570.2083 | 54 | 39
2019-04-15 05:30 | 35 | 34 |  |  | 43570.2292 | 56 | 43
2019-04-15 06:00 | 39 | 38 |  |  | 43570.25 | 57 | 47
2019-04-15 06:30 | 44 | 43 |  |  | 43570.2708 | 62 | 54
2019-04-15 07:00 | 46 | 44 |  |  | 43570.2917 | 65 | 59
2019-04-15 07:30 | 45 | 44 |  |  | 43570.3125 | 67 | 61
2019-04-15 08:00 | 46 | 45 |  |  | 43570.3333 | 68 | 63
2019-04-15 08:30 | 47 | 46 |  |  | 43570.3542 | 70 | 66
2019-04-15 09:00 | 42 | 42 |  |  | 43570.375 | 70 | 62
2019-04-15 09:30 | 41 | 40 |  |  | 43570.3958 | 66 | 57
2019-04-15 10:00 | 46 | 44 |  |  | 43570.4167 | 69 | 63
2019-04-15 10:30 | 43 | 42 |  |  | 43570.4375 | 71 | 62
2019-04-15 11:00 | 44 | 43 |  |  | 43570.4583 | 75 | 64
2019-04-15 11:30 | 45 | 44 |  |  | 43570.4792 | 77 | 66
2019-04-15 12:00 | 45 | 45 |  |  | 43570.5 | 75 | 64
2019-04-15 12:30 | 46 | 45 |  |  | 43570.5208 | 77 | 67
2019-04-15 13:00 | 50 | 49 |  |  | 43570.5417 | 80 | 71
2019-04-15 13:30 | 52 | 52 |  |  | 43570.5625 | 83 | 74
2019-04-15 14:00 | 54 | 53 |  |  | 43570.5833 | 82 | 73
2019-04-15 14:30 | 53 | 53 |  |  | 43570.6042 | 73 | 70
2019-04-15 15:00 | 56 | 55 |  |  | 43570.625 | 71 | 71
2019-04-15 15:30 | 58 | 57 |  |  | 43570.6458 | 72 | 72
2019-04-15 16:00 | 61 | 60 |  |  | 43570.6667 | 77 | 77
2019-04-15 16:30 | 59 | 57 |  |  | 43570.6875 | 74 | 74
2019-04-15 17:00 | 60 | 58 |  |  | 43570.7083 | 74 | 73
2019-04-15 17:30 | 60 | 57 |  |  | 43570.7292 | 73 | 72
2019-04-15 18:00 | 64 | 62 |  |  | 43570.75 | 77 | 75
2019-04-15 18:30 | 66 | 63 |  |  | 43570.7708 | 77 | 75
2019-04-15 19:00 | 66 | 63 |  |  | 43570.7917 | 78 | 75
2019-04-15 19:30 | 62 | 60 |  |  | 43570.8125 | 74 | 71
2019-04-15 20:00 | 60 | 58 |  |  | 43570.8333 | 71 | 68
2019-04-15 20:30 | 56 | 54 |  |  | 43570.8542 | 67 | 65
2019-04-15 21:00 | 51 | 49 |  |  | 43570.875 | 61 | 60
2019-04-15 21:30 | 48 | 47 |  |  | 43570.8958 | 58 | 57
2019-04-15 22:00 | 47 | 45 |  |  | 43570.9167 | 57 | 56
2019-04-15 22:30 | 45 | 42 |  |  | 43570.9375 | 56 | 54
2019-04-15 23:00 | 44 | 40 |  |  | 43570.9583 | 53 | 51
2019-04-15 23:30 | 40 | 36 |  |  | 43570.9792 | 49 | 47
2019-04-16 | 38 | 32 |  |  | 43571 | 46 | 43
2019-04-16 00:30 | 38 | 32 |  |  | 43571.0208 | 45 | 42
2019-04-16 01:00 | 39 | 33 |  |  | 43571.0417 | 45 | 41
2019-04-16 01:30 | 38 | 32 |  |  | 43571.0625 | 44 | 40
2019-04-16 02:00 | 37 | 31 |  |  | 43571.0833 | 43 | 39
2019-04-16 02:30 | 37 | 31 |  |  | 43571.1042 | 43 | 39
2019-04-16 03:00 | 38 | 31 |  |  | 43571.125 | 44 | 39
2019-04-16 03:30 | 39 | 32 |  |  | 43571.1458 | 44 | 40
2019-04-16 04:00 | 40 | 33 |  |  | 43571.1667 | 44 | 40
2019-04-16 04:30 | 45 | 34 |  |  | 43571.1875 | 47 | 41
2019-04-16 05:00 | 52 | 36 |  |  | 43571.2083 | 51 | 44
2019-04-16 05:30 | 52 | 38 |  |  | 43571.2292 | 54 | 48
2019-04-16 06:00 | 51 | 40 |  |  | 43571.25 | 54 | 49
2019-04-16 06:30 | 53 | 43 |  |  | 43571.2708 | 59 | 56
2019-04-16 07:00 | 53 | 46 |  |  | 43571.2917 | 62 | 61
2019-04-16 07:30 | 54 | 43 |  |  | 43571.3125 | 61 | 61
2019-04-16 08:00 | 55 | 44 |  |  | 43571.3333 | 64 | 63
2019-04-16 08:30 | 56 | 45 |  |  | 43571.3542 | 64 | 64
2019-04-16 09:00 | 57 | 43 |  |  | 43571.375 | 64 | 63
2019-04-16 09:30 | 67 | 40 |  |  | 43571.3958 | 69 | 63
2019-04-16 10:00 | 76 | 43 |  |  | 43571.4167 | 78 | 67
2019-04-16 10:30 | 86 | 45 |  |  | 43571.4375 | 74 | 71
2019-04-16 11:00 | 89 | 47 |  |  | 43571.4583 | 73 | 71
2019-04-16 11:30 | 91 | 53 |  |  | 43571.4792 | 76 | 74
2019-04-16 12:00 | 90 | 50 |  |  | 43571.5 | 72 | 70
2019-04-16 12:30 | 90 | 47 |  |  | 43571.5208 | 72 | 70
2019-04-16 13:00 | 92 | 53 |  |  | 43571.5417 | 73 | 70
2019-04-16 13:30 | 89 | 46 |  |  | 43571.5625 | 71 | 69
2019-04-16 14:00 | 89 | 46 |  |  | 43571.5833 | 72 | 70
2019-04-16 14:30 | 92 | 54 |  |  | 43571.6042 | 73 | 71
2019-04-16 15:00 | 95 | 58 |  |  | 43571.625 | 77 | 75
2019-04-16 15:30 | 97 | 57 |  |  | 43571.6458 | 78 | 77
2019-04-16 16:00 | 96 | 55 |  |  | 43571.6667 | 77 | 75
2019-04-16 16:30 | 98 | 56 |  |  | 43571.6875 | 77 | 76
2019-04-16 17:00 | 101 | 59 |  |  | 43571.7083 | 78 | 78
2019-04-16 17:30 | 102 | 59 |  |  | 43571.7292 | 77 | 77
2019-04-16 18:00 | 103 | 60 |  |  | 43571.75 | 77 | 77
2019-04-16 18:30 | 105 | 62 |  |  | 43571.7708 | 77 | 77
2019-04-16 19:00 | 105 | 62 |  |  | 43571.7917 | 77 | 77
2019-04-16 19:30 | 96 | 58 |  |  | 43571.8125 | 73 | 73
2019-04-16 20:00 | 93 | 55 |  |  | 43571.8333 | 70 | 69
2019-04-16 20:30 | 88 | 54 |  |  | 43571.8542 | 68 | 68
2019-04-16 21:00 | 79 | 51 |  |  | 43571.875 | 66 | 64
2019-04-16 21:30 | 80 | 50 |  |  | 43571.8958 | 64 | 62
2019-04-16 22:00 | 80 | 48 |  |  | 43571.9167 | 63 | 62
2019-04-16 22:30 | 67 | 47 |  |  | 43571.9375 | 61 | 61
2019-04-16 23:00 | 65 | 47 |  |  | 43571.9583 | 60 | 59
2019-04-16 23:30 | 63 | 43 |  |  | 43571.9792 | 56 | 55
2019-04-17 | 60 | 39 |  |  | 43572 | 52 | 51
2019-04-17 00:30 | 61 | 39 |  |  | 43572.0208 | 50 | 49
2019-04-17 01:00 | 59 | 35 |  |  | 43572.0417 | 46 | 45
2019-04-17 01:30 | 57 | 36 |  |  | 43572.0625 | 45 | 44
2019-04-17 02:00 | 57 | 35 |  |  | 43572.0833 | 44 | 43
2019-04-17 02:30 | 56 | 34 |  |  | 43572.1042 | 43 | 42
2019-04-17 03:00 | 56 | 35 |  |  | 43572.125 | 43 | 43
2019-04-17 03:30 | 58 | 36 |  |  | 43572.1458 | 44 | 44
2019-04-17 04:00 | 59 | 37 |  |  | 43572.1667 | 45 | 45
2019-04-17 04:30 | 59 | 39 |  |  | 43572.1875 | 45 | 45
2019-04-17 05:00 | 60 | 40 |  |  | 43572.2083 | 49 | 48
2019-04-17 05:30 | 60 | 42 |  |  | 43572.2292 | 52 | 51
2019-04-17 06:00 | 60 | 44 |  |  | 43572.25 | 54 | 54
2019-04-17 06:30 | 61 | 48 |  |  | 43572.2708 | 60 | 60
2019-04-17 07:00 | 62 | 50 |  |  | 43572.2917 | 66 | 65
2019-04-17 07:30 | 61 | 50 |  |  | 43572.3125 | 69 | 69
2019-04-17 08:00 | 59 | 49 |  |  | 43572.3333 | 68 | 68
2019-04-17 08:30 | 63 | 50 |  |  | 43572.3542 | 71 | 70
2019-04-17 09:00 | 66 | 49 |  |  | 43572.375 | 72 | 70
2019-04-17 09:30 | 64 | 46 |  |  | 43572.3958 | 69 | 67
2019-04-17 10:00 | 65 | 46 |  |  | 43572.4167 | 71 | 69
2019-04-17 10:30 | 66 | 50 |  |  | 43572.4375 | 74 | 72
2019-04-17 11:00 | 66 | 49 |  |  | 43572.4583 | 75 | 73
2019-04-17 11:30 | 65 | 48 |  |  | 43572.4792 | 73 | 71
2019-04-17 12:00 | 66 | 50 |  |  | 43572.5 | 73 | 71
2019-04-17 12:30 | 67 | 51 |  |  | 43572.5208 | 74 | 72
2019-04-17 13:00 | 63 | 46 |  |  | 43572.5417 | 71 | 69
2019-04-17 13:30 | 65 | 48 |  |  | 43572.5625 | 70 | 68
2019-04-17 14:00 | 65 | 48 |  |  | 43572.5833 | 72 | 70
2019-04-17 14:30 | 67 | 50 |  |  | 43572.6042 | 71 | 69
2019-04-17 15:00 | 68 | 51 |  |  | 43572.625 | 73 | 71
2019-04-17 15:30 | 68 | 51 |  |  | 43572.6458 | 74 | 72
2019-04-17 16:00 | 70 | 54 |  |  | 43572.6667 | 75 | 74
2019-04-17 16:30 | 72 | 55 |  |  | 43572.6875 | 78 | 76
2019-04-17 17:00 | 76 | 60 |  |  | 43572.7083 | 81 | 80
2019-04-17 17:30 | 79 | 62 |  |  | 43572.7292 | 81 | 81
2019-04-17 18:00 | 80 | 63 |  |  | 43572.75 | 80 | 80
2019-04-17 18:30 | 80 | 61 |  |  | 43572.7708 | 77 | 76
2019-04-17 19:00 | 81 | 62 |  |  | 43572.7917 | 78 | 78
2019-04-17 19:30 | 80 | 60 |  |  | 43572.8125 | 74 | 74
2019-04-17 20:00 | 78 | 57 |  |  | 43572.8333 | 71 | 71
2019-04-17 20:30 | 74 | 55 |  |  | 43572.8542 | 69 | 69
2019-04-17 21:00 | 71 | 50 |  |  | 43572.875 | 63 | 63
2019-04-17 21:30 | 70 | 48 |  |  | 43572.8958 | 60 | 60
2019-04-17 22:00 | 62 | 45 |  |  | 43572.9167 | 60 | 60
2019-04-17 22:30 | 55 | 45 |  |  | 43572.9375 | 64 | 60
2019-04-17 23:00 | 55 | 44 |  |  | 43572.9583 | 61 | 57
2019-04-17 23:30 | 51 | 39 |  |  | 43572.9792 | 56 | 51
2019-04-18 | 48 | 35 |  |  | 43573 | 52 | 47
2019-04-18 00:30 | 49 | 34 |  |  | 43573.0208 | 51 | 45
2019-04-18 01:00 | 50 | 34 |  |  | 43573.0417 | 52 | 45
2019-04-18 01:30 | 50 | 34 |  |  | 43573.0625 | 50 | 44
2019-04-18 02:00 | 50 | 34 |  |  | 43573.0833 | 50 | 43
2019-04-18 02:30 | 50 | 34 |  |  | 43573.1042 | 50 | 43
2019-04-18 03:00 | 49 | 32 |  |  | 43573.125 | 48 | 41
2019-04-18 03:30 | 49 | 34 |  |  | 43573.1458 | 49 | 43
2019-04-18 04:00 | 48 | 35 |  |  | 43573.1667 | 48 | 43
2019-04-18 04:30 | 49 | 36 |  |  | 43573.1875 | 49 | 45
2019-04-18 05:00 | 51 | 39 |  |  | 43573.2083 | 51 | 48
2019-04-18 05:30 | 53 | 42 |  |  | 43573.2292 | 55 | 52
2019-04-18 06:00 | 56 | 48 |  |  | 43573.25 | 59 | 57
2019-04-18 06:30 | 57 | 48 |  |  | 43573.2708 | 63 | 61
2019-04-18 07:00 | 53 | 45 |  |  | 43573.2917 | 62 | 60
2019-04-18 07:30 | 50 | 42 |  |  | 43573.3125 | 61 | 60
2019-04-18 08:00 | 49 | 41 |  |  | 43573.3333 | 62 | 61
2019-04-18 08:30 | 48 | 40 |  |  | 43573.3542 | 62 | 61
2019-04-18 09:00 | 48 | 41 |  |  | 43573.375 | 62 | 61
2019-04-18 09:30 | 46 | 39 |  |  | 43573.3958 | 61 | 60
2019-04-18 10:00 | 45 | 37 |  |  | 43573.4167 | 60 | 59
2019-04-18 10:30 | 44 | 37 |  |  | 43573.4375 | 60 | 60
2019-04-18 11:00 | 47 | 41 |  |  | 43573.4583 | 63 | 62
2019-04-18 11:30 | 50 | 43 |  |  | 43573.4792 | 68 | 67
2019-04-18 12:00 | 52 | 45 |  |  | 43573.5 | 69 | 69
2019-04-18 12:30 | 50 | 44 |  |  | 43573.5208 | 66 | 65
2019-04-18 13:00 | 53 | 47 |  |  | 43573.5417 | 65 | 64
2019-04-18 13:30 | 53 | 47 |  |  | 43573.5625 | 68 | 67
2019-04-18 14:00 | 54 | 48 |  |  | 43573.5833 | 70 | 69
2019-04-18 14:30 | 56 | 50 |  |  | 43573.6042 | 72 | 71
2019-04-18 15:00 | 58 | 48 |  |  | 43573.625 | 69 | 69
2019-04-18 15:30 | 64 | 52 |  |  | 43573.6458 | 73 | 73
2019-04-18 16:00 | 68 | 56 |  |  | 43573.6667 | 74 | 74
2019-04-18 16:30 | 68 | 56 |  |  | 43573.6875 | 75 | 75
2019-04-18 17:00 | 72 | 60 |  |  | 43573.7083 | 78 | 78
2019-04-18 17:30 | 72 | 60 |  |  | 43573.7292 | 77 | 77
2019-04-18 18:00 | 73 | 61 |  |  | 43573.75 | 77 | 76
2019-04-18 18:30 | 74 | 61 |  |  | 43573.7708 | 75 | 75
2019-04-18 19:00 | 74 | 60 |  |  | 43573.7917 | 75 | 74
2019-04-18 19:30 | 73 | 59 |  |  | 43573.8125 | 73 | 72
2019-04-18 20:00 | 72 | 58 |  |  | 43573.8333 | 72 | 71
2019-04-18 20:30 | 72 | 57 |  |  | 43573.8542 | 71 | 70
2019-04-18 21:00 | 67 | 53 |  |  | 43573.875 | 66 | 65
2019-04-18 21:30 | 67 | 52 |  |  | 43573.8958 | 64 | 63
2019-04-18 22:00 | 70 | 53 |  |  | 43573.9167 | 66 | 65
2019-04-18 22:30 | 69 | 53 |  |  | 43573.9375 | 67 | 66
2019-04-18 23:00 | 71 | 53 |  |  | 43573.9583 | 66 | 65
2019-04-18 23:30 | 70 | 51 |  |  | 43573.9792 | 65 | 63
2019-04-19 | 67 | 46 |  |  | 43574 | 60 | 58
2019-04-19 00:30 | 65 | 42 |  |  | 43574.0208 | 56 | 53
2019-04-19 01:00 | 64 | 40 |  |  | 43574.0417 | 52 | 49
2019-04-19 01:30 | 63 | 38 |  |  | 43574.0625 | 49 | 46
2019-04-19 02:00 | 62 | 35 |  |  | 43574.0833 | 47 | 44
2019-04-19 02:30 | 61 | 33 |  |  | 43574.1042 | 45 | 42
2019-04-19 03:00 | 60 | 31 |  |  | 43574.125 | 44 | 41
2019-04-19 03:30 | 61 | 32 |  |  | 43574.1458 | 44 | 41
2019-04-19 04:00 | 61 | 31 |  |  | 43574.1667 | 44 | 41
2019-04-19 04:30 | 61 | 32 |  |  | 43574.1875 | 45 | 42
2019-04-19 05:00 | 62 | 34 |  |  | 43574.2083 | 47 | 44
2019-04-19 05:30 | 63 | 35 |  |  | 43574.2292 | 48 | 45
2019-04-19 06:00 | 62 | 35 |  |  | 43574.25 | 49 | 46
2019-04-19 06:30 | 63 | 35 |  |  | 43574.2708 | 51 | 48
2019-04-19 07:00 | 62 | 35 |  |  | 43574.2917 | 52 | 50
2019-04-19 07:30 | 60 | 33 |  |  | 43574.3125 | 51 | 49
2019-04-19 08:00 | 57 | 29 |  |  | 43574.3333 | 47 | 45
2019-04-19 08:30 | 57 | 30 |  |  | 43574.3542 | 48 | 47
2019-04-19 09:00 | 57 | 31 |  |  | 43574.375 | 48 | 47
2019-04-19 09:30 | 58 | 34 |  |  | 43574.3958 | 49 | 47
2019-04-19 10:00 | 57 | 32 |  |  | 43574.4167 | 49 | 48
2019-04-19 10:30 | 57 | 33 |  |  | 43574.4375 | 44 | 43
2019-04-19 11:00 | 56 | 33 |  |  | 43574.4583 | 49 | 48
2019-04-19 11:30 | 57 | 34 |  |  | 43574.4792 | 48 | 47
2019-04-19 12:00 | 57 | 34 |  |  | 43574.5 | 49 | 48
2019-04-19 12:30 | 62 | 43 |  |  | 43574.5208 | 55 | 55
2019-04-19 13:00 | 57 | 35 |  |  | 43574.5417 | 48 | 47
2019-04-19 13:30 | 52 | 27 |  |  | 43574.5625 | 42 | 42
2019-04-19 14:00 | 58 | 38 |  |  | 43574.5833 | 45 | 45
2019-04-19 14:30 | 58 | 37 |  |  | 43574.6042 | 50 | 49
2019-04-19 15:00 | 60 | 41 |  |  | 43574.625 | 58 | 58
2019-04-19 15:30 | 64 | 46 |  |  | 43574.6458 | 60 | 59
2019-04-19 16:00 | 64 | 46 |  |  | 43574.6667 | 63 | 63
2019-04-19 16:30 | 63 | 45 |  |  | 43574.6875 | 59 | 58
2019-04-19 17:00 | 64 | 47 |  |  | 43574.7083 | 62 | 62
2019-04-19 17:30 | 67 | 51 |  |  | 43574.7292 | 65 | 64
2019-04-19 18:00 | 68 | 52 |  |  | 43574.75 | 66 | 66
2019-04-19 18:30 | 68 | 53 |  |  | 43574.7708 | 67 | 66
2019-04-19 19:00 | 69 | 54 |  |  | 43574.7917 | 68 | 67
2019-04-19 19:30 | 69 | 53 |  |  | 43574.8125 | 67 | 66
2019-04-19 20:00 | 71 | 54 |  |  | 43574.8333 | 68 | 67
2019-04-19 20:30 | 69 | 52 |  |  | 43574.8542 | 66 | 65
2019-04-19 21:00 | 68 | 50 |  |  | 43574.875 | 64 | 62
2019-04-19 21:30 | 67 | 49 |  |  | 43574.8958 | 62 | 61
2019-04-19 22:00 | 67 | 49 |  |  | 43574.9167 | 63 | 62
2019-04-19 22:30 | 68 | 49 |  |  | 43574.9375 | 65 | 63
2019-04-19 23:00 | 68 | 48 |  |  | 43574.9583 | 62 | 60
2019-04-19 23:30 | 66 | 44 |  |  | 43574.9792 | 58 | 56
2019-04-20 | 62 | 39 |  |  | 43575 | 53 | 51
2019-04-20 00:30 | 62 | 37 |  |  | 43575.0208 | 51 | 49
2019-04-20 01:00 | 61 | 35 |  |  | 43575.0417 | 48 | 45
2019-04-20 01:30 | 60 | 35 |  |  | 43575.0625 | 47 | 44
2019-04-20 02:00 | 60 | 33 |  |  | 43575.0833 | 45 | 42
2019-04-20 02:30 | 60 | 33 |  |  | 43575.1042 | 45 | 42
2019-04-20 03:00 | 61 | 33 |  |  | 43575.125 | 45 | 41
2019-04-20 03:30 | 61 | 33 |  |  | 43575.1458 | 45 | 42
2019-04-20 04:00 | 61 | 33 |  |  | 43575.1667 | 45 | 42
2019-04-20 04:30 | 61 | 33 |  |  | 43575.1875 | 45 | 42
2019-04-20 05:00 | 62 | 35 |  |  | 43575.2083 | 48 | 45
2019-04-20 05:30 | 62 | 35 |  |  | 43575.2292 | 48 | 45
2019-04-20 06:00 | 62 | 35 |  |  | 43575.25 | 48 | 45
2019-04-20 06:30 | 63 | 36 |  |  | 43575.2708 | 51 | 48
2019-04-20 07:00 | 63 | 36 |  |  | 43575.2917 | 52 | 49
2019-04-20 07:30 | 61 | 35 |  |  | 43575.3125 | 50 | 48
2019-04-20 08:00 | 58 | 32 |  |  | 43575.3333 | 47 | 45
2019-04-20 08:30 | 58 | 35 |  |  | 43575.3542 | 49 | 48
2019-04-20 09:00 | 58 | 35 |  |  | 43575.375 | 52 | 51
2019-04-20 09:30 | 58 | 38 |  |  | 43575.3958 | 55 | 54
2019-04-20 10:00 | 59 | 39 |  |  | 43575.4167 | 55 | 55
2019-04-20 10:30 | 61 | 42 |  |  | 43575.4375 | 58 | 58
2019-04-20 11:00 | 59 | 39 |  |  | 43575.4583 | 54 | 53
2019-04-20 11:30 | 60 | 40 |  |  | 43575.4792 | 48 | 47
2019-04-20 12:00 | 63 | 44 |  |  | 43575.5 | 62 | 62
2019-04-20 12:30 | 62 | 44 |  |  | 43575.5208 | 58 | 57
2019-04-20 13:00 | 60 | 40 |  |  | 43575.5417 | 53 | 52
2019-04-20 13:30 | 60 | 40 |  |  | 43575.5625 | 55 | 55
2019-04-20 14:00 | 56 | 33 |  |  | 43575.5833 | 50 | 49
2019-04-20 14:30 | 60 | 40 |  |  | 43575.6042 | 49 | 48
2019-04-20 15:00 | 60 | 41 |  |  | 43575.625 | 56 | 55
2019-04-20 15:30 | 63 | 45 |  |  | 43575.6458 | 64 | 64
2019-04-20 16:00 | 67 | 50 |  |  | 43575.6667 | 65 | 65
2019-04-20 16:30 | 64 | 47 |  |  | 43575.6875 | 63 | 62
2019-04-20 17:00 | 66 | 48 |  |  | 43575.7083 | 64 | 64
2019-04-20 17:30 | 69 | 53 |  |  | 43575.7292 | 68 | 68
2019-04-20 18:00 | 70 | 55 |  |  | 43575.75 | 69 | 69
2019-04-20 18:30 | 72 | 55 |  |  | 43575.7708 | 69 | 68
2019-04-20 19:00 | 72 | 55 |  |  | 43575.7917 | 70 | 69
2019-04-20 19:30 | 72 | 54 |  |  | 43575.8125 | 69 | 68
2019-04-20 20:00 | 72 | 55 |  |  | 43575.8333 | 70 | 69
2019-04-20 20:30 | 72 | 56 |  |  | 43575.8542 | 70 | 69
2019-04-20 21:00 | 72 | 55 |  |  | 43575.875 | 69 | 68
2019-04-20 21:30 | 74 | 56 |  |  | 43575.8958 | 69 | 68
2019-04-20 22:00 | 72 | 54 |  |  | 43575.9167 | 68 | 67
2019-04-20 22:30 | 73 | 54 |  |  | 43575.9375 | 69 | 68
2019-04-20 23:00 | 72 | 53 |  |  | 43575.9583 | 66 | 64
2019-04-20 23:30 | 68 | 47 |  |  | 43575.9792 | 61 | 59
2019-04-21 | 66 | 45 |  |  | 43576 | 59 | 57
2019-04-21 00:30 | 65 | 42 |  |  | 43576.0208 | 56 | 54
2019-04-21 01:00 | 65 | 41 |  |  | 43576.0417 | 55 | 52
2019-04-21 01:30 | 65 | 40 |  |  | 43576.0625 | 53 | 50
2019-04-21 02:00 | 62 | 37 |  |  | 43576.0833 | 49 | 47
2019-04-21 02:30 | 61 | 37 |  |  | 43576.1042 | 49 | 48
2019-04-21 03:00 | 60 | 36 |  |  | 43576.125 | 47 | 46
2019-04-21 03:30 | 60 | 36 |  |  | 43576.1458 | 47 | 46
2019-04-21 04:00 | 59 | 34 |  |  | 43576.1667 | 45 | 43
2019-04-21 04:30 | 60 | 35 |  |  | 43576.1875 | 47 | 45
2019-04-21 05:00 | 60 | 35 |  |  | 43576.2083 | 46 | 45
2019-04-21 05:30 | 59 | 35 |  |  | 43576.2292 | 45 | 44
2019-04-21 06:00 | 59 | 35 |  |  | 43576.25 | 46 | 45
2019-04-21 06:30 | 60 | 35 |  |  | 43576.2708 | 49 | 48
2019-04-21 07:00 | 61 | 36 |  |  | 43576.2917 | 51 | 49
2019-04-21 07:30 | 59 | 34 |  |  | 43576.3125 | 49 | 48
2019-04-21 08:00 | 58 | 32 |  |  | 43576.3333 | 48 | 46
2019-04-21 08:30 | 58 | 34 |  |  | 43576.3542 | 49 | 48
2019-04-21 09:00 | 58 | 33 |  |  | 43576.375 | 49 | 48
2019-04-21 09:30 | 59 | 35 |  |  | 43576.3958 | 52 | 51
2019-04-21 10:00 | 61 | 39 |  |  | 43576.4167 | 55 | 53
2019-04-21 10:30 | 60 | 38 |  |  | 43576.4375 | 54 | 53
2019-04-21 11:00 | 61 | 41 |  |  | 43576.4583 | 56 | 56
2019-04-21 11:30 | 60 | 40 |  |  | 43576.4792 | 49 | 48
2019-04-21 12:00 | 58 | 36 |  |  | 43576.5 | 46 | 45
2019-04-21 12:30 | 57 | 36 |  |  | 43576.5208 | 49 | 48
2019-04-21 13:00 | 58 | 37 |  |  | 43576.5417 | 48 | 47
2019-04-21 13:30 | 57 | 35 |  |  | 43576.5625 | 48 | 47
2019-04-21 14:00 | 57 | 35 |  |  | 43576.5833 | 47 | 46
2019-04-21 14:30 | 56 | 32 |  |  | 43576.6042 | 45 | 44
2019-04-21 15:00 | 58 | 35 |  |  | 43576.625 | 48 | 47
2019-04-21 15:30 | 56 | 34 |  |  | 43576.6458 | 47 | 46
2019-04-21 16:00 | 61 | 42 |  |  | 43576.6667 | 56 | 55
2019-04-21 16:30 | 62 | 43 |  |  | 43576.6875 | 58 | 57
2019-04-21 17:00 | 64 | 47 |  |  | 43576.7083 | 62 | 61
2019-04-21 17:30 | 66 | 50 |  |  | 43576.7292 | 63 | 62
2019-04-21 18:00 | 67 | 50 |  |  | 43576.75 | 64 | 63
2019-04-21 18:30 | 68 | 50 |  |  | 43576.7708 | 64 | 63
2019-04-21 19:00 | 68 | 51 |  |  | 43576.7917 | 66 | 65
2019-04-21 19:30 | 70 | 52 |  |  | 43576.8125 | 66 | 65
2019-04-21 20:00 | 69 | 51 |  |  | 43576.8333 | 65 | 64
2019-04-21 20:30 | 68 | 50 |  |  | 43576.8542 | 65 | 64
2019-04-21 21:00 | 70 | 53 |  |  | 43576.875 | 66 | 65
2019-04-21 21:30 | 71 | 52 |  |  | 43576.8958 | 66 | 65
2019-04-21 22:00 | 71 | 52 |  |  | 43576.9167 | 66 | 65
2019-04-21 22:30 | 70 | 52 |  |  | 43576.9375 | 66 | 65
2019-04-21 23:00 | 70 | 50 |  |  | 43576.9583 | 62 | 61
2019-04-21 23:30 | 66 | 45 |  |  | 43576.9792 | 60 | 58
2019-04-22 | 65 | 43 |  |  | 43577 | 56 | 55
2019-04-22 00:30 | 64 | 40 |  |  | 43577.0208 | 53 | 51
2019-04-22 01:00 | 63 | 39 |  |  | 43577.0417 | 51 | 48
2019-04-22 01:30 | 61 | 34 |  |  | 43577.0625 | 47 | 44
2019-04-22 02:00 | 61 | 33 |  |  | 43577.0833 | 45 | 42
2019-04-22 02:30 | 61 | 33 |  |  | 43577.1042 | 46 | 43
2019-04-22 03:00 | 61 | 33 |  |  | 43577.125 | 46 | 43
2019-04-22 03:30 | 62 | 34 |  |  | 43577.1458 | 47 | 44
2019-04-22 04:00 | 62 | 35 |  |  | 43577.1667 | 47 | 44
2019-04-22 04:30 | 61 | 33 |  |  | 43577.1875 | 45 | 42
2019-04-22 05:00 | 60 | 32 |  |  | 43577.2083 | 45 | 43
2019-04-22 05:30 | 60 | 33 |  |  | 43577.2292 | 47 | 44
2019-04-22 06:00 | 61 | 34 |  |  | 43577.25 | 49 | 46
2019-04-22 06:30 | 62 | 36 |  |  | 43577.2708 | 51 | 49
2019-04-22 07:00 | 62 | 37 |  |  | 43577.2917 | 54 | 51
2019-04-22 07:30 | 61 | 36 |  |  | 43577.3125 | 54 | 52
2019-04-22 08:00 | 57 | 32 |  |  | 43577.3333 | 50 | 48
2019-04-22 08:30 | 58 | 34 |  |  | 43577.3542 | 52 | 50
2019-04-22 09:00 | 60 | 38 |  |  | 43577.375 | 55 | 54
2019-04-22 09:30 | 60 | 40 |  |  | 43577.3958 | 57 | 56
2019-04-22 10:00 | 60 | 40 |  |  | 43577.4167 | 57 | 56
2019-04-22 10:30 | 63 | 45 |  |  | 43577.4375 | 64 | 64
2019-04-22 11:00 | 60 | 42 |  |  | 43577.4583 | 62 | 62
2019-04-22 11:30 | 59 | 42 |  |  | 43577.4792 | 54 | 54
2019-04-22 12:00 | 57 | 38 |  |  | 43577.5 | 56 | 56
2019-04-22 12:30 | 61 | 45 |  |  | 43577.5208 | 60 | 60
2019-04-22 13:00 | 60 | 43 |  |  | 43577.5417 | 60 | 60
2019-04-22 13:30 | 59 | 43 |  |  | 43577.5625 | 55 | 54
2019-04-22 14:00 | 59 | 42 |  |  | 43577.5833 | 57 | 56
2019-04-22 14:30 | 60 | 44 |  |  | 43577.6042 | 55 | 55
2019-04-22 15:00 | 61 | 45 |  |  | 43577.625 | 59 | 59
2019-04-22 15:30 | 64 | 49 |  |  | 43577.6458 | 63 | 63
2019-04-22 16:00 | 64 | 50 |  |  | 43577.6667 | 64 | 64
2019-04-22 16:30 | 66 | 51 |  |  | 43577.6875 | 66 | 66
2019-04-22 17:00 | 73 | 52 |  |  | 43577.7083 | 72 | 69
2019-04-22 17:30 | 78 | 56 |  |  | 43577.7292 | 78 | 72
2019-04-22 18:00 | 81 | 59 |  |  | 43577.75 | 82 | 75
2019-04-22 18:30 | 82 | 60 |  |  | 43577.7708 | 82 | 74
2019-04-22 19:00 | 82 | 59 |  |  | 43577.7917 | 82 | 74
2019-04-22 19:30 | 82 | 58 |  |  | 43577.8125 | 81 | 72
2019-04-22 20:00 | 83 | 59 |  |  | 43577.8333 | 82 | 73
2019-04-22 20:30 | 81 | 56 |  |  | 43577.8542 | 80 | 70
2019-04-22 21:00 | 72 | 51 |  |  | 43577.875 | 68 | 65
2019-04-22 21:30 | 69 | 50 |  |  | 43577.8958 | 65 | 63
2019-04-22 22:00 | 69 | 51 |  |  | 43577.9167 | 67 | 65
2019-04-22 22:30 | 68 | 49 |  |  | 43577.9375 | 66 | 64
2019-04-22 23:00 | 68 | 48 |  |  | 43577.9583 | 63 | 61
2019-04-22 23:30 | 67 | 46 |  |  | 43577.9792 | 61 | 58
2019-04-23 | 66 | 44 |  |  | 43578 | 58 | 56
2019-04-23 00:30 | 64 | 41 |  |  | 43578.0208 | 54 | 52
2019-04-23 01:00 | 62 | 37 |  |  | 43578.0417 | 51 | 48
2019-04-23 01:30 | 61 | 35 |  |  | 43578.0625 | 48 | 45
2019-04-23 02:00 | 61 | 35 |  |  | 43578.0833 | 48 | 46
2019-04-23 02:30 | 60 | 34 |  |  | 43578.1042 | 46 | 43
2019-04-23 03:00 | 60 | 34 |  |  | 43578.125 | 46 | 43
2019-04-23 03:30 | 61 | 34 |  |  | 43578.1458 | 48 | 45
2019-04-23 04:00 | 61 | 35 |  |  | 43578.1667 | 48 | 46
2019-04-23 04:30 | 62 | 37 |  |  | 43578.1875 | 50 | 47
2019-04-23 05:00 | 64 | 40 |  |  | 43578.2083 | 52 | 50
2019-04-23 05:30 | 65 | 44 |  |  | 43578.2292 | 55 | 53
2019-04-23 06:00 | 67 | 48 |  |  | 43578.25 | 60 | 59
2019-04-23 06:30 | 71 | 54 |  |  | 43578.2708 | 70 | 69
2019-04-23 07:00 | 71 | 57 |  |  | 43578.2917 | 75 | 75
2019-04-23 07:30 | 69 | 58 |  |  | 43578.3125 | 78 | 78
2019-04-23 08:00 | 68 | 59 |  |  | 43578.3333 | 81 | 81
2019-04-23 08:30 | 68 | 59 |  |  | 43578.3542 | 83 | 83
2019-04-23 09:00 | 67 | 57 |  |  | 43578.375 | 80 | 80
2019-04-23 09:30 | 68 | 58 |  |  | 43578.3958 | 82 | 82
2019-04-23 10:00 | 70 | 60 |  |  | 43578.4167 | 81 | 81
2019-04-23 10:30 | 70 | 59 |  |  | 43578.4375 | 80 | 80
2019-04-23 11:00 | 66 | 56 |  |  | 43578.4583 | 80 | 80
2019-04-23 11:30 | 67 | 58 |  |  | 43578.4792 | 80 | 80
2019-04-23 12:00 | 69 | 61 |  |  | 43578.5 | 84 | 84
2019-04-23 12:30 | 67 | 58 |  |  | 43578.5208 | 85 | 85
2019-04-23 13:00 | 68 | 60 |  |  | 43578.5417 | 83 | 82
2019-04-23 13:30 | 68 | 60 |  |  | 43578.5625 | 82 | 82
2019-04-23 14:00 | 70 | 64 |  |  | 43578.5833 | 86 | 85
2019-04-23 14:30 | 71 | 64 |  |  | 43578.6042 | 87 | 86
2019-04-23 15:00 | 71 | 65 |  |  | 43578.625 | 86 | 86
2019-04-23 15:30 | 71 | 65 |  |  | 43578.6458 | 85 | 85
2019-04-23 16:00 | 71 | 64 |  |  | 43578.6667 | 83 | 83
2019-04-23 16:30 | 71 | 63 |  |  | 43578.6875 | 82 | 82
2019-04-23 17:00 | 71 | 63 |  |  | 43578.7083 | 82 | 82
2019-04-23 17:30 | 73 | 65 |  |  | 43578.7292 | 82 | 82
2019-04-23 18:00 | 78 | 67 |  |  | 43578.75 | 85 | 84
2019-04-23 18:30 | 81 | 64 |  |  | 43578.7708 | 84 | 80
2019-04-23 19:00 | 82 | 65 |  |  | 43578.7917 | 85 | 81
2019-04-23 19:30 | 81 | 63 |  |  | 43578.8125 | 82 | 78
2019-04-23 20:00 | 76 | 62 |  |  | 43578.8333 | 78 | 77
2019-04-23 20:30 | 73 | 62 |  |  | 43578.8542 | 76 | 76
2019-04-23 21:00 | 70 | 58 |  |  | 43578.875 | 72 | 71
2019-04-23 21:30 | 70 | 57 |  |  | 43578.8958 | 69 | 69
2019-04-23 22:00 | 72 | 57 |  |  | 43578.9167 | 69 | 68
2019-04-23 22:30 | 69 | 54 |  |  | 43578.9375 | 67 | 66
2019-04-23 23:00 | 68 | 53 |  |  | 43578.9583 | 64 | 63
2019-04-23 23:30 | 67 | 50 |  |  | 43578.9792 | 62 | 61
2019-04-24 | 66 | 46 |  |  | 43579 | 59 | 57
2019-04-24 00:30 | 63 | 41 |  |  | 43579.0208 | 54 | 52
2019-04-24 01:00 | 61 | 38 |  |  | 43579.0417 | 50 | 48
2019-04-24 01:30 | 62 | 36 |  |  | 43579.0625 | 49 | 46
2019-04-24 02:00 | 61 | 35 |  |  | 43579.0833 | 48 | 45
2019-04-24 02:30 | 61 | 34 |  |  | 43579.1042 | 48 | 45
2019-04-24 03:00 | 61 | 35 |  |  | 43579.125 | 48 | 45
2019-04-24 03:30 | 60 | 35 |  |  | 43579.1458 | 47 | 44
2019-04-24 04:00 | 61 | 35 |  |  | 43579.1667 | 47 | 44
2019-04-24 04:30 | 62 | 37 |  |  | 43579.1875 | 50 | 47
2019-04-24 05:00 | 63 | 39 |  |  | 43579.2083 | 52 | 49
2019-04-24 05:30 | 65 | 43 |  |  | 43579.2292 | 55 | 53
2019-04-24 06:00 | 66 | 48 |  |  | 43579.25 | 60 | 58
2019-04-24 06:30 | 71 | 55 |  |  | 43579.2708 | 69 | 68
2019-04-24 07:00 | 72 | 58 |  |  | 43579.2917 | 75 | 75
2019-04-24 07:30 | 73 | 60 |  |  | 43579.3125 | 80 | 80
2019-04-24 08:00 | 71 | 59 |  |  | 43579.3333 | 77 | 77
2019-04-24 08:30 | 70 | 57 |  |  | 43579.3542 | 76 | 76
2019-04-24 09:00 | 67 | 54 |  |  | 43579.375 | 79 | 79
2019-04-24 09:30 | 66 | 54 |  |  | 43579.3958 | 77 | 77
2019-04-24 10:00 | 65 | 53 |  |  | 43579.4167 | 76 | 76
2019-04-24 10:30 | 66 | 54 |  |  | 43579.4375 | 76 | 76
2019-04-24 11:00 | 67 | 56 |  |  | 43579.4583 | 79 | 79
2019-04-24 11:30 | 68 | 56 |  |  | 43579.4792 | 77 | 77
2019-04-24 12:00 | 67 | 55 |  |  | 43579.5 | 79 | 79
2019-04-24 12:30 | 66 | 55 |  |  | 43579.5208 | 78 | 78
2019-04-24 13:00 | 69 | 58 |  |  | 43579.5417 | 79 | 79
2019-04-24 13:30 | 70 | 59 |  |  | 43579.5625 | 77 | 76
2019-04-24 14:00 | 71 | 60 |  |  | 43579.5833 | 81 | 81
2019-04-24 14:30 | 69 | 58 |  |  | 43579.6042 | 80 | 80
2019-04-24 15:00 | 70 | 59 |  |  | 43579.625 | 77 | 77
2019-04-24 15:30 | 74 | 63 |  |  | 43579.6458 | 81 | 81
2019-04-24 16:00 | 75 | 63 |  |  | 43579.6667 | 82 | 82
2019-04-24 16:30 | 73 | 61 |  |  | 43579.6875 | 80 | 80
2019-04-24 17:00 | 75 | 63 |  |  | 43579.7083 | 81 | 81
2019-04-24 17:30 | 77 | 65 |  |  | 43579.7292 | 83 | 82
2019-04-24 18:00 | 76 | 64 |  |  | 43579.75 | 81 | 81
2019-04-24 18:30 | 76 | 63 |  |  | 43579.7708 | 78 | 78
2019-04-24 19:00 | 77 | 63 |  |  | 43579.7917 | 78 | 78
2019-04-24 19:30 | 75 | 61 |  |  | 43579.8125 | 75 | 75
2019-04-24 20:00 | 76 | 62 |  |  | 43579.8333 | 75 | 75
2019-04-24 20:30 | 75 | 62 |  |  | 43579.8542 | 75 | 74
2019-04-24 21:00 | 72 | 58 |  |  | 43579.875 | 71 | 70
2019-04-24 21:30 | 71 | 56 |  |  | 43579.8958 | 68 | 67
2019-04-24 22:00 | 70 | 54 |  |  | 43579.9167 | 67 | 67
2019-04-24 22:30 | 70 | 54 |  |  | 43579.9375 | 67 | 66
2019-04-24 23:00 | 71 | 54 |  |  | 43579.9583 | 66 | 65
2019-04-24 23:30 | 69 | 50 |  |  | 43579.9792 | 63 | 62
2019-04-25 | 67 | 46 |  |  | 43580 | 59 | 58
2019-04-25 00:30 | 65 | 42 |  |  | 43580.0208 | 54 | 52
2019-04-25 01:00 | 63 | 38 |  |  | 43580.0417 | 50 | 48
2019-04-25 01:30 | 62 | 36 |  |  | 43580.0625 | 47 | 44
2019-04-25 02:00 | 61 | 34 |  |  | 43580.0833 | 45 | 42
2019-04-25 02:30 | 59 | 33 |  |  | 43580.1042 | 43 | 41
2019-04-25 03:00 | 56 | 32 |  |  | 43580.125 | 43 | 42
2019-04-25 03:30 | 55 | 34 |  |  | 43580.1458 | 43 | 43
2019-04-25 04:00 | 57 | 37 |  |  | 43580.1667 | 47 | 47
2019-04-25 04:30 | 57 | 38 |  |  | 43580.1875 | 47 | 47
2019-04-25 05:00 | 57 | 38 |  |  | 43580.2083 | 47 | 47
2019-04-25 05:30 | 58 | 38 |  |  | 43580.2292 | 48 | 48
2019-04-25 06:00 | 57 | 38 |  |  | 43580.25 | 49 | 49
2019-04-25 06:30 | 59 | 39 |  |  | 43580.2708 | 51 | 51
2019-04-25 07:00 | 59 | 41 |  |  | 43580.2917 | 54 | 54
2019-04-25 07:30 | 58 | 39 |  |  | 43580.3125 | 53 | 53
2019-04-25 08:00 | 55 | 37 |  |  | 43580.3333 | 51 | 51
2019-04-25 08:30 | 56 | 38 |  |  | 43580.3542 | 56 | 55
2019-04-25 09:00 | 58 | 42 |  |  | 43580.375 | 56 | 56
2019-04-25 09:30 | 58 | 41 |  |  | 43580.3958 | 56 | 56
2019-04-25 10:00 | 58 | 43 |  |  | 43580.4167 | 57 | 57
2019-04-25 10:30 | 57 | 43 |  |  | 43580.4375 | 56 | 56
2019-04-25 11:00 | 57 | 41 |  |  | 43580.4583 | 55 | 55
2019-04-25 11:30 | 58 | 43 |  |  | 43580.4792 | 54 | 54
2019-04-25 12:00 | 57 | 42 |  |  | 43580.5 | 57 | 56
2019-04-25 12:30 | 57 | 42 |  |  | 43580.5208 | 57 | 57
2019-04-25 13:00 | 57 | 41 |  |  | 43580.5417 | 58 | 57
2019-04-25 13:30 | 57 | 43 |  |  | 43580.5625 | 59 | 59
2019-04-25 14:00 | 59 | 45 |  |  | 43580.5833 | 58 | 57
2019-04-25 14:30 | 62 | 49 |  |  | 43580.6042 | 59 | 59
2019-04-25 15:00 | 61 | 48 |  |  | 43580.625 | 60 | 60
2019-04-25 15:30 | 63 | 50 |  |  | 43580.6458 | 65 | 64
2019-04-25 16:00 | 64 | 52 |  |  | 43580.6667 | 66 | 66
2019-04-25 16:30 | 67 | 54 |  |  | 43580.6875 | 68 | 68
2019-04-25 17:00 | 68 | 55 |  |  | 43580.7083 | 69 | 69
2019-04-25 17:30 | 69 | 57 |  |  | 43580.7292 | 72 | 72
2019-04-25 18:00 | 71 | 58 |  |  | 43580.75 | 73 | 73
2019-04-25 18:30 | 70 | 58 |  |  | 43580.7708 | 73 | 73
2019-04-25 19:00 | 72 | 60 |  |  | 43580.7917 | 74 | 74
2019-04-25 19:30 | 73 | 61 |  |  | 43580.8125 | 74 | 74
2019-04-25 20:00 | 73 | 60 |  |  | 43580.8333 | 73 | 73
2019-04-25 20:30 | 71 | 58 |  |  | 43580.8542 | 71 | 71
2019-04-25 21:00 | 68 | 54 |  |  | 43580.875 | 67 | 67
2019-04-25 21:30 | 68 | 53 |  |  | 43580.8958 | 66 | 66
2019-04-25 22:00 | 67 | 52 |  |  | 43580.9167 | 66 | 66
2019-04-25 22:30 | 68 | 52 |  |  | 43580.9375 | 67 | 67
2019-04-25 23:00 | 67 | 51 |  |  | 43580.9583 | 64 | 64
2019-04-25 23:30 | 65 | 49 |  |  | 43580.9792 | 62 | 62
2019-04-26 | 62 | 44 |  |  | 43581 | 57 | 57
2019-04-26 00:30 | 61 | 42 |  |  | 43581.0208 | 54 | 54
2019-04-26 01:00 | 59 | 39 |  |  | 43581.0417 | 50 | 50
2019-04-26 01:30 | 57 | 38 |  |  | 43581.0625 | 48 | 48
2019-04-26 02:00 | 56 | 37 |  |  | 43581.0833 | 47 | 47
2019-04-26 02:30 | 57 | 38 |  |  | 43581.1042 | 48 | 48
2019-04-26 03:00 | 59 | 40 |  |  | 43581.125 | 49 | 49
2019-04-26 03:30 | 59 | 41 |  |  | 43581.1458 | 50 | 50
2019-04-26 04:00 | 60 | 42 |  |  | 43581.1667 | 51 | 51
2019-04-26 04:30 | 61 | 44 |  |  | 43581.1875 | 54 | 54
2019-04-26 05:00 | 62 | 45 |  |  | 43581.2083 | 54 | 54
2019-04-26 05:30 | 63 | 47 |  |  | 43581.2292 | 58 | 58
2019-04-26 06:00 | 65 | 50 |  |  | 43581.25 | 62 | 62
2019-04-26 06:30 | 67 | 54 |  |  | 43581.2708 | 70 | 70
2019-04-26 07:00 | 70 | 57 |  |  | 43581.2917 | 74 | 74
2019-04-26 07:30 | 70 | 58 |  |  | 43581.3125 | 78 | 78
2019-04-26 08:00 | 70 | 59 |  |  | 43581.3333 | 81 | 81
2019-04-26 08:30 | 69 | 57 |  |  | 43581.3542 | 82 | 82
2019-04-26 09:00 | 67 | 55 |  |  | 43581.375 | 77 | 77
2019-04-26 09:30 | 66 | 55 |  |  | 43581.3958 | 81 | 80
2019-04-26 10:00 | 70 | 60 |  |  | 43581.4167 | 83 | 82
2019-04-26 10:30 | 73 | 63 |  |  | 43581.4375 | 86 | 86
2019-04-26 11:00 | 74 | 64 |  |  | 43581.4583 | 88 | 87
2019-04-26 11:30 | 73 | 62 |  |  | 43581.4792 | 84 | 84
2019-04-26 12:00 | 72 | 61 |  |  | 43581.5 | 83 | 83
2019-04-26 12:30 | 73 | 62 |  |  | 43581.5208 | 84 | 84
2019-04-26 13:00 | 76 | 65 |  |  | 43581.5417 | 86 | 86
2019-04-26 13:30 | 73 | 61 |  |  | 43581.5625 | 84 | 84
2019-04-26 14:00 | 70 | 58 |  |  | 43581.5833 | 76 | 76
2019-04-26 14:30 | 71 | 60 |  |  | 43581.6042 | 81 | 81
2019-04-26 15:00 | 74 | 63 |  |  | 43581.625 | 85 | 85
2019-04-26 15:30 | 70 | 58 |  |  | 43581.6458 | 80 | 80
2019-04-26 16:00 | 74 | 63 |  |  | 43581.6667 | 83 | 83
2019-04-26 16:30 | 73 | 62 |  |  | 43581.6875 | 81 | 81
2019-04-26 17:00 | 71 | 59 |  |  | 43581.7083 | 77 | 77
2019-04-26 17:30 | 72 | 60 |  |  | 43581.7292 | 77 | 77
2019-04-26 18:00 | 71 | 60 |  |  | 43581.75 | 76 | 76
2019-04-26 18:30 | 71 | 58 |  |  | 43581.7708 | 73 | 73
2019-04-26 19:00 | 72 | 58 |  |  | 43581.7917 | 73 | 73
2019-04-26 19:30 | 71 | 58 |  |  | 43581.8125 | 72 | 72
2019-04-26 20:00 | 71 | 58 |  |  | 43581.8333 | 72 | 72
2019-04-26 20:30 | 70 | 58 |  |  | 43581.8542 | 72 | 72
2019-04-26 21:00 | 68 | 56 |  |  | 43581.875 | 69 | 69
2019-04-26 21:30 | 66 | 54 |  |  | 43581.8958 | 66 | 66
2019-04-26 22:00 | 65 | 52 |  |  | 43581.9167 | 66 | 66
2019-04-26 22:30 | 66 | 52 |  |  | 43581.9375 | 67 | 67
2019-04-26 23:00 | 67 | 53 |  |  | 43581.9583 | 65 | 65
2019-04-26 23:30 | 65 | 50 |  |  | 43581.9792 | 63 | 63
2019-04-27 | 62 | 46 |  |  | 43582 | 59 | 58
2019-04-27 00:30 | 60 | 42 |  |  | 43582.0208 | 55 | 55
2019-04-27 01:00 | 58 | 40 |  |  | 43582.0417 | 51 | 51
2019-04-27 01:30 | 57 | 37 |  |  | 43582.0625 | 48 | 48
2019-04-27 02:00 | 56 | 35 |  |  | 43582.0833 | 46 | 45
2019-04-27 02:30 | 56 | 35 |  |  | 43582.1042 | 45 | 45
2019-04-27 03:00 | 55 | 34 |  |  | 43582.125 | 43 | 43
2019-04-27 03:30 | 53 | 33 |  |  | 43582.1458 | 43 | 43
2019-04-27 04:00 | 53 | 33 |  |  | 43582.1667 | 43 | 43
2019-04-27 04:30 | 53 | 34 |  |  | 43582.1875 | 44 | 44
2019-04-27 05:00 | 53 | 34 |  |  | 43582.2083 | 44 | 44
2019-04-27 05:30 | 55 | 36 |  |  | 43582.2292 | 45 | 45
2019-04-27 06:00 | 56 | 38 |  |  | 43582.25 | 48 | 48
2019-04-27 06:30 | 57 | 40 |  |  | 43582.2708 | 52 | 52
2019-04-27 07:00 | 58 | 41 |  |  | 43582.2917 | 54 | 54
2019-04-27 07:30 | 57 | 41 |  |  | 43582.3125 | 55 | 55
2019-04-27 08:00 | 55 | 38 |  |  | 43582.3333 | 53 | 53
2019-04-27 08:30 | 54 | 38 |  |  | 43582.3542 | 54 | 54
2019-04-27 09:00 | 52 | 37 |  |  | 43582.375 | 53 | 53
2019-04-27 09:30 | 50 | 35 |  |  | 43582.3958 | 52 | 51
2019-04-27 10:00 | 50 | 35 |  |  | 43582.4167 | 51 | 51
2019-04-27 10:30 | 49 | 33 |  |  | 43582.4375 | 49 | 49
2019-04-27 11:00 | 50 | 33 |  |  | 43582.4583 | 49 | 49
2019-04-27 11:30 | 51 | 35 |  |  | 43582.4792 | 52 | 51
2019-04-27 12:00 | 50 | 35 |  |  | 43582.5 | 52 | 52
2019-04-27 12:30 | 49 | 34 |  |  | 43582.5208 | 50 | 49
2019-04-27 13:00 | 51 | 36 |  |  | 43582.5417 | 52 | 52
2019-04-27 13:30 | 51 | 37 |  |  | 43582.5625 | 51 | 50
2019-04-27 14:00 | 54 | 41 |  |  | 43582.5833 | 51 | 50
2019-04-27 14:30 | 54 | 41 |  |  | 43582.6042 | 54 | 54
2019-04-27 15:00 | 56 | 44 |  |  | 43582.625 | 56 | 56
2019-04-27 15:30 | 59 | 46 |  |  | 43582.6458 | 58 | 58
2019-04-27 16:00 | 61 | 49 |  |  | 43582.6667 | 63 | 63
2019-04-27 16:30 | 62 | 50 |  |  | 43582.6875 | 64 | 64
2019-04-27 17:00 | 63 | 51 |  |  | 43582.7083 | 66 | 65
2019-04-27 17:30 | 63 | 51 |  |  | 43582.7292 | 65 | 65
2019-04-27 18:00 | 64 | 52 |  |  | 43582.75 | 66 | 66
2019-04-27 18:30 | 66 | 53 |  |  | 43582.7708 | 67 | 67
2019-04-27 19:00 | 66 | 53 |  |  | 43582.7917 | 67 | 66
2019-04-27 19:30 | 67 | 53 |  |  | 43582.8125 | 67 | 67
2019-04-27 20:00 | 66 | 54 |  |  | 43582.8333 | 68 | 68
2019-04-27 20:30 | 66 | 54 |  |  | 43582.8542 | 69 | 69
2019-04-27 21:00 | 66 | 54 |  |  | 43582.875 | 67 | 67
2019-04-27 21:30 | 66 | 52 |  |  | 43582.8958 | 65 | 65
2019-04-27 22:00 | 64 | 50 |  |  | 43582.9167 | 65 | 65
2019-04-27 22:30 | 63 | 49 |  |  | 43582.9375 | 64 | 64
2019-04-27 23:00 | 63 | 49 |  |  | 43582.9583 | 62 | 62
2019-04-27 23:30 | 63 | 46 |  |  | 43582.9792 | 59 | 59
2019-04-28 | 61 | 43 |  |  | 43583 | 56 | 56
2019-04-28 00:30 | 59 | 39 |  |  | 43583.0208 | 52 | 52
2019-04-28 01:00 | 57 | 37 |  |  | 43583.0417 | 49 | 48
2019-04-28 01:30 | 57 | 36 |  |  | 43583.0625 | 46 | 46
2019-04-28 02:00 | 57 | 33 |  |  | 43583.0833 | 44 | 44
2019-04-28 02:30 | 57 | 32 |  |  | 43583.1042 | 43 | 43
2019-04-28 03:00 | 57 | 32 |  |  | 43583.125 | 42 | 42
2019-04-28 03:30 | 58 | 33 |  |  | 43583.1458 | 43 | 43
2019-04-28 04:00 | 58 | 33 |  |  | 43583.1667 | 43 | 43
2019-04-28 04:30 | 58 | 33 |  |  | 43583.1875 | 43 | 43
2019-04-28 05:00 | 58 | 33 |  |  | 43583.2083 | 45 | 44
2019-04-28 05:30 | 59 | 35 |  |  | 43583.2292 | 46 | 46
2019-04-28 06:00 | 59 | 35 |  |  | 43583.25 | 47 | 47
2019-04-28 06:30 | 60 | 36 |  |  | 43583.2708 | 48 | 48
2019-04-28 07:00 | 60 | 35 |  |  | 43583.2917 | 48 | 48
2019-04-28 07:30 | 58 | 33 |  |  | 43583.3125 | 46 | 46
2019-04-28 08:00 | 54 | 28 |  |  | 43583.3333 | 43 | 43
2019-04-28 08:30 | 53 | 28 |  |  | 43583.3542 | 43 | 43
2019-04-28 09:00 | 52 | 28 |  |  | 43583.375 | 43 | 43
2019-04-28 09:30 | 52 | 29 |  |  | 43583.3958 | 45 | 45
2019-04-28 10:00 | 52 | 30 |  |  | 43583.4167 | 46 | 46
2019-04-28 10:30 | 53 | 31 |  |  | 43583.4375 | 45 | 45
2019-04-28 11:00 | 54 | 32 |  |  | 43583.4583 | 47 | 46
2019-04-28 11:30 | 53 | 32 |  |  | 43583.4792 | 47 | 46
2019-04-28 12:00 | 52 | 30 |  |  | 43583.5 | 45 | 45
2019-04-28 12:30 | 51 | 29 |  |  | 43583.5208 | 44 | 43
2019-04-28 13:00 | 51 | 31 |  |  | 43583.5417 | 46 | 45
2019-04-28 13:30 | 53 | 34 |  |  | 43583.5625 | 48 | 48
2019-04-28 14:00 | 53 | 35 |  |  | 43583.5833 | 48 | 48
2019-04-28 14:30 | 54 | 35 |  |  | 43583.6042 | 49 | 49
2019-04-28 15:00 | 56 | 39 |  |  | 43583.625 | 53 | 53
2019-04-28 15:30 | 59 | 43 |  |  | 43583.6458 | 57 | 56
2019-04-28 16:00 | 65 | 50 |  |  | 43583.6667 | 64 | 63
2019-04-28 16:30 | 64 | 49 |  |  | 43583.6875 | 63 | 63
2019-04-28 17:00 | 66 | 52 |  |  | 43583.7083 | 66 | 65
2019-04-28 17:30 | 68 | 53 |  |  | 43583.7292 | 66 | 66
2019-04-28 18:00 | 72 | 56 |  |  | 43583.75 | 70 | 70
2019-04-28 18:30 | 71 | 56 |  |  | 43583.7708 | 70 | 70
2019-04-28 19:00 | 71 | 56 |  |  | 43583.7917 | 70 | 70
2019-04-28 19:30 | 70 | 54 |  |  | 43583.8125 | 68 | 68
2019-04-28 20:00 | 68 | 52 |  |  | 43583.8333 | 66 | 66
2019-04-28 20:30 | 69 | 53 |  |  | 43583.8542 | 68 | 68
2019-04-28 21:00 | 66 | 49 |  |  | 43583.875 | 63 | 63
2019-04-28 21:30 | 64 | 46 |  |  | 43583.8958 | 59 | 59
2019-04-28 22:00 | 65 | 47 |  |  | 43583.9167 | 61 | 61
2019-04-28 22:30 | 65 | 46 |  |  | 43583.9375 | 61 | 61
2019-04-28 23:00 | 65 | 46 |  |  | 43583.9583 | 58 | 58
2019-04-28 23:30 | 64 | 43 |  |  | 43583.9792 | 56 | 56
2019-04-29 | 60 | 39 |  |  | 43584 | 53 | 53
2019-04-29 00:30 | 60 | 38 |  |  | 43584.0208 | 49 | 49
2019-04-29 01:00 | 58 | 36 |  |  | 43584.0417 | 48 | 48
2019-04-29 01:30 | 57 | 34 |  |  | 43584.0625 | 45 | 45
2019-04-29 02:00 | 57 | 33 |  |  | 43584.0833 | 44 | 44
2019-04-29 02:30 | 57 | 33 |  |  | 43584.1042 | 44 | 43
2019-04-29 03:00 | 59 | 35 |  |  | 43584.125 | 45 | 45
2019-04-29 03:30 | 60 | 35 |  |  | 43584.1458 | 45 | 45
2019-04-29 04:00 | 58 | 35 |  |  | 43584.1667 | 44 | 44
2019-04-29 04:30 | 59 | 35 |  |  | 43584.1875 | 46 | 46
2019-04-29 05:00 | 60 | 39 |  |  | 43584.2083 | 49 | 49
2019-04-29 05:30 | 63 | 44 |  |  | 43584.2292 | 54 | 54
2019-04-29 06:00 | 66 | 51 |  |  | 43584.25 | 61 | 61
2019-04-29 06:30 | 70 | 57 |  |  | 43584.2708 | 71 | 71
2019-04-29 07:00 | 71 | 60 |  |  | 43584.2917 | 78 | 77
2019-04-29 07:30 | 76 | 61 |  |  | 43584.3125 | 84 | 82
2019-04-29 08:00 | 78 | 61 |  |  | 43584.3333 | 85 | 83
2019-04-29 08:30 | 80 | 64 |  |  | 43584.3542 | 89 | 88
2019-04-29 09:00 | 79 | 62 |  |  | 43584.375 | 88 | 86
2019-04-29 09:30 | 78 | 62 |  |  | 43584.3958 | 87 | 85
2019-04-29 10:00 | 80 | 66 |  |  | 43584.4167 | 90 | 87
2019-04-29 10:30 | 79 | 64 |  |  | 43584.4375 | 87 | 85
2019-04-29 11:00 | 77 | 62 |  |  | 43584.4583 | 89 | 86
2019-04-29 11:30 | 79 | 65 |  |  | 43584.4792 | 91 | 88
2019-04-29 12:00 | 81 | 67 |  |  | 43584.5 | 88 | 85
2019-04-29 12:30 | 76 | 60 |  |  | 43584.5208 | 85 | 83
2019-04-29 13:00 | 77 | 61 |  |  | 43584.5417 | 83 | 80
2019-04-29 13:30 | 73 | 56 |  |  | 43584.5625 | 82 | 79
2019-04-29 14:00 | 74 | 58 |  |  | 43584.5833 | 85 | 82
2019-04-29 14:30 | 75 | 60 |  |  | 43584.6042 | 84 | 81
2019-04-29 15:00 | 73 | 57 |  |  | 43584.625 | 84 | 82
2019-04-29 15:30 | 74 | 58 |  |  | 43584.6458 | 83 | 81
2019-04-29 16:00 | 76 | 61 |  |  | 43584.6667 | 85 | 83
2019-04-29 16:30 | 79 | 62 |  |  | 43584.6875 | 83 | 81
2019-04-29 17:00 | 81 | 64 |  |  | 43584.7083 | 86 | 84
2019-04-29 17:30 | 83 | 67 |  |  | 43584.7292 | 87 | 86
2019-04-29 18:00 | 85 | 69 |  |  | 43584.75 | 88 | 87
2019-04-29 18:30 | 85 | 67 |  |  | 43584.7708 | 85 | 84
2019-04-29 19:00 | 85 | 67 |  |  | 43584.7917 | 85 | 84
2019-04-29 19:30 | 81 | 64 |  |  | 43584.8125 | 82 | 81
2019-04-29 20:00 | 82 | 63 |  |  | 43584.8333 | 80 | 79
2019-04-29 20:30 | 82 | 63 |  |  | 43584.8542 | 79 | 78
2019-04-29 21:00 | 80 | 59 |  |  | 43584.875 | 75 | 74
2019-04-29 21:30 | 63 | 55 |  |  | 43584.8958 | 69 | 69
2019-04-29 22:00 | 61 | 53 |  |  | 43584.9167 | 68 | 67
2019-04-29 22:30 | 59 | 50 |  |  | 43584.9375 | 65 | 64
2019-04-29 23:00 | 58 | 49 |  |  | 43584.9583 | 62 | 61
2019-04-29 23:30 | 58 | 47 |  |  | 43584.9792 | 62 | 60
2019-04-30 | 56 | 44 |  |  | 43585 | 59 | 57
2019-04-30 00:30 | 54 | 42 |  |  | 43585.0208 | 56 | 53
2019-04-30 01:00 | 52 | 38 |  |  | 43585.0417 | 51 | 48
2019-04-30 01:30 | 51 | 37 |  |  | 43585.0625 | 50 | 47
2019-04-30 02:00 | 51 | 37 |  |  | 43585.0833 | 49 | 47
2019-04-30 02:30 | 48 | 34 |  |  | 43585.1042 | 46 | 44
2019-04-30 03:00 | 48 | 34 |  |  | 43585.125 | 46 | 43
2019-04-30 03:30 | 48 | 34 |  |  | 43585.1458 | 46 | 44
2019-04-30 04:00 | 49 | 36 |  |  | 43585.1667 | 47 | 45
2019-04-30 04:30 | 49 | 36 |  |  | 43585.1875 | 47 | 45
2019-04-30 05:00 | 50 | 37 |  |  | 43585.2083 | 50 | 48
2019-04-30 05:30 | 54 | 43 |  |  | 43585.2292 | 55 | 54
2019-04-30 06:00 | 58 | 49 |  |  | 43585.25 | 62 | 62
2019-04-30 06:30 | 62 | 55 |  |  | 43585.2708 | 73 | 73
2019-04-30 07:00 | 75 | 69 |  |  | 43585.2917 | 92 | 91
2019-04-30 07:30 | 76 | 70 |  |  | 43585.3125 | 95 | 95
2019-04-30 08:00 | 75 | 69 |  |  | 43585.3333 | 94 | 94
2019-04-30 08:30 | 71 | 65 |  |  | 43585.3542 | 92 | 92
2019-04-30 09:00 | 68 | 62 |  |  | 43585.375 | 91 | 91
2019-04-30 09:30 | 68 | 62 |  |  | 43585.3958 | 88 | 88
2019-04-30 10:00 | 66 | 59 |  |  | 43585.4167 | 87 | 87
2019-04-30 10:30 | 72 | 64 |  |  | 43585.4375 | 97 | 96
2019-04-30 11:00 | 82 | 73 |  |  | 43585.4583 | 101 | 99
2019-04-30 11:30 | 76 | 66 |  |  | 43585.4792 | 96 | 93
2019-04-30 12:00 | 75 | 65 |  |  | 43585.5 | 94 | 91
2019-04-30 12:30 | 79 | 70 |  |  | 43585.5208 | 95 | 93
2019-04-30 13:00 | 77 | 68 |  |  | 43585.5417 | 94 | 91
2019-04-30 13:30 | 77 | 68 |  |  | 43585.5625 | 95 | 92
2019-04-30 14:00 | 76 | 67 |  |  | 43585.5833 | 94 | 91
2019-04-30 14:30 | 79 | 70 |  |  | 43585.6042 | 98 | 96
2019-04-30 15:00 | 78 | 69 |  |  | 43585.625 | 94 | 91
2019-04-30 15:30 | 78 | 68 |  |  | 43585.6458 | 95 | 92
2019-04-30 16:00 | 80 | 70 |  |  | 43585.6667 | 99 | 95
2019-04-30 16:30 | 80 | 69 |  |  | 43585.6875 | 97 | 93
2019-04-30 17:00 | 82 | 71 |  |  | 43585.7083 | 98 | 94
2019-04-30 17:30 | 85 | 73 |  |  | 43585.7292 | 101 | 95
2019-04-30 18:00 | 89 | 78 |  |  | 43585.75 | 105 | 98
2019-04-30 18:30 | 87 | 75 |  |  | 43585.7708 | 100 | 93
2019-04-30 19:00 | 86 | 74 |  |  | 43585.7917 | 99 | 93
2019-04-30 19:30 | 84 | 74 |  |  | 43585.8125 | 97 | 92
2019-04-30 20:00 | 82 | 72 |  |  | 43585.8333 | 93 | 89
2019-04-30 20:30 | 81 | 69 |  |  | 43585.8542 | 92 | 86
2019-04-30 21:00 | 79 | 67 |  |  | 43585.875 | 89 | 83
2019-04-30 21:30 | 72 | 59 |  |  | 43585.8958 | 80 | 75
2019-04-30 22:00 | 64 | 54 |  |  | 43585.9167 | 70 | 68
2019-04-30 22:30 | 63 | 52 |  |  | 43585.9375 | 69 | 67
2019-04-30 23:00 | 63 | 52 |  |  | 43585.9583 | 67 | 65
2019-04-30 23:30 | 61 | 49 |  |  | 43585.9792 | 65 | 62
2019-05-01 | 59 | 44 |  |  | 43586 | 61 | 58
2019-05-01 00:30 | 58 | 42 |  |  | 43586.0208 | 59 | 54
2019-05-01 01:00 | 56 | 40 |  |  | 43586.0417 | 55 | 50
2019-05-01 01:30 | 54 | 36 |  |  | 43586.0625 | 52 | 47
2019-05-01 02:00 | 54 | 36 |  |  | 43586.0833 | 52 | 47
2019-05-01 02:30 | 56 | 37 |  |  | 43586.1042 | 52 | 47
2019-05-01 03:00 | 55 | 37 |  |  | 43586.125 | 53 | 47
2019-05-01 03:30 | 56 | 37 |  |  | 43586.1458 | 54 | 49
2019-05-01 04:00 | 56 | 37 |  |  | 43586.1667 | 54 | 48
2019-05-01 04:30 | 56 | 38 |  |  | 43586.1875 | 53 | 48
2019-05-01 05:00 | 57 | 40 |  |  | 43586.2083 | 55 | 50
2019-05-01 05:30 | 60 | 45 |  |  | 43586.2292 | 60 | 56
2019-05-01 06:00 | 62 | 50 |  |  | 43586.25 | 65 | 62
2019-05-01 06:30 | 63 | 54 |  |  | 43586.2708 | 72 | 70
2019-05-01 07:00 | 67 | 57 |  |  | 43586.2917 | 78 | 76
2019-05-01 07:30 | 69 | 60 |  |  | 43586.3125 | 81 | 80
2019-05-01 08:00 | 65 | 56 |  |  | 43586.3333 | 81 | 80
2019-05-01 08:30 | 62 | 53 |  |  | 43586.3542 | 82 | 81
2019-05-01 09:00 | 70 | 64 |  |  | 43586.375 | 102 | 102
2019-05-01 09:30 | 68 | 63 |  |  | 43586.3958 | 104 | 104
2019-05-01 10:00 | 63 | 53 |  |  | 43586.4167 | 86 | 85
2019-05-01 10:30 | 58 | 47 |  |  | 43586.4375 | 75 | 73
2019-05-01 11:00 | 59 | 48 |  |  | 43586.4583 | 71 | 69
2019-05-01 11:30 | 54 | 43 |  |  | 43586.4792 | 65 | 64
2019-05-01 12:00 | 54 | 42 |  |  | 43586.5 | 64 | 62
2019-05-01 12:30 | 57 | 46 |  |  | 43586.5208 | 67 | 65
2019-05-01 13:00 | 60 | 50 |  |  | 43586.5417 | 72 | 70
2019-05-01 13:30 | 58 | 47 |  |  | 43586.5625 | 72 | 70
2019-05-01 14:00 | 56 | 45 |  |  | 43586.5833 | 71 | 69
2019-05-01 14:30 | 58 | 47 |  |  | 43586.6042 | 74 | 72
2019-05-01 15:00 | 60 | 49 |  |  | 43586.625 | 76 | 74
2019-05-01 15:30 | 61 | 49 |  |  | 43586.6458 | 75 | 73
2019-05-01 16:00 | 65 | 54 |  |  | 43586.6667 | 80 | 78
2019-05-01 16:30 | 72 | 63 |  |  | 43586.6875 | 85 | 82
2019-05-01 17:00 | 76 | 67 |  |  | 43586.7083 | 88 | 85
2019-05-01 17:30 | 75 | 65 |  |  | 43586.7292 | 86 | 83
2019-05-01 18:00 | 77 | 66 |  |  | 43586.75 | 88 | 83
2019-05-01 18:30 | 77 | 65 |  |  | 43586.7708 | 85 | 80
2019-05-01 19:00 | 78 | 65 |  |  | 43586.7917 | 85 | 80
2019-05-01 19:30 | 76 | 62 |  |  | 43586.8125 | 83 | 77
2019-05-01 20:00 | 74 | 61 |  |  | 43586.8333 | 80 | 74
2019-05-01 20:30 | 75 | 61 |  |  | 43586.8542 | 81 | 74
2019-05-01 21:00 | 74 | 59 |  |  | 43586.875 | 80 | 73
2019-05-01 21:30 | 70 | 56 |  |  | 43586.8958 | 75 | 69
2019-05-01 22:00 | 64 | 55 |  |  | 43586.9167 | 71 | 69
2019-05-01 22:30 | 63 | 54 |  |  | 43586.9375 | 69 | 69
2019-05-01 23:00 | 61 | 52 |  |  | 43586.9583 | 66 | 65
2019-05-01 23:30 | 59 | 49 |  |  | 43586.9792 | 63 | 62
2019-05-02 | 56 | 44 |  |  | 43587 | 58 | 57
2019-05-02 00:30 | 53 | 41 |  |  | 43587.0208 | 54 | 52
2019-05-02 01:00 | 53 | 39 |  |  | 43587.0417 | 52 | 50
2019-05-02 01:30 | 53 | 38 |  |  | 43587.0625 | 50 | 48
2019-05-02 02:00 | 51 | 36 |  |  | 43587.0833 | 48 | 45
2019-05-02 02:30 | 51 | 35 |  |  | 43587.1042 | 48 | 45
2019-05-02 03:00 | 51 | 36 |  |  | 43587.125 | 48 | 45
2019-05-02 03:30 | 51 | 35 |  |  | 43587.1458 | 48 | 45
2019-05-02 04:00 | 50 | 33 |  |  | 43587.1667 | 47 | 44
2019-05-02 04:30 | 52 | 36 |  |  | 43587.1875 | 50 | 47
2019-05-02 05:00 | 53 | 39 |  |  | 43587.2083 | 53 | 50
2019-05-02 05:30 | 59 | 46 |  |  | 43587.2292 | 59 | 57
2019-05-02 06:00 | 62 | 53 |  |  | 43587.25 | 65 | 64
2019-05-02 06:30 | 65 | 57 |  |  | 43587.2708 | 73 | 72
2019-05-02 07:00 | 65 | 59 |  |  | 43587.2917 | 76 | 75
2019-05-02 07:30 | 66 | 59 |  |  | 43587.3125 | 78 | 78
2019-05-02 08:00 | 63 | 56 |  |  | 43587.3333 | 76 | 75
2019-05-02 08:30 | 59 | 53 |  |  | 43587.3542 | 73 | 73
2019-05-02 09:00 | 57 | 52 |  |  | 43587.375 | 73 | 73
2019-05-02 09:30 | 60 | 54 |  |  | 43587.3958 | 75 | 75
2019-05-02 10:00 | 64 | 59 |  |  | 43587.4167 | 84 | 84
2019-05-02 10:30 | 62 | 56 |  |  | 43587.4375 | 77 | 76
2019-05-02 11:00 | 63 | 58 |  |  | 43587.4583 | 76 | 76
2019-05-02 11:30 | 63 | 58 |  |  | 43587.4792 | 77 | 77
2019-05-02 12:00 | 67 | 62 |  |  | 43587.5 | 84 | 83
2019-05-02 12:30 | 66 | 60 |  |  | 43587.5208 | 83 | 83
2019-05-02 13:00 | 59 | 53 |  |  | 43587.5417 | 75 | 75
2019-05-02 13:30 | 59 | 54 |  |  | 43587.5625 | 76 | 76
2019-05-02 14:00 | 61 | 55 |  |  | 43587.5833 | 74 | 74
2019-05-02 14:30 | 61 | 56 |  |  | 43587.6042 | 76 | 76
2019-05-02 15:00 | 61 | 55 |  |  | 43587.625 | 75 | 75
2019-05-02 15:30 | 63 | 57 |  |  | 43587.6458 | 75 | 75
2019-05-02 16:00 | 65 | 59 |  |  | 43587.6667 | 80 | 80
2019-05-02 16:30 | 67 | 60 |  |  | 43587.6875 | 79 | 79
2019-05-02 17:00 | 68 | 62 |  |  | 43587.7083 | 79 | 79
2019-05-02 17:30 | 71 | 64 |  |  | 43587.7292 | 80 | 80
2019-05-02 18:00 | 73 | 66 |  |  | 43587.75 | 82 | 81
2019-05-02 18:30 | 72 | 66 |  |  | 43587.7708 | 79 | 79
2019-05-02 19:00 | 74 | 66 |  |  | 43587.7917 | 80 | 79
2019-05-02 19:30 | 72 | 65 |  |  | 43587.8125 | 78 | 77
2019-05-02 20:00 | 71 | 64 |  |  | 43587.8333 | 77 | 77
2019-05-02 20:30 | 69 | 62 |  |  | 43587.8542 | 75 | 75
2019-05-02 21:00 | 64 | 57 |  |  | 43587.875 | 69 | 69
2019-05-02 21:30 | 62 | 55 |  |  | 43587.8958 | 66 | 66
2019-05-02 22:00 | 62 | 54 |  |  | 43587.9167 | 67 | 67
2019-05-02 22:30 | 61 | 53 |  |  | 43587.9375 | 66 | 65
2019-05-02 23:00 | 60 | 50 |  |  | 43587.9583 | 62 | 61
2019-05-02 23:30 | 58 | 47 |  |  | 43587.9792 | 60 | 58
2019-05-03 | 56 | 44 |  |  | 43588 | 56 | 55
2019-05-03 00:30 | 53 | 40 |  |  | 43588.0208 | 52 | 50
2019-05-03 01:00 | 50 | 36 |  |  | 43588.0417 | 48 | 47
2019-05-03 01:30 | 50 | 36 |  |  | 43588.0625 | 47 | 46
2019-05-03 02:00 | 49 | 35 |  |  | 43588.0833 | 46 | 44
2019-05-03 02:30 | 50 | 35 |  |  | 43588.1042 | 47 | 45
2019-05-03 03:00 | 50 | 35 |  |  | 43588.125 | 46 | 45
2019-05-03 03:30 | 50 | 36 |  |  | 43588.1458 | 46 | 44
2019-05-03 04:00 | 51 | 36 |  |  | 43588.1667 | 47 | 46
2019-05-03 04:30 | 50 | 38 |  |  | 43588.1875 | 49 | 48
2019-05-03 05:00 | 53 | 42 |  |  | 43588.2083 | 52 | 51
2019-05-03 05:30 | 56 | 47 |  |  | 43588.2292 | 57 | 57
2019-05-03 06:00 | 60 | 53 |  |  | 43588.25 | 63 | 63
2019-05-03 06:30 | 64 | 57 |  |  | 43588.2708 | 71 | 70
2019-05-03 07:00 | 63 | 58 |  |  | 43588.2917 | 75 | 75
2019-05-03 07:30 | 61 | 56 |  |  | 43588.3125 | 75 | 75
2019-05-03 08:00 | 60 | 55 |  |  | 43588.3333 | 74 | 74
2019-05-03 08:30 | 56 | 52 |  |  | 43588.3542 | 74 | 73
2019-05-03 09:00 | 55 | 52 |  |  | 43588.375 | 74 | 74
2019-05-03 09:30 | 55 | 52 |  |  | 43588.3958 | 71 | 71
2019-05-03 10:00 | 52 | 49 |  |  | 43588.4167 | 70 | 70
2019-05-03 10:30 | 57 | 54 |  |  | 43588.4375 | 75 | 75
2019-05-03 11:00 | 59 | 56 |  |  | 43588.4583 | 79 | 79
2019-05-03 11:30 | 58 | 55 |  |  | 43588.4792 | 79 | 79
2019-05-03 12:00 | 58 | 55 |  |  | 43588.5 | 81 | 81
2019-05-03 12:30 | 62 | 59 |  |  | 43588.5208 | 81 | 81
2019-05-03 13:00 | 63 | 61 |  |  | 43588.5417 | 77 | 77
2019-05-03 13:30 | 55 | 52 |  |  | 43588.5625 | 71 | 71
2019-05-03 14:00 | 52 | 47 |  |  | 43588.5833 | 66 | 65
2019-05-03 14:30 | 54 | 50 |  |  | 43588.6042 | 72 | 72
2019-05-03 15:00 | 59 | 55 |  |  | 43588.625 | 75 | 75
2019-05-03 15:30 | 62 | 58 |  |  | 43588.6458 | 76 | 76
2019-05-03 16:00 | 65 | 61 |  |  | 43588.6667 | 80 | 80
2019-05-03 16:30 | 66 | 61 |  |  | 43588.6875 | 79 | 79
2019-05-03 17:00 | 67 | 62 |  |  | 43588.7083 | 79 | 79
2019-05-03 17:30 | 67 | 63 |  |  | 43588.7292 | 79 | 79
2019-05-03 18:00 | 67 | 62 |  |  | 43588.75 | 78 | 78
2019-05-03 18:30 | 66 | 60 |  |  | 43588.7708 | 75 | 75
2019-05-03 19:00 | 66 | 61 |  |  | 43588.7917 | 75 | 75
2019-05-03 19:30 | 63 | 58 |  |  | 43588.8125 | 73 | 73
2019-05-03 20:00 | 61 | 56 |  |  | 43588.8333 | 70 | 70
2019-05-03 20:30 | 59 | 54 |  |  | 43588.8542 | 68 | 68
2019-05-03 21:00 | 56 | 51 |  |  | 43588.875 | 64 | 64
2019-05-03 21:30 | 57 | 51 |  |  | 43588.8958 | 64 | 64
2019-05-03 22:00 | 58 | 50 |  |  | 43588.9167 | 63 | 63
2019-05-03 22:30 | 57 | 47 |  |  | 43588.9375 | 62 | 62
2019-05-03 23:00 | 56 | 46 |  |  | 43588.9583 | 59 | 58
2019-05-03 23:30 | 55 | 44 |  |  | 43588.9792 | 58 | 57
2019-05-04 | 54 | 43 |  |  | 43589 | 57 | 56
2019-05-04 00:30 | 54 | 41 |  |  | 43589.0208 | 53 | 52
2019-05-04 01:00 | 54 | 41 |  |  | 43589.0417 | 52 | 51
2019-05-04 01:30 | 53 | 39 |  |  | 43589.0625 | 51 | 49
2019-05-04 02:00 | 52 | 38 |  |  | 43589.0833 | 49 | 47
2019-05-04 02:30 | 50 | 35 |  |  | 43589.1042 | 46 | 44
2019-05-04 03:00 | 49 | 33 |  |  | 43589.125 | 45 | 43
2019-05-04 03:30 | 49 | 34 |  |  | 43589.1458 | 46 | 44
2019-05-04 04:00 | 49 | 33 |  |  | 43589.1667 | 46 | 44
2019-05-04 04:30 | 50 | 35 |  |  | 43589.1875 | 48 | 46
2019-05-04 05:00 | 53 | 38 |  |  | 43589.2083 | 50 | 48
2019-05-04 05:30 | 54 | 40 |  |  | 43589.2292 | 52 | 50
2019-05-04 06:00 | 55 | 42 |  |  | 43589.25 | 55 | 53
2019-05-04 06:30 | 58 | 46 |  |  | 43589.2708 | 59 | 58
2019-05-04 07:00 | 59 | 46 |  |  | 43589.2917 | 60 | 59
2019-05-04 07:30 | 58 | 47 |  |  | 43589.3125 | 62 | 61
2019-05-04 08:00 | 57 | 46 |  |  | 43589.3333 | 63 | 62
2019-05-04 08:30 | 57 | 47 |  |  | 43589.3542 | 63 | 62
2019-05-04 09:00 | 58 | 49 |  |  | 43589.375 | 65 | 64
2019-05-04 09:30 | 59 | 50 |  |  | 43589.3958 | 67 | 66
2019-05-04 10:00 | 62 | 50 |  |  | 43589.4167 | 68 | 66
2019-05-04 10:30 | 60 | 49 |  |  | 43589.4375 | 66 | 64
2019-05-04 11:00 | 64 | 53 |  |  | 43589.4583 | 72 | 70
2019-05-04 11:30 | 64 | 53 |  |  | 43589.4792 | 71 | 69
2019-05-04 12:00 | 62 | 49 |  |  | 43589.5 | 67 | 64
2019-05-04 12:30 | 64 | 51 |  |  | 43589.5208 | 68 | 65
2019-05-04 13:00 | 63 | 51 |  |  | 43589.5417 | 69 | 66
2019-05-04 13:30 | 63 | 51 |  |  | 43589.5625 | 68 | 65
2019-05-04 14:00 | 66 | 55 |  |  | 43589.5833 | 69 | 66
2019-05-04 14:30 | 71 | 60 |  |  | 43589.6042 | 76 | 73
2019-05-04 15:00 | 69 | 57 |  |  | 43589.625 | 73 | 70
2019-05-04 15:30 | 69 | 57 |  |  | 43589.6458 | 73 | 69
2019-05-04 16:00 | 71 | 59 |  |  | 43589.6667 | 75 | 72
2019-05-04 16:30 | 70 | 57 |  |  | 43589.6875 | 73 | 70
2019-05-04 17:00 | 69 | 57 |  |  | 43589.7083 | 73 | 69
2019-05-04 17:30 | 70 | 59 |  |  | 43589.7292 | 76 | 72
2019-05-04 18:00 | 67 | 57 |  |  | 43589.75 | 74 | 71
2019-05-04 18:30 | 67 | 56 |  |  | 43589.7708 | 73 | 70
2019-05-04 19:00 | 67 | 56 |  |  | 43589.7917 | 73 | 69
2019-05-04 19:30 | 66 | 54 |  |  | 43589.8125 | 70 | 67
2019-05-04 20:00 | 65 | 53 |  |  | 43589.8333 | 70 | 66
2019-05-04 20:30 | 65 | 52 |  |  | 43589.8542 | 68 | 65
2019-05-04 21:00 | 63 | 50 |  |  | 43589.875 | 66 | 62
2019-05-04 21:30 | 63 | 48 |  |  | 43589.8958 | 64 | 60
2019-05-04 22:00 | 62 | 48 |  |  | 43589.9167 | 64 | 59
2019-05-04 22:30 | 62 | 47 |  |  | 43589.9375 | 64 | 60
2019-05-04 23:00 | 61 | 46 |  |  | 43589.9583 | 62 | 57
2019-05-04 23:30 | 60 | 43 |  |  | 43589.9792 | 60 | 54
2019-05-05 | 59 | 42 |  |  | 43590 | 57 | 53
2019-05-05 00:30 | 55 | 41 |  |  | 43590.0208 | 54 | 52
2019-05-05 01:00 | 54 | 40 |  |  | 43590.0417 | 53 | 51
2019-05-05 01:30 | 53 | 38 |  |  | 43590.0625 | 50 | 49
2019-05-05 02:00 | 52 | 37 |  |  | 43590.0833 | 48 | 47
2019-05-05 02:30 | 51 | 36 |  |  | 43590.1042 | 47 | 46
2019-05-05 03:00 | 52 | 36 |  |  | 43590.125 | 46 | 45
2019-05-05 03:30 | 53 | 37 |  |  | 43590.1458 | 48 | 45
2019-05-05 04:00 | 68 | 38 |  |  | 43590.1667 | 53 | 46
2019-05-05 04:30 | 68 | 39 |  |  | 43590.1875 | 53 | 47
2019-05-05 05:00 | 69 | 39 |  |  | 43590.2083 | 53 | 47
2019-05-05 05:30 | 69 | 39 |  |  | 43590.2292 | 54 | 48
2019-05-05 06:00 | 68 | 38 |  |  | 43590.25 | 53 | 47
2019-05-05 06:30 | 68 | 38 |  |  | 43590.2708 | 55 | 49
2019-05-05 07:00 | 67 | 37 |  |  | 43590.2917 | 54 | 48
2019-05-05 07:30 | 66 | 35 |  |  | 43590.3125 | 53 | 47
2019-05-05 08:00 | 64 | 33 |  |  | 43590.3333 | 50 | 44
2019-05-05 08:30 | 64 | 34 |  |  | 43590.3542 | 50 | 45
2019-05-05 09:00 | 64 | 34 |  |  | 43590.375 | 50 | 45
2019-05-05 09:30 | 62 | 32 |  |  | 43590.3958 | 47 | 42
2019-05-05 10:00 | 59 | 28 |  |  | 43590.4167 | 44 | 39
2019-05-05 10:30 | 59 | 27 |  |  | 43590.4375 | 43 | 38
2019-05-05 11:00 | 57 | 28 |  |  | 43590.4583 | 41 | 38
2019-05-05 11:30 | 51 | 29 |  |  | 43590.4792 | 41 | 40
2019-05-05 12:00 | 43 | 30 |  |  | 43590.5 | 41 | 40
2019-05-05 12:30 | 44 | 30 |  |  | 43590.5208 | 41 | 41
2019-05-05 13:00 | 45 | 32 |  |  | 43590.5417 | 42 | 42
2019-05-05 13:30 | 43 | 30 |  |  | 43590.5625 | 41 | 41
2019-05-05 14:00 | 44 | 31 |  |  | 43590.5833 | 41 | 41
2019-05-05 14:30 | 45 | 32 |  |  | 43590.6042 | 42 | 42
2019-05-05 15:00 | 46 | 34 |  |  | 43590.625 | 44 | 43
2019-05-05 15:30 | 49 | 36 |  |  | 43590.6458 | 47 | 46
2019-05-05 16:00 | 51 | 40 |  |  | 43590.6667 | 51 | 51
2019-05-05 16:30 | 53 | 43 |  |  | 43590.6875 | 55 | 54
2019-05-05 17:00 | 51 | 47 |  |  | 43590.7083 | 59 | 59
2019-05-05 17:30 | 54 | 51 |  |  | 43590.7292 | 63 | 63
2019-05-05 18:00 | 57 | 53 |  |  | 43590.75 | 66 | 66
2019-05-05 18:30 | 58 | 55 |  |  | 43590.7708 | 67 | 67
2019-05-05 19:00 | 59 | 55 |  |  | 43590.7917 | 67 | 67
2019-05-05 19:30 | 55 | 51 |  |  | 43590.8125 | 63 | 63
2019-05-05 20:00 | 54 | 50 |  |  | 43590.8333 | 62 | 62
2019-05-05 20:30 | 53 | 50 |  |  | 43590.8542 | 61 | 61
2019-05-05 21:00 | 52 | 49 |  |  | 43590.875 | 59 | 59
2019-05-05 21:30 | 53 | 50 |  |  | 43590.8958 | 61 | 61
2019-05-05 22:00 | 54 | 50 |  |  | 43590.9167 | 62 | 62
2019-05-05 22:30 | 55 | 51 |  |  | 43590.9375 | 63 | 63
2019-05-05 23:00 | 55 | 51 |  |  | 43590.9583 | 62 | 62
2019-05-05 23:30 | 54 | 50 |  |  | 43590.9792 | 61 | 61
2019-05-06 | 54 | 49 |  |  | 43591 | 60 | 59
2019-05-06 00:30 | 51 | 46 |  |  | 43591.0208 | 56 | 56
2019-05-06 01:00 | 48 | 43 |  |  | 43591.0417 | 53 | 53
2019-05-06 01:30 | 48 | 42 |  |  | 43591.0625 | 52 | 51
2019-05-06 02:00 | 46 | 40 |  |  | 43591.0833 | 50 | 48
2019-05-06 02:30 | 46 | 41 |  |  | 43591.1042 | 52 | 49
2019-05-06 03:00 | 46 | 40 |  |  | 43591.125 | 52 | 49
2019-05-06 03:30 | 46 | 40 |  |  | 43591.1458 | 52 | 49
2019-05-06 04:00 | 47 | 41 |  |  | 43591.1667 | 52 | 49
2019-05-06 04:30 | 47 | 41 |  |  | 43591.1875 | 52 | 49
2019-05-06 05:00 | 48 | 42 |  |  | 43591.2083 | 54 | 51
2019-05-06 05:30 | 49 | 44 |  |  | 43591.2292 | 56 | 53
2019-05-06 06:00 | 51 | 45 |  |  | 43591.25 | 57 | 54
2019-05-06 06:30 | 49 | 43 |  |  | 43591.2708 | 57 | 54
2019-05-06 07:00 | 44 | 38 |  |  | 43591.2917 | 53 | 51
2019-05-06 07:30 | 42 | 35 |  |  | 43591.3125 | 51 | 48
2019-05-06 08:00 | 40 | 33 |  |  | 43591.3333 | 49 | 47
2019-05-06 08:30 | 41 | 36 |  |  | 43591.3542 | 51 | 49
2019-05-06 09:00 | 40 | 35 |  |  | 43591.375 | 49 | 48
2019-05-06 09:30 | 38 | 32 |  |  | 43591.3958 | 47 | 46
2019-05-06 10:00 | 36 | 31 |  |  | 43591.4167 | 45 | 44
2019-05-06 10:30 | 34 | 29 |  |  | 43591.4375 | 42 | 41
2019-05-06 11:00 | 33 | 28 |  |  | 43591.4583 | 40 | 39
2019-05-06 11:30 | 34 | 28 |  |  | 43591.4792 | 41 | 40
2019-05-06 12:00 | 33 | 28 |  |  | 43591.5 | 40 | 39
2019-05-06 12:30 | 34 | 28 |  |  | 43591.5208 | 40 | 39
2019-05-06 13:00 | 34 | 29 |  |  | 43591.5417 | 41 | 40
2019-05-06 13:30 | 35 | 30 |  |  | 43591.5625 | 41 | 40
2019-05-06 14:00 | 35 | 30 |  |  | 43591.5833 | 41 | 40
2019-05-06 14:30 | 37 | 32 |  |  | 43591.6042 | 44 | 43
2019-05-06 15:00 | 38 | 34 |  |  | 43591.625 | 47 | 46
2019-05-06 15:30 | 39 | 36 |  |  | 43591.6458 | 48 | 48
2019-05-06 16:00 | 40 | 37 |  |  | 43591.6667 | 49 | 49
2019-05-06 16:30 | 43 | 39 |  |  | 43591.6875 | 52 | 51
2019-05-06 17:00 | 51 | 43 |  |  | 43591.7083 | 62 | 56
2019-05-06 17:30 | 58 | 49 |  |  | 43591.7292 | 71 | 62
2019-05-06 18:00 | 62 | 53 |  |  | 43591.75 | 76 | 67
2019-05-06 18:30 | 64 | 55 |  |  | 43591.7708 | 77 | 68
2019-05-06 19:00 | 64 | 55 |  |  | 43591.7917 | 77 | 68
2019-05-06 19:30 | 62 | 52 |  |  | 43591.8125 | 75 | 66
2019-05-06 20:00 | 62 | 52 |  |  | 43591.8333 | 74 | 65
2019-05-06 20:30 | 61 | 51 |  |  | 43591.8542 | 74 | 64
2019-05-06 21:00 | 51 | 47 |  |  | 43591.875 | 60 | 58
2019-05-06 21:30 | 48 | 45 |  |  | 43591.8958 | 58 | 56
2019-05-06 22:00 | 52 | 48 |  |  | 43591.9167 | 62 | 61
2019-05-06 22:30 | 52 | 48 |  |  | 43591.9375 | 62 | 60
2019-05-06 23:00 | 51 | 47 |  |  | 43591.9583 | 59 | 57
2019-05-06 23:30 | 49 | 45 |  |  | 43591.9792 | 58 | 56
2019-05-07 | 47 | 41 |  |  | 43592 | 55 | 52
2019-05-07 00:30 | 45 | 38 |  |  | 43592.0208 | 52 | 49
2019-05-07 01:00 | 42 | 35 |  |  | 43592.0417 | 48 | 45
2019-05-07 01:30 | 40 | 33 |  |  | 43592.0625 | 45 | 41
2019-05-07 02:00 | 39 | 31 |  |  | 43592.0833 | 43 | 39
2019-05-07 02:30 | 39 | 32 |  |  | 43592.1042 | 44 | 40
2019-05-07 03:00 | 41 | 34 |  |  | 43592.125 | 46 | 42
2019-05-07 03:30 | 44 | 36 |  |  | 43592.1458 | 49 | 44
2019-05-07 04:00 | 44 | 36 |  |  | 43592.1667 | 50 | 46
2019-05-07 04:30 | 47 | 40 |  |  | 43592.1875 | 52 | 48
2019-05-07 05:00 | 51 | 45 |  |  | 43592.2083 | 57 | 54
2019-05-07 05:30 | 55 | 50 |  |  | 43592.2292 | 62 | 59
2019-05-07 06:00 | 59 | 55 |  |  | 43592.25 | 67 | 65
2019-05-07 06:30 | 60 | 58 |  |  | 43592.2708 | 71 | 70
2019-05-07 07:00 | 59 | 56 |  |  | 43592.2917 | 74 | 71
2019-05-07 07:30 | 56 | 51 |  |  | 43592.3125 | 74 | 71
2019-05-07 08:00 | 54 | 49 |  |  | 43592.3333 | 73 | 70
2019-05-07 08:30 | 55 | 49 |  |  | 43592.3542 | 74 | 70
2019-05-07 09:00 | 54 | 49 |  |  | 43592.375 | 73 | 70
2019-05-07 09:30 | 51 | 46 |  |  | 43592.3958 | 70 | 67
2019-05-07 10:00 | 62 | 59 |  |  | 43592.4167 | 94 | 93
2019-05-07 10:30 | 62 | 59 |  |  | 43592.4375 | 95 | 94
2019-05-07 11:00 | 61 | 58 |  |  | 43592.4583 | 94 | 93
2019-05-07 11:30 | 59 | 56 |  |  | 43592.4792 | 91 | 90
2019-05-07 12:00 | 63 | 57 |  |  | 43592.5 | 97 | 92
2019-05-07 12:30 | 66 | 59 |  |  | 43592.5208 | 101 | 95
2019-05-07 13:00 | 69 | 62 |  |  | 43592.5417 | 104 | 97
2019-05-07 13:30 | 73 | 67 |  |  | 43592.5625 | 110 | 104
2019-05-07 14:00 | 74 | 68 |  |  | 43592.5833 | 111 | 105
2019-05-07 14:30 | 77 | 72 |  |  | 43592.6042 | 114 | 108
2019-05-07 15:00 | 76 | 70 |  |  | 43592.625 | 108 | 102
2019-05-07 15:30 | 64 | 60 |  |  | 43592.6458 | 83 | 78
2019-05-07 16:00 | 71 | 66 |  |  | 43592.6667 | 89 | 84
2019-05-07 16:30 | 74 | 69 |  |  | 43592.6875 | 90 | 85
2019-05-07 17:00 | 78 | 74 |  |  | 43592.7083 | 94 | 89
2019-05-07 17:30 | 78 | 74 |  |  | 43592.7292 | 92 | 86
2019-05-07 18:00 | 80 | 76 |  |  | 43592.75 | 94 | 89
2019-05-07 18:30 | 80 | 75 |  |  | 43592.7708 | 92 | 85
2019-05-07 19:00 | 81 | 76 |  |  | 43592.7917 | 93 | 85
2019-05-07 19:30 | 77 | 73 |  |  | 43592.8125 | 88 | 82
2019-05-07 20:00 | 75 | 71 |  |  | 43592.8333 | 86 | 80
2019-05-07 20:30 | 76 | 71 |  |  | 43592.8542 | 87 | 81
2019-05-07 21:00 | 74 | 70 |  |  | 43592.875 | 83 | 78
2019-05-07 21:30 | 69 | 66 |  |  | 43592.8958 | 78 | 74
2019-05-07 22:00 | 66 | 63 |  |  | 43592.9167 | 77 | 72
2019-05-07 22:30 | 63 | 59 |  |  | 43592.9375 | 74 | 69
2019-05-07 23:00 | 63 | 58 |  |  | 43592.9583 | 71 | 65
2019-05-07 23:30 | 64 | 59 |  |  | 43592.9792 | 73 | 68
2019-05-08 | 63 | 57 |  |  | 43593 | 71 | 66
2019-05-08 00:30 | 61 | 55 |  |  | 43593.0208 | 69 | 63
2019-05-08 01:00 | 60 | 53 |  |  | 43593.0417 | 66 | 58
2019-05-08 01:30 | 56 | 48 |  |  | 43593.0625 | 62 | 54
2019-05-08 02:00 | 54 | 46 |  |  | 43593.0833 | 60 | 52
2019-05-08 02:30 | 54 | 45 |  |  | 43593.1042 | 60 | 52
2019-05-08 03:00 | 55 | 46 |  |  | 43593.125 | 61 | 53
2019-05-08 03:30 | 56 | 47 |  |  | 43593.1458 | 61 | 53
2019-05-08 04:00 | 58 | 49 |  |  | 43593.1667 | 63 | 55
2019-05-08 04:30 | 59 | 51 |  |  | 43593.1875 | 64 | 56
2019-05-08 05:00 | 60 | 52 |  |  | 43593.2083 | 66 | 58
2019-05-08 05:30 | 65 | 59 |  |  | 43593.2292 | 71 | 64
2019-05-08 06:00 | 69 | 64 |  |  | 43593.25 | 76 | 71
2019-05-08 06:30 | 71 | 66 |  |  | 43593.2708 | 83 | 77
2019-05-08 07:00 | 71 | 65 |  |  | 43593.2917 | 85 | 79
2019-05-08 07:30 | 69 | 65 |  |  | 43593.3125 | 86 | 81
2019-05-08 08:00 | 72 | 67 |  |  | 43593.3333 | 89 | 85
2019-05-08 08:30 | 74 | 70 |  |  | 43593.3542 | 91 | 87
2019-05-08 09:00 | 76 | 71 |  |  | 43593.375 | 95 | 91
2019-05-08 09:30 | 85 | 80 |  |  | 43593.3958 | 111 | 108
2019-05-08 10:00 | 83 | 79 |  |  | 43593.4167 | 110 | 107
2019-05-08 10:30 | 79 | 76 |  |  | 43593.4375 | 106 | 104
2019-05-08 11:00 | 81 | 77 |  |  | 43593.4583 | 107 | 104
2019-05-08 11:30 | 79 | 75 |  |  | 43593.4792 | 105 | 101
2019-05-08 12:00 | 82 | 78 |  |  | 43593.5 | 107 | 104
2019-05-08 12:30 | 83 | 77 |  |  | 43593.5208 | 107 | 103
2019-05-08 13:00 | 82 | 77 |  |  | 43593.5417 | 106 | 102
2019-05-08 13:30 | 85 | 81 |  |  | 43593.5625 | 111 | 108
2019-05-08 14:00 | 88 | 86 |  |  | 43593.5833 | 113 | 111
2019-05-08 14:30 | 88 | 86 |  |  | 43593.6042 | 114 | 111
2019-05-08 15:00 | 91 | 89 |  |  | 43593.625 | 117 | 115
2019-05-08 15:30 | 95 | 93 |  |  | 43593.6458 | 122 | 119
2019-05-08 16:00 | 94 | 91 |  |  | 43593.6667 | 121 | 118
2019-05-08 16:30 | 87 | 84 |  |  | 43593.6875 | 113 | 110
2019-05-08 17:00 | 88 | 86 |  |  | 43593.7083 | 115 | 111
2019-05-08 17:30 | 92 | 90 |  |  | 43593.7292 | 118 | 113
2019-05-08 18:00 | 95 | 92 |  |  | 43593.75 | 120 | 115
2019-05-08 18:30 | 92 | 89 |  |  | 43593.7708 | 116 | 112
2019-05-08 19:00 | 96 | 93 |  |  | 43593.7917 | 119 | 114
2019-05-08 19:30 | 96 | 94 |  |  | 43593.8125 | 116 | 113
2019-05-08 20:00 | 96 | 95 |  |  | 43593.8333 | 114 | 114
2019-05-08 20:30 | 95 | 94 |  |  | 43593.8542 | 112 | 111
2019-05-08 21:00 | 91 | 90 |  |  | 43593.875 | 108 | 107
2019-05-08 21:30 | 88 | 86 |  |  | 43593.8958 | 103 | 101
2019-05-08 22:00 | 85 | 83 |  |  | 43593.9167 | 101 | 99
2019-05-08 22:30 | 80 | 77 |  |  | 43593.9375 | 97 | 95
2019-05-08 23:00 | 76 | 73 |  |  | 43593.9583 | 92 | 89
2019-05-08 23:30 | 73 | 70 |  |  | 43593.9792 | 89 | 85
2019-05-09 | 68 | 64 |  |  | 43594 | 84 | 80
2019-05-09 00:30 | 64 | 59 |  |  | 43594.0208 | 78 | 74
2019-05-09 01:00 | 63 | 58 |  |  | 43594.0417 | 76 | 71
2019-05-09 01:30 | 61 | 56 |  |  | 43594.0625 | 74 | 68
2019-05-09 02:00 | 61 | 56 |  |  | 43594.0833 | 73 | 67
2019-05-09 02:30 | 60 | 55 |  |  | 43594.1042 | 71 | 67
2019-05-09 03:00 | 59 | 54 |  |  | 43594.125 | 70 | 66
2019-05-09 03:30 | 58 | 53 |  |  | 43594.1458 | 70 | 66
2019-05-09 04:00 | 60 | 55 |  |  | 43594.1667 | 71 | 66
2019-05-09 04:30 | 61 | 56 |  |  | 43594.1875 | 72 | 68
2019-05-09 05:00 | 65 | 61 |  |  | 43594.2083 | 76 | 73
2019-05-09 05:30 | 70 | 67 |  |  | 43594.2292 | 82 | 79
2019-05-09 06:00 | 74 | 72 |  |  | 43594.25 | 88 | 86
2019-05-09 06:30 | 78 | 77 |  |  | 43594.2708 | 97 | 96
2019-05-09 07:00 | 83 | 82 |  |  | 43594.2917 | 106 | 105
2019-05-09 07:30 | 88 | 86 |  |  | 43594.3125 | 115 | 112
2019-05-09 08:00 | 88 | 84 |  |  | 43594.3333 | 116 | 111
2019-05-09 08:30 | 84 | 79 |  |  | 43594.3542 | 113 | 106
2019-05-09 09:00 | 83 | 78 |  |  | 43594.375 | 112 | 104
2019-05-09 09:30 | 80 | 77 |  |  | 43594.3958 | 106 | 103
2019-05-09 10:00 | 78 | 76 |  |  | 43594.4167 | 103 | 101
2019-05-09 10:30 | 76 | 74 |  |  | 43594.4375 | 101 | 99
2019-05-09 11:00 | 77 | 75 |  |  | 43594.4583 | 102 | 100
2019-05-09 11:30 | 76 | 74 |  |  | 43594.4792 | 102 | 100
2019-05-09 12:00 | 73 | 71 |  |  | 43594.5 | 100 | 98
2019-05-09 12:30 | 74 | 72 |  |  | 43594.5208 | 101 | 99
2019-05-09 13:00 | 77 | 75 |  |  | 43594.5417 | 103 | 101
2019-05-09 13:30 | 77 | 75 |  |  | 43594.5625 | 105 | 103
2019-05-09 14:00 | 81 | 79 |  |  | 43594.5833 | 107 | 106
2019-05-09 14:30 | 82 | 81 |  |  | 43594.6042 | 109 | 107
2019-05-09 15:00 | 87 | 85 |  |  | 43594.625 | 114 | 112
2019-05-09 15:30 | 89 | 87 |  |  | 43594.6458 | 116 | 114
2019-05-09 16:00 | 93 | 91 |  |  | 43594.6667 | 120 | 118
2019-05-09 16:30 | 96 | 94 |  |  | 43594.6875 | 124 | 120
2019-05-09 17:00 | 101 | 98 |  |  | 43594.7083 | 128 | 123
2019-05-09 17:30 | 103 | 100 |  |  | 43594.7292 | 130 | 125
2019-05-09 18:00 | 104 | 101 |  |  | 43594.75 | 131 | 125
2019-05-09 18:30 | 101 | 97 |  |  | 43594.7708 | 126 | 119
2019-05-09 19:00 | 101 | 98 |  |  | 43594.7917 | 126 | 120
2019-05-09 19:30 | 100 | 97 |  |  | 43594.8125 | 124 | 118
2019-05-09 20:00 | 99 | 96 |  |  | 43594.8333 | 122 | 116
2019-05-09 20:30 | 96 | 94 |  |  | 43594.8542 | 117 | 115
2019-05-09 21:00 | 89 | 88 |  |  | 43594.875 | 109 | 108
2019-05-09 21:30 | 85 | 83 |  |  | 43594.8958 | 104 | 101
2019-05-09 22:00 | 82 | 80 |  |  | 43594.9167 | 104 | 101
2019-05-09 22:30 | 79 | 77 |  |  | 43594.9375 | 101 | 99
2019-05-09 23:00 | 74 | 71 |  |  | 43594.9583 | 93 | 90
2019-05-09 23:30 | 71 | 68 |  |  | 43594.9792 | 90 | 85
2019-05-10 | 68 | 64 |  |  | 43595 | 87 | 82
2019-05-10 00:30 | 67 | 62 |  |  | 43595.0208 | 84 | 77
2019-05-10 01:00 | 67 | 61 |  |  | 43595.0417 | 82 | 75
2019-05-10 01:30 | 66 | 59 |  |  | 43595.0625 | 79 | 72
2019-05-10 02:00 | 65 | 58 |  |  | 43595.0833 | 77 | 71
2019-05-10 02:30 | 65 | 58 |  |  | 43595.1042 | 77 | 71
2019-05-10 03:00 | 63 | 57 |  |  | 43595.125 | 75 | 69
2019-05-10 03:30 | 63 | 56 |  |  | 43595.1458 | 75 | 69
2019-05-10 04:00 | 64 | 58 |  |  | 43595.1667 | 76 | 70
2019-05-10 04:30 | 64 | 58 |  |  | 43595.1875 | 77 | 71
2019-05-10 05:00 | 65 | 59 |  |  | 43595.2083 | 79 | 74
2019-05-10 05:30 | 70 | 66 |  |  | 43595.2292 | 85 | 80
2019-05-10 06:00 | 74 | 71 |  |  | 43595.25 | 90 | 87
2019-05-10 06:30 | 77 | 75 |  |  | 43595.2708 | 98 | 96
2019-05-10 07:00 | 81 | 78 |  |  | 43595.2917 | 107 | 103
2019-05-10 07:30 | 87 | 83 |  |  | 43595.3125 | 115 | 112
2019-05-10 08:00 | 84 | 81 |  |  | 43595.3333 | 116 | 114
2019-05-10 08:30 | 85 | 82 |  |  | 43595.3542 | 115 | 112
2019-05-10 09:00 | 76 | 73 |  |  | 43595.375 | 107 | 104
2019-05-10 09:30 | 72 | 70 |  |  | 43595.3958 | 101 | 99
2019-05-10 10:00 | 74 | 71 |  |  | 43595.4167 | 104 | 102
2019-05-10 10:30 | 76 | 74 |  |  | 43595.4375 | 109 | 107
2019-05-10 11:00 | 73 | 72 |  |  | 43595.4583 | 103 | 102
2019-05-10 11:30 | 74 | 72 |  |  | 43595.4792 | 104 | 104
2019-05-10 12:00 | 68 | 67 |  |  | 43595.5 | 99 | 99
2019-05-10 12:30 | 67 | 66 |  |  | 43595.5208 | 98 | 98
2019-05-10 13:00 | 71 | 70 |  |  | 43595.5417 | 101 | 100
2019-05-10 13:30 | 76 | 75 |  |  | 43595.5625 | 105 | 105
2019-05-10 14:00 | 76 | 75 |  |  | 43595.5833 | 107 | 106
2019-05-10 14:30 | 79 | 77 |  |  | 43595.6042 | 108 | 106
2019-05-10 15:00 | 83 | 81 |  |  | 43595.625 | 114 | 113
2019-05-10 15:30 | 92 | 89 |  |  | 43595.6458 | 120 | 118
2019-05-10 16:00 | 92 | 90 |  |  | 43595.6667 | 122 | 120
2019-05-10 16:30 | 93 | 91 |  |  | 43595.6875 | 121 | 119
2019-05-10 17:00 | 96 | 94 |  |  | 43595.7083 | 124 | 121
2019-05-10 17:30 | 98 | 96 |  |  | 43595.7292 | 125 | 122
2019-05-10 18:00 | 98 | 95 |  |  | 43595.75 | 123 | 121
2019-05-10 18:30 | 96 | 93 |  |  | 43595.7708 | 120 | 116
2019-05-10 19:00 | 95 | 92 |  |  | 43595.7917 | 119 | 115
2019-05-10 19:30 | 94 | 90 |  |  | 43595.8125 | 116 | 112
2019-05-10 20:00 | 91 | 88 |  |  | 43595.8333 | 113 | 108
2019-05-10 20:30 | 89 | 85 |  |  | 43595.8542 | 110 | 105
2019-05-10 21:00 | 85 | 81 |  |  | 43595.875 | 105 | 101
2019-05-10 21:30 | 82 | 78 |  |  | 43595.8958 | 102 | 97
2019-05-10 22:00 | 77 | 75 |  |  | 43595.9167 | 96 | 94
2019-05-10 22:30 | 74 | 71 |  |  | 43595.9375 | 94 | 92
2019-05-10 23:00 | 68 | 65 |  |  | 43595.9583 | 87 | 84
2019-05-10 23:30 | 63 | 60 |  |  | 43595.9792 | 82 | 79
2019-05-11 | 61 | 57 |  |  | 43596 | 80 | 76
2019-05-11 00:30 | 60 | 56 |  |  | 43596.0208 | 76 | 72
2019-05-11 01:00 | 58 | 54 |  |  | 43596.0417 | 73 | 69
2019-05-11 01:30 | 58 | 55 |  |  | 43596.0625 | 71 | 69
2019-05-11 02:00 | 58 | 54 |  |  | 43596.0833 | 69 | 67
2019-05-11 02:30 | 56 | 53 |  |  | 43596.1042 | 68 | 65
2019-05-11 03:00 | 55 | 51 |  |  | 43596.125 | 67 | 65
2019-05-11 03:30 | 55 | 51 |  |  | 43596.1458 | 71 | 63
2019-05-11 04:00 | 54 | 49 |  |  | 43596.1667 | 71 | 62
2019-05-11 04:30 | 56 | 51 |  |  | 43596.1875 | 72 | 63
2019-05-11 05:00 | 56 | 51 |  |  | 43596.2083 | 73 | 64
2019-05-11 05:30 | 56 | 51 |  |  | 43596.2292 | 74 | 65
2019-05-11 06:00 | 57 | 53 |  |  | 43596.25 | 77 | 68
2019-05-11 06:30 | 60 | 55 |  |  | 43596.2708 | 80 | 71
2019-05-11 07:00 | 60 | 55 |  |  | 43596.2917 | 81 | 72
2019-05-11 07:30 | 55 | 51 |  |  | 43596.3125 | 78 | 71
2019-05-11 08:00 | 51 | 47 |  |  | 43596.3333 | 75 | 69
2019-05-11 08:30 | 49 | 46 |  |  | 43596.3542 | 74 | 69
2019-05-11 09:00 | 49 | 47 |  |  | 43596.375 | 73 | 68
2019-05-11 09:30 | 49 | 47 |  |  | 43596.3958 | 73 | 68
2019-05-11 10:00 | 47 | 45 |  |  | 43596.4167 | 70 | 64
2019-05-11 10:30 | 45 | 42 |  |  | 43596.4375 | 67 | 61
2019-05-11 11:00 | 44 | 41 |  |  | 43596.4583 | 65 | 59
2019-05-11 11:30 | 44 | 40 |  |  | 43596.4792 | 64 | 57
2019-05-11 12:00 | 42 | 38 |  |  | 43596.5 | 63 | 56
2019-05-11 12:30 | 42 | 38 |  |  | 43596.5208 | 63 | 56
2019-05-11 13:00 | 43 | 39 |  |  | 43596.5417 | 63 | 56
2019-05-11 13:30 | 45 | 40 |  |  | 43596.5625 | 66 | 58
2019-05-11 14:00 | 47 | 42 |  |  | 43596.5833 | 68 | 59
2019-05-11 14:30 | 49 | 44 |  |  | 43596.6042 | 70 | 62
2019-05-11 15:00 | 51 | 46 |  |  | 43596.625 | 73 | 66
2019-05-11 15:30 | 54 | 49 |  |  | 43596.6458 | 77 | 69
2019-05-11 16:00 | 58 | 54 |  |  | 43596.6667 | 81 | 74
2019-05-11 16:30 | 61 | 57 |  |  | 43596.6875 | 87 | 79
2019-05-11 17:00 | 65 | 61 |  |  | 43596.7083 | 91 | 83
2019-05-11 17:30 | 68 | 65 |  |  | 43596.7292 | 95 | 87
2019-05-11 18:00 | 72 | 68 |  |  | 43596.75 | 98 | 91
2019-05-11 18:30 | 71 | 67 |  |  | 43596.7708 | 98 | 90
2019-05-11 19:00 | 72 | 68 |  |  | 43596.7917 | 98 | 90
2019-05-11 19:30 | 71 | 67 |  |  | 43596.8125 | 97 | 89
2019-05-11 20:00 | 70 | 66 |  |  | 43596.8333 | 95 | 88
2019-05-11 20:30 | 68 | 65 |  |  | 43596.8542 | 94 | 87
2019-05-11 21:00 | 66 | 62 |  |  | 43596.875 | 90 | 82
2019-05-11 21:30 | 65 | 61 |  |  | 43596.8958 | 89 | 80
2019-05-11 22:00 | 64 | 60 |  |  | 43596.9167 | 90 | 81
2019-05-11 22:30 | 64 | 59 |  |  | 43596.9375 | 90 | 81
2019-05-11 23:00 | 62 | 58 |  |  | 43596.9583 | 86 | 77
2019-05-11 23:30 | 61 | 55 |  |  | 43596.9792 | 85 | 74
2019-05-12 | 58 | 52 |  |  | 43597 | 82 | 70
2019-05-12 00:30 | 57 | 50 |  |  | 43597.0208 | 79 | 66
2019-05-12 01:00 | 54 | 49 |  |  | 43597.0417 | 74 | 63
2019-05-12 01:30 | 53 | 47 |  |  | 43597.0625 | 71 | 61
2019-05-12 02:00 | 52 | 46 |  |  | 43597.0833 | 69 | 59
2019-05-12 02:30 | 52 | 46 |  |  | 43597.1042 | 69 | 59
2019-05-12 03:00 | 50 | 44 |  |  | 43597.125 | 67 | 57
2019-05-12 03:30 | 50 | 44 |  |  | 43597.1458 | 66 | 56
2019-05-12 04:00 | 50 | 43 |  |  | 43597.1667 | 66 | 56
2019-05-12 04:30 | 50 | 44 |  |  | 43597.1875 | 66 | 57
2019-05-12 05:00 | 51 | 45 |  |  | 43597.2083 | 67 | 58
2019-05-12 05:30 | 51 | 45 |  |  | 43597.2292 | 69 | 59
2019-05-12 06:00 | 52 | 46 |  |  | 43597.25 | 71 | 62
2019-05-12 06:30 | 54 | 48 |  |  | 43597.2708 | 72 | 63
2019-05-12 07:00 | 53 | 47 |  |  | 43597.2917 | 74 | 65
2019-05-12 07:30 | 50 | 45 |  |  | 43597.3125 | 72 | 64
2019-05-12 08:00 | 49 | 45 |  |  | 43597.3333 | 70 | 63
2019-05-12 08:30 | 50 | 47 |  |  | 43597.3542 | 73 | 67
2019-05-12 09:00 | 53 | 50 |  |  | 43597.375 | 76 | 71
2019-05-12 09:30 | 50 | 46 |  |  | 43597.3958 | 74 | 68
2019-05-12 10:00 | 48 | 45 |  |  | 43597.4167 | 71 | 65
2019-05-12 10:30 | 51 | 47 |  |  | 43597.4375 | 72 | 67
2019-05-12 11:00 | 49 | 46 |  |  | 43597.4583 | 73 | 67
2019-05-12 11:30 | 45 | 41 |  |  | 43597.4792 | 68 | 61
2019-05-12 12:00 | 43 | 39 |  |  | 43597.5 | 64 | 58
2019-05-12 12:30 | 44 | 40 |  |  | 43597.5208 | 64 | 58
2019-05-12 13:00 | 47 | 43 |  |  | 43597.5417 | 66 | 59
2019-05-12 13:30 | 48 | 45 |  |  | 43597.5625 | 70 | 65
2019-05-12 14:00 | 51 | 48 |  |  | 43597.5833 | 70 | 65
2019-05-12 14:30 | 52 | 49 |  |  | 43597.6042 | 72 | 68
2019-05-12 15:00 | 53 | 50 |  |  | 43597.625 | 75 | 70
2019-05-12 15:30 | 56 | 53 |  |  | 43597.6458 | 78 | 74
2019-05-12 16:00 | 60 | 57 |  |  | 43597.6667 | 81 | 77
2019-05-12 16:30 | 60 | 58 |  |  | 43597.6875 | 83 | 79
2019-05-12 17:00 | 62 | 60 |  |  | 43597.7083 | 87 | 82
2019-05-12 17:30 | 66 | 64 |  |  | 43597.7292 | 91 | 87
2019-05-12 18:00 | 70 | 67 |  |  | 43597.75 | 95 | 90
2019-05-12 18:30 | 70 | 67 |  |  | 43597.7708 | 95 | 89
2019-05-12 19:00 | 70 | 68 |  |  | 43597.7917 | 96 | 90
2019-05-12 19:30 | 69 | 66 |  |  | 43597.8125 | 94 | 88
2019-05-12 20:00 | 68 | 65 |  |  | 43597.8333 | 92 | 86
2019-05-12 20:30 | 67 | 64 |  |  | 43597.8542 | 92 | 86
2019-05-12 21:00 | 64 | 61 |  |  | 43597.875 | 88 | 82
2019-05-12 21:30 | 62 | 58 |  |  | 43597.8958 | 85 | 78
2019-05-12 22:00 | 61 | 57 |  |  | 43597.9167 | 85 | 78
2019-05-12 22:30 | 63 | 60 |  |  | 43597.9375 | 87 | 81
2019-05-12 23:00 | 63 | 60 |  |  | 43597.9583 | 86 | 79
2019-05-12 23:30 | 61 | 57 |  |  | 43597.9792 | 83 | 76
2019-05-13 | 56 | 52 |  |  | 43598 | 78 | 70
2019-05-13 00:30 | 55 | 50 |  |  | 43598.0208 | 77 | 67
2019-05-13 01:00 | 55 | 49 |  |  | 43598.0417 | 75 | 65
2019-05-13 01:30 | 55 | 48 |  |  | 43598.0625 | 74 | 63
2019-05-13 02:00 | 54 | 47 |  |  | 43598.0833 | 73 | 62
2019-05-13 02:30 | 53 | 47 |  |  | 43598.1042 | 71 | 60
2019-05-13 03:00 | 54 | 47 |  |  | 43598.125 | 72 | 60
2019-05-13 03:30 | 54 | 47 |  |  | 43598.1458 | 72 | 60
2019-05-13 04:00 | 55 | 49 |  |  | 43598.1667 | 73 | 61
2019-05-13 04:30 | 55 | 49 |  |  | 43598.1875 | 74 | 62
2019-05-13 05:00 | 56 | 51 |  |  | 43598.2083 | 76 | 65
2019-05-13 05:30 | 62 | 59 |  |  | 43598.2292 | 81 | 72
2019-05-13 06:00 | 68 | 66 |  |  | 43598.25 | 86 | 80
2019-05-13 06:30 | 73 | 71 |  |  | 43598.2708 | 95 | 91
2019-05-13 07:00 | 73 | 73 |  |  | 43598.2917 | 99 | 97
2019-05-13 07:30 | 78 | 78 |  |  | 43598.3125 | 108 | 107
2019-05-13 08:00 | 77 | 77 |  |  | 43598.3333 | 109 | 109
2019-05-13 08:30 | 77 | 77 |  |  | 43598.3542 | 110 | 108
2019-05-13 09:00 | 74 | 74 |  |  | 43598.375 | 106 | 103
2019-05-13 09:30 | 74 | 74 |  |  | 43598.3958 | 103 | 101
2019-05-13 10:00 | 77 | 77 |  |  | 43598.4167 | 108 | 107
2019-05-13 10:30 | 74 | 74 |  |  | 43598.4375 | 103 | 102
2019-05-13 11:00 | 77 | 77 |  |  | 43598.4583 | 108 | 107
2019-05-13 11:30 | 76 | 76 |  |  | 43598.4792 | 105 | 104
2019-05-13 12:00 | 78 | 78 |  |  | 43598.5 | 107 | 106
2019-05-13 12:30 | 79 | 79 |  |  | 43598.5208 | 112 | 111
2019-05-13 13:00 | 84 | 84 |  |  | 43598.5417 | 114 | 112
2019-05-13 13:30 | 83 | 83 |  |  | 43598.5625 | 112 | 110
2019-05-13 14:00 | 85 | 85 |  |  | 43598.5833 | 114 | 112
2019-05-13 14:30 | 83 | 83 |  |  | 43598.6042 | 113 | 111
2019-05-13 15:00 | 82 | 82 |  |  | 43598.625 | 111 | 109
2019-05-13 15:30 | 79 | 79 |  |  | 43598.6458 | 109 | 106
2019-05-13 16:00 | 79 | 78 |  |  | 43598.6667 | 109 | 105
2019-05-13 16:30 | 80 | 79 |  |  | 43598.6875 | 113 | 106
2019-05-13 17:00 | 82 | 82 |  |  | 43598.7083 | 115 | 109
2019-05-13 17:30 | 85 | 84 |  |  | 43598.7292 | 117 | 110
2019-05-13 18:00 | 86 | 85 |  |  | 43598.75 | 118 | 110
2019-05-13 18:30 | 83 | 82 |  |  | 43598.7708 | 115 | 105
2019-05-13 19:00 | 83 | 82 |  |  | 43598.7917 | 115 | 105
2019-05-13 19:30 | 80 | 79 |  |  | 43598.8125 | 111 | 102
2019-05-13 20:00 | 79 | 77 |  |  | 43598.8333 | 108 | 99
2019-05-13 20:30 | 77 | 75 |  |  | 43598.8542 | 107 | 98
2019-05-13 21:00 | 74 | 69 |  |  | 43598.875 | 103 | 91
2019-05-13 21:30 | 71 | 65 |  |  | 43598.8958 | 97 | 87
2019-05-13 22:00 | 67 | 63 |  |  | 43598.9167 | 93 | 86
2019-05-13 22:30 | 67 | 63 |  |  | 43598.9375 | 93 | 86
2019-05-13 23:00 | 66 | 62 |  |  | 43598.9583 | 90 | 82
2019-05-13 23:30 | 64 | 59 |  |  | 43598.9792 | 86 | 78
2019-05-14 | 60 | 54 |  |  | 43599 | 82 | 72
2019-05-14 00:30 | 61 | 54 |  |  | 43599.0208 | 80 | 69
2019-05-14 01:00 | 59 | 52 |  |  | 43599.0417 | 78 | 66
2019-05-14 01:30 | 57 | 50 |  |  | 43599.0625 | 76 | 64
2019-05-14 02:00 | 57 | 49 |  |  | 43599.0833 | 75 | 61
2019-05-14 02:30 | 57 | 49 |  |  | 43599.1042 | 76 | 62
2019-05-14 03:00 | 56 | 49 |  |  | 43599.125 | 76 | 62
2019-05-14 03:30 | 56 | 48 |  |  | 43599.1458 | 74 | 60
2019-05-14 04:00 | 56 | 48 |  |  | 43599.1667 | 74 | 60
2019-05-14 04:30 | 57 | 50 |  |  | 43599.1875 | 76 | 63
2019-05-14 05:00 | 61 | 54 |  |  | 43599.2083 | 80 | 67
2019-05-14 05:30 | 64 | 58 |  |  | 43599.2292 | 83 | 72
2019-05-14 06:00 | 67 | 62 |  |  | 43599.25 | 87 | 78
2019-05-14 06:30 | 70 | 66 |  |  | 43599.2708 | 94 | 88
2019-05-14 07:00 | 74 | 70 |  |  | 43599.2917 | 103 | 95
2019-05-14 07:30 | 78 | 73 |  |  | 43599.3125 | 111 | 101
2019-05-14 08:00 | 77 | 74 |  |  | 43599.3333 | 112 | 104
2019-05-14 08:30 | 76 | 73 |  |  | 43599.3542 | 111 | 104
2019-05-14 09:00 | 75 | 72 |  |  | 43599.375 | 110 | 103
2019-05-14 09:30 | 72 | 68 |  |  | 43599.3958 | 107 | 99
2019-05-14 10:00 | 70 | 67 |  |  | 43599.4167 | 106 | 99
2019-05-14 10:30 | 71 | 68 |  |  | 43599.4375 | 105 | 97
2019-05-14 11:00 | 72 | 68 |  |  | 43599.4583 | 106 | 99
2019-05-14 11:30 | 73 | 69 |  |  | 43599.4792 | 108 | 101
2019-05-14 12:00 | 72 | 68 |  |  | 43599.5 | 105 | 98
2019-05-14 12:30 | 72 | 69 |  |  | 43599.5208 | 105 | 97
2019-05-14 13:00 | 75 | 71 |  |  | 43599.5417 | 110 | 103
2019-05-14 13:30 | 77 | 74 |  |  | 43599.5625 | 112 | 105
2019-05-14 14:00 | 83 | 80 |  |  | 43599.5833 | 117 | 110
2019-05-14 14:30 | 85 | 83 |  |  | 43599.6042 | 119 | 112
2019-05-14 15:00 | 83 | 82 |  |  | 43599.625 | 116 | 111
2019-05-14 15:30 | 83 | 82 |  |  | 43599.6458 | 117 | 111
2019-05-14 16:00 | 83 | 82 |  |  | 43599.6667 | 117 | 111
2019-05-14 16:30 | 81 | 79 |  |  | 43599.6875 | 115 | 109
2019-05-14 17:00 | 81 | 80 |  |  | 43599.7083 | 115 | 109
2019-05-14 17:30 | 81 | 80 |  |  | 43599.7292 | 116 | 109
2019-05-14 18:00 | 81 | 80 |  |  | 43599.75 | 116 | 110
2019-05-14 18:30 | 79 | 78 |  |  | 43599.7708 | 114 | 106
2019-05-14 19:00 | 80 | 79 |  |  | 43599.7917 | 114 | 106
2019-05-14 19:30 | 78 | 77 |  |  | 43599.8125 | 113 | 103
2019-05-14 20:00 | 78 | 75 |  |  | 43599.8333 | 111 | 101
2019-05-14 20:30 | 77 | 74 |  |  | 43599.8542 | 110 | 100
2019-05-14 21:00 | 74 | 70 |  |  | 43599.875 | 104 | 94
2019-05-14 21:30 | 71 | 67 |  |  | 43599.8958 | 98 | 88
2019-05-14 22:00 | 68 | 65 |  |  | 43599.9167 | 93 | 87
2019-05-14 22:30 | 66 | 63 |  |  | 43599.9375 | 92 | 85
2019-05-14 23:00 | 64 | 61 |  |  | 43599.9583 | 88 | 81
2019-05-14 23:30 | 62 | 58 |  |  | 43599.9792 | 85 | 77
2019-05-15 | 59 | 55 |  |  | 43600 | 82 | 72
2019-05-15 00:30 | 56 | 53 |  |  | 43600.0208 | 75 | 68
2019-05-15 01:00 | 53 | 49 |  |  | 43600.0417 | 70 | 63
2019-05-15 01:30 | 51 | 48 |  |  | 43600.0625 | 69 | 61
2019-05-15 02:00 | 52 | 48 |  |  | 43600.0833 | 68 | 60
2019-05-15 02:30 | 52 | 48 |  |  | 43600.1042 | 68 | 61
2019-05-15 03:00 | 52 | 48 |  |  | 43600.125 | 67 | 60
2019-05-15 03:30 | 51 | 47 |  |  | 43600.1458 | 67 | 59
2019-05-15 04:00 | 52 | 48 |  |  | 43600.1667 | 68 | 60
2019-05-15 04:30 | 55 | 51 |  |  | 43600.1875 | 71 | 64
2019-05-15 05:00 | 57 | 54 |  |  | 43600.2083 | 74 | 67
2019-05-15 05:30 | 62 | 60 |  |  | 43600.2292 | 79 | 74
2019-05-15 06:00 | 66 | 65 |  |  | 43600.25 | 85 | 80
2019-05-15 06:30 | 72 | 67 |  |  | 43600.2708 | 100 | 89
2019-05-15 07:00 | 76 | 71 |  |  | 43600.2917 | 108 | 97
2019-05-15 07:30 | 78 | 74 |  |  | 43600.3125 | 114 | 103
2019-05-15 08:00 | 79 | 75 |  |  | 43600.3333 | 115 | 105
2019-05-15 08:30 | 75 | 71 |  |  | 43600.3542 | 113 | 103
2019-05-15 09:00 | 73 | 68 |  |  | 43600.375 | 111 | 100
2019-05-15 09:30 | 70 | 66 |  |  | 43600.3958 | 105 | 93
2019-05-15 10:00 | 67 | 63 |  |  | 43600.4167 | 104 | 94
2019-05-15 10:30 | 69 | 66 |  |  | 43600.4375 | 103 | 93
2019-05-15 11:00 | 70 | 67 |  |  | 43600.4583 | 106 | 97
2019-05-15 11:30 | 70 | 67 |  |  | 43600.4792 | 107 | 98
2019-05-15 12:00 | 73 | 70 |  |  | 43600.5 | 107 | 99
2019-05-15 12:30 | 76 | 74 |  |  | 43600.5208 | 113 | 105
2019-05-15 13:00 | 80 | 78 |  |  | 43600.5417 | 112 | 104
2019-05-15 13:30 | 78 | 76 |  |  | 43600.5625 | 110 | 101
2019-05-15 14:00 | 77 | 74 |  |  | 43600.5833 | 109 | 100
2019-05-15 14:30 | 78 | 76 |  |  | 43600.6042 | 111 | 103
2019-05-15 15:00 | 80 | 77 |  |  | 43600.625 | 113 | 104
2019-05-15 15:30 | 79 | 75 |  |  | 43600.6458 | 111 | 102
2019-05-15 16:00 | 81 | 76 |  |  | 43600.6667 | 116 | 105
2019-05-15 16:30 | 81 | 75 |  |  | 43600.6875 | 118 | 104
2019-05-15 17:00 | 83 | 77 |  |  | 43600.7083 | 120 | 106
2019-05-15 17:30 | 84 | 80 |  |  | 43600.7292 | 122 | 108
2019-05-15 18:00 | 82 | 80 |  |  | 43600.75 | 120 | 108
2019-05-15 18:30 | 79 | 77 |  |  | 43600.7708 | 117 | 103
2019-05-15 19:00 | 81 | 78 |  |  | 43600.7917 | 119 | 104
2019-05-15 19:30 | 78 | 76 |  |  | 43600.8125 | 112 | 101
2019-05-15 20:00 | 75 | 75 |  |  | 43600.8333 | 102 | 98
2019-05-15 20:30 | 75 | 74 |  |  | 43600.8542 | 101 | 96
2019-05-15 21:00 | 71 | 71 |  |  | 43600.875 | 96 | 91
2019-05-15 21:30 | 67 | 67 |  |  | 43600.8958 | 92 | 87
2019-05-15 22:00 | 65 | 64 |  |  | 43600.9167 | 91 | 86
2019-05-15 22:30 | 65 | 64 |  |  | 43600.9375 | 90 | 85
2019-05-15 23:00 | 62 | 59 |  |  | 43600.9583 | 86 | 78
2019-05-15 23:30 | 59 | 55 |  |  | 43600.9792 | 82 | 74
2019-05-16 | 55 | 51 |  |  | 43601 | 80 | 70
2019-05-16 00:30 | 54 | 49 |  |  | 43601.0208 | 76 | 65
2019-05-16 01:00 | 52 | 46 |  |  | 43601.0417 | 73 | 61
2019-05-16 01:30 | 51 | 44 |  |  | 43601.0625 | 71 | 57
2019-05-16 02:00 | 48 | 42 |  |  | 43601.0833 | 68 | 55
2019-05-16 02:30 | 47 | 42 |  |  | 43601.1042 | 66 | 55
2019-05-16 03:00 | 48 | 43 |  |  | 43601.125 | 67 | 56
2019-05-16 03:30 | 48 | 43 |  |  | 43601.1458 | 67 | 56
2019-05-16 04:00 | 48 | 43 |  |  | 43601.1667 | 67 | 57
2019-05-16 04:30 | 48 | 44 |  |  | 43601.1875 | 69 | 58
2019-05-16 05:00 | 50 | 45 |  |  | 43601.2083 | 70 | 61
2019-05-16 05:30 | 55 | 52 |  |  | 43601.2292 | 75 | 67
2019-05-16 06:00 | 61 | 58 |  |  | 43601.25 | 82 | 75
2019-05-16 06:30 | 65 | 63 |  |  | 43601.2708 | 89 | 84
2019-05-16 07:00 | 67 | 66 |  |  | 43601.2917 | 94 | 91
2019-05-16 07:30 | 73 | 70 |  |  | 43601.3125 | 99 | 98
2019-05-16 08:00 | 75 | 70 |  |  | 43601.3333 | 102 | 99
2019-05-16 08:30 | 75 | 67 |  |  | 43601.3542 | 103 | 98
2019-05-16 09:00 | 72 | 64 |  |  | 43601.375 | 101 | 96
2019-05-16 09:30 | 72 | 65 |  |  | 43601.3958 | 102 | 98
2019-05-16 10:00 | 72 | 67 |  |  | 43601.4167 | 104 | 101
2019-05-16 10:30 | 74 | 67 |  |  | 43601.4375 | 102 | 98
2019-05-16 11:00 | 77 | 71 |  |  | 43601.4583 | 105 | 102
2019-05-16 11:30 | 73 | 67 |  |  | 43601.4792 | 100 | 96
2019-05-16 12:00 | 72 | 66 |  |  | 43601.5 | 98 | 95
2019-05-16 12:30 | 70 | 63 |  |  | 43601.5208 | 99 | 96
2019-05-16 13:00 | 74 | 68 |  |  | 43601.5417 | 105 | 102
2019-05-16 13:30 | 74 | 69 |  |  | 43601.5625 | 106 | 103
2019-05-16 14:00 | 76 | 70 |  |  | 43601.5833 | 105 | 102
2019-05-16 14:30 | 76 | 70 |  |  | 43601.6042 | 105 | 102
2019-05-16 15:00 | 77 | 71 |  |  | 43601.625 | 107 | 103
2019-05-16 15:30 | 78 | 72 |  |  | 43601.6458 | 107 | 103
2019-05-16 16:00 | 80 | 74 |  |  | 43601.6667 | 108 | 105
2019-05-16 16:30 | 81 | 74 |  |  | 43601.6875 | 108 | 103
2019-05-16 17:00 | 82 | 76 |  |  | 43601.7083 | 111 | 106
2019-05-16 17:30 | 83 | 77 |  |  | 43601.7292 | 112 | 107
2019-05-16 18:00 | 88 | 80 |  |  | 43601.75 | 115 | 109
2019-05-16 18:30 | 87 | 78 |  |  | 43601.7708 | 113 | 106
2019-05-16 19:00 | 87 | 78 |  |  | 43601.7917 | 112 | 105
2019-05-16 19:30 | 83 | 77 |  |  | 43601.8125 | 108 | 103
2019-05-16 20:00 | 82 | 75 |  |  | 43601.8333 | 104 | 100
2019-05-16 20:30 | 80 | 73 |  |  | 43601.8542 | 102 | 97
2019-05-16 21:00 | 77 | 69 |  |  | 43601.875 | 98 | 92
2019-05-16 21:30 | 75 | 66 |  |  | 43601.8958 | 95 | 89
2019-05-16 22:00 | 74 | 65 |  |  | 43601.9167 | 94 | 87
2019-05-16 22:30 | 73 | 64 |  |  | 43601.9375 | 92 | 86
2019-05-16 23:00 | 69 | 62 |  |  | 43601.9583 | 84 | 81
2019-05-16 23:30 | 65 | 58 |  |  | 43601.9792 | 81 | 78
2019-05-17 | 62 | 54 |  |  | 43602 | 77 | 73
2019-05-17 00:30 | 62 | 52 |  |  | 43602.0208 | 74 | 69
2019-05-17 01:00 | 59 | 48 |  |  | 43602.0417 | 69 | 64
2019-05-17 01:30 | 57 | 46 |  |  | 43602.0625 | 68 | 62
2019-05-17 02:00 | 58 | 46 |  |  | 43602.0833 | 67 | 61
2019-05-17 02:30 | 58 | 46 |  |  | 43602.1042 | 67 | 60
2019-05-17 03:00 | 57 | 45 |  |  | 43602.125 | 66 | 59
2019-05-17 03:30 | 58 | 46 |  |  | 43602.1458 | 66 | 60
2019-05-17 04:00 | 59 | 46 |  |  | 43602.1667 | 67 | 61
2019-05-17 04:30 | 60 | 47 |  |  | 43602.1875 | 68 | 62
2019-05-17 05:00 | 61 | 50 |  |  | 43602.2083 | 71 | 65
2019-05-17 05:30 | 64 | 55 |  |  | 43602.2292 | 76 | 71
2019-05-17 06:00 | 68 | 61 |  |  | 43602.25 | 82 | 79
2019-05-17 06:30 | 74 | 69 |  |  | 43602.2708 | 94 | 92
2019-05-17 07:00 | 78 | 73 |  |  | 43602.2917 | 102 | 100
2019-05-17 07:30 | 82 | 76 |  |  | 43602.3125 | 110 | 107
2019-05-17 08:00 | 84 | 77 |  |  | 43602.3333 | 115 | 111
2019-05-17 08:30 | 89 | 82 |  |  | 43602.3542 | 118 | 114
2019-05-17 09:00 | 87 | 80 |  |  | 43602.375 | 116 | 112
2019-05-17 09:30 | 82 | 74 |  |  | 43602.3958 | 111 | 107
2019-05-17 10:00 | 76 | 68 |  |  | 43602.4167 | 103 | 99
2019-05-17 10:30 | 76 | 67 |  |  | 43602.4375 | 101 | 97
2019-05-17 11:00 | 73 | 66 |  |  | 43602.4583 | 97 | 93
2019-05-17 11:30 | 77 | 71 |  |  | 43602.4792 | 102 | 98
2019-05-17 12:00 | 80 | 73 |  |  | 43602.5 | 104 | 101
2019-05-17 12:30 | 79 | 72 |  |  | 43602.5208 | 106 | 103
2019-05-17 13:00 | 79 | 71 |  |  | 43602.5417 | 107 | 103
2019-05-17 13:30 | 80 | 72 |  |  | 43602.5625 | 105 | 102
2019-05-17 14:00 | 78 | 71 |  |  | 43602.5833 | 98 | 94
2019-05-17 14:30 | 74 | 66 |  |  | 43602.6042 | 94 | 90
2019-05-17 15:00 | 74 | 65 |  |  | 43602.625 | 97 | 93
2019-05-17 15:30 | 73 | 64 |  |  | 43602.6458 | 99 | 95
2019-05-17 16:00 | 77 | 69 |  |  | 43602.6667 | 101 | 97
2019-05-17 16:30 | 77 | 67 |  |  | 43602.6875 | 103 | 97
2019-05-17 17:00 | 80 | 70 |  |  | 43602.7083 | 106 | 100
2019-05-17 17:30 | 80 | 70 |  |  | 43602.7292 | 105 | 99
2019-05-17 18:00 | 80 | 69 |  |  | 43602.75 | 103 | 96
2019-05-17 18:30 | 79 | 66 |  |  | 43602.7708 | 100 | 92
2019-05-17 19:00 | 79 | 66 |  |  | 43602.7917 | 100 | 91
2019-05-17 19:30 | 77 | 64 |  |  | 43602.8125 | 97 | 89
2019-05-17 20:00 | 76 | 63 |  |  | 43602.8333 | 96 | 87
2019-05-17 20:30 | 75 | 62 |  |  | 43602.8542 | 95 | 87
2019-05-17 21:00 | 69 | 58 |  |  | 43602.875 | 86 | 81
2019-05-17 21:30 | 63 | 55 |  |  | 43602.8958 | 81 | 78
2019-05-17 22:00 | 64 | 55 |  |  | 43602.9167 | 81 | 78
2019-05-17 22:30 | 64 | 55 |  |  | 43602.9375 | 81 | 78
2019-05-17 23:00 | 64 | 54 |  |  | 43602.9583 | 78 | 75
2019-05-17 23:30 | 60 | 50 |  |  | 43602.9792 | 74 | 70
2019-05-18 | 57 | 46 |  |  | 43603 | 70 | 67
2019-05-18 00:30 | 57 | 46 |  |  | 43603.0208 | 69 | 64
2019-05-18 01:00 | 56 | 45 |  |  | 43603.0417 | 66 | 61
2019-05-18 01:30 | 55 | 42 |  |  | 43603.0625 | 64 | 58
2019-05-18 02:00 | 55 | 42 |  |  | 43603.0833 | 63 | 57
2019-05-18 02:30 | 54 | 40 |  |  | 43603.1042 | 62 | 55
2019-05-18 03:00 | 54 | 41 |  |  | 43603.125 | 61 | 55
2019-05-18 03:30 | 55 | 41 |  |  | 43603.1458 | 62 | 55
2019-05-18 04:00 | 55 | 42 |  |  | 43603.1667 | 62 | 55
2019-05-18 04:30 | 56 | 43 |  |  | 43603.1875 | 63 | 57
2019-05-18 05:00 | 56 | 43 |  |  | 43603.2083 | 64 | 57
2019-05-18 05:30 | 57 | 44 |  |  | 43603.2292 | 65 | 59
2019-05-18 06:00 | 57 | 46 |  |  | 43603.25 | 66 | 60
2019-05-18 06:30 | 58 | 47 |  |  | 43603.2708 | 68 | 63
2019-05-18 07:00 | 57 | 46 |  |  | 43603.2917 | 69 | 64
2019-05-18 07:30 | 55 | 46 |  |  | 43603.3125 | 68 | 64
2019-05-18 08:00 | 55 | 46 |  |  | 43603.3333 | 71 | 68
2019-05-18 08:30 | 56 | 47 |  |  | 43603.3542 | 72 | 69
2019-05-18 09:00 | 56 | 48 |  |  | 43603.375 | 74 | 71
2019-05-18 09:30 | 57 | 49 |  |  | 43603.3958 | 76 | 74
2019-05-18 10:00 | 62 | 55 |  |  | 43603.4167 | 80 | 77
2019-05-18 10:30 | 64 | 58 |  |  | 43603.4375 | 81 | 79
2019-05-18 11:00 | 62 | 55 |  |  | 43603.4583 | 77 | 75
2019-05-18 11:30 | 58 | 50 |  |  | 43603.4792 | 74 | 72
2019-05-18 12:00 | 57 | 49 |  |  | 43603.5 | 73 | 71
2019-05-18 12:30 | 60 | 52 |  |  | 43603.5208 | 76 | 73
2019-05-18 13:00 | 61 | 53 |  |  | 43603.5417 | 79 | 77
2019-05-18 13:30 | 62 | 54 |  |  | 43603.5625 | 80 | 77
2019-05-18 14:00 | 58 | 49 |  |  | 43603.5833 | 75 | 72
2019-05-18 14:30 | 64 | 57 |  |  | 43603.6042 | 76 | 74
2019-05-18 15:00 | 63 | 56 |  |  | 43603.625 | 76 | 74
2019-05-18 15:30 | 61 | 54 |  |  | 43603.6458 | 75 | 73
2019-05-18 16:00 | 62 | 54 |  |  | 43603.6667 | 77 | 75
2019-05-18 16:30 | 61 | 54 |  |  | 43603.6875 | 78 | 76
2019-05-18 17:00 | 64 | 56 |  |  | 43603.7083 | 82 | 79
2019-05-18 17:30 | 68 | 61 |  |  | 43603.7292 | 86 | 83
2019-05-18 18:00 | 69 | 62 |  |  | 43603.75 | 87 | 85
2019-05-18 18:30 | 69 | 62 |  |  | 43603.7708 | 87 | 84
2019-05-18 19:00 | 69 | 62 |  |  | 43603.7917 | 87 | 84
2019-05-18 19:30 | 69 | 62 |  |  | 43603.8125 | 86 | 83
2019-05-18 20:00 | 69 | 62 |  |  | 43603.8333 | 86 | 83
2019-05-18 20:30 | 68 | 61 |  |  | 43603.8542 | 85 | 83
2019-05-18 21:00 | 67 | 60 |  |  | 43603.875 | 83 | 80
2019-05-18 21:30 | 67 | 59 |  |  | 43603.8958 | 81 | 78
2019-05-18 22:00 | 67 | 58 |  |  | 43603.9167 | 82 | 79
2019-05-18 22:30 | 67 | 59 |  |  | 43603.9375 | 83 | 80
2019-05-18 23:00 | 68 | 59 |  |  | 43603.9583 | 81 | 77
2019-05-18 23:30 | 65 | 56 |  |  | 43603.9792 | 78 | 74
2019-05-19 | 62 | 52 |  |  | 43604 | 74 | 70
2019-05-19 00:30 | 60 | 49 |  |  | 43604.0208 | 71 | 65
2019-05-19 01:00 | 58 | 46 |  |  | 43604.0417 | 67 | 61
2019-05-19 01:30 | 56 | 42 |  |  | 43604.0625 | 64 | 58
2019-05-19 02:00 | 55 | 40 |  |  | 43604.0833 | 63 | 56
2019-05-19 02:30 | 54 | 39 |  |  | 43604.1042 | 60 | 53
2019-05-19 03:00 | 50 | 38 |  |  | 43604.125 | 58 | 53
2019-05-19 03:30 | 48 | 42 |  |  | 43604.1458 | 59 | 56
2019-05-19 04:00 | 48 | 41 |  |  | 43604.1667 | 58 | 55
2019-05-19 04:30 | 47 | 40 |  |  | 43604.1875 | 58 | 56
2019-05-19 05:00 | 47 | 41 |  |  | 43604.2083 | 59 | 56
2019-05-19 05:30 | 48 | 42 |  |  | 43604.2292 | 61 | 58
2019-05-19 06:00 | 50 | 44 |  |  | 43604.25 | 63 | 60
2019-05-19 06:30 | 52 | 46 |  |  | 43604.2708 | 65 | 63
2019-05-19 07:00 | 52 | 46 |  |  | 43604.2917 | 67 | 65
2019-05-19 07:30 | 53 | 47 |  |  | 43604.3125 | 69 | 67
2019-05-19 08:00 | 52 | 47 |  |  | 43604.3333 | 70 | 68
2019-05-19 08:30 | 50 | 45 |  |  | 43604.3542 | 70 | 69
2019-05-19 09:00 | 49 | 44 |  |  | 43604.375 | 70 | 69
2019-05-19 09:30 | 49 | 45 |  |  | 43604.3958 | 72 | 71
2019-05-19 10:00 | 51 | 47 |  |  | 43604.4167 | 73 | 72
2019-05-19 10:30 | 49 | 45 |  |  | 43604.4375 | 69 | 68
2019-05-19 11:00 | 49 | 45 |  |  | 43604.4583 | 68 | 67
2019-05-19 11:30 | 51 | 48 |  |  | 43604.4792 | 67 | 66
2019-05-19 12:00 | 49 | 45 |  |  | 43604.5 | 62 | 61
2019-05-19 12:30 | 46 | 42 |  |  | 43604.5208 | 62 | 61
2019-05-19 13:00 | 49 | 46 |  |  | 43604.5417 | 67 | 66
2019-05-19 13:30 | 50 | 46 |  |  | 43604.5625 | 67 | 66
2019-05-19 14:00 | 51 | 48 |  |  | 43604.5833 | 66 | 66
2019-05-19 14:30 | 51 | 48 |  |  | 43604.6042 | 69 | 69
2019-05-19 15:00 | 54 | 51 |  |  | 43604.625 | 74 | 73
2019-05-19 15:30 | 57 | 55 |  |  | 43604.6458 | 77 | 77
2019-05-19 16:00 | 60 | 57 |  |  | 43604.6667 | 79 | 78
2019-05-19 16:30 | 61 | 58 |  |  | 43604.6875 | 81 | 80
2019-05-19 17:00 | 64 | 62 |  |  | 43604.7083 | 84 | 83
2019-05-19 17:30 | 68 | 65 |  |  | 43604.7292 | 87 | 87
2019-05-19 18:00 | 71 | 69 |  |  | 43604.75 | 91 | 91
2019-05-19 18:30 | 70 | 68 |  |  | 43604.7708 | 90 | 90
2019-05-19 19:00 | 71 | 68 |  |  | 43604.7917 | 90 | 90
2019-05-19 19:30 | 69 | 66 |  |  | 43604.8125 | 89 | 88
2019-05-19 20:00 | 67 | 65 |  |  | 43604.8333 | 88 | 87
2019-05-19 20:30 | 67 | 65 |  |  | 43604.8542 | 88 | 88
2019-05-19 21:00 | 65 | 62 |  |  | 43604.875 | 84 | 83
2019-05-19 21:30 | 62 | 59 |  |  | 43604.8958 | 81 | 80
2019-05-19 22:00 | 62 | 59 |  |  | 43604.9167 | 81 | 80
2019-05-19 22:30 | 62 | 59 |  |  | 43604.9375 | 82 | 81
2019-05-19 23:00 | 61 | 58 |  |  | 43604.9583 | 79 | 78
2019-05-19 23:30 | 59 | 55 |  |  | 43604.9792 | 76 | 75
2019-05-20 | 57 | 52 |  |  | 43605 | 72 | 71
2019-05-20 00:30 | 54 | 49 |  |  | 43605.0208 | 68 | 66
2019-05-20 01:00 | 52 | 47 |  |  | 43605.0417 | 65 | 63
2019-05-20 01:30 | 51 | 45 |  |  | 43605.0625 | 63 | 61
2019-05-20 02:00 | 50 | 44 |  |  | 43605.0833 | 62 | 59
2019-05-20 02:30 | 49 | 43 |  |  | 43605.1042 | 60 | 58
2019-05-20 03:00 | 48 | 42 |  |  | 43605.125 | 59 | 57
2019-05-20 03:30 | 49 | 42 |  |  | 43605.1458 | 60 | 57
2019-05-20 04:00 | 47 | 41 |  |  | 43605.1667 | 58 | 56
2019-05-20 04:30 | 49 | 44 |  |  | 43605.1875 | 61 | 58
2019-05-20 05:00 | 52 | 47 |  |  | 43605.2083 | 64 | 61
2019-05-20 05:30 | 56 | 52 |  |  | 43605.2292 | 68 | 67
2019-05-20 06:00 | 58 | 56 |  |  | 43605.25 | 74 | 73
2019-05-20 06:30 | 63 | 61 |  |  | 43605.2708 | 83 | 83
2019-05-20 07:00 | 66 | 64 |  |  | 43605.2917 | 90 | 89
2019-05-20 07:30 | 69 | 67 |  |  | 43605.3125 | 97 | 97
2019-05-20 08:00 | 71 | 69 |  |  | 43605.3333 | 100 | 100
2019-05-20 08:30 | 67 | 66 |  |  | 43605.3542 | 95 | 94
2019-05-20 09:00 | 66 | 65 |  |  | 43605.375 | 96 | 95
2019-05-20 09:30 | 64 | 62 |  |  | 43605.3958 | 93 | 92
2019-05-20 10:00 | 69 | 68 |  |  | 43605.4167 | 97 | 97
2019-05-20 10:30 | 66 | 65 |  |  | 43605.4375 | 97 | 97
2019-05-20 11:00 | 64 | 63 |  |  | 43605.4583 | 98 | 98
2019-05-20 11:30 | 62 | 61 |  |  | 43605.4792 | 92 | 92
2019-05-20 12:00 | 64 | 63 |  |  | 43605.5 | 94 | 94
2019-05-20 12:30 | 66 | 65 |  |  | 43605.5208 | 98 | 98
2019-05-20 13:00 | 67 | 66 |  |  | 43605.5417 | 97 | 97
2019-05-20 13:30 | 70 | 69 |  |  | 43605.5625 | 101 | 101
2019-05-20 14:00 | 70 | 70 |  |  | 43605.5833 | 100 | 100
2019-05-20 14:30 | 73 | 72 |  |  | 43605.6042 | 102 | 102
2019-05-20 15:00 | 74 | 73 |  |  | 43605.625 | 104 | 104
2019-05-20 15:30 | 78 | 77 |  |  | 43605.6458 | 106 | 106
2019-05-20 16:00 | 78 | 77 |  |  | 43605.6667 | 106 | 106
2019-05-20 16:30 | 79 | 78 |  |  | 43605.6875 | 107 | 107
2019-05-20 17:00 | 80 | 80 |  |  | 43605.7083 | 111 | 111
2019-05-20 17:30 | 83 | 83 |  |  | 43605.7292 | 113 | 113
2019-05-20 18:00 | 84 | 84 |  |  | 43605.75 | 113 | 113
2019-05-20 18:30 | 82 | 82 |  |  | 43605.7708 | 110 | 110
2019-05-20 19:00 | 81 | 81 |  |  | 43605.7917 | 109 | 108
2019-05-20 19:30 | 78 | 78 |  |  | 43605.8125 | 104 | 104
2019-05-20 20:00 | 76 | 76 |  |  | 43605.8333 | 102 | 101
2019-05-20 20:30 | 76 | 76 |  |  | 43605.8542 | 101 | 101
2019-05-20 21:00 | 72 | 72 |  |  | 43605.875 | 96 | 96
2019-05-20 21:30 | 68 | 68 |  |  | 43605.8958 | 90 | 90
2019-05-20 22:00 | 68 | 68 |  |  | 43605.9167 | 92 | 92
2019-05-20 22:30 | 65 | 65 |  |  | 43605.9375 | 89 | 89
2019-05-20 23:00 | 64 | 64 |  |  | 43605.9583 | 84 | 84
2019-05-20 23:30 | 64 | 64 |  |  | 43605.9792 | 84 | 84
2019-05-21 | 58 | 58 |  |  | 43606 | 78 | 78
2019-05-21 00:30 | 55 | 55 |  |  | 43606.0208 | 73 | 73
2019-05-21 01:00 | 52 | 52 |  |  | 43606.0417 | 69 | 69
2019-05-21 01:30 | 50 | 50 |  |  | 43606.0625 | 66 | 66
2019-05-21 02:00 | 49 | 49 |  |  | 43606.0833 | 66 | 65
2019-05-21 02:30 | 49 | 49 |  |  | 43606.1042 | 65 | 65
2019-05-21 03:00 | 48 | 48 |  |  | 43606.125 | 63 | 63
2019-05-21 03:30 | 47 | 47 |  |  | 43606.1458 | 63 | 62
2019-05-21 04:00 | 48 | 48 |  |  | 43606.1667 | 64 | 63
2019-05-21 04:30 | 50 | 50 |  |  | 43606.1875 | 66 | 66
2019-05-21 05:00 | 54 | 53 |  |  | 43606.2083 | 70 | 69
2019-05-21 05:30 | 59 | 59 |  |  | 43606.2292 | 75 | 75
2019-05-21 06:00 | 64 | 64 |  |  | 43606.25 | 83 | 83
2019-05-21 06:30 | 69 | 69 |  |  | 43606.2708 | 94 | 94
2019-05-21 07:00 | 73 | 73 |  |  | 43606.2917 | 100 | 100
2019-05-21 07:30 | 75 | 75 |  |  | 43606.3125 | 106 | 105
2019-05-21 08:00 | 73 | 72 |  |  | 43606.3333 | 107 | 103
2019-05-21 08:30 | 72 | 70 |  |  | 43606.3542 | 106 | 103
2019-05-21 09:00 | 73 | 71 |  |  | 43606.375 | 109 | 105
2019-05-21 09:30 | 71 | 70 |  |  | 43606.3958 | 106 | 103
2019-05-21 10:00 | 69 | 67 |  |  | 43606.4167 | 102 | 99
2019-05-21 10:30 | 65 | 64 |  |  | 43606.4375 | 99 | 96
2019-05-21 11:00 | 67 | 66 |  |  | 43606.4583 | 98 | 95
2019-05-21 11:30 | 69 | 68 |  |  | 43606.4792 | 99 | 96
2019-05-21 12:00 | 68 | 67 |  |  | 43606.5 | 98 | 96
2019-05-21 12:30 | 69 | 68 |  |  | 43606.5208 | 99 | 97
2019-05-21 13:00 | 69 | 68 |  |  | 43606.5417 | 99 | 96
2019-05-21 13:30 | 65 | 64 |  |  | 43606.5625 | 96 | 93
2019-05-21 14:00 | 65 | 64 |  |  | 43606.5833 | 99 | 97
2019-05-21 14:30 | 67 | 66 |  |  | 43606.6042 | 100 | 98
2019-05-21 15:00 | 70 | 69 |  |  | 43606.625 | 103 | 101
2019-05-21 15:30 | 75 | 74 |  |  | 43606.6458 | 110 | 107
2019-05-21 16:00 | 79 | 77 |  |  | 43606.6667 | 113 | 110
2019-05-21 16:30 | 80 | 78 |  |  | 43606.6875 | 114 | 111
2019-05-21 17:00 | 83 | 82 |  |  | 43606.7083 | 117 | 114
2019-05-21 17:30 | 86 | 84 |  |  | 43606.7292 | 120 | 115
2019-05-21 18:00 | 87 | 85 |  |  | 43606.75 | 120 | 115
2019-05-21 18:30 | 85 | 83 |  |  | 43606.7708 | 117 | 111
2019-05-21 19:00 | 85 | 82 |  |  | 43606.7917 | 115 | 109
2019-05-21 19:30 | 81 | 80 |  |  | 43606.8125 | 110 | 107
2019-05-21 20:00 | 79 | 79 |  |  | 43606.8333 | 104 | 104
2019-05-21 20:30 | 78 | 78 |  |  | 43606.8542 | 103 | 102
2019-05-21 21:00 | 73 | 73 |  |  | 43606.875 | 98 | 97
2019-05-21 21:30 | 69 | 69 |  |  | 43606.8958 | 93 | 92
2019-05-21 22:00 | 69 | 69 |  |  | 43606.9167 | 93 | 92
2019-05-21 22:30 | 67 | 67 |  |  | 43606.9375 | 91 | 90
2019-05-21 23:00 | 67 | 67 |  |  | 43606.9583 | 88 | 87
2019-05-21 23:30 | 65 | 65 |  |  | 43606.9792 | 85 | 84
2019-05-22 | 60 | 59 |  |  | 43607 | 80 | 78
2019-05-22 00:30 | 55 | 54 |  |  | 43607.0208 | 74 | 72
2019-05-22 01:00 | 51 | 50 |  |  | 43607.0417 | 70 | 67
2019-05-22 01:30 | 49 | 47 |  |  | 43607.0625 | 67 | 64
2019-05-22 02:00 | 46 | 44 |  |  | 43607.0833 | 64 | 60
2019-05-22 02:30 | 45 | 44 |  |  | 43607.1042 | 62 | 60
2019-05-22 03:00 | 45 | 44 |  |  | 43607.125 | 62 | 60
2019-05-22 03:30 | 45 | 44 |  |  | 43607.1458 | 62 | 60
2019-05-22 04:00 | 45 | 44 |  |  | 43607.1667 | 62 | 60
2019-05-22 04:30 | 47 | 46 |  |  | 43607.1875 | 65 | 63
2019-05-22 05:00 | 51 | 50 |  |  | 43607.2083 | 67 | 66
2019-05-22 05:30 | 56 | 55 |  |  | 43607.2292 | 73 | 72
2019-05-22 06:00 | 62 | 62 |  |  | 43607.25 | 80 | 80
2019-05-22 06:30 | 66 | 66 |  |  | 43607.2708 | 89 | 89
2019-05-22 07:00 | 68 | 68 |  |  | 43607.2917 | 98 | 95
2019-05-22 07:30 | 73 | 72 |  |  | 43607.3125 | 106 | 104
2019-05-22 08:00 | 72 | 71 |  |  | 43607.3333 | 107 | 104
2019-05-22 08:30 | 73 | 72 |  |  | 43607.3542 | 107 | 105
2019-05-22 09:00 | 70 | 70 |  |  | 43607.375 | 105 | 103
2019-05-22 09:30 | 67 | 66 |  |  | 43607.3958 | 101 | 99
2019-05-22 10:00 | 65 | 65 |  |  | 43607.4167 | 98 | 96
2019-05-22 10:30 | 65 | 65 |  |  | 43607.4375 | 97 | 96
2019-05-22 11:00 | 67 | 67 |  |  | 43607.4583 | 101 | 99
2019-05-22 11:30 | 74 | 74 |  |  | 43607.4792 | 109 | 108
2019-05-22 12:00 | 74 | 74 |  |  | 43607.5 | 108 | 107
2019-05-22 12:30 | 70 | 70 |  |  | 43607.5208 | 105 | 103
2019-05-22 13:00 | 73 | 72 |  |  | 43607.5417 | 106 | 104
2019-05-22 13:30 | 72 | 72 |  |  | 43607.5625 | 103 | 102
2019-05-22 14:00 | 73 | 73 |  |  | 43607.5833 | 103 | 102
2019-05-22 14:30 | 71 | 71 |  |  | 43607.6042 | 103 | 102
2019-05-22 15:00 | 71 | 71 |  |  | 43607.625 | 104 | 103
2019-05-22 15:30 | 73 | 72 |  |  | 43607.6458 | 105 | 104
2019-05-22 16:00 | 74 | 74 |  |  | 43607.6667 | 107 | 105
2019-05-22 16:30 | 76 | 75 |  |  | 43607.6875 | 108 | 106
2019-05-22 17:00 | 79 | 78 |  |  | 43607.7083 | 112 | 110
2019-05-22 17:30 | 82 | 81 |  |  | 43607.7292 | 115 | 113
2019-05-22 18:00 | 83 | 82 |  |  | 43607.75 | 114 | 112
2019-05-22 18:30 | 81 | 80 |  |  | 43607.7708 | 112 | 109
2019-05-22 19:00 | 80 | 79 |  |  | 43607.7917 | 111 | 108
2019-05-22 19:30 | 79 | 77 |  |  | 43607.8125 | 108 | 104
2019-05-22 20:00 | 78 | 77 |  |  | 43607.8333 | 107 | 103
2019-05-22 20:30 | 77 | 76 |  |  | 43607.8542 | 106 | 102
2019-05-22 21:00 | 71 | 71 |  |  | 43607.875 | 96 | 95
2019-05-22 21:30 | 66 | 66 |  |  | 43607.8958 | 90 | 90
2019-05-22 22:00 | 64 | 64 |  |  | 43607.9167 | 90 | 89
2019-05-22 22:30 | 62 | 62 |  |  | 43607.9375 | 87 | 87
2019-05-22 23:00 | 61 | 61 |  |  | 43607.9583 | 82 | 82
2019-05-22 23:30 | 57 | 57 |  |  | 43607.9792 | 78 | 77
2019-05-23 | 52 | 52 |  |  | 43608 | 73 | 72
2019-05-23 00:30 | 49 | 49 |  |  | 43608.0208 | 69 | 68
2019-05-23 01:00 | 46 | 45 |  |  | 43608.0417 | 64 | 63
2019-05-23 01:30 | 44 | 44 |  |  | 43608.0625 | 62 | 61
2019-05-23 02:00 | 44 | 44 |  |  | 43608.0833 | 61 | 60
2019-05-23 02:30 | 44 | 43 |  |  | 43608.1042 | 60 | 60
2019-05-23 03:00 | 44 | 43 |  |  | 43608.125 | 60 | 59
2019-05-23 03:30 | 44 | 44 |  |  | 43608.1458 | 63 | 60
2019-05-23 04:00 | 45 | 44 |  |  | 43608.1667 | 63 | 60
2019-05-23 04:30 | 48 | 47 |  |  | 43608.1875 | 65 | 62
2019-05-23 05:00 | 50 | 49 |  |  | 43608.2083 | 68 | 65
2019-05-23 05:30 | 54 | 53 |  |  | 43608.2292 | 72 | 70
2019-05-23 06:00 | 59 | 58 |  |  | 43608.25 | 77 | 76
2019-05-23 06:30 | 66 | 64 |  |  | 43608.2708 | 88 | 87
2019-05-23 07:00 | 72 | 70 |  |  | 43608.2917 | 97 | 96
2019-05-23 07:30 | 75 | 74 |  |  | 43608.3125 | 105 | 104
2019-05-23 08:00 | 71 | 71 |  |  | 43608.3333 | 104 | 102
2019-05-23 08:30 | 69 | 68 |  |  | 43608.3542 | 100 | 99
2019-05-23 09:00 | 66 | 65 |  |  | 43608.375 | 98 | 96
2019-05-23 09:30 | 64 | 63 |  |  | 43608.3958 | 96 | 94
2019-05-23 10:00 | 65 | 64 |  |  | 43608.4167 | 97 | 95
2019-05-23 10:30 | 63 | 62 |  |  | 43608.4375 | 90 | 88
2019-05-23 11:00 | 64 | 63 |  |  | 43608.4583 | 95 | 94
2019-05-23 11:30 | 68 | 67 |  |  | 43608.4792 | 99 | 98
2019-05-23 12:00 | 68 | 67 |  |  | 43608.5 | 100 | 98
2019-05-23 12:30 | 70 | 70 |  |  | 43608.5208 | 102 | 101
2019-05-23 13:00 | 70 | 69 |  |  | 43608.5417 | 98 | 96
2019-05-23 13:30 | 66 | 65 |  |  | 43608.5625 | 96 | 94
2019-05-23 14:00 | 68 | 68 |  |  | 43608.5833 | 100 | 98
2019-05-23 14:30 | 72 | 71 |  |  | 43608.6042 | 103 | 102
2019-05-23 15:00 | 75 | 74 |  |  | 43608.625 | 105 | 103
2019-05-23 15:30 | 73 | 73 |  |  | 43608.6458 | 104 | 102
2019-05-23 16:00 | 73 | 72 |  |  | 43608.6667 | 104 | 103
2019-05-23 16:30 | 74 | 74 |  |  | 43608.6875 | 105 | 103
2019-05-23 17:00 | 76 | 76 |  |  | 43608.7083 | 112 | 106
2019-05-23 17:30 | 79 | 79 |  |  | 43608.7292 | 115 | 109
2019-05-23 18:00 | 81 | 81 |  |  | 43608.75 | 116 | 110
2019-05-23 18:30 | 79 | 79 |  |  | 43608.7708 | 114 | 107
2019-05-23 19:00 | 80 | 80 |  |  | 43608.7917 | 115 | 107
2019-05-23 19:30 | 80 | 80 |  |  | 43608.8125 | 112 | 105
2019-05-23 20:00 | 77 | 77 |  |  | 43608.8333 | 105 | 101
2019-05-23 20:30 | 76 | 76 |  |  | 43608.8542 | 103 | 101
2019-05-23 21:00 | 73 | 72 |  |  | 43608.875 | 96 | 95
2019-05-23 21:30 | 70 | 68 |  |  | 43608.8958 | 91 | 90
2019-05-23 22:00 | 68 | 66 |  |  | 43608.9167 | 89 | 89
2019-05-23 22:30 | 65 | 63 |  |  | 43608.9375 | 87 | 86
2019-05-23 23:00 | 62 | 61 |  |  | 43608.9583 | 83 | 82
2019-05-23 23:30 | 57 | 55 |  |  | 43608.9792 | 78 | 77
2019-05-24 | 52 | 51 |  |  | 43609 | 73 | 72
2019-05-24 00:30 | 49 | 48 |  |  | 43609.0208 | 69 | 67
2019-05-24 01:00 | 47 | 46 |  |  | 43609.0417 | 65 | 63
2019-05-24 01:30 | 44 | 43 |  |  | 43609.0625 | 62 | 60
2019-05-24 02:00 | 44 | 43 |  |  | 43609.0833 | 60 | 59
2019-05-24 02:30 | 43 | 42 |  |  | 43609.1042 | 60 | 58
2019-05-24 03:00 | 44 | 42 |  |  | 43609.125 | 60 | 58
2019-05-24 03:30 | 45 | 44 |  |  | 43609.1458 | 61 | 60
2019-05-24 04:00 | 46 | 45 |  |  | 43609.1667 | 63 | 61
2019-05-24 04:30 | 49 | 48 |  |  | 43609.1875 | 65 | 63
2019-05-24 05:00 | 52 | 51 |  |  | 43609.2083 | 68 | 67
2019-05-24 05:30 | 56 | 54 |  |  | 43609.2292 | 72 | 71
2019-05-24 06:00 | 61 | 60 |  |  | 43609.25 | 78 | 78
2019-05-24 06:30 | 66 | 64 |  |  | 43609.2708 | 87 | 87
2019-05-24 07:00 | 70 | 68 |  |  | 43609.2917 | 95 | 95
2019-05-24 07:30 | 73 | 71 |  |  | 43609.3125 | 102 | 101
2019-05-24 08:00 | 69 | 68 |  |  | 43609.3333 | 102 | 100
2019-05-24 08:30 | 66 | 66 |  |  | 43609.3542 | 101 | 98
2019-05-24 09:00 | 64 | 63 |  |  | 43609.375 | 97 | 95
2019-05-24 09:30 | 62 | 61 |  |  | 43609.3958 | 94 | 92
2019-05-24 10:00 | 61 | 60 |  |  | 43609.4167 | 93 | 91
2019-05-24 10:30 | 60 | 59 |  |  | 43609.4375 | 92 | 90
2019-05-24 11:00 | 60 | 59 |  |  | 43609.4583 | 92 | 91
2019-05-24 11:30 | 62 | 60 |  |  | 43609.4792 | 91 | 90
2019-05-24 12:00 | 63 | 62 |  |  | 43609.5 | 94 | 92
2019-05-24 12:30 | 61 | 60 |  |  | 43609.5208 | 94 | 92
2019-05-24 13:00 | 63 | 62 |  |  | 43609.5417 | 95 | 92
2019-05-24 13:30 | 66 | 65 |  |  | 43609.5625 | 98 | 96
2019-05-24 14:00 | 70 | 69 |  |  | 43609.5833 | 100 | 98
2019-05-24 14:30 | 70 | 69 |  |  | 43609.6042 | 102 | 100
2019-05-24 15:00 | 67 | 66 |  |  | 43609.625 | 99 | 97
2019-05-24 15:30 | 68 | 67 |  |  | 43609.6458 | 101 | 98
2019-05-24 16:00 | 70 | 69 |  |  | 43609.6667 | 102 | 100
2019-05-24 16:30 | 70 | 69 |  |  | 43609.6875 | 102 | 99
2019-05-24 17:00 | 73 | 72 |  |  | 43609.7083 | 105 | 102
2019-05-24 17:30 | 76 | 76 |  |  | 43609.7292 | 108 | 105
2019-05-24 18:00 | 75 | 75 |  |  | 43609.75 | 107 | 103
2019-05-24 18:30 | 72 | 72 |  |  | 43609.7708 | 103 | 99
2019-05-24 19:00 | 72 | 72 |  |  | 43609.7917 | 103 | 99
2019-05-24 19:30 | 71 | 71 |  |  | 43609.8125 | 100 | 97
2019-05-24 20:00 | 69 | 68 |  |  | 43609.8333 | 97 | 94
2019-05-24 20:30 | 68 | 68 |  |  | 43609.8542 | 97 | 93
2019-05-24 21:00 | 66 | 65 |  |  | 43609.875 | 93 | 89
2019-05-24 21:30 | 63 | 62 |  |  | 43609.8958 | 89 | 85
2019-05-24 22:00 | 61 | 61 |  |  | 43609.9167 | 89 | 85
2019-05-24 22:30 | 59 | 59 |  |  | 43609.9375 | 87 | 84
2019-05-24 23:00 | 58 | 57 |  |  | 43609.9583 | 81 | 79
2019-05-24 23:30 | 55 | 55 |  |  | 43609.9792 | 79 | 76
2019-05-25 | 51 | 51 |  |  | 43610 | 75 | 71
2019-05-25 00:30 | 49 | 48 |  |  | 43610.0208 | 71 | 67
2019-05-25 01:00 | 47 | 47 |  |  | 43610.0417 | 67 | 64
2019-05-25 01:30 | 45 | 45 |  |  | 43610.0625 | 65 | 62
2019-05-25 02:00 | 45 | 45 |  |  | 43610.0833 | 64 | 60
2019-05-25 02:30 | 45 | 45 |  |  | 43610.1042 | 63 | 60
2019-05-25 03:00 | 47 | 46 |  |  | 43610.125 | 64 | 60
2019-05-25 03:30 | 47 | 47 |  |  | 43610.1458 | 65 | 61
2019-05-25 04:00 | 47 | 47 |  |  | 43610.1667 | 65 | 61
2019-05-25 04:30 | 48 | 48 |  |  | 43610.1875 | 66 | 62
2019-05-25 05:00 | 50 | 50 |  |  | 43610.2083 | 67 | 63
2019-05-25 05:30 | 51 | 51 |  |  | 43610.2292 | 69 | 65
2019-05-25 06:00 | 53 | 53 |  |  | 43610.25 | 71 | 68
2019-05-25 06:30 | 54 | 54 |  |  | 43610.2708 | 74 | 70
2019-05-25 07:00 | 55 | 55 |  |  | 43610.2917 | 76 | 73
2019-05-25 07:30 | 53 | 53 |  |  | 43610.3125 | 76 | 74
2019-05-25 08:00 | 52 | 51 |  |  | 43610.3333 | 75 | 73
2019-05-25 08:30 | 52 | 51 |  |  | 43610.3542 | 76 | 75
2019-05-25 09:00 | 53 | 52 |  |  | 43610.375 | 76 | 75
2019-05-25 09:30 | 53 | 52 |  |  | 43610.3958 | 76 | 75
2019-05-25 10:00 | 53 | 52 |  |  | 43610.4167 | 75 | 74
2019-05-25 10:30 | 54 | 53 |  |  | 43610.4375 | 75 | 74
2019-05-25 11:00 | 54 | 53 |  |  | 43610.4583 | 73 | 71
2019-05-25 11:30 | 54 | 53 |  |  | 43610.4792 | 75 | 74
2019-05-25 12:00 | 54 | 53 |  |  | 43610.5 | 75 | 73
2019-05-25 12:30 | 56 | 55 |  |  | 43610.5208 | 77 | 76
2019-05-25 13:00 | 57 | 56 |  |  | 43610.5417 | 77 | 76
2019-05-25 13:30 | 58 | 57 |  |  | 43610.5625 | 76 | 75
2019-05-25 14:00 | 58 | 57 |  |  | 43610.5833 | 80 | 79
2019-05-25 14:30 | 58 | 58 |  |  | 43610.6042 | 80 | 79
2019-05-25 15:00 | 60 | 59 |  |  | 43610.625 | 81 | 79
2019-05-25 15:30 | 61 | 60 |  |  | 43610.6458 | 82 | 80
2019-05-25 16:00 | 62 | 61 |  |  | 43610.6667 | 86 | 85
2019-05-25 16:30 | 61 | 61 |  |  | 43610.6875 | 85 | 84
2019-05-25 17:00 | 65 | 64 |  |  | 43610.7083 | 89 | 88
2019-05-25 17:30 | 67 | 67 |  |  | 43610.7292 | 93 | 92
2019-05-25 18:00 | 67 | 67 |  |  | 43610.75 | 94 | 93
2019-05-25 18:30 | 66 | 66 |  |  | 43610.7708 | 93 | 91
2019-05-25 19:00 | 66 | 66 |  |  | 43610.7917 | 93 | 91
2019-05-25 19:30 | 65 | 65 |  |  | 43610.8125 | 91 | 89
2019-05-25 20:00 | 65 | 64 |  |  | 43610.8333 | 90 | 88
2019-05-25 20:30 | 64 | 63 |  |  | 43610.8542 | 90 | 88
2019-05-25 21:00 | 60 | 60 |  |  | 43610.875 | 85 | 83
2019-05-25 21:30 | 59 | 58 |  |  | 43610.8958 | 83 | 80
2019-05-25 22:00 | 60 | 60 |  |  | 43610.9167 | 84 | 82
2019-05-25 22:30 | 60 | 60 |  |  | 43610.9375 | 85 | 83
2019-05-25 23:00 | 60 | 60 |  |  | 43610.9583 | 83 | 80
2019-05-25 23:30 | 59 | 58 |  |  | 43610.9792 | 82 | 78
2019-05-26 | 54 | 54 |  |  | 43611 | 77 | 73
2019-05-26 00:30 | 52 | 52 |  |  | 43611.0208 | 74 | 69
2019-05-26 01:00 | 50 | 50 |  |  | 43611.0417 | 71 | 66
2019-05-26 01:30 | 49 | 49 |  |  | 43611.0625 | 69 | 64
2019-05-26 02:00 | 49 | 49 |  |  | 43611.0833 | 67 | 64
2019-05-26 02:30 | 48 | 48 |  |  | 43611.1042 | 66 | 62
2019-05-26 03:00 | 47 | 47 |  |  | 43611.125 | 65 | 61
2019-05-26 03:30 | 46 | 46 |  |  | 43611.1458 | 65 | 61
2019-05-26 04:00 | 46 | 46 |  |  | 43611.1667 | 65 | 61
2019-05-26 04:30 | 46 | 46 |  |  | 43611.1875 | 65 | 61
2019-05-26 05:00 | 49 | 49 |  |  | 43611.2083 | 65 | 61
2019-05-26 05:30 | 49 | 49 |  |  | 43611.2292 | 67 | 63
2019-05-26 06:00 | 50 | 50 |  |  | 43611.25 | 69 | 65
2019-05-26 06:30 | 52 | 52 |  |  | 43611.2708 | 71 | 68
2019-05-26 07:00 | 52 | 52 |  |  | 43611.2917 | 73 | 69
2019-05-26 07:30 | 53 | 53 |  |  | 43611.3125 | 73 | 70
2019-05-26 08:00 | 51 | 50 |  |  | 43611.3333 | 72 | 69
2019-05-26 08:30 | 54 | 54 |  |  | 43611.3542 | 76 | 73
2019-05-26 09:00 | 56 | 56 |  |  | 43611.375 | 76 | 74
2019-05-26 09:30 | 56 | 56 |  |  | 43611.3958 | 80 | 78
2019-05-26 10:00 | 57 | 56 |  |  | 43611.4167 | 80 | 78
2019-05-26 10:30 | 54 | 54 |  |  | 43611.4375 | 77 | 75
2019-05-26 11:00 | 54 | 53 |  |  | 43611.4583 | 75 | 74
2019-05-26 11:30 | 52 | 51 |  |  | 43611.4792 | 73 | 71
2019-05-26 12:00 | 50 | 49 |  |  | 43611.5 | 72 | 70
2019-05-26 12:30 | 48 | 47 |  |  | 43611.5208 | 70 | 68
2019-05-26 13:00 | 44 | 43 |  |  | 43611.5417 | 64 | 63
2019-05-26 13:30 | 51 | 50 |  |  | 43611.5625 | 67 | 65
2019-05-26 14:00 | 60 | 59 |  |  | 43611.5833 | 81 | 80
2019-05-26 14:30 | 62 | 61 |  |  | 43611.6042 | 80 | 79
2019-05-26 15:00 | 66 | 66 |  |  | 43611.625 | 85 | 84
2019-05-26 15:30 | 67 | 67 |  |  | 43611.6458 | 87 | 86
2019-05-26 16:00 | 68 | 67 |  |  | 43611.6667 | 88 | 87
2019-05-26 16:30 | 71 | 70 |  |  | 43611.6875 | 92 | 91
2019-05-26 17:00 | 73 | 72 |  |  | 43611.7083 | 94 | 93
2019-05-26 17:30 | 77 | 77 |  |  | 43611.7292 | 99 | 97
2019-05-26 18:00 | 77 | 77 |  |  | 43611.75 | 101 | 98
2019-05-26 18:30 | 75 | 75 |  |  | 43611.7708 | 99 | 96
2019-05-26 19:00 | 76 | 76 |  |  | 43611.7917 | 99 | 96
2019-05-26 19:30 | 73 | 73 |  |  | 43611.8125 | 97 | 94
2019-05-26 20:00 | 70 | 70 |  |  | 43611.8333 | 95 | 91
2019-05-26 20:30 | 68 | 68 |  |  | 43611.8542 | 93 | 89
2019-05-26 21:00 | 64 | 64 |  |  | 43611.875 | 89 | 85
2019-05-26 21:30 | 62 | 61 |  |  | 43611.8958 | 86 | 82
2019-05-26 22:00 | 61 | 61 |  |  | 43611.9167 | 86 | 82
2019-05-26 22:30 | 62 | 62 |  |  | 43611.9375 | 88 | 83
2019-05-26 23:00 | 63 | 63 |  |  | 43611.9583 | 87 | 82
2019-05-26 23:30 | 60 | 60 |  |  | 43611.9792 | 84 | 79
2019-05-27 | 56 | 56 |  |  | 43612 | 80 | 75
2019-05-27 00:30 | 54 | 54 |  |  | 43612.0208 | 75 | 71
2019-05-27 01:00 | 53 | 53 |  |  | 43612.0417 | 72 | 68
2019-05-27 01:30 | 51 | 51 |  |  | 43612.0625 | 70 | 67
2019-05-27 02:00 | 51 | 50 |  |  | 43612.0833 | 69 | 65
2019-05-27 02:30 | 51 | 51 |  |  | 43612.1042 | 67 | 65
2019-05-27 03:00 | 51 | 51 |  |  | 43612.125 | 67 | 65
2019-05-27 03:30 | 49 | 49 |  |  | 43612.1458 | 66 | 64
2019-05-27 04:00 | 50 | 49 |  |  | 43612.1667 | 66 | 64
2019-05-27 04:30 | 52 | 52 |  |  | 43612.1875 | 68 | 66
2019-05-27 05:00 | 55 | 55 |  |  | 43612.2083 | 71 | 69
2019-05-27 05:30 | 60 | 59 |  |  | 43612.2292 | 75 | 74
2019-05-27 06:00 | 66 | 65 |  |  | 43612.25 | 83 | 82
2019-05-27 06:30 | 70 | 70 |  |  | 43612.2708 | 97 | 92
2019-05-27 07:00 | 74 | 74 |  |  | 43612.2917 | 106 | 100
2019-05-27 07:30 | 76 | 76 |  |  | 43612.3125 | 112 | 106
2019-05-27 08:00 | 72 | 72 |  |  | 43612.3333 | 109 | 104
2019-05-27 08:30 | 69 | 69 |  |  | 43612.3542 | 106 | 101
2019-05-27 09:00 | 69 | 69 |  |  | 43612.375 | 108 | 104
2019-05-27 09:30 | 67 | 67 |  |  | 43612.3958 | 105 | 100
2019-05-27 10:00 | 63 | 63 |  |  | 43612.4167 | 100 | 95
2019-05-27 10:30 | 63 | 63 |  |  | 43612.4375 | 99 | 94
2019-05-27 11:00 | 62 | 62 |  |  | 43612.4583 | 99 | 95
2019-05-27 11:30 | 60 | 60 |  |  | 43612.4792 | 96 | 91
2019-05-27 12:00 | 59 | 59 |  |  | 43612.5 | 93 | 88
2019-05-27 12:30 | 59 | 59 |  |  | 43612.5208 | 94 | 89
2019-05-27 13:00 | 60 | 60 |  |  | 43612.5417 | 94 | 90
2019-05-27 13:30 | 64 | 64 |  |  | 43612.5625 | 98 | 94
2019-05-27 14:00 | 66 | 66 |  |  | 43612.5833 | 100 | 96
2019-05-27 14:30 | 67 | 67 |  |  | 43612.6042 | 101 | 97
2019-05-27 15:00 | 71 | 71 |  |  | 43612.625 | 104 | 100
2019-05-27 15:30 | 74 | 74 |  |  | 43612.6458 | 108 | 103
2019-05-27 16:00 | 76 | 76 |  |  | 43612.6667 | 111 | 105
2019-05-27 16:30 | 79 | 79 |  |  | 43612.6875 | 114 | 109
2019-05-27 17:00 | 83 | 83 |  |  | 43612.7083 | 117 | 111
2019-05-27 17:30 | 91 | 87 |  |  | 43612.7292 | 122 | 113
2019-05-27 18:00 | 98 | 89 |  |  | 43612.75 | 123 | 113
2019-05-27 18:30 | 96 | 86 |  |  | 43612.7708 | 121 | 109
2019-05-27 19:00 | 95 | 87 |  |  | 43612.7917 | 119 | 109
2019-05-27 19:30 | 93 | 84 |  |  | 43612.8125 | 116 | 106
2019-05-27 20:00 | 90 | 82 |  |  | 43612.8333 | 113 | 104
2019-05-27 20:30 | 87 | 80 |  |  | 43612.8542 | 112 | 102
2019-05-27 21:00 | 79 | 75 |  |  | 43612.875 | 98 | 95
2019-05-27 21:30 | 76 | 72 |  |  | 43612.8958 | 94 | 91
2019-05-27 22:00 | 73 | 71 |  |  | 43612.9167 | 92 | 91
2019-05-27 22:30 | 68 | 66 |  |  | 43612.9375 | 87 | 86
2019-05-27 23:00 | 65 | 63 |  |  | 43612.9583 | 82 | 81
2019-05-27 23:30 | 62 | 60 |  |  | 43612.9792 | 79 | 78
2019-05-28 | 59 | 55 |  |  | 43613 | 75 | 74
2019-05-28 00:30 | 56 | 52 |  |  | 43613.0208 | 71 | 69
2019-05-28 01:00 | 55 | 51 |  |  | 43613.0417 | 68 | 65
2019-05-28 01:30 | 55 | 50 |  |  | 43613.0625 | 66 | 64
2019-05-28 02:00 | 55 | 50 |  |  | 43613.0833 | 65 | 62
2019-05-28 02:30 | 53 | 49 |  |  | 43613.1042 | 64 | 62
2019-05-28 03:00 | 53 | 49 |  |  | 43613.125 | 63 | 62
2019-05-28 03:30 | 54 | 50 |  |  | 43613.1458 | 65 | 63
2019-05-28 04:00 | 55 | 50 |  |  | 43613.1667 | 64 | 63
2019-05-28 04:30 | 56 | 51 |  |  | 43613.1875 | 65 | 64
2019-05-28 05:00 | 58 | 55 |  |  | 43613.2083 | 69 | 68
2019-05-28 05:30 | 61 | 59 |  |  | 43613.2292 | 73 | 73
2019-05-28 06:00 | 66 | 65 |  |  | 43613.25 | 81 | 81
2019-05-28 06:30 | 72 | 70 |  |  | 43613.2708 | 92 | 92
2019-05-28 07:00 | 78 | 77 |  |  | 43613.2917 | 102 | 102
2019-05-28 07:30 | 83 | 81 |  |  | 43613.3125 | 111 | 109
2019-05-28 08:00 | 80 | 78 |  |  | 43613.3333 | 109 | 107
2019-05-28 08:30 | 77 | 74 |  |  | 43613.3542 | 105 | 103
2019-05-28 09:00 | 73 | 70 |  |  | 43613.375 | 101 | 99
2019-05-28 09:30 | 71 | 68 |  |  | 43613.3958 | 97 | 95
2019-05-28 10:00 | 68 | 65 |  |  | 43613.4167 | 94 | 92
2019-05-28 10:30 | 64 | 61 |  |  | 43613.4375 | 90 | 88
2019-05-28 11:00 | 61 | 58 |  |  | 43613.4583 | 87 | 85
2019-05-28 11:30 | 58 | 54 |  |  | 43613.4792 | 83 | 81
2019-05-28 12:00 | 56 | 52 |  |  | 43613.5 | 82 | 80
2019-05-28 12:30 | 56 | 52 |  |  | 43613.5208 | 83 | 81
2019-05-28 13:00 | 56 | 52 |  |  | 43613.5417 | 83 | 81
2019-05-28 13:30 | 58 | 54 |  |  | 43613.5625 | 84 | 82
2019-05-28 14:00 | 61 | 57 |  |  | 43613.5833 | 87 | 85
2019-05-28 14:30 | 64 | 61 |  |  | 43613.6042 | 90 | 88
2019-05-28 15:00 | 67 | 64 |  |  | 43613.625 | 94 | 92
2019-05-28 15:30 | 72 | 69 |  |  | 43613.6458 | 98 | 96
2019-05-28 16:00 | 77 | 73 |  |  | 43613.6667 | 103 | 101
2019-05-28 16:30 | 82 | 79 |  |  | 43613.6875 | 108 | 105
2019-05-28 17:00 | 86 | 84 |  |  | 43613.7083 | 111 | 109
2019-05-28 17:30 | 89 | 86 |  |  | 43613.7292 | 114 | 111
2019-05-28 18:00 | 93 | 89 |  |  | 43613.75 | 117 | 113
2019-05-28 18:30 | 92 | 88 |  |  | 43613.7708 | 114 | 110
2019-05-28 19:00 | 93 | 89 |  |  | 43613.7917 | 115 | 111
2019-05-28 19:30 | 90 | 86 |  |  | 43613.8125 | 112 | 107
2019-05-28 20:00 | 89 | 85 |  |  | 43613.8333 | 109 | 105
2019-05-28 20:30 | 88 | 84 |  |  | 43613.8542 | 109 | 105
2019-05-28 21:00 | 84 | 82 |  |  | 43613.875 | 103 | 102
2019-05-28 21:30 | 81 | 79 |  |  | 43613.8958 | 99 | 97
2019-05-28 22:00 | 78 | 76 |  |  | 43613.9167 | 97 | 96
2019-05-28 22:30 | 74 | 72 |  |  | 43613.9375 | 93 | 92
2019-05-28 23:00 | 70 | 67 |  |  | 43613.9583 | 88 | 86
2019-05-28 23:30 | 65 | 62 |  |  | 43613.9792 | 82 | 80
2019-05-29 | 58 | 54 |  |  | 43614 | 76 | 74
2019-05-29 00:30 | 55 | 50 |  |  | 43614.0208 | 71 | 68
2019-05-29 01:00 | 53 | 47 |  |  | 43614.0417 | 67 | 64
2019-05-29 01:30 | 52 | 46 |  |  | 43614.0625 | 64 | 60
2019-05-29 02:00 | 52 | 45 |  |  | 43614.0833 | 62 | 59
2019-05-29 02:30 | 51 | 45 |  |  | 43614.1042 | 62 | 59
2019-05-29 03:00 | 51 | 45 |  |  | 43614.125 | 62 | 59
2019-05-29 03:30 | 53 | 47 |  |  | 43614.1458 | 63 | 60
2019-05-29 04:00 | 55 | 48 |  |  | 43614.1667 | 65 | 63
2019-05-29 04:30 | 57 | 50 |  |  | 43614.1875 | 68 | 65
2019-05-29 05:00 | 60 | 54 |  |  | 43614.2083 | 72 | 69
2019-05-29 05:30 | 64 | 60 |  |  | 43614.2292 | 78 | 76
2019-05-29 06:00 | 68 | 65 |  |  | 43614.25 | 85 | 84
2019-05-29 06:30 | 75 | 73 |  |  | 43614.2708 | 96 | 95
2019-05-29 07:00 | 80 | 79 |  |  | 43614.2917 | 106 | 106
2019-05-29 07:30 | 85 | 82 |  |  | 43614.3125 | 114 | 113
2019-05-29 08:00 | 82 | 79 |  |  | 43614.3333 | 113 | 111
2019-05-29 08:30 | 75 | 72 |  |  | 43614.3542 | 107 | 105
2019-05-29 09:00 | 70 | 67 |  |  | 43614.375 | 100 | 99
2019-05-29 09:30 | 67 | 64 |  |  | 43614.3958 | 97 | 95
2019-05-29 10:00 | 64 | 61 |  |  | 43614.4167 | 93 | 92
2019-05-29 10:30 | 62 | 59 |  |  | 43614.4375 | 90 | 89
2019-05-29 11:00 | 58 | 57 |  |  | 43614.4583 | 87 | 87
2019-05-29 11:30 | 56 | 55 |  |  | 43614.4792 | 84 | 84
2019-05-29 12:00 | 56 | 55 |  |  | 43614.5 | 83 | 83
2019-05-29 12:30 | 55 | 53 |  |  | 43614.5208 | 81 | 81
2019-05-29 13:00 | 57 | 56 |  |  | 43614.5417 | 84 | 84
2019-05-29 13:30 | 57 | 56 |  |  | 43614.5625 | 86 | 86
2019-05-29 14:00 | 60 | 60 |  |  | 43614.5833 | 89 | 89
2019-05-29 14:30 | 62 | 61 |  |  | 43614.6042 | 92 | 92
2019-05-29 15:00 | 63 | 63 |  |  | 43614.625 | 93 | 93
2019-05-29 15:30 | 68 | 67 |  |  | 43614.6458 | 98 | 98
2019-05-29 16:00 | 73 | 73 |  |  | 43614.6667 | 103 | 103
2019-05-29 16:30 | 78 | 77 |  |  | 43614.6875 | 107 | 106
2019-05-29 17:00 | 85 | 83 |  |  | 43614.7083 | 112 | 110
2019-05-29 17:30 | 90 | 87 |  |  | 43614.7292 | 116 | 113
2019-05-29 18:00 | 91 | 88 |  |  | 43614.75 | 117 | 115
2019-05-29 18:30 | 90 | 87 |  |  | 43614.7708 | 114 | 111
2019-05-29 19:00 | 91 | 87 |  |  | 43614.7917 | 115 | 112
2019-05-29 19:30 | 90 | 87 |  |  | 43614.8125 | 114 | 110
2019-05-29 20:00 | 87 | 84 |  |  | 43614.8333 | 110 | 107
2019-05-29 20:30 | 86 | 83 |  |  | 43614.8542 | 109 | 105
2019-05-29 21:00 | 82 | 78 |  |  | 43614.875 | 104 | 100
2019-05-29 21:30 | 80 | 75 |  |  | 43614.8958 | 100 | 96
2019-05-29 22:00 | 77 | 72 |  |  | 43614.9167 | 99 | 94
2019-05-29 22:30 | 71 | 68 |  |  | 43614.9375 | 91 | 90
2019-05-29 23:00 | 67 | 64 |  |  | 43614.9583 | 86 | 84
2019-05-29 23:30 | 62 | 58 |  |  | 43614.9792 | 80 | 78
2019-05-30 | 56 | 51 |  |  | 43615 | 74 | 72
2019-05-30 00:30 | 52 | 47 |  |  | 43615.0208 | 68 | 65
2019-05-30 01:00 | 51 | 45 |  |  | 43615.0417 | 66 | 62
2019-05-30 01:30 | 51 | 43 |  |  | 43615.0625 | 64 | 60
2019-05-30 02:00 | 50 | 42 |  |  | 43615.0833 | 63 | 58
2019-05-30 02:30 | 50 | 43 |  |  | 43615.1042 | 62 | 57
2019-05-30 03:00 | 51 | 43 |  |  | 43615.125 | 62 | 57
2019-05-30 03:30 | 51 | 43 |  |  | 43615.1458 | 63 | 58
2019-05-30 04:00 | 54 | 47 |  |  | 43615.1667 | 65 | 59
2019-05-30 04:30 | 57 | 49 |  |  | 43615.1875 | 67 | 62
2019-05-30 05:00 | 59 | 53 |  |  | 43615.2083 | 70 | 66
2019-05-30 05:30 | 61 | 56 |  |  | 43615.2292 | 74 | 70
2019-05-30 06:00 | 66 | 62 |  |  | 43615.25 | 80 | 78
2019-05-30 06:30 | 73 | 70 |  |  | 43615.2708 | 92 | 90
2019-05-30 07:00 | 80 | 77 |  |  | 43615.2917 | 104 | 103
2019-05-30 07:30 | 84 | 81 |  |  | 43615.3125 | 113 | 111
2019-05-30 08:00 | 81 | 78 |  |  | 43615.3333 | 110 | 108
2019-05-30 08:30 | 77 | 73 |  |  | 43615.3542 | 106 | 104
2019-05-30 09:00 | 73 | 69 |  |  | 43615.375 | 101 | 98
2019-05-30 09:30 | 69 | 66 |  |  | 43615.3958 | 97 | 95
2019-05-30 10:00 | 66 | 63 |  |  | 43615.4167 | 93 | 91
2019-05-30 10:30 | 64 | 61 |  |  | 43615.4375 | 89 | 88
2019-05-30 11:00 | 63 | 61 |  |  | 43615.4583 | 88 | 87
2019-05-30 11:30 | 59 | 58 |  |  | 43615.4792 | 84 | 84
2019-05-30 12:00 | 59 | 58 |  |  | 43615.5 | 84 | 84
2019-05-30 12:30 | 58 | 57 |  |  | 43615.5208 | 84 | 84
2019-05-30 13:00 | 58 | 56 |  |  | 43615.5417 | 83 | 83
2019-05-30 13:30 | 60 | 59 |  |  | 43615.5625 | 86 | 85
2019-05-30 14:00 | 63 | 61 |  |  | 43615.5833 | 88 | 87
2019-05-30 14:30 | 65 | 63 |  |  | 43615.6042 | 90 | 89
2019-05-30 15:00 | 68 | 67 |  |  | 43615.625 | 93 | 92
2019-05-30 15:30 | 70 | 68 |  |  | 43615.6458 | 94 | 94
2019-05-30 16:00 | 74 | 72 |  |  | 43615.6667 | 99 | 98
2019-05-30 16:30 | 77 | 73 |  |  | 43615.6875 | 104 | 100
2019-05-30 17:00 | 83 | 78 |  |  | 43615.7083 | 112 | 104
2019-05-30 17:30 | 89 | 83 |  |  | 43615.7292 | 116 | 108
2019-05-30 18:00 | 91 | 85 |  |  | 43615.75 | 117 | 110
2019-05-30 18:30 | 89 | 84 |  |  | 43615.7708 | 112 | 106
2019-05-30 19:00 | 91 | 86 |  |  | 43615.7917 | 113 | 107
2019-05-30 19:30 | 90 | 85 |  |  | 43615.8125 | 112 | 106
2019-05-30 20:00 | 87 | 85 |  |  | 43615.8333 | 106 | 104
2019-05-30 20:30 | 86 | 85 |  |  | 43615.8542 | 105 | 105
2019-05-30 21:00 | 81 | 80 |  |  | 43615.875 | 100 | 100
2019-05-30 21:30 | 77 | 75 |  |  | 43615.8958 | 95 | 94
2019-05-30 22:00 | 74 | 73 |  |  | 43615.9167 | 93 | 92
2019-05-30 22:30 | 68 | 67 |  |  | 43615.9375 | 88 | 87
2019-05-30 23:00 | 66 | 64 |  |  | 43615.9583 | 84 | 83
2019-05-30 23:30 | 60 | 58 |  |  | 43615.9792 | 78 | 77
2019-05-31 | 54 | 51 |  |  | 43616 | 71 | 70
2019-05-31 00:30 | 50 | 47 |  |  | 43616.0208 | 66 | 65
2019-05-31 01:00 | 47 | 45 |  |  | 43616.0417 | 61 | 61
2019-05-31 01:30 | 46 | 43 |  |  | 43616.0625 | 60 | 59
2019-05-31 02:00 | 46 | 42 |  |  | 43616.0833 | 58 | 58
2019-05-31 02:30 | 48 | 43 |  |  | 43616.1042 | 59 | 58
2019-05-31 03:00 | 49 | 44 |  |  | 43616.125 | 59 | 58
2019-05-31 03:30 | 50 | 46 |  |  | 43616.1458 | 61 | 60
2019-05-31 04:00 | 53 | 49 |  |  | 43616.1667 | 63 | 62
2019-05-31 04:30 | 55 | 51 |  |  | 43616.1875 | 66 | 65
2019-05-31 05:00 | 58 | 54 |  |  | 43616.2083 | 69 | 68
2019-05-31 05:30 | 61 | 58 |  |  | 43616.2292 | 73 | 73
2019-05-31 06:00 | 67 | 66 |  |  | 43616.25 | 81 | 81
2019-05-31 06:30 | 77 | 77 |  |  | 43616.2708 | 97 | 97
2019-05-31 07:00 | 89 | 87 |  |  | 43616.2917 | 112 | 112
2019-05-31 07:30 | 103 | 93 |  |  | 43616.3125 | 127 | 123
2019-05-31 08:00 | 99 | 90 |  |  | 43616.3333 | 126 | 122
2019-05-31 08:30 | 93 | 83 |  |  | 43616.3542 | 120 | 116
2019-05-31 09:00 | 88 | 77 |  |  | 43616.375 | 115 | 110
2019-05-31 09:30 | 89 | 71 |  |  | 43616.3958 | 108 | 104
2019-05-31 10:00 | 90 | 68 |  |  | 43616.4167 | 100 | 97
2019-05-31 10:30 | 88 | 66 |  |  | 43616.4375 | 98 | 95
2019-05-31 11:00 | 82 | 64 |  |  | 43616.4583 | 95 | 93
2019-05-31 11:30 | 71 | 61 |  |  | 43616.4792 | 88 | 88
2019-05-31 12:00 | 70 | 60 |  |  | 43616.5 | 87 | 86
2019-05-31 12:30 | 70 | 59 |  |  | 43616.5208 | 85 | 85
2019-05-31 13:00 | 72 | 62 |  |  | 43616.5417 | 90 | 90
2019-05-31 13:30 | 76 | 66 |  |  | 43616.5625 | 93 | 93
2019-05-31 14:00 | 76 | 64 |  |  | 43616.5833 | 89 | 89
2019-05-31 14:30 | 78 | 66 |  |  | 43616.6042 | 92 | 92
2019-05-31 15:00 | 81 | 71 |  |  | 43616.625 | 97 | 97
2019-05-31 15:30 | 82 | 72 |  |  | 43616.6458 | 97 | 97
2019-05-31 16:00 | 86 | 76 |  |  | 43616.6667 | 101 | 101
2019-05-31 16:30 | 91 | 81 |  |  | 43616.6875 | 106 | 105
2019-05-31 17:00 | 96 | 85 |  |  | 43616.7083 | 111 | 110
2019-05-31 17:30 | 107 | 88 |  |  | 43616.7292 | 116 | 115
2019-05-31 18:00 | 111 | 91 |  |  | 43616.75 | 117 | 117
2019-05-31 18:30 | 109 | 88 |  |  | 43616.7708 | 114 | 113
2019-05-31 19:00 | 110 | 89 |  |  | 43616.7917 | 114 | 114
2019-05-31 19:30 | 109 | 88 |  |  | 43616.8125 | 112 | 112
2019-05-31 20:00 | 108 | 88 |  |  | 43616.8333 | 112 | 111
2019-05-31 20:30 | 108 | 89 |  |  | 43616.8542 | 113 | 112
2019-05-31 21:00 | 107 | 86 |  |  | 43616.875 | 109 | 108
2019-05-31 21:30 | 105 | 81 |  |  | 43616.8958 | 102 | 102
2019-05-31 22:00 | 99 | 79 |  |  | 43616.9167 | 100 | 100
2019-05-31 22:30 | 88 | 77 |  |  | 43616.9375 | 97 | 96
2019-05-31 23:00 | 85 | 73 |  |  | 43616.9583 | 92 | 91
2019-05-31 23:30 | 80 | 66 |  |  | 43616.9792 | 85 | 84
2019-06-01 | 74 | 58 |  |  | 43617 | 78 | 77
2019-06-01 00:30 | 69 | 51 |  |  | 43617.0208 | 71 | 70
2019-06-01 01:00 | 67 | 47 |  |  | 43617.0417 | 66 | 65
2019-06-01 01:30 | 64 | 43 |  |  | 43617.0625 | 62 | 61
2019-06-01 02:00 | 62 | 42 |  |  | 43617.0833 | 60 | 59
2019-06-01 02:30 | 60 | 40 |  |  | 43617.1042 | 58 | 57
2019-06-01 03:00 | 61 | 41 |  |  | 43617.125 | 58 | 57
2019-06-01 03:30 | 62 | 43 |  |  | 43617.1458 | 59 | 59
2019-06-01 04:00 | 63 | 44 |  |  | 43617.1667 | 60 | 60
2019-06-01 04:30 | 64 | 46 |  |  | 43617.1875 | 62 | 61
2019-06-01 05:00 | 66 | 48 |  |  | 43617.2083 | 66 | 66
2019-06-01 05:30 | 68 | 51 |  |  | 43617.2292 | 68 | 68
2019-06-01 06:00 | 69 | 54 |  |  | 43617.25 | 70 | 70
2019-06-01 06:30 | 70 | 56 |  |  | 43617.2708 | 75 | 75
2019-06-01 07:00 | 72 | 58 |  |  | 43617.2917 | 80 | 80
2019-06-01 07:30 | 74 | 61 |  |  | 43617.3125 | 84 | 83
2019-06-01 08:00 | 73 | 60 |  |  | 43617.3333 | 86 | 86
2019-06-01 08:30 | 56 | 42 |  |  | 43617.3542 | 76 | 76
2019-06-01 09:00 | 68 | 55 |  |  | 43617.375 | 81 | 81
2019-06-01 09:30 | 68 | 53 |  |  | 43617.3958 | 76 | 76
2019-06-01 10:00 | 65 | 49 |  |  | 43617.4167 | 72 | 71
2019-06-01 10:30 | 60 | 43 |  |  | 43617.4375 | 67 | 67
2019-06-01 11:00 | 58 | 40 |  |  | 43617.4583 | 64 | 64
2019-06-01 11:30 | 56 | 37 |  |  | 43617.4792 | 60 | 60
2019-06-01 12:00 | 56 | 35 |  |  | 43617.5 | 59 | 58
2019-06-01 12:30 | 56 | 35 |  |  | 43617.5208 | 58 | 58
2019-06-01 13:00 | 59 | 39 |  |  | 43617.5417 | 60 | 59
2019-06-01 13:30 | 61 | 42 |  |  | 43617.5625 | 64 | 64
2019-06-01 14:00 | 64 | 47 |  |  | 43617.5833 | 70 | 70
2019-06-01 14:30 | 64 | 47 |  |  | 43617.6042 | 73 | 72
2019-06-01 15:00 | 67 | 50 |  |  | 43617.625 | 73 | 72
2019-06-01 15:30 | 69 | 54 |  |  | 43617.6458 | 77 | 77
2019-06-01 16:00 | 71 | 57 |  |  | 43617.6667 | 81 | 80
2019-06-01 16:30 | 74 | 60 |  |  | 43617.6875 | 84 | 84
2019-06-01 17:00 | 77 | 65 |  |  | 43617.7083 | 90 | 90
2019-06-01 17:30 | 80 | 68 |  |  | 43617.7292 | 94 | 94
2019-06-01 18:00 | 80 | 67 |  |  | 43617.75 | 94 | 94
2019-06-01 18:30 | 79 | 66 |  |  | 43617.7708 | 92 | 92
2019-06-01 19:00 | 79 | 66 |  |  | 43617.7917 | 92 | 92
2019-06-01 19:30 | 79 | 66 |  |  | 43617.8125 | 92 | 92
2019-06-01 20:00 | 80 | 65 |  |  | 43617.8333 | 91 | 90
2019-06-01 20:30 | 79 | 65 |  |  | 43617.8542 | 90 | 90
2019-06-01 21:00 | 77 | 62 |  |  | 43617.875 | 87 | 86
2019-06-01 21:30 | 76 | 60 |  |  | 43617.8958 | 83 | 83
2019-06-01 22:00 | 76 | 60 |  |  | 43617.9167 | 84 | 83
2019-06-01 22:30 | 77 | 60 |  |  | 43617.9375 | 83 | 83
2019-06-01 23:00 | 74 | 58 |  |  | 43617.9583 | 80 | 79
2019-06-01 23:30 | 71 | 54 |  |  | 43617.9792 | 76 | 75
2019-06-02 | 68 | 50 |  |  | 43618 | 72 | 71
2019-06-02 00:30 | 64 | 44 |  |  | 43618.0208 | 66 | 65
2019-06-02 01:00 | 61 | 39 |  |  | 43618.0417 | 60 | 59
2019-06-02 01:30 | 59 | 36 |  |  | 43618.0625 | 57 | 56
2019-06-02 02:00 | 58 | 36 |  |  | 43618.0833 | 54 | 53
2019-06-02 02:30 | 58 | 34 |  |  | 43618.1042 | 53 | 52
2019-06-02 03:00 | 58 | 33 |  |  | 43618.125 | 53 | 52
2019-06-02 03:30 | 58 | 33 |  |  | 43618.1458 | 52 | 51
2019-06-02 04:00 | 57 | 32 |  |  | 43618.1667 | 50 | 50
2019-06-02 04:30 | 57 | 32 |  |  | 43618.1875 | 51 | 51
2019-06-02 05:00 | 58 | 33 |  |  | 43618.2083 | 53 | 52
2019-06-02 05:30 | 59 | 36 |  |  | 43618.2292 | 55 | 54
2019-06-02 06:00 | 60 | 39 |  |  | 43618.25 | 58 | 57
2019-06-02 06:30 | 61 | 40 |  |  | 43618.2708 | 61 | 60
2019-06-02 07:00 | 61 | 40 |  |  | 43618.2917 | 62 | 62
2019-06-02 07:30 | 61 | 40 |  |  | 43618.3125 | 64 | 63
2019-06-02 08:00 | 58 | 38 |  |  | 43618.3333 | 62 | 62
2019-06-02 08:30 | 58 | 38 |  |  | 43618.3542 | 64 | 63
2019-06-02 09:00 | 59 | 40 |  |  | 43618.375 | 70 | 70
2019-06-02 09:30 | 61 | 44 |  |  | 43618.3958 | 74 | 74
2019-06-02 10:00 | 64 | 49 |  |  | 43618.4167 | 74 | 74
2019-06-02 10:30 | 62 | 47 |  |  | 43618.4375 | 69 | 69
2019-06-02 11:00 | 58 | 39 |  |  | 43618.4583 | 62 | 62
2019-06-02 11:30 | 59 | 42 |  |  | 43618.4792 | 62 | 62
2019-06-02 12:00 | 58 | 41 |  |  | 43618.5 | 64 | 64
2019-06-02 12:30 | 59 | 42 |  |  | 43618.5208 | 64 | 64
2019-06-02 13:00 | 63 | 48 |  |  | 43618.5417 | 68 | 68
2019-06-02 13:30 | 69 | 56 |  |  | 43618.5625 | 77 | 77
2019-06-02 14:00 | 70 | 57 |  |  | 43618.5833 | 82 | 82
2019-06-02 14:30 | 65 | 51 |  |  | 43618.6042 | 76 | 76
2019-06-02 15:00 | 63 | 48 |  |  | 43618.625 | 69 | 69
2019-06-02 15:30 | 64 | 49 |  |  | 43618.6458 | 72 | 72
2019-06-02 16:00 | 66 | 52 |  |  | 43618.6667 | 75 | 75
2019-06-02 16:30 | 70 | 57 |  |  | 43618.6875 | 82 | 82
2019-06-02 17:00 | 75 | 62 |  |  | 43618.7083 | 87 | 87
2019-06-02 17:30 | 82 | 69 |  |  | 43618.7292 | 93 | 93
2019-06-02 18:00 | 84 | 72 |  |  | 43618.75 | 96 | 96
2019-06-02 18:30 | 84 | 72 |  |  | 43618.7708 | 97 | 97
2019-06-02 19:00 | 85 | 73 |  |  | 43618.7917 | 97 | 97
2019-06-02 19:30 | 84 | 71 |  |  | 43618.8125 | 96 | 95
2019-06-02 20:00 | 82 | 69 |  |  | 43618.8333 | 94 | 94
2019-06-02 20:30 | 82 | 69 |  |  | 43618.8542 | 93 | 93
2019-06-02 21:00 | 78 | 65 |  |  | 43618.875 | 89 | 88
2019-06-02 21:30 | 75 | 62 |  |  | 43618.8958 | 85 | 85
2019-06-02 22:00 | 75 | 61 |  |  | 43618.9167 | 85 | 84
2019-06-02 22:30 | 74 | 59 |  |  | 43618.9375 | 83 | 83
2019-06-02 23:00 | 72 | 56 |  |  | 43618.9583 | 79 | 78
2019-06-02 23:30 | 70 | 54 |  |  | 43618.9792 | 76 | 75
2019-06-03 | 67 | 48 |  |  | 43619 | 70 | 69
2019-06-03 00:30 | 66 | 47 |  |  | 43619.0208 | 67 | 66
2019-06-03 01:00 | 64 | 44 |  |  | 43619.0417 | 63 | 63
2019-06-03 01:30 | 63 | 42 |  |  | 43619.0625 | 61 | 61
2019-06-03 02:00 | 64 | 43 |  |  | 43619.0833 | 60 | 60
2019-06-03 02:30 | 63 | 42 |  |  | 43619.1042 | 60 | 59
2019-06-03 03:00 | 64 | 43 |  |  | 43619.125 | 59 | 59
2019-06-03 03:30 | 63 | 42 |  |  | 43619.1458 | 59 | 59
2019-06-03 04:00 | 63 | 43 |  |  | 43619.1667 | 59 | 59
2019-06-03 04:30 | 64 | 44 |  |  | 43619.1875 | 61 | 61
2019-06-03 05:00 | 65 | 46 |  |  | 43619.2083 | 64 | 64
2019-06-03 05:30 | 68 | 52 |  |  | 43619.2292 | 68 | 68
2019-06-03 06:00 | 71 | 58 |  |  | 43619.25 | 76 | 76
2019-06-03 06:30 | 76 | 66 |  |  | 43619.2708 | 89 | 89
2019-06-03 07:00 | 84 | 74 |  |  | 43619.2917 | 100 | 100
2019-06-03 07:30 | 93 | 79 |  |  | 43619.3125 | 111 | 109
2019-06-03 08:00 | 97 | 74 |  |  | 43619.3333 | 117 | 109
2019-06-03 08:30 | 93 | 70 |  |  | 43619.3542 | 113 | 105
2019-06-03 09:00 | 86 | 67 |  |  | 43619.375 | 105 | 101
2019-06-03 09:30 | 78 | 63 |  |  | 43619.3958 | 97 | 95
2019-06-03 10:00 | 76 | 60 |  |  | 43619.4167 | 94 | 93
2019-06-03 10:30 | 73 | 57 |  |  | 43619.4375 | 90 | 88
2019-06-03 11:00 | 73 | 57 |  |  | 43619.4583 | 85 | 84
2019-06-03 11:30 | 98 | 88 |  |  | 43619.4792 | 60 | 59
2019-06-03 12:00 | 70 | 57 |  |  | 43619.5 | 85 | 85
2019-06-03 12:30 | 60 | 46 |  |  | 43619.5208 | 98 | 98
2019-06-03 13:00 | 69 | 56 |  |  | 43619.5417 | 89 | 88
2019-06-03 13:30 | 72 | 60 |  |  | 43619.5625 | 90 | 90
2019-06-03 14:00 | 72 | 60 |  |  | 43619.5833 | 89 | 89
2019-06-03 14:30 | 74 | 63 |  |  | 43619.6042 | 91 | 91
2019-06-03 15:00 | 72 | 61 |  |  | 43619.625 | 89 | 89
2019-06-03 15:30 | 74 | 63 |  |  | 43619.6458 | 91 | 91
2019-06-03 16:00 | 80 | 69 |  |  | 43619.6667 | 96 | 96
2019-06-03 16:30 | 83 | 73 |  |  | 43619.6875 | 101 | 100
2019-06-03 17:00 | 89 | 79 |  |  | 43619.7083 | 107 | 106
2019-06-03 17:30 | 94 | 84 |  |  | 43619.7292 | 111 | 111
2019-06-03 18:00 | 96 | 86 |  |  | 43619.75 | 111 | 111
2019-06-03 18:30 | 97 | 86 |  |  | 43619.7708 | 110 | 109
2019-06-03 19:00 | 96 | 85 |  |  | 43619.7917 | 109 | 108
2019-06-03 19:30 | 89 | 78 |  |  | 43619.8125 | 103 | 102
2019-06-03 20:00 | 89 | 77 |  |  | 43619.8333 | 103 | 102
2019-06-03 20:30 | 89 | 77 |  |  | 43619.8542 | 103 | 102
2019-06-03 21:00 | 84 | 75 |  |  | 43619.875 | 99 | 99
2019-06-03 21:30 | 81 | 72 |  |  | 43619.8958 | 93 | 93
2019-06-03 22:00 | 80 | 69 |  |  | 43619.9167 | 92 | 91
2019-06-03 22:30 | 79 | 67 |  |  | 43619.9375 | 89 | 89
2019-06-03 23:00 | 77 | 65 |  |  | 43619.9583 | 85 | 84
2019-06-03 23:30 | 75 | 60 |  |  | 43619.9792 | 80 | 79
2019-06-04 | 70 | 54 |  |  | 43620 | 74 | 73
2019-06-04 00:30 | 69 | 51 |  |  | 43620.0208 | 70 | 69
2019-06-04 01:00 | 68 | 49 |  |  | 43620.0417 | 66 | 65
2019-06-04 01:30 | 66 | 47 |  |  | 43620.0625 | 64 | 64
2019-06-04 02:00 | 65 | 46 |  |  | 43620.0833 | 62 | 61
2019-06-04 02:30 | 64 | 45 |  |  | 43620.1042 | 59 | 59
2019-06-04 03:00 | 64 | 44 |  |  | 43620.125 | 59 | 59
2019-06-04 03:30 | 64 | 44 |  |  | 43620.1458 | 59 | 59
2019-06-04 04:00 | 65 | 46 |  |  | 43620.1667 | 61 | 61
2019-06-04 04:30 | 66 | 48 |  |  | 43620.1875 | 63 | 62
2019-06-04 05:00 | 68 | 51 |  |  | 43620.2083 | 67 | 66
2019-06-04 05:30 | 71 | 57 |  |  | 43620.2292 | 73 | 73
2019-06-04 06:00 | 76 | 66 |  |  | 43620.25 | 83 | 83
2019-06-04 06:30 | 85 | 77 |  |  | 43620.2708 | 99 | 99
2019-06-04 07:00 | 93 | 86 |  |  | 43620.2917 | 114 | 114
2019-06-04 07:30 | 91 | 90 |  |  | 43620.3125 | 123 | 123
2019-06-04 08:00 | 89 | 88 |  |  | 43620.3333 | 122 | 122
2019-06-04 08:30 | 80 | 79 |  |  | 43620.3542 | 114 | 114
2019-06-04 09:00 | 73 | 73 |  |  | 43620.375 | 108 | 108
2019-06-04 09:30 | 68 | 68 |  |  | 43620.3958 | 101 | 101
2019-06-04 10:00 | 64 | 64 |  |  | 43620.4167 | 96 | 96
2019-06-04 10:30 | 61 | 60 |  |  | 43620.4375 | 92 | 92
2019-06-04 11:00 | 58 | 57 |  |  | 43620.4583 | 89 | 89
2019-06-04 11:30 | 55 | 54 |  |  | 43620.4792 | 85 | 85
2019-06-04 12:00 | 53 | 52 |  |  | 43620.5 | 83 | 83
2019-06-04 12:30 | 52 | 51 |  |  | 43620.5208 | 83 | 83
2019-06-04 13:00 | 52 | 51 |  |  | 43620.5417 | 83 | 83
2019-06-04 13:30 | 54 | 53 |  |  | 43620.5625 | 84 | 84
2019-06-04 14:00 | 56 | 55 |  |  | 43620.5833 | 85 | 85
2019-06-04 14:30 | 60 | 59 |  |  | 43620.6042 | 87 | 87
2019-06-04 15:00 | 63 | 62 |  |  | 43620.625 | 91 | 91
2019-06-04 15:30 | 65 | 65 |  |  | 43620.6458 | 94 | 94
2019-06-04 16:00 | 74 | 74 |  |  | 43620.6667 | 104 | 104
2019-06-04 16:30 | 84 | 83 |  |  | 43620.6875 | 113 | 113
2019-06-04 17:00 | 89 | 88 |  |  | 43620.7083 | 118 | 118
2019-06-04 17:30 | 96 | 95 |  |  | 43620.7292 | 125 | 125
2019-06-04 18:00 | 100 | 97 |  |  | 43620.75 | 132 | 129
2019-06-04 18:30 | 100 | 97 |  |  | 43620.7708 | 130 | 128
2019-06-04 19:00 | 104 | 101 |  |  | 43620.7917 | 134 | 131
2019-06-04 19:30 | 104 | 101 |  |  | 43620.8125 | 131 | 128
2019-06-04 20:00 | 101 | 98 |  |  | 43620.8333 | 128 | 125
2019-06-04 20:30 | 99 | 96 |  |  | 43620.8542 | 126 | 123
2019-06-04 21:00 | 94 | 92 |  |  | 43620.875 | 121 | 119
2019-06-04 21:30 | 89 | 87 |  |  | 43620.8958 | 114 | 111
2019-06-04 22:00 | 85 | 82 |  |  | 43620.9167 | 109 | 106
2019-06-04 22:30 | 80 | 76 |  |  | 43620.9375 | 105 | 100
2019-06-04 23:00 | 75 | 71 |  |  | 43620.9583 | 99 | 92
2019-06-04 23:30 | 66 | 64 |  |  | 43620.9792 | 96 | 85
2019-06-05 | 58 | 57 |  |  | 43621 | 84 | 77
2019-06-05 00:30 | 54 | 52 |  |  | 43621.0208 | 79 | 71
2019-06-05 01:00 | 51 | 49 |  |  | 43621.0417 | 75 | 66
2019-06-05 01:30 | 49 | 46 |  |  | 43621.0625 | 72 | 62
2019-06-05 02:00 | 48 | 45 |  |  | 43621.0833 | 72 | 60
2019-06-05 02:30 | 47 | 44 |  |  | 43621.1042 | 71 | 59
2019-06-05 03:00 | 46 | 43 |  |  | 43621.125 | 70 | 58
2019-06-05 03:30 | 47 | 44 |  |  | 43621.1458 | 70 | 58
2019-06-05 04:00 | 48 | 45 |  |  | 43621.1667 | 70 | 58
2019-06-05 04:30 | 49 | 46 |  |  | 43621.1875 | 71 | 59
2019-06-05 05:00 | 52 | 50 |  |  | 43621.2083 | 75 | 64
2019-06-05 05:30 | 60 | 59 |  |  | 43621.2292 | 83 | 73
2019-06-05 06:00 | 69 | 67 |  |  | 43621.25 | 93 | 84
2019-06-05 06:30 | 79 | 78 |  |  | 43621.2708 | 107 | 100
2019-06-05 07:00 | 89 | 86 |  |  | 43621.2917 | 116 | 113
2019-06-05 07:30 | 93 | 91 |  |  | 43621.3125 | 124 | 122
2019-06-05 08:00 | 90 | 88 |  |  | 43621.3333 | 122 | 120
2019-06-05 08:30 | 84 | 82 |  |  | 43621.3542 | 115 | 114
2019-06-05 09:00 | 77 | 74 |  |  | 43621.375 | 108 | 106
2019-06-05 09:30 | 69 | 67 |  |  | 43621.3958 | 100 | 99
2019-06-05 10:00 | 65 | 63 |  |  | 43621.4167 | 95 | 93
2019-06-05 10:30 | 60 | 58 |  |  | 43621.4375 | 90 | 88
2019-06-05 11:00 | 59 | 56 |  |  | 43621.4583 | 87 | 86
2019-06-05 11:30 | 57 | 55 |  |  | 43621.4792 | 85 | 84
2019-06-05 12:00 | 57 | 54 |  |  | 43621.5 | 84 | 82
2019-06-05 12:30 | 57 | 54 |  |  | 43621.5208 | 84 | 83
2019-06-05 13:00 | 58 | 55 |  |  | 43621.5417 | 85 | 83
2019-06-05 13:30 | 64 | 62 |  |  | 43621.5625 | 91 | 89
2019-06-05 14:00 | 70 | 67 |  |  | 43621.5833 | 94 | 92
2019-06-05 14:30 | 73 | 71 |  |  | 43621.6042 | 99 | 97
2019-06-05 15:00 | 71 | 68 |  |  | 43621.625 | 96 | 94
2019-06-05 15:30 | 70 | 67 |  |  | 43621.6458 | 96 | 94
2019-06-05 16:00 | 72 | 69 |  |  | 43621.6667 | 101 | 98
2019-06-05 16:30 | 75 | 72 |  |  | 43621.6875 | 104 | 100
2019-06-05 17:00 | 81 | 77 |  |  | 43621.7083 | 109 | 105
2019-06-05 17:30 | 85 | 83 |  |  | 43621.7292 | 114 | 112
2019-06-05 18:00 | 87 | 85 |  |  | 43621.75 | 116 | 114
2019-06-05 18:30 | 86 | 83 |  |  | 43621.7708 | 114 | 110
2019-06-05 19:00 | 88 | 85 |  |  | 43621.7917 | 115 | 112
2019-06-05 19:30 | 85 | 82 |  |  | 43621.8125 | 112 | 109
2019-06-05 20:00 | 85 | 82 |  |  | 43621.8333 | 111 | 108
2019-06-05 20:30 | 84 | 82 |  |  | 43621.8542 | 110 | 107
2019-06-05 21:00 | 79 | 76 |  |  | 43621.875 | 105 | 101
2019-06-05 21:30 | 76 | 73 |  |  | 43621.8958 | 101 | 96
2019-06-05 22:00 | 72 | 68 |  |  | 43621.9167 | 99 | 95
2019-06-05 22:30 | 70 | 66 |  |  | 43621.9375 | 96 | 92
2019-06-05 23:00 | 69 | 64 |  |  | 43621.9583 | 93 | 88
2019-06-05 23:30 | 64 | 59 |  |  | 43621.9792 | 86 | 82
2019-06-06 | 55 | 52 |  |  | 43622 | 76 | 74
2019-06-06 00:30 | 49 | 46 |  |  | 43622.0208 | 67 | 67
2019-06-06 01:00 | 46 | 42 |  |  | 43622.0417 | 63 | 61
2019-06-06 01:30 | 45 | 41 |  |  | 43622.0625 | 60 | 59
2019-06-06 02:00 | 43 | 38 |  |  | 43622.0833 | 57 | 56
2019-06-06 02:30 | 43 | 38 |  |  | 43622.1042 | 57 | 55
2019-06-06 03:00 | 44 | 39 |  |  | 43622.125 | 57 | 55
2019-06-06 03:30 | 43 | 38 |  |  | 43622.1458 | 57 | 55
2019-06-06 04:00 | 45 | 40 |  |  | 43622.1667 | 57 | 55
2019-06-06 04:30 | 47 | 42 |  |  | 43622.1875 | 59 | 57
2019-06-06 05:00 | 49 | 45 |  |  | 43622.2083 | 62 | 60
2019-06-06 05:30 | 52 | 49 |  |  | 43622.2292 | 67 | 66
2019-06-06 06:00 | 60 | 58 |  |  | 43622.25 | 76 | 76
2019-06-06 06:30 | 72 | 71 |  |  | 43622.2708 | 94 | 93
2019-06-06 07:00 | 79 | 79 |  |  | 43622.2917 | 107 | 107
2019-06-06 07:30 | 86 | 86 |  |  | 43622.3125 | 119 | 119
2019-06-06 08:00 | 85 | 83 |  |  | 43622.3333 | 119 | 118
2019-06-06 08:30 | 80 | 78 |  |  | 43622.3542 | 114 | 112
2019-06-06 09:00 | 76 | 74 |  |  | 43622.375 | 108 | 107
2019-06-06 09:30 | 70 | 68 |  |  | 43622.3958 | 101 | 100
2019-06-06 10:00 | 72 | 64 |  |  | 43622.4167 | 97 | 95
2019-06-06 10:30 | 70 | 63 |  |  | 43622.4375 | 95 | 93
2019-06-06 11:00 | 69 | 65 |  |  | 43622.4583 | 97 | 97
2019-06-06 11:30 | 65 | 61 |  |  | 43622.4792 | 91 | 90
2019-06-06 12:00 | 61 | 57 |  |  | 43622.5 | 87 | 86
2019-06-06 12:30 | 62 | 57 |  |  | 43622.5208 | 86 | 85
2019-06-06 13:00 | 65 | 61 |  |  | 43622.5417 | 86 | 85
2019-06-06 13:30 | 67 | 63 |  |  | 43622.5625 | 91 | 90
2019-06-06 14:00 | 68 | 65 |  |  | 43622.5833 | 94 | 93
2019-06-06 14:30 | 70 | 67 |  |  | 43622.6042 | 97 | 96
2019-06-06 15:00 | 73 | 69 |  |  | 43622.625 | 96 | 95
2019-06-06 15:30 | 75 | 70 |  |  | 43622.6458 | 98 | 97
2019-06-06 16:00 | 77 | 73 |  |  | 43622.6667 | 100 | 98
2019-06-06 16:30 | 78 | 74 |  |  | 43622.6875 | 102 | 101
2019-06-06 17:00 | 85 | 80 |  |  | 43622.7083 | 109 | 106
2019-06-06 17:30 | 91 | 84 |  |  | 43622.7292 | 118 | 111
2019-06-06 18:00 | 92 | 86 |  |  | 43622.75 | 119 | 113
2019-06-06 18:30 | 91 | 84 |  |  | 43622.7708 | 116 | 110
2019-06-06 19:00 | 91 | 85 |  |  | 43622.7917 | 118 | 111
2019-06-06 19:30 | 92 | 85 |  |  | 43622.8125 | 116 | 108
2019-06-06 20:00 | 90 | 82 |  |  | 43622.8333 | 114 | 107
2019-06-06 20:30 | 90 | 83 |  |  | 43622.8542 | 115 | 108
2019-06-06 21:00 | 88 | 81 |  |  | 43622.875 | 111 | 105
2019-06-06 21:30 | 81 | 73 |  |  | 43622.8958 | 103 | 96
2019-06-06 22:00 | 78 | 69 |  |  | 43622.9167 | 100 | 93
2019-06-06 22:30 | 76 | 67 |  |  | 43622.9375 | 97 | 91
2019-06-06 23:00 | 74 | 64 |  |  | 43622.9583 | 92 | 85
2019-06-06 23:30 | 69 | 58 |  |  | 43622.9792 | 86 | 79
2019-06-07 | 62 | 50 |  |  | 43623 | 78 | 72
2019-06-07 00:30 | 58 | 46 |  |  | 43623.0208 | 71 | 64
2019-06-07 01:00 | 54 | 44 |  |  | 43623.0417 | 65 | 61
2019-06-07 01:30 | 52 | 40 |  |  | 43623.0625 | 61 | 58
2019-06-07 02:00 | 51 | 40 |  |  | 43623.0833 | 61 | 57
2019-06-07 02:30 | 52 | 41 |  |  | 43623.1042 | 61 | 57
2019-06-07 03:00 | 54 | 41 |  |  | 43623.125 | 61 | 57
2019-06-07 03:30 | 53 | 41 |  |  | 43623.1458 | 61 | 57
2019-06-07 04:00 | 54 | 42 |  |  | 43623.1667 | 61 | 57
2019-06-07 04:30 | 55 | 44 |  |  | 43623.1875 | 62 | 58
2019-06-07 05:00 | 58 | 47 |  |  | 43623.2083 | 65 | 62
2019-06-07 05:30 | 62 | 54 |  |  | 43623.2292 | 71 | 68
2019-06-07 06:00 | 66 | 60 |  |  | 43623.25 | 79 | 77
2019-06-07 06:30 | 73 | 70 |  |  | 43623.2708 | 92 | 91
2019-06-07 07:00 | 81 | 76 |  |  | 43623.2917 | 106 | 104
2019-06-07 07:30 | 88 | 83 |  |  | 43623.3125 | 116 | 114
2019-06-07 08:00 | 85 | 81 |  |  | 43623.3333 | 115 | 113
2019-06-07 08:30 | 83 | 79 |  |  | 43623.3542 | 113 | 111
2019-06-07 09:00 | 77 | 70 |  |  | 43623.375 | 106 | 103
2019-06-07 09:30 | 70 | 61 |  |  | 43623.3958 | 97 | 93
2019-06-07 10:00 | 69 | 60 |  |  | 43623.4167 | 94 | 90
2019-06-07 10:30 | 67 | 57 |  |  | 43623.4375 | 91 | 87
2019-06-07 11:00 | 67 | 58 |  |  | 43623.4583 | 91 | 87
2019-06-07 11:30 | 70 | 61 |  |  | 43623.4792 | 94 | 90
2019-06-07 12:00 | 70 | 62 |  |  | 43623.5 | 94 | 90
2019-06-07 12:30 | 73 | 64 |  |  | 43623.5208 | 95 | 91
2019-06-07 13:00 | 76 | 68 |  |  | 43623.5417 | 99 | 95
2019-06-07 13:30 | 78 | 70 |  |  | 43623.5625 | 101 | 97
2019-06-07 14:00 | 75 | 67 |  |  | 43623.5833 | 99 | 95
2019-06-07 14:30 | 78 | 70 |  |  | 43623.6042 | 101 | 97
2019-06-07 15:00 | 77 | 69 |  |  | 43623.625 | 99 | 95
2019-06-07 15:30 | 77 | 68 |  |  | 43623.6458 | 101 | 96
2019-06-07 16:00 | 78 | 70 |  |  | 43623.6667 | 101 | 96
2019-06-07 16:30 | 80 | 72 |  |  | 43623.6875 | 104 | 100
2019-06-07 17:00 | 84 | 76 |  |  | 43623.7083 | 108 | 104
2019-06-07 17:30 | 88 | 81 |  |  | 43623.7292 | 112 | 108
2019-06-07 18:00 | 87 | 80 |  |  | 43623.75 | 111 | 107
2019-06-07 18:30 | 85 | 77 |  |  | 43623.7708 | 108 | 103
2019-06-07 19:00 | 87 | 79 |  |  | 43623.7917 | 110 | 105
2019-06-07 19:30 | 86 | 78 |  |  | 43623.8125 | 109 | 103
2019-06-07 20:00 | 84 | 76 |  |  | 43623.8333 | 106 | 100
2019-06-07 20:30 | 82 | 73 |  |  | 43623.8542 | 104 | 98
2019-06-07 21:00 | 78 | 69 |  |  | 43623.875 | 100 | 94
2019-06-07 21:30 | 75 | 65 |  |  | 43623.8958 | 96 | 90
2019-06-07 22:00 | 74 | 64 |  |  | 43623.9167 | 95 | 89
2019-06-07 22:30 | 71 | 62 |  |  | 43623.9375 | 91 | 87
2019-06-07 23:00 | 68 | 60 |  |  | 43623.9583 | 86 | 83
2019-06-07 23:30 | 64 | 55 |  |  | 43623.9792 | 81 | 77
2019-06-08 | 60 | 49 |  |  | 43624 | 75 | 71
2019-06-08 00:30 | 57 | 44 |  |  | 43624.0208 | 69 | 64
2019-06-08 01:00 | 55 | 41 |  |  | 43624.0417 | 66 | 59
2019-06-08 01:30 | 56 | 40 |  |  | 43624.0625 | 64 | 57
2019-06-08 02:00 | 58 | 39 |  |  | 43624.0833 | 63 | 55
2019-06-08 02:30 | 58 | 39 |  |  | 43624.1042 | 64 | 55
2019-06-08 03:00 | 59 | 41 |  |  | 43624.125 | 63 | 55
2019-06-08 03:30 | 59 | 41 |  |  | 43624.1458 | 63 | 57
2019-06-08 04:00 | 59 | 41 |  |  | 43624.1667 | 64 | 57
2019-06-08 04:30 | 60 | 43 |  |  | 43624.1875 | 64 | 58
2019-06-08 05:00 | 61 | 45 |  |  | 43624.2083 | 66 | 60
2019-06-08 05:30 | 62 | 46 |  |  | 43624.2292 | 66 | 60
2019-06-08 06:00 | 62 | 47 |  |  | 43624.25 | 69 | 63
2019-06-08 06:30 | 61 | 47 |  |  | 43624.2708 | 71 | 66
2019-06-08 07:00 | 62 | 49 |  |  | 43624.2917 | 74 | 70
2019-06-08 07:30 | 62 | 51 |  |  | 43624.3125 | 76 | 73
2019-06-08 08:00 | 62 | 53 |  |  | 43624.3333 | 79 | 77
2019-06-08 08:30 | 66 | 58 |  |  | 43624.3542 | 85 | 83
2019-06-08 09:00 | 68 | 60 |  |  | 43624.375 | 87 | 86
2019-06-08 09:30 | 67 | 61 |  |  | 43624.3958 | 88 | 86
2019-06-08 10:00 | 68 | 62 |  |  | 43624.4167 | 90 | 89
2019-06-08 10:30 | 71 | 65 |  |  | 43624.4375 | 93 | 92
2019-06-08 11:00 | 70 | 63 |  |  | 43624.4583 | 91 | 89
2019-06-08 11:30 | 71 | 63 |  |  | 43624.4792 | 91 | 88
2019-06-08 12:00 | 70 | 62 |  |  | 43624.5 | 90 | 88
2019-06-08 12:30 | 70 | 62 |  |  | 43624.5208 | 88 | 86
2019-06-08 13:00 | 69 | 60 |  |  | 43624.5417 | 87 | 85
2019-06-08 13:30 | 73 | 65 |  |  | 43624.5625 | 91 | 89
2019-06-08 14:00 | 73 | 65 |  |  | 43624.5833 | 90 | 87
2019-06-08 14:30 | 74 | 65 |  |  | 43624.6042 | 91 | 88
2019-06-08 15:00 | 75 | 67 |  |  | 43624.625 | 92 | 90
2019-06-08 15:30 | 75 | 67 |  |  | 43624.6458 | 94 | 91
2019-06-08 16:00 | 73 | 65 |  |  | 43624.6667 | 92 | 90
2019-06-08 16:30 | 74 | 66 |  |  | 43624.6875 | 94 | 91
2019-06-08 17:00 | 78 | 72 |  |  | 43624.7083 | 99 | 97
2019-06-08 17:30 | 81 | 75 |  |  | 43624.7292 | 104 | 101
2019-06-08 18:00 | 80 | 74 |  |  | 43624.75 | 103 | 100
2019-06-08 18:30 | 78 | 71 |  |  | 43624.7708 | 101 | 98
2019-06-08 19:00 | 79 | 72 |  |  | 43624.7917 | 102 | 99
2019-06-08 19:30 | 77 | 71 |  |  | 43624.8125 | 99 | 97
2019-06-08 20:00 | 77 | 71 |  |  | 43624.8333 | 99 | 96
2019-06-08 20:30 | 76 | 70 |  |  | 43624.8542 | 98 | 96
2019-06-08 21:00 | 73 | 66 |  |  | 43624.875 | 94 | 91
2019-06-08 21:30 | 71 | 63 |  |  | 43624.8958 | 90 | 87
2019-06-08 22:00 | 69 | 61 |  |  | 43624.9167 | 89 | 86
2019-06-08 22:30 | 67 | 59 |  |  | 43624.9375 | 87 | 84
2019-06-08 23:00 | 67 | 58 |  |  | 43624.9583 | 84 | 80
2019-06-08 23:30 | 63 | 53 |  |  | 43624.9792 | 80 | 76
2019-06-09 | 61 | 49 |  |  | 43625 | 76 | 71
2019-06-09 00:30 | 59 | 46 |  |  | 43625.0208 | 72 | 66
2019-06-09 01:00 | 58 | 44 |  |  | 43625.0417 | 69 | 62
2019-06-09 01:30 | 57 | 43 |  |  | 43625.0625 | 67 | 61
2019-06-09 02:00 | 55 | 41 |  |  | 43625.0833 | 63 | 58
2019-06-09 02:30 | 56 | 41 |  |  | 43625.1042 | 63 | 57
2019-06-09 03:00 | 55 | 41 |  |  | 43625.125 | 61 | 56
2019-06-09 03:30 | 56 | 42 |  |  | 43625.1458 | 63 | 57
2019-06-09 04:00 | 55 | 42 |  |  | 43625.1667 | 63 | 57
2019-06-09 04:30 | 57 | 44 |  |  | 43625.1875 | 64 | 59
2019-06-09 05:00 | 58 | 45 |  |  | 43625.2083 | 65 | 59
2019-06-09 05:30 | 59 | 47 |  |  | 43625.2292 | 65 | 60
2019-06-09 06:00 | 59 | 47 |  |  | 43625.25 | 67 | 62
2019-06-09 06:30 | 60 | 48 |  |  | 43625.2708 | 69 | 65
2019-06-09 07:00 | 61 | 49 |  |  | 43625.2917 | 71 | 67
2019-06-09 07:30 | 60 | 48 |  |  | 43625.3125 | 72 | 68
2019-06-09 08:00 | 60 | 49 |  |  | 43625.3333 | 71 | 67
2019-06-09 08:30 | 58 | 49 |  |  | 43625.3542 | 71 | 68
2019-06-09 09:00 | 59 | 51 |  |  | 43625.375 | 73 | 71
2019-06-09 09:30 | 58 | 50 |  |  | 43625.3958 | 73 | 71
2019-06-09 10:00 | 54 | 45 |  |  | 43625.4167 | 69 | 67
2019-06-09 10:30 | 52 | 42 |  |  | 43625.4375 | 66 | 64
2019-06-09 11:00 | 52 | 42 |  |  | 43625.4583 | 64 | 62
2019-06-09 11:30 | 52 | 41 |  |  | 43625.4792 | 63 | 61
2019-06-09 12:00 | 53 | 43 |  |  | 43625.5 | 64 | 62
2019-06-09 12:30 | 52 | 42 |  |  | 43625.5208 | 64 | 61
2019-06-09 13:00 | 52 | 42 |  |  | 43625.5417 | 64 | 61
2019-06-09 13:30 | 55 | 45 |  |  | 43625.5625 | 67 | 64
2019-06-09 14:00 | 57 | 49 |  |  | 43625.5833 | 68 | 66
2019-06-09 14:30 | 59 | 50 |  |  | 43625.6042 | 70 | 68
2019-06-09 15:00 | 60 | 52 |  |  | 43625.625 | 71 | 69
2019-06-09 15:30 | 62 | 54 |  |  | 43625.6458 | 74 | 72
2019-06-09 16:00 | 63 | 56 |  |  | 43625.6667 | 78 | 77
2019-06-09 16:30 | 67 | 60 |  |  | 43625.6875 | 84 | 81
2019-06-09 17:00 | 71 | 65 |  |  | 43625.7083 | 90 | 88
2019-06-09 17:30 | 78 | 72 |  |  | 43625.7292 | 97 | 94
2019-06-09 18:00 | 82 | 76 |  |  | 43625.75 | 101 | 99
2019-06-09 18:30 | 82 | 76 |  |  | 43625.7708 | 100 | 98
2019-06-09 19:00 | 81 | 74 |  |  | 43625.7917 | 100 | 98
2019-06-09 19:30 | 79 | 73 |  |  | 43625.8125 | 98 | 95
2019-06-09 20:00 | 79 | 71 |  |  | 43625.8333 | 97 | 94
2019-06-09 20:30 | 78 | 71 |  |  | 43625.8542 | 96 | 93
2019-06-09 21:00 | 74 | 67 |  |  | 43625.875 | 93 | 89
2019-06-09 21:30 | 72 | 63 |  |  | 43625.8958 | 88 | 84
2019-06-09 22:00 | 71 | 62 |  |  | 43625.9167 | 88 | 84
2019-06-09 22:30 | 69 | 61 |  |  | 43625.9375 | 87 | 84
2019-06-09 23:00 | 67 | 58 |  |  | 43625.9583 | 84 | 80
2019-06-09 23:30 | 65 | 56 |  |  | 43625.9792 | 80 | 76
2019-06-10 | 61 | 51 |  |  | 43626 | 76 | 71
2019-06-10 00:30 | 62 | 50 |  |  | 43626.0208 | 73 | 68
2019-06-10 01:00 | 61 | 50 |  |  | 43626.0417 | 70 | 66
2019-06-10 01:30 | 58 | 46 |  |  | 43626.0625 | 66 | 62
2019-06-10 02:00 | 57 | 44 |  |  | 43626.0833 | 64 | 60
2019-06-10 02:30 | 57 | 45 |  |  | 43626.1042 | 64 | 60
2019-06-10 03:00 | 58 | 45 |  |  | 43626.125 | 65 | 60
2019-06-10 03:30 | 58 | 46 |  |  | 43626.1458 | 64 | 60
2019-06-10 04:00 | 56 | 46 |  |  | 43626.1667 | 63 | 60
2019-06-10 04:30 | 57 | 46 |  |  | 43626.1875 | 64 | 61
2019-06-10 05:00 | 57 | 48 |  |  | 43626.2083 | 66 | 63
2019-06-10 05:30 | 60 | 53 |  |  | 43626.2292 | 71 | 70
2019-06-10 06:00 | 66 | 61 |  |  | 43626.25 | 80 | 79
2019-06-10 06:30 | 74 | 70 |  |  | 43626.2708 | 93 | 92
2019-06-10 07:00 | 79 | 78 |  |  | 43626.2917 | 104 | 104
2019-06-10 07:30 | 87 | 86 |  |  | 43626.3125 | 115 | 115
2019-06-10 08:00 | 87 | 86 |  |  | 43626.3333 | 115 | 115
2019-06-10 08:30 | 83 | 83 |  |  | 43626.3542 | 112 | 112
2019-06-10 09:00 | 79 | 78 |  |  | 43626.375 | 107 | 107
2019-06-10 09:30 | 75 | 74 |  |  | 43626.3958 | 103 | 103
2019-06-10 10:00 | 71 | 70 |  |  | 43626.4167 | 99 | 99
2019-06-10 10:30 | 68 | 67 |  |  | 43626.4375 | 95 | 95
2019-06-10 11:00 | 65 | 64 |  |  | 43626.4583 | 93 | 93
2019-06-10 11:30 | 66 | 65 |  |  | 43626.4792 | 93 | 93
2019-06-10 12:00 | 67 | 65 |  |  | 43626.5 | 94 | 94
2019-06-10 12:30 | 68 | 64 |  |  | 43626.5208 | 93 | 92
2019-06-10 13:00 | 69 | 65 |  |  | 43626.5417 | 93 | 93
2019-06-10 13:30 | 70 | 66 |  |  | 43626.5625 | 96 | 95
2019-06-10 14:00 | 71 | 67 |  |  | 43626.5833 | 97 | 97
2019-06-10 14:30 | 73 | 70 |  |  | 43626.6042 | 100 | 99
2019-06-10 15:00 | 74 | 71 |  |  | 43626.625 | 101 | 100
2019-06-10 15:30 | 74 | 70 |  |  | 43626.6458 | 100 | 100
2019-06-10 16:00 | 81 | 80 |  |  | 43626.6667 | 109 | 108
2019-06-10 16:30 | 86 | 85 |  |  | 43626.6875 | 113 | 112
2019-06-10 17:00 | 88 | 87 |  |  | 43626.7083 | 115 | 115
2019-06-10 17:30 | 92 | 90 |  |  | 43626.7292 | 117 | 117
2019-06-10 18:00 | 94 | 93 |  |  | 43626.75 | 119 | 118
2019-06-10 18:30 | 90 | 89 |  |  | 43626.7708 | 114 | 114
2019-06-10 19:00 | 90 | 89 |  |  | 43626.7917 | 113 | 112
2019-06-10 19:30 | 86 | 85 |  |  | 43626.8125 | 109 | 108
2019-06-10 20:00 | 85 | 83 |  |  | 43626.8333 | 108 | 107
2019-06-10 20:30 | 83 | 81 |  |  | 43626.8542 | 106 | 105
2019-06-10 21:00 | 79 | 77 |  |  | 43626.875 | 100 | 100
2019-06-10 21:30 | 76 | 72 |  |  | 43626.8958 | 95 | 93
2019-06-10 22:00 | 73 | 69 |  |  | 43626.9167 | 92 | 91
2019-06-10 22:30 | 69 | 64 |  |  | 43626.9375 | 88 | 87
2019-06-10 23:00 | 66 | 61 |  |  | 43626.9583 | 83 | 81
2019-06-10 23:30 | 63 | 57 |  |  | 43626.9792 | 79 | 77
2019-06-11 | 60 | 52 |  |  | 43627 | 74 | 72
2019-06-11 00:30 | 58 | 49 |  |  | 43627.0208 | 70 | 67
2019-06-11 01:00 | 56 | 46 |  |  | 43627.0417 | 66 | 62
2019-06-11 01:30 | 54 | 43 |  |  | 43627.0625 | 63 | 59
2019-06-11 02:00 | 53 | 42 |  |  | 43627.0833 | 62 | 57
2019-06-11 02:30 | 53 | 41 |  |  | 43627.1042 | 61 | 56
2019-06-11 03:00 | 55 | 42 |  |  | 43627.125 | 62 | 58
2019-06-11 03:30 | 56 | 44 |  |  | 43627.1458 | 63 | 59
2019-06-11 04:00 | 57 | 45 |  |  | 43627.1667 | 64 | 60
2019-06-11 04:30 | 59 | 47 |  |  | 43627.1875 | 66 | 61
2019-06-11 05:00 | 60 | 50 |  |  | 43627.2083 | 68 | 64
2019-06-11 05:30 | 62 | 54 |  |  | 43627.2292 | 73 | 70
2019-06-11 06:00 | 64 | 58 |  |  | 43627.25 | 78 | 77
2019-06-11 06:30 | 69 | 67 |  |  | 43627.2708 | 91 | 91
2019-06-11 07:00 | 73 | 72 |  |  | 43627.2917 | 101 | 101
2019-06-11 07:30 | 82 | 81 |  |  | 43627.3125 | 112 | 112
2019-06-11 08:00 | 81 | 81 |  |  | 43627.3333 | 112 | 112
2019-06-11 08:30 | 76 | 76 |  |  | 43627.3542 | 108 | 108
2019-06-11 09:00 | 72 | 72 |  |  | 43627.375 | 104 | 104
2019-06-11 09:30 | 68 | 68 |  |  | 43627.3958 | 99 | 99
2019-06-11 10:00 | 63 | 62 |  |  | 43627.4167 | 94 | 93
2019-06-11 10:30 | 59 | 59 |  |  | 43627.4375 | 90 | 90
2019-06-11 11:00 | 57 | 57 |  |  | 43627.4583 | 89 | 89
2019-06-11 11:30 | 53 | 53 |  |  | 43627.4792 | 80 | 79
2019-06-11 12:00 | 49 | 49 |  |  | 43627.5 | 72 | 72
2019-06-11 12:30 | 50 | 50 |  |  | 43627.5208 | 73 | 72
2019-06-11 13:00 | 51 | 50 |  |  | 43627.5417 | 74 | 73
2019-06-11 13:30 | 53 | 53 |  |  | 43627.5625 | 76 | 76
2019-06-11 14:00 | 60 | 60 |  |  | 43627.5833 | 86 | 85
2019-06-11 14:30 | 68 | 68 |  |  | 43627.6042 | 98 | 97
2019-06-11 15:00 | 70 | 70 |  |  | 43627.625 | 100 | 99
2019-06-11 15:30 | 73 | 73 |  |  | 43627.6458 | 102 | 102
2019-06-11 16:00 | 77 | 76 |  |  | 43627.6667 | 106 | 106
2019-06-11 16:30 | 82 | 81 |  |  | 43627.6875 | 109 | 109
2019-06-11 17:00 | 85 | 84 |  |  | 43627.7083 | 112 | 112
2019-06-11 17:30 | 89 | 88 |  |  | 43627.7292 | 116 | 116
2019-06-11 18:00 | 90 | 90 |  |  | 43627.75 | 116 | 116
2019-06-11 18:30 | 87 | 86 |  |  | 43627.7708 | 112 | 112
2019-06-11 19:00 | 88 | 87 |  |  | 43627.7917 | 112 | 112
2019-06-11 19:30 | 86 | 86 |  |  | 43627.8125 | 109 | 109
2019-06-11 20:00 | 86 | 83 |  |  | 43627.8333 | 107 | 106
2019-06-11 20:30 | 84 | 81 |  |  | 43627.8542 | 105 | 104
2019-06-11 21:00 | 80 | 77 |  |  | 43627.875 | 100 | 100
2019-06-11 21:30 | 77 | 74 |  |  | 43627.8958 | 95 | 94
2019-06-11 22:00 | 77 | 73 |  |  | 43627.9167 | 95 | 94
2019-06-11 22:30 | 73 | 70 |  |  | 43627.9375 | 92 | 91
2019-06-11 23:00 | 69 | 65 |  |  | 43627.9583 | 85 | 84
2019-06-11 23:30 | 65 | 60 |  |  | 43627.9792 | 80 | 78
2019-06-12 | 62 | 56 |  |  | 43628 | 76 | 74
2019-06-12 00:30 | 60 | 54 |  |  | 43628.0208 | 72 | 70
2019-06-12 01:00 | 59 | 52 |  |  | 43628.0417 | 69 | 67
2019-06-12 01:30 | 58 | 50 |  |  | 43628.0625 | 66 | 64
2019-06-12 02:00 | 57 | 50 |  |  | 43628.0833 | 65 | 63
2019-06-12 02:30 | 57 | 50 |  |  | 43628.1042 | 65 | 63
2019-06-12 03:00 | 57 | 50 |  |  | 43628.125 | 65 | 63
2019-06-12 03:30 | 57 | 50 |  |  | 43628.1458 | 65 | 63
2019-06-12 04:00 | 55 | 48 |  |  | 43628.1667 | 63 | 62
2019-06-12 04:30 | 57 | 50 |  |  | 43628.1875 | 65 | 64
2019-06-12 05:00 | 60 | 53 |  |  | 43628.2083 | 69 | 68
2019-06-12 05:30 | 65 | 60 |  |  | 43628.2292 | 76 | 75
2019-06-12 06:00 | 70 | 66 |  |  | 43628.25 | 84 | 83
2019-06-12 06:30 | 75 | 73 |  |  | 43628.2708 | 95 | 94
2019-06-12 07:00 | 79 | 79 |  |  | 43628.2917 | 105 | 105
2019-06-12 07:30 | 87 | 86 |  |  | 43628.3125 | 116 | 116
2019-06-12 08:00 | 86 | 84 |  |  | 43628.3333 | 116 | 114
2019-06-12 08:30 | 79 | 78 |  |  | 43628.3542 | 111 | 109
2019-06-12 09:00 | 72 | 71 |  |  | 43628.375 | 103 | 101
2019-06-12 09:30 | 69 | 67 |  |  | 43628.3958 | 99 | 98
2019-06-12 10:00 | 67 | 65 |  |  | 43628.4167 | 98 | 97
2019-06-12 10:30 | 64 | 62 |  |  | 43628.4375 | 96 | 95
2019-06-12 11:00 | 65 | 63 |  |  | 43628.4583 | 96 | 94
2019-06-12 11:30 | 67 | 65 |  |  | 43628.4792 | 93 | 92
2019-06-12 12:00 | 69 | 67 |  |  | 43628.5 | 97 | 96
2019-06-12 12:30 | 68 | 67 |  |  | 43628.5208 | 100 | 99
2019-06-12 13:00 | 72 | 71 |  |  | 43628.5417 | 101 | 99
2019-06-12 13:30 | 73 | 72 |  |  | 43628.5625 | 99 | 98
2019-06-12 14:00 | 73 | 71 |  |  | 43628.5833 | 100 | 99
2019-06-12 14:30 | 74 | 73 |  |  | 43628.6042 | 102 | 100
2019-06-12 15:00 | 76 | 74 |  |  | 43628.625 | 102 | 101
2019-06-12 15:30 | 77 | 75 |  |  | 43628.6458 | 104 | 102
2019-06-12 16:00 | 81 | 79 |  |  | 43628.6667 | 109 | 107
2019-06-12 16:30 | 84 | 82 |  |  | 43628.6875 | 112 | 110
2019-06-12 17:00 | 86 | 84 |  |  | 43628.7083 | 112 | 110
2019-06-12 17:30 | 88 | 86 |  |  | 43628.7292 | 114 | 113
2019-06-12 18:00 | 89 | 88 |  |  | 43628.75 | 115 | 114
2019-06-12 18:30 | 86 | 85 |  |  | 43628.7708 | 112 | 110
2019-06-12 19:00 | 87 | 86 |  |  | 43628.7917 | 112 | 110
2019-06-12 19:30 | 85 | 84 |  |  | 43628.8125 | 110 | 108
2019-06-12 20:00 | 85 | 83 |  |  | 43628.8333 | 108 | 105
2019-06-12 20:30 | 84 | 82 |  |  | 43628.8542 | 107 | 104
2019-06-12 21:00 | 80 | 78 |  |  | 43628.875 | 103 | 99
2019-06-12 21:30 | 76 | 73 |  |  | 43628.8958 | 98 | 94
2019-06-12 22:00 | 79 | 71 |  |  | 43628.9167 | 99 | 93
2019-06-12 22:30 | 72 | 64 |  |  | 43628.9375 | 94 | 89
2019-06-12 23:00 | 67 | 58 |  |  | 43628.9583 | 88 | 82
2019-06-12 23:30 | 61 | 55 |  |  | 43628.9792 | 77 | 76
2019-06-13 | 58 | 51 |  |  | 43629 | 72 | 71
2019-06-13 00:30 | 57 | 50 |  |  | 43629.0208 | 70 | 68
2019-06-13 01:00 | 56 | 49 |  |  | 43629.0417 | 66 | 65
2019-06-13 01:30 | 56 | 48 |  |  | 43629.0625 | 64 | 63
2019-06-13 02:00 | 57 | 49 |  |  | 43629.0833 | 65 | 63
2019-06-13 02:30 | 56 | 49 |  |  | 43629.1042 | 64 | 62
2019-06-13 03:00 | 54 | 48 |  |  | 43629.125 | 63 | 62
2019-06-13 03:30 | 55 | 47 |  |  | 43629.1458 | 62 | 61
2019-06-13 04:00 | 55 | 47 |  |  | 43629.1667 | 62 | 60
2019-06-13 04:30 | 55 | 48 |  |  | 43629.1875 | 63 | 61
2019-06-13 05:00 | 58 | 52 |  |  | 43629.2083 | 68 | 66
2019-06-13 05:30 | 61 | 56 |  |  | 43629.2292 | 72 | 71
2019-06-13 06:00 | 67 | 62 |  |  | 43629.25 | 80 | 79
2019-06-13 06:30 | 72 | 69 |  |  | 43629.2708 | 90 | 89
2019-06-13 07:00 | 74 | 71 |  |  | 43629.2917 | 97 | 97
2019-06-13 07:30 | 84 | 82 |  |  | 43629.3125 | 114 | 114
2019-06-13 08:00 | 85 | 83 |  |  | 43629.3333 | 117 | 117
2019-06-13 08:30 | 81 | 79 |  |  | 43629.3542 | 113 | 113
2019-06-13 09:00 | 78 | 76 |  |  | 43629.375 | 112 | 112
2019-06-13 09:30 | 73 | 70 |  |  | 43629.3958 | 104 | 104
2019-06-13 10:00 | 70 | 67 |  |  | 43629.4167 | 98 | 98
2019-06-13 10:30 | 69 | 66 |  |  | 43629.4375 | 101 | 101
2019-06-13 11:00 | 70 | 67 |  |  | 43629.4583 | 101 | 101
2019-06-13 11:30 | 67 | 64 |  |  | 43629.4792 | 96 | 96
2019-06-13 12:00 | 60 | 58 |  |  | 43629.5 | 87 | 87
2019-06-13 12:30 | 67 | 65 |  |  | 43629.5208 | 94 | 94
2019-06-13 13:00 | 72 | 70 |  |  | 43629.5417 | 96 | 96
2019-06-13 13:30 | 73 | 71 |  |  | 43629.5625 | 99 | 98
2019-06-13 14:00 | 75 | 73 |  |  | 43629.5833 | 104 | 104
2019-06-13 14:30 | 75 | 72 |  |  | 43629.6042 | 101 | 101
2019-06-13 15:00 | 73 | 71 |  |  | 43629.625 | 101 | 101
2019-06-13 15:30 | 73 | 70 |  |  | 43629.6458 | 99 | 99
2019-06-13 16:00 | 75 | 73 |  |  | 43629.6667 | 102 | 102
2019-06-13 16:30 | 80 | 77 |  |  | 43629.6875 | 105 | 105
2019-06-13 17:00 | 84 | 81 |  |  | 43629.7083 | 110 | 109
2019-06-13 17:30 | 89 | 85 |  |  | 43629.7292 | 114 | 112
2019-06-13 18:00 | 90 | 86 |  |  | 43629.75 | 116 | 113
2019-06-13 18:30 | 90 | 85 |  |  | 43629.7708 | 114 | 110
2019-06-13 19:00 | 91 | 86 |  |  | 43629.7917 | 114 | 110
2019-06-13 19:30 | 89 | 83 |  |  | 43629.8125 | 112 | 107
2019-06-13 20:00 | 88 | 82 |  |  | 43629.8333 | 110 | 105
2019-06-13 20:30 | 87 | 81 |  |  | 43629.8542 | 109 | 105
2019-06-13 21:00 | 82 | 76 |  |  | 43629.875 | 104 | 100
2019-06-13 21:30 | 81 | 73 |  |  | 43629.8958 | 102 | 95
2019-06-13 22:00 | 78 | 69 |  |  | 43629.9167 | 99 | 92
2019-06-13 22:30 | 70 | 63 |  |  | 43629.9375 | 91 | 87
2019-06-13 23:00 | 67 | 60 |  |  | 43629.9583 | 85 | 82
2019-06-13 23:30 | 63 | 55 |  |  | 43629.9792 | 80 | 76
2019-06-14 | 63 | 49 |  |  | 43630 | 76 | 70
2019-06-14 00:30 | 62 | 46 |  |  | 43630.0208 | 72 | 66
2019-06-14 01:00 | 61 | 45 |  |  | 43630.0417 | 69 | 63
2019-06-14 01:30 | 61 | 45 |  |  | 43630.0625 | 68 | 61
2019-06-14 02:00 | 62 | 45 |  |  | 43630.0833 | 67 | 60
2019-06-14 02:30 | 62 | 45 |  |  | 43630.1042 | 68 | 60
2019-06-14 03:00 | 62 | 45 |  |  | 43630.125 | 68 | 60
2019-06-14 03:30 | 63 | 47 |  |  | 43630.1458 | 68 | 60
2019-06-14 04:00 | 63 | 48 |  |  | 43630.1667 | 68 | 62
2019-06-14 04:30 | 65 | 51 |  |  | 43630.1875 | 71 | 65
2019-06-14 05:00 | 68 | 55 |  |  | 43630.2083 | 73 | 68
2019-06-14 05:30 | 68 | 57 |  |  | 43630.2292 | 76 | 72
2019-06-14 06:00 | 70 | 62 |  |  | 43630.25 | 82 | 79
2019-06-14 06:30 | 74 | 70 |  |  | 43630.2708 | 93 | 91
2019-06-14 07:00 | 78 | 75 |  |  | 43630.2917 | 104 | 103
2019-06-14 07:30 | 88 | 83 |  |  | 43630.3125 | 119 | 117
2019-06-14 08:00 | 87 | 80 |  |  | 43630.3333 | 118 | 115
2019-06-14 08:30 | 84 | 77 |  |  | 43630.3542 | 115 | 112
2019-06-14 09:00 | 80 | 73 |  |  | 43630.375 | 110 | 107
2019-06-14 09:30 | 78 | 71 |  |  | 43630.3958 | 107 | 104
2019-06-14 10:00 | 76 | 69 |  |  | 43630.4167 | 106 | 103
2019-06-14 10:30 | 72 | 65 |  |  | 43630.4375 | 100 | 97
2019-06-14 11:00 | 69 | 61 |  |  | 43630.4583 | 99 | 96
2019-06-14 11:30 | 67 | 61 |  |  | 43630.4792 | 97 | 94
2019-06-14 12:00 | 68 | 61 |  |  | 43630.5 | 98 | 95
2019-06-14 12:30 | 66 | 59 |  |  | 43630.5208 | 92 | 89
2019-06-14 13:00 | 67 | 59 |  |  | 43630.5417 | 90 | 88
2019-06-14 13:30 | 68 | 61 |  |  | 43630.5625 | 94 | 92
2019-06-14 14:00 | 71 | 65 |  |  | 43630.5833 | 98 | 95
2019-06-14 14:30 | 71 | 65 |  |  | 43630.6042 | 97 | 95
2019-06-14 15:00 | 73 | 67 |  |  | 43630.625 | 99 | 96
2019-06-14 15:30 | 75 | 68 |  |  | 43630.6458 | 100 | 97
2019-06-14 16:00 | 77 | 71 |  |  | 43630.6667 | 102 | 100
2019-06-14 16:30 | 82 | 77 |  |  | 43630.6875 | 108 | 106
2019-06-14 17:00 | 85 | 79 |  |  | 43630.7083 | 111 | 108
2019-06-14 17:30 | 88 | 81 |  |  | 43630.7292 | 112 | 109
2019-06-14 18:00 | 88 | 81 |  |  | 43630.75 | 111 | 107
2019-06-14 18:30 | 85 | 77 |  |  | 43630.7708 | 107 | 102
2019-06-14 19:00 | 86 | 78 |  |  | 43630.7917 | 107 | 101
2019-06-14 19:30 | 84 | 75 |  |  | 43630.8125 | 104 | 98
2019-06-14 20:00 | 81 | 73 |  |  | 43630.8333 | 102 | 96
2019-06-14 20:30 | 79 | 71 |  |  | 43630.8542 | 101 | 95
2019-06-14 21:00 | 76 | 68 |  |  | 43630.875 | 96 | 91
2019-06-14 21:30 | 74 | 65 |  |  | 43630.8958 | 93 | 87
2019-06-14 22:00 | 72 | 64 |  |  | 43630.9167 | 91 | 86
2019-06-14 22:30 | 66 | 59 |  |  | 43630.9375 | 85 | 83
2019-06-14 23:00 | 63 | 55 |  |  | 43630.9583 | 79 | 76
2019-06-14 23:30 | 60 | 51 |  |  | 43630.9792 | 75 | 72
2019-06-15 | 54 | 44 |  |  | 43631 | 69 | 65
2019-06-15 00:30 | 51 | 39 |  |  | 43631.0208 | 64 | 59
2019-06-15 01:00 | 48 | 37 |  |  | 43631.0417 | 61 | 55
2019-06-15 01:30 | 46 | 33 |  |  | 43631.0625 | 58 | 52
2019-06-15 02:00 | 46 | 32 |  |  | 43631.0833 | 57 | 51
2019-06-15 02:30 | 47 | 32 |  |  | 43631.1042 | 57 | 50
2019-06-15 03:00 | 47 | 32 |  |  | 43631.125 | 56 | 49
2019-06-15 03:30 | 47 | 33 |  |  | 43631.1458 | 57 | 50
2019-06-15 04:00 | 49 | 35 |  |  | 43631.1667 | 58 | 51
2019-06-15 04:30 | 49 | 37 |  |  | 43631.1875 | 58 | 54
2019-06-15 05:00 | 50 | 38 |  |  | 43631.2083 | 60 | 55
2019-06-15 05:30 | 50 | 40 |  |  | 43631.2292 | 61 | 57
2019-06-15 06:00 | 51 | 41 |  |  | 43631.25 | 62 | 59
2019-06-15 06:30 | 51 | 43 |  |  | 43631.2708 | 64 | 61
2019-06-15 07:00 | 51 | 42 |  |  | 43631.2917 | 66 | 63
2019-06-15 07:30 | 53 | 46 |  |  | 43631.3125 | 70 | 68
2019-06-15 08:00 | 54 | 47 |  |  | 43631.3333 | 71 | 69
2019-06-15 08:30 | 53 | 47 |  |  | 43631.3542 | 72 | 70
2019-06-15 09:00 | 54 | 47 |  |  | 43631.375 | 73 | 72
2019-06-15 09:30 | 53 | 47 |  |  | 43631.3958 | 72 | 71
2019-06-15 10:00 | 50 | 44 |  |  | 43631.4167 | 69 | 68
2019-06-15 10:30 | 49 | 43 |  |  | 43631.4375 | 68 | 67
2019-06-15 11:00 | 49 | 43 |  |  | 43631.4583 | 67 | 66
2019-06-15 11:30 | 48 | 41 |  |  | 43631.4792 | 66 | 65
2019-06-15 12:00 | 46 | 39 |  |  | 43631.5 | 64 | 63
2019-06-15 12:30 | 44 | 37 |  |  | 43631.5208 | 63 | 61
2019-06-15 13:00 | 45 | 38 |  |  | 43631.5417 | 63 | 62
2019-06-15 13:30 | 48 | 41 |  |  | 43631.5625 | 67 | 65
2019-06-15 14:00 | 50 | 43 |  |  | 43631.5833 | 68 | 67
2019-06-15 14:30 | 53 | 46 |  |  | 43631.6042 | 71 | 70
2019-06-15 15:00 | 55 | 49 |  |  | 43631.625 | 73 | 72
2019-06-15 15:30 | 58 | 52 |  |  | 43631.6458 | 76 | 75
2019-06-15 16:00 | 62 | 57 |  |  | 43631.6667 | 79 | 78
2019-06-15 16:30 | 62 | 57 |  |  | 43631.6875 | 81 | 80
2019-06-15 17:00 | 64 | 59 |  |  | 43631.7083 | 85 | 83
2019-06-15 17:30 | 70 | 63 |  |  | 43631.7292 | 91 | 88
2019-06-15 18:00 | 73 | 64 |  |  | 43631.75 | 95 | 89
2019-06-15 18:30 | 72 | 62 |  |  | 43631.7708 | 94 | 88
2019-06-15 19:00 | 72 | 62 |  |  | 43631.7917 | 94 | 88
2019-06-15 19:30 | 69 | 61 |  |  | 43631.8125 | 90 | 86
2019-06-15 20:00 | 65 | 59 |  |  | 43631.8333 | 86 | 85
2019-06-15 20:30 | 64 | 58 |  |  | 43631.8542 | 84 | 83
2019-06-15 21:00 | 60 | 54 |  |  | 43631.875 | 79 | 78
2019-06-15 21:30 | 59 | 52 |  |  | 43631.8958 | 77 | 75
2019-06-15 22:00 | 60 | 53 |  |  | 43631.9167 | 78 | 77
2019-06-15 22:30 | 59 | 53 |  |  | 43631.9375 | 78 | 76
2019-06-15 23:00 | 56 | 49 |  |  | 43631.9583 | 73 | 71
2019-06-15 23:30 | 55 | 47 |  |  | 43631.9792 | 70 | 68
2019-06-16 | 53 | 44 |  |  | 43632 | 67 | 65
2019-06-16 00:30 | 51 | 42 |  |  | 43632.0208 | 63 | 61
2019-06-16 01:00 | 49 | 40 |  |  | 43632.0417 | 60 | 58
2019-06-16 01:30 | 47 | 38 |  |  | 43632.0625 | 57 | 55
2019-06-16 02:00 | 45 | 35 |  |  | 43632.0833 | 55 | 52
2019-06-16 02:30 | 45 | 35 |  |  | 43632.1042 | 55 | 52
2019-06-16 03:00 | 40 | 36 |  |  | 43632.125 | 58 | 52
2019-06-16 03:30 | 41 | 36 |  |  | 43632.1458 | 59 | 52
2019-06-16 04:00 | 42 | 36 |  |  | 43632.1667 | 58 | 52
2019-06-16 04:30 | 42 | 37 |  |  | 43632.1875 | 58 | 52
2019-06-16 05:00 | 43 | 38 |  |  | 43632.2083 | 58 | 52
2019-06-16 05:30 | 43 | 38 |  |  | 43632.2292 | 61 | 54
2019-06-16 06:00 | 46 | 41 |  |  | 43632.25 | 63 | 57
2019-06-16 06:30 | 46 | 41 |  |  | 43632.2708 | 66 | 60
2019-06-16 07:00 | 46 | 41 |  |  | 43632.2917 | 67 | 61
2019-06-16 07:30 | 47 | 42 |  |  | 43632.3125 | 69 | 63
2019-06-16 08:00 | 43 | 38 |  |  | 43632.3333 | 66 | 60
2019-06-16 08:30 | 42 | 37 |  |  | 43632.3542 | 65 | 59
2019-06-16 09:00 | 44 | 40 |  |  | 43632.375 | 68 | 63
2019-06-16 09:30 | 48 | 45 |  |  | 43632.3958 | 73 | 68
2019-06-16 10:00 | 50 | 46 |  |  | 43632.4167 | 73 | 68
2019-06-16 10:30 | 49 | 46 |  |  | 43632.4375 | 74 | 68
2019-06-16 11:00 | 52 | 49 |  |  | 43632.4583 | 74 | 68
2019-06-16 11:30 | 48 | 43 |  |  | 43632.4792 | 72 | 66
2019-06-16 12:00 | 47 | 43 |  |  | 43632.5 | 67 | 60
2019-06-16 12:30 | 48 | 44 |  |  | 43632.5208 | 64 | 57
2019-06-16 13:00 | 48 | 44 |  |  | 43632.5417 | 70 | 63
2019-06-16 13:30 | 48 | 44 |  |  | 43632.5625 | 73 | 67
2019-06-16 14:00 | 45 | 40 |  |  | 43632.5833 | 66 | 59
2019-06-16 14:30 | 49 | 45 |  |  | 43632.6042 | 69 | 63
2019-06-16 15:00 | 55 | 51 |  |  | 43632.625 | 77 | 72
2019-06-16 15:30 | 60 | 58 |  |  | 43632.6458 | 83 | 79
2019-06-16 16:00 | 63 | 60 |  |  | 43632.6667 | 87 | 83
2019-06-16 16:30 | 65 | 62 |  |  | 43632.6875 | 89 | 84
2019-06-16 17:00 | 65 | 62 |  |  | 43632.7083 | 91 | 86
2019-06-16 17:30 | 68 | 65 |  |  | 43632.7292 | 93 | 88
2019-06-16 18:00 | 69 | 66 |  |  | 43632.75 | 94 | 89
2019-06-16 18:30 | 69 | 65 |  |  | 43632.7708 | 94 | 88
2019-06-16 19:00 | 69 | 65 |  |  | 43632.7917 | 94 | 89
2019-06-16 19:30 | 69 | 65 |  |  | 43632.8125 | 93 | 87
2019-06-16 20:00 | 68 | 63 |  |  | 43632.8333 | 92 | 86
2019-06-16 20:30 | 67 | 63 |  |  | 43632.8542 | 92 | 86
2019-06-16 21:00 | 63 | 58 |  |  | 43632.875 | 87 | 81
2019-06-16 21:30 | 60 | 55 |  |  | 43632.8958 | 84 | 77
2019-06-16 22:00 | 57 | 54 |  |  | 43632.9167 | 83 | 76
2019-06-16 22:30 | 56 | 53 |  |  | 43632.9375 | 80 | 75
2019-06-16 23:00 | 53 | 49 |  |  | 43632.9583 | 77 | 71
2019-06-16 23:30 | 50 | 46 |  |  | 43632.9792 | 73 | 67
2019-06-17 | 49 | 45 |  |  | 43633 | 69 | 64
2019-06-17 00:30 | 48 | 43 |  |  | 43633.0208 | 68 | 62
2019-06-17 01:00 | 47 | 41 |  |  | 43633.0417 | 65 | 59
2019-06-17 01:30 | 45 | 40 |  |  | 43633.0625 | 63 | 57
2019-06-17 02:00 | 44 | 39 |  |  | 43633.0833 | 60 | 56
2019-06-17 02:30 | 44 | 39 |  |  | 43633.1042 | 60 | 55
2019-06-17 03:00 | 43 | 38 |  |  | 43633.125 | 59 | 54
2019-06-17 03:30 | 43 | 38 |  |  | 43633.1458 | 59 | 54
2019-06-17 04:00 | 44 | 39 |  |  | 43633.1667 | 60 | 55
2019-06-17 04:30 | 46 | 42 |  |  | 43633.1875 | 62 | 58
2019-06-17 05:00 | 49 | 45 |  |  | 43633.2083 | 66 | 62
2019-06-17 05:30 | 53 | 50 |  |  | 43633.2292 | 70 | 67
2019-06-17 06:00 | 59 | 58 |  |  | 43633.25 | 78 | 76
2019-06-17 06:30 | 66 | 64 |  |  | 43633.2708 | 88 | 86
2019-06-17 07:00 | 72 | 70 |  |  | 43633.2917 | 97 | 95
2019-06-17 07:30 | 77 | 76 |  |  | 43633.3125 | 105 | 104
2019-06-17 08:00 | 78 | 76 |  |  | 43633.3333 | 109 | 107
2019-06-17 08:30 | 73 | 72 |  |  | 43633.3542 | 104 | 103
2019-06-17 09:00 | 68 | 66 |  |  | 43633.375 | 96 | 96
2019-06-17 09:30 | 64 | 64 |  |  | 43633.3958 | 93 | 92
2019-06-17 10:00 | 60 | 59 |  |  | 43633.4167 | 88 | 88
2019-06-17 10:30 | 58 | 58 |  |  | 43633.4375 | 85 | 85
2019-06-17 11:00 | 56 | 55 |  |  | 43633.4583 | 82 | 82
2019-06-17 11:30 | 54 | 54 |  |  | 43633.4792 | 81 | 81
2019-06-17 12:00 | 54 | 54 |  |  | 43633.5 | 81 | 81
2019-06-17 12:30 | 52 | 52 |  |  | 43633.5208 | 80 | 79
2019-06-17 13:00 | 53 | 53 |  |  | 43633.5417 | 80 | 79
2019-06-17 13:30 | 55 | 55 |  |  | 43633.5625 | 82 | 82
2019-06-17 14:00 | 55 | 54 |  |  | 43633.5833 | 81 | 81
2019-06-17 14:30 | 57 | 56 |  |  | 43633.6042 | 85 | 83
2019-06-17 15:00 | 59 | 58 |  |  | 43633.625 | 88 | 85
2019-06-17 15:30 | 63 | 61 |  |  | 43633.6458 | 92 | 88
2019-06-17 16:00 | 67 | 65 |  |  | 43633.6667 | 96 | 92
2019-06-17 16:30 | 72 | 68 |  |  | 43633.6875 | 103 | 95
2019-06-17 17:00 | 77 | 73 |  |  | 43633.7083 | 108 | 100
2019-06-17 17:30 | 81 | 76 |  |  | 43633.7292 | 113 | 105
2019-06-17 18:00 | 84 | 79 |  |  | 43633.75 | 115 | 106
2019-06-17 18:30 | 83 | 78 |  |  | 43633.7708 | 113 | 103
2019-06-17 19:00 | 84 | 79 |  |  | 43633.7917 | 114 | 104
2019-06-17 19:30 | 82 | 76 |  |  | 43633.8125 | 112 | 101
2019-06-17 20:00 | 81 | 77 |  |  | 43633.8333 | 109 | 101
2019-06-17 20:30 | 80 | 76 |  |  | 43633.8542 | 108 | 101
2019-06-17 21:00 | 77 | 72 |  |  | 43633.875 | 105 | 95
2019-06-17 21:30 | 73 | 68 |  |  | 43633.8958 | 100 | 90
2019-06-17 22:00 | 73 | 67 |  |  | 43633.9167 | 101 | 88
2019-06-17 22:30 | 70 | 64 |  |  | 43633.9375 | 97 | 85
2019-06-17 23:00 | 65 | 61 |  |  | 43633.9583 | 88 | 80
2019-06-17 23:30 | 61 | 56 |  |  | 43633.9792 | 83 | 75
2019-06-18 | 56 | 51 |  |  | 43634 | 79 | 71
2019-06-18 00:30 | 55 | 50 |  |  | 43634.0208 | 75 | 67
2019-06-18 01:00 | 52 | 47 |  |  | 43634.0417 | 71 | 63
2019-06-18 01:30 | 51 | 45 |  |  | 43634.0625 | 69 | 61
2019-06-18 02:00 | 52 | 46 |  |  | 43634.0833 | 70 | 61
2019-06-18 02:30 | 51 | 45 |  |  | 43634.1042 | 69 | 59
2019-06-18 03:00 | 51 | 45 |  |  | 43634.125 | 69 | 59
2019-06-18 03:30 | 51 | 45 |  |  | 43634.1458 | 69 | 59
2019-06-18 04:00 | 53 | 47 |  |  | 43634.1667 | 69 | 59
2019-06-18 04:30 | 54 | 48 |  |  | 43634.1875 | 71 | 62
2019-06-18 05:00 | 56 | 51 |  |  | 43634.2083 | 74 | 65
2019-06-18 05:30 | 61 | 58 |  |  | 43634.2292 | 79 | 73
2019-06-18 06:00 | 66 | 64 |  |  | 43634.25 | 87 | 82
2019-06-18 06:30 | 74 | 72 |  |  | 43634.2708 | 100 | 95
2019-06-18 07:00 | 84 | 80 |  |  | 43634.2917 | 116 | 108
2019-06-18 07:30 | 87 | 83 |  |  | 43634.3125 | 125 | 117
2019-06-18 08:00 | 87 | 83 |  |  | 43634.3333 | 125 | 116
2019-06-18 08:30 | 80 | 76 |  |  | 43634.3542 | 118 | 108
2019-06-18 09:00 | 72 | 69 |  |  | 43634.375 | 108 | 101
2019-06-18 09:30 | 67 | 63 |  |  | 43634.3958 | 102 | 95
2019-06-18 10:00 | 61 | 60 |  |  | 43634.4167 | 93 | 89
2019-06-18 10:30 | 58 | 57 |  |  | 43634.4375 | 87 | 85
2019-06-18 11:00 | 55 | 55 |  |  | 43634.4583 | 83 | 83
2019-06-18 11:30 | 55 | 54 |  |  | 43634.4792 | 82 | 81
2019-06-18 12:00 | 54 | 54 |  |  | 43634.5 | 81 | 80
2019-06-18 12:30 | 53 | 53 |  |  | 43634.5208 | 81 | 80
2019-06-18 13:00 | 54 | 54 |  |  | 43634.5417 | 81 | 80
2019-06-18 13:30 | 55 | 55 |  |  | 43634.5625 | 82 | 82
2019-06-18 14:00 | 57 | 57 |  |  | 43634.5833 | 84 | 83
2019-06-18 14:30 | 60 | 60 |  |  | 43634.6042 | 87 | 86
2019-06-18 15:00 | 62 | 62 |  |  | 43634.625 | 90 | 88
2019-06-18 15:30 | 65 | 65 |  |  | 43634.6458 | 93 | 91
2019-06-18 16:00 | 70 | 70 |  |  | 43634.6667 | 98 | 97
2019-06-18 16:30 | 73 | 72 |  |  | 43634.6875 | 102 | 100
2019-06-18 17:00 | 77 | 77 |  |  | 43634.7083 | 107 | 106
2019-06-18 17:30 | 82 | 82 |  |  | 43634.7292 | 112 | 110
2019-06-18 18:00 | 84 | 84 |  |  | 43634.75 | 114 | 112
2019-06-18 18:30 | 83 | 83 |  |  | 43634.7708 | 113 | 110
2019-06-18 19:00 | 84 | 84 |  |  | 43634.7917 | 113 | 110
2019-06-18 19:30 | 82 | 81 |  |  | 43634.8125 | 111 | 108
2019-06-18 20:00 | 81 | 81 |  |  | 43634.8333 | 109 | 106
2019-06-18 20:30 | 79 | 79 |  |  | 43634.8542 | 108 | 105
2019-06-18 21:00 | 77 | 77 |  |  | 43634.875 | 104 | 101
2019-06-18 21:30 | 73 | 73 |  |  | 43634.8958 | 99 | 95
2019-06-18 22:00 | 72 | 72 |  |  | 43634.9167 | 98 | 94
2019-06-18 22:30 | 69 | 67 |  |  | 43634.9375 | 95 | 90
2019-06-18 23:00 | 68 | 64 |  |  | 43634.9583 | 90 | 83
2019-06-18 23:30 | 64 | 60 |  |  | 43634.9792 | 86 | 79
2019-06-19 | 61 | 56 |  |  | 43635 | 82 | 75
2019-06-19 00:30 | 57 | 52 |  |  | 43635.0208 | 78 | 69
2019-06-19 01:00 | 53 | 47 |  |  | 43635.0417 | 73 | 63
2019-06-19 01:30 | 51 | 44 |  |  | 43635.0625 | 71 | 60
2019-06-19 02:00 | 48 | 41 |  |  | 43635.0833 | 68 | 56
2019-06-19 02:30 | 47 | 40 |  |  | 43635.1042 | 66 | 54
2019-06-19 03:00 | 48 | 41 |  |  | 43635.125 | 66 | 54
2019-06-19 03:30 | 47 | 40 |  |  | 43635.1458 | 66 | 54
2019-06-19 04:00 | 47 | 40 |  |  | 43635.1667 | 67 | 55
2019-06-19 04:30 | 50 | 44 |  |  | 43635.1875 | 69 | 57
2019-06-19 05:00 | 56 | 50 |  |  | 43635.2083 | 74 | 63
2019-06-19 05:30 | 60 | 55 |  |  | 43635.2292 | 78 | 69
2019-06-19 06:00 | 67 | 64 |  |  | 43635.25 | 87 | 81
2019-06-19 06:30 | 74 | 73 |  |  | 43635.2708 | 100 | 96
2019-06-19 07:00 | 81 | 81 |  |  | 43635.2917 | 111 | 109
2019-06-19 07:30 | 86 | 86 |  |  | 43635.3125 | 120 | 118
2019-06-19 08:00 | 80 | 80 |  |  | 43635.3333 | 116 | 114
2019-06-19 08:30 | 70 | 70 |  |  | 43635.3542 | 103 | 100
2019-06-19 09:00 | 71 | 67 |  |  | 43635.375 | 103 | 98
2019-06-19 09:30 | 71 | 66 |  |  | 43635.3958 | 99 | 95
2019-06-19 10:00 | 68 | 61 |  |  | 43635.4167 | 92 | 91
2019-06-19 10:30 | 66 | 60 |  |  | 43635.4375 | 89 | 87
2019-06-19 11:00 | 64 | 57 |  |  | 43635.4583 | 87 | 85
2019-06-19 11:30 | 64 | 57 |  |  | 43635.4792 | 88 | 86
2019-06-19 12:00 | 67 | 61 |  |  | 43635.5 | 94 | 92
2019-06-19 12:30 | 67 | 61 |  |  | 43635.5208 | 94 | 92
2019-06-19 13:00 | 67 | 60 |  |  | 43635.5417 | 93 | 91
2019-06-19 13:30 | 66 | 59 |  |  | 43635.5625 | 93 | 92
2019-06-19 14:00 | 67 | 61 |  |  | 43635.5833 | 95 | 94
2019-06-19 14:30 | 69 | 64 |  |  | 43635.6042 | 98 | 96
2019-06-19 15:00 | 70 | 66 |  |  | 43635.625 | 101 | 100
2019-06-19 15:30 | 73 | 69 |  |  | 43635.6458 | 104 | 103
2019-06-19 16:00 | 78 | 74 |  |  | 43635.6667 | 110 | 109
2019-06-19 16:30 | 79 | 77 |  |  | 43635.6875 | 113 | 112
2019-06-19 17:00 | 83 | 82 |  |  | 43635.7083 | 119 | 116
2019-06-19 17:30 | 86 | 84 |  |  | 43635.7292 | 122 | 119
2019-06-19 18:00 | 87 | 85 |  |  | 43635.75 | 123 | 120
2019-06-19 18:30 | 86 | 84 |  |  | 43635.7708 | 122 | 118
2019-06-19 19:00 | 86 | 84 |  |  | 43635.7917 | 122 | 118
2019-06-19 19:30 | 84 | 81 |  |  | 43635.8125 | 119 | 115
2019-06-19 20:00 | 82 | 79 |  |  | 43635.8333 | 117 | 113
2019-06-19 20:30 | 81 | 78 |  |  | 43635.8542 | 116 | 112
2019-06-19 21:00 | 77 | 74 |  |  | 43635.875 | 112 | 106
2019-06-19 21:30 | 74 | 71 |  |  | 43635.8958 | 106 | 102
2019-06-19 22:00 | 72 | 70 |  |  | 43635.9167 | 102 | 101
2019-06-19 22:30 | 69 | 68 |  |  | 43635.9375 | 99 | 98
2019-06-19 23:00 | 68 | 67 |  |  | 43635.9583 | 95 | 94
2019-06-19 23:30 | 65 | 63 |  |  | 43635.9792 | 91 | 89
2019-06-20 | 59 | 58 |  |  | 43636 | 87 | 82
2019-06-20 00:30 | 57 | 53 |  |  | 43636.0208 | 84 | 75
2019-06-20 01:00 | 55 | 51 |  |  | 43636.0417 | 81 | 71
2019-06-20 01:30 | 52 | 47 |  |  | 43636.0625 | 77 | 66
2019-06-20 02:00 | 47 | 43 |  |  | 43636.0833 | 73 | 63
2019-06-20 02:30 | 48 | 43 |  |  | 43636.1042 | 72 | 62
2019-06-20 03:00 | 47 | 43 |  |  | 43636.125 | 72 | 62
2019-06-20 03:30 | 47 | 44 |  |  | 43636.1458 | 73 | 64
2019-06-20 04:00 | 48 | 44 |  |  | 43636.1667 | 72 | 62
2019-06-20 04:30 | 49 | 46 |  |  | 43636.1875 | 74 | 64
2019-06-20 05:00 | 53 | 49 |  |  | 43636.2083 | 77 | 69
2019-06-20 05:30 | 59 | 57 |  |  | 43636.2292 | 83 | 77
2019-06-20 06:00 | 68 | 66 |  |  | 43636.25 | 92 | 88
2019-06-20 06:30 | 78 | 76 |  |  | 43636.2708 | 104 | 104
2019-06-20 07:00 | 87 | 82 |  |  | 43636.2917 | 118 | 117
2019-06-20 07:30 | 90 | 86 |  |  | 43636.3125 | 125 | 124
2019-06-20 08:00 | 88 | 84 |  |  | 43636.3333 | 125 | 124
2019-06-20 08:30 | 84 | 81 |  |  | 43636.3542 | 122 | 121
2019-06-20 09:00 | 86 | 79 |  |  | 43636.375 | 118 | 117
2019-06-20 09:30 | 86 | 76 |  |  | 43636.3958 | 117 | 115
2019-06-20 10:00 | 89 | 80 |  |  | 43636.4167 | 122 | 120
2019-06-20 10:30 | 91 | 81 |  |  | 43636.4375 | 121 | 119
2019-06-20 11:00 | 91 | 81 |  |  | 43636.4583 | 124 | 122
2019-06-20 11:30 | 84 | 78 |  |  | 43636.4792 | 116 | 113
2019-06-20 12:00 | 82 | 75 |  |  | 43636.5 | 116 | 111
2019-06-20 12:30 | 80 | 72 |  |  | 43636.5208 | 114 | 109
2019-06-20 13:00 | 82 | 74 |  |  | 43636.5417 | 117 | 111
2019-06-20 13:30 | 85 | 77 |  |  | 43636.5625 | 115 | 110
2019-06-20 14:00 | 86 | 78 |  |  | 43636.5833 | 118 | 113
2019-06-20 14:30 | 85 | 78 |  |  | 43636.6042 | 117 | 112
2019-06-20 15:00 | 84 | 76 |  |  | 43636.625 | 116 | 112
2019-06-20 15:30 | 85 | 78 |  |  | 43636.6458 | 117 | 112
2019-06-20 16:00 | 88 | 81 |  |  | 43636.6667 | 120 | 115
2019-06-20 16:30 | 91 | 83 |  |  | 43636.6875 | 122 | 116
2019-06-20 17:00 | 89 | 85 |  |  | 43636.7083 | 125 | 121
2019-06-20 17:30 | 90 | 87 |  |  | 43636.7292 | 128 | 125
2019-06-20 18:00 | 90 | 88 |  |  | 43636.75 | 128 | 124
2019-06-20 18:30 | 90 | 87 |  |  | 43636.7708 | 126 | 122
2019-06-20 19:00 | 90 | 87 |  |  | 43636.7917 | 126 | 122
2019-06-20 19:30 | 87 | 85 |  |  | 43636.8125 | 121 | 119
2019-06-20 20:00 | 86 | 84 |  |  | 43636.8333 | 120 | 117
2019-06-20 20:30 | 85 | 83 |  |  | 43636.8542 | 119 | 116
2019-06-20 21:00 | 80 | 78 |  |  | 43636.875 | 112 | 110
2019-06-20 21:30 | 74 | 73 |  |  | 43636.8958 | 104 | 103
2019-06-20 22:00 | 73 | 72 |  |  | 43636.9167 | 103 | 102
2019-06-20 22:30 | 70 | 69 |  |  | 43636.9375 | 99 | 98
2019-06-20 23:00 | 68 | 66 |  |  | 43636.9583 | 94 | 93
2019-06-20 23:30 | 65 | 63 |  |  | 43636.9792 | 91 | 89
2019-06-21 | 58 | 58 |  |  | 43637 | 87 | 83
2019-06-21 00:30 | 54 | 54 |  |  | 43637.0208 | 82 | 76
2019-06-21 01:00 | 51 | 50 |  |  | 43637.0417 | 79 | 72
2019-06-21 01:30 | 48 | 47 |  |  | 43637.0625 | 74 | 68
2019-06-21 02:00 | 43 | 43 |  |  | 43637.0833 | 70 | 64
2019-06-21 02:30 | 43 | 42 |  |  | 43637.1042 | 69 | 63
2019-06-21 03:00 | 44 | 43 |  |  | 43637.125 | 69 | 63
2019-06-21 03:30 | 43 | 43 |  |  | 43637.1458 | 69 | 63
2019-06-21 04:00 | 42 | 42 |  |  | 43637.1667 | 69 | 63
2019-06-21 04:30 | 44 | 44 |  |  | 43637.1875 | 71 | 65
2019-06-21 05:00 | 48 | 48 |  |  | 43637.2083 | 74 | 68
2019-06-21 05:30 | 53 | 53 |  |  | 43637.2292 | 79 | 75
2019-06-21 06:00 | 60 | 60 |  |  | 43637.25 | 86 | 83
2019-06-21 06:30 | 68 | 68 |  |  | 43637.2708 | 98 | 96
2019-06-21 07:00 | 74 | 73 |  |  | 43637.2917 | 108 | 107
2019-06-21 07:30 | 80 | 80 |  |  | 43637.3125 | 118 | 117
2019-06-21 08:00 | 79 | 79 |  |  | 43637.3333 | 119 | 118
2019-06-21 08:30 | 76 | 76 |  |  | 43637.3542 | 117 | 117
2019-06-21 09:00 | 73 | 73 |  |  | 43637.375 | 114 | 113
2019-06-21 09:30 | 69 | 69 |  |  | 43637.3958 | 108 | 107
2019-06-21 10:00 | 64 | 64 |  |  | 43637.4167 | 102 | 101
2019-06-21 10:30 | 60 | 60 |  |  | 43637.4375 | 96 | 95
2019-06-21 11:00 | 57 | 57 |  |  | 43637.4583 | 94 | 93
2019-06-21 11:30 | 56 | 56 |  |  | 43637.4792 | 91 | 90
2019-06-21 12:00 | 53 | 52 |  |  | 43637.5 | 88 | 87
2019-06-21 12:30 | 53 | 52 |  |  | 43637.5208 | 89 | 88
2019-06-21 13:00 | 52 | 51 |  |  | 43637.5417 | 88 | 87
2019-06-21 13:30 | 53 | 53 |  |  | 43637.5625 | 89 | 88
2019-06-21 14:00 | 54 | 54 |  |  | 43637.5833 | 90 | 89
2019-06-21 14:30 | 56 | 56 |  |  | 43637.6042 | 92 | 91
2019-06-21 15:00 | 59 | 59 |  |  | 43637.625 | 94 | 93
2019-06-21 15:30 | 62 | 61 |  |  | 43637.6458 | 97 | 96
2019-06-21 16:00 | 66 | 66 |  |  | 43637.6667 | 102 | 101
2019-06-21 16:30 | 67 | 67 |  |  | 43637.6875 | 103 | 101
2019-06-21 17:00 | 69 | 69 |  |  | 43637.7083 | 106 | 104
2019-06-21 17:30 | 72 | 72 |  |  | 43637.7292 | 109 | 107
2019-06-21 18:00 | 73 | 73 |  |  | 43637.75 | 110 | 107
2019-06-21 18:30 | 71 | 71 |  |  | 43637.7708 | 107 | 104
2019-06-21 19:00 | 72 | 72 |  |  | 43637.7917 | 107 | 104
2019-06-21 19:30 | 72 | 72 |  |  | 43637.8125 | 107 | 103
2019-06-21 20:00 | 71 | 71 |  |  | 43637.8333 | 105 | 102
2019-06-21 20:30 | 70 | 70 |  |  | 43637.8542 | 105 | 101
2019-06-21 21:00 | 67 | 67 |  |  | 43637.875 | 101 | 96
2019-06-21 21:30 | 64 | 64 |  |  | 43637.8958 | 97 | 92
2019-06-21 22:00 | 63 | 63 |  |  | 43637.9167 | 96 | 93
2019-06-21 22:30 | 63 | 63 |  |  | 43637.9375 | 95 | 91
2019-06-21 23:00 | 60 | 60 |  |  | 43637.9583 | 90 | 86
2019-06-21 23:30 | 56 | 56 |  |  | 43637.9792 | 87 | 82
2019-06-22 | 51 | 51 |  |  | 43638 | 82 | 77
2019-06-22 00:30 | 50 | 49 |  |  | 43638.0208 | 78 | 72
2019-06-22 01:00 | 47 | 47 |  |  | 43638.0417 | 73 | 68
2019-06-22 01:30 | 44 | 43 |  |  | 43638.0625 | 70 | 65
2019-06-22 02:00 | 47 | 41 |  |  | 43638.0833 | 71 | 61
2019-06-22 02:30 | 46 | 40 |  |  | 43638.1042 | 70 | 60
2019-06-22 03:00 | 46 | 40 |  |  | 43638.125 | 69 | 59
2019-06-22 03:30 | 46 | 40 |  |  | 43638.1458 | 70 | 59
2019-06-22 04:00 | 47 | 42 |  |  | 43638.1667 | 70 | 60
2019-06-22 04:30 | 48 | 42 |  |  | 43638.1875 | 70 | 60
2019-06-22 05:00 | 49 | 44 |  |  | 43638.2083 | 71 | 61
2019-06-22 05:30 | 51 | 46 |  |  | 43638.2292 | 74 | 64
2019-06-22 06:00 | 54 | 49 |  |  | 43638.25 | 77 | 68
2019-06-22 06:30 | 56 | 53 |  |  | 43638.2708 | 81 | 74
2019-06-22 07:00 | 59 | 56 |  |  | 43638.2917 | 85 | 78
2019-06-22 07:30 | 60 | 57 |  |  | 43638.3125 | 89 | 83
2019-06-22 08:00 | 57 | 55 |  |  | 43638.3333 | 87 | 82
2019-06-22 08:30 | 57 | 55 |  |  | 43638.3542 | 88 | 83
2019-06-22 09:00 | 55 | 53 |  |  | 43638.375 | 86 | 81
2019-06-22 09:30 | 52 | 49 |  |  | 43638.3958 | 83 | 78
2019-06-22 10:00 | 49 | 47 |  |  | 43638.4167 | 80 | 75
2019-06-22 10:30 | 48 | 45 |  |  | 43638.4375 | 76 | 71
2019-06-22 11:00 | 45 | 42 |  |  | 43638.4583 | 73 | 68
2019-06-22 11:30 | 44 | 40 |  |  | 43638.4792 | 71 | 65
2019-06-22 12:00 | 42 | 39 |  |  | 43638.5 | 70 | 63
2019-06-22 12:30 | 43 | 38 |  |  | 43638.5208 | 69 | 62
2019-06-22 13:00 | 41 | 36 |  |  | 43638.5417 | 67 | 60
2019-06-22 13:30 | 42 | 37 |  |  | 43638.5625 | 68 | 61
2019-06-22 14:00 | 42 | 37 |  |  | 43638.5833 | 69 | 62
2019-06-22 14:30 | 44 | 39 |  |  | 43638.6042 | 71 | 64
2019-06-22 15:00 | 46 | 42 |  |  | 43638.625 | 74 | 68
2019-06-22 15:30 | 49 | 45 |  |  | 43638.6458 | 77 | 71
2019-06-22 16:00 | 52 | 49 |  |  | 43638.6667 | 82 | 76
2019-06-22 16:30 | 56 | 53 |  |  | 43638.6875 | 86 | 81
2019-06-22 17:00 | 60 | 57 |  |  | 43638.7083 | 92 | 87
2019-06-22 17:30 | 64 | 62 |  |  | 43638.7292 | 98 | 93
2019-06-22 18:00 | 68 | 67 |  |  | 43638.75 | 102 | 98
2019-06-22 18:30 | 69 | 69 |  |  | 43638.7708 | 103 | 100
2019-06-22 19:00 | 70 | 70 |  |  | 43638.7917 | 105 | 101
2019-06-22 19:30 | 70 | 70 |  |  | 43638.8125 | 104 | 100
2019-06-22 20:00 | 71 | 67 |  |  | 43638.8333 | 103 | 97
2019-06-22 20:30 | 71 | 67 |  |  | 43638.8542 | 104 | 98
2019-06-22 21:00 | 69 | 65 |  |  | 43638.875 | 100 | 94
2019-06-22 21:30 | 67 | 62 |  |  | 43638.8958 | 98 | 91
2019-06-22 22:00 | 67 | 63 |  |  | 43638.9167 | 98 | 91
2019-06-22 22:30 | 68 | 63 |  |  | 43638.9375 | 98 | 91
2019-06-22 23:00 | 69 | 63 |  |  | 43638.9583 | 96 | 88
2019-06-22 23:30 | 66 | 60 |  |  | 43638.9792 | 93 | 84
2019-06-23 | 64 | 57 |  |  | 43639 | 90 | 80
2019-06-23 00:30 | 60 | 52 |  |  | 43639.0208 | 85 | 75
2019-06-23 01:00 | 58 | 50 |  |  | 43639.0417 | 83 | 71
2019-06-23 01:30 | 55 | 47 |  |  | 43639.0625 | 78 | 67
2019-06-23 02:00 | 53 | 44 |  |  | 43639.0833 | 75 | 64
2019-06-23 02:30 | 51 | 42 |  |  | 43639.1042 | 73 | 61
2019-06-23 03:00 | 51 | 42 |  |  | 43639.125 | 72 | 61
2019-06-23 03:30 | 50 | 42 |  |  | 43639.1458 | 72 | 60
2019-06-23 04:00 | 51 | 42 |  |  | 43639.1667 | 72 | 60
2019-06-23 04:30 | 52 | 43 |  |  | 43639.1875 | 72 | 60
2019-06-23 05:00 | 53 | 45 |  |  | 43639.2083 | 73 | 62
2019-06-23 05:30 | 54 | 46 |  |  | 43639.2292 | 75 | 64
2019-06-23 06:00 | 56 | 49 |  |  | 43639.25 | 78 | 68
2019-06-23 06:30 | 56 | 49 |  |  | 43639.2708 | 80 | 70
2019-06-23 07:00 | 57 | 50 |  |  | 43639.2917 | 84 | 74
2019-06-23 07:30 | 57 | 52 |  |  | 43639.3125 | 84 | 76
2019-06-23 08:00 | 58 | 53 |  |  | 43639.3333 | 86 | 78
2019-06-23 08:30 | 58 | 54 |  |  | 43639.3542 | 86 | 80
2019-06-23 09:00 | 56 | 52 |  |  | 43639.375 | 86 | 80
2019-06-23 09:30 | 55 | 51 |  |  | 43639.3958 | 85 | 79
2019-06-23 10:00 | 54 | 49 |  |  | 43639.4167 | 82 | 76
2019-06-23 10:30 | 54 | 49 |  |  | 43639.4375 | 79 | 73
2019-06-23 11:00 | 52 | 46 |  |  | 43639.4583 | 77 | 70
2019-06-23 11:30 | 48 | 41 |  |  | 43639.4792 | 72 | 64
2019-06-23 12:00 | 45 | 39 |  |  | 43639.5 | 70 | 61
2019-06-23 12:30 | 45 | 37 |  |  | 43639.5208 | 69 | 60
2019-06-23 13:00 | 46 | 38 |  |  | 43639.5417 | 70 | 61
2019-06-23 13:30 | 49 | 42 |  |  | 43639.5625 | 73 | 65
2019-06-23 14:00 | 51 | 44 |  |  | 43639.5833 | 77 | 69
2019-06-23 14:30 | 55 | 49 |  |  | 43639.6042 | 81 | 73
2019-06-23 15:00 | 57 | 52 |  |  | 43639.625 | 83 | 76
2019-06-23 15:30 | 59 | 54 |  |  | 43639.6458 | 85 | 78
2019-06-23 16:00 | 60 | 56 |  |  | 43639.6667 | 87 | 81
2019-06-23 16:30 | 63 | 59 |  |  | 43639.6875 | 90 | 84
2019-06-23 17:00 | 67 | 63 |  |  | 43639.7083 | 96 | 90
2019-06-23 17:30 | 74 | 71 |  |  | 43639.7292 | 105 | 99
2019-06-23 18:00 | 76 | 75 |  |  | 43639.75 | 109 | 106
2019-06-23 18:30 | 76 | 76 |  |  | 43639.7708 | 109 | 106
2019-06-23 19:00 | 75 | 75 |  |  | 43639.7917 | 110 | 107
2019-06-23 19:30 | 74 | 74 |  |  | 43639.8125 | 109 | 106
2019-06-23 20:00 | 74 | 74 |  |  | 43639.8333 | 108 | 105
2019-06-23 20:30 | 74 | 73 |  |  | 43639.8542 | 108 | 105
2019-06-23 21:00 | 71 | 71 |  |  | 43639.875 | 104 | 101
2019-06-23 21:30 | 69 | 68 |  |  | 43639.8958 | 101 | 97
2019-06-23 22:00 | 67 | 67 |  |  | 43639.9167 | 100 | 95
2019-06-23 22:30 | 67 | 67 |  |  | 43639.9375 | 99 | 95
2019-06-23 23:00 | 65 | 64 |  |  | 43639.9583 | 95 | 89
2019-06-23 23:30 | 62 | 61 |  |  | 43639.9792 | 91 | 85
2019-06-24 | 60 | 58 |  |  | 43640 | 87 | 81
2019-06-24 00:30 | 57 | 55 |  |  | 43640.0208 | 84 | 77
2019-06-24 01:00 | 52 | 50 |  |  | 43640.0417 | 78 | 71
2019-06-24 01:30 | 48 | 46 |  |  | 43640.0625 | 73 | 67
2019-06-24 02:00 | 46 | 44 |  |  | 43640.0833 | 71 | 64
2019-06-24 02:30 | 46 | 44 |  |  | 43640.1042 | 70 | 63
2019-06-24 03:00 | 45 | 43 |  |  | 43640.125 | 70 | 63
2019-06-24 03:30 | 45 | 44 |  |  | 43640.1458 | 70 | 63
2019-06-24 04:00 | 46 | 45 |  |  | 43640.1667 | 71 | 64
2019-06-24 04:30 | 48 | 47 |  |  | 43640.1875 | 72 | 65
2019-06-24 05:00 | 51 | 50 |  |  | 43640.2083 | 76 | 70
2019-06-24 05:30 | 57 | 56 |  |  | 43640.2292 | 82 | 77
2019-06-24 06:00 | 67 | 66 |  |  | 43640.25 | 91 | 88
2019-06-24 06:30 | 76 | 76 |  |  | 43640.2708 | 105 | 102
2019-06-24 07:00 | 82 | 82 |  |  | 43640.2917 | 117 | 115
2019-06-24 07:30 | 89 | 89 |  |  | 43640.3125 | 129 | 127
2019-06-24 08:00 | 86 | 86 |  |  | 43640.3333 | 131 | 125
2019-06-24 08:30 | 80 | 80 |  |  | 43640.3542 | 125 | 119
2019-06-24 09:00 | 74 | 74 |  |  | 43640.375 | 118 | 112
2019-06-24 09:30 | 68 | 67 |  |  | 43640.3958 | 111 | 105
2019-06-24 10:00 | 64 | 63 |  |  | 43640.4167 | 107 | 100
2019-06-24 10:30 | 62 | 61 |  |  | 43640.4375 | 103 | 96
2019-06-24 11:00 | 58 | 57 |  |  | 43640.4583 | 100 | 93
2019-06-24 11:30 | 58 | 57 |  |  | 43640.4792 | 98 | 91
2019-06-24 12:00 | 57 | 56 |  |  | 43640.5 | 96 | 89
2019-06-24 12:30 | 57 | 56 |  |  | 43640.5208 | 96 | 88
2019-06-24 13:00 | 56 | 55 |  |  | 43640.5417 | 95 | 87
2019-06-24 13:30 | 60 | 59 |  |  | 43640.5625 | 98 | 91
2019-06-24 14:00 | 61 | 60 |  |  | 43640.5833 | 98 | 91
2019-06-24 14:30 | 62 | 61 |  |  | 43640.6042 | 99 | 92
2019-06-24 15:00 | 65 | 64 |  |  | 43640.625 | 103 | 96
2019-06-24 15:30 | 69 | 68 |  |  | 43640.6458 | 107 | 100
2019-06-24 16:00 | 74 | 73 |  |  | 43640.6667 | 113 | 107
2019-06-24 16:30 | 79 | 78 |  |  | 43640.6875 | 116 | 109
2019-06-24 17:00 | 82 | 81 |  |  | 43640.7083 | 121 | 114
2019-06-24 17:30 | 91 | 89 |  |  | 43640.7292 | 129 | 122
2019-06-24 18:00 | 95 | 93 |  |  | 43640.75 | 133 | 125
2019-06-24 18:30 | 94 | 92 |  |  | 43640.7708 | 132 | 124
2019-06-24 19:00 | 95 | 93 |  |  | 43640.7917 | 133 | 125
2019-06-24 19:30 | 94 | 92 |  |  | 43640.8125 | 131 | 122
2019-06-24 20:00 | 91 | 90 |  |  | 43640.8333 | 129 | 120
2019-06-24 20:30 | 89 | 87 |  |  | 43640.8542 | 128 | 119
2019-06-24 21:00 | 86 | 85 |  |  | 43640.875 | 124 | 115
2019-06-24 21:30 | 82 | 80 |  |  | 43640.8958 | 118 | 109
2019-06-24 22:00 | 80 | 78 |  |  | 43640.9167 | 117 | 107
2019-06-24 22:30 | 75 | 72 |  |  | 43640.9375 | 112 | 101
2019-06-24 23:00 | 70 | 68 |  |  | 43640.9583 | 104 | 93
2019-06-24 23:30 | 66 | 65 |  |  | 43640.9792 | 95 | 89
2019-06-25 | 60 | 59 |  |  | 43641 | 88 | 83
2019-06-25 00:30 | 56 | 54 |  |  | 43641.0208 | 83 | 76
2019-06-25 01:00 | 52 | 51 |  |  | 43641.0417 | 77 | 71
2019-06-25 01:30 | 48 | 47 |  |  | 43641.0625 | 74 | 67
2019-06-25 02:00 | 46 | 45 |  |  | 43641.0833 | 71 | 65
2019-06-25 02:30 | 46 | 44 |  |  | 43641.1042 | 71 | 64
2019-06-25 03:00 | 46 | 45 |  |  | 43641.125 | 70 | 63
2019-06-25 03:30 | 46 | 46 |  |  | 43641.1458 | 69 | 65
2019-06-25 04:00 | 47 | 46 |  |  | 43641.1667 | 69 | 64
2019-06-25 04:30 | 48 | 48 |  |  | 43641.1875 | 71 | 66
2019-06-25 05:00 | 54 | 53 |  |  | 43641.2083 | 75 | 71
2019-06-25 05:30 | 61 | 61 |  |  | 43641.2292 | 82 | 79
2019-06-25 06:00 | 69 | 69 |  |  | 43641.25 | 91 | 89
2019-06-25 06:30 | 76 | 76 |  |  | 43641.2708 | 104 | 103
2019-06-25 07:00 | 83 | 83 |  |  | 43641.2917 | 117 | 116
2019-06-25 07:30 | 89 | 89 |  |  | 43641.3125 | 130 | 126
2019-06-25 08:00 | 86 | 86 |  |  | 43641.3333 | 128 | 125
2019-06-25 08:30 | 81 | 81 |  |  | 43641.3542 | 123 | 120
2019-06-25 09:00 | 77 | 77 |  |  | 43641.375 | 119 | 116
2019-06-25 09:30 | 74 | 74 |  |  | 43641.3958 | 115 | 112
2019-06-25 10:00 | 67 | 66 |  |  | 43641.4167 | 110 | 106
2019-06-25 10:30 | 67 | 66 |  |  | 43641.4375 | 107 | 103
2019-06-25 11:00 | 66 | 65 |  |  | 43641.4583 | 106 | 102
2019-06-25 11:30 | 65 | 65 |  |  | 43641.4792 | 110 | 106
2019-06-25 12:00 | 67 | 66 |  |  | 43641.5 | 106 | 101
2019-06-25 12:30 | 70 | 70 |  |  | 43641.5208 | 107 | 102
2019-06-25 13:00 | 69 | 68 |  |  | 43641.5417 | 107 | 103
2019-06-25 13:30 | 70 | 70 |  |  | 43641.5625 | 109 | 105
2019-06-25 14:00 | 69 | 69 |  |  | 43641.5833 | 106 | 102
2019-06-25 14:30 | 70 | 70 |  |  | 43641.6042 | 108 | 103
2019-06-25 15:00 | 69 | 69 |  |  | 43641.625 | 108 | 104
2019-06-25 15:30 | 72 | 71 |  |  | 43641.6458 | 109 | 105
2019-06-25 16:00 | 78 | 78 |  |  | 43641.6667 | 117 | 112
2019-06-25 16:30 | 80 | 80 |  |  | 43641.6875 | 119 | 115
2019-06-25 17:00 | 85 | 84 |  |  | 43641.7083 | 124 | 119
2019-06-25 17:30 | 90 | 90 |  |  | 43641.7292 | 129 | 124
2019-06-25 18:00 | 90 | 90 |  |  | 43641.75 | 130 | 125
2019-06-25 18:30 | 88 | 87 |  |  | 43641.7708 | 127 | 121
2019-06-25 19:00 | 89 | 88 |  |  | 43641.7917 | 128 | 121
2019-06-25 19:30 | 87 | 87 |  |  | 43641.8125 | 125 | 118
2019-06-25 20:00 | 87 | 86 |  |  | 43641.8333 | 124 | 117
2019-06-25 20:30 | 86 | 86 |  |  | 43641.8542 | 123 | 116
2019-06-25 21:00 | 83 | 82 |  |  | 43641.875 | 119 | 111
2019-06-25 21:30 | 78 | 77 |  |  | 43641.8958 | 114 | 105
2019-06-25 22:00 | 79 | 78 |  |  | 43641.9167 | 113 | 105
2019-06-25 22:30 | 74 | 73 |  |  | 43641.9375 | 110 | 102
2019-06-25 23:00 | 71 | 69 |  |  | 43641.9583 | 104 | 95
2019-06-25 23:30 | 64 | 63 |  |  | 43641.9792 | 95 | 89
2019-06-26 | 56 | 56 |  |  | 43642 | 85 | 81
2019-06-26 00:30 | 53 | 53 |  |  | 43642.0208 | 80 | 76
2019-06-26 01:00 | 51 | 51 |  |  | 43642.0417 | 76 | 71
2019-06-26 01:30 | 48 | 48 |  |  | 43642.0625 | 73 | 68
2019-06-26 02:00 | 47 | 46 |  |  | 43642.0833 | 71 | 65
2019-06-26 02:30 | 46 | 46 |  |  | 43642.1042 | 69 | 64
2019-06-26 03:00 | 46 | 46 |  |  | 43642.125 | 68 | 64
2019-06-26 03:30 | 46 | 46 |  |  | 43642.1458 | 67 | 64
2019-06-26 04:00 | 47 | 47 |  |  | 43642.1667 | 68 | 65
2019-06-26 04:30 | 48 | 48 |  |  | 43642.1875 | 70 | 66
2019-06-26 05:00 | 53 | 52 |  |  | 43642.2083 | 74 | 71
2019-06-26 05:30 | 59 | 58 |  |  | 43642.2292 | 80 | 77
2019-06-26 06:00 | 66 | 66 |  |  | 43642.25 | 88 | 87
2019-06-26 06:30 | 75 | 75 |  |  | 43642.2708 | 102 | 100
2019-06-26 07:00 | 82 | 82 |  |  | 43642.2917 | 113 | 112
2019-06-26 07:30 | 90 | 90 |  |  | 43642.3125 | 126 | 125
2019-06-26 08:00 | 90 | 90 |  |  | 43642.3333 | 129 | 128
2019-06-26 08:30 | 91 | 91 |  |  | 43642.3542 | 131 | 131
2019-06-26 09:00 | 85 | 85 |  |  | 43642.375 | 124 | 123
2019-06-26 09:30 | 84 | 84 |  |  | 43642.3958 | 125 | 124
2019-06-26 10:00 | 81 | 81 |  |  | 43642.4167 | 124 | 123
2019-06-26 10:30 | 79 | 79 |  |  | 43642.4375 | 123 | 122
2019-06-26 11:00 | 85 | 85 |  |  | 43642.4583 | 125 | 124
2019-06-26 11:30 | 88 | 88 |  |  | 43642.4792 | 128 | 127
2019-06-26 12:00 | 92 | 92 |  |  | 43642.5 | 130 | 129
2019-06-26 12:30 | 91 | 91 |  |  | 43642.5208 | 127 | 126
2019-06-26 13:00 | 90 | 90 |  |  | 43642.5417 | 124 | 123
2019-06-26 13:30 | 91 | 91 |  |  | 43642.5625 | 126 | 125
2019-06-26 14:00 | 91 | 91 |  |  | 43642.5833 | 126 | 124
2019-06-26 14:30 | 91 | 91 |  |  | 43642.6042 | 126 | 125
2019-06-26 15:00 | 90 | 90 |  |  | 43642.625 | 126 | 124
2019-06-26 15:30 | 90 | 89 |  |  | 43642.6458 | 124 | 122
2019-06-26 16:00 | 94 | 94 |  |  | 43642.6667 | 128 | 126
2019-06-26 16:30 | 95 | 95 |  |  | 43642.6875 | 129 | 128
2019-06-26 17:00 | 97 | 97 |  |  | 43642.7083 | 133 | 131
2019-06-26 17:30 | 98 | 98 |  |  | 43642.7292 | 136 | 132
2019-06-26 18:00 | 99 | 99 |  |  | 43642.75 | 137 | 132
2019-06-26 18:30 | 98 | 98 |  |  | 43642.7708 | 134 | 129
2019-06-26 19:00 | 98 | 97 |  |  | 43642.7917 | 133 | 128
2019-06-26 19:30 | 96 | 96 |  |  | 43642.8125 | 131 | 126
2019-06-26 20:00 | 96 | 95 |  |  | 43642.8333 | 130 | 123
2019-06-26 20:30 | 96 | 95 |  |  | 43642.8542 | 129 | 122
2019-06-26 21:00 | 93 | 91 |  |  | 43642.875 | 125 | 118
2019-06-26 21:30 | 88 | 87 |  |  | 43642.8958 | 119 | 111
2019-06-26 22:00 | 85 | 83 |  |  | 43642.9167 | 116 | 109
2019-06-26 22:30 | 81 | 79 |  |  | 43642.9375 | 113 | 105
2019-06-26 23:00 | 77 | 75 |  |  | 43642.9583 | 108 | 98
2019-06-26 23:30 | 73 | 71 |  |  | 43642.9792 | 102 | 93
2019-06-27 | 66 | 65 |  |  | 43643 | 92 | 86
2019-06-27 00:30 | 59 | 58 |  |  | 43643.0208 | 85 | 78
2019-06-27 01:00 | 54 | 53 |  |  | 43643.0417 | 80 | 72
2019-06-27 01:30 | 51 | 50 |  |  | 43643.0625 | 77 | 69
2019-06-27 02:00 | 51 | 49 |  |  | 43643.0833 | 76 | 66
2019-06-27 02:30 | 51 | 49 |  |  | 43643.1042 | 74 | 64
2019-06-27 03:00 | 52 | 50 |  |  | 43643.125 | 74 | 64
2019-06-27 03:30 | 53 | 51 |  |  | 43643.1458 | 75 | 65
2019-06-27 04:00 | 53 | 51 |  |  | 43643.1667 | 75 | 65
2019-06-27 04:30 | 56 | 54 |  |  | 43643.1875 | 77 | 68
2019-06-27 05:00 | 59 | 57 |  |  | 43643.2083 | 81 | 72
2019-06-27 05:30 | 64 | 63 |  |  | 43643.2292 | 85 | 78
2019-06-27 06:00 | 71 | 71 |  |  | 43643.25 | 93 | 88
2019-06-27 06:30 | 78 | 78 |  |  | 43643.2708 | 103 | 101
2019-06-27 07:00 | 86 | 86 |  |  | 43643.2917 | 117 | 114
2019-06-27 07:30 | 89 | 89 |  |  | 43643.3125 | 125 | 122
2019-06-27 08:00 | 89 | 89 |  |  | 43643.3333 | 126 | 124
2019-06-27 08:30 | 86 | 86 |  |  | 43643.3542 | 125 | 122
2019-06-27 09:00 | 80 | 80 |  |  | 43643.375 | 119 | 117
2019-06-27 09:30 | 73 | 73 |  |  | 43643.3958 | 113 | 111
2019-06-27 10:00 | 69 | 69 |  |  | 43643.4167 | 106 | 105
2019-06-27 10:30 | 70 | 69 |  |  | 43643.4375 | 101 | 100
2019-06-27 11:00 | 69 | 69 |  |  | 43643.4583 | 103 | 102
2019-06-27 11:30 | 67 | 67 |  |  | 43643.4792 | 102 | 101
2019-06-27 12:00 | 64 | 64 |  |  | 43643.5 | 94 | 92
2019-06-27 12:30 | 65 | 65 |  |  | 43643.5208 | 98 | 96
2019-06-27 13:00 | 67 | 67 |  |  | 43643.5417 | 98 | 96
2019-06-27 13:30 | 70 | 70 |  |  | 43643.5625 | 100 | 98
2019-06-27 14:00 | 70 | 70 |  |  | 43643.5833 | 106 | 104
2019-06-27 14:30 | 76 | 76 |  |  | 43643.6042 | 109 | 108
2019-06-27 15:00 | 76 | 76 |  |  | 43643.625 | 108 | 106
2019-06-27 15:30 | 82 | 82 |  |  | 43643.6458 | 112 | 110
2019-06-27 16:00 | 83 | 83 |  |  | 43643.6667 | 116 | 114
2019-06-27 16:30 | 83 | 83 |  |  | 43643.6875 | 116 | 113
2019-06-27 17:00 | 85 | 84 |  |  | 43643.7083 | 118 | 115
2019-06-27 17:30 | 88 | 87 |  |  | 43643.7292 | 120 | 119
2019-06-27 18:00 | 92 | 91 |  |  | 43643.75 | 123 | 122
2019-06-27 18:30 | 92 | 90 |  |  | 43643.7708 | 123 | 120
2019-06-27 19:00 | 92 | 90 |  |  | 43643.7917 | 124 | 121
2019-06-27 19:30 | 90 | 88 |  |  | 43643.8125 | 121 | 118
2019-06-27 20:00 | 89 | 87 |  |  | 43643.8333 | 120 | 117
2019-06-27 20:30 | 89 | 87 |  |  | 43643.8542 | 120 | 117
2019-06-27 21:00 | 86 | 84 |  |  | 43643.875 | 115 | 112
2019-06-27 21:30 | 82 | 80 |  |  | 43643.8958 | 108 | 107
2019-06-27 22:00 | 81 | 79 |  |  | 43643.9167 | 107 | 105
2019-06-27 22:30 | 80 | 77 |  |  | 43643.9375 | 104 | 102
2019-06-27 23:00 | 79 | 76 |  |  | 43643.9583 | 100 | 97
2019-06-27 23:30 | 75 | 71 |  |  | 43643.9792 | 95 | 92
2019-06-28 | 71 | 67 |  |  | 43644 | 90 | 88
2019-06-28 00:30 | 67 | 63 |  |  | 43644.0208 | 84 | 82
2019-06-28 01:00 | 62 | 57 |  |  | 43644.0417 | 78 | 76
2019-06-28 01:30 | 59 | 54 |  |  | 43644.0625 | 76 | 73
2019-06-28 02:00 | 58 | 52 |  |  | 43644.0833 | 73 | 70
2019-06-28 02:30 | 55 | 52 |  |  | 43644.1042 | 75 | 69
2019-06-28 03:00 | 53 | 51 |  |  | 43644.125 | 76 | 69
2019-06-28 03:30 | 53 | 51 |  |  | 43644.1458 | 76 | 69
2019-06-28 04:00 | 53 | 51 |  |  | 43644.1667 | 76 | 69
2019-06-28 04:30 | 54 | 52 |  |  | 43644.1875 | 77 | 70
2019-06-28 05:00 | 57 | 55 |  |  | 43644.2083 | 80 | 74
2019-06-28 05:30 | 62 | 61 |  |  | 43644.2292 | 85 | 80
2019-06-28 06:00 | 69 | 68 |  |  | 43644.25 | 93 | 88
2019-06-28 06:30 | 75 | 75 |  |  | 43644.2708 | 104 | 101
2019-06-28 07:00 | 81 | 80 |  |  | 43644.2917 | 114 | 111
2019-06-28 07:30 | 89 | 89 |  |  | 43644.3125 | 124 | 122
2019-06-28 08:00 | 87 | 87 |  |  | 43644.3333 | 125 | 122
2019-06-28 08:30 | 83 | 82 |  |  | 43644.3542 | 122 | 120
2019-06-28 09:00 | 82 | 82 |  |  | 43644.375 | 122 | 120
2019-06-28 09:30 | 83 | 83 |  |  | 43644.3958 | 118 | 116
2019-06-28 10:00 | 72 | 71 |  |  | 43644.4167 | 106 | 104
2019-06-28 10:30 | 69 | 69 |  |  | 43644.4375 | 105 | 104
2019-06-28 11:00 | 71 | 71 |  |  | 43644.4583 | 108 | 106
2019-06-28 11:30 | 74 | 74 |  |  | 43644.4792 | 109 | 107
2019-06-28 12:00 | 62 | 62 |  |  | 43644.5 | 96 | 95
2019-06-28 12:30 | 62 | 62 |  |  | 43644.5208 | 99 | 97
2019-06-28 13:00 | 63 | 63 |  |  | 43644.5417 | 99 | 97
2019-06-28 13:30 | 65 | 65 |  |  | 43644.5625 | 102 | 100
2019-06-28 14:00 | 73 | 73 |  |  | 43644.5833 | 107 | 105
2019-06-28 14:30 | 70 | 70 |  |  | 43644.6042 | 100 | 98
2019-06-28 15:00 | 72 | 72 |  |  | 43644.625 | 102 | 100
2019-06-28 15:30 | 76 | 75 |  |  | 43644.6458 | 100 | 99
2019-06-28 16:00 | 75 | 74 |  |  | 43644.6667 | 102 | 100
2019-06-28 16:30 | 75 | 75 |  |  | 43644.6875 | 104 | 102
2019-06-28 17:00 | 76 | 76 |  |  | 43644.7083 | 106 | 104
2019-06-28 17:30 | 78 | 78 |  |  | 43644.7292 | 106 | 104
2019-06-28 18:00 | 79 | 78 |  |  | 43644.75 | 111 | 103
2019-06-28 18:30 | 77 | 75 |  |  | 43644.7708 | 110 | 100
2019-06-28 19:00 | 79 | 76 |  |  | 43644.7917 | 111 | 101
2019-06-28 19:30 | 78 | 76 |  |  | 43644.8125 | 109 | 101
2019-06-28 20:00 | 78 | 76 |  |  | 43644.8333 | 108 | 100
2019-06-28 20:30 | 77 | 76 |  |  | 43644.8542 | 106 | 99
2019-06-28 21:00 | 75 | 73 |  |  | 43644.875 | 103 | 96
2019-06-28 21:30 | 72 | 71 |  |  | 43644.8958 | 99 | 93
2019-06-28 22:00 | 70 | 70 |  |  | 43644.9167 | 95 | 92
2019-06-28 22:30 | 67 | 67 |  |  | 43644.9375 | 92 | 89
2019-06-28 23:00 | 65 | 64 |  |  | 43644.9583 | 89 | 85
2019-06-28 23:30 | 61 | 61 |  |  | 43644.9792 | 86 | 81
2019-06-29 | 57 | 56 |  |  | 43645 | 81 | 76
2019-06-29 00:30 | 54 | 53 |  |  | 43645.0208 | 77 | 71
2019-06-29 01:00 | 53 | 51 |  |  | 43645.0417 | 74 | 67
2019-06-29 01:30 | 50 | 48 |  |  | 43645.0625 | 71 | 64
2019-06-29 02:00 | 47 | 45 |  |  | 43645.0833 | 68 | 61
2019-06-29 02:30 | 46 | 45 |  |  | 43645.1042 | 68 | 61
2019-06-29 03:00 | 45 | 45 |  |  | 43645.125 | 68 | 60
2019-06-29 03:30 | 50 | 45 |  |  | 43645.1458 | 68 | 60
2019-06-29 04:00 | 53 | 45 |  |  | 43645.1667 | 69 | 59
2019-06-29 04:30 | 54 | 47 |  |  | 43645.1875 | 70 | 60
2019-06-29 05:00 | 55 | 47 |  |  | 43645.2083 | 70 | 61
2019-06-29 05:30 | 55 | 48 |  |  | 43645.2292 | 72 | 62
2019-06-29 06:00 | 55 | 49 |  |  | 43645.25 | 72 | 63
2019-06-29 06:30 | 58 | 53 |  |  | 43645.2708 | 76 | 69
2019-06-29 07:00 | 61 | 56 |  |  | 43645.2917 | 80 | 73
2019-06-29 07:30 | 62 | 57 |  |  | 43645.3125 | 83 | 77
2019-06-29 08:00 | 61 | 57 |  |  | 43645.3333 | 82 | 77
2019-06-29 08:30 | 58 | 54 |  |  | 43645.3542 | 80 | 75
2019-06-29 09:00 | 55 | 51 |  |  | 43645.375 | 80 | 75
2019-06-29 09:30 | 55 | 51 |  |  | 43645.3958 | 80 | 75
2019-06-29 10:00 | 55 | 52 |  |  | 43645.4167 | 77 | 72
2019-06-29 10:30 | 51 | 47 |  |  | 43645.4375 | 74 | 70
2019-06-29 11:00 | 48 | 44 |  |  | 43645.4583 | 73 | 69
2019-06-29 11:30 | 50 | 46 |  |  | 43645.4792 | 72 | 68
2019-06-29 12:00 | 51 | 47 |  |  | 43645.5 | 74 | 69
2019-06-29 12:30 | 48 | 44 |  |  | 43645.5208 | 69 | 64
2019-06-29 13:00 | 45 | 40 |  |  | 43645.5417 | 68 | 63
2019-06-29 13:30 | 47 | 42 |  |  | 43645.5625 | 74 | 70
2019-06-29 14:00 | 51 | 46 |  |  | 43645.5833 | 77 | 73
2019-06-29 14:30 | 51 | 46 |  |  | 43645.6042 | 71 | 66
2019-06-29 15:00 | 53 | 49 |  |  | 43645.625 | 72 | 67
2019-06-29 15:30 | 56 | 52 |  |  | 43645.6458 | 78 | 73
2019-06-29 16:00 | 58 | 54 |  |  | 43645.6667 | 81 | 77
2019-06-29 16:30 | 60 | 57 |  |  | 43645.6875 | 83 | 79
2019-06-29 17:00 | 65 | 61 |  |  | 43645.7083 | 88 | 85
2019-06-29 17:30 | 69 | 65 |  |  | 43645.7292 | 93 | 87
2019-06-29 18:00 | 72 | 67 |  |  | 43645.75 | 96 | 90
2019-06-29 18:30 | 71 | 66 |  |  | 43645.7708 | 95 | 89
2019-06-29 19:00 | 73 | 69 |  |  | 43645.7917 | 97 | 91
2019-06-29 19:30 | 72 | 67 |  |  | 43645.8125 | 96 | 90
2019-06-29 20:00 | 71 | 67 |  |  | 43645.8333 | 95 | 89
2019-06-29 20:30 | 72 | 68 |  |  | 43645.8542 | 96 | 90
2019-06-29 21:00 | 69 | 65 |  |  | 43645.875 | 92 | 86
2019-06-29 21:30 | 69 | 64 |  |  | 43645.8958 | 90 | 83
2019-06-29 22:00 | 69 | 64 |  |  | 43645.9167 | 91 | 84
2019-06-29 22:30 | 68 | 62 |  |  | 43645.9375 | 90 | 83
2019-06-29 23:00 | 66 | 61 |  |  | 43645.9583 | 87 | 79
2019-06-29 23:30 | 65 | 59 |  |  | 43645.9792 | 85 | 77
2019-06-30 | 62 | 55 |  |  | 43646 | 83 | 73
2019-06-30 00:30 | 60 | 52 |  |  | 43646.0208 | 79 | 68
2019-06-30 01:00 | 58 | 50 |  |  | 43646.0417 | 76 | 65
2019-06-30 01:30 | 55 | 47 |  |  | 43646.0625 | 71 | 62
2019-06-30 02:00 | 52 | 45 |  |  | 43646.0833 | 69 | 59
2019-06-30 02:30 | 51 | 43 |  |  | 43646.1042 | 68 | 58
2019-06-30 03:00 | 49 | 42 |  |  | 43646.125 | 66 | 57
2019-06-30 03:30 | 48 | 42 |  |  | 43646.1458 | 64 | 57
2019-06-30 04:00 | 49 | 43 |  |  | 43646.1667 | 64 | 57
2019-06-30 04:30 | 50 | 44 |  |  | 43646.1875 | 64 | 57
2019-06-30 05:00 | 51 | 45 |  |  | 43646.2083 | 65 | 58
2019-06-30 05:30 | 50 | 45 |  |  | 43646.2292 | 65 | 58
2019-06-30 06:00 | 51 | 45 |  |  | 43646.25 | 67 | 60
2019-06-30 06:30 | 54 | 49 |  |  | 43646.2708 | 69 | 63
2019-06-30 07:00 | 55 | 49 |  |  | 43646.2917 | 72 | 66
2019-06-30 07:30 | 56 | 51 |  |  | 43646.3125 | 74 | 69
2019-06-30 08:00 | 54 | 49 |  |  | 43646.3333 | 73 | 68
2019-06-30 08:30 | 52 | 48 |  |  | 43646.3542 | 72 | 68
2019-06-30 09:00 | 50 | 46 |  |  | 43646.375 | 69 | 65
2019-06-30 09:30 | 48 | 42 |  |  | 43646.3958 | 68 | 62
2019-06-30 10:00 | 46 | 37 |  |  | 43646.4167 | 66 | 59
2019-06-30 10:30 | 47 | 38 |  |  | 43646.4375 | 65 | 58
2019-06-30 11:00 | 48 | 39 |  |  | 43646.4583 | 64 | 58
2019-06-30 11:30 | 46 | 37 |  |  | 43646.4792 | 63 | 56
2019-06-30 12:00 | 46 | 37 |  |  | 43646.5 | 63 | 55
2019-06-30 12:30 | 45 | 36 |  |  | 43646.5208 | 62 | 54
2019-06-30 13:00 | 46 | 37 |  |  | 43646.5417 | 62 | 54
2019-06-30 13:30 | 46 | 37 |  |  | 43646.5625 | 63 | 56
2019-06-30 14:00 | 48 | 40 |  |  | 43646.5833 | 65 | 57
2019-06-30 14:30 | 49 | 41 |  |  | 43646.6042 | 66 | 59
2019-06-30 15:00 | 50 | 41 |  |  | 43646.625 | 66 | 60
2019-06-30 15:30 | 52 | 45 |  |  | 43646.6458 | 70 | 64
2019-06-30 16:00 | 57 | 50 |  |  | 43646.6667 | 76 | 70
2019-06-30 16:30 | 64 | 54 |  |  | 43646.6875 | 77 | 76
2019-06-30 17:00 | 69 | 58 |  |  | 43646.7083 | 82 | 82
2019-06-30 17:30 | 71 | 61 |  |  | 43646.7292 | 85 | 85
2019-06-30 18:00 | 74 | 65 |  |  | 43646.75 | 90 | 90
2019-06-30 18:30 | 74 | 66 |  |  | 43646.7708 | 90 | 90
2019-06-30 19:00 | 75 | 66 |  |  | 43646.7917 | 91 | 91
2019-06-30 19:30 | 74 | 65 |  |  | 43646.8125 | 90 | 90
2019-06-30 20:00 | 72 | 63 |  |  | 43646.8333 | 88 | 88
2019-06-30 20:30 | 72 | 63 |  |  | 43646.8542 | 88 | 88
2019-06-30 21:00 | 67 | 60 |  |  | 43646.875 | 85 | 84
2019-06-30 21:30 | 65 | 59 |  |  | 43646.8958 | 85 | 80
2019-06-30 22:00 | 66 | 59 |  |  | 43646.9167 | 86 | 81
2019-06-30 22:30 | 66 | 60 |  |  | 43646.9375 | 87 | 82
2019-06-30 23:00 | 65 | 58 |  |  | 43646.9583 | 83 | 77
2019-06-30 23:30 | 61 | 53 |  |  | 43646.9792 | 79 | 72
2019-07-01 | 57 | 48 |  |  | 43647 | 74 | 67
2019-07-01 00:30 | 55 | 46 |  |  | 43647.0208 | 72 | 64
2019-07-01 01:00 | 53 | 43 |  |  | 43647.0417 | 68 | 59
2019-07-01 01:30 | 51 | 40 |  |  | 43647.0625 | 66 | 57
2019-07-01 02:00 | 50 | 40 |  |  | 43647.0833 | 62 | 54
2019-07-01 02:30 | 49 | 40 |  |  | 43647.1042 | 62 | 54
2019-07-01 03:00 | 47 | 38 |  |  | 43647.125 | 61 | 53
2019-07-01 03:30 | 47 | 38 |  |  | 43647.1458 | 61 | 53
2019-07-01 04:00 | 51 | 42 |  |  | 43647.1667 | 64 | 57
2019-07-01 04:30 | 55 | 47 |  |  | 43647.1875 | 68 | 61
2019-07-01 05:00 | 56 | 48 |  |  | 43647.2083 | 70 | 63
2019-07-01 05:30 | 59 | 52 |  |  | 43647.2292 | 74 | 68
2019-07-01 06:00 | 63 | 58 |  |  | 43647.25 | 79 | 75
2019-07-01 06:30 | 71 | 64 |  |  | 43647.2708 | 87 | 85
2019-07-01 07:00 | 78 | 67 |  |  | 43647.2917 | 96 | 93
2019-07-01 07:30 | 80 | 71 |  |  | 43647.3125 | 102 | 101
2019-07-01 08:00 | 78 | 68 |  |  | 43647.3333 | 102 | 100
2019-07-01 08:30 | 73 | 63 |  |  | 43647.3542 | 98 | 97
2019-07-01 09:00 | 70 | 60 |  |  | 43647.375 | 94 | 93
2019-07-01 09:30 | 71 | 61 |  |  | 43647.3958 | 94 | 93
2019-07-01 10:00 | 70 | 62 |  |  | 43647.4167 | 92 | 91
2019-07-01 10:30 | 70 | 59 |  |  | 43647.4375 | 91 | 89
2019-07-01 11:00 | 69 | 58 |  |  | 43647.4583 | 89 | 88
2019-07-01 11:30 | 71 | 61 |  |  | 43647.4792 | 90 | 88
2019-07-01 12:00 | 75 | 65 |  |  | 43647.5 | 94 | 93
2019-07-01 12:30 | 87 | 73 |  |  | 43647.5208 | 101 | 101
2019-07-01 13:00 | 92 | 79 |  |  | 43647.5417 | 104 | 103
2019-07-01 13:30 | 91 | 76 |  |  | 43647.5625 | 101 | 101
2019-07-01 14:00 | 88 | 72 |  |  | 43647.5833 | 96 | 95
2019-07-01 14:30 | 84 | 68 |  |  | 43647.6042 | 93 | 93
2019-07-01 15:00 | 83 | 66 |  |  | 43647.625 | 95 | 94
2019-07-01 15:30 | 85 | 69 |  |  | 43647.6458 | 98 | 97
2019-07-01 16:00 | 90 | 75 |  |  | 43647.6667 | 103 | 102
2019-07-01 16:30 | 87 | 77 |  |  | 43647.6875 | 106 | 106
2019-07-01 17:00 | 89 | 81 |  |  | 43647.7083 | 109 | 109
2019-07-01 17:30 | 92 | 84 |  |  | 43647.7292 | 110 | 110
2019-07-01 18:00 | 93 | 84 |  |  | 43647.75 | 110 | 109
2019-07-01 18:30 | 91 | 81 |  |  | 43647.7708 | 106 | 105
2019-07-01 19:00 | 91 | 80 |  |  | 43647.7917 | 106 | 105
2019-07-01 19:30 | 87 | 78 |  |  | 43647.8125 | 103 | 102
2019-07-01 20:00 | 83 | 76 |  |  | 43647.8333 | 100 | 100
2019-07-01 20:30 | 83 | 76 |  |  | 43647.8542 | 100 | 100
2019-07-01 21:00 | 80 | 73 |  |  | 43647.875 | 95 | 95
2019-07-01 21:30 | 79 | 71 |  |  | 43647.8958 | 92 | 92
2019-07-01 22:00 | 78 | 69 |  |  | 43647.9167 | 90 | 90
2019-07-01 22:30 | 77 | 67 |  |  | 43647.9375 | 89 | 88
2019-07-01 23:00 | 77 | 67 |  |  | 43647.9583 | 86 | 86
2019-07-01 23:30 | 75 | 63 |  |  | 43647.9792 | 82 | 82
2019-07-02 | 72 | 59 |  |  | 43648 | 79 | 78
2019-07-02 00:30 | 71 | 56 |  |  | 43648.0208 | 74 | 73
2019-07-02 01:00 | 68 | 53 |  |  | 43648.0417 | 70 | 68
2019-07-02 01:30 | 67 | 51 |  |  | 43648.0625 | 66 | 65
2019-07-02 02:00 | 64 | 50 |  |  | 43648.0833 | 64 | 64
2019-07-02 02:30 | 64 | 49 |  |  | 43648.1042 | 64 | 63
2019-07-02 03:00 | 63 | 48 |  |  | 43648.125 | 63 | 62
2019-07-02 03:30 | 63 | 48 |  |  | 43648.1458 | 63 | 63
2019-07-02 04:00 | 63 | 49 |  |  | 43648.1667 | 63 | 62
2019-07-02 04:30 | 66 | 52 |  |  | 43648.1875 | 67 | 66
2019-07-02 05:00 | 68 | 54 |  |  | 43648.2083 | 70 | 70
2019-07-02 05:30 | 71 | 60 |  |  | 43648.2292 | 75 | 75
2019-07-02 06:00 | 74 | 65 |  |  | 43648.25 | 82 | 81
2019-07-02 06:30 | 76 | 68 |  |  | 43648.2708 | 89 | 89
2019-07-02 07:00 | 76 | 69 |  |  | 43648.2917 | 95 | 95
2019-07-02 07:30 | 77 | 72 |  |  | 43648.3125 | 102 | 102
2019-07-02 08:00 | 77 | 72 |  |  | 43648.3333 | 105 | 104
2019-07-02 08:30 | 72 | 67 |  |  | 43648.3542 | 102 | 101
2019-07-02 09:00 | 69 | 64 |  |  | 43648.375 | 97 | 96
2019-07-02 09:30 | 70 | 64 |  |  | 43648.3958 | 97 | 96
2019-07-02 10:00 | 68 | 63 |  |  | 43648.4167 | 95 | 95
2019-07-02 10:30 | 69 | 64 |  |  | 43648.4375 | 94 | 94
2019-07-02 11:00 | 68 | 62 |  |  | 43648.4583 | 94 | 94
2019-07-02 11:30 | 67 | 62 |  |  | 43648.4792 | 93 | 92
2019-07-02 12:00 | 69 | 63 |  |  | 43648.5 | 93 | 93
2019-07-02 12:30 | 69 | 63 |  |  | 43648.5208 | 94 | 94
2019-07-02 13:00 | 72 | 66 |  |  | 43648.5417 | 97 | 96
2019-07-02 13:30 | 75 | 70 |  |  | 43648.5625 | 99 | 98
2019-07-02 14:00 | 77 | 72 |  |  | 43648.5833 | 101 | 101
2019-07-02 14:30 | 77 | 73 |  |  | 43648.6042 | 99 | 99
2019-07-02 15:00 | 75 | 70 |  |  | 43648.625 | 98 | 97
2019-07-02 15:30 | 75 | 71 |  |  | 43648.6458 | 99 | 98
2019-07-02 16:00 | 79 | 74 |  |  | 43648.6667 | 102 | 102
2019-07-02 16:30 | 84 | 78 |  |  | 43648.6875 | 104 | 104
2019-07-02 17:00 | 84 | 78 |  |  | 43648.7083 | 105 | 105
2019-07-02 17:30 | 86 | 77 |  |  | 43648.7292 | 104 | 104
2019-07-02 18:00 | 96 | 78 |  |  | 43648.75 | 107 | 106
2019-07-02 18:30 | 97 | 78 |  |  | 43648.7708 | 105 | 104
2019-07-02 19:00 | 96 | 77 |  |  | 43648.7917 | 105 | 103
2019-07-02 19:30 | 95 | 76 |  |  | 43648.8125 | 103 | 101
2019-07-02 20:00 | 93 | 74 |  |  | 43648.8333 | 101 | 99
2019-07-02 20:30 | 93 | 75 |  |  | 43648.8542 | 102 | 100
2019-07-02 21:00 | 90 | 72 |  |  | 43648.875 | 98 | 96
2019-07-02 21:30 | 87 | 68 |  |  | 43648.8958 | 93 | 91
2019-07-02 22:00 | 86 | 66 |  |  | 43648.9167 | 92 | 90
2019-07-02 22:30 | 75 | 63 |  |  | 43648.9375 | 87 | 87
2019-07-02 23:00 | 71 | 63 |  |  | 43648.9583 | 83 | 83
2019-07-02 23:30 | 70 | 60 |  |  | 43648.9792 | 80 | 79
2019-07-03 | 67 | 56 |  |  | 43649 | 75 | 74
2019-07-03 00:30 | 66 | 53 |  |  | 43649.0208 | 71 | 70
2019-07-03 01:00 | 65 | 51 |  |  | 43649.0417 | 67 | 66
2019-07-03 01:30 | 64 | 50 |  |  | 43649.0625 | 65 | 64
2019-07-03 02:00 | 61 | 47 |  |  | 43649.0833 | 62 | 61
2019-07-03 02:30 | 59 | 45 |  |  | 43649.1042 | 60 | 60
2019-07-03 03:00 | 59 | 45 |  |  | 43649.125 | 60 | 59
2019-07-03 03:30 | 59 | 45 |  |  | 43649.1458 | 60 | 59
2019-07-03 04:00 | 59 | 45 |  |  | 43649.1667 | 60 | 59
2019-07-03 04:30 | 63 | 49 |  |  | 43649.1875 | 64 | 64
2019-07-03 05:00 | 66 | 54 |  |  | 43649.2083 | 69 | 68
2019-07-03 05:30 | 69 | 59 |  |  | 43649.2292 | 73 | 73
2019-07-03 06:00 | 73 | 65 |  |  | 43649.25 | 81 | 81
2019-07-03 06:30 | 74 | 67 |  |  | 43649.2708 | 87 | 87
2019-07-03 07:00 | 75 | 69 |  |  | 43649.2917 | 95 | 95
2019-07-03 07:30 | 80 | 74 |  |  | 43649.3125 | 104 | 104
2019-07-03 08:00 | 76 | 70 |  |  | 43649.3333 | 103 | 103
2019-07-03 08:30 | 74 | 68 |  |  | 43649.3542 | 101 | 101
2019-07-03 09:00 | 73 | 67 |  |  | 43649.375 | 99 | 99
2019-07-03 09:30 | 74 | 68 |  |  | 43649.3958 | 96 | 96
2019-07-03 10:00 | 71 | 64 |  |  | 43649.4167 | 94 | 94
2019-07-03 10:30 | 70 | 63 |  |  | 43649.4375 | 92 | 92
2019-07-03 11:00 | 70 | 64 |  |  | 43649.4583 | 93 | 93
2019-07-03 11:30 | 76 | 70 |  |  | 43649.4792 | 97 | 97
2019-07-03 12:00 | 74 | 68 |  |  | 43649.5 | 95 | 95
2019-07-03 12:30 | 73 | 67 |  |  | 43649.5208 | 95 | 95
2019-07-03 13:00 | 73 | 67 |  |  | 43649.5417 | 95 | 95
2019-07-03 13:30 | 74 | 68 |  |  | 43649.5625 | 94 | 94
2019-07-03 14:00 | 75 | 69 |  |  | 43649.5833 | 93 | 93
2019-07-03 14:30 | 76 | 70 |  |  | 43649.6042 | 97 | 97
2019-07-03 15:00 | 79 | 73 |  |  | 43649.625 | 100 | 100
2019-07-03 15:30 | 81 | 74 |  |  | 43649.6458 | 99 | 99
2019-07-03 16:00 | 81 | 75 |  |  | 43649.6667 | 101 | 101
2019-07-03 16:30 | 84 | 75 |  |  | 43649.6875 | 102 | 101
2019-07-03 17:00 | 87 | 77 |  |  | 43649.7083 | 104 | 102
2019-07-03 17:30 | 90 | 79 |  |  | 43649.7292 | 105 | 104
2019-07-03 18:00 | 92 | 82 |  |  | 43649.75 | 107 | 105
2019-07-03 18:30 | 90 | 79 |  |  | 43649.7708 | 104 | 101
2019-07-03 19:00 | 91 | 80 |  |  | 43649.7917 | 104 | 102
2019-07-03 19:30 | 89 | 77 |  |  | 43649.8125 | 101 | 99
2019-07-03 20:00 | 86 | 76 |  |  | 43649.8333 | 98 | 96
2019-07-03 20:30 | 85 | 75 |  |  | 43649.8542 | 98 | 96
2019-07-03 21:00 | 82 | 74 |  |  | 43649.875 | 95 | 94
2019-07-03 21:30 | 80 | 73 |  |  | 43649.8958 | 92 | 91
2019-07-03 22:00 | 80 | 72 |  |  | 43649.9167 | 93 | 93
2019-07-03 22:30 | 79 | 71 |  |  | 43649.9375 | 92 | 92
2019-07-03 23:00 | 77 | 68 |  |  | 43649.9583 | 87 | 87
2019-07-03 23:30 | 75 | 65 |  |  | 43649.9792 | 82 | 81
2019-07-04 | 71 | 59 |  |  | 43650 | 77 | 76
2019-07-04 00:30 | 68 | 55 |  |  | 43650.0208 | 71 | 70
2019-07-04 01:00 | 66 | 52 |  |  | 43650.0417 | 67 | 66
2019-07-04 01:30 | 64 | 50 |  |  | 43650.0625 | 65 | 63
2019-07-04 02:00 | 64 | 49 |  |  | 43650.0833 | 63 | 62
2019-07-04 02:30 | 64 | 49 |  |  | 43650.1042 | 63 | 61
2019-07-04 03:00 | 64 | 48 |  |  | 43650.125 | 63 | 61
2019-07-04 03:30 | 64 | 48 |  |  | 43650.1458 | 63 | 61
2019-07-04 04:00 | 65 | 49 |  |  | 43650.1667 | 63 | 61
2019-07-04 04:30 | 66 | 51 |  |  | 43650.1875 | 65 | 63
2019-07-04 05:00 | 70 | 55 |  |  | 43650.2083 | 69 | 67
2019-07-04 05:30 | 72 | 60 |  |  | 43650.2292 | 73 | 72
2019-07-04 06:00 | 73 | 63 |  |  | 43650.25 | 78 | 77
2019-07-04 06:30 | 73 | 66 |  |  | 43650.2708 | 84 | 84
2019-07-04 07:00 | 74 | 68 |  |  | 43650.2917 | 91 | 91
2019-07-04 07:30 | 79 | 72 |  |  | 43650.3125 | 101 | 101
2019-07-04 08:00 | 77 | 71 |  |  | 43650.3333 | 102 | 102
2019-07-04 08:30 | 77 | 72 |  |  | 43650.3542 | 105 | 105
2019-07-04 09:00 | 77 | 72 |  |  | 43650.375 | 101 | 101
2019-07-04 09:30 | 74 | 68 |  |  | 43650.3958 | 94 | 93
2019-07-04 10:00 | 73 | 67 |  |  | 43650.4167 | 92 | 92
2019-07-04 10:30 | 70 | 66 |  |  | 43650.4375 | 94 | 94
2019-07-04 11:00 | 72 | 67 |  |  | 43650.4583 | 95 | 95
2019-07-04 11:30 | 72 | 67 |  |  | 43650.4792 | 90 | 90
2019-07-04 12:00 | 69 | 64 |  |  | 43650.5 | 89 | 89
2019-07-04 12:30 | 68 | 62 |  |  | 43650.5208 | 90 | 90
2019-07-04 13:00 | 70 | 64 |  |  | 43650.5417 | 86 | 85
2019-07-04 13:30 | 71 | 66 |  |  | 43650.5625 | 92 | 92
2019-07-04 14:00 | 77 | 72 |  |  | 43650.5833 | 93 | 93
2019-07-04 14:30 | 77 | 72 |  |  | 43650.6042 | 94 | 94
2019-07-04 15:00 | 81 | 76 |  |  | 43650.625 | 98 | 98
2019-07-04 15:30 | 82 | 76 |  |  | 43650.6458 | 98 | 98
2019-07-04 16:00 | 83 | 76 |  |  | 43650.6667 | 100 | 99
2019-07-04 16:30 | 83 | 75 |  |  | 43650.6875 | 100 | 100
2019-07-04 17:00 | 83 | 76 |  |  | 43650.7083 | 103 | 103
2019-07-04 17:30 | 84 | 78 |  |  | 43650.7292 | 103 | 103
2019-07-04 18:00 | 85 | 79 |  |  | 43650.75 | 103 | 103
2019-07-04 18:30 | 85 | 79 |  |  | 43650.7708 | 101 | 101
2019-07-04 19:00 | 86 | 80 |  |  | 43650.7917 | 101 | 101
2019-07-04 19:30 | 85 | 78 |  |  | 43650.8125 | 99 | 99
2019-07-04 20:00 | 85 | 78 |  |  | 43650.8333 | 98 | 97
2019-07-04 20:30 | 84 | 77 |  |  | 43650.8542 | 97 | 97
2019-07-04 21:00 | 81 | 74 |  |  | 43650.875 | 94 | 94
2019-07-04 21:30 | 78 | 71 |  |  | 43650.8958 | 89 | 89
2019-07-04 22:00 | 78 | 70 |  |  | 43650.9167 | 89 | 88
2019-07-04 22:30 | 76 | 67 |  |  | 43650.9375 | 86 | 86
2019-07-04 23:00 | 77 | 67 |  |  | 43650.9583 | 85 | 84
2019-07-04 23:30 | 74 | 63 |  |  | 43650.9792 | 81 | 80
2019-07-05 | 69 | 56 |  |  | 43651 | 75 | 74
2019-07-05 00:30 | 67 | 53 |  |  | 43651.0208 | 70 | 69
2019-07-05 01:00 | 66 | 51 |  |  | 43651.0417 | 67 | 66
2019-07-05 01:30 | 64 | 49 |  |  | 43651.0625 | 65 | 63
2019-07-05 02:00 | 64 | 49 |  |  | 43651.0833 | 65 | 63
2019-07-05 02:30 | 64 | 48 |  |  | 43651.1042 | 64 | 62
2019-07-05 03:00 | 64 | 48 |  |  | 43651.125 | 64 | 62
2019-07-05 03:30 | 65 | 49 |  |  | 43651.1458 | 65 | 63
2019-07-05 04:00 | 66 | 50 |  |  | 43651.1667 | 65 | 63
2019-07-05 04:30 | 67 | 51 |  |  | 43651.1875 | 66 | 64
2019-07-05 05:00 | 67 | 53 |  |  | 43651.2083 | 68 | 66
2019-07-05 05:30 | 69 | 56 |  |  | 43651.2292 | 71 | 70
2019-07-05 06:00 | 72 | 62 |  |  | 43651.25 | 77 | 76
2019-07-05 06:30 | 74 | 66 |  |  | 43651.2708 | 84 | 84
2019-07-05 07:00 | 82 | 68 |  |  | 43651.2917 | 96 | 92
2019-07-05 07:30 | 84 | 72 |  |  | 43651.3125 | 102 | 99
2019-07-05 08:00 | 84 | 71 |  |  | 43651.3333 | 104 | 101
2019-07-05 08:30 | 85 | 72 |  |  | 43651.3542 | 106 | 102
2019-07-05 09:00 | 85 | 72 |  |  | 43651.375 | 105 | 101
2019-07-05 09:30 | 84 | 71 |  |  | 43651.3958 | 104 | 101
2019-07-05 10:00 | 80 | 65 |  |  | 43651.4167 | 101 | 97
2019-07-05 10:30 | 81 | 66 |  |  | 43651.4375 | 97 | 93
2019-07-05 11:00 | 82 | 68 |  |  | 43651.4583 | 99 | 95
2019-07-05 11:30 | 81 | 66 |  |  | 43651.4792 | 101 | 97
2019-07-05 12:00 | 81 | 67 |  |  | 43651.5 | 97 | 93
2019-07-05 12:30 | 84 | 71 |  |  | 43651.5208 | 99 | 96
2019-07-05 13:00 | 86 | 73 |  |  | 43651.5417 | 103 | 99
2019-07-05 13:30 | 84 | 70 |  |  | 43651.5625 | 100 | 96
2019-07-05 14:00 | 84 | 68 |  |  | 43651.5833 | 97 | 92
2019-07-05 14:30 | 87 | 71 |  |  | 43651.6042 | 101 | 96
2019-07-05 15:00 | 89 | 74 |  |  | 43651.625 | 104 | 99
2019-07-05 15:30 | 91 | 76 |  |  | 43651.6458 | 107 | 102
2019-07-05 16:00 | 92 | 77 |  |  | 43651.6667 | 109 | 104
2019-07-05 16:30 | 91 | 76 |  |  | 43651.6875 | 108 | 102
2019-07-05 17:00 | 91 | 76 |  |  | 43651.7083 | 107 | 101
2019-07-05 17:30 | 92 | 76 |  |  | 43651.7292 | 108 | 102
2019-07-05 18:00 | 93 | 78 |  |  | 43651.75 | 108 | 102
2019-07-05 18:30 | 93 | 76 |  |  | 43651.7708 | 106 | 99
2019-07-05 19:00 | 93 | 76 |  |  | 43651.7917 | 105 | 98
2019-07-05 19:30 | 93 | 76 |  |  | 43651.8125 | 105 | 98
2019-07-05 20:00 | 93 | 75 |  |  | 43651.8333 | 103 | 96
2019-07-05 20:30 | 91 | 73 |  |  | 43651.8542 | 101 | 94
2019-07-05 21:00 | 86 | 70 |  |  | 43651.875 | 97 | 91
2019-07-05 21:30 | 84 | 68 |  |  | 43651.8958 | 94 | 89
2019-07-05 22:00 | 85 | 69 |  |  | 43651.9167 | 97 | 91
2019-07-05 22:30 | 79 | 69 |  |  | 43651.9375 | 91 | 90
2019-07-05 23:00 | 78 | 69 |  |  | 43651.9583 | 87 | 87
2019-07-05 23:30 | 76 | 66 |  |  | 43651.9792 | 84 | 84
2019-07-06 | 73 | 61 |  |  | 43652 | 80 | 79
2019-07-06 00:30 | 71 | 58 |  |  | 43652.0208 | 75 | 74
2019-07-06 01:00 | 69 | 55 |  |  | 43652.0417 | 71 | 70
2019-07-06 01:30 | 68 | 52 |  |  | 43652.0625 | 68 | 67
2019-07-06 02:00 | 66 | 50 |  |  | 43652.0833 | 65 | 64
2019-07-06 02:30 | 66 | 50 |  |  | 43652.1042 | 65 | 63
2019-07-06 03:00 | 65 | 48 |  |  | 43652.125 | 64 | 62
2019-07-06 03:30 | 64 | 47 |  |  | 43652.1458 | 63 | 61
2019-07-06 04:00 | 64 | 47 |  |  | 43652.1667 | 63 | 61
2019-07-06 04:30 | 66 | 49 |  |  | 43652.1875 | 64 | 62
2019-07-06 05:00 | 67 | 50 |  |  | 43652.2083 | 66 | 64
2019-07-06 05:30 | 69 | 53 |  |  | 43652.2292 | 69 | 67
2019-07-06 06:00 | 71 | 56 |  |  | 43652.25 | 72 | 70
2019-07-06 06:30 | 72 | 58 |  |  | 43652.2708 | 74 | 72
2019-07-06 07:00 | 71 | 57 |  |  | 43652.2917 | 75 | 74
2019-07-06 07:30 | 72 | 59 |  |  | 43652.3125 | 78 | 77
2019-07-06 08:00 | 72 | 59 |  |  | 43652.3333 | 80 | 79
2019-07-06 08:30 | 72 | 62 |  |  | 43652.3542 | 85 | 84
2019-07-06 09:00 | 75 | 65 |  |  | 43652.375 | 89 | 88
2019-07-06 09:30 | 76 | 67 |  |  | 43652.3958 | 91 | 90
2019-07-06 10:00 | 73 | 65 |  |  | 43652.4167 | 88 | 87
2019-07-06 10:30 | 71 | 62 |  |  | 43652.4375 | 86 | 86
2019-07-06 11:00 | 69 | 58 |  |  | 43652.4583 | 79 | 79
2019-07-06 11:30 | 70 | 59 |  |  | 43652.4792 | 79 | 79
2019-07-06 12:00 | 68 | 57 |  |  | 43652.5 | 79 | 79
2019-07-06 12:30 | 66 | 54 |  |  | 43652.5208 | 77 | 77
2019-07-06 13:00 | 70 | 59 |  |  | 43652.5417 | 78 | 78
2019-07-06 13:30 | 72 | 60 |  |  | 43652.5625 | 80 | 80
2019-07-06 14:00 | 70 | 58 |  |  | 43652.5833 | 75 | 74
2019-07-06 14:30 | 72 | 61 |  |  | 43652.6042 | 83 | 82
2019-07-06 15:00 | 72 | 61 |  |  | 43652.625 | 83 | 83
2019-07-06 15:30 | 74 | 63 |  |  | 43652.6458 | 85 | 85
2019-07-06 16:00 | 76 | 66 |  |  | 43652.6667 | 87 | 86
2019-07-06 16:30 | 75 | 66 |  |  | 43652.6875 | 85 | 85
2019-07-06 17:00 | 80 | 69 |  |  | 43652.7083 | 91 | 91
2019-07-06 17:30 | 83 | 72 |  |  | 43652.7292 | 94 | 94
2019-07-06 18:00 | 83 | 72 |  |  | 43652.75 | 94 | 94
2019-07-06 18:30 | 83 | 73 |  |  | 43652.7708 | 94 | 94
2019-07-06 19:00 | 83 | 73 |  |  | 43652.7917 | 95 | 94
2019-07-06 19:30 | 82 | 71 |  |  | 43652.8125 | 93 | 93
2019-07-06 20:00 | 79 | 71 |  |  | 43652.8333 | 92 | 92
2019-07-06 20:30 | 78 | 70 |  |  | 43652.8542 | 92 | 92
2019-07-06 21:00 | 75 | 66 |  |  | 43652.875 | 87 | 87
2019-07-06 21:30 | 74 | 65 |  |  | 43652.8958 | 85 | 85
2019-07-06 22:00 | 74 | 65 |  |  | 43652.9167 | 86 | 86
2019-07-06 22:30 | 75 | 66 |  |  | 43652.9375 | 87 | 87
2019-07-06 23:00 | 75 | 65 |  |  | 43652.9583 | 84 | 84
2019-07-06 23:30 | 73 | 62 |  |  | 43652.9792 | 82 | 82
2019-07-07 | 70 | 58 |  |  | 43653 | 77 | 76
2019-07-07 00:30 | 70 | 54 |  |  | 43653.0208 | 72 | 71
2019-07-07 01:00 | 67 | 51 |  |  | 43653.0417 | 69 | 67
2019-07-07 01:30 | 66 | 48 |  |  | 43653.0625 | 66 | 64
2019-07-07 02:00 | 65 | 47 |  |  | 43653.0833 | 63 | 61
2019-07-07 02:30 | 65 | 47 |  |  | 43653.1042 | 62 | 60
2019-07-07 03:00 | 65 | 47 |  |  | 43653.125 | 62 | 60
2019-07-07 03:30 | 64 | 46 |  |  | 43653.1458 | 62 | 59
2019-07-07 04:00 | 64 | 45 |  |  | 43653.1667 | 61 | 59
2019-07-07 04:30 | 65 | 47 |  |  | 43653.1875 | 62 | 60
2019-07-07 05:00 | 65 | 47 |  |  | 43653.2083 | 62 | 60
2019-07-07 05:30 | 65 | 47 |  |  | 43653.2292 | 63 | 61
2019-07-07 06:00 | 67 | 50 |  |  | 43653.25 | 66 | 64
2019-07-07 06:30 | 66 | 49 |  |  | 43653.2708 | 67 | 65
2019-07-07 07:00 | 67 | 51 |  |  | 43653.2917 | 70 | 68
2019-07-07 07:30 | 68 | 52 |  |  | 43653.3125 | 72 | 70
2019-07-07 08:00 | 68 | 53 |  |  | 43653.3333 | 71 | 70
2019-07-07 08:30 | 65 | 51 |  |  | 43653.3542 | 70 | 69
2019-07-07 09:00 | 62 | 48 |  |  | 43653.375 | 67 | 66
2019-07-07 09:30 | 58 | 45 |  |  | 43653.3958 | 66 | 66
2019-07-07 10:00 | 56 | 42 |  |  | 43653.4167 | 62 | 62
2019-07-07 10:30 | 56 | 42 |  |  | 43653.4375 | 63 | 63
2019-07-07 11:00 | 53 | 39 |  |  | 43653.4583 | 65 | 64
2019-07-07 11:30 | 55 | 41 |  |  | 43653.4792 | 68 | 67
2019-07-07 12:00 | 58 | 45 |  |  | 43653.5 | 70 | 69
2019-07-07 12:30 | 63 | 51 |  |  | 43653.5208 | 73 | 72
2019-07-07 13:00 | 63 | 50 |  |  | 43653.5417 | 72 | 72
2019-07-07 13:30 | 65 | 53 |  |  | 43653.5625 | 71 | 70
2019-07-07 14:00 | 68 | 56 |  |  | 43653.5833 | 72 | 72
2019-07-07 14:30 | 68 | 56 |  |  | 43653.6042 | 73 | 73
2019-07-07 15:00 | 67 | 55 |  |  | 43653.625 | 74 | 73
2019-07-07 15:30 | 66 | 54 |  |  | 43653.6458 | 73 | 72
2019-07-07 16:00 | 66 | 54 |  |  | 43653.6667 | 74 | 74
2019-07-07 16:30 | 68 | 57 |  |  | 43653.6875 | 77 | 77
2019-07-07 17:00 | 70 | 60 |  |  | 43653.7083 | 82 | 82
2019-07-07 17:30 | 73 | 64 |  |  | 43653.7292 | 87 | 86
2019-07-07 18:00 | 77 | 66 |  |  | 43653.75 | 89 | 88
2019-07-07 18:30 | 77 | 66 |  |  | 43653.7708 | 91 | 90
2019-07-07 19:00 | 77 | 67 |  |  | 43653.7917 | 91 | 90
2019-07-07 19:30 | 76 | 65 |  |  | 43653.8125 | 90 | 89
2019-07-07 20:00 | 76 | 65 |  |  | 43653.8333 | 89 | 88
2019-07-07 20:30 | 75 | 65 |  |  | 43653.8542 | 88 | 88
2019-07-07 21:00 | 73 | 63 |  |  | 43653.875 | 85 | 84
2019-07-07 21:30 | 71 | 60 |  |  | 43653.8958 | 82 | 82
2019-07-07 22:00 | 71 | 59 |  |  | 43653.9167 | 82 | 81
2019-07-07 22:30 | 71 | 59 |  |  | 43653.9375 | 83 | 82
2019-07-07 23:00 | 72 | 59 |  |  | 43653.9583 | 81 | 80
2019-07-07 23:30 | 71 | 57 |  |  | 43653.9792 | 78 | 77
2019-07-08 | 67 | 53 |  |  | 43654 | 73 | 71
2019-07-08 00:30 | 65 | 50 |  |  | 43654.0208 | 68 | 67
2019-07-08 01:00 | 63 | 47 |  |  | 43654.0417 | 64 | 63
2019-07-08 01:30 | 64 | 46 |  |  | 43654.0625 | 63 | 61
2019-07-08 02:00 | 73 | 43 |  |  | 43654.0833 | 62 | 58
2019-07-08 02:30 | 72 | 41 |  |  | 43654.1042 | 61 | 57
2019-07-08 03:00 | 71 | 42 |  |  | 43654.125 | 60 | 57
2019-07-08 03:30 | 71 | 43 |  |  | 43654.1458 | 60 | 57
2019-07-08 04:00 | 71 | 43 |  |  | 43654.1667 | 60 | 57
2019-07-08 04:30 | 71 | 44 |  |  | 43654.1875 | 62 | 59
2019-07-08 05:00 | 73 | 48 |  |  | 43654.2083 | 65 | 62
2019-07-08 05:30 | 74 | 52 |  |  | 43654.2292 | 69 | 67
2019-07-08 06:00 | 78 | 59 |  |  | 43654.25 | 75 | 74
2019-07-08 06:30 | 80 | 64 |  |  | 43654.2708 | 84 | 83
2019-07-08 07:00 | 82 | 67 |  |  | 43654.2917 | 92 | 91
2019-07-08 07:30 | 77 | 63 |  |  | 43654.3125 | 96 | 96
2019-07-08 08:00 | 59 | 44 |  |  | 43654.3333 | 88 | 88
2019-07-08 08:30 | 59 | 45 |  |  | 43654.3542 | 89 | 89
2019-07-08 09:00 | 59 | 47 |  |  | 43654.375 | 89 | 89
2019-07-08 09:30 | 60 | 49 |  |  | 43654.3958 | 89 | 89
2019-07-08 10:00 | 59 | 48 |  |  | 43654.4167 | 85 | 85
2019-07-08 10:30 | 56 | 41 |  |  | 43654.4375 | 80 | 80
2019-07-08 11:00 | 55 | 40 |  |  | 43654.4583 | 74 | 74
2019-07-08 11:30 | 57 | 41 |  |  | 43654.4792 | 79 | 79
2019-07-08 12:00 | 55 | 38 |  |  | 43654.5 | 80 | 80
2019-07-08 12:30 | 60 | 45 |  |  | 43654.5208 | 81 | 81
2019-07-08 13:00 | 63 | 50 |  |  | 43654.5417 | 88 | 88
2019-07-08 13:30 | 63 | 51 |  |  | 43654.5625 | 88 | 88
2019-07-08 14:00 | 62 | 48 |  |  | 43654.5833 | 84 | 84
2019-07-08 14:30 | 63 | 48 |  |  | 43654.6042 | 83 | 83
2019-07-08 15:00 | 65 | 52 |  |  | 43654.625 | 89 | 89
2019-07-08 15:30 | 65 | 50 |  |  | 43654.6458 | 86 | 86
2019-07-08 16:00 | 64 | 49 |  |  | 43654.6667 | 87 | 87
2019-07-08 16:30 | 64 | 49 |  |  | 43654.6875 | 87 | 86
2019-07-08 17:00 | 64 | 49 |  |  | 43654.7083 | 87 | 87
2019-07-08 17:30 | 64 | 52 |  |  | 43654.7292 | 90 | 90
2019-07-08 18:00 | 63 | 53 |  |  | 43654.75 | 92 | 92
2019-07-08 18:30 | 63 | 53 |  |  | 43654.7708 | 90 | 90
2019-07-08 19:00 | 62 | 53 |  |  | 43654.7917 | 90 | 90
2019-07-08 19:30 | 60 | 50 |  |  | 43654.8125 | 88 | 88
2019-07-08 20:00 | 59 | 49 |  |  | 43654.8333 | 86 | 86
2019-07-08 20:30 | 58 | 48 |  |  | 43654.8542 | 84 | 84
2019-07-08 21:00 | 56 | 45 |  |  | 43654.875 | 81 | 81
2019-07-08 21:30 | 55 | 43 |  |  | 43654.8958 | 77 | 76
2019-07-08 22:00 | 55 | 43 |  |  | 43654.9167 | 76 | 76
2019-07-08 22:30 | 55 | 41 |  |  | 43654.9375 | 74 | 74
2019-07-08 23:00 | 54 | 40 |  |  | 43654.9583 | 70 | 70
2019-07-08 23:30 | 53 | 38 |  |  | 43654.9792 | 67 | 67
2019-07-09 | 52 | 35 |  |  | 43655 | 63 | 62
2019-07-09 00:30 | 50 | 33 |  |  | 43655.0208 | 59 | 58
2019-07-09 01:00 | 49 | 32 |  |  | 43655.0417 | 56 | 56
2019-07-09 01:30 | 49 | 30 |  |  | 43655.0625 | 54 | 54
2019-07-09 02:00 | 49 | 29 |  |  | 43655.0833 | 52 | 52
2019-07-09 02:30 | 49 | 29 |  |  | 43655.1042 | 51 | 51
2019-07-09 03:00 | 49 | 29 |  |  | 43655.125 | 53 | 53
2019-07-09 03:30 | 49 | 29 |  |  | 43655.1458 | 53 | 53
2019-07-09 04:00 | 49 | 30 |  |  | 43655.1667 | 53 | 53
2019-07-09 04:30 | 50 | 31 |  |  | 43655.1875 | 55 | 54
2019-07-09 05:00 | 51 | 34 |  |  | 43655.2083 | 58 | 57
2019-07-09 05:30 | 52 | 37 |  |  | 43655.2292 | 61 | 61
2019-07-09 06:00 | 53 | 41 |  |  | 43655.25 | 66 | 66
2019-07-09 06:30 | 55 | 46 |  |  | 43655.2708 | 75 | 75
2019-07-09 07:00 | 55 | 47 |  |  | 43655.2917 | 83 | 83
2019-07-09 07:30 | 57 | 49 |  |  | 43655.3125 | 90 | 90
2019-07-09 08:00 | 54 | 47 |  |  | 43655.3333 | 91 | 90
2019-07-09 08:30 | 53 | 45 |  |  | 43655.3542 | 90 | 89
2019-07-09 09:00 | 53 | 45 |  |  | 43655.375 | 87 | 87
2019-07-09 09:30 | 53 | 44 |  |  | 43655.3958 | 85 | 84
2019-07-09 10:00 | 53 | 44 |  |  | 43655.4167 | 82 | 81
2019-07-09 10:30 | 52 | 43 |  |  | 43655.4375 | 79 | 78
2019-07-09 11:00 | 50 | 41 |  |  | 43655.4583 | 77 | 76
2019-07-09 11:30 | 51 | 41 |  |  | 43655.4792 | 75 | 75
2019-07-09 12:00 | 50 | 40 |  |  | 43655.5 | 75 | 74
2019-07-09 12:30 | 51 | 40 |  |  | 43655.5208 | 74 | 74
2019-07-09 13:00 | 52 | 41 |  |  | 43655.5417 | 76 | 76
2019-07-09 13:30 | 53 | 42 |  |  | 43655.5625 | 78 | 78
2019-07-09 14:00 | 54 | 44 |  |  | 43655.5833 | 80 | 80
2019-07-09 14:30 | 54 | 45 |  |  | 43655.6042 | 79 | 79
2019-07-09 15:00 | 55 | 45 |  |  | 43655.625 | 81 | 81
2019-07-09 15:30 | 54 | 44 |  |  | 43655.6458 | 81 | 80
2019-07-09 16:00 | 55 | 45 |  |  | 43655.6667 | 83 | 82
2019-07-09 16:30 | 55 | 44 |  |  | 43655.6875 | 83 | 83
2019-07-09 17:00 | 58 | 47 |  |  | 43655.7083 | 85 | 85
2019-07-09 17:30 | 62 | 49 |  |  | 43655.7292 | 87 | 87
2019-07-09 18:00 | 62 | 49 |  |  | 43655.75 | 89 | 88
2019-07-09 18:30 | 62 | 49 |  |  | 43655.7708 | 87 | 87
2019-07-09 19:00 | 62 | 49 |  |  | 43655.7917 | 87 | 87
2019-07-09 19:30 | 61 | 48 |  |  | 43655.8125 | 85 | 84
2019-07-09 20:00 | 59 | 48 |  |  | 43655.8333 | 83 | 83
2019-07-09 20:30 | 58 | 46 |  |  | 43655.8542 | 83 | 83
2019-07-09 21:00 | 56 | 45 |  |  | 43655.875 | 80 | 80
2019-07-09 21:30 | 54 | 43 |  |  | 43655.8958 | 76 | 76
2019-07-09 22:00 | 53 | 41 |  |  | 43655.9167 | 75 | 75
2019-07-09 22:30 | 52 | 38 |  |  | 43655.9375 | 72 | 72
2019-07-09 23:00 | 51 | 36 |  |  | 43655.9583 | 67 | 67
2019-07-09 23:30 | 48 | 33 |  |  | 43655.9792 | 64 | 64
2019-07-10 | 47 | 31 |  |  | 43656 | 61 | 61
2019-07-10 00:30 | 47 | 30 |  |  | 43656.0208 | 57 | 56
2019-07-10 01:00 | 46 | 29 |  |  | 43656.0417 | 54 | 54
2019-07-10 01:30 | 45 | 28 |  |  | 43656.0625 | 52 | 52
2019-07-10 02:00 | 45 | 27 |  |  | 43656.0833 | 50 | 50
2019-07-10 02:30 | 45 | 27 |  |  | 43656.1042 | 49 | 49
2019-07-10 03:00 | 46 | 28 |  |  | 43656.125 | 50 | 50
2019-07-10 03:30 | 46 | 28 |  |  | 43656.1458 | 52 | 51
2019-07-10 04:00 | 47 | 29 |  |  | 43656.1667 | 52 | 52
2019-07-10 04:30 | 48 | 31 |  |  | 43656.1875 | 53 | 53
2019-07-10 05:00 | 48 | 33 |  |  | 43656.2083 | 56 | 56
2019-07-10 05:30 | 48 | 34 |  |  | 43656.2292 | 60 | 60
2019-07-10 06:00 | 47 | 36 |  |  | 43656.25 | 64 | 64
2019-07-10 06:30 | 49 | 39 |  |  | 43656.2708 | 73 | 73
2019-07-10 07:00 | 52 | 42 |  |  | 43656.2917 | 82 | 81
2019-07-10 07:30 | 56 | 47 |  |  | 43656.3125 | 92 | 91
2019-07-10 08:00 | 60 | 48 |  |  | 43656.3333 | 94 | 94
2019-07-10 08:30 | 60 | 48 |  |  | 43656.3542 | 93 | 93
2019-07-10 09:00 | 59 | 46 |  |  | 43656.375 | 89 | 88
2019-07-10 09:30 | 58 | 45 |  |  | 43656.3958 | 86 | 85
2019-07-10 10:00 | 57 | 43 |  |  | 43656.4167 | 83 | 82
2019-07-10 10:30 | 56 | 42 |  |  | 43656.4375 | 80 | 80
2019-07-10 11:00 | 56 | 42 |  |  | 43656.4583 | 79 | 78
2019-07-10 11:30 | 55 | 41 |  |  | 43656.4792 | 77 | 77
2019-07-10 12:00 | 54 | 40 |  |  | 43656.5 | 76 | 75
2019-07-10 12:30 | 55 | 40 |  |  | 43656.5208 | 76 | 75
2019-07-10 13:00 | 55 | 40 |  |  | 43656.5417 | 76 | 75
2019-07-10 13:30 | 56 | 41 |  |  | 43656.5625 | 77 | 77
2019-07-10 14:00 | 56 | 42 |  |  | 43656.5833 | 79 | 78
2019-07-10 14:30 | 58 | 44 |  |  | 43656.6042 | 79 | 79
2019-07-10 15:00 | 59 | 46 |  |  | 43656.625 | 82 | 81
2019-07-10 15:30 | 60 | 47 |  |  | 43656.6458 | 82 | 82
2019-07-10 16:00 | 61 | 47 |  |  | 43656.6667 | 84 | 84
2019-07-10 16:30 | 61 | 47 |  |  | 43656.6875 | 86 | 85
2019-07-10 17:00 | 61 | 48 |  |  | 43656.7083 | 87 | 86
2019-07-10 17:30 | 64 | 48 |  |  | 43656.7292 | 89 | 87
2019-07-10 18:00 | 67 | 50 |  |  | 43656.75 | 91 | 88
2019-07-10 18:30 | 66 | 48 |  |  | 43656.7708 | 88 | 85
2019-07-10 19:00 | 65 | 49 |  |  | 43656.7917 | 89 | 86
2019-07-10 19:30 | 64 | 47 |  |  | 43656.8125 | 86 | 84
2019-07-10 20:00 | 64 | 47 |  |  | 43656.8333 | 85 | 82
2019-07-10 20:30 | 64 | 46 |  |  | 43656.8542 | 84 | 82
2019-07-10 21:00 | 61 | 44 |  |  | 43656.875 | 81 | 78
2019-07-10 21:30 | 58 | 42 |  |  | 43656.8958 | 77 | 75
2019-07-10 22:00 | 58 | 42 |  |  | 43656.9167 | 76 | 74
2019-07-10 22:30 | 55 | 39 |  |  | 43656.9375 | 73 | 72
2019-07-10 23:00 | 54 | 38 |  |  | 43656.9583 | 69 | 68
2019-07-10 23:30 | 51 | 36 |  |  | 43656.9792 | 65 | 65
2019-07-11 | 49 | 33 |  |  | 43657 | 61 | 61
2019-07-11 00:30 | 48 | 32 |  |  | 43657.0208 | 58 | 58
2019-07-11 01:00 | 48 | 31 |  |  | 43657.0417 | 55 | 55
2019-07-11 01:30 | 46 | 29 |  |  | 43657.0625 | 52 | 52
2019-07-11 02:00 | 46 | 29 |  |  | 43657.0833 | 51 | 51
2019-07-11 02:30 | 48 | 31 |  |  | 43657.1042 | 52 | 52
2019-07-11 03:00 | 48 | 31 |  |  | 43657.125 | 52 | 52
2019-07-11 03:30 | 49 | 33 |  |  | 43657.1458 | 53 | 53
2019-07-11 04:00 | 50 | 34 |  |  | 43657.1667 | 55 | 55
2019-07-11 04:30 | 50 | 34 |  |  | 43657.1875 | 56 | 56
2019-07-11 05:00 | 51 | 36 |  |  | 43657.2083 | 59 | 59
2019-07-11 05:30 | 52 | 39 |  |  | 43657.2292 | 62 | 62
2019-07-11 06:00 | 53 | 42 |  |  | 43657.25 | 68 | 68
2019-07-11 06:30 | 55 | 46 |  |  | 43657.2708 | 77 | 77
2019-07-11 07:00 | 57 | 47 |  |  | 43657.2917 | 84 | 84
2019-07-11 07:30 | 60 | 50 |  |  | 43657.3125 | 93 | 92
2019-07-11 08:00 | 65 | 49 |  |  | 43657.3333 | 95 | 94
2019-07-11 08:30 | 63 | 46 |  |  | 43657.3542 | 93 | 92
2019-07-11 09:00 | 63 | 46 |  |  | 43657.375 | 90 | 89
2019-07-11 09:30 | 61 | 45 |  |  | 43657.3958 | 87 | 86
2019-07-11 10:00 | 60 | 45 |  |  | 43657.4167 | 85 | 84
2019-07-11 10:30 | 59 | 43 |  |  | 43657.4375 | 82 | 80
2019-07-11 11:00 | 59 | 42 |  |  | 43657.4583 | 80 | 78
2019-07-11 11:30 | 57 | 40 |  |  | 43657.4792 | 76 | 75
2019-07-11 12:00 | 57 | 40 |  |  | 43657.5 | 75 | 74
2019-07-11 12:30 | 58 | 41 |  |  | 43657.5208 | 76 | 75
2019-07-11 13:00 | 58 | 41 |  |  | 43657.5417 | 76 | 75
2019-07-11 13:30 | 59 | 43 |  |  | 43657.5625 | 78 | 77
2019-07-11 14:00 | 59 | 42 |  |  | 43657.5833 | 80 | 79
2019-07-11 14:30 | 60 | 43 |  |  | 43657.6042 | 81 | 80
2019-07-11 15:00 | 61 | 46 |  |  | 43657.625 | 84 | 83
2019-07-11 15:30 | 62 | 47 |  |  | 43657.6458 | 86 | 85
2019-07-11 16:00 | 65 | 46 |  |  | 43657.6667 | 88 | 86
2019-07-11 16:30 | 76 | 46 |  |  | 43657.6875 | 94 | 87
2019-07-11 17:00 | 76 | 47 |  |  | 43657.7083 | 95 | 89
2019-07-11 17:30 | 79 | 46 |  |  | 43657.7292 | 92 | 88
2019-07-11 18:00 | 82 | 48 |  |  | 43657.75 | 94 | 90
2019-07-11 18:30 | 82 | 48 |  |  | 43657.7708 | 92 | 87
2019-07-11 19:00 | 80 | 49 |  |  | 43657.7917 | 92 | 89
2019-07-11 19:30 | 73 | 47 |  |  | 43657.8125 | 88 | 86
2019-07-11 20:00 | 73 | 46 |  |  | 43657.8333 | 86 | 84
2019-07-11 20:30 | 73 | 46 |  |  | 43657.8542 | 86 | 84
2019-07-11 21:00 | 70 | 44 |  |  | 43657.875 | 82 | 81
2019-07-11 21:30 | 69 | 42 |  |  | 43657.8958 | 77 | 76
2019-07-11 22:00 | 61 | 41 |  |  | 43657.9167 | 75 | 75
2019-07-11 22:30 | 48 | 40 |  |  | 43657.9375 | 74 | 72
2019-07-11 23:00 | 48 | 39 |  |  | 43657.9583 | 71 | 68
2019-07-11 23:30 | 47 | 38 |  |  | 43657.9792 | 69 | 66
2019-07-12 | 45 | 34 |  |  | 43658 | 65 | 62
2019-07-12 00:30 | 44 | 33 |  |  | 43658.0208 | 61 | 57
2019-07-12 01:00 | 42 | 31 |  |  | 43658.0417 | 58 | 54
2019-07-12 01:30 | 42 | 31 |  |  | 43658.0625 | 56 | 53
2019-07-12 02:00 | 42 | 31 |  |  | 43658.0833 | 55 | 51
2019-07-12 02:30 | 42 | 31 |  |  | 43658.1042 | 53 | 50
2019-07-12 03:00 | 39 | 30 |  |  | 43658.125 | 52 | 50
2019-07-12 03:30 | 39 | 29 |  |  | 43658.1458 | 52 | 50
2019-07-12 04:00 | 39 | 29 |  |  | 43658.1667 | 52 | 50
2019-07-12 04:30 | 39 | 29 |  |  | 43658.1875 | 53 | 51
2019-07-12 05:00 | 41 | 32 |  |  | 43658.2083 | 56 | 54
2019-07-12 05:30 | 42 | 35 |  |  | 43658.2292 | 59 | 58
2019-07-12 06:00 | 45 | 39 |  |  | 43658.25 | 65 | 65
2019-07-12 06:30 | 48 | 44 |  |  | 43658.2708 | 75 | 75
2019-07-12 07:00 | 51 | 45 |  |  | 43658.2917 | 83 | 83
2019-07-12 07:30 | 62 | 49 |  |  | 43658.3125 | 93 | 92
2019-07-12 08:00 | 63 | 48 |  |  | 43658.3333 | 93 | 92
2019-07-12 08:30 | 61 | 46 |  |  | 43658.3542 | 92 | 91
2019-07-12 09:00 | 59 | 43 |  |  | 43658.375 | 87 | 85
2019-07-12 09:30 | 58 | 40 |  |  | 43658.3958 | 81 | 80
2019-07-12 10:00 | 56 | 39 |  |  | 43658.4167 | 79 | 77
2019-07-12 10:30 | 53 | 37 |  |  | 43658.4375 | 75 | 73
2019-07-12 11:00 | 52 | 37 |  |  | 43658.4583 | 75 | 72
2019-07-12 11:30 | 52 | 35 |  |  | 43658.4792 | 73 | 70
2019-07-12 12:00 | 52 | 36 |  |  | 43658.5 | 74 | 71
2019-07-12 12:30 | 52 | 36 |  |  | 43658.5208 | 74 | 70
2019-07-12 13:00 | 52 | 36 |  |  | 43658.5417 | 73 | 70
2019-07-12 13:30 | 53 | 36 |  |  | 43658.5625 | 74 | 71
2019-07-12 14:00 | 53 | 37 |  |  | 43658.5833 | 75 | 72
2019-07-12 14:30 | 53 | 37 |  |  | 43658.6042 | 75 | 72
2019-07-12 15:00 | 53 | 38 |  |  | 43658.625 | 75 | 73
2019-07-12 15:30 | 56 | 39 |  |  | 43658.6458 | 77 | 75
2019-07-12 16:00 | 58 | 43 |  |  | 43658.6667 | 80 | 78
2019-07-12 16:30 | 73 | 43 |  |  | 43658.6875 | 88 | 81
2019-07-12 17:00 | 74 | 44 |  |  | 43658.7083 | 90 | 83
2019-07-12 17:30 | 77 | 47 |  |  | 43658.7292 | 93 | 87
2019-07-12 18:00 | 78 | 47 |  |  | 43658.75 | 91 | 86
2019-07-12 18:30 | 76 | 46 |  |  | 43658.7708 | 87 | 84
2019-07-12 19:00 | 71 | 46 |  |  | 43658.7917 | 85 | 83
2019-07-12 19:30 | 70 | 45 |  |  | 43658.8125 | 84 | 82
2019-07-12 20:00 | 70 | 44 |  |  | 43658.8333 | 82 | 80
2019-07-12 20:30 | 71 | 45 |  |  | 43658.8542 | 82 | 80
2019-07-12 21:00 | 67 | 42 |  |  | 43658.875 | 78 | 77
2019-07-12 21:30 | 47 | 39 |  |  | 43658.8958 | 73 | 71
2019-07-12 22:00 | 46 | 39 |  |  | 43658.9167 | 73 | 70
2019-07-12 22:30 | 45 | 37 |  |  | 43658.9375 | 71 | 69
2019-07-12 23:00 | 45 | 36 |  |  | 43658.9583 | 68 | 66
2019-07-12 23:30 | 43 | 33 |  |  | 43658.9792 | 65 | 62
2019-07-13 | 41 | 30 |  |  | 43659 | 61 | 58
2019-07-13 00:30 | 39 | 29 |  |  | 43659.0208 | 57 | 54
2019-07-13 01:00 | 39 | 28 |  |  | 43659.0417 | 54 | 52
2019-07-13 01:30 | 38 | 27 |  |  | 43659.0625 | 52 | 49
2019-07-13 02:00 | 38 | 27 |  |  | 43659.0833 | 51 | 48
2019-07-13 02:30 | 37 | 27 |  |  | 43659.1042 | 50 | 48
2019-07-13 03:00 | 39 | 29 |  |  | 43659.125 | 50 | 48
2019-07-13 03:30 | 39 | 29 |  |  | 43659.1458 | 50 | 48
2019-07-13 04:00 | 40 | 31 |  |  | 43659.1667 | 53 | 51
2019-07-13 04:30 | 41 | 32 |  |  | 43659.1875 | 53 | 51
2019-07-13 05:00 | 41 | 32 |  |  | 43659.2083 | 52 | 51
2019-07-13 05:30 | 42 | 33 |  |  | 43659.2292 | 55 | 54
2019-07-13 06:00 | 41 | 33 |  |  | 43659.25 | 56 | 54
2019-07-13 06:30 | 41 | 33 |  |  | 43659.2708 | 58 | 57
2019-07-13 07:00 | 40 | 31 |  |  | 43659.2917 | 59 | 58
2019-07-13 07:30 | 38 | 30 |  |  | 43659.3125 | 60 | 59
2019-07-13 08:00 | 36 | 28 |  |  | 43659.3333 | 59 | 58
2019-07-13 08:30 | 36 | 29 |  |  | 43659.3542 | 59 | 59
2019-07-13 09:00 | 36 | 28 |  |  | 43659.375 | 60 | 59
2019-07-13 09:30 | 35 | 28 |  |  | 43659.3958 | 58 | 58
2019-07-13 10:00 | 35 | 28 |  |  | 43659.4167 | 56 | 56
2019-07-13 10:30 | 36 | 28 |  |  | 43659.4375 | 55 | 55
2019-07-13 11:00 | 36 | 29 |  |  | 43659.4583 | 55 | 55
2019-07-13 11:30 | 35 | 28 |  |  | 43659.4792 | 54 | 54
2019-07-13 12:00 | 33 | 26 |  |  | 43659.5 | 51 | 51
2019-07-13 12:30 | 32 | 24 |  |  | 43659.5208 | 49 | 48
2019-07-13 13:00 | 33 | 25 |  |  | 43659.5417 | 50 | 50
2019-07-13 13:30 | 33 | 25 |  |  | 43659.5625 | 51 | 51
2019-07-13 14:00 | 35 | 27 |  |  | 43659.5833 | 53 | 52
2019-07-13 14:30 | 36 | 28 |  |  | 43659.6042 | 53 | 53
2019-07-13 15:00 | 36 | 28 |  |  | 43659.625 | 55 | 54
2019-07-13 15:30 | 37 | 29 |  |  | 43659.6458 | 57 | 56
2019-07-13 16:00 | 39 | 32 |  |  | 43659.6667 | 62 | 61
2019-07-13 16:30 | 41 | 35 |  |  | 43659.6875 | 66 | 66
2019-07-13 17:00 | 42 | 36 |  |  | 43659.7083 | 69 | 68
2019-07-13 17:30 | 43 | 38 |  |  | 43659.7292 | 72 | 71
2019-07-13 18:00 | 45 | 40 |  |  | 43659.75 | 75 | 74
2019-07-13 18:30 | 46 | 41 |  |  | 43659.7708 | 76 | 76
2019-07-13 19:00 | 47 | 41 |  |  | 43659.7917 | 76 | 75
2019-07-13 19:30 | 45 | 40 |  |  | 43659.8125 | 74 | 74
2019-07-13 20:00 | 44 | 38 |  |  | 43659.8333 | 73 | 72
2019-07-13 20:30 | 44 | 38 |  |  | 43659.8542 | 74 | 73
2019-07-13 21:00 | 43 | 37 |  |  | 43659.875 | 71 | 70
2019-07-13 21:30 | 42 | 36 |  |  | 43659.8958 | 68 | 68
2019-07-13 22:00 | 42 | 35 |  |  | 43659.9167 | 68 | 68
2019-07-13 22:30 | 41 | 34 |  |  | 43659.9375 | 67 | 67
2019-07-13 23:00 | 40 | 33 |  |  | 43659.9583 | 64 | 64
2019-07-13 23:30 | 39 | 31 |  |  | 43659.9792 | 62 | 61
2019-07-14 | 39 | 30 |  |  | 43660 | 59 | 59
2019-07-14 00:30 | 38 | 29 |  |  | 43660.0208 | 56 | 55
2019-07-14 01:00 | 38 | 28 |  |  | 43660.0417 | 54 | 53
2019-07-14 01:30 | 37 | 27 |  |  | 43660.0625 | 52 | 50
2019-07-14 02:00 | 37 | 26 |  |  | 43660.0833 | 50 | 48
2019-07-14 02:30 | 36 | 26 |  |  | 43660.1042 | 49 | 47
2019-07-14 03:00 | 38 | 28 |  |  | 43660.125 | 49 | 47
2019-07-14 03:30 | 39 | 28 |  |  | 43660.1458 | 49 | 47
2019-07-14 04:00 | 39 | 28 |  |  | 43660.1667 | 51 | 49
2019-07-14 04:30 | 38 | 29 |  |  | 43660.1875 | 52 | 51
2019-07-14 05:00 | 39 | 30 |  |  | 43660.2083 | 52 | 51
2019-07-14 05:30 | 39 | 30 |  |  | 43660.2292 | 53 | 52
2019-07-14 06:00 | 40 | 31 |  |  | 43660.25 | 55 | 54
2019-07-14 06:30 | 38 | 30 |  |  | 43660.2708 | 55 | 55
2019-07-14 07:00 | 36 | 28 |  |  | 43660.2917 | 55 | 55
2019-07-14 07:30 | 33 | 26 |  |  | 43660.3125 | 55 | 55
2019-07-14 08:00 | 32 | 25 |  |  | 43660.3333 | 55 | 55
2019-07-14 08:30 | 32 | 26 |  |  | 43660.3542 | 57 | 57
2019-07-14 09:00 | 32 | 25 |  |  | 43660.375 | 56 | 56
2019-07-14 09:30 | 32 | 25 |  |  | 43660.3958 | 56 | 56
2019-07-14 10:00 | 32 | 26 |  |  | 43660.4167 | 54 | 54
2019-07-14 10:30 | 32 | 26 |  |  | 43660.4375 | 53 | 53
2019-07-14 11:00 | 32 | 25 |  |  | 43660.4583 | 51 | 51
2019-07-14 11:30 | 31 | 23 |  |  | 43660.4792 | 48 | 48
2019-07-14 12:00 | 31 | 23 |  |  | 43660.5 | 47 | 47
2019-07-14 12:30 | 30 | 22 |  |  | 43660.5208 | 46 | 46
2019-07-14 13:00 | 30 | 22 |  |  | 43660.5417 | 45 | 45
2019-07-14 13:30 | 31 | 23 |  |  | 43660.5625 | 47 | 47
2019-07-14 14:00 | 32 | 24 |  |  | 43660.5833 | 48 | 48
2019-07-14 14:30 | 32 | 25 |  |  | 43660.6042 | 50 | 50
2019-07-14 15:00 | 35 | 28 |  |  | 43660.625 | 53 | 53
2019-07-14 15:30 | 36 | 30 |  |  | 43660.6458 | 56 | 56
2019-07-14 16:00 | 38 | 32 |  |  | 43660.6667 | 61 | 61
2019-07-14 16:30 | 41 | 34 |  |  | 43660.6875 | 65 | 65
2019-07-14 17:00 | 42 | 36 |  |  | 43660.7083 | 70 | 70
2019-07-14 17:30 | 46 | 41 |  |  | 43660.7292 | 77 | 76
2019-07-14 18:00 | 51 | 45 |  |  | 43660.75 | 84 | 83
2019-07-14 18:30 | 53 | 48 |  |  | 43660.7708 | 86 | 86
2019-07-14 19:00 | 55 | 49 |  |  | 43660.7917 | 89 | 87
2019-07-14 19:30 | 55 | 49 |  |  | 43660.8125 | 88 | 87
2019-07-14 20:00 | 54 | 49 |  |  | 43660.8333 | 87 | 85
2019-07-14 20:30 | 55 | 50 |  |  | 43660.8542 | 88 | 86
2019-07-14 21:00 | 54 | 48 |  |  | 43660.875 | 84 | 83
2019-07-14 21:30 | 52 | 45 |  |  | 43660.8958 | 80 | 79
2019-07-14 22:00 | 52 | 44 |  |  | 43660.9167 | 79 | 78
2019-07-14 22:30 | 50 | 42 |  |  | 43660.9375 | 76 | 75
2019-07-14 23:00 | 50 | 42 |  |  | 43660.9583 | 73 | 71
2019-07-14 23:30 | 48 | 40 |  |  | 43660.9792 | 70 | 68
2019-07-15 | 45 | 37 |  |  | 43661 | 66 | 64
2019-07-15 00:30 | 46 | 36 |  |  | 43661.0208 | 64 | 62
2019-07-15 01:00 | 47 | 36 |  |  | 43661.0417 | 63 | 60
2019-07-15 01:30 | 46 | 36 |  |  | 43661.0625 | 61 | 58
2019-07-15 02:00 | 44 | 35 |  |  | 43661.0833 | 59 | 57
2019-07-15 02:30 | 44 | 34 |  |  | 43661.1042 | 57 | 55
2019-07-15 03:00 | 43 | 34 |  |  | 43661.125 | 57 | 55
2019-07-15 03:30 | 44 | 34 |  |  | 43661.1458 | 57 | 56
2019-07-15 04:00 | 43 | 34 |  |  | 43661.1667 | 57 | 56
2019-07-15 04:30 | 43 | 33 |  |  | 43661.1875 | 59 | 57
2019-07-15 05:00 | 44 | 35 |  |  | 43661.2083 | 60 | 59
2019-07-15 05:30 | 47 | 39 |  |  | 43661.2292 | 64 | 63
2019-07-15 06:00 | 48 | 43 |  |  | 43661.25 | 70 | 70
2019-07-15 06:30 | 59 | 46 |  |  | 43661.2708 | 79 | 78
2019-07-15 07:00 | 65 | 53 |  |  | 43661.2917 | 91 | 91
2019-07-15 07:30 | 68 | 61 |  |  | 43661.3125 | 105 | 104
2019-07-15 08:00 | 72 | 60 |  |  | 43661.3333 | 105 | 104
2019-07-15 08:30 | 74 | 54 |  |  | 43661.3542 | 99 | 98
2019-07-15 09:00 | 67 | 49 |  |  | 43661.375 | 92 | 91
2019-07-15 09:30 | 68 | 48 |  |  | 43661.3958 | 89 | 89
2019-07-15 10:00 | 69 | 52 |  |  | 43661.4167 | 89 | 89
2019-07-15 10:30 | 66 | 51 |  |  | 43661.4375 | 87 | 87
2019-07-15 11:00 | 64 | 49 |  |  | 43661.4583 | 84 | 84
2019-07-15 11:30 | 63 | 47 |  |  | 43661.4792 | 80 | 80
2019-07-15 12:00 | 62 | 45 |  |  | 43661.5 | 79 | 79
2019-07-15 12:30 | 61 | 43 |  |  | 43661.5208 | 77 | 77
2019-07-15 13:00 | 60 | 40 |  |  | 43661.5417 | 75 | 75
2019-07-15 13:30 | 59 | 40 |  |  | 43661.5625 | 76 | 76
2019-07-15 14:00 | 55 | 38 |  |  | 43661.5833 | 73 | 73
2019-07-15 14:30 | 55 | 38 |  |  | 43661.6042 | 75 | 74
2019-07-15 15:00 | 57 | 40 |  |  | 43661.625 | 78 | 78
2019-07-15 15:30 | 59 | 43 |  |  | 43661.6458 | 80 | 80
2019-07-15 16:00 | 65 | 48 |  |  | 43661.6667 | 84 | 84
2019-07-15 16:30 | 68 | 51 |  |  | 43661.6875 | 87 | 87
2019-07-15 17:00 | 77 | 54 |  |  | 43661.7083 | 92 | 92
2019-07-15 17:30 | 85 | 56 |  |  | 43661.7292 | 99 | 97
2019-07-15 18:00 | 94 | 60 |  |  | 43661.75 | 102 | 102
2019-07-15 18:30 | 95 | 60 |  |  | 43661.7708 | 102 | 102
2019-07-15 19:00 | 97 | 62 |  |  | 43661.7917 | 103 | 103
2019-07-15 19:30 | 95 | 60 |  |  | 43661.8125 | 100 | 100
2019-07-15 20:00 | 92 | 58 |  |  | 43661.8333 | 98 | 98
2019-07-15 20:30 | 91 | 59 |  |  | 43661.8542 | 98 | 98
2019-07-15 21:00 | 87 | 55 |  |  | 43661.875 | 93 | 93
2019-07-15 21:30 | 86 | 52 |  |  | 43661.8958 | 88 | 88
2019-07-15 22:00 | 87 | 50 |  |  | 43661.9167 | 86 | 86
2019-07-15 22:30 | 96 | 45 |  |  | 43661.9375 | 80 | 79
2019-07-15 23:00 | 100 | 42 |  |  | 43661.9583 | 74 | 73
2019-07-15 23:30 | 85 | 38 |  |  | 43661.9792 | 68 | 68
2019-07-16 | 65 | 36 |  |  | 43662 | 63 | 62
2019-07-16 00:30 | 63 | 34 |  |  | 43662.0208 | 60 | 59
2019-07-16 01:00 | 64 | 33 |  |  | 43662.0417 | 57 | 56
2019-07-16 01:30 | 63 | 31 |  |  | 43662.0625 | 54 | 53
2019-07-16 02:00 | 63 | 31 |  |  | 43662.0833 | 53 | 52
2019-07-16 02:30 | 63 | 31 |  |  | 43662.1042 | 53 | 52
2019-07-16 03:00 | 63 | 31 |  |  | 43662.125 | 52 | 51
2019-07-16 03:30 | 64 | 32 |  |  | 43662.1458 | 52 | 51
2019-07-16 04:00 | 63 | 32 |  |  | 43662.1667 | 52 | 51
2019-07-16 04:30 | 63 | 32 |  |  | 43662.1875 | 53 | 52
2019-07-16 05:00 | 63 | 32 |  |  | 43662.2083 | 54 | 53
2019-07-16 05:30 | 62 | 36 |  |  | 43662.2292 | 59 | 58
2019-07-16 06:00 | 72 | 43 |  |  | 43662.25 | 67 | 67
2019-07-16 06:30 | 90 | 49 |  |  | 43662.2708 | 88 | 82
2019-07-16 07:00 | 94 | 55 |  |  | 43662.2917 | 100 | 96
2019-07-16 07:30 | 79 | 60 |  |  | 43662.3125 | 110 | 109
2019-07-16 08:00 | 62 | 56 |  |  | 43662.3333 | 107 | 107
2019-07-16 08:30 | 54 | 51 |  |  | 43662.3542 | 101 | 99
2019-07-16 09:00 | 47 | 45 |  |  | 43662.375 | 93 | 91
2019-07-16 09:30 | 41 | 38 |  |  | 43662.3958 | 85 | 84
2019-07-16 10:00 | 38 | 36 |  |  | 43662.4167 | 81 | 79
2019-07-16 10:30 | 35 | 34 |  |  | 43662.4375 | 75 | 74
2019-07-16 11:00 | 35 | 34 |  |  | 43662.4583 | 72 | 72
2019-07-16 11:30 | 34 | 34 |  |  | 43662.4792 | 71 | 71
2019-07-16 12:00 | 34 | 34 |  |  | 43662.5 | 70 | 70
2019-07-16 12:30 | 35 | 35 |  |  | 43662.5208 | 70 | 70
2019-07-16 13:00 | 37 | 37 |  |  | 43662.5417 | 71 | 70
2019-07-16 13:30 | 38 | 38 |  |  | 43662.5625 | 72 | 71
2019-07-16 14:00 | 40 | 39 |  |  | 43662.5833 | 73 | 73
2019-07-16 14:30 | 40 | 40 |  |  | 43662.6042 | 73 | 73
2019-07-16 15:00 | 42 | 42 |  |  | 43662.625 | 76 | 76
2019-07-16 15:30 | 43 | 43 |  |  | 43662.6458 | 77 | 77
2019-07-16 16:00 | 46 | 46 |  |  | 43662.6667 | 81 | 81
2019-07-16 16:30 | 49 | 48 |  |  | 43662.6875 | 85 | 85
2019-07-16 17:00 | 51 | 49 |  |  | 43662.7083 | 88 | 87
2019-07-16 17:30 | 52 | 50 |  |  | 43662.7292 | 90 | 90
2019-07-16 18:00 | 55 | 54 |  |  | 43662.75 | 94 | 94
2019-07-16 18:30 | 57 | 56 |  |  | 43662.7708 | 95 | 94
2019-07-16 19:00 | 59 | 58 |  |  | 43662.7917 | 97 | 97
2019-07-16 19:30 | 59 | 58 |  |  | 43662.8125 | 96 | 95
2019-07-16 20:00 | 59 | 58 |  |  | 43662.8333 | 94 | 94
2019-07-16 20:30 | 58 | 57 |  |  | 43662.8542 | 94 | 93
2019-07-16 21:00 | 54 | 53 |  |  | 43662.875 | 89 | 89
2019-07-16 21:30 | 52 | 51 |  |  | 43662.8958 | 85 | 84
2019-07-16 22:00 | 49 | 48 |  |  | 43662.9167 | 82 | 82
2019-07-16 22:30 | 46 | 45 |  |  | 43662.9375 | 78 | 78
2019-07-16 23:00 | 43 | 41 |  |  | 43662.9583 | 73 | 72
2019-07-16 23:30 | 42 | 38 |  |  | 43662.9792 | 69 | 67
2019-07-17 | 41 | 34 |  |  | 43663 | 64 | 61
2019-07-17 00:30 | 41 | 32 |  |  | 43663.0208 | 60 | 56
2019-07-17 01:00 | 41 | 31 |  |  | 43663.0417 | 57 | 53
2019-07-17 01:30 | 39 | 29 |  |  | 43663.0625 | 54 | 51
2019-07-17 02:00 | 39 | 29 |  |  | 43663.0833 | 52 | 49
2019-07-17 02:30 | 39 | 29 |  |  | 43663.1042 | 52 | 49
2019-07-17 03:00 | 37 | 29 |  |  | 43663.125 | 50 | 48
2019-07-17 03:30 | 38 | 29 |  |  | 43663.1458 | 51 | 49
2019-07-17 04:00 | 38 | 30 |  |  | 43663.1667 | 52 | 50
2019-07-17 04:30 | 40 | 32 |  |  | 43663.1875 | 53 | 51
2019-07-17 05:00 | 43 | 36 |  |  | 43663.2083 | 57 | 55
2019-07-17 05:30 | 45 | 39 |  |  | 43663.2292 | 62 | 61
2019-07-17 06:00 | 48 | 43 |  |  | 43663.25 | 69 | 68
2019-07-17 06:30 | 53 | 48 |  |  | 43663.2708 | 82 | 82
2019-07-17 07:00 | 57 | 54 |  |  | 43663.2917 | 96 | 95
2019-07-17 07:30 | 62 | 58 |  |  | 43663.3125 | 106 | 104
2019-07-17 08:00 | 59 | 55 |  |  | 43663.3333 | 103 | 101
2019-07-17 08:30 | 54 | 50 |  |  | 43663.3542 | 97 | 95
2019-07-17 09:00 | 50 | 45 |  |  | 43663.375 | 90 | 87
2019-07-17 09:30 | 45 | 41 |  |  | 43663.3958 | 83 | 81
2019-07-17 10:00 | 44 | 40 |  |  | 43663.4167 | 79 | 77
2019-07-17 10:30 | 42 | 39 |  |  | 43663.4375 | 75 | 74
2019-07-17 11:00 | 42 | 39 |  |  | 43663.4583 | 74 | 73
2019-07-17 11:30 | 40 | 39 |  |  | 43663.4792 | 71 | 71
2019-07-17 12:00 | 40 | 38 |  |  | 43663.5 | 71 | 71
2019-07-17 12:30 | 40 | 39 |  |  | 43663.5208 | 71 | 71
2019-07-17 13:00 | 42 | 40 |  |  | 43663.5417 | 72 | 72
2019-07-17 13:30 | 43 | 42 |  |  | 43663.5625 | 73 | 73
2019-07-17 14:00 | 45 | 44 |  |  | 43663.5833 | 76 | 76
2019-07-17 14:30 | 46 | 45 |  |  | 43663.6042 | 77 | 77
2019-07-17 15:00 | 46 | 45 |  |  | 43663.625 | 78 | 78
2019-07-17 15:30 | 47 | 46 |  |  | 43663.6458 | 80 | 80
2019-07-17 16:00 | 49 | 47 |  |  | 43663.6667 | 82 | 82
2019-07-17 16:30 | 51 | 50 |  |  | 43663.6875 | 85 | 85
2019-07-17 17:00 | 53 | 52 |  |  | 43663.7083 | 88 | 88
2019-07-17 17:30 | 56 | 53 |  |  | 43663.7292 | 90 | 89
2019-07-17 18:00 | 57 | 54 |  |  | 43663.75 | 93 | 92
2019-07-17 18:30 | 57 | 54 |  |  | 43663.7708 | 92 | 91
2019-07-17 19:00 | 60 | 56 |  |  | 43663.7917 | 93 | 92
2019-07-17 19:30 | 58 | 55 |  |  | 43663.8125 | 92 | 91
2019-07-17 20:00 | 58 | 55 |  |  | 43663.8333 | 91 | 90
2019-07-17 20:30 | 57 | 54 |  |  | 43663.8542 | 91 | 90
2019-07-17 21:00 | 56 | 53 |  |  | 43663.875 | 87 | 86
2019-07-17 21:30 | 55 | 51 |  |  | 43663.8958 | 84 | 83
2019-07-17 22:00 | 54 | 50 |  |  | 43663.9167 | 83 | 81
2019-07-17 22:30 | 50 | 47 |  |  | 43663.9375 | 80 | 79
2019-07-17 23:00 | 49 | 45 |  |  | 43663.9583 | 76 | 75
2019-07-17 23:30 | 46 | 42 |  |  | 43663.9792 | 71 | 70
2019-07-18 | 43 | 39 |  |  | 43664 | 66 | 65
2019-07-18 00:30 | 40 | 36 |  |  | 43664.0208 | 61 | 60
2019-07-18 01:00 | 38 | 34 |  |  | 43664.0417 | 58 | 57
2019-07-18 01:30 | 36 | 32 |  |  | 43664.0625 | 55 | 54
2019-07-18 02:00 | 35 | 31 |  |  | 43664.0833 | 53 | 52
2019-07-18 02:30 | 34 | 30 |  |  | 43664.1042 | 52 | 51
2019-07-18 03:00 | 34 | 30 |  |  | 43664.125 | 51 | 51
2019-07-18 03:30 | 34 | 29 |  |  | 43664.1458 | 51 | 51
2019-07-18 04:00 | 33 | 29 |  |  | 43664.1667 | 51 | 51
2019-07-18 04:30 | 34 | 29 |  |  | 43664.1875 | 52 | 51
2019-07-18 05:00 | 37 | 33 |  |  | 43664.2083 | 56 | 55
2019-07-18 05:30 | 40 | 37 |  |  | 43664.2292 | 61 | 61
2019-07-18 06:00 | 45 | 43 |  |  | 43664.25 | 69 | 69
2019-07-18 06:30 | 50 | 48 |  |  | 43664.2708 | 81 | 81
2019-07-18 07:00 | 52 | 50 |  |  | 43664.2917 | 94 | 94
2019-07-18 07:30 | 58 | 53 |  |  | 43664.3125 | 105 | 103
2019-07-18 08:00 | 58 | 50 |  |  | 43664.3333 | 106 | 103
2019-07-18 08:30 | 52 | 44 |  |  | 43664.3542 | 101 | 97
2019-07-18 09:00 | 45 | 41 |  |  | 43664.375 | 98 | 97
2019-07-18 09:30 | 40 | 39 |  |  | 43664.3958 | 89 | 89
2019-07-18 10:00 | 39 | 37 |  |  | 43664.4167 | 82 | 82
2019-07-18 10:30 | 38 | 37 |  |  | 43664.4375 | 80 | 80
2019-07-18 11:00 | 36 | 35 |  |  | 43664.4583 | 78 | 77
2019-07-18 11:30 | 34 | 33 |  |  | 43664.4792 | 75 | 75
2019-07-18 12:00 | 33 | 32 |  |  | 43664.5 | 73 | 73
2019-07-18 12:30 | 33 | 31 |  |  | 43664.5208 | 73 | 73
2019-07-18 13:00 | 35 | 33 |  |  | 43664.5417 | 74 | 74
2019-07-18 13:30 | 37 | 36 |  |  | 43664.5625 | 77 | 76
2019-07-18 14:00 | 38 | 37 |  |  | 43664.5833 | 79 | 79
2019-07-18 14:30 | 41 | 40 |  |  | 43664.6042 | 81 | 81
2019-07-18 15:00 | 46 | 45 |  |  | 43664.625 | 81 | 81
2019-07-18 15:30 | 47 | 46 |  |  | 43664.6458 | 83 | 83
2019-07-18 16:00 | 49 | 48 |  |  | 43664.6667 | 86 | 86
2019-07-18 16:30 | 49 | 48 |  |  | 43664.6875 | 86 | 86
2019-07-18 17:00 | 52 | 50 |  |  | 43664.7083 | 89 | 89
2019-07-18 17:30 | 54 | 51 |  |  | 43664.7292 | 91 | 91
2019-07-18 18:00 | 57 | 54 |  |  | 43664.75 | 95 | 94
2019-07-18 18:30 | 57 | 54 |  |  | 43664.7708 | 94 | 93
2019-07-18 19:00 | 59 | 56 |  |  | 43664.7917 | 96 | 95
2019-07-18 19:30 | 59 | 56 |  |  | 43664.8125 | 95 | 94
2019-07-18 20:00 | 60 | 57 |  |  | 43664.8333 | 95 | 94
2019-07-18 20:30 | 61 | 57 |  |  | 43664.8542 | 95 | 94
2019-07-18 21:00 | 58 | 54 |  |  | 43664.875 | 91 | 90
2019-07-18 21:30 | 55 | 52 |  |  | 43664.8958 | 86 | 85
2019-07-18 22:00 | 54 | 50 |  |  | 43664.9167 | 84 | 83
2019-07-18 22:30 | 51 | 48 |  |  | 43664.9375 | 81 | 80
2019-07-18 23:00 | 49 | 45 |  |  | 43664.9583 | 75 | 74
2019-07-18 23:30 | 46 | 41 |  |  | 43664.9792 | 71 | 69
2019-07-19 | 42 | 38 |  |  | 43665 | 67 | 66
2019-07-19 00:30 | 40 | 36 |  |  | 43665.0208 | 63 | 63
2019-07-19 01:00 | 39 | 34 |  |  | 43665.0417 | 59 | 58
2019-07-19 01:30 | 37 | 31 |  |  | 43665.0625 | 56 | 55
2019-07-19 02:00 | 35 | 29 |  |  | 43665.0833 | 54 | 52
2019-07-19 02:30 | 34 | 28 |  |  | 43665.1042 | 51 | 50
2019-07-19 03:00 | 34 | 27 |  |  | 43665.125 | 51 | 50
2019-07-19 03:30 | 34 | 28 |  |  | 43665.1458 | 52 | 50
2019-07-19 04:00 | 35 | 28 |  |  | 43665.1667 | 52 | 50
2019-07-19 04:30 | 35 | 29 |  |  | 43665.1875 | 54 | 52
2019-07-19 05:00 | 39 | 34 |  |  | 43665.2083 | 57 | 56
2019-07-19 05:30 | 43 | 39 |  |  | 43665.2292 | 63 | 62
2019-07-19 06:00 | 45 | 42 |  |  | 43665.25 | 69 | 68
2019-07-19 06:30 | 51 | 47 |  |  | 43665.2708 | 81 | 80
2019-07-19 07:00 | 55 | 53 |  |  | 43665.2917 | 94 | 94
2019-07-19 07:30 | 62 | 58 |  |  | 43665.3125 | 106 | 104
2019-07-19 08:00 | 60 | 55 |  |  | 43665.3333 | 104 | 103
2019-07-19 08:30 | 56 | 51 |  |  | 43665.3542 | 100 | 99
2019-07-19 09:00 | 50 | 46 |  |  | 43665.375 | 93 | 92
2019-07-19 09:30 | 48 | 45 |  |  | 43665.3958 | 88 | 88
2019-07-19 10:00 | 47 | 44 |  |  | 43665.4167 | 84 | 84
2019-07-19 10:30 | 47 | 43 |  |  | 43665.4375 | 81 | 80
2019-07-19 11:00 | 46 | 42 |  |  | 43665.4583 | 79 | 78
2019-07-19 11:30 | 45 | 40 |  |  | 43665.4792 | 75 | 74
2019-07-19 12:00 | 45 | 40 |  |  | 43665.5 | 74 | 73
2019-07-19 12:30 | 43 | 38 |  |  | 43665.5208 | 72 | 71
2019-07-19 13:00 | 44 | 39 |  |  | 43665.5417 | 74 | 73
2019-07-19 13:30 | 44 | 39 |  |  | 43665.5625 | 74 | 73
2019-07-19 14:00 | 45 | 41 |  |  | 43665.5833 | 75 | 74
2019-07-19 14:30 | 45 | 41 |  |  | 43665.6042 | 75 | 75
2019-07-19 15:00 | 45 | 41 |  |  | 43665.625 | 76 | 76
2019-07-19 15:30 | 47 | 43 |  |  | 43665.6458 | 78 | 78
2019-07-19 16:00 | 49 | 44 |  |  | 43665.6667 | 82 | 81
2019-07-19 16:30 | 52 | 46 |  |  | 43665.6875 | 85 | 83
2019-07-19 17:00 | 56 | 50 |  |  | 43665.7083 | 90 | 88
2019-07-19 17:30 | 48 | 41 |  |  | 43665.7292 | 72 | 70
2019-07-19 18:00 | 47 | 40 |  |  | 43665.75 | 70 | 68
2019-07-19 18:30 | 47 | 39 |  |  | 43665.7708 | 71 | 67
2019-07-19 19:00 | 48 | 40 |  |  | 43665.7917 | 71 | 68
2019-07-19 19:30 | 45 | 36 |  |  | 43665.8125 | 66 | 62
2019-07-19 20:00 | 44 | 37 |  |  | 43665.8333 | 65 | 62
2019-07-19 20:30 | 45 | 38 |  |  | 43665.8542 | 66 | 64
2019-07-19 21:00 | 41 | 36 |  |  | 43665.875 | 61 | 61
2019-07-19 21:30 | 38 | 33 |  |  | 43665.8958 | 58 | 57
2019-07-19 22:00 | 37 | 32 |  |  | 43665.9167 | 57 | 56
2019-07-19 22:30 | 35 | 31 |  |  | 43665.9375 | 55 | 55
2019-07-19 23:00 | 32 | 29 |  |  | 43665.9583 | 51 | 51
2019-07-19 23:30 | 30 | 26 |  |  | 43665.9792 | 48 | 48
2019-07-20 | 30 | 26 |  |  | 43666 | 48 | 48
2019-07-20 00:30 | 29 | 24 |  |  | 43666.0208 | 44 | 44
2019-07-20 01:00 | 27 | 22 |  |  | 43666.0417 | 41 | 41
2019-07-20 01:30 | 26 | 21 |  |  | 43666.0625 | 39 | 39
2019-07-20 02:00 | 25 | 19 |  |  | 43666.0833 | 37 | 37
2019-07-20 02:30 | 23 | 17 |  |  | 43666.1042 | 36 | 35
2019-07-20 03:00 | 24 | 19 |  |  | 43666.125 | 36 | 36
2019-07-20 03:30 | 25 | 20 |  |  | 43666.1458 | 38 | 37
2019-07-20 04:00 | 27 | 22 |  |  | 43666.1667 | 39 | 39
2019-07-20 04:30 | 27 | 22 |  |  | 43666.1875 | 40 | 40
2019-07-20 05:00 | 27 | 22 |  |  | 43666.2083 | 41 | 40
2019-07-20 05:30 | 28 | 24 |  |  | 43666.2292 | 43 | 43
2019-07-20 06:00 | 29 | 25 |  |  | 43666.25 | 44 | 44
2019-07-20 06:30 | 30 | 26 |  |  | 43666.2708 | 47 | 47
2019-07-20 07:00 | 30 | 26 |  |  | 43666.2917 | 49 | 49
2019-07-20 07:30 | 30 | 27 |  |  | 43666.3125 | 51 | 51
2019-07-20 08:00 | 27 | 24 |  |  | 43666.3333 | 47 | 47
2019-07-20 08:30 | 27 | 24 |  |  | 43666.3542 | 47 | 47
2019-07-20 09:00 | 27 | 24 |  |  | 43666.375 | 47 | 47
2019-07-20 09:30 | 28 | 25 |  |  | 43666.3958 | 47 | 47
2019-07-20 10:00 | 27 | 24 |  |  | 43666.4167 | 46 | 46
2019-07-20 10:30 | 26 | 23 |  |  | 43666.4375 | 44 | 44
2019-07-20 11:00 | 27 | 23 |  |  | 43666.4583 | 43 | 43
2019-07-20 11:30 | 25 | 21 |  |  | 43666.4792 | 41 | 41
2019-07-20 12:00 | 25 | 20 |  |  | 43666.5 | 40 | 40
2019-07-20 12:30 | 25 | 20 |  |  | 43666.5208 | 40 | 40
2019-07-20 13:00 | 24 | 20 |  |  | 43666.5417 | 39 | 39
2019-07-20 13:30 | 25 | 20 |  |  | 43666.5625 | 41 | 41
2019-07-20 14:00 | 27 | 22 |  |  | 43666.5833 | 42 | 41
2019-07-20 14:30 | 28 | 23 |  |  | 43666.6042 | 43 | 43
2019-07-20 15:00 | 29 | 25 |  |  | 43666.625 | 45 | 45
2019-07-20 15:30 | 29 | 25 |  |  | 43666.6458 | 47 | 47
2019-07-20 16:00 | 32 | 28 |  |  | 43666.6667 | 50 | 50
2019-07-20 16:30 | 35 | 32 |  |  | 43666.6875 | 55 | 55
2019-07-20 17:00 | 36 | 33 |  |  | 43666.7083 | 58 | 58
2019-07-20 17:30 | 38 | 33 |  |  | 43666.7292 | 60 | 59
2019-07-20 18:00 | 41 | 33 |  |  | 43666.75 | 65 | 62
2019-07-20 18:30 | 41 | 34 |  |  | 43666.7708 | 66 | 63
2019-07-20 19:00 | 43 | 35 |  |  | 43666.7917 | 67 | 64
2019-07-20 19:30 | 42 | 34 |  |  | 43666.8125 | 66 | 63
2019-07-20 20:00 | 41 | 34 |  |  | 43666.8333 | 65 | 62
2019-07-20 20:30 | 41 | 34 |  |  | 43666.8542 | 65 | 63
2019-07-20 21:00 | 40 | 31 |  |  | 43666.875 | 61 | 59
2019-07-20 21:30 | 38 | 30 |  |  | 43666.8958 | 60 | 57
2019-07-20 22:00 | 33 | 31 |  |  | 43666.9167 | 57 | 56
2019-07-20 22:30 | 34 | 32 |  |  | 43666.9375 | 57 | 57
2019-07-20 23:00 | 33 | 31 |  |  | 43666.9583 | 55 | 54
2019-07-20 23:30 | 32 | 29 |  |  | 43666.9792 | 52 | 52
2019-07-21 | 28 | 26 |  |  | 43667 | 46 | 46
2019-07-21 00:30 | 27 | 24 |  |  | 43667.0208 | 44 | 43
2019-07-21 01:00 | 29 | 26 |  |  | 43667.0417 | 44 | 44
2019-07-21 01:30 | 29 | 26 |  |  | 43667.0625 | 42 | 42
2019-07-21 02:00 | 27 | 24 |  |  | 43667.0833 | 40 | 40
2019-07-21 02:30 | 27 | 24 |  |  | 43667.1042 | 40 | 40
2019-07-21 03:00 | 28 | 25 |  |  | 43667.125 | 42 | 42
2019-07-21 03:30 | 29 | 25 |  |  | 43667.1458 | 42 | 42
2019-07-21 04:00 | 28 | 25 |  |  | 43667.1667 | 42 | 42
2019-07-21 04:30 | 29 | 25 |  |  | 43667.1875 | 42 | 42
2019-07-21 05:00 | 28 | 25 |  |  | 43667.2083 | 42 | 42
2019-07-21 05:30 | 28 | 25 |  |  | 43667.2292 | 44 | 43
2019-07-21 06:00 | 29 | 27 |  |  | 43667.25 | 45 | 45
2019-07-21 06:30 | 30 | 28 |  |  | 43667.2708 | 47 | 47
2019-07-21 07:00 | 29 | 27 |  |  | 43667.2917 | 49 | 48
2019-07-21 07:30 | 27 | 24 |  |  | 43667.3125 | 47 | 47
2019-07-21 08:00 | 26 | 23 |  |  | 43667.3333 | 46 | 45
2019-07-21 08:30 | 23 | 20 |  |  | 43667.3542 | 40 | 40
2019-07-21 09:00 | 22 | 19 |  |  | 43667.375 | 40 | 40
2019-07-21 09:30 | 23 | 19 |  |  | 43667.3958 | 41 | 41
2019-07-21 10:00 | 24 | 20 |  |  | 43667.4167 | 40 | 40
2019-07-21 10:30 | 25 | 21 |  |  | 43667.4375 | 40 | 40
2019-07-21 11:00 | 26 | 22 |  |  | 43667.4583 | 40 | 40
2019-07-21 11:30 | 26 | 22 |  |  | 43667.4792 | 39 | 39
2019-07-21 12:00 | 26 | 22 |  |  | 43667.5 | 39 | 39
2019-07-21 12:30 | 26 | 21 |  |  | 43667.5208 | 39 | 38
2019-07-21 13:00 | 27 | 22 |  |  | 43667.5417 | 38 | 38
2019-07-21 13:30 | 26 | 22 |  |  | 43667.5625 | 39 | 39
2019-07-21 14:00 | 27 | 23 |  |  | 43667.5833 | 41 | 41
2019-07-21 14:30 | 28 | 24 |  |  | 43667.6042 | 42 | 42
2019-07-21 15:00 | 27 | 23 |  |  | 43667.625 | 41 | 41
2019-07-21 15:30 | 29 | 25 |  |  | 43667.6458 | 45 | 45
2019-07-21 16:00 | 32 | 29 |  |  | 43667.6667 | 49 | 49
2019-07-21 16:30 | 32 | 28 |  |  | 43667.6875 | 50 | 50
2019-07-21 17:00 | 33 | 30 |  |  | 43667.7083 | 53 | 53
2019-07-21 17:30 | 35 | 31 |  |  | 43667.7292 | 56 | 56
2019-07-21 18:00 | 37 | 34 |  |  | 43667.75 | 60 | 60
2019-07-21 18:30 | 39 | 36 |  |  | 43667.7708 | 62 | 62
2019-07-21 19:00 | 39 | 36 |  |  | 43667.7917 | 64 | 64
2019-07-21 19:30 | 39 | 36 |  |  | 43667.8125 | 63 | 63
2019-07-21 20:00 | 38 | 35 |  |  | 43667.8333 | 62 | 62
2019-07-21 20:30 | 37 | 34 |  |  | 43667.8542 | 60 | 60
2019-07-21 21:00 | 35 | 32 |  |  | 43667.875 | 58 | 58
2019-07-21 21:30 | 36 | 33 |  |  | 43667.8958 | 58 | 58
2019-07-21 22:00 | 36 | 33 |  |  | 43667.9167 | 60 | 60
2019-07-21 22:30 | 36 | 33 |  |  | 43667.9375 | 58 | 58
2019-07-21 23:00 | 35 | 32 |  |  | 43667.9583 | 54 | 54
2019-07-21 23:30 | 33 | 30 |  |  | 43667.9792 | 51 | 51
2019-07-22 | 31 | 28 |  |  | 43668 | 48 | 48
2019-07-22 00:30 | 31 | 26 |  |  | 43668.0208 | 46 | 45
2019-07-22 01:00 | 31 | 25 |  |  | 43668.0417 | 44 | 43
2019-07-22 01:30 | 30 | 25 |  |  | 43668.0625 | 42 | 42
2019-07-22 02:00 | 30 | 24 |  |  | 43668.0833 | 41 | 41
2019-07-22 02:30 | 29 | 24 |  |  | 43668.1042 | 41 | 41
2019-07-22 03:00 | 28 | 24 |  |  | 43668.125 | 40 | 40
2019-07-22 03:30 | 27 | 23 |  |  | 43668.1458 | 39 | 39
2019-07-22 04:00 | 28 | 24 |  |  | 43668.1667 | 38 | 38
2019-07-22 04:30 | 28 | 24 |  |  | 43668.1875 | 40 | 40
2019-07-22 05:00 | 30 | 26 |  |  | 43668.2083 | 42 | 42
2019-07-22 05:30 | 32 | 30 |  |  | 43668.2292 | 46 | 46
2019-07-22 06:00 | 34 | 32 |  |  | 43668.25 | 51 | 51
2019-07-22 06:30 | 36 | 34 |  |  | 43668.2708 | 56 | 56
2019-07-22 07:00 | 39 | 36 |  |  | 43668.2917 | 64 | 63
2019-07-22 07:30 | 44 | 41 |  |  | 43668.3125 | 73 | 72
2019-07-22 08:00 | 44 | 41 |  |  | 43668.3333 | 73 | 73
2019-07-22 08:30 | 43 | 41 |  |  | 43668.3542 | 71 | 70
2019-07-22 09:00 | 41 | 38 |  |  | 43668.375 | 69 | 69
2019-07-22 09:30 | 36 | 34 |  |  | 43668.3958 | 63 | 63
2019-07-22 10:00 | 32 | 31 |  |  | 43668.4167 | 58 | 58
2019-07-22 10:30 | 30 | 29 |  |  | 43668.4375 | 54 | 54
2019-07-22 11:00 | 29 | 27 |  |  | 43668.4583 | 52 | 52
2019-07-22 11:30 | 29 | 27 |  |  | 43668.4792 | 52 | 52
2019-07-22 12:00 | 30 | 29 |  |  | 43668.5 | 55 | 55
2019-07-22 12:30 | 30 | 28 |  |  | 43668.5208 | 56 | 56
2019-07-22 13:00 | 32 | 30 |  |  | 43668.5417 | 57 | 56
2019-07-22 13:30 | 32 | 30 |  |  | 43668.5625 | 55 | 55
2019-07-22 14:00 | 33 | 31 |  |  | 43668.5833 | 56 | 56
2019-07-22 14:30 | 33 | 31 |  |  | 43668.6042 | 57 | 57
2019-07-22 15:00 | 34 | 33 |  |  | 43668.625 | 58 | 58
2019-07-22 15:30 | 35 | 33 |  |  | 43668.6458 | 59 | 59
2019-07-22 16:00 | 36 | 35 |  |  | 43668.6667 | 60 | 60
2019-07-22 16:30 | 36 | 34 |  |  | 43668.6875 | 58 | 58
2019-07-22 17:00 | 38 | 36 |  |  | 43668.7083 | 62 | 62
2019-07-22 17:30 | 39 | 37 |  |  | 43668.7292 | 63 | 63
2019-07-22 18:00 | 42 | 40 |  |  | 43668.75 | 66 | 66
2019-07-22 18:30 | 43 | 40 |  |  | 43668.7708 | 66 | 66
2019-07-22 19:00 | 44 | 42 |  |  | 43668.7917 | 67 | 67
2019-07-22 19:30 | 43 | 40 |  |  | 43668.8125 | 65 | 65
2019-07-22 20:00 | 42 | 39 |  |  | 43668.8333 | 63 | 63
2019-07-22 20:30 | 40 | 37 |  |  | 43668.8542 | 62 | 62
2019-07-22 21:00 | 36 | 34 |  |  | 43668.875 | 58 | 57
2019-07-22 21:30 | 36 | 33 |  |  | 43668.8958 | 55 | 54
2019-07-22 22:00 | 36 | 33 |  |  | 43668.9167 | 55 | 54
2019-07-22 22:30 | 36 | 32 |  |  | 43668.9375 | 54 | 54
2019-07-22 23:00 | 35 | 32 |  |  | 43668.9583 | 52 | 52
2019-07-22 23:30 | 34 | 31 |  |  | 43668.9792 | 50 | 50
2019-07-23 | 31 | 27 |  |  | 43669 | 46 | 46
2019-07-23 00:30 | 31 | 26 |  |  | 43669.0208 | 44 | 43
2019-07-23 01:00 | 30 | 25 |  |  | 43669.0417 | 41 | 40
2019-07-23 01:30 | 29 | 24 |  |  | 43669.0625 | 39 | 38
2019-07-23 02:00 | 28 | 23 |  |  | 43669.0833 | 38 | 37
2019-07-23 02:30 | 28 | 23 |  |  | 43669.1042 | 38 | 38
2019-07-23 03:00 | 28 | 24 |  |  | 43669.125 | 38 | 38
2019-07-23 03:30 | 30 | 26 |  |  | 43669.1458 | 40 | 40
2019-07-23 04:00 | 30 | 26 |  |  | 43669.1667 | 40 | 40
2019-07-23 04:30 | 30 | 26 |  |  | 43669.1875 | 40 | 40
2019-07-23 05:00 | 29 | 25 |  |  | 43669.2083 | 40 | 40
2019-07-23 05:30 | 31 | 29 |  |  | 43669.2292 | 44 | 44
2019-07-23 06:00 | 35 | 33 |  |  | 43669.25 | 50 | 50
2019-07-23 06:30 | 37 | 35 |  |  | 43669.2708 | 57 | 57
2019-07-23 07:00 | 39 | 36 |  |  | 43669.2917 | 63 | 63
2019-07-23 07:30 | 43 | 40 |  |  | 43669.3125 | 72 | 72
2019-07-23 08:00 | 44 | 38 |  |  | 43669.3333 | 71 | 70
2019-07-23 08:30 | 41 | 37 |  |  | 43669.3542 | 68 | 68
2019-07-23 09:00 | 38 | 34 |  |  | 43669.375 | 64 | 63
2019-07-23 09:30 | 47 | 45 |  |  | 43669.3958 | 88 | 88
2019-07-23 10:00 | 46 | 45 |  |  | 43669.4167 | 88 | 88
2019-07-23 10:30 | 43 | 41 |  |  | 43669.4375 | 82 | 82
2019-07-23 11:00 | 42 | 40 |  |  | 43669.4583 | 79 | 79
2019-07-23 11:30 | 42 | 40 |  |  | 43669.4792 | 79 | 78
2019-07-23 12:00 | 40 | 38 |  |  | 43669.5 | 76 | 76
2019-07-23 12:30 | 40 | 39 |  |  | 43669.5208 | 78 | 78
2019-07-23 13:00 | 43 | 42 |  |  | 43669.5417 | 81 | 81
2019-07-23 13:30 | 44 | 43 |  |  | 43669.5625 | 82 | 82
2019-07-23 14:00 | 48 | 47 |  |  | 43669.5833 | 88 | 87
2019-07-23 14:30 | 48 | 47 |  |  | 43669.6042 | 89 | 88
2019-07-23 15:00 | 51 | 50 |  |  | 43669.625 | 92 | 92
2019-07-23 15:30 | 52 | 51 |  |  | 43669.6458 | 94 | 93
2019-07-23 16:00 | 52 | 51 |  |  | 43669.6667 | 94 | 94
2019-07-23 16:30 | 55 | 52 |  |  | 43669.6875 | 98 | 98
2019-07-23 17:00 | 57 | 54 |  |  | 43669.7083 | 101 | 100
2019-07-23 17:30 | 60 | 57 |  |  | 43669.7292 | 107 | 106
2019-07-23 18:00 | 60 | 57 |  |  | 43669.75 | 108 | 107
2019-07-23 18:30 | 60 | 56 |  |  | 43669.7708 | 106 | 105
2019-07-23 19:00 | 62 | 58 |  |  | 43669.7917 | 108 | 107
2019-07-23 19:30 | 60 | 56 |  |  | 43669.8125 | 106 | 105
2019-07-23 20:00 | 60 | 56 |  |  | 43669.8333 | 104 | 103
2019-07-23 20:30 | 57 | 54 |  |  | 43669.8542 | 101 | 101
2019-07-23 21:00 | 54 | 52 |  |  | 43669.875 | 97 | 97
2019-07-23 21:30 | 53 | 50 |  |  | 43669.8958 | 93 | 93
2019-07-23 22:00 | 52 | 49 |  |  | 43669.9167 | 94 | 94
2019-07-23 22:30 | 51 | 48 |  |  | 43669.9375 | 91 | 91
2019-07-23 23:00 | 51 | 48 |  |  | 43669.9583 | 88 | 87
2019-07-23 23:30 | 48 | 45 |  |  | 43669.9792 | 84 | 83
2019-07-24 | 47 | 43 |  |  | 43670 | 79 | 78
2019-07-24 00:30 | 44 | 41 |  |  | 43670.0208 | 74 | 74
2019-07-24 01:00 | 41 | 37 |  |  | 43670.0417 | 70 | 69
2019-07-24 01:30 | 39 | 35 |  |  | 43670.0625 | 66 | 65
2019-07-24 02:00 | 37 | 33 |  |  | 43670.0833 | 62 | 61
2019-07-24 02:30 | 37 | 33 |  |  | 43670.1042 | 61 | 61
2019-07-24 03:00 | 37 | 33 |  |  | 43670.125 | 61 | 60
2019-07-24 03:30 | 37 | 33 |  |  | 43670.1458 | 60 | 60
2019-07-24 04:00 | 36 | 32 |  |  | 43670.1667 | 60 | 60
2019-07-24 04:30 | 36 | 32 |  |  | 43670.1875 | 61 | 61
2019-07-24 05:00 | 39 | 36 |  |  | 43670.2083 | 65 | 65
2019-07-24 05:30 | 43 | 41 |  |  | 43670.2292 | 71 | 71
2019-07-24 06:00 | 48 | 46 |  |  | 43670.25 | 81 | 81
2019-07-24 06:30 | 53 | 51 |  |  | 43670.2708 | 93 | 93
2019-07-24 07:00 | 58 | 56 |  |  | 43670.2917 | 106 | 105
2019-07-24 07:30 | 62 | 61 |  |  | 43670.3125 | 117 | 116
2019-07-24 08:00 | 59 | 59 |  |  | 43670.3333 | 114 | 113
2019-07-24 08:30 | 57 | 55 |  |  | 43670.3542 | 107 | 106
2019-07-24 09:00 | 51 | 49 |  |  | 43670.375 | 99 | 98
2019-07-24 09:30 | 49 | 48 |  |  | 43670.3958 | 96 | 93
2019-07-24 10:00 | 50 | 44 |  |  | 43670.4167 | 90 | 88
2019-07-24 10:30 | 47 | 42 |  |  | 43670.4375 | 85 | 83
2019-07-24 11:00 | 46 | 39 |  |  | 43670.4583 | 81 | 79
2019-07-24 11:30 | 45 | 38 |  |  | 43670.4792 | 80 | 77
2019-07-24 12:00 | 45 | 38 |  |  | 43670.5 | 79 | 77
2019-07-24 12:30 | 46 | 39 |  |  | 43670.5208 | 80 | 77
2019-07-24 13:00 | 45 | 39 |  |  | 43670.5417 | 80 | 78
2019-07-24 13:30 | 47 | 41 |  |  | 43670.5625 | 83 | 80
2019-07-24 14:00 | 47 | 41 |  |  | 43670.5833 | 85 | 82
2019-07-24 14:30 | 48 | 43 |  |  | 43670.6042 | 86 | 83
2019-07-24 15:00 | 49 | 44 |  |  | 43670.625 | 87 | 85
2019-07-24 15:30 | 50 | 44 |  |  | 43670.6458 | 88 | 86
2019-07-24 16:00 | 54 | 49 |  |  | 43670.6667 | 94 | 93
2019-07-24 16:30 | 54 | 51 |  |  | 43670.6875 | 97 | 96
2019-07-24 17:00 | 56 | 53 |  |  | 43670.7083 | 101 | 100
2019-07-24 17:30 | 55 | 51 |  |  | 43670.7292 | 100 | 99
2019-07-24 18:00 | 56 | 52 |  |  | 43670.75 | 101 | 101
2019-07-24 18:30 | 56 | 52 |  |  | 43670.7708 | 100 | 100
2019-07-24 19:00 | 58 | 54 |  |  | 43670.7917 | 102 | 102
2019-07-24 19:30 | 57 | 52 |  |  | 43670.8125 | 99 | 99
2019-07-24 20:00 | 56 | 51 |  |  | 43670.8333 | 97 | 97
2019-07-24 20:30 | 55 | 50 |  |  | 43670.8542 | 97 | 96
2019-07-24 21:00 | 53 | 49 |  |  | 43670.875 | 94 | 93
2019-07-24 21:30 | 51 | 47 |  |  | 43670.8958 | 89 | 89
2019-07-24 22:00 | 51 | 45 |  |  | 43670.9167 | 87 | 87
2019-07-24 22:30 | 47 | 42 |  |  | 43670.9375 | 83 | 83
2019-07-24 23:00 | 46 | 41 |  |  | 43670.9583 | 78 | 78
2019-07-24 23:30 | 44 | 38 |  |  | 43670.9792 | 74 | 74
2019-07-25 | 44 | 36 |  |  | 43671 | 71 | 71
2019-07-25 00:30 | 41 | 33 |  |  | 43671.0208 | 65 | 65
2019-07-25 01:00 | 38 | 30 |  |  | 43671.0417 | 61 | 61
2019-07-25 01:30 | 35 | 27 |  |  | 43671.0625 | 57 | 57
2019-07-25 02:00 | 35 | 27 |  |  | 43671.0833 | 57 | 56
2019-07-25 02:30 | 35 | 27 |  |  | 43671.1042 | 56 | 56
2019-07-25 03:00 | 35 | 27 |  |  | 43671.125 | 56 | 55
2019-07-25 03:30 | 37 | 30 |  |  | 43671.1458 | 58 | 57
2019-07-25 04:00 | 36 | 29 |  |  | 43671.1667 | 57 | 56
2019-07-25 04:30 | 36 | 28 |  |  | 43671.1875 | 57 | 56
2019-07-25 05:00 | 38 | 32 |  |  | 43671.2083 | 62 | 61
2019-07-25 05:30 | 43 | 38 |  |  | 43671.2292 | 69 | 68
2019-07-25 06:00 | 47 | 43 |  |  | 43671.25 | 77 | 76
2019-07-25 06:30 | 50 | 46 |  |  | 43671.2708 | 89 | 88
2019-07-25 07:00 | 51 | 50 |  |  | 43671.2917 | 100 | 98
2019-07-25 07:30 | 54 | 53 |  |  | 43671.3125 | 109 | 107
2019-07-25 08:00 | 55 | 54 |  |  | 43671.3333 | 111 | 109
2019-07-25 08:30 | 54 | 52 |  |  | 43671.3542 | 109 | 107
2019-07-25 09:00 | 50 | 48 |  |  | 43671.375 | 101 | 98
2019-07-25 09:30 | 46 | 44 |  |  | 43671.3958 | 94 | 91
2019-07-25 10:00 | 43 | 42 |  |  | 43671.4167 | 89 | 86
2019-07-25 10:30 | 41 | 39 |  |  | 43671.4375 | 84 | 81
2019-07-25 11:00 | 40 | 39 |  |  | 43671.4583 | 83 | 79
2019-07-25 11:30 | 39 | 38 |  |  | 43671.4792 | 82 | 78
2019-07-25 12:00 | 40 | 40 |  |  | 43671.5 | 83 | 78
2019-07-25 12:30 | 41 | 40 |  |  | 43671.5208 | 84 | 79
2019-07-25 13:00 | 42 | 41 |  |  | 43671.5417 | 86 | 81
2019-07-25 13:30 | 42 | 41 |  |  | 43671.5625 | 85 | 81
2019-07-25 14:00 | 44 | 43 |  |  | 43671.5833 | 86 | 82
2019-07-25 14:30 | 43 | 43 |  |  | 43671.6042 | 87 | 83
2019-07-25 15:00 | 44 | 43 |  |  | 43671.625 | 88 | 85
2019-07-25 15:30 | 46 | 45 |  |  | 43671.6458 | 90 | 86
2019-07-25 16:00 | 49 | 48 |  |  | 43671.6667 | 96 | 93
2019-07-25 16:30 | 50 | 48 |  |  | 43671.6875 | 97 | 95
2019-07-25 17:00 | 52 | 50 |  |  | 43671.7083 | 100 | 98
2019-07-25 17:30 | 53 | 51 |  |  | 43671.7292 | 102 | 101
2019-07-25 18:00 | 56 | 53 |  |  | 43671.75 | 103 | 103
2019-07-25 18:30 | 56 | 53 |  |  | 43671.7708 | 104 | 103
2019-07-25 19:00 | 58 | 55 |  |  | 43671.7917 | 105 | 104
2019-07-25 19:30 | 57 | 54 |  |  | 43671.8125 | 103 | 102
2019-07-25 20:00 | 56 | 53 |  |  | 43671.8333 | 101 | 100
2019-07-25 20:30 | 53 | 50 |  |  | 43671.8542 | 98 | 97
2019-07-25 21:00 | 49 | 47 |  |  | 43671.875 | 93 | 92
2019-07-25 21:30 | 48 | 45 |  |  | 43671.8958 | 88 | 88
2019-07-25 22:00 | 47 | 44 |  |  | 43671.9167 | 87 | 86
2019-07-25 22:30 | 47 | 43 |  |  | 43671.9375 | 85 | 85
2019-07-25 23:00 | 47 | 43 |  |  | 43671.9583 | 83 | 82
2019-07-25 23:30 | 46 | 41 |  |  | 43671.9792 | 79 | 79
2019-07-26 | 41 | 37 |  |  | 43672 | 74 | 73
2019-07-26 00:30 | 36 | 34 |  |  | 43672.0208 | 68 | 68
2019-07-26 01:00 | 35 | 33 |  |  | 43672.0417 | 64 | 64
2019-07-26 01:30 | 33 | 32 |  |  | 43672.0625 | 61 | 61
2019-07-26 02:00 | 32 | 31 |  |  | 43672.0833 | 59 | 59
2019-07-26 02:30 | 31 | 30 |  |  | 43672.1042 | 58 | 58
2019-07-26 03:00 | 31 | 30 |  |  | 43672.125 | 57 | 57
2019-07-26 03:30 | 31 | 30 |  |  | 43672.1458 | 57 | 57
2019-07-26 04:00 | 31 | 30 |  |  | 43672.1667 | 58 | 58
2019-07-26 04:30 | 31 | 30 |  |  | 43672.1875 | 59 | 59
2019-07-26 05:00 | 34 | 33 |  |  | 43672.2083 | 63 | 63
2019-07-26 05:30 | 38 | 37 |  |  | 43672.2292 | 69 | 69
2019-07-26 06:00 | 42 | 42 |  |  | 43672.25 | 76 | 76
2019-07-26 06:30 | 48 | 48 |  |  | 43672.2708 | 88 | 87
2019-07-26 07:00 | 50 | 50 |  |  | 43672.2917 | 96 | 96
2019-07-26 07:30 | 55 | 53 |  |  | 43672.3125 | 106 | 104
2019-07-26 08:00 | 52 | 49 |  |  | 43672.3333 | 105 | 102
2019-07-26 08:30 | 47 | 44 |  |  | 43672.3542 | 97 | 96
2019-07-26 09:00 | 45 | 42 |  |  | 43672.375 | 95 | 94
2019-07-26 09:30 | 43 | 40 |  |  | 43672.3958 | 91 | 89
2019-07-26 10:00 | 38 | 35 |  |  | 43672.4167 | 85 | 83
2019-07-26 10:30 | 37 | 34 |  |  | 43672.4375 | 83 | 81
2019-07-26 11:00 | 38 | 36 |  |  | 43672.4583 | 83 | 82
2019-07-26 11:30 | 39 | 37 |  |  | 43672.4792 | 84 | 82
2019-07-26 12:00 | 42 | 40 |  |  | 43672.5 | 85 | 83
2019-07-26 12:30 | 37 | 34 |  |  | 43672.5208 | 83 | 82
2019-07-26 13:00 | 39 | 37 |  |  | 43672.5417 | 85 | 84
2019-07-26 13:30 | 39 | 37 |  |  | 43672.5625 | 84 | 82
2019-07-26 14:00 | 40 | 38 |  |  | 43672.5833 | 84 | 83
2019-07-26 14:30 | 40 | 37 |  |  | 43672.6042 | 84 | 82
2019-07-26 15:00 | 43 | 41 |  |  | 43672.625 | 87 | 86
2019-07-26 15:30 | 44 | 42 |  |  | 43672.6458 | 87 | 86
2019-07-26 16:00 | 43 | 41 |  |  | 43672.6667 | 86 | 85
2019-07-26 16:30 | 46 | 43 |  |  | 43672.6875 | 90 | 88
2019-07-26 17:00 | 50 | 47 |  |  | 43672.7083 | 96 | 94
2019-07-26 17:30 | 55 | 52 |  |  | 43672.7292 | 102 | 100
2019-07-26 18:00 | 53 | 49 |  |  | 43672.75 | 101 | 98
2019-07-26 18:30 | 53 | 49 |  |  | 43672.7708 | 101 | 97
2019-07-26 19:00 | 54 | 49 |  |  | 43672.7917 | 102 | 98
2019-07-26 19:30 | 52 | 48 |  |  | 43672.8125 | 99 | 96
2019-07-26 20:00 | 48 | 46 |  |  | 43672.8333 | 94 | 93
2019-07-26 20:30 | 45 | 44 |  |  | 43672.8542 | 91 | 91
2019-07-26 21:00 | 42 | 41 |  |  | 43672.875 | 85 | 85
2019-07-26 21:30 | 39 | 38 |  |  | 43672.8958 | 81 | 81
2019-07-26 22:00 | 37 | 36 |  |  | 43672.9167 | 79 | 79
2019-07-26 22:30 | 35 | 34 |  |  | 43672.9375 | 77 | 77
2019-07-26 23:00 | 35 | 34 |  |  | 43672.9583 | 75 | 75
2019-07-26 23:30 | 34 | 33 |  |  | 43672.9792 | 71 | 71
2019-07-27 | 32 | 30 |  |  | 43673 | 66 | 65
2019-07-27 00:30 | 29 | 27 |  |  | 43673.0208 | 61 | 60
2019-07-27 01:00 | 31 | 28 |  |  | 43673.0417 | 60 | 59
2019-07-27 01:30 | 27 | 24 |  |  | 43673.0625 | 55 | 54
2019-07-27 02:00 | 22 | 19 |  |  | 43673.0833 | 48 | 47
2019-07-27 02:30 | 18 | 17 |  |  | 43673.1042 | 46 | 44
2019-07-27 03:00 | 18 | 18 |  |  | 43673.125 | 50 | 45
2019-07-27 03:30 | 21 | 21 |  |  | 43673.1458 | 53 | 48
2019-07-27 04:00 | 21 | 21 |  |  | 43673.1667 | 54 | 48
2019-07-27 04:30 | 23 | 22 |  |  | 43673.1875 | 55 | 50
2019-07-27 05:00 | 25 | 25 |  |  | 43673.2083 | 58 | 53
2019-07-27 05:30 | 27 | 27 |  |  | 43673.2292 | 60 | 56
2019-07-27 06:00 | 29 | 29 |  |  | 43673.25 | 64 | 59
2019-07-27 06:30 | 29 | 29 |  |  | 43673.2708 | 66 | 62
2019-07-27 07:00 | 29 | 29 |  |  | 43673.2917 | 66 | 63
2019-07-27 07:30 | 28 | 28 |  |  | 43673.3125 | 67 | 64
2019-07-27 08:00 | 28 | 28 |  |  | 43673.3333 | 67 | 64
2019-07-27 08:30 | 29 | 29 |  |  | 43673.3542 | 67 | 65
2019-07-27 09:00 | 28 | 28 |  |  | 43673.375 | 66 | 64
2019-07-27 09:30 | 28 | 28 |  |  | 43673.3958 | 65 | 63
2019-07-27 10:00 | 26 | 26 |  |  | 43673.4167 | 61 | 58
2019-07-27 10:30 | 25 | 24 |  |  | 43673.4375 | 57 | 55
2019-07-27 11:00 | 23 | 23 |  |  | 43673.4583 | 54 | 52
2019-07-27 11:30 | 21 | 20 |  |  | 43673.4792 | 52 | 50
2019-07-27 12:00 | 20 | 19 |  |  | 43673.5 | 50 | 48
2019-07-27 12:30 | 19 | 19 |  |  | 43673.5208 | 50 | 47
2019-07-27 13:00 | 18 | 17 |  |  | 43673.5417 | 49 | 46
2019-07-27 13:30 | 20 | 20 |  |  | 43673.5625 | 49 | 47
2019-07-27 14:00 | 20 | 19 |  |  | 43673.5833 | 49 | 47
2019-07-27 14:30 | 22 | 22 |  |  | 43673.6042 | 53 | 50
2019-07-27 15:00 | 25 | 24 |  |  | 43673.625 | 57 | 55
2019-07-27 15:30 | 27 | 26 |  |  | 43673.6458 | 61 | 59
2019-07-27 16:00 | 30 | 29 |  |  | 43673.6667 | 66 | 64
2019-07-27 16:30 | 32 | 31 |  |  | 43673.6875 | 71 | 69
2019-07-27 17:00 | 34 | 34 |  |  | 43673.7083 | 76 | 74
2019-07-27 17:30 | 36 | 36 |  |  | 43673.7292 | 79 | 78
2019-07-27 18:00 | 39 | 39 |  |  | 43673.75 | 84 | 83
2019-07-27 18:30 | 38 | 38 |  |  | 43673.7708 | 84 | 83
2019-07-27 19:00 | 40 | 40 |  |  | 43673.7917 | 86 | 85
2019-07-27 19:30 | 40 | 40 |  |  | 43673.8125 | 86 | 85
2019-07-27 20:00 | 43 | 42 |  |  | 43673.8333 | 88 | 87
2019-07-27 20:30 | 40 | 40 |  |  | 43673.8542 | 86 | 85
2019-07-27 21:00 | 37 | 37 |  |  | 43673.875 | 81 | 80
2019-07-27 21:30 | 34 | 34 |  |  | 43673.8958 | 78 | 76
2019-07-27 22:00 | 35 | 35 |  |  | 43673.9167 | 78 | 76
2019-07-27 22:30 | 35 | 35 |  |  | 43673.9375 | 80 | 78
2019-07-27 23:00 | 35 | 35 |  |  | 43673.9583 | 78 | 76
2019-07-27 23:30 | 34 | 34 |  |  | 43673.9792 | 75 | 73
2019-07-28 | 31 | 31 |  |  | 43674 | 70 | 67
2019-07-28 00:30 | 30 | 30 |  |  | 43674.0208 | 67 | 64
2019-07-28 01:00 | 29 | 29 |  |  | 43674.0417 | 65 | 61
2019-07-28 01:30 | 25 | 25 |  |  | 43674.0625 | 60 | 55
2019-07-28 02:00 | 23 | 23 |  |  | 43674.0833 | 58 | 53
2019-07-28 02:30 | 23 | 23 |  |  | 43674.1042 | 57 | 52
2019-07-28 03:00 | 23 | 23 |  |  | 43674.125 | 56 | 50
2019-07-28 03:30 | 23 | 23 |  |  | 43674.1458 | 57 | 51
2019-07-28 04:00 | 24 | 23 |  |  | 43674.1667 | 56 | 50
2019-07-28 04:30 | 25 | 25 |  |  | 43674.1875 | 57 | 52
2019-07-28 05:00 | 25 | 25 |  |  | 43674.2083 | 58 | 53
2019-07-28 05:30 | 25 | 25 |  |  | 43674.2292 | 59 | 54
2019-07-28 06:00 | 27 | 27 |  |  | 43674.25 | 61 | 56
2019-07-28 06:30 | 28 | 28 |  |  | 43674.2708 | 64 | 59
2019-07-28 07:00 | 28 | 28 |  |  | 43674.2917 | 65 | 61
2019-07-28 07:30 | 26 | 26 |  |  | 43674.3125 | 64 | 60
2019-07-28 08:00 | 25 | 25 |  |  | 43674.3333 | 62 | 59
2019-07-28 08:30 | 26 | 25 |  |  | 43674.3542 | 62 | 59
2019-07-28 09:00 | 24 | 24 |  |  | 43674.375 | 59 | 55
2019-07-28 09:30 | 23 | 23 |  |  | 43674.3958 | 58 | 54
2019-07-28 10:00 | 23 | 23 |  |  | 43674.4167 | 58 | 55
2019-07-28 10:30 | 23 | 23 |  |  | 43674.4375 | 56 | 54
2019-07-28 11:00 | 23 | 23 |  |  | 43674.4583 | 55 | 52
2019-07-28 11:30 | 25 | 25 |  |  | 43674.4792 | 56 | 54
2019-07-28 12:00 | 25 | 25 |  |  | 43674.5 | 53 | 51
2019-07-28 12:30 | 25 | 25 |  |  | 43674.5208 | 56 | 54
2019-07-28 13:00 | 25 | 25 |  |  | 43674.5417 | 54 | 52
2019-07-28 13:30 | 25 | 25 |  |  | 43674.5625 | 53 | 50
2019-07-28 14:00 | 25 | 25 |  |  | 43674.5833 | 55 | 52
2019-07-28 14:30 | 30 | 29 |  |  | 43674.6042 | 63 | 60
2019-07-28 15:00 | 34 | 34 |  |  | 43674.625 | 67 | 65
2019-07-28 15:30 | 35 | 35 |  |  | 43674.6458 | 70 | 68
2019-07-28 16:00 | 35 | 35 |  |  | 43674.6667 | 73 | 71
2019-07-28 16:30 | 35 | 35 |  |  | 43674.6875 | 74 | 72
2019-07-28 17:00 | 34 | 34 |  |  | 43674.7083 | 76 | 74
2019-07-28 17:30 | 38 | 38 |  |  | 43674.7292 | 81 | 79
2019-07-28 18:00 | 40 | 40 |  |  | 43674.75 | 85 | 84
2019-07-28 18:30 | 42 | 42 |  |  | 43674.7708 | 88 | 86
2019-07-28 19:00 | 41 | 41 |  |  | 43674.7917 | 88 | 87
2019-07-28 19:30 | 40 | 40 |  |  | 43674.8125 | 86 | 84
2019-07-28 20:00 | 39 | 39 |  |  | 43674.8333 | 84 | 83
2019-07-28 20:30 | 38 | 38 |  |  | 43674.8542 | 84 | 82
2019-07-28 21:00 | 36 | 36 |  |  | 43674.875 | 80 | 78
2019-07-28 21:30 | 34 | 34 |  |  | 43674.8958 | 76 | 74
2019-07-28 22:00 | 36 | 36 |  |  | 43674.9167 | 78 | 76
2019-07-28 22:30 | 37 | 37 |  |  | 43674.9375 | 79 | 78
2019-07-28 23:00 | 37 | 37 |  |  | 43674.9583 | 78 | 75
2019-07-28 23:30 | 36 | 36 |  |  | 43674.9792 | 75 | 73
2019-07-29 | 32 | 32 |  |  | 43675 | 69 | 66
2019-07-29 00:30 | 29 | 29 |  |  | 43675.0208 | 64 | 61
2019-07-29 01:00 | 27 | 27 |  |  | 43675.0417 | 62 | 58
2019-07-29 01:30 | 24 | 24 |  |  | 43675.0625 | 58 | 53
2019-07-29 02:00 | 22 | 22 |  |  | 43675.0833 | 55 | 50
2019-07-29 02:30 | 23 | 23 |  |  | 43675.1042 | 57 | 52
2019-07-29 03:00 | 27 | 26 |  |  | 43675.125 | 59 | 54
2019-07-29 03:30 | 26 | 26 |  |  | 43675.1458 | 59 | 54
2019-07-29 04:00 | 27 | 27 |  |  | 43675.1667 | 60 | 55
2019-07-29 04:30 | 29 | 29 |  |  | 43675.1875 | 63 | 58
2019-07-29 05:00 | 30 | 30 |  |  | 43675.2083 | 63 | 59
2019-07-29 05:30 | 32 | 32 |  |  | 43675.2292 | 67 | 63
2019-07-29 06:00 | 36 | 36 |  |  | 43675.25 | 72 | 70
2019-07-29 06:30 | 41 | 40 |  |  | 43675.2708 | 81 | 80
2019-07-29 07:00 | 48 | 47 |  |  | 43675.2917 | 93 | 93
2019-07-29 07:30 | 52 | 50 |  |  | 43675.3125 | 101 | 101
2019-07-29 08:00 | 51 | 49 |  |  | 43675.3333 | 102 | 102
2019-07-29 08:30 | 49 | 47 |  |  | 43675.3542 | 98 | 98
2019-07-29 09:00 | 45 | 43 |  |  | 43675.375 | 92 | 92
2019-07-29 09:30 | 43 | 41 |  |  | 43675.3958 | 87 | 87
2019-07-29 10:00 | 41 | 39 |  |  | 43675.4167 | 83 | 83
2019-07-29 10:30 | 39 | 37 |  |  | 43675.4375 | 79 | 79
2019-07-29 11:00 | 39 | 37 |  |  | 43675.4583 | 79 | 79
2019-07-29 11:30 | 39 | 38 |  |  | 43675.4792 | 80 | 80
2019-07-29 12:00 | 42 | 41 |  |  | 43675.5 | 84 | 84
2019-07-29 12:30 | 40 | 39 |  |  | 43675.5208 | 82 | 82
2019-07-29 13:00 | 40 | 39 |  |  | 43675.5417 | 81 | 80
2019-07-29 13:30 | 40 | 39 |  |  | 43675.5625 | 83 | 82
2019-07-29 14:00 | 42 | 40 |  |  | 43675.5833 | 84 | 84
2019-07-29 14:30 | 43 | 41 |  |  | 43675.6042 | 84 | 84
2019-07-29 15:00 | 42 | 41 |  |  | 43675.625 | 84 | 84
2019-07-29 15:30 | 44 | 43 |  |  | 43675.6458 | 83 | 83
2019-07-29 16:00 | 48 | 46 |  |  | 43675.6667 | 90 | 90
2019-07-29 16:30 | 49 | 47 |  |  | 43675.6875 | 93 | 93
2019-07-29 17:00 | 51 | 49 |  |  | 43675.7083 | 97 | 97
2019-07-29 17:30 | 53 | 50 |  |  | 43675.7292 | 100 | 100
2019-07-29 18:00 | 54 | 51 |  |  | 43675.75 | 102 | 102
2019-07-29 18:30 | 54 | 51 |  |  | 43675.7708 | 102 | 102
2019-07-29 19:00 | 55 | 52 |  |  | 43675.7917 | 103 | 102
2019-07-29 19:30 | 55 | 51 |  |  | 43675.8125 | 100 | 100
2019-07-29 20:00 | 54 | 50 |  |  | 43675.8333 | 97 | 97
2019-07-29 20:30 | 52 | 49 |  |  | 43675.8542 | 96 | 96
2019-07-29 21:00 | 49 | 46 |  |  | 43675.875 | 91 | 91
2019-07-29 21:30 | 46 | 43 |  |  | 43675.8958 | 84 | 84
2019-07-29 22:00 | 45 | 42 |  |  | 43675.9167 | 83 | 82
2019-07-29 22:30 | 44 | 40 |  |  | 43675.9375 | 80 | 80
2019-07-29 23:00 | 42 | 38 |  |  | 43675.9583 | 77 | 76
2019-07-29 23:30 | 40 | 39 |  |  | 43675.9792 | 78 | 74
2019-07-30 | 35 | 34 |  |  | 43676 | 74 | 68
2019-07-30 00:30 | 32 | 32 |  |  | 43676.0208 | 74 | 63
2019-07-30 01:00 | 29 | 29 |  |  | 43676.0417 | 70 | 58
2019-07-30 01:30 | 28 | 28 |  |  | 43676.0625 | 68 | 55
2019-07-30 02:00 | 24 | 24 |  |  | 43676.0833 | 64 | 50
2019-07-30 02:30 | 22 | 22 |  |  | 43676.1042 | 63 | 49
2019-07-30 03:00 | 24 | 24 |  |  | 43676.125 | 64 | 49
2019-07-30 03:30 | 24 | 24 |  |  | 43676.1458 | 65 | 50
2019-07-30 04:00 | 24 | 24 |  |  | 43676.1667 | 65 | 50
2019-07-30 04:30 | 26 | 26 |  |  | 43676.1875 | 66 | 53
2019-07-30 05:00 | 30 | 29 |  |  | 43676.2083 | 70 | 57
2019-07-30 05:30 | 35 | 35 |  |  | 43676.2292 | 76 | 65
2019-07-30 06:00 | 40 | 39 |  |  | 43676.25 | 82 | 73
2019-07-30 06:30 | 44 | 43 |  |  | 43676.2708 | 89 | 83
2019-07-30 07:00 | 48 | 46 |  |  | 43676.2917 | 96 | 92
2019-07-30 07:30 | 55 | 53 |  |  | 43676.3125 | 106 | 104
2019-07-30 08:00 | 53 | 51 |  |  | 43676.3333 | 104 | 103
2019-07-30 08:30 | 50 | 48 |  |  | 43676.3542 | 98 | 96
2019-07-30 09:00 | 46 | 43 |  |  | 43676.375 | 90 | 88
2019-07-30 09:30 | 44 | 41 |  |  | 43676.3958 | 85 | 83
2019-07-30 10:00 | 41 | 37 |  |  | 43676.4167 | 77 | 75
2019-07-30 10:30 | 38 | 33 |  |  | 43676.4375 | 70 | 68
2019-07-30 11:00 | 37 | 32 |  |  | 43676.4583 | 68 | 66
2019-07-30 11:30 | 39 | 34 |  |  | 43676.4792 | 72 | 70
2019-07-30 12:00 | 38 | 33 |  |  | 43676.5 | 71 | 70
2019-07-30 12:30 | 37 | 33 |  |  | 43676.5208 | 72 | 70
2019-07-30 13:00 | 39 | 35 |  |  | 43676.5417 | 73 | 71
2019-07-30 13:30 | 42 | 38 |  |  | 43676.5625 | 78 | 76
2019-07-30 14:00 | 43 | 39 |  |  | 43676.5833 | 79 | 77
2019-07-30 14:30 | 44 | 41 |  |  | 43676.6042 | 81 | 79
2019-07-30 15:00 | 45 | 42 |  |  | 43676.625 | 84 | 82
2019-07-30 15:30 | 45 | 42 |  |  | 43676.6458 | 85 | 83
2019-07-30 16:00 | 49 | 47 |  |  | 43676.6667 | 90 | 88
2019-07-30 16:30 | 50 | 48 |  |  | 43676.6875 | 94 | 92
2019-07-30 17:00 | 52 | 52 |  |  | 43676.7083 | 98 | 98
2019-07-30 17:30 | 52 | 52 |  |  | 43676.7292 | 98 | 98
2019-07-30 18:00 | 51 | 50 |  |  | 43676.75 | 99 | 99
2019-07-30 18:30 | 50 | 50 |  |  | 43676.7708 | 97 | 97
2019-07-30 19:00 | 51 | 50 |  |  | 43676.7917 | 98 | 98
2019-07-30 19:30 | 49 | 48 |  |  | 43676.8125 | 95 | 95
2019-07-30 20:00 | 49 | 48 |  |  | 43676.8333 | 93 | 93
2019-07-30 20:30 | 49 | 48 |  |  | 43676.8542 | 92 | 92
2019-07-30 21:00 | 46 | 46 |  |  | 43676.875 | 89 | 88
2019-07-30 21:30 | 44 | 43 |  |  | 43676.8958 | 83 | 83
2019-07-30 22:00 | 43 | 42 |  |  | 43676.9167 | 83 | 83
2019-07-30 22:30 | 42 | 41 |  |  | 43676.9375 | 80 | 80
2019-07-30 23:00 | 42 | 40 |  |  | 43676.9583 | 78 | 77
2019-07-30 23:30 | 40 | 39 |  |  | 43676.9792 | 75 | 74
2019-07-31 | 37 | 37 |  |  | 43677 | 74 | 70
2019-07-31 00:30 | 36 | 34 |  |  | 43677.0208 | 69 | 63
2019-07-31 01:00 | 33 | 30 |  |  | 43677.0417 | 66 | 59
2019-07-31 01:30 | 33 | 30 |  |  | 43677.0625 | 64 | 57
2019-07-31 02:00 | 30 | 27 |  |  | 43677.0833 | 61 | 52
2019-07-31 02:30 | 28 | 26 |  |  | 43677.1042 | 60 | 51
2019-07-31 03:00 | 30 | 27 |  |  | 43677.125 | 60 | 52
2019-07-31 03:30 | 29 | 26 |  |  | 43677.1458 | 59 | 51
2019-07-31 04:00 | 28 | 26 |  |  | 43677.1667 | 59 | 50
2019-07-31 04:30 | 30 | 27 |  |  | 43677.1875 | 61 | 53
2019-07-31 05:00 | 33 | 31 |  |  | 43677.2083 | 65 | 58
2019-07-31 05:30 | 37 | 34 |  |  | 43677.2292 | 69 | 62
2019-07-31 06:00 | 39 | 38 |  |  | 43677.25 | 72 | 69
2019-07-31 06:30 | 44 | 43 |  |  | 43677.2708 | 82 | 82
2019-07-31 07:00 | 48 | 48 |  |  | 43677.2917 | 94 | 94
2019-07-31 07:30 | 52 | 51 |  |  | 43677.3125 | 102 | 102
2019-07-31 08:00 | 49 | 48 |  |  | 43677.3333 | 98 | 98
2019-07-31 08:30 | 37 | 37 |  |  | 43677.3542 | 75 | 75
2019-07-31 09:00 | 32 | 32 |  |  | 43677.375 | 65 | 65
2019-07-31 09:30 | 30 | 30 |  |  | 43677.3958 | 60 | 59
2019-07-31 10:00 | 26 | 26 |  |  | 43677.4167 | 54 | 54
2019-07-31 10:30 | 24 | 24 |  |  | 43677.4375 | 51 | 51
2019-07-31 11:00 | 24 | 23 |  |  | 43677.4583 | 49 | 49
2019-07-31 11:30 | 22 | 22 |  |  | 43677.4792 | 47 | 46
2019-07-31 12:00 | 22 | 22 |  |  | 43677.5 | 48 | 47
2019-07-31 12:30 | 24 | 24 |  |  | 43677.5208 | 50 | 49
2019-07-31 13:00 | 28 | 28 |  |  | 43677.5417 | 53 | 52
2019-07-31 13:30 | 32 | 31 |  |  | 43677.5625 | 59 | 58
2019-07-31 14:00 | 33 | 33 |  |  | 43677.5833 | 60 | 60
2019-07-31 14:30 | 32 | 31 |  |  | 43677.6042 | 59 | 59
2019-07-31 15:00 | 45 | 45 |  |  | 43677.625 | 81 | 81
2019-07-31 15:30 | 46 | 46 |  |  | 43677.6458 | 87 | 87
2019-07-31 16:00 | 50 | 50 |  |  | 43677.6667 | 90 | 90
2019-07-31 16:30 | 48 | 47 |  |  | 43677.6875 | 90 | 90
2019-07-31 17:00 | 51 | 51 |  |  | 43677.7083 | 95 | 95
2019-07-31 17:30 | 53 | 52 |  |  | 43677.7292 | 99 | 99
2019-07-31 18:00 | 54 | 52 |  |  | 43677.75 | 101 | 101
2019-07-31 18:30 | 52 | 51 |  |  | 43677.7708 | 99 | 98
2019-07-31 19:00 | 54 | 53 |  |  | 43677.7917 | 101 | 100
2019-07-31 19:30 | 53 | 51 |  |  | 43677.8125 | 98 | 97
2019-07-31 20:00 | 55 | 51 |  |  | 43677.8333 | 95 | 94
2019-07-31 20:30 | 54 | 50 |  |  | 43677.8542 | 95 | 94
2019-07-31 21:00 | 56 | 47 |  |  | 43677.875 | 91 | 89
2019-07-31 21:30 | 56 | 45 |  |  | 43677.8958 | 87 | 85
2019-07-31 22:00 | 57 | 45 |  |  | 43677.9167 | 87 | 85
2019-07-31 22:30 | 55 | 42 |  |  | 43677.9375 | 84 | 82
2019-07-31 23:00 | 55 | 43 |  |  | 43677.9583 | 84 | 81
2019-07-31 23:30 | 54 | 41 |  |  | 43677.9792 | 80 | 77
2019-08-01 | 52 | 35 |  |  | 43678 | 73 | 69
2019-08-01 00:30 | 50 | 32 |  |  | 43678.0208 | 67 | 62
2019-08-01 01:00 | 48 | 29 |  |  | 43678.0417 | 62 | 57
2019-08-01 01:30 | 47 | 26 |  |  | 43678.0625 | 59 | 54
2019-08-01 02:00 | 45 | 25 |  |  | 43678.0833 | 57 | 51
2019-08-01 02:30 | 45 | 25 |  |  | 43678.1042 | 57 | 51
2019-08-01 03:00 | 46 | 25 |  |  | 43678.125 | 57 | 51
2019-08-01 03:30 | 46 | 26 |  |  | 43678.1458 | 57 | 52
2019-08-01 04:00 | 46 | 25 |  |  | 43678.1667 | 57 | 51
2019-08-01 04:30 | 45 | 25 |  |  | 43678.1875 | 56 | 51
2019-08-01 05:00 | 46 | 26 |  |  | 43678.2083 | 58 | 54
2019-08-01 05:30 | 47 | 31 |  |  | 43678.2292 | 63 | 60
2019-08-01 06:00 | 49 | 36 |  |  | 43678.25 | 71 | 69
2019-08-01 06:30 | 47 | 39 |  |  | 43678.2708 | 80 | 79
2019-08-01 07:00 | 49 | 43 |  |  | 43678.2917 | 90 | 90
2019-08-01 07:30 | 53 | 48 |  |  | 43678.3125 | 99 | 99
2019-08-01 08:00 | 44 | 39 |  |  | 43678.3333 | 80 | 80
2019-08-01 08:30 | 39 | 32 |  |  | 43678.3542 | 67 | 67
2019-08-01 09:00 | 37 | 31 |  |  | 43678.375 | 65 | 65
2019-08-01 09:30 | 34 | 29 |  |  | 43678.3958 | 60 | 60
2019-08-01 10:00 | 34 | 28 |  |  | 43678.4167 | 61 | 61
2019-08-01 10:30 | 37 | 33 |  |  | 43678.4375 | 59 | 59
2019-08-01 11:00 | 35 | 31 |  |  | 43678.4583 | 59 | 59
2019-08-01 11:30 | 36 | 33 |  |  | 43678.4792 | 61 | 61
2019-08-01 12:00 | 41 | 38 |  |  | 43678.5 | 61 | 61
2019-08-01 12:30 | 41 | 38 |  |  | 43678.5208 | 65 | 65
2019-08-01 13:00 | 38 | 34 |  |  | 43678.5417 | 66 | 65
2019-08-01 13:30 | 37 | 33 |  |  | 43678.5625 | 63 | 62
2019-08-01 14:00 | 34 | 29 |  |  | 43678.5833 | 60 | 59
2019-08-01 14:30 | 36 | 32 |  |  | 43678.6042 | 63 | 62
2019-08-01 15:00 | 38 | 34 |  |  | 43678.625 | 70 | 70
2019-08-01 15:30 | 48 | 44 |  |  | 43678.6458 | 83 | 83
2019-08-01 16:00 | 47 | 43 |  |  | 43678.6667 | 83 | 83
2019-08-01 16:30 | 50 | 45 |  |  | 43678.6875 | 88 | 88
2019-08-01 17:00 | 52 | 47 |  |  | 43678.7083 | 93 | 93
2019-08-01 17:30 | 50 | 45 |  |  | 43678.7292 | 90 | 90
2019-08-01 18:00 | 48 | 46 |  |  | 43678.75 | 94 | 94
2019-08-01 18:30 | 49 | 48 |  |  | 43678.7708 | 95 | 95
2019-08-01 19:00 | 51 | 50 |  |  | 43678.7917 | 97 | 97
2019-08-01 19:30 | 50 | 50 |  |  | 43678.8125 | 95 | 95
2019-08-01 20:00 | 49 | 48 |  |  | 43678.8333 | 93 | 93
2019-08-01 20:30 | 48 | 47 |  |  | 43678.8542 | 92 | 92
2019-08-01 21:00 | 45 | 43 |  |  | 43678.875 | 86 | 86
2019-08-01 21:30 | 43 | 41 |  |  | 43678.8958 | 81 | 81
2019-08-01 22:00 | 40 | 39 |  |  | 43678.9167 | 78 | 78
2019-08-01 22:30 | 38 | 36 |  |  | 43678.9375 | 75 | 75
2019-08-01 23:00 | 37 | 35 |  |  | 43678.9583 | 70 | 70
2019-08-01 23:30 | 36 | 33 |  |  | 43678.9792 | 67 | 67
2019-08-02 | 34 | 31 |  |  | 43679 | 64 | 63
2019-08-02 00:30 | 32 | 28 |  |  | 43679.0208 | 59 | 58
2019-08-02 01:00 | 32 | 27 |  |  | 43679.0417 | 57 | 55
2019-08-02 01:30 | 27 | 26 |  |  | 43679.0625 | 58 | 52
2019-08-02 02:00 | 25 | 24 |  |  | 43679.0833 | 55 | 49
2019-08-02 02:30 | 25 | 24 |  |  | 43679.1042 | 55 | 49
2019-08-02 03:00 | 26 | 24 |  |  | 43679.125 | 56 | 49
2019-08-02 03:30 | 26 | 25 |  |  | 43679.1458 | 56 | 50
2019-08-02 04:00 | 26 | 25 |  |  | 43679.1667 | 57 | 50
2019-08-02 04:30 | 27 | 26 |  |  | 43679.1875 | 58 | 52
2019-08-02 05:00 | 30 | 29 |  |  | 43679.2083 | 61 | 56
2019-08-02 05:30 | 34 | 33 |  |  | 43679.2292 | 66 | 61
2019-08-02 06:00 | 36 | 36 |  |  | 43679.25 | 70 | 67
2019-08-02 06:30 | 40 | 40 |  |  | 43679.2708 | 79 | 78
2019-08-02 07:00 | 44 | 44 |  |  | 43679.2917 | 90 | 89
2019-08-02 07:30 | 49 | 49 |  |  | 43679.3125 | 99 | 98
2019-08-02 08:00 | 44 | 44 |  |  | 43679.3333 | 94 | 93
2019-08-02 08:30 | 40 | 40 |  |  | 43679.3542 | 87 | 85
2019-08-02 09:00 | 38 | 38 |  |  | 43679.375 | 82 | 81
2019-08-02 09:30 | 36 | 36 |  |  | 43679.3958 | 77 | 76
2019-08-02 10:00 | 36 | 35 |  |  | 43679.4167 | 74 | 74
2019-08-02 10:30 | 34 | 34 |  |  | 43679.4375 | 70 | 70
2019-08-02 11:00 | 34 | 33 |  |  | 43679.4583 | 71 | 71
2019-08-02 11:30 | 37 | 37 |  |  | 43679.4792 | 75 | 75
2019-08-02 12:00 | 39 | 38 |  |  | 43679.5 | 77 | 77
2019-08-02 12:30 | 40 | 40 |  |  | 43679.5208 | 77 | 77
2019-08-02 13:00 | 42 | 41 |  |  | 43679.5417 | 78 | 78
2019-08-02 13:30 | 43 | 43 |  |  | 43679.5625 | 78 | 78
2019-08-02 14:00 | 65 | 64 |  |  | 43679.5833 | 93 | 93
2019-08-02 14:30 | 67 | 66 |  |  | 43679.6042 | 97 | 97
2019-08-02 15:00 | 65 | 64 |  |  | 43679.625 | 99 | 99
2019-08-02 15:30 | 68 | 68 |  |  | 43679.6458 | 99 | 99
2019-08-02 16:00 | 73 | 73 |  |  | 43679.6667 | 106 | 106
2019-08-02 16:30 | 75 | 75 |  |  | 43679.6875 | 105 | 105
2019-08-02 17:00 | 73 | 73 |  |  | 43679.7083 | 104 | 104
2019-08-02 17:30 | 74 | 74 |  |  | 43679.7292 | 106 | 106
2019-08-02 18:00 | 75 | 75 |  |  | 43679.75 | 108 | 107
2019-08-02 18:30 | 74 | 74 |  |  | 43679.7708 | 107 | 106
2019-08-02 19:00 | 75 | 74 |  |  | 43679.7917 | 107 | 106
2019-08-02 19:30 | 72 | 72 |  |  | 43679.8125 | 104 | 103
2019-08-02 20:00 | 71 | 71 |  |  | 43679.8333 | 101 | 101
2019-08-02 20:30 | 72 | 72 |  |  | 43679.8542 | 103 | 102
2019-08-02 21:00 | 68 | 68 |  |  | 43679.875 | 97 | 97
2019-08-02 21:30 | 64 | 63 |  |  | 43679.8958 | 91 | 91
2019-08-02 22:00 | 64 | 64 |  |  | 43679.9167 | 92 | 91
2019-08-02 22:30 | 61 | 60 |  |  | 43679.9375 | 88 | 87
2019-08-02 23:00 | 59 | 59 |  |  | 43679.9583 | 85 | 84
2019-08-02 23:30 | 57 | 57 |  |  | 43679.9792 | 84 | 82
2019-08-03 | 54 | 54 |  |  | 43680 | 79 | 77
2019-08-03 00:30 | 52 | 52 |  |  | 43680.0208 | 75 | 72
2019-08-03 01:00 | 49 | 49 |  |  | 43680.0417 | 71 | 67
2019-08-03 01:30 | 48 | 46 |  |  | 43680.0625 | 70 | 64
2019-08-03 02:00 | 47 | 43 |  |  | 43680.0833 | 68 | 60
2019-08-03 02:30 | 46 | 43 |  |  | 43680.1042 | 66 | 58
2019-08-03 03:00 | 45 | 43 |  |  | 43680.125 | 65 | 60
2019-08-03 03:30 | 45 | 43 |  |  | 43680.1458 | 65 | 59
2019-08-03 04:00 | 44 | 41 |  |  | 43680.1667 | 63 | 57
2019-08-03 04:30 | 42 | 40 |  |  | 43680.1875 | 61 | 56
2019-08-03 05:00 | 48 | 46 |  |  | 43680.2083 | 68 | 63
2019-08-03 05:30 | 52 | 50 |  |  | 43680.2292 | 73 | 68
2019-08-03 06:00 | 54 | 52 |  |  | 43680.25 | 76 | 71
2019-08-03 06:30 | 55 | 53 |  |  | 43680.2708 | 78 | 74
2019-08-03 07:00 | 55 | 54 |  |  | 43680.2917 | 80 | 77
2019-08-03 07:30 | 52 | 52 |  |  | 43680.3125 | 77 | 74
2019-08-03 08:00 | 50 | 50 |  |  | 43680.3333 | 75 | 73
2019-08-03 08:30 | 47 | 47 |  |  | 43680.3542 | 72 | 70
2019-08-03 09:00 | 48 | 47 |  |  | 43680.375 | 73 | 71
2019-08-03 09:30 | 46 | 46 |  |  | 43680.3958 | 71 | 70
2019-08-03 10:00 | 46 | 45 |  |  | 43680.4167 | 70 | 68
2019-08-03 10:30 | 43 | 42 |  |  | 43680.4375 | 65 | 63
2019-08-03 11:00 | 40 | 39 |  |  | 43680.4583 | 62 | 60
2019-08-03 11:30 | 38 | 37 |  |  | 43680.4792 | 60 | 58
2019-08-03 12:00 | 41 | 40 |  |  | 43680.5 | 64 | 61
2019-08-03 12:30 | 42 | 41 |  |  | 43680.5208 | 64 | 62
2019-08-03 13:00 | 44 | 43 |  |  | 43680.5417 | 63 | 60
2019-08-03 13:30 | 44 | 43 |  |  | 43680.5625 | 65 | 62
2019-08-03 14:00 | 45 | 44 |  |  | 43680.5833 | 66 | 63
2019-08-03 14:30 | 50 | 49 |  |  | 43680.6042 | 69 | 66
2019-08-03 15:00 | 49 | 48 |  |  | 43680.625 | 73 | 70
2019-08-03 15:30 | 53 | 52 |  |  | 43680.6458 | 77 | 75
2019-08-03 16:00 | 56 | 55 |  |  | 43680.6667 | 81 | 78
2019-08-03 16:30 | 58 | 57 |  |  | 43680.6875 | 85 | 82
2019-08-03 17:00 | 58 | 57 |  |  | 43680.7083 | 87 | 84
2019-08-03 17:30 | 59 | 57 |  |  | 43680.7292 | 90 | 85
2019-08-03 18:00 | 64 | 61 |  |  | 43680.75 | 96 | 91
2019-08-03 18:30 | 64 | 62 |  |  | 43680.7708 | 97 | 93
2019-08-03 19:00 | 66 | 64 |  |  | 43680.7917 | 99 | 94
2019-08-03 19:30 | 63 | 61 |  |  | 43680.8125 | 96 | 92
2019-08-03 20:00 | 62 | 60 |  |  | 43680.8333 | 95 | 90
2019-08-03 20:30 | 62 | 60 |  |  | 43680.8542 | 95 | 90
2019-08-03 21:00 | 60 | 58 |  |  | 43680.875 | 92 | 86
2019-08-03 21:30 | 57 | 55 |  |  | 43680.8958 | 88 | 83
2019-08-03 22:00 | 56 | 55 |  |  | 43680.9167 | 86 | 83
2019-08-03 22:30 | 55 | 54 |  |  | 43680.9375 | 85 | 81
2019-08-03 23:00 | 53 | 52 |  |  | 43680.9583 | 81 | 77
2019-08-03 23:30 | 51 | 49 |  |  | 43680.9792 | 78 | 74
2019-08-04 | 50 | 48 |  |  | 43681 | 75 | 71
2019-08-04 00:30 | 50 | 48 |  |  | 43681.0208 | 74 | 68
2019-08-04 01:00 | 48 | 45 |  |  | 43681.0417 | 71 | 65
2019-08-04 01:30 | 45 | 42 |  |  | 43681.0625 | 67 | 60
2019-08-04 02:00 | 44 | 40 |  |  | 43681.0833 | 65 | 57
2019-08-04 02:30 | 44 | 41 |  |  | 43681.1042 | 66 | 59
2019-08-04 03:00 | 42 | 41 |  |  | 43681.125 | 70 | 58
2019-08-04 03:30 | 42 | 41 |  |  | 43681.1458 | 69 | 56
2019-08-04 04:00 | 42 | 41 |  |  | 43681.1667 | 69 | 56
2019-08-04 04:30 | 40 | 39 |  |  | 43681.1875 | 68 | 55
2019-08-04 05:00 | 40 | 39 |  |  | 43681.2083 | 68 | 54
2019-08-04 05:30 | 41 | 40 |  |  | 43681.2292 | 69 | 56
2019-08-04 06:00 | 41 | 40 |  |  | 43681.25 | 70 | 58
2019-08-04 06:30 | 43 | 42 |  |  | 43681.2708 | 74 | 61
2019-08-04 07:00 | 44 | 43 |  |  | 43681.2917 | 75 | 64
2019-08-04 07:30 | 41 | 41 |  |  | 43681.3125 | 74 | 63
2019-08-04 08:00 | 40 | 39 |  |  | 43681.3333 | 73 | 63
2019-08-04 08:30 | 41 | 41 |  |  | 43681.3542 | 75 | 66
2019-08-04 09:00 | 37 | 37 |  |  | 43681.375 | 70 | 62
2019-08-04 09:30 | 37 | 36 |  |  | 43681.3958 | 68 | 60
2019-08-04 10:00 | 40 | 35 |  |  | 43681.4167 | 64 | 58
2019-08-04 10:30 | 40 | 34 |  |  | 43681.4375 | 63 | 57
2019-08-04 11:00 | 39 | 33 |  |  | 43681.4583 | 62 | 55
2019-08-04 11:30 | 37 | 30 |  |  | 43681.4792 | 57 | 49
2019-08-04 12:00 | 35 | 27 |  |  | 43681.5 | 54 | 45
2019-08-04 12:30 | 35 | 27 |  |  | 43681.5208 | 53 | 45
2019-08-04 13:00 | 34 | 27 |  |  | 43681.5417 | 53 | 45
2019-08-04 13:30 | 35 | 28 |  |  | 43681.5625 | 55 | 47
2019-08-04 14:00 | 37 | 30 |  |  | 43681.5833 | 56 | 49
2019-08-04 14:30 | 40 | 33 |  |  | 43681.6042 | 59 | 52
2019-08-04 15:00 | 41 | 35 |  |  | 43681.625 | 62 | 56
2019-08-04 15:30 | 43 | 38 |  |  | 43681.6458 | 66 | 60
2019-08-04 16:00 | 47 | 42 |  |  | 43681.6667 | 71 | 65
2019-08-04 16:30 | 51 | 47 |  |  | 43681.6875 | 77 | 72
2019-08-04 17:00 | 53 | 50 |  |  | 43681.7083 | 80 | 75
2019-08-04 17:30 | 57 | 54 |  |  | 43681.7292 | 86 | 82
2019-08-04 18:00 | 64 | 61 |  |  | 43681.75 | 95 | 91
2019-08-04 18:30 | 65 | 63 |  |  | 43681.7708 | 99 | 95
2019-08-04 19:00 | 69 | 67 |  |  | 43681.7917 | 102 | 99
2019-08-04 19:30 | 66 | 64 |  |  | 43681.8125 | 99 | 95
2019-08-04 20:00 | 65 | 63 |  |  | 43681.8333 | 98 | 94
2019-08-04 20:30 | 65 | 63 |  |  | 43681.8542 | 98 | 94
2019-08-04 21:00 | 63 | 61 |  |  | 43681.875 | 93 | 89
2019-08-04 21:30 | 59 | 56 |  |  | 43681.8958 | 88 | 84
2019-08-04 22:00 | 59 | 57 |  |  | 43681.9167 | 88 | 84
2019-08-04 22:30 | 61 | 58 |  |  | 43681.9375 | 89 | 85
2019-08-04 23:00 | 59 | 55 |  |  | 43681.9583 | 86 | 81
2019-08-04 23:30 | 56 | 52 |  |  | 43681.9792 | 83 | 77
2019-08-05 | 55 | 51 |  |  | 43682 | 79 | 73
2019-08-05 00:30 | 51 | 46 |  |  | 43682.0208 | 73 | 67
2019-08-05 01:00 | 46 | 41 |  |  | 43682.0417 | 66 | 61
2019-08-05 01:30 | 44 | 38 |  |  | 43682.0625 | 63 | 57
2019-08-05 02:00 | 44 | 38 |  |  | 43682.0833 | 63 | 56
2019-08-05 02:30 | 44 | 38 |  |  | 43682.1042 | 63 | 56
2019-08-05 03:00 | 45 | 39 |  |  | 43682.125 | 64 | 57
2019-08-05 03:30 | 47 | 41 |  |  | 43682.1458 | 66 | 59
2019-08-05 04:00 | 47 | 42 |  |  | 43682.1667 | 66 | 59
2019-08-05 04:30 | 48 | 43 |  |  | 43682.1875 | 68 | 62
2019-08-05 05:00 | 51 | 47 |  |  | 43682.2083 | 71 | 65
2019-08-05 05:30 | 56 | 53 |  |  | 43682.2292 | 76 | 71
2019-08-05 06:00 | 60 | 57 |  |  | 43682.25 | 83 | 78
2019-08-05 06:30 | 66 | 65 |  |  | 43682.2708 | 95 | 92
2019-08-05 07:00 | 75 | 74 |  |  | 43682.2917 | 107 | 106
2019-08-05 07:30 | 80 | 80 |  |  | 43682.3125 | 117 | 117
2019-08-05 08:00 | 72 | 72 |  |  | 43682.3333 | 109 | 109
2019-08-05 08:30 | 68 | 68 |  |  | 43682.3542 | 102 | 102
2019-08-05 09:00 | 59 | 58 |  |  | 43682.375 | 92 | 92
2019-08-05 09:30 | 57 | 56 |  |  | 43682.3958 | 89 | 89
2019-08-05 10:00 | 55 | 54 |  |  | 43682.4167 | 84 | 84
2019-08-05 10:30 | 55 | 54 |  |  | 43682.4375 | 84 | 84
2019-08-05 11:00 | 58 | 57 |  |  | 43682.4583 | 86 | 86
2019-08-05 11:30 | 58 | 57 |  |  | 43682.4792 | 87 | 87
2019-08-05 12:00 | 55 | 54 |  |  | 43682.5 | 83 | 83
2019-08-05 12:30 | 54 | 53 |  |  | 43682.5208 | 82 | 82
2019-08-05 13:00 | 55 | 54 |  |  | 43682.5417 | 84 | 84
2019-08-05 13:30 | 55 | 55 |  |  | 43682.5625 | 83 | 82
2019-08-05 14:00 | 56 | 55 |  |  | 43682.5833 | 82 | 82
2019-08-05 14:30 | 59 | 58 |  |  | 43682.6042 | 85 | 85
2019-08-05 15:00 | 61 | 60 |  |  | 43682.625 | 89 | 89
2019-08-05 15:30 | 62 | 61 |  |  | 43682.6458 | 91 | 91
2019-08-05 16:00 | 64 | 63 |  |  | 43682.6667 | 94 | 94
2019-08-05 16:30 | 65 | 65 |  |  | 43682.6875 | 96 | 96
2019-08-05 17:00 | 69 | 68 |  |  | 43682.7083 | 100 | 99
2019-08-05 17:30 | 74 | 72 |  |  | 43682.7292 | 105 | 105
2019-08-05 18:00 | 80 | 78 |  |  | 43682.75 | 112 | 112
2019-08-05 18:30 | 81 | 79 |  |  | 43682.7708 | 113 | 113
2019-08-05 19:00 | 83 | 81 |  |  | 43682.7917 | 115 | 114
2019-08-05 19:30 | 81 | 79 |  |  | 43682.8125 | 112 | 111
2019-08-05 20:00 | 79 | 77 |  |  | 43682.8333 | 109 | 109
2019-08-05 20:30 | 80 | 78 |  |  | 43682.8542 | 109 | 109
2019-08-05 21:00 | 74 | 72 |  |  | 43682.875 | 102 | 102
2019-08-05 21:30 | 69 | 67 |  |  | 43682.8958 | 95 | 95
2019-08-05 22:00 | 67 | 64 |  |  | 43682.9167 | 93 | 92
2019-08-05 22:30 | 62 | 61 |  |  | 43682.9375 | 88 | 88
2019-08-05 23:00 | 60 | 58 |  |  | 43682.9583 | 84 | 84
2019-08-05 23:30 | 57 | 55 |  |  | 43682.9792 | 80 | 80
2019-08-06 | 55 | 51 |  |  | 43683 | 77 | 76
2019-08-06 00:30 | 61 | 50 |  |  | 43683.0208 | 75 | 72
2019-08-06 01:00 | 60 | 48 |  |  | 43683.0417 | 71 | 68
2019-08-06 01:30 | 58 | 45 |  |  | 43683.0625 | 68 | 64
2019-08-06 02:00 | 54 | 41 |  |  | 43683.0833 | 63 | 59
2019-08-06 02:30 | 55 | 41 |  |  | 43683.1042 | 63 | 59
2019-08-06 03:00 | 56 | 44 |  |  | 43683.125 | 65 | 61
2019-08-06 03:30 | 60 | 47 |  |  | 43683.1458 | 68 | 65
2019-08-06 04:00 | 60 | 48 |  |  | 43683.1667 | 70 | 67
2019-08-06 04:30 | 62 | 50 |  |  | 43683.1875 | 73 | 70
2019-08-06 05:00 | 64 | 54 |  |  | 43683.2083 | 76 | 74
2019-08-06 05:30 | 68 | 61 |  |  | 43683.2292 | 83 | 81
2019-08-06 06:00 | 72 | 66 |  |  | 43683.25 | 90 | 89
2019-08-06 06:30 | 74 | 69 |  |  | 43683.2708 | 98 | 97
2019-08-06 07:00 | 79 | 76 |  |  | 43683.2917 | 110 | 109
2019-08-06 07:30 | 83 | 80 |  |  | 43683.3125 | 118 | 118
2019-08-06 08:00 | 78 | 73 |  |  | 43683.3333 | 112 | 111
2019-08-06 08:30 | 70 | 65 |  |  | 43683.3542 | 102 | 102
2019-08-06 09:00 | 65 | 58 |  |  | 43683.375 | 94 | 93
2019-08-06 09:30 | 58 | 53 |  |  | 43683.3958 | 86 | 86
2019-08-06 10:00 | 55 | 51 |  |  | 43683.4167 | 82 | 82
2019-08-06 10:30 | 56 | 52 |  |  | 43683.4375 | 81 | 81
2019-08-06 11:00 | 55 | 50 |  |  | 43683.4583 | 79 | 79
2019-08-06 11:30 | 53 | 49 |  |  | 43683.4792 | 78 | 78
2019-08-06 12:00 | 53 | 49 |  |  | 43683.5 | 78 | 78
2019-08-06 12:30 | 55 | 50 |  |  | 43683.5208 | 79 | 79
2019-08-06 13:00 | 57 | 52 |  |  | 43683.5417 | 81 | 81
2019-08-06 13:30 | 57 | 53 |  |  | 43683.5625 | 84 | 84
2019-08-06 14:00 | 62 | 58 |  |  | 43683.5833 | 89 | 89
2019-08-06 14:30 | 63 | 59 |  |  | 43683.6042 | 88 | 88
2019-08-06 15:00 | 64 | 60 |  |  | 43683.625 | 88 | 88
2019-08-06 15:30 | 67 | 63 |  |  | 43683.6458 | 93 | 93
2019-08-06 16:00 | 69 | 65 |  |  | 43683.6667 | 95 | 95
2019-08-06 16:30 | 71 | 68 |  |  | 43683.6875 | 97 | 97
2019-08-06 17:00 | 75 | 72 |  |  | 43683.7083 | 102 | 101
2019-08-06 17:30 | 79 | 75 |  |  | 43683.7292 | 106 | 106
2019-08-06 18:00 | 83 | 80 |  |  | 43683.75 | 113 | 113
2019-08-06 18:30 | 84 | 81 |  |  | 43683.7708 | 114 | 113
2019-08-06 19:00 | 84 | 82 |  |  | 43683.7917 | 115 | 114
2019-08-06 19:30 | 81 | 78 |  |  | 43683.8125 | 111 | 110
2019-08-06 20:00 | 80 | 76 |  |  | 43683.8333 | 108 | 107
2019-08-06 20:30 | 80 | 76 |  |  | 43683.8542 | 108 | 107
2019-08-06 21:00 | 77 | 73 |  |  | 43683.875 | 103 | 102
2019-08-06 21:30 | 72 | 68 |  |  | 43683.8958 | 95 | 94
2019-08-06 22:00 | 69 | 64 |  |  | 43683.9167 | 93 | 91
2019-08-06 22:30 | 67 | 61 |  |  | 43683.9375 | 89 | 88
2019-08-06 23:00 | 66 | 60 |  |  | 43683.9583 | 86 | 84
2019-08-06 23:30 | 62 | 55 |  |  | 43683.9792 | 80 | 78
2019-08-07 | 61 | 52 |  |  | 43684 | 77 | 74
2019-08-07 00:30 | 60 | 50 |  |  | 43684.0208 | 73 | 70
2019-08-07 01:00 | 58 | 46 |  |  | 43684.0417 | 70 | 65
2019-08-07 01:30 | 56 | 44 |  |  | 43684.0625 | 67 | 62
2019-08-07 02:00 | 56 | 42 |  |  | 43684.0833 | 65 | 60
2019-08-07 02:30 | 55 | 42 |  |  | 43684.1042 | 65 | 60
2019-08-07 03:00 | 54 | 43 |  |  | 43684.125 | 63 | 60
2019-08-07 03:30 | 54 | 43 |  |  | 43684.1458 | 63 | 61
2019-08-07 04:00 | 54 | 43 |  |  | 43684.1667 | 64 | 62
2019-08-07 04:30 | 55 | 46 |  |  | 43684.1875 | 66 | 64
2019-08-07 05:00 | 59 | 50 |  |  | 43684.2083 | 70 | 68
2019-08-07 05:30 | 64 | 56 |  |  | 43684.2292 | 78 | 76
2019-08-07 06:00 | 67 | 61 |  |  | 43684.25 | 85 | 84
2019-08-07 06:30 | 71 | 66 |  |  | 43684.2708 | 94 | 94
2019-08-07 07:00 | 76 | 72 |  |  | 43684.2917 | 105 | 105
2019-08-07 07:30 | 83 | 79 |  |  | 43684.3125 | 117 | 116
2019-08-07 08:00 | 86 | 79 |  |  | 43684.3333 | 119 | 117
2019-08-07 08:30 | 82 | 75 |  |  | 43684.3542 | 115 | 113
2019-08-07 09:00 | 77 | 70 |  |  | 43684.375 | 108 | 107
2019-08-07 09:30 | 76 | 69 |  |  | 43684.3958 | 104 | 102
2019-08-07 10:00 | 75 | 68 |  |  | 43684.4167 | 101 | 99
2019-08-07 10:30 | 71 | 63 |  |  | 43684.4375 | 95 | 93
2019-08-07 11:00 | 69 | 59 |  |  | 43684.4583 | 93 | 90
2019-08-07 11:30 | 69 | 60 |  |  | 43684.4792 | 96 | 93
2019-08-07 12:00 | 67 | 58 |  |  | 43684.5 | 92 | 90
2019-08-07 12:30 | 67 | 57 |  |  | 43684.5208 | 92 | 89
2019-08-07 13:00 | 71 | 62 |  |  | 43684.5417 | 99 | 97
2019-08-07 13:30 | 75 | 67 |  |  | 43684.5625 | 105 | 102
2019-08-07 14:00 | 79 | 72 |  |  | 43684.5833 | 108 | 106
2019-08-07 14:30 | 78 | 70 |  |  | 43684.6042 | 107 | 105
2019-08-07 15:00 | 79 | 71 |  |  | 43684.625 | 107 | 105
2019-08-07 15:30 | 78 | 70 |  |  | 43684.6458 | 106 | 104
2019-08-07 16:00 | 86 | 78 |  |  | 43684.6667 | 115 | 112
2019-08-07 16:30 | 84 | 76 |  |  | 43684.6875 | 113 | 110
2019-08-07 17:00 | 87 | 79 |  |  | 43684.7083 | 117 | 114
2019-08-07 17:30 | 90 | 81 |  |  | 43684.7292 | 120 | 117
2019-08-07 18:00 | 92 | 85 |  |  | 43684.75 | 123 | 120
2019-08-07 18:30 | 93 | 85 |  |  | 43684.7708 | 123 | 119
2019-08-07 19:00 | 94 | 85 |  |  | 43684.7917 | 124 | 120
2019-08-07 19:30 | 92 | 84 |  |  | 43684.8125 | 121 | 117
2019-08-07 20:00 | 90 | 82 |  |  | 43684.8333 | 119 | 115
2019-08-07 20:30 | 89 | 81 |  |  | 43684.8542 | 118 | 113
2019-08-07 21:00 | 86 | 77 |  |  | 43684.875 | 112 | 108
2019-08-07 21:30 | 82 | 73 |  |  | 43684.8958 | 107 | 102
2019-08-07 22:00 | 78 | 71 |  |  | 43684.9167 | 102 | 99
2019-08-07 22:30 | 74 | 66 |  |  | 43684.9375 | 96 | 94
2019-08-07 23:00 | 71 | 63 |  |  | 43684.9583 | 91 | 88
2019-08-07 23:30 | 70 | 62 |  |  | 43684.9792 | 89 | 86
2019-08-08 | 68 | 58 |  |  | 43685 | 85 | 81
2019-08-08 00:30 | 67 | 55 |  |  | 43685.0208 | 80 | 76
2019-08-08 01:00 | 64 | 52 |  |  | 43685.0417 | 75 | 70
2019-08-08 01:30 | 61 | 48 |  |  | 43685.0625 | 71 | 66
2019-08-08 02:00 | 59 | 45 |  |  | 43685.0833 | 68 | 62
2019-08-08 02:30 | 59 | 44 |  |  | 43685.1042 | 66 | 60
2019-08-08 03:00 | 59 | 44 |  |  | 43685.125 | 66 | 60
2019-08-08 03:30 | 58 | 43 |  |  | 43685.1458 | 66 | 60
2019-08-08 04:00 | 59 | 45 |  |  | 43685.1667 | 67 | 61
2019-08-08 04:30 | 61 | 48 |  |  | 43685.1875 | 69 | 64
2019-08-08 05:00 | 65 | 52 |  |  | 43685.2083 | 74 | 68
2019-08-08 05:30 | 68 | 57 |  |  | 43685.2292 | 80 | 76
2019-08-08 06:00 | 71 | 62 |  |  | 43685.25 | 85 | 82
2019-08-08 06:30 | 76 | 68 |  |  | 43685.2708 | 96 | 94
2019-08-08 07:00 | 81 | 75 |  |  | 43685.2917 | 107 | 106
2019-08-08 07:30 | 85 | 80 |  |  | 43685.3125 | 115 | 115
2019-08-08 08:00 | 80 | 75 |  |  | 43685.3333 | 112 | 112
2019-08-08 08:30 | 72 | 71 |  |  | 43685.3542 | 106 | 106
2019-08-08 09:00 | 65 | 64 |  |  | 43685.375 | 95 | 95
2019-08-08 09:30 | 67 | 66 |  |  | 43685.3958 | 95 | 95
2019-08-08 10:00 | 64 | 63 |  |  | 43685.4167 | 90 | 90
2019-08-08 10:30 | 56 | 55 |  |  | 43685.4375 | 83 | 83
2019-08-08 11:00 | 53 | 52 |  |  | 43685.4583 | 80 | 80
2019-08-08 11:30 | 53 | 51 |  |  | 43685.4792 | 80 | 80
2019-08-08 12:00 | 53 | 51 |  |  | 43685.5 | 80 | 79
2019-08-08 12:30 | 54 | 52 |  |  | 43685.5208 | 81 | 81
2019-08-08 13:00 | 57 | 56 |  |  | 43685.5417 | 84 | 84
2019-08-08 13:30 | 62 | 61 |  |  | 43685.5625 | 88 | 87
2019-08-08 14:00 | 62 | 61 |  |  | 43685.5833 | 91 | 90
2019-08-08 14:30 | 61 | 60 |  |  | 43685.6042 | 89 | 89
2019-08-08 15:00 | 61 | 60 |  |  | 43685.625 | 89 | 89
2019-08-08 15:30 | 66 | 65 |  |  | 43685.6458 | 96 | 95
2019-08-08 16:00 | 69 | 68 |  |  | 43685.6667 | 100 | 100
2019-08-08 16:30 | 72 | 71 |  |  | 43685.6875 | 102 | 102
2019-08-08 17:00 | 72 | 71 |  |  | 43685.7083 | 103 | 103
2019-08-08 17:30 | 77 | 76 |  |  | 43685.7292 | 108 | 108
2019-08-08 18:00 | 82 | 81 |  |  | 43685.75 | 114 | 114
2019-08-08 18:30 | 83 | 81 |  |  | 43685.7708 | 115 | 115
2019-08-08 19:00 | 84 | 83 |  |  | 43685.7917 | 117 | 117
2019-08-08 19:30 | 83 | 82 |  |  | 43685.8125 | 114 | 114
2019-08-08 20:00 | 83 | 82 |  |  | 43685.8333 | 112 | 112
2019-08-08 20:30 | 81 | 80 |  |  | 43685.8542 | 111 | 111
2019-08-08 21:00 | 76 | 74 |  |  | 43685.875 | 104 | 104
2019-08-08 21:30 | 71 | 69 |  |  | 43685.8958 | 97 | 97
2019-08-08 22:00 | 69 | 67 |  |  | 43685.9167 | 95 | 94
2019-08-08 22:30 | 66 | 63 |  |  | 43685.9375 | 92 | 91
2019-08-08 23:00 | 65 | 62 |  |  | 43685.9583 | 88 | 87
2019-08-08 23:30 | 61 | 57 |  |  | 43685.9792 | 83 | 82
2019-08-09 | 57 | 53 |  |  | 43686 | 77 | 76
2019-08-09 00:30 | 56 | 51 |  |  | 43686.0208 | 73 | 71
2019-08-09 01:00 | 53 | 48 |  |  | 43686.0417 | 69 | 67
2019-08-09 01:30 | 52 | 46 |  |  | 43686.0625 | 66 | 64
2019-08-09 02:00 | 51 | 45 |  |  | 43686.0833 | 64 | 61
2019-08-09 02:30 | 50 | 43 |  |  | 43686.1042 | 62 | 59
2019-08-09 03:00 | 50 | 43 |  |  | 43686.125 | 63 | 60
2019-08-09 03:30 | 57 | 45 |  |  | 43686.1458 | 66 | 61
2019-08-09 04:00 | 62 | 45 |  |  | 43686.1667 | 67 | 61
2019-08-09 04:30 | 61 | 44 |  |  | 43686.1875 | 67 | 61
2019-08-09 05:00 | 64 | 48 |  |  | 43686.2083 | 71 | 66
2019-08-09 05:30 | 68 | 56 |  |  | 43686.2292 | 78 | 74
2019-08-09 06:00 | 70 | 59 |  |  | 43686.25 | 82 | 79
2019-08-09 06:30 | 74 | 65 |  |  | 43686.2708 | 91 | 90
2019-08-09 07:00 | 79 | 72 |  |  | 43686.2917 | 102 | 101
2019-08-09 07:30 | 81 | 75 |  |  | 43686.3125 | 108 | 107
2019-08-09 08:00 | 74 | 68 |  |  | 43686.3333 | 101 | 100
2019-08-09 08:30 | 67 | 59 |  |  | 43686.3542 | 90 | 90
2019-08-09 09:00 | 64 | 55 |  |  | 43686.375 | 85 | 85
2019-08-09 09:30 | 58 | 48 |  |  | 43686.3958 | 77 | 76
2019-08-09 10:00 | 56 | 46 |  |  | 43686.4167 | 74 | 73
2019-08-09 10:30 | 54 | 45 |  |  | 43686.4375 | 72 | 72
2019-08-09 11:00 | 52 | 43 |  |  | 43686.4583 | 69 | 69
2019-08-09 11:30 | 51 | 42 |  |  | 43686.4792 | 67 | 67
2019-08-09 12:00 | 50 | 40 |  |  | 43686.5 | 66 | 65
2019-08-09 12:30 | 49 | 39 |  |  | 43686.5208 | 65 | 64
2019-08-09 13:00 | 50 | 40 |  |  | 43686.5417 | 67 | 66
2019-08-09 13:30 | 50 | 40 |  |  | 43686.5625 | 67 | 66
2019-08-09 14:00 | 52 | 42 |  |  | 43686.5833 | 68 | 67
2019-08-09 14:30 | 54 | 45 |  |  | 43686.6042 | 71 | 71
2019-08-09 15:00 | 56 | 48 |  |  | 43686.625 | 75 | 75
2019-08-09 15:30 | 59 | 50 |  |  | 43686.6458 | 79 | 78
2019-08-09 16:00 | 65 | 57 |  |  | 43686.6667 | 87 | 86
2019-08-09 16:30 | 67 | 60 |  |  | 43686.6875 | 89 | 89
2019-08-09 17:00 | 70 | 63 |  |  | 43686.7083 | 94 | 94
2019-08-09 17:30 | 74 | 67 |  |  | 43686.7292 | 99 | 98
2019-08-09 18:00 | 77 | 70 |  |  | 43686.75 | 103 | 102
2019-08-09 18:30 | 77 | 70 |  |  | 43686.7708 | 103 | 101
2019-08-09 19:00 | 78 | 71 |  |  | 43686.7917 | 104 | 102
2019-08-09 19:30 | 78 | 70 |  |  | 43686.8125 | 102 | 101
2019-08-09 20:00 | 77 | 70 |  |  | 43686.8333 | 100 | 99
2019-08-09 20:30 | 75 | 67 |  |  | 43686.8542 | 97 | 96
2019-08-09 21:00 | 71 | 63 |  |  | 43686.875 | 92 | 90
2019-08-09 21:30 | 69 | 60 |  |  | 43686.8958 | 88 | 86
2019-08-09 22:00 | 68 | 59 |  |  | 43686.9167 | 87 | 85
2019-08-09 22:30 | 66 | 56 |  |  | 43686.9375 | 84 | 82
2019-08-09 23:00 | 63 | 53 |  |  | 43686.9583 | 78 | 76
2019-08-09 23:30 | 61 | 49 |  |  | 43686.9792 | 74 | 71
2019-08-10 | 59 | 45 |  |  | 43687 | 69 | 66
2019-08-10 00:30 | 57 | 41 |  |  | 43687.0208 | 65 | 61
2019-08-10 01:00 | 57 | 40 |  |  | 43687.0417 | 63 | 58
2019-08-10 01:30 | 58 | 40 |  |  | 43687.0625 | 62 | 57
2019-08-10 02:00 | 57 | 38 |  |  | 43687.0833 | 61 | 54
2019-08-10 02:30 | 56 | 36 |  |  | 43687.1042 | 59 | 53
2019-08-10 03:00 | 55 | 35 |  |  | 43687.125 | 58 | 52
2019-08-10 03:30 | 55 | 36 |  |  | 43687.1458 | 59 | 52
2019-08-10 04:00 | 56 | 37 |  |  | 43687.1667 | 60 | 54
2019-08-10 04:30 | 58 | 39 |  |  | 43687.1875 | 62 | 55
2019-08-10 05:00 | 58 | 40 |  |  | 43687.2083 | 63 | 57
2019-08-10 05:30 | 60 | 42 |  |  | 43687.2292 | 65 | 59
2019-08-10 06:00 | 61 | 45 |  |  | 43687.25 | 68 | 63
2019-08-10 06:30 | 60 | 44 |  |  | 43687.2708 | 69 | 64
2019-08-10 07:00 | 59 | 43 |  |  | 43687.2917 | 70 | 65
2019-08-10 07:30 | 58 | 43 |  |  | 43687.3125 | 70 | 66
2019-08-10 08:00 | 54 | 39 |  |  | 43687.3333 | 66 | 62
2019-08-10 08:30 | 52 | 37 |  |  | 43687.3542 | 64 | 61
2019-08-10 09:00 | 51 | 35 |  |  | 43687.375 | 61 | 58
2019-08-10 09:30 | 51 | 35 |  |  | 43687.3958 | 61 | 58
2019-08-10 10:00 | 50 | 34 |  |  | 43687.4167 | 59 | 56
2019-08-10 10:30 | 49 | 32 |  |  | 43687.4375 | 56 | 53
2019-08-10 11:00 | 49 | 32 |  |  | 43687.4583 | 55 | 51
2019-08-10 11:30 | 47 | 29 |  |  | 43687.4792 | 51 | 48
2019-08-10 12:00 | 45 | 26 |  |  | 43687.5 | 49 | 45
2019-08-10 12:30 | 45 | 25 |  |  | 43687.5208 | 47 | 43
2019-08-10 13:00 | 44 | 24 |  |  | 43687.5417 | 46 | 41
2019-08-10 13:30 | 45 | 25 |  |  | 43687.5625 | 47 | 43
2019-08-10 14:00 | 46 | 27 |  |  | 43687.5833 | 50 | 46
2019-08-10 14:30 | 47 | 28 |  |  | 43687.6042 | 51 | 47
2019-08-10 15:00 | 47 | 29 |  |  | 43687.625 | 53 | 49
2019-08-10 15:30 | 50 | 34 |  |  | 43687.6458 | 58 | 55
2019-08-10 16:00 | 55 | 40 |  |  | 43687.6667 | 66 | 64
2019-08-10 16:30 | 59 | 46 |  |  | 43687.6875 | 73 | 70
2019-08-10 17:00 | 61 | 49 |  |  | 43687.7083 | 78 | 76
2019-08-10 17:30 | 65 | 54 |  |  | 43687.7292 | 84 | 82
2019-08-10 18:00 | 69 | 60 |  |  | 43687.75 | 91 | 90
2019-08-10 18:30 | 71 | 63 |  |  | 43687.7708 | 95 | 93
2019-08-10 19:00 | 72 | 63 |  |  | 43687.7917 | 95 | 94
2019-08-10 19:30 | 71 | 62 |  |  | 43687.8125 | 94 | 92
2019-08-10 20:00 | 71 | 62 |  |  | 43687.8333 | 93 | 92
2019-08-10 20:30 | 69 | 60 |  |  | 43687.8542 | 91 | 89
2019-08-10 21:00 | 67 | 58 |  |  | 43687.875 | 88 | 86
2019-08-10 21:30 | 65 | 55 |  |  | 43687.8958 | 84 | 82
2019-08-10 22:00 | 65 | 55 |  |  | 43687.9167 | 83 | 82
2019-08-10 22:30 | 65 | 55 |  |  | 43687.9375 | 84 | 82
2019-08-10 23:00 | 66 | 55 |  |  | 43687.9583 | 82 | 80
2019-08-10 23:30 | 62 | 50 |  |  | 43687.9792 | 77 | 74
2019-08-11 | 60 | 47 |  |  | 43688 | 73 | 70
2019-08-11 00:30 | 62 | 47 |  |  | 43688.0208 | 72 | 68
2019-08-11 01:00 | 62 | 46 |  |  | 43688.0417 | 70 | 65
2019-08-11 01:30 | 59 | 42 |  |  | 43688.0625 | 65 | 60
2019-08-11 02:00 | 58 | 41 |  |  | 43688.0833 | 65 | 59
2019-08-11 02:30 | 58 | 41 |  |  | 43688.1042 | 65 | 58
2019-08-11 03:00 | 54 | 38 |  |  | 43688.125 | 60 | 55
2019-08-11 03:30 | 54 | 39 |  |  | 43688.1458 | 61 | 57
2019-08-11 04:00 | 55 | 40 |  |  | 43688.1667 | 61 | 57
2019-08-11 04:30 | 55 | 41 |  |  | 43688.1875 | 62 | 57
2019-08-11 05:00 | 55 | 41 |  |  | 43688.2083 | 62 | 58
2019-08-11 05:30 | 56 | 42 |  |  | 43688.2292 | 64 | 60
2019-08-11 06:00 | 59 | 45 |  |  | 43688.25 | 68 | 64
2019-08-11 06:30 | 59 | 46 |  |  | 43688.2708 | 71 | 67
2019-08-11 07:00 | 59 | 45 |  |  | 43688.2917 | 72 | 68
2019-08-11 07:30 | 53 | 41 |  |  | 43688.3125 | 69 | 66
2019-08-11 08:00 | 43 | 29 |  |  | 43688.3333 | 58 | 57
2019-08-11 08:30 | 43 | 30 |  |  | 43688.3542 | 59 | 58
2019-08-11 09:00 | 43 | 30 |  |  | 43688.375 | 59 | 58
2019-08-11 09:30 | 43 | 29 |  |  | 43688.3958 | 58 | 57
2019-08-11 10:00 | 42 | 27 |  |  | 43688.4167 | 55 | 54
2019-08-11 10:30 | 39 | 25 |  |  | 43688.4375 | 52 | 51
2019-08-11 11:00 | 45 | 28 |  |  | 43688.4583 | 51 | 49
2019-08-11 11:30 | 43 | 27 |  |  | 43688.4792 | 49 | 47
2019-08-11 12:00 | 42 | 25 |  |  | 43688.5 | 47 | 44
2019-08-11 12:30 | 43 | 26 |  |  | 43688.5208 | 48 | 45
2019-08-11 13:00 | 43 | 25 |  |  | 43688.5417 | 48 | 45
2019-08-11 13:30 | 43 | 26 |  |  | 43688.5625 | 48 | 45
2019-08-11 14:00 | 43 | 26 |  |  | 43688.5833 | 47 | 44
2019-08-11 14:30 | 45 | 30 |  |  | 43688.6042 | 51 | 48
2019-08-11 15:00 | 47 | 32 |  |  | 43688.625 | 54 | 52
2019-08-11 15:30 | 50 | 36 |  |  | 43688.6458 | 60 | 58
2019-08-11 16:00 | 53 | 41 |  |  | 43688.6667 | 66 | 64
2019-08-11 16:30 | 56 | 45 |  |  | 43688.6875 | 72 | 71
2019-08-11 17:00 | 61 | 52 |  |  | 43688.7083 | 81 | 79
2019-08-11 17:30 | 66 | 57 |  |  | 43688.7292 | 87 | 85
2019-08-11 18:00 | 75 | 69 |  |  | 43688.75 | 99 | 99
2019-08-11 18:30 | 78 | 73 |  |  | 43688.7708 | 106 | 106
2019-08-11 19:00 | 81 | 75 |  |  | 43688.7917 | 108 | 108
2019-08-11 19:30 | 80 | 75 |  |  | 43688.8125 | 107 | 107
2019-08-11 20:00 | 79 | 73 |  |  | 43688.8333 | 105 | 105
2019-08-11 20:30 | 79 | 73 |  |  | 43688.8542 | 105 | 105
2019-08-11 21:00 | 75 | 69 |  |  | 43688.875 | 100 | 100
2019-08-11 21:30 | 72 | 66 |  |  | 43688.8958 | 96 | 96
2019-08-11 22:00 | 71 | 65 |  |  | 43688.9167 | 94 | 94
2019-08-11 22:30 | 69 | 63 |  |  | 43688.9375 | 92 | 92
2019-08-11 23:00 | 67 | 61 |  |  | 43688.9583 | 87 | 87
2019-08-11 23:30 | 67 | 60 |  |  | 43688.9792 | 85 | 85
2019-08-12 | 64 | 55 |  |  | 43689 | 80 | 80
2019-08-12 00:30 | 62 | 52 |  |  | 43689.0208 | 75 | 74
2019-08-12 01:00 | 60 | 49 |  |  | 43689.0417 | 70 | 70
2019-08-12 01:30 | 58 | 46 |  |  | 43689.0625 | 66 | 66
2019-08-12 02:00 | 56 | 45 |  |  | 43689.0833 | 65 | 64
2019-08-12 02:30 | 54 | 43 |  |  | 43689.1042 | 62 | 62
2019-08-12 03:00 | 53 | 42 |  |  | 43689.125 | 62 | 62
2019-08-12 03:30 | 54 | 44 |  |  | 43689.1458 | 63 | 63
2019-08-12 04:00 | 54 | 43 |  |  | 43689.1667 | 62 | 62
2019-08-12 04:30 | 55 | 44 |  |  | 43689.1875 | 63 | 63
2019-08-12 05:00 | 58 | 48 |  |  | 43689.2083 | 67 | 67
2019-08-12 05:30 | 62 | 55 |  |  | 43689.2292 | 75 | 75
2019-08-12 06:00 | 66 | 61 |  |  | 43689.25 | 83 | 83
2019-08-12 06:30 | 74 | 66 |  |  | 43689.2708 | 94 | 93
2019-08-12 07:00 | 79 | 74 |  |  | 43689.2917 | 106 | 106
2019-08-12 07:30 | 82 | 78 |  |  | 43689.3125 | 115 | 115
2019-08-12 08:00 | 74 | 70 |  |  | 43689.3333 | 108 | 108
2019-08-12 08:30 | 69 | 65 |  |  | 43689.3542 | 101 | 101
2019-08-12 09:00 | 66 | 62 |  |  | 43689.375 | 97 | 97
2019-08-12 09:30 | 60 | 55 |  |  | 43689.3958 | 88 | 88
2019-08-12 10:00 | 57 | 51 |  |  | 43689.4167 | 83 | 83
2019-08-12 10:30 | 56 | 51 |  |  | 43689.4375 | 81 | 81
2019-08-12 11:00 | 54 | 50 |  |  | 43689.4583 | 80 | 79
2019-08-12 11:30 | 52 | 48 |  |  | 43689.4792 | 77 | 77
2019-08-12 12:00 | 51 | 46 |  |  | 43689.5 | 75 | 74
2019-08-12 12:30 | 50 | 45 |  |  | 43689.5208 | 75 | 74
2019-08-12 13:00 | 50 | 45 |  |  | 43689.5417 | 74 | 73
2019-08-12 13:30 | 51 | 46 |  |  | 43689.5625 | 75 | 74
2019-08-12 14:00 | 53 | 49 |  |  | 43689.5833 | 77 | 76
2019-08-12 14:30 | 54 | 50 |  |  | 43689.6042 | 78 | 77
2019-08-12 15:00 | 54 | 50 |  |  | 43689.625 | 80 | 79
2019-08-12 15:30 | 59 | 55 |  |  | 43689.6458 | 85 | 84
2019-08-12 16:00 | 64 | 60 |  |  | 43689.6667 | 92 | 91
2019-08-12 16:30 | 70 | 67 |  |  | 43689.6875 | 98 | 98
2019-08-12 17:00 | 74 | 68 |  |  | 43689.7083 | 101 | 101
2019-08-12 17:30 | 78 | 73 |  |  | 43689.7292 | 107 | 107
2019-08-12 18:00 | 85 | 80 |  |  | 43689.75 | 117 | 117
2019-08-12 18:30 | 88 | 83 |  |  | 43689.7708 | 120 | 120
2019-08-12 19:00 | 89 | 84 |  |  | 43689.7917 | 122 | 121
2019-08-12 19:30 | 87 | 82 |  |  | 43689.8125 | 119 | 119
2019-08-12 20:00 | 87 | 82 |  |  | 43689.8333 | 118 | 118
2019-08-12 20:30 | 85 | 80 |  |  | 43689.8542 | 117 | 117
2019-08-12 21:00 | 84 | 78 |  |  | 43689.875 | 111 | 111
2019-08-12 21:30 | 80 | 73 |  |  | 43689.8958 | 105 | 104
2019-08-12 22:00 | 77 | 71 |  |  | 43689.9167 | 101 | 101
2019-08-12 22:30 | 72 | 67 |  |  | 43689.9375 | 97 | 96
2019-08-12 23:00 | 69 | 63 |  |  | 43689.9583 | 90 | 90
2019-08-12 23:30 | 64 | 57 |  |  | 43689.9792 | 83 | 83
2019-08-13 | 59 | 52 |  |  | 43690 | 78 | 77
2019-08-13 00:30 | 58 | 49 |  |  | 43690.0208 | 72 | 72
2019-08-13 01:00 | 58 | 49 |  |  | 43690.0417 | 70 | 69
2019-08-13 01:30 | 59 | 48 |  |  | 43690.0625 | 69 | 69
2019-08-13 02:00 | 58 | 47 |  |  | 43690.0833 | 67 | 66
2019-08-13 02:30 | 57 | 46 |  |  | 43690.1042 | 66 | 66
2019-08-13 03:00 | 55 | 45 |  |  | 43690.125 | 64 | 64
2019-08-13 03:30 | 54 | 44 |  |  | 43690.1458 | 62 | 62
2019-08-13 04:00 | 54 | 44 |  |  | 43690.1667 | 63 | 63
2019-08-13 04:30 | 58 | 49 |  |  | 43690.1875 | 69 | 69
2019-08-13 05:00 | 61 | 53 |  |  | 43690.2083 | 74 | 74
2019-08-13 05:30 | 67 | 61 |  |  | 43690.2292 | 83 | 83
2019-08-13 06:00 | 72 | 67 |  |  | 43690.25 | 91 | 91
2019-08-13 06:30 | 78 | 73 |  |  | 43690.2708 | 105 | 105
2019-08-13 07:00 | 83 | 80 |  |  | 43690.2917 | 117 | 117
2019-08-13 07:30 | 83 | 81 |  |  | 43690.3125 | 124 | 123
2019-08-13 08:00 | 78 | 76 |  |  | 43690.3333 | 118 | 117
2019-08-13 08:30 | 71 | 68 |  |  | 43690.3542 | 110 | 109
2019-08-13 09:00 | 63 | 60 |  |  | 43690.375 | 99 | 98
2019-08-13 09:30 | 59 | 55 |  |  | 43690.3958 | 92 | 91
2019-08-13 10:00 | 53 | 52 |  |  | 43690.4167 | 90 | 86
2019-08-13 10:30 | 52 | 52 |  |  | 43690.4375 | 86 | 84
2019-08-13 11:00 | 50 | 50 |  |  | 43690.4583 | 81 | 81
2019-08-13 11:30 | 48 | 48 |  |  | 43690.4792 | 79 | 79
2019-08-13 12:00 | 49 | 49 |  |  | 43690.5 | 78 | 77
2019-08-13 12:30 | 54 | 54 |  |  | 43690.5208 | 80 | 80
2019-08-13 13:00 | 56 | 56 |  |  | 43690.5417 | 86 | 85
2019-08-13 13:30 | 57 | 56 |  |  | 43690.5625 | 87 | 87
2019-08-13 14:00 | 58 | 57 |  |  | 43690.5833 | 89 | 88
2019-08-13 14:30 | 60 | 60 |  |  | 43690.6042 | 89 | 88
2019-08-13 15:00 | 56 | 56 |  |  | 43690.625 | 84 | 84
2019-08-13 15:30 | 55 | 54 |  |  | 43690.6458 | 84 | 83
2019-08-13 16:00 | 58 | 58 |  |  | 43690.6667 | 89 | 88
2019-08-13 16:30 | 63 | 62 |  |  | 43690.6875 | 93 | 93
2019-08-13 17:00 | 69 | 67 |  |  | 43690.7083 | 100 | 100
2019-08-13 17:30 | 74 | 72 |  |  | 43690.7292 | 105 | 104
2019-08-13 18:00 | 78 | 77 |  |  | 43690.75 | 111 | 111
2019-08-13 18:30 | 82 | 81 |  |  | 43690.7708 | 116 | 116
2019-08-13 19:00 | 82 | 81 |  |  | 43690.7917 | 116 | 116
2019-08-13 19:30 | 81 | 80 |  |  | 43690.8125 | 114 | 114
2019-08-13 20:00 | 80 | 79 |  |  | 43690.8333 | 113 | 113
2019-08-13 20:30 | 79 | 78 |  |  | 43690.8542 | 112 | 112
2019-08-13 21:00 | 77 | 76 |  |  | 43690.875 | 108 | 108
2019-08-13 21:30 | 73 | 72 |  |  | 43690.8958 | 104 | 104
2019-08-13 22:00 | 70 | 69 |  |  | 43690.9167 | 103 | 103
2019-08-13 22:30 | 67 | 66 |  |  | 43690.9375 | 98 | 98
2019-08-13 23:00 | 65 | 64 |  |  | 43690.9583 | 93 | 93
2019-08-13 23:30 | 58 | 57 |  |  | 43690.9792 | 85 | 84
2019-08-14 | 53 | 51 |  |  | 43691 | 77 | 77
2019-08-14 00:30 | 48 | 46 |  |  | 43691.0208 | 70 | 69
2019-08-14 01:00 | 45 | 43 |  |  | 43691.0417 | 65 | 64
2019-08-14 01:30 | 42 | 40 |  |  | 43691.0625 | 61 | 61
2019-08-14 02:00 | 42 | 39 |  |  | 43691.0833 | 60 | 60
2019-08-14 02:30 | 43 | 40 |  |  | 43691.1042 | 62 | 62
2019-08-14 03:00 | 43 | 40 |  |  | 43691.125 | 62 | 62
2019-08-14 03:30 | 42 | 39 |  |  | 43691.1458 | 62 | 61
2019-08-14 04:00 | 44 | 41 |  |  | 43691.1667 | 62 | 62
2019-08-14 04:30 | 45 | 42 |  |  | 43691.1875 | 64 | 63
2019-08-14 05:00 | 46 | 43 |  |  | 43691.2083 | 66 | 66
2019-08-14 05:30 | 49 | 46 |  |  | 43691.2292 | 71 | 70
2019-08-14 06:00 | 52 | 50 |  |  | 43691.25 | 74 | 74
2019-08-14 06:30 | 53 | 51 |  |  | 43691.2708 | 78 | 78
2019-08-14 07:00 | 54 | 51 |  |  | 43691.2917 | 82 | 81
2019-08-14 07:30 | 53 | 50 |  |  | 43691.3125 | 83 | 82
2019-08-14 08:00 | 51 | 49 |  |  | 43691.3333 | 80 | 79
2019-08-14 08:30 | 51 | 49 |  |  | 43691.3542 | 79 | 78
2019-08-14 09:00 | 47 | 45 |  |  | 43691.375 | 75 | 75
2019-08-14 09:30 | 44 | 43 |  |  | 43691.3958 | 72 | 72
2019-08-14 10:00 | 45 | 42 |  |  | 43691.4167 | 73 | 73
2019-08-14 10:30 | 46 | 44 |  |  | 43691.4375 | 72 | 71
2019-08-14 11:00 | 43 | 40 |  |  | 43691.4583 | 65 | 65
2019-08-14 11:30 | 43 | 40 |  |  | 43691.4792 | 63 | 62
2019-08-14 12:00 | 41 | 38 |  |  | 43691.5 | 64 | 64
2019-08-14 12:30 | 39 | 36 |  |  | 43691.5208 | 63 | 63
2019-08-14 13:00 | 39 | 36 |  |  | 43691.5417 | 63 | 62
2019-08-14 13:30 | 43 | 40 |  |  | 43691.5625 | 60 | 59
2019-08-14 14:00 | 49 | 46 |  |  | 43691.5833 | 62 | 61
2019-08-14 14:30 | 49 | 46 |  |  | 43691.6042 | 67 | 66
2019-08-14 15:00 | 48 | 45 |  |  | 43691.625 | 73 | 72
2019-08-14 15:30 | 48 | 45 |  |  | 43691.6458 | 72 | 71
2019-08-14 16:00 | 52 | 49 |  |  | 43691.6667 | 74 | 73
2019-08-14 16:30 | 55 | 52 |  |  | 43691.6875 | 78 | 77
2019-08-14 17:00 | 59 | 57 |  |  | 43691.7083 | 87 | 86
2019-08-14 17:30 | 66 | 64 |  |  | 43691.7292 | 96 | 95
2019-08-14 18:00 | 73 | 71 |  |  | 43691.75 | 104 | 104
2019-08-14 18:30 | 76 | 74 |  |  | 43691.7708 | 108 | 107
2019-08-14 19:00 | 79 | 77 |  |  | 43691.7917 | 112 | 112
2019-08-14 19:30 | 77 | 75 |  |  | 43691.8125 | 110 | 109
2019-08-14 20:00 | 76 | 74 |  |  | 43691.8333 | 108 | 107
2019-08-14 20:30 | 76 | 73 |  |  | 43691.8542 | 108 | 107
2019-08-14 21:00 | 72 | 70 |  |  | 43691.875 | 104 | 103
2019-08-14 21:30 | 69 | 67 |  |  | 43691.8958 | 99 | 98
2019-08-14 22:00 | 67 | 65 |  |  | 43691.9167 | 97 | 96
2019-08-14 22:30 | 64 | 61 |  |  | 43691.9375 | 94 | 94
2019-08-14 23:00 | 61 | 59 |  |  | 43691.9583 | 89 | 88
2019-08-14 23:30 | 60 | 56 |  |  | 43691.9792 | 85 | 84
2019-08-15 | 55 | 51 |  |  | 43692 | 78 | 77
2019-08-15 00:30 | 53 | 50 |  |  | 43692.0208 | 74 | 74
2019-08-15 01:00 | 51 | 47 |  |  | 43692.0417 | 70 | 70
2019-08-15 01:30 | 50 | 45 |  |  | 43692.0625 | 68 | 66
2019-08-15 02:00 | 46 | 42 |  |  | 43692.0833 | 63 | 62
2019-08-15 02:30 | 48 | 45 |  |  | 43692.1042 | 65 | 65
2019-08-15 03:00 | 49 | 46 |  |  | 43692.125 | 66 | 66
2019-08-15 03:30 | 50 | 46 |  |  | 43692.1458 | 66 | 66
2019-08-15 04:00 | 51 | 48 |  |  | 43692.1667 | 68 | 67
2019-08-15 04:30 | 53 | 51 |  |  | 43692.1875 | 71 | 71
2019-08-15 05:00 | 56 | 53 |  |  | 43692.2083 | 74 | 74
2019-08-15 05:30 | 63 | 61 |  |  | 43692.2292 | 82 | 82
2019-08-15 06:00 | 72 | 71 |  |  | 43692.25 | 94 | 94
2019-08-15 06:30 | 81 | 77 |  |  | 43692.2708 | 108 | 108
2019-08-15 07:00 | 87 | 84 |  |  | 43692.2917 | 120 | 119
2019-08-15 07:30 | 90 | 86 |  |  | 43692.3125 | 127 | 125
2019-08-15 08:00 | 83 | 77 |  |  | 43692.3333 | 118 | 116
2019-08-15 08:30 | 75 | 67 |  |  | 43692.3542 | 109 | 106
2019-08-15 09:00 | 69 | 62 |  |  | 43692.375 | 103 | 99
2019-08-15 09:30 | 63 | 57 |  |  | 43692.3958 | 97 | 92
2019-08-15 10:00 | 60 | 54 |  |  | 43692.4167 | 93 | 88
2019-08-15 10:30 | 57 | 50 |  |  | 43692.4375 | 88 | 82
2019-08-15 11:00 | 57 | 50 |  |  | 43692.4583 | 87 | 82
2019-08-15 11:30 | 56 | 49 |  |  | 43692.4792 | 87 | 81
2019-08-15 12:00 | 55 | 48 |  |  | 43692.5 | 87 | 81
2019-08-15 12:30 | 55 | 48 |  |  | 43692.5208 | 87 | 81
2019-08-15 13:00 | 57 | 49 |  |  | 43692.5417 | 87 | 83
2019-08-15 13:30 | 60 | 52 |  |  | 43692.5625 | 88 | 84
2019-08-15 14:00 | 64 | 56 |  |  | 43692.5833 | 93 | 90
2019-08-15 14:30 | 64 | 57 |  |  | 43692.6042 | 93 | 90
2019-08-15 15:00 | 67 | 59 |  |  | 43692.625 | 95 | 92
2019-08-15 15:30 | 72 | 64 |  |  | 43692.6458 | 100 | 97
2019-08-15 16:00 | 75 | 67 |  |  | 43692.6667 | 104 | 102
2019-08-15 16:30 | 77 | 70 |  |  | 43692.6875 | 108 | 106
2019-08-15 17:00 | 81 | 73 |  |  | 43692.7083 | 112 | 110
2019-08-15 17:30 | 83 | 75 |  |  | 43692.7292 | 113 | 111
2019-08-15 18:00 | 89 | 82 |  |  | 43692.75 | 121 | 120
2019-08-15 18:30 | 92 | 85 |  |  | 43692.7708 | 123 | 122
2019-08-15 19:00 | 93 | 87 |  |  | 43692.7917 | 126 | 124
2019-08-15 19:30 | 92 | 86 |  |  | 43692.8125 | 123 | 122
2019-08-15 20:00 | 91 | 84 |  |  | 43692.8333 | 121 | 120
2019-08-15 20:30 | 89 | 82 |  |  | 43692.8542 | 119 | 118
2019-08-15 21:00 | 86 | 79 |  |  | 43692.875 | 114 | 113
2019-08-15 21:30 | 83 | 76 |  |  | 43692.8958 | 109 | 108
2019-08-15 22:00 | 81 | 73 |  |  | 43692.9167 | 106 | 105
2019-08-15 22:30 | 78 | 69 |  |  | 43692.9375 | 102 | 102
2019-08-15 23:00 | 75 | 66 |  |  | 43692.9583 | 95 | 95
2019-08-15 23:30 | 73 | 62 |  |  | 43692.9792 | 90 | 90
2019-08-16 | 69 | 57 |  |  | 43693 | 83 | 82
2019-08-16 00:30 | 68 | 55 |  |  | 43693.0208 | 79 | 79
2019-08-16 01:00 | 67 | 53 |  |  | 43693.0417 | 76 | 76
2019-08-16 01:30 | 68 | 52 |  |  | 43693.0625 | 73 | 72
2019-08-16 02:00 | 74 | 48 |  |  | 43693.0833 | 67 | 67
2019-08-16 02:30 | 73 | 45 |  |  | 43693.1042 | 64 | 64
2019-08-16 03:00 | 70 | 44 |  |  | 43693.125 | 63 | 63
2019-08-16 03:30 | 71 | 45 |  |  | 43693.1458 | 66 | 66
2019-08-16 04:00 | 72 | 47 |  |  | 43693.1667 | 66 | 66
2019-08-16 04:30 | 73 | 48 |  |  | 43693.1875 | 68 | 68
2019-08-16 05:00 | 75 | 52 |  |  | 43693.2083 | 72 | 72
2019-08-16 05:30 | 78 | 58 |  |  | 43693.2292 | 80 | 79
2019-08-16 06:00 | 72 | 66 |  |  | 43693.25 | 89 | 89
2019-08-16 06:30 | 72 | 69 |  |  | 43693.2708 | 101 | 99
2019-08-16 07:00 | 78 | 75 |  |  | 43693.2917 | 113 | 110
2019-08-16 07:30 | 88 | 79 |  |  | 43693.3125 | 129 | 119
2019-08-16 08:00 | 85 | 76 |  |  | 43693.3333 | 128 | 117
2019-08-16 08:30 | 74 | 67 |  |  | 43693.3542 | 121 | 108
2019-08-16 09:00 | 60 | 56 |  |  | 43693.375 | 108 | 93
2019-08-16 09:30 | 54 | 54 |  |  | 43693.3958 | 98 | 89
2019-08-16 10:00 | 53 | 50 |  |  | 43693.4167 | 85 | 82
2019-08-16 10:30 | 49 | 47 |  |  | 43693.4375 | 81 | 78
2019-08-16 11:00 | 47 | 45 |  |  | 43693.4583 | 79 | 76
2019-08-16 11:30 | 45 | 43 |  |  | 43693.4792 | 78 | 75
2019-08-16 12:00 | 44 | 41 |  |  | 43693.5 | 77 | 74
2019-08-16 12:30 | 43 | 41 |  |  | 43693.5208 | 77 | 74
2019-08-16 13:00 | 47 | 46 |  |  | 43693.5417 | 84 | 81
2019-08-16 13:30 | 53 | 51 |  |  | 43693.5625 | 92 | 90
2019-08-16 14:00 | 53 | 51 |  |  | 43693.5833 | 92 | 89
2019-08-16 14:30 | 54 | 52 |  |  | 43693.6042 | 91 | 88
2019-08-16 15:00 | 58 | 56 |  |  | 43693.625 | 91 | 88
2019-08-16 15:30 | 61 | 59 |  |  | 43693.6458 | 93 | 90
2019-08-16 16:00 | 63 | 61 |  |  | 43693.6667 | 99 | 97
2019-08-16 16:30 | 65 | 64 |  |  | 43693.6875 | 104 | 100
2019-08-16 17:00 | 68 | 68 |  |  | 43693.7083 | 109 | 103
2019-08-16 17:30 | 71 | 71 |  |  | 43693.7292 | 113 | 107
2019-08-16 18:00 | 72 | 72 |  |  | 43693.75 | 117 | 109
2019-08-16 18:30 | 70 | 70 |  |  | 43693.7708 | 117 | 108
2019-08-16 19:00 | 70 | 70 |  |  | 43693.7917 | 118 | 108
2019-08-16 19:30 | 70 | 70 |  |  | 43693.8125 | 118 | 107
2019-08-16 20:00 | 70 | 70 |  |  | 43693.8333 | 112 | 106
2019-08-16 20:30 | 69 | 69 |  |  | 43693.8542 | 110 | 105
2019-08-16 21:00 | 66 | 66 |  |  | 43693.875 | 106 | 100
2019-08-16 21:30 | 63 | 63 |  |  | 43693.8958 | 103 | 96
2019-08-16 22:00 | 63 | 63 |  |  | 43693.9167 | 104 | 96
2019-08-16 22:30 | 61 | 61 |  |  | 43693.9375 | 102 | 94
2019-08-16 23:00 | 60 | 60 |  |  | 43693.9583 | 99 | 90
2019-08-16 23:30 | 57 | 57 |  |  | 43693.9792 | 97 | 87
2019-08-17 | 49 | 49 |  |  | 43694 | 89 | 77
2019-08-17 00:30 | 45 | 45 |  |  | 43694.0208 | 81 | 70
2019-08-17 01:00 | 42 | 41 |  |  | 43694.0417 | 77 | 65
2019-08-17 01:30 | 39 | 39 |  |  | 43694.0625 | 74 | 61
2019-08-17 02:00 | 36 | 36 |  |  | 43694.0833 | 72 | 57
2019-08-17 02:30 | 36 | 36 |  |  | 43694.1042 | 72 | 58
2019-08-17 03:00 | 38 | 38 |  |  | 43694.125 | 73 | 58
2019-08-17 03:30 | 38 | 38 |  |  | 43694.1458 | 69 | 58
2019-08-17 04:00 | 38 | 37 |  |  | 43694.1667 | 69 | 58
2019-08-17 04:30 | 39 | 39 |  |  | 43694.1875 | 70 | 59
2019-08-17 05:00 | 39 | 39 |  |  | 43694.2083 | 71 | 61
2019-08-17 05:30 | 44 | 44 |  |  | 43694.2292 | 76 | 66
2019-08-17 06:00 | 46 | 46 |  |  | 43694.25 | 78 | 69
2019-08-17 06:30 | 47 | 47 |  |  | 43694.2708 | 80 | 71
2019-08-17 07:00 | 50 | 50 |  |  | 43694.2917 | 85 | 77
2019-08-17 07:30 | 48 | 48 |  |  | 43694.3125 | 84 | 77
2019-08-17 08:00 | 45 | 45 |  |  | 43694.3333 | 80 | 73
2019-08-17 08:30 | 45 | 44 |  |  | 43694.3542 | 80 | 74
2019-08-17 09:00 | 44 | 43 |  |  | 43694.375 | 78 | 71
2019-08-17 09:30 | 41 | 40 |  |  | 43694.3958 | 75 | 68
2019-08-17 10:00 | 38 | 37 |  |  | 43694.4167 | 70 | 64
2019-08-17 10:30 | 36 | 35 |  |  | 43694.4375 | 67 | 61
2019-08-17 11:00 | 33 | 32 |  |  | 43694.4583 | 64 | 56
2019-08-17 11:30 | 32 | 31 |  |  | 43694.4792 | 61 | 54
2019-08-17 12:00 | 32 | 30 |  |  | 43694.5 | 61 | 54
2019-08-17 12:30 | 31 | 30 |  |  | 43694.5208 | 61 | 54
2019-08-17 13:00 | 32 | 31 |  |  | 43694.5417 | 61 | 54
2019-08-17 13:30 | 32 | 31 |  |  | 43694.5625 | 61 | 54
2019-08-17 14:00 | 33 | 32 |  |  | 43694.5833 | 62 | 55
2019-08-17 14:30 | 33 | 32 |  |  | 43694.6042 | 62 | 55
2019-08-17 15:00 | 37 | 36 |  |  | 43694.625 | 66 | 60
2019-08-17 15:30 | 40 | 39 |  |  | 43694.6458 | 71 | 65
2019-08-17 16:00 | 45 | 44 |  |  | 43694.6667 | 77 | 72
2019-08-17 16:30 | 48 | 48 |  |  | 43694.6875 | 82 | 77
2019-08-17 17:00 | 54 | 53 |  |  | 43694.7083 | 90 | 84
2019-08-17 17:30 | 58 | 58 |  |  | 43694.7292 | 95 | 90
2019-08-17 18:00 | 63 | 63 |  |  | 43694.75 | 102 | 97
2019-08-17 18:30 | 65 | 65 |  |  | 43694.7708 | 105 | 100
2019-08-17 19:00 | 67 | 67 |  |  | 43694.7917 | 106 | 102
2019-08-17 19:30 | 66 | 65 |  |  | 43694.8125 | 103 | 100
2019-08-17 20:00 | 68 | 67 |  |  | 43694.8333 | 105 | 100
2019-08-17 20:30 | 67 | 66 |  |  | 43694.8542 | 104 | 99
2019-08-17 21:00 | 66 | 65 |  |  | 43694.875 | 101 | 97
2019-08-17 21:30 | 64 | 63 |  |  | 43694.8958 | 97 | 94
2019-08-17 22:00 | 64 | 62 |  |  | 43694.9167 | 98 | 93
2019-08-17 22:30 | 65 | 64 |  |  | 43694.9375 | 98 | 94
2019-08-17 23:00 | 64 | 63 |  |  | 43694.9583 | 95 | 91
2019-08-17 23:30 | 61 | 59 |  |  | 43694.9792 | 91 | 86
2019-08-18 | 55 | 53 |  |  | 43695 | 85 | 79
2019-08-18 00:30 | 53 | 51 |  |  | 43695.0208 | 81 | 75
2019-08-18 01:00 | 48 | 48 |  |  | 43695.0417 | 76 | 70
2019-08-18 01:30 | 45 | 44 |  |  | 43695.0625 | 73 | 64
2019-08-18 02:00 | 46 | 43 |  |  | 43695.0833 | 71 | 63
2019-08-18 02:30 | 48 | 45 |  |  | 43695.1042 | 73 | 65
2019-08-18 03:00 | 49 | 46 |  |  | 43695.125 | 75 | 66
2019-08-18 03:30 | 51 | 48 |  |  | 43695.1458 | 77 | 68
2019-08-18 04:00 | 50 | 47 |  |  | 43695.1667 | 77 | 68
2019-08-18 04:30 | 50 | 47 |  |  | 43695.1875 | 77 | 68
2019-08-18 05:00 | 50 | 47 |  |  | 43695.2083 | 76 | 67
2019-08-18 05:30 | 51 | 48 |  |  | 43695.2292 | 77 | 68
2019-08-18 06:00 | 52 | 49 |  |  | 43695.25 | 79 | 70
2019-08-18 06:30 | 50 | 47 |  |  | 43695.2708 | 79 | 70
2019-08-18 07:00 | 50 | 47 |  |  | 43695.2917 | 80 | 72
2019-08-18 07:30 | 46 | 43 |  |  | 43695.3125 | 76 | 68
2019-08-18 08:00 | 41 | 39 |  |  | 43695.3333 | 71 | 63
2019-08-18 08:30 | 38 | 36 |  |  | 43695.3542 | 68 | 61
2019-08-18 09:00 | 36 | 34 |  |  | 43695.375 | 67 | 60
2019-08-18 09:30 | 34 | 32 |  |  | 43695.3958 | 65 | 59
2019-08-18 10:00 | 36 | 34 |  |  | 43695.4167 | 65 | 59
2019-08-18 10:30 | 38 | 37 |  |  | 43695.4375 | 67 | 61
2019-08-18 11:00 | 39 | 38 |  |  | 43695.4583 | 69 | 64
2019-08-18 11:30 | 41 | 40 |  |  | 43695.4792 | 68 | 63
2019-08-18 12:00 | 34 | 33 |  |  | 43695.5 | 60 | 55
2019-08-18 12:30 | 33 | 32 |  |  | 43695.5208 | 59 | 53
2019-08-18 13:00 | 36 | 35 |  |  | 43695.5417 | 62 | 57
2019-08-18 13:30 | 35 | 34 |  |  | 43695.5625 | 62 | 56
2019-08-18 14:00 | 36 | 35 |  |  | 43695.5833 | 62 | 57
2019-08-18 14:30 | 35 | 34 |  |  | 43695.6042 | 61 | 56
2019-08-18 15:00 | 36 | 35 |  |  | 43695.625 | 63 | 58
2019-08-18 15:30 | 38 | 37 |  |  | 43695.6458 | 67 | 61
2019-08-18 16:00 | 43 | 42 |  |  | 43695.6667 | 73 | 67
2019-08-18 16:30 | 52 | 51 |  |  | 43695.6875 | 84 | 78
2019-08-18 17:00 | 61 | 60 |  |  | 43695.7083 | 92 | 87
2019-08-18 17:30 | 67 | 66 |  |  | 43695.7292 | 100 | 94
2019-08-18 18:00 | 74 | 73 |  |  | 43695.75 | 109 | 104
2019-08-18 18:30 | 78 | 77 |  |  | 43695.7708 | 115 | 110
2019-08-18 19:00 | 79 | 78 |  |  | 43695.7917 | 116 | 111
2019-08-18 19:30 | 78 | 76 |  |  | 43695.8125 | 113 | 108
2019-08-18 20:00 | 74 | 73 |  |  | 43695.8333 | 110 | 105
2019-08-18 20:30 | 76 | 75 |  |  | 43695.8542 | 111 | 106
2019-08-18 21:00 | 73 | 72 |  |  | 43695.875 | 107 | 102
2019-08-18 21:30 | 69 | 68 |  |  | 43695.8958 | 102 | 98
2019-08-18 22:00 | 70 | 69 |  |  | 43695.9167 | 103 | 98
2019-08-18 22:30 | 71 | 70 |  |  | 43695.9375 | 104 | 100
2019-08-18 23:00 | 70 | 68 |  |  | 43695.9583 | 101 | 95
2019-08-18 23:30 | 66 | 64 |  |  | 43695.9792 | 97 | 90
2019-08-19 | 60 | 58 |  |  | 43696 | 91 | 84
2019-08-19 00:30 | 60 | 58 |  |  | 43696.0208 | 89 | 81
2019-08-19 01:00 | 58 | 56 |  |  | 43696.0417 | 86 | 78
2019-08-19 01:30 | 53 | 50 |  |  | 43696.0625 | 81 | 72
2019-08-19 02:00 | 49 | 46 |  |  | 43696.0833 | 76 | 67
2019-08-19 02:30 | 49 | 46 |  |  | 43696.1042 | 76 | 66
2019-08-19 03:00 | 50 | 46 |  |  | 43696.125 | 76 | 66
2019-08-19 03:30 | 50 | 47 |  |  | 43696.1458 | 76 | 66
2019-08-19 04:00 | 50 | 47 |  |  | 43696.1667 | 75 | 67
2019-08-19 04:30 | 51 | 49 |  |  | 43696.1875 | 76 | 69
2019-08-19 05:00 | 54 | 52 |  |  | 43696.2083 | 79 | 72
2019-08-19 05:30 | 59 | 58 |  |  | 43696.2292 | 84 | 78
2019-08-19 06:00 | 64 | 63 |  |  | 43696.25 | 91 | 86
2019-08-19 06:30 | 72 | 69 |  |  | 43696.2708 | 99 | 97
2019-08-19 07:00 | 75 | 72 |  |  | 43696.2917 | 107 | 106
2019-08-19 07:30 | 80 | 76 |  |  | 43696.3125 | 113 | 113
2019-08-19 08:00 | 75 | 73 |  |  | 43696.3333 | 111 | 111
2019-08-19 08:30 | 70 | 68 |  |  | 43696.3542 | 104 | 104
2019-08-19 09:00 | 65 | 62 |  |  | 43696.375 | 98 | 97
2019-08-19 09:30 | 59 | 57 |  |  | 43696.3958 | 91 | 90
2019-08-19 10:00 | 55 | 54 |  |  | 43696.4167 | 86 | 86
2019-08-19 10:30 | 53 | 51 |  |  | 43696.4375 | 83 | 83
2019-08-19 11:00 | 52 | 50 |  |  | 43696.4583 | 82 | 82
2019-08-19 11:30 | 51 | 50 |  |  | 43696.4792 | 80 | 80
2019-08-19 12:00 | 50 | 48 |  |  | 43696.5 | 78 | 78
2019-08-19 12:30 | 49 | 48 |  |  | 43696.5208 | 78 | 78
2019-08-19 13:00 | 52 | 50 |  |  | 43696.5417 | 80 | 80
2019-08-19 13:30 | 54 | 52 |  |  | 43696.5625 | 83 | 83
2019-08-19 14:00 | 58 | 57 |  |  | 43696.5833 | 87 | 87
2019-08-19 14:30 | 58 | 57 |  |  | 43696.6042 | 88 | 88
2019-08-19 15:00 | 59 | 58 |  |  | 43696.625 | 89 | 89
2019-08-19 15:30 | 61 | 59 |  |  | 43696.6458 | 90 | 90
2019-08-19 16:00 | 67 | 65 |  |  | 43696.6667 | 98 | 97
2019-08-19 16:30 | 74 | 71 |  |  | 43696.6875 | 104 | 104
2019-08-19 17:00 | 78 | 76 |  |  | 43696.7083 | 109 | 109
2019-08-19 17:30 | 79 | 77 |  |  | 43696.7292 | 110 | 109
2019-08-19 18:00 | 84 | 83 |  |  | 43696.75 | 118 | 117
2019-08-19 18:30 | 85 | 85 |  |  | 43696.7708 | 120 | 120
2019-08-19 19:00 | 85 | 85 |  |  | 43696.7917 | 120 | 120
2019-08-19 19:30 | 83 | 83 |  |  | 43696.8125 | 118 | 117
2019-08-19 20:00 | 81 | 81 |  |  | 43696.8333 | 115 | 115
2019-08-19 20:30 | 79 | 79 |  |  | 43696.8542 | 113 | 113
2019-08-19 21:00 | 75 | 75 |  |  | 43696.875 | 106 | 106
2019-08-19 21:30 | 70 | 70 |  |  | 43696.8958 | 99 | 99
2019-08-19 22:00 | 68 | 68 |  |  | 43696.9167 | 98 | 98
2019-08-19 22:30 | 66 | 66 |  |  | 43696.9375 | 95 | 95
2019-08-19 23:00 | 67 | 67 |  |  | 43696.9583 | 94 | 93
2019-08-19 23:30 | 66 | 65 |  |  | 43696.9792 | 92 | 91
2019-08-20 | 61 | 61 |  |  | 43697 | 86 | 85
2019-08-20 00:30 | 58 | 57 |  |  | 43697.0208 | 81 | 79
2019-08-20 01:00 | 55 | 55 |  |  | 43697.0417 | 79 | 74
2019-08-20 01:30 | 52 | 52 |  |  | 43697.0625 | 77 | 72
2019-08-20 02:00 | 52 | 52 |  |  | 43697.0833 | 75 | 71
2019-08-20 02:30 | 52 | 52 |  |  | 43697.1042 | 75 | 71
2019-08-20 03:00 | 52 | 52 |  |  | 43697.125 | 74 | 71
2019-08-20 03:30 | 51 | 51 |  |  | 43697.1458 | 73 | 69
2019-08-20 04:00 | 52 | 52 |  |  | 43697.1667 | 74 | 70
2019-08-20 04:30 | 55 | 55 |  |  | 43697.1875 | 77 | 73
2019-08-20 05:00 | 58 | 57 |  |  | 43697.2083 | 80 | 77
2019-08-20 05:30 | 64 | 64 |  |  | 43697.2292 | 87 | 84
2019-08-20 06:00 | 70 | 69 |  |  | 43697.25 | 93 | 91
2019-08-20 06:30 | 73 | 72 |  |  | 43697.2708 | 102 | 101
2019-08-20 07:00 | 80 | 78 |  |  | 43697.2917 | 112 | 112
2019-08-20 07:30 | 79 | 78 |  |  | 43697.3125 | 117 | 116
2019-08-20 08:00 | 72 | 71 |  |  | 43697.3333 | 110 | 109
2019-08-20 08:30 | 65 | 64 |  |  | 43697.3542 | 103 | 101
2019-08-20 09:00 | 60 | 59 |  |  | 43697.375 | 96 | 95
2019-08-20 09:30 | 56 | 55 |  |  | 43697.3958 | 89 | 89
2019-08-20 10:00 | 52 | 51 |  |  | 43697.4167 | 83 | 82
2019-08-20 10:30 | 47 | 45 |  |  | 43697.4375 | 76 | 76
2019-08-20 11:00 | 46 | 44 |  |  | 43697.4583 | 74 | 74
2019-08-20 11:30 | 45 | 43 |  |  | 43697.4792 | 72 | 72
2019-08-20 12:00 | 44 | 42 |  |  | 43697.5 | 71 | 70
2019-08-20 12:30 | 44 | 42 |  |  | 43697.5208 | 70 | 70
2019-08-20 13:00 | 43 | 40 |  |  | 43697.5417 | 68 | 67
2019-08-20 13:30 | 45 | 43 |  |  | 43697.5625 | 70 | 70
2019-08-20 14:00 | 48 | 45 |  |  | 43697.5833 | 74 | 73
2019-08-20 14:30 | 49 | 47 |  |  | 43697.6042 | 76 | 76
2019-08-20 15:00 | 50 | 48 |  |  | 43697.625 | 78 | 78
2019-08-20 15:30 | 52 | 50 |  |  | 43697.6458 | 82 | 81
2019-08-20 16:00 | 57 | 55 |  |  | 43697.6667 | 87 | 87
2019-08-20 16:30 | 65 | 64 |  |  | 43697.6875 | 97 | 97
2019-08-20 17:00 | 74 | 73 |  |  | 43697.7083 | 111 | 109
2019-08-20 17:30 | 77 | 76 |  |  | 43697.7292 | 115 | 112
2019-08-20 18:00 | 82 | 82 |  |  | 43697.75 | 123 | 120
2019-08-20 18:30 | 87 | 87 |  |  | 43697.7708 | 127 | 124
2019-08-20 19:00 | 90 | 90 |  |  | 43697.7917 | 131 | 128
2019-08-20 19:30 | 87 | 87 |  |  | 43697.8125 | 127 | 124
2019-08-20 20:00 | 86 | 86 |  |  | 43697.8333 | 127 | 122
2019-08-20 20:30 | 86 | 86 |  |  | 43697.8542 | 127 | 123
2019-08-20 21:00 | 83 | 83 |  |  | 43697.875 | 121 | 117
2019-08-20 21:30 | 79 | 79 |  |  | 43697.8958 | 116 | 112
2019-08-20 22:00 | 78 | 78 |  |  | 43697.9167 | 111 | 109
2019-08-20 22:30 | 78 | 77 |  |  | 43697.9375 | 110 | 108
2019-08-20 23:00 | 76 | 76 |  |  | 43697.9583 | 106 | 105
2019-08-20 23:30 | 71 | 71 |  |  | 43697.9792 | 101 | 98
2019-08-21 | 65 | 65 |  |  | 43698 | 93 | 91
2019-08-21 00:30 | 61 | 61 |  |  | 43698.0208 | 89 | 86
2019-08-21 01:00 | 58 | 58 |  |  | 43698.0417 | 84 | 80
2019-08-21 01:30 | 53 | 53 |  |  | 43698.0625 | 79 | 74
2019-08-21 02:00 | 54 | 54 |  |  | 43698.0833 | 78 | 75
2019-08-21 02:30 | 53 | 53 |  |  | 43698.1042 | 78 | 76
2019-08-21 03:00 | 53 | 53 |  |  | 43698.125 | 75 | 74
2019-08-21 03:30 | 54 | 54 |  |  | 43698.1458 | 76 | 74
2019-08-21 04:00 | 53 | 53 |  |  | 43698.1667 | 76 | 74
2019-08-21 04:30 | 54 | 54 |  |  | 43698.1875 | 77 | 75
2019-08-21 05:00 | 59 | 59 |  |  | 43698.2083 | 81 | 80
2019-08-21 05:30 | 67 | 67 |  |  | 43698.2292 | 90 | 88
2019-08-21 06:00 | 74 | 74 |  |  | 43698.25 | 99 | 98
2019-08-21 06:30 | 79 | 79 |  |  | 43698.2708 | 109 | 108
2019-08-21 07:00 | 85 | 84 |  |  | 43698.2917 | 118 | 118
2019-08-21 07:30 | 83 | 82 |  |  | 43698.3125 | 120 | 120
2019-08-21 08:00 | 74 | 73 |  |  | 43698.3333 | 110 | 110
2019-08-21 08:30 | 66 | 64 |  |  | 43698.3542 | 101 | 101
2019-08-21 09:00 | 60 | 58 |  |  | 43698.375 | 93 | 92
2019-08-21 09:30 | 56 | 53 |  |  | 43698.3958 | 88 | 87
2019-08-21 10:00 | 53 | 50 |  |  | 43698.4167 | 84 | 84
2019-08-21 10:30 | 52 | 48 |  |  | 43698.4375 | 80 | 80
2019-08-21 11:00 | 51 | 47 |  |  | 43698.4583 | 78 | 78
2019-08-21 11:30 | 50 | 46 |  |  | 43698.4792 | 76 | 76
2019-08-21 12:00 | 49 | 45 |  |  | 43698.5 | 75 | 75
2019-08-21 12:30 | 49 | 45 |  |  | 43698.5208 | 75 | 75
2019-08-21 13:00 | 50 | 47 |  |  | 43698.5417 | 77 | 77
2019-08-21 13:30 | 53 | 49 |  |  | 43698.5625 | 79 | 79
2019-08-21 14:00 | 54 | 51 |  |  | 43698.5833 | 81 | 81
2019-08-21 14:30 | 56 | 52 |  |  | 43698.6042 | 83 | 83
2019-08-21 15:00 | 57 | 54 |  |  | 43698.625 | 86 | 86
2019-08-21 15:30 | 60 | 58 |  |  | 43698.6458 | 91 | 91
2019-08-21 16:00 | 64 | 62 |  |  | 43698.6667 | 96 | 96
2019-08-21 16:30 | 70 | 68 |  |  | 43698.6875 | 102 | 101
2019-08-21 17:00 | 77 | 75 |  |  | 43698.7083 | 110 | 109
2019-08-21 17:30 | 80 | 79 |  |  | 43698.7292 | 115 | 113
2019-08-21 18:00 | 83 | 82 |  |  | 43698.75 | 119 | 117
2019-08-21 18:30 | 86 | 85 |  |  | 43698.7708 | 121 | 119
2019-08-21 19:00 | 86 | 85 |  |  | 43698.7917 | 122 | 120
2019-08-21 19:30 | 83 | 82 |  |  | 43698.8125 | 119 | 117
2019-08-21 20:00 | 82 | 82 |  |  | 43698.8333 | 117 | 115
2019-08-21 20:30 | 83 | 82 |  |  | 43698.8542 | 117 | 115
2019-08-21 21:00 | 80 | 79 |  |  | 43698.875 | 112 | 110
2019-08-21 21:30 | 76 | 76 |  |  | 43698.8958 | 108 | 107
2019-08-21 22:00 | 76 | 75 |  |  | 43698.9167 | 108 | 106
2019-08-21 22:30 | 73 | 72 |  |  | 43698.9375 | 107 | 105
2019-08-21 23:00 | 72 | 72 |  |  | 43698.9583 | 104 | 102
2019-08-21 23:30 | 68 | 67 |  |  | 43698.9792 | 97 | 94
2019-08-22 | 59 | 58 |  |  | 43699 | 88 | 85
2019-08-22 00:30 | 56 | 56 |  |  | 43699.0208 | 84 | 80
2019-08-22 01:00 | 55 | 55 |  |  | 43699.0417 | 81 | 76
2019-08-22 01:30 | 51 | 51 |  |  | 43699.0625 | 77 | 71
2019-08-22 02:00 | 49 | 49 |  |  | 43699.0833 | 75 | 69
2019-08-22 02:30 | 49 | 49 |  |  | 43699.1042 | 74 | 70
2019-08-22 03:00 | 50 | 50 |  |  | 43699.125 | 74 | 70
2019-08-22 03:30 | 51 | 51 |  |  | 43699.1458 | 75 | 71
2019-08-22 04:00 | 51 | 51 |  |  | 43699.1667 | 75 | 71
2019-08-22 04:30 | 52 | 51 |  |  | 43699.1875 | 75 | 71
2019-08-22 05:00 | 55 | 55 |  |  | 43699.2083 | 78 | 75
2019-08-22 05:30 | 62 | 62 |  |  | 43699.2292 | 85 | 83
2019-08-22 06:00 | 73 | 72 |  |  | 43699.25 | 96 | 94
2019-08-22 06:30 | 78 | 77 |  |  | 43699.2708 | 105 | 104
2019-08-22 07:00 | 76 | 75 |  |  | 43699.2917 | 106 | 105
2019-08-22 07:30 | 74 | 73 |  |  | 43699.3125 | 106 | 106
2019-08-22 08:00 | 72 | 71 |  |  | 43699.3333 | 105 | 105
2019-08-22 08:30 | 66 | 64 |  |  | 43699.3542 | 97 | 97
2019-08-22 09:00 | 62 | 59 |  |  | 43699.375 | 92 | 92
2019-08-22 09:30 | 56 | 53 |  |  | 43699.3958 | 85 | 85
2019-08-22 10:00 | 54 | 50 |  |  | 43699.4167 | 82 | 82
2019-08-22 10:30 | 53 | 49 |  |  | 43699.4375 | 79 | 79
2019-08-22 11:00 | 53 | 49 |  |  | 43699.4583 | 78 | 78
2019-08-22 11:30 | 51 | 47 |  |  | 43699.4792 | 76 | 76
2019-08-22 12:00 | 51 | 47 |  |  | 43699.5 | 75 | 75
2019-08-22 12:30 | 48 | 44 |  |  | 43699.5208 | 72 | 72
2019-08-22 13:00 | 49 | 45 |  |  | 43699.5417 | 73 | 73
2019-08-22 13:30 | 52 | 47 |  |  | 43699.5625 | 77 | 77
2019-08-22 14:00 | 54 | 49 |  |  | 43699.5833 | 79 | 79
2019-08-22 14:30 | 56 | 52 |  |  | 43699.6042 | 80 | 80
2019-08-22 15:00 | 59 | 55 |  |  | 43699.625 | 84 | 84
2019-08-22 15:30 | 62 | 59 |  |  | 43699.6458 | 90 | 90
2019-08-22 16:00 | 69 | 66 |  |  | 43699.6667 | 98 | 98
2019-08-22 16:30 | 73 | 71 |  |  | 43699.6875 | 104 | 103
2019-08-22 17:00 | 77 | 75 |  |  | 43699.7083 | 108 | 107
2019-08-22 17:30 | 77 | 77 |  |  | 43699.7292 | 112 | 110
2019-08-22 18:00 | 81 | 80 |  |  | 43699.75 | 118 | 116
2019-08-22 18:30 | 81 | 80 |  |  | 43699.7708 | 119 | 116
2019-08-22 19:00 | 82 | 82 |  |  | 43699.7917 | 121 | 118
2019-08-22 19:30 | 80 | 80 |  |  | 43699.8125 | 118 | 115
2019-08-22 20:00 | 80 | 79 |  |  | 43699.8333 | 115 | 114
2019-08-22 20:30 | 78 | 78 |  |  | 43699.8542 | 113 | 112
2019-08-22 21:00 | 74 | 74 |  |  | 43699.875 | 108 | 106
2019-08-22 21:30 | 70 | 70 |  |  | 43699.8958 | 103 | 100
2019-08-22 22:00 | 69 | 68 |  |  | 43699.9167 | 101 | 98
2019-08-22 22:30 | 65 | 65 |  |  | 43699.9375 | 98 | 95
2019-08-22 23:00 | 63 | 62 |  |  | 43699.9583 | 93 | 89
2019-08-22 23:30 | 56 | 55 |  |  | 43699.9792 | 86 | 81
2019-08-23 | 52 | 52 |  |  | 43700 | 82 | 77
2019-08-23 00:30 | 50 | 49 |  |  | 43700.0208 | 75 | 70
2019-08-23 01:00 | 45 | 44 |  |  | 43700.0417 | 68 | 63
2019-08-23 01:30 | 41 | 40 |  |  | 43700.0625 | 65 | 59
2019-08-23 02:00 | 38 | 38 |  |  | 43700.0833 | 62 | 56
2019-08-23 02:30 | 42 | 41 |  |  | 43700.1042 | 63 | 59
2019-08-23 03:00 | 42 | 42 |  |  | 43700.125 | 64 | 60
2019-08-23 03:30 | 44 | 43 |  |  | 43700.1458 | 65 | 61
2019-08-23 04:00 | 43 | 42 |  |  | 43700.1667 | 63 | 59
2019-08-23 04:30 | 43 | 42 |  |  | 43700.1875 | 64 | 61
2019-08-23 05:00 | 45 | 44 |  |  | 43700.2083 | 66 | 63
2019-08-23 05:30 | 52 | 51 |  |  | 43700.2292 | 72 | 69
2019-08-23 06:00 | 58 | 57 |  |  | 43700.25 | 79 | 77
2019-08-23 06:30 | 62 | 61 |  |  | 43700.2708 | 88 | 87
2019-08-23 07:00 | 65 | 64 |  |  | 43700.2917 | 97 | 96
2019-08-23 07:30 | 69 | 67 |  |  | 43700.3125 | 102 | 101
2019-08-23 08:00 | 67 | 65 |  |  | 43700.3333 | 96 | 96
2019-08-23 08:30 | 64 | 61 |  |  | 43700.3542 | 83 | 83
2019-08-23 09:00 | 60 | 56 |  |  | 43700.375 | 77 | 77
2019-08-23 09:30 | 56 | 52 |  |  | 43700.3958 | 73 | 73
2019-08-23 10:00 | 56 | 50 |  |  | 43700.4167 | 70 | 70
2019-08-23 10:30 | 55 | 49 |  |  | 43700.4375 | 68 | 68
2019-08-23 11:00 | 53 | 47 |  |  | 43700.4583 | 66 | 66
2019-08-23 11:30 | 51 | 45 |  |  | 43700.4792 | 61 | 61
2019-08-23 12:00 | 50 | 44 |  |  | 43700.5 | 61 | 61
2019-08-23 12:30 | 51 | 44 |  |  | 43700.5208 | 64 | 64
2019-08-23 13:00 | 51 | 45 |  |  | 43700.5417 | 64 | 64
2019-08-23 13:30 | 51 | 45 |  |  | 43700.5625 | 64 | 64
2019-08-23 14:00 | 52 | 47 |  |  | 43700.5833 | 66 | 65
2019-08-23 14:30 | 52 | 47 |  |  | 43700.6042 | 76 | 75
2019-08-23 15:00 | 52 | 48 |  |  | 43700.625 | 79 | 79
2019-08-23 15:30 | 55 | 51 |  |  | 43700.6458 | 82 | 82
2019-08-23 16:00 | 59 | 55 |  |  | 43700.6667 | 87 | 87
2019-08-23 16:30 | 65 | 61 |  |  | 43700.6875 | 93 | 93
2019-08-23 17:00 | 67 | 64 |  |  | 43700.7083 | 96 | 96
2019-08-23 17:30 | 69 | 67 |  |  | 43700.7292 | 100 | 100
2019-08-23 18:00 | 74 | 72 |  |  | 43700.75 | 105 | 105
2019-08-23 18:30 | 74 | 72 |  |  | 43700.7708 | 105 | 105
2019-08-23 19:00 | 75 | 73 |  |  | 43700.7917 | 106 | 106
2019-08-23 19:30 | 72 | 71 |  |  | 43700.8125 | 104 | 104
2019-08-23 20:00 | 73 | 71 |  |  | 43700.8333 | 104 | 104
2019-08-23 20:30 | 71 | 70 |  |  | 43700.8542 | 102 | 101
2019-08-23 21:00 | 67 | 65 |  |  | 43700.875 | 97 | 96
2019-08-23 21:30 | 65 | 63 |  |  | 43700.8958 | 93 | 93
2019-08-23 22:00 | 62 | 60 |  |  | 43700.9167 | 89 | 88
2019-08-23 22:30 | 60 | 58 |  |  | 43700.9375 | 88 | 87
2019-08-23 23:00 | 61 | 60 |  |  | 43700.9583 | 88 | 86
2019-08-23 23:30 | 57 | 57 |  |  | 43700.9792 | 84 | 83
2019-08-24 | 52 | 51 |  |  | 43701 | 77 | 75
2019-08-24 00:30 | 46 | 44 |  |  | 43701.0208 | 68 | 66
2019-08-24 01:00 | 43 | 42 |  |  | 43701.0417 | 63 | 62
2019-08-24 01:30 | 43 | 41 |  |  | 43701.0625 | 63 | 62
2019-08-24 02:00 | 44 | 43 |  |  | 43701.0833 | 63 | 62
2019-08-24 02:30 | 45 | 43 |  |  | 43701.1042 | 63 | 62
2019-08-24 03:00 | 44 | 43 |  |  | 43701.125 | 63 | 62
2019-08-24 03:30 | 43 | 42 |  |  | 43701.1458 | 62 | 61
2019-08-24 04:00 | 44 | 43 |  |  | 43701.1667 | 64 | 63
2019-08-24 04:30 | 44 | 43 |  |  | 43701.1875 | 64 | 63
2019-08-24 05:00 | 45 | 43 |  |  | 43701.2083 | 64 | 63
2019-08-24 05:30 | 46 | 44 |  |  | 43701.2292 | 66 | 65
2019-08-24 06:00 | 50 | 49 |  |  | 43701.25 | 71 | 70
2019-08-24 06:30 | 49 | 48 |  |  | 43701.2708 | 73 | 72
2019-08-24 07:00 | 48 | 47 |  |  | 43701.2917 | 72 | 71
2019-08-24 07:30 | 46 | 44 |  |  | 43701.3125 | 70 | 70
2019-08-24 08:00 | 44 | 42 |  |  | 43701.3333 | 68 | 67
2019-08-24 08:30 | 43 | 41 |  |  | 43701.3542 | 68 | 67
2019-08-24 09:00 | 43 | 41 |  |  | 43701.375 | 68 | 67
2019-08-24 09:30 | 42 | 40 |  |  | 43701.3958 | 66 | 66
2019-08-24 10:00 | 40 | 38 |  |  | 43701.4167 | 64 | 63
2019-08-24 10:30 | 41 | 38 |  |  | 43701.4375 | 63 | 62
2019-08-24 11:00 | 43 | 41 |  |  | 43701.4583 | 62 | 62
2019-08-24 11:30 | 37 | 34 |  |  | 43701.4792 | 56 | 56
2019-08-24 12:00 | 37 | 34 |  |  | 43701.5 | 56 | 56
2019-08-24 12:30 | 36 | 34 |  |  | 43701.5208 | 56 | 56
2019-08-24 13:00 | 33 | 30 |  |  | 43701.5417 | 53 | 52
2019-08-24 13:30 | 34 | 31 |  |  | 43701.5625 | 55 | 54
2019-08-24 14:00 | 34 | 31 |  |  | 43701.5833 | 54 | 53
2019-08-24 14:30 | 34 | 31 |  |  | 43701.6042 | 55 | 54
2019-08-24 15:00 | 37 | 35 |  |  | 43701.625 | 59 | 58
2019-08-24 15:30 | 38 | 35 |  |  | 43701.6458 | 60 | 59
2019-08-24 16:00 | 41 | 39 |  |  | 43701.6667 | 65 | 64
2019-08-24 16:30 | 47 | 45 |  |  | 43701.6875 | 73 | 72
2019-08-24 17:00 | 52 | 50 |  |  | 43701.7083 | 79 | 78
2019-08-24 17:30 | 57 | 55 |  |  | 43701.7292 | 84 | 83
2019-08-24 18:00 | 63 | 63 |  |  | 43701.75 | 91 | 91
2019-08-24 18:30 | 68 | 68 |  |  | 43701.7708 | 97 | 97
2019-08-24 19:00 | 70 | 70 |  |  | 43701.7917 | 100 | 99
2019-08-24 19:30 | 69 | 68 |  |  | 43701.8125 | 97 | 97
2019-08-24 20:00 | 69 | 67 |  |  | 43701.8333 | 96 | 96
2019-08-24 20:30 | 68 | 67 |  |  | 43701.8542 | 96 | 96
2019-08-24 21:00 | 66 | 64 |  |  | 43701.875 | 92 | 92
2019-08-24 21:30 | 61 | 60 |  |  | 43701.8958 | 88 | 87
2019-08-24 22:00 | 60 | 58 |  |  | 43701.9167 | 87 | 86
2019-08-24 22:30 | 58 | 57 |  |  | 43701.9375 | 85 | 84
2019-08-24 23:00 | 55 | 54 |  |  | 43701.9583 | 80 | 79
2019-08-24 23:30 | 52 | 50 |  |  | 43701.9792 | 75 | 75
2019-08-25 | 46 | 45 |  |  | 43702 | 70 | 69
2019-08-25 00:30 | 42 | 40 |  |  | 43702.0208 | 64 | 62
2019-08-25 01:00 | 38 | 36 |  |  | 43702.0417 | 59 | 57
2019-08-25 01:30 | 36 | 35 |  |  | 43702.0625 | 56 | 54
2019-08-25 02:00 | 36 | 35 |  |  | 43702.0833 | 56 | 54
2019-08-25 02:30 | 36 | 35 |  |  | 43702.1042 | 55 | 54
2019-08-25 03:00 | 38 | 36 |  |  | 43702.125 | 56 | 55
2019-08-25 03:30 | 40 | 37 |  |  | 43702.1458 | 58 | 56
2019-08-25 04:00 | 43 | 37 |  |  | 43702.1667 | 60 | 55
2019-08-25 04:30 | 45 | 38 |  |  | 43702.1875 | 60 | 55
2019-08-25 05:00 | 46 | 39 |  |  | 43702.2083 | 62 | 57
2019-08-25 05:30 | 47 | 40 |  |  | 43702.2292 | 64 | 60
2019-08-25 06:00 | 48 | 41 |  |  | 43702.25 | 65 | 61
2019-08-25 06:30 | 46 | 39 |  |  | 43702.2708 | 66 | 61
2019-08-25 07:00 | 45 | 38 |  |  | 43702.2917 | 65 | 61
2019-08-25 07:30 | 44 | 37 |  |  | 43702.3125 | 63 | 60
2019-08-25 08:00 | 43 | 35 |  |  | 43702.3333 | 61 | 58
2019-08-25 08:30 | 44 | 35 |  |  | 43702.3542 | 61 | 58
2019-08-25 09:00 | 34 | 33 |  |  | 43702.375 | 58 | 56
2019-08-25 09:30 | 33 | 31 |  |  | 43702.3958 | 59 | 55
2019-08-25 10:00 | 32 | 29 |  |  | 43702.4167 | 56 | 50
2019-08-25 10:30 | 29 | 26 |  |  | 43702.4375 | 53 | 47
2019-08-25 11:00 | 29 | 25 |  |  | 43702.4583 | 53 | 46
2019-08-25 11:30 | 31 | 28 |  |  | 43702.4792 | 55 | 49
2019-08-25 12:00 | 31 | 27 |  |  | 43702.5 | 55 | 49
2019-08-25 12:30 | 30 | 27 |  |  | 43702.5208 | 55 | 49
2019-08-25 13:00 | 30 | 26 |  |  | 43702.5417 | 56 | 49
2019-08-25 13:30 | 31 | 28 |  |  | 43702.5625 | 56 | 49
2019-08-25 14:00 | 29 | 26 |  |  | 43702.5833 | 53 | 46
2019-08-25 14:30 | 31 | 28 |  |  | 43702.6042 | 55 | 49
2019-08-25 15:00 | 33 | 30 |  |  | 43702.625 | 57 | 51
2019-08-25 15:30 | 35 | 33 |  |  | 43702.6458 | 60 | 55
2019-08-25 16:00 | 40 | 37 |  |  | 43702.6667 | 66 | 60
2019-08-25 16:30 | 42 | 42 |  |  | 43702.6875 | 69 | 66
2019-08-25 17:00 | 48 | 48 |  |  | 43702.7083 | 78 | 76
2019-08-25 17:30 | 54 | 54 |  |  | 43702.7292 | 85 | 83
2019-08-25 18:00 | 62 | 62 |  |  | 43702.75 | 93 | 92
2019-08-25 18:30 | 67 | 67 |  |  | 43702.7708 | 100 | 99
2019-08-25 19:00 | 68 | 68 |  |  | 43702.7917 | 102 | 101
2019-08-25 19:30 | 66 | 66 |  |  | 43702.8125 | 99 | 97
2019-08-25 20:00 | 65 | 65 |  |  | 43702.8333 | 97 | 95
2019-08-25 20:30 | 64 | 64 |  |  | 43702.8542 | 96 | 95
2019-08-25 21:00 | 60 | 60 |  |  | 43702.875 | 92 | 90
2019-08-25 21:30 | 55 | 54 |  |  | 43702.8958 | 86 | 84
2019-08-25 22:00 | 54 | 54 |  |  | 43702.9167 | 86 | 84
2019-08-25 22:30 | 53 | 53 |  |  | 43702.9375 | 85 | 83
2019-08-25 23:00 | 52 | 52 |  |  | 43702.9583 | 81 | 79
2019-08-25 23:30 | 48 | 48 |  |  | 43702.9792 | 77 | 74
2019-08-26 | 45 | 45 |  |  | 43703 | 73 | 70
2019-08-26 00:30 | 41 | 41 |  |  | 43703.0208 | 68 | 64
2019-08-26 01:00 | 38 | 38 |  |  | 43703.0417 | 64 | 59
2019-08-26 01:30 | 36 | 36 |  |  | 43703.0625 | 61 | 56
2019-08-26 02:00 | 35 | 35 |  |  | 43703.0833 | 60 | 55
2019-08-26 02:30 | 34 | 34 |  |  | 43703.1042 | 57 | 52
2019-08-26 03:00 | 32 | 32 |  |  | 43703.125 | 57 | 51
2019-08-26 03:30 | 32 | 32 |  |  | 43703.1458 | 56 | 51
2019-08-26 04:00 | 33 | 33 |  |  | 43703.1667 | 57 | 51
2019-08-26 04:30 | 34 | 34 |  |  | 43703.1875 | 58 | 53
2019-08-26 05:00 | 39 | 39 |  |  | 43703.2083 | 63 | 58
2019-08-26 05:30 | 45 | 45 |  |  | 43703.2292 | 70 | 66
2019-08-26 06:00 | 52 | 52 |  |  | 43703.25 | 77 | 74
2019-08-26 06:30 | 58 | 58 |  |  | 43703.2708 | 89 | 86
2019-08-26 07:00 | 66 | 66 |  |  | 43703.2917 | 103 | 99
2019-08-26 07:30 | 66 | 66 |  |  | 43703.3125 | 107 | 103
2019-08-26 08:00 | 65 | 65 |  |  | 43703.3333 | 105 | 102
2019-08-26 08:30 | 61 | 61 |  |  | 43703.3542 | 101 | 98
2019-08-26 09:00 | 55 | 55 |  |  | 43703.375 | 93 | 90
2019-08-26 09:30 | 52 | 52 |  |  | 43703.3958 | 88 | 85
2019-08-26 10:00 | 46 | 46 |  |  | 43703.4167 | 83 | 79
2019-08-26 10:30 | 45 | 44 |  |  | 43703.4375 | 80 | 77
2019-08-26 11:00 | 44 | 43 |  |  | 43703.4583 | 79 | 76
2019-08-26 11:30 | 45 | 43 |  |  | 43703.4792 | 76 | 76
2019-08-26 12:00 | 42 | 41 |  |  | 43703.5 | 74 | 73
2019-08-26 12:30 | 41 | 39 |  |  | 43703.5208 | 73 | 73
2019-08-26 13:00 | 42 | 40 |  |  | 43703.5417 | 73 | 73
2019-08-26 13:30 | 43 | 41 |  |  | 43703.5625 | 76 | 75
2019-08-26 14:00 | 42 | 40 |  |  | 43703.5833 | 76 | 74
2019-08-26 14:30 | 45 | 44 |  |  | 43703.6042 | 79 | 76
2019-08-26 15:00 | 48 | 47 |  |  | 43703.625 | 87 | 84
2019-08-26 15:30 | 52 | 51 |  |  | 43703.6458 | 93 | 87
2019-08-26 16:00 | 55 | 55 |  |  | 43703.6667 | 96 | 89
2019-08-26 16:30 | 55 | 55 |  |  | 43703.6875 | 98 | 90
2019-08-26 17:00 | 62 | 62 |  |  | 43703.7083 | 105 | 98
2019-08-26 17:30 | 67 | 67 |  |  | 43703.7292 | 110 | 103
2019-08-26 18:00 | 73 | 73 |  |  | 43703.75 | 116 | 109
2019-08-26 18:30 | 73 | 73 |  |  | 43703.7708 | 115 | 107
2019-08-26 19:00 | 73 | 73 |  |  | 43703.7917 | 115 | 108
2019-08-26 19:30 | 73 | 73 |  |  | 43703.8125 | 113 | 108
2019-08-26 20:00 | 72 | 72 |  |  | 43703.8333 | 107 | 106
2019-08-26 20:30 | 71 | 70 |  |  | 43703.8542 | 105 | 104
2019-08-26 21:00 | 65 | 65 |  |  | 43703.875 | 99 | 97
2019-08-26 21:30 | 62 | 62 |  |  | 43703.8958 | 95 | 93
2019-08-26 22:00 | 60 | 59 |  |  | 43703.9167 | 94 | 91
2019-08-26 22:30 | 53 | 53 |  |  | 43703.9375 | 87 | 84
2019-08-26 23:00 | 49 | 49 |  |  | 43703.9583 | 81 | 78
2019-08-26 23:30 | 44 | 44 |  |  | 43703.9792 | 76 | 71
2019-08-27 | 41 | 41 |  |  | 43704 | 72 | 67
2019-08-27 00:30 | 36 | 36 |  |  | 43704.0208 | 67 | 60
2019-08-27 01:00 | 34 | 33 |  |  | 43704.0417 | 61 | 55
2019-08-27 01:30 | 33 | 32 |  |  | 43704.0625 | 59 | 53
2019-08-27 02:00 | 31 | 30 |  |  | 43704.0833 | 57 | 51
2019-08-27 02:30 | 31 | 31 |  |  | 43704.1042 | 57 | 51
2019-08-27 03:00 | 31 | 31 |  |  | 43704.125 | 58 | 51
2019-08-27 03:30 | 31 | 31 |  |  | 43704.1458 | 57 | 51
2019-08-27 04:00 | 31 | 30 |  |  | 43704.1667 | 57 | 50
2019-08-27 04:30 | 31 | 31 |  |  | 43704.1875 | 58 | 52
2019-08-27 05:00 | 34 | 34 |  |  | 43704.2083 | 61 | 55
2019-08-27 05:30 | 38 | 38 |  |  | 43704.2292 | 65 | 61
2019-08-27 06:00 | 45 | 43 |  |  | 43704.25 | 71 | 68
2019-08-27 06:30 | 55 | 53 |  |  | 43704.2708 | 86 | 84
2019-08-27 07:00 | 63 | 61 |  |  | 43704.2917 | 98 | 96
2019-08-27 07:30 | 66 | 64 |  |  | 43704.3125 | 105 | 104
2019-08-27 08:00 | 64 | 63 |  |  | 43704.3333 | 106 | 104
2019-08-27 08:30 | 64 | 64 |  |  | 43704.3542 | 104 | 102
2019-08-27 09:00 | 62 | 61 |  |  | 43704.375 | 100 | 98
2019-08-27 09:30 | 60 | 59 |  |  | 43704.3958 | 97 | 95
2019-08-27 10:00 | 59 | 58 |  |  | 43704.4167 | 95 | 93
2019-08-27 10:30 | 54 | 53 |  |  | 43704.4375 | 88 | 87
2019-08-27 11:00 | 53 | 50 |  |  | 43704.4583 | 85 | 85
2019-08-27 11:30 | 54 | 50 |  |  | 43704.4792 | 85 | 85
2019-08-27 12:00 | 53 | 49 |  |  | 43704.5 | 84 | 84
2019-08-27 12:30 | 50 | 46 |  |  | 43704.5208 | 81 | 81
2019-08-27 13:00 | 52 | 48 |  |  | 43704.5417 | 83 | 83
2019-08-27 13:30 | 52 | 48 |  |  | 43704.5625 | 81 | 81
2019-08-27 14:00 | 56 | 52 |  |  | 43704.5833 | 87 | 87
2019-08-27 14:30 | 60 | 56 |  |  | 43704.6042 | 89 | 89
2019-08-27 15:00 | 63 | 59 |  |  | 43704.625 | 95 | 95
2019-08-27 15:30 | 61 | 58 |  |  | 43704.6458 | 91 | 90
2019-08-27 16:00 | 66 | 64 |  |  | 43704.6667 | 98 | 98
2019-08-27 16:30 | 67 | 65 |  |  | 43704.6875 | 98 | 98
2019-08-27 17:00 | 74 | 73 |  |  | 43704.7083 | 105 | 104
2019-08-27 17:30 | 79 | 78 |  |  | 43704.7292 | 112 | 111
2019-08-27 18:00 | 83 | 82 |  |  | 43704.75 | 117 | 116
2019-08-27 18:30 | 85 | 85 |  |  | 43704.7708 | 118 | 117
2019-08-27 19:00 | 87 | 87 |  |  | 43704.7917 | 122 | 120
2019-08-27 19:30 | 85 | 85 |  |  | 43704.8125 | 118 | 117
2019-08-27 20:00 | 84 | 83 |  |  | 43704.8333 | 116 | 115
2019-08-27 20:30 | 81 | 80 |  |  | 43704.8542 | 113 | 111
2019-08-27 21:00 | 78 | 78 |  |  | 43704.875 | 108 | 107
2019-08-27 21:30 | 75 | 74 |  |  | 43704.8958 | 103 | 102
2019-08-27 22:00 | 72 | 71 |  |  | 43704.9167 | 103 | 101
2019-08-27 22:30 | 67 | 66 |  |  | 43704.9375 | 97 | 95
2019-08-27 23:00 | 62 | 62 |  |  | 43704.9583 | 91 | 89
2019-08-27 23:30 | 58 | 57 |  |  | 43704.9792 | 85 | 83
2019-08-28 | 51 | 51 |  |  | 43705 | 79 | 77
2019-08-28 00:30 | 47 | 47 |  |  | 43705.0208 | 73 | 70
2019-08-28 01:00 | 46 | 45 |  |  | 43705.0417 | 70 | 66
2019-08-28 01:30 | 44 | 43 |  |  | 43705.0625 | 68 | 63
2019-08-28 02:00 | 42 | 42 |  |  | 43705.0833 | 66 | 61
2019-08-28 02:30 | 43 | 42 |  |  | 43705.1042 | 65 | 62
2019-08-28 03:00 | 42 | 41 |  |  | 43705.125 | 64 | 61
2019-08-28 03:30 | 42 | 42 |  |  | 43705.1458 | 64 | 61
2019-08-28 04:00 | 42 | 42 |  |  | 43705.1667 | 64 | 61
2019-08-28 04:30 | 43 | 43 |  |  | 43705.1875 | 66 | 63
2019-08-28 05:00 | 46 | 46 |  |  | 43705.2083 | 70 | 66
2019-08-28 05:30 | 51 | 50 |  |  | 43705.2292 | 74 | 71
2019-08-28 06:00 | 56 | 55 |  |  | 43705.25 | 80 | 78
2019-08-28 06:30 | 64 | 63 |  |  | 43705.2708 | 93 | 92
2019-08-28 07:00 | 70 | 68 |  |  | 43705.2917 | 104 | 104
2019-08-28 07:30 | 70 | 69 |  |  | 43705.3125 | 109 | 108
2019-08-28 08:00 | 68 | 66 |  |  | 43705.3333 | 106 | 106
2019-08-28 08:30 | 65 | 64 |  |  | 43705.3542 | 101 | 100
2019-08-28 09:00 | 69 | 68 |  |  | 43705.375 | 103 | 103
2019-08-28 09:30 | 69 | 67 |  |  | 43705.3958 | 103 | 102
2019-08-28 10:00 | 68 | 65 |  |  | 43705.4167 | 101 | 101
2019-08-28 10:30 | 66 | 63 |  |  | 43705.4375 | 98 | 98
2019-08-28 11:00 | 66 | 64 |  |  | 43705.4583 | 98 | 98
2019-08-28 11:30 | 77 | 75 |  |  | 43705.4792 | 112 | 112
2019-08-28 12:00 | 72 | 71 |  |  | 43705.5 | 113 | 112
2019-08-28 12:30 | 58 | 58 |  |  | 43705.5208 | 99 | 96
2019-08-28 13:00 | 62 | 62 |  |  | 43705.5417 | 100 | 97
2019-08-28 13:30 | 65 | 65 |  |  | 43705.5625 | 102 | 99
2019-08-28 14:00 | 71 | 70 |  |  | 43705.5833 | 107 | 104
2019-08-28 14:30 | 69 | 69 |  |  | 43705.6042 | 104 | 101
2019-08-28 15:00 | 71 | 70 |  |  | 43705.625 | 106 | 103
2019-08-28 15:30 | 73 | 72 |  |  | 43705.6458 | 109 | 106
2019-08-28 16:00 | 75 | 75 |  |  | 43705.6667 | 113 | 109
2019-08-28 16:30 | 76 | 75 |  |  | 43705.6875 | 113 | 109
2019-08-28 17:00 | 79 | 79 |  |  | 43705.7083 | 118 | 114
2019-08-28 17:30 | 82 | 82 |  |  | 43705.7292 | 124 | 119
2019-08-28 18:00 | 84 | 84 |  |  | 43705.75 | 126 | 121
2019-08-28 18:30 | 84 | 84 |  |  | 43705.7708 | 125 | 119
2019-08-28 19:00 | 88 | 88 |  |  | 43705.7917 | 128 | 121
2019-08-28 19:30 | 86 | 86 |  |  | 43705.8125 | 125 | 118
2019-08-28 20:00 | 83 | 83 |  |  | 43705.8333 | 120 | 115
2019-08-28 20:30 | 80 | 80 |  |  | 43705.8542 | 116 | 112
2019-08-28 21:00 | 77 | 76 |  |  | 43705.875 | 111 | 108
2019-08-28 21:30 | 73 | 73 |  |  | 43705.8958 | 106 | 102
2019-08-28 22:00 | 69 | 69 |  |  | 43705.9167 | 103 | 98
2019-08-28 22:30 | 66 | 66 |  |  | 43705.9375 | 99 | 94
2019-08-28 23:00 | 62 | 62 |  |  | 43705.9583 | 93 | 88
2019-08-28 23:30 | 58 | 57 |  |  | 43705.9792 | 83 | 81
2019-08-29 | 51 | 50 |  |  | 43706 | 75 | 73
2019-08-29 00:30 | 46 | 45 |  |  | 43706.0208 | 68 | 65
2019-08-29 01:00 | 43 | 43 |  |  | 43706.0417 | 65 | 62
2019-08-29 01:30 | 41 | 41 |  |  | 43706.0625 | 63 | 60
2019-08-29 02:00 | 40 | 40 |  |  | 43706.0833 | 62 | 58
2019-08-29 02:30 | 40 | 39 |  |  | 43706.1042 | 61 | 57
2019-08-29 03:00 | 39 | 39 |  |  | 43706.125 | 60 | 56
2019-08-29 03:30 | 40 | 40 |  |  | 43706.1458 | 61 | 57
2019-08-29 04:00 | 41 | 40 |  |  | 43706.1667 | 60 | 57
2019-08-29 04:30 | 44 | 43 |  |  | 43706.1875 | 64 | 61
2019-08-29 05:00 | 48 | 47 |  |  | 43706.2083 | 67 | 65
2019-08-29 05:30 | 54 | 53 |  |  | 43706.2292 | 74 | 72
2019-08-29 06:00 | 60 | 59 |  |  | 43706.25 | 81 | 80
2019-08-29 06:30 | 68 | 67 |  |  | 43706.2708 | 96 | 95
2019-08-29 07:00 | 78 | 76 |  |  | 43706.2917 | 110 | 109
2019-08-29 07:30 | 83 | 82 |  |  | 43706.3125 | 119 | 119
2019-08-29 08:00 | 81 | 80 |  |  | 43706.3333 | 119 | 119
2019-08-29 08:30 | 78 | 77 |  |  | 43706.3542 | 118 | 118
2019-08-29 09:00 | 72 | 71 |  |  | 43706.375 | 111 | 110
2019-08-29 09:30 | 72 | 71 |  |  | 43706.3958 | 109 | 108
2019-08-29 10:00 | 73 | 71 |  |  | 43706.4167 | 106 | 106
2019-08-29 10:30 | 68 | 67 |  |  | 43706.4375 | 99 | 99
2019-08-29 11:00 | 68 | 66 |  |  | 43706.4583 | 96 | 96
2019-08-29 11:30 | 71 | 69 |  |  | 43706.4792 | 98 | 98
2019-08-29 12:00 | 68 | 66 |  |  | 43706.5 | 96 | 96
2019-08-29 12:30 | 70 | 68 |  |  | 43706.5208 | 98 | 98
2019-08-29 13:00 | 72 | 70 |  |  | 43706.5417 | 100 | 100
2019-08-29 13:30 | 72 | 71 |  |  | 43706.5625 | 102 | 101
2019-08-29 14:00 | 74 | 72 |  |  | 43706.5833 | 103 | 103
2019-08-29 14:30 | 74 | 73 |  |  | 43706.6042 | 104 | 104
2019-08-29 15:00 | 74 | 73 |  |  | 43706.625 | 103 | 103
2019-08-29 15:30 | 73 | 72 |  |  | 43706.6458 | 104 | 103
2019-08-29 16:00 | 75 | 74 |  |  | 43706.6667 | 106 | 105
2019-08-29 16:30 | 78 | 77 |  |  | 43706.6875 | 108 | 107
2019-08-29 17:00 | 83 | 82 |  |  | 43706.7083 | 114 | 113
2019-08-29 17:30 | 87 | 86 |  |  | 43706.7292 | 120 | 119
2019-08-29 18:00 | 93 | 93 |  |  | 43706.75 | 128 | 127
2019-08-29 18:30 | 91 | 91 |  |  | 43706.7708 | 126 | 124
2019-08-29 19:00 | 90 | 90 |  |  | 43706.7917 | 125 | 123
2019-08-29 19:30 | 89 | 89 |  |  | 43706.8125 | 124 | 122
2019-08-29 20:00 | 89 | 89 |  |  | 43706.8333 | 123 | 121
2019-08-29 20:30 | 87 | 87 |  |  | 43706.8542 | 121 | 119
2019-08-29 21:00 | 82 | 82 |  |  | 43706.875 | 115 | 112
2019-08-29 21:30 | 76 | 76 |  |  | 43706.8958 | 107 | 105
2019-08-29 22:00 | 72 | 72 |  |  | 43706.9167 | 104 | 101
2019-08-29 22:30 | 68 | 68 |  |  | 43706.9375 | 101 | 99
2019-08-29 23:00 | 64 | 64 |  |  | 43706.9583 | 93 | 91
2019-08-29 23:30 | 58 | 58 |  |  | 43706.9792 | 87 | 84
2019-08-30 | 52 | 52 |  |  | 43707 | 80 | 77
2019-08-30 00:30 | 46 | 46 |  |  | 43707.0208 | 74 | 70
2019-08-30 01:00 | 45 | 45 |  |  | 43707.0417 | 70 | 66
2019-08-30 01:30 | 42 | 42 |  |  | 43707.0625 | 66 | 63
2019-08-30 02:00 | 41 | 41 |  |  | 43707.0833 | 64 | 61
2019-08-30 02:30 | 43 | 42 |  |  | 43707.1042 | 64 | 62
2019-08-30 03:00 | 43 | 42 |  |  | 43707.125 | 64 | 62
2019-08-30 03:30 | 44 | 42 |  |  | 43707.1458 | 64 | 62
2019-08-30 04:00 | 43 | 42 |  |  | 43707.1667 | 63 | 61
2019-08-30 04:30 | 43 | 42 |  |  | 43707.1875 | 64 | 62
2019-08-30 05:00 | 46 | 45 |  |  | 43707.2083 | 67 | 65
2019-08-30 05:30 | 53 | 51 |  |  | 43707.2292 | 74 | 73
2019-08-30 06:00 | 60 | 58 |  |  | 43707.25 | 82 | 82
2019-08-30 06:30 | 65 | 65 |  |  | 43707.2708 | 98 | 94
2019-08-30 07:00 | 72 | 72 |  |  | 43707.2917 | 113 | 106
2019-08-30 07:30 | 76 | 76 |  |  | 43707.3125 | 118 | 112
2019-08-30 08:00 | 72 | 72 |  |  | 43707.3333 | 115 | 110
2019-08-30 08:30 | 66 | 66 |  |  | 43707.3542 | 104 | 103
2019-08-30 09:00 | 61 | 59 |  |  | 43707.375 | 94 | 94
2019-08-30 09:30 | 57 | 56 |  |  | 43707.3958 | 90 | 90
2019-08-30 10:00 | 57 | 55 |  |  | 43707.4167 | 88 | 88
2019-08-30 10:30 | 53 | 51 |  |  | 43707.4375 | 82 | 82
2019-08-30 11:00 | 54 | 52 |  |  | 43707.4583 | 82 | 82
2019-08-30 11:30 | 55 | 53 |  |  | 43707.4792 | 85 | 84
2019-08-30 12:00 | 55 | 53 |  |  | 43707.5 | 85 | 84
2019-08-30 12:30 | 58 | 57 |  |  | 43707.5208 | 90 | 89
2019-08-30 13:00 | 57 | 55 |  |  | 43707.5417 | 90 | 88
2019-08-30 13:30 | 56 | 55 |  |  | 43707.5625 | 92 | 90
2019-08-30 14:00 | 56 | 56 |  |  | 43707.5833 | 92 | 89
2019-08-30 14:30 | 58 | 57 |  |  | 43707.6042 | 92 | 90
2019-08-30 15:00 | 59 | 58 |  |  | 43707.625 | 91 | 89
2019-08-30 15:30 | 63 | 62 |  |  | 43707.6458 | 93 | 90
2019-08-30 16:00 | 63 | 63 |  |  | 43707.6667 | 97 | 95
2019-08-30 16:30 | 64 | 64 |  |  | 43707.6875 | 100 | 96
2019-08-30 17:00 | 69 | 68 |  |  | 43707.7083 | 104 | 101
2019-08-30 17:30 | 73 | 73 |  |  | 43707.7292 | 109 | 105
2019-08-30 18:00 | 76 | 75 |  |  | 43707.75 | 111 | 108
2019-08-30 18:30 | 75 | 75 |  |  | 43707.7708 | 111 | 107
2019-08-30 19:00 | 76 | 76 |  |  | 43707.7917 | 113 | 109
2019-08-30 19:30 | 73 | 73 |  |  | 43707.8125 | 110 | 105
2019-08-30 20:00 | 73 | 73 |  |  | 43707.8333 | 109 | 104
2019-08-30 20:30 | 73 | 73 |  |  | 43707.8542 | 108 | 104
2019-08-30 21:00 | 68 | 68 |  |  | 43707.875 | 101 | 98
2019-08-30 21:30 | 62 | 61 |  |  | 43707.8958 | 93 | 90
2019-08-30 22:00 | 60 | 60 |  |  | 43707.9167 | 92 | 89
2019-08-30 22:30 | 59 | 58 |  |  | 43707.9375 | 91 | 88
2019-08-30 23:00 | 57 | 56 |  |  | 43707.9583 | 86 | 83
2019-08-30 23:30 | 52 | 52 |  |  | 43707.9792 | 82 | 78
2019-08-31 | 48 | 47 |  |  | 43708 | 77 | 72
2019-08-31 00:30 | 43 | 42 |  |  | 43708.0208 | 71 | 64
2019-08-31 01:00 | 43 | 40 |  |  | 43708.0417 | 72 | 60
2019-08-31 01:30 | 41 | 38 |  |  | 43708.0625 | 71 | 57
2019-08-31 02:00 | 41 | 38 |  |  | 43708.0833 | 71 | 56
2019-08-31 02:30 | 39 | 36 |  |  | 43708.1042 | 70 | 55
2019-08-31 03:00 | 38 | 35 |  |  | 43708.125 | 68 | 53
2019-08-31 03:30 | 39 | 36 |  |  | 43708.1458 | 69 | 55
2019-08-31 04:00 | 42 | 39 |  |  | 43708.1667 | 68 | 58
2019-08-31 04:30 | 43 | 39 |  |  | 43708.1875 | 69 | 59
2019-08-31 05:00 | 44 | 40 |  |  | 43708.2083 | 70 | 60
2019-08-31 05:30 | 48 | 45 |  |  | 43708.2292 | 74 | 64
2019-08-31 06:00 | 50 | 46 |  |  | 43708.25 | 75 | 66
2019-08-31 06:30 | 49 | 45 |  |  | 43708.2708 | 75 | 67
2019-08-31 07:00 | 46 | 41 |  |  | 43708.2917 | 73 | 64
2019-08-31 07:30 | 45 | 39 |  |  | 43708.3125 | 71 | 63
2019-08-31 08:00 | 45 | 39 |  |  | 43708.3333 | 70 | 63
2019-08-31 08:30 | 44 | 38 |  |  | 43708.3542 | 69 | 62
2019-08-31 09:00 | 42 | 35 |  |  | 43708.375 | 65 | 59
2019-08-31 09:30 | 40 | 33 |  |  | 43708.3958 | 63 | 56
2019-08-31 10:00 | 39 | 31 |  |  | 43708.4167 | 62 | 54
2019-08-31 10:30 | 39 | 32 |  |  | 43708.4375 | 61 | 53
2019-08-31 11:00 | 37 | 30 |  |  | 43708.4583 | 59 | 51
2019-08-31 11:30 | 36 | 28 |  |  | 43708.4792 | 57 | 49
2019-08-31 12:00 | 37 | 30 |  |  | 43708.5 | 57 | 48
2019-08-31 12:30 | 37 | 32 |  |  | 43708.5208 | 57 | 45
2019-08-31 13:00 | 37 | 32 |  |  | 43708.5417 | 61 | 50
2019-08-31 13:30 | 39 | 34 |  |  | 43708.5625 | 59 | 48
2019-08-31 14:00 | 37 | 31 |  |  | 43708.5833 | 60 | 49
2019-08-31 14:30 | 37 | 32 |  |  | 43708.6042 | 61 | 50
2019-08-31 15:00 | 40 | 35 |  |  | 43708.625 | 62 | 51
2019-08-31 15:30 | 42 | 37 |  |  | 43708.6458 | 66 | 56
2019-08-31 16:00 | 44 | 40 |  |  | 43708.6667 | 70 | 61
2019-08-31 16:30 | 46 | 41 |  |  | 43708.6875 | 73 | 65
2019-08-31 17:00 | 52 | 48 |  |  | 43708.7083 | 83 | 75
2019-08-31 17:30 | 57 | 54 |  |  | 43708.7292 | 87 | 80
2019-08-31 18:00 | 61 | 57 |  |  | 43708.75 | 92 | 86
2019-08-31 18:30 | 63 | 61 |  |  | 43708.7708 | 101 | 92
2019-08-31 19:00 | 64 | 64 |  |  | 43708.7917 | 116 | 96
2019-08-31 19:30 | 62 | 62 |  |  | 43708.8125 | 114 | 94
2019-08-31 20:00 | 61 | 61 |  |  | 43708.8333 | 114 | 93
2019-08-31 20:30 | 61 | 61 |  |  | 43708.8542 | 107 | 92
2019-08-31 21:00 | 59 | 57 |  |  | 43708.875 | 94 | 85
2019-08-31 21:30 | 56 | 54 |  |  | 43708.8958 | 91 | 81
2019-08-31 22:00 | 54 | 52 |  |  | 43708.9167 | 91 | 80
2019-08-31 22:30 | 53 | 51 |  |  | 43708.9375 | 89 | 79
2019-08-31 23:00 | 51 | 49 |  |  | 43708.9583 | 86 | 75
2019-08-31 23:30 | 47 | 45 |  |  | 43708.9792 | 83 | 70
2019-09-01 | 42 | 39 |  |  | 43709 | 76 | 63
2019-09-01 00:30 | 40 | 37 |  |  | 43709.0208 | 70 | 58
2019-09-01 01:00 | 41 | 35 |  |  | 43709.0417 | 65 | 55
2019-09-01 01:30 | 42 | 34 |  |  | 43709.0625 | 59 | 53
2019-09-01 02:00 | 41 | 34 |  |  | 43709.0833 | 57 | 51
2019-09-01 02:30 | 39 | 31 |  |  | 43709.1042 | 54 | 47
2019-09-01 03:00 | 36 | 27 |  |  | 43709.125 | 50 | 43
2019-09-01 03:30 | 37 | 29 |  |  | 43709.1458 | 52 | 45
2019-09-01 04:00 | 39 | 30 |  |  | 43709.1667 | 52 | 46
2019-09-01 04:30 | 42 | 33 |  |  | 43709.1875 | 55 | 50
2019-09-01 05:00 | 45 | 37 |  |  | 43709.2083 | 59 | 54
2019-09-01 05:30 | 47 | 39 |  |  | 43709.2292 | 62 | 57
2019-09-01 06:00 | 48 | 40 |  |  | 43709.25 | 63 | 58
2019-09-01 06:30 | 46 | 39 |  |  | 43709.2708 | 65 | 60
2019-09-01 07:00 | 44 | 39 |  |  | 43709.2917 | 64 | 61
2019-09-01 07:30 | 36 | 36 |  |  | 43709.3125 | 61 | 60
2019-09-01 08:00 | 32 | 32 |  |  | 43709.3333 | 57 | 55
2019-09-01 08:30 | 32 | 32 |  |  | 43709.3542 | 58 | 55
2019-09-01 09:00 | 32 | 32 |  |  | 43709.375 | 58 | 55
2019-09-01 09:30 | 31 | 31 |  |  | 43709.3958 | 57 | 54
2019-09-01 10:00 | 30 | 29 |  |  | 43709.4167 | 55 | 52
2019-09-01 10:30 | 30 | 29 |  |  | 43709.4375 | 54 | 51
2019-09-01 11:00 | 29 | 29 |  |  | 43709.4583 | 53 | 50
2019-09-01 11:30 | 29 | 29 |  |  | 43709.4792 | 53 | 49
2019-09-01 12:00 | 30 | 30 |  |  | 43709.5 | 53 | 50
2019-09-01 12:30 | 29 | 29 |  |  | 43709.5208 | 52 | 50
2019-09-01 13:00 | 30 | 30 |  |  | 43709.5417 | 53 | 50
2019-09-01 13:30 | 30 | 30 |  |  | 43709.5625 | 53 | 51
2019-09-01 14:00 | 32 | 32 |  |  | 43709.5833 | 55 | 52
2019-09-01 14:30 | 34 | 33 |  |  | 43709.6042 | 58 | 55
2019-09-01 15:00 | 35 | 35 |  |  | 43709.625 | 59 | 56
2019-09-01 15:30 | 35 | 34 |  |  | 43709.6458 | 59 | 56
2019-09-01 16:00 | 40 | 40 |  |  | 43709.6667 | 66 | 64
2019-09-01 16:30 | 47 | 47 |  |  | 43709.6875 | 73 | 71
2019-09-01 17:00 | 52 | 52 |  |  | 43709.7083 | 80 | 79
2019-09-01 17:30 | 57 | 56 |  |  | 43709.7292 | 83 | 83
2019-09-01 18:00 | 63 | 62 |  |  | 43709.75 | 89 | 89
2019-09-01 18:30 | 67 | 67 |  |  | 43709.7708 | 95 | 95
2019-09-01 19:00 | 68 | 68 |  |  | 43709.7917 | 97 | 97
2019-09-01 19:30 | 67 | 66 |  |  | 43709.8125 | 95 | 95
2019-09-01 20:00 | 65 | 65 |  |  | 43709.8333 | 94 | 94
2019-09-01 20:30 | 64 | 64 |  |  | 43709.8542 | 93 | 92
2019-09-01 21:00 | 62 | 61 |  |  | 43709.875 | 89 | 88
2019-09-01 21:30 | 57 | 56 |  |  | 43709.8958 | 84 | 84
2019-09-01 22:00 | 56 | 55 |  |  | 43709.9167 | 84 | 84
2019-09-01 22:30 | 52 | 51 |  |  | 43709.9375 | 80 | 79
2019-09-01 23:00 | 50 | 49 |  |  | 43709.9583 | 75 | 75
2019-09-01 23:30 | 50 | 48 |  |  | 43709.9792 | 74 | 74
2019-09-02 | 49 | 47 |  |  | 43710 | 72 | 72
2019-09-02 00:30 | 43 | 42 |  |  | 43710.0208 | 65 | 65
2019-09-02 01:00 | 40 | 39 |  |  | 43710.0417 | 59 | 59
2019-09-02 01:30 | 38 | 37 |  |  | 43710.0625 | 57 | 57
2019-09-02 02:00 | 40 | 39 |  |  | 43710.0833 | 59 | 59
2019-09-02 02:30 | 42 | 41 |  |  | 43710.1042 | 62 | 61
2019-09-02 03:00 | 44 | 42 |  |  | 43710.125 | 61 | 61
2019-09-02 03:30 | 44 | 42 |  |  | 43710.1458 | 63 | 62
2019-09-02 04:00 | 45 | 45 |  |  | 43710.1667 | 65 | 64
2019-09-02 04:30 | 47 | 46 |  |  | 43710.1875 | 67 | 66
2019-09-02 05:00 | 51 | 50 |  |  | 43710.2083 | 71 | 70
2019-09-02 05:30 | 54 | 54 |  |  | 43710.2292 | 76 | 74
2019-09-02 06:00 | 59 | 59 |  |  | 43710.25 | 82 | 80
2019-09-02 06:30 | 61 | 61 |  |  | 43710.2708 | 91 | 87
2019-09-02 07:00 | 65 | 65 |  |  | 43710.2917 | 99 | 93
2019-09-02 07:30 | 67 | 67 |  |  | 43710.3125 | 103 | 98
2019-09-02 08:00 | 64 | 64 |  |  | 43710.3333 | 102 | 97
2019-09-02 08:30 | 61 | 60 |  |  | 43710.3542 | 99 | 93
2019-09-02 09:00 | 56 | 56 |  |  | 43710.375 | 94 | 88
2019-09-02 09:30 | 54 | 53 |  |  | 43710.3958 | 90 | 84
2019-09-02 10:00 | 53 | 53 |  |  | 43710.4167 | 89 | 82
2019-09-02 10:30 | 51 | 51 |  |  | 43710.4375 | 87 | 80
2019-09-02 11:00 | 51 | 50 |  |  | 43710.4583 | 85 | 79
2019-09-02 11:30 | 51 | 50 |  |  | 43710.4792 | 86 | 78
2019-09-02 12:00 | 50 | 49 |  |  | 43710.5 | 86 | 78
2019-09-02 12:30 | 49 | 49 |  |  | 43710.5208 | 87 | 78
2019-09-02 13:00 | 50 | 50 |  |  | 43710.5417 | 88 | 79
2019-09-02 13:30 | 51 | 51 |  |  | 43710.5625 | 89 | 81
2019-09-02 14:00 | 54 | 54 |  |  | 43710.5833 | 93 | 85
2019-09-02 14:30 | 57 | 56 |  |  | 43710.6042 | 98 | 88
2019-09-02 15:00 | 58 | 58 |  |  | 43710.625 | 99 | 89
2019-09-02 15:30 | 63 | 62 |  |  | 43710.6458 | 102 | 93
2019-09-02 16:00 | 66 | 66 |  |  | 43710.6667 | 106 | 98
2019-09-02 16:30 | 69 | 68 |  |  | 43710.6875 | 109 | 101
2019-09-02 17:00 | 73 | 72 |  |  | 43710.7083 | 112 | 105
2019-09-02 17:30 | 76 | 76 |  |  | 43710.7292 | 115 | 109
2019-09-02 18:00 | 78 | 78 |  |  | 43710.75 | 117 | 112
2019-09-02 18:30 | 79 | 79 |  |  | 43710.7708 | 118 | 113
2019-09-02 19:00 | 80 | 80 |  |  | 43710.7917 | 120 | 114
2019-09-02 19:30 | 77 | 77 |  |  | 43710.8125 | 115 | 110
2019-09-02 20:00 | 75 | 75 |  |  | 43710.8333 | 111 | 106
2019-09-02 20:30 | 73 | 73 |  |  | 43710.8542 | 109 | 104
2019-09-02 21:00 | 67 | 67 |  |  | 43710.875 | 103 | 97
2019-09-02 21:30 | 63 | 63 |  |  | 43710.8958 | 97 | 90
2019-09-02 22:00 | 62 | 62 |  |  | 43710.9167 | 96 | 90
2019-09-02 22:30 | 59 | 59 |  |  | 43710.9375 | 94 | 88
2019-09-02 23:00 | 58 | 58 |  |  | 43710.9583 | 91 | 85
2019-09-02 23:30 | 53 | 53 |  |  | 43710.9792 | 86 | 80
2019-09-03 | 50 | 50 |  |  | 43711 | 83 | 76
2019-09-03 00:30 | 47 | 47 |  |  | 43711.0208 | 79 | 71
2019-09-03 01:00 | 46 | 46 |  |  | 43711.0417 | 76 | 69
2019-09-03 01:30 | 44 | 44 |  |  | 43711.0625 | 74 | 66
2019-09-03 02:00 | 46 | 46 |  |  | 43711.0833 | 75 | 68
2019-09-03 02:30 | 47 | 47 |  |  | 43711.1042 | 75 | 68
2019-09-03 03:00 | 46 | 46 |  |  | 43711.125 | 75 | 67
2019-09-03 03:30 | 46 | 46 |  |  | 43711.1458 | 78 | 68
2019-09-03 04:00 | 46 | 46 |  |  | 43711.1667 | 76 | 67
2019-09-03 04:30 | 45 | 45 |  |  | 43711.1875 | 76 | 66
2019-09-03 05:00 | 51 | 51 |  |  | 43711.2083 | 80 | 71
2019-09-03 05:30 | 56 | 56 |  |  | 43711.2292 | 86 | 77
2019-09-03 06:00 | 60 | 60 |  |  | 43711.25 | 92 | 82
2019-09-03 06:30 | 62 | 62 |  |  | 43711.2708 | 94 | 87
2019-09-03 07:00 | 67 | 66 |  |  | 43711.2917 | 102 | 95
2019-09-03 07:30 | 68 | 67 |  |  | 43711.3125 | 99 | 99
2019-09-03 08:00 | 66 | 65 |  |  | 43711.3333 | 99 | 99
2019-09-03 08:30 | 62 | 61 |  |  | 43711.3542 | 95 | 95
2019-09-03 09:00 | 56 | 55 |  |  | 43711.375 | 88 | 88
2019-09-03 09:30 | 54 | 53 |  |  | 43711.3958 | 86 | 85
2019-09-03 10:00 | 50 | 50 |  |  | 43711.4167 | 91 | 80
2019-09-03 10:30 | 52 | 50 |  |  | 43711.4375 | 95 | 80
2019-09-03 11:00 | 51 | 49 |  |  | 43711.4583 | 95 | 79
2019-09-03 11:30 | 50 | 49 |  |  | 43711.4792 | 95 | 79
2019-09-03 12:00 | 50 | 48 |  |  | 43711.5 | 95 | 78
2019-09-03 12:30 | 50 | 48 |  |  | 43711.5208 | 95 | 79
2019-09-03 13:00 | 51 | 49 |  |  | 43711.5417 | 96 | 79
2019-09-03 13:30 | 52 | 50 |  |  | 43711.5625 | 95 | 82
2019-09-03 14:00 | 52 | 51 |  |  | 43711.5833 | 95 | 82
2019-09-03 14:30 | 55 | 54 |  |  | 43711.6042 | 97 | 85
2019-09-03 15:00 | 55 | 54 |  |  | 43711.625 | 97 | 85
2019-09-03 15:30 | 57 | 56 |  |  | 43711.6458 | 98 | 88
2019-09-03 16:00 | 61 | 61 |  |  | 43711.6667 | 102 | 93
2019-09-03 16:30 | 69 | 69 |  |  | 43711.6875 | 110 | 103
2019-09-03 17:00 | 76 | 76 |  |  | 43711.7083 | 114 | 110
2019-09-03 17:30 | 79 | 79 |  |  | 43711.7292 | 116 | 114
2019-09-03 18:00 | 83 | 83 |  |  | 43711.75 | 118 | 116
2019-09-03 18:30 | 83 | 83 |  |  | 43711.7708 | 118 | 116
2019-09-03 19:00 | 83 | 83 |  |  | 43711.7917 | 118 | 116
2019-09-03 19:30 | 79 | 79 |  |  | 43711.8125 | 114 | 112
2019-09-03 20:00 | 77 | 77 |  |  | 43711.8333 | 111 | 109
2019-09-03 20:30 | 77 | 76 |  |  | 43711.8542 | 110 | 108
2019-09-03 21:00 | 70 | 70 |  |  | 43711.875 | 104 | 101
2019-09-03 21:30 | 67 | 67 |  |  | 43711.8958 | 103 | 97
2019-09-03 22:00 | 65 | 65 |  |  | 43711.9167 | 101 | 95
2019-09-03 22:30 | 62 | 62 |  |  | 43711.9375 | 98 | 92
2019-09-03 23:00 | 59 | 59 |  |  | 43711.9583 | 93 | 86
2019-09-03 23:30 | 55 | 55 |  |  | 43711.9792 | 88 | 81
2019-09-04 | 50 | 50 |  |  | 43712 | 83 | 76
2019-09-04 00:30 | 45 | 45 |  |  | 43712.0208 | 79 | 70
2019-09-04 01:00 | 43 | 42 |  |  | 43712.0417 | 75 | 65
2019-09-04 01:30 | 41 | 41 |  |  | 43712.0625 | 73 | 63
2019-09-04 02:00 | 41 | 41 |  |  | 43712.0833 | 72 | 63
2019-09-04 02:30 | 43 | 43 |  |  | 43712.1042 | 72 | 63
2019-09-04 03:00 | 43 | 43 |  |  | 43712.125 | 72 | 63
2019-09-04 03:30 | 44 | 44 |  |  | 43712.1458 | 73 | 65
2019-09-04 04:00 | 44 | 44 |  |  | 43712.1667 | 74 | 66
2019-09-04 04:30 | 46 | 46 |  |  | 43712.1875 | 76 | 67
2019-09-04 05:00 | 50 | 50 |  |  | 43712.2083 | 80 | 72
2019-09-04 05:30 | 54 | 54 |  |  | 43712.2292 | 86 | 78
2019-09-04 06:00 | 58 | 58 |  |  | 43712.25 | 90 | 82
2019-09-04 06:30 | 62 | 62 |  |  | 43712.2708 | 98 | 92
2019-09-04 07:00 | 70 | 70 |  |  | 43712.2917 | 108 | 102
2019-09-04 07:30 | 77 | 76 |  |  | 43712.3125 | 115 | 110
2019-09-04 08:00 | 77 | 76 |  |  | 43712.3333 | 116 | 112
2019-09-04 08:30 | 74 | 73 |  |  | 43712.3542 | 111 | 107
2019-09-04 09:00 | 70 | 69 |  |  | 43712.375 | 107 | 102
2019-09-04 09:30 | 66 | 65 |  |  | 43712.3958 | 104 | 98
2019-09-04 10:00 | 64 | 64 |  |  | 43712.4167 | 107 | 97
2019-09-04 10:30 | 63 | 63 |  |  | 43712.4375 | 106 | 95
2019-09-04 11:00 | 63 | 63 |  |  | 43712.4583 | 107 | 96
2019-09-04 11:30 | 64 | 64 |  |  | 43712.4792 | 106 | 96
2019-09-04 12:00 | 66 | 66 |  |  | 43712.5 | 109 | 99
2019-09-04 12:30 | 67 | 67 |  |  | 43712.5208 | 110 | 100
2019-09-04 13:00 | 70 | 70 |  |  | 43712.5417 | 112 | 103
2019-09-04 13:30 | 74 | 73 |  |  | 43712.5625 | 120 | 108
2019-09-04 14:00 | 76 | 75 |  |  | 43712.5833 | 123 | 110
2019-09-04 14:30 | 76 | 75 |  |  | 43712.6042 | 117 | 111
2019-09-04 15:00 | 77 | 77 |  |  | 43712.625 | 117 | 112
2019-09-04 15:30 | 79 | 79 |  |  | 43712.6458 | 118 | 113
2019-09-04 16:00 | 83 | 83 |  |  | 43712.6667 | 122 | 118
2019-09-04 16:30 | 85 | 85 |  |  | 43712.6875 | 124 | 120
2019-09-04 17:00 | 86 | 86 |  |  | 43712.7083 | 123 | 120
2019-09-04 17:30 | 87 | 87 |  |  | 43712.7292 | 124 | 122
2019-09-04 18:00 | 85 | 85 |  |  | 43712.75 | 122 | 120
2019-09-04 18:30 | 84 | 84 |  |  | 43712.7708 | 119 | 117
2019-09-04 19:00 | 83 | 83 |  |  | 43712.7917 | 118 | 116
2019-09-04 19:30 | 80 | 80 |  |  | 43712.8125 | 113 | 111
2019-09-04 20:00 | 77 | 77 |  |  | 43712.8333 | 111 | 108
2019-09-04 20:30 | 76 | 76 |  |  | 43712.8542 | 109 | 107
2019-09-04 21:00 | 72 | 72 |  |  | 43712.875 | 101 | 100
2019-09-04 21:30 | 66 | 66 |  |  | 43712.8958 | 95 | 93
2019-09-04 22:00 | 65 | 65 |  |  | 43712.9167 | 95 | 93
2019-09-04 22:30 | 60 | 60 |  |  | 43712.9375 | 90 | 88
2019-09-04 23:00 | 58 | 58 |  |  | 43712.9583 | 86 | 84
2019-09-04 23:30 | 55 | 54 |  |  | 43712.9792 | 80 | 80
2019-09-05 | 49 | 47 |  |  | 43713 | 72 | 71
2019-09-05 00:30 | 47 | 45 |  |  | 43713.0208 | 68 | 66
2019-09-05 01:00 | 43 | 41 |  |  | 43713.0417 | 63 | 62
2019-09-05 01:30 | 40 | 38 |  |  | 43713.0625 | 59 | 58
2019-09-05 02:00 | 40 | 38 |  |  | 43713.0833 | 58 | 57
2019-09-05 02:30 | 43 | 40 |  |  | 43713.1042 | 60 | 58
2019-09-05 03:00 | 40 | 37 |  |  | 43713.125 | 58 | 55
2019-09-05 03:30 | 40 | 37 |  |  | 43713.1458 | 58 | 55
2019-09-05 04:00 | 40 | 36 |  |  | 43713.1667 | 58 | 55
2019-09-05 04:30 | 41 | 38 |  |  | 43713.1875 | 59 | 56
2019-09-05 05:00 | 45 | 41 |  |  | 43713.2083 | 63 | 60
2019-09-05 05:30 | 50 | 46 |  |  | 43713.2292 | 68 | 65
2019-09-05 06:00 | 55 | 50 |  |  | 43713.25 | 75 | 71
2019-09-05 06:30 | 63 | 59 |  |  | 43713.2708 | 88 | 85
2019-09-05 07:00 | 69 | 66 |  |  | 43713.2917 | 98 | 97
2019-09-05 07:30 | 71 | 69 |  |  | 43713.3125 | 103 | 103
2019-09-05 08:00 | 70 | 67 |  |  | 43713.3333 | 103 | 101
2019-09-05 08:30 | 69 | 67 |  |  | 43713.3542 | 102 | 101
2019-09-05 09:00 | 66 | 63 |  |  | 43713.375 | 98 | 96
2019-09-05 09:30 | 64 | 61 |  |  | 43713.3958 | 95 | 93
2019-09-05 10:00 | 63 | 60 |  |  | 43713.4167 | 96 | 93
2019-09-05 10:30 | 64 | 60 |  |  | 43713.4375 | 96 | 93
2019-09-05 11:00 | 65 | 61 |  |  | 43713.4583 | 96 | 93
2019-09-05 11:30 | 66 | 61 |  |  | 43713.4792 | 98 | 94
2019-09-05 12:00 | 67 | 63 |  |  | 43713.5 | 100 | 97
2019-09-05 12:30 | 69 | 65 |  |  | 43713.5208 | 103 | 99
2019-09-05 13:00 | 69 | 65 |  |  | 43713.5417 | 104 | 101
2019-09-05 13:30 | 70 | 66 |  |  | 43713.5625 | 104 | 101
2019-09-05 14:00 | 71 | 67 |  |  | 43713.5833 | 104 | 102
2019-09-05 14:30 | 72 | 69 |  |  | 43713.6042 | 105 | 103
2019-09-05 15:00 | 73 | 70 |  |  | 43713.625 | 107 | 104
2019-09-05 15:30 | 77 | 74 |  |  | 43713.6458 | 111 | 109
2019-09-05 16:00 | 79 | 77 |  |  | 43713.6667 | 114 | 113
2019-09-05 16:30 | 81 | 80 |  |  | 43713.6875 | 116 | 115
2019-09-05 17:00 | 81 | 80 |  |  | 43713.7083 | 117 | 117
2019-09-05 17:30 | 80 | 79 |  |  | 43713.7292 | 116 | 116
2019-09-05 18:00 | 80 | 79 |  |  | 43713.75 | 115 | 115
2019-09-05 18:30 | 81 | 80 |  |  | 43713.7708 | 115 | 114
2019-09-05 19:00 | 82 | 81 |  |  | 43713.7917 | 115 | 115
2019-09-05 19:30 | 78 | 77 |  |  | 43713.8125 | 111 | 111
2019-09-05 20:00 | 77 | 77 |  |  | 43713.8333 | 109 | 109
2019-09-05 20:30 | 76 | 75 |  |  | 43713.8542 | 106 | 106
2019-09-05 21:00 | 71 | 70 |  |  | 43713.875 | 101 | 100
2019-09-05 21:30 | 66 | 65 |  |  | 43713.8958 | 94 | 94
2019-09-05 22:00 | 64 | 62 |  |  | 43713.9167 | 92 | 92
2019-09-05 22:30 | 61 | 59 |  |  | 43713.9375 | 89 | 89
2019-09-05 23:00 | 57 | 56 |  |  | 43713.9583 | 83 | 83
2019-09-05 23:30 | 52 | 51 |  |  | 43713.9792 | 78 | 78
2019-09-06 | 47 | 46 |  |  | 43714 | 71 | 70
2019-09-06 00:30 | 46 | 44 |  |  | 43714.0208 | 67 | 66
2019-09-06 01:00 | 44 | 42 |  |  | 43714.0417 | 65 | 64
2019-09-06 01:30 | 43 | 42 |  |  | 43714.0625 | 63 | 62
2019-09-06 02:00 | 45 | 42 |  |  | 43714.0833 | 61 | 61
2019-09-06 02:30 | 49 | 43 |  |  | 43714.1042 | 62 | 62
2019-09-06 03:00 | 49 | 43 |  |  | 43714.125 | 62 | 62
2019-09-06 03:30 | 49 | 44 |  |  | 43714.1458 | 63 | 63
2019-09-06 04:00 | 50 | 44 |  |  | 43714.1667 | 63 | 63
2019-09-06 04:30 | 51 | 46 |  |  | 43714.1875 | 65 | 65
2019-09-06 05:00 | 53 | 48 |  |  | 43714.2083 | 68 | 68
2019-09-06 05:30 | 59 | 53 |  |  | 43714.2292 | 74 | 74
2019-09-06 06:00 | 65 | 59 |  |  | 43714.25 | 81 | 81
2019-09-06 06:30 | 67 | 61 |  |  | 43714.2708 | 87 | 87
2019-09-06 07:00 | 72 | 65 |  |  | 43714.2917 | 94 | 94
2019-09-06 07:30 | 74 | 67 |  |  | 43714.3125 | 100 | 100
2019-09-06 08:00 | 71 | 63 |  |  | 43714.3333 | 95 | 95
2019-09-06 08:30 | 66 | 57 |  |  | 43714.3542 | 90 | 89
2019-09-06 09:00 | 63 | 52 |  |  | 43714.375 | 85 | 84
2019-09-06 09:30 | 62 | 51 |  |  | 43714.3958 | 83 | 81
2019-09-06 10:00 | 63 | 52 |  |  | 43714.4167 | 84 | 83
2019-09-06 10:30 | 62 | 50 |  |  | 43714.4375 | 84 | 82
2019-09-06 11:00 | 63 | 51 |  |  | 43714.4583 | 84 | 82
2019-09-06 11:30 | 60 | 49 |  |  | 43714.4792 | 82 | 80
2019-09-06 12:00 | 60 | 48 |  |  | 43714.5 | 81 | 80
2019-09-06 12:30 | 61 | 50 |  |  | 43714.5208 | 84 | 82
2019-09-06 13:00 | 65 | 56 |  |  | 43714.5417 | 90 | 89
2019-09-06 13:30 | 67 | 57 |  |  | 43714.5625 | 93 | 91
2019-09-06 14:00 | 69 | 59 |  |  | 43714.5833 | 94 | 93
2019-09-06 14:30 | 71 | 62 |  |  | 43714.6042 | 97 | 97
2019-09-06 15:00 | 74 | 65 |  |  | 43714.625 | 102 | 102
2019-09-06 15:30 | 77 | 69 |  |  | 43714.6458 | 106 | 105
2019-09-06 16:00 | 81 | 76 |  |  | 43714.6667 | 113 | 113
2019-09-06 16:30 | 90 | 81 |  |  | 43714.6875 | 119 | 119
2019-09-06 17:00 | 93 | 84 |  |  | 43714.7083 | 122 | 122
2019-09-06 17:30 | 94 | 85 |  |  | 43714.7292 | 122 | 122
2019-09-06 18:00 | 91 | 82 |  |  | 43714.75 | 117 | 117
2019-09-06 18:30 | 88 | 79 |  |  | 43714.7708 | 113 | 113
2019-09-06 19:00 | 88 | 79 |  |  | 43714.7917 | 112 | 112
2019-09-06 19:30 | 80 | 74 |  |  | 43714.8125 | 107 | 107
2019-09-06 20:00 | 78 | 73 |  |  | 43714.8333 | 104 | 104
2019-09-06 20:30 | 76 | 70 |  |  | 43714.8542 | 102 | 102
2019-09-06 21:00 | 72 | 66 |  |  | 43714.875 | 96 | 96
2019-09-06 21:30 | 69 | 62 |  |  | 43714.8958 | 91 | 91
2019-09-06 22:00 | 67 | 60 |  |  | 43714.9167 | 90 | 90
2019-09-06 22:30 | 65 | 58 |  |  | 43714.9375 | 86 | 86
2019-09-06 23:00 | 63 | 57 |  |  | 43714.9583 | 83 | 82
2019-09-06 23:30 | 57 | 51 |  |  | 43714.9792 | 75 | 75
2019-09-07 | 51 | 45 |  |  | 43715 | 69 | 68
2019-09-07 00:30 | 52 | 44 |  |  | 43715.0208 | 65 | 65
2019-09-07 01:00 | 53 | 43 |  |  | 43715.0417 | 63 | 63
2019-09-07 01:30 | 52 | 42 |  |  | 43715.0625 | 60 | 60
2019-09-07 02:00 | 51 | 41 |  |  | 43715.0833 | 59 | 59
2019-09-07 02:30 | 50 | 40 |  |  | 43715.1042 | 59 | 59
2019-09-07 03:00 | 51 | 42 |  |  | 43715.125 | 60 | 60
2019-09-07 03:30 | 52 | 42 |  |  | 43715.1458 | 62 | 62
2019-09-07 04:00 | 52 | 42 |  |  | 43715.1667 | 62 | 61
2019-09-07 04:30 | 51 | 42 |  |  | 43715.1875 | 62 | 61
2019-09-07 05:00 | 51 | 43 |  |  | 43715.2083 | 63 | 63
2019-09-07 05:30 | 53 | 45 |  |  | 43715.2292 | 65 | 65
2019-09-07 06:00 | 53 | 45 |  |  | 43715.25 | 67 | 67
2019-09-07 06:30 | 52 | 44 |  |  | 43715.2708 | 67 | 67
2019-09-07 07:00 | 50 | 40 |  |  | 43715.2917 | 64 | 64
2019-09-07 07:30 | 48 | 36 |  |  | 43715.3125 | 61 | 61
2019-09-07 08:00 | 47 | 34 |  |  | 43715.3333 | 59 | 59
2019-09-07 08:30 | 47 | 33 |  |  | 43715.3542 | 58 | 58
2019-09-07 09:00 | 47 | 32 |  |  | 43715.375 | 56 | 56
2019-09-07 09:30 | 47 | 32 |  |  | 43715.3958 | 56 | 56
2019-09-07 10:00 | 46 | 31 |  |  | 43715.4167 | 54 | 54
2019-09-07 10:30 | 47 | 31 |  |  | 43715.4375 | 53 | 53
2019-09-07 11:00 | 46 | 32 |  |  | 43715.4583 | 53 | 53
2019-09-07 11:30 | 45 | 29 |  |  | 43715.4792 | 50 | 49
2019-09-07 12:00 | 45 | 29 |  |  | 43715.5 | 49 | 48
2019-09-07 12:30 | 44 | 28 |  |  | 43715.5208 | 50 | 49
2019-09-07 13:00 | 44 | 28 |  |  | 43715.5417 | 50 | 49
2019-09-07 13:30 | 46 | 30 |  |  | 43715.5625 | 53 | 52
2019-09-07 14:00 | 46 | 31 |  |  | 43715.5833 | 54 | 53
2019-09-07 14:30 | 49 | 35 |  |  | 43715.6042 | 58 | 57
2019-09-07 15:00 | 51 | 37 |  |  | 43715.625 | 60 | 60
2019-09-07 15:30 | 55 | 41 |  |  | 43715.6458 | 66 | 66
2019-09-07 16:00 | 57 | 45 |  |  | 43715.6667 | 71 | 71
2019-09-07 16:30 | 60 | 48 |  |  | 43715.6875 | 75 | 75
2019-09-07 17:00 | 65 | 54 |  |  | 43715.7083 | 83 | 83
2019-09-07 17:30 | 66 | 56 |  |  | 43715.7292 | 86 | 86
2019-09-07 18:00 | 67 | 57 |  |  | 43715.75 | 88 | 88
2019-09-07 18:30 | 68 | 60 |  |  | 43715.7708 | 92 | 91
2019-09-07 19:00 | 68 | 61 |  |  | 43715.7917 | 93 | 93
2019-09-07 19:30 | 67 | 59 |  |  | 43715.8125 | 90 | 90
2019-09-07 20:00 | 65 | 58 |  |  | 43715.8333 | 89 | 89
2019-09-07 20:30 | 63 | 57 |  |  | 43715.8542 | 88 | 88
2019-09-07 21:00 | 61 | 54 |  |  | 43715.875 | 84 | 84
2019-09-07 21:30 | 58 | 51 |  |  | 43715.8958 | 80 | 79
2019-09-07 22:00 | 56 | 50 |  |  | 43715.9167 | 80 | 79
2019-09-07 22:30 | 55 | 49 |  |  | 43715.9375 | 79 | 78
2019-09-07 23:00 | 55 | 48 |  |  | 43715.9583 | 77 | 76
2019-09-07 23:30 | 52 | 45 |  |  | 43715.9792 | 73 | 72
2019-09-08 | 49 | 43 |  |  | 43716 | 69 | 68
2019-09-08 00:30 | 46 | 38 |  |  | 43716.0208 | 63 | 62
2019-09-08 01:00 | 49 | 39 |  |  | 43716.0417 | 63 | 61
2019-09-08 01:30 | 53 | 38 |  |  | 43716.0625 | 63 | 59
2019-09-08 02:00 | 54 | 38 |  |  | 43716.0833 | 61 | 58
2019-09-08 02:30 | 56 | 39 |  |  | 43716.1042 | 60 | 58
2019-09-08 03:00 | 56 | 39 |  |  | 43716.125 | 60 | 57
2019-09-08 03:30 | 57 | 39 |  |  | 43716.1458 | 60 | 58
2019-09-08 04:00 | 56 | 39 |  |  | 43716.1667 | 59 | 57
2019-09-08 04:30 | 56 | 39 |  |  | 43716.1875 | 59 | 57
2019-09-08 05:00 | 56 | 38 |  |  | 43716.2083 | 59 | 57
2019-09-08 05:30 | 56 | 39 |  |  | 43716.2292 | 59 | 57
2019-09-08 06:00 | 56 | 39 |  |  | 43716.25 | 61 | 58
2019-09-08 06:30 | 54 | 36 |  |  | 43716.2708 | 60 | 57
2019-09-08 07:00 | 52 | 32 |  |  | 43716.2917 | 56 | 54
2019-09-08 07:30 | 49 | 27 |  |  | 43716.3125 | 52 | 49
2019-09-08 08:00 | 49 | 27 |  |  | 43716.3333 | 51 | 49
2019-09-08 08:30 | 51 | 28 |  |  | 43716.3542 | 52 | 50
2019-09-08 09:00 | 52 | 30 |  |  | 43716.375 | 52 | 51
2019-09-08 09:30 | 50 | 27 |  |  | 43716.3958 | 49 | 48
2019-09-08 10:00 | 50 | 27 |  |  | 43716.4167 | 48 | 46
2019-09-08 10:30 | 50 | 25 |  |  | 43716.4375 | 45 | 44
2019-09-08 11:00 | 49 | 25 |  |  | 43716.4583 | 43 | 42
2019-09-08 11:30 | 52 | 27 |  |  | 43716.4792 | 46 | 45
2019-09-08 12:00 | 52 | 27 |  |  | 43716.5 | 46 | 45
2019-09-08 12:30 | 51 | 28 |  |  | 43716.5208 | 48 | 47
2019-09-08 13:00 | 52 | 29 |  |  | 43716.5417 | 50 | 49
2019-09-08 13:30 | 53 | 31 |  |  | 43716.5625 | 52 | 51
2019-09-08 14:00 | 53 | 32 |  |  | 43716.5833 | 54 | 53
2019-09-08 14:30 | 55 | 35 |  |  | 43716.6042 | 57 | 56
2019-09-08 15:00 | 56 | 36 |  |  | 43716.625 | 58 | 57
2019-09-08 15:30 | 57 | 38 |  |  | 43716.6458 | 62 | 61
2019-09-08 16:00 | 62 | 43 |  |  | 43716.6667 | 67 | 66
2019-09-08 16:30 | 65 | 48 |  |  | 43716.6875 | 74 | 73
2019-09-08 17:00 | 64 | 53 |  |  | 43716.7083 | 82 | 82
2019-09-08 17:30 | 58 | 57 |  |  | 43716.7292 | 87 | 87
2019-09-08 18:00 | 59 | 59 |  |  | 43716.75 | 90 | 90
2019-09-08 18:30 | 64 | 64 |  |  | 43716.7708 | 95 | 95
2019-09-08 19:00 | 65 | 65 |  |  | 43716.7917 | 97 | 97
2019-09-08 19:30 | 62 | 62 |  |  | 43716.8125 | 94 | 94
2019-09-08 20:00 | 62 | 61 |  |  | 43716.8333 | 92 | 92
2019-09-08 20:30 | 62 | 62 |  |  | 43716.8542 | 94 | 94
2019-09-08 21:00 | 59 | 58 |  |  | 43716.875 | 89 | 89
2019-09-08 21:30 | 58 | 58 |  |  | 43716.8958 | 88 | 88
2019-09-08 22:00 | 57 | 57 |  |  | 43716.9167 | 89 | 89
2019-09-08 22:30 | 58 | 58 |  |  | 43716.9375 | 89 | 89
2019-09-08 23:00 | 57 | 57 |  |  | 43716.9583 | 86 | 86
2019-09-08 23:30 | 52 | 52 |  |  | 43716.9792 | 79 | 79
2019-09-09 | 46 | 46 |  |  | 43717 | 72 | 72
2019-09-09 00:30 | 46 | 45 |  |  | 43717.0208 | 70 | 69
2019-09-09 01:00 | 42 | 42 |  |  | 43717.0417 | 65 | 65
2019-09-09 01:30 | 40 | 40 |  |  | 43717.0625 | 62 | 62
2019-09-09 02:00 | 41 | 41 |  |  | 43717.0833 | 62 | 62
2019-09-09 02:30 | 41 | 41 |  |  | 43717.1042 | 62 | 62
2019-09-09 03:00 | 41 | 41 |  |  | 43717.125 | 62 | 62
2019-09-09 03:30 | 43 | 43 |  |  | 43717.1458 | 65 | 64
2019-09-09 04:00 | 44 | 44 |  |  | 43717.1667 | 65 | 65
2019-09-09 04:30 | 45 | 45 |  |  | 43717.1875 | 67 | 67
2019-09-09 05:00 | 46 | 46 |  |  | 43717.2083 | 67 | 66
2019-09-09 05:30 | 51 | 51 |  |  | 43717.2292 | 73 | 73
2019-09-09 06:00 | 54 | 54 |  |  | 43717.25 | 77 | 77
2019-09-09 06:30 | 56 | 56 |  |  | 43717.2708 | 82 | 82
2019-09-09 07:00 | 60 | 60 |  |  | 43717.2917 | 90 | 90
2019-09-09 07:30 | 63 | 62 |  |  | 43717.3125 | 96 | 96
2019-09-09 08:00 | 58 | 57 |  |  | 43717.3333 | 91 | 91
2019-09-09 08:30 | 53 | 53 |  |  | 43717.3542 | 87 | 86
2019-09-09 09:00 | 50 | 49 |  |  | 43717.375 | 82 | 82
2019-09-09 09:30 | 48 | 46 |  |  | 43717.3958 | 78 | 78
2019-09-09 10:00 | 46 | 44 |  |  | 43717.4167 | 76 | 75
2019-09-09 10:30 | 45 | 44 |  |  | 43717.4375 | 74 | 73
2019-09-09 11:00 | 45 | 43 |  |  | 43717.4583 | 73 | 72
2019-09-09 11:30 | 45 | 43 |  |  | 43717.4792 | 72 | 71
2019-09-09 12:00 | 45 | 43 |  |  | 43717.5 | 72 | 71
2019-09-09 12:30 | 44 | 42 |  |  | 43717.5208 | 71 | 70
2019-09-09 13:00 | 44 | 42 |  |  | 43717.5417 | 71 | 70
2019-09-09 13:30 | 46 | 44 |  |  | 43717.5625 | 73 | 72
2019-09-09 14:00 | 47 | 45 |  |  | 43717.5833 | 74 | 73
2019-09-09 14:30 | 49 | 46 |  |  | 43717.6042 | 75 | 74
2019-09-09 15:00 | 48 | 47 |  |  | 43717.625 | 76 | 75
2019-09-09 15:30 | 51 | 50 |  |  | 43717.6458 | 78 | 78
2019-09-09 16:00 | 58 | 57 |  |  | 43717.6667 | 87 | 87
2019-09-09 16:30 | 62 | 62 |  |  | 43717.6875 | 93 | 93
2019-09-09 17:00 | 69 | 68 |  |  | 43717.7083 | 101 | 101
2019-09-09 17:30 | 74 | 74 |  |  | 43717.7292 | 107 | 107
2019-09-09 18:00 | 76 | 76 |  |  | 43717.75 | 110 | 110
2019-09-09 18:30 | 78 | 78 |  |  | 43717.7708 | 112 | 112
2019-09-09 19:00 | 80 | 80 |  |  | 43717.7917 | 115 | 114
2019-09-09 19:30 | 77 | 77 |  |  | 43717.8125 | 110 | 110
2019-09-09 20:00 | 74 | 74 |  |  | 43717.8333 | 106 | 105
2019-09-09 20:30 | 73 | 73 |  |  | 43717.8542 | 107 | 107
2019-09-09 21:00 | 69 | 69 |  |  | 43717.875 | 102 | 101
2019-09-09 21:30 | 64 | 64 |  |  | 43717.8958 | 95 | 95
2019-09-09 22:00 | 60 | 59 |  |  | 43717.9167 | 91 | 90
2019-09-09 22:30 | 58 | 58 |  |  | 43717.9375 | 88 | 88
2019-09-09 23:00 | 55 | 55 |  |  | 43717.9583 | 83 | 83
2019-09-09 23:30 | 51 | 51 |  |  | 43717.9792 | 79 | 79
2019-09-10 | 48 | 48 |  |  | 43718 | 76 | 75
2019-09-10 00:30 | 43 | 43 |  |  | 43718.0208 | 69 | 68
2019-09-10 01:00 | 41 | 41 |  |  | 43718.0417 | 66 | 64
2019-09-10 01:30 | 38 | 38 |  |  | 43718.0625 | 62 | 61
2019-09-10 02:00 | 38 | 37 |  |  | 43718.0833 | 61 | 59
2019-09-10 02:30 | 38 | 37 |  |  | 43718.1042 | 60 | 58
2019-09-10 03:00 | 37 | 37 |  |  | 43718.125 | 60 | 58
2019-09-10 03:30 | 36 | 36 |  |  | 43718.1458 | 59 | 57
2019-09-10 04:00 | 36 | 36 |  |  | 43718.1667 | 59 | 57
2019-09-10 04:30 | 39 | 38 |  |  | 43718.1875 | 61 | 59
2019-09-10 05:00 | 41 | 40 |  |  | 43718.2083 | 64 | 62
2019-09-10 05:30 | 45 | 45 |  |  | 43718.2292 | 69 | 68
2019-09-10 06:00 | 49 | 49 |  |  | 43718.25 | 74 | 74
2019-09-10 06:30 | 56 | 56 |  |  | 43718.2708 | 85 | 85
2019-09-10 07:00 | 64 | 64 |  |  | 43718.2917 | 96 | 96
2019-09-10 07:30 | 65 | 65 |  |  | 43718.3125 | 102 | 102
2019-09-10 08:00 | 62 | 62 |  |  | 43718.3333 | 99 | 99
2019-09-10 08:30 | 58 | 57 |  |  | 43718.3542 | 93 | 93
2019-09-10 09:00 | 52 | 52 |  |  | 43718.375 | 86 | 86
2019-09-10 09:30 | 49 | 49 |  |  | 43718.3958 | 81 | 81
2019-09-10 10:00 | 48 | 47 |  |  | 43718.4167 | 79 | 78
2019-09-10 10:30 | 47 | 45 |  |  | 43718.4375 | 77 | 76
2019-09-10 11:00 | 47 | 46 |  |  | 43718.4583 | 77 | 76
2019-09-10 11:30 | 46 | 44 |  |  | 43718.4792 | 75 | 74
2019-09-10 12:00 | 47 | 45 |  |  | 43718.5 | 76 | 76
2019-09-10 12:30 | 47 | 45 |  |  | 43718.5208 | 75 | 75
2019-09-10 13:00 | 48 | 47 |  |  | 43718.5417 | 77 | 77
2019-09-10 13:30 | 51 | 50 |  |  | 43718.5625 | 82 | 81
2019-09-10 14:00 | 53 | 51 |  |  | 43718.5833 | 85 | 85
2019-09-10 14:30 | 51 | 50 |  |  | 43718.6042 | 82 | 82
2019-09-10 15:00 | 53 | 53 |  |  | 43718.625 | 81 | 81
2019-09-10 15:30 | 57 | 56 |  |  | 43718.6458 | 85 | 85
2019-09-10 16:00 | 61 | 61 |  |  | 43718.6667 | 93 | 93
2019-09-10 16:30 | 65 | 65 |  |  | 43718.6875 | 98 | 98
2019-09-10 17:00 | 69 | 69 |  |  | 43718.7083 | 103 | 103
2019-09-10 17:30 | 72 | 72 |  |  | 43718.7292 | 107 | 107
2019-09-10 18:00 | 74 | 74 |  |  | 43718.75 | 110 | 110
2019-09-10 18:30 | 75 | 75 |  |  | 43718.7708 | 110 | 110
2019-09-10 19:00 | 76 | 76 |  |  | 43718.7917 | 112 | 112
2019-09-10 19:30 | 74 | 74 |  |  | 43718.8125 | 108 | 108
2019-09-10 20:00 | 72 | 71 |  |  | 43718.8333 | 106 | 106
2019-09-10 20:30 | 71 | 71 |  |  | 43718.8542 | 105 | 105
2019-09-10 21:00 | 71 | 71 |  |  | 43718.875 | 104 | 104
2019-09-10 21:30 | 70 | 70 |  |  | 43718.8958 | 101 | 101
2019-09-10 22:00 | 67 | 67 |  |  | 43718.9167 | 100 | 100
2019-09-10 22:30 | 63 | 63 |  |  | 43718.9375 | 96 | 96
2019-09-10 23:00 | 59 | 59 |  |  | 43718.9583 | 89 | 89
2019-09-10 23:30 | 55 | 55 |  |  | 43718.9792 | 84 | 84
2019-09-11 | 50 | 50 |  |  | 43719 | 78 | 78
2019-09-11 00:30 | 45 | 45 |  |  | 43719.0208 | 70 | 70
2019-09-11 01:00 | 43 | 43 |  |  | 43719.0417 | 67 | 67
2019-09-11 01:30 | 41 | 41 |  |  | 43719.0625 | 65 | 65
2019-09-11 02:00 | 39 | 39 |  |  | 43719.0833 | 62 | 62
2019-09-11 02:30 | 39 | 39 |  |  | 43719.1042 | 62 | 61
2019-09-11 03:00 | 38 | 38 |  |  | 43719.125 | 61 | 60
2019-09-11 03:30 | 39 | 39 |  |  | 43719.1458 | 61 | 61
2019-09-11 04:00 | 39 | 39 |  |  | 43719.1667 | 62 | 61
2019-09-11 04:30 | 41 | 41 |  |  | 43719.1875 | 63 | 63
2019-09-11 05:00 | 44 | 44 |  |  | 43719.2083 | 67 | 66
2019-09-11 05:30 | 49 | 49 |  |  | 43719.2292 | 71 | 71
2019-09-11 06:00 | 54 | 54 |  |  | 43719.25 | 78 | 78
2019-09-11 06:30 | 59 | 59 |  |  | 43719.2708 | 89 | 89
2019-09-11 07:00 | 64 | 64 |  |  | 43719.2917 | 98 | 98
2019-09-11 07:30 | 66 | 66 |  |  | 43719.3125 | 104 | 103
2019-09-11 08:00 | 64 | 64 |  |  | 43719.3333 | 102 | 101
2019-09-11 08:30 | 61 | 61 |  |  | 43719.3542 | 98 | 97
2019-09-11 09:00 | 57 | 56 |  |  | 43719.375 | 91 | 91
2019-09-11 09:30 | 55 | 54 |  |  | 43719.3958 | 87 | 87
2019-09-11 10:00 | 55 | 54 |  |  | 43719.4167 | 86 | 86
2019-09-11 10:30 | 63 | 62 |  |  | 43719.4375 | 93 | 93
2019-09-11 11:00 | 66 | 65 |  |  | 43719.4583 | 95 | 95
2019-09-11 11:30 | 63 | 62 |  |  | 43719.4792 | 94 | 94
2019-09-11 12:00 | 61 | 60 |  |  | 43719.5 | 99 | 98
2019-09-11 12:30 | 62 | 61 |  |  | 43719.5208 | 97 | 97
2019-09-11 13:00 | 58 | 58 |  |  | 43719.5417 | 87 | 87
2019-09-11 13:30 | 52 | 52 |  |  | 43719.5625 | 82 | 82
2019-09-11 14:00 | 52 | 52 |  |  | 43719.5833 | 81 | 81
2019-09-11 14:30 | 57 | 56 |  |  | 43719.6042 | 82 | 82
2019-09-11 15:00 | 60 | 60 |  |  | 43719.625 | 87 | 87
2019-09-11 15:30 | 62 | 61 |  |  | 43719.6458 | 93 | 93
2019-09-11 16:00 | 64 | 63 |  |  | 43719.6667 | 97 | 97
2019-09-11 16:30 | 66 | 64 |  |  | 43719.6875 | 98 | 98
2019-09-11 17:00 | 70 | 70 |  |  | 43719.7083 | 105 | 104
2019-09-11 17:30 | 75 | 75 |  |  | 43719.7292 | 108 | 108
2019-09-11 18:00 | 78 | 78 |  |  | 43719.75 | 112 | 111
2019-09-11 18:30 | 80 | 80 |  |  | 43719.7708 | 114 | 113
2019-09-11 19:00 | 81 | 80 |  |  | 43719.7917 | 115 | 114
2019-09-11 19:30 | 77 | 77 |  |  | 43719.8125 | 112 | 111
2019-09-11 20:00 | 77 | 76 |  |  | 43719.8333 | 110 | 109
2019-09-11 20:30 | 75 | 75 |  |  | 43719.8542 | 108 | 107
2019-09-11 21:00 | 70 | 70 |  |  | 43719.875 | 101 | 101
2019-09-11 21:30 | 67 | 66 |  |  | 43719.8958 | 97 | 97
2019-09-11 22:00 | 65 | 65 |  |  | 43719.9167 | 96 | 95
2019-09-11 22:30 | 61 | 61 |  |  | 43719.9375 | 92 | 91
2019-09-11 23:00 | 59 | 59 |  |  | 43719.9583 | 88 | 88
2019-09-11 23:30 | 55 | 54 |  |  | 43719.9792 | 83 | 82
2019-09-12 | 47 | 46 |  |  | 43720 | 73 | 72
2019-09-12 00:30 | 42 | 42 |  |  | 43720.0208 | 67 | 66
2019-09-12 01:00 | 40 | 40 |  |  | 43720.0417 | 65 | 63
2019-09-12 01:30 | 38 | 38 |  |  | 43720.0625 | 62 | 60
2019-09-12 02:00 | 38 | 37 |  |  | 43720.0833 | 61 | 59
2019-09-12 02:30 | 38 | 37 |  |  | 43720.1042 | 61 | 59
2019-09-12 03:00 | 39 | 38 |  |  | 43720.125 | 63 | 60
2019-09-12 03:30 | 40 | 40 |  |  | 43720.1458 | 63 | 61
2019-09-12 04:00 | 42 | 42 |  |  | 43720.1667 | 65 | 62
2019-09-12 04:30 | 44 | 44 |  |  | 43720.1875 | 68 | 65
2019-09-12 05:00 | 48 | 47 |  |  | 43720.2083 | 72 | 69
2019-09-12 05:30 | 53 | 53 |  |  | 43720.2292 | 78 | 75
2019-09-12 06:00 | 58 | 58 |  |  | 43720.25 | 84 | 81
2019-09-12 06:30 | 61 | 61 |  |  | 43720.2708 | 93 | 89
2019-09-12 07:00 | 67 | 67 |  |  | 43720.2917 | 102 | 98
2019-09-12 07:30 | 68 | 68 |  |  | 43720.3125 | 108 | 103
2019-09-12 08:00 | 63 | 63 |  |  | 43720.3333 | 105 | 99
2019-09-12 08:30 | 58 | 57 |  |  | 43720.3542 | 99 | 92
2019-09-12 09:00 | 51 | 51 |  |  | 43720.375 | 93 | 84
2019-09-12 09:30 | 50 | 49 |  |  | 43720.3958 | 90 | 81
2019-09-12 10:00 | 49 | 48 |  |  | 43720.4167 | 89 | 79
2019-09-12 10:30 | 49 | 48 |  |  | 43720.4375 | 86 | 77
2019-09-12 11:00 | 48 | 47 |  |  | 43720.4583 | 86 | 78
2019-09-12 11:30 | 47 | 46 |  |  | 43720.4792 | 84 | 75
2019-09-12 12:00 | 46 | 45 |  |  | 43720.5 | 84 | 75
2019-09-12 12:30 | 45 | 44 |  |  | 43720.5208 | 83 | 73
2019-09-12 13:00 | 47 | 46 |  |  | 43720.5417 | 84 | 75
2019-09-12 13:30 | 48 | 47 |  |  | 43720.5625 | 86 | 78
2019-09-12 14:00 | 48 | 48 |  |  | 43720.5833 | 87 | 79
2019-09-12 14:30 | 51 | 50 |  |  | 43720.6042 | 89 | 81
2019-09-12 15:00 | 53 | 53 |  |  | 43720.625 | 90 | 84
2019-09-12 15:30 | 57 | 57 |  |  | 43720.6458 | 94 | 88
2019-09-12 16:00 | 62 | 62 |  |  | 43720.6667 | 99 | 94
2019-09-12 16:30 | 65 | 65 |  |  | 43720.6875 | 103 | 99
2019-09-12 17:00 | 69 | 69 |  |  | 43720.7083 | 105 | 103
2019-09-12 17:30 | 71 | 71 |  |  | 43720.7292 | 107 | 105
2019-09-12 18:00 | 74 | 74 |  |  | 43720.75 | 110 | 108
2019-09-12 18:30 | 77 | 77 |  |  | 43720.7708 | 112 | 111
2019-09-12 19:00 | 79 | 79 |  |  | 43720.7917 | 115 | 113
2019-09-12 19:30 | 76 | 75 |  |  | 43720.8125 | 110 | 109
2019-09-12 20:00 | 75 | 75 |  |  | 43720.8333 | 110 | 108
2019-09-12 20:30 | 76 | 75 |  |  | 43720.8542 | 110 | 108
2019-09-12 21:00 | 72 | 71 |  |  | 43720.875 | 106 | 104
2019-09-12 21:30 | 68 | 67 |  |  | 43720.8958 | 100 | 98
2019-09-12 22:00 | 64 | 64 |  |  | 43720.9167 | 96 | 95
2019-09-12 22:30 | 61 | 61 |  |  | 43720.9375 | 93 | 91
2019-09-12 23:00 | 59 | 58 |  |  | 43720.9583 | 89 | 88
2019-09-12 23:30 | 54 | 53 |  |  | 43720.9792 | 83 | 82
2019-09-13 | 48 | 47 |  |  | 43721 | 76 | 75
2019-09-13 00:30 | 43 | 42 |  |  | 43721.0208 | 68 | 67
2019-09-13 01:00 | 41 | 39 |  |  | 43721.0417 | 63 | 63
2019-09-13 01:30 | 39 | 37 |  |  | 43721.0625 | 60 | 60
2019-09-13 02:00 | 39 | 37 |  |  | 43721.0833 | 59 | 59
2019-09-13 02:30 | 38 | 37 |  |  | 43721.1042 | 59 | 58
2019-09-13 03:00 | 38 | 37 |  |  | 43721.125 | 59 | 58
2019-09-13 03:30 | 38 | 37 |  |  | 43721.1458 | 59 | 58
2019-09-13 04:00 | 38 | 37 |  |  | 43721.1667 | 59 | 58
2019-09-13 04:30 | 38 | 37 |  |  | 43721.1875 | 59 | 58
2019-09-13 05:00 | 39 | 38 |  |  | 43721.2083 | 62 | 60
2019-09-13 05:30 | 44 | 43 |  |  | 43721.2292 | 67 | 65
2019-09-13 06:00 | 49 | 49 |  |  | 43721.25 | 76 | 74
2019-09-13 06:30 | 57 | 57 |  |  | 43721.2708 | 89 | 86
2019-09-13 07:00 | 62 | 62 |  |  | 43721.2917 | 99 | 95
2019-09-13 07:30 | 64 | 64 |  |  | 43721.3125 | 104 | 100
2019-09-13 08:00 | 61 | 61 |  |  | 43721.3333 | 100 | 97
2019-09-13 08:30 | 57 | 57 |  |  | 43721.3542 | 95 | 92
2019-09-13 09:00 | 52 | 52 |  |  | 43721.375 | 89 | 85
2019-09-13 09:30 | 48 | 48 |  |  | 43721.3958 | 85 | 80
2019-09-13 10:00 | 47 | 46 |  |  | 43721.4167 | 84 | 78
2019-09-13 10:30 | 45 | 45 |  |  | 43721.4375 | 83 | 77
2019-09-13 11:00 | 46 | 45 |  |  | 43721.4583 | 83 | 77
2019-09-13 11:30 | 46 | 45 |  |  | 43721.4792 | 82 | 75
2019-09-13 12:00 | 45 | 44 |  |  | 43721.5 | 81 | 74
2019-09-13 12:30 | 46 | 46 |  |  | 43721.5208 | 84 | 77
2019-09-13 13:00 | 47 | 46 |  |  | 43721.5417 | 84 | 77
2019-09-13 13:30 | 48 | 48 |  |  | 43721.5625 | 86 | 79
2019-09-13 14:00 | 49 | 49 |  |  | 43721.5833 | 85 | 80
2019-09-13 14:30 | 52 | 52 |  |  | 43721.6042 | 87 | 83
2019-09-13 15:00 | 55 | 54 |  |  | 43721.625 | 89 | 85
2019-09-13 15:30 | 56 | 55 |  |  | 43721.6458 | 91 | 87
2019-09-13 16:00 | 60 | 60 |  |  | 43721.6667 | 96 | 93
2019-09-13 16:30 | 63 | 63 |  |  | 43721.6875 | 99 | 97
2019-09-13 17:00 | 67 | 67 |  |  | 43721.7083 | 105 | 103
2019-09-13 17:30 | 69 | 69 |  |  | 43721.7292 | 107 | 105
2019-09-13 18:00 | 69 | 69 |  |  | 43721.75 | 108 | 105
2019-09-13 18:30 | 70 | 70 |  |  | 43721.7708 | 107 | 105
2019-09-13 19:00 | 70 | 70 |  |  | 43721.7917 | 106 | 104
2019-09-13 19:30 | 68 | 68 |  |  | 43721.8125 | 104 | 102
2019-09-13 20:00 | 67 | 67 |  |  | 43721.8333 | 101 | 100
2019-09-13 20:30 | 67 | 67 |  |  | 43721.8542 | 100 | 99
2019-09-13 21:00 | 64 | 64 |  |  | 43721.875 | 96 | 95
2019-09-13 21:30 | 59 | 59 |  |  | 43721.8958 | 90 | 89
2019-09-13 22:00 | 58 | 58 |  |  | 43721.9167 | 89 | 89
2019-09-13 22:30 | 56 | 55 |  |  | 43721.9375 | 86 | 86
2019-09-13 23:00 | 53 | 52 |  |  | 43721.9583 | 82 | 81
2019-09-13 23:30 | 50 | 49 |  |  | 43721.9792 | 77 | 77
2019-09-14 | 47 | 46 |  |  | 43722 | 72 | 72
2019-09-14 00:30 | 42 | 41 |  |  | 43722.0208 | 66 | 65
2019-09-14 01:00 | 38 | 37 |  |  | 43722.0417 | 61 | 60
2019-09-14 01:30 | 37 | 36 |  |  | 43722.0625 | 58 | 57
2019-09-14 02:00 | 35 | 33 |  |  | 43722.0833 | 55 | 55
2019-09-14 02:30 | 33 | 31 |  |  | 43722.1042 | 53 | 53
2019-09-14 03:00 | 32 | 30 |  |  | 43722.125 | 52 | 51
2019-09-14 03:30 | 32 | 31 |  |  | 43722.1458 | 54 | 52
2019-09-14 04:00 | 32 | 31 |  |  | 43722.1667 | 53 | 52
2019-09-14 04:30 | 33 | 32 |  |  | 43722.1875 | 55 | 53
2019-09-14 05:00 | 33 | 33 |  |  | 43722.2083 | 55 | 53
2019-09-14 05:30 | 35 | 35 |  |  | 43722.2292 | 57 | 56
2019-09-14 06:00 | 36 | 35 |  |  | 43722.25 | 59 | 57
2019-09-14 06:30 | 35 | 34 |  |  | 43722.2708 | 59 | 58
2019-09-14 07:00 | 36 | 35 |  |  | 43722.2917 | 60 | 58
2019-09-14 07:30 | 35 | 35 |  |  | 43722.3125 | 60 | 58
2019-09-14 08:00 | 35 | 35 |  |  | 43722.3333 | 61 | 58
2019-09-14 08:30 | 35 | 35 |  |  | 43722.3542 | 61 | 58
2019-09-14 09:00 | 34 | 34 |  |  | 43722.375 | 60 | 57
2019-09-14 09:30 | 32 | 32 |  |  | 43722.3958 | 60 | 56
2019-09-14 10:00 | 32 | 32 |  |  | 43722.4167 | 60 | 55
2019-09-14 10:30 | 32 | 32 |  |  | 43722.4375 | 59 | 55
2019-09-14 11:00 | 32 | 32 |  |  | 43722.4583 | 60 | 55
2019-09-14 11:30 | 31 | 31 |  |  | 43722.4792 | 59 | 54
2019-09-14 12:00 | 31 | 31 |  |  | 43722.5 | 59 | 54
2019-09-14 12:30 | 31 | 31 |  |  | 43722.5208 | 58 | 53
2019-09-14 13:00 | 32 | 32 |  |  | 43722.5417 | 58 | 53
2019-09-14 13:30 | 34 | 33 |  |  | 43722.5625 | 62 | 57
2019-09-14 14:00 | 35 | 35 |  |  | 43722.5833 | 63 | 58
2019-09-14 14:30 | 37 | 37 |  |  | 43722.6042 | 64 | 60
2019-09-14 15:00 | 39 | 39 |  |  | 43722.625 | 67 | 62
2019-09-14 15:30 | 42 | 42 |  |  | 43722.6458 | 71 | 67
2019-09-14 16:00 | 46 | 46 |  |  | 43722.6667 | 76 | 72
2019-09-14 16:30 | 49 | 49 |  |  | 43722.6875 | 81 | 77
2019-09-14 17:00 | 55 | 54 |  |  | 43722.7083 | 87 | 84
2019-09-14 17:30 | 58 | 58 |  |  | 43722.7292 | 90 | 87
2019-09-14 18:00 | 59 | 59 |  |  | 43722.75 | 92 | 90
2019-09-14 18:30 | 62 | 62 |  |  | 43722.7708 | 94 | 93
2019-09-14 19:00 | 64 | 64 |  |  | 43722.7917 | 96 | 95
2019-09-14 19:30 | 60 | 60 |  |  | 43722.8125 | 93 | 91
2019-09-14 20:00 | 58 | 58 |  |  | 43722.8333 | 90 | 89
2019-09-14 20:30 | 57 | 57 |  |  | 43722.8542 | 89 | 88
2019-09-14 21:00 | 52 | 52 |  |  | 43722.875 | 82 | 81
2019-09-14 21:30 | 51 | 51 |  |  | 43722.8958 | 80 | 78
2019-09-14 22:00 | 50 | 49 |  |  | 43722.9167 | 79 | 78
2019-09-14 22:30 | 49 | 49 |  |  | 43722.9375 | 79 | 77
2019-09-14 23:00 | 48 | 47 |  |  | 43722.9583 | 75 | 74
2019-09-14 23:30 | 45 | 45 |  |  | 43722.9792 | 72 | 71
2019-09-15 | 42 | 41 |  |  | 43723 | 69 | 67
2019-09-15 00:30 | 39 | 39 |  |  | 43723.0208 | 64 | 62
2019-09-15 01:00 | 35 | 35 |  |  | 43723.0417 | 59 | 57
2019-09-15 01:30 | 34 | 34 |  |  | 43723.0625 | 57 | 55
2019-09-15 02:00 | 33 | 32 |  |  | 43723.0833 | 54 | 52
2019-09-15 02:30 | 32 | 32 |  |  | 43723.1042 | 54 | 52
2019-09-15 03:00 | 31 | 31 |  |  | 43723.125 | 53 | 51
2019-09-15 03:30 | 34 | 33 |  |  | 43723.1458 | 57 | 54
2019-09-15 04:00 | 33 | 33 |  |  | 43723.1667 | 56 | 53
2019-09-15 04:30 | 34 | 34 |  |  | 43723.1875 | 57 | 53
2019-09-15 05:00 | 35 | 35 |  |  | 43723.2083 | 58 | 55
2019-09-15 05:30 | 36 | 36 |  |  | 43723.2292 | 59 | 56
2019-09-15 06:00 | 34 | 33 |  |  | 43723.25 | 58 | 55
2019-09-15 06:30 | 34 | 32 |  |  | 43723.2708 | 56 | 54
2019-09-15 07:00 | 37 | 30 |  |  | 43723.2917 | 54 | 53
2019-09-15 07:30 | 36 | 29 |  |  | 43723.3125 | 54 | 53
2019-09-15 08:00 | 35 | 29 |  |  | 43723.3333 | 53 | 51
2019-09-15 08:30 | 35 | 29 |  |  | 43723.3542 | 54 | 52
2019-09-15 09:00 | 35 | 30 |  |  | 43723.375 | 56 | 54
2019-09-15 09:30 | 35 | 30 |  |  | 43723.3958 | 57 | 55
2019-09-15 10:00 | 33 | 28 |  |  | 43723.4167 | 55 | 52
2019-09-15 10:30 | 33 | 29 |  |  | 43723.4375 | 55 | 52
2019-09-15 11:00 | 32 | 28 |  |  | 43723.4583 | 55 | 51
2019-09-15 11:30 | 32 | 27 |  |  | 43723.4792 | 53 | 50
2019-09-15 12:00 | 32 | 26 |  |  | 43723.5 | 52 | 49
2019-09-15 12:30 | 30 | 25 |  |  | 43723.5208 | 50 | 47
2019-09-15 13:00 | 30 | 26 |  |  | 43723.5417 | 51 | 48
2019-09-15 13:30 | 32 | 28 |  |  | 43723.5625 | 54 | 51
2019-09-15 14:00 | 32 | 28 |  |  | 43723.5833 | 52 | 49
2019-09-15 14:30 | 34 | 30 |  |  | 43723.6042 | 55 | 51
2019-09-15 15:00 | 35 | 32 |  |  | 43723.625 | 57 | 54
2019-09-15 15:30 | 37 | 34 |  |  | 43723.6458 | 60 | 57
2019-09-15 16:00 | 41 | 38 |  |  | 43723.6667 | 66 | 63
2019-09-15 16:30 | 47 | 44 |  |  | 43723.6875 | 74 | 71
2019-09-15 17:00 | 54 | 51 |  |  | 43723.7083 | 82 | 80
2019-09-15 17:30 | 59 | 56 |  |  | 43723.7292 | 86 | 85
2019-09-15 18:00 | 61 | 58 |  |  | 43723.75 | 89 | 89
2019-09-15 18:30 | 66 | 63 |  |  | 43723.7708 | 96 | 95
2019-09-15 19:00 | 67 | 64 |  |  | 43723.7917 | 98 | 97
2019-09-15 19:30 | 65 | 62 |  |  | 43723.8125 | 94 | 94
2019-09-15 20:00 | 62 | 59 |  |  | 43723.8333 | 91 | 90
2019-09-15 20:30 | 61 | 58 |  |  | 43723.8542 | 90 | 89
2019-09-15 21:00 | 59 | 56 |  |  | 43723.875 | 88 | 87
2019-09-15 21:30 | 59 | 56 |  |  | 43723.8958 | 86 | 85
2019-09-15 22:00 | 60 | 57 |  |  | 43723.9167 | 87 | 87
2019-09-15 22:30 | 61 | 58 |  |  | 43723.9375 | 88 | 87
2019-09-15 23:00 | 58 | 54 |  |  | 43723.9583 | 82 | 81
2019-09-15 23:30 | 52 | 48 |  |  | 43723.9792 | 75 | 75
2019-09-16 | 48 | 43 |  |  | 43724 | 69 | 69
2019-09-16 00:30 | 47 | 41 |  |  | 43724.0208 | 64 | 64
2019-09-16 01:00 | 46 | 40 |  |  | 43724.0417 | 62 | 62
2019-09-16 01:30 | 44 | 37 |  |  | 43724.0625 | 58 | 58
2019-09-16 02:00 | 42 | 35 |  |  | 43724.0833 | 56 | 56
2019-09-16 02:30 | 43 | 36 |  |  | 43724.1042 | 57 | 57
2019-09-16 03:00 | 44 | 36 |  |  | 43724.125 | 57 | 57
2019-09-16 03:30 | 45 | 38 |  |  | 43724.1458 | 59 | 59
2019-09-16 04:00 | 47 | 41 |  |  | 43724.1667 | 60 | 60
2019-09-16 04:30 | 48 | 42 |  |  | 43724.1875 | 61 | 61
2019-09-16 05:00 | 49 | 43 |  |  | 43724.2083 | 63 | 63
2019-09-16 05:30 | 51 | 47 |  |  | 43724.2292 | 67 | 67
2019-09-16 06:00 | 53 | 50 |  |  | 43724.25 | 72 | 72
2019-09-16 06:30 | 57 | 55 |  |  | 43724.2708 | 82 | 81
2019-09-16 07:00 | 63 | 61 |  |  | 43724.2917 | 91 | 91
2019-09-16 07:30 | 63 | 62 |  |  | 43724.3125 | 96 | 95
2019-09-16 08:00 | 61 | 60 |  |  | 43724.3333 | 94 | 93
2019-09-16 08:30 | 56 | 55 |  |  | 43724.3542 | 90 | 88
2019-09-16 09:00 | 53 | 51 |  |  | 43724.375 | 85 | 83
2019-09-16 09:30 | 52 | 50 |  |  | 43724.3958 | 83 | 81
2019-09-16 10:00 | 50 | 48 |  |  | 43724.4167 | 80 | 78
2019-09-16 10:30 | 49 | 48 |  |  | 43724.4375 | 79 | 76
2019-09-16 11:00 | 48 | 46 |  |  | 43724.4583 | 79 | 76
2019-09-16 11:30 | 48 | 46 |  |  | 43724.4792 | 77 | 76
2019-09-16 12:00 | 47 | 45 |  |  | 43724.5 | 77 | 76
2019-09-16 12:30 | 48 | 46 |  |  | 43724.5208 | 79 | 77
2019-09-16 13:00 | 49 | 47 |  |  | 43724.5417 | 81 | 79
2019-09-16 13:30 | 52 | 50 |  |  | 43724.5625 | 83 | 82
2019-09-16 14:00 | 55 | 52 |  |  | 43724.5833 | 85 | 84
2019-09-16 14:30 | 58 | 55 |  |  | 43724.6042 | 87 | 87
2019-09-16 15:00 | 58 | 56 |  |  | 43724.625 | 89 | 88
2019-09-16 15:30 | 60 | 58 |  |  | 43724.6458 | 92 | 91
2019-09-16 16:00 | 63 | 61 |  |  | 43724.6667 | 97 | 96
2019-09-16 16:30 | 68 | 66 |  |  | 43724.6875 | 101 | 101
2019-09-16 17:00 | 75 | 73 |  |  | 43724.7083 | 108 | 107
2019-09-16 17:30 | 80 | 78 |  |  | 43724.7292 | 111 | 111
2019-09-16 18:00 | 81 | 79 |  |  | 43724.75 | 113 | 112
2019-09-16 18:30 | 83 | 80 |  |  | 43724.7708 | 113 | 113
2019-09-16 19:00 | 82 | 79 |  |  | 43724.7917 | 113 | 113
2019-09-16 19:30 | 79 | 76 |  |  | 43724.8125 | 107 | 107
2019-09-16 20:00 | 78 | 74 |  |  | 43724.8333 | 106 | 105
2019-09-16 20:30 | 76 | 73 |  |  | 43724.8542 | 105 | 105
2019-09-16 21:00 | 70 | 67 |  |  | 43724.875 | 97 | 97
2019-09-16 21:30 | 67 | 62 |  |  | 43724.8958 | 91 | 91
2019-09-16 22:00 | 62 | 59 |  |  | 43724.9167 | 88 | 88
2019-09-16 22:30 | 60 | 55 |  |  | 43724.9375 | 86 | 86
2019-09-16 23:00 | 59 | 53 |  |  | 43724.9583 | 82 | 82
2019-09-16 23:30 | 56 | 50 |  |  | 43724.9792 | 77 | 77
2019-09-17 | 51 | 43 |  |  | 43725 | 70 | 70
2019-09-17 00:30 | 49 | 41 |  |  | 43725.0208 | 66 | 65
2019-09-17 01:00 | 47 | 37 |  |  | 43725.0417 | 61 | 61
2019-09-17 01:30 | 43 | 35 |  |  | 43725.0625 | 58 | 57
2019-09-17 02:00 | 42 | 35 |  |  | 43725.0833 | 57 | 56
2019-09-17 02:30 | 41 | 34 |  |  | 43725.1042 | 54 | 54
2019-09-17 03:00 | 41 | 34 |  |  | 43725.125 | 55 | 54
2019-09-17 03:30 | 41 | 34 |  |  | 43725.1458 | 54 | 53
2019-09-17 04:00 | 40 | 33 |  |  | 43725.1667 | 53 | 53
2019-09-17 04:30 | 42 | 35 |  |  | 43725.1875 | 56 | 56
2019-09-17 05:00 | 48 | 42 |  |  | 43725.2083 | 63 | 63
2019-09-17 05:30 | 52 | 47 |  |  | 43725.2292 | 68 | 68
2019-09-17 06:00 | 55 | 52 |  |  | 43725.25 | 74 | 73
2019-09-17 06:30 | 59 | 57 |  |  | 43725.2708 | 83 | 83
2019-09-17 07:00 | 61 | 58 |  |  | 43725.2917 | 88 | 88
2019-09-17 07:30 | 60 | 58 |  |  | 43725.3125 | 92 | 91
2019-09-17 08:00 | 57 | 55 |  |  | 43725.3333 | 90 | 89
2019-09-17 08:30 | 54 | 53 |  |  | 43725.3542 | 87 | 85
2019-09-17 09:00 | 53 | 52 |  |  | 43725.375 | 87 | 85
2019-09-17 09:30 | 53 | 51 |  |  | 43725.3958 | 86 | 85
2019-09-17 10:00 | 52 | 50 |  |  | 43725.4167 | 83 | 82
2019-09-17 10:30 | 50 | 47 |  |  | 43725.4375 | 80 | 79
2019-09-17 11:00 | 48 | 45 |  |  | 43725.4583 | 77 | 76
2019-09-17 11:30 | 50 | 47 |  |  | 43725.4792 | 77 | 76
2019-09-17 12:00 | 49 | 47 |  |  | 43725.5 | 78 | 77
2019-09-17 12:30 | 49 | 46 |  |  | 43725.5208 | 80 | 78
2019-09-17 13:00 | 49 | 47 |  |  | 43725.5417 | 80 | 79
2019-09-17 13:30 | 48 | 46 |  |  | 43725.5625 | 78 | 77
2019-09-17 14:00 | 50 | 48 |  |  | 43725.5833 | 83 | 81
2019-09-17 14:30 | 53 | 51 |  |  | 43725.6042 | 88 | 86
2019-09-17 15:00 | 61 | 59 |  |  | 43725.625 | 97 | 96
2019-09-17 15:30 | 70 | 68 |  |  | 43725.6458 | 105 | 104
2019-09-17 16:00 | 72 | 72 |  |  | 43725.6667 | 108 | 107
2019-09-17 16:30 | 76 | 76 |  |  | 43725.6875 | 112 | 111
2019-09-17 17:00 | 82 | 82 |  |  | 43725.7083 | 118 | 117
2019-09-17 17:30 | 86 | 85 |  |  | 43725.7292 | 119 | 119
2019-09-17 18:00 | 88 | 87 |  |  | 43725.75 | 120 | 120
2019-09-17 18:30 | 85 | 84 |  |  | 43725.7708 | 117 | 117
2019-09-17 19:00 | 85 | 84 |  |  | 43725.7917 | 116 | 116
2019-09-17 19:30 | 82 | 80 |  |  | 43725.8125 | 111 | 111
2019-09-17 20:00 | 80 | 77 |  |  | 43725.8333 | 108 | 107
2019-09-17 20:30 | 79 | 74 |  |  | 43725.8542 | 105 | 105
2019-09-17 21:00 | 75 | 67 |  |  | 43725.875 | 99 | 98
2019-09-17 21:30 | 72 | 63 |  |  | 43725.8958 | 93 | 92
2019-09-17 22:00 | 70 | 60 |  |  | 43725.9167 | 91 | 90
2019-09-17 22:30 | 66 | 57 |  |  | 43725.9375 | 88 | 87
2019-09-17 23:00 | 62 | 54 |  |  | 43725.9583 | 82 | 82
2019-09-17 23:30 | 59 | 51 |  |  | 43725.9792 | 78 | 78
2019-09-18 | 55 | 46 |  |  | 43726 | 72 | 72
2019-09-18 00:30 | 53 | 42 |  |  | 43726.0208 | 65 | 65
2019-09-18 01:00 | 50 | 39 |  |  | 43726.0417 | 61 | 61
2019-09-18 01:30 | 50 | 37 |  |  | 43726.0625 | 59 | 59
2019-09-18 02:00 | 49 | 38 |  |  | 43726.0833 | 60 | 60
2019-09-18 02:30 | 48 | 38 |  |  | 43726.1042 | 60 | 60
2019-09-18 03:00 | 49 | 38 |  |  | 43726.125 | 59 | 59
2019-09-18 03:30 | 49 | 38 |  |  | 43726.1458 | 59 | 59
2019-09-18 04:00 | 47 | 35 |  |  | 43726.1667 | 57 | 57
2019-09-18 04:30 | 46 | 35 |  |  | 43726.1875 | 57 | 57
2019-09-18 05:00 | 46 | 35 |  |  | 43726.2083 | 57 | 57
2019-09-18 05:30 | 50 | 42 |  |  | 43726.2292 | 64 | 64
2019-09-18 06:00 | 57 | 50 |  |  | 43726.25 | 74 | 74
2019-09-18 06:30 | 61 | 55 |  |  | 43726.2708 | 84 | 84
2019-09-18 07:00 | 73 | 58 |  |  | 43726.2917 | 97 | 92
2019-09-18 07:30 | 72 | 58 |  |  | 43726.3125 | 102 | 96
2019-09-18 08:00 | 67 | 54 |  |  | 43726.3333 | 100 | 92
2019-09-18 08:30 | 63 | 50 |  |  | 43726.3542 | 96 | 87
2019-09-18 09:00 | 60 | 46 |  |  | 43726.375 | 91 | 82
2019-09-18 09:30 | 57 | 43 |  |  | 43726.3958 | 88 | 77
2019-09-18 10:00 | 48 | 40 |  |  | 43726.4167 | 78 | 72
2019-09-18 10:30 | 43 | 39 |  |  | 43726.4375 | 72 | 70
2019-09-18 11:00 | 42 | 38 |  |  | 43726.4583 | 71 | 69
2019-09-18 11:30 | 41 | 37 |  |  | 43726.4792 | 69 | 66
2019-09-18 12:00 | 41 | 37 |  |  | 43726.5 | 70 | 67
2019-09-18 12:30 | 41 | 36 |  |  | 43726.5208 | 70 | 67
2019-09-18 13:00 | 44 | 38 |  |  | 43726.5417 | 70 | 69
2019-09-18 13:30 | 44 | 39 |  |  | 43726.5625 | 71 | 70
2019-09-18 14:00 | 47 | 42 |  |  | 43726.5833 | 75 | 74
2019-09-18 14:30 | 51 | 47 |  |  | 43726.6042 | 81 | 79
2019-09-18 15:00 | 53 | 50 |  |  | 43726.625 | 85 | 83
2019-09-18 15:30 | 56 | 53 |  |  | 43726.6458 | 88 | 87
2019-09-18 16:00 | 62 | 58 |  |  | 43726.6667 | 93 | 93
2019-09-18 16:30 | 67 | 63 |  |  | 43726.6875 | 99 | 98
2019-09-18 17:00 | 74 | 70 |  |  | 43726.7083 | 106 | 106
2019-09-18 17:30 | 78 | 73 |  |  | 43726.7292 | 108 | 107
2019-09-18 18:00 | 80 | 74 |  |  | 43726.75 | 108 | 108
2019-09-18 18:30 | 82 | 76 |  |  | 43726.7708 | 109 | 109
2019-09-18 19:00 | 84 | 78 |  |  | 43726.7917 | 111 | 111
2019-09-18 19:30 | 81 | 75 |  |  | 43726.8125 | 107 | 107
2019-09-18 20:00 | 80 | 74 |  |  | 43726.8333 | 104 | 104
2019-09-18 20:30 | 78 | 72 |  |  | 43726.8542 | 103 | 103
2019-09-18 21:00 | 73 | 68 |  |  | 43726.875 | 97 | 97
2019-09-18 21:30 | 70 | 64 |  |  | 43726.8958 | 93 | 93
2019-09-18 22:00 | 68 | 62 |  |  | 43726.9167 | 91 | 91
2019-09-18 22:30 | 65 | 59 |  |  | 43726.9375 | 89 | 89
2019-09-18 23:00 | 63 | 56 |  |  | 43726.9583 | 84 | 84
2019-09-18 23:30 | 58 | 51 |  |  | 43726.9792 | 77 | 77
2019-09-19 | 56 | 48 |  |  | 43727 | 73 | 73
2019-09-19 00:30 | 55 | 45 |  |  | 43727.0208 | 69 | 69
2019-09-19 01:00 | 53 | 42 |  |  | 43727.0417 | 65 | 64
2019-09-19 01:30 | 52 | 40 |  |  | 43727.0625 | 61 | 61
2019-09-19 02:00 | 49 | 36 |  |  | 43727.0833 | 58 | 58
2019-09-19 02:30 | 51 | 38 |  |  | 43727.1042 | 59 | 58
2019-09-19 03:00 | 52 | 39 |  |  | 43727.125 | 60 | 60
2019-09-19 03:30 | 53 | 40 |  |  | 43727.1458 | 61 | 61
2019-09-19 04:00 | 54 | 42 |  |  | 43727.1667 | 64 | 64
2019-09-19 04:30 | 55 | 44 |  |  | 43727.1875 | 66 | 65
2019-09-19 05:00 | 57 | 45 |  |  | 43727.2083 | 67 | 67
2019-09-19 05:30 | 59 | 50 |  |  | 43727.2292 | 71 | 71
2019-09-19 06:00 | 61 | 53 |  |  | 43727.25 | 76 | 76
2019-09-19 06:30 | 69 | 56 |  |  | 43727.2708 | 84 | 83
2019-09-19 07:00 | 77 | 61 |  |  | 43727.2917 | 95 | 92
2019-09-19 07:30 | 76 | 62 |  |  | 43727.3125 | 100 | 96
2019-09-19 08:00 | 73 | 59 |  |  | 43727.3333 | 99 | 95
2019-09-19 08:30 | 67 | 53 |  |  | 43727.3542 | 94 | 88
2019-09-19 09:00 | 64 | 50 |  |  | 43727.375 | 90 | 84
2019-09-19 09:30 | 61 | 46 |  |  | 43727.3958 | 86 | 79
2019-09-19 10:00 | 60 | 43 |  |  | 43727.4167 | 82 | 75
2019-09-19 10:30 | 59 | 42 |  |  | 43727.4375 | 80 | 74
2019-09-19 11:00 | 58 | 42 |  |  | 43727.4583 | 81 | 73
2019-09-19 11:30 | 59 | 43 |  |  | 43727.4792 | 81 | 73
2019-09-19 12:00 | 58 | 43 |  |  | 43727.5 | 81 | 73
2019-09-19 12:30 | 58 | 42 |  |  | 43727.5208 | 81 | 74
2019-09-19 13:00 | 59 | 44 |  |  | 43727.5417 | 83 | 75
2019-09-19 13:30 | 60 | 45 |  |  | 43727.5625 | 83 | 75
2019-09-19 14:00 | 63 | 49 |  |  | 43727.5833 | 85 | 77
2019-09-19 14:30 | 64 | 51 |  |  | 43727.6042 | 89 | 81
2019-09-19 15:00 | 65 | 53 |  |  | 43727.625 | 93 | 86
2019-09-19 15:30 | 69 | 57 |  |  | 43727.6458 | 98 | 92
2019-09-19 16:00 | 73 | 60 |  |  | 43727.6667 | 101 | 95
2019-09-19 16:30 | 77 | 65 |  |  | 43727.6875 | 106 | 101
2019-09-19 17:00 | 83 | 72 |  |  | 43727.7083 | 112 | 108
2019-09-19 17:30 | 86 | 75 |  |  | 43727.7292 | 115 | 111
2019-09-19 18:00 | 88 | 76 |  |  | 43727.75 | 115 | 112
2019-09-19 18:30 | 90 | 77 |  |  | 43727.7708 | 114 | 112
2019-09-19 19:00 | 91 | 79 |  |  | 43727.7917 | 115 | 113
2019-09-19 19:30 | 89 | 76 |  |  | 43727.8125 | 112 | 109
2019-09-19 20:00 | 88 | 75 |  |  | 43727.8333 | 111 | 107
2019-09-19 20:30 | 86 | 74 |  |  | 43727.8542 | 110 | 106
2019-09-19 21:00 | 83 | 69 |  |  | 43727.875 | 104 | 100
2019-09-19 21:30 | 80 | 66 |  |  | 43727.8958 | 98 | 94
2019-09-19 22:00 | 77 | 64 |  |  | 43727.9167 | 98 | 94
2019-09-19 22:30 | 74 | 63 |  |  | 43727.9375 | 96 | 94
2019-09-19 23:00 | 66 | 61 |  |  | 43727.9583 | 89 | 89
2019-09-19 23:30 | 62 | 56 |  |  | 43727.9792 | 84 | 84
2019-09-20 | 57 | 49 |  |  | 43728 | 76 | 76
2019-09-20 00:30 | 55 | 47 |  |  | 43728.0208 | 70 | 70
2019-09-20 01:00 | 55 | 46 |  |  | 43728.0417 | 68 | 67
2019-09-20 01:30 | 53 | 43 |  |  | 43728.0625 | 64 | 63
2019-09-20 02:00 | 51 | 41 |  |  | 43728.0833 | 61 | 60
2019-09-20 02:30 | 52 | 40 |  |  | 43728.1042 | 61 | 60
2019-09-20 03:00 | 52 | 42 |  |  | 43728.125 | 62 | 62
2019-09-20 03:30 | 52 | 43 |  |  | 43728.1458 | 62 | 62
2019-09-20 04:00 | 52 | 42 |  |  | 43728.1667 | 62 | 62
2019-09-20 04:30 | 52 | 42 |  |  | 43728.1875 | 63 | 63
2019-09-20 05:00 | 55 | 46 |  |  | 43728.2083 | 67 | 67
2019-09-20 05:30 | 58 | 51 |  |  | 43728.2292 | 72 | 72
2019-09-20 06:00 | 61 | 55 |  |  | 43728.25 | 79 | 79
2019-09-20 06:30 | 61 | 56 |  |  | 43728.2708 | 83 | 83
2019-09-20 07:00 | 60 | 56 |  |  | 43728.2917 | 87 | 87
2019-09-20 07:30 | 62 | 58 |  |  | 43728.3125 | 91 | 91
2019-09-20 08:00 | 66 | 56 |  |  | 43728.3333 | 94 | 90
2019-09-20 08:30 | 70 | 54 |  |  | 43728.3542 | 94 | 88
2019-09-20 09:00 | 67 | 51 |  |  | 43728.375 | 93 | 86
2019-09-20 09:30 | 67 | 52 |  |  | 43728.3958 | 94 | 87
2019-09-20 10:00 | 68 | 54 |  |  | 43728.4167 | 95 | 88
2019-09-20 10:30 | 68 | 54 |  |  | 43728.4375 | 94 | 86
2019-09-20 11:00 | 66 | 52 |  |  | 43728.4583 | 94 | 86
2019-09-20 11:30 | 65 | 52 |  |  | 43728.4792 | 93 | 84
2019-09-20 12:00 | 65 | 51 |  |  | 43728.5 | 90 | 81
2019-09-20 12:30 | 58 | 50 |  |  | 43728.5208 | 84 | 79
2019-09-20 13:00 | 54 | 51 |  |  | 43728.5417 | 83 | 80
2019-09-20 13:30 | 54 | 51 |  |  | 43728.5625 | 85 | 83
2019-09-20 14:00 | 55 | 52 |  |  | 43728.5833 | 84 | 82
2019-09-20 14:30 | 57 | 54 |  |  | 43728.6042 | 82 | 80
2019-09-20 15:00 | 56 | 53 |  |  | 43728.625 | 84 | 82
2019-09-20 15:30 | 57 | 53 |  |  | 43728.6458 | 86 | 85
2019-09-20 16:00 | 65 | 61 |  |  | 43728.6667 | 93 | 93
2019-09-20 16:30 | 69 | 64 |  |  | 43728.6875 | 97 | 96
2019-09-20 17:00 | 74 | 70 |  |  | 43728.7083 | 103 | 103
2019-09-20 17:30 | 75 | 71 |  |  | 43728.7292 | 105 | 104
2019-09-20 18:00 | 75 | 70 |  |  | 43728.75 | 103 | 103
2019-09-20 18:30 | 76 | 71 |  |  | 43728.7708 | 103 | 103
2019-09-20 19:00 | 78 | 73 |  |  | 43728.7917 | 104 | 104
2019-09-20 19:30 | 72 | 67 |  |  | 43728.8125 | 96 | 96
2019-09-20 20:00 | 70 | 65 |  |  | 43728.8333 | 93 | 93
2019-09-20 20:30 | 68 | 64 |  |  | 43728.8542 | 90 | 90
2019-09-20 21:00 | 64 | 59 |  |  | 43728.875 | 85 | 85
2019-09-20 21:30 | 62 | 56 |  |  | 43728.8958 | 80 | 80
2019-09-20 22:00 | 62 | 56 |  |  | 43728.9167 | 80 | 80
2019-09-20 22:30 | 61 | 54 |  |  | 43728.9375 | 80 | 80
2019-09-20 23:00 | 59 | 52 |  |  | 43728.9583 | 76 | 76
2019-09-20 23:30 | 55 | 46 |  |  | 43728.9792 | 70 | 70
2019-09-21 | 52 | 43 |  |  | 43729 | 67 | 67
2019-09-21 00:30 | 50 | 42 |  |  | 43729.0208 | 63 | 63
2019-09-21 01:00 | 48 | 39 |  |  | 43729.0417 | 60 | 60
2019-09-21 01:30 | 49 | 39 |  |  | 43729.0625 | 58 | 58
2019-09-21 02:00 | 49 | 39 |  |  | 43729.0833 | 58 | 58
2019-09-21 02:30 | 48 | 38 |  |  | 43729.1042 | 56 | 56
2019-09-21 03:00 | 47 | 35 |  |  | 43729.125 | 56 | 56
2019-09-21 03:30 | 45 | 33 |  |  | 43729.1458 | 55 | 55
2019-09-21 04:00 | 44 | 32 |  |  | 43729.1667 | 54 | 54
2019-09-21 04:30 | 45 | 33 |  |  | 43729.1875 | 53 | 53
2019-09-21 05:00 | 46 | 35 |  |  | 43729.2083 | 56 | 56
2019-09-21 05:30 | 46 | 35 |  |  | 43729.2292 | 56 | 56
2019-09-21 06:00 | 47 | 35 |  |  | 43729.25 | 58 | 58
2019-09-21 06:30 | 50 | 40 |  |  | 43729.2708 | 62 | 62
2019-09-21 07:00 | 48 | 38 |  |  | 43729.2917 | 61 | 61
2019-09-21 07:30 | 45 | 35 |  |  | 43729.3125 | 57 | 57
2019-09-21 08:00 | 42 | 33 |  |  | 43729.3333 | 54 | 54
2019-09-21 08:30 | 42 | 33 |  |  | 43729.3542 | 62 | 61
2019-09-21 09:00 | 43 | 36 |  |  | 43729.375 | 64 | 64
2019-09-21 09:30 | 43 | 36 |  |  | 43729.3958 | 66 | 65
2019-09-21 10:00 | 42 | 34 |  |  | 43729.4167 | 62 | 60
2019-09-21 10:30 | 38 | 31 |  |  | 43729.4375 | 56 | 55
2019-09-21 11:00 | 36 | 27 |  |  | 43729.4583 | 53 | 51
2019-09-21 11:30 | 33 | 23 |  |  | 43729.4792 | 49 | 48
2019-09-21 12:00 | 32 | 21 |  |  | 43729.5 | 49 | 47
2019-09-21 12:30 | 30 | 19 |  |  | 43729.5208 | 46 | 44
2019-09-21 13:00 | 31 | 20 |  |  | 43729.5417 | 46 | 45
2019-09-21 13:30 | 32 | 21 |  |  | 43729.5625 | 48 | 47
2019-09-21 14:00 | 33 | 23 |  |  | 43729.5833 | 48 | 46
2019-09-21 14:30 | 34 | 25 |  |  | 43729.6042 | 49 | 48
2019-09-21 15:00 | 38 | 29 |  |  | 43729.625 | 52 | 52
2019-09-21 15:30 | 40 | 33 |  |  | 43729.6458 | 56 | 56
2019-09-21 16:00 | 44 | 38 |  |  | 43729.6667 | 62 | 62
2019-09-21 16:30 | 49 | 43 |  |  | 43729.6875 | 69 | 69
2019-09-21 17:00 | 55 | 49 |  |  | 43729.7083 | 76 | 76
2019-09-21 17:30 | 59 | 53 |  |  | 43729.7292 | 79 | 79
2019-09-21 18:00 | 60 | 54 |  |  | 43729.75 | 82 | 82
2019-09-21 18:30 | 65 | 58 |  |  | 43729.7708 | 87 | 87
2019-09-21 19:00 | 67 | 60 |  |  | 43729.7917 | 90 | 89
2019-09-21 19:30 | 64 | 57 |  |  | 43729.8125 | 86 | 86
2019-09-21 20:00 | 63 | 55 |  |  | 43729.8333 | 84 | 84
2019-09-21 20:30 | 61 | 53 |  |  | 43729.8542 | 82 | 82
2019-09-21 21:00 | 58 | 50 |  |  | 43729.875 | 77 | 77
2019-09-21 21:30 | 58 | 49 |  |  | 43729.8958 | 75 | 75
2019-09-21 22:00 | 55 | 47 |  |  | 43729.9167 | 75 | 75
2019-09-21 22:30 | 54 | 46 |  |  | 43729.9375 | 74 | 74
2019-09-21 23:00 | 53 | 45 |  |  | 43729.9583 | 70 | 70
2019-09-21 23:30 | 50 | 41 |  |  | 43729.9792 | 66 | 66
2019-09-22 | 49 | 38 |  |  | 43730 | 63 | 63
2019-09-22 00:30 | 46 | 34 |  |  | 43730.0208 | 57 | 57
2019-09-22 01:00 | 45 | 31 |  |  | 43730.0417 | 53 | 53
2019-09-22 01:30 | 45 | 31 |  |  | 43730.0625 | 52 | 52
2019-09-22 02:00 | 42 | 30 |  |  | 43730.0833 | 50 | 50
2019-09-22 02:30 | 41 | 31 |  |  | 43730.1042 | 52 | 51
2019-09-22 03:00 | 43 | 33 |  |  | 43730.125 | 53 | 53
2019-09-22 03:30 | 45 | 36 |  |  | 43730.1458 | 57 | 56
2019-09-22 04:00 | 47 | 38 |  |  | 43730.1667 | 58 | 58
2019-09-22 04:30 | 47 | 37 |  |  | 43730.1875 | 57 | 57
2019-09-22 05:00 | 47 | 38 |  |  | 43730.2083 | 59 | 59
2019-09-22 05:30 | 48 | 38 |  |  | 43730.2292 | 60 | 59
2019-09-22 06:00 | 47 | 38 |  |  | 43730.25 | 59 | 59
2019-09-22 06:30 | 45 | 34 |  |  | 43730.2708 | 56 | 56
2019-09-22 07:00 | 43 | 32 |  |  | 43730.2917 | 55 | 55
2019-09-22 07:30 | 40 | 31 |  |  | 43730.3125 | 54 | 53
2019-09-22 08:00 | 41 | 31 |  |  | 43730.3333 | 56 | 56
2019-09-22 08:30 | 40 | 32 |  |  | 43730.3542 | 58 | 57
2019-09-22 09:00 | 39 | 31 |  |  | 43730.375 | 56 | 55
2019-09-22 09:30 | 40 | 32 |  |  | 43730.3958 | 59 | 57
2019-09-22 10:00 | 39 | 32 |  |  | 43730.4167 | 55 | 53
2019-09-22 10:30 | 38 | 30 |  |  | 43730.4375 | 52 | 51
2019-09-22 11:00 | 38 | 31 |  |  | 43730.4583 | 52 | 51
2019-09-22 11:30 | 36 | 29 |  |  | 43730.4792 | 52 | 50
2019-09-22 12:00 | 34 | 27 |  |  | 43730.5 | 48 | 45
2019-09-22 12:30 | 34 | 26 |  |  | 43730.5208 | 44 | 42
2019-09-22 13:00 | 33 | 25 |  |  | 43730.5417 | 43 | 40
2019-09-22 13:30 | 33 | 25 |  |  | 43730.5625 | 46 | 44
2019-09-22 14:00 | 32 | 25 |  |  | 43730.5833 | 48 | 45
2019-09-22 14:30 | 34 | 27 |  |  | 43730.6042 | 50 | 47
2019-09-22 15:00 | 36 | 30 |  |  | 43730.625 | 53 | 51
2019-09-22 15:30 | 39 | 33 |  |  | 43730.6458 | 57 | 54
2019-09-22 16:00 | 43 | 38 |  |  | 43730.6667 | 63 | 60
2019-09-22 16:30 | 47 | 42 |  |  | 43730.6875 | 69 | 67
2019-09-22 17:00 | 56 | 52 |  |  | 43730.7083 | 79 | 77
2019-09-22 17:30 | 60 | 55 |  |  | 43730.7292 | 82 | 81
2019-09-22 18:00 | 62 | 57 |  |  | 43730.75 | 85 | 84
2019-09-22 18:30 | 67 | 61 |  |  | 43730.7708 | 91 | 91
2019-09-22 19:00 | 68 | 63 |  |  | 43730.7917 | 93 | 92
2019-09-22 19:30 | 65 | 60 |  |  | 43730.8125 | 89 | 89
2019-09-22 20:00 | 64 | 59 |  |  | 43730.8333 | 88 | 87
2019-09-22 20:30 | 63 | 58 |  |  | 43730.8542 | 86 | 86
2019-09-22 21:00 | 60 | 55 |  |  | 43730.875 | 82 | 82
2019-09-22 21:30 | 58 | 52 |  |  | 43730.8958 | 78 | 77
2019-09-22 22:00 | 56 | 50 |  |  | 43730.9167 | 76 | 76
2019-09-22 22:30 | 54 | 48 |  |  | 43730.9375 | 76 | 76
2019-09-22 23:00 | 53 | 47 |  |  | 43730.9583 | 73 | 73
2019-09-22 23:30 | 52 | 46 |  |  | 43730.9792 | 70 | 70
2019-09-23 | 49 | 42 |  |  | 43731 | 65 | 65
2019-09-23 00:30 | 47 | 39 |  |  | 43731.0208 | 60 | 60
2019-09-23 01:00 | 44 | 36 |  |  | 43731.0417 | 55 | 55
2019-09-23 01:30 | 43 | 33 |  |  | 43731.0625 | 53 | 53
2019-09-23 02:00 | 46 | 36 |  |  | 43731.0833 | 55 | 55
2019-09-23 02:30 | 48 | 38 |  |  | 43731.1042 | 58 | 58
2019-09-23 03:00 | 47 | 38 |  |  | 43731.125 | 57 | 57
2019-09-23 03:30 | 45 | 35 |  |  | 43731.1458 | 55 | 55
2019-09-23 04:00 | 46 | 36 |  |  | 43731.1667 | 55 | 55
2019-09-23 04:30 | 48 | 38 |  |  | 43731.1875 | 58 | 58
2019-09-23 05:00 | 50 | 41 |  |  | 43731.2083 | 60 | 60
2019-09-23 05:30 | 51 | 44 |  |  | 43731.2292 | 64 | 63
2019-09-23 06:00 | 53 | 47 |  |  | 43731.25 | 67 | 67
2019-09-23 06:30 | 55 | 50 |  |  | 43731.2708 | 75 | 74
2019-09-23 07:00 | 56 | 52 |  |  | 43731.2917 | 81 | 80
2019-09-23 07:30 | 56 | 53 |  |  | 43731.3125 | 84 | 84
2019-09-23 08:00 | 51 | 50 |  |  | 43731.3333 | 91 | 90
2019-09-23 08:30 | 44 | 42 |  |  | 43731.3542 | 101 | 100
2019-09-23 09:00 | 41 | 39 |  |  | 43731.375 | 97 | 96
2019-09-23 09:30 | 43 | 41 |  |  | 43731.3958 | 97 | 96
2019-09-23 10:00 | 39 | 38 |  |  | 43731.4167 | 93 | 92
2019-09-23 10:30 | 39 | 37 |  |  | 43731.4375 | 91 | 90
2019-09-23 11:00 | 38 | 36 |  |  | 43731.4583 | 89 | 88
2019-09-23 11:30 | 39 | 37 |  |  | 43731.4792 | 89 | 88
2019-09-23 12:00 | 39 | 37 |  |  | 43731.5 | 90 | 89
2019-09-23 12:30 | 39 | 37 |  |  | 43731.5208 | 91 | 90
2019-09-23 13:00 | 41 | 39 |  |  | 43731.5417 | 94 | 92
2019-09-23 13:30 | 44 | 41 |  |  | 43731.5625 | 97 | 97
2019-09-23 14:00 | 48 | 45 |  |  | 43731.5833 | 99 | 99
2019-09-23 14:30 | 54 | 53 |  |  | 43731.6042 | 108 | 108
2019-09-23 15:00 | 57 | 57 |  |  | 43731.625 | 122 | 121
2019-09-23 15:30 | 59 | 59 |  |  | 43731.6458 | 120 | 120
2019-09-23 16:00 | 57 | 57 |  |  | 43731.6667 | 120 | 119
2019-09-23 16:30 | 57 | 57 |  |  | 43731.6875 | 122 | 122
2019-09-23 17:00 | 59 | 59 |  |  | 43731.7083 | 125 | 124
2019-09-23 17:30 | 61 | 60 |  |  | 43731.7292 | 125 | 125
2019-09-23 18:00 | 61 | 61 |  |  | 43731.75 | 124 | 124
2019-09-23 18:30 | 61 | 60 |  |  | 43731.7708 | 122 | 122
2019-09-23 19:00 | 59 | 59 |  |  | 43731.7917 | 121 | 121
2019-09-23 19:30 | 56 | 55 |  |  | 43731.8125 | 116 | 116
2019-09-23 20:00 | 55 | 55 |  |  | 43731.8333 | 114 | 114
2019-09-23 20:30 | 53 | 53 |  |  | 43731.8542 | 112 | 112
2019-09-23 21:00 | 48 | 47 |  |  | 43731.875 | 105 | 104
2019-09-23 21:30 | 43 | 42 |  |  | 43731.8958 | 98 | 98
2019-09-23 22:00 | 39 | 38 |  |  | 43731.9167 | 94 | 94
2019-09-23 22:30 | 35 | 34 |  |  | 43731.9375 | 91 | 91
2019-09-23 23:00 | 34 | 32 |  |  | 43731.9583 | 85 | 85
2019-09-23 23:30 | 31 | 30 |  |  | 43731.9792 | 81 | 81
2019-09-24 | 29 | 27 |  |  | 43732 | 77 | 77
2019-09-24 00:30 | 26 | 24 |  |  | 43732.0208 | 70 | 70
2019-09-24 01:00 | 22 | 20 |  |  | 43732.0417 | 63 | 63
2019-09-24 01:30 | 20 | 18 |  |  | 43732.0625 | 61 | 61
2019-09-24 02:00 | 20 | 17 |  |  | 43732.0833 | 58 | 58
2019-09-24 02:30 | 21 | 19 |  |  | 43732.1042 | 59 | 59
2019-09-24 03:00 | 22 | 20 |  |  | 43732.125 | 60 | 60
2019-09-24 03:30 | 25 | 23 |  |  | 43732.1458 | 63 | 63
2019-09-24 04:00 | 25 | 23 |  |  | 43732.1667 | 64 | 64
2019-09-24 04:30 | 25 | 23 |  |  | 43732.1875 | 64 | 64
2019-09-24 05:00 | 24 | 22 |  |  | 43732.2083 | 65 | 65
2019-09-24 05:30 | 28 | 27 |  |  | 43732.2292 | 71 | 71
2019-09-24 06:00 | 30 | 29 |  |  | 43732.25 | 75 | 75
2019-09-24 06:30 | 30 | 29 |  |  | 43732.2708 | 83 | 83
2019-09-24 07:00 | 31 | 30 |  |  | 43732.2917 | 89 | 89
2019-09-24 07:30 | 33 | 33 |  |  | 43732.3125 | 95 | 95
2019-09-24 08:00 | 38 | 38 |  |  | 43732.3333 | 99 | 99
2019-09-24 08:30 | 42 | 42 |  |  | 43732.3542 | 103 | 103
2019-09-24 09:00 | 49 | 49 |  |  | 43732.375 | 107 | 107
2019-09-24 09:30 | 50 | 50 |  |  | 43732.3958 | 108 | 107
2019-09-24 10:00 | 49 | 49 |  |  | 43732.4167 | 104 | 103
2019-09-24 10:30 | 48 | 48 |  |  | 43732.4375 | 99 | 98
2019-09-24 11:00 | 35 | 35 |  |  | 43732.4583 | 90 | 88
2019-09-24 11:30 | 36 | 36 |  |  | 43732.4792 | 91 | 89
2019-09-24 12:00 | 36 | 36 |  |  | 43732.5 | 92 | 90
2019-09-24 12:30 | 35 | 35 |  |  | 43732.5208 | 95 | 93
2019-09-24 13:00 | 35 | 35 |  |  | 43732.5417 | 92 | 91
2019-09-24 13:30 | 36 | 36 |  |  | 43732.5625 | 94 | 92
2019-09-24 14:00 | 34 | 34 |  |  | 43732.5833 | 95 | 93
2019-09-24 14:30 | 39 | 38 |  |  | 43732.6042 | 97 | 95
2019-09-24 15:00 | 39 | 39 |  |  | 43732.625 | 105 | 104
2019-09-24 15:30 | 40 | 40 |  |  | 43732.6458 | 100 | 99
2019-09-24 16:00 | 47 | 47 |  |  | 43732.6667 | 109 | 109
2019-09-24 16:30 | 45 | 45 |  |  | 43732.6875 | 108 | 107
2019-09-24 17:00 | 51 | 51 |  |  | 43732.7083 | 112 | 112
2019-09-24 17:30 | 53 | 53 |  |  | 43732.7292 | 115 | 115
2019-09-24 18:00 | 55 | 55 |  |  | 43732.75 | 117 | 116
2019-09-24 18:30 | 57 | 57 |  |  | 43732.7708 | 118 | 118
2019-09-24 19:00 | 58 | 57 |  |  | 43732.7917 | 119 | 119
2019-09-24 19:30 | 53 | 53 |  |  | 43732.8125 | 114 | 114
2019-09-24 20:00 | 51 | 50 |  |  | 43732.8333 | 110 | 110
2019-09-24 20:30 | 48 | 48 |  |  | 43732.8542 | 107 | 107
2019-09-24 21:00 | 43 | 42 |  |  | 43732.875 | 100 | 100
2019-09-24 21:30 | 37 | 36 |  |  | 43732.8958 | 94 | 94
2019-09-24 22:00 | 36 | 36 |  |  | 43732.9167 | 93 | 93
2019-09-24 22:30 | 34 | 34 |  |  | 43732.9375 | 91 | 90
2019-09-24 23:00 | 33 | 32 |  |  | 43732.9583 | 86 | 85
2019-09-24 23:30 | 29 | 28 |  |  | 43732.9792 | 80 | 80
2019-09-25 | 24 | 23 |  |  | 43733 | 73 | 73
2019-09-25 00:30 | 24 | 24 |  |  | 43733.0208 | 69 | 69
2019-09-25 01:00 | 22 | 21 |  |  | 43733.0417 | 64 | 63
2019-09-25 01:30 | 19 | 18 |  |  | 43733.0625 | 60 | 60
2019-09-25 02:00 | 18 | 17 |  |  | 43733.0833 | 57 | 57
2019-09-25 02:30 | 18 | 16 |  |  | 43733.1042 | 56 | 56
2019-09-25 03:00 | 19 | 18 |  |  | 43733.125 | 57 | 57
2019-09-25 03:30 | 23 | 21 |  |  | 43733.1458 | 59 | 59
2019-09-25 04:00 | 22 | 21 |  |  | 43733.1667 | 59 | 59
2019-09-25 04:30 | 22 | 21 |  |  | 43733.1875 | 60 | 60
2019-09-25 05:00 | 24 | 24 |  |  | 43733.2083 | 64 | 64
2019-09-25 05:30 | 28 | 27 |  |  | 43733.2292 | 71 | 70
2019-09-25 06:00 | 27 | 27 |  |  | 43733.25 | 74 | 73
2019-09-25 06:30 | 32 | 31 |  |  | 43733.2708 | 85 | 84
2019-09-25 07:00 | 34 | 34 |  |  | 43733.2917 | 92 | 91
2019-09-25 07:30 | 38 | 38 |  |  | 43733.3125 | 101 | 100
2019-09-25 08:00 | 43 | 43 |  |  | 43733.3333 | 109 | 107
2019-09-25 08:30 | 41 | 41 |  |  | 43733.3542 | 108 | 106
2019-09-25 09:00 | 39 | 39 |  |  | 43733.375 | 105 | 103
2019-09-25 09:30 | 51 | 51 |  |  | 43733.3958 | 115 | 114
2019-09-25 10:00 | 59 | 59 |  |  | 43733.4167 | 116 | 114
2019-09-25 10:30 | 55 | 55 |  |  | 43733.4375 | 117 | 116
2019-09-25 11:00 | 45 | 45 |  |  | 43733.4583 | 109 | 107
2019-09-25 11:30 | 36 | 36 |  |  | 43733.4792 | 97 | 96
2019-09-25 12:00 | 40 | 40 |  |  | 43733.5 | 103 | 101
2019-09-25 12:30 | 38 | 38 |  |  | 43733.5208 | 102 | 100
2019-09-25 13:00 | 37 | 37 |  |  | 43733.5417 | 99 | 98
2019-09-25 13:30 | 39 | 39 |  |  | 43733.5625 | 99 | 97
2019-09-25 14:00 | 40 | 40 |  |  | 43733.5833 | 98 | 97
2019-09-25 14:30 | 39 | 39 |  |  | 43733.6042 | 101 | 99
2019-09-25 15:00 | 43 | 43 |  |  | 43733.625 | 106 | 104
2019-09-25 15:30 | 47 | 47 |  |  | 43733.6458 | 110 | 109
2019-09-25 16:00 | 49 | 49 |  |  | 43733.6667 | 115 | 114
2019-09-25 16:30 | 47 | 47 |  |  | 43733.6875 | 116 | 116
2019-09-25 17:00 | 56 | 55 |  |  | 43733.7083 | 124 | 123
2019-09-25 17:30 | 59 | 59 |  |  | 43733.7292 | 125 | 125
2019-09-25 18:00 | 59 | 59 |  |  | 43733.75 | 125 | 125
2019-09-25 18:30 | 57 | 57 |  |  | 43733.7708 | 123 | 123
2019-09-25 19:00 | 60 | 60 |  |  | 43733.7917 | 126 | 126
2019-09-25 19:30 | 59 | 58 |  |  | 43733.8125 | 123 | 123
2019-09-25 20:00 | 57 | 57 |  |  | 43733.8333 | 120 | 120
2019-09-25 20:30 | 54 | 54 |  |  | 43733.8542 | 117 | 117
2019-09-25 21:00 | 50 | 50 |  |  | 43733.875 | 111 | 111
2019-09-25 21:30 | 45 | 45 |  |  | 43733.8958 | 104 | 104
2019-09-25 22:00 | 42 | 42 |  |  | 43733.9167 | 101 | 101
2019-09-25 22:30 | 42 | 42 |  |  | 43733.9375 | 100 | 99
2019-09-25 23:00 | 40 | 39 |  |  | 43733.9583 | 95 | 95
2019-09-25 23:30 | 37 | 36 |  |  | 43733.9792 | 89 | 89
2019-09-26 | 32 | 31 |  |  | 43734 | 81 | 81
2019-09-26 00:30 | 28 | 26 |  |  | 43734.0208 | 73 | 72
2019-09-26 01:00 | 27 | 26 |  |  | 43734.0417 | 70 | 70
2019-09-26 01:30 | 24 | 23 |  |  | 43734.0625 | 67 | 67
2019-09-26 02:00 | 23 | 22 |  |  | 43734.0833 | 65 | 65
2019-09-26 02:30 | 22 | 21 |  |  | 43734.1042 | 64 | 64
2019-09-26 03:00 | 22 | 21 |  |  | 43734.125 | 64 | 63
2019-09-26 03:30 | 23 | 22 |  |  | 43734.1458 | 63 | 63
2019-09-26 04:00 | 23 | 22 |  |  | 43734.1667 | 63 | 63
2019-09-26 04:30 | 24 | 23 |  |  | 43734.1875 | 65 | 65
2019-09-26 05:00 | 27 | 26 |  |  | 43734.2083 | 69 | 69
2019-09-26 05:30 | 30 | 30 |  |  | 43734.2292 | 74 | 74
2019-09-26 06:00 | 33 | 33 |  |  | 43734.25 | 80 | 79
2019-09-26 06:30 | 39 | 39 |  |  | 43734.2708 | 91 | 90
2019-09-26 07:00 | 43 | 43 |  |  | 43734.2917 | 100 | 99
2019-09-26 07:30 | 46 | 46 |  |  | 43734.3125 | 107 | 106
2019-09-26 08:00 | 46 | 46 |  |  | 43734.3333 | 109 | 107
2019-09-26 08:30 | 47 | 47 |  |  | 43734.3542 | 112 | 112
2019-09-26 09:00 | 47 | 47 |  |  | 43734.375 | 111 | 111
2019-09-26 09:30 | 54 | 54 |  |  | 43734.3958 | 115 | 115
2019-09-26 10:00 | 53 | 53 |  |  | 43734.4167 | 110 | 110
2019-09-26 10:30 | 50 | 50 |  |  | 43734.4375 | 103 | 103
2019-09-26 11:00 | 39 | 39 |  |  | 43734.4583 | 93 | 93
2019-09-26 11:30 | 38 | 37 |  |  | 43734.4792 | 87 | 87
2019-09-26 12:00 | 34 | 34 |  |  | 43734.5 | 87 | 86
2019-09-26 12:30 | 31 | 30 |  |  | 43734.5208 | 87 | 87
2019-09-26 13:00 | 40 | 39 |  |  | 43734.5417 | 95 | 94
2019-09-26 13:30 | 52 | 52 |  |  | 43734.5625 | 107 | 106
2019-09-26 14:00 | 52 | 52 |  |  | 43734.5833 | 115 | 115
2019-09-26 14:30 | 47 | 47 |  |  | 43734.6042 | 109 | 109
2019-09-26 15:00 | 46 | 45 |  |  | 43734.625 | 104 | 103
2019-09-26 15:30 | 42 | 42 |  |  | 43734.6458 | 99 | 99
2019-09-26 16:00 | 46 | 45 |  |  | 43734.6667 | 104 | 104
2019-09-26 16:30 | 49 | 48 |  |  | 43734.6875 | 110 | 110
2019-09-26 17:00 | 53 | 52 |  |  | 43734.7083 | 117 | 116
2019-09-26 17:30 | 56 | 55 |  |  | 43734.7292 | 119 | 119
2019-09-26 18:00 | 58 | 57 |  |  | 43734.75 | 122 | 122
2019-09-26 18:30 | 61 | 60 |  |  | 43734.7708 | 126 | 126
2019-09-26 19:00 | 60 | 58 |  |  | 43734.7917 | 124 | 124
2019-09-26 19:30 | 58 | 57 |  |  | 43734.8125 | 120 | 120
2019-09-26 20:00 | 57 | 56 |  |  | 43734.8333 | 118 | 118
2019-09-26 20:30 | 55 | 54 |  |  | 43734.8542 | 117 | 117
2019-09-26 21:00 | 52 | 50 |  |  | 43734.875 | 111 | 110
2019-09-26 21:30 | 46 | 46 |  |  | 43734.8958 | 105 | 105
2019-09-26 22:00 | 45 | 44 |  |  | 43734.9167 | 104 | 104
2019-09-26 22:30 | 43 | 42 |  |  | 43734.9375 | 101 | 101
2019-09-26 23:00 | 43 | 42 |  |  | 43734.9583 | 95 | 95
2019-09-26 23:30 | 41 | 39 |  |  | 43734.9792 | 91 | 91
2019-09-27 | 38 | 36 |  |  | 43735 | 85 | 85
2019-09-27 00:30 | 34 | 32 |  |  | 43735.0208 | 77 | 77
2019-09-27 01:00 | 29 | 27 |  |  | 43735.0417 | 69 | 69
2019-09-27 01:30 | 27 | 24 |  |  | 43735.0625 | 65 | 65
2019-09-27 02:00 | 27 | 26 |  |  | 43735.0833 | 65 | 65
2019-09-27 02:30 | 29 | 27 |  |  | 43735.1042 | 66 | 66
2019-09-27 03:00 | 28 | 27 |  |  | 43735.125 | 65 | 65
2019-09-27 03:30 | 27 | 26 |  |  | 43735.1458 | 65 | 65
2019-09-27 04:00 | 29 | 27 |  |  | 43735.1667 | 66 | 66
2019-09-27 04:30 | 30 | 29 |  |  | 43735.1875 | 68 | 68
2019-09-27 05:00 | 33 | 32 |  |  | 43735.2083 | 72 | 72
2019-09-27 05:30 | 33 | 33 |  |  | 43735.2292 | 74 | 74
2019-09-27 06:00 | 33 | 33 |  |  | 43735.25 | 77 | 77
2019-09-27 06:30 | 34 | 34 |  |  | 43735.2708 | 84 | 84
2019-09-27 07:00 | 41 | 41 |  |  | 43735.2917 | 95 | 94
2019-09-27 07:30 | 44 | 44 |  |  | 43735.3125 | 104 | 102
2019-09-27 08:00 | 43 | 42 |  |  | 43735.3333 | 105 | 102
2019-09-27 08:30 | 42 | 42 |  |  | 43735.3542 | 104 | 101
2019-09-27 09:00 | 41 | 40 |  |  | 43735.375 | 100 | 97
2019-09-27 09:30 | 40 | 39 |  |  | 43735.3958 | 98 | 94
2019-09-27 10:00 | 39 | 38 |  |  | 43735.4167 | 97 | 93
2019-09-27 10:30 | 36 | 35 |  |  | 43735.4375 | 94 | 90
2019-09-27 11:00 | 34 | 33 |  |  | 43735.4583 | 90 | 87
2019-09-27 11:30 | 35 | 34 |  |  | 43735.4792 | 92 | 90
2019-09-27 12:00 | 38 | 38 |  |  | 43735.5 | 97 | 95
2019-09-27 12:30 | 35 | 35 |  |  | 43735.5208 | 90 | 88
2019-09-27 13:00 | 37 | 37 |  |  | 43735.5417 | 91 | 89
2019-09-27 13:30 | 38 | 38 |  |  | 43735.5625 | 88 | 86
2019-09-27 14:00 | 37 | 37 |  |  | 43735.5833 | 89 | 88
2019-09-27 14:30 | 32 | 32 |  |  | 43735.6042 | 88 | 86
2019-09-27 15:00 | 34 | 34 |  |  | 43735.625 | 92 | 90
2019-09-27 15:30 | 44 | 44 |  |  | 43735.6458 | 103 | 102
2019-09-27 16:00 | 50 | 50 |  |  | 43735.6667 | 109 | 108
2019-09-27 16:30 | 50 | 50 |  |  | 43735.6875 | 113 | 112
2019-09-27 17:00 | 56 | 56 |  |  | 43735.7083 | 121 | 120
2019-09-27 17:30 | 63 | 63 |  |  | 43735.7292 | 131 | 131
2019-09-27 18:00 | 63 | 63 |  |  | 43735.75 | 133 | 132
2019-09-27 18:30 | 60 | 59 |  |  | 43735.7708 | 129 | 129
2019-09-27 19:00 | 60 | 60 |  |  | 43735.7917 | 129 | 129
2019-09-27 19:30 | 58 | 58 |  |  | 43735.8125 | 126 | 125
2019-09-27 20:00 | 57 | 55 |  |  | 43735.8333 | 120 | 119
2019-09-27 20:30 | 56 | 54 |  |  | 43735.8542 | 118 | 117
2019-09-27 21:00 | 52 | 49 |  |  | 43735.875 | 112 | 111
2019-09-27 21:30 | 50 | 47 |  |  | 43735.8958 | 108 | 106
2019-09-27 22:00 | 48 | 44 |  |  | 43735.9167 | 105 | 104
2019-09-27 22:30 | 46 | 42 |  |  | 43735.9375 | 103 | 102
2019-09-27 23:00 | 45 | 40 |  |  | 43735.9583 | 99 | 97
2019-09-27 23:30 | 43 | 37 |  |  | 43735.9792 | 94 | 92
2019-09-28 | 38 | 32 |  |  | 43736 | 86 | 84
2019-09-28 00:30 | 35 | 29 |  |  | 43736.0208 | 78 | 76
2019-09-28 01:00 | 34 | 28 |  |  | 43736.0417 | 74 | 72
2019-09-28 01:30 | 32 | 26 |  |  | 43736.0625 | 71 | 68
2019-09-28 02:00 | 30 | 23 |  |  | 43736.0833 | 67 | 64
2019-09-28 02:30 | 30 | 22 |  |  | 43736.1042 | 66 | 63
2019-09-28 03:00 | 30 | 22 |  |  | 43736.125 | 66 | 63
2019-09-28 03:30 | 32 | 25 |  |  | 43736.1458 | 68 | 66
2019-09-28 04:00 | 32 | 26 |  |  | 43736.1667 | 69 | 67
2019-09-28 04:30 | 32 | 27 |  |  | 43736.1875 | 69 | 68
2019-09-28 05:00 | 33 | 28 |  |  | 43736.2083 | 69 | 68
2019-09-28 05:30 | 31 | 26 |  |  | 43736.2292 | 68 | 67
2019-09-28 06:00 | 31 | 26 |  |  | 43736.25 | 69 | 68
2019-09-28 06:30 | 29 | 24 |  |  | 43736.2708 | 71 | 69
2019-09-28 07:00 | 29 | 25 |  |  | 43736.2917 | 74 | 72
2019-09-28 07:30 | 28 | 24 |  |  | 43736.3125 | 73 | 72
2019-09-28 08:00 | 28 | 25 |  |  | 43736.3333 | 73 | 73
2019-09-28 08:30 | 30 | 27 |  |  | 43736.3542 | 77 | 77
2019-09-28 09:00 | 30 | 28 |  |  | 43736.375 | 78 | 78
2019-09-28 09:30 | 28 | 27 |  |  | 43736.3958 | 76 | 76
2019-09-28 10:00 | 28 | 26 |  |  | 43736.4167 | 74 | 74
2019-09-28 10:30 | 28 | 26 |  |  | 43736.4375 | 74 | 74
2019-09-28 11:00 | 28 | 26 |  |  | 43736.4583 | 74 | 74
2019-09-28 11:30 | 28 | 27 |  |  | 43736.4792 | 75 | 74
2019-09-28 12:00 | 29 | 28 |  |  | 43736.5 | 77 | 77
2019-09-28 12:30 | 29 | 28 |  |  | 43736.5208 | 79 | 78
2019-09-28 13:00 | 30 | 30 |  |  | 43736.5417 | 80 | 80
2019-09-28 13:30 | 38 | 37 |  |  | 43736.5625 | 90 | 90
2019-09-28 14:00 | 40 | 39 |  |  | 43736.5833 | 94 | 94
2019-09-28 14:30 | 46 | 45 |  |  | 43736.6042 | 103 | 103
2019-09-28 15:00 | 48 | 48 |  |  | 43736.625 | 105 | 105
2019-09-28 15:30 | 42 | 41 |  |  | 43736.6458 | 95 | 95
2019-09-28 16:00 | 42 | 41 |  |  | 43736.6667 | 95 | 95
2019-09-28 16:30 | 47 | 45 |  |  | 43736.6875 | 103 | 103
2019-09-28 17:00 | 49 | 48 |  |  | 43736.7083 | 107 | 107
2019-09-28 17:30 | 51 | 50 |  |  | 43736.7292 | 110 | 110
2019-09-28 18:00 | 51 | 50 |  |  | 43736.75 | 111 | 111
2019-09-28 18:30 | 53 | 51 |  |  | 43736.7708 | 114 | 114
2019-09-28 19:00 | 52 | 52 |  |  | 43736.7917 | 115 | 115
2019-09-28 19:30 | 50 | 50 |  |  | 43736.8125 | 111 | 111
2019-09-28 20:00 | 50 | 50 |  |  | 43736.8333 | 111 | 111
2019-09-28 20:30 | 49 | 49 |  |  | 43736.8542 | 110 | 110
2019-09-28 21:00 | 45 | 45 |  |  | 43736.875 | 106 | 106
2019-09-28 21:30 | 43 | 43 |  |  | 43736.8958 | 102 | 102
2019-09-28 22:00 | 41 | 41 |  |  | 43736.9167 | 99 | 99
2019-09-28 22:30 | 39 | 38 |  |  | 43736.9375 | 96 | 96
2019-09-28 23:00 | 35 | 35 |  |  | 43736.9583 | 91 | 90
2019-09-28 23:30 | 32 | 32 |  |  | 43736.9792 | 87 | 87
2019-09-29 | 31 | 31 |  |  | 43737 | 83 | 83
2019-09-29 00:30 | 28 | 28 |  |  | 43737.0208 | 76 | 76
2019-09-29 01:00 | 26 | 26 |  |  | 43737.0417 | 71 | 71
2019-09-29 01:30 | 23 | 23 |  |  | 43737.0625 | 68 | 67
2019-09-29 02:00 | 23 | 23 |  |  | 43737.0833 | 66 | 66
2019-09-29 02:30 | 24 | 24 |  |  | 43737.1042 | 66 | 66
2019-09-29 03:00 | 23 | 23 |  |  | 43737.125 | 65 | 65
2019-09-29 03:30 | 23 | 23 |  |  | 43737.1458 | 65 | 65
2019-09-29 04:00 | 26 | 26 |  |  | 43737.1667 | 68 | 67
2019-09-29 04:30 | 26 | 26 |  |  | 43737.1875 | 68 | 68
2019-09-29 05:00 | 28 | 28 |  |  | 43737.2083 | 70 | 70
2019-09-29 05:30 | 29 | 28 |  |  | 43737.2292 | 71 | 71
2019-09-29 06:00 | 29 | 29 |  |  | 43737.25 | 72 | 72
2019-09-29 06:30 | 27 | 26 |  |  | 43737.2708 | 71 | 71
2019-09-29 07:00 | 24 | 24 |  |  | 43737.2917 | 70 | 70
2019-09-29 07:30 | 20 | 20 |  |  | 43737.3125 | 66 | 66
2019-09-29 08:00 | 19 | 19 |  |  | 43737.3333 | 65 | 65
2019-09-29 08:30 | 19 | 19 |  |  | 43737.3542 | 65 | 65
2019-09-29 09:00 | 21 | 20 |  |  | 43737.375 | 66 | 66
2019-09-29 09:30 | 20 | 20 |  |  | 43737.3958 | 64 | 64
2019-09-29 10:00 | 20 | 20 |  |  | 43737.4167 | 64 | 64
2019-09-29 10:30 | 23 | 22 |  |  | 43737.4375 | 65 | 65
2019-09-29 11:00 | 23 | 23 |  |  | 43737.4583 | 65 | 65
2019-09-29 11:30 | 24 | 24 |  |  | 43737.4792 | 65 | 65
2019-09-29 12:00 | 22 | 22 |  |  | 43737.5 | 64 | 63
2019-09-29 12:30 | 22 | 22 |  |  | 43737.5208 | 63 | 62
2019-09-29 13:00 | 22 | 22 |  |  | 43737.5417 | 63 | 62
2019-09-29 13:30 | 22 | 22 |  |  | 43737.5625 | 64 | 63
2019-09-29 14:00 | 24 | 24 |  |  | 43737.5833 | 66 | 65
2019-09-29 14:30 | 26 | 26 |  |  | 43737.6042 | 69 | 68
2019-09-29 15:00 | 28 | 28 |  |  | 43737.625 | 72 | 71
2019-09-29 15:30 | 32 | 31 |  |  | 43737.6458 | 79 | 79
2019-09-29 16:00 | 32 | 32 |  |  | 43737.6667 | 82 | 82
2019-09-29 16:30 | 36 | 36 |  |  | 43737.6875 | 90 | 89
2019-09-29 17:00 | 42 | 42 |  |  | 43737.7083 | 99 | 98
2019-09-29 17:30 | 44 | 44 |  |  | 43737.7292 | 103 | 103
2019-09-29 18:00 | 47 | 47 |  |  | 43737.75 | 107 | 107
2019-09-29 18:30 | 50 | 50 |  |  | 43737.7708 | 112 | 112
2019-09-29 19:00 | 52 | 52 |  |  | 43737.7917 | 115 | 115
2019-09-29 19:30 | 48 | 48 |  |  | 43737.8125 | 110 | 110
2019-09-29 20:00 | 45 | 45 |  |  | 43737.8333 | 107 | 107
2019-09-29 20:30 | 46 | 46 |  |  | 43737.8542 | 108 | 108
2019-09-29 21:00 | 44 | 44 |  |  | 43737.875 | 104 | 104
2019-09-29 21:30 | 41 | 41 |  |  | 43737.8958 | 99 | 99
2019-09-29 22:00 | 41 | 41 |  |  | 43737.9167 | 100 | 99
2019-09-29 22:30 | 39 | 39 |  |  | 43737.9375 | 98 | 98
2019-09-29 23:00 | 37 | 37 |  |  | 43737.9583 | 93 | 93
2019-09-29 23:30 | 33 | 33 |  |  | 43737.9792 | 87 | 87
2019-09-30 | 29 | 29 |  |  | 43738 | 80 | 80
2019-09-30 00:30 | 27 | 27 |  |  | 43738.0208 | 74 | 74
2019-09-30 01:00 | 24 | 24 |  |  | 43738.0417 | 70 | 70
2019-09-30 01:30 | 23 | 23 |  |  | 43738.0625 | 67 | 67
2019-09-30 02:00 | 23 | 22 |  |  | 43738.0833 | 65 | 65
2019-09-30 02:30 | 23 | 23 |  |  | 43738.1042 | 66 | 66
2019-09-30 03:00 | 24 | 24 |  |  | 43738.125 | 66 | 66
2019-09-30 03:30 | 22 | 22 |  |  | 43738.1458 | 65 | 64
2019-09-30 04:00 | 22 | 22 |  |  | 43738.1667 | 65 | 65
2019-09-30 04:30 | 23 | 23 |  |  | 43738.1875 | 66 | 66
2019-09-30 05:00 | 24 | 24 |  |  | 43738.2083 | 69 | 69
2019-09-30 05:30 | 30 | 30 |  |  | 43738.2292 | 77 | 76
2019-09-30 06:00 | 36 | 36 |  |  | 43738.25 | 84 | 84
2019-09-30 06:30 | 39 | 38 |  |  | 43738.2708 | 94 | 93
2019-09-30 07:00 | 45 | 44 |  |  | 43738.2917 | 105 | 104
2019-09-30 07:30 | 50 | 50 |  |  | 43738.3125 | 115 | 114
2019-09-30 08:00 | 52 | 51 |  |  | 43738.3333 | 120 | 119
2019-09-30 08:30 | 50 | 50 |  |  | 43738.3542 | 120 | 119
2019-09-30 09:00 | 48 | 48 |  |  | 43738.375 | 118 | 117
2019-09-30 09:30 | 48 | 48 |  |  | 43738.3958 | 116 | 115
2019-09-30 10:00 | 51 | 50 |  |  | 43738.4167 | 117 | 116
2019-09-30 10:30 | 52 | 51 |  |  | 43738.4375 | 119 | 119
2019-09-30 11:00 | 51 | 51 |  |  | 43738.4583 | 118 | 118
2019-09-30 11:30 | 50 | 49 |  |  | 43738.4792 | 117 | 116
2019-09-30 12:00 | 50 | 49 |  |  | 43738.5 | 117 | 116
2019-09-30 12:30 | 49 | 49 |  |  | 43738.5208 | 116 | 115
2019-09-30 13:00 | 50 | 50 |  |  | 43738.5417 | 116 | 115
2019-09-30 13:30 | 50 | 50 |  |  | 43738.5625 | 117 | 116
2019-09-30 14:00 | 48 | 48 |  |  | 43738.5833 | 118 | 118
2019-09-30 14:30 | 51 | 51 |  |  | 43738.6042 | 122 | 121
2019-09-30 15:00 | 53 | 53 |  |  | 43738.625 | 127 | 127
2019-09-30 15:30 | 59 | 59 |  |  | 43738.6458 | 133 | 132
2019-09-30 16:00 | 59 | 59 |  |  | 43738.6667 | 134 | 134
2019-09-30 16:30 | 63 | 63 |  |  | 43738.6875 | 138 | 137
2019-09-30 17:00 | 67 | 67 |  |  | 43738.7083 | 143 | 143
2019-09-30 17:30 | 66 | 66 |  |  | 43738.7292 | 142 | 142
2019-09-30 18:00 | 64 | 64 |  |  | 43738.75 | 139 | 139
2019-09-30 18:30 | 64 | 64 |  |  | 43738.7708 | 137 | 137
2019-09-30 19:00 | 64 | 64 |  |  | 43738.7917 | 137 | 136
2019-09-30 19:30 | 61 | 60 |  |  | 43738.8125 | 131 | 130
2019-09-30 20:00 | 60 | 59 |  |  | 43738.8333 | 128 | 127
2019-09-30 20:30 | 58 | 57 |  |  | 43738.8542 | 124 | 124
2019-09-30 21:00 | 56 | 56 |  |  | 43738.875 | 120 | 119
2019-09-30 21:30 | 51 | 51 |  |  | 43738.8958 | 113 | 112
2019-09-30 22:00 | 50 | 49 |  |  | 43738.9167 | 110 | 109
2019-09-30 22:30 | 48 | 47 |  |  | 43738.9375 | 107 | 106
2019-09-30 23:00 | 44 | 43 |  |  | 43738.9583 | 101 | 101
2019-09-30 23:30 | 40 | 39 |  |  | 43738.9792 | 95 | 94
2019-10-01 | 35 | 35 |  |  | 43739 | 88 | 87
2019-10-01 00:30 | 32 | 30 |  |  | 43739.0208 | 80 | 79
2019-10-01 01:00 | 30 | 28 |  |  | 43739.0417 | 76 | 74
2019-10-01 01:30 | 29 | 27 |  |  | 43739.0625 | 73 | 71
2019-10-01 02:00 | 28 | 27 |  |  | 43739.0833 | 71 | 70
2019-10-01 02:30 | 29 | 28 |  |  | 43739.1042 | 71 | 70
2019-10-01 03:00 | 28 | 27 |  |  | 43739.125 | 72 | 71
2019-10-01 03:30 | 28 | 27 |  |  | 43739.1458 | 72 | 71
2019-10-01 04:00 | 28 | 27 |  |  | 43739.1667 | 71 | 70
2019-10-01 04:30 | 28 | 27 |  |  | 43739.1875 | 72 | 71
2019-10-01 05:00 | 29 | 28 |  |  | 43739.2083 | 74 | 73
2019-10-01 05:30 | 33 | 32 |  |  | 43739.2292 | 80 | 79
2019-10-01 06:00 | 37 | 36 |  |  | 43739.25 | 86 | 85
2019-10-01 06:30 | 42 | 42 |  |  | 43739.2708 | 97 | 97
2019-10-01 07:00 | 45 | 45 |  |  | 43739.2917 | 107 | 107
2019-10-01 07:30 | 51 | 51 |  |  | 43739.3125 | 118 | 118
2019-10-01 08:00 | 61 | 61 |  |  | 43739.3333 | 128 | 128
2019-10-01 08:30 | 67 | 67 |  |  | 43739.3542 | 136 | 136
2019-10-01 09:00 | 67 | 67 |  |  | 43739.375 | 138 | 138
2019-10-01 09:30 | 69 | 68 |  |  | 43739.3958 | 136 | 136
2019-10-01 10:00 | 71 | 71 |  |  | 43739.4167 | 136 | 136
2019-10-01 10:30 | 67 | 67 |  |  | 43739.4375 | 135 | 135
2019-10-01 11:00 | 63 | 63 |  |  | 43739.4583 | 129 | 129
2019-10-01 11:30 | 57 | 57 |  |  | 43739.4792 | 123 | 123
2019-10-01 12:00 | 58 | 58 |  |  | 43739.5 | 123 | 123
2019-10-01 12:30 | 63 | 62 |  |  | 43739.5208 | 127 | 127
2019-10-01 13:00 | 63 | 62 |  |  | 43739.5417 | 128 | 128
2019-10-01 13:30 | 53 | 53 |  |  | 43739.5625 | 116 | 116
2019-10-01 14:00 | 55 | 54 |  |  | 43739.5833 | 119 | 119
2019-10-01 14:30 | 62 | 62 |  |  | 43739.6042 | 126 | 126
2019-10-01 15:00 | 60 | 59 |  |  | 43739.625 | 126 | 126
2019-10-01 15:30 | 60 | 60 |  |  | 43739.6458 | 127 | 127
2019-10-01 16:00 | 65 | 64 |  |  | 43739.6667 | 135 | 135
2019-10-01 16:30 | 65 | 65 |  |  | 43739.6875 | 136 | 136
2019-10-01 17:00 | 67 | 66 |  |  | 43739.7083 | 139 | 139
2019-10-01 17:30 | 69 | 68 |  |  | 43739.7292 | 141 | 141
2019-10-01 18:00 | 74 | 73 |  |  | 43739.75 | 144 | 143
2019-10-01 18:30 | 72 | 71 |  |  | 43739.7708 | 142 | 141
2019-10-01 19:00 | 72 | 70 |  |  | 43739.7917 | 143 | 141
2019-10-01 19:30 | 70 | 68 |  |  | 43739.8125 | 137 | 135
2019-10-01 20:00 | 68 | 66 |  |  | 43739.8333 | 133 | 132
2019-10-01 20:30 | 67 | 65 |  |  | 43739.8542 | 131 | 130
2019-10-01 21:00 | 64 | 62 |  |  | 43739.875 | 126 | 124
2019-10-01 21:30 | 59 | 56 |  |  | 43739.8958 | 119 | 117
2019-10-01 22:00 | 57 | 54 |  |  | 43739.9167 | 115 | 113
2019-10-01 22:30 | 55 | 52 |  |  | 43739.9375 | 112 | 110
2019-10-01 23:00 | 50 | 47 |  |  | 43739.9583 | 104 | 102
2019-10-01 23:30 | 45 | 41 |  |  | 43739.9792 | 97 | 94
2019-10-02 | 42 | 39 |  |  | 43740 | 92 | 89
2019-10-02 00:30 | 42 | 38 |  |  | 43740.0208 | 88 | 85
2019-10-02 01:00 | 38 | 34 |  |  | 43740.0417 | 82 | 80
2019-10-02 01:30 | 37 | 34 |  |  | 43740.0625 | 80 | 77
2019-10-02 02:00 | 36 | 33 |  |  | 43740.0833 | 77 | 75
2019-10-02 02:30 | 36 | 33 |  |  | 43740.1042 | 77 | 75
2019-10-02 03:00 | 36 | 33 |  |  | 43740.125 | 76 | 74
2019-10-02 03:30 | 35 | 33 |  |  | 43740.1458 | 76 | 75
2019-10-02 04:00 | 36 | 34 |  |  | 43740.1667 | 77 | 76
2019-10-02 04:30 | 37 | 35 |  |  | 43740.1875 | 78 | 77
2019-10-02 05:00 | 43 | 42 |  |  | 43740.2083 | 85 | 84
2019-10-02 05:30 | 44 | 43 |  |  | 43740.2292 | 89 | 88
2019-10-02 06:00 | 43 | 42 |  |  | 43740.25 | 91 | 91
2019-10-02 06:30 | 45 | 45 |  |  | 43740.2708 | 99 | 99
2019-10-02 07:00 | 49 | 48 |  |  | 43740.2917 | 108 | 108
2019-10-02 07:30 | 58 | 57 |  |  | 43740.3125 | 119 | 119
2019-10-02 08:00 | 60 | 59 |  |  | 43740.3333 | 124 | 124
2019-10-02 08:30 | 64 | 63 |  |  | 43740.3542 | 130 | 130
2019-10-02 09:00 | 70 | 68 |  |  | 43740.375 | 132 | 132
2019-10-02 09:30 | 58 | 56 |  |  | 43740.3958 | 118 | 118
2019-10-02 10:00 | 51 | 49 |  |  | 43740.4167 | 111 | 110
2019-10-02 10:30 | 49 | 48 |  |  | 43740.4375 | 108 | 108
2019-10-02 11:00 | 46 | 45 |  |  | 43740.4583 | 103 | 103
2019-10-02 11:30 | 46 | 44 |  |  | 43740.4792 | 104 | 104
2019-10-02 12:00 | 46 | 45 |  |  | 43740.5 | 102 | 102
2019-10-02 12:30 | 49 | 48 |  |  | 43740.5208 | 106 | 106
2019-10-02 13:00 | 46 | 44 |  |  | 43740.5417 | 103 | 103
2019-10-02 13:30 | 47 | 45 |  |  | 43740.5625 | 104 | 104
2019-10-02 14:00 | 49 | 48 |  |  | 43740.5833 | 107 | 107
2019-10-02 14:30 | 50 | 48 |  |  | 43740.6042 | 109 | 109
2019-10-02 15:00 | 49 | 48 |  |  | 43740.625 | 108 | 108
2019-10-02 15:30 | 52 | 51 |  |  | 43740.6458 | 113 | 112
2019-10-02 16:00 | 58 | 57 |  |  | 43740.6667 | 121 | 121
2019-10-02 16:30 | 57 | 55 |  |  | 43740.6875 | 124 | 124
2019-10-02 17:00 | 61 | 59 |  |  | 43740.7083 | 130 | 130
2019-10-02 17:30 | 60 | 58 |  |  | 43740.7292 | 130 | 130
2019-10-02 18:00 | 61 | 59 |  |  | 43740.75 | 132 | 131
2019-10-02 18:30 | 61 | 59 |  |  | 43740.7708 | 132 | 131
2019-10-02 19:00 | 61 | 60 |  |  | 43740.7917 | 133 | 132
2019-10-02 19:30 | 60 | 58 |  |  | 43740.8125 | 129 | 128
2019-10-02 20:00 | 60 | 58 |  |  | 43740.8333 | 125 | 124
2019-10-02 20:30 | 59 | 57 |  |  | 43740.8542 | 123 | 122
2019-10-02 21:00 | 56 | 54 |  |  | 43740.875 | 117 | 116
2019-10-02 21:30 | 52 | 50 |  |  | 43740.8958 | 111 | 110
2019-10-02 22:00 | 51 | 48 |  |  | 43740.9167 | 109 | 107
2019-10-02 22:30 | 48 | 45 |  |  | 43740.9375 | 104 | 103
2019-10-02 23:00 | 46 | 42 |  |  | 43740.9583 | 99 | 98
2019-10-02 23:30 | 41 | 36 |  |  | 43740.9792 | 94 | 92
2019-10-03 | 39 | 33 |  |  | 43741 | 88 | 85
2019-10-03 00:30 | 35 | 29 |  |  | 43741.0208 | 79 | 76
2019-10-03 01:00 | 31 | 27 |  |  | 43741.0417 | 72 | 71
2019-10-03 01:30 | 29 | 24 |  |  | 43741.0625 | 69 | 68
2019-10-03 02:00 | 28 | 23 |  |  | 43741.0833 | 67 | 65
2019-10-03 02:30 | 28 | 23 |  |  | 43741.1042 | 66 | 64
2019-10-03 03:00 | 28 | 23 |  |  | 43741.125 | 65 | 64
2019-10-03 03:30 | 28 | 22 |  |  | 43741.1458 | 65 | 63
2019-10-03 04:00 | 28 | 23 |  |  | 43741.1667 | 66 | 64
2019-10-03 04:30 | 29 | 24 |  |  | 43741.1875 | 68 | 67
2019-10-03 05:00 | 31 | 28 |  |  | 43741.2083 | 72 | 71
2019-10-03 05:30 | 35 | 32 |  |  | 43741.2292 | 77 | 76
2019-10-03 06:00 | 36 | 34 |  |  | 43741.25 | 83 | 83
2019-10-03 06:30 | 41 | 39 |  |  | 43741.2708 | 93 | 93
2019-10-03 07:00 | 42 | 41 |  |  | 43741.2917 | 99 | 99
2019-10-03 07:30 | 44 | 43 |  |  | 43741.3125 | 107 | 107
2019-10-03 08:00 | 46 | 45 |  |  | 43741.3333 | 108 | 108
2019-10-03 08:30 | 44 | 43 |  |  | 43741.3542 | 106 | 106
2019-10-03 09:00 | 44 | 43 |  |  | 43741.375 | 103 | 103
2019-10-03 09:30 | 42 | 41 |  |  | 43741.3958 | 100 | 100
2019-10-03 10:00 | 41 | 40 |  |  | 43741.4167 | 97 | 97
2019-10-03 10:30 | 41 | 40 |  |  | 43741.4375 | 95 | 95
2019-10-03 11:00 | 42 | 41 |  |  | 43741.4583 | 95 | 95
2019-10-03 11:30 | 40 | 39 |  |  | 43741.4792 | 94 | 93
2019-10-03 12:00 | 40 | 39 |  |  | 43741.5 | 94 | 94
2019-10-03 12:30 | 40 | 39 |  |  | 43741.5208 | 95 | 95
2019-10-03 13:00 | 40 | 39 |  |  | 43741.5417 | 95 | 95
2019-10-03 13:30 | 41 | 40 |  |  | 43741.5625 | 98 | 97
2019-10-03 14:00 | 43 | 42 |  |  | 43741.5833 | 100 | 100
2019-10-03 14:30 | 45 | 44 |  |  | 43741.6042 | 102 | 102
2019-10-03 15:00 | 46 | 44 |  |  | 43741.625 | 106 | 106
2019-10-03 15:30 | 48 | 46 |  |  | 43741.6458 | 110 | 110
2019-10-03 16:00 | 53 | 51 |  |  | 43741.6667 | 117 | 117
2019-10-03 16:30 | 57 | 55 |  |  | 43741.6875 | 124 | 124
2019-10-03 17:00 | 61 | 59 |  |  | 43741.7083 | 130 | 130
2019-10-03 17:30 | 61 | 59 |  |  | 43741.7292 | 132 | 131
2019-10-03 18:00 | 61 | 59 |  |  | 43741.75 | 132 | 130
2019-10-03 18:30 | 61 | 58 |  |  | 43741.7708 | 132 | 130
2019-10-03 19:00 | 63 | 60 |  |  | 43741.7917 | 134 | 132
2019-10-03 19:30 | 61 | 58 |  |  | 43741.8125 | 130 | 128
2019-10-03 20:00 | 61 | 58 |  |  | 43741.8333 | 126 | 125
2019-10-03 20:30 | 59 | 56 |  |  | 43741.8542 | 124 | 122
2019-10-03 21:00 | 58 | 54 |  |  | 43741.875 | 118 | 116
2019-10-03 21:30 | 54 | 49 |  |  | 43741.8958 | 111 | 108
2019-10-03 22:00 | 51 | 46 |  |  | 43741.9167 | 108 | 105
2019-10-03 22:30 | 49 | 43 |  |  | 43741.9375 | 105 | 102
2019-10-03 23:00 | 47 | 42 |  |  | 43741.9583 | 99 | 97
2019-10-03 23:30 | 44 | 39 |  |  | 43741.9792 | 94 | 92
2019-10-04 | 42 | 34 |  |  | 43742 | 88 | 85
2019-10-04 00:30 | 41 | 31 |  |  | 43742.0208 | 81 | 77
2019-10-04 01:00 | 39 | 28 |  |  | 43742.0417 | 75 | 71
2019-10-04 01:30 | 38 | 28 |  |  | 43742.0625 | 73 | 70
2019-10-04 02:00 | 38 | 27 |  |  | 43742.0833 | 73 | 69
2019-10-04 02:30 | 37 | 26 |  |  | 43742.1042 | 71 | 67
2019-10-04 03:00 | 39 | 29 |  |  | 43742.125 | 72 | 69
2019-10-04 03:30 | 40 | 31 |  |  | 43742.1458 | 74 | 70
2019-10-04 04:00 | 41 | 32 |  |  | 43742.1667 | 75 | 71
2019-10-04 04:30 | 42 | 33 |  |  | 43742.1875 | 77 | 74
2019-10-04 05:00 | 43 | 35 |  |  | 43742.2083 | 80 | 77
2019-10-04 05:30 | 43 | 36 |  |  | 43742.2292 | 82 | 80
2019-10-04 06:00 | 42 | 35 |  |  | 43742.25 | 84 | 82
2019-10-04 06:30 | 42 | 38 |  |  | 43742.2708 | 91 | 90
2019-10-04 07:00 | 44 | 40 |  |  | 43742.2917 | 96 | 95
2019-10-04 07:30 | 45 | 42 |  |  | 43742.3125 | 102 | 101
2019-10-04 08:00 | 41 | 40 |  |  | 43742.3333 | 101 | 101
2019-10-04 08:30 | 41 | 39 |  |  | 43742.3542 | 100 | 100
2019-10-04 09:00 | 40 | 38 |  |  | 43742.375 | 98 | 98
2019-10-04 09:30 | 40 | 38 |  |  | 43742.3958 | 97 | 97
2019-10-04 10:00 | 38 | 36 |  |  | 43742.4167 | 94 | 94
2019-10-04 10:30 | 38 | 36 |  |  | 43742.4375 | 94 | 94
2019-10-04 11:00 | 37 | 35 |  |  | 43742.4583 | 92 | 92
2019-10-04 11:30 | 35 | 33 |  |  | 43742.4792 | 91 | 91
2019-10-04 12:00 | 34 | 32 |  |  | 43742.5 | 90 | 90
2019-10-04 12:30 | 37 | 34 |  |  | 43742.5208 | 91 | 91
2019-10-04 13:00 | 37 | 35 |  |  | 43742.5417 | 91 | 91
2019-10-04 13:30 | 38 | 35 |  |  | 43742.5625 | 91 | 91
2019-10-04 14:00 | 39 | 37 |  |  | 43742.5833 | 94 | 94
2019-10-04 14:30 | 41 | 39 |  |  | 43742.6042 | 97 | 97
2019-10-04 15:00 | 44 | 41 |  |  | 43742.625 | 102 | 102
2019-10-04 15:30 | 45 | 42 |  |  | 43742.6458 | 105 | 105
2019-10-04 16:00 | 50 | 47 |  |  | 43742.6667 | 114 | 114
2019-10-04 16:30 | 53 | 51 |  |  | 43742.6875 | 119 | 118
2019-10-04 17:00 | 59 | 57 |  |  | 43742.7083 | 127 | 127
2019-10-04 17:30 | 62 | 59 |  |  | 43742.7292 | 130 | 129
2019-10-04 18:00 | 66 | 62 |  |  | 43742.75 | 132 | 131
2019-10-04 18:30 | 66 | 62 |  |  | 43742.7708 | 131 | 130
2019-10-04 19:00 | 68 | 64 |  |  | 43742.7917 | 132 | 131
2019-10-04 19:30 | 67 | 62 |  |  | 43742.8125 | 129 | 127
2019-10-04 20:00 | 67 | 61 |  |  | 43742.8333 | 128 | 126
2019-10-04 20:30 | 63 | 58 |  |  | 43742.8542 | 125 | 123
2019-10-04 21:00 | 60 | 55 |  |  | 43742.875 | 118 | 116
2019-10-04 21:30 | 55 | 50 |  |  | 43742.8958 | 112 | 110
2019-10-04 22:00 | 55 | 48 |  |  | 43742.9167 | 109 | 107
2019-10-04 22:30 | 53 | 46 |  |  | 43742.9375 | 107 | 105
2019-10-04 23:00 | 50 | 43 |  |  | 43742.9583 | 101 | 98
2019-10-04 23:30 | 49 | 40 |  |  | 43742.9792 | 97 | 94
2019-10-05 | 47 | 37 |  |  | 43743 | 92 | 88
2019-10-05 00:30 | 45 | 34 |  |  | 43743.0208 | 86 | 81
2019-10-05 01:00 | 44 | 32 |  |  | 43743.0417 | 83 | 78
2019-10-05 01:30 | 43 | 34 |  |  | 43743.0625 | 80 | 76
2019-10-05 02:00 | 43 | 33 |  |  | 43743.0833 | 79 | 75
2019-10-05 02:30 | 43 | 33 |  |  | 43743.1042 | 78 | 75
2019-10-05 03:00 | 40 | 30 |  |  | 43743.125 | 74 | 72
2019-10-05 03:30 | 42 | 32 |  |  | 43743.1458 | 76 | 73
2019-10-05 04:00 | 41 | 32 |  |  | 43743.1667 | 74 | 72
2019-10-05 04:30 | 42 | 34 |  |  | 43743.1875 | 76 | 73
2019-10-05 05:00 | 44 | 36 |  |  | 43743.2083 | 78 | 75
2019-10-05 05:30 | 44 | 36 |  |  | 43743.2292 | 78 | 76
2019-10-05 06:00 | 43 | 34 |  |  | 43743.25 | 79 | 76
2019-10-05 06:30 | 38 | 28 |  |  | 43743.2708 | 74 | 72
2019-10-05 07:00 | 34 | 23 |  |  | 43743.2917 | 70 | 68
2019-10-05 07:30 | 32 | 22 |  |  | 43743.3125 | 69 | 67
2019-10-05 08:00 | 32 | 22 |  |  | 43743.3333 | 69 | 68
2019-10-05 08:30 | 31 | 22 |  |  | 43743.3542 | 69 | 68
2019-10-05 09:00 | 29 | 20 |  |  | 43743.375 | 68 | 67
2019-10-05 09:30 | 27 | 19 |  |  | 43743.3958 | 68 | 68
2019-10-05 10:00 | 28 | 21 |  |  | 43743.4167 | 68 | 68
2019-10-05 10:30 | 28 | 22 |  |  | 43743.4375 | 68 | 67
2019-10-05 11:00 | 29 | 23 |  |  | 43743.4583 | 68 | 68
2019-10-05 11:30 | 26 | 20 |  |  | 43743.4792 | 64 | 64
2019-10-05 12:00 | 26 | 19 |  |  | 43743.5 | 64 | 64
2019-10-05 12:30 | 24 | 17 |  |  | 43743.5208 | 61 | 61
2019-10-05 13:00 | 24 | 17 |  |  | 43743.5417 | 60 | 59
2019-10-05 13:30 | 26 | 21 |  |  | 43743.5625 | 65 | 64
2019-10-05 14:00 | 27 | 21 |  |  | 43743.5833 | 66 | 66
2019-10-05 14:30 | 30 | 25 |  |  | 43743.6042 | 71 | 71
2019-10-05 15:00 | 32 | 28 |  |  | 43743.625 | 78 | 78
2019-10-05 15:30 | 35 | 31 |  |  | 43743.6458 | 82 | 82
2019-10-05 16:00 | 37 | 32 |  |  | 43743.6667 | 87 | 87
2019-10-05 16:30 | 41 | 35 |  |  | 43743.6875 | 94 | 93
2019-10-05 17:00 | 45 | 40 |  |  | 43743.7083 | 100 | 99
2019-10-05 17:30 | 51 | 47 |  |  | 43743.7292 | 106 | 105
2019-10-05 18:00 | 53 | 49 |  |  | 43743.75 | 109 | 108
2019-10-05 18:30 | 56 | 53 |  |  | 43743.7708 | 114 | 113
2019-10-05 19:00 | 58 | 55 |  |  | 43743.7917 | 116 | 116
2019-10-05 19:30 | 56 | 52 |  |  | 43743.8125 | 113 | 112
2019-10-05 20:00 | 54 | 50 |  |  | 43743.8333 | 110 | 109
2019-10-05 20:30 | 53 | 49 |  |  | 43743.8542 | 110 | 109
2019-10-05 21:00 | 51 | 46 |  |  | 43743.875 | 105 | 104
2019-10-05 21:30 | 50 | 45 |  |  | 43743.8958 | 102 | 101
2019-10-05 22:00 | 51 | 46 |  |  | 43743.9167 | 104 | 102
2019-10-05 22:30 | 49 | 43 |  |  | 43743.9375 | 101 | 100
2019-10-05 23:00 | 47 | 41 |  |  | 43743.9583 | 97 | 96
2019-10-05 23:30 | 46 | 39 |  |  | 43743.9792 | 94 | 92
2019-10-06 | 43 | 36 |  |  | 43744 | 89 | 87
2019-10-06 00:30 | 43 | 34 |  |  | 43744.0208 | 84 | 82
2019-10-06 01:00 | 44 | 34 |  |  | 43744.0417 | 83 | 79
2019-10-06 01:30 | 46 | 37 |  |  | 43744.0625 | 83 | 79
2019-10-06 02:00 | 46 | 35 |  |  | 43744.0833 | 81 | 77
2019-10-06 02:30 | 45 | 34 |  |  | 43744.1042 | 79 | 75
2019-10-06 03:00 | 44 | 33 |  |  | 43744.125 | 78 | 73
2019-10-06 03:30 | 44 | 34 |  |  | 43744.1458 | 78 | 74
2019-10-06 04:00 | 43 | 34 |  |  | 43744.1667 | 76 | 73
2019-10-06 04:30 | 43 | 35 |  |  | 43744.1875 | 77 | 74
2019-10-06 05:00 | 44 | 35 |  |  | 43744.2083 | 77 | 74
2019-10-06 05:30 | 44 | 35 |  |  | 43744.2292 | 78 | 75
2019-10-06 06:00 | 45 | 36 |  |  | 43744.25 | 79 | 76
2019-10-06 06:30 | 42 | 31 |  |  | 43744.2708 | 76 | 72
2019-10-06 07:00 | 37 | 25 |  |  | 43744.2917 | 71 | 68
2019-10-06 07:30 | 32 | 21 |  |  | 43744.3125 | 69 | 67
2019-10-06 08:00 | 31 | 19 |  |  | 43744.3333 | 66 | 64
2019-10-06 08:30 | 32 | 21 |  |  | 43744.3542 | 66 | 64
2019-10-06 09:00 | 30 | 22 |  |  | 43744.375 | 66 | 65
2019-10-06 09:30 | 30 | 22 |  |  | 43744.3958 | 69 | 68
2019-10-06 10:00 | 30 | 22 |  |  | 43744.4167 | 69 | 69
2019-10-06 10:30 | 30 | 23 |  |  | 43744.4375 | 68 | 68
2019-10-06 11:00 | 30 | 22 |  |  | 43744.4583 | 67 | 67
2019-10-06 11:30 | 27 | 19 |  |  | 43744.4792 | 61 | 60
2019-10-06 12:00 | 25 | 17 |  |  | 43744.5 | 57 | 57
2019-10-06 12:30 | 25 | 17 |  |  | 43744.5208 | 57 | 56
2019-10-06 13:00 | 25 | 17 |  |  | 43744.5417 | 57 | 56
2019-10-06 13:30 | 25 | 17 |  |  | 43744.5625 | 58 | 57
2019-10-06 14:00 | 27 | 21 |  |  | 43744.5833 | 61 | 61
2019-10-06 14:30 | 29 | 24 |  |  | 43744.6042 | 64 | 64
2019-10-06 15:00 | 29 | 23 |  |  | 43744.625 | 65 | 65
2019-10-06 15:30 | 32 | 27 |  |  | 43744.6458 | 72 | 71
2019-10-06 16:00 | 36 | 32 |  |  | 43744.6667 | 80 | 80
2019-10-06 16:30 | 37 | 32 |  |  | 43744.6875 | 84 | 84
2019-10-06 17:00 | 41 | 36 |  |  | 43744.7083 | 92 | 91
2019-10-06 17:30 | 45 | 40 |  |  | 43744.7292 | 96 | 95
2019-10-06 18:00 | 51 | 46 |  |  | 43744.75 | 104 | 103
2019-10-06 18:30 | 55 | 51 |  |  | 43744.7708 | 110 | 110
2019-10-06 19:00 | 56 | 52 |  |  | 43744.7917 | 112 | 112
2019-10-06 19:30 | 54 | 50 |  |  | 43744.8125 | 109 | 108
2019-10-06 20:00 | 53 | 48 |  |  | 43744.8333 | 107 | 106
2019-10-06 20:30 | 52 | 48 |  |  | 43744.8542 | 107 | 106
2019-10-06 21:00 | 49 | 44 |  |  | 43744.875 | 101 | 100
2019-10-06 21:30 | 45 | 40 |  |  | 43744.8958 | 97 | 96
2019-10-06 22:00 | 45 | 39 |  |  | 43744.9167 | 97 | 96
2019-10-06 22:30 | 44 | 38 |  |  | 43744.9375 | 96 | 95
2019-10-06 23:00 | 44 | 37 |  |  | 43744.9583 | 92 | 91
2019-10-06 23:30 | 42 | 34 |  |  | 43744.9792 | 88 | 86
2019-10-07 | 41 | 33 |  |  | 43745 | 84 | 82
2019-10-07 00:30 | 40 | 30 |  |  | 43745.0208 | 79 | 76
2019-10-07 01:00 | 40 | 30 |  |  | 43745.0417 | 76 | 72
2019-10-07 01:30 | 42 | 32 |  |  | 43745.0625 | 77 | 73
2019-10-07 02:00 | 40 | 29 |  |  | 43745.0833 | 74 | 71
2019-10-07 02:30 | 39 | 28 |  |  | 43745.1042 | 72 | 69
2019-10-07 03:00 | 38 | 28 |  |  | 43745.125 | 70 | 67
2019-10-07 03:30 | 39 | 28 |  |  | 43745.1458 | 71 | 68
2019-10-07 04:00 | 39 | 28 |  |  | 43745.1667 | 71 | 68
2019-10-07 04:30 | 39 | 29 |  |  | 43745.1875 | 71 | 68
2019-10-07 05:00 | 38 | 28 |  |  | 43745.2083 | 70 | 67
2019-10-07 05:30 | 38 | 28 |  |  | 43745.2292 | 71 | 68
2019-10-07 06:00 | 37 | 26 |  |  | 43745.25 | 71 | 68
2019-10-07 06:30 | 35 | 24 |  |  | 43745.2708 | 71 | 69
2019-10-07 07:00 | 34 | 23 |  |  | 43745.2917 | 72 | 70
2019-10-07 07:30 | 32 | 22 |  |  | 43745.3125 | 73 | 72
2019-10-07 08:00 | 33 | 23 |  |  | 43745.3333 | 74 | 73
2019-10-07 08:30 | 33 | 25 |  |  | 43745.3542 | 76 | 76
2019-10-07 09:00 | 32 | 25 |  |  | 43745.375 | 76 | 76
2019-10-07 09:30 | 30 | 24 |  |  | 43745.3958 | 73 | 73
2019-10-07 10:00 | 31 | 26 |  |  | 43745.4167 | 74 | 74
2019-10-07 10:30 | 31 | 27 |  |  | 43745.4375 | 75 | 75
2019-10-07 11:00 | 31 | 27 |  |  | 43745.4583 | 74 | 74
2019-10-07 11:30 | 33 | 28 |  |  | 43745.4792 | 75 | 75
2019-10-07 12:00 | 34 | 30 |  |  | 43745.5 | 76 | 76
2019-10-07 12:30 | 38 | 33 |  |  | 43745.5208 | 82 | 81
2019-10-07 13:00 | 38 | 33 |  |  | 43745.5417 | 83 | 82
2019-10-07 13:30 | 40 | 34 |  |  | 43745.5625 | 83 | 82
2019-10-07 14:00 | 57 | 35 |  |  | 43745.5833 | 84 | 84
2019-10-07 14:30 | 66 | 38 |  |  | 43745.6042 | 90 | 89
2019-10-07 15:00 | 63 | 38 |  |  | 43745.625 | 94 | 92
2019-10-07 15:30 | 65 | 43 |  |  | 43745.6458 | 104 | 102
2019-10-07 16:00 | 66 | 44 |  |  | 43745.6667 | 104 | 102
2019-10-07 16:30 | 69 | 49 |  |  | 43745.6875 | 111 | 109
2019-10-07 17:00 | 75 | 55 |  |  | 43745.7083 | 120 | 118
2019-10-07 17:30 | 81 | 61 |  |  | 43745.7292 | 127 | 126
2019-10-07 18:00 | 86 | 65 |  |  | 43745.75 | 131 | 130
2019-10-07 18:30 | 87 | 66 |  |  | 43745.7708 | 134 | 133
2019-10-07 19:00 | 87 | 66 |  |  | 43745.7917 | 134 | 133
2019-10-07 19:30 | 85 | 63 |  |  | 43745.8125 | 130 | 129
2019-10-07 20:00 | 82 | 60 |  |  | 43745.8333 | 127 | 126
2019-10-07 20:30 | 82 | 59 |  |  | 43745.8542 | 125 | 123
2019-10-07 21:00 | 70 | 52 |  |  | 43745.875 | 115 | 115
2019-10-07 21:30 | 58 | 47 |  |  | 43745.8958 | 108 | 108
2019-10-07 22:00 | 58 | 45 |  |  | 43745.9167 | 106 | 106
2019-10-07 22:30 | 57 | 44 |  |  | 43745.9375 | 103 | 103
2019-10-07 23:00 | 56 | 43 |  |  | 43745.9583 | 99 | 98
2019-10-07 23:30 | 53 | 40 |  |  | 43745.9792 | 94 | 94
2019-10-08 | 51 | 36 |  |  | 43746 | 89 | 89
2019-10-08 00:30 | 50 | 34 |  |  | 43746.0208 | 83 | 82
2019-10-08 01:00 | 49 | 31 |  |  | 43746.0417 | 78 | 78
2019-10-08 01:30 | 49 | 32 |  |  | 43746.0625 | 77 | 76
2019-10-08 02:00 | 52 | 35 |  |  | 43746.0833 | 79 | 78
2019-10-08 02:30 | 52 | 35 |  |  | 43746.1042 | 79 | 78
2019-10-08 03:00 | 52 | 34 |  |  | 43746.125 | 77 | 76
2019-10-08 03:30 | 51 | 33 |  |  | 43746.1458 | 77 | 76
2019-10-08 04:00 | 49 | 31 |  |  | 43746.1667 | 74 | 73
2019-10-08 04:30 | 48 | 30 |  |  | 43746.1875 | 75 | 74
2019-10-08 05:00 | 47 | 30 |  |  | 43746.2083 | 77 | 76
2019-10-08 05:30 | 49 | 35 |  |  | 43746.2292 | 82 | 82
2019-10-08 06:00 | 52 | 41 |  |  | 43746.25 | 90 | 90
2019-10-08 06:30 | 55 | 46 |  |  | 43746.2708 | 102 | 102
2019-10-08 07:00 | 50 | 48 |  |  | 43746.2917 | 111 | 111
2019-10-08 07:30 | 54 | 50 |  |  | 43746.3125 | 121 | 118
2019-10-08 08:00 | 58 | 52 |  |  | 43746.3333 | 129 | 126
2019-10-08 08:30 | 59 | 54 |  |  | 43746.3542 | 134 | 131
2019-10-08 09:00 | 58 | 52 |  |  | 43746.375 | 127 | 124
2019-10-08 09:30 | 57 | 52 |  |  | 43746.3958 | 125 | 123
2019-10-08 10:00 | 55 | 51 |  |  | 43746.4167 | 125 | 123
2019-10-08 10:30 | 66 | 63 |  |  | 43746.4375 | 135 | 134
2019-10-08 11:00 | 69 | 66 |  |  | 43746.4583 | 139 | 138
2019-10-08 11:30 | 69 | 66 |  |  | 43746.4792 | 133 | 131
2019-10-08 12:00 | 65 | 62 |  |  | 43746.5 | 138 | 136
2019-10-08 12:30 | 73 | 71 |  |  | 43746.5208 | 146 | 145
2019-10-08 13:00 | 79 | 79 |  |  | 43746.5417 | 159 | 158
2019-10-08 13:30 | 83 | 83 |  |  | 43746.5625 | 159 | 158
2019-10-08 14:00 | 86 | 86 |  |  | 43746.5833 | 166 | 166
2019-10-08 14:30 | 87 | 87 |  |  | 43746.6042 | 163 | 163
2019-10-08 15:00 | 85 | 85 |  |  | 43746.625 | 164 | 164
2019-10-08 15:30 | 87 | 87 |  |  | 43746.6458 | 167 | 167
2019-10-08 16:00 | 87 | 86 |  |  | 43746.6667 | 172 | 171
2019-10-08 16:30 | 88 | 88 |  |  | 43746.6875 | 174 | 173
2019-10-08 17:00 | 89 | 89 |  |  | 43746.7083 | 174 | 172
2019-10-08 17:30 | 81 | 81 |  |  | 43746.7292 | 169 | 167
2019-10-08 18:00 | 75 | 75 |  |  | 43746.75 | 165 | 160
2019-10-08 18:30 | 72 | 72 |  |  | 43746.7708 | 161 | 155
2019-10-08 19:00 | 72 | 72 |  |  | 43746.7917 | 161 | 156
2019-10-08 19:30 | 69 | 69 |  |  | 43746.8125 | 153 | 148
2019-10-08 20:00 | 67 | 66 |  |  | 43746.8333 | 148 | 145
2019-10-08 20:30 | 69 | 69 |  |  | 43746.8542 | 146 | 142
2019-10-08 21:00 | 69 | 69 |  |  | 43746.875 | 141 | 137
2019-10-08 21:30 | 65 | 65 |  |  | 43746.8958 | 133 | 131
2019-10-08 22:00 | 63 | 62 |  |  | 43746.9167 | 126 | 125
2019-10-08 22:30 | 59 | 58 |  |  | 43746.9375 | 120 | 119
2019-10-08 23:00 | 54 | 53 |  |  | 43746.9583 | 112 | 111
2019-10-08 23:30 | 48 | 47 |  |  | 43746.9792 | 104 | 102
2019-10-09 | 42 | 42 |  |  | 43747 | 96 | 95
2019-10-09 00:30 | 39 | 38 |  |  | 43747.0208 | 89 | 88
2019-10-09 01:00 | 36 | 35 |  |  | 43747.0417 | 84 | 82
2019-10-09 01:30 | 35 | 35 |  |  | 43747.0625 | 83 | 80
2019-10-09 02:00 | 35 | 35 |  |  | 43747.0833 | 82 | 79
2019-10-09 02:30 | 35 | 35 |  |  | 43747.1042 | 81 | 78
2019-10-09 03:00 | 34 | 34 |  |  | 43747.125 | 80 | 77
2019-10-09 03:30 | 34 | 34 |  |  | 43747.1458 | 79 | 76
2019-10-09 04:00 | 33 | 33 |  |  | 43747.1667 | 78 | 75
2019-10-09 04:30 | 33 | 32 |  |  | 43747.1875 | 78 | 75
2019-10-09 05:00 | 35 | 35 |  |  | 43747.2083 | 82 | 79
2019-10-09 05:30 | 40 | 40 |  |  | 43747.2292 | 88 | 86
2019-10-09 06:00 | 44 | 44 |  |  | 43747.25 | 94 | 92
2019-10-09 06:30 | 50 | 50 |  |  | 43747.2708 | 106 | 105
2019-10-09 07:00 | 56 | 56 |  |  | 43747.2917 | 117 | 116
2019-10-09 07:30 | 59 | 58 |  |  | 43747.3125 | 123 | 123
2019-10-09 08:00 | 64 | 63 |  |  | 43747.3333 | 129 | 128
2019-10-09 08:30 | 63 | 63 |  |  | 43747.3542 | 127 | 127
2019-10-09 09:00 | 58 | 58 |  |  | 43747.375 | 123 | 123
2019-10-09 09:30 | 59 | 59 |  |  | 43747.3958 | 122 | 122
2019-10-09 10:00 | 61 | 61 |  |  | 43747.4167 | 122 | 122
2019-10-09 10:30 | 63 | 63 |  |  | 43747.4375 | 125 | 124
2019-10-09 11:00 | 60 | 59 |  |  | 43747.4583 | 122 | 121
2019-10-09 11:30 | 58 | 57 |  |  | 43747.4792 | 120 | 119
2019-10-09 12:00 | 58 | 58 |  |  | 43747.5 | 118 | 117
2019-10-09 12:30 | 58 | 58 |  |  | 43747.5208 | 116 | 116
2019-10-09 13:00 | 58 | 57 |  |  | 43747.5417 | 116 | 115
2019-10-09 13:30 | 58 | 58 |  |  | 43747.5625 | 109 | 109
2019-10-09 14:00 | 55 | 55 |  |  | 43747.5833 | 112 | 111
2019-10-09 14:30 | 55 | 55 |  |  | 43747.6042 | 117 | 116
2019-10-09 15:00 | 59 | 59 |  |  | 43747.625 | 123 | 121
2019-10-09 15:30 | 62 | 62 |  |  | 43747.6458 | 127 | 125
2019-10-09 16:00 | 66 | 66 |  |  | 43747.6667 | 133 | 131
2019-10-09 16:30 | 68 | 68 |  |  | 43747.6875 | 136 | 135
2019-10-09 17:00 | 73 | 73 |  |  | 43747.7083 | 143 | 141
2019-10-09 17:30 | 75 | 75 |  |  | 43747.7292 | 146 | 145
2019-10-09 18:00 | 74 | 74 |  |  | 43747.75 | 146 | 144
2019-10-09 18:30 | 73 | 73 |  |  | 43747.7708 | 146 | 143
2019-10-09 19:00 | 73 | 73 |  |  | 43747.7917 | 148 | 144
2019-10-09 19:30 | 70 | 70 |  |  | 43747.8125 | 142 | 139
2019-10-09 20:00 | 68 | 68 |  |  | 43747.8333 | 135 | 134
2019-10-09 20:30 | 67 | 66 |  |  | 43747.8542 | 132 | 132
2019-10-09 21:00 | 62 | 62 |  |  | 43747.875 | 126 | 125
2019-10-09 21:30 | 57 | 57 |  |  | 43747.8958 | 118 | 117
2019-10-09 22:00 | 55 | 54 |  |  | 43747.9167 | 115 | 113
2019-10-09 22:30 | 51 | 51 |  |  | 43747.9375 | 111 | 108
2019-10-09 23:00 | 48 | 48 |  |  | 43747.9583 | 106 | 103
2019-10-09 23:30 | 44 | 44 |  |  | 43747.9792 | 99 | 96
2019-10-10 | 39 | 39 |  |  | 43748 | 91 | 88
2019-10-10 00:30 | 36 | 36 |  |  | 43748.0208 | 85 | 81
2019-10-10 01:00 | 33 | 33 |  |  | 43748.0417 | 80 | 75
2019-10-10 01:30 | 31 | 31 |  |  | 43748.0625 | 76 | 72
2019-10-10 02:00 | 32 | 32 |  |  | 43748.0833 | 76 | 72
2019-10-10 02:30 | 32 | 32 |  |  | 43748.1042 | 76 | 72
2019-10-10 03:00 | 32 | 32 |  |  | 43748.125 | 74 | 71
2019-10-10 03:30 | 32 | 32 |  |  | 43748.1458 | 74 | 72
2019-10-10 04:00 | 32 | 32 |  |  | 43748.1667 | 74 | 71
2019-10-10 04:30 | 33 | 33 |  |  | 43748.1875 | 77 | 75
2019-10-10 05:00 | 38 | 38 |  |  | 43748.2083 | 83 | 81
2019-10-10 05:30 | 41 | 41 |  |  | 43748.2292 | 87 | 86
2019-10-10 06:00 | 43 | 43 |  |  | 43748.25 | 91 | 90
2019-10-10 06:30 | 48 | 47 |  |  | 43748.2708 | 101 | 101
2019-10-10 07:00 | 52 | 51 |  |  | 43748.2917 | 111 | 110
2019-10-10 07:30 | 60 | 60 |  |  | 43748.3125 | 121 | 121
2019-10-10 08:00 | 60 | 59 |  |  | 43748.3333 | 119 | 119
2019-10-10 08:30 | 59 | 59 |  |  | 43748.3542 | 118 | 118
2019-10-10 09:00 | 57 | 56 |  |  | 43748.375 | 116 | 116
2019-10-10 09:30 | 62 | 61 |  |  | 43748.3958 | 123 | 122
2019-10-10 10:00 | 66 | 65 |  |  | 43748.4167 | 129 | 129
2019-10-10 10:30 | 66 | 65 |  |  | 43748.4375 | 124 | 124
2019-10-10 11:00 | 67 | 66 |  |  | 43748.4583 | 122 | 122
2019-10-10 11:30 | 61 | 60 |  |  | 43748.4792 | 115 | 115
2019-10-10 12:00 | 59 | 58 |  |  | 43748.5 | 118 | 118
2019-10-10 12:30 | 58 | 58 |  |  | 43748.5208 | 118 | 118
2019-10-10 13:00 | 63 | 62 |  |  | 43748.5417 | 115 | 115
2019-10-10 13:30 | 63 | 62 |  |  | 43748.5625 | 121 | 121
2019-10-10 14:00 | 59 | 58 |  |  | 43748.5833 | 118 | 117
2019-10-10 14:30 | 55 | 55 |  |  | 43748.6042 | 113 | 113
2019-10-10 15:00 | 59 | 59 |  |  | 43748.625 | 117 | 117
2019-10-10 15:30 | 64 | 63 |  |  | 43748.6458 | 124 | 124
2019-10-10 16:00 | 66 | 66 |  |  | 43748.6667 | 129 | 129
2019-10-10 16:30 | 70 | 70 |  |  | 43748.6875 | 134 | 133
2019-10-10 17:00 | 72 | 72 |  |  | 43748.7083 | 139 | 138
2019-10-10 17:30 | 72 | 72 |  |  | 43748.7292 | 141 | 140
2019-10-10 18:00 | 70 | 70 |  |  | 43748.75 | 141 | 139
2019-10-10 18:30 | 72 | 72 |  |  | 43748.7708 | 143 | 141
2019-10-10 19:00 | 73 | 73 |  |  | 43748.7917 | 145 | 143
2019-10-10 19:30 | 72 | 71 |  |  | 43748.8125 | 140 | 138
2019-10-10 20:00 | 70 | 70 |  |  | 43748.8333 | 137 | 135
2019-10-10 20:30 | 67 | 67 |  |  | 43748.8542 | 134 | 132
2019-10-10 21:00 | 62 | 62 |  |  | 43748.875 | 127 | 125
2019-10-10 21:30 | 57 | 57 |  |  | 43748.8958 | 120 | 117
2019-10-10 22:00 | 54 | 54 |  |  | 43748.9167 | 117 | 113
2019-10-10 22:30 | 50 | 50 |  |  | 43748.9375 | 112 | 108
2019-10-10 23:00 | 48 | 48 |  |  | 43748.9583 | 108 | 103
2019-10-10 23:30 | 45 | 44 |  |  | 43748.9792 | 102 | 96
2019-10-11 | 39 | 39 |  |  | 43749 | 91 | 88
2019-10-11 00:30 | 38 | 37 |  |  | 43749.0208 | 88 | 84
2019-10-11 01:00 | 35 | 34 |  |  | 43749.0417 | 82 | 78
2019-10-11 01:30 | 35 | 35 |  |  | 43749.0625 | 82 | 77
2019-10-11 02:00 | 35 | 34 |  |  | 43749.0833 | 81 | 75
2019-10-11 02:30 | 33 | 33 |  |  | 43749.1042 | 77 | 73
2019-10-11 03:00 | 32 | 32 |  |  | 43749.125 | 75 | 70
2019-10-11 03:30 | 30 | 30 |  |  | 43749.1458 | 73 | 68
2019-10-11 04:00 | 29 | 29 |  |  | 43749.1667 | 72 | 68
2019-10-11 04:30 | 30 | 30 |  |  | 43749.1875 | 75 | 71
2019-10-11 05:00 | 35 | 35 |  |  | 43749.2083 | 81 | 77
2019-10-11 05:30 | 39 | 39 |  |  | 43749.2292 | 86 | 84
2019-10-11 06:00 | 43 | 43 |  |  | 43749.25 | 93 | 91
2019-10-11 06:30 | 48 | 48 |  |  | 43749.2708 | 102 | 100
2019-10-11 07:00 | 51 | 51 |  |  | 43749.2917 | 110 | 109
2019-10-11 07:30 | 58 | 57 |  |  | 43749.3125 | 120 | 120
2019-10-11 08:00 | 58 | 57 |  |  | 43749.3333 | 118 | 118
2019-10-11 08:30 | 58 | 57 |  |  | 43749.3542 | 124 | 124
2019-10-11 09:00 | 55 | 54 |  |  | 43749.375 | 118 | 118
2019-10-11 09:30 | 54 | 52 |  |  | 43749.3958 | 112 | 111
2019-10-11 10:00 | 57 | 56 |  |  | 43749.4167 | 114 | 114
2019-10-11 10:30 | 65 | 64 |  |  | 43749.4375 | 125 | 125
2019-10-11 11:00 | 64 | 62 |  |  | 43749.4583 | 129 | 128
2019-10-11 11:30 | 65 | 63 |  |  | 43749.4792 | 130 | 130
2019-10-11 12:00 | 58 | 55 |  |  | 43749.5 | 112 | 112
2019-10-11 12:30 | 62 | 59 |  |  | 43749.5208 | 115 | 114
2019-10-11 13:00 | 53 | 49 |  |  | 43749.5417 | 117 | 116
2019-10-11 13:30 | 52 | 47 |  |  | 43749.5625 | 115 | 114
2019-10-11 14:00 | 59 | 54 |  |  | 43749.5833 | 117 | 115
2019-10-11 14:30 | 55 | 51 |  |  | 43749.6042 | 121 | 120
2019-10-11 15:00 | 72 | 69 |  |  | 43749.625 | 134 | 133
2019-10-11 15:30 | 78 | 74 |  |  | 43749.6458 | 139 | 138
2019-10-11 16:00 | 79 | 75 |  |  | 43749.6667 | 140 | 138
2019-10-11 16:30 | 79 | 75 |  |  | 43749.6875 | 140 | 138
2019-10-11 17:00 | 77 | 73 |  |  | 43749.7083 | 142 | 140
2019-10-11 17:30 | 76 | 70 |  |  | 43749.7292 | 140 | 137
2019-10-11 18:00 | 75 | 69 |  |  | 43749.75 | 138 | 134
2019-10-11 18:30 | 74 | 68 |  |  | 43749.7708 | 136 | 132
2019-10-11 19:00 | 75 | 70 |  |  | 43749.7917 | 137 | 133
2019-10-11 19:30 | 72 | 67 |  |  | 43749.8125 | 132 | 129
2019-10-11 20:00 | 70 | 65 |  |  | 43749.8333 | 129 | 126
2019-10-11 20:30 | 69 | 64 |  |  | 43749.8542 | 128 | 125
2019-10-11 21:00 | 66 | 60 |  |  | 43749.875 | 122 | 118
2019-10-11 21:30 | 63 | 57 |  |  | 43749.8958 | 117 | 113
2019-10-11 22:00 | 60 | 54 |  |  | 43749.9167 | 113 | 109
2019-10-11 22:30 | 59 | 53 |  |  | 43749.9375 | 111 | 106
2019-10-11 23:00 | 58 | 50 |  |  | 43749.9583 | 106 | 101
2019-10-11 23:30 | 53 | 46 |  |  | 43749.9792 | 99 | 94
2019-10-12 | 50 | 40 |  |  | 43750 | 92 | 87
2019-10-12 00:30 | 49 | 39 |  |  | 43750.0208 | 87 | 83
2019-10-12 01:00 | 46 | 35 |  |  | 43750.0417 | 81 | 77
2019-10-12 01:30 | 45 | 33 |  |  | 43750.0625 | 77 | 73
2019-10-12 02:00 | 44 | 31 |  |  | 43750.0833 | 75 | 70
2019-10-12 02:30 | 44 | 31 |  |  | 43750.1042 | 73 | 68
2019-10-12 03:00 | 45 | 32 |  |  | 43750.125 | 74 | 69
2019-10-12 03:30 | 46 | 33 |  |  | 43750.1458 | 75 | 69
2019-10-12 04:00 | 45 | 31 |  |  | 43750.1667 | 73 | 68
2019-10-12 04:30 | 45 | 31 |  |  | 43750.1875 | 74 | 68
2019-10-12 05:00 | 45 | 32 |  |  | 43750.2083 | 73 | 68
2019-10-12 05:30 | 44 | 31 |  |  | 43750.2292 | 74 | 69
2019-10-12 06:00 | 45 | 32 |  |  | 43750.25 | 76 | 71
2019-10-12 06:30 | 46 | 34 |  |  | 43750.2708 | 80 | 76
2019-10-12 07:00 | 48 | 38 |  |  | 43750.2917 | 85 | 82
2019-10-12 07:30 | 49 | 42 |  |  | 43750.3125 | 92 | 89
2019-10-12 08:00 | 51 | 44 |  |  | 43750.3333 | 95 | 93
2019-10-12 08:30 | 50 | 45 |  |  | 43750.3542 | 98 | 97
2019-10-12 09:00 | 53 | 48 |  |  | 43750.375 | 103 | 102
2019-10-12 09:30 | 54 | 49 |  |  | 43750.3958 | 106 | 105
2019-10-12 10:00 | 57 | 52 |  |  | 43750.4167 | 110 | 109
2019-10-12 10:30 | 61 | 57 |  |  | 43750.4375 | 112 | 111
2019-10-12 11:00 | 63 | 59 |  |  | 43750.4583 | 115 | 114
2019-10-12 11:30 | 63 | 58 |  |  | 43750.4792 | 111 | 110
2019-10-12 12:00 | 62 | 57 |  |  | 43750.5 | 106 | 105
2019-10-12 12:30 | 54 | 49 |  |  | 43750.5208 | 94 | 93
2019-10-12 13:00 | 39 | 28 |  |  | 43750.5417 | 75 | 73
2019-10-12 13:30 | 33 | 19 |  |  | 43750.5625 | 64 | 61
2019-10-12 14:00 | 34 | 21 |  |  | 43750.5833 | 62 | 59
2019-10-12 14:30 | 39 | 29 |  |  | 43750.6042 | 69 | 66
2019-10-12 15:00 | 42 | 33 |  |  | 43750.625 | 78 | 76
2019-10-12 15:30 | 39 | 30 |  |  | 43750.6458 | 75 | 73
2019-10-12 16:00 | 45 | 37 |  |  | 43750.6667 | 84 | 82
2019-10-12 16:30 | 48 | 41 |  |  | 43750.6875 | 90 | 88
2019-10-12 17:00 | 55 | 49 |  |  | 43750.7083 | 101 | 99
2019-10-12 17:30 | 60 | 55 |  |  | 43750.7292 | 107 | 106
2019-10-12 18:00 | 62 | 57 |  |  | 43750.75 | 110 | 108
2019-10-12 18:30 | 66 | 61 |  |  | 43750.7708 | 117 | 115
2019-10-12 19:00 | 68 | 63 |  |  | 43750.7917 | 121 | 119
2019-10-12 19:30 | 68 | 62 |  |  | 43750.8125 | 118 | 115
2019-10-12 20:00 | 67 | 62 |  |  | 43750.8333 | 116 | 113
2019-10-12 20:30 | 66 | 60 |  |  | 43750.8542 | 115 | 112
2019-10-12 21:00 | 63 | 57 |  |  | 43750.875 | 110 | 107
2019-10-12 21:30 | 61 | 54 |  |  | 43750.8958 | 106 | 103
2019-10-12 22:00 | 61 | 55 |  |  | 43750.9167 | 106 | 103
2019-10-12 22:30 | 60 | 53 |  |  | 43750.9375 | 105 | 102
2019-10-12 23:00 | 60 | 52 |  |  | 43750.9583 | 102 | 98
2019-10-12 23:30 | 57 | 49 |  |  | 43750.9792 | 97 | 93
2019-10-13 | 54 | 44 |  |  | 43751 | 91 | 86
2019-10-13 00:30 | 51 | 39 |  |  | 43751.0208 | 84 | 79
2019-10-13 01:00 | 47 | 35 |  |  | 43751.0417 | 79 | 72
2019-10-13 01:30 | 44 | 33 |  |  | 43751.0625 | 73 | 68
2019-10-13 02:00 | 43 | 31 |  |  | 43751.0833 | 71 | 65
2019-10-13 02:30 | 43 | 31 |  |  | 43751.1042 | 69 | 64
2019-10-13 03:00 | 45 | 33 |  |  | 43751.125 | 69 | 64
2019-10-13 03:30 | 44 | 32 |  |  | 43751.1458 | 70 | 64
2019-10-13 04:00 | 42 | 30 |  |  | 43751.1667 | 68 | 62
2019-10-13 04:30 | 43 | 31 |  |  | 43751.1875 | 69 | 64
2019-10-13 05:00 | 43 | 31 |  |  | 43751.2083 | 70 | 64
2019-10-13 05:30 | 42 | 30 |  |  | 43751.2292 | 69 | 64
2019-10-13 06:00 | 40 | 29 |  |  | 43751.25 | 68 | 64
2019-10-13 06:30 | 38 | 26 |  |  | 43751.2708 | 66 | 62
2019-10-13 07:00 | 36 | 23 |  |  | 43751.2917 | 64 | 60
2019-10-13 07:30 | 35 | 23 |  |  | 43751.3125 | 63 | 60
2019-10-13 08:00 | 34 | 22 |  |  | 43751.3333 | 61 | 58
2019-10-13 08:30 | 33 | 21 |  |  | 43751.3542 | 60 | 57
2019-10-13 09:00 | 32 | 20 |  |  | 43751.375 | 59 | 57
2019-10-13 09:30 | 30 | 19 |  |  | 43751.3958 | 58 | 56
2019-10-13 10:00 | 30 | 19 |  |  | 43751.4167 | 56 | 54
2019-10-13 10:30 | 29 | 19 |  |  | 43751.4375 | 55 | 53
2019-10-13 11:00 | 29 | 18 |  |  | 43751.4583 | 54 | 52
2019-10-13 11:30 | 28 | 19 |  |  | 43751.4792 | 56 | 55
2019-10-13 12:00 | 31 | 23 |  |  | 43751.5 | 64 | 63
2019-10-13 12:30 | 32 | 25 |  |  | 43751.5208 | 67 | 66
2019-10-13 13:00 | 33 | 25 |  |  | 43751.5417 | 69 | 68
2019-10-13 13:30 | 37 | 31 |  |  | 43751.5625 | 75 | 74
2019-10-13 14:00 | 39 | 33 |  |  | 43751.5833 | 77 | 76
2019-10-13 14:30 | 40 | 34 |  |  | 43751.6042 | 78 | 77
2019-10-13 15:00 | 39 | 33 |  |  | 43751.625 | 75 | 74
2019-10-13 15:30 | 43 | 37 |  |  | 43751.6458 | 76 | 76
2019-10-13 16:00 | 47 | 42 |  |  | 43751.6667 | 86 | 85
2019-10-13 16:30 | 51 | 46 |  |  | 43751.6875 | 92 | 91
2019-10-13 17:00 | 57 | 53 |  |  | 43751.7083 | 101 | 100
2019-10-13 17:30 | 59 | 55 |  |  | 43751.7292 | 106 | 105
2019-10-13 18:00 | 62 | 58 |  |  | 43751.75 | 111 | 110
2019-10-13 18:30 | 66 | 61 |  |  | 43751.7708 | 118 | 117
2019-10-13 19:00 | 68 | 63 |  |  | 43751.7917 | 122 | 121
2019-10-13 19:30 | 64 | 61 |  |  | 43751.8125 | 119 | 118
2019-10-13 20:00 | 65 | 61 |  |  | 43751.8333 | 117 | 116
2019-10-13 20:30 | 63 | 58 |  |  | 43751.8542 | 115 | 114
2019-10-13 21:00 | 60 | 55 |  |  | 43751.875 | 110 | 108
2019-10-13 21:30 | 57 | 52 |  |  | 43751.8958 | 105 | 103
2019-10-13 22:00 | 55 | 49 |  |  | 43751.9167 | 102 | 100
2019-10-13 22:30 | 55 | 48 |  |  | 43751.9375 | 101 | 99
2019-10-13 23:00 | 53 | 46 |  |  | 43751.9583 | 96 | 94
2019-10-13 23:30 | 50 | 42 |  |  | 43751.9792 | 92 | 89
2019-10-14 | 46 | 38 |  |  | 43752 | 85 | 82
2019-10-14 00:30 | 44 | 35 |  |  | 43752.0208 | 78 | 75
2019-10-14 01:00 | 41 | 32 |  |  | 43752.0417 | 72 | 70
2019-10-14 01:30 | 42 | 32 |  |  | 43752.0625 | 71 | 68
2019-10-14 02:00 | 41 | 32 |  |  | 43752.0833 | 69 | 66
2019-10-14 02:30 | 41 | 31 |  |  | 43752.1042 | 67 | 64
2019-10-14 03:00 | 40 | 29 |  |  | 43752.125 | 66 | 63
2019-10-14 03:30 | 39 | 28 |  |  | 43752.1458 | 66 | 63
2019-10-14 04:00 | 38 | 28 |  |  | 43752.1667 | 66 | 62
2019-10-14 04:30 | 39 | 28 |  |  | 43752.1875 | 68 | 65
2019-10-14 05:00 | 41 | 32 |  |  | 43752.2083 | 73 | 70
2019-10-14 05:30 | 44 | 36 |  |  | 43752.2292 | 79 | 76
2019-10-14 06:00 | 46 | 40 |  |  | 43752.25 | 84 | 83
2019-10-14 06:30 | 48 | 44 |  |  | 43752.2708 | 96 | 95
2019-10-14 07:00 | 52 | 50 |  |  | 43752.2917 | 105 | 104
2019-10-14 07:30 | 58 | 55 |  |  | 43752.3125 | 115 | 115
2019-10-14 08:00 | 57 | 55 |  |  | 43752.3333 | 114 | 114
2019-10-14 08:30 | 57 | 55 |  |  | 43752.3542 | 113 | 113
2019-10-14 09:00 | 55 | 53 |  |  | 43752.375 | 112 | 112
2019-10-14 09:30 | 54 | 51 |  |  | 43752.3958 | 110 | 110
2019-10-14 10:00 | 57 | 54 |  |  | 43752.4167 | 110 | 110
2019-10-14 10:30 | 58 | 56 |  |  | 43752.4375 | 112 | 112
2019-10-14 11:00 | 60 | 57 |  |  | 43752.4583 | 113 | 113
2019-10-14 11:30 | 58 | 55 |  |  | 43752.4792 | 112 | 112
2019-10-14 12:00 | 58 | 54 |  |  | 43752.5 | 111 | 111
2019-10-14 12:30 | 57 | 52 |  |  | 43752.5208 | 108 | 108
2019-10-14 13:00 | 57 | 53 |  |  | 43752.5417 | 106 | 106
2019-10-14 13:30 | 58 | 54 |  |  | 43752.5625 | 106 | 105
2019-10-14 14:00 | 57 | 53 |  |  | 43752.5833 | 106 | 106
2019-10-14 14:30 | 58 | 54 |  |  | 43752.6042 | 109 | 109
2019-10-14 15:00 | 60 | 56 |  |  | 43752.625 | 112 | 112
2019-10-14 15:30 | 64 | 61 |  |  | 43752.6458 | 119 | 118
2019-10-14 16:00 | 69 | 65 |  |  | 43752.6667 | 125 | 125
2019-10-14 16:30 | 74 | 70 |  |  | 43752.6875 | 133 | 132
2019-10-14 17:00 | 81 | 74 |  |  | 43752.7083 | 141 | 138
2019-10-14 17:30 | 84 | 76 |  |  | 43752.7292 | 144 | 140
2019-10-14 18:00 | 84 | 76 |  |  | 43752.75 | 144 | 140
2019-10-14 18:30 | 86 | 78 |  |  | 43752.7708 | 146 | 141
2019-10-14 19:00 | 87 | 79 |  |  | 43752.7917 | 147 | 143
2019-10-14 19:30 | 84 | 76 |  |  | 43752.8125 | 142 | 137
2019-10-14 20:00 | 83 | 75 |  |  | 43752.8333 | 138 | 133
2019-10-14 20:30 | 81 | 73 |  |  | 43752.8542 | 135 | 131
2019-10-14 21:00 | 76 | 70 |  |  | 43752.875 | 127 | 124
2019-10-14 21:30 | 72 | 65 |  |  | 43752.8958 | 120 | 117
2019-10-14 22:00 | 69 | 63 |  |  | 43752.9167 | 117 | 114
2019-10-14 22:30 | 67 | 60 |  |  | 43752.9375 | 112 | 109
2019-10-14 23:00 | 66 | 58 |  |  | 43752.9583 | 107 | 104
2019-10-14 23:30 | 61 | 52 |  |  | 43752.9792 | 101 | 97
2019-10-15 | 56 | 45 |  |  | 43753 | 94 | 89
2019-10-15 00:30 | 52 | 42 |  |  | 43753.0208 | 86 | 81
2019-10-15 01:00 | 49 | 37 |  |  | 43753.0417 | 79 | 75
2019-10-15 01:30 | 47 | 35 |  |  | 43753.0625 | 76 | 71
2019-10-15 02:00 | 43 | 33 |  |  | 43753.0833 | 72 | 69
2019-10-15 02:30 | 43 | 33 |  |  | 43753.1042 | 72 | 68
2019-10-15 03:00 | 44 | 34 |  |  | 43753.125 | 71 | 67
2019-10-15 03:30 | 42 | 34 |  |  | 43753.1458 | 71 | 68
2019-10-15 04:00 | 41 | 33 |  |  | 43753.1667 | 70 | 68
2019-10-15 04:30 | 43 | 35 |  |  | 43753.1875 | 72 | 70
2019-10-15 05:00 | 45 | 38 |  |  | 43753.2083 | 76 | 74
2019-10-15 05:30 | 49 | 43 |  |  | 43753.2292 | 83 | 82
2019-10-15 06:00 | 52 | 46 |  |  | 43753.25 | 90 | 89
2019-10-15 06:30 | 58 | 54 |  |  | 43753.2708 | 105 | 104
2019-10-15 07:00 | 64 | 61 |  |  | 43753.2917 | 117 | 116
2019-10-15 07:30 | 74 | 72 |  |  | 43753.3125 | 131 | 130
2019-10-15 08:00 | 78 | 75 |  |  | 43753.3333 | 137 | 137
2019-10-15 08:30 | 78 | 75 |  |  | 43753.3542 | 137 | 137
2019-10-15 09:00 | 73 | 70 |  |  | 43753.375 | 136 | 135
2019-10-15 09:30 | 72 | 68 |  |  | 43753.3958 | 131 | 131
2019-10-15 10:00 | 73 | 70 |  |  | 43753.4167 | 128 | 128
2019-10-15 10:30 | 73 | 71 |  |  | 43753.4375 | 131 | 131
2019-10-15 11:00 | 76 | 73 |  |  | 43753.4583 | 138 | 138
2019-10-15 11:30 | 79 | 76 |  |  | 43753.4792 | 138 | 138
2019-10-15 12:00 | 65 | 61 |  |  | 43753.5 | 121 | 121
2019-10-15 12:30 | 53 | 45 |  |  | 43753.5208 | 109 | 107
2019-10-15 13:00 | 69 | 63 |  |  | 43753.5417 | 125 | 124
2019-10-15 13:30 | 61 | 56 |  |  | 43753.5625 | 118 | 117
2019-10-15 14:00 | 55 | 50 |  |  | 43753.5833 | 111 | 110
2019-10-15 14:30 | 59 | 54 |  |  | 43753.6042 | 117 | 116
2019-10-15 15:00 | 56 | 51 |  |  | 43753.625 | 117 | 116
2019-10-15 15:30 | 59 | 54 |  |  | 43753.6458 | 119 | 118
2019-10-15 16:00 | 63 | 58 |  |  | 43753.6667 | 126 | 125
2019-10-15 16:30 | 68 | 63 |  |  | 43753.6875 | 133 | 132
2019-10-15 17:00 | 75 | 70 |  |  | 43753.7083 | 141 | 140
2019-10-15 17:30 | 79 | 74 |  |  | 43753.7292 | 146 | 144
2019-10-15 18:00 | 83 | 78 |  |  | 43753.75 | 148 | 146
2019-10-15 18:30 | 86 | 80 |  |  | 43753.7708 | 150 | 147
2019-10-15 19:00 | 90 | 83 |  |  | 43753.7917 | 154 | 150
2019-10-15 19:30 | 88 | 80 |  |  | 43753.8125 | 148 | 144
2019-10-15 20:00 | 85 | 77 |  |  | 43753.8333 | 143 | 139
2019-10-15 20:30 | 82 | 75 |  |  | 43753.8542 | 140 | 136
2019-10-15 21:00 | 78 | 71 |  |  | 43753.875 | 133 | 129
2019-10-15 21:30 | 74 | 66 |  |  | 43753.8958 | 126 | 122
2019-10-15 22:00 | 67 | 60 |  |  | 43753.9167 | 119 | 117
2019-10-15 22:30 | 64 | 57 |  |  | 43753.9375 | 115 | 113
2019-10-15 23:00 | 63 | 55 |  |  | 43753.9583 | 110 | 108
2019-10-15 23:30 | 58 | 50 |  |  | 43753.9792 | 103 | 101
2019-10-16 | 54 | 44 |  |  | 43754 | 95 | 92
2019-10-16 00:30 | 51 | 41 |  |  | 43754.0208 | 88 | 85
2019-10-16 01:00 | 46 | 39 |  |  | 43754.0417 | 85 | 81
2019-10-16 01:30 | 41 | 36 |  |  | 43754.0625 | 84 | 78
2019-10-16 02:00 | 40 | 35 |  |  | 43754.0833 | 82 | 75
2019-10-16 02:30 | 39 | 34 |  |  | 43754.1042 | 80 | 73
2019-10-16 03:00 | 38 | 33 |  |  | 43754.125 | 79 | 71
2019-10-16 03:30 | 38 | 32 |  |  | 43754.1458 | 80 | 72
2019-10-16 04:00 | 37 | 31 |  |  | 43754.1667 | 80 | 73
2019-10-16 04:30 | 38 | 33 |  |  | 43754.1875 | 82 | 75
2019-10-16 05:00 | 40 | 36 |  |  | 43754.2083 | 85 | 79
2019-10-16 05:30 | 43 | 39 |  |  | 43754.2292 | 90 | 85
2019-10-16 06:00 | 46 | 42 |  |  | 43754.25 | 96 | 91
2019-10-16 06:30 | 49 | 48 |  |  | 43754.2708 | 106 | 104
2019-10-16 07:00 | 55 | 50 |  |  | 43754.2917 | 115 | 115
2019-10-16 07:30 | 60 | 54 |  |  | 43754.3125 | 123 | 122
2019-10-16 08:00 | 63 | 58 |  |  | 43754.3333 | 128 | 128
2019-10-16 08:30 | 62 | 57 |  |  | 43754.3542 | 130 | 130
2019-10-16 09:00 | 59 | 54 |  |  | 43754.375 | 122 | 122
2019-10-16 09:30 | 63 | 59 |  |  | 43754.3958 | 126 | 126
2019-10-16 10:00 | 63 | 58 |  |  | 43754.4167 | 125 | 124
2019-10-16 10:30 | 61 | 56 |  |  | 43754.4375 | 121 | 121
2019-10-16 11:00 | 61 | 57 |  |  | 43754.4583 | 123 | 123
2019-10-16 11:30 | 59 | 55 |  |  | 43754.4792 | 121 | 121
2019-10-16 12:00 | 60 | 54 |  |  | 43754.5 | 120 | 119
2019-10-16 12:30 | 59 | 53 |  |  | 43754.5208 | 118 | 117
2019-10-16 13:00 | 56 | 50 |  |  | 43754.5417 | 114 | 114
2019-10-16 13:30 | 56 | 51 |  |  | 43754.5625 | 115 | 115
2019-10-16 14:00 | 59 | 55 |  |  | 43754.5833 | 119 | 119
2019-10-16 14:30 | 59 | 56 |  |  | 43754.6042 | 122 | 122
2019-10-16 15:00 | 62 | 58 |  |  | 43754.625 | 127 | 127
2019-10-16 15:30 | 63 | 59 |  |  | 43754.6458 | 129 | 129
2019-10-16 16:00 | 68 | 63 |  |  | 43754.6667 | 135 | 135
2019-10-16 16:30 | 72 | 67 |  |  | 43754.6875 | 141 | 140
2019-10-16 17:00 | 75 | 70 |  |  | 43754.7083 | 146 | 146
2019-10-16 17:30 | 79 | 73 |  |  | 43754.7292 | 148 | 147
2019-10-16 18:00 | 82 | 77 |  |  | 43754.75 | 151 | 148
2019-10-16 18:30 | 82 | 75 |  |  | 43754.7708 | 149 | 146
2019-10-16 19:00 | 83 | 77 |  |  | 43754.7917 | 151 | 148
2019-10-16 19:30 | 82 | 75 |  |  | 43754.8125 | 147 | 143
2019-10-16 20:00 | 79 | 72 |  |  | 43754.8333 | 141 | 138
2019-10-16 20:30 | 74 | 71 |  |  | 43754.8542 | 134 | 133
2019-10-16 21:00 | 72 | 67 |  |  | 43754.875 | 128 | 127
2019-10-16 21:30 | 66 | 61 |  |  | 43754.8958 | 121 | 119
2019-10-16 22:00 | 63 | 57 |  |  | 43754.9167 | 116 | 114
2019-10-16 22:30 | 63 | 56 |  |  | 43754.9375 | 115 | 111
2019-10-16 23:00 | 60 | 52 |  |  | 43754.9583 | 108 | 105
2019-10-16 23:30 | 56 | 49 |  |  | 43754.9792 | 102 | 100
2019-10-17 | 51 | 43 |  |  | 43755 | 95 | 93
2019-10-17 00:30 | 50 | 40 |  |  | 43755.0208 | 90 | 86
2019-10-17 01:00 | 47 | 37 |  |  | 43755.0417 | 84 | 81
2019-10-17 01:30 | 46 | 37 |  |  | 43755.0625 | 80 | 78
2019-10-17 02:00 | 46 | 38 |  |  | 43755.0833 | 80 | 78
2019-10-17 02:30 | 47 | 39 |  |  | 43755.1042 | 78 | 76
2019-10-17 03:00 | 46 | 37 |  |  | 43755.125 | 76 | 74
2019-10-17 03:30 | 46 | 37 |  |  | 43755.1458 | 76 | 74
2019-10-17 04:00 | 45 | 36 |  |  | 43755.1667 | 75 | 73
2019-10-17 04:30 | 45 | 35 |  |  | 43755.1875 | 76 | 74
2019-10-17 05:00 | 44 | 36 |  |  | 43755.2083 | 80 | 78
2019-10-17 05:30 | 48 | 40 |  |  | 43755.2292 | 87 | 85
2019-10-17 06:00 | 49 | 43 |  |  | 43755.25 | 92 | 90
2019-10-17 06:30 | 50 | 46 |  |  | 43755.2708 | 103 | 102
2019-10-17 07:00 | 51 | 48 |  |  | 43755.2917 | 108 | 107
2019-10-17 07:30 | 57 | 55 |  |  | 43755.3125 | 116 | 116
2019-10-17 08:00 | 57 | 55 |  |  | 43755.3333 | 120 | 120
2019-10-17 08:30 | 55 | 52 |  |  | 43755.3542 | 119 | 118
2019-10-17 09:00 | 59 | 55 |  |  | 43755.375 | 122 | 121
2019-10-17 09:30 | 58 | 55 |  |  | 43755.3958 | 120 | 120
2019-10-17 10:00 | 61 | 58 |  |  | 43755.4167 | 119 | 118
2019-10-17 10:30 | 64 | 61 |  |  | 43755.4375 | 126 | 126
2019-10-17 11:00 | 60 | 58 |  |  | 43755.4583 | 122 | 122
2019-10-17 11:30 | 60 | 58 |  |  | 43755.4792 | 122 | 122
2019-10-17 12:00 | 60 | 58 |  |  | 43755.5 | 122 | 121
2019-10-17 12:30 | 57 | 54 |  |  | 43755.5208 | 120 | 120
2019-10-17 13:00 | 60 | 58 |  |  | 43755.5417 | 123 | 123
2019-10-17 13:30 | 64 | 61 |  |  | 43755.5625 | 125 | 125
2019-10-17 14:00 | 64 | 61 |  |  | 43755.5833 | 127 | 127
2019-10-17 14:30 | 65 | 62 |  |  | 43755.6042 | 124 | 124
2019-10-17 15:00 | 67 | 64 |  |  | 43755.625 | 131 | 131
2019-10-17 15:30 | 72 | 69 |  |  | 43755.6458 | 141 | 141
2019-10-17 16:00 | 80 | 76 |  |  | 43755.6667 | 149 | 149
2019-10-17 16:30 | 91 | 88 |  |  | 43755.6875 | 161 | 161
2019-10-17 17:00 | 92 | 89 |  |  | 43755.7083 | 164 | 163
2019-10-17 17:30 | 90 | 85 |  |  | 43755.7292 | 156 | 154
2019-10-17 18:00 | 88 | 83 |  |  | 43755.75 | 153 | 150
2019-10-17 18:30 | 89 | 84 |  |  | 43755.7708 | 152 | 150
2019-10-17 19:00 | 90 | 85 |  |  | 43755.7917 | 154 | 152
2019-10-17 19:30 | 88 | 82 |  |  | 43755.8125 | 150 | 147
2019-10-17 20:00 | 85 | 79 |  |  | 43755.8333 | 147 | 144
2019-10-17 20:30 | 82 | 78 |  |  | 43755.8542 | 144 | 142
2019-10-17 21:00 | 78 | 74 |  |  | 43755.875 | 134 | 133
2019-10-17 21:30 | 71 | 65 |  |  | 43755.8958 | 124 | 122
2019-10-17 22:00 | 68 | 62 |  |  | 43755.9167 | 118 | 116
2019-10-17 22:30 | 66 | 60 |  |  | 43755.9375 | 115 | 114
2019-10-17 23:00 | 63 | 58 |  |  | 43755.9583 | 108 | 107
2019-10-17 23:30 | 58 | 52 |  |  | 43755.9792 | 102 | 101
2019-10-18 | 57 | 51 |  |  | 43756 | 99 | 97
2019-10-18 00:30 | 53 | 48 |  |  | 43756.0208 | 92 | 90
2019-10-18 01:00 | 54 | 44 |  |  | 43756.0417 | 86 | 84
2019-10-18 01:30 | 54 | 44 |  |  | 43756.0625 | 85 | 83
2019-10-18 02:00 | 54 | 43 |  |  | 43756.0833 | 83 | 80
2019-10-18 02:30 | 53 | 43 |  |  | 43756.1042 | 82 | 79
2019-10-18 03:00 | 53 | 42 |  |  | 43756.125 | 82 | 79
2019-10-18 03:30 | 53 | 43 |  |  | 43756.1458 | 82 | 79
2019-10-18 04:00 | 53 | 42 |  |  | 43756.1667 | 81 | 78
2019-10-18 04:30 | 52 | 41 |  |  | 43756.1875 | 82 | 79
2019-10-18 05:00 | 51 | 40 |  |  | 43756.2083 | 82 | 80
2019-10-18 05:30 | 54 | 44 |  |  | 43756.2292 | 88 | 86
2019-10-18 06:00 | 55 | 46 |  |  | 43756.25 | 92 | 90
2019-10-18 06:30 | 52 | 46 |  |  | 43756.2708 | 98 | 98
2019-10-18 07:00 | 56 | 52 |  |  | 43756.2917 | 106 | 106
2019-10-18 07:30 | 60 | 56 |  |  | 43756.3125 | 117 | 117
2019-10-18 08:00 | 61 | 57 |  |  | 43756.3333 | 121 | 121
2019-10-18 08:30 | 68 | 64 |  |  | 43756.3542 | 131 | 131
2019-10-18 09:00 | 64 | 56 |  |  | 43756.375 | 123 | 122
2019-10-18 09:30 | 63 | 55 |  |  | 43756.3958 | 122 | 120
2019-10-18 10:00 | 63 | 55 |  |  | 43756.4167 | 119 | 117
2019-10-18 10:30 | 65 | 58 |  |  | 43756.4375 | 122 | 120
2019-10-18 11:00 | 67 | 60 |  |  | 43756.4583 | 125 | 124
2019-10-18 11:30 | 68 | 61 |  |  | 43756.4792 | 125 | 124
2019-10-18 12:00 | 68 | 61 |  |  | 43756.5 | 123 | 122
2019-10-18 12:30 | 67 | 60 |  |  | 43756.5208 | 122 | 121
2019-10-18 13:00 | 68 | 60 |  |  | 43756.5417 | 123 | 122
2019-10-18 13:30 | 68 | 60 |  |  | 43756.5625 | 123 | 122
2019-10-18 14:00 | 67 | 58 |  |  | 43756.5833 | 121 | 119
2019-10-18 14:30 | 69 | 59 |  |  | 43756.6042 | 122 | 120
2019-10-18 15:00 | 67 | 59 |  |  | 43756.625 | 122 | 120
2019-10-18 15:30 | 68 | 61 |  |  | 43756.6458 | 126 | 124
2019-10-18 16:00 | 71 | 64 |  |  | 43756.6667 | 130 | 128
2019-10-18 16:30 | 75 | 67 |  |  | 43756.6875 | 137 | 134
2019-10-18 17:00 | 79 | 69 |  |  | 43756.7083 | 142 | 138
2019-10-18 17:30 | 80 | 70 |  |  | 43756.7292 | 143 | 138
2019-10-18 18:00 | 79 | 68 |  |  | 43756.75 | 140 | 135
2019-10-18 18:30 | 80 | 67 |  |  | 43756.7708 | 139 | 133
2019-10-18 19:00 | 82 | 69 |  |  | 43756.7917 | 141 | 136
2019-10-18 19:30 | 78 | 66 |  |  | 43756.8125 | 137 | 131
2019-10-18 20:00 | 73 | 62 |  |  | 43756.8333 | 130 | 126
2019-10-18 20:30 | 72 | 61 |  |  | 43756.8542 | 127 | 123
2019-10-18 21:00 | 70 | 58 |  |  | 43756.875 | 121 | 117
2019-10-18 21:30 | 69 | 56 |  |  | 43756.8958 | 116 | 111
2019-10-18 22:00 | 66 | 53 |  |  | 43756.9167 | 113 | 109
2019-10-18 22:30 | 65 | 52 |  |  | 43756.9375 | 111 | 106
2019-10-18 23:00 | 62 | 48 |  |  | 43756.9583 | 105 | 100
2019-10-18 23:30 | 53 | 43 |  |  | 43756.9792 | 94 | 93
2019-10-19 | 47 | 38 |  |  | 43757 | 87 | 86
2019-10-19 00:30 | 44 | 36 |  |  | 43757.0208 | 81 | 81
2019-10-19 01:00 | 44 | 38 |  |  | 43757.0417 | 80 | 79
2019-10-19 01:30 | 43 | 35 |  |  | 43757.0625 | 76 | 76
2019-10-19 02:00 | 45 | 37 |  |  | 43757.0833 | 77 | 76
2019-10-19 02:30 | 47 | 39 |  |  | 43757.1042 | 78 | 77
2019-10-19 03:00 | 48 | 40 |  |  | 43757.125 | 79 | 77
2019-10-19 03:30 | 49 | 41 |  |  | 43757.1458 | 80 | 79
2019-10-19 04:00 | 49 | 42 |  |  | 43757.1667 | 81 | 80
2019-10-19 04:30 | 49 | 42 |  |  | 43757.1875 | 80 | 79
2019-10-19 05:00 | 48 | 40 |  |  | 43757.2083 | 79 | 78
2019-10-19 05:30 | 48 | 40 |  |  | 43757.2292 | 81 | 79
2019-10-19 06:00 | 46 | 38 |  |  | 43757.25 | 79 | 78
2019-10-19 06:30 | 44 | 35 |  |  | 43757.2708 | 80 | 79
2019-10-19 07:00 | 43 | 35 |  |  | 43757.2917 | 81 | 80
2019-10-19 07:30 | 43 | 35 |  |  | 43757.3125 | 84 | 84
2019-10-19 08:00 | 45 | 37 |  |  | 43757.3333 | 90 | 90
2019-10-19 08:30 | 48 | 40 |  |  | 43757.3542 | 94 | 93
2019-10-19 09:00 | 56 | 50 |  |  | 43757.375 | 99 | 98
2019-10-19 09:30 | 65 | 58 |  |  | 43757.3958 | 113 | 112
2019-10-19 10:00 | 66 | 58 |  |  | 43757.4167 | 116 | 115
2019-10-19 10:30 | 60 | 52 |  |  | 43757.4375 | 114 | 112
2019-10-19 11:00 | 58 | 49 |  |  | 43757.4583 | 101 | 100
2019-10-19 11:30 | 67 | 60 |  |  | 43757.4792 | 113 | 112
2019-10-19 12:00 | 70 | 64 |  |  | 43757.5 | 118 | 117
2019-10-19 12:30 | 63 | 56 |  |  | 43757.5208 | 112 | 111
2019-10-19 13:00 | 46 | 38 |  |  | 43757.5417 | 88 | 87
2019-10-19 13:30 | 42 | 35 |  |  | 43757.5625 | 82 | 82
2019-10-19 14:00 | 46 | 40 |  |  | 43757.5833 | 90 | 90
2019-10-19 14:30 | 45 | 40 |  |  | 43757.6042 | 82 | 82
2019-10-19 15:00 | 49 | 44 |  |  | 43757.625 | 88 | 88
2019-10-19 15:30 | 52 | 45 |  |  | 43757.6458 | 99 | 99
2019-10-19 16:00 | 58 | 51 |  |  | 43757.6667 | 109 | 108
2019-10-19 16:30 | 57 | 53 |  |  | 43757.6875 | 109 | 109
2019-10-19 17:00 | 60 | 57 |  |  | 43757.7083 | 112 | 112
2019-10-19 17:30 | 60 | 56 |  |  | 43757.7292 | 112 | 111
2019-10-19 18:00 | 66 | 62 |  |  | 43757.75 | 118 | 117
2019-10-19 18:30 | 69 | 65 |  |  | 43757.7708 | 124 | 123
2019-10-19 19:00 | 69 | 66 |  |  | 43757.7917 | 126 | 126
2019-10-19 19:30 | 67 | 63 |  |  | 43757.8125 | 123 | 122
2019-10-19 20:00 | 66 | 62 |  |  | 43757.8333 | 120 | 120
2019-10-19 20:30 | 64 | 60 |  |  | 43757.8542 | 118 | 118
2019-10-19 21:00 | 61 | 57 |  |  | 43757.875 | 112 | 112
2019-10-19 21:30 | 57 | 53 |  |  | 43757.8958 | 107 | 107
2019-10-19 22:00 | 56 | 52 |  |  | 43757.9167 | 106 | 106
2019-10-19 22:30 | 56 | 51 |  |  | 43757.9375 | 105 | 104
2019-10-19 23:00 | 55 | 49 |  |  | 43757.9583 | 102 | 101
2019-10-19 23:30 | 53 | 47 |  |  | 43757.9792 | 97 | 96
2019-10-20 | 48 | 41 |  |  | 43758 | 91 | 89
2019-10-20 00:30 | 47 | 40 |  |  | 43758.0208 | 87 | 85
2019-10-20 01:00 | 50 | 44 |  |  | 43758.0417 | 86 | 85
2019-10-20 01:30 | 47 | 40 |  |  | 43758.0625 | 82 | 80
2019-10-20 02:00 | 45 | 38 |  |  | 43758.0833 | 78 | 76
2019-10-20 02:30 | 45 | 38 |  |  | 43758.1042 | 78 | 76
2019-10-20 03:00 | 43 | 37 |  |  | 43758.125 | 76 | 74
2019-10-20 03:30 | 43 | 36 |  |  | 43758.1458 | 75 | 73
2019-10-20 04:00 | 42 | 36 |  |  | 43758.1667 | 75 | 72
2019-10-20 04:30 | 42 | 35 |  |  | 43758.1875 | 74 | 72
2019-10-20 05:00 | 40 | 34 |  |  | 43758.2083 | 72 | 71
2019-10-20 05:30 | 39 | 33 |  |  | 43758.2292 | 73 | 71
2019-10-20 06:00 | 39 | 32 |  |  | 43758.25 | 72 | 71
2019-10-20 06:30 | 35 | 28 |  |  | 43758.2708 | 68 | 67
2019-10-20 07:00 | 34 | 26 |  |  | 43758.2917 | 68 | 66
2019-10-20 07:30 | 31 | 21 |  |  | 43758.3125 | 64 | 63
2019-10-20 08:00 | 28 | 19 |  |  | 43758.3333 | 62 | 61
2019-10-20 08:30 | 26 | 17 |  |  | 43758.3542 | 62 | 61
2019-10-20 09:00 | 26 | 17 |  |  | 43758.375 | 61 | 61
2019-10-20 09:30 | 30 | 16 |  |  | 43758.3958 | 63 | 61
2019-10-20 10:00 | 30 | 15 |  |  | 43758.4167 | 62 | 60
2019-10-20 10:30 | 30 | 16 |  |  | 43758.4375 | 61 | 59
2019-10-20 11:00 | 29 | 16 |  |  | 43758.4583 | 60 | 58
2019-10-20 11:30 | 30 | 18 |  |  | 43758.4792 | 60 | 58
2019-10-20 12:00 | 30 | 19 |  |  | 43758.5 | 61 | 59
2019-10-20 12:30 | 30 | 19 |  |  | 43758.5208 | 61 | 59
2019-10-20 13:00 | 29 | 19 |  |  | 43758.5417 | 56 | 54
2019-10-20 13:30 | 30 | 21 |  |  | 43758.5625 | 55 | 53
2019-10-20 14:00 | 33 | 25 |  |  | 43758.5833 | 65 | 64
2019-10-20 14:30 | 34 | 26 |  |  | 43758.6042 | 69 | 67
2019-10-20 15:00 | 37 | 29 |  |  | 43758.625 | 73 | 72
2019-10-20 15:30 | 40 | 33 |  |  | 43758.6458 | 80 | 78
2019-10-20 16:00 | 42 | 35 |  |  | 43758.6667 | 84 | 83
2019-10-20 16:30 | 45 | 39 |  |  | 43758.6875 | 90 | 89
2019-10-20 17:00 | 46 | 40 |  |  | 43758.7083 | 94 | 92
2019-10-20 17:30 | 54 | 49 |  |  | 43758.7292 | 103 | 102
2019-10-20 18:00 | 63 | 58 |  |  | 43758.75 | 116 | 114
2019-10-20 18:30 | 65 | 60 |  |  | 43758.7708 | 120 | 119
2019-10-20 19:00 | 67 | 61 |  |  | 43758.7917 | 124 | 122
2019-10-20 19:30 | 65 | 59 |  |  | 43758.8125 | 121 | 118
2019-10-20 20:00 | 63 | 57 |  |  | 43758.8333 | 118 | 115
2019-10-20 20:30 | 61 | 56 |  |  | 43758.8542 | 116 | 114
2019-10-20 21:00 | 60 | 54 |  |  | 43758.875 | 111 | 109
2019-10-20 21:30 | 57 | 49 |  |  | 43758.8958 | 106 | 103
2019-10-20 22:00 | 55 | 48 |  |  | 43758.9167 | 104 | 100
2019-10-20 22:30 | 54 | 46 |  |  | 43758.9375 | 103 | 99
2019-10-20 23:00 | 53 | 43 |  |  | 43758.9583 | 100 | 96
2019-10-20 23:30 | 51 | 41 |  |  | 43758.9792 | 96 | 92
2019-10-21 | 46 | 37 |  |  | 43759 | 89 | 86
2019-10-21 00:30 | 47 | 36 |  |  | 43759.0208 | 85 | 81
2019-10-21 01:00 | 46 | 34 |  |  | 43759.0417 | 81 | 76
2019-10-21 01:30 | 44 | 32 |  |  | 43759.0625 | 77 | 72
2019-10-21 02:00 | 44 | 32 |  |  | 43759.0833 | 76 | 71
2019-10-21 02:30 | 44 | 32 |  |  | 43759.1042 | 76 | 71
2019-10-21 03:00 | 43 | 33 |  |  | 43759.125 | 75 | 70
2019-10-21 03:30 | 42 | 32 |  |  | 43759.1458 | 74 | 70
2019-10-21 04:00 | 42 | 32 |  |  | 43759.1667 | 74 | 70
2019-10-21 04:30 | 42 | 32 |  |  | 43759.1875 | 74 | 70
2019-10-21 05:00 | 44 | 36 |  |  | 43759.2083 | 78 | 75
2019-10-21 05:30 | 48 | 41 |  |  | 43759.2292 | 84 | 81
2019-10-21 06:00 | 51 | 44 |  |  | 43759.25 | 91 | 88
2019-10-21 06:30 | 51 | 46 |  |  | 43759.2708 | 98 | 97
2019-10-21 07:00 | 50 | 45 |  |  | 43759.2917 | 102 | 101
2019-10-21 07:30 | 51 | 47 |  |  | 43759.3125 | 107 | 106
2019-10-21 08:00 | 53 | 49 |  |  | 43759.3333 | 111 | 110
2019-10-21 08:30 | 56 | 53 |  |  | 43759.3542 | 114 | 114
2019-10-21 09:00 | 57 | 53 |  |  | 43759.375 | 113 | 113
2019-10-21 09:30 | 57 | 50 |  |  | 43759.3958 | 111 | 109
2019-10-21 10:00 | 55 | 48 |  |  | 43759.4167 | 111 | 108
2019-10-21 10:30 | 55 | 48 |  |  | 43759.4375 | 109 | 107
2019-10-21 11:00 | 56 | 49 |  |  | 43759.4583 | 107 | 105
2019-10-21 11:30 | 57 | 50 |  |  | 43759.4792 | 107 | 104
2019-10-21 12:00 | 56 | 50 |  |  | 43759.5 | 108 | 106
2019-10-21 12:30 | 56 | 49 |  |  | 43759.5208 | 105 | 102
2019-10-21 13:00 | 57 | 50 |  |  | 43759.5417 | 105 | 102
2019-10-21 13:30 | 59 | 52 |  |  | 43759.5625 | 106 | 103
2019-10-21 14:00 | 56 | 49 |  |  | 43759.5833 | 105 | 102
2019-10-21 14:30 | 58 | 51 |  |  | 43759.6042 | 109 | 106
2019-10-21 15:00 | 58 | 52 |  |  | 43759.625 | 112 | 110
2019-10-21 15:30 | 63 | 57 |  |  | 43759.6458 | 119 | 116
2019-10-21 16:00 | 68 | 61 |  |  | 43759.6667 | 125 | 122
2019-10-21 16:30 | 73 | 67 |  |  | 43759.6875 | 132 | 128
2019-10-21 17:00 | 77 | 71 |  |  | 43759.7083 | 138 | 135
2019-10-21 17:30 | 84 | 77 |  |  | 43759.7292 | 145 | 141
2019-10-21 18:00 | 87 | 79 |  |  | 43759.75 | 148 | 143
2019-10-21 18:30 | 88 | 80 |  |  | 43759.7708 | 148 | 142
2019-10-21 19:00 | 87 | 80 |  |  | 43759.7917 | 151 | 145
2019-10-21 19:30 | 85 | 77 |  |  | 43759.8125 | 145 | 139
2019-10-21 20:00 | 83 | 76 |  |  | 43759.8333 | 141 | 135
2019-10-21 20:30 | 80 | 74 |  |  | 43759.8542 | 136 | 133
2019-10-21 21:00 | 75 | 70 |  |  | 43759.875 | 128 | 126
2019-10-21 21:30 | 70 | 65 |  |  | 43759.8958 | 120 | 118
2019-10-21 22:00 | 64 | 58 |  |  | 43759.9167 | 114 | 112
2019-10-21 22:30 | 63 | 57 |  |  | 43759.9375 | 111 | 108
2019-10-21 23:00 | 59 | 52 |  |  | 43759.9583 | 105 | 101
2019-10-21 23:30 | 55 | 46 |  |  | 43759.9792 | 97 | 93
2019-10-22 | 52 | 42 |  |  | 43760 | 93 | 88
2019-10-22 00:30 | 51 | 41 |  |  | 43760.0208 | 89 | 84
2019-10-22 01:00 | 51 | 42 |  |  | 43760.0417 | 87 | 82
2019-10-22 01:30 | 49 | 40 |  |  | 43760.0625 | 83 | 79
2019-10-22 02:00 | 49 | 40 |  |  | 43760.0833 | 81 | 77
2019-10-22 02:30 | 47 | 38 |  |  | 43760.1042 | 78 | 74
2019-10-22 03:00 | 47 | 38 |  |  | 43760.125 | 77 | 73
2019-10-22 03:30 | 47 | 39 |  |  | 43760.1458 | 79 | 75
2019-10-22 04:00 | 46 | 38 |  |  | 43760.1667 | 79 | 74
2019-10-22 04:30 | 46 | 37 |  |  | 43760.1875 | 80 | 77
2019-10-22 05:00 | 54 | 44 |  |  | 43760.2083 | 91 | 87
2019-10-22 05:30 | 52 | 43 |  |  | 43760.2292 | 91 | 88
2019-10-22 06:00 | 52 | 45 |  |  | 43760.25 | 95 | 93
2019-10-22 06:30 | 53 | 48 |  |  | 43760.2708 | 103 | 101
2019-10-22 07:00 | 54 | 50 |  |  | 43760.2917 | 107 | 106
2019-10-22 07:30 | 56 | 52 |  |  | 43760.3125 | 114 | 113
2019-10-22 08:00 | 57 | 53 |  |  | 43760.3333 | 116 | 115
2019-10-22 08:30 | 52 | 47 |  |  | 43760.3542 | 109 | 108
2019-10-22 09:00 | 54 | 49 |  |  | 43760.375 | 109 | 108
2019-10-22 09:30 | 57 | 53 |  |  | 43760.3958 | 115 | 114
2019-10-22 10:00 | 63 | 59 |  |  | 43760.4167 | 118 | 118
2019-10-22 10:30 | 61 | 57 |  |  | 43760.4375 | 117 | 117
2019-10-22 11:00 | 61 | 58 |  |  | 43760.4583 | 120 | 120
2019-10-22 11:30 | 61 | 58 |  |  | 43760.4792 | 121 | 121
2019-10-22 12:00 | 64 | 61 |  |  | 43760.5 | 123 | 123
2019-10-22 12:30 | 63 | 60 |  |  | 43760.5208 | 121 | 120
2019-10-22 13:00 | 58 | 55 |  |  | 43760.5417 | 115 | 115
2019-10-22 13:30 | 58 | 56 |  |  | 43760.5625 | 114 | 114
2019-10-22 14:00 | 58 | 56 |  |  | 43760.5833 | 113 | 113
2019-10-22 14:30 | 59 | 56 |  |  | 43760.6042 | 115 | 114
2019-10-22 15:00 | 60 | 57 |  |  | 43760.625 | 115 | 115
2019-10-22 15:30 | 61 | 58 |  |  | 43760.6458 | 117 | 117
2019-10-22 16:00 | 64 | 61 |  |  | 43760.6667 | 125 | 125
2019-10-22 16:30 | 67 | 64 |  |  | 43760.6875 | 131 | 130
2019-10-22 17:00 | 78 | 74 |  |  | 43760.7083 | 142 | 141
2019-10-22 17:30 | 80 | 77 |  |  | 43760.7292 | 144 | 143
2019-10-22 18:00 | 80 | 77 |  |  | 43760.75 | 145 | 144
2019-10-22 18:30 | 82 | 78 |  |  | 43760.7708 | 145 | 143
2019-10-22 19:00 | 85 | 81 |  |  | 43760.7917 | 149 | 147
2019-10-22 19:30 | 82 | 78 |  |  | 43760.8125 | 144 | 142
2019-10-22 20:00 | 80 | 76 |  |  | 43760.8333 | 139 | 137
2019-10-22 20:30 | 78 | 75 |  |  | 43760.8542 | 134 | 134
2019-10-22 21:00 | 75 | 71 |  |  | 43760.875 | 128 | 127
2019-10-22 21:30 | 71 | 67 |  |  | 43760.8958 | 122 | 120
2019-10-22 22:00 | 67 | 63 |  |  | 43760.9167 | 117 | 115
2019-10-22 22:30 | 65 | 59 |  |  | 43760.9375 | 112 | 110
2019-10-22 23:00 | 61 | 55 |  |  | 43760.9583 | 106 | 104
2019-10-22 23:30 | 56 | 49 |  |  | 43760.9792 | 99 | 96
2019-10-23 | 55 | 47 |  |  | 43761 | 95 | 91
2019-10-23 00:30 | 55 | 46 |  |  | 43761.0208 | 91 | 87
2019-10-23 01:00 | 52 | 44 |  |  | 43761.0417 | 87 | 83
2019-10-23 01:30 | 51 | 41 |  |  | 43761.0625 | 84 | 79
2019-10-23 02:00 | 50 | 39 |  |  | 43761.0833 | 82 | 77
2019-10-23 02:30 | 50 | 39 |  |  | 43761.1042 | 82 | 76
2019-10-23 03:00 | 49 | 37 |  |  | 43761.125 | 81 | 75
2019-10-23 03:30 | 48 | 37 |  |  | 43761.1458 | 80 | 74
2019-10-23 04:00 | 48 | 37 |  |  | 43761.1667 | 80 | 74
2019-10-23 04:30 | 48 | 37 |  |  | 43761.1875 | 82 | 76
2019-10-23 05:00 | 50 | 39 |  |  | 43761.2083 | 85 | 80
2019-10-23 05:30 | 53 | 45 |  |  | 43761.2292 | 91 | 87
2019-10-23 06:00 | 56 | 48 |  |  | 43761.25 | 96 | 93
2019-10-23 06:30 | 54 | 48 |  |  | 43761.2708 | 102 | 100
2019-10-23 07:00 | 53 | 49 |  |  | 43761.2917 | 107 | 106
2019-10-23 07:30 | 56 | 53 |  |  | 43761.3125 | 114 | 113
2019-10-23 08:00 | 56 | 53 |  |  | 43761.3333 | 113 | 113
2019-10-23 08:30 | 55 | 52 |  |  | 43761.3542 | 113 | 113
2019-10-23 09:00 | 57 | 55 |  |  | 43761.375 | 115 | 115
2019-10-23 09:30 | 59 | 56 |  |  | 43761.3958 | 117 | 117
2019-10-23 10:00 | 57 | 54 |  |  | 43761.4167 | 114 | 114
2019-10-23 10:30 | 53 | 50 |  |  | 43761.4375 | 110 | 110
2019-10-23 11:00 | 52 | 50 |  |  | 43761.4583 | 109 | 109
2019-10-23 11:30 | 51 | 48 |  |  | 43761.4792 | 106 | 106
2019-10-23 12:00 | 50 | 48 |  |  | 43761.5 | 106 | 106
2019-10-23 12:30 | 52 | 49 |  |  | 43761.5208 | 107 | 107
2019-10-23 13:00 | 52 | 49 |  |  | 43761.5417 | 108 | 108
2019-10-23 13:30 | 51 | 48 |  |  | 43761.5625 | 108 | 108
2019-10-23 14:00 | 52 | 49 |  |  | 43761.5833 | 110 | 110
2019-10-23 14:30 | 58 | 51 |  |  | 43761.6042 | 114 | 112
2019-10-23 15:00 | 56 | 50 |  |  | 43761.625 | 115 | 112
2019-10-23 15:30 | 60 | 52 |  |  | 43761.6458 | 119 | 116
2019-10-23 16:00 | 65 | 58 |  |  | 43761.6667 | 126 | 123
2019-10-23 16:30 | 69 | 62 |  |  | 43761.6875 | 133 | 129
2019-10-23 17:00 | 76 | 69 |  |  | 43761.7083 | 141 | 138
2019-10-23 17:30 | 79 | 72 |  |  | 43761.7292 | 145 | 141
2019-10-23 18:00 | 80 | 72 |  |  | 43761.75 | 148 | 142
2019-10-23 18:30 | 82 | 74 |  |  | 43761.7708 | 147 | 142
2019-10-23 19:00 | 85 | 78 |  |  | 43761.7917 | 151 | 146
2019-10-23 19:30 | 83 | 75 |  |  | 43761.8125 | 146 | 141
2019-10-23 20:00 | 82 | 73 |  |  | 43761.8333 | 140 | 134
2019-10-23 20:30 | 78 | 70 |  |  | 43761.8542 | 136 | 130
2019-10-23 21:00 | 71 | 66 |  |  | 43761.875 | 125 | 123
2019-10-23 21:30 | 68 | 62 |  |  | 43761.8958 | 119 | 117
2019-10-23 22:00 | 65 | 60 |  |  | 43761.9167 | 115 | 113
2019-10-23 22:30 | 62 | 54 |  |  | 43761.9375 | 110 | 107
2019-10-23 23:00 | 59 | 50 |  |  | 43761.9583 | 103 | 99
2019-10-23 23:30 | 53 | 45 |  |  | 43761.9792 | 96 | 93
2019-10-24 | 50 | 40 |  |  | 43762 | 90 | 87
2019-10-24 00:30 | 50 | 40 |  |  | 43762.0208 | 87 | 83
2019-10-24 01:00 | 49 | 38 |  |  | 43762.0417 | 84 | 79
2019-10-24 01:30 | 49 | 38 |  |  | 43762.0625 | 82 | 77
2019-10-24 02:00 | 47 | 37 |  |  | 43762.0833 | 80 | 75
2019-10-24 02:30 | 46 | 37 |  |  | 43762.1042 | 78 | 75
2019-10-24 03:00 | 48 | 40 |  |  | 43762.125 | 79 | 76
2019-10-24 03:30 | 48 | 40 |  |  | 43762.1458 | 81 | 77
2019-10-24 04:00 | 48 | 39 |  |  | 43762.1667 | 79 | 76
2019-10-24 04:30 | 48 | 40 |  |  | 43762.1875 | 80 | 77
2019-10-24 05:00 | 50 | 42 |  |  | 43762.2083 | 84 | 81
2019-10-24 05:30 | 50 | 43 |  |  | 43762.2292 | 87 | 84
2019-10-24 06:00 | 52 | 46 |  |  | 43762.25 | 92 | 89
2019-10-24 06:30 | 54 | 49 |  |  | 43762.2708 | 101 | 100
2019-10-24 07:00 | 54 | 50 |  |  | 43762.2917 | 105 | 105
2019-10-24 07:30 | 56 | 53 |  |  | 43762.3125 | 112 | 112
2019-10-24 08:00 | 56 | 52 |  |  | 43762.3333 | 113 | 112
2019-10-24 08:30 | 54 | 50 |  |  | 43762.3542 | 111 | 110
2019-10-24 09:00 | 55 | 51 |  |  | 43762.375 | 110 | 110
2019-10-24 09:30 | 53 | 49 |  |  | 43762.3958 | 107 | 107
2019-10-24 10:00 | 52 | 49 |  |  | 43762.4167 | 106 | 105
2019-10-24 10:30 | 51 | 48 |  |  | 43762.4375 | 104 | 104
2019-10-24 11:00 | 49 | 46 |  |  | 43762.4583 | 102 | 102
2019-10-24 11:30 | 48 | 46 |  |  | 43762.4792 | 102 | 102
2019-10-24 12:00 | 49 | 46 |  |  | 43762.5 | 103 | 103
2019-10-24 12:30 | 50 | 43 |  |  | 43762.5208 | 103 | 101
2019-10-24 13:00 | 49 | 41 |  |  | 43762.5417 | 102 | 99
2019-10-24 13:30 | 49 | 42 |  |  | 43762.5625 | 103 | 100
2019-10-24 14:00 | 51 | 44 |  |  | 43762.5833 | 106 | 103
2019-10-24 14:30 | 54 | 48 |  |  | 43762.6042 | 112 | 108
2019-10-24 15:00 | 56 | 50 |  |  | 43762.625 | 117 | 113
2019-10-24 15:30 | 58 | 51 |  |  | 43762.6458 | 122 | 117
2019-10-24 16:00 | 62 | 56 |  |  | 43762.6667 | 128 | 123
2019-10-24 16:30 | 65 | 60 |  |  | 43762.6875 | 131 | 128
2019-10-24 17:00 | 72 | 66 |  |  | 43762.7083 | 140 | 136
2019-10-24 17:30 | 73 | 68 |  |  | 43762.7292 | 142 | 138
2019-10-24 18:00 | 75 | 70 |  |  | 43762.75 | 143 | 140
2019-10-24 18:30 | 78 | 73 |  |  | 43762.7708 | 143 | 140
2019-10-24 19:00 | 83 | 78 |  |  | 43762.7917 | 149 | 145
2019-10-24 19:30 | 80 | 75 |  |  | 43762.8125 | 144 | 141
2019-10-24 20:00 | 78 | 74 |  |  | 43762.8333 | 137 | 135
2019-10-24 20:30 | 76 | 72 |  |  | 43762.8542 | 133 | 131
2019-10-24 21:00 | 73 | 68 |  |  | 43762.875 | 126 | 125
2019-10-24 21:30 | 69 | 63 |  |  | 43762.8958 | 119 | 116
2019-10-24 22:00 | 67 | 60 |  |  | 43762.9167 | 116 | 113
2019-10-24 22:30 | 68 | 61 |  |  | 43762.9375 | 116 | 113
2019-10-24 23:00 | 63 | 54 |  |  | 43762.9583 | 108 | 103
2019-10-24 23:30 | 59 | 51 |  |  | 43762.9792 | 103 | 98
2019-10-25 | 56 | 47 |  |  | 43763 | 98 | 93
2019-10-25 00:30 | 52 | 44 |  |  | 43763.0208 | 90 | 87
2019-10-25 01:00 | 50 | 43 |  |  | 43763.0417 | 86 | 83
2019-10-25 01:30 | 50 | 42 |  |  | 43763.0625 | 83 | 80
2019-10-25 02:00 | 49 | 40 |  |  | 43763.0833 | 81 | 77
2019-10-25 02:30 | 50 | 41 |  |  | 43763.1042 | 80 | 76
2019-10-25 03:00 | 50 | 41 |  |  | 43763.125 | 79 | 75
2019-10-25 03:30 | 50 | 42 |  |  | 43763.1458 | 80 | 76
2019-10-25 04:00 | 49 | 41 |  |  | 43763.1667 | 79 | 75
2019-10-25 04:30 | 50 | 41 |  |  | 43763.1875 | 82 | 79
2019-10-25 05:00 | 49 | 41 |  |  | 43763.2083 | 83 | 80
2019-10-25 05:30 | 52 | 44 |  |  | 43763.2292 | 88 | 85
2019-10-25 06:00 | 51 | 45 |  |  | 43763.25 | 92 | 90
2019-10-25 06:30 | 50 | 45 |  |  | 43763.2708 | 98 | 97
2019-10-25 07:00 | 49 | 46 |  |  | 43763.2917 | 102 | 102
2019-10-25 07:30 | 51 | 49 |  |  | 43763.3125 | 108 | 108
2019-10-25 08:00 | 52 | 49 |  |  | 43763.3333 | 111 | 111
2019-10-25 08:30 | 52 | 49 |  |  | 43763.3542 | 111 | 111
2019-10-25 09:00 | 48 | 46 |  |  | 43763.375 | 106 | 106
2019-10-25 09:30 | 49 | 46 |  |  | 43763.3958 | 105 | 105
2019-10-25 10:00 | 49 | 46 |  |  | 43763.4167 | 105 | 105
2019-10-25 10:30 | 50 | 47 |  |  | 43763.4375 | 106 | 106
2019-10-25 11:00 | 48 | 45 |  |  | 43763.4583 | 104 | 104
2019-10-25 11:30 | 48 | 44 |  |  | 43763.4792 | 103 | 103
2019-10-25 12:00 | 49 | 45 |  |  | 43763.5 | 105 | 104
2019-10-25 12:30 | 50 | 44 |  |  | 43763.5208 | 105 | 104
2019-10-25 13:00 | 55 | 47 |  |  | 43763.5417 | 109 | 106
2019-10-25 13:30 | 53 | 47 |  |  | 43763.5625 | 110 | 109
2019-10-25 14:00 | 52 | 46 |  |  | 43763.5833 | 109 | 108
2019-10-25 14:30 | 58 | 51 |  |  | 43763.6042 | 115 | 113
2019-10-25 15:00 | 58 | 51 |  |  | 43763.625 | 117 | 114
2019-10-25 15:30 | 60 | 52 |  |  | 43763.6458 | 119 | 116
2019-10-25 16:00 | 62 | 55 |  |  | 43763.6667 | 123 | 120
2019-10-25 16:30 | 68 | 61 |  |  | 43763.6875 | 131 | 128
2019-10-25 17:00 | 76 | 69 |  |  | 43763.7083 | 139 | 136
2019-10-25 17:30 | 79 | 71 |  |  | 43763.7292 | 141 | 138
2019-10-25 18:00 | 82 | 72 |  |  | 43763.75 | 143 | 137
2019-10-25 18:30 | 81 | 71 |  |  | 43763.7708 | 141 | 135
2019-10-25 19:00 | 83 | 74 |  |  | 43763.7917 | 144 | 138
2019-10-25 19:30 | 81 | 72 |  |  | 43763.8125 | 139 | 133
2019-10-25 20:00 | 81 | 71 |  |  | 43763.8333 | 138 | 131
2019-10-25 20:30 | 77 | 68 |  |  | 43763.8542 | 134 | 128
2019-10-25 21:00 | 70 | 63 |  |  | 43763.875 | 123 | 120
2019-10-25 21:30 | 67 | 59 |  |  | 43763.8958 | 117 | 114
2019-10-25 22:00 | 66 | 57 |  |  | 43763.9167 | 116 | 112
2019-10-25 22:30 | 63 | 54 |  |  | 43763.9375 | 112 | 108
2019-10-25 23:00 | 64 | 54 |  |  | 43763.9583 | 110 | 105
2019-10-25 23:30 | 62 | 52 |  |  | 43763.9792 | 107 | 101
2019-10-26 | 59 | 48 |  |  | 43764 | 101 | 95
2019-10-26 00:30 | 58 | 47 |  |  | 43764.0208 | 96 | 90
2019-10-26 01:00 | 55 | 45 |  |  | 43764.0417 | 87 | 83
2019-10-26 01:30 | 56 | 47 |  |  | 43764.0625 | 86 | 82
2019-10-26 02:00 | 54 | 45 |  |  | 43764.0833 | 83 | 79
2019-10-26 02:30 | 53 | 42 |  |  | 43764.1042 | 82 | 77
2019-10-26 03:00 | 51 | 42 |  |  | 43764.125 | 80 | 77
2019-10-26 03:30 | 50 | 41 |  |  | 43764.1458 | 80 | 76
2019-10-26 04:00 | 50 | 41 |  |  | 43764.1667 | 79 | 75
2019-10-26 04:30 | 50 | 41 |  |  | 43764.1875 | 80 | 76
2019-10-26 05:00 | 50 | 41 |  |  | 43764.2083 | 80 | 76
2019-10-26 05:30 | 51 | 42 |  |  | 43764.2292 | 80 | 77
2019-10-26 06:00 | 48 | 39 |  |  | 43764.25 | 78 | 75
2019-10-26 06:30 | 43 | 33 |  |  | 43764.2708 | 75 | 72
2019-10-26 07:00 | 38 | 29 |  |  | 43764.2917 | 71 | 69
2019-10-26 07:30 | 36 | 29 |  |  | 43764.3125 | 73 | 71
2019-10-26 08:00 | 33 | 27 |  |  | 43764.3333 | 70 | 68
2019-10-26 08:30 | 31 | 25 |  |  | 43764.3542 | 67 | 66
2019-10-26 09:00 | 29 | 24 |  |  | 43764.375 | 66 | 65
2019-10-26 09:30 | 28 | 22 |  |  | 43764.3958 | 65 | 64
2019-10-26 10:00 | 29 | 23 |  |  | 43764.4167 | 64 | 63
2019-10-26 10:30 | 28 | 21 |  |  | 43764.4375 | 61 | 61
2019-10-26 11:00 | 27 | 20 |  |  | 43764.4583 | 60 | 59
2019-10-26 11:30 | 26 | 20 |  |  | 43764.4792 | 59 | 58
2019-10-26 12:00 | 27 | 20 |  |  | 43764.5 | 58 | 56
2019-10-26 12:30 | 27 | 22 |  |  | 43764.5208 | 59 | 59
2019-10-26 13:00 | 26 | 22 |  |  | 43764.5417 | 59 | 59
2019-10-26 13:30 | 27 | 23 |  |  | 43764.5625 | 60 | 60
2019-10-26 14:00 | 29 | 25 |  |  | 43764.5833 | 62 | 62
2019-10-26 14:30 | 32 | 29 |  |  | 43764.6042 | 66 | 66
2019-10-26 15:00 | 35 | 32 |  |  | 43764.625 | 71 | 71
2019-10-26 15:30 | 39 | 36 |  |  | 43764.6458 | 78 | 77
2019-10-26 16:00 | 42 | 39 |  |  | 43764.6667 | 85 | 84
2019-10-26 16:30 | 47 | 44 |  |  | 43764.6875 | 93 | 93
2019-10-26 17:00 | 54 | 51 |  |  | 43764.7083 | 102 | 101
2019-10-26 17:30 | 57 | 53 |  |  | 43764.7292 | 106 | 104
2019-10-26 18:00 | 60 | 55 |  |  | 43764.75 | 110 | 108
2019-10-26 18:30 | 62 | 58 |  |  | 43764.7708 | 114 | 112
2019-10-26 19:00 | 65 | 61 |  |  | 43764.7917 | 117 | 115
2019-10-26 19:30 | 63 | 59 |  |  | 43764.8125 | 114 | 113
2019-10-26 20:00 | 60 | 57 |  |  | 43764.8333 | 111 | 110
2019-10-26 20:30 | 58 | 55 |  |  | 43764.8542 | 109 | 108
2019-10-26 21:00 | 56 | 52 |  |  | 43764.875 | 105 | 103
2019-10-26 21:30 | 53 | 49 |  |  | 43764.8958 | 100 | 99
2019-10-26 22:00 | 52 | 48 |  |  | 43764.9167 | 99 | 97
2019-10-26 22:30 | 52 | 47 |  |  | 43764.9375 | 98 | 96
2019-10-26 23:00 | 49 | 43 |  |  | 43764.9583 | 93 | 91
2019-10-26 23:30 | 45 | 39 |  |  | 43764.9792 | 87 | 85
2019-10-27 | 42 | 35 |  |  | 43765 | 82 | 79
2019-10-27 00:30 | 42 | 34 |  |  | 43765.0208 | 78 | 75
2019-10-27 01:00 | 41 | 33 |  |  | 43765.0417 | 76 | 72
2019-10-27 01:30 | 34 | 31 |  |  | 43765.0625 | 76 | 68
2019-10-27 02:00 | 31 | 29 |  |  | 43765.0833 | 72 | 64
2019-10-27 02:30 | 31 | 29 |  |  | 43765.1042 | 71 | 64
2019-10-27 03:00 | 29 | 27 |  |  | 43765.125 | 70 | 62
2019-10-27 03:30 | 29 | 27 |  |  | 43765.1458 | 70 | 62
2019-10-27 04:00 | 29 | 27 |  |  | 43765.1667 | 69 | 61
2019-10-27 04:30 | 28 | 26 |  |  | 43765.1875 | 68 | 60
2019-10-27 05:00 | 27 | 24 |  |  | 43765.2083 | 67 | 59
2019-10-27 05:30 | 27 | 25 |  |  | 43765.2292 | 68 | 60
2019-10-27 06:00 | 24 | 23 |  |  | 43765.25 | 65 | 58
2019-10-27 06:30 | 20 | 18 |  |  | 43765.2708 | 60 | 54
2019-10-27 07:00 | 19 | 17 |  |  | 43765.2917 | 60 | 54
2019-10-27 07:30 | 18 | 17 |  |  | 43765.3125 | 60 | 55
2019-10-27 08:00 | 17 | 16 |  |  | 43765.3333 | 58 | 54
2019-10-27 08:30 | 18 | 18 |  |  | 43765.3542 | 60 | 57
2019-10-27 09:00 | 17 | 17 |  |  | 43765.375 | 59 | 56
2019-10-27 09:30 | 17 | 16 |  |  | 43765.3958 | 58 | 57
2019-10-27 10:00 | 19 | 19 |  |  | 43765.4167 | 59 | 58
2019-10-27 10:30 | 20 | 19 |  |  | 43765.4375 | 58 | 57
2019-10-27 11:00 | 22 | 21 |  |  | 43765.4583 | 59 | 58
2019-10-27 11:30 | 23 | 22 |  |  | 43765.4792 | 58 | 58
2019-10-27 12:00 | 24 | 22 |  |  | 43765.5 | 59 | 58
2019-10-27 12:30 | 24 | 22 |  |  | 43765.5208 | 58 | 57
2019-10-27 13:00 | 24 | 24 |  |  | 43765.5417 | 59 | 59
2019-10-27 13:30 | 25 | 24 |  |  | 43765.5625 | 61 | 61
2019-10-27 14:00 | 26 | 26 |  |  | 43765.5833 | 64 | 64
2019-10-27 14:30 | 30 | 30 |  |  | 43765.6042 | 69 | 69
2019-10-27 15:00 | 34 | 34 |  |  | 43765.625 | 74 | 74
2019-10-27 15:30 | 38 | 37 |  |  | 43765.6458 | 80 | 80
2019-10-27 16:00 | 43 | 42 |  |  | 43765.6667 | 87 | 86
2019-10-27 16:30 | 45 | 44 |  |  | 43765.6875 | 94 | 93
2019-10-27 17:00 | 52 | 50 |  |  | 43765.7083 | 103 | 103
2019-10-27 17:30 | 57 | 56 |  |  | 43765.7292 | 110 | 109
2019-10-27 18:00 | 58 | 57 |  |  | 43765.75 | 112 | 112
2019-10-27 18:30 | 60 | 59 |  |  | 43765.7708 | 118 | 117
2019-10-27 19:00 | 63 | 61 |  |  | 43765.7917 | 122 | 122
2019-10-27 19:30 | 59 | 58 |  |  | 43765.8125 | 118 | 117
2019-10-27 20:00 | 57 | 55 |  |  | 43765.8333 | 115 | 115
2019-10-27 20:30 | 54 | 53 |  |  | 43765.8542 | 112 | 112
2019-10-27 21:00 | 50 | 48 |  |  | 43765.875 | 106 | 106
2019-10-27 21:30 | 46 | 45 |  |  | 43765.8958 | 101 | 101
2019-10-27 22:00 | 45 | 43 |  |  | 43765.9167 | 98 | 98
2019-10-27 22:30 | 43 | 41 |  |  | 43765.9375 | 96 | 96
2019-10-27 23:00 | 44 | 42 |  |  | 43765.9583 | 93 | 92
2019-10-27 23:30 | 40 | 37 |  |  | 43765.9792 | 88 | 87
2019-10-28 | 36 | 33 |  |  | 43766 | 81 | 80
2019-10-28 00:30 | 36 | 33 |  |  | 43766.0208 | 79 | 78
2019-10-28 01:00 | 33 | 30 |  |  | 43766.0417 | 73 | 72
2019-10-28 01:30 | 32 | 29 |  |  | 43766.0625 | 70 | 69
2019-10-28 02:00 | 38 | 27 |  |  | 43766.0833 | 69 | 66
2019-10-28 02:30 | 37 | 26 |  |  | 43766.1042 | 66 | 64
2019-10-28 03:00 | 38 | 27 |  |  | 43766.125 | 67 | 65
2019-10-28 03:30 | 38 | 27 |  |  | 43766.1458 | 67 | 65
2019-10-28 04:00 | 37 | 26 |  |  | 43766.1667 | 67 | 64
2019-10-28 04:30 | 38 | 27 |  |  | 43766.1875 | 67 | 65
2019-10-28 05:00 | 39 | 30 |  |  | 43766.2083 | 70 | 69
2019-10-28 05:30 | 42 | 34 |  |  | 43766.2292 | 76 | 75
2019-10-28 06:00 | 46 | 39 |  |  | 43766.25 | 85 | 83
2019-10-28 06:30 | 50 | 45 |  |  | 43766.2708 | 96 | 95
2019-10-28 07:00 | 56 | 53 |  |  | 43766.2917 | 109 | 109
2019-10-28 07:30 | 59 | 59 |  |  | 43766.3125 | 119 | 119
2019-10-28 08:00 | 63 | 62 |  |  | 43766.3333 | 126 | 126
2019-10-28 08:30 | 63 | 62 |  |  | 43766.3542 | 126 | 126
2019-10-28 09:00 | 61 | 61 |  |  | 43766.375 | 126 | 126
2019-10-28 09:30 | 57 | 57 |  |  | 43766.3958 | 123 | 123
2019-10-28 10:00 | 53 | 53 |  |  | 43766.4167 | 115 | 114
2019-10-28 10:30 | 57 | 56 |  |  | 43766.4375 | 115 | 115
2019-10-28 11:00 | 62 | 62 |  |  | 43766.4583 | 121 | 121
2019-10-28 11:30 | 63 | 62 |  |  | 43766.4792 | 121 | 121
2019-10-28 12:00 | 59 | 58 |  |  | 43766.5 | 119 | 119
2019-10-28 12:30 | 63 | 63 |  |  | 43766.5208 | 122 | 122
2019-10-28 13:00 | 61 | 61 |  |  | 43766.5417 | 124 | 124
2019-10-28 13:30 | 58 | 57 |  |  | 43766.5625 | 120 | 120
2019-10-28 14:00 | 51 | 50 |  |  | 43766.5833 | 113 | 113
2019-10-28 14:30 | 53 | 52 |  |  | 43766.6042 | 117 | 116
2019-10-28 15:00 | 53 | 53 |  |  | 43766.625 | 119 | 119
2019-10-28 15:30 | 56 | 55 |  |  | 43766.6458 | 121 | 121
2019-10-28 16:00 | 58 | 57 |  |  | 43766.6667 | 124 | 124
2019-10-28 16:30 | 61 | 60 |  |  | 43766.6875 | 128 | 127
2019-10-28 17:00 | 65 | 64 |  |  | 43766.7083 | 132 | 131
2019-10-28 17:30 | 68 | 67 |  |  | 43766.7292 | 134 | 133
2019-10-28 18:00 | 72 | 70 |  |  | 43766.75 | 136 | 135
2019-10-28 18:30 | 72 | 71 |  |  | 43766.7708 | 136 | 135
2019-10-28 19:00 | 76 | 74 |  |  | 43766.7917 | 139 | 138
2019-10-28 19:30 | 72 | 70 |  |  | 43766.8125 | 133 | 132
2019-10-28 20:00 | 69 | 67 |  |  | 43766.8333 | 129 | 128
2019-10-28 20:30 | 68 | 66 |  |  | 43766.8542 | 128 | 126
2019-10-28 21:00 | 65 | 60 |  |  | 43766.875 | 120 | 118
2019-10-28 21:30 | 62 | 55 |  |  | 43766.8958 | 114 | 111
2019-10-28 22:00 | 58 | 49 |  |  | 43766.9167 | 109 | 106
2019-10-28 22:30 | 56 | 46 |  |  | 43766.9375 | 105 | 102
2019-10-28 23:00 | 55 | 44 |  |  | 43766.9583 | 100 | 95
2019-10-28 23:30 | 51 | 39 |  |  | 43766.9792 | 94 | 89
2019-10-29 | 47 | 35 |  |  | 43767 | 88 | 83
2019-10-29 00:30 | 45 | 34 |  |  | 43767.0208 | 81 | 78
2019-10-29 01:00 | 45 | 33 |  |  | 43767.0417 | 79 | 75
2019-10-29 01:30 | 44 | 31 |  |  | 43767.0625 | 76 | 71
2019-10-29 02:00 | 44 | 31 |  |  | 43767.0833 | 75 | 70
2019-10-29 02:30 | 44 | 30 |  |  | 43767.1042 | 74 | 69
2019-10-29 03:00 | 45 | 33 |  |  | 43767.125 | 75 | 70
2019-10-29 03:30 | 43 | 32 |  |  | 43767.1458 | 74 | 70
2019-10-29 04:00 | 43 | 31 |  |  | 43767.1667 | 74 | 70
2019-10-29 04:30 | 42 | 30 |  |  | 43767.1875 | 74 | 70
2019-10-29 05:00 | 44 | 34 |  |  | 43767.2083 | 77 | 74
2019-10-29 05:30 | 48 | 39 |  |  | 43767.2292 | 83 | 80
2019-10-29 06:00 | 48 | 40 |  |  | 43767.25 | 85 | 83
2019-10-29 06:30 | 50 | 45 |  |  | 43767.2708 | 95 | 94
2019-10-29 07:00 | 52 | 47 |  |  | 43767.2917 | 102 | 101
2019-10-29 07:30 | 55 | 51 |  |  | 43767.3125 | 109 | 109
2019-10-29 08:00 | 52 | 51 |  |  | 43767.3333 | 111 | 111
2019-10-29 08:30 | 49 | 47 |  |  | 43767.3542 | 109 | 109
2019-10-29 09:00 | 49 | 46 |  |  | 43767.375 | 107 | 107
2019-10-29 09:30 | 49 | 45 |  |  | 43767.3958 | 107 | 106
2019-10-29 10:00 | 50 | 47 |  |  | 43767.4167 | 107 | 107
2019-10-29 10:30 | 54 | 51 |  |  | 43767.4375 | 109 | 109
2019-10-29 11:00 | 53 | 51 |  |  | 43767.4583 | 107 | 107
2019-10-29 11:30 | 53 | 49 |  |  | 43767.4792 | 106 | 106
2019-10-29 12:00 | 54 | 50 |  |  | 43767.5 | 108 | 108
2019-10-29 12:30 | 53 | 50 |  |  | 43767.5208 | 107 | 107
2019-10-29 13:00 | 52 | 49 |  |  | 43767.5417 | 105 | 105
2019-10-29 13:30 | 50 | 48 |  |  | 43767.5625 | 105 | 105
2019-10-29 14:00 | 50 | 48 |  |  | 43767.5833 | 106 | 106
2019-10-29 14:30 | 54 | 53 |  |  | 43767.6042 | 114 | 113
2019-10-29 15:00 | 54 | 53 |  |  | 43767.625 | 115 | 114
2019-10-29 15:30 | 54 | 53 |  |  | 43767.6458 | 118 | 117
2019-10-29 16:00 | 59 | 57 |  |  | 43767.6667 | 123 | 123
2019-10-29 16:30 | 65 | 62 |  |  | 43767.6875 | 129 | 129
2019-10-29 17:00 | 75 | 68 |  |  | 43767.7083 | 135 | 135
2019-10-29 17:30 | 76 | 71 |  |  | 43767.7292 | 136 | 136
2019-10-29 18:00 | 74 | 72 |  |  | 43767.75 | 137 | 137
2019-10-29 18:30 | 78 | 75 |  |  | 43767.7708 | 138 | 138
2019-10-29 19:00 | 80 | 77 |  |  | 43767.7917 | 141 | 141
2019-10-29 19:30 | 76 | 73 |  |  | 43767.8125 | 136 | 136
2019-10-29 20:00 | 73 | 70 |  |  | 43767.8333 | 133 | 133
2019-10-29 20:30 | 70 | 66 |  |  | 43767.8542 | 129 | 129
2019-10-29 21:00 | 67 | 63 |  |  | 43767.875 | 123 | 123
2019-10-29 21:30 | 64 | 59 |  |  | 43767.8958 | 116 | 116
2019-10-29 22:00 | 65 | 54 |  |  | 43767.9167 | 112 | 111
2019-10-29 22:30 | 64 | 52 |  |  | 43767.9375 | 110 | 109
2019-10-29 23:00 | 63 | 49 |  |  | 43767.9583 | 104 | 103
2019-10-29 23:30 | 60 | 46 |  |  | 43767.9792 | 98 | 98
2019-10-30 | 58 | 42 |  |  | 43768 | 93 | 92
2019-10-30 00:30 | 57 | 39 |  |  | 43768.0208 | 87 | 86
2019-10-30 01:00 | 57 | 38 |  |  | 43768.0417 | 83 | 81
2019-10-30 01:30 | 55 | 36 |  |  | 43768.0625 | 81 | 79
2019-10-30 02:00 | 56 | 36 |  |  | 43768.0833 | 79 | 77
2019-10-30 02:30 | 57 | 37 |  |  | 43768.1042 | 79 | 77
2019-10-30 03:00 | 54 | 37 |  |  | 43768.125 | 78 | 77
2019-10-30 03:30 | 53 | 34 |  |  | 43768.1458 | 77 | 76
2019-10-30 04:00 | 52 | 33 |  |  | 43768.1667 | 76 | 75
2019-10-30 04:30 | 52 | 35 |  |  | 43768.1875 | 78 | 77
2019-10-30 05:00 | 52 | 36 |  |  | 43768.2083 | 81 | 80
2019-10-30 05:30 | 55 | 41 |  |  | 43768.2292 | 86 | 85
2019-10-30 06:00 | 55 | 43 |  |  | 43768.25 | 90 | 90
2019-10-30 06:30 | 57 | 46 |  |  | 43768.2708 | 100 | 99
2019-10-30 07:00 | 62 | 54 |  |  | 43768.2917 | 112 | 112
2019-10-30 07:30 | 65 | 59 |  |  | 43768.3125 | 122 | 121
2019-10-30 08:00 | 62 | 56 |  |  | 43768.3333 | 125 | 125
2019-10-30 08:30 | 61 | 56 |  |  | 43768.3542 | 121 | 121
2019-10-30 09:00 | 68 | 63 |  |  | 43768.375 | 130 | 130
2019-10-30 09:30 | 64 | 59 |  |  | 43768.3958 | 129 | 129
2019-10-30 10:00 | 61 | 56 |  |  | 43768.4167 | 125 | 125
2019-10-30 10:30 | 64 | 58 |  |  | 43768.4375 | 122 | 122
2019-10-30 11:00 | 65 | 63 |  |  | 43768.4583 | 129 | 129
2019-10-30 11:30 | 62 | 60 |  |  | 43768.4792 | 130 | 130
2019-10-30 12:00 | 64 | 62 |  |  | 43768.5 | 129 | 129
2019-10-30 12:30 | 57 | 54 |  |  | 43768.5208 | 119 | 119
2019-10-30 13:00 | 62 | 59 |  |  | 43768.5417 | 122 | 122
2019-10-30 13:30 | 66 | 64 |  |  | 43768.5625 | 134 | 134
2019-10-30 14:00 | 67 | 64 |  |  | 43768.5833 | 133 | 133
2019-10-30 14:30 | 67 | 65 |  |  | 43768.6042 | 131 | 131
2019-10-30 15:00 | 61 | 58 |  |  | 43768.625 | 120 | 120
2019-10-30 15:30 | 56 | 52 |  |  | 43768.6458 | 111 | 111
2019-10-30 16:00 | 47 | 42 |  |  | 43768.6667 | 92 | 92
2019-10-30 16:30 | 47 | 42 |  |  | 43768.6875 | 85 | 85
2019-10-30 17:00 | 53 | 48 |  |  | 43768.7083 | 93 | 93
2019-10-30 17:30 | 56 | 51 |  |  | 43768.7292 | 96 | 95
2019-10-30 18:00 | 60 | 55 |  |  | 43768.75 | 98 | 97
2019-10-30 18:30 | 59 | 55 |  |  | 43768.7708 | 97 | 96
2019-10-30 19:00 | 61 | 57 |  |  | 43768.7917 | 98 | 98
2019-10-30 19:30 | 59 | 55 |  |  | 43768.8125 | 96 | 95
2019-10-30 20:00 | 55 | 51 |  |  | 43768.8333 | 92 | 92
2019-10-30 20:30 | 53 | 48 |  |  | 43768.8542 | 89 | 89
2019-10-30 21:00 | 52 | 43 |  |  | 43768.875 | 82 | 82
2019-10-30 21:30 | 52 | 41 |  |  | 43768.8958 | 79 | 79
2019-10-30 22:00 | 51 | 40 |  |  | 43768.9167 | 77 | 76
2019-10-30 22:30 | 50 | 38 |  |  | 43768.9375 | 76 | 75
2019-10-30 23:00 | 49 | 36 |  |  | 43768.9583 | 71 | 70
2019-10-30 23:30 | 47 | 33 |  |  | 43768.9792 | 66 | 65
2019-10-31 | 44 | 28 |  |  | 43769 | 62 | 61
2019-10-31 00:30 | 43 | 27 |  |  | 43769.0208 | 57 | 56
2019-10-31 01:00 | 44 | 28 |  |  | 43769.0417 | 56 | 55
2019-10-31 01:30 | 43 | 27 |  |  | 43769.0625 | 55 | 53
2019-10-31 02:00 | 44 | 26 |  |  | 43769.0833 | 53 | 52
2019-10-31 02:30 | 40 | 25 |  |  | 43769.1042 | 50 | 50
2019-10-31 03:00 | 40 | 25 |  |  | 43769.125 | 51 | 51
2019-10-31 03:30 | 39 | 24 |  |  | 43769.1458 | 49 | 49
2019-10-31 04:00 | 40 | 25 |  |  | 43769.1667 | 49 | 49
2019-10-31 04:30 | 41 | 27 |  |  | 43769.1875 | 51 | 51
2019-10-31 05:00 | 41 | 28 |  |  | 43769.2083 | 54 | 54
2019-10-31 05:30 | 43 | 32 |  |  | 43769.2292 | 59 | 59
2019-10-31 06:00 | 43 | 32 |  |  | 43769.25 | 61 | 61
2019-10-31 06:30 | 41 | 32 |  |  | 43769.2708 | 65 | 65
2019-10-31 07:00 | 37 | 32 |  |  | 43769.2917 | 71 | 70
2019-10-31 07:30 | 35 | 33 |  |  | 43769.3125 | 77 | 76
2019-10-31 08:00 | 35 | 34 |  |  | 43769.3333 | 81 | 79
2019-10-31 08:30 | 36 | 34 |  |  | 43769.3542 | 83 | 81
2019-10-31 09:00 | 38 | 37 |  |  | 43769.375 | 87 | 85
2019-10-31 09:30 | 40 | 39 |  |  | 43769.3958 | 88 | 86
2019-10-31 10:00 | 37 | 37 |  |  | 43769.4167 | 85 | 82
2019-10-31 10:30 | 37 | 36 |  |  | 43769.4375 | 83 | 81
2019-10-31 11:00 | 37 | 36 |  |  | 43769.4583 | 79 | 77
2019-10-31 11:30 | 33 | 32 |  |  | 43769.4792 | 72 | 69
2019-10-31 12:00 | 31 | 31 |  |  | 43769.5 | 70 | 66
2019-10-31 12:30 | 30 | 29 |  |  | 43769.5208 | 70 | 66
2019-10-31 13:00 | 29 | 29 |  |  | 43769.5417 | 69 | 66
2019-10-31 13:30 | 28 | 28 |  |  | 43769.5625 | 70 | 67
2019-10-31 14:00 | 28 | 27 |  |  | 43769.5833 | 69 | 66
2019-10-31 14:30 | 31 | 30 |  |  | 43769.6042 | 75 | 72
2019-10-31 15:00 | 33 | 32 |  |  | 43769.625 | 79 | 76
2019-10-31 15:30 | 34 | 33 |  |  | 43769.6458 | 83 | 81
2019-10-31 16:00 | 35 | 34 |  |  | 43769.6667 | 82 | 80
2019-10-31 16:30 | 40 | 38 |  |  | 43769.6875 | 86 | 85
2019-10-31 17:00 | 43 | 41 |  |  | 43769.7083 | 89 | 88
2019-10-31 17:30 | 46 | 43 |  |  | 43769.7292 | 89 | 89
2019-10-31 18:00 | 46 | 43 |  |  | 43769.75 | 89 | 89
2019-10-31 18:30 | 48 | 45 |  |  | 43769.7708 | 90 | 90
2019-10-31 19:00 | 51 | 49 |  |  | 43769.7917 | 95 | 95
2019-10-31 19:30 | 51 | 49 |  |  | 43769.8125 | 93 | 93
2019-10-31 20:00 | 51 | 49 |  |  | 43769.8333 | 91 | 90
2019-10-31 20:30 | 51 | 49 |  |  | 43769.8542 | 91 | 90
2019-10-31 21:00 | 55 | 45 |  |  | 43769.875 | 83 | 83
2019-10-31 21:30 | 54 | 40 |  |  | 43769.8958 | 77 | 77
2019-10-31 22:00 | 56 | 42 |  |  | 43769.9167 | 78 | 78
2019-10-31 22:30 | 52 | 36 |  |  | 43769.9375 | 74 | 74
2019-10-31 23:00 | 51 | 34 |  |  | 43769.9583 | 70 | 70
2019-10-31 23:30 | 49 | 30 |  |  | 43769.9792 | 64 | 64
2019-11-01 | 48 | 27 |  |  | 43770 | 60 | 60
2019-11-01 00:30 | 48 | 27 |  |  | 43770.0208 | 59 | 58
2019-11-01 01:00 | 49 | 27 |  |  | 43770.0417 | 57 | 56
2019-11-01 01:30 | 49 | 25 |  |  | 43770.0625 | 54 | 53
2019-11-01 02:00 | 47 | 23 |  |  | 43770.0833 | 52 | 51
2019-11-01 02:30 | 46 | 22 |  |  | 43770.1042 | 50 | 50
2019-11-01 03:00 | 46 | 22 |  |  | 43770.125 | 50 | 50
2019-11-01 03:30 | 46 | 23 |  |  | 43770.1458 | 51 | 51
2019-11-01 04:00 | 46 | 23 |  |  | 43770.1667 | 52 | 52
2019-11-01 04:30 | 47 | 25 |  |  | 43770.1875 | 54 | 54
2019-11-01 05:00 | 48 | 27 |  |  | 43770.2083 | 57 | 57
2019-11-01 05:30 | 50 | 30 |  |  | 43770.2292 | 62 | 62
2019-11-01 06:00 | 51 | 33 |  |  | 43770.25 | 66 | 65
2019-11-01 06:30 | 49 | 33 |  |  | 43770.2708 | 72 | 72
2019-11-01 07:00 | 51 | 38 |  |  | 43770.2917 | 80 | 80
2019-11-01 07:30 | 52 | 41 |  |  | 43770.3125 | 85 | 84
2019-11-01 08:00 | 50 | 39 |  |  | 43770.3333 | 85 | 84
2019-11-01 08:30 | 48 | 37 |  |  | 43770.3542 | 85 | 84
2019-11-01 09:00 | 45 | 33 |  |  | 43770.375 | 84 | 83
2019-11-01 09:30 | 45 | 34 |  |  | 43770.3958 | 84 | 83
2019-11-01 10:00 | 46 | 35 |  |  | 43770.4167 | 79 | 78
2019-11-01 10:30 | 55 | 45 |  |  | 43770.4375 | 69 | 67
2019-11-01 11:00 | 56 | 46 |  |  | 43770.4583 | 79 | 78
2019-11-01 11:30 | 60 | 52 |  |  | 43770.4792 | 73 | 72
2019-11-01 12:00 | 58 | 48 |  |  | 43770.5 | 69 | 68
2019-11-01 12:30 | 59 | 49 |  |  | 43770.5208 | 69 | 68
2019-11-01 13:00 | 58 | 48 |  |  | 43770.5417 | 66 | 66
2019-11-01 13:30 | 58 | 48 |  |  | 43770.5625 | 68 | 67
2019-11-01 14:00 | 58 | 48 |  |  | 43770.5833 | 68 | 67
2019-11-01 14:30 | 53 | 42 |  |  | 43770.6042 | 65 | 64
2019-11-01 15:00 | 53 | 41 |  |  | 43770.625 | 63 | 62
2019-11-01 15:30 | 55 | 42 |  |  | 43770.6458 | 61 | 60
2019-11-01 16:00 | 54 | 38 |  |  | 43770.6667 | 59 | 58
2019-11-01 16:30 | 58 | 44 |  |  | 43770.6875 | 64 | 64
2019-11-01 17:00 | 62 | 49 |  |  | 43770.7083 | 69 | 69
2019-11-01 17:30 | 64 | 51 |  |  | 43770.7292 | 69 | 69
2019-11-01 18:00 | 65 | 51 |  |  | 43770.75 | 69 | 69
2019-11-01 18:30 | 65 | 52 |  |  | 43770.7708 | 69 | 69
2019-11-01 19:00 | 68 | 56 |  |  | 43770.7917 | 72 | 72
2019-11-01 19:30 | 66 | 53 |  |  | 43770.8125 | 69 | 69
2019-11-01 20:00 | 67 | 52 |  |  | 43770.8333 | 67 | 67
2019-11-01 20:30 | 67 | 52 |  |  | 43770.8542 | 68 | 67
2019-11-01 21:00 | 65 | 49 |  |  | 43770.875 | 63 | 63
2019-11-01 21:30 | 62 | 46 |  |  | 43770.8958 | 60 | 60
2019-11-01 22:00 | 62 | 45 |  |  | 43770.9167 | 60 | 59
2019-11-01 22:30 | 61 | 43 |  |  | 43770.9375 | 58 | 58
2019-11-01 23:00 | 62 | 42 |  |  | 43770.9583 | 57 | 56
2019-11-01 23:30 | 62 | 42 |  |  | 43770.9792 | 57 | 56
2019-11-02 | 60 | 36 |  |  | 43771 | 51 | 50
2019-11-02 00:30 | 59 | 34 |  |  | 43771.0208 | 49 | 47
2019-11-02 01:00 | 60 | 31 |  |  | 43771.0417 | 45 | 42
2019-11-02 01:30 | 62 | 30 |  |  | 43771.0625 | 45 | 41
2019-11-02 02:00 | 60 | 30 |  |  | 43771.0833 | 42 | 40
2019-11-02 02:30 | 55 | 27 |  |  | 43771.1042 | 38 | 37
2019-11-02 03:00 | 53 | 26 |  |  | 43771.125 | 35 | 35
2019-11-02 03:30 | 53 | 26 |  |  | 43771.1458 | 36 | 36
2019-11-02 04:00 | 51 | 24 |  |  | 43771.1667 | 33 | 33
2019-11-02 04:30 | 52 | 25 |  |  | 43771.1875 | 35 | 35
2019-11-02 05:00 | 55 | 29 |  |  | 43771.2083 | 39 | 39
2019-11-02 05:30 | 55 | 27 |  |  | 43771.2292 | 37 | 37
2019-11-02 06:00 | 55 | 26 |  |  | 43771.25 | 37 | 37
2019-11-02 06:30 | 53 | 22 |  |  | 43771.2708 | 37 | 37
2019-11-02 07:00 | 49 | 19 |  |  | 43771.2917 | 33 | 33
2019-11-02 07:30 | 49 | 19 |  |  | 43771.3125 | 35 | 35
2019-11-02 08:00 | 48 | 21 |  |  | 43771.3333 | 38 | 37
2019-11-02 08:30 | 49 | 24 |  |  | 43771.3542 | 41 | 41
2019-11-02 09:00 | 50 | 27 |  |  | 43771.375 | 44 | 44
2019-11-02 09:30 | 53 | 29 |  |  | 43771.3958 | 45 | 45
2019-11-02 10:00 | 56 | 35 |  |  | 43771.4167 | 49 | 49
2019-11-02 10:30 | 48 | 31 |  |  | 43771.4375 | 48 | 47
2019-11-02 11:00 | 40 | 30 |  |  | 43771.4583 | 45 | 44
2019-11-02 11:30 | 42 | 31 |  |  | 43771.4792 | 51 | 50
2019-11-02 12:00 | 40 | 29 |  |  | 43771.5 | 43 | 41
2019-11-02 12:30 | 38 | 25 |  |  | 43771.5208 | 45 | 43
2019-11-02 13:00 | 39 | 28 |  |  | 43771.5417 | 48 | 46
2019-11-02 13:30 | 41 | 31 |  |  | 43771.5625 | 44 | 42
2019-11-02 14:00 | 41 | 31 |  |  | 43771.5833 | 40 | 38
2019-11-02 14:30 | 39 | 29 |  |  | 43771.6042 | 42 | 40
2019-11-02 15:00 | 37 | 25 |  |  | 43771.625 | 43 | 41
2019-11-02 15:30 | 40 | 28 |  |  | 43771.6458 | 46 | 44
2019-11-02 16:00 | 42 | 31 |  |  | 43771.6667 | 48 | 47
2019-11-02 16:30 | 42 | 31 |  |  | 43771.6875 | 49 | 48
2019-11-02 17:00 | 46 | 36 |  |  | 43771.7083 | 54 | 53
2019-11-02 17:30 | 48 | 39 |  |  | 43771.7292 | 55 | 54
2019-11-02 18:00 | 52 | 43 |  |  | 43771.75 | 59 | 59
2019-11-02 18:30 | 57 | 47 |  |  | 43771.7708 | 64 | 63
2019-11-02 19:00 | 61 | 52 |  |  | 43771.7917 | 69 | 68
2019-11-02 19:30 | 59 | 50 |  |  | 43771.8125 | 67 | 67
2019-11-02 20:00 | 58 | 50 |  |  | 43771.8333 | 66 | 65
2019-11-02 20:30 | 57 | 49 |  |  | 43771.8542 | 67 | 65
2019-11-02 21:00 | 53 | 45 |  |  | 43771.875 | 62 | 61
2019-11-02 21:30 | 52 | 42 |  |  | 43771.8958 | 58 | 57
2019-11-02 22:00 | 51 | 41 |  |  | 43771.9167 | 58 | 57
2019-11-02 22:30 | 52 | 41 |  |  | 43771.9375 | 57 | 56
2019-11-02 23:00 | 58 | 41 |  |  | 43771.9583 | 56 | 55
2019-11-02 23:30 | 57 | 37 |  |  | 43771.9792 | 52 | 51
2019-11-03 | 55 | 34 |  |  | 43772 | 49 | 47
2019-11-03 00:30 | 54 | 32 |  |  | 43772.0208 | 46 | 45
2019-11-03 01:00 | 53 | 31 |  |  | 43772.0417 | 44 | 43
2019-11-03 01:30 | 54 | 30 |  |  | 43772.0625 | 44 | 42
2019-11-03 02:00 | 56 | 30 |  |  | 43772.0833 | 44 | 42
2019-11-03 02:30 | 55 | 30 |  |  | 43772.1042 | 45 | 42
2019-11-03 03:00 | 55 | 30 |  |  | 43772.125 | 44 | 41
2019-11-03 03:30 | 54 | 28 |  |  | 43772.1458 | 44 | 40
2019-11-03 04:00 | 52 | 25 |  |  | 43772.1667 | 41 | 36
2019-11-03 04:30 | 52 | 25 |  |  | 43772.1875 | 43 | 38
2019-11-03 05:00 | 52 | 26 |  |  | 43772.2083 | 42 | 37
2019-11-03 05:30 | 53 | 25 |  |  | 43772.2292 | 42 | 38
2019-11-03 06:00 | 52 | 24 |  |  | 43772.25 | 41 | 36
2019-11-03 06:30 | 51 | 20 |  |  | 43772.2708 | 37 | 32
2019-11-03 07:00 | 50 | 17 |  |  | 43772.2917 | 37 | 32
2019-11-03 07:30 | 49 | 16 |  |  | 43772.3125 | 39 | 34
2019-11-03 08:00 | 48 | 18 |  |  | 43772.3333 | 40 | 34
2019-11-03 08:30 | 49 | 24 |  |  | 43772.3542 | 44 | 38
2019-11-03 09:00 | 48 | 25 |  |  | 43772.375 | 48 | 42
2019-11-03 09:30 | 47 | 25 |  |  | 43772.3958 | 51 | 44
2019-11-03 10:00 | 47 | 25 |  |  | 43772.4167 | 48 | 41
2019-11-03 10:30 | 48 | 28 |  |  | 43772.4375 | 48 | 40
2019-11-03 11:00 | 45 | 21 |  |  | 43772.4583 | 45 | 35
2019-11-03 11:30 | 44 | 19 |  |  | 43772.4792 | 45 | 35
2019-11-03 12:00 | 43 | 17 |  |  | 43772.5 | 43 | 33
2019-11-03 12:30 | 42 | 14 |  |  | 43772.5208 | 40 | 30
2019-11-03 13:00 | 42 | 16 |  |  | 43772.5417 | 39 | 27
2019-11-03 13:30 | 42 | 15 |  |  | 43772.5625 | 40 | 29
2019-11-03 14:00 | 42 | 16 |  |  | 43772.5833 | 41 | 30
2019-11-03 14:30 | 43 | 17 |  |  | 43772.6042 | 42 | 31
2019-11-03 15:00 | 46 | 21 |  |  | 43772.625 | 42 | 35
2019-11-03 15:30 | 50 | 27 |  |  | 43772.6458 | 46 | 41
2019-11-03 16:00 | 53 | 31 |  |  | 43772.6667 | 49 | 45
2019-11-03 16:30 | 54 | 33 |  |  | 43772.6875 | 51 | 47
2019-11-03 17:00 | 57 | 41 |  |  | 43772.7083 | 59 | 54
2019-11-03 17:30 | 65 | 49 |  |  | 43772.7292 | 65 | 62
2019-11-03 18:00 | 70 | 55 |  |  | 43772.75 | 72 | 69
2019-11-03 18:30 | 74 | 59 |  |  | 43772.7708 | 75 | 73
2019-11-03 19:00 | 93 | 62 |  |  | 43772.7917 | 84 | 79
2019-11-03 19:30 | 93 | 61 |  |  | 43772.8125 | 83 | 77
2019-11-03 20:00 | 95 | 60 |  |  | 43772.8333 | 80 | 76
2019-11-03 20:30 | 93 | 57 |  |  | 43772.8542 | 77 | 75
2019-11-03 21:00 | 77 | 53 |  |  | 43772.875 | 68 | 68
2019-11-03 21:30 | 74 | 50 |  |  | 43772.8958 | 65 | 65
2019-11-03 22:00 | 73 | 48 |  |  | 43772.9167 | 63 | 63
2019-11-03 22:30 | 73 | 46 |  |  | 43772.9375 | 62 | 62
2019-11-03 23:00 | 73 | 44 |  |  | 43772.9583 | 59 | 59
2019-11-03 23:30 | 71 | 41 |  |  | 43772.9792 | 56 | 55
2019-11-04 | 67 | 34 |  |  | 43773 | 48 | 48
2019-11-04 00:30 | 66 | 32 |  |  | 43773.0208 | 46 | 45
2019-11-04 01:00 | 67 | 33 |  |  | 43773.0417 | 45 | 45
2019-11-04 01:30 | 67 | 36 |  |  | 43773.0625 | 48 | 48
2019-11-04 02:00 | 66 | 37 |  |  | 43773.0833 | 50 | 49
2019-11-04 02:30 | 67 | 38 |  |  | 43773.1042 | 50 | 50
2019-11-04 03:00 | 65 | 36 |  |  | 43773.125 | 49 | 48
2019-11-04 03:30 | 65 | 35 |  |  | 43773.1458 | 48 | 48
2019-11-04 04:00 | 65 | 35 |  |  | 43773.1667 | 47 | 47
2019-11-04 04:30 | 65 | 36 |  |  | 43773.1875 | 49 | 48
2019-11-04 05:00 | 65 | 38 |  |  | 43773.2083 | 51 | 50
2019-11-04 05:30 | 64 | 37 |  |  | 43773.2292 | 49 | 48
2019-11-04 06:00 | 63 | 37 |  |  | 43773.25 | 50 | 49
2019-11-04 06:30 | 70 | 38 |  |  | 43773.2708 | 58 | 54
2019-11-04 07:00 | 73 | 40 |  |  | 43773.2917 | 62 | 56
2019-11-04 07:30 | 89 | 59 |  |  | 43773.3125 | 71 | 59
2019-11-04 08:00 | 112 | 90 |  |  | 43773.3333 | 63 | 49
2019-11-04 08:30 | 101 | 91 |  |  | 43773.3542 | 53 | 47
2019-11-04 09:00 | 93 | 91 |  |  | 43773.375 | 51 | 51
2019-11-04 09:30 | 85 | 82 |  |  | 43773.3958 | 49 | 49
2019-11-04 10:00 | 77 | 75 |  |  | 43773.4167 | 41 | 41
2019-11-04 10:30 | 80 | 78 |  |  | 43773.4375 | 42 | 42
2019-11-04 11:00 | 84 | 83 |  |  | 43773.4583 | 49 | 48
2019-11-04 11:30 | 83 | 82 |  |  | 43773.4792 | 45 | 43
2019-11-04 12:00 | 86 | 85 |  |  | 43773.5 | 44 | 40
2019-11-04 12:30 | 98 | 97 |  |  | 43773.5208 | 54 | 51
2019-11-04 13:00 | 100 | 99 |  |  | 43773.5417 | 53 | 51
2019-11-04 13:30 | 103 | 102 |  |  | 43773.5625 | 54 | 52
2019-11-04 14:00 | 100 | 99 |  |  | 43773.5833 | 53 | 51
2019-11-04 14:30 | 95 | 94 |  |  | 43773.6042 | 45 | 43
2019-11-04 15:00 | 96 | 94 |  |  | 43773.625 | 46 | 43
2019-11-04 15:30 | 99 | 97 |  |  | 43773.6458 | 46 | 42
2019-11-04 16:00 | 108 | 106 |  |  | 43773.6667 | 47 | 44
2019-11-04 16:30 | 107 | 104 |  |  | 43773.6875 | 56 | 53
2019-11-04 17:00 | 114 | 111 |  |  | 43773.7083 | 57 | 55
2019-11-04 17:30 | 116 | 113 |  |  | 43773.7292 | 58 | 55
2019-11-04 18:00 | 114 | 112 |  |  | 43773.75 | 55 | 52
2019-11-04 18:30 | 113 | 110 |  |  | 43773.7708 | 54 | 51
2019-11-04 19:00 | 117 | 114 |  |  | 43773.7917 | 57 | 53
2019-11-04 19:30 | 114 | 111 |  |  | 43773.8125 | 54 | 51
2019-11-04 20:00 | 111 | 108 |  |  | 43773.8333 | 51 | 50
2019-11-04 20:30 | 108 | 106 |  |  | 43773.8542 | 51 | 50
2019-11-04 21:00 | 100 | 100 |  |  | 43773.875 | 47 | 45
2019-11-04 21:30 | 94 | 94 |  |  | 43773.8958 | 44 | 41
2019-11-04 22:00 | 90 | 89 |  |  | 43773.9167 | 42 | 39
2019-11-04 22:30 | 84 | 84 |  |  | 43773.9375 | 39 | 35
2019-11-04 23:00 | 80 | 80 |  |  | 43773.9583 | 36 | 32
2019-11-04 23:30 | 74 | 74 |  |  | 43773.9792 | 32 | 27
2019-11-05 | 66 | 66 |  |  | 43774 | 28 | 23
2019-11-05 00:30 | 64 | 64 |  |  | 43774.0208 | 29 | 26
2019-11-05 01:00 | 63 | 63 |  |  | 43774.0417 | 29 | 25
2019-11-05 01:30 | 63 | 62 |  |  | 43774.0625 | 29 | 26
2019-11-05 02:00 | 61 | 61 |  |  | 43774.0833 | 28 | 25
2019-11-05 02:30 | 61 | 61 |  |  | 43774.1042 | 29 | 25
2019-11-05 03:00 | 59 | 58 |  |  | 43774.125 | 26 | 22
2019-11-05 03:30 | 59 | 59 |  |  | 43774.1458 | 27 | 24
2019-11-05 04:00 | 60 | 59 |  |  | 43774.1667 | 28 | 25
2019-11-05 04:30 | 61 | 60 |  |  | 43774.1875 | 28 | 25
2019-11-05 05:00 | 63 | 62 |  |  | 43774.2083 | 30 | 27
2019-11-05 05:30 | 64 | 63 |  |  | 43774.2292 | 28 | 25
2019-11-05 06:00 | 67 | 66 |  |  | 43774.25 | 30 | 27
2019-11-05 06:30 | 73 | 73 |  |  | 43774.2708 | 34 | 33
2019-11-05 07:00 | 75 | 75 |  |  | 43774.2917 | 37 | 35
2019-11-05 07:30 | 79 | 78 |  |  | 43774.3125 | 39 | 38
2019-11-05 08:00 | 76 | 75 |  |  | 43774.3333 | 38 | 36
2019-11-05 08:30 | 73 | 73 |  |  | 43774.3542 | 37 | 33
2019-11-05 09:00 | 72 | 72 |  |  | 43774.375 | 39 | 35
2019-11-05 09:30 | 72 | 72 |  |  | 43774.3958 | 41 | 37
2019-11-05 10:00 | 74 | 74 |  |  | 43774.4167 | 42 | 38
2019-11-05 10:30 | 78 | 77 |  |  | 43774.4375 | 42 | 39
2019-11-05 11:00 | 84 | 84 |  |  | 43774.4583 | 45 | 42
2019-11-05 11:30 | 84 | 83 |  |  | 43774.4792 | 53 | 51
2019-11-05 12:00 | 82 | 81 |  |  | 43774.5 | 48 | 46
2019-11-05 12:30 | 82 | 81 |  |  | 43774.5208 | 47 | 46
2019-11-05 13:00 | 77 | 76 |  |  | 43774.5417 | 46 | 44
2019-11-05 13:30 | 74 | 74 |  |  | 43774.5625 | 46 | 42
2019-11-05 14:00 | 75 | 75 |  |  | 43774.5833 | 46 | 42
2019-11-05 14:30 | 77 | 77 |  |  | 43774.6042 | 46 | 43
2019-11-05 15:00 | 78 | 78 |  |  | 43774.625 | 44 | 41
2019-11-05 15:30 | 81 | 81 |  |  | 43774.6458 | 46 | 43
2019-11-05 16:00 | 87 | 87 |  |  | 43774.6667 | 48 | 45
2019-11-05 16:30 | 94 | 94 |  |  | 43774.6875 | 52 | 48
2019-11-05 17:00 | 98 | 98 |  |  | 43774.7083 | 53 | 49
2019-11-05 17:30 | 101 | 101 |  |  | 43774.7292 | 56 | 51
2019-11-05 18:00 | 101 | 101 |  |  | 43774.75 | 54 | 49
2019-11-05 18:30 | 99 | 99 |  |  | 43774.7708 | 52 | 46
2019-11-05 19:00 | 103 | 103 |  |  | 43774.7917 | 54 | 47
2019-11-05 19:30 | 101 | 101 |  |  | 43774.8125 | 52 | 45
2019-11-05 20:00 | 98 | 97 |  |  | 43774.8333 | 47 | 42
2019-11-05 20:30 | 94 | 94 |  |  | 43774.8542 | 45 | 41
2019-11-05 21:00 | 92 | 91 |  |  | 43774.875 | 41 | 41
2019-11-05 21:30 | 86 | 86 |  |  | 43774.8958 | 37 | 36
2019-11-05 22:00 | 82 | 82 |  |  | 43774.9167 | 37 | 35
2019-11-05 22:30 | 79 | 79 |  |  | 43774.9375 | 37 | 35
2019-11-05 23:00 | 76 | 75 |  |  | 43774.9583 | 35 | 31
2019-11-05 23:30 | 69 | 68 |  |  | 43774.9792 | 32 | 29
2019-11-06 | 63 | 63 |  |  | 43775 | 31 | 26
2019-11-06 00:30 | 61 | 61 |  |  | 43775.0208 | 29 | 25
2019-11-06 01:00 | 59 | 59 |  |  | 43775.0417 | 27 | 24
2019-11-06 01:30 | 58 | 57 |  |  | 43775.0625 | 24 | 22
2019-11-06 02:00 | 55 | 55 |  |  | 43775.0833 | 23 | 20
2019-11-06 02:30 | 55 | 54 |  |  | 43775.1042 | 21 | 20
2019-11-06 03:00 | 55 | 54 |  |  | 43775.125 | 20 | 18
2019-11-06 03:30 | 55 | 54 |  |  | 43775.1458 | 21 | 19
2019-11-06 04:00 | 56 | 55 |  |  | 43775.1667 | 22 | 20
2019-11-06 04:30 | 56 | 56 |  |  | 43775.1875 | 25 | 20
2019-11-06 05:00 | 58 | 58 |  |  | 43775.2083 | 27 | 22
2019-11-06 05:30 | 59 | 59 |  |  | 43775.2292 | 25 | 20
2019-11-06 06:00 | 60 | 60 |  |  | 43775.25 | 25 | 20
2019-11-06 06:30 | 63 | 63 |  |  | 43775.2708 | 27 | 21
2019-11-06 07:00 | 64 | 63 |  |  | 43775.2917 | 30 | 18
2019-11-06 07:30 | 65 | 65 |  |  | 43775.3125 | 30 | 21
2019-11-06 08:00 | 64 | 64 |  |  | 43775.3333 | 30 | 23
2019-11-06 08:30 | 62 | 62 |  |  | 43775.3542 | 30 | 23
2019-11-06 09:00 | 62 | 62 |  |  | 43775.375 | 29 | 27
2019-11-06 09:30 | 64 | 62 |  |  | 43775.3958 | 32 | 31
2019-11-06 10:00 | 63 | 61 |  |  | 43775.4167 | 30 | 29
2019-11-06 10:30 | 66 | 64 |  |  | 43775.4375 | 34 | 33
2019-11-06 11:00 | 68 | 66 |  |  | 43775.4583 | 37 | 36
2019-11-06 11:30 | 68 | 67 |  |  | 43775.4792 | 39 | 36
2019-11-06 12:00 | 70 | 69 |  |  | 43775.5 | 42 | 39
2019-11-06 12:30 | 67 | 66 |  |  | 43775.5208 | 37 | 35
2019-11-06 13:00 | 68 | 67 |  |  | 43775.5417 | 36 | 34
2019-11-06 13:30 | 72 | 71 |  |  | 43775.5625 | 39 | 36
2019-11-06 14:00 | 75 | 75 |  |  | 43775.5833 | 40 | 37
2019-11-06 14:30 | 79 | 78 |  |  | 43775.6042 | 42 | 39
2019-11-06 15:00 | 79 | 79 |  |  | 43775.625 | 38 | 37
2019-11-06 15:30 | 81 | 81 |  |  | 43775.6458 | 37 | 36
2019-11-06 16:00 | 85 | 85 |  |  | 43775.6667 | 39 | 38
2019-11-06 16:30 | 91 | 91 |  |  | 43775.6875 | 41 | 41
2019-11-06 17:00 | 93 | 93 |  |  | 43775.7083 | 41 | 40
2019-11-06 17:30 | 96 | 96 |  |  | 43775.7292 | 42 | 42
2019-11-06 18:00 | 100 | 100 |  |  | 43775.75 | 48 | 48
2019-11-06 18:30 | 101 | 101 |  |  | 43775.7708 | 48 | 48
2019-11-06 19:00 | 105 | 105 |  |  | 43775.7917 | 50 | 50
2019-11-06 19:30 | 103 | 103 |  |  | 43775.8125 | 48 | 48
2019-11-06 20:00 | 101 | 101 |  |  | 43775.8333 | 47 | 46
2019-11-06 20:30 | 100 | 100 |  |  | 43775.8542 | 49 | 48
2019-11-06 21:00 | 95 | 95 |  |  | 43775.875 | 49 | 46
2019-11-06 21:30 | 90 | 90 |  |  | 43775.8958 | 45 | 43
2019-11-06 22:00 | 88 | 88 |  |  | 43775.9167 | 48 | 45
2019-11-06 22:30 | 86 | 86 |  |  | 43775.9375 | 48 | 45
2019-11-06 23:00 | 83 | 83 |  |  | 43775.9583 | 44 | 41
2019-11-06 23:30 | 79 | 79 |  |  | 43775.9792 | 41 | 40
2019-11-07 | 73 | 73 |  |  | 43776 | 38 | 38
2019-11-07 00:30 | 70 | 69 |  |  | 43776.0208 | 39 | 38
2019-11-07 01:00 | 68 | 67 |  |  | 43776.0417 | 39 | 38
2019-11-07 01:30 | 65 | 64 |  |  | 43776.0625 | 37 | 35
2019-11-07 02:00 | 64 | 64 |  |  | 43776.0833 | 37 | 36
2019-11-07 02:30 | 66 | 65 |  |  | 43776.1042 | 40 | 39
2019-11-07 03:00 | 66 | 65 |  |  | 43776.125 | 40 | 39
2019-11-07 03:30 | 65 | 64 |  |  | 43776.1458 | 39 | 38
2019-11-07 04:00 | 64 | 64 |  |  | 43776.1667 | 38 | 37
2019-11-07 04:30 | 64 | 63 |  |  | 43776.1875 | 36 | 36
2019-11-07 05:00 | 66 | 65 |  |  | 43776.2083 | 37 | 37
2019-11-07 05:30 | 68 | 67 |  |  | 43776.2292 | 36 | 36
2019-11-07 06:00 | 67 | 66 |  |  | 43776.25 | 32 | 31
2019-11-07 06:30 | 68 | 67 |  |  | 43776.2708 | 28 | 28
2019-11-07 07:00 | 72 | 71 |  |  | 43776.2917 | 34 | 34
2019-11-07 07:30 | 73 | 73 |  |  | 43776.3125 | 36 | 35
2019-11-07 08:00 | 72 | 72 |  |  | 43776.3333 | 36 | 36
2019-11-07 08:30 | 69 | 69 |  |  | 43776.3542 | 34 | 34
2019-11-07 09:00 | 67 | 67 |  |  | 43776.375 | 34 | 34
2019-11-07 09:30 | 68 | 68 |  |  | 43776.3958 | 36 | 36
2019-11-07 10:00 | 68 | 68 |  |  | 43776.4167 | 37 | 36
2019-11-07 10:30 | 69 | 69 |  |  | 43776.4375 | 37 | 36
2019-11-07 11:00 | 72 | 71 |  |  | 43776.4583 | 38 | 38
2019-11-07 11:30 | 73 | 73 |  |  | 43776.4792 | 38 | 38
2019-11-07 12:00 | 75 | 74 |  |  | 43776.5 | 39 | 39
2019-11-07 12:30 | 77 | 77 |  |  | 43776.5208 | 40 | 39
2019-11-07 13:00 | 80 | 80 |  |  | 43776.5417 | 43 | 42
2019-11-07 13:30 | 84 | 83 |  |  | 43776.5625 | 42 | 41
2019-11-07 14:00 | 89 | 88 |  |  | 43776.5833 | 45 | 45
2019-11-07 14:30 | 90 | 90 |  |  | 43776.6042 | 43 | 42
2019-11-07 15:00 | 91 | 91 |  |  | 43776.625 | 40 | 38
2019-11-07 15:30 | 94 | 93 |  |  | 43776.6458 | 40 | 38
2019-11-07 16:00 | 100 | 100 |  |  | 43776.6667 | 43 | 41
2019-11-07 16:30 | 101 | 101 |  |  | 43776.6875 | 41 | 38
2019-11-07 17:00 | 105 | 105 |  |  | 43776.7083 | 45 | 42
2019-11-07 17:30 | 106 | 106 |  |  | 43776.7292 | 48 | 46
2019-11-07 18:00 | 107 | 107 |  |  | 43776.75 | 49 | 49
2019-11-07 18:30 | 108 | 108 |  |  | 43776.7708 | 51 | 51
2019-11-07 19:00 | 112 | 112 |  |  | 43776.7917 | 54 | 53
2019-11-07 19:30 | 109 | 109 |  |  | 43776.8125 | 51 | 50
2019-11-07 20:00 | 107 | 107 |  |  | 43776.8333 | 51 | 50
2019-11-07 20:30 | 106 | 106 |  |  | 43776.8542 | 53 | 51
2019-11-07 21:00 | 101 | 101 |  |  | 43776.875 | 51 | 49
2019-11-07 21:30 | 95 | 95 |  |  | 43776.8958 | 47 | 44
2019-11-07 22:00 | 92 | 91 |  |  | 43776.9167 | 48 | 45
2019-11-07 22:30 | 88 | 88 |  |  | 43776.9375 | 46 | 44
2019-11-07 23:00 | 84 | 83 |  |  | 43776.9583 | 42 | 39
2019-11-07 23:30 | 78 | 78 |  |  | 43776.9792 | 38 | 35
2019-11-08 | 72 | 72 |  |  | 43777 | 36 | 33
2019-11-08 00:30 | 69 | 68 |  |  | 43777.0208 | 37 | 33
2019-11-08 01:00 | 66 | 66 |  |  | 43777.0417 | 37 | 33
2019-11-08 01:30 | 65 | 65 |  |  | 43777.0625 | 38 | 34
2019-11-08 02:00 | 64 | 64 |  |  | 43777.0833 | 37 | 35
2019-11-08 02:30 | 64 | 64 |  |  | 43777.1042 | 34 | 33
2019-11-08 03:00 | 64 | 64 |  |  | 43777.125 | 36 | 35
2019-11-08 03:30 | 64 | 64 |  |  | 43777.1458 | 36 | 35
2019-11-08 04:00 | 64 | 64 |  |  | 43777.1667 | 35 | 34
2019-11-08 04:30 | 62 | 62 |  |  | 43777.1875 | 33 | 32
2019-11-08 05:00 | 63 | 63 |  |  | 43777.2083 | 33 | 32
2019-11-08 05:30 | 65 | 65 |  |  | 43777.2292 | 32 | 31
2019-11-08 06:00 | 65 | 65 |  |  | 43777.25 | 29 | 29
2019-11-08 06:30 | 67 | 67 |  |  | 43777.2708 | 28 | 28
2019-11-08 07:00 | 69 | 68 |  |  | 43777.2917 | 28 | 28
2019-11-08 07:30 | 72 | 71 |  |  | 43777.3125 | 31 | 31
2019-11-08 08:00 | 74 | 72 |  |  | 43777.3333 | 35 | 34
2019-11-08 08:30 | 63 | 61 |  |  | 43777.3542 | 48 | 48
2019-11-08 09:00 | 46 | 44 |  |  | 43777.375 | 67 | 67
2019-11-08 09:30 | 49 | 47 |  |  | 43777.3958 | 72 | 71
2019-11-08 10:00 | 52 | 50 |  |  | 43777.4167 | 75 | 75
2019-11-08 10:30 | 54 | 53 |  |  | 43777.4375 | 76 | 76
2019-11-08 11:00 | 58 | 57 |  |  | 43777.4583 | 80 | 80
2019-11-08 11:30 | 60 | 60 |  |  | 43777.4792 | 82 | 82
2019-11-08 12:00 | 61 | 60 |  |  | 43777.5 | 83 | 83
2019-11-08 12:30 | 63 | 62 |  |  | 43777.5208 | 85 | 85
2019-11-08 13:00 | 68 | 66 |  |  | 43777.5417 | 89 | 88
2019-11-08 13:30 | 67 | 66 |  |  | 43777.5625 | 86 | 85
2019-11-08 14:00 | 66 | 66 |  |  | 43777.5833 | 89 | 84
2019-11-08 14:30 | 70 | 70 |  |  | 43777.6042 | 92 | 88
2019-11-08 15:00 | 70 | 70 |  |  | 43777.625 | 95 | 88
2019-11-08 15:30 | 72 | 72 |  |  | 43777.6458 | 96 | 90
2019-11-08 16:00 | 79 | 79 |  |  | 43777.6667 | 99 | 95
2019-11-08 16:30 | 84 | 84 |  |  | 43777.6875 | 104 | 99
2019-11-08 17:00 | 87 | 87 |  |  | 43777.7083 | 108 | 103
2019-11-08 17:30 | 87 | 87 |  |  | 43777.7292 | 108 | 103
2019-11-08 18:00 | 84 | 84 |  |  | 43777.75 | 104 | 99
2019-11-08 18:30 | 84 | 83 |  |  | 43777.7708 | 98 | 97
2019-11-08 19:00 | 85 | 84 |  |  | 43777.7917 | 99 | 98
2019-11-08 19:30 | 82 | 81 |  |  | 43777.8125 | 96 | 95
2019-11-08 20:00 | 78 | 78 |  |  | 43777.8333 | 94 | 93
2019-11-08 20:30 | 74 | 73 |  |  | 43777.8542 | 90 | 89
2019-11-08 21:00 | 68 | 67 |  |  | 43777.875 | 83 | 83
2019-11-08 21:30 | 64 | 63 |  |  | 43777.8958 | 79 | 78
2019-11-08 22:00 | 62 | 61 |  |  | 43777.9167 | 78 | 77
2019-11-08 22:30 | 59 | 59 |  |  | 43777.9375 | 76 | 75
2019-11-08 23:00 | 58 | 57 |  |  | 43777.9583 | 73 | 73
2019-11-08 23:30 | 54 | 53 |  |  | 43777.9792 | 69 | 68
2019-11-09 | 50 | 49 |  |  | 43778 | 64 | 64
2019-11-09 00:30 | 47 | 47 |  |  | 43778.0208 | 62 | 62
2019-11-09 01:00 | 46 | 46 |  |  | 43778.0417 | 61 | 60
2019-11-09 01:30 | 44 | 44 |  |  | 43778.0625 | 59 | 58
2019-11-09 02:00 | 43 | 43 |  |  | 43778.0833 | 57 | 56
2019-11-09 02:30 | 43 | 43 |  |  | 43778.1042 | 56 | 55
2019-11-09 03:00 | 42 | 41 |  |  | 43778.125 | 56 | 55
2019-11-09 03:30 | 40 | 40 |  |  | 43778.1458 | 55 | 54
2019-11-09 04:00 | 40 | 40 |  |  | 43778.1667 | 56 | 55
2019-11-09 04:30 | 42 | 41 |  |  | 43778.1875 | 56 | 55
2019-11-09 05:00 | 41 | 41 |  |  | 43778.2083 | 55 | 54
2019-11-09 05:30 | 41 | 41 |  |  | 43778.2292 | 56 | 55
2019-11-09 06:00 | 39 | 39 |  |  | 43778.25 | 54 | 53
2019-11-09 06:30 | 38 | 37 |  |  | 43778.2708 | 53 | 53
2019-11-09 07:00 | 37 | 37 |  |  | 43778.2917 | 53 | 53
2019-11-09 07:30 | 37 | 36 |  |  | 43778.3125 | 53 | 53
2019-11-09 08:00 | 38 | 37 |  |  | 43778.3333 | 54 | 54
2019-11-09 08:30 | 40 | 39 |  |  | 43778.3542 | 57 | 57
2019-11-09 09:00 | 40 | 38 |  |  | 43778.375 | 56 | 56
2019-11-09 09:30 | 41 | 40 |  |  | 43778.3958 | 57 | 57
2019-11-09 10:00 | 43 | 42 |  |  | 43778.4167 | 58 | 58
2019-11-09 10:30 | 43 | 42 |  |  | 43778.4375 | 59 | 59
2019-11-09 11:00 | 44 | 43 |  |  | 43778.4583 | 60 | 60
2019-11-09 11:30 | 44 | 42 |  |  | 43778.4792 | 59 | 59
2019-11-09 12:00 | 44 | 43 |  |  | 43778.5 | 59 | 59
2019-11-09 12:30 | 45 | 44 |  |  | 43778.5208 | 59 | 58
2019-11-09 13:00 | 47 | 46 |  |  | 43778.5417 | 61 | 61
2019-11-09 13:30 | 49 | 47 |  |  | 43778.5625 | 61 | 61
2019-11-09 14:00 | 51 | 50 |  |  | 43778.5833 | 62 | 62
2019-11-09 14:30 | 54 | 53 |  |  | 43778.6042 | 65 | 65
2019-11-09 15:00 | 56 | 55 |  |  | 43778.625 | 66 | 66
2019-11-09 15:30 | 58 | 57 |  |  | 43778.6458 | 70 | 70
2019-11-09 16:00 | 60 | 59 |  |  | 43778.6667 | 73 | 72
2019-11-09 16:30 | 59 | 59 |  |  | 43778.6875 | 73 | 72
2019-11-09 17:00 | 59 | 59 |  |  | 43778.7083 | 74 | 72
2019-11-09 17:30 | 59 | 59 |  |  | 43778.7292 | 75 | 73
2019-11-09 18:00 | 59 | 59 |  |  | 43778.75 | 77 | 75
2019-11-09 18:30 | 59 | 59 |  |  | 43778.7708 | 78 | 76
2019-11-09 19:00 | 63 | 63 |  |  | 43778.7917 | 82 | 80
2019-11-09 19:30 | 62 | 62 |  |  | 43778.8125 | 80 | 78
2019-11-09 20:00 | 59 | 59 |  |  | 43778.8333 | 77 | 75
2019-11-09 20:30 | 57 | 57 |  |  | 43778.8542 | 75 | 73
2019-11-09 21:00 | 56 | 56 |  |  | 43778.875 | 74 | 71
2019-11-09 21:30 | 56 | 56 |  |  | 43778.8958 | 74 | 72
2019-11-09 22:00 | 54 | 54 |  |  | 43778.9167 | 73 | 71
2019-11-09 22:30 | 55 | 55 |  |  | 43778.9375 | 74 | 71
2019-11-09 23:00 | 53 | 53 |  |  | 43778.9583 | 71 | 68
2019-11-09 23:30 | 50 | 50 |  |  | 43778.9792 | 68 | 65
2019-11-10 | 47 | 47 |  |  | 43779 | 62 | 61
2019-11-10 00:30 | 45 | 44 |  |  | 43779.0208 | 59 | 58
2019-11-10 01:00 | 42 | 42 |  |  | 43779.0417 | 56 | 55
2019-11-10 01:30 | 41 | 41 |  |  | 43779.0625 | 55 | 53
2019-11-10 02:00 | 40 | 40 |  |  | 43779.0833 | 54 | 51
2019-11-10 02:30 | 38 | 38 |  |  | 43779.1042 | 53 | 50
2019-11-10 03:00 | 39 | 38 |  |  | 43779.125 | 51 | 49
2019-11-10 03:30 | 38 | 38 |  |  | 43779.1458 | 52 | 49
2019-11-10 04:00 | 38 | 38 |  |  | 43779.1667 | 52 | 50
2019-11-10 04:30 | 38 | 38 |  |  | 43779.1875 | 51 | 49
2019-11-10 05:00 | 37 | 37 |  |  | 43779.2083 | 51 | 49
2019-11-10 05:30 | 35 | 35 |  |  | 43779.2292 | 49 | 47
2019-11-10 06:00 | 33 | 33 |  |  | 43779.25 | 47 | 46
2019-11-10 06:30 | 32 | 32 |  |  | 43779.2708 | 45 | 45
2019-11-10 07:00 | 30 | 30 |  |  | 43779.2917 | 44 | 44
2019-11-10 07:30 | 29 | 29 |  |  | 43779.3125 | 42 | 42
2019-11-10 08:00 | 28 | 28 |  |  | 43779.3333 | 42 | 42
2019-11-10 08:30 | 30 | 29 |  |  | 43779.3542 | 44 | 44
2019-11-10 09:00 | 31 | 30 |  |  | 43779.375 | 44 | 44
2019-11-10 09:30 | 31 | 30 |  |  | 43779.3958 | 44 | 44
2019-11-10 10:00 | 32 | 31 |  |  | 43779.4167 | 46 | 46
2019-11-10 10:30 | 33 | 32 |  |  | 43779.4375 | 46 | 46
2019-11-10 11:00 | 34 | 32 |  |  | 43779.4583 | 47 | 47
2019-11-10 11:30 | 34 | 33 |  |  | 43779.4792 | 47 | 47
2019-11-10 12:00 | 35 | 34 |  |  | 43779.5 | 47 | 47
2019-11-10 12:30 | 41 | 40 |  |  | 43779.5208 | 55 | 55
2019-11-10 13:00 | 43 | 42 |  |  | 43779.5417 | 55 | 55
2019-11-10 13:30 | 44 | 43 |  |  | 43779.5625 | 56 | 56
2019-11-10 14:00 | 46 | 44 |  |  | 43779.5833 | 57 | 57
2019-11-10 14:30 | 48 | 47 |  |  | 43779.6042 | 59 | 59
2019-11-10 15:00 | 50 | 49 |  |  | 43779.625 | 61 | 60
2019-11-10 15:30 | 53 | 52 |  |  | 43779.6458 | 65 | 64
2019-11-10 16:00 | 57 | 56 |  |  | 43779.6667 | 69 | 69
2019-11-10 16:30 | 59 | 58 |  |  | 43779.6875 | 69 | 69
2019-11-10 17:00 | 57 | 56 |  |  | 43779.7083 | 65 | 65
2019-11-10 17:30 | 58 | 57 |  |  | 43779.7292 | 66 | 66
2019-11-10 18:00 | 60 | 60 |  |  | 43779.75 | 70 | 69
2019-11-10 18:30 | 59 | 59 |  |  | 43779.7708 | 73 | 72
2019-11-10 19:00 | 60 | 60 |  |  | 43779.7917 | 75 | 75
2019-11-10 19:30 | 58 | 58 |  |  | 43779.8125 | 73 | 73
2019-11-10 20:00 | 56 | 56 |  |  | 43779.8333 | 71 | 70
2019-11-10 20:30 | 57 | 57 |  |  | 43779.8542 | 73 | 72
2019-11-10 21:00 | 55 | 54 |  |  | 43779.875 | 70 | 69
2019-11-10 21:30 | 54 | 53 |  |  | 43779.8958 | 69 | 68
2019-11-10 22:00 | 51 | 50 |  |  | 43779.9167 | 67 | 66
2019-11-10 22:30 | 49 | 49 |  |  | 43779.9375 | 65 | 65
2019-11-10 23:00 | 47 | 46 |  |  | 43779.9583 | 60 | 60
2019-11-10 23:30 | 44 | 43 |  |  | 43779.9792 | 58 | 57
2019-11-11 | 41 | 41 |  |  | 43780 | 56 | 55
2019-11-11 00:30 | 40 | 40 |  |  | 43780.0208 | 54 | 53
2019-11-11 01:00 | 38 | 38 |  |  | 43780.0417 | 51 | 50
2019-11-11 01:30 | 38 | 37 |  |  | 43780.0625 | 49 | 49
2019-11-11 02:00 | 36 | 36 |  |  | 43780.0833 | 49 | 48
2019-11-11 02:30 | 37 | 37 |  |  | 43780.1042 | 49 | 48
2019-11-11 03:00 | 36 | 36 |  |  | 43780.125 | 48 | 47
2019-11-11 03:30 | 38 | 37 |  |  | 43780.1458 | 50 | 49
2019-11-11 04:00 | 38 | 38 |  |  | 43780.1667 | 50 | 49
2019-11-11 04:30 | 38 | 38 |  |  | 43780.1875 | 50 | 49
2019-11-11 05:00 | 40 | 39 |  |  | 43780.2083 | 52 | 51
2019-11-11 05:30 | 39 | 38 |  |  | 43780.2292 | 50 | 50
2019-11-11 06:00 | 42 | 41 |  |  | 43780.25 | 53 | 52
2019-11-11 06:30 | 45 | 44 |  |  | 43780.2708 | 59 | 59
2019-11-11 07:00 | 47 | 47 |  |  | 43780.2917 | 64 | 64
2019-11-11 07:30 | 50 | 49 |  |  | 43780.3125 | 68 | 68
2019-11-11 08:00 | 51 | 50 |  |  | 43780.3333 | 70 | 70
2019-11-11 08:30 | 53 | 52 |  |  | 43780.3542 | 73 | 73
2019-11-11 09:00 | 56 | 55 |  |  | 43780.375 | 76 | 76
2019-11-11 09:30 | 57 | 56 |  |  | 43780.3958 | 77 | 77
2019-11-11 10:00 | 56 | 56 |  |  | 43780.4167 | 77 | 76
2019-11-11 10:30 | 54 | 54 |  |  | 43780.4375 | 74 | 74
2019-11-11 11:00 | 53 | 52 |  |  | 43780.4583 | 74 | 73
2019-11-11 11:30 | 55 | 53 |  |  | 43780.4792 | 73 | 73
2019-11-11 12:00 | 54 | 52 |  |  | 43780.5 | 72 | 72
2019-11-11 12:30 | 53 | 51 |  |  | 43780.5208 | 70 | 70
2019-11-11 13:00 | 55 | 52 |  |  | 43780.5417 | 74 | 74
2019-11-11 13:30 | 56 | 54 |  |  | 43780.5625 | 74 | 74
2019-11-11 14:00 | 59 | 56 |  |  | 43780.5833 | 75 | 75
2019-11-11 14:30 | 59 | 57 |  |  | 43780.6042 | 76 | 75
2019-11-11 15:00 | 56 | 55 |  |  | 43780.625 | 77 | 76
2019-11-11 15:30 | 58 | 57 |  |  | 43780.6458 | 78 | 77
2019-11-11 16:00 | 60 | 59 |  |  | 43780.6667 | 79 | 77
2019-11-11 16:30 | 61 | 60 |  |  | 43780.6875 | 79 | 78
2019-11-11 17:00 | 64 | 63 |  |  | 43780.7083 | 82 | 80
2019-11-11 17:30 | 65 | 64 |  |  | 43780.7292 | 82 | 80
2019-11-11 18:00 | 62 | 62 |  |  | 43780.75 | 80 | 77
2019-11-11 18:30 | 63 | 63 |  |  | 43780.7708 | 83 | 79
2019-11-11 19:00 | 68 | 68 |  |  | 43780.7917 | 87 | 84
2019-11-11 19:30 | 68 | 68 |  |  | 43780.8125 | 87 | 84
2019-11-11 20:00 | 65 | 65 |  |  | 43780.8333 | 81 | 79
2019-11-11 20:30 | 66 | 65 |  |  | 43780.8542 | 80 | 78
2019-11-11 21:00 | 61 | 60 |  |  | 43780.875 | 74 | 72
2019-11-11 21:30 | 57 | 56 |  |  | 43780.8958 | 69 | 68
2019-11-11 22:00 | 58 | 55 |  |  | 43780.9167 | 69 | 69
2019-11-11 22:30 | 54 | 51 |  |  | 43780.9375 | 65 | 65
2019-11-11 23:00 | 53 | 50 |  |  | 43780.9583 | 62 | 62
2019-11-11 23:30 | 47 | 45 |  |  | 43780.9792 | 58 | 58
2019-11-12 | 43 | 40 |  |  | 43781 | 55 | 55
2019-11-12 00:30 | 43 | 41 |  |  | 43781.0208 | 55 | 55
2019-11-12 01:00 | 43 | 41 |  |  | 43781.0417 | 54 | 54
2019-11-12 01:30 | 44 | 42 |  |  | 43781.0625 | 54 | 54
2019-11-12 02:00 | 44 | 42 |  |  | 43781.0833 | 54 | 54
2019-11-12 02:30 | 43 | 41 |  |  | 43781.1042 | 54 | 54
2019-11-12 03:00 | 42 | 40 |  |  | 43781.125 | 54 | 54
2019-11-12 03:30 | 42 | 40 |  |  | 43781.1458 | 54 | 54
2019-11-12 04:00 | 42 | 40 |  |  | 43781.1667 | 54 | 54
2019-11-12 04:30 | 42 | 40 |  |  | 43781.1875 | 53 | 53
2019-11-12 05:00 | 43 | 41 |  |  | 43781.2083 | 54 | 54
2019-11-12 05:30 | 42 | 39 |  |  | 43781.2292 | 52 | 52
2019-11-12 06:00 | 43 | 40 |  |  | 43781.25 | 53 | 53
2019-11-12 06:30 | 46 | 42 |  |  | 43781.2708 | 58 | 58
2019-11-12 07:00 | 50 | 45 |  |  | 43781.2917 | 64 | 64
2019-11-12 07:30 | 53 | 48 |  |  | 43781.3125 | 71 | 71
2019-11-12 08:00 | 53 | 50 |  |  | 43781.3333 | 74 | 74
2019-11-12 08:30 | 53 | 49 |  |  | 43781.3542 | 75 | 74
2019-11-12 09:00 | 53 | 49 |  |  | 43781.375 | 75 | 75
2019-11-12 09:30 | 54 | 49 |  |  | 43781.3958 | 74 | 74
2019-11-12 10:00 | 56 | 51 |  |  | 43781.4167 | 74 | 74
2019-11-12 10:30 | 58 | 52 |  |  | 43781.4375 | 76 | 75
2019-11-12 11:00 | 58 | 52 |  |  | 43781.4583 | 75 | 75
2019-11-12 11:30 | 60 | 54 |  |  | 43781.4792 | 76 | 76
2019-11-12 12:00 | 60 | 55 |  |  | 43781.5 | 77 | 77
2019-11-12 12:30 | 57 | 54 |  |  | 43781.5208 | 76 | 76
2019-11-12 13:00 | 58 | 55 |  |  | 43781.5417 | 76 | 76
2019-11-12 13:30 | 60 | 57 |  |  | 43781.5625 | 78 | 78
2019-11-12 14:00 | 61 | 58 |  |  | 43781.5833 | 78 | 78
2019-11-12 14:30 | 62 | 60 |  |  | 43781.6042 | 79 | 79
2019-11-12 15:00 | 62 | 59 |  |  | 43781.625 | 79 | 79
2019-11-12 15:30 | 64 | 61 |  |  | 43781.6458 | 81 | 81
2019-11-12 16:00 | 65 | 63 |  |  | 43781.6667 | 82 | 82
2019-11-12 16:30 | 68 | 67 |  |  | 43781.6875 | 86 | 84
2019-11-12 17:00 | 70 | 70 |  |  | 43781.7083 | 92 | 88
2019-11-12 17:30 | 71 | 70 |  |  | 43781.7292 | 89 | 87
2019-11-12 18:00 | 70 | 69 |  |  | 43781.75 | 85 | 84
2019-11-12 18:30 | 70 | 69 |  |  | 43781.7708 | 85 | 84
2019-11-12 19:00 | 73 | 72 |  |  | 43781.7917 | 89 | 87
2019-11-12 19:30 | 71 | 70 |  |  | 43781.8125 | 85 | 85
2019-11-12 20:00 | 72 | 69 |  |  | 43781.8333 | 83 | 83
2019-11-12 20:30 | 72 | 69 |  |  | 43781.8542 | 82 | 82
2019-11-12 21:00 | 68 | 65 |  |  | 43781.875 | 78 | 78
2019-11-12 21:30 | 64 | 61 |  |  | 43781.8958 | 72 | 72
2019-11-12 22:00 | 62 | 59 |  |  | 43781.9167 | 71 | 71
2019-11-12 22:30 | 59 | 56 |  |  | 43781.9375 | 69 | 69
2019-11-12 23:00 | 53 | 51 |  |  | 43781.9583 | 63 | 63
2019-11-12 23:30 | 48 | 47 |  |  | 43781.9792 | 59 | 59
2019-11-13 | 44 | 43 |  |  | 43782 | 56 | 55
2019-11-13 00:30 | 42 | 41 |  |  | 43782.0208 | 54 | 53
2019-11-13 01:00 | 42 | 41 |  |  | 43782.0417 | 53 | 52
2019-11-13 01:30 | 41 | 40 |  |  | 43782.0625 | 52 | 51
2019-11-13 02:00 | 41 | 40 |  |  | 43782.0833 | 52 | 51
2019-11-13 02:30 | 40 | 40 |  |  | 43782.1042 | 52 | 50
2019-11-13 03:00 | 40 | 39 |  |  | 43782.125 | 51 | 48
2019-11-13 03:30 | 40 | 39 |  |  | 43782.1458 | 52 | 49
2019-11-13 04:00 | 40 | 39 |  |  | 43782.1667 | 50 | 48
2019-11-13 04:30 | 38 | 38 |  |  | 43782.1875 | 50 | 47
2019-11-13 05:00 | 37 | 37 |  |  | 43782.2083 | 49 | 47
2019-11-13 05:30 | 37 | 37 |  |  | 43782.2292 | 51 | 48
2019-11-13 06:00 | 37 | 36 |  |  | 43782.25 | 50 | 49
2019-11-13 06:30 | 41 | 40 |  |  | 43782.2708 | 57 | 56
2019-11-13 07:00 | 43 | 42 |  |  | 43782.2917 | 62 | 61
2019-11-13 07:30 | 45 | 44 |  |  | 43782.3125 | 65 | 65
2019-11-13 08:00 | 47 | 46 |  |  | 43782.3333 | 69 | 68
2019-11-13 08:30 | 46 | 45 |  |  | 43782.3542 | 69 | 68
2019-11-13 09:00 | 48 | 47 |  |  | 43782.375 | 72 | 71
2019-11-13 09:30 | 50 | 49 |  |  | 43782.3958 | 74 | 73
2019-11-13 10:00 | 51 | 51 |  |  | 43782.4167 | 75 | 74
2019-11-13 10:30 | 53 | 52 |  |  | 43782.4375 | 75 | 74
2019-11-13 11:00 | 56 | 55 |  |  | 43782.4583 | 76 | 76
2019-11-13 11:30 | 56 | 55 |  |  | 43782.4792 | 76 | 76
2019-11-13 12:00 | 56 | 55 |  |  | 43782.5 | 78 | 78
2019-11-13 12:30 | 56 | 56 |  |  | 43782.5208 | 78 | 78
2019-11-13 13:00 | 58 | 58 |  |  | 43782.5417 | 80 | 80
2019-11-13 13:30 | 59 | 58 |  |  | 43782.5625 | 82 | 82
2019-11-13 14:00 | 60 | 60 |  |  | 43782.5833 | 86 | 84
2019-11-13 14:30 | 62 | 62 |  |  | 43782.6042 | 92 | 86
2019-11-13 15:00 | 62 | 61 |  |  | 43782.625 | 91 | 86
2019-11-13 15:30 | 61 | 60 |  |  | 43782.6458 | 90 | 85
2019-11-13 16:00 | 62 | 61 |  |  | 43782.6667 | 91 | 85
2019-11-13 16:30 | 63 | 62 |  |  | 43782.6875 | 90 | 85
2019-11-13 17:00 | 64 | 64 |  |  | 43782.7083 | 91 | 86
2019-11-13 17:30 | 63 | 63 |  |  | 43782.7292 | 86 | 83
2019-11-13 18:00 | 61 | 61 |  |  | 43782.75 | 81 | 80
2019-11-13 18:30 | 61 | 60 |  |  | 43782.7708 | 80 | 78
2019-11-13 19:00 | 65 | 65 |  |  | 43782.7917 | 82 | 82
2019-11-13 19:30 | 61 | 61 |  |  | 43782.8125 | 79 | 78
2019-11-13 20:00 | 59 | 59 |  |  | 43782.8333 | 75 | 75
2019-11-13 20:30 | 59 | 59 |  |  | 43782.8542 | 76 | 76
2019-11-13 21:00 | 59 | 58 |  |  | 43782.875 | 74 | 73
2019-11-13 21:30 | 59 | 57 |  |  | 43782.8958 | 73 | 72
2019-11-13 22:00 | 57 | 55 |  |  | 43782.9167 | 72 | 71
2019-11-13 22:30 | 56 | 55 |  |  | 43782.9375 | 72 | 71
2019-11-13 23:00 | 53 | 52 |  |  | 43782.9583 | 68 | 68
2019-11-13 23:30 | 49 | 47 |  |  | 43782.9792 | 64 | 63
2019-11-14 | 44 | 42 |  |  | 43783 | 58 | 57
2019-11-14 00:30 | 41 | 39 |  |  | 43783.0208 | 54 | 53
2019-11-14 01:00 | 39 | 38 |  |  | 43783.0417 | 52 | 51
2019-11-14 01:30 | 41 | 39 |  |  | 43783.0625 | 52 | 51
2019-11-14 02:00 | 41 | 39 |  |  | 43783.0833 | 52 | 52
2019-11-14 02:30 | 39 | 38 |  |  | 43783.1042 | 52 | 51
2019-11-14 03:00 | 39 | 38 |  |  | 43783.125 | 52 | 51
2019-11-14 03:30 | 38 | 37 |  |  | 43783.1458 | 51 | 50
2019-11-14 04:00 | 37 | 36 |  |  | 43783.1667 | 51 | 50
2019-11-14 04:30 | 38 | 36 |  |  | 43783.1875 | 51 | 50
2019-11-14 05:00 | 37 | 35 |  |  | 43783.2083 | 49 | 48
2019-11-14 05:30 | 37 | 36 |  |  | 43783.2292 | 50 | 49
2019-11-14 06:00 | 40 | 38 |  |  | 43783.25 | 53 | 52
2019-11-14 06:30 | 42 | 39 |  |  | 43783.2708 | 60 | 58
2019-11-14 07:00 | 44 | 41 |  |  | 43783.2917 | 64 | 63
2019-11-14 07:30 | 49 | 47 |  |  | 43783.3125 | 72 | 70
2019-11-14 08:00 | 51 | 49 |  |  | 43783.3333 | 75 | 73
2019-11-14 08:30 | 50 | 48 |  |  | 43783.3542 | 74 | 73
2019-11-14 09:00 | 50 | 48 |  |  | 43783.375 | 75 | 74
2019-11-14 09:30 | 49 | 48 |  |  | 43783.3958 | 75 | 74
2019-11-14 10:00 | 49 | 47 |  |  | 43783.4167 | 74 | 72
2019-11-14 10:30 | 51 | 49 |  |  | 43783.4375 | 75 | 74
2019-11-14 11:00 | 51 | 49 |  |  | 43783.4583 | 75 | 74
2019-11-14 11:30 | 51 | 50 |  |  | 43783.4792 | 75 | 74
2019-11-14 12:00 | 51 | 51 |  |  | 43783.5 | 75 | 75
2019-11-14 12:30 | 51 | 50 |  |  | 43783.5208 | 75 | 75
2019-11-14 13:00 | 53 | 52 |  |  | 43783.5417 | 76 | 76
2019-11-14 13:30 | 55 | 54 |  |  | 43783.5625 | 79 | 78
2019-11-14 14:00 | 59 | 58 |  |  | 43783.5833 | 81 | 80
2019-11-14 14:30 | 60 | 60 |  |  | 43783.6042 | 82 | 82
2019-11-14 15:00 | 60 | 60 |  |  | 43783.625 | 82 | 81
2019-11-14 15:30 | 57 | 57 |  |  | 43783.6458 | 80 | 78
2019-11-14 16:00 | 51 | 50 |  |  | 43783.6667 | 75 | 74
2019-11-14 16:30 | 52 | 50 |  |  | 43783.6875 | 76 | 74
2019-11-14 17:00 | 54 | 52 |  |  | 43783.7083 | 79 | 77
2019-11-14 17:30 | 54 | 53 |  |  | 43783.7292 | 78 | 77
2019-11-14 18:00 | 56 | 54 |  |  | 43783.75 | 79 | 78
2019-11-14 18:30 | 55 | 54 |  |  | 43783.7708 | 79 | 77
2019-11-14 19:00 | 59 | 58 |  |  | 43783.7917 | 82 | 81
2019-11-14 19:30 | 58 | 57 |  |  | 43783.8125 | 80 | 79
2019-11-14 20:00 | 56 | 55 |  |  | 43783.8333 | 77 | 76
2019-11-14 20:30 | 54 | 54 |  |  | 43783.8542 | 76 | 75
2019-11-14 21:00 | 54 | 54 |  |  | 43783.875 | 75 | 74
2019-11-14 21:30 | 51 | 50 |  |  | 43783.8958 | 70 | 70
2019-11-14 22:00 | 50 | 50 |  |  | 43783.9167 | 71 | 71
2019-11-14 22:30 | 49 | 48 |  |  | 43783.9375 | 70 | 69
2019-11-14 23:00 | 46 | 46 |  |  | 43783.9583 | 64 | 64
2019-11-14 23:30 | 43 | 42 |  |  | 43783.9792 | 61 | 61
2019-11-15 | 40 | 39 |  |  | 43784 | 58 | 58
2019-11-15 00:30 | 38 | 37 |  |  | 43784.0208 | 54 | 54
2019-11-15 01:00 | 38 | 37 |  |  | 43784.0417 | 54 | 54
2019-11-15 01:30 | 37 | 36 |  |  | 43784.0625 | 52 | 52
2019-11-15 02:00 | 38 | 37 |  |  | 43784.0833 | 54 | 53
2019-11-15 02:30 | 39 | 38 |  |  | 43784.1042 | 55 | 55
2019-11-15 03:00 | 39 | 39 |  |  | 43784.125 | 56 | 56
2019-11-15 03:30 | 40 | 40 |  |  | 43784.1458 | 57 | 57
2019-11-15 04:00 | 39 | 39 |  |  | 43784.1667 | 56 | 56
2019-11-15 04:30 | 36 | 36 |  |  | 43784.1875 | 53 | 53
2019-11-15 05:00 | 35 | 34 |  |  | 43784.2083 | 50 | 50
2019-11-15 05:30 | 35 | 34 |  |  | 43784.2292 | 52 | 51
2019-11-15 06:00 | 36 | 35 |  |  | 43784.25 | 55 | 54
2019-11-15 06:30 | 40 | 39 |  |  | 43784.2708 | 62 | 61
2019-11-15 07:00 | 43 | 41 |  |  | 43784.2917 | 68 | 67
2019-11-15 07:30 | 47 | 45 |  |  | 43784.3125 | 75 | 74
2019-11-15 08:00 | 48 | 47 |  |  | 43784.3333 | 77 | 76
2019-11-15 08:30 | 48 | 47 |  |  | 43784.3542 | 81 | 80
2019-11-15 09:00 | 47 | 46 |  |  | 43784.375 | 82 | 81
2019-11-15 09:30 | 46 | 46 |  |  | 43784.3958 | 79 | 79
2019-11-15 10:00 | 45 | 45 |  |  | 43784.4167 | 78 | 78
2019-11-15 10:30 | 47 | 47 |  |  | 43784.4375 | 79 | 79
2019-11-15 11:00 | 49 | 48 |  |  | 43784.4583 | 81 | 81
2019-11-15 11:30 | 51 | 51 |  |  | 43784.4792 | 83 | 83
2019-11-15 12:00 | 52 | 52 |  |  | 43784.5 | 84 | 84
2019-11-15 12:30 | 54 | 53 |  |  | 43784.5208 | 85 | 85
2019-11-15 13:00 | 56 | 55 |  |  | 43784.5417 | 87 | 87
2019-11-15 13:30 | 57 | 57 |  |  | 43784.5625 | 87 | 87
2019-11-15 14:00 | 59 | 59 |  |  | 43784.5833 | 87 | 87
2019-11-15 14:30 | 62 | 60 |  |  | 43784.6042 | 87 | 87
2019-11-15 15:00 | 63 | 62 |  |  | 43784.625 | 87 | 87
2019-11-15 15:30 | 64 | 63 |  |  | 43784.6458 | 88 | 88
2019-11-15 16:00 | 66 | 64 |  |  | 43784.6667 | 90 | 90
2019-11-15 16:30 | 67 | 66 |  |  | 43784.6875 | 90 | 90
2019-11-15 17:00 | 66 | 66 |  |  | 43784.7083 | 89 | 89
2019-11-15 17:30 | 60 | 59 |  |  | 43784.7292 | 85 | 85
2019-11-15 18:00 | 55 | 54 |  |  | 43784.75 | 80 | 80
2019-11-15 18:30 | 53 | 53 |  |  | 43784.7708 | 78 | 77
2019-11-15 19:00 | 55 | 54 |  |  | 43784.7917 | 80 | 80
2019-11-15 19:30 | 53 | 52 |  |  | 43784.8125 | 78 | 78
2019-11-15 20:00 | 55 | 52 |  |  | 43784.8333 | 77 | 76
2019-11-15 20:30 | 54 | 52 |  |  | 43784.8542 | 76 | 76
2019-11-15 21:00 | 52 | 49 |  |  | 43784.875 | 73 | 72
2019-11-15 21:30 | 49 | 47 |  |  | 43784.8958 | 68 | 68
2019-11-15 22:00 | 49 | 48 |  |  | 43784.9167 | 68 | 67
2019-11-15 22:30 | 47 | 46 |  |  | 43784.9375 | 67 | 67
2019-11-15 23:00 | 46 | 45 |  |  | 43784.9583 | 64 | 64
2019-11-15 23:30 | 43 | 41 |  |  | 43784.9792 | 60 | 60
2019-11-16 | 41 | 37 |  |  | 43785 | 56 | 56
2019-11-16 00:30 | 41 | 35 |  |  | 43785.0208 | 53 | 53
2019-11-16 01:00 | 43 | 36 |  |  | 43785.0417 | 54 | 53
2019-11-16 01:30 | 42 | 35 |  |  | 43785.0625 | 53 | 52
2019-11-16 02:00 | 40 | 33 |  |  | 43785.0833 | 51 | 50
2019-11-16 02:30 | 39 | 32 |  |  | 43785.1042 | 48 | 47
2019-11-16 03:00 | 39 | 32 |  |  | 43785.125 | 48 | 47
2019-11-16 03:30 | 41 | 34 |  |  | 43785.1458 | 50 | 49
2019-11-16 04:00 | 41 | 33 |  |  | 43785.1667 | 50 | 49
2019-11-16 04:30 | 39 | 32 |  |  | 43785.1875 | 49 | 48
2019-11-16 05:00 | 37 | 30 |  |  | 43785.2083 | 47 | 46
2019-11-16 05:30 | 35 | 29 |  |  | 43785.2292 | 45 | 45
2019-11-16 06:00 | 35 | 29 |  |  | 43785.25 | 45 | 44
2019-11-16 06:30 | 32 | 27 |  |  | 43785.2708 | 44 | 44
2019-11-16 07:00 | 30 | 25 |  |  | 43785.2917 | 43 | 43
2019-11-16 07:30 | 28 | 24 |  |  | 43785.3125 | 42 | 42
2019-11-16 08:00 | 27 | 24 |  |  | 43785.3333 | 43 | 43
2019-11-16 08:30 | 27 | 25 |  |  | 43785.3542 | 45 | 45
2019-11-16 09:00 | 29 | 28 |  |  | 43785.375 | 48 | 47
2019-11-16 09:30 | 36 | 35 |  |  | 43785.3958 | 53 | 53
2019-11-16 10:00 | 39 | 38 |  |  | 43785.4167 | 55 | 55
2019-11-16 10:30 | 44 | 42 |  |  | 43785.4375 | 58 | 58
2019-11-16 11:00 | 47 | 46 |  |  | 43785.4583 | 61 | 61
2019-11-16 11:30 | 52 | 51 |  |  | 43785.4792 | 66 | 66
2019-11-16 12:00 | 54 | 53 |  |  | 43785.5 | 69 | 69
2019-11-16 12:30 | 56 | 55 |  |  | 43785.5208 | 70 | 70
2019-11-16 13:00 | 62 | 60 |  |  | 43785.5417 | 75 | 74
2019-11-16 13:30 | 65 | 64 |  |  | 43785.5625 | 79 | 78
2019-11-16 14:00 | 71 | 70 |  |  | 43785.5833 | 78 | 78
2019-11-16 14:30 | 71 | 70 |  |  | 43785.6042 | 82 | 81
2019-11-16 15:00 | 71 | 70 |  |  | 43785.625 | 81 | 80
2019-11-16 15:30 | 71 | 69 |  |  | 43785.6458 | 79 | 77
2019-11-16 16:00 | 70 | 68 |  |  | 43785.6667 | 80 | 79
2019-11-16 16:30 | 70 | 68 |  |  | 43785.6875 | 80 | 78
2019-11-16 17:00 | 72 | 70 |  |  | 43785.7083 | 82 | 80
2019-11-16 17:30 | 73 | 71 |  |  | 43785.7292 | 83 | 82
2019-11-16 18:00 | 72 | 70 |  |  | 43785.75 | 84 | 83
2019-11-16 18:30 | 73 | 70 |  |  | 43785.7708 | 86 | 85
2019-11-16 19:00 | 75 | 73 |  |  | 43785.7917 | 90 | 89
2019-11-16 19:30 | 74 | 72 |  |  | 43785.8125 | 88 | 87
2019-11-16 20:00 | 73 | 71 |  |  | 43785.8333 | 87 | 86
2019-11-16 20:30 | 71 | 68 |  |  | 43785.8542 | 85 | 84
2019-11-16 21:00 | 67 | 65 |  |  | 43785.875 | 80 | 79
2019-11-16 21:30 | 62 | 58 |  |  | 43785.8958 | 76 | 75
2019-11-16 22:00 | 60 | 57 |  |  | 43785.9167 | 76 | 76
2019-11-16 22:30 | 59 | 56 |  |  | 43785.9375 | 74 | 73
2019-11-16 23:00 | 58 | 54 |  |  | 43785.9583 | 71 | 70
2019-11-16 23:30 | 54 | 51 |  |  | 43785.9792 | 68 | 67
2019-11-17 | 50 | 46 |  |  | 43786 | 63 | 62
2019-11-17 00:30 | 50 | 45 |  |  | 43786.0208 | 60 | 59
2019-11-17 01:00 | 48 | 44 |  |  | 43786.0417 | 58 | 57
2019-11-17 01:30 | 46 | 43 |  |  | 43786.0625 | 57 | 57
2019-11-17 02:00 | 45 | 41 |  |  | 43786.0833 | 56 | 56
2019-11-17 02:30 | 45 | 42 |  |  | 43786.1042 | 56 | 56
2019-11-17 03:00 | 46 | 42 |  |  | 43786.125 | 57 | 57
2019-11-17 03:30 | 46 | 42 |  |  | 43786.1458 | 55 | 55
2019-11-17 04:00 | 45 | 41 |  |  | 43786.1667 | 54 | 54
2019-11-17 04:30 | 46 | 42 |  |  | 43786.1875 | 55 | 55
2019-11-17 05:00 | 49 | 41 |  |  | 43786.2083 | 55 | 54
2019-11-17 05:30 | 52 | 39 |  |  | 43786.2292 | 55 | 53
2019-11-17 06:00 | 52 | 38 |  |  | 43786.25 | 53 | 51
2019-11-17 06:30 | 48 | 33 |  |  | 43786.2708 | 50 | 47
2019-11-17 07:00 | 44 | 29 |  |  | 43786.2917 | 46 | 44
2019-11-17 07:30 | 44 | 30 |  |  | 43786.3125 | 46 | 44
2019-11-17 08:00 | 44 | 31 |  |  | 43786.3333 | 47 | 45
2019-11-17 08:30 | 40 | 27 |  |  | 43786.3542 | 46 | 45
2019-11-17 09:00 | 41 | 30 |  |  | 43786.375 | 48 | 47
2019-11-17 09:30 | 42 | 32 |  |  | 43786.3958 | 49 | 49
2019-11-17 10:00 | 42 | 34 |  |  | 43786.4167 | 51 | 51
2019-11-17 10:30 | 45 | 37 |  |  | 43786.4375 | 53 | 52
2019-11-17 11:00 | 48 | 41 |  |  | 43786.4583 | 57 | 56
2019-11-17 11:30 | 50 | 43 |  |  | 43786.4792 | 56 | 55
2019-11-17 12:00 | 52 | 45 |  |  | 43786.5 | 59 | 59
2019-11-17 12:30 | 67 | 61 |  |  | 43786.5208 | 78 | 77
2019-11-17 13:00 | 65 | 58 |  |  | 43786.5417 | 75 | 74
2019-11-17 13:30 | 68 | 61 |  |  | 43786.5625 | 79 | 78
2019-11-17 14:00 | 55 | 47 |  |  | 43786.5833 | 55 | 52
2019-11-17 14:30 | 55 | 46 |  |  | 43786.6042 | 56 | 53
2019-11-17 15:00 | 57 | 50 |  |  | 43786.625 | 61 | 59
2019-11-17 15:30 | 59 | 52 |  |  | 43786.6458 | 62 | 60
2019-11-17 16:00 | 59 | 52 |  |  | 43786.6667 | 63 | 61
2019-11-17 16:30 | 61 | 55 |  |  | 43786.6875 | 65 | 64
2019-11-17 17:00 | 62 | 56 |  |  | 43786.7083 | 66 | 65
2019-11-17 17:30 | 64 | 58 |  |  | 43786.7292 | 68 | 67
2019-11-17 18:00 | 67 | 60 |  |  | 43786.75 | 72 | 70
2019-11-17 18:30 | 69 | 62 |  |  | 43786.7708 | 76 | 74
2019-11-17 19:00 | 73 | 65 |  |  | 43786.7917 | 81 | 80
2019-11-17 19:30 | 72 | 64 |  |  | 43786.8125 | 81 | 79
2019-11-17 20:00 | 71 | 63 |  |  | 43786.8333 | 79 | 78
2019-11-17 20:30 | 69 | 62 |  |  | 43786.8542 | 78 | 76
2019-11-17 21:00 | 65 | 58 |  |  | 43786.875 | 73 | 72
2019-11-17 21:30 | 64 | 57 |  |  | 43786.8958 | 72 | 71
2019-11-17 22:00 | 61 | 54 |  |  | 43786.9167 | 70 | 69
2019-11-17 22:30 | 59 | 52 |  |  | 43786.9375 | 68 | 67
2019-11-17 23:00 | 57 | 49 |  |  | 43786.9583 | 65 | 63
2019-11-17 23:30 | 55 | 47 |  |  | 43786.9792 | 63 | 61
2019-11-18 | 53 | 44 |  |  | 43787 | 61 | 59
2019-11-18 00:30 | 52 | 41 |  |  | 43787.0208 | 58 | 56
2019-11-18 01:00 | 52 | 40 |  |  | 43787.0417 | 54 | 52
2019-11-18 01:30 | 51 | 40 |  |  | 43787.0625 | 54 | 52
2019-11-18 02:00 | 50 | 40 |  |  | 43787.0833 | 53 | 52
2019-11-18 02:30 | 52 | 41 |  |  | 43787.1042 | 54 | 53
2019-11-18 03:00 | 51 | 40 |  |  | 43787.125 | 53 | 52
2019-11-18 03:30 | 51 | 40 |  |  | 43787.1458 | 53 | 52
2019-11-18 04:00 | 51 | 40 |  |  | 43787.1667 | 53 | 52
2019-11-18 04:30 | 51 | 40 |  |  | 43787.1875 | 53 | 52
2019-11-18 05:00 | 52 | 41 |  |  | 43787.2083 | 55 | 53
2019-11-18 05:30 | 52 | 42 |  |  | 43787.2292 | 55 | 54
2019-11-18 06:00 | 52 | 42 |  |  | 43787.25 | 56 | 55
2019-11-18 06:30 | 52 | 45 |  |  | 43787.2708 | 61 | 60
2019-11-18 07:00 | 55 | 49 |  |  | 43787.2917 | 67 | 67
2019-11-18 07:30 | 58 | 53 |  |  | 43787.3125 | 75 | 75
2019-11-18 08:00 | 60 | 53 |  |  | 43787.3333 | 77 | 76
2019-11-18 08:30 | 63 | 54 |  |  | 43787.3542 | 78 | 77
2019-11-18 09:00 | 60 | 50 |  |  | 43787.375 | 75 | 74
2019-11-18 09:30 | 60 | 51 |  |  | 43787.3958 | 76 | 75
2019-11-18 10:00 | 58 | 51 |  |  | 43787.4167 | 76 | 76
2019-11-18 10:30 | 57 | 50 |  |  | 43787.4375 | 76 | 76
2019-11-18 11:00 | 60 | 54 |  |  | 43787.4583 | 79 | 79
2019-11-18 11:30 | 60 | 54 |  |  | 43787.4792 | 78 | 78
2019-11-18 12:00 | 58 | 52 |  |  | 43787.5 | 77 | 77
2019-11-18 12:30 | 59 | 52 |  |  | 43787.5208 | 76 | 76
2019-11-18 13:00 | 58 | 52 |  |  | 43787.5417 | 75 | 75
2019-11-18 13:30 | 58 | 51 |  |  | 43787.5625 | 74 | 74
2019-11-18 14:00 | 59 | 53 |  |  | 43787.5833 | 75 | 75
2019-11-18 14:30 | 59 | 53 |  |  | 43787.6042 | 75 | 75
2019-11-18 15:00 | 60 | 54 |  |  | 43787.625 | 75 | 75
2019-11-18 15:30 | 61 | 55 |  |  | 43787.6458 | 71 | 71
2019-11-18 16:00 | 66 | 59 |  |  | 43787.6667 | 68 | 65
2019-11-18 16:30 | 70 | 62 |  |  | 43787.6875 | 72 | 69
2019-11-18 17:00 | 73 | 65 |  |  | 43787.7083 | 74 | 71
2019-11-18 17:30 | 75 | 66 |  |  | 43787.7292 | 74 | 70
2019-11-18 18:00 | 76 | 67 |  |  | 43787.75 | 76 | 72
2019-11-18 18:30 | 75 | 64 |  |  | 43787.7708 | 84 | 80
2019-11-18 19:00 | 78 | 68 |  |  | 43787.7917 | 88 | 84
2019-11-18 19:30 | 76 | 66 |  |  | 43787.8125 | 85 | 81
2019-11-18 20:00 | 73 | 64 |  |  | 43787.8333 | 81 | 78
2019-11-18 20:30 | 71 | 62 |  |  | 43787.8542 | 78 | 76
2019-11-18 21:00 | 68 | 57 |  |  | 43787.875 | 74 | 72
2019-11-18 21:30 | 65 | 53 |  |  | 43787.8958 | 69 | 66
2019-11-18 22:00 | 62 | 51 |  |  | 43787.9167 | 67 | 64
2019-11-18 22:30 | 59 | 48 |  |  | 43787.9375 | 65 | 62
2019-11-18 23:00 | 58 | 46 |  |  | 43787.9583 | 61 | 59
2019-11-18 23:30 | 50 | 40 |  |  | 43787.9792 | 54 | 52
2019-11-19 | 46 | 34 |  |  | 43788 | 48 | 46
2019-11-19 00:30 | 44 | 33 |  |  | 43788.0208 | 47 | 45
2019-11-19 01:00 | 45 | 34 |  |  | 43788.0417 | 46 | 45
2019-11-19 01:30 | 46 | 34 |  |  | 43788.0625 | 47 | 45
2019-11-19 02:00 | 48 | 35 |  |  | 43788.0833 | 48 | 46
2019-11-19 02:30 | 49 | 37 |  |  | 43788.1042 | 51 | 48
2019-11-19 03:00 | 49 | 37 |  |  | 43788.125 | 51 | 49
2019-11-19 03:30 | 51 | 39 |  |  | 43788.1458 | 52 | 50
2019-11-19 04:00 | 50 | 38 |  |  | 43788.1667 | 51 | 49
2019-11-19 04:30 | 48 | 36 |  |  | 43788.1875 | 48 | 46
2019-11-19 05:00 | 48 | 37 |  |  | 43788.2083 | 50 | 48
2019-11-19 05:30 | 50 | 40 |  |  | 43788.2292 | 53 | 51
2019-11-19 06:00 | 52 | 42 |  |  | 43788.25 | 56 | 55
2019-11-19 06:30 | 52 | 43 |  |  | 43788.2708 | 60 | 60
2019-11-19 07:00 | 49 | 42 |  |  | 43788.2917 | 61 | 61
2019-11-19 07:30 | 54 | 49 |  |  | 43788.3125 | 70 | 70
2019-11-19 08:00 | 55 | 51 |  |  | 43788.3333 | 60 | 60
2019-11-19 08:30 | 53 | 49 |  |  | 43788.3542 | 59 | 58
2019-11-19 09:00 | 51 | 46 |  |  | 43788.375 | 58 | 58
2019-11-19 09:30 | 52 | 47 |  |  | 43788.3958 | 59 | 58
2019-11-19 10:00 | 52 | 48 |  |  | 43788.4167 | 58 | 58
2019-11-19 10:30 | 53 | 49 |  |  | 43788.4375 | 58 | 58
2019-11-19 11:00 | 53 | 48 |  |  | 43788.4583 | 68 | 68
2019-11-19 11:30 | 55 | 49 |  |  | 43788.4792 | 71 | 71
2019-11-19 12:00 | 58 | 52 |  |  | 43788.5 | 74 | 73
2019-11-19 12:30 | 59 | 53 |  |  | 43788.5208 | 76 | 75
2019-11-19 13:00 | 65 | 56 |  |  | 43788.5417 | 81 | 77
2019-11-19 13:30 | 67 | 59 |  |  | 43788.5625 | 83 | 79
2019-11-19 14:00 | 71 | 63 |  |  | 43788.5833 | 86 | 82
2019-11-19 14:30 | 73 | 66 |  |  | 43788.6042 | 88 | 84
2019-11-19 15:00 | 71 | 64 |  |  | 43788.625 | 85 | 82
2019-11-19 15:30 | 73 | 65 |  |  | 43788.6458 | 85 | 81
2019-11-19 16:00 | 77 | 70 |  |  | 43788.6667 | 89 | 85
2019-11-19 16:30 | 81 | 74 |  |  | 43788.6875 | 93 | 88
2019-11-19 17:00 | 87 | 79 |  |  | 43788.7083 | 98 | 92
2019-11-19 17:30 | 89 | 79 |  |  | 43788.7292 | 98 | 92
2019-11-19 18:00 | 86 | 77 |  |  | 43788.75 | 94 | 90
2019-11-19 18:30 | 84 | 77 |  |  | 43788.7708 | 92 | 89
2019-11-19 19:00 | 88 | 80 |  |  | 43788.7917 | 96 | 93
2019-11-19 19:30 | 87 | 78 |  |  | 43788.8125 | 94 | 90
2019-11-19 20:00 | 82 | 76 |  |  | 43788.8333 | 89 | 88
2019-11-19 20:30 | 83 | 77 |  |  | 43788.8542 | 90 | 89
2019-11-19 21:00 | 80 | 74 |  |  | 43788.875 | 87 | 86
2019-11-19 21:30 | 76 | 69 |  |  | 43788.8958 | 82 | 80
2019-11-19 22:00 | 73 | 67 |  |  | 43788.9167 | 80 | 79
2019-11-19 22:30 | 68 | 62 |  |  | 43788.9375 | 76 | 75
2019-11-19 23:00 | 68 | 61 |  |  | 43788.9583 | 74 | 72
2019-11-19 23:30 | 63 | 57 |  |  | 43788.9792 | 70 | 69
2019-11-20 | 59 | 51 |  |  | 43789 | 65 | 64
2019-11-20 00:30 | 59 | 49 |  |  | 43789.0208 | 62 | 61
2019-11-20 01:00 | 57 | 47 |  |  | 43789.0417 | 59 | 58
2019-11-20 01:30 | 57 | 47 |  |  | 43789.0625 | 58 | 57
2019-11-20 02:00 | 57 | 46 |  |  | 43789.0833 | 57 | 56
2019-11-20 02:30 | 57 | 46 |  |  | 43789.1042 | 57 | 55
2019-11-20 03:00 | 56 | 45 |  |  | 43789.125 | 56 | 55
2019-11-20 03:30 | 55 | 45 |  |  | 43789.1458 | 57 | 55
2019-11-20 04:00 | 55 | 45 |  |  | 43789.1667 | 57 | 55
2019-11-20 04:30 | 55 | 45 |  |  | 43789.1875 | 57 | 55
2019-11-20 05:00 | 56 | 46 |  |  | 43789.2083 | 59 | 58
2019-11-20 05:30 | 57 | 47 |  |  | 43789.2292 | 60 | 59
2019-11-20 06:00 | 57 | 49 |  |  | 43789.25 | 62 | 61
2019-11-20 06:30 | 57 | 50 |  |  | 43789.2708 | 67 | 67
2019-11-20 07:00 | 57 | 50 |  |  | 43789.2917 | 70 | 70
2019-11-20 07:30 | 61 | 55 |  |  | 43789.3125 | 78 | 78
2019-11-20 08:00 | 63 | 55 |  |  | 43789.3333 | 81 | 80
2019-11-20 08:30 | 64 | 55 |  |  | 43789.3542 | 83 | 82
2019-11-20 09:00 | 63 | 53 |  |  | 43789.375 | 82 | 80
2019-11-20 09:30 | 65 | 56 |  |  | 43789.3958 | 84 | 82
2019-11-20 10:00 | 67 | 59 |  |  | 43789.4167 | 86 | 84
2019-11-20 10:30 | 68 | 60 |  |  | 43789.4375 | 86 | 85
2019-11-20 11:00 | 70 | 63 |  |  | 43789.4583 | 89 | 87
2019-11-20 11:30 | 71 | 65 |  |  | 43789.4792 | 91 | 89
2019-11-20 12:00 | 73 | 67 |  |  | 43789.5 | 91 | 90
2019-11-20 12:30 | 74 | 67 |  |  | 43789.5208 | 92 | 91
2019-11-20 13:00 | 75 | 69 |  |  | 43789.5417 | 93 | 91
2019-11-20 13:30 | 79 | 71 |  |  | 43789.5625 | 96 | 92
2019-11-20 14:00 | 87 | 74 |  |  | 43789.5833 | 105 | 94
2019-11-20 14:30 | 89 | 76 |  |  | 43789.6042 | 109 | 96
2019-11-20 15:00 | 88 | 74 |  |  | 43789.625 | 109 | 95
2019-11-20 15:30 | 88 | 75 |  |  | 43789.6458 | 112 | 96
2019-11-20 16:00 | 87 | 79 |  |  | 43789.6667 | 113 | 100
2019-11-20 16:30 | 81 | 75 |  |  | 43789.6875 | 109 | 98
2019-11-20 17:00 | 77 | 72 |  |  | 43789.7083 | 107 | 97
2019-11-20 17:30 | 77 | 73 |  |  | 43789.7292 | 104 | 98
2019-11-20 18:00 | 81 | 74 |  |  | 43789.75 | 107 | 98
2019-11-20 18:30 | 80 | 73 |  |  | 43789.7708 | 105 | 96
2019-11-20 19:00 | 82 | 76 |  |  | 43789.7917 | 108 | 100
2019-11-20 19:30 | 82 | 75 |  |  | 43789.8125 | 107 | 99
2019-11-20 20:00 | 82 | 75 |  |  | 43789.8333 | 106 | 97
2019-11-20 20:30 | 81 | 73 |  |  | 43789.8542 | 98 | 93
2019-11-20 21:00 | 78 | 69 |  |  | 43789.875 | 91 | 88
2019-11-20 21:30 | 71 | 65 |  |  | 43789.8958 | 82 | 81
2019-11-20 22:00 | 75 | 69 |  |  | 43789.9167 | 83 | 82
2019-11-20 22:30 | 74 | 67 |  |  | 43789.9375 | 84 | 83
2019-11-20 23:00 | 73 | 65 |  |  | 43789.9583 | 81 | 80
2019-11-20 23:30 | 69 | 61 |  |  | 43789.9792 | 76 | 75
2019-11-21 | 65 | 55 |  |  | 43790 | 70 | 69
2019-11-21 00:30 | 65 | 53 |  |  | 43790.0208 | 68 | 67
2019-11-21 01:00 | 64 | 51 |  |  | 43790.0417 | 64 | 63
2019-11-21 01:30 | 62 | 51 |  |  | 43790.0625 | 64 | 62
2019-11-21 02:00 | 63 | 51 |  |  | 43790.0833 | 64 | 63
2019-11-21 02:30 | 63 | 51 |  |  | 43790.1042 | 64 | 63
2019-11-21 03:00 | 62 | 50 |  |  | 43790.125 | 63 | 62
2019-11-21 03:30 | 62 | 50 |  |  | 43790.1458 | 62 | 61
2019-11-21 04:00 | 60 | 48 |  |  | 43790.1667 | 61 | 59
2019-11-21 04:30 | 58 | 45 |  |  | 43790.1875 | 59 | 58
2019-11-21 05:00 | 58 | 45 |  |  | 43790.2083 | 60 | 59
2019-11-21 05:30 | 60 | 49 |  |  | 43790.2292 | 65 | 64
2019-11-21 06:00 | 63 | 53 |  |  | 43790.25 | 69 | 68
2019-11-21 06:30 | 63 | 55 |  |  | 43790.2708 | 73 | 73
2019-11-21 07:00 | 65 | 57 |  |  | 43790.2917 | 77 | 77
2019-11-21 07:30 | 68 | 60 |  |  | 43790.3125 | 82 | 81
2019-11-21 08:00 | 67 | 60 |  |  | 43790.3333 | 82 | 82
2019-11-21 08:30 | 66 | 60 |  |  | 43790.3542 | 83 | 83
2019-11-21 09:00 | 64 | 58 |  |  | 43790.375 | 82 | 82
2019-11-21 09:30 | 67 | 58 |  |  | 43790.3958 | 83 | 81
2019-11-21 10:00 | 66 | 57 |  |  | 43790.4167 | 82 | 80
2019-11-21 10:30 | 64 | 55 |  |  | 43790.4375 | 81 | 79
2019-11-21 11:00 | 64 | 55 |  |  | 43790.4583 | 79 | 78
2019-11-21 11:30 | 62 | 53 |  |  | 43790.4792 | 77 | 75
2019-11-21 12:00 | 59 | 50 |  |  | 43790.5 | 73 | 72
2019-11-21 12:30 | 58 | 49 |  |  | 43790.5208 | 72 | 71
2019-11-21 13:00 | 60 | 51 |  |  | 43790.5417 | 74 | 72
2019-11-21 13:30 | 63 | 54 |  |  | 43790.5625 | 76 | 75
2019-11-21 14:00 | 65 | 56 |  |  | 43790.5833 | 78 | 77
2019-11-21 14:30 | 67 | 60 |  |  | 43790.6042 | 81 | 80
2019-11-21 15:00 | 67 | 59 |  |  | 43790.625 | 81 | 79
2019-11-21 15:30 | 68 | 62 |  |  | 43790.6458 | 82 | 81
2019-11-21 16:00 | 71 | 66 |  |  | 43790.6667 | 85 | 83
2019-11-21 16:30 | 75 | 70 |  |  | 43790.6875 | 89 | 86
2019-11-21 17:00 | 78 | 73 |  |  | 43790.7083 | 91 | 88
2019-11-21 17:30 | 80 | 74 |  |  | 43790.7292 | 92 | 88
2019-11-21 18:00 | 80 | 74 |  |  | 43790.75 | 91 | 88
2019-11-21 18:30 | 80 | 74 |  |  | 43790.7708 | 90 | 88
2019-11-21 19:00 | 83 | 78 |  |  | 43790.7917 | 94 | 91
2019-11-21 19:30 | 82 | 77 |  |  | 43790.8125 | 92 | 90
2019-11-21 20:00 | 79 | 76 |  |  | 43790.8333 | 89 | 89
2019-11-21 20:30 | 77 | 75 |  |  | 43790.8542 | 88 | 88
2019-11-21 21:00 | 76 | 73 |  |  | 43790.875 | 86 | 86
2019-11-21 21:30 | 73 | 70 |  |  | 43790.8958 | 82 | 81
2019-11-21 22:00 | 70 | 67 |  |  | 43790.9167 | 79 | 78
2019-11-21 22:30 | 66 | 62 |  |  | 43790.9375 | 75 | 74
2019-11-21 23:00 | 66 | 61 |  |  | 43790.9583 | 72 | 72
2019-11-21 23:30 | 63 | 57 |  |  | 43790.9792 | 69 | 68
2019-11-22 | 58 | 51 |  |  | 43791 | 64 | 63
2019-11-22 00:30 | 57 | 49 |  |  | 43791.0208 | 62 | 61
2019-11-22 01:00 | 56 | 47 |  |  | 43791.0417 | 60 | 58
2019-11-22 01:30 | 56 | 47 |  |  | 43791.0625 | 59 | 57
2019-11-22 02:00 | 55 | 45 |  |  | 43791.0833 | 57 | 55
2019-11-22 02:30 | 54 | 44 |  |  | 43791.1042 | 56 | 54
2019-11-22 03:00 | 54 | 43 |  |  | 43791.125 | 56 | 54
2019-11-22 03:30 | 54 | 43 |  |  | 43791.1458 | 55 | 53
2019-11-22 04:00 | 53 | 42 |  |  | 43791.1667 | 54 | 53
2019-11-22 04:30 | 53 | 43 |  |  | 43791.1875 | 55 | 53
2019-11-22 05:00 | 55 | 44 |  |  | 43791.2083 | 57 | 56
2019-11-22 05:30 | 56 | 46 |  |  | 43791.2292 | 59 | 57
2019-11-22 06:00 | 55 | 46 |  |  | 43791.25 | 61 | 59
2019-11-22 06:30 | 55 | 48 |  |  | 43791.2708 | 64 | 63
2019-11-22 07:00 | 54 | 49 |  |  | 43791.2917 | 67 | 67
2019-11-22 07:30 | 55 | 52 |  |  | 43791.3125 | 71 | 71
2019-11-22 08:00 | 54 | 51 |  |  | 43791.3333 | 71 | 71
2019-11-22 08:30 | 52 | 49 |  |  | 43791.3542 | 71 | 71
2019-11-22 09:00 | 50 | 47 |  |  | 43791.375 | 68 | 68
2019-11-22 09:30 | 52 | 49 |  |  | 43791.3958 | 71 | 71
2019-11-22 10:00 | 53 | 51 |  |  | 43791.4167 | 72 | 72
2019-11-22 10:30 | 52 | 50 |  |  | 43791.4375 | 71 | 71
2019-11-22 11:00 | 49 | 47 |  |  | 43791.4583 | 69 | 69
2019-11-22 11:30 | 50 | 48 |  |  | 43791.4792 | 70 | 70
2019-11-22 12:00 | 52 | 49 |  |  | 43791.5 | 71 | 71
2019-11-22 12:30 | 51 | 49 |  |  | 43791.5208 | 69 | 68
2019-11-22 13:00 | 51 | 49 |  |  | 43791.5417 | 68 | 68
2019-11-22 13:30 | 52 | 50 |  |  | 43791.5625 | 68 | 68
2019-11-22 14:00 | 52 | 49 |  |  | 43791.5833 | 66 | 66
2019-11-22 14:30 | 55 | 52 |  |  | 43791.6042 | 69 | 69
2019-11-22 15:00 | 59 | 55 |  |  | 43791.625 | 73 | 71
2019-11-22 15:30 | 63 | 58 |  |  | 43791.6458 | 76 | 74
2019-11-22 16:00 | 67 | 62 |  |  | 43791.6667 | 81 | 79
2019-11-22 16:30 | 72 | 67 |  |  | 43791.6875 | 86 | 83
2019-11-22 17:00 | 74 | 69 |  |  | 43791.7083 | 89 | 87
2019-11-22 17:30 | 76 | 70 |  |  | 43791.7292 | 90 | 87
2019-11-22 18:00 | 76 | 71 |  |  | 43791.75 | 88 | 86
2019-11-22 18:30 | 78 | 71 |  |  | 43791.7708 | 87 | 85
2019-11-22 19:00 | 83 | 73 |  |  | 43791.7917 | 90 | 87
2019-11-22 19:30 | 82 | 71 |  |  | 43791.8125 | 89 | 85
2019-11-22 20:00 | 77 | 69 |  |  | 43791.8333 | 84 | 82
2019-11-22 20:30 | 75 | 67 |  |  | 43791.8542 | 82 | 81
2019-11-22 21:00 | 74 | 64 |  |  | 43791.875 | 79 | 77
2019-11-22 21:30 | 71 | 61 |  |  | 43791.8958 | 75 | 74
2019-11-22 22:00 | 70 | 60 |  |  | 43791.9167 | 76 | 74
2019-11-22 22:30 | 68 | 57 |  |  | 43791.9375 | 73 | 71
2019-11-22 23:00 | 68 | 57 |  |  | 43791.9583 | 71 | 69
2019-11-22 23:30 | 65 | 53 |  |  | 43791.9792 | 67 | 65
2019-11-23 | 62 | 48 |  |  | 43792 | 64 | 62
2019-11-23 00:30 | 62 | 48 |  |  | 43792.0208 | 64 | 60
2019-11-23 01:00 | 65 | 49 |  |  | 43792.0417 | 65 | 61
2019-11-23 01:30 | 64 | 48 |  |  | 43792.0625 | 64 | 59
2019-11-23 02:00 | 63 | 47 |  |  | 43792.0833 | 62 | 57
2019-11-23 02:30 | 61 | 45 |  |  | 43792.1042 | 61 | 55
2019-11-23 03:00 | 60 | 43 |  |  | 43792.125 | 60 | 54
2019-11-23 03:30 | 60 | 44 |  |  | 43792.1458 | 60 | 55
2019-11-23 04:00 | 60 | 43 |  |  | 43792.1667 | 59 | 53
2019-11-23 04:30 | 59 | 41 |  |  | 43792.1875 | 58 | 52
2019-11-23 05:00 | 58 | 40 |  |  | 43792.2083 | 58 | 52
2019-11-23 05:30 | 59 | 40 |  |  | 43792.2292 | 57 | 51
2019-11-23 06:00 | 58 | 38 |  |  | 43792.25 | 56 | 50
2019-11-23 06:30 | 53 | 34 |  |  | 43792.2708 | 52 | 47
2019-11-23 07:00 | 48 | 30 |  |  | 43792.2917 | 48 | 44
2019-11-23 07:30 | 41 | 29 |  |  | 43792.3125 | 46 | 43
2019-11-23 08:00 | 37 | 33 |  |  | 43792.3333 | 49 | 48
2019-11-23 08:30 | 34 | 29 |  |  | 43792.3542 | 47 | 46
2019-11-23 09:00 | 34 | 30 |  |  | 43792.375 | 47 | 46
2019-11-23 09:30 | 33 | 29 |  |  | 43792.3958 | 48 | 47
2019-11-23 10:00 | 32 | 29 |  |  | 43792.4167 | 45 | 45
2019-11-23 10:30 | 31 | 28 |  |  | 43792.4375 | 43 | 43
2019-11-23 11:00 | 32 | 29 |  |  | 43792.4583 | 43 | 43
2019-11-23 11:30 | 33 | 30 |  |  | 43792.4792 | 44 | 43
2019-11-23 12:00 | 33 | 30 |  |  | 43792.5 | 42 | 42
2019-11-23 12:30 | 33 | 31 |  |  | 43792.5208 | 43 | 43
2019-11-23 13:00 | 35 | 32 |  |  | 43792.5417 | 44 | 43
2019-11-23 13:30 | 37 | 35 |  |  | 43792.5625 | 45 | 45
2019-11-23 14:00 | 38 | 36 |  |  | 43792.5833 | 46 | 46
2019-11-23 14:30 | 41 | 38 |  |  | 43792.6042 | 48 | 48
2019-11-23 15:00 | 42 | 40 |  |  | 43792.625 | 50 | 49
2019-11-23 15:30 | 44 | 42 |  |  | 43792.6458 | 53 | 52
2019-11-23 16:00 | 49 | 44 |  |  | 43792.6667 | 57 | 55
2019-11-23 16:30 | 53 | 49 |  |  | 43792.6875 | 63 | 61
2019-11-23 17:00 | 57 | 53 |  |  | 43792.7083 | 68 | 66
2019-11-23 17:30 | 58 | 54 |  |  | 43792.7292 | 69 | 67
2019-11-23 18:00 | 62 | 58 |  |  | 43792.75 | 74 | 71
2019-11-23 18:30 | 64 | 59 |  |  | 43792.7708 | 77 | 73
2019-11-23 19:00 | 67 | 63 |  |  | 43792.7917 | 82 | 79
2019-11-23 19:30 | 69 | 65 |  |  | 43792.8125 | 83 | 80
2019-11-23 20:00 | 71 | 66 |  |  | 43792.8333 | 85 | 81
2019-11-23 20:30 | 67 | 64 |  |  | 43792.8542 | 81 | 79
2019-11-23 21:00 | 65 | 61 |  |  | 43792.875 | 77 | 76
2019-11-23 21:30 | 63 | 60 |  |  | 43792.8958 | 76 | 75
2019-11-23 22:00 | 61 | 57 |  |  | 43792.9167 | 75 | 72
2019-11-23 22:30 | 61 | 57 |  |  | 43792.9375 | 75 | 72
2019-11-23 23:00 | 61 | 56 |  |  | 43792.9583 | 72 | 69
2019-11-23 23:30 | 58 | 53 |  |  | 43792.9792 | 70 | 66
2019-11-24 | 53 | 47 |  |  | 43793 | 65 | 61
2019-11-24 00:30 | 53 | 46 |  |  | 43793.0208 | 63 | 59
2019-11-24 01:00 | 52 | 45 |  |  | 43793.0417 | 61 | 56
2019-11-24 01:30 | 50 | 43 |  |  | 43793.0625 | 60 | 54
2019-11-24 02:00 | 51 | 43 |  |  | 43793.0833 | 60 | 54
2019-11-24 02:30 | 52 | 45 |  |  | 43793.1042 | 61 | 55
2019-11-24 03:00 | 52 | 44 |  |  | 43793.125 | 61 | 55
2019-11-24 03:30 | 51 | 43 |  |  | 43793.1458 | 60 | 55
2019-11-24 04:00 | 51 | 42 |  |  | 43793.1667 | 60 | 54
2019-11-24 04:30 | 49 | 41 |  |  | 43793.1875 | 59 | 53
2019-11-24 05:00 | 49 | 40 |  |  | 43793.2083 | 58 | 52
2019-11-24 05:30 | 50 | 41 |  |  | 43793.2292 | 58 | 53
2019-11-24 06:00 | 48 | 39 |  |  | 43793.25 | 57 | 52
2019-11-24 06:30 | 44 | 33 |  |  | 43793.2708 | 53 | 48
2019-11-24 07:00 | 39 | 28 |  |  | 43793.2917 | 49 | 44
2019-11-24 07:30 | 37 | 27 |  |  | 43793.3125 | 48 | 44
2019-11-24 08:00 | 36 | 27 |  |  | 43793.3333 | 48 | 44
2019-11-24 08:30 | 37 | 29 |  |  | 43793.3542 | 49 | 46
2019-11-24 09:00 | 37 | 30 |  |  | 43793.375 | 49 | 47
2019-11-24 09:30 | 37 | 32 |  |  | 43793.3958 | 48 | 47
2019-11-24 10:00 | 38 | 33 |  |  | 43793.4167 | 48 | 47
2019-11-24 10:30 | 40 | 36 |  |  | 43793.4375 | 49 | 48
2019-11-24 11:00 | 41 | 37 |  |  | 43793.4583 | 49 | 48
2019-11-24 11:30 | 40 | 36 |  |  | 43793.4792 | 48 | 47
2019-11-24 12:00 | 39 | 35 |  |  | 43793.5 | 49 | 48
2019-11-24 12:30 | 39 | 35 |  |  | 43793.5208 | 48 | 47
2019-11-24 13:00 | 40 | 36 |  |  | 43793.5417 | 49 | 48
2019-11-24 13:30 | 42 | 39 |  |  | 43793.5625 | 48 | 47
2019-11-24 14:00 | 44 | 41 |  |  | 43793.5833 | 52 | 50
2019-11-24 14:30 | 54 | 51 |  |  | 43793.6042 | 56 | 55
2019-11-24 15:00 | 54 | 50 |  |  | 43793.625 | 63 | 61
2019-11-24 15:30 | 58 | 55 |  |  | 43793.6458 | 72 | 70
2019-11-24 16:00 | 57 | 53 |  |  | 43793.6667 | 70 | 67
2019-11-24 16:30 | 53 | 49 |  |  | 43793.6875 | 62 | 59
2019-11-24 17:00 | 59 | 56 |  |  | 43793.7083 | 67 | 64
2019-11-24 17:30 | 64 | 60 |  |  | 43793.7292 | 73 | 70
2019-11-24 18:00 | 69 | 63 |  |  | 43793.75 | 80 | 75
2019-11-24 18:30 | 72 | 66 |  |  | 43793.7708 | 85 | 79
2019-11-24 19:00 | 75 | 68 |  |  | 43793.7917 | 90 | 83
2019-11-24 19:30 | 75 | 68 |  |  | 43793.8125 | 89 | 82
2019-11-24 20:00 | 73 | 66 |  |  | 43793.8333 | 87 | 81
2019-11-24 20:30 | 70 | 65 |  |  | 43793.8542 | 83 | 80
2019-11-24 21:00 | 67 | 62 |  |  | 43793.875 | 80 | 77
2019-11-24 21:30 | 63 | 58 |  |  | 43793.8958 | 75 | 73
2019-11-24 22:00 | 62 | 57 |  |  | 43793.9167 | 75 | 72
2019-11-24 22:30 | 62 | 57 |  |  | 43793.9375 | 76 | 74
2019-11-24 23:00 | 60 | 55 |  |  | 43793.9583 | 72 | 70
2019-11-24 23:30 | 56 | 50 |  |  | 43793.9792 | 68 | 65
2019-11-25 | 53 | 46 |  |  | 43794 | 63 | 60
2019-11-25 00:30 | 52 | 45 |  |  | 43794.0208 | 62 | 58
2019-11-25 01:00 | 52 | 45 |  |  | 43794.0417 | 61 | 56
2019-11-25 01:30 | 51 | 44 |  |  | 43794.0625 | 60 | 56
2019-11-25 02:00 | 51 | 44 |  |  | 43794.0833 | 60 | 55
2019-11-25 02:30 | 50 | 42 |  |  | 43794.1042 | 58 | 54
2019-11-25 03:00 | 50 | 44 |  |  | 43794.125 | 58 | 55
2019-11-25 03:30 | 52 | 45 |  |  | 43794.1458 | 60 | 57
2019-11-25 04:00 | 51 | 44 |  |  | 43794.1667 | 59 | 56
2019-11-25 04:30 | 51 | 44 |  |  | 43794.1875 | 60 | 57
2019-11-25 05:00 | 51 | 44 |  |  | 43794.2083 | 60 | 56
2019-11-25 05:30 | 53 | 46 |  |  | 43794.2292 | 62 | 60
2019-11-25 06:00 | 54 | 49 |  |  | 43794.25 | 66 | 64
2019-11-25 06:30 | 55 | 51 |  |  | 43794.2708 | 70 | 69
2019-11-25 07:00 | 54 | 52 |  |  | 43794.2917 | 69 | 68
2019-11-25 07:30 | 57 | 54 |  |  | 43794.3125 | 79 | 78
2019-11-25 08:00 | 57 | 56 |  |  | 43794.3333 | 82 | 82
2019-11-25 08:30 | 60 | 58 |  |  | 43794.3542 | 82 | 82
2019-11-25 09:00 | 61 | 59 |  |  | 43794.375 | 84 | 84
2019-11-25 09:30 | 63 | 61 |  |  | 43794.3958 | 85 | 85
2019-11-25 10:00 | 66 | 64 |  |  | 43794.4167 | 88 | 88
2019-11-25 10:30 | 63 | 61 |  |  | 43794.4375 | 86 | 86
2019-11-25 11:00 | 58 | 56 |  |  | 43794.4583 | 82 | 82
2019-11-25 11:30 | 54 | 52 |  |  | 43794.4792 | 77 | 77
2019-11-25 12:00 | 55 | 51 |  |  | 43794.5 | 77 | 76
2019-11-25 12:30 | 54 | 51 |  |  | 43794.5208 | 76 | 75
2019-11-25 13:00 | 55 | 52 |  |  | 43794.5417 | 76 | 75
2019-11-25 13:30 | 55 | 53 |  |  | 43794.5625 | 76 | 75
2019-11-25 14:00 | 55 | 54 |  |  | 43794.5833 | 76 | 74
2019-11-25 14:30 | 55 | 55 |  |  | 43794.6042 | 77 | 75
2019-11-25 15:00 | 57 | 56 |  |  | 43794.625 | 77 | 76
2019-11-25 15:30 | 60 | 60 |  |  | 43794.6458 | 81 | 79
2019-11-25 16:00 | 64 | 63 |  |  | 43794.6667 | 83 | 82
2019-11-25 16:30 | 67 | 67 |  |  | 43794.6875 | 85 | 84
2019-11-25 17:00 | 73 | 72 |  |  | 43794.7083 | 92 | 90
2019-11-25 17:30 | 74 | 73 |  |  | 43794.7292 | 92 | 90
2019-11-25 18:00 | 77 | 75 |  |  | 43794.75 | 93 | 91
2019-11-25 18:30 | 76 | 76 |  |  | 43794.7708 | 91 | 91
2019-11-25 19:00 | 80 | 80 |  |  | 43794.7917 | 95 | 95
2019-11-25 19:30 | 78 | 78 |  |  | 43794.8125 | 92 | 92
2019-11-25 20:00 | 77 | 75 |  |  | 43794.8333 | 90 | 90
2019-11-25 20:30 | 75 | 74 |  |  | 43794.8542 | 88 | 88
2019-11-25 21:00 | 70 | 69 |  |  | 43794.875 | 83 | 83
2019-11-25 21:30 | 68 | 66 |  |  | 43794.8958 | 79 | 79
2019-11-25 22:00 | 68 | 65 |  |  | 43794.9167 | 81 | 81
2019-11-25 22:30 | 65 | 63 |  |  | 43794.9375 | 78 | 78
2019-11-25 23:00 | 65 | 62 |  |  | 43794.9583 | 76 | 76
2019-11-25 23:30 | 61 | 58 |  |  | 43794.9792 | 72 | 71
2019-11-26 | 56 | 53 |  |  | 43795 | 67 | 66
2019-11-26 00:30 | 57 | 53 |  |  | 43795.0208 | 67 | 67
2019-11-26 01:00 | 56 | 52 |  |  | 43795.0417 | 65 | 65
2019-11-26 01:30 | 56 | 53 |  |  | 43795.0625 | 65 | 65
2019-11-26 02:00 | 57 | 53 |  |  | 43795.0833 | 65 | 65
2019-11-26 02:30 | 56 | 52 |  |  | 43795.1042 | 64 | 64
2019-11-26 03:00 | 56 | 52 |  |  | 43795.125 | 65 | 64
2019-11-26 03:30 | 57 | 53 |  |  | 43795.1458 | 66 | 66
2019-11-26 04:00 | 58 | 54 |  |  | 43795.1667 | 67 | 67
2019-11-26 04:30 | 58 | 54 |  |  | 43795.1875 | 67 | 67
2019-11-26 05:00 | 59 | 55 |  |  | 43795.2083 | 69 | 68
2019-11-26 05:30 | 59 | 56 |  |  | 43795.2292 | 70 | 70
2019-11-26 06:00 | 55 | 53 |  |  | 43795.25 | 67 | 67
2019-11-26 06:30 | 53 | 50 |  |  | 43795.2708 | 68 | 68
2019-11-26 07:00 | 53 | 51 |  |  | 43795.2917 | 71 | 71
2019-11-26 07:30 | 55 | 54 |  |  | 43795.3125 | 77 | 77
2019-11-26 08:00 | 59 | 57 |  |  | 43795.3333 | 80 | 80
2019-11-26 08:30 | 61 | 59 |  |  | 43795.3542 | 83 | 83
2019-11-26 09:00 | 68 | 66 |  |  | 43795.375 | 92 | 90
2019-11-26 09:30 | 70 | 68 |  |  | 43795.3958 | 95 | 93
2019-11-26 10:00 | 65 | 64 |  |  | 43795.4167 | 92 | 90
2019-11-26 10:30 | 61 | 59 |  |  | 43795.4375 | 88 | 86
2019-11-26 11:00 | 62 | 60 |  |  | 43795.4583 | 87 | 85
2019-11-26 11:30 | 60 | 59 |  |  | 43795.4792 | 82 | 81
2019-11-26 12:00 | 58 | 58 |  |  | 43795.5 | 81 | 79
2019-11-26 12:30 | 58 | 57 |  |  | 43795.5208 | 78 | 78
2019-11-26 13:00 | 62 | 61 |  |  | 43795.5417 | 84 | 84
2019-11-26 13:30 | 65 | 63 |  |  | 43795.5625 | 87 | 87
2019-11-26 14:00 | 73 | 66 |  |  | 43795.5833 | 92 | 90
2019-11-26 14:30 | 79 | 67 |  |  | 43795.6042 | 94 | 92
2019-11-26 15:00 | 77 | 66 |  |  | 43795.625 | 90 | 88
2019-11-26 15:30 | 79 | 69 |  |  | 43795.6458 | 91 | 90
2019-11-26 16:00 | 82 | 72 |  |  | 43795.6667 | 95 | 94
2019-11-26 16:30 | 96 | 77 |  |  | 43795.6875 | 101 | 101
2019-11-26 17:00 | 94 | 73 |  |  | 43795.7083 | 102 | 102
2019-11-26 17:30 | 89 | 72 |  |  | 43795.7292 | 101 | 101
2019-11-26 18:00 | 87 | 73 |  |  | 43795.75 | 101 | 101
2019-11-26 18:30 | 84 | 73 |  |  | 43795.7708 | 100 | 99
2019-11-26 19:00 | 85 | 76 |  |  | 43795.7917 | 104 | 104
2019-11-26 19:30 | 86 | 75 |  |  | 43795.8125 | 102 | 102
2019-11-26 20:00 | 84 | 74 |  |  | 43795.8333 | 100 | 99
2019-11-26 20:30 | 77 | 71 |  |  | 43795.8542 | 97 | 97
2019-11-26 21:00 | 71 | 68 |  |  | 43795.875 | 92 | 92
2019-11-26 21:30 | 67 | 65 |  |  | 43795.8958 | 87 | 86
2019-11-26 22:00 | 64 | 62 |  |  | 43795.9167 | 85 | 85
2019-11-26 22:30 | 61 | 59 |  |  | 43795.9375 | 81 | 81
2019-11-26 23:00 | 58 | 55 |  |  | 43795.9583 | 76 | 75
2019-11-26 23:30 | 61 | 56 |  |  | 43795.9792 | 74 | 73
2019-11-27 | 61 | 52 |  |  | 43796 | 70 | 69
2019-11-27 00:30 | 64 | 54 |  |  | 43796.0208 | 72 | 71
2019-11-27 01:00 | 64 | 54 |  |  | 43796.0417 | 70 | 69
2019-11-27 01:30 | 63 | 53 |  |  | 43796.0625 | 68 | 67
2019-11-27 02:00 | 61 | 51 |  |  | 43796.0833 | 66 | 65
2019-11-27 02:30 | 60 | 49 |  |  | 43796.1042 | 65 | 64
2019-11-27 03:00 | 60 | 49 |  |  | 43796.125 | 64 | 62
2019-11-27 03:30 | 58 | 47 |  |  | 43796.1458 | 63 | 61
2019-11-27 04:00 | 59 | 47 |  |  | 43796.1667 | 62 | 60
2019-11-27 04:30 | 58 | 47 |  |  | 43796.1875 | 62 | 61
2019-11-27 05:00 | 60 | 48 |  |  | 43796.2083 | 65 | 63
2019-11-27 05:30 | 59 | 48 |  |  | 43796.2292 | 65 | 64
2019-11-27 06:00 | 56 | 46 |  |  | 43796.25 | 65 | 64
2019-11-27 06:30 | 61 | 53 |  |  | 43796.2708 | 74 | 74
2019-11-27 07:00 | 62 | 54 |  |  | 43796.2917 | 80 | 80
2019-11-27 07:30 | 62 | 60 |  |  | 43796.3125 | 89 | 89
2019-11-27 08:00 | 65 | 64 |  |  | 43796.3333 | 95 | 94
2019-11-27 08:30 | 68 | 67 |  |  | 43796.3542 | 99 | 98
2019-11-27 09:00 | 73 | 72 |  |  | 43796.375 | 104 | 103
2019-11-27 09:30 | 75 | 70 |  |  | 43796.3958 | 104 | 101
2019-11-27 10:00 | 78 | 74 |  |  | 43796.4167 | 106 | 103
2019-11-27 10:30 | 82 | 79 |  |  | 43796.4375 | 108 | 105
2019-11-27 11:00 | 83 | 79 |  |  | 43796.4583 | 106 | 103
2019-11-27 11:30 | 81 | 77 |  |  | 43796.4792 | 108 | 106
2019-11-27 12:00 | 77 | 74 |  |  | 43796.5 | 106 | 103
2019-11-27 12:30 | 77 | 72 |  |  | 43796.5208 | 105 | 100
2019-11-27 13:00 | 77 | 72 |  |  | 43796.5417 | 104 | 100
2019-11-27 13:30 | 76 | 73 |  |  | 43796.5625 | 106 | 103
2019-11-27 14:00 | 83 | 79 |  |  | 43796.5833 | 114 | 107
2019-11-27 14:30 | 85 | 80 |  |  | 43796.6042 | 118 | 108
2019-11-27 15:00 | 86 | 80 |  |  | 43796.625 | 117 | 108
2019-11-27 15:30 | 87 | 85 |  |  | 43796.6458 | 113 | 110
2019-11-27 16:00 | 83 | 82 |  |  | 43796.6667 | 111 | 108
2019-11-27 16:30 | 79 | 77 |  |  | 43796.6875 | 107 | 104
2019-11-27 17:00 | 80 | 78 |  |  | 43796.7083 | 106 | 103
2019-11-27 17:30 | 77 | 76 |  |  | 43796.7292 | 101 | 99
2019-11-27 18:00 | 73 | 73 |  |  | 43796.75 | 90 | 90
2019-11-27 18:30 | 72 | 72 |  |  | 43796.7708 | 88 | 88
2019-11-27 19:00 | 75 | 75 |  |  | 43796.7917 | 92 | 92
2019-11-27 19:30 | 72 | 72 |  |  | 43796.8125 | 88 | 88
2019-11-27 20:00 | 71 | 71 |  |  | 43796.8333 | 87 | 87
2019-11-27 20:30 | 70 | 70 |  |  | 43796.8542 | 86 | 86
2019-11-27 21:00 | 69 | 69 |  |  | 43796.875 | 84 | 84
2019-11-27 21:30 | 67 | 67 |  |  | 43796.8958 | 81 | 81
2019-11-27 22:00 | 65 | 65 |  |  | 43796.9167 | 81 | 80
2019-11-27 22:30 | 65 | 65 |  |  | 43796.9375 | 80 | 80
2019-11-27 23:00 | 61 | 60 |  |  | 43796.9583 | 74 | 74
2019-11-27 23:30 | 56 | 56 |  |  | 43796.9792 | 69 | 69
2019-11-28 | 52 | 52 |  |  | 43797 | 66 | 66
2019-11-28 00:30 | 51 | 49 |  |  | 43797.0208 | 62 | 62
2019-11-28 01:00 | 49 | 46 |  |  | 43797.0417 | 59 | 59
2019-11-28 01:30 | 49 | 46 |  |  | 43797.0625 | 57 | 57
2019-11-28 02:00 | 50 | 47 |  |  | 43797.0833 | 59 | 59
2019-11-28 02:30 | 49 | 47 |  |  | 43797.1042 | 58 | 58
2019-11-28 03:00 | 50 | 47 |  |  | 43797.125 | 57 | 57
2019-11-28 03:30 | 48 | 45 |  |  | 43797.1458 | 57 | 57
2019-11-28 04:00 | 47 | 44 |  |  | 43797.1667 | 56 | 56
2019-11-28 04:30 | 46 | 43 |  |  | 43797.1875 | 54 | 54
2019-11-28 05:00 | 48 | 45 |  |  | 43797.2083 | 57 | 57
2019-11-28 05:30 | 50 | 48 |  |  | 43797.2292 | 60 | 60
2019-11-28 06:00 | 51 | 49 |  |  | 43797.25 | 62 | 62
2019-11-28 06:30 | 54 | 52 |  |  | 43797.2708 | 69 | 69
2019-11-28 07:00 | 58 | 56 |  |  | 43797.2917 | 76 | 76
2019-11-28 07:30 | 63 | 61 |  |  | 43797.3125 | 82 | 82
2019-11-28 08:00 | 64 | 62 |  |  | 43797.3333 | 83 | 83
2019-11-28 08:30 | 64 | 62 |  |  | 43797.3542 | 84 | 84
2019-11-28 09:00 | 64 | 62 |  |  | 43797.375 | 85 | 85
2019-11-28 09:30 | 65 | 64 |  |  | 43797.3958 | 89 | 89
2019-11-28 10:00 | 67 | 64 |  |  | 43797.4167 | 92 | 91
2019-11-28 10:30 | 68 | 65 |  |  | 43797.4375 | 92 | 91
2019-11-28 11:00 | 71 | 68 |  |  | 43797.4583 | 94 | 93
2019-11-28 11:30 | 69 | 66 |  |  | 43797.4792 | 94 | 94
2019-11-28 12:00 | 67 | 64 |  |  | 43797.5 | 89 | 88
2019-11-28 12:30 | 68 | 65 |  |  | 43797.5208 | 88 | 88
2019-11-28 13:00 | 69 | 66 |  |  | 43797.5417 | 87 | 86
2019-11-28 13:30 | 66 | 63 |  |  | 43797.5625 | 85 | 85
2019-11-28 14:00 | 61 | 58 |  |  | 43797.5833 | 77 | 77
2019-11-28 14:30 | 60 | 57 |  |  | 43797.6042 | 76 | 76
2019-11-28 15:00 | 64 | 62 |  |  | 43797.625 | 80 | 80
2019-11-28 15:30 | 65 | 62 |  |  | 43797.6458 | 81 | 80
2019-11-28 16:00 | 68 | 65 |  |  | 43797.6667 | 82 | 80
2019-11-28 16:30 | 72 | 68 |  |  | 43797.6875 | 86 | 83
2019-11-28 17:00 | 75 | 71 |  |  | 43797.7083 | 89 | 86
2019-11-28 17:30 | 76 | 71 |  |  | 43797.7292 | 89 | 86
2019-11-28 18:00 | 77 | 72 |  |  | 43797.75 | 88 | 86
2019-11-28 18:30 | 78 | 73 |  |  | 43797.7708 | 89 | 86
2019-11-28 19:00 | 82 | 78 |  |  | 43797.7917 | 94 | 91
2019-11-28 19:30 | 81 | 77 |  |  | 43797.8125 | 93 | 91
2019-11-28 20:00 | 80 | 75 |  |  | 43797.8333 | 91 | 89
2019-11-28 20:30 | 78 | 74 |  |  | 43797.8542 | 90 | 88
2019-11-28 21:00 | 73 | 71 |  |  | 43797.875 | 84 | 84
2019-11-28 21:30 | 69 | 66 |  |  | 43797.8958 | 79 | 78
2019-11-28 22:00 | 67 | 65 |  |  | 43797.9167 | 78 | 78
2019-11-28 22:30 | 64 | 61 |  |  | 43797.9375 | 75 | 74
2019-11-28 23:00 | 62 | 58 |  |  | 43797.9583 | 70 | 68
2019-11-28 23:30 | 59 | 54 |  |  | 43797.9792 | 67 | 66
2019-11-29 | 56 | 51 |  |  | 43798 | 64 | 63
2019-11-29 00:30 | 54 | 50 |  |  | 43798.0208 | 62 | 61
2019-11-29 01:00 | 52 | 46 |  |  | 43798.0417 | 58 | 57
2019-11-29 01:30 | 51 | 46 |  |  | 43798.0625 | 58 | 56
2019-11-29 02:00 | 52 | 47 |  |  | 43798.0833 | 59 | 57
2019-11-29 02:30 | 52 | 46 |  |  | 43798.1042 | 58 | 57
2019-11-29 03:00 | 52 | 46 |  |  | 43798.125 | 58 | 56
2019-11-29 03:30 | 52 | 46 |  |  | 43798.1458 | 58 | 56
2019-11-29 04:00 | 50 | 44 |  |  | 43798.1667 | 57 | 55
2019-11-29 04:30 | 51 | 45 |  |  | 43798.1875 | 58 | 56
2019-11-29 05:00 | 51 | 46 |  |  | 43798.2083 | 60 | 58
2019-11-29 05:30 | 52 | 46 |  |  | 43798.2292 | 61 | 59
2019-11-29 06:00 | 52 | 47 |  |  | 43798.25 | 62 | 61
2019-11-29 06:30 | 51 | 48 |  |  | 43798.2708 | 65 | 65
2019-11-29 07:00 | 51 | 47 |  |  | 43798.2917 | 67 | 67
2019-11-29 07:30 | 58 | 56 |  |  | 43798.3125 | 75 | 75
2019-11-29 08:00 | 53 | 51 |  |  | 43798.3333 | 75 | 75
2019-11-29 08:30 | 49 | 46 |  |  | 43798.3542 | 74 | 73
2019-11-29 09:00 | 51 | 45 |  |  | 43798.375 | 78 | 76
2019-11-29 09:30 | 54 | 49 |  |  | 43798.3958 | 79 | 77
2019-11-29 10:00 | 55 | 50 |  |  | 43798.4167 | 77 | 75
2019-11-29 10:30 | 52 | 47 |  |  | 43798.4375 | 75 | 74
2019-11-29 11:00 | 51 | 46 |  |  | 43798.4583 | 77 | 75
2019-11-29 11:30 | 50 | 45 |  |  | 43798.4792 | 75 | 73
2019-11-29 12:00 | 49 | 44 |  |  | 43798.5 | 73 | 71
2019-11-29 12:30 | 50 | 45 |  |  | 43798.5208 | 74 | 72
2019-11-29 13:00 | 50 | 45 |  |  | 43798.5417 | 73 | 71
2019-11-29 13:30 | 51 | 45 |  |  | 43798.5625 | 74 | 72
2019-11-29 14:00 | 51 | 45 |  |  | 43798.5833 | 74 | 71
2019-11-29 14:30 | 60 | 55 |  |  | 43798.6042 | 79 | 75
2019-11-29 15:00 | 60 | 56 |  |  | 43798.625 | 79 | 75
2019-11-29 15:30 | 61 | 58 |  |  | 43798.6458 | 81 | 77
2019-11-29 16:00 | 67 | 62 |  |  | 43798.6667 | 84 | 81
2019-11-29 16:30 | 71 | 67 |  |  | 43798.6875 | 86 | 85
2019-11-29 17:00 | 75 | 70 |  |  | 43798.7083 | 89 | 88
2019-11-29 17:30 | 74 | 69 |  |  | 43798.7292 | 88 | 86
2019-11-29 18:00 | 72 | 68 |  |  | 43798.75 | 84 | 84
2019-11-29 18:30 | 71 | 69 |  |  | 43798.7708 | 84 | 84
2019-11-29 19:00 | 73 | 71 |  |  | 43798.7917 | 87 | 87
2019-11-29 19:30 | 72 | 69 |  |  | 43798.8125 | 85 | 85
2019-11-29 20:00 | 69 | 67 |  |  | 43798.8333 | 84 | 83
2019-11-29 20:30 | 69 | 67 |  |  | 43798.8542 | 84 | 83
2019-11-29 21:00 | 65 | 64 |  |  | 43798.875 | 81 | 80
2019-11-29 21:30 | 63 | 61 |  |  | 43798.8958 | 79 | 77
2019-11-29 22:00 | 65 | 63 |  |  | 43798.9167 | 80 | 79
2019-11-29 22:30 | 65 | 63 |  |  | 43798.9375 | 82 | 81
2019-11-29 23:00 | 63 | 60 |  |  | 43798.9583 | 76 | 75
2019-11-29 23:30 | 62 | 54 |  |  | 43798.9792 | 68 | 68
2019-11-30 | 60 | 51 |  |  | 43799 | 66 | 66
2019-11-30 00:30 | 60 | 51 |  |  | 43799.0208 | 66 | 66
2019-11-30 01:00 | 58 | 48 |  |  | 43799.0417 | 62 | 62
2019-11-30 01:30 | 56 | 45 |  |  | 43799.0625 | 58 | 58
2019-11-30 02:00 | 57 | 46 |  |  | 43799.0833 | 58 | 58
2019-11-30 02:30 | 56 | 44 |  |  | 43799.1042 | 57 | 57
2019-11-30 03:00 | 56 | 45 |  |  | 43799.125 | 58 | 57
2019-11-30 03:30 | 56 | 45 |  |  | 43799.1458 | 59 | 59
2019-11-30 04:00 | 56 | 46 |  |  | 43799.1667 | 60 | 60
2019-11-30 04:30 | 55 | 45 |  |  | 43799.1875 | 58 | 58
2019-11-30 05:00 | 55 | 44 |  |  | 43799.2083 | 58 | 58
2019-11-30 05:30 | 58 | 42 |  |  | 43799.2292 | 56 | 56
2019-11-30 06:00 | 56 | 40 |  |  | 43799.25 | 54 | 54
2019-11-30 06:30 | 52 | 36 |  |  | 43799.2708 | 52 | 51
2019-11-30 07:00 | 49 | 33 |  |  | 43799.2917 | 49 | 49
2019-11-30 07:30 | 42 | 28 |  |  | 43799.3125 | 47 | 46
2019-11-30 08:00 | 36 | 23 |  |  | 43799.3333 | 45 | 43
2019-11-30 08:30 | 37 | 25 |  |  | 43799.3542 | 47 | 45
2019-11-30 09:00 | 38 | 28 |  |  | 43799.375 | 50 | 48
2019-11-30 09:30 | 41 | 33 |  |  | 43799.3958 | 55 | 53
2019-11-30 10:00 | 46 | 36 |  |  | 43799.4167 | 57 | 56
2019-11-30 10:30 | 48 | 38 |  |  | 43799.4375 | 58 | 57
2019-11-30 11:00 | 49 | 40 |  |  | 43799.4583 | 60 | 59
2019-11-30 11:30 | 49 | 40 |  |  | 43799.4792 | 59 | 59
2019-11-30 12:00 | 49 | 40 |  |  | 43799.5 | 57 | 57
2019-11-30 12:30 | 48 | 40 |  |  | 43799.5208 | 57 | 57
2019-11-30 13:00 | 52 | 44 |  |  | 43799.5417 | 60 | 60
2019-11-30 13:30 | 51 | 43 |  |  | 43799.5625 | 60 | 60
2019-11-30 14:00 | 50 | 42 |  |  | 43799.5833 | 58 | 58
2019-11-30 14:30 | 51 | 42 |  |  | 43799.6042 | 59 | 59
2019-11-30 15:00 | 54 | 45 |  |  | 43799.625 | 61 | 61
2019-11-30 15:30 | 67 | 58 |  |  | 43799.6458 | 70 | 70
2019-11-30 16:00 | 69 | 60 |  |  | 43799.6667 | 74 | 74
2019-11-30 16:30 | 76 | 65 |  |  | 43799.6875 | 77 | 77
2019-11-30 17:00 | 77 | 66 |  |  | 43799.7083 | 81 | 81
2019-11-30 17:30 | 74 | 63 |  |  | 43799.7292 | 79 | 79
2019-11-30 18:00 | 75 | 64 |  |  | 43799.75 | 81 | 81
2019-11-30 18:30 | 79 | 68 |  |  | 43799.7708 | 86 | 86
2019-11-30 19:00 | 83 | 73 |  |  | 43799.7917 | 90 | 90
2019-11-30 19:30 | 83 | 74 |  |  | 43799.8125 | 91 | 91
2019-11-30 20:00 | 83 | 74 |  |  | 43799.8333 | 90 | 90
2019-11-30 20:30 | 82 | 73 |  |  | 43799.8542 | 89 | 89
2019-11-30 21:00 | 82 | 73 |  |  | 43799.875 | 88 | 88
2019-11-30 21:30 | 80 | 72 |  |  | 43799.8958 | 87 | 87
2019-11-30 22:00 | 80 | 72 |  |  | 43799.9167 | 89 | 89
2019-11-30 22:30 | 80 | 71 |  |  | 43799.9375 | 89 | 89
2019-11-30 23:00 | 76 | 68 |  |  | 43799.9583 | 82 | 82
2019-11-30 23:30 | 75 | 64 |  |  | 43799.9792 | 80 | 79
2019-12-01 | 76 | 59 |  |  | 43800 | 75 | 75
2019-12-01 00:30 | 77 | 59 |  |  | 43800.0208 | 72 | 72
2019-12-01 01:00 | 75 | 56 |  |  | 43800.0417 | 70 | 69
2019-12-01 01:30 | 73 | 53 |  |  | 43800.0625 | 68 | 66
2019-12-01 02:00 | 73 | 52 |  |  | 43800.0833 | 67 | 65
2019-12-01 02:30 | 71 | 50 |  |  | 43800.1042 | 64 | 62
2019-12-01 03:00 | 72 | 50 |  |  | 43800.125 | 65 | 63
2019-12-01 03:30 | 72 | 50 |  |  | 43800.1458 | 65 | 63
2019-12-01 04:00 | 71 | 49 |  |  | 43800.1667 | 64 | 62
2019-12-01 04:30 | 71 | 48 |  |  | 43800.1875 | 65 | 63
2019-12-01 05:00 | 71 | 47 |  |  | 43800.2083 | 63 | 61
2019-12-01 05:30 | 70 | 46 |  |  | 43800.2292 | 62 | 60
2019-12-01 06:00 | 68 | 44 |  |  | 43800.25 | 61 | 59
2019-12-01 06:30 | 63 | 37 |  |  | 43800.2708 | 56 | 54
2019-12-01 07:00 | 59 | 33 |  |  | 43800.2917 | 52 | 51
2019-12-01 07:30 | 57 | 33 |  |  | 43800.3125 | 53 | 52
2019-12-01 08:00 | 56 | 35 |  |  | 43800.3333 | 49 | 49
2019-12-01 08:30 | 59 | 41 |  |  | 43800.3542 | 61 | 60
2019-12-01 09:00 | 53 | 35 |  |  | 43800.375 | 55 | 55
2019-12-01 09:30 | 55 | 39 |  |  | 43800.3958 | 57 | 57
2019-12-01 10:00 | 56 | 41 |  |  | 43800.4167 | 57 | 57
2019-12-01 10:30 | 57 | 44 |  |  | 43800.4375 | 56 | 56
2019-12-01 11:00 | 61 | 49 |  |  | 43800.4583 | 61 | 61
2019-12-01 11:30 | 67 | 54 |  |  | 43800.4792 | 66 | 65
2019-12-01 12:00 | 65 | 52 |  |  | 43800.5 | 59 | 59
2019-12-01 12:30 | 67 | 54 |  |  | 43800.5208 | 66 | 65
2019-12-01 13:00 | 68 | 55 |  |  | 43800.5417 | 63 | 62
2019-12-01 13:30 | 71 | 64 |  |  | 43800.5625 | 74 | 74
2019-12-01 14:00 | 85 | 80 |  |  | 43800.5833 | 85 | 84
2019-12-01 14:30 | 80 | 74 |  |  | 43800.6042 | 93 | 93
2019-12-01 15:00 | 71 | 60 |  |  | 43800.625 | 78 | 77
2019-12-01 15:30 | 77 | 69 |  |  | 43800.6458 | 79 | 79
2019-12-01 16:00 | 81 | 74 |  |  | 43800.6667 | 84 | 83
2019-12-01 16:30 | 84 | 77 |  |  | 43800.6875 | 87 | 87
2019-12-01 17:00 | 86 | 79 |  |  | 43800.7083 | 91 | 91
2019-12-01 17:30 | 85 | 77 |  |  | 43800.7292 | 89 | 89
2019-12-01 18:00 | 88 | 80 |  |  | 43800.75 | 94 | 93
2019-12-01 18:30 | 88 | 80 |  |  | 43800.7708 | 95 | 95
2019-12-01 19:00 | 89 | 81 |  |  | 43800.7917 | 96 | 95
2019-12-01 19:30 | 89 | 81 |  |  | 43800.8125 | 96 | 96
2019-12-01 20:00 | 89 | 81 |  |  | 43800.8333 | 96 | 95
2019-12-01 20:30 | 87 | 79 |  |  | 43800.8542 | 94 | 94
2019-12-01 21:00 | 84 | 77 |  |  | 43800.875 | 91 | 91
2019-12-01 21:30 | 83 | 76 |  |  | 43800.8958 | 91 | 91
2019-12-01 22:00 | 83 | 75 |  |  | 43800.9167 | 91 | 91
2019-12-01 22:30 | 80 | 72 |  |  | 43800.9375 | 88 | 88
2019-12-01 23:00 | 77 | 69 |  |  | 43800.9583 | 83 | 83
2019-12-01 23:30 | 74 | 66 |  |  | 43800.9792 | 80 | 80
2019-12-02 | 71 | 63 |  |  | 43801 | 77 | 77
2019-12-02 00:30 | 72 | 60 |  |  | 43801.0208 | 74 | 73
2019-12-02 01:00 | 76 | 58 |  |  | 43801.0417 | 71 | 69
2019-12-02 01:30 | 75 | 56 |  |  | 43801.0625 | 69 | 68
2019-12-02 02:00 | 75 | 56 |  |  | 43801.0833 | 68 | 67
2019-12-02 02:30 | 75 | 55 |  |  | 43801.1042 | 68 | 67
2019-12-02 03:00 | 74 | 54 |  |  | 43801.125 | 68 | 66
2019-12-02 03:30 | 73 | 52 |  |  | 43801.1458 | 67 | 65
2019-12-02 04:00 | 73 | 52 |  |  | 43801.1667 | 67 | 65
2019-12-02 04:30 | 72 | 53 |  |  | 43801.1875 | 67 | 65
2019-12-02 05:00 | 74 | 54 |  |  | 43801.2083 | 69 | 67
2019-12-02 05:30 | 75 | 56 |  |  | 43801.2292 | 72 | 71
2019-12-02 06:00 | 76 | 59 |  |  | 43801.25 | 76 | 75
2019-12-02 06:30 | 76 | 62 |  |  | 43801.2708 | 82 | 82
2019-12-02 07:00 | 77 | 64 |  |  | 43801.2917 | 86 | 86
2019-12-02 07:30 | 80 | 69 |  |  | 43801.3125 | 93 | 93
2019-12-02 08:00 | 89 | 71 |  |  | 43801.3333 | 100 | 98
2019-12-02 08:30 | 91 | 71 |  |  | 43801.3542 | 103 | 99
2019-12-02 09:00 | 91 | 71 |  |  | 43801.375 | 103 | 99
2019-12-02 09:30 | 90 | 69 |  |  | 43801.3958 | 100 | 96
2019-12-02 10:00 | 90 | 67 |  |  | 43801.4167 | 99 | 95
2019-12-02 10:30 | 89 | 66 |  |  | 43801.4375 | 97 | 93
2019-12-02 11:00 | 89 | 68 |  |  | 43801.4583 | 99 | 94
2019-12-02 11:30 | 90 | 69 |  |  | 43801.4792 | 99 | 95
2019-12-02 12:00 | 92 | 71 |  |  | 43801.5 | 100 | 96
2019-12-02 12:30 | 93 | 73 |  |  | 43801.5208 | 101 | 98
2019-12-02 13:00 | 97 | 76 |  |  | 43801.5417 | 105 | 102
2019-12-02 13:30 | 98 | 79 |  |  | 43801.5625 | 107 | 104
2019-12-02 14:00 | 104 | 82 |  |  | 43801.5833 | 108 | 108
2019-12-02 14:30 | 112 | 86 |  |  | 43801.6042 | 112 | 112
2019-12-02 15:00 | 113 | 88 |  |  | 43801.625 | 114 | 114
2019-12-02 15:30 | 113 | 89 |  |  | 43801.6458 | 115 | 115
2019-12-02 16:00 | 115 | 92 |  |  | 43801.6667 | 117 | 117
2019-12-02 16:30 | 116 | 92 |  |  | 43801.6875 | 117 | 117
2019-12-02 17:00 | 109 | 85 |  |  | 43801.7083 | 116 | 116
2019-12-02 17:30 | 113 | 91 |  |  | 43801.7292 | 120 | 120
2019-12-02 18:00 | 115 | 92 |  |  | 43801.75 | 120 | 119
2019-12-02 18:30 | 112 | 90 |  |  | 43801.7708 | 115 | 115
2019-12-02 19:00 | 107 | 89 |  |  | 43801.7917 | 116 | 115
2019-12-02 19:30 | 107 | 89 |  |  | 43801.8125 | 115 | 114
2019-12-02 20:00 | 107 | 89 |  |  | 43801.8333 | 114 | 113
2019-12-02 20:30 | 103 | 88 |  |  | 43801.8542 | 113 | 111
2019-12-02 21:00 | 90 | 83 |  |  | 43801.875 | 106 | 106
2019-12-02 21:30 | 78 | 76 |  |  | 43801.8958 | 98 | 97
2019-12-02 22:00 | 73 | 71 |  |  | 43801.9167 | 94 | 92
2019-12-02 22:30 | 78 | 75 |  |  | 43801.9375 | 94 | 91
2019-12-02 23:00 | 79 | 74 |  |  | 43801.9583 | 88 | 88
2019-12-02 23:30 | 75 | 69 |  |  | 43801.9792 | 85 | 84
2019-12-03 | 72 | 64 |  |  | 43802 | 80 | 79
2019-12-03 00:30 | 71 | 61 |  |  | 43802.0208 | 76 | 75
2019-12-03 01:00 | 69 | 58 |  |  | 43802.0417 | 73 | 71
2019-12-03 01:30 | 67 | 56 |  |  | 43802.0625 | 70 | 68
2019-12-03 02:00 | 67 | 55 |  |  | 43802.0833 | 69 | 67
2019-12-03 02:30 | 66 | 54 |  |  | 43802.1042 | 67 | 65
2019-12-03 03:00 | 66 | 54 |  |  | 43802.125 | 67 | 64
2019-12-03 03:30 | 64 | 52 |  |  | 43802.1458 | 66 | 63
2019-12-03 04:00 | 63 | 51 |  |  | 43802.1667 | 64 | 61
2019-12-03 04:30 | 63 | 51 |  |  | 43802.1875 | 64 | 61
2019-12-03 05:00 | 64 | 51 |  |  | 43802.2083 | 66 | 63
2019-12-03 05:30 | 65 | 54 |  |  | 43802.2292 | 68 | 66
2019-12-03 06:00 | 65 | 54 |  |  | 43802.25 | 69 | 67
2019-12-03 06:30 | 64 | 56 |  |  | 43802.2708 | 73 | 72
2019-12-03 07:00 | 65 | 59 |  |  | 43802.2917 | 78 | 77
2019-12-03 07:30 | 65 | 59 |  |  | 43802.3125 | 80 | 80
2019-12-03 08:00 | 64 | 58 |  |  | 43802.3333 | 80 | 80
2019-12-03 08:30 | 57 | 50 |  |  | 43802.3542 | 67 | 67
2019-12-03 09:00 | 50 | 42 |  |  | 43802.375 | 53 | 52
2019-12-03 09:30 | 51 | 43 |  |  | 43802.3958 | 53 | 53
2019-12-03 10:00 | 53 | 45 |  |  | 43802.4167 | 55 | 54
2019-12-03 10:30 | 55 | 47 |  |  | 43802.4375 | 56 | 56
2019-12-03 11:00 | 58 | 50 |  |  | 43802.4583 | 59 | 58
2019-12-03 11:30 | 57 | 51 |  |  | 43802.4792 | 61 | 61
2019-12-03 12:00 | 59 | 53 |  |  | 43802.5 | 63 | 62
2019-12-03 12:30 | 59 | 54 |  |  | 43802.5208 | 64 | 63
2019-12-03 13:00 | 63 | 58 |  |  | 43802.5417 | 67 | 66
2019-12-03 13:30 | 65 | 60 |  |  | 43802.5625 | 68 | 67
2019-12-03 14:00 | 66 | 61 |  |  | 43802.5833 | 69 | 68
2019-12-03 14:30 | 70 | 65 |  |  | 43802.6042 | 74 | 74
2019-12-03 15:00 | 90 | 86 |  |  | 43802.625 | 110 | 110
2019-12-03 15:30 | 92 | 90 |  |  | 43802.6458 | 115 | 114
2019-12-03 16:00 | 96 | 93 |  |  | 43802.6667 | 117 | 115
2019-12-03 16:30 | 93 | 90 |  |  | 43802.6875 | 118 | 116
2019-12-03 17:00 | 91 | 88 |  |  | 43802.7083 | 118 | 115
2019-12-03 17:30 | 92 | 89 |  |  | 43802.7292 | 118 | 115
2019-12-03 18:00 | 93 | 90 |  |  | 43802.75 | 116 | 112
2019-12-03 18:30 | 93 | 88 |  |  | 43802.7708 | 113 | 109
2019-12-03 19:00 | 91 | 88 |  |  | 43802.7917 | 111 | 109
2019-12-03 19:30 | 90 | 87 |  |  | 43802.8125 | 111 | 108
2019-12-03 20:00 | 91 | 88 |  |  | 43802.8333 | 112 | 110
2019-12-03 20:30 | 86 | 83 |  |  | 43802.8542 | 107 | 106
2019-12-03 21:00 | 81 | 77 |  |  | 43802.875 | 102 | 100
2019-12-03 21:30 | 78 | 73 |  |  | 43802.8958 | 96 | 94
2019-12-03 22:00 | 73 | 69 |  |  | 43802.9167 | 91 | 91
2019-12-03 22:30 | 72 | 68 |  |  | 43802.9375 | 90 | 89
2019-12-03 23:00 | 77 | 69 |  |  | 43802.9583 | 87 | 85
2019-12-03 23:30 | 76 | 67 |  |  | 43802.9792 | 85 | 83
2019-12-04 | 72 | 62 |  |  | 43803 | 80 | 78
2019-12-04 00:30 | 70 | 60 |  |  | 43803.0208 | 77 | 74
2019-12-04 01:00 | 68 | 57 |  |  | 43803.0417 | 73 | 70
2019-12-04 01:30 | 67 | 55 |  |  | 43803.0625 | 72 | 68
2019-12-04 02:00 | 66 | 54 |  |  | 43803.0833 | 70 | 66
2019-12-04 02:30 | 65 | 52 |  |  | 43803.1042 | 69 | 65
2019-12-04 03:00 | 65 | 52 |  |  | 43803.125 | 69 | 64
2019-12-04 03:30 | 65 | 52 |  |  | 43803.1458 | 67 | 63
2019-12-04 04:00 | 64 | 50 |  |  | 43803.1667 | 67 | 63
2019-12-04 04:30 | 62 | 48 |  |  | 43803.1875 | 65 | 61
2019-12-04 05:00 | 63 | 50 |  |  | 43803.2083 | 68 | 64
2019-12-04 05:30 | 63 | 50 |  |  | 43803.2292 | 69 | 64
2019-12-04 06:00 | 63 | 50 |  |  | 43803.25 | 69 | 66
2019-12-04 06:30 | 63 | 53 |  |  | 43803.2708 | 73 | 71
2019-12-04 07:00 | 62 | 54 |  |  | 43803.2917 | 76 | 75
2019-12-04 07:30 | 64 | 57 |  |  | 43803.3125 | 82 | 81
2019-12-04 08:00 | 64 | 56 |  |  | 43803.3333 | 82 | 81
2019-12-04 08:30 | 64 | 57 |  |  | 43803.3542 | 83 | 82
2019-12-04 09:00 | 64 | 57 |  |  | 43803.375 | 84 | 83
2019-12-04 09:30 | 64 | 57 |  |  | 43803.3958 | 83 | 82
2019-12-04 10:00 | 65 | 57 |  |  | 43803.4167 | 84 | 82
2019-12-04 10:30 | 69 | 59 |  |  | 43803.4375 | 87 | 84
2019-12-04 11:00 | 71 | 63 |  |  | 43803.4583 | 89 | 86
2019-12-04 11:30 | 70 | 65 |  |  | 43803.4792 | 91 | 90
2019-12-04 12:00 | 72 | 68 |  |  | 43803.5 | 93 | 91
2019-12-04 12:30 | 75 | 70 |  |  | 43803.5208 | 95 | 93
2019-12-04 13:00 | 76 | 71 |  |  | 43803.5417 | 95 | 94
2019-12-04 13:30 | 78 | 73 |  |  | 43803.5625 | 95 | 94
2019-12-04 14:00 | 80 | 75 |  |  | 43803.5833 | 97 | 96
2019-12-04 14:30 | 82 | 77 |  |  | 43803.6042 | 99 | 97
2019-12-04 15:00 | 81 | 76 |  |  | 43803.625 | 98 | 97
2019-12-04 15:30 | 81 | 78 |  |  | 43803.6458 | 98 | 97
2019-12-04 16:00 | 80 | 79 |  |  | 43803.6667 | 99 | 98
2019-12-04 16:30 | 82 | 80 |  |  | 43803.6875 | 102 | 100
2019-12-04 17:00 | 76 | 74 |  |  | 43803.7083 | 101 | 99
2019-12-04 17:30 | 78 | 76 |  |  | 43803.7292 | 102 | 101
2019-12-04 18:00 | 77 | 76 |  |  | 43803.75 | 100 | 99
2019-12-04 18:30 | 75 | 73 |  |  | 43803.7708 | 96 | 96
2019-12-04 19:00 | 74 | 73 |  |  | 43803.7917 | 97 | 97
2019-12-04 19:30 | 74 | 73 |  |  | 43803.8125 | 97 | 97
2019-12-04 20:00 | 74 | 72 |  |  | 43803.8333 | 95 | 95
2019-12-04 20:30 | 73 | 70 |  |  | 43803.8542 | 93 | 92
2019-12-04 21:00 | 71 | 68 |  |  | 43803.875 | 89 | 88
2019-12-04 21:30 | 68 | 64 |  |  | 43803.8958 | 84 | 83
2019-12-04 22:00 | 69 | 65 |  |  | 43803.9167 | 86 | 84
2019-12-04 22:30 | 70 | 64 |  |  | 43803.9375 | 86 | 84
2019-12-04 23:00 | 72 | 59 |  |  | 43803.9583 | 81 | 78
2019-12-04 23:30 | 75 | 60 |  |  | 43803.9792 | 79 | 75
2019-12-05 | 72 | 57 |  |  | 43804 | 77 | 73
2019-12-05 00:30 | 72 | 56 |  |  | 43804.0208 | 75 | 71
2019-12-05 01:00 | 72 | 54 |  |  | 43804.0417 | 72 | 67
2019-12-05 01:30 | 71 | 53 |  |  | 43804.0625 | 71 | 66
2019-12-05 02:00 | 70 | 52 |  |  | 43804.0833 | 70 | 64
2019-12-05 02:30 | 70 | 51 |  |  | 43804.1042 | 70 | 63
2019-12-05 03:00 | 69 | 51 |  |  | 43804.125 | 70 | 63
2019-12-05 03:30 | 68 | 50 |  |  | 43804.1458 | 68 | 61
2019-12-05 04:00 | 67 | 48 |  |  | 43804.1667 | 67 | 59
2019-12-05 04:30 | 65 | 47 |  |  | 43804.1875 | 66 | 59
2019-12-05 05:00 | 66 | 48 |  |  | 43804.2083 | 68 | 60
2019-12-05 05:30 | 66 | 49 |  |  | 43804.2292 | 68 | 61
2019-12-05 06:00 | 64 | 48 |  |  | 43804.25 | 67 | 61
2019-12-05 06:30 | 63 | 49 |  |  | 43804.2708 | 70 | 66
2019-12-05 07:00 | 63 | 52 |  |  | 43804.2917 | 73 | 71
2019-12-05 07:30 | 62 | 55 |  |  | 43804.3125 | 78 | 76
2019-12-05 08:00 | 64 | 58 |  |  | 43804.3333 | 82 | 81
2019-12-05 08:30 | 63 | 58 |  |  | 43804.3542 | 83 | 82
2019-12-05 09:00 | 62 | 58 |  |  | 43804.375 | 83 | 82
2019-12-05 09:30 | 65 | 61 |  |  | 43804.3958 | 86 | 85
2019-12-05 10:00 | 68 | 64 |  |  | 43804.4167 | 88 | 88
2019-12-05 10:30 | 77 | 66 |  |  | 43804.4375 | 91 | 90
2019-12-05 11:00 | 83 | 68 |  |  | 43804.4583 | 93 | 91
2019-12-05 11:30 | 83 | 68 |  |  | 43804.4792 | 94 | 92
2019-12-05 12:00 | 84 | 70 |  |  | 43804.5 | 94 | 92
2019-12-05 12:30 | 84 | 70 |  |  | 43804.5208 | 94 | 92
2019-12-05 13:00 | 87 | 74 |  |  | 43804.5417 | 97 | 95
2019-12-05 13:30 | 90 | 78 |  |  | 43804.5625 | 101 | 100
2019-12-05 14:00 | 92 | 81 |  |  | 43804.5833 | 104 | 103
2019-12-05 14:30 | 97 | 86 |  |  | 43804.6042 | 107 | 106
2019-12-05 15:00 | 97 | 87 |  |  | 43804.625 | 108 | 108
2019-12-05 15:30 | 102 | 88 |  |  | 43804.6458 | 110 | 109
2019-12-05 16:00 | 92 | 82 |  |  | 43804.6667 | 108 | 106
2019-12-05 16:30 | 90 | 81 |  |  | 43804.6875 | 106 | 105
2019-12-05 17:00 | 91 | 82 |  |  | 43804.7083 | 107 | 106
2019-12-05 17:30 | 91 | 81 |  |  | 43804.7292 | 105 | 104
2019-12-05 18:00 | 91 | 80 |  |  | 43804.75 | 102 | 101
2019-12-05 18:30 | 81 | 76 |  |  | 43804.7708 | 99 | 98
2019-12-05 19:00 | 80 | 77 |  |  | 43804.7917 | 103 | 100
2019-12-05 19:30 | 80 | 77 |  |  | 43804.8125 | 102 | 100
2019-12-05 20:00 | 80 | 77 |  |  | 43804.8333 | 104 | 101
2019-12-05 20:30 | 79 | 77 |  |  | 43804.8542 | 104 | 100
2019-12-05 21:00 | 77 | 74 |  |  | 43804.875 | 100 | 97
2019-12-05 21:30 | 79 | 71 |  |  | 43804.8958 | 93 | 92
2019-12-05 22:00 | 88 | 74 |  |  | 43804.9167 | 90 | 89
2019-12-05 22:30 | 90 | 73 |  |  | 43804.9375 | 87 | 87
2019-12-05 23:00 | 86 | 67 |  |  | 43804.9583 | 80 | 80
2019-12-05 23:30 | 73 | 65 |  |  | 43804.9792 | 79 | 77
2019-12-06 | 69 | 60 |  |  | 43805 | 75 | 73
2019-12-06 00:30 | 67 | 58 |  |  | 43805.0208 | 72 | 70
2019-12-06 01:00 | 65 | 55 |  |  | 43805.0417 | 69 | 66
2019-12-06 01:30 | 67 | 56 |  |  | 43805.0625 | 70 | 67
2019-12-06 02:00 | 67 | 56 |  |  | 43805.0833 | 69 | 67
2019-12-06 02:30 | 64 | 55 |  |  | 43805.1042 | 67 | 66
2019-12-06 03:00 | 63 | 54 |  |  | 43805.125 | 65 | 64
2019-12-06 03:30 | 63 | 53 |  |  | 43805.1458 | 65 | 64
2019-12-06 04:00 | 62 | 52 |  |  | 43805.1667 | 64 | 64
2019-12-06 04:30 | 62 | 51 |  |  | 43805.1875 | 64 | 62
2019-12-06 05:00 | 62 | 51 |  |  | 43805.2083 | 64 | 63
2019-12-06 05:30 | 61 | 51 |  |  | 43805.2292 | 64 | 63
2019-12-06 06:00 | 58 | 50 |  |  | 43805.25 | 63 | 62
2019-12-06 06:30 | 56 | 50 |  |  | 43805.2708 | 66 | 66
2019-12-06 07:00 | 56 | 50 |  |  | 43805.2917 | 68 | 68
2019-12-06 07:30 | 58 | 54 |  |  | 43805.3125 | 75 | 75
2019-12-06 08:00 | 58 | 54 |  |  | 43805.3333 | 78 | 78
2019-12-06 08:30 | 65 | 57 |  |  | 43805.3542 | 83 | 83
2019-12-06 09:00 | 66 | 59 |  |  | 43805.375 | 85 | 85
2019-12-06 09:30 | 67 | 60 |  |  | 43805.3958 | 88 | 87
2019-12-06 10:00 | 69 | 65 |  |  | 43805.4167 | 93 | 92
2019-12-06 10:30 | 71 | 66 |  |  | 43805.4375 | 95 | 92
2019-12-06 11:00 | 73 | 69 |  |  | 43805.4583 | 98 | 94
2019-12-06 11:30 | 74 | 71 |  |  | 43805.4792 | 99 | 95
2019-12-06 12:00 | 77 | 74 |  |  | 43805.5 | 100 | 97
2019-12-06 12:30 | 79 | 76 |  |  | 43805.5208 | 101 | 98
2019-12-06 13:00 | 84 | 79 |  |  | 43805.5417 | 108 | 101
2019-12-06 13:30 | 86 | 83 |  |  | 43805.5625 | 110 | 104
2019-12-06 14:00 | 88 | 86 |  |  | 43805.5833 | 112 | 107
2019-12-06 14:30 | 88 | 86 |  |  | 43805.6042 | 111 | 106
2019-12-06 15:00 | 89 | 88 |  |  | 43805.625 | 112 | 108
2019-12-06 15:30 | 88 | 86 |  |  | 43805.6458 | 113 | 108
2019-12-06 16:00 | 85 | 84 |  |  | 43805.6667 | 115 | 110
2019-12-06 16:30 | 87 | 86 |  |  | 43805.6875 | 117 | 112
2019-12-06 17:00 | 88 | 87 |  |  | 43805.7083 | 123 | 118
2019-12-06 17:30 | 36 | 35 |  |  | 43805.7292 | 95 | 91
2019-12-06 18:00 | 46 | 44 |  |  | 43805.75 | 95 | 89
2019-12-06 18:30 | 57 | 48 |  |  | 43805.7708 | 98 | 87
2019-12-06 19:00 | 101 | 82 |  |  | 43805.7917 | 124 | 105
2019-12-06 19:30 | 100 | 82 |  |  | 43805.8125 | 123 | 105
2019-12-06 20:00 | 100 | 84 |  |  | 43805.8333 | 122 | 106
2019-12-06 20:30 | 101 | 89 |  |  | 43805.8542 | 122 | 111
2019-12-06 21:00 | 96 | 86 |  |  | 43805.875 | 114 | 107
2019-12-06 21:30 | 95 | 86 |  |  | 43805.8958 | 111 | 106
2019-12-06 22:00 | 94 | 86 |  |  | 43805.9167 | 114 | 108
2019-12-06 22:30 | 89 | 79 |  |  | 43805.9375 | 106 | 99
2019-12-06 23:00 | 89 | 69 |  |  | 43805.9583 | 95 | 87
2019-12-06 23:30 | 90 | 65 |  |  | 43805.9792 | 93 | 83
2019-12-07 | 85 | 59 |  |  | 43806 | 87 | 77
2019-12-07 00:30 | 86 | 59 |  |  | 43806.0208 | 87 | 77
2019-12-07 01:00 | 85 | 58 |  |  | 43806.0417 | 86 | 75
2019-12-07 01:30 | 84 | 54 |  |  | 43806.0625 | 82 | 71
2019-12-07 02:00 | 84 | 53 |  |  | 43806.0833 | 80 | 68
2019-12-07 02:30 | 83 | 51 |  |  | 43806.1042 | 79 | 66
2019-12-07 03:00 | 83 | 51 |  |  | 43806.125 | 79 | 66
2019-12-07 03:30 | 82 | 49 |  |  | 43806.1458 | 77 | 64
2019-12-07 04:00 | 82 | 48 |  |  | 43806.1667 | 77 | 63
2019-12-07 04:30 | 80 | 46 |  |  | 43806.1875 | 75 | 60
2019-12-07 05:00 | 83 | 48 |  |  | 43806.2083 | 76 | 61
2019-12-07 05:30 | 87 | 51 |  |  | 43806.2292 | 78 | 62
2019-12-07 06:00 | 86 | 50 |  |  | 43806.25 | 77 | 61
2019-12-07 06:30 | 82 | 45 |  |  | 43806.2708 | 73 | 57
2019-12-07 07:00 | 78 | 43 |  |  | 43806.2917 | 70 | 56
2019-12-07 07:30 | 77 | 44 |  |  | 43806.3125 | 70 | 58
2019-12-07 08:00 | 77 | 46 |  |  | 43806.3333 | 72 | 62
2019-12-07 08:30 | 78 | 51 |  |  | 43806.3542 | 76 | 67
2019-12-07 09:00 | 81 | 55 |  |  | 43806.375 | 82 | 72
2019-12-07 09:30 | 86 | 59 |  |  | 43806.3958 | 90 | 76
2019-12-07 10:00 | 88 | 63 |  |  | 43806.4167 | 94 | 80
2019-12-07 10:30 | 88 | 65 |  |  | 43806.4375 | 96 | 82
2019-12-07 11:00 | 89 | 68 |  |  | 43806.4583 | 96 | 84
2019-12-07 11:30 | 98 | 71 |  |  | 43806.4792 | 94 | 87
2019-12-07 12:00 | 107 | 73 |  |  | 43806.5 | 93 | 89
2019-12-07 12:30 | 106 | 73 |  |  | 43806.5208 | 92 | 88
2019-12-07 13:00 | 106 | 74 |  |  | 43806.5417 | 93 | 89
2019-12-07 13:30 | 105 | 72 |  |  | 43806.5625 | 91 | 87
2019-12-07 14:00 | 106 | 74 |  |  | 43806.5833 | 93 | 89
2019-12-07 14:30 | 99 | 68 |  |  | 43806.6042 | 91 | 87
2019-12-07 15:00 | 99 | 68 |  |  | 43806.625 | 93 | 89
2019-12-07 15:30 | 102 | 70 |  |  | 43806.6458 | 95 | 90
2019-12-07 16:00 | 104 | 74 |  |  | 43806.6667 | 100 | 95
2019-12-07 16:30 | 106 | 76 |  |  | 43806.6875 | 102 | 97
2019-12-07 17:00 | 108 | 78 |  |  | 43806.7083 | 105 | 100
2019-12-07 17:30 | 107 | 75 |  |  | 43806.7292 | 103 | 98
2019-12-07 18:00 | 100 | 72 |  |  | 43806.75 | 106 | 97
2019-12-07 18:30 | 96 | 70 |  |  | 43806.7708 | 104 | 97
2019-12-07 19:00 | 96 | 72 |  |  | 43806.7917 | 106 | 99
2019-12-07 19:30 | 81 | 69 |  |  | 43806.8125 | 111 | 94
2019-12-07 20:00 | 79 | 67 |  |  | 43806.8333 | 109 | 92
2019-12-07 20:30 | 77 | 65 |  |  | 43806.8542 | 107 | 91
2019-12-07 21:00 | 76 | 63 |  |  | 43806.875 | 104 | 87
2019-12-07 21:30 | 78 | 63 |  |  | 43806.8958 | 101 | 82
2019-12-07 22:00 | 87 | 67 |  |  | 43806.9167 | 104 | 84
2019-12-07 22:30 | 88 | 68 |  |  | 43806.9375 | 105 | 85
2019-12-07 23:00 | 86 | 66 |  |  | 43806.9583 | 102 | 81
2019-12-07 23:30 | 80 | 62 |  |  | 43806.9792 | 95 | 78
2019-12-08 | 75 | 59 |  |  | 43807 | 89 | 75
2019-12-08 00:30 | 76 | 58 |  |  | 43807.0208 | 88 | 72
2019-12-08 01:00 | 75 | 56 |  |  | 43807.0417 | 87 | 70
2019-12-08 01:30 | 75 | 55 |  |  | 43807.0625 | 86 | 69
2019-12-08 02:00 | 76 | 56 |  |  | 43807.0833 | 86 | 68
2019-12-08 02:30 | 75 | 53 |  |  | 43807.1042 | 85 | 66
2019-12-08 03:00 | 72 | 50 |  |  | 43807.125 | 84 | 64
2019-12-08 03:30 | 72 | 50 |  |  | 43807.1458 | 83 | 63
2019-12-08 04:00 | 72 | 49 |  |  | 43807.1667 | 83 | 63
2019-12-08 04:30 | 72 | 49 |  |  | 43807.1875 | 83 | 63
2019-12-08 05:00 | 73 | 49 |  |  | 43807.2083 | 84 | 63
2019-12-08 05:30 | 73 | 48 |  |  | 43807.2292 | 84 | 63
2019-12-08 06:00 | 71 | 46 |  |  | 43807.25 | 84 | 62
2019-12-08 06:30 | 68 | 43 |  |  | 43807.2708 | 80 | 58
2019-12-08 07:00 | 63 | 39 |  |  | 43807.2917 | 77 | 55
2019-12-08 07:30 | 62 | 40 |  |  | 43807.3125 | 76 | 56
2019-12-08 08:00 | 60 | 37 |  |  | 43807.3333 | 75 | 57
2019-12-08 08:30 | 60 | 40 |  |  | 43807.3542 | 78 | 61
2019-12-08 09:00 | 64 | 46 |  |  | 43807.375 | 78 | 63
2019-12-08 09:30 | 64 | 48 |  |  | 43807.3958 | 79 | 65
2019-12-08 10:00 | 67 | 50 |  |  | 43807.4167 | 80 | 66
2019-12-08 10:30 | 67 | 50 |  |  | 43807.4375 | 78 | 63
2019-12-08 11:00 | 65 | 47 |  |  | 43807.4583 | 75 | 60
2019-12-08 11:30 | 64 | 46 |  |  | 43807.4792 | 72 | 55
2019-12-08 12:00 | 64 | 46 |  |  | 43807.5 | 70 | 53
2019-12-08 12:30 | 64 | 47 |  |  | 43807.5208 | 71 | 54
2019-12-08 13:00 | 65 | 49 |  |  | 43807.5417 | 75 | 60
2019-12-08 13:30 | 67 | 50 |  |  | 43807.5625 | 78 | 63
2019-12-08 14:00 | 72 | 51 |  |  | 43807.5833 | 84 | 63
2019-12-08 14:30 | 74 | 53 |  |  | 43807.6042 | 88 | 65
2019-12-08 15:00 | 73 | 52 |  |  | 43807.625 | 86 | 63
2019-12-08 15:30 | 74 | 54 |  |  | 43807.6458 | 89 | 66
2019-12-08 16:00 | 75 | 58 |  |  | 43807.6667 | 91 | 69
2019-12-08 16:30 | 76 | 60 |  |  | 43807.6875 | 93 | 71
2019-12-08 17:00 | 79 | 63 |  |  | 43807.7083 | 97 | 77
2019-12-08 17:30 | 82 | 66 |  |  | 43807.7292 | 100 | 79
2019-12-08 18:00 | 83 | 67 |  |  | 43807.75 | 103 | 82
2019-12-08 18:30 | 87 | 69 |  |  | 43807.7708 | 108 | 87
2019-12-08 19:00 | 91 | 74 |  |  | 43807.7917 | 113 | 92
2019-12-08 19:30 | 90 | 74 |  |  | 43807.8125 | 112 | 93
2019-12-08 20:00 | 91 | 75 |  |  | 43807.8333 | 114 | 94
2019-12-08 20:30 | 92 | 74 |  |  | 43807.8542 | 113 | 93
2019-12-08 21:00 | 94 | 75 |  |  | 43807.875 | 114 | 93
2019-12-08 21:30 | 92 | 73 |  |  | 43807.8958 | 112 | 91
2019-12-08 22:00 | 93 | 73 |  |  | 43807.9167 | 113 | 92
2019-12-08 22:30 | 89 | 71 |  |  | 43807.9375 | 111 | 89
2019-12-08 23:00 | 87 | 68 |  |  | 43807.9583 | 108 | 85
2019-12-08 23:30 | 81 | 64 |  |  | 43807.9792 | 100 | 82
2019-12-09 | 78 | 62 |  |  | 43808 | 95 | 78
2019-12-09 00:30 | 78 | 58 |  |  | 43808.0208 | 93 | 73
2019-12-09 01:00 | 77 | 57 |  |  | 43808.0417 | 91 | 71
2019-12-09 01:30 | 77 | 56 |  |  | 43808.0625 | 91 | 70
2019-12-09 02:00 | 75 | 54 |  |  | 43808.0833 | 89 | 67
2019-12-09 02:30 | 75 | 53 |  |  | 43808.1042 | 89 | 67
2019-12-09 03:00 | 75 | 53 |  |  | 43808.125 | 89 | 66
2019-12-09 03:30 | 75 | 53 |  |  | 43808.1458 | 90 | 67
2019-12-09 04:00 | 74 | 52 |  |  | 43808.1667 | 89 | 65
2019-12-09 04:30 | 73 | 50 |  |  | 43808.1875 | 87 | 63
2019-12-09 05:00 | 73 | 50 |  |  | 43808.2083 | 87 | 63
2019-12-09 05:30 | 70 | 48 |  |  | 43808.2292 | 85 | 62
2019-12-09 06:00 | 69 | 49 |  |  | 43808.25 | 84 | 64
2019-12-09 06:30 | 73 | 56 |  |  | 43808.2708 | 92 | 74
2019-12-09 07:00 | 76 | 59 |  |  | 43808.2917 | 97 | 79
2019-12-09 07:30 | 79 | 63 |  |  | 43808.3125 | 101 | 86
2019-12-09 08:00 | 79 | 63 |  |  | 43808.3333 | 101 | 89
2019-12-09 08:30 | 70 | 64 |  |  | 43808.3542 | 99 | 91
2019-12-09 09:00 | 71 | 65 |  |  | 43808.375 | 103 | 93
2019-12-09 09:30 | 77 | 71 |  |  | 43808.3958 | 109 | 98
2019-12-09 10:00 | 79 | 73 |  |  | 43808.4167 | 110 | 98
2019-12-09 10:30 | 79 | 72 |  |  | 43808.4375 | 109 | 96
2019-12-09 11:00 | 81 | 73 |  |  | 43808.4583 | 112 | 97
2019-12-09 11:30 | 78 | 73 |  |  | 43808.4792 | 109 | 97
2019-12-09 12:00 | 79 | 74 |  |  | 43808.5 | 109 | 97
2019-12-09 12:30 | 80 | 75 |  |  | 43808.5208 | 109 | 97
2019-12-09 13:00 | 81 | 77 |  |  | 43808.5417 | 112 | 100
2019-12-09 13:30 | 80 | 77 |  |  | 43808.5625 | 111 | 100
2019-12-09 14:00 | 82 | 78 |  |  | 43808.5833 | 113 | 102
2019-12-09 14:30 | 86 | 83 |  |  | 43808.6042 | 116 | 104
2019-12-09 15:00 | 83 | 80 |  |  | 43808.625 | 114 | 102
2019-12-09 15:30 | 84 | 80 |  |  | 43808.6458 | 114 | 102
2019-12-09 16:00 | 88 | 84 |  |  | 43808.6667 | 119 | 106
2019-12-09 16:30 | 91 | 87 |  |  | 43808.6875 | 120 | 107
2019-12-09 17:00 | 93 | 89 |  |  | 43808.7083 | 123 | 110
2019-12-09 17:30 | 92 | 88 |  |  | 43808.7292 | 125 | 110
2019-12-09 18:00 | 86 | 82 |  |  | 43808.75 | 122 | 107
2019-12-09 18:30 | 84 | 81 |  |  | 43808.7708 | 116 | 104
2019-12-09 19:00 | 87 | 84 |  |  | 43808.7917 | 120 | 108
2019-12-09 19:30 | 88 | 85 |  |  | 43808.8125 | 120 | 108
2019-12-09 20:00 | 88 | 86 |  |  | 43808.8333 | 119 | 109
2019-12-09 20:30 | 85 | 84 |  |  | 43808.8542 | 114 | 106
2019-12-09 21:00 | 80 | 79 |  |  | 43808.875 | 107 | 101
2019-12-09 21:30 | 75 | 74 |  |  | 43808.8958 | 99 | 95
2019-12-09 22:00 | 74 | 73 |  |  | 43808.9167 | 98 | 94
2019-12-09 22:30 | 75 | 73 |  |  | 43808.9375 | 96 | 90
2019-12-09 23:00 | 80 | 72 |  |  | 43808.9583 | 99 | 85
2019-12-09 23:30 | 78 | 68 |  |  | 43808.9792 | 98 | 81
2019-12-10 | 70 | 63 |  |  | 43809 | 88 | 77
2019-12-10 00:30 | 67 | 60 |  |  | 43809.0208 | 84 | 73
2019-12-10 01:00 | 65 | 57 |  |  | 43809.0417 | 81 | 69
2019-12-10 01:30 | 64 | 55 |  |  | 43809.0625 | 79 | 66
2019-12-10 02:00 | 64 | 54 |  |  | 43809.0833 | 79 | 65
2019-12-10 02:30 | 63 | 53 |  |  | 43809.1042 | 78 | 64
2019-12-10 03:00 | 62 | 53 |  |  | 43809.125 | 78 | 64
2019-12-10 03:30 | 62 | 53 |  |  | 43809.1458 | 77 | 62
2019-12-10 04:00 | 60 | 51 |  |  | 43809.1667 | 76 | 61
2019-12-10 04:30 | 60 | 50 |  |  | 43809.1875 | 75 | 61
2019-12-10 05:00 | 61 | 51 |  |  | 43809.2083 | 76 | 62
2019-12-10 05:30 | 62 | 53 |  |  | 43809.2292 | 78 | 65
2019-12-10 06:00 | 64 | 56 |  |  | 43809.25 | 80 | 69
2019-12-10 06:30 | 67 | 60 |  |  | 43809.2708 | 89 | 77
2019-12-10 07:00 | 70 | 62 |  |  | 43809.2917 | 93 | 82
2019-12-10 07:30 | 69 | 67 |  |  | 43809.3125 | 92 | 91
2019-12-10 08:00 | 71 | 70 |  |  | 43809.3333 | 96 | 96
2019-12-10 08:30 | 75 | 73 |  |  | 43809.3542 | 98 | 98
2019-12-10 09:00 | 75 | 73 |  |  | 43809.375 | 97 | 97
2019-12-10 09:30 | 78 | 76 |  |  | 43809.3958 | 100 | 100
2019-12-10 10:00 | 77 | 75 |  |  | 43809.4167 | 103 | 103
2019-12-10 10:30 | 79 | 78 |  |  | 43809.4375 | 105 | 105
2019-12-10 11:00 | 76 | 75 |  |  | 43809.4583 | 101 | 100
2019-12-10 11:30 | 75 | 74 |  |  | 43809.4792 | 99 | 98
2019-12-10 12:00 | 77 | 76 |  |  | 43809.5 | 101 | 100
2019-12-10 12:30 | 80 | 78 |  |  | 43809.5208 | 104 | 103
2019-12-10 13:00 | 80 | 79 |  |  | 43809.5417 | 102 | 101
2019-12-10 13:30 | 82 | 82 |  |  | 43809.5625 | 104 | 103
2019-12-10 14:00 | 85 | 84 |  |  | 43809.5833 | 106 | 105
2019-12-10 14:30 | 86 | 85 |  |  | 43809.6042 | 105 | 104
2019-12-10 15:00 | 89 | 86 |  |  | 43809.625 | 106 | 106
2019-12-10 15:30 | 90 | 87 |  |  | 43809.6458 | 107 | 106
2019-12-10 16:00 | 90 | 87 |  |  | 43809.6667 | 107 | 107
2019-12-10 16:30 | 84 | 80 |  |  | 43809.6875 | 106 | 105
2019-12-10 17:00 | 89 | 85 |  |  | 43809.7083 | 111 | 110
2019-12-10 17:30 | 89 | 84 |  |  | 43809.7292 | 110 | 109
2019-12-10 18:00 | 86 | 82 |  |  | 43809.75 | 104 | 104
2019-12-10 18:30 | 86 | 80 |  |  | 43809.7708 | 100 | 100
2019-12-10 19:00 | 89 | 83 |  |  | 43809.7917 | 103 | 103
2019-12-10 19:30 | 88 | 82 |  |  | 43809.8125 | 102 | 102
2019-12-10 20:00 | 89 | 84 |  |  | 43809.8333 | 104 | 104
2019-12-10 20:30 | 88 | 83 |  |  | 43809.8542 | 104 | 103
2019-12-10 21:00 | 85 | 79 |  |  | 43809.875 | 99 | 98
2019-12-10 21:30 | 81 | 75 |  |  | 43809.8958 | 95 | 94
2019-12-10 22:00 | 81 | 73 |  |  | 43809.9167 | 94 | 94
2019-12-10 22:30 | 78 | 72 |  |  | 43809.9375 | 92 | 92
2019-12-10 23:00 | 76 | 70 |  |  | 43809.9583 | 87 | 87
2019-12-10 23:30 | 81 | 73 |  |  | 43809.9792 | 87 | 87
2019-12-11 | 79 | 67 |  |  | 43810 | 81 | 81
2019-12-11 00:30 | 78 | 63 |  |  | 43810.0208 | 76 | 75
2019-12-11 01:00 | 75 | 59 |  |  | 43810.0417 | 71 | 71
2019-12-11 01:30 | 76 | 59 |  |  | 43810.0625 | 70 | 69
2019-12-11 02:00 | 77 | 59 |  |  | 43810.0833 | 71 | 71
2019-12-11 02:30 | 75 | 56 |  |  | 43810.1042 | 68 | 67
2019-12-11 03:00 | 72 | 52 |  |  | 43810.125 | 66 | 64
2019-12-11 03:30 | 72 | 52 |  |  | 43810.1458 | 66 | 64
2019-12-11 04:00 | 71 | 52 |  |  | 43810.1667 | 64 | 62
2019-12-11 04:30 | 71 | 52 |  |  | 43810.1875 | 64 | 63
2019-12-11 05:00 | 71 | 53 |  |  | 43810.2083 | 66 | 65
2019-12-11 05:30 | 73 | 55 |  |  | 43810.2292 | 69 | 68
2019-12-11 06:00 | 73 | 56 |  |  | 43810.25 | 71 | 70
2019-12-11 06:30 | 72 | 59 |  |  | 43810.2708 | 77 | 77
2019-12-11 07:00 | 72 | 63 |  |  | 43810.2917 | 83 | 83
2019-12-11 07:30 | 75 | 66 |  |  | 43810.3125 | 90 | 90
2019-12-11 08:00 | 89 | 69 |  |  | 43810.3333 | 98 | 94
2019-12-11 08:30 | 90 | 69 |  |  | 43810.3542 | 98 | 96
2019-12-11 09:00 | 98 | 74 |  |  | 43810.375 | 106 | 105
2019-12-11 09:30 | 99 | 77 |  |  | 43810.3958 | 110 | 109
2019-12-11 10:00 | 106 | 78 |  |  | 43810.4167 | 110 | 110
2019-12-11 10:30 | 109 | 81 |  |  | 43810.4375 | 113 | 112
2019-12-11 11:00 | 109 | 82 |  |  | 43810.4583 | 113 | 113
2019-12-11 11:30 | 112 | 85 |  |  | 43810.4792 | 116 | 116
2019-12-11 12:00 | 116 | 89 |  |  | 43810.5 | 120 | 120
2019-12-11 12:30 | 117 | 91 |  |  | 43810.5208 | 122 | 122
2019-12-11 13:00 | 118 | 94 |  |  | 43810.5417 | 124 | 123
2019-12-11 13:30 | 120 | 99 |  |  | 43810.5625 | 127 | 127
2019-12-11 14:00 | 118 | 99 |  |  | 43810.5833 | 130 | 130
2019-12-11 14:30 | 110 | 92 |  |  | 43810.6042 | 129 | 129
2019-12-11 15:00 | 110 | 90 |  |  | 43810.625 | 129 | 128
2019-12-11 15:30 | 110 | 89 |  |  | 43810.6458 | 126 | 126
2019-12-11 16:00 | 115 | 94 |  |  | 43810.6667 | 128 | 128
2019-12-11 16:30 | 116 | 93 |  |  | 43810.6875 | 122 | 121
2019-12-11 17:00 | 118 | 94 |  |  | 43810.7083 | 124 | 123
2019-12-11 17:30 | 120 | 92 |  |  | 43810.7292 | 120 | 120
2019-12-11 18:00 | 122 | 88 |  |  | 43810.75 | 116 | 115
2019-12-11 18:30 | 121 | 86 |  |  | 43810.7708 | 112 | 111
2019-12-11 19:00 | 122 | 88 |  |  | 43810.7917 | 114 | 113
2019-12-11 19:30 | 122 | 88 |  |  | 43810.8125 | 113 | 112
2019-12-11 20:00 | 122 | 87 |  |  | 43810.8333 | 112 | 110
2019-12-11 20:30 | 121 | 87 |  |  | 43810.8542 | 112 | 110
2019-12-11 21:00 | 120 | 85 |  |  | 43810.875 | 109 | 108
2019-12-11 21:30 | 117 | 82 |  |  | 43810.8958 | 104 | 102
2019-12-11 22:00 | 112 | 82 |  |  | 43810.9167 | 108 | 105
2019-12-11 22:30 | 101 | 74 |  |  | 43810.9375 | 103 | 102
2019-12-11 23:00 | 88 | 74 |  |  | 43810.9583 | 95 | 93
2019-12-11 23:30 | 89 | 71 |  |  | 43810.9792 | 92 | 88
2019-12-12 | 85 | 64 |  |  | 43811 | 86 | 80
2019-12-12 00:30 | 83 | 61 |  |  | 43811.0208 | 80 | 75
2019-12-12 01:00 | 82 | 58 |  |  | 43811.0417 | 76 | 71
2019-12-12 01:30 | 80 | 55 |  |  | 43811.0625 | 73 | 68
2019-12-12 02:00 | 81 | 55 |  |  | 43811.0833 | 73 | 67
2019-12-12 02:30 | 80 | 53 |  |  | 43811.1042 | 71 | 65
2019-12-12 03:00 | 80 | 54 |  |  | 43811.125 | 72 | 66
2019-12-12 03:30 | 80 | 54 |  |  | 43811.1458 | 71 | 65
2019-12-12 04:00 | 79 | 53 |  |  | 43811.1667 | 71 | 65
2019-12-12 04:30 | 78 | 51 |  |  | 43811.1875 | 70 | 63
2019-12-12 05:00 | 77 | 52 |  |  | 43811.2083 | 70 | 63
2019-12-12 05:30 | 78 | 53 |  |  | 43811.2292 | 72 | 66
2019-12-12 06:00 | 84 | 57 |  |  | 43811.25 | 73 | 70
2019-12-12 06:30 | 85 | 58 |  |  | 43811.2708 | 77 | 76
2019-12-12 07:00 | 87 | 63 |  |  | 43811.2917 | 84 | 82
2019-12-12 07:30 | 95 | 67 |  |  | 43811.3125 | 90 | 90
2019-12-12 08:00 | 83 | 71 |  |  | 43811.3333 | 98 | 98
2019-12-12 08:30 | 84 | 74 |  |  | 43811.3542 | 101 | 101
2019-12-12 09:00 | 87 | 77 |  |  | 43811.375 | 105 | 104
2019-12-12 09:30 | 90 | 81 |  |  | 43811.3958 | 112 | 111
2019-12-12 10:00 | 90 | 81 |  |  | 43811.4167 | 111 | 111
2019-12-12 10:30 | 91 | 84 |  |  | 43811.4375 | 112 | 111
2019-12-12 11:00 | 88 | 85 |  |  | 43811.4583 | 112 | 112
2019-12-12 11:30 | 89 | 85 |  |  | 43811.4792 | 112 | 112
2019-12-12 12:00 | 91 | 86 |  |  | 43811.5 | 113 | 113
2019-12-12 12:30 | 90 | 85 |  |  | 43811.5208 | 113 | 113
2019-12-12 13:00 | 90 | 85 |  |  | 43811.5417 | 112 | 112
2019-12-12 13:30 | 91 | 89 |  |  | 43811.5625 | 108 | 108
2019-12-12 14:00 | 92 | 91 |  |  | 43811.5833 | 105 | 105
2019-12-12 14:30 | 92 | 91 |  |  | 43811.6042 | 105 | 105
2019-12-12 15:00 | 89 | 89 |  |  | 43811.625 | 99 | 99
2019-12-12 15:30 | 86 | 86 |  |  | 43811.6458 | 108 | 108
2019-12-12 16:00 | 86 | 86 |  |  | 43811.6667 | 111 | 111
2019-12-12 16:30 | 87 | 87 |  |  | 43811.6875 | 112 | 112
2019-12-12 17:00 | 88 | 88 |  |  | 43811.7083 | 117 | 117
2019-12-12 17:30 | 88 | 87 |  |  | 43811.7292 | 117 | 117
2019-12-12 18:00 | 87 | 85 |  |  | 43811.75 | 114 | 114
2019-12-12 18:30 | 83 | 82 |  |  | 43811.7708 | 107 | 107
2019-12-12 19:00 | 86 | 86 |  |  | 43811.7917 | 110 | 110
2019-12-12 19:30 | 89 | 88 |  |  | 43811.8125 | 111 | 111
2019-12-12 20:00 | 88 | 88 |  |  | 43811.8333 | 112 | 111
2019-12-12 20:30 | 87 | 87 |  |  | 43811.8542 | 110 | 110
2019-12-12 21:00 | 86 | 85 |  |  | 43811.875 | 107 | 107
2019-12-12 21:30 | 81 | 80 |  |  | 43811.8958 | 101 | 101
2019-12-12 22:00 | 80 | 78 |  |  | 43811.9167 | 100 | 100
2019-12-12 22:30 | 87 | 84 |  |  | 43811.9375 | 102 | 102
2019-12-12 23:00 | 88 | 84 |  |  | 43811.9583 | 99 | 99
2019-12-12 23:30 | 79 | 75 |  |  | 43811.9792 | 91 | 91
2019-12-13 | 75 | 70 |  |  | 43812 | 87 | 87
2019-12-13 00:30 | 73 | 67 |  |  | 43812.0208 | 83 | 83
2019-12-13 01:00 | 70 | 64 |  |  | 43812.0417 | 78 | 78
2019-12-13 01:30 | 66 | 62 |  |  | 43812.0625 | 76 | 75
2019-12-13 02:00 | 64 | 60 |  |  | 43812.0833 | 74 | 74
2019-12-13 02:30 | 64 | 60 |  |  | 43812.1042 | 75 | 74
2019-12-13 03:00 | 63 | 60 |  |  | 43812.125 | 73 | 72
2019-12-13 03:30 | 63 | 59 |  |  | 43812.1458 | 72 | 72
2019-12-13 04:00 | 61 | 57 |  |  | 43812.1667 | 72 | 71
2019-12-13 04:30 | 63 | 59 |  |  | 43812.1875 | 73 | 72
2019-12-13 05:00 | 62 | 58 |  |  | 43812.2083 | 73 | 73
2019-12-13 05:30 | 64 | 60 |  |  | 43812.2292 | 76 | 75
2019-12-13 06:00 | 64 | 60 |  |  | 43812.25 | 78 | 77
2019-12-13 06:30 | 65 | 63 |  |  | 43812.2708 | 84 | 82
2019-12-13 07:00 | 69 | 68 |  |  | 43812.2917 | 93 | 91
2019-12-13 07:30 | 74 | 73 |  |  | 43812.3125 | 101 | 99
2019-12-13 08:00 | 77 | 74 |  |  | 43812.3333 | 101 | 101
2019-12-13 08:30 | 77 | 73 |  |  | 43812.3542 | 102 | 102
2019-12-13 09:00 | 87 | 85 |  |  | 43812.375 | 110 | 110
2019-12-13 09:30 | 97 | 96 |  |  | 43812.3958 | 119 | 119
2019-12-13 10:00 | 96 | 95 |  |  | 43812.4167 | 118 | 118
2019-12-13 10:30 | 94 | 93 |  |  | 43812.4375 | 120 | 120
2019-12-13 11:00 | 92 | 92 |  |  | 43812.4583 | 122 | 121
2019-12-13 11:30 | 95 | 95 |  |  | 43812.4792 | 120 | 119
2019-12-13 12:00 | 94 | 94 |  |  | 43812.5 | 116 | 116
2019-12-13 12:30 | 91 | 91 |  |  | 43812.5208 | 110 | 110
2019-12-13 13:00 | 95 | 95 |  |  | 43812.5417 | 115 | 115
2019-12-13 13:30 | 101 | 100 |  |  | 43812.5625 | 124 | 123
2019-12-13 14:00 | 94 | 94 |  |  | 43812.5833 | 124 | 123
2019-12-13 14:30 | 90 | 89 |  |  | 43812.6042 | 114 | 114
2019-12-13 15:00 | 94 | 94 |  |  | 43812.625 | 118 | 117
2019-12-13 15:30 | 105 | 104 |  |  | 43812.6458 | 121 | 121
2019-12-13 16:00 | 94 | 93 |  |  | 43812.6667 | 123 | 123
2019-12-13 16:30 | 84 | 83 |  |  | 43812.6875 | 110 | 110
2019-12-13 17:00 | 86 | 85 |  |  | 43812.7083 | 108 | 108
2019-12-13 17:30 | 85 | 84 |  |  | 43812.7292 | 107 | 105
2019-12-13 18:00 | 86 | 85 |  |  | 43812.75 | 106 | 105
2019-12-13 18:30 | 88 | 87 |  |  | 43812.7708 | 104 | 104
2019-12-13 19:00 | 83 | 82 |  |  | 43812.7917 | 104 | 103
2019-12-13 19:30 | 81 | 80 |  |  | 43812.8125 | 101 | 101
2019-12-13 20:00 | 81 | 80 |  |  | 43812.8333 | 102 | 101
2019-12-13 20:30 | 79 | 78 |  |  | 43812.8542 | 100 | 99
2019-12-13 21:00 | 76 | 75 |  |  | 43812.875 | 96 | 95
2019-12-13 21:30 | 72 | 71 |  |  | 43812.8958 | 91 | 90
2019-12-13 22:00 | 69 | 67 |  |  | 43812.9167 | 89 | 88
2019-12-13 22:30 | 69 | 68 |  |  | 43812.9375 | 91 | 90
2019-12-13 23:00 | 67 | 66 |  |  | 43812.9583 | 87 | 86
2019-12-13 23:30 | 65 | 59 |  |  | 43812.9792 | 79 | 79
2019-12-14 | 60 | 54 |  |  | 43813 | 72 | 72
2019-12-14 00:30 | 57 | 49 |  |  | 43813.0208 | 68 | 67
2019-12-14 01:00 | 56 | 48 |  |  | 43813.0417 | 64 | 64
2019-12-14 01:30 | 60 | 52 |  |  | 43813.0625 | 65 | 64
2019-12-14 02:00 | 61 | 52 |  |  | 43813.0833 | 64 | 64
2019-12-14 02:30 | 60 | 51 |  |  | 43813.1042 | 64 | 64
2019-12-14 03:00 | 59 | 50 |  |  | 43813.125 | 62 | 62
2019-12-14 03:30 | 59 | 50 |  |  | 43813.1458 | 63 | 63
2019-12-14 04:00 | 59 | 51 |  |  | 43813.1667 | 63 | 63
2019-12-14 04:30 | 61 | 52 |  |  | 43813.1875 | 65 | 65
2019-12-14 05:00 | 62 | 53 |  |  | 43813.2083 | 66 | 66
2019-12-14 05:30 | 59 | 50 |  |  | 43813.2292 | 63 | 63
2019-12-14 06:00 | 57 | 48 |  |  | 43813.25 | 61 | 61
2019-12-14 06:30 | 57 | 49 |  |  | 43813.2708 | 64 | 64
2019-12-14 07:00 | 57 | 49 |  |  | 43813.2917 | 65 | 65
2019-12-14 07:30 | 58 | 52 |  |  | 43813.3125 | 66 | 66
2019-12-14 08:00 | 58 | 52 |  |  | 43813.3333 | 68 | 68
2019-12-14 08:30 | 59 | 54 |  |  | 43813.3542 | 74 | 73
2019-12-14 09:00 | 58 | 52 |  |  | 43813.375 | 73 | 72
2019-12-14 09:30 | 58 | 53 |  |  | 43813.3958 | 70 | 70
2019-12-14 10:00 | 61 | 56 |  |  | 43813.4167 | 74 | 73
2019-12-14 10:30 | 59 | 56 |  |  | 43813.4375 | 78 | 76
2019-12-14 11:00 | 59 | 56 |  |  | 43813.4583 | 79 | 77
2019-12-14 11:30 | 59 | 57 |  |  | 43813.4792 | 77 | 76
2019-12-14 12:00 | 59 | 57 |  |  | 43813.5 | 76 | 74
2019-12-14 12:30 | 59 | 56 |  |  | 43813.5208 | 75 | 73
2019-12-14 13:00 | 59 | 58 |  |  | 43813.5417 | 77 | 74
2019-12-14 13:30 | 61 | 60 |  |  | 43813.5625 | 78 | 76
2019-12-14 14:00 | 62 | 61 |  |  | 43813.5833 | 79 | 77
2019-12-14 14:30 | 67 | 67 |  |  | 43813.6042 | 84 | 81
2019-12-14 15:00 | 69 | 68 |  |  | 43813.625 | 85 | 82
2019-12-14 15:30 | 72 | 72 |  |  | 43813.6458 | 88 | 86
2019-12-14 16:00 | 76 | 75 |  |  | 43813.6667 | 91 | 90
2019-12-14 16:30 | 77 | 76 |  |  | 43813.6875 | 92 | 92
2019-12-14 17:00 | 76 | 75 |  |  | 43813.7083 | 94 | 94
2019-12-14 17:30 | 69 | 69 |  |  | 43813.7292 | 93 | 93
2019-12-14 18:00 | 70 | 69 |  |  | 43813.75 | 94 | 94
2019-12-14 18:30 | 69 | 68 |  |  | 43813.7708 | 95 | 94
2019-12-14 19:00 | 71 | 71 |  |  | 43813.7917 | 100 | 98
2019-12-14 19:30 | 71 | 70 |  |  | 43813.8125 | 99 | 98
2019-12-14 20:00 | 71 | 71 |  |  | 43813.8333 | 99 | 98
2019-12-14 20:30 | 74 | 73 |  |  | 43813.8542 | 101 | 100
2019-12-14 21:00 | 69 | 69 |  |  | 43813.875 | 95 | 94
2019-12-14 21:30 | 68 | 67 |  |  | 43813.8958 | 92 | 91
2019-12-14 22:00 | 75 | 74 |  |  | 43813.9167 | 95 | 94
2019-12-14 22:30 | 78 | 78 |  |  | 43813.9375 | 98 | 97
2019-12-14 23:00 | 79 | 79 |  |  | 43813.9583 | 97 | 96
2019-12-14 23:30 | 76 | 75 |  |  | 43813.9792 | 94 | 92
2019-12-15 | 69 | 69 |  |  | 43814 | 87 | 85
2019-12-15 00:30 | 68 | 66 |  |  | 43814.0208 | 82 | 81
2019-12-15 01:00 | 65 | 63 |  |  | 43814.0417 | 78 | 76
2019-12-15 01:30 | 64 | 62 |  |  | 43814.0625 | 76 | 75
2019-12-15 02:00 | 63 | 60 |  |  | 43814.0833 | 76 | 75
2019-12-15 02:30 | 63 | 60 |  |  | 43814.1042 | 74 | 73
2019-12-15 03:00 | 61 | 57 |  |  | 43814.125 | 72 | 71
2019-12-15 03:30 | 59 | 56 |  |  | 43814.1458 | 70 | 68
2019-12-15 04:00 | 56 | 53 |  |  | 43814.1667 | 68 | 67
2019-12-15 04:30 | 54 | 51 |  |  | 43814.1875 | 66 | 65
2019-12-15 05:00 | 54 | 50 |  |  | 43814.2083 | 66 | 64
2019-12-15 05:30 | 53 | 50 |  |  | 43814.2292 | 65 | 64
2019-12-15 06:00 | 52 | 48 |  |  | 43814.25 | 64 | 63
2019-12-15 06:30 | 51 | 47 |  |  | 43814.2708 | 63 | 62
2019-12-15 07:00 | 47 | 43 |  |  | 43814.2917 | 59 | 57
2019-12-15 07:30 | 46 | 43 |  |  | 43814.3125 | 61 | 59
2019-12-15 08:00 | 48 | 45 |  |  | 43814.3333 | 62 | 61
2019-12-15 08:30 | 50 | 48 |  |  | 43814.3542 | 63 | 62
2019-12-15 09:00 | 52 | 49 |  |  | 43814.375 | 65 | 63
2019-12-15 09:30 | 53 | 51 |  |  | 43814.3958 | 66 | 65
2019-12-15 10:00 | 56 | 55 |  |  | 43814.4167 | 68 | 66
2019-12-15 10:30 | 60 | 59 |  |  | 43814.4375 | 72 | 70
2019-12-15 11:00 | 63 | 61 |  |  | 43814.4583 | 73 | 72
2019-12-15 11:30 | 64 | 64 |  |  | 43814.4792 | 77 | 75
2019-12-15 12:00 | 67 | 66 |  |  | 43814.5 | 78 | 77
2019-12-15 12:30 | 67 | 67 |  |  | 43814.5208 | 78 | 77
2019-12-15 13:00 | 69 | 68 |  |  | 43814.5417 | 78 | 77
2019-12-15 13:30 | 72 | 72 |  |  | 43814.5625 | 81 | 79
2019-12-15 14:00 | 74 | 74 |  |  | 43814.5833 | 82 | 81
2019-12-15 14:30 | 76 | 76 |  |  | 43814.6042 | 86 | 85
2019-12-15 15:00 | 80 | 80 |  |  | 43814.625 | 87 | 86
2019-12-15 15:30 | 77 | 77 |  |  | 43814.6458 | 90 | 90
2019-12-15 16:00 | 82 | 82 |  |  | 43814.6667 | 94 | 93
2019-12-15 16:30 | 83 | 83 |  |  | 43814.6875 | 96 | 96
2019-12-15 17:00 | 80 | 80 |  |  | 43814.7083 | 98 | 98
2019-12-15 17:30 | 80 | 79 |  |  | 43814.7292 | 99 | 99
2019-12-15 18:00 | 76 | 76 |  |  | 43814.75 | 97 | 97
2019-12-15 18:30 | 76 | 76 |  |  | 43814.7708 | 98 | 98
2019-12-15 19:00 | 77 | 77 |  |  | 43814.7917 | 101 | 101
2019-12-15 19:30 | 77 | 77 |  |  | 43814.8125 | 102 | 102
2019-12-15 20:00 | 76 | 76 |  |  | 43814.8333 | 101 | 101
2019-12-15 20:30 | 74 | 74 |  |  | 43814.8542 | 100 | 99
2019-12-15 21:00 | 72 | 72 |  |  | 43814.875 | 96 | 96
2019-12-15 21:30 | 70 | 70 |  |  | 43814.8958 | 93 | 93
2019-12-15 22:00 | 70 | 70 |  |  | 43814.9167 | 94 | 94
2019-12-15 22:30 | 68 | 68 |  |  | 43814.9375 | 93 | 92
2019-12-15 23:00 | 75 | 73 |  |  | 43814.9583 | 91 | 90
2019-12-15 23:30 | 69 | 67 |  |  | 43814.9792 | 85 | 84
2019-12-16 | 64 | 62 |  |  | 43815 | 80 | 79
2019-12-16 00:30 | 63 | 61 |  |  | 43815.0208 | 77 | 77
2019-12-16 01:00 | 63 | 60 |  |  | 43815.0417 | 74 | 74
2019-12-16 01:30 | 60 | 57 |  |  | 43815.0625 | 72 | 72
2019-12-16 02:00 | 59 | 56 |  |  | 43815.0833 | 70 | 70
2019-12-16 02:30 | 58 | 55 |  |  | 43815.1042 | 68 | 68
2019-12-16 03:00 | 57 | 54 |  |  | 43815.125 | 68 | 68
2019-12-16 03:30 | 56 | 53 |  |  | 43815.1458 | 67 | 67
2019-12-16 04:00 | 56 | 52 |  |  | 43815.1667 | 66 | 66
2019-12-16 04:30 | 56 | 53 |  |  | 43815.1875 | 67 | 67
2019-12-16 05:00 | 57 | 54 |  |  | 43815.2083 | 69 | 68
2019-12-16 05:30 | 62 | 59 |  |  | 43815.2292 | 74 | 74
2019-12-16 06:00 | 67 | 65 |  |  | 43815.25 | 81 | 80
2019-12-16 06:30 | 71 | 70 |  |  | 43815.2708 | 87 | 87
2019-12-16 07:00 | 74 | 73 |  |  | 43815.2917 | 93 | 93
2019-12-16 07:30 | 75 | 75 |  |  | 43815.3125 | 100 | 99
2019-12-16 08:00 | 74 | 74 |  |  | 43815.3333 | 100 | 99
2019-12-16 08:30 | 72 | 72 |  |  | 43815.3542 | 100 | 99
2019-12-16 09:00 | 75 | 75 |  |  | 43815.375 | 103 | 102
2019-12-16 09:30 | 84 | 84 |  |  | 43815.3958 | 111 | 110
2019-12-16 10:00 | 84 | 84 |  |  | 43815.4167 | 112 | 110
2019-12-16 10:30 | 86 | 85 |  |  | 43815.4375 | 113 | 112
2019-12-16 11:00 | 89 | 89 |  |  | 43815.4583 | 116 | 115
2019-12-16 11:30 | 91 | 90 |  |  | 43815.4792 | 117 | 115
2019-12-16 12:00 | 93 | 93 |  |  | 43815.5 | 119 | 117
2019-12-16 12:30 | 96 | 96 |  |  | 43815.5208 | 122 | 120
2019-12-16 13:00 | 100 | 99 |  |  | 43815.5417 | 126 | 125
2019-12-16 13:30 | 103 | 103 |  |  | 43815.5625 | 128 | 128
2019-12-16 14:00 | 109 | 108 |  |  | 43815.5833 | 134 | 133
2019-12-16 14:30 | 105 | 103 |  |  | 43815.6042 | 135 | 134
2019-12-16 15:00 | 103 | 102 |  |  | 43815.625 | 132 | 132
2019-12-16 15:30 | 104 | 104 |  |  | 43815.6458 | 135 | 135
2019-12-16 16:00 | 100 | 100 |  |  | 43815.6667 | 126 | 126
2019-12-16 16:30 | 99 | 99 |  |  | 43815.6875 | 123 | 123
2019-12-16 17:00 | 100 | 100 |  |  | 43815.7083 | 125 | 124
2019-12-16 17:30 | 100 | 100 |  |  | 43815.7292 | 122 | 122
2019-12-16 18:00 | 100 | 100 |  |  | 43815.75 | 121 | 121
2019-12-16 18:30 | 92 | 92 |  |  | 43815.7708 | 114 | 113
2019-12-16 19:00 | 93 | 92 |  |  | 43815.7917 | 112 | 112
2019-12-16 19:30 | 89 | 89 |  |  | 43815.8125 | 107 | 107
2019-12-16 20:00 | 85 | 85 |  |  | 43815.8333 | 103 | 103
2019-12-16 20:30 | 87 | 87 |  |  | 43815.8542 | 106 | 106
2019-12-16 21:00 | 87 | 87 |  |  | 43815.875 | 106 | 106
2019-12-16 21:30 | 85 | 85 |  |  | 43815.8958 | 100 | 100
2019-12-16 22:00 | 82 | 82 |  |  | 43815.9167 | 96 | 96
2019-12-16 22:30 | 74 | 74 |  |  | 43815.9375 | 88 | 88
2019-12-16 23:00 | 70 | 70 |  |  | 43815.9583 | 82 | 82
2019-12-16 23:30 | 68 | 67 |  |  | 43815.9792 | 80 | 80
2019-12-17 | 66 | 65 |  |  | 43816 | 78 | 78
2019-12-17 00:30 | 63 | 62 |  |  | 43816.0208 | 74 | 74
2019-12-17 01:00 | 58 | 58 |  |  | 43816.0417 | 68 | 68
2019-12-17 01:30 | 58 | 58 |  |  | 43816.0625 | 68 | 68
2019-12-17 02:00 | 59 | 58 |  |  | 43816.0833 | 68 | 68
2019-12-17 02:30 | 58 | 57 |  |  | 43816.1042 | 67 | 67
2019-12-17 03:00 | 59 | 58 |  |  | 43816.125 | 69 | 69
2019-12-17 03:30 | 56 | 55 |  |  | 43816.1458 | 66 | 66
2019-12-17 04:00 | 54 | 53 |  |  | 43816.1667 | 63 | 63
2019-12-17 04:30 | 51 | 50 |  |  | 43816.1875 | 61 | 61
2019-12-17 05:00 | 50 | 49 |  |  | 43816.2083 | 61 | 60
2019-12-17 05:30 | 52 | 51 |  |  | 43816.2292 | 62 | 62
2019-12-17 06:00 | 53 | 52 |  |  | 43816.25 | 65 | 65
2019-12-17 06:30 | 56 | 55 |  |  | 43816.2708 | 73 | 73
2019-12-17 07:00 | 59 | 59 |  |  | 43816.2917 | 79 | 79
2019-12-17 07:30 | 63 | 63 |  |  | 43816.3125 | 85 | 85
2019-12-17 08:00 | 64 | 64 |  |  | 43816.3333 | 88 | 88
2019-12-17 08:30 | 67 | 67 |  |  | 43816.3542 | 88 | 87
2019-12-17 09:00 | 70 | 69 |  |  | 43816.375 | 88 | 87
2019-12-17 09:30 | 70 | 69 |  |  | 43816.3958 | 89 | 88
2019-12-17 10:00 | 71 | 71 |  |  | 43816.4167 | 89 | 88
2019-12-17 10:30 | 71 | 70 |  |  | 43816.4375 | 86 | 86
2019-12-17 11:00 | 70 | 70 |  |  | 43816.4583 | 84 | 84
2019-12-17 11:30 | 66 | 66 |  |  | 43816.4792 | 79 | 79
2019-12-17 12:00 | 63 | 63 |  |  | 43816.5 | 75 | 75
2019-12-17 12:30 | 65 | 65 |  |  | 43816.5208 | 74 | 74
2019-12-17 13:00 | 67 | 67 |  |  | 43816.5417 | 74 | 74
2019-12-17 13:30 | 69 | 69 |  |  | 43816.5625 | 76 | 76
2019-12-17 14:00 | 70 | 70 |  |  | 43816.5833 | 76 | 76
2019-12-17 14:30 | 74 | 73 |  |  | 43816.6042 | 79 | 79
2019-12-17 15:00 | 75 | 74 |  |  | 43816.625 | 79 | 79
2019-12-17 15:30 | 80 | 79 |  |  | 43816.6458 | 84 | 83
2019-12-17 16:00 | 86 | 84 |  |  | 43816.6667 | 90 | 89
2019-12-17 16:30 | 91 | 88 |  |  | 43816.6875 | 91 | 90
2019-12-17 17:00 | 95 | 93 |  |  | 43816.7083 | 95 | 95
2019-12-17 17:30 | 93 | 92 |  |  | 43816.7292 | 95 | 95
2019-12-17 18:00 | 86 | 86 |  |  | 43816.75 | 100 | 100
2019-12-17 18:30 | 86 | 85 |  |  | 43816.7708 | 99 | 99
2019-12-17 19:00 | 88 | 88 |  |  | 43816.7917 | 102 | 102
2019-12-17 19:30 | 89 | 89 |  |  | 43816.8125 | 102 | 102
2019-12-17 20:00 | 88 | 88 |  |  | 43816.8333 | 101 | 101
2019-12-17 20:30 | 88 | 88 |  |  | 43816.8542 | 101 | 101
2019-12-17 21:00 | 84 | 84 |  |  | 43816.875 | 96 | 96
2019-12-17 21:30 | 78 | 78 |  |  | 43816.8958 | 90 | 90
2019-12-17 22:00 | 73 | 73 |  |  | 43816.9167 | 86 | 86
2019-12-17 22:30 | 70 | 70 |  |  | 43816.9375 | 83 | 83
2019-12-17 23:00 | 68 | 68 |  |  | 43816.9583 | 80 | 80
2019-12-17 23:30 | 65 | 65 |  |  | 43816.9792 | 78 | 78
2019-12-18 | 60 | 60 |  |  | 43817 | 73 | 73
2019-12-18 00:30 | 56 | 56 |  |  | 43817.0208 | 68 | 68
2019-12-18 01:00 | 55 | 55 |  |  | 43817.0417 | 65 | 65
2019-12-18 01:30 | 54 | 54 |  |  | 43817.0625 | 63 | 63
2019-12-18 02:00 | 53 | 53 |  |  | 43817.0833 | 63 | 63
2019-12-18 02:30 | 53 | 53 |  |  | 43817.1042 | 62 | 62
2019-12-18 03:00 | 54 | 53 |  |  | 43817.125 | 63 | 63
2019-12-18 03:30 | 54 | 53 |  |  | 43817.1458 | 64 | 64
2019-12-18 04:00 | 52 | 51 |  |  | 43817.1667 | 62 | 62
2019-12-18 04:30 | 52 | 52 |  |  | 43817.1875 | 62 | 62
2019-12-18 05:00 | 53 | 52 |  |  | 43817.2083 | 63 | 63
2019-12-18 05:30 | 53 | 53 |  |  | 43817.2292 | 64 | 64
2019-12-18 06:00 | 53 | 53 |  |  | 43817.25 | 65 | 65
2019-12-18 06:30 | 57 | 57 |  |  | 43817.2708 | 72 | 72
2019-12-18 07:00 | 57 | 57 |  |  | 43817.2917 | 75 | 75
2019-12-18 07:30 | 60 | 60 |  |  | 43817.3125 | 82 | 82
2019-12-18 08:00 | 57 | 57 |  |  | 43817.3333 | 77 | 77
2019-12-18 08:30 | 59 | 58 |  |  | 43817.3542 | 80 | 80
2019-12-18 09:00 | 62 | 62 |  |  | 43817.375 | 85 | 84
2019-12-18 09:30 | 61 | 61 |  |  | 43817.3958 | 84 | 84
2019-12-18 10:00 | 58 | 58 |  |  | 43817.4167 | 80 | 80
2019-12-18 10:30 | 56 | 56 |  |  | 43817.4375 | 76 | 76
2019-12-18 11:00 | 55 | 55 |  |  | 43817.4583 | 75 | 74
2019-12-18 11:30 | 55 | 54 |  |  | 43817.4792 | 75 | 74
2019-12-18 12:00 | 55 | 54 |  |  | 43817.5 | 74 | 73
2019-12-18 12:30 | 54 | 54 |  |  | 43817.5208 | 73 | 73
2019-12-18 13:00 | 56 | 56 |  |  | 43817.5417 | 74 | 73
2019-12-18 13:30 | 58 | 58 |  |  | 43817.5625 | 75 | 74
2019-12-18 14:00 | 59 | 58 |  |  | 43817.5833 | 76 | 75
2019-12-18 14:30 | 61 | 60 |  |  | 43817.6042 | 78 | 77
2019-12-18 15:00 | 61 | 61 |  |  | 43817.625 | 78 | 77
2019-12-18 15:30 | 64 | 63 |  |  | 43817.6458 | 81 | 80
2019-12-18 16:00 | 69 | 68 |  |  | 43817.6667 | 86 | 85
2019-12-18 16:30 | 72 | 72 |  |  | 43817.6875 | 89 | 88
2019-12-18 17:00 | 75 | 75 |  |  | 43817.7083 | 91 | 90
2019-12-18 17:30 | 76 | 76 |  |  | 43817.7292 | 90 | 90
2019-12-18 18:00 | 77 | 77 |  |  | 43817.75 | 90 | 90
2019-12-18 18:30 | 77 | 77 |  |  | 43817.7708 | 90 | 90
2019-12-18 19:00 | 80 | 80 |  |  | 43817.7917 | 94 | 94
2019-12-18 19:30 | 82 | 82 |  |  | 43817.8125 | 94 | 94
2019-12-18 20:00 | 79 | 79 |  |  | 43817.8333 | 92 | 92
2019-12-18 20:30 | 78 | 78 |  |  | 43817.8542 | 90 | 90
2019-12-18 21:00 | 74 | 74 |  |  | 43817.875 | 86 | 86
2019-12-18 21:30 | 71 | 71 |  |  | 43817.8958 | 83 | 82
2019-12-18 22:00 | 66 | 66 |  |  | 43817.9167 | 79 | 79
2019-12-18 22:30 | 64 | 64 |  |  | 43817.9375 | 78 | 78
2019-12-18 23:00 | 63 | 63 |  |  | 43817.9583 | 75 | 75
2019-12-18 23:30 | 60 | 60 |  |  | 43817.9792 | 73 | 73
2019-12-19 | 55 | 55 |  |  | 43818 | 68 | 68
2019-12-19 00:30 | 51 | 51 |  |  | 43818.0208 | 63 | 63
2019-12-19 01:00 | 49 | 49 |  |  | 43818.0417 | 61 | 61
2019-12-19 01:30 | 46 | 46 |  |  | 43818.0625 | 59 | 59
2019-12-19 02:00 | 45 | 45 |  |  | 43818.0833 | 58 | 58
2019-12-19 02:30 | 44 | 44 |  |  | 43818.1042 | 57 | 57
2019-12-19 03:00 | 46 | 46 |  |  | 43818.125 | 58 | 58
2019-12-19 03:30 | 46 | 45 |  |  | 43818.1458 | 58 | 57
2019-12-19 04:00 | 46 | 45 |  |  | 43818.1667 | 58 | 57
2019-12-19 04:30 | 45 | 44 |  |  | 43818.1875 | 57 | 56
2019-12-19 05:00 | 47 | 45 |  |  | 43818.2083 | 59 | 58
2019-12-19 05:30 | 48 | 46 |  |  | 43818.2292 | 60 | 60
2019-12-19 06:00 | 50 | 49 |  |  | 43818.25 | 63 | 63
2019-12-19 06:30 | 52 | 50 |  |  | 43818.2708 | 67 | 67
2019-12-19 07:00 | 52 | 49 |  |  | 43818.2917 | 69 | 69
2019-12-19 07:30 | 53 | 50 |  |  | 43818.3125 | 71 | 71
2019-12-19 08:00 | 54 | 50 |  |  | 43818.3333 | 73 | 73
2019-12-19 08:30 | 58 | 54 |  |  | 43818.3542 | 78 | 77
2019-12-19 09:00 | 62 | 56 |  |  | 43818.375 | 81 | 80
2019-12-19 09:30 | 63 | 57 |  |  | 43818.3958 | 81 | 80
2019-12-19 10:00 | 64 | 57 |  |  | 43818.4167 | 81 | 80
2019-12-19 10:30 | 63 | 55 |  |  | 43818.4375 | 78 | 77
2019-12-19 11:00 | 62 | 54 |  |  | 43818.4583 | 75 | 74
2019-12-19 11:30 | 58 | 50 |  |  | 43818.4792 | 71 | 70
2019-12-19 12:00 | 57 | 49 |  |  | 43818.5 | 70 | 69
2019-12-19 12:30 | 57 | 49 |  |  | 43818.5208 | 70 | 69
2019-12-19 13:00 | 56 | 49 |  |  | 43818.5417 | 68 | 67
2019-12-19 13:30 | 58 | 52 |  |  | 43818.5625 | 70 | 70
2019-12-19 14:00 | 62 | 57 |  |  | 43818.5833 | 76 | 75
2019-12-19 14:30 | 65 | 61 |  |  | 43818.6042 | 79 | 78
2019-12-19 15:00 | 64 | 59 |  |  | 43818.625 | 76 | 76
2019-12-19 15:30 | 62 | 58 |  |  | 43818.6458 | 76 | 76
2019-12-19 16:00 | 69 | 66 |  |  | 43818.6667 | 83 | 83
2019-12-19 16:30 | 75 | 72 |  |  | 43818.6875 | 89 | 89
2019-12-19 17:00 | 77 | 75 |  |  | 43818.7083 | 92 | 92
2019-12-19 17:30 | 79 | 77 |  |  | 43818.7292 | 95 | 95
2019-12-19 18:00 | 80 | 78 |  |  | 43818.75 | 96 | 95
2019-12-19 18:30 | 80 | 79 |  |  | 43818.7708 | 96 | 95
2019-12-19 19:00 | 84 | 83 |  |  | 43818.7917 | 100 | 100
2019-12-19 19:30 | 84 | 83 |  |  | 43818.8125 | 100 | 99
2019-12-19 20:00 | 82 | 81 |  |  | 43818.8333 | 97 | 97
2019-12-19 20:30 | 81 | 80 |  |  | 43818.8542 | 97 | 96
2019-12-19 21:00 | 80 | 79 |  |  | 43818.875 | 96 | 95
2019-12-19 21:30 | 72 | 71 |  |  | 43818.8958 | 89 | 88
2019-12-19 22:00 | 68 | 68 |  |  | 43818.9167 | 87 | 86
2019-12-19 22:30 | 65 | 64 |  |  | 43818.9375 | 84 | 83
2019-12-19 23:00 | 63 | 62 |  |  | 43818.9583 | 80 | 79
2019-12-19 23:30 | 58 | 58 |  |  | 43818.9792 | 76 | 75
2019-12-20 | 53 | 52 |  |  | 43819 | 71 | 70
2019-12-20 00:30 | 51 | 49 |  |  | 43819.0208 | 66 | 65
2019-12-20 01:00 | 51 | 48 |  |  | 43819.0417 | 62 | 62
2019-12-20 01:30 | 48 | 45 |  |  | 43819.0625 | 60 | 60
2019-12-20 02:00 | 47 | 44 |  |  | 43819.0833 | 58 | 58
2019-12-20 02:30 | 45 | 42 |  |  | 43819.1042 | 55 | 55
2019-12-20 03:00 | 45 | 42 |  |  | 43819.125 | 56 | 56
2019-12-20 03:30 | 45 | 43 |  |  | 43819.1458 | 57 | 57
2019-12-20 04:00 | 45 | 42 |  |  | 43819.1667 | 57 | 57
2019-12-20 04:30 | 45 | 42 |  |  | 43819.1875 | 57 | 57
2019-12-20 05:00 | 45 | 42 |  |  | 43819.2083 | 58 | 58
2019-12-20 05:30 | 45 | 43 |  |  | 43819.2292 | 59 | 59
2019-12-20 06:00 | 49 | 46 |  |  | 43819.25 | 64 | 63
2019-12-20 06:30 | 51 | 48 |  |  | 43819.2708 | 68 | 68
2019-12-20 07:00 | 49 | 45 |  |  | 43819.2917 | 69 | 69
2019-12-20 07:30 | 51 | 47 |  |  | 43819.3125 | 72 | 72
2019-12-20 08:00 | 55 | 49 |  |  | 43819.3333 | 76 | 75
2019-12-20 08:30 | 54 | 48 |  |  | 43819.3542 | 77 | 76
2019-12-20 09:00 | 55 | 47 |  |  | 43819.375 | 77 | 76
2019-12-20 09:30 | 53 | 47 |  |  | 43819.3958 | 75 | 75
2019-12-20 10:00 | 55 | 49 |  |  | 43819.4167 | 78 | 77
2019-12-20 10:30 | 55 | 50 |  |  | 43819.4375 | 77 | 77
2019-12-20 11:00 | 57 | 52 |  |  | 43819.4583 | 78 | 78
2019-12-20 11:30 | 57 | 52 |  |  | 43819.4792 | 76 | 76
2019-12-20 12:00 | 54 | 49 |  |  | 43819.5 | 74 | 74
2019-12-20 12:30 | 54 | 50 |  |  | 43819.5208 | 73 | 73
2019-12-20 13:00 | 56 | 52 |  |  | 43819.5417 | 75 | 75
2019-12-20 13:30 | 61 | 58 |  |  | 43819.5625 | 79 | 79
2019-12-20 14:00 | 65 | 61 |  |  | 43819.5833 | 82 | 82
2019-12-20 14:30 | 78 | 64 |  |  | 43819.6042 | 85 | 85
2019-12-20 15:00 | 76 | 61 |  |  | 43819.625 | 83 | 83
2019-12-20 15:30 | 77 | 62 |  |  | 43819.6458 | 85 | 84
2019-12-20 16:00 | 81 | 66 |  |  | 43819.6667 | 88 | 87
2019-12-20 16:30 | 82 | 69 |  |  | 43819.6875 | 90 | 90
2019-12-20 17:00 | 83 | 72 |  |  | 43819.7083 | 92 | 92
2019-12-20 17:30 | 82 | 75 |  |  | 43819.7292 | 94 | 94
2019-12-20 18:00 | 83 | 77 |  |  | 43819.75 | 97 | 97
2019-12-20 18:30 | 80 | 76 |  |  | 43819.7708 | 95 | 95
2019-12-20 19:00 | 81 | 77 |  |  | 43819.7917 | 97 | 97
2019-12-20 19:30 | 82 | 78 |  |  | 43819.8125 | 98 | 98
2019-12-20 20:00 | 80 | 76 |  |  | 43819.8333 | 95 | 95
2019-12-20 20:30 | 76 | 74 |  |  | 43819.8542 | 94 | 93
2019-12-20 21:00 | 72 | 72 |  |  | 43819.875 | 91 | 90
2019-12-20 21:30 | 65 | 64 |  |  | 43819.8958 | 84 | 83
2019-12-20 22:00 | 62 | 61 |  |  | 43819.9167 | 83 | 82
2019-12-20 22:30 | 61 | 60 |  |  | 43819.9375 | 81 | 80
2019-12-20 23:00 | 58 | 57 |  |  | 43819.9583 | 77 | 75
2019-12-20 23:30 | 55 | 54 |  |  | 43819.9792 | 73 | 72
2019-12-21 | 50 | 50 |  |  | 43820 | 69 | 68
2019-12-21 00:30 | 46 | 46 |  |  | 43820.0208 | 64 | 62
2019-12-21 01:00 | 44 | 44 |  |  | 43820.0417 | 61 | 59
2019-12-21 01:30 | 41 | 41 |  |  | 43820.0625 | 57 | 55
2019-12-21 02:00 | 40 | 40 |  |  | 43820.0833 | 56 | 53
2019-12-21 02:30 | 40 | 40 |  |  | 43820.1042 | 57 | 53
2019-12-21 03:00 | 40 | 40 |  |  | 43820.125 | 56 | 53
2019-12-21 03:30 | 40 | 40 |  |  | 43820.1458 | 56 | 53
2019-12-21 04:00 | 40 | 40 |  |  | 43820.1667 | 56 | 53
2019-12-21 04:30 | 40 | 40 |  |  | 43820.1875 | 56 | 53
2019-12-21 05:00 | 41 | 41 |  |  | 43820.2083 | 57 | 53
2019-12-21 05:30 | 42 | 42 |  |  | 43820.2292 | 58 | 55
2019-12-21 06:00 | 40 | 40 |  |  | 43820.25 | 57 | 54
2019-12-21 06:30 | 37 | 37 |  |  | 43820.2708 | 54 | 52
2019-12-21 07:00 | 35 | 35 |  |  | 43820.2917 | 52 | 50
2019-12-21 07:30 | 35 | 35 |  |  | 43820.3125 | 53 | 50
2019-12-21 08:00 | 35 | 34 |  |  | 43820.3333 | 53 | 51
2019-12-21 08:30 | 37 | 36 |  |  | 43820.3542 | 56 | 53
2019-12-21 09:00 | 36 | 36 |  |  | 43820.375 | 56 | 53
2019-12-21 09:30 | 37 | 37 |  |  | 43820.3958 | 55 | 53
2019-12-21 10:00 | 39 | 38 |  |  | 43820.4167 | 55 | 53
2019-12-21 10:30 | 39 | 39 |  |  | 43820.4375 | 54 | 52
2019-12-21 11:00 | 37 | 37 |  |  | 43820.4583 | 52 | 51
2019-12-21 11:30 | 37 | 37 |  |  | 43820.4792 | 53 | 51
2019-12-21 12:00 | 39 | 39 |  |  | 43820.5 | 54 | 52
2019-12-21 12:30 | 40 | 40 |  |  | 43820.5208 | 54 | 54
2019-12-21 13:00 | 43 | 42 |  |  | 43820.5417 | 55 | 55
2019-12-21 13:30 | 45 | 44 |  |  | 43820.5625 | 55 | 55
2019-12-21 14:00 | 46 | 44 |  |  | 43820.5833 | 55 | 55
2019-12-21 14:30 | 46 | 44 |  |  | 43820.6042 | 53 | 53
2019-12-21 15:00 | 45 | 44 |  |  | 43820.625 | 54 | 54
2019-12-21 15:30 | 47 | 47 |  |  | 43820.6458 | 57 | 56
2019-12-21 16:00 | 50 | 50 |  |  | 43820.6667 | 61 | 61
2019-12-21 16:30 | 53 | 52 |  |  | 43820.6875 | 65 | 64
2019-12-21 17:00 | 58 | 57 |  |  | 43820.7083 | 71 | 71
2019-12-21 17:30 | 62 | 62 |  |  | 43820.7292 | 76 | 76
2019-12-21 18:00 | 65 | 65 |  |  | 43820.75 | 81 | 81
2019-12-21 18:30 | 68 | 68 |  |  | 43820.7708 | 84 | 84
2019-12-21 19:00 | 70 | 70 |  |  | 43820.7917 | 88 | 88
2019-12-21 19:30 | 72 | 71 |  |  | 43820.8125 | 90 | 89
2019-12-21 20:00 | 72 | 72 |  |  | 43820.8333 | 90 | 89
2019-12-21 20:30 | 70 | 70 |  |  | 43820.8542 | 88 | 88
2019-12-21 21:00 | 65 | 65 |  |  | 43820.875 | 83 | 83
2019-12-21 21:30 | 66 | 66 |  |  | 43820.8958 | 84 | 84
2019-12-21 22:00 | 66 | 65 |  |  | 43820.9167 | 85 | 84
2019-12-21 22:30 | 67 | 67 |  |  | 43820.9375 | 85 | 85
2019-12-21 23:00 | 66 | 66 |  |  | 43820.9583 | 83 | 83
2019-12-21 23:30 | 63 | 63 |  |  | 43820.9792 | 81 | 81
2019-12-22 | 63 | 57 |  |  | 43821 | 74 | 73
2019-12-22 00:30 | 63 | 53 |  |  | 43821.0208 | 69 | 67
2019-12-22 01:00 | 62 | 51 |  |  | 43821.0417 | 66 | 64
2019-12-22 01:30 | 61 | 49 |  |  | 43821.0625 | 64 | 62
2019-12-22 02:00 | 60 | 47 |  |  | 43821.0833 | 62 | 60
2019-12-22 02:30 | 59 | 46 |  |  | 43821.1042 | 61 | 58
2019-12-22 03:00 | 57 | 45 |  |  | 43821.125 | 60 | 58
2019-12-22 03:30 | 56 | 43 |  |  | 43821.1458 | 58 | 56
2019-12-22 04:00 | 55 | 42 |  |  | 43821.1667 | 57 | 55
2019-12-22 04:30 | 55 | 43 |  |  | 43821.1875 | 57 | 55
2019-12-22 05:00 | 56 | 43 |  |  | 43821.2083 | 58 | 56
2019-12-22 05:30 | 55 | 42 |  |  | 43821.2292 | 57 | 55
2019-12-22 06:00 | 55 | 41 |  |  | 43821.25 | 56 | 54
2019-12-22 06:30 | 51 | 36 |  |  | 43821.2708 | 53 | 50
2019-12-22 07:00 | 46 | 32 |  |  | 43821.2917 | 48 | 46
2019-12-22 07:30 | 42 | 29 |  |  | 43821.3125 | 45 | 44
2019-12-22 08:00 | 42 | 30 |  |  | 43821.3333 | 45 | 44
2019-12-22 08:30 | 41 | 31 |  |  | 43821.3542 | 46 | 46
2019-12-22 09:00 | 42 | 32 |  |  | 43821.375 | 44 | 44
2019-12-22 09:30 | 42 | 32 |  |  | 43821.3958 | 45 | 45
2019-12-22 10:00 | 44 | 35 |  |  | 43821.4167 | 49 | 48
2019-12-22 10:30 | 46 | 38 |  |  | 43821.4375 | 50 | 50
2019-12-22 11:00 | 48 | 41 |  |  | 43821.4583 | 52 | 52
2019-12-22 11:30 | 48 | 41 |  |  | 43821.4792 | 55 | 55
2019-12-22 12:00 | 49 | 43 |  |  | 43821.5 | 57 | 57
2019-12-22 12:30 | 53 | 48 |  |  | 43821.5208 | 59 | 59
2019-12-22 13:00 | 56 | 50 |  |  | 43821.5417 | 59 | 59
2019-12-22 13:30 | 64 | 54 |  |  | 43821.5625 | 62 | 62
2019-12-22 14:00 | 65 | 56 |  |  | 43821.5833 | 63 | 63
2019-12-22 14:30 | 64 | 54 |  |  | 43821.6042 | 63 | 63
2019-12-22 15:00 | 62 | 53 |  |  | 43821.625 | 63 | 63
2019-12-22 15:30 | 62 | 55 |  |  | 43821.6458 | 65 | 65
2019-12-22 16:00 | 59 | 58 |  |  | 43821.6667 | 70 | 70
2019-12-22 16:30 | 62 | 61 |  |  | 43821.6875 | 74 | 74
2019-12-22 17:00 | 68 | 67 |  |  | 43821.7083 | 80 | 80
2019-12-22 17:30 | 75 | 73 |  |  | 43821.7292 | 87 | 87
2019-12-22 18:00 | 77 | 75 |  |  | 43821.75 | 90 | 90
2019-12-22 18:30 | 80 | 78 |  |  | 43821.7708 | 93 | 93
2019-12-22 19:00 | 82 | 80 |  |  | 43821.7917 | 95 | 95
2019-12-22 19:30 | 81 | 79 |  |  | 43821.8125 | 95 | 95
2019-12-22 20:00 | 82 | 80 |  |  | 43821.8333 | 96 | 96
2019-12-22 20:30 | 80 | 78 |  |  | 43821.8542 | 95 | 94
2019-12-22 21:00 | 78 | 76 |  |  | 43821.875 | 92 | 92
2019-12-22 21:30 | 75 | 73 |  |  | 43821.8958 | 91 | 91
2019-12-22 22:00 | 73 | 70 |  |  | 43821.9167 | 88 | 87
2019-12-22 22:30 | 71 | 69 |  |  | 43821.9375 | 87 | 86
2019-12-22 23:00 | 68 | 65 |  |  | 43821.9583 | 83 | 82
2019-12-22 23:30 | 63 | 60 |  |  | 43821.9792 | 77 | 77
2019-12-23 | 59 | 55 |  |  | 43822 | 72 | 72
2019-12-23 00:30 | 56 | 53 |  |  | 43822.0208 | 68 | 67
2019-12-23 01:00 | 52 | 51 |  |  | 43822.0417 | 67 | 64
2019-12-23 01:30 | 51 | 50 |  |  | 43822.0625 | 66 | 63
2019-12-23 02:00 | 49 | 47 |  |  | 43822.0833 | 64 | 61
2019-12-23 02:30 | 48 | 47 |  |  | 43822.1042 | 63 | 59
2019-12-23 03:00 | 48 | 47 |  |  | 43822.125 | 63 | 59
2019-12-23 03:30 | 48 | 46 |  |  | 43822.1458 | 61 | 57
2019-12-23 04:00 | 46 | 45 |  |  | 43822.1667 | 62 | 58
2019-12-23 04:30 | 46 | 45 |  |  | 43822.1875 | 62 | 58
2019-12-23 05:00 | 48 | 46 |  |  | 43822.2083 | 63 | 59
2019-12-23 05:30 | 49 | 47 |  |  | 43822.2292 | 65 | 61
2019-12-23 06:00 | 51 | 50 |  |  | 43822.25 | 68 | 65
2019-12-23 06:30 | 54 | 53 |  |  | 43822.2708 | 73 | 71
2019-12-23 07:00 | 54 | 54 |  |  | 43822.2917 | 75 | 75
2019-12-23 07:30 | 57 | 57 |  |  | 43822.3125 | 80 | 79
2019-12-23 08:00 | 58 | 58 |  |  | 43822.3333 | 82 | 82
2019-12-23 08:30 | 59 | 59 |  |  | 43822.3542 | 82 | 82
2019-12-23 09:00 | 59 | 59 |  |  | 43822.375 | 80 | 80
2019-12-23 09:30 | 60 | 60 |  |  | 43822.3958 | 80 | 80
2019-12-23 10:00 | 61 | 61 |  |  | 43822.4167 | 81 | 81
2019-12-23 10:30 | 59 | 59 |  |  | 43822.4375 | 82 | 81
2019-12-23 11:00 | 56 | 56 |  |  | 43822.4583 | 81 | 80
2019-12-23 11:30 | 57 | 57 |  |  | 43822.4792 | 79 | 78
2019-12-23 12:00 | 58 | 58 |  |  | 43822.5 | 82 | 81
2019-12-23 12:30 | 55 | 54 |  |  | 43822.5208 | 80 | 79
2019-12-23 13:00 | 57 | 57 |  |  | 43822.5417 | 80 | 78
2019-12-23 13:30 | 59 | 58 |  |  | 43822.5625 | 80 | 78
2019-12-23 14:00 | 62 | 62 |  |  | 43822.5833 | 80 | 78
2019-12-23 14:30 | 62 | 61 |  |  | 43822.6042 | 80 | 77
2019-12-23 15:00 | 65 | 64 |  |  | 43822.625 | 81 | 79
2019-12-23 15:30 | 68 | 68 |  |  | 43822.6458 | 85 | 83
2019-12-23 16:00 | 69 | 69 |  |  | 43822.6667 | 86 | 85
2019-12-23 16:30 | 70 | 70 |  |  | 43822.6875 | 87 | 86
2019-12-23 17:00 | 71 | 71 |  |  | 43822.7083 | 91 | 89
2019-12-23 17:30 | 73 | 72 |  |  | 43822.7292 | 93 | 91
2019-12-23 18:00 | 76 | 76 |  |  | 43822.75 | 96 | 93
2019-12-23 18:30 | 79 | 78 |  |  | 43822.7708 | 98 | 94
2019-12-23 19:00 | 81 | 81 |  |  | 43822.7917 | 102 | 97
2019-12-23 19:30 | 81 | 80 |  |  | 43822.8125 | 100 | 96
2019-12-23 20:00 | 79 | 78 |  |  | 43822.8333 | 99 | 94
2019-12-23 20:30 | 78 | 77 |  |  | 43822.8542 | 97 | 92
2019-12-23 21:00 | 75 | 74 |  |  | 43822.875 | 95 | 91
2019-12-23 21:30 | 74 | 74 |  |  | 43822.8958 | 93 | 89
2019-12-23 22:00 | 72 | 71 |  |  | 43822.9167 | 91 | 87
2019-12-23 22:30 | 72 | 72 |  |  | 43822.9375 | 91 | 87
2019-12-23 23:00 | 70 | 69 |  |  | 43822.9583 | 88 | 83
2019-12-23 23:30 | 63 | 62 |  |  | 43822.9792 | 82 | 76
2019-12-24 | 58 | 57 |  |  | 43823 | 77 | 71
2019-12-24 00:30 | 54 | 52 |  |  | 43823.0208 | 71 | 64
2019-12-24 01:00 | 50 | 48 |  |  | 43823.0417 | 66 | 59
2019-12-24 01:30 | 46 | 44 |  |  | 43823.0625 | 62 | 53
2019-12-24 02:00 | 46 | 43 |  |  | 43823.0833 | 63 | 53
2019-12-24 02:30 | 47 | 44 |  |  | 43823.1042 | 64 | 54
2019-12-24 03:00 | 47 | 44 |  |  | 43823.125 | 64 | 54
2019-12-24 03:30 | 45 | 42 |  |  | 43823.1458 | 63 | 52
2019-12-24 04:00 | 45 | 42 |  |  | 43823.1667 | 63 | 52
2019-12-24 04:30 | 44 | 41 |  |  | 43823.1875 | 62 | 52
2019-12-24 05:00 | 47 | 44 |  |  | 43823.2083 | 65 | 55
2019-12-24 05:30 | 49 | 46 |  |  | 43823.2292 | 68 | 59
2019-12-24 06:00 | 49 | 47 |  |  | 43823.25 | 70 | 61
2019-12-24 06:30 | 50 | 49 |  |  | 43823.2708 | 72 | 67
2019-12-24 07:00 | 51 | 50 |  |  | 43823.2917 | 72 | 69
2019-12-24 07:30 | 54 | 54 |  |  | 43823.3125 | 76 | 73
2019-12-24 08:00 | 56 | 55 |  |  | 43823.3333 | 80 | 78
2019-12-24 08:30 | 57 | 56 |  |  | 43823.3542 | 81 | 80
2019-12-24 09:00 | 58 | 58 |  |  | 43823.375 | 83 | 82
2019-12-24 09:30 | 58 | 58 |  |  | 43823.3958 | 77 | 76
2019-12-24 10:00 | 62 | 62 |  |  | 43823.4167 | 82 | 81
2019-12-24 10:30 | 64 | 64 |  |  | 43823.4375 | 82 | 81
2019-12-24 11:00 | 69 | 69 |  |  | 43823.4583 | 87 | 86
2019-12-24 11:30 | 64 | 64 |  |  | 43823.4792 | 83 | 82
2019-12-24 12:00 | 56 | 56 |  |  | 43823.5 | 76 | 75
2019-12-24 12:30 | 57 | 57 |  |  | 43823.5208 | 75 | 74
2019-12-24 13:00 | 58 | 58 |  |  | 43823.5417 | 73 | 72
2019-12-24 13:30 | 60 | 60 |  |  | 43823.5625 | 77 | 76
2019-12-24 14:00 | 56 | 56 |  |  | 43823.5833 | 77 | 76
2019-12-24 14:30 | 60 | 60 |  |  | 43823.6042 | 74 | 74
2019-12-24 15:00 | 61 | 61 |  |  | 43823.625 | 80 | 79
2019-12-24 15:30 | 54 | 54 |  |  | 43823.6458 | 74 | 73
2019-12-24 16:00 | 58 | 58 |  |  | 43823.6667 | 77 | 76
2019-12-24 16:30 | 65 | 64 |  |  | 43823.6875 | 84 | 82
2019-12-24 17:00 | 65 | 65 |  |  | 43823.7083 | 85 | 84
2019-12-24 17:30 | 69 | 69 |  |  | 43823.7292 | 87 | 85
2019-12-24 18:00 | 69 | 68 |  |  | 43823.75 | 87 | 85
2019-12-24 18:30 | 63 | 63 |  |  | 43823.7708 | 86 | 78
2019-12-24 19:00 | 64 | 64 |  |  | 43823.7917 | 88 | 78
2019-12-24 19:30 | 63 | 63 |  |  | 43823.8125 | 87 | 78
2019-12-24 20:00 | 62 | 62 |  |  | 43823.8333 | 85 | 76
2019-12-24 20:30 | 62 | 62 |  |  | 43823.8542 | 84 | 75
2019-12-24 21:00 | 59 | 59 |  |  | 43823.875 | 81 | 71
2019-12-24 21:30 | 56 | 56 |  |  | 43823.8958 | 78 | 68
2019-12-24 22:00 | 54 | 54 |  |  | 43823.9167 | 78 | 67
2019-12-24 22:30 | 54 | 54 |  |  | 43823.9375 | 78 | 67
2019-12-24 23:00 | 52 | 52 |  |  | 43823.9583 | 77 | 65
2019-12-24 23:30 | 49 | 49 |  |  | 43823.9792 | 76 | 62
2019-12-25 | 45 | 45 |  |  | 43824 | 69 | 57
2019-12-25 00:30 | 43 | 43 |  |  | 43824.0208 | 65 | 55
2019-12-25 01:00 | 39 | 39 |  |  | 43824.0417 | 61 | 50
2019-12-25 01:30 | 36 | 36 |  |  | 43824.0625 | 59 | 47
2019-12-25 02:00 | 36 | 36 |  |  | 43824.0833 | 58 | 46
2019-12-25 02:30 | 36 | 36 |  |  | 43824.1042 | 58 | 46
2019-12-25 03:00 | 39 | 39 |  |  | 43824.125 | 59 | 47
2019-12-25 03:30 | 39 | 39 |  |  | 43824.1458 | 59 | 47
2019-12-25 04:00 | 38 | 37 |  |  | 43824.1667 | 59 | 47
2019-12-25 04:30 | 37 | 37 |  |  | 43824.1875 | 58 | 46
2019-12-25 05:00 | 35 | 35 |  |  | 43824.2083 | 56 | 44
2019-12-25 05:30 | 34 | 34 |  |  | 43824.2292 | 57 | 44
2019-12-25 06:00 | 33 | 33 |  |  | 43824.25 | 58 | 45
2019-12-25 06:30 | 33 | 33 |  |  | 43824.2708 | 59 | 47
2019-12-25 07:00 | 32 | 32 |  |  | 43824.2917 | 57 | 46
2019-12-25 07:30 | 33 | 33 |  |  | 43824.3125 | 59 | 50
2019-12-25 08:00 | 30 | 30 |  |  | 43824.3333 | 56 | 47
2019-12-25 08:30 | 29 | 29 |  |  | 43824.3542 | 53 | 44
2019-12-25 09:00 | 29 | 29 |  |  | 43824.375 | 52 | 44
2019-12-25 09:30 | 31 | 30 |  |  | 43824.3958 | 54 | 47
2019-12-25 10:00 | 36 | 35 |  |  | 43824.4167 | 54 | 47
2019-12-25 10:30 | 31 | 30 |  |  | 43824.4375 | 54 | 48
2019-12-25 11:00 | 39 | 39 |  |  | 43824.4583 | 58 | 52
2019-12-25 11:30 | 39 | 38 |  |  | 43824.4792 | 59 | 54
2019-12-25 12:00 | 32 | 32 |  |  | 43824.5 | 55 | 49
2019-12-25 12:30 | 31 | 31 |  |  | 43824.5208 | 49 | 41
2019-12-25 13:00 | 27 | 26 |  |  | 43824.5417 | 45 | 36
2019-12-25 13:30 | 29 | 29 |  |  | 43824.5625 | 47 | 39
2019-12-25 14:00 | 30 | 29 |  |  | 43824.5833 | 49 | 41
2019-12-25 14:30 | 24 | 24 |  |  | 43824.6042 | 46 | 37
2019-12-25 15:00 | 23 | 22 |  |  | 43824.625 | 44 | 35
2019-12-25 15:30 | 26 | 25 |  |  | 43824.6458 | 48 | 40
2019-12-25 16:00 | 34 | 34 |  |  | 43824.6667 | 54 | 47
2019-12-25 16:30 | 35 | 35 |  |  | 43824.6875 | 56 | 49
2019-12-25 17:00 | 38 | 38 |  |  | 43824.7083 | 58 | 51
2019-12-25 17:30 | 41 | 40 |  |  | 43824.7292 | 59 | 53
2019-12-25 18:00 | 46 | 45 |  |  | 43824.75 | 65 | 58
2019-12-25 18:30 | 49 | 49 |  |  | 43824.7708 | 69 | 62
2019-12-25 19:00 | 52 | 52 |  |  | 43824.7917 | 73 | 66
2019-12-25 19:30 | 51 | 51 |  |  | 43824.8125 | 72 | 64
2019-12-25 20:00 | 52 | 52 |  |  | 43824.8333 | 72 | 64
2019-12-25 20:30 | 51 | 51 |  |  | 43824.8542 | 70 | 63
2019-12-25 21:00 | 49 | 49 |  |  | 43824.875 | 68 | 60
2019-12-25 21:30 | 45 | 45 |  |  | 43824.8958 | 65 | 57
2019-12-25 22:00 | 45 | 45 |  |  | 43824.9167 | 65 | 56
2019-12-25 22:30 | 47 | 47 |  |  | 43824.9375 | 67 | 60
2019-12-25 23:00 | 46 | 46 |  |  | 43824.9583 | 65 | 57
2019-12-25 23:30 | 43 | 43 |  |  | 43824.9792 | 64 | 54
2019-12-26 | 39 | 39 |  |  | 43825 | 59 | 49
2019-12-26 00:30 | 36 | 36 |  |  | 43825.0208 | 56 | 44
2019-12-26 01:00 | 35 | 35 |  |  | 43825.0417 | 55 | 42
2019-12-26 01:30 | 34 | 34 |  |  | 43825.0625 | 55 | 41
2019-12-26 02:00 | 35 | 34 |  |  | 43825.0833 | 59 | 39
2019-12-26 02:30 | 36 | 34 |  |  | 43825.1042 | 61 | 39
2019-12-26 03:00 | 36 | 34 |  |  | 43825.125 | 62 | 40
2019-12-26 03:30 | 36 | 34 |  |  | 43825.1458 | 62 | 40
2019-12-26 04:00 | 36 | 33 |  |  | 43825.1667 | 61 | 39
2019-12-26 04:30 | 35 | 32 |  |  | 43825.1875 | 61 | 39
2019-12-26 05:00 | 33 | 30 |  |  | 43825.2083 | 59 | 37
2019-12-26 05:30 | 34 | 29 |  |  | 43825.2292 | 53 | 37
2019-12-26 06:00 | 33 | 28 |  |  | 43825.25 | 53 | 37
2019-12-26 06:30 | 32 | 26 |  |  | 43825.2708 | 51 | 36
2019-12-26 07:00 | 30 | 22 |  |  | 43825.2917 | 48 | 35
2019-12-26 07:30 | 32 | 25 |  |  | 43825.3125 | 49 | 37
2019-12-26 08:00 | 34 | 26 |  |  | 43825.3333 | 49 | 39
2019-12-26 08:30 | 37 | 30 |  |  | 43825.3542 | 52 | 43
2019-12-26 09:00 | 43 | 36 |  |  | 43825.375 | 56 | 49
2019-12-26 09:30 | 46 | 40 |  |  | 43825.3958 | 57 | 51
2019-12-26 10:00 | 48 | 42 |  |  | 43825.4167 | 58 | 51
2019-12-26 10:30 | 49 | 42 |  |  | 43825.4375 | 59 | 53
2019-12-26 11:00 | 38 | 31 |  |  | 43825.4583 | 53 | 46
2019-12-26 11:30 | 39 | 30 |  |  | 43825.4792 | 46 | 37
2019-12-26 12:00 | 35 | 26 |  |  | 43825.5 | 47 | 39
2019-12-26 12:30 | 37 | 29 |  |  | 43825.5208 | 43 | 34
2019-12-26 13:00 | 35 | 25 |  |  | 43825.5417 | 37 | 27
2019-12-26 13:30 | 34 | 23 |  |  | 43825.5625 | 42 | 33
2019-12-26 14:00 | 39 | 30 |  |  | 43825.5833 | 44 | 37
2019-12-26 14:30 | 39 | 31 |  |  | 43825.6042 | 47 | 39
2019-12-26 15:00 | 40 | 31 |  |  | 43825.625 | 46 | 38
2019-12-26 15:30 | 43 | 35 |  |  | 43825.6458 | 49 | 43
2019-12-26 16:00 | 45 | 38 |  |  | 43825.6667 | 55 | 48
2019-12-26 16:30 | 47 | 41 |  |  | 43825.6875 | 58 | 51
2019-12-26 17:00 | 49 | 45 |  |  | 43825.7083 | 65 | 56
2019-12-26 17:30 | 51 | 48 |  |  | 43825.7292 | 71 | 59
2019-12-26 18:00 | 53 | 51 |  |  | 43825.75 | 75 | 63
2019-12-26 18:30 | 52 | 50 |  |  | 43825.7708 | 75 | 62
2019-12-26 19:00 | 53 | 51 |  |  | 43825.7917 | 77 | 64
2019-12-26 19:30 | 54 | 52 |  |  | 43825.8125 | 77 | 65
2019-12-26 20:00 | 54 | 52 |  |  | 43825.8333 | 78 | 65
2019-12-26 20:30 | 54 | 52 |  |  | 43825.8542 | 76 | 64
2019-12-26 21:00 | 50 | 48 |  |  | 43825.875 | 73 | 59
2019-12-26 21:30 | 47 | 45 |  |  | 43825.8958 | 71 | 57
2019-12-26 22:00 | 47 | 44 |  |  | 43825.9167 | 72 | 57
2019-12-26 22:30 | 50 | 48 |  |  | 43825.9375 | 74 | 61
2019-12-26 23:00 | 52 | 50 |  |  | 43825.9583 | 76 | 62
2019-12-26 23:30 | 48 | 46 |  |  | 43825.9792 | 73 | 58
2019-12-27 | 43 | 41 |  |  | 43826 | 69 | 52
2019-12-27 00:30 | 42 | 40 |  |  | 43826.0208 | 69 | 51
2019-12-27 01:00 | 41 | 39 |  |  | 43826.0417 | 67 | 48
2019-12-27 01:30 | 39 | 37 |  |  | 43826.0625 | 65 | 45
2019-12-27 02:00 | 38 | 36 |  |  | 43826.0833 | 64 | 44
2019-12-27 02:30 | 37 | 34 |  |  | 43826.1042 | 63 | 42
2019-12-27 03:00 | 37 | 35 |  |  | 43826.125 | 63 | 42
2019-12-27 03:30 | 36 | 34 |  |  | 43826.1458 | 63 | 41
2019-12-27 04:00 | 35 | 33 |  |  | 43826.1667 | 61 | 40
2019-12-27 04:30 | 36 | 34 |  |  | 43826.1875 | 62 | 41
2019-12-27 05:00 | 36 | 33 |  |  | 43826.2083 | 62 | 41
2019-12-27 05:30 | 35 | 33 |  |  | 43826.2292 | 63 | 41
2019-12-27 06:00 | 35 | 32 |  |  | 43826.25 | 64 | 42
2019-12-27 06:30 | 34 | 31 |  |  | 43826.2708 | 62 | 43
2019-12-27 07:00 | 39 | 30 |  |  | 43826.2917 | 54 | 45
2019-12-27 07:30 | 37 | 27 |  |  | 43826.3125 | 49 | 43
2019-12-27 08:00 | 34 | 26 |  |  | 43826.3333 | 42 | 38
2019-12-27 08:30 | 35 | 28 |  |  | 43826.3542 | 45 | 42
2019-12-27 09:00 | 41 | 36 |  |  | 43826.375 | 53 | 51
2019-12-27 09:30 | 42 | 36 |  |  | 43826.3958 | 49 | 47
2019-12-27 10:00 | 43 | 38 |  |  | 43826.4167 | 51 | 49
2019-12-27 10:30 | 46 | 41 |  |  | 43826.4375 | 50 | 48
2019-12-27 11:00 | 43 | 37 |  |  | 43826.4583 | 51 | 48
2019-12-27 11:30 | 42 | 37 |  |  | 43826.4792 | 44 | 41
2019-12-27 12:00 | 41 | 34 |  |  | 43826.5 | 58 | 55
2019-12-27 12:30 | 43 | 37 |  |  | 43826.5208 | 59 | 57
2019-12-27 13:00 | 44 | 38 |  |  | 43826.5417 | 59 | 56
2019-12-27 13:30 | 45 | 39 |  |  | 43826.5625 | 56 | 53
2019-12-27 14:00 | 44 | 39 |  |  | 43826.5833 | 50 | 46
2019-12-27 14:30 | 44 | 39 |  |  | 43826.6042 | 52 | 49
2019-12-27 15:00 | 44 | 38 |  |  | 43826.625 | 54 | 51
2019-12-27 15:30 | 45 | 40 |  |  | 43826.6458 | 58 | 55
2019-12-27 16:00 | 47 | 42 |  |  | 43826.6667 | 60 | 58
2019-12-27 16:30 | 50 | 45 |  |  | 43826.6875 | 63 | 61
2019-12-27 17:00 | 57 | 51 |  |  | 43826.7083 | 68 | 67
2019-12-27 17:30 | 64 | 52 |  |  | 43826.7292 | 68 | 67
2019-12-27 18:00 | 64 | 53 |  |  | 43826.75 | 67 | 66
2019-12-27 18:30 | 66 | 52 |  |  | 43826.7708 | 67 | 65
2019-12-27 19:00 | 67 | 53 |  |  | 43826.7917 | 69 | 67
2019-12-27 19:30 | 67 | 54 |  |  | 43826.8125 | 69 | 67
2019-12-27 20:00 | 65 | 53 |  |  | 43826.8333 | 68 | 66
2019-12-27 20:30 | 66 | 54 |  |  | 43826.8542 | 70 | 68
2019-12-27 21:00 | 67 | 54 |  |  | 43826.875 | 70 | 68
2019-12-27 21:30 | 67 | 54 |  |  | 43826.8958 | 70 | 68
2019-12-27 22:00 | 66 | 52 |  |  | 43826.9167 | 69 | 67
2019-12-27 22:30 | 67 | 53 |  |  | 43826.9375 | 70 | 68
2019-12-27 23:00 | 69 | 55 |  |  | 43826.9583 | 71 | 69
2019-12-27 23:30 | 67 | 51 |  |  | 43826.9792 | 68 | 66
2019-12-28 | 62 | 45 |  |  | 43827 | 61 | 58
2019-12-28 00:30 | 60 | 42 |  |  | 43827.0208 | 58 | 54
2019-12-28 01:00 | 60 | 42 |  |  | 43827.0417 | 58 | 54
2019-12-28 01:30 | 59 | 40 |  |  | 43827.0625 | 55 | 51
2019-12-28 02:00 | 58 | 39 |  |  | 43827.0833 | 53 | 49
2019-12-28 02:30 | 58 | 39 |  |  | 43827.1042 | 53 | 49
2019-12-28 03:00 | 57 | 37 |  |  | 43827.125 | 51 | 48
2019-12-28 03:30 | 57 | 37 |  |  | 43827.1458 | 51 | 48
2019-12-28 04:00 | 56 | 36 |  |  | 43827.1667 | 51 | 47
2019-12-28 04:30 | 54 | 34 |  |  | 43827.1875 | 48 | 45
2019-12-28 05:00 | 49 | 34 |  |  | 43827.2083 | 46 | 45
2019-12-28 05:30 | 50 | 35 |  |  | 43827.2292 | 47 | 47
2019-12-28 06:00 | 52 | 36 |  |  | 43827.25 | 50 | 49
2019-12-28 06:30 | 50 | 34 |  |  | 43827.2708 | 48 | 47
2019-12-28 07:00 | 46 | 31 |  |  | 43827.2917 | 45 | 45
2019-12-28 07:30 | 45 | 31 |  |  | 43827.3125 | 46 | 46
2019-12-28 08:00 | 45 | 32 |  |  | 43827.3333 | 48 | 48
2019-12-28 08:30 | 47 | 36 |  |  | 43827.3542 | 49 | 49
2019-12-28 09:00 | 43 | 30 |  |  | 43827.375 | 48 | 48
2019-12-28 09:30 | 47 | 36 |  |  | 43827.3958 | 53 | 53
2019-12-28 10:00 | 46 | 35 |  |  | 43827.4167 | 47 | 47
2019-12-28 10:30 | 43 | 32 |  |  | 43827.4375 | 42 | 42
2019-12-28 11:00 | 39 | 28 |  |  | 43827.4583 | 39 | 39
2019-12-28 11:30 | 37 | 24 |  |  | 43827.4792 | 38 | 38
2019-12-28 12:00 | 39 | 27 |  |  | 43827.5 | 41 | 41
2019-12-28 12:30 | 39 | 27 |  |  | 43827.5208 | 42 | 42
2019-12-28 13:00 | 41 | 30 |  |  | 43827.5417 | 43 | 43
2019-12-28 13:30 | 43 | 32 |  |  | 43827.5625 | 47 | 47
2019-12-28 14:00 | 47 | 35 |  |  | 43827.5833 | 50 | 50
2019-12-28 14:30 | 46 | 35 |  |  | 43827.6042 | 48 | 48
2019-12-28 15:00 | 45 | 33 |  |  | 43827.625 | 48 | 47
2019-12-28 15:30 | 47 | 36 |  |  | 43827.6458 | 50 | 50
2019-12-28 16:00 | 49 | 40 |  |  | 43827.6667 | 53 | 53
2019-12-28 16:30 | 50 | 42 |  |  | 43827.6875 | 56 | 56
2019-12-28 17:00 | 54 | 46 |  |  | 43827.7083 | 59 | 59
2019-12-28 17:30 | 55 | 47 |  |  | 43827.7292 | 61 | 61
2019-12-28 18:00 | 56 | 48 |  |  | 43827.75 | 62 | 62
2019-12-28 18:30 | 59 | 50 |  |  | 43827.7708 | 65 | 64
2019-12-28 19:00 | 62 | 53 |  |  | 43827.7917 | 68 | 68
2019-12-28 19:30 | 63 | 56 |  |  | 43827.8125 | 70 | 70
2019-12-28 20:00 | 64 | 56 |  |  | 43827.8333 | 71 | 71
2019-12-28 20:30 | 67 | 60 |  |  | 43827.8542 | 75 | 75
2019-12-28 21:00 | 67 | 59 |  |  | 43827.875 | 74 | 73
2019-12-28 21:30 | 68 | 59 |  |  | 43827.8958 | 73 | 73
2019-12-28 22:00 | 66 | 57 |  |  | 43827.9167 | 72 | 71
2019-12-28 22:30 | 66 | 56 |  |  | 43827.9375 | 72 | 72
2019-12-28 23:00 | 67 | 56 |  |  | 43827.9583 | 71 | 71
2019-12-28 23:30 | 65 | 54 |  |  | 43827.9792 | 69 | 68
2019-12-29 | 61 | 49 |  |  | 43828 | 65 | 64
2019-12-29 00:30 | 59 | 46 |  |  | 43828.0208 | 59 | 58
2019-12-29 01:00 | 56 | 43 |  |  | 43828.0417 | 56 | 55
2019-12-29 01:30 | 55 | 41 |  |  | 43828.0625 | 54 | 54
2019-12-29 02:00 | 55 | 40 |  |  | 43828.0833 | 53 | 52
2019-12-29 02:30 | 54 | 39 |  |  | 43828.1042 | 52 | 51
2019-12-29 03:00 | 53 | 37 |  |  | 43828.125 | 50 | 49
2019-12-29 03:30 | 53 | 37 |  |  | 43828.1458 | 50 | 49
2019-12-29 04:00 | 53 | 38 |  |  | 43828.1667 | 52 | 51
2019-12-29 04:30 | 52 | 38 |  |  | 43828.1875 | 52 | 52
2019-12-29 05:00 | 51 | 36 |  |  | 43828.2083 | 49 | 49
2019-12-29 05:30 | 51 | 35 |  |  | 43828.2292 | 49 | 49
2019-12-29 06:00 | 51 | 34 |  |  | 43828.25 | 49 | 48
2019-12-29 06:30 | 49 | 31 |  |  | 43828.2708 | 47 | 47
2019-12-29 07:00 | 47 | 29 |  |  | 43828.2917 | 46 | 45
2019-12-29 07:30 | 45 | 28 |  |  | 43828.3125 | 44 | 43
2019-12-29 08:00 | 43 | 25 |  |  | 43828.3333 | 40 | 40
2019-12-29 08:30 | 44 | 25 |  |  | 43828.3542 | 44 | 43
2019-12-29 09:00 | 46 | 25 |  |  | 43828.375 | 42 | 41
2019-12-29 09:30 | 46 | 27 |  |  | 43828.3958 | 41 | 40
2019-12-29 10:00 | 44 | 25 |  |  | 43828.4167 | 43 | 42
2019-12-29 10:30 | 42 | 23 |  |  | 43828.4375 | 41 | 40
2019-12-29 11:00 | 41 | 20 |  |  | 43828.4583 | 37 | 36
2019-12-29 11:30 | 40 | 22 |  |  | 43828.4792 | 37 | 37
2019-12-29 12:00 | 39 | 20 |  |  | 43828.5 | 35 | 34
2019-12-29 12:30 | 39 | 20 |  |  | 43828.5208 | 34 | 33
2019-12-29 13:00 | 40 | 23 |  |  | 43828.5417 | 36 | 35
2019-12-29 13:30 | 44 | 28 |  |  | 43828.5625 | 40 | 40
2019-12-29 14:00 | 45 | 31 |  |  | 43828.5833 | 43 | 43
2019-12-29 14:30 | 46 | 32 |  |  | 43828.6042 | 44 | 43
2019-12-29 15:00 | 45 | 30 |  |  | 43828.625 | 41 | 40
2019-12-29 15:30 | 45 | 32 |  |  | 43828.6458 | 43 | 42
2019-12-29 16:00 | 49 | 37 |  |  | 43828.6667 | 48 | 47
2019-12-29 16:30 | 53 | 40 |  |  | 43828.6875 | 53 | 51
2019-12-29 17:00 | 58 | 45 |  |  | 43828.7083 | 59 | 56
2019-12-29 17:30 | 58 | 45 |  |  | 43828.7292 | 58 | 54
2019-12-29 18:00 | 61 | 46 |  |  | 43828.75 | 60 | 56
2019-12-29 18:30 | 61 | 46 |  |  | 43828.7708 | 62 | 57
2019-12-29 19:00 | 65 | 51 |  |  | 43828.7917 | 67 | 63
2019-12-29 19:30 | 65 | 51 |  |  | 43828.8125 | 68 | 64
2019-12-29 20:00 | 64 | 52 |  |  | 43828.8333 | 68 | 66
2019-12-29 20:30 | 65 | 54 |  |  | 43828.8542 | 69 | 68
2019-12-29 21:00 | 62 | 50 |  |  | 43828.875 | 66 | 64
2019-12-29 21:30 | 61 | 48 |  |  | 43828.8958 | 65 | 63
2019-12-29 22:00 | 62 | 48 |  |  | 43828.9167 | 66 | 64
2019-12-29 22:30 | 61 | 47 |  |  | 43828.9375 | 65 | 63
2019-12-29 23:00 | 61 | 46 |  |  | 43828.9583 | 63 | 61
2019-12-29 23:30 | 58 | 43 |  |  | 43828.9792 | 60 | 57
2019-12-30 | 56 | 39 |  |  | 43829 | 55 | 52
2019-12-30 00:30 | 54 | 35 |  |  | 43829.0208 | 51 | 48
2019-12-30 01:00 | 54 | 33 |  |  | 43829.0417 | 49 | 45
2019-12-30 01:30 | 54 | 33 |  |  | 43829.0625 | 48 | 44
2019-12-30 02:00 | 54 | 34 |  |  | 43829.0833 | 51 | 46
2019-12-30 02:30 | 54 | 34 |  |  | 43829.1042 | 51 | 46
2019-12-30 03:00 | 55 | 34 |  |  | 43829.125 | 51 | 47
2019-12-30 03:30 | 55 | 35 |  |  | 43829.1458 | 51 | 46
2019-12-30 04:00 | 55 | 35 |  |  | 43829.1667 | 51 | 47
2019-12-30 04:30 | 55 | 35 |  |  | 43829.1875 | 52 | 48
2019-12-30 05:00 | 55 | 35 |  |  | 43829.2083 | 52 | 48
2019-12-30 05:30 | 56 | 36 |  |  | 43829.2292 | 53 | 49
2019-12-30 06:00 | 56 | 37 |  |  | 43829.25 | 56 | 52
2019-12-30 06:30 | 54 | 36 |  |  | 43829.2708 | 57 | 54
2019-12-30 07:00 | 52 | 34 |  |  | 43829.2917 | 54 | 51
2019-12-30 07:30 | 50 | 35 |  |  | 43829.3125 | 56 | 55
2019-12-30 08:00 | 47 | 32 |  |  | 43829.3333 | 59 | 58
2019-12-30 08:30 | 52 | 37 |  |  | 43829.3542 | 59 | 57
2019-12-30 09:00 | 54 | 39 |  |  | 43829.375 | 62 | 59
2019-12-30 09:30 | 55 | 41 |  |  | 43829.3958 | 65 | 62
2019-12-30 10:00 | 55 | 41 |  |  | 43829.4167 | 65 | 63
2019-12-30 10:30 | 55 | 40 |  |  | 43829.4375 | 60 | 59
2019-12-30 11:00 | 52 | 37 |  |  | 43829.4583 | 57 | 56
2019-12-30 11:30 | 50 | 35 |  |  | 43829.4792 | 53 | 51
2019-12-30 12:00 | 51 | 37 |  |  | 43829.5 | 54 | 52
2019-12-30 12:30 | 51 | 37 |  |  | 43829.5208 | 54 | 53
2019-12-30 13:00 | 48 | 35 |  |  | 43829.5417 | 49 | 49
2019-12-30 13:30 | 48 | 38 |  |  | 43829.5625 | 51 | 51
2019-12-30 14:00 | 48 | 39 |  |  | 43829.5833 | 54 | 54
2019-12-30 14:30 | 49 | 38 |  |  | 43829.6042 | 53 | 53
2019-12-30 15:00 | 50 | 38 |  |  | 43829.625 | 53 | 53
2019-12-30 15:30 | 57 | 46 |  |  | 43829.6458 | 61 | 61
2019-12-30 16:00 | 62 | 52 |  |  | 43829.6667 | 67 | 67
2019-12-30 16:30 | 63 | 54 |  |  | 43829.6875 | 69 | 68
2019-12-30 17:00 | 63 | 54 |  |  | 43829.7083 | 68 | 68
2019-12-30 17:30 | 68 | 59 |  |  | 43829.7292 | 72 | 72
2019-12-30 18:00 | 67 | 58 |  |  | 43829.75 | 70 | 69
2019-12-30 18:30 | 70 | 60 |  |  | 43829.7708 | 72 | 72
2019-12-30 19:00 | 78 | 68 |  |  | 43829.7917 | 83 | 83
2019-12-30 19:30 | 77 | 67 |  |  | 43829.8125 | 82 | 82
2019-12-30 20:00 | 78 | 68 |  |  | 43829.8333 | 82 | 82
2019-12-30 20:30 | 75 | 64 |  |  | 43829.8542 | 79 | 79
2019-12-30 21:00 | 71 | 61 |  |  | 43829.875 | 75 | 75
2019-12-30 21:30 | 70 | 59 |  |  | 43829.8958 | 72 | 72
2019-12-30 22:00 | 69 | 59 |  |  | 43829.9167 | 74 | 74
2019-12-30 22:30 | 67 | 57 |  |  | 43829.9375 | 72 | 72
2019-12-30 23:00 | 67 | 55 |  |  | 43829.9583 | 69 | 69
2019-12-30 23:30 | 64 | 51 |  |  | 43829.9792 | 67 | 67
2019-12-31 | 63 | 50 |  |  | 43830 | 65 | 65
2019-12-31 00:30 | 63 | 49 |  |  | 43830.0208 | 63 | 63
2019-12-31 01:00 | 62 | 47 |  |  | 43830.0417 | 62 | 61
2019-12-31 01:30 | 61 | 45 |  |  | 43830.0625 | 59 | 59
2019-12-31 02:00 | 61 | 45 |  |  | 43830.0833 | 58 | 58
2019-12-31 02:30 | 60 | 44 |  |  | 43830.1042 | 58 | 57
2019-12-31 03:00 | 60 | 43 |  |  | 43830.125 | 56 | 55
2019-12-31 03:30 | 59 | 42 |  |  | 43830.1458 | 55 | 55
2019-12-31 04:00 | 57 | 41 |  |  | 43830.1667 | 55 | 55
2019-12-31 04:30 | 56 | 39 |  |  | 43830.1875 | 53 | 53
2019-12-31 05:00 | 56 | 39 |  |  | 43830.2083 | 53 | 52
2019-12-31 05:30 | 56 | 38 |  |  | 43830.2292 | 53 | 53
2019-12-31 06:00 | 56 | 39 |  |  | 43830.25 | 56 | 55
2019-12-31 06:30 | 55 | 40 |  |  | 43830.2708 | 58 | 58
2019-12-31 07:00 | 54 | 38 |  |  | 43830.2917 | 60 | 59
2019-12-31 07:30 | 52 | 39 |  |  | 43830.3125 | 58 | 58
2019-12-31 08:00 | 52 | 39 |  |  | 43830.3333 | 62 | 62
2019-12-31 08:30 | 52 | 41 |  |  | 43830.3542 | 61 | 61
2019-12-31 09:00 | 52 | 41 |  |  | 43830.375 | 60 | 60
2019-12-31 09:30 | 51 | 41 |  |  | 43830.3958 | 61 | 61
2019-12-31 10:00 | 52 | 42 |  |  | 43830.4167 | 64 | 64
2019-12-31 10:30 | 54 | 44 |  |  | 43830.4375 | 66 | 66
2019-12-31 11:00 | 58 | 48 |  |  | 43830.4583 | 63 | 63
2019-12-31 11:30 | 60 | 49 |  |  | 43830.4792 | 62 | 62
2019-12-31 12:00 | 57 | 45 |  |  | 43830.5 | 64 | 64
2019-12-31 12:30 | 57 | 45 |  |  | 43830.5208 | 60 | 59
2019-12-31 13:00 | 59 | 48 |  |  | 43830.5417 | 63 | 63
2019-12-31 13:30 | 61 | 49 |  |  | 43830.5625 | 67 | 67
2019-12-31 14:00 | 64 | 53 |  |  | 43830.5833 | 67 | 67
2019-12-31 14:30 | 62 | 52 |  |  | 43830.6042 | 64 | 64
2019-12-31 15:00 | 60 | 48 |  |  | 43830.625 | 61 | 61
2019-12-31 15:30 | 57 | 45 |  |  | 43830.6458 | 61 | 61
2019-12-31 16:00 | 58 | 46 |  |  | 43830.6667 | 61 | 61
2019-12-31 16:30 | 61 | 49 |  |  | 43830.6875 | 64 | 64
2019-12-31 17:00 | 64 | 53 |  |  | 43830.7083 | 69 | 69
2019-12-31 17:30 | 67 | 55 |  |  | 43830.7292 | 70 | 70
2019-12-31 18:00 | 70 | 57 |  |  | 43830.75 | 72 | 72
2019-12-31 18:30 | 71 | 58 |  |  | 43830.7708 | 73 | 73
2019-12-31 19:00 | 73 | 61 |  |  | 43830.7917 | 76 | 76
2019-12-31 19:30 | 74 | 61 |  |  | 43830.8125 | 77 | 77
2019-12-31 20:00 | 73 | 60 |  |  | 43830.8333 | 76 | 76
2019-12-31 20:30 | 72 | 60 |  |  | 43830.8542 | 76 | 76
2019-12-31 21:00 | 69 | 56 |  |  | 43830.875 | 73 | 72
2019-12-31 21:30 | 68 | 54 |  |  | 43830.8958 | 70 | 69
2019-12-31 22:00 | 69 | 55 |  |  | 43830.9167 | 72 | 71
2019-12-31 22:30 | 68 | 53 |  |  | 43830.9375 | 71 | 70
2019-12-31 23:00 | 68 | 53 |  |  | 43830.9583 | 70 | 69
2019-12-31 23:30 | 66 | 50 |  |  | 43830.9792 | 68 | 67
2020-01-01 | 65 | 49 |  |  | 43831 | 66 | 65
2020-01-01 00:30 | 64 | 48 |  |  | 43831.0208 | 64 | 63
2020-01-01 01:00 | 63 | 47 |  |  | 43831.0417 | 63 | 62
2020-01-01 01:30 | 63 | 47 |  |  | 43831.0625 | 62 | 61
2020-01-01 02:00 | 62 | 45 |  |  | 43831.0833 | 59 | 59
2020-01-01 02:30 | 61 | 44 |  |  | 43831.1042 | 58 | 57
2020-01-01 03:00 | 62 | 45 |  |  | 43831.125 | 59 | 58
2020-01-01 03:30 | 62 | 44 |  |  | 43831.1458 | 59 | 58
2020-01-01 04:00 | 62 | 44 |  |  | 43831.1667 | 58 | 57
2020-01-01 04:30 | 60 | 41 |  |  | 43831.1875 | 55 | 54
2020-01-01 05:00 | 58 | 39 |  |  | 43831.2083 | 53 | 52
2020-01-01 05:30 | 57 | 38 |  |  | 43831.2292 | 53 | 52
2020-01-01 06:00 | 57 | 38 |  |  | 43831.25 | 52 | 51
2020-01-01 06:30 | 54 | 35 |  |  | 43831.2708 | 51 | 50
2020-01-01 07:00 | 51 | 30 |  |  | 43831.2917 | 47 | 47
2020-01-01 07:30 | 47 | 26 |  |  | 43831.3125 | 43 | 42
2020-01-01 08:00 | 45 | 25 |  |  | 43831.3333 | 42 | 42
2020-01-01 08:30 | 45 | 28 |  |  | 43831.3542 | 43 | 43
2020-01-01 09:00 | 47 | 30 |  |  | 43831.375 | 46 | 46
2020-01-01 09:30 | 46 | 29 |  |  | 43831.3958 | 45 | 45
2020-01-01 10:00 | 48 | 31 |  |  | 43831.4167 | 48 | 48
2020-01-01 10:30 | 48 | 31 |  |  | 43831.4375 | 45 | 45
2020-01-01 11:00 | 48 | 31 |  |  | 43831.4583 | 44 | 44
2020-01-01 11:30 | 50 | 32 |  |  | 43831.4792 | 45 | 45
2020-01-01 12:00 | 52 | 34 |  |  | 43831.5 | 47 | 46
2020-01-01 12:30 | 51 | 34 |  |  | 43831.5208 | 46 | 46
2020-01-01 13:00 | 53 | 37 |  |  | 43831.5417 | 49 | 49
2020-01-01 13:30 | 54 | 39 |  |  | 43831.5625 | 51 | 51
2020-01-01 14:00 | 55 | 42 |  |  | 43831.5833 | 53 | 53
2020-01-01 14:30 | 57 | 45 |  |  | 43831.6042 | 56 | 56
2020-01-01 15:00 | 60 | 46 |  |  | 43831.625 | 57 | 57
2020-01-01 15:30 | 62 | 49 |  |  | 43831.6458 | 60 | 60
2020-01-01 16:00 | 66 | 53 |  |  | 43831.6667 | 63 | 63
2020-01-01 16:30 | 68 | 55 |  |  | 43831.6875 | 66 | 65
2020-01-01 17:00 | 70 | 58 |  |  | 43831.7083 | 69 | 69
2020-01-01 17:30 | 72 | 60 |  |  | 43831.7292 | 72 | 71
2020-01-01 18:00 | 74 | 62 |  |  | 43831.75 | 74 | 73
2020-01-01 18:30 | 77 | 64 |  |  | 43831.7708 | 77 | 76
2020-01-01 19:00 | 79 | 65 |  |  | 43831.7917 | 81 | 80
2020-01-01 19:30 | 78 | 66 |  |  | 43831.8125 | 82 | 81
2020-01-01 20:00 | 80 | 67 |  |  | 43831.8333 | 82 | 81
2020-01-01 20:30 | 79 | 66 |  |  | 43831.8542 | 81 | 80
2020-01-01 21:00 | 77 | 64 |  |  | 43831.875 | 79 | 78
2020-01-01 21:30 | 74 | 61 |  |  | 43831.8958 | 75 | 74
2020-01-01 22:00 | 73 | 59 |  |  | 43831.9167 | 74 | 73
2020-01-01 22:30 | 72 | 58 |  |  | 43831.9375 | 73 | 72
2020-01-01 23:00 | 70 | 55 |  |  | 43831.9583 | 69 | 68
2020-01-01 23:30 | 69 | 54 |  |  | 43831.9792 | 67 | 66
2020-01-02 | 66 | 49 |  |  | 43832 | 64 | 62
2020-01-02 00:30 | 66 | 47 |  |  | 43832.0208 | 62 | 60
2020-01-02 01:00 | 65 | 45 |  |  | 43832.0417 | 60 | 57
2020-01-02 01:30 | 63 | 42 |  |  | 43832.0625 | 58 | 54
2020-01-02 02:00 | 65 | 44 |  |  | 43832.0833 | 58 | 55
2020-01-02 02:30 | 65 | 43 |  |  | 43832.1042 | 58 | 55
2020-01-02 03:00 | 64 | 43 |  |  | 43832.125 | 57 | 54
2020-01-02 03:30 | 64 | 42 |  |  | 43832.1458 | 57 | 54
2020-01-02 04:00 | 64 | 42 |  |  | 43832.1667 | 57 | 54
2020-01-02 04:30 | 63 | 41 |  |  | 43832.1875 | 58 | 55
2020-01-02 05:00 | 62 | 40 |  |  | 43832.2083 | 57 | 54
2020-01-02 05:30 | 63 | 41 |  |  | 43832.2292 | 59 | 55
2020-01-02 06:00 | 64 | 43 |  |  | 43832.25 | 62 | 59
2020-01-02 06:30 | 62 | 42 |  |  | 43832.2708 | 62 | 61
2020-01-02 07:00 | 56 | 41 |  |  | 43832.2917 | 63 | 63
2020-01-02 07:30 | 54 | 43 |  |  | 43832.3125 | 67 | 67
2020-01-02 08:00 | 56 | 46 |  |  | 43832.3333 | 69 | 69
2020-01-02 08:30 | 61 | 48 |  |  | 43832.3542 | 72 | 72
2020-01-02 09:00 | 59 | 48 |  |  | 43832.375 | 72 | 72
2020-01-02 09:30 | 60 | 48 |  |  | 43832.3958 | 71 | 71
2020-01-02 10:00 | 61 | 48 |  |  | 43832.4167 | 72 | 72
2020-01-02 10:30 | 60 | 48 |  |  | 43832.4375 | 70 | 70
2020-01-02 11:00 | 62 | 49 |  |  | 43832.4583 | 70 | 69
2020-01-02 11:30 | 63 | 49 |  |  | 43832.4792 | 69 | 68
2020-01-02 12:00 | 63 | 49 |  |  | 43832.5 | 69 | 68
2020-01-02 12:30 | 64 | 50 |  |  | 43832.5208 | 70 | 69
2020-01-02 13:00 | 65 | 51 |  |  | 43832.5417 | 70 | 69
2020-01-02 13:30 | 65 | 52 |  |  | 43832.5625 | 71 | 70
2020-01-02 14:00 | 68 | 56 |  |  | 43832.5833 | 73 | 72
2020-01-02 14:30 | 70 | 59 |  |  | 43832.6042 | 76 | 75
2020-01-02 15:00 | 74 | 59 |  |  | 43832.625 | 78 | 75
2020-01-02 15:30 | 77 | 62 |  |  | 43832.6458 | 82 | 78
2020-01-02 16:00 | 80 | 67 |  |  | 43832.6667 | 87 | 82
2020-01-02 16:30 | 84 | 71 |  |  | 43832.6875 | 90 | 86
2020-01-02 17:00 | 86 | 76 |  |  | 43832.7083 | 93 | 90
2020-01-02 17:30 | 88 | 80 |  |  | 43832.7292 | 96 | 92
2020-01-02 18:00 | 89 | 82 |  |  | 43832.75 | 95 | 94
2020-01-02 18:30 | 88 | 80 |  |  | 43832.7708 | 95 | 93
2020-01-02 19:00 | 90 | 81 |  |  | 43832.7917 | 97 | 95
2020-01-02 19:30 | 92 | 84 |  |  | 43832.8125 | 99 | 97
2020-01-02 20:00 | 91 | 83 |  |  | 43832.8333 | 98 | 96
2020-01-02 20:30 | 89 | 81 |  |  | 43832.8542 | 97 | 94
2020-01-02 21:00 | 87 | 79 |  |  | 43832.875 | 93 | 91
2020-01-02 21:30 | 81 | 75 |  |  | 43832.8958 | 87 | 87
2020-01-02 22:00 | 77 | 73 |  |  | 43832.9167 | 85 | 85
2020-01-02 22:30 | 74 | 68 |  |  | 43832.9375 | 81 | 81
2020-01-02 23:00 | 71 | 65 |  |  | 43832.9583 | 76 | 76
2020-01-02 23:30 | 66 | 59 |  |  | 43832.9792 | 70 | 70
2020-01-03 | 64 | 53 |  |  | 43833 | 66 | 65
2020-01-03 00:30 | 65 | 50 |  |  | 43833.0208 | 62 | 61
2020-01-03 01:00 | 66 | 50 |  |  | 43833.0417 | 61 | 60
2020-01-03 01:30 | 67 | 50 |  |  | 43833.0625 | 62 | 60
2020-01-03 02:00 | 67 | 50 |  |  | 43833.0833 | 62 | 60
2020-01-03 02:30 | 66 | 48 |  |  | 43833.1042 | 61 | 59
2020-01-03 03:00 | 66 | 49 |  |  | 43833.125 | 61 | 59
2020-01-03 03:30 | 66 | 48 |  |  | 43833.1458 | 60 | 58
2020-01-03 04:00 | 66 | 47 |  |  | 43833.1667 | 60 | 58
2020-01-03 04:30 | 67 | 48 |  |  | 43833.1875 | 61 | 59
2020-01-03 05:00 | 67 | 49 |  |  | 43833.2083 | 62 | 60
2020-01-03 05:30 | 66 | 48 |  |  | 43833.2292 | 62 | 60
2020-01-03 06:00 | 66 | 48 |  |  | 43833.25 | 62 | 61
2020-01-03 06:30 | 65 | 49 |  |  | 43833.2708 | 65 | 64
2020-01-03 07:00 | 63 | 49 |  |  | 43833.2917 | 67 | 66
2020-01-03 07:30 | 61 | 49 |  |  | 43833.3125 | 69 | 69
2020-01-03 08:00 | 63 | 52 |  |  | 43833.3333 | 73 | 73
2020-01-03 08:30 | 64 | 54 |  |  | 43833.3542 | 73 | 73
2020-01-03 09:00 | 67 | 57 |  |  | 43833.375 | 76 | 76
2020-01-03 09:30 | 66 | 56 |  |  | 43833.3958 | 76 | 76
2020-01-03 10:00 | 66 | 57 |  |  | 43833.4167 | 77 | 77
2020-01-03 10:30 | 66 | 58 |  |  | 43833.4375 | 76 | 76
2020-01-03 11:00 | 64 | 57 |  |  | 43833.4583 | 74 | 74
2020-01-03 11:30 | 61 | 53 |  |  | 43833.4792 | 70 | 70
2020-01-03 12:00 | 60 | 53 |  |  | 43833.5 | 69 | 68
2020-01-03 12:30 | 61 | 54 |  |  | 43833.5208 | 68 | 68
2020-01-03 13:00 | 61 | 54 |  |  | 43833.5417 | 67 | 67
2020-01-03 13:30 | 66 | 56 |  |  | 43833.5625 | 69 | 68
2020-01-03 14:00 | 67 | 56 |  |  | 43833.5833 | 68 | 67
2020-01-03 14:30 | 67 | 58 |  |  | 43833.6042 | 70 | 70
2020-01-03 15:00 | 69 | 62 |  |  | 43833.625 | 74 | 74
2020-01-03 15:30 | 73 | 66 |  |  | 43833.6458 | 79 | 79
2020-01-03 16:00 | 77 | 69 |  |  | 43833.6667 | 83 | 83
2020-01-03 16:30 | 81 | 69 |  |  | 43833.6875 | 83 | 81
2020-01-03 17:00 | 80 | 73 |  |  | 43833.7083 | 87 | 85
2020-01-03 17:30 | 82 | 75 |  |  | 43833.7292 | 89 | 88
2020-01-03 18:00 | 79 | 74 |  |  | 43833.75 | 87 | 87
2020-01-03 18:30 | 79 | 73 |  |  | 43833.7708 | 86 | 86
2020-01-03 19:00 | 80 | 75 |  |  | 43833.7917 | 88 | 88
2020-01-03 19:30 | 81 | 76 |  |  | 43833.8125 | 90 | 90
2020-01-03 20:00 | 81 | 75 |  |  | 43833.8333 | 90 | 90
2020-01-03 20:30 | 81 | 75 |  |  | 43833.8542 | 89 | 89
2020-01-03 21:00 | 79 | 72 |  |  | 43833.875 | 87 | 86
2020-01-03 21:30 | 78 | 72 |  |  | 43833.8958 | 86 | 86
2020-01-03 22:00 | 76 | 70 |  |  | 43833.9167 | 84 | 84
2020-01-03 22:30 | 74 | 68 |  |  | 43833.9375 | 82 | 82
2020-01-03 23:00 | 75 | 64 |  |  | 43833.9583 | 77 | 77
2020-01-03 23:30 | 71 | 60 |  |  | 43833.9792 | 73 | 73
2020-01-04 | 65 | 55 |  |  | 43834 | 67 | 67
2020-01-04 00:30 | 64 | 53 |  |  | 43834.0208 | 65 | 65
2020-01-04 01:00 | 64 | 52 |  |  | 43834.0417 | 64 | 64
2020-01-04 01:30 | 63 | 49 |  |  | 43834.0625 | 60 | 60
2020-01-04 02:00 | 62 | 48 |  |  | 43834.0833 | 59 | 59
2020-01-04 02:30 | 62 | 48 |  |  | 43834.1042 | 60 | 60
2020-01-04 03:00 | 63 | 48 |  |  | 43834.125 | 60 | 60
2020-01-04 03:30 | 62 | 48 |  |  | 43834.1458 | 59 | 59
2020-01-04 04:00 | 62 | 47 |  |  | 43834.1667 | 59 | 59
2020-01-04 04:30 | 62 | 47 |  |  | 43834.1875 | 58 | 58
2020-01-04 05:00 | 62 | 46 |  |  | 43834.2083 | 57 | 57
2020-01-04 05:30 | 59 | 44 |  |  | 43834.2292 | 56 | 56
2020-01-04 06:00 | 59 | 44 |  |  | 43834.25 | 56 | 56
2020-01-04 06:30 | 57 | 42 |  |  | 43834.2708 | 54 | 54
2020-01-04 07:00 | 54 | 40 |  |  | 43834.2917 | 52 | 52
2020-01-04 07:30 | 51 | 37 |  |  | 43834.3125 | 50 | 49
2020-01-04 08:00 | 49 | 37 |  |  | 43834.3333 | 50 | 50
2020-01-04 08:30 | 49 | 38 |  |  | 43834.3542 | 53 | 52
2020-01-04 09:00 | 52 | 41 |  |  | 43834.375 | 56 | 55
2020-01-04 09:30 | 51 | 41 |  |  | 43834.3958 | 56 | 55
2020-01-04 10:00 | 50 | 40 |  |  | 43834.4167 | 53 | 53
2020-01-04 10:30 | 50 | 38 |  |  | 43834.4375 | 52 | 51
2020-01-04 11:00 | 49 | 38 |  |  | 43834.4583 | 50 | 50
2020-01-04 11:30 | 48 | 37 |  |  | 43834.4792 | 49 | 48
2020-01-04 12:00 | 49 | 39 |  |  | 43834.5 | 48 | 48
2020-01-04 12:30 | 56 | 42 |  |  | 43834.5208 | 52 | 51
2020-01-04 13:00 | 67 | 44 |  |  | 43834.5417 | 58 | 52
2020-01-04 13:30 | 69 | 46 |  |  | 43834.5625 | 60 | 54
2020-01-04 14:00 | 69 | 47 |  |  | 43834.5833 | 61 | 55
2020-01-04 14:30 | 69 | 47 |  |  | 43834.6042 | 61 | 55
2020-01-04 15:00 | 68 | 46 |  |  | 43834.625 | 60 | 54
2020-01-04 15:30 | 69 | 46 |  |  | 43834.6458 | 59 | 53
2020-01-04 16:00 | 72 | 46 |  |  | 43834.6667 | 60 | 55
2020-01-04 16:30 | 77 | 53 |  |  | 43834.6875 | 65 | 62
2020-01-04 17:00 | 78 | 57 |  |  | 43834.7083 | 71 | 67
2020-01-04 17:30 | 81 | 58 |  |  | 43834.7292 | 75 | 71
2020-01-04 18:00 | 83 | 59 |  |  | 43834.75 | 77 | 74
2020-01-04 18:30 | 85 | 65 |  |  | 43834.7708 | 83 | 79
2020-01-04 19:00 | 86 | 67 |  |  | 43834.7917 | 87 | 83
2020-01-04 19:30 | 84 | 66 |  |  | 43834.8125 | 88 | 84
2020-01-04 20:00 | 86 | 67 |  |  | 43834.8333 | 90 | 86
2020-01-04 20:30 | 86 | 68 |  |  | 43834.8542 | 89 | 85
2020-01-04 21:00 | 84 | 66 |  |  | 43834.875 | 87 | 82
2020-01-04 21:30 | 75 | 66 |  |  | 43834.8958 | 82 | 81
2020-01-04 22:00 | 69 | 66 |  |  | 43834.9167 | 80 | 80
2020-01-04 22:30 | 68 | 64 |  |  | 43834.9375 | 79 | 79
2020-01-04 23:00 | 66 | 63 |  |  | 43834.9583 | 75 | 75
2020-01-04 23:30 | 61 | 57 |  |  | 43834.9792 | 70 | 70
2020-01-05 | 58 | 53 |  |  | 43835 | 66 | 66
2020-01-05 00:30 | 57 | 50 |  |  | 43835.0208 | 64 | 63
2020-01-05 01:00 | 55 | 48 |  |  | 43835.0417 | 61 | 60
2020-01-05 01:30 | 56 | 48 |  |  | 43835.0625 | 61 | 60
2020-01-05 02:00 | 54 | 46 |  |  | 43835.0833 | 59 | 58
2020-01-05 02:30 | 51 | 42 |  |  | 43835.1042 | 56 | 55
2020-01-05 03:00 | 50 | 41 |  |  | 43835.125 | 55 | 54
2020-01-05 03:30 | 51 | 42 |  |  | 43835.1458 | 56 | 54
2020-01-05 04:00 | 51 | 43 |  |  | 43835.1667 | 56 | 54
2020-01-05 04:30 | 50 | 41 |  |  | 43835.1875 | 54 | 53
2020-01-05 05:00 | 49 | 40 |  |  | 43835.2083 | 54 | 53
2020-01-05 05:30 | 49 | 39 |  |  | 43835.2292 | 54 | 52
2020-01-05 06:00 | 50 | 39 |  |  | 43835.25 | 55 | 53
2020-01-05 06:30 | 46 | 35 |  |  | 43835.2708 | 51 | 49
2020-01-05 07:00 | 42 | 31 |  |  | 43835.2917 | 47 | 46
2020-01-05 07:30 | 39 | 29 |  |  | 43835.3125 | 44 | 44
2020-01-05 08:00 | 36 | 27 |  |  | 43835.3333 | 42 | 42
2020-01-05 08:30 | 36 | 29 |  |  | 43835.3542 | 44 | 44
2020-01-05 09:00 | 35 | 29 |  |  | 43835.375 | 44 | 44
2020-01-05 09:30 | 36 | 30 |  |  | 43835.3958 | 45 | 45
2020-01-05 10:00 | 35 | 30 |  |  | 43835.4167 | 45 | 45
2020-01-05 10:30 | 38 | 33 |  |  | 43835.4375 | 47 | 47
2020-01-05 11:00 | 40 | 36 |  |  | 43835.4583 | 50 | 49
2020-01-05 11:30 | 38 | 34 |  |  | 43835.4792 | 47 | 46
2020-01-05 12:00 | 40 | 37 |  |  | 43835.5 | 49 | 49
2020-01-05 12:30 | 42 | 39 |  |  | 43835.5208 | 51 | 51
2020-01-05 13:00 | 44 | 41 |  |  | 43835.5417 | 52 | 52
2020-01-05 13:30 | 49 | 45 |  |  | 43835.5625 | 55 | 55
2020-01-05 14:00 | 55 | 51 |  |  | 43835.5833 | 60 | 59
2020-01-05 14:30 | 60 | 56 |  |  | 43835.6042 | 64 | 63
2020-01-05 15:00 | 59 | 55 |  |  | 43835.625 | 63 | 62
2020-01-05 15:30 | 60 | 56 |  |  | 43835.6458 | 65 | 64
2020-01-05 16:00 | 67 | 63 |  |  | 43835.6667 | 73 | 71
2020-01-05 16:30 | 71 | 66 |  |  | 43835.6875 | 78 | 75
2020-01-05 17:00 | 74 | 68 |  |  | 43835.7083 | 81 | 78
2020-01-05 17:30 | 77 | 71 |  |  | 43835.7292 | 84 | 81
2020-01-05 18:00 | 79 | 72 |  |  | 43835.75 | 87 | 84
2020-01-05 18:30 | 80 | 73 |  |  | 43835.7708 | 89 | 86
2020-01-05 19:00 | 82 | 76 |  |  | 43835.7917 | 93 | 91
2020-01-05 19:30 | 85 | 78 |  |  | 43835.8125 | 96 | 94
2020-01-05 20:00 | 86 | 79 |  |  | 43835.8333 | 96 | 93
2020-01-05 20:30 | 86 | 79 |  |  | 43835.8542 | 97 | 94
2020-01-05 21:00 | 86 | 78 |  |  | 43835.875 | 96 | 92
2020-01-05 21:30 | 85 | 77 |  |  | 43835.8958 | 95 | 91
2020-01-05 22:00 | 81 | 73 |  |  | 43835.9167 | 93 | 89
2020-01-05 22:30 | 83 | 74 |  |  | 43835.9375 | 94 | 91
2020-01-05 23:00 | 82 | 73 |  |  | 43835.9583 | 91 | 87
2020-01-05 23:30 | 76 | 67 |  |  | 43835.9792 | 85 | 81
2020-01-06 | 71 | 60 |  |  | 43836 | 79 | 74
2020-01-06 00:30 | 68 | 57 |  |  | 43836.0208 | 75 | 70
2020-01-06 01:00 | 66 | 55 |  |  | 43836.0417 | 71 | 67
2020-01-06 01:30 | 63 | 52 |  |  | 43836.0625 | 68 | 64
2020-01-06 02:00 | 60 | 50 |  |  | 43836.0833 | 67 | 63
2020-01-06 02:30 | 59 | 48 |  |  | 43836.1042 | 65 | 61
2020-01-06 03:00 | 58 | 47 |  |  | 43836.125 | 64 | 60
2020-01-06 03:30 | 58 | 48 |  |  | 43836.1458 | 64 | 60
2020-01-06 04:00 | 58 | 47 |  |  | 43836.1667 | 63 | 59
2020-01-06 04:30 | 60 | 49 |  |  | 43836.1875 | 65 | 61
2020-01-06 05:00 | 61 | 51 |  |  | 43836.2083 | 67 | 63
2020-01-06 05:30 | 62 | 53 |  |  | 43836.2292 | 69 | 66
2020-01-06 06:00 | 64 | 56 |  |  | 43836.25 | 73 | 70
2020-01-06 06:30 | 65 | 58 |  |  | 43836.2708 | 77 | 75
2020-01-06 07:00 | 65 | 61 |  |  | 43836.2917 | 81 | 81
2020-01-06 07:30 | 68 | 65 |  |  | 43836.3125 | 86 | 86
2020-01-06 08:00 | 67 | 64 |  |  | 43836.3333 | 85 | 85
2020-01-06 08:30 | 69 | 65 |  |  | 43836.3542 | 89 | 88
2020-01-06 09:00 | 71 | 67 |  |  | 43836.375 | 94 | 93
2020-01-06 09:30 | 76 | 72 |  |  | 43836.3958 | 97 | 96
2020-01-06 10:00 | 79 | 76 |  |  | 43836.4167 | 97 | 96
2020-01-06 10:30 | 82 | 79 |  |  | 43836.4375 | 99 | 98
2020-01-06 11:00 | 81 | 78 |  |  | 43836.4583 | 99 | 98
2020-01-06 11:30 | 83 | 80 |  |  | 43836.4792 | 100 | 99
2020-01-06 12:00 | 82 | 79 |  |  | 43836.5 | 98 | 98
2020-01-06 12:30 | 80 | 78 |  |  | 43836.5208 | 100 | 100
2020-01-06 13:00 | 84 | 82 |  |  | 43836.5417 | 104 | 104
2020-01-06 13:30 | 90 | 87 |  |  | 43836.5625 | 106 | 106
2020-01-06 14:00 | 94 | 91 |  |  | 43836.5833 | 109 | 109
2020-01-06 14:30 | 96 | 93 |  |  | 43836.6042 | 110 | 110
2020-01-06 15:00 | 93 | 91 |  |  | 43836.625 | 108 | 108
2020-01-06 15:30 | 97 | 89 |  |  | 43836.6458 | 107 | 106
2020-01-06 16:00 | 102 | 92 |  |  | 43836.6667 | 112 | 110
2020-01-06 16:30 | 103 | 94 |  |  | 43836.6875 | 114 | 112
2020-01-06 17:00 | 106 | 96 |  |  | 43836.7083 | 114 | 113
2020-01-06 17:30 | 108 | 96 |  |  | 43836.7292 | 112 | 112
2020-01-06 18:00 | 115 | 93 |  |  | 43836.75 | 106 | 106
2020-01-06 18:30 | 113 | 90 |  |  | 43836.7708 | 101 | 101
2020-01-06 19:00 | 114 | 91 |  |  | 43836.7917 | 103 | 103
2020-01-06 19:30 | 114 | 92 |  |  | 43836.8125 | 103 | 103
2020-01-06 20:00 | 114 | 92 |  |  | 43836.8333 | 103 | 103
2020-01-06 20:30 | 113 | 91 |  |  | 43836.8542 | 101 | 101
2020-01-06 21:00 | 111 | 87 |  |  | 43836.875 | 97 | 97
2020-01-06 21:30 | 104 | 82 |  |  | 43836.8958 | 92 | 92
2020-01-06 22:00 | 90 | 78 |  |  | 43836.9167 | 89 | 88
2020-01-06 22:30 | 88 | 78 |  |  | 43836.9375 | 90 | 88
2020-01-06 23:00 | 86 | 75 |  |  | 43836.9583 | 86 | 85
2020-01-06 23:30 | 82 | 69 |  |  | 43836.9792 | 81 | 80
2020-01-07 | 80 | 64 |  |  | 43837 | 77 | 75
2020-01-07 00:30 | 80 | 61 |  |  | 43837.0208 | 74 | 71
2020-01-07 01:00 | 82 | 58 |  |  | 43837.0417 | 72 | 68
2020-01-07 01:30 | 82 | 58 |  |  | 43837.0625 | 71 | 67
2020-01-07 02:00 | 81 | 57 |  |  | 43837.0833 | 70 | 66
2020-01-07 02:30 | 81 | 55 |  |  | 43837.1042 | 70 | 65
2020-01-07 03:00 | 81 | 55 |  |  | 43837.125 | 70 | 65
2020-01-07 03:30 | 80 | 55 |  |  | 43837.1458 | 68 | 64
2020-01-07 04:00 | 80 | 53 |  |  | 43837.1667 | 68 | 63
2020-01-07 04:30 | 81 | 55 |  |  | 43837.1875 | 68 | 64
2020-01-07 05:00 | 80 | 54 |  |  | 43837.2083 | 69 | 64
2020-01-07 05:30 | 81 | 56 |  |  | 43837.2292 | 71 | 67
2020-01-07 06:00 | 82 | 58 |  |  | 43837.25 | 74 | 70
2020-01-07 06:30 | 80 | 61 |  |  | 43837.2708 | 77 | 75
2020-01-07 07:00 | 81 | 64 |  |  | 43837.2917 | 81 | 79
2020-01-07 07:30 | 85 | 70 |  |  | 43837.3125 | 90 | 89
2020-01-07 08:00 | 92 | 77 |  |  | 43837.3333 | 96 | 95
2020-01-07 08:30 | 88 | 78 |  |  | 43837.3542 | 97 | 96
2020-01-07 09:00 | 86 | 79 |  |  | 43837.375 | 96 | 96
2020-01-07 09:30 | 90 | 83 |  |  | 43837.3958 | 102 | 102
2020-01-07 10:00 | 91 | 86 |  |  | 43837.4167 | 103 | 103
2020-01-07 10:30 | 90 | 85 |  |  | 43837.4375 | 100 | 100
2020-01-07 11:00 | 93 | 87 |  |  | 43837.4583 | 101 | 101
2020-01-07 11:30 | 91 | 84 |  |  | 43837.4792 | 100 | 99
2020-01-07 12:00 | 92 | 84 |  |  | 43837.5 | 98 | 96
2020-01-07 12:30 | 89 | 80 |  |  | 43837.5208 | 97 | 96
2020-01-07 13:00 | 87 | 78 |  |  | 43837.5417 | 98 | 97
2020-01-07 13:30 | 91 | 83 |  |  | 43837.5625 | 99 | 98
2020-01-07 14:00 | 94 | 86 |  |  | 43837.5833 | 99 | 99
2020-01-07 14:30 | 96 | 88 |  |  | 43837.6042 | 101 | 100
2020-01-07 15:00 | 93 | 84 |  |  | 43837.625 | 99 | 98
2020-01-07 15:30 | 91 | 84 |  |  | 43837.6458 | 100 | 99
2020-01-07 16:00 | 94 | 86 |  |  | 43837.6667 | 103 | 102
2020-01-07 16:30 | 94 | 85 |  |  | 43837.6875 | 102 | 101
2020-01-07 17:00 | 97 | 90 |  |  | 43837.7083 | 106 | 105
2020-01-07 17:30 | 97 | 92 |  |  | 43837.7292 | 107 | 106
2020-01-07 18:00 | 97 | 91 |  |  | 43837.75 | 105 | 104
2020-01-07 18:30 | 95 | 90 |  |  | 43837.7708 | 102 | 102
2020-01-07 19:00 | 95 | 91 |  |  | 43837.7917 | 103 | 103
2020-01-07 19:30 | 96 | 92 |  |  | 43837.8125 | 104 | 104
2020-01-07 20:00 | 95 | 91 |  |  | 43837.8333 | 103 | 103
2020-01-07 20:30 | 94 | 90 |  |  | 43837.8542 | 101 | 101
2020-01-07 21:00 | 91 | 87 |  |  | 43837.875 | 98 | 97
2020-01-07 21:30 | 87 | 83 |  |  | 43837.8958 | 94 | 94
2020-01-07 22:00 | 82 | 79 |  |  | 43837.9167 | 91 | 91
2020-01-07 22:30 | 81 | 78 |  |  | 43837.9375 | 90 | 90
2020-01-07 23:00 | 79 | 74 |  |  | 43837.9583 | 85 | 85
2020-01-07 23:30 | 76 | 69 |  |  | 43837.9792 | 81 | 81
2020-01-08 | 70 | 63 |  |  | 43838 | 75 | 75
2020-01-08 00:30 | 68 | 61 |  |  | 43838.0208 | 73 | 72
2020-01-08 01:00 | 66 | 58 |  |  | 43838.0417 | 69 | 68
2020-01-08 01:30 | 68 | 56 |  |  | 43838.0625 | 67 | 66
2020-01-08 02:00 | 67 | 54 |  |  | 43838.0833 | 65 | 64
2020-01-08 02:30 | 66 | 54 |  |  | 43838.1042 | 65 | 65
2020-01-08 03:00 | 67 | 54 |  |  | 43838.125 | 65 | 65
2020-01-08 03:30 | 67 | 54 |  |  | 43838.1458 | 65 | 65
2020-01-08 04:00 | 67 | 54 |  |  | 43838.1667 | 65 | 65
2020-01-08 04:30 | 66 | 53 |  |  | 43838.1875 | 63 | 63
2020-01-08 05:00 | 67 | 54 |  |  | 43838.2083 | 64 | 63
2020-01-08 05:30 | 68 | 56 |  |  | 43838.2292 | 65 | 65
2020-01-08 06:00 | 69 | 59 |  |  | 43838.25 | 69 | 69
2020-01-08 06:30 | 68 | 60 |  |  | 43838.2708 | 73 | 73
2020-01-08 07:00 | 63 | 61 |  |  | 43838.2917 | 77 | 77
2020-01-08 07:30 | 66 | 65 |  |  | 43838.3125 | 83 | 83
2020-01-08 08:00 | 69 | 68 |  |  | 43838.3333 | 86 | 86
2020-01-08 08:30 | 73 | 70 |  |  | 43838.3542 | 91 | 91
2020-01-08 09:00 | 75 | 72 |  |  | 43838.375 | 93 | 92
2020-01-08 09:30 | 76 | 73 |  |  | 43838.3958 | 95 | 94
2020-01-08 10:00 | 75 | 72 |  |  | 43838.4167 | 95 | 93
2020-01-08 10:30 | 77 | 75 |  |  | 43838.4375 | 96 | 95
2020-01-08 11:00 | 81 | 78 |  |  | 43838.4583 | 100 | 98
2020-01-08 11:30 | 81 | 78 |  |  | 43838.4792 | 99 | 97
2020-01-08 12:00 | 78 | 77 |  |  | 43838.5 | 100 | 94
2020-01-08 12:30 | 77 | 77 |  |  | 43838.5208 | 100 | 94
2020-01-08 13:00 | 78 | 77 |  |  | 43838.5417 | 100 | 95
2020-01-08 13:30 | 80 | 80 |  |  | 43838.5625 | 101 | 96
2020-01-08 14:00 | 79 | 79 |  |  | 43838.5833 | 99 | 95
2020-01-08 14:30 | 81 | 81 |  |  | 43838.6042 | 99 | 96
2020-01-08 15:00 | 80 | 80 |  |  | 43838.625 | 98 | 94
2020-01-08 15:30 | 82 | 82 |  |  | 43838.6458 | 100 | 97
2020-01-08 16:00 | 84 | 84 |  |  | 43838.6667 | 103 | 98
2020-01-08 16:30 | 88 | 88 |  |  | 43838.6875 | 107 | 102
2020-01-08 17:00 | 92 | 92 |  |  | 43838.7083 | 111 | 106
2020-01-08 17:30 | 95 | 94 |  |  | 43838.7292 | 112 | 105
2020-01-08 18:00 | 96 | 96 |  |  | 43838.75 | 112 | 105
2020-01-08 18:30 | 93 | 93 |  |  | 43838.7708 | 112 | 102
2020-01-08 19:00 | 95 | 95 |  |  | 43838.7917 | 117 | 105
2020-01-08 19:30 | 96 | 95 |  |  | 43838.8125 | 118 | 107
2020-01-08 20:00 | 95 | 95 |  |  | 43838.8333 | 118 | 106
2020-01-08 20:30 | 95 | 95 |  |  | 43838.8542 | 116 | 104
2020-01-08 21:00 | 91 | 90 |  |  | 43838.875 | 107 | 100
2020-01-08 21:30 | 87 | 86 |  |  | 43838.8958 | 100 | 95
2020-01-08 22:00 | 85 | 82 |  |  | 43838.9167 | 97 | 93
2020-01-08 22:30 | 82 | 80 |  |  | 43838.9375 | 95 | 91
2020-01-08 23:00 | 77 | 76 |  |  | 43838.9583 | 90 | 85
2020-01-08 23:30 | 71 | 69 |  |  | 43838.9792 | 85 | 79
2020-01-09 | 66 | 65 |  |  | 43839 | 80 | 74
2020-01-09 00:30 | 63 | 62 |  |  | 43839.0208 | 78 | 71
2020-01-09 01:00 | 59 | 58 |  |  | 43839.0417 | 74 | 66
2020-01-09 01:30 | 55 | 55 |  |  | 43839.0625 | 72 | 63
2020-01-09 02:00 | 53 | 53 |  |  | 43839.0833 | 72 | 62
2020-01-09 02:30 | 53 | 53 |  |  | 43839.1042 | 73 | 63
2020-01-09 03:00 | 54 | 54 |  |  | 43839.125 | 73 | 63
2020-01-09 03:30 | 55 | 55 |  |  | 43839.1458 | 73 | 63
2020-01-09 04:00 | 54 | 54 |  |  | 43839.1667 | 72 | 63
2020-01-09 04:30 | 52 | 52 |  |  | 43839.1875 | 70 | 60
2020-01-09 05:00 | 51 | 51 |  |  | 43839.2083 | 69 | 59
2020-01-09 05:30 | 53 | 53 |  |  | 43839.2292 | 71 | 61
2020-01-09 06:00 | 58 | 58 |  |  | 43839.25 | 76 | 68
2020-01-09 06:30 | 62 | 62 |  |  | 43839.2708 | 80 | 74
2020-01-09 07:00 | 65 | 65 |  |  | 43839.2917 | 84 | 80
2020-01-09 07:30 | 66 | 66 |  |  | 43839.3125 | 93 | 84
2020-01-09 08:00 | 68 | 68 |  |  | 43839.3333 | 101 | 87
2020-01-09 08:30 | 73 | 73 |  |  | 43839.3542 | 102 | 90
2020-01-09 09:00 | 75 | 74 |  |  | 43839.375 | 104 | 94
2020-01-09 09:30 | 76 | 75 |  |  | 43839.3958 | 105 | 96
2020-01-09 10:00 | 76 | 76 |  |  | 43839.4167 | 107 | 96
2020-01-09 10:30 | 76 | 76 |  |  | 43839.4375 | 105 | 95
2020-01-09 11:00 | 76 | 75 |  |  | 43839.4583 | 105 | 94
2020-01-09 11:30 | 75 | 74 |  |  | 43839.4792 | 103 | 93
2020-01-09 12:00 | 75 | 74 |  |  | 43839.5 | 102 | 92
2020-01-09 12:30 | 76 | 75 |  |  | 43839.5208 | 102 | 91
2020-01-09 13:00 | 78 | 78 |  |  | 43839.5417 | 103 | 93
2020-01-09 13:30 | 80 | 80 |  |  | 43839.5625 | 105 | 95
2020-01-09 14:00 | 82 | 82 |  |  | 43839.5833 | 110 | 97
2020-01-09 14:30 | 82 | 82 |  |  | 43839.6042 | 114 | 96
2020-01-09 15:00 | 81 | 81 |  |  | 43839.625 | 113 | 96
2020-01-09 15:30 | 81 | 81 |  |  | 43839.6458 | 114 | 97
2020-01-09 16:00 | 84 | 83 |  |  | 43839.6667 | 118 | 99
2020-01-09 16:30 | 91 | 91 |  |  | 43839.6875 | 125 | 105
2020-01-09 17:00 | 92 | 92 |  |  | 43839.7083 | 127 | 106
2020-01-09 17:30 | 93 | 93 |  |  | 43839.7292 | 125 | 107
2020-01-09 18:00 | 94 | 93 |  |  | 43839.75 | 128 | 106
2020-01-09 18:30 | 94 | 93 |  |  | 43839.7708 | 131 | 105
2020-01-09 19:00 | 95 | 94 |  |  | 43839.7917 | 133 | 106
2020-01-09 19:30 | 95 | 94 |  |  | 43839.8125 | 133 | 106
2020-01-09 20:00 | 94 | 94 |  |  | 43839.8333 | 134 | 106
2020-01-09 20:30 | 94 | 93 |  |  | 43839.8542 | 134 | 106
2020-01-09 21:00 | 90 | 88 |  |  | 43839.875 | 116 | 100
2020-01-09 21:30 | 88 | 84 |  |  | 43839.8958 | 103 | 94
2020-01-09 22:00 | 87 | 83 |  |  | 43839.9167 | 103 | 93
2020-01-09 22:30 | 83 | 79 |  |  | 43839.9375 | 100 | 90
2020-01-09 23:00 | 81 | 76 |  |  | 43839.9583 | 98 | 86
2020-01-09 23:30 | 72 | 69 |  |  | 43839.9792 | 93 | 80
2020-01-10 | 66 | 65 |  |  | 43840 | 90 | 75
2020-01-10 00:30 | 64 | 63 |  |  | 43840.0208 | 88 | 72
2020-01-10 01:00 | 61 | 59 |  |  | 43840.0417 | 86 | 69
2020-01-10 01:30 | 59 | 58 |  |  | 43840.0625 | 85 | 67
2020-01-10 02:00 | 58 | 57 |  |  | 43840.0833 | 85 | 66
2020-01-10 02:30 | 58 | 56 |  |  | 43840.1042 | 85 | 65
2020-01-10 03:00 | 58 | 56 |  |  | 43840.125 | 85 | 65
2020-01-10 03:30 | 57 | 56 |  |  | 43840.1458 | 83 | 63
2020-01-10 04:00 | 57 | 56 |  |  | 43840.1667 | 85 | 65
2020-01-10 04:30 | 57 | 56 |  |  | 43840.1875 | 83 | 63
2020-01-10 05:00 | 58 | 56 |  |  | 43840.2083 | 84 | 64
2020-01-10 05:30 | 59 | 57 |  |  | 43840.2292 | 85 | 66
2020-01-10 06:00 | 60 | 58 |  |  | 43840.25 | 86 | 67
2020-01-10 06:30 | 60 | 60 |  |  | 43840.2708 | 83 | 75
2020-01-10 07:00 | 68 | 65 |  |  | 43840.2917 | 84 | 83
2020-01-10 07:30 | 71 | 70 |  |  | 43840.3125 | 88 | 88
2020-01-10 08:00 | 76 | 75 |  |  | 43840.3333 | 92 | 91
2020-01-10 08:30 | 84 | 82 |  |  | 43840.3542 | 99 | 98
2020-01-10 09:00 | 82 | 81 |  |  | 43840.375 | 100 | 98
2020-01-10 09:30 | 81 | 79 |  |  | 43840.3958 | 98 | 97
2020-01-10 10:00 | 80 | 78 |  |  | 43840.4167 | 97 | 96
2020-01-10 10:30 | 76 | 75 |  |  | 43840.4375 | 94 | 93
2020-01-10 11:00 | 71 | 69 |  |  | 43840.4583 | 92 | 90
2020-01-10 11:30 | 71 | 69 |  |  | 43840.4792 | 91 | 89
2020-01-10 12:00 | 71 | 68 |  |  | 43840.5 | 91 | 88
2020-01-10 12:30 | 75 | 72 |  |  | 43840.5208 | 93 | 91
2020-01-10 13:00 | 77 | 74 |  |  | 43840.5417 | 95 | 93
2020-01-10 13:30 | 77 | 75 |  |  | 43840.5625 | 94 | 93
2020-01-10 14:00 | 78 | 77 |  |  | 43840.5833 | 95 | 94
2020-01-10 14:30 | 80 | 77 |  |  | 43840.6042 | 96 | 94
2020-01-10 15:00 | 78 | 76 |  |  | 43840.625 | 94 | 93
2020-01-10 15:30 | 80 | 80 |  |  | 43840.6458 | 95 | 94
2020-01-10 16:00 | 84 | 83 |  |  | 43840.6667 | 100 | 98
2020-01-10 16:30 | 85 | 84 |  |  | 43840.6875 | 102 | 101
2020-01-10 17:00 | 92 | 90 |  |  | 43840.7083 | 112 | 107
2020-01-10 17:30 | 90 | 87 |  |  | 43840.7292 | 106 | 101
2020-01-10 18:00 | 85 | 85 |  |  | 43840.75 | 99 | 98
2020-01-10 18:30 | 86 | 86 |  |  | 43840.7708 | 98 | 98
2020-01-10 19:00 | 88 | 87 |  |  | 43840.7917 | 101 | 101
2020-01-10 19:30 | 89 | 89 |  |  | 43840.8125 | 101 | 101
2020-01-10 20:00 | 87 | 87 |  |  | 43840.8333 | 100 | 100
2020-01-10 20:30 | 87 | 86 |  |  | 43840.8542 | 99 | 98
2020-01-10 21:00 | 87 | 86 |  |  | 43840.875 | 98 | 98
2020-01-10 21:30 | 83 | 82 |  |  | 43840.8958 | 95 | 94
2020-01-10 22:00 | 82 | 81 |  |  | 43840.9167 | 94 | 93
2020-01-10 22:30 | 79 | 78 |  |  | 43840.9375 | 92 | 91
2020-01-10 23:00 | 75 | 74 |  |  | 43840.9583 | 86 | 85
2020-01-10 23:30 | 70 | 69 |  |  | 43840.9792 | 82 | 81
2020-01-11 | 67 | 65 |  |  | 43841 | 78 | 77
2020-01-11 00:30 | 67 | 64 |  |  | 43841.0208 | 77 | 76
2020-01-11 01:00 | 68 | 64 |  |  | 43841.0417 | 76 | 75
2020-01-11 01:30 | 65 | 62 |  |  | 43841.0625 | 73 | 72
2020-01-11 02:00 | 62 | 59 |  |  | 43841.0833 | 70 | 69
2020-01-11 02:30 | 62 | 58 |  |  | 43841.1042 | 70 | 69
2020-01-11 03:00 | 62 | 58 |  |  | 43841.125 | 69 | 68
2020-01-11 03:30 | 61 | 57 |  |  | 43841.1458 | 69 | 68
2020-01-11 04:00 | 60 | 56 |  |  | 43841.1667 | 68 | 67
2020-01-11 04:30 | 60 | 56 |  |  | 43841.1875 | 67 | 65
2020-01-11 05:00 | 59 | 55 |  |  | 43841.2083 | 66 | 64
2020-01-11 05:30 | 58 | 54 |  |  | 43841.2292 | 65 | 63
2020-01-11 06:00 | 58 | 54 |  |  | 43841.25 | 66 | 65
2020-01-11 06:30 | 57 | 53 |  |  | 43841.2708 | 65 | 64
2020-01-11 07:00 | 55 | 51 |  |  | 43841.2917 | 65 | 64
2020-01-11 07:30 | 51 | 48 |  |  | 43841.3125 | 62 | 61
2020-01-11 08:00 | 49 | 47 |  |  | 43841.3333 | 61 | 61
2020-01-11 08:30 | 51 | 49 |  |  | 43841.3542 | 64 | 64
2020-01-11 09:00 | 54 | 53 |  |  | 43841.375 | 64 | 63
2020-01-11 09:30 | 61 | 60 |  |  | 43841.3958 | 75 | 75
2020-01-11 10:00 | 64 | 63 |  |  | 43841.4167 | 77 | 76
2020-01-11 10:30 | 62 | 60 |  |  | 43841.4375 | 75 | 74
2020-01-11 11:00 | 60 | 59 |  |  | 43841.4583 | 73 | 73
2020-01-11 11:30 | 58 | 57 |  |  | 43841.4792 | 68 | 68
2020-01-11 12:00 | 66 | 65 |  |  | 43841.5 | 69 | 69
2020-01-11 12:30 | 81 | 80 |  |  | 43841.5208 | 89 | 88
2020-01-11 13:00 | 87 | 86 |  |  | 43841.5417 | 101 | 100
2020-01-11 13:30 | 87 | 86 |  |  | 43841.5625 | 100 | 99
2020-01-11 14:00 | 85 | 84 |  |  | 43841.5833 | 93 | 92
2020-01-11 14:30 | 80 | 79 |  |  | 43841.6042 | 87 | 85
2020-01-11 15:00 | 75 | 75 |  |  | 43841.625 | 81 | 79
2020-01-11 15:30 | 73 | 73 |  |  | 43841.6458 | 81 | 81
2020-01-11 16:00 | 77 | 77 |  |  | 43841.6667 | 81 | 80
2020-01-11 16:30 | 78 | 78 |  |  | 43841.6875 | 87 | 86
2020-01-11 17:00 | 81 | 81 |  |  | 43841.7083 | 89 | 88
2020-01-11 17:30 | 82 | 81 |  |  | 43841.7292 | 90 | 90
2020-01-11 18:00 | 83 | 82 |  |  | 43841.75 | 93 | 92
2020-01-11 18:30 | 83 | 83 |  |  | 43841.7708 | 95 | 94
2020-01-11 19:00 | 89 | 89 |  |  | 43841.7917 | 102 | 101
2020-01-11 19:30 | 89 | 88 |  |  | 43841.8125 | 101 | 100
2020-01-11 20:00 | 89 | 88 |  |  | 43841.8333 | 100 | 99
2020-01-11 20:30 | 90 | 86 |  |  | 43841.8542 | 99 | 97
2020-01-11 21:00 | 88 | 84 |  |  | 43841.875 | 97 | 94
2020-01-11 21:30 | 87 | 83 |  |  | 43841.8958 | 96 | 93
2020-01-11 22:00 | 84 | 80 |  |  | 43841.9167 | 94 | 92
2020-01-11 22:30 | 84 | 80 |  |  | 43841.9375 | 94 | 92
2020-01-11 23:00 | 81 | 77 |  |  | 43841.9583 | 89 | 87
2020-01-11 23:30 | 76 | 71 |  |  | 43841.9792 | 84 | 81
2020-01-12 | 72 | 66 |  |  | 43842 | 79 | 76
2020-01-12 00:30 | 70 | 63 |  |  | 43842.0208 | 76 | 72
2020-01-12 01:00 | 67 | 58 |  |  | 43842.0417 | 72 | 67
2020-01-12 01:30 | 66 | 56 |  |  | 43842.0625 | 71 | 65
2020-01-12 02:00 | 63 | 54 |  |  | 43842.0833 | 70 | 64
2020-01-12 02:30 | 62 | 53 |  |  | 43842.1042 | 69 | 63
2020-01-12 03:00 | 62 | 53 |  |  | 43842.125 | 68 | 64
2020-01-12 03:30 | 62 | 53 |  |  | 43842.1458 | 67 | 63
2020-01-12 04:00 | 61 | 51 |  |  | 43842.1667 | 66 | 62
2020-01-12 04:30 | 61 | 53 |  |  | 43842.1875 | 67 | 64
2020-01-12 05:00 | 60 | 52 |  |  | 43842.2083 | 66 | 63
2020-01-12 05:30 | 61 | 51 |  |  | 43842.2292 | 66 | 63
2020-01-12 06:00 | 59 | 49 |  |  | 43842.25 | 65 | 61
2020-01-12 06:30 | 57 | 47 |  |  | 43842.2708 | 62 | 59
2020-01-12 07:00 | 55 | 46 |  |  | 43842.2917 | 63 | 59
2020-01-12 07:30 | 54 | 46 |  |  | 43842.3125 | 62 | 60
2020-01-12 08:00 | 52 | 46 |  |  | 43842.3333 | 60 | 59
2020-01-12 08:30 | 49 | 43 |  |  | 43842.3542 | 59 | 58
2020-01-12 09:00 | 51 | 45 |  |  | 43842.375 | 62 | 61
2020-01-12 09:30 | 58 | 53 |  |  | 43842.3958 | 74 | 73
2020-01-12 10:00 | 61 | 57 |  |  | 43842.4167 | 78 | 77
2020-01-12 10:30 | 52 | 48 |  |  | 43842.4375 | 65 | 64
2020-01-12 11:00 | 49 | 45 |  |  | 43842.4583 | 58 | 57
2020-01-12 11:30 | 55 | 52 |  |  | 43842.4792 | 59 | 59
2020-01-12 12:00 | 63 | 60 |  |  | 43842.5 | 69 | 69
2020-01-12 12:30 | 66 | 63 |  |  | 43842.5208 | 72 | 72
2020-01-12 13:00 | 67 | 63 |  |  | 43842.5417 | 78 | 77
2020-01-12 13:30 | 73 | 69 |  |  | 43842.5625 | 83 | 82
2020-01-12 14:00 | 78 | 75 |  |  | 43842.5833 | 87 | 86
2020-01-12 14:30 | 80 | 76 |  |  | 43842.6042 | 85 | 84
2020-01-12 15:00 | 70 | 65 |  |  | 43842.625 | 78 | 76
2020-01-12 15:30 | 71 | 66 |  |  | 43842.6458 | 79 | 76
2020-01-12 16:00 | 75 | 70 |  |  | 43842.6667 | 84 | 82
2020-01-12 16:30 | 73 | 68 |  |  | 43842.6875 | 81 | 79
2020-01-12 17:00 | 75 | 70 |  |  | 43842.7083 | 85 | 83
2020-01-12 17:30 | 79 | 74 |  |  | 43842.7292 | 89 | 86
2020-01-12 18:00 | 80 | 75 |  |  | 43842.75 | 87 | 85
2020-01-12 18:30 | 80 | 75 |  |  | 43842.7708 | 88 | 85
2020-01-12 19:00 | 83 | 78 |  |  | 43842.7917 | 92 | 89
2020-01-12 19:30 | 84 | 79 |  |  | 43842.8125 | 93 | 91
2020-01-12 20:00 | 82 | 77 |  |  | 43842.8333 | 92 | 89
2020-01-12 20:30 | 81 | 76 |  |  | 43842.8542 | 91 | 88
2020-01-12 21:00 | 78 | 72 |  |  | 43842.875 | 87 | 83
2020-01-12 21:30 | 75 | 69 |  |  | 43842.8958 | 84 | 81
2020-01-12 22:00 | 73 | 67 |  |  | 43842.9167 | 83 | 80
2020-01-12 22:30 | 73 | 67 |  |  | 43842.9375 | 83 | 80
2020-01-12 23:00 | 73 | 66 |  |  | 43842.9583 | 81 | 78
2020-01-12 23:30 | 70 | 62 |  |  | 43842.9792 | 77 | 74
2020-01-13 | 65 | 58 |  |  | 43843 | 72 | 69
2020-01-13 00:30 | 63 | 55 |  |  | 43843.0208 | 68 | 66
2020-01-13 01:00 | 62 | 53 |  |  | 43843.0417 | 66 | 63
2020-01-13 01:30 | 60 | 51 |  |  | 43843.0625 | 65 | 62
2020-01-13 02:00 | 60 | 51 |  |  | 43843.0833 | 66 | 62
2020-01-13 02:30 | 62 | 53 |  |  | 43843.1042 | 67 | 63
2020-01-13 03:00 | 59 | 50 |  |  | 43843.125 | 64 | 60
2020-01-13 03:30 | 60 | 50 |  |  | 43843.1458 | 65 | 61
2020-01-13 04:00 | 58 | 48 |  |  | 43843.1667 | 64 | 60
2020-01-13 04:30 | 59 | 50 |  |  | 43843.1875 | 64 | 61
2020-01-13 05:00 | 59 | 50 |  |  | 43843.2083 | 64 | 60
2020-01-13 05:30 | 60 | 52 |  |  | 43843.2292 | 66 | 62
2020-01-13 06:00 | 63 | 54 |  |  | 43843.25 | 71 | 68
2020-01-13 06:30 | 67 | 61 |  |  | 43843.2708 | 78 | 77
2020-01-13 07:00 | 68 | 63 |  |  | 43843.2917 | 83 | 82
2020-01-13 07:30 | 66 | 61 |  |  | 43843.3125 | 83 | 82
2020-01-13 08:00 | 70 | 65 |  |  | 43843.3333 | 90 | 89
2020-01-13 08:30 | 76 | 69 |  |  | 43843.3542 | 96 | 93
2020-01-13 09:00 | 73 | 65 |  |  | 43843.375 | 92 | 89
2020-01-13 09:30 | 78 | 71 |  |  | 43843.3958 | 101 | 98
2020-01-13 10:00 | 77 | 71 |  |  | 43843.4167 | 98 | 96
2020-01-13 10:30 | 81 | 77 |  |  | 43843.4375 | 99 | 98
2020-01-13 11:00 | 83 | 79 |  |  | 43843.4583 | 97 | 96
2020-01-13 11:30 | 82 | 78 |  |  | 43843.4792 | 95 | 94
2020-01-13 12:00 | 74 | 70 |  |  | 43843.5 | 87 | 86
2020-01-13 12:30 | 73 | 69 |  |  | 43843.5208 | 88 | 87
2020-01-13 13:00 | 72 | 68 |  |  | 43843.5417 | 85 | 84
2020-01-13 13:30 | 73 | 69 |  |  | 43843.5625 | 89 | 88
2020-01-13 14:00 | 78 | 75 |  |  | 43843.5833 | 90 | 89
2020-01-13 14:30 | 78 | 74 |  |  | 43843.6042 | 88 | 87
2020-01-13 15:00 | 75 | 72 |  |  | 43843.625 | 83 | 82
2020-01-13 15:30 | 74 | 70 |  |  | 43843.6458 | 78 | 76
2020-01-13 16:00 | 78 | 74 |  |  | 43843.6667 | 87 | 86
2020-01-13 16:30 | 84 | 79 |  |  | 43843.6875 | 96 | 94
2020-01-13 17:00 | 89 | 85 |  |  | 43843.7083 | 99 | 97
2020-01-13 17:30 | 87 | 82 |  |  | 43843.7292 | 96 | 93
2020-01-13 18:00 | 86 | 82 |  |  | 43843.75 | 93 | 91
2020-01-13 18:30 | 88 | 84 |  |  | 43843.7708 | 94 | 92
2020-01-13 19:00 | 90 | 86 |  |  | 43843.7917 | 95 | 94
2020-01-13 19:30 | 91 | 86 |  |  | 43843.8125 | 96 | 94
2020-01-13 20:00 | 90 | 85 |  |  | 43843.8333 | 95 | 93
2020-01-13 20:30 | 88 | 84 |  |  | 43843.8542 | 93 | 91
2020-01-13 21:00 | 85 | 80 |  |  | 43843.875 | 89 | 87
2020-01-13 21:30 | 82 | 77 |  |  | 43843.8958 | 86 | 83
2020-01-13 22:00 | 80 | 75 |  |  | 43843.9167 | 87 | 83
2020-01-13 22:30 | 80 | 74 |  |  | 43843.9375 | 86 | 82
2020-01-13 23:00 | 76 | 70 |  |  | 43843.9583 | 81 | 76
2020-01-13 23:30 | 70 | 64 |  |  | 43843.9792 | 77 | 72
2020-01-14 | 67 | 56 |  |  | 43844 | 71 | 65
2020-01-14 00:30 | 66 | 54 |  |  | 43844.0208 | 70 | 62
2020-01-14 01:00 | 65 | 52 |  |  | 43844.0417 | 67 | 59
2020-01-14 01:30 | 61 | 49 |  |  | 43844.0625 | 63 | 56
2020-01-14 02:00 | 60 | 47 |  |  | 43844.0833 | 62 | 55
2020-01-14 02:30 | 60 | 47 |  |  | 43844.1042 | 62 | 55
2020-01-14 03:00 | 60 | 47 |  |  | 43844.125 | 62 | 55
2020-01-14 03:30 | 60 | 47 |  |  | 43844.1458 | 61 | 55
2020-01-14 04:00 | 60 | 47 |  |  | 43844.1667 | 61 | 54
2020-01-14 04:30 | 59 | 47 |  |  | 43844.1875 | 61 | 54
2020-01-14 05:00 | 59 | 47 |  |  | 43844.2083 | 61 | 54
2020-01-14 05:30 | 62 | 51 |  |  | 43844.2292 | 65 | 59
2020-01-14 06:00 | 65 | 55 |  |  | 43844.25 | 70 | 65
2020-01-14 06:30 | 66 | 58 |  |  | 43844.2708 | 75 | 72
2020-01-14 07:00 | 67 | 61 |  |  | 43844.2917 | 78 | 76
2020-01-14 07:30 | 67 | 63 |  |  | 43844.3125 | 81 | 80
2020-01-14 08:00 | 78 | 75 |  |  | 43844.3333 | 101 | 100
2020-01-14 08:30 | 81 | 78 |  |  | 43844.3542 | 106 | 105
2020-01-14 09:00 | 82 | 79 |  |  | 43844.375 | 107 | 106
2020-01-14 09:30 | 80 | 78 |  |  | 43844.3958 | 110 | 110
2020-01-14 10:00 | 81 | 78 |  |  | 43844.4167 | 109 | 109
2020-01-14 10:30 | 79 | 77 |  |  | 43844.4375 | 111 | 111
2020-01-14 11:00 | 84 | 83 |  |  | 43844.4583 | 117 | 117
2020-01-14 11:30 | 71 | 70 |  |  | 43844.4792 | 91 | 91
2020-01-14 12:00 | 76 | 75 |  |  | 43844.5 | 95 | 95
2020-01-14 12:30 | 84 | 82 |  |  | 43844.5208 | 104 | 104
2020-01-14 13:00 | 80 | 79 |  |  | 43844.5417 | 98 | 98
2020-01-14 13:30 | 81 | 80 |  |  | 43844.5625 | 95 | 95
2020-01-14 14:00 | 80 | 79 |  |  | 43844.5833 | 92 | 91
2020-01-14 14:30 | 82 | 81 |  |  | 43844.6042 | 94 | 93
2020-01-14 15:00 | 81 | 80 |  |  | 43844.625 | 97 | 96
2020-01-14 15:30 | 87 | 86 |  |  | 43844.6458 | 96 | 95
2020-01-14 16:00 | 78 | 76 |  |  | 43844.6667 | 91 | 90
2020-01-14 16:30 | 88 | 86 |  |  | 43844.6875 | 94 | 93
2020-01-14 17:00 | 88 | 86 |  |  | 43844.7083 | 97 | 95
2020-01-14 17:30 | 88 | 86 |  |  | 43844.7292 | 97 | 96
2020-01-14 18:00 | 89 | 87 |  |  | 43844.75 | 96 | 96
2020-01-14 18:30 | 87 | 87 |  |  | 43844.7708 | 95 | 95
2020-01-14 19:00 | 92 | 91 |  |  | 43844.7917 | 99 | 99
2020-01-14 19:30 | 91 | 90 |  |  | 43844.8125 | 99 | 98
2020-01-14 20:00 | 92 | 91 |  |  | 43844.8333 | 99 | 99
2020-01-14 20:30 | 91 | 91 |  |  | 43844.8542 | 99 | 99
2020-01-14 21:00 | 86 | 85 |  |  | 43844.875 | 94 | 94
2020-01-14 21:30 | 81 | 80 |  |  | 43844.8958 | 88 | 87
2020-01-14 22:00 | 79 | 78 |  |  | 43844.9167 | 87 | 86
2020-01-14 22:30 | 76 | 75 |  |  | 43844.9375 | 84 | 84
2020-01-14 23:00 | 72 | 69 |  |  | 43844.9583 | 77 | 76
2020-01-14 23:30 | 69 | 66 |  |  | 43844.9792 | 75 | 74
2020-01-15 | 65 | 61 |  |  | 43845 | 71 | 69
2020-01-15 00:30 | 62 | 57 |  |  | 43845.0208 | 67 | 65
2020-01-15 01:00 | 61 | 55 |  |  | 43845.0417 | 65 | 63
2020-01-15 01:30 | 59 | 53 |  |  | 43845.0625 | 62 | 60
2020-01-15 02:00 | 56 | 50 |  |  | 43845.0833 | 61 | 58
2020-01-15 02:30 | 55 | 50 |  |  | 43845.1042 | 60 | 58
2020-01-15 03:00 | 56 | 51 |  |  | 43845.125 | 59 | 59
2020-01-15 03:30 | 55 | 51 |  |  | 43845.1458 | 61 | 60
2020-01-15 04:00 | 55 | 50 |  |  | 43845.1667 | 60 | 59
2020-01-15 04:30 | 55 | 51 |  |  | 43845.1875 | 59 | 58
2020-01-15 05:00 | 55 | 52 |  |  | 43845.2083 | 61 | 61
2020-01-15 05:30 | 58 | 55 |  |  | 43845.2292 | 66 | 65
2020-01-15 06:00 | 62 | 59 |  |  | 43845.25 | 70 | 69
2020-01-15 06:30 | 65 | 63 |  |  | 43845.2708 | 76 | 75
2020-01-15 07:00 | 66 | 64 |  |  | 43845.2917 | 80 | 79
2020-01-15 07:30 | 72 | 69 |  |  | 43845.3125 | 87 | 86
2020-01-15 08:00 | 76 | 70 |  |  | 43845.3333 | 93 | 93
2020-01-15 08:30 | 99 | 94 |  |  | 43845.3542 | 133 | 133
2020-01-15 09:00 | 110 | 105 |  |  | 43845.375 | 140 | 140
2020-01-15 09:30 | 113 | 109 |  |  | 43845.3958 | 143 | 143
2020-01-15 10:00 | 105 | 101 |  |  | 43845.4167 | 137 | 137
2020-01-15 10:30 | 99 | 95 |  |  | 43845.4375 | 138 | 138
2020-01-15 11:00 | 96 | 92 |  |  | 43845.4583 | 130 | 130
2020-01-15 11:30 | 92 | 88 |  |  | 43845.4792 | 119 | 119
2020-01-15 12:00 | 91 | 87 |  |  | 43845.5 | 125 | 124
2020-01-15 12:30 | 99 | 94 |  |  | 43845.5208 | 132 | 132
2020-01-15 13:00 | 99 | 95 |  |  | 43845.5417 | 131 | 130
2020-01-15 13:30 | 83 | 79 |  |  | 43845.5625 | 98 | 98
2020-01-15 14:00 | 81 | 76 |  |  | 43845.5833 | 91 | 91
2020-01-15 14:30 | 84 | 80 |  |  | 43845.6042 | 93 | 93
2020-01-15 15:00 | 83 | 81 |  |  | 43845.625 | 95 | 95
2020-01-15 15:30 | 83 | 83 |  |  | 43845.6458 | 101 | 100
2020-01-15 16:00 | 89 | 88 |  |  | 43845.6667 | 107 | 106
2020-01-15 16:30 | 97 | 97 |  |  | 43845.6875 | 109 | 109
2020-01-15 17:00 | 99 | 98 |  |  | 43845.7083 | 110 | 109
2020-01-15 17:30 | 98 | 97 |  |  | 43845.7292 | 109 | 109
2020-01-15 18:00 | 100 | 97 |  |  | 43845.75 | 108 | 107
2020-01-15 18:30 | 97 | 94 |  |  | 43845.7708 | 103 | 103
2020-01-15 19:00 | 99 | 96 |  |  | 43845.7917 | 105 | 105
2020-01-15 19:30 | 97 | 95 |  |  | 43845.8125 | 105 | 104
2020-01-15 20:00 | 98 | 96 |  |  | 43845.8333 | 104 | 104
2020-01-15 20:30 | 98 | 95 |  |  | 43845.8542 | 105 | 104
2020-01-15 21:00 | 95 | 93 |  |  | 43845.875 | 101 | 101
2020-01-15 21:30 | 93 | 90 |  |  | 43845.8958 | 98 | 98
2020-01-15 22:00 | 89 | 86 |  |  | 43845.9167 | 97 | 96
2020-01-15 22:30 | 85 | 82 |  |  | 43845.9375 | 95 | 94
2020-01-15 23:00 | 82 | 78 |  |  | 43845.9583 | 90 | 89
2020-01-15 23:30 | 77 | 72 |  |  | 43845.9792 | 82 | 82
2020-01-16 | 73 | 67 |  |  | 43846 | 76 | 76
2020-01-16 00:30 | 71 | 64 |  |  | 43846.0208 | 73 | 73
2020-01-16 01:00 | 70 | 61 |  |  | 43846.0417 | 70 | 70
2020-01-16 01:30 | 66 | 57 |  |  | 43846.0625 | 65 | 65
2020-01-16 02:00 | 66 | 56 |  |  | 43846.0833 | 65 | 65
2020-01-16 02:30 | 67 | 57 |  |  | 43846.1042 | 65 | 65
2020-01-16 03:00 | 68 | 57 |  |  | 43846.125 | 66 | 66
2020-01-16 03:30 | 68 | 58 |  |  | 43846.1458 | 66 | 66
2020-01-16 04:00 | 68 | 58 |  |  | 43846.1667 | 65 | 65
2020-01-16 04:30 | 67 | 58 |  |  | 43846.1875 | 66 | 66
2020-01-16 05:00 | 68 | 58 |  |  | 43846.2083 | 68 | 68
2020-01-16 05:30 | 69 | 60 |  |  | 43846.2292 | 68 | 68
2020-01-16 06:00 | 70 | 61 |  |  | 43846.25 | 71 | 71
2020-01-16 06:30 | 71 | 63 |  |  | 43846.2708 | 75 | 75
2020-01-16 07:00 | 73 | 65 |  |  | 43846.2917 | 79 | 79
2020-01-16 07:30 | 74 | 69 |  |  | 43846.3125 | 85 | 85
2020-01-16 08:00 | 78 | 72 |  |  | 43846.3333 | 91 | 91
2020-01-16 08:30 | 82 | 77 |  |  | 43846.3542 | 99 | 99
2020-01-16 09:00 | 87 | 80 |  |  | 43846.375 | 102 | 102
2020-01-16 09:30 | 90 | 83 |  |  | 43846.3958 | 107 | 107
2020-01-16 10:00 | 93 | 86 |  |  | 43846.4167 | 104 | 103
2020-01-16 10:30 | 91 | 85 |  |  | 43846.4375 | 100 | 99
2020-01-16 11:00 | 89 | 82 |  |  | 43846.4583 | 100 | 99
2020-01-16 11:30 | 90 | 84 |  |  | 43846.4792 | 103 | 103
2020-01-16 12:00 | 95 | 89 |  |  | 43846.5 | 107 | 106
2020-01-16 12:30 | 94 | 88 |  |  | 43846.5208 | 112 | 111
2020-01-16 13:00 | 94 | 88 |  |  | 43846.5417 | 107 | 107
2020-01-16 13:30 | 94 | 88 |  |  | 43846.5625 | 104 | 103
2020-01-16 14:00 | 97 | 89 |  |  | 43846.5833 | 108 | 107
2020-01-16 14:30 | 96 | 89 |  |  | 43846.6042 | 106 | 105
2020-01-16 15:00 | 90 | 83 |  |  | 43846.625 | 97 | 97
2020-01-16 15:30 | 87 | 79 |  |  | 43846.6458 | 95 | 93
2020-01-16 16:00 | 88 | 81 |  |  | 43846.6667 | 96 | 95
2020-01-16 16:30 | 87 | 79 |  |  | 43846.6875 | 97 | 95
2020-01-16 17:00 | 89 | 82 |  |  | 43846.7083 | 97 | 96
2020-01-16 17:30 | 89 | 82 |  |  | 43846.7292 | 96 | 94
2020-01-16 18:00 | 92 | 84 |  |  | 43846.75 | 96 | 94
2020-01-16 18:30 | 92 | 83 |  |  | 43846.7708 | 95 | 93
2020-01-16 19:00 | 93 | 85 |  |  | 43846.7917 | 97 | 95
2020-01-16 19:30 | 94 | 86 |  |  | 43846.8125 | 97 | 96
2020-01-16 20:00 | 96 | 89 |  |  | 43846.8333 | 99 | 97
2020-01-16 20:30 | 97 | 90 |  |  | 43846.8542 | 100 | 98
2020-01-16 21:00 | 91 | 87 |  |  | 43846.875 | 95 | 94
2020-01-16 21:30 | 86 | 82 |  |  | 43846.8958 | 90 | 90
2020-01-16 22:00 | 85 | 81 |  |  | 43846.9167 | 90 | 90
2020-01-16 22:30 | 83 | 78 |  |  | 43846.9375 | 87 | 87
2020-01-16 23:00 | 80 | 75 |  |  | 43846.9583 | 82 | 82
2020-01-16 23:30 | 74 | 68 |  |  | 43846.9792 | 76 | 76
2020-01-17 | 71 | 63 |  |  | 43847 | 72 | 72
2020-01-17 00:30 | 69 | 61 |  |  | 43847.0208 | 70 | 70
2020-01-17 01:00 | 67 | 57 |  |  | 43847.0417 | 65 | 65
2020-01-17 01:30 | 64 | 55 |  |  | 43847.0625 | 63 | 63
2020-01-17 02:00 | 62 | 53 |  |  | 43847.0833 | 62 | 62
2020-01-17 02:30 | 61 | 53 |  |  | 43847.1042 | 62 | 62
2020-01-17 03:00 | 61 | 55 |  |  | 43847.125 | 63 | 63
2020-01-17 03:30 | 61 | 55 |  |  | 43847.1458 | 62 | 61
2020-01-17 04:00 | 60 | 54 |  |  | 43847.1667 | 62 | 62
2020-01-17 04:30 | 60 | 53 |  |  | 43847.1875 | 62 | 62
2020-01-17 05:00 | 60 | 54 |  |  | 43847.2083 | 62 | 62
2020-01-17 05:30 | 64 | 58 |  |  | 43847.2292 | 66 | 66
2020-01-17 06:00 | 68 | 63 |  |  | 43847.25 | 71 | 70
2020-01-17 06:30 | 70 | 66 |  |  | 43847.2708 | 78 | 77
2020-01-17 07:00 | 74 | 69 |  |  | 43847.2917 | 82 | 82
2020-01-17 07:30 | 78 | 71 |  |  | 43847.3125 | 89 | 88
2020-01-17 08:00 | 77 | 70 |  |  | 43847.3333 | 89 | 89
2020-01-17 08:30 | 73 | 67 |  |  | 43847.3542 | 90 | 90
2020-01-17 09:00 | 75 | 69 |  |  | 43847.375 | 91 | 91
2020-01-17 09:30 | 76 | 70 |  |  | 43847.3958 | 92 | 92
2020-01-17 10:00 | 79 | 73 |  |  | 43847.4167 | 94 | 94
2020-01-17 10:30 | 77 | 71 |  |  | 43847.4375 | 92 | 92
2020-01-17 11:00 | 78 | 72 |  |  | 43847.4583 | 95 | 95
2020-01-17 11:30 | 81 | 75 |  |  | 43847.4792 | 89 | 89
2020-01-17 12:00 | 84 | 79 |  |  | 43847.5 | 94 | 94
2020-01-17 12:30 | 71 | 67 |  |  | 43847.5208 | 77 | 77
2020-01-17 13:00 | 68 | 64 |  |  | 43847.5417 | 74 | 73
2020-01-17 13:30 | 82 | 74 |  |  | 43847.5625 | 94 | 93
2020-01-17 14:00 | 85 | 76 |  |  | 43847.5833 | 97 | 96
2020-01-17 14:30 | 85 | 76 |  |  | 43847.6042 | 93 | 91
2020-01-17 15:00 | 96 | 88 |  |  | 43847.625 | 98 | 97
2020-01-17 15:30 | 101 | 92 |  |  | 43847.6458 | 105 | 104
2020-01-17 16:00 | 99 | 90 |  |  | 43847.6667 | 103 | 101
2020-01-17 16:30 | 97 | 89 |  |  | 43847.6875 | 103 | 102
2020-01-17 17:00 | 99 | 91 |  |  | 43847.7083 | 105 | 104
2020-01-17 17:30 | 98 | 91 |  |  | 43847.7292 | 104 | 103
2020-01-17 18:00 | 97 | 90 |  |  | 43847.75 | 101 | 99
2020-01-17 18:30 | 91 | 89 |  |  | 43847.7708 | 97 | 96
2020-01-17 19:00 | 93 | 91 |  |  | 43847.7917 | 100 | 99
2020-01-17 19:30 | 93 | 92 |  |  | 43847.8125 | 100 | 100
2020-01-17 20:00 | 93 | 91 |  |  | 43847.8333 | 100 | 100
2020-01-17 20:30 | 92 | 90 |  |  | 43847.8542 | 100 | 100
2020-01-17 21:00 | 88 | 87 |  |  | 43847.875 | 97 | 97
2020-01-17 21:30 | 84 | 83 |  |  | 43847.8958 | 92 | 92
2020-01-17 22:00 | 81 | 79 |  |  | 43847.9167 | 89 | 89
2020-01-17 22:30 | 80 | 78 |  |  | 43847.9375 | 89 | 88
2020-01-17 23:00 | 79 | 77 |  |  | 43847.9583 | 86 | 85
2020-01-17 23:30 | 73 | 70 |  |  | 43847.9792 | 80 | 78
2020-01-18 | 67 | 63 |  |  | 43848 | 73 | 71
2020-01-18 00:30 | 64 | 60 |  |  | 43848.0208 | 70 | 69
2020-01-18 01:00 | 62 | 58 |  |  | 43848.0417 | 67 | 66
2020-01-18 01:30 | 62 | 58 |  |  | 43848.0625 | 67 | 66
2020-01-18 02:00 | 59 | 54 |  |  | 43848.0833 | 63 | 62
2020-01-18 02:30 | 58 | 54 |  |  | 43848.1042 | 62 | 60
2020-01-18 03:00 | 58 | 54 |  |  | 43848.125 | 63 | 61
2020-01-18 03:30 | 58 | 54 |  |  | 43848.1458 | 63 | 62
2020-01-18 04:00 | 56 | 52 |  |  | 43848.1667 | 60 | 59
2020-01-18 04:30 | 55 | 51 |  |  | 43848.1875 | 59 | 58
2020-01-18 05:00 | 54 | 50 |  |  | 43848.2083 | 58 | 56
2020-01-18 05:30 | 53 | 50 |  |  | 43848.2292 | 58 | 57
2020-01-18 06:00 | 54 | 50 |  |  | 43848.25 | 59 | 58
2020-01-18 06:30 | 54 | 50 |  |  | 43848.2708 | 61 | 60
2020-01-18 07:00 | 52 | 49 |  |  | 43848.2917 | 59 | 58
2020-01-18 07:30 | 44 | 40 |  |  | 43848.3125 | 53 | 52
2020-01-18 08:00 | 35 | 27 |  |  | 43848.3333 | 46 | 43
2020-01-18 08:30 | 40 | 30 |  |  | 43848.3542 | 53 | 49
2020-01-18 09:00 | 39 | 34 |  |  | 43848.375 | 51 | 49
2020-01-18 09:30 | 35 | 32 |  |  | 43848.3958 | 48 | 47
2020-01-18 10:00 | 35 | 32 |  |  | 43848.4167 | 51 | 50
2020-01-18 10:30 | 37 | 34 |  |  | 43848.4375 | 51 | 50
2020-01-18 11:00 | 36 | 33 |  |  | 43848.4583 | 54 | 54
2020-01-18 11:30 | 40 | 38 |  |  | 43848.4792 | 59 | 59
2020-01-18 12:00 | 43 | 41 |  |  | 43848.5 | 57 | 57
2020-01-18 12:30 | 46 | 43 |  |  | 43848.5208 | 63 | 63
2020-01-18 13:00 | 47 | 45 |  |  | 43848.5417 | 64 | 63
2020-01-18 13:30 | 46 | 43 |  |  | 43848.5625 | 65 | 64
2020-01-18 14:00 | 51 | 49 |  |  | 43848.5833 | 67 | 66
2020-01-18 14:30 | 52 | 49 |  |  | 43848.6042 | 67 | 67
2020-01-18 15:00 | 60 | 58 |  |  | 43848.625 | 70 | 69
2020-01-18 15:30 | 62 | 61 |  |  | 43848.6458 | 67 | 67
2020-01-18 16:00 | 67 | 66 |  |  | 43848.6667 | 75 | 75
2020-01-18 16:30 | 73 | 73 |  |  | 43848.6875 | 84 | 84
2020-01-18 17:00 | 76 | 76 |  |  | 43848.7083 | 87 | 87
2020-01-18 17:30 | 78 | 77 |  |  | 43848.7292 | 87 | 87
2020-01-18 18:00 | 80 | 78 |  |  | 43848.75 | 88 | 87
2020-01-18 18:30 | 85 | 83 |  |  | 43848.7708 | 94 | 93
2020-01-18 19:00 | 88 | 86 |  |  | 43848.7917 | 97 | 96
2020-01-18 19:30 | 90 | 88 |  |  | 43848.8125 | 98 | 98
2020-01-18 20:00 | 90 | 88 |  |  | 43848.8333 | 98 | 98
2020-01-18 20:30 | 89 | 87 |  |  | 43848.8542 | 98 | 97
2020-01-18 21:00 | 86 | 84 |  |  | 43848.875 | 94 | 94
2020-01-18 21:30 | 83 | 81 |  |  | 43848.8958 | 91 | 90
2020-01-18 22:00 | 81 | 79 |  |  | 43848.9167 | 90 | 90
2020-01-18 22:30 | 80 | 78 |  |  | 43848.9375 | 89 | 88
2020-01-18 23:00 | 74 | 73 |  |  | 43848.9583 | 82 | 82
2020-01-18 23:30 | 70 | 67 |  |  | 43848.9792 | 78 | 78
2020-01-19 | 66 | 63 |  |  | 43849 | 75 | 74
2020-01-19 00:30 | 64 | 61 |  |  | 43849.0208 | 72 | 71
2020-01-19 01:00 | 63 | 60 |  |  | 43849.0417 | 68 | 68
2020-01-19 01:30 | 59 | 56 |  |  | 43849.0625 | 65 | 64
2020-01-19 02:00 | 57 | 53 |  |  | 43849.0833 | 63 | 62
2020-01-19 02:30 | 56 | 52 |  |  | 43849.1042 | 62 | 61
2020-01-19 03:00 | 55 | 51 |  |  | 43849.125 | 62 | 61
2020-01-19 03:30 | 55 | 51 |  |  | 43849.1458 | 62 | 61
2020-01-19 04:00 | 55 | 51 |  |  | 43849.1667 | 62 | 61
2020-01-19 04:30 | 54 | 50 |  |  | 43849.1875 | 60 | 59
2020-01-19 05:00 | 53 | 49 |  |  | 43849.2083 | 59 | 58
2020-01-19 05:30 | 51 | 47 |  |  | 43849.2292 | 58 | 57
2020-01-19 06:00 | 52 | 45 |  |  | 43849.25 | 57 | 56
2020-01-19 06:30 | 50 | 42 |  |  | 43849.2708 | 54 | 52
2020-01-19 07:00 | 45 | 37 |  |  | 43849.2917 | 50 | 48
2020-01-19 07:30 | 41 | 35 |  |  | 43849.3125 | 49 | 48
2020-01-19 08:00 | 33 | 28 |  |  | 43849.3333 | 45 | 45
2020-01-19 08:30 | 37 | 33 |  |  | 43849.3542 | 51 | 51
2020-01-19 09:00 | 38 | 35 |  |  | 43849.375 | 51 | 51
2020-01-19 09:30 | 44 | 42 |  |  | 43849.3958 | 60 | 60
2020-01-19 10:00 | 47 | 45 |  |  | 43849.4167 | 65 | 65
2020-01-19 10:30 | 46 | 45 |  |  | 43849.4375 | 57 | 57
2020-01-19 11:00 | 36 | 34 |  |  | 43849.4583 | 48 | 48
2020-01-19 11:30 | 47 | 46 |  |  | 43849.4792 | 56 | 56
2020-01-19 12:00 | 72 | 70 |  |  | 43849.5 | 78 | 78
2020-01-19 12:30 | 71 | 68 |  |  | 43849.5208 | 83 | 83
2020-01-19 13:00 | 62 | 57 |  |  | 43849.5417 | 75 | 74
2020-01-19 13:30 | 63 | 58 |  |  | 43849.5625 | 73 | 72
2020-01-19 14:00 | 65 | 61 |  |  | 43849.5833 | 76 | 76
2020-01-19 14:30 | 72 | 68 |  |  | 43849.6042 | 82 | 81
2020-01-19 15:00 | 75 | 72 |  |  | 43849.625 | 77 | 76
2020-01-19 15:30 | 70 | 67 |  |  | 43849.6458 | 78 | 76
2020-01-19 16:00 | 79 | 75 |  |  | 43849.6667 | 87 | 86
2020-01-19 16:30 | 90 | 87 |  |  | 43849.6875 | 96 | 95
2020-01-19 17:00 | 86 | 84 |  |  | 43849.7083 | 93 | 93
2020-01-19 17:30 | 87 | 84 |  |  | 43849.7292 | 94 | 93
2020-01-19 18:00 | 86 | 83 |  |  | 43849.75 | 95 | 94
2020-01-19 18:30 | 90 | 87 |  |  | 43849.7708 | 99 | 97
2020-01-19 19:00 | 97 | 94 |  |  | 43849.7917 | 107 | 106
2020-01-19 19:30 | 100 | 96 |  |  | 43849.8125 | 110 | 108
2020-01-19 20:00 | 100 | 95 |  |  | 43849.8333 | 112 | 107
2020-01-19 20:30 | 99 | 96 |  |  | 43849.8542 | 110 | 109
2020-01-19 21:00 | 96 | 93 |  |  | 43849.875 | 107 | 106
2020-01-19 21:30 | 92 | 89 |  |  | 43849.8958 | 102 | 101
2020-01-19 22:00 | 88 | 85 |  |  | 43849.9167 | 100 | 99
2020-01-19 22:30 | 85 | 82 |  |  | 43849.9375 | 98 | 97
2020-01-19 23:00 | 81 | 77 |  |  | 43849.9583 | 92 | 91
2020-01-19 23:30 | 74 | 70 |  |  | 43849.9792 | 86 | 84
2020-01-20 | 71 | 66 |  |  | 43850 | 81 | 80
2020-01-20 00:30 | 69 | 63 |  |  | 43850.0208 | 77 | 75
2020-01-20 01:00 | 67 | 59 |  |  | 43850.0417 | 73 | 70
2020-01-20 01:30 | 67 | 59 |  |  | 43850.0625 | 74 | 71
2020-01-20 02:00 | 66 | 58 |  |  | 43850.0833 | 72 | 69
2020-01-20 02:30 | 66 | 59 |  |  | 43850.1042 | 73 | 70
2020-01-20 03:00 | 67 | 59 |  |  | 43850.125 | 74 | 71
2020-01-20 03:30 | 67 | 59 |  |  | 43850.1458 | 74 | 70
2020-01-20 04:00 | 66 | 58 |  |  | 43850.1667 | 73 | 69
2020-01-20 04:30 | 67 | 59 |  |  | 43850.1875 | 73 | 70
2020-01-20 05:00 | 67 | 60 |  |  | 43850.2083 | 74 | 71
2020-01-20 05:30 | 70 | 64 |  |  | 43850.2292 | 78 | 75
2020-01-20 06:00 | 73 | 67 |  |  | 43850.25 | 82 | 79
2020-01-20 06:30 | 77 | 73 |  |  | 43850.2708 | 91 | 89
2020-01-20 07:00 | 78 | 76 |  |  | 43850.2917 | 95 | 94
2020-01-20 07:30 | 84 | 82 |  |  | 43850.3125 | 107 | 106
2020-01-20 08:00 | 86 | 84 |  |  | 43850.3333 | 110 | 109
2020-01-20 08:30 | 87 | 85 |  |  | 43850.3542 | 112 | 111
2020-01-20 09:00 | 89 | 86 |  |  | 43850.375 | 114 | 112
2020-01-20 09:30 | 91 | 89 |  |  | 43850.3958 | 114 | 113
2020-01-20 10:00 | 92 | 90 |  |  | 43850.4167 | 116 | 115
2020-01-20 10:30 | 94 | 91 |  |  | 43850.4375 | 115 | 114
2020-01-20 11:00 | 98 | 96 |  |  | 43850.4583 | 116 | 115
2020-01-20 11:30 | 102 | 99 |  |  | 43850.4792 | 122 | 121
2020-01-20 12:00 | 101 | 99 |  |  | 43850.5 | 124 | 124
2020-01-20 12:30 | 99 | 97 |  |  | 43850.5208 | 123 | 122
2020-01-20 13:00 | 103 | 101 |  |  | 43850.5417 | 127 | 126
2020-01-20 13:30 | 107 | 105 |  |  | 43850.5625 | 131 | 130
2020-01-20 14:00 | 105 | 103 |  |  | 43850.5833 | 133 | 131
2020-01-20 14:30 | 108 | 106 |  |  | 43850.6042 | 131 | 128
2020-01-20 15:00 | 114 | 113 |  |  | 43850.625 | 142 | 139
2020-01-20 15:30 | 117 | 116 |  |  | 43850.6458 | 143 | 141
2020-01-20 16:00 | 106 | 100 |  |  | 43850.6667 | 147 | 145
2020-01-20 16:30 | 100 | 92 |  |  | 43850.6875 | 141 | 137
2020-01-20 17:00 | 103 | 96 |  |  | 43850.7083 | 137 | 133
2020-01-20 17:30 | 101 | 95 |  |  | 43850.7292 | 131 | 128
2020-01-20 18:00 | 97 | 91 |  |  | 43850.75 | 124 | 120
2020-01-20 18:30 | 94 | 87 |  |  | 43850.7708 | 120 | 115
2020-01-20 19:00 | 96 | 90 |  |  | 43850.7917 | 121 | 117
2020-01-20 19:30 | 95 | 91 |  |  | 43850.8125 | 117 | 113
2020-01-20 20:00 | 102 | 98 |  |  | 43850.8333 | 118 | 114
2020-01-20 20:30 | 101 | 97 |  |  | 43850.8542 | 114 | 110
2020-01-20 21:00 | 97 | 94 |  |  | 43850.875 | 107 | 105
2020-01-20 21:30 | 92 | 88 |  |  | 43850.8958 | 101 | 98
2020-01-20 22:00 | 90 | 87 |  |  | 43850.9167 | 99 | 97
2020-01-20 22:30 | 87 | 83 |  |  | 43850.9375 | 96 | 94
2020-01-20 23:00 | 84 | 81 |  |  | 43850.9583 | 91 | 91
2020-01-20 23:30 | 77 | 74 |  |  | 43850.9792 | 85 | 85
2020-01-21 | 70 | 67 |  |  | 43851 | 79 | 78
2020-01-21 00:30 | 71 | 67 |  |  | 43851.0208 | 78 | 77
2020-01-21 01:00 | 74 | 66 |  |  | 43851.0417 | 76 | 74
2020-01-21 01:30 | 75 | 66 |  |  | 43851.0625 | 75 | 74
2020-01-21 02:00 | 73 | 65 |  |  | 43851.0833 | 73 | 72
2020-01-21 02:30 | 74 | 64 |  |  | 43851.1042 | 73 | 71
2020-01-21 03:00 | 74 | 64 |  |  | 43851.125 | 75 | 73
2020-01-21 03:30 | 73 | 63 |  |  | 43851.1458 | 73 | 71
2020-01-21 04:00 | 72 | 62 |  |  | 43851.1667 | 72 | 70
2020-01-21 04:30 | 73 | 63 |  |  | 43851.1875 | 74 | 71
2020-01-21 05:00 | 72 | 63 |  |  | 43851.2083 | 74 | 71
2020-01-21 05:30 | 75 | 66 |  |  | 43851.2292 | 77 | 75
2020-01-21 06:00 | 78 | 70 |  |  | 43851.25 | 82 | 80
2020-01-21 06:30 | 77 | 74 |  |  | 43851.2708 | 90 | 89
2020-01-21 07:00 | 80 | 77 |  |  | 43851.2917 | 97 | 96
2020-01-21 07:30 | 80 | 78 |  |  | 43851.3125 | 100 | 100
2020-01-21 08:00 | 91 | 90 |  |  | 43851.3333 | 113 | 112
2020-01-21 08:30 | 98 | 95 |  |  | 43851.3542 | 132 | 131
2020-01-21 09:00 | 99 | 96 |  |  | 43851.375 | 133 | 131
2020-01-21 09:30 | 102 | 98 |  |  | 43851.3958 | 136 | 135
2020-01-21 10:00 | 103 | 100 |  |  | 43851.4167 | 137 | 137
2020-01-21 10:30 | 105 | 102 |  |  | 43851.4375 | 139 | 138
2020-01-21 11:00 | 110 | 107 |  |  | 43851.4583 | 145 | 144
2020-01-21 11:30 | 114 | 111 |  |  | 43851.4792 | 147 | 146
2020-01-21 12:00 | 117 | 116 |  |  | 43851.5 | 152 | 152
2020-01-21 12:30 | 124 | 122 |  |  | 43851.5208 | 159 | 158
2020-01-21 13:00 | 124 | 123 |  |  | 43851.5417 | 162 | 161
2020-01-21 13:30 | 112 | 110 |  |  | 43851.5625 | 135 | 134
2020-01-21 14:00 | 110 | 109 |  |  | 43851.5833 | 136 | 135
2020-01-21 14:30 | 108 | 106 |  |  | 43851.6042 | 136 | 135
2020-01-21 15:00 | 108 | 106 |  |  | 43851.625 | 137 | 135
2020-01-21 15:30 | 110 | 108 |  |  | 43851.6458 | 140 | 138
2020-01-21 16:00 | 115 | 113 |  |  | 43851.6667 | 145 | 143
2020-01-21 16:30 | 114 | 112 |  |  | 43851.6875 | 137 | 135
2020-01-21 17:00 | 102 | 101 |  |  | 43851.7083 | 120 | 120
2020-01-21 17:30 | 104 | 102 |  |  | 43851.7292 | 120 | 118
2020-01-21 18:00 | 105 | 103 |  |  | 43851.75 | 118 | 115
2020-01-21 18:30 | 100 | 98 |  |  | 43851.7708 | 112 | 110
2020-01-21 19:00 | 102 | 101 |  |  | 43851.7917 | 115 | 114
2020-01-21 19:30 | 100 | 99 |  |  | 43851.8125 | 115 | 114
2020-01-21 20:00 | 100 | 99 |  |  | 43851.8333 | 115 | 115
2020-01-21 20:30 | 99 | 99 |  |  | 43851.8542 | 115 | 115
2020-01-21 21:00 | 103 | 102 |  |  | 43851.875 | 114 | 114
2020-01-21 21:30 | 99 | 99 |  |  | 43851.8958 | 109 | 109
2020-01-21 22:00 | 94 | 94 |  |  | 43851.9167 | 105 | 105
2020-01-21 22:30 | 90 | 90 |  |  | 43851.9375 | 100 | 100
2020-01-21 23:00 | 84 | 84 |  |  | 43851.9583 | 94 | 94
2020-01-21 23:30 | 79 | 79 |  |  | 43851.9792 | 89 | 89
2020-01-22 | 73 | 72 |  |  | 43852 | 84 | 84
2020-01-22 00:30 | 70 | 68 |  |  | 43852.0208 | 79 | 79
2020-01-22 01:00 | 69 | 66 |  |  | 43852.0417 | 77 | 77
2020-01-22 01:30 | 68 | 64 |  |  | 43852.0625 | 74 | 74
2020-01-22 02:00 | 68 | 65 |  |  | 43852.0833 | 74 | 74
2020-01-22 02:30 | 67 | 64 |  |  | 43852.1042 | 74 | 74
2020-01-22 03:00 | 66 | 62 |  |  | 43852.125 | 72 | 72
2020-01-22 03:30 | 66 | 62 |  |  | 43852.1458 | 72 | 71
2020-01-22 04:00 | 65 | 62 |  |  | 43852.1667 | 71 | 71
2020-01-22 04:30 | 63 | 59 |  |  | 43852.1875 | 70 | 70
2020-01-22 05:00 | 65 | 61 |  |  | 43852.2083 | 72 | 71
2020-01-22 05:30 | 67 | 64 |  |  | 43852.2292 | 75 | 75
2020-01-22 06:00 | 68 | 66 |  |  | 43852.25 | 78 | 78
2020-01-22 06:30 | 69 | 67 |  |  | 43852.2708 | 82 | 82
2020-01-22 07:00 | 74 | 72 |  |  | 43852.2917 | 89 | 89
2020-01-22 07:30 | 77 | 75 |  |  | 43852.3125 | 95 | 95
2020-01-22 08:00 | 99 | 97 |  |  | 43852.3333 | 138 | 138
2020-01-22 08:30 | 105 | 103 |  |  | 43852.3542 | 146 | 146
2020-01-22 09:00 | 107 | 105 |  |  | 43852.375 | 148 | 148
2020-01-22 09:30 | 113 | 109 |  |  | 43852.3958 | 157 | 155
2020-01-22 10:00 | 114 | 110 |  |  | 43852.4167 | 158 | 156
2020-01-22 10:30 | 114 | 111 |  |  | 43852.4375 | 157 | 156
2020-01-22 11:00 | 97 | 93 |  |  | 43852.4583 | 120 | 119
2020-01-22 11:30 | 92 | 92 |  |  | 43852.4792 | 112 | 112
2020-01-22 12:00 | 96 | 96 |  |  | 43852.5 | 118 | 118
2020-01-22 12:30 | 99 | 99 |  |  | 43852.5208 | 121 | 121
2020-01-22 13:00 | 104 | 104 |  |  | 43852.5417 | 125 | 125
2020-01-22 13:30 | 108 | 107 |  |  | 43852.5625 | 128 | 127
2020-01-22 14:00 | 110 | 109 |  |  | 43852.5833 | 135 | 131
2020-01-22 14:30 | 107 | 105 |  |  | 43852.6042 | 134 | 127
2020-01-22 15:00 | 111 | 108 |  |  | 43852.625 | 139 | 132
2020-01-22 15:30 | 106 | 102 |  |  | 43852.6458 | 132 | 124
2020-01-22 16:00 | 109 | 107 |  |  | 43852.6667 | 136 | 130
2020-01-22 16:30 | 107 | 105 |  |  | 43852.6875 | 135 | 128
2020-01-22 17:00 | 107 | 104 |  |  | 43852.7083 | 137 | 129
2020-01-22 17:30 | 108 | 106 |  |  | 43852.7292 | 134 | 129
2020-01-22 18:00 | 106 | 105 |  |  | 43852.75 | 130 | 127
2020-01-22 18:30 | 103 | 101 |  |  | 43852.7708 | 123 | 120
2020-01-22 19:00 | 103 | 102 |  |  | 43852.7917 | 122 | 121
2020-01-22 19:30 | 105 | 104 |  |  | 43852.8125 | 122 | 121
2020-01-22 20:00 | 105 | 104 |  |  | 43852.8333 | 122 | 121
2020-01-22 20:30 | 104 | 104 |  |  | 43852.8542 | 122 | 121
2020-01-22 21:00 | 101 | 100 |  |  | 43852.875 | 116 | 115
2020-01-22 21:30 | 103 | 102 |  |  | 43852.8958 | 113 | 111
2020-01-22 22:00 | 105 | 103 |  |  | 43852.9167 | 115 | 113
2020-01-22 22:30 | 105 | 103 |  |  | 43852.9375 | 115 | 113
2020-01-22 23:00 | 101 | 99 |  |  | 43852.9583 | 111 | 109
2020-01-22 23:30 | 94 | 92 |  |  | 43852.9792 | 103 | 102
2020-01-23 | 88 | 86 |  |  | 43853 | 97 | 97
2020-01-23 00:30 | 88 | 85 |  |  | 43853.0208 | 96 | 95
2020-01-23 01:00 | 85 | 82 |  |  | 43853.0417 | 91 | 90
2020-01-23 01:30 | 82 | 77 |  |  | 43853.0625 | 88 | 86
2020-01-23 02:00 | 81 | 77 |  |  | 43853.0833 | 87 | 86
2020-01-23 02:30 | 80 | 75 |  |  | 43853.1042 | 86 | 84
2020-01-23 03:00 | 78 | 73 |  |  | 43853.125 | 84 | 83
2020-01-23 03:30 | 77 | 72 |  |  | 43853.1458 | 84 | 82
2020-01-23 04:00 | 73 | 68 |  |  | 43853.1667 | 81 | 79
2020-01-23 04:30 | 74 | 69 |  |  | 43853.1875 | 82 | 80
2020-01-23 05:00 | 78 | 74 |  |  | 43853.2083 | 86 | 84
2020-01-23 05:30 | 83 | 79 |  |  | 43853.2292 | 91 | 89
2020-01-23 06:00 | 85 | 81 |  |  | 43853.25 | 94 | 93
2020-01-23 06:30 | 89 | 84 |  |  | 43853.2708 | 102 | 99
2020-01-23 07:00 | 91 | 85 |  |  | 43853.2917 | 108 | 103
2020-01-23 07:30 | 99 | 93 |  |  | 43853.3125 | 117 | 112
2020-01-23 08:00 | 99 | 96 |  |  | 43853.3333 | 118 | 115
2020-01-23 08:30 | 103 | 100 |  |  | 43853.3542 | 125 | 123
2020-01-23 09:00 | 106 | 103 |  |  | 43853.375 | 130 | 128
2020-01-23 09:30 | 113 | 110 |  |  | 43853.3958 | 133 | 129
2020-01-23 10:00 | 113 | 109 |  |  | 43853.4167 | 137 | 134
2020-01-23 10:30 | 113 | 108 |  |  | 43853.4375 | 135 | 132
2020-01-23 11:00 | 107 | 102 |  |  | 43853.4583 | 133 | 129
2020-01-23 11:30 | 108 | 104 |  |  | 43853.4792 | 131 | 127
2020-01-23 12:00 | 111 | 107 |  |  | 43853.5 | 130 | 126
2020-01-23 12:30 | 99 | 93 |  |  | 43853.5208 | 121 | 116
2020-01-23 13:00 | 90 | 83 |  |  | 43853.5417 | 110 | 106
2020-01-23 13:30 | 85 | 78 |  |  | 43853.5625 | 106 | 102
2020-01-23 14:00 | 93 | 87 |  |  | 43853.5833 | 115 | 111
2020-01-23 14:30 | 93 | 89 |  |  | 43853.6042 | 114 | 110
2020-01-23 15:00 | 92 | 90 |  |  | 43853.625 | 112 | 108
2020-01-23 15:30 | 99 | 97 |  |  | 43853.6458 | 116 | 112
2020-01-23 16:00 | 100 | 98 |  |  | 43853.6667 | 118 | 114
2020-01-23 16:30 | 99 | 97 |  |  | 43853.6875 | 118 | 114
2020-01-23 17:00 | 97 | 94 |  |  | 43853.7083 | 113 | 108
2020-01-23 17:30 | 101 | 97 |  |  | 43853.7292 | 115 | 110
2020-01-23 18:00 | 103 | 101 |  |  | 43853.75 | 113 | 110
2020-01-23 18:30 | 96 | 94 |  |  | 43853.7708 | 109 | 106
2020-01-23 19:00 | 93 | 92 |  |  | 43853.7917 | 111 | 108
2020-01-23 19:30 | 95 | 94 |  |  | 43853.8125 | 113 | 111
2020-01-23 20:00 | 94 | 93 |  |  | 43853.8333 | 112 | 109
2020-01-23 20:30 | 93 | 92 |  |  | 43853.8542 | 111 | 108
2020-01-23 21:00 | 90 | 89 |  |  | 43853.875 | 107 | 103
2020-01-23 21:30 | 97 | 93 |  |  | 43853.8958 | 107 | 102
2020-01-23 22:00 | 93 | 91 |  |  | 43853.9167 | 103 | 101
2020-01-23 22:30 | 94 | 91 |  |  | 43853.9375 | 104 | 101
2020-01-23 23:00 | 90 | 87 |  |  | 43853.9583 | 98 | 96
2020-01-23 23:30 | 81 | 79 |  |  | 43853.9792 | 91 | 90
2020-01-24 | 76 | 73 |  |  | 43854 | 84 | 83
2020-01-24 00:30 | 75 | 70 |  |  | 43854.0208 | 80 | 79
2020-01-24 01:00 | 75 | 69 |  |  | 43854.0417 | 79 | 77
2020-01-24 01:30 | 74 | 67 |  |  | 43854.0625 | 78 | 76
2020-01-24 02:00 | 74 | 66 |  |  | 43854.0833 | 76 | 74
2020-01-24 02:30 | 72 | 64 |  |  | 43854.1042 | 75 | 73
2020-01-24 03:00 | 70 | 62 |  |  | 43854.125 | 73 | 71
2020-01-24 03:30 | 68 | 60 |  |  | 43854.1458 | 70 | 69
2020-01-24 04:00 | 67 | 58 |  |  | 43854.1667 | 69 | 68
2020-01-24 04:30 | 67 | 59 |  |  | 43854.1875 | 70 | 69
2020-01-24 05:00 | 70 | 62 |  |  | 43854.2083 | 73 | 72
2020-01-24 05:30 | 71 | 64 |  |  | 43854.2292 | 76 | 75
2020-01-24 06:00 | 72 | 65 |  |  | 43854.25 | 79 | 77
2020-01-24 06:30 | 73 | 68 |  |  | 43854.2708 | 84 | 84
2020-01-24 07:00 | 76 | 72 |  |  | 43854.2917 | 92 | 91
2020-01-24 07:30 | 81 | 75 |  |  | 43854.3125 | 100 | 97
2020-01-24 08:00 | 84 | 78 |  |  | 43854.3333 | 104 | 101
2020-01-24 08:30 | 87 | 82 |  |  | 43854.3542 | 108 | 107
2020-01-24 09:00 | 94 | 90 |  |  | 43854.375 | 119 | 117
2020-01-24 09:30 | 102 | 99 |  |  | 43854.3958 | 127 | 125
2020-01-24 10:00 | 109 | 105 |  |  | 43854.4167 | 133 | 130
2020-01-24 10:30 | 112 | 107 |  |  | 43854.4375 | 136 | 131
2020-01-24 11:00 | 114 | 107 |  |  | 43854.4583 | 139 | 133
2020-01-24 11:30 | 113 | 107 |  |  | 43854.4792 | 141 | 135
2020-01-24 12:00 | 112 | 106 |  |  | 43854.5 | 136 | 129
2020-01-24 12:30 | 107 | 99 |  |  | 43854.5208 | 132 | 124
2020-01-24 13:00 | 115 | 109 |  |  | 43854.5417 | 140 | 133
2020-01-24 13:30 | 120 | 109 |  |  | 43854.5625 | 152 | 135
2020-01-24 14:00 | 113 | 102 |  |  | 43854.5833 | 150 | 130
2020-01-24 14:30 | 116 | 104 |  |  | 43854.6042 | 149 | 132
2020-01-24 15:00 | 114 | 99 |  |  | 43854.625 | 143 | 132
2020-01-24 15:30 | 118 | 104 |  |  | 43854.6458 | 146 | 134
2020-01-24 16:00 | 116 | 102 |  |  | 43854.6667 | 144 | 132
2020-01-24 16:30 | 116 | 102 |  |  | 43854.6875 | 144 | 131
2020-01-24 17:00 | 118 | 105 |  |  | 43854.7083 | 146 | 134
2020-01-24 17:30 | 105 | 99 |  |  | 43854.7292 | 144 | 126
2020-01-24 18:00 | 100 | 96 |  |  | 43854.75 | 146 | 119
2020-01-24 18:30 | 90 | 90 |  |  | 43854.7708 | 139 | 110
2020-01-24 19:00 | 90 | 90 |  |  | 43854.7917 | 124 | 110
2020-01-24 19:30 | 89 | 88 |  |  | 43854.8125 | 123 | 109
2020-01-24 20:00 | 87 | 87 |  |  | 43854.8333 | 121 | 107
2020-01-24 20:30 | 86 | 86 |  |  | 43854.8542 | 122 | 106
2020-01-24 21:00 | 85 | 84 |  |  | 43854.875 | 120 | 103
2020-01-24 21:30 | 92 | 91 |  |  | 43854.8958 | 121 | 104
2020-01-24 22:00 | 90 | 88 |  |  | 43854.9167 | 120 | 102
2020-01-24 22:30 | 90 | 87 |  |  | 43854.9375 | 121 | 102
2020-01-24 23:00 | 88 | 85 |  |  | 43854.9583 | 117 | 96
2020-01-24 23:30 | 81 | 80 |  |  | 43854.9792 | 105 | 92
2020-01-25 | 75 | 75 |  |  | 43855 | 97 | 86
2020-01-25 00:30 | 72 | 71 |  |  | 43855.0208 | 94 | 83
2020-01-25 01:00 | 71 | 69 |  |  | 43855.0417 | 93 | 79
2020-01-25 01:30 | 68 | 66 |  |  | 43855.0625 | 91 | 77
2020-01-25 02:00 | 66 | 64 |  |  | 43855.0833 | 90 | 74
2020-01-25 02:30 | 65 | 63 |  |  | 43855.1042 | 88 | 72
2020-01-25 03:00 | 66 | 63 |  |  | 43855.125 | 89 | 72
2020-01-25 03:30 | 66 | 63 |  |  | 43855.1458 | 87 | 73
2020-01-25 04:00 | 64 | 61 |  |  | 43855.1667 | 87 | 72
2020-01-25 04:30 | 63 | 61 |  |  | 43855.1875 | 86 | 72
2020-01-25 05:00 | 62 | 59 |  |  | 43855.2083 | 85 | 69
2020-01-25 05:30 | 60 | 58 |  |  | 43855.2292 | 83 | 69
2020-01-25 06:00 | 62 | 60 |  |  | 43855.25 | 84 | 71
2020-01-25 06:30 | 61 | 59 |  |  | 43855.2708 | 84 | 72
2020-01-25 07:00 | 61 | 60 |  |  | 43855.2917 | 85 | 74
2020-01-25 07:30 | 64 | 63 |  |  | 43855.3125 | 90 | 80
2020-01-25 08:00 | 68 | 68 |  |  | 43855.3333 | 91 | 85
2020-01-25 08:30 | 72 | 72 |  |  | 43855.3542 | 95 | 90
2020-01-25 09:00 | 76 | 76 |  |  | 43855.375 | 104 | 97
2020-01-25 09:30 | 81 | 81 |  |  | 43855.3958 | 111 | 103
2020-01-25 10:00 | 79 | 78 |  |  | 43855.4167 | 114 | 96
2020-01-25 10:30 | 75 | 74 |  |  | 43855.4375 | 110 | 91
2020-01-25 11:00 | 74 | 73 |  |  | 43855.4583 | 104 | 83
2020-01-25 11:30 | 72 | 71 |  |  | 43855.4792 | 99 | 77
2020-01-25 12:00 | 67 | 66 |  |  | 43855.5 | 99 | 78
2020-01-25 12:30 | 65 | 64 |  |  | 43855.5208 | 97 | 77
2020-01-25 13:00 | 80 | 79 |  |  | 43855.5417 | 106 | 87
2020-01-25 13:30 | 88 | 88 |  |  | 43855.5625 | 114 | 95
2020-01-25 14:00 | 91 | 91 |  |  | 43855.5833 | 119 | 99
2020-01-25 14:30 | 90 | 89 |  |  | 43855.6042 | 119 | 100
2020-01-25 15:00 | 87 | 86 |  |  | 43855.625 | 117 | 98
2020-01-25 15:30 | 85 | 85 |  |  | 43855.6458 | 111 | 97
2020-01-25 16:00 | 85 | 85 |  |  | 43855.6667 | 111 | 99
2020-01-25 16:30 | 87 | 86 |  |  | 43855.6875 | 113 | 100
2020-01-25 17:00 | 86 | 85 |  |  | 43855.7083 | 112 | 99
2020-01-25 17:30 | 83 | 82 |  |  | 43855.7292 | 110 | 96
2020-01-25 18:00 | 84 | 83 |  |  | 43855.75 | 111 | 97
2020-01-25 18:30 | 83 | 82 |  |  | 43855.7708 | 112 | 97
2020-01-25 19:00 | 86 | 85 |  |  | 43855.7917 | 115 | 100
2020-01-25 19:30 | 87 | 86 |  |  | 43855.8125 | 115 | 101
2020-01-25 20:00 | 87 | 86 |  |  | 43855.8333 | 113 | 101
2020-01-25 20:30 | 85 | 84 |  |  | 43855.8542 | 112 | 99
2020-01-25 21:00 | 80 | 80 |  |  | 43855.875 | 106 | 95
2020-01-25 21:30 | 78 | 76 |  |  | 43855.8958 | 103 | 90
2020-01-25 22:00 | 77 | 74 |  |  | 43855.9167 | 103 | 89
2020-01-25 22:30 | 76 | 73 |  |  | 43855.9375 | 102 | 89
2020-01-25 23:00 | 75 | 73 |  |  | 43855.9583 | 97 | 87
2020-01-25 23:30 | 71 | 69 |  |  | 43855.9792 | 93 | 83
2020-01-26 | 67 | 64 |  |  | 43856 | 90 | 78
2020-01-26 00:30 | 66 | 63 |  |  | 43856.0208 | 88 | 75
2020-01-26 01:00 | 63 | 60 |  |  | 43856.0417 | 87 | 71
2020-01-26 01:30 | 61 | 57 |  |  | 43856.0625 | 85 | 68
2020-01-26 02:00 | 58 | 54 |  |  | 43856.0833 | 82 | 64
2020-01-26 02:30 | 58 | 53 |  |  | 43856.1042 | 83 | 64
2020-01-26 03:00 | 58 | 54 |  |  | 43856.125 | 84 | 64
2020-01-26 03:30 | 57 | 52 |  |  | 43856.1458 | 83 | 63
2020-01-26 04:00 | 58 | 53 |  |  | 43856.1667 | 82 | 62
2020-01-26 04:30 | 58 | 53 |  |  | 43856.1875 | 82 | 62
2020-01-26 05:00 | 58 | 53 |  |  | 43856.2083 | 82 | 62
2020-01-26 05:30 | 56 | 51 |  |  | 43856.2292 | 81 | 60
2020-01-26 06:00 | 57 | 51 |  |  | 43856.25 | 82 | 61
2020-01-26 06:30 | 54 | 48 |  |  | 43856.2708 | 81 | 60
2020-01-26 07:00 | 53 | 47 |  |  | 43856.2917 | 80 | 60
2020-01-26 07:30 | 52 | 48 |  |  | 43856.3125 | 80 | 62
2020-01-26 08:00 | 54 | 50 |  |  | 43856.3333 | 79 | 62
2020-01-26 08:30 | 54 | 52 |  |  | 43856.3542 | 79 | 65
2020-01-26 09:00 | 59 | 57 |  |  | 43856.375 | 82 | 68
2020-01-26 09:30 | 61 | 60 |  |  | 43856.3958 | 85 | 73
2020-01-26 10:00 | 58 | 57 |  |  | 43856.4167 | 82 | 71
2020-01-26 10:30 | 58 | 57 |  |  | 43856.4375 | 78 | 67
2020-01-26 11:00 | 57 | 56 |  |  | 43856.4583 | 76 | 65
2020-01-26 11:30 | 56 | 53 |  |  | 43856.4792 | 71 | 64
2020-01-26 12:00 | 61 | 55 |  |  | 43856.5 | 77 | 68
2020-01-26 12:30 | 63 | 56 |  |  | 43856.5208 | 77 | 66
2020-01-26 13:00 | 62 | 55 |  |  | 43856.5417 | 77 | 65
2020-01-26 13:30 | 64 | 56 |  |  | 43856.5625 | 81 | 70
2020-01-26 14:00 | 67 | 59 |  |  | 43856.5833 | 81 | 71
2020-01-26 14:30 | 67 | 60 |  |  | 43856.6042 | 80 | 68
2020-01-26 15:00 | 66 | 58 |  |  | 43856.625 | 80 | 68
2020-01-26 15:30 | 70 | 64 |  |  | 43856.6458 | 83 | 72
2020-01-26 16:00 | 72 | 66 |  |  | 43856.6667 | 86 | 75
2020-01-26 16:30 | 75 | 69 |  |  | 43856.6875 | 90 | 79
2020-01-26 17:00 | 77 | 72 |  |  | 43856.7083 | 93 | 82
2020-01-26 17:30 | 81 | 75 |  |  | 43856.7292 | 96 | 85
2020-01-26 18:00 | 83 | 77 |  |  | 43856.75 | 99 | 87
2020-01-26 18:30 | 84 | 78 |  |  | 43856.7708 | 101 | 89
2020-01-26 19:00 | 86 | 80 |  |  | 43856.7917 | 103 | 92
2020-01-26 19:30 | 86 | 80 |  |  | 43856.8125 | 104 | 93
2020-01-26 20:00 | 86 | 80 |  |  | 43856.8333 | 104 | 93
2020-01-26 20:30 | 86 | 79 |  |  | 43856.8542 | 103 | 92
2020-01-26 21:00 | 84 | 78 |  |  | 43856.875 | 102 | 91
2020-01-26 21:30 | 83 | 78 |  |  | 43856.8958 | 101 | 92
2020-01-26 22:00 | 82 | 76 |  |  | 43856.9167 | 101 | 91
2020-01-26 22:30 | 82 | 76 |  |  | 43856.9375 | 101 | 90
2020-01-26 23:00 | 78 | 72 |  |  | 43856.9583 | 95 | 86
2020-01-26 23:30 | 74 | 67 |  |  | 43856.9792 | 91 | 82
2020-01-27 | 72 | 63 |  |  | 43857 | 88 | 77
2020-01-27 00:30 | 70 | 60 |  |  | 43857.0208 | 85 | 73
2020-01-27 01:00 | 68 | 57 |  |  | 43857.0417 | 82 | 68
2020-01-27 01:30 | 67 | 56 |  |  | 43857.0625 | 80 | 66
2020-01-27 02:00 | 64 | 53 |  |  | 43857.0833 | 79 | 64
2020-01-27 02:30 | 63 | 51 |  |  | 43857.1042 | 78 | 62
2020-01-27 03:00 | 63 | 50 |  |  | 43857.125 | 78 | 61
2020-01-27 03:30 | 63 | 50 |  |  | 43857.1458 | 77 | 61
2020-01-27 04:00 | 62 | 49 |  |  | 43857.1667 | 76 | 60
2020-01-27 04:30 | 63 | 50 |  |  | 43857.1875 | 78 | 61
2020-01-27 05:00 | 62 | 49 |  |  | 43857.2083 | 77 | 61
2020-01-27 05:30 | 61 | 47 |  |  | 43857.2292 | 76 | 60
2020-01-27 06:00 | 61 | 46 |  |  | 43857.25 | 76 | 60
2020-01-27 06:30 | 60 | 47 |  |  | 43857.2708 | 78 | 63
2020-01-27 07:00 | 60 | 48 |  |  | 43857.2917 | 79 | 66
2020-01-27 07:30 | 63 | 51 |  |  | 43857.3125 | 84 | 71
2020-01-27 08:00 | 66 | 53 |  |  | 43857.3333 | 89 | 74
2020-01-27 08:30 | 67 | 54 |  |  | 43857.3542 | 90 | 74
2020-01-27 09:00 | 69 | 56 |  |  | 43857.375 | 93 | 75
2020-01-27 09:30 | 71 | 57 |  |  | 43857.3958 | 95 | 77
2020-01-27 10:00 | 73 | 60 |  |  | 43857.4167 | 94 | 75
2020-01-27 10:30 | 71 | 59 |  |  | 43857.4375 | 91 | 72
2020-01-27 11:00 | 69 | 57 |  |  | 43857.4583 | 89 | 71
2020-01-27 11:30 | 71 | 60 |  |  | 43857.4792 | 89 | 71
2020-01-27 12:00 | 72 | 61 |  |  | 43857.5 | 89 | 71
2020-01-27 12:30 | 68 | 64 |  |  | 43857.5208 | 89 | 76
2020-01-27 13:00 | 70 | 65 |  |  | 43857.5417 | 89 | 76
2020-01-27 13:30 | 74 | 70 |  |  | 43857.5625 | 96 | 84
2020-01-27 14:00 | 78 | 73 |  |  | 43857.5833 | 101 | 86
2020-01-27 14:30 | 79 | 74 |  |  | 43857.6042 | 104 | 88
2020-01-27 15:00 | 80 | 74 |  |  | 43857.625 | 103 | 87
2020-01-27 15:30 | 82 | 76 |  |  | 43857.6458 | 104 | 88
2020-01-27 16:00 | 83 | 76 |  |  | 43857.6667 | 105 | 87
2020-01-27 16:30 | 86 | 81 |  |  | 43857.6875 | 108 | 92
2020-01-27 17:00 | 88 | 81 |  |  | 43857.7083 | 110 | 93
2020-01-27 17:30 | 90 | 83 |  |  | 43857.7292 | 113 | 96
2020-01-27 18:00 | 89 | 83 |  |  | 43857.75 | 113 | 94
2020-01-27 18:30 | 89 | 82 |  |  | 43857.7708 | 114 | 94
2020-01-27 19:00 | 91 | 83 |  |  | 43857.7917 | 116 | 97
2020-01-27 19:30 | 90 | 83 |  |  | 43857.8125 | 116 | 97
2020-01-27 20:00 | 87 | 83 |  |  | 43857.8333 | 110 | 98
2020-01-27 20:30 | 86 | 82 |  |  | 43857.8542 | 107 | 97
2020-01-27 21:00 | 81 | 78 |  |  | 43857.875 | 101 | 94
2020-01-27 21:30 | 77 | 74 |  |  | 43857.8958 | 96 | 89
2020-01-27 22:00 | 72 | 70 |  |  | 43857.9167 | 92 | 86
2020-01-27 22:30 | 70 | 68 |  |  | 43857.9375 | 90 | 86
2020-01-27 23:00 | 68 | 66 |  |  | 43857.9583 | 87 | 82
2020-01-27 23:30 | 64 | 62 |  |  | 43857.9792 | 83 | 78
2020-01-28 | 60 | 58 |  |  | 43858 | 79 | 75
2020-01-28 00:30 | 58 | 56 |  |  | 43858.0208 | 75 | 70
2020-01-28 01:00 | 56 | 53 |  |  | 43858.0417 | 73 | 67
2020-01-28 01:30 | 55 | 52 |  |  | 43858.0625 | 72 | 66
2020-01-28 02:00 | 55 | 52 |  |  | 43858.0833 | 72 | 66
2020-01-28 02:30 | 55 | 52 |  |  | 43858.1042 | 71 | 65
2020-01-28 03:00 | 54 | 51 |  |  | 43858.125 | 71 | 64
2020-01-28 03:30 | 55 | 51 |  |  | 43858.1458 | 71 | 64
2020-01-28 04:00 | 54 | 50 |  |  | 43858.1667 | 70 | 62
2020-01-28 04:30 | 54 | 51 |  |  | 43858.1875 | 71 | 64
2020-01-28 05:00 | 55 | 52 |  |  | 43858.2083 | 72 | 65
2020-01-28 05:30 | 60 | 57 |  |  | 43858.2292 | 78 | 72
2020-01-28 06:00 | 61 | 59 |  |  | 43858.25 | 81 | 75
2020-01-28 06:30 | 69 | 67 |  |  | 43858.2708 | 92 | 85
2020-01-28 07:00 | 72 | 70 |  |  | 43858.2917 | 99 | 92
2020-01-28 07:30 | 79 | 77 |  |  | 43858.3125 | 109 | 103
2020-01-28 08:00 | 84 | 83 |  |  | 43858.3333 | 114 | 108
2020-01-28 08:30 | 86 | 84 |  |  | 43858.3542 | 111 | 105
2020-01-28 09:00 | 83 | 82 |  |  | 43858.375 | 111 | 105
2020-01-28 09:30 | 86 | 84 |  |  | 43858.3958 | 115 | 110
2020-01-28 10:00 | 87 | 86 |  |  | 43858.4167 | 112 | 106
2020-01-28 10:30 | 87 | 86 |  |  | 43858.4375 | 115 | 110
2020-01-28 11:00 | 87 | 86 |  |  | 43858.4583 | 113 | 108
2020-01-28 11:30 | 85 | 84 |  |  | 43858.4792 | 108 | 103
2020-01-28 12:00 | 81 | 80 |  |  | 43858.5 | 109 | 106
2020-01-28 12:30 | 85 | 83 |  |  | 43858.5208 | 113 | 112
2020-01-28 13:00 | 87 | 84 |  |  | 43858.5417 | 113 | 111
2020-01-28 13:30 | 89 | 87 |  |  | 43858.5625 | 107 | 105
2020-01-28 14:00 | 85 | 82 |  |  | 43858.5833 | 109 | 108
2020-01-28 14:30 | 84 | 81 |  |  | 43858.6042 | 110 | 109
2020-01-28 15:00 | 84 | 80 |  |  | 43858.625 | 109 | 108
2020-01-28 15:30 | 88 | 84 |  |  | 43858.6458 | 110 | 109
2020-01-28 16:00 | 92 | 89 |  |  | 43858.6667 | 114 | 113
2020-01-28 16:30 | 95 | 92 |  |  | 43858.6875 | 117 | 115
2020-01-28 17:00 | 98 | 96 |  |  | 43858.7083 | 118 | 117
2020-01-28 17:30 | 99 | 97 |  |  | 43858.7292 | 118 | 117
2020-01-28 18:00 | 96 | 96 |  |  | 43858.75 | 114 | 113
2020-01-28 18:30 | 94 | 93 |  |  | 43858.7708 | 109 | 108
2020-01-28 19:00 | 97 | 96 |  |  | 43858.7917 | 113 | 112
2020-01-28 19:30 | 99 | 98 |  |  | 43858.8125 | 114 | 113
2020-01-28 20:00 | 97 | 97 |  |  | 43858.8333 | 112 | 112
2020-01-28 20:30 | 96 | 96 |  |  | 43858.8542 | 111 | 111
2020-01-28 21:00 | 94 | 93 |  |  | 43858.875 | 108 | 108
2020-01-28 21:30 | 89 | 88 |  |  | 43858.8958 | 102 | 101
2020-01-28 22:00 | 84 | 83 |  |  | 43858.9167 | 97 | 97
2020-01-28 22:30 | 81 | 80 |  |  | 43858.9375 | 93 | 93
2020-01-28 23:00 | 79 | 77 |  |  | 43858.9583 | 90 | 89
2020-01-28 23:30 | 71 | 69 |  |  | 43858.9792 | 83 | 82
2020-01-29 | 63 | 61 |  |  | 43859 | 75 | 74
2020-01-29 00:30 | 64 | 60 |  |  | 43859.0208 | 74 | 72
2020-01-29 01:00 | 66 | 60 |  |  | 43859.0417 | 73 | 71
2020-01-29 01:30 | 66 | 61 |  |  | 43859.0625 | 72 | 70
2020-01-29 02:00 | 65 | 60 |  |  | 43859.0833 | 70 | 68
2020-01-29 02:30 | 64 | 58 |  |  | 43859.1042 | 68 | 67
2020-01-29 03:00 | 63 | 57 |  |  | 43859.125 | 67 | 66
2020-01-29 03:30 | 62 | 56 |  |  | 43859.1458 | 66 | 65
2020-01-29 04:00 | 61 | 55 |  |  | 43859.1667 | 66 | 65
2020-01-29 04:30 | 61 | 55 |  |  | 43859.1875 | 67 | 66
2020-01-29 05:00 | 64 | 59 |  |  | 43859.2083 | 69 | 68
2020-01-29 05:30 | 67 | 62 |  |  | 43859.2292 | 73 | 72
2020-01-29 06:00 | 66 | 61 |  |  | 43859.25 | 74 | 73
2020-01-29 06:30 | 73 | 70 |  |  | 43859.2708 | 86 | 85
2020-01-29 07:00 | 78 | 76 |  |  | 43859.2917 | 95 | 95
2020-01-29 07:30 | 87 | 84 |  |  | 43859.3125 | 106 | 105
2020-01-29 08:00 | 89 | 86 |  |  | 43859.3333 | 109 | 109
2020-01-29 08:30 | 88 | 85 |  |  | 43859.3542 | 110 | 110
2020-01-29 09:00 | 88 | 86 |  |  | 43859.375 | 110 | 110
2020-01-29 09:30 | 92 | 90 |  |  | 43859.3958 | 114 | 113
2020-01-29 10:00 | 93 | 91 |  |  | 43859.4167 | 115 | 114
2020-01-29 10:30 | 96 | 91 |  |  | 43859.4375 | 119 | 114
2020-01-29 11:00 | 97 | 90 |  |  | 43859.4583 | 119 | 114
2020-01-29 11:30 | 94 | 90 |  |  | 43859.4792 | 119 | 114
2020-01-29 12:00 | 93 | 90 |  |  | 43859.5 | 118 | 115
2020-01-29 12:30 | 92 | 90 |  |  | 43859.5208 | 118 | 115
2020-01-29 13:00 | 93 | 91 |  |  | 43859.5417 | 118 | 115
2020-01-29 13:30 | 97 | 95 |  |  | 43859.5625 | 122 | 119
2020-01-29 14:00 | 104 | 101 |  |  | 43859.5833 | 126 | 120
2020-01-29 14:30 | 101 | 98 |  |  | 43859.6042 | 123 | 118
2020-01-29 15:00 | 97 | 94 |  |  | 43859.625 | 122 | 117
2020-01-29 15:30 | 101 | 97 |  |  | 43859.6458 | 125 | 120
2020-01-29 16:00 | 109 | 108 |  |  | 43859.6667 | 134 | 129
2020-01-29 16:30 | 110 | 110 |  |  | 43859.6875 | 135 | 131
2020-01-29 17:00 | 117 | 115 |  |  | 43859.7083 | 140 | 137
2020-01-29 17:30 | 123 | 117 |  |  | 43859.7292 | 139 | 138
2020-01-29 18:00 | 118 | 115 |  |  | 43859.75 | 135 | 133
2020-01-29 18:30 | 111 | 109 |  |  | 43859.7708 | 126 | 125
2020-01-29 19:00 | 111 | 109 |  |  | 43859.7917 | 128 | 126
2020-01-29 19:30 | 110 | 108 |  |  | 43859.8125 | 127 | 125
2020-01-29 20:00 | 111 | 107 |  |  | 43859.8333 | 126 | 124
2020-01-29 20:30 | 108 | 105 |  |  | 43859.8542 | 122 | 121
2020-01-29 21:00 | 108 | 101 |  |  | 43859.875 | 118 | 116
2020-01-29 21:30 | 101 | 94 |  |  | 43859.8958 | 109 | 108
2020-01-29 22:00 | 96 | 90 |  |  | 43859.9167 | 105 | 104
2020-01-29 22:30 | 92 | 87 |  |  | 43859.9375 | 101 | 101
2020-01-29 23:00 | 91 | 85 |  |  | 43859.9583 | 97 | 97
2020-01-29 23:30 | 86 | 78 |  |  | 43859.9792 | 91 | 91
2020-01-30 | 84 | 71 |  |  | 43860 | 85 | 84
2020-01-30 00:30 | 81 | 68 |  |  | 43860.0208 | 79 | 79
2020-01-30 01:00 | 79 | 66 |  |  | 43860.0417 | 76 | 76
2020-01-30 01:30 | 69 | 65 |  |  | 43860.0625 | 77 | 74
2020-01-30 02:00 | 69 | 65 |  |  | 43860.0833 | 77 | 73
2020-01-30 02:30 | 67 | 64 |  |  | 43860.1042 | 76 | 72
2020-01-30 03:00 | 66 | 63 |  |  | 43860.125 | 75 | 71
2020-01-30 03:30 | 65 | 60 |  |  | 43860.1458 | 73 | 69
2020-01-30 04:00 | 64 | 60 |  |  | 43860.1667 | 73 | 69
2020-01-30 04:30 | 65 | 61 |  |  | 43860.1875 | 75 | 70
2020-01-30 05:00 | 67 | 63 |  |  | 43860.2083 | 77 | 73
2020-01-30 05:30 | 68 | 64 |  |  | 43860.2292 | 80 | 76
2020-01-30 06:00 | 70 | 66 |  |  | 43860.25 | 83 | 79
2020-01-30 06:30 | 73 | 71 |  |  | 43860.2708 | 90 | 87
2020-01-30 07:00 | 77 | 76 |  |  | 43860.2917 | 96 | 94
2020-01-30 07:30 | 88 | 86 |  |  | 43860.3125 | 102 | 96
2020-01-30 08:00 | 91 | 90 |  |  | 43860.3333 | 102 | 97
2020-01-30 08:30 | 89 | 89 |  |  | 43860.3542 | 101 | 97
2020-01-30 09:00 | 89 | 88 |  |  | 43860.375 | 103 | 99
2020-01-30 09:30 | 94 | 93 |  |  | 43860.3958 | 108 | 105
2020-01-30 10:00 | 99 | 97 |  |  | 43860.4167 | 110 | 107
2020-01-30 10:30 | 101 | 96 |  |  | 43860.4375 | 108 | 104
2020-01-30 11:00 | 101 | 98 |  |  | 43860.4583 | 108 | 103
2020-01-30 11:30 | 99 | 97 |  |  | 43860.4792 | 110 | 106
2020-01-30 12:00 | 99 | 97 |  |  | 43860.5 | 110 | 107
2020-01-30 12:30 | 94 | 92 |  |  | 43860.5208 | 104 | 100
2020-01-30 13:00 | 95 | 93 |  |  | 43860.5417 | 103 | 99
2020-01-30 13:30 | 94 | 91 |  |  | 43860.5625 | 103 | 99
2020-01-30 14:00 | 92 | 89 |  |  | 43860.5833 | 107 | 102
2020-01-30 14:30 | 91 | 89 |  |  | 43860.6042 | 107 | 102
2020-01-30 15:00 | 92 | 90 |  |  | 43860.625 | 107 | 103
2020-01-30 15:30 | 97 | 96 |  |  | 43860.6458 | 108 | 104
2020-01-30 16:00 | 103 | 103 |  |  | 43860.6667 | 113 | 110
2020-01-30 16:30 | 103 | 102 |  |  | 43860.6875 | 115 | 111
2020-01-30 17:00 | 106 | 105 |  |  | 43860.7083 | 116 | 112
2020-01-30 17:30 | 105 | 104 |  |  | 43860.7292 | 115 | 113
2020-01-30 18:00 | 100 | 99 |  |  | 43860.75 | 113 | 111
2020-01-30 18:30 | 98 | 98 |  |  | 43860.7708 | 109 | 108
2020-01-30 19:00 | 99 | 99 |  |  | 43860.7917 | 110 | 109
2020-01-30 19:30 | 103 | 103 |  |  | 43860.8125 | 111 | 110
2020-01-30 20:00 | 98 | 98 |  |  | 43860.8333 | 106 | 105
2020-01-30 20:30 | 96 | 96 |  |  | 43860.8542 | 102 | 102
2020-01-30 21:00 | 98 | 98 |  |  | 43860.875 | 98 | 98
2020-01-30 21:30 | 91 | 91 |  |  | 43860.8958 | 100 | 100
2020-01-30 22:00 | 87 | 87 |  |  | 43860.9167 | 100 | 100
2020-01-30 22:30 | 83 | 81 |  |  | 43860.9375 | 92 | 92
2020-01-30 23:00 | 79 | 77 |  |  | 43860.9583 | 87 | 87
2020-01-30 23:30 | 73 | 71 |  |  | 43860.9792 | 82 | 82
2020-01-31 | 69 | 64 |  |  | 43861 | 76 | 75
2020-01-31 00:30 | 71 | 62 |  |  | 43861.0208 | 74 | 73
2020-01-31 01:00 | 70 | 61 |  |  | 43861.0417 | 71 | 69
2020-01-31 01:30 | 69 | 59 |  |  | 43861.0625 | 70 | 69
2020-01-31 02:00 | 71 | 61 |  |  | 43861.0833 | 72 | 70
2020-01-31 02:30 | 70 | 60 |  |  | 43861.1042 | 71 | 69
2020-01-31 03:00 | 69 | 59 |  |  | 43861.125 | 71 | 69
2020-01-31 03:30 | 68 | 59 |  |  | 43861.1458 | 71 | 69
2020-01-31 04:00 | 68 | 59 |  |  | 43861.1667 | 71 | 68
2020-01-31 04:30 | 67 | 58 |  |  | 43861.1875 | 70 | 68
2020-01-31 05:00 | 69 | 61 |  |  | 43861.2083 | 73 | 70
2020-01-31 05:30 | 71 | 63 |  |  | 43861.2292 | 75 | 73
2020-01-31 06:00 | 72 | 65 |  |  | 43861.25 | 78 | 76
2020-01-31 06:30 | 71 | 66 |  |  | 43861.2708 | 82 | 81
2020-01-31 07:00 | 70 | 66 |  |  | 43861.2917 | 85 | 84
2020-01-31 07:30 | 81 | 79 |  |  | 43861.3125 | 90 | 89
2020-01-31 08:00 | 84 | 80 |  |  | 43861.3333 | 96 | 94
2020-01-31 08:30 | 83 | 80 |  |  | 43861.3542 | 97 | 95
2020-01-31 09:00 | 85 | 82 |  |  | 43861.375 | 97 | 95
2020-01-31 09:30 | 85 | 81 |  |  | 43861.3958 | 98 | 96
2020-01-31 10:00 | 84 | 80 |  |  | 43861.4167 | 102 | 100
2020-01-31 10:30 | 92 | 89 |  |  | 43861.4375 | 106 | 105
2020-01-31 11:00 | 94 | 91 |  |  | 43861.4583 | 105 | 103
2020-01-31 11:30 | 93 | 90 |  |  | 43861.4792 | 103 | 101
2020-01-31 12:00 | 90 | 87 |  |  | 43861.5 | 101 | 100
2020-01-31 12:30 | 89 | 85 |  |  | 43861.5208 | 101 | 99
2020-01-31 13:00 | 92 | 88 |  |  | 43861.5417 | 100 | 98
2020-01-31 13:30 | 90 | 86 |  |  | 43861.5625 | 96 | 93
2020-01-31 14:00 | 83 | 79 |  |  | 43861.5833 | 96 | 94
2020-01-31 14:30 | 89 | 85 |  |  | 43861.6042 | 108 | 106
2020-01-31 15:00 | 89 | 84 |  |  | 43861.625 | 104 | 102
2020-01-31 15:30 | 86 | 81 |  |  | 43861.6458 | 103 | 101
2020-01-31 16:00 | 91 | 86 |  |  | 43861.6667 | 112 | 110
2020-01-31 16:30 | 93 | 87 |  |  | 43861.6875 | 115 | 113
2020-01-31 17:00 | 90 | 82 |  |  | 43861.7083 | 117 | 111
2020-01-31 17:30 | 94 | 84 |  |  | 43861.7292 | 121 | 111
2020-01-31 18:00 | 92 | 81 |  |  | 43861.75 | 117 | 106
2020-01-31 18:30 | 88 | 79 |  |  | 43861.7708 | 110 | 103
2020-01-31 19:00 | 90 | 83 |  |  | 43861.7917 | 113 | 109
2020-01-31 19:30 | 96 | 90 |  |  | 43861.8125 | 118 | 114
2020-01-31 20:00 | 94 | 89 |  |  | 43861.8333 | 115 | 110
2020-01-31 20:30 | 91 | 85 |  |  | 43861.8542 | 110 | 104
2020-01-31 21:00 | 92 | 85 |  |  | 43861.875 | 108 | 101
2020-01-31 21:30 | 83 | 80 |  |  | 43861.8958 | 95 | 94
2020-01-31 22:00 | 83 | 80 |  |  | 43861.9167 | 95 | 94
2020-01-31 22:30 | 82 | 78 |  |  | 43861.9375 | 96 | 95
2020-01-31 23:00 | 81 | 77 |  |  | 43861.9583 | 93 | 92
2020-01-31 23:30 | 76 | 72 |  |  | 43861.9792 | 87 | 86
2020-02-01 | 72 | 67 |  |  | 43862 | 82 | 81
2020-02-01 00:30 | 72 | 64 |  |  | 43862.0208 | 79 | 78
2020-02-01 01:00 | 75 | 63 |  |  | 43862.0417 | 79 | 75
2020-02-01 01:30 | 75 | 62 |  |  | 43862.0625 | 78 | 74
2020-02-01 02:00 | 72 | 59 |  |  | 43862.0833 | 75 | 70
2020-02-01 02:30 | 69 | 54 |  |  | 43862.1042 | 71 | 65
2020-02-01 03:00 | 67 | 53 |  |  | 43862.125 | 69 | 63
2020-02-01 03:30 | 66 | 52 |  |  | 43862.1458 | 69 | 63
2020-02-01 04:00 | 67 | 53 |  |  | 43862.1667 | 70 | 63
2020-02-01 04:30 | 67 | 52 |  |  | 43862.1875 | 69 | 62
2020-02-01 05:00 | 65 | 50 |  |  | 43862.2083 | 67 | 60
2020-02-01 05:30 | 65 | 50 |  |  | 43862.2292 | 67 | 60
2020-02-01 06:00 | 65 | 49 |  |  | 43862.25 | 66 | 60
2020-02-01 06:30 | 61 | 46 |  |  | 43862.2708 | 64 | 60
2020-02-01 07:00 | 59 | 46 |  |  | 43862.2917 | 65 | 62
2020-02-01 07:30 | 57 | 46 |  |  | 43862.3125 | 63 | 61
2020-02-01 08:00 | 57 | 48 |  |  | 43862.3333 | 64 | 62
2020-02-01 08:30 | 59 | 50 |  |  | 43862.3542 | 66 | 64
2020-02-01 09:00 | 62 | 52 |  |  | 43862.375 | 68 | 67
2020-02-01 09:30 | 63 | 54 |  |  | 43862.3958 | 70 | 69
2020-02-01 10:00 | 62 | 54 |  |  | 43862.4167 | 68 | 67
2020-02-01 10:30 | 62 | 55 |  |  | 43862.4375 | 70 | 69
2020-02-01 11:00 | 65 | 58 |  |  | 43862.4583 | 72 | 71
2020-02-01 11:30 | 65 | 60 |  |  | 43862.4792 | 73 | 73
2020-02-01 12:00 | 66 | 62 |  |  | 43862.5 | 75 | 75
2020-02-01 12:30 | 68 | 63 |  |  | 43862.5208 | 76 | 75
2020-02-01 13:00 | 68 | 64 |  |  | 43862.5417 | 75 | 74
2020-02-01 13:30 | 71 | 67 |  |  | 43862.5625 | 76 | 75
2020-02-01 14:00 | 75 | 70 |  |  | 43862.5833 | 78 | 77
2020-02-01 14:30 | 75 | 70 |  |  | 43862.6042 | 80 | 79
2020-02-01 15:00 | 78 | 73 |  |  | 43862.625 | 85 | 84
2020-02-01 15:30 | 77 | 73 |  |  | 43862.6458 | 88 | 87
2020-02-01 16:00 | 78 | 74 |  |  | 43862.6667 | 90 | 89
2020-02-01 16:30 | 80 | 76 |  |  | 43862.6875 | 93 | 90
2020-02-01 17:00 | 84 | 81 |  |  | 43862.7083 | 98 | 95
2020-02-01 17:30 | 86 | 82 |  |  | 43862.7292 | 100 | 97
2020-02-01 18:00 | 88 | 84 |  |  | 43862.75 | 102 | 99
2020-02-01 18:30 | 89 | 85 |  |  | 43862.7708 | 103 | 100
2020-02-01 19:00 | 88 | 84 |  |  | 43862.7917 | 105 | 101
2020-02-01 19:30 | 89 | 85 |  |  | 43862.8125 | 106 | 102
2020-02-01 20:00 | 88 | 84 |  |  | 43862.8333 | 104 | 101
2020-02-01 20:30 | 83 | 80 |  |  | 43862.8542 | 100 | 96
2020-02-01 21:00 | 81 | 77 |  |  | 43862.875 | 95 | 93
2020-02-01 21:30 | 77 | 75 |  |  | 43862.8958 | 91 | 90
2020-02-01 22:00 | 74 | 73 |  |  | 43862.9167 | 90 | 90
2020-02-01 22:30 | 74 | 73 |  |  | 43862.9375 | 89 | 89
2020-02-01 23:00 | 72 | 71 |  |  | 43862.9583 | 85 | 85
2020-02-01 23:30 | 71 | 68 |  |  | 43862.9792 | 83 | 83
2020-02-02 | 68 | 64 |  |  | 43863 | 78 | 78
2020-02-02 00:30 | 66 | 61 |  |  | 43863.0208 | 74 | 73
2020-02-02 01:00 | 62 | 56 |  |  | 43863.0417 | 69 | 68
2020-02-02 01:30 | 59 | 52 |  |  | 43863.0625 | 65 | 63
2020-02-02 02:00 | 60 | 53 |  |  | 43863.0833 | 66 | 64
2020-02-02 02:30 | 61 | 53 |  |  | 43863.1042 | 67 | 65
2020-02-02 03:00 | 61 | 53 |  |  | 43863.125 | 67 | 65
2020-02-02 03:30 | 62 | 53 |  |  | 43863.1458 | 67 | 65
2020-02-02 04:00 | 61 | 53 |  |  | 43863.1667 | 67 | 65
2020-02-02 04:30 | 62 | 54 |  |  | 43863.1875 | 66 | 64
2020-02-02 05:00 | 61 | 53 |  |  | 43863.2083 | 65 | 63
2020-02-02 05:30 | 59 | 50 |  |  | 43863.2292 | 63 | 62
2020-02-02 06:00 | 58 | 49 |  |  | 43863.25 | 63 | 61
2020-02-02 06:30 | 55 | 45 |  |  | 43863.2708 | 59 | 58
2020-02-02 07:00 | 51 | 42 |  |  | 43863.2917 | 56 | 55
2020-02-02 07:30 | 50 | 42 |  |  | 43863.3125 | 57 | 56
2020-02-02 08:00 | 49 | 41 |  |  | 43863.3333 | 57 | 56
2020-02-02 08:30 | 49 | 44 |  |  | 43863.3542 | 59 | 59
2020-02-02 09:00 | 48 | 44 |  |  | 43863.375 | 59 | 59
2020-02-02 09:30 | 52 | 48 |  |  | 43863.3958 | 63 | 63
2020-02-02 10:00 | 53 | 49 |  |  | 43863.4167 | 64 | 64
2020-02-02 10:30 | 55 | 51 |  |  | 43863.4375 | 65 | 65
2020-02-02 11:00 | 56 | 52 |  |  | 43863.4583 | 64 | 64
2020-02-02 11:30 | 57 | 54 |  |  | 43863.4792 | 65 | 65
2020-02-02 12:00 | 62 | 55 |  |  | 43863.5 | 68 | 66
2020-02-02 12:30 | 66 | 60 |  |  | 43863.5208 | 73 | 70
2020-02-02 13:00 | 69 | 65 |  |  | 43863.5417 | 78 | 76
2020-02-02 13:30 | 74 | 70 |  |  | 43863.5625 | 84 | 82
2020-02-02 14:00 | 79 | 75 |  |  | 43863.5833 | 89 | 86
2020-02-02 14:30 | 82 | 78 |  |  | 43863.6042 | 91 | 89
2020-02-02 15:00 | 82 | 80 |  |  | 43863.625 | 92 | 90
2020-02-02 15:30 | 85 | 83 |  |  | 43863.6458 | 95 | 94
2020-02-02 16:00 | 88 | 88 |  |  | 43863.6667 | 99 | 98
2020-02-02 16:30 | 93 | 93 |  |  | 43863.6875 | 104 | 103
2020-02-02 17:00 | 96 | 95 |  |  | 43863.7083 | 108 | 107
2020-02-02 17:30 | 98 | 98 |  |  | 43863.7292 | 110 | 110
2020-02-02 18:00 | 101 | 101 |  |  | 43863.75 | 114 | 114
2020-02-02 18:30 | 102 | 101 |  |  | 43863.7708 | 119 | 117
2020-02-02 19:00 | 102 | 101 |  |  | 43863.7917 | 122 | 121
2020-02-02 19:30 | 105 | 104 |  |  | 43863.8125 | 125 | 123
2020-02-02 20:00 | 98 | 97 |  |  | 43863.8333 | 122 | 121
2020-02-02 20:30 | 96 | 94 |  |  | 43863.8542 | 118 | 117
2020-02-02 21:00 | 93 | 90 |  |  | 43863.875 | 114 | 112
2020-02-02 21:30 | 91 | 88 |  |  | 43863.8958 | 111 | 109
2020-02-02 22:00 | 99 | 95 |  |  | 43863.9167 | 114 | 111
2020-02-02 22:30 | 95 | 92 |  |  | 43863.9375 | 111 | 110
2020-02-02 23:00 | 94 | 90 |  |  | 43863.9583 | 107 | 105
2020-02-02 23:30 | 87 | 85 |  |  | 43863.9792 | 101 | 100
2020-02-03 | 84 | 77 |  |  | 43864 | 94 | 93
2020-02-03 00:30 | 81 | 73 |  |  | 43864.0208 | 90 | 88
2020-02-03 01:00 | 80 | 72 |  |  | 43864.0417 | 87 | 85
2020-02-03 01:30 | 75 | 66 |  |  | 43864.0625 | 82 | 79
2020-02-03 02:00 | 73 | 63 |  |  | 43864.0833 | 80 | 77
2020-02-03 02:30 | 72 | 62 |  |  | 43864.1042 | 78 | 76
2020-02-03 03:00 | 72 | 62 |  |  | 43864.125 | 78 | 75
2020-02-03 03:30 | 73 | 63 |  |  | 43864.1458 | 80 | 76
2020-02-03 04:00 | 74 | 63 |  |  | 43864.1667 | 79 | 76
2020-02-03 04:30 | 74 | 64 |  |  | 43864.1875 | 80 | 77
2020-02-03 05:00 | 76 | 67 |  |  | 43864.2083 | 82 | 79
2020-02-03 05:30 | 77 | 68 |  |  | 43864.2292 | 84 | 82
2020-02-03 06:00 | 80 | 72 |  |  | 43864.25 | 89 | 87
2020-02-03 06:30 | 82 | 77 |  |  | 43864.2708 | 95 | 94
2020-02-03 07:00 | 84 | 80 |  |  | 43864.2917 | 100 | 99
2020-02-03 07:30 | 86 | 84 |  |  | 43864.3125 | 107 | 106
2020-02-03 08:00 | 88 | 87 |  |  | 43864.3333 | 111 | 110
2020-02-03 08:30 | 88 | 86 |  |  | 43864.3542 | 112 | 111
2020-02-03 09:00 | 90 | 89 |  |  | 43864.375 | 114 | 114
2020-02-03 09:30 | 93 | 93 |  |  | 43864.3958 | 118 | 118
2020-02-03 10:00 | 93 | 93 |  |  | 43864.4167 | 118 | 118
2020-02-03 10:30 | 94 | 93 |  |  | 43864.4375 | 121 | 121
2020-02-03 11:00 | 97 | 96 |  |  | 43864.4583 | 124 | 123
2020-02-03 11:30 | 100 | 97 |  |  | 43864.4792 | 129 | 124
2020-02-03 12:00 | 102 | 99 |  |  | 43864.5 | 131 | 126
2020-02-03 12:30 | 106 | 104 |  |  | 43864.5208 | 135 | 131
2020-02-03 13:00 | 107 | 105 |  |  | 43864.5417 | 135 | 131
2020-02-03 13:30 | 108 | 107 |  |  | 43864.5625 | 135 | 132
2020-02-03 14:00 | 110 | 108 |  |  | 43864.5833 | 136 | 133
2020-02-03 14:30 | 111 | 109 |  |  | 43864.6042 | 137 | 133
2020-02-03 15:00 | 104 | 103 |  |  | 43864.625 | 134 | 131
2020-02-03 15:30 | 105 | 105 |  |  | 43864.6458 | 135 | 132
2020-02-03 16:00 | 112 | 111 |  |  | 43864.6667 | 140 | 138
2020-02-03 16:30 | 121 | 114 |  |  | 43864.6875 | 145 | 144
2020-02-03 17:00 | 124 | 116 |  |  | 43864.7083 | 150 | 148
2020-02-03 17:30 | 124 | 115 |  |  | 43864.7292 | 148 | 145
2020-02-03 18:00 | 125 | 117 |  |  | 43864.75 | 147 | 145
2020-02-03 18:30 | 118 | 114 |  |  | 43864.7708 | 144 | 140
2020-02-03 19:00 | 117 | 115 |  |  | 43864.7917 | 143 | 142
2020-02-03 19:30 | 118 | 115 |  |  | 43864.8125 | 143 | 142
2020-02-03 20:00 | 118 | 115 |  |  | 43864.8333 | 142 | 141
2020-02-03 20:30 | 116 | 114 |  |  | 43864.8542 | 140 | 140
2020-02-03 21:00 | 110 | 109 |  |  | 43864.875 | 133 | 132
2020-02-03 21:30 | 103 | 103 |  |  | 43864.8958 | 128 | 122
2020-02-03 22:00 | 98 | 97 |  |  | 43864.9167 | 127 | 122
2020-02-03 22:30 | 93 | 93 |  |  | 43864.9375 | 123 | 119
2020-02-03 23:00 | 93 | 92 |  |  | 43864.9583 | 113 | 109
2020-02-03 23:30 | 89 | 87 |  |  | 43864.9792 | 106 | 102
2020-02-04 | 84 | 82 |  |  | 43865 | 101 | 96
2020-02-04 00:30 | 81 | 79 |  |  | 43865.0208 | 97 | 93
2020-02-04 01:00 | 79 | 76 |  |  | 43865.0417 | 92 | 87
2020-02-04 01:30 | 75 | 72 |  |  | 43865.0625 | 88 | 83
2020-02-04 02:00 | 73 | 69 |  |  | 43865.0833 | 86 | 81
2020-02-04 02:30 | 72 | 69 |  |  | 43865.1042 | 86 | 80
2020-02-04 03:00 | 71 | 67 |  |  | 43865.125 | 86 | 80
2020-02-04 03:30 | 70 | 66 |  |  | 43865.1458 | 84 | 78
2020-02-04 04:00 | 70 | 66 |  |  | 43865.1667 | 85 | 78
2020-02-04 04:30 | 71 | 67 |  |  | 43865.1875 | 85 | 79
2020-02-04 05:00 | 73 | 70 |  |  | 43865.2083 | 88 | 82
2020-02-04 05:30 | 75 | 73 |  |  | 43865.2292 | 90 | 86
2020-02-04 06:00 | 76 | 74 |  |  | 43865.25 | 93 | 88
2020-02-04 06:30 | 81 | 79 |  |  | 43865.2708 | 100 | 95
2020-02-04 07:00 | 85 | 84 |  |  | 43865.2917 | 106 | 103
2020-02-04 07:30 | 89 | 89 |  |  | 43865.3125 | 115 | 111
2020-02-04 08:00 | 92 | 92 |  |  | 43865.3333 | 118 | 115
2020-02-04 08:30 | 97 | 97 |  |  | 43865.3542 | 124 | 121
2020-02-04 09:00 | 101 | 101 |  |  | 43865.375 | 131 | 127
2020-02-04 09:30 | 98 | 98 |  |  | 43865.3958 | 128 | 124
2020-02-04 10:00 | 94 | 94 |  |  | 43865.4167 | 127 | 123
2020-02-04 10:30 | 97 | 96 |  |  | 43865.4375 | 128 | 124
2020-02-04 11:00 | 100 | 100 |  |  | 43865.4583 | 127 | 123
2020-02-04 11:30 | 99 | 99 |  |  | 43865.4792 | 125 | 121
2020-02-04 12:00 | 95 | 94 |  |  | 43865.5 | 122 | 118
2020-02-04 12:30 | 96 | 96 |  |  | 43865.5208 | 123 | 118
2020-02-04 13:00 | 102 | 102 |  |  | 43865.5417 | 129 | 125
2020-02-04 13:30 | 102 | 101 |  |  | 43865.5625 | 127 | 123
2020-02-04 14:00 | 100 | 100 |  |  | 43865.5833 | 125 | 120
2020-02-04 14:30 | 102 | 101 |  |  | 43865.6042 | 130 | 125
2020-02-04 15:00 | 101 | 100 |  |  | 43865.625 | 129 | 124
2020-02-04 15:30 | 98 | 97 |  |  | 43865.6458 | 124 | 118
2020-02-04 16:00 | 97 | 96 |  |  | 43865.6667 | 121 | 115
2020-02-04 16:30 | 95 | 94 |  |  | 43865.6875 | 120 | 113
2020-02-04 17:00 | 96 | 95 |  |  | 43865.7083 | 120 | 113
2020-02-04 17:30 | 96 | 95 |  |  | 43865.7292 | 118 | 111
2020-02-04 18:00 | 97 | 94 |  |  | 43865.75 | 118 | 109
2020-02-04 18:30 | 96 | 94 |  |  | 43865.7708 | 116 | 108
2020-02-04 19:00 | 100 | 98 |  |  | 43865.7917 | 118 | 111
2020-02-04 19:30 | 98 | 96 |  |  | 43865.8125 | 117 | 110
2020-02-04 20:00 | 96 | 94 |  |  | 43865.8333 | 115 | 107
2020-02-04 20:30 | 95 | 93 |  |  | 43865.8542 | 114 | 106
2020-02-04 21:00 | 89 | 88 |  |  | 43865.875 | 105 | 100
2020-02-04 21:30 | 83 | 82 |  |  | 43865.8958 | 99 | 93
2020-02-04 22:00 | 81 | 80 |  |  | 43865.9167 | 97 | 92
2020-02-04 22:30 | 79 | 78 |  |  | 43865.9375 | 95 | 90
2020-02-04 23:00 | 76 | 75 |  |  | 43865.9583 | 90 | 85
2020-02-04 23:30 | 71 | 70 |  |  | 43865.9792 | 86 | 80
2020-02-05 | 66 | 63 |  |  | 43866 | 81 | 74
2020-02-05 00:30 | 64 | 61 |  |  | 43866.0208 | 79 | 71
2020-02-05 01:00 | 64 | 60 |  |  | 43866.0417 | 78 | 69
2020-02-05 01:30 | 63 | 59 |  |  | 43866.0625 | 77 | 67
2020-02-05 02:00 | 61 | 58 |  |  | 43866.0833 | 76 | 66
2020-02-05 02:30 | 61 | 57 |  |  | 43866.1042 | 75 | 65
2020-02-05 03:00 | 60 | 57 |  |  | 43866.125 | 75 | 65
2020-02-05 03:30 | 60 | 56 |  |  | 43866.1458 | 75 | 65
2020-02-05 04:00 | 59 | 55 |  |  | 43866.1667 | 74 | 64
2020-02-05 04:30 | 60 | 56 |  |  | 43866.1875 | 75 | 65
2020-02-05 05:00 | 63 | 59 |  |  | 43866.2083 | 78 | 68
2020-02-05 05:30 | 65 | 63 |  |  | 43866.2292 | 80 | 73
2020-02-05 06:00 | 69 | 67 |  |  | 43866.25 | 85 | 78
2020-02-05 06:30 | 74 | 73 |  |  | 43866.2708 | 92 | 88
2020-02-05 07:00 | 79 | 78 |  |  | 43866.2917 | 98 | 95
2020-02-05 07:30 | 84 | 83 |  |  | 43866.3125 | 107 | 103
2020-02-05 08:00 | 90 | 89 |  |  | 43866.3333 | 116 | 110
2020-02-05 08:30 | 94 | 92 |  |  | 43866.3542 | 119 | 114
2020-02-05 09:00 | 94 | 93 |  |  | 43866.375 | 119 | 114
2020-02-05 09:30 | 97 | 96 |  |  | 43866.3958 | 124 | 119
2020-02-05 10:00 | 96 | 95 |  |  | 43866.4167 | 120 | 116
2020-02-05 10:30 | 91 | 91 |  |  | 43866.4375 | 117 | 112
2020-02-05 11:00 | 87 | 86 |  |  | 43866.4583 | 111 | 106
2020-02-05 11:30 | 81 | 80 |  |  | 43866.4792 | 111 | 106
2020-02-05 12:00 | 87 | 86 |  |  | 43866.5 | 119 | 115
2020-02-05 12:30 | 90 | 89 |  |  | 43866.5208 | 116 | 111
2020-02-05 13:00 | 89 | 87 |  |  | 43866.5417 | 114 | 109
2020-02-05 13:30 | 93 | 92 |  |  | 43866.5625 | 117 | 112
2020-02-05 14:00 | 94 | 93 |  |  | 43866.5833 | 118 | 113
2020-02-05 14:30 | 92 | 91 |  |  | 43866.6042 | 117 | 112
2020-02-05 15:00 | 88 | 87 |  |  | 43866.625 | 113 | 106
2020-02-05 15:30 | 87 | 85 |  |  | 43866.6458 | 112 | 105
2020-02-05 16:00 | 88 | 86 |  |  | 43866.6667 | 113 | 106
2020-02-05 16:30 | 88 | 86 |  |  | 43866.6875 | 113 | 105
2020-02-05 17:00 | 92 | 90 |  |  | 43866.7083 | 115 | 108
2020-02-05 17:30 | 93 | 91 |  |  | 43866.7292 | 116 | 108
2020-02-05 18:00 | 92 | 90 |  |  | 43866.75 | 114 | 104
2020-02-05 18:30 | 93 | 90 |  |  | 43866.7708 | 113 | 103
2020-02-05 19:00 | 94 | 91 |  |  | 43866.7917 | 114 | 105
2020-02-05 19:30 | 92 | 90 |  |  | 43866.8125 | 111 | 102
2020-02-05 20:00 | 91 | 89 |  |  | 43866.8333 | 108 | 101
2020-02-05 20:30 | 88 | 86 |  |  | 43866.8542 | 104 | 97
2020-02-05 21:00 | 81 | 80 |  |  | 43866.875 | 94 | 90
2020-02-05 21:30 | 76 | 76 |  |  | 43866.8958 | 89 | 86
2020-02-05 22:00 | 74 | 73 |  |  | 43866.9167 | 88 | 85
2020-02-05 22:30 | 72 | 71 |  |  | 43866.9375 | 87 | 83
2020-02-05 23:00 | 68 | 67 |  |  | 43866.9583 | 83 | 78
2020-02-05 23:30 | 64 | 62 |  |  | 43866.9792 | 78 | 73
2020-02-06 | 58 | 56 |  |  | 43867 | 73 | 67
2020-02-06 00:30 | 55 | 53 |  |  | 43867.0208 | 70 | 63
2020-02-06 01:00 | 56 | 53 |  |  | 43867.0417 | 69 | 61
2020-02-06 01:30 | 54 | 51 |  |  | 43867.0625 | 67 | 59
2020-02-06 02:00 | 52 | 49 |  |  | 43867.0833 | 66 | 58
2020-02-06 02:30 | 53 | 50 |  |  | 43867.1042 | 66 | 58
2020-02-06 03:00 | 53 | 50 |  |  | 43867.125 | 66 | 58
2020-02-06 03:30 | 53 | 50 |  |  | 43867.1458 | 67 | 59
2020-02-06 04:00 | 54 | 51 |  |  | 43867.1667 | 68 | 60
2020-02-06 04:30 | 55 | 52 |  |  | 43867.1875 | 68 | 61
2020-02-06 05:00 | 58 | 55 |  |  | 43867.2083 | 71 | 64
2020-02-06 05:30 | 60 | 58 |  |  | 43867.2292 | 74 | 67
2020-02-06 06:00 | 63 | 61 |  |  | 43867.25 | 77 | 72
2020-02-06 06:30 | 67 | 66 |  |  | 43867.2708 | 84 | 81
2020-02-06 07:00 | 71 | 70 |  |  | 43867.2917 | 90 | 87
2020-02-06 07:30 | 77 | 77 |  |  | 43867.3125 | 97 | 95
2020-02-06 08:00 | 78 | 78 |  |  | 43867.3333 | 99 | 97
2020-02-06 08:30 | 77 | 76 |  |  | 43867.3542 | 99 | 97
2020-02-06 09:00 | 78 | 78 |  |  | 43867.375 | 101 | 98
2020-02-06 09:30 | 81 | 81 |  |  | 43867.3958 | 101 | 99
2020-02-06 10:00 | 78 | 78 |  |  | 43867.4167 | 96 | 93
2020-02-06 10:30 | 78 | 77 |  |  | 43867.4375 | 97 | 95
2020-02-06 11:00 | 75 | 75 |  |  | 43867.4583 | 96 | 94
2020-02-06 11:30 | 73 | 73 |  |  | 43867.4792 | 93 | 91
2020-02-06 12:00 | 73 | 73 |  |  | 43867.5 | 91 | 89
2020-02-06 12:30 | 74 | 74 |  |  | 43867.5208 | 95 | 93
2020-02-06 13:00 | 83 | 83 |  |  | 43867.5417 | 107 | 106
2020-02-06 13:30 | 83 | 83 |  |  | 43867.5625 | 109 | 108
2020-02-06 14:00 | 83 | 83 |  |  | 43867.5833 | 114 | 111
2020-02-06 14:30 | 89 | 89 |  |  | 43867.6042 | 109 | 106
2020-02-06 15:00 | 87 | 87 |  |  | 43867.625 | 107 | 105
2020-02-06 15:30 | 86 | 86 |  |  | 43867.6458 | 108 | 106
2020-02-06 16:00 | 86 | 86 |  |  | 43867.6667 | 109 | 107
2020-02-06 16:30 | 87 | 87 |  |  | 43867.6875 | 110 | 107
2020-02-06 17:00 | 86 | 86 |  |  | 43867.7083 | 109 | 106
2020-02-06 17:30 | 87 | 86 |  |  | 43867.7292 | 109 | 105
2020-02-06 18:00 | 89 | 88 |  |  | 43867.75 | 110 | 105
2020-02-06 18:30 | 89 | 88 |  |  | 43867.7708 | 110 | 104
2020-02-06 19:00 | 91 | 90 |  |  | 43867.7917 | 111 | 105
2020-02-06 19:30 | 90 | 89 |  |  | 43867.8125 | 108 | 103
2020-02-06 20:00 | 90 | 89 |  |  | 43867.8333 | 108 | 102
2020-02-06 20:30 | 90 | 89 |  |  | 43867.8542 | 108 | 102
2020-02-06 21:00 | 87 | 86 |  |  | 43867.875 | 104 | 98
2020-02-06 21:30 | 84 | 82 |  |  | 43867.8958 | 101 | 94
2020-02-06 22:00 | 82 | 80 |  |  | 43867.9167 | 100 | 93
2020-02-06 22:30 | 80 | 77 |  |  | 43867.9375 | 99 | 91
2020-02-06 23:00 | 77 | 74 |  |  | 43867.9583 | 95 | 87
2020-02-06 23:30 | 71 | 69 |  |  | 43867.9792 | 88 | 80
2020-02-07 | 63 | 60 |  |  | 43868 | 80 | 71
2020-02-07 00:30 | 60 | 57 |  |  | 43868.0208 | 74 | 66
2020-02-07 01:00 | 57 | 54 |  |  | 43868.0417 | 71 | 62
2020-02-07 01:30 | 55 | 51 |  |  | 43868.0625 | 69 | 60
2020-02-07 02:00 | 55 | 51 |  |  | 43868.0833 | 70 | 60
2020-02-07 02:30 | 56 | 52 |  |  | 43868.1042 | 70 | 60
2020-02-07 03:00 | 54 | 50 |  |  | 43868.125 | 69 | 59
2020-02-07 03:30 | 54 | 50 |  |  | 43868.1458 | 69 | 59
2020-02-07 04:00 | 54 | 50 |  |  | 43868.1667 | 68 | 57
2020-02-07 04:30 | 54 | 50 |  |  | 43868.1875 | 68 | 58
2020-02-07 05:00 | 56 | 52 |  |  | 43868.2083 | 72 | 62
2020-02-07 05:30 | 60 | 57 |  |  | 43868.2292 | 76 | 68
2020-02-07 06:00 | 63 | 61 |  |  | 43868.25 | 79 | 73
2020-02-07 06:30 | 72 | 70 |  |  | 43868.2708 | 90 | 85
2020-02-07 07:00 | 76 | 75 |  |  | 43868.2917 | 97 | 93
2020-02-07 07:30 | 75 | 74 |  |  | 43868.3125 | 98 | 95
2020-02-07 08:00 | 76 | 76 |  |  | 43868.3333 | 99 | 97
2020-02-07 08:30 | 72 | 72 |  |  | 43868.3542 | 98 | 96
2020-02-07 09:00 | 71 | 71 |  |  | 43868.375 | 94 | 92
2020-02-07 09:30 | 63 | 62 |  |  | 43868.3958 | 89 | 87
2020-02-07 10:00 | 66 | 66 |  |  | 43868.4167 | 94 | 92
2020-02-07 10:30 | 75 | 75 |  |  | 43868.4375 | 99 | 97
2020-02-07 11:00 | 79 | 79 |  |  | 43868.4583 | 96 | 94
2020-02-07 11:30 | 69 | 69 |  |  | 43868.4792 | 89 | 87
2020-02-07 12:00 | 69 | 69 |  |  | 43868.5 | 94 | 92
2020-02-07 12:30 | 77 | 77 |  |  | 43868.5208 | 96 | 94
2020-02-07 13:00 | 74 | 74 |  |  | 43868.5417 | 96 | 94
2020-02-07 13:30 | 75 | 75 |  |  | 43868.5625 | 96 | 94
2020-02-07 14:00 | 78 | 78 |  |  | 43868.5833 | 101 | 99
2020-02-07 14:30 | 86 | 86 |  |  | 43868.6042 | 110 | 106
2020-02-07 15:00 | 88 | 87 |  |  | 43868.625 | 109 | 103
2020-02-07 15:30 | 88 | 87 |  |  | 43868.6458 | 112 | 106
2020-02-07 16:00 | 91 | 89 |  |  | 43868.6667 | 116 | 110
2020-02-07 16:30 | 92 | 91 |  |  | 43868.6875 | 118 | 111
2020-02-07 17:00 | 93 | 91 |  |  | 43868.7083 | 117 | 109
2020-02-07 17:30 | 96 | 93 |  |  | 43868.7292 | 121 | 112
2020-02-07 18:00 | 96 | 93 |  |  | 43868.75 | 120 | 110
2020-02-07 18:30 | 94 | 92 |  |  | 43868.7708 | 116 | 108
2020-02-07 19:00 | 96 | 94 |  |  | 43868.7917 | 116 | 110
2020-02-07 19:30 | 95 | 93 |  |  | 43868.8125 | 115 | 109
2020-02-07 20:00 | 94 | 92 |  |  | 43868.8333 | 113 | 106
2020-02-07 20:30 | 91 | 90 |  |  | 43868.8542 | 110 | 104
2020-02-07 21:00 | 90 | 89 |  |  | 43868.875 | 107 | 102
2020-02-07 21:30 | 86 | 85 |  |  | 43868.8958 | 103 | 97
2020-02-07 22:00 | 83 | 82 |  |  | 43868.9167 | 100 | 95
2020-02-07 22:30 | 79 | 78 |  |  | 43868.9375 | 97 | 92
2020-02-07 23:00 | 77 | 76 |  |  | 43868.9583 | 94 | 89
2020-02-07 23:30 | 71 | 70 |  |  | 43868.9792 | 89 | 83
2020-02-08 | 66 | 64 |  |  | 43869 | 83 | 77
2020-02-08 00:30 | 62 | 60 |  |  | 43869.0208 | 78 | 71
2020-02-08 01:00 | 59 | 57 |  |  | 43869.0417 | 76 | 68
2020-02-08 01:30 | 60 | 57 |  |  | 43869.0625 | 76 | 69
2020-02-08 02:00 | 59 | 56 |  |  | 43869.0833 | 74 | 67
2020-02-08 02:30 | 57 | 55 |  |  | 43869.1042 | 72 | 66
2020-02-08 03:00 | 57 | 54 |  |  | 43869.125 | 72 | 65
2020-02-08 03:30 | 56 | 53 |  |  | 43869.1458 | 73 | 66
2020-02-08 04:00 | 56 | 53 |  |  | 43869.1667 | 73 | 66
2020-02-08 04:30 | 57 | 55 |  |  | 43869.1875 | 73 | 66
2020-02-08 05:00 | 59 | 56 |  |  | 43869.2083 | 75 | 68
2020-02-08 05:30 | 60 | 57 |  |  | 43869.2292 | 76 | 69
2020-02-08 06:00 | 59 | 56 |  |  | 43869.25 | 76 | 69
2020-02-08 06:30 | 59 | 56 |  |  | 43869.2708 | 76 | 70
2020-02-08 07:00 | 56 | 53 |  |  | 43869.2917 | 73 | 67
2020-02-08 07:30 | 56 | 54 |  |  | 43869.3125 | 75 | 70
2020-02-08 08:00 | 59 | 58 |  |  | 43869.3333 | 80 | 76
2020-02-08 08:30 | 65 | 64 |  |  | 43869.3542 | 86 | 83
2020-02-08 09:00 | 63 | 62 |  |  | 43869.375 | 83 | 79
2020-02-08 09:30 | 59 | 58 |  |  | 43869.3958 | 75 | 72
2020-02-08 10:00 | 53 | 52 |  |  | 43869.4167 | 76 | 72
2020-02-08 10:30 | 51 | 48 |  |  | 43869.4375 | 75 | 68
2020-02-08 11:00 | 55 | 53 |  |  | 43869.4583 | 79 | 73
2020-02-08 11:30 | 59 | 57 |  |  | 43869.4792 | 85 | 79
2020-02-08 12:00 | 64 | 63 |  |  | 43869.5 | 85 | 79
2020-02-08 12:30 | 62 | 61 |  |  | 43869.5208 | 78 | 71
2020-02-08 13:00 | 56 | 55 |  |  | 43869.5417 | 76 | 69
2020-02-08 13:30 | 62 | 60 |  |  | 43869.5625 | 82 | 75
2020-02-08 14:00 | 68 | 67 |  |  | 43869.5833 | 91 | 85
2020-02-08 14:30 | 74 | 73 |  |  | 43869.6042 | 92 | 87
2020-02-08 15:00 | 72 | 70 |  |  | 43869.625 | 87 | 81
2020-02-08 15:30 | 76 | 75 |  |  | 43869.6458 | 97 | 91
2020-02-08 16:00 | 78 | 77 |  |  | 43869.6667 | 103 | 98
2020-02-08 16:30 | 77 | 75 |  |  | 43869.6875 | 103 | 97
2020-02-08 17:00 | 80 | 79 |  |  | 43869.7083 | 102 | 96
2020-02-08 17:30 | 84 | 83 |  |  | 43869.7292 | 106 | 100
2020-02-08 18:00 | 86 | 84 |  |  | 43869.75 | 107 | 100
2020-02-08 18:30 | 88 | 86 |  |  | 43869.7708 | 108 | 101
2020-02-08 19:00 | 89 | 87 |  |  | 43869.7917 | 109 | 103
2020-02-08 19:30 | 89 | 87 |  |  | 43869.8125 | 109 | 103
2020-02-08 20:00 | 89 | 87 |  |  | 43869.8333 | 110 | 104
2020-02-08 20:30 | 88 | 86 |  |  | 43869.8542 | 109 | 102
2020-02-08 21:00 | 87 | 85 |  |  | 43869.875 | 107 | 100
2020-02-08 21:30 | 85 | 83 |  |  | 43869.8958 | 106 | 98
2020-02-08 22:00 | 86 | 83 |  |  | 43869.9167 | 107 | 98
2020-02-08 22:30 | 84 | 81 |  |  | 43869.9375 | 106 | 96
2020-02-08 23:00 | 81 | 78 |  |  | 43869.9583 | 100 | 92
2020-02-08 23:30 | 77 | 74 |  |  | 43869.9792 | 94 | 88
2020-02-09 | 72 | 69 |  |  | 43870 | 89 | 83
2020-02-09 00:30 | 68 | 65 |  |  | 43870.0208 | 84 | 77
2020-02-09 01:00 | 64 | 61 |  |  | 43870.0417 | 80 | 72
2020-02-09 01:30 | 63 | 60 |  |  | 43870.0625 | 79 | 70
2020-02-09 02:00 | 63 | 59 |  |  | 43870.0833 | 79 | 70
2020-02-09 02:30 | 61 | 57 |  |  | 43870.1042 | 76 | 68
2020-02-09 03:00 | 59 | 56 |  |  | 43870.125 | 75 | 68
2020-02-09 03:30 | 58 | 54 |  |  | 43870.1458 | 74 | 67
2020-02-09 04:00 | 57 | 53 |  |  | 43870.1667 | 73 | 65
2020-02-09 04:30 | 57 | 54 |  |  | 43870.1875 | 73 | 65
2020-02-09 05:00 | 57 | 54 |  |  | 43870.2083 | 73 | 65
2020-02-09 05:30 | 56 | 53 |  |  | 43870.2292 | 72 | 64
2020-02-09 06:00 | 55 | 52 |  |  | 43870.25 | 72 | 64
2020-02-09 06:30 | 56 | 53 |  |  | 43870.2708 | 74 | 66
2020-02-09 07:00 | 53 | 50 |  |  | 43870.2917 | 71 | 64
2020-02-09 07:30 | 51 | 49 |  |  | 43870.3125 | 69 | 63
2020-02-09 08:00 | 50 | 47 |  |  | 43870.3333 | 66 | 59
2020-02-09 08:30 | 51 | 49 |  |  | 43870.3542 | 69 | 63
2020-02-09 09:00 | 49 | 47 |  |  | 43870.375 | 67 | 61
2020-02-09 09:30 | 49 | 48 |  |  | 43870.3958 | 66 | 62
2020-02-09 10:00 | 59 | 58 |  |  | 43870.4167 | 73 | 69
2020-02-09 10:30 | 72 | 72 |  |  | 43870.4375 | 85 | 81
2020-02-09 11:00 | 77 | 76 |  |  | 43870.4583 | 93 | 89
2020-02-09 11:30 | 78 | 77 |  |  | 43870.4792 | 93 | 87
2020-02-09 12:00 | 67 | 64 |  |  | 43870.5 | 85 | 78
2020-02-09 12:30 | 56 | 52 |  |  | 43870.5208 | 74 | 66
2020-02-09 13:00 | 54 | 50 |  |  | 43870.5417 | 76 | 68
2020-02-09 13:30 | 66 | 64 |  |  | 43870.5625 | 87 | 80
2020-02-09 14:00 | 74 | 72 |  |  | 43870.5833 | 91 | 85
2020-02-09 14:30 | 69 | 67 |  |  | 43870.6042 | 91 | 84
2020-02-09 15:00 | 83 | 81 |  |  | 43870.625 | 97 | 91
2020-02-09 15:30 | 91 | 89 |  |  | 43870.6458 | 106 | 101
2020-02-09 16:00 | 84 | 82 |  |  | 43870.6667 | 107 | 101
2020-02-09 16:30 | 78 | 76 |  |  | 43870.6875 | 99 | 94
2020-02-09 17:00 | 83 | 82 |  |  | 43870.7083 | 101 | 96
2020-02-09 17:30 | 89 | 87 |  |  | 43870.7292 | 107 | 102
2020-02-09 18:00 | 89 | 87 |  |  | 43870.75 | 108 | 103
2020-02-09 18:30 | 87 | 85 |  |  | 43870.7708 | 106 | 101
2020-02-09 19:00 | 89 | 88 |  |  | 43870.7917 | 110 | 105
2020-02-09 19:30 | 90 | 88 |  |  | 43870.8125 | 111 | 105
2020-02-09 20:00 | 89 | 87 |  |  | 43870.8333 | 111 | 105
2020-02-09 20:30 | 90 | 88 |  |  | 43870.8542 | 111 | 106
2020-02-09 21:00 | 88 | 86 |  |  | 43870.875 | 107 | 103
2020-02-09 21:30 | 84 | 83 |  |  | 43870.8958 | 104 | 100
2020-02-09 22:00 | 83 | 82 |  |  | 43870.9167 | 103 | 99
2020-02-09 22:30 | 79 | 78 |  |  | 43870.9375 | 99 | 96
2020-02-09 23:00 | 75 | 74 |  |  | 43870.9583 | 93 | 90
2020-02-09 23:30 | 72 | 70 |  |  | 43870.9792 | 90 | 86
2020-02-10 | 68 | 66 |  |  | 43871 | 86 | 82
2020-02-10 00:30 | 65 | 63 |  |  | 43871.0208 | 82 | 77
2020-02-10 01:00 | 63 | 60 |  |  | 43871.0417 | 79 | 74
2020-02-10 01:30 | 63 | 60 |  |  | 43871.0625 | 79 | 73
2020-02-10 02:00 | 65 | 62 |  |  | 43871.0833 | 80 | 74
2020-02-10 02:30 | 63 | 59 |  |  | 43871.1042 | 78 | 72
2020-02-10 03:00 | 61 | 58 |  |  | 43871.125 | 77 | 70
2020-02-10 03:30 | 61 | 57 |  |  | 43871.1458 | 76 | 69
2020-02-10 04:00 | 57 | 54 |  |  | 43871.1667 | 73 | 65
2020-02-10 04:30 | 57 | 54 |  |  | 43871.1875 | 72 | 66
2020-02-10 05:00 | 61 | 58 |  |  | 43871.2083 | 76 | 70
2020-02-10 05:30 | 62 | 60 |  |  | 43871.2292 | 78 | 72
2020-02-10 06:00 | 64 | 63 |  |  | 43871.25 | 81 | 76
2020-02-10 06:30 | 68 | 67 |  |  | 43871.2708 | 87 | 84
2020-02-10 07:00 | 71 | 71 |  |  | 43871.2917 | 95 | 92
2020-02-10 07:30 | 79 | 78 |  |  | 43871.3125 | 107 | 103
2020-02-10 08:00 | 86 | 83 |  |  | 43871.3333 | 116 | 109
2020-02-10 08:30 | 86 | 84 |  |  | 43871.3542 | 117 | 109
2020-02-10 09:00 | 82 | 80 |  |  | 43871.375 | 111 | 104
2020-02-10 09:30 | 81 | 79 |  |  | 43871.3958 | 111 | 104
2020-02-10 10:00 | 88 | 86 |  |  | 43871.4167 | 118 | 110
2020-02-10 10:30 | 92 | 89 |  |  | 43871.4375 | 123 | 114
2020-02-10 11:00 | 85 | 83 |  |  | 43871.4583 | 113 | 105
2020-02-10 11:30 | 84 | 82 |  |  | 43871.4792 | 106 | 100
2020-02-10 12:00 | 86 | 85 |  |  | 43871.5 | 116 | 110
2020-02-10 12:30 | 92 | 90 |  |  | 43871.5208 | 117 | 111
2020-02-10 13:00 | 89 | 88 |  |  | 43871.5417 | 115 | 109
2020-02-10 13:30 | 92 | 90 |  |  | 43871.5625 | 113 | 107
2020-02-10 14:00 | 87 | 86 |  |  | 43871.5833 | 115 | 110
2020-02-10 14:30 | 89 | 88 |  |  | 43871.6042 | 117 | 113
2020-02-10 15:00 | 92 | 91 |  |  | 43871.625 | 115 | 111
2020-02-10 15:30 | 97 | 97 |  |  | 43871.6458 | 119 | 116
2020-02-10 16:00 | 104 | 103 |  |  | 43871.6667 | 125 | 122
2020-02-10 16:30 | 101 | 101 |  |  | 43871.6875 | 124 | 120
2020-02-10 17:00 | 100 | 100 |  |  | 43871.7083 | 124 | 119
2020-02-10 17:30 | 107 | 107 |  |  | 43871.7292 | 131 | 125
2020-02-10 18:00 | 107 | 106 |  |  | 43871.75 | 132 | 125
2020-02-10 18:30 | 107 | 106 |  |  | 43871.7708 | 131 | 125
2020-02-10 19:00 | 110 | 110 |  |  | 43871.7917 | 134 | 128
2020-02-10 19:30 | 109 | 108 |  |  | 43871.8125 | 132 | 127
2020-02-10 20:00 | 107 | 107 |  |  | 43871.8333 | 126 | 123
2020-02-10 20:30 | 103 | 103 |  |  | 43871.8542 | 121 | 118
2020-02-10 21:00 | 99 | 98 |  |  | 43871.875 | 115 | 113
2020-02-10 21:30 | 94 | 94 |  |  | 43871.8958 | 111 | 109
2020-02-10 22:00 | 90 | 89 |  |  | 43871.9167 | 107 | 104
2020-02-10 22:30 | 83 | 83 |  |  | 43871.9375 | 100 | 98
2020-02-10 23:00 | 80 | 79 |  |  | 43871.9583 | 95 | 92
2020-02-10 23:30 | 75 | 73 |  |  | 43871.9792 | 90 | 87
2020-02-11 | 71 | 69 |  |  | 43872 | 86 | 82
2020-02-11 00:30 | 68 | 66 |  |  | 43872.0208 | 81 | 76
2020-02-11 01:00 | 63 | 61 |  |  | 43872.0417 | 76 | 71
2020-02-11 01:30 | 59 | 57 |  |  | 43872.0625 | 73 | 66
2020-02-11 02:00 | 60 | 58 |  |  | 43872.0833 | 73 | 67
2020-02-11 02:30 | 60 | 58 |  |  | 43872.1042 | 73 | 67
2020-02-11 03:00 | 58 | 56 |  |  | 43872.125 | 72 | 66
2020-02-11 03:30 | 58 | 56 |  |  | 43872.1458 | 71 | 66
2020-02-11 04:00 | 58 | 56 |  |  | 43872.1667 | 71 | 66
2020-02-11 04:30 | 59 | 57 |  |  | 43872.1875 | 73 | 67
2020-02-11 05:00 | 61 | 59 |  |  | 43872.2083 | 75 | 70
2020-02-11 05:30 | 66 | 64 |  |  | 43872.2292 | 81 | 76
2020-02-11 06:00 | 71 | 70 |  |  | 43872.25 | 87 | 83
2020-02-11 06:30 | 76 | 75 |  |  | 43872.2708 | 95 | 92
2020-02-11 07:00 | 82 | 81 |  |  | 43872.2917 | 101 | 99
2020-02-11 07:30 | 92 | 92 |  |  | 43872.3125 | 107 | 104
2020-02-11 08:00 | 92 | 91 |  |  | 43872.3333 | 111 | 105
2020-02-11 08:30 | 87 | 85 |  |  | 43872.3542 | 105 | 101
2020-02-11 09:00 | 84 | 82 |  |  | 43872.375 | 106 | 101
2020-02-11 09:30 | 83 | 82 |  |  | 43872.3958 | 110 | 106
2020-02-11 10:00 | 88 | 88 |  |  | 43872.4167 | 109 | 107
2020-02-11 10:30 | 93 | 92 |  |  | 43872.4375 | 108 | 105
2020-02-11 11:00 | 94 | 93 |  |  | 43872.4583 | 107 | 105
2020-02-11 11:30 | 95 | 95 |  |  | 43872.4792 | 111 | 109
2020-02-11 12:00 | 96 | 95 |  |  | 43872.5 | 113 | 111
2020-02-11 12:30 | 89 | 87 |  |  | 43872.5208 | 117 | 113
2020-02-11 13:00 | 92 | 90 |  |  | 43872.5417 | 116 | 113
2020-02-11 13:30 | 95 | 94 |  |  | 43872.5625 | 116 | 115
2020-02-11 14:00 | 94 | 91 |  |  | 43872.5833 | 116 | 115
2020-02-11 14:30 | 97 | 97 |  |  | 43872.6042 | 115 | 115
2020-02-11 15:00 | 94 | 93 |  |  | 43872.625 | 113 | 112
2020-02-11 15:30 | 91 | 90 |  |  | 43872.6458 | 117 | 117
2020-02-11 16:00 | 97 | 96 |  |  | 43872.6667 | 125 | 124
2020-02-11 16:30 | 97 | 96 |  |  | 43872.6875 | 119 | 119
2020-02-11 17:00 | 95 | 94 |  |  | 43872.7083 | 114 | 113
2020-02-11 17:30 | 101 | 100 |  |  | 43872.7292 | 117 | 116
2020-02-11 18:00 | 102 | 101 |  |  | 43872.75 | 120 | 118
2020-02-11 18:30 | 106 | 105 |  |  | 43872.7708 | 122 | 121
2020-02-11 19:00 | 111 | 110 |  |  | 43872.7917 | 127 | 126
2020-02-11 19:30 | 110 | 109 |  |  | 43872.8125 | 127 | 126
2020-02-11 20:00 | 106 | 105 |  |  | 43872.8333 | 122 | 122
2020-02-11 20:30 | 106 | 104 |  |  | 43872.8542 | 122 | 121
2020-02-11 21:00 | 101 | 99 |  |  | 43872.875 | 116 | 115
2020-02-11 21:30 | 98 | 95 |  |  | 43872.8958 | 112 | 111
2020-02-11 22:00 | 94 | 93 |  |  | 43872.9167 | 110 | 109
2020-02-11 22:30 | 92 | 91 |  |  | 43872.9375 | 108 | 107
2020-02-11 23:00 | 89 | 88 |  |  | 43872.9583 | 102 | 101
2020-02-11 23:30 | 82 | 80 |  |  | 43872.9792 | 94 | 93
2020-02-12 | 78 | 74 |  |  | 43873 | 89 | 87
2020-02-12 00:30 | 74 | 70 |  |  | 43873.0208 | 84 | 82
2020-02-12 01:00 | 71 | 66 |  |  | 43873.0417 | 79 | 78
2020-02-12 01:30 | 70 | 65 |  |  | 43873.0625 | 79 | 77
2020-02-12 02:00 | 72 | 67 |  |  | 43873.0833 | 79 | 77
2020-02-12 02:30 | 71 | 65 |  |  | 43873.1042 | 77 | 76
2020-02-12 03:00 | 71 | 65 |  |  | 43873.125 | 76 | 75
2020-02-12 03:30 | 70 | 64 |  |  | 43873.1458 | 75 | 73
2020-02-12 04:00 | 67 | 62 |  |  | 43873.1667 | 74 | 73
2020-02-12 04:30 | 67 | 62 |  |  | 43873.1875 | 74 | 73
2020-02-12 05:00 | 69 | 64 |  |  | 43873.2083 | 77 | 75
2020-02-12 05:30 | 70 | 66 |  |  | 43873.2292 | 81 | 80
2020-02-12 06:00 | 73 | 69 |  |  | 43873.25 | 84 | 82
2020-02-12 06:30 | 76 | 73 |  |  | 43873.2708 | 92 | 91
2020-02-12 07:00 | 79 | 77 |  |  | 43873.2917 | 100 | 99
2020-02-12 07:30 | 84 | 82 |  |  | 43873.3125 | 109 | 108
2020-02-12 08:00 | 90 | 88 |  |  | 43873.3333 | 115 | 115
2020-02-12 08:30 | 93 | 89 |  |  | 43873.3542 | 108 | 106
2020-02-12 09:00 | 89 | 85 |  |  | 43873.375 | 103 | 100
2020-02-12 09:30 | 87 | 83 |  |  | 43873.3958 | 107 | 105
2020-02-12 10:00 | 89 | 85 |  |  | 43873.4167 | 114 | 113
2020-02-12 10:30 | 93 | 90 |  |  | 43873.4375 | 113 | 112
2020-02-12 11:00 | 97 | 94 |  |  | 43873.4583 | 112 | 110
2020-02-12 11:30 | 97 | 94 |  |  | 43873.4792 | 114 | 112
2020-02-12 12:00 | 90 | 86 |  |  | 43873.5 | 106 | 105
2020-02-12 12:30 | 95 | 92 |  |  | 43873.5208 | 117 | 116
2020-02-12 13:00 | 99 | 96 |  |  | 43873.5417 | 118 | 117
2020-02-12 13:30 | 100 | 97 |  |  | 43873.5625 | 114 | 113
2020-02-12 14:00 | 97 | 96 |  |  | 43873.5833 | 109 | 109
2020-02-12 14:30 | 98 | 96 |  |  | 43873.6042 | 113 | 113
2020-02-12 15:00 | 100 | 98 |  |  | 43873.625 | 106 | 105
2020-02-12 15:30 | 92 | 90 |  |  | 43873.6458 | 107 | 106
2020-02-12 16:00 | 92 | 90 |  |  | 43873.6667 | 114 | 113
2020-02-12 16:30 | 94 | 92 |  |  | 43873.6875 | 114 | 113
2020-02-12 17:00 | 98 | 96 |  |  | 43873.7083 | 118 | 117
2020-02-12 17:30 | 97 | 95 |  |  | 43873.7292 | 116 | 114
2020-02-12 18:00 | 97 | 95 |  |  | 43873.75 | 113 | 112
2020-02-12 18:30 | 97 | 95 |  |  | 43873.7708 | 111 | 110
2020-02-12 19:00 | 99 | 97 |  |  | 43873.7917 | 113 | 112
2020-02-12 19:30 | 98 | 96 |  |  | 43873.8125 | 112 | 111
2020-02-12 20:00 | 98 | 96 |  |  | 43873.8333 | 112 | 110
2020-02-12 20:30 | 99 | 97 |  |  | 43873.8542 | 113 | 111
2020-02-12 21:00 | 94 | 92 |  |  | 43873.875 | 106 | 105
2020-02-12 21:30 | 91 | 89 |  |  | 43873.8958 | 104 | 103
2020-02-12 22:00 | 87 | 85 |  |  | 43873.9167 | 101 | 99
2020-02-12 22:30 | 86 | 83 |  |  | 43873.9375 | 98 | 96
2020-02-12 23:00 | 82 | 79 |  |  | 43873.9583 | 93 | 91
2020-02-12 23:30 | 79 | 76 |  |  | 43873.9792 | 88 | 87
2020-02-13 | 74 | 71 |  |  | 43874 | 83 | 82
2020-02-13 00:30 | 71 | 66 |  |  | 43874.0208 | 77 | 75
2020-02-13 01:00 | 66 | 61 |  |  | 43874.0417 | 71 | 70
2020-02-13 01:30 | 66 | 61 |  |  | 43874.0625 | 70 | 69
2020-02-13 02:00 | 67 | 61 |  |  | 43874.0833 | 70 | 67
2020-02-13 02:30 | 65 | 59 |  |  | 43874.1042 | 69 | 67
2020-02-13 03:00 | 65 | 58 |  |  | 43874.125 | 69 | 66
2020-02-13 03:30 | 65 | 58 |  |  | 43874.1458 | 69 | 66
2020-02-13 04:00 | 65 | 58 |  |  | 43874.1667 | 69 | 66
2020-02-13 04:30 | 65 | 58 |  |  | 43874.1875 | 69 | 67
2020-02-13 05:00 | 66 | 59 |  |  | 43874.2083 | 70 | 68
2020-02-13 05:30 | 67 | 61 |  |  | 43874.2292 | 72 | 70
2020-02-13 06:00 | 64 | 59 |  |  | 43874.25 | 73 | 71
2020-02-13 06:30 | 70 | 67 |  |  | 43874.2708 | 82 | 81
2020-02-13 07:00 | 74 | 72 |  |  | 43874.2917 | 92 | 92
2020-02-13 07:30 | 77 | 76 |  |  | 43874.3125 | 99 | 99
2020-02-13 08:00 | 77 | 75 |  |  | 43874.3333 | 99 | 99
2020-02-13 08:30 | 78 | 77 |  |  | 43874.3542 | 102 | 102
2020-02-13 09:00 | 82 | 80 |  |  | 43874.375 | 103 | 103
2020-02-13 09:30 | 82 | 80 |  |  | 43874.3958 | 102 | 101
2020-02-13 10:00 | 78 | 76 |  |  | 43874.4167 | 100 | 99
2020-02-13 10:30 | 76 | 73 |  |  | 43874.4375 | 97 | 96
2020-02-13 11:00 | 75 | 72 |  |  | 43874.4583 | 97 | 96
2020-02-13 11:30 | 76 | 74 |  |  | 43874.4792 | 98 | 97
2020-02-13 12:00 | 78 | 76 |  |  | 43874.5 | 102 | 101
2020-02-13 12:30 | 67 | 65 |  |  | 43874.5208 | 98 | 97
2020-02-13 13:00 | 70 | 69 |  |  | 43874.5417 | 99 | 98
2020-02-13 13:30 | 86 | 85 |  |  | 43874.5625 | 106 | 105
2020-02-13 14:00 | 86 | 83 |  |  | 43874.5833 | 104 | 103
2020-02-13 14:30 | 84 | 81 |  |  | 43874.6042 | 103 | 102
2020-02-13 15:00 | 81 | 78 |  |  | 43874.625 | 102 | 100
2020-02-13 15:30 | 82 | 79 |  |  | 43874.6458 | 102 | 100
2020-02-13 16:00 | 83 | 80 |  |  | 43874.6667 | 101 | 99
2020-02-13 16:30 | 80 | 77 |  |  | 43874.6875 | 99 | 97
2020-02-13 17:00 | 82 | 78 |  |  | 43874.7083 | 100 | 98
2020-02-13 17:30 | 86 | 82 |  |  | 43874.7292 | 102 | 100
2020-02-13 18:00 | 87 | 84 |  |  | 43874.75 | 104 | 101
2020-02-13 18:30 | 90 | 86 |  |  | 43874.7708 | 105 | 102
2020-02-13 19:00 | 92 | 89 |  |  | 43874.7917 | 108 | 105
2020-02-13 19:30 | 90 | 87 |  |  | 43874.8125 | 106 | 103
2020-02-13 20:00 | 90 | 86 |  |  | 43874.8333 | 105 | 102
2020-02-13 20:30 | 91 | 87 |  |  | 43874.8542 | 105 | 101
2020-02-13 21:00 | 90 | 84 |  |  | 43874.875 | 102 | 98
2020-02-13 21:30 | 84 | 79 |  |  | 43874.8958 | 94 | 91
2020-02-13 22:00 | 82 | 77 |  |  | 43874.9167 | 92 | 89
2020-02-13 22:30 | 80 | 77 |  |  | 43874.9375 | 90 | 89
2020-02-13 23:00 | 79 | 75 |  |  | 43874.9583 | 86 | 85
2020-02-13 23:30 | 75 | 70 |  |  | 43874.9792 | 83 | 81
2020-02-14 | 71 | 66 |  |  | 43875 | 79 | 77
2020-02-14 00:30 | 69 | 64 |  |  | 43875.0208 | 75 | 73
2020-02-14 01:00 | 66 | 59 |  |  | 43875.0417 | 72 | 69
2020-02-14 01:30 | 65 | 57 |  |  | 43875.0625 | 70 | 67
2020-02-14 02:00 | 62 | 54 |  |  | 43875.0833 | 66 | 63
2020-02-14 02:30 | 58 | 50 |  |  | 43875.1042 | 63 | 59
2020-02-14 03:00 | 58 | 50 |  |  | 43875.125 | 62 | 59
2020-02-14 03:30 | 57 | 49 |  |  | 43875.1458 | 61 | 57
2020-02-14 04:00 | 57 | 48 |  |  | 43875.1667 | 60 | 57
2020-02-14 04:30 | 58 | 49 |  |  | 43875.1875 | 62 | 58
2020-02-14 05:00 | 60 | 52 |  |  | 43875.2083 | 64 | 61
2020-02-14 05:30 | 62 | 54 |  |  | 43875.2292 | 68 | 65
2020-02-14 06:00 | 63 | 57 |  |  | 43875.25 | 72 | 70
2020-02-14 06:30 | 64 | 60 |  |  | 43875.2708 | 77 | 77
2020-02-14 07:00 | 66 | 64 |  |  | 43875.2917 | 82 | 82
2020-02-14 07:30 | 71 | 68 |  |  | 43875.3125 | 90 | 89
2020-02-14 08:00 | 69 | 64 |  |  | 43875.3333 | 89 | 87
2020-02-14 08:30 | 69 | 64 |  |  | 43875.3542 | 90 | 89
2020-02-14 09:00 | 66 | 62 |  |  | 43875.375 | 88 | 87
2020-02-14 09:30 | 67 | 63 |  |  | 43875.3958 | 89 | 88
2020-02-14 10:00 | 70 | 67 |  |  | 43875.4167 | 91 | 90
2020-02-14 10:30 | 68 | 65 |  |  | 43875.4375 | 87 | 87
2020-02-14 11:00 | 68 | 65 |  |  | 43875.4583 | 86 | 86
2020-02-14 11:30 | 72 | 68 |  |  | 43875.4792 | 92 | 91
2020-02-14 12:00 | 71 | 65 |  |  | 43875.5 | 93 | 90
2020-02-14 12:30 | 68 | 62 |  |  | 43875.5208 | 86 | 83
2020-02-14 13:00 | 70 | 65 |  |  | 43875.5417 | 92 | 89
2020-02-14 13:30 | 77 | 72 |  |  | 43875.5625 | 96 | 94
2020-02-14 14:00 | 85 | 80 |  |  | 43875.5833 | 99 | 96
2020-02-14 14:30 | 91 | 86 |  |  | 43875.6042 | 105 | 103
2020-02-14 15:00 | 91 | 86 |  |  | 43875.625 | 106 | 103
2020-02-14 15:30 | 91 | 87 |  |  | 43875.6458 | 107 | 105
2020-02-14 16:00 | 91 | 86 |  |  | 43875.6667 | 110 | 108
2020-02-14 16:30 | 92 | 87 |  |  | 43875.6875 | 110 | 107
2020-02-14 17:00 | 92 | 87 |  |  | 43875.7083 | 114 | 111
2020-02-14 17:30 | 94 | 89 |  |  | 43875.7292 | 115 | 111
2020-02-14 18:00 | 94 | 89 |  |  | 43875.75 | 112 | 108
2020-02-14 18:30 | 93 | 88 |  |  | 43875.7708 | 109 | 105
2020-02-14 19:00 | 94 | 90 |  |  | 43875.7917 | 112 | 108
2020-02-14 19:30 | 95 | 90 |  |  | 43875.8125 | 110 | 106
2020-02-14 20:00 | 93 | 88 |  |  | 43875.8333 | 109 | 104
2020-02-14 20:30 | 91 | 86 |  |  | 43875.8542 | 107 | 103
2020-02-14 21:00 | 87 | 84 |  |  | 43875.875 | 102 | 101
2020-02-14 21:30 | 80 | 78 |  |  | 43875.8958 | 94 | 94
2020-02-14 22:00 | 77 | 75 |  |  | 43875.9167 | 92 | 92
2020-02-14 22:30 | 77 | 74 |  |  | 43875.9375 | 92 | 92
2020-02-14 23:00 | 75 | 73 |  |  | 43875.9583 | 87 | 87
2020-02-14 23:30 | 71 | 69 |  |  | 43875.9792 | 83 | 83
2020-02-15 | 65 | 63 |  |  | 43876 | 77 | 77
2020-02-15 00:30 | 64 | 61 |  |  | 43876.0208 | 73 | 73
2020-02-15 01:00 | 59 | 56 |  |  | 43876.0417 | 68 | 68
2020-02-15 01:30 | 60 | 56 |  |  | 43876.0625 | 68 | 68
2020-02-15 02:00 | 61 | 56 |  |  | 43876.0833 | 69 | 68
2020-02-15 02:30 | 60 | 55 |  |  | 43876.1042 | 68 | 67
2020-02-15 03:00 | 59 | 54 |  |  | 43876.125 | 68 | 67
2020-02-15 03:30 | 57 | 52 |  |  | 43876.1458 | 66 | 65
2020-02-15 04:00 | 57 | 51 |  |  | 43876.1667 | 65 | 65
2020-02-15 04:30 | 55 | 50 |  |  | 43876.1875 | 64 | 64
2020-02-15 05:00 | 56 | 51 |  |  | 43876.2083 | 65 | 65
2020-02-15 05:30 | 56 | 51 |  |  | 43876.2292 | 66 | 66
2020-02-15 06:00 | 55 | 50 |  |  | 43876.25 | 65 | 65
2020-02-15 06:30 | 54 | 49 |  |  | 43876.2708 | 66 | 65
2020-02-15 07:00 | 53 | 49 |  |  | 43876.2917 | 67 | 67
2020-02-15 07:30 | 50 | 47 |  |  | 43876.3125 | 65 | 65
2020-02-15 08:00 | 49 | 47 |  |  | 43876.3333 | 66 | 66
2020-02-15 08:30 | 50 | 48 |  |  | 43876.3542 | 70 | 69
2020-02-15 09:00 | 52 | 50 |  |  | 43876.375 | 73 | 73
2020-02-15 09:30 | 60 | 57 |  |  | 43876.3958 | 80 | 80
2020-02-15 10:00 | 62 | 59 |  |  | 43876.4167 | 80 | 80
2020-02-15 10:30 | 63 | 61 |  |  | 43876.4375 | 81 | 81
2020-02-15 11:00 | 68 | 67 |  |  | 43876.4583 | 86 | 86
2020-02-15 11:30 | 72 | 70 |  |  | 43876.4792 | 91 | 91
2020-02-15 12:00 | 77 | 73 |  |  | 43876.5 | 93 | 91
2020-02-15 12:30 | 77 | 72 |  |  | 43876.5208 | 89 | 86
2020-02-15 13:00 | 75 | 70 |  |  | 43876.5417 | 87 | 83
2020-02-15 13:30 | 80 | 76 |  |  | 43876.5625 | 91 | 87
2020-02-15 14:00 | 85 | 82 |  |  | 43876.5833 | 94 | 90
2020-02-15 14:30 | 85 | 81 |  |  | 43876.6042 | 92 | 87
2020-02-15 15:00 | 85 | 81 |  |  | 43876.625 | 93 | 89
2020-02-15 15:30 | 89 | 85 |  |  | 43876.6458 | 97 | 94
2020-02-15 16:00 | 92 | 88 |  |  | 43876.6667 | 104 | 100
2020-02-15 16:30 | 95 | 91 |  |  | 43876.6875 | 107 | 103
2020-02-15 17:00 | 102 | 91 |  |  | 43876.7083 | 106 | 106
2020-02-15 17:30 | 103 | 90 |  |  | 43876.7292 | 106 | 105
2020-02-15 18:00 | 105 | 92 |  |  | 43876.75 | 108 | 108
2020-02-15 18:30 | 108 | 94 |  |  | 43876.7708 | 112 | 111
2020-02-15 19:00 | 109 | 98 |  |  | 43876.7917 | 117 | 116
2020-02-15 19:30 | 109 | 99 |  |  | 43876.8125 | 118 | 118
2020-02-15 20:00 | 107 | 97 |  |  | 43876.8333 | 116 | 116
2020-02-15 20:30 | 109 | 97 |  |  | 43876.8542 | 115 | 115
2020-02-15 21:00 | 101 | 92 |  |  | 43876.875 | 111 | 110
2020-02-15 21:30 | 92 | 90 |  |  | 43876.8958 | 111 | 105
2020-02-15 22:00 | 87 | 85 |  |  | 43876.9167 | 109 | 101
2020-02-15 22:30 | 85 | 84 |  |  | 43876.9375 | 104 | 99
2020-02-15 23:00 | 83 | 83 |  |  | 43876.9583 | 99 | 96
2020-02-15 23:30 | 77 | 76 |  |  | 43876.9792 | 94 | 91
2020-02-16 | 72 | 72 |  |  | 43877 | 89 | 86
2020-02-16 00:30 | 73 | 71 |  |  | 43877.0208 | 89 | 85
2020-02-16 01:00 | 67 | 65 |  |  | 43877.0417 | 83 | 78
2020-02-16 01:30 | 65 | 63 |  |  | 43877.0625 | 81 | 76
2020-02-16 02:00 | 64 | 61 |  |  | 43877.0833 | 79 | 73
2020-02-16 02:30 | 62 | 59 |  |  | 43877.1042 | 78 | 71
2020-02-16 03:00 | 61 | 57 |  |  | 43877.125 | 77 | 70
2020-02-16 03:30 | 59 | 56 |  |  | 43877.1458 | 76 | 69
2020-02-16 04:00 | 61 | 57 |  |  | 43877.1667 | 77 | 70
2020-02-16 04:30 | 61 | 58 |  |  | 43877.1875 | 77 | 70
2020-02-16 05:00 | 62 | 58 |  |  | 43877.2083 | 78 | 70
2020-02-16 05:30 | 59 | 56 |  |  | 43877.2292 | 75 | 68
2020-02-16 06:00 | 57 | 54 |  |  | 43877.25 | 74 | 68
2020-02-16 06:30 | 56 | 53 |  |  | 43877.2708 | 74 | 68
2020-02-16 07:00 | 56 | 53 |  |  | 43877.2917 | 74 | 68
2020-02-16 07:30 | 53 | 51 |  |  | 43877.3125 | 71 | 67
2020-02-16 08:00 | 53 | 51 |  |  | 43877.3333 | 71 | 68
2020-02-16 08:30 | 57 | 56 |  |  | 43877.3542 | 74 | 71
2020-02-16 09:00 | 59 | 58 |  |  | 43877.375 | 77 | 74
2020-02-16 09:30 | 64 | 63 |  |  | 43877.3958 | 81 | 78
2020-02-16 10:00 | 67 | 65 |  |  | 43877.4167 | 84 | 78
2020-02-16 10:30 | 69 | 68 |  |  | 43877.4375 | 87 | 81
2020-02-16 11:00 | 71 | 70 |  |  | 43877.4583 | 89 | 85
2020-02-16 11:30 | 72 | 71 |  |  | 43877.4792 | 88 | 83
2020-02-16 12:00 | 75 | 74 |  |  | 43877.5 | 90 | 85
2020-02-16 12:30 | 76 | 75 |  |  | 43877.5208 | 91 | 87
2020-02-16 13:00 | 77 | 77 |  |  | 43877.5417 | 94 | 91
2020-02-16 13:30 | 83 | 82 |  |  | 43877.5625 | 99 | 95
2020-02-16 14:00 | 84 | 83 |  |  | 43877.5833 | 99 | 95
2020-02-16 14:30 | 87 | 86 |  |  | 43877.6042 | 103 | 98
2020-02-16 15:00 | 87 | 85 |  |  | 43877.625 | 104 | 97
2020-02-16 15:30 | 90 | 88 |  |  | 43877.6458 | 106 | 99
2020-02-16 16:00 | 93 | 92 |  |  | 43877.6667 | 110 | 103
2020-02-16 16:30 | 97 | 96 |  |  | 43877.6875 | 117 | 110
2020-02-16 17:00 | 99 | 98 |  |  | 43877.7083 | 120 | 113
2020-02-16 17:30 | 95 | 94 |  |  | 43877.7292 | 122 | 111
2020-02-16 18:00 | 96 | 93 |  |  | 43877.75 | 125 | 112
2020-02-16 18:30 | 96 | 93 |  |  | 43877.7708 | 127 | 113
2020-02-16 19:00 | 97 | 94 |  |  | 43877.7917 | 130 | 116
2020-02-16 19:30 | 96 | 94 |  |  | 43877.8125 | 130 | 116
2020-02-16 20:00 | 95 | 93 |  |  | 43877.8333 | 128 | 115
2020-02-16 20:30 | 92 | 91 |  |  | 43877.8542 | 121 | 113
2020-02-16 21:00 | 87 | 86 |  |  | 43877.875 | 113 | 108
2020-02-16 21:30 | 85 | 84 |  |  | 43877.8958 | 111 | 106
2020-02-16 22:00 | 82 | 81 |  |  | 43877.9167 | 111 | 104
2020-02-16 22:30 | 86 | 83 |  |  | 43877.9375 | 113 | 103
2020-02-16 23:00 | 84 | 80 |  |  | 43877.9583 | 109 | 97
2020-02-16 23:30 | 80 | 74 |  |  | 43877.9792 | 105 | 91
2020-02-17 | 75 | 69 |  |  | 43878 | 100 | 85
2020-02-17 00:30 | 72 | 67 |  |  | 43878.0208 | 95 | 81
2020-02-17 01:00 | 66 | 63 |  |  | 43878.0417 | 85 | 76
2020-02-17 01:30 | 67 | 63 |  |  | 43878.0625 | 84 | 75
2020-02-17 02:00 | 68 | 64 |  |  | 43878.0833 | 85 | 75
2020-02-17 02:30 | 67 | 62 |  |  | 43878.1042 | 84 | 74
2020-02-17 03:00 | 65 | 60 |  |  | 43878.125 | 82 | 72
2020-02-17 03:30 | 65 | 61 |  |  | 43878.1458 | 83 | 73
2020-02-17 04:00 | 66 | 61 |  |  | 43878.1667 | 84 | 73
2020-02-17 04:30 | 63 | 58 |  |  | 43878.1875 | 81 | 70
2020-02-17 05:00 | 64 | 59 |  |  | 43878.2083 | 82 | 72
2020-02-17 05:30 | 65 | 61 |  |  | 43878.2292 | 83 | 75
2020-02-17 06:00 | 67 | 64 |  |  | 43878.25 | 88 | 80
2020-02-17 06:30 | 73 | 70 |  |  | 43878.2708 | 99 | 90
2020-02-17 07:00 | 77 | 75 |  |  | 43878.2917 | 105 | 98
2020-02-17 07:30 | 83 | 81 |  |  | 43878.3125 | 114 | 107
2020-02-17 08:00 | 88 | 85 |  |  | 43878.3333 | 124 | 112
2020-02-17 08:30 | 87 | 83 |  |  | 43878.3542 | 126 | 113
2020-02-17 09:00 | 85 | 80 |  |  | 43878.375 | 124 | 107
2020-02-17 09:30 | 89 | 85 |  |  | 43878.3958 | 121 | 100
2020-02-17 10:00 | 88 | 86 |  |  | 43878.4167 | 111 | 100
2020-02-17 10:30 | 88 | 87 |  |  | 43878.4375 | 106 | 97
2020-02-17 11:00 | 88 | 87 |  |  | 43878.4583 | 107 | 97
2020-02-17 11:30 | 90 | 89 |  |  | 43878.4792 | 109 | 100
2020-02-17 12:00 | 92 | 91 |  |  | 43878.5 | 112 | 104
2020-02-17 12:30 | 95 | 94 |  |  | 43878.5208 | 116 | 107
2020-02-17 13:00 | 96 | 95 |  |  | 43878.5417 | 118 | 109
2020-02-17 13:30 | 97 | 94 |  |  | 43878.5625 | 122 | 118
2020-02-17 14:00 | 97 | 94 |  |  | 43878.5833 | 122 | 119
2020-02-17 14:30 | 99 | 96 |  |  | 43878.6042 | 126 | 122
2020-02-17 15:00 | 101 | 97 |  |  | 43878.625 | 126 | 122
2020-02-17 15:30 | 103 | 100 |  |  | 43878.6458 | 128 | 125
2020-02-17 16:00 | 108 | 103 |  |  | 43878.6667 | 134 | 127
2020-02-17 16:30 | 115 | 107 |  |  | 43878.6875 | 143 | 131
2020-02-17 17:00 | 117 | 107 |  |  | 43878.7083 | 147 | 132
2020-02-17 17:30 | 114 | 106 |  |  | 43878.7292 | 145 | 131
2020-02-17 18:00 | 112 | 105 |  |  | 43878.75 | 139 | 129
2020-02-17 18:30 | 109 | 102 |  |  | 43878.7708 | 135 | 126
2020-02-17 19:00 | 110 | 107 |  |  | 43878.7917 | 135 | 131
2020-02-17 19:30 | 109 | 106 |  |  | 43878.8125 | 135 | 130
2020-02-17 20:00 | 106 | 102 |  |  | 43878.8333 | 131 | 126
2020-02-17 20:30 | 102 | 99 |  |  | 43878.8542 | 128 | 124
2020-02-17 21:00 | 96 | 93 |  |  | 43878.875 | 121 | 117
2020-02-17 21:30 | 95 | 92 |  |  | 43878.8958 | 118 | 114
2020-02-17 22:00 | 95 | 92 |  |  | 43878.9167 | 115 | 111
2020-02-17 22:30 | 92 | 88 |  |  | 43878.9375 | 111 | 108
2020-02-17 23:00 | 90 | 85 |  |  | 43878.9583 | 107 | 103
2020-02-17 23:30 | 86 | 80 |  |  | 43878.9792 | 102 | 97
2020-02-18 | 81 | 75 |  |  | 43879 | 96 | 92
2020-02-18 00:30 | 78 | 70 |  |  | 43879.0208 | 91 | 86
2020-02-18 01:00 | 75 | 66 |  |  | 43879.0417 | 87 | 81
2020-02-18 01:30 | 74 | 64 |  |  | 43879.0625 | 85 | 78
2020-02-18 02:00 | 75 | 65 |  |  | 43879.0833 | 87 | 79
2020-02-18 02:30 | 74 | 63 |  |  | 43879.1042 | 85 | 78
2020-02-18 03:00 | 69 | 62 |  |  | 43879.125 | 84 | 76
2020-02-18 03:30 | 62 | 61 |  |  | 43879.1458 | 77 | 73
2020-02-18 04:00 | 61 | 60 |  |  | 43879.1667 | 76 | 72
2020-02-18 04:30 | 61 | 60 |  |  | 43879.1875 | 76 | 72
2020-02-18 05:00 | 64 | 62 |  |  | 43879.2083 | 79 | 75
2020-02-18 05:30 | 66 | 65 |  |  | 43879.2292 | 81 | 78
2020-02-18 06:00 | 70 | 70 |  |  | 43879.25 | 86 | 84
2020-02-18 06:30 | 76 | 75 |  |  | 43879.2708 | 94 | 92
2020-02-18 07:00 | 81 | 81 |  |  | 43879.2917 | 101 | 100
2020-02-18 07:30 | 84 | 84 |  |  | 43879.3125 | 108 | 106
2020-02-18 08:00 | 82 | 82 |  |  | 43879.3333 | 109 | 107
2020-02-18 08:30 | 88 | 86 |  |  | 43879.3542 | 121 | 115
2020-02-18 09:00 | 90 | 88 |  |  | 43879.375 | 121 | 113
2020-02-18 09:30 | 91 | 88 |  |  | 43879.3958 | 120 | 111
2020-02-18 10:00 | 94 | 91 |  |  | 43879.4167 | 125 | 116
2020-02-18 10:30 | 94 | 91 |  |  | 43879.4375 | 125 | 116
2020-02-18 11:00 | 94 | 91 |  |  | 43879.4583 | 124 | 116
2020-02-18 11:30 | 91 | 88 |  |  | 43879.4792 | 121 | 114
2020-02-18 12:00 | 93 | 90 |  |  | 43879.5 | 122 | 115
2020-02-18 12:30 | 95 | 92 |  |  | 43879.5208 | 122 | 115
2020-02-18 13:00 | 92 | 90 |  |  | 43879.5417 | 121 | 115
2020-02-18 13:30 | 93 | 91 |  |  | 43879.5625 | 123 | 116
2020-02-18 14:00 | 95 | 93 |  |  | 43879.5833 | 124 | 116
2020-02-18 14:30 | 96 | 93 |  |  | 43879.6042 | 127 | 117
2020-02-18 15:00 | 95 | 93 |  |  | 43879.625 | 125 | 116
2020-02-18 15:30 | 101 | 98 |  |  | 43879.6458 | 129 | 121
2020-02-18 16:00 | 110 | 108 |  |  | 43879.6667 | 136 | 128
2020-02-18 16:30 | 113 | 112 |  |  | 43879.6875 | 144 | 134
2020-02-18 17:00 | 112 | 111 |  |  | 43879.7083 | 146 | 136
2020-02-18 17:30 | 111 | 109 |  |  | 43879.7292 | 147 | 133
2020-02-18 18:00 | 112 | 110 |  |  | 43879.75 | 147 | 133
2020-02-18 18:30 | 111 | 110 |  |  | 43879.7708 | 140 | 130
2020-02-18 19:00 | 113 | 111 |  |  | 43879.7917 | 142 | 134
2020-02-18 19:30 | 112 | 111 |  |  | 43879.8125 | 142 | 134
2020-02-18 20:00 | 110 | 109 |  |  | 43879.8333 | 141 | 132
2020-02-18 20:30 | 110 | 108 |  |  | 43879.8542 | 139 | 131
2020-02-18 21:00 | 106 | 105 |  |  | 43879.875 | 134 | 125
2020-02-18 21:30 | 102 | 102 |  |  | 43879.8958 | 127 | 121
2020-02-18 22:00 | 101 | 101 |  |  | 43879.9167 | 116 | 112
2020-02-18 22:30 | 105 | 104 |  |  | 43879.9375 | 111 | 105
2020-02-18 23:00 | 96 | 96 |  |  | 43879.9583 | 113 | 108
2020-02-18 23:30 | 92 | 92 |  |  | 43879.9792 | 108 | 106
2020-02-19 | 87 | 86 |  |  | 43880 | 102 | 100
2020-02-19 00:30 | 85 | 84 |  |  | 43880.0208 | 99 | 96
2020-02-19 01:00 | 81 | 80 |  |  | 43880.0417 | 94 | 91
2020-02-19 01:30 | 80 | 78 |  |  | 43880.0625 | 92 | 89
2020-02-19 02:00 | 80 | 79 |  |  | 43880.0833 | 92 | 88
2020-02-19 02:30 | 78 | 77 |  |  | 43880.1042 | 90 | 86
2020-02-19 03:00 | 77 | 75 |  |  | 43880.125 | 89 | 85
2020-02-19 03:30 | 75 | 73 |  |  | 43880.1458 | 88 | 83
2020-02-19 04:00 | 73 | 72 |  |  | 43880.1667 | 86 | 81
2020-02-19 04:30 | 74 | 73 |  |  | 43880.1875 | 89 | 84
2020-02-19 05:00 | 77 | 76 |  |  | 43880.2083 | 91 | 86
2020-02-19 05:30 | 78 | 77 |  |  | 43880.2292 | 93 | 89
2020-02-19 06:00 | 81 | 80 |  |  | 43880.25 | 96 | 93
2020-02-19 06:30 | 82 | 81 |  |  | 43880.2708 | 102 | 97
2020-02-19 07:00 | 84 | 83 |  |  | 43880.2917 | 109 | 102
2020-02-19 07:30 | 93 | 91 |  |  | 43880.3125 | 120 | 113
2020-02-19 08:00 | 91 | 89 |  |  | 43880.3333 | 118 | 109
2020-02-19 08:30 | 86 | 84 |  |  | 43880.3542 | 118 | 110
2020-02-19 09:00 | 89 | 86 |  |  | 43880.375 | 121 | 113
2020-02-19 09:30 | 97 | 95 |  |  | 43880.3958 | 129 | 122
2020-02-19 10:00 | 96 | 94 |  |  | 43880.4167 | 127 | 121
2020-02-19 10:30 | 93 | 91 |  |  | 43880.4375 | 127 | 121
2020-02-19 11:00 | 94 | 92 |  |  | 43880.4583 | 128 | 120
2020-02-19 11:30 | 101 | 98 |  |  | 43880.4792 | 136 | 127
2020-02-19 12:00 | 102 | 100 |  |  | 43880.5 | 137 | 129
2020-02-19 12:30 | 103 | 101 |  |  | 43880.5208 | 140 | 133
2020-02-19 13:00 | 108 | 106 |  |  | 43880.5417 | 141 | 135
2020-02-19 13:30 | 117 | 115 |  |  | 43880.5625 | 150 | 142
2020-02-19 14:00 | 116 | 115 |  |  | 43880.5833 | 152 | 144
2020-02-19 14:30 | 119 | 115 |  |  | 43880.6042 | 161 | 145
2020-02-19 15:00 | 120 | 115 |  |  | 43880.625 | 162 | 145
2020-02-19 15:30 | 117 | 112 |  |  | 43880.6458 | 160 | 142
2020-02-19 16:00 | 118 | 111 |  |  | 43880.6667 | 159 | 144
2020-02-19 16:30 | 126 | 114 |  |  | 43880.6875 | 157 | 146
2020-02-19 17:00 | 129 | 117 |  |  | 43880.7083 | 156 | 147
2020-02-19 17:30 | 129 | 117 |  |  | 43880.7292 | 156 | 145
2020-02-19 18:00 | 118 | 115 |  |  | 43880.75 | 165 | 143
2020-02-19 18:30 | 115 | 114 |  |  | 43880.7708 | 164 | 140
2020-02-19 19:00 | 118 | 117 |  |  | 43880.7917 | 165 | 140
2020-02-19 19:30 | 115 | 114 |  |  | 43880.8125 | 162 | 138
2020-02-19 20:00 | 110 | 108 |  |  | 43880.8333 | 160 | 136
2020-02-19 20:30 | 105 | 104 |  |  | 43880.8542 | 155 | 130
2020-02-19 21:00 | 99 | 98 |  |  | 43880.875 | 140 | 122
2020-02-19 21:30 | 93 | 92 |  |  | 43880.8958 | 131 | 112
2020-02-19 22:00 | 95 | 94 |  |  | 43880.9167 | 124 | 111
2020-02-19 22:30 | 85 | 85 |  |  | 43880.9375 | 110 | 101
2020-02-19 23:00 | 81 | 81 |  |  | 43880.9583 | 105 | 95
2020-02-19 23:30 | 77 | 77 |  |  | 43880.9792 | 102 | 89
2020-02-20 | 73 | 73 |  |  | 43881 | 95 | 87
2020-02-20 00:30 | 73 | 73 |  |  | 43881.0208 | 93 | 85
2020-02-20 01:00 | 72 | 72 |  |  | 43881.0417 | 91 | 83
2020-02-20 01:30 | 69 | 69 |  |  | 43881.0625 | 89 | 80
2020-02-20 02:00 | 68 | 68 |  |  | 43881.0833 | 87 | 78
2020-02-20 02:30 | 67 | 67 |  |  | 43881.1042 | 87 | 76
2020-02-20 03:00 | 66 | 66 |  |  | 43881.125 | 87 | 76
2020-02-20 03:30 | 65 | 65 |  |  | 43881.1458 | 87 | 76
2020-02-20 04:00 | 64 | 64 |  |  | 43881.1667 | 85 | 74
2020-02-20 04:30 | 64 | 64 |  |  | 43881.1875 | 86 | 74
2020-02-20 05:00 | 64 | 64 |  |  | 43881.2083 | 86 | 74
2020-02-20 05:30 | 67 | 66 |  |  | 43881.2292 | 88 | 77
2020-02-20 06:00 | 69 | 69 |  |  | 43881.25 | 90 | 81
2020-02-20 06:30 | 74 | 74 |  |  | 43881.2708 | 99 | 90
2020-02-20 07:00 | 69 | 68 |  |  | 43881.2917 | 104 | 90
2020-02-20 07:30 | 69 | 68 |  |  | 43881.3125 | 108 | 95
2020-02-20 08:00 | 68 | 68 |  |  | 43881.3333 | 106 | 95
2020-02-20 08:30 | 67 | 66 |  |  | 43881.3542 | 104 | 94
2020-02-20 09:00 | 66 | 65 |  |  | 43881.375 | 103 | 92
2020-02-20 09:30 | 70 | 70 |  |  | 43881.3958 | 107 | 96
2020-02-20 10:00 | 72 | 72 |  |  | 43881.4167 | 111 | 100
2020-02-20 10:30 | 70 | 70 |  |  | 43881.4375 | 112 | 102
2020-02-20 11:00 | 70 | 70 |  |  | 43881.4583 | 114 | 104
2020-02-20 11:30 | 72 | 72 |  |  | 43881.4792 | 120 | 108
2020-02-20 12:00 | 75 | 74 |  |  | 43881.5 | 126 | 112
2020-02-20 12:30 | 77 | 77 |  |  | 43881.5208 | 128 | 114
2020-02-20 13:00 | 80 | 79 |  |  | 43881.5417 | 130 | 116
2020-02-20 13:30 | 83 | 82 |  |  | 43881.5625 | 132 | 120
2020-02-20 14:00 | 85 | 84 |  |  | 43881.5833 | 134 | 122
2020-02-20 14:30 | 86 | 86 |  |  | 43881.6042 | 134 | 122
2020-02-20 15:00 | 88 | 87 |  |  | 43881.625 | 136 | 123
2020-02-20 15:30 | 91 | 88 |  |  | 43881.6458 | 134 | 124
2020-02-20 16:00 | 95 | 92 |  |  | 43881.6667 | 136 | 125
2020-02-20 16:30 | 101 | 97 |  |  | 43881.6875 | 141 | 129
2020-02-20 17:00 | 99 | 96 |  |  | 43881.7083 | 142 | 129
2020-02-20 17:30 | 96 | 92 |  |  | 43881.7292 | 140 | 127
2020-02-20 18:00 | 96 | 91 |  |  | 43881.75 | 138 | 124
2020-02-20 18:30 | 93 | 89 |  |  | 43881.7708 | 129 | 119
2020-02-20 19:00 | 96 | 95 |  |  | 43881.7917 | 132 | 123
2020-02-20 19:30 | 104 | 103 |  |  | 43881.8125 | 137 | 128
2020-02-20 20:00 | 101 | 100 |  |  | 43881.8333 | 135 | 124
2020-02-20 20:30 | 101 | 100 |  |  | 43881.8542 | 133 | 123
2020-02-20 21:00 | 98 | 98 |  |  | 43881.875 | 128 | 118
2020-02-20 21:30 | 93 | 92 |  |  | 43881.8958 | 121 | 111
2020-02-20 22:00 | 94 | 93 |  |  | 43881.9167 | 119 | 108
2020-02-20 22:30 | 92 | 92 |  |  | 43881.9375 | 112 | 105
2020-02-20 23:00 | 90 | 89 |  |  | 43881.9583 | 106 | 100
2020-02-20 23:30 | 84 | 83 |  |  | 43881.9792 | 100 | 95
2020-02-21 | 79 | 78 |  |  | 43882 | 96 | 89
2020-02-21 00:30 | 75 | 72 |  |  | 43882.0208 | 89 | 82
2020-02-21 01:00 | 72 | 69 |  |  | 43882.0417 | 87 | 79
2020-02-21 01:30 | 71 | 68 |  |  | 43882.0625 | 85 | 77
2020-02-21 02:00 | 70 | 67 |  |  | 43882.0833 | 85 | 76
2020-02-21 02:30 | 71 | 68 |  |  | 43882.1042 | 85 | 76
2020-02-21 03:00 | 70 | 67 |  |  | 43882.125 | 84 | 75
2020-02-21 03:30 | 69 | 66 |  |  | 43882.1458 | 83 | 74
2020-02-21 04:00 | 68 | 65 |  |  | 43882.1667 | 82 | 73
2020-02-21 04:30 | 68 | 64 |  |  | 43882.1875 | 83 | 73
2020-02-21 05:00 | 69 | 65 |  |  | 43882.2083 | 83 | 74
2020-02-21 05:30 | 67 | 65 |  |  | 43882.2292 | 83 | 74
2020-02-21 06:00 | 67 | 64 |  |  | 43882.25 | 83 | 76
2020-02-21 06:30 | 73 | 71 |  |  | 43882.2708 | 94 | 86
2020-02-21 07:00 | 77 | 74 |  |  | 43882.2917 | 101 | 93
2020-02-21 07:30 | 82 | 80 |  |  | 43882.3125 | 106 | 100
2020-02-21 08:00 | 81 | 80 |  |  | 43882.3333 | 107 | 103
2020-02-21 08:30 | 78 | 78 |  |  | 43882.3542 | 104 | 101
2020-02-21 09:00 | 80 | 79 |  |  | 43882.375 | 108 | 105
2020-02-21 09:30 | 81 | 80 |  |  | 43882.3958 | 110 | 107
2020-02-21 10:00 | 86 | 85 |  |  | 43882.4167 | 113 | 110
2020-02-21 10:30 | 88 | 86 |  |  | 43882.4375 | 112 | 111
2020-02-21 11:00 | 89 | 87 |  |  | 43882.4583 | 114 | 114
2020-02-21 11:30 | 92 | 90 |  |  | 43882.4792 | 115 | 114
2020-02-21 12:00 | 91 | 90 |  |  | 43882.5 | 114 | 113
2020-02-21 12:30 | 92 | 90 |  |  | 43882.5208 | 112 | 112
2020-02-21 13:00 | 92 | 90 |  |  | 43882.5417 | 107 | 106
2020-02-21 13:30 | 90 | 87 |  |  | 43882.5625 | 107 | 105
2020-02-21 14:00 | 93 | 90 |  |  | 43882.5833 | 112 | 111
2020-02-21 14:30 | 94 | 91 |  |  | 43882.6042 | 114 | 113
2020-02-21 15:00 | 92 | 89 |  |  | 43882.625 | 109 | 108
2020-02-21 15:30 | 95 | 93 |  |  | 43882.6458 | 113 | 112
2020-02-21 16:00 | 101 | 98 |  |  | 43882.6667 | 117 | 116
2020-02-21 16:30 | 103 | 100 |  |  | 43882.6875 | 120 | 118
2020-02-21 17:00 | 104 | 102 |  |  | 43882.7083 | 122 | 120
2020-02-21 17:30 | 104 | 100 |  |  | 43882.7292 | 119 | 117
2020-02-21 18:00 | 104 | 100 |  |  | 43882.75 | 117 | 114
2020-02-21 18:30 | 103 | 99 |  |  | 43882.7708 | 115 | 112
2020-02-21 19:00 | 105 | 101 |  |  | 43882.7917 | 118 | 114
2020-02-21 19:30 | 102 | 98 |  |  | 43882.8125 | 116 | 112
2020-02-21 20:00 | 101 | 96 |  |  | 43882.8333 | 114 | 110
2020-02-21 20:30 | 97 | 94 |  |  | 43882.8542 | 109 | 107
2020-02-21 21:00 | 94 | 92 |  |  | 43882.875 | 105 | 105
2020-02-21 21:30 | 90 | 88 |  |  | 43882.8958 | 101 | 101
2020-02-21 22:00 | 88 | 85 |  |  | 43882.9167 | 100 | 98
2020-02-21 22:30 | 88 | 84 |  |  | 43882.9375 | 100 | 98
2020-02-21 23:00 | 86 | 81 |  |  | 43882.9583 | 96 | 94
2020-02-21 23:30 | 80 | 75 |  |  | 43882.9792 | 90 | 88
2020-02-22 | 74 | 68 |  |  | 43883 | 83 | 80
2020-02-22 00:30 | 71 | 65 |  |  | 43883.0208 | 79 | 76
2020-02-22 01:00 | 69 | 63 |  |  | 43883.0417 | 76 | 73
2020-02-22 01:30 | 69 | 62 |  |  | 43883.0625 | 75 | 72
2020-02-22 02:00 | 69 | 61 |  |  | 43883.0833 | 74 | 71
2020-02-22 02:30 | 69 | 61 |  |  | 43883.1042 | 73 | 70
2020-02-22 03:00 | 68 | 61 |  |  | 43883.125 | 72 | 69
2020-02-22 03:30 | 66 | 59 |  |  | 43883.1458 | 71 | 67
2020-02-22 04:00 | 65 | 58 |  |  | 43883.1667 | 70 | 67
2020-02-22 04:30 | 64 | 56 |  |  | 43883.1875 | 69 | 65
2020-02-22 05:00 | 64 | 56 |  |  | 43883.2083 | 68 | 64
2020-02-22 05:30 | 62 | 54 |  |  | 43883.2292 | 68 | 64
2020-02-22 06:00 | 60 | 53 |  |  | 43883.25 | 66 | 63
2020-02-22 06:30 | 60 | 53 |  |  | 43883.2708 | 67 | 64
2020-02-22 07:00 | 60 | 54 |  |  | 43883.2917 | 68 | 67
2020-02-22 07:30 | 61 | 56 |  |  | 43883.3125 | 71 | 70
2020-02-22 08:00 | 59 | 55 |  |  | 43883.3333 | 71 | 70
2020-02-22 08:30 | 65 | 61 |  |  | 43883.3542 | 76 | 76
2020-02-22 09:00 | 65 | 61 |  |  | 43883.375 | 78 | 78
2020-02-22 09:30 | 68 | 65 |  |  | 43883.3958 | 80 | 80
2020-02-22 10:00 | 70 | 67 |  |  | 43883.4167 | 80 | 80
2020-02-22 10:30 | 67 | 64 |  |  | 43883.4375 | 82 | 82
2020-02-22 11:00 | 72 | 69 |  |  | 43883.4583 | 81 | 81
2020-02-22 11:30 | 74 | 69 |  |  | 43883.4792 | 82 | 81
2020-02-22 12:00 | 73 | 68 |  |  | 43883.5 | 87 | 85
2020-02-22 12:30 | 75 | 70 |  |  | 43883.5208 | 82 | 80
2020-02-22 13:00 | 78 | 73 |  |  | 43883.5417 | 87 | 85
2020-02-22 13:30 | 81 | 77 |  |  | 43883.5625 | 91 | 89
2020-02-22 14:00 | 83 | 78 |  |  | 43883.5833 | 91 | 89
2020-02-22 14:30 | 78 | 73 |  |  | 43883.6042 | 87 | 86
2020-02-22 15:00 | 74 | 69 |  |  | 43883.625 | 82 | 80
2020-02-22 15:30 | 70 | 65 |  |  | 43883.6458 | 78 | 76
2020-02-22 16:00 | 74 | 70 |  |  | 43883.6667 | 85 | 83
2020-02-22 16:30 | 75 | 71 |  |  | 43883.6875 | 88 | 86
2020-02-22 17:00 | 77 | 73 |  |  | 43883.7083 | 88 | 86
2020-02-22 17:30 | 76 | 72 |  |  | 43883.7292 | 89 | 87
2020-02-22 18:00 | 78 | 74 |  |  | 43883.75 | 90 | 89
2020-02-22 18:30 | 79 | 75 |  |  | 43883.7708 | 90 | 88
2020-02-22 19:00 | 83 | 79 |  |  | 43883.7917 | 94 | 92
2020-02-22 19:30 | 82 | 78 |  |  | 43883.8125 | 93 | 91
2020-02-22 20:00 | 81 | 77 |  |  | 43883.8333 | 92 | 90
2020-02-22 20:30 | 81 | 78 |  |  | 43883.8542 | 93 | 92
2020-02-22 21:00 | 79 | 75 |  |  | 43883.875 | 91 | 89
2020-02-22 21:30 | 76 | 71 |  |  | 43883.8958 | 87 | 85
2020-02-22 22:00 | 74 | 69 |  |  | 43883.9167 | 84 | 82
2020-02-22 22:30 | 76 | 71 |  |  | 43883.9375 | 86 | 84
2020-02-22 23:00 | 75 | 69 |  |  | 43883.9583 | 84 | 81
2020-02-22 23:30 | 69 | 62 |  |  | 43883.9792 | 77 | 74
2020-02-23 | 64 | 56 |  |  | 43884 | 72 | 67
2020-02-23 00:30 | 64 | 54 |  |  | 43884.0208 | 70 | 65
2020-02-23 01:00 | 62 | 52 |  |  | 43884.0417 | 67 | 62
2020-02-23 01:30 | 61 | 50 |  |  | 43884.0625 | 66 | 60
2020-02-23 02:00 | 61 | 51 |  |  | 43884.0833 | 65 | 61
2020-02-23 02:30 | 60 | 50 |  |  | 43884.1042 | 65 | 60
2020-02-23 03:00 | 60 | 49 |  |  | 43884.125 | 65 | 60
2020-02-23 03:30 | 58 | 49 |  |  | 43884.1458 | 63 | 60
2020-02-23 04:00 | 55 | 47 |  |  | 43884.1667 | 60 | 58
2020-02-23 04:30 | 56 | 48 |  |  | 43884.1875 | 61 | 59
2020-02-23 05:00 | 57 | 49 |  |  | 43884.2083 | 61 | 59
2020-02-23 05:30 | 55 | 47 |  |  | 43884.2292 | 60 | 58
2020-02-23 06:00 | 55 | 47 |  |  | 43884.25 | 60 | 58
2020-02-23 06:30 | 55 | 47 |  |  | 43884.2708 | 60 | 58
2020-02-23 07:00 | 52 | 44 |  |  | 43884.2917 | 59 | 57
2020-02-23 07:30 | 52 | 43 |  |  | 43884.3125 | 60 | 58
2020-02-23 08:00 | 50 | 42 |  |  | 43884.3333 | 57 | 55
2020-02-23 08:30 | 53 | 45 |  |  | 43884.3542 | 66 | 64
2020-02-23 09:00 | 56 | 48 |  |  | 43884.375 | 70 | 68
2020-02-23 09:30 | 60 | 54 |  |  | 43884.3958 | 68 | 66
2020-02-23 10:00 | 65 | 59 |  |  | 43884.4167 | 73 | 71
2020-02-23 10:30 | 66 | 61 |  |  | 43884.4375 | 76 | 74
2020-02-23 11:00 | 68 | 64 |  |  | 43884.4583 | 77 | 75
2020-02-23 11:30 | 63 | 58 |  |  | 43884.4792 | 75 | 74
2020-02-23 12:00 | 68 | 64 |  |  | 43884.5 | 82 | 81
2020-02-23 12:30 | 66 | 61 |  |  | 43884.5208 | 79 | 78
2020-02-23 13:00 | 65 | 60 |  |  | 43884.5417 | 76 | 75
2020-02-23 13:30 | 68 | 64 |  |  | 43884.5625 | 78 | 77
2020-02-23 14:00 | 71 | 66 |  |  | 43884.5833 | 79 | 78
2020-02-23 14:30 | 68 | 63 |  |  | 43884.6042 | 77 | 76
2020-02-23 15:00 | 63 | 58 |  |  | 43884.625 | 74 | 73
2020-02-23 15:30 | 64 | 60 |  |  | 43884.6458 | 73 | 72
2020-02-23 16:00 | 66 | 61 |  |  | 43884.6667 | 77 | 76
2020-02-23 16:30 | 66 | 62 |  |  | 43884.6875 | 77 | 76
2020-02-23 17:00 | 69 | 65 |  |  | 43884.7083 | 80 | 78
2020-02-23 17:30 | 73 | 68 |  |  | 43884.7292 | 82 | 81
2020-02-23 18:00 | 75 | 71 |  |  | 43884.75 | 85 | 84
2020-02-23 18:30 | 77 | 73 |  |  | 43884.7708 | 88 | 86
2020-02-23 19:00 | 81 | 77 |  |  | 43884.7917 | 92 | 91
2020-02-23 19:30 | 81 | 77 |  |  | 43884.8125 | 91 | 90
2020-02-23 20:00 | 79 | 75 |  |  | 43884.8333 | 90 | 89
2020-02-23 20:30 | 78 | 74 |  |  | 43884.8542 | 88 | 87
2020-02-23 21:00 | 75 | 70 |  |  | 43884.875 | 83 | 82
2020-02-23 21:30 | 72 | 67 |  |  | 43884.8958 | 82 | 80
2020-02-23 22:00 | 69 | 63 |  |  | 43884.9167 | 78 | 76
2020-02-23 22:30 | 68 | 62 |  |  | 43884.9375 | 78 | 76
2020-02-23 23:00 | 67 | 60 |  |  | 43884.9583 | 75 | 73
2020-02-23 23:30 | 65 | 58 |  |  | 43884.9792 | 73 | 71
2020-02-24 | 60 | 53 |  |  | 43885 | 68 | 65
2020-02-24 00:30 | 59 | 50 |  |  | 43885.0208 | 65 | 61
2020-02-24 01:00 | 57 | 48 |  |  | 43885.0417 | 62 | 58
2020-02-24 01:30 | 56 | 46 |  |  | 43885.0625 | 61 | 56
2020-02-24 02:00 | 56 | 46 |  |  | 43885.0833 | 60 | 56
2020-02-24 02:30 | 56 | 45 |  |  | 43885.1042 | 59 | 56
2020-02-24 03:00 | 55 | 46 |  |  | 43885.125 | 58 | 55
2020-02-24 03:30 | 55 | 45 |  |  | 43885.1458 | 58 | 55
2020-02-24 04:00 | 56 | 47 |  |  | 43885.1667 | 60 | 56
2020-02-24 04:30 | 57 | 48 |  |  | 43885.1875 | 62 | 58
2020-02-24 05:00 | 61 | 53 |  |  | 43885.2083 | 66 | 63
2020-02-24 05:30 | 65 | 58 |  |  | 43885.2292 | 70 | 67
2020-02-24 06:00 | 65 | 60 |  |  | 43885.25 | 72 | 70
2020-02-24 06:30 | 68 | 64 |  |  | 43885.2708 | 77 | 76
2020-02-24 07:00 | 71 | 66 |  |  | 43885.2917 | 82 | 81
2020-02-24 07:30 | 79 | 74 |  |  | 43885.3125 | 94 | 92
2020-02-24 08:00 | 83 | 78 |  |  | 43885.3333 | 100 | 98
2020-02-24 08:30 | 83 | 77 |  |  | 43885.3542 | 102 | 98
2020-02-24 09:00 | 86 | 78 |  |  | 43885.375 | 103 | 98
2020-02-24 09:30 | 89 | 81 |  |  | 43885.3958 | 103 | 98
2020-02-24 10:00 | 95 | 88 |  |  | 43885.4167 | 112 | 108
2020-02-24 10:30 | 99 | 90 |  |  | 43885.4375 | 119 | 111
2020-02-24 11:00 | 96 | 87 |  |  | 43885.4583 | 120 | 113
2020-02-24 11:30 | 89 | 78 |  |  | 43885.4792 | 108 | 100
2020-02-24 12:00 | 93 | 85 |  |  | 43885.5 | 111 | 104
2020-02-24 12:30 | 93 | 86 |  |  | 43885.5208 | 113 | 107
2020-02-24 13:00 | 87 | 80 |  |  | 43885.5417 | 112 | 105
2020-02-24 13:30 | 82 | 74 |  |  | 43885.5625 | 107 | 100
2020-02-24 14:00 | 83 | 75 |  |  | 43885.5833 | 99 | 92
2020-02-24 14:30 | 80 | 72 |  |  | 43885.6042 | 96 | 88
2020-02-24 15:00 | 84 | 76 |  |  | 43885.625 | 101 | 94
2020-02-24 15:30 | 88 | 81 |  |  | 43885.6458 | 106 | 99
2020-02-24 16:00 | 94 | 87 |  |  | 43885.6667 | 111 | 105
2020-02-24 16:30 | 95 | 88 |  |  | 43885.6875 | 113 | 105
2020-02-24 17:00 | 95 | 87 |  |  | 43885.7083 | 111 | 103
2020-02-24 17:30 | 96 | 87 |  |  | 43885.7292 | 111 | 102
2020-02-24 18:00 | 94 | 85 |  |  | 43885.75 | 108 | 98
2020-02-24 18:30 | 95 | 85 |  |  | 43885.7708 | 109 | 97
2020-02-24 19:00 | 97 | 88 |  |  | 43885.7917 | 112 | 101
2020-02-24 19:30 | 95 | 87 |  |  | 43885.8125 | 110 | 99
2020-02-24 20:00 | 92 | 84 |  |  | 43885.8333 | 105 | 96
2020-02-24 20:30 | 89 | 84 |  |  | 43885.8542 | 101 | 96
2020-02-24 21:00 | 87 | 81 |  |  | 43885.875 | 99 | 93
2020-02-24 21:30 | 84 | 77 |  |  | 43885.8958 | 94 | 87
2020-02-24 22:00 | 81 | 75 |  |  | 43885.9167 | 92 | 85
2020-02-24 22:30 | 78 | 72 |  |  | 43885.9375 | 86 | 82
2020-02-24 23:00 | 76 | 69 |  |  | 43885.9583 | 84 | 79
2020-02-24 23:30 | 74 | 66 |  |  | 43885.9792 | 81 | 75
2020-02-25 | 69 | 59 |  |  | 43886 | 76 | 69
2020-02-25 00:30 | 67 | 55 |  |  | 43886.0208 | 73 | 64
2020-02-25 01:00 | 64 | 52 |  |  | 43886.0417 | 70 | 60
2020-02-25 01:30 | 63 | 50 |  |  | 43886.0625 | 68 | 58
2020-02-25 02:00 | 62 | 49 |  |  | 43886.0833 | 66 | 56
2020-02-25 02:30 | 61 | 47 |  |  | 43886.1042 | 65 | 54
2020-02-25 03:00 | 60 | 48 |  |  | 43886.125 | 64 | 55
2020-02-25 03:30 | 60 | 48 |  |  | 43886.1458 | 64 | 55
2020-02-25 04:00 | 61 | 48 |  |  | 43886.1667 | 66 | 57
2020-02-25 04:30 | 63 | 51 |  |  | 43886.1875 | 68 | 60
2020-02-25 05:00 | 66 | 55 |  |  | 43886.2083 | 72 | 64
2020-02-25 05:30 | 68 | 58 |  |  | 43886.2292 | 74 | 67
2020-02-25 06:00 | 70 | 61 |  |  | 43886.25 | 77 | 71
2020-02-25 06:30 | 71 | 61 |  |  | 43886.2708 | 82 | 75
2020-02-25 07:00 | 76 | 64 |  |  | 43886.2917 | 89 | 80
2020-02-25 07:30 | 82 | 70 |  |  | 43886.3125 | 100 | 90
2020-02-25 08:00 | 82 | 71 |  |  | 43886.3333 | 103 | 92
2020-02-25 08:30 | 78 | 66 |  |  | 43886.3542 | 99 | 88
2020-02-25 09:00 | 77 | 66 |  |  | 43886.375 | 101 | 91
2020-02-25 09:30 | 82 | 72 |  |  | 43886.3958 | 106 | 96
2020-02-25 10:00 | 86 | 78 |  |  | 43886.4167 | 110 | 99
2020-02-25 10:30 | 87 | 79 |  |  | 43886.4375 | 110 | 100
2020-02-25 11:00 | 86 | 77 |  |  | 43886.4583 | 109 | 100
2020-02-25 11:30 | 85 | 77 |  |  | 43886.4792 | 105 | 96
2020-02-25 12:00 | 86 | 78 |  |  | 43886.5 | 103 | 93
2020-02-25 12:30 | 84 | 75 |  |  | 43886.5208 | 103 | 91
2020-02-25 13:00 | 87 | 78 |  |  | 43886.5417 | 106 | 95
2020-02-25 13:30 | 87 | 78 |  |  | 43886.5625 | 113 | 103
2020-02-25 14:00 | 89 | 81 |  |  | 43886.5833 | 110 | 99
2020-02-25 14:30 | 88 | 79 |  |  | 43886.6042 | 107 | 95
2020-02-25 15:00 | 88 | 79 |  |  | 43886.625 | 109 | 97
2020-02-25 15:30 | 92 | 82 |  |  | 43886.6458 | 114 | 102
2020-02-25 16:00 | 93 | 82 |  |  | 43886.6667 | 117 | 105
2020-02-25 16:30 | 93 | 83 |  |  | 43886.6875 | 114 | 102
2020-02-25 17:00 | 97 | 88 |  |  | 43886.7083 | 114 | 102
2020-02-25 17:30 | 96 | 87 |  |  | 43886.7292 | 114 | 101
2020-02-25 18:00 | 96 | 87 |  |  | 43886.75 | 114 | 101
2020-02-25 18:30 | 94 | 86 |  |  | 43886.7708 | 110 | 97
2020-02-25 19:00 | 97 | 90 |  |  | 43886.7917 | 114 | 102
2020-02-25 19:30 | 97 | 90 |  |  | 43886.8125 | 114 | 101
2020-02-25 20:00 | 97 | 90 |  |  | 43886.8333 | 114 | 102
2020-02-25 20:30 | 96 | 89 |  |  | 43886.8542 | 112 | 100
2020-02-25 21:00 | 91 | 85 |  |  | 43886.875 | 104 | 95
2020-02-25 21:30 | 88 | 83 |  |  | 43886.8958 | 100 | 92
2020-02-25 22:00 | 85 | 79 |  |  | 43886.9167 | 98 | 90
2020-02-25 22:30 | 85 | 78 |  |  | 43886.9375 | 97 | 88
2020-02-25 23:00 | 82 | 76 |  |  | 43886.9583 | 91 | 85
2020-02-25 23:30 | 78 | 72 |  |  | 43886.9792 | 86 | 79
2020-02-26 | 75 | 67 |  |  | 43887 | 82 | 75
2020-02-26 00:30 | 73 | 63 |  |  | 43887.0208 | 80 | 71
2020-02-26 01:00 | 70 | 60 |  |  | 43887.0417 | 76 | 66
2020-02-26 01:30 | 68 | 57 |  |  | 43887.0625 | 73 | 63
2020-02-26 02:00 | 67 | 55 |  |  | 43887.0833 | 73 | 62
2020-02-26 02:30 | 65 | 52 |  |  | 43887.1042 | 71 | 59
2020-02-26 03:00 | 63 | 51 |  |  | 43887.125 | 70 | 58
2020-02-26 03:30 | 63 | 50 |  |  | 43887.1458 | 70 | 58
2020-02-26 04:00 | 64 | 51 |  |  | 43887.1667 | 71 | 59
2020-02-26 04:30 | 66 | 53 |  |  | 43887.1875 | 73 | 62
2020-02-26 05:00 | 68 | 56 |  |  | 43887.2083 | 75 | 65
2020-02-26 05:30 | 72 | 61 |  |  | 43887.2292 | 79 | 70
2020-02-26 06:00 | 74 | 64 |  |  | 43887.25 | 84 | 75
2020-02-26 06:30 | 77 | 70 |  |  | 43887.2708 | 89 | 83
2020-02-26 07:00 | 77 | 71 |  |  | 43887.2917 | 93 | 87
2020-02-26 07:30 | 82 | 73 |  |  | 43887.3125 | 103 | 93
2020-02-26 08:00 | 84 | 75 |  |  | 43887.3333 | 107 | 97
2020-02-26 08:30 | 82 | 74 |  |  | 43887.3542 | 107 | 100
2020-02-26 09:00 | 79 | 72 |  |  | 43887.375 | 103 | 97
2020-02-26 09:30 | 85 | 79 |  |  | 43887.3958 | 109 | 104
2020-02-26 10:00 | 86 | 81 |  |  | 43887.4167 | 109 | 104
2020-02-26 10:30 | 86 | 82 |  |  | 43887.4375 | 109 | 105
2020-02-26 11:00 | 93 | 90 |  |  | 43887.4583 | 116 | 113
2020-02-26 11:30 | 89 | 85 |  |  | 43887.4792 | 112 | 109
2020-02-26 12:00 | 86 | 83 |  |  | 43887.5 | 110 | 106
2020-02-26 12:30 | 88 | 85 |  |  | 43887.5208 | 110 | 107
2020-02-26 13:00 | 89 | 86 |  |  | 43887.5417 | 112 | 109
2020-02-26 13:30 | 95 | 93 |  |  | 43887.5625 | 116 | 113
2020-02-26 14:00 | 101 | 98 |  |  | 43887.5833 | 123 | 121
2020-02-26 14:30 | 100 | 98 |  |  | 43887.6042 | 124 | 121
2020-02-26 15:00 | 99 | 95 |  |  | 43887.625 | 118 | 114
2020-02-26 15:30 | 102 | 98 |  |  | 43887.6458 | 121 | 117
2020-02-26 16:00 | 104 | 101 |  |  | 43887.6667 | 122 | 118
2020-02-26 16:30 | 110 | 106 |  |  | 43887.6875 | 127 | 122
2020-02-26 17:00 | 111 | 107 |  |  | 43887.7083 | 127 | 122
2020-02-26 17:30 | 112 | 108 |  |  | 43887.7292 | 127 | 121
2020-02-26 18:00 | 110 | 105 |  |  | 43887.75 | 124 | 117
2020-02-26 18:30 | 108 | 104 |  |  | 43887.7708 | 121 | 113
2020-02-26 19:00 | 112 | 108 |  |  | 43887.7917 | 125 | 117
2020-02-26 19:30 | 110 | 106 |  |  | 43887.8125 | 124 | 116
2020-02-26 20:00 | 108 | 105 |  |  | 43887.8333 | 120 | 115
2020-02-26 20:30 | 106 | 103 |  |  | 43887.8542 | 118 | 114
2020-02-26 21:00 | 101 | 98 |  |  | 43887.875 | 112 | 108
2020-02-26 21:30 | 97 | 95 |  |  | 43887.8958 | 108 | 104
2020-02-26 22:00 | 95 | 92 |  |  | 43887.9167 | 106 | 104
2020-02-26 22:30 | 93 | 91 |  |  | 43887.9375 | 104 | 103
2020-02-26 23:00 | 89 | 88 |  |  | 43887.9583 | 99 | 98
2020-02-26 23:30 | 84 | 82 |  |  | 43887.9792 | 94 | 92
2020-02-27 | 79 | 76 |  |  | 43888 | 88 | 86
2020-02-27 00:30 | 77 | 73 |  |  | 43888.0208 | 84 | 81
2020-02-27 01:00 | 74 | 70 |  |  | 43888.0417 | 81 | 78
2020-02-27 01:30 | 71 | 66 |  |  | 43888.0625 | 77 | 74
2020-02-27 02:00 | 70 | 65 |  |  | 43888.0833 | 75 | 72
2020-02-27 02:30 | 67 | 61 |  |  | 43888.1042 | 74 | 71
2020-02-27 03:00 | 67 | 61 |  |  | 43888.125 | 73 | 70
2020-02-27 03:30 | 66 | 60 |  |  | 43888.1458 | 72 | 69
2020-02-27 04:00 | 65 | 59 |  |  | 43888.1667 | 71 | 68
2020-02-27 04:30 | 67 | 61 |  |  | 43888.1875 | 73 | 69
2020-02-27 05:00 | 70 | 65 |  |  | 43888.2083 | 76 | 72
2020-02-27 05:30 | 71 | 67 |  |  | 43888.2292 | 78 | 76
2020-02-27 06:00 | 71 | 67 |  |  | 43888.25 | 79 | 77
2020-02-27 06:30 | 76 | 73 |  |  | 43888.2708 | 88 | 87
2020-02-27 07:00 | 78 | 76 |  |  | 43888.2917 | 92 | 92
2020-02-27 07:30 | 85 | 82 |  |  | 43888.3125 | 103 | 102
2020-02-27 08:00 | 89 | 85 |  |  | 43888.3333 | 112 | 108
2020-02-27 08:30 | 91 | 88 |  |  | 43888.3542 | 115 | 111
2020-02-27 09:00 | 98 | 96 |  |  | 43888.375 | 121 | 117
2020-02-27 09:30 | 101 | 99 |  |  | 43888.3958 | 122 | 119
2020-02-27 10:00 | 104 | 102 |  |  | 43888.4167 | 120 | 117
2020-02-27 10:30 | 102 | 100 |  |  | 43888.4375 | 120 | 117
2020-02-27 11:00 | 96 | 93 |  |  | 43888.4583 | 115 | 112
2020-02-27 11:30 | 85 | 81 |  |  | 43888.4792 | 111 | 107
2020-02-27 12:00 | 87 | 83 |  |  | 43888.5 | 113 | 109
2020-02-27 12:30 | 85 | 81 |  |  | 43888.5208 | 107 | 103
2020-02-27 13:00 | 93 | 90 |  |  | 43888.5417 | 117 | 113
2020-02-27 13:30 | 101 | 98 |  |  | 43888.5625 | 122 | 118
2020-02-27 14:00 | 108 | 105 |  |  | 43888.5833 | 120 | 116
2020-02-27 14:30 | 102 | 99 |  |  | 43888.6042 | 130 | 127
2020-02-27 15:00 | 97 | 94 |  |  | 43888.625 | 122 | 118
2020-02-27 15:30 | 90 | 85 |  |  | 43888.6458 | 110 | 105
2020-02-27 16:00 | 87 | 82 |  |  | 43888.6667 | 101 | 95
2020-02-27 16:30 | 93 | 90 |  |  | 43888.6875 | 103 | 98
2020-02-27 17:00 | 102 | 100 |  |  | 43888.7083 | 114 | 109
2020-02-27 17:30 | 98 | 95 |  |  | 43888.7292 | 113 | 107
2020-02-27 18:00 | 98 | 94 |  |  | 43888.75 | 110 | 104
2020-02-27 18:30 | 99 | 94 |  |  | 43888.7708 | 110 | 102
2020-02-27 19:00 | 101 | 96 |  |  | 43888.7917 | 112 | 103
2020-02-27 19:30 | 98 | 94 |  |  | 43888.8125 | 109 | 101
2020-02-27 20:00 | 97 | 92 |  |  | 43888.8333 | 107 | 99
2020-02-27 20:30 | 95 | 90 |  |  | 43888.8542 | 106 | 97
2020-02-27 21:00 | 89 | 84 |  |  | 43888.875 | 99 | 90
2020-02-27 21:30 | 84 | 79 |  |  | 43888.8958 | 90 | 85
2020-02-27 22:00 | 78 | 74 |  |  | 43888.9167 | 84 | 81
2020-02-27 22:30 | 77 | 73 |  |  | 43888.9375 | 83 | 81
2020-02-27 23:00 | 77 | 72 |  |  | 43888.9583 | 82 | 78
2020-02-27 23:30 | 74 | 69 |  |  | 43888.9792 | 79 | 75
2020-02-28 | 69 | 62 |  |  | 43889 | 73 | 69
2020-02-28 00:30 | 64 | 57 |  |  | 43889.0208 | 67 | 62
2020-02-28 01:00 | 63 | 55 |  |  | 43889.0417 | 63 | 59
2020-02-28 01:30 | 63 | 55 |  |  | 43889.0625 | 64 | 60
2020-02-28 02:00 | 62 | 54 |  |  | 43889.0833 | 63 | 59
2020-02-28 02:30 | 61 | 53 |  |  | 43889.1042 | 63 | 59
2020-02-28 03:00 | 61 | 52 |  |  | 43889.125 | 61 | 56
2020-02-28 03:30 | 60 | 50 |  |  | 43889.1458 | 60 | 56
2020-02-28 04:00 | 59 | 51 |  |  | 43889.1667 | 60 | 55
2020-02-28 04:30 | 60 | 52 |  |  | 43889.1875 | 62 | 58
2020-02-28 05:00 | 63 | 55 |  |  | 43889.2083 | 65 | 61
2020-02-28 05:30 | 66 | 59 |  |  | 43889.2292 | 69 | 66
2020-02-28 06:00 | 67 | 60 |  |  | 43889.25 | 71 | 68
2020-02-28 06:30 | 70 | 65 |  |  | 43889.2708 | 77 | 76
2020-02-28 07:00 | 74 | 71 |  |  | 43889.2917 | 85 | 84
2020-02-28 07:30 | 73 | 71 |  |  | 43889.3125 | 88 | 88
2020-02-28 08:00 | 71 | 67 |  |  | 43889.3333 | 85 | 84
2020-02-28 08:30 | 69 | 66 |  |  | 43889.3542 | 84 | 84
2020-02-28 09:00 | 67 | 65 |  |  | 43889.375 | 84 | 83
2020-02-28 09:30 | 69 | 67 |  |  | 43889.3958 | 86 | 85
2020-02-28 10:00 | 69 | 68 |  |  | 43889.4167 | 85 | 85
2020-02-28 10:30 | 74 | 72 |  |  | 43889.4375 | 87 | 86
2020-02-28 11:00 | 77 | 74 |  |  | 43889.4583 | 90 | 88
2020-02-28 11:30 | 77 | 73 |  |  | 43889.4792 | 91 | 89
2020-02-28 12:00 | 78 | 75 |  |  | 43889.5 | 92 | 90
2020-02-28 12:30 | 81 | 78 |  |  | 43889.5208 | 93 | 92
2020-02-28 13:00 | 84 | 81 |  |  | 43889.5417 | 96 | 95
2020-02-28 13:30 | 84 | 81 |  |  | 43889.5625 | 96 | 94
2020-02-28 14:00 | 87 | 84 |  |  | 43889.5833 | 98 | 97
2020-02-28 14:30 | 94 | 92 |  |  | 43889.6042 | 104 | 103
2020-02-28 15:00 | 101 | 99 |  |  | 43889.625 | 106 | 105
2020-02-28 15:30 | 109 | 107 |  |  | 43889.6458 | 119 | 118
2020-02-28 16:00 | 111 | 109 |  |  | 43889.6667 | 124 | 123
2020-02-28 16:30 | 107 | 104 |  |  | 43889.6875 | 122 | 119
2020-02-28 17:00 | 107 | 103 |  |  | 43889.7083 | 122 | 119
2020-02-28 17:30 | 104 | 98 |  |  | 43889.7292 | 119 | 114
2020-02-28 18:00 | 98 | 93 |  |  | 43889.75 | 111 | 106
2020-02-28 18:30 | 96 | 92 |  |  | 43889.7708 | 106 | 102
2020-02-28 19:00 | 97 | 95 |  |  | 43889.7917 | 108 | 106
2020-02-28 19:30 | 95 | 93 |  |  | 43889.8125 | 107 | 105
2020-02-28 20:00 | 96 | 93 |  |  | 43889.8333 | 108 | 105
2020-02-28 20:30 | 98 | 95 |  |  | 43889.8542 | 109 | 106
2020-02-28 21:00 | 96 | 92 |  |  | 43889.875 | 105 | 102
2020-02-28 21:30 | 92 | 89 |  |  | 43889.8958 | 100 | 97
2020-02-28 22:00 | 91 | 87 |  |  | 43889.9167 | 100 | 97
2020-02-28 22:30 | 88 | 84 |  |  | 43889.9375 | 98 | 94
2020-02-28 23:00 | 86 | 81 |  |  | 43889.9583 | 94 | 90
2020-02-28 23:30 | 80 | 76 |  |  | 43889.9792 | 88 | 84
2020-02-29 | 76 | 70 |  |  | 43890 | 81 | 78
2020-02-29 00:30 | 74 | 65 |  |  | 43890.0208 | 77 | 73
2020-02-29 01:00 | 72 | 63 |  |  | 43890.0417 | 74 | 70
2020-02-29 01:30 | 70 | 60 |  |  | 43890.0625 | 72 | 67
2020-02-29 02:00 | 68 | 57 |  |  | 43890.0833 | 68 | 64
2020-02-29 02:30 | 66 | 54 |  |  | 43890.1042 | 67 | 62
2020-02-29 03:00 | 63 | 53 |  |  | 43890.125 | 64 | 61
2020-02-29 03:30 | 61 | 52 |  |  | 43890.1458 | 62 | 60
2020-02-29 04:00 | 61 | 52 |  |  | 43890.1667 | 62 | 60
2020-02-29 04:30 | 61 | 52 |  |  | 43890.1875 | 61 | 59
2020-02-29 05:00 | 61 | 51 |  |  | 43890.2083 | 61 | 59
2020-02-29 05:30 | 63 | 54 |  |  | 43890.2292 | 64 | 62
2020-02-29 06:00 | 63 | 55 |  |  | 43890.25 | 65 | 63
2020-02-29 06:30 | 64 | 55 |  |  | 43890.2708 | 66 | 64
2020-02-29 07:00 | 60 | 51 |  |  | 43890.2917 | 64 | 63
2020-02-29 07:30 | 57 | 49 |  |  | 43890.3125 | 62 | 61
2020-02-29 08:00 | 55 | 48 |  |  | 43890.3333 | 61 | 61
2020-02-29 08:30 | 57 | 51 |  |  | 43890.3542 | 65 | 64
2020-02-29 09:00 | 63 | 57 |  |  | 43890.375 | 71 | 70
2020-02-29 09:30 | 67 | 61 |  |  | 43890.3958 | 73 | 72
2020-02-29 10:00 | 67 | 62 |  |  | 43890.4167 | 70 | 70
2020-02-29 10:30 | 65 | 61 |  |  | 43890.4375 | 67 | 67
2020-02-29 11:00 | 61 | 56 |  |  | 43890.4583 | 66 | 65
2020-02-29 11:30 | 61 | 56 |  |  | 43890.4792 | 73 | 72
2020-02-29 12:00 | 64 | 60 |  |  | 43890.5 | 78 | 78
2020-02-29 12:30 | 69 | 65 |  |  | 43890.5208 | 80 | 80
2020-02-29 13:00 | 71 | 66 |  |  | 43890.5417 | 80 | 80
2020-02-29 13:30 | 78 | 74 |  |  | 43890.5625 | 87 | 86
2020-02-29 14:00 | 76 | 72 |  |  | 43890.5833 | 82 | 81
2020-02-29 14:30 | 77 | 73 |  |  | 43890.6042 | 73 | 72
2020-02-29 15:00 | 67 | 62 |  |  | 43890.625 | 71 | 70
2020-02-29 15:30 | 71 | 67 |  |  | 43890.6458 | 74 | 73
2020-02-29 16:00 | 76 | 71 |  |  | 43890.6667 | 78 | 76
2020-02-29 16:30 | 80 | 75 |  |  | 43890.6875 | 80 | 79
2020-02-29 17:00 | 84 | 79 |  |  | 43890.7083 | 85 | 84
2020-02-29 17:30 | 86 | 80 |  |  | 43890.7292 | 89 | 88
2020-02-29 18:00 | 86 | 79 |  |  | 43890.75 | 89 | 87
2020-02-29 18:30 | 86 | 79 |  |  | 43890.7708 | 89 | 86
2020-02-29 19:00 | 88 | 81 |  |  | 43890.7917 | 93 | 91
2020-02-29 19:30 | 88 | 81 |  |  | 43890.8125 | 93 | 91
2020-02-29 20:00 | 87 | 79 |  |  | 43890.8333 | 91 | 89
2020-02-29 20:30 | 86 | 77 |  |  | 43890.8542 | 90 | 87
2020-02-29 21:00 | 82 | 72 |  |  | 43890.875 | 85 | 81
2020-02-29 21:30 | 78 | 69 |  |  | 43890.8958 | 82 | 79
2020-02-29 22:00 | 74 | 66 |  |  | 43890.9167 | 81 | 78
2020-02-29 22:30 | 72 | 64 |  |  | 43890.9375 | 79 | 76
2020-02-29 23:00 | 73 | 64 |  |  | 43890.9583 | 78 | 74
2020-02-29 23:30 | 71 | 60 |  |  | 43890.9792 | 75 | 71
2020-03-01 | 67 | 57 |  |  | 43891 | 71 | 68
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 18. Historic line rating
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 798 | 730 | 812 | 730 | 812 | 730
Feeders | 717 | 160 | 148 | 164 | 148 | 164 | 148
| 718 | 160 | 148 | 164 | 148 | 164 | 148
| 7296 | 160 | 148 | 164 | 148 | 164 | 148
| 791 | 159 | 143 | 160 | 143 | 160 | 143
| 7295 | 159 | 143 | 160 | 143 | 160 | 143

## 21. Annual constraint duration
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (hours)

## 22. Constraint dur. (peak day)
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (peak day, hours)