## Cover Page
AER Rule | Field Name | Value(s)
1 | Transmission line ID | 132kV F7156, F7156R from T056 Townsville South to H013 Ross
2 | Constraint primary driver | Asset condition
3 | Location of constraint (start, decimal degrees, latitude and longitude) | -19.3583 | 146.8503
4 | Location of constraint (end, decimal degrees, latitude and longitude) | -19.3511 | 146.8527
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
5 | Forecast asset rating (MVA) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
6 | Forecast maximum demand 10% PoE (MVA) | 151.11 | 151.56 | 150.44 | 150.39 | 114.32 | 114.4 | 114.36 | 114.34 | 113.71 | 114.63 | 115.55
| Forecast maximum demand 50% PoE (MVA) | 144.71 | 144.72 | 144.73 | 144.6 | 108.24 | 108.58 | 110.63 | 110.67 | 110.84 | 110.07 | 109.3
7 | Voltage Level (kV) | Financial year 2021: 132
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
8 | Maximum load at risk (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100
| Maximum load at risk (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 95 | 95 | 95
9 | Energy at risk (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 35
10 | Preferred investment | Financial year 2021: Line refit works on the 132kV transmisson lines between Townsville south and Ross substations
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
11 | Capital cost ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0
12 | Operating cost ($m, nominal) | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
13 | Preferred investment cost accuracy | Financial year 2021: 0.3
14 | Preferred investment proposed timing | Financial year 2021: 2028-06-30
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
15 | Demand reduction to defer by 1 year (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Annual deferall value ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Historic load trace
18 | Historic line rating
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
19 | Annual economic cost of constraint ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3899 | 1.3899 | 1.3899 | 1.3899
20 | VCR ($m/MWh) | Financial year 2021: 0.03971
21 | Annual constraint duration
22 | Constraint duration on peak demand day

## 17. Historic load trace
Date/Time | Load (MVA) | Load (MW) | Load switching affected?
2017-03-01 00:30 | 69 | 68
2017-03-01 01:00 | 69 | 68
2017-03-01 01:30 | 68 | 68
2017-03-01 02:00 | 70 | 67
2017-03-01 02:30 | 70 | 68
2017-03-01 03:00 | 70 | 68
2017-03-01 03:30 | 69 | 67
2017-03-01 04:00 | 69 | 66
2017-03-01 04:30 | 69 | 67
2017-03-01 05:00 | 69 | 67
2017-03-01 05:30 | 69 | 66
2017-03-01 06:00 | 69 | 67
2017-03-01 06:30 | 66 | 66
2017-03-01 07:00 | 66 | 66
2017-03-01 07:30 | 68 | 68
2017-03-01 08:00 | 70 | 70
2017-03-01 08:30 | 71 | 70
2017-03-01 09:00 | 71 | 71
2017-03-01 09:30 | 72 | 72
2017-03-01 10:00 | 73 | 73
2017-03-01 10:30 | 74 | 74
2017-03-01 11:00 | 74 | 74
2017-03-01 11:30 | 75 | 74
2017-03-01 12:00 | 75 | 75
2017-03-01 12:30 | 76 | 76
2017-03-01 13:00 | 76 | 76
2017-03-01 13:30 | 77 | 77
2017-03-01 14:00 | 74 | 74
2017-03-01 14:30 | 73 | 72
2017-03-01 15:00 | 74 | 73
2017-03-01 15:30 | 74 | 73
2017-03-01 16:00 | 74 | 73
2017-03-01 16:30 | 73 | 71
2017-03-01 17:00 | 74 | 72
2017-03-01 17:30 | 79 | 78
2017-03-01 18:00 | 80 | 79
2017-03-01 18:30 | 79 | 78
2017-03-01 19:00 | 80 | 79
2017-03-01 19:30 | 79 | 79
2017-03-01 20:00 | 78 | 77
2017-03-01 20:30 | 77 | 76
2017-03-01 21:00 | 76 | 75
2017-03-01 21:30 | 75 | 75
2017-03-01 22:00 | 74 | 74
2017-03-01 22:30 | 74 | 73
2017-03-01 23:00 | 74 | 72
2017-03-01 23:30 | 74 | 72
2017-03-02 | 73 | 70
2017-03-02 00:30 | 73 | 71
2017-03-02 01:00 | 73 | 70
2017-03-02 01:30 | 71 | 69
2017-03-02 02:00 | 71 | 69
2017-03-02 02:30 | 69 | 69
2017-03-02 03:00 | 69 | 69
2017-03-02 03:30 | 68 | 68
2017-03-02 04:00 | 68 | 68
2017-03-02 04:30 | 69 | 69
2017-03-02 05:00 | 69 | 69
2017-03-02 05:30 | 68 | 68
2017-03-02 06:00 | 68 | 67
2017-03-02 06:30 | 68 | 68
2017-03-02 07:00 | 67 | 67
2017-03-02 07:30 | 69 | 68
2017-03-02 08:00 | 69 | 68
2017-03-02 08:30 | 70 | 69
2017-03-02 09:00 | 69 | 68
2017-03-02 09:30 | 67 | 66
2017-03-02 10:00 | 68 | 67
2017-03-02 10:30 | 68 | 67
2017-03-02 11:00 | 71 | 70
2017-03-02 11:30 | 70 | 70
2017-03-02 12:00 | 68 | 68
2017-03-02 12:30 | 68 | 68
2017-03-02 13:00 | 70 | 69
2017-03-02 13:30 | 73 | 72
2017-03-02 14:00 | 73 | 72
2017-03-02 14:30 | 75 | 74
2017-03-02 15:00 | 76 | 75
2017-03-02 15:30 | 76 | 75
2017-03-02 16:00 | 76 | 75
2017-03-02 16:30 | 76 | 75
2017-03-02 17:00 | 74 | 73
2017-03-02 17:30 | 75 | 74
2017-03-02 18:00 | 75 | 74
2017-03-02 18:30 | 78 | 77
2017-03-02 19:00 | 78 | 77
2017-03-02 19:30 | 77 | 76
2017-03-02 20:00 | 78 | 77
2017-03-02 20:30 | 77 | 76
2017-03-02 21:00 | 76 | 75
2017-03-02 21:30 | 75 | 74
2017-03-02 22:00 | 74 | 72
2017-03-02 22:30 | 74 | 73
2017-03-02 23:00 | 74 | 72
2017-03-02 23:30 | 72 | 70
2017-03-03 | 71 | 70
2017-03-03 00:30 | 71 | 71
2017-03-03 01:00 | 71 | 70
2017-03-03 01:30 | 70 | 69
2017-03-03 02:00 | 70 | 68
2017-03-03 02:30 | 69 | 68
2017-03-03 03:00 | 69 | 67
2017-03-03 03:30 | 69 | 68
2017-03-03 04:00 | 70 | 68
2017-03-03 04:30 | 69 | 68
2017-03-03 05:00 | 69 | 68
2017-03-03 05:30 | 70 | 69
2017-03-03 06:00 | 69 | 68
2017-03-03 06:30 | 71 | 70
2017-03-03 07:00 | 68 | 67
2017-03-03 07:30 | 71 | 71
2017-03-03 08:00 | 71 | 71
2017-03-03 08:30 | 73 | 73
2017-03-03 09:00 | 73 | 73
2017-03-03 09:30 | 74 | 74
2017-03-03 10:00 | 75 | 74
2017-03-03 10:30 | 75 | 74
2017-03-03 11:00 | 74 | 74
2017-03-03 11:30 | 74 | 73
2017-03-03 12:00 | 73 | 73
2017-03-03 12:30 | 75 | 74
2017-03-03 13:00 | 72 | 71
2017-03-03 13:30 | 73 | 71
2017-03-03 14:00 | 74 | 73
2017-03-03 14:30 | 75 | 73
2017-03-03 15:00 | 75 | 74
2017-03-03 15:30 | 76 | 74
2017-03-03 16:00 | 74 | 72
2017-03-03 16:30 | 75 | 73
2017-03-03 17:00 | 75 | 73
2017-03-03 17:30 | 75 | 73
2017-03-03 18:00 | 75 | 72
2017-03-03 18:30 | 76 | 74
2017-03-03 19:00 | 71 | 66
2017-03-03 19:30 | 75 | 74
2017-03-03 20:00 | 74 | 74
2017-03-03 20:30 | 74 | 73
2017-03-03 21:00 | 73 | 72
2017-03-03 21:30 | 73 | 72
2017-03-03 22:00 | 72 | 71
2017-03-03 22:30 | 72 | 71
2017-03-03 23:00 | 72 | 70
2017-03-03 23:30 | 71 | 70
2017-03-04 | 70 | 69
2017-03-04 00:30 | 71 | 70
2017-03-04 01:00 | 72 | 70
2017-03-04 01:30 | 70 | 69
2017-03-04 02:00 | 70 | 69
2017-03-04 02:30 | 70 | 69
2017-03-04 03:00 | 71 | 70
2017-03-04 03:30 | 71 | 69
2017-03-04 04:00 | 70 | 69
2017-03-04 04:30 | 70 | 69
2017-03-04 05:00 | 70 | 68
2017-03-04 05:30 | 69 | 68
2017-03-04 06:00 | 69 | 68
2017-03-04 06:30 | 70 | 68
2017-03-04 07:00 | 71 | 69
2017-03-04 07:30 | 70 | 68
2017-03-04 08:00 | 71 | 69
2017-03-04 08:30 | 72 | 71
2017-03-04 09:00 | 73 | 72
2017-03-04 09:30 | 74 | 72
2017-03-04 10:00 | 74 | 73
2017-03-04 10:30 | 73 | 71
2017-03-04 11:00 | 73 | 71
2017-03-04 11:30 | 73 | 71
2017-03-04 12:00 | 73 | 71
2017-03-04 12:30 | 73 | 72
2017-03-04 13:00 | 74 | 72
2017-03-04 13:30 | 73 | 72
2017-03-04 14:00 | 73 | 71
2017-03-04 14:30 | 74 | 73
2017-03-04 15:00 | 75 | 73
2017-03-04 15:30 | 70 | 69
2017-03-04 16:00 | 75 | 74
2017-03-04 16:30 | 71 | 71
2017-03-04 17:00 | 70 | 69
2017-03-04 17:30 | 69 | 69
2017-03-04 18:00 | 69 | 69
2017-03-04 18:30 | 71 | 70
2017-03-04 19:00 | 69 | 69
2017-03-04 19:30 | 70 | 69
2017-03-04 20:00 | 73 | 71
2017-03-04 20:30 | 74 | 72
2017-03-04 21:00 | 71 | 70
2017-03-04 21:30 | 71 | 69
2017-03-04 22:00 | 70 | 69
2017-03-04 22:30 | 70 | 69
2017-03-04 23:00 | 70 | 69
2017-03-04 23:30 | 67 | 67
2017-03-05 | 67 | 66
2017-03-05 00:30 | 67 | 67
2017-03-05 01:00 | 67 | 66
2017-03-05 01:30 | 67 | 66
2017-03-05 02:00 | 66 | 66
2017-03-05 02:30 | 67 | 67
2017-03-05 03:00 | 69 | 68
2017-03-05 03:30 | 69 | 69
2017-03-05 04:00 | 70 | 69
2017-03-05 04:30 | 68 | 68
2017-03-05 05:00 | 69 | 68
2017-03-05 05:30 | 68 | 67
2017-03-05 06:00 | 68 | 67
2017-03-05 06:30 | 68 | 67
2017-03-05 07:00 | 68 | 67
2017-03-05 07:30 | 69 | 69
2017-03-05 08:00 | 69 | 68
2017-03-05 08:30 | 70 | 69
2017-03-05 09:00 | 70 | 68
2017-03-05 09:30 | 69 | 68
2017-03-05 10:00 | 70 | 69
2017-03-05 10:30 | 72 | 70
2017-03-05 11:00 | 73 | 70
2017-03-05 11:30 | 73 | 70
2017-03-05 12:00 | 73 | 71
2017-03-05 12:30 | 73 | 71
2017-03-05 13:00 | 75 | 72
2017-03-05 13:30 | 75 | 72
2017-03-05 14:00 | 76 | 73
2017-03-05 14:30 | 76 | 74
2017-03-05 15:00 | 78 | 76
2017-03-05 15:30 | 80 | 77
2017-03-05 16:00 | 66 | 62
2017-03-05 16:30 | 50 | 45
2017-03-05 17:00 | 48 | 42
2017-03-05 17:30 | 25 | 2
2017-03-05 18:00 | 27 | 8
2017-03-05 18:30 | 34 | 22
2017-03-05 19:00 | 49 | 45
2017-03-05 19:30 | 27 | 17
2017-03-05 20:00 | 49 | 43
2017-03-05 20:30 | 73 | 70
2017-03-05 21:00 | 76 | 73
2017-03-05 21:30 | 75 | 72
2017-03-05 22:00 | 72 | 69
2017-03-05 22:30 | 71 | 68
2017-03-05 23:00 | 71 | 68
2017-03-05 23:30 | 70 | 68
2017-03-06 | 70 | 68
2017-03-06 00:30 | 70 | 69
2017-03-06 01:00 | 70 | 69
2017-03-06 01:30 | 70 | 69
2017-03-06 02:00 | 70 | 69
2017-03-06 02:30 | 71 | 70
2017-03-06 03:00 | 71 | 69
2017-03-06 03:30 | 69 | 68
2017-03-06 04:00 | 69 | 68
2017-03-06 04:30 | 70 | 68
2017-03-06 05:00 | 70 | 69
2017-03-06 05:30 | 69 | 67
2017-03-06 06:00 | 68 | 67
2017-03-06 06:30 | 71 | 69
2017-03-06 07:00 | 74 | 73
2017-03-06 07:30 | 74 | 73
2017-03-06 08:00 | 74 | 73
2017-03-06 08:30 | 75 | 74
2017-03-06 09:00 | 77 | 76
2017-03-06 09:30 | 78 | 77
2017-03-06 10:00 | 77 | 74
2017-03-06 10:30 | 73 | 73
2017-03-06 11:00 | 74 | 74
2017-03-06 11:30 | 75 | 75
2017-03-06 12:00 | 77 | 77
2017-03-06 12:30 | 77 | 77
2017-03-06 13:00 | 78 | 78
2017-03-06 13:30 | 77 | 76
2017-03-06 14:00 | 77 | 76
2017-03-06 14:30 | 78 | 78
2017-03-06 15:00 | 79 | 79
2017-03-06 15:30 | 79 | 78
2017-03-06 16:00 | 81 | 80
2017-03-06 16:30 | 82 | 81
2017-03-06 17:00 | 81 | 80
2017-03-06 17:30 | 81 | 79
2017-03-06 18:00 | 81 | 80
2017-03-06 18:30 | 82 | 80
2017-03-06 19:00 | 83 | 82
2017-03-06 19:30 | 83 | 82
2017-03-06 20:00 | 82 | 81
2017-03-06 20:30 | 80 | 79
2017-03-06 21:00 | 78 | 77
2017-03-06 21:30 | 77 | 76
2017-03-06 22:00 | 77 | 75
2017-03-06 22:30 | 76 | 74
2017-03-06 23:00 | 75 | 72
2017-03-06 23:30 | 75 | 72
2017-03-07 | 76 | 74
2017-03-07 00:30 | 77 | 74
2017-03-07 01:00 | 77 | 74
2017-03-07 01:30 | 77 | 74
2017-03-07 02:00 | 77 | 73
2017-03-07 02:30 | 76 | 73
2017-03-07 03:00 | 76 | 72
2017-03-07 03:30 | 75 | 71
2017-03-07 04:00 | 75 | 71
2017-03-07 04:30 | 75 | 72
2017-03-07 05:00 | 76 | 73
2017-03-07 05:30 | 75 | 71
2017-03-07 06:00 | 75 | 71
2017-03-07 06:30 | 77 | 74
2017-03-07 07:00 | 79 | 75
2017-03-07 07:30 | 79 | 76
2017-03-07 08:00 | 78 | 76
2017-03-07 08:30 | 78 | 76
2017-03-07 09:00 | 78 | 76
2017-03-07 09:30 | 78 | 76
2017-03-07 10:00 | 78 | 76
2017-03-07 10:30 | 79 | 77
2017-03-07 11:00 | 79 | 77
2017-03-07 11:30 | 79 | 77
2017-03-07 12:00 | 78 | 76
2017-03-07 12:30 | 79 | 77
2017-03-07 13:00 | 80 | 78
2017-03-07 13:30 | 81 | 79
2017-03-07 14:00 | 81 | 79
2017-03-07 14:30 | 81 | 79
2017-03-07 15:00 | 80 | 78
2017-03-07 15:30 | 80 | 78
2017-03-07 16:00 | 80 | 78
2017-03-07 16:30 | 79 | 78
2017-03-07 17:00 | 79 | 77
2017-03-07 17:30 | 81 | 79
2017-03-07 18:00 | 81 | 79
2017-03-07 18:30 | 80 | 78
2017-03-07 19:00 | 81 | 79
2017-03-07 19:30 | 81 | 79
2017-03-07 20:00 | 80 | 79
2017-03-07 20:30 | 81 | 80
2017-03-07 21:00 | 81 | 79
2017-03-07 21:30 | 79 | 77
2017-03-07 22:00 | 76 | 75
2017-03-07 22:30 | 77 | 76
2017-03-07 23:00 | 74 | 73
2017-03-07 23:30 | 73 | 73
2017-03-08 | 72 | 72
2017-03-08 00:30 | 71 | 71
2017-03-08 01:00 | 71 | 70
2017-03-08 01:30 | 70 | 69
2017-03-08 02:00 | 70 | 69
2017-03-08 02:30 | 70 | 69
2017-03-08 03:00 | 70 | 69
2017-03-08 03:30 | 70 | 69
2017-03-08 04:00 | 70 | 69
2017-03-08 04:30 | 70 | 69
2017-03-08 05:00 | 62 | 60
2017-03-08 05:30 | 55 | 50
2017-03-08 06:00 | 51 | 42
2017-03-08 06:30 | 41 | 36
2017-03-08 07:00 | 38 | 37
2017-03-08 07:30 | 41 | 41
2017-03-08 08:00 | 41 | 41
2017-03-08 08:30 | 39 | 39
2017-03-08 09:00 | 39 | 39
2017-03-08 09:30 | 39 | 39
2017-03-08 10:00 | 39 | 39
2017-03-08 10:30 | 40 | 40
2017-03-08 11:00 | 40 | 40
2017-03-08 11:30 | 41 | 40
2017-03-08 12:00 | 42 | 41
2017-03-08 12:30 | 41 | 40
2017-03-08 13:00 | 41 | 40
2017-03-08 13:30 | 41 | 40
2017-03-08 14:00 | 42 | 41
2017-03-08 14:30 | 44 | 43
2017-03-08 15:00 | 44 | 44
2017-03-08 15:30 | 45 | 45
2017-03-08 16:00 | 43 | 41
2017-03-08 16:30 | 46 | 45
2017-03-08 17:00 | 48 | 46
2017-03-08 17:30 | 47 | 45
2017-03-08 18:00 | 48 | 46
2017-03-08 18:30 | 51 | 49
2017-03-08 19:00 | 61 | 61
2017-03-08 19:30 | 72 | 72
2017-03-08 20:00 | 76 | 75
2017-03-08 20:30 | 76 | 75
2017-03-08 21:00 | 76 | 75
2017-03-08 21:30 | 77 | 76
2017-03-08 22:00 | 73 | 72
2017-03-08 22:30 | 72 | 71
2017-03-08 23:00 | 71 | 70
2017-03-08 23:30 | 71 | 70
2017-03-09 | 73 | 71
2017-03-09 00:30 | 71 | 67
2017-03-09 01:00 | 70 | 67
2017-03-09 01:30 | 70 | 67
2017-03-09 02:00 | 69 | 66
2017-03-09 02:30 | 68 | 65
2017-03-09 03:00 | 68 | 65
2017-03-09 03:30 | 67 | 64
2017-03-09 04:00 | 67 | 64
2017-03-09 04:30 | 68 | 65
2017-03-09 05:00 | 68 | 65
2017-03-09 05:30 | 67 | 65
2017-03-09 06:00 | 68 | 65
2017-03-09 06:30 | 69 | 66
2017-03-09 07:00 | 70 | 66
2017-03-09 07:30 | 73 | 68
2017-03-09 08:00 | 73 | 67
2017-03-09 08:30 | 71 | 66
2017-03-09 09:00 | 72 | 70
2017-03-09 09:30 | 77 | 75
2017-03-09 10:00 | 77 | 75
2017-03-09 10:30 | 78 | 75
2017-03-09 11:00 | 78 | 75
2017-03-09 11:30 | 78 | 76
2017-03-09 12:00 | 78 | 77
2017-03-09 12:30 | 79 | 78
2017-03-09 13:00 | 80 | 79
2017-03-09 13:30 | 82 | 81
2017-03-09 14:00 | 83 | 82
2017-03-09 14:30 | 82 | 82
2017-03-09 15:00 | 80 | 79
2017-03-09 15:30 | 80 | 80
2017-03-09 16:00 | 81 | 81
2017-03-09 16:30 | 81 | 81
2017-03-09 17:00 | 74 | 74
2017-03-09 17:30 | 73 | 73
2017-03-09 18:00 | 72 | 72
2017-03-09 18:30 | 71 | 71
2017-03-09 19:00 | 71 | 71
2017-03-09 19:30 | 71 | 71
2017-03-09 20:00 | 70 | 70
2017-03-09 20:30 | 70 | 69
2017-03-09 21:00 | 69 | 69
2017-03-09 21:30 | 69 | 69
2017-03-09 22:00 | 66 | 66
2017-03-09 22:30 | 68 | 68
2017-03-09 23:00 | 67 | 67
2017-03-09 23:30 | 68 | 67
2017-03-10 | 67 | 67
2017-03-10 00:30 | 62 | 61
2017-03-10 01:00 | 61 | 60
2017-03-10 01:30 | 60 | 59
2017-03-10 02:00 | 60 | 58
2017-03-10 02:30 | 59 | 58
2017-03-10 03:00 | 59 | 58
2017-03-10 03:30 | 59 | 58
2017-03-10 04:00 | 58 | 57
2017-03-10 04:30 | 57 | 56
2017-03-10 05:00 | 58 | 57
2017-03-10 05:30 | 58 | 57
2017-03-10 06:00 | 58 | 58
2017-03-10 06:30 | 60 | 57
2017-03-10 07:00 | 59 | 58
2017-03-10 07:30 | 66 | 64
2017-03-10 08:00 | 70 | 67
2017-03-10 08:30 | 70 | 68
2017-03-10 09:00 | 70 | 68
2017-03-10 09:30 | 71 | 68
2017-03-10 10:00 | 72 | 69
2017-03-10 10:30 | 72 | 69
2017-03-10 11:00 | 72 | 70
2017-03-10 11:30 | 73 | 72
2017-03-10 12:00 | 73 | 72
2017-03-10 12:30 | 75 | 74
2017-03-10 13:00 | 75 | 74
2017-03-10 13:30 | 74 | 74
2017-03-10 14:00 | 73 | 72
2017-03-10 14:30 | 73 | 72
2017-03-10 15:00 | 73 | 72
2017-03-10 15:30 | 73 | 72
2017-03-10 16:00 | 74 | 73
2017-03-10 16:30 | 75 | 74
2017-03-10 17:00 | 76 | 74
2017-03-10 17:30 | 75 | 74
2017-03-10 18:00 | 76 | 73
2017-03-10 18:30 | 76 | 74
2017-03-10 19:00 | 77 | 75
2017-03-10 19:30 | 78 | 76
2017-03-10 20:00 | 78 | 76
2017-03-10 20:30 | 76 | 75
2017-03-10 21:00 | 75 | 74
2017-03-10 21:30 | 75 | 73
2017-03-10 22:00 | 71 | 70
2017-03-10 22:30 | 71 | 69
2017-03-10 23:00 | 70 | 68
2017-03-10 23:30 | 70 | 68
2017-03-11 | 69 | 68
2017-03-11 00:30 | 64 | 62
2017-03-11 01:00 | 62 | 60
2017-03-11 01:30 | 62 | 60
2017-03-11 02:00 | 61 | 59
2017-03-11 02:30 | 61 | 59
2017-03-11 03:00 | 61 | 59
2017-03-11 03:30 | 61 | 59
2017-03-11 04:00 | 61 | 59
2017-03-11 04:30 | 61 | 59
2017-03-11 05:00 | 61 | 60
2017-03-11 05:30 | 61 | 59
2017-03-11 06:00 | 61 | 59
2017-03-11 06:30 | 60 | 58
2017-03-11 07:00 | 59 | 57
2017-03-11 07:30 | 61 | 59
2017-03-11 08:00 | 62 | 61
2017-03-11 08:30 | 62 | 61
2017-03-11 09:00 | 61 | 60
2017-03-11 09:30 | 66 | 65
2017-03-11 10:00 | 71 | 70
2017-03-11 10:30 | 71 | 69
2017-03-11 11:00 | 70 | 68
2017-03-11 11:30 | 71 | 68
2017-03-11 12:00 | 71 | 68
2017-03-11 12:30 | 71 | 69
2017-03-11 13:00 | 72 | 70
2017-03-11 13:30 | 72 | 70
2017-03-11 14:00 | 76 | 72
2017-03-11 14:30 | 77 | 72
2017-03-11 15:00 | 76 | 72
2017-03-11 15:30 | 76 | 72
2017-03-11 16:00 | 77 | 72
2017-03-11 16:30 | 78 | 73
2017-03-11 17:00 | 77 | 73
2017-03-11 17:30 | 78 | 74
2017-03-11 18:00 | 78 | 74
2017-03-11 18:30 | 76 | 72
2017-03-11 19:00 | 76 | 72
2017-03-11 19:30 | 71 | 68
2017-03-11 20:00 | 68 | 66
2017-03-11 20:30 | 68 | 65
2017-03-11 21:00 | 68 | 65
2017-03-11 21:30 | 68 | 65
2017-03-11 22:00 | 68 | 64
2017-03-11 22:30 | 66 | 63
2017-03-11 23:00 | 64 | 62
2017-03-11 23:30 | 63 | 61
2017-03-12 | 63 | 61
2017-03-12 00:30 | 63 | 61
2017-03-12 01:00 | 62 | 60
2017-03-12 01:30 | 62 | 60
2017-03-12 02:00 | 62 | 60
2017-03-12 02:30 | 61 | 59
2017-03-12 03:00 | 61 | 59
2017-03-12 03:30 | 61 | 59
2017-03-12 04:00 | 61 | 59
2017-03-12 04:30 | 61 | 59
2017-03-12 05:00 | 61 | 60
2017-03-12 05:30 | 60 | 59
2017-03-12 06:00 | 60 | 58
2017-03-12 06:30 | 60 | 58
2017-03-12 07:00 | 60 | 58
2017-03-12 07:30 | 61 | 59
2017-03-12 08:00 | 61 | 60
2017-03-12 08:30 | 61 | 60
2017-03-12 09:00 | 61 | 60
2017-03-12 09:30 | 62 | 61
2017-03-12 10:00 | 61 | 60
2017-03-12 10:30 | 62 | 61
2017-03-12 11:00 | 62 | 61
2017-03-12 11:30 | 64 | 61
2017-03-12 12:00 | 64 | 62
2017-03-12 12:30 | 65 | 63
2017-03-12 13:00 | 66 | 63
2017-03-12 13:30 | 66 | 64
2017-03-12 14:00 | 66 | 64
2017-03-12 14:30 | 68 | 66
2017-03-12 15:00 | 68 | 66
2017-03-12 15:30 | 67 | 65
2017-03-12 16:00 | 69 | 67
2017-03-12 16:30 | 65 | 62
2017-03-12 17:00 | 69 | 67
2017-03-12 17:30 | 66 | 63
2017-03-12 18:00 | 65 | 63
2017-03-12 18:30 | 70 | 68
2017-03-12 19:00 | 68 | 66
2017-03-12 19:30 | 69 | 68
2017-03-12 20:00 | 67 | 67
2017-03-12 20:30 | 67 | 66
2017-03-12 21:00 | 67 | 66
2017-03-12 21:30 | 68 | 66
2017-03-12 22:00 | 66 | 64
2017-03-12 22:30 | 66 | 64
2017-03-12 23:00 | 64 | 63
2017-03-12 23:30 | 62 | 61
2017-03-13 | 61 | 60
2017-03-13 00:30 | 61 | 60
2017-03-13 01:00 | 61 | 60
2017-03-13 01:30 | 59 | 59
2017-03-13 02:00 | 63 | 61
2017-03-13 02:30 | 67 | 66
2017-03-13 03:00 | 63 | 62
2017-03-13 03:30 | 60 | 59
2017-03-13 04:00 | 60 | 59
2017-03-13 04:30 | 60 | 59
2017-03-13 05:00 | 62 | 61
2017-03-13 05:30 | 63 | 62
2017-03-13 06:00 | 64 | 63
2017-03-13 06:30 | 64 | 63
2017-03-13 07:00 | 65 | 63
2017-03-13 07:30 | 66 | 64
2017-03-13 08:00 | 66 | 66
2017-03-13 08:30 | 68 | 67
2017-03-13 09:00 | 66 | 66
2017-03-13 09:30 | 69 | 67
2017-03-13 10:00 | 73 | 71
2017-03-13 10:30 | 74 | 72
2017-03-13 11:00 | 72 | 71
2017-03-13 11:30 | 69 | 68
2017-03-13 12:00 | 72 | 71
2017-03-13 12:30 | 79 | 79
2017-03-13 13:00 | 81 | 81
2017-03-13 13:30 | 82 | 81
2017-03-13 14:00 | 77 | 77
2017-03-13 14:30 | 78 | 77
2017-03-13 15:00 | 79 | 78
2017-03-13 15:30 | 78 | 77
2017-03-13 16:00 | 77 | 75
2017-03-13 16:30 | 76 | 75
2017-03-13 17:00 | 75 | 74
2017-03-13 17:30 | 74 | 73
2017-03-13 18:00 | 75 | 74
2017-03-13 18:30 | 75 | 74
2017-03-13 19:00 | 74 | 72
2017-03-13 19:30 | 74 | 73
2017-03-13 20:00 | 77 | 76
2017-03-13 20:30 | 76 | 75
2017-03-13 21:00 | 76 | 75
2017-03-13 21:30 | 77 | 75
2017-03-13 22:00 | 76 | 74
2017-03-13 22:30 | 76 | 73
2017-03-13 23:00 | 75 | 72
2017-03-13 23:30 | 75 | 71
2017-03-14 | 73 | 70
2017-03-14 00:30 | 74 | 70
2017-03-14 01:00 | 74 | 70
2017-03-14 01:30 | 74 | 70
2017-03-14 02:00 | 74 | 70
2017-03-14 02:30 | 71 | 68
2017-03-14 03:00 | 68 | 66
2017-03-14 03:30 | 70 | 69
2017-03-14 04:00 | 70 | 69
2017-03-14 04:30 | 72 | 71
2017-03-14 05:00 | 72 | 71
2017-03-14 05:30 | 72 | 70
2017-03-14 06:00 | 71 | 70
2017-03-14 06:30 | 69 | 68
2017-03-14 07:00 | 67 | 67
2017-03-14 07:30 | 68 | 68
2017-03-14 08:00 | 68 | 68
2017-03-14 08:30 | 68 | 68
2017-03-14 09:00 | 73 | 72
2017-03-14 09:30 | 74 | 74
2017-03-14 10:00 | 71 | 71
2017-03-14 10:30 | 70 | 70
2017-03-14 11:00 | 70 | 69
2017-03-14 11:30 | 68 | 68
2017-03-14 12:00 | 68 | 68
2017-03-14 12:30 | 68 | 68
2017-03-14 13:00 | 69 | 69
2017-03-14 13:30 | 71 | 71
2017-03-14 14:00 | 71 | 71
2017-03-14 14:30 | 67 | 67
2017-03-14 15:00 | 76 | 75
2017-03-14 15:30 | 77 | 76
2017-03-14 16:00 | 76 | 76
2017-03-14 16:30 | 76 | 75
2017-03-14 17:00 | 79 | 78
2017-03-14 17:30 | 79 | 78
2017-03-14 18:00 | 79 | 78
2017-03-14 18:30 | 80 | 79
2017-03-14 19:00 | 77 | 75
2017-03-14 19:30 | 76 | 75
2017-03-14 20:00 | 78 | 77
2017-03-14 20:30 | 78 | 77
2017-03-14 21:00 | 78 | 77
2017-03-14 21:30 | 78 | 77
2017-03-14 22:00 | 77 | 76
2017-03-14 22:30 | 76 | 75
2017-03-14 23:00 | 76 | 74
2017-03-14 23:30 | 76 | 73
2017-03-15 | 75 | 73
2017-03-15 00:30 | 69 | 67
2017-03-15 01:00 | 67 | 66
2017-03-15 01:30 | 66 | 65
2017-03-15 02:00 | 65 | 65
2017-03-15 02:30 | 65 | 65
2017-03-15 03:00 | 65 | 64
2017-03-15 03:30 | 65 | 65
2017-03-15 04:00 | 67 | 66
2017-03-15 04:30 | 67 | 66
2017-03-15 05:00 | 67 | 67
2017-03-15 05:30 | 68 | 67
2017-03-15 06:00 | 67 | 66
2017-03-15 06:30 | 66 | 65
2017-03-15 07:00 | 71 | 70
2017-03-15 07:30 | 75 | 74
2017-03-15 08:00 | 75 | 75
2017-03-15 08:30 | 76 | 75
2017-03-15 09:00 | 76 | 76
2017-03-15 09:30 | 74 | 73
2017-03-15 10:00 | 76 | 76
2017-03-15 10:30 | 76 | 76
2017-03-15 11:00 | 76 | 76
2017-03-15 11:30 | 78 | 77
2017-03-15 12:00 | 79 | 78
2017-03-15 12:30 | 78 | 77
2017-03-15 13:00 | 76 | 76
2017-03-15 13:30 | 75 | 74
2017-03-15 14:00 | 74 | 73
2017-03-15 14:30 | 74 | 73
2017-03-15 15:00 | 74 | 73
2017-03-15 15:30 | 74 | 74
2017-03-15 16:00 | 75 | 75
2017-03-15 16:30 | 66 | 63
2017-03-15 17:00 | 63 | 58
2017-03-15 17:30 | 63 | 58
2017-03-15 18:00 | 65 | 59
2017-03-15 18:30 | 70 | 67
2017-03-15 19:00 | 71 | 68
2017-03-15 19:30 | 65 | 60
2017-03-15 20:00 | 63 | 56
2017-03-15 20:30 | 55 | 46
2017-03-15 21:00 | 53 | 44
2017-03-15 21:30 | 53 | 43
2017-03-15 22:00 | 52 | 41
2017-03-15 22:30 | 54 | 41
2017-03-15 23:00 | 43 | 40
2017-03-15 23:30 | 42 | 40
2017-03-16 | 42 | 40
2017-03-16 00:30 | 36 | 35
2017-03-16 01:00 | 33 | 31
2017-03-16 01:30 | 31 | 29
2017-03-16 02:00 | 36 | 35
2017-03-16 02:30 | 42 | 42
2017-03-16 03:00 | 42 | 42
2017-03-16 03:30 | 42 | 42
2017-03-16 04:00 | 43 | 43
2017-03-16 04:30 | 43 | 42
2017-03-16 05:00 | 42 | 42
2017-03-16 05:30 | 52 | 52
2017-03-16 06:00 | 56 | 56
2017-03-16 06:30 | 58 | 58
2017-03-16 07:00 | 64 | 62
2017-03-16 07:30 | 70 | 68
2017-03-16 08:00 | 70 | 69
2017-03-16 08:30 | 71 | 70
2017-03-16 09:00 | 71 | 70
2017-03-16 09:30 | 71 | 70
2017-03-16 10:00 | 72 | 70
2017-03-16 10:30 | 71 | 70
2017-03-16 11:00 | 75 | 74
2017-03-16 11:30 | 80 | 79
2017-03-16 12:00 | 80 | 80
2017-03-16 12:30 | 79 | 78
2017-03-16 13:00 | 76 | 75
2017-03-16 13:30 | 76 | 75
2017-03-16 14:00 | 76 | 75
2017-03-16 14:30 | 76 | 74
2017-03-16 15:00 | 76 | 75
2017-03-16 15:30 | 59 | 50
2017-03-16 16:00 | 61 | 52
2017-03-16 16:30 | 62 | 55
2017-03-16 17:00 | 62 | 50
2017-03-16 17:30 | 63 | 53
2017-03-16 18:00 | 50 | 48
2017-03-16 18:30 | 53 | 53
2017-03-16 19:00 | 49 | 48
2017-03-16 19:30 | 57 | 57
2017-03-16 20:00 | 73 | 73
2017-03-16 20:30 | 76 | 75
2017-03-16 21:00 | 75 | 74
2017-03-16 21:30 | 73 | 72
2017-03-16 22:00 | 72 | 72
2017-03-16 22:30 | 73 | 73
2017-03-16 23:00 | 73 | 72
2017-03-16 23:30 | 72 | 71
2017-03-17 | 72 | 71
2017-03-17 00:30 | 67 | 66
2017-03-17 01:00 | 65 | 63
2017-03-17 01:30 | 64 | 63
2017-03-17 02:00 | 64 | 63
2017-03-17 02:30 | 64 | 63
2017-03-17 03:00 | 63 | 62
2017-03-17 03:30 | 63 | 62
2017-03-17 04:00 | 63 | 62
2017-03-17 04:30 | 64 | 63
2017-03-17 05:00 | 64 | 62
2017-03-17 05:30 | 63 | 62
2017-03-17 06:00 | 68 | 67
2017-03-17 06:30 | 71 | 70
2017-03-17 07:00 | 70 | 69
2017-03-17 07:30 | 72 | 71
2017-03-17 08:00 | 73 | 72
2017-03-17 08:30 | 75 | 74
2017-03-17 09:00 | 76 | 75
2017-03-17 09:30 | 76 | 75
2017-03-17 10:00 | 77 | 75
2017-03-17 10:30 | 76 | 75
2017-03-17 11:00 | 76 | 75
2017-03-17 11:30 | 76 | 75
2017-03-17 12:00 | 77 | 75
2017-03-17 12:30 | 75 | 75
2017-03-17 13:00 | 76 | 75
2017-03-17 13:30 | 76 | 75
2017-03-17 14:00 | 76 | 75
2017-03-17 14:30 | 77 | 77
2017-03-17 15:00 | 79 | 79
2017-03-17 15:30 | 81 | 80
2017-03-17 16:00 | 81 | 80
2017-03-17 16:30 | 82 | 81
2017-03-17 17:00 | 82 | 82
2017-03-17 17:30 | 83 | 81
2017-03-17 18:00 | 83 | 81
2017-03-17 18:30 | 83 | 81
2017-03-17 19:00 | 82 | 80
2017-03-17 19:30 | 83 | 81
2017-03-17 20:00 | 83 | 81
2017-03-17 20:30 | 83 | 80
2017-03-17 21:00 | 82 | 80
2017-03-17 21:30 | 82 | 79
2017-03-17 22:00 | 81 | 79
2017-03-17 22:30 | 81 | 80
2017-03-17 23:00 | 85 | 83
2017-03-17 23:30 | 85 | 83
2017-03-18 | 84 | 82
2017-03-18 00:30 | 77 | 76
2017-03-18 01:00 | 76 | 75
2017-03-18 01:30 | 76 | 75
2017-03-18 02:00 | 76 | 74
2017-03-18 02:30 | 75 | 74
2017-03-18 03:00 | 75 | 74
2017-03-18 03:30 | 75 | 74
2017-03-18 04:00 | 74 | 72
2017-03-18 04:30 | 74 | 72
2017-03-18 05:00 | 74 | 72
2017-03-18 05:30 | 73 | 71
2017-03-18 06:00 | 73 | 71
2017-03-18 06:30 | 72 | 71
2017-03-18 07:00 | 73 | 71
2017-03-18 07:30 | 74 | 73
2017-03-18 08:00 | 75 | 74
2017-03-18 08:30 | 74 | 73
2017-03-18 09:00 | 72 | 71
2017-03-18 09:30 | 76 | 74
2017-03-18 10:00 | 80 | 78
2017-03-18 10:30 | 82 | 80
2017-03-18 11:00 | 81 | 79
2017-03-18 11:30 | 83 | 81
2017-03-18 12:00 | 83 | 82
2017-03-18 12:30 | 83 | 82
2017-03-18 13:00 | 82 | 81
2017-03-18 13:30 | 83 | 81
2017-03-18 14:00 | 82 | 79
2017-03-18 14:30 | 81 | 79
2017-03-18 15:00 | 80 | 77
2017-03-18 15:30 | 80 | 78
2017-03-18 16:00 | 82 | 80
2017-03-18 16:30 | 83 | 81
2017-03-18 17:00 | 83 | 81
2017-03-18 17:30 | 84 | 82
2017-03-18 18:00 | 84 | 82
2017-03-18 18:30 | 83 | 81
2017-03-18 19:00 | 84 | 83
2017-03-18 19:30 | 85 | 83
2017-03-18 20:00 | 85 | 84
2017-03-18 20:30 | 83 | 82
2017-03-18 21:00 | 85 | 84
2017-03-18 21:30 | 84 | 82
2017-03-18 22:00 | 84 | 82
2017-03-18 22:30 | 77 | 75
2017-03-18 23:00 | 74 | 72
2017-03-18 23:30 | 74 | 73
2017-03-19 | 73 | 72
2017-03-19 00:30 | 74 | 71
2017-03-19 01:00 | 73 | 71
2017-03-19 01:30 | 73 | 71
2017-03-19 02:00 | 72 | 70
2017-03-19 02:30 | 72 | 70
2017-03-19 03:00 | 72 | 69
2017-03-19 03:30 | 72 | 69
2017-03-19 04:00 | 72 | 69
2017-03-19 04:30 | 72 | 69
2017-03-19 05:00 | 72 | 69
2017-03-19 05:30 | 72 | 69
2017-03-19 06:00 | 71 | 69
2017-03-19 06:30 | 71 | 68
2017-03-19 07:00 | 71 | 68
2017-03-19 07:30 | 72 | 70
2017-03-19 08:00 | 72 | 70
2017-03-19 08:30 | 72 | 70
2017-03-19 09:00 | 72 | 70
2017-03-19 09:30 | 70 | 67
2017-03-19 10:00 | 57 | 47
2017-03-19 10:30 | 61 | 55
2017-03-19 11:00 | 67 | 66
2017-03-19 11:30 | 69 | 68
2017-03-19 12:00 | 68 | 67
2017-03-19 12:30 | 68 | 67
2017-03-19 13:00 | 68 | 66
2017-03-19 13:30 | 71 | 70
2017-03-19 14:00 | 69 | 68
2017-03-19 14:30 | 69 | 68
2017-03-19 15:00 | 68 | 67
2017-03-19 15:30 | 57 | 51
2017-03-19 16:00 | 55 | 42
2017-03-19 16:30 | 72 | 70
2017-03-19 17:00 | 61 | 48
2017-03-19 17:30 | 59 | 40
2017-03-19 18:00 | 60 | 46
2017-03-19 18:30 | 60 | 49
2017-03-19 19:00 | 57 | 40
2017-03-19 19:30 | 59 | 47
2017-03-19 20:00 | 61 | 51
2017-03-19 20:30 | 62 | 52
2017-03-19 21:00 | 70 | 66
2017-03-19 21:30 | 73 | 69
2017-03-19 22:00 | 74 | 70
2017-03-19 22:30 | 73 | 69
2017-03-19 23:00 | 72 | 68
2017-03-19 23:30 | 73 | 68
2017-03-20 | 72 | 67
2017-03-20 00:30 | 71 | 67
2017-03-20 01:00 | 71 | 67
2017-03-20 01:30 | 70 | 67
2017-03-20 02:00 | 70 | 66
2017-03-20 02:30 | 70 | 67
2017-03-20 03:00 | 68 | 65
2017-03-20 03:30 | 68 | 64
2017-03-20 04:00 | 67 | 63
2017-03-20 04:30 | 66 | 62
2017-03-20 05:00 | 67 | 63
2017-03-20 05:30 | 67 | 64
2017-03-20 06:00 | 72 | 68
2017-03-20 06:30 | 73 | 69
2017-03-20 07:00 | 53 | 47
2017-03-20 07:30 | 60 | 60
2017-03-20 08:00 | 68 | 68
2017-03-20 08:30 | 48 | 48
2017-03-20 09:00 | 39 | 39
2017-03-20 09:30 | 39 | 39
2017-03-20 10:00 | 39 | 39
2017-03-20 10:30 | 38 | 38
2017-03-20 11:00 | 39 | 39
2017-03-20 11:30 | 39 | 39
2017-03-20 12:00 | 39 | 39
2017-03-20 12:30 | 39 | 39
2017-03-20 13:00 | 39 | 39
2017-03-20 13:30 | 40 | 40
2017-03-20 14:00 | 39 | 39
2017-03-20 14:30 | 39 | 39
2017-03-20 15:00 | 40 | 40
2017-03-20 15:30 | 39 | 39
2017-03-20 16:00 | 39 | 39
2017-03-20 16:30 | 49 | 49
2017-03-20 17:00 | 50 | 49
2017-03-20 17:30 | 54 | 54
2017-03-20 18:00 | 56 | 55
2017-03-20 18:30 | 61 | 60
2017-03-20 19:00 | 55 | 55
2017-03-20 19:30 | 67 | 66
2017-03-20 20:00 | 74 | 72
2017-03-20 20:30 | 74 | 72
2017-03-20 21:00 | 73 | 71
2017-03-20 21:30 | 73 | 71
2017-03-20 22:00 | 72 | 71
2017-03-20 22:30 | 72 | 71
2017-03-20 23:00 | 72 | 69
2017-03-20 23:30 | 72 | 69
2017-03-21 | 71 | 68
2017-03-21 00:30 | 67 | 63
2017-03-21 01:00 | 65 | 61
2017-03-21 01:30 | 65 | 61
2017-03-21 02:00 | 65 | 61
2017-03-21 02:30 | 65 | 61
2017-03-21 03:00 | 65 | 61
2017-03-21 03:30 | 64 | 60
2017-03-21 04:00 | 64 | 60
2017-03-21 04:30 | 63 | 59
2017-03-21 05:00 | 62 | 58
2017-03-21 05:30 | 63 | 58
2017-03-21 06:00 | 65 | 61
2017-03-21 06:30 | 69 | 65
2017-03-21 07:00 | 68 | 64
2017-03-21 07:30 | 69 | 65
2017-03-21 08:00 | 68 | 68
2017-03-21 08:30 | 68 | 68
2017-03-21 09:00 | 68 | 67
2017-03-21 09:30 | 68 | 68
2017-03-21 10:00 | 68 | 68
2017-03-21 10:30 | 69 | 68
2017-03-21 11:00 | 69 | 69
2017-03-21 11:30 | 69 | 68
2017-03-21 12:00 | 69 | 69
2017-03-21 12:30 | 68 | 68
2017-03-21 13:00 | 69 | 69
2017-03-21 13:30 | 69 | 69
2017-03-21 14:00 | 69 | 69
2017-03-21 14:30 | 70 | 70
2017-03-21 15:00 | 73 | 73
2017-03-21 15:30 | 78 | 78
2017-03-21 16:00 | 76 | 76
2017-03-21 16:30 | 79 | 79
2017-03-21 17:00 | 77 | 77
2017-03-21 17:30 | 77 | 76
2017-03-21 18:00 | 75 | 75
2017-03-21 18:30 | 75 | 75
2017-03-21 19:00 | 74 | 73
2017-03-21 19:30 | 74 | 73
2017-03-21 20:00 | 75 | 74
2017-03-21 20:30 | 73 | 73
2017-03-21 21:00 | 73 | 73
2017-03-21 21:30 | 67 | 67
2017-03-21 22:00 | 65 | 65
2017-03-21 22:30 | 63 | 63
2017-03-21 23:00 | 62 | 62
2017-03-21 23:30 | 61 | 60
2017-03-22 | 60 | 60
2017-03-22 00:30 | 59 | 59
2017-03-22 01:00 | 60 | 60
2017-03-22 01:30 | 59 | 59
2017-03-22 02:00 | 59 | 59
2017-03-22 02:30 | 60 | 60
2017-03-22 03:00 | 60 | 60
2017-03-22 03:30 | 59 | 59
2017-03-22 04:00 | 59 | 59
2017-03-22 04:30 | 59 | 59
2017-03-22 05:00 | 58 | 58
2017-03-22 05:30 | 59 | 59
2017-03-22 06:00 | 60 | 60
2017-03-22 06:30 | 60 | 60
2017-03-22 07:00 | 59 | 59
2017-03-22 07:30 | 62 | 61
2017-03-22 08:00 | 63 | 63
2017-03-22 08:30 | 60 | 60
2017-03-22 09:00 | 58 | 58
2017-03-22 09:30 | 61 | 61
2017-03-22 10:00 | 66 | 65
2017-03-22 10:30 | 66 | 66
2017-03-22 11:00 | 66 | 66
2017-03-22 11:30 | 66 | 66
2017-03-22 12:00 | 66 | 66
2017-03-22 12:30 | 67 | 67
2017-03-22 13:00 | 66 | 65
2017-03-22 13:30 | 66 | 66
2017-03-22 14:00 | 67 | 66
2017-03-22 14:30 | 67 | 67
2017-03-22 15:00 | 67 | 67
2017-03-22 15:30 | 68 | 68
2017-03-22 16:00 | 74 | 74
2017-03-22 16:30 | 75 | 75
2017-03-22 17:00 | 76 | 76
2017-03-22 17:30 | 77 | 77
2017-03-22 18:00 | 76 | 76
2017-03-22 18:30 | 73 | 73
2017-03-22 19:00 | 74 | 74
2017-03-22 19:30 | 74 | 74
2017-03-22 20:00 | 74 | 74
2017-03-22 20:30 | 75 | 74
2017-03-22 21:00 | 75 | 75
2017-03-22 21:30 | 75 | 75
2017-03-22 22:00 | 75 | 75
2017-03-22 22:30 | 74 | 74
2017-03-22 23:00 | 67 | 67
2017-03-22 23:30 | 64 | 63
2017-03-23 | 62 | 62
2017-03-23 00:30 | 63 | 63
2017-03-23 01:00 | 62 | 61
2017-03-23 01:30 | 61 | 61
2017-03-23 02:00 | 61 | 61
2017-03-23 02:30 | 61 | 61
2017-03-23 03:00 | 61 | 60
2017-03-23 03:30 | 61 | 60
2017-03-23 04:00 | 61 | 61
2017-03-23 04:30 | 61 | 60
2017-03-23 05:00 | 61 | 61
2017-03-23 05:30 | 61 | 61
2017-03-23 06:00 | 61 | 61
2017-03-23 06:30 | 62 | 61
2017-03-23 07:00 | 60 | 59
2017-03-23 07:30 | 60 | 59
2017-03-23 08:00 | 60 | 60
2017-03-23 08:30 | 61 | 60
2017-03-23 09:00 | 60 | 60
2017-03-23 09:30 | 63 | 63
2017-03-23 10:00 | 70 | 70
2017-03-23 10:30 | 69 | 69
2017-03-23 11:00 | 68 | 68
2017-03-23 11:30 | 70 | 69
2017-03-23 12:00 | 70 | 69
2017-03-23 12:30 | 70 | 70
2017-03-23 13:00 | 68 | 68
2017-03-23 13:30 | 66 | 66
2017-03-23 14:00 | 66 | 66
2017-03-23 14:30 | 68 | 68
2017-03-23 15:00 | 71 | 71
2017-03-23 15:30 | 71 | 71
2017-03-23 16:00 | 71 | 71
2017-03-23 16:30 | 71 | 71
2017-03-23 17:00 | 73 | 73
2017-03-23 17:30 | 73 | 73
2017-03-23 18:00 | 73 | 73
2017-03-23 18:30 | 74 | 73
2017-03-23 19:00 | 75 | 75
2017-03-23 19:30 | 74 | 74
2017-03-23 20:00 | 74 | 74
2017-03-23 20:30 | 74 | 74
2017-03-23 21:00 | 74 | 74
2017-03-23 21:30 | 73 | 73
2017-03-23 22:00 | 72 | 72
2017-03-23 22:30 | 71 | 70
2017-03-23 23:00 | 63 | 63
2017-03-23 23:30 | 60 | 60
2017-03-24 | 60 | 60
2017-03-24 00:30 | 58 | 58
2017-03-24 01:00 | 58 | 58
2017-03-24 01:30 | 58 | 58
2017-03-24 02:00 | 59 | 58
2017-03-24 02:30 | 59 | 58
2017-03-24 03:00 | 58 | 58
2017-03-24 03:30 | 58 | 58
2017-03-24 04:00 | 58 | 57
2017-03-24 04:30 | 60 | 59
2017-03-24 05:00 | 61 | 60
2017-03-24 05:30 | 62 | 61
2017-03-24 06:00 | 63 | 62
2017-03-24 06:30 | 61 | 61
2017-03-24 07:00 | 66 | 66
2017-03-24 07:30 | 71 | 70
2017-03-24 08:00 | 71 | 71
2017-03-24 08:30 | 71 | 71
2017-03-24 09:00 | 70 | 70
2017-03-24 09:30 | 70 | 70
2017-03-24 10:00 | 70 | 70
2017-03-24 10:30 | 70 | 70
2017-03-24 11:00 | 72 | 72
2017-03-24 11:30 | 71 | 71
2017-03-24 12:00 | 71 | 71
2017-03-24 12:30 | 72 | 72
2017-03-24 13:00 | 71 | 71
2017-03-24 13:30 | 71 | 71
2017-03-24 14:00 | 71 | 71
2017-03-24 14:30 | 71 | 71
2017-03-24 15:00 | 72 | 72
2017-03-24 15:30 | 72 | 72
2017-03-24 16:00 | 73 | 73
2017-03-24 16:30 | 72 | 72
2017-03-24 17:00 | 72 | 72
2017-03-24 17:30 | 72 | 72
2017-03-24 18:00 | 72 | 72
2017-03-24 18:30 | 72 | 72
2017-03-24 19:00 | 73 | 73
2017-03-24 19:30 | 74 | 74
2017-03-24 20:00 | 74 | 74
2017-03-24 20:30 | 73 | 73
2017-03-24 21:00 | 72 | 72
2017-03-24 21:30 | 66 | 66
2017-03-24 22:00 | 64 | 64
2017-03-24 22:30 | 64 | 64
2017-03-24 23:00 | 64 | 63
2017-03-24 23:30 | 63 | 63
2017-03-25 | 62 | 62
2017-03-25 00:30 | 62 | 62
2017-03-25 01:00 | 62 | 61
2017-03-25 01:30 | 65 | 63
2017-03-25 02:00 | 65 | 63
2017-03-25 02:30 | 65 | 63
2017-03-25 03:00 | 65 | 63
2017-03-25 03:30 | 65 | 63
2017-03-25 04:00 | 65 | 62
2017-03-25 04:30 | 64 | 61
2017-03-25 05:00 | 63 | 61
2017-03-25 05:30 | 64 | 61
2017-03-25 06:00 | 64 | 62
2017-03-25 06:30 | 63 | 61
2017-03-25 07:00 | 63 | 61
2017-03-25 07:30 | 63 | 61
2017-03-25 08:00 | 64 | 62
2017-03-25 08:30 | 63 | 62
2017-03-25 09:00 | 62 | 61
2017-03-25 09:30 | 64 | 63
2017-03-25 10:00 | 64 | 63
2017-03-25 10:30 | 64 | 62
2017-03-25 11:00 | 64 | 63
2017-03-25 11:30 | 70 | 68
2017-03-25 12:00 | 72 | 70
2017-03-25 12:30 | 72 | 70
2017-03-25 13:00 | 72 | 70
2017-03-25 13:30 | 73 | 71
2017-03-25 14:00 | 74 | 72
2017-03-25 14:30 | 74 | 72
2017-03-25 15:00 | 74 | 72
2017-03-25 15:30 | 75 | 73
2017-03-25 16:00 | 76 | 74
2017-03-25 16:30 | 76 | 75
2017-03-25 17:00 | 74 | 73
2017-03-25 17:30 | 77 | 75
2017-03-25 18:00 | 78 | 76
2017-03-25 18:30 | 80 | 78
2017-03-25 19:00 | 80 | 79
2017-03-25 19:30 | 74 | 74
2017-03-25 20:00 | 72 | 72
2017-03-25 20:30 | 72 | 71
2017-03-25 21:00 | 70 | 69
2017-03-25 21:30 | 69 | 68
2017-03-25 22:00 | 68 | 67
2017-03-25 22:30 | 67 | 66
2017-03-25 23:00 | 66 | 64
2017-03-25 23:30 | 66 | 64
2017-03-26 | 67 | 65
2017-03-26 00:30 | 71 | 69
2017-03-26 01:00 | 71 | 69
2017-03-26 01:30 | 71 | 69
2017-03-26 02:00 | 72 | 68
2017-03-26 02:30 | 71 | 68
2017-03-26 03:00 | 70 | 67
2017-03-26 03:30 | 70 | 67
2017-03-26 04:00 | 70 | 66
2017-03-26 04:30 | 70 | 67
2017-03-26 05:00 | 70 | 66
2017-03-26 05:30 | 70 | 66
2017-03-26 06:00 | 71 | 67
2017-03-26 06:30 | 71 | 68
2017-03-26 07:00 | 71 | 67
2017-03-26 07:30 | 71 | 68
2017-03-26 08:00 | 70 | 67
2017-03-26 08:30 | 70 | 67
2017-03-26 09:00 | 70 | 67
2017-03-26 09:30 | 70 | 68
2017-03-26 10:00 | 70 | 68
2017-03-26 10:30 | 70 | 68
2017-03-26 11:00 | 72 | 69
2017-03-26 11:30 | 71 | 69
2017-03-26 12:00 | 71 | 68
2017-03-26 12:30 | 70 | 68
2017-03-26 13:00 | 71 | 69
2017-03-26 13:30 | 71 | 69
2017-03-26 14:00 | 71 | 68
2017-03-26 14:30 | 71 | 69
2017-03-26 15:00 | 70 | 68
2017-03-26 15:30 | 72 | 70
2017-03-26 16:00 | 62 | 55
2017-03-26 16:30 | 61 | 54
2017-03-26 17:00 | 57 | 45
2017-03-26 17:30 | 65 | 52
2017-03-26 18:00 | 69 | 53
2017-03-26 18:30 | 70 | 56
2017-03-26 19:00 | 65 | 51
2017-03-26 19:30 | 67 | 59
2017-03-26 20:00 | 69 | 61
2017-03-26 20:30 | 78 | 74
2017-03-26 21:00 | 78 | 75
2017-03-26 21:30 | 78 | 75
2017-03-26 22:00 | 78 | 75
2017-03-26 22:30 | 78 | 74
2017-03-26 23:00 | 77 | 74
2017-03-26 23:30 | 76 | 72
2017-03-27 | 77 | 73
2017-03-27 00:30 | 76 | 72
2017-03-27 01:00 | 75 | 71
2017-03-27 01:30 | 75 | 71
2017-03-27 02:00 | 75 | 71
2017-03-27 02:30 | 75 | 70
2017-03-27 03:00 | 75 | 71
2017-03-27 03:30 | 75 | 71
2017-03-27 04:00 | 75 | 71
2017-03-27 04:30 | 76 | 72
2017-03-27 05:00 | 76 | 72
2017-03-27 05:30 | 75 | 72
2017-03-27 06:00 | 76 | 72
2017-03-27 06:30 | 76 | 73
2017-03-27 07:00 | 75 | 72
2017-03-27 07:30 | 71 | 67
2017-03-27 08:00 | 69 | 64
2017-03-27 08:30 | 67 | 62
2017-03-27 09:00 | 67 | 61
2017-03-27 09:30 | 69 | 66
2017-03-27 10:00 | 71 | 68
2017-03-27 10:30 | 70 | 68
2017-03-27 11:00 | 69 | 66
2017-03-27 11:30 | 67 | 64
2017-03-27 12:00 | 66 | 62
2017-03-27 12:30 | 62 | 51
2017-03-27 13:00 | 61 | 50
2017-03-27 13:30 | 57 | 40
2017-03-27 14:00 | 56 | 37
2017-03-27 14:30 | 56 | 37
2017-03-27 15:00 | 56 | 37
2017-03-27 15:30 | 56 | 36
2017-03-27 16:00 | 48 | 36
2017-03-27 16:30 | 40 | 35
2017-03-27 17:00 | 40 | 34
2017-03-27 17:30 | 41 | 36
2017-03-27 18:00 | 41 | 36
2017-03-27 18:30 | 41 | 35
2017-03-27 19:00 | 40 | 35
2017-03-27 19:30 | 39 | 34
2017-03-27 20:00 | 39 | 34
2017-03-27 20:30 | 39 | 33
2017-03-27 21:00 | 40 | 33
2017-03-27 21:30 | 41 | 31
2017-03-27 22:00 | 40 | 31
2017-03-27 22:30 | 39 | 30
2017-03-27 23:00 | 39 | 30
2017-03-27 23:30 | 40 | 30
2017-03-28 | 35 | 28
2017-03-28 00:30 | 36 | 28
2017-03-28 01:00 | 29 | 22
2017-03-28 01:30 | 27 | 20
2017-03-28 02:00 | 27 | 19
2017-03-28 02:30 | 28 | 20
2017-03-28 03:00 | 28 | 20
2017-03-28 03:30 | 28 | 21
2017-03-28 04:00 | 27 | 19
2017-03-28 04:30 | 27 | 20
2017-03-28 05:00 | 27 | 20
2017-03-28 05:30 | 27 | 19
2017-03-28 06:00 | 27 | 19
2017-03-28 06:30 | 26 | 19
2017-03-28 07:00 | 25 | 18
2017-03-28 07:30 | 25 | 18
2017-03-28 08:00 | 24 | 17
2017-03-28 08:30 | 24 | 17
2017-03-28 09:00 | 23 | 17
2017-03-28 09:30 | 23 | 17
2017-03-28 10:00 | 22 | 17
2017-03-28 10:30 | 22 | 16
2017-03-28 11:00 | 22 | 17
2017-03-28 11:30 | 21 | 16
2017-03-28 12:00 | 21 | 15
2017-03-28 12:30 | 25 | 20
2017-03-28 13:00 | 27 | 22
2017-03-28 13:30 | 26 | 21
2017-03-28 14:00 | 25 | 21
2017-03-28 14:30 | 25 | 21
2017-03-28 15:00 | 26 | 22
2017-03-28 15:30 | 25 | 21
2017-03-28 16:00 | 11 | 0
2017-03-28 16:30 | 23 | 22
2017-03-28 17:00 | 29 | 29
2017-03-28 17:30 | 26 | 25
2017-03-28 18:00 | 25 | 24
2017-03-28 18:30 | 23 | 23
2017-03-28 19:00 | 27 | 26
2017-03-28 19:30 | 28 | 28
2017-03-28 20:00 | 27 | 27
2017-03-28 20:30 | 20 | 19
2017-03-28 21:00 | 16 | 14
2017-03-28 21:30 | 8 | 4
2017-03-28 22:00 | 7 | 3
2017-03-28 22:30 | 8 | 3
2017-03-28 23:00 | 10 | 7
2017-03-28 23:30 | 18 | 16
2017-03-29 | 18 | 16
2017-03-29 00:30 | 18 | 16
2017-03-29 01:00 | 19 | 16
2017-03-29 01:30 | 24 | 22
2017-03-29 02:00 | 27 | 25
2017-03-29 02:30 | 29 | 27
2017-03-29 03:00 | 31 | 29
2017-03-29 03:30 | 31 | 29
2017-03-29 04:00 | 31 | 30
2017-03-29 04:30 | 48 | 48
2017-03-29 05:00 | 56 | 55
2017-03-29 05:30 | 57 | 56
2017-03-29 06:00 | 56 | 55
2017-03-29 06:30 | 56 | 56
2017-03-29 07:00 | 57 | 56
2017-03-29 07:30 | 60 | 58
2017-03-29 08:00 | 58 | 58
2017-03-29 08:30 | 59 | 58
2017-03-29 09:00 | 59 | 59
2017-03-29 09:30 | 60 | 59
2017-03-29 10:00 | 60 | 60
2017-03-29 10:30 | 63 | 63
2017-03-29 11:00 | 64 | 64
2017-03-29 11:30 | 64 | 64
2017-03-29 12:00 | 65 | 64
2017-03-29 12:30 | 70 | 70
2017-03-29 13:00 | 71 | 71
2017-03-29 13:30 | 73 | 73
2017-03-29 14:00 | 73 | 73
2017-03-29 14:30 | 74 | 74
2017-03-29 15:00 | 76 | 76
2017-03-29 15:30 | 76 | 75
2017-03-29 16:00 | 75 | 74
2017-03-29 16:30 | 74 | 73
2017-03-29 17:00 | 70 | 68
2017-03-29 17:30 | 74 | 72
2017-03-29 18:00 | 67 | 63
2017-03-29 18:30 | 66 | 59
2017-03-29 19:00 | 62 | 55
2017-03-29 19:30 | 66 | 63
2017-03-29 20:00 | 69 | 67
2017-03-29 20:30 | 70 | 68
2017-03-29 21:00 | 69 | 67
2017-03-29 21:30 | 69 | 66
2017-03-29 22:00 | 69 | 67
2017-03-29 22:30 | 63 | 61
2017-03-29 23:00 | 61 | 59
2017-03-29 23:30 | 62 | 59
2017-03-30 | 62 | 59
2017-03-30 00:30 | 60 | 59
2017-03-30 01:00 | 60 | 59
2017-03-30 01:30 | 60 | 58
2017-03-30 02:00 | 60 | 57
2017-03-30 02:30 | 60 | 57
2017-03-30 03:00 | 59 | 56
2017-03-30 03:30 | 59 | 57
2017-03-30 04:00 | 59 | 57
2017-03-30 04:30 | 60 | 57
2017-03-30 05:00 | 60 | 58
2017-03-30 05:30 | 61 | 59
2017-03-30 06:00 | 61 | 59
2017-03-30 06:30 | 66 | 63
2017-03-30 07:00 | 68 | 66
2017-03-30 07:30 | 68 | 67
2017-03-30 08:00 | 69 | 68
2017-03-30 08:30 | 70 | 69
2017-03-30 09:00 | 70 | 69
2017-03-30 09:30 | 69 | 68
2017-03-30 10:00 | 71 | 70
2017-03-30 10:30 | 70 | 70
2017-03-30 11:00 | 69 | 69
2017-03-30 11:30 | 51 | 41
2017-03-30 12:00 | 59 | 55
2017-03-30 12:30 | 59 | 54
2017-03-30 13:00 | 59 | 55
2017-03-30 13:30 | 62 | 59
2017-03-30 14:00 | 73 | 72
2017-03-30 14:30 | 77 | 77
2017-03-30 15:00 | 73 | 73
2017-03-30 15:30 | 74 | 73
2017-03-30 16:00 | 73 | 73
2017-03-30 16:30 | 74 | 73
2017-03-30 17:00 | 74 | 73
2017-03-30 17:30 | 76 | 76
2017-03-30 18:00 | 76 | 76
2017-03-30 18:30 | 77 | 77
2017-03-30 19:00 | 78 | 78
2017-03-30 19:30 | 79 | 78
2017-03-30 20:00 | 79 | 79
2017-03-30 20:30 | 76 | 76
2017-03-30 21:00 | 77 | 77
2017-03-30 21:30 | 76 | 75
2017-03-30 22:00 | 76 | 75
2017-03-30 22:30 | 75 | 73
2017-03-30 23:00 | 74 | 73
2017-03-30 23:30 | 72 | 71
2017-03-31 | 69 | 68
2017-03-31 00:30 | 64 | 63
2017-03-31 01:00 | 63 | 63
2017-03-31 01:30 | 63 | 62
2017-03-31 02:00 | 62 | 62
2017-03-31 02:30 | 62 | 61
2017-03-31 03:00 | 61 | 60
2017-03-31 03:30 | 61 | 60
2017-03-31 04:00 | 62 | 61
2017-03-31 04:30 | 62 | 62
2017-03-31 05:00 | 63 | 62
2017-03-31 05:30 | 63 | 62
2017-03-31 06:00 | 64 | 63
2017-03-31 06:30 | 68 | 67
2017-03-31 07:00 | 71 | 70
2017-03-31 07:30 | 70 | 69
2017-03-31 08:00 | 70 | 70
2017-03-31 08:30 | 69 | 69
2017-03-31 09:00 | 68 | 68
2017-03-31 09:30 | 66 | 66
2017-03-31 10:00 | 66 | 66
2017-03-31 10:30 | 65 | 64
2017-03-31 11:00 | 65 | 65
2017-03-31 11:30 | 65 | 64
2017-03-31 12:00 | 63 | 62
2017-03-31 12:30 | 66 | 65
2017-03-31 13:00 | 67 | 66
2017-03-31 13:30 | 68 | 67
2017-03-31 14:00 | 68 | 67
2017-03-31 14:30 | 68 | 67
2017-03-31 15:00 | 69 | 68
2017-03-31 15:30 | 69 | 68
2017-03-31 16:00 | 72 | 72
2017-03-31 16:30 | 74 | 73
2017-03-31 17:00 | 65 | 62
2017-03-31 17:30 | 71 | 65
2017-03-31 18:00 | 82 | 74
2017-03-31 18:30 | 82 | 73
2017-03-31 19:00 | 83 | 75
2017-03-31 19:30 | 84 | 75
2017-03-31 20:00 | 84 | 75
2017-03-31 20:30 | 85 | 75
2017-03-31 21:00 | 85 | 75
2017-03-31 21:30 | 85 | 74
2017-03-31 22:00 | 83 | 71
2017-03-31 22:30 | 76 | 70
2017-03-31 23:00 | 72 | 69
2017-03-31 23:30 | 72 | 69
2017-04-01 | 69 | 68
2017-04-01 00:30 | 62 | 61
2017-04-01 01:00 | 61 | 60
2017-04-01 01:30 | 61 | 60
2017-04-01 02:00 | 59 | 58
2017-04-01 02:30 | 59 | 58
2017-04-01 03:00 | 60 | 58
2017-04-01 03:30 | 59 | 58
2017-04-01 04:00 | 59 | 57
2017-04-01 04:30 | 59 | 57
2017-04-01 05:00 | 59 | 57
2017-04-01 05:30 | 59 | 57
2017-04-01 06:00 | 58 | 57
2017-04-01 06:30 | 58 | 57
2017-04-01 07:00 | 58 | 57
2017-04-01 07:30 | 58 | 57
2017-04-01 08:00 | 58 | 56
2017-04-01 08:30 | 57 | 56
2017-04-01 09:00 | 57 | 56
2017-04-01 09:30 | 58 | 57
2017-04-01 10:00 | 59 | 57
2017-04-01 10:30 | 59 | 56
2017-04-01 11:00 | 58 | 56
2017-04-01 11:30 | 58 | 56
2017-04-01 12:00 | 59 | 57
2017-04-01 12:30 | 59 | 57
2017-04-01 13:00 | 59 | 57
2017-04-01 13:30 | 59 | 57
2017-04-01 14:00 | 59 | 57
2017-04-01 14:30 | 61 | 59
2017-04-01 15:00 | 61 | 60
2017-04-01 15:30 | 61 | 59
2017-04-01 16:00 | 62 | 60
2017-04-01 16:30 | 63 | 62
2017-04-01 17:00 | 65 | 63
2017-04-01 17:30 | 66 | 65
2017-04-01 18:00 | 66 | 65
2017-04-01 18:30 | 65 | 63
2017-04-01 19:00 | 65 | 63
2017-04-01 19:30 | 67 | 65
2017-04-01 20:00 | 66 | 65
2017-04-01 20:30 | 65 | 63
2017-04-01 21:00 | 63 | 62
2017-04-01 21:30 | 64 | 62
2017-04-01 22:00 | 64 | 61
2017-04-01 22:30 | 63 | 60
2017-04-01 23:00 | 62 | 59
2017-04-01 23:30 | 60 | 59
2017-04-02 | 60 | 59
2017-04-02 00:30 | 61 | 59
2017-04-02 01:00 | 61 | 59
2017-04-02 01:30 | 61 | 59
2017-04-02 02:00 | 61 | 58
2017-04-02 02:30 | 61 | 58
2017-04-02 03:00 | 60 | 58
2017-04-02 03:30 | 60 | 58
2017-04-02 04:00 | 60 | 57
2017-04-02 04:30 | 59 | 57
2017-04-02 05:00 | 59 | 56
2017-04-02 05:30 | 60 | 57
2017-04-02 06:00 | 59 | 57
2017-04-02 06:30 | 59 | 57
2017-04-02 07:00 | 59 | 57
2017-04-02 07:30 | 60 | 57
2017-04-02 08:00 | 60 | 58
2017-04-02 08:30 | 60 | 59
2017-04-02 09:00 | 60 | 59
2017-04-02 09:30 | 60 | 59
2017-04-02 10:00 | 60 | 59
2017-04-02 10:30 | 61 | 60
2017-04-02 11:00 | 60 | 60
2017-04-02 11:30 | 60 | 59
2017-04-02 12:00 | 60 | 59
2017-04-02 12:30 | 60 | 59
2017-04-02 13:00 | 60 | 59
2017-04-02 13:30 | 61 | 60
2017-04-02 14:00 | 62 | 61
2017-04-02 14:30 | 63 | 61
2017-04-02 15:00 | 64 | 62
2017-04-02 15:30 | 64 | 63
2017-04-02 16:00 | 64 | 63
2017-04-02 16:30 | 65 | 64
2017-04-02 17:00 | 66 | 65
2017-04-02 17:30 | 67 | 65
2017-04-02 18:00 | 66 | 65
2017-04-02 18:30 | 67 | 66
2017-04-02 19:00 | 68 | 67
2017-04-02 19:30 | 69 | 68
2017-04-02 20:00 | 67 | 66
2017-04-02 20:30 | 66 | 65
2017-04-02 21:00 | 66 | 65
2017-04-02 21:30 | 65 | 63
2017-04-02 22:00 | 65 | 63
2017-04-02 22:30 | 64 | 61
2017-04-02 23:00 | 64 | 61
2017-04-02 23:30 | 63 | 60
2017-04-03 | 64 | 60
2017-04-03 00:30 | 64 | 60
2017-04-03 01:00 | 65 | 61
2017-04-03 01:30 | 64 | 61
2017-04-03 02:00 | 64 | 60
2017-04-03 02:30 | 60 | 60
2017-04-03 03:00 | 60 | 60
2017-04-03 03:30 | 60 | 59
2017-04-03 04:00 | 59 | 59
2017-04-03 04:30 | 60 | 60
2017-04-03 05:00 | 62 | 62
2017-04-03 05:30 | 61 | 61
2017-04-03 06:00 | 62 | 61
2017-04-03 06:30 | 63 | 63
2017-04-03 07:00 | 63 | 63
2017-04-03 07:30 | 66 | 65
2017-04-03 08:00 | 67 | 65
2017-04-03 08:30 | 68 | 65
2017-04-03 09:00 | 67 | 64
2017-04-03 09:30 | 67 | 64
2017-04-03 10:00 | 67 | 64
2017-04-03 10:30 | 67 | 64
2017-04-03 11:00 | 67 | 65
2017-04-03 11:30 | 67 | 65
2017-04-03 12:00 | 67 | 64
2017-04-03 12:30 | 68 | 66
2017-04-03 13:00 | 69 | 67
2017-04-03 13:30 | 68 | 67
2017-04-03 14:00 | 69 | 67
2017-04-03 14:30 | 69 | 68
2017-04-03 15:00 | 70 | 68
2017-04-03 15:30 | 72 | 70
2017-04-03 16:00 | 71 | 70
2017-04-03 16:30 | 72 | 71
2017-04-03 17:00 | 74 | 72
2017-04-03 17:30 | 74 | 72
2017-04-03 18:00 | 74 | 71
2017-04-03 18:30 | 74 | 71
2017-04-03 19:00 | 76 | 73
2017-04-03 19:30 | 75 | 73
2017-04-03 20:00 | 75 | 73
2017-04-03 20:30 | 73 | 70
2017-04-03 21:00 | 73 | 70
2017-04-03 21:30 | 70 | 67
2017-04-03 22:00 | 68 | 65
2017-04-03 22:30 | 68 | 64
2017-04-03 23:00 | 67 | 64
2017-04-03 23:30 | 67 | 63
2017-04-04 | 66 | 63
2017-04-04 00:30 | 63 | 61
2017-04-04 01:00 | 64 | 61
2017-04-04 01:30 | 63 | 61
2017-04-04 02:00 | 63 | 60
2017-04-04 02:30 | 63 | 60
2017-04-04 03:00 | 63 | 60
2017-04-04 03:30 | 63 | 60
2017-04-04 04:00 | 63 | 60
2017-04-04 04:30 | 63 | 60
2017-04-04 05:00 | 62 | 59
2017-04-04 05:30 | 63 | 60
2017-04-04 06:00 | 63 | 60
2017-04-04 06:30 | 65 | 63
2017-04-04 07:00 | 68 | 65
2017-04-04 07:30 | 70 | 67
2017-04-04 08:00 | 70 | 67
2017-04-04 08:30 | 67 | 64
2017-04-04 09:00 | 67 | 65
2017-04-04 09:30 | 67 | 65
2017-04-04 10:00 | 66 | 64
2017-04-04 10:30 | 66 | 64
2017-04-04 11:00 | 67 | 65
2017-04-04 11:30 | 66 | 64
2017-04-04 12:00 | 67 | 65
2017-04-04 12:30 | 68 | 66
2017-04-04 13:00 | 68 | 66
2017-04-04 13:30 | 69 | 67
2017-04-04 14:00 | 70 | 68
2017-04-04 14:30 | 70 | 69
2017-04-04 15:00 | 70 | 69
2017-04-04 15:30 | 69 | 68
2017-04-04 16:00 | 71 | 69
2017-04-04 16:30 | 72 | 70
2017-04-04 17:00 | 73 | 71
2017-04-04 17:30 | 73 | 71
2017-04-04 18:00 | 73 | 71
2017-04-04 18:30 | 72 | 69
2017-04-04 19:00 | 75 | 72
2017-04-04 19:30 | 74 | 72
2017-04-04 20:00 | 74 | 71
2017-04-04 20:30 | 74 | 71
2017-04-04 21:00 | 73 | 71
2017-04-04 21:30 | 72 | 69
2017-04-04 22:00 | 71 | 67
2017-04-04 22:30 | 70 | 66
2017-04-04 23:00 | 67 | 65
2017-04-04 23:30 | 64 | 64
2017-04-05 | 65 | 65
2017-04-05 00:30 | 62 | 62
2017-04-05 01:00 | 62 | 62
2017-04-05 01:30 | 61 | 61
2017-04-05 02:00 | 61 | 61
2017-04-05 02:30 | 61 | 61
2017-04-05 03:00 | 60 | 60
2017-04-05 03:30 | 60 | 60
2017-04-05 04:00 | 60 | 59
2017-04-05 04:30 | 60 | 60
2017-04-05 05:00 | 60 | 60
2017-04-05 05:30 | 61 | 60
2017-04-05 06:00 | 60 | 59
2017-04-05 06:30 | 62 | 62
2017-04-05 07:00 | 64 | 63
2017-04-05 07:30 | 64 | 64
2017-04-05 08:00 | 65 | 64
2017-04-05 08:30 | 64 | 64
2017-04-05 09:00 | 66 | 65
2017-04-05 09:30 | 68 | 66
2017-04-05 10:00 | 68 | 66
2017-04-05 10:30 | 68 | 66
2017-04-05 11:00 | 69 | 66
2017-04-05 11:30 | 68 | 66
2017-04-05 12:00 | 71 | 69
2017-04-05 12:30 | 78 | 76
2017-04-05 13:00 | 76 | 74
2017-04-05 13:30 | 70 | 68
2017-04-05 14:00 | 70 | 68
2017-04-05 14:30 | 70 | 68
2017-04-05 15:00 | 71 | 69
2017-04-05 15:30 | 75 | 73
2017-04-05 16:00 | 72 | 70
2017-04-05 16:30 | 73 | 72
2017-04-05 17:00 | 74 | 72
2017-04-05 17:30 | 73 | 71
2017-04-05 18:00 | 73 | 71
2017-04-05 18:30 | 74 | 72
2017-04-05 19:00 | 74 | 73
2017-04-05 19:30 | 75 | 73
2017-04-05 20:00 | 75 | 73
2017-04-05 20:30 | 74 | 72
2017-04-05 21:00 | 72 | 70
2017-04-05 21:30 | 72 | 69
2017-04-05 22:00 | 71 | 68
2017-04-05 22:30 | 73 | 70
2017-04-05 23:00 | 72 | 69
2017-04-05 23:30 | 71 | 68
2017-04-06 | 69 | 65
2017-04-06 00:30 | 64 | 64
2017-04-06 01:00 | 63 | 63
2017-04-06 01:30 | 62 | 62
2017-04-06 02:00 | 61 | 61
2017-04-06 02:30 | 61 | 61
2017-04-06 03:00 | 61 | 61
2017-04-06 03:30 | 60 | 60
2017-04-06 04:00 | 60 | 60
2017-04-06 04:30 | 61 | 60
2017-04-06 05:00 | 60 | 60
2017-04-06 05:30 | 59 | 59
2017-04-06 06:00 | 60 | 60
2017-04-06 06:30 | 62 | 61
2017-04-06 07:00 | 65 | 64
2017-04-06 07:30 | 66 | 65
2017-04-06 08:00 | 70 | 69
2017-04-06 08:30 | 72 | 69
2017-04-06 09:00 | 71 | 69
2017-04-06 09:30 | 72 | 70
2017-04-06 10:00 | 69 | 67
2017-04-06 10:30 | 67 | 64
2017-04-06 11:00 | 67 | 64
2017-04-06 11:30 | 67 | 64
2017-04-06 12:00 | 68 | 65
2017-04-06 12:30 | 69 | 67
2017-04-06 13:00 | 68 | 66
2017-04-06 13:30 | 68 | 66
2017-04-06 14:00 | 69 | 67
2017-04-06 14:30 | 69 | 67
2017-04-06 15:00 | 73 | 72
2017-04-06 15:30 | 72 | 70
2017-04-06 16:00 | 72 | 70
2017-04-06 16:30 | 73 | 71
2017-04-06 17:00 | 73 | 71
2017-04-06 17:30 | 74 | 72
2017-04-06 18:00 | 74 | 71
2017-04-06 18:30 | 74 | 71
2017-04-06 19:00 | 75 | 73
2017-04-06 19:30 | 76 | 74
2017-04-06 20:00 | 75 | 73
2017-04-06 20:30 | 76 | 74
2017-04-06 21:00 | 75 | 73
2017-04-06 21:30 | 73 | 70
2017-04-06 22:00 | 71 | 69
2017-04-06 22:30 | 68 | 67
2017-04-06 23:00 | 67 | 65
2017-04-06 23:30 | 66 | 65
2017-04-07 | 66 | 64
2017-04-07 00:30 | 67 | 65
2017-04-07 01:00 | 66 | 65
2017-04-07 01:30 | 67 | 65
2017-04-07 02:00 | 66 | 64
2017-04-07 02:30 | 66 | 63
2017-04-07 03:00 | 64 | 62
2017-04-07 03:30 | 62 | 62
2017-04-07 04:00 | 63 | 63
2017-04-07 04:30 | 63 | 62
2017-04-07 05:00 | 63 | 63
2017-04-07 05:30 | 63 | 63
2017-04-07 06:00 | 63 | 62
2017-04-07 06:30 | 64 | 63
2017-04-07 07:00 | 66 | 65
2017-04-07 07:30 | 67 | 66
2017-04-07 08:00 | 67 | 66
2017-04-07 08:30 | 67 | 66
2017-04-07 09:00 | 72 | 72
2017-04-07 09:30 | 67 | 67
2017-04-07 10:00 | 67 | 67
2017-04-07 10:30 | 66 | 65
2017-04-07 11:00 | 65 | 65
2017-04-07 11:30 | 71 | 71
2017-04-07 12:00 | 71 | 71
2017-04-07 12:30 | 68 | 67
2017-04-07 13:00 | 68 | 68
2017-04-07 13:30 | 69 | 69
2017-04-07 14:00 | 75 | 75
2017-04-07 14:30 | 69 | 69
2017-04-07 15:00 | 70 | 70
2017-04-07 15:30 | 78 | 78
2017-04-07 16:00 | 73 | 72
2017-04-07 16:30 | 79 | 79
2017-04-07 17:00 | 78 | 78
2017-04-07 17:30 | 79 | 79
2017-04-07 18:00 | 79 | 79
2017-04-07 18:30 | 79 | 79
2017-04-07 19:00 | 79 | 79
2017-04-07 19:30 | 80 | 80
2017-04-07 20:00 | 79 | 79
2017-04-07 20:30 | 73 | 73
2017-04-07 21:00 | 71 | 71
2017-04-07 21:30 | 70 | 70
2017-04-07 22:00 | 70 | 70
2017-04-07 22:30 | 68 | 68
2017-04-07 23:00 | 67 | 67
2017-04-07 23:30 | 66 | 66
2017-04-08 | 66 | 65
2017-04-08 00:30 | 67 | 66
2017-04-08 01:00 | 64 | 63
2017-04-08 01:30 | 64 | 63
2017-04-08 02:00 | 62 | 61
2017-04-08 02:30 | 62 | 61
2017-04-08 03:00 | 63 | 62
2017-04-08 03:30 | 63 | 62
2017-04-08 04:00 | 63 | 62
2017-04-08 04:30 | 63 | 62
2017-04-08 05:00 | 63 | 62
2017-04-08 05:30 | 63 | 62
2017-04-08 06:00 | 63 | 62
2017-04-08 06:30 | 63 | 62
2017-04-08 07:00 | 64 | 63
2017-04-08 07:30 | 65 | 64
2017-04-08 08:00 | 64 | 63
2017-04-08 08:30 | 64 | 64
2017-04-08 09:00 | 67 | 67
2017-04-08 09:30 | 68 | 68
2017-04-08 10:00 | 68 | 68
2017-04-08 10:30 | 68 | 68
2017-04-08 11:00 | 67 | 67
2017-04-08 11:30 | 68 | 68
2017-04-08 12:00 | 69 | 69
2017-04-08 12:30 | 69 | 69
2017-04-08 13:00 | 70 | 70
2017-04-08 13:30 | 69 | 69
2017-04-08 14:00 | 69 | 69
2017-04-08 14:30 | 69 | 69
2017-04-08 15:00 | 70 | 70
2017-04-08 15:30 | 70 | 70
2017-04-08 16:00 | 70 | 70
2017-04-08 16:30 | 71 | 71
2017-04-08 17:00 | 74 | 74
2017-04-08 17:30 | 74 | 74
2017-04-08 18:00 | 74 | 74
2017-04-08 18:30 | 74 | 74
2017-04-08 19:00 | 75 | 75
2017-04-08 19:30 | 75 | 75
2017-04-08 20:00 | 73 | 73
2017-04-08 20:30 | 72 | 72
2017-04-08 21:00 | 71 | 71
2017-04-08 21:30 | 71 | 71
2017-04-08 22:00 | 70 | 70
2017-04-08 22:30 | 69 | 69
2017-04-08 23:00 | 68 | 68
2017-04-08 23:30 | 68 | 68
2017-04-09 | 67 | 67
2017-04-09 00:30 | 67 | 66
2017-04-09 01:00 | 67 | 66
2017-04-09 01:30 | 66 | 65
2017-04-09 02:00 | 66 | 66
2017-04-09 02:30 | 66 | 65
2017-04-09 03:00 | 65 | 64
2017-04-09 03:30 | 65 | 64
2017-04-09 04:00 | 65 | 64
2017-04-09 04:30 | 65 | 64
2017-04-09 05:00 | 65 | 64
2017-04-09 05:30 | 65 | 64
2017-04-09 06:00 | 64 | 63
2017-04-09 06:30 | 64 | 63
2017-04-09 07:00 | 65 | 64
2017-04-09 07:30 | 66 | 65
2017-04-09 08:00 | 66 | 65
2017-04-09 08:30 | 66 | 65
2017-04-09 09:00 | 66 | 65
2017-04-09 09:30 | 66 | 66
2017-04-09 10:00 | 66 | 66
2017-04-09 10:30 | 66 | 66
2017-04-09 11:00 | 66 | 65
2017-04-09 11:30 | 66 | 66
2017-04-09 12:00 | 67 | 67
2017-04-09 12:30 | 68 | 67
2017-04-09 13:00 | 68 | 68
2017-04-09 13:30 | 68 | 68
2017-04-09 14:00 | 68 | 68
2017-04-09 14:30 | 69 | 69
2017-04-09 15:00 | 69 | 69
2017-04-09 15:30 | 69 | 69
2017-04-09 16:00 | 71 | 71
2017-04-09 16:30 | 71 | 71
2017-04-09 17:00 | 73 | 73
2017-04-09 17:30 | 74 | 74
2017-04-09 18:00 | 72 | 72
2017-04-09 18:30 | 74 | 74
2017-04-09 19:00 | 76 | 76
2017-04-09 19:30 | 76 | 76
2017-04-09 20:00 | 75 | 74
2017-04-09 20:30 | 74 | 73
2017-04-09 21:00 | 73 | 73
2017-04-09 21:30 | 73 | 72
2017-04-09 22:00 | 71 | 70
2017-04-09 22:30 | 72 | 70
2017-04-09 23:00 | 71 | 70
2017-04-09 23:30 | 69 | 68
2017-04-10 | 67 | 67
2017-04-10 00:30 | 70 | 67
2017-04-10 01:00 | 69 | 67
2017-04-10 01:30 | 69 | 66
2017-04-10 02:00 | 68 | 66
2017-04-10 02:30 | 68 | 66
2017-04-10 03:00 | 68 | 66
2017-04-10 03:30 | 67 | 66
2017-04-10 04:00 | 67 | 65
2017-04-10 04:30 | 68 | 66
2017-04-10 05:00 | 70 | 68
2017-04-10 05:30 | 70 | 68
2017-04-10 06:00 | 70 | 68
2017-04-10 06:30 | 71 | 69
2017-04-10 07:00 | 68 | 67
2017-04-10 07:30 | 73 | 72
2017-04-10 08:00 | 75 | 74
2017-04-10 08:30 | 77 | 76
2017-04-10 09:00 | 77 | 76
2017-04-10 09:30 | 79 | 78
2017-04-10 10:00 | 78 | 77
2017-04-10 10:30 | 76 | 75
2017-04-10 11:00 | 77 | 76
2017-04-10 11:30 | 76 | 76
2017-04-10 12:00 | 77 | 76
2017-04-10 12:30 | 78 | 77
2017-04-10 13:00 | 78 | 77
2017-04-10 13:30 | 79 | 78
2017-04-10 14:00 | 79 | 78
2017-04-10 14:30 | 77 | 76
2017-04-10 15:00 | 76 | 75
2017-04-10 15:30 | 76 | 75
2017-04-10 16:00 | 76 | 76
2017-04-10 16:30 | 76 | 76
2017-04-10 17:00 | 77 | 77
2017-04-10 17:30 | 77 | 76
2017-04-10 18:00 | 78 | 78
2017-04-10 18:30 | 80 | 80
2017-04-10 19:00 | 81 | 80
2017-04-10 19:30 | 80 | 79
2017-04-10 20:00 | 78 | 78
2017-04-10 20:30 | 76 | 76
2017-04-10 21:00 | 76 | 75
2017-04-10 21:30 | 75 | 75
2017-04-10 22:00 | 74 | 74
2017-04-10 22:30 | 73 | 73
2017-04-10 23:00 | 73 | 73
2017-04-10 23:30 | 72 | 72
2017-04-11 | 72 | 72
2017-04-11 00:30 | 72 | 72
2017-04-11 01:00 | 72 | 72
2017-04-11 01:30 | 72 | 72
2017-04-11 02:00 | 71 | 71
2017-04-11 02:30 | 72 | 72
2017-04-11 03:00 | 72 | 72
2017-04-11 03:30 | 72 | 72
2017-04-11 04:00 | 72 | 72
2017-04-11 04:30 | 71 | 71
2017-04-11 05:00 | 72 | 72
2017-04-11 05:30 | 73 | 73
2017-04-11 06:00 | 73 | 73
2017-04-11 06:30 | 73 | 72
2017-04-11 07:00 | 75 | 74
2017-04-11 07:30 | 74 | 74
2017-04-11 08:00 | 75 | 74
2017-04-11 08:30 | 75 | 74
2017-04-11 09:00 | 74 | 74
2017-04-11 09:30 | 74 | 73
2017-04-11 10:00 | 73 | 72
2017-04-11 10:30 | 73 | 73
2017-04-11 11:00 | 73 | 73
2017-04-11 11:30 | 74 | 74
2017-04-11 12:00 | 74 | 74
2017-04-11 12:30 | 74 | 74
2017-04-11 13:00 | 74 | 74
2017-04-11 13:30 | 75 | 75
2017-04-11 14:00 | 76 | 75
2017-04-11 14:30 | 76 | 76
2017-04-11 15:00 | 77 | 77
2017-04-11 15:30 | 77 | 76
2017-04-11 16:00 | 77 | 77
2017-04-11 16:30 | 80 | 80
2017-04-11 17:00 | 80 | 80
2017-04-11 17:30 | 81 | 81
2017-04-11 18:00 | 81 | 80
2017-04-11 18:30 | 65 | 58
2017-04-11 19:00 | 72 | 68
2017-04-11 19:30 | 82 | 81
2017-04-11 20:00 | 82 | 81
2017-04-11 20:30 | 80 | 80
2017-04-11 21:00 | 80 | 79
2017-04-11 21:30 | 79 | 78
2017-04-11 22:00 | 77 | 76
2017-04-11 22:30 | 77 | 75
2017-04-11 23:00 | 76 | 75
2017-04-11 23:30 | 75 | 74
2017-04-12 | 75 | 74
2017-04-12 00:30 | 74 | 73
2017-04-12 01:00 | 68 | 68
2017-04-12 01:30 | 68 | 67
2017-04-12 02:00 | 67 | 67
2017-04-12 02:30 | 67 | 67
2017-04-12 03:00 | 67 | 67
2017-04-12 03:30 | 67 | 66
2017-04-12 04:00 | 67 | 67
2017-04-12 04:30 | 67 | 67
2017-04-12 05:00 | 67 | 66
2017-04-12 05:30 | 67 | 67
2017-04-12 06:00 | 68 | 67
2017-04-12 06:30 | 70 | 68
2017-04-12 07:00 | 72 | 71
2017-04-12 07:30 | 74 | 73
2017-04-12 08:00 | 74 | 73
2017-04-12 08:30 | 76 | 75
2017-04-12 09:00 | 75 | 75
2017-04-12 09:30 | 75 | 75
2017-04-12 10:00 | 74 | 74
2017-04-12 10:30 | 74 | 73
2017-04-12 11:00 | 76 | 75
2017-04-12 11:30 | 78 | 77
2017-04-12 12:00 | 77 | 77
2017-04-12 12:30 | 77 | 77
2017-04-12 13:00 | 79 | 78
2017-04-12 13:30 | 80 | 79
2017-04-12 14:00 | 79 | 79
2017-04-12 14:30 | 79 | 78
2017-04-12 15:00 | 79 | 78
2017-04-12 15:30 | 81 | 80
2017-04-12 16:00 | 81 | 80
2017-04-12 16:30 | 80 | 80
2017-04-12 17:00 | 82 | 82
2017-04-12 17:30 | 82 | 82
2017-04-12 18:00 | 82 | 82
2017-04-12 18:30 | 82 | 81
2017-04-12 19:00 | 85 | 84
2017-04-12 19:30 | 86 | 85
2017-04-12 20:00 | 84 | 83
2017-04-12 20:30 | 82 | 81
2017-04-12 21:00 | 82 | 81
2017-04-12 21:30 | 81 | 80
2017-04-12 22:00 | 82 | 81
2017-04-12 22:30 | 79 | 77
2017-04-12 23:00 | 78 | 76
2017-04-12 23:30 | 77 | 75
2017-04-13 | 76 | 73
2017-04-13 00:30 | 75 | 73
2017-04-13 01:00 | 73 | 72
2017-04-13 01:30 | 72 | 72
2017-04-13 02:00 | 72 | 71
2017-04-13 02:30 | 72 | 71
2017-04-13 03:00 | 71 | 70
2017-04-13 03:30 | 71 | 70
2017-04-13 04:00 | 71 | 70
2017-04-13 04:30 | 72 | 71
2017-04-13 05:00 | 71 | 70
2017-04-13 05:30 | 71 | 70
2017-04-13 06:00 | 71 | 70
2017-04-13 06:30 | 75 | 74
2017-04-13 07:00 | 77 | 76
2017-04-13 07:30 | 78 | 77
2017-04-13 08:00 | 79 | 78
2017-04-13 08:30 | 78 | 77
2017-04-13 09:00 | 78 | 77
2017-04-13 09:30 | 78 | 77
2017-04-13 10:00 | 77 | 76
2017-04-13 10:30 | 77 | 76
2017-04-13 11:00 | 77 | 76
2017-04-13 11:30 | 78 | 77
2017-04-13 12:00 | 79 | 78
2017-04-13 12:30 | 79 | 79
2017-04-13 13:00 | 79 | 79
2017-04-13 13:30 | 79 | 78
2017-04-13 14:00 | 78 | 78
2017-04-13 14:30 | 80 | 80
2017-04-13 15:00 | 82 | 82
2017-04-13 15:30 | 83 | 83
2017-04-13 16:00 | 84 | 84
2017-04-13 16:30 | 85 | 84
2017-04-13 17:00 | 86 | 85
2017-04-13 17:30 | 86 | 85
2017-04-13 18:00 | 85 | 84
2017-04-13 18:30 | 86 | 86
2017-04-13 19:00 | 87 | 86
2017-04-13 19:30 | 86 | 85
2017-04-13 20:00 | 86 | 85
2017-04-13 20:30 | 84 | 83
2017-04-13 21:00 | 84 | 83
2017-04-13 21:30 | 84 | 83
2017-04-13 22:00 | 82 | 81
2017-04-13 22:30 | 82 | 81
2017-04-13 23:00 | 83 | 81
2017-04-13 23:30 | 82 | 80
2017-04-14 | 78 | 76
2017-04-14 00:30 | 76 | 75
2017-04-14 01:00 | 70 | 70
2017-04-14 01:30 | 71 | 71
2017-04-14 02:00 | 72 | 71
2017-04-14 02:30 | 71 | 71
2017-04-14 03:00 | 71 | 70
2017-04-14 03:30 | 70 | 69
2017-04-14 04:00 | 70 | 69
2017-04-14 04:30 | 69 | 68
2017-04-14 05:00 | 69 | 68
2017-04-14 05:30 | 70 | 69
2017-04-14 06:00 | 69 | 68
2017-04-14 06:30 | 71 | 70
2017-04-14 07:00 | 72 | 71
2017-04-14 07:30 | 72 | 71
2017-04-14 08:00 | 72 | 71
2017-04-14 08:30 | 72 | 72
2017-04-14 09:00 | 73 | 72
2017-04-14 09:30 | 72 | 72
2017-04-14 10:00 | 72 | 71
2017-04-14 10:30 | 71 | 70
2017-04-14 11:00 | 70 | 69
2017-04-14 11:30 | 71 | 70
2017-04-14 12:00 | 72 | 71
2017-04-14 12:30 | 73 | 72
2017-04-14 13:00 | 74 | 73
2017-04-14 13:30 | 74 | 74
2017-04-14 14:00 | 73 | 73
2017-04-14 14:30 | 75 | 74
2017-04-14 15:00 | 75 | 74
2017-04-14 15:30 | 74 | 74
2017-04-14 16:00 | 75 | 74
2017-04-14 16:30 | 76 | 76
2017-04-14 17:00 | 77 | 76
2017-04-14 17:30 | 76 | 76
2017-04-14 18:00 | 76 | 76
2017-04-14 18:30 | 78 | 77
2017-04-14 19:00 | 78 | 78
2017-04-14 19:30 | 79 | 78
2017-04-14 20:00 | 78 | 78
2017-04-14 20:30 | 76 | 76
2017-04-14 21:00 | 75 | 75
2017-04-14 21:30 | 75 | 75
2017-04-14 22:00 | 75 | 75
2017-04-14 22:30 | 75 | 74
2017-04-14 23:00 | 74 | 73
2017-04-14 23:30 | 74 | 73
2017-04-15 | 70 | 70
2017-04-15 00:30 | 69 | 69
2017-04-15 01:00 | 69 | 68
2017-04-15 01:30 | 69 | 68
2017-04-15 02:00 | 69 | 68
2017-04-15 02:30 | 68 | 68
2017-04-15 03:00 | 68 | 68
2017-04-15 03:30 | 67 | 67
2017-04-15 04:00 | 69 | 68
2017-04-15 04:30 | 68 | 67
2017-04-15 05:00 | 69 | 68
2017-04-15 05:30 | 68 | 67
2017-04-15 06:00 | 67 | 66
2017-04-15 06:30 | 67 | 66
2017-04-15 07:00 | 68 | 67
2017-04-15 07:30 | 69 | 68
2017-04-15 08:00 | 69 | 68
2017-04-15 08:30 | 68 | 68
2017-04-15 09:00 | 70 | 68
2017-04-15 09:30 | 69 | 68
2017-04-15 10:00 | 68 | 67
2017-04-15 10:30 | 68 | 66
2017-04-15 11:00 | 68 | 67
2017-04-15 11:30 | 69 | 68
2017-04-15 12:00 | 70 | 69
2017-04-15 12:30 | 71 | 69
2017-04-15 13:00 | 70 | 68
2017-04-15 13:30 | 69 | 68
2017-04-15 14:00 | 70 | 68
2017-04-15 14:30 | 71 | 69
2017-04-15 15:00 | 71 | 69
2017-04-15 15:30 | 71 | 69
2017-04-15 16:00 | 71 | 69
2017-04-15 16:30 | 72 | 70
2017-04-15 17:00 | 73 | 71
2017-04-15 17:30 | 73 | 72
2017-04-15 18:00 | 74 | 72
2017-04-15 18:30 | 74 | 73
2017-04-15 19:00 | 76 | 75
2017-04-15 19:30 | 75 | 75
2017-04-15 20:00 | 74 | 73
2017-04-15 20:30 | 74 | 73
2017-04-15 21:00 | 72 | 71
2017-04-15 21:30 | 72 | 71
2017-04-15 22:00 | 72 | 70
2017-04-15 22:30 | 71 | 70
2017-04-15 23:00 | 70 | 69
2017-04-15 23:30 | 70 | 68
2017-04-16 | 70 | 68
2017-04-16 00:30 | 70 | 68
2017-04-16 01:00 | 69 | 67
2017-04-16 01:30 | 70 | 67
2017-04-16 02:00 | 69 | 67
2017-04-16 02:30 | 69 | 67
2017-04-16 03:00 | 70 | 67
2017-04-16 03:30 | 69 | 66
2017-04-16 04:00 | 70 | 66
2017-04-16 04:30 | 70 | 66
2017-04-16 05:00 | 68 | 65
2017-04-16 05:30 | 69 | 65
2017-04-16 06:00 | 68 | 65
2017-04-16 06:30 | 67 | 63
2017-04-16 07:00 | 67 | 64
2017-04-16 07:30 | 68 | 65
2017-04-16 08:00 | 69 | 65
2017-04-16 08:30 | 69 | 66
2017-04-16 09:00 | 69 | 67
2017-04-16 09:30 | 68 | 66
2017-04-16 10:00 | 68 | 66
2017-04-16 10:30 | 68 | 66
2017-04-16 11:00 | 69 | 67
2017-04-16 11:30 | 69 | 67
2017-04-16 12:00 | 69 | 67
2017-04-16 12:30 | 69 | 67
2017-04-16 13:00 | 69 | 67
2017-04-16 13:30 | 69 | 67
2017-04-16 14:00 | 70 | 67
2017-04-16 14:30 | 70 | 68
2017-04-16 15:00 | 70 | 68
2017-04-16 15:30 | 70 | 68
2017-04-16 16:00 | 70 | 68
2017-04-16 16:30 | 71 | 69
2017-04-16 17:00 | 72 | 70
2017-04-16 17:30 | 73 | 71
2017-04-16 18:00 | 73 | 72
2017-04-16 18:30 | 74 | 72
2017-04-16 19:00 | 74 | 73
2017-04-16 19:30 | 74 | 73
2017-04-16 20:00 | 74 | 73
2017-04-16 20:30 | 71 | 70
2017-04-16 21:00 | 71 | 69
2017-04-16 21:30 | 71 | 69
2017-04-16 22:00 | 70 | 69
2017-04-16 22:30 | 70 | 68
2017-04-16 23:00 | 69 | 68
2017-04-16 23:30 | 67 | 66
2017-04-17 | 68 | 67
2017-04-17 00:30 | 67 | 66
2017-04-17 01:00 | 67 | 66
2017-04-17 01:30 | 67 | 66
2017-04-17 02:00 | 67 | 66
2017-04-17 02:30 | 67 | 66
2017-04-17 03:00 | 67 | 66
2017-04-17 03:30 | 66 | 65
2017-04-17 04:00 | 66 | 65
2017-04-17 04:30 | 66 | 65
2017-04-17 05:00 | 66 | 65
2017-04-17 05:30 | 66 | 65
2017-04-17 06:00 | 67 | 65
2017-04-17 06:30 | 66 | 65
2017-04-17 07:00 | 65 | 64
2017-04-17 07:30 | 66 | 65
2017-04-17 08:00 | 67 | 66
2017-04-17 08:30 | 67 | 66
2017-04-17 09:00 | 67 | 66
2017-04-17 09:30 | 66 | 65
2017-04-17 10:00 | 66 | 66
2017-04-17 10:30 | 67 | 66
2017-04-17 11:00 | 66 | 66
2017-04-17 11:30 | 67 | 67
2017-04-17 12:00 | 68 | 68
2017-04-17 12:30 | 68 | 68
2017-04-17 13:00 | 68 | 68
2017-04-17 13:30 | 67 | 67
2017-04-17 14:00 | 67 | 67
2017-04-17 14:30 | 69 | 68
2017-04-17 15:00 | 71 | 69
2017-04-17 15:30 | 71 | 70
2017-04-17 16:00 | 70 | 69
2017-04-17 16:30 | 72 | 71
2017-04-17 17:00 | 73 | 72
2017-04-17 17:30 | 74 | 73
2017-04-17 18:00 | 74 | 73
2017-04-17 18:30 | 73 | 72
2017-04-17 19:00 | 74 | 73
2017-04-17 19:30 | 74 | 74
2017-04-17 20:00 | 73 | 72
2017-04-17 20:30 | 71 | 70
2017-04-17 21:00 | 71 | 70
2017-04-17 21:30 | 71 | 70
2017-04-17 22:00 | 71 | 69
2017-04-17 22:30 | 71 | 69
2017-04-17 23:00 | 70 | 67
2017-04-17 23:30 | 70 | 67
2017-04-18 | 70 | 68
2017-04-18 00:30 | 70 | 67
2017-04-18 01:00 | 70 | 67
2017-04-18 01:30 | 69 | 66
2017-04-18 02:00 | 69 | 66
2017-04-18 02:30 | 70 | 67
2017-04-18 03:00 | 70 | 66
2017-04-18 03:30 | 69 | 66
2017-04-18 04:00 | 69 | 65
2017-04-18 04:30 | 69 | 66
2017-04-18 05:00 | 69 | 66
2017-04-18 05:30 | 70 | 66
2017-04-18 06:00 | 69 | 66
2017-04-18 06:30 | 68 | 66
2017-04-18 07:00 | 70 | 68
2017-04-18 07:30 | 70 | 69
2017-04-18 08:00 | 70 | 69
2017-04-18 08:30 | 69 | 68
2017-04-18 09:00 | 69 | 69
2017-04-18 09:30 | 69 | 69
2017-04-18 10:00 | 70 | 70
2017-04-18 10:30 | 70 | 70
2017-04-18 11:00 | 70 | 70
2017-04-18 11:30 | 70 | 70
2017-04-18 12:00 | 69 | 69
2017-04-18 12:30 | 70 | 70
2017-04-18 13:00 | 71 | 70
2017-04-18 13:30 | 71 | 70
2017-04-18 14:00 | 71 | 70
2017-04-18 14:30 | 72 | 71
2017-04-18 15:00 | 72 | 71
2017-04-18 15:30 | 73 | 72
2017-04-18 16:00 | 74 | 73
2017-04-18 16:30 | 75 | 74
2017-04-18 17:00 | 75 | 74
2017-04-18 17:30 | 75 | 74
2017-04-18 18:00 | 76 | 75
2017-04-18 18:30 | 77 | 76
2017-04-18 19:00 | 78 | 77
2017-04-18 19:30 | 78 | 77
2017-04-18 20:00 | 76 | 75
2017-04-18 20:30 | 76 | 74
2017-04-18 21:00 | 76 | 74
2017-04-18 21:30 | 74 | 72
2017-04-18 22:00 | 74 | 72
2017-04-18 22:30 | 73 | 70
2017-04-18 23:00 | 73 | 70
2017-04-18 23:30 | 73 | 69
2017-04-19 | 72 | 68
2017-04-19 00:30 | 72 | 68
2017-04-19 01:00 | 72 | 68
2017-04-19 01:30 | 72 | 67
2017-04-19 02:00 | 70 | 66
2017-04-19 02:30 | 70 | 64
2017-04-19 03:00 | 70 | 64
2017-04-19 03:30 | 68 | 63
2017-04-19 04:00 | 68 | 62
2017-04-19 04:30 | 52 | 48
2017-04-19 05:00 | 46 | 45
2017-04-19 05:30 | 39 | 35
2017-04-19 06:00 | 38 | 34
2017-04-19 06:30 | 35 | 30
2017-04-19 07:00 | 35 | 30
2017-04-19 07:30 | 35 | 32
2017-04-19 08:00 | 34 | 31
2017-04-19 08:30 | 34 | 32
2017-04-19 09:00 | 33 | 31
2017-04-19 09:30 | 35 | 31
2017-04-19 10:00 | 48 | 31
2017-04-19 10:30 | 49 | 32
2017-04-19 11:00 | 51 | 34
2017-04-19 11:30 | 52 | 35
2017-04-19 12:00 | 52 | 35
2017-04-19 12:30 | 52 | 35
2017-04-19 13:00 | 72 | 61
2017-04-19 13:30 | 78 | 65
2017-04-19 14:00 | 78 | 65
2017-04-19 14:30 | 69 | 64
2017-04-19 15:00 | 67 | 65
2017-04-19 15:30 | 68 | 65
2017-04-19 16:00 | 68 | 65
2017-04-19 16:30 | 69 | 67
2017-04-19 17:00 | 70 | 67
2017-04-19 17:30 | 65 | 62
2017-04-19 18:00 | 44 | 41
2017-04-19 18:30 | 44 | 40
2017-04-19 19:00 | 46 | 43
2017-04-19 19:30 | 53 | 52
2017-04-19 20:00 | 56 | 55
2017-04-19 20:30 | 58 | 57
2017-04-19 21:00 | 57 | 56
2017-04-19 21:30 | 63 | 62
2017-04-19 22:00 | 64 | 64
2017-04-19 22:30 | 64 | 64
2017-04-19 23:00 | 66 | 66
2017-04-19 23:30 | 66 | 66
2017-04-20 | 67 | 67
2017-04-20 00:30 | 68 | 68
2017-04-20 01:00 | 69 | 69
2017-04-20 01:30 | 71 | 71
2017-04-20 02:00 | 72 | 72
2017-04-20 02:30 | 72 | 72
2017-04-20 03:00 | 73 | 73
2017-04-20 03:30 | 74 | 74
2017-04-20 04:00 | 73 | 73
2017-04-20 04:30 | 73 | 73
2017-04-20 05:00 | 72 | 72
2017-04-20 05:30 | 73 | 73
2017-04-20 06:00 | 74 | 73
2017-04-20 06:30 | 72 | 72
2017-04-20 07:00 | 72 | 72
2017-04-20 07:30 | 75 | 74
2017-04-20 08:00 | 75 | 74
2017-04-20 08:30 | 75 | 74
2017-04-20 09:00 | 74 | 73
2017-04-20 09:30 | 74 | 72
2017-04-20 10:00 | 74 | 72
2017-04-20 10:30 | 75 | 73
2017-04-20 11:00 | 74 | 73
2017-04-20 11:30 | 73 | 72
2017-04-20 12:00 | 74 | 73
2017-04-20 12:30 | 74 | 73
2017-04-20 13:00 | 75 | 73
2017-04-20 13:30 | 75 | 74
2017-04-20 14:00 | 75 | 74
2017-04-20 14:30 | 76 | 75
2017-04-20 15:00 | 78 | 77
2017-04-20 15:30 | 78 | 77
2017-04-20 16:00 | 82 | 81
2017-04-20 16:30 | 83 | 81
2017-04-20 17:00 | 83 | 81
2017-04-20 17:30 | 83 | 81
2017-04-20 18:00 | 83 | 81
2017-04-20 18:30 | 83 | 82
2017-04-20 19:00 | 84 | 82
2017-04-20 19:30 | 83 | 82
2017-04-20 20:00 | 82 | 80
2017-04-20 20:30 | 81 | 79
2017-04-20 21:00 | 81 | 80
2017-04-20 21:30 | 76 | 75
2017-04-20 22:00 | 74 | 74
2017-04-20 22:30 | 74 | 73
2017-04-20 23:00 | 74 | 73
2017-04-20 23:30 | 73 | 72
2017-04-21 | 73 | 71
2017-04-21 00:30 | 73 | 72
2017-04-21 01:00 | 73 | 72
2017-04-21 01:30 | 73 | 72
2017-04-21 02:00 | 73 | 72
2017-04-21 02:30 | 73 | 72
2017-04-21 03:00 | 72 | 71
2017-04-21 03:30 | 73 | 72
2017-04-21 04:00 | 73 | 72
2017-04-21 04:30 | 72 | 71
2017-04-21 05:00 | 72 | 71
2017-04-21 05:30 | 72 | 71
2017-04-21 06:00 | 72 | 71
2017-04-21 06:30 | 74 | 73
2017-04-21 07:00 | 73 | 72
2017-04-21 07:30 | 74 | 73
2017-04-21 08:00 | 75 | 74
2017-04-21 08:30 | 74 | 72
2017-04-21 09:00 | 73 | 71
2017-04-21 09:30 | 73 | 71
2017-04-21 10:00 | 73 | 72
2017-04-21 10:30 | 73 | 72
2017-04-21 11:00 | 74 | 72
2017-04-21 11:30 | 74 | 72
2017-04-21 12:00 | 75 | 74
2017-04-21 12:30 | 74 | 73
2017-04-21 13:00 | 74 | 73
2017-04-21 13:30 | 75 | 74
2017-04-21 14:00 | 75 | 74
2017-04-21 14:30 | 77 | 76
2017-04-21 15:00 | 79 | 77
2017-04-21 15:30 | 77 | 76
2017-04-21 16:00 | 81 | 79
2017-04-21 16:30 | 82 | 80
2017-04-21 17:00 | 83 | 82
2017-04-21 17:30 | 84 | 82
2017-04-21 18:00 | 85 | 83
2017-04-21 18:30 | 84 | 82
2017-04-21 19:00 | 85 | 83
2017-04-21 19:30 | 86 | 84
2017-04-21 20:00 | 83 | 82
2017-04-21 20:30 | 81 | 80
2017-04-21 21:00 | 81 | 80
2017-04-21 21:30 | 76 | 76
2017-04-21 22:00 | 75 | 74
2017-04-21 22:30 | 75 | 74
2017-04-21 23:00 | 75 | 74
2017-04-21 23:30 | 74 | 73
2017-04-22 | 74 | 72
2017-04-22 00:30 | 73 | 72
2017-04-22 01:00 | 69 | 68
2017-04-22 01:30 | 69 | 68
2017-04-22 02:00 | 69 | 67
2017-04-22 02:30 | 69 | 67
2017-04-22 03:00 | 69 | 68
2017-04-22 03:30 | 69 | 68
2017-04-22 04:00 | 69 | 67
2017-04-22 04:30 | 69 | 67
2017-04-22 05:00 | 69 | 67
2017-04-22 05:30 | 68 | 67
2017-04-22 06:00 | 67 | 66
2017-04-22 06:30 | 67 | 65
2017-04-22 07:00 | 66 | 65
2017-04-22 07:30 | 68 | 67
2017-04-22 08:00 | 69 | 68
2017-04-22 08:30 | 68 | 68
2017-04-22 09:00 | 68 | 68
2017-04-22 09:30 | 69 | 68
2017-04-22 10:00 | 68 | 68
2017-04-22 10:30 | 68 | 68
2017-04-22 11:00 | 67 | 67
2017-04-22 11:30 | 66 | 66
2017-04-22 12:00 | 66 | 66
2017-04-22 12:30 | 67 | 67
2017-04-22 13:00 | 67 | 66
2017-04-22 13:30 | 67 | 67
2017-04-22 14:00 | 67 | 67
2017-04-22 14:30 | 68 | 67
2017-04-22 15:00 | 69 | 68
2017-04-22 15:30 | 69 | 68
2017-04-22 16:00 | 70 | 69
2017-04-22 16:30 | 71 | 70
2017-04-22 17:00 | 72 | 71
2017-04-22 17:30 | 72 | 71
2017-04-22 18:00 | 72 | 72
2017-04-22 18:30 | 73 | 72
2017-04-22 19:00 | 73 | 73
2017-04-22 19:30 | 73 | 72
2017-04-22 20:00 | 73 | 72
2017-04-22 20:30 | 71 | 70
2017-04-22 21:00 | 71 | 70
2017-04-22 21:30 | 71 | 71
2017-04-22 22:00 | 71 | 70
2017-04-22 22:30 | 71 | 70
2017-04-22 23:00 | 71 | 70
2017-04-22 23:30 | 69 | 68
2017-04-23 | 69 | 68
2017-04-23 00:30 | 69 | 68
2017-04-23 01:00 | 69 | 68
2017-04-23 01:30 | 68 | 66
2017-04-23 02:00 | 68 | 66
2017-04-23 02:30 | 68 | 66
2017-04-23 03:00 | 68 | 67
2017-04-23 03:30 | 69 | 67
2017-04-23 04:00 | 68 | 67
2017-04-23 04:30 | 68 | 66
2017-04-23 05:00 | 68 | 66
2017-04-23 05:30 | 68 | 67
2017-04-23 06:00 | 67 | 66
2017-04-23 06:30 | 67 | 66
2017-04-23 07:00 | 67 | 65
2017-04-23 07:30 | 68 | 67
2017-04-23 08:00 | 68 | 67
2017-04-23 08:30 | 68 | 67
2017-04-23 09:00 | 68 | 68
2017-04-23 09:30 | 69 | 68
2017-04-23 10:00 | 69 | 69
2017-04-23 10:30 | 69 | 68
2017-04-23 11:00 | 68 | 68
2017-04-23 11:30 | 68 | 67
2017-04-23 12:00 | 69 | 68
2017-04-23 12:30 | 68 | 67
2017-04-23 13:00 | 68 | 68
2017-04-23 13:30 | 69 | 68
2017-04-23 14:00 | 68 | 67
2017-04-23 14:30 | 68 | 67
2017-04-23 15:00 | 69 | 68
2017-04-23 15:30 | 69 | 68
2017-04-23 16:00 | 69 | 69
2017-04-23 16:30 | 70 | 69
2017-04-23 17:00 | 70 | 69
2017-04-23 17:30 | 71 | 70
2017-04-23 18:00 | 71 | 71
2017-04-23 18:30 | 73 | 73
2017-04-23 19:00 | 73 | 73
2017-04-23 19:30 | 72 | 72
2017-04-23 20:00 | 71 | 70
2017-04-23 20:30 | 70 | 70
2017-04-23 21:00 | 69 | 69
2017-04-23 21:30 | 69 | 69
2017-04-23 22:00 | 69 | 68
2017-04-23 22:30 | 68 | 67
2017-04-23 23:00 | 68 | 67
2017-04-23 23:30 | 68 | 67
2017-04-24 | 68 | 66
2017-04-24 00:30 | 68 | 66
2017-04-24 01:00 | 68 | 66
2017-04-24 01:30 | 68 | 66
2017-04-24 02:00 | 67 | 66
2017-04-24 02:30 | 67 | 66
2017-04-24 03:00 | 67 | 66
2017-04-24 03:30 | 68 | 66
2017-04-24 04:00 | 68 | 67
2017-04-24 04:30 | 68 | 67
2017-04-24 05:00 | 68 | 67
2017-04-24 05:30 | 68 | 67
2017-04-24 06:00 | 68 | 67
2017-04-24 06:30 | 68 | 67
2017-04-24 07:00 | 70 | 68
2017-04-24 07:30 | 72 | 70
2017-04-24 08:00 | 71 | 70
2017-04-24 08:30 | 70 | 69
2017-04-24 09:00 | 69 | 69
2017-04-24 09:30 | 69 | 69
2017-04-24 10:00 | 69 | 68
2017-04-24 10:30 | 68 | 68
2017-04-24 11:00 | 68 | 67
2017-04-24 11:30 | 69 | 68
2017-04-24 12:00 | 69 | 68
2017-04-24 12:30 | 68 | 68
2017-04-24 13:00 | 68 | 67
2017-04-24 13:30 | 69 | 68
2017-04-24 14:00 | 69 | 68
2017-04-24 14:30 | 69 | 68
2017-04-24 15:00 | 70 | 69
2017-04-24 15:30 | 70 | 69
2017-04-24 16:00 | 71 | 70
2017-04-24 16:30 | 71 | 70
2017-04-24 17:00 | 72 | 71
2017-04-24 17:30 | 73 | 72
2017-04-24 18:00 | 73 | 72
2017-04-24 18:30 | 75 | 74
2017-04-24 19:00 | 75 | 74
2017-04-24 19:30 | 74 | 73
2017-04-24 20:00 | 74 | 71
2017-04-24 20:30 | 73 | 70
2017-04-24 21:00 | 74 | 70
2017-04-24 21:30 | 73 | 70
2017-04-24 22:00 | 73 | 70
2017-04-24 22:30 | 72 | 70
2017-04-24 23:00 | 72 | 69
2017-04-24 23:30 | 71 | 68
2017-04-25 | 72 | 68
2017-04-25 00:30 | 72 | 68
2017-04-25 01:00 | 71 | 68
2017-04-25 01:30 | 71 | 68
2017-04-25 02:00 | 71 | 68
2017-04-25 02:30 | 71 | 67
2017-04-25 03:00 | 70 | 67
2017-04-25 03:30 | 70 | 67
2017-04-25 04:00 | 71 | 67
2017-04-25 04:30 | 71 | 68
2017-04-25 05:00 | 70 | 67
2017-04-25 05:30 | 70 | 67
2017-04-25 06:00 | 70 | 67
2017-04-25 06:30 | 70 | 67
2017-04-25 07:00 | 71 | 67
2017-04-25 07:30 | 70 | 67
2017-04-25 08:00 | 69 | 67
2017-04-25 08:30 | 69 | 67
2017-04-25 09:00 | 69 | 67
2017-04-25 09:30 | 69 | 67
2017-04-25 10:00 | 68 | 65
2017-04-25 10:30 | 67 | 65
2017-04-25 11:00 | 68 | 65
2017-04-25 11:30 | 69 | 67
2017-04-25 12:00 | 68 | 66
2017-04-25 12:30 | 68 | 66
2017-04-25 13:00 | 68 | 66
2017-04-25 13:30 | 71 | 69
2017-04-25 14:00 | 72 | 70
2017-04-25 14:30 | 70 | 68
2017-04-25 15:00 | 71 | 69
2017-04-25 15:30 | 71 | 69
2017-04-25 16:00 | 70 | 68
2017-04-25 16:30 | 72 | 70
2017-04-25 17:00 | 73 | 71
2017-04-25 17:30 | 74 | 72
2017-04-25 18:00 | 75 | 73
2017-04-25 18:30 | 75 | 74
2017-04-25 19:00 | 74 | 74
2017-04-25 19:30 | 72 | 71
2017-04-25 20:00 | 72 | 71
2017-04-25 20:30 | 71 | 70
2017-04-25 21:00 | 71 | 70
2017-04-25 21:30 | 71 | 70
2017-04-25 22:00 | 72 | 70
2017-04-25 22:30 | 71 | 69
2017-04-25 23:00 | 71 | 68
2017-04-25 23:30 | 72 | 69
2017-04-26 | 72 | 69
2017-04-26 00:30 | 72 | 68
2017-04-26 01:00 | 72 | 68
2017-04-26 01:30 | 71 | 68
2017-04-26 02:00 | 71 | 68
2017-04-26 02:30 | 70 | 67
2017-04-26 03:00 | 69 | 67
2017-04-26 03:30 | 68 | 67
2017-04-26 04:00 | 68 | 67
2017-04-26 04:30 | 68 | 67
2017-04-26 05:00 | 68 | 66
2017-04-26 05:30 | 68 | 67
2017-04-26 06:00 | 68 | 67
2017-04-26 06:30 | 69 | 68
2017-04-26 07:00 | 71 | 70
2017-04-26 07:30 | 64 | 62
2017-04-26 08:00 | 54 | 52
2017-04-26 08:30 | 54 | 52
2017-04-26 09:00 | 54 | 52
2017-04-26 09:30 | 55 | 52
2017-04-26 10:00 | 54 | 53
2017-04-26 10:30 | 55 | 53
2017-04-26 11:00 | 60 | 58
2017-04-26 11:30 | 60 | 57
2017-04-26 12:00 | 60 | 57
2017-04-26 12:30 | 60 | 57
2017-04-26 13:00 | 60 | 56
2017-04-26 13:30 | 60 | 57
2017-04-26 14:00 | 60 | 57
2017-04-26 14:30 | 64 | 61
2017-04-26 15:00 | 65 | 62
2017-04-26 15:30 | 64 | 61
2017-04-26 16:00 | 65 | 62
2017-04-26 16:30 | 67 | 64
2017-04-26 17:00 | 76 | 72
2017-04-26 17:30 | 76 | 72
2017-04-26 18:00 | 75 | 72
2017-04-26 18:30 | 75 | 72
2017-04-26 19:00 | 76 | 73
2017-04-26 19:30 | 75 | 72
2017-04-26 20:00 | 74 | 71
2017-04-26 20:30 | 74 | 70
2017-04-26 21:00 | 73 | 69
2017-04-26 21:30 | 73 | 70
2017-04-26 22:00 | 68 | 64
2017-04-26 22:30 | 68 | 64
2017-04-26 23:00 | 68 | 64
2017-04-26 23:30 | 68 | 63
2017-04-27 | 69 | 64
2017-04-27 00:30 | 69 | 64
2017-04-27 01:00 | 69 | 64
2017-04-27 01:30 | 69 | 64
2017-04-27 02:00 | 68 | 63
2017-04-27 02:30 | 67 | 64
2017-04-27 03:00 | 67 | 63
2017-04-27 03:30 | 67 | 63
2017-04-27 04:00 | 66 | 63
2017-04-27 04:30 | 67 | 64
2017-04-27 05:00 | 66 | 63
2017-04-27 05:30 | 67 | 63
2017-04-27 06:00 | 66 | 63
2017-04-27 06:30 | 67 | 64
2017-04-27 07:00 | 69 | 67
2017-04-27 07:30 | 67 | 65
2017-04-27 08:00 | 65 | 63
2017-04-27 08:30 | 64 | 62
2017-04-27 09:00 | 65 | 63
2017-04-27 09:30 | 64 | 63
2017-04-27 10:00 | 63 | 62
2017-04-27 10:30 | 65 | 63
2017-04-27 11:00 | 64 | 63
2017-04-27 11:30 | 65 | 63
2017-04-27 12:00 | 65 | 63
2017-04-27 12:30 | 65 | 64
2017-04-27 13:00 | 65 | 64
2017-04-27 13:30 | 64 | 63
2017-04-27 14:00 | 64 | 63
2017-04-27 14:30 | 66 | 65
2017-04-27 15:00 | 66 | 64
2017-04-27 15:30 | 66 | 64
2017-04-27 16:00 | 65 | 64
2017-04-27 16:30 | 72 | 71
2017-04-27 17:00 | 75 | 74
2017-04-27 17:30 | 76 | 75
2017-04-27 18:00 | 71 | 69
2017-04-27 18:30 | 60 | 49
2017-04-27 19:00 | 68 | 64
2017-04-27 19:30 | 71 | 69
2017-04-27 20:00 | 71 | 69
2017-04-27 20:30 | 72 | 70
2017-04-27 21:00 | 72 | 70
2017-04-27 21:30 | 66 | 64
2017-04-27 22:00 | 65 | 63
2017-04-27 22:30 | 66 | 63
2017-04-27 23:00 | 65 | 62
2017-04-27 23:30 | 66 | 63
2017-04-28 | 67 | 63
2017-04-28 00:30 | 64 | 60
2017-04-28 01:00 | 56 | 53
2017-04-28 01:30 | 57 | 53
2017-04-28 02:00 | 54 | 54
2017-04-28 02:30 | 54 | 53
2017-04-28 03:00 | 53 | 53
2017-04-28 03:30 | 53 | 53
2017-04-28 04:00 | 53 | 53
2017-04-28 04:30 | 52 | 52
2017-04-28 05:00 | 53 | 53
2017-04-28 05:30 | 52 | 52
2017-04-28 06:00 | 53 | 52
2017-04-28 06:30 | 51 | 51
2017-04-28 07:00 | 43 | 42
2017-04-28 07:30 | 52 | 48
2017-04-28 08:00 | 53 | 50
2017-04-28 08:30 | 52 | 50
2017-04-28 09:00 | 52 | 50
2017-04-28 09:30 | 52 | 50
2017-04-28 10:00 | 52 | 50
2017-04-28 10:30 | 52 | 50
2017-04-28 11:00 | 52 | 50
2017-04-28 11:30 | 52 | 51
2017-04-28 12:00 | 52 | 51
2017-04-28 12:30 | 52 | 51
2017-04-28 13:00 | 53 | 51
2017-04-28 13:30 | 54 | 53
2017-04-28 14:00 | 54 | 53
2017-04-28 14:30 | 55 | 54
2017-04-28 15:00 | 56 | 55
2017-04-28 15:30 | 55 | 54
2017-04-28 16:00 | 56 | 54
2017-04-28 16:30 | 56 | 54
2017-04-28 17:00 | 56 | 54
2017-04-28 17:30 | 56 | 54
2017-04-28 18:00 | 56 | 54
2017-04-28 18:30 | 56 | 54
2017-04-28 19:00 | 56 | 54
2017-04-28 19:30 | 56 | 55
2017-04-28 20:00 | 56 | 55
2017-04-28 20:30 | 55 | 54
2017-04-28 21:00 | 56 | 54
2017-04-28 21:30 | 56 | 54
2017-04-28 22:00 | 55 | 54
2017-04-28 22:30 | 54 | 53
2017-04-28 23:00 | 54 | 53
2017-04-28 23:30 | 52 | 51
2017-04-29 | 54 | 53
2017-04-29 00:30 | 54 | 53
2017-04-29 01:00 | 56 | 54
2017-04-29 01:30 | 56 | 54
2017-04-29 02:00 | 55 | 54
2017-04-29 02:30 | 55 | 54
2017-04-29 03:00 | 56 | 54
2017-04-29 03:30 | 55 | 53
2017-04-29 04:00 | 55 | 53
2017-04-29 04:30 | 55 | 53
2017-04-29 05:00 | 55 | 54
2017-04-29 05:30 | 54 | 53
2017-04-29 06:00 | 55 | 53
2017-04-29 06:30 | 54 | 52
2017-04-29 07:00 | 54 | 52
2017-04-29 07:30 | 54 | 52
2017-04-29 08:00 | 51 | 51
2017-04-29 08:30 | 51 | 51
2017-04-29 09:00 | 51 | 51
2017-04-29 09:30 | 51 | 51
2017-04-29 10:00 | 50 | 50
2017-04-29 10:30 | 51 | 51
2017-04-29 11:00 | 52 | 52
2017-04-29 11:30 | 52 | 52
2017-04-29 12:00 | 52 | 52
2017-04-29 12:30 | 52 | 52
2017-04-29 13:00 | 52 | 52
2017-04-29 13:30 | 52 | 52
2017-04-29 14:00 | 52 | 52
2017-04-29 14:30 | 52 | 51
2017-04-29 15:00 | 51 | 51
2017-04-29 15:30 | 51 | 51
2017-04-29 16:00 | 52 | 52
2017-04-29 16:30 | 52 | 52
2017-04-29 17:00 | 52 | 52
2017-04-29 17:30 | 53 | 52
2017-04-29 18:00 | 55 | 54
2017-04-29 18:30 | 55 | 55
2017-04-29 19:00 | 56 | 54
2017-04-29 19:30 | 57 | 55
2017-04-29 20:00 | 57 | 55
2017-04-29 20:30 | 56 | 54
2017-04-29 21:00 | 57 | 54
2017-04-29 21:30 | 57 | 54
2017-04-29 22:00 | 55 | 53
2017-04-29 22:30 | 54 | 53
2017-04-29 23:00 | 55 | 54
2017-04-29 23:30 | 55 | 54
2017-04-30 | 55 | 54
2017-04-30 00:30 | 55 | 53
2017-04-30 01:00 | 56 | 54
2017-04-30 01:30 | 55 | 54
2017-04-30 02:00 | 55 | 54
2017-04-30 02:30 | 55 | 54
2017-04-30 03:00 | 55 | 54
2017-04-30 03:30 | 56 | 54
2017-04-30 04:00 | 56 | 54
2017-04-30 04:30 | 56 | 54
2017-04-30 05:00 | 55 | 54
2017-04-30 05:30 | 55 | 54
2017-04-30 06:00 | 55 | 53
2017-04-30 06:30 | 55 | 54
2017-04-30 07:00 | 55 | 53
2017-04-30 07:30 | 54 | 53
2017-04-30 08:00 | 54 | 53
2017-04-30 08:30 | 55 | 53
2017-04-30 09:00 | 56 | 54
2017-04-30 09:30 | 56 | 54
2017-04-30 10:00 | 55 | 54
2017-04-30 10:30 | 55 | 54
2017-04-30 11:00 | 55 | 53
2017-04-30 11:30 | 55 | 53
2017-04-30 12:00 | 56 | 54
2017-04-30 12:30 | 56 | 54
2017-04-30 13:00 | 56 | 54
2017-04-30 13:30 | 55 | 52
2017-04-30 14:00 | 55 | 54
2017-04-30 14:30 | 54 | 54
2017-04-30 15:00 | 55 | 54
2017-04-30 15:30 | 55 | 54
2017-04-30 16:00 | 54 | 53
2017-04-30 16:30 | 54 | 53
2017-04-30 17:00 | 54 | 53
2017-04-30 17:30 | 54 | 53
2017-04-30 18:00 | 47 | 45
2017-04-30 18:30 | 43 | 38
2017-04-30 19:00 | 54 | 53
2017-04-30 19:30 | 55 | 55
2017-04-30 20:00 | 56 | 55
2017-04-30 20:30 | 54 | 53
2017-04-30 21:00 | 54 | 53
2017-04-30 21:30 | 53 | 53
2017-04-30 22:00 | 53 | 52
2017-04-30 22:30 | 54 | 53
2017-04-30 23:00 | 54 | 53
2017-04-30 23:30 | 53 | 52
2017-05-01 | 54 | 53
2017-05-01 00:30 | 55 | 54
2017-05-01 01:00 | 55 | 54
2017-05-01 01:30 | 55 | 54
2017-05-01 02:00 | 55 | 54
2017-05-01 02:30 | 55 | 54
2017-05-01 03:00 | 55 | 53
2017-05-01 03:30 | 55 | 54
2017-05-01 04:00 | 54 | 52
2017-05-01 04:30 | 54 | 52
2017-05-01 05:00 | 54 | 52
2017-05-01 05:30 | 55 | 53
2017-05-01 06:00 | 54 | 53
2017-05-01 06:30 | 54 | 52
2017-05-01 07:00 | 52 | 51
2017-05-01 07:30 | 53 | 51
2017-05-01 08:00 | 53 | 52
2017-05-01 08:30 | 53 | 52
2017-05-01 09:00 | 53 | 52
2017-05-01 09:30 | 53 | 52
2017-05-01 10:00 | 52 | 52
2017-05-01 10:30 | 52 | 51
2017-05-01 11:00 | 51 | 51
2017-05-01 11:30 | 52 | 52
2017-05-01 12:00 | 53 | 53
2017-05-01 12:30 | 52 | 52
2017-05-01 13:00 | 52 | 52
2017-05-01 13:30 | 53 | 52
2017-05-01 14:00 | 53 | 52
2017-05-01 14:30 | 54 | 54
2017-05-01 15:00 | 54 | 54
2017-05-01 15:30 | 54 | 53
2017-05-01 16:00 | 54 | 54
2017-05-01 16:30 | 54 | 54
2017-05-01 17:00 | 54 | 54
2017-05-01 17:30 | 54 | 54
2017-05-01 18:00 | 51 | 50
2017-05-01 18:30 | 54 | 54
2017-05-01 19:00 | 54 | 54
2017-05-01 19:30 | 54 | 53
2017-05-01 20:00 | 54 | 54
2017-05-01 20:30 | 53 | 53
2017-05-01 21:00 | 53 | 53
2017-05-01 21:30 | 53 | 52
2017-05-01 22:00 | 53 | 52
2017-05-01 22:30 | 53 | 53
2017-05-01 23:00 | 54 | 53
2017-05-01 23:30 | 53 | 52
2017-05-02 | 54 | 53
2017-05-02 00:30 | 54 | 53
2017-05-02 01:00 | 54 | 53
2017-05-02 01:30 | 53 | 52
2017-05-02 02:00 | 54 | 53
2017-05-02 02:30 | 54 | 53
2017-05-02 03:00 | 54 | 53
2017-05-02 03:30 | 53 | 52
2017-05-02 04:00 | 54 | 52
2017-05-02 04:30 | 53 | 51
2017-05-02 05:00 | 53 | 52
2017-05-02 05:30 | 53 | 52
2017-05-02 06:00 | 54 | 52
2017-05-02 06:30 | 53 | 52
2017-05-02 07:00 | 44 | 36
2017-05-02 07:30 | 48 | 44
2017-05-02 08:00 | 53 | 49
2017-05-02 08:30 | 54 | 50
2017-05-02 09:00 | 54 | 50
2017-05-02 09:30 | 53 | 50
2017-05-02 10:00 | 54 | 51
2017-05-02 10:30 | 54 | 50
2017-05-02 11:00 | 55 | 51
2017-05-02 11:30 | 54 | 51
2017-05-02 12:00 | 49 | 46
2017-05-02 12:30 | 49 | 47
2017-05-02 13:00 | 49 | 46
2017-05-02 13:30 | 49 | 46
2017-05-02 14:00 | 49 | 47
2017-05-02 14:30 | 50 | 47
2017-05-02 15:00 | 51 | 48
2017-05-02 15:30 | 51 | 48
2017-05-02 16:00 | 51 | 48
2017-05-02 16:30 | 51 | 48
2017-05-02 17:00 | 51 | 49
2017-05-02 17:30 | 51 | 48
2017-05-02 18:00 | 43 | 32
2017-05-02 18:30 | 43 | 28
2017-05-02 19:00 | 45 | 38
2017-05-02 19:30 | 50 | 47
2017-05-02 20:00 | 51 | 48
2017-05-02 20:30 | 50 | 46
2017-05-02 21:00 | 50 | 46
2017-05-02 21:30 | 48 | 45
2017-05-02 22:00 | 48 | 45
2017-05-02 22:30 | 49 | 47
2017-05-02 23:00 | 50 | 48
2017-05-02 23:30 | 50 | 49
2017-05-03 | 50 | 49
2017-05-03 00:30 | 50 | 49
2017-05-03 01:00 | 51 | 50
2017-05-03 01:30 | 50 | 50
2017-05-03 02:00 | 50 | 49
2017-05-03 02:30 | 51 | 50
2017-05-03 03:00 | 51 | 50
2017-05-03 03:30 | 51 | 50
2017-05-03 04:00 | 51 | 50
2017-05-03 04:30 | 51 | 50
2017-05-03 05:00 | 50 | 49
2017-05-03 05:30 | 50 | 50
2017-05-03 06:00 | 50 | 50
2017-05-03 06:30 | 49 | 49
2017-05-03 07:00 | 35 | 29
2017-05-03 07:30 | 36 | 33
2017-05-03 08:00 | 46 | 46
2017-05-03 08:30 | 47 | 47
2017-05-03 09:00 | 47 | 47
2017-05-03 09:30 | 47 | 47
2017-05-03 10:00 | 48 | 48
2017-05-03 10:30 | 49 | 49
2017-05-03 11:00 | 55 | 55
2017-05-03 11:30 | 55 | 55
2017-05-03 12:00 | 56 | 56
2017-05-03 12:30 | 55 | 55
2017-05-03 13:00 | 54 | 54
2017-05-03 13:30 | 52 | 52
2017-05-03 14:00 | 54 | 54
2017-05-03 14:30 | 60 | 60
2017-05-03 15:00 | 60 | 60
2017-05-03 15:30 | 60 | 60
2017-05-03 16:00 | 60 | 60
2017-05-03 16:30 | 59 | 59
2017-05-03 17:00 | 60 | 60
2017-05-03 17:30 | 59 | 59
2017-05-03 18:00 | 51 | 46
2017-05-03 18:30 | 46 | 40
2017-05-03 19:00 | 55 | 55
2017-05-03 19:30 | 58 | 58
2017-05-03 20:00 | 59 | 58
2017-05-03 20:30 | 58 | 58
2017-05-03 21:00 | 58 | 58
2017-05-03 21:30 | 58 | 58
2017-05-03 22:00 | 60 | 59
2017-05-03 22:30 | 60 | 59
2017-05-03 23:00 | 59 | 58
2017-05-03 23:30 | 60 | 59
2017-05-04 | 61 | 60
2017-05-04 00:30 | 61 | 60
2017-05-04 01:00 | 62 | 61
2017-05-04 01:30 | 63 | 62
2017-05-04 02:00 | 63 | 62
2017-05-04 02:30 | 64 | 63
2017-05-04 03:00 | 63 | 62
2017-05-04 03:30 | 63 | 62
2017-05-04 04:00 | 63 | 62
2017-05-04 04:30 | 63 | 62
2017-05-04 05:00 | 62 | 61
2017-05-04 05:30 | 63 | 62
2017-05-04 06:00 | 62 | 61
2017-05-04 06:30 | 60 | 60
2017-05-04 07:00 | 63 | 62
2017-05-04 07:30 | 60 | 60
2017-05-04 08:00 | 58 | 58
2017-05-04 08:30 | 58 | 58
2017-05-04 09:00 | 58 | 58
2017-05-04 09:30 | 58 | 58
2017-05-04 10:00 | 59 | 59
2017-05-04 10:30 | 60 | 60
2017-05-04 11:00 | 62 | 62
2017-05-04 11:30 | 61 | 61
2017-05-04 12:00 | 59 | 59
2017-05-04 12:30 | 59 | 59
2017-05-04 13:00 | 60 | 60
2017-05-04 13:30 | 60 | 60
2017-05-04 14:00 | 59 | 59
2017-05-04 14:30 | 60 | 60
2017-05-04 15:00 | 60 | 60
2017-05-04 15:30 | 59 | 59
2017-05-04 16:00 | 60 | 60
2017-05-04 16:30 | 59 | 59
2017-05-04 17:00 | 60 | 60
2017-05-04 17:30 | 58 | 58
2017-05-04 18:00 | 54 | 51
2017-05-04 18:30 | 51 | 45
2017-05-04 19:00 | 57 | 55
2017-05-04 19:30 | 56 | 56
2017-05-04 20:00 | 57 | 57
2017-05-04 20:30 | 58 | 58
2017-05-04 21:00 | 58 | 58
2017-05-04 21:30 | 59 | 58
2017-05-04 22:00 | 59 | 58
2017-05-04 22:30 | 60 | 59
2017-05-04 23:00 | 60 | 60
2017-05-04 23:30 | 61 | 60
2017-05-05 | 62 | 61
2017-05-05 00:30 | 59 | 58
2017-05-05 01:00 | 51 | 50
2017-05-05 01:30 | 51 | 50
2017-05-05 02:00 | 51 | 50
2017-05-05 02:30 | 51 | 50
2017-05-05 03:00 | 51 | 50
2017-05-05 03:30 | 50 | 49
2017-05-05 04:00 | 51 | 50
2017-05-05 04:30 | 51 | 50
2017-05-05 05:00 | 52 | 51
2017-05-05 05:30 | 51 | 50
2017-05-05 06:00 | 51 | 50
2017-05-05 06:30 | 49 | 49
2017-05-05 07:00 | 48 | 47
2017-05-05 07:30 | 49 | 48
2017-05-05 08:00 | 49 | 48
2017-05-05 08:30 | 49 | 47
2017-05-05 09:00 | 48 | 46
2017-05-05 09:30 | 55 | 52
2017-05-05 10:00 | 58 | 55
2017-05-05 10:30 | 58 | 55
2017-05-05 11:00 | 58 | 55
2017-05-05 11:30 | 58 | 56
2017-05-05 12:00 | 59 | 56
2017-05-05 12:30 | 59 | 56
2017-05-05 13:00 | 60 | 57
2017-05-05 13:30 | 60 | 57
2017-05-05 14:00 | 60 | 57
2017-05-05 14:30 | 60 | 57
2017-05-05 15:00 | 60 | 57
2017-05-05 15:30 | 61 | 57
2017-05-05 16:00 | 60 | 57
2017-05-05 16:30 | 60 | 57
2017-05-05 17:00 | 60 | 57
2017-05-05 17:30 | 61 | 57
2017-05-05 18:00 | 61 | 58
2017-05-05 18:30 | 60 | 57
2017-05-05 19:00 | 61 | 58
2017-05-05 19:30 | 61 | 58
2017-05-05 20:00 | 62 | 59
2017-05-05 20:30 | 62 | 59
2017-05-05 21:00 | 62 | 58
2017-05-05 21:30 | 62 | 59
2017-05-05 22:00 | 61 | 59
2017-05-05 22:30 | 60 | 58
2017-05-05 23:00 | 59 | 57
2017-05-05 23:30 | 60 | 58
2017-05-06 | 59 | 58
2017-05-06 00:30 | 60 | 59
2017-05-06 01:00 | 60 | 59
2017-05-06 01:30 | 60 | 59
2017-05-06 02:00 | 59 | 58
2017-05-06 02:30 | 59 | 58
2017-05-06 03:00 | 59 | 58
2017-05-06 03:30 | 58 | 57
2017-05-06 04:00 | 59 | 58
2017-05-06 04:30 | 58 | 57
2017-05-06 05:00 | 57 | 56
2017-05-06 05:30 | 58 | 57
2017-05-06 06:00 | 58 | 57
2017-05-06 06:30 | 58 | 57
2017-05-06 07:00 | 58 | 57
2017-05-06 07:30 | 57 | 56
2017-05-06 08:00 | 58 | 57
2017-05-06 08:30 | 57 | 56
2017-05-06 09:00 | 57 | 55
2017-05-06 09:30 | 57 | 54
2017-05-06 10:00 | 57 | 55
2017-05-06 10:30 | 57 | 54
2017-05-06 11:00 | 56 | 54
2017-05-06 11:30 | 57 | 55
2017-05-06 12:00 | 57 | 55
2017-05-06 12:30 | 58 | 55
2017-05-06 13:00 | 57 | 54
2017-05-06 13:30 | 57 | 54
2017-05-06 14:00 | 57 | 55
2017-05-06 14:30 | 58 | 56
2017-05-06 15:00 | 59 | 57
2017-05-06 15:30 | 60 | 58
2017-05-06 16:00 | 59 | 57
2017-05-06 16:30 | 59 | 57
2017-05-06 17:00 | 60 | 58
2017-05-06 17:30 | 59 | 57
2017-05-06 18:00 | 60 | 57
2017-05-06 18:30 | 60 | 58
2017-05-06 19:00 | 60 | 58
2017-05-06 19:30 | 60 | 58
2017-05-06 20:00 | 61 | 59
2017-05-06 20:30 | 59 | 57
2017-05-06 21:00 | 59 | 56
2017-05-06 21:30 | 58 | 56
2017-05-06 22:00 | 58 | 56
2017-05-06 22:30 | 59 | 56
2017-05-06 23:00 | 56 | 56
2017-05-06 23:30 | 55 | 55
2017-05-07 | 55 | 55
2017-05-07 00:30 | 55 | 55
2017-05-07 01:00 | 56 | 56
2017-05-07 01:30 | 56 | 56
2017-05-07 02:00 | 56 | 56
2017-05-07 02:30 | 56 | 56
2017-05-07 03:00 | 55 | 55
2017-05-07 03:30 | 55 | 55
2017-05-07 04:00 | 56 | 56
2017-05-07 04:30 | 56 | 56
2017-05-07 05:00 | 55 | 55
2017-05-07 05:30 | 55 | 55
2017-05-07 06:00 | 54 | 54
2017-05-07 06:30 | 54 | 54
2017-05-07 07:00 | 55 | 55
2017-05-07 07:30 | 55 | 55
2017-05-07 08:00 | 55 | 55
2017-05-07 08:30 | 54 | 54
2017-05-07 09:00 | 54 | 54
2017-05-07 09:30 | 56 | 53
2017-05-07 10:00 | 56 | 53
2017-05-07 10:30 | 55 | 52
2017-05-07 11:00 | 55 | 52
2017-05-07 11:30 | 55 | 53
2017-05-07 12:00 | 57 | 54
2017-05-07 12:30 | 55 | 52
2017-05-07 13:00 | 56 | 54
2017-05-07 13:30 | 57 | 55
2017-05-07 14:00 | 58 | 56
2017-05-07 14:30 | 59 | 57
2017-05-07 15:00 | 59 | 57
2017-05-07 15:30 | 59 | 57
2017-05-07 16:00 | 58 | 56
2017-05-07 16:30 | 59 | 57
2017-05-07 17:00 | 59 | 57
2017-05-07 17:30 | 59 | 57
2017-05-07 18:00 | 60 | 58
2017-05-07 18:30 | 58 | 56
2017-05-07 19:00 | 59 | 57
2017-05-07 19:30 | 60 | 58
2017-05-07 20:00 | 59 | 58
2017-05-07 20:30 | 58 | 56
2017-05-07 21:00 | 58 | 56
2017-05-07 21:30 | 58 | 56
2017-05-07 22:00 | 58 | 55
2017-05-07 22:30 | 58 | 56
2017-05-07 23:00 | 58 | 55
2017-05-07 23:30 | 57 | 55
2017-05-08 | 58 | 55
2017-05-08 00:30 | 57 | 55
2017-05-08 01:00 | 56 | 55
2017-05-08 01:30 | 57 | 55
2017-05-08 02:00 | 57 | 55
2017-05-08 02:30 | 57 | 55
2017-05-08 03:00 | 57 | 55
2017-05-08 03:30 | 57 | 55
2017-05-08 04:00 | 57 | 55
2017-05-08 04:30 | 56 | 54
2017-05-08 05:00 | 57 | 55
2017-05-08 05:30 | 57 | 55
2017-05-08 06:00 | 56 | 54
2017-05-08 06:30 | 57 | 55
2017-05-08 07:00 | 53 | 49
2017-05-08 07:30 | 53 | 50
2017-05-08 08:00 | 56 | 54
2017-05-08 08:30 | 55 | 53
2017-05-08 09:00 | 54 | 53
2017-05-08 09:30 | 55 | 53
2017-05-08 10:00 | 55 | 53
2017-05-08 10:30 | 55 | 53
2017-05-08 11:00 | 55 | 52
2017-05-08 11:30 | 56 | 54
2017-05-08 12:00 | 56 | 54
2017-05-08 12:30 | 56 | 54
2017-05-08 13:00 | 57 | 55
2017-05-08 13:30 | 57 | 55
2017-05-08 14:00 | 57 | 55
2017-05-08 14:30 | 58 | 56
2017-05-08 15:00 | 58 | 57
2017-05-08 15:30 | 58 | 56
2017-05-08 16:00 | 58 | 57
2017-05-08 16:30 | 58 | 57
2017-05-08 17:00 | 57 | 56
2017-05-08 17:30 | 47 | 39
2017-05-08 18:00 | 46 | 32
2017-05-08 18:30 | 41 | 27
2017-05-08 19:00 | 42 | 33
2017-05-08 19:30 | 52 | 49
2017-05-08 20:00 | 53 | 51
2017-05-08 20:30 | 52 | 50
2017-05-08 21:00 | 56 | 55
2017-05-08 21:30 | 58 | 57
2017-05-08 22:00 | 57 | 56
2017-05-08 22:30 | 47 | 39
2017-05-08 23:00 | 51 | 45
2017-05-08 23:30 | 53 | 50
2017-05-09 | 53 | 50
2017-05-09 00:30 | 58 | 56
2017-05-09 01:00 | 58 | 56
2017-05-09 01:30 | 58 | 56
2017-05-09 02:00 | 58 | 56
2017-05-09 02:30 | 57 | 56
2017-05-09 03:00 | 56 | 55
2017-05-09 03:30 | 56 | 55
2017-05-09 04:00 | 56 | 55
2017-05-09 04:30 | 56 | 55
2017-05-09 05:00 | 57 | 55
2017-05-09 05:30 | 54 | 52
2017-05-09 06:00 | 51 | 48
2017-05-09 06:30 | 50 | 47
2017-05-09 07:00 | 43 | 37
2017-05-09 07:30 | 41 | 34
2017-05-09 08:00 | 40 | 33
2017-05-09 08:30 | 40 | 33
2017-05-09 09:00 | 50 | 48
2017-05-09 09:30 | 55 | 54
2017-05-09 10:00 | 55 | 54
2017-05-09 10:30 | 55 | 54
2017-05-09 11:00 | 54 | 53
2017-05-09 11:30 | 54 | 53
2017-05-09 12:00 | 55 | 54
2017-05-09 12:30 | 55 | 53
2017-05-09 13:00 | 62 | 61
2017-05-09 13:30 | 72 | 71
2017-05-09 14:00 | 73 | 72
2017-05-09 14:30 | 75 | 74
2017-05-09 15:00 | 75 | 74
2017-05-09 15:30 | 75 | 74
2017-05-09 16:00 | 75 | 74
2017-05-09 16:30 | 75 | 74
2017-05-09 17:00 | 75 | 74
2017-05-09 17:30 | 76 | 75
2017-05-09 18:00 | 63 | 56
2017-05-09 18:30 | 67 | 62
2017-05-09 19:00 | 72 | 70
2017-05-09 19:30 | 76 | 75
2017-05-09 20:00 | 69 | 65
2017-05-09 20:30 | 71 | 67
2017-05-09 21:00 | 75 | 74
2017-05-09 21:30 | 74 | 73
2017-05-09 22:00 | 75 | 73
2017-05-09 22:30 | 62 | 54
2017-05-09 23:00 | 56 | 49
2017-05-09 23:30 | 69 | 68
2017-05-10 | 70 | 68
2017-05-10 00:30 | 70 | 68
2017-05-10 01:00 | 69 | 68
2017-05-10 01:30 | 69 | 68
2017-05-10 02:00 | 69 | 68
2017-05-10 02:30 | 69 | 67
2017-05-10 03:00 | 69 | 68
2017-05-10 03:30 | 70 | 68
2017-05-10 04:00 | 68 | 67
2017-05-10 04:30 | 69 | 67
2017-05-10 05:00 | 69 | 68
2017-05-10 05:30 | 70 | 69
2017-05-10 06:00 | 67 | 66
2017-05-10 06:30 | 55 | 47
2017-05-10 07:00 | 52 | 42
2017-05-10 07:30 | 55 | 47
2017-05-10 08:00 | 51 | 41
2017-05-10 08:30 | 55 | 49
2017-05-10 09:00 | 65 | 63
2017-05-10 09:30 | 71 | 69
2017-05-10 10:00 | 67 | 63
2017-05-10 10:30 | 64 | 60
2017-05-10 11:00 | 68 | 65
2017-05-10 11:30 | 74 | 73
2017-05-10 12:00 | 75 | 74
2017-05-10 12:30 | 75 | 74
2017-05-10 13:00 | 75 | 74
2017-05-10 13:30 | 76 | 75
2017-05-10 14:00 | 75 | 73
2017-05-10 14:30 | 77 | 76
2017-05-10 15:00 | 77 | 75
2017-05-10 15:30 | 77 | 76
2017-05-10 16:00 | 77 | 76
2017-05-10 16:30 | 78 | 76
2017-05-10 17:00 | 81 | 80
2017-05-10 17:30 | 76 | 71
2017-05-10 18:00 | 66 | 57
2017-05-10 18:30 | 60 | 58
2017-05-10 19:00 | 60 | 58
2017-05-10 19:30 | 76 | 76
2017-05-10 20:00 | 81 | 81
2017-05-10 20:30 | 81 | 81
2017-05-10 21:00 | 79 | 78
2017-05-10 21:30 | 77 | 77
2017-05-10 22:00 | 76 | 76
2017-05-10 22:30 | 58 | 57
2017-05-10 23:00 | 69 | 69
2017-05-10 23:30 | 73 | 73
2017-05-11 | 73 | 73
2017-05-11 00:30 | 72 | 72
2017-05-11 01:00 | 72 | 72
2017-05-11 01:30 | 74 | 74
2017-05-11 02:00 | 73 | 73
2017-05-11 02:30 | 72 | 72
2017-05-11 03:00 | 71 | 71
2017-05-11 03:30 | 71 | 71
2017-05-11 04:00 | 71 | 71
2017-05-11 04:30 | 72 | 72
2017-05-11 05:00 | 72 | 72
2017-05-11 05:30 | 71 | 71
2017-05-11 06:00 | 71 | 71
2017-05-11 06:30 | 73 | 73
2017-05-11 07:00 | 72 | 72
2017-05-11 07:30 | 74 | 74
2017-05-11 08:00 | 74 | 74
2017-05-11 08:30 | 73 | 73
2017-05-11 09:00 | 73 | 72
2017-05-11 09:30 | 72 | 72
2017-05-11 10:00 | 71 | 71
2017-05-11 10:30 | 72 | 72
2017-05-11 11:00 | 72 | 71
2017-05-11 11:30 | 72 | 72
2017-05-11 12:00 | 72 | 72
2017-05-11 12:30 | 72 | 72
2017-05-11 13:00 | 72 | 71
2017-05-11 13:30 | 72 | 72
2017-05-11 14:00 | 74 | 74
2017-05-11 14:30 | 75 | 75
2017-05-11 15:00 | 75 | 75
2017-05-11 15:30 | 77 | 76
2017-05-11 16:00 | 77 | 77
2017-05-11 16:30 | 77 | 77
2017-05-11 17:00 | 78 | 78
2017-05-11 17:30 | 82 | 81
2017-05-11 18:00 | 62 | 61
2017-05-11 18:30 | 60 | 59
2017-05-11 19:00 | 60 | 59
2017-05-11 19:30 | 60 | 59
2017-05-11 20:00 | 49 | 46
2017-05-11 20:30 | 52 | 50
2017-05-11 21:00 | 59 | 58
2017-05-11 21:30 | 62 | 61
2017-05-11 22:00 | 59 | 58
2017-05-11 22:30 | 59 | 58
2017-05-11 23:00 | 61 | 60
2017-05-11 23:30 | 66 | 66
2017-05-12 | 71 | 71
2017-05-12 00:30 | 73 | 72
2017-05-12 01:00 | 69 | 68
2017-05-12 01:30 | 68 | 68
2017-05-12 02:00 | 69 | 68
2017-05-12 02:30 | 69 | 68
2017-05-12 03:00 | 70 | 69
2017-05-12 03:30 | 66 | 66
2017-05-12 04:00 | 52 | 52
2017-05-12 04:30 | 46 | 45
2017-05-12 05:00 | 46 | 45
2017-05-12 05:30 | 46 | 45
2017-05-12 06:00 | 46 | 46
2017-05-12 06:30 | 47 | 47
2017-05-12 07:00 | 61 | 61
2017-05-12 07:30 | 59 | 59
2017-05-12 08:00 | 48 | 48
2017-05-12 08:30 | 62 | 61
2017-05-12 09:00 | 71 | 69
2017-05-12 09:30 | 67 | 65
2017-05-12 10:00 | 56 | 56
2017-05-12 10:30 | 52 | 51
2017-05-12 11:00 | 64 | 63
2017-05-12 11:30 | 71 | 69
2017-05-12 12:00 | 72 | 70
2017-05-12 12:30 | 70 | 70
2017-05-12 13:00 | 70 | 70
2017-05-12 13:30 | 62 | 61
2017-05-12 14:00 | 67 | 66
2017-05-12 14:30 | 54 | 49
2017-05-12 15:00 | 51 | 45
2017-05-12 15:30 | 52 | 45
2017-05-12 16:00 | 52 | 45
2017-05-12 16:30 | 53 | 46
2017-05-12 17:00 | 57 | 50
2017-05-12 17:30 | 58 | 50
2017-05-12 18:00 | 58 | 50
2017-05-12 18:30 | 57 | 50
2017-05-12 19:00 | 57 | 50
2017-05-12 19:30 | 63 | 59
2017-05-12 20:00 | 72 | 71
2017-05-12 20:30 | 71 | 70
2017-05-12 21:00 | 70 | 69
2017-05-12 21:30 | 70 | 69
2017-05-12 22:00 | 70 | 69
2017-05-12 22:30 | 57 | 52
2017-05-12 23:00 | 66 | 63
2017-05-12 23:30 | 69 | 68
2017-05-13 | 69 | 68
2017-05-13 00:30 | 70 | 68
2017-05-13 01:00 | 69 | 68
2017-05-13 01:30 | 69 | 67
2017-05-13 02:00 | 68 | 67
2017-05-13 02:30 | 68 | 67
2017-05-13 03:00 | 68 | 66
2017-05-13 03:30 | 68 | 66
2017-05-13 04:00 | 69 | 67
2017-05-13 04:30 | 70 | 68
2017-05-13 05:00 | 69 | 68
2017-05-13 05:30 | 69 | 68
2017-05-13 06:00 | 69 | 67
2017-05-13 06:30 | 68 | 67
2017-05-13 07:00 | 69 | 67
2017-05-13 07:30 | 66 | 63
2017-05-13 08:00 | 56 | 47
2017-05-13 08:30 | 55 | 47
2017-05-13 09:00 | 54 | 47
2017-05-13 09:30 | 53 | 46
2017-05-13 10:00 | 53 | 46
2017-05-13 10:30 | 54 | 46
2017-05-13 11:00 | 54 | 47
2017-05-13 11:30 | 53 | 47
2017-05-13 12:00 | 63 | 61
2017-05-13 12:30 | 68 | 67
2017-05-13 13:00 | 67 | 66
2017-05-13 13:30 | 67 | 67
2017-05-13 14:00 | 68 | 67
2017-05-13 14:30 | 68 | 68
2017-05-13 15:00 | 70 | 69
2017-05-13 15:30 | 70 | 70
2017-05-13 16:00 | 68 | 67
2017-05-13 16:30 | 71 | 71
2017-05-13 17:00 | 59 | 55
2017-05-13 17:30 | 57 | 49
2017-05-13 18:00 | 57 | 50
2017-05-13 18:30 | 57 | 50
2017-05-13 19:00 | 57 | 51
2017-05-13 19:30 | 68 | 66
2017-05-13 20:00 | 73 | 73
2017-05-13 20:30 | 72 | 72
2017-05-13 21:00 | 72 | 71
2017-05-13 21:30 | 72 | 71
2017-05-13 22:00 | 72 | 71
2017-05-13 22:30 | 72 | 71
2017-05-13 23:00 | 71 | 70
2017-05-13 23:30 | 71 | 70
2017-05-14 | 70 | 69
2017-05-14 00:30 | 71 | 69
2017-05-14 01:00 | 70 | 68
2017-05-14 01:30 | 70 | 68
2017-05-14 02:00 | 70 | 67
2017-05-14 02:30 | 67 | 67
2017-05-14 03:00 | 68 | 67
2017-05-14 03:30 | 69 | 68
2017-05-14 04:00 | 69 | 69
2017-05-14 04:30 | 69 | 68
2017-05-14 05:00 | 69 | 68
2017-05-14 05:30 | 68 | 68
2017-05-14 06:00 | 68 | 68
2017-05-14 06:30 | 68 | 67
2017-05-14 07:00 | 68 | 67
2017-05-14 07:30 | 68 | 68
2017-05-14 08:00 | 67 | 67
2017-05-14 08:30 | 63 | 63
2017-05-14 09:00 | 61 | 61
2017-05-14 09:30 | 69 | 68
2017-05-14 10:00 | 66 | 66
2017-05-14 10:30 | 71 | 69
2017-05-14 11:00 | 71 | 69
2017-05-14 11:30 | 71 | 69
2017-05-14 12:00 | 70 | 68
2017-05-14 12:30 | 70 | 68
2017-05-14 13:00 | 60 | 60
2017-05-14 13:30 | 69 | 67
2017-05-14 14:00 | 70 | 68
2017-05-14 14:30 | 71 | 69
2017-05-14 15:00 | 71 | 69
2017-05-14 15:30 | 72 | 70
2017-05-14 16:00 | 73 | 71
2017-05-14 16:30 | 73 | 71
2017-05-14 17:00 | 74 | 72
2017-05-14 17:30 | 72 | 70
2017-05-14 18:00 | 54 | 54
2017-05-14 18:30 | 70 | 69
2017-05-14 19:00 | 76 | 74
2017-05-14 19:30 | 76 | 74
2017-05-14 20:00 | 76 | 74
2017-05-14 20:30 | 72 | 71
2017-05-14 21:00 | 72 | 70
2017-05-14 21:30 | 71 | 70
2017-05-14 22:00 | 70 | 69
2017-05-14 22:30 | 70 | 69
2017-05-14 23:00 | 70 | 69
2017-05-14 23:30 | 68 | 68
2017-05-15 | 68 | 68
2017-05-15 00:30 | 68 | 68
2017-05-15 01:00 | 68 | 67
2017-05-15 01:30 | 67 | 67
2017-05-15 02:00 | 67 | 67
2017-05-15 02:30 | 67 | 67
2017-05-15 03:00 | 68 | 67
2017-05-15 03:30 | 68 | 67
2017-05-15 04:00 | 67 | 67
2017-05-15 04:30 | 67 | 67
2017-05-15 05:00 | 67 | 67
2017-05-15 05:30 | 67 | 67
2017-05-15 06:00 | 67 | 67
2017-05-15 06:30 | 68 | 68
2017-05-15 07:00 | 51 | 51
2017-05-15 07:30 | 60 | 60
2017-05-15 08:00 | 56 | 47
2017-05-15 08:30 | 64 | 62
2017-05-15 09:00 | 68 | 68
2017-05-15 09:30 | 65 | 64
2017-05-15 10:00 | 66 | 65
2017-05-15 10:30 | 67 | 66
2017-05-15 11:00 | 59 | 57
2017-05-15 11:30 | 61 | 59
2017-05-15 12:00 | 59 | 58
2017-05-15 12:30 | 66 | 66
2017-05-15 13:00 | 66 | 66
2017-05-15 13:30 | 56 | 54
2017-05-15 14:00 | 60 | 59
2017-05-15 14:30 | 54 | 51
2017-05-15 15:00 | 64 | 62
2017-05-15 15:30 | 59 | 52
2017-05-15 16:00 | 65 | 62
2017-05-15 16:30 | 59 | 53
2017-05-15 17:00 | 57 | 48
2017-05-15 17:30 | 56 | 47
2017-05-15 18:00 | 54 | 46
2017-05-15 18:30 | 54 | 48
2017-05-15 19:00 | 53 | 47
2017-05-15 19:30 | 63 | 63
2017-05-15 20:00 | 67 | 67
2017-05-15 20:30 | 67 | 66
2017-05-15 21:00 | 66 | 65
2017-05-15 21:30 | 66 | 65
2017-05-15 22:00 | 66 | 65
2017-05-15 22:30 | 46 | 45
2017-05-15 23:00 | 59 | 59
2017-05-15 23:30 | 64 | 63
2017-05-16 | 64 | 63
2017-05-16 00:30 | 64 | 63
2017-05-16 01:00 | 64 | 63
2017-05-16 01:30 | 64 | 63
2017-05-16 02:00 | 64 | 63
2017-05-16 02:30 | 64 | 63
2017-05-16 03:00 | 64 | 63
2017-05-16 03:30 | 64 | 63
2017-05-16 04:00 | 65 | 64
2017-05-16 04:30 | 64 | 63
2017-05-16 05:00 | 64 | 63
2017-05-16 05:30 | 64 | 63
2017-05-16 06:00 | 65 | 64
2017-05-16 06:30 | 51 | 51
2017-05-16 07:00 | 33 | 32
2017-05-16 07:30 | 40 | 39
2017-05-16 08:00 | 41 | 41
2017-05-16 08:30 | 57 | 57
2017-05-16 09:00 | 63 | 63
2017-05-16 09:30 | 52 | 50
2017-05-16 10:00 | 58 | 58
2017-05-16 10:30 | 59 | 59
2017-05-16 11:00 | 58 | 58
2017-05-16 11:30 | 59 | 59
2017-05-16 12:00 | 59 | 59
2017-05-16 12:30 | 59 | 59
2017-05-16 13:00 | 59 | 59
2017-05-16 13:30 | 60 | 60
2017-05-16 14:00 | 60 | 60
2017-05-16 14:30 | 64 | 64
2017-05-16 15:00 | 66 | 66
2017-05-16 15:30 | 67 | 67
2017-05-16 16:00 | 59 | 58
2017-05-16 16:30 | 63 | 63
2017-05-16 17:00 | 66 | 66
2017-05-16 17:30 | 60 | 59
2017-05-16 18:00 | 47 | 36
2017-05-16 18:30 | 50 | 43
2017-05-16 19:00 | 51 | 47
2017-05-16 19:30 | 61 | 60
2017-05-16 20:00 | 66 | 66
2017-05-16 20:30 | 55 | 51
2017-05-16 21:00 | 53 | 46
2017-05-16 21:30 | 53 | 45
2017-05-16 22:00 | 61 | 57
2017-05-16 22:30 | 55 | 48
2017-05-16 23:00 | 53 | 43
2017-05-16 23:30 | 44 | 42
2017-05-17 | 55 | 55
2017-05-17 00:30 | 60 | 59
2017-05-17 01:00 | 61 | 61
2017-05-17 01:30 | 62 | 61
2017-05-17 02:00 | 62 | 62
2017-05-17 02:30 | 62 | 61
2017-05-17 03:00 | 62 | 62
2017-05-17 03:30 | 63 | 62
2017-05-17 04:00 | 63 | 62
2017-05-17 04:30 | 63 | 63
2017-05-17 05:00 | 64 | 63
2017-05-17 05:30 | 47 | 47
2017-05-17 06:00 | 42 | 42
2017-05-17 06:30 | 42 | 42
2017-05-17 07:00 | 41 | 41
2017-05-17 07:30 | 38 | 38
2017-05-17 08:00 | 32 | 31
2017-05-17 08:30 | 43 | 43
2017-05-17 09:00 | 48 | 48
2017-05-17 09:30 | 56 | 56
2017-05-17 10:00 | 58 | 56
2017-05-17 10:30 | 61 | 60
2017-05-17 11:00 | 50 | 47
2017-05-17 11:30 | 54 | 54
2017-05-17 12:00 | 49 | 49
2017-05-17 12:30 | 64 | 64
2017-05-17 13:00 | 66 | 65
2017-05-17 13:30 | 66 | 65
2017-05-17 14:00 | 58 | 56
2017-05-17 14:30 | 52 | 44
2017-05-17 15:00 | 52 | 44
2017-05-17 15:30 | 53 | 44
2017-05-17 16:00 | 53 | 44
2017-05-17 16:30 | 53 | 44
2017-05-17 17:00 | 53 | 44
2017-05-17 17:30 | 54 | 44
2017-05-17 18:00 | 54 | 43
2017-05-17 18:30 | 54 | 45
2017-05-17 19:00 | 54 | 45
2017-05-17 19:30 | 54 | 45
2017-05-17 20:00 | 54 | 45
2017-05-17 20:30 | 55 | 44
2017-05-17 21:00 | 53 | 44
2017-05-17 21:30 | 52 | 43
2017-05-17 22:00 | 43 | 42
2017-05-17 22:30 | 42 | 42
2017-05-17 23:00 | 41 | 41
2017-05-17 23:30 | 42 | 42
2017-05-18 | 42 | 41
2017-05-18 00:30 | 42 | 41
2017-05-18 01:00 | 41 | 40
2017-05-18 01:30 | 41 | 40
2017-05-18 02:00 | 41 | 40
2017-05-18 02:30 | 54 | 54
2017-05-18 03:00 | 59 | 58
2017-05-18 03:30 | 59 | 58
2017-05-18 04:00 | 57 | 57
2017-05-18 04:30 | 58 | 58
2017-05-18 05:00 | 59 | 58
2017-05-18 05:30 | 58 | 57
2017-05-18 06:00 | 40 | 40
2017-05-18 06:30 | 32 | 32
2017-05-18 07:00 | 30 | 28
2017-05-18 07:30 | 29 | 28
2017-05-18 08:00 | 31 | 28
2017-05-18 08:30 | 43 | 24
2017-05-18 09:00 | 41 | 24
2017-05-18 09:30 | 42 | 27
2017-05-18 10:00 | 44 | 27
2017-05-18 10:30 | 47 | 26
2017-05-18 11:00 | 47 | 26
2017-05-18 11:30 | 47 | 26
2017-05-18 12:00 | 47 | 26
2017-05-18 12:30 | 47 | 27
2017-05-18 13:00 | 48 | 26
2017-05-18 13:30 | 48 | 27
2017-05-18 14:00 | 48 | 27
2017-05-18 14:30 | 48 | 27
2017-05-18 15:00 | 49 | 24
2017-05-18 15:30 | 49 | 25
2017-05-18 16:00 | 50 | 29
2017-05-18 16:30 | 50 | 29
2017-05-18 17:00 | 49 | 29
2017-05-18 17:30 | 47 | 32
2017-05-18 18:00 | 49 | 39
2017-05-18 18:30 | 48 | 42
2017-05-18 19:00 | 48 | 42
2017-05-18 19:30 | 48 | 41
2017-05-18 20:00 | 48 | 41
2017-05-18 20:30 | 52 | 47
2017-05-18 21:00 | 56 | 53
2017-05-18 21:30 | 59 | 56
2017-05-18 22:00 | 60 | 58
2017-05-18 22:30 | 61 | 59
2017-05-18 23:00 | 41 | 37
2017-05-18 23:30 | 38 | 38
2017-05-19 | 51 | 51
2017-05-19 00:30 | 59 | 58
2017-05-19 01:00 | 59 | 58
2017-05-19 01:30 | 58 | 57
2017-05-19 02:00 | 57 | 56
2017-05-19 02:30 | 57 | 56
2017-05-19 03:00 | 57 | 56
2017-05-19 03:30 | 56 | 56
2017-05-19 04:00 | 56 | 56
2017-05-19 04:30 | 57 | 57
2017-05-19 05:00 | 58 | 57
2017-05-19 05:30 | 58 | 57
2017-05-19 06:00 | 58 | 57
2017-05-19 06:30 | 43 | 43
2017-05-19 07:00 | 39 | 39
2017-05-19 07:30 | 38 | 38
2017-05-19 08:00 | 38 | 38
2017-05-19 08:30 | 38 | 38
2017-05-19 09:00 | 39 | 39
2017-05-19 09:30 | 40 | 40
2017-05-19 10:00 | 40 | 40
2017-05-19 10:30 | 40 | 40
2017-05-19 11:00 | 40 | 40
2017-05-19 11:30 | 15 | 14
2017-05-19 12:00 | 9 | 6
2017-05-19 12:30 | 8 | 4
2017-05-19 13:00 | 14 | 10
2017-05-19 13:30 | 35 | 33
2017-05-19 14:00 | 45 | 44
2017-05-19 14:30 | 47 | 45
2017-05-19 15:00 | 47 | 46
2017-05-19 15:30 | 46 | 45
2017-05-19 16:00 | 41 | 40
2017-05-19 16:30 | 42 | 41
2017-05-19 17:00 | 41 | 40
2017-05-19 17:30 | 41 | 40
2017-05-19 18:00 | 42 | 41
2017-05-19 18:30 | 42 | 41
2017-05-19 19:00 | 49 | 48
2017-05-19 19:30 | 52 | 52
2017-05-19 20:00 | 51 | 51
2017-05-19 20:30 | 49 | 49
2017-05-19 21:00 | 49 | 49
2017-05-19 21:30 | 49 | 49
2017-05-19 22:00 | 53 | 53
2017-05-19 22:30 | 44 | 43
2017-05-19 23:00 | 41 | 39
2017-05-19 23:30 | 41 | 39
2017-05-20 | 46 | 45
2017-05-20 00:30 | 48 | 48
2017-05-20 01:00 | 49 | 49
2017-05-20 01:30 | 53 | 53
2017-05-20 02:00 | 53 | 53
2017-05-20 02:30 | 53 | 53
2017-05-20 03:00 | 52 | 52
2017-05-20 03:30 | 53 | 53
2017-05-20 04:00 | 49 | 49
2017-05-20 04:30 | 39 | 37
2017-05-20 05:00 | 39 | 37
2017-05-20 05:30 | 39 | 37
2017-05-20 06:00 | 39 | 37
2017-05-20 06:30 | 39 | 37
2017-05-20 07:00 | 39 | 37
2017-05-20 07:30 | 39 | 38
2017-05-20 08:00 | 39 | 37
2017-05-20 08:30 | 40 | 40
2017-05-20 09:00 | 41 | 41
2017-05-20 09:30 | 42 | 41
2017-05-20 10:00 | 42 | 41
2017-05-20 10:30 | 43 | 42
2017-05-20 11:00 | 42 | 41
2017-05-20 11:30 | 42 | 41
2017-05-20 12:00 | 42 | 41
2017-05-20 12:30 | 42 | 40
2017-05-20 13:00 | 42 | 40
2017-05-20 13:30 | 41 | 39
2017-05-20 14:00 | 41 | 39
2017-05-20 14:30 | 42 | 40
2017-05-20 15:00 | 43 | 41
2017-05-20 15:30 | 42 | 40
2017-05-20 16:00 | 42 | 40
2017-05-20 16:30 | 42 | 40
2017-05-20 17:00 | 43 | 41
2017-05-20 17:30 | 43 | 41
2017-05-20 18:00 | 44 | 42
2017-05-20 18:30 | 44 | 43
2017-05-20 19:00 | 44 | 43
2017-05-20 19:30 | 44 | 43
2017-05-20 20:00 | 45 | 44
2017-05-20 20:30 | 43 | 42
2017-05-20 21:00 | 43 | 42
2017-05-20 21:30 | 43 | 42
2017-05-20 22:00 | 43 | 42
2017-05-20 22:30 | 44 | 41
2017-05-20 23:00 | 42 | 41
2017-05-20 23:30 | 41 | 40
2017-05-21 | 42 | 41
2017-05-21 00:30 | 42 | 41
2017-05-21 01:00 | 42 | 41
2017-05-21 01:30 | 42 | 40
2017-05-21 02:00 | 41 | 40
2017-05-21 02:30 | 41 | 40
2017-05-21 03:00 | 41 | 40
2017-05-21 03:30 | 41 | 40
2017-05-21 04:00 | 41 | 40
2017-05-21 04:30 | 41 | 40
2017-05-21 05:00 | 41 | 40
2017-05-21 05:30 | 42 | 40
2017-05-21 06:00 | 40 | 39
2017-05-21 06:30 | 41 | 39
2017-05-21 07:00 | 41 | 39
2017-05-21 07:30 | 41 | 39
2017-05-21 08:00 | 41 | 39
2017-05-21 08:30 | 40 | 39
2017-05-21 09:00 | 40 | 39
2017-05-21 09:30 | 40 | 39
2017-05-21 10:00 | 40 | 39
2017-05-21 10:30 | 40 | 39
2017-05-21 11:00 | 40 | 39
2017-05-21 11:30 | 39 | 39
2017-05-21 12:00 | 39 | 39
2017-05-21 12:30 | 39 | 38
2017-05-21 13:00 | 39 | 39
2017-05-21 13:30 | 38 | 38
2017-05-21 14:00 | 39 | 38
2017-05-21 14:30 | 40 | 40
2017-05-21 15:00 | 41 | 40
2017-05-21 15:30 | 41 | 40
2017-05-21 16:00 | 41 | 41
2017-05-21 16:30 | 41 | 41
2017-05-21 17:00 | 42 | 41
2017-05-21 17:30 | 42 | 42
2017-05-21 18:00 | 44 | 43
2017-05-21 18:30 | 45 | 44
2017-05-21 19:00 | 45 | 44
2017-05-21 19:30 | 45 | 44
2017-05-21 20:00 | 45 | 43
2017-05-21 20:30 | 43 | 42
2017-05-21 21:00 | 43 | 41
2017-05-21 21:30 | 43 | 41
2017-05-21 22:00 | 42 | 40
2017-05-21 22:30 | 43 | 39
2017-05-21 23:00 | 43 | 39
2017-05-21 23:30 | 43 | 39
2017-05-22 | 42 | 39
2017-05-22 00:30 | 41 | 39
2017-05-22 01:00 | 40 | 39
2017-05-22 01:30 | 40 | 39
2017-05-22 02:00 | 40 | 39
2017-05-22 02:30 | 40 | 39
2017-05-22 03:00 | 40 | 39
2017-05-22 03:30 | 41 | 40
2017-05-22 04:00 | 42 | 41
2017-05-22 04:30 | 42 | 41
2017-05-22 05:00 | 42 | 41
2017-05-22 05:30 | 41 | 40
2017-05-22 06:00 | 41 | 39
2017-05-22 06:30 | 43 | 42
2017-05-22 07:00 | 44 | 44
2017-05-22 07:30 | 43 | 43
2017-05-22 08:00 | 44 | 44
2017-05-22 08:30 | 44 | 44
2017-05-22 09:00 | 45 | 45
2017-05-22 09:30 | 44 | 44
2017-05-22 10:00 | 44 | 44
2017-05-22 10:30 | 44 | 44
2017-05-22 11:00 | 44 | 44
2017-05-22 11:30 | 44 | 44
2017-05-22 12:00 | 46 | 46
2017-05-22 12:30 | 50 | 49
2017-05-22 13:00 | 49 | 49
2017-05-22 13:30 | 49 | 49
2017-05-22 14:00 | 51 | 50
2017-05-22 14:30 | 52 | 51
2017-05-22 15:00 | 51 | 51
2017-05-22 15:30 | 52 | 52
2017-05-22 16:00 | 52 | 52
2017-05-22 16:30 | 52 | 52
2017-05-22 17:00 | 53 | 52
2017-05-22 17:30 | 53 | 52
2017-05-22 18:00 | 53 | 53
2017-05-22 18:30 | 53 | 53
2017-05-22 19:00 | 49 | 48
2017-05-22 19:30 | 49 | 49
2017-05-22 20:00 | 49 | 49
2017-05-22 20:30 | 48 | 47
2017-05-22 21:00 | 48 | 47
2017-05-22 21:30 | 48 | 47
2017-05-22 22:00 | 48 | 47
2017-05-22 22:30 | 46 | 46
2017-05-22 23:00 | 46 | 46
2017-05-22 23:30 | 47 | 47
2017-05-23 | 50 | 50
2017-05-23 00:30 | 51 | 51
2017-05-23 01:00 | 52 | 52
2017-05-23 01:30 | 56 | 56
2017-05-23 02:00 | 59 | 59
2017-05-23 02:30 | 59 | 58
2017-05-23 03:00 | 58 | 58
2017-05-23 03:30 | 59 | 59
2017-05-23 04:00 | 60 | 59
2017-05-23 04:30 | 60 | 59
2017-05-23 05:00 | 60 | 60
2017-05-23 05:30 | 61 | 61
2017-05-23 06:00 | 62 | 61
2017-05-23 06:30 | 62 | 61
2017-05-23 07:00 | 46 | 46
2017-05-23 07:30 | 56 | 56
2017-05-23 08:00 | 64 | 62
2017-05-23 08:30 | 65 | 63
2017-05-23 09:00 | 64 | 62
2017-05-23 09:30 | 64 | 62
2017-05-23 10:00 | 64 | 62
2017-05-23 10:30 | 65 | 63
2017-05-23 11:00 | 68 | 65
2017-05-23 11:30 | 68 | 66
2017-05-23 12:00 | 68 | 65
2017-05-23 12:30 | 69 | 66
2017-05-23 13:00 | 69 | 66
2017-05-23 13:30 | 69 | 66
2017-05-23 14:00 | 70 | 67
2017-05-23 14:30 | 71 | 69
2017-05-23 15:00 | 73 | 70
2017-05-23 15:30 | 73 | 70
2017-05-23 16:00 | 72 | 69
2017-05-23 16:30 | 72 | 68
2017-05-23 17:00 | 72 | 69
2017-05-23 17:30 | 75 | 71
2017-05-23 18:00 | 77 | 72
2017-05-23 18:30 | 77 | 73
2017-05-23 19:00 | 78 | 74
2017-05-23 19:30 | 75 | 71
2017-05-23 20:00 | 74 | 71
2017-05-23 20:30 | 73 | 69
2017-05-23 21:00 | 75 | 71
2017-05-23 21:30 | 73 | 69
2017-05-23 22:00 | 73 | 68
2017-05-23 22:30 | 72 | 68
2017-05-23 23:00 | 70 | 67
2017-05-23 23:30 | 69 | 66
2017-05-24 | 68 | 65
2017-05-24 00:30 | 68 | 65
2017-05-24 01:00 | 68 | 64
2017-05-24 01:30 | 66 | 65
2017-05-24 02:00 | 65 | 65
2017-05-24 02:30 | 64 | 64
2017-05-24 03:00 | 65 | 65
2017-05-24 03:30 | 65 | 65
2017-05-24 04:00 | 65 | 65
2017-05-24 04:30 | 65 | 65
2017-05-24 05:00 | 65 | 65
2017-05-24 05:30 | 67 | 66
2017-05-24 06:00 | 66 | 66
2017-05-24 06:30 | 67 | 67
2017-05-24 07:00 | 66 | 66
2017-05-24 07:30 | 67 | 67
2017-05-24 08:00 | 62 | 62
2017-05-24 08:30 | 59 | 59
2017-05-24 09:00 | 66 | 66
2017-05-24 09:30 | 66 | 66
2017-05-24 10:00 | 65 | 65
2017-05-24 10:30 | 66 | 66
2017-05-24 11:00 | 66 | 65
2017-05-24 11:30 | 65 | 65
2017-05-24 12:00 | 65 | 65
2017-05-24 12:30 | 66 | 66
2017-05-24 13:00 | 66 | 66
2017-05-24 13:30 | 67 | 67
2017-05-24 14:00 | 66 | 66
2017-05-24 14:30 | 67 | 67
2017-05-24 15:00 | 69 | 69
2017-05-24 15:30 | 69 | 69
2017-05-24 16:00 | 70 | 70
2017-05-24 16:30 | 69 | 69
2017-05-24 17:00 | 69 | 68
2017-05-24 17:30 | 70 | 70
2017-05-24 18:00 | 68 | 68
2017-05-24 18:30 | 70 | 70
2017-05-24 19:00 | 71 | 71
2017-05-24 19:30 | 69 | 69
2017-05-24 20:00 | 69 | 69
2017-05-24 20:30 | 68 | 68
2017-05-24 21:00 | 68 | 68
2017-05-24 21:30 | 67 | 67
2017-05-24 22:00 | 67 | 67
2017-05-24 22:30 | 55 | 54
2017-05-24 23:00 | 46 | 45
2017-05-24 23:30 | 58 | 58
2017-05-25 | 64 | 64
2017-05-25 00:30 | 64 | 64
2017-05-25 01:00 | 60 | 60
2017-05-25 01:30 | 60 | 60
2017-05-25 02:00 | 60 | 60
2017-05-25 02:30 | 60 | 60
2017-05-25 03:00 | 61 | 61
2017-05-25 03:30 | 61 | 61
2017-05-25 04:00 | 61 | 60
2017-05-25 04:30 | 60 | 60
2017-05-25 05:00 | 60 | 60
2017-05-25 05:30 | 61 | 60
2017-05-25 06:00 | 62 | 61
2017-05-25 06:30 | 46 | 46
2017-05-25 07:00 | 41 | 41
2017-05-25 07:30 | 41 | 41
2017-05-25 08:00 | 42 | 42
2017-05-25 08:30 | 56 | 56
2017-05-25 09:00 | 63 | 63
2017-05-25 09:30 | 63 | 63
2017-05-25 10:00 | 63 | 62
2017-05-25 10:30 | 63 | 63
2017-05-25 11:00 | 64 | 63
2017-05-25 11:30 | 63 | 62
2017-05-25 12:00 | 63 | 63
2017-05-25 12:30 | 64 | 63
2017-05-25 13:00 | 65 | 65
2017-05-25 13:30 | 66 | 66
2017-05-25 14:00 | 66 | 66
2017-05-25 14:30 | 66 | 66
2017-05-25 15:00 | 66 | 66
2017-05-25 15:30 | 66 | 65
2017-05-25 16:00 | 66 | 66
2017-05-25 16:30 | 67 | 67
2017-05-25 17:00 | 68 | 68
2017-05-25 17:30 | 56 | 51
2017-05-25 18:00 | 54 | 46
2017-05-25 18:30 | 53 | 46
2017-05-25 19:00 | 54 | 47
2017-05-25 19:30 | 53 | 45
2017-05-25 20:00 | 53 | 45
2017-05-25 20:30 | 53 | 45
2017-05-25 21:00 | 53 | 44
2017-05-25 21:30 | 53 | 44
2017-05-25 22:00 | 54 | 44
2017-05-25 22:30 | 54 | 43
2017-05-25 23:00 | 54 | 43
2017-05-25 23:30 | 46 | 42
2017-05-26 | 43 | 42
2017-05-26 00:30 | 43 | 42
2017-05-26 01:00 | 43 | 42
2017-05-26 01:30 | 43 | 42
2017-05-26 02:00 | 59 | 59
2017-05-26 02:30 | 61 | 61
2017-05-26 03:00 | 61 | 61
2017-05-26 03:30 | 61 | 61
2017-05-26 04:00 | 61 | 61
2017-05-26 04:30 | 62 | 62
2017-05-26 05:00 | 62 | 62
2017-05-26 05:30 | 62 | 62
2017-05-26 06:00 | 63 | 62
2017-05-26 06:30 | 48 | 47
2017-05-26 07:00 | 43 | 43
2017-05-26 07:30 | 44 | 44
2017-05-26 08:00 | 44 | 44
2017-05-26 08:30 | 58 | 57
2017-05-26 09:00 | 64 | 63
2017-05-26 09:30 | 64 | 64
2017-05-26 10:00 | 63 | 62
2017-05-26 10:30 | 62 | 61
2017-05-26 11:00 | 62 | 62
2017-05-26 11:30 | 63 | 63
2017-05-26 12:00 | 63 | 62
2017-05-26 12:30 | 67 | 66
2017-05-26 13:00 | 67 | 66
2017-05-26 13:30 | 67 | 66
2017-05-26 14:00 | 67 | 67
2017-05-26 14:30 | 69 | 68
2017-05-26 15:00 | 69 | 69
2017-05-26 15:30 | 68 | 67
2017-05-26 16:00 | 69 | 68
2017-05-26 16:30 | 69 | 68
2017-05-26 17:00 | 69 | 69
2017-05-26 17:30 | 58 | 52
2017-05-26 18:00 | 56 | 48
2017-05-26 18:30 | 65 | 63
2017-05-26 19:00 | 69 | 68
2017-05-26 19:30 | 70 | 69
2017-05-26 20:00 | 69 | 68
2017-05-26 20:30 | 69 | 68
2017-05-26 21:00 | 69 | 68
2017-05-26 21:30 | 68 | 67
2017-05-26 22:00 | 68 | 67
2017-05-26 22:30 | 68 | 67
2017-05-26 23:00 | 68 | 67
2017-05-26 23:30 | 68 | 66
2017-05-27 | 69 | 66
2017-05-27 00:30 | 68 | 65
2017-05-27 01:00 | 68 | 65
2017-05-27 01:30 | 68 | 65
2017-05-27 02:00 | 68 | 65
2017-05-27 02:30 | 68 | 66
2017-05-27 03:00 | 68 | 65
2017-05-27 03:30 | 68 | 65
2017-05-27 04:00 | 68 | 65
2017-05-27 04:30 | 68 | 65
2017-05-27 05:00 | 68 | 65
2017-05-27 05:30 | 68 | 65
2017-05-27 06:00 | 68 | 65
2017-05-27 06:30 | 68 | 66
2017-05-27 07:00 | 67 | 65
2017-05-27 07:30 | 68 | 66
2017-05-27 08:00 | 68 | 66
2017-05-27 08:30 | 69 | 67
2017-05-27 09:00 | 68 | 67
2017-05-27 09:30 | 67 | 66
2017-05-27 10:00 | 67 | 65
2017-05-27 10:30 | 66 | 65
2017-05-27 11:00 | 67 | 65
2017-05-27 11:30 | 66 | 65
2017-05-27 12:00 | 67 | 65
2017-05-27 12:30 | 67 | 65
2017-05-27 13:00 | 67 | 65
2017-05-27 13:30 | 67 | 65
2017-05-27 14:00 | 67 | 65
2017-05-27 14:30 | 67 | 65
2017-05-27 15:00 | 67 | 65
2017-05-27 15:30 | 68 | 66
2017-05-27 16:00 | 69 | 67
2017-05-27 16:30 | 70 | 69
2017-05-27 17:00 | 71 | 69
2017-05-27 17:30 | 72 | 70
2017-05-27 18:00 | 64 | 60
2017-05-27 18:30 | 58 | 49
2017-05-27 19:00 | 70 | 68
2017-05-27 19:30 | 72 | 71
2017-05-27 20:00 | 72 | 71
2017-05-27 20:30 | 71 | 70
2017-05-27 21:00 | 71 | 69
2017-05-27 21:30 | 71 | 69
2017-05-27 22:00 | 71 | 69
2017-05-27 22:30 | 71 | 69
2017-05-27 23:00 | 71 | 69
2017-05-27 23:30 | 70 | 68
2017-05-28 | 70 | 68
2017-05-28 00:30 | 70 | 68
2017-05-28 01:00 | 70 | 68
2017-05-28 01:30 | 70 | 67
2017-05-28 02:00 | 69 | 67
2017-05-28 02:30 | 69 | 67
2017-05-28 03:00 | 69 | 67
2017-05-28 03:30 | 69 | 67
2017-05-28 04:00 | 69 | 67
2017-05-28 04:30 | 69 | 67
2017-05-28 05:00 | 69 | 67
2017-05-28 05:30 | 68 | 66
2017-05-28 06:00 | 68 | 66
2017-05-28 06:30 | 68 | 66
2017-05-28 07:00 | 68 | 66
2017-05-28 07:30 | 69 | 66
2017-05-28 08:00 | 69 | 66
2017-05-28 08:30 | 69 | 67
2017-05-28 09:00 | 68 | 66
2017-05-28 09:30 | 69 | 67
2017-05-28 10:00 | 70 | 66
2017-05-28 10:30 | 70 | 66
2017-05-28 11:00 | 70 | 66
2017-05-28 11:30 | 70 | 67
2017-05-28 12:00 | 70 | 67
2017-05-28 12:30 | 70 | 67
2017-05-28 13:00 | 70 | 67
2017-05-28 13:30 | 71 | 67
2017-05-28 14:00 | 70 | 67
2017-05-28 14:30 | 71 | 68
2017-05-28 15:00 | 72 | 68
2017-05-28 15:30 | 72 | 69
2017-05-28 16:00 | 74 | 71
2017-05-28 16:30 | 74 | 71
2017-05-28 17:00 | 74 | 70
2017-05-28 17:30 | 74 | 71
2017-05-28 18:00 | 69 | 65
2017-05-28 18:30 | 68 | 64
2017-05-28 19:00 | 74 | 72
2017-05-28 19:30 | 74 | 72
2017-05-28 20:00 | 73 | 70
2017-05-28 20:30 | 73 | 71
2017-05-28 21:00 | 72 | 70
2017-05-28 21:30 | 72 | 69
2017-05-28 22:00 | 72 | 69
2017-05-28 22:30 | 71 | 68
2017-05-28 23:00 | 72 | 67
2017-05-28 23:30 | 71 | 67
2017-05-29 | 71 | 67
2017-05-29 00:30 | 67 | 67
2017-05-29 01:00 | 67 | 66
2017-05-29 01:30 | 67 | 66
2017-05-29 02:00 | 66 | 66
2017-05-29 02:30 | 67 | 66
2017-05-29 03:00 | 67 | 66
2017-05-29 03:30 | 66 | 66
2017-05-29 04:00 | 67 | 66
2017-05-29 04:30 | 67 | 66
2017-05-29 05:00 | 66 | 66
2017-05-29 05:30 | 66 | 66
2017-05-29 06:00 | 66 | 66
2017-05-29 06:30 | 68 | 67
2017-05-29 07:00 | 48 | 47
2017-05-29 07:30 | 63 | 63
2017-05-29 08:00 | 70 | 70
2017-05-29 08:30 | 70 | 70
2017-05-29 09:00 | 70 | 69
2017-05-29 09:30 | 69 | 69
2017-05-29 10:00 | 68 | 67
2017-05-29 10:30 | 69 | 69
2017-05-29 11:00 | 69 | 68
2017-05-29 11:30 | 69 | 68
2017-05-29 12:00 | 67 | 66
2017-05-29 12:30 | 68 | 67
2017-05-29 13:00 | 68 | 67
2017-05-29 13:30 | 69 | 68
2017-05-29 14:00 | 68 | 67
2017-05-29 14:30 | 68 | 67
2017-05-29 15:00 | 70 | 69
2017-05-29 15:30 | 70 | 69
2017-05-29 16:00 | 71 | 70
2017-05-29 16:30 | 71 | 70
2017-05-29 17:00 | 66 | 64
2017-05-29 17:30 | 60 | 53
2017-05-29 18:00 | 60 | 54
2017-05-29 18:30 | 61 | 55
2017-05-29 19:00 | 60 | 54
2017-05-29 19:30 | 66 | 62
2017-05-29 20:00 | 70 | 69
2017-05-29 20:30 | 70 | 69
2017-05-29 21:00 | 70 | 68
2017-05-29 21:30 | 69 | 67
2017-05-29 22:00 | 70 | 67
2017-05-29 22:30 | 69 | 67
2017-05-29 23:00 | 68 | 65
2017-05-29 23:30 | 65 | 65
2017-05-30 | 65 | 64
2017-05-30 00:30 | 65 | 65
2017-05-30 01:00 | 65 | 65
2017-05-30 01:30 | 65 | 65
2017-05-30 02:00 | 65 | 64
2017-05-30 02:30 | 65 | 64
2017-05-30 03:00 | 64 | 64
2017-05-30 03:30 | 60 | 60
2017-05-30 04:00 | 41 | 38
2017-05-30 04:30 | 59 | 59
2017-05-30 05:00 | 66 | 65
2017-05-30 05:30 | 66 | 66
2017-05-30 06:00 | 66 | 66
2017-05-30 06:30 | 55 | 55
2017-05-30 07:00 | 50 | 50
2017-05-30 07:30 | 51 | 51
2017-05-30 08:00 | 52 | 52
2017-05-30 08:30 | 52 | 52
2017-05-30 09:00 | 56 | 56
2017-05-30 09:30 | 54 | 54
2017-05-30 10:00 | 60 | 59
2017-05-30 10:30 | 62 | 60
2017-05-30 11:00 | 62 | 60
2017-05-30 11:30 | 61 | 59
2017-05-30 12:00 | 61 | 59
2017-05-30 12:30 | 62 | 60
2017-05-30 13:00 | 62 | 60
2017-05-30 13:30 | 65 | 63
2017-05-30 14:00 | 67 | 65
2017-05-30 14:30 | 68 | 67
2017-05-30 15:00 | 69 | 68
2017-05-30 15:30 | 71 | 69
2017-05-30 16:00 | 70 | 69
2017-05-30 16:30 | 70 | 69
2017-05-30 17:00 | 64 | 63
2017-05-30 17:30 | 53 | 53
2017-05-30 18:00 | 52 | 52
2017-05-30 18:30 | 53 | 53
2017-05-30 19:00 | 54 | 54
2017-05-30 19:30 | 62 | 61
2017-05-30 20:00 | 56 | 56
2017-05-30 20:30 | 52 | 52
2017-05-30 21:00 | 64 | 63
2017-05-30 21:30 | 68 | 67
2017-05-30 22:00 | 67 | 67
2017-05-30 22:30 | 67 | 66
2017-05-30 23:00 | 66 | 66
2017-05-30 23:30 | 66 | 66
2017-05-31 | 66 | 66
2017-05-31 00:30 | 66 | 65
2017-05-31 01:00 | 65 | 65
2017-05-31 01:30 | 65 | 65
2017-05-31 02:00 | 65 | 65
2017-05-31 02:30 | 65 | 65
2017-05-31 03:00 | 65 | 65
2017-05-31 03:30 | 65 | 65
2017-05-31 04:00 | 64 | 64
2017-05-31 04:30 | 65 | 65
2017-05-31 05:00 | 65 | 64
2017-05-31 05:30 | 65 | 65
2017-05-31 06:00 | 66 | 66
2017-05-31 06:30 | 55 | 54
2017-05-31 07:00 | 49 | 47
2017-05-31 07:30 | 50 | 49
2017-05-31 08:00 | 54 | 50
2017-05-31 08:30 | 67 | 60
2017-05-31 09:00 | 70 | 66
2017-05-31 09:30 | 56 | 52
2017-05-31 10:00 | 53 | 49
2017-05-31 10:30 | 56 | 53
2017-05-31 11:00 | 61 | 56
2017-05-31 11:30 | 61 | 57
2017-05-31 12:00 | 61 | 57
2017-05-31 12:30 | 62 | 59
2017-05-31 13:00 | 62 | 58
2017-05-31 13:30 | 62 | 59
2017-05-31 14:00 | 62 | 58
2017-05-31 14:30 | 68 | 64
2017-05-31 15:00 | 77 | 74
2017-05-31 15:30 | 78 | 75
2017-05-31 16:00 | 79 | 76
2017-05-31 16:30 | 80 | 76
2017-05-31 17:00 | 80 | 75
2017-05-31 17:30 | 62 | 57
2017-05-31 18:00 | 60 | 57
2017-05-31 18:30 | 60 | 58
2017-05-31 19:00 | 60 | 58
2017-05-31 19:30 | 59 | 57
2017-05-31 20:00 | 59 | 56
2017-05-31 20:30 | 59 | 55
2017-05-31 21:00 | 58 | 54
2017-05-31 21:30 | 57 | 53
2017-05-31 22:00 | 57 | 53
2017-05-31 22:30 | 57 | 53
2017-05-31 23:00 | 57 | 52
2017-05-31 23:30 | 57 | 52
2017-06-01 | 65 | 63
2017-06-01 00:30 | 66 | 66
2017-06-01 01:00 | 66 | 66
2017-06-01 01:30 | 65 | 65
2017-06-01 02:00 | 65 | 65
2017-06-01 02:30 | 66 | 66
2017-06-01 03:00 | 66 | 65
2017-06-01 03:30 | 65 | 65
2017-06-01 04:00 | 66 | 66
2017-06-01 04:30 | 66 | 66
2017-06-01 05:00 | 66 | 66
2017-06-01 05:30 | 66 | 66
2017-06-01 06:00 | 57 | 56
2017-06-01 06:30 | 50 | 49
2017-06-01 07:00 | 49 | 47
2017-06-01 07:30 | 51 | 49
2017-06-01 08:00 | 46 | 44
2017-06-01 08:30 | 57 | 56
2017-06-01 09:00 | 70 | 70
2017-06-01 09:30 | 69 | 69
2017-06-01 10:00 | 68 | 68
2017-06-01 10:30 | 67 | 67
2017-06-01 11:00 | 67 | 67
2017-06-01 11:30 | 67 | 67
2017-06-01 12:00 | 68 | 68
2017-06-01 12:30 | 69 | 69
2017-06-01 13:00 | 69 | 69
2017-06-01 13:30 | 69 | 69
2017-06-01 14:00 | 69 | 69
2017-06-01 14:30 | 70 | 70
2017-06-01 15:00 | 71 | 70
2017-06-01 15:30 | 71 | 71
2017-06-01 16:00 | 71 | 71
2017-06-01 16:30 | 73 | 73
2017-06-01 17:00 | 77 | 77
2017-06-01 17:30 | 77 | 77
2017-06-01 18:00 | 62 | 61
2017-06-01 18:30 | 58 | 56
2017-06-01 19:00 | 72 | 71
2017-06-01 19:30 | 79 | 79
2017-06-01 20:00 | 79 | 79
2017-06-01 20:30 | 78 | 78
2017-06-01 21:00 | 77 | 77
2017-06-01 21:30 | 77 | 77
2017-06-01 22:00 | 75 | 75
2017-06-01 22:30 | 76 | 76
2017-06-01 23:00 | 74 | 74
2017-06-01 23:30 | 74 | 74
2017-06-02 | 71 | 71
2017-06-02 00:30 | 70 | 69
2017-06-02 01:00 | 70 | 69
2017-06-02 01:30 | 70 | 69
2017-06-02 02:00 | 69 | 69
2017-06-02 02:30 | 70 | 69
2017-06-02 03:00 | 69 | 69
2017-06-02 03:30 | 68 | 68
2017-06-02 04:00 | 69 | 68
2017-06-02 04:30 | 69 | 69
2017-06-02 05:00 | 70 | 70
2017-06-02 05:30 | 71 | 71
2017-06-02 06:00 | 72 | 71
2017-06-02 06:30 | 72 | 72
2017-06-02 07:00 | 75 | 74
2017-06-02 07:30 | 76 | 75
2017-06-02 08:00 | 75 | 75
2017-06-02 08:30 | 74 | 74
2017-06-02 09:00 | 74 | 73
2017-06-02 09:30 | 72 | 71
2017-06-02 10:00 | 70 | 69
2017-06-02 10:30 | 69 | 67
2017-06-02 11:00 | 69 | 67
2017-06-02 11:30 | 68 | 66
2017-06-02 12:00 | 68 | 67
2017-06-02 12:30 | 70 | 68
2017-06-02 13:00 | 70 | 69
2017-06-02 13:30 | 71 | 70
2017-06-02 14:00 | 72 | 71
2017-06-02 14:30 | 72 | 71
2017-06-02 15:00 | 72 | 71
2017-06-02 15:30 | 72 | 71
2017-06-02 16:00 | 72 | 70
2017-06-02 16:30 | 73 | 71
2017-06-02 17:00 | 76 | 74
2017-06-02 17:30 | 68 | 62
2017-06-02 18:00 | 70 | 65
2017-06-02 18:30 | 70 | 66
2017-06-02 19:00 | 70 | 65
2017-06-02 19:30 | 70 | 65
2017-06-02 20:00 | 71 | 66
2017-06-02 20:30 | 71 | 65
2017-06-02 21:00 | 77 | 76
2017-06-02 21:30 | 76 | 74
2017-06-02 22:00 | 76 | 74
2017-06-02 22:30 | 77 | 75
2017-06-02 23:00 | 75 | 73
2017-06-02 23:30 | 75 | 73
2017-06-03 | 72 | 71
2017-06-03 00:30 | 72 | 72
2017-06-03 01:00 | 69 | 68
2017-06-03 01:30 | 68 | 68
2017-06-03 02:00 | 68 | 67
2017-06-03 02:30 | 67 | 66
2017-06-03 03:00 | 67 | 67
2017-06-03 03:30 | 67 | 66
2017-06-03 04:00 | 67 | 67
2017-06-03 04:30 | 67 | 66
2017-06-03 05:00 | 67 | 66
2017-06-03 05:30 | 67 | 66
2017-06-03 06:00 | 66 | 66
2017-06-03 06:30 | 60 | 60
2017-06-03 07:00 | 67 | 67
2017-06-03 07:30 | 68 | 68
2017-06-03 08:00 | 69 | 68
2017-06-03 08:30 | 69 | 68
2017-06-03 09:00 | 69 | 68
2017-06-03 09:30 | 68 | 67
2017-06-03 10:00 | 68 | 67
2017-06-03 10:30 | 67 | 67
2017-06-03 11:00 | 65 | 65
2017-06-03 11:30 | 66 | 65
2017-06-03 12:00 | 67 | 66
2017-06-03 12:30 | 67 | 66
2017-06-03 13:00 | 65 | 65
2017-06-03 13:30 | 66 | 65
2017-06-03 14:00 | 67 | 66
2017-06-03 14:30 | 67 | 66
2017-06-03 15:00 | 68 | 67
2017-06-03 15:30 | 68 | 68
2017-06-03 16:00 | 70 | 69
2017-06-03 16:30 | 71 | 70
2017-06-03 17:00 | 71 | 71
2017-06-03 17:30 | 72 | 72
2017-06-03 18:00 | 66 | 65
2017-06-03 18:30 | 59 | 51
2017-06-03 19:00 | 71 | 69
2017-06-03 19:30 | 72 | 71
2017-06-03 20:00 | 71 | 70
2017-06-03 20:30 | 70 | 69
2017-06-03 21:00 | 71 | 69
2017-06-03 21:30 | 71 | 69
2017-06-03 22:00 | 70 | 68
2017-06-03 22:30 | 70 | 68
2017-06-03 23:00 | 70 | 67
2017-06-03 23:30 | 66 | 66
2017-06-04 | 67 | 67
2017-06-04 00:30 | 67 | 67
2017-06-04 01:00 | 66 | 66
2017-06-04 01:30 | 66 | 66
2017-06-04 02:00 | 66 | 66
2017-06-04 02:30 | 65 | 65
2017-06-04 03:00 | 65 | 65
2017-06-04 03:30 | 65 | 65
2017-06-04 04:00 | 65 | 65
2017-06-04 04:30 | 65 | 65
2017-06-04 05:00 | 66 | 66
2017-06-04 05:30 | 65 | 65
2017-06-04 06:00 | 65 | 65
2017-06-04 06:30 | 65 | 65
2017-06-04 07:00 | 65 | 65
2017-06-04 07:30 | 66 | 66
2017-06-04 08:00 | 67 | 67
2017-06-04 08:30 | 67 | 67
2017-06-04 09:00 | 67 | 67
2017-06-04 09:30 | 67 | 67
2017-06-04 10:00 | 67 | 66
2017-06-04 10:30 | 66 | 65
2017-06-04 11:00 | 66 | 65
2017-06-04 11:30 | 66 | 65
2017-06-04 12:00 | 66 | 65
2017-06-04 12:30 | 66 | 65
2017-06-04 13:00 | 66 | 65
2017-06-04 13:30 | 66 | 65
2017-06-04 14:00 | 66 | 65
2017-06-04 14:30 | 68 | 67
2017-06-04 15:00 | 68 | 67
2017-06-04 15:30 | 68 | 68
2017-06-04 16:00 | 70 | 69
2017-06-04 16:30 | 70 | 70
2017-06-04 17:00 | 70 | 70
2017-06-04 17:30 | 72 | 71
2017-06-04 18:00 | 72 | 72
2017-06-04 18:30 | 73 | 72
2017-06-04 19:00 | 72 | 72
2017-06-04 19:30 | 73 | 72
2017-06-04 20:00 | 72 | 71
2017-06-04 20:30 | 72 | 70
2017-06-04 21:00 | 72 | 70
2017-06-04 21:30 | 71 | 69
2017-06-04 22:00 | 71 | 68
2017-06-04 22:30 | 70 | 68
2017-06-04 23:00 | 71 | 69
2017-06-04 23:30 | 68 | 67
2017-06-05 | 67 | 67
2017-06-05 00:30 | 67 | 67
2017-06-05 01:00 | 66 | 66
2017-06-05 01:30 | 65 | 65
2017-06-05 02:00 | 66 | 66
2017-06-05 02:30 | 66 | 66
2017-06-05 03:00 | 66 | 66
2017-06-05 03:30 | 65 | 65
2017-06-05 04:00 | 66 | 66
2017-06-05 04:30 | 66 | 66
2017-06-05 05:00 | 67 | 67
2017-06-05 05:30 | 68 | 68
2017-06-05 06:00 | 68 | 68
2017-06-05 06:30 | 58 | 58
2017-06-05 07:00 | 55 | 55
2017-06-05 07:30 | 57 | 57
2017-06-05 08:00 | 56 | 56
2017-06-05 08:30 | 63 | 63
2017-06-05 09:00 | 65 | 64
2017-06-05 09:30 | 65 | 63
2017-06-05 10:00 | 65 | 63
2017-06-05 10:30 | 65 | 63
2017-06-05 11:00 | 65 | 63
2017-06-05 11:30 | 65 | 63
2017-06-05 12:00 | 65 | 63
2017-06-05 12:30 | 64 | 62
2017-06-05 13:00 | 63 | 62
2017-06-05 13:30 | 64 | 63
2017-06-05 14:00 | 64 | 63
2017-06-05 14:30 | 66 | 65
2017-06-05 15:00 | 66 | 65
2017-06-05 15:30 | 67 | 66
2017-06-05 16:00 | 67 | 66
2017-06-05 16:30 | 68 | 67
2017-06-05 17:00 | 69 | 68
2017-06-05 17:30 | 62 | 58
2017-06-05 18:00 | 61 | 56
2017-06-05 18:30 | 61 | 56
2017-06-05 19:00 | 60 | 56
2017-06-05 19:30 | 60 | 55
2017-06-05 20:00 | 60 | 54
2017-06-05 20:30 | 60 | 54
2017-06-05 21:00 | 68 | 66
2017-06-05 21:30 | 69 | 66
2017-06-05 22:00 | 67 | 66
2017-06-05 22:30 | 66 | 65
2017-06-05 23:00 | 65 | 63
2017-06-05 23:30 | 66 | 64
2017-06-06 | 66 | 64
2017-06-06 00:30 | 66 | 64
2017-06-06 01:00 | 66 | 64
2017-06-06 01:30 | 64 | 63
2017-06-06 02:00 | 64 | 63
2017-06-06 02:30 | 64 | 63
2017-06-06 03:00 | 64 | 63
2017-06-06 03:30 | 64 | 64
2017-06-06 04:00 | 64 | 63
2017-06-06 04:30 | 63 | 62
2017-06-06 05:00 | 62 | 62
2017-06-06 05:30 | 63 | 62
2017-06-06 06:00 | 62 | 61
2017-06-06 06:30 | 52 | 52
2017-06-06 07:00 | 52 | 52
2017-06-06 07:30 | 55 | 55
2017-06-06 08:00 | 57 | 56
2017-06-06 08:30 | 67 | 67
2017-06-06 09:00 | 68 | 68
2017-06-06 09:30 | 67 | 66
2017-06-06 10:00 | 67 | 66
2017-06-06 10:30 | 67 | 67
2017-06-06 11:00 | 71 | 70
2017-06-06 11:30 | 72 | 72
2017-06-06 12:00 | 73 | 72
2017-06-06 12:30 | 72 | 72
2017-06-06 13:00 | 72 | 71
2017-06-06 13:30 | 71 | 71
2017-06-06 14:00 | 71 | 71
2017-06-06 14:30 | 73 | 73
2017-06-06 15:00 | 75 | 74
2017-06-06 15:30 | 74 | 74
2017-06-06 16:00 | 75 | 75
2017-06-06 16:30 | 78 | 78
2017-06-06 17:00 | 80 | 79
2017-06-06 17:30 | 71 | 68
2017-06-06 18:00 | 72 | 69
2017-06-06 18:30 | 72 | 69
2017-06-06 19:00 | 72 | 69
2017-06-06 19:30 | 71 | 68
2017-06-06 20:00 | 71 | 69
2017-06-06 20:30 | 71 | 68
2017-06-06 21:00 | 75 | 74
2017-06-06 21:30 | 76 | 75
2017-06-06 22:00 | 69 | 69
2017-06-06 22:30 | 67 | 67
2017-06-06 23:00 | 67 | 66
2017-06-06 23:30 | 67 | 66
2017-06-07 | 67 | 66
2017-06-07 00:30 | 67 | 66
2017-06-07 01:00 | 65 | 64
2017-06-07 01:30 | 65 | 65
2017-06-07 02:00 | 66 | 65
2017-06-07 02:30 | 65 | 64
2017-06-07 03:00 | 65 | 64
2017-06-07 03:30 | 65 | 64
2017-06-07 04:00 | 65 | 64
2017-06-07 04:30 | 64 | 63
2017-06-07 05:00 | 65 | 64
2017-06-07 05:30 | 65 | 64
2017-06-07 06:00 | 65 | 64
2017-06-07 06:30 | 55 | 54
2017-06-07 07:00 | 55 | 54
2017-06-07 07:30 | 55 | 55
2017-06-07 08:00 | 56 | 55
2017-06-07 08:30 | 66 | 66
2017-06-07 09:00 | 66 | 65
2017-06-07 09:30 | 67 | 66
2017-06-07 10:00 | 67 | 66
2017-06-07 10:30 | 66 | 66
2017-06-07 11:00 | 66 | 65
2017-06-07 11:30 | 66 | 65
2017-06-07 12:00 | 66 | 65
2017-06-07 12:30 | 66 | 65
2017-06-07 13:00 | 66 | 65
2017-06-07 13:30 | 66 | 65
2017-06-07 14:00 | 66 | 65
2017-06-07 14:30 | 68 | 67
2017-06-07 15:00 | 68 | 68
2017-06-07 15:30 | 68 | 68
2017-06-07 16:00 | 69 | 69
2017-06-07 16:30 | 70 | 69
2017-06-07 17:00 | 69 | 68
2017-06-07 17:30 | 62 | 59
2017-06-07 18:00 | 61 | 59
2017-06-07 18:30 | 62 | 59
2017-06-07 19:00 | 60 | 58
2017-06-07 19:30 | 62 | 59
2017-06-07 20:00 | 61 | 59
2017-06-07 20:30 | 61 | 59
2017-06-07 21:00 | 67 | 66
2017-06-07 21:30 | 68 | 67
2017-06-07 22:00 | 68 | 68
2017-06-07 22:30 | 69 | 68
2017-06-07 23:00 | 69 | 68
2017-06-07 23:30 | 68 | 67
2017-06-08 | 68 | 67
2017-06-08 00:30 | 67 | 66
2017-06-08 01:00 | 66 | 66
2017-06-08 01:30 | 67 | 66
2017-06-08 02:00 | 66 | 65
2017-06-08 02:30 | 66 | 65
2017-06-08 03:00 | 65 | 64
2017-06-08 03:30 | 66 | 64
2017-06-08 04:00 | 66 | 65
2017-06-08 04:30 | 67 | 65
2017-06-08 05:00 | 67 | 66
2017-06-08 05:30 | 69 | 68
2017-06-08 06:00 | 70 | 68
2017-06-08 06:30 | 60 | 60
2017-06-08 07:00 | 54 | 54
2017-06-08 07:30 | 60 | 58
2017-06-08 08:00 | 62 | 60
2017-06-08 08:30 | 69 | 69
2017-06-08 09:00 | 69 | 69
2017-06-08 09:30 | 69 | 69
2017-06-08 10:00 | 70 | 70
2017-06-08 10:30 | 70 | 70
2017-06-08 11:00 | 71 | 71
2017-06-08 11:30 | 71 | 71
2017-06-08 12:00 | 70 | 70
2017-06-08 12:30 | 71 | 71
2017-06-08 13:00 | 71 | 71
2017-06-08 13:30 | 72 | 72
2017-06-08 14:00 | 71 | 71
2017-06-08 14:30 | 71 | 71
2017-06-08 15:00 | 71 | 71
2017-06-08 15:30 | 73 | 73
2017-06-08 16:00 | 72 | 72
2017-06-08 16:30 | 72 | 72
2017-06-08 17:00 | 73 | 73
2017-06-08 17:30 | 67 | 67
2017-06-08 18:00 | 63 | 61
2017-06-08 18:30 | 65 | 64
2017-06-08 19:00 | 66 | 65
2017-06-08 19:30 | 64 | 63
2017-06-08 20:00 | 64 | 62
2017-06-08 20:30 | 62 | 60
2017-06-08 21:00 | 69 | 69
2017-06-08 21:30 | 69 | 69
2017-06-08 22:00 | 69 | 69
2017-06-08 22:30 | 67 | 66
2017-06-08 23:00 | 65 | 64
2017-06-08 23:30 | 65 | 63
2017-06-09 | 65 | 64
2017-06-09 00:30 | 64 | 64
2017-06-09 01:00 | 65 | 64
2017-06-09 01:30 | 65 | 64
2017-06-09 02:00 | 64 | 64
2017-06-09 02:30 | 64 | 63
2017-06-09 03:00 | 63 | 62
2017-06-09 03:30 | 64 | 63
2017-06-09 04:00 | 65 | 64
2017-06-09 04:30 | 64 | 64
2017-06-09 05:00 | 65 | 64
2017-06-09 05:30 | 65 | 64
2017-06-09 06:00 | 64 | 63
2017-06-09 06:30 | 54 | 54
2017-06-09 07:00 | 53 | 53
2017-06-09 07:30 | 54 | 54
2017-06-09 08:00 | 58 | 55
2017-06-09 08:30 | 63 | 62
2017-06-09 09:00 | 58 | 56
2017-06-09 09:30 | 43 | 23
2017-06-09 10:00 | 28 | 25
2017-06-09 10:30 | 45 | 45
2017-06-09 11:00 | 54 | 54
2017-06-09 11:30 | 60 | 58
2017-06-09 12:00 | 60 | 60
2017-06-09 12:30 | 61 | 61
2017-06-09 13:00 | 61 | 61
2017-06-09 13:30 | 65 | 65
2017-06-09 14:00 | 65 | 65
2017-06-09 14:30 | 66 | 66
2017-06-09 15:00 | 66 | 66
2017-06-09 15:30 | 62 | 59
2017-06-09 16:00 | 64 | 63
2017-06-09 16:30 | 65 | 64
2017-06-09 17:00 | 66 | 65
2017-06-09 17:30 | 63 | 61
2017-06-09 18:00 | 60 | 58
2017-06-09 18:30 | 61 | 59
2017-06-09 19:00 | 66 | 65
2017-06-09 19:30 | 68 | 68
2017-06-09 20:00 | 67 | 67
2017-06-09 20:30 | 66 | 66
2017-06-09 21:00 | 67 | 66
2017-06-09 21:30 | 67 | 66
2017-06-09 22:00 | 66 | 65
2017-06-09 22:30 | 63 | 62
2017-06-09 23:00 | 62 | 61
2017-06-09 23:30 | 63 | 62
2017-06-10 | 63 | 61
2017-06-10 00:30 | 63 | 61
2017-06-10 01:00 | 63 | 61
2017-06-10 01:30 | 63 | 61
2017-06-10 02:00 | 63 | 61
2017-06-10 02:30 | 63 | 61
2017-06-10 03:00 | 63 | 60
2017-06-10 03:30 | 63 | 60
2017-06-10 04:00 | 62 | 60
2017-06-10 04:30 | 63 | 61
2017-06-10 05:00 | 64 | 61
2017-06-10 05:30 | 63 | 61
2017-06-10 06:00 | 63 | 60
2017-06-10 06:30 | 62 | 59
2017-06-10 07:00 | 62 | 59
2017-06-10 07:30 | 65 | 63
2017-06-10 08:00 | 66 | 64
2017-06-10 08:30 | 66 | 65
2017-06-10 09:00 | 68 | 66
2017-06-10 09:30 | 69 | 68
2017-06-10 10:00 | 68 | 68
2017-06-10 10:30 | 69 | 68
2017-06-10 11:00 | 68 | 67
2017-06-10 11:30 | 67 | 66
2017-06-10 12:00 | 67 | 66
2017-06-10 12:30 | 67 | 67
2017-06-10 13:00 | 66 | 65
2017-06-10 13:30 | 66 | 65
2017-06-10 14:00 | 66 | 65
2017-06-10 14:30 | 66 | 65
2017-06-10 15:00 | 66 | 66
2017-06-10 15:30 | 67 | 66
2017-06-10 16:00 | 68 | 67
2017-06-10 16:30 | 68 | 68
2017-06-10 17:00 | 69 | 68
2017-06-10 17:30 | 69 | 69
2017-06-10 18:00 | 66 | 65
2017-06-10 18:30 | 67 | 66
2017-06-10 19:00 | 66 | 66
2017-06-10 19:30 | 66 | 66
2017-06-10 20:00 | 66 | 65
2017-06-10 20:30 | 66 | 65
2017-06-10 21:00 | 66 | 65
2017-06-10 21:30 | 66 | 65
2017-06-10 22:00 | 66 | 65
2017-06-10 22:30 | 63 | 62
2017-06-10 23:00 | 62 | 61
2017-06-10 23:30 | 62 | 61
2017-06-11 | 62 | 60
2017-06-11 00:30 | 62 | 60
2017-06-11 01:00 | 63 | 60
2017-06-11 01:30 | 62 | 60
2017-06-11 02:00 | 62 | 60
2017-06-11 02:30 | 62 | 60
2017-06-11 03:00 | 62 | 60
2017-06-11 03:30 | 62 | 59
2017-06-11 04:00 | 61 | 59
2017-06-11 04:30 | 62 | 59
2017-06-11 05:00 | 62 | 59
2017-06-11 05:30 | 62 | 59
2017-06-11 06:00 | 62 | 59
2017-06-11 06:30 | 61 | 59
2017-06-11 07:00 | 61 | 59
2017-06-11 07:30 | 64 | 62
2017-06-11 08:00 | 64 | 62
2017-06-11 08:30 | 65 | 62
2017-06-11 09:00 | 64 | 62
2017-06-11 09:30 | 64 | 62
2017-06-11 10:00 | 65 | 63
2017-06-11 10:30 | 65 | 63
2017-06-11 11:00 | 64 | 62
2017-06-11 11:30 | 64 | 62
2017-06-11 12:00 | 64 | 62
2017-06-11 12:30 | 64 | 62
2017-06-11 13:00 | 64 | 62
2017-06-11 13:30 | 64 | 62
2017-06-11 14:00 | 64 | 62
2017-06-11 14:30 | 65 | 63
2017-06-11 15:00 | 65 | 63
2017-06-11 15:30 | 64 | 62
2017-06-11 16:00 | 65 | 63
2017-06-11 16:30 | 66 | 64
2017-06-11 17:00 | 66 | 65
2017-06-11 17:30 | 67 | 66
2017-06-11 18:00 | 67 | 66
2017-06-11 18:30 | 66 | 66
2017-06-11 19:00 | 67 | 66
2017-06-11 19:30 | 66 | 66
2017-06-11 20:00 | 66 | 65
2017-06-11 20:30 | 65 | 64
2017-06-11 21:00 | 65 | 64
2017-06-11 21:30 | 65 | 64
2017-06-11 22:00 | 64 | 63
2017-06-11 22:30 | 62 | 61
2017-06-11 23:00 | 62 | 61
2017-06-11 23:30 | 62 | 60
2017-06-12 | 62 | 60
2017-06-12 00:30 | 63 | 61
2017-06-12 01:00 | 61 | 60
2017-06-12 01:30 | 61 | 60
2017-06-12 02:00 | 61 | 60
2017-06-12 02:30 | 61 | 60
2017-06-12 03:00 | 61 | 60
2017-06-12 03:30 | 61 | 59
2017-06-12 04:00 | 62 | 60
2017-06-12 04:30 | 62 | 60
2017-06-12 05:00 | 61 | 60
2017-06-12 05:30 | 62 | 61
2017-06-12 06:00 | 62 | 61
2017-06-12 06:30 | 62 | 61
2017-06-12 07:00 | 63 | 62
2017-06-12 07:30 | 66 | 65
2017-06-12 08:00 | 66 | 66
2017-06-12 08:30 | 65 | 65
2017-06-12 09:00 | 65 | 64
2017-06-12 09:30 | 64 | 63
2017-06-12 10:00 | 64 | 63
2017-06-12 10:30 | 63 | 63
2017-06-12 11:00 | 63 | 62
2017-06-12 11:30 | 63 | 62
2017-06-12 12:00 | 63 | 62
2017-06-12 12:30 | 63 | 62
2017-06-12 13:00 | 63 | 62
2017-06-12 13:30 | 63 | 62
2017-06-12 14:00 | 63 | 62
2017-06-12 14:30 | 63 | 62
2017-06-12 15:00 | 64 | 63
2017-06-12 15:30 | 65 | 64
2017-06-12 16:00 | 65 | 64
2017-06-12 16:30 | 66 | 65
2017-06-12 17:00 | 67 | 66
2017-06-12 17:30 | 60 | 58
2017-06-12 18:00 | 59 | 57
2017-06-12 18:30 | 60 | 58
2017-06-12 19:00 | 62 | 60
2017-06-12 19:30 | 66 | 65
2017-06-12 20:00 | 66 | 65
2017-06-12 20:30 | 67 | 66
2017-06-12 21:00 | 66 | 66
2017-06-12 21:30 | 66 | 65
2017-06-12 22:00 | 66 | 65
2017-06-12 22:30 | 64 | 63
2017-06-12 23:00 | 62 | 61
2017-06-12 23:30 | 64 | 62
2017-06-13 | 63 | 62
2017-06-13 00:30 | 63 | 61
2017-06-13 01:00 | 62 | 60
2017-06-13 01:30 | 61 | 60
2017-06-13 02:00 | 61 | 60
2017-06-13 02:30 | 61 | 60
2017-06-13 03:00 | 61 | 60
2017-06-13 03:30 | 60 | 59
2017-06-13 04:00 | 62 | 61
2017-06-13 04:30 | 65 | 64
2017-06-13 05:00 | 65 | 64
2017-06-13 05:30 | 65 | 64
2017-06-13 06:00 | 67 | 66
2017-06-13 06:30 | 69 | 68
2017-06-13 07:00 | 70 | 69
2017-06-13 07:30 | 72 | 70
2017-06-13 08:00 | 73 | 71
2017-06-13 08:30 | 73 | 72
2017-06-13 09:00 | 75 | 74
2017-06-13 09:30 | 76 | 75
2017-06-13 10:00 | 75 | 74
2017-06-13 10:30 | 75 | 74
2017-06-13 11:00 | 75 | 74
2017-06-13 11:30 | 75 | 74
2017-06-13 12:00 | 75 | 74
2017-06-13 12:30 | 75 | 74
2017-06-13 13:00 | 75 | 74
2017-06-13 13:30 | 76 | 75
2017-06-13 14:00 | 76 | 75
2017-06-13 14:30 | 76 | 75
2017-06-13 15:00 | 77 | 75
2017-06-13 15:30 | 78 | 77
2017-06-13 16:00 | 78 | 77
2017-06-13 16:30 | 78 | 77
2017-06-13 17:00 | 75 | 73
2017-06-13 17:30 | 78 | 76
2017-06-13 18:00 | 80 | 79
2017-06-13 18:30 | 81 | 80
2017-06-13 19:00 | 80 | 78
2017-06-13 19:30 | 76 | 74
2017-06-13 20:00 | 76 | 74
2017-06-13 20:30 | 76 | 75
2017-06-13 21:00 | 75 | 73
2017-06-13 21:30 | 74 | 73
2017-06-13 22:00 | 73 | 71
2017-06-13 22:30 | 71 | 69
2017-06-13 23:00 | 69 | 68
2017-06-13 23:30 | 69 | 68
2017-06-14 | 69 | 68
2017-06-14 00:30 | 68 | 67
2017-06-14 01:00 | 69 | 68
2017-06-14 01:30 | 69 | 68
2017-06-14 02:00 | 69 | 68
2017-06-14 02:30 | 69 | 68
2017-06-14 03:00 | 69 | 68
2017-06-14 03:30 | 69 | 68
2017-06-14 04:00 | 69 | 68
2017-06-14 04:30 | 69 | 68
2017-06-14 05:00 | 68 | 68
2017-06-14 05:30 | 68 | 67
2017-06-14 06:00 | 69 | 68
2017-06-14 06:30 | 69 | 68
2017-06-14 07:00 | 74 | 72
2017-06-14 07:30 | 75 | 73
2017-06-14 08:00 | 75 | 73
2017-06-14 08:30 | 75 | 73
2017-06-14 09:00 | 74 | 72
2017-06-14 09:30 | 73 | 71
2017-06-14 10:00 | 72 | 70
2017-06-14 10:30 | 71 | 69
2017-06-14 11:00 | 71 | 69
2017-06-14 11:30 | 71 | 69
2017-06-14 12:00 | 71 | 69
2017-06-14 12:30 | 71 | 70
2017-06-14 13:00 | 72 | 70
2017-06-14 13:30 | 72 | 71
2017-06-14 14:00 | 72 | 71
2017-06-14 14:30 | 73 | 72
2017-06-14 15:00 | 73 | 71
2017-06-14 15:30 | 72 | 71
2017-06-14 16:00 | 72 | 71
2017-06-14 16:30 | 72 | 71
2017-06-14 17:00 | 73 | 72
2017-06-14 17:30 | 75 | 73
2017-06-14 18:00 | 77 | 76
2017-06-14 18:30 | 78 | 76
2017-06-14 19:00 | 78 | 77
2017-06-14 19:30 | 74 | 72
2017-06-14 20:00 | 75 | 73
2017-06-14 20:30 | 76 | 75
2017-06-14 21:00 | 74 | 73
2017-06-14 21:30 | 74 | 72
2017-06-14 22:00 | 72 | 71
2017-06-14 22:30 | 70 | 68
2017-06-14 23:00 | 69 | 68
2017-06-14 23:30 | 68 | 67
2017-06-15 | 68 | 67
2017-06-15 00:30 | 68 | 67
2017-06-15 01:00 | 64 | 62
2017-06-15 01:30 | 64 | 62
2017-06-15 02:00 | 64 | 62
2017-06-15 02:30 | 63 | 62
2017-06-15 03:00 | 62 | 61
2017-06-15 03:30 | 62 | 61
2017-06-15 04:00 | 62 | 61
2017-06-15 04:30 | 62 | 61
2017-06-15 05:00 | 63 | 61
2017-06-15 05:30 | 63 | 62
2017-06-15 06:00 | 63 | 62
2017-06-15 06:30 | 65 | 62
2017-06-15 07:00 | 61 | 60
2017-06-15 07:30 | 66 | 66
2017-06-15 08:00 | 66 | 66
2017-06-15 08:30 | 66 | 65
2017-06-15 09:00 | 65 | 65
2017-06-15 09:30 | 65 | 65
2017-06-15 10:00 | 64 | 64
2017-06-15 10:30 | 65 | 64
2017-06-15 11:00 | 65 | 65
2017-06-15 11:30 | 65 | 64
2017-06-15 12:00 | 65 | 65
2017-06-15 12:30 | 65 | 65
2017-06-15 13:00 | 65 | 65
2017-06-15 13:30 | 65 | 65
2017-06-15 14:00 | 65 | 65
2017-06-15 14:30 | 67 | 67
2017-06-15 15:00 | 69 | 68
2017-06-15 15:30 | 68 | 67
2017-06-15 16:00 | 68 | 67
2017-06-15 16:30 | 70 | 69
2017-06-15 17:00 | 70 | 70
2017-06-15 17:30 | 70 | 70
2017-06-15 18:00 | 69 | 69
2017-06-15 18:30 | 70 | 70
2017-06-15 19:00 | 70 | 70
2017-06-15 19:30 | 70 | 69
2017-06-15 20:00 | 69 | 69
2017-06-15 20:30 | 70 | 69
2017-06-15 21:00 | 70 | 69
2017-06-15 21:30 | 70 | 68
2017-06-15 22:00 | 69 | 68
2017-06-15 22:30 | 65 | 65
2017-06-15 23:00 | 65 | 64
2017-06-15 23:30 | 64 | 63
2017-06-16 | 64 | 63
2017-06-16 00:30 | 64 | 63
2017-06-16 01:00 | 64 | 63
2017-06-16 01:30 | 64 | 63
2017-06-16 02:00 | 64 | 63
2017-06-16 02:30 | 63 | 62
2017-06-16 03:00 | 63 | 62
2017-06-16 03:30 | 62 | 61
2017-06-16 04:00 | 62 | 61
2017-06-16 04:30 | 63 | 62
2017-06-16 05:00 | 62 | 61
2017-06-16 05:30 | 63 | 62
2017-06-16 06:00 | 63 | 62
2017-06-16 06:30 | 63 | 62
2017-06-16 07:00 | 64 | 64
2017-06-16 07:30 | 66 | 66
2017-06-16 08:00 | 66 | 66
2017-06-16 08:30 | 67 | 66
2017-06-16 09:00 | 66 | 65
2017-06-16 09:30 | 66 | 65
2017-06-16 10:00 | 65 | 64
2017-06-16 10:30 | 66 | 65
2017-06-16 11:00 | 65 | 64
2017-06-16 11:30 | 65 | 64
2017-06-16 12:00 | 65 | 65
2017-06-16 12:30 | 70 | 69
2017-06-16 13:00 | 70 | 69
2017-06-16 13:30 | 69 | 68
2017-06-16 14:00 | 70 | 69
2017-06-16 14:30 | 72 | 71
2017-06-16 15:00 | 72 | 71
2017-06-16 15:30 | 73 | 72
2017-06-16 16:00 | 72 | 71
2017-06-16 16:30 | 73 | 72
2017-06-16 17:00 | 73 | 72
2017-06-16 17:30 | 74 | 73
2017-06-16 18:00 | 74 | 74
2017-06-16 18:30 | 75 | 74
2017-06-16 19:00 | 74 | 74
2017-06-16 19:30 | 74 | 73
2017-06-16 20:00 | 73 | 72
2017-06-16 20:30 | 73 | 72
2017-06-16 21:00 | 72 | 71
2017-06-16 21:30 | 72 | 71
2017-06-16 22:00 | 71 | 70
2017-06-16 22:30 | 69 | 67
2017-06-16 23:00 | 68 | 67
2017-06-16 23:30 | 68 | 67
2017-06-17 | 67 | 66
2017-06-17 00:30 | 66 | 65
2017-06-17 01:00 | 65 | 64
2017-06-17 01:30 | 66 | 64
2017-06-17 02:00 | 66 | 65
2017-06-17 02:30 | 65 | 64
2017-06-17 03:00 | 65 | 64
2017-06-17 03:30 | 65 | 64
2017-06-17 04:00 | 65 | 63
2017-06-17 04:30 | 65 | 64
2017-06-17 05:00 | 65 | 64
2017-06-17 05:30 | 65 | 64
2017-06-17 06:00 | 65 | 64
2017-06-17 06:30 | 65 | 64
2017-06-17 07:00 | 65 | 64
2017-06-17 07:30 | 69 | 67
2017-06-17 08:00 | 69 | 68
2017-06-17 08:30 | 69 | 68
2017-06-17 09:00 | 69 | 68
2017-06-17 09:30 | 69 | 68
2017-06-17 10:00 | 69 | 68
2017-06-17 10:30 | 69 | 68
2017-06-17 11:00 | 69 | 68
2017-06-17 11:30 | 68 | 68
2017-06-17 12:00 | 69 | 69
2017-06-17 12:30 | 69 | 69
2017-06-17 13:00 | 70 | 69
2017-06-17 13:30 | 69 | 69
2017-06-17 14:00 | 70 | 69
2017-06-17 14:30 | 70 | 69
2017-06-17 15:00 | 71 | 71
2017-06-17 15:30 | 71 | 71
2017-06-17 16:00 | 72 | 71
2017-06-17 16:30 | 72 | 71
2017-06-17 17:00 | 72 | 71
2017-06-17 17:30 | 73 | 72
2017-06-17 18:00 | 74 | 74
2017-06-17 18:30 | 76 | 75
2017-06-17 19:00 | 75 | 75
2017-06-17 19:30 | 73 | 73
2017-06-17 20:00 | 74 | 73
2017-06-17 20:30 | 72 | 71
2017-06-17 21:00 | 72 | 71
2017-06-17 21:30 | 67 | 65
2017-06-17 22:00 | 67 | 65
2017-06-17 22:30 | 66 | 64
2017-06-17 23:00 | 66 | 64
2017-06-17 23:30 | 69 | 67
2017-06-18 | 66 | 65
2017-06-18 00:30 | 65 | 63
2017-06-18 01:00 | 65 | 63
2017-06-18 01:30 | 61 | 60
2017-06-18 02:00 | 60 | 60
2017-06-18 02:30 | 59 | 59
2017-06-18 03:00 | 60 | 60
2017-06-18 03:30 | 63 | 63
2017-06-18 04:00 | 61 | 60
2017-06-18 04:30 | 43 | 43
2017-06-18 05:00 | 45 | 44
2017-06-18 05:30 | 54 | 54
2017-06-18 06:00 | 64 | 64
2017-06-18 06:30 | 64 | 63
2017-06-18 07:00 | 65 | 65
2017-06-18 07:30 | 68 | 68
2017-06-18 08:00 | 69 | 68
2017-06-18 08:30 | 69 | 68
2017-06-18 09:00 | 68 | 68
2017-06-18 09:30 | 69 | 68
2017-06-18 10:00 | 71 | 70
2017-06-18 10:30 | 68 | 67
2017-06-18 11:00 | 68 | 68
2017-06-18 11:30 | 68 | 67
2017-06-18 12:00 | 68 | 67
2017-06-18 12:30 | 68 | 67
2017-06-18 13:00 | 69 | 68
2017-06-18 13:30 | 69 | 68
2017-06-18 14:00 | 70 | 69
2017-06-18 14:30 | 71 | 70
2017-06-18 15:00 | 71 | 70
2017-06-18 15:30 | 71 | 70
2017-06-18 16:00 | 71 | 71
2017-06-18 16:30 | 73 | 72
2017-06-18 17:00 | 72 | 72
2017-06-18 17:30 | 72 | 72
2017-06-18 18:00 | 72 | 72
2017-06-18 18:30 | 73 | 72
2017-06-18 19:00 | 74 | 74
2017-06-18 19:30 | 74 | 73
2017-06-18 20:00 | 73 | 73
2017-06-18 20:30 | 73 | 73
2017-06-18 21:00 | 73 | 73
2017-06-18 21:30 | 72 | 72
2017-06-18 22:00 | 71 | 70
2017-06-18 22:30 | 71 | 70
2017-06-18 23:00 | 71 | 70
2017-06-18 23:30 | 70 | 70
2017-06-19 | 68 | 67
2017-06-19 00:30 | 67 | 66
2017-06-19 01:00 | 67 | 66
2017-06-19 01:30 | 67 | 66
2017-06-19 02:00 | 67 | 66
2017-06-19 02:30 | 68 | 67
2017-06-19 03:00 | 67 | 66
2017-06-19 03:30 | 67 | 66
2017-06-19 04:00 | 68 | 67
2017-06-19 04:30 | 69 | 68
2017-06-19 05:00 | 72 | 71
2017-06-19 05:30 | 72 | 71
2017-06-19 06:00 | 72 | 71
2017-06-19 06:30 | 75 | 74
2017-06-19 07:00 | 76 | 75
2017-06-19 07:30 | 77 | 76
2017-06-19 08:00 | 75 | 75
2017-06-19 08:30 | 73 | 72
2017-06-19 09:00 | 75 | 74
2017-06-19 09:30 | 78 | 78
2017-06-19 10:00 | 70 | 70
2017-06-19 10:30 | 70 | 69
2017-06-19 11:00 | 70 | 69
2017-06-19 11:30 | 69 | 69
2017-06-19 12:00 | 71 | 71
2017-06-19 12:30 | 71 | 70
2017-06-19 13:00 | 72 | 72
2017-06-19 13:30 | 72 | 71
2017-06-19 14:00 | 71 | 71
2017-06-19 14:30 | 73 | 72
2017-06-19 15:00 | 74 | 73
2017-06-19 15:30 | 77 | 76
2017-06-19 16:00 | 78 | 77
2017-06-19 16:30 | 79 | 79
2017-06-19 17:00 | 80 | 80
2017-06-19 17:30 | 80 | 80
2017-06-19 18:00 | 80 | 80
2017-06-19 18:30 | 82 | 81
2017-06-19 19:00 | 80 | 79
2017-06-19 19:30 | 80 | 79
2017-06-19 20:00 | 79 | 79
2017-06-19 20:30 | 79 | 78
2017-06-19 21:00 | 79 | 78
2017-06-19 21:30 | 78 | 77
2017-06-19 22:00 | 76 | 75
2017-06-19 22:30 | 75 | 73
2017-06-19 23:00 | 70 | 70
2017-06-19 23:30 | 69 | 68
2017-06-20 | 68 | 68
2017-06-20 00:30 | 65 | 64
2017-06-20 01:00 | 66 | 65
2017-06-20 01:30 | 66 | 65
2017-06-20 02:00 | 66 | 65
2017-06-20 02:30 | 67 | 66
2017-06-20 03:00 | 67 | 67
2017-06-20 03:30 | 67 | 67
2017-06-20 04:00 | 67 | 67
2017-06-20 04:30 | 68 | 67
2017-06-20 05:00 | 67 | 66
2017-06-20 05:30 | 67 | 66
2017-06-20 06:00 | 68 | 67
2017-06-20 06:30 | 69 | 67
2017-06-20 07:00 | 70 | 69
2017-06-20 07:30 | 72 | 71
2017-06-20 08:00 | 71 | 70
2017-06-20 08:30 | 70 | 69
2017-06-20 09:00 | 70 | 70
2017-06-20 09:30 | 69 | 68
2017-06-20 10:00 | 70 | 69
2017-06-20 10:30 | 69 | 69
2017-06-20 11:00 | 69 | 68
2017-06-20 11:30 | 68 | 68
2017-06-20 12:00 | 69 | 69
2017-06-20 12:30 | 68 | 68
2017-06-20 13:00 | 69 | 68
2017-06-20 13:30 | 64 | 63
2017-06-20 14:00 | 48 | 46
2017-06-20 14:30 | 39 | 39
2017-06-20 15:00 | 37 | 37
2017-06-20 15:30 | 40 | 40
2017-06-20 16:00 | 41 | 41
2017-06-20 16:30 | 43 | 42
2017-06-20 17:00 | 43 | 43
2017-06-20 17:30 | 44 | 43
2017-06-20 18:00 | 43 | 42
2017-06-20 18:30 | 45 | 45
2017-06-20 19:00 | 46 | 46
2017-06-20 19:30 | 45 | 44
2017-06-20 20:00 | 44 | 43
2017-06-20 20:30 | 45 | 44
2017-06-20 21:00 | 49 | 48
2017-06-20 21:30 | 54 | 54
2017-06-20 22:00 | 52 | 52
2017-06-20 22:30 | 51 | 50
2017-06-20 23:00 | 50 | 50
2017-06-20 23:30 | 41 | 41
2017-06-21 | 40 | 40
2017-06-21 00:30 | 42 | 42
2017-06-21 01:00 | 40 | 40
2017-06-21 01:30 | 40 | 40
2017-06-21 02:00 | 41 | 41
2017-06-21 02:30 | 34 | 32
2017-06-21 03:00 | 32 | 29
2017-06-21 03:30 | 30 | 26
2017-06-21 04:00 | 30 | 26
2017-06-21 04:30 | 36 | 35
2017-06-21 05:00 | 48 | 48
2017-06-21 05:30 | 59 | 58
2017-06-21 06:00 | 62 | 60
2017-06-21 06:30 | 64 | 61
2017-06-21 07:00 | 63 | 61
2017-06-21 07:30 | 64 | 62
2017-06-21 08:00 | 67 | 64
2017-06-21 08:30 | 67 | 64
2017-06-21 09:00 | 66 | 63
2017-06-21 09:30 | 65 | 61
2017-06-21 10:00 | 63 | 60
2017-06-21 10:30 | 64 | 61
2017-06-21 11:00 | 64 | 61
2017-06-21 11:30 | 64 | 61
2017-06-21 12:00 | 65 | 61
2017-06-21 12:30 | 65 | 61
2017-06-21 13:00 | 65 | 62
2017-06-21 13:30 | 65 | 62
2017-06-21 14:00 | 66 | 62
2017-06-21 14:30 | 67 | 63
2017-06-21 15:00 | 68 | 65
2017-06-21 15:30 | 69 | 66
2017-06-21 16:00 | 71 | 68
2017-06-21 16:30 | 73 | 70
2017-06-21 17:00 | 71 | 68
2017-06-21 17:30 | 70 | 67
2017-06-21 18:00 | 70 | 66
2017-06-21 18:30 | 74 | 70
2017-06-21 19:00 | 75 | 71
2017-06-21 19:30 | 74 | 70
2017-06-21 20:00 | 74 | 71
2017-06-21 20:30 | 73 | 69
2017-06-21 21:00 | 72 | 69
2017-06-21 21:30 | 72 | 69
2017-06-21 22:00 | 69 | 66
2017-06-21 22:30 | 67 | 63
2017-06-21 23:00 | 65 | 63
2017-06-21 23:30 | 65 | 63
2017-06-22 | 66 | 64
2017-06-22 00:30 | 65 | 64
2017-06-22 01:00 | 64 | 63
2017-06-22 01:30 | 63 | 62
2017-06-22 02:00 | 63 | 61
2017-06-22 02:30 | 62 | 61
2017-06-22 03:00 | 64 | 63
2017-06-22 03:30 | 63 | 62
2017-06-22 04:00 | 63 | 61
2017-06-22 04:30 | 63 | 62
2017-06-22 05:00 | 62 | 61
2017-06-22 05:30 | 62 | 61
2017-06-22 06:00 | 63 | 62
2017-06-22 06:30 | 65 | 63
2017-06-22 07:00 | 67 | 65
2017-06-22 07:30 | 69 | 67
2017-06-22 08:00 | 70 | 67
2017-06-22 08:30 | 69 | 67
2017-06-22 09:00 | 93 | 92
2017-06-22 09:30 | 92 | 91
2017-06-22 10:00 | 92 | 92
2017-06-22 10:30 | 95 | 94
2017-06-22 11:00 | 96 | 95
2017-06-22 11:30 | 98 | 98
2017-06-22 12:00 | 101 | 99
2017-06-22 12:30 | 101 | 99
2017-06-22 13:00 | 78 | 76
2017-06-22 13:30 | 70 | 69
2017-06-22 14:00 | 68 | 66
2017-06-22 14:30 | 68 | 66
2017-06-22 15:00 | 68 | 67
2017-06-22 15:30 | 69 | 67
2017-06-22 16:00 | 71 | 70
2017-06-22 16:30 | 72 | 72
2017-06-22 17:00 | 72 | 71
2017-06-22 17:30 | 72 | 71
2017-06-22 18:00 | 73 | 72
2017-06-22 18:30 | 74 | 74
2017-06-22 19:00 | 75 | 74
2017-06-22 19:30 | 75 | 75
2017-06-22 20:00 | 75 | 74
2017-06-22 20:30 | 70 | 69
2017-06-22 21:00 | 66 | 66
2017-06-22 21:30 | 66 | 65
2017-06-22 22:00 | 65 | 63
2017-06-22 22:30 | 66 | 64
2017-06-22 23:00 | 64 | 63
2017-06-22 23:30 | 65 | 63
2017-06-23 | 63 | 62
2017-06-23 00:30 | 62 | 61
2017-06-23 01:00 | 62 | 61
2017-06-23 01:30 | 62 | 61
2017-06-23 02:00 | 61 | 60
2017-06-23 02:30 | 61 | 60
2017-06-23 03:00 | 59 | 58
2017-06-23 03:30 | 60 | 58
2017-06-23 04:00 | 61 | 60
2017-06-23 04:30 | 61 | 59
2017-06-23 05:00 | 60 | 59
2017-06-23 05:30 | 60 | 59
2017-06-23 06:00 | 62 | 61
2017-06-23 06:30 | 63 | 62
2017-06-23 07:00 | 62 | 61
2017-06-23 07:30 | 65 | 65
2017-06-23 08:00 | 67 | 66
2017-06-23 08:30 | 65 | 65
2017-06-23 09:00 | 64 | 63
2017-06-23 09:30 | 64 | 63
2017-06-23 10:00 | 62 | 62
2017-06-23 10:30 | 62 | 62
2017-06-23 11:00 | 61 | 61
2017-06-23 11:30 | 62 | 62
2017-06-23 12:00 | 63 | 63
2017-06-23 12:30 | 61 | 61
2017-06-23 13:00 | 63 | 63
2017-06-23 13:30 | 62 | 62
2017-06-23 14:00 | 63 | 63
2017-06-23 14:30 | 64 | 64
2017-06-23 15:00 | 64 | 64
2017-06-23 15:30 | 65 | 64
2017-06-23 16:00 | 65 | 65
2017-06-23 16:30 | 64 | 64
2017-06-23 17:00 | 65 | 65
2017-06-23 17:30 | 66 | 66
2017-06-23 18:00 | 66 | 66
2017-06-23 18:30 | 66 | 66
2017-06-23 19:00 | 67 | 67
2017-06-23 19:30 | 67 | 67
2017-06-23 20:00 | 66 | 66
2017-06-23 20:30 | 66 | 65
2017-06-23 21:00 | 65 | 65
2017-06-23 21:30 | 65 | 65
2017-06-23 22:00 | 65 | 64
2017-06-23 22:30 | 62 | 61
2017-06-23 23:00 | 62 | 61
2017-06-23 23:30 | 64 | 63
2017-06-24 | 62 | 61
2017-06-24 00:30 | 61 | 60
2017-06-24 01:00 | 61 | 60
2017-06-24 01:30 | 62 | 61
2017-06-24 02:00 | 60 | 59
2017-06-24 02:30 | 60 | 58
2017-06-24 03:00 | 59 | 59
2017-06-24 03:30 | 58 | 57
2017-06-24 04:00 | 57 | 56
2017-06-24 04:30 | 59 | 58
2017-06-24 05:00 | 59 | 57
2017-06-24 05:30 | 59 | 58
2017-06-24 06:00 | 58 | 57
2017-06-24 06:30 | 59 | 58
2017-06-24 07:00 | 60 | 59
2017-06-24 07:30 | 62 | 61
2017-06-24 08:00 | 62 | 61
2017-06-24 08:30 | 63 | 62
2017-06-24 09:00 | 63 | 62
2017-06-24 09:30 | 64 | 62
2017-06-24 10:00 | 60 | 60
2017-06-24 10:30 | 62 | 62
2017-06-24 11:00 | 62 | 62
2017-06-24 11:30 | 61 | 60
2017-06-24 12:00 | 61 | 61
2017-06-24 12:30 | 60 | 60
2017-06-24 13:00 | 59 | 58
2017-06-24 13:30 | 60 | 59
2017-06-24 14:00 | 61 | 60
2017-06-24 14:30 | 63 | 62
2017-06-24 15:00 | 62 | 62
2017-06-24 15:30 | 62 | 61
2017-06-24 16:00 | 63 | 62
2017-06-24 16:30 | 64 | 63
2017-06-24 17:00 | 65 | 65
2017-06-24 17:30 | 66 | 66
2017-06-24 18:00 | 64 | 64
2017-06-24 18:30 | 66 | 66
2017-06-24 19:00 | 65 | 64
2017-06-24 19:30 | 64 | 63
2017-06-24 20:00 | 62 | 62
2017-06-24 20:30 | 61 | 61
2017-06-24 21:00 | 61 | 60
2017-06-24 21:30 | 60 | 59
2017-06-24 22:00 | 55 | 54
2017-06-24 22:30 | 54 | 53
2017-06-24 23:00 | 55 | 53
2017-06-24 23:30 | 54 | 53
2017-06-25 | 53 | 52
2017-06-25 00:30 | 52 | 50
2017-06-25 01:00 | 52 | 50
2017-06-25 01:30 | 52 | 50
2017-06-25 02:00 | 51 | 49
2017-06-25 02:30 | 52 | 50
2017-06-25 03:00 | 52 | 50
2017-06-25 03:30 | 51 | 49
2017-06-25 04:00 | 51 | 49
2017-06-25 04:30 | 51 | 50
2017-06-25 05:00 | 52 | 51
2017-06-25 05:30 | 52 | 50
2017-06-25 06:00 | 51 | 49
2017-06-25 06:30 | 50 | 49
2017-06-25 07:00 | 53 | 51
2017-06-25 07:30 | 53 | 52
2017-06-25 08:00 | 53 | 52
2017-06-25 08:30 | 56 | 55
2017-06-25 09:00 | 58 | 57
2017-06-25 09:30 | 59 | 57
2017-06-25 10:00 | 58 | 57
2017-06-25 10:30 | 58 | 57
2017-06-25 11:00 | 58 | 57
2017-06-25 11:30 | 58 | 56
2017-06-25 12:00 | 58 | 57
2017-06-25 12:30 | 59 | 58
2017-06-25 13:00 | 58 | 57
2017-06-25 13:30 | 59 | 58
2017-06-25 14:00 | 58 | 57
2017-06-25 14:30 | 59 | 57
2017-06-25 15:00 | 59 | 58
2017-06-25 15:30 | 60 | 59
2017-06-25 16:00 | 60 | 59
2017-06-25 16:30 | 61 | 60
2017-06-25 17:00 | 61 | 60
2017-06-25 17:30 | 60 | 59
2017-06-25 18:00 | 58 | 58
2017-06-25 18:30 | 60 | 60
2017-06-25 19:00 | 59 | 59
2017-06-25 19:30 | 59 | 59
2017-06-25 20:00 | 60 | 59
2017-06-25 20:30 | 58 | 58
2017-06-25 21:00 | 58 | 57
2017-06-25 21:30 | 58 | 57
2017-06-25 22:00 | 57 | 57
2017-06-25 22:30 | 56 | 55
2017-06-25 23:00 | 55 | 53
2017-06-25 23:30 | 55 | 53
2017-06-26 | 55 | 53
2017-06-26 00:30 | 54 | 53
2017-06-26 01:00 | 54 | 52
2017-06-26 01:30 | 54 | 52
2017-06-26 02:00 | 53 | 52
2017-06-26 02:30 | 52 | 50
2017-06-26 03:00 | 50 | 48
2017-06-26 03:30 | 50 | 48
2017-06-26 04:00 | 51 | 50
2017-06-26 04:30 | 51 | 49
2017-06-26 05:00 | 50 | 49
2017-06-26 05:30 | 52 | 51
2017-06-26 06:00 | 52 | 51
2017-06-26 06:30 | 51 | 50
2017-06-26 07:00 | 51 | 50
2017-06-26 07:30 | 53 | 52
2017-06-26 08:00 | 55 | 54
2017-06-26 08:30 | 51 | 50
2017-06-26 09:00 | 49 | 49
2017-06-26 09:30 | 49 | 49
2017-06-26 10:00 | 50 | 50
2017-06-26 10:30 | 50 | 50
2017-06-26 11:00 | 49 | 49
2017-06-26 11:30 | 49 | 49
2017-06-26 12:00 | 50 | 50
2017-06-26 12:30 | 51 | 51
2017-06-26 13:00 | 51 | 51
2017-06-26 13:30 | 52 | 52
2017-06-26 14:00 | 53 | 53
2017-06-26 14:30 | 54 | 54
2017-06-26 15:00 | 53 | 53
2017-06-26 15:30 | 56 | 56
2017-06-26 16:00 | 55 | 55
2017-06-26 16:30 | 54 | 53
2017-06-26 17:00 | 54 | 54
2017-06-26 17:30 | 55 | 54
2017-06-26 18:00 | 56 | 56
2017-06-26 18:30 | 57 | 57
2017-06-26 19:00 | 57 | 57
2017-06-26 19:30 | 57 | 57
2017-06-26 20:00 | 56 | 56
2017-06-26 20:30 | 55 | 54
2017-06-26 21:00 | 54 | 54
2017-06-26 21:30 | 54 | 54
2017-06-26 22:00 | 53 | 53
2017-06-26 22:30 | 52 | 52
2017-06-26 23:00 | 49 | 48
2017-06-26 23:30 | 48 | 48
2017-06-27 | 48 | 48
2017-06-27 00:30 | 48 | 47
2017-06-27 01:00 | 46 | 45
2017-06-27 01:30 | 46 | 45
2017-06-27 02:00 | 45 | 44
2017-06-27 02:30 | 46 | 45
2017-06-27 03:00 | 47 | 46
2017-06-27 03:30 | 49 | 48
2017-06-27 04:00 | 48 | 47
2017-06-27 04:30 | 49 | 48
2017-06-27 05:00 | 52 | 50
2017-06-27 05:30 | 53 | 52
2017-06-27 06:00 | 54 | 53
2017-06-27 06:30 | 56 | 55
2017-06-27 07:00 | 55 | 53
2017-06-27 07:30 | 57 | 56
2017-06-27 08:00 | 56 | 55
2017-06-27 08:30 | 59 | 58
2017-06-27 09:00 | 62 | 61
2017-06-27 09:30 | 59 | 58
2017-06-27 10:00 | 59 | 59
2017-06-27 10:30 | 61 | 60
2017-06-27 11:00 | 60 | 60
2017-06-27 11:30 | 61 | 61
2017-06-27 12:00 | 53 | 52
2017-06-27 12:30 | 59 | 59
2017-06-27 13:00 | 58 | 58
2017-06-27 13:30 | 59 | 59
2017-06-27 14:00 | 59 | 58
2017-06-27 14:30 | 59 | 59
2017-06-27 15:00 | 56 | 56
2017-06-27 15:30 | 58 | 57
2017-06-27 16:00 | 58 | 57
2017-06-27 16:30 | 57 | 56
2017-06-27 17:00 | 61 | 61
2017-06-27 17:30 | 63 | 63
2017-06-27 18:00 | 57 | 52
2017-06-27 18:30 | 58 | 54
2017-06-27 19:00 | 57 | 53
2017-06-27 19:30 | 51 | 46
2017-06-27 20:00 | 49 | 44
2017-06-27 20:30 | 47 | 43
2017-06-27 21:00 | 43 | 43
2017-06-27 21:30 | 42 | 42
2017-06-27 22:00 | 43 | 43
2017-06-27 22:30 | 35 | 35
2017-06-27 23:00 | 32 | 32
2017-06-27 23:30 | 42 | 41
2017-06-28 | 52 | 51
2017-06-28 00:30 | 51 | 50
2017-06-28 01:00 | 50 | 49
2017-06-28 01:30 | 43 | 43
2017-06-28 02:00 | 44 | 44
2017-06-28 02:30 | 48 | 48
2017-06-28 03:00 | 49 | 49
2017-06-28 03:30 | 51 | 50
2017-06-28 04:00 | 52 | 52
2017-06-28 04:30 | 56 | 55
2017-06-28 05:00 | 59 | 58
2017-06-28 05:30 | 61 | 60
2017-06-28 06:00 | 61 | 60
2017-06-28 06:30 | 57 | 56
2017-06-28 07:00 | 55 | 53
2017-06-28 07:30 | 57 | 56
2017-06-28 08:00 | 59 | 57
2017-06-28 08:30 | 60 | 59
2017-06-28 09:00 | 59 | 57
2017-06-28 09:30 | 58 | 56
2017-06-28 10:00 | 60 | 58
2017-06-28 10:30 | 60 | 58
2017-06-28 11:00 | 59 | 57
2017-06-28 11:30 | 61 | 58
2017-06-28 12:00 | 61 | 59
2017-06-28 12:30 | 61 | 58
2017-06-28 13:00 | 65 | 62
2017-06-28 13:30 | 64 | 63
2017-06-28 14:00 | 65 | 63
2017-06-28 14:30 | 67 | 65
2017-06-28 15:00 | 65 | 63
2017-06-28 15:30 | 66 | 64
2017-06-28 16:00 | 63 | 62
2017-06-28 16:30 | 59 | 58
2017-06-28 17:00 | 57 | 57
2017-06-28 17:30 | 46 | 46
2017-06-28 18:00 | 44 | 43
2017-06-28 18:30 | 45 | 44
2017-06-28 19:00 | 45 | 44
2017-06-28 19:30 | 50 | 50
2017-06-28 20:00 | 60 | 60
2017-06-28 20:30 | 58 | 58
2017-06-28 21:00 | 54 | 53
2017-06-28 21:30 | 53 | 53
2017-06-28 22:00 | 53 | 53
2017-06-28 22:30 | 51 | 51
2017-06-28 23:00 | 50 | 50
2017-06-28 23:30 | 50 | 50
2017-06-29 | 50 | 50
2017-06-29 00:30 | 49 | 49
2017-06-29 01:00 | 44 | 44
2017-06-29 01:30 | 44 | 44
2017-06-29 02:00 | 45 | 45
2017-06-29 02:30 | 44 | 44
2017-06-29 03:00 | 44 | 44
2017-06-29 03:30 | 43 | 43
2017-06-29 04:00 | 43 | 43
2017-06-29 04:30 | 43 | 43
2017-06-29 05:00 | 44 | 44
2017-06-29 05:30 | 45 | 44
2017-06-29 06:00 | 43 | 43
2017-06-29 06:30 | 42 | 42
2017-06-29 07:00 | 44 | 44
2017-06-29 07:30 | 48 | 47
2017-06-29 08:00 | 43 | 43
2017-06-29 08:30 | 49 | 46
2017-06-29 09:00 | 48 | 46
2017-06-29 09:30 | 48 | 46
2017-06-29 10:00 | 53 | 51
2017-06-29 10:30 | 52 | 50
2017-06-29 11:00 | 52 | 50
2017-06-29 11:30 | 52 | 50
2017-06-29 12:00 | 51 | 48
2017-06-29 12:30 | 50 | 48
2017-06-29 13:00 | 51 | 48
2017-06-29 13:30 | 52 | 50
2017-06-29 14:00 | 55 | 53
2017-06-29 14:30 | 54 | 52
2017-06-29 15:00 | 54 | 52
2017-06-29 15:30 | 55 | 53
2017-06-29 16:00 | 54 | 52
2017-06-29 16:30 | 55 | 53
2017-06-29 17:00 | 52 | 47
2017-06-29 17:30 | 47 | 35
2017-06-29 18:00 | 48 | 35
2017-06-29 18:30 | 47 | 35
2017-06-29 19:00 | 54 | 50
2017-06-29 19:30 | 57 | 54
2017-06-29 20:00 | 56 | 53
2017-06-29 20:30 | 55 | 52
2017-06-29 21:00 | 55 | 52
2017-06-29 21:30 | 56 | 51
2017-06-29 22:00 | 54 | 50
2017-06-29 22:30 | 53 | 50
2017-06-29 23:00 | 50 | 49
2017-06-29 23:30 | 48 | 46
2017-06-30 | 46 | 44
2017-06-30 00:30 | 45 | 45
2017-06-30 01:00 | 48 | 46
2017-06-30 01:30 | 47 | 46
2017-06-30 02:00 | 47 | 45
2017-06-30 02:30 | 48 | 46
2017-06-30 03:00 | 48 | 47
2017-06-30 03:30 | 47 | 45
2017-06-30 04:00 | 47 | 45
2017-06-30 04:30 | 47 | 45
2017-06-30 05:00 | 47 | 45
2017-06-30 05:30 | 47 | 45
2017-06-30 06:00 | 48 | 46
2017-06-30 06:30 | 50 | 47
2017-06-30 07:00 | 31 | 31
2017-06-30 07:30 | 31 | 31
2017-06-30 08:00 | 30 | 30
2017-06-30 08:30 | 31 | 31
2017-06-30 09:00 | 50 | 49
2017-06-30 09:30 | 51 | 51
2017-06-30 10:00 | 51 | 50
2017-06-30 10:30 | 50 | 49
2017-06-30 11:00 | 49 | 48
2017-06-30 11:30 | 51 | 50
2017-06-30 12:00 | 53 | 52
2017-06-30 12:30 | 52 | 52
2017-06-30 13:00 | 52 | 52
2017-06-30 13:30 | 51 | 51
2017-06-30 14:00 | 52 | 51
2017-06-30 14:30 | 53 | 52
2017-06-30 15:00 | 53 | 52
2017-06-30 15:30 | 53 | 53
2017-06-30 16:00 | 53 | 53
2017-06-30 16:30 | 53 | 53
2017-06-30 17:00 | 53 | 53
2017-06-30 17:30 | 53 | 53
2017-06-30 18:00 | 45 | 44
2017-06-30 18:30 | 43 | 43
2017-06-30 19:00 | 54 | 54
2017-06-30 19:30 | 56 | 55
2017-06-30 20:00 | 55 | 54
2017-06-30 20:30 | 54 | 54
2017-06-30 21:00 | 54 | 53
2017-06-30 21:30 | 53 | 52
2017-06-30 22:00 | 54 | 52
2017-06-30 22:30 | 51 | 50
2017-06-30 23:00 | 49 | 46
2017-06-30 23:30 | 48 | 46
2017-07-01 | 47 | 46
2017-07-01 00:30 | 47 | 45
2017-07-01 01:00 | 45 | 44
2017-07-01 01:30 | 45 | 43
2017-07-01 02:00 | 46 | 44
2017-07-01 02:30 | 45 | 44
2017-07-01 03:00 | 44 | 42
2017-07-01 03:30 | 43 | 42
2017-07-01 04:00 | 45 | 43
2017-07-01 04:30 | 45 | 44
2017-07-01 05:00 | 45 | 42
2017-07-01 05:30 | 46 | 44
2017-07-01 06:00 | 46 | 44
2017-07-01 06:30 | 46 | 44
2017-07-01 07:00 | 47 | 45
2017-07-01 07:30 | 50 | 49
2017-07-01 08:00 | 51 | 49
2017-07-01 08:30 | 50 | 49
2017-07-01 09:00 | 49 | 48
2017-07-01 09:30 | 48 | 47
2017-07-01 10:00 | 46 | 45
2017-07-01 10:30 | 47 | 46
2017-07-01 11:00 | 48 | 47
2017-07-01 11:30 | 48 | 47
2017-07-01 12:00 | 49 | 48
2017-07-01 12:30 | 51 | 50
2017-07-01 13:00 | 50 | 49
2017-07-01 13:30 | 50 | 49
2017-07-01 14:00 | 48 | 48
2017-07-01 14:30 | 47 | 47
2017-07-01 15:00 | 48 | 47
2017-07-01 15:30 | 47 | 46
2017-07-01 16:00 | 50 | 50
2017-07-01 16:30 | 51 | 50
2017-07-01 17:00 | 50 | 49
2017-07-01 17:30 | 51 | 50
2017-07-01 18:00 | 52 | 51
2017-07-01 18:30 | 44 | 44
2017-07-01 19:00 | 50 | 50
2017-07-01 19:30 | 52 | 51
2017-07-01 20:00 | 52 | 52
2017-07-01 20:30 | 50 | 50
2017-07-01 21:00 | 50 | 50
2017-07-01 21:30 | 50 | 50
2017-07-01 22:00 | 48 | 48
2017-07-01 22:30 | 46 | 45
2017-07-01 23:00 | 44 | 43
2017-07-01 23:30 | 46 | 44
2017-07-02 | 46 | 44
2017-07-02 00:30 | 45 | 43
2017-07-02 01:00 | 46 | 44
2017-07-02 01:30 | 46 | 45
2017-07-02 02:00 | 45 | 43
2017-07-02 02:30 | 44 | 42
2017-07-02 03:00 | 43 | 42
2017-07-02 03:30 | 45 | 43
2017-07-02 04:00 | 45 | 43
2017-07-02 04:30 | 44 | 43
2017-07-02 05:00 | 46 | 44
2017-07-02 05:30 | 45 | 44
2017-07-02 06:00 | 46 | 44
2017-07-02 06:30 | 48 | 47
2017-07-02 07:00 | 49 | 47
2017-07-02 07:30 | 49 | 48
2017-07-02 08:00 | 49 | 48
2017-07-02 08:30 | 51 | 50
2017-07-02 09:00 | 52 | 50
2017-07-02 09:30 | 53 | 52
2017-07-02 10:00 | 52 | 51
2017-07-02 10:30 | 49 | 48
2017-07-02 11:00 | 48 | 47
2017-07-02 11:30 | 47 | 46
2017-07-02 12:00 | 47 | 46
2017-07-02 12:30 | 47 | 45
2017-07-02 13:00 | 46 | 45
2017-07-02 13:30 | 46 | 45
2017-07-02 14:00 | 46 | 44
2017-07-02 14:30 | 45 | 44
2017-07-02 15:00 | 49 | 48
2017-07-02 15:30 | 47 | 46
2017-07-02 16:00 | 48 | 47
2017-07-02 16:30 | 47 | 46
2017-07-02 17:00 | 47 | 46
2017-07-02 17:30 | 47 | 46
2017-07-02 18:00 | 40 | 39
2017-07-02 18:30 | 41 | 41
2017-07-02 19:00 | 46 | 45
2017-07-02 19:30 | 48 | 46
2017-07-02 20:00 | 48 | 47
2017-07-02 20:30 | 48 | 46
2017-07-02 21:00 | 47 | 46
2017-07-02 21:30 | 47 | 45
2017-07-02 22:00 | 48 | 46
2017-07-02 22:30 | 47 | 45
2017-07-02 23:00 | 46 | 44
2017-07-02 23:30 | 45 | 42
2017-07-03 | 44 | 41
2017-07-03 00:30 | 41 | 40
2017-07-03 01:00 | 43 | 42
2017-07-03 01:30 | 42 | 41
2017-07-03 02:00 | 41 | 40
2017-07-03 02:30 | 42 | 40
2017-07-03 03:00 | 42 | 41
2017-07-03 03:30 | 42 | 41
2017-07-03 04:00 | 41 | 40
2017-07-03 04:30 | 42 | 41
2017-07-03 05:00 | 43 | 42
2017-07-03 05:30 | 44 | 43
2017-07-03 06:00 | 42 | 41
2017-07-03 06:30 | 44 | 43
2017-07-03 07:00 | 45 | 44
2017-07-03 07:30 | 44 | 44
2017-07-03 08:00 | 44 | 44
2017-07-03 08:30 | 30 | 30
2017-07-03 09:00 | 39 | 39
2017-07-03 09:30 | 28 | 28
2017-07-03 10:00 | 40 | 40
2017-07-03 10:30 | 44 | 43
2017-07-03 11:00 | 44 | 43
2017-07-03 11:30 | 45 | 44
2017-07-03 12:00 | 46 | 45
2017-07-03 12:30 | 48 | 47
2017-07-03 13:00 | 51 | 51
2017-07-03 13:30 | 52 | 52
2017-07-03 14:00 | 51 | 50
2017-07-03 14:30 | 51 | 51
2017-07-03 15:00 | 51 | 50
2017-07-03 15:30 | 50 | 50
2017-07-03 16:00 | 50 | 49
2017-07-03 16:30 | 50 | 50
2017-07-03 17:00 | 52 | 52
2017-07-03 17:30 | 52 | 52
2017-07-03 18:00 | 46 | 46
2017-07-03 18:30 | 52 | 48
2017-07-03 19:00 | 53 | 49
2017-07-03 19:30 | 53 | 50
2017-07-03 20:00 | 53 | 49
2017-07-03 20:30 | 52 | 48
2017-07-03 21:00 | 53 | 48
2017-07-03 21:30 | 52 | 47
2017-07-03 22:00 | 48 | 45
2017-07-03 22:30 | 48 | 44
2017-07-03 23:00 | 48 | 44
2017-07-03 23:30 | 47 | 43
2017-07-04 | 46 | 42
2017-07-04 00:30 | 46 | 41
2017-07-04 01:00 | 42 | 42
2017-07-04 01:30 | 42 | 41
2017-07-04 02:00 | 41 | 39
2017-07-04 02:30 | 42 | 41
2017-07-04 03:00 | 44 | 42
2017-07-04 03:30 | 44 | 43
2017-07-04 04:00 | 44 | 43
2017-07-04 04:30 | 47 | 46
2017-07-04 05:00 | 47 | 46
2017-07-04 05:30 | 47 | 46
2017-07-04 06:00 | 47 | 46
2017-07-04 06:30 | 48 | 48
2017-07-04 07:00 | 49 | 49
2017-07-04 07:30 | 49 | 49
2017-07-04 08:00 | 50 | 50
2017-07-04 08:30 | 50 | 49
2017-07-04 09:00 | 50 | 49
2017-07-04 09:30 | 50 | 49
2017-07-04 10:00 | 50 | 49
2017-07-04 10:30 | 51 | 50
2017-07-04 11:00 | 54 | 53
2017-07-04 11:30 | 56 | 55
2017-07-04 12:00 | 56 | 55
2017-07-04 12:30 | 55 | 54
2017-07-04 13:00 | 56 | 55
2017-07-04 13:30 | 56 | 55
2017-07-04 14:00 | 56 | 55
2017-07-04 14:30 | 58 | 58
2017-07-04 15:00 | 58 | 58
2017-07-04 15:30 | 58 | 58
2017-07-04 16:00 | 58 | 57
2017-07-04 16:30 | 58 | 57
2017-07-04 17:00 | 59 | 59
2017-07-04 17:30 | 63 | 63
2017-07-04 18:00 | 65 | 64
2017-07-04 18:30 | 67 | 66
2017-07-04 19:00 | 67 | 67
2017-07-04 19:30 | 67 | 67
2017-07-04 20:00 | 67 | 67
2017-07-04 20:30 | 63 | 62
2017-07-04 21:00 | 61 | 60
2017-07-04 21:30 | 61 | 61
2017-07-04 22:00 | 58 | 58
2017-07-04 22:30 | 53 | 52
2017-07-04 23:00 | 52 | 51
2017-07-04 23:30 | 50 | 50
2017-07-05 | 51 | 50
2017-07-05 00:30 | 52 | 50
2017-07-05 01:00 | 50 | 48
2017-07-05 01:30 | 49 | 47
2017-07-05 02:00 | 50 | 48
2017-07-05 02:30 | 49 | 47
2017-07-05 03:00 | 50 | 48
2017-07-05 03:30 | 48 | 46
2017-07-05 04:00 | 48 | 46
2017-07-05 04:30 | 48 | 46
2017-07-05 05:00 | 50 | 48
2017-07-05 05:30 | 48 | 45
2017-07-05 06:00 | 47 | 45
2017-07-05 06:30 | 49 | 48
2017-07-05 07:00 | 50 | 49
2017-07-05 07:30 | 51 | 50
2017-07-05 08:00 | 51 | 49
2017-07-05 08:30 | 54 | 50
2017-07-05 09:00 | 53 | 50
2017-07-05 09:30 | 53 | 50
2017-07-05 10:00 | 54 | 52
2017-07-05 10:30 | 54 | 51
2017-07-05 11:00 | 54 | 50
2017-07-05 11:30 | 54 | 51
2017-07-05 12:00 | 53 | 51
2017-07-05 12:30 | 54 | 52
2017-07-05 13:00 | 52 | 50
2017-07-05 13:30 | 53 | 51
2017-07-05 14:00 | 55 | 52
2017-07-05 14:30 | 55 | 52
2017-07-05 15:00 | 54 | 52
2017-07-05 15:30 | 55 | 53
2017-07-05 16:00 | 56 | 54
2017-07-05 16:30 | 54 | 52
2017-07-05 17:00 | 56 | 53
2017-07-05 17:30 | 59 | 57
2017-07-05 18:00 | 60 | 59
2017-07-05 18:30 | 60 | 59
2017-07-05 19:00 | 60 | 58
2017-07-05 19:30 | 60 | 58
2017-07-05 20:00 | 61 | 59
2017-07-05 20:30 | 59 | 58
2017-07-05 21:00 | 58 | 56
2017-07-05 21:30 | 56 | 53
2017-07-05 22:00 | 54 | 51
2017-07-05 22:30 | 52 | 49
2017-07-05 23:00 | 52 | 49
2017-07-05 23:30 | 61 | 57
2017-07-06 | 63 | 58
2017-07-06 00:30 | 62 | 57
2017-07-06 01:00 | 59 | 52
2017-07-06 01:30 | 58 | 51
2017-07-06 02:00 | 50 | 43
2017-07-06 02:30 | 49 | 41
2017-07-06 03:00 | 48 | 40
2017-07-06 03:30 | 49 | 41
2017-07-06 04:00 | 49 | 42
2017-07-06 04:30 | 50 | 42
2017-07-06 05:00 | 51 | 43
2017-07-06 05:30 | 54 | 47
2017-07-06 06:00 | 55 | 48
2017-07-06 06:30 | 51 | 48
2017-07-06 07:00 | 58 | 57
2017-07-06 07:30 | 59 | 59
2017-07-06 08:00 | 63 | 63
2017-07-06 08:30 | 64 | 63
2017-07-06 09:00 | 62 | 61
2017-07-06 09:30 | 58 | 57
2017-07-06 10:00 | 58 | 57
2017-07-06 10:30 | 56 | 55
2017-07-06 11:00 | 57 | 56
2017-07-06 11:30 | 57 | 56
2017-07-06 12:00 | 57 | 56
2017-07-06 12:30 | 56 | 55
2017-07-06 13:00 | 57 | 57
2017-07-06 13:30 | 55 | 55
2017-07-06 14:00 | 54 | 53
2017-07-06 14:30 | 56 | 56
2017-07-06 15:00 | 57 | 56
2017-07-06 15:30 | 57 | 57
2017-07-06 16:00 | 57 | 57
2017-07-06 16:30 | 51 | 50
2017-07-06 17:00 | 51 | 51
2017-07-06 17:30 | 52 | 51
2017-07-06 18:00 | 52 | 52
2017-07-06 18:30 | 52 | 52
2017-07-06 19:00 | 53 | 53
2017-07-06 19:30 | 53 | 53
2017-07-06 20:00 | 52 | 52
2017-07-06 20:30 | 52 | 52
2017-07-06 21:00 | 52 | 52
2017-07-06 21:30 | 52 | 52
2017-07-06 22:00 | 50 | 50
2017-07-06 22:30 | 45 | 45
2017-07-06 23:00 | 45 | 45
2017-07-06 23:30 | 45 | 45
2017-07-07 | 45 | 44
2017-07-07 00:30 | 44 | 43
2017-07-07 01:00 | 43 | 43
2017-07-07 01:30 | 42 | 42
2017-07-07 02:00 | 45 | 43
2017-07-07 02:30 | 48 | 44
2017-07-07 03:00 | 48 | 45
2017-07-07 03:30 | 47 | 44
2017-07-07 04:00 | 47 | 44
2017-07-07 04:30 | 48 | 44
2017-07-07 05:00 | 46 | 44
2017-07-07 05:30 | 45 | 42
2017-07-07 06:00 | 46 | 44
2017-07-07 06:30 | 42 | 42
2017-07-07 07:00 | 43 | 43
2017-07-07 07:30 | 46 | 46
2017-07-07 08:00 | 48 | 47
2017-07-07 08:30 | 47 | 47
2017-07-07 09:00 | 48 | 48
2017-07-07 09:30 | 49 | 49
2017-07-07 10:00 | 50 | 50
2017-07-07 10:30 | 53 | 53
2017-07-07 11:00 | 50 | 50
2017-07-07 11:30 | 47 | 47
2017-07-07 12:00 | 50 | 50
2017-07-07 12:30 | 50 | 50
2017-07-07 13:00 | 50 | 50
2017-07-07 13:30 | 49 | 49
2017-07-07 14:00 | 50 | 50
2017-07-07 14:30 | 51 | 51
2017-07-07 15:00 | 54 | 54
2017-07-07 15:30 | 56 | 56
2017-07-07 16:00 | 57 | 57
2017-07-07 16:30 | 57 | 57
2017-07-07 17:00 | 58 | 58
2017-07-07 17:30 | 59 | 59
2017-07-07 18:00 | 60 | 60
2017-07-07 18:30 | 60 | 60
2017-07-07 19:00 | 60 | 60
2017-07-07 19:30 | 60 | 60
2017-07-07 20:00 | 58 | 58
2017-07-07 20:30 | 59 | 59
2017-07-07 21:00 | 59 | 59
2017-07-07 21:30 | 57 | 57
2017-07-07 22:00 | 57 | 57
2017-07-07 22:30 | 57 | 56
2017-07-07 23:00 | 56 | 56
2017-07-07 23:30 | 56 | 55
2017-07-08 | 53 | 52
2017-07-08 00:30 | 51 | 51
2017-07-08 01:00 | 51 | 50
2017-07-08 01:30 | 50 | 50
2017-07-08 02:00 | 50 | 50
2017-07-08 02:30 | 50 | 50
2017-07-08 03:00 | 50 | 50
2017-07-08 03:30 | 50 | 50
2017-07-08 04:00 | 50 | 50
2017-07-08 04:30 | 49 | 49
2017-07-08 05:00 | 50 | 50
2017-07-08 05:30 | 51 | 51
2017-07-08 06:00 | 47 | 47
2017-07-08 06:30 | 46 | 46
2017-07-08 07:00 | 45 | 45
2017-07-08 07:30 | 48 | 48
2017-07-08 08:00 | 53 | 53
2017-07-08 08:30 | 52 | 52
2017-07-08 09:00 | 51 | 51
2017-07-08 09:30 | 52 | 52
2017-07-08 10:00 | 52 | 52
2017-07-08 10:30 | 54 | 54
2017-07-08 11:00 | 55 | 55
2017-07-08 11:30 | 54 | 54
2017-07-08 12:00 | 53 | 53
2017-07-08 12:30 | 52 | 52
2017-07-08 13:00 | 50 | 50
2017-07-08 13:30 | 50 | 50
2017-07-08 14:00 | 49 | 49
2017-07-08 14:30 | 50 | 50
2017-07-08 15:00 | 49 | 49
2017-07-08 15:30 | 49 | 49
2017-07-08 16:00 | 49 | 48
2017-07-08 16:30 | 49 | 49
2017-07-08 17:00 | 52 | 52
2017-07-08 17:30 | 53 | 53
2017-07-08 18:00 | 53 | 53
2017-07-08 18:30 | 55 | 55
2017-07-08 19:00 | 55 | 55
2017-07-08 19:30 | 49 | 49
2017-07-08 20:00 | 54 | 54
2017-07-08 20:30 | 54 | 54
2017-07-08 21:00 | 55 | 55
2017-07-08 21:30 | 55 | 55
2017-07-08 22:00 | 54 | 54
2017-07-08 22:30 | 52 | 51
2017-07-08 23:00 | 50 | 50
2017-07-08 23:30 | 48 | 47
2017-07-09 | 47 | 46
2017-07-09 00:30 | 47 | 46
2017-07-09 01:00 | 46 | 46
2017-07-09 01:30 | 46 | 46
2017-07-09 02:00 | 45 | 45
2017-07-09 02:30 | 44 | 44
2017-07-09 03:00 | 44 | 44
2017-07-09 03:30 | 46 | 46
2017-07-09 04:00 | 45 | 45
2017-07-09 04:30 | 44 | 44
2017-07-09 05:00 | 49 | 49
2017-07-09 05:30 | 48 | 48
2017-07-09 06:00 | 48 | 48
2017-07-09 06:30 | 48 | 48
2017-07-09 07:00 | 48 | 48
2017-07-09 07:30 | 49 | 49
2017-07-09 08:00 | 48 | 48
2017-07-09 08:30 | 48 | 48
2017-07-09 09:00 | 48 | 48
2017-07-09 09:30 | 49 | 49
2017-07-09 10:00 | 49 | 49
2017-07-09 10:30 | 48 | 48
2017-07-09 11:00 | 50 | 49
2017-07-09 11:30 | 49 | 49
2017-07-09 12:00 | 48 | 47
2017-07-09 12:30 | 48 | 47
2017-07-09 13:00 | 47 | 47
2017-07-09 13:30 | 47 | 47
2017-07-09 14:00 | 47 | 47
2017-07-09 14:30 | 48 | 48
2017-07-09 15:00 | 48 | 48
2017-07-09 15:30 | 49 | 49
2017-07-09 16:00 | 49 | 48
2017-07-09 16:30 | 49 | 49
2017-07-09 17:00 | 49 | 49
2017-07-09 17:30 | 50 | 50
2017-07-09 18:00 | 48 | 48
2017-07-09 18:30 | 50 | 49
2017-07-09 19:00 | 52 | 50
2017-07-09 19:30 | 52 | 50
2017-07-09 20:00 | 51 | 49
2017-07-09 20:30 | 50 | 48
2017-07-09 21:00 | 50 | 49
2017-07-09 21:30 | 49 | 48
2017-07-09 22:00 | 48 | 47
2017-07-09 22:30 | 47 | 46
2017-07-09 23:00 | 45 | 44
2017-07-09 23:30 | 44 | 43
2017-07-10 | 44 | 43
2017-07-10 00:30 | 43 | 43
2017-07-10 01:00 | 43 | 43
2017-07-10 01:30 | 44 | 43
2017-07-10 02:00 | 43 | 43
2017-07-10 02:30 | 44 | 44
2017-07-10 03:00 | 45 | 45
2017-07-10 03:30 | 44 | 43
2017-07-10 04:00 | 43 | 43
2017-07-10 04:30 | 43 | 43
2017-07-10 05:00 | 43 | 42
2017-07-10 05:30 | 43 | 43
2017-07-10 06:00 | 44 | 43
2017-07-10 06:30 | 44 | 44
2017-07-10 07:00 | 47 | 46
2017-07-10 07:30 | 49 | 49
2017-07-10 08:00 | 49 | 49
2017-07-10 08:30 | 51 | 50
2017-07-10 09:00 | 51 | 50
2017-07-10 09:30 | 51 | 50
2017-07-10 10:00 | 51 | 50
2017-07-10 10:30 | 51 | 50
2017-07-10 11:00 | 50 | 49
2017-07-10 11:30 | 50 | 49
2017-07-10 12:00 | 50 | 49
2017-07-10 12:30 | 51 | 50
2017-07-10 13:00 | 51 | 50
2017-07-10 13:30 | 50 | 50
2017-07-10 14:00 | 51 | 50
2017-07-10 14:30 | 49 | 49
2017-07-10 15:00 | 50 | 50
2017-07-10 15:30 | 52 | 52
2017-07-10 16:00 | 53 | 52
2017-07-10 16:30 | 53 | 53
2017-07-10 17:00 | 54 | 53
2017-07-10 17:30 | 55 | 54
2017-07-10 18:00 | 54 | 53
2017-07-10 18:30 | 55 | 55
2017-07-10 19:00 | 56 | 56
2017-07-10 19:30 | 54 | 53
2017-07-10 20:00 | 54 | 54
2017-07-10 20:30 | 53 | 53
2017-07-10 21:00 | 53 | 52
2017-07-10 21:30 | 51 | 51
2017-07-10 22:00 | 52 | 52
2017-07-10 22:30 | 51 | 51
2017-07-10 23:00 | 47 | 47
2017-07-10 23:30 | 48 | 47
2017-07-11 | 47 | 46
2017-07-11 00:30 | 48 | 47
2017-07-11 01:00 | 46 | 45
2017-07-11 01:30 | 47 | 46
2017-07-11 02:00 | 47 | 47
2017-07-11 02:30 | 46 | 45
2017-07-11 03:00 | 46 | 46
2017-07-11 03:30 | 46 | 46
2017-07-11 04:00 | 45 | 45
2017-07-11 04:30 | 46 | 46
2017-07-11 05:00 | 48 | 48
2017-07-11 05:30 | 48 | 48
2017-07-11 06:00 | 50 | 50
2017-07-11 06:30 | 52 | 51
2017-07-11 07:00 | 52 | 52
2017-07-11 07:30 | 55 | 55
2017-07-11 08:00 | 55 | 54
2017-07-11 08:30 | 56 | 55
2017-07-11 09:00 | 56 | 54
2017-07-11 09:30 | 54 | 52
2017-07-11 10:00 | 54 | 53
2017-07-11 10:30 | 55 | 55
2017-07-11 11:00 | 57 | 57
2017-07-11 11:30 | 59 | 59
2017-07-11 12:00 | 60 | 59
2017-07-11 12:30 | 58 | 58
2017-07-11 13:00 | 58 | 58
2017-07-11 13:30 | 60 | 60
2017-07-11 14:00 | 60 | 60
2017-07-11 14:30 | 62 | 62
2017-07-11 15:00 | 64 | 64
2017-07-11 15:30 | 65 | 65
2017-07-11 16:00 | 64 | 64
2017-07-11 16:30 | 63 | 63
2017-07-11 17:00 | 66 | 66
2017-07-11 17:30 | 66 | 66
2017-07-11 18:00 | 64 | 64
2017-07-11 18:30 | 61 | 61
2017-07-11 19:00 | 66 | 66
2017-07-11 19:30 | 64 | 64
2017-07-11 20:00 | 63 | 63
2017-07-11 20:30 | 61 | 61
2017-07-11 21:00 | 60 | 60
2017-07-11 21:30 | 58 | 58
2017-07-11 22:00 | 58 | 58
2017-07-11 22:30 | 58 | 58
2017-07-11 23:00 | 55 | 55
2017-07-11 23:30 | 54 | 54
2017-07-12 | 53 | 53
2017-07-12 00:30 | 62 | 55
2017-07-12 01:00 | 60 | 54
2017-07-12 01:30 | 61 | 54
2017-07-12 02:00 | 60 | 53
2017-07-12 02:30 | 59 | 52
2017-07-12 03:00 | 60 | 53
2017-07-12 03:30 | 60 | 54
2017-07-12 04:00 | 60 | 53
2017-07-12 04:30 | 60 | 53
2017-07-12 05:00 | 59 | 52
2017-07-12 05:30 | 59 | 52
2017-07-12 06:00 | 59 | 52
2017-07-12 06:30 | 60 | 51
2017-07-12 07:00 | 53 | 52
2017-07-12 07:30 | 55 | 54
2017-07-12 08:00 | 59 | 58
2017-07-12 08:30 | 56 | 56
2017-07-12 09:00 | 54 | 54
2017-07-12 09:30 | 53 | 53
2017-07-12 10:00 | 53 | 53
2017-07-12 10:30 | 52 | 52
2017-07-12 11:00 | 53 | 53
2017-07-12 11:30 | 53 | 52
2017-07-12 12:00 | 56 | 56
2017-07-12 12:30 | 54 | 54
2017-07-12 13:00 | 52 | 52
2017-07-12 13:30 | 52 | 52
2017-07-12 14:00 | 52 | 52
2017-07-12 14:30 | 54 | 54
2017-07-12 15:00 | 54 | 54
2017-07-12 15:30 | 54 | 54
2017-07-12 16:00 | 55 | 55
2017-07-12 16:30 | 50 | 49
2017-07-12 17:00 | 60 | 55
2017-07-12 17:30 | 62 | 58
2017-07-12 18:00 | 63 | 60
2017-07-12 18:30 | 65 | 62
2017-07-12 19:00 | 66 | 63
2017-07-12 19:30 | 64 | 61
2017-07-12 20:00 | 63 | 60
2017-07-12 20:30 | 63 | 60
2017-07-12 21:00 | 61 | 58
2017-07-12 21:30 | 58 | 54
2017-07-12 22:00 | 57 | 53
2017-07-12 22:30 | 58 | 55
2017-07-12 23:00 | 59 | 57
2017-07-12 23:30 | 57 | 54
2017-07-13 | 59 | 54
2017-07-13 00:30 | 60 | 55
2017-07-13 01:00 | 57 | 51
2017-07-13 01:30 | 57 | 51
2017-07-13 02:00 | 56 | 50
2017-07-13 02:30 | 55 | 49
2017-07-13 03:00 | 55 | 49
2017-07-13 03:30 | 55 | 49
2017-07-13 04:00 | 55 | 49
2017-07-13 04:30 | 55 | 49
2017-07-13 05:00 | 54 | 48
2017-07-13 05:30 | 54 | 48
2017-07-13 06:00 | 53 | 47
2017-07-13 06:30 | 48 | 47
2017-07-13 07:00 | 50 | 49
2017-07-13 07:30 | 51 | 50
2017-07-13 08:00 | 51 | 51
2017-07-13 08:30 | 54 | 53
2017-07-13 09:00 | 54 | 53
2017-07-13 09:30 | 53 | 52
2017-07-13 10:00 | 52 | 51
2017-07-13 10:30 | 53 | 52
2017-07-13 11:00 | 51 | 50
2017-07-13 11:30 | 52 | 51
2017-07-13 12:00 | 52 | 51
2017-07-13 12:30 | 55 | 53
2017-07-13 13:00 | 55 | 54
2017-07-13 13:30 | 53 | 52
2017-07-13 14:00 | 53 | 52
2017-07-13 14:30 | 54 | 53
2017-07-13 15:00 | 53 | 52
2017-07-13 15:30 | 53 | 53
2017-07-13 16:00 | 54 | 53
2017-07-13 16:30 | 55 | 54
2017-07-13 17:00 | 54 | 53
2017-07-13 17:30 | 54 | 54
2017-07-13 18:00 | 55 | 54
2017-07-13 18:30 | 56 | 56
2017-07-13 19:00 | 55 | 55
2017-07-13 19:30 | 55 | 55
2017-07-13 20:00 | 54 | 54
2017-07-13 20:30 | 53 | 53
2017-07-13 21:00 | 53 | 53
2017-07-13 21:30 | 52 | 51
2017-07-13 22:00 | 50 | 50
2017-07-13 22:30 | 49 | 49
2017-07-13 23:00 | 47 | 47
2017-07-13 23:30 | 47 | 47
2017-07-14 | 47 | 47
2017-07-14 00:30 | 47 | 47
2017-07-14 01:00 | 46 | 46
2017-07-14 01:30 | 44 | 44
2017-07-14 02:00 | 43 | 43
2017-07-14 02:30 | 44 | 44
2017-07-14 03:00 | 42 | 42
2017-07-14 03:30 | 42 | 42
2017-07-14 04:00 | 43 | 43
2017-07-14 04:30 | 42 | 42
2017-07-14 05:00 | 42 | 42
2017-07-14 05:30 | 43 | 43
2017-07-14 06:00 | 43 | 43
2017-07-14 06:30 | 44 | 44
2017-07-14 07:00 | 44 | 44
2017-07-14 07:30 | 47 | 47
2017-07-14 08:00 | 48 | 47
2017-07-14 08:30 | 47 | 47
2017-07-14 09:00 | 48 | 48
2017-07-14 09:30 | 49 | 49
2017-07-14 10:00 | 49 | 48
2017-07-14 10:30 | 48 | 47
2017-07-14 11:00 | 48 | 47
2017-07-14 11:30 | 47 | 46
2017-07-14 12:00 | 48 | 47
2017-07-14 12:30 | 50 | 49
2017-07-14 13:00 | 51 | 50
2017-07-14 13:30 | 53 | 52
2017-07-14 14:00 | 51 | 51
2017-07-14 14:30 | 54 | 53
2017-07-14 15:00 | 53 | 52
2017-07-14 15:30 | 54 | 53
2017-07-14 16:00 | 54 | 53
2017-07-14 16:30 | 56 | 55
2017-07-14 17:00 | 54 | 53
2017-07-14 17:30 | 53 | 52
2017-07-14 18:00 | 53 | 52
2017-07-14 18:30 | 56 | 55
2017-07-14 19:00 | 56 | 55
2017-07-14 19:30 | 55 | 54
2017-07-14 20:00 | 56 | 56
2017-07-14 20:30 | 54 | 54
2017-07-14 21:00 | 53 | 53
2017-07-14 21:30 | 52 | 52
2017-07-14 22:00 | 51 | 51
2017-07-14 22:30 | 50 | 50
2017-07-14 23:00 | 49 | 48
2017-07-14 23:30 | 49 | 49
2017-07-15 | 48 | 47
2017-07-15 00:30 | 47 | 47
2017-07-15 01:00 | 46 | 46
2017-07-15 01:30 | 46 | 46
2017-07-15 02:00 | 46 | 46
2017-07-15 02:30 | 45 | 45
2017-07-15 03:00 | 45 | 45
2017-07-15 03:30 | 46 | 45
2017-07-15 04:00 | 46 | 46
2017-07-15 04:30 | 46 | 46
2017-07-15 05:00 | 48 | 48
2017-07-15 05:30 | 47 | 47
2017-07-15 06:00 | 46 | 46
2017-07-15 06:30 | 46 | 45
2017-07-15 07:00 | 46 | 45
2017-07-15 07:30 | 47 | 46
2017-07-15 08:00 | 48 | 47
2017-07-15 08:30 | 48 | 48
2017-07-15 09:00 | 47 | 47
2017-07-15 09:30 | 47 | 47
2017-07-15 10:00 | 46 | 46
2017-07-15 10:30 | 47 | 46
2017-07-15 11:00 | 47 | 46
2017-07-15 11:30 | 47 | 46
2017-07-15 12:00 | 46 | 45
2017-07-15 12:30 | 47 | 46
2017-07-15 13:00 | 47 | 46
2017-07-15 13:30 | 46 | 45
2017-07-15 14:00 | 46 | 45
2017-07-15 14:30 | 44 | 44
2017-07-15 15:00 | 46 | 45
2017-07-15 15:30 | 45 | 44
2017-07-15 16:00 | 46 | 46
2017-07-15 16:30 | 48 | 48
2017-07-15 17:00 | 49 | 49
2017-07-15 17:30 | 49 | 49
2017-07-15 18:00 | 50 | 50
2017-07-15 18:30 | 53 | 52
2017-07-15 19:00 | 49 | 48
2017-07-15 19:30 | 34 | 33
2017-07-15 20:00 | 34 | 33
2017-07-15 20:30 | 32 | 31
2017-07-15 21:00 | 32 | 31
2017-07-15 21:30 | 33 | 31
2017-07-15 22:00 | 33 | 31
2017-07-15 22:30 | 30 | 28
2017-07-15 23:00 | 31 | 28
2017-07-15 23:30 | 32 | 29
2017-07-16 | 31 | 28
2017-07-16 00:30 | 31 | 27
2017-07-16 01:00 | 32 | 28
2017-07-16 01:30 | 29 | 28
2017-07-16 02:00 | 30 | 27
2017-07-16 02:30 | 30 | 27
2017-07-16 03:00 | 30 | 28
2017-07-16 03:30 | 30 | 28
2017-07-16 04:00 | 30 | 28
2017-07-16 04:30 | 30 | 27
2017-07-16 05:00 | 30 | 27
2017-07-16 05:30 | 30 | 27
2017-07-16 06:00 | 29 | 26
2017-07-16 06:30 | 29 | 26
2017-07-16 07:00 | 29 | 26
2017-07-16 07:30 | 30 | 28
2017-07-16 08:00 | 30 | 28
2017-07-16 08:30 | 31 | 29
2017-07-16 09:00 | 31 | 29
2017-07-16 09:30 | 31 | 28
2017-07-16 10:00 | 32 | 28
2017-07-16 10:30 | 32 | 28
2017-07-16 11:00 | 32 | 29
2017-07-16 11:30 | 32 | 28
2017-07-16 12:00 | 33 | 29
2017-07-16 12:30 | 33 | 30
2017-07-16 13:00 | 32 | 28
2017-07-16 13:30 | 32 | 28
2017-07-16 14:00 | 33 | 29
2017-07-16 14:30 | 32 | 29
2017-07-16 15:00 | 34 | 30
2017-07-16 15:30 | 34 | 31
2017-07-16 16:00 | 35 | 32
2017-07-16 16:30 | 36 | 33
2017-07-16 17:00 | 36 | 33
2017-07-16 17:30 | 39 | 34
2017-07-16 18:00 | 38 | 33
2017-07-16 18:30 | 40 | 35
2017-07-16 19:00 | 31 | 27
2017-07-16 19:30 | 16 | 15
2017-07-16 20:00 | 14 | 13
2017-07-16 20:30 | 14 | 13
2017-07-16 21:00 | 14 | 13
2017-07-16 21:30 | 13 | 12
2017-07-16 22:00 | 11 | 11
2017-07-16 22:30 | 10 | 9
2017-07-16 23:00 | 10 | 10
2017-07-16 23:30 | 9 | 9
2017-07-17 | 9 | 9
2017-07-17 00:30 | 9 | 9
2017-07-17 01:00 | 8 | 8
2017-07-17 01:30 | 8 | 8
2017-07-17 02:00 | 7 | 7
2017-07-17 02:30 | 8 | 8
2017-07-17 03:00 | 6 | 6
2017-07-17 03:30 | 6 | 6
2017-07-17 04:00 | 9 | 9
2017-07-17 04:30 | 15 | 15
2017-07-17 05:00 | 17 | 17
2017-07-17 05:30 | 17 | 17
2017-07-17 06:00 | 19 | 19
2017-07-17 06:30 | 19 | 19
2017-07-17 07:00 | 15 | 15
2017-07-17 07:30 | 14 | 14
2017-07-17 08:00 | 14 | 13
2017-07-17 08:30 | 13 | 13
2017-07-17 09:00 | 14 | 13
2017-07-17 09:30 | 12 | 11
2017-07-17 10:00 | 12 | 11
2017-07-17 10:30 | 10 | 9
2017-07-17 11:00 | 11 | 10
2017-07-17 11:30 | 11 | 10
2017-07-17 12:00 | 11 | 10
2017-07-17 12:30 | 12 | 11
2017-07-17 13:00 | 11 | 10
2017-07-17 13:30 | 12 | 10
2017-07-17 14:00 | 12 | 11
2017-07-17 14:30 | 12 | 10
2017-07-17 15:00 | 12 | 11
2017-07-17 15:30 | 13 | 12
2017-07-17 16:00 | 15 | 14
2017-07-17 16:30 | 15 | 14
2017-07-17 17:00 | 15 | 14
2017-07-17 17:30 | 16 | 15
2017-07-17 18:00 | 16 | 15
2017-07-17 18:30 | 17 | 17
2017-07-17 19:00 | 18 | 17
2017-07-17 19:30 | 18 | 17
2017-07-17 20:00 | 14 | 13
2017-07-17 20:30 | 13 | 13
2017-07-17 21:00 | 12 | 12
2017-07-17 21:30 | 12 | 12
2017-07-17 22:00 | 12 | 12
2017-07-17 22:30 | 10 | 10
2017-07-17 23:00 | 8 | 8
2017-07-17 23:30 | 8 | 8
2017-07-18 | 7 | 7
2017-07-18 00:30 | 7 | 7
2017-07-18 01:00 | 7 | 7
2017-07-18 01:30 | 6 | 6
2017-07-18 02:00 | 6 | 6
2017-07-18 02:30 | 6 | 6
2017-07-18 03:00 | 6 | 6
2017-07-18 03:30 | 6 | 6
2017-07-18 04:00 | 7 | 7
2017-07-18 04:30 | 8 | 8
2017-07-18 05:00 | 8 | 8
2017-07-18 05:30 | 9 | 9
2017-07-18 06:00 | 10 | 10
2017-07-18 06:30 | 12 | 12
2017-07-18 07:00 | 12 | 12
2017-07-18 07:30 | 12 | 11
2017-07-18 08:00 | 8 | 7
2017-07-18 08:30 | 9 | 7
2017-07-18 09:00 | 9 | 7
2017-07-18 09:30 | 8 | 6
2017-07-18 10:00 | 9 | 7
2017-07-18 10:30 | 8 | 6
2017-07-18 11:00 | 9 | 7
2017-07-18 11:30 | 10 | 8
2017-07-18 12:00 | 10 | 8
2017-07-18 12:30 | 10 | 8
2017-07-18 13:00 | 10 | 9
2017-07-18 13:30 | 12 | 10
2017-07-18 14:00 | 12 | 11
2017-07-18 14:30 | 14 | 13
2017-07-18 15:00 | 14 | 13
2017-07-18 15:30 | 13 | 12
2017-07-18 16:00 | 11 | 10
2017-07-18 16:30 | 14 | 13
2017-07-18 17:00 | 18 | 16
2017-07-18 17:30 | 19 | 18
2017-07-18 18:00 | 17 | 14
2017-07-18 18:30 | 17 | 14
2017-07-18 19:00 | 17 | 13
2017-07-18 19:30 | 17 | 13
2017-07-18 20:00 | 16 | 12
2017-07-18 20:30 | 15 | 12
2017-07-18 21:00 | 14 | 12
2017-07-18 21:30 | 13 | 11
2017-07-18 22:00 | 12 | 10
2017-07-18 22:30 | 9 | 8
2017-07-18 23:00 | 6 | 6
2017-07-18 23:30 | 6 | 5
2017-07-19 | 6 | 6
2017-07-19 00:30 | 7 | 7
2017-07-19 01:00 | 8 | 8
2017-07-19 01:30 | 7 | 7
2017-07-19 02:00 | 6 | 6
2017-07-19 02:30 | 6 | 6
2017-07-19 03:00 | 5 | 5
2017-07-19 03:30 | 5 | 5
2017-07-19 04:00 | 6 | 6
2017-07-19 04:30 | 4 | 4
2017-07-19 05:00 | 5 | 5
2017-07-19 05:30 | 5 | 5
2017-07-19 06:00 | 6 | 6
2017-07-19 06:30 | 8 | 8
2017-07-19 07:00 | 10 | 10
2017-07-19 07:30 | 13 | 13
2017-07-19 08:00 | 13 | 12
2017-07-19 08:30 | 10 | 9
2017-07-19 09:00 | 7 | 6
2017-07-19 09:30 | 5 | 4
2017-07-19 10:00 | 5 | 4
2017-07-19 10:30 | 6 | 4
2017-07-19 11:00 | 7 | 6
2017-07-19 11:30 | 7 | 5
2017-07-19 12:00 | 6 | 4
2017-07-19 12:30 | 7 | 5
2017-07-19 13:00 | 7 | 5
2017-07-19 13:30 | 7 | 4
2017-07-19 14:00 | 7 | 5
2017-07-19 14:30 | 8 | 7
2017-07-19 15:00 | 8 | 7
2017-07-19 15:30 | 8 | 7
2017-07-19 16:00 | 8 | 7
2017-07-19 16:30 | 8 | 7
2017-07-19 17:00 | 9 | 8
2017-07-19 17:30 | 10 | 9
2017-07-19 18:00 | 9 | 8
2017-07-19 18:30 | 9 | 8
2017-07-19 19:00 | 10 | 9
2017-07-19 19:30 | 16 | 15
2017-07-19 20:00 | 14 | 12
2017-07-19 20:30 | 13 | 12
2017-07-19 21:00 | 13 | 12
2017-07-19 21:30 | 8 | 7
2017-07-19 22:00 | 6 | 6
2017-07-19 22:30 | 4 | 4
2017-07-19 23:00 | 3 | 3
2017-07-19 23:30 | 1 | 1
2017-07-20 | 1 | 1
2017-07-20 00:30 | 1 | 0
2017-07-20 01:00 | 2 | 1
2017-07-20 01:30 | 2 | 0
2017-07-20 02:00 | 2 | 0
2017-07-20 02:30 | 3 | 0
2017-07-20 03:00 | 2 | 0
2017-07-20 03:30 | 2 | 1
2017-07-20 04:00 | 4 | 2
2017-07-20 04:30 | 4 | 2
2017-07-20 05:00 | 3 | 1
2017-07-20 05:30 | 3 | 2
2017-07-20 06:00 | 3 | 2
2017-07-20 06:30 | 5 | 4
2017-07-20 07:00 | 8 | 6
2017-07-20 07:30 | 6 | 4
2017-07-20 08:00 | 6 | 4
2017-07-20 08:30 | 3 | 1
2017-07-20 09:00 | 4 | 3
2017-07-20 09:30 | 5 | 4
2017-07-20 10:00 | 3 | 1
2017-07-20 10:30 | 4 | 3
2017-07-20 11:00 | 8 | 7
2017-07-20 11:30 | 9 | 8
2017-07-20 12:00 | 8 | 7
2017-07-20 12:30 | 8 | 6
2017-07-20 13:00 | 7 | 6
2017-07-20 13:30 | 6 | 6
2017-07-20 14:00 | 9 | 8
2017-07-20 14:30 | 11 | 10
2017-07-20 15:00 | 14 | 13
2017-07-20 15:30 | 16 | 15
2017-07-20 16:00 | 21 | 20
2017-07-20 16:30 | 22 | 21
2017-07-20 17:00 | 22 | 20
2017-07-20 17:30 | 22 | 21
2017-07-20 18:00 | 22 | 21
2017-07-20 18:30 | 24 | 23
2017-07-20 19:00 | 24 | 24
2017-07-20 19:30 | 24 | 23
2017-07-20 20:00 | 23 | 22
2017-07-20 20:30 | 23 | 22
2017-07-20 21:00 | 24 | 22
2017-07-20 21:30 | 24 | 22
2017-07-20 22:00 | 25 | 22
2017-07-20 22:30 | 22 | 19
2017-07-20 23:00 | 15 | 13
2017-07-20 23:30 | 14 | 12
2017-07-21 | 13 | 11
2017-07-21 00:30 | 13 | 11
2017-07-21 01:00 | 13 | 10
2017-07-21 01:30 | 14 | 12
2017-07-21 02:00 | 13 | 11
2017-07-21 02:30 | 13 | 11
2017-07-21 03:00 | 13 | 11
2017-07-21 03:30 | 14 | 11
2017-07-21 04:00 | 13 | 11
2017-07-21 04:30 | 13 | 11
2017-07-21 05:00 | 14 | 12
2017-07-21 05:30 | 15 | 13
2017-07-21 06:00 | 19 | 17
2017-07-21 06:30 | 22 | 20
2017-07-21 07:00 | 22 | 21
2017-07-21 07:30 | 21 | 21
2017-07-21 08:00 | 20 | 20
2017-07-21 08:30 | 21 | 20
2017-07-21 09:00 | 21 | 21
2017-07-21 09:30 | 20 | 20
2017-07-21 10:00 | 15 | 15
2017-07-21 10:30 | 12 | 12
2017-07-21 11:00 | 17 | 17
2017-07-21 11:30 | 18 | 17
2017-07-21 12:00 | 16 | 16
2017-07-21 12:30 | 13 | 13
2017-07-21 13:00 | 13 | 13
2017-07-21 13:30 | 13 | 13
2017-07-21 14:00 | 14 | 14
2017-07-21 14:30 | 21 | 21
2017-07-21 15:00 | 22 | 22
2017-07-21 15:30 | 22 | 22
2017-07-21 16:00 | 25 | 25
2017-07-21 16:30 | 19 | 19
2017-07-21 17:00 | 18 | 18
2017-07-21 17:30 | 18 | 18
2017-07-21 18:00 | 18 | 18
2017-07-21 18:30 | 19 | 19
2017-07-21 19:00 | 20 | 20
2017-07-21 19:30 | 21 | 21
2017-07-21 20:00 | 20 | 19
2017-07-21 20:30 | 19 | 18
2017-07-21 21:00 | 19 | 18
2017-07-21 21:30 | 19 | 17
2017-07-21 22:00 | 18 | 16
2017-07-21 22:30 | 17 | 15
2017-07-21 23:00 | 17 | 13
2017-07-21 23:30 | 16 | 11
2017-07-22 | 14 | 8
2017-07-22 00:30 | 15 | 9
2017-07-22 01:00 | 12 | 5
2017-07-22 01:30 | 13 | 5
2017-07-22 02:00 | 14 | 7
2017-07-22 02:30 | 16 | 8
2017-07-22 03:00 | 15 | 7
2017-07-22 03:30 | 15 | 7
2017-07-22 04:00 | 15 | 7
2017-07-22 04:30 | 16 | 7
2017-07-22 05:00 | 15 | 7
2017-07-22 05:30 | 15 | 7
2017-07-22 06:00 | 15 | 8
2017-07-22 06:30 | 14 | 6
2017-07-22 07:00 | 13 | 5
2017-07-22 07:30 | 14 | 8
2017-07-22 08:00 | 15 | 9
2017-07-22 08:30 | 18 | 13
2017-07-22 09:00 | 18 | 13
2017-07-22 09:30 | 15 | 9
2017-07-22 10:00 | 12 | 6
2017-07-22 10:30 | 11 | 5
2017-07-22 11:00 | 11 | 6
2017-07-22 11:30 | 11 | 5
2017-07-22 12:00 | 11 | 5
2017-07-22 12:30 | 11 | 4
2017-07-22 13:00 | 12 | 5
2017-07-22 13:30 | 11 | 4
2017-07-22 14:00 | 11 | 5
2017-07-22 14:30 | 13 | 7
2017-07-22 15:00 | 13 | 7
2017-07-22 15:30 | 13 | 7
2017-07-22 16:00 | 13 | 8
2017-07-22 16:30 | 15 | 11
2017-07-22 17:00 | 16 | 11
2017-07-22 17:30 | 16 | 12
2017-07-22 18:00 | 16 | 13
2017-07-22 18:30 | 16 | 13
2017-07-22 19:00 | 15 | 12
2017-07-22 19:30 | 14 | 11
2017-07-22 20:00 | 15 | 12
2017-07-22 20:30 | 15 | 12
2017-07-22 21:00 | 15 | 10
2017-07-22 21:30 | 15 | 10
2017-07-22 22:00 | 16 | 10
2017-07-22 22:30 | 15 | 8
2017-07-22 23:00 | 14 | 8
2017-07-22 23:30 | 15 | 8
2017-07-23 | 15 | 7
2017-07-23 00:30 | 14 | 5
2017-07-23 01:00 | 15 | 5
2017-07-23 01:30 | 16 | 5
2017-07-23 02:00 | 16 | 5
2017-07-23 02:30 | 16 | 4
2017-07-23 03:00 | 11 | 5
2017-07-23 03:30 | 8 | 6
2017-07-23 04:00 | 8 | 6
2017-07-23 04:30 | 7 | 5
2017-07-23 05:00 | 8 | 5
2017-07-23 05:30 | 7 | 4
2017-07-23 06:00 | 6 | 3
2017-07-23 06:30 | 5 | 2
2017-07-23 07:00 | 5 | 3
2017-07-23 07:30 | 7 | 5
2017-07-23 08:00 | 6 | 4
2017-07-23 08:30 | 6 | 5
2017-07-23 09:00 | 7 | 6
2017-07-23 09:30 | 6 | 5
2017-07-23 10:00 | 6 | 5
2017-07-23 10:30 | 5 | 5
2017-07-23 11:00 | 6 | 6
2017-07-23 11:30 | 5 | 4
2017-07-23 12:00 | 4 | 4
2017-07-23 12:30 | 5 | 5
2017-07-23 13:00 | 5 | 5
2017-07-23 13:30 | 6 | 5
2017-07-23 14:00 | 6 | 5
2017-07-23 14:30 | 8 | 7
2017-07-23 15:00 | 7 | 7
2017-07-23 15:30 | 8 | 8
2017-07-23 16:00 | 9 | 8
2017-07-23 16:30 | 10 | 10
2017-07-23 17:00 | 11 | 11
2017-07-23 17:30 | 15 | 15
2017-07-23 18:00 | 23 | 23
2017-07-23 18:30 | 26 | 26
2017-07-23 19:00 | 24 | 24
2017-07-23 19:30 | 19 | 19
2017-07-23 20:00 | 18 | 18
2017-07-23 20:30 | 15 | 15
2017-07-23 21:00 | 13 | 13
2017-07-23 21:30 | 11 | 11
2017-07-23 22:00 | 9 | 9
2017-07-23 22:30 | 6 | 6
2017-07-23 23:00 | 6 | 6
2017-07-23 23:30 | 5 | 5
2017-07-24 | 6 | 5
2017-07-24 00:30 | 7 | 5
2017-07-24 01:00 | 8 | 6
2017-07-24 01:30 | 7 | 5
2017-07-24 02:00 | 6 | 4
2017-07-24 02:30 | 7 | 5
2017-07-24 03:00 | 8 | 6
2017-07-24 03:30 | 7 | 6
2017-07-24 04:00 | 7 | 6
2017-07-24 04:30 | 8 | 7
2017-07-24 05:00 | 9 | 7
2017-07-24 05:30 | 9 | 7
2017-07-24 06:00 | 6 | 5
2017-07-24 06:30 | 8 | 7
2017-07-24 07:00 | 8 | 8
2017-07-24 07:30 | 10 | 10
2017-07-24 08:00 | 11 | 10
2017-07-24 08:30 | 11 | 10
2017-07-24 09:00 | 9 | 8
2017-07-24 09:30 | 9 | 8
2017-07-24 10:00 | 9 | 9
2017-07-24 10:30 | 10 | 9
2017-07-24 11:00 | 9 | 8
2017-07-24 11:30 | 9 | 8
2017-07-24 12:00 | 11 | 10
2017-07-24 12:30 | 11 | 10
2017-07-24 13:00 | 10 | 9
2017-07-24 13:30 | 10 | 10
2017-07-24 14:00 | 10 | 10
2017-07-24 14:30 | 11 | 10
2017-07-24 15:00 | 12 | 11
2017-07-24 15:30 | 12 | 12
2017-07-24 16:00 | 13 | 13
2017-07-24 16:30 | 14 | 13
2017-07-24 17:00 | 15 | 15
2017-07-24 17:30 | 16 | 16
2017-07-24 18:00 | 15 | 15
2017-07-24 18:30 | 17 | 17
2017-07-24 19:00 | 18 | 18
2017-07-24 19:30 | 18 | 18
2017-07-24 20:00 | 16 | 16
2017-07-24 20:30 | 16 | 16
2017-07-24 21:00 | 15 | 15
2017-07-24 21:30 | 14 | 14
2017-07-24 22:00 | 14 | 14
2017-07-24 22:30 | 13 | 13
2017-07-24 23:00 | 11 | 11
2017-07-24 23:30 | 11 | 9
2017-07-25 | 9 | 8
2017-07-25 00:30 | 9 | 7
2017-07-25 01:00 | 9 | 7
2017-07-25 01:30 | 10 | 8
2017-07-25 02:00 | 10 | 8
2017-07-25 02:30 | 11 | 9
2017-07-25 03:00 | 9 | 6
2017-07-25 03:30 | 10 | 8
2017-07-25 04:00 | 13 | 11
2017-07-25 04:30 | 15 | 12
2017-07-25 05:00 | 18 | 16
2017-07-25 05:30 | 21 | 19
2017-07-25 06:00 | 24 | 23
2017-07-25 06:30 | 28 | 27
2017-07-25 07:00 | 29 | 29
2017-07-25 07:30 | 30 | 29
2017-07-25 08:00 | 29 | 29
2017-07-25 08:30 | 28 | 28
2017-07-25 09:00 | 28 | 28
2017-07-25 09:30 | 28 | 28
2017-07-25 10:00 | 27 | 27
2017-07-25 10:30 | 27 | 27
2017-07-25 11:00 | 26 | 26
2017-07-25 11:30 | 26 | 26
2017-07-25 12:00 | 27 | 27
2017-07-25 12:30 | 26 | 26
2017-07-25 13:00 | 25 | 25
2017-07-25 13:30 | 25 | 25
2017-07-25 14:00 | 26 | 26
2017-07-25 14:30 | 27 | 27
2017-07-25 15:00 | 28 | 28
2017-07-25 15:30 | 29 | 29
2017-07-25 16:00 | 31 | 31
2017-07-25 16:30 | 31 | 31
2017-07-25 17:00 | 31 | 31
2017-07-25 17:30 | 32 | 32
2017-07-25 18:00 | 32 | 32
2017-07-25 18:30 | 35 | 35
2017-07-25 19:00 | 36 | 36
2017-07-25 19:30 | 34 | 34
2017-07-25 20:00 | 34 | 34
2017-07-25 20:30 | 34 | 34
2017-07-25 21:00 | 31 | 31
2017-07-25 21:30 | 28 | 28
2017-07-25 22:00 | 27 | 27
2017-07-25 22:30 | 24 | 24
2017-07-25 23:00 | 22 | 22
2017-07-25 23:30 | 20 | 20
2017-07-26 | 20 | 20
2017-07-26 00:30 | 19 | 19
2017-07-26 01:00 | 20 | 19
2017-07-26 01:30 | 20 | 20
2017-07-26 02:00 | 21 | 21
2017-07-26 02:30 | 19 | 19
2017-07-26 03:00 | 19 | 19
2017-07-26 03:30 | 15 | 14
2017-07-26 04:00 | 7 | 7
2017-07-26 04:30 | 7 | 6
2017-07-26 05:00 | 7 | 7
2017-07-26 05:30 | 9 | 8
2017-07-26 06:00 | 7 | 7
2017-07-26 06:30 | 10 | 10
2017-07-26 07:00 | 14 | 14
2017-07-26 07:30 | 16 | 15
2017-07-26 08:00 | 15 | 15
2017-07-26 08:30 | 15 | 14
2017-07-26 09:00 | 14 | 13
2017-07-26 09:30 | 14 | 12
2017-07-26 10:00 | 15 | 12
2017-07-26 10:30 | 15 | 12
2017-07-26 11:00 | 14 | 11
2017-07-26 11:30 | 15 | 11
2017-07-26 12:00 | 15 | 12
2017-07-26 12:30 | 15 | 12
2017-07-26 13:00 | 14 | 12
2017-07-26 13:30 | 16 | 13
2017-07-26 14:00 | 17 | 15
2017-07-26 14:30 | 16 | 14
2017-07-26 15:00 | 16 | 13
2017-07-26 15:30 | 18 | 15
2017-07-26 16:00 | 19 | 17
2017-07-26 16:30 | 20 | 18
2017-07-26 17:00 | 21 | 19
2017-07-26 17:30 | 19 | 19
2017-07-26 18:00 | 20 | 20
2017-07-26 18:30 | 22 | 22
2017-07-26 19:00 | 23 | 23
2017-07-26 19:30 | 24 | 24
2017-07-26 20:00 | 22 | 22
2017-07-26 20:30 | 20 | 20
2017-07-26 21:00 | 20 | 20
2017-07-26 21:30 | 18 | 18
2017-07-26 22:00 | 17 | 17
2017-07-26 22:30 | 15 | 15
2017-07-26 23:00 | 15 | 14
2017-07-26 23:30 | 13 | 12
2017-07-27 | 11 | 10
2017-07-27 00:30 | 10 | 8
2017-07-27 01:00 | 11 | 9
2017-07-27 01:30 | 9 | 7
2017-07-27 02:00 | 9 | 7
2017-07-27 02:30 | 10 | 7
2017-07-27 03:00 | 11 | 9
2017-07-27 03:30 | 10 | 8
2017-07-27 04:00 | 10 | 8
2017-07-27 04:30 | 11 | 9
2017-07-27 05:00 | 10 | 9
2017-07-27 05:30 | 11 | 10
2017-07-27 06:00 | 12 | 11
2017-07-27 06:30 | 14 | 13
2017-07-27 07:00 | 15 | 15
2017-07-27 07:30 | 17 | 17
2017-07-27 08:00 | 17 | 17
2017-07-27 08:30 | 16 | 16
2017-07-27 09:00 | 15 | 15
2017-07-27 09:30 | 15 | 15
2017-07-27 10:00 | 13 | 13
2017-07-27 10:30 | 13 | 13
2017-07-27 11:00 | 13 | 13
2017-07-27 11:30 | 13 | 13
2017-07-27 12:00 | 14 | 14
2017-07-27 12:30 | 14 | 14
2017-07-27 13:00 | 15 | 14
2017-07-27 13:30 | 14 | 14
2017-07-27 14:00 | 16 | 16
2017-07-27 14:30 | 17 | 16
2017-07-27 15:00 | 15 | 15
2017-07-27 15:30 | 16 | 15
2017-07-27 16:00 | 16 | 16
2017-07-27 16:30 | 17 | 17
2017-07-27 17:00 | 20 | 19
2017-07-27 17:30 | 20 | 20
2017-07-27 18:00 | 27 | 27
2017-07-27 18:30 | 37 | 37
2017-07-27 19:00 | 25 | 25
2017-07-27 19:30 | 22 | 21
2017-07-27 20:00 | 21 | 21
2017-07-27 20:30 | 21 | 21
2017-07-27 21:00 | 20 | 20
2017-07-27 21:30 | 18 | 18
2017-07-27 22:00 | 17 | 17
2017-07-27 22:30 | 17 | 17
2017-07-27 23:00 | 20 | 20
2017-07-27 23:30 | 24 | 24
2017-07-28 | 24 | 24
2017-07-28 00:30 | 29 | 28
2017-07-28 01:00 | 27 | 27
2017-07-28 01:30 | 27 | 27
2017-07-28 02:00 | 28 | 27
2017-07-28 02:30 | 29 | 28
2017-07-28 03:00 | 28 | 27
2017-07-28 03:30 | 29 | 29
2017-07-28 04:00 | 31 | 30
2017-07-28 04:30 | 30 | 29
2017-07-28 05:00 | 30 | 29
2017-07-28 05:30 | 32 | 31
2017-07-28 06:00 | 31 | 31
2017-07-28 06:30 | 34 | 33
2017-07-28 07:00 | 37 | 36
2017-07-28 07:30 | 39 | 39
2017-07-28 08:00 | 34 | 34
2017-07-28 08:30 | 39 | 38
2017-07-28 09:00 | 46 | 46
2017-07-28 09:30 | 48 | 47
2017-07-28 10:00 | 36 | 31
2017-07-28 10:30 | 33 | 20
2017-07-28 11:00 | 48 | 42
2017-07-28 11:30 | 50 | 44
2017-07-28 12:00 | 50 | 45
2017-07-28 12:30 | 51 | 46
2017-07-28 13:00 | 48 | 43
2017-07-28 13:30 | 47 | 41
2017-07-28 14:00 | 48 | 43
2017-07-28 14:30 | 49 | 44
2017-07-28 15:00 | 51 | 45
2017-07-28 15:30 | 51 | 45
2017-07-28 16:00 | 53 | 47
2017-07-28 16:30 | 53 | 48
2017-07-28 17:00 | 53 | 48
2017-07-28 17:30 | 55 | 50
2017-07-28 18:00 | 55 | 49
2017-07-28 18:30 | 48 | 31
2017-07-28 19:00 | 46 | 26
2017-07-28 19:30 | 47 | 30
2017-07-28 20:00 | 45 | 22
2017-07-28 20:30 | 28 | 22
2017-07-28 21:00 | 28 | 22
2017-07-28 21:30 | 27 | 20
2017-07-28 22:00 | 25 | 18
2017-07-28 22:30 | 25 | 16
2017-07-28 23:00 | 25 | 16
2017-07-28 23:30 | 24 | 14
2017-07-29 | 23 | 15
2017-07-29 00:30 | 34 | 32
2017-07-29 01:00 | 33 | 32
2017-07-29 01:30 | 33 | 32
2017-07-29 02:00 | 33 | 32
2017-07-29 02:30 | 32 | 31
2017-07-29 03:00 | 32 | 30
2017-07-29 03:30 | 31 | 29
2017-07-29 04:00 | 33 | 32
2017-07-29 04:30 | 33 | 32
2017-07-29 05:00 | 32 | 31
2017-07-29 05:30 | 32 | 31
2017-07-29 06:00 | 33 | 32
2017-07-29 06:30 | 32 | 30
2017-07-29 07:00 | 32 | 31
2017-07-29 07:30 | 36 | 35
2017-07-29 08:00 | 36 | 35
2017-07-29 08:30 | 36 | 35
2017-07-29 09:00 | 35 | 34
2017-07-29 09:30 | 35 | 34
2017-07-29 10:00 | 35 | 34
2017-07-29 10:30 | 34 | 34
2017-07-29 11:00 | 34 | 34
2017-07-29 11:30 | 35 | 34
2017-07-29 12:00 | 34 | 33
2017-07-29 12:30 | 33 | 32
2017-07-29 13:00 | 34 | 33
2017-07-29 13:30 | 37 | 37
2017-07-29 14:00 | 41 | 40
2017-07-29 14:30 | 42 | 41
2017-07-29 15:00 | 43 | 42
2017-07-29 15:30 | 44 | 44
2017-07-29 16:00 | 50 | 50
2017-07-29 16:30 | 49 | 49
2017-07-29 17:00 | 47 | 47
2017-07-29 17:30 | 48 | 48
2017-07-29 18:00 | 39 | 38
2017-07-29 18:30 | 45 | 45
2017-07-29 19:00 | 43 | 43
2017-07-29 19:30 | 27 | 25
2017-07-29 20:00 | 37 | 37
2017-07-29 20:30 | 47 | 47
2017-07-29 21:00 | 46 | 46
2017-07-29 21:30 | 46 | 46
2017-07-29 22:00 | 29 | 26
2017-07-29 22:30 | 28 | 26
2017-07-29 23:00 | 27 | 24
2017-07-29 23:30 | 24 | 20
2017-07-30 | 30 | 28
2017-07-30 00:30 | 39 | 38
2017-07-30 01:00 | 39 | 39
2017-07-30 01:30 | 39 | 39
2017-07-30 02:00 | 41 | 41
2017-07-30 02:30 | 42 | 42
2017-07-30 03:00 | 43 | 43
2017-07-30 03:30 | 44 | 44
2017-07-30 04:00 | 43 | 43
2017-07-30 04:30 | 44 | 44
2017-07-30 05:00 | 42 | 42
2017-07-30 05:30 | 44 | 44
2017-07-30 06:00 | 46 | 46
2017-07-30 06:30 | 46 | 46
2017-07-30 07:00 | 46 | 46
2017-07-30 07:30 | 47 | 47
2017-07-30 08:00 | 48 | 48
2017-07-30 08:30 | 48 | 48
2017-07-30 09:00 | 49 | 49
2017-07-30 09:30 | 52 | 51
2017-07-30 10:00 | 52 | 52
2017-07-30 10:30 | 52 | 51
2017-07-30 11:00 | 52 | 52
2017-07-30 11:30 | 53 | 52
2017-07-30 12:00 | 51 | 51
2017-07-30 12:30 | 50 | 50
2017-07-30 13:00 | 52 | 51
2017-07-30 13:30 | 54 | 53
2017-07-30 14:00 | 54 | 54
2017-07-30 14:30 | 52 | 52
2017-07-30 15:00 | 53 | 53
2017-07-30 15:30 | 55 | 55
2017-07-30 16:00 | 55 | 55
2017-07-30 16:30 | 56 | 56
2017-07-30 17:00 | 58 | 57
2017-07-30 17:30 | 58 | 57
2017-07-30 18:00 | 58 | 57
2017-07-30 18:30 | 61 | 60
2017-07-30 19:00 | 62 | 60
2017-07-30 19:30 | 61 | 59
2017-07-30 20:00 | 61 | 58
2017-07-30 20:30 | 59 | 57
2017-07-30 21:00 | 56 | 55
2017-07-30 21:30 | 54 | 53
2017-07-30 22:00 | 53 | 52
2017-07-30 22:30 | 50 | 49
2017-07-30 23:00 | 48 | 46
2017-07-30 23:30 | 48 | 46
2017-07-31 | 48 | 46
2017-07-31 00:30 | 48 | 45
2017-07-31 01:00 | 47 | 44
2017-07-31 01:30 | 47 | 44
2017-07-31 02:00 | 47 | 44
2017-07-31 02:30 | 46 | 42
2017-07-31 03:00 | 46 | 43
2017-07-31 03:30 | 47 | 43
2017-07-31 04:00 | 47 | 43
2017-07-31 04:30 | 48 | 44
2017-07-31 05:00 | 49 | 45
2017-07-31 05:30 | 50 | 46
2017-07-31 06:00 | 49 | 46
2017-07-31 06:30 | 51 | 48
2017-07-31 07:00 | 53 | 51
2017-07-31 07:30 | 53 | 52
2017-07-31 08:00 | 54 | 54
2017-07-31 08:30 | 54 | 53
2017-07-31 09:00 | 55 | 55
2017-07-31 09:30 | 55 | 54
2017-07-31 10:00 | 54 | 54
2017-07-31 10:30 | 55 | 54
2017-07-31 11:00 | 54 | 54
2017-07-31 11:30 | 70 | 70
2017-07-31 12:00 | 66 | 65
2017-07-31 12:30 | 63 | 63
2017-07-31 13:00 | 64 | 64
2017-07-31 13:30 | 62 | 61
2017-07-31 14:00 | 62 | 61
2017-07-31 14:30 | 64 | 62
2017-07-31 15:00 | 62 | 60
2017-07-31 15:30 | 65 | 63
2017-07-31 16:00 | 65 | 62
2017-07-31 16:30 | 67 | 63
2017-07-31 17:00 | 67 | 63
2017-07-31 17:30 | 67 | 63
2017-07-31 18:00 | 52 | 49
2017-07-31 18:30 | 42 | 41
2017-07-31 19:00 | 43 | 42
2017-07-31 19:30 | 45 | 44
2017-07-31 20:00 | 60 | 60
2017-07-31 20:30 | 53 | 53
2017-07-31 21:00 | 52 | 52
2017-07-31 21:30 | 52 | 52
2017-07-31 22:00 | 50 | 50
2017-07-31 22:30 | 50 | 50
2017-07-31 23:00 | 50 | 49
2017-07-31 23:30 | 47 | 47
2017-08-01 | 44 | 44
2017-08-01 00:30 | 46 | 45
2017-08-01 01:00 | 46 | 46
2017-08-01 01:30 | 46 | 46
2017-08-01 02:00 | 46 | 45
2017-08-01 02:30 | 46 | 45
2017-08-01 03:00 | 47 | 46
2017-08-01 03:30 | 45 | 45
2017-08-01 04:00 | 45 | 44
2017-08-01 04:30 | 45 | 45
2017-08-01 05:00 | 45 | 44
2017-08-01 05:30 | 43 | 42
2017-08-01 06:00 | 44 | 43
2017-08-01 06:30 | 42 | 42
2017-08-01 07:00 | 31 | 30
2017-08-01 07:30 | 34 | 34
2017-08-01 08:00 | 42 | 41
2017-08-01 08:30 | 54 | 52
2017-08-01 09:00 | 53 | 51
2017-08-01 09:30 | 55 | 52
2017-08-01 10:00 | 60 | 57
2017-08-01 10:30 | 57 | 55
2017-08-01 11:00 | 56 | 53
2017-08-01 11:30 | 54 | 51
2017-08-01 12:00 | 42 | 40
2017-08-01 12:30 | 17 | 16
2017-08-01 13:00 | 17 | 16
2017-08-01 13:30 | 18 | 17
2017-08-01 14:00 | 19 | 19
2017-08-01 14:30 | 42 | 40
2017-08-01 15:00 | 49 | 46
2017-08-01 15:30 | 50 | 47
2017-08-01 16:00 | 51 | 48
2017-08-01 16:30 | 53 | 51
2017-08-01 17:00 | 55 | 53
2017-08-01 17:30 | 54 | 51
2017-08-01 18:00 | 45 | 44
2017-08-01 18:30 | 39 | 39
2017-08-01 19:00 | 36 | 36
2017-08-01 19:30 | 52 | 51
2017-08-01 20:00 | 58 | 55
2017-08-01 20:30 | 57 | 55
2017-08-01 21:00 | 55 | 53
2017-08-01 21:30 | 54 | 52
2017-08-01 22:00 | 53 | 51
2017-08-01 22:30 | 49 | 48
2017-08-01 23:00 | 47 | 46
2017-08-01 23:30 | 47 | 45
2017-08-02 | 46 | 45
2017-08-02 00:30 | 50 | 49
2017-08-02 01:00 | 47 | 46
2017-08-02 01:30 | 47 | 46
2017-08-02 02:00 | 46 | 45
2017-08-02 02:30 | 45 | 45
2017-08-02 03:00 | 45 | 44
2017-08-02 03:30 | 47 | 46
2017-08-02 04:00 | 47 | 46
2017-08-02 04:30 | 46 | 46
2017-08-02 05:00 | 46 | 45
2017-08-02 05:30 | 45 | 44
2017-08-02 06:00 | 46 | 45
2017-08-02 06:30 | 49 | 48
2017-08-02 07:00 | 33 | 33
2017-08-02 07:30 | 50 | 50
2017-08-02 08:00 | 62 | 61
2017-08-02 08:30 | 60 | 60
2017-08-02 09:00 | 41 | 40
2017-08-02 09:30 | 39 | 39
2017-08-02 10:00 | 39 | 39
2017-08-02 10:30 | 38 | 38
2017-08-02 11:00 | 40 | 40
2017-08-02 11:30 | 40 | 39
2017-08-02 12:00 | 40 | 40
2017-08-02 12:30 | 42 | 41
2017-08-02 13:00 | 42 | 41
2017-08-02 13:30 | 42 | 42
2017-08-02 14:00 | 45 | 45
2017-08-02 14:30 | 45 | 44
2017-08-02 15:00 | 43 | 43
2017-08-02 15:30 | 43 | 42
2017-08-02 16:00 | 43 | 42
2017-08-02 16:30 | 49 | 49
2017-08-02 17:00 | 60 | 59
2017-08-02 17:30 | 65 | 64
2017-08-02 18:00 | 69 | 68
2017-08-02 18:30 | 64 | 63
2017-08-02 19:00 | 59 | 59
2017-08-02 19:30 | 60 | 59
2017-08-02 20:00 | 59 | 58
2017-08-02 20:30 | 58 | 57
2017-08-02 21:00 | 57 | 56
2017-08-02 21:30 | 58 | 57
2017-08-02 22:00 | 55 | 54
2017-08-02 22:30 | 51 | 51
2017-08-02 23:00 | 50 | 49
2017-08-02 23:30 | 49 | 48
2017-08-03 | 45 | 45
2017-08-03 00:30 | 45 | 44
2017-08-03 01:00 | 44 | 43
2017-08-03 01:30 | 44 | 43
2017-08-03 02:00 | 44 | 43
2017-08-03 02:30 | 45 | 45
2017-08-03 03:00 | 45 | 45
2017-08-03 03:30 | 46 | 45
2017-08-03 04:00 | 45 | 44
2017-08-03 04:30 | 45 | 45
2017-08-03 05:00 | 43 | 42
2017-08-03 05:30 | 47 | 46
2017-08-03 06:00 | 50 | 49
2017-08-03 06:30 | 54 | 52
2017-08-03 07:00 | 44 | 44
2017-08-03 07:30 | 40 | 40
2017-08-03 08:00 | 17 | 15
2017-08-03 08:30 | 11 | 10
2017-08-03 09:00 | 11 | 11
2017-08-03 09:30 | 12 | 11
2017-08-03 10:00 | 12 | 11
2017-08-03 10:30 | 12 | 11
2017-08-03 11:00 | 12 | 12
2017-08-03 11:30 | 12 | 12
2017-08-03 12:00 | 13 | 12
2017-08-03 12:30 | 34 | 32
2017-08-03 13:00 | 49 | 45
2017-08-03 13:30 | 52 | 49
2017-08-03 14:00 | 53 | 51
2017-08-03 14:30 | 57 | 55
2017-08-03 15:00 | 57 | 55
2017-08-03 15:30 | 55 | 53
2017-08-03 16:00 | 65 | 63
2017-08-03 16:30 | 69 | 68
2017-08-03 17:00 | 71 | 69
2017-08-03 17:30 | 74 | 73
2017-08-03 18:00 | 58 | 57
2017-08-03 18:30 | 66 | 66
2017-08-03 19:00 | 72 | 71
2017-08-03 19:30 | 73 | 72
2017-08-03 20:00 | 71 | 71
2017-08-03 20:30 | 70 | 69
2017-08-03 21:00 | 68 | 68
2017-08-03 21:30 | 68 | 67
2017-08-03 22:00 | 66 | 65
2017-08-03 22:30 | 64 | 63
2017-08-03 23:00 | 59 | 58
2017-08-03 23:30 | 57 | 56
2017-08-04 | 59 | 58
2017-08-04 00:30 | 62 | 61
2017-08-04 01:00 | 61 | 60
2017-08-04 01:30 | 60 | 59
2017-08-04 02:00 | 58 | 57
2017-08-04 02:30 | 58 | 57
2017-08-04 03:00 | 57 | 55
2017-08-04 03:30 | 56 | 55
2017-08-04 04:00 | 55 | 54
2017-08-04 04:30 | 53 | 52
2017-08-04 05:00 | 52 | 50
2017-08-04 05:30 | 54 | 53
2017-08-04 06:00 | 54 | 52
2017-08-04 06:30 | 57 | 55
2017-08-04 07:00 | 58 | 57
2017-08-04 07:30 | 60 | 59
2017-08-04 08:00 | 59 | 58
2017-08-04 08:30 | 63 | 62
2017-08-04 09:00 | 63 | 62
2017-08-04 09:30 | 62 | 61
2017-08-04 10:00 | 58 | 57
2017-08-04 10:30 | 57 | 56
2017-08-04 11:00 | 57 | 56
2017-08-04 11:30 | 57 | 55
2017-08-04 12:00 | 56 | 55
2017-08-04 12:30 | 56 | 55
2017-08-04 13:00 | 57 | 56
2017-08-04 13:30 | 57 | 56
2017-08-04 14:00 | 56 | 55
2017-08-04 14:30 | 56 | 55
2017-08-04 15:00 | 57 | 55
2017-08-04 15:30 | 58 | 57
2017-08-04 16:00 | 57 | 56
2017-08-04 16:30 | 56 | 55
2017-08-04 17:00 | 57 | 56
2017-08-04 17:30 | 58 | 57
2017-08-04 18:00 | 57 | 56
2017-08-04 18:30 | 58 | 57
2017-08-04 19:00 | 58 | 57
2017-08-04 19:30 | 58 | 57
2017-08-04 20:00 | 54 | 53
2017-08-04 20:30 | 52 | 51
2017-08-04 21:00 | 51 | 50
2017-08-04 21:30 | 49 | 48
2017-08-04 22:00 | 49 | 48
2017-08-04 22:30 | 47 | 46
2017-08-04 23:00 | 45 | 44
2017-08-04 23:30 | 45 | 44
2017-08-05 | 45 | 43
2017-08-05 00:30 | 45 | 43
2017-08-05 01:00 | 48 | 46
2017-08-05 01:30 | 51 | 48
2017-08-05 02:00 | 51 | 47
2017-08-05 02:30 | 51 | 47
2017-08-05 03:00 | 48 | 44
2017-08-05 03:30 | 46 | 42
2017-08-05 04:00 | 46 | 42
2017-08-05 04:30 | 46 | 42
2017-08-05 05:00 | 46 | 42
2017-08-05 05:30 | 43 | 40
2017-08-05 06:00 | 44 | 40
2017-08-05 06:30 | 46 | 43
2017-08-05 07:00 | 47 | 43
2017-08-05 07:30 | 49 | 46
2017-08-05 08:00 | 56 | 53
2017-08-05 08:30 | 58 | 56
2017-08-05 09:00 | 57 | 55
2017-08-05 09:30 | 54 | 53
2017-08-05 10:00 | 50 | 49
2017-08-05 10:30 | 50 | 49
2017-08-05 11:00 | 51 | 50
2017-08-05 11:30 | 56 | 55
2017-08-05 12:00 | 62 | 60
2017-08-05 12:30 | 61 | 59
2017-08-05 13:00 | 61 | 60
2017-08-05 13:30 | 62 | 60
2017-08-05 14:00 | 61 | 60
2017-08-05 14:30 | 62 | 60
2017-08-05 15:00 | 58 | 57
2017-08-05 15:30 | 58 | 57
2017-08-05 16:00 | 59 | 57
2017-08-05 16:30 | 58 | 57
2017-08-05 17:00 | 59 | 58
2017-08-05 17:30 | 61 | 59
2017-08-05 18:00 | 62 | 61
2017-08-05 18:30 | 61 | 60
2017-08-05 19:00 | 60 | 59
2017-08-05 19:30 | 54 | 53
2017-08-05 20:00 | 52 | 51
2017-08-05 20:30 | 51 | 51
2017-08-05 21:00 | 51 | 51
2017-08-05 21:30 | 51 | 50
2017-08-05 22:00 | 50 | 49
2017-08-05 22:30 | 48 | 47
2017-08-05 23:00 | 45 | 44
2017-08-05 23:30 | 44 | 43
2017-08-06 | 43 | 42
2017-08-06 00:30 | 43 | 42
2017-08-06 01:00 | 44 | 42
2017-08-06 01:30 | 43 | 42
2017-08-06 02:00 | 44 | 43
2017-08-06 02:30 | 43 | 42
2017-08-06 03:00 | 42 | 40
2017-08-06 03:30 | 43 | 41
2017-08-06 04:00 | 44 | 43
2017-08-06 04:30 | 44 | 42
2017-08-06 05:00 | 43 | 41
2017-08-06 05:30 | 43 | 42
2017-08-06 06:00 | 43 | 42
2017-08-06 06:30 | 44 | 42
2017-08-06 07:00 | 44 | 43
2017-08-06 07:30 | 47 | 45
2017-08-06 08:00 | 46 | 44
2017-08-06 08:30 | 47 | 45
2017-08-06 09:00 | 47 | 46
2017-08-06 09:30 | 47 | 45
2017-08-06 10:00 | 46 | 45
2017-08-06 10:30 | 47 | 46
2017-08-06 11:00 | 48 | 47
2017-08-06 11:30 | 47 | 46
2017-08-06 12:00 | 48 | 47
2017-08-06 12:30 | 47 | 45
2017-08-06 13:00 | 46 | 45
2017-08-06 13:30 | 47 | 46
2017-08-06 14:00 | 50 | 48
2017-08-06 14:30 | 49 | 48
2017-08-06 15:00 | 49 | 47
2017-08-06 15:30 | 50 | 49
2017-08-06 16:00 | 50 | 49
2017-08-06 16:30 | 51 | 49
2017-08-06 17:00 | 51 | 49
2017-08-06 17:30 | 51 | 50
2017-08-06 18:00 | 50 | 48
2017-08-06 18:30 | 52 | 50
2017-08-06 19:00 | 53 | 51
2017-08-06 19:30 | 53 | 51
2017-08-06 20:00 | 52 | 50
2017-08-06 20:30 | 52 | 50
2017-08-06 21:00 | 53 | 50
2017-08-06 21:30 | 51 | 48
2017-08-06 22:00 | 52 | 48
2017-08-06 22:30 | 50 | 47
2017-08-06 23:00 | 47 | 43
2017-08-06 23:30 | 48 | 43
2017-08-07 | 47 | 43
2017-08-07 00:30 | 45 | 43
2017-08-07 01:00 | 44 | 42
2017-08-07 01:30 | 45 | 42
2017-08-07 02:00 | 45 | 42
2017-08-07 02:30 | 45 | 43
2017-08-07 03:00 | 45 | 43
2017-08-07 03:30 | 47 | 44
2017-08-07 04:00 | 47 | 45
2017-08-07 04:30 | 46 | 44
2017-08-07 05:00 | 48 | 46
2017-08-07 05:30 | 47 | 44
2017-08-07 06:00 | 47 | 45
2017-08-07 06:30 | 50 | 49
2017-08-07 07:00 | 49 | 46
2017-08-07 07:30 | 54 | 53
2017-08-07 08:00 | 54 | 54
2017-08-07 08:30 | 55 | 55
2017-08-07 09:00 | 55 | 55
2017-08-07 09:30 | 54 | 54
2017-08-07 10:00 | 53 | 53
2017-08-07 10:30 | 52 | 52
2017-08-07 11:00 | 53 | 53
2017-08-07 11:30 | 52 | 52
2017-08-07 12:00 | 51 | 50
2017-08-07 12:30 | 50 | 50
2017-08-07 13:00 | 53 | 53
2017-08-07 13:30 | 55 | 55
2017-08-07 14:00 | 58 | 58
2017-08-07 14:30 | 58 | 58
2017-08-07 15:00 | 57 | 57
2017-08-07 15:30 | 58 | 58
2017-08-07 16:00 | 58 | 58
2017-08-07 16:30 | 58 | 58
2017-08-07 17:00 | 58 | 58
2017-08-07 17:30 | 59 | 59
2017-08-07 18:00 | 60 | 60
2017-08-07 18:30 | 55 | 54
2017-08-07 19:00 | 62 | 62
2017-08-07 19:30 | 62 | 62
2017-08-07 20:00 | 61 | 61
2017-08-07 20:30 | 61 | 60
2017-08-07 21:00 | 54 | 53
2017-08-07 21:30 | 52 | 51
2017-08-07 22:00 | 51 | 50
2017-08-07 22:30 | 49 | 47
2017-08-07 23:00 | 46 | 45
2017-08-07 23:30 | 46 | 45
2017-08-08 | 46 | 45
2017-08-08 00:30 | 45 | 43
2017-08-08 01:00 | 45 | 44
2017-08-08 01:30 | 45 | 43
2017-08-08 02:00 | 44 | 43
2017-08-08 02:30 | 44 | 42
2017-08-08 03:00 | 45 | 43
2017-08-08 03:30 | 45 | 43
2017-08-08 04:00 | 45 | 43
2017-08-08 04:30 | 44 | 42
2017-08-08 05:00 | 46 | 45
2017-08-08 05:30 | 45 | 44
2017-08-08 06:00 | 45 | 44
2017-08-08 06:30 | 47 | 45
2017-08-08 07:00 | 37 | 28
2017-08-08 07:30 | 45 | 43
2017-08-08 08:00 | 49 | 49
2017-08-08 08:30 | 48 | 48
2017-08-08 09:00 | 46 | 46
2017-08-08 09:30 | 46 | 46
2017-08-08 10:00 | 46 | 46
2017-08-08 10:30 | 44 | 44
2017-08-08 11:00 | 44 | 44
2017-08-08 11:30 | 45 | 44
2017-08-08 12:00 | 46 | 46
2017-08-08 12:30 | 45 | 45
2017-08-08 13:00 | 46 | 46
2017-08-08 13:30 | 47 | 47
2017-08-08 14:00 | 48 | 48
2017-08-08 14:30 | 48 | 48
2017-08-08 15:00 | 51 | 51
2017-08-08 15:30 | 43 | 36
2017-08-08 16:00 | 48 | 43
2017-08-08 16:30 | 59 | 59
2017-08-08 17:00 | 59 | 59
2017-08-08 17:30 | 57 | 56
2017-08-08 18:00 | 63 | 62
2017-08-08 18:30 | 63 | 61
2017-08-08 19:00 | 58 | 57
2017-08-08 19:30 | 54 | 53
2017-08-08 20:00 | 53 | 52
2017-08-08 20:30 | 51 | 50
2017-08-08 21:00 | 52 | 51
2017-08-08 21:30 | 51 | 50
2017-08-08 22:00 | 50 | 49
2017-08-08 22:30 | 48 | 46
2017-08-08 23:00 | 47 | 45
2017-08-08 23:30 | 47 | 45
2017-08-09 | 47 | 45
2017-08-09 00:30 | 46 | 44
2017-08-09 01:00 | 44 | 44
2017-08-09 01:30 | 45 | 44
2017-08-09 02:00 | 44 | 43
2017-08-09 02:30 | 43 | 42
2017-08-09 03:00 | 45 | 44
2017-08-09 03:30 | 45 | 44
2017-08-09 04:00 | 44 | 43
2017-08-09 04:30 | 44 | 43
2017-08-09 05:00 | 46 | 45
2017-08-09 05:30 | 46 | 45
2017-08-09 06:00 | 46 | 45
2017-08-09 06:30 | 48 | 46
2017-08-09 07:00 | 29 | 29
2017-08-09 07:30 | 42 | 40
2017-08-09 08:00 | 47 | 47
2017-08-09 08:30 | 49 | 48
2017-08-09 09:00 | 51 | 50
2017-08-09 09:30 | 52 | 51
2017-08-09 10:00 | 53 | 52
2017-08-09 10:30 | 52 | 52
2017-08-09 11:00 | 53 | 52
2017-08-09 11:30 | 53 | 53
2017-08-09 12:00 | 54 | 54
2017-08-09 12:30 | 55 | 54
2017-08-09 13:00 | 49 | 49
2017-08-09 13:30 | 48 | 47
2017-08-09 14:00 | 48 | 48
2017-08-09 14:30 | 51 | 51
2017-08-09 15:00 | 53 | 53
2017-08-09 15:30 | 55 | 54
2017-08-09 16:00 | 55 | 55
2017-08-09 16:30 | 55 | 55
2017-08-09 17:00 | 52 | 51
2017-08-09 17:30 | 52 | 52
2017-08-09 18:00 | 52 | 52
2017-08-09 18:30 | 53 | 52
2017-08-09 19:00 | 38 | 37
2017-08-09 19:30 | 41 | 40
2017-08-09 20:00 | 55 | 51
2017-08-09 20:30 | 55 | 51
2017-08-09 21:00 | 54 | 51
2017-08-09 21:30 | 52 | 50
2017-08-09 22:00 | 49 | 47
2017-08-09 22:30 | 46 | 45
2017-08-09 23:00 | 46 | 44
2017-08-09 23:30 | 45 | 43
2017-08-10 | 44 | 42
2017-08-10 00:30 | 45 | 43
2017-08-10 01:00 | 44 | 43
2017-08-10 01:30 | 42 | 40
2017-08-10 02:00 | 44 | 43
2017-08-10 02:30 | 42 | 42
2017-08-10 03:00 | 42 | 41
2017-08-10 03:30 | 42 | 41
2017-08-10 04:00 | 45 | 44
2017-08-10 04:30 | 46 | 45
2017-08-10 05:00 | 47 | 47
2017-08-10 05:30 | 51 | 50
2017-08-10 06:00 | 53 | 53
2017-08-10 06:30 | 54 | 53
2017-08-10 07:00 | 33 | 33
2017-08-10 07:30 | 46 | 46
2017-08-10 08:00 | 47 | 39
2017-08-10 08:30 | 46 | 38
2017-08-10 09:00 | 44 | 36
2017-08-10 09:30 | 43 | 37
2017-08-10 10:00 | 43 | 36
2017-08-10 10:30 | 41 | 35
2017-08-10 11:00 | 43 | 40
2017-08-10 11:30 | 44 | 41
2017-08-10 12:00 | 47 | 45
2017-08-10 12:30 | 50 | 49
2017-08-10 13:00 | 52 | 51
2017-08-10 13:30 | 53 | 53
2017-08-10 14:00 | 53 | 53
2017-08-10 14:30 | 54 | 53
2017-08-10 15:00 | 53 | 53
2017-08-10 15:30 | 56 | 56
2017-08-10 16:00 | 57 | 56
2017-08-10 16:30 | 56 | 55
2017-08-10 17:00 | 56 | 56
2017-08-10 17:30 | 55 | 55
2017-08-10 18:00 | 54 | 54
2017-08-10 18:30 | 52 | 51
2017-08-10 19:00 | 52 | 51
2017-08-10 19:30 | 52 | 50
2017-08-10 20:00 | 52 | 50
2017-08-10 20:30 | 52 | 49
2017-08-10 21:00 | 49 | 46
2017-08-10 21:30 | 47 | 45
2017-08-10 22:00 | 45 | 44
2017-08-10 22:30 | 46 | 44
2017-08-10 23:00 | 48 | 46
2017-08-10 23:30 | 48 | 46
2017-08-11 | 45 | 43
2017-08-11 00:30 | 42 | 42
2017-08-11 01:00 | 41 | 41
2017-08-11 01:30 | 41 | 41
2017-08-11 02:00 | 42 | 41
2017-08-11 02:30 | 42 | 41
2017-08-11 03:00 | 42 | 42
2017-08-11 03:30 | 43 | 43
2017-08-11 04:00 | 44 | 43
2017-08-11 04:30 | 43 | 42
2017-08-11 05:00 | 43 | 42
2017-08-11 05:30 | 40 | 40
2017-08-11 06:00 | 22 | 22
2017-08-11 06:30 | 21 | 21
2017-08-11 07:00 | 22 | 22
2017-08-11 07:30 | 24 | 24
2017-08-11 08:00 | 38 | 37
2017-08-11 08:30 | 47 | 47
2017-08-11 09:00 | 43 | 42
2017-08-11 09:30 | 40 | 40
2017-08-11 10:00 | 41 | 41
2017-08-11 10:30 | 45 | 44
2017-08-11 11:00 | 45 | 45
2017-08-11 11:30 | 44 | 44
2017-08-11 12:00 | 45 | 44
2017-08-11 12:30 | 45 | 45
2017-08-11 13:00 | 45 | 44
2017-08-11 13:30 | 44 | 44
2017-08-11 14:00 | 45 | 45
2017-08-11 14:30 | 46 | 45
2017-08-11 15:00 | 46 | 46
2017-08-11 15:30 | 48 | 47
2017-08-11 16:00 | 49 | 49
2017-08-11 16:30 | 51 | 50
2017-08-11 17:00 | 49 | 49
2017-08-11 17:30 | 48 | 48
2017-08-11 18:00 | 48 | 48
2017-08-11 18:30 | 48 | 48
2017-08-11 19:00 | 48 | 48
2017-08-11 19:30 | 48 | 48
2017-08-11 20:00 | 48 | 47
2017-08-11 20:30 | 46 | 45
2017-08-11 21:00 | 45 | 45
2017-08-11 21:30 | 44 | 44
2017-08-11 22:00 | 44 | 43
2017-08-11 22:30 | 43 | 42
2017-08-11 23:00 | 43 | 41
2017-08-11 23:30 | 42 | 41
2017-08-12 | 41 | 41
2017-08-12 00:30 | 42 | 41
2017-08-12 01:00 | 42 | 41
2017-08-12 01:30 | 42 | 40
2017-08-12 02:00 | 41 | 40
2017-08-12 02:30 | 41 | 40
2017-08-12 03:00 | 41 | 40
2017-08-12 03:30 | 41 | 39
2017-08-12 04:00 | 42 | 40
2017-08-12 04:30 | 41 | 40
2017-08-12 05:00 | 42 | 41
2017-08-12 05:30 | 43 | 42
2017-08-12 06:00 | 43 | 42
2017-08-12 06:30 | 42 | 41
2017-08-12 07:00 | 41 | 40
2017-08-12 07:30 | 42 | 41
2017-08-12 08:00 | 43 | 42
2017-08-12 08:30 | 45 | 43
2017-08-12 09:00 | 44 | 40
2017-08-12 09:30 | 24 | 3
2017-08-12 10:00 | 26 | 9
2017-08-12 10:30 | 33 | 25
2017-08-12 11:00 | 45 | 41
2017-08-12 11:30 | 44 | 40
2017-08-12 12:00 | 45 | 41
2017-08-12 12:30 | 45 | 42
2017-08-12 13:00 | 45 | 42
2017-08-12 13:30 | 45 | 42
2017-08-12 14:00 | 46 | 43
2017-08-12 14:30 | 47 | 43
2017-08-12 15:00 | 46 | 43
2017-08-12 15:30 | 47 | 44
2017-08-12 16:00 | 48 | 45
2017-08-12 16:30 | 49 | 45
2017-08-12 17:00 | 46 | 45
2017-08-12 17:30 | 47 | 47
2017-08-12 18:00 | 48 | 47
2017-08-12 18:30 | 49 | 49
2017-08-12 19:00 | 51 | 50
2017-08-12 19:30 | 51 | 51
2017-08-12 20:00 | 54 | 54
2017-08-12 20:30 | 54 | 54
2017-08-12 21:00 | 54 | 54
2017-08-12 21:30 | 52 | 52
2017-08-12 22:00 | 52 | 51
2017-08-12 22:30 | 49 | 48
2017-08-12 23:00 | 47 | 47
2017-08-12 23:30 | 45 | 45
2017-08-13 | 46 | 45
2017-08-13 00:30 | 45 | 45
2017-08-13 01:00 | 45 | 44
2017-08-13 01:30 | 46 | 45
2017-08-13 02:00 | 47 | 46
2017-08-13 02:30 | 46 | 44
2017-08-13 03:00 | 46 | 45
2017-08-13 03:30 | 47 | 45
2017-08-13 04:00 | 48 | 47
2017-08-13 04:30 | 50 | 49
2017-08-13 05:00 | 49 | 48
2017-08-13 05:30 | 49 | 48
2017-08-13 06:00 | 47 | 46
2017-08-13 06:30 | 45 | 44
2017-08-13 07:00 | 45 | 44
2017-08-13 07:30 | 45 | 43
2017-08-13 08:00 | 52 | 50
2017-08-13 08:30 | 61 | 60
2017-08-13 09:00 | 61 | 60
2017-08-13 09:30 | 60 | 60
2017-08-13 10:00 | 60 | 60
2017-08-13 10:30 | 54 | 54
2017-08-13 11:00 | 53 | 53
2017-08-13 11:30 | 53 | 52
2017-08-13 12:00 | 50 | 49
2017-08-13 12:30 | 46 | 46
2017-08-13 13:00 | 47 | 44
2017-08-13 13:30 | 47 | 44
2017-08-13 14:00 | 48 | 45
2017-08-13 14:30 | 49 | 46
2017-08-13 15:00 | 49 | 46
2017-08-13 15:30 | 49 | 46
2017-08-13 16:00 | 49 | 46
2017-08-13 16:30 | 51 | 48
2017-08-13 17:00 | 51 | 48
2017-08-13 17:30 | 52 | 48
2017-08-13 18:00 | 52 | 49
2017-08-13 18:30 | 54 | 51
2017-08-13 19:00 | 55 | 51
2017-08-13 19:30 | 55 | 51
2017-08-13 20:00 | 53 | 50
2017-08-13 20:30 | 52 | 48
2017-08-13 21:00 | 50 | 46
2017-08-13 21:30 | 50 | 46
2017-08-13 22:00 | 50 | 46
2017-08-13 22:30 | 50 | 47
2017-08-13 23:00 | 49 | 46
2017-08-13 23:30 | 48 | 46
2017-08-14 | 48 | 46
2017-08-14 00:30 | 48 | 46
2017-08-14 01:00 | 49 | 48
2017-08-14 01:30 | 50 | 49
2017-08-14 02:00 | 49 | 49
2017-08-14 02:30 | 49 | 48
2017-08-14 03:00 | 47 | 46
2017-08-14 03:30 | 45 | 45
2017-08-14 04:00 | 44 | 43
2017-08-14 04:30 | 44 | 43
2017-08-14 05:00 | 45 | 44
2017-08-14 05:30 | 48 | 46
2017-08-14 06:00 | 47 | 46
2017-08-14 06:30 | 48 | 46
2017-08-14 07:00 | 45 | 44
2017-08-14 07:30 | 46 | 44
2017-08-14 08:00 | 49 | 49
2017-08-14 08:30 | 50 | 49
2017-08-14 09:00 | 49 | 49
2017-08-14 09:30 | 50 | 49
2017-08-14 10:00 | 47 | 47
2017-08-14 10:30 | 48 | 48
2017-08-14 11:00 | 48 | 48
2017-08-14 11:30 | 48 | 48
2017-08-14 12:00 | 49 | 49
2017-08-14 12:30 | 49 | 48
2017-08-14 13:00 | 48 | 48
2017-08-14 13:30 | 48 | 48
2017-08-14 14:00 | 49 | 48
2017-08-14 14:30 | 50 | 50
2017-08-14 15:00 | 49 | 49
2017-08-14 15:30 | 50 | 49
2017-08-14 16:00 | 50 | 49
2017-08-14 16:30 | 48 | 48
2017-08-14 17:00 | 50 | 49
2017-08-14 17:30 | 52 | 51
2017-08-14 18:00 | 48 | 47
2017-08-14 18:30 | 52 | 51
2017-08-14 19:00 | 64 | 63
2017-08-14 19:30 | 63 | 62
2017-08-14 20:00 | 62 | 62
2017-08-14 20:30 | 62 | 61
2017-08-14 21:00 | 62 | 62
2017-08-14 21:30 | 61 | 61
2017-08-14 22:00 | 57 | 56
2017-08-14 22:30 | 55 | 54
2017-08-14 23:00 | 56 | 55
2017-08-14 23:30 | 55 | 54
2017-08-15 | 52 | 50
2017-08-15 00:30 | 49 | 49
2017-08-15 01:00 | 49 | 48
2017-08-15 01:30 | 50 | 49
2017-08-15 02:00 | 51 | 50
2017-08-15 02:30 | 51 | 50
2017-08-15 03:00 | 50 | 49
2017-08-15 03:30 | 50 | 49
2017-08-15 04:00 | 50 | 49
2017-08-15 04:30 | 51 | 50
2017-08-15 05:00 | 50 | 49
2017-08-15 05:30 | 51 | 50
2017-08-15 06:00 | 52 | 51
2017-08-15 06:30 | 54 | 52
2017-08-15 07:00 | 38 | 37
2017-08-15 07:30 | 52 | 50
2017-08-15 08:00 | 56 | 52
2017-08-15 08:30 | 56 | 52
2017-08-15 09:00 | 55 | 52
2017-08-15 09:30 | 57 | 54
2017-08-15 10:00 | 59 | 56
2017-08-15 10:30 | 60 | 56
2017-08-15 11:00 | 60 | 56
2017-08-15 11:30 | 59 | 55
2017-08-15 12:00 | 57 | 54
2017-08-15 12:30 | 55 | 53
2017-08-15 13:00 | 55 | 53
2017-08-15 13:30 | 56 | 54
2017-08-15 14:00 | 56 | 54
2017-08-15 14:30 | 58 | 55
2017-08-15 15:00 | 58 | 56
2017-08-15 15:30 | 57 | 56
2017-08-15 16:00 | 58 | 56
2017-08-15 16:30 | 59 | 57
2017-08-15 17:00 | 59 | 57
2017-08-15 17:30 | 59 | 57
2017-08-15 18:00 | 56 | 55
2017-08-15 18:30 | 59 | 58
2017-08-15 19:00 | 58 | 57
2017-08-15 19:30 | 58 | 57
2017-08-15 20:00 | 57 | 56
2017-08-15 20:30 | 56 | 55
2017-08-15 21:00 | 53 | 52
2017-08-15 21:30 | 49 | 48
2017-08-15 22:00 | 47 | 47
2017-08-15 22:30 | 45 | 45
2017-08-15 23:00 | 47 | 46
2017-08-15 23:30 | 48 | 46
2017-08-16 | 49 | 48
2017-08-16 00:30 | 50 | 49
2017-08-16 01:00 | 49 | 47
2017-08-16 01:30 | 49 | 47
2017-08-16 02:00 | 49 | 47
2017-08-16 02:30 | 50 | 49
2017-08-16 03:00 | 50 | 48
2017-08-16 03:30 | 49 | 48
2017-08-16 04:00 | 49 | 47
2017-08-16 04:30 | 50 | 48
2017-08-16 05:00 | 48 | 47
2017-08-16 05:30 | 48 | 47
2017-08-16 06:00 | 48 | 46
2017-08-16 06:30 | 48 | 47
2017-08-16 07:00 | 50 | 50
2017-08-16 07:30 | 52 | 51
2017-08-16 08:00 | 61 | 60
2017-08-16 08:30 | 63 | 63
2017-08-16 09:00 | 61 | 61
2017-08-16 09:30 | 62 | 61
2017-08-16 10:00 | 60 | 60
2017-08-16 10:30 | 60 | 60
2017-08-16 11:00 | 59 | 59
2017-08-16 11:30 | 60 | 60
2017-08-16 12:00 | 61 | 61
2017-08-16 12:30 | 61 | 60
2017-08-16 13:00 | 60 | 60
2017-08-16 13:30 | 60 | 60
2017-08-16 14:00 | 61 | 60
2017-08-16 14:30 | 54 | 53
2017-08-16 15:00 | 53 | 52
2017-08-16 15:30 | 53 | 52
2017-08-16 16:00 | 54 | 53
2017-08-16 16:30 | 54 | 53
2017-08-16 17:00 | 54 | 53
2017-08-16 17:30 | 55 | 54
2017-08-16 18:00 | 57 | 56
2017-08-16 18:30 | 51 | 47
2017-08-16 19:00 | 49 | 43
2017-08-16 19:30 | 58 | 57
2017-08-16 20:00 | 58 | 57
2017-08-16 20:30 | 58 | 56
2017-08-16 21:00 | 62 | 61
2017-08-16 21:30 | 61 | 60
2017-08-16 22:00 | 60 | 59
2017-08-16 22:30 | 58 | 57
2017-08-16 23:00 | 57 | 55
2017-08-16 23:30 | 53 | 50
2017-08-17 | 46 | 45
2017-08-17 00:30 | 42 | 42
2017-08-17 01:00 | 40 | 39
2017-08-17 01:30 | 45 | 45
2017-08-17 02:00 | 43 | 43
2017-08-17 02:30 | 44 | 42
2017-08-17 03:00 | 44 | 42
2017-08-17 03:30 | 45 | 44
2017-08-17 04:00 | 44 | 42
2017-08-17 04:30 | 44 | 42
2017-08-17 05:00 | 46 | 44
2017-08-17 05:30 | 46 | 44
2017-08-17 06:00 | 46 | 44
2017-08-17 06:30 | 47 | 45
2017-08-17 07:00 | 50 | 47
2017-08-17 07:30 | 48 | 48
2017-08-17 08:00 | 49 | 49
2017-08-17 08:30 | 48 | 48
2017-08-17 09:00 | 47 | 46
2017-08-17 09:30 | 47 | 47
2017-08-17 10:00 | 49 | 49
2017-08-17 10:30 | 51 | 51
2017-08-17 11:00 | 49 | 49
2017-08-17 11:30 | 50 | 50
2017-08-17 12:00 | 52 | 51
2017-08-17 12:30 | 53 | 53
2017-08-17 13:00 | 53 | 53
2017-08-17 13:30 | 54 | 54
2017-08-17 14:00 | 54 | 54
2017-08-17 14:30 | 54 | 54
2017-08-17 15:00 | 55 | 55
2017-08-17 15:30 | 54 | 54
2017-08-17 16:00 | 55 | 55
2017-08-17 16:30 | 53 | 53
2017-08-17 17:00 | 39 | 35
2017-08-17 17:30 | 41 | 35
2017-08-17 18:00 | 40 | 34
2017-08-17 18:30 | 44 | 40
2017-08-17 19:00 | 60 | 60
2017-08-17 19:30 | 60 | 60
2017-08-17 20:00 | 58 | 58
2017-08-17 20:30 | 57 | 57
2017-08-17 21:00 | 58 | 57
2017-08-17 21:30 | 52 | 52
2017-08-17 22:00 | 51 | 50
2017-08-17 22:30 | 50 | 49
2017-08-17 23:00 | 48 | 47
2017-08-17 23:30 | 48 | 47
2017-08-18 | 47 | 46
2017-08-18 00:30 | 49 | 47
2017-08-18 01:00 | 47 | 44
2017-08-18 01:30 | 47 | 45
2017-08-18 02:00 | 46 | 44
2017-08-18 02:30 | 46 | 44
2017-08-18 03:00 | 46 | 44
2017-08-18 03:30 | 47 | 45
2017-08-18 04:00 | 45 | 43
2017-08-18 04:30 | 46 | 44
2017-08-18 05:00 | 46 | 44
2017-08-18 05:30 | 48 | 46
2017-08-18 06:00 | 49 | 47
2017-08-18 06:30 | 49 | 47
2017-08-18 07:00 | 50 | 47
2017-08-18 07:30 | 48 | 48
2017-08-18 08:00 | 49 | 48
2017-08-18 08:30 | 49 | 49
2017-08-18 09:00 | 49 | 49
2017-08-18 09:30 | 48 | 47
2017-08-18 10:00 | 48 | 48
2017-08-18 10:30 | 49 | 49
2017-08-18 11:00 | 48 | 47
2017-08-18 11:30 | 49 | 48
2017-08-18 12:00 | 48 | 47
2017-08-18 12:30 | 49 | 48
2017-08-18 13:00 | 38 | 33
2017-08-18 13:30 | 37 | 27
2017-08-18 14:00 | 38 | 28
2017-08-18 14:30 | 39 | 28
2017-08-18 15:00 | 40 | 30
2017-08-18 15:30 | 39 | 28
2017-08-18 16:00 | 40 | 30
2017-08-18 16:30 | 40 | 30
2017-08-18 17:00 | 44 | 34
2017-08-18 17:30 | 53 | 47
2017-08-18 18:00 | 63 | 61
2017-08-18 18:30 | 60 | 57
2017-08-18 19:00 | 54 | 50
2017-08-18 19:30 | 53 | 49
2017-08-18 20:00 | 54 | 49
2017-08-18 20:30 | 57 | 53
2017-08-18 21:00 | 58 | 54
2017-08-18 21:30 | 56 | 52
2017-08-18 22:00 | 53 | 50
2017-08-18 22:30 | 50 | 47
2017-08-18 23:00 | 48 | 45
2017-08-18 23:30 | 48 | 45
2017-08-19 | 50 | 46
2017-08-19 00:30 | 48 | 47
2017-08-19 01:00 | 49 | 47
2017-08-19 01:30 | 49 | 47
2017-08-19 02:00 | 49 | 47
2017-08-19 02:30 | 48 | 46
2017-08-19 03:00 | 48 | 47
2017-08-19 03:30 | 48 | 47
2017-08-19 04:00 | 47 | 46
2017-08-19 04:30 | 47 | 45
2017-08-19 05:00 | 45 | 43
2017-08-19 05:30 | 45 | 43
2017-08-19 06:00 | 46 | 44
2017-08-19 06:30 | 45 | 43
2017-08-19 07:00 | 42 | 41
2017-08-19 07:30 | 48 | 47
2017-08-19 08:00 | 50 | 49
2017-08-19 08:30 | 49 | 48
2017-08-19 09:00 | 48 | 47
2017-08-19 09:30 | 48 | 47
2017-08-19 10:00 | 46 | 45
2017-08-19 10:30 | 46 | 45
2017-08-19 11:00 | 45 | 44
2017-08-19 11:30 | 46 | 45
2017-08-19 12:00 | 46 | 45
2017-08-19 12:30 | 46 | 45
2017-08-19 13:00 | 48 | 47
2017-08-19 13:30 | 47 | 46
2017-08-19 14:00 | 47 | 46
2017-08-19 14:30 | 47 | 46
2017-08-19 15:00 | 47 | 46
2017-08-19 15:30 | 49 | 48
2017-08-19 16:00 | 48 | 47
2017-08-19 16:30 | 48 | 47
2017-08-19 17:00 | 48 | 48
2017-08-19 17:30 | 48 | 46
2017-08-19 18:00 | 47 | 46
2017-08-19 18:30 | 48 | 47
2017-08-19 19:00 | 50 | 49
2017-08-19 19:30 | 49 | 48
2017-08-19 20:00 | 50 | 49
2017-08-19 20:30 | 51 | 50
2017-08-19 21:00 | 50 | 50
2017-08-19 21:30 | 50 | 50
2017-08-19 22:00 | 51 | 50
2017-08-19 22:30 | 53 | 53
2017-08-19 23:00 | 49 | 49
2017-08-19 23:30 | 47 | 46
2017-08-20 | 47 | 46
2017-08-20 00:30 | 45 | 44
2017-08-20 01:00 | 45 | 45
2017-08-20 01:30 | 47 | 46
2017-08-20 02:00 | 48 | 47
2017-08-20 02:30 | 46 | 45
2017-08-20 03:00 | 48 | 47
2017-08-20 03:30 | 48 | 47
2017-08-20 04:00 | 47 | 46
2017-08-20 04:30 | 46 | 45
2017-08-20 05:00 | 47 | 46
2017-08-20 05:30 | 46 | 45
2017-08-20 06:00 | 45 | 44
2017-08-20 06:30 | 45 | 44
2017-08-20 07:00 | 43 | 41
2017-08-20 07:30 | 44 | 42
2017-08-20 08:00 | 45 | 44
2017-08-20 08:30 | 46 | 45
2017-08-20 09:00 | 45 | 44
2017-08-20 09:30 | 44 | 43
2017-08-20 10:00 | 43 | 42
2017-08-20 10:30 | 44 | 41
2017-08-20 11:00 | 44 | 42
2017-08-20 11:30 | 45 | 43
2017-08-20 12:00 | 45 | 43
2017-08-20 12:30 | 45 | 43
2017-08-20 13:00 | 45 | 43
2017-08-20 13:30 | 45 | 43
2017-08-20 14:00 | 45 | 43
2017-08-20 14:30 | 47 | 44
2017-08-20 15:00 | 48 | 45
2017-08-20 15:30 | 48 | 46
2017-08-20 16:00 | 49 | 47
2017-08-20 16:30 | 50 | 48
2017-08-20 17:00 | 48 | 47
2017-08-20 17:30 | 48 | 46
2017-08-20 18:00 | 48 | 48
2017-08-20 18:30 | 49 | 49
2017-08-20 19:00 | 50 | 49
2017-08-20 19:30 | 50 | 49
2017-08-20 20:00 | 50 | 49
2017-08-20 20:30 | 50 | 49
2017-08-20 21:00 | 50 | 49
2017-08-20 21:30 | 51 | 50
2017-08-20 22:00 | 51 | 50
2017-08-20 22:30 | 49 | 47
2017-08-20 23:00 | 47 | 45
2017-08-20 23:30 | 48 | 46
2017-08-21 | 47 | 44
2017-08-21 00:30 | 47 | 45
2017-08-21 01:00 | 47 | 45
2017-08-21 01:30 | 47 | 44
2017-08-21 02:00 | 46 | 44
2017-08-21 02:30 | 44 | 43
2017-08-21 03:00 | 44 | 44
2017-08-21 03:30 | 45 | 44
2017-08-21 04:00 | 45 | 45
2017-08-21 04:30 | 47 | 46
2017-08-21 05:00 | 44 | 44
2017-08-21 05:30 | 46 | 45
2017-08-21 06:00 | 46 | 46
2017-08-21 06:30 | 48 | 47
2017-08-21 07:00 | 50 | 49
2017-08-21 07:30 | 52 | 52
2017-08-21 08:00 | 52 | 52
2017-08-21 08:30 | 53 | 52
2017-08-21 09:00 | 52 | 52
2017-08-21 09:30 | 51 | 50
2017-08-21 10:00 | 50 | 49
2017-08-21 10:30 | 51 | 50
2017-08-21 11:00 | 48 | 47
2017-08-21 11:30 | 47 | 45
2017-08-21 12:00 | 48 | 47
2017-08-21 12:30 | 48 | 46
2017-08-21 13:00 | 49 | 47
2017-08-21 13:30 | 48 | 47
2017-08-21 14:00 | 49 | 47
2017-08-21 14:30 | 51 | 50
2017-08-21 15:00 | 51 | 50
2017-08-21 15:30 | 51 | 50
2017-08-21 16:00 | 52 | 50
2017-08-21 16:30 | 55 | 54
2017-08-21 17:00 | 60 | 60
2017-08-21 17:30 | 64 | 64
2017-08-21 18:00 | 57 | 56
2017-08-21 18:30 | 57 | 57
2017-08-21 19:00 | 49 | 49
2017-08-21 19:30 | 56 | 56
2017-08-21 20:00 | 57 | 56
2017-08-21 20:30 | 57 | 57
2017-08-21 21:00 | 55 | 54
2017-08-21 21:30 | 53 | 53
2017-08-21 22:00 | 54 | 53
2017-08-21 22:30 | 50 | 50
2017-08-21 23:00 | 46 | 46
2017-08-21 23:30 | 47 | 47
2017-08-22 | 48 | 48
2017-08-22 00:30 | 48 | 47
2017-08-22 01:00 | 48 | 47
2017-08-22 01:30 | 47 | 46
2017-08-22 02:00 | 46 | 45
2017-08-22 02:30 | 46 | 45
2017-08-22 03:00 | 46 | 45
2017-08-22 03:30 | 46 | 45
2017-08-22 04:00 | 46 | 46
2017-08-22 04:30 | 45 | 44
2017-08-22 05:00 | 46 | 45
2017-08-22 05:30 | 48 | 47
2017-08-22 06:00 | 47 | 46
2017-08-22 06:30 | 48 | 47
2017-08-22 07:00 | 44 | 44
2017-08-22 07:30 | 55 | 53
2017-08-22 08:00 | 54 | 53
2017-08-22 08:30 | 53 | 52
2017-08-22 09:00 | 51 | 51
2017-08-22 09:30 | 49 | 48
2017-08-22 10:00 | 48 | 47
2017-08-22 10:30 | 49 | 49
2017-08-22 11:00 | 47 | 47
2017-08-22 11:30 | 50 | 49
2017-08-22 12:00 | 52 | 51
2017-08-22 12:30 | 51 | 50
2017-08-22 13:00 | 53 | 52
2017-08-22 13:30 | 53 | 52
2017-08-22 14:00 | 56 | 55
2017-08-22 14:30 | 56 | 56
2017-08-22 15:00 | 54 | 54
2017-08-22 15:30 | 55 | 55
2017-08-22 16:00 | 56 | 56
2017-08-22 16:30 | 56 | 55
2017-08-22 17:00 | 55 | 55
2017-08-22 17:30 | 58 | 57
2017-08-22 18:00 | 60 | 59
2017-08-22 18:30 | 57 | 56
2017-08-22 19:00 | 58 | 57
2017-08-22 19:30 | 57 | 57
2017-08-22 20:00 | 56 | 55
2017-08-22 20:30 | 57 | 56
2017-08-22 21:00 | 65 | 64
2017-08-22 21:30 | 63 | 62
2017-08-22 22:00 | 63 | 61
2017-08-22 22:30 | 61 | 59
2017-08-22 23:00 | 59 | 57
2017-08-22 23:30 | 55 | 55
2017-08-23 | 55 | 53
2017-08-23 00:30 | 54 | 52
2017-08-23 01:00 | 54 | 52
2017-08-23 01:30 | 54 | 52
2017-08-23 02:00 | 53 | 52
2017-08-23 02:30 | 51 | 49
2017-08-23 03:00 | 49 | 47
2017-08-23 03:30 | 49 | 47
2017-08-23 04:00 | 49 | 47
2017-08-23 04:30 | 48 | 46
2017-08-23 05:00 | 48 | 45
2017-08-23 05:30 | 48 | 45
2017-08-23 06:00 | 49 | 46
2017-08-23 06:30 | 51 | 49
2017-08-23 07:00 | 53 | 51
2017-08-23 07:30 | 56 | 52
2017-08-23 08:00 | 58 | 53
2017-08-23 08:30 | 56 | 51
2017-08-23 09:00 | 56 | 51
2017-08-23 09:30 | 55 | 50
2017-08-23 10:00 | 52 | 48
2017-08-23 10:30 | 53 | 47
2017-08-23 11:00 | 53 | 47
2017-08-23 11:30 | 53 | 48
2017-08-23 12:00 | 52 | 47
2017-08-23 12:30 | 52 | 47
2017-08-23 13:00 | 52 | 47
2017-08-23 13:30 | 52 | 47
2017-08-23 14:00 | 52 | 47
2017-08-23 14:30 | 53 | 48
2017-08-23 15:00 | 55 | 50
2017-08-23 15:30 | 56 | 52
2017-08-23 16:00 | 57 | 53
2017-08-23 16:30 | 58 | 54
2017-08-23 17:00 | 58 | 54
2017-08-23 17:30 | 58 | 54
2017-08-23 18:00 | 57 | 54
2017-08-23 18:30 | 60 | 56
2017-08-23 19:00 | 60 | 56
2017-08-23 19:30 | 60 | 56
2017-08-23 20:00 | 59 | 56
2017-08-23 20:30 | 57 | 53
2017-08-23 21:00 | 55 | 52
2017-08-23 21:30 | 54 | 51
2017-08-23 22:00 | 54 | 52
2017-08-23 22:30 | 53 | 51
2017-08-23 23:00 | 53 | 50
2017-08-23 23:30 | 52 | 50
2017-08-24 | 51 | 49
2017-08-24 00:30 | 51 | 49
2017-08-24 01:00 | 51 | 50
2017-08-24 01:30 | 50 | 48
2017-08-24 02:00 | 50 | 48
2017-08-24 02:30 | 51 | 50
2017-08-24 03:00 | 50 | 49
2017-08-24 03:30 | 51 | 49
2017-08-24 04:00 | 49 | 48
2017-08-24 04:30 | 50 | 49
2017-08-24 05:00 | 51 | 49
2017-08-24 05:30 | 55 | 53
2017-08-24 06:00 | 57 | 55
2017-08-24 06:30 | 60 | 58
2017-08-24 07:00 | 54 | 53
2017-08-24 07:30 | 60 | 58
2017-08-24 08:00 | 64 | 61
2017-08-24 08:30 | 64 | 60
2017-08-24 09:00 | 63 | 59
2017-08-24 09:30 | 63 | 59
2017-08-24 10:00 | 63 | 59
2017-08-24 10:30 | 62 | 58
2017-08-24 11:00 | 63 | 59
2017-08-24 11:30 | 63 | 59
2017-08-24 12:00 | 63 | 59
2017-08-24 12:30 | 63 | 59
2017-08-24 13:00 | 62 | 58
2017-08-24 13:30 | 63 | 58
2017-08-24 14:00 | 63 | 59
2017-08-24 14:30 | 65 | 61
2017-08-24 15:00 | 64 | 60
2017-08-24 15:30 | 63 | 59
2017-08-24 16:00 | 65 | 61
2017-08-24 16:30 | 64 | 60
2017-08-24 17:00 | 62 | 58
2017-08-24 17:30 | 65 | 62
2017-08-24 18:00 | 66 | 63
2017-08-24 18:30 | 66 | 63
2017-08-24 19:00 | 65 | 65
2017-08-24 19:30 | 67 | 66
2017-08-24 20:00 | 64 | 64
2017-08-24 20:30 | 64 | 64
2017-08-24 21:00 | 65 | 64
2017-08-24 21:30 | 64 | 63
2017-08-24 22:00 | 62 | 61
2017-08-24 22:30 | 62 | 62
2017-08-24 23:00 | 63 | 62
2017-08-24 23:30 | 62 | 60
2017-08-25 | 63 | 61
2017-08-25 00:30 | 63 | 62
2017-08-25 01:00 | 62 | 60
2017-08-25 01:30 | 61 | 60
2017-08-25 02:00 | 62 | 60
2017-08-25 02:30 | 60 | 58
2017-08-25 03:00 | 60 | 58
2017-08-25 03:30 | 61 | 59
2017-08-25 04:00 | 60 | 59
2017-08-25 04:30 | 58 | 57
2017-08-25 05:00 | 58 | 56
2017-08-25 05:30 | 59 | 57
2017-08-25 06:00 | 58 | 56
2017-08-25 06:30 | 60 | 58
2017-08-25 07:00 | 41 | 41
2017-08-25 07:30 | 58 | 56
2017-08-25 08:00 | 63 | 60
2017-08-25 08:30 | 64 | 61
2017-08-25 09:00 | 64 | 60
2017-08-25 09:30 | 63 | 59
2017-08-25 10:00 | 57 | 53
2017-08-25 10:30 | 52 | 47
2017-08-25 11:00 | 52 | 47
2017-08-25 11:30 | 52 | 47
2017-08-25 12:00 | 53 | 48
2017-08-25 12:30 | 53 | 48
2017-08-25 13:00 | 53 | 48
2017-08-25 13:30 | 54 | 49
2017-08-25 14:00 | 55 | 50
2017-08-25 14:30 | 55 | 50
2017-08-25 15:00 | 56 | 50
2017-08-25 15:30 | 57 | 52
2017-08-25 16:00 | 57 | 52
2017-08-25 16:30 | 57 | 52
2017-08-25 17:00 | 54 | 53
2017-08-25 17:30 | 53 | 53
2017-08-25 18:00 | 53 | 53
2017-08-25 18:30 | 52 | 52
2017-08-25 19:00 | 53 | 53
2017-08-25 19:30 | 53 | 53
2017-08-25 20:00 | 53 | 52
2017-08-25 20:30 | 53 | 52
2017-08-25 21:00 | 52 | 52
2017-08-25 21:30 | 51 | 50
2017-08-25 22:00 | 51 | 50
2017-08-25 22:30 | 49 | 48
2017-08-25 23:00 | 48 | 47
2017-08-25 23:30 | 48 | 47
2017-08-26 | 51 | 48
2017-08-26 00:30 | 49 | 46
2017-08-26 01:00 | 48 | 45
2017-08-26 01:30 | 49 | 46
2017-08-26 02:00 | 48 | 46
2017-08-26 02:30 | 50 | 47
2017-08-26 03:00 | 50 | 47
2017-08-26 03:30 | 49 | 47
2017-08-26 04:00 | 48 | 45
2017-08-26 04:30 | 48 | 46
2017-08-26 05:00 | 48 | 46
2017-08-26 05:30 | 49 | 46
2017-08-26 06:00 | 49 | 47
2017-08-26 06:30 | 51 | 49
2017-08-26 07:00 | 51 | 49
2017-08-26 07:30 | 51 | 50
2017-08-26 08:00 | 52 | 51
2017-08-26 08:30 | 52 | 51
2017-08-26 09:00 | 51 | 50
2017-08-26 09:30 | 51 | 50
2017-08-26 10:00 | 52 | 51
2017-08-26 10:30 | 52 | 50
2017-08-26 11:00 | 51 | 50
2017-08-26 11:30 | 51 | 50
2017-08-26 12:00 | 51 | 49
2017-08-26 12:30 | 50 | 49
2017-08-26 13:00 | 50 | 49
2017-08-26 13:30 | 51 | 49
2017-08-26 14:00 | 49 | 47
2017-08-26 14:30 | 49 | 47
2017-08-26 15:00 | 49 | 47
2017-08-26 15:30 | 48 | 47
2017-08-26 16:00 | 50 | 49
2017-08-26 16:30 | 52 | 51
2017-08-26 17:00 | 53 | 52
2017-08-26 17:30 | 54 | 52
2017-08-26 18:00 | 53 | 52
2017-08-26 18:30 | 54 | 53
2017-08-26 19:00 | 55 | 54
2017-08-26 19:30 | 56 | 55
2017-08-26 20:00 | 56 | 55
2017-08-26 20:30 | 54 | 54
2017-08-26 21:00 | 53 | 53
2017-08-26 21:30 | 53 | 52
2017-08-26 22:00 | 52 | 51
2017-08-26 22:30 | 49 | 48
2017-08-26 23:00 | 47 | 46
2017-08-26 23:30 | 48 | 46
2017-08-27 | 47 | 45
2017-08-27 00:30 | 47 | 45
2017-08-27 01:00 | 47 | 45
2017-08-27 01:30 | 45 | 44
2017-08-27 02:00 | 45 | 43
2017-08-27 02:30 | 46 | 44
2017-08-27 03:00 | 46 | 44
2017-08-27 03:30 | 45 | 44
2017-08-27 04:00 | 45 | 44
2017-08-27 04:30 | 45 | 43
2017-08-27 05:00 | 45 | 44
2017-08-27 05:30 | 46 | 45
2017-08-27 06:00 | 47 | 45
2017-08-27 06:30 | 48 | 47
2017-08-27 07:00 | 48 | 47
2017-08-27 07:30 | 51 | 50
2017-08-27 08:00 | 50 | 49
2017-08-27 08:30 | 51 | 50
2017-08-27 09:00 | 53 | 52
2017-08-27 09:30 | 53 | 52
2017-08-27 10:00 | 54 | 53
2017-08-27 10:30 | 53 | 52
2017-08-27 11:00 | 53 | 52
2017-08-27 11:30 | 52 | 51
2017-08-27 12:00 | 52 | 51
2017-08-27 12:30 | 51 | 50
2017-08-27 13:00 | 50 | 49
2017-08-27 13:30 | 48 | 47
2017-08-27 14:00 | 47 | 46
2017-08-27 14:30 | 48 | 46
2017-08-27 15:00 | 47 | 46
2017-08-27 15:30 | 48 | 47
2017-08-27 16:00 | 49 | 48
2017-08-27 16:30 | 51 | 50
2017-08-27 17:00 | 53 | 52
2017-08-27 17:30 | 56 | 56
2017-08-27 18:00 | 58 | 57
2017-08-27 18:30 | 65 | 64
2017-08-27 19:00 | 67 | 66
2017-08-27 19:30 | 65 | 64
2017-08-27 20:00 | 60 | 58
2017-08-27 20:30 | 37 | 37
2017-08-27 21:00 | 52 | 52
2017-08-27 21:30 | 54 | 53
2017-08-27 22:00 | 53 | 52
2017-08-27 22:30 | 49 | 48
2017-08-27 23:00 | 49 | 48
2017-08-27 23:30 | 49 | 48
2017-08-28 | 48 | 47
2017-08-28 00:30 | 48 | 47
2017-08-28 01:00 | 47 | 47
2017-08-28 01:30 | 46 | 45
2017-08-28 02:00 | 46 | 45
2017-08-28 02:30 | 47 | 47
2017-08-28 03:00 | 47 | 46
2017-08-28 03:30 | 45 | 44
2017-08-28 04:00 | 45 | 44
2017-08-28 04:30 | 45 | 43
2017-08-28 05:00 | 44 | 43
2017-08-28 05:30 | 45 | 43
2017-08-28 06:00 | 46 | 45
2017-08-28 06:30 | 48 | 47
2017-08-28 07:00 | 38 | 38
2017-08-28 07:30 | 49 | 48
2017-08-28 08:00 | 48 | 46
2017-08-28 08:30 | 53 | 51
2017-08-28 09:00 | 54 | 51
2017-08-28 09:30 | 53 | 51
2017-08-28 10:00 | 52 | 49
2017-08-28 10:30 | 51 | 49
2017-08-28 11:00 | 50 | 49
2017-08-28 11:30 | 50 | 49
2017-08-28 12:00 | 52 | 51
2017-08-28 12:30 | 53 | 52
2017-08-28 13:00 | 56 | 55
2017-08-28 13:30 | 56 | 54
2017-08-28 14:00 | 55 | 54
2017-08-28 14:30 | 56 | 55
2017-08-28 15:00 | 58 | 56
2017-08-28 15:30 | 54 | 53
2017-08-28 16:00 | 56 | 55
2017-08-28 16:30 | 56 | 55
2017-08-28 17:00 | 59 | 58
2017-08-28 17:30 | 65 | 64
2017-08-28 18:00 | 65 | 64
2017-08-28 18:30 | 53 | 45
2017-08-28 19:00 | 50 | 42
2017-08-28 19:30 | 48 | 36
2017-08-28 20:00 | 48 | 32
2017-08-28 20:30 | 50 | 42
2017-08-28 21:00 | 57 | 54
2017-08-28 21:30 | 54 | 51
2017-08-28 22:00 | 52 | 49
2017-08-28 22:30 | 48 | 48
2017-08-28 23:00 | 47 | 47
2017-08-28 23:30 | 48 | 47
2017-08-29 | 46 | 45
2017-08-29 00:30 | 45 | 44
2017-08-29 01:00 | 44 | 43
2017-08-29 01:30 | 44 | 43
2017-08-29 02:00 | 46 | 44
2017-08-29 02:30 | 47 | 44
2017-08-29 03:00 | 47 | 44
2017-08-29 03:30 | 48 | 45
2017-08-29 04:00 | 47 | 44
2017-08-29 04:30 | 47 | 44
2017-08-29 05:00 | 47 | 44
2017-08-29 05:30 | 48 | 45
2017-08-29 06:00 | 48 | 44
2017-08-29 06:30 | 40 | 38
2017-08-29 07:00 | 28 | 28
2017-08-29 07:30 | 30 | 30
2017-08-29 08:00 | 47 | 47
2017-08-29 08:30 | 51 | 51
2017-08-29 09:00 | 50 | 50
2017-08-29 09:30 | 48 | 48
2017-08-29 10:00 | 48 | 48
2017-08-29 10:30 | 49 | 49
2017-08-29 11:00 | 52 | 52
2017-08-29 11:30 | 50 | 50
2017-08-29 12:00 | 49 | 49
2017-08-29 12:30 | 49 | 49
2017-08-29 13:00 | 50 | 50
2017-08-29 13:30 | 50 | 50
2017-08-29 14:00 | 51 | 51
2017-08-29 14:30 | 51 | 51
2017-08-29 15:00 | 51 | 51
2017-08-29 15:30 | 53 | 53
2017-08-29 16:00 | 53 | 53
2017-08-29 16:30 | 53 | 53
2017-08-29 17:00 | 53 | 53
2017-08-29 17:30 | 52 | 52
2017-08-29 18:00 | 53 | 53
2017-08-29 18:30 | 41 | 38
2017-08-29 19:00 | 40 | 35
2017-08-29 19:30 | 44 | 41
2017-08-29 20:00 | 50 | 49
2017-08-29 20:30 | 53 | 53
2017-08-29 21:00 | 52 | 52
2017-08-29 21:30 | 51 | 51
2017-08-29 22:00 | 51 | 51
2017-08-29 22:30 | 51 | 50
2017-08-29 23:00 | 49 | 49
2017-08-29 23:30 | 51 | 50
2017-08-30 | 52 | 51
2017-08-30 00:30 | 52 | 50
2017-08-30 01:00 | 51 | 49
2017-08-30 01:30 | 51 | 49
2017-08-30 02:00 | 50 | 48
2017-08-30 02:30 | 48 | 46
2017-08-30 03:00 | 48 | 47
2017-08-30 03:30 | 49 | 47
2017-08-30 04:00 | 49 | 47
2017-08-30 04:30 | 48 | 47
2017-08-30 05:00 | 50 | 48
2017-08-30 05:30 | 49 | 47
2017-08-30 06:00 | 49 | 48
2017-08-30 06:30 | 50 | 49
2017-08-30 07:00 | 40 | 33
2017-08-30 07:30 | 39 | 39
2017-08-30 08:00 | 53 | 49
2017-08-30 08:30 | 55 | 52
2017-08-30 09:00 | 55 | 52
2017-08-30 09:30 | 73 | 67
2017-08-30 10:00 | 88 | 88
2017-08-30 10:30 | 88 | 88
2017-08-30 11:00 | 84 | 84
2017-08-30 11:30 | 84 | 83
2017-08-30 12:00 | 86 | 86
2017-08-30 12:30 | 86 | 86
2017-08-30 13:00 | 87 | 87
2017-08-30 13:30 | 85 | 85
2017-08-30 14:00 | 86 | 85
2017-08-30 14:30 | 91 | 91
2017-08-30 15:00 | 111 | 110
2017-08-30 15:30 | 117 | 113
2017-08-30 16:00 | 122 | 112
2017-08-30 16:30 | 122 | 112
2017-08-30 17:00 | 115 | 113
2017-08-30 17:30 | 114 | 112
2017-08-30 18:00 | 113 | 110
2017-08-30 18:30 | 121 | 117
2017-08-30 19:00 | 121 | 117
2017-08-30 19:30 | 120 | 116
2017-08-30 20:00 | 120 | 115
2017-08-30 20:30 | 115 | 110
2017-08-30 21:00 | 113 | 108
2017-08-30 21:30 | 112 | 107
2017-08-30 22:00 | 110 | 108
2017-08-30 22:30 | 108 | 105
2017-08-30 23:00 | 104 | 101
2017-08-30 23:30 | 102 | 100
2017-08-31 | 101 | 99
2017-08-31 00:30 | 101 | 100
2017-08-31 01:00 | 100 | 99
2017-08-31 01:30 | 101 | 100
2017-08-31 02:00 | 101 | 100
2017-08-31 02:30 | 102 | 101
2017-08-31 03:00 | 101 | 99
2017-08-31 03:30 | 100 | 99
2017-08-31 04:00 | 100 | 99
2017-08-31 04:30 | 101 | 100
2017-08-31 05:00 | 99 | 98
2017-08-31 05:30 | 97 | 96
2017-08-31 06:00 | 99 | 98
2017-08-31 06:30 | 101 | 100
2017-08-31 07:00 | 94 | 90
2017-08-31 07:30 | 101 | 101
2017-08-31 08:00 | 109 | 106
2017-08-31 08:30 | 109 | 106
2017-08-31 09:00 | 108 | 108
2017-08-31 09:30 | 105 | 102
2017-08-31 10:00 | 103 | 101
2017-08-31 10:30 | 105 | 103
2017-08-31 11:00 | 108 | 105
2017-08-31 11:30 | 108 | 106
2017-08-31 12:00 | 106 | 105
2017-08-31 12:30 | 109 | 108
2017-08-31 13:00 | 109 | 108
2017-08-31 13:30 | 107 | 107
2017-08-31 14:00 | 110 | 108
2017-08-31 14:30 | 112 | 110
2017-08-31 15:00 | 111 | 109
2017-08-31 15:30 | 112 | 110
2017-08-31 16:00 | 113 | 111
2017-08-31 16:30 | 112 | 110
2017-08-31 17:00 | 114 | 112
2017-08-31 17:30 | 117 | 114
2017-08-31 18:00 | 116 | 113
2017-08-31 18:30 | 117 | 114
2017-08-31 19:00 | 119 | 117
2017-08-31 19:30 | 114 | 113
2017-08-31 20:00 | 111 | 110
2017-08-31 20:30 | 107 | 106
2017-08-31 21:00 | 105 | 102
2017-08-31 21:30 | 111 | 109
2017-08-31 22:00 | 113 | 111
2017-08-31 22:30 | 111 | 108
2017-08-31 23:00 | 108 | 102
2017-08-31 23:30 | 108 | 102
2017-09-01 | 107 | 101
2017-09-01 00:30 | 107 | 101
2017-09-01 01:00 | 108 | 102
2017-09-01 01:30 | 106 | 100
2017-09-01 02:00 | 104 | 100
2017-09-01 02:30 | 102 | 99
2017-09-01 03:00 | 101 | 98
2017-09-01 03:30 | 102 | 98
2017-09-01 04:00 | 103 | 99
2017-09-01 04:30 | 101 | 97
2017-09-01 05:00 | 99 | 96
2017-09-01 05:30 | 100 | 97
2017-09-01 06:00 | 99 | 96
2017-09-01 06:30 | 99 | 96
2017-09-01 07:00 | 103 | 100
2017-09-01 07:30 | 106 | 105
2017-09-01 08:00 | 107 | 104
2017-09-01 08:30 | 108 | 105
2017-09-01 09:00 | 108 | 107
2017-09-01 09:30 | 107 | 106
2017-09-01 10:00 | 107 | 106
2017-09-01 10:30 | 106 | 105
2017-09-01 11:00 | 107 | 106
2017-09-01 11:30 | 106 | 104
2017-09-01 12:00 | 105 | 104
2017-09-01 12:30 | 103 | 102
2017-09-01 13:00 | 102 | 101
2017-09-01 13:30 | 102 | 99
2017-09-01 14:00 | 103 | 101
2017-09-01 14:30 | 111 | 108
2017-09-01 15:00 | 112 | 110
2017-09-01 15:30 | 114 | 113
2017-09-01 16:00 | 116 | 114
2017-09-01 16:30 | 118 | 115
2017-09-01 17:00 | 118 | 116
2017-09-01 17:30 | 120 | 119
2017-09-01 18:00 | 117 | 116
2017-09-01 18:30 | 118 | 115
2017-09-01 19:00 | 119 | 117
2017-09-01 19:30 | 114 | 113
2017-09-01 20:00 | 112 | 110
2017-09-01 20:30 | 110 | 108
2017-09-01 21:00 | 110 | 108
2017-09-01 21:30 | 108 | 106
2017-09-01 22:00 | 107 | 105
2017-09-01 22:30 | 104 | 103
2017-09-01 23:00 | 102 | 99
2017-09-01 23:30 | 101 | 98
2017-09-02 | 101 | 98
2017-09-02 00:30 | 103 | 100
2017-09-02 01:00 | 104 | 100
2017-09-02 01:30 | 107 | 103
2017-09-02 02:00 | 108 | 104
2017-09-02 02:30 | 105 | 100
2017-09-02 03:00 | 105 | 100
2017-09-02 03:30 | 106 | 101
2017-09-02 04:00 | 106 | 101
2017-09-02 04:30 | 104 | 99
2017-09-02 05:00 | 105 | 99
2017-09-02 05:30 | 105 | 99
2017-09-02 06:00 | 102 | 97
2017-09-02 06:30 | 101 | 96
2017-09-02 07:00 | 102 | 98
2017-09-02 07:30 | 106 | 102
2017-09-02 08:00 | 103 | 100
2017-09-02 08:30 | 102 | 100
2017-09-02 09:00 | 102 | 100
2017-09-02 09:30 | 102 | 99
2017-09-02 10:00 | 109 | 105
2017-09-02 10:30 | 112 | 111
2017-09-02 11:00 | 113 | 111
2017-09-02 11:30 | 111 | 109
2017-09-02 12:00 | 115 | 114
2017-09-02 12:30 | 117 | 114
2017-09-02 13:00 | 116 | 113
2017-09-02 13:30 | 116 | 114
2017-09-02 14:00 | 119 | 117
2017-09-02 14:30 | 119 | 117
2017-09-02 15:00 | 119 | 117
2017-09-02 15:30 | 121 | 119
2017-09-02 16:00 | 120 | 118
2017-09-02 16:30 | 118 | 116
2017-09-02 17:00 | 119 | 117
2017-09-02 17:30 | 120 | 118
2017-09-02 18:00 | 121 | 119
2017-09-02 18:30 | 119 | 115
2017-09-02 19:00 | 124 | 120
2017-09-02 19:30 | 116 | 113
2017-09-02 20:00 | 111 | 108
2017-09-02 20:30 | 109 | 106
2017-09-02 21:00 | 110 | 106
2017-09-02 21:30 | 110 | 106
2017-09-02 22:00 | 107 | 103
2017-09-02 22:30 | 106 | 101
2017-09-02 23:00 | 103 | 98
2017-09-02 23:30 | 101 | 96
2017-09-03 | 102 | 97
2017-09-03 00:30 | 104 | 99
2017-09-03 01:00 | 103 | 98
2017-09-03 01:30 | 101 | 96
2017-09-03 02:00 | 103 | 97
2017-09-03 02:30 | 103 | 95
2017-09-03 03:00 | 102 | 95
2017-09-03 03:30 | 101 | 94
2017-09-03 04:00 | 102 | 95
2017-09-03 04:30 | 102 | 94
2017-09-03 05:00 | 101 | 93
2017-09-03 05:30 | 99 | 91
2017-09-03 06:00 | 99 | 92
2017-09-03 06:30 | 99 | 91
2017-09-03 07:00 | 101 | 94
2017-09-03 07:30 | 105 | 99
2017-09-03 08:00 | 105 | 99
2017-09-03 08:30 | 106 | 99
2017-09-03 09:00 | 107 | 101
2017-09-03 09:30 | 106 | 100
2017-09-03 10:00 | 106 | 101
2017-09-03 10:30 | 106 | 101
2017-09-03 11:00 | 108 | 103
2017-09-03 11:30 | 108 | 103
2017-09-03 12:00 | 108 | 103
2017-09-03 12:30 | 108 | 103
2017-09-03 13:00 | 107 | 101
2017-09-03 13:30 | 107 | 102
2017-09-03 14:00 | 109 | 104
2017-09-03 14:30 | 112 | 106
2017-09-03 15:00 | 110 | 105
2017-09-03 15:30 | 110 | 105
2017-09-03 16:00 | 110 | 106
2017-09-03 16:30 | 106 | 103
2017-09-03 17:00 | 106 | 103
2017-09-03 17:30 | 108 | 104
2017-09-03 18:00 | 109 | 106
2017-09-03 18:30 | 109 | 107
2017-09-03 19:00 | 111 | 109
2017-09-03 19:30 | 110 | 108
2017-09-03 20:00 | 91 | 89
2017-09-03 20:30 | 87 | 86
2017-09-03 21:00 | 88 | 86
2017-09-03 21:30 | 88 | 86
2017-09-03 22:00 | 85 | 82
2017-09-03 22:30 | 83 | 81
2017-09-03 23:00 | 81 | 78
2017-09-03 23:30 | 77 | 76
2017-09-04 | 76 | 75
2017-09-04 00:30 | 79 | 78
2017-09-04 01:00 | 78 | 76
2017-09-04 01:30 | 77 | 76
2017-09-04 02:00 | 77 | 76
2017-09-04 02:30 | 76 | 74
2017-09-04 03:00 | 77 | 76
2017-09-04 03:30 | 79 | 77
2017-09-04 04:00 | 81 | 79
2017-09-04 04:30 | 78 | 77
2017-09-04 05:00 | 78 | 77
2017-09-04 05:30 | 79 | 77
2017-09-04 06:00 | 78 | 77
2017-09-04 06:30 | 80 | 79
2017-09-04 07:00 | 86 | 85
2017-09-04 07:30 | 88 | 87
2017-09-04 08:00 | 89 | 89
2017-09-04 08:30 | 93 | 89
2017-09-04 09:00 | 93 | 89
2017-09-04 09:30 | 92 | 88
2017-09-04 10:00 | 91 | 88
2017-09-04 10:30 | 91 | 89
2017-09-04 11:00 | 86 | 85
2017-09-04 11:30 | 86 | 85
2017-09-04 12:00 | 86 | 85
2017-09-04 12:30 | 86 | 85
2017-09-04 13:00 | 86 | 86
2017-09-04 13:30 | 87 | 86
2017-09-04 14:00 | 89 | 88
2017-09-04 14:30 | 89 | 89
2017-09-04 15:00 | 91 | 90
2017-09-04 15:30 | 92 | 91
2017-09-04 16:00 | 92 | 91
2017-09-04 16:30 | 91 | 91
2017-09-04 17:00 | 91 | 90
2017-09-04 17:30 | 94 | 93
2017-09-04 18:00 | 92 | 91
2017-09-04 18:30 | 93 | 92
2017-09-04 19:00 | 84 | 80
2017-09-04 19:30 | 93 | 91
2017-09-04 20:00 | 91 | 90
2017-09-04 20:30 | 91 | 89
2017-09-04 21:00 | 90 | 88
2017-09-04 21:30 | 89 | 87
2017-09-04 22:00 | 90 | 88
2017-09-04 22:30 | 90 | 86
2017-09-04 23:00 | 88 | 85
2017-09-04 23:30 | 89 | 85
2017-09-05 | 89 | 85
2017-09-05 00:30 | 87 | 82
2017-09-05 01:00 | 87 | 82
2017-09-05 01:30 | 85 | 82
2017-09-05 02:00 | 82 | 80
2017-09-05 02:30 | 81 | 79
2017-09-05 03:00 | 82 | 80
2017-09-05 03:30 | 86 | 84
2017-09-05 04:00 | 84 | 82
2017-09-05 04:30 | 87 | 85
2017-09-05 05:00 | 88 | 86
2017-09-05 05:30 | 88 | 87
2017-09-05 06:00 | 91 | 89
2017-09-05 06:30 | 91 | 89
2017-09-05 07:00 | 95 | 93
2017-09-05 07:30 | 102 | 99
2017-09-05 08:00 | 101 | 99
2017-09-05 08:30 | 101 | 99
2017-09-05 09:00 | 103 | 101
2017-09-05 09:30 | 102 | 100
2017-09-05 10:00 | 101 | 99
2017-09-05 10:30 | 100 | 98
2017-09-05 11:00 | 100 | 98
2017-09-05 11:30 | 99 | 97
2017-09-05 12:00 | 98 | 96
2017-09-05 12:30 | 100 | 98
2017-09-05 13:00 | 101 | 99
2017-09-05 13:30 | 102 | 100
2017-09-05 14:00 | 103 | 101
2017-09-05 14:30 | 104 | 102
2017-09-05 15:00 | 104 | 102
2017-09-05 15:30 | 104 | 102
2017-09-05 16:00 | 111 | 110
2017-09-05 16:30 | 112 | 111
2017-09-05 17:00 | 110 | 109
2017-09-05 17:30 | 107 | 104
2017-09-05 18:00 | 106 | 103
2017-09-05 18:30 | 107 | 104
2017-09-05 19:00 | 109 | 107
2017-09-05 19:30 | 110 | 107
2017-09-05 20:00 | 110 | 107
2017-09-05 20:30 | 109 | 105
2017-09-05 21:00 | 108 | 104
2017-09-05 21:30 | 107 | 102
2017-09-05 22:00 | 104 | 99
2017-09-05 22:30 | 101 | 97
2017-09-05 23:00 | 100 | 96
2017-09-05 23:30 | 99 | 95
2017-09-06 | 95 | 90
2017-09-06 00:30 | 90 | 86
2017-09-06 01:00 | 90 | 85
2017-09-06 01:30 | 89 | 84
2017-09-06 02:00 | 92 | 87
2017-09-06 02:30 | 93 | 89
2017-09-06 03:00 | 87 | 87
2017-09-06 03:30 | 88 | 85
2017-09-06 04:00 | 87 | 86
2017-09-06 04:30 | 95 | 93
2017-09-06 05:00 | 100 | 98
2017-09-06 05:30 | 100 | 98
2017-09-06 06:00 | 95 | 93
2017-09-06 06:30 | 95 | 93
2017-09-06 07:00 | 96 | 93
2017-09-06 07:30 | 90 | 88
2017-09-06 08:00 | 91 | 90
2017-09-06 08:30 | 91 | 90
2017-09-06 09:00 | 86 | 86
2017-09-06 09:30 | 87 | 85
2017-09-06 10:00 | 86 | 85
2017-09-06 10:30 | 87 | 86
2017-09-06 11:00 | 87 | 86
2017-09-06 11:30 | 84 | 83
2017-09-06 12:00 | 81 | 80
2017-09-06 12:30 | 82 | 80
2017-09-06 13:00 | 84 | 83
2017-09-06 13:30 | 84 | 84
2017-09-06 14:00 | 87 | 87
2017-09-06 14:30 | 85 | 85
2017-09-06 15:00 | 84 | 83
2017-09-06 15:30 | 85 | 84
2017-09-06 16:00 | 89 | 88
2017-09-06 16:30 | 94 | 93
2017-09-06 17:00 | 102 | 101
2017-09-06 17:30 | 109 | 107
2017-09-06 18:00 | 117 | 115
2017-09-06 18:30 | 117 | 115
2017-09-06 19:00 | 117 | 115
2017-09-06 19:30 | 117 | 115
2017-09-06 20:00 | 117 | 114
2017-09-06 20:30 | 115 | 112
2017-09-06 21:00 | 115 | 112
2017-09-06 21:30 | 113 | 110
2017-09-06 22:00 | 112 | 109
2017-09-06 22:30 | 109 | 106
2017-09-06 23:00 | 105 | 101
2017-09-06 23:30 | 102 | 101
2017-09-07 | 100 | 100
2017-09-07 00:30 | 91 | 90
2017-09-07 01:00 | 91 | 91
2017-09-07 01:30 | 99 | 99
2017-09-07 02:00 | 109 | 107
2017-09-07 02:30 | 111 | 107
2017-09-07 03:00 | 109 | 106
2017-09-07 03:30 | 109 | 105
2017-09-07 04:00 | 108 | 104
2017-09-07 04:30 | 108 | 105
2017-09-07 05:00 | 108 | 105
2017-09-07 05:30 | 109 | 105
2017-09-07 06:00 | 111 | 108
2017-09-07 06:30 | 107 | 104
2017-09-07 07:00 | 105 | 102
2017-09-07 07:30 | 109 | 107
2017-09-07 08:00 | 108 | 106
2017-09-07 08:30 | 110 | 108
2017-09-07 09:00 | 112 | 111
2017-09-07 09:30 | 127 | 124
2017-09-07 10:00 | 126 | 123
2017-09-07 10:30 | 124 | 119
2017-09-07 11:00 | 124 | 120
2017-09-07 11:30 | 122 | 118
2017-09-07 12:00 | 119 | 115
2017-09-07 12:30 | 117 | 113
2017-09-07 13:00 | 118 | 114
2017-09-07 13:30 | 121 | 117
2017-09-07 14:00 | 121 | 117
2017-09-07 14:30 | 120 | 116
2017-09-07 15:00 | 123 | 118
2017-09-07 15:30 | 123 | 118
2017-09-07 16:00 | 113 | 109
2017-09-07 16:30 | 121 | 116
2017-09-07 17:00 | 122 | 119
2017-09-07 17:30 | 120 | 116
2017-09-07 18:00 | 116 | 113
2017-09-07 18:30 | 118 | 114
2017-09-07 19:00 | 118 | 114
2017-09-07 19:30 | 118 | 116
2017-09-07 20:00 | 121 | 118
2017-09-07 20:30 | 114 | 111
2017-09-07 21:00 | 110 | 106
2017-09-07 21:30 | 107 | 104
2017-09-07 22:00 | 107 | 103
2017-09-07 22:30 | 104 | 101
2017-09-07 23:00 | 102 | 99
2017-09-07 23:30 | 95 | 95
2017-09-08 | 93 | 93
2017-09-08 00:30 | 86 | 85
2017-09-08 01:00 | 82 | 81
2017-09-08 01:30 | 82 | 81
2017-09-08 02:00 | 81 | 81
2017-09-08 02:30 | 81 | 81
2017-09-08 03:00 | 79 | 79
2017-09-08 03:30 | 79 | 78
2017-09-08 04:00 | 80 | 79
2017-09-08 04:30 | 78 | 78
2017-09-08 05:00 | 78 | 77
2017-09-08 05:30 | 79 | 79
2017-09-08 06:00 | 80 | 80
2017-09-08 06:30 | 78 | 77
2017-09-08 07:00 | 83 | 82
2017-09-08 07:30 | 87 | 85
2017-09-08 08:00 | 86 | 86
2017-09-08 08:30 | 88 | 85
2017-09-08 09:00 | 89 | 87
2017-09-08 09:30 | 87 | 85
2017-09-08 10:00 | 88 | 85
2017-09-08 10:30 | 90 | 87
2017-09-08 11:00 | 87 | 84
2017-09-08 11:30 | 87 | 84
2017-09-08 12:00 | 88 | 85
2017-09-08 12:30 | 91 | 88
2017-09-08 13:00 | 87 | 86
2017-09-08 13:30 | 87 | 85
2017-09-08 14:00 | 87 | 86
2017-09-08 14:30 | 87 | 85
2017-09-08 15:00 | 86 | 84
2017-09-08 15:30 | 89 | 87
2017-09-08 16:00 | 92 | 90
2017-09-08 16:30 | 91 | 89
2017-09-08 17:00 | 96 | 93
2017-09-08 17:30 | 108 | 104
2017-09-08 18:00 | 119 | 116
2017-09-08 18:30 | 122 | 119
2017-09-08 19:00 | 116 | 113
2017-09-08 19:30 | 107 | 103
2017-09-08 20:00 | 105 | 101
2017-09-08 20:30 | 105 | 100
2017-09-08 21:00 | 104 | 99
2017-09-08 21:30 | 102 | 96
2017-09-08 22:00 | 100 | 96
2017-09-08 22:30 | 94 | 91
2017-09-08 23:00 | 92 | 91
2017-09-08 23:30 | 88 | 87
2017-09-09 | 90 | 88
2017-09-09 00:30 | 78 | 77
2017-09-09 01:00 | 75 | 74
2017-09-09 01:30 | 75 | 74
2017-09-09 02:00 | 76 | 74
2017-09-09 02:30 | 76 | 75
2017-09-09 03:00 | 75 | 75
2017-09-09 03:30 | 76 | 76
2017-09-09 04:00 | 74 | 74
2017-09-09 04:30 | 76 | 75
2017-09-09 05:00 | 78 | 77
2017-09-09 05:30 | 79 | 78
2017-09-09 06:00 | 78 | 77
2017-09-09 06:30 | 80 | 80
2017-09-09 07:00 | 83 | 82
2017-09-09 07:30 | 87 | 86
2017-09-09 08:00 | 86 | 86
2017-09-09 08:30 | 87 | 86
2017-09-09 09:00 | 84 | 84
2017-09-09 09:30 | 82 | 82
2017-09-09 10:00 | 84 | 84
2017-09-09 10:30 | 90 | 90
2017-09-09 11:00 | 89 | 89
2017-09-09 11:30 | 93 | 93
2017-09-09 12:00 | 98 | 98
2017-09-09 12:30 | 96 | 96
2017-09-09 13:00 | 89 | 89
2017-09-09 13:30 | 86 | 86
2017-09-09 14:00 | 80 | 80
2017-09-09 14:30 | 81 | 81
2017-09-09 15:00 | 80 | 80
2017-09-09 15:30 | 83 | 83
2017-09-09 16:00 | 83 | 83
2017-09-09 16:30 | 85 | 85
2017-09-09 17:00 | 86 | 86
2017-09-09 17:30 | 86 | 86
2017-09-09 18:00 | 85 | 85
2017-09-09 18:30 | 88 | 87
2017-09-09 19:00 | 90 | 90
2017-09-09 19:30 | 89 | 89
2017-09-09 20:00 | 90 | 90
2017-09-09 20:30 | 92 | 92
2017-09-09 21:00 | 93 | 93
2017-09-09 21:30 | 90 | 90
2017-09-09 22:00 | 88 | 88
2017-09-09 22:30 | 85 | 85
2017-09-09 23:00 | 84 | 83
2017-09-09 23:30 | 83 | 83
2017-09-10 | 79 | 78
2017-09-10 00:30 | 80 | 80
2017-09-10 01:00 | 79 | 77
2017-09-10 01:30 | 79 | 78
2017-09-10 02:00 | 78 | 77
2017-09-10 02:30 | 78 | 77
2017-09-10 03:00 | 77 | 76
2017-09-10 03:30 | 76 | 75
2017-09-10 04:00 | 75 | 74
2017-09-10 04:30 | 77 | 76
2017-09-10 05:00 | 78 | 77
2017-09-10 05:30 | 76 | 75
2017-09-10 06:00 | 76 | 75
2017-09-10 06:30 | 75 | 74
2017-09-10 07:00 | 76 | 75
2017-09-10 07:30 | 80 | 79
2017-09-10 08:00 | 81 | 80
2017-09-10 08:30 | 81 | 80
2017-09-10 09:00 | 81 | 81
2017-09-10 09:30 | 81 | 81
2017-09-10 10:00 | 81 | 80
2017-09-10 10:30 | 79 | 79
2017-09-10 11:00 | 79 | 79
2017-09-10 11:30 | 80 | 79
2017-09-10 12:00 | 80 | 80
2017-09-10 12:30 | 78 | 78
2017-09-10 13:00 | 79 | 79
2017-09-10 13:30 | 78 | 78
2017-09-10 14:00 | 79 | 79
2017-09-10 14:30 | 80 | 80
2017-09-10 15:00 | 83 | 83
2017-09-10 15:30 | 84 | 83
2017-09-10 16:00 | 87 | 87
2017-09-10 16:30 | 86 | 86
2017-09-10 17:00 | 88 | 87
2017-09-10 17:30 | 87 | 86
2017-09-10 18:00 | 87 | 86
2017-09-10 18:30 | 89 | 89
2017-09-10 19:00 | 91 | 89
2017-09-10 19:30 | 94 | 92
2017-09-10 20:00 | 93 | 90
2017-09-10 20:30 | 91 | 88
2017-09-10 21:00 | 91 | 87
2017-09-10 21:30 | 89 | 85
2017-09-10 22:00 | 90 | 86
2017-09-10 22:30 | 85 | 82
2017-09-10 23:00 | 81 | 79
2017-09-10 23:30 | 82 | 79
2017-09-11 | 80 | 77
2017-09-11 00:30 | 80 | 77
2017-09-11 01:00 | 80 | 78
2017-09-11 01:30 | 81 | 79
2017-09-11 02:00 | 80 | 77
2017-09-11 02:30 | 80 | 77
2017-09-11 03:00 | 78 | 78
2017-09-11 03:30 | 79 | 77
2017-09-11 04:00 | 89 | 87
2017-09-11 04:30 | 89 | 87
2017-09-11 05:00 | 91 | 85
2017-09-11 05:30 | 88 | 82
2017-09-11 06:00 | 89 | 83
2017-09-11 06:30 | 91 | 86
2017-09-11 07:00 | 93 | 90
2017-09-11 07:30 | 92 | 90
2017-09-11 08:00 | 90 | 88
2017-09-11 08:30 | 87 | 86
2017-09-11 09:00 | 85 | 84
2017-09-11 09:30 | 87 | 86
2017-09-11 10:00 | 85 | 84
2017-09-11 10:30 | 85 | 84
2017-09-11 11:00 | 87 | 85
2017-09-11 11:30 | 94 | 93
2017-09-11 12:00 | 91 | 90
2017-09-11 12:30 | 87 | 86
2017-09-11 13:00 | 92 | 91
2017-09-11 13:30 | 98 | 97
2017-09-11 14:00 | 101 | 100
2017-09-11 14:30 | 103 | 102
2017-09-11 15:00 | 103 | 102
2017-09-11 15:30 | 101 | 99
2017-09-11 16:00 | 96 | 94
2017-09-11 16:30 | 100 | 98
2017-09-11 17:00 | 107 | 105
2017-09-11 17:30 | 102 | 99
2017-09-11 18:00 | 100 | 97
2017-09-11 18:30 | 104 | 101
2017-09-11 19:00 | 107 | 104
2017-09-11 19:30 | 98 | 96
2017-09-11 20:00 | 100 | 98
2017-09-11 20:30 | 101 | 100
2017-09-11 21:00 | 101 | 99
2017-09-11 21:30 | 98 | 96
2017-09-11 22:00 | 97 | 95
2017-09-11 22:30 | 94 | 91
2017-09-11 23:00 | 90 | 87
2017-09-11 23:30 | 89 | 87
2017-09-12 | 91 | 88
2017-09-12 00:30 | 90 | 87
2017-09-12 01:00 | 86 | 84
2017-09-12 01:30 | 86 | 85
2017-09-12 02:00 | 87 | 86
2017-09-12 02:30 | 83 | 81
2017-09-12 03:00 | 82 | 81
2017-09-12 03:30 | 84 | 83
2017-09-12 04:00 | 85 | 84
2017-09-12 04:30 | 84 | 83
2017-09-12 05:00 | 81 | 80
2017-09-12 05:30 | 84 | 83
2017-09-12 06:00 | 84 | 83
2017-09-12 06:30 | 85 | 84
2017-09-12 07:00 | 92 | 91
2017-09-12 07:30 | 94 | 93
2017-09-12 08:00 | 93 | 92
2017-09-12 08:30 | 93 | 92
2017-09-12 09:00 | 92 | 91
2017-09-12 09:30 | 95 | 94
2017-09-12 10:00 | 97 | 96
2017-09-12 10:30 | 96 | 96
2017-09-12 11:00 | 95 | 94
2017-09-12 11:30 | 95 | 94
2017-09-12 12:00 | 91 | 91
2017-09-12 12:30 | 88 | 88
2017-09-12 13:00 | 88 | 87
2017-09-12 13:30 | 90 | 89
2017-09-12 14:00 | 68 | 67
2017-09-12 14:30 | 55 | 54
2017-09-12 15:00 | 59 | 58
2017-09-12 15:30 | 57 | 55
2017-09-12 16:00 | 57 | 56
2017-09-12 16:30 | 58 | 57
2017-09-12 17:00 | 60 | 59
2017-09-12 17:30 | 58 | 57
2017-09-12 18:00 | 55 | 54
2017-09-12 18:30 | 57 | 56
2017-09-12 19:00 | 58 | 57
2017-09-12 19:30 | 59 | 56
2017-09-12 20:00 | 58 | 56
2017-09-12 20:30 | 58 | 55
2017-09-12 21:00 | 57 | 54
2017-09-12 21:30 | 56 | 53
2017-09-12 22:00 | 58 | 53
2017-09-12 22:30 | 55 | 51
2017-09-12 23:00 | 52 | 49
2017-09-12 23:30 | 51 | 48
2017-09-13 | 52 | 48
2017-09-13 00:30 | 51 | 49
2017-09-13 01:00 | 49 | 48
2017-09-13 01:30 | 50 | 48
2017-09-13 02:00 | 49 | 47
2017-09-13 02:30 | 48 | 47
2017-09-13 03:00 | 48 | 46
2017-09-13 03:30 | 49 | 47
2017-09-13 04:00 | 46 | 45
2017-09-13 04:30 | 45 | 44
2017-09-13 05:00 | 45 | 43
2017-09-13 05:30 | 46 | 45
2017-09-13 06:00 | 46 | 45
2017-09-13 06:30 | 49 | 47
2017-09-13 07:00 | 72 | 70
2017-09-13 07:30 | 73 | 72
2017-09-13 08:00 | 74 | 73
2017-09-13 08:30 | 74 | 72
2017-09-13 09:00 | 60 | 59
2017-09-13 09:30 | 58 | 57
2017-09-13 10:00 | 59 | 58
2017-09-13 10:30 | 59 | 58
2017-09-13 11:00 | 58 | 57
2017-09-13 11:30 | 56 | 56
2017-09-13 12:00 | 57 | 56
2017-09-13 12:30 | 58 | 57
2017-09-13 13:00 | 59 | 58
2017-09-13 13:30 | 60 | 60
2017-09-13 14:00 | 59 | 59
2017-09-13 14:30 | 57 | 56
2017-09-13 15:00 | 58 | 57
2017-09-13 15:30 | 60 | 59
2017-09-13 16:00 | 60 | 60
2017-09-13 16:30 | 62 | 61
2017-09-13 17:00 | 63 | 62
2017-09-13 17:30 | 65 | 64
2017-09-13 18:00 | 64 | 63
2017-09-13 18:30 | 64 | 63
2017-09-13 19:00 | 65 | 65
2017-09-13 19:30 | 66 | 65
2017-09-13 20:00 | 66 | 65
2017-09-13 20:30 | 66 | 65
2017-09-13 21:00 | 66 | 65
2017-09-13 21:30 | 64 | 63
2017-09-13 22:00 | 63 | 61
2017-09-13 22:30 | 61 | 60
2017-09-13 23:00 | 61 | 59
2017-09-13 23:30 | 60 | 58
2017-09-14 | 62 | 59
2017-09-14 00:30 | 59 | 57
2017-09-14 01:00 | 56 | 55
2017-09-14 01:30 | 56 | 55
2017-09-14 02:00 | 56 | 55
2017-09-14 02:30 | 56 | 54
2017-09-14 03:00 | 56 | 55
2017-09-14 03:30 | 57 | 56
2017-09-14 04:00 | 56 | 55
2017-09-14 04:30 | 56 | 55
2017-09-14 05:00 | 56 | 55
2017-09-14 05:30 | 55 | 54
2017-09-14 06:00 | 56 | 55
2017-09-14 06:30 | 58 | 55
2017-09-14 07:00 | 60 | 57
2017-09-14 07:30 | 60 | 58
2017-09-14 08:00 | 61 | 60
2017-09-14 08:30 | 61 | 60
2017-09-14 09:00 | 60 | 59
2017-09-14 09:30 | 59 | 58
2017-09-14 10:00 | 59 | 58
2017-09-14 10:30 | 59 | 58
2017-09-14 11:00 | 59 | 58
2017-09-14 11:30 | 59 | 58
2017-09-14 12:00 | 60 | 59
2017-09-14 12:30 | 61 | 60
2017-09-14 13:00 | 64 | 63
2017-09-14 13:30 | 63 | 63
2017-09-14 14:00 | 65 | 65
2017-09-14 14:30 | 65 | 64
2017-09-14 15:00 | 68 | 68
2017-09-14 15:30 | 83 | 81
2017-09-14 16:00 | 88 | 86
2017-09-14 16:30 | 95 | 93
2017-09-14 17:00 | 102 | 100
2017-09-14 17:30 | 75 | 74
2017-09-14 18:00 | 71 | 71
2017-09-14 18:30 | 73 | 73
2017-09-14 19:00 | 71 | 70
2017-09-14 19:30 | 70 | 70
2017-09-14 20:00 | 69 | 69
2017-09-14 20:30 | 67 | 67
2017-09-14 21:00 | 67 | 66
2017-09-14 21:30 | 66 | 65
2017-09-14 22:00 | 63 | 62
2017-09-14 22:30 | 60 | 60
2017-09-14 23:00 | 58 | 57
2017-09-14 23:30 | 58 | 56
2017-09-15 | 58 | 56
2017-09-15 00:30 | 54 | 51
2017-09-15 01:00 | 52 | 48
2017-09-15 01:30 | 52 | 48
2017-09-15 02:00 | 51 | 47
2017-09-15 02:30 | 50 | 46
2017-09-15 03:00 | 51 | 46
2017-09-15 03:30 | 51 | 47
2017-09-15 04:00 | 51 | 48
2017-09-15 04:30 | 51 | 47
2017-09-15 05:00 | 50 | 46
2017-09-15 05:30 | 51 | 47
2017-09-15 06:00 | 52 | 48
2017-09-15 06:30 | 55 | 51
2017-09-15 07:00 | 58 | 54
2017-09-15 07:30 | 61 | 57
2017-09-15 08:00 | 61 | 57
2017-09-15 08:30 | 57 | 57
2017-09-15 09:00 | 57 | 57
2017-09-15 09:30 | 56 | 56
2017-09-15 10:00 | 56 | 56
2017-09-15 10:30 | 55 | 55
2017-09-15 11:00 | 54 | 54
2017-09-15 11:30 | 54 | 54
2017-09-15 12:00 | 54 | 54
2017-09-15 12:30 | 57 | 57
2017-09-15 13:00 | 58 | 58
2017-09-15 13:30 | 57 | 57
2017-09-15 14:00 | 58 | 58
2017-09-15 14:30 | 59 | 59
2017-09-15 15:00 | 57 | 57
2017-09-15 15:30 | 58 | 58
2017-09-15 16:00 | 54 | 54
2017-09-15 16:30 | 53 | 53
2017-09-15 17:00 | 52 | 52
2017-09-15 17:30 | 53 | 53
2017-09-15 18:00 | 54 | 54
2017-09-15 18:30 | 53 | 53
2017-09-15 19:00 | 56 | 56
2017-09-15 19:30 | 56 | 56
2017-09-15 20:00 | 55 | 55
2017-09-15 20:30 | 54 | 54
2017-09-15 21:00 | 54 | 53
2017-09-15 21:30 | 54 | 54
2017-09-15 22:00 | 51 | 51
2017-09-15 22:30 | 50 | 50
2017-09-15 23:00 | 49 | 48
2017-09-15 23:30 | 48 | 47
2017-09-16 | 47 | 47
2017-09-16 00:30 | 49 | 48
2017-09-16 01:00 | 50 | 48
2017-09-16 01:30 | 49 | 46
2017-09-16 02:00 | 49 | 46
2017-09-16 02:30 | 50 | 47
2017-09-16 03:00 | 50 | 48
2017-09-16 03:30 | 51 | 49
2017-09-16 04:00 | 51 | 49
2017-09-16 04:30 | 53 | 51
2017-09-16 05:00 | 51 | 49
2017-09-16 05:30 | 50 | 49
2017-09-16 06:00 | 51 | 49
2017-09-16 06:30 | 51 | 49
2017-09-16 07:00 | 52 | 51
2017-09-16 07:30 | 53 | 51
2017-09-16 08:00 | 53 | 51
2017-09-16 08:30 | 54 | 52
2017-09-16 09:00 | 56 | 53
2017-09-16 09:30 | 56 | 52
2017-09-16 10:00 | 54 | 50
2017-09-16 10:30 | 53 | 50
2017-09-16 11:00 | 55 | 52
2017-09-16 11:30 | 55 | 52
2017-09-16 12:00 | 56 | 52
2017-09-16 12:30 | 55 | 52
2017-09-16 13:00 | 56 | 53
2017-09-16 13:30 | 56 | 53
2017-09-16 14:00 | 55 | 52
2017-09-16 14:30 | 54 | 51
2017-09-16 15:00 | 53 | 49
2017-09-16 15:30 | 53 | 49
2017-09-16 16:00 | 54 | 50
2017-09-16 16:30 | 55 | 51
2017-09-16 17:00 | 55 | 51
2017-09-16 17:30 | 56 | 52
2017-09-16 18:00 | 57 | 53
2017-09-16 18:30 | 57 | 54
2017-09-16 19:00 | 57 | 54
2017-09-16 19:30 | 56 | 53
2017-09-16 20:00 | 55 | 53
2017-09-16 20:30 | 54 | 52
2017-09-16 21:00 | 52 | 50
2017-09-16 21:30 | 52 | 50
2017-09-16 22:00 | 51 | 50
2017-09-16 22:30 | 50 | 48
2017-09-16 23:00 | 48 | 46
2017-09-16 23:30 | 48 | 47
2017-09-17 | 48 | 47
2017-09-17 00:30 | 46 | 45
2017-09-17 01:00 | 47 | 45
2017-09-17 01:30 | 47 | 45
2017-09-17 02:00 | 45 | 44
2017-09-17 02:30 | 46 | 44
2017-09-17 03:00 | 47 | 45
2017-09-17 03:30 | 47 | 45
2017-09-17 04:00 | 47 | 44
2017-09-17 04:30 | 47 | 44
2017-09-17 05:00 | 47 | 45
2017-09-17 05:30 | 46 | 43
2017-09-17 06:00 | 45 | 43
2017-09-17 06:30 | 45 | 43
2017-09-17 07:00 | 47 | 45
2017-09-17 07:30 | 48 | 46
2017-09-17 08:00 | 49 | 47
2017-09-17 08:30 | 49 | 46
2017-09-17 09:00 | 50 | 48
2017-09-17 09:30 | 53 | 50
2017-09-17 10:00 | 53 | 51
2017-09-17 10:30 | 52 | 50
2017-09-17 11:00 | 53 | 51
2017-09-17 11:30 | 53 | 51
2017-09-17 12:00 | 51 | 49
2017-09-17 12:30 | 51 | 49
2017-09-17 13:00 | 52 | 49
2017-09-17 13:30 | 51 | 49
2017-09-17 14:00 | 51 | 49
2017-09-17 14:30 | 51 | 49
2017-09-17 15:00 | 53 | 50
2017-09-17 15:30 | 52 | 50
2017-09-17 16:00 | 53 | 51
2017-09-17 16:30 | 54 | 52
2017-09-17 17:00 | 53 | 51
2017-09-17 17:30 | 50 | 50
2017-09-17 18:00 | 52 | 51
2017-09-17 18:30 | 54 | 53
2017-09-17 19:00 | 53 | 53
2017-09-17 19:30 | 56 | 54
2017-09-17 20:00 | 56 | 54
2017-09-17 20:30 | 55 | 53
2017-09-17 21:00 | 54 | 52
2017-09-17 21:30 | 54 | 51
2017-09-17 22:00 | 53 | 50
2017-09-17 22:30 | 50 | 48
2017-09-17 23:00 | 48 | 46
2017-09-17 23:30 | 48 | 46
2017-09-18 | 47 | 46
2017-09-18 00:30 | 47 | 45
2017-09-18 01:00 | 50 | 48
2017-09-18 01:30 | 49 | 48
2017-09-18 02:00 | 51 | 49
2017-09-18 02:30 | 50 | 48
2017-09-18 03:00 | 49 | 47
2017-09-18 03:30 | 49 | 47
2017-09-18 04:00 | 48 | 46
2017-09-18 04:30 | 48 | 47
2017-09-18 05:00 | 47 | 46
2017-09-18 05:30 | 48 | 46
2017-09-18 06:00 | 46 | 45
2017-09-18 06:30 | 46 | 45
2017-09-18 07:00 | 48 | 48
2017-09-18 07:30 | 49 | 49
2017-09-18 08:00 | 49 | 49
2017-09-18 08:30 | 50 | 50
2017-09-18 09:00 | 51 | 51
2017-09-18 09:30 | 49 | 49
2017-09-18 10:00 | 50 | 50
2017-09-18 10:30 | 51 | 51
2017-09-18 11:00 | 53 | 53
2017-09-18 11:30 | 52 | 52
2017-09-18 12:00 | 52 | 52
2017-09-18 12:30 | 53 | 53
2017-09-18 13:00 | 53 | 53
2017-09-18 13:30 | 55 | 54
2017-09-18 14:00 | 56 | 56
2017-09-18 14:30 | 55 | 55
2017-09-18 15:00 | 56 | 56
2017-09-18 15:30 | 56 | 56
2017-09-18 16:00 | 59 | 58
2017-09-18 16:30 | 59 | 58
2017-09-18 17:00 | 56 | 55
2017-09-18 17:30 | 52 | 51
2017-09-18 18:00 | 53 | 52
2017-09-18 18:30 | 57 | 56
2017-09-18 19:00 | 60 | 59
2017-09-18 19:30 | 62 | 61
2017-09-18 20:00 | 61 | 60
2017-09-18 20:30 | 54 | 53
2017-09-18 21:00 | 52 | 52
2017-09-18 21:30 | 52 | 51
2017-09-18 22:00 | 51 | 50
2017-09-18 22:30 | 48 | 48
2017-09-18 23:00 | 48 | 47
2017-09-18 23:30 | 48 | 47
2017-09-19 | 49 | 48
2017-09-19 00:30 | 49 | 48
2017-09-19 01:00 | 49 | 48
2017-09-19 01:30 | 50 | 49
2017-09-19 02:00 | 49 | 47
2017-09-19 02:30 | 49 | 48
2017-09-19 03:00 | 48 | 47
2017-09-19 03:30 | 47 | 46
2017-09-19 04:00 | 48 | 47
2017-09-19 04:30 | 49 | 47
2017-09-19 05:00 | 49 | 48
2017-09-19 05:30 | 51 | 50
2017-09-19 06:00 | 54 | 53
2017-09-19 06:30 | 54 | 52
2017-09-19 07:00 | 54 | 52
2017-09-19 07:30 | 55 | 53
2017-09-19 08:00 | 54 | 53
2017-09-19 08:30 | 54 | 53
2017-09-19 09:00 | 28 | 27
2017-09-19 09:30 | 1 | 1
2017-09-19 10:00 | 1 | 1
2017-09-19 10:30 | 1 | 1
2017-09-19 11:00 | 1 | 1
2017-09-19 11:30 | 1 | 1
2017-09-19 12:00 | 1 | 1
2017-09-19 12:30 | 1 | 1
2017-09-19 13:00 | 1 | 1
2017-09-19 13:30 | 1 | 1
2017-09-19 14:00 | 1 | 1
2017-09-19 14:30 | 1 | 1
2017-09-19 15:00 | 1 | 1
2017-09-19 15:30 | 1 | 1
2017-09-19 16:00 | 1 | 1
2017-09-19 16:30 | 1 | 1
2017-09-19 17:00 | 1 | 1
2017-09-19 17:30 | 1 | 1
2017-09-19 18:00 | 1 | 1
2017-09-19 18:30 | 1 | 1
2017-09-19 19:00 | 1 | 1
2017-09-19 19:30 | 1 | 1
2017-09-19 20:00 | 1 | 1
2017-09-19 20:30 | 1 | 1
2017-09-19 21:00 | 1 | 1
2017-09-19 21:30 | 1 | 1
2017-09-19 22:00 | 1 | 1
2017-09-19 22:30 | 1 | 1
2017-09-19 23:00 | 1 | 1
2017-09-19 23:30 | 1 | 1
2017-09-20 | 1 | 1
2017-09-20 00:30 | 1 | 1
2017-09-20 01:00 | 1 | 1
2017-09-20 01:30 | 1 | 1
2017-09-20 02:00 | 1 | 1
2017-09-20 02:30 | 1 | 1
2017-09-20 03:00 | 1 | 1
2017-09-20 03:30 | 1 | 1
2017-09-20 04:00 | 1 | 1
2017-09-20 04:30 | 1 | 1
2017-09-20 05:00 | 1 | 1
2017-09-20 05:30 | 1 | 1
2017-09-20 06:00 | 1 | 1
2017-09-20 06:30 | 1 | 1
2017-09-20 07:00 | 1 | 1
2017-09-20 07:30 | 1 | 1
2017-09-20 08:00 | 1 | 1
2017-09-20 08:30 | 1 | 1
2017-09-20 09:00 | 1 | 1
2017-09-20 09:30 | 1 | 1
2017-09-20 10:00 | 1 | 1
2017-09-20 10:30 | 1 | 1
2017-09-20 11:00 | 1 | 1
2017-09-20 11:30 | 1 | 1
2017-09-20 12:00 | 1 | 1
2017-09-20 12:30 | 1 | 1
2017-09-20 13:00 | 1 | 1
2017-09-20 13:30 | 1 | 1
2017-09-20 14:00 | 1 | 1
2017-09-20 14:30 | 1 | 1
2017-09-20 15:00 | 1 | 1
2017-09-20 15:30 | 1 | 1
2017-09-20 16:00 | 1 | 1
2017-09-20 16:30 | 1 | 1
2017-09-20 17:00 | 1 | 1
2017-09-20 17:30 | 1 | 1
2017-09-20 18:00 | 1 | 1
2017-09-20 18:30 | 1 | 1
2017-09-20 19:00 | 1 | 1
2017-09-20 19:30 | 1 | 1
2017-09-20 20:00 | 1 | 1
2017-09-20 20:30 | 1 | 1
2017-09-20 21:00 | 1 | 1
2017-09-20 21:30 | 1 | 1
2017-09-20 22:00 | 1 | 1
2017-09-20 22:30 | 1 | 1
2017-09-20 23:00 | 1 | 1
2017-09-20 23:30 | 1 | 1
2017-09-21 | 1 | 1
2017-09-21 00:30 | 1 | 1
2017-09-21 01:00 | 1 | 1
2017-09-21 01:30 | 1 | 1
2017-09-21 02:00 | 1 | 1
2017-09-21 02:30 | 1 | 1
2017-09-21 03:00 | 1 | 1
2017-09-21 03:30 | 1 | 1
2017-09-21 04:00 | 1 | 1
2017-09-21 04:30 | 1 | 1
2017-09-21 05:00 | 1 | 1
2017-09-21 05:30 | 1 | 1
2017-09-21 06:00 | 1 | 1
2017-09-21 06:30 | 1 | 1
2017-09-21 07:00 | 1 | 1
2017-09-21 07:30 | 1 | 1
2017-09-21 08:00 | 1 | 1
2017-09-21 08:30 | 1 | 1
2017-09-21 09:00 | 1 | 1
2017-09-21 09:30 | 1 | 1
2017-09-21 10:00 | 1 | 1
2017-09-21 10:30 | 1 | 1
2017-09-21 11:00 | 1 | 1
2017-09-21 11:30 | 1 | 1
2017-09-21 12:00 | 1 | 1
2017-09-21 12:30 | 1 | 1
2017-09-21 13:00 | 1 | 1
2017-09-21 13:30 | 1 | 1
2017-09-21 14:00 | 1 | 1
2017-09-21 14:30 | 1 | 1
2017-09-21 15:00 | 1 | 1
2017-09-21 15:30 | 1 | 1
2017-09-21 16:00 | 1 | 1
2017-09-21 16:30 | 1 | 1
2017-09-21 17:00 | 1 | 1
2017-09-21 17:30 | 1 | 1
2017-09-21 18:00 | 1 | 1
2017-09-21 18:30 | 1 | 1
2017-09-21 19:00 | 1 | 1
2017-09-21 19:30 | 1 | 1
2017-09-21 20:00 | 1 | 1
2017-09-21 20:30 | 1 | 1
2017-09-21 21:00 | 1 | 1
2017-09-21 21:30 | 1 | 1
2017-09-21 22:00 | 1 | 1
2017-09-21 22:30 | 1 | 1
2017-09-21 23:00 | 1 | 1
2017-09-21 23:30 | 1 | 1
2017-09-22 | 1 | 1
2017-09-22 00:30 | 1 | 1
2017-09-22 01:00 | 1 | 1
2017-09-22 01:30 | 1 | 1
2017-09-22 02:00 | 1 | 1
2017-09-22 02:30 | 1 | 1
2017-09-22 03:00 | 1 | 1
2017-09-22 03:30 | 1 | 1
2017-09-22 04:00 | 1 | 1
2017-09-22 04:30 | 1 | 1
2017-09-22 05:00 | 1 | 1
2017-09-22 05:30 | 1 | 1
2017-09-22 06:00 | 1 | 1
2017-09-22 06:30 | 1 | 1
2017-09-22 07:00 | 1 | 1
2017-09-22 07:30 | 1 | 1
2017-09-22 08:00 | 1 | 1
2017-09-22 08:30 | 1 | 1
2017-09-22 09:00 | 1 | 1
2017-09-22 09:30 | 1 | 1
2017-09-22 10:00 | 1 | 1
2017-09-22 10:30 | 1 | 1
2017-09-22 11:00 | 1 | 1
2017-09-22 11:30 | 1 | 1
2017-09-22 12:00 | 1 | 1
2017-09-22 12:30 | 1 | 1
2017-09-22 13:00 | 1 | 1
2017-09-22 13:30 | 1 | 1
2017-09-22 14:00 | 1 | 1
2017-09-22 14:30 | 1 | 1
2017-09-22 15:00 | 1 | 1
2017-09-22 15:30 | 1 | 1
2017-09-22 16:00 | 1 | 1
2017-09-22 16:30 | 1 | 1
2017-09-22 17:00 | 1 | 1
2017-09-22 17:30 | 1 | 1
2017-09-22 18:00 | 1 | 1
2017-09-22 18:30 | 1 | 1
2017-09-22 19:00 | 1 | 1
2017-09-22 19:30 | 1 | 1
2017-09-22 20:00 | 1 | 1
2017-09-22 20:30 | 1 | 1
2017-09-22 21:00 | 1 | 1
2017-09-22 21:30 | 1 | 1
2017-09-22 22:00 | 1 | 1
2017-09-22 22:30 | 1 | 1
2017-09-22 23:00 | 1 | 1
2017-09-22 23:30 | 1 | 1
2017-09-23 | 1 | 1
2017-09-23 00:30 | 1 | 1
2017-09-23 01:00 | 1 | 1
2017-09-23 01:30 | 1 | 1
2017-09-23 02:00 | 1 | 1
2017-09-23 02:30 | 1 | 1
2017-09-23 03:00 | 1 | 1
2017-09-23 03:30 | 1 | 1
2017-09-23 04:00 | 1 | 1
2017-09-23 04:30 | 1 | 1
2017-09-23 05:00 | 1 | 1
2017-09-23 05:30 | 1 | 1
2017-09-23 06:00 | 1 | 1
2017-09-23 06:30 | 1 | 1
2017-09-23 07:00 | 1 | 1
2017-09-23 07:30 | 1 | 1
2017-09-23 08:00 | 1 | 1
2017-09-23 08:30 | 1 | 1
2017-09-23 09:00 | 1 | 1
2017-09-23 09:30 | 1 | 1
2017-09-23 10:00 | 1 | 1
2017-09-23 10:30 | 1 | 1
2017-09-23 11:00 | 1 | 1
2017-09-23 11:30 | 1 | 1
2017-09-23 12:00 | 1 | 1
2017-09-23 12:30 | 1 | 1
2017-09-23 13:00 | 1 | 1
2017-09-23 13:30 | 1 | 1
2017-09-23 14:00 | 1 | 1
2017-09-23 14:30 | 1 | 1
2017-09-23 15:00 | 1 | 1
2017-09-23 15:30 | 1 | 1
2017-09-23 16:00 | 1 | 1
2017-09-23 16:30 | 1 | 1
2017-09-23 17:00 | 1 | 1
2017-09-23 17:30 | 1 | 1
2017-09-23 18:00 | 1 | 1
2017-09-23 18:30 | 1 | 1
2017-09-23 19:00 | 1 | 1
2017-09-23 19:30 | 1 | 1
2017-09-23 20:00 | 1 | 1
2017-09-23 20:30 | 1 | 1
2017-09-23 21:00 | 1 | 1
2017-09-23 21:30 | 1 | 1
2017-09-23 22:00 | 1 | 1
2017-09-23 22:30 | 1 | 1
2017-09-23 23:00 | 1 | 1
2017-09-23 23:30 | 1 | 1
2017-09-24 | 1 | 1
2017-09-24 00:30 | 1 | 1
2017-09-24 01:00 | 1 | 1
2017-09-24 01:30 | 1 | 1
2017-09-24 02:00 | 1 | 1
2017-09-24 02:30 | 1 | 1
2017-09-24 03:00 | 1 | 1
2017-09-24 03:30 | 1 | 1
2017-09-24 04:00 | 1 | 1
2017-09-24 04:30 | 1 | 1
2017-09-24 05:00 | 1 | 1
2017-09-24 05:30 | 1 | 1
2017-09-24 06:00 | 1 | 1
2017-09-24 06:30 | 1 | 1
2017-09-24 07:00 | 1 | 1
2017-09-24 07:30 | 1 | 1
2017-09-24 08:00 | 1 | 1
2017-09-24 08:30 | 1 | 1
2017-09-24 09:00 | 1 | 1
2017-09-24 09:30 | 1 | 1
2017-09-24 10:00 | 1 | 1
2017-09-24 10:30 | 1 | 1
2017-09-24 11:00 | 1 | 1
2017-09-24 11:30 | 1 | 1
2017-09-24 12:00 | 1 | 1
2017-09-24 12:30 | 1 | 1
2017-09-24 13:00 | 1 | 1
2017-09-24 13:30 | 1 | 1
2017-09-24 14:00 | 1 | 1
2017-09-24 14:30 | 1 | 1
2017-09-24 15:00 | 1 | 1
2017-09-24 15:30 | 1 | 1
2017-09-24 16:00 | 1 | 1
2017-09-24 16:30 | 1 | 1
2017-09-24 17:00 | 1 | 1
2017-09-24 17:30 | 1 | 1
2017-09-24 18:00 | 1 | 1
2017-09-24 18:30 | 1 | 1
2017-09-24 19:00 | 1 | 1
2017-09-24 19:30 | 1 | 1
2017-09-24 20:00 | 1 | 1
2017-09-24 20:30 | 1 | 1
2017-09-24 21:00 | 1 | 1
2017-09-24 21:30 | 1 | 1
2017-09-24 22:00 | 1 | 1
2017-09-24 22:30 | 1 | 1
2017-09-24 23:00 | 1 | 1
2017-09-24 23:30 | 1 | 1
2017-09-25 | 1 | 1
2017-09-25 00:30 | 1 | 1
2017-09-25 01:00 | 1 | 1
2017-09-25 01:30 | 1 | 1
2017-09-25 02:00 | 1 | 1
2017-09-25 02:30 | 1 | 1
2017-09-25 03:00 | 1 | 1
2017-09-25 03:30 | 1 | 1
2017-09-25 04:00 | 1 | 1
2017-09-25 04:30 | 1 | 1
2017-09-25 05:00 | 1 | 1
2017-09-25 05:30 | 1 | 1
2017-09-25 06:00 | 1 | 1
2017-09-25 06:30 | 1 | 1
2017-09-25 07:00 | 1 | 1
2017-09-25 07:30 | 1 | 1
2017-09-25 08:00 | 1 | 1
2017-09-25 08:30 | 1 | 1
2017-09-25 09:00 | 1 | 1
2017-09-25 09:30 | 1 | 1
2017-09-25 10:00 | 1 | 1
2017-09-25 10:30 | 1 | 1
2017-09-25 11:00 | 1 | 1
2017-09-25 11:30 | 1 | 1
2017-09-25 12:00 | 1 | 1
2017-09-25 12:30 | 1 | 1
2017-09-25 13:00 | 1 | 1
2017-09-25 13:30 | 1 | 1
2017-09-25 14:00 | 1 | 1
2017-09-25 14:30 | 1 | 1
2017-09-25 15:00 | 1 | 1
2017-09-25 15:30 | 1 | 1
2017-09-25 16:00 | 1 | 1
2017-09-25 16:30 | 1 | 1
2017-09-25 17:00 | 1 | 1
2017-09-25 17:30 | 1 | 1
2017-09-25 18:00 | 1 | 1
2017-09-25 18:30 | 1 | 1
2017-09-25 19:00 | 1 | 1
2017-09-25 19:30 | 1 | 1
2017-09-25 20:00 | 1 | 1
2017-09-25 20:30 | 1 | 1
2017-09-25 21:00 | 1 | 1
2017-09-25 21:30 | 1 | 1
2017-09-25 22:00 | 1 | 1
2017-09-25 22:30 | 1 | 1
2017-09-25 23:00 | 1 | 1
2017-09-25 23:30 | 1 | 1
2017-09-26 | 1 | 1
2017-09-26 00:30 | 1 | 1
2017-09-26 01:00 | 1 | 1
2017-09-26 01:30 | 1 | 1
2017-09-26 02:00 | 1 | 1
2017-09-26 02:30 | 1 | 1
2017-09-26 03:00 | 1 | 1
2017-09-26 03:30 | 1 | 1
2017-09-26 04:00 | 1 | 1
2017-09-26 04:30 | 1 | 1
2017-09-26 05:00 | 1 | 1
2017-09-26 05:30 | 1 | 1
2017-09-26 06:00 | 1 | 1
2017-09-26 06:30 | 1 | 1
2017-09-26 07:00 | 1 | 1
2017-09-26 07:30 | 1 | 1
2017-09-26 08:00 | 1 | 1
2017-09-26 08:30 | 1 | 1
2017-09-26 09:00 | 1 | 1
2017-09-26 09:30 | 1 | 1
2017-09-26 10:00 | 1 | 1
2017-09-26 10:30 | 1 | 1
2017-09-26 11:00 | 1 | 1
2017-09-26 11:30 | 1 | 1
2017-09-26 12:00 | 1 | 1
2017-09-26 12:30 | 1 | 1
2017-09-26 13:00 | 1 | 1
2017-09-26 13:30 | 1 | 1
2017-09-26 14:00 | 1 | 1
2017-09-26 14:30 | 1 | 1
2017-09-26 15:00 | 1 | 1
2017-09-26 15:30 | 1 | 1
2017-09-26 16:00 | 1 | 1
2017-09-26 16:30 | 1 | 1
2017-09-26 17:00 | 1 | 1
2017-09-26 17:30 | 1 | 1
2017-09-26 18:00 | 1 | 1
2017-09-26 18:30 | 1 | 1
2017-09-26 19:00 | 1 | 1
2017-09-26 19:30 | 1 | 1
2017-09-26 20:00 | 1 | 1
2017-09-26 20:30 | 1 | 1
2017-09-26 21:00 | 1 | 1
2017-09-26 21:30 | 1 | 1
2017-09-26 22:00 | 1 | 1
2017-09-26 22:30 | 1 | 1
2017-09-26 23:00 | 1 | 1
2017-09-26 23:30 | 1 | 1
2017-09-27 | 1 | 1
2017-09-27 00:30 | 1 | 1
2017-09-27 01:00 | 1 | 1
2017-09-27 01:30 | 1 | 1
2017-09-27 02:00 | 1 | 1
2017-09-27 02:30 | 1 | 1
2017-09-27 03:00 | 1 | 1
2017-09-27 03:30 | 1 | 1
2017-09-27 04:00 | 1 | 1
2017-09-27 04:30 | 1 | 1
2017-09-27 05:00 | 1 | 1
2017-09-27 05:30 | 1 | 1
2017-09-27 06:00 | 1 | 1
2017-09-27 06:30 | 1 | 1
2017-09-27 07:00 | 1 | 1
2017-09-27 07:30 | 1 | 1
2017-09-27 08:00 | 1 | 1
2017-09-27 08:30 | 1 | 1
2017-09-27 09:00 | 1 | 1
2017-09-27 09:30 | 0 | 0
2017-09-27 10:00 | 0 | 0
2017-09-27 10:30 | 0 | 0
2017-09-27 11:00 | 0 | 0
2017-09-27 11:30 | 0 | 0
2017-09-27 12:00 | 0 | 0
2017-09-27 12:30 | 0 | 0
2017-09-27 13:00 | 0 | 0
2017-09-27 13:30 | 0 | 0
2017-09-27 14:00 | 0 | 0
2017-09-27 14:30 | 0 | 0
2017-09-27 15:00 | 0 | 0
2017-09-27 15:30 | 0 | 0
2017-09-27 16:00 | 0 | 0
2017-09-27 16:30 | 0 | 0
2017-09-27 17:00 | 0 | 0
2017-09-27 17:30 | 0 | 0
2017-09-27 18:00 | 0 | 0
2017-09-27 18:30 | 0 | 0
2017-09-27 19:00 | 0 | 0
2017-09-27 19:30 | 0 | 0
2017-09-27 20:00 | 0 | 0
2017-09-27 20:30 | 0 | 0
2017-09-27 21:00 | 0 | 0
2017-09-27 21:30 | 0 | 0
2017-09-27 22:00 | 0 | 0
2017-09-27 22:30 | 0 | 0
2017-09-27 23:00 | 0 | 0
2017-09-27 23:30 | 0 | 0
2017-09-28 | 0 | 0
2017-09-28 00:30 | 0 | 0
2017-09-28 01:00 | 0 | 0
2017-09-28 01:30 | 0 | 0
2017-09-28 02:00 | 0 | 0
2017-09-28 02:30 | 0 | 0
2017-09-28 03:00 | 0 | 0
2017-09-28 03:30 | 0 | 0
2017-09-28 04:00 | 0 | 0
2017-09-28 04:30 | 0 | 0
2017-09-28 05:00 | 0 | 0
2017-09-28 05:30 | 0 | 0
2017-09-28 06:00 | 0 | 0
2017-09-28 06:30 | 0 | 0
2017-09-28 07:00 | 0 | 0
2017-09-28 07:30 | 0 | 0
2017-09-28 08:00 | 0 | 0
2017-09-28 08:30 | 0 | 0
2017-09-28 09:00 | 0 | 0
2017-09-28 09:30 | 0 | 0
2017-09-28 10:00 | 0 | 0
2017-09-28 10:30 | 0 | 0
2017-09-28 11:00 | 0 | 0
2017-09-28 11:30 | 1 | 0
2017-09-28 12:00 | 43 | 42
2017-09-28 12:30 | 63 | 62
2017-09-28 13:00 | 69 | 68
2017-09-28 13:30 | 67 | 66
2017-09-28 14:00 | 67 | 66
2017-09-28 14:30 | 68 | 68
2017-09-28 15:00 | 68 | 67
2017-09-28 15:30 | 68 | 67
2017-09-28 16:00 | 70 | 70
2017-09-28 16:30 | 58 | 58
2017-09-28 17:00 | 48 | 48
2017-09-28 17:30 | 53 | 53
2017-09-28 18:00 | 46 | 46
2017-09-28 18:30 | 9 | 9
2017-09-28 19:00 | 7 | 6
2017-09-28 19:30 | 46 | 46
2017-09-28 20:00 | 46 | 46
2017-09-28 20:30 | 45 | 45
2017-09-28 21:00 | 58 | 56
2017-09-28 21:30 | 59 | 56
2017-09-28 22:00 | 57 | 55
2017-09-28 22:30 | 56 | 54
2017-09-28 23:00 | 54 | 52
2017-09-28 23:30 | 49 | 47
2017-09-29 | 50 | 48
2017-09-29 00:30 | 50 | 48
2017-09-29 01:00 | 48 | 47
2017-09-29 01:30 | 48 | 47
2017-09-29 02:00 | 49 | 47
2017-09-29 02:30 | 47 | 46
2017-09-29 03:00 | 47 | 45
2017-09-29 03:30 | 48 | 47
2017-09-29 04:00 | 47 | 46
2017-09-29 04:30 | 48 | 47
2017-09-29 05:00 | 48 | 47
2017-09-29 05:30 | 47 | 46
2017-09-29 06:00 | 47 | 46
2017-09-29 06:30 | 48 | 47
2017-09-29 07:00 | 50 | 49
2017-09-29 07:30 | 50 | 49
2017-09-29 08:00 | 51 | 50
2017-09-29 08:30 | 51 | 50
2017-09-29 09:00 | 50 | 50
2017-09-29 09:30 | 57 | 57
2017-09-29 10:00 | 60 | 60
2017-09-29 10:30 | 54 | 53
2017-09-29 11:00 | 53 | 53
2017-09-29 11:30 | 53 | 53
2017-09-29 12:00 | 53 | 53
2017-09-29 12:30 | 54 | 54
2017-09-29 13:00 | 57 | 57
2017-09-29 13:30 | 58 | 58
2017-09-29 14:00 | 56 | 56
2017-09-29 14:30 | 56 | 56
2017-09-29 15:00 | 56 | 56
2017-09-29 15:30 | 54 | 54
2017-09-29 16:00 | 46 | 46
2017-09-29 16:30 | 48 | 48
2017-09-29 17:00 | 50 | 50
2017-09-29 17:30 | 49 | 49
2017-09-29 18:00 | 49 | 48
2017-09-29 18:30 | 51 | 51
2017-09-29 19:00 | 50 | 50
2017-09-29 19:30 | 49 | 49
2017-09-29 20:00 | 48 | 48
2017-09-29 20:30 | 48 | 47
2017-09-29 21:00 | 43 | 42
2017-09-29 21:30 | 44 | 42
2017-09-29 22:00 | 43 | 42
2017-09-29 22:30 | 43 | 42
2017-09-29 23:00 | 42 | 41
2017-09-29 23:30 | 51 | 51
2017-09-30 | 52 | 51
2017-09-30 00:30 | 50 | 50
2017-09-30 01:00 | 50 | 50
2017-09-30 01:30 | 50 | 49
2017-09-30 02:00 | 50 | 49
2017-09-30 02:30 | 51 | 50
2017-09-30 03:00 | 53 | 52
2017-09-30 03:30 | 54 | 53
2017-09-30 04:00 | 54 | 53
2017-09-30 04:30 | 53 | 52
2017-09-30 05:00 | 52 | 51
2017-09-30 05:30 | 51 | 50
2017-09-30 06:00 | 52 | 51
2017-09-30 06:30 | 52 | 51
2017-09-30 07:00 | 52 | 51
2017-09-30 07:30 | 52 | 52
2017-09-30 08:00 | 54 | 53
2017-09-30 08:30 | 54 | 53
2017-09-30 09:00 | 54 | 54
2017-09-30 09:30 | 54 | 54
2017-09-30 10:00 | 55 | 55
2017-09-30 10:30 | 55 | 54
2017-09-30 11:00 | 54 | 54
2017-09-30 11:30 | 53 | 53
2017-09-30 12:00 | 52 | 52
2017-09-30 12:30 | 54 | 54
2017-09-30 13:00 | 56 | 56
2017-09-30 13:30 | 55 | 55
2017-09-30 14:00 | 55 | 55
2017-09-30 14:30 | 54 | 54
2017-09-30 15:00 | 53 | 53
2017-09-30 15:30 | 52 | 52
2017-09-30 16:00 | 57 | 57
2017-09-30 16:30 | 59 | 59
2017-09-30 17:00 | 58 | 58
2017-09-30 17:30 | 58 | 58
2017-09-30 18:00 | 58 | 58
2017-09-30 18:30 | 60 | 60
2017-09-30 19:00 | 51 | 49
2017-09-30 19:30 | 50 | 48
2017-09-30 20:00 | 60 | 59
2017-09-30 20:30 | 54 | 54
2017-09-30 21:00 | 54 | 53
2017-09-30 21:30 | 53 | 53
2017-09-30 22:00 | 53 | 53
2017-09-30 22:30 | 52 | 52
2017-09-30 23:00 | 53 | 52
2017-09-30 23:30 | 52 | 52
2017-10-01 | 50 | 50
2017-10-01 00:30 | 51 | 50
2017-10-01 01:00 | 51 | 50
2017-10-01 01:30 | 50 | 49
2017-10-01 02:00 | 50 | 50
2017-10-01 02:30 | 52 | 51
2017-10-01 03:00 | 51 | 50
2017-10-01 03:30 | 51 | 50
2017-10-01 04:00 | 51 | 50
2017-10-01 04:30 | 50 | 49
2017-10-01 05:00 | 50 | 49
2017-10-01 05:30 | 50 | 49
2017-10-01 06:00 | 51 | 51
2017-10-01 06:30 | 50 | 49
2017-10-01 07:00 | 50 | 50
2017-10-01 07:30 | 51 | 50
2017-10-01 08:00 | 52 | 52
2017-10-01 08:30 | 60 | 60
2017-10-01 09:00 | 62 | 62
2017-10-01 09:30 | 63 | 62
2017-10-01 10:00 | 62 | 62
2017-10-01 10:30 | 62 | 61
2017-10-01 11:00 | 62 | 61
2017-10-01 11:30 | 62 | 61
2017-10-01 12:00 | 62 | 61
2017-10-01 12:30 | 62 | 62
2017-10-01 13:00 | 64 | 63
2017-10-01 13:30 | 63 | 62
2017-10-01 14:00 | 61 | 60
2017-10-01 14:30 | 61 | 60
2017-10-01 15:00 | 61 | 60
2017-10-01 15:30 | 61 | 61
2017-10-01 16:00 | 58 | 57
2017-10-01 16:30 | 14 | 13
2017-10-01 17:00 | 10 | 8
2017-10-01 17:30 | 8 | 7
2017-10-01 18:00 | 7 | 5
2017-10-01 18:30 | 7 | 3
2017-10-01 19:00 | 7 | 4
2017-10-01 19:30 | 34 | 33
2017-10-01 20:00 | 44 | 44
2017-10-01 20:30 | 54 | 54
2017-10-01 21:00 | 57 | 56
2017-10-01 21:30 | 56 | 55
2017-10-01 22:00 | 54 | 54
2017-10-01 22:30 | 55 | 54
2017-10-01 23:00 | 54 | 53
2017-10-01 23:30 | 53 | 52
2017-10-02 | 51 | 50
2017-10-02 00:30 | 51 | 50
2017-10-02 01:00 | 51 | 50
2017-10-02 01:30 | 51 | 50
2017-10-02 02:00 | 50 | 49
2017-10-02 02:30 | 51 | 50
2017-10-02 03:00 | 50 | 49
2017-10-02 03:30 | 50 | 49
2017-10-02 04:00 | 50 | 49
2017-10-02 04:30 | 49 | 48
2017-10-02 05:00 | 48 | 47
2017-10-02 05:30 | 49 | 48
2017-10-02 06:00 | 50 | 49
2017-10-02 06:30 | 49 | 48
2017-10-02 07:00 | 50 | 50
2017-10-02 07:30 | 51 | 50
2017-10-02 08:00 | 52 | 51
2017-10-02 08:30 | 52 | 52
2017-10-02 09:00 | 50 | 50
2017-10-02 09:30 | 50 | 49
2017-10-02 10:00 | 51 | 51
2017-10-02 10:30 | 52 | 51
2017-10-02 11:00 | 51 | 51
2017-10-02 11:30 | 52 | 52
2017-10-02 12:00 | 51 | 50
2017-10-02 12:30 | 52 | 52
2017-10-02 13:00 | 52 | 51
2017-10-02 13:30 | 49 | 49
2017-10-02 14:00 | 48 | 48
2017-10-02 14:30 | 48 | 47
2017-10-02 15:00 | 49 | 48
2017-10-02 15:30 | 51 | 51
2017-10-02 16:00 | 56 | 56
2017-10-02 16:30 | 58 | 58
2017-10-02 17:00 | 59 | 59
2017-10-02 17:30 | 60 | 60
2017-10-02 18:00 | 60 | 59
2017-10-02 18:30 | 60 | 60
2017-10-02 19:00 | 61 | 61
2017-10-02 19:30 | 59 | 59
2017-10-02 20:00 | 54 | 54
2017-10-02 20:30 | 53 | 53
2017-10-02 21:00 | 54 | 54
2017-10-02 21:30 | 55 | 54
2017-10-02 22:00 | 54 | 53
2017-10-02 22:30 | 52 | 51
2017-10-02 23:00 | 53 | 52
2017-10-02 23:30 | 52 | 51
2017-10-03 | 50 | 50
2017-10-03 00:30 | 50 | 49
2017-10-03 01:00 | 50 | 50
2017-10-03 01:30 | 50 | 49
2017-10-03 02:00 | 51 | 50
2017-10-03 02:30 | 51 | 50
2017-10-03 03:00 | 50 | 49
2017-10-03 03:30 | 50 | 49
2017-10-03 04:00 | 50 | 49
2017-10-03 04:30 | 50 | 49
2017-10-03 05:00 | 49 | 49
2017-10-03 05:30 | 50 | 50
2017-10-03 06:00 | 48 | 47
2017-10-03 06:30 | 48 | 48
2017-10-03 07:00 | 50 | 50
2017-10-03 07:30 | 53 | 53
2017-10-03 08:00 | 56 | 56
2017-10-03 08:30 | 59 | 59
2017-10-03 09:00 | 59 | 59
2017-10-03 09:30 | 58 | 58
2017-10-03 10:00 | 59 | 59
2017-10-03 10:30 | 60 | 60
2017-10-03 11:00 | 60 | 59
2017-10-03 11:30 | 58 | 58
2017-10-03 12:00 | 57 | 57
2017-10-03 12:30 | 56 | 56
2017-10-03 13:00 | 56 | 56
2017-10-03 13:30 | 54 | 54
2017-10-03 14:00 | 54 | 54
2017-10-03 14:30 | 56 | 56
2017-10-03 15:00 | 56 | 56
2017-10-03 15:30 | 58 | 58
2017-10-03 16:00 | 61 | 61
2017-10-03 16:30 | 64 | 64
2017-10-03 17:00 | 64 | 64
2017-10-03 17:30 | 65 | 65
2017-10-03 18:00 | 53 | 52
2017-10-03 18:30 | 45 | 40
2017-10-03 19:00 | 58 | 57
2017-10-03 19:30 | 64 | 64
2017-10-03 20:00 | 64 | 64
2017-10-03 20:30 | 66 | 66
2017-10-03 21:00 | 63 | 63
2017-10-03 21:30 | 59 | 59
2017-10-03 22:00 | 57 | 57
2017-10-03 22:30 | 56 | 56
2017-10-03 23:00 | 55 | 55
2017-10-03 23:30 | 56 | 55
2017-10-04 | 55 | 55
2017-10-04 00:30 | 55 | 54
2017-10-04 01:00 | 55 | 54
2017-10-04 01:30 | 54 | 53
2017-10-04 02:00 | 54 | 53
2017-10-04 02:30 | 54 | 53
2017-10-04 03:00 | 53 | 53
2017-10-04 03:30 | 53 | 52
2017-10-04 04:00 | 54 | 53
2017-10-04 04:30 | 53 | 52
2017-10-04 05:00 | 52 | 52
2017-10-04 05:30 | 56 | 55
2017-10-04 06:00 | 57 | 56
2017-10-04 06:30 | 56 | 55
2017-10-04 07:00 | 55 | 54
2017-10-04 07:30 | 58 | 57
2017-10-04 08:00 | 54 | 52
2017-10-04 08:30 | 62 | 61
2017-10-04 09:00 | 60 | 60
2017-10-04 09:30 | 57 | 57
2017-10-04 10:00 | 56 | 56
2017-10-04 10:30 | 56 | 56
2017-10-04 11:00 | 52 | 51
2017-10-04 11:30 | 57 | 57
2017-10-04 12:00 | 56 | 56
2017-10-04 12:30 | 52 | 52
2017-10-04 13:00 | 50 | 50
2017-10-04 13:30 | 55 | 55
2017-10-04 14:00 | 55 | 55
2017-10-04 14:30 | 48 | 48
2017-10-04 15:00 | 53 | 53
2017-10-04 15:30 | 54 | 54
2017-10-04 16:00 | 55 | 55
2017-10-04 16:30 | 54 | 54
2017-10-04 17:00 | 49 | 48
2017-10-04 17:30 | 60 | 60
2017-10-04 18:00 | 59 | 59
2017-10-04 18:30 | 59 | 59
2017-10-04 19:00 | 58 | 58
2017-10-04 19:30 | 63 | 63
2017-10-04 20:00 | 61 | 61
2017-10-04 20:30 | 60 | 60
2017-10-04 21:00 | 59 | 59
2017-10-04 21:30 | 58 | 58
2017-10-04 22:00 | 58 | 58
2017-10-04 22:30 | 56 | 55
2017-10-04 23:00 | 57 | 57
2017-10-04 23:30 | 54 | 53
2017-10-05 | 53 | 53
2017-10-05 00:30 | 54 | 53
2017-10-05 01:00 | 54 | 53
2017-10-05 01:30 | 53 | 52
2017-10-05 02:00 | 53 | 52
2017-10-05 02:30 | 54 | 53
2017-10-05 03:00 | 54 | 52
2017-10-05 03:30 | 54 | 53
2017-10-05 04:00 | 61 | 59
2017-10-05 04:30 | 59 | 58
2017-10-05 05:00 | 57 | 56
2017-10-05 05:30 | 61 | 60
2017-10-05 06:00 | 62 | 61
2017-10-05 06:30 | 62 | 61
2017-10-05 07:00 | 63 | 63
2017-10-05 07:30 | 66 | 66
2017-10-05 08:00 | 67 | 66
2017-10-05 08:30 | 68 | 68
2017-10-05 09:00 | 72 | 72
2017-10-05 09:30 | 71 | 71
2017-10-05 10:00 | 71 | 71
2017-10-05 10:30 | 71 | 71
2017-10-05 11:00 | 72 | 72
2017-10-05 11:30 | 72 | 72
2017-10-05 12:00 | 72 | 72
2017-10-05 12:30 | 72 | 72
2017-10-05 13:00 | 72 | 72
2017-10-05 13:30 | 73 | 73
2017-10-05 14:00 | 74 | 74
2017-10-05 14:30 | 74 | 74
2017-10-05 15:00 | 72 | 72
2017-10-05 15:30 | 73 | 72
2017-10-05 16:00 | 75 | 75
2017-10-05 16:30 | 76 | 76
2017-10-05 17:00 | 64 | 64
2017-10-05 17:30 | 46 | 45
2017-10-05 18:00 | 49 | 49
2017-10-05 18:30 | 26 | 25
2017-10-05 19:00 | 32 | 31
2017-10-05 19:30 | 72 | 72
2017-10-05 20:00 | 77 | 77
2017-10-05 20:30 | 75 | 75
2017-10-05 21:00 | 75 | 75
2017-10-05 21:30 | 74 | 73
2017-10-05 22:00 | 72 | 71
2017-10-05 22:30 | 71 | 70
2017-10-05 23:00 | 71 | 70
2017-10-05 23:30 | 70 | 69
2017-10-06 | 68 | 68
2017-10-06 00:30 | 68 | 67
2017-10-06 01:00 | 64 | 64
2017-10-06 01:30 | 62 | 61
2017-10-06 02:00 | 62 | 61
2017-10-06 02:30 | 62 | 61
2017-10-06 03:00 | 60 | 59
2017-10-06 03:30 | 60 | 59
2017-10-06 04:00 | 59 | 58
2017-10-06 04:30 | 60 | 59
2017-10-06 05:00 | 60 | 59
2017-10-06 05:30 | 60 | 60
2017-10-06 06:00 | 61 | 60
2017-10-06 06:30 | 61 | 60
2017-10-06 07:00 | 64 | 62
2017-10-06 07:30 | 66 | 65
2017-10-06 08:00 | 67 | 66
2017-10-06 08:30 | 67 | 66
2017-10-06 09:00 | 66 | 65
2017-10-06 09:30 | 66 | 66
2017-10-06 10:00 | 67 | 66
2017-10-06 10:30 | 68 | 67
2017-10-06 11:00 | 61 | 60
2017-10-06 11:30 | 58 | 57
2017-10-06 12:00 | 58 | 57
2017-10-06 12:30 | 59 | 58
2017-10-06 13:00 | 60 | 59
2017-10-06 13:30 | 59 | 58
2017-10-06 14:00 | 57 | 56
2017-10-06 14:30 | 56 | 55
2017-10-06 15:00 | 49 | 46
2017-10-06 15:30 | 43 | 39
2017-10-06 16:00 | 38 | 35
2017-10-06 16:30 | 16 | 14
2017-10-06 17:00 | 35 | 32
2017-10-06 17:30 | 31 | 25
2017-10-06 18:00 | 34 | 30
2017-10-06 18:30 | 28 | 25
2017-10-06 19:00 | 13 | 8
2017-10-06 19:30 | 23 | 20
2017-10-06 20:00 | 31 | 30
2017-10-06 20:30 | 39 | 38
2017-10-06 21:00 | 35 | 33
2017-10-06 21:30 | 32 | 30
2017-10-06 22:00 | 38 | 37
2017-10-06 22:30 | 54 | 54
2017-10-06 23:00 | 59 | 59
2017-10-06 23:30 | 56 | 56
2017-10-07 | 54 | 54
2017-10-07 00:30 | 55 | 55
2017-10-07 01:00 | 53 | 53
2017-10-07 01:30 | 50 | 49
2017-10-07 02:00 | 52 | 51
2017-10-07 02:30 | 55 | 55
2017-10-07 03:00 | 55 | 54
2017-10-07 03:30 | 51 | 51
2017-10-07 04:00 | 49 | 49
2017-10-07 04:30 | 49 | 48
2017-10-07 05:00 | 48 | 48
2017-10-07 05:30 | 52 | 48
2017-10-07 06:00 | 52 | 49
2017-10-07 06:30 | 52 | 49
2017-10-07 07:00 | 52 | 49
2017-10-07 07:30 | 54 | 51
2017-10-07 08:00 | 58 | 54
2017-10-07 08:30 | 59 | 54
2017-10-07 09:00 | 58 | 53
2017-10-07 09:30 | 57 | 54
2017-10-07 10:00 | 56 | 54
2017-10-07 10:30 | 57 | 54
2017-10-07 11:00 | 56 | 54
2017-10-07 11:30 | 56 | 53
2017-10-07 12:00 | 56 | 53
2017-10-07 12:30 | 56 | 54
2017-10-07 13:00 | 58 | 55
2017-10-07 13:30 | 56 | 54
2017-10-07 14:00 | 56 | 54
2017-10-07 14:30 | 56 | 53
2017-10-07 15:00 | 56 | 53
2017-10-07 15:30 | 57 | 54
2017-10-07 16:00 | 57 | 54
2017-10-07 16:30 | 57 | 55
2017-10-07 17:00 | 55 | 53
2017-10-07 17:30 | 56 | 54
2017-10-07 18:00 | 57 | 54
2017-10-07 18:30 | 57 | 55
2017-10-07 19:00 | 57 | 55
2017-10-07 19:30 | 57 | 55
2017-10-07 20:00 | 58 | 56
2017-10-07 20:30 | 56 | 54
2017-10-07 21:00 | 56 | 54
2017-10-07 21:30 | 56 | 55
2017-10-07 22:00 | 55 | 53
2017-10-07 22:30 | 54 | 53
2017-10-07 23:00 | 52 | 51
2017-10-07 23:30 | 53 | 52
2017-10-08 | 51 | 50
2017-10-08 00:30 | 51 | 50
2017-10-08 01:00 | 50 | 50
2017-10-08 01:30 | 49 | 49
2017-10-08 02:00 | 50 | 50
2017-10-08 02:30 | 50 | 50
2017-10-08 03:00 | 52 | 51
2017-10-08 03:30 | 50 | 49
2017-10-08 04:00 | 52 | 52
2017-10-08 04:30 | 50 | 50
2017-10-08 05:00 | 49 | 48
2017-10-08 05:30 | 49 | 48
2017-10-08 06:00 | 49 | 48
2017-10-08 06:30 | 49 | 48
2017-10-08 07:00 | 48 | 47
2017-10-08 07:30 | 50 | 48
2017-10-08 08:00 | 51 | 49
2017-10-08 08:30 | 51 | 50
2017-10-08 09:00 | 53 | 52
2017-10-08 09:30 | 51 | 50
2017-10-08 10:00 | 51 | 50
2017-10-08 10:30 | 52 | 51
2017-10-08 11:00 | 53 | 53
2017-10-08 11:30 | 54 | 54
2017-10-08 12:00 | 54 | 53
2017-10-08 12:30 | 53 | 52
2017-10-08 13:00 | 55 | 54
2017-10-08 13:30 | 54 | 53
2017-10-08 14:00 | 54 | 52
2017-10-08 14:30 | 54 | 52
2017-10-08 15:00 | 53 | 51
2017-10-08 15:30 | 55 | 53
2017-10-08 16:00 | 56 | 54
2017-10-08 16:30 | 56 | 54
2017-10-08 17:00 | 54 | 52
2017-10-08 17:30 | 32 | 26
2017-10-08 18:00 | 22 | 9
2017-10-08 18:30 | 23 | 11
2017-10-08 19:00 | 19 | 11
2017-10-08 19:30 | 37 | 31
2017-10-08 20:00 | 42 | 38
2017-10-08 20:30 | 47 | 43
2017-10-08 21:00 | 55 | 53
2017-10-08 21:30 | 54 | 53
2017-10-08 22:00 | 53 | 52
2017-10-08 22:30 | 53 | 52
2017-10-08 23:00 | 53 | 53
2017-10-08 23:30 | 54 | 53
2017-10-09 | 52 | 51
2017-10-09 00:30 | 51 | 50
2017-10-09 01:00 | 50 | 50
2017-10-09 01:30 | 49 | 49
2017-10-09 02:00 | 49 | 48
2017-10-09 02:30 | 50 | 48
2017-10-09 03:00 | 49 | 48
2017-10-09 03:30 | 49 | 47
2017-10-09 04:00 | 50 | 49
2017-10-09 04:30 | 49 | 48
2017-10-09 05:00 | 48 | 47
2017-10-09 05:30 | 50 | 48
2017-10-09 06:00 | 50 | 49
2017-10-09 06:30 | 50 | 48
2017-10-09 07:00 | 52 | 50
2017-10-09 07:30 | 57 | 53
2017-10-09 08:00 | 55 | 55
2017-10-09 08:30 | 58 | 57
2017-10-09 09:00 | 62 | 62
2017-10-09 09:30 | 60 | 59
2017-10-09 10:00 | 59 | 58
2017-10-09 10:30 | 59 | 59
2017-10-09 11:00 | 59 | 59
2017-10-09 11:30 | 59 | 59
2017-10-09 12:00 | 59 | 58
2017-10-09 12:30 | 59 | 59
2017-10-09 13:00 | 61 | 61
2017-10-09 13:30 | 60 | 59
2017-10-09 14:00 | 64 | 63
2017-10-09 14:30 | 64 | 63
2017-10-09 15:00 | 63 | 62
2017-10-09 15:30 | 61 | 60
2017-10-09 16:00 | 61 | 60
2017-10-09 16:30 | 61 | 61
2017-10-09 17:00 | 38 | 38
2017-10-09 17:30 | 29 | 29
2017-10-09 18:00 | 28 | 28
2017-10-09 18:30 | 22 | 22
2017-10-09 19:00 | 14 | 8
2017-10-09 19:30 | 22 | 21
2017-10-09 20:00 | 28 | 28
2017-10-09 20:30 | 29 | 29
2017-10-09 21:00 | 53 | 52
2017-10-09 21:30 | 59 | 58
2017-10-09 22:00 | 59 | 57
2017-10-09 22:30 | 57 | 55
2017-10-09 23:00 | 53 | 53
2017-10-09 23:30 | 54 | 53
2017-10-10 | 55 | 54
2017-10-10 00:30 | 54 | 53
2017-10-10 01:00 | 54 | 52
2017-10-10 01:30 | 54 | 52
2017-10-10 02:00 | 52 | 51
2017-10-10 02:30 | 51 | 51
2017-10-10 03:00 | 53 | 51
2017-10-10 03:30 | 53 | 52
2017-10-10 04:00 | 52 | 50
2017-10-10 04:30 | 51 | 50
2017-10-10 05:00 | 52 | 51
2017-10-10 05:30 | 52 | 50
2017-10-10 06:00 | 52 | 51
2017-10-10 06:30 | 56 | 54
2017-10-10 07:00 | 58 | 57
2017-10-10 07:30 | 57 | 56
2017-10-10 08:00 | 57 | 57
2017-10-10 08:30 | 58 | 58
2017-10-10 09:00 | 57 | 57
2017-10-10 09:30 | 58 | 57
2017-10-10 10:00 | 58 | 58
2017-10-10 10:30 | 59 | 59
2017-10-10 11:00 | 57 | 56
2017-10-10 11:30 | 53 | 52
2017-10-10 12:00 | 59 | 57
2017-10-10 12:30 | 60 | 58
2017-10-10 13:00 | 47 | 47
2017-10-10 13:30 | 60 | 58
2017-10-10 14:00 | 61 | 59
2017-10-10 14:30 | 61 | 58
2017-10-10 15:00 | 61 | 58
2017-10-10 15:30 | 61 | 59
2017-10-10 16:00 | 38 | 32
2017-10-10 16:30 | 37 | 30
2017-10-10 17:00 | 10 | 2
2017-10-10 17:30 | 12 | 9
2017-10-10 18:00 | 25 | 22
2017-10-10 18:30 | 36 | 31
2017-10-10 19:00 | 23 | 20
2017-10-10 19:30 | 25 | 21
2017-10-10 20:00 | 37 | 32
2017-10-10 20:30 | 37 | 33
2017-10-10 21:00 | 58 | 57
2017-10-10 21:30 | 63 | 62
2017-10-10 22:00 | 62 | 61
2017-10-10 22:30 | 61 | 60
2017-10-10 23:00 | 54 | 53
2017-10-10 23:30 | 53 | 53
2017-10-11 | 53 | 53
2017-10-11 00:30 | 53 | 53
2017-10-11 01:00 | 53 | 53
2017-10-11 01:30 | 53 | 53
2017-10-11 02:00 | 53 | 53
2017-10-11 02:30 | 53 | 52
2017-10-11 03:00 | 52 | 52
2017-10-11 03:30 | 51 | 51
2017-10-11 04:00 | 52 | 52
2017-10-11 04:30 | 51 | 51
2017-10-11 05:00 | 52 | 52
2017-10-11 05:30 | 52 | 52
2017-10-11 06:00 | 52 | 52
2017-10-11 06:30 | 54 | 53
2017-10-11 07:00 | 39 | 39
2017-10-11 07:30 | 29 | 24
2017-10-11 08:00 | 32 | 29
2017-10-11 08:30 | 51 | 51
2017-10-11 09:00 | 57 | 56
2017-10-11 09:30 | 58 | 57
2017-10-11 10:00 | 58 | 57
2017-10-11 10:30 | 58 | 57
2017-10-11 11:00 | 39 | 39
2017-10-11 11:30 | 37 | 37
2017-10-11 12:00 | 57 | 56
2017-10-11 12:30 | 60 | 58
2017-10-11 13:00 | 59 | 58
2017-10-11 13:30 | 60 | 59
2017-10-11 14:00 | 60 | 59
2017-10-11 14:30 | 54 | 52
2017-10-11 15:00 | 59 | 58
2017-10-11 15:30 | 58 | 57
2017-10-11 16:00 | 52 | 50
2017-10-11 16:30 | 56 | 56
2017-10-11 17:00 | 36 | 36
2017-10-11 17:30 | 26 | 24
2017-10-11 18:00 | 28 | 23
2017-10-11 18:30 | 32 | 29
2017-10-11 19:00 | 33 | 30
2017-10-11 19:30 | 45 | 45
2017-10-11 20:00 | 46 | 46
2017-10-11 20:30 | 46 | 46
2017-10-11 21:00 | 56 | 55
2017-10-11 21:30 | 60 | 58
2017-10-11 22:00 | 59 | 57
2017-10-11 22:30 | 57 | 55
2017-10-11 23:00 | 56 | 54
2017-10-11 23:30 | 56 | 54
2017-10-12 | 56 | 54
2017-10-12 00:30 | 56 | 53
2017-10-12 01:00 | 54 | 53
2017-10-12 01:30 | 53 | 52
2017-10-12 02:00 | 52 | 51
2017-10-12 02:30 | 52 | 51
2017-10-12 03:00 | 51 | 50
2017-10-12 03:30 | 51 | 50
2017-10-12 04:00 | 55 | 54
2017-10-12 04:30 | 56 | 55
2017-10-12 05:00 | 55 | 54
2017-10-12 05:30 | 54 | 53
2017-10-12 06:00 | 54 | 53
2017-10-12 06:30 | 52 | 51
2017-10-12 07:00 | 38 | 30
2017-10-12 07:30 | 34 | 22
2017-10-12 08:00 | 34 | 21
2017-10-12 08:30 | 33 | 22
2017-10-12 09:00 | 36 | 29
2017-10-12 09:30 | 34 | 28
2017-10-12 10:00 | 36 | 32
2017-10-12 10:30 | 30 | 20
2017-10-12 11:00 | 30 | 20
2017-10-12 11:30 | 34 | 29
2017-10-12 12:00 | 34 | 28
2017-10-12 12:30 | 41 | 38
2017-10-12 13:00 | 41 | 38
2017-10-12 13:30 | 40 | 37
2017-10-12 14:00 | 35 | 27
2017-10-12 14:30 | 33 | 24
2017-10-12 15:00 | 35 | 31
2017-10-12 15:30 | 42 | 41
2017-10-12 16:00 | 39 | 37
2017-10-12 16:30 | 36 | 31
2017-10-12 17:00 | 39 | 38
2017-10-12 17:30 | 33 | 32
2017-10-12 18:00 | 31 | 31
2017-10-12 18:30 | 36 | 36
2017-10-12 19:00 | 29 | 28
2017-10-12 19:30 | 33 | 32
2017-10-12 20:00 | 47 | 47
2017-10-12 20:30 | 56 | 56
2017-10-12 21:00 | 58 | 58
2017-10-12 21:30 | 55 | 55
2017-10-12 22:00 | 54 | 53
2017-10-12 22:30 | 50 | 49
2017-10-12 23:00 | 53 | 52
2017-10-12 23:30 | 53 | 52
2017-10-13 | 53 | 52
2017-10-13 00:30 | 53 | 52
2017-10-13 01:00 | 54 | 52
2017-10-13 01:30 | 53 | 51
2017-10-13 02:00 | 53 | 52
2017-10-13 02:30 | 53 | 51
2017-10-13 03:00 | 52 | 51
2017-10-13 03:30 | 53 | 52
2017-10-13 04:00 | 54 | 52
2017-10-13 04:30 | 54 | 52
2017-10-13 05:00 | 53 | 52
2017-10-13 05:30 | 55 | 53
2017-10-13 06:00 | 55 | 54
2017-10-13 06:30 | 54 | 53
2017-10-13 07:00 | 53 | 53
2017-10-13 07:30 | 58 | 58
2017-10-13 08:00 | 60 | 60
2017-10-13 08:30 | 60 | 60
2017-10-13 09:00 | 60 | 60
2017-10-13 09:30 | 60 | 60
2017-10-13 10:00 | 57 | 57
2017-10-13 10:30 | 58 | 58
2017-10-13 11:00 | 59 | 59
2017-10-13 11:30 | 58 | 58
2017-10-13 12:00 | 56 | 56
2017-10-13 12:30 | 56 | 56
2017-10-13 13:00 | 59 | 59
2017-10-13 13:30 | 61 | 61
2017-10-13 14:00 | 59 | 59
2017-10-13 14:30 | 54 | 54
2017-10-13 15:00 | 55 | 55
2017-10-13 15:30 | 55 | 55
2017-10-13 16:00 | 43 | 42
2017-10-13 16:30 | 43 | 43
2017-10-13 17:00 | 43 | 42
2017-10-13 17:30 | 44 | 44
2017-10-13 18:00 | 44 | 44
2017-10-13 18:30 | 45 | 45
2017-10-13 19:00 | 27 | 27
2017-10-13 19:30 | 34 | 34
2017-10-13 20:00 | 40 | 40
2017-10-13 20:30 | 40 | 40
2017-10-13 21:00 | 52 | 52
2017-10-13 21:30 | 54 | 54
2017-10-13 22:00 | 54 | 54
2017-10-13 22:30 | 53 | 53
2017-10-13 23:00 | 54 | 53
2017-10-13 23:30 | 52 | 51
2017-10-14 | 50 | 50
2017-10-14 00:30 | 51 | 50
2017-10-14 01:00 | 52 | 51
2017-10-14 01:30 | 51 | 50
2017-10-14 02:00 | 53 | 52
2017-10-14 02:30 | 54 | 53
2017-10-14 03:00 | 52 | 50
2017-10-14 03:30 | 51 | 49
2017-10-14 04:00 | 50 | 49
2017-10-14 04:30 | 51 | 50
2017-10-14 05:00 | 51 | 49
2017-10-14 05:30 | 50 | 49
2017-10-14 06:00 | 50 | 48
2017-10-14 06:30 | 50 | 49
2017-10-14 07:00 | 51 | 50
2017-10-14 07:30 | 51 | 50
2017-10-14 08:00 | 53 | 52
2017-10-14 08:30 | 54 | 53
2017-10-14 09:00 | 55 | 54
2017-10-14 09:30 | 54 | 53
2017-10-14 10:00 | 53 | 52
2017-10-14 10:30 | 52 | 51
2017-10-14 11:00 | 52 | 51
2017-10-14 11:30 | 52 | 51
2017-10-14 12:00 | 50 | 50
2017-10-14 12:30 | 50 | 50
2017-10-14 13:00 | 52 | 51
2017-10-14 13:30 | 51 | 51
2017-10-14 14:00 | 50 | 50
2017-10-14 14:30 | 52 | 52
2017-10-14 15:00 | 52 | 52
2017-10-14 15:30 | 54 | 53
2017-10-14 16:00 | 55 | 54
2017-10-14 16:30 | 56 | 54
2017-10-14 17:00 | 56 | 55
2017-10-14 17:30 | 57 | 56
2017-10-14 18:00 | 58 | 57
2017-10-14 18:30 | 57 | 56
2017-10-14 19:00 | 57 | 56
2017-10-14 19:30 | 58 | 58
2017-10-14 20:00 | 56 | 55
2017-10-14 20:30 | 55 | 54
2017-10-14 21:00 | 58 | 57
2017-10-14 21:30 | 59 | 57
2017-10-14 22:00 | 58 | 56
2017-10-14 22:30 | 57 | 55
2017-10-14 23:00 | 57 | 54
2017-10-14 23:30 | 55 | 53
2017-10-15 | 56 | 53
2017-10-15 00:30 | 54 | 52
2017-10-15 01:00 | 53 | 52
2017-10-15 01:30 | 54 | 53
2017-10-15 02:00 | 53 | 52
2017-10-15 02:30 | 52 | 51
2017-10-15 03:00 | 52 | 50
2017-10-15 03:30 | 52 | 50
2017-10-15 04:00 | 52 | 51
2017-10-15 04:30 | 52 | 51
2017-10-15 05:00 | 51 | 51
2017-10-15 05:30 | 51 | 51
2017-10-15 06:00 | 51 | 50
2017-10-15 06:30 | 50 | 49
2017-10-15 07:00 | 50 | 50
2017-10-15 07:30 | 51 | 50
2017-10-15 08:00 | 52 | 51
2017-10-15 08:30 | 51 | 51
2017-10-15 09:00 | 53 | 52
2017-10-15 09:30 | 54 | 53
2017-10-15 10:00 | 51 | 50
2017-10-15 10:30 | 52 | 52
2017-10-15 11:00 | 53 | 53
2017-10-15 11:30 | 53 | 52
2017-10-15 12:00 | 52 | 52
2017-10-15 12:30 | 53 | 53
2017-10-15 13:00 | 53 | 52
2017-10-15 13:30 | 52 | 52
2017-10-15 14:00 | 58 | 53
2017-10-15 14:30 | 61 | 54
2017-10-15 15:00 | 61 | 54
2017-10-15 15:30 | 60 | 53
2017-10-15 16:00 | 61 | 54
2017-10-15 16:30 | 61 | 55
2017-10-15 17:00 | 59 | 51
2017-10-15 17:30 | 60 | 53
2017-10-15 18:00 | 61 | 53
2017-10-15 18:30 | 62 | 55
2017-10-15 19:00 | 61 | 53
2017-10-15 19:30 | 62 | 55
2017-10-15 20:00 | 62 | 55
2017-10-15 20:30 | 61 | 54
2017-10-15 21:00 | 64 | 54
2017-10-15 21:30 | 66 | 54
2017-10-15 22:00 | 65 | 54
2017-10-15 22:30 | 54 | 52
2017-10-15 23:00 | 54 | 51
2017-10-15 23:30 | 54 | 51
2017-10-16 | 54 | 51
2017-10-16 00:30 | 54 | 50
2017-10-16 01:00 | 54 | 51
2017-10-16 01:30 | 54 | 52
2017-10-16 02:00 | 51 | 50
2017-10-16 02:30 | 52 | 51
2017-10-16 03:00 | 53 | 51
2017-10-16 03:30 | 52 | 51
2017-10-16 04:00 | 53 | 52
2017-10-16 04:30 | 54 | 53
2017-10-16 05:00 | 54 | 53
2017-10-16 05:30 | 52 | 51
2017-10-16 06:00 | 51 | 50
2017-10-16 06:30 | 52 | 51
2017-10-16 07:00 | 51 | 51
2017-10-16 07:30 | 54 | 54
2017-10-16 08:00 | 64 | 63
2017-10-16 08:30 | 63 | 62
2017-10-16 09:00 | 60 | 59
2017-10-16 09:30 | 59 | 58
2017-10-16 10:00 | 59 | 58
2017-10-16 10:30 | 59 | 57
2017-10-16 11:00 | 60 | 59
2017-10-16 11:30 | 62 | 60
2017-10-16 12:00 | 62 | 60
2017-10-16 12:30 | 62 | 60
2017-10-16 13:00 | 62 | 61
2017-10-16 13:30 | 64 | 62
2017-10-16 14:00 | 67 | 65
2017-10-16 14:30 | 68 | 66
2017-10-16 15:00 | 67 | 65
2017-10-16 15:30 | 68 | 65
2017-10-16 16:00 | 68 | 65
2017-10-16 16:30 | 64 | 61
2017-10-16 17:00 | 63 | 60
2017-10-16 17:30 | 62 | 59
2017-10-16 18:00 | 56 | 53
2017-10-16 18:30 | 58 | 54
2017-10-16 19:00 | 57 | 55
2017-10-16 19:30 | 52 | 52
2017-10-16 20:00 | 52 | 51
2017-10-16 20:30 | 52 | 51
2017-10-16 21:00 | 52 | 50
2017-10-16 21:30 | 55 | 53
2017-10-16 22:00 | 54 | 53
2017-10-16 22:30 | 52 | 51
2017-10-16 23:00 | 53 | 51
2017-10-16 23:30 | 53 | 51
2017-10-17 | 53 | 51
2017-10-17 00:30 | 55 | 53
2017-10-17 01:00 | 54 | 53
2017-10-17 01:30 | 54 | 52
2017-10-17 02:00 | 51 | 49
2017-10-17 02:30 | 51 | 50
2017-10-17 03:00 | 50 | 48
2017-10-17 03:30 | 49 | 47
2017-10-17 04:00 | 49 | 47
2017-10-17 04:30 | 50 | 49
2017-10-17 05:00 | 52 | 50
2017-10-17 05:30 | 53 | 51
2017-10-17 06:00 | 55 | 53
2017-10-17 06:30 | 55 | 53
2017-10-17 07:00 | 55 | 53
2017-10-17 07:30 | 55 | 54
2017-10-17 08:00 | 55 | 55
2017-10-17 08:30 | 58 | 58
2017-10-17 09:00 | 64 | 64
2017-10-17 09:30 | 62 | 61
2017-10-17 10:00 | 62 | 61
2017-10-17 10:30 | 61 | 60
2017-10-17 11:00 | 63 | 63
2017-10-17 11:30 | 64 | 64
2017-10-17 12:00 | 64 | 64
2017-10-17 12:30 | 64 | 64
2017-10-17 13:00 | 63 | 63
2017-10-17 13:30 | 63 | 63
2017-10-17 14:00 | 64 | 63
2017-10-17 14:30 | 61 | 60
2017-10-17 15:00 | 61 | 60
2017-10-17 15:30 | 62 | 62
2017-10-17 16:00 | 63 | 62
2017-10-17 16:30 | 62 | 62
2017-10-17 17:00 | 62 | 61
2017-10-17 17:30 | 62 | 61
2017-10-17 18:00 | 62 | 61
2017-10-17 18:30 | 64 | 63
2017-10-17 19:00 | 65 | 64
2017-10-17 19:30 | 65 | 64
2017-10-17 20:00 | 65 | 64
2017-10-17 20:30 | 64 | 62
2017-10-17 21:00 | 61 | 59
2017-10-17 21:30 | 57 | 57
2017-10-17 22:00 | 57 | 56
2017-10-17 22:30 | 56 | 55
2017-10-17 23:00 | 56 | 55
2017-10-17 23:30 | 56 | 54
2017-10-18 | 56 | 54
2017-10-18 00:30 | 57 | 55
2017-10-18 01:00 | 57 | 56
2017-10-18 01:30 | 59 | 56
2017-10-18 02:00 | 58 | 55
2017-10-18 02:30 | 58 | 56
2017-10-18 03:00 | 58 | 56
2017-10-18 03:30 | 58 | 56
2017-10-18 04:00 | 58 | 56
2017-10-18 04:30 | 58 | 56
2017-10-18 05:00 | 58 | 55
2017-10-18 05:30 | 58 | 56
2017-10-18 06:00 | 59 | 57
2017-10-18 06:30 | 58 | 57
2017-10-18 07:00 | 56 | 55
2017-10-18 07:30 | 56 | 55
2017-10-18 08:00 | 58 | 57
2017-10-18 08:30 | 59 | 57
2017-10-18 09:00 | 62 | 60
2017-10-18 09:30 | 63 | 61
2017-10-18 10:00 | 63 | 61
2017-10-18 10:30 | 64 | 62
2017-10-18 11:00 | 63 | 61
2017-10-18 11:30 | 60 | 58
2017-10-18 12:00 | 59 | 57
2017-10-18 12:30 | 62 | 60
2017-10-18 13:00 | 62 | 61
2017-10-18 13:30 | 62 | 60
2017-10-18 14:00 | 61 | 59
2017-10-18 14:30 | 64 | 62
2017-10-18 15:00 | 64 | 62
2017-10-18 15:30 | 60 | 59
2017-10-18 16:00 | 59 | 59
2017-10-18 16:30 | 62 | 61
2017-10-18 17:00 | 65 | 64
2017-10-18 17:30 | 66 | 65
2017-10-18 18:00 | 67 | 66
2017-10-18 18:30 | 69 | 69
2017-10-18 19:00 | 71 | 70
2017-10-18 19:30 | 72 | 72
2017-10-18 20:00 | 70 | 70
2017-10-18 20:30 | 68 | 67
2017-10-18 21:00 | 67 | 67
2017-10-18 21:30 | 67 | 67
2017-10-18 22:00 | 66 | 65
2017-10-18 22:30 | 66 | 65
2017-10-18 23:00 | 66 | 65
2017-10-18 23:30 | 65 | 64
2017-10-19 | 65 | 64
2017-10-19 00:30 | 65 | 64
2017-10-19 01:00 | 65 | 63
2017-10-19 01:30 | 64 | 63
2017-10-19 02:00 | 64 | 63
2017-10-19 02:30 | 66 | 65
2017-10-19 03:00 | 65 | 64
2017-10-19 03:30 | 67 | 66
2017-10-19 04:00 | 68 | 67
2017-10-19 04:30 | 69 | 67
2017-10-19 05:00 | 69 | 67
2017-10-19 05:30 | 70 | 68
2017-10-19 06:00 | 69 | 68
2017-10-19 06:30 | 70 | 69
2017-10-19 07:00 | 71 | 70
2017-10-19 07:30 | 73 | 72
2017-10-19 08:00 | 74 | 73
2017-10-19 08:30 | 75 | 75
2017-10-19 09:00 | 78 | 77
2017-10-19 09:30 | 78 | 77
2017-10-19 10:00 | 79 | 79
2017-10-19 10:30 | 82 | 81
2017-10-19 11:00 | 81 | 80
2017-10-19 11:30 | 79 | 79
2017-10-19 12:00 | 78 | 77
2017-10-19 12:30 | 77 | 77
2017-10-19 13:00 | 78 | 77
2017-10-19 13:30 | 77 | 76
2017-10-19 14:00 | 77 | 77
2017-10-19 14:30 | 77 | 77
2017-10-19 15:00 | 77 | 75
2017-10-19 15:30 | 77 | 75
2017-10-19 16:00 | 77 | 75
2017-10-19 16:30 | 78 | 75
2017-10-19 17:00 | 77 | 75
2017-10-19 17:30 | 77 | 76
2017-10-19 18:00 | 77 | 75
2017-10-19 18:30 | 75 | 73
2017-10-19 19:00 | 78 | 76
2017-10-19 19:30 | 78 | 76
2017-10-19 20:00 | 73 | 72
2017-10-19 20:30 | 68 | 67
2017-10-19 21:00 | 68 | 67
2017-10-19 21:30 | 68 | 67
2017-10-19 22:00 | 68 | 66
2017-10-19 22:30 | 67 | 65
2017-10-19 23:00 | 66 | 64
2017-10-19 23:30 | 67 | 65
2017-10-20 | 67 | 65
2017-10-20 00:30 | 64 | 64
2017-10-20 01:00 | 64 | 64
2017-10-20 01:30 | 64 | 63
2017-10-20 02:00 | 64 | 63
2017-10-20 02:30 | 63 | 63
2017-10-20 03:00 | 63 | 63
2017-10-20 03:30 | 63 | 62
2017-10-20 04:00 | 63 | 63
2017-10-20 04:30 | 64 | 63
2017-10-20 05:00 | 64 | 63
2017-10-20 05:30 | 64 | 63
2017-10-20 06:00 | 63 | 62
2017-10-20 06:30 | 64 | 63
2017-10-20 07:00 | 64 | 64
2017-10-20 07:30 | 66 | 65
2017-10-20 08:00 | 75 | 67
2017-10-20 08:30 | 74 | 67
2017-10-20 09:00 | 77 | 70
2017-10-20 09:30 | 79 | 72
2017-10-20 10:00 | 79 | 71
2017-10-20 10:30 | 81 | 72
2017-10-20 11:00 | 77 | 72
2017-10-20 11:30 | 74 | 72
2017-10-20 12:00 | 74 | 71
2017-10-20 12:30 | 74 | 72
2017-10-20 13:00 | 72 | 71
2017-10-20 13:30 | 70 | 69
2017-10-20 14:00 | 72 | 70
2017-10-20 14:30 | 78 | 75
2017-10-20 15:00 | 77 | 75
2017-10-20 15:30 | 75 | 73
2017-10-20 16:00 | 73 | 70
2017-10-20 16:30 | 70 | 68
2017-10-20 17:00 | 67 | 65
2017-10-20 17:30 | 66 | 64
2017-10-20 18:00 | 67 | 64
2017-10-20 18:30 | 67 | 63
2017-10-20 19:00 | 67 | 64
2017-10-20 19:30 | 68 | 64
2017-10-20 20:00 | 67 | 64
2017-10-20 20:30 | 66 | 63
2017-10-20 21:00 | 66 | 62
2017-10-20 21:30 | 66 | 62
2017-10-20 22:00 | 65 | 61
2017-10-20 22:30 | 65 | 62
2017-10-20 23:00 | 63 | 60
2017-10-20 23:30 | 61 | 60
2017-10-21 | 60 | 60
2017-10-21 00:30 | 61 | 60
2017-10-21 01:00 | 61 | 60
2017-10-21 01:30 | 61 | 60
2017-10-21 02:00 | 60 | 59
2017-10-21 02:30 | 60 | 59
2017-10-21 03:00 | 60 | 59
2017-10-21 03:30 | 61 | 60
2017-10-21 04:00 | 60 | 59
2017-10-21 04:30 | 60 | 59
2017-10-21 05:00 | 60 | 59
2017-10-21 05:30 | 59 | 58
2017-10-21 06:00 | 59 | 57
2017-10-21 06:30 | 59 | 58
2017-10-21 07:00 | 59 | 58
2017-10-21 07:30 | 60 | 59
2017-10-21 08:00 | 60 | 60
2017-10-21 08:30 | 59 | 59
2017-10-21 09:00 | 59 | 59
2017-10-21 09:30 | 59 | 59
2017-10-21 10:00 | 59 | 59
2017-10-21 10:30 | 61 | 60
2017-10-21 11:00 | 60 | 60
2017-10-21 11:30 | 59 | 59
2017-10-21 12:00 | 59 | 59
2017-10-21 12:30 | 60 | 60
2017-10-21 13:00 | 60 | 59
2017-10-21 13:30 | 60 | 59
2017-10-21 14:00 | 60 | 60
2017-10-21 14:30 | 60 | 60
2017-10-21 15:00 | 61 | 60
2017-10-21 15:30 | 61 | 61
2017-10-21 16:00 | 59 | 59
2017-10-21 16:30 | 59 | 59
2017-10-21 17:00 | 60 | 59
2017-10-21 17:30 | 60 | 60
2017-10-21 18:00 | 59 | 59
2017-10-21 18:30 | 60 | 59
2017-10-21 19:00 | 60 | 60
2017-10-21 19:30 | 60 | 60
2017-10-21 20:00 | 61 | 60
2017-10-21 20:30 | 60 | 60
2017-10-21 21:00 | 60 | 59
2017-10-21 21:30 | 58 | 58
2017-10-21 22:00 | 58 | 57
2017-10-21 22:30 | 58 | 57
2017-10-21 23:00 | 57 | 57
2017-10-21 23:30 | 56 | 56
2017-10-22 | 56 | 56
2017-10-22 00:30 | 56 | 56
2017-10-22 01:00 | 55 | 55
2017-10-22 01:30 | 55 | 55
2017-10-22 02:00 | 54 | 54
2017-10-22 02:30 | 54 | 53
2017-10-22 03:00 | 54 | 54
2017-10-22 03:30 | 54 | 53
2017-10-22 04:00 | 54 | 53
2017-10-22 04:30 | 54 | 53
2017-10-22 05:00 | 53 | 52
2017-10-22 05:30 | 53 | 52
2017-10-22 06:00 | 53 | 52
2017-10-22 06:30 | 53 | 52
2017-10-22 07:00 | 54 | 54
2017-10-22 07:30 | 55 | 55
2017-10-22 08:00 | 56 | 56
2017-10-22 08:30 | 56 | 56
2017-10-22 09:00 | 54 | 54
2017-10-22 09:30 | 56 | 55
2017-10-22 10:00 | 55 | 55
2017-10-22 10:30 | 56 | 56
2017-10-22 11:00 | 57 | 56
2017-10-22 11:30 | 58 | 57
2017-10-22 12:00 | 58 | 57
2017-10-22 12:30 | 58 | 57
2017-10-22 13:00 | 58 | 57
2017-10-22 13:30 | 57 | 57
2017-10-22 14:00 | 57 | 56
2017-10-22 14:30 | 56 | 55
2017-10-22 15:00 | 55 | 55
2017-10-22 15:30 | 55 | 55
2017-10-22 16:00 | 56 | 56
2017-10-22 16:30 | 57 | 56
2017-10-22 17:00 | 58 | 57
2017-10-22 17:30 | 58 | 58
2017-10-22 18:00 | 59 | 59
2017-10-22 18:30 | 60 | 59
2017-10-22 19:00 | 61 | 60
2017-10-22 19:30 | 61 | 60
2017-10-22 20:00 | 61 | 60
2017-10-22 20:30 | 60 | 60
2017-10-22 21:00 | 60 | 60
2017-10-22 21:30 | 59 | 59
2017-10-22 22:00 | 60 | 60
2017-10-22 22:30 | 60 | 59
2017-10-22 23:00 | 60 | 60
2017-10-22 23:30 | 60 | 60
2017-10-23 | 59 | 59
2017-10-23 00:30 | 57 | 57
2017-10-23 01:00 | 56 | 56
2017-10-23 01:30 | 56 | 55
2017-10-23 02:00 | 56 | 55
2017-10-23 02:30 | 56 | 55
2017-10-23 03:00 | 56 | 55
2017-10-23 03:30 | 55 | 54
2017-10-23 04:00 | 56 | 55
2017-10-23 04:30 | 56 | 55
2017-10-23 05:00 | 56 | 55
2017-10-23 05:30 | 57 | 56
2017-10-23 06:00 | 57 | 56
2017-10-23 06:30 | 57 | 56
2017-10-23 07:00 | 57 | 56
2017-10-23 07:30 | 57 | 57
2017-10-23 08:00 | 57 | 57
2017-10-23 08:30 | 53 | 53
2017-10-23 09:00 | 53 | 53
2017-10-23 09:30 | 53 | 53
2017-10-23 10:00 | 55 | 54
2017-10-23 10:30 | 54 | 54
2017-10-23 11:00 | 55 | 55
2017-10-23 11:30 | 55 | 55
2017-10-23 12:00 | 55 | 55
2017-10-23 12:30 | 56 | 56
2017-10-23 13:00 | 55 | 55
2017-10-23 13:30 | 54 | 54
2017-10-23 14:00 | 54 | 54
2017-10-23 14:30 | 54 | 54
2017-10-23 15:00 | 57 | 57
2017-10-23 15:30 | 58 | 58
2017-10-23 16:00 | 58 | 58
2017-10-23 16:30 | 59 | 59
2017-10-23 17:00 | 60 | 60
2017-10-23 17:30 | 61 | 61
2017-10-23 18:00 | 62 | 62
2017-10-23 18:30 | 63 | 62
2017-10-23 19:00 | 63 | 63
2017-10-23 19:30 | 63 | 63
2017-10-23 20:00 | 64 | 64
2017-10-23 20:30 | 63 | 63
2017-10-23 21:00 | 61 | 60
2017-10-23 21:30 | 59 | 59
2017-10-23 22:00 | 59 | 59
2017-10-23 22:30 | 59 | 58
2017-10-23 23:00 | 58 | 57
2017-10-23 23:30 | 58 | 57
2017-10-24 | 58 | 57
2017-10-24 00:30 | 58 | 57
2017-10-24 01:00 | 57 | 57
2017-10-24 01:30 | 58 | 57
2017-10-24 02:00 | 57 | 56
2017-10-24 02:30 | 58 | 57
2017-10-24 03:00 | 58 | 56
2017-10-24 03:30 | 57 | 56
2017-10-24 04:00 | 57 | 56
2017-10-24 04:30 | 58 | 57
2017-10-24 05:00 | 59 | 58
2017-10-24 05:30 | 60 | 58
2017-10-24 06:00 | 64 | 63
2017-10-24 06:30 | 67 | 65
2017-10-24 07:00 | 67 | 65
2017-10-24 07:30 | 65 | 65
2017-10-24 08:00 | 66 | 65
2017-10-24 08:30 | 66 | 66
2017-10-24 09:00 | 65 | 65
2017-10-24 09:30 | 65 | 65
2017-10-24 10:00 | 61 | 61
2017-10-24 10:30 | 60 | 60
2017-10-24 11:00 | 58 | 58
2017-10-24 11:30 | 58 | 58
2017-10-24 12:00 | 58 | 58
2017-10-24 12:30 | 58 | 58
2017-10-24 13:00 | 58 | 58
2017-10-24 13:30 | 58 | 58
2017-10-24 14:00 | 58 | 58
2017-10-24 14:30 | 58 | 58
2017-10-24 15:00 | 58 | 58
2017-10-24 15:30 | 58 | 58
2017-10-24 16:00 | 59 | 59
2017-10-24 16:30 | 60 | 60
2017-10-24 17:00 | 60 | 60
2017-10-24 17:30 | 60 | 60
2017-10-24 18:00 | 60 | 60
2017-10-24 18:30 | 61 | 61
2017-10-24 19:00 | 62 | 62
2017-10-24 19:30 | 63 | 63
2017-10-24 20:00 | 63 | 62
2017-10-24 20:30 | 63 | 62
2017-10-24 21:00 | 62 | 62
2017-10-24 21:30 | 62 | 62
2017-10-24 22:00 | 62 | 61
2017-10-24 22:30 | 60 | 59
2017-10-24 23:00 | 58 | 58
2017-10-24 23:30 | 58 | 57
2017-10-25 | 57 | 56
2017-10-25 00:30 | 57 | 56
2017-10-25 01:00 | 58 | 57
2017-10-25 01:30 | 57 | 57
2017-10-25 02:00 | 57 | 57
2017-10-25 02:30 | 58 | 57
2017-10-25 03:00 | 58 | 57
2017-10-25 03:30 | 58 | 56
2017-10-25 04:00 | 58 | 56
2017-10-25 04:30 | 58 | 57
2017-10-25 05:00 | 58 | 57
2017-10-25 05:30 | 59 | 57
2017-10-25 06:00 | 56 | 56
2017-10-25 06:30 | 58 | 57
2017-10-25 07:00 | 58 | 57
2017-10-25 07:30 | 58 | 58
2017-10-25 08:00 | 61 | 59
2017-10-25 08:30 | 61 | 59
2017-10-25 09:00 | 61 | 59
2017-10-25 09:30 | 61 | 60
2017-10-25 10:00 | 61 | 59
2017-10-25 10:30 | 62 | 60
2017-10-25 11:00 | 62 | 61
2017-10-25 11:30 | 63 | 61
2017-10-25 12:00 | 63 | 62
2017-10-25 12:30 | 63 | 62
2017-10-25 13:00 | 63 | 62
2017-10-25 13:30 | 62 | 61
2017-10-25 14:00 | 61 | 59
2017-10-25 14:30 | 61 | 59
2017-10-25 15:00 | 60 | 59
2017-10-25 15:30 | 60 | 59
2017-10-25 16:00 | 61 | 60
2017-10-25 16:30 | 63 | 62
2017-10-25 17:00 | 63 | 62
2017-10-25 17:30 | 65 | 63
2017-10-25 18:00 | 65 | 64
2017-10-25 18:30 | 66 | 64
2017-10-25 19:00 | 67 | 65
2017-10-25 19:30 | 66 | 64
2017-10-25 20:00 | 66 | 65
2017-10-25 20:30 | 66 | 64
2017-10-25 21:00 | 65 | 63
2017-10-25 21:30 | 64 | 62
2017-10-25 22:00 | 64 | 61
2017-10-25 22:30 | 63 | 61
2017-10-25 23:00 | 61 | 60
2017-10-25 23:30 | 60 | 59
2017-10-26 | 59 | 58
2017-10-26 00:30 | 59 | 58
2017-10-26 01:00 | 60 | 58
2017-10-26 01:30 | 59 | 58
2017-10-26 02:00 | 58 | 58
2017-10-26 02:30 | 58 | 57
2017-10-26 03:00 | 58 | 57
2017-10-26 03:30 | 58 | 57
2017-10-26 04:00 | 58 | 57
2017-10-26 04:30 | 58 | 57
2017-10-26 05:00 | 59 | 58
2017-10-26 05:30 | 59 | 58
2017-10-26 06:00 | 59 | 58
2017-10-26 06:30 | 59 | 59
2017-10-26 07:00 | 60 | 60
2017-10-26 07:30 | 61 | 60
2017-10-26 08:00 | 61 | 60
2017-10-26 08:30 | 62 | 61
2017-10-26 09:00 | 63 | 62
2017-10-26 09:30 | 63 | 62
2017-10-26 10:00 | 63 | 63
2017-10-26 10:30 | 65 | 65
2017-10-26 11:00 | 64 | 64
2017-10-26 11:30 | 64 | 64
2017-10-26 12:00 | 64 | 64
2017-10-26 12:30 | 65 | 65
2017-10-26 13:00 | 65 | 65
2017-10-26 13:30 | 65 | 65
2017-10-26 14:00 | 67 | 66
2017-10-26 14:30 | 67 | 66
2017-10-26 15:00 | 67 | 67
2017-10-26 15:30 | 66 | 66
2017-10-26 16:00 | 67 | 66
2017-10-26 16:30 | 67 | 67
2017-10-26 17:00 | 65 | 65
2017-10-26 17:30 | 65 | 65
2017-10-26 18:00 | 65 | 65
2017-10-26 18:30 | 65 | 65
2017-10-26 19:00 | 70 | 69
2017-10-26 19:30 | 73 | 72
2017-10-26 20:00 | 73 | 73
2017-10-26 20:30 | 73 | 72
2017-10-26 21:00 | 70 | 68
2017-10-26 21:30 | 67 | 66
2017-10-26 22:00 | 67 | 65
2017-10-26 22:30 | 66 | 65
2017-10-26 23:00 | 64 | 62
2017-10-26 23:30 | 59 | 58
2017-10-27 | 59 | 58
2017-10-27 00:30 | 59 | 57
2017-10-27 01:00 | 59 | 57
2017-10-27 01:30 | 59 | 57
2017-10-27 02:00 | 58 | 57
2017-10-27 02:30 | 59 | 57
2017-10-27 03:00 | 59 | 57
2017-10-27 03:30 | 59 | 57
2017-10-27 04:00 | 59 | 57
2017-10-27 04:30 | 59 | 57
2017-10-27 05:00 | 59 | 57
2017-10-27 05:30 | 59 | 57
2017-10-27 06:00 | 59 | 57
2017-10-27 06:30 | 59 | 58
2017-10-27 07:00 | 60 | 58
2017-10-27 07:30 | 62 | 60
2017-10-27 08:00 | 63 | 61
2017-10-27 08:30 | 63 | 61
2017-10-27 09:00 | 63 | 61
2017-10-27 09:30 | 63 | 61
2017-10-27 10:00 | 63 | 61
2017-10-27 10:30 | 63 | 61
2017-10-27 11:00 | 64 | 62
2017-10-27 11:30 | 64 | 62
2017-10-27 12:00 | 64 | 62
2017-10-27 12:30 | 65 | 63
2017-10-27 13:00 | 65 | 63
2017-10-27 13:30 | 65 | 63
2017-10-27 14:00 | 64 | 63
2017-10-27 14:30 | 63 | 62
2017-10-27 15:00 | 64 | 63
2017-10-27 15:30 | 65 | 63
2017-10-27 16:00 | 66 | 64
2017-10-27 16:30 | 66 | 65
2017-10-27 17:00 | 67 | 66
2017-10-27 17:30 | 67 | 65
2017-10-27 18:00 | 65 | 63
2017-10-27 18:30 | 65 | 64
2017-10-27 19:00 | 67 | 65
2017-10-27 19:30 | 67 | 66
2017-10-27 20:00 | 67 | 65
2017-10-27 20:30 | 67 | 65
2017-10-27 21:00 | 66 | 64
2017-10-27 21:30 | 66 | 63
2017-10-27 22:00 | 66 | 63
2017-10-27 22:30 | 66 | 63
2017-10-27 23:00 | 65 | 62
2017-10-27 23:30 | 65 | 62
2017-10-28 | 64 | 61
2017-10-28 00:30 | 62 | 59
2017-10-28 01:00 | 63 | 60
2017-10-28 01:30 | 63 | 60
2017-10-28 02:00 | 63 | 59
2017-10-28 02:30 | 64 | 60
2017-10-28 03:00 | 63 | 59
2017-10-28 03:30 | 63 | 59
2017-10-28 04:00 | 63 | 59
2017-10-28 04:30 | 63 | 59
2017-10-28 05:00 | 63 | 59
2017-10-28 05:30 | 62 | 58
2017-10-28 06:00 | 61 | 57
2017-10-28 06:30 | 62 | 58
2017-10-28 07:00 | 62 | 59
2017-10-28 07:30 | 63 | 60
2017-10-28 08:00 | 63 | 60
2017-10-28 08:30 | 63 | 60
2017-10-28 09:00 | 63 | 60
2017-10-28 09:30 | 63 | 61
2017-10-28 10:00 | 64 | 61
2017-10-28 10:30 | 63 | 61
2017-10-28 11:00 | 64 | 62
2017-10-28 11:30 | 64 | 62
2017-10-28 12:00 | 64 | 63
2017-10-28 12:30 | 64 | 63
2017-10-28 13:00 | 64 | 63
2017-10-28 13:30 | 64 | 63
2017-10-28 14:00 | 65 | 63
2017-10-28 14:30 | 65 | 63
2017-10-28 15:00 | 65 | 63
2017-10-28 15:30 | 65 | 63
2017-10-28 16:00 | 66 | 64
2017-10-28 16:30 | 65 | 64
2017-10-28 17:00 | 66 | 65
2017-10-28 17:30 | 67 | 66
2017-10-28 18:00 | 67 | 66
2017-10-28 18:30 | 67 | 65
2017-10-28 19:00 | 67 | 66
2017-10-28 19:30 | 67 | 65
2017-10-28 20:00 | 66 | 65
2017-10-28 20:30 | 65 | 64
2017-10-28 21:00 | 65 | 64
2017-10-28 21:30 | 65 | 64
2017-10-28 22:00 | 65 | 63
2017-10-28 22:30 | 64 | 62
2017-10-28 23:00 | 65 | 62
2017-10-28 23:30 | 65 | 63
2017-10-29 | 67 | 64
2017-10-29 00:30 | 66 | 63
2017-10-29 01:00 | 63 | 62
2017-10-29 01:30 | 62 | 60
2017-10-29 02:00 | 61 | 60
2017-10-29 02:30 | 61 | 60
2017-10-29 03:00 | 60 | 59
2017-10-29 03:30 | 60 | 59
2017-10-29 04:00 | 60 | 59
2017-10-29 04:30 | 61 | 59
2017-10-29 05:00 | 60 | 59
2017-10-29 05:30 | 61 | 59
2017-10-29 06:00 | 61 | 60
2017-10-29 06:30 | 61 | 59
2017-10-29 07:00 | 60 | 59
2017-10-29 07:30 | 61 | 59
2017-10-29 08:00 | 61 | 60
2017-10-29 08:30 | 61 | 60
2017-10-29 09:00 | 62 | 61
2017-10-29 09:30 | 60 | 60
2017-10-29 10:00 | 62 | 61
2017-10-29 10:30 | 64 | 62
2017-10-29 11:00 | 64 | 62
2017-10-29 11:30 | 65 | 63
2017-10-29 12:00 | 65 | 64
2017-10-29 12:30 | 65 | 63
2017-10-29 13:00 | 66 | 64
2017-10-29 13:30 | 65 | 64
2017-10-29 14:00 | 65 | 63
2017-10-29 14:30 | 64 | 63
2017-10-29 15:00 | 65 | 64
2017-10-29 15:30 | 64 | 62
2017-10-29 16:00 | 64 | 62
2017-10-29 16:30 | 64 | 63
2017-10-29 17:00 | 65 | 64
2017-10-29 17:30 | 65 | 64
2017-10-29 18:00 | 65 | 64
2017-10-29 18:30 | 65 | 64
2017-10-29 19:00 | 66 | 65
2017-10-29 19:30 | 65 | 64
2017-10-29 20:00 | 65 | 64
2017-10-29 20:30 | 62 | 61
2017-10-29 21:00 | 63 | 61
2017-10-29 21:30 | 62 | 60
2017-10-29 22:00 | 61 | 59
2017-10-29 22:30 | 61 | 58
2017-10-29 23:00 | 61 | 58
2017-10-29 23:30 | 60 | 57
2017-10-30 | 59 | 57
2017-10-30 00:30 | 57 | 56
2017-10-30 01:00 | 57 | 56
2017-10-30 01:30 | 57 | 55
2017-10-30 02:00 | 57 | 55
2017-10-30 02:30 | 57 | 55
2017-10-30 03:00 | 57 | 55
2017-10-30 03:30 | 57 | 55
2017-10-30 04:00 | 57 | 55
2017-10-30 04:30 | 57 | 55
2017-10-30 05:00 | 57 | 55
2017-10-30 05:30 | 57 | 55
2017-10-30 06:00 | 56 | 54
2017-10-30 06:30 | 56 | 55
2017-10-30 07:00 | 58 | 57
2017-10-30 07:30 | 58 | 57
2017-10-30 08:00 | 58 | 58
2017-10-30 08:30 | 59 | 59
2017-10-30 09:00 | 60 | 60
2017-10-30 09:30 | 61 | 61
2017-10-30 10:00 | 61 | 61
2017-10-30 10:30 | 60 | 60
2017-10-30 11:00 | 60 | 60
2017-10-30 11:30 | 61 | 61
2017-10-30 12:00 | 61 | 61
2017-10-30 12:30 | 62 | 62
2017-10-30 13:00 | 62 | 62
2017-10-30 13:30 | 63 | 62
2017-10-30 14:00 | 63 | 62
2017-10-30 14:30 | 62 | 61
2017-10-30 15:00 | 62 | 61
2017-10-30 15:30 | 63 | 61
2017-10-30 16:00 | 64 | 62
2017-10-30 16:30 | 64 | 62
2017-10-30 17:00 | 67 | 64
2017-10-30 17:30 | 67 | 64
2017-10-30 18:00 | 68 | 65
2017-10-30 18:30 | 70 | 67
2017-10-30 19:00 | 69 | 66
2017-10-30 19:30 | 65 | 63
2017-10-30 20:00 | 64 | 61
2017-10-30 20:30 | 63 | 60
2017-10-30 21:00 | 61 | 59
2017-10-30 21:30 | 60 | 58
2017-10-30 22:00 | 60 | 59
2017-10-30 22:30 | 61 | 59
2017-10-30 23:00 | 58 | 56
2017-10-30 23:30 | 55 | 54
2017-10-31 | 55 | 54
2017-10-31 00:30 | 54 | 53
2017-10-31 01:00 | 53 | 52
2017-10-31 01:30 | 53 | 52
2017-10-31 02:00 | 56 | 54
2017-10-31 02:30 | 55 | 54
2017-10-31 03:00 | 54 | 53
2017-10-31 03:30 | 53 | 52
2017-10-31 04:00 | 54 | 52
2017-10-31 04:30 | 55 | 54
2017-10-31 05:00 | 56 | 54
2017-10-31 05:30 | 57 | 55
2017-10-31 06:00 | 56 | 55
2017-10-31 06:30 | 56 | 55
2017-10-31 07:00 | 56 | 55
2017-10-31 07:30 | 57 | 56
2017-10-31 08:00 | 56 | 56
2017-10-31 08:30 | 57 | 57
2017-10-31 09:00 | 56 | 56
2017-10-31 09:30 | 49 | 48
2017-10-31 10:00 | 49 | 49
2017-10-31 10:30 | 51 | 51
2017-10-31 11:00 | 52 | 52
2017-10-31 11:30 | 55 | 55
2017-10-31 12:00 | 63 | 63
2017-10-31 12:30 | 63 | 63
2017-10-31 13:00 | 62 | 62
2017-10-31 13:30 | 64 | 64
2017-10-31 14:00 | 65 | 65
2017-10-31 14:30 | 65 | 65
2017-10-31 15:00 | 67 | 67
2017-10-31 15:30 | 67 | 67
2017-10-31 16:00 | 60 | 60
2017-10-31 16:30 | 60 | 60
2017-10-31 17:00 | 58 | 58
2017-10-31 17:30 | 59 | 59
2017-10-31 18:00 | 58 | 58
2017-10-31 18:30 | 58 | 58
2017-10-31 19:00 | 57 | 57
2017-10-31 19:30 | 59 | 59
2017-10-31 20:00 | 61 | 61
2017-10-31 20:30 | 62 | 62
2017-10-31 21:00 | 63 | 63
2017-10-31 21:30 | 66 | 66
2017-10-31 22:00 | 65 | 65
2017-10-31 22:30 | 68 | 68
2017-10-31 23:00 | 67 | 67
2017-10-31 23:30 | 67 | 67
2017-11-01 | 65 | 65
2017-11-01 00:30 | 66 | 66
2017-11-01 01:00 | 66 | 66
2017-11-01 01:30 | 64 | 64
2017-11-01 02:00 | 63 | 62
2017-11-01 02:30 | 64 | 64
2017-11-01 03:00 | 64 | 64
2017-11-01 03:30 | 64 | 64
2017-11-01 04:00 | 65 | 64
2017-11-01 04:30 | 66 | 65
2017-11-01 05:00 | 65 | 64
2017-11-01 05:30 | 63 | 63
2017-11-01 06:00 | 64 | 63
2017-11-01 06:30 | 66 | 66
2017-11-01 07:00 | 67 | 67
2017-11-01 07:30 | 68 | 67
2017-11-01 08:00 | 69 | 68
2017-11-01 08:30 | 63 | 62
2017-11-01 09:00 | 60 | 60
2017-11-01 09:30 | 61 | 60
2017-11-01 10:00 | 59 | 59
2017-11-01 10:30 | 57 | 57
2017-11-01 11:00 | 53 | 52
2017-11-01 11:30 | 49 | 48
2017-11-01 12:00 | 45 | 44
2017-11-01 12:30 | 45 | 45
2017-11-01 13:00 | 50 | 50
2017-11-01 13:30 | 56 | 56
2017-11-01 14:00 | 56 | 56
2017-11-01 14:30 | 57 | 56
2017-11-01 15:00 | 56 | 55
2017-11-01 15:30 | 59 | 59
2017-11-01 16:00 | 60 | 60
2017-11-01 16:30 | 60 | 60
2017-11-01 17:00 | 60 | 59
2017-11-01 17:30 | 60 | 59
2017-11-01 18:00 | 60 | 60
2017-11-01 18:30 | 61 | 60
2017-11-01 19:00 | 60 | 60
2017-11-01 19:30 | 60 | 60
2017-11-01 20:00 | 60 | 59
2017-11-01 20:30 | 60 | 59
2017-11-01 21:00 | 60 | 59
2017-11-01 21:30 | 58 | 57
2017-11-01 22:00 | 57 | 57
2017-11-01 22:30 | 59 | 59
2017-11-01 23:00 | 58 | 58
2017-11-01 23:30 | 58 | 57
2017-11-02 | 56 | 55
2017-11-02 00:30 | 55 | 54
2017-11-02 01:00 | 54 | 53
2017-11-02 01:30 | 55 | 54
2017-11-02 02:00 | 57 | 57
2017-11-02 02:30 | 60 | 59
2017-11-02 03:00 | 60 | 59
2017-11-02 03:30 | 60 | 59
2017-11-02 04:00 | 59 | 58
2017-11-02 04:30 | 58 | 57
2017-11-02 05:00 | 56 | 55
2017-11-02 05:30 | 56 | 55
2017-11-02 06:00 | 56 | 56
2017-11-02 06:30 | 57 | 56
2017-11-02 07:00 | 58 | 58
2017-11-02 07:30 | 59 | 59
2017-11-02 08:00 | 61 | 61
2017-11-02 08:30 | 61 | 61
2017-11-02 09:00 | 62 | 62
2017-11-02 09:30 | 61 | 61
2017-11-02 10:00 | 61 | 61
2017-11-02 10:30 | 62 | 62
2017-11-02 11:00 | 64 | 64
2017-11-02 11:30 | 61 | 60
2017-11-02 12:00 | 63 | 62
2017-11-02 12:30 | 63 | 63
2017-11-02 13:00 | 63 | 62
2017-11-02 13:30 | 62 | 61
2017-11-02 14:00 | 62 | 61
2017-11-02 14:30 | 63 | 62
2017-11-02 15:00 | 63 | 62
2017-11-02 15:30 | 62 | 61
2017-11-02 16:00 | 63 | 62
2017-11-02 16:30 | 62 | 61
2017-11-02 17:00 | 59 | 58
2017-11-02 17:30 | 57 | 56
2017-11-02 18:00 | 57 | 55
2017-11-02 18:30 | 57 | 56
2017-11-02 19:00 | 58 | 57
2017-11-02 19:30 | 58 | 57
2017-11-02 20:00 | 58 | 57
2017-11-02 20:30 | 58 | 57
2017-11-02 21:00 | 57 | 55
2017-11-02 21:30 | 54 | 52
2017-11-02 22:00 | 54 | 52
2017-11-02 22:30 | 54 | 51
2017-11-02 23:00 | 54 | 51
2017-11-02 23:30 | 53 | 51
2017-11-03 | 53 | 51
2017-11-03 00:30 | 51 | 51
2017-11-03 01:00 | 50 | 50
2017-11-03 01:30 | 50 | 50
2017-11-03 02:00 | 51 | 50
2017-11-03 02:30 | 50 | 50
2017-11-03 03:00 | 50 | 50
2017-11-03 03:30 | 49 | 49
2017-11-03 04:00 | 50 | 49
2017-11-03 04:30 | 51 | 51
2017-11-03 05:00 | 51 | 51
2017-11-03 05:30 | 50 | 50
2017-11-03 06:00 | 50 | 50
2017-11-03 06:30 | 55 | 54
2017-11-03 07:00 | 59 | 58
2017-11-03 07:30 | 56 | 56
2017-11-03 08:00 | 58 | 57
2017-11-03 08:30 | 59 | 58
2017-11-03 09:00 | 60 | 60
2017-11-03 09:30 | 60 | 59
2017-11-03 10:00 | 57 | 57
2017-11-03 10:30 | 55 | 54
2017-11-03 11:00 | 55 | 55
2017-11-03 11:30 | 56 | 56
2017-11-03 12:00 | 58 | 57
2017-11-03 12:30 | 57 | 57
2017-11-03 13:00 | 57 | 56
2017-11-03 13:30 | 56 | 56
2017-11-03 14:00 | 55 | 55
2017-11-03 14:30 | 57 | 57
2017-11-03 15:00 | 58 | 57
2017-11-03 15:30 | 59 | 58
2017-11-03 16:00 | 59 | 58
2017-11-03 16:30 | 58 | 57
2017-11-03 17:00 | 58 | 57
2017-11-03 17:30 | 58 | 58
2017-11-03 18:00 | 59 | 58
2017-11-03 18:30 | 59 | 58
2017-11-03 19:00 | 60 | 59
2017-11-03 19:30 | 59 | 58
2017-11-03 20:00 | 60 | 59
2017-11-03 20:30 | 61 | 60
2017-11-03 21:00 | 59 | 58
2017-11-03 21:30 | 59 | 57
2017-11-03 22:00 | 58 | 57
2017-11-03 22:30 | 56 | 56
2017-11-03 23:00 | 55 | 55
2017-11-03 23:30 | 55 | 54
2017-11-04 | 54 | 54
2017-11-04 00:30 | 55 | 54
2017-11-04 01:00 | 54 | 52
2017-11-04 01:30 | 52 | 51
2017-11-04 02:00 | 52 | 51
2017-11-04 02:30 | 53 | 52
2017-11-04 03:00 | 54 | 53
2017-11-04 03:30 | 54 | 53
2017-11-04 04:00 | 54 | 53
2017-11-04 04:30 | 56 | 55
2017-11-04 05:00 | 58 | 57
2017-11-04 05:30 | 59 | 58
2017-11-04 06:00 | 58 | 57
2017-11-04 06:30 | 57 | 56
2017-11-04 07:00 | 56 | 55
2017-11-04 07:30 | 58 | 57
2017-11-04 08:00 | 59 | 59
2017-11-04 08:30 | 59 | 59
2017-11-04 09:00 | 60 | 60
2017-11-04 09:30 | 62 | 62
2017-11-04 10:00 | 63 | 63
2017-11-04 10:30 | 65 | 65
2017-11-04 11:00 | 65 | 64
2017-11-04 11:30 | 67 | 66
2017-11-04 12:00 | 66 | 65
2017-11-04 12:30 | 59 | 59
2017-11-04 13:00 | 11 | 11
2017-11-04 13:30 | 4 | 4
2017-11-04 14:00 | 39 | 38
2017-11-04 14:30 | 57 | 56
2017-11-04 15:00 | 58 | 57
2017-11-04 15:30 | 59 | 58
2017-11-04 16:00 | 60 | 59
2017-11-04 16:30 | 58 | 57
2017-11-04 17:00 | 57 | 56
2017-11-04 17:30 | 58 | 57
2017-11-04 18:00 | 59 | 58
2017-11-04 18:30 | 60 | 59
2017-11-04 19:00 | 60 | 60
2017-11-04 19:30 | 60 | 60
2017-11-04 20:00 | 60 | 59
2017-11-04 20:30 | 61 | 61
2017-11-04 21:00 | 61 | 60
2017-11-04 21:30 | 60 | 58
2017-11-04 22:00 | 59 | 57
2017-11-04 22:30 | 58 | 56
2017-11-04 23:00 | 58 | 56
2017-11-04 23:30 | 57 | 55
2017-11-05 | 57 | 54
2017-11-05 00:30 | 55 | 55
2017-11-05 01:00 | 54 | 53
2017-11-05 01:30 | 54 | 52
2017-11-05 02:00 | 54 | 53
2017-11-05 02:30 | 54 | 53
2017-11-05 03:00 | 54 | 52
2017-11-05 03:30 | 53 | 52
2017-11-05 04:00 | 53 | 51
2017-11-05 04:30 | 54 | 52
2017-11-05 05:00 | 55 | 54
2017-11-05 05:30 | 57 | 56
2017-11-05 06:00 | 59 | 58
2017-11-05 06:30 | 59 | 58
2017-11-05 07:00 | 58 | 56
2017-11-05 07:30 | 58 | 57
2017-11-05 08:00 | 59 | 58
2017-11-05 08:30 | 60 | 57
2017-11-05 09:00 | 60 | 57
2017-11-05 09:30 | 60 | 57
2017-11-05 10:00 | 57 | 57
2017-11-05 10:30 | 58 | 58
2017-11-05 11:00 | 56 | 56
2017-11-05 11:30 | 56 | 56
2017-11-05 12:00 | 57 | 56
2017-11-05 12:30 | 55 | 55
2017-11-05 13:00 | 53 | 53
2017-11-05 13:30 | 53 | 53
2017-11-05 14:00 | 54 | 54
2017-11-05 14:30 | 54 | 54
2017-11-05 15:00 | 52 | 52
2017-11-05 15:30 | 53 | 52
2017-11-05 16:00 | 54 | 53
2017-11-05 16:30 | 53 | 53
2017-11-05 17:00 | 56 | 55
2017-11-05 17:30 | 60 | 59
2017-11-05 18:00 | 60 | 59
2017-11-05 18:30 | 59 | 58
2017-11-05 19:00 | 59 | 58
2017-11-05 19:30 | 60 | 59
2017-11-05 20:00 | 59 | 58
2017-11-05 20:30 | 56 | 55
2017-11-05 21:00 | 55 | 54
2017-11-05 21:30 | 55 | 54
2017-11-05 22:00 | 55 | 54
2017-11-05 22:30 | 55 | 53
2017-11-05 23:00 | 53 | 52
2017-11-05 23:30 | 52 | 52
2017-11-06 | 52 | 52
2017-11-06 00:30 | 50 | 50
2017-11-06 01:00 | 50 | 48
2017-11-06 01:30 | 51 | 49
2017-11-06 02:00 | 52 | 50
2017-11-06 02:30 | 50 | 48
2017-11-06 03:00 | 50 | 49
2017-11-06 03:30 | 53 | 52
2017-11-06 04:00 | 53 | 51
2017-11-06 04:30 | 54 | 53
2017-11-06 05:00 | 54 | 53
2017-11-06 05:30 | 55 | 53
2017-11-06 06:00 | 55 | 53
2017-11-06 06:30 | 57 | 54
2017-11-06 07:00 | 56 | 56
2017-11-06 07:30 | 58 | 58
2017-11-06 08:00 | 59 | 58
2017-11-06 08:30 | 64 | 59
2017-11-06 09:00 | 63 | 58
2017-11-06 09:30 | 64 | 59
2017-11-06 10:00 | 63 | 57
2017-11-06 10:30 | 62 | 56
2017-11-06 11:00 | 60 | 55
2017-11-06 11:30 | 61 | 55
2017-11-06 12:00 | 61 | 55
2017-11-06 12:30 | 59 | 54
2017-11-06 13:00 | 60 | 54
2017-11-06 13:30 | 60 | 54
2017-11-06 14:00 | 60 | 54
2017-11-06 14:30 | 59 | 54
2017-11-06 15:00 | 59 | 54
2017-11-06 15:30 | 60 | 55
2017-11-06 16:00 | 60 | 55
2017-11-06 16:30 | 61 | 56
2017-11-06 17:00 | 63 | 57
2017-11-06 17:30 | 61 | 55
2017-11-06 18:00 | 62 | 54
2017-11-06 18:30 | 64 | 55
2017-11-06 19:00 | 64 | 56
2017-11-06 19:30 | 64 | 56
2017-11-06 20:00 | 64 | 56
2017-11-06 20:30 | 64 | 55
2017-11-06 21:00 | 63 | 55
2017-11-06 21:30 | 61 | 54
2017-11-06 22:00 | 60 | 52
2017-11-06 22:30 | 60 | 52
2017-11-06 23:00 | 60 | 51
2017-11-06 23:30 | 60 | 51
2017-11-07 | 61 | 51
2017-11-07 00:30 | 62 | 51
2017-11-07 01:00 | 61 | 50
2017-11-07 01:30 | 57 | 50
2017-11-07 02:00 | 51 | 50
2017-11-07 02:30 | 50 | 49
2017-11-07 03:00 | 49 | 48
2017-11-07 03:30 | 49 | 48
2017-11-07 04:00 | 49 | 48
2017-11-07 04:30 | 51 | 50
2017-11-07 05:00 | 50 | 49
2017-11-07 05:30 | 49 | 48
2017-11-07 06:00 | 50 | 49
2017-11-07 06:30 | 50 | 50
2017-11-07 07:00 | 52 | 51
2017-11-07 07:30 | 54 | 54
2017-11-07 08:00 | 57 | 56
2017-11-07 08:30 | 55 | 55
2017-11-07 09:00 | 54 | 54
2017-11-07 09:30 | 54 | 54
2017-11-07 10:00 | 54 | 54
2017-11-07 10:30 | 55 | 54
2017-11-07 11:00 | 54 | 54
2017-11-07 11:30 | 59 | 59
2017-11-07 12:00 | 63 | 63
2017-11-07 12:30 | 62 | 62
2017-11-07 13:00 | 60 | 60
2017-11-07 13:30 | 60 | 60
2017-11-07 14:00 | 59 | 59
2017-11-07 14:30 | 62 | 62
2017-11-07 15:00 | 62 | 62
2017-11-07 15:30 | 58 | 58
2017-11-07 16:00 | 58 | 58
2017-11-07 16:30 | 60 | 60
2017-11-07 17:00 | 63 | 63
2017-11-07 17:30 | 64 | 64
2017-11-07 18:00 | 61 | 60
2017-11-07 18:30 | 61 | 60
2017-11-07 19:00 | 62 | 61
2017-11-07 19:30 | 63 | 62
2017-11-07 20:00 | 61 | 61
2017-11-07 20:30 | 60 | 60
2017-11-07 21:00 | 60 | 60
2017-11-07 21:30 | 58 | 57
2017-11-07 22:00 | 57 | 55
2017-11-07 22:30 | 56 | 54
2017-11-07 23:00 | 56 | 54
2017-11-07 23:30 | 56 | 53
2017-11-08 | 54 | 52
2017-11-08 00:30 | 55 | 52
2017-11-08 01:00 | 54 | 51
2017-11-08 01:30 | 54 | 51
2017-11-08 02:00 | 54 | 52
2017-11-08 02:30 | 54 | 52
2017-11-08 03:00 | 55 | 52
2017-11-08 03:30 | 55 | 52
2017-11-08 04:00 | 56 | 53
2017-11-08 04:30 | 56 | 53
2017-11-08 05:00 | 55 | 52
2017-11-08 05:30 | 55 | 53
2017-11-08 06:00 | 56 | 54
2017-11-08 06:30 | 58 | 56
2017-11-08 07:00 | 58 | 56
2017-11-08 07:30 | 58 | 57
2017-11-08 08:00 | 60 | 60
2017-11-08 08:30 | 58 | 57
2017-11-08 09:00 | 57 | 57
2017-11-08 09:30 | 57 | 57
2017-11-08 10:00 | 56 | 55
2017-11-08 10:30 | 58 | 57
2017-11-08 11:00 | 58 | 57
2017-11-08 11:30 | 58 | 57
2017-11-08 12:00 | 58 | 57
2017-11-08 12:30 | 58 | 57
2017-11-08 13:00 | 59 | 58
2017-11-08 13:30 | 60 | 59
2017-11-08 14:00 | 59 | 58
2017-11-08 14:30 | 59 | 58
2017-11-08 15:00 | 60 | 59
2017-11-08 15:30 | 59 | 58
2017-11-08 16:00 | 59 | 58
2017-11-08 16:30 | 61 | 59
2017-11-08 17:00 | 62 | 61
2017-11-08 17:30 | 63 | 62
2017-11-08 18:00 | 63 | 61
2017-11-08 18:30 | 62 | 61
2017-11-08 19:00 | 63 | 61
2017-11-08 19:30 | 61 | 60
2017-11-08 20:00 | 61 | 60
2017-11-08 20:30 | 62 | 60
2017-11-08 21:00 | 63 | 61
2017-11-08 21:30 | 62 | 60
2017-11-08 22:00 | 61 | 58
2017-11-08 22:30 | 61 | 58
2017-11-08 23:00 | 59 | 56
2017-11-08 23:30 | 57 | 55
2017-11-09 | 57 | 55
2017-11-09 00:30 | 56 | 54
2017-11-09 01:00 | 55 | 52
2017-11-09 01:30 | 56 | 53
2017-11-09 02:00 | 56 | 53
2017-11-09 02:30 | 56 | 54
2017-11-09 03:00 | 56 | 54
2017-11-09 03:30 | 56 | 53
2017-11-09 04:00 | 56 | 54
2017-11-09 04:30 | 58 | 55
2017-11-09 05:00 | 57 | 55
2017-11-09 05:30 | 58 | 55
2017-11-09 06:00 | 57 | 55
2017-11-09 06:30 | 58 | 56
2017-11-09 07:00 | 59 | 57
2017-11-09 07:30 | 60 | 59
2017-11-09 08:00 | 67 | 63
2017-11-09 08:30 | 68 | 61
2017-11-09 09:00 | 66 | 60
2017-11-09 09:30 | 66 | 60
2017-11-09 10:00 | 66 | 60
2017-11-09 10:30 | 66 | 59
2017-11-09 11:00 | 65 | 58
2017-11-09 11:30 | 66 | 59
2017-11-09 12:00 | 68 | 61
2017-11-09 12:30 | 67 | 61
2017-11-09 13:00 | 66 | 59
2017-11-09 13:30 | 67 | 60
2017-11-09 14:00 | 67 | 60
2017-11-09 14:30 | 67 | 60
2017-11-09 15:00 | 67 | 60
2017-11-09 15:30 | 69 | 62
2017-11-09 16:00 | 70 | 62
2017-11-09 16:30 | 71 | 63
2017-11-09 17:00 | 75 | 67
2017-11-09 17:30 | 76 | 67
2017-11-09 18:00 | 74 | 65
2017-11-09 18:30 | 74 | 65
2017-11-09 19:00 | 77 | 68
2017-11-09 19:30 | 78 | 69
2017-11-09 20:00 | 76 | 68
2017-11-09 20:30 | 67 | 65
2017-11-09 21:00 | 66 | 64
2017-11-09 21:30 | 64 | 63
2017-11-09 22:00 | 61 | 61
2017-11-09 22:30 | 61 | 60
2017-11-09 23:00 | 61 | 61
2017-11-09 23:30 | 62 | 61
2017-11-10 | 58 | 57
2017-11-10 00:30 | 54 | 53
2017-11-10 01:00 | 54 | 52
2017-11-10 01:30 | 54 | 53
2017-11-10 02:00 | 54 | 53
2017-11-10 02:30 | 54 | 53
2017-11-10 03:00 | 55 | 54
2017-11-10 03:30 | 54 | 53
2017-11-10 04:00 | 55 | 53
2017-11-10 04:30 | 53 | 52
2017-11-10 05:00 | 53 | 51
2017-11-10 05:30 | 53 | 51
2017-11-10 06:00 | 51 | 51
2017-11-10 06:30 | 53 | 52
2017-11-10 07:00 | 52 | 52
2017-11-10 07:30 | 55 | 54
2017-11-10 08:00 | 59 | 58
2017-11-10 08:30 | 59 | 58
2017-11-10 09:00 | 58 | 57
2017-11-10 09:30 | 58 | 57
2017-11-10 10:00 | 58 | 57
2017-11-10 10:30 | 60 | 59
2017-11-10 11:00 | 57 | 56
2017-11-10 11:30 | 57 | 56
2017-11-10 12:00 | 58 | 57
2017-11-10 12:30 | 56 | 55
2017-11-10 13:00 | 58 | 57
2017-11-10 13:30 | 59 | 58
2017-11-10 14:00 | 58 | 57
2017-11-10 14:30 | 59 | 58
2017-11-10 15:00 | 57 | 56
2017-11-10 15:30 | 58 | 57
2017-11-10 16:00 | 59 | 58
2017-11-10 16:30 | 58 | 57
2017-11-10 17:00 | 59 | 58
2017-11-10 17:30 | 59 | 58
2017-11-10 18:00 | 59 | 58
2017-11-10 18:30 | 60 | 58
2017-11-10 19:00 | 60 | 58
2017-11-10 19:30 | 60 | 58
2017-11-10 20:00 | 60 | 59
2017-11-10 20:30 | 59 | 58
2017-11-10 21:00 | 57 | 57
2017-11-10 21:30 | 56 | 56
2017-11-10 22:00 | 56 | 56
2017-11-10 22:30 | 55 | 54
2017-11-10 23:00 | 54 | 53
2017-11-10 23:30 | 53 | 52
2017-11-11 | 52 | 51
2017-11-11 00:30 | 51 | 49
2017-11-11 01:00 | 50 | 49
2017-11-11 01:30 | 51 | 50
2017-11-11 02:00 | 51 | 50
2017-11-11 02:30 | 50 | 49
2017-11-11 03:00 | 50 | 49
2017-11-11 03:30 | 50 | 49
2017-11-11 04:00 | 49 | 48
2017-11-11 04:30 | 49 | 48
2017-11-11 05:00 | 50 | 48
2017-11-11 05:30 | 49 | 48
2017-11-11 06:00 | 49 | 48
2017-11-11 06:30 | 49 | 48
2017-11-11 07:00 | 50 | 49
2017-11-11 07:30 | 51 | 50
2017-11-11 08:00 | 51 | 50
2017-11-11 08:30 | 52 | 50
2017-11-11 09:00 | 53 | 51
2017-11-11 09:30 | 53 | 51
2017-11-11 10:00 | 52 | 50
2017-11-11 10:30 | 53 | 51
2017-11-11 11:00 | 55 | 53
2017-11-11 11:30 | 56 | 53
2017-11-11 12:00 | 57 | 55
2017-11-11 12:30 | 56 | 54
2017-11-11 13:00 | 57 | 55
2017-11-11 13:30 | 58 | 56
2017-11-11 14:00 | 56 | 54
2017-11-11 14:30 | 56 | 54
2017-11-11 15:00 | 58 | 56
2017-11-11 15:30 | 58 | 56
2017-11-11 16:00 | 59 | 57
2017-11-11 16:30 | 58 | 56
2017-11-11 17:00 | 59 | 57
2017-11-11 17:30 | 60 | 58
2017-11-11 18:00 | 59 | 58
2017-11-11 18:30 | 60 | 58
2017-11-11 19:00 | 61 | 60
2017-11-11 19:30 | 65 | 63
2017-11-11 20:00 | 63 | 60
2017-11-11 20:30 | 61 | 57
2017-11-11 21:00 | 60 | 57
2017-11-11 21:30 | 60 | 57
2017-11-11 22:00 | 58 | 55
2017-11-11 22:30 | 57 | 54
2017-11-11 23:00 | 56 | 54
2017-11-11 23:30 | 57 | 56
2017-11-12 | 57 | 55
2017-11-12 00:30 | 55 | 54
2017-11-12 01:00 | 55 | 54
2017-11-12 01:30 | 56 | 55
2017-11-12 02:00 | 53 | 52
2017-11-12 02:30 | 54 | 52
2017-11-12 03:00 | 52 | 51
2017-11-12 03:30 | 52 | 51
2017-11-12 04:00 | 52 | 50
2017-11-12 04:30 | 53 | 51
2017-11-12 05:00 | 53 | 52
2017-11-12 05:30 | 52 | 51
2017-11-12 06:00 | 51 | 50
2017-11-12 06:30 | 51 | 49
2017-11-12 07:00 | 52 | 51
2017-11-12 07:30 | 52 | 50
2017-11-12 08:00 | 52 | 51
2017-11-12 08:30 | 53 | 52
2017-11-12 09:00 | 55 | 53
2017-11-12 09:30 | 58 | 57
2017-11-12 10:00 | 56 | 55
2017-11-12 10:30 | 55 | 53
2017-11-12 11:00 | 55 | 53
2017-11-12 11:30 | 56 | 53
2017-11-12 12:00 | 53 | 53
2017-11-12 12:30 | 53 | 53
2017-11-12 13:00 | 55 | 54
2017-11-12 13:30 | 56 | 56
2017-11-12 14:00 | 55 | 55
2017-11-12 14:30 | 56 | 55
2017-11-12 15:00 | 57 | 57
2017-11-12 15:30 | 57 | 57
2017-11-12 16:00 | 58 | 58
2017-11-12 16:30 | 59 | 59
2017-11-12 17:00 | 58 | 58
2017-11-12 17:30 | 58 | 58
2017-11-12 18:00 | 57 | 57
2017-11-12 18:30 | 58 | 58
2017-11-12 19:00 | 60 | 59
2017-11-12 19:30 | 59 | 59
2017-11-12 20:00 | 59 | 59
2017-11-12 20:30 | 58 | 58
2017-11-12 21:00 | 58 | 58
2017-11-12 21:30 | 56 | 56
2017-11-12 22:00 | 54 | 54
2017-11-12 22:30 | 54 | 53
2017-11-12 23:00 | 52 | 51
2017-11-12 23:30 | 50 | 49
2017-11-13 | 50 | 49
2017-11-13 00:30 | 51 | 50
2017-11-13 01:00 | 50 | 50
2017-11-13 01:30 | 51 | 49
2017-11-13 02:00 | 51 | 49
2017-11-13 02:30 | 51 | 49
2017-11-13 03:00 | 49 | 48
2017-11-13 03:30 | 49 | 48
2017-11-13 04:00 | 50 | 48
2017-11-13 04:30 | 51 | 49
2017-11-13 05:00 | 50 | 48
2017-11-13 05:30 | 49 | 48
2017-11-13 06:00 | 50 | 49
2017-11-13 06:30 | 51 | 50
2017-11-13 07:00 | 52 | 50
2017-11-13 07:30 | 53 | 52
2017-11-13 08:00 | 54 | 53
2017-11-13 08:30 | 53 | 52
2017-11-13 09:00 | 52 | 51
2017-11-13 09:30 | 52 | 51
2017-11-13 10:00 | 52 | 52
2017-11-13 10:30 | 52 | 52
2017-11-13 11:00 | 51 | 51
2017-11-13 11:30 | 52 | 51
2017-11-13 12:00 | 52 | 52
2017-11-13 12:30 | 52 | 52
2017-11-13 13:00 | 51 | 51
2017-11-13 13:30 | 53 | 52
2017-11-13 14:00 | 54 | 53
2017-11-13 14:30 | 54 | 54
2017-11-13 15:00 | 56 | 56
2017-11-13 15:30 | 60 | 59
2017-11-13 16:00 | 69 | 68
2017-11-13 16:30 | 66 | 66
2017-11-13 17:00 | 63 | 63
2017-11-13 17:30 | 67 | 65
2017-11-13 18:00 | 69 | 68
2017-11-13 18:30 | 70 | 69
2017-11-13 19:00 | 71 | 70
2017-11-13 19:30 | 68 | 67
2017-11-13 20:00 | 65 | 64
2017-11-13 20:30 | 64 | 62
2017-11-13 21:00 | 64 | 63
2017-11-13 21:30 | 64 | 62
2017-11-13 22:00 | 61 | 60
2017-11-13 22:30 | 60 | 59
2017-11-13 23:00 | 58 | 57
2017-11-13 23:30 | 57 | 56
2017-11-14 | 55 | 54
2017-11-14 00:30 | 51 | 50
2017-11-14 01:00 | 52 | 52
2017-11-14 01:30 | 52 | 52
2017-11-14 02:00 | 48 | 47
2017-11-14 02:30 | 47 | 46
2017-11-14 03:00 | 45 | 45
2017-11-14 03:30 | 45 | 44
2017-11-14 04:00 | 44 | 44
2017-11-14 04:30 | 44 | 43
2017-11-14 05:00 | 43 | 42
2017-11-14 05:30 | 42 | 41
2017-11-14 06:00 | 34 | 26
2017-11-14 06:30 | 13 | 8
2017-11-14 07:00 | 10 | 7
2017-11-14 07:30 | 11 | 9
2017-11-14 08:00 | 11 | 10
2017-11-14 08:30 | 13 | 13
2017-11-14 09:00 | 13 | 13
2017-11-14 09:30 | 14 | 14
2017-11-14 10:00 | 14 | 14
2017-11-14 10:30 | 14 | 14
2017-11-14 11:00 | 13 | 13
2017-11-14 11:30 | 16 | 16
2017-11-14 12:00 | 18 | 18
2017-11-14 12:30 | 18 | 18
2017-11-14 13:00 | 19 | 19
2017-11-14 13:30 | 19 | 18
2017-11-14 14:00 | 18 | 18
2017-11-14 14:30 | 16 | 16
2017-11-14 15:00 | 16 | 16
2017-11-14 15:30 | 20 | 20
2017-11-14 16:00 | 25 | 24
2017-11-14 16:30 | 26 | 26
2017-11-14 17:00 | 25 | 24
2017-11-14 17:30 | 23 | 23
2017-11-14 18:00 | 20 | 19
2017-11-14 18:30 | 21 | 20
2017-11-14 19:00 | 25 | 24
2017-11-14 19:30 | 25 | 25
2017-11-14 20:00 | 38 | 38
2017-11-14 20:30 | 47 | 46
2017-11-14 21:00 | 48 | 47
2017-11-14 21:30 | 50 | 49
2017-11-14 22:00 | 51 | 50
2017-11-14 22:30 | 50 | 48
2017-11-14 23:00 | 50 | 48
2017-11-14 23:30 | 51 | 49
2017-11-15 | 52 | 50
2017-11-15 00:30 | 51 | 50
2017-11-15 01:00 | 35 | 35
2017-11-15 01:30 | 48 | 48
2017-11-15 02:00 | 48 | 47
2017-11-15 02:30 | 49 | 48
2017-11-15 03:00 | 49 | 48
2017-11-15 03:30 | 51 | 50
2017-11-15 04:00 | 50 | 49
2017-11-15 04:30 | 49 | 49
2017-11-15 05:00 | 52 | 51
2017-11-15 05:30 | 51 | 50
2017-11-15 06:00 | 50 | 49
2017-11-15 06:30 | 51 | 49
2017-11-15 07:00 | 52 | 51
2017-11-15 07:30 | 55 | 54
2017-11-15 08:00 | 54 | 53
2017-11-15 08:30 | 56 | 54
2017-11-15 09:00 | 57 | 55
2017-11-15 09:30 | 56 | 54
2017-11-15 10:00 | 56 | 54
2017-11-15 10:30 | 56 | 54
2017-11-15 11:00 | 56 | 54
2017-11-15 11:30 | 58 | 56
2017-11-15 12:00 | 59 | 57
2017-11-15 12:30 | 59 | 59
2017-11-15 13:00 | 59 | 58
2017-11-15 13:30 | 59 | 59
2017-11-15 14:00 | 60 | 60
2017-11-15 14:30 | 58 | 58
2017-11-15 15:00 | 56 | 55
2017-11-15 15:30 | 50 | 49
2017-11-15 16:00 | 59 | 58
2017-11-15 16:30 | 61 | 61
2017-11-15 17:00 | 61 | 60
2017-11-15 17:30 | 62 | 61
2017-11-15 18:00 | 61 | 60
2017-11-15 18:30 | 61 | 60
2017-11-15 19:00 | 61 | 60
2017-11-15 19:30 | 61 | 61
2017-11-15 20:00 | 62 | 61
2017-11-15 20:30 | 60 | 59
2017-11-15 21:00 | 59 | 58
2017-11-15 21:30 | 58 | 57
2017-11-15 22:00 | 58 | 57
2017-11-15 22:30 | 57 | 56
2017-11-15 23:00 | 55 | 54
2017-11-15 23:30 | 54 | 53
2017-11-16 | 53 | 53
2017-11-16 00:30 | 52 | 52
2017-11-16 01:00 | 53 | 51
2017-11-16 01:30 | 53 | 51
2017-11-16 02:00 | 53 | 51
2017-11-16 02:30 | 53 | 51
2017-11-16 03:00 | 53 | 51
2017-11-16 03:30 | 53 | 51
2017-11-16 04:00 | 53 | 51
2017-11-16 04:30 | 55 | 53
2017-11-16 05:00 | 57 | 55
2017-11-16 05:30 | 57 | 55
2017-11-16 06:00 | 55 | 54
2017-11-16 06:30 | 56 | 54
2017-11-16 07:00 | 58 | 57
2017-11-16 07:30 | 64 | 63
2017-11-16 08:00 | 64 | 63
2017-11-16 08:30 | 64 | 64
2017-11-16 09:00 | 64 | 64
2017-11-16 09:30 | 65 | 65
2017-11-16 10:00 | 66 | 65
2017-11-16 10:30 | 65 | 65
2017-11-16 11:00 | 65 | 63
2017-11-16 11:30 | 67 | 65
2017-11-16 12:00 | 67 | 64
2017-11-16 12:30 | 66 | 63
2017-11-16 13:00 | 66 | 64
2017-11-16 13:30 | 65 | 65
2017-11-16 14:00 | 66 | 65
2017-11-16 14:30 | 64 | 63
2017-11-16 15:00 | 64 | 63
2017-11-16 15:30 | 67 | 67
2017-11-16 16:00 | 65 | 65
2017-11-16 16:30 | 66 | 65
2017-11-16 17:00 | 65 | 65
2017-11-16 17:30 | 65 | 64
2017-11-16 18:00 | 67 | 66
2017-11-16 18:30 | 77 | 70
2017-11-16 19:00 | 76 | 69
2017-11-16 19:30 | 75 | 67
2017-11-16 20:00 | 75 | 67
2017-11-16 20:30 | 72 | 64
2017-11-16 21:00 | 64 | 63
2017-11-16 21:30 | 63 | 62
2017-11-16 22:00 | 61 | 60
2017-11-16 22:30 | 60 | 59
2017-11-16 23:00 | 56 | 55
2017-11-16 23:30 | 56 | 54
2017-11-17 | 54 | 53
2017-11-17 00:30 | 52 | 51
2017-11-17 01:00 | 52 | 51
2017-11-17 01:30 | 51 | 51
2017-11-17 02:00 | 49 | 49
2017-11-17 02:30 | 49 | 49
2017-11-17 03:00 | 49 | 49
2017-11-17 03:30 | 49 | 49
2017-11-17 04:00 | 49 | 48
2017-11-17 04:30 | 49 | 48
2017-11-17 05:00 | 49 | 49
2017-11-17 05:30 | 48 | 48
2017-11-17 06:00 | 48 | 47
2017-11-17 06:30 | 50 | 49
2017-11-17 07:00 | 52 | 52
2017-11-17 07:30 | 54 | 53
2017-11-17 08:00 | 58 | 55
2017-11-17 08:30 | 63 | 55
2017-11-17 09:00 | 65 | 57
2017-11-17 09:30 | 66 | 59
2017-11-17 10:00 | 66 | 59
2017-11-17 10:30 | 63 | 56
2017-11-17 11:00 | 62 | 55
2017-11-17 11:30 | 62 | 55
2017-11-17 12:00 | 62 | 55
2017-11-17 12:30 | 62 | 55
2017-11-17 13:00 | 61 | 56
2017-11-17 13:30 | 62 | 56
2017-11-17 14:00 | 62 | 56
2017-11-17 14:30 | 62 | 56
2017-11-17 15:00 | 63 | 57
2017-11-17 15:30 | 66 | 59
2017-11-17 16:00 | 67 | 59
2017-11-17 16:30 | 73 | 67
2017-11-17 17:00 | 73 | 68
2017-11-17 17:30 | 72 | 67
2017-11-17 18:00 | 73 | 67
2017-11-17 18:30 | 74 | 68
2017-11-17 19:00 | 74 | 69
2017-11-17 19:30 | 75 | 69
2017-11-17 20:00 | 76 | 70
2017-11-17 20:30 | 74 | 68
2017-11-17 21:00 | 73 | 67
2017-11-17 21:30 | 73 | 67
2017-11-17 22:00 | 73 | 67
2017-11-17 22:30 | 73 | 67
2017-11-17 23:00 | 71 | 64
2017-11-17 23:30 | 71 | 63
2017-11-18 | 70 | 63
2017-11-18 00:30 | 70 | 62
2017-11-18 01:00 | 67 | 60
2017-11-18 01:30 | 60 | 60
2017-11-18 02:00 | 60 | 60
2017-11-18 02:30 | 60 | 59
2017-11-18 03:00 | 56 | 55
2017-11-18 03:30 | 54 | 54
2017-11-18 04:00 | 53 | 52
2017-11-18 04:30 | 51 | 50
2017-11-18 05:00 | 57 | 57
2017-11-18 05:30 | 58 | 57
2017-11-18 06:00 | 58 | 58
2017-11-18 06:30 | 58 | 58
2017-11-18 07:00 | 53 | 53
2017-11-18 07:30 | 51 | 50
2017-11-18 08:00 | 51 | 50
2017-11-18 08:30 | 52 | 51
2017-11-18 09:00 | 51 | 50
2017-11-18 09:30 | 48 | 47
2017-11-18 10:00 | 47 | 46
2017-11-18 10:30 | 48 | 46
2017-11-18 11:00 | 47 | 45
2017-11-18 11:30 | 47 | 45
2017-11-18 12:00 | 47 | 45
2017-11-18 12:30 | 48 | 45
2017-11-18 13:00 | 49 | 47
2017-11-18 13:30 | 48 | 46
2017-11-18 14:00 | 49 | 46
2017-11-18 14:30 | 49 | 46
2017-11-18 15:00 | 48 | 45
2017-11-18 15:30 | 52 | 50
2017-11-18 16:00 | 57 | 55
2017-11-18 16:30 | 58 | 56
2017-11-18 17:00 | 59 | 57
2017-11-18 17:30 | 59 | 57
2017-11-18 18:00 | 60 | 59
2017-11-18 18:30 | 60 | 58
2017-11-18 19:00 | 60 | 59
2017-11-18 19:30 | 61 | 60
2017-11-18 20:00 | 60 | 59
2017-11-18 20:30 | 59 | 58
2017-11-18 21:00 | 60 | 59
2017-11-18 21:30 | 60 | 59
2017-11-18 22:00 | 60 | 59
2017-11-18 22:30 | 58 | 57
2017-11-18 23:00 | 58 | 56
2017-11-18 23:30 | 59 | 58
2017-11-19 | 57 | 56
2017-11-19 00:30 | 57 | 56
2017-11-19 01:00 | 56 | 54
2017-11-19 01:30 | 57 | 55
2017-11-19 02:00 | 56 | 55
2017-11-19 02:30 | 56 | 56
2017-11-19 03:00 | 56 | 56
2017-11-19 03:30 | 55 | 55
2017-11-19 04:00 | 54 | 53
2017-11-19 04:30 | 54 | 53
2017-11-19 05:00 | 53 | 52
2017-11-19 05:30 | 52 | 51
2017-11-19 06:00 | 50 | 49
2017-11-19 06:30 | 49 | 49
2017-11-19 07:00 | 50 | 49
2017-11-19 07:30 | 50 | 49
2017-11-19 08:00 | 51 | 51
2017-11-19 08:30 | 52 | 51
2017-11-19 09:00 | 52 | 52
2017-11-19 09:30 | 50 | 50
2017-11-19 10:00 | 51 | 50
2017-11-19 10:30 | 51 | 51
2017-11-19 11:00 | 50 | 50
2017-11-19 11:30 | 50 | 50
2017-11-19 12:00 | 50 | 50
2017-11-19 12:30 | 50 | 49
2017-11-19 13:00 | 51 | 51
2017-11-19 13:30 | 51 | 50
2017-11-19 14:00 | 51 | 50
2017-11-19 14:30 | 51 | 50
2017-11-19 15:00 | 51 | 50
2017-11-19 15:30 | 51 | 51
2017-11-19 16:00 | 52 | 52
2017-11-19 16:30 | 53 | 53
2017-11-19 17:00 | 54 | 53
2017-11-19 17:30 | 54 | 54
2017-11-19 18:00 | 53 | 53
2017-11-19 18:30 | 55 | 54
2017-11-19 19:00 | 55 | 55
2017-11-19 19:30 | 56 | 56
2017-11-19 20:00 | 55 | 55
2017-11-19 20:30 | 55 | 55
2017-11-19 21:00 | 54 | 54
2017-11-19 21:30 | 54 | 54
2017-11-19 22:00 | 53 | 53
2017-11-19 22:30 | 52 | 52
2017-11-19 23:00 | 51 | 50
2017-11-19 23:30 | 50 | 50
2017-11-20 | 51 | 51
2017-11-20 00:30 | 51 | 51
2017-11-20 01:00 | 50 | 49
2017-11-20 01:30 | 50 | 50
2017-11-20 02:00 | 50 | 50
2017-11-20 02:30 | 49 | 48
2017-11-20 03:00 | 48 | 48
2017-11-20 03:30 | 49 | 48
2017-11-20 04:00 | 50 | 49
2017-11-20 04:30 | 49 | 49
2017-11-20 05:00 | 49 | 49
2017-11-20 05:30 | 50 | 50
2017-11-20 06:00 | 49 | 49
2017-11-20 06:30 | 49 | 49
2017-11-20 07:00 | 51 | 50
2017-11-20 07:30 | 52 | 52
2017-11-20 08:00 | 58 | 53
2017-11-20 08:30 | 54 | 52
2017-11-20 09:00 | 54 | 54
2017-11-20 09:30 | 53 | 53
2017-11-20 10:00 | 53 | 53
2017-11-20 10:30 | 51 | 51
2017-11-20 11:00 | 51 | 51
2017-11-20 11:30 | 52 | 51
2017-11-20 12:00 | 52 | 52
2017-11-20 12:30 | 52 | 52
2017-11-20 13:00 | 52 | 52
2017-11-20 13:30 | 53 | 53
2017-11-20 14:00 | 53 | 53
2017-11-20 14:30 | 52 | 52
2017-11-20 15:00 | 53 | 53
2017-11-20 15:30 | 56 | 56
2017-11-20 16:00 | 57 | 57
2017-11-20 16:30 | 57 | 57
2017-11-20 17:00 | 57 | 57
2017-11-20 17:30 | 57 | 56
2017-11-20 18:00 | 56 | 55
2017-11-20 18:30 | 62 | 55
2017-11-20 19:00 | 67 | 56
2017-11-20 19:30 | 63 | 56
2017-11-20 20:00 | 57 | 57
2017-11-20 20:30 | 57 | 56
2017-11-20 21:00 | 57 | 57
2017-11-20 21:30 | 55 | 55
2017-11-20 22:00 | 55 | 55
2017-11-20 22:30 | 57 | 57
2017-11-20 23:00 | 57 | 57
2017-11-20 23:30 | 57 | 57
2017-11-21 | 56 | 56
2017-11-21 00:30 | 55 | 55
2017-11-21 01:00 | 55 | 55
2017-11-21 01:30 | 54 | 54
2017-11-21 02:00 | 54 | 53
2017-11-21 02:30 | 54 | 54
2017-11-21 03:00 | 53 | 53
2017-11-21 03:30 | 54 | 54
2017-11-21 04:00 | 54 | 54
2017-11-21 04:30 | 55 | 54
2017-11-21 05:00 | 54 | 54
2017-11-21 05:30 | 54 | 54
2017-11-21 06:00 | 54 | 54
2017-11-21 06:30 | 56 | 56
2017-11-21 07:00 | 58 | 58
2017-11-21 07:30 | 68 | 68
2017-11-21 08:00 | 68 | 68
2017-11-21 08:30 | 69 | 69
2017-11-21 09:00 | 70 | 69
2017-11-21 09:30 | 69 | 69
2017-11-21 10:00 | 71 | 70
2017-11-21 10:30 | 71 | 70
2017-11-21 11:00 | 73 | 72
2017-11-21 11:30 | 67 | 66
2017-11-21 12:00 | 64 | 62
2017-11-21 12:30 | 63 | 61
2017-11-21 13:00 | 61 | 59
2017-11-21 13:30 | 61 | 59
2017-11-21 14:00 | 59 | 58
2017-11-21 14:30 | 58 | 56
2017-11-21 15:00 | 58 | 56
2017-11-21 15:30 | 59 | 57
2017-11-21 16:00 | 59 | 58
2017-11-21 16:30 | 60 | 59
2017-11-21 17:00 | 61 | 59
2017-11-21 17:30 | 61 | 59
2017-11-21 18:00 | 60 | 58
2017-11-21 18:30 | 61 | 60
2017-11-21 19:00 | 63 | 61
2017-11-21 19:30 | 62 | 60
2017-11-21 20:00 | 62 | 60
2017-11-21 20:30 | 62 | 60
2017-11-21 21:00 | 57 | 56
2017-11-21 21:30 | 58 | 57
2017-11-21 22:00 | 57 | 56
2017-11-21 22:30 | 57 | 55
2017-11-21 23:00 | 54 | 54
2017-11-21 23:30 | 53 | 53
2017-11-22 | 53 | 53
2017-11-22 00:30 | 53 | 52
2017-11-22 01:00 | 52 | 52
2017-11-22 01:30 | 52 | 52
2017-11-22 02:00 | 53 | 53
2017-11-22 02:30 | 54 | 54
2017-11-22 03:00 | 53 | 53
2017-11-22 03:30 | 54 | 53
2017-11-22 04:00 | 53 | 52
2017-11-22 04:30 | 52 | 52
2017-11-22 05:00 | 52 | 51
2017-11-22 05:30 | 53 | 52
2017-11-22 06:00 | 53 | 52
2017-11-22 06:30 | 54 | 53
2017-11-22 07:00 | 56 | 56
2017-11-22 07:30 | 58 | 58
2017-11-22 08:00 | 56 | 55
2017-11-22 08:30 | 52 | 51
2017-11-22 09:00 | 51 | 50
2017-11-22 09:30 | 52 | 51
2017-11-22 10:00 | 52 | 51
2017-11-22 10:30 | 54 | 53
2017-11-22 11:00 | 53 | 53
2017-11-22 11:30 | 55 | 54
2017-11-22 12:00 | 55 | 54
2017-11-22 12:30 | 55 | 55
2017-11-22 13:00 | 61 | 60
2017-11-22 13:30 | 64 | 63
2017-11-22 14:00 | 65 | 64
2017-11-22 14:30 | 64 | 64
2017-11-22 15:00 | 63 | 62
2017-11-22 15:30 | 60 | 60
2017-11-22 16:00 | 61 | 61
2017-11-22 16:30 | 62 | 61
2017-11-22 17:00 | 67 | 66
2017-11-22 17:30 | 68 | 67
2017-11-22 18:00 | 69 | 68
2017-11-22 18:30 | 68 | 67
2017-11-22 19:00 | 67 | 66
2017-11-22 19:30 | 65 | 64
2017-11-22 20:00 | 65 | 64
2017-11-22 20:30 | 64 | 63
2017-11-22 21:00 | 62 | 62
2017-11-22 21:30 | 61 | 61
2017-11-22 22:00 | 60 | 60
2017-11-22 22:30 | 58 | 57
2017-11-22 23:00 | 57 | 56
2017-11-22 23:30 | 56 | 55
2017-11-23 | 56 | 56
2017-11-23 00:30 | 55 | 55
2017-11-23 01:00 | 55 | 55
2017-11-23 01:30 | 55 | 55
2017-11-23 02:00 | 55 | 54
2017-11-23 02:30 | 56 | 55
2017-11-23 03:00 | 56 | 55
2017-11-23 03:30 | 56 | 56
2017-11-23 04:00 | 56 | 56
2017-11-23 04:30 | 55 | 55
2017-11-23 05:00 | 57 | 57
2017-11-23 05:30 | 59 | 58
2017-11-23 06:00 | 57 | 57
2017-11-23 06:30 | 58 | 58
2017-11-23 07:00 | 58 | 58
2017-11-23 07:30 | 60 | 60
2017-11-23 08:00 | 60 | 60
2017-11-23 08:30 | 61 | 61
2017-11-23 09:00 | 61 | 61
2017-11-23 09:30 | 59 | 59
2017-11-23 10:00 | 59 | 59
2017-11-23 10:30 | 61 | 61
2017-11-23 11:00 | 62 | 62
2017-11-23 11:30 | 61 | 61
2017-11-23 12:00 | 61 | 61
2017-11-23 12:30 | 61 | 61
2017-11-23 13:00 | 62 | 62
2017-11-23 13:30 | 61 | 61
2017-11-23 14:00 | 59 | 59
2017-11-23 14:30 | 63 | 63
2017-11-23 15:00 | 64 | 64
2017-11-23 15:30 | 64 | 64
2017-11-23 16:00 | 67 | 66
2017-11-23 16:30 | 68 | 67
2017-11-23 17:00 | 68 | 67
2017-11-23 17:30 | 67 | 66
2017-11-23 18:00 | 66 | 65
2017-11-23 18:30 | 67 | 66
2017-11-23 19:00 | 67 | 66
2017-11-23 19:30 | 67 | 67
2017-11-23 20:00 | 67 | 67
2017-11-23 20:30 | 67 | 66
2017-11-23 21:00 | 66 | 65
2017-11-23 21:30 | 64 | 64
2017-11-23 22:00 | 63 | 63
2017-11-23 22:30 | 62 | 61
2017-11-23 23:00 | 59 | 59
2017-11-23 23:30 | 58 | 58
2017-11-24 | 58 | 58
2017-11-24 00:30 | 58 | 57
2017-11-24 01:00 | 56 | 56
2017-11-24 01:30 | 57 | 56
2017-11-24 02:00 | 57 | 56
2017-11-24 02:30 | 57 | 57
2017-11-24 03:00 | 57 | 57
2017-11-24 03:30 | 56 | 56
2017-11-24 04:00 | 56 | 56
2017-11-24 04:30 | 56 | 56
2017-11-24 05:00 | 57 | 56
2017-11-24 05:30 | 57 | 57
2017-11-24 06:00 | 58 | 58
2017-11-24 06:30 | 59 | 59
2017-11-24 07:00 | 61 | 61
2017-11-24 07:30 | 64 | 64
2017-11-24 08:00 | 64 | 64
2017-11-24 08:30 | 63 | 62
2017-11-24 09:00 | 60 | 59
2017-11-24 09:30 | 60 | 59
2017-11-24 10:00 | 60 | 60
2017-11-24 10:30 | 61 | 61
2017-11-24 11:00 | 58 | 58
2017-11-24 11:30 | 59 | 59
2017-11-24 12:00 | 64 | 63
2017-11-24 12:30 | 67 | 62
2017-11-24 13:00 | 66 | 60
2017-11-24 13:30 | 66 | 60
2017-11-24 14:00 | 68 | 62
2017-11-24 14:30 | 72 | 65
2017-11-24 15:00 | 72 | 65
2017-11-24 15:30 | 73 | 67
2017-11-24 16:00 | 75 | 68
2017-11-24 16:30 | 76 | 68
2017-11-24 17:00 | 76 | 69
2017-11-24 17:30 | 76 | 69
2017-11-24 18:00 | 78 | 70
2017-11-24 18:30 | 78 | 70
2017-11-24 19:00 | 78 | 70
2017-11-24 19:30 | 79 | 71
2017-11-24 20:00 | 78 | 71
2017-11-24 20:30 | 75 | 68
2017-11-24 21:00 | 75 | 68
2017-11-24 21:30 | 75 | 67
2017-11-24 22:00 | 75 | 68
2017-11-24 22:30 | 75 | 66
2017-11-24 23:00 | 73 | 64
2017-11-24 23:30 | 70 | 64
2017-11-25 | 59 | 58
2017-11-25 00:30 | 55 | 55
2017-11-25 01:00 | 55 | 54
2017-11-25 01:30 | 54 | 54
2017-11-25 02:00 | 55 | 55
2017-11-25 02:30 | 54 | 54
2017-11-25 03:00 | 54 | 53
2017-11-25 03:30 | 54 | 53
2017-11-25 04:00 | 53 | 52
2017-11-25 04:30 | 53 | 53
2017-11-25 05:00 | 53 | 53
2017-11-25 05:30 | 54 | 53
2017-11-25 06:00 | 54 | 53
2017-11-25 06:30 | 53 | 53
2017-11-25 07:00 | 54 | 54
2017-11-25 07:30 | 55 | 55
2017-11-25 08:00 | 55 | 55
2017-11-25 08:30 | 56 | 56
2017-11-25 09:00 | 57 | 57
2017-11-25 09:30 | 56 | 56
2017-11-25 10:00 | 56 | 56
2017-11-25 10:30 | 56 | 56
2017-11-25 11:00 | 57 | 57
2017-11-25 11:30 | 56 | 56
2017-11-25 12:00 | 56 | 56
2017-11-25 12:30 | 56 | 56
2017-11-25 13:00 | 57 | 57
2017-11-25 13:30 | 59 | 58
2017-11-25 14:00 | 61 | 61
2017-11-25 14:30 | 62 | 62
2017-11-25 15:00 | 68 | 62
2017-11-25 15:30 | 70 | 62
2017-11-25 16:00 | 71 | 64
2017-11-25 16:30 | 73 | 66
2017-11-25 17:00 | 74 | 67
2017-11-25 17:30 | 75 | 68
2017-11-25 18:00 | 71 | 65
2017-11-25 18:30 | 69 | 62
2017-11-25 19:00 | 70 | 63
2017-11-25 19:30 | 69 | 62
2017-11-25 20:00 | 69 | 62
2017-11-25 20:30 | 68 | 61
2017-11-25 21:00 | 69 | 61
2017-11-25 21:30 | 68 | 61
2017-11-25 22:00 | 67 | 59
2017-11-25 22:30 | 67 | 59
2017-11-25 23:00 | 65 | 57
2017-11-25 23:30 | 58 | 56
2017-11-26 | 56 | 54
2017-11-26 00:30 | 56 | 54
2017-11-26 01:00 | 57 | 54
2017-11-26 01:30 | 56 | 53
2017-11-26 02:00 | 55 | 53
2017-11-26 02:30 | 55 | 53
2017-11-26 03:00 | 53 | 52
2017-11-26 03:30 | 53 | 52
2017-11-26 04:00 | 53 | 52
2017-11-26 04:30 | 53 | 52
2017-11-26 05:00 | 53 | 52
2017-11-26 05:30 | 53 | 52
2017-11-26 06:00 | 52 | 50
2017-11-26 06:30 | 51 | 50
2017-11-26 07:00 | 52 | 51
2017-11-26 07:30 | 53 | 52
2017-11-26 08:00 | 54 | 53
2017-11-26 08:30 | 54 | 54
2017-11-26 09:00 | 55 | 54
2017-11-26 09:30 | 55 | 55
2017-11-26 10:00 | 54 | 54
2017-11-26 10:30 | 55 | 55
2017-11-26 11:00 | 56 | 55
2017-11-26 11:30 | 55 | 54
2017-11-26 12:00 | 55 | 55
2017-11-26 12:30 | 59 | 58
2017-11-26 13:00 | 61 | 60
2017-11-26 13:30 | 61 | 60
2017-11-26 14:00 | 61 | 60
2017-11-26 14:30 | 60 | 59
2017-11-26 15:00 | 61 | 60
2017-11-26 15:30 | 62 | 61
2017-11-26 16:00 | 60 | 59
2017-11-26 16:30 | 62 | 61
2017-11-26 17:00 | 63 | 63
2017-11-26 17:30 | 66 | 65
2017-11-26 18:00 | 65 | 64
2017-11-26 18:30 | 63 | 62
2017-11-26 19:00 | 64 | 63
2017-11-26 19:30 | 64 | 63
2017-11-26 20:00 | 63 | 63
2017-11-26 20:30 | 46 | 38
2017-11-26 21:00 | 44 | 24
2017-11-26 21:30 | 49 | 42
2017-11-26 22:00 | 57 | 55
2017-11-26 22:30 | 59 | 57
2017-11-26 23:00 | 59 | 57
2017-11-26 23:30 | 58 | 57
2017-11-27 | 57 | 56
2017-11-27 00:30 | 57 | 55
2017-11-27 01:00 | 57 | 55
2017-11-27 01:30 | 57 | 55
2017-11-27 02:00 | 57 | 55
2017-11-27 02:30 | 57 | 55
2017-11-27 03:00 | 57 | 54
2017-11-27 03:30 | 56 | 54
2017-11-27 04:00 | 56 | 54
2017-11-27 04:30 | 57 | 55
2017-11-27 05:00 | 59 | 57
2017-11-27 05:30 | 61 | 58
2017-11-27 06:00 | 60 | 57
2017-11-27 06:30 | 59 | 56
2017-11-27 07:00 | 62 | 60
2017-11-27 07:30 | 62 | 60
2017-11-27 08:00 | 61 | 60
2017-11-27 08:30 | 61 | 60
2017-11-27 09:00 | 61 | 60
2017-11-27 09:30 | 61 | 61
2017-11-27 10:00 | 61 | 61
2017-11-27 10:30 | 62 | 61
2017-11-27 11:00 | 63 | 62
2017-11-27 11:30 | 61 | 61
2017-11-27 12:00 | 61 | 61
2017-11-27 12:30 | 61 | 60
2017-11-27 13:00 | 61 | 60
2017-11-27 13:30 | 60 | 59
2017-11-27 14:00 | 61 | 60
2017-11-27 14:30 | 61 | 60
2017-11-27 15:00 | 62 | 61
2017-11-27 15:30 | 65 | 64
2017-11-27 16:00 | 66 | 65
2017-11-27 16:30 | 66 | 65
2017-11-27 17:00 | 67 | 66
2017-11-27 17:30 | 67 | 66
2017-11-27 18:00 | 67 | 66
2017-11-27 18:30 | 67 | 66
2017-11-27 19:00 | 69 | 68
2017-11-27 19:30 | 69 | 68
2017-11-27 20:00 | 68 | 67
2017-11-27 20:30 | 67 | 66
2017-11-27 21:00 | 66 | 64
2017-11-27 21:30 | 64 | 63
2017-11-27 22:00 | 63 | 61
2017-11-27 22:30 | 62 | 60
2017-11-27 23:00 | 60 | 59
2017-11-27 23:30 | 60 | 58
2017-11-28 | 61 | 60
2017-11-28 00:30 | 59 | 58
2017-11-28 01:00 | 59 | 58
2017-11-28 01:30 | 58 | 57
2017-11-28 02:00 | 59 | 57
2017-11-28 02:30 | 59 | 57
2017-11-28 03:00 | 58 | 57
2017-11-28 03:30 | 57 | 55
2017-11-28 04:00 | 57 | 55
2017-11-28 04:30 | 57 | 55
2017-11-28 05:00 | 57 | 55
2017-11-28 05:30 | 57 | 55
2017-11-28 06:00 | 57 | 55
2017-11-28 06:30 | 58 | 57
2017-11-28 07:00 | 59 | 57
2017-11-28 07:30 | 60 | 59
2017-11-28 08:00 | 60 | 60
2017-11-28 08:30 | 60 | 59
2017-11-28 09:00 | 62 | 61
2017-11-28 09:30 | 63 | 63
2017-11-28 10:00 | 61 | 61
2017-11-28 10:30 | 60 | 60
2017-11-28 11:00 | 62 | 62
2017-11-28 11:30 | 62 | 62
2017-11-28 12:00 | 62 | 62
2017-11-28 12:30 | 63 | 62
2017-11-28 13:00 | 63 | 63
2017-11-28 13:30 | 61 | 60
2017-11-28 14:00 | 60 | 59
2017-11-28 14:30 | 58 | 58
2017-11-28 15:00 | 59 | 58
2017-11-28 15:30 | 60 | 59
2017-11-28 16:00 | 59 | 58
2017-11-28 16:30 | 59 | 58
2017-11-28 17:00 | 59 | 58
2017-11-28 17:30 | 60 | 59
2017-11-28 18:00 | 59 | 58
2017-11-28 18:30 | 60 | 59
2017-11-28 19:00 | 62 | 61
2017-11-28 19:30 | 61 | 60
2017-11-28 20:00 | 60 | 59
2017-11-28 20:30 | 60 | 59
2017-11-28 21:00 | 48 | 46
2017-11-28 21:30 | 42 | 36
2017-11-28 22:00 | 43 | 39
2017-11-28 22:30 | 51 | 50
2017-11-28 23:00 | 55 | 54
2017-11-28 23:30 | 54 | 53
2017-11-29 | 53 | 52
2017-11-29 00:30 | 53 | 52
2017-11-29 01:00 | 53 | 53
2017-11-29 01:30 | 54 | 54
2017-11-29 02:00 | 53 | 53
2017-11-29 02:30 | 53 | 53
2017-11-29 03:00 | 54 | 53
2017-11-29 03:30 | 52 | 52
2017-11-29 04:00 | 52 | 51
2017-11-29 04:30 | 52 | 51
2017-11-29 05:00 | 53 | 52
2017-11-29 05:30 | 54 | 53
2017-11-29 06:00 | 53 | 53
2017-11-29 06:30 | 54 | 53
2017-11-29 07:00 | 55 | 55
2017-11-29 07:30 | 59 | 58
2017-11-29 08:00 | 59 | 58
2017-11-29 08:30 | 60 | 59
2017-11-29 09:00 | 60 | 59
2017-11-29 09:30 | 60 | 60
2017-11-29 10:00 | 60 | 60
2017-11-29 10:30 | 59 | 58
2017-11-29 11:00 | 58 | 57
2017-11-29 11:30 | 58 | 57
2017-11-29 12:00 | 56 | 56
2017-11-29 12:30 | 53 | 52
2017-11-29 13:00 | 58 | 56
2017-11-29 13:30 | 57 | 55
2017-11-29 14:00 | 56 | 54
2017-11-29 14:30 | 58 | 57
2017-11-29 15:00 | 54 | 53
2017-11-29 15:30 | 55 | 54
2017-11-29 16:00 | 62 | 62
2017-11-29 16:30 | 57 | 56
2017-11-29 17:00 | 55 | 51
2017-11-29 17:30 | 63 | 62
2017-11-29 18:00 | 64 | 64
2017-11-29 18:30 | 67 | 66
2017-11-29 19:00 | 68 | 67
2017-11-29 19:30 | 69 | 68
2017-11-29 20:00 | 69 | 68
2017-11-29 20:30 | 69 | 68
2017-11-29 21:00 | 69 | 68
2017-11-29 21:30 | 69 | 68
2017-11-29 22:00 | 67 | 65
2017-11-29 22:30 | 66 | 64
2017-11-29 23:00 | 65 | 64
2017-11-29 23:30 | 64 | 63
2017-11-30 | 62 | 62
2017-11-30 00:30 | 61 | 61
2017-11-30 01:00 | 62 | 61
2017-11-30 01:30 | 60 | 60
2017-11-30 02:00 | 60 | 60
2017-11-30 02:30 | 60 | 60
2017-11-30 03:00 | 61 | 60
2017-11-30 03:30 | 60 | 60
2017-11-30 04:00 | 59 | 59
2017-11-30 04:30 | 61 | 60
2017-11-30 05:00 | 60 | 60
2017-11-30 05:30 | 59 | 59
2017-11-30 06:00 | 60 | 59
2017-11-30 06:30 | 60 | 60
2017-11-30 07:00 | 61 | 61
2017-11-30 07:30 | 62 | 62
2017-11-30 08:00 | 65 | 65
2017-11-30 08:30 | 66 | 66
2017-11-30 09:00 | 66 | 65
2017-11-30 09:30 | 66 | 66
2017-11-30 10:00 | 66 | 65
2017-11-30 10:30 | 65 | 65
2017-11-30 11:00 | 66 | 65
2017-11-30 11:30 | 66 | 66
2017-11-30 12:00 | 67 | 67
2017-11-30 12:30 | 66 | 65
2017-11-30 13:00 | 63 | 62
2017-11-30 13:30 | 68 | 67
2017-11-30 14:00 | 66 | 64
2017-11-30 14:30 | 65 | 63
2017-11-30 15:00 | 67 | 65
2017-11-30 15:30 | 69 | 68
2017-11-30 16:00 | 67 | 65
2017-11-30 16:30 | 68 | 65
2017-11-30 17:00 | 72 | 70
2017-11-30 17:30 | 75 | 73
2017-11-30 18:00 | 77 | 75
2017-11-30 18:30 | 76 | 75
2017-11-30 19:00 | 77 | 75
2017-11-30 19:30 | 77 | 76
2017-11-30 20:00 | 77 | 76
2017-11-30 20:30 | 77 | 76
2017-11-30 21:00 | 76 | 74
2017-11-30 21:30 | 74 | 72
2017-11-30 22:00 | 73 | 71
2017-11-30 22:30 | 74 | 72
2017-11-30 23:00 | 68 | 67
2017-11-30 23:30 | 66 | 65
2017-12-01 | 66 | 65
2017-12-01 00:30 | 64 | 63
2017-12-01 01:00 | 63 | 61
2017-12-01 01:30 | 63 | 62
2017-12-01 02:00 | 63 | 62
2017-12-01 02:30 | 64 | 63
2017-12-01 03:00 | 63 | 61
2017-12-01 03:30 | 63 | 61
2017-12-01 04:00 | 62 | 61
2017-12-01 04:30 | 61 | 60
2017-12-01 05:00 | 63 | 61
2017-12-01 05:30 | 62 | 61
2017-12-01 06:00 | 62 | 61
2017-12-01 06:30 | 64 | 62
2017-12-01 07:00 | 64 | 63
2017-12-01 07:30 | 66 | 65
2017-12-01 08:00 | 67 | 66
2017-12-01 08:30 | 60 | 57
2017-12-01 09:00 | 58 | 55
2017-12-01 09:30 | 64 | 63
2017-12-01 10:00 | 65 | 64
2017-12-01 10:30 | 65 | 65
2017-12-01 11:00 | 66 | 65
2017-12-01 11:30 | 60 | 58
2017-12-01 12:00 | 63 | 62
2017-12-01 12:30 | 64 | 63
2017-12-01 13:00 | 69 | 68
2017-12-01 13:30 | 71 | 70
2017-12-01 14:00 | 72 | 71
2017-12-01 14:30 | 68 | 67
2017-12-01 15:00 | 70 | 69
2017-12-01 15:30 | 72 | 64
2017-12-01 16:00 | 73 | 67
2017-12-01 16:30 | 74 | 73
2017-12-01 17:00 | 74 | 73
2017-12-01 17:30 | 75 | 74
2017-12-01 18:00 | 75 | 74
2017-12-01 18:30 | 77 | 76
2017-12-01 19:00 | 79 | 78
2017-12-01 19:30 | 79 | 78
2017-12-01 20:00 | 80 | 79
2017-12-01 20:30 | 79 | 78
2017-12-01 21:00 | 72 | 71
2017-12-01 21:30 | 70 | 69
2017-12-01 22:00 | 68 | 67
2017-12-01 22:30 | 69 | 68
2017-12-01 23:00 | 66 | 65
2017-12-01 23:30 | 66 | 65
2017-12-02 | 67 | 66
2017-12-02 00:30 | 67 | 66
2017-12-02 01:00 | 66 | 65
2017-12-02 01:30 | 66 | 65
2017-12-02 02:00 | 66 | 65
2017-12-02 02:30 | 67 | 65
2017-12-02 03:00 | 65 | 64
2017-12-02 03:30 | 65 | 64
2017-12-02 04:00 | 65 | 65
2017-12-02 04:30 | 65 | 64
2017-12-02 05:00 | 65 | 64
2017-12-02 05:30 | 64 | 64
2017-12-02 06:00 | 63 | 63
2017-12-02 06:30 | 64 | 64
2017-12-02 07:00 | 66 | 65
2017-12-02 07:30 | 68 | 67
2017-12-02 08:00 | 69 | 68
2017-12-02 08:30 | 69 | 68
2017-12-02 09:00 | 69 | 68
2017-12-02 09:30 | 68 | 68
2017-12-02 10:00 | 67 | 66
2017-12-02 10:30 | 69 | 69
2017-12-02 11:00 | 70 | 69
2017-12-02 11:30 | 68 | 67
2017-12-02 12:00 | 69 | 68
2017-12-02 12:30 | 69 | 69
2017-12-02 13:00 | 68 | 67
2017-12-02 13:30 | 69 | 69
2017-12-02 14:00 | 69 | 68
2017-12-02 14:30 | 69 | 68
2017-12-02 15:00 | 70 | 69
2017-12-02 15:30 | 69 | 69
2017-12-02 16:00 | 70 | 69
2017-12-02 16:30 | 72 | 71
2017-12-02 17:00 | 71 | 70
2017-12-02 17:30 | 71 | 71
2017-12-02 18:00 | 72 | 71
2017-12-02 18:30 | 72 | 71
2017-12-02 19:00 | 72 | 71
2017-12-02 19:30 | 74 | 73
2017-12-02 20:00 | 73 | 73
2017-12-02 20:30 | 73 | 72
2017-12-02 21:00 | 72 | 71
2017-12-02 21:30 | 70 | 70
2017-12-02 22:00 | 69 | 69
2017-12-02 22:30 | 67 | 66
2017-12-02 23:00 | 68 | 67
2017-12-02 23:30 | 66 | 66
2017-12-03 | 66 | 65
2017-12-03 00:30 | 66 | 65
2017-12-03 01:00 | 64 | 64
2017-12-03 01:30 | 65 | 64
2017-12-03 02:00 | 65 | 64
2017-12-03 02:30 | 63 | 63
2017-12-03 03:00 | 63 | 63
2017-12-03 03:30 | 64 | 64
2017-12-03 04:00 | 64 | 64
2017-12-03 04:30 | 64 | 63
2017-12-03 05:00 | 63 | 63
2017-12-03 05:30 | 63 | 63
2017-12-03 06:00 | 63 | 62
2017-12-03 06:30 | 63 | 62
2017-12-03 07:00 | 62 | 62
2017-12-03 07:30 | 65 | 64
2017-12-03 08:00 | 65 | 65
2017-12-03 08:30 | 65 | 64
2017-12-03 09:00 | 67 | 66
2017-12-03 09:30 | 66 | 65
2017-12-03 10:00 | 66 | 66
2017-12-03 10:30 | 67 | 66
2017-12-03 11:00 | 66 | 65
2017-12-03 11:30 | 66 | 65
2017-12-03 12:00 | 66 | 65
2017-12-03 12:30 | 66 | 65
2017-12-03 13:00 | 68 | 67
2017-12-03 13:30 | 68 | 67
2017-12-03 14:00 | 68 | 68
2017-12-03 14:30 | 69 | 68
2017-12-03 15:00 | 68 | 68
2017-12-03 15:30 | 69 | 68
2017-12-03 16:00 | 69 | 68
2017-12-03 16:30 | 69 | 68
2017-12-03 17:00 | 70 | 69
2017-12-03 17:30 | 71 | 70
2017-12-03 18:00 | 72 | 72
2017-12-03 18:30 | 74 | 73
2017-12-03 19:00 | 70 | 69
2017-12-03 19:30 | 75 | 74
2017-12-03 20:00 | 74 | 74
2017-12-03 20:30 | 75 | 75
2017-12-03 21:00 | 74 | 73
2017-12-03 21:30 | 71 | 71
2017-12-03 22:00 | 70 | 68
2017-12-03 22:30 | 67 | 66
2017-12-03 23:00 | 67 | 66
2017-12-03 23:30 | 67 | 66
2017-12-04 | 69 | 68
2017-12-04 00:30 | 68 | 67
2017-12-04 01:00 | 66 | 65
2017-12-04 01:30 | 65 | 64
2017-12-04 02:00 | 64 | 63
2017-12-04 02:30 | 63 | 61
2017-12-04 03:00 | 62 | 61
2017-12-04 03:30 | 62 | 60
2017-12-04 04:00 | 62 | 61
2017-12-04 04:30 | 63 | 62
2017-12-04 05:00 | 63 | 62
2017-12-04 05:30 | 62 | 61
2017-12-04 06:00 | 61 | 61
2017-12-04 06:30 | 62 | 62
2017-12-04 07:00 | 64 | 62
2017-12-04 07:30 | 63 | 62
2017-12-04 08:00 | 65 | 64
2017-12-04 08:30 | 66 | 65
2017-12-04 09:00 | 66 | 64
2017-12-04 09:30 | 59 | 58
2017-12-04 10:00 | 58 | 56
2017-12-04 10:30 | 58 | 56
2017-12-04 11:00 | 48 | 44
2017-12-04 11:30 | 46 | 40
2017-12-04 12:00 | 47 | 41
2017-12-04 12:30 | 47 | 41
2017-12-04 13:00 | 48 | 42
2017-12-04 13:30 | 53 | 49
2017-12-04 14:00 | 54 | 50
2017-12-04 14:30 | 53 | 49
2017-12-04 15:00 | 54 | 50
2017-12-04 15:30 | 55 | 51
2017-12-04 16:00 | 56 | 53
2017-12-04 16:30 | 58 | 55
2017-12-04 17:00 | 60 | 57
2017-12-04 17:30 | 60 | 57
2017-12-04 18:00 | 63 | 59
2017-12-04 18:30 | 64 | 61
2017-12-04 19:00 | 63 | 59
2017-12-04 19:30 | 63 | 59
2017-12-04 20:00 | 62 | 59
2017-12-04 20:30 | 59 | 55
2017-12-04 21:00 | 57 | 52
2017-12-04 21:30 | 56 | 50
2017-12-04 22:00 | 60 | 56
2017-12-04 22:30 | 57 | 53
2017-12-04 23:00 | 55 | 52
2017-12-04 23:30 | 52 | 50
2017-12-05 | 55 | 54
2017-12-05 00:30 | 59 | 58
2017-12-05 01:00 | 58 | 57
2017-12-05 01:30 | 57 | 56
2017-12-05 02:00 | 57 | 55
2017-12-05 02:30 | 56 | 54
2017-12-05 03:00 | 52 | 49
2017-12-05 03:30 | 51 | 48
2017-12-05 04:00 | 47 | 41
2017-12-05 04:30 | 46 | 40
2017-12-05 05:00 | 46 | 40
2017-12-05 05:30 | 46 | 40
2017-12-05 06:00 | 46 | 40
2017-12-05 06:30 | 47 | 41
2017-12-05 07:00 | 50 | 46
2017-12-05 07:30 | 56 | 52
2017-12-05 08:00 | 56 | 52
2017-12-05 08:30 | 55 | 52
2017-12-05 09:00 | 55 | 52
2017-12-05 09:30 | 54 | 51
2017-12-05 10:00 | 55 | 52
2017-12-05 10:30 | 55 | 52
2017-12-05 11:00 | 56 | 53
2017-12-05 11:30 | 61 | 58
2017-12-05 12:00 | 59 | 57
2017-12-05 12:30 | 58 | 56
2017-12-05 13:00 | 59 | 57
2017-12-05 13:30 | 61 | 59
2017-12-05 14:00 | 64 | 62
2017-12-05 14:30 | 70 | 69
2017-12-05 15:00 | 71 | 71
2017-12-05 15:30 | 71 | 70
2017-12-05 16:00 | 73 | 72
2017-12-05 16:30 | 75 | 74
2017-12-05 17:00 | 51 | 44
2017-12-05 17:30 | 59 | 53
2017-12-05 18:00 | 63 | 58
2017-12-05 18:30 | 62 | 57
2017-12-05 19:00 | 62 | 57
2017-12-05 19:30 | 63 | 58
2017-12-05 20:00 | 63 | 58
2017-12-05 20:30 | 74 | 73
2017-12-05 21:00 | 75 | 75
2017-12-05 21:30 | 73 | 73
2017-12-05 22:00 | 72 | 71
2017-12-05 22:30 | 71 | 71
2017-12-05 23:00 | 69 | 68
2017-12-05 23:30 | 69 | 68
2017-12-06 | 67 | 67
2017-12-06 00:30 | 67 | 66
2017-12-06 01:00 | 66 | 65
2017-12-06 01:30 | 68 | 68
2017-12-06 02:00 | 68 | 68
2017-12-06 02:30 | 68 | 68
2017-12-06 03:00 | 68 | 68
2017-12-06 03:30 | 68 | 67
2017-12-06 04:00 | 68 | 67
2017-12-06 04:30 | 69 | 68
2017-12-06 05:00 | 68 | 68
2017-12-06 05:30 | 68 | 68
2017-12-06 06:00 | 66 | 65
2017-12-06 06:30 | 67 | 67
2017-12-06 07:00 | 69 | 69
2017-12-06 07:30 | 72 | 72
2017-12-06 08:00 | 75 | 74
2017-12-06 08:30 | 77 | 76
2017-12-06 09:00 | 77 | 76
2017-12-06 09:30 | 76 | 75
2017-12-06 10:00 | 74 | 73
2017-12-06 10:30 | 74 | 73
2017-12-06 11:00 | 75 | 75
2017-12-06 11:30 | 75 | 74
2017-12-06 12:00 | 74 | 73
2017-12-06 12:30 | 75 | 74
2017-12-06 13:00 | 75 | 74
2017-12-06 13:30 | 75 | 75
2017-12-06 14:00 | 76 | 76
2017-12-06 14:30 | 77 | 77
2017-12-06 15:00 | 78 | 78
2017-12-06 15:30 | 79 | 78
2017-12-06 16:00 | 80 | 80
2017-12-06 16:30 | 81 | 80
2017-12-06 17:00 | 81 | 81
2017-12-06 17:30 | 80 | 79
2017-12-06 18:00 | 80 | 79
2017-12-06 18:30 | 80 | 79
2017-12-06 19:00 | 80 | 79
2017-12-06 19:30 | 81 | 80
2017-12-06 20:00 | 81 | 80
2017-12-06 20:30 | 79 | 79
2017-12-06 21:00 | 78 | 78
2017-12-06 21:30 | 77 | 76
2017-12-06 22:00 | 73 | 72
2017-12-06 22:30 | 72 | 72
2017-12-06 23:00 | 70 | 70
2017-12-06 23:30 | 70 | 69
2017-12-07 | 68 | 68
2017-12-07 00:30 | 68 | 68
2017-12-07 01:00 | 67 | 67
2017-12-07 01:30 | 67 | 67
2017-12-07 02:00 | 67 | 67
2017-12-07 02:30 | 66 | 66
2017-12-07 03:00 | 66 | 66
2017-12-07 03:30 | 66 | 66
2017-12-07 04:00 | 66 | 65
2017-12-07 04:30 | 67 | 66
2017-12-07 05:00 | 67 | 67
2017-12-07 05:30 | 67 | 67
2017-12-07 06:00 | 66 | 66
2017-12-07 06:30 | 67 | 67
2017-12-07 07:00 | 69 | 68
2017-12-07 07:30 | 72 | 72
2017-12-07 08:00 | 72 | 72
2017-12-07 08:30 | 73 | 73
2017-12-07 09:00 | 73 | 73
2017-12-07 09:30 | 72 | 72
2017-12-07 10:00 | 74 | 74
2017-12-07 10:30 | 75 | 74
2017-12-07 11:00 | 75 | 75
2017-12-07 11:30 | 76 | 75
2017-12-07 12:00 | 75 | 75
2017-12-07 12:30 | 74 | 74
2017-12-07 13:00 | 73 | 73
2017-12-07 13:30 | 74 | 73
2017-12-07 14:00 | 74 | 73
2017-12-07 14:30 | 74 | 74
2017-12-07 15:00 | 74 | 74
2017-12-07 15:30 | 75 | 75
2017-12-07 16:00 | 76 | 76
2017-12-07 16:30 | 77 | 77
2017-12-07 17:00 | 74 | 74
2017-12-07 17:30 | 78 | 78
2017-12-07 18:00 | 77 | 77
2017-12-07 18:30 | 77 | 77
2017-12-07 19:00 | 77 | 77
2017-12-07 19:30 | 78 | 77
2017-12-07 20:00 | 79 | 79
2017-12-07 20:30 | 77 | 77
2017-12-07 21:00 | 77 | 76
2017-12-07 21:30 | 75 | 75
2017-12-07 22:00 | 73 | 73
2017-12-07 22:30 | 72 | 72
2017-12-07 23:00 | 70 | 70
2017-12-07 23:30 | 69 | 69
2017-12-08 | 68 | 68
2017-12-08 00:30 | 68 | 68
2017-12-08 01:00 | 68 | 67
2017-12-08 01:30 | 68 | 67
2017-12-08 02:00 | 67 | 66
2017-12-08 02:30 | 67 | 66
2017-12-08 03:00 | 67 | 66
2017-12-08 03:30 | 66 | 66
2017-12-08 04:00 | 66 | 66
2017-12-08 04:30 | 66 | 66
2017-12-08 05:00 | 66 | 65
2017-12-08 05:30 | 66 | 66
2017-12-08 06:00 | 65 | 65
2017-12-08 06:30 | 67 | 67
2017-12-08 07:00 | 70 | 69
2017-12-08 07:30 | 72 | 72
2017-12-08 08:00 | 72 | 72
2017-12-08 08:30 | 71 | 71
2017-12-08 09:00 | 73 | 72
2017-12-08 09:30 | 73 | 72
2017-12-08 10:00 | 72 | 71
2017-12-08 10:30 | 71 | 70
2017-12-08 11:00 | 70 | 69
2017-12-08 11:30 | 69 | 68
2017-12-08 12:00 | 67 | 66
2017-12-08 12:30 | 64 | 63
2017-12-08 13:00 | 71 | 70
2017-12-08 13:30 | 73 | 73
2017-12-08 14:00 | 72 | 72
2017-12-08 14:30 | 72 | 72
2017-12-08 15:00 | 72 | 72
2017-12-08 15:30 | 73 | 73
2017-12-08 16:00 | 75 | 75
2017-12-08 16:30 | 76 | 76
2017-12-08 17:00 | 75 | 75
2017-12-08 17:30 | 75 | 75
2017-12-08 18:00 | 76 | 76
2017-12-08 18:30 | 75 | 75
2017-12-08 19:00 | 76 | 75
2017-12-08 19:30 | 77 | 76
2017-12-08 20:00 | 77 | 76
2017-12-08 20:30 | 78 | 77
2017-12-08 21:00 | 74 | 74
2017-12-08 21:30 | 73 | 73
2017-12-08 22:00 | 73 | 72
2017-12-08 22:30 | 72 | 71
2017-12-08 23:00 | 70 | 69
2017-12-08 23:30 | 69 | 68
2017-12-09 | 67 | 67
2017-12-09 00:30 | 67 | 67
2017-12-09 01:00 | 66 | 66
2017-12-09 01:30 | 66 | 66
2017-12-09 02:00 | 65 | 65
2017-12-09 02:30 | 65 | 65
2017-12-09 03:00 | 65 | 65
2017-12-09 03:30 | 65 | 65
2017-12-09 04:00 | 64 | 64
2017-12-09 04:30 | 63 | 63
2017-12-09 05:00 | 65 | 64
2017-12-09 05:30 | 65 | 64
2017-12-09 06:00 | 63 | 63
2017-12-09 06:30 | 64 | 64
2017-12-09 07:00 | 65 | 65
2017-12-09 07:30 | 67 | 66
2017-12-09 08:00 | 67 | 67
2017-12-09 08:30 | 68 | 67
2017-12-09 09:00 | 69 | 69
2017-12-09 09:30 | 69 | 69
2017-12-09 10:00 | 70 | 69
2017-12-09 10:30 | 69 | 68
2017-12-09 11:00 | 69 | 68
2017-12-09 11:30 | 67 | 67
2017-12-09 12:00 | 69 | 69
2017-12-09 12:30 | 69 | 69
2017-12-09 13:00 | 70 | 70
2017-12-09 13:30 | 70 | 70
2017-12-09 14:00 | 70 | 70
2017-12-09 14:30 | 71 | 71
2017-12-09 15:00 | 72 | 72
2017-12-09 15:30 | 72 | 71
2017-12-09 16:00 | 73 | 73
2017-12-09 16:30 | 73 | 73
2017-12-09 17:00 | 73 | 73
2017-12-09 17:30 | 74 | 74
2017-12-09 18:00 | 74 | 74
2017-12-09 18:30 | 74 | 73
2017-12-09 19:00 | 74 | 74
2017-12-09 19:30 | 75 | 75
2017-12-09 20:00 | 74 | 74
2017-12-09 20:30 | 73 | 73
2017-12-09 21:00 | 73 | 72
2017-12-09 21:30 | 72 | 72
2017-12-09 22:00 | 71 | 71
2017-12-09 22:30 | 71 | 71
2017-12-09 23:00 | 68 | 68
2017-12-09 23:30 | 67 | 67
2017-12-10 | 67 | 67
2017-12-10 00:30 | 66 | 66
2017-12-10 01:00 | 65 | 65
2017-12-10 01:30 | 65 | 65
2017-12-10 02:00 | 64 | 64
2017-12-10 02:30 | 64 | 64
2017-12-10 03:00 | 63 | 63
2017-12-10 03:30 | 63 | 63
2017-12-10 04:00 | 63 | 63
2017-12-10 04:30 | 64 | 64
2017-12-10 05:00 | 64 | 64
2017-12-10 05:30 | 64 | 63
2017-12-10 06:00 | 62 | 61
2017-12-10 06:30 | 63 | 63
2017-12-10 07:00 | 64 | 64
2017-12-10 07:30 | 66 | 65
2017-12-10 08:00 | 67 | 66
2017-12-10 08:30 | 69 | 68
2017-12-10 09:00 | 69 | 68
2017-12-10 09:30 | 69 | 69
2017-12-10 10:00 | 70 | 69
2017-12-10 10:30 | 71 | 70
2017-12-10 11:00 | 71 | 70
2017-12-10 11:30 | 71 | 70
2017-12-10 12:00 | 71 | 70
2017-12-10 12:30 | 71 | 70
2017-12-10 13:00 | 72 | 71
2017-12-10 13:30 | 72 | 71
2017-12-10 14:00 | 73 | 72
2017-12-10 14:30 | 73 | 72
2017-12-10 15:00 | 74 | 73
2017-12-10 15:30 | 75 | 74
2017-12-10 16:00 | 76 | 75
2017-12-10 16:30 | 76 | 76
2017-12-10 17:00 | 77 | 77
2017-12-10 17:30 | 77 | 76
2017-12-10 18:00 | 78 | 77
2017-12-10 18:30 | 78 | 77
2017-12-10 19:00 | 78 | 77
2017-12-10 19:30 | 79 | 78
2017-12-10 20:00 | 79 | 78
2017-12-10 20:30 | 77 | 76
2017-12-10 21:00 | 75 | 75
2017-12-10 21:30 | 74 | 73
2017-12-10 22:00 | 73 | 73
2017-12-10 22:30 | 71 | 71
2017-12-10 23:00 | 70 | 69
2017-12-10 23:30 | 68 | 68
2017-12-11 | 67 | 67
2017-12-11 00:30 | 67 | 67
2017-12-11 01:00 | 67 | 66
2017-12-11 01:30 | 67 | 66
2017-12-11 02:00 | 66 | 66
2017-12-11 02:30 | 66 | 66
2017-12-11 03:00 | 66 | 65
2017-12-11 03:30 | 65 | 65
2017-12-11 04:00 | 66 | 65
2017-12-11 04:30 | 66 | 65
2017-12-11 05:00 | 66 | 66
2017-12-11 05:30 | 66 | 65
2017-12-11 06:00 | 65 | 65
2017-12-11 06:30 | 67 | 67
2017-12-11 07:00 | 68 | 67
2017-12-11 07:30 | 70 | 70
2017-12-11 08:00 | 71 | 71
2017-12-11 08:30 | 73 | 73
2017-12-11 09:00 | 73 | 73
2017-12-11 09:30 | 73 | 73
2017-12-11 10:00 | 72 | 72
2017-12-11 10:30 | 72 | 72
2017-12-11 11:00 | 71 | 71
2017-12-11 11:30 | 72 | 72
2017-12-11 12:00 | 71 | 71
2017-12-11 12:30 | 72 | 72
2017-12-11 13:00 | 71 | 71
2017-12-11 13:30 | 72 | 72
2017-12-11 14:00 | 74 | 74
2017-12-11 14:30 | 74 | 74
2017-12-11 15:00 | 75 | 74
2017-12-11 15:30 | 76 | 75
2017-12-11 16:00 | 76 | 76
2017-12-11 16:30 | 77 | 76
2017-12-11 17:00 | 78 | 78
2017-12-11 17:30 | 78 | 78
2017-12-11 18:00 | 77 | 77
2017-12-11 18:30 | 77 | 77
2017-12-11 19:00 | 77 | 76
2017-12-11 19:30 | 77 | 76
2017-12-11 20:00 | 76 | 75
2017-12-11 20:30 | 75 | 74
2017-12-11 21:00 | 74 | 73
2017-12-11 21:30 | 73 | 71
2017-12-11 22:00 | 71 | 69
2017-12-11 22:30 | 69 | 67
2017-12-11 23:00 | 67 | 66
2017-12-11 23:30 | 67 | 66
2017-12-12 | 67 | 66
2017-12-12 00:30 | 66 | 65
2017-12-12 01:00 | 65 | 64
2017-12-12 01:30 | 65 | 63
2017-12-12 02:00 | 64 | 63
2017-12-12 02:30 | 64 | 63
2017-12-12 03:00 | 64 | 63
2017-12-12 03:30 | 64 | 63
2017-12-12 04:00 | 64 | 63
2017-12-12 04:30 | 64 | 62
2017-12-12 05:00 | 64 | 62
2017-12-12 05:30 | 63 | 62
2017-12-12 06:00 | 63 | 61
2017-12-12 06:30 | 65 | 64
2017-12-12 07:00 | 67 | 67
2017-12-12 07:30 | 69 | 69
2017-12-12 08:00 | 70 | 70
2017-12-12 08:30 | 70 | 70
2017-12-12 09:00 | 71 | 70
2017-12-12 09:30 | 71 | 70
2017-12-12 10:00 | 71 | 70
2017-12-12 10:30 | 71 | 71
2017-12-12 11:00 | 71 | 70
2017-12-12 11:30 | 71 | 71
2017-12-12 12:00 | 72 | 71
2017-12-12 12:30 | 72 | 71
2017-12-12 13:00 | 71 | 71
2017-12-12 13:30 | 72 | 71
2017-12-12 14:00 | 72 | 71
2017-12-12 14:30 | 74 | 73
2017-12-12 15:00 | 75 | 74
2017-12-12 15:30 | 76 | 75
2017-12-12 16:00 | 78 | 76
2017-12-12 16:30 | 79 | 77
2017-12-12 17:00 | 78 | 77
2017-12-12 17:30 | 77 | 75
2017-12-12 18:00 | 77 | 75
2017-12-12 18:30 | 76 | 75
2017-12-12 19:00 | 77 | 75
2017-12-12 19:30 | 78 | 77
2017-12-12 20:00 | 78 | 77
2017-12-12 20:30 | 77 | 76
2017-12-12 21:00 | 77 | 76
2017-12-12 21:30 | 76 | 75
2017-12-12 22:00 | 75 | 73
2017-12-12 22:30 | 74 | 72
2017-12-12 23:00 | 72 | 71
2017-12-12 23:30 | 70 | 70
2017-12-13 | 69 | 69
2017-12-13 00:30 | 67 | 67
2017-12-13 01:00 | 67 | 67
2017-12-13 01:30 | 67 | 67
2017-12-13 02:00 | 66 | 66
2017-12-13 02:30 | 66 | 66
2017-12-13 03:00 | 67 | 67
2017-12-13 03:30 | 69 | 69
2017-12-13 04:00 | 72 | 72
2017-12-13 04:30 | 72 | 72
2017-12-13 05:00 | 72 | 72
2017-12-13 05:30 | 72 | 71
2017-12-13 06:00 | 72 | 71
2017-12-13 06:30 | 73 | 73
2017-12-13 07:00 | 73 | 73
2017-12-13 07:30 | 74 | 74
2017-12-13 08:00 | 74 | 74
2017-12-13 08:30 | 73 | 73
2017-12-13 09:00 | 71 | 71
2017-12-13 09:30 | 71 | 71
2017-12-13 10:00 | 70 | 70
2017-12-13 10:30 | 70 | 70
2017-12-13 11:00 | 70 | 70
2017-12-13 11:30 | 71 | 71
2017-12-13 12:00 | 72 | 72
2017-12-13 12:30 | 72 | 72
2017-12-13 13:00 | 71 | 71
2017-12-13 13:30 | 71 | 71
2017-12-13 14:00 | 72 | 72
2017-12-13 14:30 | 72 | 72
2017-12-13 15:00 | 72 | 72
2017-12-13 15:30 | 73 | 73
2017-12-13 16:00 | 73 | 73
2017-12-13 16:30 | 69 | 69
2017-12-13 17:00 | 68 | 67
2017-12-13 17:30 | 75 | 75
2017-12-13 18:00 | 77 | 77
2017-12-13 18:30 | 78 | 78
2017-12-13 19:00 | 79 | 79
2017-12-13 19:30 | 79 | 79
2017-12-13 20:00 | 79 | 79
2017-12-13 20:30 | 77 | 77
2017-12-13 21:00 | 77 | 77
2017-12-13 21:30 | 76 | 76
2017-12-13 22:00 | 74 | 74
2017-12-13 22:30 | 72 | 72
2017-12-13 23:00 | 70 | 70
2017-12-13 23:30 | 69 | 69
2017-12-14 | 66 | 65
2017-12-14 00:30 | 64 | 63
2017-12-14 01:00 | 64 | 63
2017-12-14 01:30 | 63 | 62
2017-12-14 02:00 | 63 | 62
2017-12-14 02:30 | 66 | 65
2017-12-14 03:00 | 67 | 66
2017-12-14 03:30 | 67 | 67
2017-12-14 04:00 | 66 | 66
2017-12-14 04:30 | 67 | 66
2017-12-14 05:00 | 66 | 66
2017-12-14 05:30 | 66 | 66
2017-12-14 06:00 | 65 | 65
2017-12-14 06:30 | 66 | 66
2017-12-14 07:00 | 68 | 68
2017-12-14 07:30 | 70 | 70
2017-12-14 08:00 | 71 | 71
2017-12-14 08:30 | 72 | 72
2017-12-14 09:00 | 75 | 75
2017-12-14 09:30 | 75 | 75
2017-12-14 10:00 | 75 | 75
2017-12-14 10:30 | 75 | 75
2017-12-14 11:00 | 71 | 71
2017-12-14 11:30 | 70 | 70
2017-12-14 12:00 | 71 | 71
2017-12-14 12:30 | 71 | 71
2017-12-14 13:00 | 72 | 72
2017-12-14 13:30 | 72 | 72
2017-12-14 14:00 | 71 | 71
2017-12-14 14:30 | 72 | 71
2017-12-14 15:00 | 72 | 72
2017-12-14 15:30 | 73 | 73
2017-12-14 16:00 | 72 | 72
2017-12-14 16:30 | 74 | 74
2017-12-14 17:00 | 73 | 73
2017-12-14 17:30 | 75 | 75
2017-12-14 18:00 | 74 | 74
2017-12-14 18:30 | 74 | 74
2017-12-14 19:00 | 74 | 74
2017-12-14 19:30 | 75 | 74
2017-12-14 20:00 | 76 | 76
2017-12-14 20:30 | 75 | 75
2017-12-14 21:00 | 75 | 75
2017-12-14 21:30 | 74 | 73
2017-12-14 22:00 | 73 | 73
2017-12-14 22:30 | 72 | 72
2017-12-14 23:00 | 70 | 70
2017-12-14 23:30 | 70 | 69
2017-12-15 | 70 | 69
2017-12-15 00:30 | 69 | 69
2017-12-15 01:00 | 68 | 68
2017-12-15 01:30 | 68 | 68
2017-12-15 02:00 | 68 | 67
2017-12-15 02:30 | 68 | 67
2017-12-15 03:00 | 67 | 66
2017-12-15 03:30 | 66 | 65
2017-12-15 04:00 | 67 | 66
2017-12-15 04:30 | 68 | 67
2017-12-15 05:00 | 67 | 66
2017-12-15 05:30 | 68 | 67
2017-12-15 06:00 | 67 | 66
2017-12-15 06:30 | 67 | 67
2017-12-15 07:00 | 69 | 69
2017-12-15 07:30 | 71 | 70
2017-12-15 08:00 | 72 | 71
2017-12-15 08:30 | 72 | 72
2017-12-15 09:00 | 72 | 71
2017-12-15 09:30 | 72 | 71
2017-12-15 10:00 | 71 | 71
2017-12-15 10:30 | 71 | 70
2017-12-15 11:00 | 71 | 71
2017-12-15 11:30 | 71 | 71
2017-12-15 12:00 | 70 | 70
2017-12-15 12:30 | 71 | 71
2017-12-15 13:00 | 72 | 72
2017-12-15 13:30 | 72 | 72
2017-12-15 14:00 | 70 | 70
2017-12-15 14:30 | 66 | 65
2017-12-15 15:00 | 70 | 69
2017-12-15 15:30 | 74 | 74
2017-12-15 16:00 | 75 | 75
2017-12-15 16:30 | 76 | 76
2017-12-15 17:00 | 74 | 73
2017-12-15 17:30 | 68 | 67
2017-12-15 18:00 | 74 | 74
2017-12-15 18:30 | 75 | 75
2017-12-15 19:00 | 75 | 75
2017-12-15 19:30 | 77 | 77
2017-12-15 20:00 | 77 | 77
2017-12-15 20:30 | 76 | 76
2017-12-15 21:00 | 76 | 76
2017-12-15 21:30 | 76 | 76
2017-12-15 22:00 | 75 | 75
2017-12-15 22:30 | 72 | 72
2017-12-15 23:00 | 71 | 70
2017-12-15 23:30 | 70 | 69
2017-12-16 | 69 | 68
2017-12-16 00:30 | 68 | 68
2017-12-16 01:00 | 69 | 68
2017-12-16 01:30 | 68 | 68
2017-12-16 02:00 | 68 | 68
2017-12-16 02:30 | 68 | 67
2017-12-16 03:00 | 67 | 66
2017-12-16 03:30 | 67 | 66
2017-12-16 04:00 | 67 | 67
2017-12-16 04:30 | 67 | 67
2017-12-16 05:00 | 67 | 67
2017-12-16 05:30 | 67 | 66
2017-12-16 06:00 | 65 | 65
2017-12-16 06:30 | 64 | 64
2017-12-16 07:00 | 65 | 65
2017-12-16 07:30 | 67 | 66
2017-12-16 08:00 | 68 | 67
2017-12-16 08:30 | 68 | 68
2017-12-16 09:00 | 68 | 68
2017-12-16 09:30 | 68 | 68
2017-12-16 10:00 | 68 | 67
2017-12-16 10:30 | 68 | 68
2017-12-16 11:00 | 69 | 69
2017-12-16 11:30 | 70 | 70
2017-12-16 12:00 | 70 | 69
2017-12-16 12:30 | 69 | 69
2017-12-16 13:00 | 69 | 68
2017-12-16 13:30 | 69 | 69
2017-12-16 14:00 | 70 | 69
2017-12-16 14:30 | 65 | 64
2017-12-16 15:00 | 69 | 69
2017-12-16 15:30 | 65 | 64
2017-12-16 16:00 | 67 | 66
2017-12-16 16:30 | 72 | 72
2017-12-16 17:00 | 68 | 67
2017-12-16 17:30 | 71 | 70
2017-12-16 18:00 | 73 | 73
2017-12-16 18:30 | 73 | 73
2017-12-16 19:00 | 75 | 75
2017-12-16 19:30 | 76 | 76
2017-12-16 20:00 | 75 | 75
2017-12-16 20:30 | 74 | 74
2017-12-16 21:00 | 73 | 73
2017-12-16 21:30 | 71 | 71
2017-12-16 22:00 | 71 | 70
2017-12-16 22:30 | 70 | 69
2017-12-16 23:00 | 69 | 69
2017-12-16 23:30 | 70 | 69
2017-12-17 | 69 | 69
2017-12-17 00:30 | 68 | 67
2017-12-17 01:00 | 68 | 67
2017-12-17 01:30 | 67 | 67
2017-12-17 02:00 | 68 | 67
2017-12-17 02:30 | 68 | 68
2017-12-17 03:00 | 67 | 67
2017-12-17 03:30 | 67 | 67
2017-12-17 04:00 | 66 | 66
2017-12-17 04:30 | 66 | 65
2017-12-17 05:00 | 65 | 65
2017-12-17 05:30 | 66 | 66
2017-12-17 06:00 | 65 | 65
2017-12-17 06:30 | 64 | 64
2017-12-17 07:00 | 65 | 65
2017-12-17 07:30 | 67 | 66
2017-12-17 08:00 | 67 | 67
2017-12-17 08:30 | 68 | 68
2017-12-17 09:00 | 68 | 68
2017-12-17 09:30 | 68 | 68
2017-12-17 10:00 | 68 | 68
2017-12-17 10:30 | 68 | 68
2017-12-17 11:00 | 68 | 68
2017-12-17 11:30 | 69 | 69
2017-12-17 12:00 | 70 | 70
2017-12-17 12:30 | 70 | 70
2017-12-17 13:00 | 71 | 70
2017-12-17 13:30 | 71 | 71
2017-12-17 14:00 | 71 | 71
2017-12-17 14:30 | 71 | 71
2017-12-17 15:00 | 71 | 71
2017-12-17 15:30 | 71 | 71
2017-12-17 16:00 | 73 | 72
2017-12-17 16:30 | 74 | 74
2017-12-17 17:00 | 76 | 75
2017-12-17 17:30 | 76 | 76
2017-12-17 18:00 | 76 | 76
2017-12-17 18:30 | 76 | 76
2017-12-17 19:00 | 75 | 75
2017-12-17 19:30 | 77 | 77
2017-12-17 20:00 | 78 | 78
2017-12-17 20:30 | 77 | 77
2017-12-17 21:00 | 76 | 76
2017-12-17 21:30 | 75 | 75
2017-12-17 22:00 | 73 | 73
2017-12-17 22:30 | 71 | 71
2017-12-17 23:00 | 69 | 69
2017-12-17 23:30 | 69 | 68
2017-12-18 | 68 | 68
2017-12-18 00:30 | 67 | 67
2017-12-18 01:00 | 67 | 67
2017-12-18 01:30 | 66 | 66
2017-12-18 02:00 | 66 | 66
2017-12-18 02:30 | 66 | 66
2017-12-18 03:00 | 66 | 66
2017-12-18 03:30 | 66 | 66
2017-12-18 04:00 | 65 | 65
2017-12-18 04:30 | 65 | 65
2017-12-18 05:00 | 65 | 65
2017-12-18 05:30 | 65 | 65
2017-12-18 06:00 | 65 | 65
2017-12-18 06:30 | 66 | 66
2017-12-18 07:00 | 68 | 68
2017-12-18 07:30 | 70 | 69
2017-12-18 08:00 | 69 | 69
2017-12-18 08:30 | 67 | 67
2017-12-18 09:00 | 69 | 69
2017-12-18 09:30 | 69 | 69
2017-12-18 10:00 | 69 | 69
2017-12-18 10:30 | 69 | 69
2017-12-18 11:00 | 68 | 68
2017-12-18 11:30 | 68 | 67
2017-12-18 12:00 | 67 | 67
2017-12-18 12:30 | 68 | 68
2017-12-18 13:00 | 65 | 65
2017-12-18 13:30 | 68 | 68
2017-12-18 14:00 | 63 | 63
2017-12-18 14:30 | 63 | 63
2017-12-18 15:00 | 69 | 69
2017-12-18 15:30 | 72 | 72
2017-12-18 16:00 | 73 | 73
2017-12-18 16:30 | 73 | 73
2017-12-18 17:00 | 70 | 70
2017-12-18 17:30 | 70 | 70
2017-12-18 18:00 | 63 | 61
2017-12-18 18:30 | 69 | 69
2017-12-18 19:00 | 77 | 77
2017-12-18 19:30 | 79 | 79
2017-12-18 20:00 | 80 | 79
2017-12-18 20:30 | 79 | 79
2017-12-18 21:00 | 78 | 78
2017-12-18 21:30 | 76 | 76
2017-12-18 22:00 | 75 | 75
2017-12-18 22:30 | 73 | 73
2017-12-18 23:00 | 72 | 72
2017-12-18 23:30 | 72 | 72
2017-12-19 | 72 | 72
2017-12-19 00:30 | 71 | 71
2017-12-19 01:00 | 71 | 71
2017-12-19 01:30 | 70 | 70
2017-12-19 02:00 | 69 | 69
2017-12-19 02:30 | 69 | 69
2017-12-19 03:00 | 68 | 68
2017-12-19 03:30 | 67 | 67
2017-12-19 04:00 | 66 | 66
2017-12-19 04:30 | 67 | 67
2017-12-19 05:00 | 67 | 67
2017-12-19 05:30 | 66 | 66
2017-12-19 06:00 | 66 | 66
2017-12-19 06:30 | 65 | 65
2017-12-19 07:00 | 67 | 67
2017-12-19 07:30 | 69 | 69
2017-12-19 08:00 | 71 | 71
2017-12-19 08:30 | 72 | 72
2017-12-19 09:00 | 74 | 74
2017-12-19 09:30 | 74 | 74
2017-12-19 10:00 | 74 | 73
2017-12-19 10:30 | 74 | 74
2017-12-19 11:00 | 75 | 74
2017-12-19 11:30 | 74 | 74
2017-12-19 12:00 | 72 | 72
2017-12-19 12:30 | 72 | 72
2017-12-19 13:00 | 70 | 69
2017-12-19 13:30 | 70 | 70
2017-12-19 14:00 | 70 | 70
2017-12-19 14:30 | 71 | 70
2017-12-19 15:00 | 71 | 71
2017-12-19 15:30 | 56 | 53
2017-12-19 16:00 | 55 | 51
2017-12-19 16:30 | 65 | 64
2017-12-19 17:00 | 74 | 74
2017-12-19 17:30 | 76 | 76
2017-12-19 18:00 | 75 | 75
2017-12-19 18:30 | 75 | 75
2017-12-19 19:00 | 76 | 76
2017-12-19 19:30 | 77 | 77
2017-12-19 20:00 | 77 | 77
2017-12-19 20:30 | 77 | 77
2017-12-19 21:00 | 75 | 75
2017-12-19 21:30 | 74 | 74
2017-12-19 22:00 | 72 | 72
2017-12-19 22:30 | 71 | 71
2017-12-19 23:00 | 70 | 70
2017-12-19 23:30 | 69 | 69
2017-12-20 | 68 | 68
2017-12-20 00:30 | 68 | 68
2017-12-20 01:00 | 67 | 67
2017-12-20 01:30 | 67 | 66
2017-12-20 02:00 | 66 | 66
2017-12-20 02:30 | 66 | 66
2017-12-20 03:00 | 66 | 65
2017-12-20 03:30 | 66 | 65
2017-12-20 04:00 | 66 | 65
2017-12-20 04:30 | 65 | 65
2017-12-20 05:00 | 65 | 65
2017-12-20 05:30 | 65 | 64
2017-12-20 06:00 | 64 | 64
2017-12-20 06:30 | 66 | 66
2017-12-20 07:00 | 67 | 67
2017-12-20 07:30 | 69 | 69
2017-12-20 08:00 | 70 | 70
2017-12-20 08:30 | 71 | 71
2017-12-20 09:00 | 71 | 71
2017-12-20 09:30 | 72 | 71
2017-12-20 10:00 | 73 | 72
2017-12-20 10:30 | 73 | 73
2017-12-20 11:00 | 72 | 72
2017-12-20 11:30 | 72 | 71
2017-12-20 12:00 | 71 | 71
2017-12-20 12:30 | 71 | 71
2017-12-20 13:00 | 72 | 72
2017-12-20 13:30 | 69 | 69
2017-12-20 14:00 | 72 | 72
2017-12-20 14:30 | 74 | 74
2017-12-20 15:00 | 76 | 76
2017-12-20 15:30 | 79 | 79
2017-12-20 16:00 | 77 | 77
2017-12-20 16:30 | 77 | 77
2017-12-20 17:00 | 78 | 78
2017-12-20 17:30 | 78 | 78
2017-12-20 18:00 | 77 | 77
2017-12-20 18:30 | 76 | 76
2017-12-20 19:00 | 77 | 76
2017-12-20 19:30 | 79 | 78
2017-12-20 20:00 | 82 | 81
2017-12-20 20:30 | 81 | 81
2017-12-20 21:00 | 80 | 79
2017-12-20 21:30 | 82 | 81
2017-12-20 22:00 | 78 | 78
2017-12-20 22:30 | 77 | 76
2017-12-20 23:00 | 79 | 78
2017-12-20 23:30 | 80 | 80
2017-12-21 | 79 | 79
2017-12-21 00:30 | 79 | 78
2017-12-21 01:00 | 78 | 78
2017-12-21 01:30 | 77 | 76
2017-12-21 02:00 | 76 | 76
2017-12-21 02:30 | 76 | 76
2017-12-21 03:00 | 76 | 76
2017-12-21 03:30 | 76 | 76
2017-12-21 04:00 | 75 | 75
2017-12-21 04:30 | 75 | 75
2017-12-21 05:00 | 75 | 75
2017-12-21 05:30 | 75 | 75
2017-12-21 06:00 | 75 | 75
2017-12-21 06:30 | 76 | 76
2017-12-21 07:00 | 78 | 78
2017-12-21 07:30 | 81 | 81
2017-12-21 08:00 | 78 | 78
2017-12-21 08:30 | 76 | 76
2017-12-21 09:00 | 75 | 75
2017-12-21 09:30 | 75 | 75
2017-12-21 10:00 | 73 | 73
2017-12-21 10:30 | 72 | 72
2017-12-21 11:00 | 73 | 73
2017-12-21 11:30 | 74 | 74
2017-12-21 12:00 | 75 | 75
2017-12-21 12:30 | 75 | 75
2017-12-21 13:00 | 74 | 74
2017-12-21 13:30 | 74 | 73
2017-12-21 14:00 | 74 | 73
2017-12-21 14:30 | 73 | 73
2017-12-21 15:00 | 65 | 63
2017-12-21 15:30 | 66 | 64
2017-12-21 16:00 | 70 | 68
2017-12-21 16:30 | 72 | 70
2017-12-21 17:00 | 66 | 62
2017-12-21 17:30 | 73 | 70
2017-12-21 18:00 | 86 | 86
2017-12-21 18:30 | 85 | 85
2017-12-21 19:00 | 85 | 85
2017-12-21 19:30 | 84 | 84
2017-12-21 20:00 | 85 | 85
2017-12-21 20:30 | 84 | 84
2017-12-21 21:00 | 84 | 84
2017-12-21 21:30 | 83 | 82
2017-12-21 22:00 | 81 | 81
2017-12-21 22:30 | 78 | 78
2017-12-21 23:00 | 77 | 77
2017-12-21 23:30 | 76 | 76
2017-12-22 | 75 | 75
2017-12-22 00:30 | 75 | 75
2017-12-22 01:00 | 74 | 74
2017-12-22 01:30 | 74 | 74
2017-12-22 02:00 | 73 | 73
2017-12-22 02:30 | 74 | 74
2017-12-22 03:00 | 73 | 73
2017-12-22 03:30 | 73 | 73
2017-12-22 04:00 | 73 | 73
2017-12-22 04:30 | 72 | 72
2017-12-22 05:00 | 72 | 72
2017-12-22 05:30 | 71 | 71
2017-12-22 06:00 | 71 | 71
2017-12-22 06:30 | 72 | 72
2017-12-22 07:00 | 74 | 74
2017-12-22 07:30 | 75 | 75
2017-12-22 08:00 | 78 | 77
2017-12-22 08:30 | 78 | 77
2017-12-22 09:00 | 78 | 77
2017-12-22 09:30 | 78 | 77
2017-12-22 10:00 | 77 | 77
2017-12-22 10:30 | 78 | 77
2017-12-22 11:00 | 78 | 77
2017-12-22 11:30 | 78 | 77
2017-12-22 12:00 | 78 | 77
2017-12-22 12:30 | 78 | 77
2017-12-22 13:00 | 78 | 77
2017-12-22 13:30 | 79 | 77
2017-12-22 14:00 | 79 | 77
2017-12-22 14:30 | 79 | 78
2017-12-22 15:00 | 80 | 79
2017-12-22 15:30 | 81 | 80
2017-12-22 16:00 | 82 | 81
2017-12-22 16:30 | 77 | 74
2017-12-22 17:00 | 76 | 73
2017-12-22 17:30 | 83 | 81
2017-12-22 18:00 | 90 | 84
2017-12-22 18:30 | 88 | 83
2017-12-22 19:00 | 86 | 81
2017-12-22 19:30 | 87 | 83
2017-12-22 20:00 | 86 | 83
2017-12-22 20:30 | 87 | 83
2017-12-22 21:00 | 87 | 83
2017-12-22 21:30 | 86 | 82
2017-12-22 22:00 | 85 | 80
2017-12-22 22:30 | 84 | 79
2017-12-22 23:00 | 83 | 78
2017-12-22 23:30 | 80 | 77
2017-12-23 | 77 | 76
2017-12-23 00:30 | 75 | 75
2017-12-23 01:00 | 75 | 75
2017-12-23 01:30 | 74 | 74
2017-12-23 02:00 | 74 | 74
2017-12-23 02:30 | 74 | 74
2017-12-23 03:00 | 73 | 73
2017-12-23 03:30 | 73 | 73
2017-12-23 04:00 | 73 | 73
2017-12-23 04:30 | 72 | 72
2017-12-23 05:00 | 72 | 72
2017-12-23 05:30 | 71 | 71
2017-12-23 06:00 | 71 | 71
2017-12-23 06:30 | 70 | 70
2017-12-23 07:00 | 71 | 71
2017-12-23 07:30 | 73 | 73
2017-12-23 08:00 | 73 | 73
2017-12-23 08:30 | 73 | 73
2017-12-23 09:00 | 73 | 73
2017-12-23 09:30 | 73 | 73
2017-12-23 10:00 | 73 | 73
2017-12-23 10:30 | 74 | 73
2017-12-23 11:00 | 73 | 73
2017-12-23 11:30 | 74 | 74
2017-12-23 12:00 | 75 | 74
2017-12-23 12:30 | 74 | 74
2017-12-23 13:00 | 74 | 74
2017-12-23 13:30 | 74 | 74
2017-12-23 14:00 | 74 | 74
2017-12-23 14:30 | 75 | 75
2017-12-23 15:00 | 76 | 76
2017-12-23 15:30 | 76 | 76
2017-12-23 16:00 | 77 | 77
2017-12-23 16:30 | 68 | 67
2017-12-23 17:00 | 65 | 63
2017-12-23 17:30 | 66 | 64
2017-12-23 18:00 | 66 | 64
2017-12-23 18:30 | 66 | 64
2017-12-23 19:00 | 66 | 65
2017-12-23 19:30 | 67 | 65
2017-12-23 20:00 | 67 | 66
2017-12-23 20:30 | 66 | 65
2017-12-23 21:00 | 77 | 77
2017-12-23 21:30 | 79 | 79
2017-12-23 22:00 | 78 | 78
2017-12-23 22:30 | 77 | 77
2017-12-23 23:00 | 76 | 76
2017-12-23 23:30 | 75 | 75
2017-12-24 | 74 | 74
2017-12-24 00:30 | 74 | 74
2017-12-24 01:00 | 74 | 73
2017-12-24 01:30 | 73 | 72
2017-12-24 02:00 | 73 | 72
2017-12-24 02:30 | 72 | 71
2017-12-24 03:00 | 71 | 71
2017-12-24 03:30 | 71 | 71
2017-12-24 04:00 | 70 | 70
2017-12-24 04:30 | 70 | 70
2017-12-24 05:00 | 69 | 69
2017-12-24 05:30 | 70 | 69
2017-12-24 06:00 | 69 | 69
2017-12-24 06:30 | 69 | 69
2017-12-24 07:00 | 71 | 70
2017-12-24 07:30 | 71 | 71
2017-12-24 08:00 | 72 | 72
2017-12-24 08:30 | 73 | 73
2017-12-24 09:00 | 73 | 73
2017-12-24 09:30 | 75 | 75
2017-12-24 10:00 | 74 | 74
2017-12-24 10:30 | 75 | 75
2017-12-24 11:00 | 75 | 75
2017-12-24 11:30 | 75 | 75
2017-12-24 12:00 | 74 | 74
2017-12-24 12:30 | 75 | 75
2017-12-24 13:00 | 73 | 72
2017-12-24 13:30 | 70 | 69
2017-12-24 14:00 | 65 | 62
2017-12-24 14:30 | 70 | 69
2017-12-24 15:00 | 73 | 72
2017-12-24 15:30 | 77 | 77
2017-12-24 16:00 | 77 | 77
2017-12-24 16:30 | 78 | 78
2017-12-24 17:00 | 69 | 68
2017-12-24 17:30 | 71 | 70
2017-12-24 18:00 | 77 | 77
2017-12-24 18:30 | 79 | 79
2017-12-24 19:00 | 79 | 79
2017-12-24 19:30 | 79 | 79
2017-12-24 20:00 | 79 | 79
2017-12-24 20:30 | 78 | 78
2017-12-24 21:00 | 77 | 77
2017-12-24 21:30 | 76 | 76
2017-12-24 22:00 | 76 | 76
2017-12-24 22:30 | 74 | 74
2017-12-24 23:00 | 73 | 73
2017-12-24 23:30 | 72 | 72
2017-12-25 | 71 | 71
2017-12-25 00:30 | 70 | 70
2017-12-25 01:00 | 70 | 70
2017-12-25 01:30 | 69 | 69
2017-12-25 02:00 | 69 | 68
2017-12-25 02:30 | 68 | 68
2017-12-25 03:00 | 68 | 68
2017-12-25 03:30 | 68 | 68
2017-12-25 04:00 | 67 | 67
2017-12-25 04:30 | 67 | 67
2017-12-25 05:00 | 68 | 67
2017-12-25 05:30 | 67 | 66
2017-12-25 06:00 | 66 | 65
2017-12-25 06:30 | 67 | 67
2017-12-25 07:00 | 69 | 68
2017-12-25 07:30 | 69 | 69
2017-12-25 08:00 | 69 | 69
2017-12-25 08:30 | 70 | 70
2017-12-25 09:00 | 70 | 70
2017-12-25 09:30 | 70 | 70
2017-12-25 10:00 | 71 | 71
2017-12-25 10:30 | 71 | 71
2017-12-25 11:00 | 71 | 71
2017-12-25 11:30 | 70 | 70
2017-12-25 12:00 | 71 | 71
2017-12-25 12:30 | 71 | 71
2017-12-25 13:00 | 71 | 71
2017-12-25 13:30 | 70 | 70
2017-12-25 14:00 | 71 | 71
2017-12-25 14:30 | 71 | 71
2017-12-25 15:00 | 70 | 70
2017-12-25 15:30 | 71 | 71
2017-12-25 16:00 | 73 | 73
2017-12-25 16:30 | 73 | 73
2017-12-25 17:00 | 74 | 74
2017-12-25 17:30 | 75 | 75
2017-12-25 18:00 | 75 | 75
2017-12-25 18:30 | 74 | 74
2017-12-25 19:00 | 74 | 74
2017-12-25 19:30 | 74 | 74
2017-12-25 20:00 | 74 | 74
2017-12-25 20:30 | 74 | 74
2017-12-25 21:00 | 74 | 74
2017-12-25 21:30 | 73 | 73
2017-12-25 22:00 | 72 | 72
2017-12-25 22:30 | 72 | 72
2017-12-25 23:00 | 71 | 71
2017-12-25 23:30 | 69 | 69
2017-12-26 | 69 | 69
2017-12-26 00:30 | 69 | 69
2017-12-26 01:00 | 68 | 68
2017-12-26 01:30 | 69 | 68
2017-12-26 02:00 | 69 | 68
2017-12-26 02:30 | 69 | 68
2017-12-26 03:00 | 68 | 66
2017-12-26 03:30 | 69 | 66
2017-12-26 04:00 | 68 | 66
2017-12-26 04:30 | 68 | 66
2017-12-26 05:00 | 68 | 66
2017-12-26 05:30 | 68 | 66
2017-12-26 06:00 | 68 | 66
2017-12-26 06:30 | 68 | 66
2017-12-26 07:00 | 69 | 67
2017-12-26 07:30 | 71 | 69
2017-12-26 08:00 | 72 | 70
2017-12-26 08:30 | 71 | 69
2017-12-26 09:00 | 72 | 71
2017-12-26 09:30 | 72 | 71
2017-12-26 10:00 | 71 | 70
2017-12-26 10:30 | 70 | 69
2017-12-26 11:00 | 72 | 71
2017-12-26 11:30 | 71 | 70
2017-12-26 12:00 | 70 | 69
2017-12-26 12:30 | 70 | 69
2017-12-26 13:00 | 71 | 70
2017-12-26 13:30 | 71 | 70
2017-12-26 14:00 | 73 | 72
2017-12-26 14:30 | 73 | 72
2017-12-26 15:00 | 72 | 72
2017-12-26 15:30 | 73 | 72
2017-12-26 16:00 | 75 | 74
2017-12-26 16:30 | 76 | 75
2017-12-26 17:00 | 76 | 76
2017-12-26 17:30 | 77 | 76
2017-12-26 18:00 | 76 | 75
2017-12-26 18:30 | 76 | 76
2017-12-26 19:00 | 77 | 76
2017-12-26 19:30 | 78 | 77
2017-12-26 20:00 | 78 | 77
2017-12-26 20:30 | 78 | 77
2017-12-26 21:00 | 77 | 76
2017-12-26 21:30 | 76 | 76
2017-12-26 22:00 | 75 | 75
2017-12-26 22:30 | 73 | 73
2017-12-26 23:00 | 72 | 72
2017-12-26 23:30 | 72 | 71
2017-12-27 | 71 | 71
2017-12-27 00:30 | 70 | 70
2017-12-27 01:00 | 70 | 70
2017-12-27 01:30 | 70 | 70
2017-12-27 02:00 | 70 | 69
2017-12-27 02:30 | 69 | 69
2017-12-27 03:00 | 70 | 69
2017-12-27 03:30 | 69 | 69
2017-12-27 04:00 | 69 | 69
2017-12-27 04:30 | 69 | 69
2017-12-27 05:00 | 69 | 69
2017-12-27 05:30 | 69 | 69
2017-12-27 06:00 | 69 | 69
2017-12-27 06:30 | 70 | 70
2017-12-27 07:00 | 71 | 71
2017-12-27 07:30 | 73 | 72
2017-12-27 08:00 | 74 | 74
2017-12-27 08:30 | 74 | 74
2017-12-27 09:00 | 74 | 73
2017-12-27 09:30 | 73 | 73
2017-12-27 10:00 | 72 | 72
2017-12-27 10:30 | 73 | 72
2017-12-27 11:00 | 72 | 72
2017-12-27 11:30 | 73 | 72
2017-12-27 12:00 | 74 | 74
2017-12-27 12:30 | 75 | 75
2017-12-27 13:00 | 75 | 75
2017-12-27 13:30 | 76 | 76
2017-12-27 14:00 | 76 | 76
2017-12-27 14:30 | 77 | 76
2017-12-27 15:00 | 77 | 77
2017-12-27 15:30 | 78 | 77
2017-12-27 16:00 | 80 | 79
2017-12-27 16:30 | 78 | 77
2017-12-27 17:00 | 73 | 69
2017-12-27 17:30 | 78 | 76
2017-12-27 18:00 | 80 | 79
2017-12-27 18:30 | 80 | 79
2017-12-27 19:00 | 80 | 79
2017-12-27 19:30 | 81 | 80
2017-12-27 20:00 | 81 | 80
2017-12-27 20:30 | 80 | 80
2017-12-27 21:00 | 79 | 78
2017-12-27 21:30 | 78 | 78
2017-12-27 22:00 | 76 | 76
2017-12-27 22:30 | 75 | 75
2017-12-27 23:00 | 75 | 75
2017-12-27 23:30 | 75 | 74
2017-12-28 | 74 | 74
2017-12-28 00:30 | 73 | 73
2017-12-28 01:00 | 73 | 73
2017-12-28 01:30 | 73 | 72
2017-12-28 02:00 | 72 | 72
2017-12-28 02:30 | 71 | 71
2017-12-28 03:00 | 70 | 70
2017-12-28 03:30 | 71 | 71
2017-12-28 04:00 | 70 | 70
2017-12-28 04:30 | 70 | 70
2017-12-28 05:00 | 70 | 70
2017-12-28 05:30 | 71 | 71
2017-12-28 06:00 | 70 | 70
2017-12-28 06:30 | 71 | 71
2017-12-28 07:00 | 70 | 70
2017-12-28 07:30 | 73 | 73
2017-12-28 08:00 | 72 | 72
2017-12-28 08:30 | 74 | 74
2017-12-28 09:00 | 74 | 74
2017-12-28 09:30 | 74 | 74
2017-12-28 10:00 | 74 | 74
2017-12-28 10:30 | 75 | 75
2017-12-28 11:00 | 74 | 74
2017-12-28 11:30 | 73 | 73
2017-12-28 12:00 | 75 | 75
2017-12-28 12:30 | 75 | 75
2017-12-28 13:00 | 70 | 70
2017-12-28 13:30 | 69 | 68
2017-12-28 14:00 | 69 | 69
2017-12-28 14:30 | 78 | 78
2017-12-28 15:00 | 81 | 81
2017-12-28 15:30 | 82 | 82
2017-12-28 16:00 | 83 | 83
2017-12-28 16:30 | 84 | 84
2017-12-28 17:00 | 85 | 85
2017-12-28 17:30 | 78 | 78
2017-12-28 18:00 | 76 | 75
2017-12-28 18:30 | 85 | 85
2017-12-28 19:00 | 84 | 83
2017-12-28 19:30 | 85 | 85
2017-12-28 20:00 | 85 | 85
2017-12-28 20:30 | 72 | 72
2017-12-28 21:00 | 70 | 70
2017-12-28 21:30 | 78 | 78
2017-12-28 22:00 | 77 | 77
2017-12-28 22:30 | 70 | 69
2017-12-28 23:00 | 72 | 72
2017-12-28 23:30 | 75 | 75
2017-12-29 | 75 | 74
2017-12-29 00:30 | 74 | 73
2017-12-29 01:00 | 73 | 73
2017-12-29 01:30 | 74 | 74
2017-12-29 02:00 | 73 | 73
2017-12-29 02:30 | 73 | 73
2017-12-29 03:00 | 73 | 73
2017-12-29 03:30 | 73 | 73
2017-12-29 04:00 | 72 | 72
2017-12-29 04:30 | 72 | 72
2017-12-29 05:00 | 72 | 72
2017-12-29 05:30 | 72 | 72
2017-12-29 06:00 | 70 | 70
2017-12-29 06:30 | 71 | 70
2017-12-29 07:00 | 71 | 71
2017-12-29 07:30 | 72 | 72
2017-12-29 08:00 | 73 | 73
2017-12-29 08:30 | 68 | 68
2017-12-29 09:00 | 74 | 74
2017-12-29 09:30 | 67 | 67
2017-12-29 10:00 | 73 | 73
2017-12-29 10:30 | 74 | 74
2017-12-29 11:00 | 64 | 64
2017-12-29 11:30 | 71 | 71
2017-12-29 12:00 | 77 | 77
2017-12-29 12:30 | 79 | 79
2017-12-29 13:00 | 80 | 80
2017-12-29 13:30 | 80 | 80
2017-12-29 14:00 | 81 | 81
2017-12-29 14:30 | 81 | 81
2017-12-29 15:00 | 82 | 82
2017-12-29 15:30 | 82 | 82
2017-12-29 16:00 | 84 | 84
2017-12-29 16:30 | 85 | 85
2017-12-29 17:00 | 85 | 85
2017-12-29 17:30 | 87 | 86
2017-12-29 18:00 | 87 | 87
2017-12-29 18:30 | 87 | 87
2017-12-29 19:00 | 80 | 80
2017-12-29 19:30 | 75 | 75
2017-12-29 20:00 | 83 | 83
2017-12-29 20:30 | 80 | 79
2017-12-29 21:00 | 80 | 79
2017-12-29 21:30 | 79 | 79
2017-12-29 22:00 | 78 | 78
2017-12-29 22:30 | 77 | 76
2017-12-29 23:00 | 75 | 75
2017-12-29 23:30 | 75 | 75
2017-12-30 | 74 | 74
2017-12-30 00:30 | 72 | 72
2017-12-30 01:00 | 72 | 72
2017-12-30 01:30 | 71 | 71
2017-12-30 02:00 | 72 | 72
2017-12-30 02:30 | 71 | 71
2017-12-30 03:00 | 71 | 71
2017-12-30 03:30 | 71 | 71
2017-12-30 04:00 | 70 | 70
2017-12-30 04:30 | 69 | 69
2017-12-30 05:00 | 70 | 70
2017-12-30 05:30 | 70 | 70
2017-12-30 06:00 | 68 | 68
2017-12-30 06:30 | 69 | 69
2017-12-30 07:00 | 71 | 71
2017-12-30 07:30 | 71 | 71
2017-12-30 08:00 | 71 | 71
2017-12-30 08:30 | 72 | 72
2017-12-30 09:00 | 72 | 72
2017-12-30 09:30 | 71 | 71
2017-12-30 10:00 | 74 | 74
2017-12-30 10:30 | 75 | 75
2017-12-30 11:00 | 75 | 75
2017-12-30 11:30 | 76 | 76
2017-12-30 12:00 | 76 | 76
2017-12-30 12:30 | 76 | 76
2017-12-30 13:00 | 77 | 77
2017-12-30 13:30 | 77 | 77
2017-12-30 14:00 | 78 | 78
2017-12-30 14:30 | 77 | 77
2017-12-30 15:00 | 78 | 78
2017-12-30 15:30 | 78 | 78
2017-12-30 16:00 | 77 | 77
2017-12-30 16:30 | 78 | 78
2017-12-30 17:00 | 71 | 71
2017-12-30 17:30 | 67 | 67
2017-12-30 18:00 | 68 | 67
2017-12-30 18:30 | 78 | 78
2017-12-30 19:00 | 81 | 81
2017-12-30 19:30 | 81 | 81
2017-12-30 20:00 | 81 | 81
2017-12-30 20:30 | 80 | 80
2017-12-30 21:00 | 79 | 79
2017-12-30 21:30 | 79 | 79
2017-12-30 22:00 | 77 | 77
2017-12-30 22:30 | 76 | 76
2017-12-30 23:00 | 75 | 75
2017-12-30 23:30 | 74 | 74
2017-12-31 | 74 | 74
2017-12-31 00:30 | 74 | 74
2017-12-31 01:00 | 74 | 73
2017-12-31 01:30 | 74 | 73
2017-12-31 02:00 | 73 | 73
2017-12-31 02:30 | 73 | 73
2017-12-31 03:00 | 73 | 73
2017-12-31 03:30 | 72 | 72
2017-12-31 04:00 | 72 | 72
2017-12-31 04:30 | 71 | 71
2017-12-31 05:00 | 72 | 72
2017-12-31 05:30 | 71 | 71
2017-12-31 06:00 | 71 | 70
2017-12-31 06:30 | 71 | 70
2017-12-31 07:00 | 70 | 70
2017-12-31 07:30 | 71 | 71
2017-12-31 08:00 | 70 | 70
2017-12-31 08:30 | 71 | 71
2017-12-31 09:00 | 71 | 71
2017-12-31 09:30 | 71 | 71
2017-12-31 10:00 | 74 | 73
2017-12-31 10:30 | 74 | 73
2017-12-31 11:00 | 75 | 74
2017-12-31 11:30 | 75 | 74
2017-12-31 12:00 | 75 | 75
2017-12-31 12:30 | 76 | 76
2017-12-31 13:00 | 76 | 75
2017-12-31 13:30 | 77 | 76
2017-12-31 14:00 | 71 | 70
2017-12-31 14:30 | 75 | 74
2017-12-31 15:00 | 78 | 78
2017-12-31 15:30 | 79 | 79
2017-12-31 16:00 | 80 | 79
2017-12-31 16:30 | 80 | 80
2017-12-31 17:00 | 81 | 81
2017-12-31 17:30 | 83 | 82
2017-12-31 18:00 | 83 | 82
2017-12-31 18:30 | 82 | 81
2017-12-31 19:00 | 82 | 81
2017-12-31 19:30 | 82 | 82
2017-12-31 20:00 | 81 | 80
2017-12-31 20:30 | 80 | 79
2017-12-31 21:00 | 79 | 79
2017-12-31 21:30 | 78 | 78
2017-12-31 22:00 | 78 | 77
2017-12-31 22:30 | 77 | 76
2017-12-31 23:00 | 76 | 75
2017-12-31 23:30 | 76 | 75
2018-01-01 | 74 | 73
2018-01-01 00:30 | 72 | 71
2018-01-01 01:00 | 73 | 72
2018-01-01 01:30 | 73 | 72
2018-01-01 02:00 | 73 | 72
2018-01-01 02:30 | 72 | 72
2018-01-01 03:00 | 72 | 72
2018-01-01 03:30 | 72 | 72
2018-01-01 04:00 | 71 | 71
2018-01-01 04:30 | 72 | 72
2018-01-01 05:00 | 71 | 70
2018-01-01 05:30 | 71 | 71
2018-01-01 06:00 | 71 | 71
2018-01-01 06:30 | 71 | 71
2018-01-01 07:00 | 71 | 71
2018-01-01 07:30 | 72 | 71
2018-01-01 08:00 | 73 | 73
2018-01-01 08:30 | 73 | 72
2018-01-01 09:00 | 73 | 72
2018-01-01 09:30 | 73 | 73
2018-01-01 10:00 | 73 | 73
2018-01-01 10:30 | 74 | 74
2018-01-01 11:00 | 75 | 74
2018-01-01 11:30 | 76 | 75
2018-01-01 12:00 | 76 | 76
2018-01-01 12:30 | 77 | 76
2018-01-01 13:00 | 77 | 77
2018-01-01 13:30 | 77 | 76
2018-01-01 14:00 | 76 | 76
2018-01-01 14:30 | 77 | 77
2018-01-01 15:00 | 80 | 80
2018-01-01 15:30 | 84 | 83
2018-01-01 16:00 | 85 | 84
2018-01-01 16:30 | 86 | 85
2018-01-01 17:00 | 87 | 86
2018-01-01 17:30 | 88 | 87
2018-01-01 18:00 | 88 | 87
2018-01-01 18:30 | 88 | 87
2018-01-01 19:00 | 87 | 86
2018-01-01 19:30 | 88 | 87
2018-01-01 20:00 | 88 | 86
2018-01-01 20:30 | 88 | 87
2018-01-01 21:00 | 88 | 87
2018-01-01 21:30 | 83 | 82
2018-01-01 22:00 | 80 | 79
2018-01-01 22:30 | 79 | 78
2018-01-01 23:00 | 78 | 76
2018-01-01 23:30 | 77 | 75
2018-01-02 | 75 | 74
2018-01-02 00:30 | 75 | 75
2018-01-02 01:00 | 74 | 74
2018-01-02 01:30 | 74 | 74
2018-01-02 02:00 | 73 | 73
2018-01-02 02:30 | 73 | 73
2018-01-02 03:00 | 74 | 74
2018-01-02 03:30 | 73 | 73
2018-01-02 04:00 | 73 | 73
2018-01-02 04:30 | 72 | 72
2018-01-02 05:00 | 72 | 72
2018-01-02 05:30 | 72 | 72
2018-01-02 06:00 | 72 | 72
2018-01-02 06:30 | 72 | 72
2018-01-02 07:00 | 74 | 74
2018-01-02 07:30 | 77 | 77
2018-01-02 08:00 | 79 | 79
2018-01-02 08:30 | 79 | 78
2018-01-02 09:00 | 80 | 80
2018-01-02 09:30 | 79 | 79
2018-01-02 10:00 | 77 | 77
2018-01-02 10:30 | 77 | 77
2018-01-02 11:00 | 79 | 79
2018-01-02 11:30 | 79 | 79
2018-01-02 12:00 | 79 | 78
2018-01-02 12:30 | 80 | 80
2018-01-02 13:00 | 81 | 81
2018-01-02 13:30 | 74 | 74
2018-01-02 14:00 | 81 | 81
2018-01-02 14:30 | 82 | 82
2018-01-02 15:00 | 82 | 82
2018-01-02 15:30 | 73 | 71
2018-01-02 16:00 | 80 | 80
2018-01-02 16:30 | 87 | 87
2018-01-02 17:00 | 82 | 82
2018-01-02 17:30 | 82 | 82
2018-01-02 18:00 | 82 | 82
2018-01-02 18:30 | 80 | 80
2018-01-02 19:00 | 79 | 79
2018-01-02 19:30 | 78 | 78
2018-01-02 20:00 | 77 | 77
2018-01-02 20:30 | 75 | 75
2018-01-02 21:00 | 75 | 75
2018-01-02 21:30 | 74 | 74
2018-01-02 22:00 | 73 | 73
2018-01-02 22:30 | 71 | 71
2018-01-02 23:00 | 71 | 71
2018-01-02 23:30 | 71 | 71
2018-01-03 | 71 | 71
2018-01-03 00:30 | 70 | 70
2018-01-03 01:00 | 70 | 70
2018-01-03 01:30 | 69 | 69
2018-01-03 02:00 | 69 | 69
2018-01-03 02:30 | 68 | 68
2018-01-03 03:00 | 67 | 67
2018-01-03 03:30 | 67 | 67
2018-01-03 04:00 | 67 | 67
2018-01-03 04:30 | 68 | 68
2018-01-03 05:00 | 67 | 67
2018-01-03 05:30 | 67 | 67
2018-01-03 06:00 | 67 | 67
2018-01-03 06:30 | 67 | 67
2018-01-03 07:00 | 69 | 69
2018-01-03 07:30 | 71 | 71
2018-01-03 08:00 | 73 | 73
2018-01-03 08:30 | 74 | 74
2018-01-03 09:00 | 74 | 74
2018-01-03 09:30 | 74 | 74
2018-01-03 10:00 | 75 | 75
2018-01-03 10:30 | 77 | 77
2018-01-03 11:00 | 80 | 80
2018-01-03 11:30 | 81 | 81
2018-01-03 12:00 | 81 | 81
2018-01-03 12:30 | 76 | 76
2018-01-03 13:00 | 75 | 75
2018-01-03 13:30 | 73 | 73
2018-01-03 14:00 | 74 | 74
2018-01-03 14:30 | 73 | 73
2018-01-03 15:00 | 75 | 75
2018-01-03 15:30 | 74 | 74
2018-01-03 16:00 | 75 | 75
2018-01-03 16:30 | 75 | 75
2018-01-03 17:00 | 77 | 77
2018-01-03 17:30 | 77 | 77
2018-01-03 18:00 | 77 | 77
2018-01-03 18:30 | 82 | 82
2018-01-03 19:00 | 83 | 83
2018-01-03 19:30 | 85 | 85
2018-01-03 20:00 | 85 | 85
2018-01-03 20:30 | 84 | 84
2018-01-03 21:00 | 83 | 83
2018-01-03 21:30 | 82 | 82
2018-01-03 22:00 | 80 | 80
2018-01-03 22:30 | 79 | 79
2018-01-03 23:00 | 77 | 77
2018-01-03 23:30 | 76 | 76
2018-01-04 | 75 | 75
2018-01-04 00:30 | 74 | 74
2018-01-04 01:00 | 74 | 74
2018-01-04 01:30 | 73 | 73
2018-01-04 02:00 | 73 | 73
2018-01-04 02:30 | 73 | 73
2018-01-04 03:00 | 73 | 73
2018-01-04 03:30 | 72 | 72
2018-01-04 04:00 | 72 | 72
2018-01-04 04:30 | 72 | 72
2018-01-04 05:00 | 72 | 72
2018-01-04 05:30 | 71 | 71
2018-01-04 06:00 | 70 | 70
2018-01-04 06:30 | 71 | 71
2018-01-04 07:00 | 71 | 71
2018-01-04 07:30 | 73 | 73
2018-01-04 08:00 | 75 | 75
2018-01-04 08:30 | 74 | 74
2018-01-04 09:00 | 76 | 76
2018-01-04 09:30 | 77 | 77
2018-01-04 10:00 | 77 | 77
2018-01-04 10:30 | 79 | 79
2018-01-04 11:00 | 79 | 79
2018-01-04 11:30 | 79 | 79
2018-01-04 12:00 | 79 | 79
2018-01-04 12:30 | 80 | 80
2018-01-04 13:00 | 81 | 80
2018-01-04 13:30 | 80 | 80
2018-01-04 14:00 | 79 | 79
2018-01-04 14:30 | 83 | 82
2018-01-04 15:00 | 82 | 81
2018-01-04 15:30 | 83 | 82
2018-01-04 16:00 | 83 | 82
2018-01-04 16:30 | 83 | 82
2018-01-04 17:00 | 81 | 79
2018-01-04 17:30 | 75 | 71
2018-01-04 18:00 | 81 | 79
2018-01-04 18:30 | 83 | 81
2018-01-04 19:00 | 83 | 81
2018-01-04 19:30 | 84 | 82
2018-01-04 20:00 | 84 | 83
2018-01-04 20:30 | 84 | 82
2018-01-04 21:00 | 84 | 82
2018-01-04 21:30 | 82 | 80
2018-01-04 22:00 | 79 | 79
2018-01-04 22:30 | 80 | 79
2018-01-04 23:00 | 82 | 82
2018-01-04 23:30 | 79 | 79
2018-01-05 | 77 | 77
2018-01-05 00:30 | 76 | 76
2018-01-05 01:00 | 77 | 76
2018-01-05 01:30 | 76 | 75
2018-01-05 02:00 | 76 | 75
2018-01-05 02:30 | 75 | 74
2018-01-05 03:00 | 74 | 73
2018-01-05 03:30 | 72 | 71
2018-01-05 04:00 | 72 | 71
2018-01-05 04:30 | 71 | 71
2018-01-05 05:00 | 71 | 70
2018-01-05 05:30 | 70 | 70
2018-01-05 06:00 | 70 | 70
2018-01-05 06:30 | 71 | 70
2018-01-05 07:00 | 71 | 70
2018-01-05 07:30 | 72 | 72
2018-01-05 08:00 | 74 | 74
2018-01-05 08:30 | 76 | 75
2018-01-05 09:00 | 77 | 76
2018-01-05 09:30 | 76 | 76
2018-01-05 10:00 | 77 | 76
2018-01-05 10:30 | 78 | 77
2018-01-05 11:00 | 79 | 79
2018-01-05 11:30 | 79 | 79
2018-01-05 12:00 | 79 | 78
2018-01-05 12:30 | 79 | 78
2018-01-05 13:00 | 78 | 77
2018-01-05 13:30 | 77 | 76
2018-01-05 14:00 | 75 | 74
2018-01-05 14:30 | 74 | 73
2018-01-05 15:00 | 74 | 73
2018-01-05 15:30 | 75 | 73
2018-01-05 16:00 | 75 | 74
2018-01-05 16:30 | 75 | 74
2018-01-05 17:00 | 72 | 70
2018-01-05 17:30 | 76 | 74
2018-01-05 18:00 | 75 | 73
2018-01-05 18:30 | 76 | 73
2018-01-05 19:00 | 77 | 75
2018-01-05 19:30 | 78 | 77
2018-01-05 20:00 | 78 | 77
2018-01-05 20:30 | 78 | 76
2018-01-05 21:00 | 77 | 75
2018-01-05 21:30 | 77 | 75
2018-01-05 22:00 | 74 | 74
2018-01-05 22:30 | 72 | 72
2018-01-05 23:00 | 71 | 71
2018-01-05 23:30 | 70 | 70
2018-01-06 | 68 | 68
2018-01-06 00:30 | 67 | 67
2018-01-06 01:00 | 68 | 68
2018-01-06 01:30 | 67 | 67
2018-01-06 02:00 | 67 | 67
2018-01-06 02:30 | 67 | 67
2018-01-06 03:00 | 66 | 66
2018-01-06 03:30 | 67 | 67
2018-01-06 04:00 | 66 | 66
2018-01-06 04:30 | 66 | 66
2018-01-06 05:00 | 66 | 66
2018-01-06 05:30 | 66 | 66
2018-01-06 06:00 | 65 | 65
2018-01-06 06:30 | 66 | 66
2018-01-06 07:00 | 65 | 65
2018-01-06 07:30 | 67 | 67
2018-01-06 08:00 | 68 | 68
2018-01-06 08:30 | 68 | 68
2018-01-06 09:00 | 69 | 69
2018-01-06 09:30 | 69 | 69
2018-01-06 10:00 | 70 | 70
2018-01-06 10:30 | 70 | 70
2018-01-06 11:00 | 70 | 70
2018-01-06 11:30 | 69 | 69
2018-01-06 12:00 | 69 | 69
2018-01-06 12:30 | 70 | 70
2018-01-06 13:00 | 71 | 71
2018-01-06 13:30 | 70 | 70
2018-01-06 14:00 | 70 | 70
2018-01-06 14:30 | 72 | 72
2018-01-06 15:00 | 72 | 72
2018-01-06 15:30 | 72 | 72
2018-01-06 16:00 | 74 | 74
2018-01-06 16:30 | 76 | 76
2018-01-06 17:00 | 77 | 77
2018-01-06 17:30 | 75 | 75
2018-01-06 18:00 | 76 | 76
2018-01-06 18:30 | 76 | 76
2018-01-06 19:00 | 77 | 77
2018-01-06 19:30 | 77 | 77
2018-01-06 20:00 | 79 | 79
2018-01-06 20:30 | 78 | 78
2018-01-06 21:00 | 77 | 77
2018-01-06 21:30 | 76 | 76
2018-01-06 22:00 | 75 | 75
2018-01-06 22:30 | 74 | 74
2018-01-06 23:00 | 72 | 72
2018-01-06 23:30 | 71 | 71
2018-01-07 | 71 | 71
2018-01-07 00:30 | 70 | 70
2018-01-07 01:00 | 69 | 69
2018-01-07 01:30 | 70 | 70
2018-01-07 02:00 | 69 | 69
2018-01-07 02:30 | 68 | 68
2018-01-07 03:00 | 68 | 68
2018-01-07 03:30 | 68 | 68
2018-01-07 04:00 | 67 | 67
2018-01-07 04:30 | 67 | 67
2018-01-07 05:00 | 67 | 67
2018-01-07 05:30 | 67 | 67
2018-01-07 06:00 | 67 | 67
2018-01-07 06:30 | 66 | 66
2018-01-07 07:00 | 67 | 67
2018-01-07 07:30 | 68 | 68
2018-01-07 08:00 | 68 | 68
2018-01-07 08:30 | 69 | 69
2018-01-07 09:00 | 69 | 69
2018-01-07 09:30 | 69 | 69
2018-01-07 10:00 | 68 | 68
2018-01-07 10:30 | 70 | 70
2018-01-07 11:00 | 69 | 69
2018-01-07 11:30 | 70 | 70
2018-01-07 12:00 | 71 | 71
2018-01-07 12:30 | 71 | 71
2018-01-07 13:00 | 71 | 71
2018-01-07 13:30 | 71 | 71
2018-01-07 14:00 | 70 | 70
2018-01-07 14:30 | 71 | 71
2018-01-07 15:00 | 71 | 71
2018-01-07 15:30 | 66 | 65
2018-01-07 16:00 | 61 | 61
2018-01-07 16:30 | 61 | 61
2018-01-07 17:00 | 62 | 62
2018-01-07 17:30 | 63 | 63
2018-01-07 18:00 | 65 | 64
2018-01-07 18:30 | 65 | 64
2018-01-07 19:00 | 65 | 64
2018-01-07 19:30 | 66 | 66
2018-01-07 20:00 | 74 | 74
2018-01-07 20:30 | 78 | 78
2018-01-07 21:00 | 77 | 77
2018-01-07 21:30 | 76 | 76
2018-01-07 22:00 | 75 | 75
2018-01-07 22:30 | 73 | 73
2018-01-07 23:00 | 72 | 71
2018-01-07 23:30 | 71 | 71
2018-01-08 | 71 | 71
2018-01-08 00:30 | 70 | 70
2018-01-08 01:00 | 69 | 69
2018-01-08 01:30 | 69 | 69
2018-01-08 02:00 | 69 | 69
2018-01-08 02:30 | 69 | 69
2018-01-08 03:00 | 69 | 69
2018-01-08 03:30 | 68 | 68
2018-01-08 04:00 | 68 | 68
2018-01-08 04:30 | 69 | 69
2018-01-08 05:00 | 68 | 68
2018-01-08 05:30 | 68 | 68
2018-01-08 06:00 | 68 | 68
2018-01-08 06:30 | 69 | 69
2018-01-08 07:00 | 71 | 71
2018-01-08 07:30 | 73 | 73
2018-01-08 08:00 | 73 | 73
2018-01-08 08:30 | 74 | 74
2018-01-08 09:00 | 77 | 74
2018-01-08 09:30 | 76 | 74
2018-01-08 10:00 | 77 | 75
2018-01-08 10:30 | 78 | 76
2018-01-08 11:00 | 75 | 72
2018-01-08 11:30 | 77 | 76
2018-01-08 12:00 | 78 | 77
2018-01-08 12:30 | 78 | 77
2018-01-08 13:00 | 80 | 78
2018-01-08 13:30 | 76 | 72
2018-01-08 14:00 | 75 | 70
2018-01-08 14:30 | 75 | 70
2018-01-08 15:00 | 74 | 69
2018-01-08 15:30 | 74 | 68
2018-01-08 16:00 | 74 | 68
2018-01-08 16:30 | 74 | 67
2018-01-08 17:00 | 75 | 68
2018-01-08 17:30 | 75 | 68
2018-01-08 18:00 | 75 | 68
2018-01-08 18:30 | 77 | 74
2018-01-08 19:00 | 79 | 77
2018-01-08 19:30 | 80 | 78
2018-01-08 20:00 | 80 | 78
2018-01-08 20:30 | 77 | 75
2018-01-08 21:00 | 75 | 73
2018-01-08 21:30 | 74 | 72
2018-01-08 22:00 | 72 | 69
2018-01-08 22:30 | 72 | 68
2018-01-08 23:00 | 70 | 67
2018-01-08 23:30 | 70 | 68
2018-01-09 | 70 | 67
2018-01-09 00:30 | 69 | 67
2018-01-09 01:00 | 66 | 66
2018-01-09 01:30 | 65 | 65
2018-01-09 02:00 | 64 | 64
2018-01-09 02:30 | 65 | 65
2018-01-09 03:00 | 65 | 65
2018-01-09 03:30 | 63 | 63
2018-01-09 04:00 | 63 | 63
2018-01-09 04:30 | 64 | 64
2018-01-09 05:00 | 64 | 64
2018-01-09 05:30 | 64 | 64
2018-01-09 06:00 | 62 | 62
2018-01-09 06:30 | 63 | 63
2018-01-09 07:00 | 64 | 64
2018-01-09 07:30 | 66 | 66
2018-01-09 08:00 | 68 | 68
2018-01-09 08:30 | 69 | 68
2018-01-09 09:00 | 70 | 69
2018-01-09 09:30 | 69 | 68
2018-01-09 10:00 | 70 | 69
2018-01-09 10:30 | 70 | 69
2018-01-09 11:00 | 68 | 68
2018-01-09 11:30 | 69 | 69
2018-01-09 12:00 | 70 | 70
2018-01-09 12:30 | 70 | 70
2018-01-09 13:00 | 72 | 72
2018-01-09 13:30 | 72 | 72
2018-01-09 14:00 | 73 | 73
2018-01-09 14:30 | 74 | 74
2018-01-09 15:00 | 74 | 73
2018-01-09 15:30 | 75 | 74
2018-01-09 16:00 | 75 | 75
2018-01-09 16:30 | 76 | 75
2018-01-09 17:00 | 66 | 66
2018-01-09 17:30 | 63 | 63
2018-01-09 18:00 | 62 | 62
2018-01-09 18:30 | 72 | 72
2018-01-09 19:00 | 76 | 76
2018-01-09 19:30 | 78 | 77
2018-01-09 20:00 | 78 | 78
2018-01-09 20:30 | 77 | 77
2018-01-09 21:00 | 76 | 76
2018-01-09 21:30 | 75 | 74
2018-01-09 22:00 | 73 | 73
2018-01-09 22:30 | 72 | 72
2018-01-09 23:00 | 70 | 70
2018-01-09 23:30 | 70 | 70
2018-01-10 | 69 | 69
2018-01-10 00:30 | 67 | 67
2018-01-10 01:00 | 68 | 67
2018-01-10 01:30 | 67 | 67
2018-01-10 02:00 | 67 | 66
2018-01-10 02:30 | 66 | 66
2018-01-10 03:00 | 66 | 66
2018-01-10 03:30 | 65 | 65
2018-01-10 04:00 | 66 | 65
2018-01-10 04:30 | 65 | 65
2018-01-10 05:00 | 66 | 66
2018-01-10 05:30 | 66 | 66
2018-01-10 06:00 | 66 | 66
2018-01-10 06:30 | 66 | 66
2018-01-10 07:00 | 67 | 66
2018-01-10 07:30 | 68 | 68
2018-01-10 08:00 | 70 | 70
2018-01-10 08:30 | 73 | 71
2018-01-10 09:00 | 73 | 71
2018-01-10 09:30 | 73 | 71
2018-01-10 10:00 | 74 | 72
2018-01-10 10:30 | 74 | 73
2018-01-10 11:00 | 75 | 73
2018-01-10 11:30 | 74 | 72
2018-01-10 12:00 | 75 | 73
2018-01-10 12:30 | 76 | 74
2018-01-10 13:00 | 77 | 75
2018-01-10 13:30 | 69 | 65
2018-01-10 14:00 | 69 | 64
2018-01-10 14:30 | 69 | 65
2018-01-10 15:00 | 70 | 66
2018-01-10 15:30 | 70 | 66
2018-01-10 16:00 | 68 | 64
2018-01-10 16:30 | 70 | 66
2018-01-10 17:00 | 68 | 64
2018-01-10 17:30 | 70 | 66
2018-01-10 18:00 | 72 | 67
2018-01-10 18:30 | 72 | 68
2018-01-10 19:00 | 73 | 69
2018-01-10 19:30 | 74 | 71
2018-01-10 20:00 | 75 | 72
2018-01-10 20:30 | 78 | 77
2018-01-10 21:00 | 78 | 76
2018-01-10 21:30 | 77 | 75
2018-01-10 22:00 | 76 | 73
2018-01-10 22:30 | 75 | 72
2018-01-10 23:00 | 73 | 70
2018-01-10 23:30 | 73 | 69
2018-01-11 | 71 | 68
2018-01-11 00:30 | 70 | 68
2018-01-11 01:00 | 70 | 68
2018-01-11 01:30 | 70 | 68
2018-01-11 02:00 | 71 | 69
2018-01-11 02:30 | 71 | 68
2018-01-11 03:00 | 70 | 68
2018-01-11 03:30 | 69 | 66
2018-01-11 04:00 | 64 | 59
2018-01-11 04:30 | 59 | 49
2018-01-11 05:00 | 56 | 44
2018-01-11 05:30 | 51 | 39
2018-01-11 06:00 | 35 | 28
2018-01-11 06:30 | 34 | 28
2018-01-11 07:00 | 34 | 29
2018-01-11 07:30 | 36 | 33
2018-01-11 08:00 | 37 | 33
2018-01-11 08:30 | 39 | 34
2018-01-11 09:00 | 38 | 33
2018-01-11 09:30 | 38 | 32
2018-01-11 10:00 | 39 | 34
2018-01-11 10:30 | 39 | 34
2018-01-11 11:00 | 39 | 33
2018-01-11 11:30 | 38 | 34
2018-01-11 12:00 | 38 | 34
2018-01-11 12:30 | 39 | 35
2018-01-11 13:00 | 40 | 35
2018-01-11 13:30 | 40 | 36
2018-01-11 14:00 | 43 | 39
2018-01-11 14:30 | 41 | 36
2018-01-11 15:00 | 41 | 37
2018-01-11 15:30 | 43 | 39
2018-01-11 16:00 | 48 | 45
2018-01-11 16:30 | 48 | 45
2018-01-11 17:00 | 48 | 45
2018-01-11 17:30 | 49 | 46
2018-01-11 18:00 | 49 | 46
2018-01-11 18:30 | 48 | 46
2018-01-11 19:00 | 49 | 46
2018-01-11 19:30 | 49 | 47
2018-01-11 20:00 | 50 | 48
2018-01-11 20:30 | 44 | 42
2018-01-11 21:00 | 43 | 40
2018-01-11 21:30 | 44 | 40
2018-01-11 22:00 | 54 | 52
2018-01-11 22:30 | 57 | 56
2018-01-11 23:00 | 55 | 54
2018-01-11 23:30 | 57 | 57
2018-01-12 | 59 | 59
2018-01-12 00:30 | 60 | 60
2018-01-12 01:00 | 61 | 61
2018-01-12 01:30 | 62 | 62
2018-01-12 02:00 | 60 | 60
2018-01-12 02:30 | 61 | 61
2018-01-12 03:00 | 64 | 64
2018-01-12 03:30 | 64 | 64
2018-01-12 04:00 | 65 | 65
2018-01-12 04:30 | 65 | 65
2018-01-12 05:00 | 65 | 65
2018-01-12 05:30 | 66 | 66
2018-01-12 06:00 | 66 | 65
2018-01-12 06:30 | 68 | 68
2018-01-12 07:00 | 72 | 71
2018-01-12 07:30 | 73 | 73
2018-01-12 08:00 | 74 | 74
2018-01-12 08:30 | 76 | 76
2018-01-12 09:00 | 81 | 80
2018-01-12 09:30 | 82 | 80
2018-01-12 10:00 | 82 | 80
2018-01-12 10:30 | 83 | 82
2018-01-12 11:00 | 82 | 81
2018-01-12 11:30 | 80 | 79
2018-01-12 12:00 | 79 | 77
2018-01-12 12:30 | 78 | 77
2018-01-12 13:00 | 71 | 66
2018-01-12 13:30 | 68 | 62
2018-01-12 14:00 | 66 | 60
2018-01-12 14:30 | 62 | 53
2018-01-12 15:00 | 62 | 54
2018-01-12 15:30 | 54 | 51
2018-01-12 16:00 | 56 | 52
2018-01-12 16:30 | 56 | 53
2018-01-12 17:00 | 55 | 51
2018-01-12 17:30 | 54 | 50
2018-01-12 18:00 | 56 | 53
2018-01-12 18:30 | 62 | 61
2018-01-12 19:00 | 62 | 62
2018-01-12 19:30 | 63 | 63
2018-01-12 20:00 | 64 | 64
2018-01-12 20:30 | 71 | 71
2018-01-12 21:00 | 73 | 73
2018-01-12 21:30 | 73 | 72
2018-01-12 22:00 | 72 | 72
2018-01-12 22:30 | 62 | 62
2018-01-12 23:00 | 66 | 66
2018-01-12 23:30 | 68 | 67
2018-01-13 | 67 | 67
2018-01-13 00:30 | 66 | 66
2018-01-13 01:00 | 66 | 65
2018-01-13 01:30 | 66 | 66
2018-01-13 02:00 | 66 | 66
2018-01-13 02:30 | 66 | 66
2018-01-13 03:00 | 65 | 65
2018-01-13 03:30 | 65 | 65
2018-01-13 04:00 | 65 | 65
2018-01-13 04:30 | 65 | 64
2018-01-13 05:00 | 64 | 64
2018-01-13 05:30 | 62 | 62
2018-01-13 06:00 | 61 | 61
2018-01-13 06:30 | 62 | 62
2018-01-13 07:00 | 63 | 63
2018-01-13 07:30 | 64 | 64
2018-01-13 08:00 | 66 | 65
2018-01-13 08:30 | 66 | 66
2018-01-13 09:00 | 66 | 66
2018-01-13 09:30 | 67 | 66
2018-01-13 10:00 | 68 | 67
2018-01-13 10:30 | 68 | 67
2018-01-13 11:00 | 68 | 67
2018-01-13 11:30 | 67 | 66
2018-01-13 12:00 | 58 | 58
2018-01-13 12:30 | 53 | 53
2018-01-13 13:00 | 53 | 52
2018-01-13 13:30 | 58 | 58
2018-01-13 14:00 | 57 | 57
2018-01-13 14:30 | 53 | 52
2018-01-13 15:00 | 57 | 57
2018-01-13 15:30 | 59 | 59
2018-01-13 16:00 | 57 | 57
2018-01-13 16:30 | 44 | 41
2018-01-13 17:00 | 50 | 49
2018-01-13 17:30 | 54 | 53
2018-01-13 18:00 | 56 | 55
2018-01-13 18:30 | 56 | 55
2018-01-13 19:00 | 55 | 54
2018-01-13 19:30 | 72 | 72
2018-01-13 20:00 | 75 | 75
2018-01-13 20:30 | 76 | 75
2018-01-13 21:00 | 75 | 73
2018-01-13 21:30 | 73 | 72
2018-01-13 22:00 | 73 | 71
2018-01-13 22:30 | 72 | 70
2018-01-13 23:00 | 72 | 69
2018-01-13 23:30 | 72 | 69
2018-01-14 | 72 | 69
2018-01-14 00:30 | 68 | 68
2018-01-14 01:00 | 68 | 68
2018-01-14 01:30 | 70 | 69
2018-01-14 02:00 | 69 | 69
2018-01-14 02:30 | 69 | 69
2018-01-14 03:00 | 69 | 69
2018-01-14 03:30 | 69 | 69
2018-01-14 04:00 | 69 | 69
2018-01-14 04:30 | 69 | 69
2018-01-14 05:00 | 69 | 69
2018-01-14 05:30 | 67 | 67
2018-01-14 06:00 | 66 | 66
2018-01-14 06:30 | 66 | 66
2018-01-14 07:00 | 66 | 66
2018-01-14 07:30 | 66 | 66
2018-01-14 08:00 | 67 | 67
2018-01-14 08:30 | 67 | 67
2018-01-14 09:00 | 68 | 68
2018-01-14 09:30 | 68 | 68
2018-01-14 10:00 | 68 | 68
2018-01-14 10:30 | 68 | 68
2018-01-14 11:00 | 68 | 68
2018-01-14 11:30 | 69 | 69
2018-01-14 12:00 | 69 | 69
2018-01-14 12:30 | 71 | 71
2018-01-14 13:00 | 68 | 68
2018-01-14 13:30 | 62 | 61
2018-01-14 14:00 | 63 | 62
2018-01-14 14:30 | 46 | 46
2018-01-14 15:00 | 32 | 32
2018-01-14 15:30 | 18 | 9
2018-01-14 16:00 | 17 | 3
2018-01-14 16:30 | 16 | 2
2018-01-14 17:00 | 16 | 2
2018-01-14 17:30 | 16 | 3
2018-01-14 18:00 | 16 | 2
2018-01-14 18:30 | 29 | 27
2018-01-14 19:00 | 36 | 35
2018-01-14 19:30 | 37 | 37
2018-01-14 20:00 | 63 | 63
2018-01-14 20:30 | 76 | 76
2018-01-14 21:00 | 77 | 77
2018-01-14 21:30 | 76 | 76
2018-01-14 22:00 | 74 | 74
2018-01-14 22:30 | 72 | 72
2018-01-14 23:00 | 70 | 70
2018-01-14 23:30 | 70 | 70
2018-01-15 | 70 | 70
2018-01-15 00:30 | 68 | 68
2018-01-15 01:00 | 68 | 67
2018-01-15 01:30 | 67 | 67
2018-01-15 02:00 | 68 | 67
2018-01-15 02:30 | 68 | 67
2018-01-15 03:00 | 68 | 67
2018-01-15 03:30 | 68 | 67
2018-01-15 04:00 | 67 | 66
2018-01-15 04:30 | 68 | 67
2018-01-15 05:00 | 68 | 67
2018-01-15 05:30 | 67 | 66
2018-01-15 06:00 | 67 | 67
2018-01-15 06:30 | 68 | 68
2018-01-15 07:00 | 69 | 69
2018-01-15 07:30 | 71 | 71
2018-01-15 08:00 | 73 | 73
2018-01-15 08:30 | 78 | 74
2018-01-15 09:00 | 79 | 75
2018-01-15 09:30 | 79 | 75
2018-01-15 10:00 | 79 | 75
2018-01-15 10:30 | 79 | 75
2018-01-15 11:00 | 79 | 75
2018-01-15 11:30 | 78 | 74
2018-01-15 12:00 | 79 | 76
2018-01-15 12:30 | 81 | 78
2018-01-15 13:00 | 81 | 78
2018-01-15 13:30 | 77 | 72
2018-01-15 14:00 | 76 | 70
2018-01-15 14:30 | 77 | 71
2018-01-15 15:00 | 78 | 73
2018-01-15 15:30 | 78 | 74
2018-01-15 16:00 | 73 | 64
2018-01-15 16:30 | 72 | 60
2018-01-15 17:00 | 72 | 58
2018-01-15 17:30 | 70 | 56
2018-01-15 18:00 | 67 | 55
2018-01-15 18:30 | 68 | 56
2018-01-15 19:00 | 70 | 59
2018-01-15 19:30 | 69 | 58
2018-01-15 20:00 | 67 | 55
2018-01-15 20:30 | 71 | 59
2018-01-15 21:00 | 68 | 57
2018-01-15 21:30 | 56 | 54
2018-01-15 22:00 | 51 | 47
2018-01-15 22:30 | 49 | 44
2018-01-15 23:00 | 50 | 43
2018-01-15 23:30 | 49 | 42
2018-01-16 | 46 | 41
2018-01-16 00:30 | 41 | 41
2018-01-16 01:00 | 41 | 40
2018-01-16 01:30 | 41 | 40
2018-01-16 02:00 | 41 | 41
2018-01-16 02:30 | 41 | 41
2018-01-16 03:00 | 39 | 39
2018-01-16 03:30 | 41 | 41
2018-01-16 04:00 | 61 | 60
2018-01-16 04:30 | 62 | 61
2018-01-16 05:00 | 63 | 62
2018-01-16 05:30 | 63 | 62
2018-01-16 06:00 | 63 | 62
2018-01-16 06:30 | 62 | 62
2018-01-16 07:00 | 64 | 63
2018-01-16 07:30 | 66 | 65
2018-01-16 08:00 | 67 | 67
2018-01-16 08:30 | 67 | 67
2018-01-16 09:00 | 67 | 66
2018-01-16 09:30 | 68 | 67
2018-01-16 10:00 | 69 | 68
2018-01-16 10:30 | 69 | 68
2018-01-16 11:00 | 67 | 66
2018-01-16 11:30 | 65 | 64
2018-01-16 12:00 | 66 | 65
2018-01-16 12:30 | 67 | 66
2018-01-16 13:00 | 66 | 65
2018-01-16 13:30 | 60 | 56
2018-01-16 14:00 | 62 | 58
2018-01-16 14:30 | 62 | 58
2018-01-16 15:00 | 61 | 57
2018-01-16 15:30 | 65 | 61
2018-01-16 16:00 | 66 | 63
2018-01-16 16:30 | 66 | 63
2018-01-16 17:00 | 65 | 62
2018-01-16 17:30 | 66 | 62
2018-01-16 18:00 | 66 | 62
2018-01-16 18:30 | 66 | 63
2018-01-16 19:00 | 67 | 63
2018-01-16 19:30 | 67 | 64
2018-01-16 20:00 | 68 | 65
2018-01-16 20:30 | 74 | 72
2018-01-16 21:00 | 74 | 72
2018-01-16 21:30 | 73 | 71
2018-01-16 22:00 | 72 | 70
2018-01-16 22:30 | 71 | 68
2018-01-16 23:00 | 69 | 67
2018-01-16 23:30 | 70 | 68
2018-01-17 | 69 | 67
2018-01-17 00:30 | 68 | 66
2018-01-17 01:00 | 68 | 65
2018-01-17 01:30 | 68 | 66
2018-01-17 02:00 | 67 | 66
2018-01-17 02:30 | 66 | 65
2018-01-17 03:00 | 67 | 65
2018-01-17 03:30 | 68 | 66
2018-01-17 04:00 | 68 | 67
2018-01-17 04:30 | 68 | 67
2018-01-17 05:00 | 68 | 67
2018-01-17 05:30 | 66 | 65
2018-01-17 06:00 | 66 | 65
2018-01-17 06:30 | 66 | 65
2018-01-17 07:00 | 67 | 66
2018-01-17 07:30 | 68 | 68
2018-01-17 08:00 | 69 | 69
2018-01-17 08:30 | 70 | 70
2018-01-17 09:00 | 71 | 71
2018-01-17 09:30 | 72 | 72
2018-01-17 10:00 | 73 | 73
2018-01-17 10:30 | 72 | 72
2018-01-17 11:00 | 72 | 72
2018-01-17 11:30 | 73 | 72
2018-01-17 12:00 | 75 | 75
2018-01-17 12:30 | 75 | 75
2018-01-17 13:00 | 75 | 75
2018-01-17 13:30 | 75 | 75
2018-01-17 14:00 | 67 | 66
2018-01-17 14:30 | 70 | 69
2018-01-17 15:00 | 69 | 68
2018-01-17 15:30 | 69 | 68
2018-01-17 16:00 | 67 | 67
2018-01-17 16:30 | 68 | 67
2018-01-17 17:00 | 68 | 67
2018-01-17 17:30 | 69 | 67
2018-01-17 18:00 | 69 | 67
2018-01-17 18:30 | 68 | 66
2018-01-17 19:00 | 69 | 67
2018-01-17 19:30 | 69 | 68
2018-01-17 20:00 | 69 | 67
2018-01-17 20:30 | 73 | 72
2018-01-17 21:00 | 73 | 73
2018-01-17 21:30 | 72 | 72
2018-01-17 22:00 | 70 | 70
2018-01-17 22:30 | 69 | 68
2018-01-17 23:00 | 66 | 65
2018-01-17 23:30 | 65 | 64
2018-01-18 | 64 | 63
2018-01-18 00:30 | 64 | 63
2018-01-18 01:00 | 64 | 63
2018-01-18 01:30 | 64 | 62
2018-01-18 02:00 | 63 | 62
2018-01-18 02:30 | 63 | 62
2018-01-18 03:00 | 63 | 62
2018-01-18 03:30 | 61 | 60
2018-01-18 04:00 | 61 | 60
2018-01-18 04:30 | 62 | 60
2018-01-18 05:00 | 62 | 61
2018-01-18 05:30 | 63 | 61
2018-01-18 06:00 | 63 | 62
2018-01-18 06:30 | 63 | 62
2018-01-18 07:00 | 63 | 62
2018-01-18 07:30 | 64 | 63
2018-01-18 08:00 | 64 | 64
2018-01-18 08:30 | 65 | 64
2018-01-18 09:00 | 68 | 67
2018-01-18 09:30 | 69 | 69
2018-01-18 10:00 | 69 | 69
2018-01-18 10:30 | 71 | 70
2018-01-18 11:00 | 69 | 69
2018-01-18 11:30 | 69 | 69
2018-01-18 12:00 | 69 | 69
2018-01-18 12:30 | 70 | 70
2018-01-18 13:00 | 70 | 70
2018-01-18 13:30 | 70 | 69
2018-01-18 14:00 | 64 | 63
2018-01-18 14:30 | 63 | 62
2018-01-18 15:00 | 63 | 61
2018-01-18 15:30 | 59 | 58
2018-01-18 16:00 | 56 | 53
2018-01-18 16:30 | 57 | 53
2018-01-18 17:00 | 55 | 50
2018-01-18 17:30 | 57 | 52
2018-01-18 18:00 | 66 | 64
2018-01-18 18:30 | 72 | 71
2018-01-18 19:00 | 73 | 72
2018-01-18 19:30 | 74 | 73
2018-01-18 20:00 | 75 | 74
2018-01-18 20:30 | 74 | 74
2018-01-18 21:00 | 73 | 73
2018-01-18 21:30 | 69 | 68
2018-01-18 22:00 | 68 | 67
2018-01-18 22:30 | 66 | 66
2018-01-18 23:00 | 66 | 65
2018-01-18 23:30 | 63 | 63
2018-01-19 | 62 | 62
2018-01-19 00:30 | 61 | 61
2018-01-19 01:00 | 61 | 60
2018-01-19 01:30 | 62 | 62
2018-01-19 02:00 | 61 | 61
2018-01-19 02:30 | 61 | 61
2018-01-19 03:00 | 61 | 61
2018-01-19 03:30 | 61 | 60
2018-01-19 04:00 | 60 | 60
2018-01-19 04:30 | 60 | 60
2018-01-19 05:00 | 59 | 59
2018-01-19 05:30 | 59 | 59
2018-01-19 06:00 | 59 | 59
2018-01-19 06:30 | 61 | 61
2018-01-19 07:00 | 63 | 63
2018-01-19 07:30 | 65 | 64
2018-01-19 08:00 | 64 | 64
2018-01-19 08:30 | 65 | 64
2018-01-19 09:00 | 67 | 65
2018-01-19 09:30 | 68 | 67
2018-01-19 10:00 | 72 | 71
2018-01-19 10:30 | 72 | 71
2018-01-19 11:00 | 70 | 69
2018-01-19 11:30 | 68 | 67
2018-01-19 12:00 | 66 | 65
2018-01-19 12:30 | 66 | 66
2018-01-19 13:00 | 65 | 65
2018-01-19 13:30 | 64 | 63
2018-01-19 14:00 | 63 | 62
2018-01-19 14:30 | 65 | 64
2018-01-19 15:00 | 66 | 65
2018-01-19 15:30 | 69 | 65
2018-01-19 16:00 | 66 | 62
2018-01-19 16:30 | 66 | 62
2018-01-19 17:00 | 63 | 59
2018-01-19 17:30 | 61 | 58
2018-01-19 18:00 | 62 | 58
2018-01-19 18:30 | 62 | 59
2018-01-19 19:00 | 62 | 59
2018-01-19 19:30 | 62 | 59
2018-01-19 20:00 | 63 | 60
2018-01-19 20:30 | 68 | 66
2018-01-19 21:00 | 68 | 67
2018-01-19 21:30 | 68 | 66
2018-01-19 22:00 | 66 | 65
2018-01-19 22:30 | 66 | 65
2018-01-19 23:00 | 67 | 66
2018-01-19 23:30 | 64 | 64
2018-01-20 | 63 | 63
2018-01-20 00:30 | 64 | 63
2018-01-20 01:00 | 63 | 62
2018-01-20 01:30 | 63 | 62
2018-01-20 02:00 | 62 | 62
2018-01-20 02:30 | 62 | 61
2018-01-20 03:00 | 61 | 60
2018-01-20 03:30 | 61 | 60
2018-01-20 04:00 | 60 | 59
2018-01-20 04:30 | 59 | 59
2018-01-20 05:00 | 60 | 60
2018-01-20 05:30 | 60 | 60
2018-01-20 06:00 | 59 | 59
2018-01-20 06:30 | 59 | 59
2018-01-20 07:00 | 59 | 59
2018-01-20 07:30 | 59 | 59
2018-01-20 08:00 | 60 | 60
2018-01-20 08:30 | 61 | 61
2018-01-20 09:00 | 61 | 61
2018-01-20 09:30 | 61 | 61
2018-01-20 10:00 | 61 | 61
2018-01-20 10:30 | 69 | 68
2018-01-20 11:00 | 69 | 69
2018-01-20 11:30 | 68 | 68
2018-01-20 12:00 | 69 | 69
2018-01-20 12:30 | 68 | 68
2018-01-20 13:00 | 66 | 65
2018-01-20 13:30 | 56 | 56
2018-01-20 14:00 | 55 | 55
2018-01-20 14:30 | 55 | 55
2018-01-20 15:00 | 55 | 55
2018-01-20 15:30 | 56 | 56
2018-01-20 16:00 | 56 | 56
2018-01-20 16:30 | 57 | 57
2018-01-20 17:00 | 59 | 59
2018-01-20 17:30 | 59 | 59
2018-01-20 18:00 | 58 | 58
2018-01-20 18:30 | 59 | 59
2018-01-20 19:00 | 59 | 59
2018-01-20 19:30 | 60 | 60
2018-01-20 20:00 | 60 | 60
2018-01-20 20:30 | 67 | 67
2018-01-20 21:00 | 68 | 67
2018-01-20 21:30 | 66 | 66
2018-01-20 22:00 | 66 | 66
2018-01-20 22:30 | 64 | 64
2018-01-20 23:00 | 63 | 63
2018-01-20 23:30 | 62 | 62
2018-01-21 | 61 | 61
2018-01-21 00:30 | 60 | 60
2018-01-21 01:00 | 60 | 60
2018-01-21 01:30 | 60 | 60
2018-01-21 02:00 | 59 | 59
2018-01-21 02:30 | 59 | 59
2018-01-21 03:00 | 59 | 59
2018-01-21 03:30 | 58 | 58
2018-01-21 04:00 | 57 | 57
2018-01-21 04:30 | 58 | 58
2018-01-21 05:00 | 58 | 58
2018-01-21 05:30 | 57 | 57
2018-01-21 06:00 | 56 | 56
2018-01-21 06:30 | 57 | 57
2018-01-21 07:00 | 59 | 59
2018-01-21 07:30 | 60 | 60
2018-01-21 08:00 | 61 | 61
2018-01-21 08:30 | 61 | 61
2018-01-21 09:00 | 61 | 61
2018-01-21 09:30 | 61 | 61
2018-01-21 10:00 | 63 | 63
2018-01-21 10:30 | 63 | 63
2018-01-21 11:00 | 64 | 63
2018-01-21 11:30 | 63 | 63
2018-01-21 12:00 | 63 | 63
2018-01-21 12:30 | 64 | 63
2018-01-21 13:00 | 63 | 63
2018-01-21 13:30 | 56 | 56
2018-01-21 14:00 | 56 | 56
2018-01-21 14:30 | 54 | 54
2018-01-21 15:00 | 53 | 53
2018-01-21 15:30 | 55 | 55
2018-01-21 16:00 | 57 | 57
2018-01-21 16:30 | 57 | 57
2018-01-21 17:00 | 57 | 57
2018-01-21 17:30 | 55 | 55
2018-01-21 18:00 | 54 | 54
2018-01-21 18:30 | 56 | 56
2018-01-21 19:00 | 56 | 56
2018-01-21 19:30 | 58 | 58
2018-01-21 20:00 | 63 | 63
2018-01-21 20:30 | 72 | 71
2018-01-21 21:00 | 72 | 71
2018-01-21 21:30 | 71 | 70
2018-01-21 22:00 | 68 | 67
2018-01-21 22:30 | 67 | 66
2018-01-21 23:00 | 65 | 65
2018-01-21 23:30 | 64 | 64
2018-01-22 | 64 | 64
2018-01-22 00:30 | 64 | 63
2018-01-22 01:00 | 63 | 63
2018-01-22 01:30 | 63 | 63
2018-01-22 02:00 | 62 | 62
2018-01-22 02:30 | 62 | 62
2018-01-22 03:00 | 61 | 61
2018-01-22 03:30 | 62 | 62
2018-01-22 04:00 | 62 | 62
2018-01-22 04:30 | 62 | 62
2018-01-22 05:00 | 62 | 62
2018-01-22 05:30 | 63 | 63
2018-01-22 06:00 | 65 | 65
2018-01-22 06:30 | 65 | 65
2018-01-22 07:00 | 67 | 67
2018-01-22 07:30 | 68 | 68
2018-01-22 08:00 | 69 | 69
2018-01-22 08:30 | 67 | 66
2018-01-22 09:00 | 66 | 65
2018-01-22 09:30 | 65 | 65
2018-01-22 10:00 | 65 | 65
2018-01-22 10:30 | 65 | 65
2018-01-22 11:00 | 66 | 66
2018-01-22 11:30 | 66 | 65
2018-01-22 12:00 | 66 | 66
2018-01-22 12:30 | 66 | 65
2018-01-22 13:00 | 65 | 65
2018-01-22 13:30 | 56 | 56
2018-01-22 14:00 | 56 | 55
2018-01-22 14:30 | 57 | 57
2018-01-22 15:00 | 58 | 57
2018-01-22 15:30 | 57 | 57
2018-01-22 16:00 | 55 | 54
2018-01-22 16:30 | 54 | 54
2018-01-22 17:00 | 57 | 56
2018-01-22 17:30 | 60 | 58
2018-01-22 18:00 | 61 | 59
2018-01-22 18:30 | 61 | 59
2018-01-22 19:00 | 61 | 59
2018-01-22 19:30 | 62 | 60
2018-01-22 20:00 | 63 | 61
2018-01-22 20:30 | 69 | 68
2018-01-22 21:00 | 69 | 69
2018-01-22 21:30 | 68 | 68
2018-01-22 22:00 | 67 | 67
2018-01-22 22:30 | 65 | 65
2018-01-22 23:00 | 65 | 64
2018-01-22 23:30 | 64 | 63
2018-01-23 | 64 | 63
2018-01-23 00:30 | 63 | 62
2018-01-23 01:00 | 63 | 62
2018-01-23 01:30 | 64 | 63
2018-01-23 02:00 | 62 | 62
2018-01-23 02:30 | 62 | 61
2018-01-23 03:00 | 62 | 61
2018-01-23 03:30 | 61 | 61
2018-01-23 04:00 | 62 | 61
2018-01-23 04:30 | 62 | 61
2018-01-23 05:00 | 62 | 61
2018-01-23 05:30 | 62 | 61
2018-01-23 06:00 | 62 | 61
2018-01-23 06:30 | 63 | 62
2018-01-23 07:00 | 65 | 64
2018-01-23 07:30 | 66 | 65
2018-01-23 08:00 | 70 | 69
2018-01-23 08:30 | 70 | 69
2018-01-23 09:00 | 70 | 69
2018-01-23 09:30 | 71 | 69
2018-01-23 10:00 | 72 | 71
2018-01-23 10:30 | 73 | 71
2018-01-23 11:00 | 75 | 73
2018-01-23 11:30 | 74 | 72
2018-01-23 12:00 | 73 | 71
2018-01-23 12:30 | 73 | 71
2018-01-23 13:00 | 75 | 73
2018-01-23 13:30 | 67 | 66
2018-01-23 14:00 | 68 | 67
2018-01-23 14:30 | 67 | 66
2018-01-23 15:00 | 65 | 64
2018-01-23 15:30 | 65 | 64
2018-01-23 16:00 | 66 | 66
2018-01-23 16:30 | 65 | 65
2018-01-23 17:00 | 64 | 64
2018-01-23 17:30 | 63 | 63
2018-01-23 18:00 | 63 | 63
2018-01-23 18:30 | 67 | 66
2018-01-23 19:00 | 73 | 73
2018-01-23 19:30 | 73 | 72
2018-01-23 20:00 | 73 | 72
2018-01-23 20:30 | 74 | 73
2018-01-23 21:00 | 73 | 72
2018-01-23 21:30 | 71 | 70
2018-01-23 22:00 | 71 | 70
2018-01-23 22:30 | 70 | 69
2018-01-23 23:00 | 68 | 67
2018-01-23 23:30 | 67 | 66
2018-01-24 | 66 | 65
2018-01-24 00:30 | 66 | 65
2018-01-24 01:00 | 65 | 64
2018-01-24 01:30 | 65 | 64
2018-01-24 02:00 | 64 | 63
2018-01-24 02:30 | 63 | 62
2018-01-24 03:00 | 63 | 63
2018-01-24 03:30 | 64 | 63
2018-01-24 04:00 | 64 | 63
2018-01-24 04:30 | 63 | 63
2018-01-24 05:00 | 63 | 62
2018-01-24 05:30 | 63 | 62
2018-01-24 06:00 | 64 | 62
2018-01-24 06:30 | 64 | 62
2018-01-24 07:00 | 65 | 64
2018-01-24 07:30 | 67 | 65
2018-01-24 08:00 | 70 | 69
2018-01-24 08:30 | 69 | 68
2018-01-24 09:00 | 70 | 70
2018-01-24 09:30 | 70 | 70
2018-01-24 10:00 | 71 | 71
2018-01-24 10:30 | 72 | 72
2018-01-24 11:00 | 72 | 72
2018-01-24 11:30 | 72 | 72
2018-01-24 12:00 | 73 | 72
2018-01-24 12:30 | 72 | 72
2018-01-24 13:00 | 72 | 72
2018-01-24 13:30 | 63 | 63
2018-01-24 14:00 | 57 | 57
2018-01-24 14:30 | 56 | 56
2018-01-24 15:00 | 57 | 57
2018-01-24 15:30 | 59 | 58
2018-01-24 16:00 | 59 | 59
2018-01-24 16:30 | 59 | 59
2018-01-24 17:00 | 64 | 64
2018-01-24 17:30 | 63 | 63
2018-01-24 18:00 | 63 | 63
2018-01-24 18:30 | 68 | 68
2018-01-24 19:00 | 74 | 73
2018-01-24 19:30 | 75 | 74
2018-01-24 20:00 | 74 | 73
2018-01-24 20:30 | 75 | 74
2018-01-24 21:00 | 75 | 74
2018-01-24 21:30 | 74 | 73
2018-01-24 22:00 | 72 | 72
2018-01-24 22:30 | 70 | 69
2018-01-24 23:00 | 70 | 69
2018-01-24 23:30 | 73 | 72
2018-01-25 | 71 | 70
2018-01-25 00:30 | 68 | 67
2018-01-25 01:00 | 67 | 67
2018-01-25 01:30 | 67 | 66
2018-01-25 02:00 | 67 | 66
2018-01-25 02:30 | 66 | 66
2018-01-25 03:00 | 66 | 65
2018-01-25 03:30 | 65 | 65
2018-01-25 04:00 | 65 | 65
2018-01-25 04:30 | 66 | 65
2018-01-25 05:00 | 65 | 65
2018-01-25 05:30 | 66 | 66
2018-01-25 06:00 | 66 | 66
2018-01-25 06:30 | 67 | 66
2018-01-25 07:00 | 69 | 69
2018-01-25 07:30 | 72 | 72
2018-01-25 08:00 | 74 | 73
2018-01-25 08:30 | 73 | 72
2018-01-25 09:00 | 73 | 73
2018-01-25 09:30 | 73 | 72
2018-01-25 10:00 | 73 | 72
2018-01-25 10:30 | 71 | 70
2018-01-25 11:00 | 73 | 73
2018-01-25 11:30 | 72 | 71
2018-01-25 12:00 | 67 | 66
2018-01-25 12:30 | 71 | 71
2018-01-25 13:00 | 71 | 71
2018-01-25 13:30 | 68 | 68
2018-01-25 14:00 | 66 | 65
2018-01-25 14:30 | 63 | 61
2018-01-25 15:00 | 61 | 58
2018-01-25 15:30 | 65 | 63
2018-01-25 16:00 | 64 | 61
2018-01-25 16:30 | 66 | 64
2018-01-25 17:00 | 72 | 72
2018-01-25 17:30 | 74 | 73
2018-01-25 18:00 | 75 | 74
2018-01-25 18:30 | 74 | 74
2018-01-25 19:00 | 74 | 74
2018-01-25 19:30 | 75 | 75
2018-01-25 20:00 | 75 | 75
2018-01-25 20:30 | 75 | 74
2018-01-25 21:00 | 73 | 72
2018-01-25 21:30 | 73 | 73
2018-01-25 22:00 | 73 | 72
2018-01-25 22:30 | 71 | 70
2018-01-25 23:00 | 70 | 69
2018-01-25 23:30 | 70 | 69
2018-01-26 | 68 | 68
2018-01-26 00:30 | 68 | 68
2018-01-26 01:00 | 68 | 67
2018-01-26 01:30 | 67 | 66
2018-01-26 02:00 | 66 | 65
2018-01-26 02:30 | 66 | 65
2018-01-26 03:00 | 65 | 65
2018-01-26 03:30 | 65 | 64
2018-01-26 04:00 | 65 | 64
2018-01-26 04:30 | 66 | 66
2018-01-26 05:00 | 67 | 67
2018-01-26 05:30 | 67 | 67
2018-01-26 06:00 | 67 | 67
2018-01-26 06:30 | 67 | 67
2018-01-26 07:00 | 68 | 67
2018-01-26 07:30 | 70 | 70
2018-01-26 08:00 | 70 | 70
2018-01-26 08:30 | 70 | 70
2018-01-26 09:00 | 70 | 70
2018-01-26 09:30 | 72 | 71
2018-01-26 10:00 | 72 | 71
2018-01-26 10:30 | 71 | 71
2018-01-26 11:00 | 71 | 70
2018-01-26 11:30 | 71 | 71
2018-01-26 12:00 | 69 | 68
2018-01-26 12:30 | 68 | 67
2018-01-26 13:00 | 70 | 69
2018-01-26 13:30 | 70 | 70
2018-01-26 14:00 | 70 | 69
2018-01-26 14:30 | 70 | 70
2018-01-26 15:00 | 71 | 71
2018-01-26 15:30 | 72 | 72
2018-01-26 16:00 | 73 | 73
2018-01-26 16:30 | 74 | 74
2018-01-26 17:00 | 75 | 74
2018-01-26 17:30 | 75 | 75
2018-01-26 18:00 | 75 | 75
2018-01-26 18:30 | 75 | 74
2018-01-26 19:00 | 75 | 75
2018-01-26 19:30 | 75 | 75
2018-01-26 20:00 | 75 | 75
2018-01-26 20:30 | 74 | 74
2018-01-26 21:00 | 73 | 73
2018-01-26 21:30 | 73 | 73
2018-01-26 22:00 | 74 | 73
2018-01-26 22:30 | 72 | 72
2018-01-26 23:00 | 71 | 70
2018-01-26 23:30 | 70 | 69
2018-01-27 | 69 | 68
2018-01-27 00:30 | 68 | 68
2018-01-27 01:00 | 68 | 68
2018-01-27 01:30 | 68 | 67
2018-01-27 02:00 | 68 | 67
2018-01-27 02:30 | 68 | 67
2018-01-27 03:00 | 68 | 67
2018-01-27 03:30 | 68 | 67
2018-01-27 04:00 | 67 | 66
2018-01-27 04:30 | 66 | 65
2018-01-27 05:00 | 66 | 65
2018-01-27 05:30 | 67 | 66
2018-01-27 06:00 | 67 | 66
2018-01-27 06:30 | 66 | 65
2018-01-27 07:00 | 66 | 65
2018-01-27 07:30 | 68 | 67
2018-01-27 08:00 | 69 | 69
2018-01-27 08:30 | 69 | 68
2018-01-27 09:00 | 69 | 69
2018-01-27 09:30 | 69 | 69
2018-01-27 10:00 | 69 | 69
2018-01-27 10:30 | 70 | 69
2018-01-27 11:00 | 69 | 69
2018-01-27 11:30 | 70 | 70
2018-01-27 12:00 | 70 | 70
2018-01-27 12:30 | 70 | 70
2018-01-27 13:00 | 70 | 70
2018-01-27 13:30 | 70 | 69
2018-01-27 14:00 | 70 | 70
2018-01-27 14:30 | 71 | 70
2018-01-27 15:00 | 71 | 71
2018-01-27 15:30 | 70 | 69
2018-01-27 16:00 | 69 | 68
2018-01-27 16:30 | 69 | 68
2018-01-27 17:00 | 66 | 64
2018-01-27 17:30 | 71 | 71
2018-01-27 18:00 | 73 | 72
2018-01-27 18:30 | 71 | 71
2018-01-27 19:00 | 71 | 71
2018-01-27 19:30 | 75 | 75
2018-01-27 20:00 | 76 | 76
2018-01-27 20:30 | 75 | 75
2018-01-27 21:00 | 74 | 74
2018-01-27 21:30 | 74 | 74
2018-01-27 22:00 | 73 | 73
2018-01-27 22:30 | 72 | 72
2018-01-27 23:00 | 72 | 71
2018-01-27 23:30 | 70 | 70
2018-01-28 | 70 | 69
2018-01-28 00:30 | 69 | 68
2018-01-28 01:00 | 68 | 67
2018-01-28 01:30 | 67 | 67
2018-01-28 02:00 | 67 | 66
2018-01-28 02:30 | 67 | 66
2018-01-28 03:00 | 67 | 66
2018-01-28 03:30 | 67 | 66
2018-01-28 04:00 | 66 | 65
2018-01-28 04:30 | 66 | 65
2018-01-28 05:00 | 66 | 65
2018-01-28 05:30 | 65 | 64
2018-01-28 06:00 | 64 | 63
2018-01-28 06:30 | 65 | 64
2018-01-28 07:00 | 65 | 64
2018-01-28 07:30 | 68 | 67
2018-01-28 08:00 | 68 | 67
2018-01-28 08:30 | 69 | 67
2018-01-28 09:00 | 69 | 68
2018-01-28 09:30 | 68 | 67
2018-01-28 10:00 | 68 | 68
2018-01-28 10:30 | 69 | 69
2018-01-28 11:00 | 69 | 69
2018-01-28 11:30 | 70 | 69
2018-01-28 12:00 | 70 | 70
2018-01-28 12:30 | 70 | 70
2018-01-28 13:00 | 70 | 70
2018-01-28 13:30 | 71 | 71
2018-01-28 14:00 | 71 | 71
2018-01-28 14:30 | 65 | 63
2018-01-28 15:00 | 66 | 65
2018-01-28 15:30 | 67 | 66
2018-01-28 16:00 | 64 | 62
2018-01-28 16:30 | 67 | 65
2018-01-28 17:00 | 69 | 68
2018-01-28 17:30 | 70 | 69
2018-01-28 18:00 | 69 | 68
2018-01-28 18:30 | 69 | 68
2018-01-28 19:00 | 71 | 69
2018-01-28 19:30 | 77 | 77
2018-01-28 20:00 | 78 | 78
2018-01-28 20:30 | 77 | 77
2018-01-28 21:00 | 76 | 76
2018-01-28 21:30 | 75 | 75
2018-01-28 22:00 | 74 | 73
2018-01-28 22:30 | 70 | 70
2018-01-28 23:00 | 69 | 69
2018-01-28 23:30 | 68 | 67
2018-01-29 | 67 | 66
2018-01-29 00:30 | 67 | 67
2018-01-29 01:00 | 67 | 67
2018-01-29 01:30 | 66 | 66
2018-01-29 02:00 | 65 | 65
2018-01-29 02:30 | 65 | 64
2018-01-29 03:00 | 65 | 64
2018-01-29 03:30 | 64 | 64
2018-01-29 04:00 | 64 | 64
2018-01-29 04:30 | 65 | 64
2018-01-29 05:00 | 64 | 64
2018-01-29 05:30 | 64 | 64
2018-01-29 06:00 | 65 | 64
2018-01-29 06:30 | 65 | 65
2018-01-29 07:00 | 66 | 66
2018-01-29 07:30 | 69 | 69
2018-01-29 08:00 | 71 | 71
2018-01-29 08:30 | 65 | 64
2018-01-29 09:00 | 73 | 73
2018-01-29 09:30 | 74 | 74
2018-01-29 10:00 | 74 | 74
2018-01-29 10:30 | 74 | 74
2018-01-29 11:00 | 73 | 73
2018-01-29 11:30 | 71 | 71
2018-01-29 12:00 | 70 | 70
2018-01-29 12:30 | 70 | 70
2018-01-29 13:00 | 70 | 70
2018-01-29 13:30 | 65 | 65
2018-01-29 14:00 | 69 | 69
2018-01-29 14:30 | 70 | 69
2018-01-29 15:00 | 71 | 71
2018-01-29 15:30 | 71 | 71
2018-01-29 16:00 | 72 | 72
2018-01-29 16:30 | 73 | 73
2018-01-29 17:00 | 73 | 73
2018-01-29 17:30 | 73 | 73
2018-01-29 18:00 | 74 | 74
2018-01-29 18:30 | 75 | 75
2018-01-29 19:00 | 76 | 76
2018-01-29 19:30 | 77 | 77
2018-01-29 20:00 | 77 | 77
2018-01-29 20:30 | 76 | 76
2018-01-29 21:00 | 75 | 75
2018-01-29 21:30 | 74 | 74
2018-01-29 22:00 | 72 | 72
2018-01-29 22:30 | 70 | 70
2018-01-29 23:00 | 69 | 69
2018-01-29 23:30 | 68 | 68
2018-01-30 | 66 | 66
2018-01-30 00:30 | 66 | 65
2018-01-30 01:00 | 65 | 64
2018-01-30 01:30 | 65 | 64
2018-01-30 02:00 | 64 | 64
2018-01-30 02:30 | 64 | 63
2018-01-30 03:00 | 64 | 63
2018-01-30 03:30 | 63 | 62
2018-01-30 04:00 | 63 | 62
2018-01-30 04:30 | 63 | 62
2018-01-30 05:00 | 64 | 62
2018-01-30 05:30 | 63 | 61
2018-01-30 06:00 | 64 | 62
2018-01-30 06:30 | 66 | 63
2018-01-30 07:00 | 67 | 65
2018-01-30 07:30 | 69 | 67
2018-01-30 08:00 | 69 | 67
2018-01-30 08:30 | 68 | 67
2018-01-30 09:00 | 69 | 68
2018-01-30 09:30 | 69 | 68
2018-01-30 10:00 | 67 | 67
2018-01-30 10:30 | 68 | 68
2018-01-30 11:00 | 66 | 65
2018-01-30 11:30 | 68 | 68
2018-01-30 12:00 | 69 | 68
2018-01-30 12:30 | 69 | 69
2018-01-30 13:00 | 68 | 68
2018-01-30 13:30 | 69 | 68
2018-01-30 14:00 | 71 | 71
2018-01-30 14:30 | 71 | 71
2018-01-30 15:00 | 61 | 60
2018-01-30 15:30 | 64 | 63
2018-01-30 16:00 | 63 | 61
2018-01-30 16:30 | 63 | 61
2018-01-30 17:00 | 64 | 62
2018-01-30 17:30 | 72 | 71
2018-01-30 18:00 | 74 | 74
2018-01-30 18:30 | 75 | 74
2018-01-30 19:00 | 69 | 68
2018-01-30 19:30 | 64 | 62
2018-01-30 20:00 | 64 | 62
2018-01-30 20:30 | 63 | 61
2018-01-30 21:00 | 62 | 60
2018-01-30 21:30 | 58 | 57
2018-01-30 22:00 | 57 | 56
2018-01-30 22:30 | 56 | 55
2018-01-30 23:00 | 55 | 54
2018-01-30 23:30 | 58 | 58
2018-01-31 | 60 | 58
2018-01-31 00:30 | 66 | 63
2018-01-31 01:00 | 66 | 63
2018-01-31 01:30 | 65 | 62
2018-01-31 02:00 | 65 | 62
2018-01-31 02:30 | 65 | 62
2018-01-31 03:00 | 65 | 62
2018-01-31 03:30 | 64 | 62
2018-01-31 04:00 | 64 | 61
2018-01-31 04:30 | 64 | 61
2018-01-31 05:00 | 63 | 61
2018-01-31 05:30 | 64 | 62
2018-01-31 06:00 | 64 | 62
2018-01-31 06:30 | 65 | 62
2018-01-31 07:00 | 65 | 63
2018-01-31 07:30 | 61 | 60
2018-01-31 08:00 | 57 | 57
2018-01-31 08:30 | 48 | 47
2018-01-31 09:00 | 50 | 48
2018-01-31 09:30 | 50 | 47
2018-01-31 10:00 | 51 | 48
2018-01-31 10:30 | 51 | 48
2018-01-31 11:00 | 51 | 48
2018-01-31 11:30 | 51 | 48
2018-01-31 12:00 | 51 | 49
2018-01-31 12:30 | 52 | 50
2018-01-31 13:00 | 52 | 49
2018-01-31 13:30 | 51 | 48
2018-01-31 14:00 | 54 | 52
2018-01-31 14:30 | 61 | 60
2018-01-31 15:00 | 61 | 60
2018-01-31 15:30 | 63 | 62
2018-01-31 16:00 | 66 | 65
2018-01-31 16:30 | 70 | 70
2018-01-31 17:00 | 71 | 71
2018-01-31 17:30 | 71 | 71
2018-01-31 18:00 | 72 | 72
2018-01-31 18:30 | 73 | 73
2018-01-31 19:00 | 73 | 72
2018-01-31 19:30 | 72 | 72
2018-01-31 20:00 | 72 | 72
2018-01-31 20:30 | 76 | 76
2018-01-31 21:00 | 75 | 75
2018-01-31 21:30 | 74 | 74
2018-01-31 22:00 | 71 | 71
2018-01-31 22:30 | 68 | 68
2018-01-31 23:00 | 71 | 71
2018-01-31 23:30 | 68 | 68
2018-02-01 | 67 | 67
2018-02-01 00:30 | 70 | 69
2018-02-01 01:00 | 69 | 68
2018-02-01 01:30 | 68 | 67
2018-02-01 02:00 | 67 | 66
2018-02-01 02:30 | 66 | 66
2018-02-01 03:00 | 66 | 65
2018-02-01 03:30 | 65 | 65
2018-02-01 04:00 | 65 | 65
2018-02-01 04:30 | 64 | 64
2018-02-01 05:00 | 64 | 64
2018-02-01 05:30 | 64 | 64
2018-02-01 06:00 | 64 | 64
2018-02-01 06:30 | 66 | 66
2018-02-01 07:00 | 68 | 68
2018-02-01 07:30 | 68 | 68
2018-02-01 08:00 | 69 | 69
2018-02-01 08:30 | 71 | 71
2018-02-01 09:00 | 71 | 71
2018-02-01 09:30 | 71 | 71
2018-02-01 10:00 | 71 | 71
2018-02-01 10:30 | 70 | 70
2018-02-01 11:00 | 70 | 70
2018-02-01 11:30 | 70 | 70
2018-02-01 12:00 | 71 | 71
2018-02-01 12:30 | 72 | 72
2018-02-01 13:00 | 72 | 72
2018-02-01 13:30 | 75 | 74
2018-02-01 14:00 | 74 | 73
2018-02-01 14:30 | 71 | 70
2018-02-01 15:00 | 71 | 70
2018-02-01 15:30 | 72 | 71
2018-02-01 16:00 | 73 | 72
2018-02-01 16:30 | 74 | 73
2018-02-01 17:00 | 75 | 74
2018-02-01 17:30 | 76 | 75
2018-02-01 18:00 | 76 | 75
2018-02-01 18:30 | 76 | 75
2018-02-01 19:00 | 77 | 76
2018-02-01 19:30 | 76 | 75
2018-02-01 20:00 | 75 | 75
2018-02-01 20:30 | 78 | 78
2018-02-01 21:00 | 78 | 77
2018-02-01 21:30 | 76 | 75
2018-02-01 22:00 | 73 | 73
2018-02-01 22:30 | 69 | 68
2018-02-01 23:00 | 67 | 66
2018-02-01 23:30 | 65 | 64
2018-02-02 | 65 | 64
2018-02-02 00:30 | 67 | 66
2018-02-02 01:00 | 68 | 67
2018-02-02 01:30 | 67 | 67
2018-02-02 02:00 | 67 | 67
2018-02-02 02:30 | 67 | 67
2018-02-02 03:00 | 67 | 67
2018-02-02 03:30 | 66 | 66
2018-02-02 04:00 | 67 | 66
2018-02-02 04:30 | 66 | 66
2018-02-02 05:00 | 65 | 65
2018-02-02 05:30 | 65 | 65
2018-02-02 06:00 | 65 | 65
2018-02-02 06:30 | 66 | 66
2018-02-02 07:00 | 68 | 68
2018-02-02 07:30 | 69 | 69
2018-02-02 08:00 | 71 | 71
2018-02-02 08:30 | 71 | 71
2018-02-02 09:00 | 72 | 72
2018-02-02 09:30 | 72 | 72
2018-02-02 10:00 | 72 | 71
2018-02-02 10:30 | 72 | 72
2018-02-02 11:00 | 72 | 71
2018-02-02 11:30 | 71 | 70
2018-02-02 12:00 | 71 | 70
2018-02-02 12:30 | 72 | 71
2018-02-02 13:00 | 73 | 72
2018-02-02 13:30 | 73 | 73
2018-02-02 14:00 | 74 | 73
2018-02-02 14:30 | 73 | 72
2018-02-02 15:00 | 72 | 70
2018-02-02 15:30 | 72 | 70
2018-02-02 16:00 | 73 | 71
2018-02-02 16:30 | 73 | 71
2018-02-02 17:00 | 75 | 73
2018-02-02 17:30 | 75 | 73
2018-02-02 18:00 | 76 | 73
2018-02-02 18:30 | 76 | 73
2018-02-02 19:00 | 76 | 73
2018-02-02 19:30 | 76 | 73
2018-02-02 20:00 | 76 | 73
2018-02-02 20:30 | 78 | 76
2018-02-02 21:00 | 77 | 75
2018-02-02 21:30 | 76 | 74
2018-02-02 22:00 | 73 | 72
2018-02-02 22:30 | 70 | 70
2018-02-02 23:00 | 69 | 68
2018-02-02 23:30 | 67 | 66
2018-02-03 | 66 | 66
2018-02-03 00:30 | 68 | 67
2018-02-03 01:00 | 67 | 66
2018-02-03 01:30 | 67 | 66
2018-02-03 02:00 | 65 | 65
2018-02-03 02:30 | 65 | 65
2018-02-03 03:00 | 65 | 65
2018-02-03 03:30 | 65 | 65
2018-02-03 04:00 | 65 | 65
2018-02-03 04:30 | 65 | 65
2018-02-03 05:00 | 64 | 64
2018-02-03 05:30 | 64 | 64
2018-02-03 06:00 | 65 | 65
2018-02-03 06:30 | 65 | 65
2018-02-03 07:00 | 65 | 65
2018-02-03 07:30 | 63 | 62
2018-02-03 08:00 | 63 | 63
2018-02-03 08:30 | 64 | 64
2018-02-03 09:00 | 66 | 66
2018-02-03 09:30 | 66 | 66
2018-02-03 10:00 | 66 | 66
2018-02-03 10:30 | 67 | 67
2018-02-03 11:00 | 67 | 66
2018-02-03 11:30 | 66 | 66
2018-02-03 12:00 | 68 | 68
2018-02-03 12:30 | 70 | 69
2018-02-03 13:00 | 71 | 71
2018-02-03 13:30 | 72 | 71
2018-02-03 14:00 | 73 | 73
2018-02-03 14:30 | 78 | 78
2018-02-03 15:00 | 79 | 79
2018-02-03 15:30 | 76 | 76
2018-02-03 16:00 | 75 | 75
2018-02-03 16:30 | 76 | 75
2018-02-03 17:00 | 75 | 75
2018-02-03 17:30 | 76 | 76
2018-02-03 18:00 | 76 | 76
2018-02-03 18:30 | 77 | 77
2018-02-03 19:00 | 77 | 77
2018-02-03 19:30 | 77 | 77
2018-02-03 20:00 | 77 | 77
2018-02-03 20:30 | 79 | 79
2018-02-03 21:00 | 78 | 78
2018-02-03 21:30 | 76 | 76
2018-02-03 22:00 | 75 | 75
2018-02-03 22:30 | 72 | 72
2018-02-03 23:00 | 71 | 71
2018-02-03 23:30 | 71 | 71
2018-02-04 | 70 | 70
2018-02-04 00:30 | 71 | 71
2018-02-04 01:00 | 71 | 70
2018-02-04 01:30 | 71 | 71
2018-02-04 02:00 | 71 | 71
2018-02-04 02:30 | 70 | 70
2018-02-04 03:00 | 69 | 69
2018-02-04 03:30 | 68 | 68
2018-02-04 04:00 | 68 | 68
2018-02-04 04:30 | 68 | 68
2018-02-04 05:00 | 68 | 68
2018-02-04 05:30 | 68 | 67
2018-02-04 06:00 | 68 | 67
2018-02-04 06:30 | 67 | 67
2018-02-04 07:00 | 67 | 67
2018-02-04 07:30 | 65 | 65
2018-02-04 08:00 | 67 | 66
2018-02-04 08:30 | 68 | 68
2018-02-04 09:00 | 69 | 69
2018-02-04 09:30 | 70 | 70
2018-02-04 10:00 | 70 | 70
2018-02-04 10:30 | 70 | 70
2018-02-04 11:00 | 70 | 70
2018-02-04 11:30 | 71 | 71
2018-02-04 12:00 | 72 | 72
2018-02-04 12:30 | 74 | 74
2018-02-04 13:00 | 75 | 75
2018-02-04 13:30 | 75 | 75
2018-02-04 14:00 | 74 | 74
2018-02-04 14:30 | 69 | 69
2018-02-04 15:00 | 70 | 70
2018-02-04 15:30 | 69 | 69
2018-02-04 16:00 | 68 | 68
2018-02-04 16:30 | 67 | 67
2018-02-04 17:00 | 67 | 67
2018-02-04 17:30 | 67 | 67
2018-02-04 18:00 | 68 | 68
2018-02-04 18:30 | 68 | 68
2018-02-04 19:00 | 68 | 68
2018-02-04 19:30 | 66 | 66
2018-02-04 20:00 | 65 | 65
2018-02-04 20:30 | 67 | 67
2018-02-04 21:00 | 67 | 67
2018-02-04 21:30 | 65 | 65
2018-02-04 22:00 | 63 | 63
2018-02-04 22:30 | 60 | 60
2018-02-04 23:00 | 59 | 59
2018-02-04 23:30 | 57 | 57
2018-02-05 | 56 | 56
2018-02-05 00:30 | 58 | 58
2018-02-05 01:00 | 58 | 58
2018-02-05 01:30 | 58 | 58
2018-02-05 02:00 | 58 | 58
2018-02-05 02:30 | 58 | 58
2018-02-05 03:00 | 58 | 58
2018-02-05 03:30 | 58 | 58
2018-02-05 04:00 | 58 | 58
2018-02-05 04:30 | 57 | 57
2018-02-05 05:00 | 57 | 57
2018-02-05 05:30 | 58 | 58
2018-02-05 06:00 | 58 | 58
2018-02-05 06:30 | 61 | 61
2018-02-05 07:00 | 62 | 62
2018-02-05 07:30 | 64 | 64
2018-02-05 08:00 | 64 | 64
2018-02-05 08:30 | 64 | 64
2018-02-05 09:00 | 64 | 64
2018-02-05 09:30 | 64 | 64
2018-02-05 10:00 | 64 | 64
2018-02-05 10:30 | 64 | 64
2018-02-05 11:00 | 65 | 65
2018-02-05 11:30 | 64 | 64
2018-02-05 12:00 | 66 | 66
2018-02-05 12:30 | 65 | 65
2018-02-05 13:00 | 65 | 65
2018-02-05 13:30 | 65 | 65
2018-02-05 14:00 | 65 | 65
2018-02-05 14:30 | 60 | 60
2018-02-05 15:00 | 61 | 61
2018-02-05 15:30 | 62 | 62
2018-02-05 16:00 | 61 | 61
2018-02-05 16:30 | 62 | 62
2018-02-05 17:00 | 62 | 62
2018-02-05 17:30 | 66 | 66
2018-02-05 18:00 | 67 | 67
2018-02-05 18:30 | 67 | 67
2018-02-05 19:00 | 67 | 67
2018-02-05 19:30 | 68 | 68
2018-02-05 20:00 | 69 | 69
2018-02-05 20:30 | 69 | 69
2018-02-05 21:00 | 67 | 67
2018-02-05 21:30 | 66 | 66
2018-02-05 22:00 | 65 | 65
2018-02-05 22:30 | 63 | 63
2018-02-05 23:00 | 63 | 62
2018-02-05 23:30 | 62 | 62
2018-02-06 | 61 | 61
2018-02-06 00:30 | 60 | 59
2018-02-06 01:00 | 60 | 60
2018-02-06 01:30 | 61 | 61
2018-02-06 02:00 | 62 | 62
2018-02-06 02:30 | 62 | 62
2018-02-06 03:00 | 62 | 62
2018-02-06 03:30 | 62 | 62
2018-02-06 04:00 | 62 | 62
2018-02-06 04:30 | 62 | 62
2018-02-06 05:00 | 62 | 61
2018-02-06 05:30 | 62 | 62
2018-02-06 06:00 | 62 | 62
2018-02-06 06:30 | 63 | 63
2018-02-06 07:00 | 64 | 64
2018-02-06 07:30 | 64 | 64
2018-02-06 08:00 | 66 | 66
2018-02-06 08:30 | 66 | 66
2018-02-06 09:00 | 65 | 65
2018-02-06 09:30 | 65 | 65
2018-02-06 10:00 | 65 | 65
2018-02-06 10:30 | 67 | 67
2018-02-06 11:00 | 68 | 68
2018-02-06 11:30 | 62 | 62
2018-02-06 12:00 | 63 | 63
2018-02-06 12:30 | 63 | 63
2018-02-06 13:00 | 64 | 64
2018-02-06 13:30 | 64 | 64
2018-02-06 14:00 | 64 | 64
2018-02-06 14:30 | 61 | 61
2018-02-06 15:00 | 61 | 61
2018-02-06 15:30 | 61 | 61
2018-02-06 16:00 | 61 | 60
2018-02-06 16:30 | 63 | 63
2018-02-06 17:00 | 68 | 68
2018-02-06 17:30 | 68 | 68
2018-02-06 18:00 | 69 | 68
2018-02-06 18:30 | 68 | 68
2018-02-06 19:00 | 69 | 69
2018-02-06 19:30 | 70 | 70
2018-02-06 20:00 | 71 | 70
2018-02-06 20:30 | 73 | 73
2018-02-06 21:00 | 72 | 72
2018-02-06 21:30 | 70 | 70
2018-02-06 22:00 | 69 | 69
2018-02-06 22:30 | 67 | 67
2018-02-06 23:00 | 66 | 66
2018-02-06 23:30 | 66 | 66
2018-02-07 | 65 | 65
2018-02-07 00:30 | 66 | 66
2018-02-07 01:00 | 66 | 66
2018-02-07 01:30 | 65 | 65
2018-02-07 02:00 | 66 | 66
2018-02-07 02:30 | 65 | 65
2018-02-07 03:00 | 65 | 65
2018-02-07 03:30 | 66 | 66
2018-02-07 04:00 | 65 | 65
2018-02-07 04:30 | 64 | 64
2018-02-07 05:00 | 64 | 64
2018-02-07 05:30 | 65 | 65
2018-02-07 06:00 | 66 | 65
2018-02-07 06:30 | 66 | 66
2018-02-07 07:00 | 68 | 68
2018-02-07 07:30 | 67 | 67
2018-02-07 08:00 | 68 | 68
2018-02-07 08:30 | 71 | 71
2018-02-07 09:00 | 76 | 76
2018-02-07 09:30 | 75 | 75
2018-02-07 10:00 | 75 | 75
2018-02-07 10:30 | 75 | 75
2018-02-07 11:00 | 74 | 74
2018-02-07 11:30 | 76 | 76
2018-02-07 12:00 | 77 | 77
2018-02-07 12:30 | 78 | 77
2018-02-07 13:00 | 78 | 78
2018-02-07 13:30 | 77 | 76
2018-02-07 14:00 | 77 | 77
2018-02-07 14:30 | 70 | 70
2018-02-07 15:00 | 65 | 65
2018-02-07 15:30 | 64 | 64
2018-02-07 16:00 | 66 | 66
2018-02-07 16:30 | 63 | 63
2018-02-07 17:00 | 67 | 67
2018-02-07 17:30 | 69 | 69
2018-02-07 18:00 | 70 | 70
2018-02-07 18:30 | 70 | 70
2018-02-07 19:00 | 70 | 70
2018-02-07 19:30 | 71 | 71
2018-02-07 20:00 | 72 | 72
2018-02-07 20:30 | 75 | 75
2018-02-07 21:00 | 74 | 74
2018-02-07 21:30 | 72 | 72
2018-02-07 22:00 | 71 | 71
2018-02-07 22:30 | 68 | 68
2018-02-07 23:00 | 68 | 68
2018-02-07 23:30 | 67 | 67
2018-02-08 | 66 | 66
2018-02-08 00:30 | 68 | 67
2018-02-08 01:00 | 67 | 67
2018-02-08 01:30 | 67 | 67
2018-02-08 02:00 | 66 | 66
2018-02-08 02:30 | 66 | 66
2018-02-08 03:00 | 66 | 66
2018-02-08 03:30 | 67 | 67
2018-02-08 04:00 | 67 | 67
2018-02-08 04:30 | 66 | 66
2018-02-08 05:00 | 66 | 66
2018-02-08 05:30 | 66 | 66
2018-02-08 06:00 | 66 | 66
2018-02-08 06:30 | 67 | 67
2018-02-08 07:00 | 68 | 68
2018-02-08 07:30 | 67 | 67
2018-02-08 08:00 | 69 | 69
2018-02-08 08:30 | 70 | 70
2018-02-08 09:00 | 71 | 71
2018-02-08 09:30 | 68 | 68
2018-02-08 10:00 | 67 | 67
2018-02-08 10:30 | 68 | 68
2018-02-08 11:00 | 68 | 68
2018-02-08 11:30 | 67 | 67
2018-02-08 12:00 | 66 | 66
2018-02-08 12:30 | 65 | 65
2018-02-08 13:00 | 66 | 66
2018-02-08 13:30 | 67 | 67
2018-02-08 14:00 | 68 | 68
2018-02-08 14:30 | 65 | 65
2018-02-08 15:00 | 60 | 60
2018-02-08 15:30 | 52 | 51
2018-02-08 16:00 | 51 | 50
2018-02-08 16:30 | 51 | 50
2018-02-08 17:00 | 52 | 51
2018-02-08 17:30 | 54 | 53
2018-02-08 18:00 | 54 | 53
2018-02-08 18:30 | 53 | 53
2018-02-08 19:00 | 54 | 54
2018-02-08 19:30 | 55 | 55
2018-02-08 20:00 | 55 | 55
2018-02-08 20:30 | 55 | 55
2018-02-08 21:00 | 54 | 54
2018-02-08 21:30 | 57 | 57
2018-02-08 22:00 | 55 | 55
2018-02-08 22:30 | 53 | 53
2018-02-08 23:00 | 51 | 51
2018-02-08 23:30 | 51 | 51
2018-02-09 | 50 | 50
2018-02-09 00:30 | 65 | 65
2018-02-09 01:00 | 67 | 66
2018-02-09 01:30 | 66 | 66
2018-02-09 02:00 | 66 | 65
2018-02-09 02:30 | 65 | 65
2018-02-09 03:00 | 65 | 65
2018-02-09 03:30 | 65 | 64
2018-02-09 04:00 | 65 | 64
2018-02-09 04:30 | 64 | 64
2018-02-09 05:00 | 65 | 64
2018-02-09 05:30 | 65 | 64
2018-02-09 06:00 | 66 | 65
2018-02-09 06:30 | 65 | 65
2018-02-09 07:00 | 55 | 55
2018-02-09 07:30 | 53 | 53
2018-02-09 08:00 | 54 | 54
2018-02-09 08:30 | 53 | 53
2018-02-09 09:00 | 52 | 52
2018-02-09 09:30 | 52 | 52
2018-02-09 10:00 | 53 | 53
2018-02-09 10:30 | 54 | 53
2018-02-09 11:00 | 57 | 57
2018-02-09 11:30 | 69 | 68
2018-02-09 12:00 | 70 | 69
2018-02-09 12:30 | 70 | 69
2018-02-09 13:00 | 70 | 70
2018-02-09 13:30 | 71 | 71
2018-02-09 14:00 | 70 | 70
2018-02-09 14:30 | 66 | 66
2018-02-09 15:00 | 64 | 64
2018-02-09 15:30 | 64 | 64
2018-02-09 16:00 | 65 | 65
2018-02-09 16:30 | 60 | 60
2018-02-09 17:00 | 60 | 60
2018-02-09 17:30 | 58 | 58
2018-02-09 18:00 | 58 | 58
2018-02-09 18:30 | 57 | 57
2018-02-09 19:00 | 59 | 59
2018-02-09 19:30 | 68 | 68
2018-02-09 20:00 | 70 | 70
2018-02-09 20:30 | 73 | 73
2018-02-09 21:00 | 74 | 73
2018-02-09 21:30 | 73 | 72
2018-02-09 22:00 | 72 | 71
2018-02-09 22:30 | 70 | 70
2018-02-09 23:00 | 69 | 69
2018-02-09 23:30 | 68 | 68
2018-02-10 | 68 | 67
2018-02-10 00:30 | 68 | 67
2018-02-10 01:00 | 67 | 67
2018-02-10 01:30 | 67 | 66
2018-02-10 02:00 | 66 | 65
2018-02-10 02:30 | 65 | 65
2018-02-10 03:00 | 65 | 65
2018-02-10 03:30 | 65 | 64
2018-02-10 04:00 | 65 | 64
2018-02-10 04:30 | 65 | 64
2018-02-10 05:00 | 65 | 65
2018-02-10 05:30 | 65 | 64
2018-02-10 06:00 | 63 | 63
2018-02-10 06:30 | 62 | 62
2018-02-10 07:00 | 66 | 65
2018-02-10 07:30 | 67 | 67
2018-02-10 08:00 | 68 | 67
2018-02-10 08:30 | 69 | 68
2018-02-10 09:00 | 70 | 68
2018-02-10 09:30 | 71 | 69
2018-02-10 10:00 | 71 | 69
2018-02-10 10:30 | 71 | 69
2018-02-10 11:00 | 71 | 69
2018-02-10 11:30 | 71 | 69
2018-02-10 12:00 | 70 | 69
2018-02-10 12:30 | 70 | 69
2018-02-10 13:00 | 71 | 70
2018-02-10 13:30 | 71 | 70
2018-02-10 14:00 | 71 | 70
2018-02-10 14:30 | 66 | 65
2018-02-10 15:00 | 64 | 64
2018-02-10 15:30 | 65 | 64
2018-02-10 16:00 | 65 | 65
2018-02-10 16:30 | 65 | 65
2018-02-10 17:00 | 66 | 66
2018-02-10 17:30 | 64 | 64
2018-02-10 18:00 | 66 | 66
2018-02-10 18:30 | 69 | 68
2018-02-10 19:00 | 67 | 67
2018-02-10 19:30 | 68 | 68
2018-02-10 20:00 | 69 | 68
2018-02-10 20:30 | 74 | 73
2018-02-10 21:00 | 72 | 72
2018-02-10 21:30 | 71 | 71
2018-02-10 22:00 | 70 | 70
2018-02-10 22:30 | 69 | 69
2018-02-10 23:00 | 68 | 68
2018-02-10 23:30 | 67 | 67
2018-02-11 | 67 | 67
2018-02-11 00:30 | 67 | 67
2018-02-11 01:00 | 67 | 67
2018-02-11 01:30 | 66 | 66
2018-02-11 02:00 | 66 | 66
2018-02-11 02:30 | 64 | 64
2018-02-11 03:00 | 64 | 63
2018-02-11 03:30 | 64 | 64
2018-02-11 04:00 | 63 | 63
2018-02-11 04:30 | 63 | 63
2018-02-11 05:00 | 63 | 63
2018-02-11 05:30 | 63 | 63
2018-02-11 06:00 | 62 | 61
2018-02-11 06:30 | 61 | 61
2018-02-11 07:00 | 62 | 62
2018-02-11 07:30 | 65 | 64
2018-02-11 08:00 | 67 | 66
2018-02-11 08:30 | 65 | 65
2018-02-11 09:00 | 61 | 60
2018-02-11 09:30 | 61 | 61
2018-02-11 10:00 | 61 | 60
2018-02-11 10:30 | 62 | 62
2018-02-11 11:00 | 62 | 62
2018-02-11 11:30 | 62 | 62
2018-02-11 12:00 | 63 | 63
2018-02-11 12:30 | 63 | 63
2018-02-11 13:00 | 64 | 64
2018-02-11 13:30 | 64 | 64
2018-02-11 14:00 | 65 | 65
2018-02-11 14:30 | 65 | 65
2018-02-11 15:00 | 64 | 64
2018-02-11 15:30 | 65 | 65
2018-02-11 16:00 | 65 | 65
2018-02-11 16:30 | 64 | 64
2018-02-11 17:00 | 45 | 45
2018-02-11 17:30 | 29 | 24
2018-02-11 18:00 | 29 | 23
2018-02-11 18:30 | 44 | 39
2018-02-11 19:00 | 56 | 48
2018-02-11 19:30 | 60 | 52
2018-02-11 20:00 | 60 | 52
2018-02-11 20:30 | 70 | 65
2018-02-11 21:00 | 74 | 71
2018-02-11 21:30 | 77 | 77
2018-02-11 22:00 | 75 | 75
2018-02-11 22:30 | 72 | 71
2018-02-11 23:00 | 70 | 69
2018-02-11 23:30 | 68 | 67
2018-02-12 | 67 | 66
2018-02-12 00:30 | 68 | 67
2018-02-12 01:00 | 70 | 69
2018-02-12 01:30 | 70 | 70
2018-02-12 02:00 | 70 | 70
2018-02-12 02:30 | 70 | 69
2018-02-12 03:00 | 69 | 68
2018-02-12 03:30 | 67 | 66
2018-02-12 04:00 | 64 | 63
2018-02-12 04:30 | 64 | 63
2018-02-12 05:00 | 63 | 62
2018-02-12 05:30 | 62 | 62
2018-02-12 06:00 | 63 | 62
2018-02-12 06:30 | 64 | 63
2018-02-12 07:00 | 66 | 65
2018-02-12 07:30 | 69 | 69
2018-02-12 08:00 | 70 | 69
2018-02-12 08:30 | 69 | 68
2018-02-12 09:00 | 68 | 68
2018-02-12 09:30 | 68 | 68
2018-02-12 10:00 | 67 | 67
2018-02-12 10:30 | 68 | 68
2018-02-12 11:00 | 69 | 68
2018-02-12 11:30 | 70 | 69
2018-02-12 12:00 | 71 | 70
2018-02-12 12:30 | 71 | 71
2018-02-12 13:00 | 71 | 71
2018-02-12 13:30 | 71 | 71
2018-02-12 14:00 | 70 | 69
2018-02-12 14:30 | 64 | 63
2018-02-12 15:00 | 60 | 59
2018-02-12 15:30 | 62 | 60
2018-02-12 16:00 | 67 | 66
2018-02-12 16:30 | 61 | 60
2018-02-12 17:00 | 24 | 24
2018-02-12 17:30 | 21 | 21
2018-02-12 18:00 | 23 | 22
2018-02-12 18:30 | 28 | 28
2018-02-12 19:00 | 23 | 23
2018-02-12 19:30 | 23 | 23
2018-02-12 20:00 | 57 | 57
2018-02-12 20:30 | 79 | 79
2018-02-12 21:00 | 81 | 81
2018-02-12 21:30 | 79 | 79
2018-02-12 22:00 | 77 | 77
2018-02-12 22:30 | 75 | 75
2018-02-12 23:00 | 73 | 73
2018-02-12 23:30 | 71 | 71
2018-02-13 | 70 | 70
2018-02-13 00:30 | 71 | 71
2018-02-13 01:00 | 71 | 71
2018-02-13 01:30 | 70 | 70
2018-02-13 02:00 | 70 | 70
2018-02-13 02:30 | 70 | 70
2018-02-13 03:00 | 69 | 69
2018-02-13 03:30 | 69 | 69
2018-02-13 04:00 | 69 | 69
2018-02-13 04:30 | 69 | 69
2018-02-13 05:00 | 69 | 69
2018-02-13 05:30 | 69 | 69
2018-02-13 06:00 | 69 | 69
2018-02-13 06:30 | 69 | 69
2018-02-13 07:00 | 69 | 69
2018-02-13 07:30 | 69 | 69
2018-02-13 08:00 | 71 | 71
2018-02-13 08:30 | 74 | 74
2018-02-13 09:00 | 74 | 74
2018-02-13 09:30 | 65 | 63
2018-02-13 10:00 | 75 | 75
2018-02-13 10:30 | 75 | 75
2018-02-13 11:00 | 76 | 76
2018-02-13 11:30 | 66 | 65
2018-02-13 12:00 | 66 | 64
2018-02-13 12:30 | 67 | 65
2018-02-13 13:00 | 67 | 65
2018-02-13 13:30 | 67 | 65
2018-02-13 14:00 | 68 | 66
2018-02-13 14:30 | 67 | 65
2018-02-13 15:00 | 63 | 62
2018-02-13 15:30 | 45 | 45
2018-02-13 16:00 | 23 | 23
2018-02-13 16:30 | 31 | 30
2018-02-13 17:00 | 30 | 29
2018-02-13 17:30 | 9 | 7
2018-02-13 18:00 | 18 | 6
2018-02-13 18:30 | 11 | 2
2018-02-13 19:00 | 8 | 0
2018-02-13 19:30 | 13 | 9
2018-02-13 20:00 | 27 | 26
2018-02-13 20:30 | 64 | 63
2018-02-13 21:00 | 84 | 84
2018-02-13 21:30 | 84 | 84
2018-02-13 22:00 | 81 | 81
2018-02-13 22:30 | 76 | 76
2018-02-13 23:00 | 74 | 74
2018-02-13 23:30 | 73 | 73
2018-02-14 | 72 | 72
2018-02-14 00:30 | 72 | 72
2018-02-14 01:00 | 71 | 71
2018-02-14 01:30 | 71 | 70
2018-02-14 02:00 | 70 | 70
2018-02-14 02:30 | 69 | 69
2018-02-14 03:00 | 68 | 68
2018-02-14 03:30 | 68 | 68
2018-02-14 04:00 | 68 | 68
2018-02-14 04:30 | 69 | 68
2018-02-14 05:00 | 68 | 68
2018-02-14 05:30 | 70 | 70
2018-02-14 06:00 | 71 | 71
2018-02-14 06:30 | 71 | 71
2018-02-14 07:00 | 71 | 70
2018-02-14 07:30 | 56 | 56
2018-02-14 08:00 | 58 | 58
2018-02-14 08:30 | 58 | 58
2018-02-14 09:00 | 59 | 59
2018-02-14 09:30 | 59 | 59
2018-02-14 10:00 | 55 | 55
2018-02-14 10:30 | 55 | 55
2018-02-14 11:00 | 54 | 54
2018-02-14 11:30 | 55 | 55
2018-02-14 12:00 | 57 | 57
2018-02-14 12:30 | 57 | 56
2018-02-14 13:00 | 57 | 57
2018-02-14 13:30 | 58 | 57
2018-02-14 14:00 | 59 | 58
2018-02-14 14:30 | 59 | 59
2018-02-14 15:00 | 58 | 58
2018-02-14 15:30 | 19 | 19
2018-02-14 16:00 | 21 | 17
2018-02-14 16:30 | 37 | 34
2018-02-14 17:00 | 45 | 43
2018-02-14 17:30 | 51 | 49
2018-02-14 18:00 | 51 | 49
2018-02-14 18:30 | 50 | 47
2018-02-14 19:00 | 49 | 46
2018-02-14 19:30 | 48 | 46
2018-02-14 20:00 | 11 | 5
2018-02-14 20:30 | 24 | 23
2018-02-14 21:00 | 45 | 45
2018-02-14 21:30 | 62 | 61
2018-02-14 22:00 | 63 | 63
2018-02-14 22:30 | 60 | 58
2018-02-14 23:00 | 57 | 56
2018-02-14 23:30 | 56 | 55
2018-02-15 | 56 | 55
2018-02-15 00:30 | 56 | 54
2018-02-15 01:00 | 55 | 53
2018-02-15 01:30 | 54 | 52
2018-02-15 02:00 | 53 | 51
2018-02-15 02:30 | 53 | 51
2018-02-15 03:00 | 53 | 51
2018-02-15 03:30 | 53 | 51
2018-02-15 04:00 | 53 | 51
2018-02-15 04:30 | 60 | 59
2018-02-15 05:00 | 67 | 67
2018-02-15 05:30 | 68 | 68
2018-02-15 06:00 | 67 | 67
2018-02-15 06:30 | 66 | 66
2018-02-15 07:00 | 66 | 66
2018-02-15 07:30 | 57 | 56
2018-02-15 08:00 | 59 | 58
2018-02-15 08:30 | 59 | 58
2018-02-15 09:00 | 59 | 58
2018-02-15 09:30 | 59 | 58
2018-02-15 10:00 | 58 | 58
2018-02-15 10:30 | 59 | 58
2018-02-15 11:00 | 58 | 58
2018-02-15 11:30 | 58 | 58
2018-02-15 12:00 | 59 | 58
2018-02-15 12:30 | 59 | 58
2018-02-15 13:00 | 59 | 58
2018-02-15 13:30 | 60 | 58
2018-02-15 14:00 | 60 | 59
2018-02-15 14:30 | 60 | 59
2018-02-15 15:00 | 52 | 50
2018-02-15 15:30 | 30 | 29
2018-02-15 16:00 | 12 | 12
2018-02-15 16:30 | 44 | 43
2018-02-15 17:00 | 64 | 63
2018-02-15 17:30 | 44 | 44
2018-02-15 18:00 | 10 | 9
2018-02-15 18:30 | 13 | 13
2018-02-15 19:00 | 13 | 13
2018-02-15 19:30 | 14 | 14
2018-02-15 20:00 | 28 | 28
2018-02-15 20:30 | 46 | 44
2018-02-15 21:00 | 74 | 74
2018-02-15 21:30 | 78 | 77
2018-02-15 22:00 | 76 | 76
2018-02-15 22:30 | 75 | 75
2018-02-15 23:00 | 79 | 79
2018-02-15 23:30 | 74 | 74
2018-02-16 | 72 | 72
2018-02-16 00:30 | 72 | 72
2018-02-16 01:00 | 71 | 71
2018-02-16 01:30 | 70 | 70
2018-02-16 02:00 | 70 | 70
2018-02-16 02:30 | 70 | 70
2018-02-16 03:00 | 69 | 69
2018-02-16 03:30 | 69 | 69
2018-02-16 04:00 | 68 | 68
2018-02-16 04:30 | 68 | 68
2018-02-16 05:00 | 68 | 68
2018-02-16 05:30 | 69 | 68
2018-02-16 06:00 | 69 | 69
2018-02-16 06:30 | 69 | 69
2018-02-16 07:00 | 69 | 69
2018-02-16 07:30 | 58 | 57
2018-02-16 08:00 | 59 | 59
2018-02-16 08:30 | 60 | 59
2018-02-16 09:00 | 61 | 61
2018-02-16 09:30 | 61 | 61
2018-02-16 10:00 | 61 | 60
2018-02-16 10:30 | 62 | 61
2018-02-16 11:00 | 62 | 62
2018-02-16 11:30 | 62 | 62
2018-02-16 12:00 | 62 | 62
2018-02-16 12:30 | 62 | 62
2018-02-16 13:00 | 62 | 61
2018-02-16 13:30 | 62 | 61
2018-02-16 14:00 | 63 | 62
2018-02-16 14:30 | 66 | 66
2018-02-16 15:00 | 69 | 68
2018-02-16 15:30 | 71 | 69
2018-02-16 16:00 | 69 | 68
2018-02-16 16:30 | 60 | 60
2018-02-16 17:00 | 61 | 61
2018-02-16 17:30 | 65 | 65
2018-02-16 18:00 | 64 | 64
2018-02-16 18:30 | 80 | 80
2018-02-16 19:00 | 82 | 82
2018-02-16 19:30 | 83 | 83
2018-02-16 20:00 | 83 | 83
2018-02-16 20:30 | 81 | 81
2018-02-16 21:00 | 78 | 78
2018-02-16 21:30 | 76 | 75
2018-02-16 22:00 | 74 | 74
2018-02-16 22:30 | 73 | 73
2018-02-16 23:00 | 73 | 73
2018-02-16 23:30 | 72 | 72
2018-02-17 | 71 | 70
2018-02-17 00:30 | 70 | 69
2018-02-17 01:00 | 77 | 74
2018-02-17 01:30 | 73 | 71
2018-02-17 02:00 | 68 | 67
2018-02-17 02:30 | 65 | 65
2018-02-17 03:00 | 65 | 65
2018-02-17 03:30 | 65 | 65
2018-02-17 04:00 | 64 | 64
2018-02-17 04:30 | 64 | 64
2018-02-17 05:00 | 65 | 64
2018-02-17 05:30 | 64 | 63
2018-02-17 06:00 | 63 | 63
2018-02-17 06:30 | 63 | 62
2018-02-17 07:00 | 62 | 61
2018-02-17 07:30 | 56 | 54
2018-02-17 08:00 | 57 | 55
2018-02-17 08:30 | 56 | 54
2018-02-17 09:00 | 57 | 55
2018-02-17 09:30 | 59 | 58
2018-02-17 10:00 | 58 | 57
2018-02-17 10:30 | 57 | 56
2018-02-17 11:00 | 58 | 57
2018-02-17 11:30 | 59 | 58
2018-02-17 12:00 | 59 | 58
2018-02-17 12:30 | 59 | 58
2018-02-17 13:00 | 60 | 59
2018-02-17 13:30 | 61 | 60
2018-02-17 14:00 | 62 | 61
2018-02-17 14:30 | 63 | 62
2018-02-17 15:00 | 64 | 62
2018-02-17 15:30 | 65 | 63
2018-02-17 16:00 | 64 | 63
2018-02-17 16:30 | 66 | 64
2018-02-17 17:00 | 67 | 66
2018-02-17 17:30 | 67 | 66
2018-02-17 18:00 | 67 | 66
2018-02-17 18:30 | 73 | 72
2018-02-17 19:00 | 74 | 74
2018-02-17 19:30 | 75 | 75
2018-02-17 20:00 | 79 | 79
2018-02-17 20:30 | 75 | 75
2018-02-17 21:00 | 75 | 74
2018-02-17 21:30 | 73 | 73
2018-02-17 22:00 | 72 | 71
2018-02-17 22:30 | 71 | 71
2018-02-17 23:00 | 70 | 70
2018-02-17 23:30 | 69 | 69
2018-02-18 | 69 | 68
2018-02-18 00:30 | 69 | 68
2018-02-18 01:00 | 69 | 67
2018-02-18 01:30 | 68 | 67
2018-02-18 02:00 | 68 | 66
2018-02-18 02:30 | 66 | 65
2018-02-18 03:00 | 66 | 65
2018-02-18 03:30 | 65 | 64
2018-02-18 04:00 | 64 | 64
2018-02-18 04:30 | 66 | 65
2018-02-18 05:00 | 67 | 66
2018-02-18 05:30 | 67 | 66
2018-02-18 06:00 | 66 | 66
2018-02-18 06:30 | 66 | 65
2018-02-18 07:00 | 66 | 65
2018-02-18 07:30 | 62 | 60
2018-02-18 08:00 | 60 | 59
2018-02-18 08:30 | 59 | 58
2018-02-18 09:00 | 60 | 59
2018-02-18 09:30 | 62 | 61
2018-02-18 10:00 | 62 | 61
2018-02-18 10:30 | 62 | 61
2018-02-18 11:00 | 61 | 61
2018-02-18 11:30 | 61 | 61
2018-02-18 12:00 | 63 | 62
2018-02-18 12:30 | 64 | 63
2018-02-18 13:00 | 65 | 64
2018-02-18 13:30 | 65 | 64
2018-02-18 14:00 | 66 | 65
2018-02-18 14:30 | 66 | 65
2018-02-18 15:00 | 66 | 65
2018-02-18 15:30 | 66 | 65
2018-02-18 16:00 | 66 | 65
2018-02-18 16:30 | 67 | 66
2018-02-18 17:00 | 67 | 66
2018-02-18 17:30 | 70 | 68
2018-02-18 18:00 | 72 | 70
2018-02-18 18:30 | 78 | 77
2018-02-18 19:00 | 79 | 79
2018-02-18 19:30 | 80 | 80
2018-02-18 20:00 | 80 | 80
2018-02-18 20:30 | 79 | 79
2018-02-18 21:00 | 78 | 78
2018-02-18 21:30 | 76 | 76
2018-02-18 22:00 | 75 | 75
2018-02-18 22:30 | 73 | 73
2018-02-18 23:00 | 72 | 71
2018-02-18 23:30 | 72 | 72
2018-02-19 | 71 | 71
2018-02-19 00:30 | 70 | 69
2018-02-19 01:00 | 69 | 68
2018-02-19 01:30 | 69 | 69
2018-02-19 02:00 | 70 | 69
2018-02-19 02:30 | 70 | 69
2018-02-19 03:00 | 69 | 68
2018-02-19 03:30 | 68 | 67
2018-02-19 04:00 | 68 | 67
2018-02-19 04:30 | 68 | 67
2018-02-19 05:00 | 68 | 67
2018-02-19 05:30 | 67 | 67
2018-02-19 06:00 | 68 | 67
2018-02-19 06:30 | 69 | 69
2018-02-19 07:00 | 69 | 69
2018-02-19 07:30 | 69 | 68
2018-02-19 08:00 | 70 | 70
2018-02-19 08:30 | 72 | 72
2018-02-19 09:00 | 76 | 75
2018-02-19 09:30 | 76 | 75
2018-02-19 10:00 | 75 | 75
2018-02-19 10:30 | 74 | 74
2018-02-19 11:00 | 73 | 72
2018-02-19 11:30 | 72 | 71
2018-02-19 12:00 | 70 | 69
2018-02-19 12:30 | 70 | 70
2018-02-19 13:00 | 71 | 70
2018-02-19 13:30 | 71 | 70
2018-02-19 14:00 | 71 | 70
2018-02-19 14:30 | 70 | 70
2018-02-19 15:00 | 69 | 69
2018-02-19 15:30 | 67 | 67
2018-02-19 16:00 | 73 | 72
2018-02-19 16:30 | 74 | 74
2018-02-19 17:00 | 75 | 74
2018-02-19 17:30 | 74 | 73
2018-02-19 18:00 | 74 | 73
2018-02-19 18:30 | 74 | 73
2018-02-19 19:00 | 79 | 79
2018-02-19 19:30 | 78 | 78
2018-02-19 20:00 | 76 | 76
2018-02-19 20:30 | 75 | 74
2018-02-19 21:00 | 74 | 74
2018-02-19 21:30 | 72 | 72
2018-02-19 22:00 | 70 | 69
2018-02-19 22:30 | 68 | 68
2018-02-19 23:00 | 68 | 67
2018-02-19 23:30 | 67 | 67
2018-02-20 | 67 | 67
2018-02-20 00:30 | 69 | 69
2018-02-20 01:00 | 67 | 67
2018-02-20 01:30 | 67 | 67
2018-02-20 02:00 | 67 | 67
2018-02-20 02:30 | 67 | 67
2018-02-20 03:00 | 66 | 65
2018-02-20 03:30 | 65 | 65
2018-02-20 04:00 | 66 | 65
2018-02-20 04:30 | 66 | 65
2018-02-20 05:00 | 66 | 65
2018-02-20 05:30 | 66 | 66
2018-02-20 06:00 | 66 | 65
2018-02-20 06:30 | 64 | 63
2018-02-20 07:00 | 64 | 64
2018-02-20 07:30 | 63 | 63
2018-02-20 08:00 | 64 | 64
2018-02-20 08:30 | 65 | 65
2018-02-20 09:00 | 64 | 63
2018-02-20 09:30 | 62 | 58
2018-02-20 10:00 | 66 | 63
2018-02-20 10:30 | 73 | 73
2018-02-20 11:00 | 72 | 71
2018-02-20 11:30 | 70 | 69
2018-02-20 12:00 | 71 | 70
2018-02-20 12:30 | 70 | 69
2018-02-20 13:00 | 68 | 67
2018-02-20 13:30 | 67 | 66
2018-02-20 14:00 | 67 | 66
2018-02-20 14:30 | 68 | 68
2018-02-20 15:00 | 68 | 67
2018-02-20 15:30 | 68 | 68
2018-02-20 16:00 | 70 | 69
2018-02-20 16:30 | 73 | 72
2018-02-20 17:00 | 77 | 76
2018-02-20 17:30 | 78 | 77
2018-02-20 18:00 | 77 | 77
2018-02-20 18:30 | 77 | 76
2018-02-20 19:00 | 76 | 76
2018-02-20 19:30 | 76 | 75
2018-02-20 20:00 | 75 | 75
2018-02-20 20:30 | 72 | 71
2018-02-20 21:00 | 70 | 69
2018-02-20 21:30 | 67 | 66
2018-02-20 22:00 | 67 | 66
2018-02-20 22:30 | 68 | 63
2018-02-20 23:00 | 64 | 64
2018-02-20 23:30 | 61 | 61
2018-02-21 | 60 | 60
2018-02-21 00:30 | 62 | 62
2018-02-21 01:00 | 61 | 61
2018-02-21 01:30 | 61 | 61
2018-02-21 02:00 | 62 | 62
2018-02-21 02:30 | 62 | 62
2018-02-21 03:00 | 62 | 62
2018-02-21 03:30 | 62 | 62
2018-02-21 04:00 | 62 | 62
2018-02-21 04:30 | 62 | 62
2018-02-21 05:00 | 62 | 62
2018-02-21 05:30 | 61 | 61
2018-02-21 06:00 | 62 | 62
2018-02-21 06:30 | 61 | 60
2018-02-21 07:00 | 61 | 61
2018-02-21 07:30 | 64 | 63
2018-02-21 08:00 | 65 | 65
2018-02-21 08:30 | 66 | 65
2018-02-21 09:00 | 65 | 65
2018-02-21 09:30 | 65 | 65
2018-02-21 10:00 | 63 | 62
2018-02-21 10:30 | 62 | 62
2018-02-21 11:00 | 63 | 63
2018-02-21 11:30 | 63 | 62
2018-02-21 12:00 | 63 | 63
2018-02-21 12:30 | 63 | 62
2018-02-21 13:00 | 64 | 64
2018-02-21 13:30 | 63 | 63
2018-02-21 14:00 | 65 | 65
2018-02-21 14:30 | 65 | 65
2018-02-21 15:00 | 65 | 65
2018-02-21 15:30 | 63 | 62
2018-02-21 16:00 | 63 | 63
2018-02-21 16:30 | 65 | 64
2018-02-21 17:00 | 65 | 65
2018-02-21 17:30 | 65 | 64
2018-02-21 18:00 | 66 | 66
2018-02-21 18:30 | 51 | 45
2018-02-21 19:00 | 43 | 32
2018-02-21 19:30 | 54 | 51
2018-02-21 20:00 | 62 | 61
2018-02-21 20:30 | 62 | 61
2018-02-21 21:00 | 61 | 60
2018-02-21 21:30 | 60 | 59
2018-02-21 22:00 | 59 | 58
2018-02-21 22:30 | 59 | 57
2018-02-21 23:00 | 60 | 58
2018-02-21 23:30 | 59 | 57
2018-02-22 | 58 | 56
2018-02-22 00:30 | 59 | 57
2018-02-22 01:00 | 60 | 58
2018-02-22 01:30 | 62 | 60
2018-02-22 02:00 | 56 | 56
2018-02-22 02:30 | 57 | 57
2018-02-22 03:00 | 56 | 56
2018-02-22 03:30 | 56 | 56
2018-02-22 04:00 | 56 | 56
2018-02-22 04:30 | 57 | 57
2018-02-22 05:00 | 57 | 57
2018-02-22 05:30 | 57 | 57
2018-02-22 06:00 | 58 | 58
2018-02-22 06:30 | 59 | 58
2018-02-22 07:00 | 59 | 58
2018-02-22 07:30 | 58 | 57
2018-02-22 08:00 | 60 | 59
2018-02-22 08:30 | 60 | 60
2018-02-22 09:00 | 62 | 61
2018-02-22 09:30 | 61 | 60
2018-02-22 10:00 | 63 | 61
2018-02-22 10:30 | 63 | 62
2018-02-22 11:00 | 62 | 61
2018-02-22 11:30 | 63 | 62
2018-02-22 12:00 | 64 | 62
2018-02-22 12:30 | 64 | 63
2018-02-22 13:00 | 64 | 64
2018-02-22 13:30 | 63 | 63
2018-02-22 14:00 | 63 | 62
2018-02-22 14:30 | 63 | 62
2018-02-22 15:00 | 63 | 62
2018-02-22 15:30 | 64 | 64
2018-02-22 16:00 | 65 | 64
2018-02-22 16:30 | 67 | 66
2018-02-22 17:00 | 67 | 66
2018-02-22 17:30 | 67 | 65
2018-02-22 18:00 | 67 | 66
2018-02-22 18:30 | 67 | 65
2018-02-22 19:00 | 67 | 65
2018-02-22 19:30 | 68 | 66
2018-02-22 20:00 | 67 | 66
2018-02-22 20:30 | 66 | 65
2018-02-22 21:00 | 65 | 64
2018-02-22 21:30 | 63 | 62
2018-02-22 22:00 | 62 | 60
2018-02-22 22:30 | 64 | 62
2018-02-22 23:00 | 69 | 67
2018-02-22 23:30 | 69 | 67
2018-02-23 | 69 | 67
2018-02-23 00:30 | 69 | 67
2018-02-23 01:00 | 68 | 66
2018-02-23 01:30 | 68 | 66
2018-02-23 02:00 | 63 | 63
2018-02-23 02:30 | 64 | 64
2018-02-23 03:00 | 63 | 63
2018-02-23 03:30 | 64 | 64
2018-02-23 04:00 | 64 | 64
2018-02-23 04:30 | 63 | 63
2018-02-23 05:00 | 64 | 64
2018-02-23 05:30 | 65 | 65
2018-02-23 06:00 | 66 | 65
2018-02-23 06:30 | 66 | 66
2018-02-23 07:00 | 67 | 67
2018-02-23 07:30 | 69 | 69
2018-02-23 08:00 | 70 | 70
2018-02-23 08:30 | 70 | 70
2018-02-23 09:00 | 69 | 69
2018-02-23 09:30 | 69 | 69
2018-02-23 10:00 | 70 | 70
2018-02-23 10:30 | 73 | 73
2018-02-23 11:00 | 73 | 73
2018-02-23 11:30 | 73 | 73
2018-02-23 12:00 | 73 | 73
2018-02-23 12:30 | 72 | 72
2018-02-23 13:00 | 71 | 71
2018-02-23 13:30 | 71 | 71
2018-02-23 14:00 | 71 | 71
2018-02-23 14:30 | 69 | 69
2018-02-23 15:00 | 70 | 70
2018-02-23 15:30 | 69 | 69
2018-02-23 16:00 | 71 | 71
2018-02-23 16:30 | 71 | 71
2018-02-23 17:00 | 74 | 72
2018-02-23 17:30 | 76 | 72
2018-02-23 18:00 | 76 | 72
2018-02-23 18:30 | 75 | 71
2018-02-23 19:00 | 76 | 72
2018-02-23 19:30 | 76 | 72
2018-02-23 20:00 | 75 | 72
2018-02-23 20:30 | 76 | 73
2018-02-23 21:00 | 76 | 73
2018-02-23 21:30 | 75 | 72
2018-02-23 22:00 | 75 | 70
2018-02-23 22:30 | 73 | 69
2018-02-23 23:00 | 71 | 69
2018-02-23 23:30 | 70 | 68
2018-02-24 | 70 | 68
2018-02-24 00:30 | 69 | 67
2018-02-24 01:00 | 66 | 66
2018-02-24 01:30 | 65 | 65
2018-02-24 02:00 | 64 | 64
2018-02-24 02:30 | 64 | 64
2018-02-24 03:00 | 64 | 64
2018-02-24 03:30 | 65 | 65
2018-02-24 04:00 | 64 | 64
2018-02-24 04:30 | 63 | 63
2018-02-24 05:00 | 64 | 64
2018-02-24 05:30 | 64 | 64
2018-02-24 06:00 | 63 | 63
2018-02-24 06:30 | 63 | 63
2018-02-24 07:00 | 63 | 63
2018-02-24 07:30 | 65 | 65
2018-02-24 08:00 | 66 | 66
2018-02-24 08:30 | 67 | 67
2018-02-24 09:00 | 69 | 69
2018-02-24 09:30 | 73 | 73
2018-02-24 10:00 | 75 | 74
2018-02-24 10:30 | 75 | 75
2018-02-24 11:00 | 75 | 75
2018-02-24 11:30 | 75 | 74
2018-02-24 12:00 | 71 | 71
2018-02-24 12:30 | 70 | 70
2018-02-24 13:00 | 69 | 68
2018-02-24 13:30 | 70 | 70
2018-02-24 14:00 | 69 | 69
2018-02-24 14:30 | 69 | 69
2018-02-24 15:00 | 69 | 69
2018-02-24 15:30 | 68 | 68
2018-02-24 16:00 | 68 | 68
2018-02-24 16:30 | 68 | 67
2018-02-24 17:00 | 67 | 67
2018-02-24 17:30 | 67 | 67
2018-02-24 18:00 | 67 | 67
2018-02-24 18:30 | 68 | 68
2018-02-24 19:00 | 62 | 62
2018-02-24 19:30 | 62 | 62
2018-02-24 20:00 | 67 | 67
2018-02-24 20:30 | 64 | 64
2018-02-24 21:00 | 66 | 66
2018-02-24 21:30 | 68 | 68
2018-02-24 22:00 | 67 | 67
2018-02-24 22:30 | 70 | 70
2018-02-24 23:00 | 67 | 67
2018-02-24 23:30 | 65 | 65
2018-02-25 | 64 | 64
2018-02-25 00:30 | 68 | 68
2018-02-25 01:00 | 65 | 65
2018-02-25 01:30 | 64 | 64
2018-02-25 02:00 | 64 | 63
2018-02-25 02:30 | 63 | 63
2018-02-25 03:00 | 63 | 63
2018-02-25 03:30 | 62 | 62
2018-02-25 04:00 | 62 | 62
2018-02-25 04:30 | 62 | 62
2018-02-25 05:00 | 62 | 62
2018-02-25 05:30 | 61 | 61
2018-02-25 06:00 | 59 | 59
2018-02-25 06:30 | 60 | 60
2018-02-25 07:00 | 60 | 60
2018-02-25 07:30 | 62 | 62
2018-02-25 08:00 | 63 | 63
2018-02-25 08:30 | 65 | 65
2018-02-25 09:00 | 66 | 65
2018-02-25 09:30 | 67 | 66
2018-02-25 10:00 | 68 | 67
2018-02-25 10:30 | 68 | 68
2018-02-25 11:00 | 68 | 68
2018-02-25 11:30 | 68 | 68
2018-02-25 12:00 | 67 | 67
2018-02-25 12:30 | 67 | 67
2018-02-25 13:00 | 71 | 70
2018-02-25 13:30 | 74 | 73
2018-02-25 14:00 | 72 | 71
2018-02-25 14:30 | 73 | 72
2018-02-25 15:00 | 74 | 74
2018-02-25 15:30 | 72 | 72
2018-02-25 16:00 | 72 | 72
2018-02-25 16:30 | 72 | 72
2018-02-25 17:00 | 71 | 71
2018-02-25 17:30 | 71 | 71
2018-02-25 18:00 | 71 | 70
2018-02-25 18:30 | 71 | 71
2018-02-25 19:00 | 72 | 72
2018-02-25 19:30 | 73 | 72
2018-02-25 20:00 | 72 | 72
2018-02-25 20:30 | 73 | 72
2018-02-25 21:00 | 72 | 72
2018-02-25 21:30 | 71 | 71
2018-02-25 22:00 | 70 | 70
2018-02-25 22:30 | 70 | 69
2018-02-25 23:00 | 69 | 69
2018-02-25 23:30 | 68 | 68
2018-02-26 | 68 | 68
2018-02-26 00:30 | 68 | 68
2018-02-26 01:00 | 68 | 68
2018-02-26 01:30 | 68 | 67
2018-02-26 02:00 | 67 | 67
2018-02-26 02:30 | 67 | 67
2018-02-26 03:00 | 67 | 67
2018-02-26 03:30 | 67 | 67
2018-02-26 04:00 | 66 | 66
2018-02-26 04:30 | 66 | 66
2018-02-26 05:00 | 66 | 66
2018-02-26 05:30 | 67 | 67
2018-02-26 06:00 | 67 | 66
2018-02-26 06:30 | 67 | 67
2018-02-26 07:00 | 68 | 68
2018-02-26 07:30 | 70 | 70
2018-02-26 08:00 | 72 | 72
2018-02-26 08:30 | 73 | 72
2018-02-26 09:00 | 71 | 71
2018-02-26 09:30 | 71 | 70
2018-02-26 10:00 | 71 | 70
2018-02-26 10:30 | 70 | 70
2018-02-26 11:00 | 71 | 70
2018-02-26 11:30 | 72 | 71
2018-02-26 12:00 | 74 | 73
2018-02-26 12:30 | 74 | 73
2018-02-26 13:00 | 74 | 72
2018-02-26 13:30 | 74 | 73
2018-02-26 14:00 | 74 | 73
2018-02-26 14:30 | 70 | 68
2018-02-26 15:00 | 70 | 68
2018-02-26 15:30 | 73 | 71
2018-02-26 16:00 | 69 | 67
2018-02-26 16:30 | 67 | 64
2018-02-26 17:00 | 65 | 61
2018-02-26 17:30 | 67 | 63
2018-02-26 18:00 | 75 | 73
2018-02-26 18:30 | 76 | 74
2018-02-26 19:00 | 77 | 75
2018-02-26 19:30 | 76 | 75
2018-02-26 20:00 | 76 | 74
2018-02-26 20:30 | 75 | 73
2018-02-26 21:00 | 76 | 73
2018-02-26 21:30 | 75 | 73
2018-02-26 22:00 | 75 | 72
2018-02-26 22:30 | 75 | 71
2018-02-26 23:00 | 73 | 70
2018-02-26 23:30 | 71 | 69
2018-02-27 | 71 | 68
2018-02-27 00:30 | 70 | 68
2018-02-27 01:00 | 70 | 68
2018-02-27 01:30 | 70 | 68
2018-02-27 02:00 | 69 | 67
2018-02-27 02:30 | 69 | 67
2018-02-27 03:00 | 67 | 67
2018-02-27 03:30 | 67 | 66
2018-02-27 04:00 | 66 | 66
2018-02-27 04:30 | 66 | 66
2018-02-27 05:00 | 67 | 66
2018-02-27 05:30 | 68 | 68
2018-02-27 06:00 | 68 | 68
2018-02-27 06:30 | 69 | 69
2018-02-27 07:00 | 70 | 70
2018-02-27 07:30 | 73 | 72
2018-02-27 08:00 | 73 | 73
2018-02-27 08:30 | 73 | 73
2018-02-27 09:00 | 73 | 72
2018-02-27 09:30 | 74 | 73
2018-02-27 10:00 | 73 | 72
2018-02-27 10:30 | 73 | 73
2018-02-27 11:00 | 75 | 74
2018-02-27 11:30 | 75 | 74
2018-02-27 12:00 | 76 | 75
2018-02-27 12:30 | 76 | 75
2018-02-27 13:00 | 76 | 75
2018-02-27 13:30 | 75 | 75
2018-02-27 14:00 | 77 | 76
2018-02-27 14:30 | 77 | 77
2018-02-27 15:00 | 79 | 79
2018-02-27 15:30 | 78 | 77
2018-02-27 16:00 | 78 | 77
2018-02-27 16:30 | 78 | 77
2018-02-27 17:00 | 77 | 76
2018-02-27 17:30 | 76 | 74
2018-02-27 18:00 | 76 | 75
2018-02-27 18:30 | 77 | 76
2018-02-27 19:00 | 78 | 77
2018-02-27 19:30 | 78 | 77
2018-02-27 20:00 | 78 | 76
2018-02-27 20:30 | 77 | 76
2018-02-27 21:00 | 76 | 75
2018-02-27 21:30 | 75 | 73
2018-02-27 22:00 | 73 | 72
2018-02-27 22:30 | 74 | 71
2018-02-27 23:00 | 74 | 71
2018-02-27 23:30 | 73 | 70
2018-02-28 | 72 | 69
2018-02-28 00:30 | 73 | 70
2018-02-28 01:00 | 73 | 70
2018-02-28 01:30 | 71 | 68
2018-02-28 02:00 | 71 | 68
2018-02-28 02:30 | 71 | 67
2018-02-28 03:00 | 71 | 67
2018-02-28 03:30 | 71 | 67
2018-02-28 04:00 | 70 | 67
2018-02-28 04:30 | 70 | 67
2018-02-28 05:00 | 70 | 66
2018-02-28 05:30 | 70 | 67
2018-02-28 06:00 | 69 | 67
2018-02-28 06:30 | 71 | 68
2018-02-28 07:00 | 72 | 70
2018-02-28 07:30 | 73 | 71
2018-02-28 08:00 | 74 | 72
2018-02-28 08:30 | 81 | 73
2018-02-28 09:00 | 81 | 74
2018-02-28 09:30 | 80 | 72
2018-02-28 10:00 | 79 | 72
2018-02-28 10:30 | 79 | 72
2018-02-28 11:00 | 80 | 73
2018-02-28 11:30 | 82 | 74
2018-02-28 12:00 | 81 | 73
2018-02-28 12:30 | 80 | 72
2018-02-28 13:00 | 80 | 72
2018-02-28 13:30 | 80 | 71
2018-02-28 14:00 | 78 | 70
2018-02-28 14:30 | 78 | 70
2018-02-28 15:00 | 78 | 69
2018-02-28 15:30 | 78 | 68
2018-02-28 16:00 | 78 | 68
2018-02-28 16:30 | 80 | 70
2018-02-28 17:00 | 80 | 69
2018-02-28 17:30 | 81 | 69
2018-02-28 18:00 | 82 | 71
2018-02-28 18:30 | 83 | 72
2018-02-28 19:00 | 83 | 72
2018-02-28 19:30 | 83 | 72
2018-02-28 20:00 | 83 | 73
2018-02-28 20:30 | 83 | 72
2018-02-28 21:00 | 82 | 70
2018-02-28 21:30 | 74 | 69
2018-02-28 22:00 | 71 | 68
2018-02-28 22:30 | 70 | 67
2018-02-28 23:00 | 70 | 66
2018-02-28 23:30 | 69 | 65
2018-03-01 | 69 | 65
2018-03-01 00:30 | 70 | 65
2018-03-01 01:00 | 70 | 65
2018-03-01 01:30 | 70 | 65
2018-03-01 02:00 | 70 | 65
2018-03-01 02:30 | 69 | 65
2018-03-01 03:00 | 69 | 64
2018-03-01 03:30 | 69 | 65
2018-03-01 04:00 | 70 | 65
2018-03-01 04:30 | 69 | 65
2018-03-01 05:00 | 69 | 64
2018-03-01 05:30 | 69 | 65
2018-03-01 06:00 | 70 | 66
2018-03-01 06:30 | 70 | 67
2018-03-01 07:00 | 71 | 68
2018-03-01 07:30 | 72 | 70
2018-03-01 08:00 | 73 | 72
2018-03-01 08:30 | 73 | 71
2018-03-01 09:00 | 73 | 72
2018-03-01 09:30 | 74 | 73
2018-03-01 10:00 | 75 | 74
2018-03-01 10:30 | 75 | 74
2018-03-01 11:00 | 75 | 74
2018-03-01 11:30 | 71 | 70
2018-03-01 12:00 | 69 | 68
2018-03-01 12:30 | 69 | 68
2018-03-01 13:00 | 68 | 68
2018-03-01 13:30 | 69 | 68
2018-03-01 14:00 | 68 | 67
2018-03-01 14:30 | 68 | 67
2018-03-01 15:00 | 68 | 67
2018-03-01 15:30 | 67 | 67
2018-03-01 16:00 | 67 | 67
2018-03-01 16:30 | 68 | 68
2018-03-01 17:00 | 69 | 68
2018-03-01 17:30 | 69 | 68
2018-03-01 18:00 | 69 | 69
2018-03-01 18:30 | 70 | 69
2018-03-01 19:00 | 71 | 70
2018-03-01 19:30 | 71 | 71
2018-03-01 20:00 | 70 | 70
2018-03-01 20:30 | 70 | 69
2018-03-01 21:00 | 69 | 69
2018-03-01 21:30 | 73 | 73
2018-03-01 22:00 | 71 | 70
2018-03-01 22:30 | 70 | 69
2018-03-01 23:00 | 68 | 67
2018-03-01 23:30 | 67 | 66
2018-03-02 | 66 | 66
2018-03-02 00:30 | 65 | 65
2018-03-02 01:00 | 65 | 65
2018-03-02 01:30 | 65 | 65
2018-03-02 02:00 | 65 | 64
2018-03-02 02:30 | 64 | 63
2018-03-02 03:00 | 63 | 63
2018-03-02 03:30 | 63 | 63
2018-03-02 04:00 | 63 | 63
2018-03-02 04:30 | 63 | 62
2018-03-02 05:00 | 62 | 62
2018-03-02 05:30 | 63 | 63
2018-03-02 06:00 | 63 | 62
2018-03-02 06:30 | 64 | 64
2018-03-02 07:00 | 66 | 66
2018-03-02 07:30 | 67 | 67
2018-03-02 08:00 | 67 | 67
2018-03-02 08:30 | 69 | 69
2018-03-02 09:00 | 72 | 68
2018-03-02 09:30 | 72 | 69
2018-03-02 10:00 | 73 | 69
2018-03-02 10:30 | 73 | 70
2018-03-02 11:00 | 73 | 70
2018-03-02 11:30 | 71 | 68
2018-03-02 12:00 | 73 | 70
2018-03-02 12:30 | 73 | 70
2018-03-02 13:00 | 73 | 70
2018-03-02 13:30 | 74 | 71
2018-03-02 14:00 | 74 | 72
2018-03-02 14:30 | 75 | 72
2018-03-02 15:00 | 76 | 73
2018-03-02 15:30 | 75 | 73
2018-03-02 16:00 | 75 | 73
2018-03-02 16:30 | 75 | 72
2018-03-02 17:00 | 75 | 73
2018-03-02 17:30 | 75 | 72
2018-03-02 18:00 | 74 | 71
2018-03-02 18:30 | 74 | 71
2018-03-02 19:00 | 75 | 72
2018-03-02 19:30 | 76 | 73
2018-03-02 20:00 | 76 | 73
2018-03-02 20:30 | 75 | 72
2018-03-02 21:00 | 74 | 71
2018-03-02 21:30 | 74 | 70
2018-03-02 22:00 | 71 | 69
2018-03-02 22:30 | 67 | 67
2018-03-02 23:00 | 66 | 66
2018-03-02 23:30 | 66 | 66
2018-03-03 | 65 | 65
2018-03-03 00:30 | 65 | 65
2018-03-03 01:00 | 65 | 65
2018-03-03 01:30 | 65 | 65
2018-03-03 02:00 | 65 | 65
2018-03-03 02:30 | 65 | 65
2018-03-03 03:00 | 65 | 65
2018-03-03 03:30 | 65 | 65
2018-03-03 04:00 | 64 | 64
2018-03-03 04:30 | 64 | 64
2018-03-03 05:00 | 64 | 64
2018-03-03 05:30 | 64 | 63
2018-03-03 06:00 | 64 | 64
2018-03-03 06:30 | 64 | 64
2018-03-03 07:00 | 65 | 65
2018-03-03 07:30 | 65 | 65
2018-03-03 08:00 | 66 | 66
2018-03-03 08:30 | 66 | 66
2018-03-03 09:00 | 67 | 67
2018-03-03 09:30 | 68 | 68
2018-03-03 10:00 | 68 | 68
2018-03-03 10:30 | 55 | 54
2018-03-03 11:00 | 53 | 50
2018-03-03 11:30 | 52 | 50
2018-03-03 12:00 | 60 | 58
2018-03-03 12:30 | 76 | 70
2018-03-03 13:00 | 77 | 70
2018-03-03 13:30 | 77 | 71
2018-03-03 14:00 | 78 | 72
2018-03-03 14:30 | 79 | 73
2018-03-03 15:00 | 77 | 70
2018-03-03 15:30 | 75 | 68
2018-03-03 16:00 | 77 | 72
2018-03-03 16:30 | 78 | 73
2018-03-03 17:00 | 79 | 74
2018-03-03 17:30 | 79 | 74
2018-03-03 18:00 | 78 | 73
2018-03-03 18:30 | 78 | 73
2018-03-03 19:00 | 79 | 74
2018-03-03 19:30 | 79 | 75
2018-03-03 20:00 | 79 | 74
2018-03-03 20:30 | 79 | 74
2018-03-03 21:00 | 78 | 73
2018-03-03 21:30 | 78 | 72
2018-03-03 22:00 | 77 | 71
2018-03-03 22:30 | 75 | 69
2018-03-03 23:00 | 68 | 68
2018-03-03 23:30 | 68 | 67
2018-03-04 | 67 | 66
2018-03-04 00:30 | 67 | 66
2018-03-04 01:00 | 68 | 67
2018-03-04 01:30 | 67 | 67
2018-03-04 02:00 | 67 | 66
2018-03-04 02:30 | 67 | 66
2018-03-04 03:00 | 67 | 66
2018-03-04 03:30 | 66 | 65
2018-03-04 04:00 | 65 | 64
2018-03-04 04:30 | 66 | 65
2018-03-04 05:00 | 66 | 65
2018-03-04 05:30 | 67 | 66
2018-03-04 06:00 | 67 | 66
2018-03-04 06:30 | 66 | 65
2018-03-04 07:00 | 66 | 65
2018-03-04 07:30 | 65 | 64
2018-03-04 08:00 | 67 | 66
2018-03-04 08:30 | 67 | 67
2018-03-04 09:00 | 67 | 67
2018-03-04 09:30 | 67 | 67
2018-03-04 10:00 | 67 | 66
2018-03-04 10:30 | 67 | 67
2018-03-04 11:00 | 65 | 65
2018-03-04 11:30 | 67 | 66
2018-03-04 12:00 | 68 | 67
2018-03-04 12:30 | 69 | 69
2018-03-04 13:00 | 69 | 69
2018-03-04 13:30 | 70 | 69
2018-03-04 14:00 | 70 | 70
2018-03-04 14:30 | 70 | 70
2018-03-04 15:00 | 71 | 71
2018-03-04 15:30 | 71 | 71
2018-03-04 16:00 | 72 | 71
2018-03-04 16:30 | 72 | 72
2018-03-04 17:00 | 73 | 73
2018-03-04 17:30 | 73 | 73
2018-03-04 18:00 | 74 | 74
2018-03-04 18:30 | 73 | 73
2018-03-04 19:00 | 74 | 74
2018-03-04 19:30 | 74 | 74
2018-03-04 20:00 | 74 | 74
2018-03-04 20:30 | 72 | 72
2018-03-04 21:00 | 71 | 71
2018-03-04 21:30 | 70 | 69
2018-03-04 22:00 | 68 | 68
2018-03-04 22:30 | 67 | 67
2018-03-04 23:00 | 66 | 66
2018-03-04 23:30 | 66 | 66
2018-03-05 | 66 | 66
2018-03-05 00:30 | 65 | 65
2018-03-05 01:00 | 65 | 65
2018-03-05 01:30 | 64 | 63
2018-03-05 02:00 | 65 | 63
2018-03-05 02:30 | 65 | 63
2018-03-05 03:00 | 64 | 62
2018-03-05 03:30 | 64 | 61
2018-03-05 04:00 | 64 | 61
2018-03-05 04:30 | 64 | 62
2018-03-05 05:00 | 63 | 62
2018-03-05 05:30 | 63 | 62
2018-03-05 06:00 | 65 | 64
2018-03-05 06:30 | 66 | 66
2018-03-05 07:00 | 67 | 67
2018-03-05 07:30 | 70 | 69
2018-03-05 08:00 | 70 | 69
2018-03-05 08:30 | 70 | 70
2018-03-05 09:00 | 71 | 70
2018-03-05 09:30 | 73 | 73
2018-03-05 10:00 | 74 | 73
2018-03-05 10:30 | 73 | 73
2018-03-05 11:00 | 74 | 73
2018-03-05 11:30 | 74 | 73
2018-03-05 12:00 | 73 | 72
2018-03-05 12:30 | 73 | 72
2018-03-05 13:00 | 77 | 77
2018-03-05 13:30 | 77 | 77
2018-03-05 14:00 | 76 | 76
2018-03-05 14:30 | 78 | 78
2018-03-05 15:00 | 77 | 77
2018-03-05 15:30 | 72 | 72
2018-03-05 16:00 | 76 | 75
2018-03-05 16:30 | 76 | 76
2018-03-05 17:00 | 77 | 76
2018-03-05 17:30 | 77 | 76
2018-03-05 18:00 | 77 | 76
2018-03-05 18:30 | 76 | 75
2018-03-05 19:00 | 73 | 72
2018-03-05 19:30 | 73 | 73
2018-03-05 20:00 | 74 | 73
2018-03-05 20:30 | 74 | 73
2018-03-05 21:00 | 74 | 74
2018-03-05 21:30 | 71 | 71
2018-03-05 22:00 | 70 | 69
2018-03-05 22:30 | 68 | 67
2018-03-05 23:00 | 66 | 65
2018-03-05 23:30 | 70 | 69
2018-03-06 | 67 | 66
2018-03-06 00:30 | 67 | 66
2018-03-06 01:00 | 67 | 65
2018-03-06 01:30 | 66 | 65
2018-03-06 02:00 | 65 | 64
2018-03-06 02:30 | 66 | 64
2018-03-06 03:00 | 67 | 65
2018-03-06 03:30 | 66 | 64
2018-03-06 04:00 | 66 | 64
2018-03-06 04:30 | 66 | 65
2018-03-06 05:00 | 68 | 67
2018-03-06 05:30 | 68 | 67
2018-03-06 06:00 | 70 | 69
2018-03-06 06:30 | 72 | 71
2018-03-06 07:00 | 75 | 74
2018-03-06 07:30 | 77 | 77
2018-03-06 08:00 | 88 | 81
2018-03-06 08:30 | 87 | 80
2018-03-06 09:00 | 86 | 80
2018-03-06 09:30 | 86 | 80
2018-03-06 10:00 | 85 | 79
2018-03-06 10:30 | 85 | 79
2018-03-06 11:00 | 85 | 80
2018-03-06 11:30 | 84 | 80
2018-03-06 12:00 | 84 | 80
2018-03-06 12:30 | 82 | 79
2018-03-06 13:00 | 82 | 80
2018-03-06 13:30 | 86 | 81
2018-03-06 14:00 | 86 | 81
2018-03-06 14:30 | 86 | 81
2018-03-06 15:00 | 86 | 80
2018-03-06 15:30 | 85 | 79
2018-03-06 16:00 | 86 | 81
2018-03-06 16:30 | 88 | 82
2018-03-06 17:00 | 88 | 82
2018-03-06 17:30 | 89 | 83
2018-03-06 18:00 | 86 | 79
2018-03-06 18:30 | 82 | 75
2018-03-06 19:00 | 82 | 75
2018-03-06 19:30 | 81 | 75
2018-03-06 20:00 | 83 | 76
2018-03-06 20:30 | 82 | 75
2018-03-06 21:00 | 81 | 73
2018-03-06 21:30 | 76 | 71
2018-03-06 22:00 | 78 | 73
2018-03-06 22:30 | 76 | 72
2018-03-06 23:00 | 75 | 70
2018-03-06 23:30 | 74 | 69
2018-03-07 | 73 | 68
2018-03-07 00:30 | 70 | 67
2018-03-07 01:00 | 67 | 67
2018-03-07 01:30 | 66 | 66
2018-03-07 02:00 | 66 | 66
2018-03-07 02:30 | 66 | 66
2018-03-07 03:00 | 65 | 65
2018-03-07 03:30 | 64 | 64
2018-03-07 04:00 | 59 | 58
2018-03-07 04:30 | 56 | 56
2018-03-07 05:00 | 56 | 56
2018-03-07 05:30 | 57 | 56
2018-03-07 06:00 | 46 | 43
2018-03-07 06:30 | 40 | 35
2018-03-07 07:00 | 39 | 34
2018-03-07 07:30 | 39 | 35
2018-03-07 08:00 | 44 | 41
2018-03-07 08:30 | 45 | 41
2018-03-07 09:00 | 46 | 42
2018-03-07 09:30 | 45 | 41
2018-03-07 10:00 | 45 | 41
2018-03-07 10:30 | 45 | 42
2018-03-07 11:00 | 46 | 42
2018-03-07 11:30 | 49 | 47
2018-03-07 12:00 | 50 | 48
2018-03-07 12:30 | 51 | 49
2018-03-07 13:00 | 51 | 48
2018-03-07 13:30 | 51 | 47
2018-03-07 14:00 | 53 | 49
2018-03-07 14:30 | 54 | 51
2018-03-07 15:00 | 52 | 49
2018-03-07 15:30 | 51 | 47
2018-03-07 16:00 | 52 | 48
2018-03-07 16:30 | 50 | 44
2018-03-07 17:00 | 50 | 44
2018-03-07 17:30 | 51 | 45
2018-03-07 18:00 | 54 | 47
2018-03-07 18:30 | 55 | 49
2018-03-07 19:00 | 55 | 49
2018-03-07 19:30 | 54 | 49
2018-03-07 20:00 | 54 | 49
2018-03-07 20:30 | 54 | 49
2018-03-07 21:00 | 52 | 48
2018-03-07 21:30 | 60 | 59
2018-03-07 22:00 | 66 | 66
2018-03-07 22:30 | 66 | 66
2018-03-07 23:00 | 67 | 66
2018-03-07 23:30 | 66 | 65
2018-03-08 | 66 | 66
2018-03-08 00:30 | 67 | 66
2018-03-08 01:00 | 68 | 67
2018-03-08 01:30 | 69 | 68
2018-03-08 02:00 | 69 | 68
2018-03-08 02:30 | 69 | 68
2018-03-08 03:00 | 69 | 68
2018-03-08 03:30 | 68 | 67
2018-03-08 04:00 | 69 | 68
2018-03-08 04:30 | 69 | 68
2018-03-08 05:00 | 70 | 69
2018-03-08 05:30 | 71 | 70
2018-03-08 06:00 | 70 | 69
2018-03-08 06:30 | 70 | 69
2018-03-08 07:00 | 71 | 70
2018-03-08 07:30 | 73 | 71
2018-03-08 08:00 | 73 | 72
2018-03-08 08:30 | 73 | 73
2018-03-08 09:00 | 75 | 75
2018-03-08 09:30 | 75 | 75
2018-03-08 10:00 | 75 | 75
2018-03-08 10:30 | 74 | 74
2018-03-08 11:00 | 74 | 74
2018-03-08 11:30 | 73 | 73
2018-03-08 12:00 | 73 | 73
2018-03-08 12:30 | 71 | 71
2018-03-08 13:00 | 68 | 68
2018-03-08 13:30 | 69 | 69
2018-03-08 14:00 | 69 | 69
2018-03-08 14:30 | 69 | 68
2018-03-08 15:00 | 69 | 68
2018-03-08 15:30 | 69 | 69
2018-03-08 16:00 | 70 | 70
2018-03-08 16:30 | 70 | 69
2018-03-08 17:00 | 70 | 69
2018-03-08 17:30 | 70 | 69
2018-03-08 18:00 | 70 | 69
2018-03-08 18:30 | 70 | 69
2018-03-08 19:00 | 70 | 69
2018-03-08 19:30 | 70 | 70
2018-03-08 20:00 | 70 | 69
2018-03-08 20:30 | 69 | 68
2018-03-08 21:00 | 70 | 69
2018-03-08 21:30 | 69 | 68
2018-03-08 22:00 | 68 | 67
2018-03-08 22:30 | 66 | 65
2018-03-08 23:00 | 64 | 64
2018-03-08 23:30 | 64 | 63
2018-03-09 | 63 | 63
2018-03-09 00:30 | 62 | 62
2018-03-09 01:00 | 62 | 61
2018-03-09 01:30 | 61 | 61
2018-03-09 02:00 | 61 | 60
2018-03-09 02:30 | 61 | 60
2018-03-09 03:00 | 60 | 60
2018-03-09 03:30 | 60 | 60
2018-03-09 04:00 | 60 | 60
2018-03-09 04:30 | 60 | 60
2018-03-09 05:00 | 60 | 60
2018-03-09 05:30 | 61 | 61
2018-03-09 06:00 | 62 | 62
2018-03-09 06:30 | 63 | 62
2018-03-09 07:00 | 63 | 63
2018-03-09 07:30 | 64 | 64
2018-03-09 08:00 | 66 | 66
2018-03-09 08:30 | 67 | 65
2018-03-09 09:00 | 63 | 61
2018-03-09 09:30 | 62 | 60
2018-03-09 10:00 | 61 | 60
2018-03-09 10:30 | 60 | 59
2018-03-09 11:00 | 59 | 58
2018-03-09 11:30 | 63 | 62
2018-03-09 12:00 | 67 | 66
2018-03-09 12:30 | 67 | 66
2018-03-09 13:00 | 66 | 65
2018-03-09 13:30 | 66 | 65
2018-03-09 14:00 | 65 | 64
2018-03-09 14:30 | 64 | 63
2018-03-09 15:00 | 65 | 64
2018-03-09 15:30 | 65 | 64
2018-03-09 16:00 | 65 | 64
2018-03-09 16:30 | 66 | 65
2018-03-09 17:00 | 67 | 67
2018-03-09 17:30 | 68 | 68
2018-03-09 18:00 | 68 | 67
2018-03-09 18:30 | 68 | 67
2018-03-09 19:00 | 68 | 67
2018-03-09 19:30 | 68 | 67
2018-03-09 20:00 | 68 | 68
2018-03-09 20:30 | 68 | 67
2018-03-09 21:00 | 67 | 66
2018-03-09 21:30 | 70 | 70
2018-03-09 22:00 | 67 | 67
2018-03-09 22:30 | 66 | 66
2018-03-09 23:00 | 66 | 66
2018-03-09 23:30 | 64 | 64
2018-03-10 | 65 | 64
2018-03-10 00:30 | 64 | 64
2018-03-10 01:00 | 64 | 63
2018-03-10 01:30 | 64 | 63
2018-03-10 02:00 | 64 | 63
2018-03-10 02:30 | 63 | 62
2018-03-10 03:00 | 62 | 61
2018-03-10 03:30 | 62 | 61
2018-03-10 04:00 | 63 | 61
2018-03-10 04:30 | 63 | 61
2018-03-10 05:00 | 63 | 62
2018-03-10 05:30 | 63 | 62
2018-03-10 06:00 | 63 | 61
2018-03-10 06:30 | 63 | 62
2018-03-10 07:00 | 62 | 61
2018-03-10 07:30 | 63 | 62
2018-03-10 08:00 | 63 | 62
2018-03-10 08:30 | 65 | 64
2018-03-10 09:00 | 65 | 64
2018-03-10 09:30 | 67 | 66
2018-03-10 10:00 | 67 | 66
2018-03-10 10:30 | 67 | 66
2018-03-10 11:00 | 68 | 67
2018-03-10 11:30 | 69 | 68
2018-03-10 12:00 | 70 | 69
2018-03-10 12:30 | 70 | 69
2018-03-10 13:00 | 70 | 69
2018-03-10 13:30 | 71 | 70
2018-03-10 14:00 | 72 | 71
2018-03-10 14:30 | 71 | 71
2018-03-10 15:00 | 71 | 70
2018-03-10 15:30 | 72 | 71
2018-03-10 16:00 | 73 | 72
2018-03-10 16:30 | 74 | 73
2018-03-10 17:00 | 75 | 74
2018-03-10 17:30 | 76 | 76
2018-03-10 18:00 | 76 | 76
2018-03-10 18:30 | 75 | 75
2018-03-10 19:00 | 75 | 75
2018-03-10 19:30 | 76 | 75
2018-03-10 20:00 | 76 | 75
2018-03-10 20:30 | 75 | 74
2018-03-10 21:00 | 75 | 74
2018-03-10 21:30 | 73 | 73
2018-03-10 22:00 | 72 | 72
2018-03-10 22:30 | 72 | 72
2018-03-10 23:00 | 70 | 70
2018-03-10 23:30 | 69 | 68
2018-03-11 | 69 | 68
2018-03-11 00:30 | 68 | 67
2018-03-11 01:00 | 69 | 67
2018-03-11 01:30 | 69 | 66
2018-03-11 02:00 | 69 | 66
2018-03-11 02:30 | 68 | 65
2018-03-11 03:00 | 66 | 65
2018-03-11 03:30 | 66 | 66
2018-03-11 04:00 | 65 | 65
2018-03-11 04:30 | 66 | 66
2018-03-11 05:00 | 65 | 65
2018-03-11 05:30 | 66 | 66
2018-03-11 06:00 | 65 | 65
2018-03-11 06:30 | 65 | 65
2018-03-11 07:00 | 64 | 64
2018-03-11 07:30 | 66 | 66
2018-03-11 08:00 | 67 | 67
2018-03-11 08:30 | 68 | 68
2018-03-11 09:00 | 69 | 69
2018-03-11 09:30 | 70 | 70
2018-03-11 10:00 | 70 | 68
2018-03-11 10:30 | 69 | 67
2018-03-11 11:00 | 69 | 66
2018-03-11 11:30 | 68 | 66
2018-03-11 12:00 | 69 | 67
2018-03-11 12:30 | 69 | 67
2018-03-11 13:00 | 70 | 68
2018-03-11 13:30 | 71 | 69
2018-03-11 14:00 | 74 | 71
2018-03-11 14:30 | 75 | 73
2018-03-11 15:00 | 76 | 74
2018-03-11 15:30 | 74 | 73
2018-03-11 16:00 | 73 | 71
2018-03-11 16:30 | 74 | 72
2018-03-11 17:00 | 75 | 73
2018-03-11 17:30 | 75 | 73
2018-03-11 18:00 | 76 | 75
2018-03-11 18:30 | 77 | 76
2018-03-11 19:00 | 79 | 78
2018-03-11 19:30 | 79 | 78
2018-03-11 20:00 | 79 | 78
2018-03-11 20:30 | 78 | 77
2018-03-11 21:00 | 76 | 75
2018-03-11 21:30 | 76 | 75
2018-03-11 22:00 | 75 | 73
2018-03-11 22:30 | 73 | 71
2018-03-11 23:00 | 73 | 70
2018-03-11 23:30 | 71 | 69
2018-03-12 | 70 | 68
2018-03-12 00:30 | 70 | 67
2018-03-12 01:00 | 69 | 66
2018-03-12 01:30 | 69 | 66
2018-03-12 02:00 | 68 | 66
2018-03-12 02:30 | 67 | 65
2018-03-12 03:00 | 66 | 65
2018-03-12 03:30 | 66 | 65
2018-03-12 04:00 | 65 | 65
2018-03-12 04:30 | 65 | 64
2018-03-12 05:00 | 65 | 65
2018-03-12 05:30 | 66 | 66
2018-03-12 06:00 | 66 | 65
2018-03-12 06:30 | 68 | 67
2018-03-12 07:00 | 70 | 70
2018-03-12 07:30 | 73 | 73
2018-03-12 08:00 | 74 | 73
2018-03-12 08:30 | 73 | 73
2018-03-12 09:00 | 73 | 73
2018-03-12 09:30 | 73 | 73
2018-03-12 10:00 | 73 | 73
2018-03-12 10:30 | 73 | 73
2018-03-12 11:00 | 73 | 73
2018-03-12 11:30 | 73 | 73
2018-03-12 12:00 | 74 | 74
2018-03-12 12:30 | 74 | 74
2018-03-12 13:00 | 75 | 75
2018-03-12 13:30 | 75 | 75
2018-03-12 14:00 | 75 | 75
2018-03-12 14:30 | 76 | 76
2018-03-12 15:00 | 75 | 75
2018-03-12 15:30 | 75 | 75
2018-03-12 16:00 | 74 | 74
2018-03-12 16:30 | 74 | 74
2018-03-12 17:00 | 75 | 75
2018-03-12 17:30 | 76 | 76
2018-03-12 18:00 | 75 | 75
2018-03-12 18:30 | 74 | 74
2018-03-12 19:00 | 76 | 76
2018-03-12 19:30 | 77 | 77
2018-03-12 20:00 | 76 | 76
2018-03-12 20:30 | 76 | 75
2018-03-12 21:00 | 75 | 75
2018-03-12 21:30 | 74 | 73
2018-03-12 22:00 | 72 | 71
2018-03-12 22:30 | 71 | 70
2018-03-12 23:00 | 70 | 70
2018-03-12 23:30 | 69 | 68
2018-03-13 | 68 | 68
2018-03-13 00:30 | 68 | 68
2018-03-13 01:00 | 68 | 67
2018-03-13 01:30 | 69 | 67
2018-03-13 02:00 | 69 | 66
2018-03-13 02:30 | 69 | 66
2018-03-13 03:00 | 68 | 65
2018-03-13 03:30 | 67 | 64
2018-03-13 04:00 | 64 | 64
2018-03-13 04:30 | 64 | 64
2018-03-13 05:00 | 64 | 64
2018-03-13 05:30 | 64 | 64
2018-03-13 06:00 | 64 | 64
2018-03-13 06:30 | 65 | 65
2018-03-13 07:00 | 67 | 67
2018-03-13 07:30 | 70 | 70
2018-03-13 08:00 | 75 | 72
2018-03-13 08:30 | 74 | 71
2018-03-13 09:00 | 74 | 73
2018-03-13 09:30 | 76 | 75
2018-03-13 10:00 | 76 | 75
2018-03-13 10:30 | 77 | 75
2018-03-13 11:00 | 76 | 75
2018-03-13 11:30 | 77 | 76
2018-03-13 12:00 | 77 | 75
2018-03-13 12:30 | 78 | 77
2018-03-13 13:00 | 79 | 77
2018-03-13 13:30 | 79 | 78
2018-03-13 14:00 | 80 | 79
2018-03-13 14:30 | 81 | 80
2018-03-13 15:00 | 81 | 80
2018-03-13 15:30 | 81 | 80
2018-03-13 16:00 | 82 | 81
2018-03-13 16:30 | 83 | 82
2018-03-13 17:00 | 84 | 84
2018-03-13 17:30 | 85 | 84
2018-03-13 18:00 | 84 | 83
2018-03-13 18:30 | 85 | 84
2018-03-13 19:00 | 85 | 84
2018-03-13 19:30 | 87 | 86
2018-03-13 20:00 | 86 | 85
2018-03-13 20:30 | 85 | 84
2018-03-13 21:00 | 84 | 83
2018-03-13 21:30 | 83 | 82
2018-03-13 22:00 | 81 | 79
2018-03-13 22:30 | 80 | 78
2018-03-13 23:00 | 79 | 77
2018-03-13 23:30 | 78 | 75
2018-03-14 | 77 | 75
2018-03-14 00:30 | 73 | 73
2018-03-14 01:00 | 74 | 73
2018-03-14 01:30 | 73 | 73
2018-03-14 02:00 | 73 | 72
2018-03-14 02:30 | 72 | 72
2018-03-14 03:00 | 72 | 71
2018-03-14 03:30 | 71 | 71
2018-03-14 04:00 | 71 | 71
2018-03-14 04:30 | 72 | 71
2018-03-14 05:00 | 72 | 71
2018-03-14 05:30 | 72 | 72
2018-03-14 06:00 | 73 | 73
2018-03-14 06:30 | 75 | 74
2018-03-14 07:00 | 77 | 76
2018-03-14 07:30 | 79 | 79
2018-03-14 08:00 | 80 | 80
2018-03-14 08:30 | 80 | 80
2018-03-14 09:00 | 80 | 80
2018-03-14 09:30 | 80 | 80
2018-03-14 10:00 | 80 | 79
2018-03-14 10:30 | 79 | 79
2018-03-14 11:00 | 79 | 79
2018-03-14 11:30 | 79 | 78
2018-03-14 12:00 | 80 | 80
2018-03-14 12:30 | 80 | 80
2018-03-14 13:00 | 81 | 80
2018-03-14 13:30 | 81 | 81
2018-03-14 14:00 | 82 | 81
2018-03-14 14:30 | 81 | 81
2018-03-14 15:00 | 81 | 81
2018-03-14 15:30 | 83 | 82
2018-03-14 16:00 | 84 | 84
2018-03-14 16:30 | 86 | 85
2018-03-14 17:00 | 88 | 88
2018-03-14 17:30 | 88 | 88
2018-03-14 18:00 | 87 | 87
2018-03-14 18:30 | 81 | 81
2018-03-14 19:00 | 81 | 81
2018-03-14 19:30 | 80 | 80
2018-03-14 20:00 | 79 | 79
2018-03-14 20:30 | 79 | 79
2018-03-14 21:00 | 82 | 81
2018-03-14 21:30 | 81 | 80
2018-03-14 22:00 | 78 | 77
2018-03-14 22:30 | 76 | 75
2018-03-14 23:00 | 74 | 73
2018-03-14 23:30 | 73 | 72
2018-03-15 | 74 | 72
2018-03-15 00:30 | 73 | 72
2018-03-15 01:00 | 73 | 71
2018-03-15 01:30 | 73 | 71
2018-03-15 02:00 | 72 | 71
2018-03-15 02:30 | 72 | 70
2018-03-15 03:00 | 72 | 70
2018-03-15 03:30 | 73 | 71
2018-03-15 04:00 | 72 | 71
2018-03-15 04:30 | 73 | 72
2018-03-15 05:00 | 75 | 73
2018-03-15 05:30 | 75 | 74
2018-03-15 06:00 | 76 | 74
2018-03-15 06:30 | 77 | 76
2018-03-15 07:00 | 75 | 73
2018-03-15 07:30 | 67 | 63
2018-03-15 08:00 | 64 | 60
2018-03-15 08:30 | 63 | 60
2018-03-15 09:00 | 68 | 65
2018-03-15 09:30 | 70 | 69
2018-03-15 10:00 | 70 | 69
2018-03-15 10:30 | 71 | 69
2018-03-15 11:00 | 68 | 67
2018-03-15 11:30 | 67 | 66
2018-03-15 12:00 | 68 | 67
2018-03-15 12:30 | 69 | 66
2018-03-15 13:00 | 70 | 69
2018-03-15 13:30 | 72 | 72
2018-03-15 14:00 | 74 | 74
2018-03-15 14:30 | 74 | 74
2018-03-15 15:00 | 73 | 73
2018-03-15 15:30 | 73 | 73
2018-03-15 16:00 | 74 | 74
2018-03-15 16:30 | 75 | 75
2018-03-15 17:00 | 72 | 72
2018-03-15 17:30 | 76 | 76
2018-03-15 18:00 | 74 | 74
2018-03-15 18:30 | 70 | 70
2018-03-15 19:00 | 71 | 71
2018-03-15 19:30 | 72 | 72
2018-03-15 20:00 | 72 | 72
2018-03-15 20:30 | 71 | 70
2018-03-15 21:00 | 69 | 69
2018-03-15 21:30 | 72 | 72
2018-03-15 22:00 | 70 | 70
2018-03-15 22:30 | 68 | 68
2018-03-15 23:00 | 71 | 71
2018-03-15 23:30 | 72 | 72
2018-03-16 | 71 | 71
2018-03-16 00:30 | 72 | 70
2018-03-16 01:00 | 72 | 70
2018-03-16 01:30 | 71 | 69
2018-03-16 02:00 | 69 | 69
2018-03-16 02:30 | 64 | 64
2018-03-16 03:00 | 63 | 63
2018-03-16 03:30 | 63 | 63
2018-03-16 04:00 | 63 | 63
2018-03-16 04:30 | 63 | 63
2018-03-16 05:00 | 64 | 64
2018-03-16 05:30 | 69 | 69
2018-03-16 06:00 | 65 | 65
2018-03-16 06:30 | 64 | 64
2018-03-16 07:00 | 66 | 66
2018-03-16 07:30 | 68 | 68
2018-03-16 08:00 | 70 | 70
2018-03-16 08:30 | 70 | 70
2018-03-16 09:00 | 71 | 71
2018-03-16 09:30 | 70 | 70
2018-03-16 10:00 | 70 | 70
2018-03-16 10:30 | 70 | 70
2018-03-16 11:00 | 70 | 70
2018-03-16 11:30 | 70 | 70
2018-03-16 12:00 | 74 | 71
2018-03-16 12:30 | 75 | 71
2018-03-16 13:00 | 76 | 72
2018-03-16 13:30 | 76 | 73
2018-03-16 14:00 | 76 | 73
2018-03-16 14:30 | 78 | 77
2018-03-16 15:00 | 79 | 78
2018-03-16 15:30 | 79 | 78
2018-03-16 16:00 | 81 | 80
2018-03-16 16:30 | 83 | 82
2018-03-16 17:00 | 84 | 83
2018-03-16 17:30 | 84 | 83
2018-03-16 18:00 | 82 | 81
2018-03-16 18:30 | 78 | 77
2018-03-16 19:00 | 79 | 78
2018-03-16 19:30 | 80 | 79
2018-03-16 20:00 | 79 | 78
2018-03-16 20:30 | 77 | 76
2018-03-16 21:00 | 78 | 77
2018-03-16 21:30 | 78 | 77
2018-03-16 22:00 | 77 | 76
2018-03-16 22:30 | 75 | 73
2018-03-16 23:00 | 73 | 71
2018-03-16 23:30 | 74 | 71
2018-03-17 | 72 | 70
2018-03-17 00:30 | 71 | 70
2018-03-17 01:00 | 70 | 69
2018-03-17 01:30 | 68 | 68
2018-03-17 02:00 | 68 | 67
2018-03-17 02:30 | 68 | 67
2018-03-17 03:00 | 68 | 67
2018-03-17 03:30 | 67 | 66
2018-03-17 04:00 | 68 | 67
2018-03-17 04:30 | 67 | 66
2018-03-17 05:00 | 68 | 67
2018-03-17 05:30 | 68 | 67
2018-03-17 06:00 | 67 | 66
2018-03-17 06:30 | 67 | 66
2018-03-17 07:00 | 68 | 67
2018-03-17 07:30 | 70 | 69
2018-03-17 08:00 | 71 | 71
2018-03-17 08:30 | 71 | 71
2018-03-17 09:00 | 71 | 70
2018-03-17 09:30 | 65 | 65
2018-03-17 10:00 | 63 | 63
2018-03-17 10:30 | 63 | 63
2018-03-17 11:00 | 63 | 63
2018-03-17 11:30 | 64 | 63
2018-03-17 12:00 | 64 | 64
2018-03-17 12:30 | 65 | 65
2018-03-17 13:00 | 66 | 65
2018-03-17 13:30 | 67 | 67
2018-03-17 14:00 | 67 | 67
2018-03-17 14:30 | 70 | 70
2018-03-17 15:00 | 75 | 75
2018-03-17 15:30 | 75 | 75
2018-03-17 16:00 | 76 | 76
2018-03-17 16:30 | 77 | 77
2018-03-17 17:00 | 78 | 78
2018-03-17 17:30 | 79 | 79
2018-03-17 18:00 | 79 | 79
2018-03-17 18:30 | 79 | 79
2018-03-17 19:00 | 79 | 79
2018-03-17 19:30 | 80 | 79
2018-03-17 20:00 | 79 | 79
2018-03-17 20:30 | 79 | 78
2018-03-17 21:00 | 77 | 77
2018-03-17 21:30 | 77 | 77
2018-03-17 22:00 | 76 | 75
2018-03-17 22:30 | 73 | 73
2018-03-17 23:00 | 72 | 72
2018-03-17 23:30 | 71 | 71
2018-03-18 | 71 | 70
2018-03-18 00:30 | 70 | 70
2018-03-18 01:00 | 70 | 69
2018-03-18 01:30 | 69 | 69
2018-03-18 02:00 | 68 | 68
2018-03-18 02:30 | 69 | 68
2018-03-18 03:00 | 68 | 68
2018-03-18 03:30 | 68 | 68
2018-03-18 04:00 | 68 | 68
2018-03-18 04:30 | 67 | 67
2018-03-18 05:00 | 66 | 65
2018-03-18 05:30 | 66 | 65
2018-03-18 06:00 | 66 | 65
2018-03-18 06:30 | 65 | 64
2018-03-18 07:00 | 66 | 65
2018-03-18 07:30 | 68 | 67
2018-03-18 08:00 | 69 | 68
2018-03-18 08:30 | 69 | 69
2018-03-18 09:00 | 69 | 69
2018-03-18 09:30 | 69 | 69
2018-03-18 10:00 | 70 | 69
2018-03-18 10:30 | 70 | 69
2018-03-18 11:00 | 71 | 70
2018-03-18 11:30 | 70 | 70
2018-03-18 12:00 | 71 | 70
2018-03-18 12:30 | 72 | 71
2018-03-18 13:00 | 73 | 73
2018-03-18 13:30 | 75 | 75
2018-03-18 14:00 | 75 | 75
2018-03-18 14:30 | 75 | 75
2018-03-18 15:00 | 76 | 76
2018-03-18 15:30 | 76 | 76
2018-03-18 16:00 | 77 | 76
2018-03-18 16:30 | 78 | 77
2018-03-18 17:00 | 78 | 78
2018-03-18 17:30 | 79 | 79
2018-03-18 18:00 | 79 | 79
2018-03-18 18:30 | 79 | 79
2018-03-18 19:00 | 81 | 81
2018-03-18 19:30 | 81 | 81
2018-03-18 20:00 | 80 | 80
2018-03-18 20:30 | 78 | 78
2018-03-18 21:00 | 77 | 77
2018-03-18 21:30 | 77 | 76
2018-03-18 22:00 | 75 | 74
2018-03-18 22:30 | 74 | 73
2018-03-18 23:00 | 73 | 71
2018-03-18 23:30 | 72 | 71
2018-03-19 | 72 | 70
2018-03-19 00:30 | 72 | 70
2018-03-19 01:00 | 71 | 69
2018-03-19 01:30 | 70 | 68
2018-03-19 02:00 | 70 | 68
2018-03-19 02:30 | 69 | 68
2018-03-19 03:00 | 69 | 67
2018-03-19 03:30 | 68 | 66
2018-03-19 04:00 | 67 | 66
2018-03-19 04:30 | 67 | 66
2018-03-19 05:00 | 67 | 67
2018-03-19 05:30 | 68 | 68
2018-03-19 06:00 | 68 | 68
2018-03-19 06:30 | 69 | 68
2018-03-19 07:00 | 71 | 71
2018-03-19 07:30 | 74 | 73
2018-03-19 08:00 | 76 | 76
2018-03-19 08:30 | 76 | 76
2018-03-19 09:00 | 77 | 77
2018-03-19 09:30 | 78 | 78
2018-03-19 10:00 | 77 | 77
2018-03-19 10:30 | 77 | 77
2018-03-19 11:00 | 78 | 78
2018-03-19 11:30 | 75 | 75
2018-03-19 12:00 | 74 | 74
2018-03-19 12:30 | 74 | 74
2018-03-19 13:00 | 74 | 74
2018-03-19 13:30 | 74 | 74
2018-03-19 14:00 | 74 | 74
2018-03-19 14:30 | 76 | 76
2018-03-19 15:00 | 77 | 77
2018-03-19 15:30 | 77 | 77
2018-03-19 16:00 | 79 | 79
2018-03-19 16:30 | 81 | 81
2018-03-19 17:00 | 83 | 83
2018-03-19 17:30 | 83 | 83
2018-03-19 18:00 | 81 | 81
2018-03-19 18:30 | 81 | 81
2018-03-19 19:00 | 83 | 83
2018-03-19 19:30 | 84 | 84
2018-03-19 20:00 | 83 | 83
2018-03-19 20:30 | 83 | 82
2018-03-19 21:00 | 81 | 80
2018-03-19 21:30 | 80 | 79
2018-03-19 22:00 | 78 | 77
2018-03-19 22:30 | 76 | 74
2018-03-19 23:00 | 74 | 72
2018-03-19 23:30 | 74 | 72
2018-03-20 | 72 | 71
2018-03-20 00:30 | 70 | 70
2018-03-20 01:00 | 69 | 69
2018-03-20 01:30 | 69 | 69
2018-03-20 02:00 | 68 | 68
2018-03-20 02:30 | 68 | 68
2018-03-20 03:00 | 67 | 67
2018-03-20 03:30 | 66 | 66
2018-03-20 04:00 | 66 | 66
2018-03-20 04:30 | 66 | 66
2018-03-20 05:00 | 66 | 66
2018-03-20 05:30 | 66 | 66
2018-03-20 06:00 | 67 | 67
2018-03-20 06:30 | 69 | 69
2018-03-20 07:00 | 70 | 70
2018-03-20 07:30 | 72 | 72
2018-03-20 08:00 | 73 | 73
2018-03-20 08:30 | 74 | 74
2018-03-20 09:00 | 74 | 74
2018-03-20 09:30 | 75 | 74
2018-03-20 10:00 | 76 | 75
2018-03-20 10:30 | 78 | 77
2018-03-20 11:00 | 86 | 85
2018-03-20 11:30 | 87 | 86
2018-03-20 12:00 | 87 | 86
2018-03-20 12:30 | 88 | 87
2018-03-20 13:00 | 88 | 87
2018-03-20 13:30 | 88 | 87
2018-03-20 14:00 | 89 | 89
2018-03-20 14:30 | 89 | 89
2018-03-20 15:00 | 90 | 89
2018-03-20 15:30 | 90 | 90
2018-03-20 16:00 | 91 | 90
2018-03-20 16:30 | 91 | 90
2018-03-20 17:00 | 93 | 92
2018-03-20 17:30 | 92 | 91
2018-03-20 18:00 | 90 | 89
2018-03-20 18:30 | 90 | 89
2018-03-20 19:00 | 92 | 90
2018-03-20 19:30 | 92 | 91
2018-03-20 20:00 | 94 | 93
2018-03-20 20:30 | 92 | 91
2018-03-20 21:00 | 91 | 90
2018-03-20 21:30 | 89 | 89
2018-03-20 22:00 | 87 | 87
2018-03-20 22:30 | 84 | 83
2018-03-20 23:00 | 85 | 85
2018-03-20 23:30 | 83 | 82
2018-03-21 | 83 | 81
2018-03-21 00:30 | 82 | 80
2018-03-21 01:00 | 81 | 79
2018-03-21 01:30 | 80 | 79
2018-03-21 02:00 | 80 | 78
2018-03-21 02:30 | 80 | 78
2018-03-21 03:00 | 78 | 77
2018-03-21 03:30 | 78 | 77
2018-03-21 04:00 | 78 | 76
2018-03-21 04:30 | 78 | 77
2018-03-21 05:00 | 78 | 77
2018-03-21 05:30 | 78 | 77
2018-03-21 06:00 | 78 | 77
2018-03-21 06:30 | 80 | 78
2018-03-21 07:00 | 82 | 80
2018-03-21 07:30 | 83 | 82
2018-03-21 08:00 | 84 | 84
2018-03-21 08:30 | 83 | 83
2018-03-21 09:00 | 83 | 83
2018-03-21 09:30 | 83 | 83
2018-03-21 10:00 | 81 | 81
2018-03-21 10:30 | 83 | 82
2018-03-21 11:00 | 83 | 83
2018-03-21 11:30 | 84 | 84
2018-03-21 12:00 | 83 | 83
2018-03-21 12:30 | 84 | 84
2018-03-21 13:00 | 84 | 84
2018-03-21 13:30 | 84 | 84
2018-03-21 14:00 | 86 | 85
2018-03-21 14:30 | 85 | 85
2018-03-21 15:00 | 86 | 86
2018-03-21 15:30 | 86 | 85
2018-03-21 16:00 | 85 | 85
2018-03-21 16:30 | 85 | 85
2018-03-21 17:00 | 85 | 84
2018-03-21 17:30 | 85 | 84
2018-03-21 18:00 | 87 | 86
2018-03-21 18:30 | 88 | 87
2018-03-21 19:00 | 89 | 88
2018-03-21 19:30 | 88 | 87
2018-03-21 20:00 | 87 | 86
2018-03-21 20:30 | 85 | 84
2018-03-21 21:00 | 85 | 84
2018-03-21 21:30 | 82 | 82
2018-03-21 22:00 | 81 | 80
2018-03-21 22:30 | 79 | 78
2018-03-21 23:00 | 77 | 76
2018-03-21 23:30 | 76 | 75
2018-03-22 | 76 | 75
2018-03-22 00:30 | 76 | 75
2018-03-22 01:00 | 76 | 75
2018-03-22 01:30 | 76 | 75
2018-03-22 02:00 | 75 | 74
2018-03-22 02:30 | 75 | 73
2018-03-22 03:00 | 76 | 74
2018-03-22 03:30 | 73 | 73
2018-03-22 04:00 | 74 | 73
2018-03-22 04:30 | 73 | 73
2018-03-22 05:00 | 74 | 73
2018-03-22 05:30 | 74 | 73
2018-03-22 06:00 | 74 | 74
2018-03-22 06:30 | 76 | 75
2018-03-22 07:00 | 77 | 76
2018-03-22 07:30 | 77 | 77
2018-03-22 08:00 | 80 | 79
2018-03-22 08:30 | 80 | 79
2018-03-22 09:00 | 80 | 79
2018-03-22 09:30 | 79 | 78
2018-03-22 10:00 | 78 | 77
2018-03-22 10:30 | 77 | 76
2018-03-22 11:00 | 79 | 78
2018-03-22 11:30 | 80 | 79
2018-03-22 12:00 | 79 | 78
2018-03-22 12:30 | 79 | 79
2018-03-22 13:00 | 80 | 79
2018-03-22 13:30 | 80 | 80
2018-03-22 14:00 | 81 | 81
2018-03-22 14:30 | 82 | 82
2018-03-22 15:00 | 81 | 81
2018-03-22 15:30 | 82 | 82
2018-03-22 16:00 | 83 | 82
2018-03-22 16:30 | 83 | 83
2018-03-22 17:00 | 84 | 83
2018-03-22 17:30 | 86 | 86
2018-03-22 18:00 | 84 | 84
2018-03-22 18:30 | 83 | 83
2018-03-22 19:00 | 84 | 84
2018-03-22 19:30 | 85 | 85
2018-03-22 20:00 | 85 | 85
2018-03-22 20:30 | 85 | 85
2018-03-22 21:00 | 84 | 83
2018-03-22 21:30 | 83 | 82
2018-03-22 22:00 | 81 | 81
2018-03-22 22:30 | 81 | 81
2018-03-22 23:00 | 79 | 79
2018-03-22 23:30 | 79 | 78
2018-03-23 | 78 | 78
2018-03-23 00:30 | 77 | 77
2018-03-23 01:00 | 78 | 77
2018-03-23 01:30 | 78 | 77
2018-03-23 02:00 | 77 | 76
2018-03-23 02:30 | 76 | 76
2018-03-23 03:00 | 76 | 75
2018-03-23 03:30 | 76 | 75
2018-03-23 04:00 | 76 | 75
2018-03-23 04:30 | 76 | 75
2018-03-23 05:00 | 76 | 75
2018-03-23 05:30 | 76 | 75
2018-03-23 06:00 | 75 | 75
2018-03-23 06:30 | 77 | 77
2018-03-23 07:00 | 77 | 77
2018-03-23 07:30 | 79 | 79
2018-03-23 08:00 | 79 | 78
2018-03-23 08:30 | 79 | 78
2018-03-23 09:00 | 78 | 78
2018-03-23 09:30 | 78 | 78
2018-03-23 10:00 | 79 | 78
2018-03-23 10:30 | 79 | 79
2018-03-23 11:00 | 80 | 79
2018-03-23 11:30 | 79 | 79
2018-03-23 12:00 | 83 | 82
2018-03-23 12:30 | 84 | 83
2018-03-23 13:00 | 83 | 82
2018-03-23 13:30 | 82 | 82
2018-03-23 14:00 | 83 | 82
2018-03-23 14:30 | 80 | 80
2018-03-23 15:00 | 80 | 80
2018-03-23 15:30 | 78 | 77
2018-03-23 16:00 | 78 | 76
2018-03-23 16:30 | 77 | 76
2018-03-23 17:00 | 77 | 75
2018-03-23 17:30 | 77 | 75
2018-03-23 18:00 | 77 | 74
2018-03-23 18:30 | 78 | 75
2018-03-23 19:00 | 78 | 77
2018-03-23 19:30 | 79 | 77
2018-03-23 20:00 | 79 | 77
2018-03-23 20:30 | 78 | 76
2018-03-23 21:00 | 78 | 76
2018-03-23 21:30 | 77 | 75
2018-03-23 22:00 | 77 | 75
2018-03-23 22:30 | 75 | 74
2018-03-23 23:00 | 74 | 73
2018-03-23 23:30 | 73 | 72
2018-03-24 | 72 | 71
2018-03-24 00:30 | 72 | 71
2018-03-24 01:00 | 72 | 71
2018-03-24 01:30 | 71 | 70
2018-03-24 02:00 | 72 | 71
2018-03-24 02:30 | 72 | 71
2018-03-24 03:00 | 71 | 70
2018-03-24 03:30 | 72 | 70
2018-03-24 04:00 | 71 | 70
2018-03-24 04:30 | 71 | 70
2018-03-24 05:00 | 70 | 68
2018-03-24 05:30 | 70 | 69
2018-03-24 06:00 | 70 | 68
2018-03-24 06:30 | 71 | 69
2018-03-24 07:00 | 71 | 70
2018-03-24 07:30 | 72 | 71
2018-03-24 08:00 | 72 | 71
2018-03-24 08:30 | 72 | 71
2018-03-24 09:00 | 72 | 72
2018-03-24 09:30 | 72 | 71
2018-03-24 10:00 | 72 | 72
2018-03-24 10:30 | 72 | 72
2018-03-24 11:00 | 72 | 72
2018-03-24 11:30 | 72 | 71
2018-03-24 12:00 | 73 | 72
2018-03-24 12:30 | 73 | 72
2018-03-24 13:00 | 73 | 73
2018-03-24 13:30 | 73 | 73
2018-03-24 14:00 | 74 | 73
2018-03-24 14:30 | 75 | 75
2018-03-24 15:00 | 75 | 75
2018-03-24 15:30 | 76 | 75
2018-03-24 16:00 | 75 | 74
2018-03-24 16:30 | 76 | 75
2018-03-24 17:00 | 76 | 76
2018-03-24 17:30 | 77 | 76
2018-03-24 18:00 | 76 | 75
2018-03-24 18:30 | 77 | 76
2018-03-24 19:00 | 76 | 75
2018-03-24 19:30 | 76 | 76
2018-03-24 20:00 | 75 | 75
2018-03-24 20:30 | 75 | 74
2018-03-24 21:00 | 74 | 73
2018-03-24 21:30 | 74 | 73
2018-03-24 22:00 | 73 | 72
2018-03-24 22:30 | 72 | 71
2018-03-24 23:00 | 72 | 70
2018-03-24 23:30 | 71 | 69
2018-03-25 | 72 | 69
2018-03-25 00:30 | 71 | 69
2018-03-25 01:00 | 71 | 68
2018-03-25 01:30 | 71 | 68
2018-03-25 02:00 | 71 | 69
2018-03-25 02:30 | 68 | 68
2018-03-25 03:00 | 69 | 68
2018-03-25 03:30 | 68 | 68
2018-03-25 04:00 | 68 | 68
2018-03-25 04:30 | 68 | 68
2018-03-25 05:00 | 68 | 68
2018-03-25 05:30 | 68 | 68
2018-03-25 06:00 | 68 | 68
2018-03-25 06:30 | 68 | 68
2018-03-25 07:00 | 69 | 69
2018-03-25 07:30 | 70 | 69
2018-03-25 08:00 | 70 | 70
2018-03-25 08:30 | 71 | 71
2018-03-25 09:00 | 71 | 70
2018-03-25 09:30 | 70 | 69
2018-03-25 10:00 | 70 | 69
2018-03-25 10:30 | 71 | 70
2018-03-25 11:00 | 71 | 70
2018-03-25 11:30 | 72 | 71
2018-03-25 12:00 | 73 | 73
2018-03-25 12:30 | 74 | 74
2018-03-25 13:00 | 74 | 73
2018-03-25 13:30 | 73 | 72
2018-03-25 14:00 | 72 | 71
2018-03-25 14:30 | 73 | 72
2018-03-25 15:00 | 72 | 71
2018-03-25 15:30 | 74 | 73
2018-03-25 16:00 | 75 | 74
2018-03-25 16:30 | 73 | 72
2018-03-25 17:00 | 73 | 72
2018-03-25 17:30 | 74 | 73
2018-03-25 18:00 | 75 | 74
2018-03-25 18:30 | 75 | 74
2018-03-25 19:00 | 76 | 75
2018-03-25 19:30 | 76 | 75
2018-03-25 20:00 | 75 | 75
2018-03-25 20:30 | 75 | 74
2018-03-25 21:00 | 74 | 74
2018-03-25 21:30 | 73 | 72
2018-03-25 22:00 | 72 | 71
2018-03-25 22:30 | 71 | 70
2018-03-25 23:00 | 71 | 69
2018-03-25 23:30 | 70 | 68
2018-03-26 | 70 | 68
2018-03-26 00:30 | 70 | 68
2018-03-26 01:00 | 70 | 67
2018-03-26 01:30 | 69 | 67
2018-03-26 02:00 | 69 | 67
2018-03-26 02:30 | 70 | 67
2018-03-26 03:00 | 70 | 67
2018-03-26 03:30 | 69 | 66
2018-03-26 04:00 | 70 | 67
2018-03-26 04:30 | 69 | 67
2018-03-26 05:00 | 69 | 66
2018-03-26 05:30 | 69 | 66
2018-03-26 06:00 | 69 | 67
2018-03-26 06:30 | 69 | 67
2018-03-26 07:00 | 70 | 68
2018-03-26 07:30 | 71 | 71
2018-03-26 08:00 | 72 | 72
2018-03-26 08:30 | 73 | 72
2018-03-26 09:00 | 72 | 71
2018-03-26 09:30 | 72 | 72
2018-03-26 10:00 | 73 | 72
2018-03-26 10:30 | 72 | 71
2018-03-26 11:00 | 73 | 72
2018-03-26 11:30 | 74 | 73
2018-03-26 12:00 | 73 | 72
2018-03-26 12:30 | 74 | 73
2018-03-26 13:00 | 73 | 72
2018-03-26 13:30 | 73 | 72
2018-03-26 14:00 | 72 | 71
2018-03-26 14:30 | 71 | 70
2018-03-26 15:00 | 70 | 69
2018-03-26 15:30 | 68 | 67
2018-03-26 16:00 | 68 | 67
2018-03-26 16:30 | 68 | 66
2018-03-26 17:00 | 68 | 67
2018-03-26 17:30 | 69 | 67
2018-03-26 18:00 | 69 | 67
2018-03-26 18:30 | 71 | 68
2018-03-26 19:00 | 70 | 68
2018-03-26 19:30 | 71 | 69
2018-03-26 20:00 | 70 | 68
2018-03-26 20:30 | 70 | 67
2018-03-26 21:00 | 69 | 66
2018-03-26 21:30 | 68 | 66
2018-03-26 22:00 | 68 | 65
2018-03-26 22:30 | 67 | 64
2018-03-26 23:00 | 66 | 63
2018-03-26 23:30 | 65 | 62
2018-03-27 | 65 | 62
2018-03-27 00:30 | 65 | 62
2018-03-27 01:00 | 66 | 63
2018-03-27 01:30 | 65 | 62
2018-03-27 02:00 | 61 | 61
2018-03-27 02:30 | 61 | 61
2018-03-27 03:00 | 61 | 61
2018-03-27 03:30 | 61 | 61
2018-03-27 04:00 | 60 | 60
2018-03-27 04:30 | 60 | 60
2018-03-27 05:00 | 61 | 61
2018-03-27 05:30 | 62 | 62
2018-03-27 06:00 | 62 | 62
2018-03-27 06:30 | 63 | 63
2018-03-27 07:00 | 65 | 64
2018-03-27 07:30 | 67 | 66
2018-03-27 08:00 | 67 | 66
2018-03-27 08:30 | 67 | 67
2018-03-27 09:00 | 68 | 67
2018-03-27 09:30 | 66 | 65
2018-03-27 10:00 | 66 | 65
2018-03-27 10:30 | 66 | 65
2018-03-27 11:00 | 66 | 65
2018-03-27 11:30 | 66 | 65
2018-03-27 12:00 | 55 | 54
2018-03-27 12:30 | 25 | 24
2018-03-27 13:00 | 15 | 15
2018-03-27 13:30 | 16 | 15
2018-03-27 14:00 | 61 | 60
2018-03-27 14:30 | 69 | 68
2018-03-27 15:00 | 70 | 69
2018-03-27 15:30 | 69 | 68
2018-03-27 16:00 | 70 | 69
2018-03-27 16:30 | 70 | 69
2018-03-27 17:00 | 71 | 70
2018-03-27 17:30 | 72 | 71
2018-03-27 18:00 | 72 | 71
2018-03-27 18:30 | 72 | 70
2018-03-27 19:00 | 72 | 71
2018-03-27 19:30 | 73 | 72
2018-03-27 20:00 | 73 | 72
2018-03-27 20:30 | 73 | 72
2018-03-27 21:00 | 72 | 71
2018-03-27 21:30 | 72 | 70
2018-03-27 22:00 | 71 | 69
2018-03-27 22:30 | 70 | 68
2018-03-27 23:00 | 68 | 66
2018-03-27 23:30 | 69 | 67
2018-03-28 | 66 | 66
2018-03-28 00:30 | 64 | 64
2018-03-28 01:00 | 62 | 62
2018-03-28 01:30 | 62 | 61
2018-03-28 02:00 | 61 | 61
2018-03-28 02:30 | 62 | 61
2018-03-28 03:00 | 61 | 61
2018-03-28 03:30 | 61 | 61
2018-03-28 04:00 | 61 | 61
2018-03-28 04:30 | 62 | 62
2018-03-28 05:00 | 64 | 64
2018-03-28 05:30 | 64 | 64
2018-03-28 06:00 | 64 | 64
2018-03-28 06:30 | 66 | 66
2018-03-28 07:00 | 66 | 66
2018-03-28 07:30 | 68 | 67
2018-03-28 08:00 | 69 | 68
2018-03-28 08:30 | 68 | 67
2018-03-28 09:00 | 48 | 45
2018-03-28 09:30 | 24 | 15
2018-03-28 10:00 | 24 | 17
2018-03-28 10:30 | 27 | 27
2018-03-28 11:00 | 40 | 40
2018-03-28 11:30 | 48 | 48
2018-03-28 12:00 | 56 | 56
2018-03-28 12:30 | 61 | 61
2018-03-28 13:00 | 64 | 64
2018-03-28 13:30 | 71 | 71
2018-03-28 14:00 | 73 | 72
2018-03-28 14:30 | 74 | 73
2018-03-28 15:00 | 76 | 74
2018-03-28 15:30 | 73 | 72
2018-03-28 16:00 | 72 | 71
2018-03-28 16:30 | 71 | 71
2018-03-28 17:00 | 72 | 72
2018-03-28 17:30 | 72 | 71
2018-03-28 18:00 | 71 | 70
2018-03-28 18:30 | 72 | 71
2018-03-28 19:00 | 74 | 73
2018-03-28 19:30 | 74 | 74
2018-03-28 20:00 | 73 | 73
2018-03-28 20:30 | 73 | 72
2018-03-28 21:00 | 72 | 71
2018-03-28 21:30 | 72 | 71
2018-03-28 22:00 | 72 | 71
2018-03-28 22:30 | 70 | 69
2018-03-28 23:00 | 68 | 67
2018-03-28 23:30 | 68 | 67
2018-03-29 | 67 | 66
2018-03-29 00:30 | 65 | 65
2018-03-29 01:00 | 65 | 65
2018-03-29 01:30 | 64 | 64
2018-03-29 02:00 | 63 | 63
2018-03-29 02:30 | 64 | 64
2018-03-29 03:00 | 62 | 62
2018-03-29 03:30 | 62 | 62
2018-03-29 04:00 | 63 | 63
2018-03-29 04:30 | 63 | 63
2018-03-29 05:00 | 64 | 64
2018-03-29 05:30 | 64 | 64
2018-03-29 06:00 | 63 | 63
2018-03-29 06:30 | 63 | 63
2018-03-29 07:00 | 64 | 64
2018-03-29 07:30 | 65 | 65
2018-03-29 08:00 | 67 | 67
2018-03-29 08:30 | 69 | 68
2018-03-29 09:00 | 68 | 67
2018-03-29 09:30 | 69 | 69
2018-03-29 10:00 | 69 | 69
2018-03-29 10:30 | 70 | 70
2018-03-29 11:00 | 69 | 69
2018-03-29 11:30 | 70 | 69
2018-03-29 12:00 | 72 | 70
2018-03-29 12:30 | 66 | 64
2018-03-29 13:00 | 43 | 42
2018-03-29 13:30 | 29 | 29
2018-03-29 14:00 | 24 | 23
2018-03-29 14:30 | 26 | 26
2018-03-29 15:00 | 36 | 36
2018-03-29 15:30 | 49 | 49
2018-03-29 16:00 | 57 | 57
2018-03-29 16:30 | 71 | 71
2018-03-29 17:00 | 76 | 76
2018-03-29 17:30 | 78 | 76
2018-03-29 18:00 | 77 | 75
2018-03-29 18:30 | 76 | 74
2018-03-29 19:00 | 77 | 75
2018-03-29 19:30 | 77 | 75
2018-03-29 20:00 | 77 | 75
2018-03-29 20:30 | 75 | 74
2018-03-29 21:00 | 75 | 73
2018-03-29 21:30 | 74 | 72
2018-03-29 22:00 | 73 | 71
2018-03-29 22:30 | 73 | 71
2018-03-29 23:00 | 75 | 73
2018-03-29 23:30 | 71 | 69
2018-03-30 | 71 | 69
2018-03-30 00:30 | 71 | 68
2018-03-30 01:00 | 70 | 68
2018-03-30 01:30 | 70 | 67
2018-03-30 02:00 | 70 | 67
2018-03-30 02:30 | 67 | 65
2018-03-30 03:00 | 65 | 65
2018-03-30 03:30 | 65 | 65
2018-03-30 04:00 | 66 | 66
2018-03-30 04:30 | 65 | 65
2018-03-30 05:00 | 65 | 65
2018-03-30 05:30 | 66 | 66
2018-03-30 06:00 | 65 | 65
2018-03-30 06:30 | 65 | 65
2018-03-30 07:00 | 65 | 65
2018-03-30 07:30 | 66 | 66
2018-03-30 08:00 | 67 | 67
2018-03-30 08:30 | 67 | 67
2018-03-30 09:00 | 67 | 67
2018-03-30 09:30 | 66 | 66
2018-03-30 10:00 | 67 | 67
2018-03-30 10:30 | 67 | 67
2018-03-30 11:00 | 69 | 69
2018-03-30 11:30 | 70 | 70
2018-03-30 12:00 | 70 | 70
2018-03-30 12:30 | 70 | 70
2018-03-30 13:00 | 70 | 70
2018-03-30 13:30 | 71 | 71
2018-03-30 14:00 | 71 | 71
2018-03-30 14:30 | 72 | 72
2018-03-30 15:00 | 73 | 73
2018-03-30 15:30 | 74 | 74
2018-03-30 16:00 | 76 | 75
2018-03-30 16:30 | 77 | 77
2018-03-30 17:00 | 77 | 76
2018-03-30 17:30 | 77 | 77
2018-03-30 18:00 | 76 | 76
2018-03-30 18:30 | 76 | 75
2018-03-30 19:00 | 76 | 76
2018-03-30 19:30 | 77 | 77
2018-03-30 20:00 | 77 | 76
2018-03-30 20:30 | 75 | 75
2018-03-30 21:00 | 74 | 74
2018-03-30 21:30 | 74 | 73
2018-03-30 22:00 | 73 | 73
2018-03-30 22:30 | 72 | 72
2018-03-30 23:00 | 71 | 71
2018-03-30 23:30 | 70 | 70
2018-03-31 | 69 | 69
2018-03-31 00:30 | 68 | 68
2018-03-31 01:00 | 67 | 67
2018-03-31 01:30 | 67 | 67
2018-03-31 02:00 | 67 | 67
2018-03-31 02:30 | 67 | 66
2018-03-31 03:00 | 66 | 66
2018-03-31 03:30 | 66 | 65
2018-03-31 04:00 | 66 | 66
2018-03-31 04:30 | 66 | 66
2018-03-31 05:00 | 67 | 66
2018-03-31 05:30 | 66 | 66
2018-03-31 06:00 | 66 | 65
2018-03-31 06:30 | 66 | 65
2018-03-31 07:00 | 66 | 66
2018-03-31 07:30 | 67 | 67
2018-03-31 08:00 | 69 | 68
2018-03-31 08:30 | 69 | 69
2018-03-31 09:00 | 69 | 68
2018-03-31 09:30 | 69 | 69
2018-03-31 10:00 | 71 | 70
2018-03-31 10:30 | 72 | 70
2018-03-31 11:00 | 72 | 70
2018-03-31 11:30 | 71 | 70
2018-03-31 12:00 | 72 | 71
2018-03-31 12:30 | 72 | 71
2018-03-31 13:00 | 74 | 73
2018-03-31 13:30 | 74 | 72
2018-03-31 14:00 | 73 | 72
2018-03-31 14:30 | 73 | 72
2018-03-31 15:00 | 72 | 71
2018-03-31 15:30 | 72 | 71
2018-03-31 16:00 | 73 | 72
2018-03-31 16:30 | 74 | 73
2018-03-31 17:00 | 74 | 73
2018-03-31 17:30 | 75 | 75
2018-03-31 18:00 | 76 | 75
2018-03-31 18:30 | 75 | 75
2018-03-31 19:00 | 77 | 76
2018-03-31 19:30 | 77 | 76
2018-03-31 20:00 | 77 | 76
2018-03-31 20:30 | 76 | 75
2018-03-31 21:00 | 76 | 76
2018-03-31 21:30 | 75 | 74
2018-03-31 22:00 | 75 | 74
2018-03-31 22:30 | 73 | 72
2018-03-31 23:00 | 73 | 72
2018-03-31 23:30 | 72 | 70
2018-04-01 | 72 | 70
2018-04-01 00:30 | 72 | 70
2018-04-01 01:00 | 70 | 68
2018-04-01 01:30 | 71 | 68
2018-04-01 02:00 | 70 | 68
2018-04-01 02:30 | 70 | 68
2018-04-01 03:00 | 70 | 68
2018-04-01 03:30 | 66 | 66
2018-04-01 04:00 | 65 | 65
2018-04-01 04:30 | 66 | 66
2018-04-01 05:00 | 66 | 65
2018-04-01 05:30 | 67 | 67
2018-04-01 06:00 | 65 | 65
2018-04-01 06:30 | 66 | 66
2018-04-01 07:00 | 66 | 66
2018-04-01 07:30 | 67 | 67
2018-04-01 08:00 | 69 | 68
2018-04-01 08:30 | 69 | 69
2018-04-01 09:00 | 68 | 68
2018-04-01 09:30 | 69 | 68
2018-04-01 10:00 | 70 | 69
2018-04-01 10:30 | 69 | 69
2018-04-01 11:00 | 69 | 69
2018-04-01 11:30 | 70 | 70
2018-04-01 12:00 | 69 | 69
2018-04-01 12:30 | 69 | 68
2018-04-01 13:00 | 69 | 69
2018-04-01 13:30 | 68 | 67
2018-04-01 14:00 | 67 | 67
2018-04-01 14:30 | 68 | 68
2018-04-01 15:00 | 70 | 70
2018-04-01 15:30 | 69 | 69
2018-04-01 16:00 | 69 | 69
2018-04-01 16:30 | 70 | 70
2018-04-01 17:00 | 71 | 71
2018-04-01 17:30 | 71 | 71
2018-04-01 18:00 | 71 | 71
2018-04-01 18:30 | 70 | 70
2018-04-01 19:00 | 71 | 70
2018-04-01 19:30 | 71 | 71
2018-04-01 20:00 | 69 | 69
2018-04-01 20:30 | 69 | 69
2018-04-01 21:00 | 68 | 68
2018-04-01 21:30 | 69 | 69
2018-04-01 22:00 | 69 | 69
2018-04-01 22:30 | 69 | 68
2018-04-01 23:00 | 69 | 69
2018-04-01 23:30 | 68 | 67
2018-04-02 | 67 | 66
2018-04-02 00:30 | 66 | 66
2018-04-02 01:00 | 66 | 66
2018-04-02 01:30 | 66 | 65
2018-04-02 02:00 | 65 | 65
2018-04-02 02:30 | 65 | 65
2018-04-02 03:00 | 65 | 65
2018-04-02 03:30 | 65 | 65
2018-04-02 04:00 | 65 | 65
2018-04-02 04:30 | 65 | 65
2018-04-02 05:00 | 65 | 65
2018-04-02 05:30 | 65 | 65
2018-04-02 06:00 | 64 | 64
2018-04-02 06:30 | 64 | 64
2018-04-02 07:00 | 64 | 64
2018-04-02 07:30 | 65 | 65
2018-04-02 08:00 | 66 | 66
2018-04-02 08:30 | 67 | 67
2018-04-02 09:00 | 70 | 69
2018-04-02 09:30 | 70 | 69
2018-04-02 10:00 | 71 | 69
2018-04-02 10:30 | 69 | 67
2018-04-02 11:00 | 68 | 67
2018-04-02 11:30 | 70 | 68
2018-04-02 12:00 | 71 | 69
2018-04-02 12:30 | 71 | 69
2018-04-02 13:00 | 71 | 69
2018-04-02 13:30 | 71 | 70
2018-04-02 14:00 | 71 | 70
2018-04-02 14:30 | 72 | 70
2018-04-02 15:00 | 71 | 69
2018-04-02 15:30 | 70 | 68
2018-04-02 16:00 | 71 | 70
2018-04-02 16:30 | 70 | 69
2018-04-02 17:00 | 71 | 69
2018-04-02 17:30 | 70 | 69
2018-04-02 18:00 | 70 | 68
2018-04-02 18:30 | 70 | 68
2018-04-02 19:00 | 71 | 69
2018-04-02 19:30 | 71 | 70
2018-04-02 20:00 | 71 | 69
2018-04-02 20:30 | 71 | 69
2018-04-02 21:00 | 71 | 69
2018-04-02 21:30 | 69 | 67
2018-04-02 22:00 | 69 | 67
2018-04-02 22:30 | 69 | 67
2018-04-02 23:00 | 68 | 65
2018-04-02 23:30 | 68 | 65
2018-04-03 | 68 | 65
2018-04-03 00:30 | 68 | 65
2018-04-03 01:00 | 65 | 64
2018-04-03 01:30 | 64 | 64
2018-04-03 02:00 | 64 | 64
2018-04-03 02:30 | 64 | 64
2018-04-03 03:00 | 63 | 63
2018-04-03 03:30 | 63 | 63
2018-04-03 04:00 | 63 | 63
2018-04-03 04:30 | 62 | 62
2018-04-03 05:00 | 62 | 62
2018-04-03 05:30 | 62 | 62
2018-04-03 06:00 | 63 | 63
2018-04-03 06:30 | 66 | 66
2018-04-03 07:00 | 66 | 66
2018-04-03 07:30 | 69 | 68
2018-04-03 08:00 | 71 | 69
2018-04-03 08:30 | 73 | 70
2018-04-03 09:00 | 72 | 69
2018-04-03 09:30 | 72 | 69
2018-04-03 10:00 | 72 | 70
2018-04-03 10:30 | 73 | 70
2018-04-03 11:00 | 72 | 70
2018-04-03 11:30 | 72 | 69
2018-04-03 12:00 | 72 | 69
2018-04-03 12:30 | 71 | 68
2018-04-03 13:00 | 71 | 69
2018-04-03 13:30 | 73 | 71
2018-04-03 14:00 | 73 | 71
2018-04-03 14:30 | 73 | 71
2018-04-03 15:00 | 73 | 70
2018-04-03 15:30 | 72 | 70
2018-04-03 16:00 | 72 | 69
2018-04-03 16:30 | 72 | 69
2018-04-03 17:00 | 73 | 70
2018-04-03 17:30 | 72 | 69
2018-04-03 18:00 | 72 | 70
2018-04-03 18:30 | 73 | 70
2018-04-03 19:00 | 73 | 70
2018-04-03 19:30 | 72 | 69
2018-04-03 20:00 | 72 | 69
2018-04-03 20:30 | 71 | 68
2018-04-03 21:00 | 72 | 68
2018-04-03 21:30 | 71 | 67
2018-04-03 22:00 | 72 | 67
2018-04-03 22:30 | 67 | 66
2018-04-03 23:00 | 66 | 66
2018-04-03 23:30 | 65 | 65
2018-04-04 | 64 | 64
2018-04-04 00:30 | 64 | 64
2018-04-04 01:00 | 64 | 64
2018-04-04 01:30 | 64 | 64
2018-04-04 02:00 | 64 | 64
2018-04-04 02:30 | 64 | 63
2018-04-04 03:00 | 64 | 64
2018-04-04 03:30 | 64 | 63
2018-04-04 04:00 | 63 | 63
2018-04-04 04:30 | 63 | 63
2018-04-04 05:00 | 62 | 62
2018-04-04 05:30 | 63 | 63
2018-04-04 06:00 | 64 | 64
2018-04-04 06:30 | 64 | 64
2018-04-04 07:00 | 65 | 65
2018-04-04 07:30 | 67 | 67
2018-04-04 08:00 | 68 | 68
2018-04-04 08:30 | 68 | 68
2018-04-04 09:00 | 69 | 68
2018-04-04 09:30 | 69 | 69
2018-04-04 10:00 | 69 | 69
2018-04-04 10:30 | 69 | 68
2018-04-04 11:00 | 70 | 70
2018-04-04 11:30 | 70 | 69
2018-04-04 12:00 | 70 | 70
2018-04-04 12:30 | 69 | 69
2018-04-04 13:00 | 70 | 70
2018-04-04 13:30 | 70 | 69
2018-04-04 14:00 | 69 | 68
2018-04-04 14:30 | 68 | 67
2018-04-04 15:00 | 67 | 67
2018-04-04 15:30 | 68 | 67
2018-04-04 16:00 | 69 | 68
2018-04-04 16:30 | 68 | 67
2018-04-04 17:00 | 70 | 70
2018-04-04 17:30 | 70 | 70
2018-04-04 18:00 | 69 | 69
2018-04-04 18:30 | 70 | 70
2018-04-04 19:00 | 71 | 71
2018-04-04 19:30 | 70 | 70
2018-04-04 20:00 | 70 | 70
2018-04-04 20:30 | 70 | 70
2018-04-04 21:00 | 69 | 69
2018-04-04 21:30 | 68 | 68
2018-04-04 22:00 | 68 | 68
2018-04-04 22:30 | 68 | 68
2018-04-04 23:00 | 65 | 65
2018-04-04 23:30 | 65 | 64
2018-04-05 | 64 | 64
2018-04-05 00:30 | 64 | 63
2018-04-05 01:00 | 64 | 64
2018-04-05 01:30 | 63 | 63
2018-04-05 02:00 | 62 | 62
2018-04-05 02:30 | 62 | 62
2018-04-05 03:00 | 62 | 62
2018-04-05 03:30 | 62 | 62
2018-04-05 04:00 | 62 | 62
2018-04-05 04:30 | 62 | 62
2018-04-05 05:00 | 62 | 62
2018-04-05 05:30 | 63 | 63
2018-04-05 06:00 | 61 | 61
2018-04-05 06:30 | 63 | 62
2018-04-05 07:00 | 64 | 64
2018-04-05 07:30 | 65 | 65
2018-04-05 08:00 | 66 | 66
2018-04-05 08:30 | 65 | 64
2018-04-05 09:00 | 65 | 64
2018-04-05 09:30 | 64 | 63
2018-04-05 10:00 | 64 | 63
2018-04-05 10:30 | 64 | 63
2018-04-05 11:00 | 65 | 64
2018-04-05 11:30 | 66 | 65
2018-04-05 12:00 | 66 | 66
2018-04-05 12:30 | 68 | 68
2018-04-05 13:00 | 69 | 69
2018-04-05 13:30 | 69 | 69
2018-04-05 14:00 | 69 | 69
2018-04-05 14:30 | 69 | 69
2018-04-05 15:00 | 69 | 69
2018-04-05 15:30 | 69 | 69
2018-04-05 16:00 | 70 | 70
2018-04-05 16:30 | 70 | 70
2018-04-05 17:00 | 72 | 72
2018-04-05 17:30 | 71 | 71
2018-04-05 18:00 | 72 | 71
2018-04-05 18:30 | 72 | 71
2018-04-05 19:00 | 72 | 72
2018-04-05 19:30 | 73 | 73
2018-04-05 20:00 | 73 | 72
2018-04-05 20:30 | 72 | 72
2018-04-05 21:00 | 72 | 72
2018-04-05 21:30 | 70 | 70
2018-04-05 22:00 | 70 | 70
2018-04-05 22:30 | 68 | 68
2018-04-05 23:00 | 67 | 67
2018-04-05 23:30 | 64 | 64
2018-04-06 | 63 | 63
2018-04-06 00:30 | 66 | 66
2018-04-06 01:00 | 64 | 63
2018-04-06 01:30 | 64 | 63
2018-04-06 02:00 | 62 | 62
2018-04-06 02:30 | 63 | 62
2018-04-06 03:00 | 64 | 64
2018-04-06 03:30 | 64 | 64
2018-04-06 04:00 | 63 | 63
2018-04-06 04:30 | 62 | 62
2018-04-06 05:00 | 63 | 63
2018-04-06 05:30 | 64 | 64
2018-04-06 06:00 | 65 | 64
2018-04-06 06:30 | 65 | 64
2018-04-06 07:00 | 66 | 65
2018-04-06 07:30 | 67 | 66
2018-04-06 08:00 | 68 | 67
2018-04-06 08:30 | 69 | 68
2018-04-06 09:00 | 67 | 67
2018-04-06 09:30 | 68 | 67
2018-04-06 10:00 | 68 | 67
2018-04-06 10:30 | 68 | 67
2018-04-06 11:00 | 69 | 68
2018-04-06 11:30 | 71 | 69
2018-04-06 12:00 | 69 | 68
2018-04-06 12:30 | 70 | 68
2018-04-06 13:00 | 71 | 70
2018-04-06 13:30 | 71 | 70
2018-04-06 14:00 | 70 | 68
2018-04-06 14:30 | 71 | 70
2018-04-06 15:00 | 74 | 73
2018-04-06 15:30 | 73 | 72
2018-04-06 16:00 | 62 | 58
2018-04-06 16:30 | 70 | 69
2018-04-06 17:00 | 71 | 70
2018-04-06 17:30 | 71 | 70
2018-04-06 18:00 | 71 | 70
2018-04-06 18:30 | 72 | 71
2018-04-06 19:00 | 72 | 71
2018-04-06 19:30 | 73 | 72
2018-04-06 20:00 | 72 | 70
2018-04-06 20:30 | 72 | 71
2018-04-06 21:00 | 71 | 70
2018-04-06 21:30 | 71 | 70
2018-04-06 22:00 | 72 | 71
2018-04-06 22:30 | 71 | 69
2018-04-06 23:00 | 71 | 69
2018-04-06 23:30 | 70 | 68
2018-04-07 | 69 | 67
2018-04-07 00:30 | 70 | 67
2018-04-07 01:00 | 69 | 67
2018-04-07 01:30 | 68 | 66
2018-04-07 02:00 | 68 | 65
2018-04-07 02:30 | 68 | 65
2018-04-07 03:00 | 68 | 65
2018-04-07 03:30 | 68 | 65
2018-04-07 04:00 | 68 | 65
2018-04-07 04:30 | 67 | 64
2018-04-07 05:00 | 67 | 65
2018-04-07 05:30 | 67 | 65
2018-04-07 06:00 | 67 | 64
2018-04-07 06:30 | 67 | 64
2018-04-07 07:00 | 68 | 65
2018-04-07 07:30 | 68 | 65
2018-04-07 08:00 | 69 | 67
2018-04-07 08:30 | 68 | 67
2018-04-07 09:00 | 68 | 67
2018-04-07 09:30 | 67 | 66
2018-04-07 10:00 | 66 | 65
2018-04-07 10:30 | 68 | 67
2018-04-07 11:00 | 67 | 65
2018-04-07 11:30 | 68 | 66
2018-04-07 12:00 | 69 | 67
2018-04-07 12:30 | 69 | 68
2018-04-07 13:00 | 70 | 68
2018-04-07 13:30 | 70 | 69
2018-04-07 14:00 | 71 | 69
2018-04-07 14:30 | 70 | 69
2018-04-07 15:00 | 71 | 70
2018-04-07 15:30 | 72 | 71
2018-04-07 16:00 | 73 | 72
2018-04-07 16:30 | 73 | 72
2018-04-07 17:00 | 74 | 73
2018-04-07 17:30 | 73 | 72
2018-04-07 18:00 | 73 | 72
2018-04-07 18:30 | 74 | 73
2018-04-07 19:00 | 74 | 73
2018-04-07 19:30 | 74 | 73
2018-04-07 20:00 | 74 | 73
2018-04-07 20:30 | 73 | 72
2018-04-07 21:00 | 73 | 71
2018-04-07 21:30 | 72 | 71
2018-04-07 22:00 | 72 | 71
2018-04-07 22:30 | 71 | 70
2018-04-07 23:00 | 71 | 70
2018-04-07 23:30 | 70 | 69
2018-04-08 | 70 | 69
2018-04-08 00:30 | 70 | 68
2018-04-08 01:00 | 69 | 67
2018-04-08 01:30 | 66 | 65
2018-04-08 02:00 | 66 | 65
2018-04-08 02:30 | 65 | 65
2018-04-08 03:00 | 64 | 64
2018-04-08 03:30 | 65 | 64
2018-04-08 04:00 | 65 | 65
2018-04-08 04:30 | 65 | 65
2018-04-08 05:00 | 65 | 65
2018-04-08 05:30 | 64 | 64
2018-04-08 06:00 | 64 | 64
2018-04-08 06:30 | 65 | 65
2018-04-08 07:00 | 65 | 65
2018-04-08 07:30 | 66 | 66
2018-04-08 08:00 | 67 | 66
2018-04-08 08:30 | 66 | 66
2018-04-08 09:00 | 67 | 66
2018-04-08 09:30 | 66 | 65
2018-04-08 10:00 | 66 | 66
2018-04-08 10:30 | 67 | 66
2018-04-08 11:00 | 65 | 64
2018-04-08 11:30 | 65 | 65
2018-04-08 12:00 | 66 | 66
2018-04-08 12:30 | 67 | 67
2018-04-08 13:00 | 68 | 67
2018-04-08 13:30 | 69 | 69
2018-04-08 14:00 | 70 | 69
2018-04-08 14:30 | 70 | 69
2018-04-08 15:00 | 72 | 71
2018-04-08 15:30 | 73 | 72
2018-04-08 16:00 | 73 | 72
2018-04-08 16:30 | 74 | 73
2018-04-08 17:00 | 74 | 74
2018-04-08 17:30 | 74 | 74
2018-04-08 18:00 | 74 | 73
2018-04-08 18:30 | 75 | 74
2018-04-08 19:00 | 76 | 76
2018-04-08 19:30 | 76 | 76
2018-04-08 20:00 | 75 | 74
2018-04-08 20:30 | 75 | 74
2018-04-08 21:00 | 74 | 74
2018-04-08 21:30 | 74 | 73
2018-04-08 22:00 | 73 | 72
2018-04-08 22:30 | 71 | 70
2018-04-08 23:00 | 70 | 69
2018-04-08 23:30 | 70 | 69
2018-04-09 | 69 | 68
2018-04-09 00:30 | 68 | 67
2018-04-09 01:00 | 69 | 67
2018-04-09 01:30 | 68 | 66
2018-04-09 02:00 | 68 | 66
2018-04-09 02:30 | 68 | 66
2018-04-09 03:00 | 68 | 66
2018-04-09 03:30 | 68 | 66
2018-04-09 04:00 | 67 | 65
2018-04-09 04:30 | 66 | 65
2018-04-09 05:00 | 66 | 65
2018-04-09 05:30 | 66 | 65
2018-04-09 06:00 | 65 | 65
2018-04-09 06:30 | 66 | 66
2018-04-09 07:00 | 68 | 68
2018-04-09 07:30 | 69 | 69
2018-04-09 08:00 | 70 | 70
2018-04-09 08:30 | 69 | 69
2018-04-09 09:00 | 70 | 70
2018-04-09 09:30 | 71 | 71
2018-04-09 10:00 | 72 | 71
2018-04-09 10:30 | 71 | 70
2018-04-09 11:00 | 70 | 70
2018-04-09 11:30 | 71 | 71
2018-04-09 12:00 | 73 | 72
2018-04-09 12:30 | 72 | 72
2018-04-09 13:00 | 73 | 72
2018-04-09 13:30 | 74 | 73
2018-04-09 14:00 | 75 | 74
2018-04-09 14:30 | 74 | 74
2018-04-09 15:00 | 76 | 75
2018-04-09 15:30 | 75 | 75
2018-04-09 16:00 | 76 | 76
2018-04-09 16:30 | 77 | 76
2018-04-09 17:00 | 77 | 76
2018-04-09 17:30 | 77 | 77
2018-04-09 18:00 | 77 | 76
2018-04-09 18:30 | 77 | 77
2018-04-09 19:00 | 79 | 78
2018-04-09 19:30 | 78 | 78
2018-04-09 20:00 | 78 | 77
2018-04-09 20:30 | 77 | 76
2018-04-09 21:00 | 75 | 75
2018-04-09 21:30 | 74 | 74
2018-04-09 22:00 | 73 | 73
2018-04-09 22:30 | 71 | 71
2018-04-09 23:00 | 70 | 70
2018-04-09 23:30 | 69 | 69
2018-04-10 | 69 | 69
2018-04-10 00:30 | 68 | 68
2018-04-10 01:00 | 68 | 67
2018-04-10 01:30 | 70 | 67
2018-04-10 02:00 | 70 | 67
2018-04-10 02:30 | 69 | 66
2018-04-10 03:00 | 69 | 66
2018-04-10 03:30 | 68 | 65
2018-04-10 04:00 | 69 | 66
2018-04-10 04:30 | 69 | 66
2018-04-10 05:00 | 69 | 66
2018-04-10 05:30 | 69 | 66
2018-04-10 06:00 | 70 | 67
2018-04-10 06:30 | 71 | 67
2018-04-10 07:00 | 72 | 68
2018-04-10 07:30 | 69 | 69
2018-04-10 08:00 | 70 | 70
2018-04-10 08:30 | 70 | 70
2018-04-10 09:00 | 69 | 69
2018-04-10 09:30 | 68 | 68
2018-04-10 10:00 | 66 | 66
2018-04-10 10:30 | 67 | 67
2018-04-10 11:00 | 67 | 67
2018-04-10 11:30 | 67 | 67
2018-04-10 12:00 | 69 | 67
2018-04-10 12:30 | 69 | 67
2018-04-10 13:00 | 69 | 68
2018-04-10 13:30 | 69 | 68
2018-04-10 14:00 | 70 | 69
2018-04-10 14:30 | 73 | 72
2018-04-10 15:00 | 74 | 73
2018-04-10 15:30 | 74 | 73
2018-04-10 16:00 | 75 | 74
2018-04-10 16:30 | 74 | 73
2018-04-10 17:00 | 75 | 74
2018-04-10 17:30 | 76 | 75
2018-04-10 18:00 | 77 | 76
2018-04-10 18:30 | 78 | 77
2018-04-10 19:00 | 80 | 79
2018-04-10 19:30 | 78 | 77
2018-04-10 20:00 | 78 | 77
2018-04-10 20:30 | 77 | 76
2018-04-10 21:00 | 76 | 75
2018-04-10 21:30 | 74 | 73
2018-04-10 22:00 | 74 | 73
2018-04-10 22:30 | 71 | 70
2018-04-10 23:00 | 72 | 70
2018-04-10 23:30 | 70 | 69
2018-04-11 | 69 | 68
2018-04-11 00:30 | 69 | 67
2018-04-11 01:00 | 68 | 66
2018-04-11 01:30 | 66 | 66
2018-04-11 02:00 | 66 | 66
2018-04-11 02:30 | 66 | 66
2018-04-11 03:00 | 66 | 66
2018-04-11 03:30 | 64 | 64
2018-04-11 04:00 | 65 | 65
2018-04-11 04:30 | 65 | 65
2018-04-11 05:00 | 66 | 66
2018-04-11 05:30 | 67 | 66
2018-04-11 06:00 | 67 | 66
2018-04-11 06:30 | 67 | 67
2018-04-11 07:00 | 67 | 67
2018-04-11 07:30 | 67 | 66
2018-04-11 08:00 | 69 | 67
2018-04-11 08:30 | 72 | 70
2018-04-11 09:00 | 72 | 71
2018-04-11 09:30 | 71 | 70
2018-04-11 10:00 | 72 | 70
2018-04-11 10:30 | 71 | 70
2018-04-11 11:00 | 71 | 70
2018-04-11 11:30 | 70 | 69
2018-04-11 12:00 | 71 | 70
2018-04-11 12:30 | 71 | 70
2018-04-11 13:00 | 72 | 71
2018-04-11 13:30 | 71 | 70
2018-04-11 14:00 | 71 | 71
2018-04-11 14:30 | 72 | 71
2018-04-11 15:00 | 71 | 71
2018-04-11 15:30 | 70 | 70
2018-04-11 16:00 | 71 | 71
2018-04-11 16:30 | 73 | 73
2018-04-11 17:00 | 75 | 75
2018-04-11 17:30 | 75 | 75
2018-04-11 18:00 | 75 | 75
2018-04-11 18:30 | 75 | 75
2018-04-11 19:00 | 77 | 77
2018-04-11 19:30 | 77 | 77
2018-04-11 20:00 | 76 | 76
2018-04-11 20:30 | 75 | 75
2018-04-11 21:00 | 75 | 75
2018-04-11 21:30 | 74 | 74
2018-04-11 22:00 | 73 | 73
2018-04-11 22:30 | 71 | 71
2018-04-11 23:00 | 70 | 70
2018-04-11 23:30 | 69 | 69
2018-04-12 | 68 | 68
2018-04-12 00:30 | 67 | 67
2018-04-12 01:00 | 67 | 67
2018-04-12 01:30 | 67 | 67
2018-04-12 02:00 | 66 | 66
2018-04-12 02:30 | 67 | 66
2018-04-12 03:00 | 66 | 66
2018-04-12 03:30 | 67 | 67
2018-04-12 04:00 | 67 | 66
2018-04-12 04:30 | 67 | 67
2018-04-12 05:00 | 66 | 66
2018-04-12 05:30 | 66 | 66
2018-04-12 06:00 | 67 | 67
2018-04-12 06:30 | 67 | 67
2018-04-12 07:00 | 70 | 69
2018-04-12 07:30 | 71 | 70
2018-04-12 08:00 | 71 | 70
2018-04-12 08:30 | 70 | 69
2018-04-12 09:00 | 72 | 71
2018-04-12 09:30 | 73 | 72
2018-04-12 10:00 | 70 | 69
2018-04-12 10:30 | 70 | 69
2018-04-12 11:00 | 73 | 71
2018-04-12 11:30 | 72 | 71
2018-04-12 12:00 | 71 | 71
2018-04-12 12:30 | 71 | 70
2018-04-12 13:00 | 71 | 70
2018-04-12 13:30 | 71 | 70
2018-04-12 14:00 | 73 | 72
2018-04-12 14:30 | 73 | 73
2018-04-12 15:00 | 72 | 71
2018-04-12 15:30 | 73 | 73
2018-04-12 16:00 | 76 | 75
2018-04-12 16:30 | 77 | 77
2018-04-12 17:00 | 77 | 77
2018-04-12 17:30 | 77 | 77
2018-04-12 18:00 | 78 | 77
2018-04-12 18:30 | 79 | 79
2018-04-12 19:00 | 81 | 81
2018-04-12 19:30 | 81 | 80
2018-04-12 20:00 | 78 | 78
2018-04-12 20:30 | 79 | 78
2018-04-12 21:00 | 79 | 78
2018-04-12 21:30 | 78 | 77
2018-04-12 22:00 | 74 | 73
2018-04-12 22:30 | 71 | 71
2018-04-12 23:00 | 71 | 71
2018-04-12 23:30 | 71 | 71
2018-04-13 | 68 | 68
2018-04-13 00:30 | 67 | 67
2018-04-13 01:00 | 63 | 63
2018-04-13 01:30 | 54 | 53
2018-04-13 02:00 | 54 | 52
2018-04-13 02:30 | 53 | 51
2018-04-13 03:00 | 52 | 51
2018-04-13 03:30 | 51 | 50
2018-04-13 04:00 | 48 | 47
2018-04-13 04:30 | 42 | 40
2018-04-13 05:00 | 40 | 37
2018-04-13 05:30 | 40 | 37
2018-04-13 06:00 | 39 | 37
2018-04-13 06:30 | 39 | 37
2018-04-13 07:00 | 40 | 38
2018-04-13 07:30 | 46 | 45
2018-04-13 08:00 | 56 | 56
2018-04-13 08:30 | 69 | 68
2018-04-13 09:00 | 70 | 69
2018-04-13 09:30 | 70 | 70
2018-04-13 10:00 | 72 | 71
2018-04-13 10:30 | 73 | 72
2018-04-13 11:00 | 73 | 72
2018-04-13 11:30 | 72 | 71
2018-04-13 12:00 | 73 | 72
2018-04-13 12:30 | 70 | 70
2018-04-13 13:00 | 71 | 70
2018-04-13 13:30 | 71 | 70
2018-04-13 14:00 | 72 | 71
2018-04-13 14:30 | 73 | 72
2018-04-13 15:00 | 73 | 73
2018-04-13 15:30 | 77 | 76
2018-04-13 16:00 | 81 | 80
2018-04-13 16:30 | 79 | 78
2018-04-13 17:00 | 80 | 79
2018-04-13 17:30 | 80 | 79
2018-04-13 18:00 | 78 | 77
2018-04-13 18:30 | 79 | 78
2018-04-13 19:00 | 78 | 77
2018-04-13 19:30 | 78 | 77
2018-04-13 20:00 | 78 | 77
2018-04-13 20:30 | 78 | 77
2018-04-13 21:00 | 78 | 76
2018-04-13 21:30 | 77 | 75
2018-04-13 22:00 | 76 | 74
2018-04-13 22:30 | 76 | 74
2018-04-13 23:00 | 73 | 71
2018-04-13 23:30 | 69 | 67
2018-04-14 | 68 | 66
2018-04-14 00:30 | 65 | 65
2018-04-14 01:00 | 65 | 65
2018-04-14 01:30 | 64 | 64
2018-04-14 02:00 | 64 | 64
2018-04-14 02:30 | 64 | 64
2018-04-14 03:00 | 64 | 64
2018-04-14 03:30 | 63 | 63
2018-04-14 04:00 | 63 | 63
2018-04-14 04:30 | 63 | 62
2018-04-14 05:00 | 62 | 62
2018-04-14 05:30 | 62 | 62
2018-04-14 06:00 | 62 | 62
2018-04-14 06:30 | 63 | 63
2018-04-14 07:00 | 64 | 63
2018-04-14 07:30 | 64 | 64
2018-04-14 08:00 | 64 | 64
2018-04-14 08:30 | 64 | 63
2018-04-14 09:00 | 63 | 63
2018-04-14 09:30 | 62 | 62
2018-04-14 10:00 | 62 | 62
2018-04-14 10:30 | 63 | 63
2018-04-14 11:00 | 63 | 63
2018-04-14 11:30 | 62 | 61
2018-04-14 12:00 | 62 | 62
2018-04-14 12:30 | 64 | 64
2018-04-14 13:00 | 64 | 63
2018-04-14 13:30 | 64 | 64
2018-04-14 14:00 | 66 | 66
2018-04-14 14:30 | 67 | 67
2018-04-14 15:00 | 67 | 67
2018-04-14 15:30 | 68 | 68
2018-04-14 16:00 | 68 | 68
2018-04-14 16:30 | 69 | 69
2018-04-14 17:00 | 69 | 69
2018-04-14 17:30 | 69 | 69
2018-04-14 18:00 | 69 | 68
2018-04-14 18:30 | 69 | 69
2018-04-14 19:00 | 71 | 70
2018-04-14 19:30 | 73 | 72
2018-04-14 20:00 | 72 | 70
2018-04-14 20:30 | 72 | 70
2018-04-14 21:00 | 72 | 71
2018-04-14 21:30 | 71 | 69
2018-04-14 22:00 | 70 | 67
2018-04-14 22:30 | 67 | 67
2018-04-14 23:00 | 67 | 67
2018-04-14 23:30 | 67 | 67
2018-04-15 | 66 | 66
2018-04-15 00:30 | 61 | 61
2018-04-15 01:00 | 59 | 59
2018-04-15 01:30 | 59 | 59
2018-04-15 02:00 | 59 | 59
2018-04-15 02:30 | 61 | 61
2018-04-15 03:00 | 62 | 62
2018-04-15 03:30 | 61 | 61
2018-04-15 04:00 | 62 | 62
2018-04-15 04:30 | 62 | 62
2018-04-15 05:00 | 62 | 62
2018-04-15 05:30 | 61 | 61
2018-04-15 06:00 | 61 | 61
2018-04-15 06:30 | 62 | 62
2018-04-15 07:00 | 62 | 62
2018-04-15 07:30 | 61 | 61
2018-04-15 08:00 | 62 | 62
2018-04-15 08:30 | 63 | 63
2018-04-15 09:00 | 63 | 63
2018-04-15 09:30 | 63 | 63
2018-04-15 10:00 | 63 | 62
2018-04-15 10:30 | 63 | 63
2018-04-15 11:00 | 65 | 64
2018-04-15 11:30 | 64 | 64
2018-04-15 12:00 | 65 | 65
2018-04-15 12:30 | 65 | 65
2018-04-15 13:00 | 66 | 65
2018-04-15 13:30 | 66 | 66
2018-04-15 14:00 | 66 | 66
2018-04-15 14:30 | 68 | 67
2018-04-15 15:00 | 69 | 68
2018-04-15 15:30 | 68 | 67
2018-04-15 16:00 | 69 | 68
2018-04-15 16:30 | 70 | 69
2018-04-15 17:00 | 70 | 70
2018-04-15 17:30 | 71 | 70
2018-04-15 18:00 | 71 | 70
2018-04-15 18:30 | 71 | 71
2018-04-15 19:00 | 73 | 72
2018-04-15 19:30 | 73 | 73
2018-04-15 20:00 | 73 | 72
2018-04-15 20:30 | 73 | 72
2018-04-15 21:00 | 72 | 71
2018-04-15 21:30 | 72 | 71
2018-04-15 22:00 | 71 | 70
2018-04-15 22:30 | 70 | 69
2018-04-15 23:00 | 68 | 67
2018-04-15 23:30 | 68 | 67
2018-04-16 | 68 | 67
2018-04-16 00:30 | 67 | 67
2018-04-16 01:00 | 66 | 66
2018-04-16 01:30 | 66 | 66
2018-04-16 02:00 | 66 | 66
2018-04-16 02:30 | 65 | 65
2018-04-16 03:00 | 64 | 64
2018-04-16 03:30 | 65 | 65
2018-04-16 04:00 | 65 | 65
2018-04-16 04:30 | 66 | 66
2018-04-16 05:00 | 68 | 68
2018-04-16 05:30 | 68 | 68
2018-04-16 06:00 | 69 | 69
2018-04-16 06:30 | 70 | 68
2018-04-16 07:00 | 73 | 71
2018-04-16 07:30 | 72 | 71
2018-04-16 08:00 | 70 | 70
2018-04-16 08:30 | 70 | 70
2018-04-16 09:00 | 69 | 69
2018-04-16 09:30 | 70 | 70
2018-04-16 10:00 | 69 | 69
2018-04-16 10:30 | 70 | 70
2018-04-16 11:00 | 71 | 71
2018-04-16 11:30 | 71 | 71
2018-04-16 12:00 | 72 | 71
2018-04-16 12:30 | 72 | 72
2018-04-16 13:00 | 73 | 73
2018-04-16 13:30 | 74 | 74
2018-04-16 14:00 | 74 | 74
2018-04-16 14:30 | 74 | 74
2018-04-16 15:00 | 74 | 74
2018-04-16 15:30 | 75 | 75
2018-04-16 16:00 | 74 | 74
2018-04-16 16:30 | 74 | 74
2018-04-16 17:00 | 75 | 74
2018-04-16 17:30 | 74 | 74
2018-04-16 18:00 | 76 | 76
2018-04-16 18:30 | 76 | 76
2018-04-16 19:00 | 78 | 78
2018-04-16 19:30 | 79 | 78
2018-04-16 20:00 | 77 | 77
2018-04-16 20:30 | 77 | 77
2018-04-16 21:00 | 75 | 75
2018-04-16 21:30 | 72 | 72
2018-04-16 22:00 | 71 | 71
2018-04-16 22:30 | 71 | 71
2018-04-16 23:00 | 69 | 69
2018-04-16 23:30 | 68 | 68
2018-04-17 | 70 | 70
2018-04-17 00:30 | 67 | 67
2018-04-17 01:00 | 66 | 66
2018-04-17 01:30 | 67 | 66
2018-04-17 02:00 | 67 | 67
2018-04-17 02:30 | 68 | 68
2018-04-17 03:00 | 66 | 66
2018-04-17 03:30 | 66 | 65
2018-04-17 04:00 | 66 | 66
2018-04-17 04:30 | 66 | 66
2018-04-17 05:00 | 66 | 65
2018-04-17 05:30 | 66 | 66
2018-04-17 06:00 | 67 | 67
2018-04-17 06:30 | 68 | 67
2018-04-17 07:00 | 69 | 68
2018-04-17 07:30 | 70 | 70
2018-04-17 08:00 | 71 | 70
2018-04-17 08:30 | 73 | 72
2018-04-17 09:00 | 72 | 72
2018-04-17 09:30 | 73 | 72
2018-04-17 10:00 | 72 | 71
2018-04-17 10:30 | 73 | 72
2018-04-17 11:00 | 73 | 72
2018-04-17 11:30 | 73 | 72
2018-04-17 12:00 | 73 | 72
2018-04-17 12:30 | 74 | 73
2018-04-17 13:00 | 73 | 73
2018-04-17 13:30 | 73 | 72
2018-04-17 14:00 | 77 | 76
2018-04-17 14:30 | 80 | 79
2018-04-17 15:00 | 80 | 79
2018-04-17 15:30 | 80 | 79
2018-04-17 16:00 | 82 | 81
2018-04-17 16:30 | 82 | 81
2018-04-17 17:00 | 83 | 82
2018-04-17 17:30 | 83 | 82
2018-04-17 18:00 | 83 | 82
2018-04-17 18:30 | 84 | 83
2018-04-17 19:00 | 84 | 83
2018-04-17 19:30 | 83 | 82
2018-04-17 20:00 | 83 | 82
2018-04-17 20:30 | 82 | 81
2018-04-17 21:00 | 81 | 80
2018-04-17 21:30 | 80 | 80
2018-04-17 22:00 | 80 | 79
2018-04-17 22:30 | 78 | 78
2018-04-17 23:00 | 74 | 74
2018-04-17 23:30 | 70 | 70
2018-04-18 | 69 | 69
2018-04-18 00:30 | 68 | 68
2018-04-18 01:00 | 68 | 68
2018-04-18 01:30 | 68 | 68
2018-04-18 02:00 | 68 | 68
2018-04-18 02:30 | 68 | 67
2018-04-18 03:00 | 67 | 67
2018-04-18 03:30 | 68 | 67
2018-04-18 04:00 | 67 | 67
2018-04-18 04:30 | 67 | 67
2018-04-18 05:00 | 67 | 67
2018-04-18 05:30 | 67 | 67
2018-04-18 06:00 | 67 | 67
2018-04-18 06:30 | 68 | 68
2018-04-18 07:00 | 68 | 68
2018-04-18 07:30 | 70 | 69
2018-04-18 08:00 | 72 | 70
2018-04-18 08:30 | 70 | 69
2018-04-18 09:00 | 71 | 69
2018-04-18 09:30 | 72 | 70
2018-04-18 10:00 | 71 | 70
2018-04-18 10:30 | 72 | 71
2018-04-18 11:00 | 71 | 69
2018-04-18 11:30 | 71 | 70
2018-04-18 12:00 | 72 | 70
2018-04-18 12:30 | 74 | 72
2018-04-18 13:00 | 73 | 73
2018-04-18 13:30 | 74 | 74
2018-04-18 14:00 | 74 | 73
2018-04-18 14:30 | 74 | 74
2018-04-18 15:00 | 72 | 72
2018-04-18 15:30 | 72 | 72
2018-04-18 16:00 | 73 | 73
2018-04-18 16:30 | 76 | 76
2018-04-18 17:00 | 79 | 78
2018-04-18 17:30 | 81 | 80
2018-04-18 18:00 | 81 | 80
2018-04-18 18:30 | 81 | 81
2018-04-18 19:00 | 82 | 82
2018-04-18 19:30 | 82 | 81
2018-04-18 20:00 | 82 | 82
2018-04-18 20:30 | 81 | 80
2018-04-18 21:00 | 81 | 80
2018-04-18 21:30 | 80 | 79
2018-04-18 22:00 | 79 | 78
2018-04-18 22:30 | 77 | 77
2018-04-18 23:00 | 73 | 73
2018-04-18 23:30 | 69 | 69
2018-04-19 | 68 | 68
2018-04-19 00:30 | 68 | 67
2018-04-19 01:00 | 67 | 66
2018-04-19 01:30 | 67 | 67
2018-04-19 02:00 | 67 | 66
2018-04-19 02:30 | 66 | 66
2018-04-19 03:00 | 66 | 66
2018-04-19 03:30 | 65 | 65
2018-04-19 04:00 | 65 | 65
2018-04-19 04:30 | 65 | 65
2018-04-19 05:00 | 64 | 64
2018-04-19 05:30 | 65 | 64
2018-04-19 06:00 | 64 | 64
2018-04-19 06:30 | 65 | 65
2018-04-19 07:00 | 66 | 65
2018-04-19 07:30 | 66 | 65
2018-04-19 08:00 | 68 | 68
2018-04-19 08:30 | 67 | 67
2018-04-19 09:00 | 66 | 65
2018-04-19 09:30 | 71 | 70
2018-04-19 10:00 | 73 | 72
2018-04-19 10:30 | 73 | 72
2018-04-19 11:00 | 73 | 72
2018-04-19 11:30 | 74 | 73
2018-04-19 12:00 | 75 | 74
2018-04-19 12:30 | 76 | 74
2018-04-19 13:00 | 76 | 74
2018-04-19 13:30 | 76 | 74
2018-04-19 14:00 | 78 | 76
2018-04-19 14:30 | 83 | 81
2018-04-19 15:00 | 85 | 82
2018-04-19 15:30 | 84 | 83
2018-04-19 16:00 | 83 | 82
2018-04-19 16:30 | 85 | 84
2018-04-19 17:00 | 81 | 80
2018-04-19 17:30 | 78 | 77
2018-04-19 18:00 | 79 | 78
2018-04-19 18:30 | 80 | 79
2018-04-19 19:00 | 81 | 80
2018-04-19 19:30 | 80 | 80
2018-04-19 20:00 | 81 | 80
2018-04-19 20:30 | 80 | 79
2018-04-19 21:00 | 80 | 79
2018-04-19 21:30 | 79 | 78
2018-04-19 22:00 | 78 | 77
2018-04-19 22:30 | 77 | 75
2018-04-19 23:00 | 73 | 72
2018-04-19 23:30 | 69 | 68
2018-04-20 | 69 | 67
2018-04-20 00:30 | 68 | 66
2018-04-20 01:00 | 66 | 66
2018-04-20 01:30 | 65 | 65
2018-04-20 02:00 | 65 | 64
2018-04-20 02:30 | 66 | 65
2018-04-20 03:00 | 66 | 65
2018-04-20 03:30 | 66 | 66
2018-04-20 04:00 | 65 | 65
2018-04-20 04:30 | 66 | 65
2018-04-20 05:00 | 66 | 65
2018-04-20 05:30 | 66 | 66
2018-04-20 06:00 | 66 | 66
2018-04-20 06:30 | 67 | 66
2018-04-20 07:00 | 67 | 67
2018-04-20 07:30 | 68 | 68
2018-04-20 08:00 | 69 | 69
2018-04-20 08:30 | 71 | 70
2018-04-20 09:00 | 71 | 70
2018-04-20 09:30 | 71 | 70
2018-04-20 10:00 | 70 | 69
2018-04-20 10:30 | 70 | 69
2018-04-20 11:00 | 70 | 69
2018-04-20 11:30 | 71 | 70
2018-04-20 12:00 | 71 | 71
2018-04-20 12:30 | 72 | 71
2018-04-20 13:00 | 71 | 71
2018-04-20 13:30 | 71 | 70
2018-04-20 14:00 | 71 | 70
2018-04-20 14:30 | 75 | 74
2018-04-20 15:00 | 79 | 78
2018-04-20 15:30 | 79 | 78
2018-04-20 16:00 | 79 | 79
2018-04-20 16:30 | 80 | 79
2018-04-20 17:00 | 80 | 79
2018-04-20 17:30 | 80 | 79
2018-04-20 18:00 | 80 | 79
2018-04-20 18:30 | 80 | 80
2018-04-20 19:00 | 82 | 81
2018-04-20 19:30 | 82 | 81
2018-04-20 20:00 | 82 | 81
2018-04-20 20:30 | 81 | 80
2018-04-20 21:00 | 80 | 79
2018-04-20 21:30 | 80 | 79
2018-04-20 22:00 | 79 | 78
2018-04-20 22:30 | 79 | 78
2018-04-20 23:00 | 76 | 75
2018-04-20 23:30 | 71 | 69
2018-04-21 | 71 | 69
2018-04-21 00:30 | 70 | 68
2018-04-21 01:00 | 70 | 68
2018-04-21 01:30 | 70 | 68
2018-04-21 02:00 | 70 | 68
2018-04-21 02:30 | 69 | 67
2018-04-21 03:00 | 69 | 66
2018-04-21 03:30 | 66 | 66
2018-04-21 04:00 | 65 | 65
2018-04-21 04:30 | 65 | 65
2018-04-21 05:00 | 67 | 67
2018-04-21 05:30 | 67 | 67
2018-04-21 06:00 | 67 | 67
2018-04-21 06:30 | 67 | 67
2018-04-21 07:00 | 66 | 66
2018-04-21 07:30 | 66 | 66
2018-04-21 08:00 | 66 | 66
2018-04-21 08:30 | 66 | 65
2018-04-21 09:00 | 67 | 67
2018-04-21 09:30 | 67 | 66
2018-04-21 10:00 | 67 | 66
2018-04-21 10:30 | 67 | 66
2018-04-21 11:00 | 66 | 66
2018-04-21 11:30 | 67 | 65
2018-04-21 12:00 | 67 | 65
2018-04-21 12:30 | 68 | 66
2018-04-21 13:00 | 68 | 67
2018-04-21 13:30 | 69 | 68
2018-04-21 14:00 | 70 | 69
2018-04-21 14:30 | 70 | 69
2018-04-21 15:00 | 70 | 68
2018-04-21 15:30 | 70 | 69
2018-04-21 16:00 | 71 | 69
2018-04-21 16:30 | 71 | 70
2018-04-21 17:00 | 72 | 71
2018-04-21 17:30 | 72 | 71
2018-04-21 18:00 | 72 | 71
2018-04-21 18:30 | 73 | 72
2018-04-21 19:00 | 73 | 73
2018-04-21 19:30 | 73 | 73
2018-04-21 20:00 | 73 | 72
2018-04-21 20:30 | 72 | 72
2018-04-21 21:00 | 72 | 71
2018-04-21 21:30 | 72 | 71
2018-04-21 22:00 | 71 | 70
2018-04-21 22:30 | 70 | 68
2018-04-21 23:00 | 70 | 68
2018-04-21 23:30 | 69 | 67
2018-04-22 | 67 | 67
2018-04-22 00:30 | 66 | 66
2018-04-22 01:00 | 65 | 65
2018-04-22 01:30 | 65 | 64
2018-04-22 02:00 | 64 | 64
2018-04-22 02:30 | 64 | 64
2018-04-22 03:00 | 65 | 65
2018-04-22 03:30 | 64 | 64
2018-04-22 04:00 | 64 | 64
2018-04-22 04:30 | 63 | 63
2018-04-22 05:00 | 63 | 63
2018-04-22 05:30 | 64 | 64
2018-04-22 06:00 | 64 | 64
2018-04-22 06:30 | 64 | 64
2018-04-22 07:00 | 63 | 63
2018-04-22 07:30 | 64 | 64
2018-04-22 08:00 | 66 | 66
2018-04-22 08:30 | 67 | 67
2018-04-22 09:00 | 67 | 67
2018-04-22 09:30 | 67 | 67
2018-04-22 10:00 | 67 | 66
2018-04-22 10:30 | 67 | 66
2018-04-22 11:00 | 67 | 67
2018-04-22 11:30 | 67 | 67
2018-04-22 12:00 | 67 | 66
2018-04-22 12:30 | 67 | 67
2018-04-22 13:00 | 67 | 67
2018-04-22 13:30 | 67 | 67
2018-04-22 14:00 | 68 | 67
2018-04-22 14:30 | 68 | 67
2018-04-22 15:00 | 69 | 68
2018-04-22 15:30 | 70 | 69
2018-04-22 16:00 | 70 | 69
2018-04-22 16:30 | 70 | 69
2018-04-22 17:00 | 71 | 70
2018-04-22 17:30 | 73 | 72
2018-04-22 18:00 | 73 | 72
2018-04-22 18:30 | 74 | 73
2018-04-22 19:00 | 74 | 74
2018-04-22 19:30 | 74 | 74
2018-04-22 20:00 | 74 | 73
2018-04-22 20:30 | 73 | 72
2018-04-22 21:00 | 72 | 71
2018-04-22 21:30 | 72 | 71
2018-04-22 22:00 | 71 | 69
2018-04-22 22:30 | 70 | 68
2018-04-22 23:00 | 67 | 67
2018-04-22 23:30 | 67 | 67
2018-04-23 | 67 | 66
2018-04-23 00:30 | 65 | 65
2018-04-23 01:00 | 65 | 65
2018-04-23 01:30 | 64 | 64
2018-04-23 02:00 | 65 | 65
2018-04-23 02:30 | 63 | 63
2018-04-23 03:00 | 63 | 63
2018-04-23 03:30 | 64 | 64
2018-04-23 04:00 | 64 | 64
2018-04-23 04:30 | 63 | 63
2018-04-23 05:00 | 64 | 64
2018-04-23 05:30 | 64 | 64
2018-04-23 06:00 | 64 | 64
2018-04-23 06:30 | 66 | 66
2018-04-23 07:00 | 67 | 67
2018-04-23 07:30 | 67 | 67
2018-04-23 08:00 | 69 | 69
2018-04-23 08:30 | 70 | 70
2018-04-23 09:00 | 69 | 69
2018-04-23 09:30 | 69 | 69
2018-04-23 10:00 | 68 | 68
2018-04-23 10:30 | 68 | 68
2018-04-23 11:00 | 68 | 68
2018-04-23 11:30 | 68 | 68
2018-04-23 12:00 | 69 | 68
2018-04-23 12:30 | 70 | 69
2018-04-23 13:00 | 70 | 69
2018-04-23 13:30 | 70 | 69
2018-04-23 14:00 | 71 | 70
2018-04-23 14:30 | 71 | 70
2018-04-23 15:00 | 70 | 69
2018-04-23 15:30 | 71 | 70
2018-04-23 16:00 | 71 | 70
2018-04-23 16:30 | 72 | 71
2018-04-23 17:00 | 72 | 71
2018-04-23 17:30 | 73 | 72
2018-04-23 18:00 | 74 | 72
2018-04-23 18:30 | 74 | 74
2018-04-23 19:00 | 75 | 75
2018-04-23 19:30 | 75 | 74
2018-04-23 20:00 | 75 | 74
2018-04-23 20:30 | 74 | 73
2018-04-23 21:00 | 73 | 72
2018-04-23 21:30 | 73 | 71
2018-04-23 22:00 | 73 | 71
2018-04-23 22:30 | 71 | 69
2018-04-23 23:00 | 69 | 67
2018-04-23 23:30 | 66 | 66
2018-04-24 | 65 | 65
2018-04-24 00:30 | 65 | 65
2018-04-24 01:00 | 65 | 65
2018-04-24 01:30 | 64 | 64
2018-04-24 02:00 | 63 | 63
2018-04-24 02:30 | 64 | 64
2018-04-24 03:00 | 64 | 64
2018-04-24 03:30 | 63 | 63
2018-04-24 04:00 | 63 | 63
2018-04-24 04:30 | 64 | 64
2018-04-24 05:00 | 63 | 63
2018-04-24 05:30 | 64 | 64
2018-04-24 06:00 | 65 | 64
2018-04-24 06:30 | 66 | 65
2018-04-24 07:00 | 68 | 68
2018-04-24 07:30 | 68 | 68
2018-04-24 08:00 | 68 | 68
2018-04-24 08:30 | 68 | 68
2018-04-24 09:00 | 68 | 68
2018-04-24 09:30 | 68 | 68
2018-04-24 10:00 | 67 | 67
2018-04-24 10:30 | 66 | 66
2018-04-24 11:00 | 67 | 66
2018-04-24 11:30 | 67 | 67
2018-04-24 12:00 | 67 | 67
2018-04-24 12:30 | 69 | 68
2018-04-24 13:00 | 69 | 69
2018-04-24 13:30 | 70 | 70
2018-04-24 14:00 | 69 | 69
2018-04-24 14:30 | 70 | 70
2018-04-24 15:00 | 70 | 70
2018-04-24 15:30 | 71 | 71
2018-04-24 16:00 | 71 | 70
2018-04-24 16:30 | 73 | 73
2018-04-24 17:00 | 73 | 73
2018-04-24 17:30 | 73 | 73
2018-04-24 18:00 | 74 | 74
2018-04-24 18:30 | 75 | 74
2018-04-24 19:00 | 75 | 75
2018-04-24 19:30 | 75 | 75
2018-04-24 20:00 | 75 | 75
2018-04-24 20:30 | 74 | 74
2018-04-24 21:00 | 73 | 73
2018-04-24 21:30 | 72 | 72
2018-04-24 22:00 | 71 | 71
2018-04-24 22:30 | 70 | 70
2018-04-24 23:00 | 69 | 68
2018-04-24 23:30 | 67 | 67
2018-04-25 | 67 | 66
2018-04-25 00:30 | 66 | 66
2018-04-25 01:00 | 66 | 66
2018-04-25 01:30 | 67 | 67
2018-04-25 02:00 | 65 | 65
2018-04-25 02:30 | 65 | 65
2018-04-25 03:00 | 65 | 65
2018-04-25 03:30 | 64 | 64
2018-04-25 04:00 | 37 | 31
2018-04-25 04:30 | 36 | 30
2018-04-25 05:00 | 41 | 37
2018-04-25 05:30 | 46 | 44
2018-04-25 06:00 | 48 | 47
2018-04-25 06:30 | 48 | 47
2018-04-25 07:00 | 47 | 46
2018-04-25 07:30 | 48 | 48
2018-04-25 08:00 | 52 | 51
2018-04-25 08:30 | 65 | 65
2018-04-25 09:00 | 67 | 67
2018-04-25 09:30 | 67 | 67
2018-04-25 10:00 | 53 | 52
2018-04-25 10:30 | 40 | 36
2018-04-25 11:00 | 45 | 43
2018-04-25 11:30 | 55 | 55
2018-04-25 12:00 | 66 | 66
2018-04-25 12:30 | 65 | 65
2018-04-25 13:00 | 68 | 67
2018-04-25 13:30 | 68 | 67
2018-04-25 14:00 | 68 | 68
2018-04-25 14:30 | 68 | 68
2018-04-25 15:00 | 69 | 68
2018-04-25 15:30 | 69 | 69
2018-04-25 16:00 | 70 | 69
2018-04-25 16:30 | 71 | 70
2018-04-25 17:00 | 72 | 71
2018-04-25 17:30 | 72 | 72
2018-04-25 18:00 | 73 | 72
2018-04-25 18:30 | 74 | 73
2018-04-25 19:00 | 73 | 73
2018-04-25 19:30 | 72 | 72
2018-04-25 20:00 | 72 | 72
2018-04-25 20:30 | 72 | 71
2018-04-25 21:00 | 66 | 66
2018-04-25 21:30 | 54 | 53
2018-04-25 22:00 | 53 | 52
2018-04-25 22:30 | 51 | 50
2018-04-25 23:00 | 47 | 46
2018-04-25 23:30 | 39 | 34
2018-04-26 | 38 | 33
2018-04-26 00:30 | 38 | 33
2018-04-26 01:00 | 38 | 33
2018-04-26 01:30 | 37 | 32
2018-04-26 02:00 | 37 | 32
2018-04-26 02:30 | 37 | 32
2018-04-26 03:00 | 37 | 31
2018-04-26 03:30 | 37 | 31
2018-04-26 04:00 | 37 | 32
2018-04-26 04:30 | 37 | 31
2018-04-26 05:00 | 37 | 32
2018-04-26 05:30 | 37 | 32
2018-04-26 06:00 | 37 | 32
2018-04-26 06:30 | 37 | 33
2018-04-26 07:00 | 38 | 34
2018-04-26 07:30 | 38 | 34
2018-04-26 08:00 | 40 | 36
2018-04-26 08:30 | 39 | 36
2018-04-26 09:00 | 36 | 32
2018-04-26 09:30 | 36 | 32
2018-04-26 10:00 | 36 | 33
2018-04-26 10:30 | 37 | 34
2018-04-26 11:00 | 37 | 34
2018-04-26 11:30 | 38 | 35
2018-04-26 12:00 | 38 | 35
2018-04-26 12:30 | 39 | 36
2018-04-26 13:00 | 42 | 39
2018-04-26 13:30 | 41 | 39
2018-04-26 14:00 | 42 | 39
2018-04-26 14:30 | 42 | 39
2018-04-26 15:00 | 42 | 39
2018-04-26 15:30 | 42 | 39
2018-04-26 16:00 | 42 | 40
2018-04-26 16:30 | 43 | 40
2018-04-26 17:00 | 44 | 41
2018-04-26 17:30 | 44 | 41
2018-04-26 18:00 | 44 | 42
2018-04-26 18:30 | 44 | 42
2018-04-26 19:00 | 45 | 43
2018-04-26 19:30 | 46 | 43
2018-04-26 20:00 | 45 | 43
2018-04-26 20:30 | 44 | 42
2018-04-26 21:00 | 42 | 38
2018-04-26 21:30 | 42 | 37
2018-04-26 22:00 | 41 | 36
2018-04-26 22:30 | 41 | 37
2018-04-26 23:00 | 39 | 35
2018-04-26 23:30 | 39 | 34
2018-04-27 | 38 | 34
2018-04-27 00:30 | 37 | 33
2018-04-27 01:00 | 38 | 33
2018-04-27 01:30 | 37 | 32
2018-04-27 02:00 | 37 | 32
2018-04-27 02:30 | 37 | 31
2018-04-27 03:00 | 37 | 32
2018-04-27 03:30 | 36 | 29
2018-04-27 04:00 | 36 | 29
2018-04-27 04:30 | 37 | 31
2018-04-27 05:00 | 37 | 31
2018-04-27 05:30 | 37 | 31
2018-04-27 06:00 | 37 | 32
2018-04-27 06:30 | 38 | 33
2018-04-27 07:00 | 38 | 34
2018-04-27 07:30 | 39 | 35
2018-04-27 08:00 | 39 | 37
2018-04-27 08:30 | 39 | 36
2018-04-27 09:00 | 38 | 34
2018-04-27 09:30 | 37 | 34
2018-04-27 10:00 | 36 | 33
2018-04-27 10:30 | 34 | 34
2018-04-27 11:00 | 12 | 12
2018-04-27 11:30 | 0 | 0
2018-04-27 12:00 | 0 | 0
2018-04-27 12:30 | 23 | 23
2018-04-27 13:00 | 35 | 35
2018-04-27 13:30 | 33 | 33
2018-04-27 14:00 | 33 | 33
2018-04-27 14:30 | 35 | 35
2018-04-27 15:00 | 36 | 36
2018-04-27 15:30 | 36 | 36
2018-04-27 16:00 | 39 | 38
2018-04-27 16:30 | 40 | 40
2018-04-27 17:00 | 40 | 40
2018-04-27 17:30 | 40 | 40
2018-04-27 18:00 | 41 | 41
2018-04-27 18:30 | 42 | 42
2018-04-27 19:00 | 42 | 42
2018-04-27 19:30 | 42 | 42
2018-04-27 20:00 | 44 | 44
2018-04-27 20:30 | 47 | 47
2018-04-27 21:00 | 54 | 53
2018-04-27 21:30 | 56 | 56
2018-04-27 22:00 | 55 | 55
2018-04-27 22:30 | 53 | 53
2018-04-27 23:00 | 51 | 51
2018-04-27 23:30 | 52 | 52
2018-04-28 | 48 | 48
2018-04-28 00:30 | 48 | 48
2018-04-28 01:00 | 47 | 47
2018-04-28 01:30 | 47 | 47
2018-04-28 02:00 | 47 | 46
2018-04-28 02:30 | 46 | 46
2018-04-28 03:00 | 46 | 46
2018-04-28 03:30 | 46 | 46
2018-04-28 04:00 | 46 | 46
2018-04-28 04:30 | 47 | 47
2018-04-28 05:00 | 47 | 47
2018-04-28 05:30 | 46 | 46
2018-04-28 06:00 | 47 | 47
2018-04-28 06:30 | 47 | 47
2018-04-28 07:00 | 46 | 46
2018-04-28 07:30 | 47 | 46
2018-04-28 08:00 | 50 | 49
2018-04-28 08:30 | 51 | 50
2018-04-28 09:00 | 51 | 50
2018-04-28 09:30 | 51 | 50
2018-04-28 10:00 | 47 | 47
2018-04-28 10:30 | 44 | 43
2018-04-28 11:00 | 39 | 38
2018-04-28 11:30 | 35 | 34
2018-04-28 12:00 | 34 | 33
2018-04-28 12:30 | 35 | 34
2018-04-28 13:00 | 42 | 41
2018-04-28 13:30 | 47 | 47
2018-04-28 14:00 | 43 | 42
2018-04-28 14:30 | 43 | 42
2018-04-28 15:00 | 44 | 43
2018-04-28 15:30 | 49 | 49
2018-04-28 16:00 | 60 | 60
2018-04-28 16:30 | 59 | 59
2018-04-28 17:00 | 61 | 61
2018-04-28 17:30 | 64 | 64
2018-04-28 18:00 | 65 | 65
2018-04-28 18:30 | 66 | 66
2018-04-28 19:00 | 65 | 65
2018-04-28 19:30 | 65 | 65
2018-04-28 20:00 | 64 | 64
2018-04-28 20:30 | 64 | 64
2018-04-28 21:00 | 63 | 63
2018-04-28 21:30 | 62 | 62
2018-04-28 22:00 | 62 | 62
2018-04-28 22:30 | 60 | 60
2018-04-28 23:00 | 60 | 60
2018-04-28 23:30 | 59 | 59
2018-04-29 | 58 | 58
2018-04-29 00:30 | 57 | 57
2018-04-29 01:00 | 57 | 57
2018-04-29 01:30 | 57 | 57
2018-04-29 02:00 | 57 | 56
2018-04-29 02:30 | 56 | 56
2018-04-29 03:00 | 56 | 56
2018-04-29 03:30 | 55 | 55
2018-04-29 04:00 | 55 | 55
2018-04-29 04:30 | 56 | 56
2018-04-29 05:00 | 56 | 56
2018-04-29 05:30 | 56 | 56
2018-04-29 06:00 | 56 | 56
2018-04-29 06:30 | 57 | 57
2018-04-29 07:00 | 61 | 61
2018-04-29 07:30 | 60 | 60
2018-04-29 08:00 | 59 | 59
2018-04-29 08:30 | 59 | 59
2018-04-29 09:00 | 59 | 59
2018-04-29 09:30 | 64 | 63
2018-04-29 10:00 | 64 | 64
2018-04-29 10:30 | 61 | 61
2018-04-29 11:00 | 59 | 59
2018-04-29 11:30 | 59 | 59
2018-04-29 12:00 | 59 | 59
2018-04-29 12:30 | 63 | 62
2018-04-29 13:00 | 62 | 62
2018-04-29 13:30 | 63 | 63
2018-04-29 14:00 | 59 | 59
2018-04-29 14:30 | 59 | 59
2018-04-29 15:00 | 62 | 62
2018-04-29 15:30 | 65 | 65
2018-04-29 16:00 | 68 | 67
2018-04-29 16:30 | 72 | 72
2018-04-29 17:00 | 76 | 76
2018-04-29 17:30 | 82 | 80
2018-04-29 18:00 | 86 | 84
2018-04-29 18:30 | 88 | 88
2018-04-29 19:00 | 88 | 88
2018-04-29 19:30 | 87 | 87
2018-04-29 20:00 | 86 | 85
2018-04-29 20:30 | 81 | 80
2018-04-29 21:00 | 76 | 75
2018-04-29 21:30 | 75 | 74
2018-04-29 22:00 | 74 | 72
2018-04-29 22:30 | 72 | 69
2018-04-29 23:00 | 72 | 70
2018-04-29 23:30 | 72 | 70
2018-04-30 | 66 | 66
2018-04-30 00:30 | 65 | 64
2018-04-30 01:00 | 65 | 65
2018-04-30 01:30 | 65 | 65
2018-04-30 02:00 | 64 | 64
2018-04-30 02:30 | 64 | 63
2018-04-30 03:00 | 64 | 64
2018-04-30 03:30 | 63 | 63
2018-04-30 04:00 | 64 | 64
2018-04-30 04:30 | 64 | 64
2018-04-30 05:00 | 64 | 64
2018-04-30 05:30 | 65 | 65
2018-04-30 06:00 | 65 | 65
2018-04-30 06:30 | 67 | 67
2018-04-30 07:00 | 67 | 67
2018-04-30 07:30 | 68 | 68
2018-04-30 08:00 | 71 | 68
2018-04-30 08:30 | 66 | 63
2018-04-30 09:00 | 66 | 63
2018-04-30 09:30 | 66 | 63
2018-04-30 10:00 | 49 | 43
2018-04-30 10:30 | 46 | 35
2018-04-30 11:00 | 48 | 35
2018-04-30 11:30 | 46 | 35
2018-04-30 12:00 | 36 | 33
2018-04-30 12:30 | 38 | 37
2018-04-30 13:00 | 37 | 36
2018-04-30 13:30 | 40 | 39
2018-04-30 14:00 | 36 | 35
2018-04-30 14:30 | 38 | 36
2018-04-30 15:00 | 51 | 50
2018-04-30 15:30 | 57 | 57
2018-04-30 16:00 | 60 | 59
2018-04-30 16:30 | 65 | 65
2018-04-30 17:00 | 73 | 71
2018-04-30 17:30 | 75 | 73
2018-04-30 18:00 | 74 | 72
2018-04-30 18:30 | 78 | 77
2018-04-30 19:00 | 78 | 77
2018-04-30 19:30 | 78 | 76
2018-04-30 20:00 | 77 | 76
2018-04-30 20:30 | 76 | 74
2018-04-30 21:00 | 76 | 74
2018-04-30 21:30 | 75 | 73
2018-04-30 22:00 | 76 | 73
2018-04-30 22:30 | 72 | 70
2018-04-30 23:00 | 71 | 69
2018-04-30 23:30 | 69 | 67
2018-05-01 | 69 | 67
2018-05-01 00:30 | 67 | 67
2018-05-01 01:00 | 67 | 66
2018-05-01 01:30 | 67 | 66
2018-05-01 02:00 | 66 | 66
2018-05-01 02:30 | 65 | 65
2018-05-01 03:00 | 66 | 66
2018-05-01 03:30 | 65 | 65
2018-05-01 04:00 | 65 | 65
2018-05-01 04:30 | 65 | 65
2018-05-01 05:00 | 65 | 65
2018-05-01 05:30 | 65 | 65
2018-05-01 06:00 | 66 | 66
2018-05-01 06:30 | 68 | 68
2018-05-01 07:00 | 70 | 70
2018-05-01 07:30 | 69 | 69
2018-05-01 08:00 | 67 | 66
2018-05-01 08:30 | 62 | 61
2018-05-01 09:00 | 57 | 55
2018-05-01 09:30 | 62 | 60
2018-05-01 10:00 | 54 | 49
2018-05-01 10:30 | 50 | 41
2018-05-01 11:00 | 45 | 35
2018-05-01 11:30 | 49 | 42
2018-05-01 12:00 | 49 | 42
2018-05-01 12:30 | 47 | 39
2018-05-01 13:00 | 50 | 43
2018-05-01 13:30 | 41 | 40
2018-05-01 14:00 | 45 | 45
2018-05-01 14:30 | 62 | 61
2018-05-01 15:00 | 66 | 64
2018-05-01 15:30 | 66 | 65
2018-05-01 16:00 | 67 | 66
2018-05-01 16:30 | 70 | 68
2018-05-01 17:00 | 72 | 70
2018-05-01 17:30 | 72 | 70
2018-05-01 18:00 | 72 | 70
2018-05-01 18:30 | 72 | 71
2018-05-01 19:00 | 72 | 71
2018-05-01 19:30 | 72 | 70
2018-05-01 20:00 | 72 | 70
2018-05-01 20:30 | 72 | 70
2018-05-01 21:00 | 70 | 68
2018-05-01 21:30 | 68 | 66
2018-05-01 22:00 | 67 | 65
2018-05-01 22:30 | 66 | 64
2018-05-01 23:00 | 63 | 63
2018-05-01 23:30 | 63 | 63
2018-05-02 | 63 | 62
2018-05-02 00:30 | 62 | 62
2018-05-02 01:00 | 62 | 62
2018-05-02 01:30 | 62 | 62
2018-05-02 02:00 | 62 | 62
2018-05-02 02:30 | 62 | 62
2018-05-02 03:00 | 62 | 62
2018-05-02 03:30 | 62 | 62
2018-05-02 04:00 | 62 | 61
2018-05-02 04:30 | 62 | 62
2018-05-02 05:00 | 62 | 62
2018-05-02 05:30 | 62 | 62
2018-05-02 06:00 | 63 | 63
2018-05-02 06:30 | 65 | 64
2018-05-02 07:00 | 66 | 66
2018-05-02 07:30 | 65 | 64
2018-05-02 08:00 | 61 | 61
2018-05-02 08:30 | 58 | 57
2018-05-02 09:00 | 56 | 55
2018-05-02 09:30 | 53 | 52
2018-05-02 10:00 | 51 | 50
2018-05-02 10:30 | 51 | 50
2018-05-02 11:00 | 49 | 48
2018-05-02 11:30 | 51 | 50
2018-05-02 12:00 | 53 | 51
2018-05-02 12:30 | 59 | 58
2018-05-02 13:00 | 56 | 54
2018-05-02 13:30 | 56 | 54
2018-05-02 14:00 | 57 | 56
2018-05-02 14:30 | 55 | 54
2018-05-02 15:00 | 52 | 51
2018-05-02 15:30 | 53 | 52
2018-05-02 16:00 | 57 | 56
2018-05-02 16:30 | 62 | 61
2018-05-02 17:00 | 66 | 65
2018-05-02 17:30 | 69 | 68
2018-05-02 18:00 | 71 | 70
2018-05-02 18:30 | 71 | 71
2018-05-02 19:00 | 71 | 70
2018-05-02 19:30 | 71 | 71
2018-05-02 20:00 | 72 | 71
2018-05-02 20:30 | 71 | 71
2018-05-02 21:00 | 70 | 70
2018-05-02 21:30 | 69 | 68
2018-05-02 22:00 | 69 | 68
2018-05-02 22:30 | 69 | 67
2018-05-02 23:00 | 68 | 66
2018-05-02 23:30 | 68 | 66
2018-05-03 | 68 | 66
2018-05-03 00:30 | 68 | 66
2018-05-03 01:00 | 66 | 64
2018-05-03 01:30 | 64 | 64
2018-05-03 02:00 | 65 | 65
2018-05-03 02:30 | 65 | 64
2018-05-03 03:00 | 64 | 64
2018-05-03 03:30 | 64 | 64
2018-05-03 04:00 | 64 | 64
2018-05-03 04:30 | 66 | 66
2018-05-03 05:00 | 69 | 69
2018-05-03 05:30 | 69 | 69
2018-05-03 06:00 | 69 | 69
2018-05-03 06:30 | 70 | 69
2018-05-03 07:00 | 70 | 69
2018-05-03 07:30 | 69 | 68
2018-05-03 08:00 | 67 | 67
2018-05-03 08:30 | 71 | 70
2018-05-03 09:00 | 72 | 71
2018-05-03 09:30 | 74 | 72
2018-05-03 10:00 | 73 | 72
2018-05-03 10:30 | 73 | 72
2018-05-03 11:00 | 70 | 69
2018-05-03 11:30 | 73 | 72
2018-05-03 12:00 | 69 | 68
2018-05-03 12:30 | 63 | 62
2018-05-03 13:00 | 59 | 59
2018-05-03 13:30 | 59 | 59
2018-05-03 14:00 | 64 | 63
2018-05-03 14:30 | 61 | 61
2018-05-03 15:00 | 60 | 60
2018-05-03 15:30 | 62 | 62
2018-05-03 16:00 | 62 | 61
2018-05-03 16:30 | 64 | 63
2018-05-03 17:00 | 67 | 66
2018-05-03 17:30 | 69 | 68
2018-05-03 18:00 | 70 | 69
2018-05-03 18:30 | 70 | 69
2018-05-03 19:00 | 70 | 69
2018-05-03 19:30 | 71 | 70
2018-05-03 20:00 | 70 | 69
2018-05-03 20:30 | 69 | 69
2018-05-03 21:00 | 67 | 66
2018-05-03 21:30 | 68 | 67
2018-05-03 22:00 | 64 | 63
2018-05-03 22:30 | 63 | 62
2018-05-03 23:00 | 62 | 62
2018-05-03 23:30 | 62 | 61
2018-05-04 | 62 | 61
2018-05-04 00:30 | 62 | 62
2018-05-04 01:00 | 62 | 61
2018-05-04 01:30 | 62 | 62
2018-05-04 02:00 | 62 | 61
2018-05-04 02:30 | 61 | 61
2018-05-04 03:00 | 61 | 61
2018-05-04 03:30 | 61 | 61
2018-05-04 04:00 | 61 | 61
2018-05-04 04:30 | 61 | 61
2018-05-04 05:00 | 62 | 62
2018-05-04 05:30 | 62 | 62
2018-05-04 06:00 | 63 | 63
2018-05-04 06:30 | 61 | 60
2018-05-04 07:00 | 62 | 62
2018-05-04 07:30 | 63 | 63
2018-05-04 08:00 | 63 | 63
2018-05-04 08:30 | 62 | 62
2018-05-04 09:00 | 56 | 56
2018-05-04 09:30 | 51 | 51
2018-05-04 10:00 | 53 | 53
2018-05-04 10:30 | 50 | 50
2018-05-04 11:00 | 48 | 48
2018-05-04 11:30 | 49 | 49
2018-05-04 12:00 | 51 | 51
2018-05-04 12:30 | 51 | 50
2018-05-04 13:00 | 56 | 55
2018-05-04 13:30 | 55 | 55
2018-05-04 14:00 | 57 | 57
2018-05-04 14:30 | 54 | 53
2018-05-04 15:00 | 60 | 59
2018-05-04 15:30 | 59 | 59
2018-05-04 16:00 | 60 | 60
2018-05-04 16:30 | 63 | 62
2018-05-04 17:00 | 66 | 66
2018-05-04 17:30 | 68 | 68
2018-05-04 18:00 | 69 | 68
2018-05-04 18:30 | 69 | 68
2018-05-04 19:00 | 69 | 68
2018-05-04 19:30 | 69 | 68
2018-05-04 20:00 | 68 | 67
2018-05-04 20:30 | 68 | 67
2018-05-04 21:00 | 67 | 66
2018-05-04 21:30 | 66 | 65
2018-05-04 22:00 | 59 | 58
2018-05-04 22:30 | 54 | 54
2018-05-04 23:00 | 55 | 54
2018-05-04 23:30 | 52 | 52
2018-05-05 | 52 | 51
2018-05-05 00:30 | 54 | 53
2018-05-05 01:00 | 55 | 54
2018-05-05 01:30 | 55 | 55
2018-05-05 02:00 | 55 | 54
2018-05-05 02:30 | 55 | 54
2018-05-05 03:00 | 55 | 55
2018-05-05 03:30 | 55 | 55
2018-05-05 04:00 | 60 | 59
2018-05-05 04:30 | 61 | 61
2018-05-05 05:00 | 60 | 60
2018-05-05 05:30 | 61 | 61
2018-05-05 06:00 | 62 | 61
2018-05-05 06:30 | 59 | 59
2018-05-05 07:00 | 58 | 58
2018-05-05 07:30 | 58 | 58
2018-05-05 08:00 | 58 | 58
2018-05-05 08:30 | 56 | 56
2018-05-05 09:00 | 54 | 54
2018-05-05 09:30 | 53 | 53
2018-05-05 10:00 | 53 | 53
2018-05-05 10:30 | 54 | 53
2018-05-05 11:00 | 55 | 54
2018-05-05 11:30 | 54 | 54
2018-05-05 12:00 | 56 | 56
2018-05-05 12:30 | 59 | 58
2018-05-05 13:00 | 55 | 55
2018-05-05 13:30 | 55 | 55
2018-05-05 14:00 | 55 | 55
2018-05-05 14:30 | 55 | 54
2018-05-05 15:00 | 55 | 55
2018-05-05 15:30 | 57 | 57
2018-05-05 16:00 | 59 | 58
2018-05-05 16:30 | 61 | 61
2018-05-05 17:00 | 65 | 64
2018-05-05 17:30 | 67 | 66
2018-05-05 18:00 | 68 | 67
2018-05-05 18:30 | 69 | 68
2018-05-05 19:00 | 69 | 68
2018-05-05 19:30 | 69 | 68
2018-05-05 20:00 | 68 | 67
2018-05-05 20:30 | 68 | 67
2018-05-05 21:00 | 67 | 66
2018-05-05 21:30 | 67 | 65
2018-05-05 22:00 | 67 | 65
2018-05-05 22:30 | 66 | 63
2018-05-05 23:00 | 64 | 63
2018-05-05 23:30 | 62 | 62
2018-05-06 | 62 | 62
2018-05-06 00:30 | 63 | 63
2018-05-06 01:00 | 63 | 63
2018-05-06 01:30 | 63 | 63
2018-05-06 02:00 | 63 | 62
2018-05-06 02:30 | 62 | 62
2018-05-06 03:00 | 62 | 62
2018-05-06 03:30 | 62 | 62
2018-05-06 04:00 | 62 | 62
2018-05-06 04:30 | 62 | 62
2018-05-06 05:00 | 62 | 62
2018-05-06 05:30 | 62 | 62
2018-05-06 06:00 | 62 | 62
2018-05-06 06:30 | 60 | 60
2018-05-06 07:00 | 60 | 60
2018-05-06 07:30 | 60 | 59
2018-05-06 08:00 | 59 | 58
2018-05-06 08:30 | 57 | 57
2018-05-06 09:00 | 55 | 55
2018-05-06 09:30 | 54 | 54
2018-05-06 10:00 | 53 | 53
2018-05-06 10:30 | 53 | 53
2018-05-06 11:00 | 53 | 53
2018-05-06 11:30 | 54 | 54
2018-05-06 12:00 | 55 | 55
2018-05-06 12:30 | 55 | 55
2018-05-06 13:00 | 54 | 54
2018-05-06 13:30 | 56 | 56
2018-05-06 14:00 | 59 | 59
2018-05-06 14:30 | 62 | 62
2018-05-06 15:00 | 56 | 56
2018-05-06 15:30 | 62 | 62
2018-05-06 16:00 | 61 | 61
2018-05-06 16:30 | 62 | 62
2018-05-06 17:00 | 64 | 64
2018-05-06 17:30 | 65 | 65
2018-05-06 18:00 | 65 | 65
2018-05-06 18:30 | 67 | 67
2018-05-06 19:00 | 68 | 67
2018-05-06 19:30 | 69 | 67
2018-05-06 20:00 | 69 | 67
2018-05-06 20:30 | 68 | 66
2018-05-06 21:00 | 68 | 66
2018-05-06 21:30 | 67 | 65
2018-05-06 22:00 | 66 | 64
2018-05-06 22:30 | 66 | 64
2018-05-06 23:00 | 65 | 63
2018-05-06 23:30 | 65 | 62
2018-05-07 | 64 | 62
2018-05-07 00:30 | 65 | 62
2018-05-07 01:00 | 66 | 63
2018-05-07 01:30 | 63 | 62
2018-05-07 02:00 | 62 | 62
2018-05-07 02:30 | 62 | 62
2018-05-07 03:00 | 62 | 62
2018-05-07 03:30 | 62 | 62
2018-05-07 04:00 | 63 | 63
2018-05-07 04:30 | 63 | 63
2018-05-07 05:00 | 63 | 63
2018-05-07 05:30 | 63 | 63
2018-05-07 06:00 | 63 | 63
2018-05-07 06:30 | 61 | 61
2018-05-07 07:00 | 61 | 61
2018-05-07 07:30 | 60 | 60
2018-05-07 08:00 | 59 | 59
2018-05-07 08:30 | 58 | 58
2018-05-07 09:00 | 58 | 57
2018-05-07 09:30 | 56 | 56
2018-05-07 10:00 | 58 | 58
2018-05-07 10:30 | 57 | 57
2018-05-07 11:00 | 57 | 57
2018-05-07 11:30 | 57 | 57
2018-05-07 12:00 | 58 | 57
2018-05-07 12:30 | 59 | 59
2018-05-07 13:00 | 61 | 61
2018-05-07 13:30 | 63 | 62
2018-05-07 14:00 | 64 | 63
2018-05-07 14:30 | 59 | 59
2018-05-07 15:00 | 61 | 61
2018-05-07 15:30 | 61 | 60
2018-05-07 16:00 | 64 | 63
2018-05-07 16:30 | 65 | 64
2018-05-07 17:00 | 68 | 68
2018-05-07 17:30 | 69 | 68
2018-05-07 18:00 | 69 | 68
2018-05-07 18:30 | 71 | 70
2018-05-07 19:00 | 71 | 70
2018-05-07 19:30 | 70 | 69
2018-05-07 20:00 | 69 | 68
2018-05-07 20:30 | 68 | 67
2018-05-07 21:00 | 67 | 66
2018-05-07 21:30 | 67 | 66
2018-05-07 22:00 | 66 | 65
2018-05-07 22:30 | 65 | 65
2018-05-07 23:00 | 65 | 64
2018-05-07 23:30 | 63 | 63
2018-05-08 | 63 | 63
2018-05-08 00:30 | 63 | 62
2018-05-08 01:00 | 63 | 63
2018-05-08 01:30 | 62 | 62
2018-05-08 02:00 | 63 | 62
2018-05-08 02:30 | 62 | 62
2018-05-08 03:00 | 61 | 61
2018-05-08 03:30 | 61 | 61
2018-05-08 04:00 | 62 | 62
2018-05-08 04:30 | 62 | 61
2018-05-08 05:00 | 62 | 61
2018-05-08 05:30 | 62 | 62
2018-05-08 06:00 | 62 | 62
2018-05-08 06:30 | 63 | 62
2018-05-08 07:00 | 63 | 62
2018-05-08 07:30 | 64 | 62
2018-05-08 08:00 | 62 | 60
2018-05-08 08:30 | 58 | 56
2018-05-08 09:00 | 55 | 53
2018-05-08 09:30 | 52 | 50
2018-05-08 10:00 | 50 | 48
2018-05-08 10:30 | 50 | 47
2018-05-08 11:00 | 50 | 47
2018-05-08 11:30 | 50 | 47
2018-05-08 12:00 | 52 | 49
2018-05-08 12:30 | 50 | 48
2018-05-08 13:00 | 51 | 48
2018-05-08 13:30 | 54 | 52
2018-05-08 14:00 | 54 | 51
2018-05-08 14:30 | 53 | 50
2018-05-08 15:00 | 54 | 51
2018-05-08 15:30 | 57 | 54
2018-05-08 16:00 | 56 | 54
2018-05-08 16:30 | 63 | 62
2018-05-08 17:00 | 63 | 63
2018-05-08 17:30 | 64 | 63
2018-05-08 18:00 | 57 | 52
2018-05-08 18:30 | 66 | 64
2018-05-08 19:00 | 71 | 70
2018-05-08 19:30 | 71 | 70
2018-05-08 20:00 | 71 | 70
2018-05-08 20:30 | 70 | 69
2018-05-08 21:00 | 70 | 69
2018-05-08 21:30 | 70 | 69
2018-05-08 22:00 | 69 | 68
2018-05-08 22:30 | 69 | 67
2018-05-08 23:00 | 66 | 64
2018-05-08 23:30 | 64 | 63
2018-05-09 | 64 | 63
2018-05-09 00:30 | 64 | 62
2018-05-09 01:00 | 63 | 61
2018-05-09 01:30 | 63 | 61
2018-05-09 02:00 | 63 | 61
2018-05-09 02:30 | 62 | 60
2018-05-09 03:00 | 61 | 59
2018-05-09 03:30 | 62 | 60
2018-05-09 04:00 | 63 | 60
2018-05-09 04:30 | 63 | 61
2018-05-09 05:00 | 63 | 61
2018-05-09 05:30 | 63 | 61
2018-05-09 06:00 | 62 | 61
2018-05-09 06:30 | 61 | 59
2018-05-09 07:00 | 61 | 59
2018-05-09 07:30 | 60 | 59
2018-05-09 08:00 | 61 | 60
2018-05-09 08:30 | 64 | 63
2018-05-09 09:00 | 67 | 66
2018-05-09 09:30 | 58 | 58
2018-05-09 10:00 | 52 | 50
2018-05-09 10:30 | 52 | 48
2018-05-09 11:00 | 44 | 38
2018-05-09 11:30 | 39 | 28
2018-05-09 12:00 | 39 | 30
2018-05-09 12:30 | 50 | 48
2018-05-09 13:00 | 55 | 53
2018-05-09 13:30 | 53 | 51
2018-05-09 14:00 | 52 | 50
2018-05-09 14:30 | 53 | 51
2018-05-09 15:00 | 56 | 54
2018-05-09 15:30 | 55 | 54
2018-05-09 16:00 | 61 | 59
2018-05-09 16:30 | 64 | 63
2018-05-09 17:00 | 66 | 65
2018-05-09 17:30 | 75 | 74
2018-05-09 18:00 | 74 | 74
2018-05-09 18:30 | 78 | 75
2018-05-09 19:00 | 80 | 74
2018-05-09 19:30 | 80 | 74
2018-05-09 20:00 | 80 | 73
2018-05-09 20:30 | 80 | 72
2018-05-09 21:00 | 76 | 72
2018-05-09 21:30 | 72 | 71
2018-05-09 22:00 | 71 | 70
2018-05-09 22:30 | 70 | 69
2018-05-09 23:00 | 69 | 68
2018-05-09 23:30 | 68 | 67
2018-05-10 | 64 | 63
2018-05-10 00:30 | 65 | 64
2018-05-10 01:00 | 64 | 63
2018-05-10 01:30 | 64 | 63
2018-05-10 02:00 | 64 | 63
2018-05-10 02:30 | 63 | 62
2018-05-10 03:00 | 64 | 63
2018-05-10 03:30 | 64 | 63
2018-05-10 04:00 | 64 | 62
2018-05-10 04:30 | 64 | 63
2018-05-10 05:00 | 64 | 63
2018-05-10 05:30 | 63 | 62
2018-05-10 06:00 | 63 | 62
2018-05-10 06:30 | 64 | 63
2018-05-10 07:00 | 71 | 63
2018-05-10 07:30 | 69 | 61
2018-05-10 08:00 | 66 | 57
2018-05-10 08:30 | 67 | 58
2018-05-10 09:00 | 65 | 54
2018-05-10 09:30 | 63 | 52
2018-05-10 10:00 | 65 | 54
2018-05-10 10:30 | 63 | 52
2018-05-10 11:00 | 61 | 49
2018-05-10 11:30 | 62 | 50
2018-05-10 12:00 | 62 | 52
2018-05-10 12:30 | 64 | 54
2018-05-10 13:00 | 63 | 51
2018-05-10 13:30 | 62 | 50
2018-05-10 14:00 | 65 | 52
2018-05-10 14:30 | 64 | 53
2018-05-10 15:00 | 63 | 53
2018-05-10 15:30 | 66 | 56
2018-05-10 16:00 | 66 | 57
2018-05-10 16:30 | 70 | 61
2018-05-10 17:00 | 75 | 67
2018-05-10 17:30 | 80 | 71
2018-05-10 18:00 | 81 | 73
2018-05-10 18:30 | 82 | 74
2018-05-10 19:00 | 82 | 74
2018-05-10 19:30 | 82 | 74
2018-05-10 20:00 | 82 | 73
2018-05-10 20:30 | 82 | 73
2018-05-10 21:00 | 74 | 71
2018-05-10 21:30 | 71 | 70
2018-05-10 22:00 | 70 | 68
2018-05-10 22:30 | 70 | 68
2018-05-10 23:00 | 70 | 67
2018-05-10 23:30 | 67 | 65
2018-05-11 | 64 | 62
2018-05-11 00:30 | 63 | 62
2018-05-11 01:00 | 63 | 62
2018-05-11 01:30 | 64 | 62
2018-05-11 02:00 | 64 | 62
2018-05-11 02:30 | 63 | 61
2018-05-11 03:00 | 63 | 61
2018-05-11 03:30 | 63 | 61
2018-05-11 04:00 | 63 | 61
2018-05-11 04:30 | 64 | 62
2018-05-11 05:00 | 67 | 66
2018-05-11 05:30 | 68 | 66
2018-05-11 06:00 | 68 | 66
2018-05-11 06:30 | 67 | 66
2018-05-11 07:00 | 68 | 67
2018-05-11 07:30 | 67 | 67
2018-05-11 08:00 | 66 | 65
2018-05-11 08:30 | 69 | 68
2018-05-11 09:00 | 69 | 68
2018-05-11 09:30 | 68 | 66
2018-05-11 10:00 | 61 | 60
2018-05-11 10:30 | 57 | 55
2018-05-11 11:00 | 61 | 60
2018-05-11 11:30 | 61 | 59
2018-05-11 12:00 | 57 | 55
2018-05-11 12:30 | 57 | 55
2018-05-11 13:00 | 57 | 55
2018-05-11 13:30 | 57 | 55
2018-05-11 14:00 | 62 | 60
2018-05-11 14:30 | 62 | 61
2018-05-11 15:00 | 60 | 58
2018-05-11 15:30 | 58 | 56
2018-05-11 16:00 | 66 | 64
2018-05-11 16:30 | 70 | 68
2018-05-11 17:00 | 74 | 72
2018-05-11 17:30 | 77 | 75
2018-05-11 18:00 | 79 | 77
2018-05-11 18:30 | 80 | 78
2018-05-11 19:00 | 80 | 78
2018-05-11 19:30 | 79 | 77
2018-05-11 20:00 | 79 | 76
2018-05-11 20:30 | 78 | 75
2018-05-11 21:00 | 78 | 75
2018-05-11 21:30 | 77 | 74
2018-05-11 22:00 | 74 | 72
2018-05-11 22:30 | 72 | 71
2018-05-11 23:00 | 72 | 70
2018-05-11 23:30 | 69 | 67
2018-05-12 | 70 | 68
2018-05-12 00:30 | 66 | 64
2018-05-12 01:00 | 63 | 63
2018-05-12 01:30 | 62 | 62
2018-05-12 02:00 | 62 | 62
2018-05-12 02:30 | 62 | 62
2018-05-12 03:00 | 61 | 61
2018-05-12 03:30 | 62 | 61
2018-05-12 04:00 | 62 | 62
2018-05-12 04:30 | 63 | 63
2018-05-12 05:00 | 63 | 63
2018-05-12 05:30 | 62 | 62
2018-05-12 06:00 | 62 | 62
2018-05-12 06:30 | 63 | 62
2018-05-12 07:00 | 63 | 62
2018-05-12 07:30 | 61 | 61
2018-05-12 08:00 | 60 | 60
2018-05-12 08:30 | 56 | 56
2018-05-12 09:00 | 53 | 53
2018-05-12 09:30 | 53 | 53
2018-05-12 10:00 | 53 | 51
2018-05-12 10:30 | 53 | 51
2018-05-12 11:00 | 53 | 51
2018-05-12 11:30 | 53 | 51
2018-05-12 12:00 | 53 | 52
2018-05-12 12:30 | 54 | 52
2018-05-12 13:00 | 56 | 53
2018-05-12 13:30 | 54 | 51
2018-05-12 14:00 | 54 | 52
2018-05-12 14:30 | 54 | 52
2018-05-12 15:00 | 53 | 51
2018-05-12 15:30 | 55 | 53
2018-05-12 16:00 | 58 | 56
2018-05-12 16:30 | 61 | 60
2018-05-12 17:00 | 64 | 63
2018-05-12 17:30 | 67 | 66
2018-05-12 18:00 | 70 | 69
2018-05-12 18:30 | 70 | 69
2018-05-12 19:00 | 70 | 68
2018-05-12 19:30 | 68 | 67
2018-05-12 20:00 | 68 | 66
2018-05-12 20:30 | 48 | 37
2018-05-12 21:00 | 36 | 32
2018-05-12 21:30 | 36 | 32
2018-05-12 22:00 | 42 | 40
2018-05-12 22:30 | 45 | 44
2018-05-12 23:00 | 46 | 45
2018-05-12 23:30 | 45 | 45
2018-05-13 | 45 | 45
2018-05-13 00:30 | 45 | 44
2018-05-13 01:00 | 47 | 46
2018-05-13 01:30 | 58 | 58
2018-05-13 02:00 | 58 | 58
2018-05-13 02:30 | 58 | 58
2018-05-13 03:00 | 58 | 58
2018-05-13 03:30 | 58 | 58
2018-05-13 04:00 | 58 | 58
2018-05-13 04:30 | 58 | 58
2018-05-13 05:00 | 58 | 58
2018-05-13 05:30 | 59 | 59
2018-05-13 06:00 | 59 | 59
2018-05-13 06:30 | 59 | 59
2018-05-13 07:00 | 58 | 58
2018-05-13 07:30 | 58 | 58
2018-05-13 08:00 | 58 | 58
2018-05-13 08:30 | 61 | 61
2018-05-13 09:00 | 60 | 60
2018-05-13 09:30 | 59 | 58
2018-05-13 10:00 | 58 | 58
2018-05-13 10:30 | 58 | 58
2018-05-13 11:00 | 58 | 58
2018-05-13 11:30 | 58 | 58
2018-05-13 12:00 | 57 | 57
2018-05-13 12:30 | 54 | 54
2018-05-13 13:00 | 43 | 43
2018-05-13 13:30 | 44 | 44
2018-05-13 14:00 | 44 | 44
2018-05-13 14:30 | 45 | 45
2018-05-13 15:00 | 46 | 46
2018-05-13 15:30 | 48 | 48
2018-05-13 16:00 | 53 | 53
2018-05-13 16:30 | 56 | 56
2018-05-13 17:00 | 59 | 59
2018-05-13 17:30 | 59 | 59
2018-05-13 18:00 | 61 | 61
2018-05-13 18:30 | 62 | 62
2018-05-13 19:00 | 63 | 61
2018-05-13 19:30 | 63 | 61
2018-05-13 20:00 | 64 | 61
2018-05-13 20:30 | 62 | 59
2018-05-13 21:00 | 61 | 59
2018-05-13 21:30 | 60 | 57
2018-05-13 22:00 | 61 | 56
2018-05-13 22:30 | 60 | 55
2018-05-13 23:00 | 59 | 54
2018-05-13 23:30 | 60 | 55
2018-05-14 | 60 | 55
2018-05-14 00:30 | 57 | 55
2018-05-14 01:00 | 54 | 54
2018-05-14 01:30 | 54 | 54
2018-05-14 02:00 | 54 | 54
2018-05-14 02:30 | 54 | 54
2018-05-14 03:00 | 54 | 54
2018-05-14 03:30 | 54 | 54
2018-05-14 04:00 | 54 | 54
2018-05-14 04:30 | 54 | 54
2018-05-14 05:00 | 55 | 55
2018-05-14 05:30 | 55 | 55
2018-05-14 06:00 | 55 | 55
2018-05-14 06:30 | 56 | 56
2018-05-14 07:00 | 57 | 57
2018-05-14 07:30 | 56 | 56
2018-05-14 08:00 | 53 | 53
2018-05-14 08:30 | 48 | 48
2018-05-14 09:00 | 45 | 45
2018-05-14 09:30 | 43 | 43
2018-05-14 10:00 | 43 | 43
2018-05-14 10:30 | 45 | 45
2018-05-14 11:00 | 48 | 47
2018-05-14 11:30 | 48 | 48
2018-05-14 12:00 | 48 | 48
2018-05-14 12:30 | 49 | 49
2018-05-14 13:00 | 50 | 50
2018-05-14 13:30 | 50 | 50
2018-05-14 14:00 | 52 | 52
2018-05-14 14:30 | 54 | 54
2018-05-14 15:00 | 54 | 54
2018-05-14 15:30 | 54 | 54
2018-05-14 16:00 | 58 | 58
2018-05-14 16:30 | 60 | 60
2018-05-14 17:00 | 53 | 53
2018-05-14 17:30 | 70 | 70
2018-05-14 18:00 | 72 | 72
2018-05-14 18:30 | 74 | 74
2018-05-14 19:00 | 74 | 74
2018-05-14 19:30 | 74 | 74
2018-05-14 20:00 | 73 | 73
2018-05-14 20:30 | 72 | 72
2018-05-14 21:00 | 71 | 71
2018-05-14 21:30 | 70 | 70
2018-05-14 22:00 | 69 | 69
2018-05-14 22:30 | 68 | 68
2018-05-14 23:00 | 64 | 64
2018-05-14 23:30 | 64 | 64
2018-05-15 | 64 | 64
2018-05-15 00:30 | 63 | 63
2018-05-15 01:00 | 62 | 62
2018-05-15 01:30 | 63 | 63
2018-05-15 02:00 | 63 | 63
2018-05-15 02:30 | 63 | 63
2018-05-15 03:00 | 63 | 63
2018-05-15 03:30 | 62 | 62
2018-05-15 04:00 | 63 | 62
2018-05-15 04:30 | 62 | 62
2018-05-15 05:00 | 62 | 62
2018-05-15 05:30 | 62 | 62
2018-05-15 06:00 | 62 | 62
2018-05-15 06:30 | 65 | 65
2018-05-15 07:00 | 66 | 66
2018-05-15 07:30 | 66 | 66
2018-05-15 08:00 | 67 | 67
2018-05-15 08:30 | 69 | 69
2018-05-15 09:00 | 66 | 66
2018-05-15 09:30 | 66 | 66
2018-05-15 10:00 | 59 | 59
2018-05-15 10:30 | 51 | 51
2018-05-15 11:00 | 51 | 51
2018-05-15 11:30 | 51 | 51
2018-05-15 12:00 | 52 | 52
2018-05-15 12:30 | 52 | 52
2018-05-15 13:00 | 52 | 52
2018-05-15 13:30 | 52 | 52
2018-05-15 14:00 | 54 | 54
2018-05-15 14:30 | 56 | 56
2018-05-15 15:00 | 57 | 57
2018-05-15 15:30 | 58 | 58
2018-05-15 16:00 | 62 | 62
2018-05-15 16:30 | 65 | 65
2018-05-15 17:00 | 71 | 70
2018-05-15 17:30 | 74 | 74
2018-05-15 18:00 | 70 | 70
2018-05-15 18:30 | 57 | 56
2018-05-15 19:00 | 70 | 70
2018-05-15 19:30 | 75 | 75
2018-05-15 20:00 | 73 | 73
2018-05-15 20:30 | 74 | 71
2018-05-15 21:00 | 72 | 69
2018-05-15 21:30 | 72 | 71
2018-05-15 22:00 | 71 | 70
2018-05-15 22:30 | 70 | 69
2018-05-15 23:00 | 64 | 64
2018-05-15 23:30 | 56 | 56
2018-05-16 | 67 | 67
2018-05-16 00:30 | 67 | 67
2018-05-16 01:00 | 64 | 64
2018-05-16 01:30 | 65 | 64
2018-05-16 02:00 | 62 | 61
2018-05-16 02:30 | 61 | 61
2018-05-16 03:00 | 60 | 60
2018-05-16 03:30 | 61 | 60
2018-05-16 04:00 | 60 | 60
2018-05-16 04:30 | 61 | 61
2018-05-16 05:00 | 61 | 61
2018-05-16 05:30 | 61 | 61
2018-05-16 06:00 | 62 | 62
2018-05-16 06:30 | 62 | 61
2018-05-16 07:00 | 62 | 62
2018-05-16 07:30 | 63 | 62
2018-05-16 08:00 | 55 | 53
2018-05-16 08:30 | 52 | 49
2018-05-16 09:00 | 56 | 55
2018-05-16 09:30 | 58 | 57
2018-05-16 10:00 | 61 | 61
2018-05-16 10:30 | 58 | 57
2018-05-16 11:00 | 56 | 55
2018-05-16 11:30 | 56 | 55
2018-05-16 12:00 | 56 | 55
2018-05-16 12:30 | 57 | 56
2018-05-16 13:00 | 55 | 54
2018-05-16 13:30 | 56 | 55
2018-05-16 14:00 | 61 | 60
2018-05-16 14:30 | 59 | 58
2018-05-16 15:00 | 62 | 61
2018-05-16 15:30 | 61 | 60
2018-05-16 16:00 | 65 | 64
2018-05-16 16:30 | 67 | 66
2018-05-16 17:00 | 67 | 66
2018-05-16 17:30 | 68 | 67
2018-05-16 18:00 | 68 | 67
2018-05-16 18:30 | 67 | 67
2018-05-16 19:00 | 68 | 67
2018-05-16 19:30 | 66 | 66
2018-05-16 20:00 | 66 | 65
2018-05-16 20:30 | 65 | 64
2018-05-16 21:00 | 65 | 64
2018-05-16 21:30 | 65 | 63
2018-05-16 22:00 | 64 | 63
2018-05-16 22:30 | 64 | 62
2018-05-16 23:00 | 63 | 61
2018-05-16 23:30 | 61 | 61
2018-05-17 | 61 | 61
2018-05-17 00:30 | 61 | 61
2018-05-17 01:00 | 60 | 60
2018-05-17 01:30 | 51 | 51
2018-05-17 02:00 | 32 | 26
2018-05-17 02:30 | 34 | 28
2018-05-17 03:00 | 44 | 43
2018-05-17 03:30 | 52 | 52
2018-05-17 04:00 | 57 | 57
2018-05-17 04:30 | 58 | 58
2018-05-17 05:00 | 59 | 58
2018-05-17 05:30 | 60 | 60
2018-05-17 06:00 | 60 | 60
2018-05-17 06:30 | 60 | 60
2018-05-17 07:00 | 61 | 61
2018-05-17 07:30 | 63 | 62
2018-05-17 08:00 | 64 | 63
2018-05-17 08:30 | 63 | 62
2018-05-17 09:00 | 61 | 60
2018-05-17 09:30 | 59 | 58
2018-05-17 10:00 | 57 | 56
2018-05-17 10:30 | 53 | 52
2018-05-17 11:00 | 49 | 48
2018-05-17 11:30 | 48 | 47
2018-05-17 12:00 | 50 | 49
2018-05-17 12:30 | 51 | 50
2018-05-17 13:00 | 52 | 51
2018-05-17 13:30 | 53 | 52
2018-05-17 14:00 | 59 | 58
2018-05-17 14:30 | 61 | 60
2018-05-17 15:00 | 61 | 60
2018-05-17 15:30 | 62 | 61
2018-05-17 16:00 | 64 | 63
2018-05-17 16:30 | 65 | 64
2018-05-17 17:00 | 66 | 66
2018-05-17 17:30 | 68 | 67
2018-05-17 18:00 | 70 | 69
2018-05-17 18:30 | 70 | 69
2018-05-17 19:00 | 70 | 69
2018-05-17 19:30 | 69 | 68
2018-05-17 20:00 | 69 | 69
2018-05-17 20:30 | 68 | 67
2018-05-17 21:00 | 68 | 67
2018-05-17 21:30 | 68 | 66
2018-05-17 22:00 | 67 | 65
2018-05-17 22:30 | 66 | 65
2018-05-17 23:00 | 65 | 63
2018-05-17 23:30 | 54 | 52
2018-05-18 | 62 | 62
2018-05-18 00:30 | 63 | 62
2018-05-18 01:00 | 63 | 63
2018-05-18 01:30 | 63 | 63
2018-05-18 02:00 | 63 | 63
2018-05-18 02:30 | 62 | 62
2018-05-18 03:00 | 63 | 62
2018-05-18 03:30 | 63 | 62
2018-05-18 04:00 | 62 | 62
2018-05-18 04:30 | 62 | 61
2018-05-18 05:00 | 62 | 62
2018-05-18 05:30 | 63 | 62
2018-05-18 06:00 | 64 | 64
2018-05-18 06:30 | 64 | 63
2018-05-18 07:00 | 59 | 58
2018-05-18 07:30 | 64 | 60
2018-05-18 08:00 | 67 | 64
2018-05-18 08:30 | 61 | 57
2018-05-18 09:00 | 64 | 59
2018-05-18 09:30 | 59 | 54
2018-05-18 10:00 | 58 | 53
2018-05-18 10:30 | 57 | 52
2018-05-18 11:00 | 55 | 50
2018-05-18 11:30 | 55 | 50
2018-05-18 12:00 | 56 | 51
2018-05-18 12:30 | 57 | 53
2018-05-18 13:00 | 60 | 55
2018-05-18 13:30 | 59 | 55
2018-05-18 14:00 | 61 | 58
2018-05-18 14:30 | 64 | 61
2018-05-18 15:00 | 60 | 57
2018-05-18 15:30 | 68 | 65
2018-05-18 16:00 | 68 | 65
2018-05-18 16:30 | 58 | 54
2018-05-18 17:00 | 43 | 37
2018-05-18 17:30 | 59 | 58
2018-05-18 18:00 | 68 | 68
2018-05-18 18:30 | 70 | 70
2018-05-18 19:00 | 73 | 72
2018-05-18 19:30 | 76 | 73
2018-05-18 20:00 | 76 | 73
2018-05-18 20:30 | 74 | 72
2018-05-18 21:00 | 73 | 70
2018-05-18 21:30 | 73 | 70
2018-05-18 22:00 | 72 | 69
2018-05-18 22:30 | 71 | 68
2018-05-18 23:00 | 70 | 68
2018-05-18 23:30 | 68 | 66
2018-05-19 | 68 | 66
2018-05-19 00:30 | 67 | 66
2018-05-19 01:00 | 67 | 65
2018-05-19 01:30 | 67 | 65
2018-05-19 02:00 | 66 | 64
2018-05-19 02:30 | 67 | 64
2018-05-19 03:00 | 67 | 65
2018-05-19 03:30 | 66 | 64
2018-05-19 04:00 | 66 | 64
2018-05-19 04:30 | 66 | 64
2018-05-19 05:00 | 67 | 65
2018-05-19 05:30 | 67 | 65
2018-05-19 06:00 | 67 | 65
2018-05-19 06:30 | 66 | 64
2018-05-19 07:00 | 66 | 64
2018-05-19 07:30 | 66 | 64
2018-05-19 08:00 | 64 | 61
2018-05-19 08:30 | 62 | 60
2018-05-19 09:00 | 64 | 59
2018-05-19 09:30 | 62 | 58
2018-05-19 10:00 | 59 | 55
2018-05-19 10:30 | 57 | 54
2018-05-19 11:00 | 51 | 46
2018-05-19 11:30 | 52 | 45
2018-05-19 12:00 | 57 | 52
2018-05-19 12:30 | 61 | 56
2018-05-19 13:00 | 61 | 56
2018-05-19 13:30 | 61 | 56
2018-05-19 14:00 | 63 | 58
2018-05-19 14:30 | 66 | 63
2018-05-19 15:00 | 69 | 66
2018-05-19 15:30 | 70 | 66
2018-05-19 16:00 | 71 | 67
2018-05-19 16:30 | 72 | 68
2018-05-19 17:00 | 72 | 69
2018-05-19 17:30 | 72 | 70
2018-05-19 18:00 | 73 | 70
2018-05-19 18:30 | 72 | 70
2018-05-19 19:00 | 72 | 70
2018-05-19 19:30 | 72 | 69
2018-05-19 20:00 | 71 | 69
2018-05-19 20:30 | 72 | 70
2018-05-19 21:00 | 72 | 69
2018-05-19 21:30 | 69 | 67
2018-05-19 22:00 | 69 | 67
2018-05-19 22:30 | 69 | 67
2018-05-19 23:00 | 69 | 67
2018-05-19 23:30 | 67 | 65
2018-05-20 | 67 | 65
2018-05-20 00:30 | 65 | 64
2018-05-20 01:00 | 64 | 63
2018-05-20 01:30 | 63 | 63
2018-05-20 02:00 | 63 | 63
2018-05-20 02:30 | 62 | 62
2018-05-20 03:00 | 62 | 62
2018-05-20 03:30 | 62 | 62
2018-05-20 04:00 | 63 | 63
2018-05-20 04:30 | 63 | 63
2018-05-20 05:00 | 63 | 63
2018-05-20 05:30 | 63 | 63
2018-05-20 06:00 | 63 | 63
2018-05-20 06:30 | 63 | 63
2018-05-20 07:00 | 63 | 62
2018-05-20 07:30 | 61 | 61
2018-05-20 08:00 | 61 | 61
2018-05-20 08:30 | 62 | 61
2018-05-20 09:00 | 64 | 60
2018-05-20 09:30 | 61 | 57
2018-05-20 10:00 | 60 | 56
2018-05-20 10:30 | 56 | 52
2018-05-20 11:00 | 58 | 54
2018-05-20 11:30 | 60 | 56
2018-05-20 12:00 | 60 | 56
2018-05-20 12:30 | 59 | 55
2018-05-20 13:00 | 59 | 55
2018-05-20 13:30 | 61 | 57
2018-05-20 14:00 | 61 | 57
2018-05-20 14:30 | 62 | 58
2018-05-20 15:00 | 63 | 60
2018-05-20 15:30 | 61 | 55
2018-05-20 16:00 | 69 | 64
2018-05-20 16:30 | 72 | 68
2018-05-20 17:00 | 73 | 69
2018-05-20 17:30 | 73 | 70
2018-05-20 18:00 | 75 | 72
2018-05-20 18:30 | 75 | 72
2018-05-20 19:00 | 75 | 72
2018-05-20 19:30 | 75 | 72
2018-05-20 20:00 | 75 | 72
2018-05-20 20:30 | 74 | 70
2018-05-20 21:00 | 73 | 69
2018-05-20 21:30 | 72 | 67
2018-05-20 22:00 | 71 | 66
2018-05-20 22:30 | 69 | 66
2018-05-20 23:00 | 69 | 66
2018-05-20 23:30 | 66 | 64
2018-05-21 | 66 | 64
2018-05-21 00:30 | 59 | 53
2018-05-21 01:00 | 66 | 63
2018-05-21 01:30 | 66 | 64
2018-05-21 02:00 | 66 | 63
2018-05-21 02:30 | 66 | 63
2018-05-21 03:00 | 66 | 63
2018-05-21 03:30 | 66 | 63
2018-05-21 04:00 | 66 | 63
2018-05-21 04:30 | 67 | 64
2018-05-21 05:00 | 67 | 64
2018-05-21 05:30 | 67 | 64
2018-05-21 06:00 | 67 | 65
2018-05-21 06:30 | 67 | 65
2018-05-21 07:00 | 67 | 65
2018-05-21 07:30 | 67 | 65
2018-05-21 08:00 | 67 | 65
2018-05-21 08:30 | 64 | 61
2018-05-21 09:00 | 63 | 60
2018-05-21 09:30 | 61 | 57
2018-05-21 10:00 | 61 | 57
2018-05-21 10:30 | 61 | 57
2018-05-21 11:00 | 60 | 56
2018-05-21 11:30 | 59 | 55
2018-05-21 12:00 | 60 | 57
2018-05-21 12:30 | 59 | 55
2018-05-21 13:00 | 59 | 55
2018-05-21 13:30 | 60 | 56
2018-05-21 14:00 | 61 | 57
2018-05-21 14:30 | 63 | 60
2018-05-21 15:00 | 65 | 61
2018-05-21 15:30 | 66 | 63
2018-05-21 16:00 | 68 | 65
2018-05-21 16:30 | 72 | 69
2018-05-21 17:00 | 74 | 71
2018-05-21 17:30 | 78 | 76
2018-05-21 18:00 | 79 | 76
2018-05-21 18:30 | 68 | 61
2018-05-21 19:00 | 75 | 72
2018-05-21 19:30 | 76 | 74
2018-05-21 20:00 | 76 | 74
2018-05-21 20:30 | 75 | 73
2018-05-21 21:00 | 75 | 72
2018-05-21 21:30 | 73 | 71
2018-05-21 22:00 | 72 | 70
2018-05-21 22:30 | 71 | 68
2018-05-21 23:00 | 71 | 68
2018-05-21 23:30 | 70 | 67
2018-05-22 | 69 | 66
2018-05-22 00:30 | 67 | 65
2018-05-22 01:00 | 67 | 65
2018-05-22 01:30 | 67 | 64
2018-05-22 02:00 | 66 | 64
2018-05-22 02:30 | 65 | 63
2018-05-22 03:00 | 66 | 64
2018-05-22 03:30 | 66 | 64
2018-05-22 04:00 | 66 | 63
2018-05-22 04:30 | 66 | 63
2018-05-22 05:00 | 67 | 64
2018-05-22 05:30 | 66 | 64
2018-05-22 06:00 | 66 | 64
2018-05-22 06:30 | 65 | 64
2018-05-22 07:00 | 57 | 52
2018-05-22 07:30 | 63 | 61
2018-05-22 08:00 | 64 | 62
2018-05-22 08:30 | 60 | 59
2018-05-22 09:00 | 57 | 56
2018-05-22 09:30 | 57 | 56
2018-05-22 10:00 | 56 | 54
2018-05-22 10:30 | 1 | 0
2018-05-22 11:00 | 51 | 49
2018-05-22 11:30 | 41 | 40
2018-05-22 12:00 | 58 | 55
2018-05-22 12:30 | 59 | 56
2018-05-22 13:00 | 58 | 55
2018-05-22 13:30 | 47 | 44
2018-05-22 14:00 | 57 | 57
2018-05-22 14:30 | 57 | 57
2018-05-22 15:00 | 57 | 57
2018-05-22 15:30 | 57 | 57
2018-05-22 16:00 | 58 | 58
2018-05-22 16:30 | 62 | 62
2018-05-22 17:00 | 67 | 67
2018-05-22 17:30 | 72 | 71
2018-05-22 18:00 | 68 | 64
2018-05-22 18:30 | 75 | 73
2018-05-22 19:00 | 75 | 73
2018-05-22 19:30 | 74 | 72
2018-05-22 20:00 | 75 | 72
2018-05-22 20:30 | 74 | 71
2018-05-22 21:00 | 72 | 70
2018-05-22 21:30 | 71 | 68
2018-05-22 22:00 | 67 | 65
2018-05-22 22:30 | 67 | 65
2018-05-22 23:00 | 66 | 64
2018-05-22 23:30 | 66 | 64
2018-05-23 | 66 | 64
2018-05-23 00:30 | 66 | 63
2018-05-23 01:00 | 66 | 63
2018-05-23 01:30 | 66 | 63
2018-05-23 02:00 | 65 | 63
2018-05-23 02:30 | 65 | 62
2018-05-23 03:00 | 64 | 61
2018-05-23 03:30 | 65 | 61
2018-05-23 04:00 | 65 | 62
2018-05-23 04:30 | 66 | 63
2018-05-23 05:00 | 66 | 63
2018-05-23 05:30 | 66 | 64
2018-05-23 06:00 | 66 | 64
2018-05-23 06:30 | 67 | 63
2018-05-23 07:00 | 55 | 40
2018-05-23 07:30 | 66 | 60
2018-05-23 08:00 | 65 | 61
2018-05-23 08:30 | 62 | 57
2018-05-23 09:00 | 57 | 52
2018-05-23 09:30 | 57 | 52
2018-05-23 10:00 | 57 | 52
2018-05-23 10:30 | 57 | 52
2018-05-23 11:00 | 57 | 52
2018-05-23 11:30 | 58 | 53
2018-05-23 12:00 | 57 | 53
2018-05-23 12:30 | 57 | 53
2018-05-23 13:00 | 57 | 52
2018-05-23 13:30 | 57 | 52
2018-05-23 14:00 | 56 | 52
2018-05-23 14:30 | 57 | 53
2018-05-23 15:00 | 58 | 54
2018-05-23 15:30 | 59 | 55
2018-05-23 16:00 | 61 | 57
2018-05-23 16:30 | 66 | 62
2018-05-23 17:00 | 71 | 67
2018-05-23 17:30 | 72 | 69
2018-05-23 18:00 | 73 | 71
2018-05-23 18:30 | 75 | 73
2018-05-23 19:00 | 75 | 73
2018-05-23 19:30 | 74 | 72
2018-05-23 20:00 | 75 | 73
2018-05-23 20:30 | 74 | 72
2018-05-23 21:00 | 74 | 71
2018-05-23 21:30 | 73 | 70
2018-05-23 22:00 | 72 | 69
2018-05-23 22:30 | 70 | 67
2018-05-23 23:00 | 69 | 66
2018-05-23 23:30 | 67 | 65
2018-05-24 | 67 | 65
2018-05-24 00:30 | 65 | 64
2018-05-24 01:00 | 64 | 64
2018-05-24 01:30 | 64 | 63
2018-05-24 02:00 | 64 | 64
2018-05-24 02:30 | 63 | 63
2018-05-24 03:00 | 53 | 53
2018-05-24 03:30 | 63 | 63
2018-05-24 04:00 | 64 | 63
2018-05-24 04:30 | 64 | 64
2018-05-24 05:00 | 64 | 64
2018-05-24 05:30 | 65 | 65
2018-05-24 06:00 | 65 | 65
2018-05-24 06:30 | 65 | 65
2018-05-24 07:00 | 51 | 51
2018-05-24 07:30 | 64 | 64
2018-05-24 08:00 | 66 | 66
2018-05-24 08:30 | 60 | 60
2018-05-24 09:00 | 58 | 57
2018-05-24 09:30 | 56 | 56
2018-05-24 10:00 | 54 | 53
2018-05-24 10:30 | 53 | 52
2018-05-24 11:00 | 53 | 52
2018-05-24 11:30 | 53 | 53
2018-05-24 12:00 | 53 | 52
2018-05-24 12:30 | 57 | 56
2018-05-24 13:00 | 58 | 57
2018-05-24 13:30 | 53 | 52
2018-05-24 14:00 | 55 | 54
2018-05-24 14:30 | 55 | 55
2018-05-24 15:00 | 58 | 58
2018-05-24 15:30 | 62 | 61
2018-05-24 16:00 | 65 | 65
2018-05-24 16:30 | 67 | 66
2018-05-24 17:00 | 69 | 68
2018-05-24 17:30 | 71 | 70
2018-05-24 18:00 | 73 | 72
2018-05-24 18:30 | 72 | 72
2018-05-24 19:00 | 73 | 73
2018-05-24 19:30 | 73 | 73
2018-05-24 20:00 | 73 | 73
2018-05-24 20:30 | 73 | 72
2018-05-24 21:00 | 72 | 71
2018-05-24 21:30 | 71 | 70
2018-05-24 22:00 | 71 | 69
2018-05-24 22:30 | 70 | 68
2018-05-24 23:00 | 70 | 68
2018-05-24 23:30 | 69 | 67
2018-05-25 | 69 | 67
2018-05-25 00:30 | 67 | 65
2018-05-25 01:00 | 67 | 65
2018-05-25 01:30 | 67 | 65
2018-05-25 02:00 | 67 | 64
2018-05-25 02:30 | 65 | 64
2018-05-25 03:00 | 64 | 64
2018-05-25 03:30 | 64 | 64
2018-05-25 04:00 | 64 | 64
2018-05-25 04:30 | 64 | 64
2018-05-25 05:00 | 65 | 65
2018-05-25 05:30 | 66 | 66
2018-05-25 06:00 | 67 | 66
2018-05-25 06:30 | 67 | 66
2018-05-25 07:00 | 67 | 66
2018-05-25 07:30 | 69 | 69
2018-05-25 08:00 | 69 | 69
2018-05-25 08:30 | 71 | 70
2018-05-25 09:00 | 70 | 69
2018-05-25 09:30 | 68 | 67
2018-05-25 10:00 | 61 | 59
2018-05-25 10:30 | 56 | 55
2018-05-25 11:00 | 54 | 52
2018-05-25 11:30 | 54 | 52
2018-05-25 12:00 | 56 | 55
2018-05-25 12:30 | 56 | 55
2018-05-25 13:00 | 52 | 51
2018-05-25 13:30 | 59 | 58
2018-05-25 14:00 | 61 | 60
2018-05-25 14:30 | 64 | 63
2018-05-25 15:00 | 64 | 63
2018-05-25 15:30 | 64 | 63
2018-05-25 16:00 | 67 | 67
2018-05-25 16:30 | 70 | 70
2018-05-25 17:00 | 73 | 72
2018-05-25 17:30 | 73 | 72
2018-05-25 18:00 | 67 | 64
2018-05-25 18:30 | 74 | 73
2018-05-25 19:00 | 73 | 72
2018-05-25 19:30 | 72 | 71
2018-05-25 20:00 | 72 | 71
2018-05-25 20:30 | 71 | 69
2018-05-25 21:00 | 71 | 69
2018-05-25 21:30 | 70 | 69
2018-05-25 22:00 | 71 | 69
2018-05-25 22:30 | 69 | 67
2018-05-25 23:00 | 68 | 66
2018-05-25 23:30 | 66 | 65
2018-05-26 | 66 | 65
2018-05-26 00:30 | 65 | 65
2018-05-26 01:00 | 65 | 64
2018-05-26 01:30 | 65 | 65
2018-05-26 02:00 | 65 | 65
2018-05-26 02:30 | 64 | 64
2018-05-26 03:00 | 64 | 64
2018-05-26 03:30 | 64 | 64
2018-05-26 04:00 | 64 | 64
2018-05-26 04:30 | 64 | 63
2018-05-26 05:00 | 64 | 64
2018-05-26 05:30 | 65 | 64
2018-05-26 06:00 | 64 | 64
2018-05-26 06:30 | 63 | 62
2018-05-26 07:00 | 64 | 64
2018-05-26 07:30 | 64 | 63
2018-05-26 08:00 | 62 | 62
2018-05-26 08:30 | 60 | 60
2018-05-26 09:00 | 57 | 57
2018-05-26 09:30 | 58 | 57
2018-05-26 10:00 | 75 | 75
2018-05-26 10:30 | 77 | 77
2018-05-26 11:00 | 50 | 50
2018-05-26 11:30 | 50 | 49
2018-05-26 12:00 | 54 | 54
2018-05-26 12:30 | 55 | 55
2018-05-26 13:00 | 56 | 56
2018-05-26 13:30 | 53 | 53
2018-05-26 14:00 | 55 | 55
2018-05-26 14:30 | 55 | 55
2018-05-26 15:00 | 55 | 55
2018-05-26 15:30 | 62 | 62
2018-05-26 16:00 | 59 | 59
2018-05-26 16:30 | 61 | 61
2018-05-26 17:00 | 65 | 65
2018-05-26 17:30 | 69 | 69
2018-05-26 18:00 | 71 | 71
2018-05-26 18:30 | 70 | 70
2018-05-26 19:00 | 71 | 70
2018-05-26 19:30 | 69 | 69
2018-05-26 20:00 | 70 | 69
2018-05-26 20:30 | 68 | 68
2018-05-26 21:00 | 68 | 68
2018-05-26 21:30 | 68 | 68
2018-05-26 22:00 | 68 | 67
2018-05-26 22:30 | 67 | 67
2018-05-26 23:00 | 66 | 65
2018-05-26 23:30 | 65 | 65
2018-05-27 | 65 | 65
2018-05-27 00:30 | 65 | 65
2018-05-27 01:00 | 65 | 65
2018-05-27 01:30 | 64 | 64
2018-05-27 02:00 | 64 | 64
2018-05-27 02:30 | 65 | 65
2018-05-27 03:00 | 64 | 64
2018-05-27 03:30 | 63 | 63
2018-05-27 04:00 | 52 | 52
2018-05-27 04:30 | 60 | 60
2018-05-27 05:00 | 63 | 63
2018-05-27 05:30 | 63 | 63
2018-05-27 06:00 | 63 | 63
2018-05-27 06:30 | 62 | 62
2018-05-27 07:00 | 63 | 63
2018-05-27 07:30 | 62 | 62
2018-05-27 08:00 | 60 | 60
2018-05-27 08:30 | 58 | 58
2018-05-27 09:00 | 55 | 55
2018-05-27 09:30 | 53 | 53
2018-05-27 10:00 | 53 | 53
2018-05-27 10:30 | 52 | 52
2018-05-27 11:00 | 56 | 56
2018-05-27 11:30 | 59 | 59
2018-05-27 12:00 | 60 | 60
2018-05-27 12:30 | 59 | 59
2018-05-27 13:00 | 57 | 57
2018-05-27 13:30 | 61 | 61
2018-05-27 14:00 | 64 | 64
2018-05-27 14:30 | 59 | 59
2018-05-27 15:00 | 59 | 59
2018-05-27 15:30 | 61 | 61
2018-05-27 16:00 | 65 | 65
2018-05-27 16:30 | 70 | 70
2018-05-27 17:00 | 76 | 76
2018-05-27 17:30 | 81 | 81
2018-05-27 18:00 | 84 | 83
2018-05-27 18:30 | 83 | 82
2018-05-27 19:00 | 73 | 73
2018-05-27 19:30 | 73 | 72
2018-05-27 20:00 | 73 | 73
2018-05-27 20:30 | 73 | 72
2018-05-27 21:00 | 72 | 71
2018-05-27 21:30 | 72 | 70
2018-05-27 22:00 | 71 | 70
2018-05-27 22:30 | 69 | 67
2018-05-27 23:00 | 69 | 67
2018-05-27 23:30 | 68 | 66
2018-05-28 | 66 | 66
2018-05-28 00:30 | 65 | 65
2018-05-28 01:00 | 65 | 65
2018-05-28 01:30 | 65 | 65
2018-05-28 02:00 | 65 | 65
2018-05-28 02:30 | 64 | 64
2018-05-28 03:00 | 63 | 63
2018-05-28 03:30 | 64 | 64
2018-05-28 04:00 | 63 | 63
2018-05-28 04:30 | 64 | 64
2018-05-28 05:00 | 64 | 64
2018-05-28 05:30 | 64 | 64
2018-05-28 06:00 | 65 | 65
2018-05-28 06:30 | 67 | 67
2018-05-28 07:00 | 68 | 68
2018-05-28 07:30 | 68 | 68
2018-05-28 08:00 | 69 | 67
2018-05-28 08:30 | 69 | 67
2018-05-28 09:00 | 66 | 64
2018-05-28 09:30 | 66 | 65
2018-05-28 10:00 | 66 | 64
2018-05-28 10:30 | 65 | 63
2018-05-28 11:00 | 63 | 61
2018-05-28 11:30 | 65 | 63
2018-05-28 12:00 | 68 | 66
2018-05-28 12:30 | 69 | 67
2018-05-28 13:00 | 70 | 69
2018-05-28 13:30 | 67 | 65
2018-05-28 14:00 | 67 | 65
2018-05-28 14:30 | 67 | 65
2018-05-28 15:00 | 69 | 67
2018-05-28 15:30 | 71 | 69
2018-05-28 16:00 | 73 | 71
2018-05-28 16:30 | 71 | 69
2018-05-28 17:00 | 69 | 67
2018-05-28 17:30 | 64 | 59
2018-05-28 18:00 | 76 | 75
2018-05-28 18:30 | 77 | 76
2018-05-28 19:00 | 77 | 76
2018-05-28 19:30 | 78 | 77
2018-05-28 20:00 | 78 | 77
2018-05-28 20:30 | 77 | 76
2018-05-28 21:00 | 76 | 74
2018-05-28 21:30 | 74 | 72
2018-05-28 22:00 | 69 | 69
2018-05-28 22:30 | 69 | 69
2018-05-28 23:00 | 67 | 67
2018-05-28 23:30 | 68 | 68
2018-05-29 | 66 | 66
2018-05-29 00:30 | 66 | 66
2018-05-29 01:00 | 66 | 66
2018-05-29 01:30 | 65 | 65
2018-05-29 02:00 | 66 | 66
2018-05-29 02:30 | 65 | 65
2018-05-29 03:00 | 65 | 65
2018-05-29 03:30 | 65 | 65
2018-05-29 04:00 | 65 | 65
2018-05-29 04:30 | 65 | 65
2018-05-29 05:00 | 65 | 65
2018-05-29 05:30 | 66 | 66
2018-05-29 06:00 | 67 | 67
2018-05-29 06:30 | 68 | 68
2018-05-29 07:00 | 69 | 68
2018-05-29 07:30 | 70 | 70
2018-05-29 08:00 | 70 | 68
2018-05-29 08:30 | 67 | 65
2018-05-29 09:00 | 62 | 60
2018-05-29 09:30 | 62 | 60
2018-05-29 10:00 | 61 | 59
2018-05-29 10:30 | 63 | 61
2018-05-29 11:00 | 61 | 59
2018-05-29 11:30 | 62 | 59
2018-05-29 12:00 | 62 | 60
2018-05-29 12:30 | 66 | 64
2018-05-29 13:00 | 65 | 63
2018-05-29 13:30 | 65 | 63
2018-05-29 14:00 | 61 | 59
2018-05-29 14:30 | 62 | 59
2018-05-29 15:00 | 60 | 57
2018-05-29 15:30 | 60 | 57
2018-05-29 16:00 | 63 | 61
2018-05-29 16:30 | 70 | 68
2018-05-29 17:00 | 71 | 69
2018-05-29 17:30 | 75 | 73
2018-05-29 18:00 | 57 | 49
2018-05-29 18:30 | 60 | 55
2018-05-29 19:00 | 61 | 57
2018-05-29 19:30 | 67 | 65
2018-05-29 20:00 | 73 | 72
2018-05-29 20:30 | 72 | 71
2018-05-29 21:00 | 72 | 71
2018-05-29 21:30 | 72 | 71
2018-05-29 22:00 | 71 | 70
2018-05-29 22:30 | 70 | 69
2018-05-29 23:00 | 70 | 69
2018-05-29 23:30 | 69 | 67
2018-05-30 | 68 | 67
2018-05-30 00:30 | 68 | 66
2018-05-30 01:00 | 68 | 66
2018-05-30 01:30 | 68 | 65
2018-05-30 02:00 | 68 | 65
2018-05-30 02:30 | 68 | 65
2018-05-30 03:00 | 67 | 65
2018-05-30 03:30 | 63 | 59
2018-05-30 04:00 | 63 | 63
2018-05-30 04:30 | 65 | 65
2018-05-30 05:00 | 65 | 65
2018-05-30 05:30 | 66 | 66
2018-05-30 06:00 | 66 | 66
2018-05-30 06:30 | 68 | 68
2018-05-30 07:00 | 70 | 69
2018-05-30 07:30 | 70 | 68
2018-05-30 08:00 | 67 | 65
2018-05-30 08:30 | 64 | 62
2018-05-30 09:00 | 60 | 58
2018-05-30 09:30 | 57 | 56
2018-05-30 10:00 | 57 | 55
2018-05-30 10:30 | 56 | 54
2018-05-30 11:00 | 56 | 53
2018-05-30 11:30 | 55 | 53
2018-05-30 12:00 | 48 | 45
2018-05-30 12:30 | 34 | 33
2018-05-30 13:00 | 34 | 34
2018-05-30 13:30 | 34 | 34
2018-05-30 14:00 | 38 | 38
2018-05-30 14:30 | 43 | 43
2018-05-30 15:00 | 66 | 65
2018-05-30 15:30 | 59 | 59
2018-05-30 16:00 | 62 | 62
2018-05-30 16:30 | 65 | 65
2018-05-30 17:00 | 70 | 69
2018-05-30 17:30 | 73 | 72
2018-05-30 18:00 | 75 | 75
2018-05-30 18:30 | 75 | 75
2018-05-30 19:00 | 77 | 76
2018-05-30 19:30 | 76 | 76
2018-05-30 20:00 | 76 | 75
2018-05-30 20:30 | 75 | 75
2018-05-30 21:00 | 75 | 74
2018-05-30 21:30 | 75 | 74
2018-05-30 22:00 | 74 | 72
2018-05-30 22:30 | 72 | 70
2018-05-30 23:00 | 70 | 69
2018-05-30 23:30 | 70 | 69
2018-05-31 | 70 | 68
2018-05-31 00:30 | 70 | 68
2018-05-31 01:00 | 69 | 67
2018-05-31 01:30 | 69 | 67
2018-05-31 02:00 | 68 | 66
2018-05-31 02:30 | 68 | 66
2018-05-31 03:00 | 69 | 66
2018-05-31 03:30 | 68 | 66
2018-05-31 04:00 | 69 | 66
2018-05-31 04:30 | 69 | 66
2018-05-31 05:00 | 69 | 66
2018-05-31 05:30 | 70 | 67
2018-05-31 06:00 | 70 | 68
2018-05-31 06:30 | 70 | 68
2018-05-31 07:00 | 70 | 68
2018-05-31 07:30 | 71 | 69
2018-05-31 08:00 | 70 | 67
2018-05-31 08:30 | 67 | 64
2018-05-31 09:00 | 66 | 62
2018-05-31 09:30 | 62 | 58
2018-05-31 10:00 | 62 | 57
2018-05-31 10:30 | 58 | 57
2018-05-31 11:00 | 55 | 55
2018-05-31 11:30 | 56 | 55
2018-05-31 12:00 | 56 | 56
2018-05-31 12:30 | 56 | 56
2018-05-31 13:00 | 55 | 55
2018-05-31 13:30 | 54 | 54
2018-05-31 14:00 | 57 | 56
2018-05-31 14:30 | 62 | 61
2018-05-31 15:00 | 68 | 67
2018-05-31 15:30 | 70 | 69
2018-05-31 16:00 | 70 | 70
2018-05-31 16:30 | 71 | 71
2018-05-31 17:00 | 72 | 72
2018-05-31 17:30 | 74 | 74
2018-05-31 18:00 | 78 | 78
2018-05-31 18:30 | 79 | 79
2018-05-31 19:00 | 79 | 79
2018-05-31 19:30 | 79 | 79
2018-05-31 20:00 | 75 | 75
2018-05-31 20:30 | 69 | 69
2018-05-31 21:00 | 75 | 75
2018-05-31 21:30 | 73 | 73
2018-05-31 22:00 | 71 | 71
2018-05-31 22:30 | 70 | 70
2018-05-31 23:00 | 70 | 70
2018-05-31 23:30 | 69 | 69
2018-06-01 | 68 | 68
2018-06-01 00:30 | 68 | 68
2018-06-01 01:00 | 67 | 67
2018-06-01 01:30 | 69 | 69
2018-06-01 02:00 | 66 | 66
2018-06-01 02:30 | 66 | 66
2018-06-01 03:00 | 65 | 65
2018-06-01 03:30 | 65 | 65
2018-06-01 04:00 | 65 | 65
2018-06-01 04:30 | 66 | 66
2018-06-01 05:00 | 67 | 67
2018-06-01 05:30 | 68 | 68
2018-06-01 06:00 | 69 | 69
2018-06-01 06:30 | 69 | 69
2018-06-01 07:00 | 71 | 71
2018-06-01 07:30 | 69 | 69
2018-06-01 08:00 | 66 | 66
2018-06-01 08:30 | 64 | 64
2018-06-01 09:00 | 63 | 62
2018-06-01 09:30 | 59 | 59
2018-06-01 10:00 | 56 | 56
2018-06-01 10:30 | 54 | 54
2018-06-01 11:00 | 52 | 52
2018-06-01 11:30 | 52 | 52
2018-06-01 12:00 | 52 | 52
2018-06-01 12:30 | 52 | 52
2018-06-01 13:00 | 52 | 52
2018-06-01 13:30 | 53 | 52
2018-06-01 14:00 | 55 | 55
2018-06-01 14:30 | 55 | 55
2018-06-01 15:00 | 53 | 53
2018-06-01 15:30 | 55 | 55
2018-06-01 16:00 | 57 | 57
2018-06-01 16:30 | 61 | 61
2018-06-01 17:00 | 68 | 68
2018-06-01 17:30 | 73 | 73
2018-06-01 18:00 | 72 | 72
2018-06-01 18:30 | 73 | 73
2018-06-01 19:00 | 74 | 74
2018-06-01 19:30 | 73 | 73
2018-06-01 20:00 | 73 | 73
2018-06-01 20:30 | 73 | 73
2018-06-01 21:00 | 73 | 73
2018-06-01 21:30 | 73 | 72
2018-06-01 22:00 | 72 | 71
2018-06-01 22:30 | 70 | 70
2018-06-01 23:00 | 69 | 69
2018-06-01 23:30 | 67 | 67
2018-06-02 | 66 | 65
2018-06-02 00:30 | 65 | 65
2018-06-02 01:00 | 64 | 64
2018-06-02 01:30 | 65 | 65
2018-06-02 02:00 | 64 | 64
2018-06-02 02:30 | 64 | 64
2018-06-02 03:00 | 63 | 63
2018-06-02 03:30 | 63 | 63
2018-06-02 04:00 | 63 | 63
2018-06-02 04:30 | 63 | 63
2018-06-02 05:00 | 64 | 64
2018-06-02 05:30 | 65 | 65
2018-06-02 06:00 | 65 | 65
2018-06-02 06:30 | 64 | 64
2018-06-02 07:00 | 64 | 64
2018-06-02 07:30 | 62 | 62
2018-06-02 08:00 | 59 | 59
2018-06-02 08:30 | 46 | 45
2018-06-02 09:00 | 50 | 50
2018-06-02 09:30 | 47 | 47
2018-06-02 10:00 | 47 | 47
2018-06-02 10:30 | 46 | 46
2018-06-02 11:00 | 48 | 48
2018-06-02 11:30 | 47 | 47
2018-06-02 12:00 | 47 | 47
2018-06-02 12:30 | 46 | 46
2018-06-02 13:00 | 47 | 47
2018-06-02 13:30 | 47 | 47
2018-06-02 14:00 | 46 | 46
2018-06-02 14:30 | 48 | 47
2018-06-02 15:00 | 48 | 48
2018-06-02 15:30 | 51 | 51
2018-06-02 16:00 | 53 | 53
2018-06-02 16:30 | 57 | 57
2018-06-02 17:00 | 64 | 64
2018-06-02 17:30 | 71 | 70
2018-06-02 18:00 | 73 | 71
2018-06-02 18:30 | 74 | 73
2018-06-02 19:00 | 74 | 73
2018-06-02 19:30 | 74 | 73
2018-06-02 20:00 | 72 | 71
2018-06-02 20:30 | 72 | 71
2018-06-02 21:00 | 71 | 70
2018-06-02 21:30 | 72 | 70
2018-06-02 22:00 | 72 | 70
2018-06-02 22:30 | 69 | 67
2018-06-02 23:00 | 68 | 66
2018-06-02 23:30 | 68 | 66
2018-06-03 | 66 | 66
2018-06-03 00:30 | 64 | 64
2018-06-03 01:00 | 64 | 64
2018-06-03 01:30 | 65 | 65
2018-06-03 02:00 | 65 | 65
2018-06-03 02:30 | 64 | 64
2018-06-03 03:00 | 63 | 63
2018-06-03 03:30 | 63 | 63
2018-06-03 04:00 | 64 | 64
2018-06-03 04:30 | 63 | 63
2018-06-03 05:00 | 64 | 64
2018-06-03 05:30 | 64 | 64
2018-06-03 06:00 | 64 | 64
2018-06-03 06:30 | 63 | 63
2018-06-03 07:00 | 63 | 63
2018-06-03 07:30 | 62 | 62
2018-06-03 08:00 | 57 | 57
2018-06-03 08:30 | 52 | 51
2018-06-03 09:00 | 49 | 49
2018-06-03 09:30 | 47 | 47
2018-06-03 10:00 | 47 | 47
2018-06-03 10:30 | 47 | 46
2018-06-03 11:00 | 46 | 46
2018-06-03 11:30 | 44 | 44
2018-06-03 12:00 | 46 | 45
2018-06-03 12:30 | 45 | 45
2018-06-03 13:00 | 45 | 45
2018-06-03 13:30 | 46 | 46
2018-06-03 14:00 | 46 | 46
2018-06-03 14:30 | 47 | 47
2018-06-03 15:00 | 46 | 46
2018-06-03 15:30 | 47 | 47
2018-06-03 16:00 | 51 | 51
2018-06-03 16:30 | 57 | 57
2018-06-03 17:00 | 63 | 63
2018-06-03 17:30 | 70 | 70
2018-06-03 18:00 | 72 | 72
2018-06-03 18:30 | 75 | 73
2018-06-03 19:00 | 76 | 73
2018-06-03 19:30 | 76 | 73
2018-06-03 20:00 | 75 | 72
2018-06-03 20:30 | 72 | 67
2018-06-03 21:00 | 65 | 64
2018-06-03 21:30 | 70 | 70
2018-06-03 22:00 | 70 | 70
2018-06-03 22:30 | 67 | 67
2018-06-03 23:00 | 65 | 65
2018-06-03 23:30 | 65 | 65
2018-06-04 | 65 | 65
2018-06-04 00:30 | 64 | 64
2018-06-04 01:00 | 65 | 64
2018-06-04 01:30 | 64 | 64
2018-06-04 02:00 | 64 | 64
2018-06-04 02:30 | 63 | 63
2018-06-04 03:00 | 63 | 63
2018-06-04 03:30 | 63 | 63
2018-06-04 04:00 | 62 | 62
2018-06-04 04:30 | 63 | 63
2018-06-04 05:00 | 65 | 65
2018-06-04 05:30 | 65 | 65
2018-06-04 06:00 | 68 | 68
2018-06-04 06:30 | 70 | 70
2018-06-04 07:00 | 69 | 69
2018-06-04 07:30 | 69 | 69
2018-06-04 08:00 | 65 | 64
2018-06-04 08:30 | 61 | 57
2018-06-04 09:00 | 54 | 50
2018-06-04 09:30 | 53 | 50
2018-06-04 10:00 | 53 | 50
2018-06-04 10:30 | 51 | 49
2018-06-04 11:00 | 50 | 49
2018-06-04 11:30 | 51 | 49
2018-06-04 12:00 | 52 | 49
2018-06-04 12:30 | 51 | 48
2018-06-04 13:00 | 52 | 49
2018-06-04 13:30 | 51 | 49
2018-06-04 14:00 | 52 | 49
2018-06-04 14:30 | 51 | 50
2018-06-04 15:00 | 52 | 50
2018-06-04 15:30 | 52 | 50
2018-06-04 16:00 | 56 | 54
2018-06-04 16:30 | 58 | 57
2018-06-04 17:00 | 66 | 64
2018-06-04 17:30 | 73 | 71
2018-06-04 18:00 | 63 | 58
2018-06-04 18:30 | 68 | 65
2018-06-04 19:00 | 76 | 75
2018-06-04 19:30 | 76 | 75
2018-06-04 20:00 | 76 | 75
2018-06-04 20:30 | 76 | 74
2018-06-04 21:00 | 74 | 72
2018-06-04 21:30 | 72 | 70
2018-06-04 22:00 | 72 | 70
2018-06-04 22:30 | 69 | 67
2018-06-04 23:00 | 70 | 68
2018-06-04 23:30 | 67 | 64
2018-06-05 | 67 | 65
2018-06-05 00:30 | 66 | 63
2018-06-05 01:00 | 66 | 63
2018-06-05 01:30 | 67 | 64
2018-06-05 02:00 | 64 | 64
2018-06-05 02:30 | 63 | 63
2018-06-05 03:00 | 63 | 63
2018-06-05 03:30 | 63 | 63
2018-06-05 04:00 | 62 | 62
2018-06-05 04:30 | 62 | 62
2018-06-05 05:00 | 63 | 63
2018-06-05 05:30 | 65 | 65
2018-06-05 06:00 | 66 | 66
2018-06-05 06:30 | 67 | 66
2018-06-05 07:00 | 68 | 66
2018-06-05 07:30 | 63 | 60
2018-06-05 08:00 | 60 | 56
2018-06-05 08:30 | 57 | 54
2018-06-05 09:00 | 54 | 51
2018-06-05 09:30 | 50 | 48
2018-06-05 10:00 | 50 | 47
2018-06-05 10:30 | 49 | 46
2018-06-05 11:00 | 46 | 46
2018-06-05 11:30 | 47 | 46
2018-06-05 12:00 | 48 | 47
2018-06-05 12:30 | 49 | 48
2018-06-05 13:00 | 48 | 48
2018-06-05 13:30 | 48 | 48
2018-06-05 14:00 | 50 | 49
2018-06-05 14:30 | 53 | 52
2018-06-05 15:00 | 54 | 53
2018-06-05 15:30 | 54 | 53
2018-06-05 16:00 | 56 | 55
2018-06-05 16:30 | 58 | 57
2018-06-05 17:00 | 64 | 63
2018-06-05 17:30 | 43 | 40
2018-06-05 18:00 | 60 | 59
2018-06-05 18:30 | 56 | 56
2018-06-05 19:00 | 48 | 47
2018-06-05 19:30 | 53 | 52
2018-06-05 20:00 | 52 | 52
2018-06-05 20:30 | 67 | 67
2018-06-05 21:00 | 70 | 70
2018-06-05 21:30 | 70 | 70
2018-06-05 22:00 | 70 | 69
2018-06-05 22:30 | 69 | 69
2018-06-05 23:00 | 67 | 67
2018-06-05 23:30 | 66 | 66
2018-06-06 | 67 | 66
2018-06-06 00:30 | 66 | 66
2018-06-06 01:00 | 66 | 65
2018-06-06 01:30 | 65 | 65
2018-06-06 02:00 | 65 | 65
2018-06-06 02:30 | 64 | 64
2018-06-06 03:00 | 64 | 64
2018-06-06 03:30 | 64 | 63
2018-06-06 04:00 | 64 | 64
2018-06-06 04:30 | 65 | 64
2018-06-06 05:00 | 65 | 65
2018-06-06 05:30 | 66 | 65
2018-06-06 06:00 | 66 | 65
2018-06-06 06:30 | 68 | 68
2018-06-06 07:00 | 60 | 60
2018-06-06 07:30 | 66 | 66
2018-06-06 08:00 | 45 | 45
2018-06-06 08:30 | 48 | 48
2018-06-06 09:00 | 52 | 52
2018-06-06 09:30 | 49 | 49
2018-06-06 10:00 | 50 | 50
2018-06-06 10:30 | 48 | 48
2018-06-06 11:00 | 48 | 48
2018-06-06 11:30 | 48 | 48
2018-06-06 12:00 | 48 | 48
2018-06-06 12:30 | 48 | 47
2018-06-06 13:00 | 48 | 47
2018-06-06 13:30 | 48 | 48
2018-06-06 14:00 | 48 | 48
2018-06-06 14:30 | 52 | 52
2018-06-06 15:00 | 52 | 51
2018-06-06 15:30 | 54 | 53
2018-06-06 16:00 | 54 | 54
2018-06-06 16:30 | 59 | 59
2018-06-06 17:00 | 67 | 67
2018-06-06 17:30 | 71 | 70
2018-06-06 18:00 | 72 | 72
2018-06-06 18:30 | 74 | 73
2018-06-06 19:00 | 74 | 74
2018-06-06 19:30 | 77 | 76
2018-06-06 20:00 | 76 | 76
2018-06-06 20:30 | 76 | 75
2018-06-06 21:00 | 75 | 74
2018-06-06 21:30 | 74 | 74
2018-06-06 22:00 | 63 | 62
2018-06-06 22:30 | 63 | 63
2018-06-06 23:00 | 69 | 69
2018-06-06 23:30 | 65 | 65
2018-06-07 | 65 | 65
2018-06-07 00:30 | 65 | 65
2018-06-07 01:00 | 64 | 64
2018-06-07 01:30 | 64 | 64
2018-06-07 02:00 | 64 | 64
2018-06-07 02:30 | 63 | 63
2018-06-07 03:00 | 64 | 63
2018-06-07 03:30 | 63 | 63
2018-06-07 04:00 | 64 | 64
2018-06-07 04:30 | 64 | 64
2018-06-07 05:00 | 64 | 64
2018-06-07 05:30 | 65 | 65
2018-06-07 06:00 | 65 | 65
2018-06-07 06:30 | 66 | 65
2018-06-07 07:00 | 66 | 65
2018-06-07 07:30 | 65 | 65
2018-06-07 08:00 | 62 | 62
2018-06-07 08:30 | 56 | 56
2018-06-07 09:00 | 53 | 53
2018-06-07 09:30 | 51 | 51
2018-06-07 10:00 | 49 | 49
2018-06-07 10:30 | 40 | 40
2018-06-07 11:00 | 44 | 43
2018-06-07 11:30 | 48 | 48
2018-06-07 12:00 | 48 | 47
2018-06-07 12:30 | 49 | 48
2018-06-07 13:00 | 48 | 48
2018-06-07 13:30 | 50 | 50
2018-06-07 14:00 | 48 | 48
2018-06-07 14:30 | 49 | 49
2018-06-07 15:00 | 49 | 49
2018-06-07 15:30 | 50 | 50
2018-06-07 16:00 | 53 | 53
2018-06-07 16:30 | 57 | 57
2018-06-07 17:00 | 58 | 57
2018-06-07 17:30 | 49 | 48
2018-06-07 18:00 | 46 | 40
2018-06-07 18:30 | 47 | 41
2018-06-07 19:00 | 45 | 38
2018-06-07 19:30 | 51 | 47
2018-06-07 20:00 | 56 | 54
2018-06-07 20:30 | 70 | 70
2018-06-07 21:00 | 75 | 75
2018-06-07 21:30 | 76 | 76
2018-06-07 22:00 | 75 | 75
2018-06-07 22:30 | 71 | 71
2018-06-07 23:00 | 67 | 67
2018-06-07 23:30 | 66 | 66
2018-06-08 | 65 | 65
2018-06-08 00:30 | 65 | 65
2018-06-08 01:00 | 64 | 63
2018-06-08 01:30 | 64 | 64
2018-06-08 02:00 | 64 | 64
2018-06-08 02:30 | 64 | 64
2018-06-08 03:00 | 63 | 63
2018-06-08 03:30 | 63 | 63
2018-06-08 04:00 | 64 | 64
2018-06-08 04:30 | 63 | 63
2018-06-08 05:00 | 64 | 64
2018-06-08 05:30 | 65 | 65
2018-06-08 06:00 | 65 | 65
2018-06-08 06:30 | 65 | 65
2018-06-08 07:00 | 67 | 67
2018-06-08 07:30 | 67 | 66
2018-06-08 08:00 | 61 | 61
2018-06-08 08:30 | 55 | 55
2018-06-08 09:00 | 52 | 51
2018-06-08 09:30 | 49 | 48
2018-06-08 10:00 | 49 | 48
2018-06-08 10:30 | 48 | 46
2018-06-08 11:00 | 48 | 46
2018-06-08 11:30 | 49 | 48
2018-06-08 12:00 | 50 | 48
2018-06-08 12:30 | 50 | 49
2018-06-08 13:00 | 50 | 49
2018-06-08 13:30 | 50 | 49
2018-06-08 14:00 | 50 | 49
2018-06-08 14:30 | 47 | 46
2018-06-08 15:00 | 55 | 55
2018-06-08 15:30 | 57 | 57
2018-06-08 16:00 | 60 | 60
2018-06-08 16:30 | 62 | 62
2018-06-08 17:00 | 70 | 69
2018-06-08 17:30 | 61 | 61
2018-06-08 18:00 | 57 | 56
2018-06-08 18:30 | 57 | 57
2018-06-08 19:00 | 57 | 56
2018-06-08 19:30 | 73 | 73
2018-06-08 20:00 | 78 | 78
2018-06-08 20:30 | 77 | 77
2018-06-08 21:00 | 77 | 77
2018-06-08 21:30 | 76 | 76
2018-06-08 22:00 | 75 | 75
2018-06-08 22:30 | 74 | 74
2018-06-08 23:00 | 69 | 69
2018-06-08 23:30 | 67 | 67
2018-06-09 | 67 | 66
2018-06-09 00:30 | 65 | 65
2018-06-09 01:00 | 63 | 63
2018-06-09 01:30 | 63 | 63
2018-06-09 02:00 | 64 | 64
2018-06-09 02:30 | 64 | 64
2018-06-09 03:00 | 63 | 63
2018-06-09 03:30 | 63 | 63
2018-06-09 04:00 | 63 | 63
2018-06-09 04:30 | 63 | 63
2018-06-09 05:00 | 63 | 63
2018-06-09 05:30 | 64 | 64
2018-06-09 06:00 | 64 | 64
2018-06-09 06:30 | 64 | 63
2018-06-09 07:00 | 65 | 65
2018-06-09 07:30 | 67 | 67
2018-06-09 08:00 | 67 | 67
2018-06-09 08:30 | 68 | 67
2018-06-09 09:00 | 65 | 65
2018-06-09 09:30 | 62 | 62
2018-06-09 10:00 | 63 | 63
2018-06-09 10:30 | 60 | 60
2018-06-09 11:00 | 56 | 56
2018-06-09 11:30 | 53 | 53
2018-06-09 12:00 | 52 | 52
2018-06-09 12:30 | 50 | 50
2018-06-09 13:00 | 56 | 56
2018-06-09 13:30 | 60 | 60
2018-06-09 14:00 | 58 | 57
2018-06-09 14:30 | 54 | 54
2018-06-09 15:00 | 56 | 56
2018-06-09 15:30 | 57 | 57
2018-06-09 16:00 | 56 | 56
2018-06-09 16:30 | 63 | 63
2018-06-09 17:00 | 71 | 71
2018-06-09 17:30 | 76 | 76
2018-06-09 18:00 | 77 | 77
2018-06-09 18:30 | 79 | 78
2018-06-09 19:00 | 79 | 78
2018-06-09 19:30 | 78 | 78
2018-06-09 20:00 | 78 | 77
2018-06-09 20:30 | 78 | 77
2018-06-09 21:00 | 77 | 77
2018-06-09 21:30 | 77 | 76
2018-06-09 22:00 | 77 | 77
2018-06-09 22:30 | 75 | 74
2018-06-09 23:00 | 73 | 73
2018-06-09 23:30 | 72 | 72
2018-06-10 | 66 | 66
2018-06-10 00:30 | 53 | 53
2018-06-10 01:00 | 64 | 64
2018-06-10 01:30 | 63 | 63
2018-06-10 02:00 | 63 | 63
2018-06-10 02:30 | 64 | 63
2018-06-10 03:00 | 63 | 63
2018-06-10 03:30 | 63 | 63
2018-06-10 04:00 | 63 | 62
2018-06-10 04:30 | 62 | 62
2018-06-10 05:00 | 62 | 62
2018-06-10 05:30 | 62 | 62
2018-06-10 06:00 | 63 | 63
2018-06-10 06:30 | 64 | 63
2018-06-10 07:00 | 64 | 64
2018-06-10 07:30 | 62 | 62
2018-06-10 08:00 | 55 | 55
2018-06-10 08:30 | 49 | 49
2018-06-10 09:00 | 47 | 46
2018-06-10 09:30 | 46 | 45
2018-06-10 10:00 | 45 | 45
2018-06-10 10:30 | 46 | 45
2018-06-10 11:00 | 45 | 45
2018-06-10 11:30 | 48 | 48
2018-06-10 12:00 | 48 | 48
2018-06-10 12:30 | 48 | 48
2018-06-10 13:00 | 48 | 48
2018-06-10 13:30 | 47 | 47
2018-06-10 14:00 | 46 | 46
2018-06-10 14:30 | 48 | 48
2018-06-10 15:00 | 50 | 50
2018-06-10 15:30 | 49 | 49
2018-06-10 16:00 | 52 | 52
2018-06-10 16:30 | 57 | 57
2018-06-10 17:00 | 64 | 64
2018-06-10 17:30 | 69 | 69
2018-06-10 18:00 | 72 | 71
2018-06-10 18:30 | 74 | 73
2018-06-10 19:00 | 74 | 73
2018-06-10 19:30 | 74 | 73
2018-06-10 20:00 | 74 | 72
2018-06-10 20:30 | 74 | 72
2018-06-10 21:00 | 73 | 72
2018-06-10 21:30 | 73 | 71
2018-06-10 22:00 | 72 | 70
2018-06-10 22:30 | 70 | 68
2018-06-10 23:00 | 69 | 66
2018-06-10 23:30 | 67 | 65
2018-06-11 | 64 | 64
2018-06-11 00:30 | 65 | 65
2018-06-11 01:00 | 65 | 65
2018-06-11 01:30 | 64 | 64
2018-06-11 02:00 | 64 | 64
2018-06-11 02:30 | 64 | 64
2018-06-11 03:00 | 64 | 64
2018-06-11 03:30 | 63 | 63
2018-06-11 04:00 | 63 | 63
2018-06-11 04:30 | 63 | 63
2018-06-11 05:00 | 64 | 64
2018-06-11 05:30 | 65 | 65
2018-06-11 06:00 | 65 | 65
2018-06-11 06:30 | 66 | 66
2018-06-11 07:00 | 68 | 67
2018-06-11 07:30 | 68 | 68
2018-06-11 08:00 | 64 | 64
2018-06-11 08:30 | 55 | 54
2018-06-11 09:00 | 52 | 51
2018-06-11 09:30 | 53 | 53
2018-06-11 10:00 | 50 | 50
2018-06-11 10:30 | 50 | 50
2018-06-11 11:00 | 51 | 50
2018-06-11 11:30 | 51 | 50
2018-06-11 12:00 | 51 | 50
2018-06-11 12:30 | 51 | 50
2018-06-11 13:00 | 53 | 52
2018-06-11 13:30 | 54 | 53
2018-06-11 14:00 | 55 | 54
2018-06-11 14:30 | 55 | 55
2018-06-11 15:00 | 55 | 55
2018-06-11 15:30 | 56 | 55
2018-06-11 16:00 | 60 | 59
2018-06-11 16:30 | 65 | 65
2018-06-11 17:00 | 73 | 72
2018-06-11 17:30 | 78 | 77
2018-06-11 18:00 | 81 | 80
2018-06-11 18:30 | 81 | 80
2018-06-11 19:00 | 82 | 81
2018-06-11 19:30 | 82 | 81
2018-06-11 20:00 | 82 | 80
2018-06-11 20:30 | 82 | 80
2018-06-11 21:00 | 81 | 79
2018-06-11 21:30 | 80 | 78
2018-06-11 22:00 | 80 | 77
2018-06-11 22:30 | 77 | 74
2018-06-11 23:00 | 75 | 71
2018-06-11 23:30 | 71 | 70
2018-06-12 | 69 | 69
2018-06-12 00:30 | 68 | 68
2018-06-12 01:00 | 68 | 68
2018-06-12 01:30 | 68 | 68
2018-06-12 02:00 | 67 | 67
2018-06-12 02:30 | 67 | 67
2018-06-12 03:00 | 68 | 67
2018-06-12 03:30 | 67 | 67
2018-06-12 04:00 | 67 | 67
2018-06-12 04:30 | 66 | 66
2018-06-12 05:00 | 66 | 66
2018-06-12 05:30 | 68 | 68
2018-06-12 06:00 | 68 | 68
2018-06-12 06:30 | 69 | 69
2018-06-12 07:00 | 70 | 70
2018-06-12 07:30 | 70 | 70
2018-06-12 08:00 | 67 | 67
2018-06-12 08:30 | 64 | 64
2018-06-12 09:00 | 58 | 58
2018-06-12 09:30 | 55 | 55
2018-06-12 10:00 | 52 | 52
2018-06-12 10:30 | 53 | 53
2018-06-12 11:00 | 53 | 53
2018-06-12 11:30 | 54 | 53
2018-06-12 12:00 | 56 | 55
2018-06-12 12:30 | 58 | 57
2018-06-12 13:00 | 57 | 56
2018-06-12 13:30 | 36 | 36
2018-06-12 14:00 | 37 | 37
2018-06-12 14:30 | 41 | 41
2018-06-12 15:00 | 60 | 60
2018-06-12 15:30 | 62 | 62
2018-06-12 16:00 | 65 | 65
2018-06-12 16:30 | 62 | 62
2018-06-12 17:00 | 68 | 68
2018-06-12 17:30 | 74 | 73
2018-06-12 18:00 | 80 | 78
2018-06-12 18:30 | 83 | 81
2018-06-12 19:00 | 81 | 80
2018-06-12 19:30 | 80 | 78
2018-06-12 20:00 | 80 | 79
2018-06-12 20:30 | 78 | 77
2018-06-12 21:00 | 76 | 74
2018-06-12 21:30 | 58 | 56
2018-06-12 22:00 | 71 | 71
2018-06-12 22:30 | 69 | 69
2018-06-12 23:00 | 68 | 67
2018-06-12 23:30 | 67 | 66
2018-06-13 | 66 | 65
2018-06-13 00:30 | 65 | 65
2018-06-13 01:00 | 64 | 63
2018-06-13 01:30 | 64 | 63
2018-06-13 02:00 | 63 | 62
2018-06-13 02:30 | 64 | 64
2018-06-13 03:00 | 64 | 64
2018-06-13 03:30 | 64 | 64
2018-06-13 04:00 | 65 | 65
2018-06-13 04:30 | 64 | 64
2018-06-13 05:00 | 64 | 63
2018-06-13 05:30 | 64 | 63
2018-06-13 06:00 | 65 | 64
2018-06-13 06:30 | 67 | 67
2018-06-13 07:00 | 69 | 69
2018-06-13 07:30 | 71 | 71
2018-06-13 08:00 | 70 | 70
2018-06-13 08:30 | 63 | 62
2018-06-13 09:00 | 59 | 58
2018-06-13 09:30 | 53 | 52
2018-06-13 10:00 | 54 | 53
2018-06-13 10:30 | 54 | 53
2018-06-13 11:00 | 51 | 50
2018-06-13 11:30 | 50 | 48
2018-06-13 12:00 | 51 | 50
2018-06-13 12:30 | 49 | 48
2018-06-13 13:00 | 51 | 49
2018-06-13 13:30 | 51 | 50
2018-06-13 14:00 | 51 | 49
2018-06-13 14:30 | 54 | 52
2018-06-13 15:00 | 52 | 50
2018-06-13 15:30 | 52 | 51
2018-06-13 16:00 | 53 | 52
2018-06-13 16:30 | 59 | 58
2018-06-13 17:00 | 65 | 64
2018-06-13 17:30 | 70 | 69
2018-06-13 18:00 | 74 | 73
2018-06-13 18:30 | 74 | 73
2018-06-13 19:00 | 73 | 72
2018-06-13 19:30 | 71 | 70
2018-06-13 20:00 | 70 | 69
2018-06-13 20:30 | 69 | 67
2018-06-13 21:00 | 68 | 66
2018-06-13 21:30 | 68 | 65
2018-06-13 22:00 | 68 | 65
2018-06-13 22:30 | 64 | 62
2018-06-13 23:00 | 62 | 60
2018-06-13 23:30 | 61 | 60
2018-06-14 | 58 | 58
2018-06-14 00:30 | 57 | 56
2018-06-14 01:00 | 57 | 56
2018-06-14 01:30 | 56 | 55
2018-06-14 02:00 | 55 | 54
2018-06-14 02:30 | 56 | 55
2018-06-14 03:00 | 56 | 56
2018-06-14 03:30 | 56 | 56
2018-06-14 04:00 | 54 | 53
2018-06-14 04:30 | 54 | 54
2018-06-14 05:00 | 54 | 54
2018-06-14 05:30 | 46 | 46
2018-06-14 06:00 | 34 | 32
2018-06-14 06:30 | 31 | 23
2018-06-14 07:00 | 34 | 26
2018-06-14 07:30 | 32 | 25
2018-06-14 08:00 | 29 | 23
2018-06-14 08:30 | 27 | 20
2018-06-14 09:00 | 25 | 18
2018-06-14 09:30 | 22 | 15
2018-06-14 10:00 | 21 | 13
2018-06-14 10:30 | 21 | 12
2018-06-14 11:00 | 24 | 15
2018-06-14 11:30 | 25 | 17
2018-06-14 12:00 | 24 | 17
2018-06-14 12:30 | 24 | 17
2018-06-14 13:00 | 26 | 18
2018-06-14 13:30 | 29 | 23
2018-06-14 14:00 | 32 | 28
2018-06-14 14:30 | 34 | 30
2018-06-14 15:00 | 33 | 29
2018-06-14 15:30 | 33 | 30
2018-06-14 16:00 | 35 | 32
2018-06-14 16:30 | 34 | 31
2018-06-14 17:00 | 39 | 36
2018-06-14 17:30 | 42 | 39
2018-06-14 18:00 | 43 | 41
2018-06-14 18:30 | 44 | 42
2018-06-14 19:00 | 42 | 39
2018-06-14 19:30 | 42 | 39
2018-06-14 20:00 | 47 | 46
2018-06-14 20:30 | 65 | 65
2018-06-14 21:00 | 66 | 66
2018-06-14 21:30 | 68 | 68
2018-06-14 22:00 | 68 | 68
2018-06-14 22:30 | 67 | 67
2018-06-14 23:00 | 68 | 68
2018-06-14 23:30 | 67 | 67
2018-06-15 | 67 | 67
2018-06-15 00:30 | 60 | 60
2018-06-15 01:00 | 58 | 57
2018-06-15 01:30 | 66 | 66
2018-06-15 02:00 | 66 | 66
2018-06-15 02:30 | 66 | 66
2018-06-15 03:00 | 66 | 66
2018-06-15 03:30 | 66 | 66
2018-06-15 04:00 | 66 | 66
2018-06-15 04:30 | 66 | 66
2018-06-15 05:00 | 68 | 68
2018-06-15 05:30 | 69 | 69
2018-06-15 06:00 | 69 | 69
2018-06-15 06:30 | 70 | 70
2018-06-15 07:00 | 73 | 71
2018-06-15 07:30 | 72 | 70
2018-06-15 08:00 | 65 | 63
2018-06-15 08:30 | 59 | 57
2018-06-15 09:00 | 55 | 53
2018-06-15 09:30 | 55 | 52
2018-06-15 10:00 | 54 | 51
2018-06-15 10:30 | 53 | 51
2018-06-15 11:00 | 51 | 50
2018-06-15 11:30 | 49 | 48
2018-06-15 12:00 | 50 | 49
2018-06-15 12:30 | 54 | 52
2018-06-15 13:00 | 52 | 51
2018-06-15 13:30 | 53 | 52
2018-06-15 14:00 | 55 | 54
2018-06-15 14:30 | 55 | 53
2018-06-15 15:00 | 53 | 52
2018-06-15 15:30 | 56 | 54
2018-06-15 16:00 | 59 | 58
2018-06-15 16:30 | 60 | 58
2018-06-15 17:00 | 68 | 67
2018-06-15 17:30 | 73 | 72
2018-06-15 18:00 | 74 | 74
2018-06-15 18:30 | 74 | 73
2018-06-15 19:00 | 75 | 74
2018-06-15 19:30 | 75 | 74
2018-06-15 20:00 | 72 | 71
2018-06-15 20:30 | 73 | 72
2018-06-15 21:00 | 73 | 72
2018-06-15 21:30 | 72 | 71
2018-06-15 22:00 | 70 | 68
2018-06-15 22:30 | 70 | 68
2018-06-15 23:00 | 69 | 67
2018-06-15 23:30 | 67 | 65
2018-06-16 | 67 | 65
2018-06-16 00:30 | 65 | 64
2018-06-16 01:00 | 66 | 66
2018-06-16 01:30 | 65 | 65
2018-06-16 02:00 | 63 | 63
2018-06-16 02:30 | 64 | 64
2018-06-16 03:00 | 63 | 63
2018-06-16 03:30 | 63 | 63
2018-06-16 04:00 | 63 | 63
2018-06-16 04:30 | 64 | 63
2018-06-16 05:00 | 64 | 64
2018-06-16 05:30 | 63 | 63
2018-06-16 06:00 | 62 | 62
2018-06-16 06:30 | 64 | 64
2018-06-16 07:00 | 64 | 63
2018-06-16 07:30 | 64 | 64
2018-06-16 08:00 | 63 | 62
2018-06-16 08:30 | 62 | 61
2018-06-16 09:00 | 56 | 56
2018-06-16 09:30 | 42 | 42
2018-06-16 10:00 | 58 | 57
2018-06-16 10:30 | 57 | 56
2018-06-16 11:00 | 55 | 54
2018-06-16 11:30 | 51 | 51
2018-06-16 12:00 | 50 | 50
2018-06-16 12:30 | 45 | 44
2018-06-16 13:00 | 40 | 40
2018-06-16 13:30 | 45 | 44
2018-06-16 14:00 | 50 | 50
2018-06-16 14:30 | 52 | 52
2018-06-16 15:00 | 47 | 47
2018-06-16 15:30 | 47 | 47
2018-06-16 16:00 | 49 | 49
2018-06-16 16:30 | 51 | 51
2018-06-16 17:00 | 58 | 57
2018-06-16 17:30 | 65 | 64
2018-06-16 18:00 | 66 | 65
2018-06-16 18:30 | 65 | 64
2018-06-16 19:00 | 64 | 63
2018-06-16 19:30 | 63 | 62
2018-06-16 20:00 | 63 | 62
2018-06-16 20:30 | 63 | 61
2018-06-16 21:00 | 62 | 60
2018-06-16 21:30 | 62 | 59
2018-06-16 22:00 | 62 | 59
2018-06-16 22:30 | 60 | 57
2018-06-16 23:00 | 58 | 55
2018-06-16 23:30 | 59 | 56
2018-06-17 | 57 | 54
2018-06-17 00:30 | 57 | 53
2018-06-17 01:00 | 54 | 52
2018-06-17 01:30 | 52 | 52
2018-06-17 02:00 | 53 | 53
2018-06-17 02:30 | 52 | 52
2018-06-17 03:00 | 52 | 52
2018-06-17 03:30 | 51 | 51
2018-06-17 04:00 | 51 | 51
2018-06-17 04:30 | 53 | 53
2018-06-17 05:00 | 52 | 52
2018-06-17 05:30 | 52 | 52
2018-06-17 06:00 | 51 | 51
2018-06-17 06:30 | 52 | 52
2018-06-17 07:00 | 53 | 53
2018-06-17 07:30 | 52 | 52
2018-06-17 08:00 | 49 | 49
2018-06-17 08:30 | 50 | 50
2018-06-17 09:00 | 48 | 47
2018-06-17 09:30 | 46 | 46
2018-06-17 10:00 | 43 | 43
2018-06-17 10:30 | 43 | 42
2018-06-17 11:00 | 37 | 36
2018-06-17 11:30 | 37 | 37
2018-06-17 12:00 | 38 | 38
2018-06-17 12:30 | 39 | 38
2018-06-17 13:00 | 39 | 39
2018-06-17 13:30 | 41 | 41
2018-06-17 14:00 | 44 | 43
2018-06-17 14:30 | 47 | 46
2018-06-17 15:00 | 45 | 45
2018-06-17 15:30 | 50 | 49
2018-06-17 16:00 | 47 | 47
2018-06-17 16:30 | 54 | 53
2018-06-17 17:00 | 58 | 58
2018-06-17 17:30 | 72 | 71
2018-06-17 18:00 | 74 | 74
2018-06-17 18:30 | 77 | 76
2018-06-17 19:00 | 70 | 67
2018-06-17 19:30 | 77 | 75
2018-06-17 20:00 | 76 | 75
2018-06-17 20:30 | 75 | 74
2018-06-17 21:00 | 75 | 73
2018-06-17 21:30 | 72 | 70
2018-06-17 22:00 | 72 | 70
2018-06-17 22:30 | 71 | 69
2018-06-17 23:00 | 67 | 64
2018-06-17 23:30 | 65 | 62
2018-06-18 | 66 | 63
2018-06-18 00:30 | 65 | 62
2018-06-18 01:00 | 63 | 63
2018-06-18 01:30 | 61 | 61
2018-06-18 02:00 | 63 | 63
2018-06-18 02:30 | 62 | 62
2018-06-18 03:00 | 61 | 61
2018-06-18 03:30 | 61 | 61
2018-06-18 04:00 | 61 | 61
2018-06-18 04:30 | 61 | 61
2018-06-18 05:00 | 62 | 62
2018-06-18 05:30 | 63 | 63
2018-06-18 06:00 | 61 | 61
2018-06-18 06:30 | 51 | 51
2018-06-18 07:00 | 32 | 30
2018-06-18 07:30 | 32 | 29
2018-06-18 08:00 | 31 | 24
2018-06-18 08:30 | 35 | 28
2018-06-18 09:00 | 33 | 32
2018-06-18 09:30 | 41 | 40
2018-06-18 10:00 | 38 | 38
2018-06-18 10:30 | 37 | 37
2018-06-18 11:00 | 38 | 38
2018-06-18 11:30 | 38 | 38
2018-06-18 12:00 | 38 | 38
2018-06-18 12:30 | 38 | 37
2018-06-18 13:00 | 38 | 37
2018-06-18 13:30 | 38 | 37
2018-06-18 14:00 | 44 | 44
2018-06-18 14:30 | 49 | 49
2018-06-18 15:00 | 50 | 50
2018-06-18 15:30 | 51 | 51
2018-06-18 16:00 | 54 | 54
2018-06-18 16:30 | 57 | 56
2018-06-18 17:00 | 64 | 63
2018-06-18 17:30 | 73 | 72
2018-06-18 18:00 | 67 | 63
2018-06-18 18:30 | 62 | 54
2018-06-18 19:00 | 70 | 66
2018-06-18 19:30 | 78 | 77
2018-06-18 20:00 | 76 | 75
2018-06-18 20:30 | 79 | 78
2018-06-18 21:00 | 75 | 74
2018-06-18 21:30 | 73 | 71
2018-06-18 22:00 | 71 | 70
2018-06-18 22:30 | 69 | 67
2018-06-18 23:00 | 67 | 65
2018-06-18 23:30 | 65 | 64
2018-06-19 | 63 | 63
2018-06-19 00:30 | 62 | 62
2018-06-19 01:00 | 62 | 62
2018-06-19 01:30 | 62 | 61
2018-06-19 02:00 | 61 | 61
2018-06-19 02:30 | 60 | 60
2018-06-19 03:00 | 61 | 61
2018-06-19 03:30 | 61 | 61
2018-06-19 04:00 | 61 | 61
2018-06-19 04:30 | 61 | 61
2018-06-19 05:00 | 62 | 62
2018-06-19 05:30 | 58 | 58
2018-06-19 06:00 | 56 | 56
2018-06-19 06:30 | 59 | 59
2018-06-19 07:00 | 21 | 16
2018-06-19 07:30 | 18 | 13
2018-06-19 08:00 | 42 | 42
2018-06-19 08:30 | 45 | 45
2018-06-19 09:00 | 39 | 39
2018-06-19 09:30 | 38 | 38
2018-06-19 10:00 | 39 | 38
2018-06-19 10:30 | 38 | 38
2018-06-19 11:00 | 37 | 36
2018-06-19 11:30 | 37 | 36
2018-06-19 12:00 | 36 | 35
2018-06-19 12:30 | 36 | 35
2018-06-19 13:00 | 37 | 37
2018-06-19 13:30 | 39 | 38
2018-06-19 14:00 | 40 | 40
2018-06-19 14:30 | 40 | 40
2018-06-19 15:00 | 43 | 43
2018-06-19 15:30 | 45 | 44
2018-06-19 16:00 | 45 | 45
2018-06-19 16:30 | 44 | 43
2018-06-19 17:00 | 53 | 53
2018-06-19 17:30 | 67 | 67
2018-06-19 18:00 | 56 | 48
2018-06-19 18:30 | 53 | 37
2018-06-19 19:00 | 62 | 58
2018-06-19 19:30 | 64 | 62
2018-06-19 20:00 | 64 | 62
2018-06-19 20:30 | 65 | 63
2018-06-19 21:00 | 64 | 62
2018-06-19 21:30 | 64 | 61
2018-06-19 22:00 | 62 | 59
2018-06-19 22:30 | 61 | 58
2018-06-19 23:00 | 59 | 56
2018-06-19 23:30 | 58 | 55
2018-06-20 | 54 | 54
2018-06-20 00:30 | 54 | 54
2018-06-20 01:00 | 54 | 54
2018-06-20 01:30 | 54 | 53
2018-06-20 02:00 | 54 | 54
2018-06-20 02:30 | 54 | 54
2018-06-20 03:00 | 53 | 53
2018-06-20 03:30 | 54 | 54
2018-06-20 04:00 | 54 | 54
2018-06-20 04:30 | 55 | 55
2018-06-20 05:00 | 55 | 55
2018-06-20 05:30 | 56 | 56
2018-06-20 06:00 | 57 | 56
2018-06-20 06:30 | 58 | 57
2018-06-20 07:00 | 60 | 59
2018-06-20 07:30 | 59 | 58
2018-06-20 08:00 | 53 | 52
2018-06-20 08:30 | 45 | 43
2018-06-20 09:00 | 42 | 40
2018-06-20 09:30 | 43 | 42
2018-06-20 10:00 | 41 | 40
2018-06-20 10:30 | 41 | 39
2018-06-20 11:00 | 38 | 36
2018-06-20 11:30 | 39 | 37
2018-06-20 12:00 | 38 | 36
2018-06-20 12:30 | 40 | 38
2018-06-20 13:00 | 39 | 37
2018-06-20 13:30 | 38 | 36
2018-06-20 14:00 | 39 | 37
2018-06-20 14:30 | 40 | 38
2018-06-20 15:00 | 41 | 39
2018-06-20 15:30 | 40 | 38
2018-06-20 16:00 | 41 | 39
2018-06-20 16:30 | 43 | 41
2018-06-20 17:00 | 51 | 49
2018-06-20 17:30 | 60 | 59
2018-06-20 18:00 | 64 | 63
2018-06-20 18:30 | 65 | 64
2018-06-20 19:00 | 66 | 65
2018-06-20 19:30 | 66 | 65
2018-06-20 20:00 | 65 | 64
2018-06-20 20:30 | 57 | 55
2018-06-20 21:00 | 58 | 58
2018-06-20 21:30 | 63 | 62
2018-06-20 22:00 | 60 | 60
2018-06-20 22:30 | 57 | 57
2018-06-20 23:00 | 56 | 56
2018-06-20 23:30 | 56 | 56
2018-06-21 | 55 | 55
2018-06-21 00:30 | 55 | 55
2018-06-21 01:00 | 56 | 56
2018-06-21 01:30 | 56 | 55
2018-06-21 02:00 | 55 | 55
2018-06-21 02:30 | 55 | 55
2018-06-21 03:00 | 55 | 55
2018-06-21 03:30 | 57 | 57
2018-06-21 04:00 | 59 | 59
2018-06-21 04:30 | 59 | 59
2018-06-21 05:00 | 58 | 58
2018-06-21 05:30 | 58 | 58
2018-06-21 06:00 | 60 | 59
2018-06-21 06:30 | 62 | 61
2018-06-21 07:00 | 49 | 49
2018-06-21 07:30 | 56 | 56
2018-06-21 08:00 | 50 | 50
2018-06-21 08:30 | 46 | 46
2018-06-21 09:00 | 46 | 46
2018-06-21 09:30 | 45 | 45
2018-06-21 10:00 | 44 | 44
2018-06-21 10:30 | 41 | 41
2018-06-21 11:00 | 39 | 38
2018-06-21 11:30 | 37 | 37
2018-06-21 12:00 | 38 | 38
2018-06-21 12:30 | 38 | 38
2018-06-21 13:00 | 40 | 40
2018-06-21 13:30 | 42 | 42
2018-06-21 14:00 | 45 | 45
2018-06-21 14:30 | 45 | 45
2018-06-21 15:00 | 45 | 45
2018-06-21 15:30 | 45 | 45
2018-06-21 16:00 | 45 | 44
2018-06-21 16:30 | 43 | 43
2018-06-21 17:00 | 51 | 51
2018-06-21 17:30 | 60 | 60
2018-06-21 18:00 | 65 | 65
2018-06-21 18:30 | 68 | 68
2018-06-21 19:00 | 68 | 68
2018-06-21 19:30 | 66 | 66
2018-06-21 20:00 | 65 | 65
2018-06-21 20:30 | 64 | 64
2018-06-21 21:00 | 65 | 64
2018-06-21 21:30 | 63 | 63
2018-06-21 22:00 | 63 | 63
2018-06-21 22:30 | 60 | 60
2018-06-21 23:00 | 59 | 59
2018-06-21 23:30 | 58 | 57
2018-06-22 | 56 | 56
2018-06-22 00:30 | 55 | 54
2018-06-22 01:00 | 57 | 57
2018-06-22 01:30 | 55 | 54
2018-06-22 02:00 | 55 | 54
2018-06-22 02:30 | 53 | 53
2018-06-22 03:00 | 56 | 56
2018-06-22 03:30 | 56 | 56
2018-06-22 04:00 | 55 | 55
2018-06-22 04:30 | 58 | 58
2018-06-22 05:00 | 58 | 58
2018-06-22 05:30 | 46 | 45
2018-06-22 06:00 | 56 | 56
2018-06-22 06:30 | 57 | 57
2018-06-22 07:00 | 56 | 56
2018-06-22 07:30 | 50 | 50
2018-06-22 08:00 | 48 | 48
2018-06-22 08:30 | 39 | 39
2018-06-22 09:00 | 39 | 39
2018-06-22 09:30 | 38 | 38
2018-06-22 10:00 | 38 | 38
2018-06-22 10:30 | 39 | 38
2018-06-22 11:00 | 37 | 37
2018-06-22 11:30 | 38 | 38
2018-06-22 12:00 | 39 | 38
2018-06-22 12:30 | 40 | 39
2018-06-22 13:00 | 41 | 40
2018-06-22 13:30 | 41 | 39
2018-06-22 14:00 | 41 | 40
2018-06-22 14:30 | 43 | 42
2018-06-22 15:00 | 43 | 41
2018-06-22 15:30 | 46 | 44
2018-06-22 16:00 | 46 | 45
2018-06-22 16:30 | 44 | 43
2018-06-22 17:00 | 50 | 49
2018-06-22 17:30 | 62 | 61
2018-06-22 18:00 | 63 | 62
2018-06-22 18:30 | 64 | 63
2018-06-22 19:00 | 63 | 62
2018-06-22 19:30 | 62 | 61
2018-06-22 20:00 | 62 | 61
2018-06-22 20:30 | 63 | 62
2018-06-22 21:00 | 62 | 62
2018-06-22 21:30 | 61 | 60
2018-06-22 22:00 | 60 | 59
2018-06-22 22:30 | 57 | 57
2018-06-22 23:00 | 57 | 56
2018-06-22 23:30 | 55 | 55
2018-06-23 | 54 | 53
2018-06-23 00:30 | 55 | 55
2018-06-23 01:00 | 53 | 53
2018-06-23 01:30 | 53 | 53
2018-06-23 02:00 | 53 | 53
2018-06-23 02:30 | 52 | 52
2018-06-23 03:00 | 53 | 53
2018-06-23 03:30 | 53 | 53
2018-06-23 04:00 | 54 | 53
2018-06-23 04:30 | 53 | 53
2018-06-23 05:00 | 54 | 53
2018-06-23 05:30 | 56 | 56
2018-06-23 06:00 | 55 | 55
2018-06-23 06:30 | 55 | 54
2018-06-23 07:00 | 55 | 55
2018-06-23 07:30 | 53 | 53
2018-06-23 08:00 | 43 | 42
2018-06-23 08:30 | 37 | 37
2018-06-23 09:00 | 38 | 37
2018-06-23 09:30 | 35 | 35
2018-06-23 10:00 | 36 | 36
2018-06-23 10:30 | 36 | 36
2018-06-23 11:00 | 35 | 35
2018-06-23 11:30 | 34 | 33
2018-06-23 12:00 | 32 | 31
2018-06-23 12:30 | 32 | 32
2018-06-23 13:00 | 31 | 30
2018-06-23 13:30 | 29 | 29
2018-06-23 14:00 | 30 | 30
2018-06-23 14:30 | 32 | 31
2018-06-23 15:00 | 22 | 21
2018-06-23 15:30 | 44 | 43
2018-06-23 16:00 | 48 | 48
2018-06-23 16:30 | 50 | 50
2018-06-23 17:00 | 55 | 55
2018-06-23 17:30 | 64 | 63
2018-06-23 18:00 | 71 | 70
2018-06-23 18:30 | 74 | 73
2018-06-23 19:00 | 71 | 70
2018-06-23 19:30 | 69 | 68
2018-06-23 20:00 | 66 | 65
2018-06-23 20:30 | 62 | 61
2018-06-23 21:00 | 55 | 55
2018-06-23 21:30 | 55 | 55
2018-06-23 22:00 | 55 | 54
2018-06-23 22:30 | 54 | 54
2018-06-23 23:00 | 53 | 52
2018-06-23 23:30 | 53 | 53
2018-06-24 | 51 | 51
2018-06-24 00:30 | 51 | 51
2018-06-24 01:00 | 50 | 50
2018-06-24 01:30 | 50 | 49
2018-06-24 02:00 | 50 | 49
2018-06-24 02:30 | 49 | 49
2018-06-24 03:00 | 49 | 49
2018-06-24 03:30 | 49 | 49
2018-06-24 04:00 | 49 | 49
2018-06-24 04:30 | 48 | 48
2018-06-24 05:00 | 49 | 49
2018-06-24 05:30 | 50 | 50
2018-06-24 06:00 | 52 | 52
2018-06-24 06:30 | 52 | 52
2018-06-24 07:00 | 52 | 51
2018-06-24 07:30 | 51 | 50
2018-06-24 08:00 | 47 | 46
2018-06-24 08:30 | 40 | 39
2018-06-24 09:00 | 36 | 35
2018-06-24 09:30 | 35 | 34
2018-06-24 10:00 | 33 | 32
2018-06-24 10:30 | 34 | 34
2018-06-24 11:00 | 32 | 32
2018-06-24 11:30 | 32 | 31
2018-06-24 12:00 | 31 | 30
2018-06-24 12:30 | 31 | 31
2018-06-24 13:00 | 32 | 31
2018-06-24 13:30 | 30 | 30
2018-06-24 14:00 | 32 | 31
2018-06-24 14:30 | 36 | 35
2018-06-24 15:00 | 36 | 35
2018-06-24 15:30 | 38 | 37
2018-06-24 16:00 | 40 | 40
2018-06-24 16:30 | 49 | 48
2018-06-24 17:00 | 53 | 53
2018-06-24 17:30 | 56 | 55
2018-06-24 18:00 | 47 | 47
2018-06-24 18:30 | 55 | 54
2018-06-24 19:00 | 59 | 58
2018-06-24 19:30 | 62 | 61
2018-06-24 20:00 | 61 | 61
2018-06-24 20:30 | 52 | 52
2018-06-24 21:00 | 59 | 58
2018-06-24 21:30 | 57 | 57
2018-06-24 22:00 | 57 | 56
2018-06-24 22:30 | 55 | 54
2018-06-24 23:00 | 54 | 54
2018-06-24 23:30 | 45 | 45
2018-06-25 | 49 | 49
2018-06-25 00:30 | 51 | 51
2018-06-25 01:00 | 51 | 51
2018-06-25 01:30 | 51 | 51
2018-06-25 02:00 | 50 | 50
2018-06-25 02:30 | 50 | 50
2018-06-25 03:00 | 49 | 49
2018-06-25 03:30 | 49 | 49
2018-06-25 04:00 | 50 | 49
2018-06-25 04:30 | 50 | 50
2018-06-25 05:00 | 51 | 51
2018-06-25 05:30 | 50 | 50
2018-06-25 06:00 | 50 | 49
2018-06-25 06:30 | 53 | 52
2018-06-25 07:00 | 53 | 52
2018-06-25 07:30 | 53 | 52
2018-06-25 08:00 | 52 | 51
2018-06-25 08:30 | 52 | 51
2018-06-25 09:00 | 51 | 51
2018-06-25 09:30 | 48 | 47
2018-06-25 10:00 | 41 | 40
2018-06-25 10:30 | 37 | 36
2018-06-25 11:00 | 35 | 34
2018-06-25 11:30 | 34 | 33
2018-06-25 12:00 | 36 | 35
2018-06-25 12:30 | 46 | 45
2018-06-25 13:00 | 45 | 44
2018-06-25 13:30 | 45 | 44
2018-06-25 14:00 | 46 | 45
2018-06-25 14:30 | 46 | 45
2018-06-25 15:00 | 49 | 48
2018-06-25 15:30 | 54 | 53
2018-06-25 16:00 | 60 | 58
2018-06-25 16:30 | 60 | 60
2018-06-25 17:00 | 61 | 61
2018-06-25 17:30 | 66 | 65
2018-06-25 18:00 | 53 | 47
2018-06-25 18:30 | 43 | 36
2018-06-25 19:00 | 37 | 35
2018-06-25 19:30 | 43 | 43
2018-06-25 20:00 | 52 | 52
2018-06-25 20:30 | 61 | 60
2018-06-25 21:00 | 60 | 59
2018-06-25 21:30 | 57 | 57
2018-06-25 22:00 | 53 | 52
2018-06-25 22:30 | 38 | 37
2018-06-25 23:00 | 38 | 37
2018-06-25 23:30 | 39 | 37
2018-06-26 | 38 | 37
2018-06-26 00:30 | 39 | 38
2018-06-26 01:00 | 39 | 38
2018-06-26 01:30 | 38 | 37
2018-06-26 02:00 | 37 | 36
2018-06-26 02:30 | 38 | 36
2018-06-26 03:00 | 41 | 40
2018-06-26 03:30 | 47 | 46
2018-06-26 04:00 | 48 | 48
2018-06-26 04:30 | 48 | 48
2018-06-26 05:00 | 47 | 47
2018-06-26 05:30 | 47 | 47
2018-06-26 06:00 | 45 | 45
2018-06-26 06:30 | 45 | 44
2018-06-26 07:00 | 44 | 43
2018-06-26 07:30 | 58 | 58
2018-06-26 08:00 | 58 | 58
2018-06-26 08:30 | 54 | 54
2018-06-26 09:00 | 51 | 50
2018-06-26 09:30 | 52 | 51
2018-06-26 10:00 | 54 | 53
2018-06-26 10:30 | 57 | 56
2018-06-26 11:00 | 53 | 52
2018-06-26 11:30 | 45 | 44
2018-06-26 12:00 | 42 | 41
2018-06-26 12:30 | 42 | 41
2018-06-26 13:00 | 42 | 41
2018-06-26 13:30 | 44 | 43
2018-06-26 14:00 | 45 | 44
2018-06-26 14:30 | 44 | 43
2018-06-26 15:00 | 44 | 43
2018-06-26 15:30 | 53 | 52
2018-06-26 16:00 | 54 | 53
2018-06-26 16:30 | 58 | 57
2018-06-26 17:00 | 60 | 59
2018-06-26 17:30 | 61 | 61
2018-06-26 18:00 | 65 | 64
2018-06-26 18:30 | 66 | 65
2018-06-26 19:00 | 66 | 65
2018-06-26 19:30 | 65 | 64
2018-06-26 20:00 | 64 | 62
2018-06-26 20:30 | 63 | 62
2018-06-26 21:00 | 63 | 61
2018-06-26 21:30 | 62 | 61
2018-06-26 22:00 | 61 | 58
2018-06-26 22:30 | 58 | 55
2018-06-26 23:00 | 54 | 51
2018-06-26 23:30 | 52 | 49
2018-06-27 | 51 | 49
2018-06-27 00:30 | 50 | 49
2018-06-27 01:00 | 51 | 51
2018-06-27 01:30 | 49 | 49
2018-06-27 02:00 | 49 | 49
2018-06-27 02:30 | 48 | 48
2018-06-27 03:00 | 47 | 47
2018-06-27 03:30 | 47 | 47
2018-06-27 04:00 | 48 | 48
2018-06-27 04:30 | 50 | 50
2018-06-27 05:00 | 51 | 51
2018-06-27 05:30 | 50 | 50
2018-06-27 06:00 | 51 | 51
2018-06-27 06:30 | 51 | 51
2018-06-27 07:00 | 51 | 51
2018-06-27 07:30 | 48 | 48
2018-06-27 08:00 | 46 | 46
2018-06-27 08:30 | 46 | 46
2018-06-27 09:00 | 45 | 45
2018-06-27 09:30 | 37 | 36
2018-06-27 10:00 | 35 | 34
2018-06-27 10:30 | 37 | 37
2018-06-27 11:00 | 36 | 36
2018-06-27 11:30 | 36 | 36
2018-06-27 12:00 | 35 | 35
2018-06-27 12:30 | 40 | 39
2018-06-27 13:00 | 42 | 42
2018-06-27 13:30 | 37 | 37
2018-06-27 14:00 | 40 | 39
2018-06-27 14:30 | 40 | 39
2018-06-27 15:00 | 46 | 46
2018-06-27 15:30 | 47 | 47
2018-06-27 16:00 | 47 | 46
2018-06-27 16:30 | 47 | 47
2018-06-27 17:00 | 44 | 43
2018-06-27 17:30 | 50 | 50
2018-06-27 18:00 | 53 | 53
2018-06-27 18:30 | 55 | 55
2018-06-27 19:00 | 54 | 54
2018-06-27 19:30 | 53 | 53
2018-06-27 20:00 | 53 | 53
2018-06-27 20:30 | 53 | 53
2018-06-27 21:00 | 58 | 58
2018-06-27 21:30 | 52 | 51
2018-06-27 22:00 | 70 | 70
2018-06-27 22:30 | 70 | 70
2018-06-27 23:00 | 68 | 68
2018-06-27 23:30 | 69 | 69
2018-06-28 | 68 | 68
2018-06-28 00:30 | 66 | 65
2018-06-28 01:00 | 68 | 68
2018-06-28 01:30 | 66 | 66
2018-06-28 02:00 | 66 | 66
2018-06-28 02:30 | 62 | 62
2018-06-28 03:00 | 56 | 56
2018-06-28 03:30 | 55 | 54
2018-06-28 04:00 | 51 | 51
2018-06-28 04:30 | 51 | 51
2018-06-28 05:00 | 53 | 53
2018-06-28 05:30 | 53 | 53
2018-06-28 06:00 | 52 | 52
2018-06-28 06:30 | 53 | 53
2018-06-28 07:00 | 54 | 54
2018-06-28 07:30 | 51 | 51
2018-06-28 08:00 | 45 | 45
2018-06-28 08:30 | 38 | 38
2018-06-28 09:00 | 37 | 37
2018-06-28 09:30 | 46 | 46
2018-06-28 10:00 | 50 | 50
2018-06-28 10:30 | 52 | 52
2018-06-28 11:00 | 54 | 54
2018-06-28 11:30 | 53 | 53
2018-06-28 12:00 | 49 | 49
2018-06-28 12:30 | 47 | 47
2018-06-28 13:00 | 45 | 45
2018-06-28 13:30 | 47 | 47
2018-06-28 14:00 | 47 | 47
2018-06-28 14:30 | 56 | 56
2018-06-28 15:00 | 58 | 58
2018-06-28 15:30 | 59 | 59
2018-06-28 16:00 | 57 | 57
2018-06-28 16:30 | 56 | 56
2018-06-28 17:00 | 56 | 56
2018-06-28 17:30 | 66 | 66
2018-06-28 18:00 | 69 | 69
2018-06-28 18:30 | 72 | 72
2018-06-28 19:00 | 70 | 68
2018-06-28 19:30 | 66 | 64
2018-06-28 20:00 | 66 | 64
2018-06-28 20:30 | 64 | 61
2018-06-28 21:00 | 62 | 60
2018-06-28 21:30 | 60 | 58
2018-06-28 22:00 | 58 | 56
2018-06-28 22:30 | 58 | 56
2018-06-28 23:00 | 57 | 55
2018-06-28 23:30 | 57 | 53
2018-06-29 | 53 | 52
2018-06-29 00:30 | 50 | 50
2018-06-29 01:00 | 51 | 51
2018-06-29 01:30 | 52 | 52
2018-06-29 02:00 | 50 | 50
2018-06-29 02:30 | 51 | 51
2018-06-29 03:00 | 51 | 51
2018-06-29 03:30 | 51 | 51
2018-06-29 04:00 | 51 | 51
2018-06-29 04:30 | 51 | 51
2018-06-29 05:00 | 50 | 50
2018-06-29 05:30 | 52 | 52
2018-06-29 06:00 | 51 | 51
2018-06-29 06:30 | 52 | 52
2018-06-29 07:00 | 53 | 53
2018-06-29 07:30 | 43 | 43
2018-06-29 08:00 | 43 | 43
2018-06-29 08:30 | 38 | 38
2018-06-29 09:00 | 35 | 35
2018-06-29 09:30 | 33 | 32
2018-06-29 10:00 | 32 | 32
2018-06-29 10:30 | 34 | 34
2018-06-29 11:00 | 35 | 34
2018-06-29 11:30 | 35 | 35
2018-06-29 12:00 | 34 | 34
2018-06-29 12:30 | 35 | 34
2018-06-29 13:00 | 35 | 35
2018-06-29 13:30 | 33 | 33
2018-06-29 14:00 | 34 | 34
2018-06-29 14:30 | 35 | 35
2018-06-29 15:00 | 35 | 35
2018-06-29 15:30 | 35 | 34
2018-06-29 16:00 | 35 | 35
2018-06-29 16:30 | 40 | 40
2018-06-29 17:00 | 48 | 48
2018-06-29 17:30 | 54 | 54
2018-06-29 18:00 | 57 | 57
2018-06-29 18:30 | 58 | 57
2018-06-29 19:00 | 59 | 58
2018-06-29 19:30 | 58 | 57
2018-06-29 20:00 | 58 | 57
2018-06-29 20:30 | 57 | 57
2018-06-29 21:00 | 56 | 55
2018-06-29 21:30 | 55 | 55
2018-06-29 22:00 | 55 | 55
2018-06-29 22:30 | 54 | 54
2018-06-29 23:00 | 54 | 53
2018-06-29 23:30 | 52 | 52
2018-06-30 | 51 | 51
2018-06-30 00:30 | 50 | 50
2018-06-30 01:00 | 49 | 48
2018-06-30 01:30 | 49 | 49
2018-06-30 02:00 | 49 | 49
2018-06-30 02:30 | 49 | 48
2018-06-30 03:00 | 48 | 48
2018-06-30 03:30 | 48 | 48
2018-06-30 04:00 | 48 | 48
2018-06-30 04:30 | 48 | 48
2018-06-30 05:00 | 48 | 48
2018-06-30 05:30 | 49 | 49
2018-06-30 06:00 | 48 | 48
2018-06-30 06:30 | 49 | 49
2018-06-30 07:00 | 50 | 50
2018-06-30 07:30 | 48 | 48
2018-06-30 08:00 | 38 | 38
2018-06-30 08:30 | 32 | 32
2018-06-30 09:00 | 31 | 31
2018-06-30 09:30 | 30 | 30
2018-06-30 10:00 | 31 | 31
2018-06-30 10:30 | 30 | 30
2018-06-30 11:00 | 30 | 30
2018-06-30 11:30 | 30 | 29
2018-06-30 12:00 | 31 | 30
2018-06-30 12:30 | 31 | 31
2018-06-30 13:00 | 32 | 32
2018-06-30 13:30 | 31 | 31
2018-06-30 14:00 | 36 | 36
2018-06-30 14:30 | 36 | 36
2018-06-30 15:00 | 37 | 37
2018-06-30 15:30 | 39 | 38
2018-06-30 16:00 | 45 | 45
2018-06-30 16:30 | 50 | 50
2018-06-30 17:00 | 52 | 52
2018-06-30 17:30 | 56 | 55
2018-06-30 18:00 | 56 | 56
2018-06-30 18:30 | 56 | 55
2018-06-30 19:00 | 51 | 51
2018-06-30 19:30 | 55 | 54
2018-06-30 20:00 | 54 | 54
2018-06-30 20:30 | 55 | 54
2018-06-30 21:00 | 55 | 54
2018-06-30 21:30 | 54 | 53
2018-06-30 22:00 | 54 | 53
2018-06-30 22:30 | 52 | 52
2018-06-30 23:00 | 49 | 49
2018-06-30 23:30 | 48 | 48
2018-07-01 | 48 | 48
2018-07-01 00:30 | 48 | 48
2018-07-01 01:00 | 49 | 49
2018-07-01 01:30 | 49 | 49
2018-07-01 02:00 | 48 | 48
2018-07-01 02:30 | 48 | 48
2018-07-01 03:00 | 47 | 47
2018-07-01 03:30 | 47 | 47
2018-07-01 04:00 | 47 | 47
2018-07-01 04:30 | 46 | 46
2018-07-01 05:00 | 47 | 47
2018-07-01 05:30 | 48 | 48
2018-07-01 06:00 | 47 | 47
2018-07-01 06:30 | 48 | 48
2018-07-01 07:00 | 49 | 49
2018-07-01 07:30 | 48 | 48
2018-07-01 08:00 | 48 | 48
2018-07-01 08:30 | 50 | 50
2018-07-01 09:00 | 48 | 48
2018-07-01 09:30 | 46 | 46
2018-07-01 10:00 | 46 | 46
2018-07-01 10:30 | 39 | 39
2018-07-01 11:00 | 33 | 33
2018-07-01 11:30 | 31 | 31
2018-07-01 12:00 | 33 | 33
2018-07-01 12:30 | 31 | 31
2018-07-01 13:00 | 33 | 33
2018-07-01 13:30 | 32 | 32
2018-07-01 14:00 | 35 | 35
2018-07-01 14:30 | 33 | 33
2018-07-01 15:00 | 36 | 36
2018-07-01 15:30 | 41 | 41
2018-07-01 16:00 | 44 | 44
2018-07-01 16:30 | 46 | 46
2018-07-01 17:00 | 50 | 50
2018-07-01 17:30 | 52 | 52
2018-07-01 18:00 | 53 | 53
2018-07-01 18:30 | 56 | 56
2018-07-01 19:00 | 55 | 55
2018-07-01 19:30 | 54 | 54
2018-07-01 20:00 | 54 | 54
2018-07-01 20:30 | 54 | 54
2018-07-01 21:00 | 53 | 53
2018-07-01 21:30 | 53 | 53
2018-07-01 22:00 | 52 | 52
2018-07-01 22:30 | 50 | 50
2018-07-01 23:00 | 49 | 49
2018-07-01 23:30 | 48 | 48
2018-07-02 | 49 | 49
2018-07-02 00:30 | 50 | 49
2018-07-02 01:00 | 49 | 49
2018-07-02 01:30 | 49 | 49
2018-07-02 02:00 | 49 | 49
2018-07-02 02:30 | 47 | 47
2018-07-02 03:00 | 47 | 47
2018-07-02 03:30 | 48 | 48
2018-07-02 04:00 | 48 | 48
2018-07-02 04:30 | 41 | 41
2018-07-02 05:00 | 44 | 44
2018-07-02 05:30 | 47 | 47
2018-07-02 06:00 | 50 | 50
2018-07-02 06:30 | 52 | 52
2018-07-02 07:00 | 54 | 54
2018-07-02 07:30 | 54 | 54
2018-07-02 08:00 | 53 | 52
2018-07-02 08:30 | 51 | 51
2018-07-02 09:00 | 51 | 51
2018-07-02 09:30 | 49 | 49
2018-07-02 10:00 | 43 | 43
2018-07-02 10:30 | 41 | 41
2018-07-02 11:00 | 43 | 43
2018-07-02 11:30 | 39 | 39
2018-07-02 12:00 | 38 | 38
2018-07-02 12:30 | 40 | 40
2018-07-02 13:00 | 45 | 45
2018-07-02 13:30 | 44 | 44
2018-07-02 14:00 | 45 | 44
2018-07-02 14:30 | 39 | 38
2018-07-02 15:00 | 45 | 45
2018-07-02 15:30 | 49 | 48
2018-07-02 16:00 | 52 | 52
2018-07-02 16:30 | 60 | 58
2018-07-02 17:00 | 66 | 63
2018-07-02 17:30 | 66 | 64
2018-07-02 18:00 | 67 | 65
2018-07-02 18:30 | 69 | 66
2018-07-02 19:00 | 68 | 66
2018-07-02 19:30 | 71 | 69
2018-07-02 20:00 | 76 | 75
2018-07-02 20:30 | 75 | 73
2018-07-02 21:00 | 68 | 66
2018-07-02 21:30 | 63 | 61
2018-07-02 22:00 | 61 | 59
2018-07-02 22:30 | 59 | 56
2018-07-02 23:00 | 55 | 54
2018-07-02 23:30 | 60 | 60
2018-07-03 | 59 | 59
2018-07-03 00:30 | 59 | 59
2018-07-03 01:00 | 57 | 57
2018-07-03 01:30 | 57 | 57
2018-07-03 02:00 | 57 | 57
2018-07-03 02:30 | 55 | 55
2018-07-03 03:00 | 55 | 55
2018-07-03 03:30 | 56 | 56
2018-07-03 04:00 | 56 | 56
2018-07-03 04:30 | 56 | 56
2018-07-03 05:00 | 55 | 55
2018-07-03 05:30 | 55 | 55
2018-07-03 06:00 | 56 | 56
2018-07-03 06:30 | 58 | 58
2018-07-03 07:00 | 62 | 62
2018-07-03 07:30 | 60 | 59
2018-07-03 08:00 | 51 | 50
2018-07-03 08:30 | 30 | 28
2018-07-03 09:00 | 30 | 28
2018-07-03 09:30 | 34 | 33
2018-07-03 10:00 | 31 | 31
2018-07-03 10:30 | 30 | 29
2018-07-03 11:00 | 31 | 30
2018-07-03 11:30 | 36 | 34
2018-07-03 12:00 | 37 | 35
2018-07-03 12:30 | 32 | 31
2018-07-03 13:00 | 41 | 40
2018-07-03 13:30 | 42 | 42
2018-07-03 14:00 | 45 | 45
2018-07-03 14:30 | 42 | 42
2018-07-03 15:00 | 47 | 47
2018-07-03 15:30 | 50 | 50
2018-07-03 16:00 | 46 | 46
2018-07-03 16:30 | 48 | 48
2018-07-03 17:00 | 55 | 55
2018-07-03 17:30 | 64 | 64
2018-07-03 18:00 | 79 | 78
2018-07-03 18:30 | 85 | 84
2018-07-03 19:00 | 81 | 81
2018-07-03 19:30 | 76 | 76
2018-07-03 20:00 | 75 | 75
2018-07-03 20:30 | 74 | 74
2018-07-03 21:00 | 65 | 65
2018-07-03 21:30 | 58 | 58
2018-07-03 22:00 | 53 | 53
2018-07-03 22:30 | 56 | 56
2018-07-03 23:00 | 62 | 62
2018-07-03 23:30 | 62 | 62
2018-07-04 | 60 | 60
2018-07-04 00:30 | 55 | 55
2018-07-04 01:00 | 52 | 52
2018-07-04 01:30 | 52 | 52
2018-07-04 02:00 | 51 | 51
2018-07-04 02:30 | 51 | 51
2018-07-04 03:00 | 50 | 50
2018-07-04 03:30 | 50 | 50
2018-07-04 04:00 | 50 | 50
2018-07-04 04:30 | 50 | 50
2018-07-04 05:00 | 50 | 50
2018-07-04 05:30 | 51 | 51
2018-07-04 06:00 | 51 | 51
2018-07-04 06:30 | 52 | 52
2018-07-04 07:00 | 53 | 53
2018-07-04 07:30 | 48 | 48
2018-07-04 08:00 | 24 | 24
2018-07-04 08:30 | 11 | 2
2018-07-04 09:00 | 11 | 6
2018-07-04 09:30 | 27 | 27
2018-07-04 10:00 | 26 | 25
2018-07-04 10:30 | 31 | 31
2018-07-04 11:00 | 32 | 31
2018-07-04 11:30 | 34 | 34
2018-07-04 12:00 | 35 | 34
2018-07-04 12:30 | 35 | 34
2018-07-04 13:00 | 35 | 34
2018-07-04 13:30 | 29 | 29
2018-07-04 14:00 | 25 | 24
2018-07-04 14:30 | 25 | 24
2018-07-04 15:00 | 27 | 25
2018-07-04 15:30 | 26 | 25
2018-07-04 16:00 | 28 | 26
2018-07-04 16:30 | 27 | 26
2018-07-04 17:00 | 41 | 40
2018-07-04 17:30 | 61 | 61
2018-07-04 18:00 | 63 | 63
2018-07-04 18:30 | 64 | 64
2018-07-04 19:00 | 65 | 65
2018-07-04 19:30 | 63 | 63
2018-07-04 20:00 | 63 | 63
2018-07-04 20:30 | 62 | 62
2018-07-04 21:00 | 62 | 62
2018-07-04 21:30 | 56 | 56
2018-07-04 22:00 | 54 | 54
2018-07-04 22:30 | 54 | 54
2018-07-04 23:00 | 53 | 53
2018-07-04 23:30 | 53 | 53
2018-07-05 | 41 | 41
2018-07-05 00:30 | 49 | 49
2018-07-05 01:00 | 49 | 49
2018-07-05 01:30 | 50 | 50
2018-07-05 02:00 | 49 | 49
2018-07-05 02:30 | 48 | 48
2018-07-05 03:00 | 48 | 48
2018-07-05 03:30 | 48 | 48
2018-07-05 04:00 | 47 | 47
2018-07-05 04:30 | 48 | 48
2018-07-05 05:00 | 49 | 49
2018-07-05 05:30 | 49 | 49
2018-07-05 06:00 | 49 | 49
2018-07-05 06:30 | 50 | 50
2018-07-05 07:00 | 53 | 52
2018-07-05 07:30 | 50 | 50
2018-07-05 08:00 | 41 | 41
2018-07-05 08:30 | 33 | 33
2018-07-05 09:00 | 44 | 44
2018-07-05 09:30 | 44 | 44
2018-07-05 10:00 | 43 | 43
2018-07-05 10:30 | 43 | 43
2018-07-05 11:00 | 44 | 42
2018-07-05 11:30 | 42 | 41
2018-07-05 12:00 | 43 | 41
2018-07-05 12:30 | 43 | 41
2018-07-05 13:00 | 42 | 41
2018-07-05 13:30 | 41 | 40
2018-07-05 14:00 | 36 | 34
2018-07-05 14:30 | 36 | 36
2018-07-05 15:00 | 35 | 34
2018-07-05 15:30 | 37 | 36
2018-07-05 16:00 | 36 | 35
2018-07-05 16:30 | 36 | 35
2018-07-05 17:00 | 41 | 41
2018-07-05 17:30 | 52 | 51
2018-07-05 18:00 | 56 | 56
2018-07-05 18:30 | 58 | 57
2018-07-05 19:00 | 59 | 57
2018-07-05 19:30 | 59 | 58
2018-07-05 20:00 | 59 | 57
2018-07-05 20:30 | 57 | 55
2018-07-05 21:00 | 57 | 55
2018-07-05 21:30 | 55 | 53
2018-07-05 22:00 | 56 | 52
2018-07-05 22:30 | 52 | 52
2018-07-05 23:00 | 52 | 52
2018-07-05 23:30 | 50 | 50
2018-07-06 | 50 | 49
2018-07-06 00:30 | 50 | 50
2018-07-06 01:00 | 50 | 50
2018-07-06 01:30 | 49 | 49
2018-07-06 02:00 | 49 | 49
2018-07-06 02:30 | 49 | 49
2018-07-06 03:00 | 49 | 49
2018-07-06 03:30 | 48 | 48
2018-07-06 04:00 | 49 | 49
2018-07-06 04:30 | 48 | 48
2018-07-06 05:00 | 48 | 48
2018-07-06 05:30 | 49 | 49
2018-07-06 06:00 | 49 | 49
2018-07-06 06:30 | 50 | 50
2018-07-06 07:00 | 51 | 51
2018-07-06 07:30 | 42 | 42
2018-07-06 08:00 | 28 | 27
2018-07-06 08:30 | 22 | 21
2018-07-06 09:00 | 22 | 22
2018-07-06 09:30 | 25 | 23
2018-07-06 10:00 | 25 | 24
2018-07-06 10:30 | 25 | 24
2018-07-06 11:00 | 25 | 24
2018-07-06 11:30 | 26 | 25
2018-07-06 12:00 | 22 | 21
2018-07-06 12:30 | 31 | 30
2018-07-06 13:00 | 29 | 28
2018-07-06 13:30 | 28 | 27
2018-07-06 14:00 | 26 | 25
2018-07-06 14:30 | 26 | 26
2018-07-06 15:00 | 25 | 23
2018-07-06 15:30 | 29 | 28
2018-07-06 16:00 | 28 | 27
2018-07-06 16:30 | 39 | 38
2018-07-06 17:00 | 43 | 42
2018-07-06 17:30 | 52 | 51
2018-07-06 18:00 | 56 | 55
2018-07-06 18:30 | 57 | 56
2018-07-06 19:00 | 58 | 57
2018-07-06 19:30 | 59 | 58
2018-07-06 20:00 | 59 | 58
2018-07-06 20:30 | 58 | 57
2018-07-06 21:00 | 57 | 57
2018-07-06 21:30 | 57 | 56
2018-07-06 22:00 | 55 | 54
2018-07-06 22:30 | 54 | 53
2018-07-06 23:00 | 53 | 53
2018-07-06 23:30 | 52 | 52
2018-07-07 | 52 | 51
2018-07-07 00:30 | 51 | 51
2018-07-07 01:00 | 51 | 51
2018-07-07 01:30 | 51 | 51
2018-07-07 02:00 | 50 | 50
2018-07-07 02:30 | 51 | 51
2018-07-07 03:00 | 52 | 52
2018-07-07 03:30 | 50 | 50
2018-07-07 04:00 | 50 | 50
2018-07-07 04:30 | 50 | 50
2018-07-07 05:00 | 50 | 50
2018-07-07 05:30 | 51 | 51
2018-07-07 06:00 | 50 | 50
2018-07-07 06:30 | 52 | 52
2018-07-07 07:00 | 52 | 52
2018-07-07 07:30 | 27 | 26
2018-07-07 08:00 | 29 | 25
2018-07-07 08:30 | 48 | 48
2018-07-07 09:00 | 48 | 48
2018-07-07 09:30 | 47 | 47
2018-07-07 10:00 | 43 | 43
2018-07-07 10:30 | 41 | 41
2018-07-07 11:00 | 41 | 41
2018-07-07 11:30 | 41 | 41
2018-07-07 12:00 | 42 | 42
2018-07-07 12:30 | 39 | 39
2018-07-07 13:00 | 35 | 35
2018-07-07 13:30 | 36 | 36
2018-07-07 14:00 | 39 | 39
2018-07-07 14:30 | 41 | 41
2018-07-07 15:00 | 38 | 38
2018-07-07 15:30 | 39 | 38
2018-07-07 16:00 | 42 | 42
2018-07-07 16:30 | 47 | 47
2018-07-07 17:00 | 50 | 50
2018-07-07 17:30 | 54 | 54
2018-07-07 18:00 | 57 | 56
2018-07-07 18:30 | 58 | 57
2018-07-07 19:00 | 57 | 57
2018-07-07 19:30 | 57 | 57
2018-07-07 20:00 | 55 | 55
2018-07-07 20:30 | 55 | 54
2018-07-07 21:00 | 55 | 55
2018-07-07 21:30 | 55 | 55
2018-07-07 22:00 | 55 | 54
2018-07-07 22:30 | 47 | 47
2018-07-07 23:00 | 53 | 53
2018-07-07 23:30 | 51 | 51
2018-07-08 | 50 | 50
2018-07-08 00:30 | 51 | 50
2018-07-08 01:00 | 50 | 50
2018-07-08 01:30 | 51 | 51
2018-07-08 02:00 | 51 | 51
2018-07-08 02:30 | 51 | 51
2018-07-08 03:00 | 50 | 50
2018-07-08 03:30 | 50 | 50
2018-07-08 04:00 | 50 | 49
2018-07-08 04:30 | 49 | 49
2018-07-08 05:00 | 49 | 49
2018-07-08 05:30 | 49 | 49
2018-07-08 06:00 | 49 | 49
2018-07-08 06:30 | 50 | 49
2018-07-08 07:00 | 52 | 52
2018-07-08 07:30 | 49 | 49
2018-07-08 08:00 | 41 | 41
2018-07-08 08:30 | 34 | 34
2018-07-08 09:00 | 34 | 34
2018-07-08 09:30 | 33 | 33
2018-07-08 10:00 | 32 | 32
2018-07-08 10:30 | 32 | 31
2018-07-08 11:00 | 36 | 34
2018-07-08 11:30 | 33 | 33
2018-07-08 12:00 | 31 | 31
2018-07-08 12:30 | 31 | 31
2018-07-08 13:00 | 33 | 32
2018-07-08 13:30 | 35 | 34
2018-07-08 14:00 | 31 | 30
2018-07-08 14:30 | 32 | 31
2018-07-08 15:00 | 31 | 31
2018-07-08 15:30 | 33 | 33
2018-07-08 16:00 | 32 | 31
2018-07-08 16:30 | 34 | 34
2018-07-08 17:00 | 40 | 40
2018-07-08 17:30 | 51 | 51
2018-07-08 18:00 | 59 | 59
2018-07-08 18:30 | 61 | 61
2018-07-08 19:00 | 62 | 61
2018-07-08 19:30 | 60 | 59
2018-07-08 20:00 | 59 | 58
2018-07-08 20:30 | 58 | 57
2018-07-08 21:00 | 57 | 57
2018-07-08 21:30 | 54 | 53
2018-07-08 22:00 | 54 | 53
2018-07-08 22:30 | 54 | 53
2018-07-08 23:00 | 52 | 52
2018-07-08 23:30 | 52 | 52
2018-07-09 | 52 | 52
2018-07-09 00:30 | 49 | 49
2018-07-09 01:00 | 49 | 49
2018-07-09 01:30 | 49 | 49
2018-07-09 02:00 | 50 | 50
2018-07-09 02:30 | 50 | 50
2018-07-09 03:00 | 48 | 48
2018-07-09 03:30 | 50 | 50
2018-07-09 04:00 | 52 | 52
2018-07-09 04:30 | 50 | 50
2018-07-09 05:00 | 50 | 50
2018-07-09 05:30 | 51 | 51
2018-07-09 06:00 | 51 | 51
2018-07-09 06:30 | 52 | 52
2018-07-09 07:00 | 54 | 54
2018-07-09 07:30 | 50 | 50
2018-07-09 08:00 | 29 | 29
2018-07-09 08:30 | 25 | 24
2018-07-09 09:00 | 14 | 14
2018-07-09 09:30 | 25 | 25
2018-07-09 10:00 | 24 | 24
2018-07-09 10:30 | 24 | 24
2018-07-09 11:00 | 26 | 26
2018-07-09 11:30 | 23 | 23
2018-07-09 12:00 | 24 | 24
2018-07-09 12:30 | 27 | 26
2018-07-09 13:00 | 29 | 29
2018-07-09 13:30 | 29 | 29
2018-07-09 14:00 | 29 | 28
2018-07-09 14:30 | 29 | 28
2018-07-09 15:00 | 30 | 30
2018-07-09 15:30 | 30 | 30
2018-07-09 16:00 | 35 | 34
2018-07-09 16:30 | 35 | 35
2018-07-09 17:00 | 40 | 40
2018-07-09 17:30 | 50 | 50
2018-07-09 18:00 | 56 | 56
2018-07-09 18:30 | 60 | 60
2018-07-09 19:00 | 59 | 59
2018-07-09 19:30 | 59 | 59
2018-07-09 20:00 | 57 | 57
2018-07-09 20:30 | 56 | 56
2018-07-09 21:00 | 55 | 55
2018-07-09 21:30 | 54 | 54
2018-07-09 22:00 | 53 | 53
2018-07-09 22:30 | 51 | 51
2018-07-09 23:00 | 50 | 50
2018-07-09 23:30 | 50 | 50
2018-07-10 | 50 | 50
2018-07-10 00:30 | 54 | 54
2018-07-10 01:00 | 52 | 52
2018-07-10 01:30 | 52 | 52
2018-07-10 02:00 | 51 | 51
2018-07-10 02:30 | 51 | 50
2018-07-10 03:00 | 51 | 51
2018-07-10 03:30 | 52 | 52
2018-07-10 04:00 | 52 | 52
2018-07-10 04:30 | 53 | 53
2018-07-10 05:00 | 56 | 56
2018-07-10 05:30 | 60 | 59
2018-07-10 06:00 | 62 | 62
2018-07-10 06:30 | 64 | 63
2018-07-10 07:00 | 63 | 63
2018-07-10 07:30 | 54 | 53
2018-07-10 08:00 | 40 | 40
2018-07-10 08:30 | 34 | 34
2018-07-10 09:00 | 33 | 33
2018-07-10 09:30 | 31 | 31
2018-07-10 10:00 | 30 | 30
2018-07-10 10:30 | 30 | 30
2018-07-10 11:00 | 28 | 27
2018-07-10 11:30 | 31 | 31
2018-07-10 12:00 | 32 | 32
2018-07-10 12:30 | 32 | 32
2018-07-10 13:00 | 32 | 32
2018-07-10 13:30 | 32 | 32
2018-07-10 14:00 | 34 | 34
2018-07-10 14:30 | 34 | 34
2018-07-10 15:00 | 33 | 33
2018-07-10 15:30 | 33 | 33
2018-07-10 16:00 | 34 | 34
2018-07-10 16:30 | 33 | 33
2018-07-10 17:00 | 36 | 36
2018-07-10 17:30 | 55 | 54
2018-07-10 18:00 | 62 | 62
2018-07-10 18:30 | 53 | 52
2018-07-10 19:00 | 62 | 60
2018-07-10 19:30 | 63 | 62
2018-07-10 20:00 | 62 | 60
2018-07-10 20:30 | 61 | 59
2018-07-10 21:00 | 56 | 52
2018-07-10 21:30 | 60 | 58
2018-07-10 22:00 | 58 | 57
2018-07-10 22:30 | 57 | 55
2018-07-10 23:00 | 56 | 54
2018-07-10 23:30 | 57 | 54
2018-07-11 | 53 | 53
2018-07-11 00:30 | 52 | 52
2018-07-11 01:00 | 53 | 52
2018-07-11 01:30 | 51 | 51
2018-07-11 02:00 | 52 | 51
2018-07-11 02:30 | 52 | 51
2018-07-11 03:00 | 52 | 52
2018-07-11 03:30 | 52 | 52
2018-07-11 04:00 | 51 | 51
2018-07-11 04:30 | 52 | 52
2018-07-11 05:00 | 52 | 51
2018-07-11 05:30 | 52 | 52
2018-07-11 06:00 | 52 | 51
2018-07-11 06:30 | 54 | 54
2018-07-11 07:00 | 57 | 57
2018-07-11 07:30 | 48 | 48
2018-07-11 08:00 | 31 | 30
2018-07-11 08:30 | 25 | 24
2018-07-11 09:00 | 25 | 25
2018-07-11 09:30 | 25 | 24
2018-07-11 10:00 | 26 | 24
2018-07-11 10:30 | 22 | 21
2018-07-11 11:00 | 21 | 19
2018-07-11 11:30 | 10 | 4
2018-07-11 12:00 | 10 | 4
2018-07-11 12:30 | 10 | 5
2018-07-11 13:00 | 12 | 9
2018-07-11 13:30 | 15 | 13
2018-07-11 14:00 | 14 | 12
2018-07-11 14:30 | 15 | 13
2018-07-11 15:00 | 16 | 15
2018-07-11 15:30 | 14 | 12
2018-07-11 16:00 | 20 | 18
2018-07-11 16:30 | 27 | 25
2018-07-11 17:00 | 35 | 34
2018-07-11 17:30 | 60 | 59
2018-07-11 18:00 | 70 | 69
2018-07-11 18:30 | 69 | 69
2018-07-11 19:00 | 70 | 69
2018-07-11 19:30 | 69 | 69
2018-07-11 20:00 | 68 | 68
2018-07-11 20:30 | 67 | 66
2018-07-11 21:00 | 65 | 65
2018-07-11 21:30 | 63 | 63
2018-07-11 22:00 | 59 | 59
2018-07-11 22:30 | 54 | 54
2018-07-11 23:00 | 54 | 54
2018-07-11 23:30 | 53 | 53
2018-07-12 | 53 | 53
2018-07-12 00:30 | 53 | 52
2018-07-12 01:00 | 51 | 51
2018-07-12 01:30 | 50 | 50
2018-07-12 02:00 | 50 | 50
2018-07-12 02:30 | 49 | 49
2018-07-12 03:00 | 50 | 50
2018-07-12 03:30 | 52 | 52
2018-07-12 04:00 | 51 | 51
2018-07-12 04:30 | 52 | 52
2018-07-12 05:00 | 53 | 53
2018-07-12 05:30 | 52 | 52
2018-07-12 06:00 | 53 | 52
2018-07-12 06:30 | 54 | 54
2018-07-12 07:00 | 48 | 48
2018-07-12 07:30 | 42 | 42
2018-07-12 08:00 | 25 | 25
2018-07-12 08:30 | 16 | 16
2018-07-12 09:00 | 11 | 10
2018-07-12 09:30 | 5 | 4
2018-07-12 10:00 | 4 | 3
2018-07-12 10:30 | 3 | 3
2018-07-12 11:00 | 3 | 3
2018-07-12 11:30 | 3 | 3
2018-07-12 12:00 | 3 | 3
2018-07-12 12:30 | 4 | 4
2018-07-12 13:00 | 7 | 7
2018-07-12 13:30 | 12 | 11
2018-07-12 14:00 | 12 | 12
2018-07-12 14:30 | 8 | 8
2018-07-12 15:00 | 7 | 6
2018-07-12 15:30 | 10 | 10
2018-07-12 16:00 | 16 | 16
2018-07-12 16:30 | 21 | 21
2018-07-12 17:00 | 31 | 31
2018-07-12 17:30 | 50 | 50
2018-07-12 18:00 | 58 | 58
2018-07-12 18:30 | 60 | 60
2018-07-12 19:00 | 61 | 60
2018-07-12 19:30 | 60 | 60
2018-07-12 20:00 | 58 | 58
2018-07-12 20:30 | 56 | 56
2018-07-12 21:00 | 56 | 56
2018-07-12 21:30 | 54 | 54
2018-07-12 22:00 | 52 | 52
2018-07-12 22:30 | 51 | 51
2018-07-12 23:00 | 49 | 49
2018-07-12 23:30 | 49 | 49
2018-07-13 | 49 | 49
2018-07-13 00:30 | 46 | 46
2018-07-13 01:00 | 50 | 50
2018-07-13 01:30 | 49 | 49
2018-07-13 02:00 | 49 | 49
2018-07-13 02:30 | 49 | 49
2018-07-13 03:00 | 49 | 49
2018-07-13 03:30 | 50 | 50
2018-07-13 04:00 | 48 | 48
2018-07-13 04:30 | 48 | 48
2018-07-13 05:00 | 50 | 50
2018-07-13 05:30 | 51 | 50
2018-07-13 06:00 | 49 | 49
2018-07-13 06:30 | 51 | 50
2018-07-13 07:00 | 53 | 52
2018-07-13 07:30 | 40 | 39
2018-07-13 08:00 | 26 | 25
2018-07-13 08:30 | 17 | 17
2018-07-13 09:00 | 10 | 10
2018-07-13 09:30 | 5 | 5
2018-07-13 10:00 | 4 | 3
2018-07-13 10:30 | 4 | 4
2018-07-13 11:00 | 1 | 1
2018-07-13 11:30 | 10 | 9
2018-07-13 12:00 | 5 | 0
2018-07-13 12:30 | 14 | 8
2018-07-13 13:00 | 17 | 15
2018-07-13 13:30 | 15 | 13
2018-07-13 14:00 | 11 | 11
2018-07-13 14:30 | 11 | 3
2018-07-13 15:00 | 14 | 10
2018-07-13 15:30 | 19 | 16
2018-07-13 16:00 | 23 | 23
2018-07-13 16:30 | 29 | 29
2018-07-13 17:00 | 41 | 41
2018-07-13 17:30 | 56 | 56
2018-07-13 18:00 | 42 | 41
2018-07-13 18:30 | 37 | 34
2018-07-13 19:00 | 37 | 34
2018-07-13 19:30 | 49 | 49
2018-07-13 20:00 | 63 | 63
2018-07-13 20:30 | 65 | 65
2018-07-13 21:00 | 53 | 53
2018-07-13 21:30 | 58 | 58
2018-07-13 22:00 | 59 | 59
2018-07-13 22:30 | 58 | 58
2018-07-13 23:00 | 51 | 51
2018-07-13 23:30 | 51 | 51
2018-07-14 | 49 | 49
2018-07-14 00:30 | 49 | 49
2018-07-14 01:00 | 49 | 48
2018-07-14 01:30 | 48 | 48
2018-07-14 02:00 | 48 | 48
2018-07-14 02:30 | 48 | 48
2018-07-14 03:00 | 47 | 47
2018-07-14 03:30 | 48 | 48
2018-07-14 04:00 | 48 | 48
2018-07-14 04:30 | 48 | 48
2018-07-14 05:00 | 48 | 48
2018-07-14 05:30 | 47 | 47
2018-07-14 06:00 | 46 | 46
2018-07-14 06:30 | 47 | 47
2018-07-14 07:00 | 49 | 49
2018-07-14 07:30 | 45 | 45
2018-07-14 08:00 | 34 | 34
2018-07-14 08:30 | 26 | 26
2018-07-14 09:00 | 25 | 25
2018-07-14 09:30 | 21 | 21
2018-07-14 10:00 | 18 | 18
2018-07-14 10:30 | 16 | 16
2018-07-14 11:00 | 17 | 17
2018-07-14 11:30 | 16 | 15
2018-07-14 12:00 | 16 | 15
2018-07-14 12:30 | 16 | 15
2018-07-14 13:00 | 13 | 12
2018-07-14 13:30 | 9 | 8
2018-07-14 14:00 | 11 | 9
2018-07-14 14:30 | 12 | 10
2018-07-14 15:00 | 11 | 10
2018-07-14 15:30 | 13 | 12
2018-07-14 16:00 | 20 | 19
2018-07-14 16:30 | 26 | 26
2018-07-14 17:00 | 33 | 33
2018-07-14 17:30 | 48 | 48
2018-07-14 18:00 | 54 | 54
2018-07-14 18:30 | 57 | 57
2018-07-14 19:00 | 56 | 56
2018-07-14 19:30 | 56 | 56
2018-07-14 20:00 | 55 | 55
2018-07-14 20:30 | 54 | 54
2018-07-14 21:00 | 54 | 54
2018-07-14 21:30 | 53 | 53
2018-07-14 22:00 | 54 | 53
2018-07-14 22:30 | 52 | 52
2018-07-14 23:00 | 52 | 52
2018-07-14 23:30 | 51 | 50
2018-07-15 | 50 | 50
2018-07-15 00:30 | 50 | 50
2018-07-15 01:00 | 50 | 49
2018-07-15 01:30 | 49 | 49
2018-07-15 02:00 | 49 | 49
2018-07-15 02:30 | 48 | 48
2018-07-15 03:00 | 48 | 48
2018-07-15 03:30 | 48 | 48
2018-07-15 04:00 | 49 | 49
2018-07-15 04:30 | 48 | 48
2018-07-15 05:00 | 48 | 48
2018-07-15 05:30 | 48 | 48
2018-07-15 06:00 | 39 | 39
2018-07-15 06:30 | 47 | 47
2018-07-15 07:00 | 48 | 48
2018-07-15 07:30 | 41 | 41
2018-07-15 08:00 | 25 | 25
2018-07-15 08:30 | 18 | 18
2018-07-15 09:00 | 12 | 11
2018-07-15 09:30 | 6 | 4
2018-07-15 10:00 | 13 | 12
2018-07-15 10:30 | 32 | 29
2018-07-15 11:00 | 31 | 28
2018-07-15 11:30 | 30 | 30
2018-07-15 12:00 | 30 | 29
2018-07-15 12:30 | 27 | 22
2018-07-15 13:00 | 25 | 21
2018-07-15 13:30 | 24 | 22
2018-07-15 14:00 | 18 | 15
2018-07-15 14:30 | 11 | 5
2018-07-15 15:00 | 12 | 7
2018-07-15 15:30 | 18 | 15
2018-07-15 16:00 | 24 | 22
2018-07-15 16:30 | 34 | 32
2018-07-15 17:00 | 39 | 38
2018-07-15 17:30 | 50 | 49
2018-07-15 18:00 | 54 | 54
2018-07-15 18:30 | 44 | 38
2018-07-15 19:00 | 48 | 44
2018-07-15 19:30 | 56 | 55
2018-07-15 20:00 | 54 | 52
2018-07-15 20:30 | 54 | 53
2018-07-15 21:00 | 53 | 52
2018-07-15 21:30 | 54 | 53
2018-07-15 22:00 | 53 | 52
2018-07-15 22:30 | 52 | 52
2018-07-15 23:00 | 50 | 50
2018-07-15 23:30 | 49 | 48
2018-07-16 | 50 | 49
2018-07-16 00:30 | 51 | 51
2018-07-16 01:00 | 51 | 49
2018-07-16 01:30 | 50 | 47
2018-07-16 02:00 | 50 | 48
2018-07-16 02:30 | 50 | 48
2018-07-16 03:00 | 49 | 47
2018-07-16 03:30 | 48 | 46
2018-07-16 04:00 | 48 | 46
2018-07-16 04:30 | 49 | 46
2018-07-16 05:00 | 50 | 48
2018-07-16 05:30 | 50 | 48
2018-07-16 06:00 | 51 | 48
2018-07-16 06:30 | 53 | 49
2018-07-16 07:00 | 53 | 51
2018-07-16 07:30 | 48 | 48
2018-07-16 08:00 | 20 | 20
2018-07-16 08:30 | 12 | 12
2018-07-16 09:00 | 5 | 4
2018-07-16 09:30 | 6 | 3
2018-07-16 10:00 | 23 | 20
2018-07-16 10:30 | 38 | 37
2018-07-16 11:00 | 37 | 36
2018-07-16 11:30 | 38 | 37
2018-07-16 12:00 | 38 | 37
2018-07-16 12:30 | 37 | 34
2018-07-16 13:00 | 32 | 32
2018-07-16 13:30 | 31 | 31
2018-07-16 14:00 | 31 | 31
2018-07-16 14:30 | 27 | 27
2018-07-16 15:00 | 4 | 4
2018-07-16 15:30 | 15 | 15
2018-07-16 16:00 | 24 | 24
2018-07-16 16:30 | 31 | 31
2018-07-16 17:00 | 37 | 37
2018-07-16 17:30 | 50 | 50
2018-07-16 18:00 | 57 | 56
2018-07-16 18:30 | 59 | 58
2018-07-16 19:00 | 58 | 58
2018-07-16 19:30 | 58 | 58
2018-07-16 20:00 | 57 | 57
2018-07-16 20:30 | 56 | 55
2018-07-16 21:00 | 55 | 55
2018-07-16 21:30 | 55 | 55
2018-07-16 22:00 | 53 | 53
2018-07-16 22:30 | 54 | 54
2018-07-16 23:00 | 53 | 53
2018-07-16 23:30 | 51 | 51
2018-07-17 | 49 | 49
2018-07-17 00:30 | 50 | 50
2018-07-17 01:00 | 49 | 49
2018-07-17 01:30 | 49 | 49
2018-07-17 02:00 | 49 | 49
2018-07-17 02:30 | 43 | 43
2018-07-17 03:00 | 50 | 50
2018-07-17 03:30 | 50 | 50
2018-07-17 04:00 | 51 | 51
2018-07-17 04:30 | 51 | 51
2018-07-17 05:00 | 50 | 50
2018-07-17 05:30 | 51 | 51
2018-07-17 06:00 | 51 | 51
2018-07-17 06:30 | 52 | 52
2018-07-17 07:00 | 54 | 53
2018-07-17 07:30 | 51 | 51
2018-07-17 08:00 | 39 | 39
2018-07-17 08:30 | 30 | 30
2018-07-17 09:00 | 18 | 18
2018-07-17 09:30 | 12 | 12
2018-07-17 10:00 | 9 | 9
2018-07-17 10:30 | 7 | 7
2018-07-17 11:00 | 6 | 5
2018-07-17 11:30 | 6 | 5
2018-07-17 12:00 | 6 | 5
2018-07-17 12:30 | 6 | 5
2018-07-17 13:00 | 6 | 5
2018-07-17 13:30 | 6 | 6
2018-07-17 14:00 | 6 | 5
2018-07-17 14:30 | 7 | 6
2018-07-17 15:00 | 7 | 6
2018-07-17 15:30 | 9 | 8
2018-07-17 16:00 | 11 | 10
2018-07-17 16:30 | 21 | 21
2018-07-17 17:00 | 27 | 27
2018-07-17 17:30 | 32 | 32
2018-07-17 18:00 | 45 | 44
2018-07-17 18:30 | 48 | 47
2018-07-17 19:00 | 49 | 48
2018-07-17 19:30 | 51 | 51
2018-07-17 20:00 | 51 | 51
2018-07-17 20:30 | 50 | 50
2018-07-17 21:00 | 50 | 49
2018-07-17 21:30 | 59 | 59
2018-07-17 22:00 | 60 | 60
2018-07-17 22:30 | 58 | 58
2018-07-17 23:00 | 54 | 54
2018-07-17 23:30 | 52 | 51
2018-07-18 | 54 | 54
2018-07-18 00:30 | 54 | 54
2018-07-18 01:00 | 52 | 51
2018-07-18 01:30 | 51 | 50
2018-07-18 02:00 | 51 | 50
2018-07-18 02:30 | 50 | 49
2018-07-18 03:00 | 50 | 49
2018-07-18 03:30 | 50 | 49
2018-07-18 04:00 | 50 | 49
2018-07-18 04:30 | 49 | 49
2018-07-18 05:00 | 47 | 46
2018-07-18 05:30 | 47 | 46
2018-07-18 06:00 | 47 | 46
2018-07-18 06:30 | 36 | 31
2018-07-18 07:00 | 37 | 33
2018-07-18 07:30 | 33 | 28
2018-07-18 08:00 | 21 | 9
2018-07-18 08:30 | 19 | 2
2018-07-18 09:00 | 19 | 7
2018-07-18 09:30 | 20 | 19
2018-07-18 10:00 | 31 | 31
2018-07-18 10:30 | 33 | 33
2018-07-18 11:00 | 18 | 18
2018-07-18 11:30 | 5 | 2
2018-07-18 12:00 | 5 | 3
2018-07-18 12:30 | 6 | 5
2018-07-18 13:00 | 6 | 4
2018-07-18 13:30 | 5 | 4
2018-07-18 14:00 | 5 | 3
2018-07-18 14:30 | 6 | 4
2018-07-18 15:00 | 5 | 3
2018-07-18 15:30 | 7 | 6
2018-07-18 16:00 | 10 | 9
2018-07-18 16:30 | 19 | 18
2018-07-18 17:00 | 30 | 29
2018-07-18 17:30 | 36 | 36
2018-07-18 18:00 | 47 | 46
2018-07-18 18:30 | 49 | 47
2018-07-18 19:00 | 50 | 48
2018-07-18 19:30 | 50 | 48
2018-07-18 20:00 | 49 | 48
2018-07-18 20:30 | 61 | 61
2018-07-18 21:00 | 64 | 64
2018-07-18 21:30 | 63 | 63
2018-07-18 22:00 | 62 | 62
2018-07-18 22:30 | 57 | 57
2018-07-18 23:00 | 57 | 57
2018-07-18 23:30 | 51 | 51
2018-07-19 | 50 | 50
2018-07-19 00:30 | 50 | 50
2018-07-19 01:00 | 50 | 50
2018-07-19 01:30 | 49 | 49
2018-07-19 02:00 | 49 | 49
2018-07-19 02:30 | 49 | 49
2018-07-19 03:00 | 49 | 48
2018-07-19 03:30 | 49 | 49
2018-07-19 04:00 | 50 | 50
2018-07-19 04:30 | 52 | 52
2018-07-19 05:00 | 52 | 52
2018-07-19 05:30 | 54 | 54
2018-07-19 06:00 | 53 | 53
2018-07-19 06:30 | 40 | 40
2018-07-19 07:00 | 38 | 37
2018-07-19 07:30 | 27 | 26
2018-07-19 08:00 | 9 | 8
2018-07-19 08:30 | 4 | 1
2018-07-19 09:00 | 26 | 26
2018-07-19 09:30 | 29 | 29
2018-07-19 10:00 | 35 | 33
2018-07-19 10:30 | 25 | 24
2018-07-19 11:00 | 10 | 8
2018-07-19 11:30 | 11 | 9
2018-07-19 12:00 | 12 | 10
2018-07-19 12:30 | 13 | 12
2018-07-19 13:00 | 12 | 11
2018-07-19 13:30 | 15 | 14
2018-07-19 14:00 | 29 | 27
2018-07-19 14:30 | 29 | 27
2018-07-19 15:00 | 19 | 19
2018-07-19 15:30 | 19 | 19
2018-07-19 16:00 | 18 | 15
2018-07-19 16:30 | 21 | 18
2018-07-19 17:00 | 34 | 33
2018-07-19 17:30 | 40 | 40
2018-07-19 18:00 | 41 | 40
2018-07-19 18:30 | 42 | 42
2018-07-19 19:00 | 43 | 43
2018-07-19 19:30 | 42 | 41
2018-07-19 20:00 | 41 | 41
2018-07-19 20:30 | 40 | 39
2018-07-19 21:00 | 39 | 39
2018-07-19 21:30 | 40 | 39
2018-07-19 22:00 | 38 | 38
2018-07-19 22:30 | 35 | 35
2018-07-19 23:00 | 51 | 51
2018-07-19 23:30 | 48 | 47
2018-07-20 | 47 | 47
2018-07-20 00:30 | 47 | 47
2018-07-20 01:00 | 45 | 45
2018-07-20 01:30 | 44 | 44
2018-07-20 02:00 | 45 | 44
2018-07-20 02:30 | 43 | 43
2018-07-20 03:00 | 44 | 43
2018-07-20 03:30 | 44 | 44
2018-07-20 04:00 | 45 | 45
2018-07-20 04:30 | 44 | 44
2018-07-20 05:00 | 45 | 45
2018-07-20 05:30 | 35 | 35
2018-07-20 06:00 | 43 | 43
2018-07-20 06:30 | 35 | 35
2018-07-20 07:00 | 31 | 31
2018-07-20 07:30 | 21 | 21
2018-07-20 08:00 | 4 | 3
2018-07-20 08:30 | 5 | 5
2018-07-20 09:00 | 8 | 8
2018-07-20 09:30 | 7 | 6
2018-07-20 10:00 | 10 | 6
2018-07-20 10:30 | 10 | 1
2018-07-20 11:00 | 11 | 4
2018-07-20 11:30 | 10 | 0
2018-07-20 12:00 | 9 | 3
2018-07-20 12:30 | 11 | 5
2018-07-20 13:00 | 12 | 6
2018-07-20 13:30 | 14 | 6
2018-07-20 14:00 | 13 | 6
2018-07-20 14:30 | 12 | 6
2018-07-20 15:00 | 21 | 18
2018-07-20 15:30 | 22 | 20
2018-07-20 16:00 | 28 | 26
2018-07-20 16:30 | 35 | 34
2018-07-20 17:00 | 41 | 40
2018-07-20 17:30 | 34 | 33
2018-07-20 18:00 | 40 | 39
2018-07-20 18:30 | 41 | 41
2018-07-20 19:00 | 40 | 40
2018-07-20 19:30 | 40 | 40
2018-07-20 20:00 | 39 | 39
2018-07-20 20:30 | 39 | 38
2018-07-20 21:00 | 39 | 38
2018-07-20 21:30 | 53 | 53
2018-07-20 22:00 | 57 | 57
2018-07-20 22:30 | 57 | 57
2018-07-20 23:00 | 55 | 55
2018-07-20 23:30 | 49 | 49
2018-07-21 | 48 | 48
2018-07-21 00:30 | 47 | 47
2018-07-21 01:00 | 47 | 46
2018-07-21 01:30 | 46 | 45
2018-07-21 02:00 | 46 | 45
2018-07-21 02:30 | 46 | 45
2018-07-21 03:00 | 46 | 46
2018-07-21 03:30 | 48 | 48
2018-07-21 04:00 | 49 | 49
2018-07-21 04:30 | 50 | 49
2018-07-21 05:00 | 49 | 48
2018-07-21 05:30 | 49 | 49
2018-07-21 06:00 | 49 | 49
2018-07-21 06:30 | 34 | 34
2018-07-21 07:00 | 30 | 29
2018-07-21 07:30 | 19 | 18
2018-07-21 08:00 | 5 | 1
2018-07-21 08:30 | 12 | 11
2018-07-21 09:00 | 13 | 2
2018-07-21 09:30 | 14 | 6
2018-07-21 10:00 | 14 | 9
2018-07-21 10:30 | 12 | 9
2018-07-21 11:00 | 11 | 8
2018-07-21 11:30 | 11 | 8
2018-07-21 12:00 | 11 | 7
2018-07-21 12:30 | 10 | 6
2018-07-21 13:00 | 9 | 5
2018-07-21 13:30 | 11 | 7
2018-07-21 14:00 | 11 | 7
2018-07-21 14:30 | 9 | 4
2018-07-21 15:00 | 7 | 2
2018-07-21 15:30 | 8 | 2
2018-07-21 16:00 | 21 | 18
2018-07-21 16:30 | 27 | 25
2018-07-21 17:00 | 36 | 35
2018-07-21 17:30 | 46 | 45
2018-07-21 18:00 | 53 | 52
2018-07-21 18:30 | 39 | 38
2018-07-21 19:00 | 35 | 34
2018-07-21 19:30 | 35 | 33
2018-07-21 20:00 | 35 | 32
2018-07-21 20:30 | 35 | 32
2018-07-21 21:00 | 35 | 32
2018-07-21 21:30 | 35 | 31
2018-07-21 22:00 | 34 | 31
2018-07-21 22:30 | 31 | 30
2018-07-21 23:00 | 30 | 29
2018-07-21 23:30 | 29 | 29
2018-07-22 | 46 | 43
2018-07-22 00:30 | 49 | 47
2018-07-22 01:00 | 47 | 46
2018-07-22 01:30 | 47 | 47
2018-07-22 02:00 | 46 | 45
2018-07-22 02:30 | 45 | 45
2018-07-22 03:00 | 45 | 45
2018-07-22 03:30 | 40 | 40
2018-07-22 04:00 | 46 | 46
2018-07-22 04:30 | 46 | 46
2018-07-22 05:00 | 45 | 45
2018-07-22 05:30 | 45 | 44
2018-07-22 06:00 | 44 | 44
2018-07-22 06:30 | 30 | 29
2018-07-22 07:00 | 28 | 26
2018-07-22 07:30 | 16 | 14
2018-07-22 08:00 | 6 | 1
2018-07-22 08:30 | 4 | 1
2018-07-22 09:00 | 2 | 1
2018-07-22 09:30 | 3 | 3
2018-07-22 10:00 | 6 | 5
2018-07-22 10:30 | 4 | 4
2018-07-22 11:00 | 4 | 4
2018-07-22 11:30 | 4 | 4
2018-07-22 12:00 | 3 | 3
2018-07-22 12:30 | 3 | 3
2018-07-22 13:00 | 6 | 6
2018-07-22 13:30 | 10 | 10
2018-07-22 14:00 | 10 | 10
2018-07-22 14:30 | 8 | 8
2018-07-22 15:00 | 17 | 17
2018-07-22 15:30 | 18 | 18
2018-07-22 16:00 | 23 | 23
2018-07-22 16:30 | 28 | 28
2018-07-22 17:00 | 38 | 38
2018-07-22 17:30 | 25 | 25
2018-07-22 18:00 | 27 | 27
2018-07-22 18:30 | 24 | 24
2018-07-22 19:00 | 28 | 28
2018-07-22 19:30 | 29 | 29
2018-07-22 20:00 | 29 | 29
2018-07-22 20:30 | 28 | 28
2018-07-22 21:00 | 28 | 28
2018-07-22 21:30 | 39 | 39
2018-07-22 22:00 | 46 | 46
2018-07-22 22:30 | 45 | 44
2018-07-22 23:00 | 44 | 43
2018-07-22 23:30 | 43 | 43
2018-07-23 | 43 | 43
2018-07-23 00:30 | 42 | 42
2018-07-23 01:00 | 42 | 42
2018-07-23 01:30 | 43 | 42
2018-07-23 02:00 | 42 | 41
2018-07-23 02:30 | 42 | 42
2018-07-23 03:00 | 43 | 42
2018-07-23 03:30 | 42 | 42
2018-07-23 04:00 | 42 | 42
2018-07-23 04:30 | 42 | 42
2018-07-23 05:00 | 42 | 42
2018-07-23 05:30 | 42 | 41
2018-07-23 06:00 | 43 | 42
2018-07-23 06:30 | 27 | 27
2018-07-23 07:00 | 26 | 26
2018-07-23 07:30 | 27 | 26
2018-07-23 08:00 | 24 | 23
2018-07-23 08:30 | 33 | 33
2018-07-23 09:00 | 26 | 26
2018-07-23 09:30 | 21 | 21
2018-07-23 10:00 | 19 | 19
2018-07-23 10:30 | 19 | 19
2018-07-23 11:00 | 19 | 19
2018-07-23 11:30 | 21 | 21
2018-07-23 12:00 | 21 | 20
2018-07-23 12:30 | 19 | 19
2018-07-23 13:00 | 20 | 20
2018-07-23 13:30 | 27 | 27
2018-07-23 14:00 | 23 | 23
2018-07-23 14:30 | 23 | 22
2018-07-23 15:00 | 25 | 25
2018-07-23 15:30 | 32 | 32
2018-07-23 16:00 | 49 | 49
2018-07-23 16:30 | 52 | 52
2018-07-23 17:00 | 53 | 53
2018-07-23 17:30 | 36 | 36
2018-07-23 18:00 | 37 | 37
2018-07-23 18:30 | 38 | 38
2018-07-23 19:00 | 38 | 38
2018-07-23 19:30 | 38 | 38
2018-07-23 20:00 | 37 | 37
2018-07-23 20:30 | 36 | 36
2018-07-23 21:00 | 37 | 37
2018-07-23 21:30 | 36 | 36
2018-07-23 22:00 | 35 | 35
2018-07-23 22:30 | 32 | 32
2018-07-23 23:00 | 42 | 42
2018-07-23 23:30 | 50 | 49
2018-07-24 | 49 | 48
2018-07-24 00:30 | 48 | 48
2018-07-24 01:00 | 51 | 51
2018-07-24 01:30 | 54 | 53
2018-07-24 02:00 | 54 | 54
2018-07-24 02:30 | 54 | 54
2018-07-24 03:00 | 54 | 54
2018-07-24 03:30 | 52 | 52
2018-07-24 04:00 | 53 | 52
2018-07-24 04:30 | 53 | 52
2018-07-24 05:00 | 54 | 53
2018-07-24 05:30 | 54 | 53
2018-07-24 06:00 | 54 | 54
2018-07-24 06:30 | 37 | 37
2018-07-24 07:00 | 36 | 35
2018-07-24 07:30 | 34 | 34
2018-07-24 08:00 | 29 | 28
2018-07-24 08:30 | 24 | 23
2018-07-24 09:00 | 35 | 35
2018-07-24 09:30 | 30 | 29
2018-07-24 10:00 | 28 | 28
2018-07-24 10:30 | 26 | 26
2018-07-24 11:00 | 28 | 27
2018-07-24 11:30 | 33 | 32
2018-07-24 12:00 | 30 | 28
2018-07-24 12:30 | 29 | 27
2018-07-24 13:00 | 29 | 27
2018-07-24 13:30 | 29 | 27
2018-07-24 14:00 | 30 | 29
2018-07-24 14:30 | 32 | 30
2018-07-24 15:00 | 36 | 35
2018-07-24 15:30 | 44 | 43
2018-07-24 16:00 | 42 | 41
2018-07-24 16:30 | 51 | 50
2018-07-24 17:00 | 58 | 57
2018-07-24 17:30 | 43 | 42
2018-07-24 18:00 | 41 | 40
2018-07-24 18:30 | 42 | 42
2018-07-24 19:00 | 42 | 42
2018-07-24 19:30 | 42 | 42
2018-07-24 20:00 | 41 | 41
2018-07-24 20:30 | 39 | 39
2018-07-24 21:00 | 35 | 35
2018-07-24 21:30 | 51 | 50
2018-07-24 22:00 | 54 | 53
2018-07-24 22:30 | 53 | 52
2018-07-24 23:00 | 52 | 51
2018-07-24 23:30 | 49 | 48
2018-07-25 | 46 | 45
2018-07-25 00:30 | 45 | 44
2018-07-25 01:00 | 45 | 44
2018-07-25 01:30 | 44 | 43
2018-07-25 02:00 | 44 | 43
2018-07-25 02:30 | 44 | 43
2018-07-25 03:00 | 44 | 43
2018-07-25 03:30 | 46 | 45
2018-07-25 04:00 | 47 | 46
2018-07-25 04:30 | 49 | 48
2018-07-25 05:00 | 48 | 47
2018-07-25 05:30 | 48 | 48
2018-07-25 06:00 | 49 | 48
2018-07-25 06:30 | 31 | 31
2018-07-25 07:00 | 32 | 31
2018-07-25 07:30 | 28 | 27
2018-07-25 08:00 | 21 | 21
2018-07-25 08:30 | 16 | 15
2018-07-25 09:00 | 25 | 25
2018-07-25 09:30 | 21 | 21
2018-07-25 10:00 | 18 | 18
2018-07-25 10:30 | 19 | 19
2018-07-25 11:00 | 22 | 22
2018-07-25 11:30 | 21 | 21
2018-07-25 12:00 | 20 | 20
2018-07-25 12:30 | 19 | 19
2018-07-25 13:00 | 23 | 23
2018-07-25 13:30 | 26 | 26
2018-07-25 14:00 | 27 | 27
2018-07-25 14:30 | 22 | 22
2018-07-25 15:00 | 19 | 19
2018-07-25 15:30 | 36 | 35
2018-07-25 16:00 | 31 | 29
2018-07-25 16:30 | 39 | 34
2018-07-25 17:00 | 46 | 43
2018-07-25 17:30 | 58 | 55
2018-07-25 18:00 | 54 | 48
2018-07-25 18:30 | 56 | 49
2018-07-25 19:00 | 50 | 43
2018-07-25 19:30 | 46 | 38
2018-07-25 20:00 | 47 | 39
2018-07-25 20:30 | 47 | 38
2018-07-25 21:00 | 47 | 37
2018-07-25 21:30 | 53 | 49
2018-07-25 22:00 | 56 | 54
2018-07-25 22:30 | 53 | 53
2018-07-25 23:00 | 49 | 48
2018-07-25 23:30 | 45 | 43
2018-07-26 | 44 | 43
2018-07-26 00:30 | 44 | 43
2018-07-26 01:00 | 44 | 43
2018-07-26 01:30 | 43 | 42
2018-07-26 02:00 | 43 | 42
2018-07-26 02:30 | 43 | 42
2018-07-26 03:00 | 43 | 42
2018-07-26 03:30 | 43 | 42
2018-07-26 04:00 | 43 | 42
2018-07-26 04:30 | 44 | 43
2018-07-26 05:00 | 43 | 43
2018-07-26 05:30 | 44 | 43
2018-07-26 06:00 | 45 | 44
2018-07-26 06:30 | 47 | 46
2018-07-26 07:00 | 47 | 46
2018-07-26 07:30 | 28 | 27
2018-07-26 08:00 | 23 | 22
2018-07-26 08:30 | 21 | 21
2018-07-26 09:00 | 17 | 17
2018-07-26 09:30 | 20 | 20
2018-07-26 10:00 | 22 | 17
2018-07-26 10:30 | 21 | 16
2018-07-26 11:00 | 21 | 17
2018-07-26 11:30 | 21 | 16
2018-07-26 12:00 | 19 | 11
2018-07-26 12:30 | 18 | 9
2018-07-26 13:00 | 17 | 9
2018-07-26 13:30 | 18 | 10
2018-07-26 14:00 | 20 | 13
2018-07-26 14:30 | 23 | 18
2018-07-26 15:00 | 28 | 25
2018-07-26 15:30 | 27 | 24
2018-07-26 16:00 | 24 | 23
2018-07-26 16:30 | 31 | 31
2018-07-26 17:00 | 44 | 44
2018-07-26 17:30 | 41 | 41
2018-07-26 18:00 | 47 | 47
2018-07-26 18:30 | 52 | 52
2018-07-26 19:00 | 49 | 49
2018-07-26 19:30 | 44 | 44
2018-07-26 20:00 | 43 | 43
2018-07-26 20:30 | 56 | 55
2018-07-26 21:00 | 57 | 56
2018-07-26 21:30 | 55 | 54
2018-07-26 22:00 | 54 | 53
2018-07-26 22:30 | 51 | 50
2018-07-26 23:00 | 49 | 47
2018-07-26 23:30 | 47 | 45
2018-07-27 | 45 | 44
2018-07-27 00:30 | 44 | 44
2018-07-27 01:00 | 45 | 44
2018-07-27 01:30 | 44 | 43
2018-07-27 02:00 | 51 | 51
2018-07-27 02:30 | 54 | 53
2018-07-27 03:00 | 38 | 38
2018-07-27 03:30 | 54 | 53
2018-07-27 04:00 | 53 | 52
2018-07-27 04:30 | 53 | 53
2018-07-27 05:00 | 49 | 48
2018-07-27 05:30 | 45 | 45
2018-07-27 06:00 | 46 | 45
2018-07-27 06:30 | 36 | 36
2018-07-27 07:00 | 33 | 33
2018-07-27 07:30 | 31 | 31
2018-07-27 08:00 | 30 | 30
2018-07-27 08:30 | 26 | 26
2018-07-27 09:00 | 19 | 19
2018-07-27 09:30 | 12 | 12
2018-07-27 10:00 | 9 | 9
2018-07-27 10:30 | 10 | 10
2018-07-27 11:00 | 11 | 11
2018-07-27 11:30 | 9 | 9
2018-07-27 12:00 | 8 | 8
2018-07-27 12:30 | 5 | 4
2018-07-27 13:00 | 3 | 2
2018-07-27 13:30 | 3 | 1
2018-07-27 14:00 | 7 | 7
2018-07-27 14:30 | 20 | 20
2018-07-27 15:00 | 17 | 16
2018-07-27 15:30 | 10 | 5
2018-07-27 16:00 | 14 | 13
2018-07-27 16:30 | 10 | 7
2018-07-27 17:00 | 29 | 29
2018-07-27 17:30 | 46 | 45
2018-07-27 18:00 | 60 | 60
2018-07-27 18:30 | 62 | 62
2018-07-27 19:00 | 62 | 62
2018-07-27 19:30 | 62 | 62
2018-07-27 20:00 | 59 | 59
2018-07-27 20:30 | 58 | 58
2018-07-27 21:00 | 57 | 57
2018-07-27 21:30 | 56 | 56
2018-07-27 22:00 | 54 | 53
2018-07-27 22:30 | 49 | 49
2018-07-27 23:00 | 45 | 45
2018-07-27 23:30 | 43 | 42
2018-07-28 | 41 | 41
2018-07-28 00:30 | 41 | 40
2018-07-28 01:00 | 41 | 41
2018-07-28 01:30 | 40 | 40
2018-07-28 02:00 | 40 | 40
2018-07-28 02:30 | 40 | 40
2018-07-28 03:00 | 40 | 40
2018-07-28 03:30 | 40 | 40
2018-07-28 04:00 | 46 | 45
2018-07-28 04:30 | 50 | 50
2018-07-28 05:00 | 46 | 46
2018-07-28 05:30 | 45 | 45
2018-07-28 06:00 | 47 | 46
2018-07-28 06:30 | 46 | 46
2018-07-28 07:00 | 47 | 46
2018-07-28 07:30 | 45 | 45
2018-07-28 08:00 | 36 | 36
2018-07-28 08:30 | 26 | 26
2018-07-28 09:00 | 19 | 19
2018-07-28 09:30 | 13 | 13
2018-07-28 10:00 | 10 | 8
2018-07-28 10:30 | 8 | 6
2018-07-28 11:00 | 9 | 8
2018-07-28 11:30 | 7 | 6
2018-07-28 12:00 | 5 | 4
2018-07-28 12:30 | 6 | 4
2018-07-28 13:00 | 7 | 5
2018-07-28 13:30 | 5 | 4
2018-07-28 14:00 | 5 | 3
2018-07-28 14:30 | 3 | 0
2018-07-28 15:00 | 6 | 5
2018-07-28 15:30 | 7 | 7
2018-07-28 16:00 | 13 | 13
2018-07-28 16:30 | 20 | 20
2018-07-28 17:00 | 31 | 31
2018-07-28 17:30 | 46 | 46
2018-07-28 18:00 | 55 | 55
2018-07-28 18:30 | 59 | 59
2018-07-28 19:00 | 57 | 57
2018-07-28 19:30 | 56 | 55
2018-07-28 20:00 | 57 | 56
2018-07-28 20:30 | 58 | 57
2018-07-28 21:00 | 57 | 56
2018-07-28 21:30 | 57 | 56
2018-07-28 22:00 | 57 | 55
2018-07-28 22:30 | 54 | 53
2018-07-28 23:00 | 53 | 51
2018-07-28 23:30 | 49 | 49
2018-07-29 | 48 | 47
2018-07-29 00:30 | 47 | 47
2018-07-29 01:00 | 48 | 47
2018-07-29 01:30 | 48 | 47
2018-07-29 02:00 | 46 | 46
2018-07-29 02:30 | 46 | 46
2018-07-29 03:00 | 46 | 46
2018-07-29 03:30 | 45 | 45
2018-07-29 04:00 | 45 | 44
2018-07-29 04:30 | 45 | 45
2018-07-29 05:00 | 47 | 47
2018-07-29 05:30 | 48 | 47
2018-07-29 06:00 | 47 | 47
2018-07-29 06:30 | 49 | 49
2018-07-29 07:00 | 49 | 49
2018-07-29 07:30 | 45 | 45
2018-07-29 08:00 | 34 | 33
2018-07-29 08:30 | 24 | 24
2018-07-29 09:00 | 20 | 19
2018-07-29 09:30 | 11 | 10
2018-07-29 10:00 | 11 | 10
2018-07-29 10:30 | 11 | 11
2018-07-29 11:00 | 6 | 6
2018-07-29 11:30 | 11 | 7
2018-07-29 12:00 | 5 | 4
2018-07-29 12:30 | 4 | 4
2018-07-29 13:00 | 3 | 2
2018-07-29 13:30 | 4 | 3
2018-07-29 14:00 | 3 | 3
2018-07-29 14:30 | 4 | 4
2018-07-29 15:00 | 5 | 4
2018-07-29 15:30 | 6 | 5
2018-07-29 16:00 | 9 | 9
2018-07-29 16:30 | 16 | 16
2018-07-29 17:00 | 28 | 28
2018-07-29 17:30 | 40 | 40
2018-07-29 18:00 | 48 | 48
2018-07-29 18:30 | 51 | 51
2018-07-29 19:00 | 53 | 52
2018-07-29 19:30 | 52 | 51
2018-07-29 20:00 | 53 | 52
2018-07-29 20:30 | 55 | 54
2018-07-29 21:00 | 52 | 51
2018-07-29 21:30 | 52 | 50
2018-07-29 22:00 | 51 | 49
2018-07-29 22:30 | 51 | 49
2018-07-29 23:00 | 50 | 47
2018-07-29 23:30 | 49 | 46
2018-07-30 | 50 | 46
2018-07-30 00:30 | 48 | 45
2018-07-30 01:00 | 48 | 45
2018-07-30 01:30 | 41 | 38
2018-07-30 02:00 | 46 | 45
2018-07-30 02:30 | 45 | 45
2018-07-30 03:00 | 47 | 46
2018-07-30 03:30 | 47 | 46
2018-07-30 04:00 | 46 | 46
2018-07-30 04:30 | 46 | 45
2018-07-30 05:00 | 46 | 46
2018-07-30 05:30 | 45 | 45
2018-07-30 06:00 | 46 | 45
2018-07-30 06:30 | 46 | 46
2018-07-30 07:00 | 48 | 48
2018-07-30 07:30 | 44 | 43
2018-07-30 08:00 | 29 | 27
2018-07-30 08:30 | 16 | 4
2018-07-30 09:00 | 13 | 2
2018-07-30 09:30 | 15 | 10
2018-07-30 10:00 | 20 | 17
2018-07-30 10:30 | 23 | 21
2018-07-30 11:00 | 34 | 32
2018-07-30 11:30 | 45 | 44
2018-07-30 12:00 | 47 | 46
2018-07-30 12:30 | 45 | 45
2018-07-30 13:00 | 46 | 46
2018-07-30 13:30 | 47 | 47
2018-07-30 14:00 | 46 | 46
2018-07-30 14:30 | 27 | 27
2018-07-30 15:00 | 5 | 5
2018-07-30 15:30 | 10 | 10
2018-07-30 16:00 | 8 | 8
2018-07-30 16:30 | 0 | 0
2018-07-30 17:00 | 1 | 1
2018-07-30 17:30 | 25 | 25
2018-07-30 18:00 | 39 | 39
2018-07-30 18:30 | 42 | 40
2018-07-30 19:00 | 35 | 34
2018-07-30 19:30 | 30 | 30
2018-07-30 20:00 | 31 | 30
2018-07-30 20:30 | 34 | 33
2018-07-30 21:00 | 34 | 34
2018-07-30 21:30 | 35 | 34
2018-07-30 22:00 | 37 | 35
2018-07-30 22:30 | 36 | 35
2018-07-30 23:00 | 36 | 34
2018-07-30 23:30 | 34 | 33
2018-07-31 | 35 | 34
2018-07-31 00:30 | 35 | 34
2018-07-31 01:00 | 36 | 36
2018-07-31 01:30 | 34 | 34
2018-07-31 02:00 | 29 | 29
2018-07-31 02:30 | 31 | 30
2018-07-31 03:00 | 30 | 29
2018-07-31 03:30 | 30 | 29
2018-07-31 04:00 | 29 | 28
2018-07-31 04:30 | 30 | 29
2018-07-31 05:00 | 31 | 30
2018-07-31 05:30 | 30 | 29
2018-07-31 06:00 | 31 | 30
2018-07-31 06:30 | 31 | 30
2018-07-31 07:00 | 31 | 30
2018-07-31 07:30 | 22 | 22
2018-07-31 08:00 | 10 | 8
2018-07-31 08:30 | 8 | 4
2018-07-31 09:00 | 10 | 8
2018-07-31 09:30 | 15 | 13
2018-07-31 10:00 | 19 | 17
2018-07-31 10:30 | 22 | 22
2018-07-31 11:00 | 48 | 47
2018-07-31 11:30 | 48 | 48
2018-07-31 12:00 | 44 | 44
2018-07-31 12:30 | 43 | 43
2018-07-31 13:00 | 48 | 47
2018-07-31 13:30 | 36 | 36
2018-07-31 14:00 | 31 | 31
2018-07-31 14:30 | 35 | 35
2018-07-31 15:00 | 21 | 21
2018-07-31 15:30 | 19 | 19
2018-07-31 16:00 | 12 | 12
2018-07-31 16:30 | 4 | 3
2018-07-31 17:00 | 9 | 8
2018-07-31 17:30 | 29 | 23
2018-07-31 18:00 | 35 | 30
2018-07-31 18:30 | 34 | 30
2018-07-31 19:00 | 29 | 26
2018-07-31 19:30 | 30 | 27
2018-07-31 20:00 | 30 | 26
2018-07-31 20:30 | 31 | 27
2018-07-31 21:00 | 29 | 26
2018-07-31 21:30 | 24 | 11
2018-07-31 22:00 | 27 | 25
2018-07-31 22:30 | 30 | 28
2018-07-31 23:00 | 30 | 29
2018-07-31 23:30 | 30 | 28
2018-08-01 | 30 | 29
2018-08-01 00:30 | 30 | 29
2018-08-01 01:00 | 30 | 28
2018-08-01 01:30 | 30 | 29
2018-08-01 02:00 | 31 | 29
2018-08-01 02:30 | 31 | 31
2018-08-01 03:00 | 32 | 31
2018-08-01 03:30 | 34 | 34
2018-08-01 04:00 | 34 | 34
2018-08-01 04:30 | 33 | 33
2018-08-01 05:00 | 33 | 32
2018-08-01 05:30 | 34 | 33
2018-08-01 06:00 | 36 | 35
2018-08-01 06:30 | 36 | 36
2018-08-01 07:00 | 37 | 37
2018-08-01 07:30 | 33 | 33
2018-08-01 08:00 | 21 | 20
2018-08-01 08:30 | 10 | 9
2018-08-01 09:00 | 4 | 3
2018-08-01 09:30 | 2 | 0
2018-08-01 10:00 | 5 | 3
2018-08-01 10:30 | 12 | 7
2018-08-01 11:00 | 6 | 4
2018-08-01 11:30 | 7 | 4
2018-08-01 12:00 | 8 | 4
2018-08-01 12:30 | 3 | 1
2018-08-01 13:00 | 2 | 2
2018-08-01 13:30 | 8 | 6
2018-08-01 14:00 | 8 | 5
2018-08-01 14:30 | 8 | 5
2018-08-01 15:00 | 10 | 7
2018-08-01 15:30 | 11 | 8
2018-08-01 16:00 | 8 | 4
2018-08-01 16:30 | 13 | 8
2018-08-01 17:00 | 11 | 6
2018-08-01 17:30 | 28 | 28
2018-08-01 18:00 | 42 | 41
2018-08-01 18:30 | 45 | 44
2018-08-01 19:00 | 35 | 27
2018-08-01 19:30 | 39 | 32
2018-08-01 20:00 | 43 | 38
2018-08-01 20:30 | 44 | 39
2018-08-01 21:00 | 45 | 40
2018-08-01 21:30 | 44 | 40
2018-08-01 22:00 | 43 | 39
2018-08-01 22:30 | 42 | 37
2018-08-01 23:00 | 44 | 39
2018-08-01 23:30 | 44 | 39
2018-08-02 | 40 | 35
2018-08-02 00:30 | 36 | 33
2018-08-02 01:00 | 28 | 27
2018-08-02 01:30 | 28 | 27
2018-08-02 02:00 | 28 | 27
2018-08-02 02:30 | 29 | 28
2018-08-02 03:00 | 31 | 30
2018-08-02 03:30 | 31 | 29
2018-08-02 04:00 | 31 | 30
2018-08-02 04:30 | 32 | 31
2018-08-02 05:00 | 33 | 32
2018-08-02 05:30 | 34 | 32
2018-08-02 06:00 | 35 | 33
2018-08-02 06:30 | 31 | 31
2018-08-02 07:00 | 33 | 30
2018-08-02 07:30 | 19 | 13
2018-08-02 08:00 | 13 | 8
2018-08-02 08:30 | 10 | 1
2018-08-02 09:00 | 12 | 7
2018-08-02 09:30 | 15 | 11
2018-08-02 10:00 | 17 | 13
2018-08-02 10:30 | 16 | 14
2018-08-02 11:00 | 13 | 10
2018-08-02 11:30 | 14 | 10
2018-08-02 12:00 | 14 | 11
2018-08-02 12:30 | 13 | 10
2018-08-02 13:00 | 13 | 9
2018-08-02 13:30 | 12 | 8
2018-08-02 14:00 | 12 | 8
2018-08-02 14:30 | 13 | 10
2018-08-02 15:00 | 14 | 11
2018-08-02 15:30 | 14 | 10
2018-08-02 16:00 | 10 | 5
2018-08-02 16:30 | 9 | 4
2018-08-02 17:00 | 15 | 13
2018-08-02 17:30 | 26 | 26
2018-08-02 18:00 | 32 | 32
2018-08-02 18:30 | 31 | 30
2018-08-02 19:00 | 28 | 24
2018-08-02 19:30 | 29 | 27
2018-08-02 20:00 | 31 | 29
2018-08-02 20:30 | 31 | 29
2018-08-02 21:00 | 32 | 30
2018-08-02 21:30 | 32 | 30
2018-08-02 22:00 | 32 | 32
2018-08-02 22:30 | 34 | 32
2018-08-02 23:00 | 35 | 33
2018-08-02 23:30 | 34 | 32
2018-08-03 | 35 | 33
2018-08-03 00:30 | 35 | 34
2018-08-03 01:00 | 33 | 31
2018-08-03 01:30 | 32 | 30
2018-08-03 02:00 | 32 | 30
2018-08-03 02:30 | 33 | 31
2018-08-03 03:00 | 32 | 31
2018-08-03 03:30 | 32 | 31
2018-08-03 04:00 | 32 | 30
2018-08-03 04:30 | 30 | 29
2018-08-03 05:00 | 30 | 28
2018-08-03 05:30 | 30 | 29
2018-08-03 06:00 | 31 | 30
2018-08-03 06:30 | 30 | 28
2018-08-03 07:00 | 30 | 28
2018-08-03 07:30 | 22 | 21
2018-08-03 08:00 | 10 | 8
2018-08-03 08:30 | 3 | 2
2018-08-03 09:00 | 8 | 8
2018-08-03 09:30 | 12 | 12
2018-08-03 10:00 | 11 | 11
2018-08-03 10:30 | 14 | 14
2018-08-03 11:00 | 10 | 10
2018-08-03 11:30 | 12 | 12
2018-08-03 12:00 | 5 | 4
2018-08-03 12:30 | 13 | 13
2018-08-03 13:00 | 10 | 10
2018-08-03 13:30 | 12 | 12
2018-08-03 14:00 | 11 | 10
2018-08-03 14:30 | 10 | 9
2018-08-03 15:00 | 12 | 12
2018-08-03 15:30 | 14 | 14
2018-08-03 16:00 | 11 | 11
2018-08-03 16:30 | 3 | 0
2018-08-03 17:00 | 11 | 10
2018-08-03 17:30 | 29 | 28
2018-08-03 18:00 | 44 | 43
2018-08-03 18:30 | 48 | 46
2018-08-03 19:00 | 43 | 41
2018-08-03 19:30 | 39 | 37
2018-08-03 20:00 | 38 | 36
2018-08-03 20:30 | 34 | 32
2018-08-03 21:00 | 30 | 30
2018-08-03 21:30 | 35 | 34
2018-08-03 22:00 | 36 | 35
2018-08-03 22:30 | 36 | 34
2018-08-03 23:00 | 35 | 34
2018-08-03 23:30 | 34 | 33
2018-08-04 | 35 | 33
2018-08-04 00:30 | 33 | 32
2018-08-04 01:00 | 33 | 32
2018-08-04 01:30 | 34 | 33
2018-08-04 02:00 | 35 | 34
2018-08-04 02:30 | 35 | 34
2018-08-04 03:00 | 33 | 33
2018-08-04 03:30 | 34 | 33
2018-08-04 04:00 | 33 | 33
2018-08-04 04:30 | 33 | 32
2018-08-04 05:00 | 34 | 33
2018-08-04 05:30 | 36 | 35
2018-08-04 06:00 | 34 | 34
2018-08-04 06:30 | 35 | 34
2018-08-04 07:00 | 36 | 35
2018-08-04 07:30 | 34 | 34
2018-08-04 08:00 | 22 | 21
2018-08-04 08:30 | 10 | 8
2018-08-04 09:00 | 8 | 1
2018-08-04 09:30 | 9 | 4
2018-08-04 10:00 | 10 | 6
2018-08-04 10:30 | 13 | 8
2018-08-04 11:00 | 14 | 9
2018-08-04 11:30 | 11 | 5
2018-08-04 12:00 | 10 | 3
2018-08-04 12:30 | 12 | 6
2018-08-04 13:00 | 7 | 6
2018-08-04 13:30 | 4 | 4
2018-08-04 14:00 | 10 | 7
2018-08-04 14:30 | 11 | 5
2018-08-04 15:00 | 12 | 11
2018-08-04 15:30 | 11 | 9
2018-08-04 16:00 | 6 | 3
2018-08-04 16:30 | 7 | 4
2018-08-04 17:00 | 16 | 15
2018-08-04 17:30 | 27 | 27
2018-08-04 18:00 | 34 | 33
2018-08-04 18:30 | 36 | 36
2018-08-04 19:00 | 39 | 36
2018-08-04 19:30 | 39 | 36
2018-08-04 20:00 | 38 | 36
2018-08-04 20:30 | 40 | 37
2018-08-04 21:00 | 37 | 35
2018-08-04 21:30 | 35 | 35
2018-08-04 22:00 | 35 | 34
2018-08-04 22:30 | 34 | 34
2018-08-04 23:00 | 34 | 33
2018-08-04 23:30 | 34 | 34
2018-08-05 | 36 | 36
2018-08-05 00:30 | 35 | 35
2018-08-05 01:00 | 34 | 34
2018-08-05 01:30 | 34 | 33
2018-08-05 02:00 | 35 | 35
2018-08-05 02:30 | 34 | 33
2018-08-05 03:00 | 34 | 34
2018-08-05 03:30 | 34 | 34
2018-08-05 04:00 | 34 | 34
2018-08-05 04:30 | 24 | 24
2018-08-05 05:00 | 35 | 34
2018-08-05 05:30 | 35 | 35
2018-08-05 06:00 | 35 | 34
2018-08-05 06:30 | 35 | 34
2018-08-05 07:00 | 37 | 36
2018-08-05 07:30 | 31 | 31
2018-08-05 08:00 | 18 | 18
2018-08-05 08:30 | 10 | 9
2018-08-05 09:00 | 4 | 0
2018-08-05 09:30 | 8 | 7
2018-08-05 10:00 | 4 | 2
2018-08-05 10:30 | 4 | 2
2018-08-05 11:00 | 12 | 11
2018-08-05 11:30 | 9 | 8
2018-08-05 12:00 | 7 | 6
2018-08-05 12:30 | 10 | 9
2018-08-05 13:00 | 9 | 9
2018-08-05 13:30 | 7 | 6
2018-08-05 14:00 | 4 | 2
2018-08-05 14:30 | 9 | 8
2018-08-05 15:00 | 12 | 10
2018-08-05 15:30 | 11 | 7
2018-08-05 16:00 | 10 | 5
2018-08-05 16:30 | 9 | 6
2018-08-05 17:00 | 16 | 14
2018-08-05 17:30 | 30 | 29
2018-08-05 18:00 | 43 | 43
2018-08-05 18:30 | 46 | 46
2018-08-05 19:00 | 36 | 31
2018-08-05 19:30 | 30 | 30
2018-08-05 20:00 | 41 | 40
2018-08-05 20:30 | 41 | 41
2018-08-05 21:00 | 43 | 42
2018-08-05 21:30 | 42 | 42
2018-08-05 22:00 | 39 | 38
2018-08-05 22:30 | 39 | 38
2018-08-05 23:00 | 39 | 39
2018-08-05 23:30 | 38 | 37
2018-08-06 | 38 | 37
2018-08-06 00:30 | 39 | 38
2018-08-06 01:00 | 38 | 37
2018-08-06 01:30 | 37 | 36
2018-08-06 02:00 | 38 | 37
2018-08-06 02:30 | 37 | 37
2018-08-06 03:00 | 35 | 34
2018-08-06 03:30 | 35 | 35
2018-08-06 04:00 | 38 | 37
2018-08-06 04:30 | 37 | 37
2018-08-06 05:00 | 36 | 36
2018-08-06 05:30 | 37 | 37
2018-08-06 06:00 | 36 | 36
2018-08-06 06:30 | 36 | 35
2018-08-06 07:00 | 36 | 36
2018-08-06 07:30 | 33 | 31
2018-08-06 08:00 | 24 | 21
2018-08-06 08:30 | 16 | 10
2018-08-06 09:00 | 12 | 5
2018-08-06 09:30 | 12 | 1
2018-08-06 10:00 | 12 | 3
2018-08-06 10:30 | 13 | 5
2018-08-06 11:00 | 17 | 11
2018-08-06 11:30 | 16 | 10
2018-08-06 12:00 | 21 | 15
2018-08-06 12:30 | 19 | 12
2018-08-06 13:00 | 18 | 12
2018-08-06 13:30 | 20 | 13
2018-08-06 14:00 | 20 | 13
2018-08-06 14:30 | 18 | 12
2018-08-06 15:00 | 12 | 7
2018-08-06 15:30 | 15 | 13
2018-08-06 16:00 | 13 | 4
2018-08-06 16:30 | 14 | 6
2018-08-06 17:00 | 28 | 26
2018-08-06 17:30 | 42 | 41
2018-08-06 18:00 | 54 | 54
2018-08-06 18:30 | 52 | 52
2018-08-06 19:00 | 34 | 34
2018-08-06 19:30 | 37 | 37
2018-08-06 20:00 | 45 | 45
2018-08-06 20:30 | 48 | 48
2018-08-06 21:00 | 49 | 48
2018-08-06 21:30 | 47 | 47
2018-08-06 22:00 | 44 | 44
2018-08-06 22:30 | 46 | 45
2018-08-06 23:00 | 41 | 40
2018-08-06 23:30 | 38 | 38
2018-08-07 | 37 | 37
2018-08-07 00:30 | 38 | 38
2018-08-07 01:00 | 40 | 39
2018-08-07 01:30 | 38 | 38
2018-08-07 02:00 | 38 | 38
2018-08-07 02:30 | 40 | 40
2018-08-07 03:00 | 44 | 44
2018-08-07 03:30 | 44 | 44
2018-08-07 04:00 | 46 | 46
2018-08-07 04:30 | 48 | 48
2018-08-07 05:00 | 50 | 50
2018-08-07 05:30 | 51 | 51
2018-08-07 06:00 | 51 | 51
2018-08-07 06:30 | 50 | 50
2018-08-07 07:00 | 50 | 50
2018-08-07 07:30 | 45 | 45
2018-08-07 08:00 | 42 | 42
2018-08-07 08:30 | 39 | 39
2018-08-07 09:00 | 41 | 39
2018-08-07 09:30 | 30 | 25
2018-08-07 10:00 | 39 | 35
2018-08-07 10:30 | 37 | 33
2018-08-07 11:00 | 35 | 30
2018-08-07 11:30 | 38 | 33
2018-08-07 12:00 | 38 | 33
2018-08-07 12:30 | 32 | 27
2018-08-07 13:00 | 37 | 33
2018-08-07 13:30 | 29 | 23
2018-08-07 14:00 | 21 | 16
2018-08-07 14:30 | 12 | 11
2018-08-07 15:00 | 18 | 18
2018-08-07 15:30 | 27 | 27
2018-08-07 16:00 | 34 | 33
2018-08-07 16:30 | 40 | 39
2018-08-07 17:00 | 49 | 47
2018-08-07 17:30 | 53 | 50
2018-08-07 18:00 | 55 | 52
2018-08-07 18:30 | 53 | 50
2018-08-07 19:00 | 53 | 50
2018-08-07 19:30 | 52 | 48
2018-08-07 20:00 | 50 | 47
2018-08-07 20:30 | 47 | 44
2018-08-07 21:00 | 46 | 43
2018-08-07 21:30 | 47 | 43
2018-08-07 22:00 | 43 | 40
2018-08-07 22:30 | 41 | 38
2018-08-07 23:00 | 39 | 34
2018-08-07 23:30 | 32 | 32
2018-08-08 | 32 | 31
2018-08-08 00:30 | 32 | 32
2018-08-08 01:00 | 33 | 33
2018-08-08 01:30 | 34 | 33
2018-08-08 02:00 | 25 | 25
2018-08-08 02:30 | 35 | 34
2018-08-08 03:00 | 33 | 32
2018-08-08 03:30 | 34 | 33
2018-08-08 04:00 | 33 | 33
2018-08-08 04:30 | 35 | 34
2018-08-08 05:00 | 34 | 33
2018-08-08 05:30 | 33 | 32
2018-08-08 06:00 | 38 | 38
2018-08-08 06:30 | 42 | 41
2018-08-08 07:00 | 23 | 22
2018-08-08 07:30 | 13 | 6
2018-08-08 08:00 | 14 | 8
2018-08-08 08:30 | 18 | 15
2018-08-08 09:00 | 14 | 10
2018-08-08 09:30 | 9 | 4
2018-08-08 10:00 | 8 | 1
2018-08-08 10:30 | 8 | 3
2018-08-08 11:00 | 8 | 3
2018-08-08 11:30 | 8 | 0
2018-08-08 12:00 | 10 | 3
2018-08-08 12:30 | 9 | 3
2018-08-08 13:00 | 6 | 1
2018-08-08 13:30 | 5 | 5
2018-08-08 14:00 | 6 | 6
2018-08-08 14:30 | 6 | 6
2018-08-08 15:00 | 6 | 6
2018-08-08 15:30 | 4 | 4
2018-08-08 16:00 | 2 | 0
2018-08-08 16:30 | 5 | 5
2018-08-08 17:00 | 19 | 19
2018-08-08 17:30 | 31 | 31
2018-08-08 18:00 | 41 | 41
2018-08-08 18:30 | 32 | 32
2018-08-08 19:00 | 25 | 24
2018-08-08 19:30 | 35 | 35
2018-08-08 20:00 | 25 | 25
2018-08-08 20:30 | 22 | 20
2018-08-08 21:00 | 39 | 39
2018-08-08 21:30 | 42 | 41
2018-08-08 22:00 | 41 | 41
2018-08-08 22:30 | 40 | 39
2018-08-08 23:00 | 34 | 33
2018-08-08 23:30 | 35 | 34
2018-08-09 | 35 | 34
2018-08-09 00:30 | 34 | 33
2018-08-09 01:00 | 35 | 34
2018-08-09 01:30 | 35 | 34
2018-08-09 02:00 | 36 | 35
2018-08-09 02:30 | 34 | 34
2018-08-09 03:00 | 34 | 34
2018-08-09 03:30 | 34 | 34
2018-08-09 04:00 | 35 | 34
2018-08-09 04:30 | 34 | 33
2018-08-09 05:00 | 34 | 34
2018-08-09 05:30 | 34 | 33
2018-08-09 06:00 | 35 | 34
2018-08-09 06:30 | 35 | 35
2018-08-09 07:00 | 20 | 20
2018-08-09 07:30 | 10 | 5
2018-08-09 08:00 | 8 | 3
2018-08-09 08:30 | 5 | 2
2018-08-09 09:00 | 7 | 6
2018-08-09 09:30 | 11 | 11
2018-08-09 10:00 | 12 | 12
2018-08-09 10:30 | 13 | 13
2018-08-09 11:00 | 14 | 14
2018-08-09 11:30 | 12 | 12
2018-08-09 12:00 | 11 | 11
2018-08-09 12:30 | 13 | 12
2018-08-09 13:00 | 13 | 12
2018-08-09 13:30 | 11 | 10
2018-08-09 14:00 | 13 | 11
2018-08-09 14:30 | 14 | 13
2018-08-09 15:00 | 14 | 13
2018-08-09 15:30 | 10 | 8
2018-08-09 16:00 | 7 | 5
2018-08-09 16:30 | 6 | 5
2018-08-09 17:00 | 16 | 16
2018-08-09 17:30 | 34 | 34
2018-08-09 18:00 | 42 | 42
2018-08-09 18:30 | 45 | 44
2018-08-09 19:00 | 43 | 42
2018-08-09 19:30 | 44 | 43
2018-08-09 20:00 | 44 | 44
2018-08-09 20:30 | 44 | 44
2018-08-09 21:00 | 44 | 43
2018-08-09 21:30 | 43 | 42
2018-08-09 22:00 | 41 | 40
2018-08-09 22:30 | 39 | 39
2018-08-09 23:00 | 37 | 37
2018-08-09 23:30 | 38 | 37
2018-08-10 | 37 | 37
2018-08-10 00:30 | 38 | 37
2018-08-10 01:00 | 34 | 34
2018-08-10 01:30 | 35 | 34
2018-08-10 02:00 | 35 | 35
2018-08-10 02:30 | 35 | 35
2018-08-10 03:00 | 35 | 35
2018-08-10 03:30 | 35 | 35
2018-08-10 04:00 | 36 | 35
2018-08-10 04:30 | 36 | 36
2018-08-10 05:00 | 38 | 38
2018-08-10 05:30 | 36 | 36
2018-08-10 06:00 | 37 | 37
2018-08-10 06:30 | 39 | 39
2018-08-10 07:00 | 21 | 20
2018-08-10 07:30 | 13 | 12
2018-08-10 08:00 | 9 | 8
2018-08-10 08:30 | 8 | 7
2018-08-10 09:00 | 2 | 2
2018-08-10 09:30 | 8 | 8
2018-08-10 10:00 | 15 | 15
2018-08-10 10:30 | 44 | 44
2018-08-10 11:00 | 47 | 45
2018-08-10 11:30 | 36 | 35
2018-08-10 12:00 | 32 | 32
2018-08-10 12:30 | 33 | 32
2018-08-10 13:00 | 31 | 29
2018-08-10 13:30 | 18 | 14
2018-08-10 14:00 | 24 | 14
2018-08-10 14:30 | 9 | 5
2018-08-10 15:00 | 6 | 2
2018-08-10 15:30 | 8 | 1
2018-08-10 16:00 | 7 | 2
2018-08-10 16:30 | 11 | 9
2018-08-10 17:00 | 14 | 13
2018-08-10 17:30 | 25 | 25
2018-08-10 18:00 | 34 | 34
2018-08-10 18:30 | 38 | 37
2018-08-10 19:00 | 38 | 37
2018-08-10 19:30 | 38 | 37
2018-08-10 20:00 | 38 | 37
2018-08-10 20:30 | 37 | 35
2018-08-10 21:00 | 37 | 36
2018-08-10 21:30 | 37 | 36
2018-08-10 22:00 | 38 | 37
2018-08-10 22:30 | 36 | 35
2018-08-10 23:00 | 36 | 35
2018-08-10 23:30 | 36 | 34
2018-08-11 | 35 | 34
2018-08-11 00:30 | 35 | 34
2018-08-11 01:00 | 36 | 35
2018-08-11 01:30 | 38 | 37
2018-08-11 02:00 | 37 | 37
2018-08-11 02:30 | 38 | 37
2018-08-11 03:00 | 37 | 37
2018-08-11 03:30 | 36 | 35
2018-08-11 04:00 | 36 | 36
2018-08-11 04:30 | 36 | 36
2018-08-11 05:00 | 35 | 35
2018-08-11 05:30 | 36 | 36
2018-08-11 06:00 | 37 | 36
2018-08-11 06:30 | 35 | 35
2018-08-11 07:00 | 35 | 34
2018-08-11 07:30 | 26 | 26
2018-08-11 08:00 | 6 | 6
2018-08-11 08:30 | 7 | 6
2018-08-11 09:00 | 6 | 5
2018-08-11 09:30 | 10 | 10
2018-08-11 10:00 | 13 | 13
2018-08-11 10:30 | 13 | 13
2018-08-11 11:00 | 13 | 13
2018-08-11 11:30 | 35 | 35
2018-08-11 12:00 | 45 | 44
2018-08-11 12:30 | 24 | 24
2018-08-11 13:00 | 16 | 10
2018-08-11 13:30 | 17 | 10
2018-08-11 14:00 | 16 | 10
2018-08-11 14:30 | 16 | 10
2018-08-11 15:00 | 14 | 8
2018-08-11 15:30 | 12 | 6
2018-08-11 16:00 | 11 | 3
2018-08-11 16:30 | 12 | 6
2018-08-11 17:00 | 18 | 15
2018-08-11 17:30 | 32 | 30
2018-08-11 18:00 | 40 | 39
2018-08-11 18:30 | 42 | 42
2018-08-11 19:00 | 42 | 39
2018-08-11 19:30 | 42 | 40
2018-08-11 20:00 | 42 | 40
2018-08-11 20:30 | 44 | 41
2018-08-11 21:00 | 44 | 42
2018-08-11 21:30 | 43 | 40
2018-08-11 22:00 | 40 | 37
2018-08-11 22:30 | 37 | 34
2018-08-11 23:00 | 36 | 34
2018-08-11 23:30 | 34 | 33
2018-08-12 | 34 | 34
2018-08-12 00:30 | 34 | 34
2018-08-12 01:00 | 33 | 33
2018-08-12 01:30 | 33 | 32
2018-08-12 02:00 | 33 | 33
2018-08-12 02:30 | 34 | 33
2018-08-12 03:00 | 33 | 32
2018-08-12 03:30 | 32 | 32
2018-08-12 04:00 | 33 | 33
2018-08-12 04:30 | 33 | 32
2018-08-12 05:00 | 33 | 33
2018-08-12 05:30 | 33 | 33
2018-08-12 06:00 | 33 | 33
2018-08-12 06:30 | 33 | 33
2018-08-12 07:00 | 34 | 34
2018-08-12 07:30 | 26 | 26
2018-08-12 08:00 | 13 | 13
2018-08-12 08:30 | 6 | 5
2018-08-12 09:00 | 4 | 3
2018-08-12 09:30 | 8 | 8
2018-08-12 10:00 | 5 | 3
2018-08-12 10:30 | 7 | 1
2018-08-12 11:00 | 11 | 7
2018-08-12 11:30 | 13 | 9
2018-08-12 12:00 | 13 | 10
2018-08-12 12:30 | 13 | 10
2018-08-12 13:00 | 12 | 9
2018-08-12 13:30 | 13 | 9
2018-08-12 14:00 | 13 | 9
2018-08-12 14:30 | 12 | 9
2018-08-12 15:00 | 12 | 9
2018-08-12 15:30 | 8 | 3
2018-08-12 16:00 | 9 | 8
2018-08-12 16:30 | 15 | 14
2018-08-12 17:00 | 13 | 12
2018-08-12 17:30 | 20 | 20
2018-08-12 18:00 | 33 | 32
2018-08-12 18:30 | 36 | 36
2018-08-12 19:00 | 37 | 36
2018-08-12 19:30 | 39 | 37
2018-08-12 20:00 | 39 | 37
2018-08-12 20:30 | 38 | 36
2018-08-12 21:00 | 39 | 36
2018-08-12 21:30 | 37 | 34
2018-08-12 22:00 | 35 | 33
2018-08-12 22:30 | 35 | 32
2018-08-12 23:00 | 36 | 33
2018-08-12 23:30 | 37 | 33
2018-08-13 | 36 | 33
2018-08-13 00:30 | 36 | 33
2018-08-13 01:00 | 36 | 32
2018-08-13 01:30 | 32 | 31
2018-08-13 02:00 | 33 | 32
2018-08-13 02:30 | 33 | 33
2018-08-13 03:00 | 33 | 32
2018-08-13 03:30 | 33 | 33
2018-08-13 04:00 | 34 | 34
2018-08-13 04:30 | 34 | 33
2018-08-13 05:00 | 33 | 33
2018-08-13 05:30 | 33 | 33
2018-08-13 06:00 | 35 | 34
2018-08-13 06:30 | 34 | 33
2018-08-13 07:00 | 34 | 33
2018-08-13 07:30 | 27 | 27
2018-08-13 08:00 | 19 | 14
2018-08-13 08:30 | 13 | 2
2018-08-13 09:00 | 13 | 5
2018-08-13 09:30 | 15 | 9
2018-08-13 10:00 | 18 | 12
2018-08-13 10:30 | 18 | 12
2018-08-13 11:00 | 18 | 12
2018-08-13 11:30 | 14 | 14
2018-08-13 12:00 | 13 | 13
2018-08-13 12:30 | 12 | 12
2018-08-13 13:00 | 12 | 12
2018-08-13 13:30 | 12 | 12
2018-08-13 14:00 | 12 | 11
2018-08-13 14:30 | 11 | 11
2018-08-13 15:00 | 10 | 10
2018-08-13 15:30 | 10 | 10
2018-08-13 16:00 | 5 | 5
2018-08-13 16:30 | 3 | 3
2018-08-13 17:00 | 13 | 13
2018-08-13 17:30 | 27 | 27
2018-08-13 18:00 | 35 | 35
2018-08-13 18:30 | 35 | 35
2018-08-13 19:00 | 31 | 30
2018-08-13 19:30 | 38 | 38
2018-08-13 20:00 | 38 | 38
2018-08-13 20:30 | 37 | 37
2018-08-13 21:00 | 37 | 37
2018-08-13 21:30 | 35 | 35
2018-08-13 22:00 | 34 | 34
2018-08-13 22:30 | 33 | 33
2018-08-13 23:00 | 33 | 33
2018-08-13 23:30 | 33 | 33
2018-08-14 | 35 | 35
2018-08-14 00:30 | 35 | 35
2018-08-14 01:00 | 35 | 35
2018-08-14 01:30 | 35 | 35
2018-08-14 02:00 | 29 | 28
2018-08-14 02:30 | 38 | 34
2018-08-14 03:00 | 43 | 37
2018-08-14 03:30 | 43 | 37
2018-08-14 04:00 | 43 | 37
2018-08-14 04:30 | 41 | 35
2018-08-14 05:00 | 41 | 35
2018-08-14 05:30 | 42 | 35
2018-08-14 06:00 | 42 | 36
2018-08-14 06:30 | 41 | 35
2018-08-14 07:00 | 42 | 36
2018-08-14 07:30 | 31 | 24
2018-08-14 08:00 | 23 | 11
2018-08-14 08:30 | 21 | 3
2018-08-14 09:00 | 29 | 9
2018-08-14 09:30 | 30 | 15
2018-08-14 10:00 | 29 | 16
2018-08-14 10:30 | 26 | 14
2018-08-14 11:00 | 25 | 13
2018-08-14 11:30 | 24 | 12
2018-08-14 12:00 | 24 | 13
2018-08-14 12:30 | 24 | 13
2018-08-14 13:00 | 23 | 12
2018-08-14 13:30 | 21 | 10
2018-08-14 14:00 | 21 | 11
2018-08-14 14:30 | 22 | 11
2018-08-14 15:00 | 21 | 10
2018-08-14 15:30 | 18 | 4
2018-08-14 16:00 | 17 | 3
2018-08-14 16:30 | 17 | 5
2018-08-14 17:00 | 23 | 18
2018-08-14 17:30 | 35 | 32
2018-08-14 18:00 | 44 | 43
2018-08-14 18:30 | 45 | 43
2018-08-14 19:00 | 48 | 47
2018-08-14 19:30 | 50 | 50
2018-08-14 20:00 | 48 | 47
2018-08-14 20:30 | 50 | 48
2018-08-14 21:00 | 49 | 48
2018-08-14 21:30 | 49 | 48
2018-08-14 22:00 | 49 | 47
2018-08-14 22:30 | 48 | 46
2018-08-14 23:00 | 46 | 44
2018-08-14 23:30 | 45 | 42
2018-08-15 | 43 | 40
2018-08-15 00:30 | 39 | 36
2018-08-15 01:00 | 40 | 36
2018-08-15 01:30 | 40 | 36
2018-08-15 02:00 | 40 | 36
2018-08-15 02:30 | 40 | 35
2018-08-15 03:00 | 41 | 36
2018-08-15 03:30 | 40 | 36
2018-08-15 04:00 | 40 | 35
2018-08-15 04:30 | 39 | 35
2018-08-15 05:00 | 40 | 36
2018-08-15 05:30 | 40 | 35
2018-08-15 06:00 | 40 | 36
2018-08-15 06:30 | 41 | 37
2018-08-15 07:00 | 38 | 35
2018-08-15 07:30 | 31 | 28
2018-08-15 08:00 | 26 | 23
2018-08-15 08:30 | 25 | 22
2018-08-15 09:00 | 11 | 1
2018-08-15 09:30 | 10 | 1
2018-08-15 10:00 | 10 | 1
2018-08-15 10:30 | 13 | 7
2018-08-15 11:00 | 13 | 10
2018-08-15 11:30 | 20 | 19
2018-08-15 12:00 | 11 | 10
2018-08-15 12:30 | 13 | 11
2018-08-15 13:00 | 11 | 10
2018-08-15 13:30 | 11 | 11
2018-08-15 14:00 | 12 | 12
2018-08-15 14:30 | 9 | 9
2018-08-15 15:00 | 12 | 12
2018-08-15 15:30 | 14 | 14
2018-08-15 16:00 | 9 | 9
2018-08-15 16:30 | 2 | 0
2018-08-15 17:00 | 12 | 12
2018-08-15 17:30 | 25 | 24
2018-08-15 18:00 | 16 | 15
2018-08-15 18:30 | 18 | 16
2018-08-15 19:00 | 32 | 16
2018-08-15 19:30 | 33 | 14
2018-08-15 20:00 | 35 | 15
2018-08-15 20:30 | 35 | 15
2018-08-15 21:00 | 37 | 29
2018-08-15 21:30 | 37 | 32
2018-08-15 22:00 | 38 | 32
2018-08-15 22:30 | 36 | 30
2018-08-15 23:00 | 36 | 30
2018-08-15 23:30 | 37 | 31
2018-08-16 | 37 | 31
2018-08-16 00:30 | 32 | 31
2018-08-16 01:00 | 32 | 32
2018-08-16 01:30 | 33 | 33
2018-08-16 02:00 | 33 | 33
2018-08-16 02:30 | 33 | 33
2018-08-16 03:00 | 34 | 34
2018-08-16 03:30 | 33 | 33
2018-08-16 04:00 | 34 | 34
2018-08-16 04:30 | 36 | 36
2018-08-16 05:00 | 37 | 37
2018-08-16 05:30 | 38 | 37
2018-08-16 06:00 | 36 | 36
2018-08-16 06:30 | 23 | 21
2018-08-16 07:00 | 22 | 20
2018-08-16 07:30 | 13 | 10
2018-08-16 08:00 | 7 | 3
2018-08-16 08:30 | 5 | 1
2018-08-16 09:00 | 5 | 3
2018-08-16 09:30 | 8 | 6
2018-08-16 10:00 | 9 | 8
2018-08-16 10:30 | 8 | 8
2018-08-16 11:00 | 2 | 0
2018-08-16 11:30 | 10 | 9
2018-08-16 12:00 | 8 | 8
2018-08-16 12:30 | 4 | 4
2018-08-16 13:00 | 4 | 2
2018-08-16 13:30 | 3 | 1
2018-08-16 14:00 | 4 | 1
2018-08-16 14:30 | 5 | 4
2018-08-16 15:00 | 6 | 4
2018-08-16 15:30 | 7 | 5
2018-08-16 16:00 | 11 | 8
2018-08-16 16:30 | 15 | 14
2018-08-16 17:00 | 25 | 25
2018-08-16 17:30 | 41 | 41
2018-08-16 18:00 | 33 | 32
2018-08-16 18:30 | 33 | 31
2018-08-16 19:00 | 31 | 30
2018-08-16 19:30 | 30 | 28
2018-08-16 20:00 | 31 | 29
2018-08-16 20:30 | 31 | 29
2018-08-16 21:00 | 43 | 43
2018-08-16 21:30 | 45 | 45
2018-08-16 22:00 | 43 | 43
2018-08-16 22:30 | 39 | 39
2018-08-16 23:00 | 36 | 35
2018-08-16 23:30 | 31 | 30
2018-08-17 | 31 | 31
2018-08-17 00:30 | 21 | 21
2018-08-17 01:00 | 31 | 31
2018-08-17 01:30 | 31 | 31
2018-08-17 02:00 | 32 | 32
2018-08-17 02:30 | 33 | 32
2018-08-17 03:00 | 32 | 32
2018-08-17 03:30 | 32 | 31
2018-08-17 04:00 | 31 | 31
2018-08-17 04:30 | 31 | 31
2018-08-17 05:00 | 31 | 31
2018-08-17 05:30 | 31 | 31
2018-08-17 06:00 | 31 | 31
2018-08-17 06:30 | 17 | 15
2018-08-17 07:00 | 15 | 12
2018-08-17 07:30 | 7 | 1
2018-08-17 08:00 | 12 | 11
2018-08-17 08:30 | 8 | 7
2018-08-17 09:00 | 10 | 10
2018-08-17 09:30 | 14 | 14
2018-08-17 10:00 | 15 | 15
2018-08-17 10:30 | 15 | 14
2018-08-17 11:00 | 16 | 16
2018-08-17 11:30 | 15 | 15
2018-08-17 12:00 | 14 | 14
2018-08-17 12:30 | 14 | 14
2018-08-17 13:00 | 14 | 14
2018-08-17 13:30 | 13 | 13
2018-08-17 14:00 | 13 | 13
2018-08-17 14:30 | 13 | 13
2018-08-17 15:00 | 13 | 13
2018-08-17 15:30 | 13 | 13
2018-08-17 16:00 | 10 | 10
2018-08-17 16:30 | 2 | 2
2018-08-17 17:00 | 7 | 7
2018-08-17 17:30 | 12 | 12
2018-08-17 18:00 | 21 | 21
2018-08-17 18:30 | 16 | 15
2018-08-17 19:00 | 15 | 14
2018-08-17 19:30 | 15 | 14
2018-08-17 20:00 | 16 | 15
2018-08-17 20:30 | 23 | 23
2018-08-17 21:00 | 23 | 23
2018-08-17 21:30 | 22 | 22
2018-08-17 22:00 | 23 | 23
2018-08-17 22:30 | 22 | 22
2018-08-17 23:00 | 22 | 22
2018-08-17 23:30 | 22 | 22
2018-08-18 | 22 | 21
2018-08-18 00:30 | 31 | 31
2018-08-18 01:00 | 32 | 32
2018-08-18 01:30 | 36 | 36
2018-08-18 02:00 | 39 | 39
2018-08-18 02:30 | 39 | 39
2018-08-18 03:00 | 36 | 36
2018-08-18 03:30 | 32 | 32
2018-08-18 04:00 | 32 | 32
2018-08-18 04:30 | 33 | 32
2018-08-18 05:00 | 33 | 32
2018-08-18 05:30 | 32 | 31
2018-08-18 06:00 | 32 | 32
2018-08-18 06:30 | 16 | 14
2018-08-18 07:00 | 15 | 12
2018-08-18 07:30 | 10 | 5
2018-08-18 08:00 | 12 | 10
2018-08-18 08:30 | 13 | 12
2018-08-18 09:00 | 19 | 19
2018-08-18 09:30 | 19 | 19
2018-08-18 10:00 | 15 | 14
2018-08-18 10:30 | 15 | 14
2018-08-18 11:00 | 15 | 15
2018-08-18 11:30 | 15 | 14
2018-08-18 12:00 | 15 | 14
2018-08-18 12:30 | 13 | 12
2018-08-18 13:00 | 12 | 11
2018-08-18 13:30 | 15 | 14
2018-08-18 14:00 | 14 | 13
2018-08-18 14:30 | 13 | 13
2018-08-18 15:00 | 14 | 13
2018-08-18 15:30 | 14 | 14
2018-08-18 16:00 | 13 | 12
2018-08-18 16:30 | 7 | 5
2018-08-18 17:00 | 12 | 10
2018-08-18 17:30 | 18 | 16
2018-08-18 18:00 | 26 | 24
2018-08-18 18:30 | 17 | 16
2018-08-18 19:00 | 17 | 16
2018-08-18 19:30 | 16 | 15
2018-08-18 20:00 | 16 | 15
2018-08-18 20:30 | 24 | 24
2018-08-18 21:00 | 24 | 24
2018-08-18 21:30 | 24 | 24
2018-08-18 22:00 | 23 | 23
2018-08-18 22:30 | 22 | 22
2018-08-18 23:00 | 22 | 22
2018-08-18 23:30 | 22 | 22
2018-08-19 | 22 | 22
2018-08-19 00:30 | 36 | 36
2018-08-19 01:00 | 35 | 35
2018-08-19 01:30 | 33 | 33
2018-08-19 02:00 | 35 | 35
2018-08-19 02:30 | 34 | 34
2018-08-19 03:00 | 32 | 32
2018-08-19 03:30 | 32 | 32
2018-08-19 04:00 | 33 | 33
2018-08-19 04:30 | 32 | 32
2018-08-19 05:00 | 32 | 32
2018-08-19 05:30 | 34 | 33
2018-08-19 06:00 | 34 | 34
2018-08-19 06:30 | 21 | 20
2018-08-19 07:00 | 17 | 11
2018-08-19 07:30 | 13 | 3
2018-08-19 08:00 | 17 | 12
2018-08-19 08:30 | 17 | 13
2018-08-19 09:00 | 21 | 18
2018-08-19 09:30 | 23 | 20
2018-08-19 10:00 | 19 | 17
2018-08-19 10:30 | 14 | 13
2018-08-19 11:00 | 14 | 13
2018-08-19 11:30 | 13 | 12
2018-08-19 12:00 | 13 | 12
2018-08-19 12:30 | 13 | 12
2018-08-19 13:00 | 13 | 12
2018-08-19 13:30 | 13 | 12
2018-08-19 14:00 | 12 | 10
2018-08-19 14:30 | 12 | 10
2018-08-19 15:00 | 12 | 10
2018-08-19 15:30 | 11 | 9
2018-08-19 16:00 | 7 | 4
2018-08-19 16:30 | 9 | 4
2018-08-19 17:00 | 18 | 16
2018-08-19 17:30 | 20 | 18
2018-08-19 18:00 | 27 | 25
2018-08-19 18:30 | 20 | 19
2018-08-19 19:00 | 18 | 17
2018-08-19 19:30 | 17 | 16
2018-08-19 20:00 | 18 | 17
2018-08-19 20:30 | 26 | 26
2018-08-19 21:00 | 27 | 27
2018-08-19 21:30 | 24 | 24
2018-08-19 22:00 | 27 | 27
2018-08-19 22:30 | 24 | 24
2018-08-19 23:00 | 23 | 23
2018-08-19 23:30 | 24 | 23
2018-08-20 | 24 | 23
2018-08-20 00:30 | 23 | 22
2018-08-20 01:00 | 30 | 29
2018-08-20 01:30 | 34 | 34
2018-08-20 02:00 | 34 | 33
2018-08-20 02:30 | 28 | 27
2018-08-20 03:00 | 26 | 26
2018-08-20 03:30 | 33 | 33
2018-08-20 04:00 | 34 | 33
2018-08-20 04:30 | 33 | 33
2018-08-20 05:00 | 34 | 34
2018-08-20 05:30 | 34 | 33
2018-08-20 06:00 | 35 | 35
2018-08-20 06:30 | 18 | 16
2018-08-20 07:00 | 16 | 15
2018-08-20 07:30 | 7 | 4
2018-08-20 08:00 | 10 | 9
2018-08-20 08:30 | 17 | 11
2018-08-20 09:00 | 24 | 17
2018-08-20 09:30 | 26 | 20
2018-08-20 10:00 | 21 | 15
2018-08-20 10:30 | 21 | 16
2018-08-20 11:00 | 21 | 16
2018-08-20 11:30 | 20 | 15
2018-08-20 12:00 | 21 | 16
2018-08-20 12:30 | 22 | 16
2018-08-20 13:00 | 21 | 15
2018-08-20 13:30 | 20 | 15
2018-08-20 14:00 | 20 | 15
2018-08-20 14:30 | 19 | 13
2018-08-20 15:00 | 19 | 13
2018-08-20 15:30 | 19 | 13
2018-08-20 16:00 | 17 | 10
2018-08-20 16:30 | 14 | 3
2018-08-20 17:00 | 16 | 6
2018-08-20 17:30 | 17 | 4
2018-08-20 18:00 | 23 | 9
2018-08-20 18:30 | 27 | 8
2018-08-20 19:00 | 26 | 8
2018-08-20 19:30 | 28 | 8
2018-08-20 20:00 | 28 | 9
2018-08-20 20:30 | 28 | 8
2018-08-20 21:00 | 29 | 8
2018-08-20 21:30 | 28 | 23
2018-08-20 22:00 | 30 | 26
2018-08-20 22:30 | 30 | 25
2018-08-20 23:00 | 32 | 25
2018-08-20 23:30 | 35 | 13
2018-08-21 | 35 | 14
2018-08-21 00:30 | 36 | 15
2018-08-21 01:00 | 37 | 16
2018-08-21 01:30 | 38 | 9
2018-08-21 02:00 | 40 | 4
2018-08-21 02:30 | 22 | 1
2018-08-21 03:00 | 17 | 1
2018-08-21 03:30 | 17 | 0
2018-08-21 04:00 | 18 | 1
2018-08-21 04:30 | 20 | 3
2018-08-21 05:00 | 19 | 5
2018-08-21 05:30 | 19 | 5
2018-08-21 06:00 | 18 | 3
2018-08-21 06:30 | 17 | 5
2018-08-21 07:00 | 14 | 1
2018-08-21 07:30 | 17 | 1
2018-08-21 08:00 | 20 | 12
2018-08-21 08:30 | 26 | 19
2018-08-21 09:00 | 29 | 23
2018-08-21 09:30 | 38 | 35
2018-08-21 10:00 | 42 | 41
2018-08-21 10:30 | 42 | 41
2018-08-21 11:00 | 42 | 41
2018-08-21 11:30 | 42 | 42
2018-08-21 12:00 | 39 | 37
2018-08-21 12:30 | 36 | 34
2018-08-21 13:00 | 38 | 36
2018-08-21 13:30 | 38 | 36
2018-08-21 14:00 | 36 | 34
2018-08-21 14:30 | 36 | 34
2018-08-21 15:00 | 38 | 36
2018-08-21 15:30 | 37 | 35
2018-08-21 16:00 | 34 | 31
2018-08-21 16:30 | 30 | 27
2018-08-21 17:00 | 23 | 17
2018-08-21 17:30 | 17 | 6
2018-08-21 18:00 | 15 | 1
2018-08-21 18:30 | 15 | 1
2018-08-21 19:00 | 15 | 1
2018-08-21 19:30 | 16 | 1
2018-08-21 20:00 | 22 | 8
2018-08-21 20:30 | 23 | 8
2018-08-21 21:00 | 23 | 9
2018-08-21 21:30 | 18 | 2
2018-08-21 22:00 | 18 | 0
2018-08-21 22:30 | 17 | 1
2018-08-21 23:00 | 18 | 4
2018-08-21 23:30 | 18 | 7
2018-08-22 | 18 | 6
2018-08-22 00:30 | 19 | 6
2018-08-22 01:00 | 19 | 5
2018-08-22 01:30 | 19 | 3
2018-08-22 02:00 | 19 | 2
2018-08-22 02:30 | 19 | 1
2018-08-22 03:00 | 19 | 1
2018-08-22 03:30 | 19 | 1
2018-08-22 04:00 | 18 | 0
2018-08-22 04:30 | 17 | 0
2018-08-22 05:00 | 17 | 1
2018-08-22 05:30 | 16 | 2
2018-08-22 06:00 | 16 | 1
2018-08-22 06:30 | 15 | 3
2018-08-22 07:00 | 16 | 5
2018-08-22 07:30 | 18 | 12
2018-08-22 08:00 | 20 | 16
2018-08-22 08:30 | 20 | 19
2018-08-22 09:00 | 21 | 19
2018-08-22 09:30 | 23 | 21
2018-08-22 10:00 | 34 | 34
2018-08-22 10:30 | 47 | 46
2018-08-22 11:00 | 46 | 45
2018-08-22 11:30 | 45 | 45
2018-08-22 12:00 | 46 | 46
2018-08-22 12:30 | 46 | 45
2018-08-22 13:00 | 46 | 46
2018-08-22 13:30 | 46 | 45
2018-08-22 14:00 | 44 | 44
2018-08-22 14:30 | 43 | 42
2018-08-22 15:00 | 38 | 37
2018-08-22 15:30 | 35 | 33
2018-08-22 16:00 | 35 | 33
2018-08-22 16:30 | 26 | 25
2018-08-22 17:00 | 13 | 7
2018-08-22 17:30 | 19 | 16
2018-08-22 18:00 | 27 | 24
2018-08-22 18:30 | 28 | 27
2018-08-22 19:00 | 38 | 29
2018-08-22 19:30 | 38 | 30
2018-08-22 20:00 | 38 | 32
2018-08-22 20:30 | 40 | 34
2018-08-22 21:00 | 41 | 35
2018-08-22 21:30 | 38 | 32
2018-08-22 22:00 | 33 | 28
2018-08-22 22:30 | 30 | 26
2018-08-22 23:00 | 31 | 27
2018-08-22 23:30 | 31 | 27
2018-08-23 | 31 | 26
2018-08-23 00:30 | 32 | 27
2018-08-23 01:00 | 33 | 28
2018-08-23 01:30 | 33 | 28
2018-08-23 02:00 | 34 | 29
2018-08-23 02:30 | 33 | 28
2018-08-23 03:00 | 34 | 28
2018-08-23 03:30 | 33 | 28
2018-08-23 04:00 | 35 | 29
2018-08-23 04:30 | 35 | 29
2018-08-23 05:00 | 35 | 30
2018-08-23 05:30 | 35 | 30
2018-08-23 06:00 | 35 | 30
2018-08-23 06:30 | 34 | 30
2018-08-23 07:00 | 32 | 27
2018-08-23 07:30 | 25 | 19
2018-08-23 08:00 | 22 | 19
2018-08-23 08:30 | 13 | 9
2018-08-23 09:00 | 9 | 2
2018-08-23 09:30 | 11 | 9
2018-08-23 10:00 | 14 | 12
2018-08-23 10:30 | 17 | 15
2018-08-23 11:00 | 18 | 16
2018-08-23 11:30 | 20 | 18
2018-08-23 12:00 | 21 | 19
2018-08-23 12:30 | 22 | 20
2018-08-23 13:00 | 22 | 20
2018-08-23 13:30 | 21 | 18
2018-08-23 14:00 | 18 | 15
2018-08-23 14:30 | 19 | 16
2018-08-23 15:00 | 20 | 17
2018-08-23 15:30 | 25 | 22
2018-08-23 16:00 | 24 | 21
2018-08-23 16:30 | 18 | 13
2018-08-23 17:00 | 13 | 2
2018-08-23 17:30 | 25 | 19
2018-08-23 18:00 | 30 | 21
2018-08-23 18:30 | 40 | 24
2018-08-23 19:00 | 42 | 28
2018-08-23 19:30 | 47 | 36
2018-08-23 20:00 | 47 | 37
2018-08-23 20:30 | 48 | 35
2018-08-23 21:00 | 45 | 34
2018-08-23 21:30 | 44 | 40
2018-08-23 22:00 | 40 | 36
2018-08-23 22:30 | 37 | 32
2018-08-23 23:00 | 37 | 31
2018-08-23 23:30 | 38 | 32
2018-08-24 | 35 | 32
2018-08-24 00:30 | 32 | 32
2018-08-24 01:00 | 32 | 32
2018-08-24 01:30 | 32 | 32
2018-08-24 02:00 | 32 | 32
2018-08-24 02:30 | 32 | 32
2018-08-24 03:00 | 33 | 33
2018-08-24 03:30 | 33 | 33
2018-08-24 04:00 | 33 | 33
2018-08-24 04:30 | 33 | 33
2018-08-24 05:00 | 32 | 32
2018-08-24 05:30 | 32 | 32
2018-08-24 06:00 | 33 | 33
2018-08-24 06:30 | 32 | 32
2018-08-24 07:00 | 30 | 29
2018-08-24 07:30 | 21 | 21
2018-08-24 08:00 | 9 | 8
2018-08-24 08:30 | 5 | 3
2018-08-24 09:00 | 11 | 10
2018-08-24 09:30 | 8 | 7
2018-08-24 10:00 | 12 | 11
2018-08-24 10:30 | 13 | 13
2018-08-24 11:00 | 11 | 10
2018-08-24 11:30 | 10 | 10
2018-08-24 12:00 | 12 | 11
2018-08-24 12:30 | 11 | 11
2018-08-24 13:00 | 11 | 11
2018-08-24 13:30 | 10 | 9
2018-08-24 14:00 | 9 | 8
2018-08-24 14:30 | 8 | 7
2018-08-24 15:00 | 11 | 10
2018-08-24 15:30 | 8 | 7
2018-08-24 16:00 | 4 | 2
2018-08-24 16:30 | 11 | 10
2018-08-24 17:00 | 26 | 26
2018-08-24 17:30 | 30 | 30
2018-08-24 18:00 | 28 | 28
2018-08-24 18:30 | 27 | 27
2018-08-24 19:00 | 27 | 27
2018-08-24 19:30 | 28 | 28
2018-08-24 20:00 | 28 | 28
2018-08-24 20:30 | 29 | 29
2018-08-24 21:00 | 35 | 35
2018-08-24 21:30 | 36 | 36
2018-08-24 22:00 | 36 | 36
2018-08-24 22:30 | 36 | 35
2018-08-24 23:00 | 36 | 36
2018-08-24 23:30 | 35 | 35
2018-08-25 | 35 | 35
2018-08-25 00:30 | 35 | 35
2018-08-25 01:00 | 34 | 34
2018-08-25 01:30 | 34 | 34
2018-08-25 02:00 | 34 | 34
2018-08-25 02:30 | 37 | 37
2018-08-25 03:00 | 36 | 36
2018-08-25 03:30 | 36 | 35
2018-08-25 04:00 | 36 | 36
2018-08-25 04:30 | 36 | 36
2018-08-25 05:00 | 36 | 36
2018-08-25 05:30 | 37 | 37
2018-08-25 06:00 | 36 | 36
2018-08-25 06:30 | 27 | 27
2018-08-25 07:00 | 26 | 26
2018-08-25 07:30 | 18 | 18
2018-08-25 08:00 | 4 | 3
2018-08-25 08:30 | 14 | 13
2018-08-25 09:00 | 3 | 1
2018-08-25 09:30 | 2 | 0
2018-08-25 10:00 | 4 | 3
2018-08-25 10:30 | 3 | 3
2018-08-25 11:00 | 3 | 2
2018-08-25 11:30 | 2 | 2
2018-08-25 12:00 | 9 | 9
2018-08-25 12:30 | 7 | 7
2018-08-25 13:00 | 4 | 4
2018-08-25 13:30 | 3 | 1
2018-08-25 14:00 | 2 | 2
2018-08-25 14:30 | 3 | 3
2018-08-25 15:00 | 3 | 3
2018-08-25 15:30 | 6 | 6
2018-08-25 16:00 | 9 | 9
2018-08-25 16:30 | 13 | 13
2018-08-25 17:00 | 23 | 23
2018-08-25 17:30 | 29 | 29
2018-08-25 18:00 | 34 | 34
2018-08-25 18:30 | 32 | 32
2018-08-25 19:00 | 27 | 25
2018-08-25 19:30 | 47 | 47
2018-08-25 20:00 | 57 | 57
2018-08-25 20:30 | 56 | 56
2018-08-25 21:00 | 60 | 60
2018-08-25 21:30 | 54 | 54
2018-08-25 22:00 | 53 | 52
2018-08-25 22:30 | 52 | 51
2018-08-25 23:00 | 50 | 50
2018-08-25 23:30 | 50 | 50
2018-08-26 | 51 | 50
2018-08-26 00:30 | 49 | 49
2018-08-26 01:00 | 49 | 49
2018-08-26 01:30 | 51 | 51
2018-08-26 02:00 | 50 | 50
2018-08-26 02:30 | 49 | 49
2018-08-26 03:00 | 50 | 50
2018-08-26 03:30 | 49 | 49
2018-08-26 04:00 | 50 | 50
2018-08-26 04:30 | 50 | 50
2018-08-26 05:00 | 50 | 50
2018-08-26 05:30 | 49 | 49
2018-08-26 06:00 | 48 | 48
2018-08-26 06:30 | 38 | 38
2018-08-26 07:00 | 35 | 35
2018-08-26 07:30 | 28 | 28
2018-08-26 08:00 | 25 | 25
2018-08-26 08:30 | 16 | 16
2018-08-26 09:00 | 15 | 15
2018-08-26 09:30 | 11 | 11
2018-08-26 10:00 | 18 | 18
2018-08-26 10:30 | 16 | 16
2018-08-26 11:00 | 27 | 27
2018-08-26 11:30 | 18 | 18
2018-08-26 12:00 | 19 | 19
2018-08-26 12:30 | 12 | 12
2018-08-26 13:00 | 12 | 12
2018-08-26 13:30 | 17 | 17
2018-08-26 14:00 | 23 | 23
2018-08-26 14:30 | 31 | 31
2018-08-26 15:00 | 30 | 30
2018-08-26 15:30 | 13 | 13
2018-08-26 16:00 | 13 | 13
2018-08-26 16:30 | 20 | 20
2018-08-26 17:00 | 34 | 34
2018-08-26 17:30 | 42 | 42
2018-08-26 18:00 | 41 | 41
2018-08-26 18:30 | 44 | 39
2018-08-26 19:00 | 39 | 30
2018-08-26 19:30 | 43 | 38
2018-08-26 20:00 | 47 | 44
2018-08-26 20:30 | 49 | 46
2018-08-26 21:00 | 50 | 47
2018-08-26 21:30 | 50 | 47
2018-08-26 22:00 | 50 | 47
2018-08-26 22:30 | 47 | 44
2018-08-26 23:00 | 47 | 43
2018-08-26 23:30 | 47 | 43
2018-08-27 | 47 | 43
2018-08-27 00:30 | 47 | 44
2018-08-27 01:00 | 45 | 44
2018-08-27 01:30 | 43 | 43
2018-08-27 02:00 | 42 | 42
2018-08-27 02:30 | 43 | 42
2018-08-27 03:00 | 43 | 43
2018-08-27 03:30 | 44 | 43
2018-08-27 04:00 | 44 | 44
2018-08-27 04:30 | 44 | 44
2018-08-27 05:00 | 44 | 43
2018-08-27 05:30 | 44 | 44
2018-08-27 06:00 | 46 | 46
2018-08-27 06:30 | 38 | 38
2018-08-27 07:00 | 35 | 35
2018-08-27 07:30 | 24 | 24
2018-08-27 08:00 | 11 | 11
2018-08-27 08:30 | 7 | 5
2018-08-27 09:00 | 5 | 0
2018-08-27 09:30 | 6 | 3
2018-08-27 10:00 | 6 | 4
2018-08-27 10:30 | 7 | 5
2018-08-27 11:00 | 7 | 5
2018-08-27 11:30 | 5 | 3
2018-08-27 12:00 | 5 | 3
2018-08-27 12:30 | 5 | 2
2018-08-27 13:00 | 5 | 2
2018-08-27 13:30 | 4 | 0
2018-08-27 14:00 | 3 | 0
2018-08-27 14:30 | 3 | 1
2018-08-27 15:00 | 3 | 0
2018-08-27 15:30 | 4 | 2
2018-08-27 16:00 | 7 | 6
2018-08-27 16:30 | 14 | 14
2018-08-27 17:00 | 26 | 26
2018-08-27 17:30 | 37 | 37
2018-08-27 18:00 | 18 | 18
2018-08-27 18:30 | 26 | 22
2018-08-27 19:00 | 27 | 24
2018-08-27 19:30 | 27 | 24
2018-08-27 20:00 | 37 | 36
2018-08-27 20:30 | 42 | 42
2018-08-27 21:00 | 55 | 55
2018-08-27 21:30 | 50 | 50
2018-08-27 22:00 | 48 | 47
2018-08-27 22:30 | 45 | 45
2018-08-27 23:00 | 45 | 45
2018-08-27 23:30 | 44 | 44
2018-08-28 | 42 | 42
2018-08-28 00:30 | 43 | 43
2018-08-28 01:00 | 44 | 44
2018-08-28 01:30 | 42 | 42
2018-08-28 02:00 | 42 | 42
2018-08-28 02:30 | 42 | 42
2018-08-28 03:00 | 43 | 43
2018-08-28 03:30 | 44 | 44
2018-08-28 04:00 | 46 | 46
2018-08-28 04:30 | 46 | 46
2018-08-28 05:00 | 46 | 45
2018-08-28 05:30 | 47 | 47
2018-08-28 06:00 | 46 | 46
2018-08-28 06:30 | 34 | 33
2018-08-28 07:00 | 24 | 24
2018-08-28 07:30 | 13 | 12
2018-08-28 08:00 | 4 | 3
2018-08-28 08:30 | 10 | 10
2018-08-28 09:00 | 6 | 6
2018-08-28 09:30 | 2 | 2
2018-08-28 10:00 | 0 | 0
2018-08-28 10:30 | 0 | 0
2018-08-28 11:00 | 2 | 2
2018-08-28 11:30 | 1 | 1
2018-08-28 12:00 | 1 | 1
2018-08-28 12:30 | 1 | 1
2018-08-28 13:00 | 2 | 2
2018-08-28 13:30 | 1 | 0
2018-08-28 14:00 | 1 | 1
2018-08-28 14:30 | 2 | 2
2018-08-28 15:00 | 3 | 3
2018-08-28 15:30 | 3 | 3
2018-08-28 16:00 | 7 | 7
2018-08-28 16:30 | 15 | 15
2018-08-28 17:00 | 26 | 26
2018-08-28 17:30 | 30 | 30
2018-08-28 18:00 | 39 | 38
2018-08-28 18:30 | 36 | 35
2018-08-28 19:00 | 27 | 23
2018-08-28 19:30 | 32 | 30
2018-08-28 20:00 | 33 | 32
2018-08-28 20:30 | 36 | 34
2018-08-28 21:00 | 36 | 35
2018-08-28 21:30 | 52 | 52
2018-08-28 22:00 | 51 | 51
2018-08-28 22:30 | 48 | 48
2018-08-28 23:00 | 42 | 42
2018-08-28 23:30 | 40 | 39
2018-08-29 | 40 | 40
2018-08-29 00:30 | 41 | 41
2018-08-29 01:00 | 41 | 41
2018-08-29 01:30 | 40 | 40
2018-08-29 02:00 | 41 | 41
2018-08-29 02:30 | 42 | 41
2018-08-29 03:00 | 41 | 41
2018-08-29 03:30 | 40 | 40
2018-08-29 04:00 | 40 | 40
2018-08-29 04:30 | 42 | 42
2018-08-29 05:00 | 41 | 41
2018-08-29 05:30 | 41 | 41
2018-08-29 06:00 | 41 | 41
2018-08-29 06:30 | 26 | 25
2018-08-29 07:00 | 20 | 18
2018-08-29 07:30 | 8 | 0
2018-08-29 08:00 | 18 | 17
2018-08-29 08:30 | 7 | 5
2018-08-29 09:00 | 2 | 1
2018-08-29 09:30 | 5 | 4
2018-08-29 10:00 | 6 | 6
2018-08-29 10:30 | 6 | 5
2018-08-29 11:00 | 6 | 5
2018-08-29 11:30 | 5 | 5
2018-08-29 12:00 | 6 | 6
2018-08-29 12:30 | 7 | 6
2018-08-29 13:00 | 6 | 5
2018-08-29 13:30 | 4 | 4
2018-08-29 14:00 | 3 | 2
2018-08-29 14:30 | 3 | 2
2018-08-29 15:00 | 2 | 1
2018-08-29 15:30 | 4 | 3
2018-08-29 16:00 | 4 | 4
2018-08-29 16:30 | 11 | 11
2018-08-29 17:00 | 27 | 27
2018-08-29 17:30 | 39 | 39
2018-08-29 18:00 | 38 | 38
2018-08-29 18:30 | 42 | 42
2018-08-29 19:00 | 43 | 43
2018-08-29 19:30 | 33 | 32
2018-08-29 20:00 | 29 | 28
2018-08-29 20:30 | 36 | 35
2018-08-29 21:00 | 37 | 37
2018-08-29 21:30 | 35 | 35
2018-08-29 22:00 | 43 | 43
2018-08-29 22:30 | 38 | 38
2018-08-29 23:00 | 35 | 35
2018-08-29 23:30 | 43 | 43
2018-08-30 | 44 | 44
2018-08-30 00:30 | 44 | 43
2018-08-30 01:00 | 44 | 44
2018-08-30 01:30 | 44 | 44
2018-08-30 02:00 | 45 | 45
2018-08-30 02:30 | 44 | 44
2018-08-30 03:00 | 46 | 46
2018-08-30 03:30 | 44 | 43
2018-08-30 04:00 | 49 | 49
2018-08-30 04:30 | 53 | 53
2018-08-30 05:00 | 53 | 53
2018-08-30 05:30 | 55 | 55
2018-08-30 06:00 | 46 | 45
2018-08-30 06:30 | 44 | 44
2018-08-30 07:00 | 31 | 30
2018-08-30 07:30 | 18 | 15
2018-08-30 08:00 | 19 | 18
2018-08-30 08:30 | 22 | 21
2018-08-30 09:00 | 21 | 21
2018-08-30 09:30 | 24 | 24
2018-08-30 10:00 | 39 | 39
2018-08-30 10:30 | 26 | 26
2018-08-30 11:00 | 27 | 27
2018-08-30 11:30 | 21 | 21
2018-08-30 12:00 | 15 | 15
2018-08-30 12:30 | 12 | 12
2018-08-30 13:00 | 11 | 11
2018-08-30 13:30 | 12 | 12
2018-08-30 14:00 | 11 | 11
2018-08-30 14:30 | 13 | 13
2018-08-30 15:00 | 13 | 13
2018-08-30 15:30 | 13 | 13
2018-08-30 16:00 | 16 | 16
2018-08-30 16:30 | 24 | 24
2018-08-30 17:00 | 30 | 30
2018-08-30 17:30 | 36 | 36
2018-08-30 18:00 | 40 | 40
2018-08-30 18:30 | 40 | 39
2018-08-30 19:00 | 36 | 35
2018-08-30 19:30 | 35 | 35
2018-08-30 20:00 | 40 | 40
2018-08-30 20:30 | 40 | 40
2018-08-30 21:00 | 44 | 44
2018-08-30 21:30 | 48 | 48
2018-08-30 22:00 | 52 | 52
2018-08-30 22:30 | 53 | 53
2018-08-30 23:00 | 53 | 53
2018-08-30 23:30 | 54 | 54
2018-08-31 | 54 | 53
2018-08-31 00:30 | 50 | 50
2018-08-31 01:00 | 44 | 44
2018-08-31 01:30 | 44 | 44
2018-08-31 02:00 | 44 | 44
2018-08-31 02:30 | 44 | 43
2018-08-31 03:00 | 44 | 43
2018-08-31 03:30 | 44 | 43
2018-08-31 04:00 | 43 | 42
2018-08-31 04:30 | 42 | 41
2018-08-31 05:00 | 43 | 42
2018-08-31 05:30 | 42 | 42
2018-08-31 06:00 | 43 | 42
2018-08-31 06:30 | 27 | 27
2018-08-31 07:00 | 22 | 22
2018-08-31 07:30 | 10 | 10
2018-08-31 08:00 | 9 | 9
2018-08-31 08:30 | 8 | 8
2018-08-31 09:00 | 4 | 3
2018-08-31 09:30 | 4 | 3
2018-08-31 10:00 | 3 | 2
2018-08-31 10:30 | 4 | 3
2018-08-31 11:00 | 5 | 4
2018-08-31 11:30 | 5 | 3
2018-08-31 12:00 | 5 | 4
2018-08-31 12:30 | 5 | 3
2018-08-31 13:00 | 5 | 4
2018-08-31 13:30 | 5 | 3
2018-08-31 14:00 | 5 | 3
2018-08-31 14:30 | 4 | 2
2018-08-31 15:00 | 3 | 1
2018-08-31 15:30 | 3 | 0
2018-08-31 16:00 | 4 | 3
2018-08-31 16:30 | 12 | 12
2018-08-31 17:00 | 23 | 23
2018-08-31 17:30 | 25 | 25
2018-08-31 18:00 | 31 | 31
2018-08-31 18:30 | 28 | 28
2018-08-31 19:00 | 25 | 25
2018-08-31 19:30 | 33 | 33
2018-08-31 20:00 | 33 | 33
2018-08-31 20:30 | 33 | 33
2018-08-31 21:00 | 33 | 33
2018-08-31 21:30 | 32 | 32
2018-08-31 22:00 | 33 | 33
2018-08-31 22:30 | 37 | 36
2018-08-31 23:00 | 40 | 39
2018-08-31 23:30 | 44 | 43
2018-09-01 | 42 | 42
2018-09-01 00:30 | 42 | 42
2018-09-01 01:00 | 41 | 41
2018-09-01 01:30 | 41 | 40
2018-09-01 02:00 | 40 | 39
2018-09-01 02:30 | 41 | 40
2018-09-01 03:00 | 40 | 40
2018-09-01 03:30 | 39 | 39
2018-09-01 04:00 | 39 | 39
2018-09-01 04:30 | 40 | 39
2018-09-01 05:00 | 40 | 39
2018-09-01 05:30 | 40 | 40
2018-09-01 06:00 | 42 | 41
2018-09-01 06:30 | 40 | 39
2018-09-01 07:00 | 39 | 39
2018-09-01 07:30 | 34 | 34
2018-09-01 08:00 | 23 | 22
2018-09-01 08:30 | 5 | 1
2018-09-01 09:00 | 5 | 1
2018-09-01 09:30 | 6 | 1
2018-09-01 10:00 | 8 | 4
2018-09-01 10:30 | 8 | 4
2018-09-01 11:00 | 7 | 4
2018-09-01 11:30 | 7 | 3
2018-09-01 12:00 | 6 | 3
2018-09-01 12:30 | 5 | 1
2018-09-01 13:00 | 7 | 2
2018-09-01 13:30 | 7 | 2
2018-09-01 14:00 | 5 | 0
2018-09-01 14:30 | 6 | 0
2018-09-01 15:00 | 6 | 4
2018-09-01 15:30 | 11 | 11
2018-09-01 16:00 | 15 | 15
2018-09-01 16:30 | 21 | 21
2018-09-01 17:00 | 27 | 27
2018-09-01 17:30 | 29 | 29
2018-09-01 18:00 | 33 | 33
2018-09-01 18:30 | 35 | 35
2018-09-01 19:00 | 32 | 32
2018-09-01 19:30 | 35 | 35
2018-09-01 20:00 | 35 | 35
2018-09-01 20:30 | 35 | 35
2018-09-01 21:00 | 34 | 34
2018-09-01 21:30 | 33 | 33
2018-09-01 22:00 | 33 | 33
2018-09-01 22:30 | 31 | 31
2018-09-01 23:00 | 29 | 29
2018-09-01 23:30 | 28 | 28
2018-09-02 | 38 | 38
2018-09-02 00:30 | 41 | 40
2018-09-02 01:00 | 34 | 34
2018-09-02 01:30 | 38 | 38
2018-09-02 02:00 | 40 | 40
2018-09-02 02:30 | 39 | 39
2018-09-02 03:00 | 41 | 40
2018-09-02 03:30 | 40 | 40
2018-09-02 04:00 | 40 | 40
2018-09-02 04:30 | 39 | 39
2018-09-02 05:00 | 40 | 40
2018-09-02 05:30 | 40 | 40
2018-09-02 06:00 | 41 | 41
2018-09-02 06:30 | 42 | 41
2018-09-02 07:00 | 39 | 39
2018-09-02 07:30 | 29 | 29
2018-09-02 08:00 | 21 | 21
2018-09-02 08:30 | 13 | 12
2018-09-02 09:00 | 9 | 4
2018-09-02 09:30 | 8 | 1
2018-09-02 10:00 | 9 | 2
2018-09-02 10:30 | 11 | 4
2018-09-02 11:00 | 10 | 4
2018-09-02 11:30 | 10 | 2
2018-09-02 12:00 | 10 | 2
2018-09-02 12:30 | 9 | 2
2018-09-02 13:00 | 10 | 2
2018-09-02 13:30 | 10 | 3
2018-09-02 14:00 | 9 | 2
2018-09-02 14:30 | 9 | 1
2018-09-02 15:00 | 9 | 0
2018-09-02 15:30 | 9 | 1
2018-09-02 16:00 | 10 | 6
2018-09-02 16:30 | 16 | 14
2018-09-02 17:00 | 25 | 24
2018-09-02 17:30 | 27 | 26
2018-09-02 18:00 | 33 | 33
2018-09-02 18:30 | 20 | 17
2018-09-02 19:00 | 18 | 14
2018-09-02 19:30 | 25 | 24
2018-09-02 20:00 | 28 | 28
2018-09-02 20:30 | 31 | 31
2018-09-02 21:00 | 33 | 33
2018-09-02 21:30 | 34 | 34
2018-09-02 22:00 | 32 | 32
2018-09-02 22:30 | 30 | 30
2018-09-02 23:00 | 31 | 31
2018-09-02 23:30 | 40 | 40
2018-09-03 | 41 | 41
2018-09-03 00:30 | 42 | 42
2018-09-03 01:00 | 41 | 41
2018-09-03 01:30 | 41 | 41
2018-09-03 02:00 | 41 | 41
2018-09-03 02:30 | 40 | 39
2018-09-03 03:00 | 42 | 41
2018-09-03 03:30 | 42 | 42
2018-09-03 04:00 | 41 | 41
2018-09-03 04:30 | 41 | 41
2018-09-03 05:00 | 42 | 42
2018-09-03 05:30 | 42 | 41
2018-09-03 06:00 | 42 | 42
2018-09-03 06:30 | 32 | 32
2018-09-03 07:00 | 27 | 26
2018-09-03 07:30 | 17 | 16
2018-09-03 08:00 | 8 | 7
2018-09-03 08:30 | 9 | 9
2018-09-03 09:00 | 11 | 10
2018-09-03 09:30 | 10 | 9
2018-09-03 10:00 | 10 | 9
2018-09-03 10:30 | 10 | 8
2018-09-03 11:00 | 17 | 16
2018-09-03 11:30 | 16 | 16
2018-09-03 12:00 | 16 | 15
2018-09-03 12:30 | 17 | 16
2018-09-03 13:00 | 17 | 16
2018-09-03 13:30 | 16 | 15
2018-09-03 14:00 | 10 | 9
2018-09-03 14:30 | 5 | 0
2018-09-03 15:00 | 5 | 0
2018-09-03 15:30 | 5 | 1
2018-09-03 16:00 | 7 | 5
2018-09-03 16:30 | 15 | 15
2018-09-03 17:00 | 27 | 27
2018-09-03 17:30 | 34 | 34
2018-09-03 18:00 | 22 | 21
2018-09-03 18:30 | 34 | 31
2018-09-03 19:00 | 32 | 29
2018-09-03 19:30 | 33 | 30
2018-09-03 20:00 | 45 | 45
2018-09-03 20:30 | 43 | 43
2018-09-03 21:00 | 51 | 51
2018-09-03 21:30 | 52 | 51
2018-09-03 22:00 | 51 | 51
2018-09-03 22:30 | 48 | 47
2018-09-03 23:00 | 44 | 44
2018-09-03 23:30 | 41 | 40
2018-09-04 | 40 | 40
2018-09-04 00:30 | 41 | 40
2018-09-04 01:00 | 40 | 40
2018-09-04 01:30 | 41 | 41
2018-09-04 02:00 | 40 | 40
2018-09-04 02:30 | 41 | 40
2018-09-04 03:00 | 40 | 39
2018-09-04 03:30 | 39 | 38
2018-09-04 04:00 | 39 | 38
2018-09-04 04:30 | 40 | 39
2018-09-04 05:00 | 40 | 40
2018-09-04 05:30 | 41 | 40
2018-09-04 06:00 | 42 | 41
2018-09-04 06:30 | 43 | 42
2018-09-04 07:00 | 11 | 11
2018-09-04 07:30 | 13 | 12
2018-09-04 08:00 | 5 | 5
2018-09-04 08:30 | 7 | 6
2018-09-04 09:00 | 7 | 3
2018-09-04 09:30 | 7 | 3
2018-09-04 10:00 | 6 | 2
2018-09-04 10:30 | 7 | 0
2018-09-04 11:00 | 7 | 2
2018-09-04 11:30 | 7 | 1
2018-09-04 12:00 | 6 | 2
2018-09-04 12:30 | 7 | 1
2018-09-04 13:00 | 8 | 6
2018-09-04 13:30 | 8 | 7
2018-09-04 14:00 | 12 | 11
2018-09-04 14:30 | 12 | 11
2018-09-04 15:00 | 19 | 19
2018-09-04 15:30 | 20 | 20
2018-09-04 16:00 | 9 | 7
2018-09-04 16:30 | 16 | 15
2018-09-04 17:00 | 25 | 25
2018-09-04 17:30 | 39 | 39
2018-09-04 18:00 | 36 | 36
2018-09-04 18:30 | 29 | 28
2018-09-04 19:00 | 23 | 20
2018-09-04 19:30 | 31 | 30
2018-09-04 20:00 | 49 | 49
2018-09-04 20:30 | 52 | 51
2018-09-04 21:00 | 51 | 50
2018-09-04 21:30 | 50 | 49
2018-09-04 22:00 | 50 | 49
2018-09-04 22:30 | 39 | 39
2018-09-04 23:00 | 40 | 39
2018-09-04 23:30 | 43 | 41
2018-09-05 | 42 | 41
2018-09-05 00:30 | 43 | 41
2018-09-05 01:00 | 41 | 39
2018-09-05 01:30 | 42 | 40
2018-09-05 02:00 | 42 | 41
2018-09-05 02:30 | 43 | 42
2018-09-05 03:00 | 42 | 41
2018-09-05 03:30 | 42 | 41
2018-09-05 04:00 | 42 | 41
2018-09-05 04:30 | 43 | 42
2018-09-05 05:00 | 42 | 41
2018-09-05 05:30 | 42 | 41
2018-09-05 06:00 | 43 | 42
2018-09-05 06:30 | 45 | 44
2018-09-05 07:00 | 17 | 17
2018-09-05 07:30 | 6 | 6
2018-09-05 08:00 | 3 | 3
2018-09-05 08:30 | 9 | 9
2018-09-05 09:00 | 3 | 1
2018-09-05 09:30 | 3 | 2
2018-09-05 10:00 | 14 | 14
2018-09-05 10:30 | 15 | 15
2018-09-05 11:00 | 6 | 6
2018-09-05 11:30 | 5 | 5
2018-09-05 12:00 | 2 | 1
2018-09-05 12:30 | 4 | 3
2018-09-05 13:00 | 12 | 9
2018-09-05 13:30 | 15 | 4
2018-09-05 14:00 | 14 | 5
2018-09-05 14:30 | 14 | 7
2018-09-05 15:00 | 15 | 4
2018-09-05 15:30 | 15 | 8
2018-09-05 16:00 | 16 | 11
2018-09-05 16:30 | 19 | 14
2018-09-05 17:00 | 38 | 38
2018-09-05 17:30 | 38 | 36
2018-09-05 18:00 | 19 | 16
2018-09-05 18:30 | 19 | 16
2018-09-05 19:00 | 19 | 15
2018-09-05 19:30 | 18 | 15
2018-09-05 20:00 | 22 | 20
2018-09-05 20:30 | 31 | 30
2018-09-05 21:00 | 38 | 37
2018-09-05 21:30 | 40 | 40
2018-09-05 22:00 | 47 | 47
2018-09-05 22:30 | 47 | 47
2018-09-05 23:00 | 46 | 45
2018-09-05 23:30 | 44 | 43
2018-09-06 | 43 | 42
2018-09-06 00:30 | 44 | 43
2018-09-06 01:00 | 43 | 43
2018-09-06 01:30 | 42 | 41
2018-09-06 02:00 | 42 | 41
2018-09-06 02:30 | 42 | 41
2018-09-06 03:00 | 41 | 40
2018-09-06 03:30 | 41 | 41
2018-09-06 04:00 | 43 | 42
2018-09-06 04:30 | 44 | 43
2018-09-06 05:00 | 44 | 44
2018-09-06 05:30 | 44 | 43
2018-09-06 06:00 | 44 | 43
2018-09-06 06:30 | 33 | 33
2018-09-06 07:00 | 21 | 20
2018-09-06 07:30 | 11 | 11
2018-09-06 08:00 | 8 | 8
2018-09-06 08:30 | 9 | 6
2018-09-06 09:00 | 10 | 6
2018-09-06 09:30 | 9 | 1
2018-09-06 10:00 | 9 | 1
2018-09-06 10:30 | 8 | 0
2018-09-06 11:00 | 9 | 0
2018-09-06 11:30 | 10 | 5
2018-09-06 12:00 | 9 | 1
2018-09-06 12:30 | 19 | 18
2018-09-06 13:00 | 18 | 14
2018-09-06 13:30 | 24 | 21
2018-09-06 14:00 | 20 | 16
2018-09-06 14:30 | 20 | 16
2018-09-06 15:00 | 19 | 16
2018-09-06 15:30 | 18 | 14
2018-09-06 16:00 | 29 | 27
2018-09-06 16:30 | 28 | 26
2018-09-06 17:00 | 27 | 26
2018-09-06 17:30 | 31 | 30
2018-09-06 18:00 | 39 | 39
2018-09-06 18:30 | 49 | 48
2018-09-06 19:00 | 31 | 31
2018-09-06 19:30 | 38 | 38
2018-09-06 20:00 | 46 | 46
2018-09-06 20:30 | 51 | 50
2018-09-06 21:00 | 39 | 39
2018-09-06 21:30 | 47 | 46
2018-09-06 22:00 | 50 | 49
2018-09-06 22:30 | 50 | 48
2018-09-06 23:00 | 48 | 47
2018-09-06 23:30 | 47 | 46
2018-09-07 | 48 | 47
2018-09-07 00:30 | 49 | 48
2018-09-07 01:00 | 49 | 48
2018-09-07 01:30 | 49 | 48
2018-09-07 02:00 | 47 | 46
2018-09-07 02:30 | 46 | 45
2018-09-07 03:00 | 44 | 43
2018-09-07 03:30 | 45 | 43
2018-09-07 04:00 | 45 | 43
2018-09-07 04:30 | 45 | 43
2018-09-07 05:00 | 46 | 45
2018-09-07 05:30 | 45 | 44
2018-09-07 06:00 | 45 | 43
2018-09-07 06:30 | 45 | 44
2018-09-07 07:00 | 27 | 27
2018-09-07 07:30 | 14 | 13
2018-09-07 08:00 | 18 | 13
2018-09-07 08:30 | 18 | 13
2018-09-07 09:00 | 16 | 3
2018-09-07 09:30 | 20 | 7
2018-09-07 10:00 | 19 | 6
2018-09-07 10:30 | 18 | 5
2018-09-07 11:00 | 18 | 2
2018-09-07 11:30 | 18 | 1
2018-09-07 12:00 | 18 | 1
2018-09-07 12:30 | 18 | 0
2018-09-07 13:00 | 19 | 2
2018-09-07 13:30 | 19 | 3
2018-09-07 14:00 | 18 | 2
2018-09-07 14:30 | 18 | 0
2018-09-07 15:00 | 19 | 5
2018-09-07 15:30 | 20 | 11
2018-09-07 16:00 | 21 | 13
2018-09-07 16:30 | 25 | 18
2018-09-07 17:00 | 31 | 28
2018-09-07 17:30 | 42 | 42
2018-09-07 18:00 | 43 | 43
2018-09-07 18:30 | 36 | 26
2018-09-07 19:00 | 35 | 21
2018-09-07 19:30 | 36 | 30
2018-09-07 20:00 | 36 | 33
2018-09-07 20:30 | 39 | 38
2018-09-07 21:00 | 43 | 42
2018-09-07 21:30 | 44 | 43
2018-09-07 22:00 | 41 | 40
2018-09-07 22:30 | 42 | 40
2018-09-07 23:00 | 47 | 44
2018-09-07 23:30 | 46 | 43
2018-09-08 | 46 | 43
2018-09-08 00:30 | 46 | 44
2018-09-08 01:00 | 45 | 42
2018-09-08 01:30 | 44 | 42
2018-09-08 02:00 | 44 | 42
2018-09-08 02:30 | 44 | 41
2018-09-08 03:00 | 44 | 41
2018-09-08 03:30 | 44 | 42
2018-09-08 04:00 | 44 | 42
2018-09-08 04:30 | 44 | 42
2018-09-08 05:00 | 44 | 42
2018-09-08 05:30 | 45 | 44
2018-09-08 06:00 | 46 | 44
2018-09-08 06:30 | 45 | 43
2018-09-08 07:00 | 41 | 39
2018-09-08 07:30 | 31 | 28
2018-09-08 08:00 | 21 | 16
2018-09-08 08:30 | 15 | 7
2018-09-08 09:00 | 14 | 5
2018-09-08 09:30 | 13 | 5
2018-09-08 10:00 | 13 | 2
2018-09-08 10:30 | 13 | 0
2018-09-08 11:00 | 13 | 3
2018-09-08 11:30 | 18 | 2
2018-09-08 12:00 | 18 | 2
2018-09-08 12:30 | 17 | 5
2018-09-08 13:00 | 19 | 2
2018-09-08 13:30 | 18 | 0
2018-09-08 14:00 | 19 | 2
2018-09-08 14:30 | 18 | 0
2018-09-08 15:00 | 19 | 0
2018-09-08 15:30 | 21 | 3
2018-09-08 16:00 | 21 | 3
2018-09-08 16:30 | 22 | 11
2018-09-08 17:00 | 28 | 22
2018-09-08 17:30 | 42 | 38
2018-09-08 18:00 | 44 | 41
2018-09-08 18:30 | 49 | 49
2018-09-08 19:00 | 49 | 49
2018-09-08 19:30 | 49 | 49
2018-09-08 20:00 | 49 | 49
2018-09-08 20:30 | 49 | 49
2018-09-08 21:00 | 49 | 49
2018-09-08 21:30 | 48 | 48
2018-09-08 22:00 | 47 | 46
2018-09-08 22:30 | 45 | 44
2018-09-08 23:00 | 43 | 42
2018-09-08 23:30 | 43 | 42
2018-09-09 | 43 | 42
2018-09-09 00:30 | 45 | 44
2018-09-09 01:00 | 44 | 42
2018-09-09 01:30 | 42 | 41
2018-09-09 02:00 | 43 | 41
2018-09-09 02:30 | 41 | 40
2018-09-09 03:00 | 42 | 41
2018-09-09 03:30 | 42 | 41
2018-09-09 04:00 | 42 | 41
2018-09-09 04:30 | 42 | 41
2018-09-09 05:00 | 43 | 42
2018-09-09 05:30 | 42 | 42
2018-09-09 06:00 | 42 | 41
2018-09-09 06:30 | 42 | 41
2018-09-09 07:00 | 36 | 35
2018-09-09 07:30 | 24 | 22
2018-09-09 08:00 | 16 | 12
2018-09-09 08:30 | 13 | 4
2018-09-09 09:00 | 13 | 2
2018-09-09 09:30 | 15 | 6
2018-09-09 10:00 | 15 | 6
2018-09-09 10:30 | 14 | 5
2018-09-09 11:00 | 15 | 7
2018-09-09 11:30 | 15 | 6
2018-09-09 12:00 | 14 | 5
2018-09-09 12:30 | 14 | 3
2018-09-09 13:00 | 14 | 2
2018-09-09 13:30 | 13 | 1
2018-09-09 14:00 | 13 | 2
2018-09-09 14:30 | 13 | 1
2018-09-09 15:00 | 13 | 2
2018-09-09 15:30 | 13 | 4
2018-09-09 16:00 | 15 | 9
2018-09-09 16:30 | 20 | 16
2018-09-09 17:00 | 27 | 24
2018-09-09 17:30 | 38 | 36
2018-09-09 18:00 | 48 | 46
2018-09-09 18:30 | 29 | 29
2018-09-09 19:00 | 15 | 14
2018-09-09 19:30 | 27 | 27
2018-09-09 20:00 | 18 | 18
2018-09-09 20:30 | 32 | 32
2018-09-09 21:00 | 48 | 47
2018-09-09 21:30 | 50 | 49
2018-09-09 22:00 | 50 | 48
2018-09-09 22:30 | 47 | 45
2018-09-09 23:00 | 47 | 45
2018-09-09 23:30 | 48 | 46
2018-09-10 | 48 | 47
2018-09-10 00:30 | 48 | 46
2018-09-10 01:00 | 48 | 46
2018-09-10 01:30 | 48 | 47
2018-09-10 02:00 | 46 | 45
2018-09-10 02:30 | 45 | 44
2018-09-10 03:00 | 46 | 44
2018-09-10 03:30 | 47 | 45
2018-09-10 04:00 | 46 | 45
2018-09-10 04:30 | 46 | 44
2018-09-10 05:00 | 45 | 44
2018-09-10 05:30 | 46 | 44
2018-09-10 06:00 | 47 | 45
2018-09-10 06:30 | 48 | 46
2018-09-10 07:00 | 42 | 40
2018-09-10 07:30 | 30 | 27
2018-09-10 08:00 | 23 | 16
2018-09-10 08:30 | 20 | 7
2018-09-10 09:00 | 19 | 0
2018-09-10 09:30 | 18 | 3
2018-09-10 10:00 | 16 | 3
2018-09-10 10:30 | 17 | 4
2018-09-10 11:00 | 18 | 5
2018-09-10 11:30 | 17 | 4
2018-09-10 12:00 | 17 | 4
2018-09-10 12:30 | 17 | 4
2018-09-10 13:00 | 16 | 3
2018-09-10 13:30 | 16 | 2
2018-09-10 14:00 | 15 | 2
2018-09-10 14:30 | 16 | 2
2018-09-10 15:00 | 15 | 1
2018-09-10 15:30 | 15 | 3
2018-09-10 16:00 | 15 | 7
2018-09-10 16:30 | 20 | 15
2018-09-10 17:00 | 29 | 26
2018-09-10 17:30 | 41 | 38
2018-09-10 18:00 | 48 | 46
2018-09-10 18:30 | 33 | 33
2018-09-10 19:00 | 19 | 17
2018-09-10 19:30 | 41 | 41
2018-09-10 20:00 | 51 | 50
2018-09-10 20:30 | 50 | 49
2018-09-10 21:00 | 50 | 50
2018-09-10 21:30 | 49 | 48
2018-09-10 22:00 | 49 | 48
2018-09-10 22:30 | 48 | 47
2018-09-10 23:00 | 46 | 44
2018-09-10 23:30 | 46 | 44
2018-09-11 | 46 | 44
2018-09-11 00:30 | 46 | 44
2018-09-11 01:00 | 45 | 44
2018-09-11 01:30 | 46 | 44
2018-09-11 02:00 | 43 | 42
2018-09-11 02:30 | 43 | 41
2018-09-11 03:00 | 44 | 42
2018-09-11 03:30 | 44 | 42
2018-09-11 04:00 | 44 | 42
2018-09-11 04:30 | 44 | 42
2018-09-11 05:00 | 44 | 43
2018-09-11 05:30 | 45 | 43
2018-09-11 06:00 | 45 | 43
2018-09-11 06:30 | 48 | 46
2018-09-11 07:00 | 44 | 42
2018-09-11 07:30 | 34 | 32
2018-09-11 08:00 | 27 | 23
2018-09-11 08:30 | 17 | 14
2018-09-11 09:00 | 5 | 2
2018-09-11 09:30 | 4 | 3
2018-09-11 10:00 | 11 | 11
2018-09-11 10:30 | 9 | 9
2018-09-11 11:00 | 6 | 6
2018-09-11 11:30 | 4 | 1
2018-09-11 12:00 | 3 | 1
2018-09-11 12:30 | 4 | 0
2018-09-11 13:00 | 8 | 8
2018-09-11 13:30 | 9 | 9
2018-09-11 14:00 | 8 | 8
2018-09-11 14:30 | 11 | 10
2018-09-11 15:00 | 8 | 7
2018-09-11 15:30 | 6 | 5
2018-09-11 16:00 | 7 | 7
2018-09-11 16:30 | 14 | 14
2018-09-11 17:00 | 31 | 30
2018-09-11 17:30 | 39 | 39
2018-09-11 18:00 | 47 | 47
2018-09-11 18:30 | 49 | 49
2018-09-11 19:00 | 49 | 48
2018-09-11 19:30 | 48 | 48
2018-09-11 20:00 | 49 | 49
2018-09-11 20:30 | 48 | 48
2018-09-11 21:00 | 47 | 47
2018-09-11 21:30 | 47 | 46
2018-09-11 22:00 | 46 | 46
2018-09-11 22:30 | 44 | 43
2018-09-11 23:00 | 45 | 42
2018-09-11 23:30 | 45 | 43
2018-09-12 | 45 | 43
2018-09-12 00:30 | 46 | 43
2018-09-12 01:00 | 45 | 43
2018-09-12 01:30 | 43 | 41
2018-09-12 02:00 | 16 | 15
2018-09-12 02:30 | 15 | 9
2018-09-12 03:00 | 15 | 10
2018-09-12 03:30 | 16 | 14
2018-09-12 04:00 | 28 | 28
2018-09-12 04:30 | 41 | 40
2018-09-12 05:00 | 41 | 40
2018-09-12 05:30 | 42 | 41
2018-09-12 06:00 | 45 | 43
2018-09-12 06:30 | 45 | 43
2018-09-12 07:00 | 43 | 41
2018-09-12 07:30 | 38 | 36
2018-09-12 08:00 | 32 | 31
2018-09-12 08:30 | 29 | 29
2018-09-12 09:00 | 23 | 23
2018-09-12 09:30 | 5 | 5
2018-09-12 10:00 | 2 | 1
2018-09-12 10:30 | 2 | 2
2018-09-12 11:00 | 5 | 5
2018-09-12 11:30 | 19 | 19
2018-09-12 12:00 | 19 | 19
2018-09-12 12:30 | 20 | 19
2018-09-12 13:00 | 10 | 9
2018-09-12 13:30 | 7 | 5
2018-09-12 14:00 | 4 | 2
2018-09-12 14:30 | 4 | 3
2018-09-12 15:00 | 3 | 3
2018-09-12 15:30 | 9 | 8
2018-09-12 16:00 | 7 | 6
2018-09-12 16:30 | 22 | 22
2018-09-12 17:00 | 39 | 38
2018-09-12 17:30 | 42 | 42
2018-09-12 18:00 | 47 | 46
2018-09-12 18:30 | 48 | 48
2018-09-12 19:00 | 43 | 43
2018-09-12 19:30 | 45 | 45
2018-09-12 20:00 | 49 | 49
2018-09-12 20:30 | 48 | 48
2018-09-12 21:00 | 48 | 48
2018-09-12 21:30 | 47 | 46
2018-09-12 22:00 | 43 | 43
2018-09-12 22:30 | 44 | 43
2018-09-12 23:00 | 44 | 44
2018-09-12 23:30 | 43 | 43
2018-09-13 | 43 | 43
2018-09-13 00:30 | 43 | 43
2018-09-13 01:00 | 43 | 43
2018-09-13 01:30 | 45 | 44
2018-09-13 02:00 | 44 | 44
2018-09-13 02:30 | 42 | 42
2018-09-13 03:00 | 43 | 42
2018-09-13 03:30 | 43 | 43
2018-09-13 04:00 | 51 | 47
2018-09-13 04:30 | 51 | 48
2018-09-13 05:00 | 52 | 49
2018-09-13 05:30 | 53 | 50
2018-09-13 06:00 | 55 | 52
2018-09-13 06:30 | 58 | 54
2018-09-13 07:00 | 55 | 49
2018-09-13 07:30 | 49 | 41
2018-09-13 08:00 | 42 | 33
2018-09-13 08:30 | 33 | 24
2018-09-13 09:00 | 21 | 18
2018-09-13 09:30 | 19 | 15
2018-09-13 10:00 | 19 | 15
2018-09-13 10:30 | 18 | 15
2018-09-13 11:00 | 18 | 15
2018-09-13 11:30 | 16 | 12
2018-09-13 12:00 | 12 | 11
2018-09-13 12:30 | 8 | 2
2018-09-13 13:00 | 15 | 14
2018-09-13 13:30 | 17 | 16
2018-09-13 14:00 | 21 | 20
2018-09-13 14:30 | 10 | 8
2018-09-13 15:00 | 16 | 16
2018-09-13 15:30 | 19 | 17
2018-09-13 16:00 | 19 | 19
2018-09-13 16:30 | 25 | 23
2018-09-13 17:00 | 34 | 34
2018-09-13 17:30 | 47 | 46
2018-09-13 18:00 | 56 | 55
2018-09-13 18:30 | 56 | 56
2018-09-13 19:00 | 59 | 55
2018-09-13 19:30 | 58 | 54
2018-09-13 20:00 | 57 | 52
2018-09-13 20:30 | 51 | 47
2018-09-13 21:00 | 51 | 47
2018-09-13 21:30 | 47 | 45
2018-09-13 22:00 | 45 | 45
2018-09-13 22:30 | 43 | 43
2018-09-13 23:00 | 42 | 42
2018-09-13 23:30 | 42 | 42
2018-09-14 | 42 | 41
2018-09-14 00:30 | 42 | 41
2018-09-14 01:00 | 44 | 43
2018-09-14 01:30 | 43 | 43
2018-09-14 02:00 | 45 | 42
2018-09-14 02:30 | 45 | 43
2018-09-14 03:00 | 47 | 45
2018-09-14 03:30 | 46 | 44
2018-09-14 04:00 | 46 | 44
2018-09-14 04:30 | 47 | 45
2018-09-14 05:00 | 46 | 44
2018-09-14 05:30 | 46 | 44
2018-09-14 06:00 | 46 | 44
2018-09-14 06:30 | 47 | 45
2018-09-14 07:00 | 42 | 39
2018-09-14 07:30 | 32 | 27
2018-09-14 08:00 | 25 | 17
2018-09-14 08:30 | 21 | 9
2018-09-14 09:00 | 19 | 1
2018-09-14 09:30 | 20 | 4
2018-09-14 10:00 | 24 | 21
2018-09-14 10:30 | 34 | 32
2018-09-14 11:00 | 35 | 33
2018-09-14 11:30 | 38 | 36
2018-09-14 12:00 | 34 | 33
2018-09-14 12:30 | 29 | 26
2018-09-14 13:00 | 25 | 21
2018-09-14 13:30 | 22 | 18
2018-09-14 14:00 | 22 | 17
2018-09-14 14:30 | 22 | 14
2018-09-14 15:00 | 20 | 13
2018-09-14 15:30 | 18 | 8
2018-09-14 16:00 | 19 | 4
2018-09-14 16:30 | 24 | 14
2018-09-14 17:00 | 32 | 25
2018-09-14 17:30 | 43 | 39
2018-09-14 18:00 | 54 | 51
2018-09-14 18:30 | 55 | 53
2018-09-14 19:00 | 55 | 53
2018-09-14 19:30 | 54 | 52
2018-09-14 20:00 | 29 | 28
2018-09-14 20:30 | 21 | 18
2018-09-14 21:00 | 20 | 18
2018-09-14 21:30 | 19 | 17
2018-09-14 22:00 | 20 | 19
2018-09-14 22:30 | 20 | 19
2018-09-14 23:00 | 18 | 17
2018-09-14 23:30 | 17 | 16
2018-09-15 | 15 | 15
2018-09-15 00:30 | 16 | 15
2018-09-15 01:00 | 16 | 15
2018-09-15 01:30 | 23 | 22
2018-09-15 02:00 | 35 | 35
2018-09-15 02:30 | 43 | 42
2018-09-15 03:00 | 43 | 43
2018-09-15 03:30 | 43 | 42
2018-09-15 04:00 | 44 | 43
2018-09-15 04:30 | 44 | 44
2018-09-15 05:00 | 43 | 42
2018-09-15 05:30 | 45 | 44
2018-09-15 06:00 | 45 | 44
2018-09-15 06:30 | 43 | 42
2018-09-15 07:00 | 37 | 36
2018-09-15 07:30 | 26 | 25
2018-09-15 08:00 | 18 | 16
2018-09-15 08:30 | 14 | 9
2018-09-15 09:00 | 11 | 2
2018-09-15 09:30 | 13 | 2
2018-09-15 10:00 | 18 | 12
2018-09-15 10:30 | 14 | 3
2018-09-15 11:00 | 14 | 2
2018-09-15 11:30 | 14 | 5
2018-09-15 12:00 | 18 | 12
2018-09-15 12:30 | 17 | 12
2018-09-15 13:00 | 17 | 12
2018-09-15 13:30 | 18 | 12
2018-09-15 14:00 | 17 | 11
2018-09-15 14:30 | 16 | 10
2018-09-15 15:00 | 15 | 8
2018-09-15 15:30 | 13 | 4
2018-09-15 16:00 | 12 | 4
2018-09-15 16:30 | 16 | 11
2018-09-15 17:00 | 24 | 21
2018-09-15 17:30 | 39 | 37
2018-09-15 18:00 | 49 | 48
2018-09-15 18:30 | 53 | 51
2018-09-15 19:00 | 49 | 48
2018-09-15 19:30 | 53 | 51
2018-09-15 20:00 | 52 | 50
2018-09-15 20:30 | 52 | 50
2018-09-15 21:00 | 52 | 50
2018-09-15 21:30 | 51 | 49
2018-09-15 22:00 | 50 | 48
2018-09-15 22:30 | 50 | 48
2018-09-15 23:00 | 50 | 48
2018-09-15 23:30 | 48 | 47
2018-09-16 | 48 | 47
2018-09-16 00:30 | 48 | 47
2018-09-16 01:00 | 47 | 46
2018-09-16 01:30 | 47 | 46
2018-09-16 02:00 | 45 | 45
2018-09-16 02:30 | 46 | 45
2018-09-16 03:00 | 46 | 45
2018-09-16 03:30 | 45 | 44
2018-09-16 04:00 | 45 | 45
2018-09-16 04:30 | 44 | 44
2018-09-16 05:00 | 45 | 44
2018-09-16 05:30 | 44 | 44
2018-09-16 06:00 | 43 | 42
2018-09-16 06:30 | 42 | 41
2018-09-16 07:00 | 36 | 36
2018-09-16 07:30 | 25 | 24
2018-09-16 08:00 | 14 | 11
2018-09-16 08:30 | 10 | 5
2018-09-16 09:00 | 9 | 1
2018-09-16 09:30 | 12 | 7
2018-09-16 10:00 | 15 | 12
2018-09-16 10:30 | 13 | 13
2018-09-16 11:00 | 19 | 12
2018-09-16 11:30 | 11 | 10
2018-09-16 12:00 | 11 | 8
2018-09-16 12:30 | 17 | 8
2018-09-16 13:00 | 14 | 8
2018-09-16 13:30 | 16 | 6
2018-09-16 14:00 | 11 | 7
2018-09-16 14:30 | 11 | 6
2018-09-16 15:00 | 8 | 3
2018-09-16 15:30 | 3 | 1
2018-09-16 16:00 | 10 | 7
2018-09-16 16:30 | 22 | 21
2018-09-16 17:00 | 30 | 29
2018-09-16 17:30 | 41 | 41
2018-09-16 18:00 | 50 | 50
2018-09-16 18:30 | 58 | 56
2018-09-16 19:00 | 72 | 72
2018-09-16 19:30 | 73 | 73
2018-09-16 20:00 | 73 | 73
2018-09-16 20:30 | 72 | 71
2018-09-16 21:00 | 72 | 72
2018-09-16 21:30 | 71 | 71
2018-09-16 22:00 | 70 | 70
2018-09-16 22:30 | 69 | 68
2018-09-16 23:00 | 67 | 66
2018-09-16 23:30 | 68 | 66
2018-09-17 | 68 | 67
2018-09-17 00:30 | 69 | 68
2018-09-17 01:00 | 68 | 67
2018-09-17 01:30 | 67 | 67
2018-09-17 02:00 | 67 | 66
2018-09-17 02:30 | 66 | 65
2018-09-17 03:00 | 64 | 64
2018-09-17 03:30 | 62 | 62
2018-09-17 04:00 | 61 | 60
2018-09-17 04:30 | 64 | 64
2018-09-17 05:00 | 64 | 64
2018-09-17 05:30 | 66 | 65
2018-09-17 06:00 | 66 | 66
2018-09-17 06:30 | 66 | 65
2018-09-17 07:00 | 62 | 61
2018-09-17 07:30 | 55 | 54
2018-09-17 08:00 | 46 | 44
2018-09-17 08:30 | 37 | 35
2018-09-17 09:00 | 31 | 28
2018-09-17 09:30 | 24 | 19
2018-09-17 10:00 | 19 | 8
2018-09-17 10:30 | 19 | 16
2018-09-17 11:00 | 4 | 1
2018-09-17 11:30 | 2 | 2
2018-09-17 12:00 | 6 | 6
2018-09-17 12:30 | 20 | 13
2018-09-17 13:00 | 18 | 18
2018-09-17 13:30 | 27 | 25
2018-09-17 14:00 | 10 | 8
2018-09-17 14:30 | 8 | 1
2018-09-17 15:00 | 7 | 4
2018-09-17 15:30 | 12 | 11
2018-09-17 16:00 | 20 | 20
2018-09-17 16:30 | 28 | 27
2018-09-17 17:00 | 38 | 38
2018-09-17 17:30 | 55 | 55
2018-09-17 18:00 | 64 | 64
2018-09-17 18:30 | 66 | 66
2018-09-17 19:00 | 66 | 66
2018-09-17 19:30 | 68 | 68
2018-09-17 20:00 | 67 | 67
2018-09-17 20:30 | 65 | 65
2018-09-17 21:00 | 64 | 64
2018-09-17 21:30 | 63 | 62
2018-09-17 22:00 | 62 | 62
2018-09-17 22:30 | 60 | 60
2018-09-17 23:00 | 59 | 58
2018-09-17 23:30 | 59 | 58
2018-09-18 | 57 | 56
2018-09-18 00:30 | 57 | 56
2018-09-18 01:00 | 56 | 56
2018-09-18 01:30 | 56 | 55
2018-09-18 02:00 | 57 | 56
2018-09-18 02:30 | 60 | 59
2018-09-18 03:00 | 61 | 60
2018-09-18 03:30 | 60 | 59
2018-09-18 04:00 | 61 | 60
2018-09-18 04:30 | 60 | 59
2018-09-18 05:00 | 58 | 58
2018-09-18 05:30 | 55 | 54
2018-09-18 06:00 | 55 | 55
2018-09-18 06:30 | 55 | 55
2018-09-18 07:00 | 55 | 55
2018-09-18 07:30 | 54 | 54
2018-09-18 08:00 | 53 | 52
2018-09-18 08:30 | 42 | 41
2018-09-18 09:00 | 44 | 44
2018-09-18 09:30 | 22 | 21
2018-09-18 10:00 | 18 | 18
2018-09-18 10:30 | 21 | 19
2018-09-18 11:00 | 25 | 25
2018-09-18 11:30 | 16 | 15
2018-09-18 12:00 | 16 | 15
2018-09-18 12:30 | 13 | 12
2018-09-18 13:00 | 19 | 19
2018-09-18 13:30 | 15 | 14
2018-09-18 14:00 | 22 | 22
2018-09-18 14:30 | 11 | 8
2018-09-18 15:00 | 19 | 18
2018-09-18 15:30 | 23 | 23
2018-09-18 16:00 | 22 | 20
2018-09-18 16:30 | 30 | 30
2018-09-18 17:00 | 39 | 39
2018-09-18 17:30 | 54 | 54
2018-09-18 18:00 | 64 | 64
2018-09-18 18:30 | 68 | 67
2018-09-18 19:00 | 47 | 47
2018-09-18 19:30 | 49 | 49
2018-09-18 20:00 | 63 | 62
2018-09-18 20:30 | 66 | 65
2018-09-18 21:00 | 65 | 64
2018-09-18 21:30 | 64 | 63
2018-09-18 22:00 | 58 | 57
2018-09-18 22:30 | 53 | 53
2018-09-18 23:00 | 53 | 52
2018-09-18 23:30 | 53 | 52
2018-09-19 | 51 | 51
2018-09-19 00:30 | 53 | 52
2018-09-19 01:00 | 53 | 52
2018-09-19 01:30 | 52 | 52
2018-09-19 02:00 | 48 | 47
2018-09-19 02:30 | 49 | 48
2018-09-19 03:00 | 47 | 46
2018-09-19 03:30 | 48 | 47
2018-09-19 04:00 | 48 | 47
2018-09-19 04:30 | 46 | 45
2018-09-19 05:00 | 46 | 45
2018-09-19 05:30 | 47 | 46
2018-09-19 06:00 | 47 | 46
2018-09-19 06:30 | 49 | 47
2018-09-19 07:00 | 43 | 42
2018-09-19 07:30 | 40 | 39
2018-09-19 08:00 | 32 | 31
2018-09-19 08:30 | 21 | 19
2018-09-19 09:00 | 17 | 10
2018-09-19 09:30 | 19 | 10
2018-09-19 10:00 | 25 | 21
2018-09-19 10:30 | 6 | 6
2018-09-19 11:00 | 15 | 11
2018-09-19 11:30 | 26 | 25
2018-09-19 12:00 | 27 | 26
2018-09-19 12:30 | 29 | 29
2018-09-19 13:00 | 22 | 21
2018-09-19 13:30 | 16 | 15
2018-09-19 14:00 | 17 | 16
2018-09-19 14:30 | 8 | 5
2018-09-19 15:00 | 9 | 6
2018-09-19 15:30 | 8 | 1
2018-09-19 16:00 | 9 | 5
2018-09-19 16:30 | 15 | 13
2018-09-19 17:00 | 24 | 24
2018-09-19 17:30 | 41 | 41
2018-09-19 18:00 | 53 | 53
2018-09-19 18:30 | 60 | 58
2018-09-19 19:00 | 60 | 58
2018-09-19 19:30 | 61 | 59
2018-09-19 20:00 | 60 | 58
2018-09-19 20:30 | 59 | 57
2018-09-19 21:00 | 59 | 57
2018-09-19 21:30 | 59 | 57
2018-09-19 22:00 | 58 | 57
2018-09-19 22:30 | 55 | 53
2018-09-19 23:00 | 54 | 52
2018-09-19 23:30 | 53 | 52
2018-09-20 | 53 | 52
2018-09-20 00:30 | 51 | 50
2018-09-20 01:00 | 49 | 47
2018-09-20 01:30 | 47 | 46
2018-09-20 02:00 | 47 | 45
2018-09-20 02:30 | 47 | 45
2018-09-20 03:00 | 47 | 46
2018-09-20 03:30 | 47 | 45
2018-09-20 04:00 | 46 | 44
2018-09-20 04:30 | 46 | 44
2018-09-20 05:00 | 46 | 44
2018-09-20 05:30 | 46 | 45
2018-09-20 06:00 | 46 | 45
2018-09-20 06:30 | 46 | 44
2018-09-20 07:00 | 38 | 35
2018-09-20 07:30 | 30 | 26
2018-09-20 08:00 | 21 | 14
2018-09-20 08:30 | 19 | 12
2018-09-20 09:00 | 16 | 4
2018-09-20 09:30 | 20 | 10
2018-09-20 10:00 | 19 | 17
2018-09-20 10:30 | 32 | 31
2018-09-20 11:00 | 32 | 31
2018-09-20 11:30 | 10 | 6
2018-09-20 12:00 | 29 | 28
2018-09-20 12:30 | 15 | 13
2018-09-20 13:00 | 34 | 34
2018-09-20 13:30 | 42 | 40
2018-09-20 14:00 | 34 | 33
2018-09-20 14:30 | 9 | 9
2018-09-20 15:00 | 9 | 2
2018-09-20 15:30 | 10 | 5
2018-09-20 16:00 | 14 | 11
2018-09-20 16:30 | 17 | 15
2018-09-20 17:00 | 25 | 24
2018-09-20 17:30 | 52 | 50
2018-09-20 18:00 | 53 | 53
2018-09-20 18:30 | 29 | 24
2018-09-20 19:00 | 38 | 29
2018-09-20 19:30 | 49 | 45
2018-09-20 20:00 | 58 | 57
2018-09-20 20:30 | 58 | 58
2018-09-20 21:00 | 58 | 57
2018-09-20 21:30 | 58 | 57
2018-09-20 22:00 | 57 | 56
2018-09-20 22:30 | 57 | 56
2018-09-20 23:00 | 53 | 52
2018-09-20 23:30 | 49 | 49
2018-09-21 | 49 | 48
2018-09-21 00:30 | 49 | 48
2018-09-21 01:00 | 48 | 47
2018-09-21 01:30 | 49 | 48
2018-09-21 02:00 | 48 | 47
2018-09-21 02:30 | 48 | 47
2018-09-21 03:00 | 47 | 46
2018-09-21 03:30 | 47 | 46
2018-09-21 04:00 | 46 | 46
2018-09-21 04:30 | 46 | 45
2018-09-21 05:00 | 48 | 47
2018-09-21 05:30 | 47 | 46
2018-09-21 06:00 | 47 | 47
2018-09-21 06:30 | 47 | 46
2018-09-21 07:00 | 41 | 40
2018-09-21 07:30 | 29 | 28
2018-09-21 08:00 | 19 | 17
2018-09-21 08:30 | 11 | 6
2018-09-21 09:00 | 9 | 4
2018-09-21 09:30 | 8 | 1
2018-09-21 10:00 | 3 | 0
2018-09-21 10:30 | 17 | 13
2018-09-21 11:00 | 29 | 21
2018-09-21 11:30 | 18 | 5
2018-09-21 12:00 | 19 | 6
2018-09-21 12:30 | 20 | 4
2018-09-21 13:00 | 21 | 3
2018-09-21 13:30 | 20 | 2
2018-09-21 14:00 | 20 | 4
2018-09-21 14:30 | 20 | 2
2018-09-21 15:00 | 20 | 5
2018-09-21 15:30 | 20 | 7
2018-09-21 16:00 | 27 | 21
2018-09-21 16:30 | 31 | 25
2018-09-21 17:00 | 36 | 32
2018-09-21 17:30 | 45 | 45
2018-09-21 18:00 | 58 | 58
2018-09-21 18:30 | 64 | 62
2018-09-21 19:00 | 64 | 61
2018-09-21 19:30 | 64 | 62
2018-09-21 20:00 | 64 | 62
2018-09-21 20:30 | 61 | 59
2018-09-21 21:00 | 61 | 60
2018-09-21 21:30 | 60 | 59
2018-09-21 22:00 | 59 | 57
2018-09-21 22:30 | 57 | 55
2018-09-21 23:00 | 54 | 53
2018-09-21 23:30 | 56 | 54
2018-09-22 | 53 | 52
2018-09-22 00:30 | 52 | 50
2018-09-22 01:00 | 52 | 50
2018-09-22 01:30 | 50 | 49
2018-09-22 02:00 | 50 | 48
2018-09-22 02:30 | 50 | 48
2018-09-22 03:00 | 50 | 49
2018-09-22 03:30 | 50 | 49
2018-09-22 04:00 | 51 | 49
2018-09-22 04:30 | 51 | 50
2018-09-22 05:00 | 50 | 48
2018-09-22 05:30 | 51 | 49
2018-09-22 06:00 | 50 | 49
2018-09-22 06:30 | 47 | 47
2018-09-22 07:00 | 40 | 40
2018-09-22 07:30 | 29 | 28
2018-09-22 08:00 | 19 | 17
2018-09-22 08:30 | 18 | 9
2018-09-22 09:00 | 16 | 6
2018-09-22 09:30 | 15 | 6
2018-09-22 10:00 | 15 | 1
2018-09-22 10:30 | 14 | 3
2018-09-22 11:00 | 17 | 9
2018-09-22 11:30 | 24 | 21
2018-09-22 12:00 | 16 | 11
2018-09-22 12:30 | 18 | 13
2018-09-22 13:00 | 19 | 15
2018-09-22 13:30 | 15 | 8
2018-09-22 14:00 | 14 | 7
2018-09-22 14:30 | 14 | 6
2018-09-22 15:00 | 17 | 12
2018-09-22 15:30 | 17 | 12
2018-09-22 16:00 | 16 | 9
2018-09-22 16:30 | 20 | 16
2018-09-22 17:00 | 33 | 31
2018-09-22 17:30 | 44 | 43
2018-09-22 18:00 | 55 | 54
2018-09-22 18:30 | 61 | 58
2018-09-22 19:00 | 59 | 56
2018-09-22 19:30 | 60 | 57
2018-09-22 20:00 | 59 | 56
2018-09-22 20:30 | 57 | 54
2018-09-22 21:00 | 56 | 53
2018-09-22 21:30 | 56 | 53
2018-09-22 22:00 | 54 | 51
2018-09-22 22:30 | 53 | 51
2018-09-22 23:00 | 53 | 51
2018-09-22 23:30 | 51 | 49
2018-09-23 | 44 | 43
2018-09-23 00:30 | 51 | 49
2018-09-23 01:00 | 51 | 49
2018-09-23 01:30 | 50 | 48
2018-09-23 02:00 | 50 | 48
2018-09-23 02:30 | 50 | 49
2018-09-23 03:00 | 49 | 47
2018-09-23 03:30 | 49 | 47
2018-09-23 04:00 | 49 | 48
2018-09-23 04:30 | 50 | 48
2018-09-23 05:00 | 50 | 48
2018-09-23 05:30 | 51 | 49
2018-09-23 06:00 | 51 | 49
2018-09-23 06:30 | 48 | 46
2018-09-23 07:00 | 41 | 39
2018-09-23 07:30 | 31 | 27
2018-09-23 08:00 | 22 | 16
2018-09-23 08:30 | 17 | 6
2018-09-23 09:00 | 15 | 5
2018-09-23 09:30 | 16 | 5
2018-09-23 10:00 | 20 | 9
2018-09-23 10:30 | 19 | 8
2018-09-23 11:00 | 17 | 4
2018-09-23 11:30 | 15 | 3
2018-09-23 12:00 | 17 | 7
2018-09-23 12:30 | 16 | 4
2018-09-23 13:00 | 18 | 8
2018-09-23 13:30 | 15 | 0
2018-09-23 14:00 | 16 | 2
2018-09-23 14:30 | 15 | 1
2018-09-23 15:00 | 16 | 2
2018-09-23 15:30 | 15 | 2
2018-09-23 16:00 | 16 | 3
2018-09-23 16:30 | 19 | 11
2018-09-23 17:00 | 27 | 22
2018-09-23 17:30 | 40 | 37
2018-09-23 18:00 | 50 | 49
2018-09-23 18:30 | 53 | 50
2018-09-23 19:00 | 54 | 51
2018-09-23 19:30 | 53 | 51
2018-09-23 20:00 | 52 | 51
2018-09-23 20:30 | 49 | 48
2018-09-23 21:00 | 49 | 48
2018-09-23 21:30 | 49 | 47
2018-09-23 22:00 | 48 | 46
2018-09-23 22:30 | 47 | 46
2018-09-23 23:00 | 46 | 45
2018-09-23 23:30 | 45 | 43
2018-09-24 | 45 | 44
2018-09-24 00:30 | 46 | 44
2018-09-24 01:00 | 45 | 44
2018-09-24 01:30 | 46 | 45
2018-09-24 02:00 | 46 | 45
2018-09-24 02:30 | 46 | 45
2018-09-24 03:00 | 49 | 48
2018-09-24 03:30 | 48 | 47
2018-09-24 04:00 | 47 | 46
2018-09-24 04:30 | 47 | 46
2018-09-24 05:00 | 48 | 47
2018-09-24 05:30 | 49 | 48
2018-09-24 06:00 | 51 | 50
2018-09-24 06:30 | 50 | 49
2018-09-24 07:00 | 43 | 42
2018-09-24 07:30 | 30 | 28
2018-09-24 08:00 | 19 | 16
2018-09-24 08:30 | 13 | 9
2018-09-24 09:00 | 12 | 2
2018-09-24 09:30 | 19 | 7
2018-09-24 10:00 | 20 | 10
2018-09-24 10:30 | 18 | 9
2018-09-24 11:00 | 18 | 9
2018-09-24 11:30 | 18 | 10
2018-09-24 12:00 | 19 | 11
2018-09-24 12:30 | 20 | 12
2018-09-24 13:00 | 22 | 19
2018-09-24 13:30 | 18 | 13
2018-09-24 14:00 | 16 | 9
2018-09-24 14:30 | 15 | 6
2018-09-24 15:00 | 15 | 2
2018-09-24 15:30 | 16 | 5
2018-09-24 16:00 | 20 | 13
2018-09-24 16:30 | 26 | 21
2018-09-24 17:00 | 40 | 38
2018-09-24 17:30 | 49 | 47
2018-09-24 18:00 | 59 | 58
2018-09-24 18:30 | 62 | 61
2018-09-24 19:00 | 64 | 62
2018-09-24 19:30 | 63 | 61
2018-09-24 20:00 | 64 | 62
2018-09-24 20:30 | 64 | 60
2018-09-24 21:00 | 63 | 59
2018-09-24 21:30 | 62 | 58
2018-09-24 22:00 | 62 | 57
2018-09-24 22:30 | 62 | 56
2018-09-24 23:00 | 62 | 56
2018-09-24 23:30 | 59 | 54
2018-09-25 | 59 | 54
2018-09-25 00:30 | 60 | 55
2018-09-25 01:00 | 62 | 57
2018-09-25 01:30 | 61 | 56
2018-09-25 02:00 | 61 | 56
2018-09-25 02:30 | 63 | 57
2018-09-25 03:00 | 62 | 57
2018-09-25 03:30 | 62 | 56
2018-09-25 04:00 | 62 | 57
2018-09-25 04:30 | 62 | 56
2018-09-25 05:00 | 62 | 56
2018-09-25 05:30 | 63 | 57
2018-09-25 06:00 | 63 | 58
2018-09-25 06:30 | 61 | 56
2018-09-25 07:00 | 58 | 54
2018-09-25 07:30 | 50 | 44
2018-09-25 08:00 | 43 | 34
2018-09-25 08:30 | 37 | 24
2018-09-25 09:00 | 17 | 17
2018-09-25 09:30 | 23 | 23
2018-09-25 10:00 | 22 | 21
2018-09-25 10:30 | 17 | 17
2018-09-25 11:00 | 25 | 25
2018-09-25 11:30 | 28 | 28
2018-09-25 12:00 | 20 | 20
2018-09-25 12:30 | 16 | 16
2018-09-25 13:00 | 14 | 14
2018-09-25 13:30 | 14 | 13
2018-09-25 14:00 | 7 | 7
2018-09-25 14:30 | 15 | 15
2018-09-25 15:00 | 7 | 7
2018-09-25 15:30 | 13 | 13
2018-09-25 16:00 | 23 | 23
2018-09-25 16:30 | 31 | 31
2018-09-25 17:00 | 37 | 35
2018-09-25 17:30 | 43 | 41
2018-09-25 18:00 | 49 | 48
2018-09-25 18:30 | 51 | 51
2018-09-25 19:00 | 50 | 49
2018-09-25 19:30 | 52 | 52
2018-09-25 20:00 | 53 | 52
2018-09-25 20:30 | 51 | 50
2018-09-25 21:00 | 50 | 50
2018-09-25 21:30 | 50 | 50
2018-09-25 22:00 | 50 | 49
2018-09-25 22:30 | 48 | 47
2018-09-25 23:00 | 48 | 47
2018-09-25 23:30 | 48 | 47
2018-09-26 | 48 | 46
2018-09-26 00:30 | 49 | 47
2018-09-26 01:00 | 48 | 46
2018-09-26 01:30 | 47 | 45
2018-09-26 02:00 | 49 | 47
2018-09-26 02:30 | 48 | 46
2018-09-26 03:00 | 47 | 46
2018-09-26 03:30 | 47 | 45
2018-09-26 04:00 | 48 | 46
2018-09-26 04:30 | 47 | 46
2018-09-26 05:00 | 48 | 47
2018-09-26 05:30 | 49 | 48
2018-09-26 06:00 | 48 | 47
2018-09-26 06:30 | 47 | 45
2018-09-26 07:00 | 45 | 43
2018-09-26 07:30 | 33 | 29
2018-09-26 08:00 | 25 | 21
2018-09-26 08:30 | 22 | 10
2018-09-26 09:00 | 21 | 0
2018-09-26 09:30 | 21 | 2
2018-09-26 10:00 | 21 | 5
2018-09-26 10:30 | 22 | 10
2018-09-26 11:00 | 21 | 8
2018-09-26 11:30 | 21 | 1
2018-09-26 12:00 | 21 | 4
2018-09-26 12:30 | 23 | 7
2018-09-26 13:00 | 22 | 4
2018-09-26 13:30 | 22 | 0
2018-09-26 14:00 | 20 | 2
2018-09-26 14:30 | 20 | 0
2018-09-26 15:00 | 22 | 4
2018-09-26 15:30 | 20 | 8
2018-09-26 16:00 | 25 | 19
2018-09-26 16:30 | 25 | 16
2018-09-26 17:00 | 35 | 31
2018-09-26 17:30 | 47 | 45
2018-09-26 18:00 | 58 | 56
2018-09-26 18:30 | 53 | 52
2018-09-26 19:00 | 60 | 58
2018-09-26 19:30 | 57 | 55
2018-09-26 20:00 | 60 | 58
2018-09-26 20:30 | 60 | 58
2018-09-26 21:00 | 59 | 57
2018-09-26 21:30 | 59 | 58
2018-09-26 22:00 | 58 | 56
2018-09-26 22:30 | 55 | 53
2018-09-26 23:00 | 51 | 49
2018-09-26 23:30 | 51 | 48
2018-09-27 | 50 | 47
2018-09-27 00:30 | 50 | 47
2018-09-27 01:00 | 50 | 47
2018-09-27 01:30 | 51 | 49
2018-09-27 02:00 | 50 | 48
2018-09-27 02:30 | 49 | 47
2018-09-27 03:00 | 49 | 46
2018-09-27 03:30 | 48 | 46
2018-09-27 04:00 | 49 | 47
2018-09-27 04:30 | 47 | 45
2018-09-27 05:00 | 46 | 44
2018-09-27 05:30 | 47 | 46
2018-09-27 06:00 | 48 | 46
2018-09-27 06:30 | 46 | 44
2018-09-27 07:00 | 37 | 36
2018-09-27 07:30 | 26 | 23
2018-09-27 08:00 | 20 | 14
2018-09-27 08:30 | 18 | 8
2018-09-27 09:00 | 21 | 14
2018-09-27 09:30 | 19 | 11
2018-09-27 10:00 | 26 | 21
2018-09-27 10:30 | 19 | 11
2018-09-27 11:00 | 17 | 6
2018-09-27 11:30 | 17 | 7
2018-09-27 12:00 | 16 | 6
2018-09-27 12:30 | 17 | 9
2018-09-27 13:00 | 16 | 3
2018-09-27 13:30 | 15 | 1
2018-09-27 14:00 | 15 | 4
2018-09-27 14:30 | 14 | 4
2018-09-27 15:00 | 15 | 2
2018-09-27 15:30 | 14 | 9
2018-09-27 16:00 | 22 | 19
2018-09-27 16:30 | 29 | 28
2018-09-27 17:00 | 43 | 42
2018-09-27 17:30 | 60 | 60
2018-09-27 18:00 | 70 | 70
2018-09-27 18:30 | 64 | 63
2018-09-27 19:00 | 48 | 48
2018-09-27 19:30 | 50 | 50
2018-09-27 20:00 | 57 | 57
2018-09-27 20:30 | 61 | 60
2018-09-27 21:00 | 59 | 58
2018-09-27 21:30 | 58 | 57
2018-09-27 22:00 | 57 | 56
2018-09-27 22:30 | 55 | 54
2018-09-27 23:00 | 50 | 49
2018-09-27 23:30 | 50 | 49
2018-09-28 | 50 | 49
2018-09-28 00:30 | 49 | 48
2018-09-28 01:00 | 49 | 48
2018-09-28 01:30 | 49 | 48
2018-09-28 02:00 | 48 | 48
2018-09-28 02:30 | 47 | 46
2018-09-28 03:00 | 48 | 48
2018-09-28 03:30 | 48 | 47
2018-09-28 04:00 | 47 | 46
2018-09-28 04:30 | 48 | 47
2018-09-28 05:00 | 48 | 47
2018-09-28 05:30 | 49 | 48
2018-09-28 06:00 | 49 | 48
2018-09-28 06:30 | 48 | 47
2018-09-28 07:00 | 39 | 38
2018-09-28 07:30 | 17 | 14
2018-09-28 08:00 | 11 | 6
2018-09-28 08:30 | 19 | 12
2018-09-28 09:00 | 18 | 10
2018-09-28 09:30 | 19 | 10
2018-09-28 10:00 | 17 | 9
2018-09-28 10:30 | 16 | 3
2018-09-28 11:00 | 16 | 6
2018-09-28 11:30 | 15 | 2
2018-09-28 12:00 | 15 | 3
2018-09-28 12:30 | 15 | 1
2018-09-28 13:00 | 15 | 2
2018-09-28 13:30 | 16 | 3
2018-09-28 14:00 | 16 | 0
2018-09-28 14:30 | 16 | 1
2018-09-28 15:00 | 18 | 12
2018-09-28 15:30 | 15 | 5
2018-09-28 16:00 | 19 | 10
2018-09-28 16:30 | 21 | 17
2018-09-28 17:00 | 30 | 27
2018-09-28 17:30 | 44 | 41
2018-09-28 18:00 | 44 | 42
2018-09-28 18:30 | 44 | 43
2018-09-28 19:00 | 45 | 44
2018-09-28 19:30 | 58 | 55
2018-09-28 20:00 | 41 | 40
2018-09-28 20:30 | 54 | 52
2018-09-28 21:00 | 54 | 52
2018-09-28 21:30 | 54 | 52
2018-09-28 22:00 | 54 | 51
2018-09-28 22:30 | 52 | 50
2018-09-28 23:00 | 52 | 50
2018-09-28 23:30 | 51 | 49
2018-09-29 | 52 | 50
2018-09-29 00:30 | 52 | 50
2018-09-29 01:00 | 50 | 48
2018-09-29 01:30 | 50 | 48
2018-09-29 02:00 | 50 | 48
2018-09-29 02:30 | 49 | 47
2018-09-29 03:00 | 49 | 48
2018-09-29 03:30 | 49 | 48
2018-09-29 04:00 | 48 | 47
2018-09-29 04:30 | 48 | 47
2018-09-29 05:00 | 49 | 48
2018-09-29 05:30 | 48 | 47
2018-09-29 06:00 | 48 | 47
2018-09-29 06:30 | 46 | 45
2018-09-29 07:00 | 38 | 36
2018-09-29 07:30 | 25 | 23
2018-09-29 08:00 | 17 | 14
2018-09-29 08:30 | 11 | 7
2018-09-29 09:00 | 12 | 7
2018-09-29 09:30 | 14 | 2
2018-09-29 10:00 | 14 | 2
2018-09-29 10:30 | 14 | 3
2018-09-29 11:00 | 17 | 6
2018-09-29 11:30 | 13 | 3
2018-09-29 12:00 | 11 | 4
2018-09-29 12:30 | 16 | 4
2018-09-29 13:00 | 18 | 3
2018-09-29 13:30 | 10 | 3
2018-09-29 14:00 | 11 | 3
2018-09-29 14:30 | 16 | 1
2018-09-29 15:00 | 18 | 0
2018-09-29 15:30 | 13 | 3
2018-09-29 16:00 | 14 | 10
2018-09-29 16:30 | 20 | 15
2018-09-29 17:00 | 28 | 25
2018-09-29 17:30 | 43 | 40
2018-09-29 18:00 | 51 | 49
2018-09-29 18:30 | 45 | 45
2018-09-29 19:00 | 52 | 51
2018-09-29 19:30 | 53 | 52
2018-09-29 20:00 | 53 | 52
2018-09-29 20:30 | 60 | 58
2018-09-29 21:00 | 61 | 60
2018-09-29 21:30 | 61 | 59
2018-09-29 22:00 | 60 | 58
2018-09-29 22:30 | 60 | 58
2018-09-29 23:00 | 59 | 58
2018-09-29 23:30 | 59 | 57
2018-09-30 | 57 | 56
2018-09-30 00:30 | 56 | 55
2018-09-30 01:00 | 59 | 58
2018-09-30 01:30 | 59 | 58
2018-09-30 02:00 | 58 | 57
2018-09-30 02:30 | 55 | 54
2018-09-30 03:00 | 52 | 51
2018-09-30 03:30 | 52 | 51
2018-09-30 04:00 | 49 | 48
2018-09-30 04:30 | 48 | 47
2018-09-30 05:00 | 49 | 48
2018-09-30 05:30 | 50 | 49
2018-09-30 06:00 | 49 | 48
2018-09-30 06:30 | 46 | 45
2018-09-30 07:00 | 37 | 36
2018-09-30 07:30 | 26 | 24
2018-09-30 08:00 | 16 | 13
2018-09-30 08:30 | 14 | 10
2018-09-30 09:00 | 12 | 9
2018-09-30 09:30 | 15 | 3
2018-09-30 10:00 | 14 | 1
2018-09-30 10:30 | 15 | 5
2018-09-30 11:00 | 18 | 5
2018-09-30 11:30 | 19 | 4
2018-09-30 12:00 | 12 | 2
2018-09-30 12:30 | 11 | 2
2018-09-30 13:00 | 11 | 3
2018-09-30 13:30 | 9 | 1
2018-09-30 14:00 | 11 | 0
2018-09-30 14:30 | 17 | 1
2018-09-30 15:00 | 12 | 1
2018-09-30 15:30 | 11 | 3
2018-09-30 16:00 | 13 | 8
2018-09-30 16:30 | 20 | 15
2018-09-30 17:00 | 30 | 27
2018-09-30 17:30 | 42 | 41
2018-09-30 18:00 | 43 | 43
2018-09-30 18:30 | 44 | 42
2018-09-30 19:00 | 45 | 43
2018-09-30 19:30 | 43 | 41
2018-09-30 20:00 | 45 | 43
2018-09-30 20:30 | 50 | 49
2018-09-30 21:00 | 49 | 48
2018-09-30 21:30 | 48 | 47
2018-09-30 22:00 | 49 | 48
2018-09-30 22:30 | 48 | 47
2018-09-30 23:00 | 48 | 47
2018-09-30 23:30 | 48 | 47
2018-10-01 | 46 | 46
2018-10-01 00:30 | 47 | 46
2018-10-01 01:00 | 47 | 46
2018-10-01 01:30 | 50 | 49
2018-10-01 02:00 | 49 | 48
2018-10-01 02:30 | 52 | 51
2018-10-01 03:00 | 51 | 50
2018-10-01 03:30 | 51 | 50
2018-10-01 04:00 | 51 | 50
2018-10-01 04:30 | 51 | 50
2018-10-01 05:00 | 52 | 52
2018-10-01 05:30 | 51 | 51
2018-10-01 06:00 | 50 | 50
2018-10-01 06:30 | 49 | 49
2018-10-01 07:00 | 47 | 46
2018-10-01 07:30 | 34 | 33
2018-10-01 08:00 | 30 | 29
2018-10-01 08:30 | 22 | 21
2018-10-01 09:00 | 28 | 27
2018-10-01 09:30 | 23 | 22
2018-10-01 10:00 | 16 | 14
2018-10-01 10:30 | 24 | 23
2018-10-01 11:00 | 22 | 19
2018-10-01 11:30 | 16 | 9
2018-10-01 12:00 | 16 | 9
2018-10-01 12:30 | 15 | 6
2018-10-01 13:00 | 16 | 3
2018-10-01 13:30 | 14 | 1
2018-10-01 14:00 | 14 | 0
2018-10-01 14:30 | 15 | 1
2018-10-01 15:00 | 14 | 1
2018-10-01 15:30 | 15 | 6
2018-10-01 16:00 | 18 | 14
2018-10-01 16:30 | 23 | 17
2018-10-01 17:00 | 32 | 29
2018-10-01 17:30 | 46 | 43
2018-10-01 18:00 | 54 | 52
2018-10-01 18:30 | 40 | 39
2018-10-01 19:00 | 31 | 31
2018-10-01 19:30 | 42 | 41
2018-10-01 20:00 | 44 | 42
2018-10-01 20:30 | 48 | 47
2018-10-01 21:00 | 50 | 48
2018-10-01 21:30 | 51 | 49
2018-10-01 22:00 | 50 | 48
2018-10-01 22:30 | 50 | 48
2018-10-01 23:00 | 49 | 48
2018-10-01 23:30 | 51 | 49
2018-10-02 | 51 | 49
2018-10-02 00:30 | 50 | 48
2018-10-02 01:00 | 50 | 48
2018-10-02 01:30 | 50 | 48
2018-10-02 02:00 | 50 | 49
2018-10-02 02:30 | 50 | 48
2018-10-02 03:00 | 50 | 49
2018-10-02 03:30 | 50 | 48
2018-10-02 04:00 | 50 | 48
2018-10-02 04:30 | 49 | 48
2018-10-02 05:00 | 49 | 48
2018-10-02 05:30 | 48 | 47
2018-10-02 06:00 | 49 | 47
2018-10-02 06:30 | 47 | 46
2018-10-02 07:00 | 36 | 35
2018-10-02 07:30 | 26 | 23
2018-10-02 08:00 | 21 | 19
2018-10-02 08:30 | 15 | 13
2018-10-02 09:00 | 10 | 6
2018-10-02 09:30 | 17 | 15
2018-10-02 10:00 | 29 | 28
2018-10-02 10:30 | 19 | 18
2018-10-02 11:00 | 28 | 27
2018-10-02 11:30 | 18 | 17
2018-10-02 12:00 | 12 | 10
2018-10-02 12:30 | 10 | 4
2018-10-02 13:00 | 8 | 3
2018-10-02 13:30 | 9 | 3
2018-10-02 14:00 | 9 | 4
2018-10-02 14:30 | 14 | 11
2018-10-02 15:00 | 9 | 2
2018-10-02 15:30 | 7 | 5
2018-10-02 16:00 | 14 | 13
2018-10-02 16:30 | 33 | 33
2018-10-02 17:00 | 42 | 42
2018-10-02 17:30 | 52 | 52
2018-10-02 18:00 | 55 | 55
2018-10-02 18:30 | 63 | 62
2018-10-02 19:00 | 52 | 52
2018-10-02 19:30 | 46 | 46
2018-10-02 20:00 | 45 | 44
2018-10-02 20:30 | 44 | 44
2018-10-02 21:00 | 49 | 49
2018-10-02 21:30 | 53 | 52
2018-10-02 22:00 | 50 | 49
2018-10-02 22:30 | 49 | 48
2018-10-02 23:00 | 49 | 47
2018-10-02 23:30 | 50 | 49
2018-10-03 | 52 | 51
2018-10-03 00:30 | 53 | 52
2018-10-03 01:00 | 53 | 52
2018-10-03 01:30 | 51 | 51
2018-10-03 02:00 | 48 | 48
2018-10-03 02:30 | 46 | 46
2018-10-03 03:00 | 48 | 47
2018-10-03 03:30 | 50 | 49
2018-10-03 04:00 | 44 | 44
2018-10-03 04:30 | 48 | 47
2018-10-03 05:00 | 49 | 48
2018-10-03 05:30 | 50 | 49
2018-10-03 06:00 | 49 | 48
2018-10-03 06:30 | 44 | 43
2018-10-03 07:00 | 34 | 33
2018-10-03 07:30 | 23 | 20
2018-10-03 08:00 | 13 | 6
2018-10-03 08:30 | 15 | 1
2018-10-03 09:00 | 15 | 3
2018-10-03 09:30 | 16 | 3
2018-10-03 10:00 | 15 | 0
2018-10-03 10:30 | 15 | 1
2018-10-03 11:00 | 16 | 2
2018-10-03 11:30 | 16 | 4
2018-10-03 12:00 | 19 | 5
2018-10-03 12:30 | 18 | 7
2018-10-03 13:00 | 14 | 6
2018-10-03 13:30 | 12 | 4
2018-10-03 14:00 | 11 | 5
2018-10-03 14:30 | 15 | 8
2018-10-03 15:00 | 18 | 5
2018-10-03 15:30 | 15 | 5
2018-10-03 16:00 | 18 | 10
2018-10-03 16:30 | 30 | 27
2018-10-03 17:00 | 36 | 34
2018-10-03 17:30 | 32 | 31
2018-10-03 18:00 | 38 | 37
2018-10-03 18:30 | 41 | 41
2018-10-03 19:00 | 42 | 41
2018-10-03 19:30 | 41 | 41
2018-10-03 20:00 | 41 | 41
2018-10-03 20:30 | 40 | 40
2018-10-03 21:00 | 44 | 44
2018-10-03 21:30 | 54 | 52
2018-10-03 22:00 | 51 | 49
2018-10-03 22:30 | 46 | 45
2018-10-03 23:00 | 41 | 41
2018-10-03 23:30 | 41 | 41
2018-10-04 | 40 | 39
2018-10-04 00:30 | 41 | 40
2018-10-04 01:00 | 44 | 43
2018-10-04 01:30 | 45 | 44
2018-10-04 02:00 | 45 | 44
2018-10-04 02:30 | 45 | 44
2018-10-04 03:00 | 45 | 44
2018-10-04 03:30 | 45 | 44
2018-10-04 04:00 | 49 | 48
2018-10-04 04:30 | 51 | 50
2018-10-04 05:00 | 51 | 51
2018-10-04 05:30 | 51 | 50
2018-10-04 06:00 | 51 | 50
2018-10-04 06:30 | 47 | 46
2018-10-04 07:00 | 29 | 28
2018-10-04 07:30 | 22 | 20
2018-10-04 08:00 | 18 | 14
2018-10-04 08:30 | 16 | 6
2018-10-04 09:00 | 16 | 3
2018-10-04 09:30 | 16 | 1
2018-10-04 10:00 | 22 | 2
2018-10-04 10:30 | 22 | 3
2018-10-04 11:00 | 16 | 1
2018-10-04 11:30 | 11 | 2
2018-10-04 12:00 | 12 | 1
2018-10-04 12:30 | 10 | 1
2018-10-04 13:00 | 11 | 0
2018-10-04 13:30 | 14 | 1
2018-10-04 14:00 | 10 | 3
2018-10-04 14:30 | 11 | 2
2018-10-04 15:00 | 13 | 2
2018-10-04 15:30 | 25 | 20
2018-10-04 16:00 | 27 | 23
2018-10-04 16:30 | 25 | 20
2018-10-04 17:00 | 33 | 29
2018-10-04 17:30 | 32 | 30
2018-10-04 18:00 | 44 | 43
2018-10-04 18:30 | 47 | 47
2018-10-04 19:00 | 47 | 47
2018-10-04 19:30 | 45 | 45
2018-10-04 20:00 | 42 | 42
2018-10-04 20:30 | 41 | 41
2018-10-04 21:00 | 40 | 40
2018-10-04 21:30 | 47 | 46
2018-10-04 22:00 | 48 | 46
2018-10-04 22:30 | 45 | 44
2018-10-04 23:00 | 45 | 44
2018-10-04 23:30 | 42 | 41
2018-10-05 | 42 | 41
2018-10-05 00:30 | 53 | 52
2018-10-05 01:00 | 53 | 52
2018-10-05 01:30 | 56 | 55
2018-10-05 02:00 | 56 | 55
2018-10-05 02:30 | 56 | 55
2018-10-05 03:00 | 50 | 49
2018-10-05 03:30 | 51 | 50
2018-10-05 04:00 | 47 | 46
2018-10-05 04:30 | 46 | 45
2018-10-05 05:00 | 47 | 46
2018-10-05 05:30 | 47 | 46
2018-10-05 06:00 | 47 | 46
2018-10-05 06:30 | 41 | 40
2018-10-05 07:00 | 34 | 32
2018-10-05 07:30 | 24 | 21
2018-10-05 08:00 | 20 | 15
2018-10-05 08:30 | 17 | 11
2018-10-05 09:00 | 20 | 17
2018-10-05 09:30 | 23 | 21
2018-10-05 10:00 | 12 | 4
2018-10-05 10:30 | 12 | 2
2018-10-05 11:00 | 13 | 1
2018-10-05 11:30 | 14 | 8
2018-10-05 12:00 | 14 | 10
2018-10-05 12:30 | 33 | 33
2018-10-05 13:00 | 7 | 2
2018-10-05 13:30 | 7 | 2
2018-10-05 14:00 | 13 | 11
2018-10-05 14:30 | 8 | 4
2018-10-05 15:00 | 7 | 1
2018-10-05 15:30 | 7 | 3
2018-10-05 16:00 | 7 | 2
2018-10-05 16:30 | 17 | 16
2018-10-05 17:00 | 29 | 28
2018-10-05 17:30 | 25 | 25
2018-10-05 18:00 | 34 | 34
2018-10-05 18:30 | 34 | 34
2018-10-05 19:00 | 29 | 29
2018-10-05 19:30 | 36 | 36
2018-10-05 20:00 | 39 | 39
2018-10-05 20:30 | 39 | 39
2018-10-05 21:00 | 38 | 38
2018-10-05 21:30 | 51 | 50
2018-10-05 22:00 | 51 | 50
2018-10-05 22:30 | 37 | 37
2018-10-05 23:00 | 47 | 46
2018-10-05 23:30 | 42 | 42
2018-10-06 | 47 | 46
2018-10-06 00:30 | 49 | 48
2018-10-06 01:00 | 48 | 47
2018-10-06 01:30 | 49 | 48
2018-10-06 02:00 | 49 | 48
2018-10-06 02:30 | 48 | 47
2018-10-06 03:00 | 47 | 46
2018-10-06 03:30 | 46 | 45
2018-10-06 04:00 | 47 | 46
2018-10-06 04:30 | 48 | 47
2018-10-06 05:00 | 48 | 47
2018-10-06 05:30 | 49 | 48
2018-10-06 06:00 | 49 | 48
2018-10-06 06:30 | 43 | 42
2018-10-06 07:00 | 41 | 40
2018-10-06 07:30 | 34 | 33
2018-10-06 08:00 | 24 | 20
2018-10-06 08:30 | 18 | 13
2018-10-06 09:00 | 14 | 0
2018-10-06 09:30 | 15 | 4
2018-10-06 10:00 | 15 | 1
2018-10-06 10:30 | 15 | 0
2018-10-06 11:00 | 15 | 4
2018-10-06 11:30 | 15 | 3
2018-10-06 12:00 | 14 | 1
2018-10-06 12:30 | 14 | 2
2018-10-06 13:00 | 14 | 2
2018-10-06 13:30 | 14 | 2
2018-10-06 14:00 | 14 | 4
2018-10-06 14:30 | 15 | 5
2018-10-06 15:00 | 16 | 3
2018-10-06 15:30 | 15 | 2
2018-10-06 16:00 | 16 | 7
2018-10-06 16:30 | 21 | 17
2018-10-06 17:00 | 28 | 25
2018-10-06 17:30 | 28 | 26
2018-10-06 18:00 | 37 | 36
2018-10-06 18:30 | 39 | 39
2018-10-06 19:00 | 40 | 40
2018-10-06 19:30 | 39 | 39
2018-10-06 20:00 | 39 | 38
2018-10-06 20:30 | 39 | 38
2018-10-06 21:00 | 41 | 40
2018-10-06 21:30 | 53 | 50
2018-10-06 22:00 | 53 | 50
2018-10-06 22:30 | 39 | 38
2018-10-06 23:00 | 47 | 46
2018-10-06 23:30 | 52 | 49
2018-10-07 | 53 | 51
2018-10-07 00:30 | 53 | 51
2018-10-07 01:00 | 53 | 50
2018-10-07 01:30 | 53 | 51
2018-10-07 02:00 | 51 | 49
2018-10-07 02:30 | 51 | 48
2018-10-07 03:00 | 51 | 48
2018-10-07 03:30 | 52 | 50
2018-10-07 04:00 | 50 | 48
2018-10-07 04:30 | 50 | 48
2018-10-07 05:00 | 50 | 48
2018-10-07 05:30 | 50 | 48
2018-10-07 06:00 | 50 | 48
2018-10-07 06:30 | 44 | 43
2018-10-07 07:00 | 37 | 36
2018-10-07 07:30 | 25 | 23
2018-10-07 08:00 | 25 | 23
2018-10-07 08:30 | 19 | 17
2018-10-07 09:00 | 13 | 10
2018-10-07 09:30 | 11 | 2
2018-10-07 10:00 | 11 | 3
2018-10-07 10:30 | 10 | 5
2018-10-07 11:00 | 12 | 3
2018-10-07 11:30 | 13 | 6
2018-10-07 12:00 | 12 | 6
2018-10-07 12:30 | 11 | 4
2018-10-07 13:00 | 11 | 4
2018-10-07 13:30 | 12 | 3
2018-10-07 14:00 | 11 | 3
2018-10-07 14:30 | 11 | 1
2018-10-07 15:00 | 11 | 0
2018-10-07 15:30 | 11 | 2
2018-10-07 16:00 | 14 | 8
2018-10-07 16:30 | 20 | 17
2018-10-07 17:00 | 29 | 27
2018-10-07 17:30 | 27 | 26
2018-10-07 18:00 | 37 | 36
2018-10-07 18:30 | 41 | 40
2018-10-07 19:00 | 42 | 42
2018-10-07 19:30 | 40 | 40
2018-10-07 20:00 | 38 | 38
2018-10-07 20:30 | 38 | 37
2018-10-07 21:00 | 39 | 39
2018-10-07 21:30 | 53 | 50
2018-10-07 22:00 | 52 | 49
2018-10-07 22:30 | 51 | 48
2018-10-07 23:00 | 50 | 47
2018-10-07 23:30 | 49 | 47
2018-10-08 | 49 | 47
2018-10-08 00:30 | 53 | 50
2018-10-08 01:00 | 52 | 49
2018-10-08 01:30 | 52 | 49
2018-10-08 02:00 | 50 | 48
2018-10-08 02:30 | 50 | 47
2018-10-08 03:00 | 50 | 48
2018-10-08 03:30 | 51 | 49
2018-10-08 04:00 | 51 | 48
2018-10-08 04:30 | 51 | 49
2018-10-08 05:00 | 51 | 48
2018-10-08 05:30 | 50 | 48
2018-10-08 06:00 | 51 | 48
2018-10-08 06:30 | 46 | 43
2018-10-08 07:00 | 38 | 35
2018-10-08 07:30 | 31 | 27
2018-10-08 08:00 | 24 | 19
2018-10-08 08:30 | 22 | 14
2018-10-08 09:00 | 24 | 12
2018-10-08 09:30 | 24 | 9
2018-10-08 10:00 | 23 | 4
2018-10-08 10:30 | 23 | 3
2018-10-08 11:00 | 21 | 2
2018-10-08 11:30 | 21 | 3
2018-10-08 12:00 | 21 | 5
2018-10-08 12:30 | 18 | 4
2018-10-08 13:00 | 11 | 2
2018-10-08 13:30 | 22 | 5
2018-10-08 14:00 | 21 | 4
2018-10-08 14:30 | 22 | 5
2018-10-08 15:00 | 24 | 5
2018-10-08 15:30 | 25 | 11
2018-10-08 16:00 | 27 | 16
2018-10-08 16:30 | 32 | 25
2018-10-08 17:00 | 30 | 25
2018-10-08 17:30 | 30 | 26
2018-10-08 18:00 | 36 | 34
2018-10-08 18:30 | 37 | 37
2018-10-08 19:00 | 38 | 38
2018-10-08 19:30 | 38 | 38
2018-10-08 20:00 | 38 | 38
2018-10-08 20:30 | 35 | 35
2018-10-08 21:00 | 34 | 34
2018-10-08 21:30 | 47 | 47
2018-10-08 22:00 | 47 | 46
2018-10-08 22:30 | 45 | 44
2018-10-08 23:00 | 47 | 46
2018-10-08 23:30 | 45 | 44
2018-10-09 | 46 | 45
2018-10-09 00:30 | 47 | 46
2018-10-09 01:00 | 46 | 44
2018-10-09 01:30 | 50 | 48
2018-10-09 02:00 | 51 | 50
2018-10-09 02:30 | 53 | 52
2018-10-09 03:00 | 52 | 50
2018-10-09 03:30 | 54 | 52
2018-10-09 04:00 | 54 | 52
2018-10-09 04:30 | 52 | 51
2018-10-09 05:00 | 52 | 51
2018-10-09 05:30 | 53 | 52
2018-10-09 06:00 | 53 | 51
2018-10-09 06:30 | 45 | 43
2018-10-09 07:00 | 37 | 36
2018-10-09 07:30 | 27 | 24
2018-10-09 08:00 | 21 | 17
2018-10-09 08:30 | 13 | 13
2018-10-09 09:00 | 5 | 2
2018-10-09 09:30 | 11 | 9
2018-10-09 10:00 | 18 | 17
2018-10-09 10:30 | 18 | 17
2018-10-09 11:00 | 12 | 10
2018-10-09 11:30 | 12 | 10
2018-10-09 12:00 | 11 | 9
2018-10-09 12:30 | 8 | 7
2018-10-09 13:00 | 8 | 8
2018-10-09 13:30 | 9 | 9
2018-10-09 14:00 | 6 | 6
2018-10-09 14:30 | 5 | 4
2018-10-09 15:00 | 4 | 3
2018-10-09 15:30 | 1 | 1
2018-10-09 16:00 | 7 | 7
2018-10-09 16:30 | 26 | 26
2018-10-09 17:00 | 26 | 26
2018-10-09 17:30 | 35 | 35
2018-10-09 18:00 | 50 | 50
2018-10-09 18:30 | 43 | 39
2018-10-09 19:00 | 41 | 35
2018-10-09 19:30 | 40 | 34
2018-10-09 20:00 | 39 | 33
2018-10-09 20:30 | 38 | 32
2018-10-09 21:00 | 39 | 34
2018-10-09 21:30 | 47 | 46
2018-10-09 22:00 | 46 | 45
2018-10-09 22:30 | 45 | 43
2018-10-09 23:00 | 43 | 43
2018-10-09 23:30 | 44 | 43
2018-10-10 | 46 | 45
2018-10-10 00:30 | 47 | 46
2018-10-10 01:00 | 46 | 44
2018-10-10 01:30 | 48 | 46
2018-10-10 02:00 | 48 | 46
2018-10-10 02:30 | 48 | 46
2018-10-10 03:00 | 47 | 45
2018-10-10 03:30 | 46 | 44
2018-10-10 04:00 | 47 | 45
2018-10-10 04:30 | 49 | 48
2018-10-10 05:00 | 51 | 50
2018-10-10 05:30 | 55 | 53
2018-10-10 06:00 | 55 | 53
2018-10-10 06:30 | 48 | 47
2018-10-10 07:00 | 39 | 38
2018-10-10 07:30 | 30 | 28
2018-10-10 08:00 | 24 | 22
2018-10-10 08:30 | 17 | 15
2018-10-10 09:00 | 14 | 12
2018-10-10 09:30 | 11 | 7
2018-10-10 10:00 | 10 | 7
2018-10-10 10:30 | 13 | 12
2018-10-10 11:00 | 16 | 15
2018-10-10 11:30 | 13 | 10
2018-10-10 12:00 | 12 | 8
2018-10-10 12:30 | 12 | 8
2018-10-10 13:00 | 13 | 8
2018-10-10 13:30 | 12 | 7
2018-10-10 14:00 | 13 | 8
2018-10-10 14:30 | 14 | 11
2018-10-10 15:00 | 15 | 12
2018-10-10 15:30 | 18 | 16
2018-10-10 16:00 | 23 | 22
2018-10-10 16:30 | 31 | 30
2018-10-10 17:00 | 40 | 39
2018-10-10 17:30 | 51 | 50
2018-10-10 18:00 | 43 | 43
2018-10-10 18:30 | 47 | 47
2018-10-10 19:00 | 48 | 48
2018-10-10 19:30 | 47 | 47
2018-10-10 20:00 | 48 | 48
2018-10-10 20:30 | 46 | 46
2018-10-10 21:00 | 43 | 43
2018-10-10 21:30 | 52 | 51
2018-10-10 22:00 | 49 | 48
2018-10-10 22:30 | 50 | 50
2018-10-10 23:00 | 49 | 49
2018-10-10 23:30 | 50 | 49
2018-10-11 | 48 | 48
2018-10-11 00:30 | 49 | 48
2018-10-11 01:00 | 51 | 50
2018-10-11 01:30 | 53 | 52
2018-10-11 02:00 | 52 | 51
2018-10-11 02:30 | 52 | 51
2018-10-11 03:00 | 52 | 51
2018-10-11 03:30 | 52 | 50
2018-10-11 04:00 | 54 | 53
2018-10-11 04:30 | 56 | 55
2018-10-11 05:00 | 55 | 54
2018-10-11 05:30 | 56 | 55
2018-10-11 06:00 | 57 | 55
2018-10-11 06:30 | 41 | 40
2018-10-11 07:00 | 29 | 28
2018-10-11 07:30 | 39 | 37
2018-10-11 08:00 | 40 | 36
2018-10-11 08:30 | 33 | 30
2018-10-11 09:00 | 21 | 15
2018-10-11 09:30 | 16 | 3
2018-10-11 10:00 | 16 | 0
2018-10-11 10:30 | 14 | 0
2018-10-11 11:00 | 16 | 0
2018-10-11 11:30 | 16 | 0
2018-10-11 12:00 | 16 | 0
2018-10-11 12:30 | 16 | 1
2018-10-11 13:00 | 16 | 2
2018-10-11 13:30 | 16 | 1
2018-10-11 14:00 | 17 | 1
2018-10-11 14:30 | 16 | 3
2018-10-11 15:00 | 16 | 5
2018-10-11 15:30 | 16 | 1
2018-10-11 16:00 | 22 | 17
2018-10-11 16:30 | 24 | 19
2018-10-11 17:00 | 23 | 20
2018-10-11 17:30 | 32 | 30
2018-10-11 18:00 | 38 | 37
2018-10-11 18:30 | 43 | 43
2018-10-11 19:00 | 44 | 41
2018-10-11 19:30 | 45 | 42
2018-10-11 20:00 | 45 | 42
2018-10-11 20:30 | 44 | 41
2018-10-11 21:00 | 44 | 40
2018-10-11 21:30 | 53 | 52
2018-10-11 22:00 | 53 | 53
2018-10-11 22:30 | 55 | 54
2018-10-11 23:00 | 53 | 52
2018-10-11 23:30 | 51 | 50
2018-10-12 | 50 | 49
2018-10-12 00:30 | 50 | 49
2018-10-12 01:00 | 49 | 48
2018-10-12 01:30 | 53 | 52
2018-10-12 02:00 | 51 | 50
2018-10-12 02:30 | 50 | 49
2018-10-12 03:00 | 50 | 48
2018-10-12 03:30 | 50 | 49
2018-10-12 04:00 | 50 | 49
2018-10-12 04:30 | 50 | 49
2018-10-12 05:00 | 50 | 49
2018-10-12 05:30 | 51 | 49
2018-10-12 06:00 | 49 | 48
2018-10-12 06:30 | 43 | 42
2018-10-12 07:00 | 34 | 34
2018-10-12 07:30 | 26 | 25
2018-10-12 08:00 | 25 | 24
2018-10-12 08:30 | 20 | 19
2018-10-12 09:00 | 17 | 16
2018-10-12 09:30 | 13 | 10
2018-10-12 10:00 | 10 | 6
2018-10-12 10:30 | 13 | 12
2018-10-12 11:00 | 24 | 23
2018-10-12 11:30 | 17 | 15
2018-10-12 12:00 | 11 | 9
2018-10-12 12:30 | 9 | 5
2018-10-12 13:00 | 9 | 5
2018-10-12 13:30 | 9 | 5
2018-10-12 14:00 | 8 | 4
2018-10-12 14:30 | 8 | 2
2018-10-12 15:00 | 8 | 1
2018-10-12 15:30 | 11 | 8
2018-10-12 16:00 | 19 | 17
2018-10-12 16:30 | 28 | 27
2018-10-12 17:00 | 27 | 27
2018-10-12 17:30 | 35 | 35
2018-10-12 18:00 | 38 | 38
2018-10-12 18:30 | 40 | 40
2018-10-12 19:00 | 40 | 40
2018-10-12 19:30 | 39 | 39
2018-10-12 20:00 | 39 | 39
2018-10-12 20:30 | 39 | 39
2018-10-12 21:00 | 39 | 39
2018-10-12 21:30 | 38 | 38
2018-10-12 22:00 | 49 | 49
2018-10-12 22:30 | 40 | 40
2018-10-12 23:00 | 41 | 41
2018-10-12 23:30 | 45 | 45
2018-10-13 | 52 | 52
2018-10-13 00:30 | 58 | 58
2018-10-13 01:00 | 59 | 59
2018-10-13 01:30 | 58 | 58
2018-10-13 02:00 | 58 | 58
2018-10-13 02:30 | 58 | 58
2018-10-13 03:00 | 58 | 58
2018-10-13 03:30 | 55 | 55
2018-10-13 04:00 | 55 | 55
2018-10-13 04:30 | 55 | 55
2018-10-13 05:00 | 57 | 57
2018-10-13 05:30 | 59 | 59
2018-10-13 06:00 | 60 | 59
2018-10-13 06:30 | 57 | 57
2018-10-13 07:00 | 54 | 54
2018-10-13 07:30 | 51 | 50
2018-10-13 08:00 | 42 | 42
2018-10-13 08:30 | 24 | 24
2018-10-13 09:00 | 27 | 27
2018-10-13 09:30 | 29 | 29
2018-10-13 10:00 | 40 | 39
2018-10-13 10:30 | 31 | 31
2018-10-13 11:00 | 25 | 25
2018-10-13 11:30 | 27 | 27
2018-10-13 12:00 | 31 | 31
2018-10-13 12:30 | 36 | 36
2018-10-13 13:00 | 22 | 21
2018-10-13 13:30 | 29 | 28
2018-10-13 14:00 | 31 | 31
2018-10-13 14:30 | 24 | 23
2018-10-13 15:00 | 35 | 35
2018-10-13 15:30 | 46 | 46
2018-10-13 16:00 | 51 | 51
2018-10-13 16:30 | 53 | 53
2018-10-13 17:00 | 54 | 54
2018-10-13 17:30 | 37 | 37
2018-10-13 18:00 | 43 | 43
2018-10-13 18:30 | 45 | 45
2018-10-13 19:00 | 45 | 45
2018-10-13 19:30 | 40 | 40
2018-10-13 20:00 | 39 | 39
2018-10-13 20:30 | 51 | 50
2018-10-13 21:00 | 48 | 47
2018-10-13 21:30 | 51 | 51
2018-10-13 22:00 | 51 | 51
2018-10-13 22:30 | 50 | 50
2018-10-13 23:00 | 50 | 50
2018-10-13 23:30 | 50 | 50
2018-10-14 | 50 | 49
2018-10-14 00:30 | 50 | 49
2018-10-14 01:00 | 50 | 49
2018-10-14 01:30 | 50 | 49
2018-10-14 02:00 | 50 | 49
2018-10-14 02:30 | 49 | 49
2018-10-14 03:00 | 50 | 50
2018-10-14 03:30 | 49 | 48
2018-10-14 04:00 | 48 | 47
2018-10-14 04:30 | 47 | 47
2018-10-14 05:00 | 48 | 48
2018-10-14 05:30 | 46 | 46
2018-10-14 06:00 | 45 | 44
2018-10-14 06:30 | 45 | 44
2018-10-14 07:00 | 41 | 40
2018-10-14 07:30 | 36 | 35
2018-10-14 08:00 | 34 | 33
2018-10-14 08:30 | 22 | 20
2018-10-14 09:00 | 17 | 14
2018-10-14 09:30 | 9 | 4
2018-10-14 10:00 | 10 | 7
2018-10-14 10:30 | 7 | 4
2018-10-14 11:00 | 8 | 1
2018-10-14 11:30 | 8 | 1
2018-10-14 12:00 | 9 | 2
2018-10-14 12:30 | 10 | 3
2018-10-14 13:00 | 8 | 1
2018-10-14 13:30 | 9 | 2
2018-10-14 14:00 | 8 | 0
2018-10-14 14:30 | 7 | 1
2018-10-14 15:00 | 7 | 2
2018-10-14 15:30 | 10 | 8
2018-10-14 16:00 | 16 | 15
2018-10-14 16:30 | 19 | 18
2018-10-14 17:00 | 21 | 21
2018-10-14 17:30 | 29 | 29
2018-10-14 18:00 | 36 | 36
2018-10-14 18:30 | 38 | 38
2018-10-14 19:00 | 37 | 37
2018-10-14 19:30 | 43 | 43
2018-10-14 20:00 | 44 | 44
2018-10-14 20:30 | 44 | 44
2018-10-14 21:00 | 43 | 43
2018-10-14 21:30 | 52 | 52
2018-10-14 22:00 | 52 | 52
2018-10-14 22:30 | 51 | 51
2018-10-14 23:00 | 50 | 50
2018-10-14 23:30 | 50 | 50
2018-10-15 | 48 | 48
2018-10-15 00:30 | 52 | 51
2018-10-15 01:00 | 52 | 52
2018-10-15 01:30 | 53 | 53
2018-10-15 02:00 | 52 | 52
2018-10-15 02:30 | 52 | 52
2018-10-15 03:00 | 52 | 52
2018-10-15 03:30 | 50 | 50
2018-10-15 04:00 | 51 | 51
2018-10-15 04:30 | 51 | 50
2018-10-15 05:00 | 52 | 52
2018-10-15 05:30 | 51 | 51
2018-10-15 06:00 | 52 | 51
2018-10-15 06:30 | 48 | 48
2018-10-15 07:00 | 36 | 36
2018-10-15 07:30 | 39 | 39
2018-10-15 08:00 | 31 | 31
2018-10-15 08:30 | 28 | 28
2018-10-15 09:00 | 22 | 22
2018-10-15 09:30 | 19 | 19
2018-10-15 10:00 | 19 | 19
2018-10-15 10:30 | 18 | 17
2018-10-15 11:00 | 9 | 8
2018-10-15 11:30 | 7 | 6
2018-10-15 12:00 | 5 | 3
2018-10-15 12:30 | 6 | 5
2018-10-15 13:00 | 3 | 1
2018-10-15 13:30 | 6 | 5
2018-10-15 14:00 | 8 | 7
2018-10-15 14:30 | 7 | 6
2018-10-15 15:00 | 8 | 8
2018-10-15 15:30 | 12 | 11
2018-10-15 16:00 | 18 | 18
2018-10-15 16:30 | 24 | 24
2018-10-15 17:00 | 22 | 22
2018-10-15 17:30 | 33 | 33
2018-10-15 18:00 | 38 | 38
2018-10-15 18:30 | 41 | 41
2018-10-15 19:00 | 42 | 42
2018-10-15 19:30 | 44 | 44
2018-10-15 20:00 | 45 | 45
2018-10-15 20:30 | 45 | 45
2018-10-15 21:00 | 51 | 50
2018-10-15 21:30 | 52 | 52
2018-10-15 22:00 | 51 | 50
2018-10-15 22:30 | 50 | 50
2018-10-15 23:00 | 49 | 49
2018-10-15 23:30 | 51 | 50
2018-10-16 | 51 | 50
2018-10-16 00:30 | 51 | 50
2018-10-16 01:00 | 50 | 49
2018-10-16 01:30 | 49 | 48
2018-10-16 02:00 | 50 | 49
2018-10-16 02:30 | 49 | 48
2018-10-16 03:00 | 49 | 48
2018-10-16 03:30 | 49 | 48
2018-10-16 04:00 | 49 | 48
2018-10-16 04:30 | 49 | 48
2018-10-16 05:00 | 50 | 49
2018-10-16 05:30 | 50 | 49
2018-10-16 06:00 | 48 | 47
2018-10-16 06:30 | 42 | 42
2018-10-16 07:00 | 37 | 36
2018-10-16 07:30 | 28 | 28
2018-10-16 08:00 | 31 | 31
2018-10-16 08:30 | 23 | 23
2018-10-16 09:00 | 10 | 10
2018-10-16 09:30 | 16 | 9
2018-10-16 10:00 | 14 | 2
2018-10-16 10:30 | 14 | 5
2018-10-16 11:00 | 15 | 4
2018-10-16 11:30 | 17 | 5
2018-10-16 12:00 | 19 | 9
2018-10-16 12:30 | 18 | 7
2018-10-16 13:00 | 19 | 7
2018-10-16 13:30 | 20 | 7
2018-10-16 14:00 | 21 | 9
2018-10-16 14:30 | 21 | 10
2018-10-16 15:00 | 28 | 23
2018-10-16 15:30 | 50 | 48
2018-10-16 16:00 | 38 | 37
2018-10-16 16:30 | 48 | 47
2018-10-16 17:00 | 49 | 48
2018-10-16 17:30 | 46 | 44
2018-10-16 18:00 | 45 | 44
2018-10-16 18:30 | 47 | 44
2018-10-16 19:00 | 49 | 47
2018-10-16 19:30 | 51 | 49
2018-10-16 20:00 | 51 | 49
2018-10-16 20:30 | 50 | 48
2018-10-16 21:00 | 46 | 42
2018-10-16 21:30 | 52 | 51
2018-10-16 22:00 | 53 | 52
2018-10-16 22:30 | 52 | 52
2018-10-16 23:00 | 51 | 50
2018-10-16 23:30 | 51 | 50
2018-10-17 | 52 | 51
2018-10-17 00:30 | 51 | 50
2018-10-17 01:00 | 55 | 54
2018-10-17 01:30 | 55 | 54
2018-10-17 02:00 | 54 | 53
2018-10-17 02:30 | 53 | 52
2018-10-17 03:00 | 54 | 53
2018-10-17 03:30 | 53 | 52
2018-10-17 04:00 | 52 | 51
2018-10-17 04:30 | 53 | 52
2018-10-17 05:00 | 53 | 52
2018-10-17 05:30 | 53 | 53
2018-10-17 06:00 | 53 | 52
2018-10-17 06:30 | 42 | 39
2018-10-17 07:00 | 34 | 30
2018-10-17 07:30 | 39 | 36
2018-10-17 08:00 | 36 | 35
2018-10-17 08:30 | 14 | 13
2018-10-17 09:00 | 5 | 2
2018-10-17 09:30 | 7 | 5
2018-10-17 10:00 | 12 | 10
2018-10-17 10:30 | 6 | 1
2018-10-17 11:00 | 7 | 3
2018-10-17 11:30 | 8 | 5
2018-10-17 12:00 | 6 | 1
2018-10-17 12:30 | 7 | 5
2018-10-17 13:00 | 10 | 8
2018-10-17 13:30 | 9 | 8
2018-10-17 14:00 | 10 | 9
2018-10-17 14:30 | 9 | 9
2018-10-17 15:00 | 7 | 6
2018-10-17 15:30 | 11 | 11
2018-10-17 16:00 | 10 | 9
2018-10-17 16:30 | 26 | 25
2018-10-17 17:00 | 34 | 33
2018-10-17 17:30 | 46 | 45
2018-10-17 18:00 | 56 | 55
2018-10-17 18:30 | 58 | 57
2018-10-17 19:00 | 49 | 46
2018-10-17 19:30 | 57 | 56
2018-10-17 20:00 | 58 | 57
2018-10-17 20:30 | 57 | 56
2018-10-17 21:00 | 60 | 60
2018-10-17 21:30 | 55 | 54
2018-10-17 22:00 | 57 | 57
2018-10-17 22:30 | 53 | 52
2018-10-17 23:00 | 51 | 49
2018-10-17 23:30 | 56 | 55
2018-10-18 | 57 | 55
2018-10-18 00:30 | 56 | 54
2018-10-18 01:00 | 55 | 54
2018-10-18 01:30 | 55 | 53
2018-10-18 02:00 | 54 | 53
2018-10-18 02:30 | 55 | 54
2018-10-18 03:00 | 54 | 52
2018-10-18 03:30 | 54 | 52
2018-10-18 04:00 | 54 | 53
2018-10-18 04:30 | 54 | 52
2018-10-18 05:00 | 53 | 51
2018-10-18 05:30 | 38 | 38
2018-10-18 06:00 | 25 | 24
2018-10-18 06:30 | 17 | 14
2018-10-18 07:00 | 14 | 12
2018-10-18 07:30 | 10 | 1
2018-10-18 08:00 | 11 | 8
2018-10-18 08:30 | 10 | 8
2018-10-18 09:00 | 11 | 5
2018-10-18 09:30 | 10 | 3
2018-10-18 10:00 | 24 | 23
2018-10-18 10:30 | 17 | 15
2018-10-18 11:00 | 22 | 21
2018-10-18 11:30 | 27 | 27
2018-10-18 12:00 | 12 | 11
2018-10-18 12:30 | 14 | 13
2018-10-18 13:00 | 19 | 18
2018-10-18 13:30 | 25 | 25
2018-10-18 14:00 | 31 | 31
2018-10-18 14:30 | 19 | 18
2018-10-18 15:00 | 18 | 17
2018-10-18 15:30 | 14 | 13
2018-10-18 16:00 | 5 | 2
2018-10-18 16:30 | 9 | 7
2018-10-18 17:00 | 18 | 16
2018-10-18 17:30 | 23 | 21
2018-10-18 18:00 | 28 | 27
2018-10-18 18:30 | 33 | 30
2018-10-18 19:00 | 33 | 30
2018-10-18 19:30 | 34 | 32
2018-10-18 20:00 | 36 | 35
2018-10-18 20:30 | 46 | 45
2018-10-18 21:00 | 60 | 60
2018-10-18 21:30 | 59 | 59
2018-10-18 22:00 | 61 | 60
2018-10-18 22:30 | 57 | 57
2018-10-18 23:00 | 54 | 54
2018-10-18 23:30 | 48 | 48
2018-10-19 | 55 | 53
2018-10-19 00:30 | 57 | 56
2018-10-19 01:00 | 55 | 54
2018-10-19 01:30 | 53 | 52
2018-10-19 02:00 | 53 | 51
2018-10-19 02:30 | 52 | 50
2018-10-19 03:00 | 51 | 50
2018-10-19 03:30 | 52 | 50
2018-10-19 04:00 | 53 | 52
2018-10-19 04:30 | 53 | 52
2018-10-19 05:00 | 54 | 52
2018-10-19 05:30 | 55 | 54
2018-10-19 06:00 | 53 | 52
2018-10-19 06:30 | 46 | 45
2018-10-19 07:00 | 38 | 37
2018-10-19 07:30 | 25 | 19
2018-10-19 08:00 | 27 | 21
2018-10-19 08:30 | 23 | 16
2018-10-19 09:00 | 20 | 13
2018-10-19 09:30 | 16 | 3
2018-10-19 10:00 | 15 | 2
2018-10-19 10:30 | 19 | 14
2018-10-19 11:00 | 19 | 12
2018-10-19 11:30 | 19 | 14
2018-10-19 12:00 | 18 | 12
2018-10-19 12:30 | 17 | 9
2018-10-19 13:00 | 17 | 10
2018-10-19 13:30 | 17 | 8
2018-10-19 14:00 | 19 | 10
2018-10-19 14:30 | 16 | 3
2018-10-19 15:00 | 15 | 1
2018-10-19 15:30 | 18 | 10
2018-10-19 16:00 | 17 | 5
2018-10-19 16:30 | 24 | 18
2018-10-19 17:00 | 32 | 28
2018-10-19 17:30 | 32 | 29
2018-10-19 18:00 | 27 | 26
2018-10-19 18:30 | 37 | 37
2018-10-19 19:00 | 40 | 40
2018-10-19 19:30 | 40 | 39
2018-10-19 20:00 | 41 | 41
2018-10-19 20:30 | 42 | 42
2018-10-19 21:00 | 41 | 41
2018-10-19 21:30 | 54 | 53
2018-10-19 22:00 | 47 | 47
2018-10-19 22:30 | 45 | 45
2018-10-19 23:00 | 46 | 46
2018-10-19 23:30 | 56 | 55
2018-10-20 | 56 | 55
2018-10-20 00:30 | 67 | 65
2018-10-20 01:00 | 66 | 65
2018-10-20 01:30 | 65 | 64
2018-10-20 02:00 | 65 | 64
2018-10-20 02:30 | 66 | 64
2018-10-20 03:00 | 65 | 63
2018-10-20 03:30 | 63 | 62
2018-10-20 04:00 | 65 | 64
2018-10-20 04:30 | 64 | 62
2018-10-20 05:00 | 64 | 63
2018-10-20 05:30 | 65 | 64
2018-10-20 06:00 | 65 | 63
2018-10-20 06:30 | 56 | 55
2018-10-20 07:00 | 45 | 43
2018-10-20 07:30 | 34 | 32
2018-10-20 08:00 | 26 | 23
2018-10-20 08:30 | 19 | 14
2018-10-20 09:00 | 17 | 10
2018-10-20 09:30 | 22 | 20
2018-10-20 10:00 | 21 | 20
2018-10-20 10:30 | 14 | 12
2018-10-20 11:00 | 16 | 14
2018-10-20 11:30 | 13 | 11
2018-10-20 12:00 | 14 | 12
2018-10-20 12:30 | 15 | 14
2018-10-20 13:00 | 13 | 11
2018-10-20 13:30 | 14 | 13
2018-10-20 14:00 | 20 | 19
2018-10-20 14:30 | 18 | 17
2018-10-20 15:00 | 16 | 15
2018-10-20 15:30 | 17 | 15
2018-10-20 16:00 | 23 | 22
2018-10-20 16:30 | 26 | 25
2018-10-20 17:00 | 24 | 24
2018-10-20 17:30 | 34 | 34
2018-10-20 18:00 | 44 | 44
2018-10-20 18:30 | 47 | 47
2018-10-20 19:00 | 51 | 51
2018-10-20 19:30 | 62 | 61
2018-10-20 20:00 | 62 | 60
2018-10-20 20:30 | 62 | 60
2018-10-20 21:00 | 62 | 60
2018-10-20 21:30 | 66 | 65
2018-10-20 22:00 | 69 | 68
2018-10-20 22:30 | 64 | 62
2018-10-20 23:00 | 61 | 59
2018-10-20 23:30 | 64 | 62
2018-10-21 | 63 | 62
2018-10-21 00:30 | 63 | 62
2018-10-21 01:00 | 64 | 64
2018-10-21 01:30 | 62 | 62
2018-10-21 02:00 | 71 | 70
2018-10-21 02:30 | 72 | 71
2018-10-21 03:00 | 71 | 70
2018-10-21 03:30 | 68 | 67
2018-10-21 04:00 | 64 | 63
2018-10-21 04:30 | 62 | 61
2018-10-21 05:00 | 61 | 60
2018-10-21 05:30 | 59 | 58
2018-10-21 06:00 | 57 | 56
2018-10-21 06:30 | 52 | 51
2018-10-21 07:00 | 42 | 40
2018-10-21 07:30 | 30 | 28
2018-10-21 08:00 | 24 | 21
2018-10-21 08:30 | 26 | 22
2018-10-21 09:00 | 20 | 18
2018-10-21 09:30 | 21 | 21
2018-10-21 10:00 | 16 | 15
2018-10-21 10:30 | 18 | 17
2018-10-21 11:00 | 12 | 12
2018-10-21 11:30 | 9 | 8
2018-10-21 12:00 | 8 | 7
2018-10-21 12:30 | 7 | 6
2018-10-21 13:00 | 7 | 5
2018-10-21 13:30 | 8 | 6
2018-10-21 14:00 | 7 | 1
2018-10-21 14:30 | 8 | 0
2018-10-21 15:00 | 7 | 3
2018-10-21 15:30 | 10 | 6
2018-10-21 16:00 | 14 | 13
2018-10-21 16:30 | 20 | 19
2018-10-21 17:00 | 30 | 29
2018-10-21 17:30 | 41 | 41
2018-10-21 18:00 | 36 | 36
2018-10-21 18:30 | 52 | 52
2018-10-21 19:00 | 55 | 55
2018-10-21 19:30 | 56 | 55
2018-10-21 20:00 | 53 | 52
2018-10-21 20:30 | 54 | 54
2018-10-21 21:00 | 59 | 58
2018-10-21 21:30 | 58 | 57
2018-10-21 22:00 | 58 | 57
2018-10-21 22:30 | 55 | 55
2018-10-21 23:00 | 52 | 51
2018-10-21 23:30 | 50 | 49
2018-10-22 | 52 | 51
2018-10-22 00:30 | 53 | 52
2018-10-22 01:00 | 53 | 51
2018-10-22 01:30 | 51 | 49
2018-10-22 02:00 | 52 | 51
2018-10-22 02:30 | 54 | 53
2018-10-22 03:00 | 55 | 55
2018-10-22 03:30 | 56 | 55
2018-10-22 04:00 | 55 | 55
2018-10-22 04:30 | 56 | 55
2018-10-22 05:00 | 56 | 55
2018-10-22 05:30 | 53 | 52
2018-10-22 06:00 | 55 | 54
2018-10-22 06:30 | 55 | 53
2018-10-22 07:00 | 54 | 53
2018-10-22 07:30 | 47 | 46
2018-10-22 08:00 | 32 | 30
2018-10-22 08:30 | 27 | 21
2018-10-22 09:00 | 26 | 21
2018-10-22 09:30 | 19 | 8
2018-10-22 10:00 | 18 | 6
2018-10-22 10:30 | 18 | 7
2018-10-22 11:00 | 19 | 9
2018-10-22 11:30 | 20 | 9
2018-10-22 12:00 | 20 | 7
2018-10-22 12:30 | 20 | 9
2018-10-22 13:00 | 22 | 8
2018-10-22 13:30 | 21 | 9
2018-10-22 14:00 | 21 | 9
2018-10-22 14:30 | 21 | 10
2018-10-22 15:00 | 19 | 11
2018-10-22 15:30 | 20 | 15
2018-10-22 16:00 | 24 | 19
2018-10-22 16:30 | 31 | 27
2018-10-22 17:00 | 39 | 36
2018-10-22 17:30 | 46 | 45
2018-10-22 18:00 | 54 | 53
2018-10-22 18:30 | 47 | 47
2018-10-22 19:00 | 33 | 33
2018-10-22 19:30 | 47 | 47
2018-10-22 20:00 | 63 | 62
2018-10-22 20:30 | 62 | 61
2018-10-22 21:00 | 64 | 63
2018-10-22 21:30 | 63 | 62
2018-10-22 22:00 | 61 | 60
2018-10-22 22:30 | 61 | 60
2018-10-22 23:00 | 61 | 60
2018-10-22 23:30 | 60 | 59
2018-10-23 | 58 | 56
2018-10-23 00:30 | 56 | 54
2018-10-23 01:00 | 56 | 54
2018-10-23 01:30 | 55 | 53
2018-10-23 02:00 | 55 | 53
2018-10-23 02:30 | 55 | 53
2018-10-23 03:00 | 53 | 52
2018-10-23 03:30 | 53 | 51
2018-10-23 04:00 | 52 | 51
2018-10-23 04:30 | 54 | 52
2018-10-23 05:00 | 53 | 52
2018-10-23 05:30 | 52 | 50
2018-10-23 06:00 | 52 | 50
2018-10-23 06:30 | 47 | 45
2018-10-23 07:00 | 44 | 42
2018-10-23 07:30 | 39 | 37
2018-10-23 08:00 | 43 | 42
2018-10-23 08:30 | 28 | 22
2018-10-23 09:00 | 23 | 10
2018-10-23 09:30 | 23 | 10
2018-10-23 10:00 | 15 | 13
2018-10-23 10:30 | 8 | 8
2018-10-23 11:00 | 10 | 8
2018-10-23 11:30 | 16 | 7
2018-10-23 12:00 | 9 | 8
2018-10-23 12:30 | 11 | 11
2018-10-23 13:00 | 12 | 11
2018-10-23 13:30 | 11 | 11
2018-10-23 14:00 | 11 | 9
2018-10-23 14:30 | 11 | 10
2018-10-23 15:00 | 14 | 14
2018-10-23 15:30 | 14 | 14
2018-10-23 16:00 | 16 | 16
2018-10-23 16:30 | 28 | 25
2018-10-23 17:00 | 33 | 29
2018-10-23 17:30 | 43 | 39
2018-10-23 18:00 | 46 | 44
2018-10-23 18:30 | 45 | 44
2018-10-23 19:00 | 36 | 30
2018-10-23 19:30 | 48 | 47
2018-10-23 20:00 | 55 | 55
2018-10-23 20:30 | 56 | 56
2018-10-23 21:00 | 56 | 56
2018-10-23 21:30 | 53 | 53
2018-10-23 22:00 | 52 | 51
2018-10-23 22:30 | 51 | 51
2018-10-23 23:00 | 50 | 50
2018-10-23 23:30 | 51 | 51
2018-10-24 | 49 | 49
2018-10-24 00:30 | 48 | 48
2018-10-24 01:00 | 49 | 48
2018-10-24 01:30 | 50 | 50
2018-10-24 02:00 | 49 | 49
2018-10-24 02:30 | 49 | 48
2018-10-24 03:00 | 48 | 48
2018-10-24 03:30 | 48 | 48
2018-10-24 04:00 | 48 | 48
2018-10-24 04:30 | 48 | 48
2018-10-24 05:00 | 49 | 49
2018-10-24 05:30 | 47 | 47
2018-10-24 06:00 | 47 | 47
2018-10-24 06:30 | 45 | 45
2018-10-24 07:00 | 32 | 31
2018-10-24 07:30 | 24 | 23
2018-10-24 08:00 | 21 | 20
2018-10-24 08:30 | 20 | 18
2018-10-24 09:00 | 14 | 13
2018-10-24 09:30 | 12 | 11
2018-10-24 10:00 | 11 | 10
2018-10-24 10:30 | 7 | 5
2018-10-24 11:00 | 8 | 6
2018-10-24 11:30 | 9 | 7
2018-10-24 12:00 | 10 | 8
2018-10-24 12:30 | 9 | 8
2018-10-24 13:00 | 10 | 9
2018-10-24 13:30 | 9 | 8
2018-10-24 14:00 | 10 | 9
2018-10-24 14:30 | 10 | 9
2018-10-24 15:00 | 13 | 13
2018-10-24 15:30 | 17 | 16
2018-10-24 16:00 | 19 | 19
2018-10-24 16:30 | 21 | 21
2018-10-24 17:00 | 32 | 32
2018-10-24 17:30 | 29 | 29
2018-10-24 18:00 | 33 | 33
2018-10-24 18:30 | 34 | 34
2018-10-24 19:00 | 39 | 38
2018-10-24 19:30 | 36 | 36
2018-10-24 20:00 | 37 | 37
2018-10-24 20:30 | 39 | 38
2018-10-24 21:00 | 37 | 37
2018-10-24 21:30 | 45 | 45
2018-10-24 22:00 | 50 | 50
2018-10-24 22:30 | 49 | 49
2018-10-24 23:00 | 49 | 49
2018-10-24 23:30 | 52 | 52
2018-10-25 | 48 | 48
2018-10-25 00:30 | 51 | 51
2018-10-25 01:00 | 52 | 52
2018-10-25 01:30 | 52 | 52
2018-10-25 02:00 | 51 | 51
2018-10-25 02:30 | 49 | 49
2018-10-25 03:00 | 50 | 50
2018-10-25 03:30 | 48 | 48
2018-10-25 04:00 | 48 | 48
2018-10-25 04:30 | 48 | 48
2018-10-25 05:00 | 47 | 47
2018-10-25 05:30 | 44 | 44
2018-10-25 06:00 | 32 | 30
2018-10-25 06:30 | 25 | 23
2018-10-25 07:00 | 23 | 21
2018-10-25 07:30 | 9 | 5
2018-10-25 08:00 | 9 | 5
2018-10-25 08:30 | 12 | 10
2018-10-25 09:00 | 10 | 8
2018-10-25 09:30 | 10 | 8
2018-10-25 10:00 | 9 | 8
2018-10-25 10:30 | 10 | 8
2018-10-25 11:00 | 12 | 10
2018-10-25 11:30 | 11 | 9
2018-10-25 12:00 | 15 | 14
2018-10-25 12:30 | 14 | 13
2018-10-25 13:00 | 16 | 15
2018-10-25 13:30 | 18 | 17
2018-10-25 14:00 | 15 | 15
2018-10-25 14:30 | 15 | 14
2018-10-25 15:00 | 16 | 15
2018-10-25 15:30 | 17 | 16
2018-10-25 16:00 | 13 | 11
2018-10-25 16:30 | 24 | 24
2018-10-25 17:00 | 19 | 18
2018-10-25 17:30 | 28 | 27
2018-10-25 18:00 | 36 | 35
2018-10-25 18:30 | 34 | 32
2018-10-25 19:00 | 32 | 29
2018-10-25 19:30 | 35 | 33
2018-10-25 20:00 | 38 | 37
2018-10-25 20:30 | 38 | 37
2018-10-25 21:00 | 48 | 48
2018-10-25 21:30 | 49 | 49
2018-10-25 22:00 | 49 | 49
2018-10-25 22:30 | 51 | 49
2018-10-25 23:00 | 50 | 48
2018-10-25 23:30 | 51 | 49
2018-10-26 | 51 | 49
2018-10-26 00:30 | 49 | 47
2018-10-26 01:00 | 50 | 48
2018-10-26 01:30 | 50 | 48
2018-10-26 02:00 | 48 | 47
2018-10-26 02:30 | 48 | 47
2018-10-26 03:00 | 50 | 49
2018-10-26 03:30 | 51 | 50
2018-10-26 04:00 | 53 | 52
2018-10-26 04:30 | 53 | 52
2018-10-26 05:00 | 53 | 52
2018-10-26 05:30 | 54 | 52
2018-10-26 06:00 | 51 | 50
2018-10-26 06:30 | 44 | 42
2018-10-26 07:00 | 34 | 31
2018-10-26 07:30 | 26 | 24
2018-10-26 08:00 | 20 | 17
2018-10-26 08:30 | 16 | 13
2018-10-26 09:00 | 16 | 12
2018-10-26 09:30 | 16 | 11
2018-10-26 10:00 | 17 | 11
2018-10-26 10:30 | 18 | 13
2018-10-26 11:00 | 18 | 13
2018-10-26 11:30 | 19 | 14
2018-10-26 12:00 | 20 | 16
2018-10-26 12:30 | 19 | 16
2018-10-26 13:00 | 20 | 16
2018-10-26 13:30 | 21 | 17
2018-10-26 14:00 | 20 | 16
2018-10-26 14:30 | 19 | 14
2018-10-26 15:00 | 20 | 16
2018-10-26 15:30 | 24 | 21
2018-10-26 16:00 | 27 | 24
2018-10-26 16:30 | 34 | 32
2018-10-26 17:00 | 41 | 40
2018-10-26 17:30 | 36 | 35
2018-10-26 18:00 | 44 | 43
2018-10-26 18:30 | 47 | 46
2018-10-26 19:00 | 49 | 49
2018-10-26 19:30 | 47 | 47
2018-10-26 20:00 | 45 | 45
2018-10-26 20:30 | 45 | 45
2018-10-26 21:00 | 44 | 44
2018-10-26 21:30 | 52 | 51
2018-10-26 22:00 | 57 | 56
2018-10-26 22:30 | 55 | 54
2018-10-26 23:00 | 55 | 54
2018-10-26 23:30 | 55 | 54
2018-10-27 | 55 | 54
2018-10-27 00:30 | 56 | 55
2018-10-27 01:00 | 54 | 53
2018-10-27 01:30 | 51 | 50
2018-10-27 02:00 | 51 | 50
2018-10-27 02:30 | 50 | 49
2018-10-27 03:00 | 51 | 50
2018-10-27 03:30 | 51 | 50
2018-10-27 04:00 | 51 | 50
2018-10-27 04:30 | 50 | 49
2018-10-27 05:00 | 51 | 50
2018-10-27 05:30 | 51 | 50
2018-10-27 06:00 | 48 | 47
2018-10-27 06:30 | 43 | 42
2018-10-27 07:00 | 33 | 33
2018-10-27 07:30 | 23 | 22
2018-10-27 08:00 | 17 | 16
2018-10-27 08:30 | 13 | 10
2018-10-27 09:00 | 10 | 6
2018-10-27 09:30 | 9 | 2
2018-10-27 10:00 | 8 | 1
2018-10-27 10:30 | 8 | 2
2018-10-27 11:00 | 9 | 2
2018-10-27 11:30 | 9 | 3
2018-10-27 12:00 | 8 | 4
2018-10-27 12:30 | 9 | 5
2018-10-27 13:00 | 9 | 5
2018-10-27 13:30 | 9 | 3
2018-10-27 14:00 | 9 | 5
2018-10-27 14:30 | 9 | 5
2018-10-27 15:00 | 11 | 7
2018-10-27 15:30 | 17 | 12
2018-10-27 16:00 | 20 | 18
2018-10-27 16:30 | 18 | 17
2018-10-27 17:00 | 15 | 15
2018-10-27 17:30 | 28 | 28
2018-10-27 18:00 | 36 | 36
2018-10-27 18:30 | 41 | 38
2018-10-27 19:00 | 42 | 39
2018-10-27 19:30 | 43 | 40
2018-10-27 20:00 | 43 | 40
2018-10-27 20:30 | 42 | 39
2018-10-27 21:00 | 42 | 39
2018-10-27 21:30 | 51 | 50
2018-10-27 22:00 | 53 | 52
2018-10-27 22:30 | 53 | 52
2018-10-27 23:00 | 53 | 52
2018-10-27 23:30 | 51 | 50
2018-10-28 | 50 | 49
2018-10-28 00:30 | 49 | 48
2018-10-28 01:00 | 48 | 48
2018-10-28 01:30 | 49 | 48
2018-10-28 02:00 | 51 | 50
2018-10-28 02:30 | 51 | 50
2018-10-28 03:00 | 51 | 50
2018-10-28 03:30 | 50 | 49
2018-10-28 04:00 | 51 | 50
2018-10-28 04:30 | 51 | 50
2018-10-28 05:00 | 50 | 49
2018-10-28 05:30 | 49 | 48
2018-10-28 06:00 | 48 | 47
2018-10-28 06:30 | 40 | 40
2018-10-28 07:00 | 30 | 29
2018-10-28 07:30 | 22 | 21
2018-10-28 08:00 | 15 | 13
2018-10-28 08:30 | 10 | 7
2018-10-28 09:00 | 9 | 6
2018-10-28 09:30 | 8 | 3
2018-10-28 10:00 | 8 | 3
2018-10-28 10:30 | 9 | 6
2018-10-28 11:00 | 10 | 8
2018-10-28 11:30 | 11 | 9
2018-10-28 12:00 | 12 | 9
2018-10-28 12:30 | 12 | 10
2018-10-28 13:00 | 14 | 12
2018-10-28 13:30 | 11 | 9
2018-10-28 14:00 | 10 | 7
2018-10-28 14:30 | 11 | 8
2018-10-28 15:00 | 13 | 11
2018-10-28 15:30 | 17 | 15
2018-10-28 16:00 | 21 | 20
2018-10-28 16:30 | 28 | 27
2018-10-28 17:00 | 36 | 35
2018-10-28 17:30 | 32 | 30
2018-10-28 18:00 | 47 | 46
2018-10-28 18:30 | 52 | 50
2018-10-28 19:00 | 54 | 52
2018-10-28 19:30 | 54 | 52
2018-10-28 20:00 | 53 | 52
2018-10-28 20:30 | 53 | 52
2018-10-28 21:00 | 56 | 55
2018-10-28 21:30 | 62 | 62
2018-10-28 22:00 | 57 | 57
2018-10-28 22:30 | 61 | 61
2018-10-28 23:00 | 63 | 62
2018-10-28 23:30 | 63 | 63
2018-10-29 | 62 | 62
2018-10-29 00:30 | 60 | 60
2018-10-29 01:00 | 61 | 60
2018-10-29 01:30 | 61 | 61
2018-10-29 02:00 | 61 | 61
2018-10-29 02:30 | 60 | 60
2018-10-29 03:00 | 61 | 61
2018-10-29 03:30 | 61 | 60
2018-10-29 04:00 | 59 | 59
2018-10-29 04:30 | 60 | 60
2018-10-29 05:00 | 60 | 60
2018-10-29 05:30 | 60 | 60
2018-10-29 06:00 | 59 | 59
2018-10-29 06:30 | 55 | 55
2018-10-29 07:00 | 46 | 46
2018-10-29 07:30 | 41 | 40
2018-10-29 08:00 | 37 | 36
2018-10-29 08:30 | 32 | 31
2018-10-29 09:00 | 21 | 20
2018-10-29 09:30 | 15 | 13
2018-10-29 10:00 | 12 | 10
2018-10-29 10:30 | 10 | 8
2018-10-29 11:00 | 11 | 8
2018-10-29 11:30 | 10 | 8
2018-10-29 12:00 | 10 | 8
2018-10-29 12:30 | 16 | 14
2018-10-29 13:00 | 20 | 18
2018-10-29 13:30 | 16 | 15
2018-10-29 14:00 | 17 | 16
2018-10-29 14:30 | 22 | 21
2018-10-29 15:00 | 21 | 20
2018-10-29 15:30 | 26 | 25
2018-10-29 16:00 | 27 | 26
2018-10-29 16:30 | 37 | 36
2018-10-29 17:00 | 46 | 46
2018-10-29 17:30 | 47 | 46
2018-10-29 18:00 | 53 | 52
2018-10-29 18:30 | 55 | 55
2018-10-29 19:00 | 57 | 57
2018-10-29 19:30 | 58 | 58
2018-10-29 20:00 | 56 | 55
2018-10-29 20:30 | 62 | 62
2018-10-29 21:00 | 63 | 63
2018-10-29 21:30 | 62 | 62
2018-10-29 22:00 | 62 | 62
2018-10-29 22:30 | 64 | 64
2018-10-29 23:00 | 64 | 64
2018-10-29 23:30 | 63 | 63
2018-10-30 | 61 | 61
2018-10-30 00:30 | 59 | 59
2018-10-30 01:00 | 58 | 58
2018-10-30 01:30 | 58 | 57
2018-10-30 02:00 | 55 | 54
2018-10-30 02:30 | 54 | 54
2018-10-30 03:00 | 53 | 53
2018-10-30 03:30 | 53 | 53
2018-10-30 04:00 | 53 | 52
2018-10-30 04:30 | 57 | 56
2018-10-30 05:00 | 59 | 58
2018-10-30 05:30 | 59 | 58
2018-10-30 06:00 | 55 | 55
2018-10-30 06:30 | 52 | 51
2018-10-30 07:00 | 33 | 32
2018-10-30 07:30 | 31 | 30
2018-10-30 08:00 | 25 | 24
2018-10-30 08:30 | 18 | 16
2018-10-30 09:00 | 20 | 19
2018-10-30 09:30 | 12 | 10
2018-10-30 10:00 | 15 | 12
2018-10-30 10:30 | 12 | 6
2018-10-30 11:00 | 10 | 4
2018-10-30 11:30 | 11 | 6
2018-10-30 12:00 | 13 | 10
2018-10-30 12:30 | 17 | 14
2018-10-30 13:00 | 14 | 11
2018-10-30 13:30 | 11 | 7
2018-10-30 14:00 | 11 | 7
2018-10-30 14:30 | 12 | 9
2018-10-30 15:00 | 15 | 12
2018-10-30 15:30 | 16 | 14
2018-10-30 16:00 | 26 | 24
2018-10-30 16:30 | 33 | 32
2018-10-30 17:00 | 35 | 34
2018-10-30 17:30 | 41 | 40
2018-10-30 18:00 | 42 | 41
2018-10-30 18:30 | 44 | 41
2018-10-30 19:00 | 39 | 33
2018-10-30 19:30 | 44 | 41
2018-10-30 20:00 | 49 | 47
2018-10-30 20:30 | 47 | 46
2018-10-30 21:00 | 50 | 48
2018-10-30 21:30 | 55 | 54
2018-10-30 22:00 | 56 | 55
2018-10-30 22:30 | 53 | 53
2018-10-30 23:00 | 52 | 51
2018-10-30 23:30 | 52 | 51
2018-10-31 | 54 | 53
2018-10-31 00:30 | 53 | 52
2018-10-31 01:00 | 53 | 52
2018-10-31 01:30 | 54 | 53
2018-10-31 02:00 | 53 | 52
2018-10-31 02:30 | 53 | 52
2018-10-31 03:00 | 52 | 51
2018-10-31 03:30 | 52 | 51
2018-10-31 04:00 | 52 | 51
2018-10-31 04:30 | 51 | 51
2018-10-31 05:00 | 51 | 50
2018-10-31 05:30 | 51 | 50
2018-10-31 06:00 | 49 | 48
2018-10-31 06:30 | 39 | 38
2018-10-31 07:00 | 37 | 36
2018-10-31 07:30 | 34 | 33
2018-10-31 08:00 | 29 | 28
2018-10-31 08:30 | 22 | 22
2018-10-31 09:00 | 10 | 7
2018-10-31 09:30 | 8 | 5
2018-10-31 10:00 | 10 | 9
2018-10-31 10:30 | 11 | 10
2018-10-31 11:00 | 11 | 10
2018-10-31 11:30 | 15 | 14
2018-10-31 12:00 | 11 | 9
2018-10-31 12:30 | 11 | 9
2018-10-31 13:00 | 16 | 14
2018-10-31 13:30 | 13 | 12
2018-10-31 14:00 | 14 | 12
2018-10-31 14:30 | 12 | 10
2018-10-31 15:00 | 17 | 16
2018-10-31 15:30 | 23 | 23
2018-10-31 16:00 | 33 | 33
2018-10-31 16:30 | 43 | 42
2018-10-31 17:00 | 40 | 39
2018-10-31 17:30 | 43 | 42
2018-10-31 18:00 | 52 | 51
2018-10-31 18:30 | 57 | 55
2018-10-31 19:00 | 58 | 56
2018-10-31 19:30 | 62 | 60
2018-10-31 20:00 | 67 | 67
2018-10-31 20:30 | 68 | 68
2018-10-31 21:00 | 65 | 65
2018-10-31 21:30 | 63 | 62
2018-10-31 22:00 | 57 | 56
2018-10-31 22:30 | 62 | 62
2018-10-31 23:00 | 59 | 59
2018-10-31 23:30 | 57 | 56
2018-11-01 | 54 | 53
2018-11-01 00:30 | 54 | 54
2018-11-01 01:00 | 55 | 54
2018-11-01 01:30 | 54 | 53
2018-11-01 02:00 | 53 | 52
2018-11-01 02:30 | 52 | 52
2018-11-01 03:00 | 53 | 52
2018-11-01 03:30 | 52 | 51
2018-11-01 04:00 | 52 | 52
2018-11-01 04:30 | 52 | 52
2018-11-01 05:00 | 52 | 52
2018-11-01 05:30 | 53 | 52
2018-11-01 06:00 | 52 | 52
2018-11-01 06:30 | 48 | 47
2018-11-01 07:00 | 39 | 39
2018-11-01 07:30 | 29 | 29
2018-11-01 08:00 | 23 | 23
2018-11-01 08:30 | 25 | 25
2018-11-01 09:00 | 30 | 29
2018-11-01 09:30 | 31 | 29
2018-11-01 10:00 | 32 | 31
2018-11-01 10:30 | 33 | 32
2018-11-01 11:00 | 27 | 25
2018-11-01 11:30 | 31 | 29
2018-11-01 12:00 | 25 | 22
2018-11-01 12:30 | 29 | 26
2018-11-01 13:00 | 33 | 32
2018-11-01 13:30 | 31 | 29
2018-11-01 14:00 | 22 | 20
2018-11-01 14:30 | 31 | 30
2018-11-01 15:00 | 20 | 18
2018-11-01 15:30 | 17 | 14
2018-11-01 16:00 | 31 | 29
2018-11-01 16:30 | 51 | 49
2018-11-01 17:00 | 51 | 49
2018-11-01 17:30 | 44 | 42
2018-11-01 18:00 | 46 | 45
2018-11-01 18:30 | 48 | 46
2018-11-01 19:00 | 47 | 43
2018-11-01 19:30 | 50 | 47
2018-11-01 20:00 | 58 | 57
2018-11-01 20:30 | 63 | 62
2018-11-01 21:00 | 63 | 62
2018-11-01 21:30 | 60 | 60
2018-11-01 22:00 | 56 | 56
2018-11-01 22:30 | 56 | 56
2018-11-01 23:00 | 54 | 54
2018-11-01 23:30 | 53 | 53
2018-11-02 | 54 | 54
2018-11-02 00:30 | 58 | 57
2018-11-02 01:00 | 58 | 57
2018-11-02 01:30 | 58 | 56
2018-11-02 02:00 | 57 | 56
2018-11-02 02:30 | 57 | 56
2018-11-02 03:00 | 57 | 56
2018-11-02 03:30 | 57 | 55
2018-11-02 04:00 | 54 | 53
2018-11-02 04:30 | 55 | 54
2018-11-02 05:00 | 58 | 57
2018-11-02 05:30 | 56 | 55
2018-11-02 06:00 | 57 | 56
2018-11-02 06:30 | 52 | 50
2018-11-02 07:00 | 47 | 45
2018-11-02 07:30 | 37 | 34
2018-11-02 08:00 | 27 | 24
2018-11-02 08:30 | 29 | 25
2018-11-02 09:00 | 24 | 21
2018-11-02 09:30 | 31 | 29
2018-11-02 10:00 | 29 | 28
2018-11-02 10:30 | 34 | 33
2018-11-02 11:00 | 30 | 28
2018-11-02 11:30 | 16 | 13
2018-11-02 12:00 | 19 | 16
2018-11-02 12:30 | 15 | 11
2018-11-02 13:00 | 17 | 13
2018-11-02 13:30 | 14 | 9
2018-11-02 14:00 | 16 | 11
2018-11-02 14:30 | 14 | 10
2018-11-02 15:00 | 13 | 8
2018-11-02 15:30 | 18 | 15
2018-11-02 16:00 | 22 | 19
2018-11-02 16:30 | 28 | 25
2018-11-02 17:00 | 41 | 39
2018-11-02 17:30 | 39 | 36
2018-11-02 18:00 | 47 | 45
2018-11-02 18:30 | 49 | 46
2018-11-02 19:00 | 53 | 49
2018-11-02 19:30 | 53 | 50
2018-11-02 20:00 | 55 | 53
2018-11-02 20:30 | 62 | 61
2018-11-02 21:00 | 61 | 61
2018-11-02 21:30 | 62 | 61
2018-11-02 22:00 | 58 | 57
2018-11-02 22:30 | 57 | 56
2018-11-02 23:00 | 57 | 56
2018-11-02 23:30 | 57 | 56
2018-11-03 | 58 | 57
2018-11-03 00:30 | 60 | 59
2018-11-03 01:00 | 60 | 59
2018-11-03 01:30 | 60 | 59
2018-11-03 02:00 | 59 | 58
2018-11-03 02:30 | 59 | 58
2018-11-03 03:00 | 60 | 59
2018-11-03 03:30 | 59 | 58
2018-11-03 04:00 | 57 | 56
2018-11-03 04:30 | 57 | 56
2018-11-03 05:00 | 55 | 54
2018-11-03 05:30 | 55 | 54
2018-11-03 06:00 | 54 | 53
2018-11-03 06:30 | 48 | 47
2018-11-03 07:00 | 38 | 37
2018-11-03 07:30 | 30 | 28
2018-11-03 08:00 | 25 | 23
2018-11-03 08:30 | 12 | 6
2018-11-03 09:00 | 11 | 4
2018-11-03 09:30 | 10 | 3
2018-11-03 10:00 | 24 | 23
2018-11-03 10:30 | 21 | 20
2018-11-03 11:00 | 19 | 17
2018-11-03 11:30 | 18 | 16
2018-11-03 12:00 | 14 | 11
2018-11-03 12:30 | 13 | 8
2018-11-03 13:00 | 12 | 8
2018-11-03 13:30 | 15 | 12
2018-11-03 14:00 | 21 | 19
2018-11-03 14:30 | 24 | 22
2018-11-03 15:00 | 16 | 13
2018-11-03 15:30 | 16 | 12
2018-11-03 16:00 | 12 | 8
2018-11-03 16:30 | 21 | 19
2018-11-03 17:00 | 37 | 35
2018-11-03 17:30 | 38 | 38
2018-11-03 18:00 | 42 | 41
2018-11-03 18:30 | 46 | 44
2018-11-03 19:00 | 48 | 44
2018-11-03 19:30 | 48 | 44
2018-11-03 20:00 | 48 | 44
2018-11-03 20:30 | 48 | 44
2018-11-03 21:00 | 48 | 43
2018-11-03 21:30 | 55 | 53
2018-11-03 22:00 | 58 | 57
2018-11-03 22:30 | 58 | 57
2018-11-03 23:00 | 55 | 54
2018-11-03 23:30 | 53 | 53
2018-11-04 | 53 | 52
2018-11-04 00:30 | 53 | 52
2018-11-04 01:00 | 52 | 51
2018-11-04 01:30 | 55 | 54
2018-11-04 02:00 | 56 | 55
2018-11-04 02:30 | 55 | 54
2018-11-04 03:00 | 54 | 53
2018-11-04 03:30 | 54 | 53
2018-11-04 04:00 | 54 | 53
2018-11-04 04:30 | 53 | 52
2018-11-04 05:00 | 53 | 51
2018-11-04 05:30 | 54 | 52
2018-11-04 06:00 | 52 | 51
2018-11-04 06:30 | 47 | 46
2018-11-04 07:00 | 40 | 39
2018-11-04 07:30 | 29 | 27
2018-11-04 08:00 | 24 | 21
2018-11-04 08:30 | 21 | 18
2018-11-04 09:00 | 22 | 18
2018-11-04 09:30 | 21 | 18
2018-11-04 10:00 | 18 | 15
2018-11-04 10:30 | 24 | 22
2018-11-04 11:00 | 15 | 11
2018-11-04 11:30 | 15 | 11
2018-11-04 12:00 | 13 | 9
2018-11-04 12:30 | 13 | 6
2018-11-04 13:00 | 12 | 6
2018-11-04 13:30 | 12 | 5
2018-11-04 14:00 | 14 | 4
2018-11-04 14:30 | 15 | 5
2018-11-04 15:00 | 17 | 11
2018-11-04 15:30 | 21 | 16
2018-11-04 16:00 | 21 | 16
2018-11-04 16:30 | 21 | 17
2018-11-04 17:00 | 34 | 31
2018-11-04 17:30 | 32 | 30
2018-11-04 18:00 | 41 | 40
2018-11-04 18:30 | 45 | 44
2018-11-04 19:00 | 49 | 48
2018-11-04 19:30 | 50 | 49
2018-11-04 20:00 | 48 | 48
2018-11-04 20:30 | 47 | 46
2018-11-04 21:00 | 46 | 45
2018-11-04 21:30 | 58 | 56
2018-11-04 22:00 | 62 | 60
2018-11-04 22:30 | 61 | 59
2018-11-04 23:00 | 58 | 56
2018-11-04 23:30 | 57 | 55
2018-11-05 | 55 | 54
2018-11-05 00:30 | 54 | 53
2018-11-05 01:00 | 53 | 52
2018-11-05 01:30 | 56 | 55
2018-11-05 02:00 | 56 | 55
2018-11-05 02:30 | 57 | 55
2018-11-05 03:00 | 56 | 55
2018-11-05 03:30 | 55 | 54
2018-11-05 04:00 | 56 | 55
2018-11-05 04:30 | 55 | 54
2018-11-05 05:00 | 56 | 54
2018-11-05 05:30 | 56 | 54
2018-11-05 06:00 | 54 | 54
2018-11-05 06:30 | 47 | 46
2018-11-05 07:00 | 37 | 36
2018-11-05 07:30 | 27 | 26
2018-11-05 08:00 | 24 | 22
2018-11-05 08:30 | 12 | 9
2018-11-05 09:00 | 12 | 9
2018-11-05 09:30 | 12 | 9
2018-11-05 10:00 | 13 | 9
2018-11-05 10:30 | 13 | 6
2018-11-05 11:00 | 14 | 7
2018-11-05 11:30 | 14 | 7
2018-11-05 12:00 | 14 | 6
2018-11-05 12:30 | 14 | 7
2018-11-05 13:00 | 15 | 9
2018-11-05 13:30 | 14 | 9
2018-11-05 14:00 | 11 | 1
2018-11-05 14:30 | 10 | 2
2018-11-05 15:00 | 9 | 2
2018-11-05 15:30 | 7 | 3
2018-11-05 16:00 | 12 | 11
2018-11-05 16:30 | 17 | 16
2018-11-05 17:00 | 29 | 29
2018-11-05 17:30 | 39 | 39
2018-11-05 18:00 | 46 | 46
2018-11-05 18:30 | 48 | 48
2018-11-05 19:00 | 47 | 46
2018-11-05 19:30 | 48 | 48
2018-11-05 20:00 | 61 | 61
2018-11-05 20:30 | 62 | 62
2018-11-05 21:00 | 70 | 69
2018-11-05 21:30 | 69 | 68
2018-11-05 22:00 | 66 | 65
2018-11-05 22:30 | 63 | 62
2018-11-05 23:00 | 62 | 61
2018-11-05 23:30 | 61 | 60
2018-11-06 | 60 | 60
2018-11-06 00:30 | 60 | 59
2018-11-06 01:00 | 61 | 60
2018-11-06 01:30 | 61 | 60
2018-11-06 02:00 | 61 | 60
2018-11-06 02:30 | 60 | 59
2018-11-06 03:00 | 60 | 59
2018-11-06 03:30 | 59 | 59
2018-11-06 04:00 | 60 | 60
2018-11-06 04:30 | 60 | 60
2018-11-06 05:00 | 60 | 59
2018-11-06 05:30 | 59 | 58
2018-11-06 06:00 | 58 | 57
2018-11-06 06:30 | 51 | 50
2018-11-06 07:00 | 41 | 40
2018-11-06 07:30 | 9 | 5
2018-11-06 08:00 | 10 | 8
2018-11-06 08:30 | 20 | 9
2018-11-06 09:00 | 24 | 18
2018-11-06 09:30 | 28 | 23
2018-11-06 10:00 | 23 | 16
2018-11-06 10:30 | 23 | 16
2018-11-06 11:00 | 28 | 23
2018-11-06 11:30 | 27 | 21
2018-11-06 12:00 | 28 | 23
2018-11-06 12:30 | 27 | 21
2018-11-06 13:00 | 26 | 21
2018-11-06 13:30 | 28 | 23
2018-11-06 14:00 | 26 | 22
2018-11-06 14:30 | 27 | 24
2018-11-06 15:00 | 28 | 24
2018-11-06 15:30 | 25 | 21
2018-11-06 16:00 | 19 | 12
2018-11-06 16:30 | 16 | 0
2018-11-06 17:00 | 21 | 11
2018-11-06 17:30 | 29 | 23
2018-11-06 18:00 | 39 | 34
2018-11-06 18:30 | 44 | 38
2018-11-06 19:00 | 46 | 39
2018-11-06 19:30 | 45 | 40
2018-11-06 20:00 | 45 | 42
2018-11-06 20:30 | 43 | 39
2018-11-06 21:00 | 41 | 37
2018-11-06 21:30 | 41 | 36
2018-11-06 22:00 | 43 | 41
2018-11-06 22:30 | 49 | 47
2018-11-06 23:00 | 57 | 57
2018-11-06 23:30 | 60 | 60
2018-11-07 | 60 | 60
2018-11-07 00:30 | 59 | 59
2018-11-07 01:00 | 60 | 60
2018-11-07 01:30 | 56 | 55
2018-11-07 02:00 | 63 | 63
2018-11-07 02:30 | 60 | 60
2018-11-07 03:00 | 59 | 59
2018-11-07 03:30 | 60 | 59
2018-11-07 04:00 | 58 | 58
2018-11-07 04:30 | 57 | 57
2018-11-07 05:00 | 55 | 54
2018-11-07 05:30 | 54 | 54
2018-11-07 06:00 | 51 | 51
2018-11-07 06:30 | 33 | 33
2018-11-07 07:00 | 16 | 10
2018-11-07 07:30 | 19 | 16
2018-11-07 08:00 | 21 | 19
2018-11-07 08:30 | 15 | 14
2018-11-07 09:00 | 16 | 13
2018-11-07 09:30 | 18 | 15
2018-11-07 10:00 | 15 | 11
2018-11-07 10:30 | 14 | 10
2018-11-07 11:00 | 15 | 11
2018-11-07 11:30 | 12 | 7
2018-11-07 12:00 | 10 | 8
2018-11-07 12:30 | 10 | 8
2018-11-07 13:00 | 6 | 4
2018-11-07 13:30 | 5 | 3
2018-11-07 14:00 | 7 | 4
2018-11-07 14:30 | 8 | 7
2018-11-07 15:00 | 6 | 2
2018-11-07 15:30 | 4 | 2
2018-11-07 16:00 | 11 | 11
2018-11-07 16:30 | 20 | 20
2018-11-07 17:00 | 31 | 31
2018-11-07 17:30 | 51 | 51
2018-11-07 18:00 | 58 | 57
2018-11-07 18:30 | 63 | 63
2018-11-07 19:00 | 59 | 59
2018-11-07 19:30 | 57 | 56
2018-11-07 20:00 | 54 | 54
2018-11-07 20:30 | 65 | 64
2018-11-07 21:00 | 65 | 63
2018-11-07 21:30 | 62 | 61
2018-11-07 22:00 | 63 | 61
2018-11-07 22:30 | 58 | 57
2018-11-07 23:00 | 58 | 57
2018-11-07 23:30 | 58 | 57
2018-11-08 | 58 | 56
2018-11-08 00:30 | 57 | 55
2018-11-08 01:00 | 56 | 54
2018-11-08 01:30 | 57 | 55
2018-11-08 02:00 | 56 | 55
2018-11-08 02:30 | 56 | 54
2018-11-08 03:00 | 55 | 54
2018-11-08 03:30 | 55 | 53
2018-11-08 04:00 | 56 | 55
2018-11-08 04:30 | 55 | 54
2018-11-08 05:00 | 55 | 54
2018-11-08 05:30 | 55 | 54
2018-11-08 06:00 | 38 | 38
2018-11-08 06:30 | 32 | 31
2018-11-08 07:00 | 27 | 26
2018-11-08 07:30 | 28 | 27
2018-11-08 08:00 | 26 | 24
2018-11-08 08:30 | 24 | 21
2018-11-08 09:00 | 27 | 24
2018-11-08 09:30 | 30 | 26
2018-11-08 10:00 | 21 | 18
2018-11-08 10:30 | 18 | 16
2018-11-08 11:00 | 18 | 15
2018-11-08 11:30 | 18 | 16
2018-11-08 12:00 | 18 | 15
2018-11-08 12:30 | 35 | 29
2018-11-08 13:00 | 39 | 33
2018-11-08 13:30 | 36 | 29
2018-11-08 14:00 | 15 | 3
2018-11-08 14:30 | 21 | 18
2018-11-08 15:00 | 22 | 20
2018-11-08 15:30 | 26 | 25
2018-11-08 16:00 | 34 | 33
2018-11-08 16:30 | 44 | 44
2018-11-08 17:00 | 54 | 53
2018-11-08 17:30 | 63 | 62
2018-11-08 18:00 | 67 | 67
2018-11-08 18:30 | 59 | 59
2018-11-08 19:00 | 59 | 58
2018-11-08 19:30 | 60 | 59
2018-11-08 20:00 | 59 | 57
2018-11-08 20:30 | 66 | 65
2018-11-08 21:00 | 65 | 65
2018-11-08 21:30 | 62 | 62
2018-11-08 22:00 | 61 | 61
2018-11-08 22:30 | 59 | 59
2018-11-08 23:00 | 59 | 58
2018-11-08 23:30 | 62 | 58
2018-11-09 | 62 | 57
2018-11-09 00:30 | 62 | 57
2018-11-09 01:00 | 61 | 56
2018-11-09 01:30 | 60 | 55
2018-11-09 02:00 | 60 | 56
2018-11-09 02:30 | 61 | 57
2018-11-09 03:00 | 61 | 57
2018-11-09 03:30 | 60 | 56
2018-11-09 04:00 | 59 | 55
2018-11-09 04:30 | 59 | 55
2018-11-09 05:00 | 60 | 56
2018-11-09 05:30 | 60 | 56
2018-11-09 06:00 | 57 | 53
2018-11-09 06:30 | 52 | 50
2018-11-09 07:00 | 53 | 52
2018-11-09 07:30 | 52 | 50
2018-11-09 08:00 | 41 | 39
2018-11-09 08:30 | 45 | 42
2018-11-09 09:00 | 40 | 38
2018-11-09 09:30 | 39 | 34
2018-11-09 10:00 | 29 | 21
2018-11-09 10:30 | 33 | 27
2018-11-09 11:00 | 26 | 18
2018-11-09 11:30 | 25 | 19
2018-11-09 12:00 | 26 | 20
2018-11-09 12:30 | 35 | 30
2018-11-09 13:00 | 27 | 20
2018-11-09 13:30 | 31 | 26
2018-11-09 14:00 | 37 | 31
2018-11-09 14:30 | 17 | 14
2018-11-09 15:00 | 16 | 12
2018-11-09 15:30 | 17 | 15
2018-11-09 16:00 | 22 | 20
2018-11-09 16:30 | 25 | 23
2018-11-09 17:00 | 33 | 31
2018-11-09 17:30 | 47 | 46
2018-11-09 18:00 | 57 | 57
2018-11-09 18:30 | 51 | 50
2018-11-09 19:00 | 51 | 50
2018-11-09 19:30 | 51 | 51
2018-11-09 20:00 | 53 | 53
2018-11-09 20:30 | 62 | 61
2018-11-09 21:00 | 63 | 61
2018-11-09 21:30 | 56 | 55
2018-11-09 22:00 | 59 | 57
2018-11-09 22:30 | 63 | 61
2018-11-09 23:00 | 61 | 59
2018-11-09 23:30 | 61 | 59
2018-11-10 | 61 | 60
2018-11-10 00:30 | 61 | 60
2018-11-10 01:00 | 59 | 58
2018-11-10 01:30 | 59 | 57
2018-11-10 02:00 | 61 | 60
2018-11-10 02:30 | 60 | 59
2018-11-10 03:00 | 59 | 58
2018-11-10 03:30 | 59 | 58
2018-11-10 04:00 | 60 | 59
2018-11-10 04:30 | 55 | 55
2018-11-10 05:00 | 51 | 51
2018-11-10 05:30 | 47 | 47
2018-11-10 06:00 | 45 | 45
2018-11-10 06:30 | 40 | 40
2018-11-10 07:00 | 33 | 33
2018-11-10 07:30 | 27 | 27
2018-11-10 08:00 | 26 | 25
2018-11-10 08:30 | 23 | 23
2018-11-10 09:00 | 11 | 10
2018-11-10 09:30 | 16 | 16
2018-11-10 10:00 | 22 | 22
2018-11-10 10:30 | 23 | 22
2018-11-10 11:00 | 26 | 26
2018-11-10 11:30 | 18 | 17
2018-11-10 12:00 | 27 | 26
2018-11-10 12:30 | 22 | 22
2018-11-10 13:00 | 16 | 15
2018-11-10 13:30 | 24 | 23
2018-11-10 14:00 | 14 | 13
2018-11-10 14:30 | 13 | 12
2018-11-10 15:00 | 15 | 15
2018-11-10 15:30 | 16 | 15
2018-11-10 16:00 | 19 | 19
2018-11-10 16:30 | 31 | 30
2018-11-10 17:00 | 29 | 29
2018-11-10 17:30 | 50 | 50
2018-11-10 18:00 | 57 | 57
2018-11-10 18:30 | 60 | 60
2018-11-10 19:00 | 61 | 61
2018-11-10 19:30 | 60 | 60
2018-11-10 20:00 | 68 | 68
2018-11-10 20:30 | 69 | 68
2018-11-10 21:00 | 68 | 67
2018-11-10 21:30 | 66 | 66
2018-11-10 22:00 | 66 | 65
2018-11-10 22:30 | 66 | 65
2018-11-10 23:00 | 65 | 64
2018-11-10 23:30 | 63 | 63
2018-11-11 | 62 | 62
2018-11-11 00:30 | 61 | 61
2018-11-11 01:00 | 62 | 62
2018-11-11 01:30 | 60 | 60
2018-11-11 02:00 | 59 | 59
2018-11-11 02:30 | 61 | 61
2018-11-11 03:00 | 59 | 59
2018-11-11 03:30 | 59 | 59
2018-11-11 04:00 | 60 | 60
2018-11-11 04:30 | 60 | 60
2018-11-11 05:00 | 60 | 60
2018-11-11 05:30 | 60 | 60
2018-11-11 06:00 | 59 | 59
2018-11-11 06:30 | 54 | 54
2018-11-11 07:00 | 45 | 45
2018-11-11 07:30 | 29 | 29
2018-11-11 08:00 | 26 | 26
2018-11-11 08:30 | 17 | 16
2018-11-11 09:00 | 11 | 10
2018-11-11 09:30 | 8 | 6
2018-11-11 10:00 | 8 | 7
2018-11-11 10:30 | 9 | 8
2018-11-11 11:00 | 10 | 9
2018-11-11 11:30 | 17 | 17
2018-11-11 12:00 | 21 | 21
2018-11-11 12:30 | 7 | 4
2018-11-11 13:00 | 9 | 8
2018-11-11 13:30 | 6 | 5
2018-11-11 14:00 | 15 | 14
2018-11-11 14:30 | 11 | 11
2018-11-11 15:00 | 12 | 12
2018-11-11 15:30 | 18 | 18
2018-11-11 16:00 | 25 | 25
2018-11-11 16:30 | 30 | 30
2018-11-11 17:00 | 39 | 39
2018-11-11 17:30 | 51 | 51
2018-11-11 18:00 | 51 | 51
2018-11-11 18:30 | 55 | 54
2018-11-11 19:00 | 47 | 45
2018-11-11 19:30 | 62 | 62
2018-11-11 20:00 | 67 | 67
2018-11-11 20:30 | 68 | 68
2018-11-11 21:00 | 68 | 68
2018-11-11 21:30 | 67 | 66
2018-11-11 22:00 | 66 | 66
2018-11-11 22:30 | 65 | 65
2018-11-11 23:00 | 63 | 63
2018-11-11 23:30 | 64 | 64
2018-11-12 | 63 | 63
2018-11-12 00:30 | 63 | 63
2018-11-12 01:00 | 63 | 63
2018-11-12 01:30 | 63 | 63
2018-11-12 02:00 | 62 | 62
2018-11-12 02:30 | 63 | 62
2018-11-12 03:00 | 63 | 62
2018-11-12 03:30 | 61 | 60
2018-11-12 04:00 | 60 | 60
2018-11-12 04:30 | 61 | 60
2018-11-12 05:00 | 62 | 62
2018-11-12 05:30 | 62 | 61
2018-11-12 06:00 | 57 | 56
2018-11-12 06:30 | 52 | 51
2018-11-12 07:00 | 42 | 40
2018-11-12 07:30 | 35 | 32
2018-11-12 08:00 | 36 | 34
2018-11-12 08:30 | 30 | 28
2018-11-12 09:00 | 29 | 27
2018-11-12 09:30 | 33 | 31
2018-11-12 10:00 | 34 | 32
2018-11-12 10:30 | 36 | 35
2018-11-12 11:00 | 23 | 21
2018-11-12 11:30 | 28 | 26
2018-11-12 12:00 | 23 | 20
2018-11-12 12:30 | 22 | 19
2018-11-12 13:00 | 23 | 20
2018-11-12 13:30 | 23 | 21
2018-11-12 14:00 | 23 | 21
2018-11-12 14:30 | 25 | 23
2018-11-12 15:00 | 21 | 18
2018-11-12 15:30 | 26 | 24
2018-11-12 16:00 | 34 | 33
2018-11-12 16:30 | 43 | 42
2018-11-12 17:00 | 53 | 52
2018-11-12 17:30 | 47 | 47
2018-11-12 18:00 | 57 | 57
2018-11-12 18:30 | 62 | 62
2018-11-12 19:00 | 66 | 66
2018-11-12 19:30 | 66 | 66
2018-11-12 20:00 | 64 | 64
2018-11-12 20:30 | 65 | 65
2018-11-12 21:00 | 63 | 63
2018-11-12 21:30 | 76 | 75
2018-11-12 22:00 | 75 | 74
2018-11-12 22:30 | 73 | 73
2018-11-12 23:00 | 73 | 72
2018-11-12 23:30 | 71 | 71
2018-11-13 | 71 | 70
2018-11-13 00:30 | 70 | 70
2018-11-13 01:00 | 72 | 71
2018-11-13 01:30 | 71 | 71
2018-11-13 02:00 | 71 | 70
2018-11-13 02:30 | 73 | 72
2018-11-13 03:00 | 74 | 73
2018-11-13 03:30 | 73 | 72
2018-11-13 04:00 | 73 | 72
2018-11-13 04:30 | 73 | 72
2018-11-13 05:00 | 74 | 73
2018-11-13 05:30 | 74 | 73
2018-11-13 06:00 | 73 | 73
2018-11-13 06:30 | 65 | 64
2018-11-13 07:00 | 54 | 53
2018-11-13 07:30 | 45 | 44
2018-11-13 08:00 | 38 | 37
2018-11-13 08:30 | 31 | 29
2018-11-13 09:00 | 31 | 29
2018-11-13 09:30 | 29 | 27
2018-11-13 10:00 | 36 | 34
2018-11-13 10:30 | 24 | 22
2018-11-13 11:00 | 25 | 24
2018-11-13 11:30 | 23 | 21
2018-11-13 12:00 | 23 | 21
2018-11-13 12:30 | 23 | 21
2018-11-13 13:00 | 25 | 22
2018-11-13 13:30 | 25 | 23
2018-11-13 14:00 | 23 | 20
2018-11-13 14:30 | 24 | 20
2018-11-13 15:00 | 25 | 22
2018-11-13 15:30 | 28 | 24
2018-11-13 16:00 | 35 | 32
2018-11-13 16:30 | 45 | 44
2018-11-13 17:00 | 54 | 53
2018-11-13 17:30 | 67 | 67
2018-11-13 18:00 | 78 | 77
2018-11-13 18:30 | 80 | 78
2018-11-13 19:00 | 77 | 75
2018-11-13 19:30 | 79 | 77
2018-11-13 20:00 | 78 | 76
2018-11-13 20:30 | 75 | 74
2018-11-13 21:00 | 74 | 73
2018-11-13 21:30 | 81 | 81
2018-11-13 22:00 | 81 | 81
2018-11-13 22:30 | 81 | 81
2018-11-13 23:00 | 80 | 80
2018-11-13 23:30 | 79 | 79
2018-11-14 | 79 | 79
2018-11-14 00:30 | 78 | 77
2018-11-14 01:00 | 76 | 76
2018-11-14 01:30 | 76 | 76
2018-11-14 02:00 | 76 | 76
2018-11-14 02:30 | 75 | 74
2018-11-14 03:00 | 74 | 73
2018-11-14 03:30 | 74 | 73
2018-11-14 04:00 | 75 | 74
2018-11-14 04:30 | 74 | 74
2018-11-14 05:00 | 75 | 75
2018-11-14 05:30 | 75 | 74
2018-11-14 06:00 | 71 | 70
2018-11-14 06:30 | 56 | 54
2018-11-14 07:00 | 47 | 44
2018-11-14 07:30 | 48 | 47
2018-11-14 08:00 | 45 | 44
2018-11-14 08:30 | 41 | 39
2018-11-14 09:00 | 40 | 38
2018-11-14 09:30 | 33 | 29
2018-11-14 10:00 | 31 | 27
2018-11-14 10:30 | 32 | 28
2018-11-14 11:00 | 30 | 27
2018-11-14 11:30 | 29 | 27
2018-11-14 12:00 | 27 | 25
2018-11-14 12:30 | 27 | 23
2018-11-14 13:00 | 25 | 19
2018-11-14 13:30 | 26 | 20
2018-11-14 14:00 | 26 | 18
2018-11-14 14:30 | 28 | 23
2018-11-14 15:00 | 29 | 26
2018-11-14 15:30 | 34 | 31
2018-11-14 16:00 | 42 | 38
2018-11-14 16:30 | 49 | 47
2018-11-14 17:00 | 60 | 58
2018-11-14 17:30 | 73 | 73
2018-11-14 18:00 | 84 | 84
2018-11-14 18:30 | 76 | 76
2018-11-14 19:00 | 74 | 74
2018-11-14 19:30 | 90 | 90
2018-11-14 20:00 | 84 | 84
2018-11-14 20:30 | 82 | 82
2018-11-14 21:00 | 88 | 88
2018-11-14 21:30 | 90 | 89
2018-11-14 22:00 | 88 | 88
2018-11-14 22:30 | 85 | 85
2018-11-14 23:00 | 81 | 80
2018-11-14 23:30 | 80 | 79
2018-11-15 | 80 | 79
2018-11-15 00:30 | 79 | 78
2018-11-15 01:00 | 78 | 78
2018-11-15 01:30 | 78 | 77
2018-11-15 02:00 | 78 | 77
2018-11-15 02:30 | 77 | 76
2018-11-15 03:00 | 76 | 76
2018-11-15 03:30 | 76 | 75
2018-11-15 04:00 | 75 | 74
2018-11-15 04:30 | 75 | 75
2018-11-15 05:00 | 75 | 74
2018-11-15 05:30 | 75 | 74
2018-11-15 06:00 | 72 | 71
2018-11-15 06:30 | 65 | 65
2018-11-15 07:00 | 58 | 57
2018-11-15 07:30 | 48 | 47
2018-11-15 08:00 | 41 | 39
2018-11-15 08:30 | 42 | 40
2018-11-15 09:00 | 39 | 36
2018-11-15 09:30 | 33 | 29
2018-11-15 10:00 | 34 | 31
2018-11-15 10:30 | 32 | 28
2018-11-15 11:00 | 32 | 23
2018-11-15 11:30 | 37 | 29
2018-11-15 12:00 | 37 | 29
2018-11-15 12:30 | 37 | 29
2018-11-15 13:00 | 37 | 29
2018-11-15 13:30 | 36 | 32
2018-11-15 14:00 | 35 | 29
2018-11-15 14:30 | 34 | 30
2018-11-15 15:00 | 32 | 27
2018-11-15 15:30 | 37 | 33
2018-11-15 16:00 | 43 | 40
2018-11-15 16:30 | 51 | 48
2018-11-15 17:00 | 54 | 52
2018-11-15 17:30 | 66 | 65
2018-11-15 18:00 | 71 | 70
2018-11-15 18:30 | 72 | 70
2018-11-15 19:00 | 72 | 72
2018-11-15 19:30 | 72 | 71
2018-11-15 20:00 | 72 | 71
2018-11-15 20:30 | 79 | 78
2018-11-15 21:00 | 80 | 79
2018-11-15 21:30 | 78 | 77
2018-11-15 22:00 | 78 | 77
2018-11-15 22:30 | 78 | 77
2018-11-15 23:00 | 80 | 79
2018-11-15 23:30 | 79 | 78
2018-11-16 | 75 | 75
2018-11-16 00:30 | 73 | 72
2018-11-16 01:00 | 72 | 72
2018-11-16 01:30 | 71 | 71
2018-11-16 02:00 | 71 | 71
2018-11-16 02:30 | 71 | 71
2018-11-16 03:00 | 71 | 70
2018-11-16 03:30 | 70 | 70
2018-11-16 04:00 | 70 | 70
2018-11-16 04:30 | 69 | 69
2018-11-16 05:00 | 69 | 69
2018-11-16 05:30 | 70 | 70
2018-11-16 06:00 | 68 | 68
2018-11-16 06:30 | 62 | 61
2018-11-16 07:00 | 50 | 49
2018-11-16 07:30 | 41 | 40
2018-11-16 08:00 | 41 | 40
2018-11-16 08:30 | 45 | 43
2018-11-16 09:00 | 35 | 32
2018-11-16 09:30 | 23 | 18
2018-11-16 10:00 | 22 | 16
2018-11-16 10:30 | 25 | 19
2018-11-16 11:00 | 28 | 20
2018-11-16 11:30 | 26 | 20
2018-11-16 12:00 | 25 | 21
2018-11-16 12:30 | 25 | 22
2018-11-16 13:00 | 30 | 23
2018-11-16 13:30 | 30 | 25
2018-11-16 14:00 | 28 | 24
2018-11-16 14:30 | 29 | 24
2018-11-16 15:00 | 30 | 26
2018-11-16 15:30 | 32 | 28
2018-11-16 16:00 | 38 | 35
2018-11-16 16:30 | 47 | 45
2018-11-16 17:00 | 50 | 48
2018-11-16 17:30 | 61 | 59
2018-11-16 18:00 | 71 | 70
2018-11-16 18:30 | 75 | 74
2018-11-16 19:00 | 77 | 76
2018-11-16 19:30 | 75 | 75
2018-11-16 20:00 | 75 | 74
2018-11-16 20:30 | 74 | 74
2018-11-16 21:00 | 72 | 72
2018-11-16 21:30 | 71 | 71
2018-11-16 22:00 | 71 | 71
2018-11-16 22:30 | 70 | 69
2018-11-16 23:00 | 71 | 70
2018-11-16 23:30 | 72 | 72
2018-11-17 | 71 | 70
2018-11-17 00:30 | 70 | 70
2018-11-17 01:00 | 70 | 70
2018-11-17 01:30 | 70 | 69
2018-11-17 02:00 | 70 | 69
2018-11-17 02:30 | 69 | 69
2018-11-17 03:00 | 70 | 69
2018-11-17 03:30 | 69 | 68
2018-11-17 04:00 | 69 | 68
2018-11-17 04:30 | 68 | 68
2018-11-17 05:00 | 67 | 67
2018-11-17 05:30 | 67 | 66
2018-11-17 06:00 | 64 | 63
2018-11-17 06:30 | 59 | 58
2018-11-17 07:00 | 46 | 44
2018-11-17 07:30 | 39 | 37
2018-11-17 08:00 | 33 | 31
2018-11-17 08:30 | 35 | 34
2018-11-17 09:00 | 25 | 22
2018-11-17 09:30 | 20 | 18
2018-11-17 10:00 | 20 | 18
2018-11-17 10:30 | 20 | 17
2018-11-17 11:00 | 18 | 15
2018-11-17 11:30 | 18 | 14
2018-11-17 12:00 | 20 | 17
2018-11-17 12:30 | 22 | 20
2018-11-17 13:00 | 22 | 20
2018-11-17 13:30 | 23 | 20
2018-11-17 14:00 | 21 | 18
2018-11-17 14:30 | 23 | 19
2018-11-17 15:00 | 23 | 20
2018-11-17 15:30 | 26 | 23
2018-11-17 16:00 | 30 | 27
2018-11-17 16:30 | 36 | 34
2018-11-17 17:00 | 47 | 45
2018-11-17 17:30 | 59 | 57
2018-11-17 18:00 | 67 | 65
2018-11-17 18:30 | 68 | 67
2018-11-17 19:00 | 67 | 67
2018-11-17 19:30 | 69 | 69
2018-11-17 20:00 | 69 | 69
2018-11-17 20:30 | 68 | 68
2018-11-17 21:00 | 67 | 67
2018-11-17 21:30 | 65 | 65
2018-11-17 22:00 | 65 | 65
2018-11-17 22:30 | 64 | 64
2018-11-17 23:00 | 63 | 63
2018-11-17 23:30 | 62 | 62
2018-11-18 | 62 | 62
2018-11-18 00:30 | 61 | 61
2018-11-18 01:00 | 62 | 62
2018-11-18 01:30 | 68 | 67
2018-11-18 02:00 | 67 | 67
2018-11-18 02:30 | 68 | 68
2018-11-18 03:00 | 68 | 67
2018-11-18 03:30 | 67 | 67
2018-11-18 04:00 | 67 | 67
2018-11-18 04:30 | 67 | 67
2018-11-18 05:00 | 67 | 67
2018-11-18 05:30 | 66 | 66
2018-11-18 06:00 | 65 | 65
2018-11-18 06:30 | 57 | 57
2018-11-18 07:00 | 53 | 52
2018-11-18 07:30 | 45 | 45
2018-11-18 08:00 | 33 | 32
2018-11-18 08:30 | 40 | 39
2018-11-18 09:00 | 36 | 36
2018-11-18 09:30 | 35 | 35
2018-11-18 10:00 | 29 | 29
2018-11-18 10:30 | 22 | 21
2018-11-18 11:00 | 21 | 20
2018-11-18 11:30 | 21 | 20
2018-11-18 12:00 | 27 | 26
2018-11-18 12:30 | 23 | 23
2018-11-18 13:00 | 29 | 28
2018-11-18 13:30 | 20 | 18
2018-11-18 14:00 | 21 | 20
2018-11-18 14:30 | 22 | 21
2018-11-18 15:00 | 25 | 23
2018-11-18 15:30 | 30 | 27
2018-11-18 16:00 | 37 | 35
2018-11-18 16:30 | 45 | 44
2018-11-18 17:00 | 52 | 51
2018-11-18 17:30 | 60 | 60
2018-11-18 18:00 | 70 | 70
2018-11-18 18:30 | 71 | 70
2018-11-18 19:00 | 72 | 71
2018-11-18 19:30 | 72 | 72
2018-11-18 20:00 | 72 | 71
2018-11-18 20:30 | 71 | 70
2018-11-18 21:00 | 69 | 68
2018-11-18 21:30 | 68 | 67
2018-11-18 22:00 | 69 | 67
2018-11-18 22:30 | 67 | 66
2018-11-18 23:00 | 67 | 65
2018-11-18 23:30 | 66 | 65
2018-11-19 | 66 | 64
2018-11-19 00:30 | 66 | 64
2018-11-19 01:00 | 72 | 71
2018-11-19 01:30 | 73 | 71
2018-11-19 02:00 | 73 | 72
2018-11-19 02:30 | 73 | 72
2018-11-19 03:00 | 72 | 71
2018-11-19 03:30 | 72 | 71
2018-11-19 04:00 | 73 | 71
2018-11-19 04:30 | 72 | 71
2018-11-19 05:00 | 73 | 71
2018-11-19 05:30 | 73 | 72
2018-11-19 06:00 | 70 | 69
2018-11-19 06:30 | 69 | 68
2018-11-19 07:00 | 67 | 66
2018-11-19 07:30 | 54 | 53
2018-11-19 08:00 | 48 | 46
2018-11-19 08:30 | 39 | 36
2018-11-19 09:00 | 30 | 28
2018-11-19 09:30 | 29 | 27
2018-11-19 10:00 | 35 | 33
2018-11-19 10:30 | 28 | 26
2018-11-19 11:00 | 39 | 37
2018-11-19 11:30 | 30 | 28
2018-11-19 12:00 | 30 | 28
2018-11-19 12:30 | 30 | 29
2018-11-19 13:00 | 40 | 40
2018-11-19 13:30 | 42 | 42
2018-11-19 14:00 | 36 | 36
2018-11-19 14:30 | 42 | 42
2018-11-19 15:00 | 39 | 39
2018-11-19 15:30 | 39 | 39
2018-11-19 16:00 | 51 | 51
2018-11-19 16:30 | 71 | 71
2018-11-19 17:00 | 79 | 79
2018-11-19 17:30 | 61 | 61
2018-11-19 18:00 | 75 | 75
2018-11-19 18:30 | 80 | 80
2018-11-19 19:00 | 84 | 83
2018-11-19 19:30 | 87 | 83
2018-11-19 20:00 | 83 | 79
2018-11-19 20:30 | 81 | 76
2018-11-19 21:00 | 80 | 76
2018-11-19 21:30 | 79 | 77
2018-11-19 22:00 | 78 | 76
2018-11-19 22:30 | 75 | 74
2018-11-19 23:00 | 73 | 72
2018-11-19 23:30 | 72 | 71
2018-11-20 | 71 | 71
2018-11-20 00:30 | 71 | 70
2018-11-20 01:00 | 71 | 70
2018-11-20 01:30 | 71 | 70
2018-11-20 02:00 | 71 | 70
2018-11-20 02:30 | 70 | 69
2018-11-20 03:00 | 70 | 69
2018-11-20 03:30 | 70 | 69
2018-11-20 04:00 | 69 | 68
2018-11-20 04:30 | 71 | 69
2018-11-20 05:00 | 72 | 70
2018-11-20 05:30 | 71 | 70
2018-11-20 06:00 | 69 | 69
2018-11-20 06:30 | 65 | 64
2018-11-20 07:00 | 55 | 54
2018-11-20 07:30 | 56 | 56
2018-11-20 08:00 | 54 | 53
2018-11-20 08:30 | 39 | 38
2018-11-20 09:00 | 44 | 44
2018-11-20 09:30 | 37 | 37
2018-11-20 10:00 | 35 | 34
2018-11-20 10:30 | 25 | 23
2018-11-20 11:00 | 23 | 21
2018-11-20 11:30 | 22 | 20
2018-11-20 12:00 | 20 | 18
2018-11-20 12:30 | 17 | 15
2018-11-20 13:00 | 17 | 15
2018-11-20 13:30 | 18 | 16
2018-11-20 14:00 | 20 | 19
2018-11-20 14:30 | 22 | 22
2018-11-20 15:00 | 27 | 26
2018-11-20 15:30 | 33 | 32
2018-11-20 16:00 | 38 | 36
2018-11-20 16:30 | 43 | 41
2018-11-20 17:00 | 48 | 46
2018-11-20 17:30 | 60 | 58
2018-11-20 18:00 | 62 | 60
2018-11-20 18:30 | 67 | 65
2018-11-20 19:00 | 56 | 51
2018-11-20 19:30 | 65 | 61
2018-11-20 20:00 | 68 | 66
2018-11-20 20:30 | 66 | 63
2018-11-20 21:00 | 66 | 62
2018-11-20 21:30 | 72 | 70
2018-11-20 22:00 | 75 | 74
2018-11-20 22:30 | 75 | 73
2018-11-20 23:00 | 74 | 72
2018-11-20 23:30 | 72 | 70
2018-11-21 | 71 | 69
2018-11-21 00:30 | 70 | 68
2018-11-21 01:00 | 70 | 68
2018-11-21 01:30 | 69 | 67
2018-11-21 02:00 | 68 | 67
2018-11-21 02:30 | 69 | 68
2018-11-21 03:00 | 69 | 68
2018-11-21 03:30 | 69 | 68
2018-11-21 04:00 | 68 | 67
2018-11-21 04:30 | 67 | 66
2018-11-21 05:00 | 67 | 66
2018-11-21 05:30 | 67 | 66
2018-11-21 06:00 | 65 | 64
2018-11-21 06:30 | 58 | 57
2018-11-21 07:00 | 47 | 47
2018-11-21 07:30 | 39 | 39
2018-11-21 08:00 | 35 | 34
2018-11-21 08:30 | 28 | 28
2018-11-21 09:00 | 26 | 25
2018-11-21 09:30 | 19 | 18
2018-11-21 10:00 | 17 | 16
2018-11-21 10:30 | 18 | 17
2018-11-21 11:00 | 18 | 17
2018-11-21 11:30 | 19 | 18
2018-11-21 12:00 | 18 | 18
2018-11-21 12:30 | 18 | 18
2018-11-21 13:00 | 19 | 18
2018-11-21 13:30 | 20 | 19
2018-11-21 14:00 | 21 | 20
2018-11-21 14:30 | 13 | 13
2018-11-21 15:00 | 20 | 19
2018-11-21 15:30 | 14 | 14
2018-11-21 16:00 | 17 | 17
2018-11-21 16:30 | 27 | 24
2018-11-21 17:00 | 36 | 33
2018-11-21 17:30 | 47 | 45
2018-11-21 18:00 | 61 | 58
2018-11-21 18:30 | 70 | 67
2018-11-21 19:00 | 64 | 57
2018-11-21 19:30 | 71 | 67
2018-11-21 20:00 | 76 | 73
2018-11-21 20:30 | 83 | 82
2018-11-21 21:00 | 79 | 79
2018-11-21 21:30 | 80 | 79
2018-11-21 22:00 | 79 | 78
2018-11-21 22:30 | 76 | 76
2018-11-21 23:00 | 76 | 75
2018-11-21 23:30 | 72 | 72
2018-11-22 | 70 | 70
2018-11-22 00:30 | 68 | 68
2018-11-22 01:00 | 68 | 67
2018-11-22 01:30 | 69 | 68
2018-11-22 02:00 | 69 | 68
2018-11-22 02:30 | 69 | 68
2018-11-22 03:00 | 68 | 67
2018-11-22 03:30 | 67 | 67
2018-11-22 04:00 | 67 | 66
2018-11-22 04:30 | 67 | 66
2018-11-22 05:00 | 67 | 67
2018-11-22 05:30 | 68 | 67
2018-11-22 06:00 | 67 | 66
2018-11-22 06:30 | 65 | 64
2018-11-22 07:00 | 58 | 58
2018-11-22 07:30 | 44 | 43
2018-11-22 08:00 | 38 | 37
2018-11-22 08:30 | 21 | 20
2018-11-22 09:00 | 10 | 10
2018-11-22 09:30 | 9 | 9
2018-11-22 10:00 | 20 | 20
2018-11-22 10:30 | 24 | 24
2018-11-22 11:00 | 10 | 10
2018-11-22 11:30 | 9 | 9
2018-11-22 12:00 | 16 | 15
2018-11-22 12:30 | 16 | 15
2018-11-22 13:00 | 43 | 42
2018-11-22 13:30 | 19 | 18
2018-11-22 14:00 | 20 | 19
2018-11-22 14:30 | 19 | 19
2018-11-22 15:00 | 20 | 20
2018-11-22 15:30 | 25 | 21
2018-11-22 16:00 | 42 | 38
2018-11-22 16:30 | 78 | 75
2018-11-22 17:00 | 83 | 80
2018-11-22 17:30 | 83 | 80
2018-11-22 18:00 | 81 | 77
2018-11-22 18:30 | 78 | 73
2018-11-22 19:00 | 77 | 66
2018-11-22 19:30 | 72 | 55
2018-11-22 20:00 | 76 | 64
2018-11-22 20:30 | 78 | 68
2018-11-22 21:00 | 82 | 75
2018-11-22 21:30 | 85 | 80
2018-11-22 22:00 | 84 | 79
2018-11-22 22:30 | 81 | 76
2018-11-22 23:00 | 77 | 73
2018-11-22 23:30 | 76 | 71
2018-11-23 | 75 | 70
2018-11-23 00:30 | 74 | 68
2018-11-23 01:00 | 73 | 68
2018-11-23 01:30 | 69 | 68
2018-11-23 02:00 | 68 | 68
2018-11-23 02:30 | 69 | 68
2018-11-23 03:00 | 68 | 68
2018-11-23 03:30 | 68 | 67
2018-11-23 04:00 | 67 | 67
2018-11-23 04:30 | 67 | 67
2018-11-23 05:00 | 68 | 68
2018-11-23 05:30 | 68 | 68
2018-11-23 06:00 | 67 | 66
2018-11-23 06:30 | 65 | 65
2018-11-23 07:00 | 53 | 53
2018-11-23 07:30 | 41 | 40
2018-11-23 08:00 | 38 | 37
2018-11-23 08:30 | 42 | 41
2018-11-23 09:00 | 28 | 27
2018-11-23 09:30 | 32 | 30
2018-11-23 10:00 | 18 | 16
2018-11-23 10:30 | 16 | 14
2018-11-23 11:00 | 12 | 9
2018-11-23 11:30 | 16 | 16
2018-11-23 12:00 | 17 | 17
2018-11-23 12:30 | 16 | 16
2018-11-23 13:00 | 15 | 14
2018-11-23 13:30 | 15 | 14
2018-11-23 14:00 | 19 | 18
2018-11-23 14:30 | 19 | 18
2018-11-23 15:00 | 23 | 22
2018-11-23 15:30 | 25 | 24
2018-11-23 16:00 | 36 | 35
2018-11-23 16:30 | 46 | 45
2018-11-23 17:00 | 53 | 52
2018-11-23 17:30 | 46 | 45
2018-11-23 18:00 | 70 | 70
2018-11-23 18:30 | 71 | 70
2018-11-23 19:00 | 73 | 72
2018-11-23 19:30 | 68 | 66
2018-11-23 20:00 | 73 | 71
2018-11-23 20:30 | 76 | 76
2018-11-23 21:00 | 75 | 74
2018-11-23 21:30 | 73 | 72
2018-11-23 22:00 | 72 | 71
2018-11-23 22:30 | 71 | 70
2018-11-23 23:00 | 71 | 70
2018-11-23 23:30 | 69 | 68
2018-11-24 | 69 | 67
2018-11-24 00:30 | 67 | 66
2018-11-24 01:00 | 67 | 66
2018-11-24 01:30 | 67 | 66
2018-11-24 02:00 | 66 | 65
2018-11-24 02:30 | 66 | 65
2018-11-24 03:00 | 66 | 64
2018-11-24 03:30 | 66 | 64
2018-11-24 04:00 | 66 | 64
2018-11-24 04:30 | 66 | 64
2018-11-24 05:00 | 66 | 64
2018-11-24 05:30 | 65 | 63
2018-11-24 06:00 | 63 | 62
2018-11-24 06:30 | 58 | 57
2018-11-24 07:00 | 52 | 51
2018-11-24 07:30 | 42 | 41
2018-11-24 08:00 | 32 | 31
2018-11-24 08:30 | 26 | 26
2018-11-24 09:00 | 27 | 25
2018-11-24 09:30 | 26 | 24
2018-11-24 10:00 | 19 | 16
2018-11-24 10:30 | 18 | 16
2018-11-24 11:00 | 21 | 20
2018-11-24 11:30 | 18 | 16
2018-11-24 12:00 | 24 | 22
2018-11-24 12:30 | 27 | 26
2018-11-24 13:00 | 27 | 26
2018-11-24 13:30 | 30 | 27
2018-11-24 14:00 | 25 | 21
2018-11-24 14:30 | 25 | 20
2018-11-24 15:00 | 26 | 22
2018-11-24 15:30 | 30 | 27
2018-11-24 16:00 | 34 | 31
2018-11-24 16:30 | 40 | 37
2018-11-24 17:00 | 47 | 44
2018-11-24 17:30 | 52 | 52
2018-11-24 18:00 | 60 | 60
2018-11-24 18:30 | 66 | 63
2018-11-24 19:00 | 68 | 66
2018-11-24 19:30 | 72 | 71
2018-11-24 20:00 | 71 | 70
2018-11-24 20:30 | 72 | 70
2018-11-24 21:00 | 75 | 74
2018-11-24 21:30 | 75 | 74
2018-11-24 22:00 | 74 | 72
2018-11-24 22:30 | 73 | 71
2018-11-24 23:00 | 72 | 70
2018-11-24 23:30 | 70 | 68
2018-11-25 | 69 | 68
2018-11-25 00:30 | 69 | 69
2018-11-25 01:00 | 69 | 68
2018-11-25 01:30 | 69 | 68
2018-11-25 02:00 | 68 | 67
2018-11-25 02:30 | 67 | 66
2018-11-25 03:00 | 67 | 66
2018-11-25 03:30 | 68 | 66
2018-11-25 04:00 | 68 | 66
2018-11-25 04:30 | 66 | 65
2018-11-25 05:00 | 66 | 65
2018-11-25 05:30 | 65 | 64
2018-11-25 06:00 | 63 | 62
2018-11-25 06:30 | 56 | 55
2018-11-25 07:00 | 45 | 44
2018-11-25 07:30 | 36 | 35
2018-11-25 08:00 | 31 | 29
2018-11-25 08:30 | 37 | 36
2018-11-25 09:00 | 25 | 23
2018-11-25 09:30 | 18 | 17
2018-11-25 10:00 | 16 | 14
2018-11-25 10:30 | 17 | 16
2018-11-25 11:00 | 21 | 21
2018-11-25 11:30 | 20 | 19
2018-11-25 12:00 | 20 | 19
2018-11-25 12:30 | 25 | 24
2018-11-25 13:00 | 29 | 28
2018-11-25 13:30 | 30 | 30
2018-11-25 14:00 | 28 | 28
2018-11-25 14:30 | 24 | 24
2018-11-25 15:00 | 30 | 29
2018-11-25 15:30 | 35 | 35
2018-11-25 16:00 | 37 | 37
2018-11-25 16:30 | 39 | 39
2018-11-25 17:00 | 48 | 48
2018-11-25 17:30 | 58 | 58
2018-11-25 18:00 | 68 | 68
2018-11-25 18:30 | 58 | 58
2018-11-25 19:00 | 53 | 45
2018-11-25 19:30 | 53 | 47
2018-11-25 20:00 | 60 | 56
2018-11-25 20:30 | 70 | 69
2018-11-25 21:00 | 70 | 70
2018-11-25 21:30 | 73 | 72
2018-11-25 22:00 | 72 | 71
2018-11-25 22:30 | 69 | 69
2018-11-25 23:00 | 71 | 71
2018-11-25 23:30 | 71 | 70
2018-11-26 | 72 | 69
2018-11-26 00:30 | 71 | 69
2018-11-26 01:00 | 71 | 69
2018-11-26 01:30 | 70 | 68
2018-11-26 02:00 | 71 | 69
2018-11-26 02:30 | 60 | 59
2018-11-26 03:00 | 48 | 48
2018-11-26 03:30 | 54 | 54
2018-11-26 04:00 | 58 | 58
2018-11-26 04:30 | 60 | 60
2018-11-26 05:00 | 60 | 59
2018-11-26 05:30 | 62 | 62
2018-11-26 06:00 | 63 | 62
2018-11-26 06:30 | 58 | 57
2018-11-26 07:00 | 45 | 43
2018-11-26 07:30 | 33 | 32
2018-11-26 08:00 | 27 | 25
2018-11-26 08:30 | 23 | 18
2018-11-26 09:00 | 20 | 13
2018-11-26 09:30 | 17 | 10
2018-11-26 10:00 | 17 | 10
2018-11-26 10:30 | 18 | 11
2018-11-26 11:00 | 22 | 17
2018-11-26 11:30 | 23 | 18
2018-11-26 12:00 | 23 | 19
2018-11-26 12:30 | 24 | 20
2018-11-26 13:00 | 32 | 31
2018-11-26 13:30 | 29 | 29
2018-11-26 14:00 | 27 | 27
2018-11-26 14:30 | 29 | 28
2018-11-26 15:00 | 31 | 30
2018-11-26 15:30 | 28 | 27
2018-11-26 16:00 | 39 | 37
2018-11-26 16:30 | 53 | 52
2018-11-26 17:00 | 60 | 59
2018-11-26 17:30 | 64 | 63
2018-11-26 18:00 | 59 | 53
2018-11-26 18:30 | 70 | 63
2018-11-26 19:00 | 68 | 63
2018-11-26 19:30 | 69 | 67
2018-11-26 20:00 | 66 | 63
2018-11-26 20:30 | 75 | 73
2018-11-26 21:00 | 72 | 71
2018-11-26 21:30 | 76 | 76
2018-11-26 22:00 | 72 | 72
2018-11-26 22:30 | 71 | 71
2018-11-26 23:00 | 71 | 70
2018-11-26 23:30 | 69 | 69
2018-11-27 | 68 | 68
2018-11-27 00:30 | 68 | 67
2018-11-27 01:00 | 67 | 67
2018-11-27 01:30 | 67 | 67
2018-11-27 02:00 | 66 | 66
2018-11-27 02:30 | 66 | 65
2018-11-27 03:00 | 66 | 66
2018-11-27 03:30 | 67 | 66
2018-11-27 04:00 | 67 | 67
2018-11-27 04:30 | 68 | 67
2018-11-27 05:00 | 67 | 66
2018-11-27 05:30 | 66 | 65
2018-11-27 06:00 | 63 | 63
2018-11-27 06:30 | 59 | 58
2018-11-27 07:00 | 49 | 48
2018-11-27 07:30 | 49 | 48
2018-11-27 08:00 | 41 | 40
2018-11-27 08:30 | 30 | 30
2018-11-27 09:00 | 29 | 29
2018-11-27 09:30 | 18 | 18
2018-11-27 10:00 | 24 | 24
2018-11-27 10:30 | 26 | 25
2018-11-27 11:00 | 26 | 25
2018-11-27 11:30 | 25 | 24
2018-11-27 12:00 | 25 | 24
2018-11-27 12:30 | 39 | 39
2018-11-27 13:00 | 28 | 27
2018-11-27 13:30 | 39 | 38
2018-11-27 14:00 | 32 | 30
2018-11-27 14:30 | 34 | 33
2018-11-27 15:00 | 45 | 44
2018-11-27 15:30 | 57 | 57
2018-11-27 16:00 | 65 | 64
2018-11-27 16:30 | 56 | 55
2018-11-27 17:00 | 49 | 48
2018-11-27 17:30 | 65 | 64
2018-11-27 18:00 | 73 | 72
2018-11-27 18:30 | 74 | 73
2018-11-27 19:00 | 76 | 75
2018-11-27 19:30 | 75 | 75
2018-11-27 20:00 | 77 | 77
2018-11-27 20:30 | 77 | 77
2018-11-27 21:00 | 80 | 80
2018-11-27 21:30 | 79 | 79
2018-11-27 22:00 | 79 | 79
2018-11-27 22:30 | 74 | 73
2018-11-27 23:00 | 75 | 74
2018-11-27 23:30 | 75 | 74
2018-11-28 | 73 | 73
2018-11-28 00:30 | 73 | 72
2018-11-28 01:00 | 73 | 72
2018-11-28 01:30 | 72 | 71
2018-11-28 02:00 | 72 | 70
2018-11-28 02:30 | 71 | 70
2018-11-28 03:00 | 71 | 69
2018-11-28 03:30 | 71 | 69
2018-11-28 04:00 | 71 | 69
2018-11-28 04:30 | 71 | 69
2018-11-28 05:00 | 70 | 68
2018-11-28 05:30 | 69 | 68
2018-11-28 06:00 | 66 | 64
2018-11-28 06:30 | 61 | 59
2018-11-28 07:00 | 55 | 53
2018-11-28 07:30 | 48 | 46
2018-11-28 08:00 | 40 | 39
2018-11-28 08:30 | 35 | 33
2018-11-28 09:00 | 26 | 24
2018-11-28 09:30 | 19 | 17
2018-11-28 10:00 | 18 | 16
2018-11-28 10:30 | 20 | 18
2018-11-28 11:00 | 26 | 25
2018-11-28 11:30 | 25 | 25
2018-11-28 12:00 | 38 | 38
2018-11-28 12:30 | 40 | 40
2018-11-28 13:00 | 24 | 24
2018-11-28 13:30 | 50 | 50
2018-11-28 14:00 | 55 | 55
2018-11-28 14:30 | 40 | 40
2018-11-28 15:00 | 51 | 51
2018-11-28 15:30 | 61 | 60
2018-11-28 16:00 | 70 | 69
2018-11-28 16:30 | 71 | 68
2018-11-28 17:00 | 67 | 64
2018-11-28 17:30 | 65 | 61
2018-11-28 18:00 | 70 | 67
2018-11-28 18:30 | 66 | 62
2018-11-28 19:00 | 70 | 66
2018-11-28 19:30 | 74 | 71
2018-11-28 20:00 | 74 | 72
2018-11-28 20:30 | 77 | 66
2018-11-28 21:00 | 80 | 66
2018-11-28 21:30 | 67 | 64
2018-11-28 22:00 | 65 | 62
2018-11-28 22:30 | 64 | 60
2018-11-28 23:00 | 64 | 59
2018-11-28 23:30 | 63 | 59
2018-11-29 | 63 | 59
2018-11-29 00:30 | 61 | 58
2018-11-29 01:00 | 60 | 58
2018-11-29 01:30 | 60 | 58
2018-11-29 02:00 | 60 | 57
2018-11-29 02:30 | 60 | 57
2018-11-29 03:00 | 60 | 57
2018-11-29 03:30 | 59 | 57
2018-11-29 04:00 | 59 | 56
2018-11-29 04:30 | 58 | 55
2018-11-29 05:00 | 57 | 54
2018-11-29 05:30 | 58 | 55
2018-11-29 06:00 | 56 | 52
2018-11-29 06:30 | 56 | 53
2018-11-29 07:00 | 56 | 52
2018-11-29 07:30 | 54 | 51
2018-11-29 08:00 | 47 | 42
2018-11-29 08:30 | 39 | 33
2018-11-29 09:00 | 30 | 23
2018-11-29 09:30 | 24 | 17
2018-11-29 10:00 | 22 | 15
2018-11-29 10:30 | 22 | 15
2018-11-29 11:00 | 23 | 16
2018-11-29 11:30 | 24 | 17
2018-11-29 12:00 | 24 | 18
2018-11-29 12:30 | 24 | 19
2018-11-29 13:00 | 26 | 20
2018-11-29 13:30 | 24 | 18
2018-11-29 14:00 | 24 | 19
2018-11-29 14:30 | 24 | 19
2018-11-29 15:00 | 25 | 21
2018-11-29 15:30 | 26 | 23
2018-11-29 16:00 | 37 | 35
2018-11-29 16:30 | 43 | 41
2018-11-29 17:00 | 57 | 55
2018-11-29 17:30 | 62 | 60
2018-11-29 18:00 | 82 | 75
2018-11-29 18:30 | 85 | 79
2018-11-29 19:00 | 87 | 80
2018-11-29 19:30 | 88 | 81
2018-11-29 20:00 | 83 | 80
2018-11-29 20:30 | 82 | 82
2018-11-29 21:00 | 83 | 82
2018-11-29 21:30 | 79 | 78
2018-11-29 22:00 | 75 | 74
2018-11-29 22:30 | 71 | 71
2018-11-29 23:00 | 69 | 69
2018-11-29 23:30 | 68 | 68
2018-11-30 | 69 | 69
2018-11-30 00:30 | 68 | 68
2018-11-30 01:00 | 68 | 68
2018-11-30 01:30 | 68 | 68
2018-11-30 02:00 | 67 | 67
2018-11-30 02:30 | 68 | 67
2018-11-30 03:00 | 66 | 66
2018-11-30 03:30 | 65 | 65
2018-11-30 04:00 | 66 | 65
2018-11-30 04:30 | 66 | 65
2018-11-30 05:00 | 67 | 65
2018-11-30 05:30 | 66 | 65
2018-11-30 06:00 | 64 | 63
2018-11-30 06:30 | 59 | 58
2018-11-30 07:00 | 50 | 48
2018-11-30 07:30 | 44 | 42
2018-11-30 08:00 | 35 | 32
2018-11-30 08:30 | 33 | 27
2018-11-30 09:00 | 27 | 20
2018-11-30 09:30 | 24 | 16
2018-11-30 10:00 | 25 | 17
2018-11-30 10:30 | 25 | 18
2018-11-30 11:00 | 25 | 17
2018-11-30 11:30 | 25 | 17
2018-11-30 12:00 | 27 | 20
2018-11-30 12:30 | 25 | 15
2018-11-30 13:00 | 32 | 23
2018-11-30 13:30 | 33 | 25
2018-11-30 14:00 | 32 | 24
2018-11-30 14:30 | 33 | 25
2018-11-30 15:00 | 33 | 26
2018-11-30 15:30 | 35 | 28
2018-11-30 16:00 | 39 | 34
2018-11-30 16:30 | 46 | 41
2018-11-30 17:00 | 51 | 47
2018-11-30 17:30 | 60 | 57
2018-11-30 18:00 | 69 | 69
2018-11-30 18:30 | 73 | 73
2018-11-30 19:00 | 65 | 64
2018-11-30 19:30 | 68 | 67
2018-11-30 20:00 | 70 | 69
2018-11-30 20:30 | 72 | 71
2018-11-30 21:00 | 72 | 71
2018-11-30 21:30 | 71 | 71
2018-11-30 22:00 | 71 | 71
2018-11-30 22:30 | 70 | 69
2018-11-30 23:00 | 71 | 70
2018-11-30 23:30 | 68 | 68
2018-12-01 | 69 | 68
2018-12-01 00:30 | 69 | 68
2018-12-01 01:00 | 69 | 68
2018-12-01 01:30 | 70 | 68
2018-12-01 02:00 | 70 | 68
2018-12-01 02:30 | 68 | 67
2018-12-01 03:00 | 68 | 66
2018-12-01 03:30 | 68 | 66
2018-12-01 04:00 | 67 | 65
2018-12-01 04:30 | 67 | 65
2018-12-01 05:00 | 66 | 65
2018-12-01 05:30 | 67 | 65
2018-12-01 06:00 | 64 | 63
2018-12-01 06:30 | 58 | 56
2018-12-01 07:00 | 48 | 45
2018-12-01 07:30 | 40 | 36
2018-12-01 08:00 | 37 | 32
2018-12-01 08:30 | 32 | 25
2018-12-01 09:00 | 27 | 15
2018-12-01 09:30 | 25 | 10
2018-12-01 10:00 | 24 | 8
2018-12-01 10:30 | 24 | 10
2018-12-01 11:00 | 25 | 10
2018-12-01 11:30 | 24 | 12
2018-12-01 12:00 | 22 | 13
2018-12-01 12:30 | 23 | 14
2018-12-01 13:00 | 24 | 15
2018-12-01 13:30 | 24 | 15
2018-12-01 14:00 | 25 | 17
2018-12-01 14:30 | 24 | 15
2018-12-01 15:00 | 23 | 14
2018-12-01 15:30 | 29 | 23
2018-12-01 16:00 | 23 | 20
2018-12-01 16:30 | 29 | 27
2018-12-01 17:00 | 35 | 34
2018-12-01 17:30 | 39 | 38
2018-12-01 18:00 | 52 | 51
2018-12-01 18:30 | 59 | 58
2018-12-01 19:00 | 58 | 58
2018-12-01 19:30 | 58 | 58
2018-12-01 20:00 | 67 | 66
2018-12-01 20:30 | 78 | 77
2018-12-01 21:00 | 77 | 76
2018-12-01 21:30 | 77 | 76
2018-12-01 22:00 | 78 | 76
2018-12-01 22:30 | 77 | 75
2018-12-01 23:00 | 81 | 80
2018-12-01 23:30 | 81 | 79
2018-12-02 | 79 | 77
2018-12-02 00:30 | 78 | 76
2018-12-02 01:00 | 76 | 75
2018-12-02 01:30 | 76 | 75
2018-12-02 02:00 | 77 | 76
2018-12-02 02:30 | 77 | 75
2018-12-02 03:00 | 77 | 76
2018-12-02 03:30 | 76 | 75
2018-12-02 04:00 | 75 | 74
2018-12-02 04:30 | 74 | 73
2018-12-02 05:00 | 74 | 73
2018-12-02 05:30 | 74 | 73
2018-12-02 06:00 | 72 | 72
2018-12-02 06:30 | 66 | 65
2018-12-02 07:00 | 56 | 54
2018-12-02 07:30 | 47 | 45
2018-12-02 08:00 | 40 | 38
2018-12-02 08:30 | 32 | 28
2018-12-02 09:00 | 27 | 23
2018-12-02 09:30 | 24 | 19
2018-12-02 10:00 | 22 | 17
2018-12-02 10:30 | 21 | 16
2018-12-02 11:00 | 21 | 12
2018-12-02 11:30 | 21 | 12
2018-12-02 12:00 | 22 | 14
2018-12-02 12:30 | 23 | 15
2018-12-02 13:00 | 23 | 16
2018-12-02 13:30 | 21 | 13
2018-12-02 14:00 | 17 | 1
2018-12-02 14:30 | 21 | 10
2018-12-02 15:00 | 23 | 16
2018-12-02 15:30 | 24 | 17
2018-12-02 16:00 | 33 | 29
2018-12-02 16:30 | 40 | 36
2018-12-02 17:00 | 42 | 38
2018-12-02 17:30 | 53 | 50
2018-12-02 18:00 | 63 | 60
2018-12-02 18:30 | 70 | 68
2018-12-02 19:00 | 63 | 58
2018-12-02 19:30 | 45 | 39
2018-12-02 20:00 | 34 | 29
2018-12-02 20:30 | 25 | 15
2018-12-02 21:00 | 41 | 35
2018-12-02 21:30 | 71 | 71
2018-12-02 22:00 | 75 | 75
2018-12-02 22:30 | 72 | 72
2018-12-02 23:00 | 71 | 71
2018-12-02 23:30 | 70 | 69
2018-12-03 | 69 | 68
2018-12-03 00:30 | 67 | 66
2018-12-03 01:00 | 66 | 65
2018-12-03 01:30 | 67 | 67
2018-12-03 02:00 | 70 | 69
2018-12-03 02:30 | 70 | 69
2018-12-03 03:00 | 70 | 68
2018-12-03 03:30 | 68 | 67
2018-12-03 04:00 | 69 | 68
2018-12-03 04:30 | 68 | 67
2018-12-03 05:00 | 69 | 67
2018-12-03 05:30 | 68 | 67
2018-12-03 06:00 | 68 | 67
2018-12-03 06:30 | 60 | 59
2018-12-03 07:00 | 51 | 50
2018-12-03 07:30 | 41 | 41
2018-12-03 08:00 | 39 | 39
2018-12-03 08:30 | 37 | 37
2018-12-03 09:00 | 29 | 29
2018-12-03 09:30 | 22 | 21
2018-12-03 10:00 | 22 | 21
2018-12-03 10:30 | 22 | 21
2018-12-03 11:00 | 23 | 21
2018-12-03 11:30 | 23 | 19
2018-12-03 12:00 | 22 | 20
2018-12-03 12:30 | 23 | 21
2018-12-03 13:00 | 25 | 23
2018-12-03 13:30 | 26 | 24
2018-12-03 14:00 | 26 | 23
2018-12-03 14:30 | 28 | 24
2018-12-03 15:00 | 36 | 32
2018-12-03 15:30 | 37 | 33
2018-12-03 16:00 | 48 | 45
2018-12-03 16:30 | 59 | 57
2018-12-03 17:00 | 76 | 75
2018-12-03 17:30 | 83 | 82
2018-12-03 18:00 | 85 | 84
2018-12-03 18:30 | 86 | 86
2018-12-03 19:00 | 82 | 82
2018-12-03 19:30 | 79 | 79
2018-12-03 20:00 | 68 | 67
2018-12-03 20:30 | 69 | 67
2018-12-03 21:00 | 67 | 65
2018-12-03 21:30 | 69 | 68
2018-12-03 22:00 | 71 | 71
2018-12-03 22:30 | 70 | 69
2018-12-03 23:00 | 71 | 70
2018-12-03 23:30 | 69 | 68
2018-12-04 | 66 | 65
2018-12-04 00:30 | 71 | 70
2018-12-04 01:00 | 72 | 72
2018-12-04 01:30 | 72 | 72
2018-12-04 02:00 | 72 | 72
2018-12-04 02:30 | 71 | 71
2018-12-04 03:00 | 71 | 71
2018-12-04 03:30 | 71 | 71
2018-12-04 04:00 | 70 | 70
2018-12-04 04:30 | 69 | 69
2018-12-04 05:00 | 70 | 70
2018-12-04 05:30 | 71 | 71
2018-12-04 06:00 | 70 | 70
2018-12-04 06:30 | 67 | 67
2018-12-04 07:00 | 59 | 58
2018-12-04 07:30 | 48 | 47
2018-12-04 08:00 | 38 | 37
2018-12-04 08:30 | 30 | 28
2018-12-04 09:00 | 26 | 25
2018-12-04 09:30 | 24 | 22
2018-12-04 10:00 | 19 | 18
2018-12-04 10:30 | 19 | 14
2018-12-04 11:00 | 20 | 16
2018-12-04 11:30 | 21 | 17
2018-12-04 12:00 | 21 | 18
2018-12-04 12:30 | 21 | 17
2018-12-04 13:00 | 21 | 18
2018-12-04 13:30 | 24 | 21
2018-12-04 14:00 | 24 | 21
2018-12-04 14:30 | 28 | 25
2018-12-04 15:00 | 26 | 24
2018-12-04 15:30 | 47 | 46
2018-12-04 16:00 | 53 | 52
2018-12-04 16:30 | 66 | 65
2018-12-04 17:00 | 74 | 73
2018-12-04 17:30 | 84 | 83
2018-12-04 18:00 | 84 | 83
2018-12-04 18:30 | 82 | 81
2018-12-04 19:00 | 84 | 83
2018-12-04 19:30 | 86 | 83
2018-12-04 20:00 | 87 | 80
2018-12-04 20:30 | 84 | 75
2018-12-04 21:00 | 78 | 74
2018-12-04 21:30 | 75 | 73
2018-12-04 22:00 | 73 | 71
2018-12-04 22:30 | 70 | 68
2018-12-04 23:00 | 68 | 64
2018-12-04 23:30 | 68 | 64
2018-12-05 | 66 | 63
2018-12-05 00:30 | 67 | 65
2018-12-05 01:00 | 65 | 63
2018-12-05 01:30 | 66 | 64
2018-12-05 02:00 | 69 | 67
2018-12-05 02:30 | 69 | 68
2018-12-05 03:00 | 69 | 68
2018-12-05 03:30 | 69 | 68
2018-12-05 04:00 | 69 | 68
2018-12-05 04:30 | 69 | 68
2018-12-05 05:00 | 68 | 67
2018-12-05 05:30 | 68 | 67
2018-12-05 06:00 | 68 | 67
2018-12-05 06:30 | 64 | 63
2018-12-05 07:00 | 61 | 60
2018-12-05 07:30 | 55 | 53
2018-12-05 08:00 | 40 | 38
2018-12-05 08:30 | 19 | 19
2018-12-05 09:00 | 16 | 16
2018-12-05 09:30 | 12 | 11
2018-12-05 10:00 | 17 | 16
2018-12-05 10:30 | 16 | 15
2018-12-05 11:00 | 13 | 12
2018-12-05 11:30 | 16 | 14
2018-12-05 12:00 | 17 | 16
2018-12-05 12:30 | 16 | 15
2018-12-05 13:00 | 18 | 17
2018-12-05 13:30 | 18 | 17
2018-12-05 14:00 | 15 | 13
2018-12-05 14:30 | 18 | 17
2018-12-05 15:00 | 29 | 28
2018-12-05 15:30 | 41 | 40
2018-12-05 16:00 | 38 | 38
2018-12-05 16:30 | 44 | 44
2018-12-05 17:00 | 62 | 62
2018-12-05 17:30 | 67 | 67
2018-12-05 18:00 | 79 | 78
2018-12-05 18:30 | 82 | 77
2018-12-05 19:00 | 82 | 78
2018-12-05 19:30 | 81 | 77
2018-12-05 20:00 | 82 | 78
2018-12-05 20:30 | 80 | 76
2018-12-05 21:00 | 77 | 70
2018-12-05 21:30 | 71 | 67
2018-12-05 22:00 | 67 | 67
2018-12-05 22:30 | 66 | 65
2018-12-05 23:00 | 59 | 58
2018-12-05 23:30 | 57 | 56
2018-12-06 | 57 | 56
2018-12-06 00:30 | 57 | 56
2018-12-06 01:00 | 58 | 56
2018-12-06 01:30 | 60 | 58
2018-12-06 02:00 | 62 | 61
2018-12-06 02:30 | 61 | 60
2018-12-06 03:00 | 63 | 61
2018-12-06 03:30 | 63 | 61
2018-12-06 04:00 | 63 | 61
2018-12-06 04:30 | 62 | 60
2018-12-06 05:00 | 62 | 60
2018-12-06 05:30 | 61 | 59
2018-12-06 06:00 | 62 | 61
2018-12-06 06:30 | 60 | 58
2018-12-06 07:00 | 61 | 60
2018-12-06 07:30 | 46 | 45
2018-12-06 08:00 | 46 | 45
2018-12-06 08:30 | 46 | 46
2018-12-06 09:00 | 41 | 41
2018-12-06 09:30 | 47 | 47
2018-12-06 10:00 | 42 | 41
2018-12-06 10:30 | 38 | 38
2018-12-06 11:00 | 30 | 30
2018-12-06 11:30 | 33 | 31
2018-12-06 12:00 | 33 | 30
2018-12-06 12:30 | 43 | 42
2018-12-06 13:00 | 42 | 41
2018-12-06 13:30 | 28 | 26
2018-12-06 14:00 | 23 | 20
2018-12-06 14:30 | 27 | 24
2018-12-06 15:00 | 27 | 24
2018-12-06 15:30 | 34 | 32
2018-12-06 16:00 | 50 | 49
2018-12-06 16:30 | 60 | 59
2018-12-06 17:00 | 52 | 51
2018-12-06 17:30 | 48 | 48
2018-12-06 18:00 | 55 | 55
2018-12-06 18:30 | 55 | 55
2018-12-06 19:00 | 56 | 56
2018-12-06 19:30 | 56 | 55
2018-12-06 20:00 | 56 | 56
2018-12-06 20:30 | 56 | 55
2018-12-06 21:00 | 55 | 55
2018-12-06 21:30 | 65 | 64
2018-12-06 22:00 | 65 | 64
2018-12-06 22:30 | 64 | 61
2018-12-06 23:00 | 63 | 61
2018-12-06 23:30 | 62 | 61
2018-12-07 | 62 | 61
2018-12-07 00:30 | 61 | 60
2018-12-07 01:00 | 62 | 61
2018-12-07 01:30 | 62 | 61
2018-12-07 02:00 | 62 | 61
2018-12-07 02:30 | 61 | 61
2018-12-07 03:00 | 61 | 61
2018-12-07 03:30 | 60 | 60
2018-12-07 04:00 | 60 | 59
2018-12-07 04:30 | 61 | 60
2018-12-07 05:00 | 60 | 59
2018-12-07 05:30 | 60 | 60
2018-12-07 06:00 | 61 | 60
2018-12-07 06:30 | 61 | 60
2018-12-07 07:00 | 58 | 56
2018-12-07 07:30 | 59 | 58
2018-12-07 08:00 | 58 | 57
2018-12-07 08:30 | 54 | 54
2018-12-07 09:00 | 50 | 50
2018-12-07 09:30 | 43 | 43
2018-12-07 10:00 | 46 | 46
2018-12-07 10:30 | 49 | 48
2018-12-07 11:00 | 38 | 38
2018-12-07 11:30 | 47 | 47
2018-12-07 12:00 | 32 | 32
2018-12-07 12:30 | 28 | 28
2018-12-07 13:00 | 35 | 35
2018-12-07 13:30 | 53 | 52
2018-12-07 14:00 | 56 | 55
2018-12-07 14:30 | 45 | 45
2018-12-07 15:00 | 51 | 50
2018-12-07 15:30 | 57 | 56
2018-12-07 16:00 | 58 | 58
2018-12-07 16:30 | 59 | 58
2018-12-07 17:00 | 58 | 57
2018-12-07 17:30 | 61 | 61
2018-12-07 18:00 | 50 | 48
2018-12-07 18:30 | 52 | 49
2018-12-07 19:00 | 57 | 52
2018-12-07 19:30 | 57 | 53
2018-12-07 20:00 | 56 | 52
2018-12-07 20:30 | 57 | 53
2018-12-07 21:00 | 59 | 55
2018-12-07 21:30 | 67 | 66
2018-12-07 22:00 | 68 | 67
2018-12-07 22:30 | 67 | 66
2018-12-07 23:00 | 65 | 64
2018-12-07 23:30 | 64 | 63
2018-12-08 | 62 | 61
2018-12-08 00:30 | 61 | 60
2018-12-08 01:00 | 60 | 58
2018-12-08 01:30 | 60 | 58
2018-12-08 02:00 | 59 | 57
2018-12-08 02:30 | 59 | 56
2018-12-08 03:00 | 59 | 56
2018-12-08 03:30 | 59 | 56
2018-12-08 04:00 | 58 | 55
2018-12-08 04:30 | 54 | 51
2018-12-08 05:00 | 53 | 50
2018-12-08 05:30 | 52 | 48
2018-12-08 06:00 | 50 | 47
2018-12-08 06:30 | 48 | 44
2018-12-08 07:00 | 46 | 42
2018-12-08 07:30 | 44 | 40
2018-12-08 08:00 | 44 | 40
2018-12-08 08:30 | 43 | 38
2018-12-08 09:00 | 19 | 16
2018-12-08 09:30 | 16 | 16
2018-12-08 10:00 | 9 | 9
2018-12-08 10:30 | 2 | 2
2018-12-08 11:00 | 5 | 5
2018-12-08 11:30 | 9 | 9
2018-12-08 12:00 | 15 | 15
2018-12-08 12:30 | 17 | 17
2018-12-08 13:00 | 20 | 20
2018-12-08 13:30 | 31 | 31
2018-12-08 14:00 | 37 | 37
2018-12-08 14:30 | 44 | 44
2018-12-08 15:00 | 54 | 54
2018-12-08 15:30 | 54 | 54
2018-12-08 16:00 | 51 | 51
2018-12-08 16:30 | 56 | 56
2018-12-08 17:00 | 56 | 56
2018-12-08 17:30 | 60 | 60
2018-12-08 18:00 | 60 | 60
2018-12-08 18:30 | 62 | 62
2018-12-08 19:00 | 63 | 62
2018-12-08 19:30 | 63 | 63
2018-12-08 20:00 | 63 | 62
2018-12-08 20:30 | 62 | 62
2018-12-08 21:00 | 64 | 63
2018-12-08 21:30 | 63 | 63
2018-12-08 22:00 | 64 | 64
2018-12-08 22:30 | 64 | 63
2018-12-08 23:00 | 63 | 62
2018-12-08 23:30 | 63 | 61
2018-12-09 | 61 | 60
2018-12-09 00:30 | 58 | 57
2018-12-09 01:00 | 59 | 57
2018-12-09 01:30 | 58 | 54
2018-12-09 02:00 | 58 | 54
2018-12-09 02:30 | 58 | 54
2018-12-09 03:00 | 57 | 54
2018-12-09 03:30 | 58 | 55
2018-12-09 04:00 | 58 | 55
2018-12-09 04:30 | 58 | 54
2018-12-09 05:00 | 58 | 55
2018-12-09 05:30 | 58 | 56
2018-12-09 06:00 | 58 | 55
2018-12-09 06:30 | 57 | 55
2018-12-09 07:00 | 58 | 56
2018-12-09 07:30 | 57 | 54
2018-12-09 08:00 | 54 | 51
2018-12-09 08:30 | 49 | 46
2018-12-09 09:00 | 42 | 37
2018-12-09 09:30 | 37 | 32
2018-12-09 10:00 | 30 | 24
2018-12-09 10:30 | 38 | 33
2018-12-09 11:00 | 40 | 35
2018-12-09 11:30 | 43 | 38
2018-12-09 12:00 | 39 | 33
2018-12-09 12:30 | 40 | 36
2018-12-09 13:00 | 38 | 34
2018-12-09 13:30 | 26 | 21
2018-12-09 14:00 | 24 | 24
2018-12-09 14:30 | 32 | 32
2018-12-09 15:00 | 33 | 33
2018-12-09 15:30 | 29 | 29
2018-12-09 16:00 | 41 | 41
2018-12-09 16:30 | 43 | 43
2018-12-09 17:00 | 44 | 44
2018-12-09 17:30 | 52 | 52
2018-12-09 18:00 | 56 | 56
2018-12-09 18:30 | 50 | 50
2018-12-09 19:00 | 52 | 52
2018-12-09 19:30 | 53 | 53
2018-12-09 20:00 | 53 | 53
2018-12-09 20:30 | 58 | 58
2018-12-09 21:00 | 59 | 59
2018-12-09 21:30 | 59 | 59
2018-12-09 22:00 | 59 | 59
2018-12-09 22:30 | 59 | 58
2018-12-09 23:00 | 57 | 57
2018-12-09 23:30 | 59 | 59
2018-12-10 | 59 | 59
2018-12-10 00:30 | 58 | 58
2018-12-10 01:00 | 59 | 59
2018-12-10 01:30 | 63 | 63
2018-12-10 02:00 | 63 | 63
2018-12-10 02:30 | 63 | 63
2018-12-10 03:00 | 63 | 63
2018-12-10 03:30 | 63 | 63
2018-12-10 04:00 | 63 | 63
2018-12-10 04:30 | 64 | 64
2018-12-10 05:00 | 64 | 64
2018-12-10 05:30 | 63 | 63
2018-12-10 06:00 | 39 | 39
2018-12-10 06:30 | 0 | 0
2018-12-10 07:00 | 0 | 0
2018-12-10 07:30 | 30 | 30
2018-12-10 08:00 | 46 | 46
2018-12-10 08:30 | 41 | 41
2018-12-10 09:00 | 35 | 35
2018-12-10 09:30 | 36 | 36
2018-12-10 10:00 | 22 | 22
2018-12-10 10:30 | 37 | 37
2018-12-10 11:00 | 34 | 34
2018-12-10 11:30 | 37 | 37
2018-12-10 12:00 | 42 | 42
2018-12-10 12:30 | 41 | 41
2018-12-10 13:00 | 36 | 36
2018-12-10 13:30 | 37 | 37
2018-12-10 14:00 | 41 | 41
2018-12-10 14:30 | 43 | 43
2018-12-10 15:00 | 34 | 34
2018-12-10 15:30 | 31 | 31
2018-12-10 16:00 | 38 | 38
2018-12-10 16:30 | 39 | 39
2018-12-10 17:00 | 44 | 44
2018-12-10 17:30 | 46 | 46
2018-12-10 18:00 | 48 | 48
2018-12-10 18:30 | 56 | 56
2018-12-10 19:00 | 59 | 59
2018-12-10 19:30 | 60 | 60
2018-12-10 20:00 | 60 | 60
2018-12-10 20:30 | 57 | 57
2018-12-10 21:00 | 57 | 56
2018-12-10 21:30 | 57 | 57
2018-12-10 22:00 | 60 | 60
2018-12-10 22:30 | 60 | 60
2018-12-10 23:00 | 60 | 60
2018-12-10 23:30 | 60 | 59
2018-12-11 | 62 | 62
2018-12-11 00:30 | 63 | 63
2018-12-11 01:00 | 64 | 64
2018-12-11 01:30 | 65 | 65
2018-12-11 02:00 | 64 | 64
2018-12-11 02:30 | 65 | 65
2018-12-11 03:00 | 65 | 65
2018-12-11 03:30 | 64 | 64
2018-12-11 04:00 | 64 | 64
2018-12-11 04:30 | 64 | 64
2018-12-11 05:00 | 64 | 64
2018-12-11 05:30 | 63 | 63
2018-12-11 06:00 | 63 | 63
2018-12-11 06:30 | 61 | 61
2018-12-11 07:00 | 58 | 58
2018-12-11 07:30 | 45 | 45
2018-12-11 08:00 | 47 | 47
2018-12-11 08:30 | 31 | 31
2018-12-11 09:00 | 27 | 26
2018-12-11 09:30 | 31 | 31
2018-12-11 10:00 | 31 | 30
2018-12-11 10:30 | 29 | 28
2018-12-11 11:00 | 22 | 21
2018-12-11 11:30 | 22 | 21
2018-12-11 12:00 | 30 | 30
2018-12-11 12:30 | 24 | 24
2018-12-11 13:00 | 13 | 12
2018-12-11 13:30 | 19 | 19
2018-12-11 14:00 | 36 | 36
2018-12-11 14:30 | 34 | 33
2018-12-11 15:00 | 19 | 19
2018-12-11 15:30 | 24 | 24
2018-12-11 16:00 | 29 | 29
2018-12-11 16:30 | 36 | 36
2018-12-11 17:00 | 47 | 47
2018-12-11 17:30 | 44 | 44
2018-12-11 18:00 | 56 | 56
2018-12-11 18:30 | 60 | 60
2018-12-11 19:00 | 63 | 63
2018-12-11 19:30 | 64 | 64
2018-12-11 20:00 | 65 | 64
2018-12-11 20:30 | 70 | 70
2018-12-11 21:00 | 68 | 68
2018-12-11 21:30 | 65 | 65
2018-12-11 22:00 | 67 | 67
2018-12-11 22:30 | 68 | 68
2018-12-11 23:00 | 68 | 67
2018-12-11 23:30 | 68 | 67
2018-12-12 | 67 | 66
2018-12-12 00:30 | 66 | 65
2018-12-12 01:00 | 66 | 65
2018-12-12 01:30 | 65 | 64
2018-12-12 02:00 | 65 | 64
2018-12-12 02:30 | 64 | 64
2018-12-12 03:00 | 65 | 64
2018-12-12 03:30 | 64 | 63
2018-12-12 04:00 | 64 | 63
2018-12-12 04:30 | 64 | 63
2018-12-12 05:00 | 63 | 63
2018-12-12 05:30 | 64 | 64
2018-12-12 06:00 | 64 | 64
2018-12-12 06:30 | 63 | 63
2018-12-12 07:00 | 50 | 50
2018-12-12 07:30 | 56 | 56
2018-12-12 08:00 | 43 | 43
2018-12-12 08:30 | 37 | 37
2018-12-12 09:00 | 43 | 43
2018-12-12 09:30 | 32 | 30
2018-12-12 10:00 | 35 | 33
2018-12-12 10:30 | 26 | 23
2018-12-12 11:00 | 26 | 24
2018-12-12 11:30 | 26 | 25
2018-12-12 12:00 | 24 | 23
2018-12-12 12:30 | 37 | 35
2018-12-12 13:00 | 23 | 16
2018-12-12 13:30 | 20 | 10
2018-12-12 14:00 | 14 | 2
2018-12-12 14:30 | 16 | 7
2018-12-12 15:00 | 17 | 5
2018-12-12 15:30 | 33 | 28
2018-12-12 16:00 | 45 | 41
2018-12-12 16:30 | 50 | 46
2018-12-12 17:00 | 48 | 44
2018-12-12 17:30 | 57 | 54
2018-12-12 18:00 | 68 | 66
2018-12-12 18:30 | 71 | 68
2018-12-12 19:00 | 74 | 71
2018-12-12 19:30 | 75 | 72
2018-12-12 20:00 | 75 | 72
2018-12-12 20:30 | 72 | 69
2018-12-12 21:00 | 68 | 65
2018-12-12 21:30 | 71 | 69
2018-12-12 22:00 | 72 | 70
2018-12-12 22:30 | 69 | 67
2018-12-12 23:00 | 64 | 63
2018-12-12 23:30 | 63 | 62
2018-12-13 | 63 | 62
2018-12-13 00:30 | 62 | 60
2018-12-13 01:00 | 63 | 61
2018-12-13 01:30 | 63 | 60
2018-12-13 02:00 | 63 | 61
2018-12-13 02:30 | 63 | 60
2018-12-13 03:00 | 63 | 60
2018-12-13 03:30 | 63 | 61
2018-12-13 04:00 | 62 | 59
2018-12-13 04:30 | 60 | 56
2018-12-13 05:00 | 57 | 53
2018-12-13 05:30 | 51 | 41
2018-12-13 06:00 | 41 | 31
2018-12-13 06:30 | 26 | 21
2018-12-13 07:00 | 21 | 16
2018-12-13 07:30 | 22 | 18
2018-12-13 08:00 | 9 | 5
2018-12-13 08:30 | 12 | 7
2018-12-13 09:00 | 12 | 8
2018-12-13 09:30 | 13 | 12
2018-12-13 10:00 | 5 | 1
2018-12-13 10:30 | 4 | 0
2018-12-13 11:00 | 5 | 4
2018-12-13 11:30 | 19 | 19
2018-12-13 12:00 | 17 | 17
2018-12-13 12:30 | 15 | 15
2018-12-13 13:00 | 11 | 11
2018-12-13 13:30 | 19 | 19
2018-12-13 14:00 | 18 | 18
2018-12-13 14:30 | 16 | 16
2018-12-13 15:00 | 7 | 2
2018-12-13 15:30 | 22 | 21
2018-12-13 16:00 | 29 | 28
2018-12-13 16:30 | 37 | 35
2018-12-13 17:00 | 40 | 39
2018-12-13 17:30 | 41 | 40
2018-12-13 18:00 | 40 | 40
2018-12-13 18:30 | 41 | 40
2018-12-13 19:00 | 41 | 39
2018-12-13 19:30 | 43 | 41
2018-12-13 20:00 | 43 | 40
2018-12-13 20:30 | 40 | 37
2018-12-13 21:00 | 37 | 34
2018-12-13 21:30 | 37 | 33
2018-12-13 22:00 | 37 | 32
2018-12-13 22:30 | 38 | 31
2018-12-13 23:00 | 39 | 31
2018-12-13 23:30 | 37 | 30
2018-12-14 | 39 | 31
2018-12-14 00:30 | 38 | 31
2018-12-14 01:00 | 38 | 30
2018-12-14 01:30 | 37 | 30
2018-12-14 02:00 | 44 | 41
2018-12-14 02:30 | 47 | 45
2018-12-14 03:00 | 55 | 54
2018-12-14 03:30 | 53 | 53
2018-12-14 04:00 | 55 | 55
2018-12-14 04:30 | 56 | 56
2018-12-14 05:00 | 56 | 56
2018-12-14 05:30 | 58 | 58
2018-12-14 06:00 | 59 | 59
2018-12-14 06:30 | 53 | 53
2018-12-14 07:00 | 52 | 52
2018-12-14 07:30 | 45 | 45
2018-12-14 08:00 | 35 | 35
2018-12-14 08:30 | 25 | 25
2018-12-14 09:00 | 8 | 8
2018-12-14 09:30 | 14 | 14
2018-12-14 10:00 | 14 | 14
2018-12-14 10:30 | 14 | 14
2018-12-14 11:00 | 12 | 12
2018-12-14 11:30 | 14 | 13
2018-12-14 12:00 | 28 | 28
2018-12-14 12:30 | 17 | 17
2018-12-14 13:00 | 19 | 19
2018-12-14 13:30 | 18 | 18
2018-12-14 14:00 | 14 | 14
2018-12-14 14:30 | 19 | 19
2018-12-14 15:00 | 21 | 21
2018-12-14 15:30 | 28 | 28
2018-12-14 16:00 | 16 | 15
2018-12-14 16:30 | 31 | 30
2018-12-14 17:00 | 51 | 50
2018-12-14 17:30 | 58 | 58
2018-12-14 18:00 | 67 | 67
2018-12-14 18:30 | 72 | 72
2018-12-14 19:00 | 74 | 74
2018-12-14 19:30 | 71 | 71
2018-12-14 20:00 | 79 | 79
2018-12-14 20:30 | 74 | 74
2018-12-14 21:00 | 71 | 70
2018-12-14 21:30 | 71 | 70
2018-12-14 22:00 | 70 | 68
2018-12-14 22:30 | 70 | 67
2018-12-14 23:00 | 70 | 67
2018-12-14 23:30 | 69 | 66
2018-12-15 | 69 | 65
2018-12-15 00:30 | 65 | 64
2018-12-15 01:00 | 64 | 64
2018-12-15 01:30 | 63 | 63
2018-12-15 02:00 | 62 | 62
2018-12-15 02:30 | 61 | 61
2018-12-15 03:00 | 61 | 61
2018-12-15 03:30 | 62 | 62
2018-12-15 04:00 | 61 | 61
2018-12-15 04:30 | 62 | 62
2018-12-15 05:00 | 62 | 62
2018-12-15 05:30 | 62 | 62
2018-12-15 06:00 | 62 | 62
2018-12-15 06:30 | 62 | 62
2018-12-15 07:00 | 61 | 61
2018-12-15 07:30 | 61 | 60
2018-12-15 08:00 | 57 | 57
2018-12-15 08:30 | 43 | 43
2018-12-15 09:00 | 36 | 36
2018-12-15 09:30 | 36 | 36
2018-12-15 10:00 | 25 | 24
2018-12-15 10:30 | 29 | 29
2018-12-15 11:00 | 24 | 23
2018-12-15 11:30 | 36 | 36
2018-12-15 12:00 | 28 | 27
2018-12-15 12:30 | 34 | 34
2018-12-15 13:00 | 39 | 39
2018-12-15 13:30 | 48 | 48
2018-12-15 14:00 | 43 | 42
2018-12-15 14:30 | 46 | 45
2018-12-15 15:00 | 55 | 53
2018-12-15 15:30 | 58 | 57
2018-12-15 16:00 | 66 | 65
2018-12-15 16:30 | 64 | 63
2018-12-15 17:00 | 67 | 66
2018-12-15 17:30 | 68 | 66
2018-12-15 18:00 | 69 | 67
2018-12-15 18:30 | 70 | 68
2018-12-15 19:00 | 71 | 69
2018-12-15 19:30 | 73 | 70
2018-12-15 20:00 | 73 | 70
2018-12-15 20:30 | 72 | 69
2018-12-15 21:00 | 71 | 67
2018-12-15 21:30 | 70 | 66
2018-12-15 22:00 | 70 | 66
2018-12-15 22:30 | 69 | 65
2018-12-15 23:00 | 69 | 65
2018-12-15 23:30 | 70 | 66
2018-12-16 | 69 | 65
2018-12-16 00:30 | 66 | 64
2018-12-16 01:00 | 64 | 64
2018-12-16 01:30 | 65 | 65
2018-12-16 02:00 | 65 | 65
2018-12-16 02:30 | 65 | 64
2018-12-16 03:00 | 64 | 64
2018-12-16 03:30 | 64 | 64
2018-12-16 04:00 | 64 | 64
2018-12-16 04:30 | 64 | 64
2018-12-16 05:00 | 65 | 65
2018-12-16 05:30 | 66 | 66
2018-12-16 06:00 | 64 | 64
2018-12-16 06:30 | 64 | 64
2018-12-16 07:00 | 65 | 65
2018-12-16 07:30 | 65 | 65
2018-12-16 08:00 | 65 | 65
2018-12-16 08:30 | 65 | 65
2018-12-16 09:00 | 66 | 66
2018-12-16 09:30 | 65 | 65
2018-12-16 10:00 | 62 | 62
2018-12-16 10:30 | 55 | 55
2018-12-16 11:00 | 47 | 46
2018-12-16 11:30 | 32 | 32
2018-12-16 12:00 | 31 | 30
2018-12-16 12:30 | 27 | 26
2018-12-16 13:00 | 29 | 28
2018-12-16 13:30 | 25 | 24
2018-12-16 14:00 | 26 | 26
2018-12-16 14:30 | 28 | 28
2018-12-16 15:00 | 36 | 36
2018-12-16 15:30 | 31 | 31
2018-12-16 16:00 | 34 | 34
2018-12-16 16:30 | 41 | 41
2018-12-16 17:00 | 49 | 49
2018-12-16 17:30 | 58 | 58
2018-12-16 18:00 | 63 | 63
2018-12-16 18:30 | 65 | 65
2018-12-16 19:00 | 70 | 68
2018-12-16 19:30 | 70 | 68
2018-12-16 20:00 | 67 | 65
2018-12-16 20:30 | 67 | 65
2018-12-16 21:00 | 67 | 64
2018-12-16 21:30 | 67 | 63
2018-12-16 22:00 | 67 | 63
2018-12-16 22:30 | 69 | 65
2018-12-16 23:00 | 69 | 65
2018-12-16 23:30 | 69 | 64
2018-12-17 | 66 | 63
2018-12-17 00:30 | 64 | 61
2018-12-17 01:00 | 65 | 63
2018-12-17 01:30 | 64 | 62
2018-12-17 02:00 | 63 | 62
2018-12-17 02:30 | 62 | 62
2018-12-17 03:00 | 62 | 62
2018-12-17 03:30 | 62 | 62
2018-12-17 04:00 | 62 | 62
2018-12-17 04:30 | 62 | 62
2018-12-17 05:00 | 62 | 62
2018-12-17 05:30 | 62 | 61
2018-12-17 06:00 | 61 | 60
2018-12-17 06:30 | 58 | 58
2018-12-17 07:00 | 55 | 55
2018-12-17 07:30 | 48 | 48
2018-12-17 08:00 | 41 | 40
2018-12-17 08:30 | 35 | 34
2018-12-17 09:00 | 27 | 25
2018-12-17 09:30 | 22 | 19
2018-12-17 10:00 | 18 | 14
2018-12-17 10:30 | 18 | 14
2018-12-17 11:00 | 19 | 16
2018-12-17 11:30 | 22 | 20
2018-12-17 12:00 | 22 | 19
2018-12-17 12:30 | 23 | 18
2018-12-17 13:00 | 25 | 22
2018-12-17 13:30 | 26 | 24
2018-12-17 14:00 | 19 | 15
2018-12-17 14:30 | 18 | 15
2018-12-17 15:00 | 22 | 18
2018-12-17 15:30 | 25 | 23
2018-12-17 16:00 | 29 | 26
2018-12-17 16:30 | 36 | 35
2018-12-17 17:00 | 46 | 45
2018-12-17 17:30 | 53 | 52
2018-12-17 18:00 | 61 | 61
2018-12-17 18:30 | 67 | 66
2018-12-17 19:00 | 71 | 69
2018-12-17 19:30 | 71 | 68
2018-12-17 20:00 | 74 | 72
2018-12-17 20:30 | 77 | 76
2018-12-17 21:00 | 77 | 75
2018-12-17 21:30 | 76 | 75
2018-12-17 22:00 | 75 | 74
2018-12-17 22:30 | 73 | 72
2018-12-17 23:00 | 73 | 71
2018-12-17 23:30 | 72 | 70
2018-12-18 | 69 | 69
2018-12-18 00:30 | 67 | 66
2018-12-18 01:00 | 66 | 66
2018-12-18 01:30 | 65 | 65
2018-12-18 02:00 | 65 | 65
2018-12-18 02:30 | 65 | 65
2018-12-18 03:00 | 65 | 65
2018-12-18 03:30 | 65 | 65
2018-12-18 04:00 | 65 | 65
2018-12-18 04:30 | 65 | 65
2018-12-18 05:00 | 66 | 66
2018-12-18 05:30 | 66 | 66
2018-12-18 06:00 | 65 | 65
2018-12-18 06:30 | 62 | 62
2018-12-18 07:00 | 57 | 57
2018-12-18 07:30 | 52 | 51
2018-12-18 08:00 | 39 | 39
2018-12-18 08:30 | 29 | 28
2018-12-18 09:00 | 24 | 23
2018-12-18 09:30 | 23 | 21
2018-12-18 10:00 | 19 | 17
2018-12-18 10:30 | 16 | 14
2018-12-18 11:00 | 19 | 17
2018-12-18 11:30 | 21 | 17
2018-12-18 12:00 | 24 | 19
2018-12-18 12:30 | 25 | 21
2018-12-18 13:00 | 19 | 11
2018-12-18 13:30 | 18 | 9
2018-12-18 14:00 | 23 | 15
2018-12-18 14:30 | 22 | 20
2018-12-18 15:00 | 23 | 23
2018-12-18 15:30 | 21 | 21
2018-12-18 16:00 | 25 | 18
2018-12-18 16:30 | 30 | 23
2018-12-18 17:00 | 34 | 28
2018-12-18 17:30 | 44 | 39
2018-12-18 18:00 | 53 | 49
2018-12-18 18:30 | 57 | 54
2018-12-18 19:00 | 59 | 54
2018-12-18 19:30 | 63 | 59
2018-12-18 20:00 | 65 | 61
2018-12-18 20:30 | 74 | 73
2018-12-18 21:00 | 75 | 74
2018-12-18 21:30 | 74 | 73
2018-12-18 22:00 | 73 | 72
2018-12-18 22:30 | 65 | 61
2018-12-18 23:00 | 58 | 55
2018-12-18 23:30 | 68 | 68
2018-12-19 | 67 | 67
2018-12-19 00:30 | 66 | 66
2018-12-19 01:00 | 65 | 65
2018-12-19 01:30 | 65 | 65
2018-12-19 02:00 | 64 | 64
2018-12-19 02:30 | 64 | 64
2018-12-19 03:00 | 64 | 64
2018-12-19 03:30 | 64 | 64
2018-12-19 04:00 | 64 | 64
2018-12-19 04:30 | 64 | 63
2018-12-19 05:00 | 63 | 63
2018-12-19 05:30 | 63 | 63
2018-12-19 06:00 | 63 | 63
2018-12-19 06:30 | 49 | 49
2018-12-19 07:00 | 40 | 40
2018-12-19 07:30 | 39 | 39
2018-12-19 08:00 | 36 | 36
2018-12-19 08:30 | 29 | 29
2018-12-19 09:00 | 27 | 26
2018-12-19 09:30 | 16 | 14
2018-12-19 10:00 | 20 | 19
2018-12-19 10:30 | 17 | 16
2018-12-19 11:00 | 21 | 19
2018-12-19 11:30 | 13 | 2
2018-12-19 12:00 | 14 | 9
2018-12-19 12:30 | 15 | 9
2018-12-19 13:00 | 13 | 5
2018-12-19 13:30 | 13 | 5
2018-12-19 14:00 | 15 | 6
2018-12-19 14:30 | 13 | 6
2018-12-19 15:00 | 12 | 6
2018-12-19 15:30 | 8 | 7
2018-12-19 16:00 | 12 | 12
2018-12-19 16:30 | 28 | 28
2018-12-19 17:00 | 40 | 40
2018-12-19 17:30 | 51 | 51
2018-12-19 18:00 | 60 | 59
2018-12-19 18:30 | 66 | 64
2018-12-19 19:00 | 59 | 50
2018-12-19 19:30 | 56 | 43
2018-12-19 20:00 | 62 | 58
2018-12-19 20:30 | 67 | 65
2018-12-19 21:00 | 67 | 64
2018-12-19 21:30 | 71 | 70
2018-12-19 22:00 | 72 | 72
2018-12-19 22:30 | 72 | 71
2018-12-19 23:00 | 69 | 68
2018-12-19 23:30 | 68 | 68
2018-12-20 | 68 | 67
2018-12-20 00:30 | 68 | 67
2018-12-20 01:00 | 68 | 67
2018-12-20 01:30 | 66 | 65
2018-12-20 02:00 | 66 | 65
2018-12-20 02:30 | 66 | 65
2018-12-20 03:00 | 65 | 64
2018-12-20 03:30 | 66 | 65
2018-12-20 04:00 | 65 | 64
2018-12-20 04:30 | 64 | 63
2018-12-20 05:00 | 64 | 63
2018-12-20 05:30 | 64 | 63
2018-12-20 06:00 | 63 | 62
2018-12-20 06:30 | 57 | 56
2018-12-20 07:00 | 47 | 45
2018-12-20 07:30 | 43 | 42
2018-12-20 08:00 | 41 | 39
2018-12-20 08:30 | 28 | 26
2018-12-20 09:00 | 23 | 21
2018-12-20 09:30 | 20 | 17
2018-12-20 10:00 | 18 | 17
2018-12-20 10:30 | 18 | 17
2018-12-20 11:00 | 13 | 9
2018-12-20 11:30 | 12 | 1
2018-12-20 12:00 | 13 | 7
2018-12-20 12:30 | 17 | 13
2018-12-20 13:00 | 20 | 16
2018-12-20 13:30 | 25 | 21
2018-12-20 14:00 | 25 | 21
2018-12-20 14:30 | 30 | 26
2018-12-20 15:00 | 26 | 19
2018-12-20 15:30 | 19 | 2
2018-12-20 16:00 | 26 | 18
2018-12-20 16:30 | 36 | 31
2018-12-20 17:00 | 41 | 36
2018-12-20 17:30 | 49 | 45
2018-12-20 18:00 | 71 | 69
2018-12-20 18:30 | 76 | 74
2018-12-20 19:00 | 78 | 77
2018-12-20 19:30 | 73 | 72
2018-12-20 20:00 | 74 | 72
2018-12-20 20:30 | 74 | 73
2018-12-20 21:00 | 74 | 73
2018-12-20 21:30 | 74 | 73
2018-12-20 22:00 | 73 | 72
2018-12-20 22:30 | 68 | 67
2018-12-20 23:00 | 70 | 69
2018-12-20 23:30 | 69 | 69
2018-12-21 | 69 | 68
2018-12-21 00:30 | 68 | 67
2018-12-21 01:00 | 67 | 66
2018-12-21 01:30 | 66 | 65
2018-12-21 02:00 | 65 | 64
2018-12-21 02:30 | 65 | 64
2018-12-21 03:00 | 64 | 63
2018-12-21 03:30 | 63 | 63
2018-12-21 04:00 | 63 | 63
2018-12-21 04:30 | 63 | 63
2018-12-21 05:00 | 63 | 62
2018-12-21 05:30 | 64 | 63
2018-12-21 06:00 | 63 | 63
2018-12-21 06:30 | 59 | 58
2018-12-21 07:00 | 54 | 53
2018-12-21 07:30 | 46 | 45
2018-12-21 08:00 | 39 | 37
2018-12-21 08:30 | 33 | 30
2018-12-21 09:00 | 28 | 23
2018-12-21 09:30 | 23 | 18
2018-12-21 10:00 | 22 | 15
2018-12-21 10:30 | 26 | 20
2018-12-21 11:00 | 32 | 28
2018-12-21 11:30 | 39 | 36
2018-12-21 12:00 | 36 | 32
2018-12-21 12:30 | 39 | 34
2018-12-21 13:00 | 30 | 25
2018-12-21 13:30 | 25 | 18
2018-12-21 14:00 | 25 | 19
2018-12-21 14:30 | 25 | 20
2018-12-21 15:00 | 28 | 23
2018-12-21 15:30 | 29 | 29
2018-12-21 16:00 | 35 | 35
2018-12-21 16:30 | 37 | 37
2018-12-21 17:00 | 48 | 48
2018-12-21 17:30 | 59 | 59
2018-12-21 18:00 | 69 | 69
2018-12-21 18:30 | 74 | 74
2018-12-21 19:00 | 76 | 76
2018-12-21 19:30 | 77 | 77
2018-12-21 20:00 | 77 | 77
2018-12-21 20:30 | 75 | 75
2018-12-21 21:00 | 74 | 74
2018-12-21 21:30 | 73 | 73
2018-12-21 22:00 | 72 | 71
2018-12-21 22:30 | 71 | 70
2018-12-21 23:00 | 70 | 70
2018-12-21 23:30 | 72 | 71
2018-12-22 | 69 | 68
2018-12-22 00:30 | 67 | 67
2018-12-22 01:00 | 67 | 66
2018-12-22 01:30 | 66 | 66
2018-12-22 02:00 | 66 | 65
2018-12-22 02:30 | 65 | 64
2018-12-22 03:00 | 65 | 64
2018-12-22 03:30 | 65 | 64
2018-12-22 04:00 | 65 | 64
2018-12-22 04:30 | 66 | 65
2018-12-22 05:00 | 66 | 65
2018-12-22 05:30 | 65 | 64
2018-12-22 06:00 | 64 | 63
2018-12-22 06:30 | 61 | 60
2018-12-22 07:00 | 57 | 55
2018-12-22 07:30 | 48 | 47
2018-12-22 08:00 | 46 | 44
2018-12-22 08:30 | 47 | 45
2018-12-22 09:00 | 44 | 42
2018-12-22 09:30 | 38 | 35
2018-12-22 10:00 | 45 | 43
2018-12-22 10:30 | 45 | 44
2018-12-22 11:00 | 54 | 53
2018-12-22 11:30 | 24 | 22
2018-12-22 12:00 | 26 | 24
2018-12-22 12:30 | 48 | 47
2018-12-22 13:00 | 45 | 44
2018-12-22 13:30 | 41 | 40
2018-12-22 14:00 | 32 | 30
2018-12-22 14:30 | 34 | 32
2018-12-22 15:00 | 43 | 41
2018-12-22 15:30 | 38 | 36
2018-12-22 16:00 | 38 | 35
2018-12-22 16:30 | 30 | 25
2018-12-22 17:00 | 33 | 30
2018-12-22 17:30 | 55 | 53
2018-12-22 18:00 | 72 | 71
2018-12-22 18:30 | 77 | 77
2018-12-22 19:00 | 80 | 80
2018-12-22 19:30 | 81 | 81
2018-12-22 20:00 | 81 | 81
2018-12-22 20:30 | 78 | 78
2018-12-22 21:00 | 78 | 78
2018-12-22 21:30 | 77 | 76
2018-12-22 22:00 | 76 | 76
2018-12-22 22:30 | 74 | 74
2018-12-22 23:00 | 74 | 74
2018-12-22 23:30 | 74 | 73
2018-12-23 | 72 | 71
2018-12-23 00:30 | 71 | 70
2018-12-23 01:00 | 71 | 70
2018-12-23 01:30 | 71 | 70
2018-12-23 02:00 | 71 | 70
2018-12-23 02:30 | 71 | 70
2018-12-23 03:00 | 70 | 69
2018-12-23 03:30 | 69 | 68
2018-12-23 04:00 | 69 | 68
2018-12-23 04:30 | 69 | 68
2018-12-23 05:00 | 70 | 69
2018-12-23 05:30 | 69 | 68
2018-12-23 06:00 | 68 | 67
2018-12-23 06:30 | 66 | 64
2018-12-23 07:00 | 60 | 58
2018-12-23 07:30 | 53 | 51
2018-12-23 08:00 | 49 | 46
2018-12-23 08:30 | 54 | 52
2018-12-23 09:00 | 53 | 51
2018-12-23 09:30 | 43 | 40
2018-12-23 10:00 | 34 | 31
2018-12-23 10:30 | 36 | 34
2018-12-23 11:00 | 35 | 33
2018-12-23 11:30 | 28 | 24
2018-12-23 12:00 | 41 | 39
2018-12-23 12:30 | 34 | 31
2018-12-23 13:00 | 34 | 32
2018-12-23 13:30 | 26 | 22
2018-12-23 14:00 | 29 | 25
2018-12-23 14:30 | 33 | 29
2018-12-23 15:00 | 44 | 40
2018-12-23 15:30 | 43 | 40
2018-12-23 16:00 | 45 | 42
2018-12-23 16:30 | 54 | 52
2018-12-23 17:00 | 62 | 60
2018-12-23 17:30 | 70 | 69
2018-12-23 18:00 | 77 | 75
2018-12-23 18:30 | 80 | 79
2018-12-23 19:00 | 81 | 81
2018-12-23 19:30 | 81 | 81
2018-12-23 20:00 | 81 | 81
2018-12-23 20:30 | 80 | 80
2018-12-23 21:00 | 79 | 79
2018-12-23 21:30 | 78 | 78
2018-12-23 22:00 | 77 | 77
2018-12-23 22:30 | 75 | 75
2018-12-23 23:00 | 75 | 74
2018-12-23 23:30 | 75 | 74
2018-12-24 | 74 | 73
2018-12-24 00:30 | 72 | 71
2018-12-24 01:00 | 72 | 70
2018-12-24 01:30 | 72 | 71
2018-12-24 02:00 | 72 | 71
2018-12-24 02:30 | 73 | 72
2018-12-24 03:00 | 74 | 73
2018-12-24 03:30 | 73 | 72
2018-12-24 04:00 | 75 | 73
2018-12-24 04:30 | 75 | 73
2018-12-24 05:00 | 76 | 74
2018-12-24 05:30 | 77 | 75
2018-12-24 06:00 | 77 | 75
2018-12-24 06:30 | 75 | 73
2018-12-24 07:00 | 71 | 69
2018-12-24 07:30 | 69 | 67
2018-12-24 08:00 | 63 | 61
2018-12-24 08:30 | 49 | 46
2018-12-24 09:00 | 41 | 38
2018-12-24 09:30 | 39 | 37
2018-12-24 10:00 | 40 | 37
2018-12-24 10:30 | 31 | 27
2018-12-24 11:00 | 40 | 37
2018-12-24 11:30 | 38 | 35
2018-12-24 12:00 | 36 | 33
2018-12-24 12:30 | 35 | 32
2018-12-24 13:00 | 38 | 36
2018-12-24 13:30 | 34 | 31
2018-12-24 14:00 | 34 | 31
2018-12-24 14:30 | 31 | 28
2018-12-24 15:00 | 38 | 35
2018-12-24 15:30 | 36 | 33
2018-12-24 16:00 | 41 | 38
2018-12-24 16:30 | 41 | 38
2018-12-24 17:00 | 54 | 52
2018-12-24 17:30 | 66 | 64
2018-12-24 18:00 | 72 | 70
2018-12-24 18:30 | 78 | 76
2018-12-24 19:00 | 81 | 81
2018-12-24 19:30 | 82 | 81
2018-12-24 20:00 | 81 | 81
2018-12-24 20:30 | 81 | 80
2018-12-24 21:00 | 81 | 80
2018-12-24 21:30 | 79 | 78
2018-12-24 22:00 | 78 | 77
2018-12-24 22:30 | 79 | 77
2018-12-24 23:00 | 77 | 76
2018-12-24 23:30 | 76 | 75
2018-12-25 | 76 | 74
2018-12-25 00:30 | 75 | 73
2018-12-25 01:00 | 75 | 72
2018-12-25 01:30 | 75 | 72
2018-12-25 02:00 | 73 | 72
2018-12-25 02:30 | 72 | 71
2018-12-25 03:00 | 71 | 71
2018-12-25 03:30 | 71 | 71
2018-12-25 04:00 | 70 | 70
2018-12-25 04:30 | 70 | 70
2018-12-25 05:00 | 70 | 70
2018-12-25 05:30 | 70 | 70
2018-12-25 06:00 | 70 | 70
2018-12-25 06:30 | 67 | 67
2018-12-25 07:00 | 64 | 64
2018-12-25 07:30 | 61 | 61
2018-12-25 08:00 | 43 | 43
2018-12-25 08:30 | 45 | 45
2018-12-25 09:00 | 44 | 44
2018-12-25 09:30 | 32 | 32
2018-12-25 10:00 | 39 | 39
2018-12-25 10:30 | 39 | 39
2018-12-25 11:00 | 41 | 40
2018-12-25 11:30 | 40 | 39
2018-12-25 12:00 | 42 | 41
2018-12-25 12:30 | 43 | 43
2018-12-25 13:00 | 36 | 35
2018-12-25 13:30 | 48 | 48
2018-12-25 14:00 | 44 | 44
2018-12-25 14:30 | 44 | 43
2018-12-25 15:00 | 45 | 44
2018-12-25 15:30 | 50 | 50
2018-12-25 16:00 | 55 | 54
2018-12-25 16:30 | 51 | 50
2018-12-25 17:00 | 62 | 61
2018-12-25 17:30 | 66 | 66
2018-12-25 18:00 | 70 | 70
2018-12-25 18:30 | 74 | 73
2018-12-25 19:00 | 77 | 76
2018-12-25 19:30 | 78 | 77
2018-12-25 20:00 | 79 | 78
2018-12-25 20:30 | 79 | 78
2018-12-25 21:00 | 78 | 77
2018-12-25 21:30 | 78 | 77
2018-12-25 22:00 | 79 | 78
2018-12-25 22:30 | 77 | 76
2018-12-25 23:00 | 75 | 75
2018-12-25 23:30 | 74 | 74
2018-12-26 | 74 | 74
2018-12-26 00:30 | 71 | 71
2018-12-26 01:00 | 72 | 72
2018-12-26 01:30 | 72 | 72
2018-12-26 02:00 | 72 | 72
2018-12-26 02:30 | 72 | 72
2018-12-26 03:00 | 72 | 72
2018-12-26 03:30 | 72 | 71
2018-12-26 04:00 | 71 | 71
2018-12-26 04:30 | 71 | 71
2018-12-26 05:00 | 70 | 70
2018-12-26 05:30 | 72 | 71
2018-12-26 06:00 | 71 | 71
2018-12-26 06:30 | 68 | 67
2018-12-26 07:00 | 65 | 64
2018-12-26 07:30 | 57 | 57
2018-12-26 08:00 | 53 | 52
2018-12-26 08:30 | 42 | 40
2018-12-26 09:00 | 33 | 32
2018-12-26 09:30 | 35 | 34
2018-12-26 10:00 | 30 | 29
2018-12-26 10:30 | 32 | 31
2018-12-26 11:00 | 38 | 37
2018-12-26 11:30 | 36 | 35
2018-12-26 12:00 | 31 | 30
2018-12-26 12:30 | 36 | 35
2018-12-26 13:00 | 49 | 48
2018-12-26 13:30 | 43 | 42
2018-12-26 14:00 | 45 | 44
2018-12-26 14:30 | 44 | 43
2018-12-26 15:00 | 36 | 34
2018-12-26 15:30 | 46 | 44
2018-12-26 16:00 | 47 | 45
2018-12-26 16:30 | 56 | 55
2018-12-26 17:00 | 65 | 64
2018-12-26 17:30 | 68 | 66
2018-12-26 18:00 | 73 | 73
2018-12-26 18:30 | 75 | 75
2018-12-26 19:00 | 81 | 80
2018-12-26 19:30 | 83 | 83
2018-12-26 20:00 | 85 | 84
2018-12-26 20:30 | 85 | 84
2018-12-26 21:00 | 83 | 83
2018-12-26 21:30 | 75 | 72
2018-12-26 22:00 | 82 | 81
2018-12-26 22:30 | 80 | 80
2018-12-26 23:00 | 80 | 80
2018-12-26 23:30 | 80 | 79
2018-12-27 | 79 | 78
2018-12-27 00:30 | 78 | 77
2018-12-27 01:00 | 77 | 77
2018-12-27 01:30 | 78 | 77
2018-12-27 02:00 | 77 | 76
2018-12-27 02:30 | 76 | 75
2018-12-27 03:00 | 76 | 76
2018-12-27 03:30 | 77 | 76
2018-12-27 04:00 | 76 | 75
2018-12-27 04:30 | 76 | 75
2018-12-27 05:00 | 77 | 76
2018-12-27 05:30 | 77 | 76
2018-12-27 06:00 | 75 | 75
2018-12-27 06:30 | 71 | 70
2018-12-27 07:00 | 67 | 67
2018-12-27 07:30 | 60 | 59
2018-12-27 08:00 | 55 | 54
2018-12-27 08:30 | 51 | 50
2018-12-27 09:00 | 49 | 48
2018-12-27 09:30 | 46 | 46
2018-12-27 10:00 | 46 | 46
2018-12-27 10:30 | 45 | 44
2018-12-27 11:00 | 40 | 39
2018-12-27 11:30 | 32 | 32
2018-12-27 12:00 | 32 | 31
2018-12-27 12:30 | 39 | 38
2018-12-27 13:00 | 33 | 32
2018-12-27 13:30 | 29 | 29
2018-12-27 14:00 | 31 | 31
2018-12-27 14:30 | 37 | 36
2018-12-27 15:00 | 36 | 36
2018-12-27 15:30 | 51 | 51
2018-12-27 16:00 | 63 | 62
2018-12-27 16:30 | 61 | 61
2018-12-27 17:00 | 62 | 61
2018-12-27 17:30 | 68 | 68
2018-12-27 18:00 | 66 | 65
2018-12-27 18:30 | 74 | 73
2018-12-27 19:00 | 76 | 76
2018-12-27 19:30 | 85 | 85
2018-12-27 20:00 | 89 | 89
2018-12-27 20:30 | 90 | 90
2018-12-27 21:00 | 89 | 89
2018-12-27 21:30 | 88 | 88
2018-12-27 22:00 | 87 | 87
2018-12-27 22:30 | 86 | 85
2018-12-27 23:00 | 85 | 84
2018-12-27 23:30 | 84 | 84
2018-12-28 | 83 | 82
2018-12-28 00:30 | 82 | 82
2018-12-28 01:00 | 81 | 81
2018-12-28 01:30 | 81 | 81
2018-12-28 02:00 | 81 | 81
2018-12-28 02:30 | 81 | 81
2018-12-28 03:00 | 80 | 80
2018-12-28 03:30 | 79 | 79
2018-12-28 04:00 | 78 | 78
2018-12-28 04:30 | 78 | 78
2018-12-28 05:00 | 78 | 78
2018-12-28 05:30 | 77 | 77
2018-12-28 06:00 | 76 | 76
2018-12-28 06:30 | 74 | 74
2018-12-28 07:00 | 70 | 70
2018-12-28 07:30 | 63 | 63
2018-12-28 08:00 | 56 | 56
2018-12-28 08:30 | 44 | 44
2018-12-28 09:00 | 38 | 38
2018-12-28 09:30 | 45 | 45
2018-12-28 10:00 | 49 | 49
2018-12-28 10:30 | 38 | 38
2018-12-28 11:00 | 35 | 35
2018-12-28 11:30 | 48 | 47
2018-12-28 12:00 | 41 | 40
2018-12-28 12:30 | 38 | 38
2018-12-28 13:00 | 33 | 33
2018-12-28 13:30 | 33 | 32
2018-12-28 14:00 | 36 | 35
2018-12-28 14:30 | 27 | 26
2018-12-28 15:00 | 25 | 25
2018-12-28 15:30 | 28 | 28
2018-12-28 16:00 | 34 | 34
2018-12-28 16:30 | 41 | 41
2018-12-28 17:00 | 53 | 53
2018-12-28 17:30 | 60 | 60
2018-12-28 18:00 | 72 | 72
2018-12-28 18:30 | 76 | 76
2018-12-28 19:00 | 79 | 79
2018-12-28 19:30 | 80 | 80
2018-12-28 20:00 | 79 | 79
2018-12-28 20:30 | 78 | 78
2018-12-28 21:00 | 86 | 85
2018-12-28 21:30 | 88 | 88
2018-12-28 22:00 | 88 | 88
2018-12-28 22:30 | 88 | 87
2018-12-28 23:00 | 84 | 83
2018-12-28 23:30 | 82 | 81
2018-12-29 | 80 | 79
2018-12-29 00:30 | 79 | 79
2018-12-29 01:00 | 80 | 79
2018-12-29 01:30 | 80 | 79
2018-12-29 02:00 | 79 | 79
2018-12-29 02:30 | 79 | 79
2018-12-29 03:00 | 79 | 79
2018-12-29 03:30 | 79 | 79
2018-12-29 04:00 | 78 | 77
2018-12-29 04:30 | 77 | 76
2018-12-29 05:00 | 77 | 76
2018-12-29 05:30 | 77 | 77
2018-12-29 06:00 | 76 | 75
2018-12-29 06:30 | 73 | 73
2018-12-29 07:00 | 67 | 67
2018-12-29 07:30 | 60 | 60
2018-12-29 08:00 | 63 | 63
2018-12-29 08:30 | 53 | 53
2018-12-29 09:00 | 41 | 40
2018-12-29 09:30 | 41 | 41
2018-12-29 10:00 | 44 | 44
2018-12-29 10:30 | 37 | 37
2018-12-29 11:00 | 39 | 38
2018-12-29 11:30 | 40 | 39
2018-12-29 12:00 | 46 | 46
2018-12-29 12:30 | 34 | 33
2018-12-29 13:00 | 42 | 41
2018-12-29 13:30 | 45 | 44
2018-12-29 14:00 | 42 | 42
2018-12-29 14:30 | 38 | 38
2018-12-29 15:00 | 46 | 46
2018-12-29 15:30 | 55 | 55
2018-12-29 16:00 | 51 | 51
2018-12-29 16:30 | 64 | 64
2018-12-29 17:00 | 67 | 67
2018-12-29 17:30 | 75 | 75
2018-12-29 18:00 | 78 | 78
2018-12-29 18:30 | 82 | 82
2018-12-29 19:00 | 85 | 85
2018-12-29 19:30 | 88 | 87
2018-12-29 20:00 | 88 | 87
2018-12-29 20:30 | 87 | 86
2018-12-29 21:00 | 86 | 85
2018-12-29 21:30 | 86 | 84
2018-12-29 22:00 | 86 | 84
2018-12-29 22:30 | 82 | 80
2018-12-29 23:00 | 70 | 70
2018-12-29 23:30 | 68 | 67
2018-12-30 | 68 | 68
2018-12-30 00:30 | 68 | 67
2018-12-30 01:00 | 68 | 67
2018-12-30 01:30 | 67 | 67
2018-12-30 02:00 | 72 | 72
2018-12-30 02:30 | 78 | 78
2018-12-30 03:00 | 78 | 78
2018-12-30 03:30 | 78 | 78
2018-12-30 04:00 | 77 | 77
2018-12-30 04:30 | 77 | 77
2018-12-30 05:00 | 77 | 77
2018-12-30 05:30 | 77 | 77
2018-12-30 06:00 | 76 | 76
2018-12-30 06:30 | 74 | 73
2018-12-30 07:00 | 68 | 68
2018-12-30 07:30 | 63 | 63
2018-12-30 08:00 | 54 | 54
2018-12-30 08:30 | 50 | 50
2018-12-30 09:00 | 43 | 43
2018-12-30 09:30 | 41 | 41
2018-12-30 10:00 | 35 | 35
2018-12-30 10:30 | 45 | 45
2018-12-30 11:00 | 38 | 38
2018-12-30 11:30 | 37 | 37
2018-12-30 12:00 | 34 | 34
2018-12-30 12:30 | 38 | 38
2018-12-30 13:00 | 37 | 37
2018-12-30 13:30 | 29 | 29
2018-12-30 14:00 | 29 | 29
2018-12-30 14:30 | 31 | 31
2018-12-30 15:00 | 32 | 32
2018-12-30 15:30 | 34 | 34
2018-12-30 16:00 | 46 | 46
2018-12-30 16:30 | 52 | 52
2018-12-30 17:00 | 50 | 50
2018-12-30 17:30 | 60 | 60
2018-12-30 18:00 | 69 | 69
2018-12-30 18:30 | 74 | 74
2018-12-30 19:00 | 78 | 78
2018-12-30 19:30 | 88 | 88
2018-12-30 20:00 | 92 | 92
2018-12-30 20:30 | 86 | 86
2018-12-30 21:00 | 86 | 85
2018-12-30 21:30 | 86 | 85
2018-12-30 22:00 | 86 | 85
2018-12-30 22:30 | 85 | 83
2018-12-30 23:00 | 84 | 83
2018-12-30 23:30 | 83 | 81
2018-12-31 | 82 | 81
2018-12-31 00:30 | 82 | 80
2018-12-31 01:00 | 82 | 80
2018-12-31 01:30 | 81 | 79
2018-12-31 02:00 | 81 | 78
2018-12-31 02:30 | 81 | 79
2018-12-31 03:00 | 80 | 77
2018-12-31 03:30 | 80 | 78
2018-12-31 04:00 | 78 | 78
2018-12-31 04:30 | 78 | 77
2018-12-31 05:00 | 78 | 77
2018-12-31 05:30 | 78 | 77
2018-12-31 06:00 | 76 | 75
2018-12-31 06:30 | 71 | 70
2018-12-31 07:00 | 67 | 66
2018-12-31 07:30 | 67 | 66
2018-12-31 08:00 | 62 | 61
2018-12-31 08:30 | 62 | 61
2018-12-31 09:00 | 57 | 57
2018-12-31 09:30 | 50 | 50
2018-12-31 10:00 | 51 | 50
2018-12-31 10:30 | 49 | 49
2018-12-31 11:00 | 36 | 35
2018-12-31 11:30 | 35 | 34
2018-12-31 12:00 | 31 | 29
2018-12-31 12:30 | 28 | 26
2018-12-31 13:00 | 34 | 33
2018-12-31 13:30 | 29 | 27
2018-12-31 14:00 | 37 | 35
2018-12-31 14:30 | 42 | 41
2018-12-31 15:00 | 29 | 28
2018-12-31 15:30 | 40 | 39
2018-12-31 16:00 | 42 | 41
2018-12-31 16:30 | 51 | 50
2018-12-31 17:00 | 56 | 55
2018-12-31 17:30 | 55 | 54
2018-12-31 18:00 | 64 | 63
2018-12-31 18:30 | 67 | 66
2018-12-31 19:00 | 70 | 70
2018-12-31 19:30 | 71 | 71
2018-12-31 20:00 | 72 | 72
2018-12-31 20:30 | 75 | 74
2018-12-31 21:00 | 73 | 73
2018-12-31 21:30 | 77 | 76
2018-12-31 22:00 | 77 | 77
2018-12-31 22:30 | 77 | 76
2018-12-31 23:00 | 76 | 75
2018-12-31 23:30 | 75 | 75
2019-01-01 | 76 | 76
2019-01-01 00:30 | 76 | 76
2019-01-01 01:00 | 77 | 76
2019-01-01 01:30 | 78 | 77
2019-01-01 02:00 | 77 | 77
2019-01-01 02:30 | 77 | 76
2019-01-01 03:00 | 76 | 76
2019-01-01 03:30 | 76 | 76
2019-01-01 04:00 | 75 | 75
2019-01-01 04:30 | 76 | 75
2019-01-01 05:00 | 76 | 75
2019-01-01 05:30 | 75 | 75
2019-01-01 06:00 | 74 | 74
2019-01-01 06:30 | 72 | 72
2019-01-01 07:00 | 69 | 69
2019-01-01 07:30 | 61 | 61
2019-01-01 08:00 | 57 | 56
2019-01-01 08:30 | 54 | 54
2019-01-01 09:00 | 40 | 39
2019-01-01 09:30 | 41 | 41
2019-01-01 10:00 | 42 | 42
2019-01-01 10:30 | 46 | 45
2019-01-01 11:00 | 42 | 41
2019-01-01 11:30 | 40 | 39
2019-01-01 12:00 | 41 | 40
2019-01-01 12:30 | 31 | 30
2019-01-01 13:00 | 33 | 33
2019-01-01 13:30 | 31 | 30
2019-01-01 14:00 | 32 | 31
2019-01-01 14:30 | 31 | 30
2019-01-01 15:00 | 34 | 33
2019-01-01 15:30 | 34 | 33
2019-01-01 16:00 | 40 | 40
2019-01-01 16:30 | 48 | 48
2019-01-01 17:00 | 60 | 60
2019-01-01 17:30 | 67 | 67
2019-01-01 18:00 | 71 | 71
2019-01-01 18:30 | 74 | 74
2019-01-01 19:00 | 76 | 75
2019-01-01 19:30 | 77 | 76
2019-01-01 20:00 | 77 | 76
2019-01-01 20:30 | 81 | 80
2019-01-01 21:00 | 83 | 83
2019-01-01 21:30 | 83 | 82
2019-01-01 22:00 | 82 | 81
2019-01-01 22:30 | 81 | 80
2019-01-01 23:00 | 80 | 79
2019-01-01 23:30 | 79 | 78
2019-01-02 | 78 | 77
2019-01-02 00:30 | 77 | 76
2019-01-02 01:00 | 77 | 76
2019-01-02 01:30 | 76 | 75
2019-01-02 02:00 | 76 | 75
2019-01-02 02:30 | 76 | 75
2019-01-02 03:00 | 76 | 74
2019-01-02 03:30 | 76 | 75
2019-01-02 04:00 | 76 | 75
2019-01-02 04:30 | 76 | 74
2019-01-02 05:00 | 76 | 74
2019-01-02 05:30 | 76 | 74
2019-01-02 06:00 | 77 | 75
2019-01-02 06:30 | 75 | 72
2019-01-02 07:00 | 73 | 70
2019-01-02 07:30 | 69 | 66
2019-01-02 08:00 | 58 | 56
2019-01-02 08:30 | 49 | 47
2019-01-02 09:00 | 43 | 40
2019-01-02 09:30 | 37 | 34
2019-01-02 10:00 | 32 | 27
2019-01-02 10:30 | 30 | 24
2019-01-02 11:00 | 23 | 13
2019-01-02 11:30 | 26 | 18
2019-01-02 12:00 | 33 | 27
2019-01-02 12:30 | 31 | 24
2019-01-02 13:00 | 24 | 15
2019-01-02 13:30 | 29 | 21
2019-01-02 14:00 | 31 | 23
2019-01-02 14:30 | 45 | 40
2019-01-02 15:00 | 44 | 39
2019-01-02 15:30 | 39 | 34
2019-01-02 16:00 | 46 | 43
2019-01-02 16:30 | 47 | 43
2019-01-02 17:00 | 57 | 53
2019-01-02 17:30 | 68 | 65
2019-01-02 18:00 | 72 | 69
2019-01-02 18:30 | 76 | 73
2019-01-02 19:00 | 77 | 75
2019-01-02 19:30 | 83 | 83
2019-01-02 20:00 | 89 | 88
2019-01-02 20:30 | 89 | 89
2019-01-02 21:00 | 87 | 87
2019-01-02 21:30 | 85 | 85
2019-01-02 22:00 | 81 | 81
2019-01-02 22:30 | 80 | 80
2019-01-02 23:00 | 79 | 79
2019-01-02 23:30 | 79 | 79
2019-01-03 | 80 | 79
2019-01-03 00:30 | 77 | 76
2019-01-03 01:00 | 77 | 76
2019-01-03 01:30 | 74 | 73
2019-01-03 02:00 | 66 | 66
2019-01-03 02:30 | 64 | 64
2019-01-03 03:00 | 59 | 59
2019-01-03 03:30 | 58 | 57
2019-01-03 04:00 | 57 | 57
2019-01-03 04:30 | 58 | 58
2019-01-03 05:00 | 54 | 54
2019-01-03 05:30 | 53 | 53
2019-01-03 06:00 | 52 | 52
2019-01-03 06:30 | 50 | 50
2019-01-03 07:00 | 47 | 47
2019-01-03 07:30 | 46 | 46
2019-01-03 08:00 | 40 | 40
2019-01-03 08:30 | 30 | 30
2019-01-03 09:00 | 23 | 23
2019-01-03 09:30 | 19 | 18
2019-01-03 10:00 | 16 | 16
2019-01-03 10:30 | 14 | 13
2019-01-03 11:00 | 13 | 13
2019-01-03 11:30 | 15 | 15
2019-01-03 12:00 | 18 | 17
2019-01-03 12:30 | 30 | 30
2019-01-03 13:00 | 26 | 26
2019-01-03 13:30 | 29 | 29
2019-01-03 14:00 | 31 | 30
2019-01-03 14:30 | 16 | 16
2019-01-03 15:00 | 24 | 23
2019-01-03 15:30 | 30 | 29
2019-01-03 16:00 | 25 | 24
2019-01-03 16:30 | 34 | 33
2019-01-03 17:00 | 44 | 43
2019-01-03 17:30 | 54 | 53
2019-01-03 18:00 | 63 | 63
2019-01-03 18:30 | 70 | 70
2019-01-03 19:00 | 69 | 69
2019-01-03 19:30 | 71 | 71
2019-01-03 20:00 | 68 | 68
2019-01-03 20:30 | 71 | 71
2019-01-03 21:00 | 78 | 78
2019-01-03 21:30 | 82 | 82
2019-01-03 22:00 | 81 | 81
2019-01-03 22:30 | 80 | 80
2019-01-03 23:00 | 79 | 78
2019-01-03 23:30 | 78 | 78
2019-01-04 | 77 | 76
2019-01-04 00:30 | 75 | 74
2019-01-04 01:00 | 74 | 74
2019-01-04 01:30 | 74 | 74
2019-01-04 02:00 | 74 | 73
2019-01-04 02:30 | 73 | 73
2019-01-04 03:00 | 73 | 73
2019-01-04 03:30 | 73 | 72
2019-01-04 04:00 | 72 | 72
2019-01-04 04:30 | 72 | 71
2019-01-04 05:00 | 70 | 70
2019-01-04 05:30 | 72 | 71
2019-01-04 06:00 | 71 | 70
2019-01-04 06:30 | 69 | 69
2019-01-04 07:00 | 65 | 65
2019-01-04 07:30 | 59 | 59
2019-01-04 08:00 | 53 | 53
2019-01-04 08:30 | 48 | 48
2019-01-04 09:00 | 62 | 62
2019-01-04 09:30 | 56 | 56
2019-01-04 10:00 | 52 | 52
2019-01-04 10:30 | 49 | 49
2019-01-04 11:00 | 43 | 43
2019-01-04 11:30 | 44 | 44
2019-01-04 12:00 | 54 | 54
2019-01-04 12:30 | 34 | 33
2019-01-04 13:00 | 34 | 34
2019-01-04 13:30 | 33 | 33
2019-01-04 14:00 | 26 | 25
2019-01-04 14:30 | 18 | 18
2019-01-04 15:00 | 22 | 22
2019-01-04 15:30 | 25 | 25
2019-01-04 16:00 | 41 | 41
2019-01-04 16:30 | 57 | 57
2019-01-04 17:00 | 55 | 55
2019-01-04 17:30 | 68 | 68
2019-01-04 18:00 | 79 | 79
2019-01-04 18:30 | 83 | 83
2019-01-04 19:00 | 77 | 77
2019-01-04 19:30 | 75 | 75
2019-01-04 20:00 | 81 | 81
2019-01-04 20:30 | 75 | 75
2019-01-04 21:00 | 79 | 79
2019-01-04 21:30 | 83 | 83
2019-01-04 22:00 | 82 | 82
2019-01-04 22:30 | 81 | 81
2019-01-04 23:00 | 80 | 80
2019-01-04 23:30 | 78 | 78
2019-01-05 | 76 | 76
2019-01-05 00:30 | 76 | 75
2019-01-05 01:00 | 74 | 74
2019-01-05 01:30 | 75 | 74
2019-01-05 02:00 | 74 | 74
2019-01-05 02:30 | 73 | 73
2019-01-05 03:00 | 73 | 73
2019-01-05 03:30 | 73 | 72
2019-01-05 04:00 | 73 | 72
2019-01-05 04:30 | 72 | 72
2019-01-05 05:00 | 71 | 71
2019-01-05 05:30 | 71 | 70
2019-01-05 06:00 | 69 | 68
2019-01-05 06:30 | 65 | 65
2019-01-05 07:00 | 58 | 58
2019-01-05 07:30 | 51 | 51
2019-01-05 08:00 | 45 | 45
2019-01-05 08:30 | 43 | 42
2019-01-05 09:00 | 43 | 42
2019-01-05 09:30 | 38 | 38
2019-01-05 10:00 | 46 | 46
2019-01-05 10:30 | 39 | 39
2019-01-05 11:00 | 43 | 42
2019-01-05 11:30 | 52 | 52
2019-01-05 12:00 | 45 | 45
2019-01-05 12:30 | 42 | 41
2019-01-05 13:00 | 39 | 39
2019-01-05 13:30 | 25 | 24
2019-01-05 14:00 | 46 | 45
2019-01-05 14:30 | 40 | 40
2019-01-05 15:00 | 35 | 35
2019-01-05 15:30 | 33 | 33
2019-01-05 16:00 | 37 | 36
2019-01-05 16:30 | 44 | 44
2019-01-05 17:00 | 50 | 50
2019-01-05 17:30 | 67 | 67
2019-01-05 18:00 | 74 | 74
2019-01-05 18:30 | 70 | 69
2019-01-05 19:00 | 71 | 69
2019-01-05 19:30 | 73 | 71
2019-01-05 20:00 | 74 | 72
2019-01-05 20:30 | 73 | 71
2019-01-05 21:00 | 72 | 70
2019-01-05 21:30 | 72 | 70
2019-01-05 22:00 | 71 | 68
2019-01-05 22:30 | 75 | 73
2019-01-05 23:00 | 73 | 71
2019-01-05 23:30 | 72 | 70
2019-01-06 | 71 | 70
2019-01-06 00:30 | 72 | 70
2019-01-06 01:00 | 77 | 76
2019-01-06 01:30 | 75 | 75
2019-01-06 02:00 | 74 | 73
2019-01-06 02:30 | 73 | 72
2019-01-06 03:00 | 72 | 71
2019-01-06 03:30 | 71 | 70
2019-01-06 04:00 | 70 | 69
2019-01-06 04:30 | 70 | 69
2019-01-06 05:00 | 70 | 69
2019-01-06 05:30 | 71 | 70
2019-01-06 06:00 | 69 | 68
2019-01-06 06:30 | 67 | 65
2019-01-06 07:00 | 64 | 62
2019-01-06 07:30 | 60 | 58
2019-01-06 08:00 | 55 | 53
2019-01-06 08:30 | 50 | 48
2019-01-06 09:00 | 51 | 49
2019-01-06 09:30 | 36 | 36
2019-01-06 10:00 | 34 | 34
2019-01-06 10:30 | 33 | 32
2019-01-06 11:00 | 34 | 33
2019-01-06 11:30 | 32 | 32
2019-01-06 12:00 | 40 | 39
2019-01-06 12:30 | 28 | 27
2019-01-06 13:00 | 32 | 31
2019-01-06 13:30 | 42 | 41
2019-01-06 14:00 | 30 | 29
2019-01-06 14:30 | 29 | 27
2019-01-06 15:00 | 32 | 30
2019-01-06 15:30 | 35 | 33
2019-01-06 16:00 | 41 | 40
2019-01-06 16:30 | 48 | 47
2019-01-06 17:00 | 56 | 56
2019-01-06 17:30 | 64 | 63
2019-01-06 18:00 | 72 | 72
2019-01-06 18:30 | 78 | 78
2019-01-06 19:00 | 81 | 81
2019-01-06 19:30 | 83 | 83
2019-01-06 20:00 | 82 | 82
2019-01-06 20:30 | 82 | 82
2019-01-06 21:00 | 80 | 80
2019-01-06 21:30 | 79 | 79
2019-01-06 22:00 | 76 | 76
2019-01-06 22:30 | 65 | 65
2019-01-06 23:00 | 64 | 64
2019-01-06 23:30 | 64 | 64
2019-01-07 | 63 | 63
2019-01-07 00:30 | 63 | 63
2019-01-07 01:00 | 62 | 62
2019-01-07 01:30 | 61 | 61
2019-01-07 02:00 | 61 | 61
2019-01-07 02:30 | 61 | 61
2019-01-07 03:00 | 61 | 61
2019-01-07 03:30 | 61 | 61
2019-01-07 04:00 | 60 | 60
2019-01-07 04:30 | 60 | 60
2019-01-07 05:00 | 60 | 60
2019-01-07 05:30 | 61 | 61
2019-01-07 06:00 | 60 | 60
2019-01-07 06:30 | 63 | 63
2019-01-07 07:00 | 66 | 66
2019-01-07 07:30 | 61 | 61
2019-01-07 08:00 | 55 | 55
2019-01-07 08:30 | 47 | 47
2019-01-07 09:00 | 48 | 46
2019-01-07 09:30 | 49 | 47
2019-01-07 10:00 | 36 | 33
2019-01-07 10:30 | 42 | 39
2019-01-07 11:00 | 45 | 43
2019-01-07 11:30 | 44 | 42
2019-01-07 12:00 | 44 | 41
2019-01-07 12:30 | 44 | 43
2019-01-07 13:00 | 37 | 34
2019-01-07 13:30 | 29 | 26
2019-01-07 14:00 | 35 | 32
2019-01-07 14:30 | 36 | 34
2019-01-07 15:00 | 33 | 30
2019-01-07 15:30 | 25 | 18
2019-01-07 16:00 | 31 | 24
2019-01-07 16:30 | 46 | 41
2019-01-07 17:00 | 52 | 48
2019-01-07 17:30 | 58 | 53
2019-01-07 18:00 | 67 | 63
2019-01-07 18:30 | 69 | 65
2019-01-07 19:00 | 74 | 70
2019-01-07 19:30 | 75 | 72
2019-01-07 20:00 | 74 | 72
2019-01-07 20:30 | 71 | 69
2019-01-07 21:00 | 67 | 64
2019-01-07 21:30 | 67 | 66
2019-01-07 22:00 | 69 | 68
2019-01-07 22:30 | 73 | 73
2019-01-07 23:00 | 71 | 71
2019-01-07 23:30 | 68 | 68
2019-01-08 | 67 | 67
2019-01-08 00:30 | 66 | 66
2019-01-08 01:00 | 66 | 65
2019-01-08 01:30 | 67 | 66
2019-01-08 02:00 | 66 | 65
2019-01-08 02:30 | 66 | 65
2019-01-08 03:00 | 65 | 65
2019-01-08 03:30 | 66 | 65
2019-01-08 04:00 | 65 | 65
2019-01-08 04:30 | 64 | 64
2019-01-08 05:00 | 65 | 65
2019-01-08 05:30 | 67 | 66
2019-01-08 06:00 | 66 | 65
2019-01-08 06:30 | 65 | 64
2019-01-08 07:00 | 64 | 63
2019-01-08 07:30 | 61 | 59
2019-01-08 08:00 | 53 | 51
2019-01-08 08:30 | 45 | 43
2019-01-08 09:00 | 29 | 25
2019-01-08 09:30 | 23 | 18
2019-01-08 10:00 | 16 | 8
2019-01-08 10:30 | 22 | 18
2019-01-08 11:00 | 28 | 26
2019-01-08 11:30 | 32 | 30
2019-01-08 12:00 | 25 | 23
2019-01-08 12:30 | 28 | 26
2019-01-08 13:00 | 36 | 35
2019-01-08 13:30 | 31 | 29
2019-01-08 14:00 | 21 | 19
2019-01-08 14:30 | 23 | 20
2019-01-08 15:00 | 24 | 21
2019-01-08 15:30 | 30 | 25
2019-01-08 16:00 | 36 | 32
2019-01-08 16:30 | 40 | 36
2019-01-08 17:00 | 49 | 46
2019-01-08 17:30 | 55 | 53
2019-01-08 18:00 | 62 | 59
2019-01-08 18:30 | 68 | 65
2019-01-08 19:00 | 71 | 67
2019-01-08 19:30 | 74 | 70
2019-01-08 20:00 | 74 | 70
2019-01-08 20:30 | 73 | 69
2019-01-08 21:00 | 73 | 69
2019-01-08 21:30 | 81 | 80
2019-01-08 22:00 | 76 | 75
2019-01-08 22:30 | 73 | 72
2019-01-08 23:00 | 71 | 70
2019-01-08 23:30 | 71 | 68
2019-01-09 | 71 | 69
2019-01-09 00:30 | 70 | 68
2019-01-09 01:00 | 70 | 68
2019-01-09 01:30 | 68 | 67
2019-01-09 02:00 | 67 | 66
2019-01-09 02:30 | 67 | 66
2019-01-09 03:00 | 67 | 66
2019-01-09 03:30 | 67 | 66
2019-01-09 04:00 | 67 | 66
2019-01-09 04:30 | 67 | 66
2019-01-09 05:00 | 67 | 65
2019-01-09 05:30 | 68 | 66
2019-01-09 06:00 | 67 | 66
2019-01-09 06:30 | 66 | 64
2019-01-09 07:00 | 63 | 61
2019-01-09 07:30 | 54 | 53
2019-01-09 08:00 | 43 | 42
2019-01-09 08:30 | 41 | 40
2019-01-09 09:00 | 40 | 39
2019-01-09 09:30 | 33 | 32
2019-01-09 10:00 | 27 | 26
2019-01-09 10:30 | 33 | 32
2019-01-09 11:00 | 34 | 33
2019-01-09 11:30 | 31 | 30
2019-01-09 12:00 | 34 | 33
2019-01-09 12:30 | 41 | 40
2019-01-09 13:00 | 41 | 39
2019-01-09 13:30 | 45 | 43
2019-01-09 14:00 | 37 | 36
2019-01-09 14:30 | 50 | 48
2019-01-09 15:00 | 50 | 49
2019-01-09 15:30 | 51 | 49
2019-01-09 16:00 | 55 | 53
2019-01-09 16:30 | 56 | 54
2019-01-09 17:00 | 57 | 55
2019-01-09 17:30 | 55 | 52
2019-01-09 18:00 | 61 | 59
2019-01-09 18:30 | 66 | 64
2019-01-09 19:00 | 69 | 65
2019-01-09 19:30 | 69 | 65
2019-01-09 20:00 | 68 | 64
2019-01-09 20:30 | 68 | 63
2019-01-09 21:00 | 66 | 62
2019-01-09 21:30 | 65 | 60
2019-01-09 22:00 | 72 | 70
2019-01-09 22:30 | 71 | 69
2019-01-09 23:00 | 68 | 68
2019-01-09 23:30 | 67 | 66
2019-01-10 | 68 | 67
2019-01-10 00:30 | 68 | 68
2019-01-10 01:00 | 68 | 68
2019-01-10 01:30 | 68 | 67
2019-01-10 02:00 | 68 | 68
2019-01-10 02:30 | 68 | 67
2019-01-10 03:00 | 68 | 67
2019-01-10 03:30 | 68 | 66
2019-01-10 04:00 | 68 | 67
2019-01-10 04:30 | 68 | 67
2019-01-10 05:00 | 69 | 68
2019-01-10 05:30 | 70 | 69
2019-01-10 06:00 | 69 | 68
2019-01-10 06:30 | 68 | 67
2019-01-10 07:00 | 69 | 68
2019-01-10 07:30 | 70 | 69
2019-01-10 08:00 | 71 | 70
2019-01-10 08:30 | 71 | 70
2019-01-10 09:00 | 68 | 67
2019-01-10 09:30 | 63 | 62
2019-01-10 10:00 | 62 | 61
2019-01-10 10:30 | 61 | 60
2019-01-10 11:00 | 60 | 59
2019-01-10 11:30 | 50 | 49
2019-01-10 12:00 | 47 | 45
2019-01-10 12:30 | 49 | 48
2019-01-10 13:00 | 39 | 37
2019-01-10 13:30 | 38 | 36
2019-01-10 14:00 | 35 | 33
2019-01-10 14:30 | 34 | 32
2019-01-10 15:00 | 34 | 30
2019-01-10 15:30 | 33 | 29
2019-01-10 16:00 | 35 | 32
2019-01-10 16:30 | 50 | 47
2019-01-10 17:00 | 52 | 49
2019-01-10 17:30 | 47 | 44
2019-01-10 18:00 | 46 | 43
2019-01-10 18:30 | 49 | 46
2019-01-10 19:00 | 58 | 50
2019-01-10 19:30 | 59 | 51
2019-01-10 20:00 | 64 | 60
2019-01-10 20:30 | 68 | 65
2019-01-10 21:00 | 69 | 66
2019-01-10 21:30 | 69 | 66
2019-01-10 22:00 | 69 | 66
2019-01-10 22:30 | 70 | 67
2019-01-10 23:00 | 70 | 67
2019-01-10 23:30 | 69 | 66
2019-01-11 | 68 | 65
2019-01-11 00:30 | 66 | 63
2019-01-11 01:00 | 66 | 63
2019-01-11 01:30 | 66 | 63
2019-01-11 02:00 | 66 | 63
2019-01-11 02:30 | 66 | 62
2019-01-11 03:00 | 66 | 62
2019-01-11 03:30 | 67 | 63
2019-01-11 04:00 | 67 | 63
2019-01-11 04:30 | 67 | 63
2019-01-11 05:00 | 68 | 63
2019-01-11 05:30 | 68 | 64
2019-01-11 06:00 | 68 | 64
2019-01-11 06:30 | 67 | 63
2019-01-11 07:00 | 62 | 57
2019-01-11 07:30 | 61 | 56
2019-01-11 08:00 | 53 | 48
2019-01-11 08:30 | 43 | 39
2019-01-11 09:00 | 33 | 29
2019-01-11 09:30 | 37 | 33
2019-01-11 10:00 | 36 | 32
2019-01-11 10:30 | 29 | 24
2019-01-11 11:00 | 27 | 20
2019-01-11 11:30 | 32 | 26
2019-01-11 12:00 | 29 | 23
2019-01-11 12:30 | 40 | 35
2019-01-11 13:00 | 25 | 18
2019-01-11 13:30 | 25 | 14
2019-01-11 14:00 | 25 | 14
2019-01-11 14:30 | 24 | 13
2019-01-11 15:00 | 26 | 17
2019-01-11 15:30 | 43 | 37
2019-01-11 16:00 | 39 | 32
2019-01-11 16:30 | 43 | 37
2019-01-11 17:00 | 49 | 44
2019-01-11 17:30 | 56 | 52
2019-01-11 18:00 | 58 | 53
2019-01-11 18:30 | 65 | 61
2019-01-11 19:00 | 71 | 67
2019-01-11 19:30 | 71 | 67
2019-01-11 20:00 | 73 | 70
2019-01-11 20:30 | 73 | 71
2019-01-11 21:00 | 77 | 75
2019-01-11 21:30 | 77 | 75
2019-01-11 22:00 | 73 | 71
2019-01-11 22:30 | 70 | 68
2019-01-11 23:00 | 69 | 67
2019-01-11 23:30 | 70 | 68
2019-01-12 | 70 | 67
2019-01-12 00:30 | 69 | 64
2019-01-12 01:00 | 69 | 64
2019-01-12 01:30 | 68 | 64
2019-01-12 02:00 | 69 | 65
2019-01-12 02:30 | 68 | 64
2019-01-12 03:00 | 68 | 63
2019-01-12 03:30 | 67 | 63
2019-01-12 04:00 | 67 | 62
2019-01-12 04:30 | 68 | 64
2019-01-12 05:00 | 68 | 64
2019-01-12 05:30 | 69 | 65
2019-01-12 06:00 | 68 | 64
2019-01-12 06:30 | 66 | 62
2019-01-12 07:00 | 59 | 55
2019-01-12 07:30 | 51 | 47
2019-01-12 08:00 | 51 | 46
2019-01-12 08:30 | 45 | 39
2019-01-12 09:00 | 34 | 25
2019-01-12 09:30 | 30 | 20
2019-01-12 10:00 | 37 | 29
2019-01-12 10:30 | 30 | 20
2019-01-12 11:00 | 32 | 23
2019-01-12 11:30 | 32 | 23
2019-01-12 12:00 | 25 | 24
2019-01-12 12:30 | 22 | 21
2019-01-12 13:00 | 28 | 28
2019-01-12 13:30 | 18 | 18
2019-01-12 14:00 | 8 | 8
2019-01-12 14:30 | 21 | 21
2019-01-12 15:00 | 13 | 12
2019-01-12 15:30 | 20 | 20
2019-01-12 16:00 | 23 | 22
2019-01-12 16:30 | 25 | 25
2019-01-12 17:00 | 35 | 35
2019-01-12 17:30 | 43 | 42
2019-01-12 18:00 | 52 | 52
2019-01-12 18:30 | 56 | 55
2019-01-12 19:00 | 60 | 59
2019-01-12 19:30 | 62 | 61
2019-01-12 20:00 | 63 | 61
2019-01-12 20:30 | 65 | 65
2019-01-12 21:00 | 69 | 69
2019-01-12 21:30 | 70 | 70
2019-01-12 22:00 | 69 | 69
2019-01-12 22:30 | 69 | 69
2019-01-12 23:00 | 69 | 68
2019-01-12 23:30 | 68 | 68
2019-01-13 | 68 | 68
2019-01-13 00:30 | 67 | 67
2019-01-13 01:00 | 66 | 66
2019-01-13 01:30 | 66 | 66
2019-01-13 02:00 | 65 | 65
2019-01-13 02:30 | 65 | 65
2019-01-13 03:00 | 64 | 64
2019-01-13 03:30 | 63 | 63
2019-01-13 04:00 | 63 | 63
2019-01-13 04:30 | 62 | 62
2019-01-13 05:00 | 63 | 63
2019-01-13 05:30 | 63 | 63
2019-01-13 06:00 | 62 | 62
2019-01-13 06:30 | 60 | 60
2019-01-13 07:00 | 57 | 57
2019-01-13 07:30 | 51 | 51
2019-01-13 08:00 | 45 | 45
2019-01-13 08:30 | 37 | 37
2019-01-13 09:00 | 31 | 31
2019-01-13 09:30 | 30 | 30
2019-01-13 10:00 | 28 | 28
2019-01-13 10:30 | 35 | 35
2019-01-13 11:00 | 35 | 35
2019-01-13 11:30 | 33 | 33
2019-01-13 12:00 | 35 | 35
2019-01-13 12:30 | 35 | 35
2019-01-13 13:00 | 34 | 34
2019-01-13 13:30 | 37 | 37
2019-01-13 14:00 | 38 | 38
2019-01-13 14:30 | 39 | 39
2019-01-13 15:00 | 41 | 40
2019-01-13 15:30 | 45 | 45
2019-01-13 16:00 | 43 | 43
2019-01-13 16:30 | 38 | 38
2019-01-13 17:00 | 46 | 46
2019-01-13 17:30 | 47 | 47
2019-01-13 18:00 | 50 | 50
2019-01-13 18:30 | 50 | 50
2019-01-13 19:00 | 53 | 53
2019-01-13 19:30 | 54 | 53
2019-01-13 20:00 | 53 | 52
2019-01-13 20:30 | 53 | 52
2019-01-13 21:00 | 64 | 64
2019-01-13 21:30 | 69 | 68
2019-01-13 22:00 | 68 | 68
2019-01-13 22:30 | 67 | 67
2019-01-13 23:00 | 67 | 67
2019-01-13 23:30 | 66 | 65
2019-01-14 | 62 | 62
2019-01-14 00:30 | 61 | 61
2019-01-14 01:00 | 61 | 61
2019-01-14 01:30 | 61 | 60
2019-01-14 02:00 | 62 | 62
2019-01-14 02:30 | 64 | 64
2019-01-14 03:00 | 64 | 64
2019-01-14 03:30 | 62 | 62
2019-01-14 04:00 | 63 | 63
2019-01-14 04:30 | 64 | 64
2019-01-14 05:00 | 64 | 64
2019-01-14 05:30 | 65 | 64
2019-01-14 06:00 | 65 | 65
2019-01-14 06:30 | 64 | 63
2019-01-14 07:00 | 59 | 58
2019-01-14 07:30 | 52 | 51
2019-01-14 08:00 | 47 | 46
2019-01-14 08:30 | 46 | 45
2019-01-14 09:00 | 45 | 44
2019-01-14 09:30 | 40 | 39
2019-01-14 10:00 | 22 | 18
2019-01-14 10:30 | 26 | 24
2019-01-14 11:00 | 24 | 21
2019-01-14 11:30 | 20 | 18
2019-01-14 12:00 | 37 | 36
2019-01-14 12:30 | 24 | 21
2019-01-14 13:00 | 19 | 15
2019-01-14 13:30 | 22 | 18
2019-01-14 14:00 | 33 | 30
2019-01-14 14:30 | 27 | 25
2019-01-14 15:00 | 39 | 37
2019-01-14 15:30 | 45 | 44
2019-01-14 16:00 | 41 | 40
2019-01-14 16:30 | 34 | 33
2019-01-14 17:00 | 39 | 38
2019-01-14 17:30 | 42 | 42
2019-01-14 18:00 | 54 | 54
2019-01-14 18:30 | 56 | 56
2019-01-14 19:00 | 59 | 59
2019-01-14 19:30 | 62 | 62
2019-01-14 20:00 | 63 | 63
2019-01-14 20:30 | 60 | 60
2019-01-14 21:00 | 60 | 59
2019-01-14 21:30 | 56 | 56
2019-01-14 22:00 | 64 | 64
2019-01-14 22:30 | 52 | 52
2019-01-14 23:00 | 59 | 59
2019-01-14 23:30 | 64 | 64
2019-01-15 | 64 | 64
2019-01-15 00:30 | 64 | 64
2019-01-15 01:00 | 64 | 64
2019-01-15 01:30 | 62 | 62
2019-01-15 02:00 | 62 | 62
2019-01-15 02:30 | 62 | 61
2019-01-15 03:00 | 62 | 61
2019-01-15 03:30 | 62 | 62
2019-01-15 04:00 | 62 | 62
2019-01-15 04:30 | 62 | 62
2019-01-15 05:00 | 62 | 62
2019-01-15 05:30 | 63 | 63
2019-01-15 06:00 | 63 | 63
2019-01-15 06:30 | 55 | 55
2019-01-15 07:00 | 53 | 52
2019-01-15 07:30 | 49 | 48
2019-01-15 08:00 | 43 | 42
2019-01-15 08:30 | 42 | 40
2019-01-15 09:00 | 33 | 30
2019-01-15 09:30 | 38 | 34
2019-01-15 10:00 | 34 | 30
2019-01-15 10:30 | 22 | 14
2019-01-15 11:00 | 30 | 25
2019-01-15 11:30 | 31 | 27
2019-01-15 12:00 | 32 | 29
2019-01-15 12:30 | 34 | 32
2019-01-15 13:00 | 24 | 20
2019-01-15 13:30 | 30 | 28
2019-01-15 14:00 | 25 | 21
2019-01-15 14:30 | 25 | 23
2019-01-15 15:00 | 30 | 27
2019-01-15 15:30 | 19 | 15
2019-01-15 16:00 | 34 | 32
2019-01-15 16:30 | 27 | 26
2019-01-15 17:00 | 18 | 17
2019-01-15 17:30 | 20 | 20
2019-01-15 18:00 | 28 | 27
2019-01-15 18:30 | 33 | 32
2019-01-15 19:00 | 37 | 37
2019-01-15 19:30 | 39 | 38
2019-01-15 20:00 | 41 | 39
2019-01-15 20:30 | 45 | 44
2019-01-15 21:00 | 55 | 54
2019-01-15 21:30 | 56 | 56
2019-01-15 22:00 | 56 | 56
2019-01-15 22:30 | 52 | 52
2019-01-15 23:00 | 52 | 52
2019-01-15 23:30 | 54 | 53
2019-01-16 | 63 | 63
2019-01-16 00:30 | 63 | 63
2019-01-16 01:00 | 62 | 62
2019-01-16 01:30 | 54 | 54
2019-01-16 02:00 | 51 | 51
2019-01-16 02:30 | 51 | 51
2019-01-16 03:00 | 60 | 60
2019-01-16 03:30 | 56 | 56
2019-01-16 04:00 | 51 | 51
2019-01-16 04:30 | 50 | 50
2019-01-16 05:00 | 52 | 52
2019-01-16 05:30 | 53 | 53
2019-01-16 06:00 | 57 | 57
2019-01-16 06:30 | 54 | 54
2019-01-16 07:00 | 52 | 52
2019-01-16 07:30 | 46 | 46
2019-01-16 08:00 | 40 | 39
2019-01-16 08:30 | 35 | 35
2019-01-16 09:00 | 27 | 27
2019-01-16 09:30 | 18 | 18
2019-01-16 10:00 | 17 | 17
2019-01-16 10:30 | 14 | 14
2019-01-16 11:00 | 13 | 13
2019-01-16 11:30 | 13 | 13
2019-01-16 12:00 | 19 | 19
2019-01-16 12:30 | 16 | 16
2019-01-16 13:00 | 15 | 15
2019-01-16 13:30 | 26 | 26
2019-01-16 14:00 | 18 | 18
2019-01-16 14:30 | 7 | 7
2019-01-16 15:00 | 10 | 10
2019-01-16 15:30 | 8 | 8
2019-01-16 16:00 | 12 | 12
2019-01-16 16:30 | 15 | 15
2019-01-16 17:00 | 27 | 27
2019-01-16 17:30 | 37 | 37
2019-01-16 18:00 | 45 | 45
2019-01-16 18:30 | 50 | 50
2019-01-16 19:00 | 53 | 53
2019-01-16 19:30 | 54 | 53
2019-01-16 20:00 | 53 | 52
2019-01-16 20:30 | 51 | 50
2019-01-16 21:00 | 60 | 60
2019-01-16 21:30 | 60 | 60
2019-01-16 22:00 | 64 | 64
2019-01-16 22:30 | 68 | 68
2019-01-16 23:00 | 67 | 67
2019-01-16 23:30 | 58 | 58
2019-01-17 | 56 | 56
2019-01-17 00:30 | 54 | 54
2019-01-17 01:00 | 53 | 53
2019-01-17 01:30 | 61 | 61
2019-01-17 02:00 | 56 | 56
2019-01-17 02:30 | 57 | 57
2019-01-17 03:00 | 61 | 61
2019-01-17 03:30 | 59 | 59
2019-01-17 04:00 | 61 | 61
2019-01-17 04:30 | 62 | 62
2019-01-17 05:00 | 56 | 56
2019-01-17 05:30 | 54 | 54
2019-01-17 06:00 | 62 | 62
2019-01-17 06:30 | 61 | 61
2019-01-17 07:00 | 39 | 39
2019-01-17 07:30 | 47 | 47
2019-01-17 08:00 | 50 | 49
2019-01-17 08:30 | 43 | 42
2019-01-17 09:00 | 20 | 18
2019-01-17 09:30 | 21 | 19
2019-01-17 10:00 | 16 | 13
2019-01-17 10:30 | 13 | 10
2019-01-17 11:00 | 11 | 7
2019-01-17 11:30 | 13 | 9
2019-01-17 12:00 | 19 | 17
2019-01-17 12:30 | 11 | 3
2019-01-17 13:00 | 14 | 8
2019-01-17 13:30 | 14 | 9
2019-01-17 14:00 | 13 | 9
2019-01-17 14:30 | 13 | 6
2019-01-17 15:00 | 16 | 13
2019-01-17 15:30 | 19 | 17
2019-01-17 16:00 | 18 | 16
2019-01-17 16:30 | 23 | 22
2019-01-17 17:00 | 26 | 25
2019-01-17 17:30 | 25 | 25
2019-01-17 18:00 | 36 | 35
2019-01-17 18:30 | 43 | 43
2019-01-17 19:00 | 48 | 48
2019-01-17 19:30 | 49 | 49
2019-01-17 20:00 | 48 | 48
2019-01-17 20:30 | 49 | 49
2019-01-17 21:00 | 64 | 64
2019-01-17 21:30 | 66 | 65
2019-01-17 22:00 | 67 | 66
2019-01-17 22:30 | 66 | 65
2019-01-17 23:00 | 63 | 63
2019-01-17 23:30 | 63 | 63
2019-01-18 | 63 | 63
2019-01-18 00:30 | 64 | 63
2019-01-18 01:00 | 67 | 66
2019-01-18 01:30 | 67 | 66
2019-01-18 02:00 | 67 | 67
2019-01-18 02:30 | 67 | 67
2019-01-18 03:00 | 66 | 66
2019-01-18 03:30 | 66 | 65
2019-01-18 04:00 | 62 | 61
2019-01-18 04:30 | 65 | 65
2019-01-18 05:00 | 66 | 65
2019-01-18 05:30 | 66 | 65
2019-01-18 06:00 | 49 | 49
2019-01-18 06:30 | 49 | 49
2019-01-18 07:00 | 46 | 46
2019-01-18 07:30 | 54 | 54
2019-01-18 08:00 | 53 | 52
2019-01-18 08:30 | 37 | 36
2019-01-18 09:00 | 41 | 41
2019-01-18 09:30 | 46 | 46
2019-01-18 10:00 | 30 | 30
2019-01-18 10:30 | 25 | 25
2019-01-18 11:00 | 34 | 34
2019-01-18 11:30 | 22 | 22
2019-01-18 12:00 | 23 | 23
2019-01-18 12:30 | 27 | 27
2019-01-18 13:00 | 29 | 29
2019-01-18 13:30 | 24 | 24
2019-01-18 14:00 | 31 | 31
2019-01-18 14:30 | 30 | 29
2019-01-18 15:00 | 30 | 29
2019-01-18 15:30 | 29 | 29
2019-01-18 16:00 | 31 | 31
2019-01-18 16:30 | 40 | 39
2019-01-18 17:00 | 44 | 43
2019-01-18 17:30 | 47 | 46
2019-01-18 18:00 | 54 | 53
2019-01-18 18:30 | 62 | 62
2019-01-18 19:00 | 65 | 64
2019-01-18 19:30 | 66 | 65
2019-01-18 20:00 | 67 | 66
2019-01-18 20:30 | 71 | 70
2019-01-18 21:00 | 71 | 71
2019-01-18 21:30 | 66 | 66
2019-01-18 22:00 | 63 | 63
2019-01-18 22:30 | 65 | 65
2019-01-18 23:00 | 65 | 65
2019-01-18 23:30 | 65 | 65
2019-01-19 | 63 | 63
2019-01-19 00:30 | 61 | 61
2019-01-19 01:00 | 67 | 67
2019-01-19 01:30 | 68 | 67
2019-01-19 02:00 | 68 | 67
2019-01-19 02:30 | 68 | 67
2019-01-19 03:00 | 67 | 67
2019-01-19 03:30 | 67 | 66
2019-01-19 04:00 | 66 | 66
2019-01-19 04:30 | 66 | 65
2019-01-19 05:00 | 66 | 66
2019-01-19 05:30 | 66 | 66
2019-01-19 06:00 | 67 | 66
2019-01-19 06:30 | 65 | 64
2019-01-19 07:00 | 63 | 62
2019-01-19 07:30 | 53 | 51
2019-01-19 08:00 | 42 | 40
2019-01-19 08:30 | 44 | 43
2019-01-19 09:00 | 35 | 33
2019-01-19 09:30 | 32 | 30
2019-01-19 10:00 | 30 | 29
2019-01-19 10:30 | 29 | 27
2019-01-19 11:00 | 37 | 36
2019-01-19 11:30 | 50 | 49
2019-01-19 12:00 | 35 | 34
2019-01-19 12:30 | 29 | 27
2019-01-19 13:00 | 30 | 29
2019-01-19 13:30 | 32 | 30
2019-01-19 14:00 | 32 | 30
2019-01-19 14:30 | 31 | 29
2019-01-19 15:00 | 33 | 32
2019-01-19 15:30 | 41 | 40
2019-01-19 16:00 | 46 | 45
2019-01-19 16:30 | 50 | 48
2019-01-19 17:00 | 52 | 51
2019-01-19 17:30 | 57 | 55
2019-01-19 18:00 | 61 | 60
2019-01-19 18:30 | 66 | 65
2019-01-19 19:00 | 68 | 68
2019-01-19 19:30 | 70 | 70
2019-01-19 20:00 | 78 | 76
2019-01-19 20:30 | 80 | 78
2019-01-19 21:00 | 80 | 78
2019-01-19 21:30 | 80 | 79
2019-01-19 22:00 | 77 | 75
2019-01-19 22:30 | 75 | 73
2019-01-19 23:00 | 73 | 71
2019-01-19 23:30 | 73 | 70
2019-01-20 | 72 | 70
2019-01-20 00:30 | 72 | 69
2019-01-20 01:00 | 72 | 69
2019-01-20 01:30 | 71 | 68
2019-01-20 02:00 | 68 | 68
2019-01-20 02:30 | 68 | 68
2019-01-20 03:00 | 69 | 68
2019-01-20 03:30 | 68 | 68
2019-01-20 04:00 | 68 | 68
2019-01-20 04:30 | 67 | 67
2019-01-20 05:00 | 67 | 67
2019-01-20 05:30 | 66 | 66
2019-01-20 06:00 | 65 | 65
2019-01-20 06:30 | 64 | 64
2019-01-20 07:00 | 64 | 63
2019-01-20 07:30 | 58 | 58
2019-01-20 08:00 | 53 | 52
2019-01-20 08:30 | 41 | 41
2019-01-20 09:00 | 41 | 41
2019-01-20 09:30 | 41 | 41
2019-01-20 10:00 | 42 | 42
2019-01-20 10:30 | 26 | 25
2019-01-20 11:00 | 27 | 26
2019-01-20 11:30 | 37 | 37
2019-01-20 12:00 | 34 | 34
2019-01-20 12:30 | 29 | 28
2019-01-20 13:00 | 30 | 30
2019-01-20 13:30 | 26 | 26
2019-01-20 14:00 | 25 | 25
2019-01-20 14:30 | 23 | 22
2019-01-20 15:00 | 22 | 21
2019-01-20 15:30 | 24 | 24
2019-01-20 16:00 | 31 | 30
2019-01-20 16:30 | 42 | 42
2019-01-20 17:00 | 55 | 54
2019-01-20 17:30 | 57 | 57
2019-01-20 18:00 | 57 | 57
2019-01-20 18:30 | 57 | 57
2019-01-20 19:00 | 56 | 56
2019-01-20 19:30 | 64 | 62
2019-01-20 20:00 | 65 | 63
2019-01-20 20:30 | 72 | 72
2019-01-20 21:00 | 74 | 73
2019-01-20 21:30 | 73 | 72
2019-01-20 22:00 | 71 | 71
2019-01-20 22:30 | 67 | 66
2019-01-20 23:00 | 70 | 69
2019-01-20 23:30 | 70 | 70
2019-01-21 | 69 | 69
2019-01-21 00:30 | 68 | 67
2019-01-21 01:00 | 67 | 67
2019-01-21 01:30 | 68 | 66
2019-01-21 02:00 | 67 | 66
2019-01-21 02:30 | 67 | 66
2019-01-21 03:00 | 66 | 65
2019-01-21 03:30 | 67 | 67
2019-01-21 04:00 | 67 | 66
2019-01-21 04:30 | 67 | 66
2019-01-21 05:00 | 67 | 66
2019-01-21 05:30 | 68 | 67
2019-01-21 06:00 | 66 | 65
2019-01-21 06:30 | 60 | 60
2019-01-21 07:00 | 58 | 58
2019-01-21 07:30 | 52 | 52
2019-01-21 08:00 | 51 | 51
2019-01-21 08:30 | 43 | 42
2019-01-21 09:00 | 38 | 37
2019-01-21 09:30 | 32 | 31
2019-01-21 10:00 | 28 | 27
2019-01-21 10:30 | 45 | 44
2019-01-21 11:00 | 46 | 45
2019-01-21 11:30 | 42 | 40
2019-01-21 12:00 | 26 | 25
2019-01-21 12:30 | 32 | 32
2019-01-21 13:00 | 32 | 31
2019-01-21 13:30 | 23 | 22
2019-01-21 14:00 | 31 | 31
2019-01-21 14:30 | 35 | 35
2019-01-21 15:00 | 33 | 33
2019-01-21 15:30 | 38 | 38
2019-01-21 16:00 | 47 | 47
2019-01-21 16:30 | 54 | 54
2019-01-21 17:00 | 65 | 65
2019-01-21 17:30 | 66 | 65
2019-01-21 18:00 | 69 | 69
2019-01-21 18:30 | 71 | 71
2019-01-21 19:00 | 70 | 70
2019-01-21 19:30 | 74 | 74
2019-01-21 20:00 | 77 | 76
2019-01-21 20:30 | 76 | 74
2019-01-21 21:00 | 80 | 78
2019-01-21 21:30 | 82 | 81
2019-01-21 22:00 | 80 | 79
2019-01-21 22:30 | 75 | 73
2019-01-21 23:00 | 79 | 77
2019-01-21 23:30 | 76 | 75
2019-01-22 | 76 | 76
2019-01-22 00:30 | 75 | 75
2019-01-22 01:00 | 75 | 74
2019-01-22 01:30 | 74 | 74
2019-01-22 02:00 | 74 | 73
2019-01-22 02:30 | 68 | 66
2019-01-22 03:00 | 69 | 68
2019-01-22 03:30 | 71 | 69
2019-01-22 04:00 | 70 | 70
2019-01-22 04:30 | 73 | 73
2019-01-22 05:00 | 74 | 74
2019-01-22 05:30 | 70 | 70
2019-01-22 06:00 | 66 | 66
2019-01-22 06:30 | 61 | 61
2019-01-22 07:00 | 57 | 56
2019-01-22 07:30 | 56 | 55
2019-01-22 08:00 | 56 | 55
2019-01-22 08:30 | 42 | 41
2019-01-22 09:00 | 37 | 37
2019-01-22 09:30 | 31 | 29
2019-01-22 10:00 | 31 | 30
2019-01-22 10:30 | 29 | 27
2019-01-22 11:00 | 36 | 35
2019-01-22 11:30 | 45 | 44
2019-01-22 12:00 | 22 | 20
2019-01-22 12:30 | 29 | 28
2019-01-22 13:00 | 33 | 31
2019-01-22 13:30 | 23 | 20
2019-01-22 14:00 | 17 | 14
2019-01-22 14:30 | 11 | 7
2019-01-22 15:00 | 11 | 1
2019-01-22 15:30 | 13 | 8
2019-01-22 16:00 | 13 | 10
2019-01-22 16:30 | 20 | 19
2019-01-22 17:00 | 27 | 26
2019-01-22 17:30 | 34 | 34
2019-01-22 18:00 | 45 | 45
2019-01-22 18:30 | 51 | 51
2019-01-22 19:00 | 54 | 54
2019-01-22 19:30 | 67 | 65
2019-01-22 20:00 | 80 | 79
2019-01-22 20:30 | 83 | 81
2019-01-22 21:00 | 81 | 80
2019-01-22 21:30 | 80 | 78
2019-01-22 22:00 | 76 | 75
2019-01-22 22:30 | 77 | 75
2019-01-22 23:00 | 80 | 78
2019-01-22 23:30 | 80 | 78
2019-01-23 | 79 | 77
2019-01-23 00:30 | 78 | 77
2019-01-23 01:00 | 78 | 77
2019-01-23 01:30 | 78 | 76
2019-01-23 02:00 | 77 | 76
2019-01-23 02:30 | 77 | 75
2019-01-23 03:00 | 75 | 74
2019-01-23 03:30 | 73 | 72
2019-01-23 04:00 | 72 | 71
2019-01-23 04:30 | 73 | 72
2019-01-23 05:00 | 73 | 72
2019-01-23 05:30 | 73 | 72
2019-01-23 06:00 | 70 | 69
2019-01-23 06:30 | 66 | 65
2019-01-23 07:00 | 62 | 61
2019-01-23 07:30 | 62 | 61
2019-01-23 08:00 | 59 | 57
2019-01-23 08:30 | 54 | 53
2019-01-23 09:00 | 54 | 53
2019-01-23 09:30 | 39 | 38
2019-01-23 10:00 | 45 | 43
2019-01-23 10:30 | 38 | 36
2019-01-23 11:00 | 30 | 28
2019-01-23 11:30 | 30 | 28
2019-01-23 12:00 | 23 | 22
2019-01-23 12:30 | 14 | 10
2019-01-23 13:00 | 19 | 17
2019-01-23 13:30 | 12 | 7
2019-01-23 14:00 | 12 | 6
2019-01-23 14:30 | 23 | 21
2019-01-23 15:00 | 27 | 25
2019-01-23 15:30 | 21 | 19
2019-01-23 16:00 | 19 | 16
2019-01-23 16:30 | 21 | 19
2019-01-23 17:00 | 28 | 27
2019-01-23 17:30 | 39 | 38
2019-01-23 18:00 | 41 | 41
2019-01-23 18:30 | 42 | 42
2019-01-23 19:00 | 62 | 62
2019-01-23 19:30 | 79 | 78
2019-01-23 20:00 | 80 | 78
2019-01-23 20:30 | 78 | 76
2019-01-23 21:00 | 77 | 76
2019-01-23 21:30 | 77 | 75
2019-01-23 22:00 | 79 | 78
2019-01-23 22:30 | 74 | 72
2019-01-23 23:00 | 69 | 68
2019-01-23 23:30 | 71 | 70
2019-01-24 | 71 | 70
2019-01-24 00:30 | 72 | 71
2019-01-24 01:00 | 72 | 71
2019-01-24 01:30 | 74 | 72
2019-01-24 02:00 | 75 | 74
2019-01-24 02:30 | 74 | 72
2019-01-24 03:00 | 75 | 74
2019-01-24 03:30 | 75 | 73
2019-01-24 04:00 | 75 | 73
2019-01-24 04:30 | 75 | 74
2019-01-24 05:00 | 75 | 74
2019-01-24 05:30 | 76 | 74
2019-01-24 06:00 | 74 | 73
2019-01-24 06:30 | 74 | 72
2019-01-24 07:00 | 66 | 65
2019-01-24 07:30 | 64 | 62
2019-01-24 08:00 | 57 | 55
2019-01-24 08:30 | 57 | 55
2019-01-24 09:00 | 59 | 58
2019-01-24 09:30 | 54 | 54
2019-01-24 10:00 | 38 | 38
2019-01-24 10:30 | 34 | 34
2019-01-24 11:00 | 32 | 32
2019-01-24 11:30 | 39 | 38
2019-01-24 12:00 | 44 | 44
2019-01-24 12:30 | 41 | 41
2019-01-24 13:00 | 35 | 34
2019-01-24 13:30 | 39 | 39
2019-01-24 14:00 | 35 | 35
2019-01-24 14:30 | 33 | 33
2019-01-24 15:00 | 27 | 26
2019-01-24 15:30 | 43 | 43
2019-01-24 16:00 | 38 | 37
2019-01-24 16:30 | 41 | 41
2019-01-24 17:00 | 48 | 48
2019-01-24 17:30 | 57 | 57
2019-01-24 18:00 | 62 | 62
2019-01-24 18:30 | 65 | 65
2019-01-24 19:00 | 68 | 68
2019-01-24 19:30 | 69 | 69
2019-01-24 20:00 | 73 | 73
2019-01-24 20:30 | 75 | 75
2019-01-24 21:00 | 72 | 72
2019-01-24 21:30 | 68 | 68
2019-01-24 22:00 | 72 | 72
2019-01-24 22:30 | 79 | 79
2019-01-24 23:00 | 78 | 77
2019-01-24 23:30 | 82 | 81
2019-01-25 | 79 | 78
2019-01-25 00:30 | 77 | 77
2019-01-25 01:00 | 77 | 75
2019-01-25 01:30 | 76 | 75
2019-01-25 02:00 | 76 | 75
2019-01-25 02:30 | 76 | 74
2019-01-25 03:00 | 76 | 74
2019-01-25 03:30 | 75 | 74
2019-01-25 04:00 | 75 | 74
2019-01-25 04:30 | 75 | 74
2019-01-25 05:00 | 75 | 74
2019-01-25 05:30 | 76 | 75
2019-01-25 06:00 | 75 | 73
2019-01-25 06:30 | 74 | 73
2019-01-25 07:00 | 72 | 71
2019-01-25 07:30 | 71 | 70
2019-01-25 08:00 | 56 | 54
2019-01-25 08:30 | 53 | 52
2019-01-25 09:00 | 60 | 59
2019-01-25 09:30 | 57 | 56
2019-01-25 10:00 | 53 | 51
2019-01-25 10:30 | 43 | 42
2019-01-25 11:00 | 50 | 49
2019-01-25 11:30 | 47 | 46
2019-01-25 12:00 | 32 | 31
2019-01-25 12:30 | 29 | 27
2019-01-25 13:00 | 31 | 29
2019-01-25 13:30 | 28 | 25
2019-01-25 14:00 | 26 | 24
2019-01-25 14:30 | 26 | 24
2019-01-25 15:00 | 34 | 33
2019-01-25 15:30 | 20 | 19
2019-01-25 16:00 | 21 | 20
2019-01-25 16:30 | 23 | 23
2019-01-25 17:00 | 29 | 29
2019-01-25 17:30 | 32 | 32
2019-01-25 18:00 | 40 | 40
2019-01-25 18:30 | 44 | 44
2019-01-25 19:00 | 48 | 48
2019-01-25 19:30 | 51 | 50
2019-01-25 20:00 | 53 | 52
2019-01-25 20:30 | 62 | 62
2019-01-25 21:00 | 73 | 73
2019-01-25 21:30 | 77 | 77
2019-01-25 22:00 | 78 | 78
2019-01-25 22:30 | 76 | 75
2019-01-25 23:00 | 77 | 76
2019-01-25 23:30 | 75 | 74
2019-01-26 | 77 | 77
2019-01-26 00:30 | 73 | 73
2019-01-26 01:00 | 73 | 72
2019-01-26 01:30 | 73 | 73
2019-01-26 02:00 | 74 | 73
2019-01-26 02:30 | 73 | 73
2019-01-26 03:00 | 72 | 72
2019-01-26 03:30 | 72 | 71
2019-01-26 04:00 | 71 | 70
2019-01-26 04:30 | 72 | 71
2019-01-26 05:00 | 72 | 71
2019-01-26 05:30 | 71 | 70
2019-01-26 06:00 | 71 | 71
2019-01-26 06:30 | 70 | 70
2019-01-26 07:00 | 69 | 68
2019-01-26 07:30 | 70 | 69
2019-01-26 08:00 | 66 | 65
2019-01-26 08:30 | 53 | 51
2019-01-26 09:00 | 47 | 45
2019-01-26 09:30 | 51 | 49
2019-01-26 10:00 | 61 | 59
2019-01-26 10:30 | 43 | 41
2019-01-26 11:00 | 44 | 42
2019-01-26 11:30 | 45 | 43
2019-01-26 12:00 | 33 | 31
2019-01-26 12:30 | 30 | 28
2019-01-26 13:00 | 41 | 39
2019-01-26 13:30 | 50 | 49
2019-01-26 14:00 | 51 | 50
2019-01-26 14:30 | 52 | 50
2019-01-26 15:00 | 58 | 56
2019-01-26 15:30 | 62 | 61
2019-01-26 16:00 | 54 | 53
2019-01-26 16:30 | 50 | 49
2019-01-26 17:00 | 53 | 52
2019-01-26 17:30 | 54 | 53
2019-01-26 18:00 | 57 | 56
2019-01-26 18:30 | 58 | 58
2019-01-26 19:00 | 60 | 60
2019-01-26 19:30 | 59 | 59
2019-01-26 20:00 | 64 | 64
2019-01-26 20:30 | 60 | 60
2019-01-26 21:00 | 60 | 60
2019-01-26 21:30 | 74 | 73
2019-01-26 22:00 | 73 | 72
2019-01-26 22:30 | 72 | 71
2019-01-26 23:00 | 74 | 73
2019-01-26 23:30 | 73 | 72
2019-01-27 | 72 | 71
2019-01-27 00:30 | 67 | 66
2019-01-27 01:00 | 71 | 70
2019-01-27 01:30 | 72 | 71
2019-01-27 02:00 | 71 | 71
2019-01-27 02:30 | 71 | 70
2019-01-27 03:00 | 71 | 70
2019-01-27 03:30 | 71 | 70
2019-01-27 04:00 | 70 | 69
2019-01-27 04:30 | 71 | 70
2019-01-27 05:00 | 70 | 70
2019-01-27 05:30 | 70 | 69
2019-01-27 06:00 | 68 | 68
2019-01-27 06:30 | 68 | 68
2019-01-27 07:00 | 66 | 65
2019-01-27 07:30 | 67 | 66
2019-01-27 08:00 | 65 | 64
2019-01-27 08:30 | 62 | 61
2019-01-27 09:00 | 62 | 61
2019-01-27 09:30 | 57 | 55
2019-01-27 10:00 | 53 | 51
2019-01-27 10:30 | 50 | 48
2019-01-27 11:00 | 53 | 52
2019-01-27 11:30 | 48 | 47
2019-01-27 12:00 | 54 | 53
2019-01-27 12:30 | 38 | 36
2019-01-27 13:00 | 42 | 41
2019-01-27 13:30 | 41 | 39
2019-01-27 14:00 | 46 | 45
2019-01-27 14:30 | 52 | 51
2019-01-27 15:00 | 54 | 53
2019-01-27 15:30 | 54 | 53
2019-01-27 16:00 | 57 | 56
2019-01-27 16:30 | 59 | 58
2019-01-27 17:00 | 53 | 52
2019-01-27 17:30 | 49 | 48
2019-01-27 18:00 | 51 | 50
2019-01-27 18:30 | 55 | 55
2019-01-27 19:00 | 63 | 62
2019-01-27 19:30 | 62 | 62
2019-01-27 20:00 | 62 | 62
2019-01-27 20:30 | 63 | 62
2019-01-27 21:00 | 67 | 66
2019-01-27 21:30 | 67 | 66
2019-01-27 22:00 | 67 | 66
2019-01-27 22:30 | 66 | 66
2019-01-27 23:00 | 67 | 67
2019-01-27 23:30 | 65 | 65
2019-01-28 | 64 | 64
2019-01-28 00:30 | 65 | 64
2019-01-28 01:00 | 65 | 64
2019-01-28 01:30 | 68 | 67
2019-01-28 02:00 | 67 | 67
2019-01-28 02:30 | 68 | 67
2019-01-28 03:00 | 64 | 63
2019-01-28 03:30 | 63 | 63
2019-01-28 04:00 | 63 | 63
2019-01-28 04:30 | 63 | 62
2019-01-28 05:00 | 62 | 62
2019-01-28 05:30 | 62 | 62
2019-01-28 06:00 | 62 | 62
2019-01-28 06:30 | 64 | 63
2019-01-28 07:00 | 64 | 63
2019-01-28 07:30 | 64 | 64
2019-01-28 08:00 | 66 | 65
2019-01-28 08:30 | 66 | 65
2019-01-28 09:00 | 67 | 66
2019-01-28 09:30 | 66 | 64
2019-01-28 10:00 | 65 | 63
2019-01-28 10:30 | 64 | 63
2019-01-28 11:00 | 63 | 62
2019-01-28 11:30 | 60 | 59
2019-01-28 12:00 | 63 | 62
2019-01-28 12:30 | 64 | 63
2019-01-28 13:00 | 63 | 62
2019-01-28 13:30 | 63 | 62
2019-01-28 14:00 | 57 | 56
2019-01-28 14:30 | 54 | 53
2019-01-28 15:00 | 48 | 47
2019-01-28 15:30 | 48 | 47
2019-01-28 16:00 | 37 | 37
2019-01-28 16:30 | 33 | 33
2019-01-28 17:00 | 30 | 29
2019-01-28 17:30 | 31 | 31
2019-01-28 18:00 | 31 | 31
2019-01-28 18:30 | 33 | 33
2019-01-28 19:00 | 38 | 38
2019-01-28 19:30 | 42 | 42
2019-01-28 20:00 | 49 | 49
2019-01-28 20:30 | 49 | 49
2019-01-28 21:00 | 52 | 52
2019-01-28 21:30 | 51 | 51
2019-01-28 22:00 | 51 | 51
2019-01-28 22:30 | 51 | 51
2019-01-28 23:00 | 65 | 64
2019-01-28 23:30 | 64 | 63
2019-01-29 | 63 | 62
2019-01-29 00:30 | 62 | 61
2019-01-29 01:00 | 63 | 62
2019-01-29 01:30 | 63 | 63
2019-01-29 02:00 | 63 | 63
2019-01-29 02:30 | 62 | 62
2019-01-29 03:00 | 63 | 62
2019-01-29 03:30 | 62 | 62
2019-01-29 04:00 | 62 | 61
2019-01-29 04:30 | 62 | 61
2019-01-29 05:00 | 63 | 63
2019-01-29 05:30 | 63 | 63
2019-01-29 06:00 | 64 | 63
2019-01-29 06:30 | 57 | 57
2019-01-29 07:00 | 42 | 42
2019-01-29 07:30 | 43 | 43
2019-01-29 08:00 | 45 | 45
2019-01-29 08:30 | 57 | 57
2019-01-29 09:00 | 56 | 56
2019-01-29 09:30 | 55 | 54
2019-01-29 10:00 | 55 | 55
2019-01-29 10:30 | 55 | 55
2019-01-29 11:00 | 52 | 52
2019-01-29 11:30 | 50 | 50
2019-01-29 12:00 | 42 | 42
2019-01-29 12:30 | 42 | 41
2019-01-29 13:00 | 51 | 51
2019-01-29 13:30 | 55 | 54
2019-01-29 14:00 | 56 | 55
2019-01-29 14:30 | 56 | 56
2019-01-29 15:00 | 56 | 56
2019-01-29 15:30 | 48 | 48
2019-01-29 16:00 | 37 | 37
2019-01-29 16:30 | 32 | 32
2019-01-29 17:00 | 39 | 39
2019-01-29 17:30 | 42 | 42
2019-01-29 18:00 | 39 | 39
2019-01-29 18:30 | 41 | 40
2019-01-29 19:00 | 43 | 41
2019-01-29 19:30 | 52 | 51
2019-01-29 20:00 | 55 | 54
2019-01-29 20:30 | 57 | 57
2019-01-29 21:00 | 57 | 57
2019-01-29 21:30 | 55 | 55
2019-01-29 22:00 | 60 | 60
2019-01-29 22:30 | 63 | 62
2019-01-29 23:00 | 56 | 56
2019-01-29 23:30 | 60 | 60
2019-01-30 | 61 | 61
2019-01-30 00:30 | 60 | 59
2019-01-30 01:00 | 61 | 60
2019-01-30 01:30 | 61 | 60
2019-01-30 02:00 | 62 | 61
2019-01-30 02:30 | 62 | 62
2019-01-30 03:00 | 62 | 62
2019-01-30 03:30 | 63 | 63
2019-01-30 04:00 | 63 | 62
2019-01-30 04:30 | 63 | 63
2019-01-30 05:00 | 63 | 63
2019-01-30 05:30 | 64 | 63
2019-01-30 06:00 | 63 | 63
2019-01-30 06:30 | 54 | 54
2019-01-30 07:00 | 52 | 52
2019-01-30 07:30 | 53 | 52
2019-01-30 08:00 | 52 | 52
2019-01-30 08:30 | 52 | 52
2019-01-30 09:00 | 52 | 52
2019-01-30 09:30 | 53 | 53
2019-01-30 10:00 | 53 | 53
2019-01-30 10:30 | 53 | 52
2019-01-30 11:00 | 53 | 53
2019-01-30 11:30 | 57 | 56
2019-01-30 12:00 | 61 | 59
2019-01-30 12:30 | 53 | 52
2019-01-30 13:00 | 54 | 53
2019-01-30 13:30 | 52 | 52
2019-01-30 14:00 | 50 | 49
2019-01-30 14:30 | 45 | 45
2019-01-30 15:00 | 53 | 52
2019-01-30 15:30 | 56 | 56
2019-01-30 16:00 | 47 | 47
2019-01-30 16:30 | 48 | 48
2019-01-30 17:00 | 50 | 50
2019-01-30 17:30 | 44 | 44
2019-01-30 18:00 | 51 | 51
2019-01-30 18:30 | 55 | 55
2019-01-30 19:00 | 59 | 59
2019-01-30 19:30 | 54 | 54
2019-01-30 20:00 | 48 | 48
2019-01-30 20:30 | 46 | 46
2019-01-30 21:00 | 59 | 59
2019-01-30 21:30 | 59 | 58
2019-01-30 22:00 | 59 | 58
2019-01-30 22:30 | 57 | 56
2019-01-30 23:00 | 58 | 58
2019-01-30 23:30 | 58 | 58
2019-01-31 | 58 | 58
2019-01-31 00:30 | 58 | 58
2019-01-31 01:00 | 60 | 60
2019-01-31 01:30 | 61 | 60
2019-01-31 02:00 | 62 | 61
2019-01-31 02:30 | 61 | 61
2019-01-31 03:00 | 61 | 60
2019-01-31 03:30 | 62 | 61
2019-01-31 04:00 | 62 | 61
2019-01-31 04:30 | 61 | 61
2019-01-31 05:00 | 62 | 61
2019-01-31 05:30 | 63 | 62
2019-01-31 06:00 | 63 | 62
2019-01-31 06:30 | 52 | 52
2019-01-31 07:00 | 36 | 36
2019-01-31 07:30 | 42 | 42
2019-01-31 08:00 | 52 | 51
2019-01-31 08:30 | 62 | 61
2019-01-31 09:00 | 62 | 61
2019-01-31 09:30 | 63 | 62
2019-01-31 10:00 | 64 | 63
2019-01-31 10:30 | 64 | 63
2019-01-31 11:00 | 64 | 62
2019-01-31 11:30 | 64 | 63
2019-01-31 12:00 | 64 | 62
2019-01-31 12:30 | 63 | 61
2019-01-31 13:00 | 59 | 56
2019-01-31 13:30 | 65 | 63
2019-01-31 14:00 | 66 | 66
2019-01-31 14:30 | 65 | 65
2019-01-31 15:00 | 65 | 65
2019-01-31 15:30 | 64 | 63
2019-01-31 16:00 | 56 | 55
2019-01-31 16:30 | 42 | 40
2019-01-31 17:00 | 49 | 47
2019-01-31 17:30 | 53 | 52
2019-01-31 18:00 | 60 | 59
2019-01-31 18:30 | 70 | 70
2019-01-31 19:00 | 73 | 73
2019-01-31 19:30 | 76 | 76
2019-01-31 20:00 | 77 | 77
2019-01-31 20:30 | 73 | 72
2019-01-31 21:00 | 71 | 70
2019-01-31 21:30 | 70 | 70
2019-01-31 22:00 | 70 | 69
2019-01-31 22:30 | 69 | 69
2019-01-31 23:00 | 69 | 68
2019-01-31 23:30 | 68 | 68
2019-02-01 | 67 | 67
2019-02-01 00:30 | 67 | 67
2019-02-01 01:00 | 66 | 66
2019-02-01 01:30 | 67 | 66
2019-02-01 02:00 | 67 | 67
2019-02-01 02:30 | 67 | 67
2019-02-01 03:00 | 67 | 67
2019-02-01 03:30 | 67 | 67
2019-02-01 04:00 | 67 | 66
2019-02-01 04:30 | 66 | 66
2019-02-01 05:00 | 65 | 65
2019-02-01 05:30 | 65 | 65
2019-02-01 06:00 | 65 | 64
2019-02-01 06:30 | 62 | 62
2019-02-01 07:00 | 57 | 57
2019-02-01 07:30 | 58 | 58
2019-02-01 08:00 | 64 | 63
2019-02-01 08:30 | 65 | 64
2019-02-01 09:00 | 62 | 61
2019-02-01 09:30 | 61 | 60
2019-02-01 10:00 | 63 | 62
2019-02-01 10:30 | 64 | 62
2019-02-01 11:00 | 63 | 62
2019-02-01 11:30 | 63 | 63
2019-02-01 12:00 | 62 | 61
2019-02-01 12:30 | 61 | 60
2019-02-01 13:00 | 59 | 58
2019-02-01 13:30 | 58 | 57
2019-02-01 14:00 | 61 | 60
2019-02-01 14:30 | 63 | 62
2019-02-01 15:00 | 64 | 63
2019-02-01 15:30 | 65 | 64
2019-02-01 16:00 | 64 | 63
2019-02-01 16:30 | 64 | 63
2019-02-01 17:00 | 65 | 64
2019-02-01 17:30 | 66 | 65
2019-02-01 18:00 | 66 | 65
2019-02-01 18:30 | 66 | 65
2019-02-01 19:00 | 66 | 66
2019-02-01 19:30 | 67 | 66
2019-02-01 20:00 | 67 | 66
2019-02-01 20:30 | 65 | 65
2019-02-01 21:00 | 64 | 64
2019-02-01 21:30 | 64 | 63
2019-02-01 22:00 | 63 | 63
2019-02-01 22:30 | 63 | 63
2019-02-01 23:00 | 64 | 64
2019-02-01 23:30 | 63 | 63
2019-02-02 | 63 | 62
2019-02-02 00:30 | 63 | 63
2019-02-02 01:00 | 62 | 62
2019-02-02 01:30 | 32 | 27
2019-02-02 02:00 | 32 | 26
2019-02-02 02:30 | 32 | 25
2019-02-02 03:00 | 31 | 25
2019-02-02 03:30 | 31 | 25
2019-02-02 04:00 | 32 | 25
2019-02-02 04:30 | 32 | 26
2019-02-02 05:00 | 43 | 41
2019-02-02 05:30 | 53 | 53
2019-02-02 06:00 | 55 | 55
2019-02-02 06:30 | 57 | 57
2019-02-02 07:00 | 59 | 58
2019-02-02 07:30 | 59 | 59
2019-02-02 08:00 | 62 | 62
2019-02-02 08:30 | 63 | 63
2019-02-02 09:00 | 65 | 64
2019-02-02 09:30 | 65 | 64
2019-02-02 10:00 | 64 | 63
2019-02-02 10:30 | 61 | 60
2019-02-02 11:00 | 61 | 60
2019-02-02 11:30 | 64 | 63
2019-02-02 12:00 | 64 | 63
2019-02-02 12:30 | 64 | 63
2019-02-02 13:00 | 63 | 63
2019-02-02 13:30 | 63 | 62
2019-02-02 14:00 | 63 | 62
2019-02-02 14:30 | 63 | 62
2019-02-02 15:00 | 64 | 63
2019-02-02 15:30 | 58 | 58
2019-02-02 16:00 | 57 | 56
2019-02-02 16:30 | 49 | 49
2019-02-02 17:00 | 40 | 40
2019-02-02 17:30 | 40 | 40
2019-02-02 18:00 | 43 | 43
2019-02-02 18:30 | 44 | 44
2019-02-02 19:00 | 46 | 46
2019-02-02 19:30 | 45 | 45
2019-02-02 20:00 | 45 | 45
2019-02-02 20:30 | 44 | 44
2019-02-02 21:00 | 44 | 43
2019-02-02 21:30 | 43 | 42
2019-02-02 22:00 | 42 | 41
2019-02-02 22:30 | 42 | 42
2019-02-02 23:00 | 42 | 41
2019-02-02 23:30 | 42 | 41
2019-02-03 | 42 | 42
2019-02-03 00:30 | 42 | 41
2019-02-03 01:00 | 41 | 40
2019-02-03 01:30 | 40 | 40
2019-02-03 02:00 | 41 | 40
2019-02-03 02:30 | 40 | 39
2019-02-03 03:00 | 41 | 40
2019-02-03 03:30 | 41 | 40
2019-02-03 04:00 | 41 | 40
2019-02-03 04:30 | 42 | 41
2019-02-03 05:00 | 42 | 41
2019-02-03 05:30 | 41 | 40
2019-02-03 06:00 | 41 | 41
2019-02-03 06:30 | 42 | 41
2019-02-03 07:00 | 42 | 41
2019-02-03 07:30 | 43 | 42
2019-02-03 08:00 | 46 | 46
2019-02-03 08:30 | 50 | 50
2019-02-03 09:00 | 50 | 50
2019-02-03 09:30 | 49 | 49
2019-02-03 10:00 | 51 | 51
2019-02-03 10:30 | 48 | 48
2019-02-03 11:00 | 58 | 57
2019-02-03 11:30 | 57 | 57
2019-02-03 12:00 | 56 | 56
2019-02-03 12:30 | 52 | 51
2019-02-03 13:00 | 58 | 57
2019-02-03 13:30 | 56 | 56
2019-02-03 14:00 | 50 | 49
2019-02-03 14:30 | 48 | 47
2019-02-03 15:00 | 51 | 51
2019-02-03 15:30 | 55 | 55
2019-02-03 16:00 | 57 | 57
2019-02-03 16:30 | 57 | 57
2019-02-03 17:00 | 57 | 57
2019-02-03 17:30 | 50 | 50
2019-02-03 18:00 | 52 | 52
2019-02-03 18:30 | 52 | 52
2019-02-03 19:00 | 45 | 44
2019-02-03 19:30 | 43 | 43
2019-02-03 20:00 | 36 | 33
2019-02-03 20:30 | 35 | 32
2019-02-03 21:00 | 34 | 31
2019-02-03 21:30 | 33 | 29
2019-02-03 22:00 | 33 | 28
2019-02-03 22:30 | 33 | 27
2019-02-03 23:00 | 33 | 27
2019-02-03 23:30 | 34 | 27
2019-02-04 | 33 | 26
2019-02-04 00:30 | 33 | 25
2019-02-04 01:00 | 34 | 26
2019-02-04 01:30 | 34 | 25
2019-02-04 02:00 | 34 | 26
2019-02-04 02:30 | 30 | 25
2019-02-04 03:00 | 30 | 25
2019-02-04 03:30 | 30 | 25
2019-02-04 04:00 | 30 | 25
2019-02-04 04:30 | 30 | 25
2019-02-04 05:00 | 30 | 25
2019-02-04 05:30 | 30 | 25
2019-02-04 06:00 | 30 | 26
2019-02-04 06:30 | 30 | 26
2019-02-04 07:00 | 29 | 25
2019-02-04 07:30 | 29 | 25
2019-02-04 08:00 | 27 | 24
2019-02-04 08:30 | 24 | 21
2019-02-04 09:00 | 20 | 16
2019-02-04 09:30 | 21 | 17
2019-02-04 10:00 | 23 | 20
2019-02-04 10:30 | 23 | 22
2019-02-04 11:00 | 24 | 23
2019-02-04 11:30 | 22 | 21
2019-02-04 12:00 | 25 | 23
2019-02-04 12:30 | 28 | 26
2019-02-04 13:00 | 30 | 29
2019-02-04 13:30 | 33 | 31
2019-02-04 14:00 | 31 | 29
2019-02-04 14:30 | 32 | 30
2019-02-04 15:00 | 31 | 29
2019-02-04 15:30 | 32 | 31
2019-02-04 16:00 | 30 | 29
2019-02-04 16:30 | 31 | 30
2019-02-04 17:00 | 33 | 31
2019-02-04 17:30 | 34 | 33
2019-02-04 18:00 | 35 | 33
2019-02-04 18:30 | 36 | 34
2019-02-04 19:00 | 36 | 35
2019-02-04 19:30 | 37 | 35
2019-02-04 20:00 | 37 | 35
2019-02-04 20:30 | 37 | 35
2019-02-04 21:00 | 35 | 33
2019-02-04 21:30 | 33 | 31
2019-02-04 22:00 | 33 | 32
2019-02-04 22:30 | 29 | 28
2019-02-04 23:00 | 28 | 27
2019-02-04 23:30 | 29 | 27
2019-02-05 | 27 | 25
2019-02-05 00:30 | 27 | 25
2019-02-05 01:00 | 29 | 25
2019-02-05 01:30 | 30 | 25
2019-02-05 02:00 | 30 | 25
2019-02-05 02:30 | 30 | 25
2019-02-05 03:00 | 30 | 25
2019-02-05 03:30 | 30 | 26
2019-02-05 04:00 | 30 | 25
2019-02-05 04:30 | 30 | 25
2019-02-05 05:00 | 30 | 25
2019-02-05 05:30 | 30 | 26
2019-02-05 06:00 | 29 | 24
2019-02-05 06:30 | 29 | 25
2019-02-05 07:00 | 28 | 25
2019-02-05 07:30 | 28 | 25
2019-02-05 08:00 | 28 | 26
2019-02-05 08:30 | 28 | 26
2019-02-05 09:00 | 28 | 26
2019-02-05 09:30 | 24 | 22
2019-02-05 10:00 | 22 | 20
2019-02-05 10:30 | 19 | 18
2019-02-05 11:00 | 20 | 20
2019-02-05 11:30 | 22 | 22
2019-02-05 12:00 | 16 | 16
2019-02-05 12:30 | 16 | 16
2019-02-05 13:00 | 17 | 17
2019-02-05 13:30 | 18 | 18
2019-02-05 14:00 | 17 | 17
2019-02-05 14:30 | 16 | 16
2019-02-05 15:00 | 32 | 31
2019-02-05 15:30 | 37 | 36
2019-02-05 16:00 | 44 | 42
2019-02-05 16:30 | 45 | 44
2019-02-05 17:00 | 47 | 45
2019-02-05 17:30 | 47 | 46
2019-02-05 18:00 | 49 | 48
2019-02-05 18:30 | 51 | 50
2019-02-05 19:00 | 51 | 50
2019-02-05 19:30 | 51 | 50
2019-02-05 20:00 | 51 | 50
2019-02-05 20:30 | 50 | 48
2019-02-05 21:00 | 49 | 48
2019-02-05 21:30 | 50 | 49
2019-02-05 22:00 | 48 | 48
2019-02-05 22:30 | 48 | 47
2019-02-05 23:00 | 47 | 47
2019-02-05 23:30 | 46 | 45
2019-02-06 | 46 | 46
2019-02-06 00:30 | 47 | 46
2019-02-06 01:00 | 47 | 47
2019-02-06 01:30 | 48 | 47
2019-02-06 02:00 | 47 | 47
2019-02-06 02:30 | 47 | 47
2019-02-06 03:00 | 47 | 47
2019-02-06 03:30 | 47 | 46
2019-02-06 04:00 | 47 | 47
2019-02-06 04:30 | 47 | 47
2019-02-06 05:00 | 47 | 46
2019-02-06 05:30 | 47 | 46
2019-02-06 06:00 | 47 | 46
2019-02-06 06:30 | 47 | 46
2019-02-06 07:00 | 47 | 46
2019-02-06 07:30 | 48 | 47
2019-02-06 08:00 | 49 | 48
2019-02-06 08:30 | 49 | 48
2019-02-06 09:00 | 50 | 49
2019-02-06 09:30 | 51 | 49
2019-02-06 10:00 | 48 | 47
2019-02-06 10:30 | 46 | 45
2019-02-06 11:00 | 47 | 45
2019-02-06 11:30 | 41 | 39
2019-02-06 12:00 | 40 | 38
2019-02-06 12:30 | 39 | 37
2019-02-06 13:00 | 44 | 43
2019-02-06 13:30 | 42 | 40
2019-02-06 14:00 | 38 | 37
2019-02-06 14:30 | 38 | 36
2019-02-06 15:00 | 29 | 28
2019-02-06 15:30 | 29 | 28
2019-02-06 16:00 | 34 | 34
2019-02-06 16:30 | 34 | 34
2019-02-06 17:00 | 37 | 36
2019-02-06 17:30 | 38 | 38
2019-02-06 18:00 | 40 | 39
2019-02-06 18:30 | 41 | 41
2019-02-06 19:00 | 42 | 42
2019-02-06 19:30 | 45 | 45
2019-02-06 20:00 | 44 | 44
2019-02-06 20:30 | 45 | 45
2019-02-06 21:00 | 43 | 43
2019-02-06 21:30 | 43 | 43
2019-02-06 22:00 | 55 | 54
2019-02-06 22:30 | 52 | 51
2019-02-06 23:00 | 51 | 50
2019-02-06 23:30 | 50 | 49
2019-02-07 | 48 | 48
2019-02-07 00:30 | 47 | 47
2019-02-07 01:00 | 48 | 47
2019-02-07 01:30 | 48 | 48
2019-02-07 02:00 | 49 | 48
2019-02-07 02:30 | 49 | 48
2019-02-07 03:00 | 47 | 46
2019-02-07 03:30 | 47 | 46
2019-02-07 04:00 | 47 | 46
2019-02-07 04:30 | 47 | 47
2019-02-07 05:00 | 48 | 47
2019-02-07 05:30 | 48 | 47
2019-02-07 06:00 | 48 | 48
2019-02-07 06:30 | 48 | 47
2019-02-07 07:00 | 48 | 47
2019-02-07 07:30 | 51 | 49
2019-02-07 08:00 | 52 | 50
2019-02-07 08:30 | 51 | 49
2019-02-07 09:00 | 45 | 43
2019-02-07 09:30 | 45 | 42
2019-02-07 10:00 | 45 | 42
2019-02-07 10:30 | 49 | 47
2019-02-07 11:00 | 49 | 48
2019-02-07 11:30 | 46 | 46
2019-02-07 12:00 | 47 | 46
2019-02-07 12:30 | 54 | 53
2019-02-07 13:00 | 55 | 54
2019-02-07 13:30 | 58 | 58
2019-02-07 14:00 | 58 | 58
2019-02-07 14:30 | 58 | 58
2019-02-07 15:00 | 61 | 61
2019-02-07 15:30 | 62 | 62
2019-02-07 16:00 | 61 | 61
2019-02-07 16:30 | 61 | 61
2019-02-07 17:00 | 60 | 60
2019-02-07 17:30 | 62 | 62
2019-02-07 18:00 | 63 | 63
2019-02-07 18:30 | 64 | 64
2019-02-07 19:00 | 65 | 65
2019-02-07 19:30 | 65 | 65
2019-02-07 20:00 | 66 | 66
2019-02-07 20:30 | 65 | 65
2019-02-07 21:00 | 63 | 63
2019-02-07 21:30 | 61 | 61
2019-02-07 22:00 | 60 | 60
2019-02-07 22:30 | 56 | 56
2019-02-07 23:00 | 55 | 55
2019-02-07 23:30 | 54 | 54
2019-02-08 | 53 | 53
2019-02-08 00:30 | 56 | 56
2019-02-08 01:00 | 59 | 58
2019-02-08 01:30 | 59 | 59
2019-02-08 02:00 | 59 | 59
2019-02-08 02:30 | 59 | 59
2019-02-08 03:00 | 60 | 60
2019-02-08 03:30 | 61 | 60
2019-02-08 04:00 | 60 | 59
2019-02-08 04:30 | 60 | 59
2019-02-08 05:00 | 59 | 59
2019-02-08 05:30 | 60 | 60
2019-02-08 06:00 | 60 | 60
2019-02-08 06:30 | 59 | 59
2019-02-08 07:00 | 58 | 57
2019-02-08 07:30 | 59 | 58
2019-02-08 08:00 | 57 | 57
2019-02-08 08:30 | 56 | 55
2019-02-08 09:00 | 56 | 55
2019-02-08 09:30 | 52 | 51
2019-02-08 10:00 | 53 | 52
2019-02-08 10:30 | 51 | 50
2019-02-08 11:00 | 47 | 44
2019-02-08 11:30 | 52 | 51
2019-02-08 12:00 | 46 | 43
2019-02-08 12:30 | 52 | 51
2019-02-08 13:00 | 54 | 54
2019-02-08 13:30 | 55 | 55
2019-02-08 14:00 | 52 | 51
2019-02-08 14:30 | 56 | 55
2019-02-08 15:00 | 62 | 61
2019-02-08 15:30 | 65 | 64
2019-02-08 16:00 | 68 | 67
2019-02-08 16:30 | 68 | 67
2019-02-08 17:00 | 68 | 67
2019-02-08 17:30 | 67 | 66
2019-02-08 18:00 | 70 | 69
2019-02-08 18:30 | 72 | 71
2019-02-08 19:00 | 73 | 72
2019-02-08 19:30 | 74 | 72
2019-02-08 20:00 | 73 | 73
2019-02-08 20:30 | 71 | 70
2019-02-08 21:00 | 71 | 69
2019-02-08 21:30 | 70 | 69
2019-02-08 22:00 | 70 | 68
2019-02-08 22:30 | 70 | 68
2019-02-08 23:00 | 69 | 66
2019-02-08 23:30 | 68 | 65
2019-02-09 | 57 | 56
2019-02-09 00:30 | 54 | 54
2019-02-09 01:00 | 56 | 55
2019-02-09 01:30 | 55 | 54
2019-02-09 02:00 | 54 | 54
2019-02-09 02:30 | 54 | 54
2019-02-09 03:00 | 60 | 60
2019-02-09 03:30 | 63 | 63
2019-02-09 04:00 | 62 | 62
2019-02-09 04:30 | 62 | 62
2019-02-09 05:00 | 62 | 62
2019-02-09 05:30 | 62 | 62
2019-02-09 06:00 | 61 | 61
2019-02-09 06:30 | 52 | 52
2019-02-09 07:00 | 51 | 51
2019-02-09 07:30 | 53 | 53
2019-02-09 08:00 | 62 | 62
2019-02-09 08:30 | 63 | 63
2019-02-09 09:00 | 63 | 63
2019-02-09 09:30 | 59 | 59
2019-02-09 10:00 | 52 | 52
2019-02-09 10:30 | 54 | 54
2019-02-09 11:00 | 55 | 55
2019-02-09 11:30 | 58 | 58
2019-02-09 12:00 | 56 | 56
2019-02-09 12:30 | 57 | 57
2019-02-09 13:00 | 57 | 57
2019-02-09 13:30 | 56 | 56
2019-02-09 14:00 | 51 | 51
2019-02-09 14:30 | 49 | 49
2019-02-09 15:00 | 42 | 42
2019-02-09 15:30 | 41 | 41
2019-02-09 16:00 | 41 | 41
2019-02-09 16:30 | 41 | 41
2019-02-09 17:00 | 44 | 44
2019-02-09 17:30 | 47 | 47
2019-02-09 18:00 | 48 | 48
2019-02-09 18:30 | 54 | 54
2019-02-09 19:00 | 60 | 60
2019-02-09 19:30 | 60 | 60
2019-02-09 20:00 | 64 | 59
2019-02-09 20:30 | 65 | 59
2019-02-09 21:00 | 66 | 61
2019-02-09 21:30 | 68 | 63
2019-02-09 22:00 | 71 | 68
2019-02-09 22:30 | 69 | 66
2019-02-09 23:00 | 66 | 66
2019-02-09 23:30 | 61 | 61
2019-02-10 | 54 | 54
2019-02-10 00:30 | 54 | 54
2019-02-10 01:00 | 57 | 57
2019-02-10 01:30 | 57 | 57
2019-02-10 02:00 | 58 | 58
2019-02-10 02:30 | 56 | 56
2019-02-10 03:00 | 56 | 56
2019-02-10 03:30 | 58 | 58
2019-02-10 04:00 | 56 | 56
2019-02-10 04:30 | 54 | 54
2019-02-10 05:00 | 53 | 53
2019-02-10 05:30 | 55 | 55
2019-02-10 06:00 | 55 | 55
2019-02-10 06:30 | 54 | 54
2019-02-10 07:00 | 52 | 52
2019-02-10 07:30 | 52 | 52
2019-02-10 08:00 | 52 | 52
2019-02-10 08:30 | 53 | 53
2019-02-10 09:00 | 52 | 52
2019-02-10 09:30 | 50 | 50
2019-02-10 10:00 | 51 | 50
2019-02-10 10:30 | 49 | 49
2019-02-10 11:00 | 48 | 48
2019-02-10 11:30 | 48 | 48
2019-02-10 12:00 | 49 | 49
2019-02-10 12:30 | 50 | 49
2019-02-10 13:00 | 51 | 51
2019-02-10 13:30 | 52 | 51
2019-02-10 14:00 | 51 | 50
2019-02-10 14:30 | 51 | 50
2019-02-10 15:00 | 51 | 50
2019-02-10 15:30 | 50 | 49
2019-02-10 16:00 | 55 | 55
2019-02-10 16:30 | 61 | 60
2019-02-10 17:00 | 65 | 65
2019-02-10 17:30 | 56 | 56
2019-02-10 18:00 | 70 | 69
2019-02-10 18:30 | 73 | 72
2019-02-10 19:00 | 68 | 68
2019-02-10 19:30 | 70 | 68
2019-02-10 20:00 | 70 | 67
2019-02-10 20:30 | 73 | 71
2019-02-10 21:00 | 73 | 71
2019-02-10 21:30 | 72 | 70
2019-02-10 22:00 | 72 | 69
2019-02-10 22:30 | 70 | 68
2019-02-10 23:00 | 70 | 67
2019-02-10 23:30 | 69 | 66
2019-02-11 | 65 | 64
2019-02-11 00:30 | 65 | 65
2019-02-11 01:00 | 64 | 64
2019-02-11 01:30 | 65 | 64
2019-02-11 02:00 | 65 | 64
2019-02-11 02:30 | 65 | 64
2019-02-11 03:00 | 64 | 64
2019-02-11 03:30 | 64 | 63
2019-02-11 04:00 | 63 | 63
2019-02-11 04:30 | 62 | 62
2019-02-11 05:00 | 62 | 62
2019-02-11 05:30 | 63 | 63
2019-02-11 06:00 | 63 | 63
2019-02-11 06:30 | 64 | 63
2019-02-11 07:00 | 64 | 62
2019-02-11 07:30 | 61 | 61
2019-02-11 08:00 | 59 | 59
2019-02-11 08:30 | 57 | 57
2019-02-11 09:00 | 54 | 54
2019-02-11 09:30 | 52 | 51
2019-02-11 10:00 | 48 | 47
2019-02-11 10:30 | 41 | 37
2019-02-11 11:00 | 42 | 37
2019-02-11 11:30 | 44 | 39
2019-02-11 12:00 | 43 | 37
2019-02-11 12:30 | 41 | 35
2019-02-11 13:00 | 42 | 36
2019-02-11 13:30 | 42 | 36
2019-02-11 14:00 | 42 | 36
2019-02-11 14:30 | 45 | 39
2019-02-11 15:00 | 48 | 43
2019-02-11 15:30 | 51 | 47
2019-02-11 16:00 | 53 | 49
2019-02-11 16:30 | 63 | 61
2019-02-11 17:00 | 69 | 68
2019-02-11 17:30 | 70 | 69
2019-02-11 18:00 | 70 | 68
2019-02-11 18:30 | 70 | 67
2019-02-11 19:00 | 73 | 70
2019-02-11 19:30 | 74 | 70
2019-02-11 20:00 | 73 | 69
2019-02-11 20:30 | 78 | 76
2019-02-11 21:00 | 77 | 75
2019-02-11 21:30 | 77 | 76
2019-02-11 22:00 | 74 | 73
2019-02-11 22:30 | 74 | 73
2019-02-11 23:00 | 74 | 73
2019-02-11 23:30 | 69 | 68
2019-02-12 | 67 | 66
2019-02-12 00:30 | 66 | 65
2019-02-12 01:00 | 66 | 65
2019-02-12 01:30 | 66 | 65
2019-02-12 02:00 | 66 | 65
2019-02-12 02:30 | 66 | 65
2019-02-12 03:00 | 66 | 65
2019-02-12 03:30 | 67 | 65
2019-02-12 04:00 | 67 | 65
2019-02-12 04:30 | 65 | 65
2019-02-12 05:00 | 65 | 65
2019-02-12 05:30 | 66 | 65
2019-02-12 06:00 | 64 | 63
2019-02-12 06:30 | 66 | 65
2019-02-12 07:00 | 66 | 65
2019-02-12 07:30 | 63 | 62
2019-02-12 08:00 | 61 | 60
2019-02-12 08:30 | 57 | 56
2019-02-12 09:00 | 52 | 51
2019-02-12 09:30 | 50 | 49
2019-02-12 10:00 | 48 | 46
2019-02-12 10:30 | 47 | 45
2019-02-12 11:00 | 48 | 46
2019-02-12 11:30 | 49 | 47
2019-02-12 12:00 | 48 | 46
2019-02-12 12:30 | 49 | 47
2019-02-12 13:00 | 50 | 49
2019-02-12 13:30 | 48 | 48
2019-02-12 14:00 | 52 | 51
2019-02-12 14:30 | 51 | 51
2019-02-12 15:00 | 53 | 52
2019-02-12 15:30 | 46 | 46
2019-02-12 16:00 | 43 | 43
2019-02-12 16:30 | 49 | 49
2019-02-12 17:00 | 51 | 51
2019-02-12 17:30 | 54 | 54
2019-02-12 18:00 | 60 | 59
2019-02-12 18:30 | 62 | 61
2019-02-12 19:00 | 48 | 47
2019-02-12 19:30 | 51 | 50
2019-02-12 20:00 | 63 | 63
2019-02-12 20:30 | 61 | 61
2019-02-12 21:00 | 64 | 64
2019-02-12 21:30 | 70 | 70
2019-02-12 22:00 | 70 | 70
2019-02-12 22:30 | 68 | 67
2019-02-12 23:00 | 67 | 67
2019-02-12 23:30 | 66 | 66
2019-02-13 | 65 | 65
2019-02-13 00:30 | 65 | 64
2019-02-13 01:00 | 65 | 64
2019-02-13 01:30 | 64 | 64
2019-02-13 02:00 | 65 | 65
2019-02-13 02:30 | 64 | 64
2019-02-13 03:00 | 63 | 63
2019-02-13 03:30 | 63 | 63
2019-02-13 04:00 | 63 | 63
2019-02-13 04:30 | 63 | 63
2019-02-13 05:00 | 63 | 63
2019-02-13 05:30 | 65 | 64
2019-02-13 06:00 | 64 | 63
2019-02-13 06:30 | 56 | 56
2019-02-13 07:00 | 56 | 56
2019-02-13 07:30 | 62 | 61
2019-02-13 08:00 | 60 | 59
2019-02-13 08:30 | 57 | 57
2019-02-13 09:00 | 53 | 53
2019-02-13 09:30 | 50 | 50
2019-02-13 10:00 | 49 | 49
2019-02-13 10:30 | 48 | 48
2019-02-13 11:00 | 47 | 46
2019-02-13 11:30 | 47 | 47
2019-02-13 12:00 | 45 | 45
2019-02-13 12:30 | 47 | 47
2019-02-13 13:00 | 48 | 47
2019-02-13 13:30 | 49 | 48
2019-02-13 14:00 | 50 | 50
2019-02-13 14:30 | 50 | 50
2019-02-13 15:00 | 51 | 51
2019-02-13 15:30 | 47 | 47
2019-02-13 16:00 | 42 | 42
2019-02-13 16:30 | 28 | 26
2019-02-13 17:00 | 58 | 52
2019-02-13 17:30 | 58 | 51
2019-02-13 18:00 | 53 | 46
2019-02-13 18:30 | 49 | 42
2019-02-13 19:00 | 48 | 41
2019-02-13 19:30 | 46 | 41
2019-02-13 20:00 | 47 | 42
2019-02-13 20:30 | 46 | 41
2019-02-13 21:00 | 44 | 38
2019-02-13 21:30 | 18 | 4
2019-02-13 22:00 | 40 | 32
2019-02-13 22:30 | 41 | 38
2019-02-13 23:00 | 68 | 67
2019-02-13 23:30 | 66 | 66
2019-02-14 | 66 | 65
2019-02-14 00:30 | 65 | 64
2019-02-14 01:00 | 64 | 64
2019-02-14 01:30 | 64 | 64
2019-02-14 02:00 | 64 | 64
2019-02-14 02:30 | 63 | 63
2019-02-14 03:00 | 64 | 63
2019-02-14 03:30 | 64 | 63
2019-02-14 04:00 | 64 | 64
2019-02-14 04:30 | 64 | 63
2019-02-14 05:00 | 64 | 64
2019-02-14 05:30 | 64 | 64
2019-02-14 06:00 | 66 | 66
2019-02-14 06:30 | 67 | 67
2019-02-14 07:00 | 68 | 67
2019-02-14 07:30 | 66 | 65
2019-02-14 08:00 | 62 | 61
2019-02-14 08:30 | 58 | 57
2019-02-14 09:00 | 55 | 54
2019-02-14 09:30 | 52 | 51
2019-02-14 10:00 | 52 | 51
2019-02-14 10:30 | 51 | 50
2019-02-14 11:00 | 50 | 49
2019-02-14 11:30 | 48 | 46
2019-02-14 12:00 | 46 | 45
2019-02-14 12:30 | 47 | 45
2019-02-14 13:00 | 49 | 47
2019-02-14 13:30 | 47 | 46
2019-02-14 14:00 | 49 | 47
2019-02-14 14:30 | 49 | 46
2019-02-14 15:00 | 51 | 48
2019-02-14 15:30 | 54 | 51
2019-02-14 16:00 | 53 | 51
2019-02-14 16:30 | 54 | 52
2019-02-14 17:00 | 57 | 55
2019-02-14 17:30 | 60 | 60
2019-02-14 18:00 | 66 | 66
2019-02-14 18:30 | 68 | 68
2019-02-14 19:00 | 71 | 71
2019-02-14 19:30 | 73 | 72
2019-02-14 20:00 | 72 | 71
2019-02-14 20:30 | 72 | 71
2019-02-14 21:00 | 75 | 74
2019-02-14 21:30 | 76 | 76
2019-02-14 22:00 | 75 | 74
2019-02-14 22:30 | 74 | 73
2019-02-14 23:00 | 72 | 71
2019-02-14 23:30 | 72 | 71
2019-02-15 | 69 | 68
2019-02-15 00:30 | 69 | 68
2019-02-15 01:00 | 68 | 67
2019-02-15 01:30 | 67 | 66
2019-02-15 02:00 | 67 | 66
2019-02-15 02:30 | 67 | 65
2019-02-15 03:00 | 67 | 66
2019-02-15 03:30 | 67 | 66
2019-02-15 04:00 | 68 | 66
2019-02-15 04:30 | 70 | 68
2019-02-15 05:00 | 71 | 69
2019-02-15 05:30 | 71 | 69
2019-02-15 06:00 | 69 | 67
2019-02-15 06:30 | 69 | 68
2019-02-15 07:00 | 68 | 67
2019-02-15 07:30 | 65 | 65
2019-02-15 08:00 | 61 | 61
2019-02-15 08:30 | 57 | 56
2019-02-15 09:00 | 47 | 46
2019-02-15 09:30 | 43 | 42
2019-02-15 10:00 | 32 | 31
2019-02-15 10:30 | 30 | 29
2019-02-15 11:00 | 27 | 26
2019-02-15 11:30 | 28 | 27
2019-02-15 12:00 | 28 | 27
2019-02-15 12:30 | 28 | 28
2019-02-15 13:00 | 28 | 28
2019-02-15 13:30 | 32 | 31
2019-02-15 14:00 | 34 | 34
2019-02-15 14:30 | 39 | 38
2019-02-15 15:00 | 40 | 39
2019-02-15 15:30 | 39 | 38
2019-02-15 16:00 | 41 | 40
2019-02-15 16:30 | 35 | 35
2019-02-15 17:00 | 42 | 41
2019-02-15 17:30 | 49 | 48
2019-02-15 18:00 | 51 | 51
2019-02-15 18:30 | 53 | 53
2019-02-15 19:00 | 56 | 56
2019-02-15 19:30 | 56 | 56
2019-02-15 20:00 | 56 | 56
2019-02-15 20:30 | 56 | 56
2019-02-15 21:00 | 56 | 56
2019-02-15 21:30 | 66 | 65
2019-02-15 22:00 | 69 | 68
2019-02-15 22:30 | 68 | 68
2019-02-15 23:00 | 67 | 66
2019-02-15 23:30 | 66 | 65
2019-02-16 | 65 | 64
2019-02-16 00:30 | 64 | 64
2019-02-16 01:00 | 64 | 63
2019-02-16 01:30 | 66 | 65
2019-02-16 02:00 | 65 | 65
2019-02-16 02:30 | 65 | 65
2019-02-16 03:00 | 66 | 65
2019-02-16 03:30 | 66 | 66
2019-02-16 04:00 | 67 | 67
2019-02-16 04:30 | 66 | 66
2019-02-16 05:00 | 66 | 66
2019-02-16 05:30 | 66 | 66
2019-02-16 06:00 | 66 | 66
2019-02-16 06:30 | 64 | 64
2019-02-16 07:00 | 61 | 61
2019-02-16 07:30 | 58 | 57
2019-02-16 08:00 | 52 | 52
2019-02-16 08:30 | 49 | 48
2019-02-16 09:00 | 47 | 46
2019-02-16 09:30 | 47 | 47
2019-02-16 10:00 | 52 | 52
2019-02-16 10:30 | 51 | 51
2019-02-16 11:00 | 43 | 43
2019-02-16 11:30 | 43 | 43
2019-02-16 12:00 | 51 | 51
2019-02-16 12:30 | 52 | 51
2019-02-16 13:00 | 45 | 45
2019-02-16 13:30 | 41 | 41
2019-02-16 14:00 | 43 | 42
2019-02-16 14:30 | 46 | 45
2019-02-16 15:00 | 42 | 42
2019-02-16 15:30 | 45 | 44
2019-02-16 16:00 | 46 | 46
2019-02-16 16:30 | 43 | 43
2019-02-16 17:00 | 51 | 51
2019-02-16 17:30 | 48 | 48
2019-02-16 18:00 | 51 | 50
2019-02-16 18:30 | 53 | 53
2019-02-16 19:00 | 54 | 54
2019-02-16 19:30 | 56 | 56
2019-02-16 20:00 | 56 | 56
2019-02-16 20:30 | 55 | 55
2019-02-16 21:00 | 54 | 54
2019-02-16 21:30 | 62 | 62
2019-02-16 22:00 | 68 | 67
2019-02-16 22:30 | 68 | 67
2019-02-16 23:00 | 67 | 66
2019-02-16 23:30 | 66 | 66
2019-02-17 | 66 | 65
2019-02-17 00:30 | 65 | 64
2019-02-17 01:00 | 65 | 64
2019-02-17 01:30 | 68 | 68
2019-02-17 02:00 | 68 | 67
2019-02-17 02:30 | 66 | 66
2019-02-17 03:00 | 66 | 66
2019-02-17 03:30 | 66 | 65
2019-02-17 04:00 | 66 | 66
2019-02-17 04:30 | 66 | 66
2019-02-17 05:00 | 66 | 65
2019-02-17 05:30 | 66 | 64
2019-02-17 06:00 | 65 | 63
2019-02-17 06:30 | 61 | 59
2019-02-17 07:00 | 62 | 60
2019-02-17 07:30 | 61 | 59
2019-02-17 08:00 | 56 | 55
2019-02-17 08:30 | 48 | 47
2019-02-17 09:00 | 44 | 43
2019-02-17 09:30 | 45 | 44
2019-02-17 10:00 | 48 | 48
2019-02-17 10:30 | 45 | 45
2019-02-17 11:00 | 51 | 50
2019-02-17 11:30 | 41 | 41
2019-02-17 12:00 | 46 | 46
2019-02-17 12:30 | 49 | 49
2019-02-17 13:00 | 52 | 52
2019-02-17 13:30 | 59 | 58
2019-02-17 14:00 | 47 | 46
2019-02-17 14:30 | 55 | 54
2019-02-17 15:00 | 40 | 40
2019-02-17 15:30 | 41 | 41
2019-02-17 16:00 | 48 | 48
2019-02-17 16:30 | 35 | 35
2019-02-17 17:00 | 41 | 40
2019-02-17 17:30 | 44 | 44
2019-02-17 18:00 | 52 | 52
2019-02-17 18:30 | 54 | 54
2019-02-17 19:00 | 55 | 55
2019-02-17 19:30 | 56 | 56
2019-02-17 20:00 | 55 | 55
2019-02-17 20:30 | 60 | 60
2019-02-17 21:00 | 69 | 69
2019-02-17 21:30 | 68 | 67
2019-02-17 22:00 | 68 | 67
2019-02-17 22:30 | 67 | 66
2019-02-17 23:00 | 65 | 65
2019-02-17 23:30 | 64 | 64
2019-02-18 | 68 | 67
2019-02-18 00:30 | 68 | 67
2019-02-18 01:00 | 67 | 67
2019-02-18 01:30 | 66 | 66
2019-02-18 02:00 | 66 | 65
2019-02-18 02:30 | 66 | 65
2019-02-18 03:00 | 65 | 65
2019-02-18 03:30 | 65 | 64
2019-02-18 04:00 | 64 | 64
2019-02-18 04:30 | 65 | 65
2019-02-18 05:00 | 65 | 65
2019-02-18 05:30 | 65 | 65
2019-02-18 06:00 | 65 | 65
2019-02-18 06:30 | 63 | 62
2019-02-18 07:00 | 63 | 62
2019-02-18 07:30 | 61 | 60
2019-02-18 08:00 | 58 | 56
2019-02-18 08:30 | 55 | 53
2019-02-18 09:00 | 51 | 50
2019-02-18 09:30 | 47 | 45
2019-02-18 10:00 | 44 | 42
2019-02-18 10:30 | 43 | 42
2019-02-18 11:00 | 40 | 38
2019-02-18 11:30 | 40 | 38
2019-02-18 12:00 | 41 | 40
2019-02-18 12:30 | 40 | 39
2019-02-18 13:00 | 41 | 39
2019-02-18 13:30 | 41 | 40
2019-02-18 14:00 | 38 | 37
2019-02-18 14:30 | 42 | 40
2019-02-18 15:00 | 42 | 41
2019-02-18 15:30 | 47 | 45
2019-02-18 16:00 | 48 | 48
2019-02-18 16:30 | 47 | 46
2019-02-18 17:00 | 51 | 50
2019-02-18 17:30 | 49 | 48
2019-02-18 18:00 | 54 | 53
2019-02-18 18:30 | 58 | 57
2019-02-18 19:00 | 59 | 59
2019-02-18 19:30 | 60 | 60
2019-02-18 20:00 | 59 | 59
2019-02-18 20:30 | 59 | 59
2019-02-18 21:00 | 61 | 61
2019-02-18 21:30 | 72 | 71
2019-02-18 22:00 | 71 | 70
2019-02-18 22:30 | 69 | 68
2019-02-18 23:00 | 68 | 67
2019-02-18 23:30 | 68 | 67
2019-02-19 | 67 | 66
2019-02-19 00:30 | 66 | 66
2019-02-19 01:00 | 66 | 66
2019-02-19 01:30 | 67 | 66
2019-02-19 02:00 | 70 | 69
2019-02-19 02:30 | 70 | 69
2019-02-19 03:00 | 70 | 69
2019-02-19 03:30 | 69 | 68
2019-02-19 04:00 | 70 | 69
2019-02-19 04:30 | 70 | 69
2019-02-19 05:00 | 67 | 66
2019-02-19 05:30 | 52 | 52
2019-02-19 06:00 | 41 | 40
2019-02-19 06:30 | 35 | 33
2019-02-19 07:00 | 35 | 34
2019-02-19 07:30 | 33 | 32
2019-02-19 08:00 | 31 | 31
2019-02-19 08:30 | 31 | 30
2019-02-19 09:00 | 29 | 29
2019-02-19 09:30 | 23 | 22
2019-02-19 10:00 | 19 | 18
2019-02-19 10:30 | 20 | 19
2019-02-19 11:00 | 18 | 17
2019-02-19 11:30 | 16 | 15
2019-02-19 12:00 | 15 | 14
2019-02-19 12:30 | 14 | 13
2019-02-19 13:00 | 15 | 14
2019-02-19 13:30 | 16 | 14
2019-02-19 14:00 | 17 | 16
2019-02-19 14:30 | 18 | 17
2019-02-19 15:00 | 19 | 18
2019-02-19 15:30 | 23 | 22
2019-02-19 16:00 | 31 | 29
2019-02-19 16:30 | 31 | 30
2019-02-19 17:00 | 40 | 39
2019-02-19 17:30 | 41 | 41
2019-02-19 18:00 | 43 | 42
2019-02-19 18:30 | 47 | 46
2019-02-19 19:00 | 52 | 52
2019-02-19 19:30 | 58 | 50
2019-02-19 20:00 | 63 | 57
2019-02-19 20:30 | 76 | 74
2019-02-19 21:00 | 76 | 73
2019-02-19 21:30 | 80 | 78
2019-02-19 22:00 | 78 | 77
2019-02-19 22:30 | 77 | 76
2019-02-19 23:00 | 76 | 75
2019-02-19 23:30 | 74 | 74
2019-02-20 | 74 | 73
2019-02-20 00:30 | 72 | 71
2019-02-20 01:00 | 72 | 71
2019-02-20 01:30 | 72 | 71
2019-02-20 02:00 | 71 | 70
2019-02-20 02:30 | 72 | 71
2019-02-20 03:00 | 72 | 70
2019-02-20 03:30 | 71 | 70
2019-02-20 04:00 | 71 | 70
2019-02-20 04:30 | 71 | 70
2019-02-20 05:00 | 71 | 69
2019-02-20 05:30 | 71 | 69
2019-02-20 06:00 | 70 | 69
2019-02-20 06:30 | 70 | 68
2019-02-20 07:00 | 68 | 67
2019-02-20 07:30 | 71 | 70
2019-02-20 08:00 | 68 | 67
2019-02-20 08:30 | 65 | 63
2019-02-20 09:00 | 61 | 60
2019-02-20 09:30 | 63 | 62
2019-02-20 10:00 | 60 | 59
2019-02-20 10:30 | 59 | 59
2019-02-20 11:00 | 59 | 59
2019-02-20 11:30 | 57 | 57
2019-02-20 12:00 | 57 | 57
2019-02-20 12:30 | 59 | 59
2019-02-20 13:00 | 58 | 58
2019-02-20 13:30 | 57 | 57
2019-02-20 14:00 | 57 | 56
2019-02-20 14:30 | 57 | 57
2019-02-20 15:00 | 57 | 57
2019-02-20 15:30 | 52 | 52
2019-02-20 16:00 | 55 | 55
2019-02-20 16:30 | 57 | 56
2019-02-20 17:00 | 60 | 59
2019-02-20 17:30 | 64 | 64
2019-02-20 18:00 | 68 | 67
2019-02-20 18:30 | 70 | 70
2019-02-20 19:00 | 74 | 73
2019-02-20 19:30 | 75 | 73
2019-02-20 20:00 | 75 | 73
2019-02-20 20:30 | 75 | 72
2019-02-20 21:00 | 72 | 69
2019-02-20 21:30 | 82 | 81
2019-02-20 22:00 | 79 | 78
2019-02-20 22:30 | 82 | 74
2019-02-20 23:00 | 80 | 71
2019-02-20 23:30 | 80 | 71
2019-02-21 | 72 | 69
2019-02-21 00:30 | 71 | 69
2019-02-21 01:00 | 71 | 70
2019-02-21 01:30 | 71 | 69
2019-02-21 02:00 | 71 | 69
2019-02-21 02:30 | 71 | 69
2019-02-21 03:00 | 70 | 69
2019-02-21 03:30 | 70 | 68
2019-02-21 04:00 | 69 | 68
2019-02-21 04:30 | 69 | 68
2019-02-21 05:00 | 70 | 68
2019-02-21 05:30 | 71 | 69
2019-02-21 06:00 | 70 | 69
2019-02-21 06:30 | 68 | 67
2019-02-21 07:00 | 66 | 66
2019-02-21 07:30 | 65 | 64
2019-02-21 08:00 | 61 | 61
2019-02-21 08:30 | 58 | 57
2019-02-21 09:00 | 53 | 53
2019-02-21 09:30 | 49 | 49
2019-02-21 10:00 | 47 | 46
2019-02-21 10:30 | 46 | 45
2019-02-21 11:00 | 46 | 45
2019-02-21 11:30 | 45 | 45
2019-02-21 12:00 | 47 | 46
2019-02-21 12:30 | 47 | 46
2019-02-21 13:00 | 44 | 44
2019-02-21 13:30 | 45 | 44
2019-02-21 14:00 | 45 | 44
2019-02-21 14:30 | 44 | 43
2019-02-21 15:00 | 46 | 45
2019-02-21 15:30 | 50 | 49
2019-02-21 16:00 | 55 | 54
2019-02-21 16:30 | 48 | 46
2019-02-21 17:00 | 53 | 50
2019-02-21 17:30 | 58 | 56
2019-02-21 18:00 | 62 | 60
2019-02-21 18:30 | 64 | 62
2019-02-21 19:00 | 68 | 63
2019-02-21 19:30 | 68 | 64
2019-02-21 20:00 | 68 | 64
2019-02-21 20:30 | 68 | 63
2019-02-21 21:00 | 67 | 62
2019-02-21 21:30 | 76 | 75
2019-02-21 22:00 | 79 | 77
2019-02-21 22:30 | 76 | 74
2019-02-21 23:00 | 75 | 73
2019-02-21 23:30 | 75 | 73
2019-02-22 | 75 | 72
2019-02-22 00:30 | 74 | 72
2019-02-22 01:00 | 72 | 71
2019-02-22 01:30 | 73 | 71
2019-02-22 02:00 | 72 | 70
2019-02-22 02:30 | 71 | 70
2019-02-22 03:00 | 71 | 69
2019-02-22 03:30 | 72 | 70
2019-02-22 04:00 | 72 | 70
2019-02-22 04:30 | 71 | 69
2019-02-22 05:00 | 71 | 69
2019-02-22 05:30 | 70 | 68
2019-02-22 06:00 | 70 | 68
2019-02-22 06:30 | 70 | 68
2019-02-22 07:00 | 69 | 67
2019-02-22 07:30 | 67 | 65
2019-02-22 08:00 | 63 | 62
2019-02-22 08:30 | 67 | 66
2019-02-22 09:00 | 64 | 63
2019-02-22 09:30 | 64 | 63
2019-02-22 10:00 | 67 | 66
2019-02-22 10:30 | 59 | 58
2019-02-22 11:00 | 47 | 46
2019-02-22 11:30 | 45 | 44
2019-02-22 12:00 | 52 | 51
2019-02-22 12:30 | 51 | 50
2019-02-22 13:00 | 52 | 52
2019-02-22 13:30 | 52 | 51
2019-02-22 14:00 | 48 | 47
2019-02-22 14:30 | 49 | 48
2019-02-22 15:00 | 47 | 46
2019-02-22 15:30 | 54 | 54
2019-02-22 16:00 | 58 | 57
2019-02-22 16:30 | 66 | 66
2019-02-22 17:00 | 69 | 68
2019-02-22 17:30 | 72 | 72
2019-02-22 18:00 | 78 | 78
2019-02-22 18:30 | 82 | 82
2019-02-22 19:00 | 85 | 84
2019-02-22 19:30 | 84 | 84
2019-02-22 20:00 | 83 | 83
2019-02-22 20:30 | 82 | 82
2019-02-22 21:00 | 81 | 81
2019-02-22 21:30 | 80 | 79
2019-02-22 22:00 | 80 | 79
2019-02-22 22:30 | 77 | 76
2019-02-22 23:00 | 75 | 74
2019-02-22 23:30 | 75 | 74
2019-02-23 | 74 | 72
2019-02-23 00:30 | 73 | 71
2019-02-23 01:00 | 73 | 72
2019-02-23 01:30 | 72 | 71
2019-02-23 02:00 | 72 | 71
2019-02-23 02:30 | 72 | 71
2019-02-23 03:00 | 71 | 70
2019-02-23 03:30 | 71 | 69
2019-02-23 04:00 | 70 | 69
2019-02-23 04:30 | 70 | 68
2019-02-23 05:00 | 70 | 68
2019-02-23 05:30 | 69 | 67
2019-02-23 06:00 | 70 | 68
2019-02-23 06:30 | 69 | 68
2019-02-23 07:00 | 68 | 67
2019-02-23 07:30 | 69 | 68
2019-02-23 08:00 | 70 | 69
2019-02-23 08:30 | 71 | 70
2019-02-23 09:00 | 67 | 66
2019-02-23 09:30 | 67 | 66
2019-02-23 10:00 | 64 | 63
2019-02-23 10:30 | 62 | 61
2019-02-23 11:00 | 51 | 49
2019-02-23 11:30 | 59 | 57
2019-02-23 12:00 | 52 | 51
2019-02-23 12:30 | 46 | 44
2019-02-23 13:00 | 51 | 49
2019-02-23 13:30 | 50 | 48
2019-02-23 14:00 | 54 | 52
2019-02-23 14:30 | 67 | 66
2019-02-23 15:00 | 67 | 66
2019-02-23 15:30 | 65 | 64
2019-02-23 16:00 | 62 | 61
2019-02-23 16:30 | 62 | 60
2019-02-23 17:00 | 68 | 67
2019-02-23 17:30 | 69 | 68
2019-02-23 18:00 | 70 | 69
2019-02-23 18:30 | 68 | 67
2019-02-23 19:00 | 69 | 67
2019-02-23 19:30 | 72 | 71
2019-02-23 20:00 | 73 | 71
2019-02-23 20:30 | 76 | 75
2019-02-23 21:00 | 78 | 77
2019-02-23 21:30 | 78 | 78
2019-02-23 22:00 | 77 | 76
2019-02-23 22:30 | 77 | 76
2019-02-23 23:00 | 76 | 75
2019-02-23 23:30 | 75 | 74
2019-02-24 | 75 | 74
2019-02-24 00:30 | 75 | 73
2019-02-24 01:00 | 74 | 73
2019-02-24 01:30 | 79 | 77
2019-02-24 02:00 | 80 | 79
2019-02-24 02:30 | 80 | 79
2019-02-24 03:00 | 80 | 79
2019-02-24 03:30 | 79 | 78
2019-02-24 04:00 | 79 | 78
2019-02-24 04:30 | 78 | 77
2019-02-24 05:00 | 78 | 77
2019-02-24 05:30 | 78 | 77
2019-02-24 06:00 | 78 | 77
2019-02-24 06:30 | 78 | 76
2019-02-24 07:00 | 77 | 75
2019-02-24 07:30 | 75 | 73
2019-02-24 08:00 | 74 | 73
2019-02-24 08:30 | 71 | 71
2019-02-24 09:00 | 67 | 67
2019-02-24 09:30 | 67 | 67
2019-02-24 10:00 | 69 | 69
2019-02-24 10:30 | 65 | 64
2019-02-24 11:00 | 52 | 52
2019-02-24 11:30 | 56 | 56
2019-02-24 12:00 | 53 | 53
2019-02-24 12:30 | 47 | 47
2019-02-24 13:00 | 52 | 52
2019-02-24 13:30 | 48 | 48
2019-02-24 14:00 | 51 | 51
2019-02-24 14:30 | 52 | 52
2019-02-24 15:00 | 57 | 57
2019-02-24 15:30 | 61 | 60
2019-02-24 16:00 | 62 | 62
2019-02-24 16:30 | 62 | 62
2019-02-24 17:00 | 68 | 67
2019-02-24 17:30 | 71 | 71
2019-02-24 18:00 | 68 | 68
2019-02-24 18:30 | 71 | 71
2019-02-24 19:00 | 74 | 73
2019-02-24 19:30 | 75 | 74
2019-02-24 20:00 | 74 | 73
2019-02-24 20:30 | 74 | 73
2019-02-24 21:00 | 73 | 72
2019-02-24 21:30 | 72 | 71
2019-02-24 22:00 | 71 | 70
2019-02-24 22:30 | 72 | 71
2019-02-24 23:00 | 71 | 70
2019-02-24 23:30 | 70 | 69
2019-02-25 | 70 | 70
2019-02-25 00:30 | 69 | 69
2019-02-25 01:00 | 70 | 70
2019-02-25 01:30 | 70 | 70
2019-02-25 02:00 | 70 | 70
2019-02-25 02:30 | 70 | 70
2019-02-25 03:00 | 70 | 70
2019-02-25 03:30 | 70 | 69
2019-02-25 04:00 | 70 | 70
2019-02-25 04:30 | 68 | 68
2019-02-25 05:00 | 69 | 69
2019-02-25 05:30 | 69 | 68
2019-02-25 06:00 | 69 | 68
2019-02-25 06:30 | 68 | 68
2019-02-25 07:00 | 68 | 67
2019-02-25 07:30 | 65 | 64
2019-02-25 08:00 | 67 | 66
2019-02-25 08:30 | 63 | 63
2019-02-25 09:00 | 56 | 56
2019-02-25 09:30 | 46 | 46
2019-02-25 10:00 | 43 | 42
2019-02-25 10:30 | 44 | 43
2019-02-25 11:00 | 45 | 44
2019-02-25 11:30 | 45 | 44
2019-02-25 12:00 | 45 | 44
2019-02-25 12:30 | 46 | 44
2019-02-25 13:00 | 47 | 46
2019-02-25 13:30 | 60 | 59
2019-02-25 14:00 | 58 | 57
2019-02-25 14:30 | 53 | 51
2019-02-25 15:00 | 44 | 42
2019-02-25 15:30 | 51 | 49
2019-02-25 16:00 | 53 | 51
2019-02-25 16:30 | 43 | 42
2019-02-25 17:00 | 55 | 54
2019-02-25 17:30 | 56 | 55
2019-02-25 18:00 | 56 | 55
2019-02-25 18:30 | 59 | 58
2019-02-25 19:00 | 61 | 61
2019-02-25 19:30 | 62 | 62
2019-02-25 20:00 | 63 | 63
2019-02-25 20:30 | 63 | 63
2019-02-25 21:00 | 62 | 62
2019-02-25 21:30 | 76 | 75
2019-02-25 22:00 | 76 | 76
2019-02-25 22:30 | 74 | 74
2019-02-25 23:00 | 72 | 72
2019-02-25 23:30 | 72 | 71
2019-02-26 | 72 | 72
2019-02-26 00:30 | 71 | 71
2019-02-26 01:00 | 72 | 72
2019-02-26 01:30 | 72 | 72
2019-02-26 02:00 | 71 | 71
2019-02-26 02:30 | 71 | 71
2019-02-26 03:00 | 71 | 71
2019-02-26 03:30 | 71 | 71
2019-02-26 04:00 | 71 | 71
2019-02-26 04:30 | 71 | 71
2019-02-26 05:00 | 71 | 70
2019-02-26 05:30 | 71 | 71
2019-02-26 06:00 | 71 | 71
2019-02-26 06:30 | 70 | 70
2019-02-26 07:00 | 70 | 70
2019-02-26 07:30 | 67 | 67
2019-02-26 08:00 | 62 | 62
2019-02-26 08:30 | 59 | 59
2019-02-26 09:00 | 53 | 52
2019-02-26 09:30 | 49 | 48
2019-02-26 10:00 | 45 | 44
2019-02-26 10:30 | 44 | 43
2019-02-26 11:00 | 46 | 46
2019-02-26 11:30 | 47 | 46
2019-02-26 12:00 | 49 | 48
2019-02-26 12:30 | 46 | 46
2019-02-26 13:00 | 54 | 54
2019-02-26 13:30 | 47 | 47
2019-02-26 14:00 | 50 | 49
2019-02-26 14:30 | 48 | 47
2019-02-26 15:00 | 51 | 51
2019-02-26 15:30 | 50 | 49
2019-02-26 16:00 | 52 | 52
2019-02-26 16:30 | 37 | 37
2019-02-26 17:00 | 42 | 42
2019-02-26 17:30 | 47 | 47
2019-02-26 18:00 | 54 | 53
2019-02-26 18:30 | 58 | 58
2019-02-26 19:00 | 61 | 61
2019-02-26 19:30 | 61 | 61
2019-02-26 20:00 | 61 | 61
2019-02-26 20:30 | 61 | 61
2019-02-26 21:00 | 60 | 60
2019-02-26 21:30 | 75 | 74
2019-02-26 22:00 | 75 | 74
2019-02-26 22:30 | 72 | 72
2019-02-26 23:00 | 71 | 70
2019-02-26 23:30 | 71 | 71
2019-02-27 | 71 | 70
2019-02-27 00:30 | 71 | 71
2019-02-27 01:00 | 72 | 71
2019-02-27 01:30 | 71 | 71
2019-02-27 02:00 | 71 | 70
2019-02-27 02:30 | 71 | 71
2019-02-27 03:00 | 70 | 70
2019-02-27 03:30 | 70 | 69
2019-02-27 04:00 | 69 | 69
2019-02-27 04:30 | 69 | 69
2019-02-27 05:00 | 68 | 68
2019-02-27 05:30 | 69 | 68
2019-02-27 06:00 | 69 | 68
2019-02-27 06:30 | 67 | 67
2019-02-27 07:00 | 66 | 66
2019-02-27 07:30 | 65 | 65
2019-02-27 08:00 | 61 | 61
2019-02-27 08:30 | 57 | 56
2019-02-27 09:00 | 59 | 58
2019-02-27 09:30 | 52 | 51
2019-02-27 10:00 | 49 | 48
2019-02-27 10:30 | 40 | 39
2019-02-27 11:00 | 41 | 40
2019-02-27 11:30 | 55 | 55
2019-02-27 12:00 | 55 | 54
2019-02-27 12:30 | 46 | 46
2019-02-27 13:00 | 44 | 43
2019-02-27 13:30 | 47 | 46
2019-02-27 14:00 | 41 | 40
2019-02-27 14:30 | 40 | 39
2019-02-27 15:00 | 39 | 38
2019-02-27 15:30 | 44 | 43
2019-02-27 16:00 | 44 | 43
2019-02-27 16:30 | 44 | 44
2019-02-27 17:00 | 52 | 52
2019-02-27 17:30 | 51 | 50
2019-02-27 18:00 | 55 | 54
2019-02-27 18:30 | 58 | 57
2019-02-27 19:00 | 60 | 60
2019-02-27 19:30 | 60 | 60
2019-02-27 20:00 | 60 | 60
2019-02-27 20:30 | 59 | 59
2019-02-27 21:00 | 57 | 57
2019-02-27 21:30 | 66 | 66
2019-02-27 22:00 | 73 | 72
2019-02-27 22:30 | 72 | 71
2019-02-27 23:00 | 70 | 69
2019-02-27 23:30 | 70 | 69
2019-02-28 | 70 | 69
2019-02-28 00:30 | 71 | 70
2019-02-28 01:00 | 71 | 70
2019-02-28 01:30 | 71 | 70
2019-02-28 02:00 | 71 | 70
2019-02-28 02:30 | 71 | 70
2019-02-28 03:00 | 70 | 69
2019-02-28 03:30 | 70 | 70
2019-02-28 04:00 | 69 | 68
2019-02-28 04:30 | 69 | 68
2019-02-28 05:00 | 69 | 69
2019-02-28 05:30 | 69 | 69
2019-02-28 06:00 | 70 | 69
2019-02-28 06:30 | 68 | 67
2019-02-28 07:00 | 66 | 66
2019-02-28 07:30 | 62 | 62
2019-02-28 08:00 | 57 | 57
2019-02-28 08:30 | 52 | 52
2019-02-28 09:00 | 48 | 48
2019-02-28 09:30 | 43 | 43
2019-02-28 10:00 | 41 | 41
2019-02-28 10:30 | 39 | 39
2019-02-28 11:00 | 45 | 45
2019-02-28 11:30 | 50 | 50
2019-02-28 12:00 | 38 | 37
2019-02-28 12:30 | 42 | 41
2019-02-28 13:00 | 40 | 40
2019-02-28 13:30 | 44 | 44
2019-02-28 14:00 | 41 | 40
2019-02-28 14:30 | 38 | 37
2019-02-28 15:00 | 43 | 42
2019-02-28 15:30 | 51 | 51
2019-02-28 16:00 | 57 | 57
2019-02-28 16:30 | 51 | 51
2019-02-28 17:00 | 51 | 51
2019-02-28 17:30 | 73 | 73
2019-02-28 18:00 | 81 | 81
2019-02-28 18:30 | 83 | 82
2019-02-28 19:00 | 84 | 83
2019-02-28 19:30 | 85 | 84
2019-02-28 20:00 | 84 | 83
2019-02-28 20:30 | 83 | 82
2019-02-28 21:00 | 82 | 82
2019-02-28 21:30 | 82 | 81
2019-02-28 22:00 | 81 | 80
2019-02-28 22:30 | 74 | 73
2019-02-28 23:00 | 71 | 71
2019-02-28 23:30 | 71 | 71
2019-03-01 | 70 | 70

## 18. Historic line rating
|  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
PQ Rating (MVA) |  | 230 | 203 | 230 | 204 | 231 | 204
Feeders | 7156 | 230 | 203 | 230 | 204 | 231 | 204

## 21. Annual constraint duration
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (hours)

## 22. Constraint dur. (peak day)
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (peak day, hours)