## Cover Page
AER Rule | Field Name | Value(s)
1 | Transmission line ID | Bergins Hill to Karana Downs
2 | Constraint primary driver | Asset Condition
3 | Location of constraint (start, decimal degrees, latitude and longitude) | -27.617 | 152.823
4 | Location of constraint (end, decimal degrees, latitude and longitude) | -27.549 | 152.819
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
5 | Forecast asset rating (MVA) | 1254 | 1254 | 1254 | 1254 | 1254 | 1254 | 1254 | 1254 | 1254 | 1254 | 1254
6 | Forecast maximum demand 10% PoE (MVA) | 1009.61 | 1012.5 | 1003.86 | 1000.95 | 1005.05 | 1002.92 | 1008.52 | 1013.7 | 1013.3 | 1022.82 | 1022.82
| Forecast maximum demand 50% PoE (MVA) | 932.69 | 935.4 | 930.76 | 933.33 | 928.58 | 925.18 | 927.06 | 932.31 | 929.61 | 916.81 | 916.81
7 | Voltage Level (kV) | Financial year 2021: 275
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
8 | Maximum load at risk (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maximum load at risk (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Energy at risk (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Preferred investment | Financial year 2021: Line refit works on the 275kV transmission line between Bergins Hill and Karana Downs
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
11 | Capital cost ($m, nominal) | Financial year 2030: 4
12 | Operating cost ($m, nominal) | Financial year 2030: 0.08; Financial year 2031: 0.08
13 | Preferred investment cost accuracy | Financial year 2021: 0.3
14 | Preferred investment proposed timing | Financial year 2021: 2030-06-30
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
15 | Demand reduction to defer by 1 year (MVA)
16 | Annual deferall value ($m, nominal)
17 | Historic load trace
18 | Historic line rating
Financial year
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
19 | Annual economic cost of constraint ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | VCR ($m/MWh) | Financial year 2021: 0.04003
21 | Annual constraint duration
22 | Constraint duration on peak demand day

## 17. Historic load trace
Date/Time | Load (MVA) | Load (MW) | Load switching affected?
2017-03-01 00:30 | 387 | 381
2017-03-01 01:00 | 385 | 381
2017-03-01 01:30 | 376 | 372
2017-03-01 02:00 | 368 | 364
2017-03-01 02:30 | 365 | 360
2017-03-01 03:00 | 357 | 352
2017-03-01 03:30 | 359 | 353
2017-03-01 04:00 | 368 | 363
2017-03-01 04:30 | 374 | 370
2017-03-01 05:00 | 381 | 377
2017-03-01 05:30 | 404 | 402
2017-03-01 06:00 | 430 | 427
2017-03-01 06:30 | 468 | 467
2017-03-01 07:00 | 507 | 502
2017-03-01 07:30 | 535 | 528
2017-03-01 08:00 | 554 | 546
2017-03-01 08:30 | 553 | 546
2017-03-01 09:00 | 557 | 552
2017-03-01 09:30 | 567 | 562
2017-03-01 10:00 | 587 | 582
2017-03-01 10:30 | 598 | 593
2017-03-01 11:00 | 604 | 598
2017-03-01 11:30 | 614 | 607
2017-03-01 12:00 | 624 | 615
2017-03-01 12:30 | 630 | 621
2017-03-01 13:00 | 633 | 625
2017-03-01 13:30 | 644 | 636
2017-03-01 14:00 | 656 | 649
2017-03-01 14:30 | 661 | 653
2017-03-01 15:00 | 660 | 652
2017-03-01 15:30 | 667 | 659
2017-03-01 16:00 | 668 | 660
2017-03-01 16:30 | 663 | 655
2017-03-01 17:00 | 665 | 656
2017-03-01 17:30 | 649 | 640
2017-03-01 18:00 | 648 | 638
2017-03-01 18:30 | 630 | 618
2017-03-01 19:00 | 630 | 623
2017-03-01 19:30 | 612 | 604
2017-03-01 20:00 | 610 | 604
2017-03-01 20:30 | 594 | 588
2017-03-01 21:00 | 570 | 567
2017-03-01 21:30 | 552 | 549
2017-03-01 22:00 | 531 | 527
2017-03-01 22:30 | 489 | 485
2017-03-01 23:00 | 462 | 459
2017-03-01 23:30 | 439 | 436
2017-03-02 | 422 | 419
2017-03-02 00:30 | 417 | 412
2017-03-02 01:00 | 406 | 401
2017-03-02 01:30 | 387 | 384
2017-03-02 02:00 | 381 | 376
2017-03-02 02:30 | 379 | 374
2017-03-02 03:00 | 378 | 374
2017-03-02 03:30 | 382 | 377
2017-03-02 04:00 | 373 | 368
2017-03-02 04:30 | 388 | 383
2017-03-02 05:00 | 402 | 398
2017-03-02 05:30 | 435 | 426
2017-03-02 06:00 | 453 | 444
2017-03-02 06:30 | 492 | 485
2017-03-02 07:00 | 536 | 525
2017-03-02 07:30 | 570 | 560
2017-03-02 08:00 | 593 | 579
2017-03-02 08:30 | 598 | 585
2017-03-02 09:00 | 594 | 582
2017-03-02 09:30 | 606 | 596
2017-03-02 10:00 | 619 | 608
2017-03-02 10:30 | 625 | 614
2017-03-02 11:00 | 627 | 616
2017-03-02 11:30 | 641 | 632
2017-03-02 12:00 | 644 | 635
2017-03-02 12:30 | 638 | 628
2017-03-02 13:00 | 640 | 630
2017-03-02 13:30 | 656 | 647
2017-03-02 14:00 | 663 | 653
2017-03-02 14:30 | 666 | 654
2017-03-02 15:00 | 668 | 656
2017-03-02 15:30 | 669 | 658
2017-03-02 16:00 | 675 | 665
2017-03-02 16:30 | 682 | 671
2017-03-02 17:00 | 682 | 670
2017-03-02 17:30 | 686 | 673
2017-03-02 18:00 | 678 | 667
2017-03-02 18:30 | 658 | 647
2017-03-02 19:00 | 666 | 657
2017-03-02 19:30 | 658 | 648
2017-03-02 20:00 | 641 | 631
2017-03-02 20:30 | 620 | 612
2017-03-02 21:00 | 592 | 590
2017-03-02 21:30 | 569 | 567
2017-03-02 22:00 | 549 | 545
2017-03-02 22:30 | 504 | 500
2017-03-02 23:00 | 475 | 474
2017-03-02 23:30 | 448 | 446
2017-03-03 | 428 | 425
2017-03-03 00:30 | 404 | 403
2017-03-03 01:00 | 398 | 396
2017-03-03 01:30 | 391 | 388
2017-03-03 02:00 | 381 | 377
2017-03-03 02:30 | 371 | 367
2017-03-03 03:00 | 366 | 362
2017-03-03 03:30 | 365 | 361
2017-03-03 04:00 | 367 | 363
2017-03-03 04:30 | 384 | 380
2017-03-03 05:00 | 396 | 393
2017-03-03 05:30 | 414 | 411
2017-03-03 06:00 | 434 | 431
2017-03-03 06:30 | 475 | 467
2017-03-03 07:00 | 522 | 514
2017-03-03 07:30 | 555 | 549
2017-03-03 08:00 | 570 | 565
2017-03-03 08:30 | 586 | 582
2017-03-03 09:00 | 588 | 585
2017-03-03 09:30 | 593 | 591
2017-03-03 10:00 | 604 | 597
2017-03-03 10:30 | 610 | 600
2017-03-03 11:00 | 621 | 612
2017-03-03 11:30 | 628 | 619
2017-03-03 12:00 | 634 | 627
2017-03-03 12:30 | 646 | 638
2017-03-03 13:00 | 670 | 660
2017-03-03 13:30 | 664 | 657
2017-03-03 14:00 | 653 | 648
2017-03-03 14:30 | 656 | 651
2017-03-03 15:00 | 658 | 652
2017-03-03 15:30 | 662 | 656
2017-03-03 16:00 | 668 | 662
2017-03-03 16:30 | 673 | 667
2017-03-03 17:00 | 680 | 673
2017-03-03 17:30 | 665 | 658
2017-03-03 18:00 | 645 | 637
2017-03-03 18:30 | 621 | 615
2017-03-03 19:00 | 633 | 628
2017-03-03 19:30 | 620 | 614
2017-03-03 20:00 | 609 | 605
2017-03-03 20:30 | 597 | 591
2017-03-03 21:00 | 575 | 572
2017-03-03 21:30 | 559 | 555
2017-03-03 22:00 | 540 | 538
2017-03-03 22:30 | 504 | 502
2017-03-03 23:00 | 475 | 474
2017-03-03 23:30 | 449 | 447
2017-03-04 | 428 | 428
2017-03-04 00:30 | 414 | 414
2017-03-04 01:00 | 407 | 407
2017-03-04 01:30 | 397 | 397
2017-03-04 02:00 | 390 | 390
2017-03-04 02:30 | 380 | 380
2017-03-04 03:00 | 364 | 363
2017-03-04 03:30 | 360 | 359
2017-03-04 04:00 | 359 | 358
2017-03-04 04:30 | 363 | 362
2017-03-04 05:00 | 374 | 373
2017-03-04 05:30 | 382 | 382
2017-03-04 06:00 | 384 | 383
2017-03-04 06:30 | 394 | 394
2017-03-04 07:00 | 411 | 411
2017-03-04 07:30 | 446 | 445
2017-03-04 08:00 | 468 | 468
2017-03-04 08:30 | 479 | 479
2017-03-04 09:00 | 486 | 486
2017-03-04 09:30 | 505 | 504
2017-03-04 10:00 | 522 | 521
2017-03-04 10:30 | 535 | 534
2017-03-04 11:00 | 540 | 539
2017-03-04 11:30 | 544 | 543
2017-03-04 12:00 | 539 | 537
2017-03-04 12:30 | 532 | 530
2017-03-04 13:00 | 531 | 529
2017-03-04 13:30 | 538 | 537
2017-03-04 14:00 | 538 | 536
2017-03-04 14:30 | 561 | 560
2017-03-04 15:00 | 571 | 569
2017-03-04 15:30 | 577 | 575
2017-03-04 16:00 | 581 | 580
2017-03-04 16:30 | 584 | 583
2017-03-04 17:00 | 583 | 582
2017-03-04 17:30 | 578 | 576
2017-03-04 18:00 | 572 | 569
2017-03-04 18:30 | 571 | 569
2017-03-04 19:00 | 573 | 571
2017-03-04 19:30 | 565 | 563
2017-03-04 20:00 | 553 | 552
2017-03-04 20:30 | 543 | 542
2017-03-04 21:00 | 524 | 523
2017-03-04 21:30 | 512 | 510
2017-03-04 22:00 | 495 | 494
2017-03-04 22:30 | 464 | 463
2017-03-04 23:00 | 439 | 438
2017-03-04 23:30 | 419 | 419
2017-03-05 | 401 | 400
2017-03-05 00:30 | 391 | 391
2017-03-05 01:00 | 390 | 389
2017-03-05 01:30 | 378 | 378
2017-03-05 02:00 | 372 | 372
2017-03-05 02:30 | 368 | 367
2017-03-05 03:00 | 369 | 368
2017-03-05 03:30 | 372 | 371
2017-03-05 04:00 | 369 | 368
2017-03-05 04:30 | 370 | 369
2017-03-05 05:00 | 370 | 369
2017-03-05 05:30 | 373 | 373
2017-03-05 06:00 | 369 | 368
2017-03-05 06:30 | 382 | 381
2017-03-05 07:00 | 389 | 388
2017-03-05 07:30 | 397 | 396
2017-03-05 08:00 | 401 | 401
2017-03-05 08:30 | 421 | 420
2017-03-05 09:00 | 433 | 433
2017-03-05 09:30 | 445 | 444
2017-03-05 10:00 | 445 | 445
2017-03-05 10:30 | 455 | 454
2017-03-05 11:00 | 470 | 470
2017-03-05 11:30 | 482 | 482
2017-03-05 12:00 | 489 | 488
2017-03-05 12:30 | 496 | 496
2017-03-05 13:00 | 497 | 496
2017-03-05 13:30 | 509 | 508
2017-03-05 14:00 | 524 | 524
2017-03-05 14:30 | 538 | 538
2017-03-05 15:00 | 552 | 552
2017-03-05 15:30 | 567 | 567
2017-03-05 16:00 | 574 | 573
2017-03-05 16:30 | 588 | 587
2017-03-05 17:00 | 598 | 597
2017-03-05 17:30 | 604 | 603
2017-03-05 18:00 | 602 | 601
2017-03-05 18:30 | 601 | 599
2017-03-05 19:00 | 625 | 624
2017-03-05 19:30 | 615 | 614
2017-03-05 20:00 | 593 | 592
2017-03-05 20:30 | 573 | 573
2017-03-05 21:00 | 551 | 550
2017-03-05 21:30 | 534 | 533
2017-03-05 22:00 | 505 | 504
2017-03-05 22:30 | 468 | 467
2017-03-05 23:00 | 451 | 451
2017-03-05 23:30 | 431 | 430
2017-03-06 | 411 | 411
2017-03-06 00:30 | 392 | 392
2017-03-06 01:00 | 382 | 382
2017-03-06 01:30 | 367 | 366
2017-03-06 02:00 | 361 | 360
2017-03-06 02:30 | 361 | 360
2017-03-06 03:00 | 351 | 351
2017-03-06 03:30 | 355 | 354
2017-03-06 04:00 | 357 | 356
2017-03-06 04:30 | 380 | 379
2017-03-06 05:00 | 390 | 390
2017-03-06 05:30 | 414 | 413
2017-03-06 06:00 | 428 | 427
2017-03-06 06:30 | 464 | 464
2017-03-06 07:00 | 521 | 514
2017-03-06 07:30 | 553 | 546
2017-03-06 08:00 | 558 | 553
2017-03-06 08:30 | 560 | 556
2017-03-06 09:00 | 569 | 565
2017-03-06 09:30 | 574 | 570
2017-03-06 10:00 | 589 | 581
2017-03-06 10:30 | 592 | 584
2017-03-06 11:00 | 607 | 598
2017-03-06 11:30 | 617 | 608
2017-03-06 12:00 | 621 | 612
2017-03-06 12:30 | 633 | 622
2017-03-06 13:00 | 642 | 632
2017-03-06 13:30 | 647 | 637
2017-03-06 14:00 | 646 | 636
2017-03-06 14:30 | 641 | 631
2017-03-06 15:00 | 644 | 634
2017-03-06 15:30 | 647 | 637
2017-03-06 16:00 | 656 | 646
2017-03-06 16:30 | 669 | 659
2017-03-06 17:00 | 682 | 672
2017-03-06 17:30 | 672 | 660
2017-03-06 18:00 | 656 | 644
2017-03-06 18:30 | 643 | 632
2017-03-06 19:00 | 648 | 639
2017-03-06 19:30 | 624 | 620
2017-03-06 20:00 | 620 | 617
2017-03-06 20:30 | 601 | 598
2017-03-06 21:00 | 569 | 566
2017-03-06 21:30 | 549 | 545
2017-03-06 22:00 | 533 | 526
2017-03-06 22:30 | 496 | 489
2017-03-06 23:00 | 462 | 458
2017-03-06 23:30 | 437 | 435
2017-03-07 | 418 | 414
2017-03-07 00:30 | 402 | 397
2017-03-07 01:00 | 389 | 386
2017-03-07 01:30 | 375 | 373
2017-03-07 02:00 | 376 | 375
2017-03-07 02:30 | 363 | 362
2017-03-07 03:00 | 360 | 359
2017-03-07 03:30 | 363 | 361
2017-03-07 04:00 | 363 | 362
2017-03-07 04:30 | 386 | 385
2017-03-07 05:00 | 392 | 391
2017-03-07 05:30 | 408 | 408
2017-03-07 06:00 | 421 | 418
2017-03-07 06:30 | 464 | 462
2017-03-07 07:00 | 513 | 507
2017-03-07 07:30 | 543 | 537
2017-03-07 08:00 | 548 | 541
2017-03-07 08:30 | 553 | 546
2017-03-07 09:00 | 551 | 544
2017-03-07 09:30 | 509 | 503
2017-03-07 10:00 | 511 | 506
2017-03-07 10:30 | 509 | 505
2017-03-07 11:00 | 514 | 509
2017-03-07 11:30 | 516 | 512
2017-03-07 12:00 | 523 | 519
2017-03-07 12:30 | 560 | 554
2017-03-07 13:00 | 569 | 564
2017-03-07 13:30 | 584 | 577
2017-03-07 14:00 | 600 | 592
2017-03-07 14:30 | 609 | 601
2017-03-07 15:00 | 604 | 596
2017-03-07 15:30 | 605 | 597
2017-03-07 16:00 | 622 | 614
2017-03-07 16:30 | 638 | 630
2017-03-07 17:00 | 647 | 639
2017-03-07 17:30 | 635 | 624
2017-03-07 18:00 | 618 | 607
2017-03-07 18:30 | 606 | 596
2017-03-07 19:00 | 618 | 609
2017-03-07 19:30 | 605 | 595
2017-03-07 20:00 | 589 | 578
2017-03-07 20:30 | 564 | 556
2017-03-07 21:00 | 529 | 526
2017-03-07 21:30 | 505 | 501
2017-03-07 22:00 | 480 | 475
2017-03-07 22:30 | 449 | 446
2017-03-07 23:00 | 434 | 430
2017-03-07 23:30 | 415 | 413
2017-03-08 | 384 | 381
2017-03-08 00:30 | 370 | 366
2017-03-08 01:00 | 357 | 352
2017-03-08 01:30 | 341 | 335
2017-03-08 02:00 | 334 | 328
2017-03-08 02:30 | 335 | 329
2017-03-08 03:00 | 338 | 334
2017-03-08 03:30 | 338 | 334
2017-03-08 04:00 | 340 | 336
2017-03-08 04:30 | 345 | 342
2017-03-08 05:00 | 361 | 358
2017-03-08 05:30 | 386 | 384
2017-03-08 06:00 | 421 | 419
2017-03-08 06:30 | 468 | 468
2017-03-08 07:00 | 506 | 505
2017-03-08 07:30 | 528 | 527
2017-03-08 08:00 | 530 | 530
2017-03-08 08:30 | 534 | 534
2017-03-08 09:00 | 532 | 532
2017-03-08 09:30 | 532 | 532
2017-03-08 10:00 | 542 | 542
2017-03-08 10:30 | 537 | 537
2017-03-08 11:00 | 541 | 541
2017-03-08 11:30 | 535 | 530
2017-03-08 12:00 | 543 | 534
2017-03-08 12:30 | 542 | 532
2017-03-08 13:00 | 540 | 532
2017-03-08 13:30 | 545 | 538
2017-03-08 14:00 | 559 | 551
2017-03-08 14:30 | 569 | 562
2017-03-08 15:00 | 580 | 574
2017-03-08 15:30 | 593 | 587
2017-03-08 16:00 | 595 | 588
2017-03-08 16:30 | 600 | 592
2017-03-08 17:00 | 610 | 602
2017-03-08 17:30 | 608 | 599
2017-03-08 18:00 | 603 | 593
2017-03-08 18:30 | 591 | 581
2017-03-08 19:00 | 595 | 588
2017-03-08 19:30 | 581 | 573
2017-03-08 20:00 | 571 | 562
2017-03-08 20:30 | 559 | 553
2017-03-08 21:00 | 527 | 525
2017-03-08 21:30 | 516 | 513
2017-03-08 22:00 | 504 | 500
2017-03-08 22:30 | 469 | 466
2017-03-08 23:00 | 450 | 448
2017-03-08 23:30 | 422 | 421
2017-03-09 | 403 | 402
2017-03-09 00:30 | 378 | 377
2017-03-09 01:00 | 363 | 361
2017-03-09 01:30 | 357 | 355
2017-03-09 02:00 | 354 | 351
2017-03-09 02:30 | 357 | 353
2017-03-09 03:00 | 361 | 357
2017-03-09 03:30 | 355 | 351
2017-03-09 04:00 | 344 | 339
2017-03-09 04:30 | 353 | 350
2017-03-09 05:00 | 384 | 381
2017-03-09 05:30 | 403 | 401
2017-03-09 06:00 | 414 | 413
2017-03-09 06:30 | 456 | 455
2017-03-09 07:00 | 496 | 490
2017-03-09 07:30 | 526 | 516
2017-03-09 08:00 | 539 | 524
2017-03-09 08:30 | 535 | 523
2017-03-09 09:00 | 530 | 522
2017-03-09 09:30 | 528 | 520
2017-03-09 10:00 | 526 | 519
2017-03-09 10:30 | 521 | 513
2017-03-09 11:00 | 524 | 516
2017-03-09 11:30 | 531 | 524
2017-03-09 12:00 | 541 | 535
2017-03-09 12:30 | 551 | 544
2017-03-09 13:00 | 565 | 557
2017-03-09 13:30 | 573 | 565
2017-03-09 14:00 | 581 | 573
2017-03-09 14:30 | 579 | 571
2017-03-09 15:00 | 578 | 570
2017-03-09 15:30 | 582 | 574
2017-03-09 16:00 | 591 | 583
2017-03-09 16:30 | 608 | 600
2017-03-09 17:00 | 616 | 608
2017-03-09 17:30 | 615 | 605
2017-03-09 18:00 | 610 | 600
2017-03-09 18:30 | 605 | 596
2017-03-09 19:00 | 624 | 618
2017-03-09 19:30 | 609 | 601
2017-03-09 20:00 | 598 | 589
2017-03-09 20:30 | 588 | 583
2017-03-09 21:00 | 557 | 555
2017-03-09 21:30 | 542 | 541
2017-03-09 22:00 | 514 | 513
2017-03-09 22:30 | 485 | 483
2017-03-09 23:00 | 455 | 454
2017-03-09 23:30 | 434 | 432
2017-03-10 | 414 | 411
2017-03-10 00:30 | 392 | 387
2017-03-10 01:00 | 389 | 383
2017-03-10 01:30 | 370 | 365
2017-03-10 02:00 | 355 | 352
2017-03-10 02:30 | 352 | 348
2017-03-10 03:00 | 359 | 355
2017-03-10 03:30 | 360 | 355
2017-03-10 04:00 | 360 | 355
2017-03-10 04:30 | 362 | 357
2017-03-10 05:00 | 371 | 367
2017-03-10 05:30 | 393 | 391
2017-03-10 06:00 | 410 | 409
2017-03-10 06:30 | 447 | 447
2017-03-10 07:00 | 482 | 481
2017-03-10 07:30 | 518 | 518
2017-03-10 08:00 | 524 | 524
2017-03-10 08:30 | 525 | 525
2017-03-10 09:00 | 516 | 516
2017-03-10 09:30 | 515 | 515
2017-03-10 10:00 | 515 | 515
2017-03-10 10:30 | 514 | 514
2017-03-10 11:00 | 515 | 515
2017-03-10 11:30 | 522 | 522
2017-03-10 12:00 | 535 | 534
2017-03-10 12:30 | 537 | 537
2017-03-10 13:00 | 545 | 545
2017-03-10 13:30 | 553 | 553
2017-03-10 14:00 | 561 | 560
2017-03-10 14:30 | 568 | 568
2017-03-10 15:00 | 582 | 581
2017-03-10 15:30 | 586 | 586
2017-03-10 16:00 | 595 | 594
2017-03-10 16:30 | 605 | 604
2017-03-10 17:00 | 615 | 614
2017-03-10 17:30 | 609 | 607
2017-03-10 18:00 | 597 | 594
2017-03-10 18:30 | 583 | 580
2017-03-10 19:00 | 585 | 583
2017-03-10 19:30 | 573 | 572
2017-03-10 20:00 | 561 | 560
2017-03-10 20:30 | 555 | 553
2017-03-10 21:00 | 541 | 541
2017-03-10 21:30 | 529 | 528
2017-03-10 22:00 | 508 | 507
2017-03-10 22:30 | 471 | 471
2017-03-10 23:00 | 441 | 441
2017-03-10 23:30 | 422 | 422
2017-03-11 | 403 | 403
2017-03-11 00:30 | 381 | 380
2017-03-11 01:00 | 369 | 369
2017-03-11 01:30 | 353 | 353
2017-03-11 02:00 | 349 | 348
2017-03-11 02:30 | 349 | 348
2017-03-11 03:00 | 353 | 352
2017-03-11 03:30 | 351 | 350
2017-03-11 04:00 | 352 | 351
2017-03-11 04:30 | 352 | 351
2017-03-11 05:00 | 354 | 353
2017-03-11 05:30 | 357 | 356
2017-03-11 06:00 | 360 | 359
2017-03-11 06:30 | 370 | 369
2017-03-11 07:00 | 381 | 380
2017-03-11 07:30 | 404 | 403
2017-03-11 08:00 | 419 | 418
2017-03-11 08:30 | 435 | 435
2017-03-11 09:00 | 434 | 434
2017-03-11 09:30 | 439 | 438
2017-03-11 10:00 | 444 | 439
2017-03-11 10:30 | 441 | 437
2017-03-11 11:00 | 443 | 439
2017-03-11 11:30 | 450 | 446
2017-03-11 12:00 | 453 | 450
2017-03-11 12:30 | 451 | 447
2017-03-11 13:00 | 460 | 455
2017-03-11 13:30 | 467 | 461
2017-03-11 14:00 | 462 | 458
2017-03-11 14:30 | 466 | 463
2017-03-11 15:00 | 471 | 469
2017-03-11 15:30 | 475 | 473
2017-03-11 16:00 | 483 | 481
2017-03-11 16:30 | 502 | 499
2017-03-11 17:00 | 510 | 507
2017-03-11 17:30 | 513 | 504
2017-03-11 18:00 | 509 | 498
2017-03-11 18:30 | 506 | 498
2017-03-11 19:00 | 511 | 506
2017-03-11 19:30 | 495 | 489
2017-03-11 20:00 | 492 | 485
2017-03-11 20:30 | 484 | 479
2017-03-11 21:00 | 467 | 463
2017-03-11 21:30 | 457 | 455
2017-03-11 22:00 | 448 | 448
2017-03-11 22:30 | 433 | 433
2017-03-11 23:00 | 427 | 427
2017-03-11 23:30 | 407 | 407
2017-03-12 | 389 | 388
2017-03-12 00:30 | 363 | 362
2017-03-12 01:00 | 352 | 351
2017-03-12 01:30 | 346 | 345
2017-03-12 02:00 | 338 | 336
2017-03-12 02:30 | 332 | 330
2017-03-12 03:00 | 335 | 333
2017-03-12 03:30 | 335 | 333
2017-03-12 04:00 | 335 | 332
2017-03-12 04:30 | 333 | 330
2017-03-12 05:00 | 337 | 334
2017-03-12 05:30 | 343 | 341
2017-03-12 06:00 | 344 | 342
2017-03-12 06:30 | 350 | 347
2017-03-12 07:00 | 357 | 355
2017-03-12 07:30 | 376 | 374
2017-03-12 08:00 | 389 | 388
2017-03-12 08:30 | 405 | 404
2017-03-12 09:00 | 417 | 416
2017-03-12 09:30 | 415 | 415
2017-03-12 10:00 | 417 | 417
2017-03-12 10:30 | 417 | 417
2017-03-12 11:00 | 430 | 430
2017-03-12 11:30 | 443 | 443
2017-03-12 12:00 | 450 | 450
2017-03-12 12:30 | 453 | 453
2017-03-12 13:00 | 452 | 452
2017-03-12 13:30 | 468 | 467
2017-03-12 14:00 | 483 | 482
2017-03-12 14:30 | 497 | 496
2017-03-12 15:00 | 510 | 510
2017-03-12 15:30 | 534 | 532
2017-03-12 16:00 | 560 | 556
2017-03-12 16:30 | 570 | 564
2017-03-12 17:00 | 568 | 563
2017-03-12 17:30 | 572 | 565
2017-03-12 18:00 | 571 | 564
2017-03-12 18:30 | 575 | 569
2017-03-12 19:00 | 592 | 587
2017-03-12 19:30 | 581 | 575
2017-03-12 20:00 | 572 | 567
2017-03-12 20:30 | 556 | 552
2017-03-12 21:00 | 533 | 532
2017-03-12 21:30 | 515 | 514
2017-03-12 22:00 | 496 | 495
2017-03-12 22:30 | 472 | 471
2017-03-12 23:00 | 458 | 457
2017-03-12 23:30 | 437 | 437
2017-03-13 | 410 | 410
2017-03-13 00:30 | 393 | 392
2017-03-13 01:00 | 373 | 373
2017-03-13 01:30 | 361 | 360
2017-03-13 02:00 | 354 | 353
2017-03-13 02:30 | 355 | 354
2017-03-13 03:00 | 355 | 354
2017-03-13 03:30 | 356 | 355
2017-03-13 04:00 | 359 | 358
2017-03-13 04:30 | 370 | 369
2017-03-13 05:00 | 381 | 380
2017-03-13 05:30 | 404 | 404
2017-03-13 06:00 | 426 | 426
2017-03-13 06:30 | 473 | 472
2017-03-13 07:00 | 507 | 506
2017-03-13 07:30 | 555 | 552
2017-03-13 08:00 | 588 | 584
2017-03-13 08:30 | 602 | 597
2017-03-13 09:00 | 610 | 604
2017-03-13 09:30 | 610 | 604
2017-03-13 10:00 | 589 | 583
2017-03-13 10:30 | 579 | 573
2017-03-13 11:00 | 581 | 575
2017-03-13 11:30 | 591 | 586
2017-03-13 12:00 | 594 | 589
2017-03-13 12:30 | 571 | 566
2017-03-13 13:00 | 564 | 560
2017-03-13 13:30 | 585 | 581
2017-03-13 14:00 | 605 | 601
2017-03-13 14:30 | 608 | 606
2017-03-13 15:00 | 605 | 602
2017-03-13 15:30 | 604 | 600
2017-03-13 16:00 | 604 | 601
2017-03-13 16:30 | 610 | 607
2017-03-13 17:00 | 609 | 605
2017-03-13 17:30 | 604 | 600
2017-03-13 18:00 | 601 | 596
2017-03-13 18:30 | 597 | 592
2017-03-13 19:00 | 602 | 598
2017-03-13 19:30 | 595 | 591
2017-03-13 20:00 | 579 | 575
2017-03-13 20:30 | 560 | 557
2017-03-13 21:00 | 529 | 529
2017-03-13 21:30 | 507 | 507
2017-03-13 22:00 | 490 | 488
2017-03-13 22:30 | 465 | 464
2017-03-13 23:00 | 451 | 451
2017-03-13 23:30 | 433 | 433
2017-03-14 | 420 | 420
2017-03-14 00:30 | 402 | 402
2017-03-14 01:00 | 390 | 390
2017-03-14 01:30 | 378 | 377
2017-03-14 02:00 | 368 | 368
2017-03-14 02:30 | 372 | 372
2017-03-14 03:00 | 374 | 374
2017-03-14 03:30 | 372 | 372
2017-03-14 04:00 | 369 | 369
2017-03-14 04:30 | 375 | 374
2017-03-14 05:00 | 385 | 385
2017-03-14 05:30 | 412 | 411
2017-03-14 06:00 | 455 | 450
2017-03-14 06:30 | 496 | 492
2017-03-14 07:00 | 530 | 525
2017-03-14 07:30 | 572 | 567
2017-03-14 08:00 | 591 | 585
2017-03-14 08:30 | 593 | 588
2017-03-14 09:00 | 598 | 594
2017-03-14 09:30 | 602 | 599
2017-03-14 10:00 | 584 | 582
2017-03-14 10:30 | 577 | 575
2017-03-14 11:00 | 592 | 588
2017-03-14 11:30 | 617 | 614
2017-03-14 12:00 | 620 | 616
2017-03-14 12:30 | 605 | 600
2017-03-14 13:00 | 574 | 570
2017-03-14 13:30 | 562 | 562
2017-03-14 14:00 | 569 | 568
2017-03-14 14:30 | 568 | 568
2017-03-14 15:00 | 558 | 557
2017-03-14 15:30 | 563 | 563
2017-03-14 16:00 | 568 | 567
2017-03-14 16:30 | 587 | 586
2017-03-14 17:00 | 596 | 595
2017-03-14 17:30 | 595 | 593
2017-03-14 18:00 | 587 | 585
2017-03-14 18:30 | 581 | 580
2017-03-14 19:00 | 596 | 596
2017-03-14 19:30 | 592 | 591
2017-03-14 20:00 | 590 | 589
2017-03-14 20:30 | 571 | 571
2017-03-14 21:00 | 539 | 538
2017-03-14 21:30 | 514 | 514
2017-03-14 22:00 | 485 | 484
2017-03-14 22:30 | 460 | 460
2017-03-14 23:00 | 442 | 441
2017-03-14 23:30 | 423 | 423
2017-03-15 | 399 | 399
2017-03-15 00:30 | 369 | 368
2017-03-15 01:00 | 349 | 349
2017-03-15 01:30 | 336 | 336
2017-03-15 02:00 | 339 | 339
2017-03-15 02:30 | 338 | 338
2017-03-15 03:00 | 337 | 336
2017-03-15 03:30 | 337 | 337
2017-03-15 04:00 | 337 | 337
2017-03-15 04:30 | 347 | 347
2017-03-15 05:00 | 365 | 365
2017-03-15 05:30 | 389 | 389
2017-03-15 06:00 | 409 | 409
2017-03-15 06:30 | 445 | 445
2017-03-15 07:00 | 507 | 506
2017-03-15 07:30 | 542 | 542
2017-03-15 08:00 | 552 | 552
2017-03-15 08:30 | 563 | 563
2017-03-15 09:00 | 570 | 569
2017-03-15 09:30 | 585 | 585
2017-03-15 10:00 | 575 | 575
2017-03-15 10:30 | 576 | 575
2017-03-15 11:00 | 586 | 585
2017-03-15 11:30 | 594 | 594
2017-03-15 12:00 | 597 | 596
2017-03-15 12:30 | 605 | 604
2017-03-15 13:00 | 610 | 610
2017-03-15 13:30 | 615 | 614
2017-03-15 14:00 | 618 | 616
2017-03-15 14:30 | 617 | 616
2017-03-15 15:00 | 613 | 611
2017-03-15 15:30 | 605 | 603
2017-03-15 16:00 | 611 | 610
2017-03-15 16:30 | 618 | 615
2017-03-15 17:00 | 618 | 613
2017-03-15 17:30 | 610 | 603
2017-03-15 18:00 | 606 | 597
2017-03-15 18:30 | 608 | 602
2017-03-15 19:00 | 634 | 627
2017-03-15 19:30 | 622 | 617
2017-03-15 20:00 | 607 | 605
2017-03-15 20:30 | 602 | 598
2017-03-15 21:00 | 559 | 558
2017-03-15 21:30 | 539 | 539
2017-03-15 22:00 | 525 | 524
2017-03-15 22:30 | 493 | 493
2017-03-15 23:00 | 476 | 475
2017-03-15 23:30 | 452 | 451
2017-03-16 | 429 | 429
2017-03-16 00:30 | 396 | 395
2017-03-16 01:00 | 379 | 379
2017-03-16 01:30 | 367 | 367
2017-03-16 02:00 | 360 | 359
2017-03-16 02:30 | 355 | 355
2017-03-16 03:00 | 353 | 353
2017-03-16 03:30 | 358 | 358
2017-03-16 04:00 | 362 | 362
2017-03-16 04:30 | 372 | 371
2017-03-16 05:00 | 384 | 383
2017-03-16 05:30 | 406 | 406
2017-03-16 06:00 | 435 | 435
2017-03-16 06:30 | 485 | 485
2017-03-16 07:00 | 525 | 525
2017-03-16 07:30 | 568 | 568
2017-03-16 08:00 | 590 | 587
2017-03-16 08:30 | 597 | 592
2017-03-16 09:00 | 605 | 602
2017-03-16 09:30 | 600 | 597
2017-03-16 10:00 | 597 | 594
2017-03-16 10:30 | 585 | 582
2017-03-16 11:00 | 586 | 584
2017-03-16 11:30 | 589 | 586
2017-03-16 12:00 | 599 | 596
2017-03-16 12:30 | 617 | 614
2017-03-16 13:00 | 622 | 620
2017-03-16 13:30 | 624 | 622
2017-03-16 14:00 | 647 | 641
2017-03-16 14:30 | 661 | 654
2017-03-16 15:00 | 681 | 674
2017-03-16 15:30 | 686 | 679
2017-03-16 16:00 | 689 | 682
2017-03-16 16:30 | 696 | 689
2017-03-16 17:00 | 703 | 695
2017-03-16 17:30 | 700 | 689
2017-03-16 18:00 | 691 | 680
2017-03-16 18:30 | 685 | 674
2017-03-16 19:00 | 680 | 669
2017-03-16 19:30 | 657 | 652
2017-03-16 20:00 | 642 | 638
2017-03-16 20:30 | 618 | 615
2017-03-16 21:00 | 583 | 580
2017-03-16 21:30 | 557 | 556
2017-03-16 22:00 | 535 | 534
2017-03-16 22:30 | 494 | 493
2017-03-16 23:00 | 471 | 470
2017-03-16 23:30 | 452 | 451
2017-03-17 | 432 | 430
2017-03-17 00:30 | 407 | 406
2017-03-17 01:00 | 384 | 384
2017-03-17 01:30 | 370 | 369
2017-03-17 02:00 | 359 | 358
2017-03-17 02:30 | 361 | 360
2017-03-17 03:00 | 364 | 363
2017-03-17 03:30 | 364 | 363
2017-03-17 04:00 | 368 | 366
2017-03-17 04:30 | 375 | 373
2017-03-17 05:00 | 379 | 378
2017-03-17 05:30 | 396 | 395
2017-03-17 06:00 | 427 | 425
2017-03-17 06:30 | 486 | 485
2017-03-17 07:00 | 512 | 512
2017-03-17 07:30 | 554 | 554
2017-03-17 08:00 | 568 | 567
2017-03-17 08:30 | 565 | 564
2017-03-17 09:00 | 561 | 560
2017-03-17 09:30 | 561 | 561
2017-03-17 10:00 | 568 | 568
2017-03-17 10:30 | 577 | 577
2017-03-17 11:00 | 585 | 585
2017-03-17 11:30 | 592 | 592
2017-03-17 12:00 | 604 | 604
2017-03-17 12:30 | 631 | 630
2017-03-17 13:00 | 642 | 640
2017-03-17 13:30 | 655 | 653
2017-03-17 14:00 | 654 | 652
2017-03-17 14:30 | 650 | 645
2017-03-17 15:00 | 651 | 647
2017-03-17 15:30 | 634 | 628
2017-03-17 16:00 | 608 | 601
2017-03-17 16:30 | 588 | 583
2017-03-17 17:00 | 580 | 575
2017-03-17 17:30 | 566 | 561
2017-03-17 18:00 | 557 | 555
2017-03-17 18:30 | 552 | 552
2017-03-17 19:00 | 555 | 555
2017-03-17 19:30 | 547 | 547
2017-03-17 20:00 | 542 | 542
2017-03-17 20:30 | 533 | 533
2017-03-17 21:00 | 520 | 520
2017-03-17 21:30 | 504 | 504
2017-03-17 22:00 | 487 | 486
2017-03-17 22:30 | 458 | 457
2017-03-17 23:00 | 447 | 447
2017-03-17 23:30 | 425 | 425
2017-03-18 | 398 | 397
2017-03-18 00:30 | 372 | 371
2017-03-18 01:00 | 362 | 361
2017-03-18 01:30 | 348 | 347
2017-03-18 02:00 | 343 | 342
2017-03-18 02:30 | 343 | 341
2017-03-18 03:00 | 347 | 345
2017-03-18 03:30 | 346 | 344
2017-03-18 04:00 | 350 | 348
2017-03-18 04:30 | 351 | 349
2017-03-18 05:00 | 347 | 345
2017-03-18 05:30 | 359 | 357
2017-03-18 06:00 | 371 | 370
2017-03-18 06:30 | 387 | 386
2017-03-18 07:00 | 397 | 396
2017-03-18 07:30 | 406 | 406
2017-03-18 08:00 | 417 | 417
2017-03-18 08:30 | 438 | 437
2017-03-18 09:00 | 445 | 445
2017-03-18 09:30 | 455 | 455
2017-03-18 10:00 | 456 | 456
2017-03-18 10:30 | 457 | 457
2017-03-18 11:00 | 456 | 455
2017-03-18 11:30 | 468 | 468
2017-03-18 12:00 | 491 | 491
2017-03-18 12:30 | 500 | 499
2017-03-18 13:00 | 491 | 491
2017-03-18 13:30 | 497 | 497
2017-03-18 14:00 | 517 | 517
2017-03-18 14:30 | 530 | 530
2017-03-18 15:00 | 543 | 542
2017-03-18 15:30 | 550 | 550
2017-03-18 16:00 | 570 | 570
2017-03-18 16:30 | 575 | 574
2017-03-18 17:00 | 588 | 587
2017-03-18 17:30 | 586 | 585
2017-03-18 18:00 | 583 | 582
2017-03-18 18:30 | 592 | 591
2017-03-18 19:00 | 602 | 602
2017-03-18 19:30 | 602 | 602
2017-03-18 20:00 | 596 | 595
2017-03-18 20:30 | 568 | 568
2017-03-18 21:00 | 538 | 538
2017-03-18 21:30 | 525 | 525
2017-03-18 22:00 | 513 | 513
2017-03-18 22:30 | 487 | 487
2017-03-18 23:00 | 458 | 457
2017-03-18 23:30 | 433 | 432
2017-03-19 | 405 | 405
2017-03-19 00:30 | 383 | 383
2017-03-19 01:00 | 374 | 373
2017-03-19 01:30 | 368 | 366
2017-03-19 02:00 | 361 | 358
2017-03-19 02:30 | 356 | 354
2017-03-19 03:00 | 358 | 354
2017-03-19 03:30 | 355 | 352
2017-03-19 04:00 | 359 | 356
2017-03-19 04:30 | 356 | 353
2017-03-19 05:00 | 356 | 353
2017-03-19 05:30 | 360 | 358
2017-03-19 06:00 | 367 | 365
2017-03-19 06:30 | 378 | 375
2017-03-19 07:00 | 391 | 389
2017-03-19 07:30 | 409 | 408
2017-03-19 08:00 | 420 | 419
2017-03-19 08:30 | 447 | 447
2017-03-19 09:00 | 482 | 481
2017-03-19 09:30 | 496 | 495
2017-03-19 10:00 | 493 | 492
2017-03-19 10:30 | 482 | 482
2017-03-19 11:00 | 479 | 478
2017-03-19 11:30 | 489 | 488
2017-03-19 12:00 | 499 | 499
2017-03-19 12:30 | 503 | 503
2017-03-19 13:00 | 514 | 514
2017-03-19 13:30 | 513 | 513
2017-03-19 14:00 | 523 | 523
2017-03-19 14:30 | 536 | 536
2017-03-19 15:00 | 539 | 538
2017-03-19 15:30 | 545 | 545
2017-03-19 16:00 | 567 | 567
2017-03-19 16:30 | 585 | 582
2017-03-19 17:00 | 593 | 590
2017-03-19 17:30 | 592 | 589
2017-03-19 18:00 | 593 | 590
2017-03-19 18:30 | 598 | 596
2017-03-19 19:00 | 602 | 601
2017-03-19 19:30 | 591 | 590
2017-03-19 20:00 | 585 | 584
2017-03-19 20:30 | 556 | 556
2017-03-19 21:00 | 534 | 534
2017-03-19 21:30 | 513 | 512
2017-03-19 22:00 | 496 | 495
2017-03-19 22:30 | 470 | 469
2017-03-19 23:00 | 459 | 457
2017-03-19 23:30 | 432 | 430
2017-03-20 | 410 | 407
2017-03-20 00:30 | 392 | 390
2017-03-20 01:00 | 388 | 385
2017-03-20 01:30 | 379 | 377
2017-03-20 02:00 | 376 | 373
2017-03-20 02:30 | 378 | 375
2017-03-20 03:00 | 385 | 382
2017-03-20 03:30 | 384 | 380
2017-03-20 04:00 | 388 | 384
2017-03-20 04:30 | 393 | 390
2017-03-20 05:00 | 398 | 395
2017-03-20 05:30 | 437 | 436
2017-03-20 06:00 | 474 | 469
2017-03-20 06:30 | 525 | 522
2017-03-20 07:00 | 576 | 569
2017-03-20 07:30 | 610 | 604
2017-03-20 08:00 | 626 | 619
2017-03-20 08:30 | 645 | 639
2017-03-20 09:00 | 657 | 651
2017-03-20 09:30 | 667 | 662
2017-03-20 10:00 | 670 | 664
2017-03-20 10:30 | 669 | 663
2017-03-20 11:00 | 668 | 662
2017-03-20 11:30 | 667 | 660
2017-03-20 12:00 | 675 | 668
2017-03-20 12:30 | 677 | 670
2017-03-20 13:00 | 673 | 665
2017-03-20 13:30 | 665 | 656
2017-03-20 14:00 | 665 | 657
2017-03-20 14:30 | 662 | 653
2017-03-20 15:00 | 662 | 651
2017-03-20 15:30 | 667 | 653
2017-03-20 16:00 | 668 | 657
2017-03-20 16:30 | 668 | 658
2017-03-20 17:00 | 678 | 667
2017-03-20 17:30 | 677 | 664
2017-03-20 18:00 | 667 | 656
2017-03-20 18:30 | 661 | 652
2017-03-20 19:00 | 662 | 653
2017-03-20 19:30 | 648 | 640
2017-03-20 20:00 | 629 | 626
2017-03-20 20:30 | 605 | 603
2017-03-20 21:00 | 573 | 570
2017-03-20 21:30 | 555 | 552
2017-03-20 22:00 | 528 | 526
2017-03-20 22:30 | 500 | 496
2017-03-20 23:00 | 480 | 475
2017-03-20 23:30 | 462 | 456
2017-03-21 | 446 | 436
2017-03-21 00:30 | 411 | 405
2017-03-21 01:00 | 394 | 390
2017-03-21 01:30 | 390 | 386
2017-03-21 02:00 | 386 | 380
2017-03-21 02:30 | 375 | 370
2017-03-21 03:00 | 381 | 376
2017-03-21 03:30 | 372 | 366
2017-03-21 04:00 | 370 | 364
2017-03-21 04:30 | 381 | 376
2017-03-21 05:00 | 398 | 394
2017-03-21 05:30 | 414 | 407
2017-03-21 06:00 | 447 | 443
2017-03-21 06:30 | 493 | 491
2017-03-21 07:00 | 536 | 535
2017-03-21 07:30 | 576 | 575
2017-03-21 08:00 | 606 | 604
2017-03-21 08:30 | 610 | 608
2017-03-21 09:00 | 613 | 612
2017-03-21 09:30 | 614 | 613
2017-03-21 10:00 | 619 | 618
2017-03-21 10:30 | 620 | 620
2017-03-21 11:00 | 608 | 608
2017-03-21 11:30 | 618 | 618
2017-03-21 12:00 | 618 | 618
2017-03-21 12:30 | 637 | 634
2017-03-21 13:00 | 636 | 631
2017-03-21 13:30 | 635 | 630
2017-03-21 14:00 | 641 | 637
2017-03-21 14:30 | 647 | 642
2017-03-21 15:00 | 650 | 644
2017-03-21 15:30 | 656 | 650
2017-03-21 16:00 | 676 | 669
2017-03-21 16:30 | 678 | 671
2017-03-21 17:00 | 677 | 670
2017-03-21 17:30 | 670 | 664
2017-03-21 18:00 | 664 | 658
2017-03-21 18:30 | 662 | 656
2017-03-21 19:00 | 667 | 660
2017-03-21 19:30 | 656 | 651
2017-03-21 20:00 | 642 | 641
2017-03-21 20:30 | 627 | 626
2017-03-21 21:00 | 601 | 599
2017-03-21 21:30 | 571 | 569
2017-03-21 22:00 | 546 | 544
2017-03-21 22:30 | 517 | 516
2017-03-21 23:00 | 498 | 497
2017-03-21 23:30 | 475 | 474
2017-03-22 | 455 | 453
2017-03-22 00:30 | 438 | 435
2017-03-22 01:00 | 426 | 423
2017-03-22 01:30 | 413 | 409
2017-03-22 02:00 | 408 | 403
2017-03-22 02:30 | 404 | 399
2017-03-22 03:00 | 401 | 397
2017-03-22 03:30 | 401 | 397
2017-03-22 04:00 | 399 | 395
2017-03-22 04:30 | 406 | 402
2017-03-22 05:00 | 396 | 393
2017-03-22 05:30 | 412 | 407
2017-03-22 06:00 | 450 | 444
2017-03-22 06:30 | 504 | 498
2017-03-22 07:00 | 546 | 542
2017-03-22 07:30 | 597 | 586
2017-03-22 08:00 | 610 | 601
2017-03-22 08:30 | 612 | 604
2017-03-22 09:00 | 613 | 606
2017-03-22 09:30 | 623 | 618
2017-03-22 10:00 | 642 | 638
2017-03-22 10:30 | 647 | 643
2017-03-22 11:00 | 655 | 652
2017-03-22 11:30 | 657 | 654
2017-03-22 12:00 | 649 | 645
2017-03-22 12:30 | 654 | 651
2017-03-22 13:00 | 662 | 659
2017-03-22 13:30 | 664 | 661
2017-03-22 14:00 | 662 | 658
2017-03-22 14:30 | 657 | 653
2017-03-22 15:00 | 652 | 648
2017-03-22 15:30 | 652 | 647
2017-03-22 16:00 | 653 | 647
2017-03-22 16:30 | 658 | 651
2017-03-22 17:00 | 663 | 657
2017-03-22 17:30 | 667 | 659
2017-03-22 18:00 | 666 | 656
2017-03-22 18:30 | 657 | 647
2017-03-22 19:00 | 656 | 646
2017-03-22 19:30 | 638 | 631
2017-03-22 20:00 | 623 | 621
2017-03-22 20:30 | 614 | 612
2017-03-22 21:00 | 588 | 585
2017-03-22 21:30 | 570 | 567
2017-03-22 22:00 | 555 | 553
2017-03-22 22:30 | 522 | 520
2017-03-22 23:00 | 478 | 478
2017-03-22 23:30 | 454 | 454
2017-03-23 | 434 | 433
2017-03-23 00:30 | 413 | 411
2017-03-23 01:00 | 403 | 400
2017-03-23 01:30 | 393 | 391
2017-03-23 02:00 | 386 | 384
2017-03-23 02:30 | 386 | 384
2017-03-23 03:00 | 389 | 387
2017-03-23 03:30 | 389 | 386
2017-03-23 04:00 | 392 | 389
2017-03-23 04:30 | 399 | 396
2017-03-23 05:00 | 401 | 399
2017-03-23 05:30 | 417 | 416
2017-03-23 06:00 | 451 | 450
2017-03-23 06:30 | 498 | 497
2017-03-23 07:00 | 542 | 541
2017-03-23 07:30 | 586 | 585
2017-03-23 08:00 | 607 | 607
2017-03-23 08:30 | 611 | 611
2017-03-23 09:00 | 608 | 608
2017-03-23 09:30 | 620 | 620
2017-03-23 10:00 | 634 | 632
2017-03-23 10:30 | 635 | 634
2017-03-23 11:00 | 630 | 629
2017-03-23 11:30 | 628 | 626
2017-03-23 12:00 | 632 | 631
2017-03-23 12:30 | 639 | 638
2017-03-23 13:00 | 648 | 647
2017-03-23 13:30 | 649 | 647
2017-03-23 14:00 | 653 | 652
2017-03-23 14:30 | 662 | 660
2017-03-23 15:00 | 663 | 662
2017-03-23 15:30 | 663 | 661
2017-03-23 16:00 | 669 | 667
2017-03-23 16:30 | 676 | 674
2017-03-23 17:00 | 686 | 684
2017-03-23 17:30 | 685 | 682
2017-03-23 18:00 | 681 | 679
2017-03-23 18:30 | 679 | 676
2017-03-23 19:00 | 678 | 675
2017-03-23 19:30 | 671 | 667
2017-03-23 20:00 | 661 | 658
2017-03-23 20:30 | 632 | 631
2017-03-23 21:00 | 611 | 608
2017-03-23 21:30 | 592 | 588
2017-03-23 22:00 | 570 | 567
2017-03-23 22:30 | 528 | 526
2017-03-23 23:00 | 490 | 489
2017-03-23 23:30 | 472 | 471
2017-03-24 | 453 | 452
2017-03-24 00:30 | 433 | 432
2017-03-24 01:00 | 422 | 421
2017-03-24 01:30 | 408 | 407
2017-03-24 02:00 | 403 | 402
2017-03-24 02:30 | 398 | 397
2017-03-24 03:00 | 395 | 394
2017-03-24 03:30 | 393 | 392
2017-03-24 04:00 | 396 | 394
2017-03-24 04:30 | 401 | 400
2017-03-24 05:00 | 399 | 398
2017-03-24 05:30 | 426 | 426
2017-03-24 06:00 | 449 | 448
2017-03-24 06:30 | 492 | 491
2017-03-24 07:00 | 533 | 532
2017-03-24 07:30 | 571 | 568
2017-03-24 08:00 | 582 | 580
2017-03-24 08:30 | 596 | 594
2017-03-24 09:00 | 612 | 609
2017-03-24 09:30 | 620 | 615
2017-03-24 10:00 | 620 | 616
2017-03-24 10:30 | 625 | 620
2017-03-24 11:00 | 631 | 628
2017-03-24 11:30 | 638 | 634
2017-03-24 12:00 | 654 | 651
2017-03-24 12:30 | 662 | 656
2017-03-24 13:00 | 666 | 659
2017-03-24 13:30 | 662 | 655
2017-03-24 14:00 | 661 | 655
2017-03-24 14:30 | 660 | 652
2017-03-24 15:00 | 646 | 637
2017-03-24 15:30 | 641 | 633
2017-03-24 16:00 | 644 | 636
2017-03-24 16:30 | 656 | 651
2017-03-24 17:00 | 664 | 658
2017-03-24 17:30 | 650 | 642
2017-03-24 18:00 | 639 | 629
2017-03-24 18:30 | 639 | 628
2017-03-24 19:00 | 654 | 643
2017-03-24 19:30 | 639 | 633
2017-03-24 20:00 | 612 | 612
2017-03-24 20:30 | 593 | 593
2017-03-24 21:00 | 574 | 573
2017-03-24 21:30 | 551 | 548
2017-03-24 22:00 | 537 | 535
2017-03-24 22:30 | 497 | 496
2017-03-24 23:00 | 469 | 468
2017-03-24 23:30 | 452 | 450
2017-03-25 | 431 | 430
2017-03-25 00:30 | 417 | 416
2017-03-25 01:00 | 412 | 410
2017-03-25 01:30 | 393 | 390
2017-03-25 02:00 | 382 | 379
2017-03-25 02:30 | 383 | 379
2017-03-25 03:00 | 392 | 388
2017-03-25 03:30 | 384 | 380
2017-03-25 04:00 | 382 | 378
2017-03-25 04:30 | 374 | 370
2017-03-25 05:00 | 382 | 378
2017-03-25 05:30 | 397 | 394
2017-03-25 06:00 | 408 | 405
2017-03-25 06:30 | 413 | 410
2017-03-25 07:00 | 425 | 423
2017-03-25 07:30 | 446 | 445
2017-03-25 08:00 | 451 | 450
2017-03-25 08:30 | 470 | 467
2017-03-25 09:00 | 474 | 471
2017-03-25 09:30 | 480 | 478
2017-03-25 10:00 | 491 | 489
2017-03-25 10:30 | 507 | 506
2017-03-25 11:00 | 510 | 509
2017-03-25 11:30 | 523 | 522
2017-03-25 12:00 | 528 | 527
2017-03-25 12:30 | 520 | 519
2017-03-25 13:00 | 519 | 517
2017-03-25 13:30 | 514 | 513
2017-03-25 14:00 | 513 | 512
2017-03-25 14:30 | 505 | 504
2017-03-25 15:00 | 517 | 516
2017-03-25 15:30 | 515 | 514
2017-03-25 16:00 | 519 | 519
2017-03-25 16:30 | 524 | 523
2017-03-25 17:00 | 531 | 530
2017-03-25 17:30 | 536 | 534
2017-03-25 18:00 | 541 | 540
2017-03-25 18:30 | 549 | 548
2017-03-25 19:00 | 547 | 546
2017-03-25 19:30 | 532 | 531
2017-03-25 20:00 | 530 | 529
2017-03-25 20:30 | 524 | 524
2017-03-25 21:00 | 511 | 510
2017-03-25 21:30 | 493 | 493
2017-03-25 22:00 | 484 | 483
2017-03-25 22:30 | 466 | 465
2017-03-25 23:00 | 442 | 441
2017-03-25 23:30 | 431 | 429
2017-03-26 | 416 | 413
2017-03-26 00:30 | 402 | 398
2017-03-26 01:00 | 394 | 390
2017-03-26 01:30 | 383 | 380
2017-03-26 02:00 | 384 | 380
2017-03-26 02:30 | 376 | 371
2017-03-26 03:00 | 378 | 372
2017-03-26 03:30 | 375 | 370
2017-03-26 04:00 | 369 | 363
2017-03-26 04:30 | 369 | 363
2017-03-26 05:00 | 369 | 363
2017-03-26 05:30 | 371 | 365
2017-03-26 06:00 | 377 | 371
2017-03-26 06:30 | 388 | 382
2017-03-26 07:00 | 398 | 393
2017-03-26 07:30 | 418 | 414
2017-03-26 08:00 | 423 | 420
2017-03-26 08:30 | 436 | 434
2017-03-26 09:00 | 452 | 451
2017-03-26 09:30 | 446 | 446
2017-03-26 10:00 | 437 | 437
2017-03-26 10:30 | 437 | 437
2017-03-26 11:00 | 440 | 440
2017-03-26 11:30 | 444 | 444
2017-03-26 12:00 | 454 | 454
2017-03-26 12:30 | 465 | 465
2017-03-26 13:00 | 475 | 475
2017-03-26 13:30 | 495 | 494
2017-03-26 14:00 | 502 | 502
2017-03-26 14:30 | 504 | 504
2017-03-26 15:00 | 518 | 517
2017-03-26 15:30 | 534 | 531
2017-03-26 16:00 | 556 | 553
2017-03-26 16:30 | 567 | 563
2017-03-26 17:00 | 581 | 575
2017-03-26 17:30 | 597 | 592
2017-03-26 18:00 | 600 | 594
2017-03-26 18:30 | 608 | 603
2017-03-26 19:00 | 609 | 605
2017-03-26 19:30 | 599 | 594
2017-03-26 20:00 | 593 | 587
2017-03-26 20:30 | 567 | 565
2017-03-26 21:00 | 549 | 549
2017-03-26 21:30 | 530 | 529
2017-03-26 22:00 | 516 | 515
2017-03-26 22:30 | 487 | 486
2017-03-26 23:00 | 463 | 463
2017-03-26 23:30 | 446 | 445
2017-03-27 | 424 | 424
2017-03-27 00:30 | 412 | 411
2017-03-27 01:00 | 409 | 407
2017-03-27 01:30 | 385 | 383
2017-03-27 02:00 | 374 | 371
2017-03-27 02:30 | 375 | 372
2017-03-27 03:00 | 377 | 374
2017-03-27 03:30 | 384 | 381
2017-03-27 04:00 | 386 | 383
2017-03-27 04:30 | 390 | 388
2017-03-27 05:00 | 397 | 395
2017-03-27 05:30 | 436 | 435
2017-03-27 06:00 | 471 | 470
2017-03-27 06:30 | 513 | 509
2017-03-27 07:00 | 546 | 543
2017-03-27 07:30 | 594 | 590
2017-03-27 08:00 | 613 | 608
2017-03-27 08:30 | 618 | 614
2017-03-27 09:00 | 617 | 614
2017-03-27 09:30 | 629 | 620
2017-03-27 10:00 | 627 | 620
2017-03-27 10:30 | 622 | 617
2017-03-27 11:00 | 619 | 613
2017-03-27 11:30 | 622 | 615
2017-03-27 12:00 | 629 | 622
2017-03-27 12:30 | 632 | 626
2017-03-27 13:00 | 643 | 638
2017-03-27 13:30 | 588 | 582
2017-03-27 14:00 | 564 | 558
2017-03-27 14:30 | 563 | 557
2017-03-27 15:00 | 568 | 562
2017-03-27 15:30 | 571 | 565
2017-03-27 16:00 | 579 | 574
2017-03-27 16:30 | 666 | 661
2017-03-27 17:00 | 691 | 685
2017-03-27 17:30 | 687 | 681
2017-03-27 18:00 | 680 | 673
2017-03-27 18:30 | 675 | 670
2017-03-27 19:00 | 679 | 674
2017-03-27 19:30 | 658 | 651
2017-03-27 20:00 | 651 | 647
2017-03-27 20:30 | 636 | 630
2017-03-27 21:00 | 608 | 607
2017-03-27 21:30 | 589 | 587
2017-03-27 22:00 | 564 | 563
2017-03-27 22:30 | 528 | 527
2017-03-27 23:00 | 503 | 502
2017-03-27 23:30 | 485 | 482
2017-03-28 | 459 | 454
2017-03-28 00:30 | 443 | 440
2017-03-28 01:00 | 421 | 418
2017-03-28 01:30 | 404 | 402
2017-03-28 02:00 | 396 | 394
2017-03-28 02:30 | 384 | 382
2017-03-28 03:00 | 389 | 386
2017-03-28 03:30 | 400 | 397
2017-03-28 04:00 | 394 | 391
2017-03-28 04:30 | 405 | 402
2017-03-28 05:00 | 426 | 424
2017-03-28 05:30 | 455 | 452
2017-03-28 06:00 | 475 | 471
2017-03-28 06:30 | 502 | 501
2017-03-28 07:00 | 528 | 528
2017-03-28 07:30 | 563 | 563
2017-03-28 08:00 | 574 | 574
2017-03-28 08:30 | 583 | 583
2017-03-28 09:00 | 589 | 589
2017-03-28 09:30 | 597 | 597
2017-03-28 10:00 | 597 | 597
2017-03-28 10:30 | 602 | 600
2017-03-28 11:00 | 604 | 602
2017-03-28 11:30 | 611 | 609
2017-03-28 12:00 | 620 | 618
2017-03-28 12:30 | 629 | 627
2017-03-28 13:00 | 634 | 632
2017-03-28 13:30 | 642 | 640
2017-03-28 14:00 | 657 | 653
2017-03-28 14:30 | 667 | 664
2017-03-28 15:00 | 678 | 674
2017-03-28 15:30 | 687 | 683
2017-03-28 16:00 | 695 | 692
2017-03-28 16:30 | 707 | 703
2017-03-28 17:00 | 718 | 714
2017-03-28 17:30 | 710 | 705
2017-03-28 18:00 | 699 | 694
2017-03-28 18:30 | 704 | 691
2017-03-28 19:00 | 706 | 693
2017-03-28 19:30 | 689 | 681
2017-03-28 20:00 | 680 | 674
2017-03-28 20:30 | 657 | 652
2017-03-28 21:00 | 618 | 616
2017-03-28 21:30 | 593 | 591
2017-03-28 22:00 | 569 | 568
2017-03-28 22:30 | 534 | 533
2017-03-28 23:00 | 514 | 513
2017-03-28 23:30 | 490 | 489
2017-03-29 | 456 | 455
2017-03-29 00:30 | 434 | 434
2017-03-29 01:00 | 426 | 425
2017-03-29 01:30 | 417 | 417
2017-03-29 02:00 | 411 | 410
2017-03-29 02:30 | 410 | 409
2017-03-29 03:00 | 402 | 401
2017-03-29 03:30 | 401 | 400
2017-03-29 04:00 | 402 | 402
2017-03-29 04:30 | 407 | 406
2017-03-29 05:00 | 408 | 407
2017-03-29 05:30 | 427 | 426
2017-03-29 06:00 | 456 | 456
2017-03-29 06:30 | 497 | 496
2017-03-29 07:00 | 527 | 527
2017-03-29 07:30 | 554 | 554
2017-03-29 08:00 | 582 | 581
2017-03-29 08:30 | 596 | 596
2017-03-29 09:00 | 598 | 597
2017-03-29 09:30 | 618 | 617
2017-03-29 10:00 | 632 | 631
2017-03-29 10:30 | 638 | 638
2017-03-29 11:00 | 641 | 640
2017-03-29 11:30 | 644 | 643
2017-03-29 12:00 | 642 | 642
2017-03-29 12:30 | 649 | 649
2017-03-29 13:00 | 664 | 664
2017-03-29 13:30 | 669 | 668
2017-03-29 14:00 | 668 | 667
2017-03-29 14:30 | 668 | 668
2017-03-29 15:00 | 677 | 676
2017-03-29 15:30 | 673 | 672
2017-03-29 16:00 | 682 | 680
2017-03-29 16:30 | 690 | 689
2017-03-29 17:00 | 693 | 693
2017-03-29 17:30 | 690 | 689
2017-03-29 18:00 | 681 | 680
2017-03-29 18:30 | 673 | 672
2017-03-29 19:00 | 672 | 671
2017-03-29 19:30 | 659 | 658
2017-03-29 20:00 | 658 | 657
2017-03-29 20:30 | 638 | 637
2017-03-29 21:00 | 620 | 619
2017-03-29 21:30 | 601 | 600
2017-03-29 22:00 | 577 | 576
2017-03-29 22:30 | 534 | 534
2017-03-29 23:00 | 504 | 503
2017-03-29 23:30 | 484 | 484
2017-03-30 | 457 | 457
2017-03-30 00:30 | 429 | 429
2017-03-30 01:00 | 414 | 414
2017-03-30 01:30 | 411 | 410
2017-03-30 02:00 | 400 | 400
2017-03-30 02:30 | 400 | 400
2017-03-30 03:00 | 402 | 402
2017-03-30 03:30 | 403 | 403
2017-03-30 04:00 | 414 | 413
2017-03-30 04:30 | 430 | 429
2017-03-30 05:00 | 434 | 433
2017-03-30 05:30 | 462 | 462
2017-03-30 06:00 | 495 | 494
2017-03-30 06:30 | 541 | 541
2017-03-30 07:00 | 592 | 592
2017-03-30 07:30 | 641 | 637
2017-03-30 08:00 | 656 | 650
2017-03-30 08:30 | 665 | 660
2017-03-30 09:00 | 676 | 671
2017-03-30 09:30 | 669 | 662
2017-03-30 10:00 | 665 | 660
2017-03-30 10:30 | 657 | 652
2017-03-30 11:00 | 649 | 643
2017-03-30 11:30 | 622 | 615
2017-03-30 12:00 | 613 | 607
2017-03-30 12:30 | 618 | 611
2017-03-30 13:00 | 606 | 597
2017-03-30 13:30 | 596 | 588
2017-03-30 14:00 | 589 | 583
2017-03-30 14:30 | 584 | 577
2017-03-30 15:00 | 578 | 571
2017-03-30 15:30 | 578 | 571
2017-03-30 16:00 | 582 | 575
2017-03-30 16:30 | 581 | 574
2017-03-30 17:00 | 591 | 584
2017-03-30 17:30 | 596 | 589
2017-03-30 18:00 | 610 | 603
2017-03-30 18:30 | 597 | 590
2017-03-30 19:00 | 599 | 592
2017-03-30 19:30 | 582 | 575
2017-03-30 20:00 | 560 | 557
2017-03-30 20:30 | 544 | 541
2017-03-30 21:00 | 514 | 513
2017-03-30 21:30 | 491 | 490
2017-03-30 22:00 | 474 | 471
2017-03-30 22:30 | 453 | 451
2017-03-30 23:00 | 433 | 432
2017-03-30 23:30 | 418 | 416
2017-03-31 | 393 | 391
2017-03-31 00:30 | 376 | 373
2017-03-31 01:00 | 371 | 367
2017-03-31 01:30 | 360 | 355
2017-03-31 02:00 | 349 | 344
2017-03-31 02:30 | 341 | 336
2017-03-31 03:00 | 341 | 335
2017-03-31 03:30 | 342 | 336
2017-03-31 04:00 | 342 | 336
2017-03-31 04:30 | 356 | 350
2017-03-31 05:00 | 356 | 351
2017-03-31 05:30 | 366 | 363
2017-03-31 06:00 | 386 | 384
2017-03-31 06:30 | 420 | 419
2017-03-31 07:00 | 457 | 456
2017-03-31 07:30 | 477 | 477
2017-03-31 08:00 | 496 | 496
2017-03-31 08:30 | 505 | 504
2017-03-31 09:00 | 504 | 504
2017-03-31 09:30 | 496 | 496
2017-03-31 10:00 | 487 | 486
2017-03-31 10:30 | 478 | 477
2017-03-31 11:00 | 477 | 477
2017-03-31 11:30 | 483 | 483
2017-03-31 12:00 | 491 | 490
2017-03-31 12:30 | 498 | 498
2017-03-31 13:00 | 509 | 509
2017-03-31 13:30 | 530 | 530
2017-03-31 14:00 | 536 | 536
2017-03-31 14:30 | 534 | 534
2017-03-31 15:00 | 540 | 540
2017-03-31 15:30 | 541 | 541
2017-03-31 16:00 | 541 | 539
2017-03-31 16:30 | 542 | 541
2017-03-31 17:00 | 551 | 549
2017-03-31 17:30 | 549 | 547
2017-03-31 18:00 | 551 | 548
2017-03-31 18:30 | 554 | 552
2017-03-31 19:00 | 555 | 552
2017-03-31 19:30 | 545 | 542
2017-03-31 20:00 | 540 | 538
2017-03-31 20:30 | 532 | 531
2017-03-31 21:00 | 523 | 522
2017-03-31 21:30 | 503 | 501
2017-03-31 22:00 | 485 | 485
2017-03-31 22:30 | 468 | 468
2017-03-31 23:00 | 453 | 453
2017-03-31 23:30 | 437 | 435
2017-04-01 | 419 | 416
2017-04-01 00:30 | 396 | 391
2017-04-01 01:00 | 384 | 377
2017-04-01 01:30 | 376 | 368
2017-04-01 02:00 | 372 | 361
2017-04-01 02:30 | 359 | 347
2017-04-01 03:00 | 354 | 341
2017-04-01 03:30 | 355 | 341
2017-04-01 04:00 | 356 | 342
2017-04-01 04:30 | 359 | 346
2017-04-01 05:00 | 366 | 353
2017-04-01 05:30 | 375 | 363
2017-04-01 06:00 | 387 | 376
2017-04-01 06:30 | 403 | 392
2017-04-01 07:00 | 414 | 404
2017-04-01 07:30 | 431 | 424
2017-04-01 08:00 | 435 | 431
2017-04-01 08:30 | 442 | 438
2017-04-01 09:00 | 445 | 443
2017-04-01 09:30 | 444 | 442
2017-04-01 10:00 | 441 | 439
2017-04-01 10:30 | 437 | 434
2017-04-01 11:00 | 436 | 433
2017-04-01 11:30 | 429 | 426
2017-04-01 12:00 | 430 | 427
2017-04-01 12:30 | 433 | 431
2017-04-01 13:00 | 436 | 434
2017-04-01 13:30 | 446 | 444
2017-04-01 14:00 | 462 | 459
2017-04-01 14:30 | 474 | 472
2017-04-01 15:00 | 481 | 479
2017-04-01 15:30 | 491 | 489
2017-04-01 16:00 | 503 | 501
2017-04-01 16:30 | 513 | 511
2017-04-01 17:00 | 528 | 526
2017-04-01 17:30 | 527 | 524
2017-04-01 18:00 | 527 | 525
2017-04-01 18:30 | 539 | 537
2017-04-01 19:00 | 544 | 543
2017-04-01 19:30 | 530 | 528
2017-04-01 20:00 | 513 | 510
2017-04-01 20:30 | 511 | 508
2017-04-01 21:00 | 495 | 491
2017-04-01 21:30 | 481 | 478
2017-04-01 22:00 | 474 | 470
2017-04-01 22:30 | 466 | 462
2017-04-01 23:00 | 456 | 451
2017-04-01 23:30 | 443 | 438
2017-04-02 | 422 | 417
2017-04-02 00:30 | 400 | 393
2017-04-02 01:00 | 390 | 382
2017-04-02 01:30 | 382 | 372
2017-04-02 02:00 | 382 | 371
2017-04-02 02:30 | 384 | 372
2017-04-02 03:00 | 382 | 370
2017-04-02 03:30 | 381 | 369
2017-04-02 04:00 | 379 | 367
2017-04-02 04:30 | 381 | 368
2017-04-02 05:00 | 370 | 357
2017-04-02 05:30 | 371 | 358
2017-04-02 06:00 | 378 | 365
2017-04-02 06:30 | 385 | 371
2017-04-02 07:00 | 400 | 388
2017-04-02 07:30 | 422 | 411
2017-04-02 08:00 | 429 | 421
2017-04-02 08:30 | 438 | 431
2017-04-02 09:00 | 451 | 445
2017-04-02 09:30 | 452 | 448
2017-04-02 10:00 | 444 | 440
2017-04-02 10:30 | 444 | 441
2017-04-02 11:00 | 436 | 433
2017-04-02 11:30 | 425 | 421
2017-04-02 12:00 | 423 | 420
2017-04-02 12:30 | 415 | 411
2017-04-02 13:00 | 414 | 410
2017-04-02 13:30 | 415 | 411
2017-04-02 14:00 | 420 | 417
2017-04-02 14:30 | 429 | 427
2017-04-02 15:00 | 425 | 422
2017-04-02 15:30 | 431 | 428
2017-04-02 16:00 | 442 | 439
2017-04-02 16:30 | 464 | 462
2017-04-02 17:00 | 481 | 478
2017-04-02 17:30 | 488 | 485
2017-04-02 18:00 | 508 | 505
2017-04-02 18:30 | 524 | 522
2017-04-02 19:00 | 523 | 521
2017-04-02 19:30 | 511 | 508
2017-04-02 20:00 | 502 | 500
2017-04-02 20:30 | 490 | 488
2017-04-02 21:00 | 470 | 467
2017-04-02 21:30 | 456 | 454
2017-04-02 22:00 | 448 | 446
2017-04-02 22:30 | 445 | 441
2017-04-02 23:00 | 440 | 436
2017-04-02 23:30 | 427 | 422
2017-04-03 | 406 | 399
2017-04-03 00:30 | 392 | 383
2017-04-03 01:00 | 384 | 373
2017-04-03 01:30 | 376 | 362
2017-04-03 02:00 | 368 | 354
2017-04-03 02:30 | 372 | 358
2017-04-03 03:00 | 367 | 351
2017-04-03 03:30 | 369 | 354
2017-04-03 04:00 | 368 | 353
2017-04-03 04:30 | 374 | 360
2017-04-03 05:00 | 385 | 371
2017-04-03 05:30 | 409 | 399
2017-04-03 06:00 | 428 | 421
2017-04-03 06:30 | 473 | 468
2017-04-03 07:00 | 498 | 495
2017-04-03 07:30 | 535 | 532
2017-04-03 08:00 | 550 | 546
2017-04-03 08:30 | 555 | 551
2017-04-03 09:00 | 552 | 549
2017-04-03 09:30 | 559 | 557
2017-04-03 10:00 | 564 | 562
2017-04-03 10:30 | 555 | 553
2017-04-03 11:00 | 545 | 543
2017-04-03 11:30 | 557 | 554
2017-04-03 12:00 | 558 | 555
2017-04-03 12:30 | 559 | 555
2017-04-03 13:00 | 550 | 546
2017-04-03 13:30 | 543 | 539
2017-04-03 14:00 | 566 | 564
2017-04-03 14:30 | 571 | 568
2017-04-03 15:00 | 568 | 565
2017-04-03 15:30 | 565 | 561
2017-04-03 16:00 | 575 | 571
2017-04-03 16:30 | 591 | 587
2017-04-03 17:00 | 605 | 601
2017-04-03 17:30 | 613 | 608
2017-04-03 18:00 | 616 | 610
2017-04-03 18:30 | 620 | 614
2017-04-03 19:00 | 619 | 611
2017-04-03 19:30 | 602 | 595
2017-04-03 20:00 | 589 | 583
2017-04-03 20:30 | 578 | 571
2017-04-03 21:00 | 555 | 548
2017-04-03 21:30 | 529 | 526
2017-04-03 22:00 | 518 | 516
2017-04-03 22:30 | 497 | 495
2017-04-03 23:00 | 482 | 480
2017-04-03 23:30 | 467 | 462
2017-04-04 | 445 | 440
2017-04-04 00:30 | 424 | 417
2017-04-04 01:00 | 410 | 402
2017-04-04 01:30 | 402 | 393
2017-04-04 02:00 | 400 | 391
2017-04-04 02:30 | 395 | 385
2017-04-04 03:00 | 398 | 387
2017-04-04 03:30 | 393 | 381
2017-04-04 04:00 | 396 | 384
2017-04-04 04:30 | 400 | 390
2017-04-04 05:00 | 410 | 401
2017-04-04 05:30 | 432 | 427
2017-04-04 06:00 | 456 | 452
2017-04-04 06:30 | 493 | 492
2017-04-04 07:00 | 522 | 522
2017-04-04 07:30 | 548 | 547
2017-04-04 08:00 | 555 | 552
2017-04-04 08:30 | 550 | 548
2017-04-04 09:00 | 548 | 546
2017-04-04 09:30 | 544 | 543
2017-04-04 10:00 | 547 | 546
2017-04-04 10:30 | 566 | 566
2017-04-04 11:00 | 558 | 556
2017-04-04 11:30 | 560 | 558
2017-04-04 12:00 | 577 | 575
2017-04-04 12:30 | 559 | 557
2017-04-04 13:00 | 573 | 571
2017-04-04 13:30 | 575 | 572
2017-04-04 14:00 | 579 | 575
2017-04-04 14:30 | 594 | 591
2017-04-04 15:00 | 576 | 574
2017-04-04 15:30 | 576 | 574
2017-04-04 16:00 | 592 | 590
2017-04-04 16:30 | 604 | 603
2017-04-04 17:00 | 612 | 610
2017-04-04 17:30 | 614 | 612
2017-04-04 18:00 | 616 | 613
2017-04-04 18:30 | 618 | 616
2017-04-04 19:00 | 622 | 620
2017-04-04 19:30 | 610 | 607
2017-04-04 20:00 | 611 | 608
2017-04-04 20:30 | 605 | 601
2017-04-04 21:00 | 575 | 572
2017-04-04 21:30 | 560 | 556
2017-04-04 22:00 | 548 | 543
2017-04-04 22:30 | 522 | 518
2017-04-04 23:00 | 501 | 497
2017-04-04 23:30 | 486 | 482
2017-04-05 | 467 | 461
2017-04-05 00:30 | 441 | 433
2017-04-05 01:00 | 429 | 420
2017-04-05 01:30 | 420 | 410
2017-04-05 02:00 | 415 | 404
2017-04-05 02:30 | 412 | 401
2017-04-05 03:00 | 411 | 399
2017-04-05 03:30 | 407 | 395
2017-04-05 04:00 | 404 | 392
2017-04-05 04:30 | 409 | 397
2017-04-05 05:00 | 415 | 405
2017-04-05 05:30 | 437 | 431
2017-04-05 06:00 | 462 | 458
2017-04-05 06:30 | 497 | 496
2017-04-05 07:00 | 529 | 526
2017-04-05 07:30 | 548 | 546
2017-04-05 08:00 | 558 | 556
2017-04-05 08:30 | 563 | 556
2017-04-05 09:00 | 545 | 542
2017-04-05 09:30 | 540 | 537
2017-04-05 10:00 | 547 | 545
2017-04-05 10:30 | 541 | 540
2017-04-05 11:00 | 541 | 540
2017-04-05 11:30 | 532 | 530
2017-04-05 12:00 | 543 | 542
2017-04-05 12:30 | 539 | 538
2017-04-05 13:00 | 548 | 546
2017-04-05 13:30 | 560 | 559
2017-04-05 14:00 | 566 | 564
2017-04-05 14:30 | 581 | 579
2017-04-05 15:00 | 609 | 606
2017-04-05 15:30 | 587 | 584
2017-04-05 16:00 | 581 | 577
2017-04-05 16:30 | 589 | 585
2017-04-05 17:00 | 597 | 592
2017-04-05 17:30 | 598 | 594
2017-04-05 18:00 | 602 | 598
2017-04-05 18:30 | 612 | 608
2017-04-05 19:00 | 615 | 610
2017-04-05 19:30 | 600 | 594
2017-04-05 20:00 | 598 | 593
2017-04-05 20:30 | 601 | 595
2017-04-05 21:00 | 576 | 572
2017-04-05 21:30 | 551 | 547
2017-04-05 22:00 | 531 | 527
2017-04-05 22:30 | 517 | 514
2017-04-05 23:00 | 505 | 501
2017-04-05 23:30 | 481 | 476
2017-04-06 | 446 | 440
2017-04-06 00:30 | 425 | 416
2017-04-06 01:00 | 409 | 399
2017-04-06 01:30 | 400 | 386
2017-04-06 02:00 | 392 | 377
2017-04-06 02:30 | 389 | 372
2017-04-06 03:00 | 393 | 375
2017-04-06 03:30 | 394 | 376
2017-04-06 04:00 | 396 | 379
2017-04-06 04:30 | 408 | 393
2017-04-06 05:00 | 421 | 408
2017-04-06 05:30 | 446 | 438
2017-04-06 06:00 | 475 | 467
2017-04-06 06:30 | 503 | 497
2017-04-06 07:00 | 541 | 538
2017-04-06 07:30 | 566 | 564
2017-04-06 08:00 | 578 | 574
2017-04-06 08:30 | 579 | 575
2017-04-06 09:00 | 572 | 569
2017-04-06 09:30 | 578 | 575
2017-04-06 10:00 | 576 | 575
2017-04-06 10:30 | 571 | 570
2017-04-06 11:00 | 575 | 574
2017-04-06 11:30 | 563 | 562
2017-04-06 12:00 | 572 | 571
2017-04-06 12:30 | 572 | 571
2017-04-06 13:00 | 575 | 574
2017-04-06 13:30 | 578 | 578
2017-04-06 14:00 | 583 | 582
2017-04-06 14:30 | 587 | 586
2017-04-06 15:00 | 581 | 580
2017-04-06 15:30 | 599 | 598
2017-04-06 16:00 | 620 | 618
2017-04-06 16:30 | 602 | 600
2017-04-06 17:00 | 614 | 611
2017-04-06 17:30 | 615 | 613
2017-04-06 18:00 | 623 | 621
2017-04-06 18:30 | 619 | 617
2017-04-06 19:00 | 617 | 614
2017-04-06 19:30 | 608 | 605
2017-04-06 20:00 | 610 | 606
2017-04-06 20:30 | 603 | 600
2017-04-06 21:00 | 586 | 583
2017-04-06 21:30 | 563 | 559
2017-04-06 22:00 | 544 | 540
2017-04-06 22:30 | 529 | 525
2017-04-06 23:00 | 514 | 512
2017-04-06 23:30 | 496 | 493
2017-04-07 | 463 | 458
2017-04-07 00:30 | 440 | 434
2017-04-07 01:00 | 424 | 415
2017-04-07 01:30 | 410 | 401
2017-04-07 02:00 | 401 | 391
2017-04-07 02:30 | 395 | 384
2017-04-07 03:00 | 392 | 382
2017-04-07 03:30 | 390 | 380
2017-04-07 04:00 | 387 | 377
2017-04-07 04:30 | 391 | 381
2017-04-07 05:00 | 402 | 394
2017-04-07 05:30 | 428 | 421
2017-04-07 06:00 | 446 | 439
2017-04-07 06:30 | 477 | 470
2017-04-07 07:00 | 510 | 499
2017-04-07 07:30 | 543 | 531
2017-04-07 08:00 | 563 | 550
2017-04-07 08:30 | 566 | 552
2017-04-07 09:00 | 555 | 543
2017-04-07 09:30 | 464 | 453
2017-04-07 10:00 | 544 | 534
2017-04-07 10:30 | 542 | 531
2017-04-07 11:00 | 537 | 524
2017-04-07 11:30 | 515 | 503
2017-04-07 12:00 | 478 | 465
2017-04-07 12:30 | 457 | 446
2017-04-07 13:00 | 545 | 532
2017-04-07 13:30 | 544 | 531
2017-04-07 14:00 | 545 | 532
2017-04-07 14:30 | 551 | 538
2017-04-07 15:00 | 555 | 543
2017-04-07 15:30 | 557 | 545
2017-04-07 16:00 | 567 | 554
2017-04-07 16:30 | 586 | 574
2017-04-07 17:00 | 600 | 588
2017-04-07 17:30 | 596 | 583
2017-04-07 18:00 | 595 | 582
2017-04-07 18:30 | 594 | 581
2017-04-07 19:00 | 593 | 580
2017-04-07 19:30 | 584 | 568
2017-04-07 20:00 | 581 | 564
2017-04-07 20:30 | 571 | 556
2017-04-07 21:00 | 546 | 533
2017-04-07 21:30 | 534 | 520
2017-04-07 22:00 | 512 | 507
2017-04-07 22:30 | 486 | 482
2017-04-07 23:00 | 473 | 469
2017-04-07 23:30 | 462 | 457
2017-04-08 | 437 | 432
2017-04-08 00:30 | 410 | 404
2017-04-08 01:00 | 396 | 390
2017-04-08 01:30 | 386 | 379
2017-04-08 02:00 | 377 | 369
2017-04-08 02:30 | 374 | 365
2017-04-08 03:00 | 371 | 362
2017-04-08 03:30 | 366 | 357
2017-04-08 04:00 | 359 | 350
2017-04-08 04:30 | 356 | 347
2017-04-08 05:00 | 356 | 347
2017-04-08 05:30 | 367 | 359
2017-04-08 06:00 | 377 | 370
2017-04-08 06:30 | 385 | 378
2017-04-08 07:00 | 389 | 383
2017-04-08 07:30 | 410 | 405
2017-04-08 08:00 | 421 | 415
2017-04-08 08:30 | 436 | 431
2017-04-08 09:00 | 445 | 440
2017-04-08 09:30 | 448 | 444
2017-04-08 10:00 | 448 | 444
2017-04-08 10:30 | 435 | 432
2017-04-08 11:00 | 428 | 425
2017-04-08 11:30 | 432 | 429
2017-04-08 12:00 | 433 | 430
2017-04-08 12:30 | 428 | 424
2017-04-08 13:00 | 441 | 438
2017-04-08 13:30 | 446 | 443
2017-04-08 14:00 | 450 | 447
2017-04-08 14:30 | 440 | 438
2017-04-08 15:00 | 447 | 444
2017-04-08 15:30 | 464 | 461
2017-04-08 16:00 | 480 | 477
2017-04-08 16:30 | 486 | 483
2017-04-08 17:00 | 499 | 496
2017-04-08 17:30 | 505 | 502
2017-04-08 18:00 | 508 | 505
2017-04-08 18:30 | 519 | 516
2017-04-08 19:00 | 517 | 513
2017-04-08 19:30 | 509 | 504
2017-04-08 20:00 | 500 | 496
2017-04-08 20:30 | 487 | 484
2017-04-08 21:00 | 470 | 466
2017-04-08 21:30 | 457 | 453
2017-04-08 22:00 | 451 | 446
2017-04-08 22:30 | 436 | 431
2017-04-08 23:00 | 415 | 410
2017-04-08 23:30 | 410 | 402
2017-04-09 | 392 | 385
2017-04-09 00:30 | 381 | 372
2017-04-09 01:00 | 374 | 365
2017-04-09 01:30 | 366 | 356
2017-04-09 02:00 | 355 | 344
2017-04-09 02:30 | 346 | 335
2017-04-09 03:00 | 346 | 334
2017-04-09 03:30 | 347 | 335
2017-04-09 04:00 | 347 | 335
2017-04-09 04:30 | 345 | 333
2017-04-09 05:00 | 344 | 332
2017-04-09 05:30 | 350 | 339
2017-04-09 06:00 | 357 | 346
2017-04-09 06:30 | 360 | 348
2017-04-09 07:00 | 369 | 358
2017-04-09 07:30 | 383 | 374
2017-04-09 08:00 | 392 | 384
2017-04-09 08:30 | 409 | 402
2017-04-09 09:00 | 413 | 407
2017-04-09 09:30 | 408 | 403
2017-04-09 10:00 | 405 | 400
2017-04-09 10:30 | 404 | 400
2017-04-09 11:00 | 405 | 401
2017-04-09 11:30 | 403 | 398
2017-04-09 12:00 | 407 | 403
2017-04-09 12:30 | 413 | 408
2017-04-09 13:00 | 415 | 411
2017-04-09 13:30 | 422 | 417
2017-04-09 14:00 | 421 | 417
2017-04-09 14:30 | 425 | 421
2017-04-09 15:00 | 434 | 431
2017-04-09 15:30 | 432 | 429
2017-04-09 16:00 | 446 | 443
2017-04-09 16:30 | 465 | 463
2017-04-09 17:00 | 487 | 484
2017-04-09 17:30 | 499 | 496
2017-04-09 18:00 | 514 | 511
2017-04-09 18:30 | 533 | 530
2017-04-09 19:00 | 528 | 525
2017-04-09 19:30 | 519 | 515
2017-04-09 20:00 | 507 | 503
2017-04-09 20:30 | 506 | 501
2017-04-09 21:00 | 491 | 487
2017-04-09 21:30 | 483 | 479
2017-04-09 22:00 | 480 | 475
2017-04-09 22:30 | 456 | 452
2017-04-09 23:00 | 435 | 431
2017-04-09 23:30 | 423 | 418
2017-04-10 | 407 | 400
2017-04-10 00:30 | 386 | 377
2017-04-10 01:00 | 367 | 357
2017-04-10 01:30 | 362 | 351
2017-04-10 02:00 | 357 | 346
2017-04-10 02:30 | 357 | 346
2017-04-10 03:00 | 344 | 332
2017-04-10 03:30 | 342 | 330
2017-04-10 04:00 | 342 | 329
2017-04-10 04:30 | 350 | 339
2017-04-10 05:00 | 366 | 356
2017-04-10 05:30 | 386 | 379
2017-04-10 06:00 | 422 | 417
2017-04-10 06:30 | 459 | 455
2017-04-10 07:00 | 486 | 482
2017-04-10 07:30 | 514 | 510
2017-04-10 08:00 | 533 | 529
2017-04-10 08:30 | 545 | 542
2017-04-10 09:00 | 541 | 539
2017-04-10 09:30 | 539 | 537
2017-04-10 10:00 | 540 | 536
2017-04-10 10:30 | 535 | 530
2017-04-10 11:00 | 535 | 531
2017-04-10 11:30 | 533 | 528
2017-04-10 12:00 | 534 | 530
2017-04-10 12:30 | 536 | 533
2017-04-10 13:00 | 547 | 543
2017-04-10 13:30 | 558 | 551
2017-04-10 14:00 | 562 | 555
2017-04-10 14:30 | 571 | 562
2017-04-10 15:00 | 577 | 570
2017-04-10 15:30 | 580 | 573
2017-04-10 16:00 | 584 | 577
2017-04-10 16:30 | 593 | 585
2017-04-10 17:00 | 608 | 600
2017-04-10 17:30 | 608 | 600
2017-04-10 18:00 | 607 | 599
2017-04-10 18:30 | 612 | 602
2017-04-10 19:00 | 606 | 594
2017-04-10 19:30 | 588 | 577
2017-04-10 20:00 | 585 | 574
2017-04-10 20:30 | 578 | 566
2017-04-10 21:00 | 554 | 546
2017-04-10 21:30 | 538 | 530
2017-04-10 22:00 | 528 | 519
2017-04-10 22:30 | 503 | 492
2017-04-10 23:00 | 477 | 465
2017-04-10 23:30 | 459 | 446
2017-04-11 | 442 | 427
2017-04-11 00:30 | 418 | 404
2017-04-11 01:00 | 401 | 387
2017-04-11 01:30 | 392 | 377
2017-04-11 02:00 | 387 | 372
2017-04-11 02:30 | 390 | 374
2017-04-11 03:00 | 392 | 376
2017-04-11 03:30 | 390 | 373
2017-04-11 04:00 | 384 | 367
2017-04-11 04:30 | 391 | 376
2017-04-11 05:00 | 399 | 384
2017-04-11 05:30 | 410 | 398
2017-04-11 06:00 | 424 | 414
2017-04-11 06:30 | 454 | 447
2017-04-11 07:00 | 487 | 480
2017-04-11 07:30 | 505 | 499
2017-04-11 08:00 | 502 | 497
2017-04-11 08:30 | 501 | 496
2017-04-11 09:00 | 494 | 488
2017-04-11 09:30 | 507 | 499
2017-04-11 10:00 | 498 | 490
2017-04-11 10:30 | 490 | 485
2017-04-11 11:00 | 481 | 477
2017-04-11 11:30 | 479 | 474
2017-04-11 12:00 | 485 | 481
2017-04-11 12:30 | 489 | 486
2017-04-11 13:00 | 498 | 493
2017-04-11 13:30 | 506 | 501
2017-04-11 14:00 | 511 | 507
2017-04-11 14:30 | 520 | 516
2017-04-11 15:00 | 505 | 502
2017-04-11 15:30 | 507 | 503
2017-04-11 16:00 | 521 | 514
2017-04-11 16:30 | 535 | 529
2017-04-11 17:00 | 547 | 540
2017-04-11 17:30 | 548 | 541
2017-04-11 18:00 | 554 | 547
2017-04-11 18:30 | 568 | 560
2017-04-11 19:00 | 568 | 558
2017-04-11 19:30 | 554 | 543
2017-04-11 20:00 | 556 | 545
2017-04-11 20:30 | 555 | 543
2017-04-11 21:00 | 535 | 521
2017-04-11 21:30 | 516 | 505
2017-04-11 22:00 | 503 | 490
2017-04-11 22:30 | 470 | 456
2017-04-11 23:00 | 445 | 433
2017-04-11 23:30 | 435 | 423
2017-04-12 | 416 | 403
2017-04-12 00:30 | 391 | 376
2017-04-12 01:00 | 372 | 355
2017-04-12 01:30 | 368 | 350
2017-04-12 02:00 | 363 | 344
2017-04-12 02:30 | 364 | 344
2017-04-12 03:00 | 366 | 345
2017-04-12 03:30 | 366 | 345
2017-04-12 04:00 | 364 | 343
2017-04-12 04:30 | 372 | 353
2017-04-12 05:00 | 386 | 369
2017-04-12 05:30 | 404 | 390
2017-04-12 06:00 | 420 | 409
2017-04-12 06:30 | 443 | 433
2017-04-12 07:00 | 467 | 461
2017-04-12 07:30 | 491 | 485
2017-04-12 08:00 | 505 | 500
2017-04-12 08:30 | 516 | 510
2017-04-12 09:00 | 503 | 499
2017-04-12 09:30 | 505 | 501
2017-04-12 10:00 | 502 | 498
2017-04-12 10:30 | 498 | 495
2017-04-12 11:00 | 502 | 500
2017-04-12 11:30 | 514 | 509
2017-04-12 12:00 | 521 | 515
2017-04-12 12:30 | 525 | 520
2017-04-12 13:00 | 537 | 532
2017-04-12 13:30 | 547 | 542
2017-04-12 14:00 | 547 | 543
2017-04-12 14:30 | 553 | 549
2017-04-12 15:00 | 552 | 548
2017-04-12 15:30 | 567 | 558
2017-04-12 16:00 | 582 | 569
2017-04-12 16:30 | 581 | 576
2017-04-12 17:00 | 587 | 582
2017-04-12 17:30 | 591 | 586
2017-04-12 18:00 | 593 | 588
2017-04-12 18:30 | 589 | 582
2017-04-12 19:00 | 589 | 580
2017-04-12 19:30 | 584 | 575
2017-04-12 20:00 | 577 | 570
2017-04-12 20:30 | 565 | 558
2017-04-12 21:00 | 553 | 549
2017-04-12 21:30 | 537 | 532
2017-04-12 22:00 | 514 | 508
2017-04-12 22:30 | 477 | 470
2017-04-12 23:00 | 452 | 444
2017-04-12 23:30 | 437 | 430
2017-04-13 | 415 | 409
2017-04-13 00:30 | 398 | 390
2017-04-13 01:00 | 385 | 376
2017-04-13 01:30 | 373 | 363
2017-04-13 02:00 | 371 | 361
2017-04-13 02:30 | 371 | 361
2017-04-13 03:00 | 369 | 359
2017-04-13 03:30 | 367 | 358
2017-04-13 04:00 | 365 | 356
2017-04-13 04:30 | 367 | 359
2017-04-13 05:00 | 377 | 369
2017-04-13 05:30 | 396 | 390
2017-04-13 06:00 | 410 | 406
2017-04-13 06:30 | 437 | 435
2017-04-13 07:00 | 465 | 461
2017-04-13 07:30 | 496 | 493
2017-04-13 08:00 | 516 | 514
2017-04-13 08:30 | 526 | 521
2017-04-13 09:00 | 519 | 514
2017-04-13 09:30 | 510 | 506
2017-04-13 10:00 | 509 | 506
2017-04-13 10:30 | 512 | 509
2017-04-13 11:00 | 513 | 510
2017-04-13 11:30 | 516 | 513
2017-04-13 12:00 | 527 | 525
2017-04-13 12:30 | 544 | 539
2017-04-13 13:00 | 549 | 545
2017-04-13 13:30 | 553 | 549
2017-04-13 14:00 | 546 | 542
2017-04-13 14:30 | 543 | 539
2017-04-13 15:00 | 551 | 546
2017-04-13 15:30 | 555 | 550
2017-04-13 16:00 | 554 | 549
2017-04-13 16:30 | 558 | 553
2017-04-13 17:00 | 574 | 568
2017-04-13 17:30 | 580 | 574
2017-04-13 18:00 | 582 | 576
2017-04-13 18:30 | 578 | 571
2017-04-13 19:00 | 578 | 571
2017-04-13 19:30 | 570 | 559
2017-04-13 20:00 | 566 | 553
2017-04-13 20:30 | 552 | 543
2017-04-13 21:00 | 538 | 529
2017-04-13 21:30 | 528 | 517
2017-04-13 22:00 | 520 | 508
2017-04-13 22:30 | 487 | 474
2017-04-13 23:00 | 465 | 455
2017-04-13 23:30 | 448 | 438
2017-04-14 | 421 | 412
2017-04-14 00:30 | 396 | 384
2017-04-14 01:00 | 368 | 353
2017-04-14 01:30 | 363 | 346
2017-04-14 02:00 | 356 | 339
2017-04-14 02:30 | 363 | 346
2017-04-14 03:00 | 367 | 350
2017-04-14 03:30 | 362 | 345
2017-04-14 04:00 | 357 | 340
2017-04-14 04:30 | 354 | 336
2017-04-14 05:00 | 353 | 335
2017-04-14 05:30 | 359 | 341
2017-04-14 06:00 | 372 | 355
2017-04-14 06:30 | 390 | 373
2017-04-14 07:00 | 401 | 385
2017-04-14 07:30 | 416 | 402
2017-04-14 08:00 | 437 | 425
2017-04-14 08:30 | 437 | 426
2017-04-14 09:00 | 435 | 425
2017-04-14 09:30 | 440 | 430
2017-04-14 10:00 | 434 | 425
2017-04-14 10:30 | 430 | 421
2017-04-14 11:00 | 426 | 418
2017-04-14 11:30 | 423 | 414
2017-04-14 12:00 | 423 | 416
2017-04-14 12:30 | 412 | 405
2017-04-14 13:00 | 422 | 415
2017-04-14 13:30 | 420 | 413
2017-04-14 14:00 | 413 | 407
2017-04-14 14:30 | 412 | 405
2017-04-14 15:00 | 422 | 415
2017-04-14 15:30 | 436 | 425
2017-04-14 16:00 | 452 | 441
2017-04-14 16:30 | 465 | 454
2017-04-14 17:00 | 485 | 475
2017-04-14 17:30 | 494 | 485
2017-04-14 18:00 | 506 | 499
2017-04-14 18:30 | 505 | 498
2017-04-14 19:00 | 504 | 496
2017-04-14 19:30 | 497 | 489
2017-04-14 20:00 | 499 | 491
2017-04-14 20:30 | 495 | 487
2017-04-14 21:00 | 478 | 469
2017-04-14 21:30 | 472 | 461
2017-04-14 22:00 | 473 | 462
2017-04-14 22:30 | 456 | 447
2017-04-14 23:00 | 438 | 430
2017-04-14 23:30 | 426 | 417
2017-04-15 | 403 | 391
2017-04-15 00:30 | 387 | 373
2017-04-15 01:00 | 381 | 367
2017-04-15 01:30 | 369 | 354
2017-04-15 02:00 | 367 | 351
2017-04-15 02:30 | 368 | 352
2017-04-15 03:00 | 374 | 358
2017-04-15 03:30 | 371 | 355
2017-04-15 04:00 | 372 | 356
2017-04-15 04:30 | 373 | 356
2017-04-15 05:00 | 372 | 356
2017-04-15 05:30 | 373 | 357
2017-04-15 06:00 | 376 | 361
2017-04-15 06:30 | 387 | 372
2017-04-15 07:00 | 389 | 374
2017-04-15 07:30 | 401 | 388
2017-04-15 08:00 | 411 | 399
2017-04-15 08:30 | 415 | 405
2017-04-15 09:00 | 415 | 406
2017-04-15 09:30 | 413 | 405
2017-04-15 10:00 | 410 | 403
2017-04-15 10:30 | 409 | 402
2017-04-15 11:00 | 410 | 404
2017-04-15 11:30 | 408 | 402
2017-04-15 12:00 | 411 | 405
2017-04-15 12:30 | 411 | 405
2017-04-15 13:00 | 411 | 406
2017-04-15 13:30 | 416 | 411
2017-04-15 14:00 | 422 | 417
2017-04-15 14:30 | 428 | 422
2017-04-15 15:00 | 431 | 425
2017-04-15 15:30 | 440 | 435
2017-04-15 16:00 | 448 | 443
2017-04-15 16:30 | 452 | 447
2017-04-15 17:00 | 463 | 458
2017-04-15 17:30 | 472 | 468
2017-04-15 18:00 | 483 | 480
2017-04-15 18:30 | 489 | 482
2017-04-15 19:00 | 492 | 483
2017-04-15 19:30 | 494 | 484
2017-04-15 20:00 | 485 | 477
2017-04-15 20:30 | 481 | 473
2017-04-15 21:00 | 464 | 457
2017-04-15 21:30 | 456 | 450
2017-04-15 22:00 | 459 | 453
2017-04-15 22:30 | 449 | 443
2017-04-15 23:00 | 432 | 425
2017-04-15 23:30 | 423 | 414
2017-04-16 | 406 | 395
2017-04-16 00:30 | 389 | 376
2017-04-16 01:00 | 383 | 369
2017-04-16 01:30 | 376 | 361
2017-04-16 02:00 | 370 | 355
2017-04-16 02:30 | 372 | 355
2017-04-16 03:00 | 372 | 353
2017-04-16 03:30 | 361 | 344
2017-04-16 04:00 | 362 | 346
2017-04-16 04:30 | 367 | 351
2017-04-16 05:00 | 363 | 347
2017-04-16 05:30 | 364 | 348
2017-04-16 06:00 | 368 | 352
2017-04-16 06:30 | 372 | 355
2017-04-16 07:00 | 377 | 361
2017-04-16 07:30 | 396 | 381
2017-04-16 08:00 | 403 | 390
2017-04-16 08:30 | 407 | 395
2017-04-16 09:00 | 410 | 400
2017-04-16 09:30 | 415 | 406
2017-04-16 10:00 | 409 | 400
2017-04-16 10:30 | 409 | 401
2017-04-16 11:00 | 399 | 391
2017-04-16 11:30 | 394 | 386
2017-04-16 12:00 | 388 | 380
2017-04-16 12:30 | 386 | 378
2017-04-16 13:00 | 392 | 384
2017-04-16 13:30 | 397 | 390
2017-04-16 14:00 | 398 | 390
2017-04-16 14:30 | 403 | 396
2017-04-16 15:00 | 401 | 394
2017-04-16 15:30 | 412 | 405
2017-04-16 16:00 | 429 | 423
2017-04-16 16:30 | 443 | 437
2017-04-16 17:00 | 450 | 446
2017-04-16 17:30 | 463 | 458
2017-04-16 18:00 | 477 | 471
2017-04-16 18:30 | 479 | 473
2017-04-16 19:00 | 475 | 469
2017-04-16 19:30 | 466 | 461
2017-04-16 20:00 | 466 | 462
2017-04-16 20:30 | 467 | 463
2017-04-16 21:00 | 457 | 453
2017-04-16 21:30 | 455 | 450
2017-04-16 22:00 | 450 | 444
2017-04-16 22:30 | 439 | 433
2017-04-16 23:00 | 428 | 421
2017-04-16 23:30 | 420 | 412
2017-04-17 | 404 | 394
2017-04-17 00:30 | 386 | 374
2017-04-17 01:00 | 378 | 365
2017-04-17 01:30 | 373 | 360
2017-04-17 02:00 | 362 | 347
2017-04-17 02:30 | 366 | 350
2017-04-17 03:00 | 360 | 343
2017-04-17 03:30 | 360 | 344
2017-04-17 04:00 | 358 | 342
2017-04-17 04:30 | 358 | 342
2017-04-17 05:00 | 359 | 343
2017-04-17 05:30 | 365 | 350
2017-04-17 06:00 | 371 | 356
2017-04-17 06:30 | 379 | 364
2017-04-17 07:00 | 394 | 379
2017-04-17 07:30 | 407 | 395
2017-04-17 08:00 | 409 | 398
2017-04-17 08:30 | 418 | 409
2017-04-17 09:00 | 419 | 411
2017-04-17 09:30 | 414 | 408
2017-04-17 10:00 | 414 | 409
2017-04-17 10:30 | 417 | 413
2017-04-17 11:00 | 421 | 417
2017-04-17 11:30 | 425 | 422
2017-04-17 12:00 | 422 | 420
2017-04-17 12:30 | 424 | 421
2017-04-17 13:00 | 434 | 431
2017-04-17 13:30 | 445 | 442
2017-04-17 14:00 | 448 | 445
2017-04-17 14:30 | 452 | 449
2017-04-17 15:00 | 457 | 454
2017-04-17 15:30 | 457 | 454
2017-04-17 16:00 | 470 | 466
2017-04-17 16:30 | 489 | 482
2017-04-17 17:00 | 506 | 493
2017-04-17 17:30 | 514 | 501
2017-04-17 18:00 | 513 | 503
2017-04-17 18:30 | 519 | 505
2017-04-17 19:00 | 523 | 509
2017-04-17 19:30 | 507 | 501
2017-04-17 20:00 | 504 | 497
2017-04-17 20:30 | 505 | 497
2017-04-17 21:00 | 487 | 479
2017-04-17 21:30 | 469 | 463
2017-04-17 22:00 | 465 | 459
2017-04-17 22:30 | 449 | 442
2017-04-17 23:00 | 435 | 427
2017-04-17 23:30 | 422 | 413
2017-04-18 | 405 | 396
2017-04-18 00:30 | 389 | 378
2017-04-18 01:00 | 381 | 369
2017-04-18 01:30 | 373 | 359
2017-04-18 02:00 | 367 | 353
2017-04-18 02:30 | 364 | 350
2017-04-18 03:00 | 366 | 352
2017-04-18 03:30 | 366 | 351
2017-04-18 04:00 | 367 | 353
2017-04-18 04:30 | 371 | 358
2017-04-18 05:00 | 384 | 372
2017-04-18 05:30 | 406 | 397
2017-04-18 06:00 | 437 | 429
2017-04-18 06:30 | 479 | 473
2017-04-18 07:00 | 509 | 499
2017-04-18 07:30 | 535 | 523
2017-04-18 08:00 | 543 | 532
2017-04-18 08:30 | 545 | 535
2017-04-18 09:00 | 547 | 537
2017-04-18 09:30 | 548 | 539
2017-04-18 10:00 | 545 | 537
2017-04-18 10:30 | 543 | 534
2017-04-18 11:00 | 541 | 532
2017-04-18 11:30 | 539 | 531
2017-04-18 12:00 | 537 | 528
2017-04-18 12:30 | 534 | 526
2017-04-18 13:00 | 542 | 534
2017-04-18 13:30 | 550 | 542
2017-04-18 14:00 | 559 | 551
2017-04-18 14:30 | 572 | 562
2017-04-18 15:00 | 580 | 571
2017-04-18 15:30 | 582 | 572
2017-04-18 16:00 | 586 | 575
2017-04-18 16:30 | 594 | 583
2017-04-18 17:00 | 606 | 595
2017-04-18 17:30 | 612 | 600
2017-04-18 18:00 | 620 | 609
2017-04-18 18:30 | 608 | 596
2017-04-18 19:00 | 603 | 590
2017-04-18 19:30 | 583 | 579
2017-04-18 20:00 | 581 | 577
2017-04-18 20:30 | 571 | 568
2017-04-18 21:00 | 552 | 548
2017-04-18 21:30 | 529 | 525
2017-04-18 22:00 | 516 | 512
2017-04-18 22:30 | 487 | 483
2017-04-18 23:00 | 460 | 456
2017-04-18 23:30 | 448 | 442
2017-04-19 | 431 | 423
2017-04-19 00:30 | 408 | 397
2017-04-19 01:00 | 400 | 388
2017-04-19 01:30 | 392 | 380
2017-04-19 02:00 | 391 | 377
2017-04-19 02:30 | 387 | 373
2017-04-19 03:00 | 382 | 368
2017-04-19 03:30 | 385 | 372
2017-04-19 04:00 | 384 | 370
2017-04-19 04:30 | 391 | 377
2017-04-19 05:00 | 404 | 392
2017-04-19 05:30 | 420 | 411
2017-04-19 06:00 | 439 | 434
2017-04-19 06:30 | 475 | 471
2017-04-19 07:00 | 500 | 494
2017-04-19 07:30 | 531 | 528
2017-04-19 08:00 | 541 | 538
2017-04-19 08:30 | 538 | 535
2017-04-19 09:00 | 532 | 530
2017-04-19 09:30 | 527 | 526
2017-04-19 10:00 | 534 | 533
2017-04-19 10:30 | 543 | 541
2017-04-19 11:00 | 545 | 543
2017-04-19 11:30 | 542 | 539
2017-04-19 12:00 | 546 | 544
2017-04-19 12:30 | 536 | 534
2017-04-19 13:00 | 540 | 537
2017-04-19 13:30 | 542 | 540
2017-04-19 14:00 | 546 | 544
2017-04-19 14:30 | 558 | 554
2017-04-19 15:00 | 556 | 552
2017-04-19 15:30 | 561 | 557
2017-04-19 16:00 | 569 | 564
2017-04-19 16:30 | 579 | 574
2017-04-19 17:00 | 588 | 583
2017-04-19 17:30 | 603 | 597
2017-04-19 18:00 | 613 | 609
2017-04-19 18:30 | 606 | 600
2017-04-19 19:00 | 602 | 596
2017-04-19 19:30 | 584 | 579
2017-04-19 20:00 | 575 | 570
2017-04-19 20:30 | 569 | 564
2017-04-19 21:00 | 552 | 548
2017-04-19 21:30 | 525 | 522
2017-04-19 22:00 | 503 | 500
2017-04-19 22:30 | 472 | 468
2017-04-19 23:00 | 452 | 447
2017-04-19 23:30 | 441 | 434
2017-04-20 | 423 | 414
2017-04-20 00:30 | 399 | 389
2017-04-20 01:00 | 390 | 379
2017-04-20 01:30 | 382 | 370
2017-04-20 02:00 | 378 | 363
2017-04-20 02:30 | 375 | 359
2017-04-20 03:00 | 376 | 360
2017-04-20 03:30 | 377 | 361
2017-04-20 04:00 | 376 | 361
2017-04-20 04:30 | 381 | 366
2017-04-20 05:00 | 389 | 375
2017-04-20 05:30 | 407 | 396
2017-04-20 06:00 | 430 | 422
2017-04-20 06:30 | 473 | 464
2017-04-20 07:00 | 496 | 487
2017-04-20 07:30 | 524 | 517
2017-04-20 08:00 | 538 | 532
2017-04-20 08:30 | 537 | 532
2017-04-20 09:00 | 537 | 533
2017-04-20 09:30 | 529 | 525
2017-04-20 10:00 | 523 | 519
2017-04-20 10:30 | 527 | 523
2017-04-20 11:00 | 527 | 523
2017-04-20 11:30 | 526 | 522
2017-04-20 12:00 | 525 | 521
2017-04-20 12:30 | 521 | 517
2017-04-20 13:00 | 525 | 521
2017-04-20 13:30 | 538 | 534
2017-04-20 14:00 | 546 | 542
2017-04-20 14:30 | 559 | 556
2017-04-20 15:00 | 565 | 561
2017-04-20 15:30 | 562 | 557
2017-04-20 16:00 | 577 | 572
2017-04-20 16:30 | 587 | 582
2017-04-20 17:00 | 596 | 591
2017-04-20 17:30 | 609 | 605
2017-04-20 18:00 | 615 | 611
2017-04-20 18:30 | 609 | 604
2017-04-20 19:00 | 603 | 597
2017-04-20 19:30 | 597 | 590
2017-04-20 20:00 | 593 | 587
2017-04-20 20:30 | 585 | 579
2017-04-20 21:00 | 565 | 560
2017-04-20 21:30 | 548 | 542
2017-04-20 22:00 | 527 | 522
2017-04-20 22:30 | 495 | 489
2017-04-20 23:00 | 474 | 468
2017-04-20 23:30 | 461 | 452
2017-04-21 | 443 | 432
2017-04-21 00:30 | 423 | 410
2017-04-21 01:00 | 411 | 397
2017-04-21 01:30 | 408 | 392
2017-04-21 02:00 | 404 | 387
2017-04-21 02:30 | 403 | 386
2017-04-21 03:00 | 404 | 387
2017-04-21 03:30 | 405 | 388
2017-04-21 04:00 | 406 | 388
2017-04-21 04:30 | 413 | 396
2017-04-21 05:00 | 426 | 410
2017-04-21 05:30 | 442 | 428
2017-04-21 06:00 | 456 | 446
2017-04-21 06:30 | 485 | 477
2017-04-21 07:00 | 504 | 498
2017-04-21 07:30 | 535 | 528
2017-04-21 08:00 | 556 | 548
2017-04-21 08:30 | 561 | 554
2017-04-21 09:00 | 547 | 540
2017-04-21 09:30 | 542 | 536
2017-04-21 10:00 | 554 | 549
2017-04-21 10:30 | 557 | 549
2017-04-21 11:00 | 557 | 547
2017-04-21 11:30 | 552 | 541
2017-04-21 12:00 | 542 | 531
2017-04-21 12:30 | 545 | 534
2017-04-21 13:00 | 553 | 543
2017-04-21 13:30 | 566 | 556
2017-04-21 14:00 | 581 | 571
2017-04-21 14:30 | 580 | 569
2017-04-21 15:00 | 577 | 564
2017-04-21 15:30 | 586 | 573
2017-04-21 16:00 | 596 | 583
2017-04-21 16:30 | 595 | 583
2017-04-21 17:00 | 603 | 593
2017-04-21 17:30 | 609 | 599
2017-04-21 18:00 | 618 | 608
2017-04-21 18:30 | 611 | 599
2017-04-21 19:00 | 609 | 596
2017-04-21 19:30 | 595 | 584
2017-04-21 20:00 | 586 | 578
2017-04-21 20:30 | 578 | 570
2017-04-21 21:00 | 554 | 546
2017-04-21 21:30 | 544 | 534
2017-04-21 22:00 | 532 | 520
2017-04-21 22:30 | 502 | 488
2017-04-21 23:00 | 481 | 467
2017-04-21 23:30 | 465 | 455
2017-04-22 | 448 | 435
2017-04-22 00:30 | 429 | 415
2017-04-22 01:00 | 413 | 398
2017-04-22 01:30 | 405 | 388
2017-04-22 02:00 | 401 | 383
2017-04-22 02:30 | 397 | 379
2017-04-22 03:00 | 398 | 379
2017-04-22 03:30 | 400 | 380
2017-04-22 04:00 | 398 | 379
2017-04-22 04:30 | 398 | 379
2017-04-22 05:00 | 396 | 377
2017-04-22 05:30 | 406 | 390
2017-04-22 06:00 | 409 | 394
2017-04-22 06:30 | 425 | 410
2017-04-22 07:00 | 437 | 425
2017-04-22 07:30 | 451 | 440
2017-04-22 08:00 | 463 | 455
2017-04-22 08:30 | 472 | 466
2017-04-22 09:00 | 477 | 469
2017-04-22 09:30 | 481 | 472
2017-04-22 10:00 | 475 | 466
2017-04-22 10:30 | 468 | 460
2017-04-22 11:00 | 462 | 454
2017-04-22 11:30 | 452 | 444
2017-04-22 12:00 | 444 | 436
2017-04-22 12:30 | 436 | 427
2017-04-22 13:00 | 427 | 417
2017-04-22 13:30 | 433 | 423
2017-04-22 14:00 | 434 | 424
2017-04-22 14:30 | 440 | 430
2017-04-22 15:00 | 447 | 437
2017-04-22 15:30 | 458 | 448
2017-04-22 16:00 | 468 | 458
2017-04-22 16:30 | 482 | 473
2017-04-22 17:00 | 499 | 491
2017-04-22 17:30 | 506 | 497
2017-04-22 18:00 | 519 | 512
2017-04-22 18:30 | 516 | 509
2017-04-22 19:00 | 511 | 503
2017-04-22 19:30 | 503 | 495
2017-04-22 20:00 | 501 | 493
2017-04-22 20:30 | 499 | 491
2017-04-22 21:00 | 482 | 473
2017-04-22 21:30 | 468 | 461
2017-04-22 22:00 | 461 | 454
2017-04-22 22:30 | 452 | 445
2017-04-22 23:00 | 441 | 433
2017-04-22 23:30 | 429 | 420
2017-04-23 | 412 | 401
2017-04-23 00:30 | 388 | 375
2017-04-23 01:00 | 376 | 360
2017-04-23 01:30 | 369 | 352
2017-04-23 02:00 | 361 | 344
2017-04-23 02:30 | 350 | 331
2017-04-23 03:00 | 356 | 337
2017-04-23 03:30 | 353 | 333
2017-04-23 04:00 | 350 | 330
2017-04-23 04:30 | 354 | 335
2017-04-23 05:00 | 353 | 334
2017-04-23 05:30 | 360 | 341
2017-04-23 06:00 | 367 | 349
2017-04-23 06:30 | 376 | 357
2017-04-23 07:00 | 382 | 363
2017-04-23 07:30 | 393 | 376
2017-04-23 08:00 | 398 | 384
2017-04-23 08:30 | 407 | 395
2017-04-23 09:00 | 409 | 398
2017-04-23 09:30 | 401 | 392
2017-04-23 10:00 | 398 | 390
2017-04-23 10:30 | 401 | 393
2017-04-23 11:00 | 405 | 398
2017-04-23 11:30 | 402 | 395
2017-04-23 12:00 | 397 | 391
2017-04-23 12:30 | 402 | 396
2017-04-23 13:00 | 407 | 401
2017-04-23 13:30 | 403 | 397
2017-04-23 14:00 | 412 | 406
2017-04-23 14:30 | 416 | 410
2017-04-23 15:00 | 420 | 415
2017-04-23 15:30 | 432 | 426
2017-04-23 16:00 | 445 | 440
2017-04-23 16:30 | 459 | 454
2017-04-23 17:00 | 476 | 470
2017-04-23 17:30 | 492 | 484
2017-04-23 18:00 | 507 | 500
2017-04-23 18:30 | 507 | 497
2017-04-23 19:00 | 494 | 484
2017-04-23 19:30 | 481 | 470
2017-04-23 20:00 | 477 | 466
2017-04-23 20:30 | 479 | 469
2017-04-23 21:00 | 467 | 454
2017-04-23 21:30 | 461 | 451
2017-04-23 22:00 | 456 | 447
2017-04-23 22:30 | 443 | 435
2017-04-23 23:00 | 430 | 421
2017-04-23 23:30 | 420 | 411
2017-04-24 | 410 | 397
2017-04-24 00:30 | 393 | 377
2017-04-24 01:00 | 380 | 363
2017-04-24 01:30 | 371 | 352
2017-04-24 02:00 | 365 | 345
2017-04-24 02:30 | 362 | 342
2017-04-24 03:00 | 360 | 340
2017-04-24 03:30 | 361 | 341
2017-04-24 04:00 | 362 | 342
2017-04-24 04:30 | 371 | 353
2017-04-24 05:00 | 382 | 365
2017-04-24 05:30 | 402 | 388
2017-04-24 06:00 | 422 | 411
2017-04-24 06:30 | 460 | 443
2017-04-24 07:00 | 476 | 458
2017-04-24 07:30 | 503 | 488
2017-04-24 08:00 | 518 | 502
2017-04-24 08:30 | 513 | 498
2017-04-24 09:00 | 502 | 488
2017-04-24 09:30 | 501 | 489
2017-04-24 10:00 | 500 | 485
2017-04-24 10:30 | 501 | 488
2017-04-24 11:00 | 503 | 491
2017-04-24 11:30 | 504 | 492
2017-04-24 12:00 | 509 | 497
2017-04-24 12:30 | 509 | 497
2017-04-24 13:00 | 510 | 499
2017-04-24 13:30 | 519 | 508
2017-04-24 14:00 | 522 | 511
2017-04-24 14:30 | 534 | 523
2017-04-24 15:00 | 533 | 522
2017-04-24 15:30 | 531 | 518
2017-04-24 16:00 | 539 | 526
2017-04-24 16:30 | 549 | 537
2017-04-24 17:00 | 562 | 547
2017-04-24 17:30 | 570 | 552
2017-04-24 18:00 | 588 | 572
2017-04-24 18:30 | 579 | 561
2017-04-24 19:00 | 561 | 545
2017-04-24 19:30 | 552 | 534
2017-04-24 20:00 | 545 | 528
2017-04-24 20:30 | 533 | 523
2017-04-24 21:00 | 517 | 510
2017-04-24 21:30 | 502 | 495
2017-04-24 22:00 | 497 | 491
2017-04-24 22:30 | 461 | 454
2017-04-24 23:00 | 443 | 436
2017-04-24 23:30 | 428 | 420
2017-04-25 | 409 | 398
2017-04-25 00:30 | 389 | 376
2017-04-25 01:00 | 381 | 366
2017-04-25 01:30 | 379 | 363
2017-04-25 02:00 | 368 | 350
2017-04-25 02:30 | 363 | 344
2017-04-25 03:00 | 371 | 352
2017-04-25 03:30 | 369 | 350
2017-04-25 04:00 | 367 | 349
2017-04-25 04:30 | 361 | 343
2017-04-25 05:00 | 369 | 350
2017-04-25 05:30 | 373 | 356
2017-04-25 06:00 | 377 | 360
2017-04-25 06:30 | 379 | 362
2017-04-25 07:00 | 390 | 373
2017-04-25 07:30 | 398 | 384
2017-04-25 08:00 | 410 | 397
2017-04-25 08:30 | 411 | 399
2017-04-25 09:00 | 413 | 403
2017-04-25 09:30 | 424 | 416
2017-04-25 10:00 | 426 | 418
2017-04-25 10:30 | 427 | 419
2017-04-25 11:00 | 410 | 402
2017-04-25 11:30 | 409 | 401
2017-04-25 12:00 | 405 | 398
2017-04-25 12:30 | 410 | 403
2017-04-25 13:00 | 412 | 406
2017-04-25 13:30 | 415 | 408
2017-04-25 14:00 | 408 | 402
2017-04-25 14:30 | 419 | 413
2017-04-25 15:00 | 427 | 421
2017-04-25 15:30 | 436 | 431
2017-04-25 16:00 | 447 | 442
2017-04-25 16:30 | 460 | 456
2017-04-25 17:00 | 485 | 482
2017-04-25 17:30 | 495 | 491
2017-04-25 18:00 | 512 | 508
2017-04-25 18:30 | 517 | 511
2017-04-25 19:00 | 513 | 506
2017-04-25 19:30 | 498 | 492
2017-04-25 20:00 | 485 | 481
2017-04-25 20:30 | 486 | 482
2017-04-25 21:00 | 474 | 470
2017-04-25 21:30 | 462 | 456
2017-04-25 22:00 | 453 | 448
2017-04-25 22:30 | 437 | 431
2017-04-25 23:00 | 414 | 408
2017-04-25 23:30 | 399 | 392
2017-04-26 | 385 | 375
2017-04-26 00:30 | 370 | 357
2017-04-26 01:00 | 367 | 352
2017-04-26 01:30 | 359 | 344
2017-04-26 02:00 | 345 | 330
2017-04-26 02:30 | 349 | 333
2017-04-26 03:00 | 357 | 339
2017-04-26 03:30 | 359 | 341
2017-04-26 04:00 | 359 | 342
2017-04-26 04:30 | 365 | 349
2017-04-26 05:00 | 374 | 359
2017-04-26 05:30 | 388 | 377
2017-04-26 06:00 | 410 | 402
2017-04-26 06:30 | 449 | 445
2017-04-26 07:00 | 482 | 480
2017-04-26 07:30 | 516 | 514
2017-04-26 08:00 | 542 | 539
2017-04-26 08:30 | 554 | 551
2017-04-26 09:00 | 558 | 556
2017-04-26 09:30 | 565 | 563
2017-04-26 10:00 | 558 | 557
2017-04-26 10:30 | 551 | 549
2017-04-26 11:00 | 560 | 559
2017-04-26 11:30 | 568 | 567
2017-04-26 12:00 | 566 | 565
2017-04-26 12:30 | 565 | 564
2017-04-26 13:00 | 554 | 553
2017-04-26 13:30 | 555 | 554
2017-04-26 14:00 | 556 | 554
2017-04-26 14:30 | 564 | 562
2017-04-26 15:00 | 558 | 556
2017-04-26 15:30 | 542 | 540
2017-04-26 16:00 | 539 | 537
2017-04-26 16:30 | 558 | 556
2017-04-26 17:00 | 582 | 580
2017-04-26 17:30 | 605 | 604
2017-04-26 18:00 | 611 | 609
2017-04-26 18:30 | 600 | 597
2017-04-26 19:00 | 594 | 591
2017-04-26 19:30 | 579 | 575
2017-04-26 20:00 | 571 | 569
2017-04-26 20:30 | 569 | 567
2017-04-26 21:00 | 547 | 544
2017-04-26 21:30 | 525 | 522
2017-04-26 22:00 | 510 | 506
2017-04-26 22:30 | 473 | 467
2017-04-26 23:00 | 450 | 443
2017-04-26 23:30 | 439 | 429
2017-04-27 | 420 | 410
2017-04-27 00:30 | 403 | 393
2017-04-27 01:00 | 391 | 380
2017-04-27 01:30 | 381 | 368
2017-04-27 02:00 | 378 | 365
2017-04-27 02:30 | 385 | 371
2017-04-27 03:00 | 388 | 374
2017-04-27 03:30 | 386 | 371
2017-04-27 04:00 | 385 | 370
2017-04-27 04:30 | 394 | 382
2017-04-27 05:00 | 405 | 394
2017-04-27 05:30 | 427 | 417
2017-04-27 06:00 | 440 | 434
2017-04-27 06:30 | 468 | 464
2017-04-27 07:00 | 498 | 496
2017-04-27 07:30 | 529 | 527
2017-04-27 08:00 | 530 | 527
2017-04-27 08:30 | 519 | 516
2017-04-27 09:00 | 501 | 498
2017-04-27 09:30 | 493 | 489
2017-04-27 10:00 | 490 | 486
2017-04-27 10:30 | 485 | 481
2017-04-27 11:00 | 482 | 478
2017-04-27 11:30 | 472 | 468
2017-04-27 12:00 | 472 | 468
2017-04-27 12:30 | 474 | 470
2017-04-27 13:00 | 470 | 466
2017-04-27 13:30 | 483 | 478
2017-04-27 14:00 | 490 | 485
2017-04-27 14:30 | 496 | 493
2017-04-27 15:00 | 503 | 499
2017-04-27 15:30 | 511 | 508
2017-04-27 16:00 | 526 | 523
2017-04-27 16:30 | 547 | 544
2017-04-27 17:00 | 564 | 561
2017-04-27 17:30 | 579 | 576
2017-04-27 18:00 | 603 | 601
2017-04-27 18:30 | 610 | 607
2017-04-27 19:00 | 597 | 594
2017-04-27 19:30 | 584 | 580
2017-04-27 20:00 | 581 | 577
2017-04-27 20:30 | 572 | 569
2017-04-27 21:00 | 546 | 543
2017-04-27 21:30 | 524 | 520
2017-04-27 22:00 | 506 | 501
2017-04-27 22:30 | 480 | 473
2017-04-27 23:00 | 462 | 453
2017-04-27 23:30 | 448 | 438
2017-04-28 | 419 | 410
2017-04-28 00:30 | 388 | 376
2017-04-28 01:00 | 371 | 356
2017-04-28 01:30 | 369 | 353
2017-04-28 02:00 | 369 | 352
2017-04-28 02:30 | 375 | 357
2017-04-28 03:00 | 381 | 362
2017-04-28 03:30 | 384 | 365
2017-04-28 04:00 | 385 | 367
2017-04-28 04:30 | 394 | 377
2017-04-28 05:00 | 406 | 390
2017-04-28 05:30 | 417 | 404
2017-04-28 06:00 | 432 | 422
2017-04-28 06:30 | 455 | 449
2017-04-28 07:00 | 477 | 474
2017-04-28 07:30 | 529 | 523
2017-04-28 08:00 | 542 | 536
2017-04-28 08:30 | 529 | 525
2017-04-28 09:00 | 503 | 498
2017-04-28 09:30 | 490 | 486
2017-04-28 10:00 | 481 | 477
2017-04-28 10:30 | 478 | 474
2017-04-28 11:00 | 473 | 470
2017-04-28 11:30 | 463 | 460
2017-04-28 12:00 | 465 | 462
2017-04-28 12:30 | 474 | 471
2017-04-28 13:00 | 485 | 483
2017-04-28 13:30 | 500 | 498
2017-04-28 14:00 | 505 | 503
2017-04-28 14:30 | 503 | 500
2017-04-28 15:00 | 510 | 508
2017-04-28 15:30 | 523 | 521
2017-04-28 16:00 | 530 | 527
2017-04-28 16:30 | 546 | 542
2017-04-28 17:00 | 551 | 545
2017-04-28 17:30 | 561 | 555
2017-04-28 18:00 | 575 | 568
2017-04-28 18:30 | 569 | 559
2017-04-28 19:00 | 560 | 549
2017-04-28 19:30 | 543 | 532
2017-04-28 20:00 | 534 | 526
2017-04-28 20:30 | 528 | 522
2017-04-28 21:00 | 520 | 514
2017-04-28 21:30 | 502 | 494
2017-04-28 22:00 | 500 | 492
2017-04-28 22:30 | 481 | 474
2017-04-28 23:00 | 453 | 447
2017-04-28 23:30 | 438 | 431
2017-04-29 | 422 | 412
2017-04-29 00:30 | 402 | 390
2017-04-29 01:00 | 396 | 381
2017-04-29 01:30 | 387 | 371
2017-04-29 02:00 | 380 | 363
2017-04-29 02:30 | 378 | 361
2017-04-29 03:00 | 376 | 359
2017-04-29 03:30 | 371 | 354
2017-04-29 04:00 | 373 | 356
2017-04-29 04:30 | 373 | 355
2017-04-29 05:00 | 373 | 356
2017-04-29 05:30 | 378 | 362
2017-04-29 06:00 | 387 | 373
2017-04-29 06:30 | 404 | 390
2017-04-29 07:00 | 415 | 402
2017-04-29 07:30 | 426 | 414
2017-04-29 08:00 | 421 | 410
2017-04-29 08:30 | 435 | 426
2017-04-29 09:00 | 430 | 422
2017-04-29 09:30 | 420 | 412
2017-04-29 10:00 | 417 | 409
2017-04-29 10:30 | 413 | 406
2017-04-29 11:00 | 405 | 397
2017-04-29 11:30 | 399 | 391
2017-04-29 12:00 | 394 | 386
2017-04-29 12:30 | 394 | 386
2017-04-29 13:00 | 395 | 387
2017-04-29 13:30 | 393 | 386
2017-04-29 14:00 | 396 | 390
2017-04-29 14:30 | 409 | 402
2017-04-29 15:00 | 417 | 411
2017-04-29 15:30 | 421 | 415
2017-04-29 16:00 | 425 | 420
2017-04-29 16:30 | 437 | 432
2017-04-29 17:00 | 453 | 449
2017-04-29 17:30 | 466 | 461
2017-04-29 18:00 | 484 | 480
2017-04-29 18:30 | 482 | 476
2017-04-29 19:00 | 482 | 476
2017-04-29 19:30 | 478 | 472
2017-04-29 20:00 | 478 | 473
2017-04-29 20:30 | 471 | 466
2017-04-29 21:00 | 456 | 450
2017-04-29 21:30 | 444 | 438
2017-04-29 22:00 | 437 | 430
2017-04-29 22:30 | 428 | 420
2017-04-29 23:00 | 416 | 408
2017-04-29 23:30 | 409 | 399
2017-04-30 | 395 | 383
2017-04-30 00:30 | 376 | 361
2017-04-30 01:00 | 367 | 350
2017-04-30 01:30 | 359 | 341
2017-04-30 02:00 | 353 | 334
2017-04-30 02:30 | 348 | 329
2017-04-30 03:00 | 345 | 325
2017-04-30 03:30 | 344 | 323
2017-04-30 04:00 | 345 | 325
2017-04-30 04:30 | 342 | 320
2017-04-30 05:00 | 344 | 321
2017-04-30 05:30 | 347 | 325
2017-04-30 06:00 | 355 | 333
2017-04-30 06:30 | 363 | 342
2017-04-30 07:00 | 369 | 346
2017-04-30 07:30 | 378 | 357
2017-04-30 08:00 | 381 | 362
2017-04-30 08:30 | 385 | 367
2017-04-30 09:00 | 384 | 366
2017-04-30 09:30 | 387 | 372
2017-04-30 10:00 | 387 | 374
2017-04-30 10:30 | 383 | 370
2017-04-30 11:00 | 377 | 365
2017-04-30 11:30 | 378 | 365
2017-04-30 12:00 | 376 | 364
2017-04-30 12:30 | 371 | 363
2017-04-30 13:00 | 371 | 364
2017-04-30 13:30 | 373 | 366
2017-04-30 14:00 | 372 | 365
2017-04-30 14:30 | 377 | 370
2017-04-30 15:00 | 381 | 375
2017-04-30 15:30 | 393 | 387
2017-04-30 16:00 | 408 | 402
2017-04-30 16:30 | 426 | 421
2017-04-30 17:00 | 437 | 433
2017-04-30 17:30 | 445 | 443
2017-04-30 18:00 | 457 | 455
2017-04-30 18:30 | 456 | 453
2017-04-30 19:00 | 450 | 447
2017-04-30 19:30 | 445 | 441
2017-04-30 20:00 | 447 | 443
2017-04-30 20:30 | 449 | 445
2017-04-30 21:00 | 437 | 435
2017-04-30 21:30 | 431 | 428
2017-04-30 22:00 | 428 | 425
2017-04-30 22:30 | 417 | 414
2017-04-30 23:00 | 410 | 406
2017-04-30 23:30 | 396 | 392
2017-05-01 | 378 | 372
2017-05-01 00:30 | 359 | 349
2017-05-01 01:00 | 343 | 331
2017-05-01 01:30 | 332 | 319
2017-05-01 02:00 | 329 | 315
2017-05-01 02:30 | 326 | 311
2017-05-01 03:00 | 322 | 307
2017-05-01 03:30 | 321 | 306
2017-05-01 04:00 | 316 | 301
2017-05-01 04:30 | 303 | 286
2017-05-01 05:00 | 314 | 298
2017-05-01 05:30 | 323 | 308
2017-05-01 06:00 | 324 | 311
2017-05-01 06:30 | 345 | 332
2017-05-01 07:00 | 355 | 342
2017-05-01 07:30 | 363 | 352
2017-05-01 08:00 | 365 | 354
2017-05-01 08:30 | 370 | 362
2017-05-01 09:00 | 373 | 365
2017-05-01 09:30 | 376 | 369
2017-05-01 10:00 | 374 | 368
2017-05-01 10:30 | 365 | 359
2017-05-01 11:00 | 363 | 357
2017-05-01 11:30 | 359 | 353
2017-05-01 12:00 | 354 | 349
2017-05-01 12:30 | 362 | 357
2017-05-01 13:00 | 365 | 360
2017-05-01 13:30 | 368 | 364
2017-05-01 14:00 | 378 | 373
2017-05-01 14:30 | 378 | 373
2017-05-01 15:00 | 389 | 385
2017-05-01 15:30 | 400 | 397
2017-05-01 16:00 | 417 | 413
2017-05-01 16:30 | 435 | 432
2017-05-01 17:00 | 452 | 450
2017-05-01 17:30 | 472 | 470
2017-05-01 18:00 | 487 | 486
2017-05-01 18:30 | 487 | 485
2017-05-01 19:00 | 490 | 488
2017-05-01 19:30 | 477 | 475
2017-05-01 20:00 | 472 | 469
2017-05-01 20:30 | 468 | 464
2017-05-01 21:00 | 435 | 433
2017-05-01 21:30 | 428 | 426
2017-05-01 22:00 | 424 | 422
2017-05-01 22:30 | 411 | 408
2017-05-01 23:00 | 402 | 399
2017-05-01 23:30 | 395 | 391
2017-05-02 | 380 | 374
2017-05-02 00:30 | 355 | 347
2017-05-02 01:00 | 342 | 331
2017-05-02 01:30 | 332 | 321
2017-05-02 02:00 | 330 | 317
2017-05-02 02:30 | 328 | 316
2017-05-02 03:00 | 328 | 314
2017-05-02 03:30 | 329 | 316
2017-05-02 04:00 | 332 | 319
2017-05-02 04:30 | 344 | 332
2017-05-02 05:00 | 351 | 341
2017-05-02 05:30 | 375 | 367
2017-05-02 06:00 | 397 | 392
2017-05-02 06:30 | 427 | 424
2017-05-02 07:00 | 464 | 460
2017-05-02 07:30 | 496 | 490
2017-05-02 08:00 | 500 | 495
2017-05-02 08:30 | 484 | 479
2017-05-02 09:00 | 475 | 470
2017-05-02 09:30 | 473 | 466
2017-05-02 10:00 | 466 | 460
2017-05-02 10:30 | 464 | 459
2017-05-02 11:00 | 463 | 459
2017-05-02 11:30 | 469 | 465
2017-05-02 12:00 | 466 | 463
2017-05-02 12:30 | 475 | 472
2017-05-02 13:00 | 484 | 482
2017-05-02 13:30 | 497 | 495
2017-05-02 14:00 | 498 | 496
2017-05-02 14:30 | 502 | 501
2017-05-02 15:00 | 512 | 510
2017-05-02 15:30 | 524 | 522
2017-05-02 16:00 | 535 | 534
2017-05-02 16:30 | 550 | 548
2017-05-02 17:00 | 559 | 557
2017-05-02 17:30 | 574 | 573
2017-05-02 18:00 | 589 | 586
2017-05-02 18:30 | 570 | 566
2017-05-02 19:00 | 566 | 561
2017-05-02 19:30 | 545 | 541
2017-05-02 20:00 | 547 | 543
2017-05-02 20:30 | 534 | 533
2017-05-02 21:00 | 506 | 505
2017-05-02 21:30 | 489 | 489
2017-05-02 22:00 | 486 | 485
2017-05-02 22:30 | 461 | 460
2017-05-02 23:00 | 450 | 449
2017-05-02 23:30 | 437 | 435
2017-05-03 | 412 | 410
2017-05-03 00:30 | 386 | 382
2017-05-03 01:00 | 373 | 366
2017-05-03 01:30 | 364 | 356
2017-05-03 02:00 | 358 | 350
2017-05-03 02:30 | 355 | 346
2017-05-03 03:00 | 354 | 345
2017-05-03 03:30 | 355 | 345
2017-05-03 04:00 | 355 | 346
2017-05-03 04:30 | 355 | 347
2017-05-03 05:00 | 363 | 355
2017-05-03 05:30 | 380 | 375
2017-05-03 06:00 | 403 | 399
2017-05-03 06:30 | 435 | 432
2017-05-03 07:00 | 466 | 464
2017-05-03 07:30 | 486 | 485
2017-05-03 08:00 | 494 | 492
2017-05-03 08:30 | 485 | 483
2017-05-03 09:00 | 485 | 484
2017-05-03 09:30 | 487 | 486
2017-05-03 10:00 | 480 | 479
2017-05-03 10:30 | 474 | 472
2017-05-03 11:00 | 479 | 478
2017-05-03 11:30 | 485 | 485
2017-05-03 12:00 | 489 | 488
2017-05-03 12:30 | 492 | 491
2017-05-03 13:00 | 499 | 497
2017-05-03 13:30 | 510 | 508
2017-05-03 14:00 | 522 | 521
2017-05-03 14:30 | 534 | 533
2017-05-03 15:00 | 533 | 532
2017-05-03 15:30 | 531 | 530
2017-05-03 16:00 | 542 | 541
2017-05-03 16:30 | 557 | 555
2017-05-03 17:00 | 567 | 565
2017-05-03 17:30 | 570 | 569
2017-05-03 18:00 | 588 | 586
2017-05-03 18:30 | 577 | 575
2017-05-03 19:00 | 570 | 569
2017-05-03 19:30 | 559 | 557
2017-05-03 20:00 | 554 | 552
2017-05-03 20:30 | 551 | 550
2017-05-03 21:00 | 530 | 529
2017-05-03 21:30 | 504 | 503
2017-05-03 22:00 | 489 | 488
2017-05-03 22:30 | 469 | 467
2017-05-03 23:00 | 458 | 457
2017-05-03 23:30 | 441 | 439
2017-05-04 | 418 | 416
2017-05-04 00:30 | 399 | 395
2017-05-04 01:00 | 384 | 379
2017-05-04 01:30 | 371 | 366
2017-05-04 02:00 | 375 | 370
2017-05-04 02:30 | 368 | 363
2017-05-04 03:00 | 363 | 357
2017-05-04 03:30 | 361 | 355
2017-05-04 04:00 | 362 | 356
2017-05-04 04:30 | 362 | 356
2017-05-04 05:00 | 369 | 365
2017-05-04 05:30 | 387 | 383
2017-05-04 06:00 | 402 | 400
2017-05-04 06:30 | 448 | 447
2017-05-04 07:00 | 488 | 488
2017-05-04 07:30 | 517 | 517
2017-05-04 08:00 | 520 | 520
2017-05-04 08:30 | 511 | 511
2017-05-04 09:00 | 499 | 499
2017-05-04 09:30 | 497 | 497
2017-05-04 10:00 | 503 | 503
2017-05-04 10:30 | 506 | 506
2017-05-04 11:00 | 502 | 502
2017-05-04 11:30 | 508 | 508
2017-05-04 12:00 | 517 | 516
2017-05-04 12:30 | 519 | 519
2017-05-04 13:00 | 512 | 512
2017-05-04 13:30 | 502 | 502
2017-05-04 14:00 | 495 | 495
2017-05-04 14:30 | 504 | 504
2017-05-04 15:00 | 508 | 508
2017-05-04 15:30 | 514 | 514
2017-05-04 16:00 | 527 | 527
2017-05-04 16:30 | 536 | 536
2017-05-04 17:00 | 551 | 551
2017-05-04 17:30 | 569 | 568
2017-05-04 18:00 | 589 | 588
2017-05-04 18:30 | 591 | 590
2017-05-04 19:00 | 580 | 579
2017-05-04 19:30 | 561 | 560
2017-05-04 20:00 | 555 | 553
2017-05-04 20:30 | 554 | 552
2017-05-04 21:00 | 534 | 531
2017-05-04 21:30 | 512 | 509
2017-05-04 22:00 | 493 | 490
2017-05-04 22:30 | 478 | 475
2017-05-04 23:00 | 456 | 454
2017-05-04 23:30 | 438 | 435
2017-05-05 | 414 | 410
2017-05-05 00:30 | 385 | 380
2017-05-05 01:00 | 363 | 355
2017-05-05 01:30 | 351 | 343
2017-05-05 02:00 | 348 | 339
2017-05-05 02:30 | 342 | 332
2017-05-05 03:00 | 344 | 334
2017-05-05 03:30 | 342 | 333
2017-05-05 04:00 | 344 | 334
2017-05-05 04:30 | 352 | 343
2017-05-05 05:00 | 356 | 348
2017-05-05 05:30 | 378 | 372
2017-05-05 06:00 | 395 | 391
2017-05-05 06:30 | 434 | 432
2017-05-05 07:00 | 465 | 464
2017-05-05 07:30 | 496 | 496
2017-05-05 08:00 | 501 | 500
2017-05-05 08:30 | 484 | 483
2017-05-05 09:00 | 466 | 465
2017-05-05 09:30 | 462 | 462
2017-05-05 10:00 | 450 | 449
2017-05-05 10:30 | 446 | 445
2017-05-05 11:00 | 447 | 447
2017-05-05 11:30 | 442 | 442
2017-05-05 12:00 | 447 | 447
2017-05-05 12:30 | 454 | 453
2017-05-05 13:00 | 456 | 456
2017-05-05 13:30 | 458 | 458
2017-05-05 14:00 | 467 | 467
2017-05-05 14:30 | 478 | 478
2017-05-05 15:00 | 484 | 483
2017-05-05 15:30 | 483 | 483
2017-05-05 16:00 | 497 | 497
2017-05-05 16:30 | 514 | 513
2017-05-05 17:00 | 534 | 533
2017-05-05 17:30 | 549 | 547
2017-05-05 18:00 | 560 | 559
2017-05-05 18:30 | 549 | 548
2017-05-05 19:00 | 539 | 538
2017-05-05 19:30 | 528 | 526
2017-05-05 20:00 | 527 | 525
2017-05-05 20:30 | 519 | 517
2017-05-05 21:00 | 500 | 499
2017-05-05 21:30 | 486 | 485
2017-05-05 22:00 | 480 | 479
2017-05-05 22:30 | 453 | 452
2017-05-05 23:00 | 428 | 427
2017-05-05 23:30 | 414 | 413
2017-05-06 | 390 | 387
2017-05-06 00:30 | 367 | 363
2017-05-06 01:00 | 361 | 356
2017-05-06 01:30 | 351 | 345
2017-05-06 02:00 | 346 | 339
2017-05-06 02:30 | 340 | 333
2017-05-06 03:00 | 341 | 333
2017-05-06 03:30 | 336 | 329
2017-05-06 04:00 | 330 | 322
2017-05-06 04:30 | 326 | 318
2017-05-06 05:00 | 329 | 321
2017-05-06 05:30 | 343 | 336
2017-05-06 06:00 | 352 | 346
2017-05-06 06:30 | 370 | 365
2017-05-06 07:00 | 383 | 378
2017-05-06 07:30 | 405 | 401
2017-05-06 08:00 | 415 | 412
2017-05-06 08:30 | 416 | 414
2017-05-06 09:00 | 421 | 419
2017-05-06 09:30 | 414 | 413
2017-05-06 10:00 | 407 | 406
2017-05-06 10:30 | 399 | 398
2017-05-06 11:00 | 393 | 393
2017-05-06 11:30 | 394 | 393
2017-05-06 12:00 | 391 | 390
2017-05-06 12:30 | 383 | 382
2017-05-06 13:00 | 385 | 384
2017-05-06 13:30 | 392 | 391
2017-05-06 14:00 | 396 | 395
2017-05-06 14:30 | 400 | 399
2017-05-06 15:00 | 402 | 401
2017-05-06 15:30 | 410 | 409
2017-05-06 16:00 | 415 | 414
2017-05-06 16:30 | 434 | 433
2017-05-06 17:00 | 449 | 448
2017-05-06 17:30 | 466 | 466
2017-05-06 18:00 | 492 | 490
2017-05-06 18:30 | 483 | 479
2017-05-06 19:00 | 475 | 471
2017-05-06 19:30 | 467 | 462
2017-05-06 20:00 | 467 | 462
2017-05-06 20:30 | 460 | 457
2017-05-06 21:00 | 437 | 435
2017-05-06 21:30 | 439 | 437
2017-05-06 22:00 | 424 | 423
2017-05-06 22:30 | 420 | 418
2017-05-06 23:00 | 407 | 405
2017-05-06 23:30 | 398 | 395
2017-05-07 | 376 | 372
2017-05-07 00:30 | 357 | 352
2017-05-07 01:00 | 352 | 346
2017-05-07 01:30 | 343 | 335
2017-05-07 02:00 | 335 | 326
2017-05-07 02:30 | 334 | 324
2017-05-07 03:00 | 339 | 329
2017-05-07 03:30 | 344 | 333
2017-05-07 04:00 | 337 | 326
2017-05-07 04:30 | 343 | 332
2017-05-07 05:00 | 344 | 334
2017-05-07 05:30 | 346 | 336
2017-05-07 06:00 | 353 | 344
2017-05-07 06:30 | 362 | 353
2017-05-07 07:00 | 369 | 360
2017-05-07 07:30 | 388 | 380
2017-05-07 08:00 | 399 | 392
2017-05-07 08:30 | 402 | 396
2017-05-07 09:00 | 400 | 394
2017-05-07 09:30 | 392 | 388
2017-05-07 10:00 | 382 | 379
2017-05-07 10:30 | 375 | 373
2017-05-07 11:00 | 369 | 366
2017-05-07 11:30 | 366 | 364
2017-05-07 12:00 | 371 | 369
2017-05-07 12:30 | 377 | 375
2017-05-07 13:00 | 377 | 375
2017-05-07 13:30 | 382 | 380
2017-05-07 14:00 | 386 | 384
2017-05-07 14:30 | 384 | 383
2017-05-07 15:00 | 389 | 388
2017-05-07 15:30 | 404 | 403
2017-05-07 16:00 | 418 | 417
2017-05-07 16:30 | 439 | 438
2017-05-07 17:00 | 454 | 454
2017-05-07 17:30 | 465 | 464
2017-05-07 18:00 | 491 | 487
2017-05-07 18:30 | 498 | 491
2017-05-07 19:00 | 488 | 481
2017-05-07 19:30 | 478 | 469
2017-05-07 20:00 | 466 | 461
2017-05-07 20:30 | 461 | 461
2017-05-07 21:00 | 443 | 442
2017-05-07 21:30 | 433 | 432
2017-05-07 22:00 | 432 | 430
2017-05-07 22:30 | 415 | 414
2017-05-07 23:00 | 398 | 396
2017-05-07 23:30 | 387 | 385
2017-05-08 | 368 | 364
2017-05-08 00:30 | 349 | 343
2017-05-08 01:00 | 345 | 338
2017-05-08 01:30 | 344 | 336
2017-05-08 02:00 | 342 | 333
2017-05-08 02:30 | 340 | 331
2017-05-08 03:00 | 339 | 330
2017-05-08 03:30 | 332 | 322
2017-05-08 04:00 | 328 | 319
2017-05-08 04:30 | 347 | 338
2017-05-08 05:00 | 356 | 349
2017-05-08 05:30 | 373 | 368
2017-05-08 06:00 | 397 | 394
2017-05-08 06:30 | 443 | 441
2017-05-08 07:00 | 479 | 478
2017-05-08 07:30 | 513 | 512
2017-05-08 08:00 | 524 | 523
2017-05-08 08:30 | 525 | 523
2017-05-08 09:00 | 383 | 383
2017-05-08 09:30 | 368 | 368
2017-05-08 10:00 | 499 | 499
2017-05-08 10:30 | 454 | 454
2017-05-08 11:00 | 402 | 401
2017-05-08 11:30 | 568 | 568
2017-05-08 12:00 | 507 | 507
2017-05-08 12:30 | 510 | 510
2017-05-08 13:00 | 516 | 516
2017-05-08 13:30 | 513 | 513
2017-05-08 14:00 | 509 | 508
2017-05-08 14:30 | 517 | 517
2017-05-08 15:00 | 527 | 527
2017-05-08 15:30 | 528 | 528
2017-05-08 16:00 | 533 | 532
2017-05-08 16:30 | 540 | 539
2017-05-08 17:00 | 554 | 553
2017-05-08 17:30 | 579 | 579
2017-05-08 18:00 | 589 | 587
2017-05-08 18:30 | 578 | 576
2017-05-08 19:00 | 572 | 569
2017-05-08 19:30 | 555 | 552
2017-05-08 20:00 | 547 | 545
2017-05-08 20:30 | 541 | 540
2017-05-08 21:00 | 520 | 520
2017-05-08 21:30 | 505 | 504
2017-05-08 22:00 | 480 | 478
2017-05-08 22:30 | 455 | 454
2017-05-08 23:00 | 437 | 436
2017-05-08 23:30 | 419 | 417
2017-05-09 | 396 | 393
2017-05-09 00:30 | 373 | 369
2017-05-09 01:00 | 360 | 356
2017-05-09 01:30 | 351 | 345
2017-05-09 02:00 | 341 | 334
2017-05-09 02:30 | 341 | 334
2017-05-09 03:00 | 339 | 333
2017-05-09 03:30 | 341 | 334
2017-05-09 04:00 | 342 | 335
2017-05-09 04:30 | 346 | 339
2017-05-09 05:00 | 359 | 353
2017-05-09 05:30 | 380 | 377
2017-05-09 06:00 | 405 | 403
2017-05-09 06:30 | 446 | 445
2017-05-09 07:00 | 491 | 490
2017-05-09 07:30 | 529 | 527
2017-05-09 08:00 | 550 | 545
2017-05-09 08:30 | 547 | 539
2017-05-09 09:00 | 524 | 517
2017-05-09 09:30 | 503 | 502
2017-05-09 10:00 | 502 | 502
2017-05-09 10:30 | 502 | 502
2017-05-09 11:00 | 498 | 497
2017-05-09 11:30 | 489 | 488
2017-05-09 12:00 | 479 | 478
2017-05-09 12:30 | 474 | 474
2017-05-09 13:00 | 475 | 475
2017-05-09 13:30 | 482 | 481
2017-05-09 14:00 | 479 | 479
2017-05-09 14:30 | 488 | 487
2017-05-09 15:00 | 493 | 493
2017-05-09 15:30 | 494 | 493
2017-05-09 16:00 | 505 | 504
2017-05-09 16:30 | 521 | 520
2017-05-09 17:00 | 530 | 529
2017-05-09 17:30 | 558 | 557
2017-05-09 18:00 | 581 | 579
2017-05-09 18:30 | 564 | 561
2017-05-09 19:00 | 556 | 554
2017-05-09 19:30 | 540 | 538
2017-05-09 20:00 | 535 | 534
2017-05-09 20:30 | 530 | 530
2017-05-09 21:00 | 511 | 511
2017-05-09 21:30 | 490 | 490
2017-05-09 22:00 | 473 | 471
2017-05-09 22:30 | 457 | 455
2017-05-09 23:00 | 435 | 433
2017-05-09 23:30 | 409 | 407
2017-05-10 | 385 | 381
2017-05-10 00:30 | 359 | 355
2017-05-10 01:00 | 358 | 353
2017-05-10 01:30 | 352 | 346
2017-05-10 02:00 | 345 | 338
2017-05-10 02:30 | 345 | 338
2017-05-10 03:00 | 346 | 339
2017-05-10 03:30 | 345 | 338
2017-05-10 04:00 | 349 | 341
2017-05-10 04:30 | 353 | 346
2017-05-10 05:00 | 363 | 358
2017-05-10 05:30 | 381 | 377
2017-05-10 06:00 | 406 | 404
2017-05-10 06:30 | 457 | 455
2017-05-10 07:00 | 500 | 498
2017-05-10 07:30 | 527 | 526
2017-05-10 08:00 | 545 | 544
2017-05-10 08:30 | 542 | 540
2017-05-10 09:00 | 532 | 530
2017-05-10 09:30 | 532 | 531
2017-05-10 10:00 | 534 | 533
2017-05-10 10:30 | 533 | 532
2017-05-10 11:00 | 538 | 537
2017-05-10 11:30 | 538 | 537
2017-05-10 12:00 | 533 | 532
2017-05-10 12:30 | 530 | 528
2017-05-10 13:00 | 521 | 520
2017-05-10 13:30 | 526 | 524
2017-05-10 14:00 | 529 | 528
2017-05-10 14:30 | 537 | 535
2017-05-10 15:00 | 533 | 531
2017-05-10 15:30 | 537 | 535
2017-05-10 16:00 | 546 | 544
2017-05-10 16:30 | 553 | 551
2017-05-10 17:00 | 570 | 568
2017-05-10 17:30 | 602 | 599
2017-05-10 18:00 | 612 | 608
2017-05-10 18:30 | 601 | 595
2017-05-10 19:00 | 595 | 589
2017-05-10 19:30 | 579 | 575
2017-05-10 20:00 | 571 | 567
2017-05-10 20:30 | 564 | 560
2017-05-10 21:00 | 543 | 538
2017-05-10 21:30 | 527 | 522
2017-05-10 22:00 | 510 | 504
2017-05-10 22:30 | 479 | 477
2017-05-10 23:00 | 451 | 449
2017-05-10 23:30 | 433 | 429
2017-05-11 | 403 | 400
2017-05-11 00:30 | 381 | 376
2017-05-11 01:00 | 370 | 364
2017-05-11 01:30 | 365 | 359
2017-05-11 02:00 | 359 | 352
2017-05-11 02:30 | 354 | 346
2017-05-11 03:00 | 354 | 346
2017-05-11 03:30 | 356 | 348
2017-05-11 04:00 | 359 | 350
2017-05-11 04:30 | 362 | 354
2017-05-11 05:00 | 372 | 366
2017-05-11 05:30 | 391 | 386
2017-05-11 06:00 | 415 | 412
2017-05-11 06:30 | 456 | 454
2017-05-11 07:00 | 496 | 493
2017-05-11 07:30 | 519 | 518
2017-05-11 08:00 | 524 | 523
2017-05-11 08:30 | 514 | 512
2017-05-11 09:00 | 490 | 488
2017-05-11 09:30 | 491 | 490
2017-05-11 10:00 | 488 | 487
2017-05-11 10:30 | 500 | 500
2017-05-11 11:00 | 495 | 495
2017-05-11 11:30 | 479 | 479
2017-05-11 12:00 | 478 | 477
2017-05-11 12:30 | 474 | 474
2017-05-11 13:00 | 466 | 465
2017-05-11 13:30 | 464 | 464
2017-05-11 14:00 | 490 | 489
2017-05-11 14:30 | 507 | 506
2017-05-11 15:00 | 512 | 511
2017-05-11 15:30 | 519 | 518
2017-05-11 16:00 | 530 | 529
2017-05-11 16:30 | 546 | 546
2017-05-11 17:00 | 547 | 547
2017-05-11 17:30 | 574 | 573
2017-05-11 18:00 | 595 | 594
2017-05-11 18:30 | 586 | 584
2017-05-11 19:00 | 585 | 583
2017-05-11 19:30 | 575 | 572
2017-05-11 20:00 | 562 | 561
2017-05-11 20:30 | 560 | 559
2017-05-11 21:00 | 544 | 543
2017-05-11 21:30 | 535 | 534
2017-05-11 22:00 | 519 | 518
2017-05-11 22:30 | 486 | 484
2017-05-11 23:00 | 458 | 455
2017-05-11 23:30 | 437 | 434
2017-05-12 | 406 | 402
2017-05-12 00:30 | 383 | 377
2017-05-12 01:00 | 369 | 363
2017-05-12 01:30 | 361 | 354
2017-05-12 02:00 | 356 | 349
2017-05-12 02:30 | 354 | 346
2017-05-12 03:00 | 352 | 344
2017-05-12 03:30 | 355 | 347
2017-05-12 04:00 | 359 | 350
2017-05-12 04:30 | 363 | 355
2017-05-12 05:00 | 367 | 360
2017-05-12 05:30 | 391 | 387
2017-05-12 06:00 | 401 | 398
2017-05-12 06:30 | 439 | 438
2017-05-12 07:00 | 475 | 474
2017-05-12 07:30 | 513 | 510
2017-05-12 08:00 | 533 | 527
2017-05-12 08:30 | 526 | 520
2017-05-12 09:00 | 510 | 504
2017-05-12 09:30 | 500 | 493
2017-05-12 10:00 | 486 | 479
2017-05-12 10:30 | 477 | 471
2017-05-12 11:00 | 469 | 464
2017-05-12 11:30 | 465 | 461
2017-05-12 12:00 | 473 | 469
2017-05-12 12:30 | 485 | 480
2017-05-12 13:00 | 487 | 482
2017-05-12 13:30 | 489 | 484
2017-05-12 14:00 | 491 | 486
2017-05-12 14:30 | 491 | 485
2017-05-12 15:00 | 489 | 484
2017-05-12 15:30 | 502 | 496
2017-05-12 16:00 | 507 | 502
2017-05-12 16:30 | 514 | 509
2017-05-12 17:00 | 523 | 518
2017-05-12 17:30 | 549 | 544
2017-05-12 18:00 | 566 | 559
2017-05-12 18:30 | 550 | 540
2017-05-12 19:00 | 547 | 535
2017-05-12 19:30 | 537 | 526
2017-05-12 20:00 | 518 | 516
2017-05-12 20:30 | 514 | 511
2017-05-12 21:00 | 495 | 492
2017-05-12 21:30 | 482 | 479
2017-05-12 22:00 | 471 | 469
2017-05-12 22:30 | 452 | 450
2017-05-12 23:00 | 432 | 430
2017-05-12 23:30 | 412 | 409
2017-05-13 | 385 | 381
2017-05-13 00:30 | 365 | 359
2017-05-13 01:00 | 347 | 340
2017-05-13 01:30 | 341 | 333
2017-05-13 02:00 | 340 | 331
2017-05-13 02:30 | 341 | 332
2017-05-13 03:00 | 333 | 324
2017-05-13 03:30 | 329 | 320
2017-05-13 04:00 | 328 | 319
2017-05-13 04:30 | 332 | 322
2017-05-13 05:00 | 331 | 322
2017-05-13 05:30 | 345 | 338
2017-05-13 06:00 | 355 | 348
2017-05-13 06:30 | 372 | 366
2017-05-13 07:00 | 389 | 383
2017-05-13 07:30 | 407 | 402
2017-05-13 08:00 | 420 | 417
2017-05-13 08:30 | 421 | 419
2017-05-13 09:00 | 419 | 417
2017-05-13 09:30 | 422 | 420
2017-05-13 10:00 | 411 | 409
2017-05-13 10:30 | 400 | 398
2017-05-13 11:00 | 403 | 402
2017-05-13 11:30 | 417 | 416
2017-05-13 12:00 | 416 | 414
2017-05-13 12:30 | 421 | 420
2017-05-13 13:00 | 419 | 418
2017-05-13 13:30 | 423 | 422
2017-05-13 14:00 | 423 | 422
2017-05-13 14:30 | 427 | 425
2017-05-13 15:00 | 429 | 428
2017-05-13 15:30 | 429 | 427
2017-05-13 16:00 | 440 | 438
2017-05-13 16:30 | 446 | 445
2017-05-13 17:00 | 472 | 471
2017-05-13 17:30 | 485 | 484
2017-05-13 18:00 | 496 | 495
2017-05-13 18:30 | 486 | 485
2017-05-13 19:00 | 478 | 477
2017-05-13 19:30 | 471 | 469
2017-05-13 20:00 | 463 | 463
2017-05-13 20:30 | 455 | 455
2017-05-13 21:00 | 443 | 443
2017-05-13 21:30 | 436 | 435
2017-05-13 22:00 | 430 | 429
2017-05-13 22:30 | 416 | 415
2017-05-13 23:00 | 412 | 411
2017-05-13 23:30 | 401 | 399
2017-05-14 | 377 | 374
2017-05-14 00:30 | 362 | 358
2017-05-14 01:00 | 348 | 342
2017-05-14 01:30 | 339 | 332
2017-05-14 02:00 | 334 | 326
2017-05-14 02:30 | 327 | 318
2017-05-14 03:00 | 326 | 317
2017-05-14 03:30 | 324 | 315
2017-05-14 04:00 | 329 | 320
2017-05-14 04:30 | 330 | 321
2017-05-14 05:00 | 331 | 321
2017-05-14 05:30 | 334 | 326
2017-05-14 06:00 | 336 | 328
2017-05-14 06:30 | 347 | 340
2017-05-14 07:00 | 362 | 354
2017-05-14 07:30 | 386 | 379
2017-05-14 08:00 | 399 | 395
2017-05-14 08:30 | 417 | 413
2017-05-14 09:00 | 424 | 421
2017-05-14 09:30 | 412 | 410
2017-05-14 10:00 | 410 | 407
2017-05-14 10:30 | 409 | 406
2017-05-14 11:00 | 409 | 407
2017-05-14 11:30 | 416 | 414
2017-05-14 12:00 | 411 | 409
2017-05-14 12:30 | 403 | 401
2017-05-14 13:00 | 406 | 403
2017-05-14 13:30 | 409 | 407
2017-05-14 14:00 | 414 | 412
2017-05-14 14:30 | 420 | 417
2017-05-14 15:00 | 413 | 410
2017-05-14 15:30 | 414 | 412
2017-05-14 16:00 | 424 | 422
2017-05-14 16:30 | 430 | 429
2017-05-14 17:00 | 446 | 445
2017-05-14 17:30 | 470 | 469
2017-05-14 18:00 | 481 | 481
2017-05-14 18:30 | 469 | 468
2017-05-14 19:00 | 467 | 466
2017-05-14 19:30 | 460 | 460
2017-05-14 20:00 | 457 | 456
2017-05-14 20:30 | 456 | 455
2017-05-14 21:00 | 442 | 442
2017-05-14 21:30 | 428 | 428
2017-05-14 22:00 | 423 | 423
2017-05-14 22:30 | 408 | 407
2017-05-14 23:00 | 402 | 401
2017-05-14 23:30 | 384 | 382
2017-05-15 | 358 | 355
2017-05-15 00:30 | 344 | 339
2017-05-15 01:00 | 338 | 330
2017-05-15 01:30 | 334 | 324
2017-05-15 02:00 | 331 | 321
2017-05-15 02:30 | 327 | 317
2017-05-15 03:00 | 326 | 316
2017-05-15 03:30 | 326 | 316
2017-05-15 04:00 | 335 | 325
2017-05-15 04:30 | 342 | 333
2017-05-15 05:00 | 352 | 344
2017-05-15 05:30 | 370 | 365
2017-05-15 06:00 | 386 | 383
2017-05-15 06:30 | 428 | 425
2017-05-15 07:00 | 474 | 472
2017-05-15 07:30 | 498 | 495
2017-05-15 08:00 | 505 | 504
2017-05-15 08:30 | 496 | 494
2017-05-15 09:00 | 479 | 478
2017-05-15 09:30 | 465 | 464
2017-05-15 10:00 | 458 | 457
2017-05-15 10:30 | 454 | 453
2017-05-15 11:00 | 454 | 453
2017-05-15 11:30 | 455 | 454
2017-05-15 12:00 | 453 | 453
2017-05-15 12:30 | 452 | 451
2017-05-15 13:00 | 457 | 456
2017-05-15 13:30 | 467 | 466
2017-05-15 14:00 | 466 | 465
2017-05-15 14:30 | 479 | 479
2017-05-15 15:00 | 482 | 482
2017-05-15 15:30 | 490 | 489
2017-05-15 16:00 | 501 | 501
2017-05-15 16:30 | 519 | 518
2017-05-15 17:00 | 537 | 536
2017-05-15 17:30 | 557 | 556
2017-05-15 18:00 | 576 | 573
2017-05-15 18:30 | 563 | 560
2017-05-15 19:00 | 550 | 548
2017-05-15 19:30 | 528 | 524
2017-05-15 20:00 | 516 | 514
2017-05-15 20:30 | 520 | 519
2017-05-15 21:00 | 497 | 496
2017-05-15 21:30 | 482 | 481
2017-05-15 22:00 | 461 | 460
2017-05-15 22:30 | 446 | 445
2017-05-15 23:00 | 423 | 422
2017-05-15 23:30 | 401 | 399
2017-05-16 | 373 | 371
2017-05-16 00:30 | 354 | 350
2017-05-16 01:00 | 350 | 344
2017-05-16 01:30 | 348 | 340
2017-05-16 02:00 | 344 | 336
2017-05-16 02:30 | 340 | 332
2017-05-16 03:00 | 337 | 329
2017-05-16 03:30 | 337 | 329
2017-05-16 04:00 | 336 | 328
2017-05-16 04:30 | 348 | 341
2017-05-16 05:00 | 363 | 357
2017-05-16 05:30 | 379 | 375
2017-05-16 06:00 | 394 | 391
2017-05-16 06:30 | 445 | 443
2017-05-16 07:00 | 496 | 494
2017-05-16 07:30 | 521 | 520
2017-05-16 08:00 | 526 | 525
2017-05-16 08:30 | 498 | 497
2017-05-16 09:00 | 478 | 478
2017-05-16 09:30 | 480 | 479
2017-05-16 10:00 | 465 | 465
2017-05-16 10:30 | 454 | 454
2017-05-16 11:00 | 453 | 453
2017-05-16 11:30 | 446 | 446
2017-05-16 12:00 | 443 | 443
2017-05-16 12:30 | 449 | 449
2017-05-16 13:00 | 450 | 450
2017-05-16 13:30 | 453 | 453
2017-05-16 14:00 | 459 | 459
2017-05-16 14:30 | 470 | 470
2017-05-16 15:00 | 474 | 474
2017-05-16 15:30 | 485 | 484
2017-05-16 16:00 | 502 | 502
2017-05-16 16:30 | 519 | 519
2017-05-16 17:00 | 528 | 528
2017-05-16 17:30 | 556 | 555
2017-05-16 18:00 | 575 | 574
2017-05-16 18:30 | 558 | 555
2017-05-16 19:00 | 556 | 553
2017-05-16 19:30 | 545 | 542
2017-05-16 20:00 | 531 | 531
2017-05-16 20:30 | 533 | 532
2017-05-16 21:00 | 507 | 507
2017-05-16 21:30 | 482 | 482
2017-05-16 22:00 | 458 | 457
2017-05-16 22:30 | 444 | 444
2017-05-16 23:00 | 424 | 423
2017-05-16 23:30 | 404 | 403
2017-05-17 | 370 | 367
2017-05-17 00:30 | 353 | 349
2017-05-17 01:00 | 343 | 337
2017-05-17 01:30 | 341 | 335
2017-05-17 02:00 | 336 | 328
2017-05-17 02:30 | 331 | 322
2017-05-17 03:00 | 331 | 322
2017-05-17 03:30 | 335 | 326
2017-05-17 04:00 | 341 | 332
2017-05-17 04:30 | 354 | 346
2017-05-17 05:00 | 359 | 352
2017-05-17 05:30 | 386 | 381
2017-05-17 06:00 | 415 | 413
2017-05-17 06:30 | 463 | 460
2017-05-17 07:00 | 489 | 488
2017-05-17 07:30 | 509 | 508
2017-05-17 08:00 | 510 | 509
2017-05-17 08:30 | 502 | 500
2017-05-17 09:00 | 484 | 482
2017-05-17 09:30 | 484 | 483
2017-05-17 10:00 | 486 | 484
2017-05-17 10:30 | 478 | 477
2017-05-17 11:00 | 466 | 465
2017-05-17 11:30 | 473 | 472
2017-05-17 12:00 | 480 | 480
2017-05-17 12:30 | 485 | 484
2017-05-17 13:00 | 486 | 485
2017-05-17 13:30 | 486 | 485
2017-05-17 14:00 | 497 | 497
2017-05-17 14:30 | 508 | 508
2017-05-17 15:00 | 511 | 511
2017-05-17 15:30 | 515 | 515
2017-05-17 16:00 | 525 | 525
2017-05-17 16:30 | 533 | 533
2017-05-17 17:00 | 553 | 552
2017-05-17 17:30 | 575 | 574
2017-05-17 18:00 | 599 | 597
2017-05-17 18:30 | 586 | 582
2017-05-17 19:00 | 579 | 575
2017-05-17 19:30 | 565 | 562
2017-05-17 20:00 | 553 | 552
2017-05-17 20:30 | 550 | 549
2017-05-17 21:00 | 521 | 520
2017-05-17 21:30 | 497 | 495
2017-05-17 22:00 | 485 | 483
2017-05-17 22:30 | 464 | 464
2017-05-17 23:00 | 444 | 443
2017-05-17 23:30 | 423 | 421
2017-05-18 | 391 | 388
2017-05-18 00:30 | 370 | 365
2017-05-18 01:00 | 363 | 356
2017-05-18 01:30 | 355 | 347
2017-05-18 02:00 | 352 | 344
2017-05-18 02:30 | 351 | 341
2017-05-18 03:00 | 349 | 340
2017-05-18 03:30 | 347 | 337
2017-05-18 04:00 | 351 | 342
2017-05-18 04:30 | 363 | 355
2017-05-18 05:00 | 375 | 368
2017-05-18 05:30 | 394 | 389
2017-05-18 06:00 | 420 | 416
2017-05-18 06:30 | 468 | 464
2017-05-18 07:00 | 503 | 501
2017-05-18 07:30 | 543 | 541
2017-05-18 08:00 | 550 | 548
2017-05-18 08:30 | 539 | 537
2017-05-18 09:00 | 524 | 522
2017-05-18 09:30 | 513 | 511
2017-05-18 10:00 | 518 | 516
2017-05-18 10:30 | 523 | 522
2017-05-18 11:00 | 522 | 520
2017-05-18 11:30 | 511 | 509
2017-05-18 12:00 | 505 | 503
2017-05-18 12:30 | 485 | 483
2017-05-18 13:00 | 482 | 481
2017-05-18 13:30 | 494 | 493
2017-05-18 14:00 | 506 | 505
2017-05-18 14:30 | 512 | 510
2017-05-18 15:00 | 516 | 515
2017-05-18 15:30 | 520 | 519
2017-05-18 16:00 | 531 | 530
2017-05-18 16:30 | 549 | 547
2017-05-18 17:00 | 572 | 570
2017-05-18 17:30 | 597 | 595
2017-05-18 18:00 | 601 | 598
2017-05-18 18:30 | 591 | 587
2017-05-18 19:00 | 585 | 580
2017-05-18 19:30 | 571 | 567
2017-05-18 20:00 | 567 | 563
2017-05-18 20:30 | 558 | 554
2017-05-18 21:00 | 527 | 524
2017-05-18 21:30 | 503 | 499
2017-05-18 22:00 | 485 | 481
2017-05-18 22:30 | 465 | 462
2017-05-18 23:00 | 452 | 449
2017-05-18 23:30 | 436 | 432
2017-05-19 | 403 | 398
2017-05-19 00:30 | 373 | 368
2017-05-19 01:00 | 364 | 357
2017-05-19 01:30 | 357 | 349
2017-05-19 02:00 | 350 | 342
2017-05-19 02:30 | 347 | 338
2017-05-19 03:00 | 344 | 335
2017-05-19 03:30 | 346 | 337
2017-05-19 04:00 | 353 | 344
2017-05-19 04:30 | 355 | 346
2017-05-19 05:00 | 364 | 357
2017-05-19 05:30 | 380 | 375
2017-05-19 06:00 | 402 | 399
2017-05-19 06:30 | 455 | 451
2017-05-19 07:00 | 508 | 498
2017-05-19 07:30 | 538 | 530
2017-05-19 08:00 | 562 | 555
2017-05-19 08:30 | 566 | 561
2017-05-19 09:00 | 562 | 557
2017-05-19 09:30 | 567 | 561
2017-05-19 10:00 | 559 | 553
2017-05-19 10:30 | 556 | 551
2017-05-19 11:00 | 552 | 546
2017-05-19 11:30 | 551 | 546
2017-05-19 12:00 | 557 | 551
2017-05-19 12:30 | 559 | 553
2017-05-19 13:00 | 552 | 546
2017-05-19 13:30 | 547 | 541
2017-05-19 14:00 | 540 | 534
2017-05-19 14:30 | 550 | 543
2017-05-19 15:00 | 547 | 540
2017-05-19 15:30 | 544 | 536
2017-05-19 16:00 | 553 | 546
2017-05-19 16:30 | 557 | 550
2017-05-19 17:00 | 564 | 559
2017-05-19 17:30 | 569 | 563
2017-05-19 18:00 | 564 | 557
2017-05-19 18:30 | 553 | 543
2017-05-19 19:00 | 537 | 533
2017-05-19 19:30 | 533 | 529
2017-05-19 20:00 | 525 | 523
2017-05-19 20:30 | 515 | 514
2017-05-19 21:00 | 501 | 500
2017-05-19 21:30 | 482 | 480
2017-05-19 22:00 | 470 | 467
2017-05-19 22:30 | 449 | 445
2017-05-19 23:00 | 431 | 428
2017-05-19 23:30 | 416 | 413
2017-05-20 | 398 | 394
2017-05-20 00:30 | 370 | 364
2017-05-20 01:00 | 352 | 344
2017-05-20 01:30 | 341 | 333
2017-05-20 02:00 | 328 | 319
2017-05-20 02:30 | 319 | 310
2017-05-20 03:00 | 314 | 303
2017-05-20 03:30 | 305 | 293
2017-05-20 04:00 | 310 | 299
2017-05-20 04:30 | 323 | 312
2017-05-20 05:00 | 329 | 319
2017-05-20 05:30 | 336 | 326
2017-05-20 06:00 | 342 | 333
2017-05-20 06:30 | 361 | 354
2017-05-20 07:00 | 377 | 370
2017-05-20 07:30 | 400 | 394
2017-05-20 08:00 | 411 | 407
2017-05-20 08:30 | 416 | 413
2017-05-20 09:00 | 417 | 415
2017-05-20 09:30 | 418 | 417
2017-05-20 10:00 | 413 | 412
2017-05-20 10:30 | 409 | 408
2017-05-20 11:00 | 408 | 408
2017-05-20 11:30 | 402 | 402
2017-05-20 12:00 | 408 | 407
2017-05-20 12:30 | 416 | 416
2017-05-20 13:00 | 420 | 420
2017-05-20 13:30 | 414 | 414
2017-05-20 14:00 | 413 | 412
2017-05-20 14:30 | 417 | 416
2017-05-20 15:00 | 423 | 422
2017-05-20 15:30 | 429 | 428
2017-05-20 16:00 | 434 | 433
2017-05-20 16:30 | 452 | 451
2017-05-20 17:00 | 473 | 472
2017-05-20 17:30 | 493 | 493
2017-05-20 18:00 | 504 | 503
2017-05-20 18:30 | 496 | 494
2017-05-20 19:00 | 491 | 490
2017-05-20 19:30 | 473 | 472
2017-05-20 20:00 | 470 | 470
2017-05-20 20:30 | 470 | 469
2017-05-20 21:00 | 455 | 454
2017-05-20 21:30 | 444 | 442
2017-05-20 22:00 | 434 | 432
2017-05-20 22:30 | 424 | 422
2017-05-20 23:00 | 413 | 410
2017-05-20 23:30 | 404 | 400
2017-05-21 | 382 | 376
2017-05-21 00:30 | 356 | 348
2017-05-21 01:00 | 345 | 336
2017-05-21 01:30 | 334 | 324
2017-05-21 02:00 | 334 | 322
2017-05-21 02:30 | 333 | 321
2017-05-21 03:00 | 329 | 317
2017-05-21 03:30 | 328 | 316
2017-05-21 04:00 | 329 | 316
2017-05-21 04:30 | 342 | 330
2017-05-21 05:00 | 352 | 340
2017-05-21 05:30 | 361 | 349
2017-05-21 06:00 | 371 | 360
2017-05-21 06:30 | 376 | 365
2017-05-21 07:00 | 386 | 374
2017-05-21 07:30 | 401 | 391
2017-05-21 08:00 | 422 | 414
2017-05-21 08:30 | 435 | 427
2017-05-21 09:00 | 437 | 431
2017-05-21 09:30 | 441 | 435
2017-05-21 10:00 | 444 | 440
2017-05-21 10:30 | 441 | 437
2017-05-21 11:00 | 430 | 426
2017-05-21 11:30 | 416 | 412
2017-05-21 12:00 | 391 | 387
2017-05-21 12:30 | 382 | 378
2017-05-21 13:00 | 379 | 375
2017-05-21 13:30 | 391 | 387
2017-05-21 14:00 | 399 | 396
2017-05-21 14:30 | 415 | 412
2017-05-21 15:00 | 421 | 418
2017-05-21 15:30 | 428 | 425
2017-05-21 16:00 | 438 | 436
2017-05-21 16:30 | 463 | 461
2017-05-21 17:00 | 484 | 482
2017-05-21 17:30 | 505 | 505
2017-05-21 18:00 | 523 | 522
2017-05-21 18:30 | 517 | 516
2017-05-21 19:00 | 510 | 509
2017-05-21 19:30 | 495 | 494
2017-05-21 20:00 | 487 | 485
2017-05-21 20:30 | 485 | 483
2017-05-21 21:00 | 471 | 469
2017-05-21 21:30 | 457 | 454
2017-05-21 22:00 | 453 | 450
2017-05-21 22:30 | 438 | 434
2017-05-21 23:00 | 431 | 427
2017-05-21 23:30 | 414 | 410
2017-05-22 | 389 | 383
2017-05-22 00:30 | 368 | 360
2017-05-22 01:00 | 353 | 344
2017-05-22 01:30 | 351 | 341
2017-05-22 02:00 | 354 | 344
2017-05-22 02:30 | 352 | 341
2017-05-22 03:00 | 351 | 340
2017-05-22 03:30 | 351 | 341
2017-05-22 04:00 | 348 | 337
2017-05-22 04:30 | 349 | 339
2017-05-22 05:00 | 357 | 349
2017-05-22 05:30 | 377 | 371
2017-05-22 06:00 | 405 | 402
2017-05-22 06:30 | 451 | 449
2017-05-22 07:00 | 491 | 490
2017-05-22 07:30 | 531 | 529
2017-05-22 08:00 | 540 | 539
2017-05-22 08:30 | 530 | 529
2017-05-22 09:00 | 513 | 512
2017-05-22 09:30 | 508 | 507
2017-05-22 10:00 | 497 | 496
2017-05-22 10:30 | 487 | 487
2017-05-22 11:00 | 486 | 486
2017-05-22 11:30 | 489 | 489
2017-05-22 12:00 | 496 | 496
2017-05-22 12:30 | 498 | 497
2017-05-22 13:00 | 497 | 497
2017-05-22 13:30 | 502 | 502
2017-05-22 14:00 | 509 | 509
2017-05-22 14:30 | 517 | 517
2017-05-22 15:00 | 524 | 524
2017-05-22 15:30 | 526 | 526
2017-05-22 16:00 | 537 | 537
2017-05-22 16:30 | 549 | 549
2017-05-22 17:00 | 563 | 563
2017-05-22 17:30 | 593 | 589
2017-05-22 18:00 | 600 | 593
2017-05-22 18:30 | 585 | 575
2017-05-22 19:00 | 583 | 571
2017-05-22 19:30 | 558 | 556
2017-05-22 20:00 | 551 | 550
2017-05-22 20:30 | 544 | 543
2017-05-22 21:00 | 527 | 526
2017-05-22 21:30 | 508 | 507
2017-05-22 22:00 | 497 | 496
2017-05-22 22:30 | 471 | 469
2017-05-22 23:00 | 451 | 449
2017-05-22 23:30 | 434 | 429
2017-05-23 | 411 | 406
2017-05-23 00:30 | 395 | 389
2017-05-23 01:00 | 381 | 373
2017-05-23 01:30 | 370 | 362
2017-05-23 02:00 | 366 | 355
2017-05-23 02:30 | 356 | 344
2017-05-23 03:00 | 360 | 348
2017-05-23 03:30 | 361 | 349
2017-05-23 04:00 | 368 | 356
2017-05-23 04:30 | 373 | 362
2017-05-23 05:00 | 382 | 373
2017-05-23 05:30 | 397 | 392
2017-05-23 06:00 | 419 | 416
2017-05-23 06:30 | 477 | 476
2017-05-23 07:00 | 518 | 518
2017-05-23 07:30 | 537 | 536
2017-05-23 08:00 | 541 | 540
2017-05-23 08:30 | 528 | 527
2017-05-23 09:00 | 508 | 506
2017-05-23 09:30 | 506 | 504
2017-05-23 10:00 | 504 | 503
2017-05-23 10:30 | 498 | 497
2017-05-23 11:00 | 495 | 495
2017-05-23 11:30 | 497 | 497
2017-05-23 12:00 | 497 | 497
2017-05-23 12:30 | 498 | 498
2017-05-23 13:00 | 494 | 493
2017-05-23 13:30 | 508 | 508
2017-05-23 14:00 | 516 | 514
2017-05-23 14:30 | 528 | 526
2017-05-23 15:00 | 541 | 539
2017-05-23 15:30 | 538 | 536
2017-05-23 16:00 | 546 | 545
2017-05-23 16:30 | 563 | 562
2017-05-23 17:00 | 581 | 579
2017-05-23 17:30 | 604 | 602
2017-05-23 18:00 | 610 | 607
2017-05-23 18:30 | 594 | 589
2017-05-23 19:00 | 589 | 584
2017-05-23 19:30 | 570 | 566
2017-05-23 20:00 | 560 | 559
2017-05-23 20:30 | 554 | 553
2017-05-23 21:00 | 537 | 537
2017-05-23 21:30 | 522 | 521
2017-05-23 22:00 | 511 | 510
2017-05-23 22:30 | 475 | 474
2017-05-23 23:00 | 458 | 456
2017-05-23 23:30 | 438 | 436
2017-05-24 | 413 | 411
2017-05-24 00:30 | 388 | 384
2017-05-24 01:00 | 374 | 369
2017-05-24 01:30 | 370 | 364
2017-05-24 02:00 | 366 | 359
2017-05-24 02:30 | 365 | 357
2017-05-24 03:00 | 364 | 357
2017-05-24 03:30 | 368 | 361
2017-05-24 04:00 | 371 | 363
2017-05-24 04:30 | 379 | 372
2017-05-24 05:00 | 387 | 381
2017-05-24 05:30 | 400 | 396
2017-05-24 06:00 | 420 | 418
2017-05-24 06:30 | 457 | 455
2017-05-24 07:00 | 493 | 490
2017-05-24 07:30 | 526 | 523
2017-05-24 08:00 | 550 | 545
2017-05-24 08:30 | 545 | 541
2017-05-24 09:00 | 529 | 525
2017-05-24 09:30 | 517 | 513
2017-05-24 10:00 | 507 | 503
2017-05-24 10:30 | 502 | 499
2017-05-24 11:00 | 495 | 492
2017-05-24 11:30 | 494 | 490
2017-05-24 12:00 | 489 | 486
2017-05-24 12:30 | 483 | 480
2017-05-24 13:00 | 486 | 484
2017-05-24 13:30 | 491 | 489
2017-05-24 14:00 | 507 | 505
2017-05-24 14:30 | 520 | 518
2017-05-24 15:00 | 522 | 520
2017-05-24 15:30 | 524 | 523
2017-05-24 16:00 | 533 | 531
2017-05-24 16:30 | 540 | 539
2017-05-24 17:00 | 548 | 547
2017-05-24 17:30 | 571 | 570
2017-05-24 18:00 | 589 | 586
2017-05-24 18:30 | 571 | 566
2017-05-24 19:00 | 572 | 567
2017-05-24 19:30 | 557 | 552
2017-05-24 20:00 | 552 | 549
2017-05-24 20:30 | 545 | 543
2017-05-24 21:00 | 529 | 529
2017-05-24 21:30 | 512 | 511
2017-05-24 22:00 | 500 | 498
2017-05-24 22:30 | 488 | 485
2017-05-24 23:00 | 480 | 478
2017-05-24 23:30 | 450 | 447
2017-05-25 | 404 | 401
2017-05-25 00:30 | 375 | 371
2017-05-25 01:00 | 363 | 357
2017-05-25 01:30 | 360 | 354
2017-05-25 02:00 | 357 | 350
2017-05-25 02:30 | 349 | 342
2017-05-25 03:00 | 348 | 340
2017-05-25 03:30 | 358 | 351
2017-05-25 04:00 | 364 | 357
2017-05-25 04:30 | 361 | 354
2017-05-25 05:00 | 374 | 368
2017-05-25 05:30 | 389 | 384
2017-05-25 06:00 | 407 | 405
2017-05-25 06:30 | 459 | 458
2017-05-25 07:00 | 508 | 502
2017-05-25 07:30 | 527 | 521
2017-05-25 08:00 | 536 | 531
2017-05-25 08:30 | 525 | 520
2017-05-25 09:00 | 507 | 503
2017-05-25 09:30 | 498 | 494
2017-05-25 10:00 | 488 | 484
2017-05-25 10:30 | 474 | 470
2017-05-25 11:00 | 462 | 459
2017-05-25 11:30 | 473 | 470
2017-05-25 12:00 | 475 | 471
2017-05-25 12:30 | 479 | 475
2017-05-25 13:00 | 479 | 476
2017-05-25 13:30 | 490 | 487
2017-05-25 14:00 | 498 | 495
2017-05-25 14:30 | 509 | 506
2017-05-25 15:00 | 510 | 507
2017-05-25 15:30 | 511 | 507
2017-05-25 16:00 | 519 | 515
2017-05-25 16:30 | 527 | 523
2017-05-25 17:00 | 541 | 536
2017-05-25 17:30 | 568 | 563
2017-05-25 18:00 | 587 | 580
2017-05-25 18:30 | 576 | 569
2017-05-25 19:00 | 569 | 565
2017-05-25 19:30 | 561 | 555
2017-05-25 20:00 | 548 | 546
2017-05-25 20:30 | 540 | 538
2017-05-25 21:00 | 523 | 521
2017-05-25 21:30 | 503 | 501
2017-05-25 22:00 | 490 | 487
2017-05-25 22:30 | 467 | 463
2017-05-25 23:00 | 440 | 436
2017-05-25 23:30 | 426 | 420
2017-05-26 | 400 | 395
2017-05-26 00:30 | 374 | 369
2017-05-26 01:00 | 363 | 356
2017-05-26 01:30 | 356 | 349
2017-05-26 02:00 | 348 | 340
2017-05-26 02:30 | 340 | 332
2017-05-26 03:00 | 339 | 331
2017-05-26 03:30 | 343 | 334
2017-05-26 04:00 | 353 | 344
2017-05-26 04:30 | 355 | 347
2017-05-26 05:00 | 363 | 356
2017-05-26 05:30 | 385 | 380
2017-05-26 06:00 | 406 | 404
2017-05-26 06:30 | 453 | 452
2017-05-26 07:00 | 497 | 494
2017-05-26 07:30 | 526 | 524
2017-05-26 08:00 | 535 | 534
2017-05-26 08:30 | 524 | 523
2017-05-26 09:00 | 501 | 500
2017-05-26 09:30 | 490 | 490
2017-05-26 10:00 | 484 | 484
2017-05-26 10:30 | 473 | 473
2017-05-26 11:00 | 465 | 465
2017-05-26 11:30 | 464 | 464
2017-05-26 12:00 | 462 | 462
2017-05-26 12:30 | 465 | 465
2017-05-26 13:00 | 464 | 464
2017-05-26 13:30 | 468 | 468
2017-05-26 14:00 | 476 | 476
2017-05-26 14:30 | 485 | 485
2017-05-26 15:00 | 488 | 488
2017-05-26 15:30 | 494 | 494
2017-05-26 16:00 | 501 | 501
2017-05-26 16:30 | 511 | 511
2017-05-26 17:00 | 526 | 526
2017-05-26 17:30 | 548 | 548
2017-05-26 18:00 | 560 | 559
2017-05-26 18:30 | 544 | 542
2017-05-26 19:00 | 542 | 540
2017-05-26 19:30 | 526 | 523
2017-05-26 20:00 | 516 | 515
2017-05-26 20:30 | 512 | 511
2017-05-26 21:00 | 493 | 492
2017-05-26 21:30 | 478 | 477
2017-05-26 22:00 | 473 | 471
2017-05-26 22:30 | 449 | 447
2017-05-26 23:00 | 429 | 426
2017-05-26 23:30 | 414 | 409
2017-05-27 | 388 | 382
2017-05-27 00:30 | 372 | 366
2017-05-27 01:00 | 360 | 353
2017-05-27 01:30 | 352 | 344
2017-05-27 02:00 | 341 | 331
2017-05-27 02:30 | 338 | 326
2017-05-27 03:00 | 336 | 324
2017-05-27 03:30 | 331 | 320
2017-05-27 04:00 | 329 | 318
2017-05-27 04:30 | 346 | 335
2017-05-27 05:00 | 351 | 341
2017-05-27 05:30 | 357 | 348
2017-05-27 06:00 | 361 | 353
2017-05-27 06:30 | 371 | 365
2017-05-27 07:00 | 392 | 386
2017-05-27 07:30 | 414 | 409
2017-05-27 08:00 | 426 | 422
2017-05-27 08:30 | 434 | 430
2017-05-27 09:00 | 435 | 433
2017-05-27 09:30 | 432 | 430
2017-05-27 10:00 | 412 | 410
2017-05-27 10:30 | 402 | 400
2017-05-27 11:00 | 397 | 396
2017-05-27 11:30 | 399 | 398
2017-05-27 12:00 | 394 | 393
2017-05-27 12:30 | 384 | 382
2017-05-27 13:00 | 382 | 380
2017-05-27 13:30 | 380 | 379
2017-05-27 14:00 | 394 | 393
2017-05-27 14:30 | 402 | 400
2017-05-27 15:00 | 409 | 407
2017-05-27 15:30 | 422 | 420
2017-05-27 16:00 | 432 | 430
2017-05-27 16:30 | 444 | 443
2017-05-27 17:00 | 459 | 458
2017-05-27 17:30 | 472 | 471
2017-05-27 18:00 | 480 | 478
2017-05-27 18:30 | 478 | 475
2017-05-27 19:00 | 472 | 469
2017-05-27 19:30 | 476 | 471
2017-05-27 20:00 | 465 | 462
2017-05-27 20:30 | 465 | 462
2017-05-27 21:00 | 453 | 450
2017-05-27 21:30 | 444 | 439
2017-05-27 22:00 | 438 | 432
2017-05-27 22:30 | 437 | 431
2017-05-27 23:00 | 430 | 424
2017-05-27 23:30 | 420 | 412
2017-05-28 | 398 | 391
2017-05-28 00:30 | 372 | 364
2017-05-28 01:00 | 359 | 350
2017-05-28 01:30 | 352 | 342
2017-05-28 02:00 | 348 | 338
2017-05-28 02:30 | 346 | 334
2017-05-28 03:00 | 346 | 334
2017-05-28 03:30 | 350 | 339
2017-05-28 04:00 | 345 | 333
2017-05-28 04:30 | 352 | 341
2017-05-28 05:00 | 356 | 344
2017-05-28 05:30 | 361 | 350
2017-05-28 06:00 | 366 | 356
2017-05-28 06:30 | 371 | 361
2017-05-28 07:00 | 374 | 364
2017-05-28 07:30 | 394 | 385
2017-05-28 08:00 | 403 | 395
2017-05-28 08:30 | 419 | 413
2017-05-28 09:00 | 427 | 422
2017-05-28 09:30 | 417 | 413
2017-05-28 10:00 | 409 | 404
2017-05-28 10:30 | 391 | 387
2017-05-28 11:00 | 386 | 382
2017-05-28 11:30 | 376 | 372
2017-05-28 12:00 | 379 | 376
2017-05-28 12:30 | 379 | 375
2017-05-28 13:00 | 377 | 374
2017-05-28 13:30 | 380 | 377
2017-05-28 14:00 | 391 | 388
2017-05-28 14:30 | 409 | 406
2017-05-28 15:00 | 425 | 423
2017-05-28 15:30 | 436 | 433
2017-05-28 16:00 | 443 | 440
2017-05-28 16:30 | 457 | 456
2017-05-28 17:00 | 471 | 471
2017-05-28 17:30 | 489 | 489
2017-05-28 18:00 | 503 | 502
2017-05-28 18:30 | 492 | 491
2017-05-28 19:00 | 487 | 485
2017-05-28 19:30 | 484 | 482
2017-05-28 20:00 | 483 | 482
2017-05-28 20:30 | 482 | 480
2017-05-28 21:00 | 465 | 462
2017-05-28 21:30 | 458 | 455
2017-05-28 22:00 | 447 | 443
2017-05-28 22:30 | 437 | 433
2017-05-28 23:00 | 428 | 425
2017-05-28 23:30 | 417 | 413
2017-05-29 | 391 | 386
2017-05-29 00:30 | 372 | 366
2017-05-29 01:00 | 364 | 357
2017-05-29 01:30 | 357 | 348
2017-05-29 02:00 | 350 | 341
2017-05-29 02:30 | 350 | 340
2017-05-29 03:00 | 349 | 339
2017-05-29 03:30 | 353 | 343
2017-05-29 04:00 | 362 | 353
2017-05-29 04:30 | 366 | 357
2017-05-29 05:00 | 378 | 370
2017-05-29 05:30 | 392 | 387
2017-05-29 06:00 | 409 | 406
2017-05-29 06:30 | 462 | 460
2017-05-29 07:00 | 496 | 493
2017-05-29 07:30 | 525 | 523
2017-05-29 08:00 | 535 | 534
2017-05-29 08:30 | 527 | 526
2017-05-29 09:00 | 514 | 513
2017-05-29 09:30 | 508 | 507
2017-05-29 10:00 | 497 | 496
2017-05-29 10:30 | 487 | 486
2017-05-29 11:00 | 481 | 480
2017-05-29 11:30 | 474 | 474
2017-05-29 12:00 | 474 | 473
2017-05-29 12:30 | 478 | 477
2017-05-29 13:00 | 482 | 482
2017-05-29 13:30 | 491 | 491
2017-05-29 14:00 | 492 | 492
2017-05-29 14:30 | 502 | 501
2017-05-29 15:00 | 506 | 506
2017-05-29 15:30 | 512 | 511
2017-05-29 16:00 | 530 | 529
2017-05-29 16:30 | 549 | 548
2017-05-29 17:00 | 571 | 568
2017-05-29 17:30 | 600 | 593
2017-05-29 18:00 | 605 | 599
2017-05-29 18:30 | 594 | 586
2017-05-29 19:00 | 586 | 576
2017-05-29 19:30 | 575 | 563
2017-05-29 20:00 | 572 | 559
2017-05-29 20:30 | 548 | 546
2017-05-29 21:00 | 529 | 527
2017-05-29 21:30 | 515 | 511
2017-05-29 22:00 | 499 | 497
2017-05-29 22:30 | 472 | 469
2017-05-29 23:00 | 455 | 454
2017-05-29 23:30 | 436 | 434
2017-05-30 | 410 | 407
2017-05-30 00:30 | 395 | 390
2017-05-30 01:00 | 382 | 376
2017-05-30 01:30 | 370 | 363
2017-05-30 02:00 | 360 | 351
2017-05-30 02:30 | 357 | 348
2017-05-30 03:00 | 357 | 347
2017-05-30 03:30 | 358 | 348
2017-05-30 04:00 | 370 | 361
2017-05-30 04:30 | 373 | 365
2017-05-30 05:00 | 389 | 382
2017-05-30 05:30 | 416 | 411
2017-05-30 06:00 | 443 | 440
2017-05-30 06:30 | 487 | 485
2017-05-30 07:00 | 528 | 524
2017-05-30 07:30 | 565 | 562
2017-05-30 08:00 | 574 | 571
2017-05-30 08:30 | 560 | 557
2017-05-30 09:00 | 539 | 536
2017-05-30 09:30 | 536 | 532
2017-05-30 10:00 | 521 | 516
2017-05-30 10:30 | 500 | 496
2017-05-30 11:00 | 495 | 491
2017-05-30 11:30 | 494 | 491
2017-05-30 12:00 | 491 | 488
2017-05-30 12:30 | 492 | 490
2017-05-30 13:00 | 496 | 494
2017-05-30 13:30 | 493 | 491
2017-05-30 14:00 | 499 | 497
2017-05-30 14:30 | 509 | 507
2017-05-30 15:00 | 516 | 515
2017-05-30 15:30 | 522 | 520
2017-05-30 16:00 | 535 | 533
2017-05-30 16:30 | 544 | 542
2017-05-30 17:00 | 582 | 580
2017-05-30 17:30 | 600 | 599
2017-05-30 18:00 | 603 | 603
2017-05-30 18:30 | 588 | 587
2017-05-30 19:00 | 581 | 581
2017-05-30 19:30 | 570 | 569
2017-05-30 20:00 | 568 | 568
2017-05-30 20:30 | 579 | 578
2017-05-30 21:00 | 553 | 551
2017-05-30 21:30 | 525 | 523
2017-05-30 22:00 | 509 | 506
2017-05-30 22:30 | 489 | 486
2017-05-30 23:00 | 467 | 465
2017-05-30 23:30 | 443 | 442
2017-05-31 | 416 | 415
2017-05-31 00:30 | 391 | 388
2017-05-31 01:00 | 380 | 376
2017-05-31 01:30 | 375 | 370
2017-05-31 02:00 | 370 | 364
2017-05-31 02:30 | 373 | 367
2017-05-31 03:00 | 370 | 364
2017-05-31 03:30 | 377 | 370
2017-05-31 04:00 | 378 | 372
2017-05-31 04:30 | 391 | 385
2017-05-31 05:00 | 403 | 399
2017-05-31 05:30 | 429 | 426
2017-05-31 06:00 | 448 | 447
2017-05-31 06:30 | 499 | 499
2017-05-31 07:00 | 537 | 537
2017-05-31 07:30 | 563 | 563
2017-05-31 08:00 | 563 | 563
2017-05-31 08:30 | 546 | 546
2017-05-31 09:00 | 523 | 523
2017-05-31 09:30 | 507 | 507
2017-05-31 10:00 | 487 | 486
2017-05-31 10:30 | 474 | 474
2017-05-31 11:00 | 480 | 480
2017-05-31 11:30 | 473 | 473
2017-05-31 12:00 | 467 | 467
2017-05-31 12:30 | 463 | 462
2017-05-31 13:00 | 456 | 456
2017-05-31 13:30 | 462 | 462
2017-05-31 14:00 | 470 | 470
2017-05-31 14:30 | 490 | 489
2017-05-31 15:00 | 507 | 507
2017-05-31 15:30 | 511 | 511
2017-05-31 16:00 | 530 | 530
2017-05-31 16:30 | 544 | 543
2017-05-31 17:00 | 570 | 568
2017-05-31 17:30 | 603 | 598
2017-05-31 18:00 | 611 | 605
2017-05-31 18:30 | 601 | 595
2017-05-31 19:00 | 598 | 591
2017-05-31 19:30 | 599 | 591
2017-05-31 20:00 | 601 | 593
2017-05-31 20:30 | 607 | 599
2017-05-31 21:00 | 582 | 576
2017-05-31 21:30 | 564 | 561
2017-05-31 22:00 | 543 | 541
2017-05-31 22:30 | 522 | 520
2017-05-31 23:00 | 497 | 494
2017-05-31 23:30 | 474 | 470
2017-06-01 | 453 | 449
2017-06-01 00:30 | 425 | 422
2017-06-01 01:00 | 409 | 404
2017-06-01 01:30 | 399 | 393
2017-06-01 02:00 | 390 | 383
2017-06-01 02:30 | 388 | 380
2017-06-01 03:00 | 386 | 379
2017-06-01 03:30 | 386 | 379
2017-06-01 04:00 | 386 | 379
2017-06-01 04:30 | 393 | 387
2017-06-01 05:00 | 409 | 403
2017-06-01 05:30 | 430 | 427
2017-06-01 06:00 | 457 | 456
2017-06-01 06:30 | 515 | 512
2017-06-01 07:00 | 569 | 565
2017-06-01 07:30 | 609 | 604
2017-06-01 08:00 | 618 | 613
2017-06-01 08:30 | 602 | 597
2017-06-01 09:00 | 570 | 564
2017-06-01 09:30 | 556 | 551
2017-06-01 10:00 | 533 | 530
2017-06-01 10:30 | 514 | 512
2017-06-01 11:00 | 503 | 502
2017-06-01 11:30 | 494 | 493
2017-06-01 12:00 | 489 | 488
2017-06-01 12:30 | 485 | 485
2017-06-01 13:00 | 488 | 488
2017-06-01 13:30 | 493 | 492
2017-06-01 14:00 | 500 | 500
2017-06-01 14:30 | 509 | 509
2017-06-01 15:00 | 518 | 518
2017-06-01 15:30 | 531 | 530
2017-06-01 16:00 | 549 | 548
2017-06-01 16:30 | 573 | 573
2017-06-01 17:00 | 599 | 597
2017-06-01 17:30 | 610 | 608
2017-06-01 18:00 | 622 | 620
2017-06-01 18:30 | 614 | 611
2017-06-01 19:00 | 614 | 612
2017-06-01 19:30 | 609 | 608
2017-06-01 20:00 | 614 | 611
2017-06-01 20:30 | 616 | 614
2017-06-01 21:00 | 608 | 605
2017-06-01 21:30 | 587 | 584
2017-06-01 22:00 | 566 | 563
2017-06-01 22:30 | 540 | 538
2017-06-01 23:00 | 513 | 511
2017-06-01 23:30 | 488 | 486
2017-06-02 | 459 | 457
2017-06-02 00:30 | 432 | 429
2017-06-02 01:00 | 411 | 407
2017-06-02 01:30 | 398 | 392
2017-06-02 02:00 | 388 | 382
2017-06-02 02:30 | 386 | 379
2017-06-02 03:00 | 385 | 378
2017-06-02 03:30 | 393 | 387
2017-06-02 04:00 | 400 | 394
2017-06-02 04:30 | 407 | 401
2017-06-02 05:00 | 415 | 410
2017-06-02 05:30 | 442 | 439
2017-06-02 06:00 | 467 | 466
2017-06-02 06:30 | 507 | 506
2017-06-02 07:00 | 550 | 549
2017-06-02 07:30 | 592 | 584
2017-06-02 08:00 | 604 | 596
2017-06-02 08:30 | 588 | 580
2017-06-02 09:00 | 567 | 557
2017-06-02 09:30 | 548 | 540
2017-06-02 10:00 | 526 | 523
2017-06-02 10:30 | 508 | 505
2017-06-02 11:00 | 494 | 492
2017-06-02 11:30 | 481 | 480
2017-06-02 12:00 | 470 | 469
2017-06-02 12:30 | 467 | 467
2017-06-02 13:00 | 466 | 465
2017-06-02 13:30 | 468 | 468
2017-06-02 14:00 | 477 | 476
2017-06-02 14:30 | 488 | 488
2017-06-02 15:00 | 492 | 492
2017-06-02 15:30 | 501 | 501
2017-06-02 16:00 | 522 | 522
2017-06-02 16:30 | 549 | 548
2017-06-02 17:00 | 578 | 577
2017-06-02 17:30 | 588 | 587
2017-06-02 18:00 | 585 | 584
2017-06-02 18:30 | 573 | 572
2017-06-02 19:00 | 574 | 573
2017-06-02 19:30 | 571 | 569
2017-06-02 20:00 | 569 | 568
2017-06-02 20:30 | 574 | 573
2017-06-02 21:00 | 561 | 559
2017-06-02 21:30 | 541 | 539
2017-06-02 22:00 | 531 | 529
2017-06-02 22:30 | 520 | 519
2017-06-02 23:00 | 498 | 496
2017-06-02 23:30 | 479 | 477
2017-06-03 | 451 | 447
2017-06-03 00:30 | 424 | 418
2017-06-03 01:00 | 401 | 396
2017-06-03 01:30 | 390 | 383
2017-06-03 02:00 | 380 | 372
2017-06-03 02:30 | 372 | 364
2017-06-03 03:00 | 374 | 366
2017-06-03 03:30 | 375 | 367
2017-06-03 04:00 | 376 | 367
2017-06-03 04:30 | 379 | 371
2017-06-03 05:00 | 385 | 377
2017-06-03 05:30 | 402 | 395
2017-06-03 06:00 | 413 | 407
2017-06-03 06:30 | 430 | 426
2017-06-03 07:00 | 439 | 436
2017-06-03 07:30 | 451 | 449
2017-06-03 08:00 | 461 | 458
2017-06-03 08:30 | 474 | 471
2017-06-03 09:00 | 466 | 463
2017-06-03 09:30 | 467 | 464
2017-06-03 10:00 | 454 | 451
2017-06-03 10:30 | 437 | 434
2017-06-03 11:00 | 421 | 418
2017-06-03 11:30 | 407 | 405
2017-06-03 12:00 | 401 | 399
2017-06-03 12:30 | 396 | 393
2017-06-03 13:00 | 395 | 393
2017-06-03 13:30 | 396 | 394
2017-06-03 14:00 | 397 | 396
2017-06-03 14:30 | 408 | 406
2017-06-03 15:00 | 424 | 422
2017-06-03 15:30 | 440 | 439
2017-06-03 16:00 | 449 | 447
2017-06-03 16:30 | 462 | 461
2017-06-03 17:00 | 489 | 488
2017-06-03 17:30 | 519 | 518
2017-06-03 18:00 | 530 | 528
2017-06-03 18:30 | 532 | 530
2017-06-03 19:00 | 527 | 525
2017-06-03 19:30 | 518 | 515
2017-06-03 20:00 | 513 | 511
2017-06-03 20:30 | 524 | 523
2017-06-03 21:00 | 507 | 505
2017-06-03 21:30 | 486 | 485
2017-06-03 22:00 | 484 | 483
2017-06-03 22:30 | 484 | 483
2017-06-03 23:00 | 469 | 468
2017-06-03 23:30 | 456 | 454
2017-06-04 | 430 | 427
2017-06-04 00:30 | 396 | 391
2017-06-04 01:00 | 382 | 375
2017-06-04 01:30 | 378 | 371
2017-06-04 02:00 | 363 | 356
2017-06-04 02:30 | 358 | 350
2017-06-04 03:00 | 353 | 344
2017-06-04 03:30 | 352 | 344
2017-06-04 04:00 | 351 | 342
2017-06-04 04:30 | 351 | 343
2017-06-04 05:00 | 356 | 347
2017-06-04 05:30 | 365 | 357
2017-06-04 06:00 | 377 | 370
2017-06-04 06:30 | 390 | 384
2017-06-04 07:00 | 404 | 397
2017-06-04 07:30 | 413 | 407
2017-06-04 08:00 | 420 | 414
2017-06-04 08:30 | 428 | 424
2017-06-04 09:00 | 427 | 423
2017-06-04 09:30 | 425 | 422
2017-06-04 10:00 | 416 | 414
2017-06-04 10:30 | 404 | 402
2017-06-04 11:00 | 391 | 388
2017-06-04 11:30 | 380 | 378
2017-06-04 12:00 | 382 | 379
2017-06-04 12:30 | 385 | 382
2017-06-04 13:00 | 388 | 385
2017-06-04 13:30 | 388 | 385
2017-06-04 14:00 | 397 | 395
2017-06-04 14:30 | 411 | 409
2017-06-04 15:00 | 418 | 416
2017-06-04 15:30 | 429 | 427
2017-06-04 16:00 | 441 | 440
2017-06-04 16:30 | 451 | 450
2017-06-04 17:00 | 469 | 469
2017-06-04 17:30 | 497 | 495
2017-06-04 18:00 | 510 | 509
2017-06-04 18:30 | 504 | 502
2017-06-04 19:00 | 505 | 503
2017-06-04 19:30 | 499 | 497
2017-06-04 20:00 | 500 | 498
2017-06-04 20:30 | 505 | 503
2017-06-04 21:00 | 489 | 488
2017-06-04 21:30 | 478 | 476
2017-06-04 22:00 | 467 | 465
2017-06-04 22:30 | 459 | 457
2017-06-04 23:00 | 439 | 438
2017-06-04 23:30 | 418 | 416
2017-06-05 | 391 | 388
2017-06-05 00:30 | 367 | 362
2017-06-05 01:00 | 354 | 349
2017-06-05 01:30 | 348 | 343
2017-06-05 02:00 | 354 | 348
2017-06-05 02:30 | 348 | 341
2017-06-05 03:00 | 353 | 346
2017-06-05 03:30 | 354 | 347
2017-06-05 04:00 | 357 | 349
2017-06-05 04:30 | 364 | 357
2017-06-05 05:00 | 385 | 379
2017-06-05 05:30 | 407 | 403
2017-06-05 06:00 | 427 | 425
2017-06-05 06:30 | 479 | 478
2017-06-05 07:00 | 529 | 528
2017-06-05 07:30 | 559 | 559
2017-06-05 08:00 | 570 | 567
2017-06-05 08:30 | 559 | 553
2017-06-05 09:00 | 544 | 533
2017-06-05 09:30 | 533 | 518
2017-06-05 10:00 | 503 | 497
2017-06-05 10:30 | 481 | 478
2017-06-05 11:00 | 478 | 475
2017-06-05 11:30 | 470 | 469
2017-06-05 12:00 | 466 | 465
2017-06-05 12:30 | 469 | 468
2017-06-05 13:00 | 472 | 471
2017-06-05 13:30 | 471 | 470
2017-06-05 14:00 | 476 | 475
2017-06-05 14:30 | 485 | 485
2017-06-05 15:00 | 487 | 486
2017-06-05 15:30 | 488 | 488
2017-06-05 16:00 | 503 | 502
2017-06-05 16:30 | 526 | 524
2017-06-05 17:00 | 554 | 552
2017-06-05 17:30 | 588 | 584
2017-06-05 18:00 | 592 | 586
2017-06-05 18:30 | 579 | 571
2017-06-05 19:00 | 576 | 570
2017-06-05 19:30 | 575 | 568
2017-06-05 20:00 | 575 | 568
2017-06-05 20:30 | 573 | 566
2017-06-05 21:00 | 544 | 539
2017-06-05 21:30 | 516 | 512
2017-06-05 22:00 | 498 | 495
2017-06-05 22:30 | 474 | 474
2017-06-05 23:00 | 451 | 451
2017-06-05 23:30 | 431 | 430
2017-06-06 | 415 | 414
2017-06-06 00:30 | 394 | 392
2017-06-06 01:00 | 371 | 368
2017-06-06 01:30 | 363 | 360
2017-06-06 02:00 | 358 | 354
2017-06-06 02:30 | 354 | 350
2017-06-06 03:00 | 352 | 347
2017-06-06 03:30 | 351 | 346
2017-06-06 04:00 | 359 | 355
2017-06-06 04:30 | 375 | 371
2017-06-06 05:00 | 389 | 385
2017-06-06 05:30 | 408 | 406
2017-06-06 06:00 | 434 | 433
2017-06-06 06:30 | 480 | 480
2017-06-06 07:00 | 534 | 533
2017-06-06 07:30 | 561 | 561
2017-06-06 08:00 | 559 | 558
2017-06-06 08:30 | 545 | 544
2017-06-06 09:00 | 525 | 524
2017-06-06 09:30 | 518 | 517
2017-06-06 10:00 | 501 | 500
2017-06-06 10:30 | 481 | 478
2017-06-06 11:00 | 478 | 476
2017-06-06 11:30 | 478 | 476
2017-06-06 12:00 | 474 | 473
2017-06-06 12:30 | 478 | 477
2017-06-06 13:00 | 487 | 486
2017-06-06 13:30 | 483 | 482
2017-06-06 14:00 | 486 | 485
2017-06-06 14:30 | 488 | 487
2017-06-06 15:00 | 497 | 495
2017-06-06 15:30 | 510 | 509
2017-06-06 16:00 | 538 | 537
2017-06-06 16:30 | 559 | 558
2017-06-06 17:00 | 605 | 604
2017-06-06 17:30 | 634 | 633
2017-06-06 18:00 | 650 | 649
2017-06-06 18:30 | 643 | 640
2017-06-06 19:00 | 645 | 642
2017-06-06 19:30 | 639 | 636
2017-06-06 20:00 | 633 | 632
2017-06-06 20:30 | 633 | 632
2017-06-06 21:00 | 599 | 598
2017-06-06 21:30 | 571 | 568
2017-06-06 22:00 | 541 | 538
2017-06-06 22:30 | 508 | 506
2017-06-06 23:00 | 483 | 481
2017-06-06 23:30 | 467 | 465
2017-06-07 | 435 | 434
2017-06-07 00:30 | 411 | 408
2017-06-07 01:00 | 400 | 396
2017-06-07 01:30 | 392 | 387
2017-06-07 02:00 | 383 | 377
2017-06-07 02:30 | 374 | 368
2017-06-07 03:00 | 373 | 366
2017-06-07 03:30 | 378 | 371
2017-06-07 04:00 | 377 | 371
2017-06-07 04:30 | 381 | 376
2017-06-07 05:00 | 394 | 390
2017-06-07 05:30 | 424 | 421
2017-06-07 06:00 | 447 | 447
2017-06-07 06:30 | 507 | 507
2017-06-07 07:00 | 567 | 567
2017-06-07 07:30 | 596 | 596
2017-06-07 08:00 | 603 | 602
2017-06-07 08:30 | 584 | 583
2017-06-07 09:00 | 566 | 565
2017-06-07 09:30 | 564 | 562
2017-06-07 10:00 | 542 | 540
2017-06-07 10:30 | 524 | 523
2017-06-07 11:00 | 510 | 509
2017-06-07 11:30 | 496 | 495
2017-06-07 12:00 | 489 | 488
2017-06-07 12:30 | 488 | 487
2017-06-07 13:00 | 499 | 498
2017-06-07 13:30 | 502 | 502
2017-06-07 14:00 | 503 | 502
2017-06-07 14:30 | 513 | 512
2017-06-07 15:00 | 522 | 522
2017-06-07 15:30 | 528 | 527
2017-06-07 16:00 | 546 | 546
2017-06-07 16:30 | 563 | 562
2017-06-07 17:00 | 595 | 594
2017-06-07 17:30 | 616 | 610
2017-06-07 18:00 | 628 | 622
2017-06-07 18:30 | 624 | 618
2017-06-07 19:00 | 624 | 617
2017-06-07 19:30 | 614 | 607
2017-06-07 20:00 | 618 | 610
2017-06-07 20:30 | 631 | 623
2017-06-07 21:00 | 606 | 602
2017-06-07 21:30 | 573 | 570
2017-06-07 22:00 | 545 | 542
2017-06-07 22:30 | 528 | 525
2017-06-07 23:00 | 500 | 498
2017-06-07 23:30 | 485 | 482
2017-06-08 | 461 | 458
2017-06-08 00:30 | 424 | 421
2017-06-08 01:00 | 409 | 405
2017-06-08 01:30 | 403 | 399
2017-06-08 02:00 | 402 | 396
2017-06-08 02:30 | 396 | 390
2017-06-08 03:00 | 395 | 390
2017-06-08 03:30 | 400 | 394
2017-06-08 04:00 | 404 | 399
2017-06-08 04:30 | 410 | 405
2017-06-08 05:00 | 421 | 417
2017-06-08 05:30 | 436 | 433
2017-06-08 06:00 | 458 | 457
2017-06-08 06:30 | 519 | 518
2017-06-08 07:00 | 576 | 575
2017-06-08 07:30 | 608 | 608
2017-06-08 08:00 | 613 | 612
2017-06-08 08:30 | 604 | 603
2017-06-08 09:00 | 595 | 593
2017-06-08 09:30 | 579 | 577
2017-06-08 10:00 | 559 | 558
2017-06-08 10:30 | 537 | 535
2017-06-08 11:00 | 522 | 520
2017-06-08 11:30 | 505 | 503
2017-06-08 12:00 | 508 | 507
2017-06-08 12:30 | 510 | 509
2017-06-08 13:00 | 500 | 499
2017-06-08 13:30 | 498 | 497
2017-06-08 14:00 | 496 | 495
2017-06-08 14:30 | 504 | 504
2017-06-08 15:00 | 511 | 510
2017-06-08 15:30 | 519 | 518
2017-06-08 16:00 | 513 | 512
2017-06-08 16:30 | 531 | 530
2017-06-08 17:00 | 555 | 555
2017-06-08 17:30 | 578 | 577
2017-06-08 18:00 | 593 | 593
2017-06-08 18:30 | 594 | 593
2017-06-08 19:00 | 596 | 595
2017-06-08 19:30 | 588 | 586
2017-06-08 20:00 | 591 | 590
2017-06-08 20:30 | 595 | 594
2017-06-08 21:00 | 577 | 574
2017-06-08 21:30 | 552 | 549
2017-06-08 22:00 | 529 | 527
2017-06-08 22:30 | 510 | 508
2017-06-08 23:00 | 483 | 482
2017-06-08 23:30 | 457 | 456
2017-06-09 | 426 | 424
2017-06-09 00:30 | 398 | 395
2017-06-09 01:00 | 385 | 380
2017-06-09 01:30 | 377 | 372
2017-06-09 02:00 | 373 | 366
2017-06-09 02:30 | 368 | 362
2017-06-09 03:00 | 368 | 362
2017-06-09 03:30 | 368 | 363
2017-06-09 04:00 | 386 | 381
2017-06-09 04:30 | 386 | 382
2017-06-09 05:00 | 397 | 394
2017-06-09 05:30 | 419 | 416
2017-06-09 06:00 | 436 | 434
2017-06-09 06:30 | 485 | 484
2017-06-09 07:00 | 528 | 524
2017-06-09 07:30 | 565 | 560
2017-06-09 08:00 | 568 | 562
2017-06-09 08:30 | 556 | 548
2017-06-09 09:00 | 506 | 500
2017-06-09 09:30 | 470 | 469
2017-06-09 10:00 | 474 | 473
2017-06-09 10:30 | 472 | 472
2017-06-09 11:00 | 469 | 469
2017-06-09 11:30 | 475 | 475
2017-06-09 12:00 | 488 | 487
2017-06-09 12:30 | 488 | 488
2017-06-09 13:00 | 495 | 495
2017-06-09 13:30 | 508 | 508
2017-06-09 14:00 | 516 | 516
2017-06-09 14:30 | 514 | 514
2017-06-09 15:00 | 514 | 513
2017-06-09 15:30 | 517 | 517
2017-06-09 16:00 | 535 | 534
2017-06-09 16:30 | 547 | 547
2017-06-09 17:00 | 564 | 564
2017-06-09 17:30 | 580 | 579
2017-06-09 18:00 | 579 | 578
2017-06-09 18:30 | 571 | 569
2017-06-09 19:00 | 564 | 562
2017-06-09 19:30 | 553 | 550
2017-06-09 20:00 | 548 | 547
2017-06-09 20:30 | 548 | 548
2017-06-09 21:00 | 532 | 532
2017-06-09 21:30 | 521 | 520
2017-06-09 22:00 | 511 | 510
2017-06-09 22:30 | 498 | 496
2017-06-09 23:00 | 478 | 476
2017-06-09 23:30 | 460 | 458
2017-06-10 | 424 | 422
2017-06-10 00:30 | 400 | 397
2017-06-10 01:00 | 373 | 369
2017-06-10 01:30 | 362 | 357
2017-06-10 02:00 | 356 | 351
2017-06-10 02:30 | 351 | 345
2017-06-10 03:00 | 351 | 345
2017-06-10 03:30 | 355 | 348
2017-06-10 04:00 | 358 | 351
2017-06-10 04:30 | 369 | 363
2017-06-10 05:00 | 371 | 365
2017-06-10 05:30 | 377 | 371
2017-06-10 06:00 | 376 | 371
2017-06-10 06:30 | 396 | 392
2017-06-10 07:00 | 410 | 406
2017-06-10 07:30 | 421 | 418
2017-06-10 08:00 | 433 | 430
2017-06-10 08:30 | 444 | 442
2017-06-10 09:00 | 448 | 446
2017-06-10 09:30 | 447 | 446
2017-06-10 10:00 | 437 | 435
2017-06-10 10:30 | 428 | 426
2017-06-10 11:00 | 430 | 428
2017-06-10 11:30 | 426 | 425
2017-06-10 12:00 | 436 | 435
2017-06-10 12:30 | 441 | 440
2017-06-10 13:00 | 441 | 440
2017-06-10 13:30 | 437 | 435
2017-06-10 14:00 | 432 | 430
2017-06-10 14:30 | 436 | 434
2017-06-10 15:00 | 443 | 441
2017-06-10 15:30 | 447 | 445
2017-06-10 16:00 | 454 | 452
2017-06-10 16:30 | 473 | 472
2017-06-10 17:00 | 501 | 501
2017-06-10 17:30 | 511 | 511
2017-06-10 18:00 | 516 | 515
2017-06-10 18:30 | 512 | 512
2017-06-10 19:00 | 508 | 508
2017-06-10 19:30 | 509 | 508
2017-06-10 20:00 | 503 | 503
2017-06-10 20:30 | 506 | 505
2017-06-10 21:00 | 491 | 489
2017-06-10 21:30 | 480 | 477
2017-06-10 22:00 | 464 | 461
2017-06-10 22:30 | 453 | 449
2017-06-10 23:00 | 448 | 445
2017-06-10 23:30 | 431 | 428
2017-06-11 | 404 | 401
2017-06-11 00:30 | 390 | 386
2017-06-11 01:00 | 374 | 368
2017-06-11 01:30 | 361 | 355
2017-06-11 02:00 | 350 | 343
2017-06-11 02:30 | 334 | 328
2017-06-11 03:00 | 333 | 327
2017-06-11 03:30 | 330 | 324
2017-06-11 04:00 | 330 | 325
2017-06-11 04:30 | 330 | 324
2017-06-11 05:00 | 331 | 326
2017-06-11 05:30 | 335 | 330
2017-06-11 06:00 | 338 | 333
2017-06-11 06:30 | 350 | 346
2017-06-11 07:00 | 361 | 357
2017-06-11 07:30 | 380 | 376
2017-06-11 08:00 | 397 | 395
2017-06-11 08:30 | 417 | 415
2017-06-11 09:00 | 439 | 438
2017-06-11 09:30 | 458 | 456
2017-06-11 10:00 | 459 | 457
2017-06-11 10:30 | 456 | 454
2017-06-11 11:00 | 454 | 452
2017-06-11 11:30 | 449 | 447
2017-06-11 12:00 | 442 | 440
2017-06-11 12:30 | 448 | 446
2017-06-11 13:00 | 442 | 440
2017-06-11 13:30 | 446 | 444
2017-06-11 14:00 | 454 | 452
2017-06-11 14:30 | 452 | 450
2017-06-11 15:00 | 444 | 442
2017-06-11 15:30 | 441 | 439
2017-06-11 16:00 | 446 | 444
2017-06-11 16:30 | 458 | 457
2017-06-11 17:00 | 476 | 475
2017-06-11 17:30 | 499 | 498
2017-06-11 18:00 | 517 | 516
2017-06-11 18:30 | 511 | 510
2017-06-11 19:00 | 509 | 508
2017-06-11 19:30 | 502 | 501
2017-06-11 20:00 | 496 | 495
2017-06-11 20:30 | 495 | 494
2017-06-11 21:00 | 475 | 474
2017-06-11 21:30 | 453 | 451
2017-06-11 22:00 | 443 | 440
2017-06-11 22:30 | 425 | 423
2017-06-11 23:00 | 416 | 415
2017-06-11 23:30 | 399 | 398
2017-06-12 | 373 | 371
2017-06-12 00:30 | 356 | 353
2017-06-12 01:00 | 348 | 344
2017-06-12 01:30 | 347 | 343
2017-06-12 02:00 | 349 | 344
2017-06-12 02:30 | 349 | 344
2017-06-12 03:00 | 361 | 356
2017-06-12 03:30 | 368 | 364
2017-06-12 04:00 | 368 | 364
2017-06-12 04:30 | 368 | 364
2017-06-12 05:00 | 377 | 373
2017-06-12 05:30 | 391 | 389
2017-06-12 06:00 | 410 | 409
2017-06-12 06:30 | 463 | 461
2017-06-12 07:00 | 506 | 499
2017-06-12 07:30 | 540 | 535
2017-06-12 08:00 | 555 | 548
2017-06-12 08:30 | 561 | 554
2017-06-12 09:00 | 558 | 550
2017-06-12 09:30 | 552 | 543
2017-06-12 10:00 | 543 | 535
2017-06-12 10:30 | 535 | 526
2017-06-12 11:00 | 524 | 516
2017-06-12 11:30 | 518 | 510
2017-06-12 12:00 | 511 | 504
2017-06-12 12:30 | 505 | 497
2017-06-12 13:00 | 510 | 503
2017-06-12 13:30 | 527 | 520
2017-06-12 14:00 | 536 | 529
2017-06-12 14:30 | 539 | 533
2017-06-12 15:00 | 539 | 533
2017-06-12 15:30 | 539 | 532
2017-06-12 16:00 | 546 | 539
2017-06-12 16:30 | 563 | 557
2017-06-12 17:00 | 595 | 589
2017-06-12 17:30 | 625 | 618
2017-06-12 18:00 | 626 | 618
2017-06-12 18:30 | 615 | 605
2017-06-12 19:00 | 612 | 602
2017-06-12 19:30 | 596 | 585
2017-06-12 20:00 | 580 | 575
2017-06-12 20:30 | 577 | 572
2017-06-12 21:00 | 551 | 546
2017-06-12 21:30 | 542 | 536
2017-06-12 22:00 | 534 | 527
2017-06-12 22:30 | 505 | 504
2017-06-12 23:00 | 491 | 490
2017-06-12 23:30 | 466 | 466
2017-06-13 | 426 | 425
2017-06-13 00:30 | 390 | 388
2017-06-13 01:00 | 381 | 379
2017-06-13 01:30 | 372 | 369
2017-06-13 02:00 | 366 | 363
2017-06-13 02:30 | 362 | 359
2017-06-13 03:00 | 361 | 357
2017-06-13 03:30 | 365 | 361
2017-06-13 04:00 | 378 | 374
2017-06-13 04:30 | 385 | 381
2017-06-13 05:00 | 410 | 407
2017-06-13 05:30 | 416 | 414
2017-06-13 06:00 | 435 | 434
2017-06-13 06:30 | 490 | 490
2017-06-13 07:00 | 533 | 532
2017-06-13 07:30 | 570 | 569
2017-06-13 08:00 | 602 | 601
2017-06-13 08:30 | 609 | 607
2017-06-13 09:00 | 604 | 602
2017-06-13 09:30 | 604 | 603
2017-06-13 10:00 | 596 | 595
2017-06-13 10:30 | 586 | 585
2017-06-13 11:00 | 582 | 581
2017-06-13 11:30 | 581 | 580
2017-06-13 12:00 | 578 | 577
2017-06-13 12:30 | 583 | 582
2017-06-13 13:00 | 591 | 590
2017-06-13 13:30 | 595 | 594
2017-06-13 14:00 | 595 | 594
2017-06-13 14:30 | 591 | 590
2017-06-13 15:00 | 582 | 581
2017-06-13 15:30 | 585 | 584
2017-06-13 16:00 | 603 | 602
2017-06-13 16:30 | 610 | 609
2017-06-13 17:00 | 619 | 618
2017-06-13 17:30 | 650 | 649
2017-06-13 18:00 | 669 | 668
2017-06-13 18:30 | 660 | 658
2017-06-13 19:00 | 657 | 654
2017-06-13 19:30 | 639 | 636
2017-06-13 20:00 | 633 | 630
2017-06-13 20:30 | 639 | 635
2017-06-13 21:00 | 612 | 607
2017-06-13 21:30 | 578 | 575
2017-06-13 22:00 | 559 | 558
2017-06-13 22:30 | 535 | 533
2017-06-13 23:00 | 520 | 517
2017-06-13 23:30 | 489 | 487
2017-06-14 | 443 | 442
2017-06-14 00:30 | 426 | 425
2017-06-14 01:00 | 406 | 404
2017-06-14 01:30 | 400 | 397
2017-06-14 02:00 | 395 | 392
2017-06-14 02:30 | 391 | 388
2017-06-14 03:00 | 388 | 386
2017-06-14 03:30 | 387 | 385
2017-06-14 04:00 | 383 | 379
2017-06-14 04:30 | 379 | 376
2017-06-14 05:00 | 415 | 413
2017-06-14 05:30 | 426 | 425
2017-06-14 06:00 | 449 | 448
2017-06-14 06:30 | 511 | 508
2017-06-14 07:00 | 554 | 549
2017-06-14 07:30 | 580 | 577
2017-06-14 08:00 | 586 | 581
2017-06-14 08:30 | 573 | 567
2017-06-14 09:00 | 569 | 563
2017-06-14 09:30 | 568 | 562
2017-06-14 10:00 | 572 | 567
2017-06-14 10:30 | 568 | 563
2017-06-14 11:00 | 558 | 552
2017-06-14 11:30 | 558 | 552
2017-06-14 12:00 | 567 | 561
2017-06-14 12:30 | 566 | 560
2017-06-14 13:00 | 575 | 570
2017-06-14 13:30 | 576 | 570
2017-06-14 14:00 | 582 | 576
2017-06-14 14:30 | 590 | 584
2017-06-14 15:00 | 592 | 585
2017-06-14 15:30 | 595 | 588
2017-06-14 16:00 | 602 | 595
2017-06-14 16:30 | 610 | 605
2017-06-14 17:00 | 623 | 619
2017-06-14 17:30 | 644 | 641
2017-06-14 18:00 | 656 | 651
2017-06-14 18:30 | 644 | 636
2017-06-14 19:00 | 641 | 632
2017-06-14 19:30 | 618 | 611
2017-06-14 20:00 | 614 | 607
2017-06-14 20:30 | 619 | 611
2017-06-14 21:00 | 590 | 587
2017-06-14 21:30 | 568 | 566
2017-06-14 22:00 | 547 | 545
2017-06-14 22:30 | 525 | 522
2017-06-14 23:00 | 506 | 503
2017-06-14 23:30 | 490 | 487
2017-06-15 | 463 | 459
2017-06-15 00:30 | 427 | 423
2017-06-15 01:00 | 407 | 403
2017-06-15 01:30 | 394 | 390
2017-06-15 02:00 | 390 | 385
2017-06-15 02:30 | 389 | 384
2017-06-15 03:00 | 384 | 379
2017-06-15 03:30 | 387 | 381
2017-06-15 04:00 | 395 | 389
2017-06-15 04:30 | 405 | 400
2017-06-15 05:00 | 413 | 408
2017-06-15 05:30 | 429 | 426
2017-06-15 06:00 | 456 | 455
2017-06-15 06:30 | 510 | 509
2017-06-15 07:00 | 546 | 544
2017-06-15 07:30 | 578 | 577
2017-06-15 08:00 | 585 | 584
2017-06-15 08:30 | 573 | 572
2017-06-15 09:00 | 558 | 557
2017-06-15 09:30 | 544 | 542
2017-06-15 10:00 | 522 | 521
2017-06-15 10:30 | 512 | 511
2017-06-15 11:00 | 520 | 519
2017-06-15 11:30 | 532 | 531
2017-06-15 12:00 | 516 | 515
2017-06-15 12:30 | 513 | 512
2017-06-15 13:00 | 510 | 510
2017-06-15 13:30 | 513 | 512
2017-06-15 14:00 | 522 | 522
2017-06-15 14:30 | 532 | 532
2017-06-15 15:00 | 536 | 535
2017-06-15 15:30 | 543 | 542
2017-06-15 16:00 | 557 | 556
2017-06-15 16:30 | 563 | 562
2017-06-15 17:00 | 578 | 577
2017-06-15 17:30 | 600 | 599
2017-06-15 18:00 | 612 | 611
2017-06-15 18:30 | 604 | 602
2017-06-15 19:00 | 604 | 601
2017-06-15 19:30 | 589 | 587
2017-06-15 20:00 | 583 | 582
2017-06-15 20:30 | 588 | 587
2017-06-15 21:00 | 571 | 570
2017-06-15 21:30 | 543 | 542
2017-06-15 22:00 | 524 | 523
2017-06-15 22:30 | 499 | 496
2017-06-15 23:00 | 481 | 479
2017-06-15 23:30 | 462 | 460
2017-06-16 | 434 | 431
2017-06-16 00:30 | 399 | 395
2017-06-16 01:00 | 386 | 381
2017-06-16 01:30 | 377 | 373
2017-06-16 02:00 | 373 | 368
2017-06-16 02:30 | 371 | 366
2017-06-16 03:00 | 368 | 364
2017-06-16 03:30 | 369 | 364
2017-06-16 04:00 | 371 | 366
2017-06-16 04:30 | 363 | 359
2017-06-16 05:00 | 372 | 369
2017-06-16 05:30 | 386 | 384
2017-06-16 06:00 | 407 | 407
2017-06-16 06:30 | 467 | 466
2017-06-16 07:00 | 515 | 514
2017-06-16 07:30 | 553 | 553
2017-06-16 08:00 | 574 | 572
2017-06-16 08:30 | 562 | 559
2017-06-16 09:00 | 535 | 533
2017-06-16 09:30 | 527 | 525
2017-06-16 10:00 | 527 | 524
2017-06-16 10:30 | 521 | 519
2017-06-16 11:00 | 519 | 518
2017-06-16 11:30 | 514 | 512
2017-06-16 12:00 | 513 | 511
2017-06-16 12:30 | 517 | 515
2017-06-16 13:00 | 512 | 510
2017-06-16 13:30 | 494 | 493
2017-06-16 14:00 | 499 | 498
2017-06-16 14:30 | 520 | 519
2017-06-16 15:00 | 524 | 523
2017-06-16 15:30 | 524 | 522
2017-06-16 16:00 | 531 | 530
2017-06-16 16:30 | 546 | 545
2017-06-16 17:00 | 553 | 552
2017-06-16 17:30 | 564 | 564
2017-06-16 18:00 | 561 | 560
2017-06-16 18:30 | 550 | 548
2017-06-16 19:00 | 543 | 541
2017-06-16 19:30 | 532 | 530
2017-06-16 20:00 | 530 | 528
2017-06-16 20:30 | 533 | 531
2017-06-16 21:00 | 508 | 507
2017-06-16 21:30 | 500 | 499
2017-06-16 22:00 | 485 | 484
2017-06-16 22:30 | 472 | 470
2017-06-16 23:00 | 459 | 457
2017-06-16 23:30 | 445 | 442
2017-06-17 | 405 | 404
2017-06-17 00:30 | 372 | 369
2017-06-17 01:00 | 357 | 354
2017-06-17 01:30 | 348 | 344
2017-06-17 02:00 | 342 | 337
2017-06-17 02:30 | 336 | 331
2017-06-17 03:00 | 334 | 328
2017-06-17 03:30 | 347 | 341
2017-06-17 04:00 | 351 | 345
2017-06-17 04:30 | 348 | 342
2017-06-17 05:00 | 353 | 347
2017-06-17 05:30 | 361 | 356
2017-06-17 06:00 | 368 | 363
2017-06-17 06:30 | 380 | 377
2017-06-17 07:00 | 392 | 389
2017-06-17 07:30 | 413 | 410
2017-06-17 08:00 | 425 | 424
2017-06-17 08:30 | 439 | 438
2017-06-17 09:00 | 441 | 440
2017-06-17 09:30 | 441 | 441
2017-06-17 10:00 | 434 | 434
2017-06-17 10:30 | 432 | 432
2017-06-17 11:00 | 440 | 440
2017-06-17 11:30 | 447 | 447
2017-06-17 12:00 | 442 | 442
2017-06-17 12:30 | 425 | 425
2017-06-17 13:00 | 428 | 428
2017-06-17 13:30 | 417 | 416
2017-06-17 14:00 | 420 | 419
2017-06-17 14:30 | 429 | 429
2017-06-17 15:00 | 433 | 433
2017-06-17 15:30 | 439 | 439
2017-06-17 16:00 | 446 | 445
2017-06-17 16:30 | 457 | 457
2017-06-17 17:00 | 478 | 478
2017-06-17 17:30 | 493 | 492
2017-06-17 18:00 | 499 | 499
2017-06-17 18:30 | 494 | 493
2017-06-17 19:00 | 483 | 482
2017-06-17 19:30 | 471 | 470
2017-06-17 20:00 | 465 | 465
2017-06-17 20:30 | 464 | 464
2017-06-17 21:00 | 449 | 449
2017-06-17 21:30 | 437 | 436
2017-06-17 22:00 | 430 | 429
2017-06-17 22:30 | 430 | 429
2017-06-17 23:00 | 424 | 423
2017-06-17 23:30 | 413 | 412
2017-06-18 | 381 | 378
2017-06-18 00:30 | 359 | 355
2017-06-18 01:00 | 352 | 347
2017-06-18 01:30 | 342 | 337
2017-06-18 02:00 | 345 | 339
2017-06-18 02:30 | 340 | 333
2017-06-18 03:00 | 337 | 330
2017-06-18 03:30 | 336 | 329
2017-06-18 04:00 | 341 | 333
2017-06-18 04:30 | 347 | 340
2017-06-18 05:00 | 347 | 340
2017-06-18 05:30 | 346 | 339
2017-06-18 06:00 | 349 | 343
2017-06-18 06:30 | 355 | 350
2017-06-18 07:00 | 363 | 357
2017-06-18 07:30 | 386 | 381
2017-06-18 08:00 | 394 | 390
2017-06-18 08:30 | 403 | 399
2017-06-18 09:00 | 402 | 399
2017-06-18 09:30 | 401 | 398
2017-06-18 10:00 | 397 | 394
2017-06-18 10:30 | 387 | 385
2017-06-18 11:00 | 381 | 378
2017-06-18 11:30 | 378 | 376
2017-06-18 12:00 | 373 | 370
2017-06-18 12:30 | 369 | 367
2017-06-18 13:00 | 374 | 372
2017-06-18 13:30 | 377 | 375
2017-06-18 14:00 | 382 | 379
2017-06-18 14:30 | 393 | 390
2017-06-18 15:00 | 401 | 398
2017-06-18 15:30 | 403 | 401
2017-06-18 16:00 | 412 | 411
2017-06-18 16:30 | 428 | 426
2017-06-18 17:00 | 461 | 459
2017-06-18 17:30 | 491 | 490
2017-06-18 18:00 | 511 | 509
2017-06-18 18:30 | 513 | 511
2017-06-18 19:00 | 500 | 497
2017-06-18 19:30 | 488 | 485
2017-06-18 20:00 | 482 | 479
2017-06-18 20:30 | 478 | 476
2017-06-18 21:00 | 459 | 458
2017-06-18 21:30 | 445 | 444
2017-06-18 22:00 | 435 | 434
2017-06-18 22:30 | 429 | 428
2017-06-18 23:00 | 423 | 421
2017-06-18 23:30 | 409 | 407
2017-06-19 | 380 | 377
2017-06-19 00:30 | 362 | 357
2017-06-19 01:00 | 352 | 347
2017-06-19 01:30 | 347 | 341
2017-06-19 02:00 | 343 | 337
2017-06-19 02:30 | 342 | 336
2017-06-19 03:00 | 339 | 332
2017-06-19 03:30 | 345 | 338
2017-06-19 04:00 | 349 | 342
2017-06-19 04:30 | 357 | 351
2017-06-19 05:00 | 373 | 368
2017-06-19 05:30 | 390 | 386
2017-06-19 06:00 | 409 | 406
2017-06-19 06:30 | 450 | 449
2017-06-19 07:00 | 494 | 492
2017-06-19 07:30 | 527 | 525
2017-06-19 08:00 | 539 | 538
2017-06-19 08:30 | 531 | 530
2017-06-19 09:00 | 503 | 501
2017-06-19 09:30 | 496 | 495
2017-06-19 10:00 | 481 | 479
2017-06-19 10:30 | 465 | 464
2017-06-19 11:00 | 467 | 465
2017-06-19 11:30 | 472 | 470
2017-06-19 12:00 | 492 | 491
2017-06-19 12:30 | 499 | 498
2017-06-19 13:00 | 488 | 487
2017-06-19 13:30 | 492 | 491
2017-06-19 14:00 | 490 | 488
2017-06-19 14:30 | 504 | 502
2017-06-19 15:00 | 497 | 496
2017-06-19 15:30 | 508 | 506
2017-06-19 16:00 | 521 | 519
2017-06-19 16:30 | 538 | 537
2017-06-19 17:00 | 558 | 556
2017-06-19 17:30 | 580 | 578
2017-06-19 18:00 | 591 | 588
2017-06-19 18:30 | 582 | 579
2017-06-19 19:00 | 573 | 570
2017-06-19 19:30 | 562 | 559
2017-06-19 20:00 | 550 | 549
2017-06-19 20:30 | 549 | 547
2017-06-19 21:00 | 526 | 525
2017-06-19 21:30 | 506 | 504
2017-06-19 22:00 | 483 | 480
2017-06-19 22:30 | 473 | 470
2017-06-19 23:00 | 457 | 454
2017-06-19 23:30 | 433 | 430
2017-06-20 | 404 | 401
2017-06-20 00:30 | 384 | 381
2017-06-20 01:00 | 374 | 370
2017-06-20 01:30 | 366 | 362
2017-06-20 02:00 | 364 | 359
2017-06-20 02:30 | 361 | 356
2017-06-20 03:00 | 358 | 353
2017-06-20 03:30 | 356 | 350
2017-06-20 04:00 | 365 | 360
2017-06-20 04:30 | 372 | 367
2017-06-20 05:00 | 378 | 374
2017-06-20 05:30 | 393 | 391
2017-06-20 06:00 | 415 | 412
2017-06-20 06:30 | 450 | 449
2017-06-20 07:00 | 487 | 486
2017-06-20 07:30 | 524 | 523
2017-06-20 08:00 | 530 | 529
2017-06-20 08:30 | 521 | 520
2017-06-20 09:00 | 516 | 515
2017-06-20 09:30 | 514 | 513
2017-06-20 10:00 | 492 | 491
2017-06-20 10:30 | 490 | 489
2017-06-20 11:00 | 496 | 495
2017-06-20 11:30 | 479 | 479
2017-06-20 12:00 | 487 | 487
2017-06-20 12:30 | 473 | 472
2017-06-20 13:00 | 465 | 464
2017-06-20 13:30 | 477 | 476
2017-06-20 14:00 | 486 | 485
2017-06-20 14:30 | 495 | 494
2017-06-20 15:00 | 500 | 498
2017-06-20 15:30 | 506 | 505
2017-06-20 16:00 | 521 | 519
2017-06-20 16:30 | 533 | 532
2017-06-20 17:00 | 566 | 565
2017-06-20 17:30 | 597 | 595
2017-06-20 18:00 | 603 | 602
2017-06-20 18:30 | 595 | 593
2017-06-20 19:00 | 591 | 587
2017-06-20 19:30 | 581 | 578
2017-06-20 20:00 | 571 | 569
2017-06-20 20:30 | 566 | 565
2017-06-20 21:00 | 538 | 536
2017-06-20 21:30 | 506 | 503
2017-06-20 22:00 | 498 | 494
2017-06-20 22:30 | 482 | 479
2017-06-20 23:00 | 461 | 459
2017-06-20 23:30 | 437 | 435
2017-06-21 | 415 | 412
2017-06-21 00:30 | 394 | 390
2017-06-21 01:00 | 387 | 382
2017-06-21 01:30 | 377 | 371
2017-06-21 02:00 | 375 | 368
2017-06-21 02:30 | 377 | 370
2017-06-21 03:00 | 373 | 365
2017-06-21 03:30 | 378 | 371
2017-06-21 04:00 | 379 | 372
2017-06-21 04:30 | 392 | 385
2017-06-21 05:00 | 399 | 392
2017-06-21 05:30 | 401 | 397
2017-06-21 06:00 | 421 | 418
2017-06-21 06:30 | 474 | 472
2017-06-21 07:00 | 518 | 516
2017-06-21 07:30 | 552 | 551
2017-06-21 08:00 | 557 | 555
2017-06-21 08:30 | 541 | 539
2017-06-21 09:00 | 520 | 518
2017-06-21 09:30 | 499 | 497
2017-06-21 10:00 | 482 | 479
2017-06-21 10:30 | 477 | 474
2017-06-21 11:00 | 475 | 472
2017-06-21 11:30 | 470 | 466
2017-06-21 12:00 | 469 | 466
2017-06-21 12:30 | 471 | 468
2017-06-21 13:00 | 473 | 470
2017-06-21 13:30 | 472 | 469
2017-06-21 14:00 | 475 | 472
2017-06-21 14:30 | 483 | 480
2017-06-21 15:00 | 492 | 489
2017-06-21 15:30 | 503 | 500
2017-06-21 16:00 | 511 | 508
2017-06-21 16:30 | 522 | 519
2017-06-21 17:00 | 539 | 538
2017-06-21 17:30 | 560 | 560
2017-06-21 18:00 | 570 | 569
2017-06-21 18:30 | 563 | 561
2017-06-21 19:00 | 564 | 563
2017-06-21 19:30 | 555 | 554
2017-06-21 20:00 | 553 | 549
2017-06-21 20:30 | 549 | 546
2017-06-21 21:00 | 516 | 515
2017-06-21 21:30 | 499 | 498
2017-06-21 22:00 | 479 | 477
2017-06-21 22:30 | 469 | 467
2017-06-21 23:00 | 454 | 452
2017-06-21 23:30 | 431 | 429
2017-06-22 | 411 | 409
2017-06-22 00:30 | 396 | 394
2017-06-22 01:00 | 392 | 389
2017-06-22 01:30 | 382 | 378
2017-06-22 02:00 | 371 | 367
2017-06-22 02:30 | 366 | 362
2017-06-22 03:00 | 367 | 363
2017-06-22 03:30 | 366 | 361
2017-06-22 04:00 | 367 | 362
2017-06-22 04:30 | 369 | 364
2017-06-22 05:00 | 376 | 373
2017-06-22 05:30 | 382 | 380
2017-06-22 06:00 | 395 | 394
2017-06-22 06:30 | 448 | 448
2017-06-22 07:00 | 489 | 489
2017-06-22 07:30 | 505 | 505
2017-06-22 08:00 | 504 | 504
2017-06-22 08:30 | 501 | 500
2017-06-22 09:00 | 481 | 481
2017-06-22 09:30 | 468 | 468
2017-06-22 10:00 | 452 | 451
2017-06-22 10:30 | 438 | 438
2017-06-22 11:00 | 433 | 433
2017-06-22 11:30 | 427 | 427
2017-06-22 12:00 | 427 | 427
2017-06-22 12:30 | 436 | 436
2017-06-22 13:00 | 462 | 462
2017-06-22 13:30 | 469 | 469
2017-06-22 14:00 | 474 | 474
2017-06-22 14:30 | 482 | 482
2017-06-22 15:00 | 488 | 487
2017-06-22 15:30 | 494 | 494
2017-06-22 16:00 | 502 | 501
2017-06-22 16:30 | 514 | 513
2017-06-22 17:00 | 530 | 530
2017-06-22 17:30 | 555 | 555
2017-06-22 18:00 | 577 | 577
2017-06-22 18:30 | 576 | 575
2017-06-22 19:00 | 578 | 578
2017-06-22 19:30 | 568 | 567
2017-06-22 20:00 | 567 | 566
2017-06-22 20:30 | 565 | 563
2017-06-22 21:00 | 554 | 550
2017-06-22 21:30 | 528 | 526
2017-06-22 22:00 | 504 | 502
2017-06-22 22:30 | 485 | 483
2017-06-22 23:00 | 463 | 461
2017-06-22 23:30 | 447 | 444
2017-06-23 | 415 | 412
2017-06-23 00:30 | 396 | 394
2017-06-23 01:00 | 384 | 381
2017-06-23 01:30 | 371 | 368
2017-06-23 02:00 | 359 | 355
2017-06-23 02:30 | 355 | 350
2017-06-23 03:00 | 350 | 345
2017-06-23 03:30 | 357 | 351
2017-06-23 04:00 | 349 | 343
2017-06-23 04:30 | 367 | 362
2017-06-23 05:00 | 381 | 377
2017-06-23 05:30 | 398 | 395
2017-06-23 06:00 | 424 | 423
2017-06-23 06:30 | 471 | 469
2017-06-23 07:00 | 510 | 508
2017-06-23 07:30 | 547 | 546
2017-06-23 08:00 | 557 | 557
2017-06-23 08:30 | 550 | 549
2017-06-23 09:00 | 532 | 532
2017-06-23 09:30 | 519 | 519
2017-06-23 10:00 | 497 | 497
2017-06-23 10:30 | 480 | 480
2017-06-23 11:00 | 471 | 471
2017-06-23 11:30 | 469 | 469
2017-06-23 12:00 | 464 | 464
2017-06-23 12:30 | 453 | 453
2017-06-23 13:00 | 447 | 447
2017-06-23 13:30 | 451 | 451
2017-06-23 14:00 | 457 | 456
2017-06-23 14:30 | 467 | 467
2017-06-23 15:00 | 469 | 469
2017-06-23 15:30 | 475 | 475
2017-06-23 16:00 | 487 | 487
2017-06-23 16:30 | 497 | 496
2017-06-23 17:00 | 521 | 521
2017-06-23 17:30 | 538 | 537
2017-06-23 18:00 | 546 | 542
2017-06-23 18:30 | 536 | 531
2017-06-23 19:00 | 539 | 534
2017-06-23 19:30 | 535 | 530
2017-06-23 20:00 | 537 | 531
2017-06-23 20:30 | 538 | 532
2017-06-23 21:00 | 518 | 510
2017-06-23 21:30 | 495 | 493
2017-06-23 22:00 | 476 | 475
2017-06-23 22:30 | 465 | 464
2017-06-23 23:00 | 450 | 449
2017-06-23 23:30 | 434 | 432
2017-06-24 | 410 | 406
2017-06-24 00:30 | 388 | 382
2017-06-24 01:00 | 379 | 371
2017-06-24 01:30 | 364 | 353
2017-06-24 02:00 | 349 | 340
2017-06-24 02:30 | 343 | 334
2017-06-24 03:00 | 340 | 332
2017-06-24 03:30 | 344 | 336
2017-06-24 04:00 | 337 | 327
2017-06-24 04:30 | 350 | 341
2017-06-24 05:00 | 355 | 347
2017-06-24 05:30 | 364 | 357
2017-06-24 06:00 | 374 | 368
2017-06-24 06:30 | 389 | 384
2017-06-24 07:00 | 403 | 399
2017-06-24 07:30 | 430 | 427
2017-06-24 08:00 | 452 | 450
2017-06-24 08:30 | 461 | 460
2017-06-24 09:00 | 457 | 456
2017-06-24 09:30 | 451 | 450
2017-06-24 10:00 | 434 | 433
2017-06-24 10:30 | 420 | 419
2017-06-24 11:00 | 400 | 398
2017-06-24 11:30 | 383 | 381
2017-06-24 12:00 | 374 | 372
2017-06-24 12:30 | 367 | 365
2017-06-24 13:00 | 369 | 367
2017-06-24 13:30 | 370 | 368
2017-06-24 14:00 | 376 | 374
2017-06-24 14:30 | 387 | 385
2017-06-24 15:00 | 393 | 391
2017-06-24 15:30 | 400 | 399
2017-06-24 16:00 | 410 | 409
2017-06-24 16:30 | 433 | 432
2017-06-24 17:00 | 455 | 454
2017-06-24 17:30 | 478 | 478
2017-06-24 18:00 | 489 | 488
2017-06-24 18:30 | 486 | 485
2017-06-24 19:00 | 488 | 486
2017-06-24 19:30 | 479 | 476
2017-06-24 20:00 | 473 | 469
2017-06-24 20:30 | 471 | 468
2017-06-24 21:00 | 455 | 454
2017-06-24 21:30 | 446 | 445
2017-06-24 22:00 | 443 | 443
2017-06-24 22:30 | 440 | 439
2017-06-24 23:00 | 435 | 434
2017-06-24 23:30 | 423 | 422
2017-06-25 | 399 | 397
2017-06-25 00:30 | 383 | 380
2017-06-25 01:00 | 370 | 365
2017-06-25 01:30 | 351 | 346
2017-06-25 02:00 | 336 | 330
2017-06-25 02:30 | 332 | 325
2017-06-25 03:00 | 323 | 315
2017-06-25 03:30 | 324 | 316
2017-06-25 04:00 | 331 | 322
2017-06-25 04:30 | 330 | 320
2017-06-25 05:00 | 327 | 317
2017-06-25 05:30 | 336 | 327
2017-06-25 06:00 | 344 | 336
2017-06-25 06:30 | 355 | 348
2017-06-25 07:00 | 369 | 361
2017-06-25 07:30 | 384 | 378
2017-06-25 08:00 | 395 | 391
2017-06-25 08:30 | 408 | 404
2017-06-25 09:00 | 405 | 402
2017-06-25 09:30 | 400 | 396
2017-06-25 10:00 | 394 | 390
2017-06-25 10:30 | 380 | 377
2017-06-25 11:00 | 370 | 366
2017-06-25 11:30 | 366 | 362
2017-06-25 12:00 | 360 | 356
2017-06-25 12:30 | 352 | 348
2017-06-25 13:00 | 350 | 346
2017-06-25 13:30 | 347 | 343
2017-06-25 14:00 | 362 | 358
2017-06-25 14:30 | 373 | 370
2017-06-25 15:00 | 385 | 382
2017-06-25 15:30 | 391 | 388
2017-06-25 16:00 | 404 | 401
2017-06-25 16:30 | 419 | 417
2017-06-25 17:00 | 445 | 443
2017-06-25 17:30 | 468 | 466
2017-06-25 18:00 | 491 | 490
2017-06-25 18:30 | 498 | 497
2017-06-25 19:00 | 495 | 494
2017-06-25 19:30 | 487 | 486
2017-06-25 20:00 | 475 | 475
2017-06-25 20:30 | 472 | 472
2017-06-25 21:00 | 450 | 448
2017-06-25 21:30 | 439 | 437
2017-06-25 22:00 | 426 | 425
2017-06-25 22:30 | 416 | 415
2017-06-25 23:00 | 413 | 411
2017-06-25 23:30 | 398 | 396
2017-06-26 | 369 | 366
2017-06-26 00:30 | 352 | 348
2017-06-26 01:00 | 344 | 339
2017-06-26 01:30 | 334 | 327
2017-06-26 02:00 | 323 | 315
2017-06-26 02:30 | 319 | 312
2017-06-26 03:00 | 315 | 307
2017-06-26 03:30 | 319 | 312
2017-06-26 04:00 | 326 | 319
2017-06-26 04:30 | 333 | 326
2017-06-26 05:00 | 342 | 336
2017-06-26 05:30 | 358 | 355
2017-06-26 06:00 | 385 | 383
2017-06-26 06:30 | 442 | 439
2017-06-26 07:00 | 485 | 482
2017-06-26 07:30 | 511 | 509
2017-06-26 08:00 | 517 | 515
2017-06-26 08:30 | 511 | 509
2017-06-26 09:00 | 496 | 494
2017-06-26 09:30 | 486 | 484
2017-06-26 10:00 | 467 | 465
2017-06-26 10:30 | 455 | 453
2017-06-26 11:00 | 446 | 444
2017-06-26 11:30 | 454 | 453
2017-06-26 12:00 | 463 | 462
2017-06-26 12:30 | 453 | 452
2017-06-26 13:00 | 434 | 434
2017-06-26 13:30 | 437 | 437
2017-06-26 14:00 | 444 | 444
2017-06-26 14:30 | 453 | 452
2017-06-26 15:00 | 467 | 466
2017-06-26 15:30 | 474 | 472
2017-06-26 16:00 | 482 | 480
2017-06-26 16:30 | 494 | 493
2017-06-26 17:00 | 518 | 516
2017-06-26 17:30 | 538 | 537
2017-06-26 18:00 | 556 | 556
2017-06-26 18:30 | 545 | 544
2017-06-26 19:00 | 540 | 538
2017-06-26 19:30 | 526 | 525
2017-06-26 20:00 | 521 | 521
2017-06-26 20:30 | 525 | 523
2017-06-26 21:00 | 507 | 505
2017-06-26 21:30 | 487 | 486
2017-06-26 22:00 | 470 | 469
2017-06-26 22:30 | 464 | 462
2017-06-26 23:00 | 455 | 452
2017-06-26 23:30 | 440 | 437
2017-06-27 | 408 | 405
2017-06-27 00:30 | 386 | 383
2017-06-27 01:00 | 378 | 373
2017-06-27 01:30 | 365 | 360
2017-06-27 02:00 | 356 | 351
2017-06-27 02:30 | 351 | 345
2017-06-27 03:00 | 344 | 339
2017-06-27 03:30 | 347 | 341
2017-06-27 04:00 | 354 | 348
2017-06-27 04:30 | 358 | 353
2017-06-27 05:00 | 371 | 367
2017-06-27 05:30 | 390 | 388
2017-06-27 06:00 | 415 | 413
2017-06-27 06:30 | 467 | 465
2017-06-27 07:00 | 507 | 505
2017-06-27 07:30 | 525 | 518
2017-06-27 08:00 | 535 | 527
2017-06-27 08:30 | 544 | 536
2017-06-27 09:00 | 543 | 536
2017-06-27 09:30 | 534 | 528
2017-06-27 10:00 | 528 | 522
2017-06-27 10:30 | 509 | 503
2017-06-27 11:00 | 498 | 493
2017-06-27 11:30 | 489 | 485
2017-06-27 12:00 | 479 | 473
2017-06-27 12:30 | 482 | 476
2017-06-27 13:00 | 487 | 481
2017-06-27 13:30 | 479 | 472
2017-06-27 14:00 | 489 | 483
2017-06-27 14:30 | 500 | 494
2017-06-27 15:00 | 506 | 499
2017-06-27 15:30 | 515 | 508
2017-06-27 16:00 | 520 | 513
2017-06-27 16:30 | 529 | 522
2017-06-27 17:00 | 556 | 548
2017-06-27 17:30 | 572 | 566
2017-06-27 18:00 | 593 | 584
2017-06-27 18:30 | 581 | 570
2017-06-27 19:00 | 578 | 566
2017-06-27 19:30 | 568 | 556
2017-06-27 20:00 | 554 | 547
2017-06-27 20:30 | 546 | 539
2017-06-27 21:00 | 519 | 514
2017-06-27 21:30 | 508 | 504
2017-06-27 22:00 | 494 | 488
2017-06-27 22:30 | 470 | 470
2017-06-27 23:00 | 461 | 461
2017-06-27 23:30 | 433 | 432
2017-06-28 | 400 | 399
2017-06-28 00:30 | 381 | 379
2017-06-28 01:00 | 370 | 367
2017-06-28 01:30 | 368 | 363
2017-06-28 02:00 | 361 | 356
2017-06-28 02:30 | 353 | 349
2017-06-28 03:00 | 346 | 341
2017-06-28 03:30 | 350 | 345
2017-06-28 04:00 | 356 | 351
2017-06-28 04:30 | 360 | 356
2017-06-28 05:00 | 368 | 364
2017-06-28 05:30 | 390 | 387
2017-06-28 06:00 | 412 | 411
2017-06-28 06:30 | 465 | 463
2017-06-28 07:00 | 511 | 510
2017-06-28 07:30 | 538 | 537
2017-06-28 08:00 | 545 | 542
2017-06-28 08:30 | 544 | 542
2017-06-28 09:00 | 528 | 526
2017-06-28 09:30 | 518 | 516
2017-06-28 10:00 | 502 | 500
2017-06-28 10:30 | 492 | 490
2017-06-28 11:00 | 485 | 483
2017-06-28 11:30 | 482 | 481
2017-06-28 12:00 | 475 | 474
2017-06-28 12:30 | 473 | 473
2017-06-28 13:00 | 480 | 480
2017-06-28 13:30 | 484 | 483
2017-06-28 14:00 | 490 | 489
2017-06-28 14:30 | 494 | 494
2017-06-28 15:00 | 500 | 500
2017-06-28 15:30 | 502 | 501
2017-06-28 16:00 | 506 | 505
2017-06-28 16:30 | 521 | 520
2017-06-28 17:00 | 543 | 542
2017-06-28 17:30 | 570 | 567
2017-06-28 18:00 | 584 | 580
2017-06-28 18:30 | 568 | 566
2017-06-28 19:00 | 562 | 560
2017-06-28 19:30 | 553 | 551
2017-06-28 20:00 | 541 | 539
2017-06-28 20:30 | 532 | 529
2017-06-28 21:00 | 511 | 510
2017-06-28 21:30 | 496 | 494
2017-06-28 22:00 | 474 | 472
2017-06-28 22:30 | 461 | 460
2017-06-28 23:00 | 457 | 456
2017-06-28 23:30 | 439 | 439
2017-06-29 | 410 | 409
2017-06-29 00:30 | 385 | 383
2017-06-29 01:00 | 368 | 365
2017-06-29 01:30 | 355 | 351
2017-06-29 02:00 | 345 | 341
2017-06-29 02:30 | 343 | 338
2017-06-29 03:00 | 334 | 329
2017-06-29 03:30 | 334 | 329
2017-06-29 04:00 | 337 | 332
2017-06-29 04:30 | 351 | 347
2017-06-29 05:00 | 360 | 356
2017-06-29 05:30 | 384 | 381
2017-06-29 06:00 | 412 | 410
2017-06-29 06:30 | 455 | 453
2017-06-29 07:00 | 487 | 482
2017-06-29 07:30 | 513 | 506
2017-06-29 08:00 | 526 | 519
2017-06-29 08:30 | 527 | 520
2017-06-29 09:00 | 519 | 510
2017-06-29 09:30 | 512 | 503
2017-06-29 10:00 | 497 | 488
2017-06-29 10:30 | 489 | 480
2017-06-29 11:00 | 477 | 469
2017-06-29 11:30 | 465 | 457
2017-06-29 12:00 | 463 | 455
2017-06-29 12:30 | 463 | 455
2017-06-29 13:00 | 459 | 452
2017-06-29 13:30 | 463 | 457
2017-06-29 14:00 | 472 | 466
2017-06-29 14:30 | 485 | 478
2017-06-29 15:00 | 490 | 484
2017-06-29 15:30 | 496 | 489
2017-06-29 16:00 | 503 | 497
2017-06-29 16:30 | 512 | 506
2017-06-29 17:00 | 532 | 526
2017-06-29 17:30 | 557 | 554
2017-06-29 18:00 | 571 | 567
2017-06-29 18:30 | 564 | 559
2017-06-29 19:00 | 550 | 547
2017-06-29 19:30 | 541 | 538
2017-06-29 20:00 | 531 | 527
2017-06-29 20:30 | 521 | 514
2017-06-29 21:00 | 510 | 501
2017-06-29 21:30 | 489 | 483
2017-06-29 22:00 | 470 | 469
2017-06-29 22:30 | 458 | 458
2017-06-29 23:00 | 447 | 446
2017-06-29 23:30 | 426 | 425
2017-06-30 | 399 | 397
2017-06-30 00:30 | 380 | 378
2017-06-30 01:00 | 364 | 361
2017-06-30 01:30 | 352 | 348
2017-06-30 02:00 | 338 | 334
2017-06-30 02:30 | 337 | 332
2017-06-30 03:00 | 329 | 324
2017-06-30 03:30 | 328 | 323
2017-06-30 04:00 | 335 | 330
2017-06-30 04:30 | 341 | 336
2017-06-30 05:00 | 354 | 350
2017-06-30 05:30 | 371 | 369
2017-06-30 06:00 | 397 | 395
2017-06-30 06:30 | 445 | 442
2017-06-30 07:00 | 475 | 472
2017-06-30 07:30 | 503 | 500
2017-06-30 08:00 | 523 | 519
2017-06-30 08:30 | 526 | 523
2017-06-30 09:00 | 471 | 468
2017-06-30 09:30 | 455 | 453
2017-06-30 10:00 | 435 | 432
2017-06-30 10:30 | 425 | 422
2017-06-30 11:00 | 418 | 415
2017-06-30 11:30 | 412 | 409
2017-06-30 12:00 | 409 | 407
2017-06-30 12:30 | 411 | 408
2017-06-30 13:00 | 414 | 412
2017-06-30 13:30 | 419 | 416
2017-06-30 14:00 | 425 | 423
2017-06-30 14:30 | 430 | 428
2017-06-30 15:00 | 440 | 438
2017-06-30 15:30 | 489 | 486
2017-06-30 16:00 | 499 | 496
2017-06-30 16:30 | 513 | 511
2017-06-30 17:00 | 540 | 537
2017-06-30 17:30 | 557 | 555
2017-06-30 18:00 | 578 | 575
2017-06-30 18:30 | 572 | 568
2017-06-30 19:00 | 568 | 564
2017-06-30 19:30 | 553 | 549
2017-06-30 20:00 | 540 | 536
2017-06-30 20:30 | 547 | 543
2017-06-30 21:00 | 525 | 522
2017-06-30 21:30 | 511 | 508
2017-06-30 22:00 | 495 | 494
2017-06-30 22:30 | 484 | 484
2017-06-30 23:00 | 477 | 476
2017-06-30 23:30 | 457 | 456
2017-07-01 | 435 | 434
2017-07-01 00:30 | 401 | 399
2017-07-01 01:00 | 383 | 379
2017-07-01 01:30 | 376 | 372
2017-07-01 02:00 | 370 | 365
2017-07-01 02:30 | 353 | 348
2017-07-01 03:00 | 351 | 345
2017-07-01 03:30 | 357 | 351
2017-07-01 04:00 | 362 | 356
2017-07-01 04:30 | 358 | 352
2017-07-01 05:00 | 361 | 356
2017-07-01 05:30 | 364 | 360
2017-07-01 06:00 | 380 | 376
2017-07-01 06:30 | 409 | 406
2017-07-01 07:00 | 435 | 433
2017-07-01 07:30 | 461 | 458
2017-07-01 08:00 | 490 | 487
2017-07-01 08:30 | 495 | 493
2017-07-01 09:00 | 497 | 494
2017-07-01 09:30 | 485 | 482
2017-07-01 10:00 | 466 | 463
2017-07-01 10:30 | 448 | 445
2017-07-01 11:00 | 426 | 424
2017-07-01 11:30 | 414 | 412
2017-07-01 12:00 | 412 | 410
2017-07-01 12:30 | 410 | 408
2017-07-01 13:00 | 408 | 406
2017-07-01 13:30 | 411 | 409
2017-07-01 14:00 | 418 | 416
2017-07-01 14:30 | 430 | 428
2017-07-01 15:00 | 426 | 425
2017-07-01 15:30 | 422 | 420
2017-07-01 16:00 | 437 | 435
2017-07-01 16:30 | 465 | 464
2017-07-01 17:00 | 507 | 506
2017-07-01 17:30 | 539 | 538
2017-07-01 18:00 | 564 | 561
2017-07-01 18:30 | 563 | 560
2017-07-01 19:00 | 561 | 558
2017-07-01 19:30 | 546 | 544
2017-07-01 20:00 | 547 | 545
2017-07-01 20:30 | 563 | 561
2017-07-01 21:00 | 546 | 542
2017-07-01 21:30 | 530 | 527
2017-07-01 22:00 | 517 | 513
2017-07-01 22:30 | 502 | 497
2017-07-01 23:00 | 480 | 477
2017-07-01 23:30 | 460 | 457
2017-07-02 | 429 | 425
2017-07-02 00:30 | 402 | 399
2017-07-02 01:00 | 383 | 379
2017-07-02 01:30 | 366 | 361
2017-07-02 02:00 | 354 | 349
2017-07-02 02:30 | 351 | 346
2017-07-02 03:00 | 348 | 343
2017-07-02 03:30 | 353 | 347
2017-07-02 04:00 | 363 | 357
2017-07-02 04:30 | 368 | 362
2017-07-02 05:00 | 375 | 370
2017-07-02 05:30 | 378 | 373
2017-07-02 06:00 | 378 | 374
2017-07-02 06:30 | 406 | 402
2017-07-02 07:00 | 426 | 423
2017-07-02 07:30 | 452 | 450
2017-07-02 08:00 | 497 | 493
2017-07-02 08:30 | 522 | 518
2017-07-02 09:00 | 509 | 505
2017-07-02 09:30 | 489 | 485
2017-07-02 10:00 | 476 | 472
2017-07-02 10:30 | 451 | 448
2017-07-02 11:00 | 438 | 436
2017-07-02 11:30 | 391 | 389
2017-07-02 12:00 | 367 | 365
2017-07-02 12:30 | 358 | 356
2017-07-02 13:00 | 358 | 356
2017-07-02 13:30 | 367 | 365
2017-07-02 14:00 | 383 | 381
2017-07-02 14:30 | 398 | 397
2017-07-02 15:00 | 404 | 402
2017-07-02 15:30 | 416 | 414
2017-07-02 16:00 | 438 | 437
2017-07-02 16:30 | 464 | 464
2017-07-02 17:00 | 489 | 488
2017-07-02 17:30 | 515 | 514
2017-07-02 18:00 | 547 | 545
2017-07-02 18:30 | 548 | 545
2017-07-02 19:00 | 551 | 547
2017-07-02 19:30 | 536 | 532
2017-07-02 20:00 | 530 | 528
2017-07-02 20:30 | 544 | 542
2017-07-02 21:00 | 545 | 542
2017-07-02 21:30 | 521 | 517
2017-07-02 22:00 | 501 | 497
2017-07-02 22:30 | 480 | 476
2017-07-02 23:00 | 462 | 457
2017-07-02 23:30 | 437 | 433
2017-07-03 | 405 | 403
2017-07-03 00:30 | 388 | 385
2017-07-03 01:00 | 377 | 374
2017-07-03 01:30 | 369 | 365
2017-07-03 02:00 | 362 | 357
2017-07-03 02:30 | 378 | 373
2017-07-03 03:00 | 382 | 377
2017-07-03 03:30 | 384 | 378
2017-07-03 04:00 | 387 | 382
2017-07-03 04:30 | 400 | 396
2017-07-03 05:00 | 418 | 414
2017-07-03 05:30 | 434 | 432
2017-07-03 06:00 | 445 | 444
2017-07-03 06:30 | 501 | 500
2017-07-03 07:00 | 550 | 548
2017-07-03 07:30 | 591 | 590
2017-07-03 08:00 | 608 | 607
2017-07-03 08:30 | 613 | 610
2017-07-03 09:00 | 602 | 600
2017-07-03 09:30 | 583 | 580
2017-07-03 10:00 | 561 | 557
2017-07-03 10:30 | 547 | 542
2017-07-03 11:00 | 527 | 521
2017-07-03 11:30 | 513 | 509
2017-07-03 12:00 | 508 | 504
2017-07-03 12:30 | 509 | 505
2017-07-03 13:00 | 522 | 518
2017-07-03 13:30 | 530 | 526
2017-07-03 14:00 | 543 | 539
2017-07-03 14:30 | 543 | 540
2017-07-03 15:00 | 540 | 536
2017-07-03 15:30 | 539 | 535
2017-07-03 16:00 | 546 | 543
2017-07-03 16:30 | 566 | 564
2017-07-03 17:00 | 581 | 580
2017-07-03 17:30 | 591 | 590
2017-07-03 18:00 | 607 | 606
2017-07-03 18:30 | 600 | 597
2017-07-03 19:00 | 595 | 592
2017-07-03 19:30 | 578 | 576
2017-07-03 20:00 | 580 | 577
2017-07-03 20:30 | 588 | 584
2017-07-03 21:00 | 575 | 570
2017-07-03 21:30 | 553 | 547
2017-07-03 22:00 | 530 | 525
2017-07-03 22:30 | 504 | 501
2017-07-03 23:00 | 474 | 471
2017-07-03 23:30 | 442 | 439
2017-07-04 | 411 | 409
2017-07-04 00:30 | 392 | 389
2017-07-04 01:00 | 368 | 365
2017-07-04 01:30 | 352 | 349
2017-07-04 02:00 | 343 | 339
2017-07-04 02:30 | 336 | 331
2017-07-04 03:00 | 339 | 334
2017-07-04 03:30 | 343 | 338
2017-07-04 04:00 | 338 | 333
2017-07-04 04:30 | 359 | 355
2017-07-04 05:00 | 381 | 378
2017-07-04 05:30 | 398 | 396
2017-07-04 06:00 | 417 | 416
2017-07-04 06:30 | 468 | 467
2017-07-04 07:00 | 504 | 502
2017-07-04 07:30 | 535 | 532
2017-07-04 08:00 | 551 | 548
2017-07-04 08:30 | 551 | 547
2017-07-04 09:00 | 538 | 534
2017-07-04 09:30 | 514 | 510
2017-07-04 10:00 | 494 | 490
2017-07-04 10:30 | 473 | 469
2017-07-04 11:00 | 470 | 467
2017-07-04 11:30 | 466 | 463
2017-07-04 12:00 | 461 | 458
2017-07-04 12:30 | 461 | 459
2017-07-04 13:00 | 463 | 460
2017-07-04 13:30 | 469 | 466
2017-07-04 14:00 | 474 | 472
2017-07-04 14:30 | 489 | 487
2017-07-04 15:00 | 496 | 494
2017-07-04 15:30 | 511 | 509
2017-07-04 16:00 | 520 | 517
2017-07-04 16:30 | 540 | 537
2017-07-04 17:00 | 562 | 559
2017-07-04 17:30 | 590 | 588
2017-07-04 18:00 | 619 | 617
2017-07-04 18:30 | 611 | 609
2017-07-04 19:00 | 600 | 598
2017-07-04 19:30 | 587 | 584
2017-07-04 20:00 | 580 | 578
2017-07-04 20:30 | 561 | 560
2017-07-04 21:00 | 539 | 539
2017-07-04 21:30 | 525 | 523
2017-07-04 22:00 | 507 | 504
2017-07-04 22:30 | 495 | 492
2017-07-04 23:00 | 474 | 471
2017-07-04 23:30 | 451 | 449
2017-07-05 | 422 | 419
2017-07-05 00:30 | 399 | 397
2017-07-05 01:00 | 387 | 384
2017-07-05 01:30 | 371 | 367
2017-07-05 02:00 | 360 | 356
2017-07-05 02:30 | 358 | 353
2017-07-05 03:00 | 370 | 366
2017-07-05 03:30 | 363 | 359
2017-07-05 04:00 | 362 | 357
2017-07-05 04:30 | 373 | 368
2017-07-05 05:00 | 383 | 379
2017-07-05 05:30 | 399 | 397
2017-07-05 06:00 | 420 | 419
2017-07-05 06:30 | 466 | 466
2017-07-05 07:00 | 507 | 507
2017-07-05 07:30 | 540 | 540
2017-07-05 08:00 | 546 | 546
2017-07-05 08:30 | 486 | 486
2017-07-05 09:00 | 471 | 471
2017-07-05 09:30 | 468 | 467
2017-07-05 10:00 | 459 | 458
2017-07-05 10:30 | 448 | 447
2017-07-05 11:00 | 438 | 437
2017-07-05 11:30 | 432 | 431
2017-07-05 12:00 | 428 | 427
2017-07-05 12:30 | 430 | 430
2017-07-05 13:00 | 431 | 430
2017-07-05 13:30 | 440 | 439
2017-07-05 14:00 | 449 | 447
2017-07-05 14:30 | 460 | 458
2017-07-05 15:00 | 469 | 467
2017-07-05 15:30 | 478 | 476
2017-07-05 16:00 | 489 | 488
2017-07-05 16:30 | 503 | 501
2017-07-05 17:00 | 577 | 576
2017-07-05 17:30 | 621 | 620
2017-07-05 18:00 | 617 | 616
2017-07-05 18:30 | 602 | 600
2017-07-05 19:00 | 601 | 599
2017-07-05 19:30 | 589 | 587
2017-07-05 20:00 | 584 | 582
2017-07-05 20:30 | 579 | 577
2017-07-05 21:00 | 553 | 551
2017-07-05 21:30 | 529 | 526
2017-07-05 22:00 | 510 | 508
2017-07-05 22:30 | 488 | 485
2017-07-05 23:00 | 472 | 471
2017-07-05 23:30 | 458 | 458
2017-07-06 | 438 | 437
2017-07-06 00:30 | 413 | 411
2017-07-06 01:00 | 392 | 388
2017-07-06 01:30 | 379 | 374
2017-07-06 02:00 | 376 | 371
2017-07-06 02:30 | 382 | 377
2017-07-06 03:00 | 378 | 373
2017-07-06 03:30 | 377 | 372
2017-07-06 04:00 | 380 | 375
2017-07-06 04:30 | 391 | 387
2017-07-06 05:00 | 393 | 388
2017-07-06 05:30 | 409 | 406
2017-07-06 06:00 | 439 | 437
2017-07-06 06:30 | 475 | 472
2017-07-06 07:00 | 505 | 503
2017-07-06 07:30 | 539 | 537
2017-07-06 08:00 | 546 | 545
2017-07-06 08:30 | 545 | 544
2017-07-06 09:00 | 534 | 533
2017-07-06 09:30 | 513 | 511
2017-07-06 10:00 | 495 | 493
2017-07-06 10:30 | 481 | 479
2017-07-06 11:00 | 474 | 472
2017-07-06 11:30 | 472 | 471
2017-07-06 12:00 | 468 | 467
2017-07-06 12:30 | 465 | 464
2017-07-06 13:00 | 461 | 460
2017-07-06 13:30 | 468 | 467
2017-07-06 14:00 | 469 | 468
2017-07-06 14:30 | 482 | 480
2017-07-06 15:00 | 486 | 485
2017-07-06 15:30 | 503 | 502
2017-07-06 16:00 | 520 | 519
2017-07-06 16:30 | 536 | 534
2017-07-06 17:00 | 556 | 554
2017-07-06 17:30 | 584 | 584
2017-07-06 18:00 | 600 | 597
2017-07-06 18:30 | 590 | 586
2017-07-06 19:00 | 595 | 591
2017-07-06 19:30 | 590 | 586
2017-07-06 20:00 | 579 | 578
2017-07-06 20:30 | 581 | 579
2017-07-06 21:00 | 569 | 567
2017-07-06 21:30 | 556 | 553
2017-07-06 22:00 | 533 | 530
2017-07-06 22:30 | 506 | 505
2017-07-06 23:00 | 483 | 482
2017-07-06 23:30 | 461 | 459
2017-07-07 | 428 | 424
2017-07-07 00:30 | 409 | 404
2017-07-07 01:00 | 397 | 389
2017-07-07 01:30 | 394 | 384
2017-07-07 02:00 | 392 | 382
2017-07-07 02:30 | 375 | 367
2017-07-07 03:00 | 387 | 380
2017-07-07 03:30 | 387 | 380
2017-07-07 04:00 | 388 | 381
2017-07-07 04:30 | 398 | 391
2017-07-07 05:00 | 408 | 401
2017-07-07 05:30 | 420 | 416
2017-07-07 06:00 | 437 | 434
2017-07-07 06:30 | 472 | 471
2017-07-07 07:00 | 510 | 509
2017-07-07 07:30 | 555 | 555
2017-07-07 08:00 | 596 | 596
2017-07-07 08:30 | 608 | 606
2017-07-07 09:00 | 599 | 596
2017-07-07 09:30 | 606 | 604
2017-07-07 10:00 | 599 | 597
2017-07-07 10:30 | 583 | 581
2017-07-07 11:00 | 578 | 577
2017-07-07 11:30 | 572 | 572
2017-07-07 12:00 | 574 | 574
2017-07-07 12:30 | 577 | 577
2017-07-07 13:00 | 564 | 564
2017-07-07 13:30 | 564 | 564
2017-07-07 14:00 | 564 | 564
2017-07-07 14:30 | 572 | 572
2017-07-07 15:00 | 573 | 573
2017-07-07 15:30 | 576 | 576
2017-07-07 16:00 | 579 | 578
2017-07-07 16:30 | 588 | 587
2017-07-07 17:00 | 607 | 606
2017-07-07 17:30 | 629 | 628
2017-07-07 18:00 | 645 | 638
2017-07-07 18:30 | 638 | 627
2017-07-07 19:00 | 629 | 620
2017-07-07 19:30 | 624 | 614
2017-07-07 20:00 | 613 | 609
2017-07-07 20:30 | 612 | 611
2017-07-07 21:00 | 601 | 599
2017-07-07 21:30 | 585 | 583
2017-07-07 22:00 | 566 | 563
2017-07-07 22:30 | 542 | 540
2017-07-07 23:00 | 524 | 523
2017-07-07 23:30 | 507 | 506
2017-07-08 | 481 | 479
2017-07-08 00:30 | 455 | 452
2017-07-08 01:00 | 426 | 423
2017-07-08 01:30 | 401 | 396
2017-07-08 02:00 | 392 | 386
2017-07-08 02:30 | 386 | 380
2017-07-08 03:00 | 384 | 378
2017-07-08 03:30 | 380 | 373
2017-07-08 04:00 | 373 | 366
2017-07-08 04:30 | 370 | 363
2017-07-08 05:00 | 381 | 374
2017-07-08 05:30 | 388 | 382
2017-07-08 06:00 | 397 | 392
2017-07-08 06:30 | 418 | 413
2017-07-08 07:00 | 443 | 438
2017-07-08 07:30 | 479 | 475
2017-07-08 08:00 | 496 | 492
2017-07-08 08:30 | 516 | 514
2017-07-08 09:00 | 517 | 515
2017-07-08 09:30 | 507 | 505
2017-07-08 10:00 | 487 | 485
2017-07-08 10:30 | 480 | 477
2017-07-08 11:00 | 456 | 453
2017-07-08 11:30 | 433 | 430
2017-07-08 12:00 | 419 | 416
2017-07-08 12:30 | 417 | 414
2017-07-08 13:00 | 411 | 408
2017-07-08 13:30 | 413 | 410
2017-07-08 14:00 | 418 | 415
2017-07-08 14:30 | 424 | 422
2017-07-08 15:00 | 431 | 429
2017-07-08 15:30 | 442 | 440
2017-07-08 16:00 | 453 | 451
2017-07-08 16:30 | 481 | 480
2017-07-08 17:00 | 515 | 513
2017-07-08 17:30 | 548 | 546
2017-07-08 18:00 | 564 | 563
2017-07-08 18:30 | 565 | 563
2017-07-08 19:00 | 565 | 563
2017-07-08 19:30 | 564 | 562
2017-07-08 20:00 | 560 | 559
2017-07-08 20:30 | 556 | 554
2017-07-08 21:00 | 547 | 545
2017-07-08 21:30 | 534 | 532
2017-07-08 22:00 | 525 | 523
2017-07-08 22:30 | 513 | 510
2017-07-08 23:00 | 500 | 496
2017-07-08 23:30 | 483 | 480
2017-07-09 | 465 | 461
2017-07-09 00:30 | 439 | 435
2017-07-09 01:00 | 427 | 421
2017-07-09 01:30 | 416 | 410
2017-07-09 02:00 | 402 | 395
2017-07-09 02:30 | 399 | 391
2017-07-09 03:00 | 394 | 386
2017-07-09 03:30 | 390 | 380
2017-07-09 04:00 | 388 | 378
2017-07-09 04:30 | 394 | 384
2017-07-09 05:00 | 396 | 387
2017-07-09 05:30 | 402 | 393
2017-07-09 06:00 | 415 | 407
2017-07-09 06:30 | 433 | 426
2017-07-09 07:00 | 448 | 442
2017-07-09 07:30 | 474 | 469
2017-07-09 08:00 | 475 | 472
2017-07-09 08:30 | 479 | 476
2017-07-09 09:00 | 481 | 478
2017-07-09 09:30 | 478 | 475
2017-07-09 10:00 | 470 | 467
2017-07-09 10:30 | 448 | 445
2017-07-09 11:00 | 429 | 426
2017-07-09 11:30 | 410 | 407
2017-07-09 12:00 | 400 | 395
2017-07-09 12:30 | 396 | 392
2017-07-09 13:00 | 390 | 386
2017-07-09 13:30 | 387 | 382
2017-07-09 14:00 | 399 | 394
2017-07-09 14:30 | 411 | 406
2017-07-09 15:00 | 428 | 424
2017-07-09 15:30 | 448 | 444
2017-07-09 16:00 | 467 | 461
2017-07-09 16:30 | 482 | 478
2017-07-09 17:00 | 517 | 513
2017-07-09 17:30 | 555 | 549
2017-07-09 18:00 | 573 | 567
2017-07-09 18:30 | 583 | 576
2017-07-09 19:00 | 584 | 578
2017-07-09 19:30 | 578 | 572
2017-07-09 20:00 | 575 | 569
2017-07-09 20:30 | 582 | 576
2017-07-09 21:00 | 560 | 554
2017-07-09 21:30 | 537 | 534
2017-07-09 22:00 | 529 | 525
2017-07-09 22:30 | 506 | 502
2017-07-09 23:00 | 488 | 484
2017-07-09 23:30 | 466 | 464
2017-07-10 | 438 | 436
2017-07-10 00:30 | 417 | 414
2017-07-10 01:00 | 404 | 401
2017-07-10 01:30 | 398 | 394
2017-07-10 02:00 | 381 | 376
2017-07-10 02:30 | 368 | 363
2017-07-10 03:00 | 365 | 359
2017-07-10 03:30 | 364 | 358
2017-07-10 04:00 | 364 | 359
2017-07-10 04:30 | 382 | 377
2017-07-10 05:00 | 398 | 394
2017-07-10 05:30 | 419 | 416
2017-07-10 06:00 | 450 | 448
2017-07-10 06:30 | 512 | 511
2017-07-10 07:00 | 554 | 553
2017-07-10 07:30 | 597 | 596
2017-07-10 08:00 | 619 | 616
2017-07-10 08:30 | 609 | 605
2017-07-10 09:00 | 588 | 583
2017-07-10 09:30 | 576 | 574
2017-07-10 10:00 | 555 | 553
2017-07-10 10:30 | 551 | 550
2017-07-10 11:00 | 543 | 542
2017-07-10 11:30 | 523 | 522
2017-07-10 12:00 | 531 | 530
2017-07-10 12:30 | 521 | 520
2017-07-10 13:00 | 520 | 518
2017-07-10 13:30 | 517 | 516
2017-07-10 14:00 | 525 | 524
2017-07-10 14:30 | 537 | 536
2017-07-10 15:00 | 545 | 544
2017-07-10 15:30 | 554 | 553
2017-07-10 16:00 | 576 | 573
2017-07-10 16:30 | 591 | 588
2017-07-10 17:00 | 624 | 619
2017-07-10 17:30 | 647 | 643
2017-07-10 18:00 | 668 | 657
2017-07-10 18:30 | 663 | 650
2017-07-10 19:00 | 657 | 642
2017-07-10 19:30 | 635 | 626
2017-07-10 20:00 | 632 | 622
2017-07-10 20:30 | 627 | 616
2017-07-10 21:00 | 603 | 593
2017-07-10 21:30 | 573 | 570
2017-07-10 22:00 | 560 | 556
2017-07-10 22:30 | 532 | 528
2017-07-10 23:00 | 491 | 488
2017-07-10 23:30 | 469 | 467
2017-07-11 | 447 | 445
2017-07-11 00:30 | 432 | 429
2017-07-11 01:00 | 430 | 425
2017-07-11 01:30 | 413 | 407
2017-07-11 02:00 | 401 | 394
2017-07-11 02:30 | 394 | 386
2017-07-11 03:00 | 390 | 382
2017-07-11 03:30 | 384 | 377
2017-07-11 04:00 | 387 | 380
2017-07-11 04:30 | 391 | 385
2017-07-11 05:00 | 406 | 400
2017-07-11 05:30 | 421 | 417
2017-07-11 06:00 | 455 | 452
2017-07-11 06:30 | 506 | 503
2017-07-11 07:00 | 549 | 544
2017-07-11 07:30 | 589 | 587
2017-07-11 08:00 | 607 | 606
2017-07-11 08:30 | 601 | 598
2017-07-11 09:00 | 573 | 569
2017-07-11 09:30 | 557 | 551
2017-07-11 10:00 | 537 | 532
2017-07-11 10:30 | 523 | 519
2017-07-11 11:00 | 523 | 518
2017-07-11 11:30 | 517 | 512
2017-07-11 12:00 | 517 | 513
2017-07-11 12:30 | 518 | 514
2017-07-11 13:00 | 519 | 515
2017-07-11 13:30 | 527 | 522
2017-07-11 14:00 | 536 | 532
2017-07-11 14:30 | 543 | 539
2017-07-11 15:00 | 556 | 552
2017-07-11 15:30 | 542 | 537
2017-07-11 16:00 | 546 | 541
2017-07-11 16:30 | 567 | 562
2017-07-11 17:00 | 595 | 590
2017-07-11 17:30 | 629 | 623
2017-07-11 18:00 | 656 | 652
2017-07-11 18:30 | 653 | 649
2017-07-11 19:00 | 641 | 636
2017-07-11 19:30 | 623 | 619
2017-07-11 20:00 | 623 | 619
2017-07-11 20:30 | 618 | 615
2017-07-11 21:00 | 602 | 598
2017-07-11 21:30 | 581 | 577
2017-07-11 22:00 | 566 | 561
2017-07-11 22:30 | 529 | 527
2017-07-11 23:00 | 495 | 495
2017-07-11 23:30 | 479 | 478
2017-07-12 | 455 | 453
2017-07-12 00:30 | 442 | 439
2017-07-12 01:00 | 431 | 427
2017-07-12 01:30 | 412 | 409
2017-07-12 02:00 | 406 | 402
2017-07-12 02:30 | 401 | 397
2017-07-12 03:00 | 397 | 392
2017-07-12 03:30 | 398 | 394
2017-07-12 04:00 | 396 | 391
2017-07-12 04:30 | 408 | 404
2017-07-12 05:00 | 427 | 424
2017-07-12 05:30 | 448 | 446
2017-07-12 06:00 | 469 | 468
2017-07-12 06:30 | 525 | 525
2017-07-12 07:00 | 580 | 578
2017-07-12 07:30 | 625 | 623
2017-07-12 08:00 | 630 | 629
2017-07-12 08:30 | 617 | 615
2017-07-12 09:00 | 594 | 592
2017-07-12 09:30 | 580 | 577
2017-07-12 10:00 | 555 | 553
2017-07-12 10:30 | 533 | 531
2017-07-12 11:00 | 517 | 515
2017-07-12 11:30 | 505 | 503
2017-07-12 12:00 | 501 | 500
2017-07-12 12:30 | 503 | 502
2017-07-12 13:00 | 513 | 512
2017-07-12 13:30 | 527 | 525
2017-07-12 14:00 | 537 | 535
2017-07-12 14:30 | 539 | 538
2017-07-12 15:00 | 542 | 539
2017-07-12 15:30 | 550 | 548
2017-07-12 16:00 | 565 | 563
2017-07-12 16:30 | 579 | 577
2017-07-12 17:00 | 602 | 600
2017-07-12 17:30 | 634 | 632
2017-07-12 18:00 | 655 | 653
2017-07-12 18:30 | 650 | 646
2017-07-12 19:00 | 651 | 647
2017-07-12 19:30 | 648 | 643
2017-07-12 20:00 | 637 | 633
2017-07-12 20:30 | 633 | 631
2017-07-12 21:00 | 615 | 612
2017-07-12 21:30 | 595 | 592
2017-07-12 22:00 | 581 | 577
2017-07-12 22:30 | 557 | 552
2017-07-12 23:00 | 535 | 531
2017-07-12 23:30 | 509 | 506
2017-07-13 | 479 | 477
2017-07-13 00:30 | 455 | 451
2017-07-13 01:00 | 430 | 425
2017-07-13 01:30 | 418 | 413
2017-07-13 02:00 | 408 | 403
2017-07-13 02:30 | 402 | 397
2017-07-13 03:00 | 396 | 391
2017-07-13 03:30 | 394 | 388
2017-07-13 04:00 | 400 | 395
2017-07-13 04:30 | 405 | 401
2017-07-13 05:00 | 422 | 418
2017-07-13 05:30 | 447 | 444
2017-07-13 06:00 | 467 | 465
2017-07-13 06:30 | 526 | 525
2017-07-13 07:00 | 566 | 564
2017-07-13 07:30 | 599 | 597
2017-07-13 08:00 | 603 | 601
2017-07-13 08:30 | 587 | 584
2017-07-13 09:00 | 566 | 563
2017-07-13 09:30 | 552 | 549
2017-07-13 10:00 | 531 | 527
2017-07-13 10:30 | 513 | 508
2017-07-13 11:00 | 502 | 497
2017-07-13 11:30 | 491 | 488
2017-07-13 12:00 | 486 | 483
2017-07-13 12:30 | 493 | 491
2017-07-13 13:00 | 509 | 506
2017-07-13 13:30 | 522 | 519
2017-07-13 14:00 | 524 | 522
2017-07-13 14:30 | 525 | 524
2017-07-13 15:00 | 521 | 518
2017-07-13 15:30 | 542 | 539
2017-07-13 16:00 | 551 | 548
2017-07-13 16:30 | 575 | 572
2017-07-13 17:00 | 586 | 584
2017-07-13 17:30 | 609 | 607
2017-07-13 18:00 | 633 | 631
2017-07-13 18:30 | 629 | 627
2017-07-13 19:00 | 633 | 630
2017-07-13 19:30 | 627 | 624
2017-07-13 20:00 | 632 | 628
2017-07-13 20:30 | 630 | 627
2017-07-13 21:00 | 608 | 606
2017-07-13 21:30 | 588 | 584
2017-07-13 22:00 | 567 | 564
2017-07-13 22:30 | 539 | 536
2017-07-13 23:00 | 515 | 514
2017-07-13 23:30 | 492 | 491
2017-07-14 | 459 | 459
2017-07-14 00:30 | 422 | 420
2017-07-14 01:00 | 405 | 402
2017-07-14 01:30 | 393 | 390
2017-07-14 02:00 | 397 | 393
2017-07-14 02:30 | 382 | 378
2017-07-14 03:00 | 378 | 374
2017-07-14 03:30 | 375 | 370
2017-07-14 04:00 | 380 | 376
2017-07-14 04:30 | 395 | 392
2017-07-14 05:00 | 403 | 400
2017-07-14 05:30 | 439 | 436
2017-07-14 06:00 | 467 | 465
2017-07-14 06:30 | 519 | 515
2017-07-14 07:00 | 568 | 561
2017-07-14 07:30 | 606 | 601
2017-07-14 08:00 | 607 | 604
2017-07-14 08:30 | 596 | 592
2017-07-14 09:00 | 578 | 574
2017-07-14 09:30 | 560 | 555
2017-07-14 10:00 | 540 | 537
2017-07-14 10:30 | 524 | 522
2017-07-14 11:00 | 514 | 512
2017-07-14 11:30 | 501 | 499
2017-07-14 12:00 | 491 | 489
2017-07-14 12:30 | 491 | 488
2017-07-14 13:00 | 502 | 499
2017-07-14 13:30 | 508 | 506
2017-07-14 14:00 | 509 | 507
2017-07-14 14:30 | 510 | 508
2017-07-14 15:00 | 514 | 512
2017-07-14 15:30 | 522 | 519
2017-07-14 16:00 | 531 | 529
2017-07-14 16:30 | 544 | 542
2017-07-14 17:00 | 562 | 560
2017-07-14 17:30 | 586 | 582
2017-07-14 18:00 | 593 | 590
2017-07-14 18:30 | 588 | 584
2017-07-14 19:00 | 589 | 585
2017-07-14 19:30 | 587 | 582
2017-07-14 20:00 | 584 | 579
2017-07-14 20:30 | 572 | 568
2017-07-14 21:00 | 551 | 549
2017-07-14 21:30 | 542 | 539
2017-07-14 22:00 | 534 | 531
2017-07-14 22:30 | 501 | 500
2017-07-14 23:00 | 484 | 482
2017-07-14 23:30 | 474 | 472
2017-07-15 | 446 | 445
2017-07-15 00:30 | 417 | 414
2017-07-15 01:00 | 400 | 397
2017-07-15 01:30 | 398 | 394
2017-07-15 02:00 | 389 | 384
2017-07-15 02:30 | 381 | 375
2017-07-15 03:00 | 374 | 368
2017-07-15 03:30 | 370 | 364
2017-07-15 04:00 | 372 | 366
2017-07-15 04:30 | 377 | 369
2017-07-15 05:00 | 386 | 379
2017-07-15 05:30 | 397 | 389
2017-07-15 06:00 | 406 | 400
2017-07-15 06:30 | 431 | 426
2017-07-15 07:00 | 442 | 437
2017-07-15 07:30 | 462 | 458
2017-07-15 08:00 | 478 | 474
2017-07-15 08:30 | 480 | 476
2017-07-15 09:00 | 477 | 473
2017-07-15 09:30 | 469 | 465
2017-07-15 10:00 | 459 | 455
2017-07-15 10:30 | 453 | 448
2017-07-15 11:00 | 429 | 424
2017-07-15 11:30 | 414 | 409
2017-07-15 12:00 | 408 | 403
2017-07-15 12:30 | 404 | 399
2017-07-15 13:00 | 404 | 399
2017-07-15 13:30 | 409 | 403
2017-07-15 14:00 | 411 | 405
2017-07-15 14:30 | 415 | 410
2017-07-15 15:00 | 421 | 415
2017-07-15 15:30 | 431 | 426
2017-07-15 16:00 | 446 | 441
2017-07-15 16:30 | 471 | 467
2017-07-15 17:00 | 499 | 497
2017-07-15 17:30 | 523 | 519
2017-07-15 18:00 | 531 | 527
2017-07-15 18:30 | 529 | 525
2017-07-15 19:00 | 528 | 523
2017-07-15 19:30 | 528 | 522
2017-07-15 20:00 | 521 | 517
2017-07-15 20:30 | 529 | 524
2017-07-15 21:00 | 515 | 509
2017-07-15 21:30 | 497 | 492
2017-07-15 22:00 | 484 | 480
2017-07-15 22:30 | 471 | 467
2017-07-15 23:00 | 458 | 453
2017-07-15 23:30 | 443 | 436
2017-07-16 | 423 | 418
2017-07-16 00:30 | 413 | 407
2017-07-16 01:00 | 396 | 388
2017-07-16 01:30 | 380 | 371
2017-07-16 02:00 | 371 | 358
2017-07-16 02:30 | 371 | 358
2017-07-16 03:00 | 363 | 349
2017-07-16 03:30 | 356 | 341
2017-07-16 04:00 | 354 | 340
2017-07-16 04:30 | 366 | 352
2017-07-16 05:00 | 359 | 345
2017-07-16 05:30 | 362 | 350
2017-07-16 06:00 | 366 | 355
2017-07-16 06:30 | 372 | 362
2017-07-16 07:00 | 379 | 369
2017-07-16 07:30 | 402 | 393
2017-07-16 08:00 | 416 | 409
2017-07-16 08:30 | 433 | 429
2017-07-16 09:00 | 452 | 449
2017-07-16 09:30 | 443 | 441
2017-07-16 10:00 | 439 | 434
2017-07-16 10:30 | 436 | 432
2017-07-16 11:00 | 422 | 417
2017-07-16 11:30 | 419 | 414
2017-07-16 12:00 | 422 | 417
2017-07-16 12:30 | 419 | 413
2017-07-16 13:00 | 416 | 410
2017-07-16 13:30 | 411 | 405
2017-07-16 14:00 | 406 | 400
2017-07-16 14:30 | 411 | 405
2017-07-16 15:00 | 413 | 407
2017-07-16 15:30 | 424 | 419
2017-07-16 16:00 | 439 | 435
2017-07-16 16:30 | 452 | 450
2017-07-16 17:00 | 479 | 478
2017-07-16 17:30 | 516 | 516
2017-07-16 18:00 | 528 | 527
2017-07-16 18:30 | 518 | 517
2017-07-16 19:00 | 514 | 514
2017-07-16 19:30 | 516 | 516
2017-07-16 20:00 | 517 | 516
2017-07-16 20:30 | 519 | 518
2017-07-16 21:00 | 506 | 504
2017-07-16 21:30 | 489 | 486
2017-07-16 22:00 | 480 | 476
2017-07-16 22:30 | 475 | 469
2017-07-16 23:00 | 462 | 457
2017-07-16 23:30 | 451 | 444
2017-07-17 | 422 | 415
2017-07-17 00:30 | 395 | 386
2017-07-17 01:00 | 378 | 366
2017-07-17 01:30 | 363 | 350
2017-07-17 02:00 | 358 | 344
2017-07-17 02:30 | 355 | 341
2017-07-17 03:00 | 354 | 340
2017-07-17 03:30 | 352 | 338
2017-07-17 04:00 | 347 | 333
2017-07-17 04:30 | 336 | 322
2017-07-17 05:00 | 354 | 343
2017-07-17 05:30 | 396 | 390
2017-07-17 06:00 | 439 | 437
2017-07-17 06:30 | 489 | 487
2017-07-17 07:00 | 531 | 529
2017-07-17 07:30 | 558 | 554
2017-07-17 08:00 | 566 | 559
2017-07-17 08:30 | 556 | 550
2017-07-17 09:00 | 543 | 535
2017-07-17 09:30 | 533 | 525
2017-07-17 10:00 | 523 | 515
2017-07-17 10:30 | 511 | 504
2017-07-17 11:00 | 502 | 495
2017-07-17 11:30 | 493 | 486
2017-07-17 12:00 | 496 | 489
2017-07-17 12:30 | 498 | 491
2017-07-17 13:00 | 500 | 493
2017-07-17 13:30 | 503 | 498
2017-07-17 14:00 | 502 | 497
2017-07-17 14:30 | 504 | 499
2017-07-17 15:00 | 504 | 498
2017-07-17 15:30 | 516 | 511
2017-07-17 16:00 | 523 | 519
2017-07-17 16:30 | 532 | 528
2017-07-17 17:00 | 558 | 555
2017-07-17 17:30 | 584 | 578
2017-07-17 18:00 | 598 | 592
2017-07-17 18:30 | 594 | 586
2017-07-17 19:00 | 587 | 580
2017-07-17 19:30 | 582 | 576
2017-07-17 20:00 | 568 | 568
2017-07-17 20:30 | 568 | 567
2017-07-17 21:00 | 544 | 544
2017-07-17 21:30 | 520 | 519
2017-07-17 22:00 | 507 | 506
2017-07-17 22:30 | 498 | 496
2017-07-17 23:00 | 484 | 481
2017-07-17 23:30 | 470 | 466
2017-07-18 | 434 | 427
2017-07-18 00:30 | 413 | 407
2017-07-18 01:00 | 411 | 403
2017-07-18 01:30 | 400 | 392
2017-07-18 02:00 | 379 | 369
2017-07-18 02:30 | 363 | 351
2017-07-18 03:00 | 371 | 360
2017-07-18 03:30 | 367 | 355
2017-07-18 04:00 | 368 | 357
2017-07-18 04:30 | 383 | 373
2017-07-18 05:00 | 405 | 397
2017-07-18 05:30 | 431 | 426
2017-07-18 06:00 | 451 | 446
2017-07-18 06:30 | 502 | 499
2017-07-18 07:00 | 538 | 537
2017-07-18 07:30 | 564 | 563
2017-07-18 08:00 | 564 | 564
2017-07-18 08:30 | 555 | 555
2017-07-18 09:00 | 538 | 537
2017-07-18 09:30 | 529 | 528
2017-07-18 10:00 | 506 | 504
2017-07-18 10:30 | 493 | 490
2017-07-18 11:00 | 486 | 484
2017-07-18 11:30 | 478 | 476
2017-07-18 12:00 | 482 | 480
2017-07-18 12:30 | 476 | 474
2017-07-18 13:00 | 474 | 471
2017-07-18 13:30 | 476 | 474
2017-07-18 14:00 | 476 | 475
2017-07-18 14:30 | 485 | 484
2017-07-18 15:00 | 491 | 489
2017-07-18 15:30 | 502 | 500
2017-07-18 16:00 | 518 | 517
2017-07-18 16:30 | 530 | 529
2017-07-18 17:00 | 550 | 549
2017-07-18 17:30 | 567 | 567
2017-07-18 18:00 | 580 | 579
2017-07-18 18:30 | 569 | 565
2017-07-18 19:00 | 567 | 562
2017-07-18 19:30 | 554 | 551
2017-07-18 20:00 | 550 | 548
2017-07-18 20:30 | 547 | 544
2017-07-18 21:00 | 530 | 526
2017-07-18 21:30 | 516 | 512
2017-07-18 22:00 | 505 | 501
2017-07-18 22:30 | 491 | 487
2017-07-18 23:00 | 477 | 472
2017-07-18 23:30 | 462 | 460
2017-07-19 | 445 | 441
2017-07-19 00:30 | 433 | 428
2017-07-19 01:00 | 413 | 406
2017-07-19 01:30 | 403 | 395
2017-07-19 02:00 | 388 | 378
2017-07-19 02:30 | 381 | 371
2017-07-19 03:00 | 370 | 359
2017-07-19 03:30 | 358 | 345
2017-07-19 04:00 | 357 | 344
2017-07-19 04:30 | 357 | 345
2017-07-19 05:00 | 366 | 356
2017-07-19 05:30 | 410 | 406
2017-07-19 06:00 | 444 | 441
2017-07-19 06:30 | 496 | 491
2017-07-19 07:00 | 535 | 531
2017-07-19 07:30 | 555 | 552
2017-07-19 08:00 | 566 | 559
2017-07-19 08:30 | 556 | 548
2017-07-19 09:00 | 539 | 531
2017-07-19 09:30 | 519 | 513
2017-07-19 10:00 | 506 | 499
2017-07-19 10:30 | 504 | 500
2017-07-19 11:00 | 493 | 488
2017-07-19 11:30 | 491 | 486
2017-07-19 12:00 | 482 | 477
2017-07-19 12:30 | 473 | 469
2017-07-19 13:00 | 478 | 474
2017-07-19 13:30 | 485 | 481
2017-07-19 14:00 | 482 | 479
2017-07-19 14:30 | 487 | 484
2017-07-19 15:00 | 494 | 492
2017-07-19 15:30 | 505 | 502
2017-07-19 16:00 | 514 | 512
2017-07-19 16:30 | 533 | 532
2017-07-19 17:00 | 563 | 561
2017-07-19 17:30 | 594 | 591
2017-07-19 18:00 | 618 | 612
2017-07-19 18:30 | 621 | 614
2017-07-19 19:00 | 617 | 614
2017-07-19 19:30 | 618 | 615
2017-07-19 20:00 | 614 | 611
2017-07-19 20:30 | 604 | 601
2017-07-19 21:00 | 575 | 571
2017-07-19 21:30 | 546 | 544
2017-07-19 22:00 | 536 | 533
2017-07-19 22:30 | 513 | 512
2017-07-19 23:00 | 492 | 491
2017-07-19 23:30 | 472 | 471
2017-07-20 | 448 | 446
2017-07-20 00:30 | 435 | 431
2017-07-20 01:00 | 421 | 416
2017-07-20 01:30 | 397 | 391
2017-07-20 02:00 | 393 | 387
2017-07-20 02:30 | 386 | 380
2017-07-20 03:00 | 389 | 383
2017-07-20 03:30 | 395 | 389
2017-07-20 04:00 | 397 | 391
2017-07-20 04:30 | 392 | 386
2017-07-20 05:00 | 404 | 400
2017-07-20 05:30 | 431 | 428
2017-07-20 06:00 | 456 | 455
2017-07-20 06:30 | 522 | 520
2017-07-20 07:00 | 579 | 573
2017-07-20 07:30 | 603 | 599
2017-07-20 08:00 | 599 | 594
2017-07-20 08:30 | 572 | 566
2017-07-20 09:00 | 558 | 550
2017-07-20 09:30 | 540 | 535
2017-07-20 10:00 | 511 | 509
2017-07-20 10:30 | 505 | 503
2017-07-20 11:00 | 497 | 494
2017-07-20 11:30 | 489 | 486
2017-07-20 12:00 | 483 | 480
2017-07-20 12:30 | 480 | 477
2017-07-20 13:00 | 468 | 465
2017-07-20 13:30 | 465 | 463
2017-07-20 14:00 | 475 | 473
2017-07-20 14:30 | 483 | 481
2017-07-20 15:00 | 496 | 493
2017-07-20 15:30 | 509 | 507
2017-07-20 16:00 | 540 | 538
2017-07-20 16:30 | 548 | 547
2017-07-20 17:00 | 577 | 576
2017-07-20 17:30 | 591 | 590
2017-07-20 18:00 | 612 | 611
2017-07-20 18:30 | 617 | 614
2017-07-20 19:00 | 620 | 617
2017-07-20 19:30 | 617 | 613
2017-07-20 20:00 | 621 | 617
2017-07-20 20:30 | 615 | 610
2017-07-20 21:00 | 593 | 586
2017-07-20 21:30 | 574 | 565
2017-07-20 22:00 | 552 | 546
2017-07-20 22:30 | 535 | 529
2017-07-20 23:00 | 513 | 507
2017-07-20 23:30 | 489 | 486
2017-07-21 | 471 | 469
2017-07-21 00:30 | 453 | 450
2017-07-21 01:00 | 443 | 439
2017-07-21 01:30 | 410 | 405
2017-07-21 02:00 | 395 | 388
2017-07-21 02:30 | 390 | 383
2017-07-21 03:00 | 389 | 381
2017-07-21 03:30 | 398 | 390
2017-07-21 04:00 | 405 | 397
2017-07-21 04:30 | 398 | 391
2017-07-21 05:00 | 404 | 398
2017-07-21 05:30 | 423 | 419
2017-07-21 06:00 | 465 | 463
2017-07-21 06:30 | 527 | 526
2017-07-21 07:00 | 576 | 575
2017-07-21 07:30 | 616 | 611
2017-07-21 08:00 | 619 | 612
2017-07-21 08:30 | 606 | 598
2017-07-21 09:00 | 587 | 576
2017-07-21 09:30 | 566 | 553
2017-07-21 10:00 | 536 | 524
2017-07-21 10:30 | 520 | 505
2017-07-21 11:00 | 499 | 488
2017-07-21 11:30 | 484 | 475
2017-07-21 12:00 | 466 | 462
2017-07-21 12:30 | 450 | 449
2017-07-21 13:00 | 449 | 447
2017-07-21 13:30 | 458 | 456
2017-07-21 14:00 | 469 | 468
2017-07-21 14:30 | 477 | 476
2017-07-21 15:00 | 474 | 473
2017-07-21 15:30 | 474 | 473
2017-07-21 16:00 | 491 | 490
2017-07-21 16:30 | 512 | 511
2017-07-21 17:00 | 531 | 529
2017-07-21 17:30 | 565 | 560
2017-07-21 18:00 | 590 | 584
2017-07-21 18:30 | 594 | 587
2017-07-21 19:00 | 594 | 587
2017-07-21 19:30 | 592 | 583
2017-07-21 20:00 | 597 | 588
2017-07-21 20:30 | 594 | 587
2017-07-21 21:00 | 575 | 572
2017-07-21 21:30 | 556 | 554
2017-07-21 22:00 | 542 | 540
2017-07-21 22:30 | 528 | 524
2017-07-21 23:00 | 520 | 515
2017-07-21 23:30 | 499 | 495
2017-07-22 | 473 | 468
2017-07-22 00:30 | 443 | 438
2017-07-22 01:00 | 424 | 417
2017-07-22 01:30 | 403 | 395
2017-07-22 02:00 | 387 | 379
2017-07-22 02:30 | 379 | 370
2017-07-22 03:00 | 382 | 372
2017-07-22 03:30 | 383 | 373
2017-07-22 04:00 | 382 | 373
2017-07-22 04:30 | 374 | 365
2017-07-22 05:00 | 375 | 367
2017-07-22 05:30 | 384 | 376
2017-07-22 06:00 | 406 | 399
2017-07-22 06:30 | 432 | 427
2017-07-22 07:00 | 459 | 455
2017-07-22 07:30 | 488 | 485
2017-07-22 08:00 | 506 | 502
2017-07-22 08:30 | 504 | 501
2017-07-22 09:00 | 493 | 490
2017-07-22 09:30 | 482 | 478
2017-07-22 10:00 | 461 | 456
2017-07-22 10:30 | 454 | 448
2017-07-22 11:00 | 435 | 429
2017-07-22 11:30 | 413 | 407
2017-07-22 12:00 | 400 | 395
2017-07-22 12:30 | 390 | 385
2017-07-22 13:00 | 386 | 381
2017-07-22 13:30 | 384 | 378
2017-07-22 14:00 | 391 | 385
2017-07-22 14:30 | 388 | 382
2017-07-22 15:00 | 400 | 395
2017-07-22 15:30 | 421 | 416
2017-07-22 16:00 | 439 | 434
2017-07-22 16:30 | 451 | 447
2017-07-22 17:00 | 472 | 469
2017-07-22 17:30 | 486 | 483
2017-07-22 18:00 | 517 | 509
2017-07-22 18:30 | 523 | 514
2017-07-22 19:00 | 530 | 521
2017-07-22 19:30 | 525 | 517
2017-07-22 20:00 | 518 | 511
2017-07-22 20:30 | 521 | 513
2017-07-22 21:00 | 500 | 497
2017-07-22 21:30 | 485 | 483
2017-07-22 22:00 | 479 | 477
2017-07-22 22:30 | 479 | 477
2017-07-22 23:00 | 480 | 478
2017-07-22 23:30 | 470 | 466
2017-07-23 | 456 | 452
2017-07-23 00:30 | 427 | 421
2017-07-23 01:00 | 422 | 414
2017-07-23 01:30 | 403 | 393
2017-07-23 02:00 | 391 | 380
2017-07-23 02:30 | 384 | 372
2017-07-23 03:00 | 371 | 359
2017-07-23 03:30 | 367 | 355
2017-07-23 04:00 | 366 | 354
2017-07-23 04:30 | 367 | 354
2017-07-23 05:00 | 370 | 358
2017-07-23 05:30 | 384 | 373
2017-07-23 06:00 | 388 | 377
2017-07-23 06:30 | 413 | 403
2017-07-23 07:00 | 434 | 425
2017-07-23 07:30 | 452 | 444
2017-07-23 08:00 | 457 | 451
2017-07-23 08:30 | 464 | 458
2017-07-23 09:00 | 463 | 458
2017-07-23 09:30 | 451 | 446
2017-07-23 10:00 | 439 | 433
2017-07-23 10:30 | 424 | 418
2017-07-23 11:00 | 402 | 396
2017-07-23 11:30 | 386 | 380
2017-07-23 12:00 | 375 | 368
2017-07-23 12:30 | 369 | 361
2017-07-23 13:00 | 367 | 359
2017-07-23 13:30 | 368 | 360
2017-07-23 14:00 | 373 | 364
2017-07-23 14:30 | 382 | 374
2017-07-23 15:00 | 401 | 394
2017-07-23 15:30 | 408 | 400
2017-07-23 16:00 | 425 | 418
2017-07-23 16:30 | 443 | 438
2017-07-23 17:00 | 461 | 458
2017-07-23 17:30 | 473 | 471
2017-07-23 18:00 | 493 | 488
2017-07-23 18:30 | 504 | 496
2017-07-23 19:00 | 511 | 504
2017-07-23 19:30 | 512 | 504
2017-07-23 20:00 | 509 | 500
2017-07-23 20:30 | 505 | 504
2017-07-23 21:00 | 494 | 491
2017-07-23 21:30 | 479 | 476
2017-07-23 22:00 | 479 | 475
2017-07-23 22:30 | 469 | 466
2017-07-23 23:00 | 457 | 454
2017-07-23 23:30 | 445 | 442
2017-07-24 | 424 | 420
2017-07-24 00:30 | 398 | 392
2017-07-24 01:00 | 379 | 371
2017-07-24 01:30 | 366 | 356
2017-07-24 02:00 | 372 | 361
2017-07-24 02:30 | 369 | 358
2017-07-24 03:00 | 364 | 352
2017-07-24 03:30 | 372 | 361
2017-07-24 04:00 | 371 | 359
2017-07-24 04:30 | 376 | 366
2017-07-24 05:00 | 395 | 386
2017-07-24 05:30 | 423 | 417
2017-07-24 06:00 | 453 | 450
2017-07-24 06:30 | 513 | 511
2017-07-24 07:00 | 565 | 564
2017-07-24 07:30 | 581 | 580
2017-07-24 08:00 | 589 | 588
2017-07-24 08:30 | 572 | 571
2017-07-24 09:00 | 559 | 557
2017-07-24 09:30 | 538 | 536
2017-07-24 10:00 | 513 | 510
2017-07-24 10:30 | 494 | 490
2017-07-24 11:00 | 477 | 473
2017-07-24 11:30 | 461 | 459
2017-07-24 12:00 | 461 | 460
2017-07-24 12:30 | 462 | 460
2017-07-24 13:00 | 464 | 463
2017-07-24 13:30 | 464 | 463
2017-07-24 14:00 | 467 | 466
2017-07-24 14:30 | 470 | 469
2017-07-24 15:00 | 473 | 473
2017-07-24 15:30 | 484 | 483
2017-07-24 16:00 | 496 | 495
2017-07-24 16:30 | 512 | 512
2017-07-24 17:00 | 534 | 533
2017-07-24 17:30 | 554 | 554
2017-07-24 18:00 | 576 | 575
2017-07-24 18:30 | 568 | 568
2017-07-24 19:00 | 572 | 571
2017-07-24 19:30 | 574 | 572
2017-07-24 20:00 | 572 | 570
2017-07-24 20:30 | 569 | 566
2017-07-24 21:00 | 546 | 543
2017-07-24 21:30 | 533 | 530
2017-07-24 22:00 | 517 | 515
2017-07-24 22:30 | 497 | 495
2017-07-24 23:00 | 480 | 477
2017-07-24 23:30 | 469 | 464
2017-07-25 | 447 | 443
2017-07-25 00:30 | 425 | 420
2017-07-25 01:00 | 412 | 405
2017-07-25 01:30 | 388 | 380
2017-07-25 02:00 | 367 | 358
2017-07-25 02:30 | 350 | 339
2017-07-25 03:00 | 350 | 339
2017-07-25 03:30 | 347 | 336
2017-07-25 04:00 | 345 | 335
2017-07-25 04:30 | 356 | 347
2017-07-25 05:00 | 372 | 363
2017-07-25 05:30 | 409 | 404
2017-07-25 06:00 | 461 | 455
2017-07-25 06:30 | 530 | 522
2017-07-25 07:00 | 586 | 580
2017-07-25 07:30 | 601 | 597
2017-07-25 08:00 | 597 | 592
2017-07-25 08:30 | 578 | 570
2017-07-25 09:00 | 563 | 552
2017-07-25 09:30 | 539 | 531
2017-07-25 10:00 | 504 | 500
2017-07-25 10:30 | 487 | 483
2017-07-25 11:00 | 468 | 466
2017-07-25 11:30 | 455 | 453
2017-07-25 12:00 | 446 | 445
2017-07-25 12:30 | 444 | 443
2017-07-25 13:00 | 447 | 447
2017-07-25 13:30 | 452 | 452
2017-07-25 14:00 | 458 | 457
2017-07-25 14:30 | 462 | 461
2017-07-25 15:00 | 467 | 466
2017-07-25 15:30 | 478 | 477
2017-07-25 16:00 | 491 | 491
2017-07-25 16:30 | 511 | 510
2017-07-25 17:00 | 539 | 538
2017-07-25 17:30 | 568 | 567
2017-07-25 18:00 | 594 | 594
2017-07-25 18:30 | 600 | 599
2017-07-25 19:00 | 603 | 601
2017-07-25 19:30 | 607 | 604
2017-07-25 20:00 | 611 | 609
2017-07-25 20:30 | 608 | 606
2017-07-25 21:00 | 580 | 579
2017-07-25 21:30 | 566 | 565
2017-07-25 22:00 | 548 | 547
2017-07-25 22:30 | 521 | 518
2017-07-25 23:00 | 493 | 490
2017-07-25 23:30 | 479 | 475
2017-07-26 | 458 | 454
2017-07-26 00:30 | 441 | 437
2017-07-26 01:00 | 423 | 418
2017-07-26 01:30 | 400 | 394
2017-07-26 02:00 | 384 | 377
2017-07-26 02:30 | 377 | 369
2017-07-26 03:00 | 376 | 367
2017-07-26 03:30 | 367 | 358
2017-07-26 04:00 | 366 | 358
2017-07-26 04:30 | 370 | 364
2017-07-26 05:00 | 386 | 382
2017-07-26 05:30 | 426 | 423
2017-07-26 06:00 | 472 | 470
2017-07-26 06:30 | 544 | 543
2017-07-26 07:00 | 604 | 602
2017-07-26 07:30 | 624 | 622
2017-07-26 08:00 | 620 | 618
2017-07-26 08:30 | 601 | 599
2017-07-26 09:00 | 574 | 570
2017-07-26 09:30 | 545 | 539
2017-07-26 10:00 | 510 | 509
2017-07-26 10:30 | 494 | 493
2017-07-26 11:00 | 483 | 482
2017-07-26 11:30 | 479 | 478
2017-07-26 12:00 | 470 | 469
2017-07-26 12:30 | 463 | 462
2017-07-26 13:00 | 457 | 456
2017-07-26 13:30 | 454 | 453
2017-07-26 14:00 | 458 | 457
2017-07-26 14:30 | 466 | 465
2017-07-26 15:00 | 471 | 471
2017-07-26 15:30 | 481 | 480
2017-07-26 16:00 | 500 | 500
2017-07-26 16:30 | 521 | 521
2017-07-26 17:00 | 555 | 555
2017-07-26 17:30 | 586 | 586
2017-07-26 18:00 | 614 | 612
2017-07-26 18:30 | 610 | 604
2017-07-26 19:00 | 616 | 611
2017-07-26 19:30 | 618 | 612
2017-07-26 20:00 | 605 | 601
2017-07-26 20:30 | 612 | 607
2017-07-26 21:00 | 588 | 585
2017-07-26 21:30 | 570 | 566
2017-07-26 22:00 | 548 | 544
2017-07-26 22:30 | 527 | 523
2017-07-26 23:00 | 510 | 506
2017-07-26 23:30 | 498 | 493
2017-07-27 | 463 | 456
2017-07-27 00:30 | 432 | 424
2017-07-27 01:00 | 408 | 399
2017-07-27 01:30 | 385 | 380
2017-07-27 02:00 | 373 | 367
2017-07-27 02:30 | 364 | 358
2017-07-27 03:00 | 361 | 354
2017-07-27 03:30 | 361 | 354
2017-07-27 04:00 | 364 | 357
2017-07-27 04:30 | 377 | 372
2017-07-27 05:00 | 399 | 394
2017-07-27 05:30 | 436 | 433
2017-07-27 06:00 | 479 | 477
2017-07-27 06:30 | 548 | 546
2017-07-27 07:00 | 596 | 594
2017-07-27 07:30 | 636 | 633
2017-07-27 08:00 | 661 | 649
2017-07-27 08:30 | 634 | 625
2017-07-27 09:00 | 600 | 595
2017-07-27 09:30 | 574 | 567
2017-07-27 10:00 | 543 | 537
2017-07-27 10:30 | 519 | 515
2017-07-27 11:00 | 504 | 501
2017-07-27 11:30 | 494 | 491
2017-07-27 12:00 | 488 | 486
2017-07-27 12:30 | 485 | 483
2017-07-27 13:00 | 482 | 481
2017-07-27 13:30 | 490 | 489
2017-07-27 14:00 | 496 | 495
2017-07-27 14:30 | 503 | 502
2017-07-27 15:00 | 507 | 506
2017-07-27 15:30 | 512 | 512
2017-07-27 16:00 | 528 | 528
2017-07-27 16:30 | 541 | 541
2017-07-27 17:00 | 560 | 559
2017-07-27 17:30 | 583 | 583
2017-07-27 18:00 | 600 | 600
2017-07-27 18:30 | 603 | 603
2017-07-27 19:00 | 605 | 605
2017-07-27 19:30 | 604 | 603
2017-07-27 20:00 | 607 | 606
2017-07-27 20:30 | 607 | 607
2017-07-27 21:00 | 582 | 581
2017-07-27 21:30 | 560 | 557
2017-07-27 22:00 | 537 | 533
2017-07-27 22:30 | 517 | 513
2017-07-27 23:00 | 498 | 494
2017-07-27 23:30 | 481 | 475
2017-07-28 | 451 | 443
2017-07-28 00:30 | 421 | 409
2017-07-28 01:00 | 403 | 391
2017-07-28 01:30 | 380 | 374
2017-07-28 02:00 | 372 | 365
2017-07-28 02:30 | 360 | 353
2017-07-28 03:00 | 354 | 347
2017-07-28 03:30 | 348 | 341
2017-07-28 04:00 | 356 | 349
2017-07-28 04:30 | 369 | 363
2017-07-28 05:00 | 394 | 389
2017-07-28 05:30 | 428 | 425
2017-07-28 06:00 | 464 | 460
2017-07-28 06:30 | 526 | 519
2017-07-28 07:00 | 572 | 567
2017-07-28 07:30 | 595 | 588
2017-07-28 08:00 | 586 | 580
2017-07-28 08:30 | 579 | 571
2017-07-28 09:00 | 561 | 551
2017-07-28 09:30 | 548 | 535
2017-07-28 10:00 | 538 | 525
2017-07-28 10:30 | 508 | 503
2017-07-28 11:00 | 495 | 492
2017-07-28 11:30 | 483 | 480
2017-07-28 12:00 | 472 | 469
2017-07-28 12:30 | 470 | 466
2017-07-28 13:00 | 468 | 465
2017-07-28 13:30 | 468 | 467
2017-07-28 14:00 | 470 | 468
2017-07-28 14:30 | 478 | 476
2017-07-28 15:00 | 481 | 480
2017-07-28 15:30 | 484 | 483
2017-07-28 16:00 | 494 | 493
2017-07-28 16:30 | 500 | 499
2017-07-28 17:00 | 519 | 519
2017-07-28 17:30 | 530 | 529
2017-07-28 18:00 | 547 | 545
2017-07-28 18:30 | 548 | 545
2017-07-28 19:00 | 550 | 546
2017-07-28 19:30 | 546 | 542
2017-07-28 20:00 | 542 | 537
2017-07-28 20:30 | 541 | 538
2017-07-28 21:00 | 524 | 520
2017-07-28 21:30 | 505 | 500
2017-07-28 22:00 | 499 | 493
2017-07-28 22:30 | 475 | 470
2017-07-28 23:00 | 455 | 452
2017-07-28 23:30 | 437 | 436
2017-07-29 | 420 | 417
2017-07-29 00:30 | 384 | 380
2017-07-29 01:00 | 377 | 372
2017-07-29 01:30 | 374 | 368
2017-07-29 02:00 | 362 | 355
2017-07-29 02:30 | 357 | 350
2017-07-29 03:00 | 352 | 345
2017-07-29 03:30 | 353 | 345
2017-07-29 04:00 | 348 | 341
2017-07-29 04:30 | 351 | 343
2017-07-29 05:00 | 358 | 351
2017-07-29 05:30 | 375 | 369
2017-07-29 06:00 | 398 | 392
2017-07-29 06:30 | 424 | 419
2017-07-29 07:00 | 445 | 440
2017-07-29 07:30 | 461 | 458
2017-07-29 08:00 | 470 | 468
2017-07-29 08:30 | 479 | 477
2017-07-29 09:00 | 473 | 471
2017-07-29 09:30 | 458 | 456
2017-07-29 10:00 | 438 | 436
2017-07-29 10:30 | 416 | 413
2017-07-29 11:00 | 400 | 397
2017-07-29 11:30 | 387 | 384
2017-07-29 12:00 | 374 | 371
2017-07-29 12:30 | 370 | 368
2017-07-29 13:00 | 368 | 365
2017-07-29 13:30 | 369 | 366
2017-07-29 14:00 | 374 | 371
2017-07-29 14:30 | 383 | 380
2017-07-29 15:00 | 397 | 394
2017-07-29 15:30 | 413 | 410
2017-07-29 16:00 | 433 | 430
2017-07-29 16:30 | 453 | 451
2017-07-29 17:00 | 472 | 470
2017-07-29 17:30 | 484 | 483
2017-07-29 18:00 | 505 | 504
2017-07-29 18:30 | 502 | 501
2017-07-29 19:00 | 503 | 503
2017-07-29 19:30 | 504 | 504
2017-07-29 20:00 | 502 | 501
2017-07-29 20:30 | 506 | 505
2017-07-29 21:00 | 491 | 489
2017-07-29 21:30 | 482 | 480
2017-07-29 22:00 | 479 | 478
2017-07-29 22:30 | 474 | 473
2017-07-29 23:00 | 469 | 468
2017-07-29 23:30 | 461 | 460
2017-07-30 | 444 | 441
2017-07-30 00:30 | 422 | 419
2017-07-30 01:00 | 400 | 396
2017-07-30 01:30 | 376 | 370
2017-07-30 02:00 | 362 | 355
2017-07-30 02:30 | 352 | 344
2017-07-30 03:00 | 340 | 332
2017-07-30 03:30 | 333 | 325
2017-07-30 04:00 | 332 | 324
2017-07-30 04:30 | 335 | 327
2017-07-30 05:00 | 339 | 332
2017-07-30 05:30 | 350 | 343
2017-07-30 06:00 | 363 | 357
2017-07-30 06:30 | 393 | 386
2017-07-30 07:00 | 415 | 408
2017-07-30 07:30 | 442 | 438
2017-07-30 08:00 | 450 | 447
2017-07-30 08:30 | 454 | 451
2017-07-30 09:00 | 452 | 449
2017-07-30 09:30 | 444 | 441
2017-07-30 10:00 | 425 | 422
2017-07-30 10:30 | 404 | 401
2017-07-30 11:00 | 383 | 380
2017-07-30 11:30 | 371 | 367
2017-07-30 12:00 | 359 | 355
2017-07-30 12:30 | 354 | 350
2017-07-30 13:00 | 350 | 346
2017-07-30 13:30 | 351 | 347
2017-07-30 14:00 | 359 | 356
2017-07-30 14:30 | 373 | 369
2017-07-30 15:00 | 385 | 382
2017-07-30 15:30 | 399 | 396
2017-07-30 16:00 | 426 | 424
2017-07-30 16:30 | 447 | 445
2017-07-30 17:00 | 464 | 463
2017-07-30 17:30 | 477 | 474
2017-07-30 18:00 | 490 | 489
2017-07-30 18:30 | 495 | 494
2017-07-30 19:00 | 497 | 495
2017-07-30 19:30 | 496 | 493
2017-07-30 20:00 | 497 | 494
2017-07-30 20:30 | 500 | 497
2017-07-30 21:00 | 486 | 484
2017-07-30 21:30 | 473 | 470
2017-07-30 22:00 | 470 | 466
2017-07-30 22:30 | 461 | 457
2017-07-30 23:00 | 452 | 448
2017-07-30 23:30 | 432 | 430
2017-07-31 | 404 | 402
2017-07-31 00:30 | 379 | 375
2017-07-31 01:00 | 364 | 360
2017-07-31 01:30 | 360 | 354
2017-07-31 02:00 | 353 | 347
2017-07-31 02:30 | 347 | 341
2017-07-31 03:00 | 345 | 339
2017-07-31 03:30 | 347 | 341
2017-07-31 04:00 | 354 | 348
2017-07-31 04:30 | 361 | 356
2017-07-31 05:00 | 371 | 367
2017-07-31 05:30 | 400 | 397
2017-07-31 06:00 | 435 | 434
2017-07-31 06:30 | 485 | 485
2017-07-31 07:00 | 538 | 538
2017-07-31 07:30 | 561 | 560
2017-07-31 08:00 | 566 | 566
2017-07-31 08:30 | 559 | 559
2017-07-31 09:00 | 536 | 536
2017-07-31 09:30 | 519 | 518
2017-07-31 10:00 | 497 | 496
2017-07-31 10:30 | 486 | 485
2017-07-31 11:00 | 479 | 477
2017-07-31 11:30 | 472 | 470
2017-07-31 12:00 | 466 | 465
2017-07-31 12:30 | 462 | 461
2017-07-31 13:00 | 465 | 464
2017-07-31 13:30 | 471 | 471
2017-07-31 14:00 | 484 | 484
2017-07-31 14:30 | 492 | 492
2017-07-31 15:00 | 500 | 499
2017-07-31 15:30 | 514 | 513
2017-07-31 16:00 | 533 | 532
2017-07-31 16:30 | 550 | 548
2017-07-31 17:00 | 561 | 559
2017-07-31 17:30 | 584 | 582
2017-07-31 18:00 | 606 | 603
2017-07-31 18:30 | 605 | 602
2017-07-31 19:00 | 603 | 599
2017-07-31 19:30 | 591 | 588
2017-07-31 20:00 | 583 | 581
2017-07-31 20:30 | 577 | 574
2017-07-31 21:00 | 558 | 554
2017-07-31 21:30 | 525 | 523
2017-07-31 22:00 | 516 | 514
2017-07-31 22:30 | 506 | 503
2017-07-31 23:00 | 503 | 499
2017-07-31 23:30 | 481 | 478
2017-08-01 | 447 | 444
2017-08-01 00:30 | 418 | 415
2017-08-01 01:00 | 401 | 397
2017-08-01 01:30 | 383 | 379
2017-08-01 02:00 | 372 | 367
2017-08-01 02:30 | 366 | 361
2017-08-01 03:00 | 365 | 360
2017-08-01 03:30 | 371 | 367
2017-08-01 04:00 | 376 | 371
2017-08-01 04:30 | 381 | 377
2017-08-01 05:00 | 398 | 395
2017-08-01 05:30 | 424 | 422
2017-08-01 06:00 | 457 | 456
2017-08-01 06:30 | 518 | 518
2017-08-01 07:00 | 555 | 555
2017-08-01 07:30 | 578 | 578
2017-08-01 08:00 | 573 | 572
2017-08-01 08:30 | 494 | 494
2017-08-01 09:00 | 475 | 475
2017-08-01 09:30 | 449 | 449
2017-08-01 10:00 | 432 | 431
2017-08-01 10:30 | 423 | 422
2017-08-01 11:00 | 411 | 410
2017-08-01 11:30 | 404 | 403
2017-08-01 12:00 | 399 | 398
2017-08-01 12:30 | 397 | 396
2017-08-01 13:00 | 397 | 396
2017-08-01 13:30 | 402 | 401
2017-08-01 14:00 | 408 | 407
2017-08-01 14:30 | 420 | 419
2017-08-01 15:00 | 428 | 427
2017-08-01 15:30 | 442 | 441
2017-08-01 16:00 | 455 | 454
2017-08-01 16:30 | 472 | 471
2017-08-01 17:00 | 497 | 496
2017-08-01 17:30 | 517 | 517
2017-08-01 18:00 | 538 | 538
2017-08-01 18:30 | 545 | 544
2017-08-01 19:00 | 546 | 546
2017-08-01 19:30 | 537 | 536
2017-08-01 20:00 | 539 | 538
2017-08-01 20:30 | 534 | 532
2017-08-01 21:00 | 521 | 518
2017-08-01 21:30 | 504 | 501
2017-08-01 22:00 | 488 | 485
2017-08-01 22:30 | 466 | 464
2017-08-01 23:00 | 450 | 447
2017-08-01 23:30 | 432 | 429
2017-08-02 | 401 | 398
2017-08-02 00:30 | 380 | 376
2017-08-02 01:00 | 362 | 357
2017-08-02 01:30 | 345 | 339
2017-08-02 02:00 | 335 | 328
2017-08-02 02:30 | 328 | 321
2017-08-02 03:00 | 322 | 315
2017-08-02 03:30 | 323 | 316
2017-08-02 04:00 | 323 | 317
2017-08-02 04:30 | 333 | 327
2017-08-02 05:00 | 352 | 347
2017-08-02 05:30 | 383 | 379
2017-08-02 06:00 | 415 | 413
2017-08-02 06:30 | 471 | 470
2017-08-02 07:00 | 510 | 509
2017-08-02 07:30 | 529 | 528
2017-08-02 08:00 | 524 | 524
2017-08-02 08:30 | 505 | 504
2017-08-02 09:00 | 488 | 487
2017-08-02 09:30 | 464 | 463
2017-08-02 10:00 | 443 | 442
2017-08-02 10:30 | 427 | 425
2017-08-02 11:00 | 411 | 408
2017-08-02 11:30 | 405 | 403
2017-08-02 12:00 | 399 | 397
2017-08-02 12:30 | 398 | 396
2017-08-02 13:00 | 408 | 406
2017-08-02 13:30 | 413 | 412
2017-08-02 14:00 | 417 | 416
2017-08-02 14:30 | 425 | 423
2017-08-02 15:00 | 430 | 428
2017-08-02 15:30 | 439 | 437
2017-08-02 16:00 | 453 | 451
2017-08-02 16:30 | 472 | 470
2017-08-02 17:00 | 490 | 489
2017-08-02 17:30 | 512 | 511
2017-08-02 18:00 | 537 | 537
2017-08-02 18:30 | 538 | 538
2017-08-02 19:00 | 542 | 541
2017-08-02 19:30 | 541 | 540
2017-08-02 20:00 | 541 | 539
2017-08-02 20:30 | 537 | 536
2017-08-02 21:00 | 520 | 518
2017-08-02 21:30 | 506 | 502
2017-08-02 22:00 | 496 | 492
2017-08-02 22:30 | 468 | 465
2017-08-02 23:00 | 440 | 438
2017-08-02 23:30 | 424 | 423
2017-08-03 | 397 | 395
2017-08-03 00:30 | 369 | 366
2017-08-03 01:00 | 354 | 350
2017-08-03 01:30 | 337 | 330
2017-08-03 02:00 | 324 | 317
2017-08-03 02:30 | 319 | 312
2017-08-03 03:00 | 320 | 312
2017-08-03 03:30 | 324 | 316
2017-08-03 04:00 | 327 | 320
2017-08-03 04:30 | 337 | 331
2017-08-03 05:00 | 353 | 348
2017-08-03 05:30 | 372 | 368
2017-08-03 06:00 | 402 | 399
2017-08-03 06:30 | 456 | 448
2017-08-03 07:00 | 488 | 480
2017-08-03 07:30 | 518 | 511
2017-08-03 08:00 | 525 | 513
2017-08-03 08:30 | 517 | 505
2017-08-03 09:00 | 507 | 494
2017-08-03 09:30 | 492 | 478
2017-08-03 10:00 | 475 | 459
2017-08-03 10:30 | 459 | 445
2017-08-03 11:00 | 445 | 433
2017-08-03 11:30 | 434 | 432
2017-08-03 12:00 | 435 | 432
2017-08-03 12:30 | 439 | 437
2017-08-03 13:00 | 434 | 432
2017-08-03 13:30 | 434 | 432
2017-08-03 14:00 | 437 | 435
2017-08-03 14:30 | 437 | 435
2017-08-03 15:00 | 439 | 437
2017-08-03 15:30 | 447 | 445
2017-08-03 16:00 | 465 | 463
2017-08-03 16:30 | 479 | 477
2017-08-03 17:00 | 493 | 491
2017-08-03 17:30 | 520 | 518
2017-08-03 18:00 | 543 | 542
2017-08-03 18:30 | 556 | 555
2017-08-03 19:00 | 540 | 540
2017-08-03 19:30 | 533 | 532
2017-08-03 20:00 | 532 | 531
2017-08-03 20:30 | 533 | 529
2017-08-03 21:00 | 517 | 514
2017-08-03 21:30 | 505 | 502
2017-08-03 22:00 | 487 | 485
2017-08-03 22:30 | 478 | 477
2017-08-03 23:00 | 457 | 456
2017-08-03 23:30 | 432 | 430
2017-08-04 | 399 | 397
2017-08-04 00:30 | 379 | 376
2017-08-04 01:00 | 360 | 356
2017-08-04 01:30 | 344 | 338
2017-08-04 02:00 | 333 | 327
2017-08-04 02:30 | 323 | 316
2017-08-04 03:00 | 319 | 313
2017-08-04 03:30 | 321 | 314
2017-08-04 04:00 | 322 | 316
2017-08-04 04:30 | 329 | 323
2017-08-04 05:00 | 344 | 339
2017-08-04 05:30 | 372 | 368
2017-08-04 06:00 | 406 | 403
2017-08-04 06:30 | 452 | 450
2017-08-04 07:00 | 491 | 490
2017-08-04 07:30 | 516 | 515
2017-08-04 08:00 | 517 | 515
2017-08-04 08:30 | 503 | 500
2017-08-04 09:00 | 478 | 476
2017-08-04 09:30 | 460 | 457
2017-08-04 10:00 | 441 | 439
2017-08-04 10:30 | 424 | 422
2017-08-04 11:00 | 412 | 410
2017-08-04 11:30 | 395 | 395
2017-08-04 12:00 | 392 | 392
2017-08-04 12:30 | 389 | 388
2017-08-04 13:00 | 387 | 386
2017-08-04 13:30 | 389 | 389
2017-08-04 14:00 | 398 | 397
2017-08-04 14:30 | 407 | 407
2017-08-04 15:00 | 463 | 463
2017-08-04 15:30 | 489 | 489
2017-08-04 16:00 | 519 | 519
2017-08-04 16:30 | 542 | 541
2017-08-04 17:00 | 567 | 565
2017-08-04 17:30 | 584 | 583
2017-08-04 18:00 | 598 | 597
2017-08-04 18:30 | 590 | 589
2017-08-04 19:00 | 595 | 594
2017-08-04 19:30 | 591 | 589
2017-08-04 20:00 | 589 | 588
2017-08-04 20:30 | 583 | 582
2017-08-04 21:00 | 570 | 568
2017-08-04 21:30 | 547 | 545
2017-08-04 22:00 | 534 | 532
2017-08-04 22:30 | 518 | 516
2017-08-04 23:00 | 500 | 498
2017-08-04 23:30 | 488 | 485
2017-08-05 | 459 | 456
2017-08-05 00:30 | 429 | 426
2017-08-05 01:00 | 407 | 403
2017-08-05 01:30 | 392 | 384
2017-08-05 02:00 | 379 | 369
2017-08-05 02:30 | 358 | 346
2017-08-05 03:00 | 348 | 335
2017-08-05 03:30 | 345 | 331
2017-08-05 04:00 | 343 | 329
2017-08-05 04:30 | 354 | 341
2017-08-05 05:00 | 352 | 339
2017-08-05 05:30 | 375 | 363
2017-08-05 06:00 | 399 | 389
2017-08-05 06:30 | 428 | 419
2017-08-05 07:00 | 453 | 447
2017-08-05 07:30 | 474 | 471
2017-08-05 08:00 | 476 | 474
2017-08-05 08:30 | 475 | 473
2017-08-05 09:00 | 464 | 462
2017-08-05 09:30 | 453 | 451
2017-08-05 10:00 | 434 | 432
2017-08-05 10:30 | 415 | 413
2017-08-05 11:00 | 393 | 390
2017-08-05 11:30 | 382 | 378
2017-08-05 12:00 | 373 | 369
2017-08-05 12:30 | 365 | 361
2017-08-05 13:00 | 363 | 359
2017-08-05 13:30 | 361 | 357
2017-08-05 14:00 | 359 | 355
2017-08-05 14:30 | 371 | 367
2017-08-05 15:00 | 359 | 355
2017-08-05 15:30 | 373 | 370
2017-08-05 16:00 | 399 | 396
2017-08-05 16:30 | 429 | 426
2017-08-05 17:00 | 463 | 460
2017-08-05 17:30 | 489 | 487
2017-08-05 18:00 | 520 | 519
2017-08-05 18:30 | 535 | 532
2017-08-05 19:00 | 539 | 537
2017-08-05 19:30 | 525 | 523
2017-08-05 20:00 | 528 | 526
2017-08-05 20:30 | 533 | 530
2017-08-05 21:00 | 519 | 517
2017-08-05 21:30 | 505 | 504
2017-08-05 22:00 | 493 | 493
2017-08-05 22:30 | 478 | 477
2017-08-05 23:00 | 472 | 471
2017-08-05 23:30 | 456 | 454
2017-08-06 | 421 | 418
2017-08-06 00:30 | 395 | 389
2017-08-06 01:00 | 375 | 368
2017-08-06 01:30 | 357 | 350
2017-08-06 02:00 | 343 | 333
2017-08-06 02:30 | 331 | 320
2017-08-06 03:00 | 326 | 315
2017-08-06 03:30 | 324 | 312
2017-08-06 04:00 | 324 | 312
2017-08-06 04:30 | 325 | 313
2017-08-06 05:00 | 333 | 322
2017-08-06 05:30 | 347 | 336
2017-08-06 06:00 | 356 | 347
2017-08-06 06:30 | 378 | 369
2017-08-06 07:00 | 398 | 389
2017-08-06 07:30 | 433 | 426
2017-08-06 08:00 | 451 | 445
2017-08-06 08:30 | 458 | 453
2017-08-06 09:00 | 453 | 448
2017-08-06 09:30 | 427 | 422
2017-08-06 10:00 | 411 | 406
2017-08-06 10:30 | 388 | 383
2017-08-06 11:00 | 366 | 360
2017-08-06 11:30 | 352 | 345
2017-08-06 12:00 | 345 | 339
2017-08-06 12:30 | 337 | 330
2017-08-06 13:00 | 331 | 324
2017-08-06 13:30 | 330 | 324
2017-08-06 14:00 | 337 | 331
2017-08-06 14:30 | 347 | 342
2017-08-06 15:00 | 365 | 361
2017-08-06 15:30 | 393 | 389
2017-08-06 16:00 | 421 | 418
2017-08-06 16:30 | 445 | 443
2017-08-06 17:00 | 468 | 467
2017-08-06 17:30 | 499 | 497
2017-08-06 18:00 | 533 | 519
2017-08-06 18:30 | 535 | 520
2017-08-06 19:00 | 537 | 523
2017-08-06 19:30 | 519 | 508
2017-08-06 20:00 | 511 | 502
2017-08-06 20:30 | 510 | 503
2017-08-06 21:00 | 486 | 484
2017-08-06 21:30 | 464 | 462
2017-08-06 22:00 | 455 | 453
2017-08-06 22:30 | 445 | 442
2017-08-06 23:00 | 436 | 433
2017-08-06 23:30 | 429 | 425
2017-08-07 | 412 | 407
2017-08-07 00:30 | 392 | 385
2017-08-07 01:00 | 376 | 368
2017-08-07 01:30 | 354 | 345
2017-08-07 02:00 | 332 | 322
2017-08-07 02:30 | 323 | 311
2017-08-07 03:00 | 317 | 304
2017-08-07 03:30 | 313 | 300
2017-08-07 04:00 | 318 | 306
2017-08-07 04:30 | 332 | 321
2017-08-07 05:00 | 354 | 345
2017-08-07 05:30 | 380 | 372
2017-08-07 06:00 | 406 | 401
2017-08-07 06:30 | 465 | 462
2017-08-07 07:00 | 519 | 517
2017-08-07 07:30 | 548 | 547
2017-08-07 08:00 | 562 | 559
2017-08-07 08:30 | 552 | 549
2017-08-07 09:00 | 529 | 526
2017-08-07 09:30 | 511 | 509
2017-08-07 10:00 | 497 | 495
2017-08-07 10:30 | 499 | 497
2017-08-07 11:00 | 492 | 490
2017-08-07 11:30 | 480 | 478
2017-08-07 12:00 | 470 | 468
2017-08-07 12:30 | 464 | 462
2017-08-07 13:00 | 463 | 461
2017-08-07 13:30 | 463 | 461
2017-08-07 14:00 | 471 | 469
2017-08-07 14:30 | 482 | 480
2017-08-07 15:00 | 492 | 490
2017-08-07 15:30 | 502 | 500
2017-08-07 16:00 | 513 | 511
2017-08-07 16:30 | 530 | 528
2017-08-07 17:00 | 543 | 542
2017-08-07 17:30 | 565 | 562
2017-08-07 18:00 | 594 | 591
2017-08-07 18:30 | 599 | 593
2017-08-07 19:00 | 591 | 586
2017-08-07 19:30 | 580 | 575
2017-08-07 20:00 | 574 | 572
2017-08-07 20:30 | 574 | 571
2017-08-07 21:00 | 550 | 547
2017-08-07 21:30 | 536 | 532
2017-08-07 22:00 | 526 | 522
2017-08-07 22:30 | 495 | 492
2017-08-07 23:00 | 479 | 476
2017-08-07 23:30 | 465 | 460
2017-08-08 | 441 | 436
2017-08-08 00:30 | 417 | 411
2017-08-08 01:00 | 396 | 388
2017-08-08 01:30 | 377 | 368
2017-08-08 02:00 | 369 | 359
2017-08-08 02:30 | 363 | 352
2017-08-08 03:00 | 359 | 348
2017-08-08 03:30 | 354 | 344
2017-08-08 04:00 | 354 | 344
2017-08-08 04:30 | 371 | 362
2017-08-08 05:00 | 394 | 387
2017-08-08 05:30 | 427 | 421
2017-08-08 06:00 | 463 | 459
2017-08-08 06:30 | 515 | 513
2017-08-08 07:00 | 574 | 569
2017-08-08 07:30 | 599 | 592
2017-08-08 08:00 | 598 | 590
2017-08-08 08:30 | 576 | 567
2017-08-08 09:00 | 549 | 539
2017-08-08 09:30 | 524 | 515
2017-08-08 10:00 | 497 | 494
2017-08-08 10:30 | 480 | 477
2017-08-08 11:00 | 465 | 462
2017-08-08 11:30 | 451 | 449
2017-08-08 12:00 | 448 | 447
2017-08-08 12:30 | 451 | 449
2017-08-08 13:00 | 450 | 448
2017-08-08 13:30 | 450 | 449
2017-08-08 14:00 | 454 | 453
2017-08-08 14:30 | 464 | 463
2017-08-08 15:00 | 476 | 475
2017-08-08 15:30 | 491 | 490
2017-08-08 16:00 | 509 | 509
2017-08-08 16:30 | 525 | 524
2017-08-08 17:00 | 540 | 540
2017-08-08 17:30 | 568 | 568
2017-08-08 18:00 | 595 | 594
2017-08-08 18:30 | 601 | 599
2017-08-08 19:00 | 597 | 595
2017-08-08 19:30 | 595 | 593
2017-08-08 20:00 | 598 | 594
2017-08-08 20:30 | 598 | 596
2017-08-08 21:00 | 580 | 577
2017-08-08 21:30 | 559 | 556
2017-08-08 22:00 | 547 | 544
2017-08-08 22:30 | 523 | 518
2017-08-08 23:00 | 501 | 497
2017-08-08 23:30 | 481 | 477
2017-08-09 | 452 | 447
2017-08-09 00:30 | 430 | 424
2017-08-09 01:00 | 413 | 405
2017-08-09 01:30 | 397 | 387
2017-08-09 02:00 | 387 | 377
2017-08-09 02:30 | 379 | 369
2017-08-09 03:00 | 376 | 365
2017-08-09 03:30 | 373 | 363
2017-08-09 04:00 | 377 | 366
2017-08-09 04:30 | 393 | 383
2017-08-09 05:00 | 407 | 398
2017-08-09 05:30 | 439 | 434
2017-08-09 06:00 | 479 | 477
2017-08-09 06:30 | 539 | 536
2017-08-09 07:00 | 582 | 577
2017-08-09 07:30 | 613 | 604
2017-08-09 08:00 | 611 | 601
2017-08-09 08:30 | 589 | 579
2017-08-09 09:00 | 553 | 543
2017-08-09 09:30 | 524 | 520
2017-08-09 10:00 | 503 | 499
2017-08-09 10:30 | 482 | 479
2017-08-09 11:00 | 460 | 458
2017-08-09 11:30 | 449 | 448
2017-08-09 12:00 | 442 | 441
2017-08-09 12:30 | 440 | 439
2017-08-09 13:00 | 441 | 440
2017-08-09 13:30 | 445 | 445
2017-08-09 14:00 | 451 | 451
2017-08-09 14:30 | 452 | 451
2017-08-09 15:00 | 457 | 457
2017-08-09 15:30 | 474 | 474
2017-08-09 16:00 | 492 | 492
2017-08-09 16:30 | 508 | 508
2017-08-09 17:00 | 530 | 529
2017-08-09 17:30 | 543 | 541
2017-08-09 18:00 | 562 | 560
2017-08-09 18:30 | 563 | 560
2017-08-09 19:00 | 568 | 565
2017-08-09 19:30 | 566 | 563
2017-08-09 20:00 | 566 | 563
2017-08-09 20:30 | 571 | 568
2017-08-09 21:00 | 561 | 559
2017-08-09 21:30 | 548 | 546
2017-08-09 22:00 | 542 | 540
2017-08-09 22:30 | 517 | 515
2017-08-09 23:00 | 497 | 494
2017-08-09 23:30 | 482 | 479
2017-08-10 | 455 | 450
2017-08-10 00:30 | 430 | 421
2017-08-10 01:00 | 413 | 405
2017-08-10 01:30 | 400 | 391
2017-08-10 02:00 | 389 | 379
2017-08-10 02:30 | 380 | 368
2017-08-10 03:00 | 376 | 364
2017-08-10 03:30 | 368 | 356
2017-08-10 04:00 | 369 | 358
2017-08-10 04:30 | 371 | 361
2017-08-10 05:00 | 390 | 381
2017-08-10 05:30 | 426 | 420
2017-08-10 06:00 | 462 | 458
2017-08-10 06:30 | 531 | 529
2017-08-10 07:00 | 587 | 579
2017-08-10 07:30 | 617 | 606
2017-08-10 08:00 | 617 | 606
2017-08-10 08:30 | 595 | 584
2017-08-10 09:00 | 564 | 554
2017-08-10 09:30 | 526 | 524
2017-08-10 10:00 | 507 | 506
2017-08-10 10:30 | 489 | 488
2017-08-10 11:00 | 477 | 477
2017-08-10 11:30 | 464 | 464
2017-08-10 12:00 | 455 | 454
2017-08-10 12:30 | 449 | 448
2017-08-10 13:00 | 440 | 440
2017-08-10 13:30 | 437 | 437
2017-08-10 14:00 | 440 | 439
2017-08-10 14:30 | 458 | 458
2017-08-10 15:00 | 472 | 472
2017-08-10 15:30 | 480 | 480
2017-08-10 16:00 | 506 | 505
2017-08-10 16:30 | 522 | 522
2017-08-10 17:00 | 541 | 541
2017-08-10 17:30 | 564 | 563
2017-08-10 18:00 | 582 | 580
2017-08-10 18:30 | 580 | 577
2017-08-10 19:00 | 581 | 578
2017-08-10 19:30 | 578 | 575
2017-08-10 20:00 | 582 | 578
2017-08-10 20:30 | 582 | 578
2017-08-10 21:00 | 557 | 555
2017-08-10 21:30 | 536 | 534
2017-08-10 22:00 | 530 | 527
2017-08-10 22:30 | 496 | 493
2017-08-10 23:00 | 481 | 479
2017-08-10 23:30 | 464 | 461
2017-08-11 | 440 | 436
2017-08-11 00:30 | 416 | 410
2017-08-11 01:00 | 405 | 398
2017-08-11 01:30 | 390 | 381
2017-08-11 02:00 | 375 | 365
2017-08-11 02:30 | 361 | 350
2017-08-11 03:00 | 363 | 351
2017-08-11 03:30 | 360 | 348
2017-08-11 04:00 | 354 | 343
2017-08-11 04:30 | 361 | 351
2017-08-11 05:00 | 377 | 368
2017-08-11 05:30 | 413 | 406
2017-08-11 06:00 | 449 | 445
2017-08-11 06:30 | 503 | 499
2017-08-11 07:00 | 545 | 543
2017-08-11 07:30 | 586 | 576
2017-08-11 08:00 | 584 | 572
2017-08-11 08:30 | 564 | 553
2017-08-11 09:00 | 547 | 535
2017-08-11 09:30 | 517 | 507
2017-08-11 10:00 | 490 | 486
2017-08-11 10:30 | 476 | 473
2017-08-11 11:00 | 464 | 461
2017-08-11 11:30 | 457 | 454
2017-08-11 12:00 | 453 | 450
2017-08-11 12:30 | 451 | 448
2017-08-11 13:00 | 453 | 450
2017-08-11 13:30 | 460 | 457
2017-08-11 14:00 | 466 | 463
2017-08-11 14:30 | 478 | 475
2017-08-11 15:00 | 485 | 482
2017-08-11 15:30 | 496 | 494
2017-08-11 16:00 | 513 | 510
2017-08-11 16:30 | 521 | 519
2017-08-11 17:00 | 537 | 535
2017-08-11 17:30 | 547 | 544
2017-08-11 18:00 | 558 | 554
2017-08-11 18:30 | 563 | 552
2017-08-11 19:00 | 559 | 549
2017-08-11 19:30 | 543 | 540
2017-08-11 20:00 | 545 | 541
2017-08-11 20:30 | 549 | 545
2017-08-11 21:00 | 537 | 533
2017-08-11 21:30 | 523 | 520
2017-08-11 22:00 | 516 | 512
2017-08-11 22:30 | 486 | 484
2017-08-11 23:00 | 466 | 463
2017-08-11 23:30 | 449 | 446
2017-08-12 | 430 | 425
2017-08-12 00:30 | 408 | 402
2017-08-12 01:00 | 390 | 382
2017-08-12 01:30 | 379 | 370
2017-08-12 02:00 | 360 | 348
2017-08-12 02:30 | 349 | 334
2017-08-12 03:00 | 339 | 323
2017-08-12 03:30 | 333 | 316
2017-08-12 04:00 | 331 | 314
2017-08-12 04:30 | 334 | 318
2017-08-12 05:00 | 340 | 324
2017-08-12 05:30 | 358 | 343
2017-08-12 06:00 | 378 | 366
2017-08-12 06:30 | 409 | 398
2017-08-12 07:00 | 427 | 416
2017-08-12 07:30 | 450 | 441
2017-08-12 08:00 | 460 | 452
2017-08-12 08:30 | 457 | 450
2017-08-12 09:00 | 451 | 444
2017-08-12 09:30 | 442 | 435
2017-08-12 10:00 | 425 | 419
2017-08-12 10:30 | 440 | 434
2017-08-12 11:00 | 456 | 451
2017-08-12 11:30 | 430 | 425
2017-08-12 12:00 | 405 | 399
2017-08-12 12:30 | 408 | 403
2017-08-12 13:00 | 415 | 409
2017-08-12 13:30 | 410 | 404
2017-08-12 14:00 | 400 | 394
2017-08-12 14:30 | 396 | 390
2017-08-12 15:00 | 399 | 394
2017-08-12 15:30 | 418 | 412
2017-08-12 16:00 | 441 | 436
2017-08-12 16:30 | 461 | 456
2017-08-12 17:00 | 481 | 476
2017-08-12 17:30 | 492 | 486
2017-08-12 18:00 | 507 | 504
2017-08-12 18:30 | 513 | 508
2017-08-12 19:00 | 513 | 507
2017-08-12 19:30 | 507 | 501
2017-08-12 20:00 | 505 | 499
2017-08-12 20:30 | 505 | 500
2017-08-12 21:00 | 483 | 480
2017-08-12 21:30 | 479 | 475
2017-08-12 22:00 | 472 | 467
2017-08-12 22:30 | 460 | 454
2017-08-12 23:00 | 449 | 444
2017-08-12 23:30 | 436 | 430
2017-08-13 | 421 | 412
2017-08-13 00:30 | 404 | 393
2017-08-13 01:00 | 386 | 373
2017-08-13 01:30 | 373 | 357
2017-08-13 02:00 | 361 | 344
2017-08-13 02:30 | 352 | 335
2017-08-13 03:00 | 348 | 331
2017-08-13 03:30 | 345 | 329
2017-08-13 04:00 | 342 | 326
2017-08-13 04:30 | 345 | 329
2017-08-13 05:00 | 345 | 330
2017-08-13 05:30 | 353 | 338
2017-08-13 06:00 | 363 | 349
2017-08-13 06:30 | 377 | 363
2017-08-13 07:00 | 388 | 374
2017-08-13 07:30 | 379 | 367
2017-08-13 08:00 | 387 | 376
2017-08-13 08:30 | 396 | 385
2017-08-13 09:00 | 390 | 380
2017-08-13 09:30 | 380 | 371
2017-08-13 10:00 | 365 | 356
2017-08-13 10:30 | 358 | 349
2017-08-13 11:00 | 345 | 336
2017-08-13 11:30 | 339 | 331
2017-08-13 12:00 | 329 | 320
2017-08-13 12:30 | 360 | 351
2017-08-13 13:00 | 366 | 356
2017-08-13 13:30 | 366 | 357
2017-08-13 14:00 | 366 | 358
2017-08-13 14:30 | 371 | 362
2017-08-13 15:00 | 380 | 372
2017-08-13 15:30 | 401 | 393
2017-08-13 16:00 | 424 | 417
2017-08-13 16:30 | 444 | 439
2017-08-13 17:00 | 463 | 458
2017-08-13 17:30 | 472 | 468
2017-08-13 18:00 | 485 | 483
2017-08-13 18:30 | 490 | 487
2017-08-13 19:00 | 490 | 487
2017-08-13 19:30 | 485 | 482
2017-08-13 20:00 | 482 | 480
2017-08-13 20:30 | 482 | 481
2017-08-13 21:00 | 476 | 473
2017-08-13 21:30 | 470 | 466
2017-08-13 22:00 | 467 | 463
2017-08-13 22:30 | 447 | 442
2017-08-13 23:00 | 436 | 431
2017-08-13 23:30 | 430 | 424
2017-08-14 | 411 | 403
2017-08-14 00:30 | 385 | 375
2017-08-14 01:00 | 371 | 359
2017-08-14 01:30 | 357 | 343
2017-08-14 02:00 | 346 | 332
2017-08-14 02:30 | 341 | 326
2017-08-14 03:00 | 339 | 324
2017-08-14 03:30 | 339 | 324
2017-08-14 04:00 | 343 | 328
2017-08-14 04:30 | 353 | 339
2017-08-14 05:00 | 366 | 353
2017-08-14 05:30 | 392 | 382
2017-08-14 06:00 | 422 | 415
2017-08-14 06:30 | 456 | 452
2017-08-14 07:00 | 496 | 492
2017-08-14 07:30 | 522 | 519
2017-08-14 08:00 | 519 | 517
2017-08-14 08:30 | 515 | 514
2017-08-14 09:00 | 499 | 498
2017-08-14 09:30 | 487 | 485
2017-08-14 10:00 | 474 | 473
2017-08-14 10:30 | 455 | 454
2017-08-14 11:00 | 452 | 452
2017-08-14 11:30 | 451 | 450
2017-08-14 12:00 | 443 | 443
2017-08-14 12:30 | 441 | 441
2017-08-14 13:00 | 448 | 448
2017-08-14 13:30 | 463 | 463
2017-08-14 14:00 | 465 | 465
2017-08-14 14:30 | 473 | 473
2017-08-14 15:00 | 477 | 477
2017-08-14 15:30 | 475 | 475
2017-08-14 16:00 | 489 | 489
2017-08-14 16:30 | 510 | 510
2017-08-14 17:00 | 529 | 529
2017-08-14 17:30 | 539 | 539
2017-08-14 18:00 | 557 | 557
2017-08-14 18:30 | 556 | 555
2017-08-14 19:00 | 552 | 550
2017-08-14 19:30 | 543 | 540
2017-08-14 20:00 | 539 | 538
2017-08-14 20:30 | 540 | 539
2017-08-14 21:00 | 520 | 518
2017-08-14 21:30 | 498 | 496
2017-08-14 22:00 | 483 | 480
2017-08-14 22:30 | 468 | 466
2017-08-14 23:00 | 461 | 460
2017-08-14 23:30 | 447 | 446
2017-08-15 | 422 | 420
2017-08-15 00:30 | 398 | 395
2017-08-15 01:00 | 384 | 380
2017-08-15 01:30 | 372 | 367
2017-08-15 02:00 | 361 | 355
2017-08-15 02:30 | 347 | 340
2017-08-15 03:00 | 336 | 329
2017-08-15 03:30 | 331 | 324
2017-08-15 04:00 | 334 | 328
2017-08-15 04:30 | 341 | 335
2017-08-15 05:00 | 367 | 362
2017-08-15 05:30 | 394 | 391
2017-08-15 06:00 | 428 | 426
2017-08-15 06:30 | 482 | 481
2017-08-15 07:00 | 522 | 520
2017-08-15 07:30 | 541 | 540
2017-08-15 08:00 | 545 | 544
2017-08-15 08:30 | 532 | 531
2017-08-15 09:00 | 511 | 510
2017-08-15 09:30 | 489 | 488
2017-08-15 10:00 | 477 | 475
2017-08-15 10:30 | 470 | 469
2017-08-15 11:00 | 463 | 462
2017-08-15 11:30 | 457 | 455
2017-08-15 12:00 | 455 | 454
2017-08-15 12:30 | 453 | 452
2017-08-15 13:00 | 456 | 455
2017-08-15 13:30 | 460 | 460
2017-08-15 14:00 | 467 | 467
2017-08-15 14:30 | 471 | 471
2017-08-15 15:00 | 478 | 477
2017-08-15 15:30 | 492 | 492
2017-08-15 16:00 | 510 | 510
2017-08-15 16:30 | 521 | 520
2017-08-15 17:00 | 537 | 535
2017-08-15 17:30 | 545 | 543
2017-08-15 18:00 | 558 | 556
2017-08-15 18:30 | 557 | 555
2017-08-15 19:00 | 551 | 550
2017-08-15 19:30 | 546 | 544
2017-08-15 20:00 | 548 | 546
2017-08-15 20:30 | 541 | 540
2017-08-15 21:00 | 519 | 519
2017-08-15 21:30 | 502 | 501
2017-08-15 22:00 | 492 | 490
2017-08-15 22:30 | 476 | 473
2017-08-15 23:00 | 459 | 456
2017-08-15 23:30 | 445 | 443
2017-08-16 | 423 | 421
2017-08-16 00:30 | 404 | 399
2017-08-16 01:00 | 386 | 381
2017-08-16 01:30 | 369 | 362
2017-08-16 02:00 | 353 | 346
2017-08-16 02:30 | 329 | 322
2017-08-16 03:00 | 316 | 309
2017-08-16 03:30 | 311 | 304
2017-08-16 04:00 | 310 | 303
2017-08-16 04:30 | 309 | 303
2017-08-16 05:00 | 318 | 312
2017-08-16 05:30 | 345 | 341
2017-08-16 06:00 | 367 | 364
2017-08-16 06:30 | 408 | 407
2017-08-16 07:00 | 441 | 439
2017-08-16 07:30 | 463 | 462
2017-08-16 08:00 | 463 | 462
2017-08-16 08:30 | 461 | 460
2017-08-16 09:00 | 455 | 455
2017-08-16 09:30 | 450 | 450
2017-08-16 10:00 | 440 | 440
2017-08-16 10:30 | 426 | 426
2017-08-16 11:00 | 420 | 420
2017-08-16 11:30 | 419 | 418
2017-08-16 12:00 | 413 | 413
2017-08-16 12:30 | 403 | 403
2017-08-16 13:00 | 406 | 406
2017-08-16 13:30 | 415 | 415
2017-08-16 14:00 | 426 | 425
2017-08-16 14:30 | 425 | 424
2017-08-16 15:00 | 437 | 437
2017-08-16 15:30 | 442 | 441
2017-08-16 16:00 | 462 | 461
2017-08-16 16:30 | 474 | 473
2017-08-16 17:00 | 487 | 486
2017-08-16 17:30 | 492 | 491
2017-08-16 18:00 | 500 | 499
2017-08-16 18:30 | 500 | 499
2017-08-16 19:00 | 497 | 497
2017-08-16 19:30 | 488 | 488
2017-08-16 20:00 | 487 | 485
2017-08-16 20:30 | 489 | 487
2017-08-16 21:00 | 468 | 467
2017-08-16 21:30 | 443 | 442
2017-08-16 22:00 | 436 | 435
2017-08-16 22:30 | 427 | 425
2017-08-16 23:00 | 413 | 411
2017-08-16 23:30 | 405 | 401
2017-08-17 | 395 | 390
2017-08-17 00:30 | 373 | 368
2017-08-17 01:00 | 364 | 357
2017-08-17 01:30 | 349 | 342
2017-08-17 02:00 | 336 | 328
2017-08-17 02:30 | 324 | 315
2017-08-17 03:00 | 319 | 311
2017-08-17 03:30 | 314 | 304
2017-08-17 04:00 | 315 | 306
2017-08-17 04:30 | 318 | 309
2017-08-17 05:00 | 330 | 323
2017-08-17 05:30 | 361 | 356
2017-08-17 06:00 | 404 | 400
2017-08-17 06:30 | 448 | 444
2017-08-17 07:00 | 479 | 477
2017-08-17 07:30 | 497 | 496
2017-08-17 08:00 | 502 | 500
2017-08-17 08:30 | 503 | 502
2017-08-17 09:00 | 497 | 496
2017-08-17 09:30 | 487 | 486
2017-08-17 10:00 | 485 | 484
2017-08-17 10:30 | 485 | 484
2017-08-17 11:00 | 480 | 479
2017-08-17 11:30 | 471 | 470
2017-08-17 12:00 | 468 | 467
2017-08-17 12:30 | 471 | 470
2017-08-17 13:00 | 477 | 476
2017-08-17 13:30 | 483 | 482
2017-08-17 14:00 | 486 | 485
2017-08-17 14:30 | 495 | 494
2017-08-17 15:00 | 502 | 502
2017-08-17 15:30 | 512 | 511
2017-08-17 16:00 | 539 | 537
2017-08-17 16:30 | 553 | 548
2017-08-17 17:00 | 571 | 566
2017-08-17 17:30 | 575 | 570
2017-08-17 18:00 | 587 | 583
2017-08-17 18:30 | 582 | 577
2017-08-17 19:00 | 580 | 576
2017-08-17 19:30 | 575 | 570
2017-08-17 20:00 | 572 | 568
2017-08-17 20:30 | 569 | 565
2017-08-17 21:00 | 549 | 547
2017-08-17 21:30 | 528 | 523
2017-08-17 22:00 | 514 | 509
2017-08-17 22:30 | 479 | 474
2017-08-17 23:00 | 460 | 457
2017-08-17 23:30 | 445 | 442
2017-08-18 | 422 | 418
2017-08-18 00:30 | 393 | 387
2017-08-18 01:00 | 375 | 368
2017-08-18 01:30 | 367 | 359
2017-08-18 02:00 | 355 | 346
2017-08-18 02:30 | 346 | 337
2017-08-18 03:00 | 341 | 332
2017-08-18 03:30 | 341 | 332
2017-08-18 04:00 | 334 | 326
2017-08-18 04:30 | 344 | 336
2017-08-18 05:00 | 360 | 353
2017-08-18 05:30 | 394 | 388
2017-08-18 06:00 | 423 | 420
2017-08-18 06:30 | 462 | 460
2017-08-18 07:00 | 495 | 494
2017-08-18 07:30 | 525 | 523
2017-08-18 08:00 | 526 | 524
2017-08-18 08:30 | 510 | 509
2017-08-18 09:00 | 493 | 492
2017-08-18 09:30 | 480 | 479
2017-08-18 10:00 | 466 | 464
2017-08-18 10:30 | 452 | 451
2017-08-18 11:00 | 448 | 448
2017-08-18 11:30 | 438 | 438
2017-08-18 12:00 | 434 | 434
2017-08-18 12:30 | 429 | 429
2017-08-18 13:00 | 432 | 432
2017-08-18 13:30 | 441 | 441
2017-08-18 14:00 | 448 | 448
2017-08-18 14:30 | 456 | 456
2017-08-18 15:00 | 472 | 472
2017-08-18 15:30 | 482 | 482
2017-08-18 16:00 | 504 | 504
2017-08-18 16:30 | 524 | 524
2017-08-18 17:00 | 542 | 541
2017-08-18 17:30 | 543 | 541
2017-08-18 18:00 | 561 | 559
2017-08-18 18:30 | 560 | 557
2017-08-18 19:00 | 563 | 561
2017-08-18 19:30 | 554 | 551
2017-08-18 20:00 | 550 | 548
2017-08-18 20:30 | 545 | 544
2017-08-18 21:00 | 528 | 526
2017-08-18 21:30 | 511 | 509
2017-08-18 22:00 | 496 | 494
2017-08-18 22:30 | 487 | 484
2017-08-18 23:00 | 471 | 468
2017-08-18 23:30 | 457 | 453
2017-08-19 | 424 | 420
2017-08-19 00:30 | 397 | 391
2017-08-19 01:00 | 383 | 376
2017-08-19 01:30 | 371 | 362
2017-08-19 02:00 | 363 | 354
2017-08-19 02:30 | 356 | 346
2017-08-19 03:00 | 349 | 339
2017-08-19 03:30 | 348 | 337
2017-08-19 04:00 | 348 | 337
2017-08-19 04:30 | 351 | 340
2017-08-19 05:00 | 358 | 347
2017-08-19 05:30 | 373 | 363
2017-08-19 06:00 | 391 | 383
2017-08-19 06:30 | 404 | 396
2017-08-19 07:00 | 417 | 410
2017-08-19 07:30 | 434 | 428
2017-08-19 08:00 | 438 | 433
2017-08-19 08:30 | 436 | 432
2017-08-19 09:00 | 433 | 429
2017-08-19 09:30 | 423 | 420
2017-08-19 10:00 | 409 | 405
2017-08-19 10:30 | 396 | 392
2017-08-19 11:00 | 378 | 373
2017-08-19 11:30 | 364 | 360
2017-08-19 12:00 | 354 | 349
2017-08-19 12:30 | 347 | 341
2017-08-19 13:00 | 344 | 338
2017-08-19 13:30 | 345 | 338
2017-08-19 14:00 | 352 | 346
2017-08-19 14:30 | 364 | 358
2017-08-19 15:00 | 371 | 366
2017-08-19 15:30 | 383 | 378
2017-08-19 16:00 | 408 | 403
2017-08-19 16:30 | 438 | 434
2017-08-19 17:00 | 475 | 472
2017-08-19 17:30 | 495 | 492
2017-08-19 18:00 | 522 | 517
2017-08-19 18:30 | 543 | 533
2017-08-19 19:00 | 549 | 539
2017-08-19 19:30 | 543 | 532
2017-08-19 20:00 | 543 | 532
2017-08-19 20:30 | 544 | 533
2017-08-19 21:00 | 525 | 514
2017-08-19 21:30 | 515 | 504
2017-08-19 22:00 | 505 | 497
2017-08-19 22:30 | 483 | 480
2017-08-19 23:00 | 482 | 480
2017-08-19 23:30 | 470 | 467
2017-08-20 | 443 | 439
2017-08-20 00:30 | 413 | 408
2017-08-20 01:00 | 392 | 385
2017-08-20 01:30 | 376 | 369
2017-08-20 02:00 | 362 | 354
2017-08-20 02:30 | 354 | 345
2017-08-20 03:00 | 353 | 344
2017-08-20 03:30 | 351 | 342
2017-08-20 04:00 | 348 | 339
2017-08-20 04:30 | 352 | 343
2017-08-20 05:00 | 354 | 346
2017-08-20 05:30 | 361 | 353
2017-08-20 06:00 | 375 | 367
2017-08-20 06:30 | 388 | 381
2017-08-20 07:00 | 406 | 399
2017-08-20 07:30 | 420 | 414
2017-08-20 08:00 | 420 | 415
2017-08-20 08:30 | 420 | 415
2017-08-20 09:00 | 412 | 407
2017-08-20 09:30 | 398 | 394
2017-08-20 10:00 | 383 | 378
2017-08-20 10:30 | 370 | 365
2017-08-20 11:00 | 354 | 348
2017-08-20 11:30 | 340 | 335
2017-08-20 12:00 | 334 | 328
2017-08-20 12:30 | 333 | 327
2017-08-20 13:00 | 330 | 324
2017-08-20 13:30 | 333 | 327
2017-08-20 14:00 | 339 | 333
2017-08-20 14:30 | 348 | 343
2017-08-20 15:00 | 363 | 358
2017-08-20 15:30 | 384 | 379
2017-08-20 16:00 | 407 | 402
2017-08-20 16:30 | 435 | 431
2017-08-20 17:00 | 473 | 470
2017-08-20 17:30 | 499 | 497
2017-08-20 18:00 | 531 | 529
2017-08-20 18:30 | 546 | 543
2017-08-20 19:00 | 544 | 542
2017-08-20 19:30 | 539 | 537
2017-08-20 20:00 | 542 | 539
2017-08-20 20:30 | 547 | 544
2017-08-20 21:00 | 530 | 527
2017-08-20 21:30 | 512 | 509
2017-08-20 22:00 | 501 | 498
2017-08-20 22:30 | 471 | 470
2017-08-20 23:00 | 461 | 459
2017-08-20 23:30 | 453 | 452
2017-08-21 | 427 | 424
2017-08-21 00:30 | 403 | 399
2017-08-21 01:00 | 385 | 379
2017-08-21 01:30 | 372 | 365
2017-08-21 02:00 | 359 | 352
2017-08-21 02:30 | 354 | 346
2017-08-21 03:00 | 348 | 338
2017-08-21 03:30 | 349 | 339
2017-08-21 04:00 | 346 | 336
2017-08-21 04:30 | 365 | 355
2017-08-21 05:00 | 385 | 377
2017-08-21 05:30 | 415 | 410
2017-08-21 06:00 | 448 | 445
2017-08-21 06:30 | 510 | 508
2017-08-21 07:00 | 555 | 554
2017-08-21 07:30 | 572 | 571
2017-08-21 08:00 | 567 | 566
2017-08-21 08:30 | 546 | 545
2017-08-21 09:00 | 533 | 532
2017-08-21 09:30 | 527 | 525
2017-08-21 10:00 | 504 | 502
2017-08-21 10:30 | 483 | 481
2017-08-21 11:00 | 462 | 460
2017-08-21 11:30 | 455 | 454
2017-08-21 12:00 | 451 | 450
2017-08-21 12:30 | 451 | 451
2017-08-21 13:00 | 461 | 460
2017-08-21 13:30 | 480 | 479
2017-08-21 14:00 | 491 | 491
2017-08-21 14:30 | 483 | 481
2017-08-21 15:00 | 492 | 491
2017-08-21 15:30 | 514 | 512
2017-08-21 16:00 | 536 | 535
2017-08-21 16:30 | 551 | 550
2017-08-21 17:00 | 558 | 557
2017-08-21 17:30 | 573 | 571
2017-08-21 18:00 | 595 | 593
2017-08-21 18:30 | 593 | 589
2017-08-21 19:00 | 593 | 589
2017-08-21 19:30 | 584 | 578
2017-08-21 20:00 | 579 | 575
2017-08-21 20:30 | 577 | 573
2017-08-21 21:00 | 551 | 549
2017-08-21 21:30 | 526 | 525
2017-08-21 22:00 | 508 | 507
2017-08-21 22:30 | 481 | 480
2017-08-21 23:00 | 459 | 459
2017-08-21 23:30 | 446 | 444
2017-08-22 | 427 | 425
2017-08-22 00:30 | 406 | 403
2017-08-22 01:00 | 388 | 385
2017-08-22 01:30 | 380 | 376
2017-08-22 02:00 | 372 | 367
2017-08-22 02:30 | 363 | 358
2017-08-22 03:00 | 360 | 355
2017-08-22 03:30 | 359 | 353
2017-08-22 04:00 | 364 | 359
2017-08-22 04:30 | 371 | 366
2017-08-22 05:00 | 388 | 383
2017-08-22 05:30 | 417 | 413
2017-08-22 06:00 | 442 | 441
2017-08-22 06:30 | 490 | 489
2017-08-22 07:00 | 525 | 525
2017-08-22 07:30 | 547 | 547
2017-08-22 08:00 | 551 | 550
2017-08-22 08:30 | 541 | 540
2017-08-22 09:00 | 514 | 513
2017-08-22 09:30 | 500 | 499
2017-08-22 10:00 | 491 | 490
2017-08-22 10:30 | 489 | 488
2017-08-22 11:00 | 481 | 481
2017-08-22 11:30 | 473 | 473
2017-08-22 12:00 | 470 | 470
2017-08-22 12:30 | 466 | 465
2017-08-22 13:00 | 467 | 467
2017-08-22 13:30 | 474 | 473
2017-08-22 14:00 | 479 | 479
2017-08-22 14:30 | 482 | 482
2017-08-22 15:00 | 491 | 490
2017-08-22 15:30 | 506 | 505
2017-08-22 16:00 | 522 | 521
2017-08-22 16:30 | 539 | 538
2017-08-22 17:00 | 549 | 549
2017-08-22 17:30 | 556 | 555
2017-08-22 18:00 | 570 | 569
2017-08-22 18:30 | 570 | 568
2017-08-22 19:00 | 569 | 567
2017-08-22 19:30 | 561 | 558
2017-08-22 20:00 | 562 | 559
2017-08-22 20:30 | 564 | 561
2017-08-22 21:00 | 542 | 539
2017-08-22 21:30 | 519 | 517
2017-08-22 22:00 | 507 | 504
2017-08-22 22:30 | 481 | 478
2017-08-22 23:00 | 470 | 468
2017-08-22 23:30 | 449 | 447
2017-08-23 | 432 | 429
2017-08-23 00:30 | 406 | 402
2017-08-23 01:00 | 395 | 389
2017-08-23 01:30 | 383 | 376
2017-08-23 02:00 | 370 | 361
2017-08-23 02:30 | 358 | 349
2017-08-23 03:00 | 357 | 347
2017-08-23 03:30 | 356 | 346
2017-08-23 04:00 | 357 | 347
2017-08-23 04:30 | 368 | 359
2017-08-23 05:00 | 382 | 374
2017-08-23 05:30 | 407 | 401
2017-08-23 06:00 | 433 | 429
2017-08-23 06:30 | 481 | 477
2017-08-23 07:00 | 505 | 502
2017-08-23 07:30 | 526 | 523
2017-08-23 08:00 | 527 | 525
2017-08-23 08:30 | 525 | 522
2017-08-23 09:00 | 522 | 520
2017-08-23 09:30 | 514 | 512
2017-08-23 10:00 | 508 | 505
2017-08-23 10:30 | 507 | 505
2017-08-23 11:00 | 494 | 492
2017-08-23 11:30 | 475 | 474
2017-08-23 12:00 | 467 | 465
2017-08-23 12:30 | 457 | 455
2017-08-23 13:00 | 466 | 465
2017-08-23 13:30 | 474 | 473
2017-08-23 14:00 | 485 | 484
2017-08-23 14:30 | 492 | 492
2017-08-23 15:00 | 494 | 493
2017-08-23 15:30 | 505 | 504
2017-08-23 16:00 | 522 | 521
2017-08-23 16:30 | 532 | 531
2017-08-23 17:00 | 547 | 546
2017-08-23 17:30 | 559 | 558
2017-08-23 18:00 | 573 | 572
2017-08-23 18:30 | 577 | 573
2017-08-23 19:00 | 576 | 571
2017-08-23 19:30 | 565 | 560
2017-08-23 20:00 | 562 | 559
2017-08-23 20:30 | 561 | 558
2017-08-23 21:00 | 535 | 534
2017-08-23 21:30 | 510 | 508
2017-08-23 22:00 | 496 | 494
2017-08-23 22:30 | 471 | 470
2017-08-23 23:00 | 452 | 451
2017-08-23 23:30 | 441 | 439
2017-08-24 | 417 | 415
2017-08-24 00:30 | 393 | 389
2017-08-24 01:00 | 383 | 379
2017-08-24 01:30 | 378 | 373
2017-08-24 02:00 | 371 | 365
2017-08-24 02:30 | 356 | 350
2017-08-24 03:00 | 353 | 347
2017-08-24 03:30 | 345 | 340
2017-08-24 04:00 | 345 | 339
2017-08-24 04:30 | 350 | 345
2017-08-24 05:00 | 370 | 366
2017-08-24 05:30 | 393 | 390
2017-08-24 06:00 | 420 | 419
2017-08-24 06:30 | 468 | 467
2017-08-24 07:00 | 509 | 509
2017-08-24 07:30 | 543 | 543
2017-08-24 08:00 | 544 | 544
2017-08-24 08:30 | 539 | 539
2017-08-24 09:00 | 534 | 534
2017-08-24 09:30 | 517 | 516
2017-08-24 10:00 | 521 | 521
2017-08-24 10:30 | 527 | 527
2017-08-24 11:00 | 514 | 514
2017-08-24 11:30 | 504 | 503
2017-08-24 12:00 | 492 | 492
2017-08-24 12:30 | 472 | 472
2017-08-24 13:00 | 465 | 465
2017-08-24 13:30 | 464 | 464
2017-08-24 14:00 | 471 | 471
2017-08-24 14:30 | 469 | 469
2017-08-24 15:00 | 485 | 485
2017-08-24 15:30 | 513 | 513
2017-08-24 16:00 | 519 | 518
2017-08-24 16:30 | 531 | 530
2017-08-24 17:00 | 546 | 545
2017-08-24 17:30 | 552 | 551
2017-08-24 18:00 | 562 | 562
2017-08-24 18:30 | 569 | 569
2017-08-24 19:00 | 564 | 563
2017-08-24 19:30 | 557 | 556
2017-08-24 20:00 | 558 | 557
2017-08-24 20:30 | 557 | 556
2017-08-24 21:00 | 542 | 540
2017-08-24 21:30 | 520 | 518
2017-08-24 22:00 | 507 | 507
2017-08-24 22:30 | 486 | 486
2017-08-24 23:00 | 471 | 471
2017-08-24 23:30 | 462 | 461
2017-08-25 | 437 | 436
2017-08-25 00:30 | 411 | 409
2017-08-25 01:00 | 394 | 391
2017-08-25 01:30 | 376 | 372
2017-08-25 02:00 | 364 | 359
2017-08-25 02:30 | 358 | 353
2017-08-25 03:00 | 357 | 352
2017-08-25 03:30 | 356 | 350
2017-08-25 04:00 | 356 | 351
2017-08-25 04:30 | 364 | 359
2017-08-25 05:00 | 375 | 371
2017-08-25 05:30 | 406 | 403
2017-08-25 06:00 | 433 | 431
2017-08-25 06:30 | 476 | 476
2017-08-25 07:00 | 510 | 509
2017-08-25 07:30 | 531 | 530
2017-08-25 08:00 | 537 | 533
2017-08-25 08:30 | 501 | 494
2017-08-25 09:00 | 454 | 446
2017-08-25 09:30 | 443 | 434
2017-08-25 10:00 | 420 | 416
2017-08-25 10:30 | 411 | 409
2017-08-25 11:00 | 415 | 414
2017-08-25 11:30 | 459 | 458
2017-08-25 12:00 | 459 | 459
2017-08-25 12:30 | 461 | 461
2017-08-25 13:00 | 452 | 452
2017-08-25 13:30 | 456 | 456
2017-08-25 14:00 | 458 | 458
2017-08-25 14:30 | 466 | 465
2017-08-25 15:00 | 459 | 458
2017-08-25 15:30 | 463 | 462
2017-08-25 16:00 | 485 | 484
2017-08-25 16:30 | 501 | 500
2017-08-25 17:00 | 521 | 521
2017-08-25 17:30 | 534 | 533
2017-08-25 18:00 | 546 | 545
2017-08-25 18:30 | 546 | 545
2017-08-25 19:00 | 544 | 543
2017-08-25 19:30 | 536 | 535
2017-08-25 20:00 | 534 | 532
2017-08-25 20:30 | 531 | 530
2017-08-25 21:00 | 515 | 514
2017-08-25 21:30 | 499 | 499
2017-08-25 22:00 | 488 | 487
2017-08-25 22:30 | 480 | 479
2017-08-25 23:00 | 461 | 460
2017-08-25 23:30 | 449 | 447
2017-08-26 | 430 | 427
2017-08-26 00:30 | 407 | 404
2017-08-26 01:00 | 381 | 377
2017-08-26 01:30 | 369 | 364
2017-08-26 02:00 | 355 | 349
2017-08-26 02:30 | 351 | 345
2017-08-26 03:00 | 347 | 339
2017-08-26 03:30 | 346 | 338
2017-08-26 04:00 | 348 | 340
2017-08-26 04:30 | 348 | 339
2017-08-26 05:00 | 351 | 343
2017-08-26 05:30 | 362 | 355
2017-08-26 06:00 | 373 | 366
2017-08-26 06:30 | 401 | 394
2017-08-26 07:00 | 418 | 413
2017-08-26 07:30 | 437 | 433
2017-08-26 08:00 | 441 | 437
2017-08-26 08:30 | 442 | 439
2017-08-26 09:00 | 436 | 433
2017-08-26 09:30 | 427 | 424
2017-08-26 10:00 | 411 | 408
2017-08-26 10:30 | 397 | 394
2017-08-26 11:00 | 381 | 378
2017-08-26 11:30 | 369 | 366
2017-08-26 12:00 | 364 | 361
2017-08-26 12:30 | 364 | 360
2017-08-26 13:00 | 365 | 361
2017-08-26 13:30 | 371 | 367
2017-08-26 14:00 | 374 | 370
2017-08-26 14:30 | 381 | 377
2017-08-26 15:00 | 391 | 388
2017-08-26 15:30 | 405 | 401
2017-08-26 16:00 | 426 | 422
2017-08-26 16:30 | 440 | 437
2017-08-26 17:00 | 460 | 457
2017-08-26 17:30 | 474 | 472
2017-08-26 18:00 | 483 | 481
2017-08-26 18:30 | 496 | 491
2017-08-26 19:00 | 497 | 492
2017-08-26 19:30 | 496 | 490
2017-08-26 20:00 | 502 | 496
2017-08-26 20:30 | 508 | 501
2017-08-26 21:00 | 495 | 492
2017-08-26 21:30 | 487 | 486
2017-08-26 22:00 | 477 | 476
2017-08-26 22:30 | 455 | 454
2017-08-26 23:00 | 438 | 437
2017-08-26 23:30 | 428 | 426
2017-08-27 | 409 | 407
2017-08-27 00:30 | 391 | 388
2017-08-27 01:00 | 380 | 376
2017-08-27 01:30 | 370 | 365
2017-08-27 02:00 | 361 | 355
2017-08-27 02:30 | 348 | 342
2017-08-27 03:00 | 342 | 336
2017-08-27 03:30 | 342 | 337
2017-08-27 04:00 | 341 | 336
2017-08-27 04:30 | 338 | 333
2017-08-27 05:00 | 336 | 330
2017-08-27 05:30 | 345 | 340
2017-08-27 06:00 | 358 | 353
2017-08-27 06:30 | 373 | 368
2017-08-27 07:00 | 384 | 379
2017-08-27 07:30 | 400 | 396
2017-08-27 08:00 | 412 | 409
2017-08-27 08:30 | 412 | 409
2017-08-27 09:00 | 410 | 407
2017-08-27 09:30 | 410 | 407
2017-08-27 10:00 | 405 | 403
2017-08-27 10:30 | 395 | 392
2017-08-27 11:00 | 388 | 386
2017-08-27 11:30 | 398 | 396
2017-08-27 12:00 | 390 | 388
2017-08-27 12:30 | 388 | 386
2017-08-27 13:00 | 375 | 373
2017-08-27 13:30 | 387 | 385
2017-08-27 14:00 | 388 | 386
2017-08-27 14:30 | 388 | 386
2017-08-27 15:00 | 394 | 392
2017-08-27 15:30 | 408 | 406
2017-08-27 16:00 | 421 | 419
2017-08-27 16:30 | 432 | 430
2017-08-27 17:00 | 455 | 454
2017-08-27 17:30 | 465 | 464
2017-08-27 18:00 | 490 | 489
2017-08-27 18:30 | 505 | 501
2017-08-27 19:00 | 507 | 503
2017-08-27 19:30 | 502 | 497
2017-08-27 20:00 | 502 | 498
2017-08-27 20:30 | 512 | 508
2017-08-27 21:00 | 499 | 495
2017-08-27 21:30 | 478 | 477
2017-08-27 22:00 | 468 | 467
2017-08-27 22:30 | 449 | 448
2017-08-27 23:00 | 432 | 431
2017-08-27 23:30 | 421 | 420
2017-08-28 | 402 | 400
2017-08-28 00:30 | 381 | 379
2017-08-28 01:00 | 369 | 366
2017-08-28 01:30 | 363 | 360
2017-08-28 02:00 | 349 | 346
2017-08-28 02:30 | 338 | 334
2017-08-28 03:00 | 342 | 339
2017-08-28 03:30 | 339 | 335
2017-08-28 04:00 | 345 | 341
2017-08-28 04:30 | 358 | 355
2017-08-28 05:00 | 371 | 369
2017-08-28 05:30 | 402 | 399
2017-08-28 06:00 | 441 | 439
2017-08-28 06:30 | 497 | 495
2017-08-28 07:00 | 542 | 540
2017-08-28 07:30 | 557 | 553
2017-08-28 08:00 | 570 | 564
2017-08-28 08:30 | 549 | 542
2017-08-28 09:00 | 521 | 512
2017-08-28 09:30 | 495 | 490
2017-08-28 10:00 | 472 | 470
2017-08-28 10:30 | 454 | 453
2017-08-28 11:00 | 439 | 438
2017-08-28 11:30 | 429 | 428
2017-08-28 12:00 | 426 | 424
2017-08-28 12:30 | 423 | 422
2017-08-28 13:00 | 425 | 424
2017-08-28 13:30 | 427 | 426
2017-08-28 14:00 | 434 | 434
2017-08-28 14:30 | 445 | 444
2017-08-28 15:00 | 454 | 453
2017-08-28 15:30 | 472 | 471
2017-08-28 16:00 | 492 | 491
2017-08-28 16:30 | 510 | 509
2017-08-28 17:00 | 534 | 533
2017-08-28 17:30 | 560 | 554
2017-08-28 18:00 | 585 | 578
2017-08-28 18:30 | 607 | 600
2017-08-28 19:00 | 611 | 604
2017-08-28 19:30 | 599 | 590
2017-08-28 20:00 | 586 | 581
2017-08-28 20:30 | 581 | 575
2017-08-28 21:00 | 563 | 558
2017-08-28 21:30 | 549 | 544
2017-08-28 22:00 | 531 | 526
2017-08-28 22:30 | 515 | 510
2017-08-28 23:00 | 492 | 490
2017-08-28 23:30 | 470 | 469
2017-08-29 | 443 | 442
2017-08-29 00:30 | 411 | 409
2017-08-29 01:00 | 399 | 395
2017-08-29 01:30 | 389 | 384
2017-08-29 02:00 | 379 | 374
2017-08-29 02:30 | 370 | 364
2017-08-29 03:00 | 367 | 361
2017-08-29 03:30 | 368 | 362
2017-08-29 04:00 | 371 | 365
2017-08-29 04:30 | 381 | 375
2017-08-29 05:00 | 399 | 395
2017-08-29 05:30 | 433 | 431
2017-08-29 06:00 | 473 | 470
2017-08-29 06:30 | 520 | 517
2017-08-29 07:00 | 558 | 551
2017-08-29 07:30 | 572 | 565
2017-08-29 08:00 | 561 | 554
2017-08-29 08:30 | 542 | 534
2017-08-29 09:00 | 518 | 508
2017-08-29 09:30 | 501 | 498
2017-08-29 10:00 | 481 | 479
2017-08-29 10:30 | 462 | 460
2017-08-29 11:00 | 449 | 448
2017-08-29 11:30 | 438 | 437
2017-08-29 12:00 | 438 | 437
2017-08-29 12:30 | 435 | 435
2017-08-29 13:00 | 436 | 436
2017-08-29 13:30 | 442 | 442
2017-08-29 14:00 | 447 | 447
2017-08-29 14:30 | 455 | 454
2017-08-29 15:00 | 463 | 462
2017-08-29 15:30 | 472 | 471
2017-08-29 16:00 | 488 | 487
2017-08-29 16:30 | 506 | 505
2017-08-29 17:00 | 531 | 530
2017-08-29 17:30 | 563 | 561
2017-08-29 18:00 | 585 | 581
2017-08-29 18:30 | 621 | 610
2017-08-29 19:00 | 623 | 611
2017-08-29 19:30 | 596 | 586
2017-08-29 20:00 | 590 | 582
2017-08-29 20:30 | 584 | 578
2017-08-29 21:00 | 566 | 561
2017-08-29 21:30 | 540 | 537
2017-08-29 22:00 | 513 | 513
2017-08-29 22:30 | 501 | 501
2017-08-29 23:00 | 481 | 481
2017-08-29 23:30 | 460 | 459
2017-08-30 | 431 | 430
2017-08-30 00:30 | 405 | 403
2017-08-30 01:00 | 390 | 388
2017-08-30 01:30 | 377 | 374
2017-08-30 02:00 | 367 | 364
2017-08-30 02:30 | 364 | 360
2017-08-30 03:00 | 360 | 356
2017-08-30 03:30 | 358 | 355
2017-08-30 04:00 | 357 | 354
2017-08-30 04:30 | 369 | 366
2017-08-30 05:00 | 381 | 378
2017-08-30 05:30 | 409 | 407
2017-08-30 06:00 | 442 | 442
2017-08-30 06:30 | 499 | 498
2017-08-30 07:00 | 537 | 537
2017-08-30 07:30 | 545 | 545
2017-08-30 08:00 | 537 | 536
2017-08-30 08:30 | 521 | 521
2017-08-30 09:00 | 503 | 503
2017-08-30 09:30 | 486 | 486
2017-08-30 10:00 | 469 | 468
2017-08-30 10:30 | 461 | 461
2017-08-30 11:00 | 451 | 451
2017-08-30 11:30 | 443 | 443
2017-08-30 12:00 | 433 | 433
2017-08-30 12:30 | 427 | 427
2017-08-30 13:00 | 425 | 425
2017-08-30 13:30 | 429 | 429
2017-08-30 14:00 | 429 | 429
2017-08-30 14:30 | 455 | 455
2017-08-30 15:00 | 465 | 465
2017-08-30 15:30 | 477 | 477
2017-08-30 16:00 | 494 | 494
2017-08-30 16:30 | 507 | 507
2017-08-30 17:00 | 529 | 528
2017-08-30 17:30 | 551 | 551
2017-08-30 18:00 | 560 | 560
2017-08-30 18:30 | 569 | 566
2017-08-30 19:00 | 565 | 563
2017-08-30 19:30 | 557 | 555
2017-08-30 20:00 | 554 | 553
2017-08-30 20:30 | 551 | 550
2017-08-30 21:00 | 533 | 532
2017-08-30 21:30 | 510 | 509
2017-08-30 22:00 | 501 | 501
2017-08-30 22:30 | 481 | 480
2017-08-30 23:00 | 459 | 458
2017-08-30 23:30 | 446 | 444
2017-08-31 | 423 | 421
2017-08-31 00:30 | 395 | 393
2017-08-31 01:00 | 382 | 379
2017-08-31 01:30 | 371 | 367
2017-08-31 02:00 | 360 | 356
2017-08-31 02:30 | 355 | 350
2017-08-31 03:00 | 349 | 344
2017-08-31 03:30 | 347 | 342
2017-08-31 04:00 | 355 | 350
2017-08-31 04:30 | 374 | 369
2017-08-31 05:00 | 388 | 384
2017-08-31 05:30 | 415 | 412
2017-08-31 06:00 | 446 | 445
2017-08-31 06:30 | 504 | 502
2017-08-31 07:00 | 541 | 539
2017-08-31 07:30 | 552 | 551
2017-08-31 08:00 | 545 | 544
2017-08-31 08:30 | 523 | 522
2017-08-31 09:00 | 471 | 471
2017-08-31 09:30 | 432 | 431
2017-08-31 10:00 | 415 | 415
2017-08-31 10:30 | 409 | 409
2017-08-31 11:00 | 379 | 379
2017-08-31 11:30 | 356 | 356
2017-08-31 12:00 | 360 | 360
2017-08-31 12:30 | 369 | 369
2017-08-31 13:00 | 443 | 443
2017-08-31 13:30 | 465 | 465
2017-08-31 14:00 | 473 | 473
2017-08-31 14:30 | 484 | 484
2017-08-31 15:00 | 491 | 491
2017-08-31 15:30 | 497 | 496
2017-08-31 16:00 | 507 | 507
2017-08-31 16:30 | 521 | 521
2017-08-31 17:00 | 543 | 543
2017-08-31 17:30 | 556 | 556
2017-08-31 18:00 | 566 | 566
2017-08-31 18:30 | 569 | 568
2017-08-31 19:00 | 567 | 566
2017-08-31 19:30 | 562 | 560
2017-08-31 20:00 | 561 | 559
2017-08-31 20:30 | 565 | 563
2017-08-31 21:00 | 549 | 548
2017-08-31 21:30 | 531 | 529
2017-08-31 22:00 | 520 | 519
2017-08-31 22:30 | 492 | 491
2017-08-31 23:00 | 475 | 475
2017-08-31 23:30 | 457 | 457
2017-09-01 | 430 | 429
2017-09-01 00:30 | 403 | 401
2017-09-01 01:00 | 389 | 386
2017-09-01 01:30 | 379 | 375
2017-09-01 02:00 | 366 | 362
2017-09-01 02:30 | 359 | 355
2017-09-01 03:00 | 354 | 350
2017-09-01 03:30 | 355 | 351
2017-09-01 04:00 | 364 | 360
2017-09-01 04:30 | 371 | 367
2017-09-01 05:00 | 379 | 376
2017-09-01 05:30 | 410 | 408
2017-09-01 06:00 | 441 | 439
2017-09-01 06:30 | 473 | 471
2017-09-01 07:00 | 502 | 501
2017-09-01 07:30 | 512 | 511
2017-09-01 08:00 | 511 | 509
2017-09-01 08:30 | 510 | 508
2017-09-01 09:00 | 500 | 498
2017-09-01 09:30 | 475 | 475
2017-09-01 10:00 | 456 | 455
2017-09-01 10:30 | 455 | 455
2017-09-01 11:00 | 453 | 452
2017-09-01 11:30 | 446 | 446
2017-09-01 12:00 | 440 | 440
2017-09-01 12:30 | 426 | 426
2017-09-01 13:00 | 379 | 379
2017-09-01 13:30 | 383 | 383
2017-09-01 14:00 | 385 | 385
2017-09-01 14:30 | 398 | 397
2017-09-01 15:00 | 455 | 455
2017-09-01 15:30 | 466 | 466
2017-09-01 16:00 | 477 | 477
2017-09-01 16:30 | 495 | 495
2017-09-01 17:00 | 513 | 513
2017-09-01 17:30 | 528 | 527
2017-09-01 18:00 | 541 | 540
2017-09-01 18:30 | 541 | 541
2017-09-01 19:00 | 534 | 534
2017-09-01 19:30 | 520 | 519
2017-09-01 20:00 | 520 | 519
2017-09-01 20:30 | 522 | 521
2017-09-01 21:00 | 512 | 511
2017-09-01 21:30 | 502 | 501
2017-09-01 22:00 | 495 | 494
2017-09-01 22:30 | 485 | 484
2017-09-01 23:00 | 464 | 463
2017-09-01 23:30 | 452 | 450
2017-09-02 | 430 | 428
2017-09-02 00:30 | 403 | 400
2017-09-02 01:00 | 378 | 374
2017-09-02 01:30 | 364 | 359
2017-09-02 02:00 | 355 | 349
2017-09-02 02:30 | 345 | 340
2017-09-02 03:00 | 342 | 338
2017-09-02 03:30 | 340 | 335
2017-09-02 04:00 | 339 | 335
2017-09-02 04:30 | 343 | 339
2017-09-02 05:00 | 351 | 346
2017-09-02 05:30 | 364 | 359
2017-09-02 06:00 | 378 | 374
2017-09-02 06:30 | 403 | 399
2017-09-02 07:00 | 420 | 416
2017-09-02 07:30 | 433 | 430
2017-09-02 08:00 | 431 | 429
2017-09-02 08:30 | 430 | 428
2017-09-02 09:00 | 429 | 427
2017-09-02 09:30 | 418 | 416
2017-09-02 10:00 | 410 | 408
2017-09-02 10:30 | 393 | 392
2017-09-02 11:00 | 383 | 382
2017-09-02 11:30 | 373 | 372
2017-09-02 12:00 | 364 | 362
2017-09-02 12:30 | 359 | 357
2017-09-02 13:00 | 353 | 352
2017-09-02 13:30 | 355 | 353
2017-09-02 14:00 | 358 | 356
2017-09-02 14:30 | 369 | 367
2017-09-02 15:00 | 381 | 379
2017-09-02 15:30 | 394 | 392
2017-09-02 16:00 | 415 | 414
2017-09-02 16:30 | 437 | 435
2017-09-02 17:00 | 457 | 456
2017-09-02 17:30 | 468 | 468
2017-09-02 18:00 | 479 | 479
2017-09-02 18:30 | 483 | 483
2017-09-02 19:00 | 491 | 490
2017-09-02 19:30 | 477 | 476
2017-09-02 20:00 | 480 | 479
2017-09-02 20:30 | 476 | 475
2017-09-02 21:00 | 459 | 459
2017-09-02 21:30 | 452 | 451
2017-09-02 22:00 | 449 | 448
2017-09-02 22:30 | 431 | 430
2017-09-02 23:00 | 417 | 416
2017-09-02 23:30 | 408 | 406
2017-09-03 | 392 | 389
2017-09-03 00:30 | 377 | 374
2017-09-03 01:00 | 364 | 360
2017-09-03 01:30 | 352 | 347
2017-09-03 02:00 | 339 | 334
2017-09-03 02:30 | 327 | 320
2017-09-03 03:00 | 322 | 315
2017-09-03 03:30 | 315 | 308
2017-09-03 04:00 | 315 | 307
2017-09-03 04:30 | 315 | 307
2017-09-03 05:00 | 317 | 310
2017-09-03 05:30 | 326 | 319
2017-09-03 06:00 | 340 | 333
2017-09-03 06:30 | 366 | 358
2017-09-03 07:00 | 373 | 366
2017-09-03 07:30 | 390 | 383
2017-09-03 08:00 | 399 | 392
2017-09-03 08:30 | 401 | 396
2017-09-03 09:00 | 399 | 395
2017-09-03 09:30 | 388 | 384
2017-09-03 10:00 | 376 | 372
2017-09-03 10:30 | 368 | 364
2017-09-03 11:00 | 357 | 354
2017-09-03 11:30 | 350 | 347
2017-09-03 12:00 | 338 | 336
2017-09-03 12:30 | 325 | 322
2017-09-03 13:00 | 321 | 318
2017-09-03 13:30 | 325 | 323
2017-09-03 14:00 | 325 | 322
2017-09-03 14:30 | 341 | 338
2017-09-03 15:00 | 360 | 358
2017-09-03 15:30 | 379 | 378
2017-09-03 16:00 | 393 | 392
2017-09-03 16:30 | 407 | 406
2017-09-03 17:00 | 424 | 423
2017-09-03 17:30 | 437 | 437
2017-09-03 18:00 | 456 | 456
2017-09-03 18:30 | 468 | 468
2017-09-03 19:00 | 473 | 473
2017-09-03 19:30 | 471 | 470
2017-09-03 20:00 | 476 | 476
2017-09-03 20:30 | 475 | 475
2017-09-03 21:00 | 464 | 463
2017-09-03 21:30 | 457 | 456
2017-09-03 22:00 | 452 | 452
2017-09-03 22:30 | 425 | 424
2017-09-03 23:00 | 412 | 411
2017-09-03 23:30 | 402 | 400
2017-09-04 | 382 | 380
2017-09-04 00:30 | 360 | 357
2017-09-04 01:00 | 350 | 346
2017-09-04 01:30 | 339 | 334
2017-09-04 02:00 | 322 | 316
2017-09-04 02:30 | 308 | 302
2017-09-04 03:00 | 296 | 289
2017-09-04 03:30 | 298 | 291
2017-09-04 04:00 | 299 | 292
2017-09-04 04:30 | 311 | 305
2017-09-04 05:00 | 325 | 320
2017-09-04 05:30 | 351 | 347
2017-09-04 06:00 | 357 | 355
2017-09-04 06:30 | 410 | 409
2017-09-04 07:00 | 447 | 447
2017-09-04 07:30 | 481 | 481
2017-09-04 08:00 | 491 | 490
2017-09-04 08:30 | 482 | 482
2017-09-04 09:00 | 477 | 476
2017-09-04 09:30 | 470 | 470
2017-09-04 10:00 | 459 | 459
2017-09-04 10:30 | 455 | 455
2017-09-04 11:00 | 458 | 458
2017-09-04 11:30 | 457 | 457
2017-09-04 12:00 | 461 | 461
2017-09-04 12:30 | 469 | 468
2017-09-04 13:00 | 466 | 466
2017-09-04 13:30 | 468 | 468
2017-09-04 14:00 | 476 | 476
2017-09-04 14:30 | 485 | 484
2017-09-04 15:00 | 493 | 493
2017-09-04 15:30 | 497 | 496
2017-09-04 16:00 | 505 | 505
2017-09-04 16:30 | 523 | 522
2017-09-04 17:00 | 533 | 532
2017-09-04 17:30 | 536 | 535
2017-09-04 18:00 | 546 | 545
2017-09-04 18:30 | 547 | 546
2017-09-04 19:00 | 541 | 540
2017-09-04 19:30 | 529 | 528
2017-09-04 20:00 | 522 | 522
2017-09-04 20:30 | 519 | 518
2017-09-04 21:00 | 509 | 507
2017-09-04 21:30 | 494 | 492
2017-09-04 22:00 | 486 | 483
2017-09-04 22:30 | 453 | 451
2017-09-04 23:00 | 433 | 432
2017-09-04 23:30 | 421 | 419
2017-09-05 | 398 | 395
2017-09-05 00:30 | 373 | 370
2017-09-05 01:00 | 370 | 365
2017-09-05 01:30 | 362 | 358
2017-09-05 02:00 | 359 | 353
2017-09-05 02:30 | 346 | 340
2017-09-05 03:00 | 330 | 324
2017-09-05 03:30 | 329 | 322
2017-09-05 04:00 | 336 | 329
2017-09-05 04:30 | 339 | 333
2017-09-05 05:00 | 359 | 354
2017-09-05 05:30 | 395 | 391
2017-09-05 06:00 | 429 | 427
2017-09-05 06:30 | 468 | 467
2017-09-05 07:00 | 499 | 498
2017-09-05 07:30 | 507 | 505
2017-09-05 08:00 | 450 | 449
2017-09-05 08:30 | 443 | 441
2017-09-05 09:00 | 437 | 435
2017-09-05 09:30 | 422 | 421
2017-09-05 10:00 | 451 | 451
2017-09-05 10:30 | 452 | 452
2017-09-05 11:00 | 444 | 444
2017-09-05 11:30 | 436 | 435
2017-09-05 12:00 | 441 | 440
2017-09-05 12:30 | 439 | 438
2017-09-05 13:00 | 436 | 436
2017-09-05 13:30 | 456 | 456
2017-09-05 14:00 | 454 | 454
2017-09-05 14:30 | 466 | 466
2017-09-05 15:00 | 479 | 479
2017-09-05 15:30 | 489 | 489
2017-09-05 16:00 | 511 | 511
2017-09-05 16:30 | 515 | 515
2017-09-05 17:00 | 533 | 532
2017-09-05 17:30 | 535 | 535
2017-09-05 18:00 | 548 | 548
2017-09-05 18:30 | 559 | 558
2017-09-05 19:00 | 559 | 559
2017-09-05 19:30 | 548 | 547
2017-09-05 20:00 | 550 | 549
2017-09-05 20:30 | 546 | 546
2017-09-05 21:00 | 533 | 532
2017-09-05 21:30 | 513 | 513
2017-09-05 22:00 | 503 | 502
2017-09-05 22:30 | 468 | 467
2017-09-05 23:00 | 448 | 448
2017-09-05 23:30 | 436 | 436
2017-09-06 | 416 | 415
2017-09-06 00:30 | 398 | 397
2017-09-06 01:00 | 381 | 378
2017-09-06 01:30 | 369 | 366
2017-09-06 02:00 | 355 | 352
2017-09-06 02:30 | 341 | 337
2017-09-06 03:00 | 330 | 326
2017-09-06 03:30 | 321 | 317
2017-09-06 04:00 | 324 | 320
2017-09-06 04:30 | 335 | 332
2017-09-06 05:00 | 352 | 350
2017-09-06 05:30 | 384 | 382
2017-09-06 06:00 | 412 | 412
2017-09-06 06:30 | 455 | 455
2017-09-06 07:00 | 479 | 478
2017-09-06 07:30 | 496 | 495
2017-09-06 08:00 | 497 | 496
2017-09-06 08:30 | 481 | 481
2017-09-06 09:00 | 467 | 466
2017-09-06 09:30 | 459 | 458
2017-09-06 10:00 | 452 | 451
2017-09-06 10:30 | 447 | 446
2017-09-06 11:00 | 439 | 438
2017-09-06 11:30 | 437 | 436
2017-09-06 12:00 | 434 | 434
2017-09-06 12:30 | 434 | 434
2017-09-06 13:00 | 434 | 433
2017-09-06 13:30 | 437 | 437
2017-09-06 14:00 | 446 | 446
2017-09-06 14:30 | 462 | 462
2017-09-06 15:00 | 473 | 473
2017-09-06 15:30 | 487 | 487
2017-09-06 16:00 | 508 | 507
2017-09-06 16:30 | 517 | 517
2017-09-06 17:00 | 533 | 532
2017-09-06 17:30 | 543 | 541
2017-09-06 18:00 | 548 | 546
2017-09-06 18:30 | 549 | 546
2017-09-06 19:00 | 549 | 546
2017-09-06 19:30 | 543 | 538
2017-09-06 20:00 | 543 | 540
2017-09-06 20:30 | 540 | 537
2017-09-06 21:00 | 529 | 528
2017-09-06 21:30 | 514 | 513
2017-09-06 22:00 | 505 | 504
2017-09-06 22:30 | 475 | 473
2017-09-06 23:00 | 456 | 454
2017-09-06 23:30 | 438 | 437
2017-09-07 | 419 | 417
2017-09-07 00:30 | 391 | 387
2017-09-07 01:00 | 377 | 372
2017-09-07 01:30 | 365 | 359
2017-09-07 02:00 | 352 | 346
2017-09-07 02:30 | 341 | 334
2017-09-07 03:00 | 340 | 333
2017-09-07 03:30 | 339 | 332
2017-09-07 04:00 | 342 | 336
2017-09-07 04:30 | 354 | 348
2017-09-07 05:00 | 363 | 358
2017-09-07 05:30 | 382 | 378
2017-09-07 06:00 | 402 | 399
2017-09-07 06:30 | 449 | 448
2017-09-07 07:00 | 478 | 478
2017-09-07 07:30 | 506 | 505
2017-09-07 08:00 | 505 | 504
2017-09-07 08:30 | 498 | 497
2017-09-07 09:00 | 486 | 485
2017-09-07 09:30 | 469 | 468
2017-09-07 10:00 | 456 | 455
2017-09-07 10:30 | 450 | 449
2017-09-07 11:00 | 445 | 445
2017-09-07 11:30 | 442 | 441
2017-09-07 12:00 | 437 | 436
2017-09-07 12:30 | 438 | 438
2017-09-07 13:00 | 438 | 438
2017-09-07 13:30 | 450 | 450
2017-09-07 14:00 | 459 | 459
2017-09-07 14:30 | 473 | 473
2017-09-07 15:00 | 480 | 480
2017-09-07 15:30 | 492 | 491
2017-09-07 16:00 | 507 | 506
2017-09-07 16:30 | 519 | 519
2017-09-07 17:00 | 536 | 535
2017-09-07 17:30 | 543 | 541
2017-09-07 18:00 | 545 | 544
2017-09-07 18:30 | 547 | 546
2017-09-07 19:00 | 547 | 547
2017-09-07 19:30 | 542 | 541
2017-09-07 20:00 | 541 | 539
2017-09-07 20:30 | 541 | 540
2017-09-07 21:00 | 533 | 532
2017-09-07 21:30 | 511 | 511
2017-09-07 22:00 | 499 | 499
2017-09-07 22:30 | 475 | 474
2017-09-07 23:00 | 459 | 458
2017-09-07 23:30 | 444 | 443
2017-09-08 | 421 | 420
2017-09-08 00:30 | 393 | 391
2017-09-08 01:00 | 379 | 377
2017-09-08 01:30 | 370 | 366
2017-09-08 02:00 | 363 | 359
2017-09-08 02:30 | 353 | 349
2017-09-08 03:00 | 353 | 348
2017-09-08 03:30 | 350 | 346
2017-09-08 04:00 | 348 | 344
2017-09-08 04:30 | 359 | 354
2017-09-08 05:00 | 370 | 367
2017-09-08 05:30 | 392 | 390
2017-09-08 06:00 | 411 | 409
2017-09-08 06:30 | 465 | 463
2017-09-08 07:00 | 494 | 493
2017-09-08 07:30 | 521 | 520
2017-09-08 08:00 | 518 | 517
2017-09-08 08:30 | 495 | 494
2017-09-08 09:00 | 479 | 478
2017-09-08 09:30 | 468 | 467
2017-09-08 10:00 | 454 | 453
2017-09-08 10:30 | 442 | 441
2017-09-08 11:00 | 434 | 433
2017-09-08 11:30 | 429 | 429
2017-09-08 12:00 | 426 | 426
2017-09-08 12:30 | 426 | 425
2017-09-08 13:00 | 428 | 428
2017-09-08 13:30 | 436 | 436
2017-09-08 14:00 | 445 | 444
2017-09-08 14:30 | 456 | 456
2017-09-08 15:00 | 466 | 466
2017-09-08 15:30 | 478 | 477
2017-09-08 16:00 | 494 | 494
2017-09-08 16:30 | 509 | 508
2017-09-08 17:00 | 524 | 523
2017-09-08 17:30 | 528 | 528
2017-09-08 18:00 | 536 | 535
2017-09-08 18:30 | 540 | 538
2017-09-08 19:00 | 544 | 542
2017-09-08 19:30 | 540 | 538
2017-09-08 20:00 | 538 | 536
2017-09-08 20:30 | 528 | 526
2017-09-08 21:00 | 511 | 510
2017-09-08 21:30 | 496 | 495
2017-09-08 22:00 | 487 | 485
2017-09-08 22:30 | 476 | 474
2017-09-08 23:00 | 455 | 453
2017-09-08 23:30 | 440 | 438
2017-09-09 | 414 | 412
2017-09-09 00:30 | 379 | 376
2017-09-09 01:00 | 362 | 359
2017-09-09 01:30 | 356 | 352
2017-09-09 02:00 | 345 | 340
2017-09-09 02:30 | 335 | 329
2017-09-09 03:00 | 332 | 327
2017-09-09 03:30 | 330 | 325
2017-09-09 04:00 | 335 | 330
2017-09-09 04:30 | 341 | 336
2017-09-09 05:00 | 348 | 344
2017-09-09 05:30 | 360 | 356
2017-09-09 06:00 | 369 | 366
2017-09-09 06:30 | 387 | 383
2017-09-09 07:00 | 395 | 392
2017-09-09 07:30 | 406 | 404
2017-09-09 08:00 | 410 | 409
2017-09-09 08:30 | 410 | 408
2017-09-09 09:00 | 404 | 402
2017-09-09 09:30 | 394 | 393
2017-09-09 10:00 | 375 | 374
2017-09-09 10:30 | 363 | 362
2017-09-09 11:00 | 355 | 354
2017-09-09 11:30 | 344 | 343
2017-09-09 12:00 | 340 | 339
2017-09-09 12:30 | 333 | 331
2017-09-09 13:00 | 329 | 328
2017-09-09 13:30 | 331 | 330
2017-09-09 14:00 | 339 | 338
2017-09-09 14:30 | 353 | 351
2017-09-09 15:00 | 369 | 368
2017-09-09 15:30 | 388 | 386
2017-09-09 16:00 | 416 | 415
2017-09-09 16:30 | 429 | 428
2017-09-09 17:00 | 444 | 444
2017-09-09 17:30 | 458 | 458
2017-09-09 18:00 | 473 | 473
2017-09-09 18:30 | 480 | 480
2017-09-09 19:00 | 480 | 479
2017-09-09 19:30 | 480 | 480
2017-09-09 20:00 | 492 | 490
2017-09-09 20:30 | 493 | 491
2017-09-09 21:00 | 480 | 478
2017-09-09 21:30 | 464 | 463
2017-09-09 22:00 | 456 | 455
2017-09-09 22:30 | 432 | 431
2017-09-09 23:00 | 420 | 420
2017-09-09 23:30 | 413 | 411
2017-09-10 | 401 | 398
2017-09-10 00:30 | 381 | 378
2017-09-10 01:00 | 370 | 366
2017-09-10 01:30 | 362 | 358
2017-09-10 02:00 | 352 | 347
2017-09-10 02:30 | 342 | 336
2017-09-10 03:00 | 337 | 331
2017-09-10 03:30 | 339 | 332
2017-09-10 04:00 | 342 | 335
2017-09-10 04:30 | 347 | 340
2017-09-10 05:00 | 350 | 342
2017-09-10 05:30 | 357 | 350
2017-09-10 06:00 | 365 | 358
2017-09-10 06:30 | 374 | 367
2017-09-10 07:00 | 377 | 371
2017-09-10 07:30 | 390 | 384
2017-09-10 08:00 | 388 | 382
2017-09-10 08:30 | 392 | 386
2017-09-10 09:00 | 388 | 383
2017-09-10 09:30 | 382 | 378
2017-09-10 10:00 | 373 | 369
2017-09-10 10:30 | 364 | 360
2017-09-10 11:00 | 358 | 354
2017-09-10 11:30 | 348 | 345
2017-09-10 12:00 | 348 | 345
2017-09-10 12:30 | 343 | 340
2017-09-10 13:00 | 345 | 342
2017-09-10 13:30 | 348 | 345
2017-09-10 14:00 | 355 | 352
2017-09-10 14:30 | 365 | 362
2017-09-10 15:00 | 377 | 374
2017-09-10 15:30 | 393 | 390
2017-09-10 16:00 | 407 | 405
2017-09-10 16:30 | 421 | 419
2017-09-10 17:00 | 440 | 439
2017-09-10 17:30 | 456 | 455
2017-09-10 18:00 | 469 | 468
2017-09-10 18:30 | 488 | 482
2017-09-10 19:00 | 493 | 486
2017-09-10 19:30 | 480 | 473
2017-09-10 20:00 | 472 | 466
2017-09-10 20:30 | 477 | 473
2017-09-10 21:00 | 466 | 460
2017-09-10 21:30 | 448 | 445
2017-09-10 22:00 | 436 | 436
2017-09-10 22:30 | 417 | 416
2017-09-10 23:00 | 404 | 403
2017-09-10 23:30 | 392 | 390
2017-09-11 | 377 | 375
2017-09-11 00:30 | 367 | 364
2017-09-11 01:00 | 356 | 351
2017-09-11 01:30 | 346 | 340
2017-09-11 02:00 | 335 | 329
2017-09-11 02:30 | 325 | 319
2017-09-11 03:00 | 322 | 317
2017-09-11 03:30 | 325 | 320
2017-09-11 04:00 | 325 | 319
2017-09-11 04:30 | 335 | 330
2017-09-11 05:00 | 351 | 347
2017-09-11 05:30 | 371 | 368
2017-09-11 06:00 | 390 | 388
2017-09-11 06:30 | 433 | 432
2017-09-11 07:00 | 475 | 469
2017-09-11 07:30 | 489 | 484
2017-09-11 08:00 | 493 | 488
2017-09-11 08:30 | 485 | 477
2017-09-11 09:00 | 474 | 466
2017-09-11 09:30 | 466 | 459
2017-09-11 10:00 | 461 | 454
2017-09-11 10:30 | 454 | 447
2017-09-11 11:00 | 450 | 445
2017-09-11 11:30 | 446 | 441
2017-09-11 12:00 | 450 | 445
2017-09-11 12:30 | 452 | 447
2017-09-11 13:00 | 454 | 450
2017-09-11 13:30 | 460 | 456
2017-09-11 14:00 | 464 | 460
2017-09-11 14:30 | 469 | 465
2017-09-11 15:00 | 480 | 476
2017-09-11 15:30 | 493 | 487
2017-09-11 16:00 | 509 | 501
2017-09-11 16:30 | 525 | 518
2017-09-11 17:00 | 536 | 529
2017-09-11 17:30 | 544 | 536
2017-09-11 18:00 | 557 | 550
2017-09-11 18:30 | 558 | 552
2017-09-11 19:00 | 552 | 545
2017-09-11 19:30 | 536 | 528
2017-09-11 20:00 | 522 | 519
2017-09-11 20:30 | 517 | 516
2017-09-11 21:00 | 499 | 498
2017-09-11 21:30 | 474 | 474
2017-09-11 22:00 | 462 | 462
2017-09-11 22:30 | 436 | 436
2017-09-11 23:00 | 420 | 419
2017-09-11 23:30 | 408 | 407
2017-09-12 | 385 | 383
2017-09-12 00:30 | 363 | 360
2017-09-12 01:00 | 357 | 354
2017-09-12 01:30 | 348 | 344
2017-09-12 02:00 | 340 | 335
2017-09-12 02:30 | 335 | 330
2017-09-12 03:00 | 331 | 327
2017-09-12 03:30 | 329 | 325
2017-09-12 04:00 | 332 | 327
2017-09-12 04:30 | 345 | 340
2017-09-12 05:00 | 356 | 353
2017-09-12 05:30 | 375 | 373
2017-09-12 06:00 | 392 | 390
2017-09-12 06:30 | 438 | 438
2017-09-12 07:00 | 470 | 470
2017-09-12 07:30 | 496 | 496
2017-09-12 08:00 | 492 | 491
2017-09-12 08:30 | 486 | 485
2017-09-12 09:00 | 479 | 479
2017-09-12 09:30 | 480 | 479
2017-09-12 10:00 | 472 | 472
2017-09-12 10:30 | 465 | 465
2017-09-12 11:00 | 464 | 464
2017-09-12 11:30 | 463 | 462
2017-09-12 12:00 | 466 | 466
2017-09-12 12:30 | 466 | 466
2017-09-12 13:00 | 469 | 469
2017-09-12 13:30 | 473 | 472
2017-09-12 14:00 | 479 | 479
2017-09-12 14:30 | 490 | 490
2017-09-12 15:00 | 504 | 504
2017-09-12 15:30 | 511 | 510
2017-09-12 16:00 | 523 | 523
2017-09-12 16:30 | 532 | 532
2017-09-12 17:00 | 543 | 543
2017-09-12 17:30 | 548 | 548
2017-09-12 18:00 | 550 | 550
2017-09-12 18:30 | 551 | 551
2017-09-12 19:00 | 546 | 545
2017-09-12 19:30 | 536 | 535
2017-09-12 20:00 | 535 | 535
2017-09-12 20:30 | 532 | 532
2017-09-12 21:00 | 509 | 509
2017-09-12 21:30 | 492 | 492
2017-09-12 22:00 | 476 | 475
2017-09-12 22:30 | 452 | 452
2017-09-12 23:00 | 437 | 437
2017-09-12 23:30 | 420 | 419
2017-09-13 | 403 | 402
2017-09-13 00:30 | 387 | 385
2017-09-13 01:00 | 376 | 373
2017-09-13 01:30 | 364 | 360
2017-09-13 02:00 | 352 | 348
2017-09-13 02:30 | 343 | 338
2017-09-13 03:00 | 342 | 338
2017-09-13 03:30 | 339 | 334
2017-09-13 04:00 | 335 | 331
2017-09-13 04:30 | 338 | 334
2017-09-13 05:00 | 348 | 344
2017-09-13 05:30 | 370 | 368
2017-09-13 06:00 | 389 | 387
2017-09-13 06:30 | 434 | 432
2017-09-13 07:00 | 457 | 456
2017-09-13 07:30 | 471 | 471
2017-09-13 08:00 | 477 | 477
2017-09-13 08:30 | 468 | 468
2017-09-13 09:00 | 459 | 459
2017-09-13 09:30 | 461 | 460
2017-09-13 10:00 | 461 | 461
2017-09-13 10:30 | 464 | 464
2017-09-13 11:00 | 460 | 460
2017-09-13 11:30 | 463 | 463
2017-09-13 12:00 | 468 | 467
2017-09-13 12:30 | 466 | 465
2017-09-13 13:00 | 461 | 461
2017-09-13 13:30 | 469 | 469
2017-09-13 14:00 | 479 | 478
2017-09-13 14:30 | 489 | 488
2017-09-13 15:00 | 500 | 500
2017-09-13 15:30 | 499 | 499
2017-09-13 16:00 | 508 | 507
2017-09-13 16:30 | 513 | 513
2017-09-13 17:00 | 531 | 530
2017-09-13 17:30 | 533 | 533
2017-09-13 18:00 | 540 | 539
2017-09-13 18:30 | 540 | 535
2017-09-13 19:00 | 535 | 529
2017-09-13 19:30 | 526 | 519
2017-09-13 20:00 | 517 | 513
2017-09-13 20:30 | 507 | 505
2017-09-13 21:00 | 477 | 477
2017-09-13 21:30 | 467 | 467
2017-09-13 22:00 | 453 | 452
2017-09-13 22:30 | 424 | 422
2017-09-13 23:00 | 407 | 405
2017-09-13 23:30 | 389 | 385
2017-09-14 | 376 | 371
2017-09-14 00:30 | 356 | 351
2017-09-14 01:00 | 351 | 345
2017-09-14 01:30 | 355 | 348
2017-09-14 02:00 | 349 | 341
2017-09-14 02:30 | 339 | 331
2017-09-14 03:00 | 331 | 323
2017-09-14 03:30 | 334 | 326
2017-09-14 04:00 | 337 | 330
2017-09-14 04:30 | 345 | 338
2017-09-14 05:00 | 353 | 347
2017-09-14 05:30 | 377 | 373
2017-09-14 06:00 | 397 | 394
2017-09-14 06:30 | 440 | 438
2017-09-14 07:00 | 462 | 461
2017-09-14 07:30 | 501 | 498
2017-09-14 08:00 | 542 | 538
2017-09-14 08:30 | 562 | 559
2017-09-14 09:00 | 547 | 542
2017-09-14 09:30 | 529 | 523
2017-09-14 10:00 | 503 | 496
2017-09-14 10:30 | 488 | 480
2017-09-14 11:00 | 469 | 463
2017-09-14 11:30 | 464 | 457
2017-09-14 12:00 | 458 | 452
2017-09-14 12:30 | 451 | 450
2017-09-14 13:00 | 457 | 456
2017-09-14 13:30 | 446 | 446
2017-09-14 14:00 | 445 | 444
2017-09-14 14:30 | 434 | 434
2017-09-14 15:00 | 434 | 433
2017-09-14 15:30 | 450 | 450
2017-09-14 16:00 | 464 | 464
2017-09-14 16:30 | 469 | 468
2017-09-14 17:00 | 476 | 476
2017-09-14 17:30 | 482 | 482
2017-09-14 18:00 | 498 | 498
2017-09-14 18:30 | 517 | 513
2017-09-14 19:00 | 518 | 513
2017-09-14 19:30 | 516 | 509
2017-09-14 20:00 | 517 | 510
2017-09-14 20:30 | 531 | 525
2017-09-14 21:00 | 516 | 513
2017-09-14 21:30 | 491 | 491
2017-09-14 22:00 | 481 | 481
2017-09-14 22:30 | 457 | 456
2017-09-14 23:00 | 443 | 442
2017-09-14 23:30 | 431 | 429
2017-09-15 | 413 | 410
2017-09-15 00:30 | 384 | 380
2017-09-15 01:00 | 371 | 366
2017-09-15 01:30 | 368 | 362
2017-09-15 02:00 | 363 | 356
2017-09-15 02:30 | 344 | 336
2017-09-15 03:00 | 329 | 321
2017-09-15 03:30 | 321 | 314
2017-09-15 04:00 | 322 | 315
2017-09-15 04:30 | 330 | 323
2017-09-15 05:00 | 350 | 345
2017-09-15 05:30 | 370 | 367
2017-09-15 06:00 | 387 | 385
2017-09-15 06:30 | 420 | 420
2017-09-15 07:00 | 443 | 441
2017-09-15 07:30 | 467 | 464
2017-09-15 08:00 | 474 | 470
2017-09-15 08:30 | 468 | 464
2017-09-15 09:00 | 451 | 446
2017-09-15 09:30 | 444 | 439
2017-09-15 10:00 | 436 | 432
2017-09-15 10:30 | 426 | 426
2017-09-15 11:00 | 426 | 425
2017-09-15 11:30 | 426 | 425
2017-09-15 12:00 | 426 | 426
2017-09-15 12:30 | 420 | 420
2017-09-15 13:00 | 420 | 419
2017-09-15 13:30 | 424 | 424
2017-09-15 14:00 | 426 | 426
2017-09-15 14:30 | 438 | 438
2017-09-15 15:00 | 443 | 443
2017-09-15 15:30 | 450 | 449
2017-09-15 16:00 | 462 | 462
2017-09-15 16:30 | 474 | 473
2017-09-15 17:00 | 484 | 484
2017-09-15 17:30 | 484 | 484
2017-09-15 18:00 | 491 | 491
2017-09-15 18:30 | 500 | 500
2017-09-15 19:00 | 505 | 505
2017-09-15 19:30 | 501 | 500
2017-09-15 20:00 | 503 | 503
2017-09-15 20:30 | 503 | 503
2017-09-15 21:00 | 489 | 489
2017-09-15 21:30 | 481 | 481
2017-09-15 22:00 | 477 | 476
2017-09-15 22:30 | 444 | 444
2017-09-15 23:00 | 424 | 423
2017-09-15 23:30 | 410 | 409
2017-09-16 | 394 | 393
2017-09-16 00:30 | 381 | 377
2017-09-16 01:00 | 369 | 363
2017-09-16 01:30 | 359 | 352
2017-09-16 02:00 | 354 | 344
2017-09-16 02:30 | 355 | 344
2017-09-16 03:00 | 353 | 341
2017-09-16 03:30 | 352 | 341
2017-09-16 04:00 | 348 | 336
2017-09-16 04:30 | 353 | 341
2017-09-16 05:00 | 346 | 335
2017-09-16 05:30 | 355 | 345
2017-09-16 06:00 | 358 | 348
2017-09-16 06:30 | 377 | 369
2017-09-16 07:00 | 386 | 379
2017-09-16 07:30 | 401 | 395
2017-09-16 08:00 | 411 | 405
2017-09-16 08:30 | 414 | 409
2017-09-16 09:00 | 411 | 406
2017-09-16 09:30 | 405 | 400
2017-09-16 10:00 | 395 | 391
2017-09-16 10:30 | 382 | 377
2017-09-16 11:00 | 372 | 368
2017-09-16 11:30 | 362 | 358
2017-09-16 12:00 | 358 | 354
2017-09-16 12:30 | 354 | 350
2017-09-16 13:00 | 354 | 349
2017-09-16 13:30 | 358 | 354
2017-09-16 14:00 | 366 | 362
2017-09-16 14:30 | 374 | 370
2017-09-16 15:00 | 387 | 383
2017-09-16 15:30 | 399 | 396
2017-09-16 16:00 | 413 | 409
2017-09-16 16:30 | 427 | 424
2017-09-16 17:00 | 433 | 430
2017-09-16 17:30 | 437 | 434
2017-09-16 18:00 | 455 | 454
2017-09-16 18:30 | 455 | 454
2017-09-16 19:00 | 452 | 451
2017-09-16 19:30 | 449 | 448
2017-09-16 20:00 | 450 | 449
2017-09-16 20:30 | 452 | 451
2017-09-16 21:00 | 442 | 440
2017-09-16 21:30 | 438 | 436
2017-09-16 22:00 | 436 | 434
2017-09-16 22:30 | 413 | 411
2017-09-16 23:00 | 400 | 398
2017-09-16 23:30 | 388 | 384
2017-09-17 | 378 | 372
2017-09-17 00:30 | 369 | 361
2017-09-17 01:00 | 370 | 361
2017-09-17 01:30 | 357 | 347
2017-09-17 02:00 | 342 | 330
2017-09-17 02:30 | 333 | 321
2017-09-17 03:00 | 330 | 317
2017-09-17 03:30 | 330 | 318
2017-09-17 04:00 | 334 | 323
2017-09-17 04:30 | 337 | 326
2017-09-17 05:00 | 339 | 327
2017-09-17 05:30 | 345 | 334
2017-09-17 06:00 | 351 | 339
2017-09-17 06:30 | 371 | 359
2017-09-17 07:00 | 378 | 369
2017-09-17 07:30 | 392 | 383
2017-09-17 08:00 | 403 | 395
2017-09-17 08:30 | 410 | 403
2017-09-17 09:00 | 407 | 401
2017-09-17 09:30 | 412 | 407
2017-09-17 10:00 | 408 | 404
2017-09-17 10:30 | 384 | 381
2017-09-17 11:00 | 372 | 368
2017-09-17 11:30 | 363 | 359
2017-09-17 12:00 | 352 | 348
2017-09-17 12:30 | 351 | 347
2017-09-17 13:00 | 347 | 343
2017-09-17 13:30 | 342 | 339
2017-09-17 14:00 | 363 | 360
2017-09-17 14:30 | 369 | 365
2017-09-17 15:00 | 375 | 372
2017-09-17 15:30 | 391 | 388
2017-09-17 16:00 | 411 | 407
2017-09-17 16:30 | 425 | 422
2017-09-17 17:00 | 436 | 433
2017-09-17 17:30 | 448 | 446
2017-09-17 18:00 | 469 | 468
2017-09-17 18:30 | 478 | 478
2017-09-17 19:00 | 476 | 476
2017-09-17 19:30 | 473 | 472
2017-09-17 20:00 | 468 | 468
2017-09-17 20:30 | 466 | 465
2017-09-17 21:00 | 449 | 447
2017-09-17 21:30 | 443 | 441
2017-09-17 22:00 | 439 | 437
2017-09-17 22:30 | 415 | 413
2017-09-17 23:00 | 401 | 399
2017-09-17 23:30 | 392 | 390
2017-09-18 | 375 | 371
2017-09-18 00:30 | 359 | 353
2017-09-18 01:00 | 349 | 342
2017-09-18 01:30 | 344 | 335
2017-09-18 02:00 | 334 | 325
2017-09-18 02:30 | 329 | 319
2017-09-18 03:00 | 325 | 314
2017-09-18 03:30 | 322 | 311
2017-09-18 04:00 | 324 | 314
2017-09-18 04:30 | 335 | 325
2017-09-18 05:00 | 347 | 338
2017-09-18 05:30 | 362 | 356
2017-09-18 06:00 | 379 | 374
2017-09-18 06:30 | 410 | 408
2017-09-18 07:00 | 433 | 432
2017-09-18 07:30 | 457 | 456
2017-09-18 08:00 | 469 | 469
2017-09-18 08:30 | 468 | 468
2017-09-18 09:00 | 470 | 469
2017-09-18 09:30 | 470 | 470
2017-09-18 10:00 | 467 | 467
2017-09-18 10:30 | 466 | 466
2017-09-18 11:00 | 461 | 461
2017-09-18 11:30 | 455 | 455
2017-09-18 12:00 | 453 | 453
2017-09-18 12:30 | 446 | 446
2017-09-18 13:00 | 440 | 440
2017-09-18 13:30 | 443 | 443
2017-09-18 14:00 | 450 | 450
2017-09-18 14:30 | 461 | 461
2017-09-18 15:00 | 474 | 474
2017-09-18 15:30 | 491 | 490
2017-09-18 16:00 | 490 | 490
2017-09-18 16:30 | 499 | 499
2017-09-18 17:00 | 507 | 507
2017-09-18 17:30 | 505 | 505
2017-09-18 18:00 | 515 | 515
2017-09-18 18:30 | 528 | 528
2017-09-18 19:00 | 527 | 526
2017-09-18 19:30 | 523 | 522
2017-09-18 20:00 | 526 | 524
2017-09-18 20:30 | 516 | 514
2017-09-18 21:00 | 501 | 499
2017-09-18 21:30 | 495 | 492
2017-09-18 22:00 | 489 | 487
2017-09-18 22:30 | 458 | 456
2017-09-18 23:00 | 435 | 433
2017-09-18 23:30 | 416 | 413
2017-09-19 | 397 | 392
2017-09-19 00:30 | 382 | 374
2017-09-19 01:00 | 370 | 361
2017-09-19 01:30 | 357 | 347
2017-09-19 02:00 | 348 | 337
2017-09-19 02:30 | 342 | 327
2017-09-19 03:00 | 341 | 328
2017-09-19 03:30 | 343 | 329
2017-09-19 04:00 | 345 | 332
2017-09-19 04:30 | 358 | 345
2017-09-19 05:00 | 369 | 358
2017-09-19 05:30 | 385 | 376
2017-09-19 06:00 | 395 | 388
2017-09-19 06:30 | 431 | 426
2017-09-19 07:00 | 449 | 447
2017-09-19 07:30 | 475 | 474
2017-09-19 08:00 | 485 | 484
2017-09-19 08:30 | 489 | 489
2017-09-19 09:00 | 479 | 479
2017-09-19 09:30 | 472 | 472
2017-09-19 10:00 | 467 | 467
2017-09-19 10:30 | 462 | 462
2017-09-19 11:00 | 457 | 456
2017-09-19 11:30 | 452 | 452
2017-09-19 12:00 | 460 | 460
2017-09-19 12:30 | 464 | 464
2017-09-19 13:00 | 466 | 466
2017-09-19 13:30 | 473 | 473
2017-09-19 14:00 | 482 | 482
2017-09-19 14:30 | 493 | 493
2017-09-19 15:00 | 501 | 501
2017-09-19 15:30 | 516 | 515
2017-09-19 16:00 | 532 | 530
2017-09-19 16:30 | 547 | 544
2017-09-19 17:00 | 554 | 551
2017-09-19 17:30 | 557 | 554
2017-09-19 18:00 | 564 | 561
2017-09-19 18:30 | 567 | 564
2017-09-19 19:00 | 564 | 561
2017-09-19 19:30 | 554 | 549
2017-09-19 20:00 | 552 | 547
2017-09-19 20:30 | 545 | 539
2017-09-19 21:00 | 533 | 527
2017-09-19 21:30 | 519 | 510
2017-09-19 22:00 | 504 | 497
2017-09-19 22:30 | 479 | 473
2017-09-19 23:00 | 455 | 454
2017-09-19 23:30 | 437 | 436
2017-09-20 | 411 | 409
2017-09-20 00:30 | 395 | 392
2017-09-20 01:00 | 384 | 380
2017-09-20 01:30 | 378 | 373
2017-09-20 02:00 | 369 | 363
2017-09-20 02:30 | 365 | 359
2017-09-20 03:00 | 358 | 352
2017-09-20 03:30 | 355 | 349
2017-09-20 04:00 | 348 | 343
2017-09-20 04:30 | 365 | 359
2017-09-20 05:00 | 374 | 369
2017-09-20 05:30 | 400 | 397
2017-09-20 06:00 | 419 | 416
2017-09-20 06:30 | 445 | 444
2017-09-20 07:00 | 461 | 460
2017-09-20 07:30 | 487 | 487
2017-09-20 08:00 | 496 | 495
2017-09-20 08:30 | 494 | 493
2017-09-20 09:00 | 485 | 485
2017-09-20 09:30 | 482 | 481
2017-09-20 10:00 | 475 | 474
2017-09-20 10:30 | 465 | 465
2017-09-20 11:00 | 465 | 464
2017-09-20 11:30 | 461 | 461
2017-09-20 12:00 | 463 | 462
2017-09-20 12:30 | 464 | 464
2017-09-20 13:00 | 465 | 464
2017-09-20 13:30 | 470 | 470
2017-09-20 14:00 | 478 | 477
2017-09-20 14:30 | 488 | 488
2017-09-20 15:00 | 503 | 502
2017-09-20 15:30 | 510 | 509
2017-09-20 16:00 | 525 | 524
2017-09-20 16:30 | 541 | 540
2017-09-20 17:00 | 552 | 550
2017-09-20 17:30 | 550 | 548
2017-09-20 18:00 | 555 | 553
2017-09-20 18:30 | 561 | 559
2017-09-20 19:00 | 557 | 555
2017-09-20 19:30 | 546 | 544
2017-09-20 20:00 | 534 | 533
2017-09-20 20:30 | 530 | 529
2017-09-20 21:00 | 514 | 514
2017-09-20 21:30 | 497 | 496
2017-09-20 22:00 | 483 | 482
2017-09-20 22:30 | 457 | 455
2017-09-20 23:00 | 445 | 444
2017-09-20 23:30 | 437 | 436
2017-09-21 | 416 | 413
2017-09-21 00:30 | 399 | 395
2017-09-21 01:00 | 378 | 373
2017-09-21 01:30 | 370 | 363
2017-09-21 02:00 | 364 | 357
2017-09-21 02:30 | 352 | 346
2017-09-21 03:00 | 349 | 343
2017-09-21 03:30 | 350 | 344
2017-09-21 04:00 | 353 | 346
2017-09-21 04:30 | 360 | 354
2017-09-21 05:00 | 369 | 364
2017-09-21 05:30 | 392 | 388
2017-09-21 06:00 | 407 | 403
2017-09-21 06:30 | 432 | 429
2017-09-21 07:00 | 456 | 455
2017-09-21 07:30 | 480 | 480
2017-09-21 08:00 | 484 | 483
2017-09-21 08:30 | 488 | 487
2017-09-21 09:00 | 495 | 495
2017-09-21 09:30 | 506 | 505
2017-09-21 10:00 | 503 | 502
2017-09-21 10:30 | 500 | 499
2017-09-21 11:00 | 493 | 492
2017-09-21 11:30 | 482 | 481
2017-09-21 12:00 | 482 | 480
2017-09-21 12:30 | 481 | 480
2017-09-21 13:00 | 479 | 478
2017-09-21 13:30 | 481 | 480
2017-09-21 14:00 | 484 | 483
2017-09-21 14:30 | 494 | 492
2017-09-21 15:00 | 511 | 509
2017-09-21 15:30 | 519 | 517
2017-09-21 16:00 | 525 | 524
2017-09-21 16:30 | 536 | 534
2017-09-21 17:00 | 544 | 542
2017-09-21 17:30 | 547 | 545
2017-09-21 18:00 | 551 | 549
2017-09-21 18:30 | 556 | 555
2017-09-21 19:00 | 559 | 557
2017-09-21 19:30 | 548 | 546
2017-09-21 20:00 | 540 | 539
2017-09-21 20:30 | 538 | 537
2017-09-21 21:00 | 526 | 525
2017-09-21 21:30 | 516 | 513
2017-09-21 22:00 | 504 | 501
2017-09-21 22:30 | 475 | 472
2017-09-21 23:00 | 461 | 458
2017-09-21 23:30 | 446 | 444
2017-09-22 | 426 | 423
2017-09-22 00:30 | 405 | 401
2017-09-22 01:00 | 395 | 390
2017-09-22 01:30 | 384 | 377
2017-09-22 02:00 | 375 | 367
2017-09-22 02:30 | 363 | 355
2017-09-22 03:00 | 360 | 352
2017-09-22 03:30 | 358 | 350
2017-09-22 04:00 | 361 | 354
2017-09-22 04:30 | 366 | 358
2017-09-22 05:00 | 378 | 371
2017-09-22 05:30 | 402 | 397
2017-09-22 06:00 | 414 | 410
2017-09-22 06:30 | 445 | 443
2017-09-22 07:00 | 461 | 460
2017-09-22 07:30 | 490 | 490
2017-09-22 08:00 | 507 | 507
2017-09-22 08:30 | 505 | 505
2017-09-22 09:00 | 506 | 506
2017-09-22 09:30 | 504 | 504
2017-09-22 10:00 | 495 | 495
2017-09-22 10:30 | 494 | 494
2017-09-22 11:00 | 486 | 486
2017-09-22 11:30 | 480 | 480
2017-09-22 12:00 | 486 | 486
2017-09-22 12:30 | 491 | 491
2017-09-22 13:00 | 489 | 489
2017-09-22 13:30 | 490 | 490
2017-09-22 14:00 | 483 | 483
2017-09-22 14:30 | 494 | 494
2017-09-22 15:00 | 509 | 509
2017-09-22 15:30 | 522 | 521
2017-09-22 16:00 | 524 | 523
2017-09-22 16:30 | 516 | 516
2017-09-22 17:00 | 516 | 515
2017-09-22 17:30 | 508 | 507
2017-09-22 18:00 | 515 | 514
2017-09-22 18:30 | 517 | 516
2017-09-22 19:00 | 517 | 515
2017-09-22 19:30 | 499 | 497
2017-09-22 20:00 | 488 | 487
2017-09-22 20:30 | 488 | 487
2017-09-22 21:00 | 477 | 477
2017-09-22 21:30 | 470 | 469
2017-09-22 22:00 | 468 | 466
2017-09-22 22:30 | 446 | 444
2017-09-22 23:00 | 423 | 420
2017-09-22 23:30 | 413 | 409
2017-09-23 | 399 | 392
2017-09-23 00:30 | 381 | 375
2017-09-23 01:00 | 372 | 365
2017-09-23 01:30 | 365 | 357
2017-09-23 02:00 | 355 | 345
2017-09-23 02:30 | 342 | 333
2017-09-23 03:00 | 343 | 333
2017-09-23 03:30 | 343 | 333
2017-09-23 04:00 | 346 | 336
2017-09-23 04:30 | 345 | 334
2017-09-23 05:00 | 344 | 335
2017-09-23 05:30 | 359 | 350
2017-09-23 06:00 | 370 | 360
2017-09-23 06:30 | 381 | 372
2017-09-23 07:00 | 386 | 378
2017-09-23 07:30 | 398 | 392
2017-09-23 08:00 | 403 | 398
2017-09-23 08:30 | 408 | 404
2017-09-23 09:00 | 411 | 408
2017-09-23 09:30 | 409 | 407
2017-09-23 10:00 | 404 | 402
2017-09-23 10:30 | 403 | 402
2017-09-23 11:00 | 405 | 404
2017-09-23 11:30 | 403 | 402
2017-09-23 12:00 | 401 | 400
2017-09-23 12:30 | 403 | 402
2017-09-23 13:00 | 396 | 395
2017-09-23 13:30 | 394 | 393
2017-09-23 14:00 | 408 | 407
2017-09-23 14:30 | 412 | 411
2017-09-23 15:00 | 434 | 433
2017-09-23 15:30 | 458 | 456
2017-09-23 16:00 | 472 | 471
2017-09-23 16:30 | 472 | 471
2017-09-23 17:00 | 474 | 473
2017-09-23 17:30 | 467 | 466
2017-09-23 18:00 | 477 | 476
2017-09-23 18:30 | 487 | 487
2017-09-23 19:00 | 487 | 486
2017-09-23 19:30 | 470 | 469
2017-09-23 20:00 | 462 | 461
2017-09-23 20:30 | 459 | 459
2017-09-23 21:00 | 446 | 446
2017-09-23 21:30 | 442 | 441
2017-09-23 22:00 | 442 | 441
2017-09-23 22:30 | 434 | 432
2017-09-23 23:00 | 425 | 423
2017-09-23 23:30 | 416 | 414
2017-09-24 | 401 | 398
2017-09-24 00:30 | 385 | 380
2017-09-24 01:00 | 375 | 368
2017-09-24 01:30 | 358 | 350
2017-09-24 02:00 | 347 | 338
2017-09-24 02:30 | 331 | 322
2017-09-24 03:00 | 330 | 320
2017-09-24 03:30 | 322 | 311
2017-09-24 04:00 | 315 | 302
2017-09-24 04:30 | 321 | 308
2017-09-24 05:00 | 322 | 309
2017-09-24 05:30 | 334 | 321
2017-09-24 06:00 | 336 | 322
2017-09-24 06:30 | 343 | 329
2017-09-24 07:00 | 345 | 333
2017-09-24 07:30 | 356 | 346
2017-09-24 08:00 | 368 | 359
2017-09-24 08:30 | 378 | 370
2017-09-24 09:00 | 379 | 373
2017-09-24 09:30 | 380 | 374
2017-09-24 10:00 | 389 | 384
2017-09-24 10:30 | 387 | 383
2017-09-24 11:00 | 383 | 379
2017-09-24 11:30 | 376 | 373
2017-09-24 12:00 | 379 | 376
2017-09-24 12:30 | 381 | 378
2017-09-24 13:00 | 384 | 381
2017-09-24 13:30 | 386 | 384
2017-09-24 14:00 | 384 | 382
2017-09-24 14:30 | 397 | 396
2017-09-24 15:00 | 419 | 418
2017-09-24 15:30 | 438 | 436
2017-09-24 16:00 | 440 | 438
2017-09-24 16:30 | 442 | 440
2017-09-24 17:00 | 453 | 452
2017-09-24 17:30 | 451 | 449
2017-09-24 18:00 | 457 | 455
2017-09-24 18:30 | 475 | 474
2017-09-24 19:00 | 472 | 471
2017-09-24 19:30 | 462 | 461
2017-09-24 20:00 | 461 | 460
2017-09-24 20:30 | 453 | 453
2017-09-24 21:00 | 444 | 444
2017-09-24 21:30 | 436 | 435
2017-09-24 22:00 | 434 | 433
2017-09-24 22:30 | 420 | 419
2017-09-24 23:00 | 405 | 403
2017-09-24 23:30 | 399 | 397
2017-09-25 | 383 | 379
2017-09-25 00:30 | 366 | 358
2017-09-25 01:00 | 357 | 349
2017-09-25 01:30 | 347 | 338
2017-09-25 02:00 | 331 | 322
2017-09-25 02:30 | 315 | 306
2017-09-25 03:00 | 308 | 299
2017-09-25 03:30 | 310 | 301
2017-09-25 04:00 | 311 | 302
2017-09-25 04:30 | 330 | 322
2017-09-25 05:00 | 352 | 344
2017-09-25 05:30 | 381 | 375
2017-09-25 06:00 | 394 | 390
2017-09-25 06:30 | 418 | 416
2017-09-25 07:00 | 437 | 436
2017-09-25 07:30 | 473 | 472
2017-09-25 08:00 | 494 | 494
2017-09-25 08:30 | 499 | 499
2017-09-25 09:00 | 502 | 502
2017-09-25 09:30 | 502 | 501
2017-09-25 10:00 | 499 | 497
2017-09-25 10:30 | 502 | 500
2017-09-25 11:00 | 510 | 508
2017-09-25 11:30 | 516 | 514
2017-09-25 12:00 | 518 | 517
2017-09-25 12:30 | 525 | 524
2017-09-25 13:00 | 527 | 527
2017-09-25 13:30 | 538 | 534
2017-09-25 14:00 | 548 | 542
2017-09-25 14:30 | 559 | 553
2017-09-25 15:00 | 570 | 565
2017-09-25 15:30 | 579 | 574
2017-09-25 16:00 | 586 | 581
2017-09-25 16:30 | 592 | 586
2017-09-25 17:00 | 596 | 589
2017-09-25 17:30 | 611 | 602
2017-09-25 18:00 | 606 | 598
2017-09-25 18:30 | 601 | 592
2017-09-25 19:00 | 595 | 587
2017-09-25 19:30 | 559 | 553
2017-09-25 20:00 | 551 | 550
2017-09-25 20:30 | 547 | 546
2017-09-25 21:00 | 536 | 535
2017-09-25 21:30 | 506 | 505
2017-09-25 22:00 | 489 | 488
2017-09-25 22:30 | 471 | 469
2017-09-25 23:00 | 452 | 450
2017-09-25 23:30 | 432 | 431
2017-09-26 | 415 | 413
2017-09-26 00:30 | 395 | 392
2017-09-26 01:00 | 380 | 376
2017-09-26 01:30 | 374 | 369
2017-09-26 02:00 | 366 | 361
2017-09-26 02:30 | 352 | 346
2017-09-26 03:00 | 349 | 344
2017-09-26 03:30 | 337 | 331
2017-09-26 04:00 | 339 | 333
2017-09-26 04:30 | 349 | 344
2017-09-26 05:00 | 355 | 351
2017-09-26 05:30 | 385 | 383
2017-09-26 06:00 | 399 | 397
2017-09-26 06:30 | 419 | 419
2017-09-26 07:00 | 442 | 442
2017-09-26 07:30 | 469 | 469
2017-09-26 08:00 | 471 | 471
2017-09-26 08:30 | 469 | 469
2017-09-26 09:00 | 477 | 477
2017-09-26 09:30 | 488 | 488
2017-09-26 10:00 | 511 | 510
2017-09-26 10:30 | 525 | 524
2017-09-26 11:00 | 522 | 520
2017-09-26 11:30 | 486 | 484
2017-09-26 12:00 | 487 | 486
2017-09-26 12:30 | 467 | 466
2017-09-26 13:00 | 457 | 455
2017-09-26 13:30 | 471 | 470
2017-09-26 14:00 | 489 | 487
2017-09-26 14:30 | 495 | 493
2017-09-26 15:00 | 489 | 487
2017-09-26 15:30 | 495 | 494
2017-09-26 16:00 | 498 | 496
2017-09-26 16:30 | 505 | 503
2017-09-26 17:00 | 522 | 520
2017-09-26 17:30 | 521 | 519
2017-09-26 18:00 | 517 | 515
2017-09-26 18:30 | 527 | 526
2017-09-26 19:00 | 538 | 536
2017-09-26 19:30 | 517 | 515
2017-09-26 20:00 | 495 | 494
2017-09-26 20:30 | 494 | 492
2017-09-26 21:00 | 490 | 489
2017-09-26 21:30 | 474 | 472
2017-09-26 22:00 | 452 | 450
2017-09-26 22:30 | 439 | 436
2017-09-26 23:00 | 418 | 414
2017-09-26 23:30 | 396 | 393
2017-09-27 | 364 | 358
2017-09-27 00:30 | 344 | 338
2017-09-27 01:00 | 332 | 324
2017-09-27 01:30 | 312 | 303
2017-09-27 02:00 | 308 | 298
2017-09-27 02:30 | 301 | 291
2017-09-27 03:00 | 299 | 289
2017-09-27 03:30 | 299 | 288
2017-09-27 04:00 | 304 | 294
2017-09-27 04:30 | 314 | 304
2017-09-27 05:00 | 321 | 313
2017-09-27 05:30 | 334 | 329
2017-09-27 06:00 | 351 | 346
2017-09-27 06:30 | 401 | 400
2017-09-27 07:00 | 429 | 428
2017-09-27 07:30 | 467 | 467
2017-09-27 08:00 | 488 | 487
2017-09-27 08:30 | 481 | 480
2017-09-27 09:00 | 490 | 489
2017-09-27 09:30 | 494 | 493
2017-09-27 10:00 | 495 | 494
2017-09-27 10:30 | 494 | 494
2017-09-27 11:00 | 502 | 501
2017-09-27 11:30 | 503 | 502
2017-09-27 12:00 | 507 | 507
2017-09-27 12:30 | 499 | 498
2017-09-27 13:00 | 493 | 493
2017-09-27 13:30 | 493 | 492
2017-09-27 14:00 | 496 | 495
2017-09-27 14:30 | 494 | 493
2017-09-27 15:00 | 490 | 490
2017-09-27 15:30 | 483 | 482
2017-09-27 16:00 | 495 | 495
2017-09-27 16:30 | 510 | 509
2017-09-27 17:00 | 525 | 524
2017-09-27 17:30 | 528 | 527
2017-09-27 18:00 | 539 | 538
2017-09-27 18:30 | 542 | 539
2017-09-27 19:00 | 542 | 540
2017-09-27 19:30 | 535 | 533
2017-09-27 20:00 | 520 | 517
2017-09-27 20:30 | 508 | 506
2017-09-27 21:00 | 488 | 487
2017-09-27 21:30 | 475 | 474
2017-09-27 22:00 | 464 | 463
2017-09-27 22:30 | 452 | 451
2017-09-27 23:00 | 442 | 441
2017-09-27 23:30 | 429 | 428
2017-09-28 | 414 | 412
2017-09-28 00:30 | 376 | 373
2017-09-28 01:00 | 364 | 360
2017-09-28 01:30 | 359 | 354
2017-09-28 02:00 | 350 | 344
2017-09-28 02:30 | 324 | 318
2017-09-28 03:00 | 317 | 312
2017-09-28 03:30 | 317 | 312
2017-09-28 04:00 | 315 | 311
2017-09-28 04:30 | 325 | 321
2017-09-28 05:00 | 347 | 344
2017-09-28 05:30 | 368 | 367
2017-09-28 06:00 | 373 | 372
2017-09-28 06:30 | 400 | 400
2017-09-28 07:00 | 442 | 441
2017-09-28 07:30 | 466 | 466
2017-09-28 08:00 | 475 | 475
2017-09-28 08:30 | 480 | 480
2017-09-28 09:00 | 485 | 485
2017-09-28 09:30 | 485 | 485
2017-09-28 10:00 | 486 | 486
2017-09-28 10:30 | 487 | 487
2017-09-28 11:00 | 492 | 492
2017-09-28 11:30 | 497 | 497
2017-09-28 12:00 | 507 | 507
2017-09-28 12:30 | 513 | 513
2017-09-28 13:00 | 519 | 519
2017-09-28 13:30 | 530 | 529
2017-09-28 14:00 | 538 | 537
2017-09-28 14:30 | 552 | 551
2017-09-28 15:00 | 567 | 566
2017-09-28 15:30 | 590 | 585
2017-09-28 16:00 | 603 | 598
2017-09-28 16:30 | 618 | 613
2017-09-28 17:00 | 624 | 619
2017-09-28 17:30 | 611 | 605
2017-09-28 18:00 | 604 | 598
2017-09-28 18:30 | 605 | 598
2017-09-28 19:00 | 602 | 597
2017-09-28 19:30 | 582 | 579
2017-09-28 20:00 | 568 | 565
2017-09-28 20:30 | 559 | 555
2017-09-28 21:00 | 534 | 532
2017-09-28 21:30 | 514 | 513
2017-09-28 22:00 | 506 | 505
2017-09-28 22:30 | 484 | 483
2017-09-28 23:00 | 463 | 461
2017-09-28 23:30 | 437 | 435
2017-09-29 | 416 | 415
2017-09-29 00:30 | 395 | 394
2017-09-29 01:00 | 375 | 372
2017-09-29 01:30 | 366 | 362
2017-09-29 02:00 | 362 | 357
2017-09-29 02:30 | 353 | 348
2017-09-29 03:00 | 352 | 347
2017-09-29 03:30 | 352 | 347
2017-09-29 04:00 | 359 | 353
2017-09-29 04:30 | 368 | 363
2017-09-29 05:00 | 378 | 374
2017-09-29 05:30 | 398 | 394
2017-09-29 06:00 | 409 | 407
2017-09-29 06:30 | 432 | 431
2017-09-29 07:00 | 443 | 443
2017-09-29 07:30 | 455 | 455
2017-09-29 08:00 | 475 | 475
2017-09-29 08:30 | 496 | 496
2017-09-29 09:00 | 508 | 508
2017-09-29 09:30 | 516 | 516
2017-09-29 10:00 | 519 | 519
2017-09-29 10:30 | 523 | 523
2017-09-29 11:00 | 528 | 528
2017-09-29 11:30 | 530 | 529
2017-09-29 12:00 | 530 | 529
2017-09-29 12:30 | 539 | 539
2017-09-29 13:00 | 547 | 546
2017-09-29 13:30 | 551 | 550
2017-09-29 14:00 | 561 | 561
2017-09-29 14:30 | 582 | 581
2017-09-29 15:00 | 574 | 572
2017-09-29 15:30 | 575 | 574
2017-09-29 16:00 | 591 | 589
2017-09-29 16:30 | 593 | 591
2017-09-29 17:00 | 590 | 588
2017-09-29 17:30 | 571 | 569
2017-09-29 18:00 | 556 | 555
2017-09-29 18:30 | 552 | 551
2017-09-29 19:00 | 546 | 545
2017-09-29 19:30 | 536 | 534
2017-09-29 20:00 | 535 | 533
2017-09-29 20:30 | 521 | 520
2017-09-29 21:00 | 497 | 496
2017-09-29 21:30 | 480 | 478
2017-09-29 22:00 | 471 | 470
2017-09-29 22:30 | 457 | 455
2017-09-29 23:00 | 440 | 438
2017-09-29 23:30 | 420 | 418
2017-09-30 | 400 | 399
2017-09-30 00:30 | 384 | 382
2017-09-30 01:00 | 378 | 375
2017-09-30 01:30 | 369 | 366
2017-09-30 02:00 | 356 | 353
2017-09-30 02:30 | 335 | 331
2017-09-30 03:00 | 326 | 322
2017-09-30 03:30 | 322 | 318
2017-09-30 04:00 | 320 | 316
2017-09-30 04:30 | 318 | 315
2017-09-30 05:00 | 320 | 317
2017-09-30 05:30 | 334 | 331
2017-09-30 06:00 | 338 | 334
2017-09-30 06:30 | 346 | 343
2017-09-30 07:00 | 359 | 357
2017-09-30 07:30 | 379 | 378
2017-09-30 08:00 | 393 | 392
2017-09-30 08:30 | 398 | 397
2017-09-30 09:00 | 410 | 410
2017-09-30 09:30 | 421 | 420
2017-09-30 10:00 | 413 | 413
2017-09-30 10:30 | 419 | 419
2017-09-30 11:00 | 416 | 416
2017-09-30 11:30 | 413 | 412
2017-09-30 12:00 | 404 | 404
2017-09-30 12:30 | 405 | 405
2017-09-30 13:00 | 406 | 406
2017-09-30 13:30 | 415 | 415
2017-09-30 14:00 | 418 | 417
2017-09-30 14:30 | 439 | 438
2017-09-30 15:00 | 450 | 449
2017-09-30 15:30 | 452 | 452
2017-09-30 16:00 | 460 | 460
2017-09-30 16:30 | 464 | 463
2017-09-30 17:00 | 466 | 465
2017-09-30 17:30 | 455 | 453
2017-09-30 18:00 | 450 | 449
2017-09-30 18:30 | 460 | 459
2017-09-30 19:00 | 465 | 464
2017-09-30 19:30 | 446 | 445
2017-09-30 20:00 | 445 | 444
2017-09-30 20:30 | 436 | 436
2017-09-30 21:00 | 425 | 425
2017-09-30 21:30 | 421 | 421
2017-09-30 22:00 | 417 | 417
2017-09-30 22:30 | 403 | 403
2017-09-30 23:00 | 388 | 388
2017-09-30 23:30 | 376 | 375
2017-10-01 | 364 | 361
2017-10-01 00:30 | 350 | 346
2017-10-01 01:00 | 347 | 342
2017-10-01 01:30 | 342 | 337
2017-10-01 02:00 | 332 | 326
2017-10-01 02:30 | 320 | 314
2017-10-01 03:00 | 317 | 311
2017-10-01 03:30 | 307 | 302
2017-10-01 04:00 | 308 | 302
2017-10-01 04:30 | 312 | 306
2017-10-01 05:00 | 314 | 308
2017-10-01 05:30 | 324 | 318
2017-10-01 06:00 | 323 | 317
2017-10-01 06:30 | 341 | 335
2017-10-01 07:00 | 346 | 341
2017-10-01 07:30 | 367 | 362
2017-10-01 08:00 | 384 | 380
2017-10-01 08:30 | 378 | 375
2017-10-01 09:00 | 377 | 375
2017-10-01 09:30 | 369 | 367
2017-10-01 10:00 | 367 | 365
2017-10-01 10:30 | 379 | 377
2017-10-01 11:00 | 399 | 398
2017-10-01 11:30 | 397 | 396
2017-10-01 12:00 | 398 | 397
2017-10-01 12:30 | 395 | 394
2017-10-01 13:00 | 390 | 389
2017-10-01 13:30 | 379 | 378
2017-10-01 14:00 | 388 | 386
2017-10-01 14:30 | 393 | 391
2017-10-01 15:00 | 403 | 401
2017-10-01 15:30 | 406 | 405
2017-10-01 16:00 | 410 | 409
2017-10-01 16:30 | 426 | 424
2017-10-01 17:00 | 436 | 434
2017-10-01 17:30 | 436 | 435
2017-10-01 18:00 | 437 | 436
2017-10-01 18:30 | 435 | 434
2017-10-01 19:00 | 440 | 439
2017-10-01 19:30 | 428 | 427
2017-10-01 20:00 | 427 | 426
2017-10-01 20:30 | 419 | 417
2017-10-01 21:00 | 408 | 406
2017-10-01 21:30 | 401 | 399
2017-10-01 22:00 | 403 | 401
2017-10-01 22:30 | 380 | 378
2017-10-01 23:00 | 359 | 358
2017-10-01 23:30 | 355 | 352
2017-10-02 | 339 | 335
2017-10-02 00:30 | 325 | 320
2017-10-02 01:00 | 324 | 318
2017-10-02 01:30 | 326 | 319
2017-10-02 02:00 | 313 | 306
2017-10-02 02:30 | 309 | 301
2017-10-02 03:00 | 304 | 297
2017-10-02 03:30 | 303 | 296
2017-10-02 04:00 | 300 | 293
2017-10-02 04:30 | 311 | 303
2017-10-02 05:00 | 317 | 310
2017-10-02 05:30 | 327 | 320
2017-10-02 06:00 | 334 | 326
2017-10-02 06:30 | 346 | 339
2017-10-02 07:00 | 360 | 354
2017-10-02 07:30 | 384 | 380
2017-10-02 08:00 | 405 | 402
2017-10-02 08:30 | 413 | 411
2017-10-02 09:00 | 416 | 415
2017-10-02 09:30 | 418 | 418
2017-10-02 10:00 | 416 | 415
2017-10-02 10:30 | 419 | 419
2017-10-02 11:00 | 415 | 415
2017-10-02 11:30 | 424 | 424
2017-10-02 12:00 | 430 | 429
2017-10-02 12:30 | 421 | 420
2017-10-02 13:00 | 430 | 430
2017-10-02 13:30 | 423 | 422
2017-10-02 14:00 | 428 | 428
2017-10-02 14:30 | 436 | 435
2017-10-02 15:00 | 434 | 433
2017-10-02 15:30 | 439 | 438
2017-10-02 16:00 | 450 | 450
2017-10-02 16:30 | 457 | 456
2017-10-02 17:00 | 461 | 461
2017-10-02 17:30 | 470 | 469
2017-10-02 18:00 | 474 | 474
2017-10-02 18:30 | 481 | 481
2017-10-02 19:00 | 479 | 479
2017-10-02 19:30 | 466 | 465
2017-10-02 20:00 | 469 | 469
2017-10-02 20:30 | 462 | 461
2017-10-02 21:00 | 442 | 441
2017-10-02 21:30 | 429 | 429
2017-10-02 22:00 | 422 | 422
2017-10-02 22:30 | 411 | 410
2017-10-02 23:00 | 401 | 401
2017-10-02 23:30 | 390 | 389
2017-10-03 | 369 | 366
2017-10-03 00:30 | 345 | 340
2017-10-03 01:00 | 338 | 332
2017-10-03 01:30 | 343 | 335
2017-10-03 02:00 | 339 | 330
2017-10-03 02:30 | 335 | 326
2017-10-03 03:00 | 324 | 314
2017-10-03 03:30 | 324 | 314
2017-10-03 04:00 | 330 | 320
2017-10-03 04:30 | 343 | 334
2017-10-03 05:00 | 367 | 360
2017-10-03 05:30 | 383 | 378
2017-10-03 06:00 | 392 | 388
2017-10-03 06:30 | 419 | 418
2017-10-03 07:00 | 442 | 442
2017-10-03 07:30 | 485 | 485
2017-10-03 08:00 | 504 | 503
2017-10-03 08:30 | 495 | 495
2017-10-03 09:00 | 469 | 469
2017-10-03 09:30 | 468 | 467
2017-10-03 10:00 | 470 | 469
2017-10-03 10:30 | 463 | 462
2017-10-03 11:00 | 447 | 446
2017-10-03 11:30 | 439 | 439
2017-10-03 12:00 | 434 | 434
2017-10-03 12:30 | 444 | 444
2017-10-03 13:00 | 449 | 449
2017-10-03 13:30 | 441 | 441
2017-10-03 14:00 | 440 | 440
2017-10-03 14:30 | 446 | 446
2017-10-03 15:00 | 457 | 457
2017-10-03 15:30 | 481 | 480
2017-10-03 16:00 | 496 | 496
2017-10-03 16:30 | 507 | 506
2017-10-03 17:00 | 514 | 514
2017-10-03 17:30 | 516 | 515
2017-10-03 18:00 | 529 | 528
2017-10-03 18:30 | 537 | 535
2017-10-03 19:00 | 533 | 531
2017-10-03 19:30 | 520 | 517
2017-10-03 20:00 | 511 | 510
2017-10-03 20:30 | 486 | 485
2017-10-03 21:00 | 471 | 470
2017-10-03 21:30 | 458 | 457
2017-10-03 22:00 | 456 | 454
2017-10-03 22:30 | 437 | 437
2017-10-03 23:00 | 413 | 413
2017-10-03 23:30 | 404 | 404
2017-10-04 | 385 | 384
2017-10-04 00:30 | 368 | 366
2017-10-04 01:00 | 359 | 356
2017-10-04 01:30 | 349 | 346
2017-10-04 02:00 | 325 | 321
2017-10-04 02:30 | 317 | 313
2017-10-04 03:00 | 316 | 312
2017-10-04 03:30 | 322 | 317
2017-10-04 04:00 | 323 | 318
2017-10-04 04:30 | 334 | 329
2017-10-04 05:00 | 344 | 340
2017-10-04 05:30 | 362 | 359
2017-10-04 06:00 | 383 | 382
2017-10-04 06:30 | 410 | 409
2017-10-04 07:00 | 449 | 448
2017-10-04 07:30 | 487 | 486
2017-10-04 08:00 | 498 | 498
2017-10-04 08:30 | 489 | 489
2017-10-04 09:00 | 478 | 478
2017-10-04 09:30 | 475 | 475
2017-10-04 10:00 | 485 | 485
2017-10-04 10:30 | 493 | 492
2017-10-04 11:00 | 498 | 497
2017-10-04 11:30 | 489 | 489
2017-10-04 12:00 | 481 | 480
2017-10-04 12:30 | 469 | 468
2017-10-04 13:00 | 471 | 470
2017-10-04 13:30 | 469 | 468
2017-10-04 14:00 | 471 | 471
2017-10-04 14:30 | 471 | 471
2017-10-04 15:00 | 485 | 485
2017-10-04 15:30 | 495 | 494
2017-10-04 16:00 | 507 | 506
2017-10-04 16:30 | 518 | 517
2017-10-04 17:00 | 528 | 527
2017-10-04 17:30 | 534 | 532
2017-10-04 18:00 | 546 | 543
2017-10-04 18:30 | 551 | 549
2017-10-04 19:00 | 549 | 547
2017-10-04 19:30 | 536 | 532
2017-10-04 20:00 | 524 | 521
2017-10-04 20:30 | 517 | 514
2017-10-04 21:00 | 498 | 497
2017-10-04 21:30 | 486 | 485
2017-10-04 22:00 | 458 | 457
2017-10-04 22:30 | 444 | 443
2017-10-04 23:00 | 426 | 425
2017-10-04 23:30 | 411 | 411
2017-10-05 | 382 | 381
2017-10-05 00:30 | 363 | 360
2017-10-05 01:00 | 351 | 348
2017-10-05 01:30 | 343 | 339
2017-10-05 02:00 | 332 | 327
2017-10-05 02:30 | 316 | 310
2017-10-05 03:00 | 310 | 304
2017-10-05 03:30 | 319 | 314
2017-10-05 04:00 | 325 | 319
2017-10-05 04:30 | 331 | 326
2017-10-05 05:00 | 339 | 336
2017-10-05 05:30 | 388 | 384
2017-10-05 06:00 | 402 | 399
2017-10-05 06:30 | 419 | 419
2017-10-05 07:00 | 441 | 441
2017-10-05 07:30 | 464 | 464
2017-10-05 08:00 | 472 | 471
2017-10-05 08:30 | 470 | 470
2017-10-05 09:00 | 464 | 464
2017-10-05 09:30 | 470 | 470
2017-10-05 10:00 | 475 | 474
2017-10-05 10:30 | 473 | 473
2017-10-05 11:00 | 469 | 468
2017-10-05 11:30 | 469 | 469
2017-10-05 12:00 | 475 | 475
2017-10-05 12:30 | 482 | 482
2017-10-05 13:00 | 495 | 494
2017-10-05 13:30 | 502 | 501
2017-10-05 14:00 | 507 | 507
2017-10-05 14:30 | 513 | 512
2017-10-05 15:00 | 512 | 511
2017-10-05 15:30 | 524 | 519
2017-10-05 16:00 | 543 | 537
2017-10-05 16:30 | 560 | 553
2017-10-05 17:00 | 572 | 565
2017-10-05 17:30 | 566 | 556
2017-10-05 18:00 | 554 | 547
2017-10-05 18:30 | 564 | 557
2017-10-05 19:00 | 570 | 563
2017-10-05 19:30 | 554 | 547
2017-10-05 20:00 | 537 | 532
2017-10-05 20:30 | 541 | 534
2017-10-05 21:00 | 530 | 522
2017-10-05 21:30 | 512 | 500
2017-10-05 22:00 | 500 | 488
2017-10-05 22:30 | 483 | 471
2017-10-05 23:00 | 452 | 440
2017-10-05 23:30 | 439 | 428
2017-10-06 | 396 | 392
2017-10-06 00:30 | 376 | 371
2017-10-06 01:00 | 368 | 360
2017-10-06 01:30 | 361 | 352
2017-10-06 02:00 | 354 | 344
2017-10-06 02:30 | 350 | 335
2017-10-06 03:00 | 346 | 331
2017-10-06 03:30 | 340 | 325
2017-10-06 04:00 | 350 | 334
2017-10-06 04:30 | 353 | 339
2017-10-06 05:00 | 366 | 353
2017-10-06 05:30 | 379 | 368
2017-10-06 06:00 | 397 | 388
2017-10-06 06:30 | 420 | 415
2017-10-06 07:00 | 470 | 466
2017-10-06 07:30 | 499 | 495
2017-10-06 08:00 | 507 | 504
2017-10-06 08:30 | 506 | 504
2017-10-06 09:00 | 502 | 499
2017-10-06 09:30 | 501 | 499
2017-10-06 10:00 | 510 | 509
2017-10-06 10:30 | 503 | 503
2017-10-06 11:00 | 498 | 497
2017-10-06 11:30 | 504 | 502
2017-10-06 12:00 | 514 | 512
2017-10-06 12:30 | 523 | 521
2017-10-06 13:00 | 530 | 526
2017-10-06 13:30 | 549 | 546
2017-10-06 14:00 | 567 | 562
2017-10-06 14:30 | 595 | 586
2017-10-06 15:00 | 612 | 603
2017-10-06 15:30 | 605 | 592
2017-10-06 16:00 | 580 | 566
2017-10-06 16:30 | 585 | 570
2017-10-06 17:00 | 565 | 558
2017-10-06 17:30 | 568 | 560
2017-10-06 18:00 | 562 | 554
2017-10-06 18:30 | 565 | 555
2017-10-06 19:00 | 571 | 561
2017-10-06 19:30 | 546 | 544
2017-10-06 20:00 | 537 | 535
2017-10-06 20:30 | 530 | 528
2017-10-06 21:00 | 515 | 513
2017-10-06 21:30 | 497 | 493
2017-10-06 22:00 | 482 | 478
2017-10-06 22:30 | 479 | 473
2017-10-06 23:00 | 464 | 458
2017-10-06 23:30 | 447 | 438
2017-10-07 | 418 | 410
2017-10-07 00:30 | 394 | 384
2017-10-07 01:00 | 364 | 356
2017-10-07 01:30 | 356 | 348
2017-10-07 02:00 | 350 | 341
2017-10-07 02:30 | 348 | 338
2017-10-07 03:00 | 356 | 346
2017-10-07 03:30 | 361 | 350
2017-10-07 04:00 | 363 | 352
2017-10-07 04:30 | 368 | 356
2017-10-07 05:00 | 369 | 357
2017-10-07 05:30 | 372 | 361
2017-10-07 06:00 | 376 | 365
2017-10-07 06:30 | 388 | 377
2017-10-07 07:00 | 397 | 388
2017-10-07 07:30 | 422 | 415
2017-10-07 08:00 | 447 | 443
2017-10-07 08:30 | 424 | 421
2017-10-07 09:00 | 431 | 428
2017-10-07 09:30 | 439 | 437
2017-10-07 10:00 | 447 | 444
2017-10-07 10:30 | 441 | 439
2017-10-07 11:00 | 422 | 420
2017-10-07 11:30 | 421 | 418
2017-10-07 12:00 | 438 | 435
2017-10-07 12:30 | 444 | 440
2017-10-07 13:00 | 444 | 439
2017-10-07 13:30 | 449 | 445
2017-10-07 14:00 | 439 | 435
2017-10-07 14:30 | 434 | 431
2017-10-07 15:00 | 432 | 429
2017-10-07 15:30 | 440 | 436
2017-10-07 16:00 | 438 | 434
2017-10-07 16:30 | 450 | 447
2017-10-07 17:00 | 459 | 456
2017-10-07 17:30 | 460 | 457
2017-10-07 18:00 | 460 | 457
2017-10-07 18:30 | 475 | 473
2017-10-07 19:00 | 482 | 480
2017-10-07 19:30 | 474 | 471
2017-10-07 20:00 | 474 | 471
2017-10-07 20:30 | 470 | 468
2017-10-07 21:00 | 458 | 456
2017-10-07 21:30 | 451 | 448
2017-10-07 22:00 | 449 | 445
2017-10-07 22:30 | 429 | 425
2017-10-07 23:00 | 418 | 414
2017-10-07 23:30 | 407 | 402
2017-10-08 | 395 | 388
2017-10-08 00:30 | 380 | 370
2017-10-08 01:00 | 370 | 360
2017-10-08 01:30 | 355 | 344
2017-10-08 02:00 | 343 | 332
2017-10-08 02:30 | 352 | 340
2017-10-08 03:00 | 347 | 335
2017-10-08 03:30 | 347 | 335
2017-10-08 04:00 | 346 | 334
2017-10-08 04:30 | 336 | 323
2017-10-08 05:00 | 336 | 324
2017-10-08 05:30 | 345 | 332
2017-10-08 06:00 | 355 | 341
2017-10-08 06:30 | 380 | 367
2017-10-08 07:00 | 391 | 379
2017-10-08 07:30 | 401 | 390
2017-10-08 08:00 | 409 | 399
2017-10-08 08:30 | 403 | 395
2017-10-08 09:00 | 411 | 404
2017-10-08 09:30 | 423 | 419
2017-10-08 10:00 | 418 | 415
2017-10-08 10:30 | 429 | 427
2017-10-08 11:00 | 436 | 434
2017-10-08 11:30 | 436 | 434
2017-10-08 12:00 | 424 | 421
2017-10-08 12:30 | 401 | 399
2017-10-08 13:00 | 414 | 412
2017-10-08 13:30 | 431 | 429
2017-10-08 14:00 | 439 | 436
2017-10-08 14:30 | 460 | 456
2017-10-08 15:00 | 471 | 468
2017-10-08 15:30 | 470 | 467
2017-10-08 16:00 | 466 | 462
2017-10-08 16:30 | 466 | 462
2017-10-08 17:00 | 470 | 466
2017-10-08 17:30 | 472 | 469
2017-10-08 18:00 | 475 | 472
2017-10-08 18:30 | 488 | 486
2017-10-08 19:00 | 490 | 489
2017-10-08 19:30 | 479 | 476
2017-10-08 20:00 | 482 | 480
2017-10-08 20:30 | 474 | 471
2017-10-08 21:00 | 460 | 457
2017-10-08 21:30 | 445 | 443
2017-10-08 22:00 | 444 | 441
2017-10-08 22:30 | 430 | 427
2017-10-08 23:00 | 411 | 408
2017-10-08 23:30 | 410 | 405
2017-10-09 | 402 | 395
2017-10-09 00:30 | 386 | 377
2017-10-09 01:00 | 372 | 361
2017-10-09 01:30 | 357 | 346
2017-10-09 02:00 | 343 | 333
2017-10-09 02:30 | 342 | 331
2017-10-09 03:00 | 326 | 314
2017-10-09 03:30 | 332 | 321
2017-10-09 04:00 | 336 | 325
2017-10-09 04:30 | 360 | 350
2017-10-09 05:00 | 376 | 367
2017-10-09 05:30 | 404 | 397
2017-10-09 06:00 | 434 | 428
2017-10-09 06:30 | 450 | 447
2017-10-09 07:00 | 478 | 477
2017-10-09 07:30 | 528 | 526
2017-10-09 08:00 | 553 | 552
2017-10-09 08:30 | 554 | 553
2017-10-09 09:00 | 531 | 530
2017-10-09 09:30 | 521 | 520
2017-10-09 10:00 | 530 | 529
2017-10-09 10:30 | 530 | 529
2017-10-09 11:00 | 518 | 517
2017-10-09 11:30 | 512 | 511
2017-10-09 12:00 | 524 | 524
2017-10-09 12:30 | 553 | 551
2017-10-09 13:00 | 570 | 566
2017-10-09 13:30 | 571 | 565
2017-10-09 14:00 | 565 | 559
2017-10-09 14:30 | 580 | 574
2017-10-09 15:00 | 591 | 585
2017-10-09 15:30 | 606 | 599
2017-10-09 16:00 | 634 | 628
2017-10-09 16:30 | 636 | 628
2017-10-09 17:00 | 641 | 630
2017-10-09 17:30 | 652 | 638
2017-10-09 18:00 | 639 | 627
2017-10-09 18:30 | 632 | 625
2017-10-09 19:00 | 636 | 629
2017-10-09 19:30 | 626 | 618
2017-10-09 20:00 | 612 | 601
2017-10-09 20:30 | 605 | 593
2017-10-09 21:00 | 576 | 563
2017-10-09 21:30 | 551 | 536
2017-10-09 22:00 | 524 | 517
2017-10-09 22:30 | 503 | 497
2017-10-09 23:00 | 479 | 477
2017-10-09 23:30 | 465 | 462
2017-10-10 | 445 | 441
2017-10-10 00:30 | 421 | 415
2017-10-10 01:00 | 404 | 396
2017-10-10 01:30 | 395 | 386
2017-10-10 02:00 | 387 | 378
2017-10-10 02:30 | 384 | 374
2017-10-10 03:00 | 376 | 367
2017-10-10 03:30 | 374 | 364
2017-10-10 04:00 | 376 | 366
2017-10-10 04:30 | 380 | 371
2017-10-10 05:00 | 394 | 386
2017-10-10 05:30 | 417 | 410
2017-10-10 06:00 | 449 | 444
2017-10-10 06:30 | 479 | 476
2017-10-10 07:00 | 504 | 504
2017-10-10 07:30 | 539 | 539
2017-10-10 08:00 | 559 | 558
2017-10-10 08:30 | 560 | 559
2017-10-10 09:00 | 569 | 567
2017-10-10 09:30 | 579 | 574
2017-10-10 10:00 | 592 | 588
2017-10-10 10:30 | 595 | 590
2017-10-10 11:00 | 598 | 592
2017-10-10 11:30 | 610 | 605
2017-10-10 12:00 | 619 | 613
2017-10-10 12:30 | 627 | 622
2017-10-10 13:00 | 634 | 628
2017-10-10 13:30 | 638 | 631
2017-10-10 14:00 | 639 | 632
2017-10-10 14:30 | 649 | 643
2017-10-10 15:00 | 649 | 643
2017-10-10 15:30 | 655 | 648
2017-10-10 16:00 | 670 | 663
2017-10-10 16:30 | 678 | 671
2017-10-10 17:00 | 684 | 677
2017-10-10 17:30 | 678 | 671
2017-10-10 18:00 | 664 | 660
2017-10-10 18:30 | 656 | 651
2017-10-10 19:00 | 658 | 653
2017-10-10 19:30 | 643 | 637
2017-10-10 20:00 | 621 | 619
2017-10-10 20:30 | 609 | 608
2017-10-10 21:00 | 585 | 585
2017-10-10 21:30 | 561 | 560
2017-10-10 22:00 | 540 | 539
2017-10-10 22:30 | 516 | 515
2017-10-10 23:00 | 494 | 493
2017-10-10 23:30 | 469 | 468
2017-10-11 | 446 | 446
2017-10-11 00:30 | 428 | 427
2017-10-11 01:00 | 399 | 397
2017-10-11 01:30 | 384 | 381
2017-10-11 02:00 | 357 | 354
2017-10-11 02:30 | 356 | 353
2017-10-11 03:00 | 346 | 343
2017-10-11 03:30 | 341 | 338
2017-10-11 04:00 | 345 | 342
2017-10-11 04:30 | 362 | 359
2017-10-11 05:00 | 371 | 370
2017-10-11 05:30 | 414 | 413
2017-10-11 06:00 | 454 | 454
2017-10-11 06:30 | 494 | 494
2017-10-11 07:00 | 548 | 547
2017-10-11 07:30 | 588 | 588
2017-10-11 08:00 | 603 | 603
2017-10-11 08:30 | 591 | 591
2017-10-11 09:00 | 599 | 599
2017-10-11 09:30 | 607 | 607
2017-10-11 10:00 | 615 | 615
2017-10-11 10:30 | 613 | 612
2017-10-11 11:00 | 596 | 595
2017-10-11 11:30 | 592 | 591
2017-10-11 12:00 | 584 | 583
2017-10-11 12:30 | 589 | 588
2017-10-11 13:00 | 588 | 588
2017-10-11 13:30 | 611 | 610
2017-10-11 14:00 | 612 | 612
2017-10-11 14:30 | 607 | 607
2017-10-11 15:00 | 601 | 600
2017-10-11 15:30 | 611 | 610
2017-10-11 16:00 | 617 | 616
2017-10-11 16:30 | 627 | 626
2017-10-11 17:00 | 652 | 651
2017-10-11 17:30 | 644 | 643
2017-10-11 18:00 | 627 | 626
2017-10-11 18:30 | 624 | 623
2017-10-11 19:00 | 634 | 633
2017-10-11 19:30 | 618 | 616
2017-10-11 20:00 | 600 | 600
2017-10-11 20:30 | 588 | 587
2017-10-11 21:00 | 575 | 574
2017-10-11 21:30 | 551 | 551
2017-10-11 22:00 | 538 | 538
2017-10-11 22:30 | 511 | 511
2017-10-11 23:00 | 493 | 493
2017-10-11 23:30 | 464 | 464
2017-10-12 | 425 | 425
2017-10-12 00:30 | 398 | 397
2017-10-12 01:00 | 389 | 389
2017-10-12 01:30 | 365 | 363
2017-10-12 02:00 | 344 | 342
2017-10-12 02:30 | 339 | 337
2017-10-12 03:00 | 333 | 331
2017-10-12 03:30 | 329 | 327
2017-10-12 04:00 | 330 | 328
2017-10-12 04:30 | 338 | 336
2017-10-12 05:00 | 353 | 352
2017-10-12 05:30 | 391 | 390
2017-10-12 06:00 | 439 | 439
2017-10-12 06:30 | 494 | 494
2017-10-12 07:00 | 530 | 530
2017-10-12 07:30 | 565 | 563
2017-10-12 08:00 | 591 | 588
2017-10-12 08:30 | 605 | 603
2017-10-12 09:00 | 609 | 607
2017-10-12 09:30 | 611 | 610
2017-10-12 10:00 | 608 | 606
2017-10-12 10:30 | 606 | 604
2017-10-12 11:00 | 609 | 608
2017-10-12 11:30 | 605 | 603
2017-10-12 12:00 | 608 | 606
2017-10-12 12:30 | 608 | 606
2017-10-12 13:00 | 604 | 602
2017-10-12 13:30 | 602 | 601
2017-10-12 14:00 | 597 | 595
2017-10-12 14:30 | 597 | 595
2017-10-12 15:00 | 585 | 581
2017-10-12 15:30 | 593 | 589
2017-10-12 16:00 | 603 | 599
2017-10-12 16:30 | 608 | 604
2017-10-12 17:00 | 611 | 606
2017-10-12 17:30 | 613 | 608
2017-10-12 18:00 | 615 | 608
2017-10-12 18:30 | 614 | 609
2017-10-12 19:00 | 616 | 611
2017-10-12 19:30 | 605 | 598
2017-10-12 20:00 | 593 | 585
2017-10-12 20:30 | 588 | 580
2017-10-12 21:00 | 567 | 561
2017-10-12 21:30 | 547 | 538
2017-10-12 22:00 | 517 | 514
2017-10-12 22:30 | 496 | 494
2017-10-12 23:00 | 483 | 481
2017-10-12 23:30 | 458 | 456
2017-10-13 | 427 | 425
2017-10-13 00:30 | 392 | 389
2017-10-13 01:00 | 366 | 361
2017-10-13 01:30 | 364 | 358
2017-10-13 02:00 | 360 | 352
2017-10-13 02:30 | 356 | 347
2017-10-13 03:00 | 355 | 346
2017-10-13 03:30 | 344 | 336
2017-10-13 04:00 | 339 | 331
2017-10-13 04:30 | 339 | 332
2017-10-13 05:00 | 357 | 351
2017-10-13 05:30 | 387 | 383
2017-10-13 06:00 | 434 | 431
2017-10-13 06:30 | 481 | 480
2017-10-13 07:00 | 518 | 517
2017-10-13 07:30 | 557 | 552
2017-10-13 08:00 | 565 | 557
2017-10-13 08:30 | 559 | 553
2017-10-13 09:00 | 546 | 541
2017-10-13 09:30 | 550 | 546
2017-10-13 10:00 | 554 | 550
2017-10-13 10:30 | 564 | 559
2017-10-13 11:00 | 569 | 565
2017-10-13 11:30 | 571 | 569
2017-10-13 12:00 | 580 | 578
2017-10-13 12:30 | 592 | 590
2017-10-13 13:00 | 598 | 593
2017-10-13 13:30 | 588 | 583
2017-10-13 14:00 | 578 | 574
2017-10-13 14:30 | 586 | 582
2017-10-13 15:00 | 594 | 588
2017-10-13 15:30 | 610 | 604
2017-10-13 16:00 | 616 | 607
2017-10-13 16:30 | 619 | 609
2017-10-13 17:00 | 618 | 606
2017-10-13 17:30 | 607 | 594
2017-10-13 18:00 | 597 | 584
2017-10-13 18:30 | 590 | 579
2017-10-13 19:00 | 594 | 583
2017-10-13 19:30 | 579 | 572
2017-10-13 20:00 | 567 | 564
2017-10-13 20:30 | 546 | 545
2017-10-13 21:00 | 521 | 520
2017-10-13 21:30 | 505 | 503
2017-10-13 22:00 | 494 | 490
2017-10-13 22:30 | 479 | 476
2017-10-13 23:00 | 465 | 460
2017-10-13 23:30 | 446 | 441
2017-10-14 | 423 | 420
2017-10-14 00:30 | 392 | 388
2017-10-14 01:00 | 379 | 374
2017-10-14 01:30 | 369 | 362
2017-10-14 02:00 | 362 | 355
2017-10-14 02:30 | 351 | 343
2017-10-14 03:00 | 345 | 337
2017-10-14 03:30 | 339 | 331
2017-10-14 04:00 | 337 | 329
2017-10-14 04:30 | 344 | 336
2017-10-14 05:00 | 353 | 345
2017-10-14 05:30 | 363 | 355
2017-10-14 06:00 | 387 | 379
2017-10-14 06:30 | 404 | 398
2017-10-14 07:00 | 406 | 402
2017-10-14 07:30 | 427 | 423
2017-10-14 08:00 | 435 | 433
2017-10-14 08:30 | 450 | 449
2017-10-14 09:00 | 459 | 459
2017-10-14 09:30 | 467 | 466
2017-10-14 10:00 | 481 | 480
2017-10-14 10:30 | 483 | 482
2017-10-14 11:00 | 483 | 482
2017-10-14 11:30 | 474 | 472
2017-10-14 12:00 | 473 | 470
2017-10-14 12:30 | 479 | 476
2017-10-14 13:00 | 481 | 477
2017-10-14 13:30 | 479 | 474
2017-10-14 14:00 | 485 | 480
2017-10-14 14:30 | 487 | 481
2017-10-14 15:00 | 478 | 473
2017-10-14 15:30 | 479 | 476
2017-10-14 16:00 | 486 | 483
2017-10-14 16:30 | 471 | 468
2017-10-14 17:00 | 483 | 480
2017-10-14 17:30 | 483 | 481
2017-10-14 18:00 | 488 | 486
2017-10-14 18:30 | 499 | 498
2017-10-14 19:00 | 504 | 502
2017-10-14 19:30 | 491 | 490
2017-10-14 20:00 | 484 | 484
2017-10-14 20:30 | 469 | 468
2017-10-14 21:00 | 455 | 454
2017-10-14 21:30 | 447 | 445
2017-10-14 22:00 | 439 | 437
2017-10-14 22:30 | 422 | 419
2017-10-14 23:00 | 409 | 406
2017-10-14 23:30 | 400 | 396
2017-10-15 | 386 | 381
2017-10-15 00:30 | 377 | 370
2017-10-15 01:00 | 365 | 357
2017-10-15 01:30 | 348 | 339
2017-10-15 02:00 | 338 | 328
2017-10-15 02:30 | 338 | 328
2017-10-15 03:00 | 334 | 325
2017-10-15 03:30 | 333 | 324
2017-10-15 04:00 | 332 | 324
2017-10-15 04:30 | 336 | 328
2017-10-15 05:00 | 347 | 338
2017-10-15 05:30 | 353 | 344
2017-10-15 06:00 | 346 | 336
2017-10-15 06:30 | 355 | 347
2017-10-15 07:00 | 382 | 376
2017-10-15 07:30 | 399 | 393
2017-10-15 08:00 | 428 | 423
2017-10-15 08:30 | 454 | 451
2017-10-15 09:00 | 453 | 450
2017-10-15 09:30 | 435 | 433
2017-10-15 10:00 | 428 | 425
2017-10-15 10:30 | 451 | 450
2017-10-15 11:00 | 464 | 463
2017-10-15 11:30 | 461 | 460
2017-10-15 12:00 | 457 | 455
2017-10-15 12:30 | 462 | 460
2017-10-15 13:00 | 468 | 466
2017-10-15 13:30 | 465 | 462
2017-10-15 14:00 | 458 | 455
2017-10-15 14:30 | 471 | 469
2017-10-15 15:00 | 474 | 472
2017-10-15 15:30 | 481 | 478
2017-10-15 16:00 | 483 | 481
2017-10-15 16:30 | 489 | 487
2017-10-15 17:00 | 504 | 502
2017-10-15 17:30 | 507 | 504
2017-10-15 18:00 | 509 | 507
2017-10-15 18:30 | 520 | 517
2017-10-15 19:00 | 523 | 519
2017-10-15 19:30 | 509 | 504
2017-10-15 20:00 | 508 | 502
2017-10-15 20:30 | 508 | 504
2017-10-15 21:00 | 500 | 497
2017-10-15 21:30 | 479 | 476
2017-10-15 22:00 | 467 | 464
2017-10-15 22:30 | 444 | 441
2017-10-15 23:00 | 428 | 425
2017-10-15 23:30 | 420 | 416
2017-10-16 | 402 | 396
2017-10-16 00:30 | 378 | 372
2017-10-16 01:00 | 364 | 358
2017-10-16 01:30 | 355 | 348
2017-10-16 02:00 | 349 | 342
2017-10-16 02:30 | 338 | 331
2017-10-16 03:00 | 333 | 326
2017-10-16 03:30 | 334 | 327
2017-10-16 04:00 | 338 | 331
2017-10-16 04:30 | 349 | 343
2017-10-16 05:00 | 362 | 357
2017-10-16 05:30 | 390 | 386
2017-10-16 06:00 | 395 | 392
2017-10-16 06:30 | 422 | 421
2017-10-16 07:00 | 468 | 467
2017-10-16 07:30 | 504 | 501
2017-10-16 08:00 | 515 | 512
2017-10-16 08:30 | 528 | 526
2017-10-16 09:00 | 529 | 527
2017-10-16 09:30 | 535 | 533
2017-10-16 10:00 | 533 | 530
2017-10-16 10:30 | 541 | 539
2017-10-16 11:00 | 538 | 536
2017-10-16 11:30 | 530 | 528
2017-10-16 12:00 | 535 | 533
2017-10-16 12:30 | 538 | 536
2017-10-16 13:00 | 540 | 538
2017-10-16 13:30 | 550 | 548
2017-10-16 14:00 | 545 | 543
2017-10-16 14:30 | 548 | 546
2017-10-16 15:00 | 554 | 552
2017-10-16 15:30 | 561 | 558
2017-10-16 16:00 | 566 | 563
2017-10-16 16:30 | 569 | 567
2017-10-16 17:00 | 578 | 575
2017-10-16 17:30 | 582 | 579
2017-10-16 18:00 | 581 | 578
2017-10-16 18:30 | 582 | 580
2017-10-16 19:00 | 582 | 580
2017-10-16 19:30 | 568 | 565
2017-10-16 20:00 | 563 | 560
2017-10-16 20:30 | 558 | 556
2017-10-16 21:00 | 541 | 540
2017-10-16 21:30 | 524 | 522
2017-10-16 22:00 | 499 | 498
2017-10-16 22:30 | 475 | 473
2017-10-16 23:00 | 456 | 453
2017-10-16 23:30 | 435 | 433
2017-10-17 | 413 | 411
2017-10-17 00:30 | 393 | 389
2017-10-17 01:00 | 377 | 372
2017-10-17 01:30 | 365 | 359
2017-10-17 02:00 | 356 | 351
2017-10-17 02:30 | 350 | 344
2017-10-17 03:00 | 346 | 340
2017-10-17 03:30 | 349 | 343
2017-10-17 04:00 | 353 | 347
2017-10-17 04:30 | 356 | 350
2017-10-17 05:00 | 366 | 361
2017-10-17 05:30 | 382 | 379
2017-10-17 06:00 | 404 | 401
2017-10-17 06:30 | 445 | 444
2017-10-17 07:00 | 485 | 484
2017-10-17 07:30 | 518 | 518
2017-10-17 08:00 | 527 | 527
2017-10-17 08:30 | 541 | 536
2017-10-17 09:00 | 539 | 534
2017-10-17 09:30 | 538 | 533
2017-10-17 10:00 | 539 | 534
2017-10-17 10:30 | 536 | 531
2017-10-17 11:00 | 538 | 534
2017-10-17 11:30 | 538 | 533
2017-10-17 12:00 | 538 | 533
2017-10-17 12:30 | 545 | 540
2017-10-17 13:00 | 537 | 531
2017-10-17 13:30 | 539 | 534
2017-10-17 14:00 | 538 | 533
2017-10-17 14:30 | 533 | 528
2017-10-17 15:00 | 535 | 529
2017-10-17 15:30 | 541 | 534
2017-10-17 16:00 | 550 | 542
2017-10-17 16:30 | 554 | 547
2017-10-17 17:00 | 571 | 565
2017-10-17 17:30 | 574 | 567
2017-10-17 18:00 | 576 | 569
2017-10-17 18:30 | 576 | 569
2017-10-17 19:00 | 580 | 572
2017-10-17 19:30 | 569 | 560
2017-10-17 20:00 | 560 | 554
2017-10-17 20:30 | 552 | 546
2017-10-17 21:00 | 524 | 521
2017-10-17 21:30 | 500 | 499
2017-10-17 22:00 | 487 | 486
2017-10-17 22:30 | 462 | 460
2017-10-17 23:00 | 445 | 443
2017-10-17 23:30 | 431 | 428
2017-10-18 | 411 | 407
2017-10-18 00:30 | 385 | 380
2017-10-18 01:00 | 373 | 367
2017-10-18 01:30 | 359 | 352
2017-10-18 02:00 | 354 | 347
2017-10-18 02:30 | 349 | 341
2017-10-18 03:00 | 350 | 342
2017-10-18 03:30 | 338 | 330
2017-10-18 04:00 | 348 | 340
2017-10-18 04:30 | 356 | 349
2017-10-18 05:00 | 371 | 364
2017-10-18 05:30 | 391 | 385
2017-10-18 06:00 | 414 | 410
2017-10-18 06:30 | 455 | 452
2017-10-18 07:00 | 493 | 491
2017-10-18 07:30 | 519 | 517
2017-10-18 08:00 | 521 | 520
2017-10-18 08:30 | 517 | 516
2017-10-18 09:00 | 515 | 514
2017-10-18 09:30 | 519 | 518
2017-10-18 10:00 | 510 | 510
2017-10-18 10:30 | 519 | 518
2017-10-18 11:00 | 531 | 530
2017-10-18 11:30 | 521 | 520
2017-10-18 12:00 | 502 | 501
2017-10-18 12:30 | 502 | 501
2017-10-18 13:00 | 506 | 505
2017-10-18 13:30 | 517 | 516
2017-10-18 14:00 | 505 | 504
2017-10-18 14:30 | 512 | 511
2017-10-18 15:00 | 524 | 523
2017-10-18 15:30 | 535 | 534
2017-10-18 16:00 | 550 | 549
2017-10-18 16:30 | 555 | 554
2017-10-18 17:00 | 569 | 567
2017-10-18 17:30 | 575 | 573
2017-10-18 18:00 | 581 | 577
2017-10-18 18:30 | 589 | 581
2017-10-18 19:00 | 594 | 585
2017-10-18 19:30 | 585 | 575
2017-10-18 20:00 | 565 | 561
2017-10-18 20:30 | 552 | 549
2017-10-18 21:00 | 529 | 527
2017-10-18 21:30 | 509 | 507
2017-10-18 22:00 | 494 | 494
2017-10-18 22:30 | 475 | 474
2017-10-18 23:00 | 460 | 460
2017-10-18 23:30 | 446 | 444
2017-10-19 | 416 | 414
2017-10-19 00:30 | 386 | 383
2017-10-19 01:00 | 377 | 371
2017-10-19 01:30 | 367 | 361
2017-10-19 02:00 | 362 | 355
2017-10-19 02:30 | 361 | 354
2017-10-19 03:00 | 356 | 349
2017-10-19 03:30 | 357 | 350
2017-10-19 04:00 | 359 | 352
2017-10-19 04:30 | 366 | 360
2017-10-19 05:00 | 378 | 372
2017-10-19 05:30 | 397 | 392
2017-10-19 06:00 | 412 | 408
2017-10-19 06:30 | 449 | 447
2017-10-19 07:00 | 481 | 479
2017-10-19 07:30 | 501 | 500
2017-10-19 08:00 | 508 | 508
2017-10-19 08:30 | 511 | 510
2017-10-19 09:00 | 512 | 511
2017-10-19 09:30 | 511 | 510
2017-10-19 10:00 | 511 | 509
2017-10-19 10:30 | 509 | 507
2017-10-19 11:00 | 508 | 507
2017-10-19 11:30 | 507 | 506
2017-10-19 12:00 | 515 | 514
2017-10-19 12:30 | 509 | 507
2017-10-19 13:00 | 518 | 517
2017-10-19 13:30 | 516 | 515
2017-10-19 14:00 | 516 | 514
2017-10-19 14:30 | 522 | 520
2017-10-19 15:00 | 526 | 524
2017-10-19 15:30 | 533 | 531
2017-10-19 16:00 | 548 | 546
2017-10-19 16:30 | 557 | 554
2017-10-19 17:00 | 570 | 567
2017-10-19 17:30 | 568 | 564
2017-10-19 18:00 | 577 | 573
2017-10-19 18:30 | 582 | 578
2017-10-19 19:00 | 593 | 589
2017-10-19 19:30 | 586 | 581
2017-10-19 20:00 | 570 | 568
2017-10-19 20:30 | 552 | 550
2017-10-19 21:00 | 533 | 531
2017-10-19 21:30 | 515 | 512
2017-10-19 22:00 | 500 | 497
2017-10-19 22:30 | 485 | 482
2017-10-19 23:00 | 462 | 460
2017-10-19 23:30 | 443 | 441
2017-10-20 | 426 | 423
2017-10-20 00:30 | 398 | 394
2017-10-20 01:00 | 384 | 378
2017-10-20 01:30 | 374 | 367
2017-10-20 02:00 | 370 | 363
2017-10-20 02:30 | 366 | 359
2017-10-20 03:00 | 360 | 352
2017-10-20 03:30 | 362 | 354
2017-10-20 04:00 | 369 | 362
2017-10-20 04:30 | 371 | 364
2017-10-20 05:00 | 378 | 371
2017-10-20 05:30 | 398 | 392
2017-10-20 06:00 | 403 | 400
2017-10-20 06:30 | 435 | 433
2017-10-20 07:00 | 466 | 464
2017-10-20 07:30 | 487 | 485
2017-10-20 08:00 | 494 | 493
2017-10-20 08:30 | 489 | 489
2017-10-20 09:00 | 489 | 489
2017-10-20 09:30 | 497 | 497
2017-10-20 10:00 | 496 | 495
2017-10-20 10:30 | 500 | 499
2017-10-20 11:00 | 498 | 498
2017-10-20 11:30 | 485 | 484
2017-10-20 12:00 | 479 | 479
2017-10-20 12:30 | 481 | 481
2017-10-20 13:00 | 491 | 491
2017-10-20 13:30 | 490 | 490
2017-10-20 14:00 | 485 | 485
2017-10-20 14:30 | 486 | 486
2017-10-20 15:00 | 485 | 484
2017-10-20 15:30 | 485 | 484
2017-10-20 16:00 | 498 | 497
2017-10-20 16:30 | 511 | 511
2017-10-20 17:00 | 528 | 527
2017-10-20 17:30 | 532 | 531
2017-10-20 18:00 | 532 | 530
2017-10-20 18:30 | 541 | 539
2017-10-20 19:00 | 550 | 548
2017-10-20 19:30 | 535 | 534
2017-10-20 20:00 | 532 | 532
2017-10-20 20:30 | 528 | 527
2017-10-20 21:00 | 505 | 504
2017-10-20 21:30 | 490 | 490
2017-10-20 22:00 | 476 | 475
2017-10-20 22:30 | 456 | 455
2017-10-20 23:00 | 444 | 442
2017-10-20 23:30 | 431 | 429
2017-10-21 | 412 | 409
2017-10-21 00:30 | 391 | 387
2017-10-21 01:00 | 376 | 371
2017-10-21 01:30 | 371 | 365
2017-10-21 02:00 | 358 | 352
2017-10-21 02:30 | 354 | 348
2017-10-21 03:00 | 340 | 333
2017-10-21 03:30 | 334 | 327
2017-10-21 04:00 | 338 | 330
2017-10-21 04:30 | 345 | 338
2017-10-21 05:00 | 354 | 347
2017-10-21 05:30 | 362 | 355
2017-10-21 06:00 | 367 | 360
2017-10-21 06:30 | 386 | 380
2017-10-21 07:00 | 406 | 401
2017-10-21 07:30 | 442 | 439
2017-10-21 08:00 | 461 | 458
2017-10-21 08:30 | 475 | 472
2017-10-21 09:00 | 489 | 487
2017-10-21 09:30 | 503 | 502
2017-10-21 10:00 | 493 | 493
2017-10-21 10:30 | 486 | 485
2017-10-21 11:00 | 478 | 476
2017-10-21 11:30 | 474 | 473
2017-10-21 12:00 | 473 | 471
2017-10-21 12:30 | 470 | 468
2017-10-21 13:00 | 461 | 459
2017-10-21 13:30 | 457 | 455
2017-10-21 14:00 | 454 | 452
2017-10-21 14:30 | 454 | 452
2017-10-21 15:00 | 457 | 454
2017-10-21 15:30 | 453 | 450
2017-10-21 16:00 | 458 | 456
2017-10-21 16:30 | 460 | 458
2017-10-21 17:00 | 478 | 476
2017-10-21 17:30 | 480 | 478
2017-10-21 18:00 | 481 | 479
2017-10-21 18:30 | 492 | 490
2017-10-21 19:00 | 512 | 509
2017-10-21 19:30 | 504 | 501
2017-10-21 20:00 | 497 | 494
2017-10-21 20:30 | 488 | 484
2017-10-21 21:00 | 466 | 464
2017-10-21 21:30 | 458 | 456
2017-10-21 22:00 | 448 | 446
2017-10-21 22:30 | 434 | 431
2017-10-21 23:00 | 427 | 424
2017-10-21 23:30 | 415 | 412
2017-10-22 | 402 | 398
2017-10-22 00:30 | 372 | 366
2017-10-22 01:00 | 362 | 355
2017-10-22 01:30 | 357 | 350
2017-10-22 02:00 | 345 | 336
2017-10-22 02:30 | 341 | 331
2017-10-22 03:00 | 332 | 321
2017-10-22 03:30 | 335 | 324
2017-10-22 04:00 | 331 | 320
2017-10-22 04:30 | 334 | 323
2017-10-22 05:00 | 336 | 325
2017-10-22 05:30 | 337 | 325
2017-10-22 06:00 | 338 | 325
2017-10-22 06:30 | 336 | 324
2017-10-22 07:00 | 330 | 318
2017-10-22 07:30 | 340 | 329
2017-10-22 08:00 | 345 | 335
2017-10-22 08:30 | 344 | 336
2017-10-22 09:00 | 352 | 346
2017-10-22 09:30 | 353 | 348
2017-10-22 10:00 | 353 | 348
2017-10-22 10:30 | 351 | 347
2017-10-22 11:00 | 356 | 353
2017-10-22 11:30 | 359 | 356
2017-10-22 12:00 | 363 | 360
2017-10-22 12:30 | 366 | 363
2017-10-22 13:00 | 359 | 356
2017-10-22 13:30 | 356 | 353
2017-10-22 14:00 | 361 | 358
2017-10-22 14:30 | 364 | 361
2017-10-22 15:00 | 377 | 375
2017-10-22 15:30 | 389 | 387
2017-10-22 16:00 | 418 | 416
2017-10-22 16:30 | 441 | 440
2017-10-22 17:00 | 469 | 468
2017-10-22 17:30 | 481 | 480
2017-10-22 18:00 | 494 | 493
2017-10-22 18:30 | 511 | 509
2017-10-22 19:00 | 520 | 519
2017-10-22 19:30 | 510 | 508
2017-10-22 20:00 | 502 | 500
2017-10-22 20:30 | 501 | 498
2017-10-22 21:00 | 487 | 484
2017-10-22 21:30 | 472 | 469
2017-10-22 22:00 | 458 | 456
2017-10-22 22:30 | 443 | 442
2017-10-22 23:00 | 437 | 435
2017-10-22 23:30 | 425 | 423
2017-10-23 | 404 | 401
2017-10-23 00:30 | 378 | 374
2017-10-23 01:00 | 361 | 356
2017-10-23 01:30 | 348 | 342
2017-10-23 02:00 | 342 | 335
2017-10-23 02:30 | 338 | 331
2017-10-23 03:00 | 336 | 329
2017-10-23 03:30 | 338 | 330
2017-10-23 04:00 | 330 | 323
2017-10-23 04:30 | 349 | 343
2017-10-23 05:00 | 364 | 359
2017-10-23 05:30 | 389 | 385
2017-10-23 06:00 | 382 | 379
2017-10-23 06:30 | 415 | 414
2017-10-23 07:00 | 448 | 448
2017-10-23 07:30 | 472 | 471
2017-10-23 08:00 | 474 | 474
2017-10-23 08:30 | 470 | 470
2017-10-23 09:00 | 469 | 469
2017-10-23 09:30 | 501 | 500
2017-10-23 10:00 | 534 | 529
2017-10-23 10:30 | 536 | 531
2017-10-23 11:00 | 519 | 513
2017-10-23 11:30 | 503 | 497
2017-10-23 12:00 | 506 | 500
2017-10-23 12:30 | 499 | 493
2017-10-23 13:00 | 475 | 469
2017-10-23 13:30 | 469 | 463
2017-10-23 14:00 | 491 | 485
2017-10-23 14:30 | 498 | 492
2017-10-23 15:00 | 492 | 486
2017-10-23 15:30 | 511 | 505
2017-10-23 16:00 | 533 | 527
2017-10-23 16:30 | 540 | 533
2017-10-23 17:00 | 555 | 548
2017-10-23 17:30 | 564 | 557
2017-10-23 18:00 | 572 | 564
2017-10-23 18:30 | 586 | 578
2017-10-23 19:00 | 592 | 585
2017-10-23 19:30 | 581 | 572
2017-10-23 20:00 | 575 | 568
2017-10-23 20:30 | 573 | 566
2017-10-23 21:00 | 549 | 541
2017-10-23 21:30 | 523 | 519
2017-10-23 22:00 | 508 | 505
2017-10-23 22:30 | 485 | 482
2017-10-23 23:00 | 466 | 461
2017-10-23 23:30 | 445 | 442
2017-10-24 | 426 | 421
2017-10-24 00:30 | 401 | 394
2017-10-24 01:00 | 386 | 379
2017-10-24 01:30 | 371 | 363
2017-10-24 02:00 | 363 | 355
2017-10-24 02:30 | 359 | 351
2017-10-24 03:00 | 358 | 350
2017-10-24 03:30 | 357 | 349
2017-10-24 04:00 | 359 | 351
2017-10-24 04:30 | 369 | 361
2017-10-24 05:00 | 382 | 375
2017-10-24 05:30 | 406 | 399
2017-10-24 06:00 | 400 | 395
2017-10-24 06:30 | 421 | 419
2017-10-24 07:00 | 449 | 448
2017-10-24 07:30 | 470 | 470
2017-10-24 08:00 | 462 | 462
2017-10-24 08:30 | 495 | 495
2017-10-24 09:00 | 481 | 481
2017-10-24 09:30 | 485 | 485
2017-10-24 10:00 | 488 | 488
2017-10-24 10:30 | 485 | 485
2017-10-24 11:00 | 485 | 484
2017-10-24 11:30 | 485 | 484
2017-10-24 12:00 | 488 | 487
2017-10-24 12:30 | 497 | 497
2017-10-24 13:00 | 500 | 500
2017-10-24 13:30 | 507 | 506
2017-10-24 14:00 | 511 | 511
2017-10-24 14:30 | 520 | 520
2017-10-24 15:00 | 481 | 481
2017-10-24 15:30 | 473 | 473
2017-10-24 16:00 | 482 | 482
2017-10-24 16:30 | 521 | 521
2017-10-24 17:00 | 540 | 539
2017-10-24 17:30 | 563 | 562
2017-10-24 18:00 | 562 | 560
2017-10-24 18:30 | 573 | 572
2017-10-24 19:00 | 586 | 585
2017-10-24 19:30 | 573 | 571
2017-10-24 20:00 | 568 | 565
2017-10-24 20:30 | 555 | 554
2017-10-24 21:00 | 541 | 540
2017-10-24 21:30 | 522 | 521
2017-10-24 22:00 | 509 | 507
2017-10-24 22:30 | 484 | 482
2017-10-24 23:00 | 456 | 454
2017-10-24 23:30 | 442 | 440
2017-10-25 | 420 | 417
2017-10-25 00:30 | 397 | 392
2017-10-25 01:00 | 392 | 386
2017-10-25 01:30 | 374 | 367
2017-10-25 02:00 | 364 | 356
2017-10-25 02:30 | 357 | 348
2017-10-25 03:00 | 357 | 348
2017-10-25 03:30 | 356 | 347
2017-10-25 04:00 | 360 | 351
2017-10-25 04:30 | 368 | 359
2017-10-25 05:00 | 373 | 364
2017-10-25 05:30 | 375 | 368
2017-10-25 06:00 | 392 | 386
2017-10-25 06:30 | 430 | 426
2017-10-25 07:00 | 449 | 447
2017-10-25 07:30 | 469 | 467
2017-10-25 08:00 | 461 | 458
2017-10-25 08:30 | 449 | 447
2017-10-25 09:00 | 442 | 441
2017-10-25 09:30 | 440 | 438
2017-10-25 10:00 | 436 | 435
2017-10-25 10:30 | 435 | 434
2017-10-25 11:00 | 441 | 440
2017-10-25 11:30 | 446 | 442
2017-10-25 12:00 | 450 | 447
2017-10-25 12:30 | 460 | 457
2017-10-25 13:00 | 472 | 470
2017-10-25 13:30 | 490 | 488
2017-10-25 14:00 | 491 | 488
2017-10-25 14:30 | 507 | 504
2017-10-25 15:00 | 515 | 513
2017-10-25 15:30 | 527 | 525
2017-10-25 16:00 | 542 | 540
2017-10-25 16:30 | 565 | 562
2017-10-25 17:00 | 583 | 580
2017-10-25 17:30 | 591 | 586
2017-10-25 18:00 | 590 | 583
2017-10-25 18:30 | 590 | 583
2017-10-25 19:00 | 605 | 598
2017-10-25 19:30 | 590 | 583
2017-10-25 20:00 | 577 | 576
2017-10-25 20:30 | 573 | 571
2017-10-25 21:00 | 553 | 552
2017-10-25 21:30 | 535 | 533
2017-10-25 22:00 | 516 | 514
2017-10-25 22:30 | 486 | 484
2017-10-25 23:00 | 464 | 461
2017-10-25 23:30 | 444 | 442
2017-10-26 | 424 | 422
2017-10-26 00:30 | 400 | 397
2017-10-26 01:00 | 390 | 386
2017-10-26 01:30 | 378 | 373
2017-10-26 02:00 | 373 | 368
2017-10-26 02:30 | 366 | 361
2017-10-26 03:00 | 363 | 357
2017-10-26 03:30 | 357 | 351
2017-10-26 04:00 | 356 | 350
2017-10-26 04:30 | 365 | 360
2017-10-26 05:00 | 371 | 367
2017-10-26 05:30 | 393 | 389
2017-10-26 06:00 | 415 | 412
2017-10-26 06:30 | 447 | 446
2017-10-26 07:00 | 473 | 471
2017-10-26 07:30 | 508 | 504
2017-10-26 08:00 | 503 | 500
2017-10-26 08:30 | 494 | 492
2017-10-26 09:00 | 491 | 489
2017-10-26 09:30 | 494 | 492
2017-10-26 10:00 | 496 | 495
2017-10-26 10:30 | 498 | 497
2017-10-26 11:00 | 507 | 506
2017-10-26 11:30 | 511 | 511
2017-10-26 12:00 | 521 | 521
2017-10-26 12:30 | 533 | 532
2017-10-26 13:00 | 541 | 541
2017-10-26 13:30 | 560 | 558
2017-10-26 14:00 | 573 | 572
2017-10-26 14:30 | 591 | 589
2017-10-26 15:00 | 605 | 605
2017-10-26 15:30 | 616 | 616
2017-10-26 16:00 | 640 | 639
2017-10-26 16:30 | 658 | 658
2017-10-26 17:00 | 661 | 660
2017-10-26 17:30 | 658 | 657
2017-10-26 18:00 | 650 | 649
2017-10-26 18:30 | 632 | 630
2017-10-26 19:00 | 631 | 630
2017-10-26 19:30 | 619 | 617
2017-10-26 20:00 | 616 | 612
2017-10-26 20:30 | 605 | 601
2017-10-26 21:00 | 580 | 577
2017-10-26 21:30 | 560 | 556
2017-10-26 22:00 | 538 | 535
2017-10-26 22:30 | 504 | 503
2017-10-26 23:00 | 478 | 476
2017-10-26 23:30 | 454 | 452
2017-10-27 | 430 | 425
2017-10-27 00:30 | 413 | 408
2017-10-27 01:00 | 398 | 394
2017-10-27 01:30 | 381 | 377
2017-10-27 02:00 | 372 | 367
2017-10-27 02:30 | 369 | 364
2017-10-27 03:00 | 368 | 363
2017-10-27 03:30 | 368 | 363
2017-10-27 04:00 | 370 | 365
2017-10-27 04:30 | 374 | 369
2017-10-27 05:00 | 375 | 371
2017-10-27 05:30 | 396 | 392
2017-10-27 06:00 | 409 | 407
2017-10-27 06:30 | 442 | 439
2017-10-27 07:00 | 470 | 468
2017-10-27 07:30 | 490 | 489
2017-10-27 08:00 | 489 | 487
2017-10-27 08:30 | 479 | 478
2017-10-27 09:00 | 470 | 469
2017-10-27 09:30 | 463 | 462
2017-10-27 10:00 | 458 | 457
2017-10-27 10:30 | 460 | 459
2017-10-27 11:00 | 462 | 461
2017-10-27 11:30 | 463 | 462
2017-10-27 12:00 | 468 | 467
2017-10-27 12:30 | 468 | 467
2017-10-27 13:00 | 477 | 476
2017-10-27 13:30 | 488 | 488
2017-10-27 14:00 | 505 | 505
2017-10-27 14:30 | 525 | 523
2017-10-27 15:00 | 545 | 540
2017-10-27 15:30 | 558 | 554
2017-10-27 16:00 | 581 | 577
2017-10-27 16:30 | 601 | 595
2017-10-27 17:00 | 606 | 598
2017-10-27 17:30 | 594 | 585
2017-10-27 18:00 | 588 | 578
2017-10-27 18:30 | 581 | 571
2017-10-27 19:00 | 586 | 579
2017-10-27 19:30 | 576 | 568
2017-10-27 20:00 | 568 | 561
2017-10-27 20:30 | 553 | 550
2017-10-27 21:00 | 534 | 533
2017-10-27 21:30 | 515 | 513
2017-10-27 22:00 | 495 | 492
2017-10-27 22:30 | 476 | 472
2017-10-27 23:00 | 459 | 456
2017-10-27 23:30 | 443 | 439
2017-10-28 | 424 | 419
2017-10-28 00:30 | 392 | 385
2017-10-28 01:00 | 380 | 372
2017-10-28 01:30 | 372 | 363
2017-10-28 02:00 | 357 | 349
2017-10-28 02:30 | 350 | 342
2017-10-28 03:00 | 345 | 337
2017-10-28 03:30 | 342 | 334
2017-10-28 04:00 | 341 | 332
2017-10-28 04:30 | 346 | 337
2017-10-28 05:00 | 343 | 335
2017-10-28 05:30 | 353 | 343
2017-10-28 06:00 | 360 | 351
2017-10-28 06:30 | 352 | 344
2017-10-28 07:00 | 358 | 352
2017-10-28 07:30 | 369 | 365
2017-10-28 08:00 | 372 | 369
2017-10-28 08:30 | 379 | 378
2017-10-28 09:00 | 387 | 385
2017-10-28 09:30 | 387 | 386
2017-10-28 10:00 | 388 | 387
2017-10-28 10:30 | 389 | 389
2017-10-28 11:00 | 393 | 393
2017-10-28 11:30 | 394 | 393
2017-10-28 12:00 | 397 | 397
2017-10-28 12:30 | 403 | 402
2017-10-28 13:00 | 400 | 399
2017-10-28 13:30 | 403 | 403
2017-10-28 14:00 | 415 | 414
2017-10-28 14:30 | 427 | 426
2017-10-28 15:00 | 441 | 440
2017-10-28 15:30 | 464 | 463
2017-10-28 16:00 | 481 | 480
2017-10-28 16:30 | 498 | 496
2017-10-28 17:00 | 507 | 506
2017-10-28 17:30 | 506 | 504
2017-10-28 18:00 | 510 | 508
2017-10-28 18:30 | 521 | 520
2017-10-28 19:00 | 531 | 529
2017-10-28 19:30 | 523 | 520
2017-10-28 20:00 | 523 | 520
2017-10-28 20:30 | 514 | 511
2017-10-28 21:00 | 495 | 493
2017-10-28 21:30 | 478 | 476
2017-10-28 22:00 | 470 | 467
2017-10-28 22:30 | 457 | 454
2017-10-28 23:00 | 447 | 443
2017-10-28 23:30 | 435 | 430
2017-10-29 | 408 | 405
2017-10-29 00:30 | 389 | 385
2017-10-29 01:00 | 377 | 372
2017-10-29 01:30 | 363 | 357
2017-10-29 02:00 | 349 | 342
2017-10-29 02:30 | 343 | 336
2017-10-29 03:00 | 339 | 331
2017-10-29 03:30 | 334 | 325
2017-10-29 04:00 | 323 | 314
2017-10-29 04:30 | 331 | 322
2017-10-29 05:00 | 333 | 325
2017-10-29 05:30 | 336 | 327
2017-10-29 06:00 | 348 | 338
2017-10-29 06:30 | 339 | 330
2017-10-29 07:00 | 334 | 326
2017-10-29 07:30 | 343 | 337
2017-10-29 08:00 | 349 | 344
2017-10-29 08:30 | 362 | 358
2017-10-29 09:00 | 356 | 354
2017-10-29 09:30 | 368 | 367
2017-10-29 10:00 | 381 | 380
2017-10-29 10:30 | 386 | 385
2017-10-29 11:00 | 386 | 386
2017-10-29 11:30 | 403 | 402
2017-10-29 12:00 | 414 | 413
2017-10-29 12:30 | 425 | 425
2017-10-29 13:00 | 444 | 443
2017-10-29 13:30 | 462 | 461
2017-10-29 14:00 | 478 | 478
2017-10-29 14:30 | 500 | 498
2017-10-29 15:00 | 518 | 516
2017-10-29 15:30 | 531 | 529
2017-10-29 16:00 | 551 | 549
2017-10-29 16:30 | 566 | 564
2017-10-29 17:00 | 577 | 574
2017-10-29 17:30 | 568 | 564
2017-10-29 18:00 | 561 | 559
2017-10-29 18:30 | 569 | 567
2017-10-29 19:00 | 578 | 575
2017-10-29 19:30 | 557 | 553
2017-10-29 20:00 | 539 | 536
2017-10-29 20:30 | 520 | 519
2017-10-29 21:00 | 494 | 493
2017-10-29 21:30 | 478 | 477
2017-10-29 22:00 | 457 | 455
2017-10-29 22:30 | 436 | 434
2017-10-29 23:00 | 428 | 425
2017-10-29 23:30 | 416 | 412
2017-10-30 | 400 | 396
2017-10-30 00:30 | 368 | 364
2017-10-30 01:00 | 364 | 359
2017-10-30 01:30 | 357 | 351
2017-10-30 02:00 | 350 | 344
2017-10-30 02:30 | 347 | 340
2017-10-30 03:00 | 346 | 339
2017-10-30 03:30 | 347 | 339
2017-10-30 04:00 | 349 | 342
2017-10-30 04:30 | 356 | 349
2017-10-30 05:00 | 366 | 360
2017-10-30 05:30 | 394 | 388
2017-10-30 06:00 | 425 | 422
2017-10-30 06:30 | 448 | 447
2017-10-30 07:00 | 485 | 485
2017-10-30 07:30 | 520 | 520
2017-10-30 08:00 | 536 | 535
2017-10-30 08:30 | 545 | 545
2017-10-30 09:00 | 560 | 560
2017-10-30 09:30 | 564 | 564
2017-10-30 10:00 | 580 | 577
2017-10-30 10:30 | 591 | 585
2017-10-30 11:00 | 579 | 574
2017-10-30 11:30 | 586 | 581
2017-10-30 12:00 | 597 | 592
2017-10-30 12:30 | 592 | 588
2017-10-30 13:00 | 595 | 591
2017-10-30 13:30 | 601 | 598
2017-10-30 14:00 | 617 | 614
2017-10-30 14:30 | 642 | 637
2017-10-30 15:00 | 667 | 663
2017-10-30 15:30 | 661 | 656
2017-10-30 16:00 | 640 | 634
2017-10-30 16:30 | 632 | 626
2017-10-30 17:00 | 643 | 637
2017-10-30 17:30 | 651 | 644
2017-10-30 18:00 | 644 | 635
2017-10-30 18:30 | 637 | 630
2017-10-30 19:00 | 647 | 642
2017-10-30 19:30 | 638 | 632
2017-10-30 20:00 | 636 | 631
2017-10-30 20:30 | 624 | 620
2017-10-30 21:00 | 604 | 600
2017-10-30 21:30 | 584 | 576
2017-10-30 22:00 | 553 | 548
2017-10-30 22:30 | 520 | 518
2017-10-30 23:00 | 501 | 498
2017-10-30 23:30 | 473 | 469
2017-10-31 | 445 | 441
2017-10-31 00:30 | 421 | 416
2017-10-31 01:00 | 412 | 408
2017-10-31 01:30 | 396 | 391
2017-10-31 02:00 | 385 | 380
2017-10-31 02:30 | 378 | 373
2017-10-31 03:00 | 381 | 376
2017-10-31 03:30 | 384 | 378
2017-10-31 04:00 | 386 | 380
2017-10-31 04:30 | 392 | 387
2017-10-31 05:00 | 383 | 378
2017-10-31 05:30 | 402 | 398
2017-10-31 06:00 | 426 | 423
2017-10-31 06:30 | 444 | 442
2017-10-31 07:00 | 470 | 469
2017-10-31 07:30 | 503 | 502
2017-10-31 08:00 | 494 | 493
2017-10-31 08:30 | 493 | 492
2017-10-31 09:00 | 488 | 488
2017-10-31 09:30 | 480 | 479
2017-10-31 10:00 | 480 | 479
2017-10-31 10:30 | 474 | 473
2017-10-31 11:00 | 469 | 469
2017-10-31 11:30 | 467 | 467
2017-10-31 12:00 | 468 | 467
2017-10-31 12:30 | 480 | 480
2017-10-31 13:00 | 483 | 483
2017-10-31 13:30 | 484 | 484
2017-10-31 14:00 | 494 | 493
2017-10-31 14:30 | 510 | 510
2017-10-31 15:00 | 524 | 524
2017-10-31 15:30 | 546 | 545
2017-10-31 16:00 | 557 | 556
2017-10-31 16:30 | 572 | 572
2017-10-31 17:00 | 585 | 584
2017-10-31 17:30 | 589 | 587
2017-10-31 18:00 | 582 | 579
2017-10-31 18:30 | 576 | 572
2017-10-31 19:00 | 585 | 582
2017-10-31 19:30 | 575 | 570
2017-10-31 20:00 | 567 | 564
2017-10-31 20:30 | 559 | 557
2017-10-31 21:00 | 538 | 536
2017-10-31 21:30 | 526 | 524
2017-10-31 22:00 | 516 | 512
2017-10-31 22:30 | 490 | 485
2017-10-31 23:00 | 464 | 460
2017-10-31 23:30 | 435 | 430
2017-11-01 | 416 | 410
2017-11-01 00:30 | 400 | 393
2017-11-01 01:00 | 390 | 383
2017-11-01 01:30 | 384 | 376
2017-11-01 02:00 | 377 | 368
2017-11-01 02:30 | 373 | 364
2017-11-01 03:00 | 372 | 362
2017-11-01 03:30 | 369 | 359
2017-11-01 04:00 | 387 | 377
2017-11-01 04:30 | 391 | 381
2017-11-01 05:00 | 388 | 380
2017-11-01 05:30 | 401 | 393
2017-11-01 06:00 | 412 | 406
2017-11-01 06:30 | 452 | 449
2017-11-01 07:00 | 484 | 483
2017-11-01 07:30 | 504 | 503
2017-11-01 08:00 | 513 | 512
2017-11-01 08:30 | 508 | 507
2017-11-01 09:00 | 500 | 499
2017-11-01 09:30 | 507 | 506
2017-11-01 10:00 | 509 | 508
2017-11-01 10:30 | 516 | 515
2017-11-01 11:00 | 511 | 510
2017-11-01 11:30 | 508 | 507
2017-11-01 12:00 | 509 | 508
2017-11-01 12:30 | 509 | 508
2017-11-01 13:00 | 499 | 499
2017-11-01 13:30 | 493 | 492
2017-11-01 14:00 | 494 | 493
2017-11-01 14:30 | 502 | 501
2017-11-01 15:00 | 511 | 510
2017-11-01 15:30 | 523 | 522
2017-11-01 16:00 | 539 | 538
2017-11-01 16:30 | 558 | 557
2017-11-01 17:00 | 575 | 574
2017-11-01 17:30 | 579 | 577
2017-11-01 18:00 | 577 | 574
2017-11-01 18:30 | 576 | 573
2017-11-01 19:00 | 588 | 585
2017-11-01 19:30 | 571 | 568
2017-11-01 20:00 | 562 | 560
2017-11-01 20:30 | 555 | 553
2017-11-01 21:00 | 537 | 536
2017-11-01 21:30 | 532 | 531
2017-11-01 22:00 | 520 | 518
2017-11-01 22:30 | 485 | 483
2017-11-01 23:00 | 454 | 452
2017-11-01 23:30 | 441 | 439
2017-11-02 | 420 | 417
2017-11-02 00:30 | 405 | 400
2017-11-02 01:00 | 409 | 401
2017-11-02 01:30 | 403 | 395
2017-11-02 02:00 | 392 | 384
2017-11-02 02:30 | 389 | 380
2017-11-02 03:00 | 386 | 377
2017-11-02 03:30 | 388 | 378
2017-11-02 04:00 | 381 | 371
2017-11-02 04:30 | 386 | 377
2017-11-02 05:00 | 376 | 368
2017-11-02 05:30 | 391 | 383
2017-11-02 06:00 | 411 | 405
2017-11-02 06:30 | 445 | 442
2017-11-02 07:00 | 480 | 478
2017-11-02 07:30 | 506 | 505
2017-11-02 08:00 | 511 | 509
2017-11-02 08:30 | 503 | 502
2017-11-02 09:00 | 498 | 498
2017-11-02 09:30 | 504 | 503
2017-11-02 10:00 | 509 | 507
2017-11-02 10:30 | 511 | 510
2017-11-02 11:00 | 512 | 511
2017-11-02 11:30 | 511 | 510
2017-11-02 12:00 | 512 | 512
2017-11-02 12:30 | 512 | 512
2017-11-02 13:00 | 517 | 516
2017-11-02 13:30 | 523 | 522
2017-11-02 14:00 | 534 | 533
2017-11-02 14:30 | 533 | 532
2017-11-02 15:00 | 546 | 545
2017-11-02 15:30 | 548 | 547
2017-11-02 16:00 | 566 | 565
2017-11-02 16:30 | 584 | 582
2017-11-02 17:00 | 594 | 592
2017-11-02 17:30 | 591 | 588
2017-11-02 18:00 | 581 | 579
2017-11-02 18:30 | 578 | 576
2017-11-02 19:00 | 588 | 588
2017-11-02 19:30 | 580 | 579
2017-11-02 20:00 | 577 | 576
2017-11-02 20:30 | 565 | 564
2017-11-02 21:00 | 539 | 538
2017-11-02 21:30 | 525 | 523
2017-11-02 22:00 | 512 | 511
2017-11-02 22:30 | 486 | 484
2017-11-02 23:00 | 455 | 454
2017-11-02 23:30 | 430 | 429
2017-11-03 | 412 | 410
2017-11-03 00:30 | 395 | 391
2017-11-03 01:00 | 382 | 377
2017-11-03 01:30 | 377 | 369
2017-11-03 02:00 | 365 | 357
2017-11-03 02:30 | 363 | 354
2017-11-03 03:00 | 364 | 356
2017-11-03 03:30 | 366 | 357
2017-11-03 04:00 | 374 | 366
2017-11-03 04:30 | 378 | 370
2017-11-03 05:00 | 357 | 350
2017-11-03 05:30 | 358 | 351
2017-11-03 06:00 | 382 | 377
2017-11-03 06:30 | 412 | 410
2017-11-03 07:00 | 456 | 454
2017-11-03 07:30 | 519 | 511
2017-11-03 08:00 | 531 | 522
2017-11-03 08:30 | 526 | 519
2017-11-03 09:00 | 526 | 519
2017-11-03 09:30 | 527 | 521
2017-11-03 10:00 | 519 | 513
2017-11-03 10:30 | 534 | 528
2017-11-03 11:00 | 537 | 532
2017-11-03 11:30 | 533 | 528
2017-11-03 12:00 | 537 | 532
2017-11-03 12:30 | 544 | 538
2017-11-03 13:00 | 545 | 540
2017-11-03 13:30 | 534 | 528
2017-11-03 14:00 | 534 | 528
2017-11-03 14:30 | 545 | 539
2017-11-03 15:00 | 562 | 557
2017-11-03 15:30 | 572 | 566
2017-11-03 16:00 | 587 | 581
2017-11-03 16:30 | 595 | 589
2017-11-03 17:00 | 598 | 592
2017-11-03 17:30 | 592 | 585
2017-11-03 18:00 | 582 | 571
2017-11-03 18:30 | 569 | 565
2017-11-03 19:00 | 581 | 578
2017-11-03 19:30 | 571 | 568
2017-11-03 20:00 | 566 | 562
2017-11-03 20:30 | 557 | 554
2017-11-03 21:00 | 543 | 540
2017-11-03 21:30 | 527 | 524
2017-11-03 22:00 | 504 | 501
2017-11-03 22:30 | 471 | 467
2017-11-03 23:00 | 436 | 433
2017-11-03 23:30 | 410 | 408
2017-11-04 | 395 | 391
2017-11-04 00:30 | 381 | 376
2017-11-04 01:00 | 370 | 364
2017-11-04 01:30 | 357 | 351
2017-11-04 02:00 | 346 | 340
2017-11-04 02:30 | 341 | 335
2017-11-04 03:00 | 341 | 334
2017-11-04 03:30 | 345 | 337
2017-11-04 04:00 | 349 | 340
2017-11-04 04:30 | 349 | 340
2017-11-04 05:00 | 352 | 343
2017-11-04 05:30 | 358 | 349
2017-11-04 06:00 | 358 | 350
2017-11-04 06:30 | 367 | 360
2017-11-04 07:00 | 376 | 370
2017-11-04 07:30 | 387 | 384
2017-11-04 08:00 | 399 | 397
2017-11-04 08:30 | 408 | 407
2017-11-04 09:00 | 412 | 411
2017-11-04 09:30 | 407 | 407
2017-11-04 10:00 | 406 | 406
2017-11-04 10:30 | 410 | 410
2017-11-04 11:00 | 410 | 410
2017-11-04 11:30 | 414 | 414
2017-11-04 12:00 | 408 | 408
2017-11-04 12:30 | 417 | 417
2017-11-04 13:00 | 433 | 433
2017-11-04 13:30 | 438 | 438
2017-11-04 14:00 | 444 | 444
2017-11-04 14:30 | 443 | 443
2017-11-04 15:00 | 464 | 464
2017-11-04 15:30 | 470 | 470
2017-11-04 16:00 | 482 | 482
2017-11-04 16:30 | 491 | 491
2017-11-04 17:00 | 517 | 516
2017-11-04 17:30 | 512 | 511
2017-11-04 18:00 | 506 | 504
2017-11-04 18:30 | 507 | 505
2017-11-04 19:00 | 522 | 520
2017-11-04 19:30 | 515 | 513
2017-11-04 20:00 | 509 | 507
2017-11-04 20:30 | 495 | 493
2017-11-04 21:00 | 477 | 475
2017-11-04 21:30 | 469 | 467
2017-11-04 22:00 | 463 | 461
2017-11-04 22:30 | 444 | 442
2017-11-04 23:00 | 423 | 422
2017-11-04 23:30 | 413 | 412
2017-11-05 | 394 | 391
2017-11-05 00:30 | 375 | 371
2017-11-05 01:00 | 368 | 364
2017-11-05 01:30 | 362 | 356
2017-11-05 02:00 | 351 | 345
2017-11-05 02:30 | 347 | 341
2017-11-05 03:00 | 350 | 344
2017-11-05 03:30 | 352 | 345
2017-11-05 04:00 | 356 | 349
2017-11-05 04:30 | 354 | 347
2017-11-05 05:00 | 355 | 348
2017-11-05 05:30 | 362 | 355
2017-11-05 06:00 | 363 | 357
2017-11-05 06:30 | 366 | 361
2017-11-05 07:00 | 374 | 370
2017-11-05 07:30 | 394 | 390
2017-11-05 08:00 | 411 | 409
2017-11-05 08:30 | 418 | 416
2017-11-05 09:00 | 419 | 418
2017-11-05 09:30 | 427 | 427
2017-11-05 10:00 | 430 | 429
2017-11-05 10:30 | 419 | 419
2017-11-05 11:00 | 403 | 403
2017-11-05 11:30 | 419 | 419
2017-11-05 12:00 | 414 | 414
2017-11-05 12:30 | 417 | 417
2017-11-05 13:00 | 421 | 421
2017-11-05 13:30 | 430 | 430
2017-11-05 14:00 | 437 | 437
2017-11-05 14:30 | 441 | 441
2017-11-05 15:00 | 448 | 448
2017-11-05 15:30 | 462 | 462
2017-11-05 16:00 | 463 | 463
2017-11-05 16:30 | 494 | 494
2017-11-05 17:00 | 506 | 506
2017-11-05 17:30 | 510 | 509
2017-11-05 18:00 | 513 | 513
2017-11-05 18:30 | 523 | 522
2017-11-05 19:00 | 527 | 527
2017-11-05 19:30 | 519 | 519
2017-11-05 20:00 | 516 | 516
2017-11-05 20:30 | 499 | 499
2017-11-05 21:00 | 471 | 471
2017-11-05 21:30 | 459 | 458
2017-11-05 22:00 | 449 | 449
2017-11-05 22:30 | 434 | 433
2017-11-05 23:00 | 422 | 422
2017-11-05 23:30 | 399 | 399
2017-11-06 | 378 | 377
2017-11-06 00:30 | 355 | 352
2017-11-06 01:00 | 349 | 345
2017-11-06 01:30 | 342 | 338
2017-11-06 02:00 | 330 | 325
2017-11-06 02:30 | 325 | 320
2017-11-06 03:00 | 322 | 317
2017-11-06 03:30 | 328 | 322
2017-11-06 04:00 | 338 | 333
2017-11-06 04:30 | 353 | 348
2017-11-06 05:00 | 348 | 344
2017-11-06 05:30 | 371 | 368
2017-11-06 06:00 | 393 | 391
2017-11-06 06:30 | 445 | 444
2017-11-06 07:00 | 498 | 497
2017-11-06 07:30 | 517 | 517
2017-11-06 08:00 | 523 | 523
2017-11-06 08:30 | 535 | 534
2017-11-06 09:00 | 546 | 546
2017-11-06 09:30 | 554 | 553
2017-11-06 10:00 | 553 | 552
2017-11-06 10:30 | 531 | 531
2017-11-06 11:00 | 541 | 540
2017-11-06 11:30 | 554 | 553
2017-11-06 12:00 | 549 | 549
2017-11-06 12:30 | 539 | 538
2017-11-06 13:00 | 542 | 542
2017-11-06 13:30 | 547 | 547
2017-11-06 14:00 | 529 | 528
2017-11-06 14:30 | 535 | 535
2017-11-06 15:00 | 560 | 560
2017-11-06 15:30 | 566 | 565
2017-11-06 16:00 | 585 | 581
2017-11-06 16:30 | 597 | 591
2017-11-06 17:00 | 610 | 604
2017-11-06 17:30 | 604 | 596
2017-11-06 18:00 | 591 | 582
2017-11-06 18:30 | 586 | 577
2017-11-06 19:00 | 592 | 585
2017-11-06 19:30 | 579 | 571
2017-11-06 20:00 | 571 | 566
2017-11-06 20:30 | 557 | 557
2017-11-06 21:00 | 535 | 534
2017-11-06 21:30 | 515 | 514
2017-11-06 22:00 | 491 | 490
2017-11-06 22:30 | 460 | 459
2017-11-06 23:00 | 437 | 435
2017-11-06 23:30 | 416 | 414
2017-11-07 | 400 | 398
2017-11-07 00:30 | 375 | 372
2017-11-07 01:00 | 369 | 364
2017-11-07 01:30 | 353 | 348
2017-11-07 02:00 | 342 | 337
2017-11-07 02:30 | 341 | 335
2017-11-07 03:00 | 341 | 335
2017-11-07 03:30 | 342 | 336
2017-11-07 04:00 | 349 | 343
2017-11-07 04:30 | 359 | 354
2017-11-07 05:00 | 370 | 365
2017-11-07 05:30 | 394 | 390
2017-11-07 06:00 | 408 | 404
2017-11-07 06:30 | 443 | 442
2017-11-07 07:00 | 466 | 466
2017-11-07 07:30 | 509 | 509
2017-11-07 08:00 | 521 | 520
2017-11-07 08:30 | 515 | 514
2017-11-07 09:00 | 520 | 520
2017-11-07 09:30 | 526 | 526
2017-11-07 10:00 | 534 | 533
2017-11-07 10:30 | 547 | 546
2017-11-07 11:00 | 554 | 552
2017-11-07 11:30 | 545 | 543
2017-11-07 12:00 | 517 | 516
2017-11-07 12:30 | 488 | 487
2017-11-07 13:00 | 502 | 501
2017-11-07 13:30 | 485 | 485
2017-11-07 14:00 | 501 | 501
2017-11-07 14:30 | 500 | 500
2017-11-07 15:00 | 513 | 513
2017-11-07 15:30 | 514 | 514
2017-11-07 16:00 | 519 | 518
2017-11-07 16:30 | 525 | 524
2017-11-07 17:00 | 543 | 542
2017-11-07 17:30 | 545 | 544
2017-11-07 18:00 | 542 | 540
2017-11-07 18:30 | 548 | 545
2017-11-07 19:00 | 558 | 556
2017-11-07 19:30 | 552 | 549
2017-11-07 20:00 | 544 | 542
2017-11-07 20:30 | 522 | 521
2017-11-07 21:00 | 497 | 495
2017-11-07 21:30 | 490 | 488
2017-11-07 22:00 | 477 | 475
2017-11-07 22:30 | 445 | 444
2017-11-07 23:00 | 426 | 424
2017-11-07 23:30 | 417 | 413
2017-11-08 | 392 | 388
2017-11-08 00:30 | 372 | 367
2017-11-08 01:00 | 363 | 357
2017-11-08 01:30 | 353 | 346
2017-11-08 02:00 | 345 | 337
2017-11-08 02:30 | 341 | 335
2017-11-08 03:00 | 339 | 332
2017-11-08 03:30 | 340 | 333
2017-11-08 04:00 | 344 | 336
2017-11-08 04:30 | 349 | 342
2017-11-08 05:00 | 348 | 341
2017-11-08 05:30 | 365 | 359
2017-11-08 06:00 | 389 | 385
2017-11-08 06:30 | 417 | 415
2017-11-08 07:00 | 453 | 449
2017-11-08 07:30 | 481 | 476
2017-11-08 08:00 | 478 | 471
2017-11-08 08:30 | 474 | 468
2017-11-08 09:00 | 464 | 460
2017-11-08 09:30 | 465 | 461
2017-11-08 10:00 | 462 | 458
2017-11-08 10:30 | 458 | 455
2017-11-08 11:00 | 446 | 446
2017-11-08 11:30 | 443 | 443
2017-11-08 12:00 | 480 | 480
2017-11-08 12:30 | 475 | 475
2017-11-08 13:00 | 451 | 451
2017-11-08 13:30 | 465 | 465
2017-11-08 14:00 | 473 | 473
2017-11-08 14:30 | 462 | 462
2017-11-08 15:00 | 468 | 467
2017-11-08 15:30 | 480 | 479
2017-11-08 16:00 | 494 | 493
2017-11-08 16:30 | 503 | 502
2017-11-08 17:00 | 513 | 511
2017-11-08 17:30 | 509 | 507
2017-11-08 18:00 | 509 | 508
2017-11-08 18:30 | 510 | 508
2017-11-08 19:00 | 523 | 522
2017-11-08 19:30 | 515 | 514
2017-11-08 20:00 | 508 | 507
2017-11-08 20:30 | 498 | 497
2017-11-08 21:00 | 478 | 478
2017-11-08 21:30 | 464 | 463
2017-11-08 22:00 | 443 | 442
2017-11-08 22:30 | 420 | 420
2017-11-08 23:00 | 402 | 401
2017-11-08 23:30 | 385 | 383
2017-11-09 | 370 | 366
2017-11-09 00:30 | 350 | 345
2017-11-09 01:00 | 343 | 337
2017-11-09 01:30 | 332 | 325
2017-11-09 02:00 | 323 | 316
2017-11-09 02:30 | 322 | 314
2017-11-09 03:00 | 319 | 311
2017-11-09 03:30 | 322 | 314
2017-11-09 04:00 | 330 | 323
2017-11-09 04:30 | 349 | 342
2017-11-09 05:00 | 348 | 341
2017-11-09 05:30 | 361 | 355
2017-11-09 06:00 | 401 | 396
2017-11-09 06:30 | 434 | 431
2017-11-09 07:00 | 470 | 465
2017-11-09 07:30 | 487 | 483
2017-11-09 08:00 | 483 | 481
2017-11-09 08:30 | 473 | 471
2017-11-09 09:00 | 474 | 473
2017-11-09 09:30 | 479 | 478
2017-11-09 10:00 | 489 | 489
2017-11-09 10:30 | 491 | 489
2017-11-09 11:00 | 485 | 483
2017-11-09 11:30 | 485 | 484
2017-11-09 12:00 | 485 | 483
2017-11-09 12:30 | 478 | 476
2017-11-09 13:00 | 482 | 480
2017-11-09 13:30 | 464 | 462
2017-11-09 14:00 | 462 | 460
2017-11-09 14:30 | 463 | 461
2017-11-09 15:00 | 450 | 448
2017-11-09 15:30 | 453 | 452
2017-11-09 16:00 | 481 | 480
2017-11-09 16:30 | 494 | 492
2017-11-09 17:00 | 511 | 509
2017-11-09 17:30 | 514 | 512
2017-11-09 18:00 | 510 | 508
2017-11-09 18:30 | 513 | 511
2017-11-09 19:00 | 535 | 530
2017-11-09 19:30 | 536 | 528
2017-11-09 20:00 | 530 | 522
2017-11-09 20:30 | 531 | 525
2017-11-09 21:00 | 509 | 507
2017-11-09 21:30 | 491 | 489
2017-11-09 22:00 | 470 | 469
2017-11-09 22:30 | 455 | 454
2017-11-09 23:00 | 423 | 422
2017-11-09 23:30 | 397 | 396
2017-11-10 | 375 | 372
2017-11-10 00:30 | 349 | 345
2017-11-10 01:00 | 336 | 331
2017-11-10 01:30 | 328 | 322
2017-11-10 02:00 | 323 | 317
2017-11-10 02:30 | 344 | 337
2017-11-10 03:00 | 346 | 339
2017-11-10 03:30 | 349 | 342
2017-11-10 04:00 | 359 | 352
2017-11-10 04:30 | 368 | 362
2017-11-10 05:00 | 371 | 365
2017-11-10 05:30 | 365 | 360
2017-11-10 06:00 | 384 | 380
2017-11-10 06:30 | 415 | 413
2017-11-10 07:00 | 437 | 435
2017-11-10 07:30 | 459 | 459
2017-11-10 08:00 | 478 | 477
2017-11-10 08:30 | 482 | 481
2017-11-10 09:00 | 479 | 478
2017-11-10 09:30 | 481 | 480
2017-11-10 10:00 | 489 | 488
2017-11-10 10:30 | 488 | 487
2017-11-10 11:00 | 469 | 467
2017-11-10 11:30 | 477 | 476
2017-11-10 12:00 | 488 | 487
2017-11-10 12:30 | 491 | 489
2017-11-10 13:00 | 495 | 493
2017-11-10 13:30 | 495 | 493
2017-11-10 14:00 | 485 | 483
2017-11-10 14:30 | 482 | 480
2017-11-10 15:00 | 491 | 489
2017-11-10 15:30 | 507 | 504
2017-11-10 16:00 | 521 | 518
2017-11-10 16:30 | 526 | 524
2017-11-10 17:00 | 532 | 529
2017-11-10 17:30 | 527 | 524
2017-11-10 18:00 | 525 | 522
2017-11-10 18:30 | 528 | 524
2017-11-10 19:00 | 545 | 541
2017-11-10 19:30 | 535 | 531
2017-11-10 20:00 | 525 | 521
2017-11-10 20:30 | 511 | 509
2017-11-10 21:00 | 487 | 485
2017-11-10 21:30 | 471 | 470
2017-11-10 22:00 | 458 | 456
2017-11-10 22:30 | 450 | 449
2017-11-10 23:00 | 433 | 432
2017-11-10 23:30 | 420 | 417
2017-11-11 | 400 | 396
2017-11-11 00:30 | 373 | 369
2017-11-11 01:00 | 366 | 361
2017-11-11 01:30 | 356 | 349
2017-11-11 02:00 | 345 | 339
2017-11-11 02:30 | 348 | 341
2017-11-11 03:00 | 343 | 335
2017-11-11 03:30 | 347 | 340
2017-11-11 04:00 | 353 | 345
2017-11-11 04:30 | 356 | 349
2017-11-11 05:00 | 355 | 347
2017-11-11 05:30 | 355 | 346
2017-11-11 06:00 | 356 | 348
2017-11-11 06:30 | 363 | 356
2017-11-11 07:00 | 377 | 371
2017-11-11 07:30 | 394 | 390
2017-11-11 08:00 | 411 | 408
2017-11-11 08:30 | 428 | 427
2017-11-11 09:00 | 434 | 431
2017-11-11 09:30 | 427 | 424
2017-11-11 10:00 | 424 | 421
2017-11-11 10:30 | 424 | 421
2017-11-11 11:00 | 411 | 408
2017-11-11 11:30 | 403 | 401
2017-11-11 12:00 | 405 | 402
2017-11-11 12:30 | 400 | 397
2017-11-11 13:00 | 403 | 400
2017-11-11 13:30 | 396 | 393
2017-11-11 14:00 | 397 | 393
2017-11-11 14:30 | 409 | 406
2017-11-11 15:00 | 419 | 416
2017-11-11 15:30 | 417 | 414
2017-11-11 16:00 | 415 | 412
2017-11-11 16:30 | 428 | 425
2017-11-11 17:00 | 440 | 437
2017-11-11 17:30 | 446 | 443
2017-11-11 18:00 | 449 | 447
2017-11-11 18:30 | 462 | 460
2017-11-11 19:00 | 480 | 479
2017-11-11 19:30 | 474 | 472
2017-11-11 20:00 | 467 | 465
2017-11-11 20:30 | 464 | 462
2017-11-11 21:00 | 437 | 436
2017-11-11 21:30 | 420 | 419
2017-11-11 22:00 | 413 | 411
2017-11-11 22:30 | 403 | 401
2017-11-11 23:00 | 393 | 391
2017-11-11 23:30 | 383 | 380
2017-11-12 | 368 | 363
2017-11-12 00:30 | 349 | 344
2017-11-12 01:00 | 345 | 339
2017-11-12 01:30 | 334 | 329
2017-11-12 02:00 | 328 | 323
2017-11-12 02:30 | 325 | 319
2017-11-12 03:00 | 323 | 318
2017-11-12 03:30 | 330 | 325
2017-11-12 04:00 | 341 | 335
2017-11-12 04:30 | 340 | 334
2017-11-12 05:00 | 338 | 331
2017-11-12 05:30 | 343 | 336
2017-11-12 06:00 | 338 | 330
2017-11-12 06:30 | 324 | 316
2017-11-12 07:00 | 350 | 345
2017-11-12 07:30 | 364 | 359
2017-11-12 08:00 | 363 | 359
2017-11-12 08:30 | 374 | 371
2017-11-12 09:00 | 381 | 379
2017-11-12 09:30 | 376 | 374
2017-11-12 10:00 | 374 | 373
2017-11-12 10:30 | 375 | 374
2017-11-12 11:00 | 364 | 363
2017-11-12 11:30 | 356 | 355
2017-11-12 12:00 | 355 | 354
2017-11-12 12:30 | 350 | 349
2017-11-12 13:00 | 348 | 347
2017-11-12 13:30 | 356 | 355
2017-11-12 14:00 | 368 | 367
2017-11-12 14:30 | 371 | 370
2017-11-12 15:00 | 384 | 383
2017-11-12 15:30 | 389 | 388
2017-11-12 16:00 | 408 | 407
2017-11-12 16:30 | 426 | 425
2017-11-12 17:00 | 438 | 437
2017-11-12 17:30 | 453 | 452
2017-11-12 18:00 | 455 | 454
2017-11-12 18:30 | 472 | 470
2017-11-12 19:00 | 495 | 493
2017-11-12 19:30 | 493 | 490
2017-11-12 20:00 | 485 | 482
2017-11-12 20:30 | 477 | 474
2017-11-12 21:00 | 456 | 453
2017-11-12 21:30 | 441 | 439
2017-11-12 22:00 | 429 | 428
2017-11-12 22:30 | 422 | 421
2017-11-12 23:00 | 415 | 414
2017-11-12 23:30 | 404 | 402
2017-11-13 | 384 | 382
2017-11-13 00:30 | 377 | 373
2017-11-13 01:00 | 366 | 362
2017-11-13 01:30 | 356 | 352
2017-11-13 02:00 | 352 | 348
2017-11-13 02:30 | 349 | 345
2017-11-13 03:00 | 351 | 347
2017-11-13 03:30 | 355 | 350
2017-11-13 04:00 | 359 | 354
2017-11-13 04:30 | 347 | 343
2017-11-13 05:00 | 355 | 350
2017-11-13 05:30 | 385 | 381
2017-11-13 06:00 | 401 | 399
2017-11-13 06:30 | 430 | 430
2017-11-13 07:00 | 458 | 457
2017-11-13 07:30 | 476 | 476
2017-11-13 08:00 | 486 | 485
2017-11-13 08:30 | 487 | 486
2017-11-13 09:00 | 482 | 481
2017-11-13 09:30 | 484 | 484
2017-11-13 10:00 | 480 | 480
2017-11-13 10:30 | 486 | 486
2017-11-13 11:00 | 491 | 490
2017-11-13 11:30 | 482 | 481
2017-11-13 12:00 | 488 | 487
2017-11-13 12:30 | 493 | 492
2017-11-13 13:00 | 491 | 489
2017-11-13 13:30 | 486 | 485
2017-11-13 14:00 | 488 | 486
2017-11-13 14:30 | 489 | 488
2017-11-13 15:00 | 508 | 507
2017-11-13 15:30 | 528 | 526
2017-11-13 16:00 | 546 | 544
2017-11-13 16:30 | 567 | 565
2017-11-13 17:00 | 590 | 582
2017-11-13 17:30 | 589 | 579
2017-11-13 18:00 | 584 | 573
2017-11-13 18:30 | 573 | 568
2017-11-13 19:00 | 585 | 583
2017-11-13 19:30 | 578 | 576
2017-11-13 20:00 | 577 | 573
2017-11-13 20:30 | 557 | 555
2017-11-13 21:00 | 524 | 523
2017-11-13 21:30 | 502 | 501
2017-11-13 22:00 | 486 | 486
2017-11-13 22:30 | 461 | 460
2017-11-13 23:00 | 440 | 440
2017-11-13 23:30 | 424 | 422
2017-11-14 | 404 | 401
2017-11-14 00:30 | 379 | 375
2017-11-14 01:00 | 358 | 353
2017-11-14 01:30 | 351 | 344
2017-11-14 02:00 | 347 | 340
2017-11-14 02:30 | 346 | 338
2017-11-14 03:00 | 342 | 334
2017-11-14 03:30 | 343 | 335
2017-11-14 04:00 | 344 | 336
2017-11-14 04:30 | 355 | 348
2017-11-14 05:00 | 360 | 353
2017-11-14 05:30 | 375 | 369
2017-11-14 06:00 | 395 | 390
2017-11-14 06:30 | 427 | 424
2017-11-14 07:00 | 459 | 457
2017-11-14 07:30 | 488 | 482
2017-11-14 08:00 | 494 | 484
2017-11-14 08:30 | 488 | 479
2017-11-14 09:00 | 477 | 469
2017-11-14 09:30 | 487 | 478
2017-11-14 10:00 | 481 | 471
2017-11-14 10:30 | 483 | 474
2017-11-14 11:00 | 480 | 472
2017-11-14 11:30 | 474 | 466
2017-11-14 12:00 | 483 | 474
2017-11-14 12:30 | 487 | 479
2017-11-14 13:00 | 488 | 480
2017-11-14 13:30 | 497 | 489
2017-11-14 14:00 | 502 | 494
2017-11-14 14:30 | 513 | 506
2017-11-14 15:00 | 525 | 517
2017-11-14 15:30 | 531 | 523
2017-11-14 16:00 | 553 | 545
2017-11-14 16:30 | 566 | 558
2017-11-14 17:00 | 575 | 568
2017-11-14 17:30 | 574 | 566
2017-11-14 18:00 | 573 | 563
2017-11-14 18:30 | 574 | 563
2017-11-14 19:00 | 585 | 576
2017-11-14 19:30 | 580 | 571
2017-11-14 20:00 | 573 | 564
2017-11-14 20:30 | 547 | 545
2017-11-14 21:00 | 526 | 522
2017-11-14 21:30 | 513 | 509
2017-11-14 22:00 | 502 | 499
2017-11-14 22:30 | 478 | 476
2017-11-14 23:00 | 453 | 451
2017-11-14 23:30 | 433 | 430
2017-11-15 | 413 | 409
2017-11-15 00:30 | 381 | 374
2017-11-15 01:00 | 375 | 367
2017-11-15 01:30 | 366 | 357
2017-11-15 02:00 | 359 | 350
2017-11-15 02:30 | 359 | 350
2017-11-15 03:00 | 358 | 348
2017-11-15 03:30 | 360 | 351
2017-11-15 04:00 | 359 | 350
2017-11-15 04:30 | 372 | 364
2017-11-15 05:00 | 380 | 371
2017-11-15 05:30 | 395 | 387
2017-11-15 06:00 | 408 | 403
2017-11-15 06:30 | 441 | 438
2017-11-15 07:00 | 461 | 460
2017-11-15 07:30 | 498 | 497
2017-11-15 08:00 | 508 | 507
2017-11-15 08:30 | 511 | 510
2017-11-15 09:00 | 517 | 516
2017-11-15 09:30 | 521 | 517
2017-11-15 10:00 | 522 | 520
2017-11-15 10:30 | 530 | 528
2017-11-15 11:00 | 524 | 522
2017-11-15 11:30 | 521 | 519
2017-11-15 12:00 | 512 | 511
2017-11-15 12:30 | 506 | 505
2017-11-15 13:00 | 517 | 517
2017-11-15 13:30 | 534 | 533
2017-11-15 14:00 | 531 | 529
2017-11-15 14:30 | 547 | 546
2017-11-15 15:00 | 549 | 547
2017-11-15 15:30 | 538 | 535
2017-11-15 16:00 | 538 | 535
2017-11-15 16:30 | 545 | 542
2017-11-15 17:00 | 563 | 560
2017-11-15 17:30 | 567 | 563
2017-11-15 18:00 | 564 | 561
2017-11-15 18:30 | 554 | 552
2017-11-15 19:00 | 573 | 571
2017-11-15 19:30 | 567 | 562
2017-11-15 20:00 | 561 | 555
2017-11-15 20:30 | 546 | 542
2017-11-15 21:00 | 528 | 526
2017-11-15 21:30 | 515 | 512
2017-11-15 22:00 | 491 | 488
2017-11-15 22:30 | 460 | 458
2017-11-15 23:00 | 437 | 435
2017-11-15 23:30 | 424 | 421
2017-11-16 | 408 | 402
2017-11-16 00:30 | 384 | 376
2017-11-16 01:00 | 377 | 369
2017-11-16 01:30 | 368 | 360
2017-11-16 02:00 | 354 | 347
2017-11-16 02:30 | 351 | 343
2017-11-16 03:00 | 355 | 346
2017-11-16 03:30 | 361 | 352
2017-11-16 04:00 | 368 | 359
2017-11-16 04:30 | 368 | 360
2017-11-16 05:00 | 369 | 360
2017-11-16 05:30 | 382 | 374
2017-11-16 06:00 | 406 | 398
2017-11-16 06:30 | 437 | 432
2017-11-16 07:00 | 468 | 465
2017-11-16 07:30 | 497 | 495
2017-11-16 08:00 | 507 | 505
2017-11-16 08:30 | 525 | 523
2017-11-16 09:00 | 522 | 520
2017-11-16 09:30 | 537 | 535
2017-11-16 10:00 | 539 | 538
2017-11-16 10:30 | 527 | 526
2017-11-16 11:00 | 529 | 528
2017-11-16 11:30 | 528 | 527
2017-11-16 12:00 | 523 | 522
2017-11-16 12:30 | 516 | 515
2017-11-16 13:00 | 530 | 528
2017-11-16 13:30 | 538 | 535
2017-11-16 14:00 | 540 | 537
2017-11-16 14:30 | 551 | 548
2017-11-16 15:00 | 561 | 558
2017-11-16 15:30 | 561 | 558
2017-11-16 16:00 | 557 | 553
2017-11-16 16:30 | 566 | 562
2017-11-16 17:00 | 578 | 573
2017-11-16 17:30 | 573 | 567
2017-11-16 18:00 | 566 | 559
2017-11-16 18:30 | 561 | 555
2017-11-16 19:00 | 573 | 569
2017-11-16 19:30 | 562 | 557
2017-11-16 20:00 | 548 | 543
2017-11-16 20:30 | 531 | 527
2017-11-16 21:00 | 502 | 501
2017-11-16 21:30 | 493 | 491
2017-11-16 22:00 | 480 | 478
2017-11-16 22:30 | 455 | 453
2017-11-16 23:00 | 431 | 430
2017-11-16 23:30 | 407 | 404
2017-11-17 | 393 | 389
2017-11-17 00:30 | 376 | 371
2017-11-17 01:00 | 369 | 363
2017-11-17 01:30 | 363 | 356
2017-11-17 02:00 | 352 | 345
2017-11-17 02:30 | 350 | 343
2017-11-17 03:00 | 349 | 342
2017-11-17 03:30 | 352 | 346
2017-11-17 04:00 | 351 | 345
2017-11-17 04:30 | 357 | 351
2017-11-17 05:00 | 353 | 346
2017-11-17 05:30 | 367 | 361
2017-11-17 06:00 | 389 | 385
2017-11-17 06:30 | 421 | 419
2017-11-17 07:00 | 459 | 458
2017-11-17 07:30 | 500 | 500
2017-11-17 08:00 | 512 | 511
2017-11-17 08:30 | 526 | 526
2017-11-17 09:00 | 529 | 528
2017-11-17 09:30 | 534 | 533
2017-11-17 10:00 | 535 | 533
2017-11-17 10:30 | 534 | 533
2017-11-17 11:00 | 518 | 517
2017-11-17 11:30 | 511 | 510
2017-11-17 12:00 | 513 | 512
2017-11-17 12:30 | 514 | 513
2017-11-17 13:00 | 517 | 517
2017-11-17 13:30 | 528 | 528
2017-11-17 14:00 | 526 | 525
2017-11-17 14:30 | 524 | 523
2017-11-17 15:00 | 529 | 528
2017-11-17 15:30 | 533 | 532
2017-11-17 16:00 | 541 | 540
2017-11-17 16:30 | 548 | 547
2017-11-17 17:00 | 553 | 551
2017-11-17 17:30 | 548 | 545
2017-11-17 18:00 | 541 | 537
2017-11-17 18:30 | 532 | 530
2017-11-17 19:00 | 542 | 541
2017-11-17 19:30 | 530 | 529
2017-11-17 20:00 | 525 | 525
2017-11-17 20:30 | 522 | 522
2017-11-17 21:00 | 500 | 499
2017-11-17 21:30 | 492 | 490
2017-11-17 22:00 | 481 | 478
2017-11-17 22:30 | 471 | 469
2017-11-17 23:00 | 450 | 449
2017-11-17 23:30 | 425 | 423
2017-11-18 | 408 | 405
2017-11-18 00:30 | 389 | 384
2017-11-18 01:00 | 380 | 375
2017-11-18 01:30 | 373 | 366
2017-11-18 02:00 | 365 | 357
2017-11-18 02:30 | 360 | 351
2017-11-18 03:00 | 362 | 354
2017-11-18 03:30 | 361 | 352
2017-11-18 04:00 | 362 | 354
2017-11-18 04:30 | 364 | 355
2017-11-18 05:00 | 361 | 352
2017-11-18 05:30 | 368 | 359
2017-11-18 06:00 | 380 | 371
2017-11-18 06:30 | 393 | 386
2017-11-18 07:00 | 408 | 403
2017-11-18 07:30 | 426 | 422
2017-11-18 08:00 | 442 | 439
2017-11-18 08:30 | 468 | 466
2017-11-18 09:00 | 481 | 480
2017-11-18 09:30 | 497 | 496
2017-11-18 10:00 | 495 | 495
2017-11-18 10:30 | 490 | 490
2017-11-18 11:00 | 476 | 476
2017-11-18 11:30 | 482 | 481
2017-11-18 12:00 | 484 | 483
2017-11-18 12:30 | 476 | 475
2017-11-18 13:00 | 475 | 474
2017-11-18 13:30 | 470 | 469
2017-11-18 14:00 | 465 | 464
2017-11-18 14:30 | 463 | 462
2017-11-18 15:00 | 466 | 464
2017-11-18 15:30 | 464 | 463
2017-11-18 16:00 | 465 | 464
2017-11-18 16:30 | 472 | 471
2017-11-18 17:00 | 479 | 478
2017-11-18 17:30 | 471 | 470
2017-11-18 18:00 | 461 | 459
2017-11-18 18:30 | 466 | 465
2017-11-18 19:00 | 489 | 489
2017-11-18 19:30 | 483 | 483
2017-11-18 20:00 | 480 | 479
2017-11-18 20:30 | 475 | 474
2017-11-18 21:00 | 456 | 455
2017-11-18 21:30 | 448 | 446
2017-11-18 22:00 | 444 | 441
2017-11-18 22:30 | 436 | 433
2017-11-18 23:00 | 421 | 418
2017-11-18 23:30 | 408 | 403
2017-11-19 | 395 | 390
2017-11-19 00:30 | 379 | 371
2017-11-19 01:00 | 374 | 364
2017-11-19 01:30 | 364 | 354
2017-11-19 02:00 | 352 | 341
2017-11-19 02:30 | 349 | 336
2017-11-19 03:00 | 350 | 337
2017-11-19 03:30 | 349 | 336
2017-11-19 04:00 | 349 | 335
2017-11-19 04:30 | 354 | 338
2017-11-19 05:00 | 356 | 333
2017-11-19 05:30 | 358 | 334
2017-11-19 06:00 | 361 | 338
2017-11-19 06:30 | 364 | 343
2017-11-19 07:00 | 356 | 335
2017-11-19 07:30 | 378 | 360
2017-11-19 08:00 | 395 | 380
2017-11-19 08:30 | 420 | 407
2017-11-19 09:00 | 437 | 428
2017-11-19 09:30 | 432 | 423
2017-11-19 10:00 | 435 | 427
2017-11-19 10:30 | 438 | 431
2017-11-19 11:00 | 434 | 427
2017-11-19 11:30 | 435 | 428
2017-11-19 12:00 | 439 | 433
2017-11-19 12:30 | 442 | 435
2017-11-19 13:00 | 433 | 426
2017-11-19 13:30 | 429 | 422
2017-11-19 14:00 | 420 | 414
2017-11-19 14:30 | 412 | 405
2017-11-19 15:00 | 420 | 413
2017-11-19 15:30 | 422 | 415
2017-11-19 16:00 | 430 | 424
2017-11-19 16:30 | 438 | 432
2017-11-19 17:00 | 450 | 445
2017-11-19 17:30 | 453 | 448
2017-11-19 18:00 | 461 | 456
2017-11-19 18:30 | 483 | 479
2017-11-19 19:00 | 504 | 502
2017-11-19 19:30 | 501 | 499
2017-11-19 20:00 | 499 | 496
2017-11-19 20:30 | 487 | 484
2017-11-19 21:00 | 468 | 465
2017-11-19 21:30 | 461 | 457
2017-11-19 22:00 | 447 | 442
2017-11-19 22:30 | 436 | 431
2017-11-19 23:00 | 415 | 409
2017-11-19 23:30 | 407 | 400
2017-11-20 | 394 | 386
2017-11-20 00:30 | 383 | 373
2017-11-20 01:00 | 375 | 363
2017-11-20 01:30 | 367 | 354
2017-11-20 02:00 | 359 | 344
2017-11-20 02:30 | 355 | 340
2017-11-20 03:00 | 349 | 333
2017-11-20 03:30 | 349 | 334
2017-11-20 04:00 | 350 | 335
2017-11-20 04:30 | 360 | 345
2017-11-20 05:00 | 366 | 352
2017-11-20 05:30 | 383 | 370
2017-11-20 06:00 | 399 | 388
2017-11-20 06:30 | 429 | 423
2017-11-20 07:00 | 460 | 457
2017-11-20 07:30 | 477 | 474
2017-11-20 08:00 | 467 | 465
2017-11-20 08:30 | 469 | 467
2017-11-20 09:00 | 470 | 467
2017-11-20 09:30 | 472 | 471
2017-11-20 10:00 | 478 | 476
2017-11-20 10:30 | 477 | 476
2017-11-20 11:00 | 469 | 469
2017-11-20 11:30 | 477 | 476
2017-11-20 12:00 | 480 | 480
2017-11-20 12:30 | 476 | 476
2017-11-20 13:00 | 479 | 479
2017-11-20 13:30 | 482 | 481
2017-11-20 14:00 | 488 | 487
2017-11-20 14:30 | 484 | 483
2017-11-20 15:00 | 489 | 489
2017-11-20 15:30 | 505 | 504
2017-11-20 16:00 | 518 | 517
2017-11-20 16:30 | 540 | 539
2017-11-20 17:00 | 568 | 561
2017-11-20 17:30 | 572 | 563
2017-11-20 18:00 | 568 | 557
2017-11-20 18:30 | 568 | 555
2017-11-20 19:00 | 580 | 570
2017-11-20 19:30 | 568 | 557
2017-11-20 20:00 | 560 | 550
2017-11-20 20:30 | 549 | 542
2017-11-20 21:00 | 519 | 516
2017-11-20 21:30 | 494 | 492
2017-11-20 22:00 | 474 | 472
2017-11-20 22:30 | 459 | 456
2017-11-20 23:00 | 441 | 439
2017-11-20 23:30 | 417 | 414
2017-11-21 | 391 | 388
2017-11-21 00:30 | 369 | 364
2017-11-21 01:00 | 364 | 355
2017-11-21 01:30 | 358 | 349
2017-11-21 02:00 | 352 | 341
2017-11-21 02:30 | 346 | 335
2017-11-21 03:00 | 348 | 336
2017-11-21 03:30 | 347 | 336
2017-11-21 04:00 | 349 | 337
2017-11-21 04:30 | 354 | 343
2017-11-21 05:00 | 358 | 348
2017-11-21 05:30 | 373 | 364
2017-11-21 06:00 | 393 | 386
2017-11-21 06:30 | 430 | 426
2017-11-21 07:00 | 459 | 455
2017-11-21 07:30 | 487 | 485
2017-11-21 08:00 | 486 | 485
2017-11-21 08:30 | 498 | 496
2017-11-21 09:00 | 500 | 499
2017-11-21 09:30 | 500 | 499
2017-11-21 10:00 | 486 | 484
2017-11-21 10:30 | 486 | 484
2017-11-21 11:00 | 480 | 479
2017-11-21 11:30 | 489 | 488
2017-11-21 12:00 | 506 | 506
2017-11-21 12:30 | 502 | 501
2017-11-21 13:00 | 496 | 495
2017-11-21 13:30 | 489 | 488
2017-11-21 14:00 | 507 | 506
2017-11-21 14:30 | 523 | 521
2017-11-21 15:00 | 522 | 521
2017-11-21 15:30 | 526 | 524
2017-11-21 16:00 | 540 | 538
2017-11-21 16:30 | 563 | 559
2017-11-21 17:00 | 570 | 565
2017-11-21 17:30 | 574 | 569
2017-11-21 18:00 | 571 | 565
2017-11-21 18:30 | 569 | 563
2017-11-21 19:00 | 584 | 580
2017-11-21 19:30 | 582 | 578
2017-11-21 20:00 | 575 | 570
2017-11-21 20:30 | 554 | 550
2017-11-21 21:00 | 516 | 514
2017-11-21 21:30 | 493 | 490
2017-11-21 22:00 | 476 | 472
2017-11-21 22:30 | 458 | 454
2017-11-21 23:00 | 425 | 421
2017-11-21 23:30 | 406 | 401
2017-11-22 | 389 | 382
2017-11-22 00:30 | 377 | 369
2017-11-22 01:00 | 372 | 363
2017-11-22 01:30 | 361 | 351
2017-11-22 02:00 | 350 | 338
2017-11-22 02:30 | 344 | 332
2017-11-22 03:00 | 345 | 332
2017-11-22 03:30 | 345 | 332
2017-11-22 04:00 | 346 | 334
2017-11-22 04:30 | 344 | 332
2017-11-22 05:00 | 360 | 347
2017-11-22 05:30 | 375 | 364
2017-11-22 06:00 | 392 | 384
2017-11-22 06:30 | 432 | 424
2017-11-22 07:00 | 459 | 454
2017-11-22 07:30 | 486 | 475
2017-11-22 08:00 | 499 | 490
2017-11-22 08:30 | 504 | 495
2017-11-22 09:00 | 503 | 495
2017-11-22 09:30 | 513 | 504
2017-11-22 10:00 | 510 | 499
2017-11-22 10:30 | 512 | 501
2017-11-22 11:00 | 514 | 504
2017-11-22 11:30 | 518 | 508
2017-11-22 12:00 | 516 | 507
2017-11-22 12:30 | 521 | 511
2017-11-22 13:00 | 504 | 493
2017-11-22 13:30 | 507 | 496
2017-11-22 14:00 | 527 | 518
2017-11-22 14:30 | 522 | 512
2017-11-22 15:00 | 516 | 507
2017-11-22 15:30 | 517 | 507
2017-11-22 16:00 | 541 | 531
2017-11-22 16:30 | 550 | 540
2017-11-22 17:00 | 559 | 549
2017-11-22 17:30 | 554 | 543
2017-11-22 18:00 | 553 | 541
2017-11-22 18:30 | 544 | 529
2017-11-22 19:00 | 559 | 546
2017-11-22 19:30 | 548 | 544
2017-11-22 20:00 | 547 | 542
2017-11-22 20:30 | 542 | 536
2017-11-22 21:00 | 519 | 513
2017-11-22 21:30 | 503 | 498
2017-11-22 22:00 | 487 | 481
2017-11-22 22:30 | 469 | 463
2017-11-22 23:00 | 441 | 437
2017-11-22 23:30 | 424 | 420
2017-11-23 | 405 | 399
2017-11-23 00:30 | 382 | 374
2017-11-23 01:00 | 374 | 364
2017-11-23 01:30 | 361 | 349
2017-11-23 02:00 | 356 | 343
2017-11-23 02:30 | 355 | 341
2017-11-23 03:00 | 355 | 341
2017-11-23 03:30 | 356 | 342
2017-11-23 04:00 | 356 | 342
2017-11-23 04:30 | 366 | 353
2017-11-23 05:00 | 369 | 356
2017-11-23 05:30 | 383 | 371
2017-11-23 06:00 | 397 | 387
2017-11-23 06:30 | 429 | 423
2017-11-23 07:00 | 454 | 452
2017-11-23 07:30 | 479 | 478
2017-11-23 08:00 | 484 | 483
2017-11-23 08:30 | 493 | 492
2017-11-23 09:00 | 494 | 493
2017-11-23 09:30 | 497 | 497
2017-11-23 10:00 | 495 | 494
2017-11-23 10:30 | 491 | 491
2017-11-23 11:00 | 498 | 498
2017-11-23 11:30 | 500 | 500
2017-11-23 12:00 | 502 | 501
2017-11-23 12:30 | 498 | 497
2017-11-23 13:00 | 496 | 495
2017-11-23 13:30 | 511 | 511
2017-11-23 14:00 | 512 | 512
2017-11-23 14:30 | 528 | 528
2017-11-23 15:00 | 545 | 544
2017-11-23 15:30 | 555 | 554
2017-11-23 16:00 | 567 | 565
2017-11-23 16:30 | 581 | 579
2017-11-23 17:00 | 598 | 596
2017-11-23 17:30 | 601 | 598
2017-11-23 18:00 | 590 | 586
2017-11-23 18:30 | 583 | 579
2017-11-23 19:00 | 600 | 596
2017-11-23 19:30 | 594 | 590
2017-11-23 20:00 | 583 | 579
2017-11-23 20:30 | 569 | 566
2017-11-23 21:00 | 539 | 537
2017-11-23 21:30 | 529 | 525
2017-11-23 22:00 | 518 | 513
2017-11-23 22:30 | 499 | 493
2017-11-23 23:00 | 471 | 467
2017-11-23 23:30 | 434 | 428
2017-11-24 | 414 | 407
2017-11-24 00:30 | 406 | 396
2017-11-24 01:00 | 401 | 389
2017-11-24 01:30 | 387 | 374
2017-11-24 02:00 | 379 | 366
2017-11-24 02:30 | 372 | 360
2017-11-24 03:00 | 371 | 360
2017-11-24 03:30 | 371 | 361
2017-11-24 04:00 | 372 | 361
2017-11-24 04:30 | 376 | 365
2017-11-24 05:00 | 382 | 371
2017-11-24 05:30 | 401 | 391
2017-11-24 06:00 | 411 | 404
2017-11-24 06:30 | 445 | 441
2017-11-24 07:00 | 476 | 474
2017-11-24 07:30 | 516 | 510
2017-11-24 08:00 | 528 | 520
2017-11-24 08:30 | 528 | 523
2017-11-24 09:00 | 530 | 527
2017-11-24 09:30 | 530 | 526
2017-11-24 10:00 | 530 | 528
2017-11-24 10:30 | 532 | 530
2017-11-24 11:00 | 536 | 535
2017-11-24 11:30 | 542 | 540
2017-11-24 12:00 | 538 | 536
2017-11-24 12:30 | 536 | 534
2017-11-24 13:00 | 537 | 536
2017-11-24 13:30 | 541 | 539
2017-11-24 14:00 | 552 | 550
2017-11-24 14:30 | 555 | 553
2017-11-24 15:00 | 566 | 564
2017-11-24 15:30 | 567 | 565
2017-11-24 16:00 | 583 | 581
2017-11-24 16:30 | 597 | 595
2017-11-24 17:00 | 605 | 601
2017-11-24 17:30 | 598 | 593
2017-11-24 18:00 | 589 | 583
2017-11-24 18:30 | 570 | 568
2017-11-24 19:00 | 580 | 579
2017-11-24 19:30 | 573 | 572
2017-11-24 20:00 | 568 | 566
2017-11-24 20:30 | 548 | 547
2017-11-24 21:00 | 526 | 525
2017-11-24 21:30 | 530 | 529
2017-11-24 22:00 | 522 | 522
2017-11-24 22:30 | 504 | 503
2017-11-24 23:00 | 497 | 496
2017-11-24 23:30 | 479 | 478
2017-11-25 | 441 | 440
2017-11-25 00:30 | 415 | 413
2017-11-25 01:00 | 397 | 395
2017-11-25 01:30 | 382 | 379
2017-11-25 02:00 | 365 | 362
2017-11-25 02:30 | 362 | 358
2017-11-25 03:00 | 363 | 359
2017-11-25 03:30 | 365 | 361
2017-11-25 04:00 | 361 | 356
2017-11-25 04:30 | 357 | 352
2017-11-25 05:00 | 357 | 352
2017-11-25 05:30 | 364 | 359
2017-11-25 06:00 | 377 | 372
2017-11-25 06:30 | 388 | 384
2017-11-25 07:00 | 394 | 391
2017-11-25 07:30 | 405 | 403
2017-11-25 08:00 | 421 | 419
2017-11-25 08:30 | 437 | 435
2017-11-25 09:00 | 450 | 449
2017-11-25 09:30 | 466 | 464
2017-11-25 10:00 | 463 | 462
2017-11-25 10:30 | 465 | 464
2017-11-25 11:00 | 458 | 457
2017-11-25 11:30 | 457 | 457
2017-11-25 12:00 | 456 | 455
2017-11-25 12:30 | 457 | 454
2017-11-25 13:00 | 451 | 448
2017-11-25 13:30 | 448 | 447
2017-11-25 14:00 | 459 | 458
2017-11-25 14:30 | 468 | 467
2017-11-25 15:00 | 486 | 485
2017-11-25 15:30 | 506 | 505
2017-11-25 16:00 | 522 | 521
2017-11-25 16:30 | 526 | 524
2017-11-25 17:00 | 539 | 537
2017-11-25 17:30 | 526 | 523
2017-11-25 18:00 | 528 | 525
2017-11-25 18:30 | 526 | 522
2017-11-25 19:00 | 536 | 533
2017-11-25 19:30 | 531 | 529
2017-11-25 20:00 | 533 | 530
2017-11-25 20:30 | 524 | 521
2017-11-25 21:00 | 498 | 497
2017-11-25 21:30 | 492 | 491
2017-11-25 22:00 | 489 | 488
2017-11-25 22:30 | 488 | 486
2017-11-25 23:00 | 467 | 465
2017-11-25 23:30 | 439 | 436
2017-11-26 | 421 | 417
2017-11-26 00:30 | 408 | 403
2017-11-26 01:00 | 394 | 388
2017-11-26 01:30 | 386 | 380
2017-11-26 02:00 | 373 | 366
2017-11-26 02:30 | 370 | 362
2017-11-26 03:00 | 367 | 359
2017-11-26 03:30 | 362 | 353
2017-11-26 04:00 | 365 | 355
2017-11-26 04:30 | 367 | 357
2017-11-26 05:00 | 366 | 354
2017-11-26 05:30 | 367 | 353
2017-11-26 06:00 | 372 | 356
2017-11-26 06:30 | 377 | 363
2017-11-26 07:00 | 384 | 371
2017-11-26 07:30 | 400 | 390
2017-11-26 08:00 | 416 | 408
2017-11-26 08:30 | 441 | 436
2017-11-26 09:00 | 446 | 442
2017-11-26 09:30 | 440 | 436
2017-11-26 10:00 | 435 | 431
2017-11-26 10:30 | 437 | 433
2017-11-26 11:00 | 437 | 433
2017-11-26 11:30 | 432 | 428
2017-11-26 12:00 | 433 | 429
2017-11-26 12:30 | 433 | 430
2017-11-26 13:00 | 444 | 441
2017-11-26 13:30 | 450 | 447
2017-11-26 14:00 | 461 | 458
2017-11-26 14:30 | 474 | 472
2017-11-26 15:00 | 479 | 476
2017-11-26 15:30 | 493 | 490
2017-11-26 16:00 | 517 | 514
2017-11-26 16:30 | 528 | 525
2017-11-26 17:00 | 542 | 539
2017-11-26 17:30 | 538 | 533
2017-11-26 18:00 | 543 | 529
2017-11-26 18:30 | 535 | 522
2017-11-26 19:00 | 543 | 532
2017-11-26 19:30 | 543 | 532
2017-11-26 20:00 | 536 | 528
2017-11-26 20:30 | 515 | 507
2017-11-26 21:00 | 502 | 491
2017-11-26 21:30 | 481 | 468
2017-11-26 22:00 | 476 | 461
2017-11-26 22:30 | 458 | 451
2017-11-26 23:00 | 437 | 431
2017-11-26 23:30 | 420 | 414
2017-11-27 | 405 | 399
2017-11-27 00:30 | 388 | 380
2017-11-27 01:00 | 381 | 371
2017-11-27 01:30 | 367 | 356
2017-11-27 02:00 | 362 | 351
2017-11-27 02:30 | 358 | 346
2017-11-27 03:00 | 364 | 353
2017-11-27 03:30 | 367 | 355
2017-11-27 04:00 | 371 | 359
2017-11-27 04:30 | 381 | 370
2017-11-27 05:00 | 383 | 372
2017-11-27 05:30 | 407 | 398
2017-11-27 06:00 | 439 | 433
2017-11-27 06:30 | 485 | 480
2017-11-27 07:00 | 519 | 516
2017-11-27 07:30 | 554 | 551
2017-11-27 08:00 | 574 | 571
2017-11-27 08:30 | 590 | 586
2017-11-27 09:00 | 588 | 585
2017-11-27 09:30 | 581 | 578
2017-11-27 10:00 | 580 | 578
2017-11-27 10:30 | 584 | 582
2017-11-27 11:00 | 578 | 576
2017-11-27 11:30 | 579 | 578
2017-11-27 12:00 | 578 | 577
2017-11-27 12:30 | 575 | 574
2017-11-27 13:00 | 572 | 571
2017-11-27 13:30 | 576 | 575
2017-11-27 14:00 | 585 | 584
2017-11-27 14:30 | 586 | 586
2017-11-27 15:00 | 594 | 594
2017-11-27 15:30 | 607 | 605
2017-11-27 16:00 | 615 | 613
2017-11-27 16:30 | 631 | 628
2017-11-27 17:00 | 643 | 640
2017-11-27 17:30 | 633 | 629
2017-11-27 18:00 | 621 | 616
2017-11-27 18:30 | 591 | 587
2017-11-27 19:00 | 607 | 605
2017-11-27 19:30 | 603 | 599
2017-11-27 20:00 | 597 | 594
2017-11-27 20:30 | 573 | 572
2017-11-27 21:00 | 546 | 545
2017-11-27 21:30 | 530 | 528
2017-11-27 22:00 | 512 | 509
2017-11-27 22:30 | 498 | 494
2017-11-27 23:00 | 464 | 460
2017-11-27 23:30 | 430 | 425
2017-11-28 | 402 | 399
2017-11-28 00:30 | 377 | 373
2017-11-28 01:00 | 369 | 363
2017-11-28 01:30 | 360 | 354
2017-11-28 02:00 | 355 | 348
2017-11-28 02:30 | 346 | 339
2017-11-28 03:00 | 343 | 335
2017-11-28 03:30 | 343 | 335
2017-11-28 04:00 | 337 | 330
2017-11-28 04:30 | 334 | 327
2017-11-28 05:00 | 339 | 332
2017-11-28 05:30 | 366 | 360
2017-11-28 06:00 | 386 | 382
2017-11-28 06:30 | 431 | 429
2017-11-28 07:00 | 469 | 468
2017-11-28 07:30 | 506 | 505
2017-11-28 08:00 | 525 | 524
2017-11-28 08:30 | 536 | 532
2017-11-28 09:00 | 539 | 536
2017-11-28 09:30 | 543 | 540
2017-11-28 10:00 | 544 | 541
2017-11-28 10:30 | 544 | 541
2017-11-28 11:00 | 551 | 547
2017-11-28 11:30 | 561 | 556
2017-11-28 12:00 | 573 | 568
2017-11-28 12:30 | 582 | 577
2017-11-28 13:00 | 589 | 585
2017-11-28 13:30 | 599 | 595
2017-11-28 14:00 | 609 | 606
2017-11-28 14:30 | 594 | 591
2017-11-28 15:00 | 579 | 576
2017-11-28 15:30 | 588 | 584
2017-11-28 16:00 | 600 | 597
2017-11-28 16:30 | 614 | 610
2017-11-28 17:00 | 611 | 606
2017-11-28 17:30 | 604 | 597
2017-11-28 18:00 | 600 | 588
2017-11-28 18:30 | 587 | 576
2017-11-28 19:00 | 599 | 591
2017-11-28 19:30 | 596 | 590
2017-11-28 20:00 | 596 | 590
2017-11-28 20:30 | 587 | 582
2017-11-28 21:00 | 566 | 561
2017-11-28 21:30 | 552 | 547
2017-11-28 22:00 | 519 | 518
2017-11-28 22:30 | 501 | 498
2017-11-28 23:00 | 478 | 475
2017-11-28 23:30 | 442 | 440
2017-11-29 | 409 | 406
2017-11-29 00:30 | 388 | 383
2017-11-29 01:00 | 374 | 368
2017-11-29 01:30 | 374 | 367
2017-11-29 02:00 | 371 | 364
2017-11-29 02:30 | 371 | 364
2017-11-29 03:00 | 371 | 363
2017-11-29 03:30 | 372 | 365
2017-11-29 04:00 | 380 | 372
2017-11-29 04:30 | 390 | 383
2017-11-29 05:00 | 392 | 385
2017-11-29 05:30 | 403 | 397
2017-11-29 06:00 | 429 | 425
2017-11-29 06:30 | 480 | 479
2017-11-29 07:00 | 523 | 521
2017-11-29 07:30 | 547 | 545
2017-11-29 08:00 | 566 | 564
2017-11-29 08:30 | 583 | 582
2017-11-29 09:00 | 594 | 593
2017-11-29 09:30 | 605 | 603
2017-11-29 10:00 | 605 | 603
2017-11-29 10:30 | 596 | 594
2017-11-29 11:00 | 580 | 579
2017-11-29 11:30 | 574 | 573
2017-11-29 12:00 | 571 | 570
2017-11-29 12:30 | 569 | 567
2017-11-29 13:00 | 566 | 564
2017-11-29 13:30 | 572 | 571
2017-11-29 14:00 | 573 | 572
2017-11-29 14:30 | 560 | 559
2017-11-29 15:00 | 558 | 557
2017-11-29 15:30 | 551 | 550
2017-11-29 16:00 | 545 | 544
2017-11-29 16:30 | 559 | 558
2017-11-29 17:00 | 569 | 568
2017-11-29 17:30 | 557 | 555
2017-11-29 18:00 | 563 | 561
2017-11-29 18:30 | 564 | 560
2017-11-29 19:00 | 573 | 571
2017-11-29 19:30 | 569 | 567
2017-11-29 20:00 | 562 | 561
2017-11-29 20:30 | 556 | 555
2017-11-29 21:00 | 528 | 527
2017-11-29 21:30 | 516 | 514
2017-11-29 22:00 | 509 | 506
2017-11-29 22:30 | 495 | 492
2017-11-29 23:00 | 471 | 468
2017-11-29 23:30 | 443 | 440
2017-11-30 | 410 | 406
2017-11-30 00:30 | 394 | 389
2017-11-30 01:00 | 385 | 378
2017-11-30 01:30 | 374 | 365
2017-11-30 02:00 | 366 | 357
2017-11-30 02:30 | 364 | 355
2017-11-30 03:00 | 368 | 359
2017-11-30 03:30 | 368 | 358
2017-11-30 04:00 | 343 | 334
2017-11-30 04:30 | 341 | 333
2017-11-30 05:00 | 351 | 343
2017-11-30 05:30 | 375 | 368
2017-11-30 06:00 | 396 | 392
2017-11-30 06:30 | 429 | 427
2017-11-30 07:00 | 472 | 471
2017-11-30 07:30 | 500 | 499
2017-11-30 08:00 | 521 | 521
2017-11-30 08:30 | 528 | 528
2017-11-30 09:00 | 519 | 519
2017-11-30 09:30 | 535 | 535
2017-11-30 10:00 | 545 | 545
2017-11-30 10:30 | 545 | 545
2017-11-30 11:00 | 535 | 535
2017-11-30 11:30 | 531 | 531
2017-11-30 12:00 | 532 | 532
2017-11-30 12:30 | 531 | 531
2017-11-30 13:00 | 546 | 546
2017-11-30 13:30 | 560 | 560
2017-11-30 14:00 | 586 | 586
2017-11-30 14:30 | 599 | 598
2017-11-30 15:00 | 599 | 598
2017-11-30 15:30 | 587 | 586
2017-11-30 16:00 | 590 | 589
2017-11-30 16:30 | 587 | 585
2017-11-30 17:00 | 588 | 586
2017-11-30 17:30 | 574 | 572
2017-11-30 18:00 | 569 | 567
2017-11-30 18:30 | 557 | 555
2017-11-30 19:00 | 568 | 567
2017-11-30 19:30 | 565 | 563
2017-11-30 20:00 | 563 | 562
2017-11-30 20:30 | 553 | 552
2017-11-30 21:00 | 534 | 533
2017-11-30 21:30 | 530 | 527
2017-11-30 22:00 | 524 | 521
2017-11-30 22:30 | 506 | 504
2017-11-30 23:00 | 481 | 478
2017-11-30 23:30 | 457 | 455
2017-12-01 | 434 | 432
2017-12-01 00:30 | 408 | 405
2017-12-01 01:00 | 395 | 391
2017-12-01 01:30 | 378 | 373
2017-12-01 02:00 | 376 | 371
2017-12-01 02:30 | 381 | 376
2017-12-01 03:00 | 376 | 371
2017-12-01 03:30 | 372 | 367
2017-12-01 04:00 | 375 | 370
2017-12-01 04:30 | 389 | 384
2017-12-01 05:00 | 390 | 385
2017-12-01 05:30 | 411 | 407
2017-12-01 06:00 | 434 | 431
2017-12-01 06:30 | 476 | 475
2017-12-01 07:00 | 507 | 507
2017-12-01 07:30 | 546 | 545
2017-12-01 08:00 | 552 | 552
2017-12-01 08:30 | 566 | 566
2017-12-01 09:00 | 571 | 568
2017-12-01 09:30 | 576 | 572
2017-12-01 10:00 | 577 | 571
2017-12-01 10:30 | 579 | 574
2017-12-01 11:00 | 585 | 581
2017-12-01 11:30 | 564 | 559
2017-12-01 12:00 | 551 | 547
2017-12-01 12:30 | 539 | 535
2017-12-01 13:00 | 540 | 537
2017-12-01 13:30 | 546 | 543
2017-12-01 14:00 | 551 | 548
2017-12-01 14:30 | 556 | 553
2017-12-01 15:00 | 568 | 564
2017-12-01 15:30 | 581 | 577
2017-12-01 16:00 | 605 | 601
2017-12-01 16:30 | 625 | 621
2017-12-01 17:00 | 630 | 625
2017-12-01 17:30 | 618 | 611
2017-12-01 18:00 | 607 | 597
2017-12-01 18:30 | 581 | 573
2017-12-01 19:00 | 590 | 583
2017-12-01 19:30 | 598 | 592
2017-12-01 20:00 | 597 | 590
2017-12-01 20:30 | 573 | 569
2017-12-01 21:00 | 542 | 542
2017-12-01 21:30 | 529 | 528
2017-12-01 22:00 | 518 | 517
2017-12-01 22:30 | 506 | 504
2017-12-01 23:00 | 491 | 489
2017-12-01 23:30 | 477 | 473
2017-12-02 | 446 | 443
2017-12-02 00:30 | 428 | 425
2017-12-02 01:00 | 414 | 411
2017-12-02 01:30 | 400 | 396
2017-12-02 02:00 | 378 | 373
2017-12-02 02:30 | 374 | 369
2017-12-02 03:00 | 366 | 358
2017-12-02 03:30 | 359 | 350
2017-12-02 04:00 | 362 | 353
2017-12-02 04:30 | 365 | 356
2017-12-02 05:00 | 366 | 355
2017-12-02 05:30 | 379 | 368
2017-12-02 06:00 | 393 | 383
2017-12-02 06:30 | 410 | 402
2017-12-02 07:00 | 425 | 419
2017-12-02 07:30 | 441 | 438
2017-12-02 08:00 | 458 | 454
2017-12-02 08:30 | 473 | 470
2017-12-02 09:00 | 491 | 489
2017-12-02 09:30 | 505 | 503
2017-12-02 10:00 | 505 | 504
2017-12-02 10:30 | 500 | 499
2017-12-02 11:00 | 474 | 473
2017-12-02 11:30 | 456 | 455
2017-12-02 12:00 | 452 | 451
2017-12-02 12:30 | 452 | 452
2017-12-02 13:00 | 465 | 464
2017-12-02 13:30 | 473 | 472
2017-12-02 14:00 | 478 | 477
2017-12-02 14:30 | 499 | 499
2017-12-02 15:00 | 514 | 513
2017-12-02 15:30 | 510 | 509
2017-12-02 16:00 | 515 | 514
2017-12-02 16:30 | 528 | 527
2017-12-02 17:00 | 538 | 537
2017-12-02 17:30 | 535 | 533
2017-12-02 18:00 | 533 | 531
2017-12-02 18:30 | 536 | 534
2017-12-02 19:00 | 548 | 546
2017-12-02 19:30 | 541 | 540
2017-12-02 20:00 | 541 | 539
2017-12-02 20:30 | 535 | 533
2017-12-02 21:00 | 515 | 513
2017-12-02 21:30 | 500 | 498
2017-12-02 22:00 | 489 | 487
2017-12-02 22:30 | 482 | 479
2017-12-02 23:00 | 463 | 460
2017-12-02 23:30 | 451 | 447
2017-12-03 | 429 | 423
2017-12-03 00:30 | 410 | 405
2017-12-03 01:00 | 405 | 399
2017-12-03 01:30 | 390 | 384
2017-12-03 02:00 | 379 | 371
2017-12-03 02:30 | 372 | 364
2017-12-03 03:00 | 368 | 359
2017-12-03 03:30 | 368 | 359
2017-12-03 04:00 | 362 | 353
2017-12-03 04:30 | 358 | 348
2017-12-03 05:00 | 354 | 344
2017-12-03 05:30 | 356 | 345
2017-12-03 06:00 | 366 | 353
2017-12-03 06:30 | 381 | 369
2017-12-03 07:00 | 388 | 377
2017-12-03 07:30 | 403 | 394
2017-12-03 08:00 | 415 | 408
2017-12-03 08:30 | 419 | 414
2017-12-03 09:00 | 421 | 418
2017-12-03 09:30 | 426 | 424
2017-12-03 10:00 | 436 | 434
2017-12-03 10:30 | 453 | 452
2017-12-03 11:00 | 456 | 455
2017-12-03 11:30 | 457 | 455
2017-12-03 12:00 | 462 | 461
2017-12-03 12:30 | 466 | 465
2017-12-03 13:00 | 476 | 475
2017-12-03 13:30 | 475 | 474
2017-12-03 14:00 | 494 | 493
2017-12-03 14:30 | 513 | 511
2017-12-03 15:00 | 524 | 523
2017-12-03 15:30 | 527 | 526
2017-12-03 16:00 | 544 | 542
2017-12-03 16:30 | 569 | 567
2017-12-03 17:00 | 586 | 582
2017-12-03 17:30 | 592 | 587
2017-12-03 18:00 | 598 | 593
2017-12-03 18:30 | 601 | 595
2017-12-03 19:00 | 604 | 599
2017-12-03 19:30 | 603 | 597
2017-12-03 20:00 | 604 | 598
2017-12-03 20:30 | 590 | 586
2017-12-03 21:00 | 560 | 557
2017-12-03 21:30 | 541 | 539
2017-12-03 22:00 | 523 | 521
2017-12-03 22:30 | 507 | 504
2017-12-03 23:00 | 479 | 475
2017-12-03 23:30 | 455 | 452
2017-12-04 | 437 | 432
2017-12-04 00:30 | 422 | 415
2017-12-04 01:00 | 412 | 405
2017-12-04 01:30 | 404 | 397
2017-12-04 02:00 | 400 | 392
2017-12-04 02:30 | 404 | 395
2017-12-04 03:00 | 404 | 395
2017-12-04 03:30 | 403 | 394
2017-12-04 04:00 | 405 | 397
2017-12-04 04:30 | 406 | 398
2017-12-04 05:00 | 403 | 395
2017-12-04 05:30 | 420 | 413
2017-12-04 06:00 | 442 | 437
2017-12-04 06:30 | 488 | 484
2017-12-04 07:00 | 524 | 522
2017-12-04 07:30 | 565 | 561
2017-12-04 08:00 | 600 | 592
2017-12-04 08:30 | 614 | 606
2017-12-04 09:00 | 622 | 616
2017-12-04 09:30 | 630 | 625
2017-12-04 10:00 | 634 | 628
2017-12-04 10:30 | 643 | 636
2017-12-04 11:00 | 656 | 650
2017-12-04 11:30 | 661 | 655
2017-12-04 12:00 | 667 | 660
2017-12-04 12:30 | 663 | 653
2017-12-04 13:00 | 657 | 646
2017-12-04 13:30 | 641 | 630
2017-12-04 14:00 | 630 | 621
2017-12-04 14:30 | 620 | 612
2017-12-04 15:00 | 611 | 602
2017-12-04 15:30 | 603 | 593
2017-12-04 16:00 | 606 | 596
2017-12-04 16:30 | 606 | 597
2017-12-04 17:00 | 616 | 607
2017-12-04 17:30 | 615 | 605
2017-12-04 18:00 | 600 | 594
2017-12-04 18:30 | 582 | 577
2017-12-04 19:00 | 589 | 585
2017-12-04 19:30 | 585 | 580
2017-12-04 20:00 | 578 | 573
2017-12-04 20:30 | 565 | 562
2017-12-04 21:00 | 544 | 542
2017-12-04 21:30 | 536 | 533
2017-12-04 22:00 | 517 | 514
2017-12-04 22:30 | 501 | 498
2017-12-04 23:00 | 482 | 478
2017-12-04 23:30 | 462 | 458
2017-12-05 | 440 | 435
2017-12-05 00:30 | 419 | 411
2017-12-05 01:00 | 415 | 407
2017-12-05 01:30 | 405 | 395
2017-12-05 02:00 | 389 | 379
2017-12-05 02:30 | 375 | 365
2017-12-05 03:00 | 375 | 365
2017-12-05 03:30 | 381 | 371
2017-12-05 04:00 | 388 | 378
2017-12-05 04:30 | 394 | 384
2017-12-05 05:00 | 403 | 394
2017-12-05 05:30 | 419 | 410
2017-12-05 06:00 | 442 | 436
2017-12-05 06:30 | 480 | 477
2017-12-05 07:00 | 504 | 502
2017-12-05 07:30 | 539 | 536
2017-12-05 08:00 | 552 | 549
2017-12-05 08:30 | 572 | 570
2017-12-05 09:00 | 585 | 580
2017-12-05 09:30 | 580 | 572
2017-12-05 10:00 | 564 | 556
2017-12-05 10:30 | 574 | 567
2017-12-05 11:00 | 588 | 583
2017-12-05 11:30 | 563 | 556
2017-12-05 12:00 | 567 | 561
2017-12-05 12:30 | 586 | 581
2017-12-05 13:00 | 583 | 579
2017-12-05 13:30 | 572 | 568
2017-12-05 14:00 | 581 | 576
2017-12-05 14:30 | 581 | 576
2017-12-05 15:00 | 598 | 593
2017-12-05 15:30 | 623 | 616
2017-12-05 16:00 | 647 | 641
2017-12-05 16:30 | 657 | 650
2017-12-05 17:00 | 658 | 650
2017-12-05 17:30 | 655 | 646
2017-12-05 18:00 | 645 | 633
2017-12-05 18:30 | 621 | 613
2017-12-05 19:00 | 632 | 628
2017-12-05 19:30 | 625 | 621
2017-12-05 20:00 | 625 | 620
2017-12-05 20:30 | 612 | 606
2017-12-05 21:00 | 581 | 579
2017-12-05 21:30 | 562 | 560
2017-12-05 22:00 | 544 | 541
2017-12-05 22:30 | 524 | 521
2017-12-05 23:00 | 489 | 486
2017-12-05 23:30 | 454 | 451
2017-12-06 | 427 | 423
2017-12-06 00:30 | 405 | 399
2017-12-06 01:00 | 399 | 391
2017-12-06 01:30 | 389 | 380
2017-12-06 02:00 | 389 | 379
2017-12-06 02:30 | 386 | 376
2017-12-06 03:00 | 387 | 377
2017-12-06 03:30 | 385 | 374
2017-12-06 04:00 | 381 | 369
2017-12-06 04:30 | 379 | 368
2017-12-06 05:00 | 383 | 371
2017-12-06 05:30 | 400 | 389
2017-12-06 06:00 | 416 | 409
2017-12-06 06:30 | 457 | 452
2017-12-06 07:00 | 494 | 492
2017-12-06 07:30 | 524 | 521
2017-12-06 08:00 | 524 | 523
2017-12-06 08:30 | 531 | 529
2017-12-06 09:00 | 534 | 530
2017-12-06 09:30 | 538 | 534
2017-12-06 10:00 | 551 | 549
2017-12-06 10:30 | 532 | 529
2017-12-06 11:00 | 519 | 516
2017-12-06 11:30 | 515 | 513
2017-12-06 12:00 | 513 | 512
2017-12-06 12:30 | 507 | 506
2017-12-06 13:00 | 509 | 507
2017-12-06 13:30 | 521 | 519
2017-12-06 14:00 | 527 | 526
2017-12-06 14:30 | 541 | 540
2017-12-06 15:00 | 555 | 555
2017-12-06 15:30 | 572 | 570
2017-12-06 16:00 | 594 | 591
2017-12-06 16:30 | 618 | 611
2017-12-06 17:00 | 629 | 622
2017-12-06 17:30 | 628 | 620
2017-12-06 18:00 | 621 | 609
2017-12-06 18:30 | 609 | 592
2017-12-06 19:00 | 605 | 595
2017-12-06 19:30 | 604 | 595
2017-12-06 20:00 | 603 | 593
2017-12-06 20:30 | 588 | 578
2017-12-06 21:00 | 555 | 549
2017-12-06 21:30 | 538 | 535
2017-12-06 22:00 | 518 | 513
2017-12-06 22:30 | 494 | 489
2017-12-06 23:00 | 457 | 454
2017-12-06 23:30 | 432 | 428
2017-12-07 | 406 | 402
2017-12-07 00:30 | 396 | 390
2017-12-07 01:00 | 392 | 384
2017-12-07 01:30 | 373 | 363
2017-12-07 02:00 | 367 | 357
2017-12-07 02:30 | 378 | 368
2017-12-07 03:00 | 381 | 371
2017-12-07 03:30 | 381 | 371
2017-12-07 04:00 | 382 | 371
2017-12-07 04:30 | 385 | 375
2017-12-07 05:00 | 390 | 379
2017-12-07 05:30 | 394 | 384
2017-12-07 06:00 | 411 | 404
2017-12-07 06:30 | 447 | 443
2017-12-07 07:00 | 478 | 476
2017-12-07 07:30 | 506 | 502
2017-12-07 08:00 | 522 | 513
2017-12-07 08:30 | 517 | 507
2017-12-07 09:00 | 523 | 514
2017-12-07 09:30 | 537 | 528
2017-12-07 10:00 | 548 | 539
2017-12-07 10:30 | 550 | 543
2017-12-07 11:00 | 556 | 549
2017-12-07 11:30 | 570 | 561
2017-12-07 12:00 | 573 | 565
2017-12-07 12:30 | 578 | 570
2017-12-07 13:00 | 587 | 580
2017-12-07 13:30 | 599 | 593
2017-12-07 14:00 | 620 | 613
2017-12-07 14:30 | 632 | 624
2017-12-07 15:00 | 642 | 633
2017-12-07 15:30 | 657 | 648
2017-12-07 16:00 | 673 | 663
2017-12-07 16:30 | 692 | 678
2017-12-07 17:00 | 701 | 686
2017-12-07 17:30 | 701 | 688
2017-12-07 18:00 | 694 | 677
2017-12-07 18:30 | 672 | 656
2017-12-07 19:00 | 671 | 657
2017-12-07 19:30 | 665 | 651
2017-12-07 20:00 | 658 | 646
2017-12-07 20:30 | 640 | 631
2017-12-07 21:00 | 607 | 599
2017-12-07 21:30 | 589 | 578
2017-12-07 22:00 | 571 | 557
2017-12-07 22:30 | 547 | 531
2017-12-07 23:00 | 515 | 500
2017-12-07 23:30 | 503 | 486
2017-12-08 | 466 | 454
2017-12-08 00:30 | 432 | 424
2017-12-08 01:00 | 419 | 409
2017-12-08 01:30 | 408 | 397
2017-12-08 02:00 | 395 | 383
2017-12-08 02:30 | 383 | 370
2017-12-08 03:00 | 394 | 381
2017-12-08 03:30 | 396 | 384
2017-12-08 04:00 | 393 | 380
2017-12-08 04:30 | 390 | 378
2017-12-08 05:00 | 395 | 382
2017-12-08 05:30 | 414 | 403
2017-12-08 06:00 | 432 | 423
2017-12-08 06:30 | 480 | 476
2017-12-08 07:00 | 523 | 518
2017-12-08 07:30 | 559 | 550
2017-12-08 08:00 | 573 | 567
2017-12-08 08:30 | 589 | 584
2017-12-08 09:00 | 595 | 591
2017-12-08 09:30 | 603 | 599
2017-12-08 10:00 | 612 | 608
2017-12-08 10:30 | 630 | 625
2017-12-08 11:00 | 653 | 648
2017-12-08 11:30 | 679 | 674
2017-12-08 12:00 | 715 | 707
2017-12-08 12:30 | 732 | 720
2017-12-08 13:00 | 704 | 687
2017-12-08 13:30 | 653 | 635
2017-12-08 14:00 | 622 | 610
2017-12-08 14:30 | 608 | 599
2017-12-08 15:00 | 600 | 590
2017-12-08 15:30 | 590 | 580
2017-12-08 16:00 | 605 | 596
2017-12-08 16:30 | 606 | 596
2017-12-08 17:00 | 611 | 602
2017-12-08 17:30 | 608 | 598
2017-12-08 18:00 | 601 | 590
2017-12-08 18:30 | 591 | 580
2017-12-08 19:00 | 595 | 587
2017-12-08 19:30 | 592 | 584
2017-12-08 20:00 | 595 | 586
2017-12-08 20:30 | 580 | 572
2017-12-08 21:00 | 550 | 543
2017-12-08 21:30 | 541 | 533
2017-12-08 22:00 | 524 | 515
2017-12-08 22:30 | 509 | 500
2017-12-08 23:00 | 486 | 476
2017-12-08 23:30 | 460 | 450
2017-12-09 | 430 | 418
2017-12-09 00:30 | 405 | 393
2017-12-09 01:00 | 396 | 382
2017-12-09 01:30 | 379 | 364
2017-12-09 02:00 | 370 | 353
2017-12-09 02:30 | 365 | 347
2017-12-09 03:00 | 363 | 345
2017-12-09 03:30 | 370 | 351
2017-12-09 04:00 | 375 | 356
2017-12-09 04:30 | 376 | 358
2017-12-09 05:00 | 377 | 357
2017-12-09 05:30 | 378 | 357
2017-12-09 06:00 | 383 | 364
2017-12-09 06:30 | 400 | 384
2017-12-09 07:00 | 408 | 394
2017-12-09 07:30 | 418 | 407
2017-12-09 08:00 | 424 | 416
2017-12-09 08:30 | 435 | 429
2017-12-09 09:00 | 460 | 455
2017-12-09 09:30 | 510 | 504
2017-12-09 10:00 | 506 | 502
2017-12-09 10:30 | 501 | 496
2017-12-09 11:00 | 500 | 497
2017-12-09 11:30 | 487 | 482
2017-12-09 12:00 | 448 | 443
2017-12-09 12:30 | 450 | 446
2017-12-09 13:00 | 454 | 450
2017-12-09 13:30 | 464 | 460
2017-12-09 14:00 | 475 | 471
2017-12-09 14:30 | 488 | 484
2017-12-09 15:00 | 508 | 503
2017-12-09 15:30 | 521 | 516
2017-12-09 16:00 | 544 | 539
2017-12-09 16:30 | 555 | 549
2017-12-09 17:00 | 554 | 547
2017-12-09 17:30 | 547 | 538
2017-12-09 18:00 | 529 | 520
2017-12-09 18:30 | 518 | 509
2017-12-09 19:00 | 516 | 507
2017-12-09 19:30 | 514 | 506
2017-12-09 20:00 | 511 | 504
2017-12-09 20:30 | 501 | 495
2017-12-09 21:00 | 485 | 479
2017-12-09 21:30 | 461 | 455
2017-12-09 22:00 | 459 | 452
2017-12-09 22:30 | 451 | 444
2017-12-09 23:00 | 434 | 426
2017-12-09 23:30 | 413 | 403
2017-12-10 | 402 | 389
2017-12-10 00:30 | 385 | 376
2017-12-10 01:00 | 373 | 366
2017-12-10 01:30 | 360 | 352
2017-12-10 02:00 | 353 | 344
2017-12-10 02:30 | 351 | 342
2017-12-10 03:00 | 345 | 335
2017-12-10 03:30 | 343 | 333
2017-12-10 04:00 | 344 | 334
2017-12-10 04:30 | 342 | 332
2017-12-10 05:00 | 332 | 321
2017-12-10 05:30 | 340 | 328
2017-12-10 06:00 | 349 | 337
2017-12-10 06:30 | 353 | 343
2017-12-10 07:00 | 358 | 349
2017-12-10 07:30 | 363 | 356
2017-12-10 08:00 | 370 | 365
2017-12-10 08:30 | 378 | 374
2017-12-10 09:00 | 384 | 381
2017-12-10 09:30 | 388 | 386
2017-12-10 10:00 | 387 | 386
2017-12-10 10:30 | 395 | 393
2017-12-10 11:00 | 402 | 401
2017-12-10 11:30 | 400 | 399
2017-12-10 12:00 | 401 | 400
2017-12-10 12:30 | 401 | 400
2017-12-10 13:00 | 407 | 406
2017-12-10 13:30 | 413 | 413
2017-12-10 14:00 | 423 | 422
2017-12-10 14:30 | 430 | 430
2017-12-10 15:00 | 443 | 443
2017-12-10 15:30 | 458 | 458
2017-12-10 16:00 | 460 | 459
2017-12-10 16:30 | 464 | 463
2017-12-10 17:00 | 476 | 476
2017-12-10 17:30 | 485 | 484
2017-12-10 18:00 | 485 | 484
2017-12-10 18:30 | 488 | 486
2017-12-10 19:00 | 499 | 498
2017-12-10 19:30 | 504 | 503
2017-12-10 20:00 | 503 | 502
2017-12-10 20:30 | 492 | 491
2017-12-10 21:00 | 463 | 463
2017-12-10 21:30 | 450 | 450
2017-12-10 22:00 | 442 | 442
2017-12-10 22:30 | 442 | 442
2017-12-10 23:00 | 432 | 431
2017-12-10 23:30 | 411 | 410
2017-12-11 | 392 | 390
2017-12-11 00:30 | 375 | 371
2017-12-11 01:00 | 367 | 362
2017-12-11 01:30 | 355 | 350
2017-12-11 02:00 | 345 | 341
2017-12-11 02:30 | 331 | 326
2017-12-11 03:00 | 332 | 327
2017-12-11 03:30 | 335 | 330
2017-12-11 04:00 | 333 | 328
2017-12-11 04:30 | 341 | 336
2017-12-11 05:00 | 349 | 344
2017-12-11 05:30 | 369 | 366
2017-12-11 06:00 | 383 | 381
2017-12-11 06:30 | 422 | 421
2017-12-11 07:00 | 461 | 453
2017-12-11 07:30 | 494 | 488
2017-12-11 08:00 | 511 | 505
2017-12-11 08:30 | 517 | 512
2017-12-11 09:00 | 525 | 520
2017-12-11 09:30 | 536 | 532
2017-12-11 10:00 | 538 | 532
2017-12-11 10:30 | 548 | 542
2017-12-11 11:00 | 552 | 546
2017-12-11 11:30 | 552 | 545
2017-12-11 12:00 | 556 | 550
2017-12-11 12:30 | 560 | 555
2017-12-11 13:00 | 556 | 551
2017-12-11 13:30 | 549 | 544
2017-12-11 14:00 | 546 | 541
2017-12-11 14:30 | 552 | 547
2017-12-11 15:00 | 562 | 557
2017-12-11 15:30 | 559 | 554
2017-12-11 16:00 | 558 | 554
2017-12-11 16:30 | 568 | 563
2017-12-11 17:00 | 575 | 569
2017-12-11 17:30 | 573 | 566
2017-12-11 18:00 | 563 | 555
2017-12-11 18:30 | 551 | 540
2017-12-11 19:00 | 545 | 542
2017-12-11 19:30 | 542 | 539
2017-12-11 20:00 | 540 | 536
2017-12-11 20:30 | 538 | 533
2017-12-11 21:00 | 513 | 510
2017-12-11 21:30 | 499 | 496
2017-12-11 22:00 | 479 | 477
2017-12-11 22:30 | 471 | 468
2017-12-11 23:00 | 449 | 447
2017-12-11 23:30 | 432 | 430
2017-12-12 | 405 | 403
2017-12-12 00:30 | 380 | 379
2017-12-12 01:00 | 368 | 366
2017-12-12 01:30 | 357 | 354
2017-12-12 02:00 | 346 | 342
2017-12-12 02:30 | 348 | 343
2017-12-12 03:00 | 353 | 348
2017-12-12 03:30 | 352 | 347
2017-12-12 04:00 | 358 | 354
2017-12-12 04:30 | 363 | 358
2017-12-12 05:00 | 369 | 364
2017-12-12 05:30 | 383 | 379
2017-12-12 06:00 | 399 | 396
2017-12-12 06:30 | 430 | 429
2017-12-12 07:00 | 452 | 451
2017-12-12 07:30 | 490 | 488
2017-12-12 08:00 | 508 | 507
2017-12-12 08:30 | 516 | 516
2017-12-12 09:00 | 516 | 516
2017-12-12 09:30 | 523 | 523
2017-12-12 10:00 | 534 | 534
2017-12-12 10:30 | 524 | 524
2017-12-12 11:00 | 515 | 515
2017-12-12 11:30 | 516 | 516
2017-12-12 12:00 | 522 | 522
2017-12-12 12:30 | 519 | 518
2017-12-12 13:00 | 534 | 532
2017-12-12 13:30 | 542 | 541
2017-12-12 14:00 | 551 | 550
2017-12-12 14:30 | 559 | 558
2017-12-12 15:00 | 565 | 564
2017-12-12 15:30 | 566 | 565
2017-12-12 16:00 | 575 | 574
2017-12-12 16:30 | 586 | 585
2017-12-12 17:00 | 602 | 601
2017-12-12 17:30 | 599 | 597
2017-12-12 18:00 | 589 | 586
2017-12-12 18:30 | 570 | 569
2017-12-12 19:00 | 582 | 581
2017-12-12 19:30 | 579 | 578
2017-12-12 20:00 | 577 | 577
2017-12-12 20:30 | 580 | 580
2017-12-12 21:00 | 560 | 559
2017-12-12 21:30 | 536 | 535
2017-12-12 22:00 | 512 | 511
2017-12-12 22:30 | 482 | 481
2017-12-12 23:00 | 454 | 453
2017-12-12 23:30 | 429 | 428
2017-12-13 | 405 | 404
2017-12-13 00:30 | 390 | 389
2017-12-13 01:00 | 377 | 375
2017-12-13 01:30 | 363 | 361
2017-12-13 02:00 | 357 | 355
2017-12-13 02:30 | 363 | 360
2017-12-13 03:00 | 361 | 359
2017-12-13 03:30 | 363 | 360
2017-12-13 04:00 | 365 | 362
2017-12-13 04:30 | 366 | 364
2017-12-13 05:00 | 385 | 382
2017-12-13 05:30 | 409 | 406
2017-12-13 06:00 | 428 | 425
2017-12-13 06:30 | 455 | 454
2017-12-13 07:00 | 494 | 494
2017-12-13 07:30 | 523 | 523
2017-12-13 08:00 | 543 | 540
2017-12-13 08:30 | 556 | 553
2017-12-13 09:00 | 570 | 565
2017-12-13 09:30 | 579 | 574
2017-12-13 10:00 | 579 | 575
2017-12-13 10:30 | 583 | 578
2017-12-13 11:00 | 588 | 583
2017-12-13 11:30 | 586 | 583
2017-12-13 12:00 | 581 | 578
2017-12-13 12:30 | 580 | 576
2017-12-13 13:00 | 589 | 583
2017-12-13 13:30 | 596 | 591
2017-12-13 14:00 | 596 | 592
2017-12-13 14:30 | 614 | 610
2017-12-13 15:00 | 627 | 623
2017-12-13 15:30 | 625 | 621
2017-12-13 16:00 | 633 | 629
2017-12-13 16:30 | 634 | 630
2017-12-13 17:00 | 641 | 636
2017-12-13 17:30 | 631 | 626
2017-12-13 18:00 | 617 | 609
2017-12-13 18:30 | 594 | 585
2017-12-13 19:00 | 595 | 589
2017-12-13 19:30 | 593 | 588
2017-12-13 20:00 | 607 | 602
2017-12-13 20:30 | 604 | 600
2017-12-13 21:00 | 574 | 573
2017-12-13 21:30 | 550 | 550
2017-12-13 22:00 | 529 | 528
2017-12-13 22:30 | 503 | 502
2017-12-13 23:00 | 484 | 484
2017-12-13 23:30 | 452 | 451
2017-12-14 | 414 | 413
2017-12-14 00:30 | 392 | 390
2017-12-14 01:00 | 382 | 381
2017-12-14 01:30 | 373 | 371
2017-12-14 02:00 | 366 | 364
2017-12-14 02:30 | 348 | 345
2017-12-14 03:00 | 353 | 351
2017-12-14 03:30 | 357 | 355
2017-12-14 04:00 | 356 | 353
2017-12-14 04:30 | 364 | 362
2017-12-14 05:00 | 366 | 364
2017-12-14 05:30 | 382 | 380
2017-12-14 06:00 | 400 | 398
2017-12-14 06:30 | 433 | 432
2017-12-14 07:00 | 469 | 468
2017-12-14 07:30 | 498 | 497
2017-12-14 08:00 | 516 | 515
2017-12-14 08:30 | 536 | 535
2017-12-14 09:00 | 555 | 555
2017-12-14 09:30 | 568 | 567
2017-12-14 10:00 | 570 | 569
2017-12-14 10:30 | 572 | 571
2017-12-14 11:00 | 573 | 572
2017-12-14 11:30 | 555 | 555
2017-12-14 12:00 | 553 | 553
2017-12-14 12:30 | 552 | 552
2017-12-14 13:00 | 554 | 553
2017-12-14 13:30 | 567 | 566
2017-12-14 14:00 | 575 | 575
2017-12-14 14:30 | 583 | 582
2017-12-14 15:00 | 586 | 586
2017-12-14 15:30 | 613 | 612
2017-12-14 16:00 | 654 | 651
2017-12-14 16:30 | 663 | 662
2017-12-14 17:00 | 670 | 668
2017-12-14 17:30 | 669 | 666
2017-12-14 18:00 | 658 | 654
2017-12-14 18:30 | 643 | 638
2017-12-14 19:00 | 642 | 637
2017-12-14 19:30 | 643 | 640
2017-12-14 20:00 | 642 | 636
2017-12-14 20:30 | 624 | 619
2017-12-14 21:00 | 598 | 595
2017-12-14 21:30 | 572 | 568
2017-12-14 22:00 | 549 | 543
2017-12-14 22:30 | 528 | 526
2017-12-14 23:00 | 499 | 498
2017-12-14 23:30 | 460 | 459
2017-12-15 | 433 | 431
2017-12-15 00:30 | 411 | 407
2017-12-15 01:00 | 401 | 396
2017-12-15 01:30 | 387 | 385
2017-12-15 02:00 | 381 | 379
2017-12-15 02:30 | 382 | 379
2017-12-15 03:00 | 380 | 377
2017-12-15 03:30 | 383 | 380
2017-12-15 04:00 | 384 | 381
2017-12-15 04:30 | 384 | 381
2017-12-15 05:00 | 383 | 381
2017-12-15 05:30 | 401 | 398
2017-12-15 06:00 | 424 | 423
2017-12-15 06:30 | 464 | 458
2017-12-15 07:00 | 494 | 489
2017-12-15 07:30 | 539 | 534
2017-12-15 08:00 | 564 | 557
2017-12-15 08:30 | 581 | 575
2017-12-15 09:00 | 583 | 578
2017-12-15 09:30 | 583 | 578
2017-12-15 10:00 | 586 | 582
2017-12-15 10:30 | 593 | 590
2017-12-15 11:00 | 597 | 593
2017-12-15 11:30 | 599 | 596
2017-12-15 12:00 | 606 | 603
2017-12-15 12:30 | 598 | 594
2017-12-15 13:00 | 599 | 595
2017-12-15 13:30 | 604 | 601
2017-12-15 14:00 | 610 | 606
2017-12-15 14:30 | 625 | 622
2017-12-15 15:00 | 642 | 637
2017-12-15 15:30 | 646 | 642
2017-12-15 16:00 | 653 | 648
2017-12-15 16:30 | 671 | 668
2017-12-15 17:00 | 681 | 678
2017-12-15 17:30 | 669 | 664
2017-12-15 18:00 | 651 | 644
2017-12-15 18:30 | 627 | 619
2017-12-15 19:00 | 618 | 613
2017-12-15 19:30 | 621 | 616
2017-12-15 20:00 | 617 | 611
2017-12-15 20:30 | 606 | 601
2017-12-15 21:00 | 582 | 578
2017-12-15 21:30 | 568 | 564
2017-12-15 22:00 | 547 | 543
2017-12-15 22:30 | 528 | 525
2017-12-15 23:00 | 491 | 489
2017-12-15 23:30 | 469 | 468
2017-12-16 | 444 | 443
2017-12-16 00:30 | 422 | 421
2017-12-16 01:00 | 416 | 415
2017-12-16 01:30 | 402 | 400
2017-12-16 02:00 | 398 | 396
2017-12-16 02:30 | 390 | 388
2017-12-16 03:00 | 388 | 386
2017-12-16 03:30 | 386 | 384
2017-12-16 04:00 | 382 | 380
2017-12-16 04:30 | 383 | 381
2017-12-16 05:00 | 372 | 368
2017-12-16 05:30 | 378 | 374
2017-12-16 06:00 | 389 | 386
2017-12-16 06:30 | 409 | 407
2017-12-16 07:00 | 428 | 426
2017-12-16 07:30 | 452 | 451
2017-12-16 08:00 | 457 | 456
2017-12-16 08:30 | 473 | 473
2017-12-16 09:00 | 488 | 488
2017-12-16 09:30 | 506 | 504
2017-12-16 10:00 | 517 | 515
2017-12-16 10:30 | 525 | 522
2017-12-16 11:00 | 532 | 529
2017-12-16 11:30 | 534 | 531
2017-12-16 12:00 | 546 | 544
2017-12-16 12:30 | 548 | 545
2017-12-16 13:00 | 544 | 542
2017-12-16 13:30 | 558 | 556
2017-12-16 14:00 | 560 | 558
2017-12-16 14:30 | 570 | 567
2017-12-16 15:00 | 576 | 574
2017-12-16 15:30 | 586 | 584
2017-12-16 16:00 | 595 | 593
2017-12-16 16:30 | 607 | 605
2017-12-16 17:00 | 620 | 618
2017-12-16 17:30 | 607 | 605
2017-12-16 18:00 | 587 | 584
2017-12-16 18:30 | 572 | 568
2017-12-16 19:00 | 574 | 571
2017-12-16 19:30 | 574 | 571
2017-12-16 20:00 | 571 | 568
2017-12-16 20:30 | 553 | 551
2017-12-16 21:00 | 527 | 526
2017-12-16 21:30 | 513 | 511
2017-12-16 22:00 | 486 | 484
2017-12-16 22:30 | 461 | 460
2017-12-16 23:00 | 444 | 443
2017-12-16 23:30 | 432 | 430
2017-12-17 | 411 | 407
2017-12-17 00:30 | 393 | 389
2017-12-17 01:00 | 389 | 384
2017-12-17 01:30 | 375 | 370
2017-12-17 02:00 | 364 | 359
2017-12-17 02:30 | 355 | 351
2017-12-17 03:00 | 353 | 348
2017-12-17 03:30 | 348 | 343
2017-12-17 04:00 | 347 | 342
2017-12-17 04:30 | 349 | 344
2017-12-17 05:00 | 346 | 339
2017-12-17 05:30 | 350 | 343
2017-12-17 06:00 | 358 | 352
2017-12-17 06:30 | 366 | 361
2017-12-17 07:00 | 378 | 374
2017-12-17 07:30 | 394 | 391
2017-12-17 08:00 | 402 | 400
2017-12-17 08:30 | 417 | 416
2017-12-17 09:00 | 437 | 436
2017-12-17 09:30 | 449 | 448
2017-12-17 10:00 | 452 | 452
2017-12-17 10:30 | 463 | 463
2017-12-17 11:00 | 469 | 469
2017-12-17 11:30 | 478 | 478
2017-12-17 12:00 | 490 | 489
2017-12-17 12:30 | 491 | 490
2017-12-17 13:00 | 494 | 494
2017-12-17 13:30 | 501 | 500
2017-12-17 14:00 | 517 | 516
2017-12-17 14:30 | 532 | 531
2017-12-17 15:00 | 542 | 541
2017-12-17 15:30 | 549 | 548
2017-12-17 16:00 | 564 | 563
2017-12-17 16:30 | 572 | 571
2017-12-17 17:00 | 573 | 572
2017-12-17 17:30 | 567 | 565
2017-12-17 18:00 | 552 | 550
2017-12-17 18:30 | 547 | 545
2017-12-17 19:00 | 551 | 550
2017-12-17 19:30 | 552 | 551
2017-12-17 20:00 | 550 | 549
2017-12-17 20:30 | 545 | 544
2017-12-17 21:00 | 529 | 526
2017-12-17 21:30 | 516 | 514
2017-12-17 22:00 | 499 | 497
2017-12-17 22:30 | 480 | 478
2017-12-17 23:00 | 470 | 467
2017-12-17 23:30 | 452 | 450
2017-12-18 | 422 | 421
2017-12-18 00:30 | 396 | 395
2017-12-18 01:00 | 383 | 381
2017-12-18 01:30 | 375 | 372
2017-12-18 02:00 | 368 | 365
2017-12-18 02:30 | 366 | 363
2017-12-18 03:00 | 367 | 364
2017-12-18 03:30 | 366 | 363
2017-12-18 04:00 | 360 | 357
2017-12-18 04:30 | 367 | 364
2017-12-18 05:00 | 375 | 372
2017-12-18 05:30 | 396 | 393
2017-12-18 06:00 | 408 | 407
2017-12-18 06:30 | 445 | 445
2017-12-18 07:00 | 484 | 483
2017-12-18 07:30 | 530 | 529
2017-12-18 08:00 | 569 | 563
2017-12-18 08:30 | 589 | 585
2017-12-18 09:00 | 597 | 592
2017-12-18 09:30 | 601 | 596
2017-12-18 10:00 | 602 | 597
2017-12-18 10:30 | 602 | 596
2017-12-18 11:00 | 610 | 605
2017-12-18 11:30 | 611 | 607
2017-12-18 12:00 | 615 | 611
2017-12-18 12:30 | 619 | 615
2017-12-18 13:00 | 618 | 614
2017-12-18 13:30 | 618 | 615
2017-12-18 14:00 | 628 | 624
2017-12-18 14:30 | 637 | 634
2017-12-18 15:00 | 644 | 640
2017-12-18 15:30 | 657 | 653
2017-12-18 16:00 | 662 | 658
2017-12-18 16:30 | 683 | 679
2017-12-18 17:00 | 693 | 689
2017-12-18 17:30 | 687 | 682
2017-12-18 18:00 | 692 | 684
2017-12-18 18:30 | 657 | 649
2017-12-18 19:00 | 650 | 647
2017-12-18 19:30 | 643 | 640
2017-12-18 20:00 | 641 | 638
2017-12-18 20:30 | 634 | 631
2017-12-18 21:00 | 599 | 599
2017-12-18 21:30 | 576 | 576
2017-12-18 22:00 | 556 | 556
2017-12-18 22:30 | 530 | 529
2017-12-18 23:00 | 485 | 484
2017-12-18 23:30 | 470 | 469
2017-12-19 | 442 | 441
2017-12-19 00:30 | 418 | 416
2017-12-19 01:00 | 408 | 406
2017-12-19 01:30 | 400 | 398
2017-12-19 02:00 | 390 | 389
2017-12-19 02:30 | 373 | 371
2017-12-19 03:00 | 371 | 369
2017-12-19 03:30 | 372 | 370
2017-12-19 04:00 | 371 | 369
2017-12-19 04:30 | 381 | 379
2017-12-19 05:00 | 392 | 389
2017-12-19 05:30 | 417 | 415
2017-12-19 06:00 | 432 | 430
2017-12-19 06:30 | 472 | 471
2017-12-19 07:00 | 501 | 500
2017-12-19 07:30 | 544 | 542
2017-12-19 08:00 | 574 | 568
2017-12-19 08:30 | 586 | 581
2017-12-19 09:00 | 593 | 588
2017-12-19 09:30 | 597 | 593
2017-12-19 10:00 | 598 | 594
2017-12-19 10:30 | 604 | 602
2017-12-19 11:00 | 615 | 611
2017-12-19 11:30 | 625 | 621
2017-12-19 12:00 | 642 | 638
2017-12-19 12:30 | 649 | 645
2017-12-19 13:00 | 651 | 648
2017-12-19 13:30 | 668 | 664
2017-12-19 14:00 | 690 | 687
2017-12-19 14:30 | 704 | 701
2017-12-19 15:00 | 724 | 722
2017-12-19 15:30 | 758 | 755
2017-12-19 16:00 | 752 | 749
2017-12-19 16:30 | 738 | 734
2017-12-19 17:00 | 735 | 730
2017-12-19 17:30 | 728 | 723
2017-12-19 18:00 | 708 | 700
2017-12-19 18:30 | 687 | 678
2017-12-19 19:00 | 690 | 685
2017-12-19 19:30 | 687 | 683
2017-12-19 20:00 | 681 | 676
2017-12-19 20:30 | 663 | 659
2017-12-19 21:00 | 629 | 627
2017-12-19 21:30 | 604 | 601
2017-12-19 22:00 | 590 | 587
2017-12-19 22:30 | 552 | 550
2017-12-19 23:00 | 521 | 520
2017-12-19 23:30 | 486 | 485
2017-12-20 | 456 | 456
2017-12-20 00:30 | 432 | 432
2017-12-20 01:00 | 422 | 421
2017-12-20 01:30 | 411 | 411
2017-12-20 02:00 | 403 | 403
2017-12-20 02:30 | 399 | 398
2017-12-20 03:00 | 401 | 400
2017-12-20 03:30 | 399 | 399
2017-12-20 04:00 | 402 | 402
2017-12-20 04:30 | 404 | 404
2017-12-20 05:00 | 405 | 405
2017-12-20 05:30 | 420 | 419
2017-12-20 06:00 | 439 | 439
2017-12-20 06:30 | 480 | 479
2017-12-20 07:00 | 524 | 524
2017-12-20 07:30 | 576 | 575
2017-12-20 08:00 | 604 | 604
2017-12-20 08:30 | 614 | 613
2017-12-20 09:00 | 618 | 618
2017-12-20 09:30 | 633 | 632
2017-12-20 10:00 | 643 | 642
2017-12-20 10:30 | 641 | 640
2017-12-20 11:00 | 648 | 647
2017-12-20 11:30 | 652 | 651
2017-12-20 12:00 | 659 | 658
2017-12-20 12:30 | 670 | 669
2017-12-20 13:00 | 674 | 673
2017-12-20 13:30 | 707 | 706
2017-12-20 14:00 | 718 | 717
2017-12-20 14:30 | 722 | 721
2017-12-20 15:00 | 720 | 719
2017-12-20 15:30 | 719 | 718
2017-12-20 16:00 | 724 | 723
2017-12-20 16:30 | 727 | 725
2017-12-20 17:00 | 730 | 728
2017-12-20 17:30 | 722 | 720
2017-12-20 18:00 | 707 | 703
2017-12-20 18:30 | 676 | 672
2017-12-20 19:00 | 678 | 676
2017-12-20 19:30 | 683 | 681
2017-12-20 20:00 | 667 | 665
2017-12-20 20:30 | 649 | 646
2017-12-20 21:00 | 624 | 621
2017-12-20 21:30 | 612 | 609
2017-12-20 22:00 | 593 | 589
2017-12-20 22:30 | 563 | 559
2017-12-20 23:00 | 522 | 520
2017-12-20 23:30 | 490 | 488
2017-12-21 | 464 | 462
2017-12-21 00:30 | 442 | 437
2017-12-21 01:00 | 429 | 425
2017-12-21 01:30 | 412 | 407
2017-12-21 02:00 | 402 | 398
2017-12-21 02:30 | 402 | 398
2017-12-21 03:00 | 404 | 400
2017-12-21 03:30 | 404 | 401
2017-12-21 04:00 | 396 | 393
2017-12-21 04:30 | 406 | 402
2017-12-21 05:00 | 402 | 398
2017-12-21 05:30 | 413 | 410
2017-12-21 06:00 | 432 | 431
2017-12-21 06:30 | 464 | 462
2017-12-21 07:00 | 496 | 494
2017-12-21 07:30 | 537 | 534
2017-12-21 08:00 | 559 | 557
2017-12-21 08:30 | 575 | 574
2017-12-21 09:00 | 577 | 575
2017-12-21 09:30 | 587 | 586
2017-12-21 10:00 | 588 | 587
2017-12-21 10:30 | 597 | 595
2017-12-21 11:00 | 606 | 603
2017-12-21 11:30 | 616 | 613
2017-12-21 12:00 | 623 | 621
2017-12-21 12:30 | 634 | 633
2017-12-21 13:00 | 648 | 646
2017-12-21 13:30 | 662 | 660
2017-12-21 14:00 | 666 | 664
2017-12-21 14:30 | 681 | 680
2017-12-21 15:00 | 688 | 686
2017-12-21 15:30 | 683 | 682
2017-12-21 16:00 | 691 | 689
2017-12-21 16:30 | 678 | 677
2017-12-21 17:00 | 676 | 675
2017-12-21 17:30 | 657 | 657
2017-12-21 18:00 | 661 | 660
2017-12-21 18:30 | 642 | 640
2017-12-21 19:00 | 643 | 643
2017-12-21 19:30 | 654 | 654
2017-12-21 20:00 | 649 | 649
2017-12-21 20:30 | 640 | 639
2017-12-21 21:00 | 620 | 619
2017-12-21 21:30 | 598 | 597
2017-12-21 22:00 | 579 | 578
2017-12-21 22:30 | 548 | 547
2017-12-21 23:00 | 518 | 517
2017-12-21 23:30 | 480 | 479
2017-12-22 | 452 | 451
2017-12-22 00:30 | 430 | 429
2017-12-22 01:00 | 420 | 420
2017-12-22 01:30 | 409 | 409
2017-12-22 02:00 | 405 | 405
2017-12-22 02:30 | 403 | 402
2017-12-22 03:00 | 401 | 400
2017-12-22 03:30 | 395 | 394
2017-12-22 04:00 | 397 | 395
2017-12-22 04:30 | 397 | 396
2017-12-22 05:00 | 400 | 399
2017-12-22 05:30 | 412 | 411
2017-12-22 06:00 | 432 | 431
2017-12-22 06:30 | 468 | 467
2017-12-22 07:00 | 505 | 504
2017-12-22 07:30 | 546 | 544
2017-12-22 08:00 | 565 | 563
2017-12-22 08:30 | 569 | 568
2017-12-22 09:00 | 586 | 586
2017-12-22 09:30 | 582 | 581
2017-12-22 10:00 | 580 | 579
2017-12-22 10:30 | 570 | 569
2017-12-22 11:00 | 577 | 577
2017-12-22 11:30 | 576 | 576
2017-12-22 12:00 | 588 | 588
2017-12-22 12:30 | 605 | 604
2017-12-22 13:00 | 585 | 584
2017-12-22 13:30 | 583 | 582
2017-12-22 14:00 | 599 | 598
2017-12-22 14:30 | 613 | 612
2017-12-22 15:00 | 635 | 635
2017-12-22 15:30 | 633 | 633
2017-12-22 16:00 | 639 | 639
2017-12-22 16:30 | 643 | 643
2017-12-22 17:00 | 642 | 642
2017-12-22 17:30 | 624 | 624
2017-12-22 18:00 | 608 | 608
2017-12-22 18:30 | 594 | 592
2017-12-22 19:00 | 598 | 595
2017-12-22 19:30 | 596 | 593
2017-12-22 20:00 | 597 | 592
2017-12-22 20:30 | 591 | 586
2017-12-22 21:00 | 572 | 568
2017-12-22 21:30 | 558 | 555
2017-12-22 22:00 | 538 | 535
2017-12-22 22:30 | 520 | 516
2017-12-22 23:00 | 504 | 500
2017-12-22 23:30 | 480 | 476
2017-12-23 | 450 | 446
2017-12-23 00:30 | 424 | 417
2017-12-23 01:00 | 402 | 397
2017-12-23 01:30 | 385 | 381
2017-12-23 02:00 | 374 | 370
2017-12-23 02:30 | 367 | 362
2017-12-23 03:00 | 367 | 361
2017-12-23 03:30 | 369 | 363
2017-12-23 04:00 | 367 | 360
2017-12-23 04:30 | 365 | 358
2017-12-23 05:00 | 364 | 357
2017-12-23 05:30 | 369 | 361
2017-12-23 06:00 | 382 | 375
2017-12-23 06:30 | 397 | 390
2017-12-23 07:00 | 402 | 397
2017-12-23 07:30 | 410 | 407
2017-12-23 08:00 | 419 | 416
2017-12-23 08:30 | 436 | 433
2017-12-23 09:00 | 440 | 437
2017-12-23 09:30 | 458 | 456
2017-12-23 10:00 | 461 | 460
2017-12-23 10:30 | 470 | 468
2017-12-23 11:00 | 479 | 478
2017-12-23 11:30 | 495 | 494
2017-12-23 12:00 | 506 | 505
2017-12-23 12:30 | 516 | 515
2017-12-23 13:00 | 545 | 540
2017-12-23 13:30 | 545 | 535
2017-12-23 14:00 | 544 | 534
2017-12-23 14:30 | 554 | 544
2017-12-23 15:00 | 556 | 547
2017-12-23 15:30 | 583 | 575
2017-12-23 16:00 | 589 | 581
2017-12-23 16:30 | 594 | 586
2017-12-23 17:00 | 607 | 600
2017-12-23 17:30 | 610 | 602
2017-12-23 18:00 | 596 | 588
2017-12-23 18:30 | 582 | 573
2017-12-23 19:00 | 582 | 572
2017-12-23 19:30 | 580 | 574
2017-12-23 20:00 | 571 | 565
2017-12-23 20:30 | 557 | 553
2017-12-23 21:00 | 528 | 526
2017-12-23 21:30 | 508 | 506
2017-12-23 22:00 | 483 | 480
2017-12-23 22:30 | 454 | 452
2017-12-23 23:00 | 443 | 440
2017-12-23 23:30 | 421 | 419
2017-12-24 | 396 | 394
2017-12-24 00:30 | 367 | 365
2017-12-24 01:00 | 352 | 349
2017-12-24 01:30 | 338 | 336
2017-12-24 02:00 | 326 | 323
2017-12-24 02:30 | 319 | 316
2017-12-24 03:00 | 313 | 309
2017-12-24 03:30 | 312 | 308
2017-12-24 04:00 | 311 | 307
2017-12-24 04:30 | 318 | 314
2017-12-24 05:00 | 317 | 312
2017-12-24 05:30 | 326 | 319
2017-12-24 06:00 | 332 | 326
2017-12-24 06:30 | 348 | 343
2017-12-24 07:00 | 362 | 359
2017-12-24 07:30 | 375 | 374
2017-12-24 08:00 | 383 | 382
2017-12-24 08:30 | 403 | 403
2017-12-24 09:00 | 421 | 420
2017-12-24 09:30 | 438 | 437
2017-12-24 10:00 | 447 | 446
2017-12-24 10:30 | 461 | 460
2017-12-24 11:00 | 473 | 472
2017-12-24 11:30 | 492 | 492
2017-12-24 12:00 | 509 | 509
2017-12-24 12:30 | 515 | 515
2017-12-24 13:00 | 525 | 525
2017-12-24 13:30 | 540 | 540
2017-12-24 14:00 | 555 | 555
2017-12-24 14:30 | 559 | 559
2017-12-24 15:00 | 556 | 556
2017-12-24 15:30 | 561 | 561
2017-12-24 16:00 | 576 | 576
2017-12-24 16:30 | 590 | 590
2017-12-24 17:00 | 601 | 601
2017-12-24 17:30 | 598 | 598
2017-12-24 18:00 | 577 | 577
2017-12-24 18:30 | 560 | 560
2017-12-24 19:00 | 553 | 552
2017-12-24 19:30 | 551 | 551
2017-12-24 20:00 | 552 | 551
2017-12-24 20:30 | 543 | 542
2017-12-24 21:00 | 526 | 526
2017-12-24 21:30 | 518 | 517
2017-12-24 22:00 | 500 | 499
2017-12-24 22:30 | 482 | 482
2017-12-24 23:00 | 463 | 463
2017-12-24 23:30 | 436 | 435
2017-12-25 | 408 | 408
2017-12-25 00:30 | 383 | 383
2017-12-25 01:00 | 367 | 366
2017-12-25 01:30 | 354 | 353
2017-12-25 02:00 | 343 | 341
2017-12-25 02:30 | 337 | 335
2017-12-25 03:00 | 333 | 331
2017-12-25 03:30 | 325 | 323
2017-12-25 04:00 | 317 | 314
2017-12-25 04:30 | 327 | 324
2017-12-25 05:00 | 329 | 326
2017-12-25 05:30 | 335 | 331
2017-12-25 06:00 | 348 | 344
2017-12-25 06:30 | 357 | 355
2017-12-25 07:00 | 377 | 376
2017-12-25 07:30 | 411 | 410
2017-12-25 08:00 | 423 | 423
2017-12-25 08:30 | 437 | 437
2017-12-25 09:00 | 440 | 440
2017-12-25 09:30 | 446 | 445
2017-12-25 10:00 | 455 | 454
2017-12-25 10:30 | 456 | 455
2017-12-25 11:00 | 456 | 455
2017-12-25 11:30 | 456 | 456
2017-12-25 12:00 | 458 | 458
2017-12-25 12:30 | 463 | 462
2017-12-25 13:00 | 474 | 474
2017-12-25 13:30 | 478 | 478
2017-12-25 14:00 | 488 | 488
2017-12-25 14:30 | 499 | 499
2017-12-25 15:00 | 503 | 503
2017-12-25 15:30 | 523 | 523
2017-12-25 16:00 | 558 | 558
2017-12-25 16:30 | 566 | 566
2017-12-25 17:00 | 558 | 558
2017-12-25 17:30 | 542 | 541
2017-12-25 18:00 | 529 | 528
2017-12-25 18:30 | 521 | 520
2017-12-25 19:00 | 514 | 513
2017-12-25 19:30 | 490 | 489
2017-12-25 20:00 | 476 | 475
2017-12-25 20:30 | 460 | 460
2017-12-25 21:00 | 449 | 448
2017-12-25 21:30 | 445 | 445
2017-12-25 22:00 | 437 | 437
2017-12-25 22:30 | 429 | 428
2017-12-25 23:00 | 421 | 420
2017-12-25 23:30 | 400 | 398
2017-12-26 | 371 | 368
2017-12-26 00:30 | 356 | 352
2017-12-26 01:00 | 356 | 351
2017-12-26 01:30 | 343 | 340
2017-12-26 02:00 | 331 | 328
2017-12-26 02:30 | 330 | 326
2017-12-26 03:00 | 325 | 321
2017-12-26 03:30 | 321 | 317
2017-12-26 04:00 | 321 | 317
2017-12-26 04:30 | 320 | 317
2017-12-26 05:00 | 319 | 315
2017-12-26 05:30 | 320 | 315
2017-12-26 06:00 | 327 | 323
2017-12-26 06:30 | 342 | 339
2017-12-26 07:00 | 359 | 356
2017-12-26 07:30 | 374 | 373
2017-12-26 08:00 | 382 | 381
2017-12-26 08:30 | 402 | 401
2017-12-26 09:00 | 410 | 410
2017-12-26 09:30 | 405 | 404
2017-12-26 10:00 | 402 | 402
2017-12-26 10:30 | 401 | 401
2017-12-26 11:00 | 408 | 407
2017-12-26 11:30 | 423 | 423
2017-12-26 12:00 | 438 | 438
2017-12-26 12:30 | 436 | 436
2017-12-26 13:00 | 436 | 436
2017-12-26 13:30 | 441 | 441
2017-12-26 14:00 | 447 | 447
2017-12-26 14:30 | 458 | 457
2017-12-26 15:00 | 472 | 472
2017-12-26 15:30 | 507 | 506
2017-12-26 16:00 | 487 | 486
2017-12-26 16:30 | 473 | 473
2017-12-26 17:00 | 483 | 483
2017-12-26 17:30 | 485 | 485
2017-12-26 18:00 | 478 | 478
2017-12-26 18:30 | 472 | 471
2017-12-26 19:00 | 476 | 476
2017-12-26 19:30 | 470 | 469
2017-12-26 20:00 | 462 | 460
2017-12-26 20:30 | 449 | 447
2017-12-26 21:00 | 428 | 428
2017-12-26 21:30 | 413 | 413
2017-12-26 22:00 | 398 | 398
2017-12-26 22:30 | 391 | 390
2017-12-26 23:00 | 385 | 384
2017-12-26 23:30 | 370 | 367
2017-12-27 | 350 | 347
2017-12-27 00:30 | 337 | 332
2017-12-27 01:00 | 338 | 331
2017-12-27 01:30 | 335 | 328
2017-12-27 02:00 | 326 | 319
2017-12-27 02:30 | 320 | 314
2017-12-27 03:00 | 313 | 307
2017-12-27 03:30 | 318 | 312
2017-12-27 04:00 | 320 | 314
2017-12-27 04:30 | 326 | 321
2017-12-27 05:00 | 331 | 325
2017-12-27 05:30 | 341 | 335
2017-12-27 06:00 | 353 | 349
2017-12-27 06:30 | 368 | 366
2017-12-27 07:00 | 387 | 386
2017-12-27 07:30 | 414 | 413
2017-12-27 08:00 | 425 | 425
2017-12-27 08:30 | 442 | 442
2017-12-27 09:00 | 459 | 458
2017-12-27 09:30 | 475 | 474
2017-12-27 10:00 | 479 | 478
2017-12-27 10:30 | 479 | 479
2017-12-27 11:00 | 479 | 479
2017-12-27 11:30 | 479 | 479
2017-12-27 12:00 | 478 | 478
2017-12-27 12:30 | 480 | 480
2017-12-27 13:00 | 489 | 489
2017-12-27 13:30 | 500 | 500
2017-12-27 14:00 | 493 | 493
2017-12-27 14:30 | 491 | 491
2017-12-27 15:00 | 500 | 500
2017-12-27 15:30 | 497 | 497
2017-12-27 16:00 | 487 | 487
2017-12-27 16:30 | 500 | 500
2017-12-27 17:00 | 513 | 512
2017-12-27 17:30 | 503 | 502
2017-12-27 18:00 | 489 | 488
2017-12-27 18:30 | 476 | 475
2017-12-27 19:00 | 489 | 489
2017-12-27 19:30 | 496 | 496
2017-12-27 20:00 | 496 | 496
2017-12-27 20:30 | 481 | 481
2017-12-27 21:00 | 464 | 464
2017-12-27 21:30 | 449 | 448
2017-12-27 22:00 | 437 | 437
2017-12-27 22:30 | 418 | 417
2017-12-27 23:00 | 405 | 405
2017-12-27 23:30 | 387 | 387
2017-12-28 | 370 | 369
2017-12-28 00:30 | 354 | 354
2017-12-28 01:00 | 346 | 344
2017-12-28 01:30 | 321 | 318
2017-12-28 02:00 | 313 | 310
2017-12-28 02:30 | 312 | 309
2017-12-28 03:00 | 318 | 315
2017-12-28 03:30 | 320 | 316
2017-12-28 04:00 | 327 | 323
2017-12-28 04:30 | 333 | 329
2017-12-28 05:00 | 327 | 322
2017-12-28 05:30 | 333 | 329
2017-12-28 06:00 | 341 | 337
2017-12-28 06:30 | 356 | 354
2017-12-28 07:00 | 368 | 367
2017-12-28 07:30 | 397 | 397
2017-12-28 08:00 | 395 | 395
2017-12-28 08:30 | 307 | 307
2017-12-28 09:00 | 325 | 325
2017-12-28 09:30 | 339 | 339
2017-12-28 10:00 | 343 | 343
2017-12-28 10:30 | 340 | 340
2017-12-28 11:00 | 341 | 341
2017-12-28 11:30 | 344 | 344
2017-12-28 12:00 | 350 | 350
2017-12-28 12:30 | 433 | 433
2017-12-28 13:00 | 505 | 504
2017-12-28 13:30 | 515 | 514
2017-12-28 14:00 | 516 | 515
2017-12-28 14:30 | 507 | 507
2017-12-28 15:00 | 510 | 508
2017-12-28 15:30 | 514 | 510
2017-12-28 16:00 | 529 | 525
2017-12-28 16:30 | 546 | 541
2017-12-28 17:00 | 558 | 553
2017-12-28 17:30 | 545 | 540
2017-12-28 18:00 | 540 | 535
2017-12-28 18:30 | 527 | 521
2017-12-28 19:00 | 525 | 521
2017-12-28 19:30 | 528 | 525
2017-12-28 20:00 | 535 | 532
2017-12-28 20:30 | 522 | 517
2017-12-28 21:00 | 508 | 506
2017-12-28 21:30 | 499 | 498
2017-12-28 22:00 | 486 | 484
2017-12-28 22:30 | 461 | 460
2017-12-28 23:00 | 445 | 443
2017-12-28 23:30 | 425 | 424
2017-12-29 | 400 | 399
2017-12-29 00:30 | 378 | 376
2017-12-29 01:00 | 376 | 373
2017-12-29 01:30 | 362 | 359
2017-12-29 02:00 | 350 | 348
2017-12-29 02:30 | 344 | 341
2017-12-29 03:00 | 343 | 340
2017-12-29 03:30 | 342 | 339
2017-12-29 04:00 | 339 | 336
2017-12-29 04:30 | 356 | 353
2017-12-29 05:00 | 354 | 352
2017-12-29 05:30 | 356 | 354
2017-12-29 06:00 | 354 | 352
2017-12-29 06:30 | 369 | 368
2017-12-29 07:00 | 382 | 381
2017-12-29 07:30 | 435 | 435
2017-12-29 08:00 | 457 | 456
2017-12-29 08:30 | 378 | 377
2017-12-29 09:00 | 390 | 390
2017-12-29 09:30 | 400 | 398
2017-12-29 10:00 | 399 | 397
2017-12-29 10:30 | 398 | 396
2017-12-29 11:00 | 407 | 405
2017-12-29 11:30 | 403 | 402
2017-12-29 12:00 | 433 | 432
2017-12-29 12:30 | 523 | 522
2017-12-29 13:00 | 524 | 523
2017-12-29 13:30 | 516 | 515
2017-12-29 14:00 | 514 | 513
2017-12-29 14:30 | 521 | 521
2017-12-29 15:00 | 529 | 529
2017-12-29 15:30 | 532 | 532
2017-12-29 16:00 | 544 | 544
2017-12-29 16:30 | 551 | 550
2017-12-29 17:00 | 553 | 553
2017-12-29 17:30 | 566 | 566
2017-12-29 18:00 | 569 | 569
2017-12-29 18:30 | 542 | 542
2017-12-29 19:00 | 548 | 548
2017-12-29 19:30 | 551 | 551
2017-12-29 20:00 | 548 | 548
2017-12-29 20:30 | 530 | 530
2017-12-29 21:00 | 507 | 507
2017-12-29 21:30 | 484 | 484
2017-12-29 22:00 | 474 | 473
2017-12-29 22:30 | 455 | 455
2017-12-29 23:00 | 444 | 444
2017-12-29 23:30 | 430 | 429
2017-12-30 | 408 | 408
2017-12-30 00:30 | 366 | 366
2017-12-30 01:00 | 356 | 355
2017-12-30 01:30 | 342 | 342
2017-12-30 02:00 | 318 | 318
2017-12-30 02:30 | 312 | 311
2017-12-30 03:00 | 310 | 309
2017-12-30 03:30 | 315 | 314
2017-12-30 04:00 | 313 | 312
2017-12-30 04:30 | 307 | 306
2017-12-30 05:00 | 297 | 296
2017-12-30 05:30 | 294 | 293
2017-12-30 06:00 | 309 | 307
2017-12-30 06:30 | 321 | 320
2017-12-30 07:00 | 332 | 331
2017-12-30 07:30 | 355 | 355
2017-12-30 08:00 | 370 | 370
2017-12-30 08:30 | 382 | 382
2017-12-30 09:00 | 394 | 393
2017-12-30 09:30 | 392 | 391
2017-12-30 10:00 | 400 | 400
2017-12-30 10:30 | 422 | 421
2017-12-30 11:00 | 446 | 446
2017-12-30 11:30 | 447 | 447
2017-12-30 12:00 | 450 | 449
2017-12-30 12:30 | 460 | 459
2017-12-30 13:00 | 474 | 474
2017-12-30 13:30 | 474 | 474
2017-12-30 14:00 | 477 | 477
2017-12-30 14:30 | 481 | 481
2017-12-30 15:00 | 492 | 492
2017-12-30 15:30 | 499 | 498
2017-12-30 16:00 | 530 | 530
2017-12-30 16:30 | 549 | 548
2017-12-30 17:00 | 566 | 566
2017-12-30 17:30 | 562 | 562
2017-12-30 18:00 | 558 | 558
2017-12-30 18:30 | 553 | 553
2017-12-30 19:00 | 561 | 560
2017-12-30 19:30 | 565 | 565
2017-12-30 20:00 | 565 | 564
2017-12-30 20:30 | 558 | 558
2017-12-30 21:00 | 537 | 536
2017-12-30 21:30 | 516 | 516
2017-12-30 22:00 | 508 | 507
2017-12-30 22:30 | 489 | 488
2017-12-30 23:00 | 473 | 472
2017-12-30 23:30 | 455 | 454
2017-12-31 | 428 | 428
2017-12-31 00:30 | 389 | 389
2017-12-31 01:00 | 382 | 382
2017-12-31 01:30 | 375 | 375
2017-12-31 02:00 | 364 | 364
2017-12-31 02:30 | 357 | 357
2017-12-31 03:00 | 353 | 353
2017-12-31 03:30 | 353 | 353
2017-12-31 04:00 | 355 | 355
2017-12-31 04:30 | 343 | 342
2017-12-31 05:00 | 338 | 337
2017-12-31 05:30 | 340 | 339
2017-12-31 06:00 | 349 | 348
2017-12-31 06:30 | 354 | 353
2017-12-31 07:00 | 354 | 352
2017-12-31 07:30 | 359 | 358
2017-12-31 08:00 | 366 | 366
2017-12-31 08:30 | 386 | 386
2017-12-31 09:00 | 400 | 400
2017-12-31 09:30 | 420 | 420
2017-12-31 10:00 | 430 | 430
2017-12-31 10:30 | 446 | 446
2017-12-31 11:00 | 472 | 469
2017-12-31 11:30 | 493 | 489
2017-12-31 12:00 | 501 | 498
2017-12-31 12:30 | 507 | 505
2017-12-31 13:00 | 523 | 521
2017-12-31 13:30 | 543 | 541
2017-12-31 14:00 | 561 | 559
2017-12-31 14:30 | 547 | 545
2017-12-31 15:00 | 505 | 503
2017-12-31 15:30 | 524 | 521
2017-12-31 16:00 | 538 | 535
2017-12-31 16:30 | 525 | 521
2017-12-31 17:00 | 517 | 513
2017-12-31 17:30 | 508 | 505
2017-12-31 18:00 | 501 | 497
2017-12-31 18:30 | 493 | 489
2017-12-31 19:00 | 497 | 493
2017-12-31 19:30 | 498 | 496
2017-12-31 20:00 | 498 | 497
2017-12-31 20:30 | 494 | 493
2017-12-31 21:00 | 485 | 484
2017-12-31 21:30 | 484 | 484
2017-12-31 22:00 | 483 | 483
2017-12-31 22:30 | 479 | 479
2017-12-31 23:00 | 476 | 476
2017-12-31 23:30 | 466 | 466
2018-01-01 | 444 | 443
2018-01-01 00:30 | 431 | 430
2018-01-01 01:00 | 423 | 423
2018-01-01 01:30 | 412 | 411
2018-01-01 02:00 | 394 | 394
2018-01-01 02:30 | 376 | 376
2018-01-01 03:00 | 370 | 370
2018-01-01 03:30 | 368 | 368
2018-01-01 04:00 | 365 | 364
2018-01-01 04:30 | 366 | 366
2018-01-01 05:00 | 369 | 368
2018-01-01 05:30 | 369 | 368
2018-01-01 06:00 | 379 | 378
2018-01-01 06:30 | 389 | 389
2018-01-01 07:00 | 399 | 399
2018-01-01 07:30 | 421 | 421
2018-01-01 08:00 | 435 | 435
2018-01-01 08:30 | 477 | 477
2018-01-01 09:00 | 500 | 499
2018-01-01 09:30 | 517 | 516
2018-01-01 10:00 | 532 | 531
2018-01-01 10:30 | 538 | 538
2018-01-01 11:00 | 524 | 523
2018-01-01 11:30 | 517 | 517
2018-01-01 12:00 | 518 | 518
2018-01-01 12:30 | 523 | 522
2018-01-01 13:00 | 536 | 535
2018-01-01 13:30 | 554 | 553
2018-01-01 14:00 | 557 | 555
2018-01-01 14:30 | 560 | 559
2018-01-01 15:00 | 576 | 576
2018-01-01 15:30 | 596 | 595
2018-01-01 16:00 | 608 | 607
2018-01-01 16:30 | 611 | 610
2018-01-01 17:00 | 615 | 614
2018-01-01 17:30 | 616 | 615
2018-01-01 18:00 | 607 | 604
2018-01-01 18:30 | 578 | 576
2018-01-01 19:00 | 579 | 578
2018-01-01 19:30 | 574 | 573
2018-01-01 20:00 | 565 | 564
2018-01-01 20:30 | 554 | 553
2018-01-01 21:00 | 531 | 530
2018-01-01 21:30 | 508 | 505
2018-01-01 22:00 | 494 | 491
2018-01-01 22:30 | 463 | 462
2018-01-01 23:00 | 447 | 446
2018-01-01 23:30 | 420 | 419
2018-01-02 | 397 | 397
2018-01-02 00:30 | 382 | 381
2018-01-02 01:00 | 371 | 371
2018-01-02 01:30 | 362 | 362
2018-01-02 02:00 | 355 | 354
2018-01-02 02:30 | 348 | 347
2018-01-02 03:00 | 347 | 346
2018-01-02 03:30 | 349 | 348
2018-01-02 04:00 | 351 | 351
2018-01-02 04:30 | 351 | 351
2018-01-02 05:00 | 352 | 352
2018-01-02 05:30 | 363 | 363
2018-01-02 06:00 | 382 | 382
2018-01-02 06:30 | 417 | 416
2018-01-02 07:00 | 444 | 442
2018-01-02 07:30 | 484 | 483
2018-01-02 08:00 | 500 | 499
2018-01-02 08:30 | 514 | 513
2018-01-02 09:00 | 524 | 523
2018-01-02 09:30 | 526 | 526
2018-01-02 10:00 | 541 | 540
2018-01-02 10:30 | 554 | 553
2018-01-02 11:00 | 558 | 557
2018-01-02 11:30 | 555 | 554
2018-01-02 12:00 | 557 | 556
2018-01-02 12:30 | 548 | 548
2018-01-02 13:00 | 543 | 542
2018-01-02 13:30 | 559 | 558
2018-01-02 14:00 | 575 | 574
2018-01-02 14:30 | 601 | 601
2018-01-02 15:00 | 613 | 613
2018-01-02 15:30 | 626 | 625
2018-01-02 16:00 | 626 | 625
2018-01-02 16:30 | 595 | 594
2018-01-02 17:00 | 581 | 579
2018-01-02 17:30 | 571 | 569
2018-01-02 18:00 | 565 | 563
2018-01-02 18:30 | 550 | 549
2018-01-02 19:00 | 558 | 558
2018-01-02 19:30 | 538 | 537
2018-01-02 20:00 | 535 | 534
2018-01-02 20:30 | 519 | 518
2018-01-02 21:00 | 493 | 493
2018-01-02 21:30 | 479 | 478
2018-01-02 22:00 | 467 | 467
2018-01-02 22:30 | 464 | 463
2018-01-02 23:00 | 441 | 440
2018-01-02 23:30 | 420 | 419
2018-01-03 | 401 | 400
2018-01-03 00:30 | 377 | 376
2018-01-03 01:00 | 372 | 371
2018-01-03 01:30 | 361 | 360
2018-01-03 02:00 | 354 | 352
2018-01-03 02:30 | 351 | 349
2018-01-03 03:00 | 352 | 349
2018-01-03 03:30 | 351 | 349
2018-01-03 04:00 | 351 | 349
2018-01-03 04:30 | 352 | 350
2018-01-03 05:00 | 356 | 354
2018-01-03 05:30 | 371 | 369
2018-01-03 06:00 | 387 | 385
2018-01-03 06:30 | 417 | 414
2018-01-03 07:00 | 450 | 444
2018-01-03 07:30 | 473 | 467
2018-01-03 08:00 | 482 | 478
2018-01-03 08:30 | 501 | 497
2018-01-03 09:00 | 515 | 509
2018-01-03 09:30 | 518 | 513
2018-01-03 10:00 | 519 | 514
2018-01-03 10:30 | 517 | 512
2018-01-03 11:00 | 520 | 516
2018-01-03 11:30 | 527 | 523
2018-01-03 12:00 | 531 | 528
2018-01-03 12:30 | 539 | 537
2018-01-03 13:00 | 542 | 540
2018-01-03 13:30 | 558 | 556
2018-01-03 14:00 | 626 | 624
2018-01-03 14:30 | 625 | 620
2018-01-03 15:00 | 603 | 597
2018-01-03 15:30 | 574 | 571
2018-01-03 16:00 | 569 | 565
2018-01-03 16:30 | 565 | 560
2018-01-03 17:00 | 567 | 562
2018-01-03 17:30 | 565 | 560
2018-01-03 18:00 | 558 | 552
2018-01-03 18:30 | 548 | 543
2018-01-03 19:00 | 543 | 540
2018-01-03 19:30 | 545 | 542
2018-01-03 20:00 | 542 | 540
2018-01-03 20:30 | 536 | 533
2018-01-03 21:00 | 506 | 505
2018-01-03 21:30 | 487 | 487
2018-01-03 22:00 | 471 | 471
2018-01-03 22:30 | 461 | 460
2018-01-03 23:00 | 441 | 440
2018-01-03 23:30 | 425 | 423
2018-01-04 | 402 | 401
2018-01-04 00:30 | 377 | 376
2018-01-04 01:00 | 367 | 366
2018-01-04 01:30 | 356 | 354
2018-01-04 02:00 | 353 | 351
2018-01-04 02:30 | 343 | 340
2018-01-04 03:00 | 326 | 323
2018-01-04 03:30 | 342 | 340
2018-01-04 04:00 | 345 | 343
2018-01-04 04:30 | 349 | 347
2018-01-04 05:00 | 353 | 351
2018-01-04 05:30 | 366 | 364
2018-01-04 06:00 | 380 | 378
2018-01-04 06:30 | 413 | 412
2018-01-04 07:00 | 438 | 437
2018-01-04 07:30 | 453 | 453
2018-01-04 08:00 | 463 | 463
2018-01-04 08:30 | 486 | 485
2018-01-04 09:00 | 491 | 491
2018-01-04 09:30 | 496 | 496
2018-01-04 10:00 | 473 | 473
2018-01-04 10:30 | 478 | 478
2018-01-04 11:00 | 485 | 485
2018-01-04 11:30 | 477 | 477
2018-01-04 12:00 | 488 | 488
2018-01-04 12:30 | 489 | 488
2018-01-04 13:00 | 489 | 489
2018-01-04 13:30 | 496 | 496
2018-01-04 14:00 | 501 | 501
2018-01-04 14:30 | 506 | 505
2018-01-04 15:00 | 499 | 498
2018-01-04 15:30 | 493 | 492
2018-01-04 16:00 | 497 | 497
2018-01-04 16:30 | 505 | 504
2018-01-04 17:00 | 510 | 510
2018-01-04 17:30 | 507 | 507
2018-01-04 18:00 | 503 | 502
2018-01-04 18:30 | 487 | 487
2018-01-04 19:00 | 482 | 482
2018-01-04 19:30 | 487 | 487
2018-01-04 20:00 | 502 | 501
2018-01-04 20:30 | 515 | 514
2018-01-04 21:00 | 492 | 491
2018-01-04 21:30 | 473 | 472
2018-01-04 22:00 | 450 | 449
2018-01-04 22:30 | 446 | 445
2018-01-04 23:00 | 421 | 420
2018-01-04 23:30 | 394 | 393
2018-01-05 | 376 | 375
2018-01-05 00:30 | 362 | 360
2018-01-05 01:00 | 351 | 349
2018-01-05 01:30 | 346 | 343
2018-01-05 02:00 | 338 | 335
2018-01-05 02:30 | 337 | 334
2018-01-05 03:00 | 330 | 328
2018-01-05 03:30 | 333 | 330
2018-01-05 04:00 | 336 | 332
2018-01-05 04:30 | 340 | 337
2018-01-05 05:00 | 345 | 342
2018-01-05 05:30 | 357 | 354
2018-01-05 06:00 | 371 | 368
2018-01-05 06:30 | 399 | 399
2018-01-05 07:00 | 428 | 428
2018-01-05 07:30 | 441 | 440
2018-01-05 08:00 | 445 | 445
2018-01-05 08:30 | 470 | 470
2018-01-05 09:00 | 489 | 489
2018-01-05 09:30 | 514 | 514
2018-01-05 10:00 | 530 | 530
2018-01-05 10:30 | 529 | 529
2018-01-05 11:00 | 509 | 508
2018-01-05 11:30 | 511 | 511
2018-01-05 12:00 | 516 | 515
2018-01-05 12:30 | 520 | 519
2018-01-05 13:00 | 529 | 529
2018-01-05 13:30 | 540 | 539
2018-01-05 14:00 | 555 | 555
2018-01-05 14:30 | 559 | 559
2018-01-05 15:00 | 569 | 568
2018-01-05 15:30 | 580 | 579
2018-01-05 16:00 | 595 | 594
2018-01-05 16:30 | 603 | 602
2018-01-05 17:00 | 610 | 610
2018-01-05 17:30 | 593 | 592
2018-01-05 18:00 | 567 | 565
2018-01-05 18:30 | 544 | 543
2018-01-05 19:00 | 540 | 539
2018-01-05 19:30 | 536 | 536
2018-01-05 20:00 | 537 | 536
2018-01-05 20:30 | 532 | 531
2018-01-05 21:00 | 521 | 520
2018-01-05 21:30 | 499 | 498
2018-01-05 22:00 | 464 | 463
2018-01-05 22:30 | 460 | 459
2018-01-05 23:00 | 437 | 436
2018-01-05 23:30 | 424 | 423
2018-01-06 | 404 | 404
2018-01-06 00:30 | 383 | 382
2018-01-06 01:00 | 379 | 376
2018-01-06 01:30 | 370 | 367
2018-01-06 02:00 | 357 | 353
2018-01-06 02:30 | 348 | 344
2018-01-06 03:00 | 341 | 336
2018-01-06 03:30 | 331 | 326
2018-01-06 04:00 | 330 | 324
2018-01-06 04:30 | 328 | 322
2018-01-06 05:00 | 327 | 321
2018-01-06 05:30 | 332 | 325
2018-01-06 06:00 | 359 | 353
2018-01-06 06:30 | 377 | 371
2018-01-06 07:00 | 384 | 380
2018-01-06 07:30 | 400 | 397
2018-01-06 08:00 | 410 | 408
2018-01-06 08:30 | 416 | 415
2018-01-06 09:00 | 421 | 421
2018-01-06 09:30 | 430 | 430
2018-01-06 10:00 | 451 | 451
2018-01-06 10:30 | 448 | 448
2018-01-06 11:00 | 429 | 429
2018-01-06 11:30 | 441 | 441
2018-01-06 12:00 | 444 | 444
2018-01-06 12:30 | 463 | 463
2018-01-06 13:00 | 482 | 481
2018-01-06 13:30 | 489 | 489
2018-01-06 14:00 | 508 | 506
2018-01-06 14:30 | 507 | 504
2018-01-06 15:00 | 520 | 517
2018-01-06 15:30 | 549 | 546
2018-01-06 16:00 | 574 | 570
2018-01-06 16:30 | 563 | 559
2018-01-06 17:00 | 562 | 559
2018-01-06 17:30 | 561 | 558
2018-01-06 18:00 | 557 | 553
2018-01-06 18:30 | 550 | 545
2018-01-06 19:00 | 547 | 541
2018-01-06 19:30 | 539 | 538
2018-01-06 20:00 | 547 | 547
2018-01-06 20:30 | 541 | 540
2018-01-06 21:00 | 520 | 519
2018-01-06 21:30 | 508 | 507
2018-01-06 22:00 | 486 | 485
2018-01-06 22:30 | 461 | 461
2018-01-06 23:00 | 440 | 439
2018-01-06 23:30 | 412 | 412
2018-01-07 | 388 | 387
2018-01-07 00:30 | 378 | 377
2018-01-07 01:00 | 373 | 371
2018-01-07 01:30 | 365 | 363
2018-01-07 02:00 | 354 | 351
2018-01-07 02:30 | 350 | 347
2018-01-07 03:00 | 349 | 345
2018-01-07 03:30 | 345 | 342
2018-01-07 04:00 | 342 | 339
2018-01-07 04:30 | 341 | 337
2018-01-07 05:00 | 336 | 331
2018-01-07 05:30 | 344 | 337
2018-01-07 06:00 | 354 | 346
2018-01-07 06:30 | 367 | 361
2018-01-07 07:00 | 374 | 369
2018-01-07 07:30 | 390 | 386
2018-01-07 08:00 | 401 | 398
2018-01-07 08:30 | 414 | 412
2018-01-07 09:00 | 427 | 426
2018-01-07 09:30 | 434 | 434
2018-01-07 10:00 | 458 | 457
2018-01-07 10:30 | 476 | 475
2018-01-07 11:00 | 483 | 482
2018-01-07 11:30 | 482 | 481
2018-01-07 12:00 | 499 | 498
2018-01-07 12:30 | 504 | 504
2018-01-07 13:00 | 517 | 516
2018-01-07 13:30 | 527 | 526
2018-01-07 14:00 | 536 | 535
2018-01-07 14:30 | 558 | 558
2018-01-07 15:00 | 581 | 580
2018-01-07 15:30 | 597 | 596
2018-01-07 16:00 | 611 | 611
2018-01-07 16:30 | 620 | 620
2018-01-07 17:00 | 633 | 631
2018-01-07 17:30 | 641 | 631
2018-01-07 18:00 | 635 | 623
2018-01-07 18:30 | 619 | 610
2018-01-07 19:00 | 614 | 608
2018-01-07 19:30 | 609 | 603
2018-01-07 20:00 | 613 | 606
2018-01-07 20:30 | 599 | 592
2018-01-07 21:00 | 558 | 552
2018-01-07 21:30 | 538 | 531
2018-01-07 22:00 | 516 | 510
2018-01-07 22:30 | 493 | 491
2018-01-07 23:00 | 462 | 461
2018-01-07 23:30 | 430 | 429
2018-01-08 | 404 | 401
2018-01-08 00:30 | 397 | 393
2018-01-08 01:00 | 394 | 390
2018-01-08 01:30 | 376 | 372
2018-01-08 02:00 | 368 | 364
2018-01-08 02:30 | 366 | 362
2018-01-08 03:00 | 364 | 360
2018-01-08 03:30 | 363 | 359
2018-01-08 04:00 | 363 | 358
2018-01-08 04:30 | 367 | 363
2018-01-08 05:00 | 373 | 368
2018-01-08 05:30 | 382 | 378
2018-01-08 06:00 | 401 | 399
2018-01-08 06:30 | 443 | 443
2018-01-08 07:00 | 486 | 486
2018-01-08 07:30 | 520 | 520
2018-01-08 08:00 | 542 | 542
2018-01-08 08:30 | 555 | 555
2018-01-08 09:00 | 560 | 560
2018-01-08 09:30 | 567 | 566
2018-01-08 10:00 | 573 | 573
2018-01-08 10:30 | 575 | 575
2018-01-08 11:00 | 587 | 587
2018-01-08 11:30 | 588 | 588
2018-01-08 12:00 | 598 | 598
2018-01-08 12:30 | 622 | 622
2018-01-08 13:00 | 641 | 641
2018-01-08 13:30 | 663 | 663
2018-01-08 14:00 | 678 | 678
2018-01-08 14:30 | 683 | 683
2018-01-08 15:00 | 697 | 697
2018-01-08 15:30 | 706 | 706
2018-01-08 16:00 | 721 | 721
2018-01-08 16:30 | 727 | 727
2018-01-08 17:00 | 731 | 731
2018-01-08 17:30 | 726 | 726
2018-01-08 18:00 | 712 | 711
2018-01-08 18:30 | 674 | 673
2018-01-08 19:00 | 668 | 667
2018-01-08 19:30 | 661 | 661
2018-01-08 20:00 | 650 | 649
2018-01-08 20:30 | 623 | 621
2018-01-08 21:00 | 590 | 588
2018-01-08 21:30 | 568 | 566
2018-01-08 22:00 | 544 | 542
2018-01-08 22:30 | 530 | 528
2018-01-08 23:00 | 504 | 503
2018-01-08 23:30 | 477 | 476
2018-01-09 | 453 | 451
2018-01-09 00:30 | 432 | 429
2018-01-09 01:00 | 423 | 419
2018-01-09 01:30 | 412 | 408
2018-01-09 02:00 | 400 | 395
2018-01-09 02:30 | 388 | 383
2018-01-09 03:00 | 381 | 375
2018-01-09 03:30 | 375 | 369
2018-01-09 04:00 | 375 | 369
2018-01-09 04:30 | 377 | 371
2018-01-09 05:00 | 384 | 378
2018-01-09 05:30 | 396 | 391
2018-01-09 06:00 | 410 | 406
2018-01-09 06:30 | 452 | 451
2018-01-09 07:00 | 495 | 494
2018-01-09 07:30 | 520 | 520
2018-01-09 08:00 | 533 | 532
2018-01-09 08:30 | 548 | 546
2018-01-09 09:00 | 556 | 552
2018-01-09 09:30 | 565 | 562
2018-01-09 10:00 | 567 | 564
2018-01-09 10:30 | 576 | 571
2018-01-09 11:00 | 585 | 580
2018-01-09 11:30 | 587 | 582
2018-01-09 12:00 | 596 | 592
2018-01-09 12:30 | 604 | 602
2018-01-09 13:00 | 613 | 611
2018-01-09 13:30 | 621 | 619
2018-01-09 14:00 | 625 | 623
2018-01-09 14:30 | 633 | 631
2018-01-09 15:00 | 640 | 639
2018-01-09 15:30 | 653 | 652
2018-01-09 16:00 | 682 | 679
2018-01-09 16:30 | 699 | 696
2018-01-09 17:00 | 711 | 707
2018-01-09 17:30 | 703 | 698
2018-01-09 18:00 | 692 | 684
2018-01-09 18:30 | 650 | 640
2018-01-09 19:00 | 641 | 631
2018-01-09 19:30 | 632 | 623
2018-01-09 20:00 | 619 | 614
2018-01-09 20:30 | 599 | 594
2018-01-09 21:00 | 572 | 570
2018-01-09 21:30 | 555 | 553
2018-01-09 22:00 | 539 | 536
2018-01-09 22:30 | 516 | 513
2018-01-09 23:00 | 487 | 485
2018-01-09 23:30 | 468 | 465
2018-01-10 | 436 | 433
2018-01-10 00:30 | 409 | 407
2018-01-10 01:00 | 397 | 396
2018-01-10 01:30 | 388 | 386
2018-01-10 02:00 | 378 | 376
2018-01-10 02:30 | 372 | 370
2018-01-10 03:00 | 372 | 370
2018-01-10 03:30 | 370 | 368
2018-01-10 04:00 | 369 | 366
2018-01-10 04:30 | 372 | 370
2018-01-10 05:00 | 376 | 375
2018-01-10 05:30 | 396 | 395
2018-01-10 06:00 | 416 | 415
2018-01-10 06:30 | 463 | 462
2018-01-10 07:00 | 498 | 497
2018-01-10 07:30 | 531 | 529
2018-01-10 08:00 | 550 | 546
2018-01-10 08:30 | 568 | 563
2018-01-10 09:00 | 572 | 567
2018-01-10 09:30 | 582 | 578
2018-01-10 10:00 | 596 | 592
2018-01-10 10:30 | 612 | 608
2018-01-10 11:00 | 628 | 623
2018-01-10 11:30 | 634 | 628
2018-01-10 12:00 | 632 | 627
2018-01-10 12:30 | 632 | 626
2018-01-10 13:00 | 633 | 627
2018-01-10 13:30 | 638 | 633
2018-01-10 14:00 | 637 | 633
2018-01-10 14:30 | 645 | 641
2018-01-10 15:00 | 661 | 658
2018-01-10 15:30 | 664 | 661
2018-01-10 16:00 | 682 | 679
2018-01-10 16:30 | 697 | 693
2018-01-10 17:00 | 706 | 702
2018-01-10 17:30 | 705 | 700
2018-01-10 18:00 | 689 | 681
2018-01-10 18:30 | 654 | 643
2018-01-10 19:00 | 642 | 633
2018-01-10 19:30 | 637 | 632
2018-01-10 20:00 | 627 | 622
2018-01-10 20:30 | 614 | 609
2018-01-10 21:00 | 585 | 579
2018-01-10 21:30 | 564 | 556
2018-01-10 22:00 | 540 | 531
2018-01-10 22:30 | 527 | 524
2018-01-10 23:00 | 512 | 508
2018-01-10 23:30 | 476 | 473
2018-01-11 | 449 | 446
2018-01-11 00:30 | 429 | 426
2018-01-11 01:00 | 416 | 414
2018-01-11 01:30 | 404 | 402
2018-01-11 02:00 | 396 | 394
2018-01-11 02:30 | 393 | 391
2018-01-11 03:00 | 387 | 385
2018-01-11 03:30 | 387 | 385
2018-01-11 04:00 | 388 | 386
2018-01-11 04:30 | 384 | 382
2018-01-11 05:00 | 385 | 383
2018-01-11 05:30 | 402 | 401
2018-01-11 06:00 | 433 | 432
2018-01-11 06:30 | 474 | 474
2018-01-11 07:00 | 500 | 500
2018-01-11 07:30 | 525 | 524
2018-01-11 08:00 | 560 | 560
2018-01-11 08:30 | 587 | 586
2018-01-11 09:00 | 600 | 600
2018-01-11 09:30 | 616 | 616
2018-01-11 10:00 | 611 | 610
2018-01-11 10:30 | 611 | 610
2018-01-11 11:00 | 619 | 618
2018-01-11 11:30 | 636 | 635
2018-01-11 12:00 | 645 | 643
2018-01-11 12:30 | 646 | 645
2018-01-11 13:00 | 642 | 639
2018-01-11 13:30 | 651 | 646
2018-01-11 14:00 | 670 | 667
2018-01-11 14:30 | 691 | 687
2018-01-11 15:00 | 705 | 701
2018-01-11 15:30 | 705 | 700
2018-01-11 16:00 | 722 | 717
2018-01-11 16:30 | 724 | 719
2018-01-11 17:00 | 710 | 702
2018-01-11 17:30 | 704 | 699
2018-01-11 18:00 | 703 | 696
2018-01-11 18:30 | 683 | 671
2018-01-11 19:00 | 680 | 670
2018-01-11 19:30 | 670 | 664
2018-01-11 20:00 | 665 | 658
2018-01-11 20:30 | 641 | 636
2018-01-11 21:00 | 607 | 605
2018-01-11 21:30 | 580 | 576
2018-01-11 22:00 | 545 | 543
2018-01-11 22:30 | 527 | 526
2018-01-11 23:00 | 511 | 510
2018-01-11 23:30 | 488 | 486
2018-01-12 | 463 | 461
2018-01-12 00:30 | 441 | 440
2018-01-12 01:00 | 420 | 419
2018-01-12 01:30 | 407 | 405
2018-01-12 02:00 | 385 | 384
2018-01-12 02:30 | 379 | 377
2018-01-12 03:00 | 381 | 379
2018-01-12 03:30 | 381 | 379
2018-01-12 04:00 | 379 | 377
2018-01-12 04:30 | 391 | 389
2018-01-12 05:00 | 411 | 410
2018-01-12 05:30 | 418 | 417
2018-01-12 06:00 | 436 | 435
2018-01-12 06:30 | 468 | 468
2018-01-12 07:00 | 513 | 512
2018-01-12 07:30 | 553 | 551
2018-01-12 08:00 | 565 | 562
2018-01-12 08:30 | 580 | 578
2018-01-12 09:00 | 589 | 586
2018-01-12 09:30 | 603 | 601
2018-01-12 10:00 | 605 | 604
2018-01-12 10:30 | 603 | 601
2018-01-12 11:00 | 607 | 605
2018-01-12 11:30 | 610 | 608
2018-01-12 12:00 | 615 | 613
2018-01-12 12:30 | 624 | 622
2018-01-12 13:00 | 634 | 632
2018-01-12 13:30 | 652 | 646
2018-01-12 14:00 | 667 | 661
2018-01-12 14:30 | 682 | 676
2018-01-12 15:00 | 699 | 693
2018-01-12 15:30 | 714 | 707
2018-01-12 16:00 | 730 | 723
2018-01-12 16:30 | 745 | 737
2018-01-12 17:00 | 760 | 750
2018-01-12 17:30 | 754 | 741
2018-01-12 18:00 | 721 | 709
2018-01-12 18:30 | 680 | 670
2018-01-12 19:00 | 671 | 663
2018-01-12 19:30 | 665 | 658
2018-01-12 20:00 | 661 | 654
2018-01-12 20:30 | 647 | 641
2018-01-12 21:00 | 615 | 612
2018-01-12 21:30 | 592 | 592
2018-01-12 22:00 | 567 | 566
2018-01-12 22:30 | 556 | 556
2018-01-12 23:00 | 540 | 540
2018-01-12 23:30 | 507 | 506
2018-01-13 | 480 | 479
2018-01-13 00:30 | 459 | 459
2018-01-13 01:00 | 451 | 450
2018-01-13 01:30 | 441 | 438
2018-01-13 02:00 | 425 | 423
2018-01-13 02:30 | 410 | 407
2018-01-13 03:00 | 403 | 399
2018-01-13 03:30 | 398 | 394
2018-01-13 04:00 | 393 | 388
2018-01-13 04:30 | 383 | 378
2018-01-13 05:00 | 383 | 378
2018-01-13 05:30 | 401 | 396
2018-01-13 06:00 | 402 | 400
2018-01-13 06:30 | 426 | 424
2018-01-13 07:00 | 448 | 447
2018-01-13 07:30 | 459 | 458
2018-01-13 08:00 | 480 | 480
2018-01-13 08:30 | 500 | 500
2018-01-13 09:00 | 518 | 517
2018-01-13 09:30 | 534 | 533
2018-01-13 10:00 | 549 | 548
2018-01-13 10:30 | 563 | 563
2018-01-13 11:00 | 572 | 572
2018-01-13 11:30 | 577 | 577
2018-01-13 12:00 | 593 | 593
2018-01-13 12:30 | 606 | 606
2018-01-13 13:00 | 619 | 619
2018-01-13 13:30 | 617 | 617
2018-01-13 14:00 | 641 | 641
2018-01-13 14:30 | 645 | 645
2018-01-13 15:00 | 659 | 659
2018-01-13 15:30 | 672 | 672
2018-01-13 16:00 | 694 | 694
2018-01-13 16:30 | 710 | 709
2018-01-13 17:00 | 710 | 708
2018-01-13 17:30 | 683 | 681
2018-01-13 18:00 | 652 | 648
2018-01-13 18:30 | 640 | 634
2018-01-13 19:00 | 653 | 647
2018-01-13 19:30 | 641 | 637
2018-01-13 20:00 | 637 | 633
2018-01-13 20:30 | 622 | 620
2018-01-13 21:00 | 604 | 604
2018-01-13 21:30 | 584 | 584
2018-01-13 22:00 | 561 | 560
2018-01-13 22:30 | 546 | 544
2018-01-13 23:00 | 529 | 526
2018-01-13 23:30 | 500 | 498
2018-01-14 | 458 | 457
2018-01-14 00:30 | 422 | 421
2018-01-14 01:00 | 409 | 408
2018-01-14 01:30 | 392 | 391
2018-01-14 02:00 | 382 | 382
2018-01-14 02:30 | 376 | 375
2018-01-14 03:00 | 366 | 365
2018-01-14 03:30 | 356 | 355
2018-01-14 04:00 | 351 | 349
2018-01-14 04:30 | 336 | 335
2018-01-14 05:00 | 332 | 330
2018-01-14 05:30 | 336 | 333
2018-01-14 06:00 | 349 | 346
2018-01-14 06:30 | 374 | 372
2018-01-14 07:00 | 388 | 387
2018-01-14 07:30 | 408 | 408
2018-01-14 08:00 | 437 | 437
2018-01-14 08:30 | 461 | 461
2018-01-14 09:00 | 489 | 489
2018-01-14 09:30 | 523 | 523
2018-01-14 10:00 | 538 | 538
2018-01-14 10:30 | 551 | 551
2018-01-14 11:00 | 535 | 535
2018-01-14 11:30 | 510 | 510
2018-01-14 12:00 | 515 | 515
2018-01-14 12:30 | 527 | 527
2018-01-14 13:00 | 550 | 549
2018-01-14 13:30 | 568 | 567
2018-01-14 14:00 | 576 | 574
2018-01-14 14:30 | 592 | 591
2018-01-14 15:00 | 611 | 609
2018-01-14 15:30 | 610 | 607
2018-01-14 16:00 | 614 | 611
2018-01-14 16:30 | 608 | 605
2018-01-14 17:00 | 599 | 595
2018-01-14 17:30 | 570 | 564
2018-01-14 18:00 | 538 | 531
2018-01-14 18:30 | 509 | 503
2018-01-14 19:00 | 489 | 486
2018-01-14 19:30 | 481 | 479
2018-01-14 20:00 | 474 | 473
2018-01-14 20:30 | 449 | 449
2018-01-14 21:00 | 421 | 421
2018-01-14 21:30 | 405 | 405
2018-01-14 22:00 | 391 | 390
2018-01-14 22:30 | 387 | 387
2018-01-14 23:00 | 379 | 378
2018-01-14 23:30 | 359 | 359
2018-01-15 | 339 | 339
2018-01-15 00:30 | 325 | 323
2018-01-15 01:00 | 317 | 315
2018-01-15 01:30 | 299 | 297
2018-01-15 02:00 | 284 | 282
2018-01-15 02:30 | 289 | 287
2018-01-15 03:00 | 294 | 292
2018-01-15 03:30 | 298 | 295
2018-01-15 04:00 | 307 | 304
2018-01-15 04:30 | 313 | 311
2018-01-15 05:00 | 306 | 304
2018-01-15 05:30 | 323 | 322
2018-01-15 06:00 | 348 | 348
2018-01-15 06:30 | 375 | 375
2018-01-15 07:00 | 406 | 406
2018-01-15 07:30 | 423 | 423
2018-01-15 08:00 | 433 | 432
2018-01-15 08:30 | 437 | 436
2018-01-15 09:00 | 438 | 437
2018-01-15 09:30 | 436 | 435
2018-01-15 10:00 | 436 | 434
2018-01-15 10:30 | 435 | 434
2018-01-15 11:00 | 444 | 443
2018-01-15 11:30 | 453 | 452
2018-01-15 12:00 | 455 | 454
2018-01-15 12:30 | 463 | 463
2018-01-15 13:00 | 471 | 471
2018-01-15 13:30 | 477 | 476
2018-01-15 14:00 | 483 | 483
2018-01-15 14:30 | 492 | 492
2018-01-15 15:00 | 498 | 497
2018-01-15 15:30 | 505 | 504
2018-01-15 16:00 | 517 | 516
2018-01-15 16:30 | 525 | 525
2018-01-15 17:00 | 532 | 532
2018-01-15 17:30 | 527 | 526
2018-01-15 18:00 | 516 | 515
2018-01-15 18:30 | 499 | 498
2018-01-15 19:00 | 499 | 497
2018-01-15 19:30 | 497 | 496
2018-01-15 20:00 | 494 | 493
2018-01-15 20:30 | 475 | 475
2018-01-15 21:00 | 452 | 452
2018-01-15 21:30 | 434 | 433
2018-01-15 22:00 | 427 | 427
2018-01-15 22:30 | 426 | 425
2018-01-15 23:00 | 419 | 419
2018-01-15 23:30 | 396 | 395
2018-01-16 | 361 | 361
2018-01-16 00:30 | 343 | 342
2018-01-16 01:00 | 330 | 329
2018-01-16 01:30 | 322 | 320
2018-01-16 02:00 | 310 | 308
2018-01-16 02:30 | 313 | 311
2018-01-16 03:00 | 312 | 310
2018-01-16 03:30 | 315 | 313
2018-01-16 04:00 | 316 | 314
2018-01-16 04:30 | 325 | 323
2018-01-16 05:00 | 341 | 339
2018-01-16 05:30 | 341 | 340
2018-01-16 06:00 | 357 | 356
2018-01-16 06:30 | 392 | 391
2018-01-16 07:00 | 417 | 416
2018-01-16 07:30 | 435 | 434
2018-01-16 08:00 | 441 | 441
2018-01-16 08:30 | 446 | 445
2018-01-16 09:00 | 436 | 435
2018-01-16 09:30 | 432 | 432
2018-01-16 10:00 | 421 | 420
2018-01-16 10:30 | 436 | 435
2018-01-16 11:00 | 447 | 446
2018-01-16 11:30 | 444 | 444
2018-01-16 12:00 | 439 | 438
2018-01-16 12:30 | 453 | 453
2018-01-16 13:00 | 469 | 469
2018-01-16 13:30 | 475 | 475
2018-01-16 14:00 | 476 | 476
2018-01-16 14:30 | 485 | 484
2018-01-16 15:00 | 489 | 489
2018-01-16 15:30 | 492 | 492
2018-01-16 16:00 | 492 | 492
2018-01-16 16:30 | 498 | 497
2018-01-16 17:00 | 510 | 510
2018-01-16 17:30 | 525 | 525
2018-01-16 18:00 | 511 | 510
2018-01-16 18:30 | 486 | 484
2018-01-16 19:00 | 481 | 480
2018-01-16 19:30 | 484 | 484
2018-01-16 20:00 | 482 | 482
2018-01-16 20:30 | 471 | 471
2018-01-16 21:00 | 451 | 451
2018-01-16 21:30 | 418 | 418
2018-01-16 22:00 | 405 | 404
2018-01-16 22:30 | 402 | 401
2018-01-16 23:00 | 402 | 400
2018-01-16 23:30 | 378 | 375
2018-01-17 | 350 | 346
2018-01-17 00:30 | 343 | 338
2018-01-17 01:00 | 339 | 333
2018-01-17 01:30 | 333 | 327
2018-01-17 02:00 | 334 | 331
2018-01-17 02:30 | 338 | 334
2018-01-17 03:00 | 337 | 332
2018-01-17 03:30 | 344 | 339
2018-01-17 04:00 | 348 | 343
2018-01-17 04:30 | 348 | 344
2018-01-17 05:00 | 354 | 350
2018-01-17 05:30 | 363 | 360
2018-01-17 06:00 | 367 | 365
2018-01-17 06:30 | 402 | 401
2018-01-17 07:00 | 427 | 427
2018-01-17 07:30 | 445 | 444
2018-01-17 08:00 | 450 | 449
2018-01-17 08:30 | 461 | 460
2018-01-17 09:00 | 459 | 458
2018-01-17 09:30 | 463 | 461
2018-01-17 10:00 | 464 | 463
2018-01-17 10:30 | 466 | 465
2018-01-17 11:00 | 470 | 469
2018-01-17 11:30 | 475 | 474
2018-01-17 12:00 | 475 | 474
2018-01-17 12:30 | 476 | 475
2018-01-17 13:00 | 484 | 483
2018-01-17 13:30 | 490 | 490
2018-01-17 14:00 | 502 | 502
2018-01-17 14:30 | 518 | 518
2018-01-17 15:00 | 529 | 528
2018-01-17 15:30 | 533 | 533
2018-01-17 16:00 | 545 | 545
2018-01-17 16:30 | 560 | 559
2018-01-17 17:00 | 564 | 563
2018-01-17 17:30 | 566 | 564
2018-01-17 18:00 | 555 | 552
2018-01-17 18:30 | 542 | 537
2018-01-17 19:00 | 534 | 531
2018-01-17 19:30 | 531 | 528
2018-01-17 20:00 | 528 | 526
2018-01-17 20:30 | 516 | 513
2018-01-17 21:00 | 486 | 485
2018-01-17 21:30 | 479 | 479
2018-01-17 22:00 | 449 | 448
2018-01-17 22:30 | 447 | 445
2018-01-17 23:00 | 440 | 438
2018-01-17 23:30 | 420 | 417
2018-01-18 | 393 | 388
2018-01-18 00:30 | 374 | 367
2018-01-18 01:00 | 358 | 351
2018-01-18 01:30 | 345 | 339
2018-01-18 02:00 | 344 | 340
2018-01-18 02:30 | 345 | 341
2018-01-18 03:00 | 337 | 333
2018-01-18 03:30 | 333 | 329
2018-01-18 04:00 | 336 | 332
2018-01-18 04:30 | 352 | 348
2018-01-18 05:00 | 364 | 360
2018-01-18 05:30 | 386 | 383
2018-01-18 06:00 | 382 | 380
2018-01-18 06:30 | 397 | 396
2018-01-18 07:00 | 423 | 422
2018-01-18 07:30 | 435 | 435
2018-01-18 08:00 | 474 | 474
2018-01-18 08:30 | 484 | 483
2018-01-18 09:00 | 486 | 486
2018-01-18 09:30 | 471 | 469
2018-01-18 10:00 | 473 | 472
2018-01-18 10:30 | 477 | 477
2018-01-18 11:00 | 491 | 490
2018-01-18 11:30 | 498 | 497
2018-01-18 12:00 | 501 | 500
2018-01-18 12:30 | 516 | 515
2018-01-18 13:00 | 526 | 526
2018-01-18 13:30 | 530 | 530
2018-01-18 14:00 | 543 | 542
2018-01-18 14:30 | 581 | 579
2018-01-18 15:00 | 598 | 596
2018-01-18 15:30 | 590 | 588
2018-01-18 16:00 | 617 | 615
2018-01-18 16:30 | 649 | 647
2018-01-18 17:00 | 668 | 665
2018-01-18 17:30 | 652 | 648
2018-01-18 18:00 | 635 | 631
2018-01-18 18:30 | 613 | 608
2018-01-18 19:00 | 614 | 609
2018-01-18 19:30 | 613 | 609
2018-01-18 20:00 | 605 | 602
2018-01-18 20:30 | 583 | 580
2018-01-18 21:00 | 547 | 543
2018-01-18 21:30 | 512 | 509
2018-01-18 22:00 | 483 | 480
2018-01-18 22:30 | 460 | 458
2018-01-18 23:00 | 440 | 438
2018-01-18 23:30 | 411 | 407
2018-01-19 | 382 | 377
2018-01-19 00:30 | 376 | 371
2018-01-19 01:00 | 365 | 360
2018-01-19 01:30 | 353 | 347
2018-01-19 02:00 | 352 | 346
2018-01-19 02:30 | 347 | 343
2018-01-19 03:00 | 339 | 335
2018-01-19 03:30 | 342 | 337
2018-01-19 04:00 | 348 | 343
2018-01-19 04:30 | 366 | 362
2018-01-19 05:00 | 378 | 374
2018-01-19 05:30 | 377 | 374
2018-01-19 06:00 | 407 | 404
2018-01-19 06:30 | 433 | 431
2018-01-19 07:00 | 451 | 450
2018-01-19 07:30 | 455 | 455
2018-01-19 08:00 | 474 | 473
2018-01-19 08:30 | 489 | 489
2018-01-19 09:00 | 499 | 497
2018-01-19 09:30 | 502 | 500
2018-01-19 10:00 | 501 | 499
2018-01-19 10:30 | 507 | 506
2018-01-19 11:00 | 509 | 508
2018-01-19 11:30 | 511 | 510
2018-01-19 12:00 | 537 | 536
2018-01-19 12:30 | 544 | 542
2018-01-19 13:00 | 548 | 546
2018-01-19 13:30 | 580 | 579
2018-01-19 14:00 | 596 | 595
2018-01-19 14:30 | 606 | 605
2018-01-19 15:00 | 612 | 611
2018-01-19 15:30 | 624 | 624
2018-01-19 16:00 | 640 | 639
2018-01-19 16:30 | 654 | 652
2018-01-19 17:00 | 661 | 658
2018-01-19 17:30 | 650 | 646
2018-01-19 18:00 | 634 | 631
2018-01-19 18:30 | 614 | 612
2018-01-19 19:00 | 604 | 603
2018-01-19 19:30 | 604 | 603
2018-01-19 20:00 | 598 | 597
2018-01-19 20:30 | 559 | 556
2018-01-19 21:00 | 505 | 503
2018-01-19 21:30 | 484 | 482
2018-01-19 22:00 | 476 | 473
2018-01-19 22:30 | 472 | 470
2018-01-19 23:00 | 454 | 452
2018-01-19 23:30 | 430 | 428
2018-01-20 | 416 | 414
2018-01-20 00:30 | 405 | 402
2018-01-20 01:00 | 386 | 384
2018-01-20 01:30 | 362 | 360
2018-01-20 02:00 | 351 | 348
2018-01-20 02:30 | 351 | 347
2018-01-20 03:00 | 346 | 341
2018-01-20 03:30 | 335 | 330
2018-01-20 04:00 | 325 | 321
2018-01-20 04:30 | 324 | 319
2018-01-20 05:00 | 326 | 321
2018-01-20 05:30 | 329 | 324
2018-01-20 06:00 | 340 | 335
2018-01-20 06:30 | 349 | 345
2018-01-20 07:00 | 357 | 354
2018-01-20 07:30 | 358 | 356
2018-01-20 08:00 | 358 | 358
2018-01-20 08:30 | 367 | 367
2018-01-20 09:00 | 380 | 380
2018-01-20 09:30 | 390 | 388
2018-01-20 10:00 | 407 | 405
2018-01-20 10:30 | 418 | 417
2018-01-20 11:00 | 430 | 430
2018-01-20 11:30 | 431 | 431
2018-01-20 12:00 | 439 | 438
2018-01-20 12:30 | 448 | 448
2018-01-20 13:00 | 463 | 463
2018-01-20 13:30 | 468 | 468
2018-01-20 14:00 | 472 | 472
2018-01-20 14:30 | 487 | 487
2018-01-20 15:00 | 500 | 499
2018-01-20 15:30 | 511 | 511
2018-01-20 16:00 | 523 | 523
2018-01-20 16:30 | 526 | 525
2018-01-20 17:00 | 538 | 537
2018-01-20 17:30 | 538 | 537
2018-01-20 18:00 | 532 | 531
2018-01-20 18:30 | 527 | 526
2018-01-20 19:00 | 527 | 525
2018-01-20 19:30 | 530 | 529
2018-01-20 20:00 | 532 | 531
2018-01-20 20:30 | 516 | 514
2018-01-20 21:00 | 491 | 489
2018-01-20 21:30 | 481 | 478
2018-01-20 22:00 | 473 | 469
2018-01-20 22:30 | 464 | 463
2018-01-20 23:00 | 450 | 449
2018-01-20 23:30 | 424 | 422
2018-01-21 | 408 | 405
2018-01-21 00:30 | 393 | 391
2018-01-21 01:00 | 387 | 384
2018-01-21 01:30 | 378 | 375
2018-01-21 02:00 | 363 | 359
2018-01-21 02:30 | 357 | 353
2018-01-21 03:00 | 360 | 356
2018-01-21 03:30 | 355 | 351
2018-01-21 04:00 | 354 | 350
2018-01-21 04:30 | 351 | 347
2018-01-21 05:00 | 351 | 346
2018-01-21 05:30 | 353 | 347
2018-01-21 06:00 | 364 | 358
2018-01-21 06:30 | 371 | 366
2018-01-21 07:00 | 374 | 369
2018-01-21 07:30 | 379 | 376
2018-01-21 08:00 | 386 | 385
2018-01-21 08:30 | 394 | 393
2018-01-21 09:00 | 419 | 419
2018-01-21 09:30 | 446 | 445
2018-01-21 10:00 | 462 | 462
2018-01-21 10:30 | 470 | 469
2018-01-21 11:00 | 467 | 465
2018-01-21 11:30 | 458 | 457
2018-01-21 12:00 | 464 | 463
2018-01-21 12:30 | 473 | 473
2018-01-21 13:00 | 484 | 483
2018-01-21 13:30 | 488 | 487
2018-01-21 14:00 | 493 | 492
2018-01-21 14:30 | 515 | 514
2018-01-21 15:00 | 546 | 544
2018-01-21 15:30 | 538 | 536
2018-01-21 16:00 | 551 | 549
2018-01-21 16:30 | 552 | 550
2018-01-21 17:00 | 551 | 550
2018-01-21 17:30 | 554 | 551
2018-01-21 18:00 | 563 | 560
2018-01-21 18:30 | 548 | 546
2018-01-21 19:00 | 558 | 556
2018-01-21 19:30 | 545 | 544
2018-01-21 20:00 | 542 | 540
2018-01-21 20:30 | 531 | 529
2018-01-21 21:00 | 499 | 498
2018-01-21 21:30 | 487 | 486
2018-01-21 22:00 | 473 | 470
2018-01-21 22:30 | 455 | 454
2018-01-21 23:00 | 441 | 441
2018-01-21 23:30 | 415 | 415
2018-01-22 | 395 | 394
2018-01-22 00:30 | 385 | 384
2018-01-22 01:00 | 374 | 372
2018-01-22 01:30 | 368 | 365
2018-01-22 02:00 | 368 | 366
2018-01-22 02:30 | 373 | 371
2018-01-22 03:00 | 375 | 372
2018-01-22 03:30 | 374 | 371
2018-01-22 04:00 | 366 | 363
2018-01-22 04:30 | 376 | 374
2018-01-22 05:00 | 396 | 394
2018-01-22 05:30 | 409 | 407
2018-01-22 06:00 | 433 | 432
2018-01-22 06:30 | 471 | 467
2018-01-22 07:00 | 503 | 498
2018-01-22 07:30 | 539 | 533
2018-01-22 08:00 | 561 | 554
2018-01-22 08:30 | 576 | 570
2018-01-22 09:00 | 586 | 582
2018-01-22 09:30 | 597 | 592
2018-01-22 10:00 | 602 | 597
2018-01-22 10:30 | 603 | 598
2018-01-22 11:00 | 610 | 606
2018-01-22 11:30 | 616 | 611
2018-01-22 12:00 | 624 | 618
2018-01-22 12:30 | 628 | 623
2018-01-22 13:00 | 636 | 631
2018-01-22 13:30 | 650 | 645
2018-01-22 14:00 | 662 | 657
2018-01-22 14:30 | 664 | 659
2018-01-22 15:00 | 672 | 667
2018-01-22 15:30 | 683 | 678
2018-01-22 16:00 | 701 | 695
2018-01-22 16:30 | 706 | 699
2018-01-22 17:00 | 706 | 699
2018-01-22 17:30 | 695 | 685
2018-01-22 18:00 | 673 | 663
2018-01-22 18:30 | 653 | 640
2018-01-22 19:00 | 649 | 638
2018-01-22 19:30 | 648 | 638
2018-01-22 20:00 | 631 | 625
2018-01-22 20:30 | 609 | 606
2018-01-22 21:00 | 576 | 574
2018-01-22 21:30 | 555 | 552
2018-01-22 22:00 | 529 | 525
2018-01-22 22:30 | 510 | 507
2018-01-22 23:00 | 474 | 471
2018-01-22 23:30 | 441 | 438
2018-01-23 | 426 | 421
2018-01-23 00:30 | 408 | 403
2018-01-23 01:00 | 400 | 393
2018-01-23 01:30 | 386 | 381
2018-01-23 02:00 | 378 | 372
2018-01-23 02:30 | 378 | 372
2018-01-23 03:00 | 375 | 369
2018-01-23 03:30 | 376 | 370
2018-01-23 04:00 | 375 | 369
2018-01-23 04:30 | 380 | 374
2018-01-23 05:00 | 385 | 380
2018-01-23 05:30 | 399 | 394
2018-01-23 06:00 | 416 | 413
2018-01-23 06:30 | 454 | 453
2018-01-23 07:00 | 501 | 500
2018-01-23 07:30 | 526 | 525
2018-01-23 08:00 | 547 | 542
2018-01-23 08:30 | 559 | 552
2018-01-23 09:00 | 569 | 562
2018-01-23 09:30 | 578 | 569
2018-01-23 10:00 | 587 | 580
2018-01-23 10:30 | 602 | 595
2018-01-23 11:00 | 605 | 599
2018-01-23 11:30 | 604 | 598
2018-01-23 12:00 | 611 | 606
2018-01-23 12:30 | 617 | 612
2018-01-23 13:00 | 623 | 619
2018-01-23 13:30 | 631 | 625
2018-01-23 14:00 | 645 | 639
2018-01-23 14:30 | 653 | 648
2018-01-23 15:00 | 658 | 653
2018-01-23 15:30 | 671 | 666
2018-01-23 16:00 | 693 | 689
2018-01-23 16:30 | 703 | 699
2018-01-23 17:00 | 706 | 702
2018-01-23 17:30 | 702 | 697
2018-01-23 18:00 | 693 | 686
2018-01-23 18:30 | 673 | 663
2018-01-23 19:00 | 661 | 656
2018-01-23 19:30 | 657 | 652
2018-01-23 20:00 | 646 | 641
2018-01-23 20:30 | 625 | 620
2018-01-23 21:00 | 595 | 589
2018-01-23 21:30 | 566 | 564
2018-01-23 22:00 | 544 | 541
2018-01-23 22:30 | 517 | 514
2018-01-23 23:00 | 486 | 483
2018-01-23 23:30 | 453 | 450
2018-01-24 | 426 | 423
2018-01-24 00:30 | 410 | 407
2018-01-24 01:00 | 403 | 399
2018-01-24 01:30 | 400 | 395
2018-01-24 02:00 | 391 | 386
2018-01-24 02:30 | 388 | 383
2018-01-24 03:00 | 387 | 382
2018-01-24 03:30 | 388 | 383
2018-01-24 04:00 | 388 | 383
2018-01-24 04:30 | 390 | 385
2018-01-24 05:00 | 396 | 392
2018-01-24 05:30 | 411 | 408
2018-01-24 06:00 | 428 | 425
2018-01-24 06:30 | 474 | 471
2018-01-24 07:00 | 510 | 508
2018-01-24 07:30 | 541 | 540
2018-01-24 08:00 | 558 | 558
2018-01-24 08:30 | 578 | 578
2018-01-24 09:00 | 594 | 594
2018-01-24 09:30 | 610 | 610
2018-01-24 10:00 | 623 | 623
2018-01-24 10:30 | 631 | 630
2018-01-24 11:00 | 638 | 637
2018-01-24 11:30 | 636 | 635
2018-01-24 12:00 | 636 | 636
2018-01-24 12:30 | 643 | 643
2018-01-24 13:00 | 659 | 659
2018-01-24 13:30 | 675 | 673
2018-01-24 14:00 | 687 | 683
2018-01-24 14:30 | 694 | 691
2018-01-24 15:00 | 705 | 702
2018-01-24 15:30 | 705 | 702
2018-01-24 16:00 | 722 | 718
2018-01-24 16:30 | 724 | 721
2018-01-24 17:00 | 731 | 728
2018-01-24 17:30 | 722 | 716
2018-01-24 18:00 | 717 | 709
2018-01-24 18:30 | 685 | 676
2018-01-24 19:00 | 685 | 678
2018-01-24 19:30 | 679 | 673
2018-01-24 20:00 | 667 | 660
2018-01-24 20:30 | 646 | 638
2018-01-24 21:00 | 611 | 605
2018-01-24 21:30 | 592 | 585
2018-01-24 22:00 | 569 | 560
2018-01-24 22:30 | 541 | 531
2018-01-24 23:00 | 509 | 501
2018-01-24 23:30 | 465 | 462
2018-01-25 | 437 | 433
2018-01-25 00:30 | 415 | 412
2018-01-25 01:00 | 401 | 400
2018-01-25 01:30 | 389 | 387
2018-01-25 02:00 | 375 | 373
2018-01-25 02:30 | 373 | 372
2018-01-25 03:00 | 372 | 370
2018-01-25 03:30 | 374 | 372
2018-01-25 04:00 | 381 | 379
2018-01-25 04:30 | 384 | 382
2018-01-25 05:00 | 397 | 395
2018-01-25 05:30 | 406 | 405
2018-01-25 06:00 | 421 | 419
2018-01-25 06:30 | 468 | 467
2018-01-25 07:00 | 527 | 525
2018-01-25 07:30 | 570 | 569
2018-01-25 08:00 | 591 | 590
2018-01-25 08:30 | 592 | 592
2018-01-25 09:00 | 598 | 597
2018-01-25 09:30 | 617 | 613
2018-01-25 10:00 | 628 | 625
2018-01-25 10:30 | 635 | 632
2018-01-25 11:00 | 634 | 631
2018-01-25 11:30 | 647 | 644
2018-01-25 12:00 | 660 | 658
2018-01-25 12:30 | 656 | 653
2018-01-25 13:00 | 660 | 658
2018-01-25 13:30 | 670 | 667
2018-01-25 14:00 | 674 | 668
2018-01-25 14:30 | 697 | 692
2018-01-25 15:00 | 697 | 691
2018-01-25 15:30 | 698 | 692
2018-01-25 16:00 | 708 | 702
2018-01-25 16:30 | 684 | 679
2018-01-25 17:00 | 696 | 691
2018-01-25 17:30 | 698 | 691
2018-01-25 18:00 | 685 | 678
2018-01-25 18:30 | 660 | 651
2018-01-25 19:00 | 657 | 651
2018-01-25 19:30 | 660 | 655
2018-01-25 20:00 | 655 | 650
2018-01-25 20:30 | 640 | 634
2018-01-25 21:00 | 600 | 595
2018-01-25 21:30 | 582 | 577
2018-01-25 22:00 | 565 | 560
2018-01-25 22:30 | 543 | 537
2018-01-25 23:00 | 511 | 510
2018-01-25 23:30 | 478 | 477
2018-01-26 | 454 | 453
2018-01-26 00:30 | 427 | 426
2018-01-26 01:00 | 415 | 414
2018-01-26 01:30 | 401 | 400
2018-01-26 02:00 | 391 | 390
2018-01-26 02:30 | 384 | 383
2018-01-26 03:00 | 380 | 379
2018-01-26 03:30 | 378 | 376
2018-01-26 04:00 | 378 | 376
2018-01-26 04:30 | 380 | 378
2018-01-26 05:00 | 380 | 378
2018-01-26 05:30 | 381 | 378
2018-01-26 06:00 | 393 | 390
2018-01-26 06:30 | 411 | 409
2018-01-26 07:00 | 421 | 420
2018-01-26 07:30 | 442 | 441
2018-01-26 08:00 | 465 | 464
2018-01-26 08:30 | 478 | 477
2018-01-26 09:00 | 501 | 500
2018-01-26 09:30 | 520 | 519
2018-01-26 10:00 | 538 | 537
2018-01-26 10:30 | 554 | 553
2018-01-26 11:00 | 550 | 549
2018-01-26 11:30 | 546 | 545
2018-01-26 12:00 | 560 | 560
2018-01-26 12:30 | 570 | 569
2018-01-26 13:00 | 572 | 572
2018-01-26 13:30 | 577 | 576
2018-01-26 14:00 | 594 | 593
2018-01-26 14:30 | 603 | 602
2018-01-26 15:00 | 607 | 606
2018-01-26 15:30 | 610 | 610
2018-01-26 16:00 | 621 | 620
2018-01-26 16:30 | 634 | 632
2018-01-26 17:00 | 645 | 641
2018-01-26 17:30 | 639 | 635
2018-01-26 18:00 | 637 | 632
2018-01-26 18:30 | 632 | 625
2018-01-26 19:00 | 626 | 619
2018-01-26 19:30 | 619 | 615
2018-01-26 20:00 | 623 | 619
2018-01-26 20:30 | 605 | 602
2018-01-26 21:00 | 587 | 584
2018-01-26 21:30 | 573 | 573
2018-01-26 22:00 | 563 | 562
2018-01-26 22:30 | 554 | 553
2018-01-26 23:00 | 532 | 532
2018-01-26 23:30 | 506 | 506
2018-01-27 | 466 | 465
2018-01-27 00:30 | 428 | 428
2018-01-27 01:00 | 414 | 414
2018-01-27 01:30 | 403 | 402
2018-01-27 02:00 | 392 | 392
2018-01-27 02:30 | 388 | 388
2018-01-27 03:00 | 385 | 385
2018-01-27 03:30 | 381 | 381
2018-01-27 04:00 | 379 | 378
2018-01-27 04:30 | 376 | 376
2018-01-27 05:00 | 385 | 385
2018-01-27 05:30 | 391 | 390
2018-01-27 06:00 | 399 | 398
2018-01-27 06:30 | 418 | 418
2018-01-27 07:00 | 427 | 426
2018-01-27 07:30 | 440 | 439
2018-01-27 08:00 | 459 | 458
2018-01-27 08:30 | 477 | 477
2018-01-27 09:00 | 507 | 507
2018-01-27 09:30 | 552 | 551
2018-01-27 10:00 | 556 | 555
2018-01-27 10:30 | 563 | 562
2018-01-27 11:00 | 564 | 564
2018-01-27 11:30 | 567 | 566
2018-01-27 12:00 | 570 | 569
2018-01-27 12:30 | 572 | 572
2018-01-27 13:00 | 582 | 581
2018-01-27 13:30 | 590 | 590
2018-01-27 14:00 | 603 | 602
2018-01-27 14:30 | 605 | 603
2018-01-27 15:00 | 616 | 615
2018-01-27 15:30 | 624 | 623
2018-01-27 16:00 | 635 | 633
2018-01-27 16:30 | 652 | 650
2018-01-27 17:00 | 662 | 659
2018-01-27 17:30 | 653 | 649
2018-01-27 18:00 | 638 | 631
2018-01-27 18:30 | 620 | 613
2018-01-27 19:00 | 613 | 609
2018-01-27 19:30 | 608 | 605
2018-01-27 20:00 | 590 | 589
2018-01-27 20:30 | 572 | 571
2018-01-27 21:00 | 544 | 543
2018-01-27 21:30 | 515 | 515
2018-01-27 22:00 | 502 | 501
2018-01-27 22:30 | 506 | 504
2018-01-27 23:00 | 491 | 490
2018-01-27 23:30 | 455 | 454
2018-01-28 | 434 | 434
2018-01-28 00:30 | 414 | 414
2018-01-28 01:00 | 404 | 404
2018-01-28 01:30 | 394 | 393
2018-01-28 02:00 | 380 | 379
2018-01-28 02:30 | 367 | 366
2018-01-28 03:00 | 367 | 367
2018-01-28 03:30 | 366 | 366
2018-01-28 04:00 | 365 | 364
2018-01-28 04:30 | 366 | 365
2018-01-28 05:00 | 366 | 365
2018-01-28 05:30 | 368 | 367
2018-01-28 06:00 | 376 | 374
2018-01-28 06:30 | 390 | 389
2018-01-28 07:00 | 397 | 395
2018-01-28 07:30 | 413 | 412
2018-01-28 08:00 | 425 | 424
2018-01-28 08:30 | 452 | 451
2018-01-28 09:00 | 463 | 463
2018-01-28 09:30 | 467 | 466
2018-01-28 10:00 | 471 | 470
2018-01-28 10:30 | 468 | 467
2018-01-28 11:00 | 488 | 488
2018-01-28 11:30 | 499 | 497
2018-01-28 12:00 | 488 | 486
2018-01-28 12:30 | 515 | 513
2018-01-28 13:00 | 522 | 520
2018-01-28 13:30 | 541 | 540
2018-01-28 14:00 | 532 | 530
2018-01-28 14:30 | 520 | 518
2018-01-28 15:00 | 520 | 519
2018-01-28 15:30 | 527 | 526
2018-01-28 16:00 | 544 | 543
2018-01-28 16:30 | 557 | 556
2018-01-28 17:00 | 573 | 572
2018-01-28 17:30 | 575 | 573
2018-01-28 18:00 | 569 | 567
2018-01-28 18:30 | 583 | 581
2018-01-28 19:00 | 581 | 579
2018-01-28 19:30 | 577 | 574
2018-01-28 20:00 | 576 | 574
2018-01-28 20:30 | 562 | 559
2018-01-28 21:00 | 526 | 526
2018-01-28 21:30 | 511 | 510
2018-01-28 22:00 | 506 | 505
2018-01-28 22:30 | 487 | 486
2018-01-28 23:00 | 457 | 457
2018-01-28 23:30 | 432 | 431
2018-01-29 | 410 | 408
2018-01-29 00:30 | 394 | 393
2018-01-29 01:00 | 384 | 383
2018-01-29 01:30 | 380 | 377
2018-01-29 02:00 | 372 | 369
2018-01-29 02:30 | 367 | 364
2018-01-29 03:00 | 365 | 362
2018-01-29 03:30 | 362 | 360
2018-01-29 04:00 | 359 | 357
2018-01-29 04:30 | 370 | 368
2018-01-29 05:00 | 383 | 381
2018-01-29 05:30 | 402 | 401
2018-01-29 06:00 | 422 | 421
2018-01-29 06:30 | 457 | 457
2018-01-29 07:00 | 508 | 508
2018-01-29 07:30 | 554 | 554
2018-01-29 08:00 | 580 | 580
2018-01-29 08:30 | 587 | 587
2018-01-29 09:00 | 597 | 597
2018-01-29 09:30 | 599 | 599
2018-01-29 10:00 | 598 | 597
2018-01-29 10:30 | 604 | 603
2018-01-29 11:00 | 610 | 610
2018-01-29 11:30 | 596 | 596
2018-01-29 12:00 | 609 | 609
2018-01-29 12:30 | 617 | 616
2018-01-29 13:00 | 624 | 623
2018-01-29 13:30 | 629 | 629
2018-01-29 14:00 | 628 | 628
2018-01-29 14:30 | 632 | 632
2018-01-29 15:00 | 643 | 642
2018-01-29 15:30 | 647 | 644
2018-01-29 16:00 | 657 | 654
2018-01-29 16:30 | 668 | 665
2018-01-29 17:00 | 674 | 671
2018-01-29 17:30 | 662 | 657
2018-01-29 18:00 | 654 | 646
2018-01-29 18:30 | 630 | 622
2018-01-29 19:00 | 621 | 616
2018-01-29 19:30 | 614 | 609
2018-01-29 20:00 | 600 | 599
2018-01-29 20:30 | 577 | 576
2018-01-29 21:00 | 543 | 543
2018-01-29 21:30 | 520 | 520
2018-01-29 22:00 | 504 | 504
2018-01-29 22:30 | 484 | 483
2018-01-29 23:00 | 459 | 459
2018-01-29 23:30 | 437 | 437
2018-01-30 | 415 | 414
2018-01-30 00:30 | 395 | 394
2018-01-30 01:00 | 389 | 388
2018-01-30 01:30 | 377 | 377
2018-01-30 02:00 | 368 | 367
2018-01-30 02:30 | 367 | 366
2018-01-30 03:00 | 363 | 362
2018-01-30 03:30 | 364 | 362
2018-01-30 04:00 | 372 | 371
2018-01-30 04:30 | 381 | 380
2018-01-30 05:00 | 390 | 389
2018-01-30 05:30 | 407 | 406
2018-01-30 06:00 | 436 | 434
2018-01-30 06:30 | 479 | 479
2018-01-30 07:00 | 525 | 524
2018-01-30 07:30 | 553 | 553
2018-01-30 08:00 | 571 | 571
2018-01-30 08:30 | 578 | 577
2018-01-30 09:00 | 577 | 577
2018-01-30 09:30 | 582 | 582
2018-01-30 10:00 | 597 | 595
2018-01-30 10:30 | 594 | 592
2018-01-30 11:00 | 589 | 587
2018-01-30 11:30 | 595 | 593
2018-01-30 12:00 | 605 | 603
2018-01-30 12:30 | 612 | 610
2018-01-30 13:00 | 601 | 600
2018-01-30 13:30 | 617 | 616
2018-01-30 14:00 | 639 | 637
2018-01-30 14:30 | 656 | 654
2018-01-30 15:00 | 664 | 662
2018-01-30 15:30 | 688 | 686
2018-01-30 16:00 | 715 | 708
2018-01-30 16:30 | 725 | 717
2018-01-30 17:00 | 719 | 709
2018-01-30 17:30 | 700 | 690
2018-01-30 18:00 | 677 | 668
2018-01-30 18:30 | 662 | 651
2018-01-30 19:00 | 665 | 657
2018-01-30 19:30 | 670 | 663
2018-01-30 20:00 | 662 | 655
2018-01-30 20:30 | 637 | 632
2018-01-30 21:00 | 601 | 598
2018-01-30 21:30 | 578 | 575
2018-01-30 22:00 | 544 | 540
2018-01-30 22:30 | 521 | 516
2018-01-30 23:00 | 480 | 477
2018-01-30 23:30 | 447 | 446
2018-01-31 | 427 | 426
2018-01-31 00:30 | 399 | 398
2018-01-31 01:00 | 381 | 381
2018-01-31 01:30 | 366 | 365
2018-01-31 02:00 | 364 | 363
2018-01-31 02:30 | 369 | 368
2018-01-31 03:00 | 375 | 374
2018-01-31 03:30 | 370 | 368
2018-01-31 04:00 | 353 | 352
2018-01-31 04:30 | 358 | 357
2018-01-31 05:00 | 370 | 369
2018-01-31 05:30 | 377 | 376
2018-01-31 06:00 | 412 | 411
2018-01-31 06:30 | 476 | 475
2018-01-31 07:00 | 518 | 518
2018-01-31 07:30 | 549 | 549
2018-01-31 08:00 | 549 | 549
2018-01-31 08:30 | 567 | 567
2018-01-31 09:00 | 564 | 563
2018-01-31 09:30 | 579 | 578
2018-01-31 10:00 | 592 | 591
2018-01-31 10:30 | 583 | 582
2018-01-31 11:00 | 597 | 597
2018-01-31 11:30 | 619 | 618
2018-01-31 12:00 | 636 | 636
2018-01-31 12:30 | 641 | 640
2018-01-31 13:00 | 647 | 646
2018-01-31 13:30 | 661 | 660
2018-01-31 14:00 | 670 | 670
2018-01-31 14:30 | 678 | 678
2018-01-31 15:00 | 677 | 677
2018-01-31 15:30 | 689 | 689
2018-01-31 16:00 | 704 | 704
2018-01-31 16:30 | 719 | 719
2018-01-31 17:00 | 720 | 720
2018-01-31 17:30 | 693 | 692
2018-01-31 18:00 | 658 | 658
2018-01-31 18:30 | 637 | 637
2018-01-31 19:00 | 643 | 643
2018-01-31 19:30 | 620 | 619
2018-01-31 20:00 | 609 | 609
2018-01-31 20:30 | 584 | 584
2018-01-31 21:00 | 551 | 551
2018-01-31 21:30 | 526 | 526
2018-01-31 22:00 | 504 | 504
2018-01-31 22:30 | 481 | 481
2018-01-31 23:00 | 457 | 457
2018-01-31 23:30 | 428 | 428
2018-02-01 | 405 | 405
2018-02-01 00:30 | 379 | 379
2018-02-01 01:00 | 365 | 365
2018-02-01 01:30 | 356 | 356
2018-02-01 02:00 | 350 | 350
2018-02-01 02:30 | 346 | 346
2018-02-01 03:00 | 350 | 349
2018-02-01 03:30 | 352 | 352
2018-02-01 04:00 | 350 | 349
2018-02-01 04:30 | 357 | 356
2018-02-01 05:00 | 367 | 367
2018-02-01 05:30 | 395 | 395
2018-02-01 06:00 | 417 | 417
2018-02-01 06:30 | 463 | 463
2018-02-01 07:00 | 497 | 497
2018-02-01 07:30 | 522 | 521
2018-02-01 08:00 | 527 | 526
2018-02-01 08:30 | 524 | 524
2018-02-01 09:00 | 516 | 515
2018-02-01 09:30 | 512 | 512
2018-02-01 10:00 | 515 | 515
2018-02-01 10:30 | 502 | 502
2018-02-01 11:00 | 486 | 485
2018-02-01 11:30 | 509 | 509
2018-02-01 12:00 | 514 | 514
2018-02-01 12:30 | 500 | 499
2018-02-01 13:00 | 486 | 485
2018-02-01 13:30 | 493 | 491
2018-02-01 14:00 | 512 | 512
2018-02-01 14:30 | 503 | 502
2018-02-01 15:00 | 502 | 501
2018-02-01 15:30 | 498 | 497
2018-02-01 16:00 | 502 | 500
2018-02-01 16:30 | 506 | 504
2018-02-01 17:00 | 512 | 509
2018-02-01 17:30 | 521 | 519
2018-02-01 18:00 | 516 | 514
2018-02-01 18:30 | 508 | 505
2018-02-01 19:00 | 515 | 513
2018-02-01 19:30 | 516 | 514
2018-02-01 20:00 | 518 | 517
2018-02-01 20:30 | 507 | 507
2018-02-01 21:00 | 473 | 473
2018-02-01 21:30 | 442 | 441
2018-02-01 22:00 | 436 | 435
2018-02-01 22:30 | 433 | 431
2018-02-01 23:00 | 411 | 409
2018-02-01 23:30 | 397 | 395
2018-02-02 | 379 | 376
2018-02-02 00:30 | 367 | 364
2018-02-02 01:00 | 364 | 361
2018-02-02 01:30 | 348 | 344
2018-02-02 02:00 | 331 | 327
2018-02-02 02:30 | 329 | 325
2018-02-02 03:00 | 335 | 330
2018-02-02 03:30 | 335 | 331
2018-02-02 04:00 | 336 | 331
2018-02-02 04:30 | 344 | 340
2018-02-02 05:00 | 353 | 349
2018-02-02 05:30 | 373 | 371
2018-02-02 06:00 | 399 | 397
2018-02-02 06:30 | 447 | 446
2018-02-02 07:00 | 486 | 486
2018-02-02 07:30 | 511 | 511
2018-02-02 08:00 | 518 | 518
2018-02-02 08:30 | 517 | 517
2018-02-02 09:00 | 513 | 513
2018-02-02 09:30 | 521 | 521
2018-02-02 10:00 | 516 | 516
2018-02-02 10:30 | 508 | 508
2018-02-02 11:00 | 509 | 509
2018-02-02 11:30 | 494 | 494
2018-02-02 12:00 | 479 | 479
2018-02-02 12:30 | 488 | 488
2018-02-02 13:00 | 489 | 489
2018-02-02 13:30 | 479 | 479
2018-02-02 14:00 | 480 | 480
2018-02-02 14:30 | 479 | 479
2018-02-02 15:00 | 479 | 478
2018-02-02 15:30 | 473 | 473
2018-02-02 16:00 | 486 | 485
2018-02-02 16:30 | 487 | 487
2018-02-02 17:00 | 494 | 493
2018-02-02 17:30 | 482 | 481
2018-02-02 18:00 | 470 | 469
2018-02-02 18:30 | 460 | 458
2018-02-02 19:00 | 467 | 467
2018-02-02 19:30 | 473 | 472
2018-02-02 20:00 | 469 | 468
2018-02-02 20:30 | 455 | 455
2018-02-02 21:00 | 433 | 433
2018-02-02 21:30 | 436 | 435
2018-02-02 22:00 | 424 | 423
2018-02-02 22:30 | 423 | 422
2018-02-02 23:00 | 413 | 412
2018-02-02 23:30 | 391 | 389
2018-02-03 | 375 | 372
2018-02-03 00:30 | 350 | 346
2018-02-03 01:00 | 341 | 337
2018-02-03 01:30 | 331 | 327
2018-02-03 02:00 | 320 | 316
2018-02-03 02:30 | 317 | 312
2018-02-03 03:00 | 315 | 310
2018-02-03 03:30 | 314 | 309
2018-02-03 04:00 | 316 | 311
2018-02-03 04:30 | 325 | 320
2018-02-03 05:00 | 332 | 327
2018-02-03 05:30 | 338 | 333
2018-02-03 06:00 | 340 | 335
2018-02-03 06:30 | 349 | 344
2018-02-03 07:00 | 360 | 357
2018-02-03 07:30 | 386 | 384
2018-02-03 08:00 | 403 | 401
2018-02-03 08:30 | 416 | 415
2018-02-03 09:00 | 432 | 431
2018-02-03 09:30 | 442 | 441
2018-02-03 10:00 | 446 | 444
2018-02-03 10:30 | 441 | 439
2018-02-03 11:00 | 445 | 443
2018-02-03 11:30 | 434 | 431
2018-02-03 12:00 | 434 | 432
2018-02-03 12:30 | 428 | 426
2018-02-03 13:00 | 428 | 425
2018-02-03 13:30 | 435 | 433
2018-02-03 14:00 | 432 | 430
2018-02-03 14:30 | 426 | 423
2018-02-03 15:00 | 429 | 426
2018-02-03 15:30 | 431 | 428
2018-02-03 16:00 | 430 | 427
2018-02-03 16:30 | 426 | 423
2018-02-03 17:00 | 429 | 426
2018-02-03 17:30 | 436 | 433
2018-02-03 18:00 | 438 | 434
2018-02-03 18:30 | 444 | 440
2018-02-03 19:00 | 452 | 449
2018-02-03 19:30 | 459 | 457
2018-02-03 20:00 | 457 | 455
2018-02-03 20:30 | 448 | 445
2018-02-03 21:00 | 428 | 425
2018-02-03 21:30 | 420 | 417
2018-02-03 22:00 | 424 | 422
2018-02-03 22:30 | 418 | 415
2018-02-03 23:00 | 397 | 394
2018-02-03 23:30 | 378 | 375
2018-02-04 | 354 | 350
2018-02-04 00:30 | 345 | 340
2018-02-04 01:00 | 337 | 331
2018-02-04 01:30 | 328 | 322
2018-02-04 02:00 | 319 | 313
2018-02-04 02:30 | 318 | 311
2018-02-04 03:00 | 317 | 310
2018-02-04 03:30 | 317 | 310
2018-02-04 04:00 | 314 | 309
2018-02-04 04:30 | 318 | 313
2018-02-04 05:00 | 324 | 318
2018-02-04 05:30 | 327 | 321
2018-02-04 06:00 | 331 | 325
2018-02-04 06:30 | 333 | 327
2018-02-04 07:00 | 340 | 335
2018-02-04 07:30 | 358 | 353
2018-02-04 08:00 | 364 | 360
2018-02-04 08:30 | 366 | 364
2018-02-04 09:00 | 375 | 373
2018-02-04 09:30 | 375 | 374
2018-02-04 10:00 | 372 | 371
2018-02-04 10:30 | 376 | 375
2018-02-04 11:00 | 377 | 377
2018-02-04 11:30 | 384 | 384
2018-02-04 12:00 | 374 | 374
2018-02-04 12:30 | 375 | 375
2018-02-04 13:00 | 374 | 374
2018-02-04 13:30 | 381 | 380
2018-02-04 14:00 | 364 | 364
2018-02-04 14:30 | 369 | 369
2018-02-04 15:00 | 387 | 386
2018-02-04 15:30 | 400 | 400
2018-02-04 16:00 | 420 | 420
2018-02-04 16:30 | 447 | 447
2018-02-04 17:00 | 475 | 474
2018-02-04 17:30 | 490 | 489
2018-02-04 18:00 | 494 | 493
2018-02-04 18:30 | 495 | 494
2018-02-04 19:00 | 502 | 501
2018-02-04 19:30 | 506 | 505
2018-02-04 20:00 | 505 | 505
2018-02-04 20:30 | 498 | 497
2018-02-04 21:00 | 482 | 481
2018-02-04 21:30 | 465 | 464
2018-02-04 22:00 | 450 | 449
2018-02-04 22:30 | 428 | 428
2018-02-04 23:00 | 405 | 404
2018-02-04 23:30 | 383 | 382
2018-02-05 | 363 | 361
2018-02-05 00:30 | 350 | 348
2018-02-05 01:00 | 347 | 343
2018-02-05 01:30 | 345 | 341
2018-02-05 02:00 | 337 | 333
2018-02-05 02:30 | 328 | 324
2018-02-05 03:00 | 326 | 322
2018-02-05 03:30 | 329 | 325
2018-02-05 04:00 | 334 | 330
2018-02-05 04:30 | 349 | 345
2018-02-05 05:00 | 364 | 361
2018-02-05 05:30 | 387 | 384
2018-02-05 06:00 | 411 | 409
2018-02-05 06:30 | 440 | 440
2018-02-05 07:00 | 469 | 469
2018-02-05 07:30 | 485 | 485
2018-02-05 08:00 | 480 | 480
2018-02-05 08:30 | 485 | 485
2018-02-05 09:00 | 491 | 491
2018-02-05 09:30 | 501 | 501
2018-02-05 10:00 | 498 | 498
2018-02-05 10:30 | 497 | 497
2018-02-05 11:00 | 495 | 495
2018-02-05 11:30 | 490 | 490
2018-02-05 12:00 | 488 | 488
2018-02-05 12:30 | 494 | 493
2018-02-05 13:00 | 507 | 507
2018-02-05 13:30 | 518 | 518
2018-02-05 14:00 | 527 | 527
2018-02-05 14:30 | 530 | 530
2018-02-05 15:00 | 538 | 538
2018-02-05 15:30 | 557 | 557
2018-02-05 16:00 | 563 | 563
2018-02-05 16:30 | 572 | 572
2018-02-05 17:00 | 571 | 571
2018-02-05 17:30 | 559 | 559
2018-02-05 18:00 | 550 | 548
2018-02-05 18:30 | 535 | 534
2018-02-05 19:00 | 546 | 545
2018-02-05 19:30 | 543 | 542
2018-02-05 20:00 | 531 | 530
2018-02-05 20:30 | 512 | 511
2018-02-05 21:00 | 490 | 490
2018-02-05 21:30 | 468 | 468
2018-02-05 22:00 | 452 | 452
2018-02-05 22:30 | 448 | 447
2018-02-05 23:00 | 427 | 426
2018-02-05 23:30 | 412 | 411
2018-02-06 | 396 | 395
2018-02-06 00:30 | 386 | 383
2018-02-06 01:00 | 379 | 376
2018-02-06 01:30 | 367 | 364
2018-02-06 02:00 | 359 | 354
2018-02-06 02:30 | 361 | 356
2018-02-06 03:00 | 353 | 348
2018-02-06 03:30 | 345 | 339
2018-02-06 04:00 | 354 | 349
2018-02-06 04:30 | 363 | 359
2018-02-06 05:00 | 368 | 364
2018-02-06 05:30 | 378 | 375
2018-02-06 06:00 | 385 | 383
2018-02-06 06:30 | 420 | 420
2018-02-06 07:00 | 455 | 455
2018-02-06 07:30 | 470 | 470
2018-02-06 08:00 | 469 | 469
2018-02-06 08:30 | 470 | 469
2018-02-06 09:00 | 470 | 470
2018-02-06 09:30 | 482 | 482
2018-02-06 10:00 | 489 | 489
2018-02-06 10:30 | 477 | 477
2018-02-06 11:00 | 483 | 483
2018-02-06 11:30 | 492 | 492
2018-02-06 12:00 | 488 | 488
2018-02-06 12:30 | 489 | 489
2018-02-06 13:00 | 502 | 502
2018-02-06 13:30 | 511 | 511
2018-02-06 14:00 | 514 | 514
2018-02-06 14:30 | 518 | 518
2018-02-06 15:00 | 538 | 538
2018-02-06 15:30 | 559 | 559
2018-02-06 16:00 | 571 | 571
2018-02-06 16:30 | 565 | 565
2018-02-06 17:00 | 557 | 557
2018-02-06 17:30 | 555 | 555
2018-02-06 18:00 | 543 | 542
2018-02-06 18:30 | 520 | 519
2018-02-06 19:00 | 524 | 523
2018-02-06 19:30 | 531 | 531
2018-02-06 20:00 | 525 | 525
2018-02-06 20:30 | 511 | 511
2018-02-06 21:00 | 488 | 488
2018-02-06 21:30 | 466 | 466
2018-02-06 22:00 | 455 | 455
2018-02-06 22:30 | 449 | 449
2018-02-06 23:00 | 436 | 436
2018-02-06 23:30 | 419 | 418
2018-02-07 | 402 | 401
2018-02-07 00:30 | 387 | 385
2018-02-07 01:00 | 379 | 376
2018-02-07 01:30 | 368 | 363
2018-02-07 02:00 | 357 | 352
2018-02-07 02:30 | 350 | 345
2018-02-07 03:00 | 349 | 344
2018-02-07 03:30 | 350 | 344
2018-02-07 04:00 | 352 | 346
2018-02-07 04:30 | 366 | 361
2018-02-07 05:00 | 380 | 375
2018-02-07 05:30 | 394 | 390
2018-02-07 06:00 | 410 | 407
2018-02-07 06:30 | 437 | 436
2018-02-07 07:00 | 466 | 466
2018-02-07 07:30 | 478 | 478
2018-02-07 08:00 | 484 | 481
2018-02-07 08:30 | 489 | 487
2018-02-07 09:00 | 489 | 487
2018-02-07 09:30 | 493 | 490
2018-02-07 10:00 | 495 | 490
2018-02-07 10:30 | 501 | 496
2018-02-07 11:00 | 496 | 491
2018-02-07 11:30 | 492 | 487
2018-02-07 12:00 | 485 | 481
2018-02-07 12:30 | 484 | 480
2018-02-07 13:00 | 508 | 504
2018-02-07 13:30 | 507 | 502
2018-02-07 14:00 | 494 | 489
2018-02-07 14:30 | 511 | 506
2018-02-07 15:00 | 522 | 518
2018-02-07 15:30 | 524 | 520
2018-02-07 16:00 | 543 | 538
2018-02-07 16:30 | 576 | 572
2018-02-07 17:00 | 583 | 580
2018-02-07 17:30 | 583 | 578
2018-02-07 18:00 | 559 | 558
2018-02-07 18:30 | 556 | 554
2018-02-07 19:00 | 557 | 555
2018-02-07 19:30 | 553 | 552
2018-02-07 20:00 | 539 | 538
2018-02-07 20:30 | 519 | 519
2018-02-07 21:00 | 493 | 493
2018-02-07 21:30 | 468 | 468
2018-02-07 22:00 | 451 | 451
2018-02-07 22:30 | 450 | 450
2018-02-07 23:00 | 427 | 427
2018-02-07 23:30 | 406 | 406
2018-02-08 | 380 | 379
2018-02-08 00:30 | 364 | 363
2018-02-08 01:00 | 356 | 355
2018-02-08 01:30 | 346 | 345
2018-02-08 02:00 | 343 | 341
2018-02-08 02:30 | 339 | 337
2018-02-08 03:00 | 334 | 332
2018-02-08 03:30 | 334 | 332
2018-02-08 04:00 | 337 | 335
2018-02-08 04:30 | 343 | 341
2018-02-08 05:00 | 362 | 361
2018-02-08 05:30 | 376 | 375
2018-02-08 06:00 | 396 | 395
2018-02-08 06:30 | 428 | 426
2018-02-08 07:00 | 455 | 452
2018-02-08 07:30 | 465 | 462
2018-02-08 08:00 | 469 | 467
2018-02-08 08:30 | 470 | 468
2018-02-08 09:00 | 475 | 473
2018-02-08 09:30 | 498 | 496
2018-02-08 10:00 | 508 | 506
2018-02-08 10:30 | 507 | 505
2018-02-08 11:00 | 508 | 506
2018-02-08 11:30 | 509 | 506
2018-02-08 12:00 | 516 | 513
2018-02-08 12:30 | 510 | 507
2018-02-08 13:00 | 505 | 505
2018-02-08 13:30 | 520 | 520
2018-02-08 14:00 | 518 | 518
2018-02-08 14:30 | 543 | 543
2018-02-08 15:00 | 579 | 579
2018-02-08 15:30 | 599 | 599
2018-02-08 16:00 | 623 | 622
2018-02-08 16:30 | 626 | 625
2018-02-08 17:00 | 641 | 640
2018-02-08 17:30 | 637 | 637
2018-02-08 18:00 | 634 | 633
2018-02-08 18:30 | 623 | 621
2018-02-08 19:00 | 613 | 613
2018-02-08 19:30 | 608 | 608
2018-02-08 20:00 | 609 | 609
2018-02-08 20:30 | 608 | 607
2018-02-08 21:00 | 578 | 577
2018-02-08 21:30 | 547 | 546
2018-02-08 22:00 | 508 | 508
2018-02-08 22:30 | 485 | 484
2018-02-08 23:00 | 459 | 458
2018-02-08 23:30 | 436 | 434
2018-02-09 | 414 | 411
2018-02-09 00:30 | 400 | 398
2018-02-09 01:00 | 395 | 393
2018-02-09 01:30 | 385 | 382
2018-02-09 02:00 | 383 | 380
2018-02-09 02:30 | 377 | 374
2018-02-09 03:00 | 384 | 381
2018-02-09 03:30 | 383 | 379
2018-02-09 04:00 | 382 | 379
2018-02-09 04:30 | 381 | 378
2018-02-09 05:00 | 380 | 378
2018-02-09 05:30 | 401 | 399
2018-02-09 06:00 | 426 | 424
2018-02-09 06:30 | 469 | 468
2018-02-09 07:00 | 493 | 492
2018-02-09 07:30 | 519 | 518
2018-02-09 08:00 | 532 | 532
2018-02-09 08:30 | 541 | 541
2018-02-09 09:00 | 544 | 543
2018-02-09 09:30 | 550 | 550
2018-02-09 10:00 | 558 | 558
2018-02-09 10:30 | 561 | 560
2018-02-09 11:00 | 554 | 553
2018-02-09 11:30 | 544 | 544
2018-02-09 12:00 | 544 | 544
2018-02-09 12:30 | 550 | 550
2018-02-09 13:00 | 560 | 559
2018-02-09 13:30 | 573 | 573
2018-02-09 14:00 | 584 | 584
2018-02-09 14:30 | 586 | 586
2018-02-09 15:00 | 593 | 593
2018-02-09 15:30 | 606 | 606
2018-02-09 16:00 | 632 | 632
2018-02-09 16:30 | 639 | 639
2018-02-09 17:00 | 647 | 647
2018-02-09 17:30 | 639 | 639
2018-02-09 18:00 | 608 | 607
2018-02-09 18:30 | 589 | 587
2018-02-09 19:00 | 581 | 580
2018-02-09 19:30 | 572 | 571
2018-02-09 20:00 | 553 | 552
2018-02-09 20:30 | 534 | 533
2018-02-09 21:00 | 504 | 504
2018-02-09 21:30 | 484 | 483
2018-02-09 22:00 | 473 | 473
2018-02-09 22:30 | 470 | 469
2018-02-09 23:00 | 447 | 446
2018-02-09 23:30 | 419 | 418
2018-02-10 | 398 | 397
2018-02-10 00:30 | 395 | 392
2018-02-10 01:00 | 384 | 382
2018-02-10 01:30 | 370 | 367
2018-02-10 02:00 | 363 | 361
2018-02-10 02:30 | 360 | 357
2018-02-10 03:00 | 364 | 361
2018-02-10 03:30 | 362 | 359
2018-02-10 04:00 | 357 | 354
2018-02-10 04:30 | 356 | 352
2018-02-10 05:00 | 359 | 356
2018-02-10 05:30 | 364 | 361
2018-02-10 06:00 | 375 | 372
2018-02-10 06:30 | 386 | 383
2018-02-10 07:00 | 396 | 394
2018-02-10 07:30 | 416 | 415
2018-02-10 08:00 | 420 | 419
2018-02-10 08:30 | 428 | 428
2018-02-10 09:00 | 431 | 430
2018-02-10 09:30 | 430 | 430
2018-02-10 10:00 | 432 | 432
2018-02-10 10:30 | 434 | 434
2018-02-10 11:00 | 439 | 439
2018-02-10 11:30 | 447 | 447
2018-02-10 12:00 | 452 | 452
2018-02-10 12:30 | 461 | 461
2018-02-10 13:00 | 482 | 482
2018-02-10 13:30 | 481 | 481
2018-02-10 14:00 | 502 | 501
2018-02-10 14:30 | 525 | 525
2018-02-10 15:00 | 548 | 548
2018-02-10 15:30 | 561 | 561
2018-02-10 16:00 | 584 | 584
2018-02-10 16:30 | 603 | 602
2018-02-10 17:00 | 618 | 618
2018-02-10 17:30 | 626 | 625
2018-02-10 18:00 | 604 | 602
2018-02-10 18:30 | 585 | 583
2018-02-10 19:00 | 579 | 578
2018-02-10 19:30 | 572 | 571
2018-02-10 20:00 | 561 | 560
2018-02-10 20:30 | 550 | 550
2018-02-10 21:00 | 533 | 532
2018-02-10 21:30 | 517 | 517
2018-02-10 22:00 | 500 | 500
2018-02-10 22:30 | 485 | 484
2018-02-10 23:00 | 468 | 467
2018-02-10 23:30 | 445 | 445
2018-02-11 | 418 | 417
2018-02-11 00:30 | 399 | 399
2018-02-11 01:00 | 391 | 391
2018-02-11 01:30 | 379 | 378
2018-02-11 02:00 | 368 | 367
2018-02-11 02:30 | 358 | 357
2018-02-11 03:00 | 352 | 351
2018-02-11 03:30 | 351 | 350
2018-02-11 04:00 | 346 | 345
2018-02-11 04:30 | 349 | 348
2018-02-11 05:00 | 346 | 345
2018-02-11 05:30 | 354 | 352
2018-02-11 06:00 | 358 | 356
2018-02-11 06:30 | 366 | 364
2018-02-11 07:00 | 376 | 375
2018-02-11 07:30 | 385 | 385
2018-02-11 08:00 | 391 | 391
2018-02-11 08:30 | 410 | 410
2018-02-11 09:00 | 424 | 424
2018-02-11 09:30 | 437 | 437
2018-02-11 10:00 | 447 | 447
2018-02-11 10:30 | 464 | 464
2018-02-11 11:00 | 481 | 481
2018-02-11 11:30 | 496 | 495
2018-02-11 12:00 | 511 | 511
2018-02-11 12:30 | 528 | 527
2018-02-11 13:00 | 550 | 550
2018-02-11 13:30 | 567 | 567
2018-02-11 14:00 | 583 | 582
2018-02-11 14:30 | 602 | 600
2018-02-11 15:00 | 616 | 614
2018-02-11 15:30 | 631 | 628
2018-02-11 16:00 | 653 | 651
2018-02-11 16:30 | 685 | 683
2018-02-11 17:00 | 699 | 695
2018-02-11 17:30 | 683 | 681
2018-02-11 18:00 | 675 | 673
2018-02-11 18:30 | 588 | 585
2018-02-11 19:00 | 521 | 520
2018-02-11 19:30 | 504 | 502
2018-02-11 20:00 | 497 | 496
2018-02-11 20:30 | 487 | 487
2018-02-11 21:00 | 466 | 465
2018-02-11 21:30 | 451 | 451
2018-02-11 22:00 | 435 | 434
2018-02-11 22:30 | 416 | 416
2018-02-11 23:00 | 394 | 394
2018-02-11 23:30 | 390 | 389
2018-02-12 | 373 | 372
2018-02-12 00:30 | 360 | 359
2018-02-12 01:00 | 354 | 353
2018-02-12 01:30 | 347 | 346
2018-02-12 02:00 | 340 | 339
2018-02-12 02:30 | 340 | 339
2018-02-12 03:00 | 340 | 338
2018-02-12 03:30 | 346 | 344
2018-02-12 04:00 | 347 | 345
2018-02-12 04:30 | 356 | 354
2018-02-12 05:00 | 362 | 361
2018-02-12 05:30 | 375 | 375
2018-02-12 06:00 | 396 | 395
2018-02-12 06:30 | 444 | 444
2018-02-12 07:00 | 484 | 483
2018-02-12 07:30 | 518 | 515
2018-02-12 08:00 | 537 | 534
2018-02-12 08:30 | 554 | 550
2018-02-12 09:00 | 568 | 563
2018-02-12 09:30 | 578 | 574
2018-02-12 10:00 | 587 | 583
2018-02-12 10:30 | 597 | 594
2018-02-12 11:00 | 604 | 600
2018-02-12 11:30 | 614 | 609
2018-02-12 12:00 | 631 | 627
2018-02-12 12:30 | 649 | 645
2018-02-12 13:00 | 662 | 659
2018-02-12 13:30 | 682 | 679
2018-02-12 14:00 | 695 | 693
2018-02-12 14:30 | 706 | 703
2018-02-12 15:00 | 717 | 714
2018-02-12 15:30 | 735 | 732
2018-02-12 16:00 | 749 | 747
2018-02-12 16:30 | 761 | 758
2018-02-12 17:00 | 770 | 766
2018-02-12 17:30 | 777 | 773
2018-02-12 18:00 | 763 | 757
2018-02-12 18:30 | 741 | 732
2018-02-12 19:00 | 746 | 742
2018-02-12 19:30 | 745 | 741
2018-02-12 20:00 | 730 | 725
2018-02-12 20:30 | 711 | 705
2018-02-12 21:00 | 676 | 671
2018-02-12 21:30 | 639 | 638
2018-02-12 22:00 | 611 | 610
2018-02-12 22:30 | 581 | 580
2018-02-12 23:00 | 552 | 551
2018-02-12 23:30 | 520 | 520
2018-02-13 | 490 | 489
2018-02-13 00:30 | 462 | 461
2018-02-13 01:00 | 450 | 449
2018-02-13 01:30 | 439 | 438
2018-02-13 02:00 | 429 | 428
2018-02-13 02:30 | 426 | 424
2018-02-13 03:00 | 423 | 422
2018-02-13 03:30 | 423 | 422
2018-02-13 04:00 | 424 | 422
2018-02-13 04:30 | 429 | 428
2018-02-13 05:00 | 434 | 433
2018-02-13 05:30 | 450 | 449
2018-02-13 06:00 | 477 | 477
2018-02-13 06:30 | 535 | 533
2018-02-13 07:00 | 578 | 577
2018-02-13 07:30 | 611 | 608
2018-02-13 08:00 | 629 | 628
2018-02-13 08:30 | 657 | 657
2018-02-13 09:00 | 665 | 664
2018-02-13 09:30 | 654 | 652
2018-02-13 10:00 | 647 | 645
2018-02-13 10:30 | 657 | 655
2018-02-13 11:00 | 670 | 669
2018-02-13 11:30 | 674 | 673
2018-02-13 12:00 | 682 | 681
2018-02-13 12:30 | 690 | 689
2018-02-13 13:00 | 706 | 704
2018-02-13 13:30 | 713 | 712
2018-02-13 14:00 | 722 | 721
2018-02-13 14:30 | 726 | 726
2018-02-13 15:00 | 734 | 733
2018-02-13 15:30 | 748 | 747
2018-02-13 16:00 | 774 | 771
2018-02-13 16:30 | 803 | 800
2018-02-13 17:00 | 800 | 796
2018-02-13 17:30 | 772 | 768
2018-02-13 18:00 | 752 | 747
2018-02-13 18:30 | 730 | 725
2018-02-13 19:00 | 744 | 739
2018-02-13 19:30 | 719 | 711
2018-02-13 20:00 | 679 | 672
2018-02-13 20:30 | 634 | 627
2018-02-13 21:00 | 585 | 583
2018-02-13 21:30 | 559 | 556
2018-02-13 22:00 | 541 | 538
2018-02-13 22:30 | 514 | 513
2018-02-13 23:00 | 489 | 488
2018-02-13 23:30 | 463 | 462
2018-02-14 | 433 | 433
2018-02-14 00:30 | 409 | 409
2018-02-14 01:00 | 401 | 401
2018-02-14 01:30 | 387 | 387
2018-02-14 02:00 | 376 | 376
2018-02-14 02:30 | 370 | 370
2018-02-14 03:00 | 367 | 366
2018-02-14 03:30 | 358 | 357
2018-02-14 04:00 | 350 | 350
2018-02-14 04:30 | 372 | 371
2018-02-14 05:00 | 383 | 383
2018-02-14 05:30 | 405 | 405
2018-02-14 06:00 | 437 | 437
2018-02-14 06:30 | 478 | 478
2018-02-14 07:00 | 514 | 514
2018-02-14 07:30 | 545 | 545
2018-02-14 08:00 | 568 | 566
2018-02-14 08:30 | 582 | 579
2018-02-14 09:00 | 587 | 585
2018-02-14 09:30 | 602 | 597
2018-02-14 10:00 | 614 | 606
2018-02-14 10:30 | 629 | 621
2018-02-14 11:00 | 640 | 632
2018-02-14 11:30 | 658 | 648
2018-02-14 12:00 | 670 | 662
2018-02-14 12:30 | 686 | 679
2018-02-14 13:00 | 691 | 683
2018-02-14 13:30 | 710 | 702
2018-02-14 14:00 | 721 | 713
2018-02-14 14:30 | 731 | 724
2018-02-14 15:00 | 743 | 735
2018-02-14 15:30 | 756 | 748
2018-02-14 16:00 | 793 | 787
2018-02-14 16:30 | 819 | 813
2018-02-14 17:00 | 830 | 824
2018-02-14 17:30 | 821 | 814
2018-02-14 18:00 | 809 | 799
2018-02-14 18:30 | 788 | 780
2018-02-14 19:00 | 780 | 774
2018-02-14 19:30 | 775 | 765
2018-02-14 20:00 | 748 | 743
2018-02-14 20:30 | 739 | 732
2018-02-14 21:00 | 717 | 712
2018-02-14 21:30 | 673 | 667
2018-02-14 22:00 | 628 | 622
2018-02-14 22:30 | 589 | 581
2018-02-14 23:00 | 557 | 555
2018-02-14 23:30 | 530 | 528
2018-02-15 | 516 | 516
2018-02-15 00:30 | 496 | 495
2018-02-15 01:00 | 468 | 468
2018-02-15 01:30 | 454 | 454
2018-02-15 02:00 | 468 | 468
2018-02-15 02:30 | 458 | 458
2018-02-15 03:00 | 445 | 445
2018-02-15 03:30 | 436 | 436
2018-02-15 04:00 | 437 | 436
2018-02-15 04:30 | 439 | 439
2018-02-15 05:00 | 443 | 443
2018-02-15 05:30 | 473 | 473
2018-02-15 06:00 | 498 | 498
2018-02-15 06:30 | 540 | 539
2018-02-15 07:00 | 578 | 577
2018-02-15 07:30 | 609 | 608
2018-02-15 08:00 | 628 | 623
2018-02-15 08:30 | 639 | 635
2018-02-15 09:00 | 646 | 642
2018-02-15 09:30 | 663 | 660
2018-02-15 10:00 | 680 | 677
2018-02-15 10:30 | 684 | 681
2018-02-15 11:00 | 708 | 706
2018-02-15 11:30 | 722 | 720
2018-02-15 12:00 | 726 | 724
2018-02-15 12:30 | 734 | 732
2018-02-15 13:00 | 735 | 732
2018-02-15 13:30 | 749 | 745
2018-02-15 14:00 | 756 | 753
2018-02-15 14:30 | 766 | 763
2018-02-15 15:00 | 772 | 769
2018-02-15 15:30 | 800 | 796
2018-02-15 16:00 | 824 | 819
2018-02-15 16:30 | 799 | 792
2018-02-15 17:00 | 787 | 781
2018-02-15 17:30 | 773 | 769
2018-02-15 18:00 | 750 | 745
2018-02-15 18:30 | 726 | 719
2018-02-15 19:00 | 727 | 723
2018-02-15 19:30 | 719 | 715
2018-02-15 20:00 | 709 | 703
2018-02-15 20:30 | 715 | 709
2018-02-15 21:00 | 692 | 685
2018-02-15 21:30 | 643 | 633
2018-02-15 22:00 | 604 | 594
2018-02-15 22:30 | 575 | 563
2018-02-15 23:00 | 542 | 536
2018-02-15 23:30 | 512 | 507
2018-02-16 | 483 | 483
2018-02-16 00:30 | 459 | 459
2018-02-16 01:00 | 437 | 437
2018-02-16 01:30 | 421 | 421
2018-02-16 02:00 | 439 | 438
2018-02-16 02:30 | 428 | 427
2018-02-16 03:00 | 417 | 416
2018-02-16 03:30 | 410 | 409
2018-02-16 04:00 | 409 | 408
2018-02-16 04:30 | 411 | 411
2018-02-16 05:00 | 414 | 414
2018-02-16 05:30 | 433 | 432
2018-02-16 06:00 | 461 | 459
2018-02-16 06:30 | 527 | 527
2018-02-16 07:00 | 578 | 576
2018-02-16 07:30 | 602 | 601
2018-02-16 08:00 | 611 | 609
2018-02-16 08:30 | 624 | 623
2018-02-16 09:00 | 637 | 634
2018-02-16 09:30 | 652 | 649
2018-02-16 10:00 | 655 | 653
2018-02-16 10:30 | 656 | 654
2018-02-16 11:00 | 667 | 666
2018-02-16 11:30 | 679 | 677
2018-02-16 12:00 | 685 | 683
2018-02-16 12:30 | 684 | 682
2018-02-16 13:00 | 693 | 691
2018-02-16 13:30 | 708 | 706
2018-02-16 14:00 | 716 | 714
2018-02-16 14:30 | 726 | 725
2018-02-16 15:00 | 762 | 756
2018-02-16 15:30 | 769 | 762
2018-02-16 16:00 | 771 | 763
2018-02-16 16:30 | 759 | 750
2018-02-16 17:00 | 759 | 749
2018-02-16 17:30 | 721 | 715
2018-02-16 18:00 | 683 | 675
2018-02-16 18:30 | 643 | 637
2018-02-16 19:00 | 636 | 632
2018-02-16 19:30 | 629 | 625
2018-02-16 20:00 | 622 | 620
2018-02-16 20:30 | 602 | 599
2018-02-16 21:00 | 574 | 573
2018-02-16 21:30 | 561 | 560
2018-02-16 22:00 | 545 | 544
2018-02-16 22:30 | 525 | 524
2018-02-16 23:00 | 496 | 494
2018-02-16 23:30 | 471 | 470
2018-02-17 | 444 | 443
2018-02-17 00:30 | 424 | 422
2018-02-17 01:00 | 408 | 406
2018-02-17 01:30 | 402 | 400
2018-02-17 02:00 | 396 | 395
2018-02-17 02:30 | 396 | 395
2018-02-17 03:00 | 391 | 389
2018-02-17 03:30 | 384 | 382
2018-02-17 04:00 | 381 | 379
2018-02-17 04:30 | 379 | 377
2018-02-17 05:00 | 383 | 381
2018-02-17 05:30 | 394 | 392
2018-02-17 06:00 | 407 | 404
2018-02-17 06:30 | 417 | 415
2018-02-17 07:00 | 427 | 426
2018-02-17 07:30 | 458 | 457
2018-02-17 08:00 | 476 | 475
2018-02-17 08:30 | 500 | 499
2018-02-17 09:00 | 516 | 515
2018-02-17 09:30 | 521 | 520
2018-02-17 10:00 | 521 | 520
2018-02-17 10:30 | 526 | 525
2018-02-17 11:00 | 533 | 533
2018-02-17 11:30 | 536 | 536
2018-02-17 12:00 | 535 | 535
2018-02-17 12:30 | 538 | 537
2018-02-17 13:00 | 543 | 543
2018-02-17 13:30 | 549 | 548
2018-02-17 14:00 | 551 | 550
2018-02-17 14:30 | 559 | 558
2018-02-17 15:00 | 567 | 567
2018-02-17 15:30 | 563 | 563
2018-02-17 16:00 | 570 | 569
2018-02-17 16:30 | 570 | 570
2018-02-17 17:00 | 582 | 581
2018-02-17 17:30 | 564 | 563
2018-02-17 18:00 | 553 | 552
2018-02-17 18:30 | 543 | 541
2018-02-17 19:00 | 546 | 545
2018-02-17 19:30 | 564 | 562
2018-02-17 20:00 | 577 | 574
2018-02-17 20:30 | 559 | 555
2018-02-17 21:00 | 547 | 543
2018-02-17 21:30 | 533 | 529
2018-02-17 22:00 | 521 | 516
2018-02-17 22:30 | 497 | 492
2018-02-17 23:00 | 476 | 472
2018-02-17 23:30 | 453 | 447
2018-02-18 | 433 | 424
2018-02-18 00:30 | 414 | 403
2018-02-18 01:00 | 398 | 389
2018-02-18 01:30 | 389 | 381
2018-02-18 02:00 | 379 | 370
2018-02-18 02:30 | 373 | 366
2018-02-18 03:00 | 369 | 362
2018-02-18 03:30 | 365 | 357
2018-02-18 04:00 | 363 | 354
2018-02-18 04:30 | 362 | 354
2018-02-18 05:00 | 365 | 357
2018-02-18 05:30 | 370 | 361
2018-02-18 06:00 | 371 | 361
2018-02-18 06:30 | 382 | 373
2018-02-18 07:00 | 395 | 387
2018-02-18 07:30 | 413 | 406
2018-02-18 08:00 | 423 | 418
2018-02-18 08:30 | 435 | 431
2018-02-18 09:00 | 445 | 442
2018-02-18 09:30 | 458 | 456
2018-02-18 10:00 | 465 | 463
2018-02-18 10:30 | 478 | 476
2018-02-18 11:00 | 493 | 490
2018-02-18 11:30 | 500 | 496
2018-02-18 12:00 | 506 | 503
2018-02-18 12:30 | 517 | 513
2018-02-18 13:00 | 530 | 525
2018-02-18 13:30 | 536 | 531
2018-02-18 14:00 | 546 | 543
2018-02-18 14:30 | 560 | 557
2018-02-18 15:00 | 579 | 578
2018-02-18 15:30 | 592 | 586
2018-02-18 16:00 | 596 | 590
2018-02-18 16:30 | 591 | 585
2018-02-18 17:00 | 596 | 591
2018-02-18 17:30 | 591 | 585
2018-02-18 18:00 | 587 | 579
2018-02-18 18:30 | 575 | 566
2018-02-18 19:00 | 577 | 570
2018-02-18 19:30 | 587 | 578
2018-02-18 20:00 | 584 | 577
2018-02-18 20:30 | 554 | 547
2018-02-18 21:00 | 530 | 528
2018-02-18 21:30 | 519 | 517
2018-02-18 22:00 | 499 | 497
2018-02-18 22:30 | 479 | 476
2018-02-18 23:00 | 457 | 454
2018-02-18 23:30 | 429 | 426
2018-02-19 | 405 | 402
2018-02-19 00:30 | 386 | 383
2018-02-19 01:00 | 379 | 376
2018-02-19 01:30 | 371 | 369
2018-02-19 02:00 | 368 | 365
2018-02-19 02:30 | 365 | 362
2018-02-19 03:00 | 356 | 353
2018-02-19 03:30 | 354 | 351
2018-02-19 04:00 | 353 | 350
2018-02-19 04:30 | 360 | 357
2018-02-19 05:00 | 369 | 367
2018-02-19 05:30 | 390 | 388
2018-02-19 06:00 | 405 | 404
2018-02-19 06:30 | 449 | 447
2018-02-19 07:00 | 480 | 475
2018-02-19 07:30 | 508 | 506
2018-02-19 08:00 | 526 | 522
2018-02-19 08:30 | 534 | 528
2018-02-19 09:00 | 534 | 529
2018-02-19 09:30 | 537 | 533
2018-02-19 10:00 | 547 | 540
2018-02-19 10:30 | 552 | 545
2018-02-19 11:00 | 557 | 552
2018-02-19 11:30 | 563 | 559
2018-02-19 12:00 | 578 | 573
2018-02-19 12:30 | 587 | 582
2018-02-19 13:00 | 602 | 598
2018-02-19 13:30 | 612 | 609
2018-02-19 14:00 | 627 | 624
2018-02-19 14:30 | 642 | 640
2018-02-19 15:00 | 648 | 646
2018-02-19 15:30 | 662 | 661
2018-02-19 16:00 | 686 | 684
2018-02-19 16:30 | 698 | 695
2018-02-19 17:00 | 714 | 710
2018-02-19 17:30 | 706 | 701
2018-02-19 18:00 | 681 | 673
2018-02-19 18:30 | 651 | 644
2018-02-19 19:00 | 658 | 656
2018-02-19 19:30 | 651 | 648
2018-02-19 20:00 | 646 | 642
2018-02-19 20:30 | 617 | 615
2018-02-19 21:00 | 577 | 576
2018-02-19 21:30 | 551 | 549
2018-02-19 22:00 | 522 | 520
2018-02-19 22:30 | 503 | 501
2018-02-19 23:00 | 486 | 484
2018-02-19 23:30 | 466 | 463
2018-02-20 | 448 | 443
2018-02-20 00:30 | 419 | 418
2018-02-20 01:00 | 407 | 406
2018-02-20 01:30 | 394 | 393
2018-02-20 02:00 | 390 | 389
2018-02-20 02:30 | 388 | 387
2018-02-20 03:00 | 381 | 380
2018-02-20 03:30 | 379 | 378
2018-02-20 04:00 | 379 | 378
2018-02-20 04:30 | 381 | 380
2018-02-20 05:00 | 388 | 388
2018-02-20 05:30 | 408 | 408
2018-02-20 06:00 | 417 | 416
2018-02-20 06:30 | 458 | 458
2018-02-20 07:00 | 491 | 491
2018-02-20 07:30 | 518 | 518
2018-02-20 08:00 | 535 | 535
2018-02-20 08:30 | 537 | 536
2018-02-20 09:00 | 539 | 539
2018-02-20 09:30 | 526 | 526
2018-02-20 10:00 | 531 | 530
2018-02-20 10:30 | 551 | 550
2018-02-20 11:00 | 543 | 541
2018-02-20 11:30 | 540 | 539
2018-02-20 12:00 | 543 | 542
2018-02-20 12:30 | 546 | 545
2018-02-20 13:00 | 540 | 539
2018-02-20 13:30 | 549 | 548
2018-02-20 14:00 | 564 | 563
2018-02-20 14:30 | 561 | 561
2018-02-20 15:00 | 562 | 561
2018-02-20 15:30 | 569 | 568
2018-02-20 16:00 | 581 | 580
2018-02-20 16:30 | 601 | 600
2018-02-20 17:00 | 616 | 614
2018-02-20 17:30 | 609 | 608
2018-02-20 18:00 | 596 | 594
2018-02-20 18:30 | 577 | 576
2018-02-20 19:00 | 575 | 575
2018-02-20 19:30 | 569 | 569
2018-02-20 20:00 | 565 | 565
2018-02-20 20:30 | 555 | 555
2018-02-20 21:00 | 533 | 532
2018-02-20 21:30 | 519 | 518
2018-02-20 22:00 | 497 | 495
2018-02-20 22:30 | 488 | 485
2018-02-20 23:00 | 463 | 462
2018-02-20 23:30 | 434 | 433
2018-02-21 | 414 | 413
2018-02-21 00:30 | 396 | 395
2018-02-21 01:00 | 390 | 388
2018-02-21 01:30 | 380 | 378
2018-02-21 02:00 | 376 | 373
2018-02-21 02:30 | 372 | 369
2018-02-21 03:00 | 365 | 363
2018-02-21 03:30 | 364 | 361
2018-02-21 04:00 | 364 | 362
2018-02-21 04:30 | 368 | 366
2018-02-21 05:00 | 383 | 381
2018-02-21 05:30 | 400 | 399
2018-02-21 06:00 | 414 | 414
2018-02-21 06:30 | 457 | 457
2018-02-21 07:00 | 496 | 496
2018-02-21 07:30 | 520 | 520
2018-02-21 08:00 | 526 | 526
2018-02-21 08:30 | 532 | 532
2018-02-21 09:00 | 542 | 542
2018-02-21 09:30 | 547 | 547
2018-02-21 10:00 | 550 | 550
2018-02-21 10:30 | 541 | 541
2018-02-21 11:00 | 535 | 535
2018-02-21 11:30 | 527 | 527
2018-02-21 12:00 | 531 | 531
2018-02-21 12:30 | 535 | 535
2018-02-21 13:00 | 529 | 529
2018-02-21 13:30 | 516 | 516
2018-02-21 14:00 | 517 | 517
2018-02-21 14:30 | 522 | 521
2018-02-21 15:00 | 526 | 526
2018-02-21 15:30 | 530 | 530
2018-02-21 16:00 | 532 | 532
2018-02-21 16:30 | 543 | 543
2018-02-21 17:00 | 545 | 545
2018-02-21 17:30 | 544 | 544
2018-02-21 18:00 | 536 | 535
2018-02-21 18:30 | 526 | 525
2018-02-21 19:00 | 542 | 542
2018-02-21 19:30 | 535 | 535
2018-02-21 20:00 | 521 | 521
2018-02-21 20:30 | 507 | 507
2018-02-21 21:00 | 490 | 489
2018-02-21 21:30 | 476 | 475
2018-02-21 22:00 | 459 | 457
2018-02-21 22:30 | 448 | 448
2018-02-21 23:00 | 438 | 437
2018-02-21 23:30 | 422 | 421
2018-02-22 | 405 | 403
2018-02-22 00:30 | 380 | 377
2018-02-22 01:00 | 373 | 370
2018-02-22 01:30 | 366 | 362
2018-02-22 02:00 | 362 | 357
2018-02-22 02:30 | 357 | 353
2018-02-22 03:00 | 352 | 348
2018-02-22 03:30 | 348 | 344
2018-02-22 04:00 | 350 | 346
2018-02-22 04:30 | 355 | 352
2018-02-22 05:00 | 364 | 361
2018-02-22 05:30 | 383 | 382
2018-02-22 06:00 | 402 | 401
2018-02-22 06:30 | 439 | 439
2018-02-22 07:00 | 473 | 471
2018-02-22 07:30 | 507 | 506
2018-02-22 08:00 | 519 | 519
2018-02-22 08:30 | 521 | 521
2018-02-22 09:00 | 521 | 521
2018-02-22 09:30 | 523 | 523
2018-02-22 10:00 | 510 | 510
2018-02-22 10:30 | 515 | 515
2018-02-22 11:00 | 531 | 531
2018-02-22 11:30 | 533 | 533
2018-02-22 12:00 | 533 | 533
2018-02-22 12:30 | 532 | 532
2018-02-22 13:00 | 526 | 526
2018-02-22 13:30 | 526 | 526
2018-02-22 14:00 | 531 | 531
2018-02-22 14:30 | 537 | 537
2018-02-22 15:00 | 539 | 539
2018-02-22 15:30 | 543 | 543
2018-02-22 16:00 | 551 | 551
2018-02-22 16:30 | 553 | 552
2018-02-22 17:00 | 555 | 554
2018-02-22 17:30 | 557 | 556
2018-02-22 18:00 | 556 | 555
2018-02-22 18:30 | 540 | 540
2018-02-22 19:00 | 551 | 551
2018-02-22 19:30 | 542 | 542
2018-02-22 20:00 | 528 | 527
2018-02-22 20:30 | 509 | 508
2018-02-22 21:00 | 492 | 491
2018-02-22 21:30 | 476 | 475
2018-02-22 22:00 | 456 | 455
2018-02-22 22:30 | 448 | 448
2018-02-22 23:00 | 440 | 439
2018-02-22 23:30 | 424 | 423
2018-02-23 | 401 | 399
2018-02-23 00:30 | 372 | 370
2018-02-23 01:00 | 356 | 352
2018-02-23 01:30 | 351 | 347
2018-02-23 02:00 | 348 | 344
2018-02-23 02:30 | 349 | 344
2018-02-23 03:00 | 350 | 346
2018-02-23 03:30 | 351 | 346
2018-02-23 04:00 | 350 | 346
2018-02-23 04:30 | 355 | 352
2018-02-23 05:00 | 364 | 361
2018-02-23 05:30 | 384 | 382
2018-02-23 06:00 | 409 | 409
2018-02-23 06:30 | 453 | 452
2018-02-23 07:00 | 495 | 495
2018-02-23 07:30 | 526 | 525
2018-02-23 08:00 | 538 | 538
2018-02-23 08:30 | 559 | 557
2018-02-23 09:00 | 571 | 566
2018-02-23 09:30 | 566 | 563
2018-02-23 10:00 | 569 | 566
2018-02-23 10:30 | 564 | 560
2018-02-23 11:00 | 556 | 552
2018-02-23 11:30 | 546 | 542
2018-02-23 12:00 | 548 | 544
2018-02-23 12:30 | 550 | 546
2018-02-23 13:00 | 545 | 545
2018-02-23 13:30 | 542 | 542
2018-02-23 14:00 | 543 | 542
2018-02-23 14:30 | 540 | 540
2018-02-23 15:00 | 533 | 532
2018-02-23 15:30 | 531 | 530
2018-02-23 16:00 | 533 | 532
2018-02-23 16:30 | 542 | 541
2018-02-23 17:00 | 540 | 539
2018-02-23 17:30 | 530 | 528
2018-02-23 18:00 | 511 | 510
2018-02-23 18:30 | 502 | 501
2018-02-23 19:00 | 516 | 515
2018-02-23 19:30 | 516 | 514
2018-02-23 20:00 | 512 | 512
2018-02-23 20:30 | 496 | 496
2018-02-23 21:00 | 479 | 479
2018-02-23 21:30 | 472 | 470
2018-02-23 22:00 | 463 | 461
2018-02-23 22:30 | 453 | 452
2018-02-23 23:00 | 440 | 440
2018-02-23 23:30 | 421 | 421
2018-02-24 | 400 | 399
2018-02-24 00:30 | 374 | 372
2018-02-24 01:00 | 362 | 360
2018-02-24 01:30 | 347 | 345
2018-02-24 02:00 | 336 | 333
2018-02-24 02:30 | 332 | 329
2018-02-24 03:00 | 326 | 323
2018-02-24 03:30 | 326 | 322
2018-02-24 04:00 | 316 | 312
2018-02-24 04:30 | 317 | 313
2018-02-24 05:00 | 319 | 315
2018-02-24 05:30 | 332 | 330
2018-02-24 06:00 | 345 | 343
2018-02-24 06:30 | 360 | 358
2018-02-24 07:00 | 382 | 381
2018-02-24 07:30 | 425 | 424
2018-02-24 08:00 | 477 | 477
2018-02-24 08:30 | 482 | 482
2018-02-24 09:00 | 491 | 488
2018-02-24 09:30 | 505 | 503
2018-02-24 10:00 | 506 | 505
2018-02-24 10:30 | 519 | 517
2018-02-24 11:00 | 530 | 524
2018-02-24 11:30 | 517 | 511
2018-02-24 12:00 | 507 | 500
2018-02-24 12:30 | 481 | 473
2018-02-24 13:00 | 463 | 454
2018-02-24 13:30 | 478 | 471
2018-02-24 14:00 | 475 | 468
2018-02-24 14:30 | 468 | 461
2018-02-24 15:00 | 477 | 471
2018-02-24 15:30 | 493 | 487
2018-02-24 16:00 | 513 | 508
2018-02-24 16:30 | 521 | 515
2018-02-24 17:00 | 529 | 523
2018-02-24 17:30 | 536 | 527
2018-02-24 18:00 | 532 | 523
2018-02-24 18:30 | 525 | 516
2018-02-24 19:00 | 543 | 536
2018-02-24 19:30 | 538 | 530
2018-02-24 20:00 | 534 | 526
2018-02-24 20:30 | 534 | 526
2018-02-24 21:00 | 510 | 503
2018-02-24 21:30 | 491 | 485
2018-02-24 22:00 | 471 | 470
2018-02-24 22:30 | 455 | 454
2018-02-24 23:00 | 433 | 432
2018-02-24 23:30 | 414 | 413
2018-02-25 | 402 | 399
2018-02-25 00:30 | 383 | 380
2018-02-25 01:00 | 371 | 369
2018-02-25 01:30 | 362 | 359
2018-02-25 02:00 | 349 | 345
2018-02-25 02:30 | 349 | 345
2018-02-25 03:00 | 348 | 344
2018-02-25 03:30 | 347 | 343
2018-02-25 04:00 | 345 | 342
2018-02-25 04:30 | 343 | 340
2018-02-25 05:00 | 345 | 341
2018-02-25 05:30 | 349 | 346
2018-02-25 06:00 | 351 | 347
2018-02-25 06:30 | 353 | 349
2018-02-25 07:00 | 366 | 363
2018-02-25 07:30 | 387 | 386
2018-02-25 08:00 | 402 | 401
2018-02-25 08:30 | 412 | 412
2018-02-25 09:00 | 429 | 429
2018-02-25 09:30 | 448 | 447
2018-02-25 10:00 | 450 | 450
2018-02-25 10:30 | 464 | 463
2018-02-25 11:00 | 475 | 471
2018-02-25 11:30 | 485 | 481
2018-02-25 12:00 | 501 | 495
2018-02-25 12:30 | 498 | 492
2018-02-25 13:00 | 508 | 504
2018-02-25 13:30 | 514 | 511
2018-02-25 14:00 | 529 | 524
2018-02-25 14:30 | 552 | 547
2018-02-25 15:00 | 541 | 536
2018-02-25 15:30 | 550 | 543
2018-02-25 16:00 | 589 | 582
2018-02-25 16:30 | 577 | 569
2018-02-25 17:00 | 569 | 561
2018-02-25 17:30 | 564 | 554
2018-02-25 18:00 | 553 | 543
2018-02-25 18:30 | 542 | 534
2018-02-25 19:00 | 556 | 551
2018-02-25 19:30 | 550 | 544
2018-02-25 20:00 | 540 | 533
2018-02-25 20:30 | 531 | 524
2018-02-25 21:00 | 524 | 518
2018-02-25 21:30 | 513 | 507
2018-02-25 22:00 | 492 | 488
2018-02-25 22:30 | 467 | 466
2018-02-25 23:00 | 444 | 443
2018-02-25 23:30 | 423 | 422
2018-02-26 | 408 | 408
2018-02-26 00:30 | 388 | 388
2018-02-26 01:00 | 377 | 377
2018-02-26 01:30 | 357 | 357
2018-02-26 02:00 | 346 | 345
2018-02-26 02:30 | 344 | 344
2018-02-26 03:00 | 346 | 345
2018-02-26 03:30 | 338 | 337
2018-02-26 04:00 | 340 | 340
2018-02-26 04:30 | 360 | 359
2018-02-26 05:00 | 374 | 373
2018-02-26 05:30 | 396 | 395
2018-02-26 06:00 | 418 | 418
2018-02-26 06:30 | 462 | 462
2018-02-26 07:00 | 496 | 496
2018-02-26 07:30 | 523 | 523
2018-02-26 08:00 | 539 | 539
2018-02-26 08:30 | 551 | 551
2018-02-26 09:00 | 551 | 550
2018-02-26 09:30 | 565 | 565
2018-02-26 10:00 | 571 | 571
2018-02-26 10:30 | 577 | 576
2018-02-26 11:00 | 590 | 588
2018-02-26 11:30 | 597 | 592
2018-02-26 12:00 | 599 | 594
2018-02-26 12:30 | 604 | 600
2018-02-26 13:00 | 617 | 613
2018-02-26 13:30 | 632 | 630
2018-02-26 14:00 | 647 | 644
2018-02-26 14:30 | 665 | 661
2018-02-26 15:00 | 679 | 675
2018-02-26 15:30 | 687 | 683
2018-02-26 16:00 | 717 | 714
2018-02-26 16:30 | 748 | 743
2018-02-26 17:00 | 762 | 755
2018-02-26 17:30 | 761 | 753
2018-02-26 18:00 | 743 | 733
2018-02-26 18:30 | 717 | 707
2018-02-26 19:00 | 711 | 701
2018-02-26 19:30 | 668 | 664
2018-02-26 20:00 | 637 | 632
2018-02-26 20:30 | 592 | 585
2018-02-26 21:00 | 549 | 546
2018-02-26 21:30 | 516 | 514
2018-02-26 22:00 | 492 | 491
2018-02-26 22:30 | 474 | 473
2018-02-26 23:00 | 455 | 454
2018-02-26 23:30 | 437 | 434
2018-02-27 | 418 | 414
2018-02-27 00:30 | 387 | 384
2018-02-27 01:00 | 380 | 380
2018-02-27 01:30 | 376 | 375
2018-02-27 02:00 | 369 | 369
2018-02-27 02:30 | 360 | 359
2018-02-27 03:00 | 355 | 354
2018-02-27 03:30 | 355 | 354
2018-02-27 04:00 | 357 | 356
2018-02-27 04:30 | 368 | 367
2018-02-27 05:00 | 375 | 375
2018-02-27 05:30 | 401 | 401
2018-02-27 06:00 | 413 | 413
2018-02-27 06:30 | 456 | 455
2018-02-27 07:00 | 478 | 477
2018-02-27 07:30 | 510 | 509
2018-02-27 08:00 | 525 | 524
2018-02-27 08:30 | 527 | 526
2018-02-27 09:00 | 535 | 534
2018-02-27 09:30 | 533 | 532
2018-02-27 10:00 | 526 | 525
2018-02-27 10:30 | 520 | 519
2018-02-27 11:00 | 513 | 512
2018-02-27 11:30 | 513 | 512
2018-02-27 12:00 | 503 | 502
2018-02-27 12:30 | 505 | 504
2018-02-27 13:00 | 509 | 508
2018-02-27 13:30 | 515 | 514
2018-02-27 14:00 | 523 | 522
2018-02-27 14:30 | 523 | 523
2018-02-27 15:00 | 533 | 532
2018-02-27 15:30 | 539 | 538
2018-02-27 16:00 | 554 | 553
2018-02-27 16:30 | 557 | 556
2018-02-27 17:00 | 563 | 561
2018-02-27 17:30 | 556 | 555
2018-02-27 18:00 | 555 | 552
2018-02-27 18:30 | 544 | 540
2018-02-27 19:00 | 556 | 553
2018-02-27 19:30 | 540 | 538
2018-02-27 20:00 | 530 | 530
2018-02-27 20:30 | 511 | 510
2018-02-27 21:00 | 486 | 485
2018-02-27 21:30 | 474 | 473
2018-02-27 22:00 | 454 | 454
2018-02-27 22:30 | 443 | 443
2018-02-27 23:00 | 430 | 430
2018-02-27 23:30 | 413 | 412
2018-02-28 | 393 | 393
2018-02-28 00:30 | 370 | 369
2018-02-28 01:00 | 359 | 358
2018-02-28 01:30 | 352 | 350
2018-02-28 02:00 | 342 | 339
2018-02-28 02:30 | 335 | 331
2018-02-28 03:00 | 331 | 328
2018-02-28 03:30 | 332 | 329
2018-02-28 04:00 | 334 | 331
2018-02-28 04:30 | 338 | 335
2018-02-28 05:00 | 350 | 349
2018-02-28 05:30 | 378 | 377
2018-02-28 06:00 | 405 | 404
2018-02-28 06:30 | 449 | 449
2018-02-28 07:00 | 467 | 467
2018-02-28 07:30 | 469 | 469
2018-02-28 08:00 | 487 | 487
2018-02-28 08:30 | 484 | 484
2018-02-28 09:00 | 472 | 471
2018-02-28 09:30 | 474 | 473
2018-02-28 10:00 | 476 | 476
2018-02-28 10:30 | 490 | 490
2018-02-28 11:00 | 500 | 499
2018-02-28 11:30 | 505 | 504
2018-02-28 12:00 | 501 | 501
2018-02-28 12:30 | 504 | 504
2018-02-28 13:00 | 511 | 510
2018-02-28 13:30 | 516 | 516
2018-02-28 14:00 | 526 | 525
2018-02-28 14:30 | 532 | 531
2018-02-28 15:00 | 537 | 536
2018-02-28 15:30 | 552 | 552
2018-02-28 16:00 | 566 | 566
2018-02-28 16:30 | 582 | 581
2018-02-28 17:00 | 598 | 597
2018-02-28 17:30 | 589 | 587
2018-02-28 18:00 | 578 | 575
2018-02-28 18:30 | 562 | 558
2018-02-28 19:00 | 564 | 563
2018-02-28 19:30 | 561 | 559
2018-02-28 20:00 | 550 | 550
2018-02-28 20:30 | 543 | 542
2018-02-28 21:00 | 519 | 518
2018-02-28 21:30 | 499 | 498
2018-02-28 22:00 | 479 | 477
2018-02-28 22:30 | 467 | 467
2018-02-28 23:00 | 454 | 453
2018-02-28 23:30 | 431 | 428
2018-03-01 | 409 | 406
2018-03-01 00:30 | 383 | 381
2018-03-01 01:00 | 375 | 371
2018-03-01 01:30 | 364 | 361
2018-03-01 02:00 | 359 | 355
2018-03-01 02:30 | 355 | 351
2018-03-01 03:00 | 351 | 346
2018-03-01 03:30 | 350 | 346
2018-03-01 04:00 | 353 | 348
2018-03-01 04:30 | 362 | 358
2018-03-01 05:00 | 371 | 368
2018-03-01 05:30 | 386 | 384
2018-03-01 06:00 | 400 | 398
2018-03-01 06:30 | 446 | 445
2018-03-01 07:00 | 468 | 468
2018-03-01 07:30 | 492 | 491
2018-03-01 08:00 | 501 | 501
2018-03-01 08:30 | 500 | 500
2018-03-01 09:00 | 503 | 502
2018-03-01 09:30 | 513 | 513
2018-03-01 10:00 | 525 | 525
2018-03-01 10:30 | 538 | 538
2018-03-01 11:00 | 553 | 553
2018-03-01 11:30 | 566 | 566
2018-03-01 12:00 | 580 | 579
2018-03-01 12:30 | 604 | 604
2018-03-01 13:00 | 630 | 627
2018-03-01 13:30 | 648 | 646
2018-03-01 14:00 | 668 | 665
2018-03-01 14:30 | 685 | 680
2018-03-01 15:00 | 699 | 695
2018-03-01 15:30 | 719 | 714
2018-03-01 16:00 | 751 | 743
2018-03-01 16:30 | 771 | 762
2018-03-01 17:00 | 785 | 776
2018-03-01 17:30 | 782 | 772
2018-03-01 18:00 | 774 | 761
2018-03-01 18:30 | 747 | 738
2018-03-01 19:00 | 758 | 752
2018-03-01 19:30 | 744 | 740
2018-03-01 20:00 | 724 | 719
2018-03-01 20:30 | 699 | 694
2018-03-01 21:00 | 650 | 648
2018-03-01 21:30 | 610 | 606
2018-03-01 22:00 | 567 | 563
2018-03-01 22:30 | 535 | 533
2018-03-01 23:00 | 513 | 512
2018-03-01 23:30 | 477 | 476
2018-03-02 | 453 | 452
2018-03-02 00:30 | 427 | 427
2018-03-02 01:00 | 416 | 415
2018-03-02 01:30 | 409 | 409
2018-03-02 02:00 | 404 | 403
2018-03-02 02:30 | 392 | 391
2018-03-02 03:00 | 401 | 401
2018-03-02 03:30 | 388 | 387
2018-03-02 04:00 | 395 | 395
2018-03-02 04:30 | 393 | 392
2018-03-02 05:00 | 394 | 393
2018-03-02 05:30 | 414 | 413
2018-03-02 06:00 | 433 | 433
2018-03-02 06:30 | 474 | 474
2018-03-02 07:00 | 505 | 504
2018-03-02 07:30 | 534 | 534
2018-03-02 08:00 | 547 | 546
2018-03-02 08:30 | 558 | 557
2018-03-02 09:00 | 560 | 559
2018-03-02 09:30 | 566 | 566
2018-03-02 10:00 | 566 | 565
2018-03-02 10:30 | 574 | 574
2018-03-02 11:00 | 594 | 594
2018-03-02 11:30 | 604 | 603
2018-03-02 12:00 | 605 | 604
2018-03-02 12:30 | 598 | 597
2018-03-02 13:00 | 592 | 592
2018-03-02 13:30 | 604 | 603
2018-03-02 14:00 | 603 | 603
2018-03-02 14:30 | 598 | 598
2018-03-02 15:00 | 583 | 583
2018-03-02 15:30 | 573 | 572
2018-03-02 16:00 | 590 | 590
2018-03-02 16:30 | 612 | 612
2018-03-02 17:00 | 611 | 610
2018-03-02 17:30 | 597 | 597
2018-03-02 18:00 | 565 | 564
2018-03-02 18:30 | 551 | 550
2018-03-02 19:00 | 557 | 557
2018-03-02 19:30 | 544 | 544
2018-03-02 20:00 | 532 | 532
2018-03-02 20:30 | 514 | 513
2018-03-02 21:00 | 501 | 501
2018-03-02 21:30 | 493 | 493
2018-03-02 22:00 | 483 | 483
2018-03-02 22:30 | 483 | 482
2018-03-02 23:00 | 466 | 465
2018-03-02 23:30 | 434 | 433
2018-03-03 | 415 | 415
2018-03-03 00:30 | 397 | 396
2018-03-03 01:00 | 391 | 390
2018-03-03 01:30 | 385 | 384
2018-03-03 02:00 | 375 | 374
2018-03-03 02:30 | 371 | 370
2018-03-03 03:00 | 368 | 367
2018-03-03 03:30 | 365 | 364
2018-03-03 04:00 | 364 | 362
2018-03-03 04:30 | 363 | 361
2018-03-03 05:00 | 347 | 346
2018-03-03 05:30 | 365 | 364
2018-03-03 06:00 | 374 | 373
2018-03-03 06:30 | 394 | 393
2018-03-03 07:00 | 407 | 407
2018-03-03 07:30 | 440 | 440
2018-03-03 08:00 | 469 | 468
2018-03-03 08:30 | 489 | 489
2018-03-03 09:00 | 499 | 498
2018-03-03 09:30 | 503 | 503
2018-03-03 10:00 | 514 | 514
2018-03-03 10:30 | 531 | 530
2018-03-03 11:00 | 535 | 534
2018-03-03 11:30 | 531 | 530
2018-03-03 12:00 | 535 | 534
2018-03-03 12:30 | 533 | 533
2018-03-03 13:00 | 528 | 528
2018-03-03 13:30 | 550 | 549
2018-03-03 14:00 | 552 | 551
2018-03-03 14:30 | 563 | 562
2018-03-03 15:00 | 568 | 568
2018-03-03 15:30 | 568 | 567
2018-03-03 16:00 | 578 | 578
2018-03-03 16:30 | 589 | 589
2018-03-03 17:00 | 606 | 606
2018-03-03 17:30 | 603 | 602
2018-03-03 18:00 | 586 | 585
2018-03-03 18:30 | 577 | 576
2018-03-03 19:00 | 583 | 582
2018-03-03 19:30 | 578 | 576
2018-03-03 20:00 | 562 | 562
2018-03-03 20:30 | 555 | 554
2018-03-03 21:00 | 542 | 542
2018-03-03 21:30 | 535 | 535
2018-03-03 22:00 | 521 | 521
2018-03-03 22:30 | 491 | 491
2018-03-03 23:00 | 471 | 470
2018-03-03 23:30 | 449 | 449
2018-03-04 | 432 | 431
2018-03-04 00:30 | 410 | 410
2018-03-04 01:00 | 402 | 402
2018-03-04 01:30 | 392 | 392
2018-03-04 02:00 | 379 | 379
2018-03-04 02:30 | 373 | 373
2018-03-04 03:00 | 371 | 370
2018-03-04 03:30 | 370 | 369
2018-03-04 04:00 | 364 | 363
2018-03-04 04:30 | 362 | 361
2018-03-04 05:00 | 363 | 362
2018-03-04 05:30 | 365 | 364
2018-03-04 06:00 | 370 | 368
2018-03-04 06:30 | 376 | 375
2018-03-04 07:00 | 391 | 390
2018-03-04 07:30 | 410 | 409
2018-03-04 08:00 | 422 | 422
2018-03-04 08:30 | 445 | 444
2018-03-04 09:00 | 471 | 470
2018-03-04 09:30 | 491 | 491
2018-03-04 10:00 | 496 | 496
2018-03-04 10:30 | 511 | 510
2018-03-04 11:00 | 519 | 519
2018-03-04 11:30 | 526 | 526
2018-03-04 12:00 | 537 | 536
2018-03-04 12:30 | 546 | 545
2018-03-04 13:00 | 564 | 563
2018-03-04 13:30 | 586 | 585
2018-03-04 14:00 | 599 | 599
2018-03-04 14:30 | 627 | 627
2018-03-04 15:00 | 649 | 649
2018-03-04 15:30 | 648 | 648
2018-03-04 16:00 | 661 | 660
2018-03-04 16:30 | 671 | 670
2018-03-04 17:00 | 671 | 670
2018-03-04 17:30 | 669 | 668
2018-03-04 18:00 | 668 | 667
2018-03-04 18:30 | 666 | 666
2018-03-04 19:00 | 665 | 664
2018-03-04 19:30 | 644 | 643
2018-03-04 20:00 | 634 | 633
2018-03-04 20:30 | 619 | 618
2018-03-04 21:00 | 586 | 584
2018-03-04 21:30 | 559 | 557
2018-03-04 22:00 | 533 | 530
2018-03-04 22:30 | 493 | 491
2018-03-04 23:00 | 470 | 469
2018-03-04 23:30 | 459 | 457
2018-03-05 | 439 | 436
2018-03-05 00:30 | 416 | 412
2018-03-05 01:00 | 404 | 398
2018-03-05 01:30 | 395 | 389
2018-03-05 02:00 | 390 | 385
2018-03-05 02:30 | 383 | 380
2018-03-05 03:00 | 383 | 380
2018-03-05 03:30 | 381 | 377
2018-03-05 04:00 | 375 | 372
2018-03-05 04:30 | 378 | 375
2018-03-05 05:00 | 393 | 391
2018-03-05 05:30 | 414 | 413
2018-03-05 06:00 | 439 | 437
2018-03-05 06:30 | 490 | 485
2018-03-05 07:00 | 519 | 515
2018-03-05 07:30 | 558 | 551
2018-03-05 08:00 | 573 | 566
2018-03-05 08:30 | 571 | 564
2018-03-05 09:00 | 569 | 561
2018-03-05 09:30 | 577 | 570
2018-03-05 10:00 | 585 | 579
2018-03-05 10:30 | 586 | 580
2018-03-05 11:00 | 591 | 583
2018-03-05 11:30 | 586 | 577
2018-03-05 12:00 | 587 | 579
2018-03-05 12:30 | 589 | 581
2018-03-05 13:00 | 585 | 577
2018-03-05 13:30 | 584 | 577
2018-03-05 14:00 | 590 | 584
2018-03-05 14:30 | 596 | 590
2018-03-05 15:00 | 597 | 592
2018-03-05 15:30 | 610 | 605
2018-03-05 16:00 | 621 | 616
2018-03-05 16:30 | 622 | 617
2018-03-05 17:00 | 632 | 626
2018-03-05 17:30 | 629 | 622
2018-03-05 18:00 | 618 | 611
2018-03-05 18:30 | 610 | 603
2018-03-05 19:00 | 617 | 612
2018-03-05 19:30 | 599 | 593
2018-03-05 20:00 | 581 | 580
2018-03-05 20:30 | 571 | 570
2018-03-05 21:00 | 548 | 547
2018-03-05 21:30 | 532 | 530
2018-03-05 22:00 | 510 | 507
2018-03-05 22:30 | 496 | 493
2018-03-05 23:00 | 483 | 481
2018-03-05 23:30 | 468 | 465
2018-03-06 | 441 | 436
2018-03-06 00:30 | 409 | 407
2018-03-06 01:00 | 389 | 387
2018-03-06 01:30 | 370 | 366
2018-03-06 02:00 | 353 | 350
2018-03-06 02:30 | 342 | 339
2018-03-06 03:00 | 332 | 328
2018-03-06 03:30 | 330 | 326
2018-03-06 04:00 | 330 | 327
2018-03-06 04:30 | 351 | 348
2018-03-06 05:00 | 369 | 367
2018-03-06 05:30 | 393 | 391
2018-03-06 06:00 | 412 | 411
2018-03-06 06:30 | 458 | 457
2018-03-06 07:00 | 477 | 476
2018-03-06 07:30 | 516 | 514
2018-03-06 08:00 | 519 | 518
2018-03-06 08:30 | 527 | 527
2018-03-06 09:00 | 526 | 526
2018-03-06 09:30 | 533 | 533
2018-03-06 10:00 | 540 | 539
2018-03-06 10:30 | 541 | 540
2018-03-06 11:00 | 540 | 540
2018-03-06 11:30 | 523 | 522
2018-03-06 12:00 | 507 | 506
2018-03-06 12:30 | 491 | 489
2018-03-06 13:00 | 494 | 493
2018-03-06 13:30 | 500 | 499
2018-03-06 14:00 | 501 | 501
2018-03-06 14:30 | 509 | 509
2018-03-06 15:00 | 505 | 504
2018-03-06 15:30 | 498 | 497
2018-03-06 16:00 | 507 | 506
2018-03-06 16:30 | 513 | 512
2018-03-06 17:00 | 515 | 513
2018-03-06 17:30 | 521 | 519
2018-03-06 18:00 | 521 | 519
2018-03-06 18:30 | 515 | 514
2018-03-06 19:00 | 525 | 524
2018-03-06 19:30 | 511 | 510
2018-03-06 20:00 | 503 | 502
2018-03-06 20:30 | 488 | 487
2018-03-06 21:00 | 473 | 472
2018-03-06 21:30 | 458 | 456
2018-03-06 22:00 | 440 | 437
2018-03-06 22:30 | 420 | 417
2018-03-06 23:00 | 415 | 413
2018-03-06 23:30 | 404 | 402
2018-03-07 | 391 | 389
2018-03-07 00:30 | 372 | 369
2018-03-07 01:00 | 359 | 355
2018-03-07 01:30 | 348 | 343
2018-03-07 02:00 | 340 | 334
2018-03-07 02:30 | 335 | 329
2018-03-07 03:00 | 329 | 322
2018-03-07 03:30 | 333 | 327
2018-03-07 04:00 | 337 | 331
2018-03-07 04:30 | 349 | 343
2018-03-07 05:00 | 357 | 352
2018-03-07 05:30 | 378 | 375
2018-03-07 06:00 | 406 | 404
2018-03-07 06:30 | 472 | 469
2018-03-07 07:00 | 502 | 496
2018-03-07 07:30 | 536 | 532
2018-03-07 08:00 | 544 | 532
2018-03-07 08:30 | 518 | 515
2018-03-07 09:00 | 510 | 507
2018-03-07 09:30 | 521 | 519
2018-03-07 10:00 | 520 | 518
2018-03-07 10:30 | 503 | 501
2018-03-07 11:00 | 495 | 493
2018-03-07 11:30 | 503 | 501
2018-03-07 12:00 | 505 | 503
2018-03-07 12:30 | 501 | 499
2018-03-07 13:00 | 495 | 493
2018-03-07 13:30 | 482 | 479
2018-03-07 14:00 | 484 | 482
2018-03-07 14:30 | 479 | 477
2018-03-07 15:00 | 478 | 476
2018-03-07 15:30 | 477 | 475
2018-03-07 16:00 | 485 | 483
2018-03-07 16:30 | 502 | 500
2018-03-07 17:00 | 516 | 513
2018-03-07 17:30 | 520 | 516
2018-03-07 18:00 | 519 | 517
2018-03-07 18:30 | 518 | 516
2018-03-07 19:00 | 524 | 522
2018-03-07 19:30 | 511 | 508
2018-03-07 20:00 | 507 | 504
2018-03-07 20:30 | 489 | 487
2018-03-07 21:00 | 469 | 467
2018-03-07 21:30 | 454 | 452
2018-03-07 22:00 | 437 | 435
2018-03-07 22:30 | 431 | 429
2018-03-07 23:00 | 424 | 422
2018-03-07 23:30 | 404 | 403
2018-03-08 | 390 | 387
2018-03-08 00:30 | 371 | 367
2018-03-08 01:00 | 363 | 358
2018-03-08 01:30 | 354 | 350
2018-03-08 02:00 | 349 | 344
2018-03-08 02:30 | 342 | 337
2018-03-08 03:00 | 343 | 338
2018-03-08 03:30 | 344 | 339
2018-03-08 04:00 | 347 | 342
2018-03-08 04:30 | 349 | 344
2018-03-08 05:00 | 371 | 367
2018-03-08 05:30 | 385 | 382
2018-03-08 06:00 | 401 | 399
2018-03-08 06:30 | 432 | 432
2018-03-08 07:00 | 451 | 451
2018-03-08 07:30 | 469 | 468
2018-03-08 08:00 | 473 | 472
2018-03-08 08:30 | 472 | 472
2018-03-08 09:00 | 470 | 470
2018-03-08 09:30 | 469 | 469
2018-03-08 10:00 | 461 | 461
2018-03-08 10:30 | 474 | 474
2018-03-08 11:00 | 476 | 476
2018-03-08 11:30 | 469 | 469
2018-03-08 12:00 | 486 | 486
2018-03-08 12:30 | 492 | 492
2018-03-08 13:00 | 491 | 491
2018-03-08 13:30 | 497 | 496
2018-03-08 14:00 | 495 | 495
2018-03-08 14:30 | 489 | 489
2018-03-08 15:00 | 488 | 488
2018-03-08 15:30 | 488 | 488
2018-03-08 16:00 | 500 | 500
2018-03-08 16:30 | 511 | 511
2018-03-08 17:00 | 516 | 515
2018-03-08 17:30 | 521 | 520
2018-03-08 18:00 | 528 | 527
2018-03-08 18:30 | 531 | 529
2018-03-08 19:00 | 543 | 541
2018-03-08 19:30 | 535 | 531
2018-03-08 20:00 | 518 | 515
2018-03-08 20:30 | 496 | 495
2018-03-08 21:00 | 469 | 469
2018-03-08 21:30 | 457 | 457
2018-03-08 22:00 | 451 | 451
2018-03-08 22:30 | 447 | 447
2018-03-08 23:00 | 431 | 430
2018-03-08 23:30 | 409 | 408
2018-03-09 | 396 | 394
2018-03-09 00:30 | 378 | 375
2018-03-09 01:00 | 372 | 368
2018-03-09 01:30 | 366 | 361
2018-03-09 02:00 | 356 | 351
2018-03-09 02:30 | 355 | 350
2018-03-09 03:00 | 356 | 350
2018-03-09 03:30 | 357 | 352
2018-03-09 04:00 | 360 | 355
2018-03-09 04:30 | 367 | 362
2018-03-09 05:00 | 370 | 366
2018-03-09 05:30 | 387 | 384
2018-03-09 06:00 | 405 | 402
2018-03-09 06:30 | 427 | 426
2018-03-09 07:00 | 446 | 446
2018-03-09 07:30 | 470 | 470
2018-03-09 08:00 | 471 | 471
2018-03-09 08:30 | 474 | 473
2018-03-09 09:00 | 473 | 472
2018-03-09 09:30 | 498 | 498
2018-03-09 10:00 | 491 | 491
2018-03-09 10:30 | 484 | 484
2018-03-09 11:00 | 488 | 487
2018-03-09 11:30 | 490 | 490
2018-03-09 12:00 | 495 | 494
2018-03-09 12:30 | 487 | 487
2018-03-09 13:00 | 482 | 482
2018-03-09 13:30 | 477 | 477
2018-03-09 14:00 | 491 | 491
2018-03-09 14:30 | 489 | 489
2018-03-09 15:00 | 487 | 486
2018-03-09 15:30 | 498 | 498
2018-03-09 16:00 | 497 | 497
2018-03-09 16:30 | 512 | 511
2018-03-09 17:00 | 523 | 522
2018-03-09 17:30 | 510 | 509
2018-03-09 18:00 | 500 | 499
2018-03-09 18:30 | 499 | 498
2018-03-09 19:00 | 514 | 513
2018-03-09 19:30 | 494 | 493
2018-03-09 20:00 | 491 | 490
2018-03-09 20:30 | 487 | 487
2018-03-09 21:00 | 475 | 474
2018-03-09 21:30 | 463 | 462
2018-03-09 22:00 | 446 | 445
2018-03-09 22:30 | 439 | 438
2018-03-09 23:00 | 434 | 432
2018-03-09 23:30 | 417 | 414
2018-03-10 | 389 | 386
2018-03-10 00:30 | 370 | 366
2018-03-10 01:00 | 365 | 361
2018-03-10 01:30 | 357 | 352
2018-03-10 02:00 | 347 | 341
2018-03-10 02:30 | 342 | 336
2018-03-10 03:00 | 339 | 333
2018-03-10 03:30 | 338 | 332
2018-03-10 04:00 | 330 | 323
2018-03-10 04:30 | 334 | 327
2018-03-10 05:00 | 336 | 329
2018-03-10 05:30 | 342 | 336
2018-03-10 06:00 | 353 | 347
2018-03-10 06:30 | 369 | 364
2018-03-10 07:00 | 382 | 378
2018-03-10 07:30 | 402 | 399
2018-03-10 08:00 | 410 | 409
2018-03-10 08:30 | 405 | 404
2018-03-10 09:00 | 424 | 423
2018-03-10 09:30 | 435 | 434
2018-03-10 10:00 | 440 | 439
2018-03-10 10:30 | 442 | 441
2018-03-10 11:00 | 418 | 417
2018-03-10 11:30 | 422 | 421
2018-03-10 12:00 | 404 | 403
2018-03-10 12:30 | 405 | 403
2018-03-10 13:00 | 407 | 406
2018-03-10 13:30 | 425 | 423
2018-03-10 14:00 | 412 | 410
2018-03-10 14:30 | 411 | 409
2018-03-10 15:00 | 421 | 420
2018-03-10 15:30 | 433 | 432
2018-03-10 16:00 | 432 | 431
2018-03-10 16:30 | 437 | 436
2018-03-10 17:00 | 451 | 450
2018-03-10 17:30 | 458 | 456
2018-03-10 18:00 | 457 | 456
2018-03-10 18:30 | 461 | 460
2018-03-10 19:00 | 475 | 474
2018-03-10 19:30 | 467 | 466
2018-03-10 20:00 | 456 | 455
2018-03-10 20:30 | 443 | 442
2018-03-10 21:00 | 426 | 424
2018-03-10 21:30 | 417 | 416
2018-03-10 22:00 | 419 | 417
2018-03-10 22:30 | 415 | 413
2018-03-10 23:00 | 403 | 402
2018-03-10 23:30 | 387 | 384
2018-03-11 | 370 | 367
2018-03-11 00:30 | 352 | 348
2018-03-11 01:00 | 349 | 343
2018-03-11 01:30 | 340 | 334
2018-03-11 02:00 | 332 | 324
2018-03-11 02:30 | 331 | 323
2018-03-11 03:00 | 327 | 320
2018-03-11 03:30 | 326 | 318
2018-03-11 04:00 | 326 | 318
2018-03-11 04:30 | 324 | 316
2018-03-11 05:00 | 325 | 316
2018-03-11 05:30 | 331 | 323
2018-03-11 06:00 | 336 | 327
2018-03-11 06:30 | 344 | 335
2018-03-11 07:00 | 346 | 338
2018-03-11 07:30 | 361 | 354
2018-03-11 08:00 | 373 | 368
2018-03-11 08:30 | 381 | 377
2018-03-11 09:00 | 395 | 391
2018-03-11 09:30 | 414 | 411
2018-03-11 10:00 | 417 | 414
2018-03-11 10:30 | 402 | 400
2018-03-11 11:00 | 410 | 408
2018-03-11 11:30 | 410 | 408
2018-03-11 12:00 | 401 | 399
2018-03-11 12:30 | 386 | 383
2018-03-11 13:00 | 424 | 422
2018-03-11 13:30 | 426 | 424
2018-03-11 14:00 | 409 | 407
2018-03-11 14:30 | 421 | 419
2018-03-11 15:00 | 427 | 425
2018-03-11 15:30 | 423 | 421
2018-03-11 16:00 | 432 | 430
2018-03-11 16:30 | 445 | 443
2018-03-11 17:00 | 452 | 451
2018-03-11 17:30 | 463 | 462
2018-03-11 18:00 | 466 | 465
2018-03-11 18:30 | 477 | 477
2018-03-11 19:00 | 495 | 495
2018-03-11 19:30 | 481 | 480
2018-03-11 20:00 | 471 | 470
2018-03-11 20:30 | 459 | 458
2018-03-11 21:00 | 450 | 449
2018-03-11 21:30 | 433 | 432
2018-03-11 22:00 | 423 | 422
2018-03-11 22:30 | 407 | 406
2018-03-11 23:00 | 386 | 384
2018-03-11 23:30 | 373 | 370
2018-03-12 | 353 | 350
2018-03-12 00:30 | 342 | 337
2018-03-12 01:00 | 333 | 328
2018-03-12 01:30 | 326 | 320
2018-03-12 02:00 | 316 | 309
2018-03-12 02:30 | 315 | 307
2018-03-12 03:00 | 316 | 308
2018-03-12 03:30 | 316 | 308
2018-03-12 04:00 | 318 | 310
2018-03-12 04:30 | 324 | 317
2018-03-12 05:00 | 337 | 331
2018-03-12 05:30 | 367 | 363
2018-03-12 06:00 | 380 | 377
2018-03-12 06:30 | 423 | 422
2018-03-12 07:00 | 444 | 443
2018-03-12 07:30 | 464 | 464
2018-03-12 08:00 | 477 | 477
2018-03-12 08:30 | 471 | 471
2018-03-12 09:00 | 454 | 454
2018-03-12 09:30 | 451 | 451
2018-03-12 10:00 | 438 | 438
2018-03-12 10:30 | 443 | 443
2018-03-12 11:00 | 443 | 443
2018-03-12 11:30 | 466 | 466
2018-03-12 12:00 | 482 | 482
2018-03-12 12:30 | 434 | 434
2018-03-12 13:00 | 461 | 461
2018-03-12 13:30 | 462 | 462
2018-03-12 14:00 | 469 | 469
2018-03-12 14:30 | 475 | 475
2018-03-12 15:00 | 492 | 492
2018-03-12 15:30 | 500 | 499
2018-03-12 16:00 | 512 | 511
2018-03-12 16:30 | 528 | 527
2018-03-12 17:00 | 542 | 541
2018-03-12 17:30 | 544 | 542
2018-03-12 18:00 | 533 | 531
2018-03-12 18:30 | 523 | 522
2018-03-12 19:00 | 533 | 532
2018-03-12 19:30 | 520 | 518
2018-03-12 20:00 | 517 | 514
2018-03-12 20:30 | 505 | 502
2018-03-12 21:00 | 484 | 482
2018-03-12 21:30 | 475 | 473
2018-03-12 22:00 | 461 | 459
2018-03-12 22:30 | 444 | 441
2018-03-12 23:00 | 428 | 426
2018-03-12 23:30 | 411 | 409
2018-03-13 | 389 | 387
2018-03-13 00:30 | 368 | 365
2018-03-13 01:00 | 360 | 355
2018-03-13 01:30 | 353 | 348
2018-03-13 02:00 | 344 | 339
2018-03-13 02:30 | 341 | 335
2018-03-13 03:00 | 342 | 336
2018-03-13 03:30 | 342 | 336
2018-03-13 04:00 | 344 | 337
2018-03-13 04:30 | 350 | 345
2018-03-13 05:00 | 353 | 349
2018-03-13 05:30 | 376 | 373
2018-03-13 06:00 | 401 | 398
2018-03-13 06:30 | 435 | 433
2018-03-13 07:00 | 451 | 450
2018-03-13 07:30 | 472 | 472
2018-03-13 08:00 | 483 | 483
2018-03-13 08:30 | 462 | 462
2018-03-13 09:00 | 467 | 467
2018-03-13 09:30 | 481 | 481
2018-03-13 10:00 | 492 | 492
2018-03-13 10:30 | 502 | 502
2018-03-13 11:00 | 503 | 502
2018-03-13 11:30 | 506 | 506
2018-03-13 12:00 | 505 | 504
2018-03-13 12:30 | 502 | 501
2018-03-13 13:00 | 508 | 507
2018-03-13 13:30 | 519 | 517
2018-03-13 14:00 | 514 | 512
2018-03-13 14:30 | 510 | 508
2018-03-13 15:00 | 513 | 511
2018-03-13 15:30 | 508 | 506
2018-03-13 16:00 | 506 | 504
2018-03-13 16:30 | 515 | 513
2018-03-13 17:00 | 525 | 524
2018-03-13 17:30 | 536 | 534
2018-03-13 18:00 | 536 | 534
2018-03-13 18:30 | 531 | 529
2018-03-13 19:00 | 536 | 535
2018-03-13 19:30 | 524 | 522
2018-03-13 20:00 | 513 | 510
2018-03-13 20:30 | 496 | 494
2018-03-13 21:00 | 465 | 465
2018-03-13 21:30 | 455 | 453
2018-03-13 22:00 | 439 | 437
2018-03-13 22:30 | 430 | 429
2018-03-13 23:00 | 419 | 417
2018-03-13 23:30 | 405 | 403
2018-03-14 | 387 | 385
2018-03-14 00:30 | 369 | 367
2018-03-14 01:00 | 362 | 359
2018-03-14 01:30 | 354 | 351
2018-03-14 02:00 | 349 | 346
2018-03-14 02:30 | 340 | 336
2018-03-14 03:00 | 332 | 328
2018-03-14 03:30 | 333 | 329
2018-03-14 04:00 | 331 | 328
2018-03-14 04:30 | 341 | 338
2018-03-14 05:00 | 344 | 341
2018-03-14 05:30 | 361 | 360
2018-03-14 06:00 | 382 | 382
2018-03-14 06:30 | 419 | 419
2018-03-14 07:00 | 445 | 445
2018-03-14 07:30 | 468 | 468
2018-03-14 08:00 | 473 | 473
2018-03-14 08:30 | 465 | 465
2018-03-14 09:00 | 453 | 452
2018-03-14 09:30 | 468 | 468
2018-03-14 10:00 | 468 | 468
2018-03-14 10:30 | 471 | 470
2018-03-14 11:00 | 465 | 464
2018-03-14 11:30 | 437 | 437
2018-03-14 12:00 | 455 | 455
2018-03-14 12:30 | 480 | 480
2018-03-14 13:00 | 487 | 487
2018-03-14 13:30 | 485 | 485
2018-03-14 14:00 | 490 | 490
2018-03-14 14:30 | 497 | 497
2018-03-14 15:00 | 504 | 504
2018-03-14 15:30 | 517 | 517
2018-03-14 16:00 | 533 | 533
2018-03-14 16:30 | 547 | 547
2018-03-14 17:00 | 556 | 556
2018-03-14 17:30 | 552 | 552
2018-03-14 18:00 | 544 | 543
2018-03-14 18:30 | 538 | 537
2018-03-14 19:00 | 554 | 553
2018-03-14 19:30 | 538 | 537
2018-03-14 20:00 | 522 | 521
2018-03-14 20:30 | 504 | 504
2018-03-14 21:00 | 479 | 479
2018-03-14 21:30 | 463 | 463
2018-03-14 22:00 | 448 | 448
2018-03-14 22:30 | 437 | 436
2018-03-14 23:00 | 423 | 422
2018-03-14 23:30 | 407 | 407
2018-03-15 | 390 | 389
2018-03-15 00:30 | 371 | 369
2018-03-15 01:00 | 361 | 358
2018-03-15 01:30 | 344 | 340
2018-03-15 02:00 | 337 | 333
2018-03-15 02:30 | 332 | 328
2018-03-15 03:00 | 332 | 328
2018-03-15 03:30 | 332 | 327
2018-03-15 04:00 | 336 | 332
2018-03-15 04:30 | 339 | 336
2018-03-15 05:00 | 349 | 346
2018-03-15 05:30 | 367 | 365
2018-03-15 06:00 | 389 | 388
2018-03-15 06:30 | 430 | 430
2018-03-15 07:00 | 452 | 452
2018-03-15 07:30 | 488 | 487
2018-03-15 08:00 | 507 | 507
2018-03-15 08:30 | 510 | 510
2018-03-15 09:00 | 492 | 492
2018-03-15 09:30 | 483 | 483
2018-03-15 10:00 | 484 | 484
2018-03-15 10:30 | 485 | 485
2018-03-15 11:00 | 495 | 495
2018-03-15 11:30 | 499 | 498
2018-03-15 12:00 | 509 | 508
2018-03-15 12:30 | 513 | 513
2018-03-15 13:00 | 525 | 524
2018-03-15 13:30 | 540 | 539
2018-03-15 14:00 | 547 | 546
2018-03-15 14:30 | 561 | 561
2018-03-15 15:00 | 571 | 570
2018-03-15 15:30 | 570 | 569
2018-03-15 16:00 | 584 | 583
2018-03-15 16:30 | 592 | 592
2018-03-15 17:00 | 603 | 602
2018-03-15 17:30 | 595 | 594
2018-03-15 18:00 | 587 | 585
2018-03-15 18:30 | 588 | 585
2018-03-15 19:00 | 604 | 602
2018-03-15 19:30 | 585 | 583
2018-03-15 20:00 | 568 | 566
2018-03-15 20:30 | 552 | 551
2018-03-15 21:00 | 521 | 519
2018-03-15 21:30 | 487 | 485
2018-03-15 22:00 | 462 | 459
2018-03-15 22:30 | 450 | 448
2018-03-15 23:00 | 437 | 434
2018-03-15 23:30 | 408 | 407
2018-03-16 | 389 | 388
2018-03-16 00:30 | 372 | 370
2018-03-16 01:00 | 362 | 359
2018-03-16 01:30 | 349 | 346
2018-03-16 02:00 | 343 | 339
2018-03-16 02:30 | 339 | 335
2018-03-16 03:00 | 339 | 334
2018-03-16 03:30 | 340 | 335
2018-03-16 04:00 | 340 | 336
2018-03-16 04:30 | 347 | 342
2018-03-16 05:00 | 347 | 343
2018-03-16 05:30 | 366 | 363
2018-03-16 06:00 | 392 | 390
2018-03-16 06:30 | 429 | 428
2018-03-16 07:00 | 451 | 450
2018-03-16 07:30 | 476 | 475
2018-03-16 08:00 | 487 | 485
2018-03-16 08:30 | 489 | 487
2018-03-16 09:00 | 483 | 481
2018-03-16 09:30 | 491 | 489
2018-03-16 10:00 | 496 | 494
2018-03-16 10:30 | 498 | 497
2018-03-16 11:00 | 491 | 490
2018-03-16 11:30 | 490 | 489
2018-03-16 12:00 | 485 | 484
2018-03-16 12:30 | 499 | 498
2018-03-16 13:00 | 515 | 514
2018-03-16 13:30 | 530 | 530
2018-03-16 14:00 | 526 | 526
2018-03-16 14:30 | 536 | 535
2018-03-16 15:00 | 550 | 549
2018-03-16 15:30 | 559 | 558
2018-03-16 16:00 | 573 | 573
2018-03-16 16:30 | 590 | 590
2018-03-16 17:00 | 594 | 593
2018-03-16 17:30 | 585 | 584
2018-03-16 18:00 | 566 | 563
2018-03-16 18:30 | 553 | 550
2018-03-16 19:00 | 559 | 556
2018-03-16 19:30 | 545 | 542
2018-03-16 20:00 | 538 | 536
2018-03-16 20:30 | 531 | 530
2018-03-16 21:00 | 507 | 505
2018-03-16 21:30 | 491 | 488
2018-03-16 22:00 | 472 | 470
2018-03-16 22:30 | 448 | 447
2018-03-16 23:00 | 440 | 438
2018-03-16 23:30 | 426 | 423
2018-03-17 | 393 | 391
2018-03-17 00:30 | 372 | 370
2018-03-17 01:00 | 366 | 362
2018-03-17 01:30 | 361 | 357
2018-03-17 02:00 | 349 | 344
2018-03-17 02:30 | 341 | 337
2018-03-17 03:00 | 336 | 331
2018-03-17 03:30 | 334 | 329
2018-03-17 04:00 | 335 | 330
2018-03-17 04:30 | 335 | 330
2018-03-17 05:00 | 337 | 333
2018-03-17 05:30 | 348 | 344
2018-03-17 06:00 | 357 | 352
2018-03-17 06:30 | 366 | 362
2018-03-17 07:00 | 371 | 368
2018-03-17 07:30 | 386 | 384
2018-03-17 08:00 | 386 | 385
2018-03-17 08:30 | 398 | 398
2018-03-17 09:00 | 400 | 400
2018-03-17 09:30 | 404 | 404
2018-03-17 10:00 | 401 | 401
2018-03-17 10:30 | 399 | 399
2018-03-17 11:00 | 399 | 399
2018-03-17 11:30 | 400 | 400
2018-03-17 12:00 | 406 | 406
2018-03-17 12:30 | 413 | 413
2018-03-17 13:00 | 430 | 429
2018-03-17 13:30 | 452 | 452
2018-03-17 14:00 | 456 | 455
2018-03-17 14:30 | 472 | 471
2018-03-17 15:00 | 484 | 483
2018-03-17 15:30 | 498 | 497
2018-03-17 16:00 | 506 | 505
2018-03-17 16:30 | 515 | 515
2018-03-17 17:00 | 537 | 535
2018-03-17 17:30 | 540 | 534
2018-03-17 18:00 | 523 | 516
2018-03-17 18:30 | 510 | 505
2018-03-17 19:00 | 528 | 524
2018-03-17 19:30 | 514 | 510
2018-03-17 20:00 | 501 | 501
2018-03-17 20:30 | 491 | 491
2018-03-17 21:00 | 466 | 466
2018-03-17 21:30 | 454 | 454
2018-03-17 22:00 | 435 | 435
2018-03-17 22:30 | 434 | 434
2018-03-17 23:00 | 430 | 430
2018-03-17 23:30 | 402 | 401
2018-03-18 | 378 | 377
2018-03-18 00:30 | 353 | 351
2018-03-18 01:00 | 347 | 344
2018-03-18 01:30 | 338 | 336
2018-03-18 02:00 | 323 | 320
2018-03-18 02:30 | 318 | 315
2018-03-18 03:00 | 315 | 312
2018-03-18 03:30 | 315 | 311
2018-03-18 04:00 | 318 | 314
2018-03-18 04:30 | 319 | 315
2018-03-18 05:00 | 319 | 314
2018-03-18 05:30 | 313 | 309
2018-03-18 06:00 | 318 | 313
2018-03-18 06:30 | 333 | 328
2018-03-18 07:00 | 341 | 336
2018-03-18 07:30 | 320 | 318
2018-03-18 08:00 | 316 | 315
2018-03-18 08:30 | 329 | 328
2018-03-18 09:00 | 345 | 345
2018-03-18 09:30 | 362 | 361
2018-03-18 10:00 | 368 | 368
2018-03-18 10:30 | 372 | 372
2018-03-18 11:00 | 377 | 377
2018-03-18 11:30 | 376 | 375
2018-03-18 12:00 | 394 | 394
2018-03-18 12:30 | 407 | 406
2018-03-18 13:00 | 428 | 428
2018-03-18 13:30 | 439 | 439
2018-03-18 14:00 | 457 | 457
2018-03-18 14:30 | 477 | 477
2018-03-18 15:00 | 501 | 500
2018-03-18 15:30 | 514 | 514
2018-03-18 16:00 | 542 | 542
2018-03-18 16:30 | 543 | 542
2018-03-18 17:00 | 553 | 552
2018-03-18 17:30 | 557 | 556
2018-03-18 18:00 | 548 | 547
2018-03-18 18:30 | 557 | 556
2018-03-18 19:00 | 564 | 563
2018-03-18 19:30 | 552 | 551
2018-03-18 20:00 | 545 | 544
2018-03-18 20:30 | 533 | 532
2018-03-18 21:00 | 506 | 505
2018-03-18 21:30 | 476 | 475
2018-03-18 22:00 | 449 | 448
2018-03-18 22:30 | 438 | 437
2018-03-18 23:00 | 421 | 420
2018-03-18 23:30 | 410 | 409
2018-03-19 | 382 | 381
2018-03-19 00:30 | 359 | 357
2018-03-19 01:00 | 347 | 345
2018-03-19 01:30 | 341 | 340
2018-03-19 02:00 | 331 | 329
2018-03-19 02:30 | 333 | 331
2018-03-19 03:00 | 333 | 331
2018-03-19 03:30 | 333 | 331
2018-03-19 04:00 | 338 | 336
2018-03-19 04:30 | 352 | 350
2018-03-19 05:00 | 364 | 362
2018-03-19 05:30 | 387 | 386
2018-03-19 06:00 | 408 | 407
2018-03-19 06:30 | 453 | 452
2018-03-19 07:00 | 486 | 486
2018-03-19 07:30 | 510 | 507
2018-03-19 08:00 | 521 | 517
2018-03-19 08:30 | 531 | 527
2018-03-19 09:00 | 544 | 540
2018-03-19 09:30 | 539 | 536
2018-03-19 10:00 | 538 | 535
2018-03-19 10:30 | 539 | 537
2018-03-19 11:00 | 547 | 544
2018-03-19 11:30 | 553 | 550
2018-03-19 12:00 | 565 | 561
2018-03-19 12:30 | 578 | 575
2018-03-19 13:00 | 592 | 589
2018-03-19 13:30 | 600 | 597
2018-03-19 14:00 | 610 | 608
2018-03-19 14:30 | 618 | 616
2018-03-19 15:00 | 628 | 625
2018-03-19 15:30 | 637 | 633
2018-03-19 16:00 | 660 | 657
2018-03-19 16:30 | 684 | 682
2018-03-19 17:00 | 693 | 690
2018-03-19 17:30 | 688 | 683
2018-03-19 18:00 | 675 | 667
2018-03-19 18:30 | 667 | 658
2018-03-19 19:00 | 659 | 651
2018-03-19 19:30 | 642 | 632
2018-03-19 20:00 | 612 | 610
2018-03-19 20:30 | 595 | 593
2018-03-19 21:00 | 576 | 575
2018-03-19 21:30 | 557 | 555
2018-03-19 22:00 | 521 | 518
2018-03-19 22:30 | 502 | 500
2018-03-19 23:00 | 482 | 479
2018-03-19 23:30 | 453 | 451
2018-03-20 | 425 | 424
2018-03-20 00:30 | 401 | 400
2018-03-20 01:00 | 385 | 384
2018-03-20 01:30 | 377 | 376
2018-03-20 02:00 | 370 | 368
2018-03-20 02:30 | 369 | 367
2018-03-20 03:00 | 364 | 362
2018-03-20 03:30 | 363 | 361
2018-03-20 04:00 | 368 | 366
2018-03-20 04:30 | 371 | 370
2018-03-20 05:00 | 382 | 381
2018-03-20 05:30 | 392 | 391
2018-03-20 06:00 | 418 | 418
2018-03-20 06:30 | 470 | 470
2018-03-20 07:00 | 512 | 511
2018-03-20 07:30 | 540 | 539
2018-03-20 08:00 | 548 | 547
2018-03-20 08:30 | 548 | 548
2018-03-20 09:00 | 537 | 537
2018-03-20 09:30 | 536 | 536
2018-03-20 10:00 | 532 | 532
2018-03-20 10:30 | 539 | 539
2018-03-20 11:00 | 544 | 544
2018-03-20 11:30 | 543 | 542
2018-03-20 12:00 | 555 | 555
2018-03-20 12:30 | 569 | 568
2018-03-20 13:00 | 571 | 570
2018-03-20 13:30 | 574 | 574
2018-03-20 14:00 | 576 | 576
2018-03-20 14:30 | 575 | 574
2018-03-20 15:00 | 568 | 568
2018-03-20 15:30 | 575 | 575
2018-03-20 16:00 | 586 | 585
2018-03-20 16:30 | 594 | 593
2018-03-20 17:00 | 592 | 591
2018-03-20 17:30 | 591 | 589
2018-03-20 18:00 | 581 | 577
2018-03-20 18:30 | 574 | 572
2018-03-20 19:00 | 580 | 578
2018-03-20 19:30 | 564 | 563
2018-03-20 20:00 | 550 | 549
2018-03-20 20:30 | 535 | 533
2018-03-20 21:00 | 516 | 515
2018-03-20 21:30 | 493 | 492
2018-03-20 22:00 | 472 | 472
2018-03-20 22:30 | 463 | 462
2018-03-20 23:00 | 438 | 437
2018-03-20 23:30 | 418 | 416
2018-03-21 | 391 | 390
2018-03-21 00:30 | 368 | 366
2018-03-21 01:00 | 354 | 353
2018-03-21 01:30 | 339 | 337
2018-03-21 02:00 | 328 | 326
2018-03-21 02:30 | 333 | 330
2018-03-21 03:00 | 332 | 329
2018-03-21 03:30 | 332 | 329
2018-03-21 04:00 | 340 | 337
2018-03-21 04:30 | 352 | 350
2018-03-21 05:00 | 371 | 368
2018-03-21 05:30 | 396 | 395
2018-03-21 06:00 | 424 | 423
2018-03-21 06:30 | 459 | 459
2018-03-21 07:00 | 482 | 482
2018-03-21 07:30 | 495 | 495
2018-03-21 08:00 | 511 | 511
2018-03-21 08:30 | 515 | 515
2018-03-21 09:00 | 518 | 518
2018-03-21 09:30 | 518 | 518
2018-03-21 10:00 | 528 | 528
2018-03-21 10:30 | 521 | 520
2018-03-21 11:00 | 510 | 510
2018-03-21 11:30 | 524 | 523
2018-03-21 12:00 | 519 | 519
2018-03-21 12:30 | 522 | 521
2018-03-21 13:00 | 529 | 529
2018-03-21 13:30 | 514 | 514
2018-03-21 14:00 | 511 | 510
2018-03-21 14:30 | 505 | 505
2018-03-21 15:00 | 518 | 518
2018-03-21 15:30 | 530 | 530
2018-03-21 16:00 | 541 | 540
2018-03-21 16:30 | 550 | 549
2018-03-21 17:00 | 551 | 549
2018-03-21 17:30 | 552 | 551
2018-03-21 18:00 | 550 | 549
2018-03-21 18:30 | 550 | 549
2018-03-21 19:00 | 545 | 544
2018-03-21 19:30 | 529 | 527
2018-03-21 20:00 | 520 | 519
2018-03-21 20:30 | 513 | 512
2018-03-21 21:00 | 492 | 491
2018-03-21 21:30 | 470 | 470
2018-03-21 22:00 | 457 | 456
2018-03-21 22:30 | 453 | 453
2018-03-21 23:00 | 445 | 444
2018-03-21 23:30 | 426 | 425
2018-03-22 | 404 | 402
2018-03-22 00:30 | 382 | 379
2018-03-22 01:00 | 369 | 368
2018-03-22 01:30 | 347 | 345
2018-03-22 02:00 | 339 | 336
2018-03-22 02:30 | 345 | 343
2018-03-22 03:00 | 361 | 359
2018-03-22 03:30 | 370 | 367
2018-03-22 04:00 | 370 | 367
2018-03-22 04:30 | 369 | 367
2018-03-22 05:00 | 372 | 370
2018-03-22 05:30 | 392 | 391
2018-03-22 06:00 | 413 | 412
2018-03-22 06:30 | 450 | 450
2018-03-22 07:00 | 487 | 486
2018-03-22 07:30 | 513 | 513
2018-03-22 08:00 | 516 | 516
2018-03-22 08:30 | 520 | 519
2018-03-22 09:00 | 519 | 519
2018-03-22 09:30 | 505 | 504
2018-03-22 10:00 | 502 | 501
2018-03-22 10:30 | 514 | 513
2018-03-22 11:00 | 526 | 526
2018-03-22 11:30 | 507 | 505
2018-03-22 12:00 | 500 | 499
2018-03-22 12:30 | 488 | 487
2018-03-22 13:00 | 495 | 495
2018-03-22 13:30 | 490 | 489
2018-03-22 14:00 | 498 | 498
2018-03-22 14:30 | 504 | 504
2018-03-22 15:00 | 508 | 508
2018-03-22 15:30 | 526 | 526
2018-03-22 16:00 | 545 | 545
2018-03-22 16:30 | 555 | 555
2018-03-22 17:00 | 569 | 568
2018-03-22 17:30 | 568 | 567
2018-03-22 18:00 | 565 | 564
2018-03-22 18:30 | 561 | 559
2018-03-22 19:00 | 555 | 554
2018-03-22 19:30 | 540 | 538
2018-03-22 20:00 | 533 | 532
2018-03-22 20:30 | 525 | 523
2018-03-22 21:00 | 502 | 500
2018-03-22 21:30 | 479 | 477
2018-03-22 22:00 | 456 | 455
2018-03-22 22:30 | 444 | 444
2018-03-22 23:00 | 437 | 436
2018-03-22 23:30 | 422 | 421
2018-03-23 | 399 | 397
2018-03-23 00:30 | 378 | 375
2018-03-23 01:00 | 369 | 365
2018-03-23 01:30 | 352 | 348
2018-03-23 02:00 | 343 | 338
2018-03-23 02:30 | 343 | 338
2018-03-23 03:00 | 345 | 340
2018-03-23 03:30 | 348 | 343
2018-03-23 04:00 | 344 | 339
2018-03-23 04:30 | 347 | 343
2018-03-23 05:00 | 351 | 347
2018-03-23 05:30 | 377 | 374
2018-03-23 06:00 | 397 | 396
2018-03-23 06:30 | 434 | 433
2018-03-23 07:00 | 465 | 465
2018-03-23 07:30 | 487 | 487
2018-03-23 08:00 | 495 | 495
2018-03-23 08:30 | 506 | 506
2018-03-23 09:00 | 494 | 493
2018-03-23 09:30 | 502 | 502
2018-03-23 10:00 | 517 | 517
2018-03-23 10:30 | 500 | 500
2018-03-23 11:00 | 498 | 498
2018-03-23 11:30 | 492 | 492
2018-03-23 12:00 | 497 | 497
2018-03-23 12:30 | 494 | 493
2018-03-23 13:00 | 493 | 492
2018-03-23 13:30 | 510 | 509
2018-03-23 14:00 | 525 | 524
2018-03-23 14:30 | 527 | 526
2018-03-23 15:00 | 532 | 532
2018-03-23 15:30 | 527 | 527
2018-03-23 16:00 | 525 | 525
2018-03-23 16:30 | 540 | 540
2018-03-23 17:00 | 545 | 545
2018-03-23 17:30 | 537 | 536
2018-03-23 18:00 | 530 | 528
2018-03-23 18:30 | 526 | 525
2018-03-23 19:00 | 527 | 527
2018-03-23 19:30 | 517 | 516
2018-03-23 20:00 | 514 | 513
2018-03-23 20:30 | 507 | 505
2018-03-23 21:00 | 488 | 486
2018-03-23 21:30 | 473 | 471
2018-03-23 22:00 | 460 | 458
2018-03-23 22:30 | 448 | 446
2018-03-23 23:00 | 433 | 431
2018-03-23 23:30 | 413 | 410
2018-03-24 | 386 | 384
2018-03-24 00:30 | 369 | 366
2018-03-24 01:00 | 356 | 353
2018-03-24 01:30 | 348 | 344
2018-03-24 02:00 | 338 | 334
2018-03-24 02:30 | 333 | 328
2018-03-24 03:00 | 330 | 325
2018-03-24 03:30 | 331 | 325
2018-03-24 04:00 | 332 | 326
2018-03-24 04:30 | 337 | 331
2018-03-24 05:00 | 335 | 329
2018-03-24 05:30 | 347 | 342
2018-03-24 06:00 | 356 | 351
2018-03-24 06:30 | 372 | 367
2018-03-24 07:00 | 389 | 385
2018-03-24 07:30 | 403 | 400
2018-03-24 08:00 | 416 | 414
2018-03-24 08:30 | 438 | 437
2018-03-24 09:00 | 434 | 433
2018-03-24 09:30 | 438 | 437
2018-03-24 10:00 | 436 | 435
2018-03-24 10:30 | 438 | 438
2018-03-24 11:00 | 440 | 440
2018-03-24 11:30 | 440 | 440
2018-03-24 12:00 | 435 | 435
2018-03-24 12:30 | 427 | 427
2018-03-24 13:00 | 419 | 419
2018-03-24 13:30 | 417 | 417
2018-03-24 14:00 | 423 | 423
2018-03-24 14:30 | 435 | 435
2018-03-24 15:00 | 447 | 447
2018-03-24 15:30 | 457 | 457
2018-03-24 16:00 | 482 | 482
2018-03-24 16:30 | 491 | 491
2018-03-24 17:00 | 498 | 498
2018-03-24 17:30 | 494 | 493
2018-03-24 18:00 | 491 | 490
2018-03-24 18:30 | 506 | 506
2018-03-24 19:00 | 507 | 506
2018-03-24 19:30 | 491 | 490
2018-03-24 20:00 | 479 | 478
2018-03-24 20:30 | 470 | 469
2018-03-24 21:00 | 459 | 458
2018-03-24 21:30 | 447 | 446
2018-03-24 22:00 | 439 | 438
2018-03-24 22:30 | 429 | 427
2018-03-24 23:00 | 410 | 409
2018-03-24 23:30 | 388 | 387
2018-03-25 | 365 | 363
2018-03-25 00:30 | 346 | 343
2018-03-25 01:00 | 328 | 325
2018-03-25 01:30 | 320 | 316
2018-03-25 02:00 | 311 | 307
2018-03-25 02:30 | 313 | 308
2018-03-25 03:00 | 312 | 307
2018-03-25 03:30 | 302 | 296
2018-03-25 04:00 | 290 | 284
2018-03-25 04:30 | 290 | 283
2018-03-25 05:00 | 293 | 286
2018-03-25 05:30 | 320 | 313
2018-03-25 06:00 | 330 | 324
2018-03-25 06:30 | 336 | 329
2018-03-25 07:00 | 343 | 336
2018-03-25 07:30 | 358 | 354
2018-03-25 08:00 | 359 | 355
2018-03-25 08:30 | 363 | 361
2018-03-25 09:00 | 369 | 368
2018-03-25 09:30 | 379 | 379
2018-03-25 10:00 | 392 | 391
2018-03-25 10:30 | 396 | 396
2018-03-25 11:00 | 401 | 401
2018-03-25 11:30 | 395 | 395
2018-03-25 12:00 | 391 | 391
2018-03-25 12:30 | 405 | 405
2018-03-25 13:00 | 405 | 404
2018-03-25 13:30 | 407 | 407
2018-03-25 14:00 | 419 | 419
2018-03-25 14:30 | 428 | 428
2018-03-25 15:00 | 428 | 427
2018-03-25 15:30 | 454 | 453
2018-03-25 16:00 | 473 | 472
2018-03-25 16:30 | 484 | 484
2018-03-25 17:00 | 494 | 494
2018-03-25 17:30 | 497 | 497
2018-03-25 18:00 | 495 | 495
2018-03-25 18:30 | 513 | 512
2018-03-25 19:00 | 513 | 512
2018-03-25 19:30 | 496 | 494
2018-03-25 20:00 | 476 | 474
2018-03-25 20:30 | 469 | 468
2018-03-25 21:00 | 446 | 446
2018-03-25 21:30 | 419 | 419
2018-03-25 22:00 | 407 | 406
2018-03-25 22:30 | 399 | 399
2018-03-25 23:00 | 394 | 393
2018-03-25 23:30 | 379 | 378
2018-03-26 | 361 | 360
2018-03-26 00:30 | 348 | 346
2018-03-26 01:00 | 341 | 337
2018-03-26 01:30 | 330 | 326
2018-03-26 02:00 | 325 | 321
2018-03-26 02:30 | 325 | 320
2018-03-26 03:00 | 308 | 303
2018-03-26 03:30 | 310 | 305
2018-03-26 04:00 | 322 | 318
2018-03-26 04:30 | 347 | 343
2018-03-26 05:00 | 359 | 356
2018-03-26 05:30 | 389 | 388
2018-03-26 06:00 | 430 | 429
2018-03-26 06:30 | 473 | 473
2018-03-26 07:00 | 503 | 502
2018-03-26 07:30 | 529 | 528
2018-03-26 08:00 | 542 | 541
2018-03-26 08:30 | 548 | 546
2018-03-26 09:00 | 554 | 550
2018-03-26 09:30 | 559 | 559
2018-03-26 10:00 | 562 | 561
2018-03-26 10:30 | 567 | 565
2018-03-26 11:00 | 571 | 569
2018-03-26 11:30 | 567 | 566
2018-03-26 12:00 | 568 | 567
2018-03-26 12:30 | 570 | 568
2018-03-26 13:00 | 558 | 556
2018-03-26 13:30 | 559 | 557
2018-03-26 14:00 | 563 | 560
2018-03-26 14:30 | 572 | 569
2018-03-26 15:00 | 583 | 581
2018-03-26 15:30 | 590 | 588
2018-03-26 16:00 | 598 | 596
2018-03-26 16:30 | 602 | 600
2018-03-26 17:00 | 615 | 613
2018-03-26 17:30 | 616 | 615
2018-03-26 18:00 | 612 | 611
2018-03-26 18:30 | 616 | 616
2018-03-26 19:00 | 618 | 617
2018-03-26 19:30 | 597 | 597
2018-03-26 20:00 | 589 | 589
2018-03-26 20:30 | 575 | 574
2018-03-26 21:00 | 550 | 550
2018-03-26 21:30 | 535 | 534
2018-03-26 22:00 | 508 | 508
2018-03-26 22:30 | 490 | 490
2018-03-26 23:00 | 477 | 477
2018-03-26 23:30 | 455 | 455
2018-03-27 | 436 | 436
2018-03-27 00:30 | 417 | 417
2018-03-27 01:00 | 405 | 405
2018-03-27 01:30 | 391 | 390
2018-03-27 02:00 | 378 | 378
2018-03-27 02:30 | 377 | 376
2018-03-27 03:00 | 376 | 375
2018-03-27 03:30 | 377 | 376
2018-03-27 04:00 | 377 | 376
2018-03-27 04:30 | 384 | 383
2018-03-27 05:00 | 392 | 391
2018-03-27 05:30 | 421 | 421
2018-03-27 06:00 | 449 | 448
2018-03-27 06:30 | 481 | 480
2018-03-27 07:00 | 506 | 505
2018-03-27 07:30 | 532 | 532
2018-03-27 08:00 | 552 | 549
2018-03-27 08:30 | 552 | 551
2018-03-27 09:00 | 555 | 553
2018-03-27 09:30 | 565 | 564
2018-03-27 10:00 | 569 | 567
2018-03-27 10:30 | 572 | 570
2018-03-27 11:00 | 565 | 563
2018-03-27 11:30 | 569 | 567
2018-03-27 12:00 | 576 | 574
2018-03-27 12:30 | 578 | 575
2018-03-27 13:00 | 570 | 567
2018-03-27 13:30 | 555 | 550
2018-03-27 14:00 | 530 | 525
2018-03-27 14:30 | 539 | 534
2018-03-27 15:00 | 552 | 548
2018-03-27 15:30 | 570 | 567
2018-03-27 16:00 | 576 | 573
2018-03-27 16:30 | 582 | 579
2018-03-27 17:00 | 587 | 583
2018-03-27 17:30 | 584 | 579
2018-03-27 18:00 | 582 | 576
2018-03-27 18:30 | 576 | 570
2018-03-27 19:00 | 572 | 565
2018-03-27 19:30 | 555 | 548
2018-03-27 20:00 | 549 | 544
2018-03-27 20:30 | 540 | 536
2018-03-27 21:00 | 512 | 511
2018-03-27 21:30 | 500 | 500
2018-03-27 22:00 | 481 | 481
2018-03-27 22:30 | 451 | 451
2018-03-27 23:00 | 433 | 432
2018-03-27 23:30 | 408 | 408
2018-03-28 | 377 | 377
2018-03-28 00:30 | 357 | 357
2018-03-28 01:00 | 349 | 349
2018-03-28 01:30 | 342 | 341
2018-03-28 02:00 | 330 | 329
2018-03-28 02:30 | 318 | 316
2018-03-28 03:00 | 312 | 310
2018-03-28 03:30 | 317 | 316
2018-03-28 04:00 | 318 | 316
2018-03-28 04:30 | 333 | 332
2018-03-28 05:00 | 360 | 359
2018-03-28 05:30 | 372 | 372
2018-03-28 06:00 | 396 | 396
2018-03-28 06:30 | 446 | 445
2018-03-28 07:00 | 471 | 469
2018-03-28 07:30 | 491 | 490
2018-03-28 08:00 | 500 | 500
2018-03-28 08:30 | 505 | 505
2018-03-28 09:00 | 510 | 510
2018-03-28 09:30 | 511 | 511
2018-03-28 10:00 | 508 | 508
2018-03-28 10:30 | 514 | 514
2018-03-28 11:00 | 521 | 520
2018-03-28 11:30 | 515 | 515
2018-03-28 12:00 | 514 | 513
2018-03-28 12:30 | 517 | 516
2018-03-28 13:00 | 523 | 523
2018-03-28 13:30 | 536 | 536
2018-03-28 14:00 | 547 | 547
2018-03-28 14:30 | 559 | 559
2018-03-28 15:00 | 573 | 572
2018-03-28 15:30 | 589 | 589
2018-03-28 16:00 | 599 | 598
2018-03-28 16:30 | 612 | 611
2018-03-28 17:00 | 624 | 623
2018-03-28 17:30 | 617 | 616
2018-03-28 18:00 | 606 | 605
2018-03-28 18:30 | 599 | 598
2018-03-28 19:00 | 597 | 595
2018-03-28 19:30 | 580 | 576
2018-03-28 20:00 | 567 | 566
2018-03-28 20:30 | 555 | 553
2018-03-28 21:00 | 531 | 528
2018-03-28 21:30 | 513 | 511
2018-03-28 22:00 | 495 | 493
2018-03-28 22:30 | 486 | 483
2018-03-28 23:00 | 464 | 461
2018-03-28 23:30 | 445 | 441
2018-03-29 | 426 | 421
2018-03-29 00:30 | 408 | 404
2018-03-29 01:00 | 397 | 392
2018-03-29 01:30 | 389 | 384
2018-03-29 02:00 | 376 | 368
2018-03-29 02:30 | 372 | 364
2018-03-29 03:00 | 375 | 367
2018-03-29 03:30 | 378 | 371
2018-03-29 04:00 | 384 | 377
2018-03-29 04:30 | 387 | 380
2018-03-29 05:00 | 396 | 391
2018-03-29 05:30 | 416 | 414
2018-03-29 06:00 | 446 | 443
2018-03-29 06:30 | 478 | 475
2018-03-29 07:00 | 501 | 500
2018-03-29 07:30 | 543 | 541
2018-03-29 08:00 | 556 | 546
2018-03-29 08:30 | 566 | 559
2018-03-29 09:00 | 568 | 560
2018-03-29 09:30 | 582 | 576
2018-03-29 10:00 | 576 | 570
2018-03-29 10:30 | 580 | 575
2018-03-29 11:00 | 574 | 568
2018-03-29 11:30 | 565 | 559
2018-03-29 12:00 | 565 | 560
2018-03-29 12:30 | 562 | 557
2018-03-29 13:00 | 569 | 564
2018-03-29 13:30 | 569 | 564
2018-03-29 14:00 | 573 | 568
2018-03-29 14:30 | 576 | 571
2018-03-29 15:00 | 590 | 585
2018-03-29 15:30 | 586 | 580
2018-03-29 16:00 | 582 | 575
2018-03-29 16:30 | 590 | 583
2018-03-29 17:00 | 596 | 588
2018-03-29 17:30 | 582 | 574
2018-03-29 18:00 | 587 | 578
2018-03-29 18:30 | 584 | 574
2018-03-29 19:00 | 586 | 576
2018-03-29 19:30 | 567 | 561
2018-03-29 20:00 | 548 | 547
2018-03-29 20:30 | 525 | 524
2018-03-29 21:00 | 504 | 503
2018-03-29 21:30 | 492 | 491
2018-03-29 22:00 | 467 | 465
2018-03-29 22:30 | 455 | 453
2018-03-29 23:00 | 439 | 436
2018-03-29 23:30 | 423 | 420
2018-03-30 | 407 | 403
2018-03-30 00:30 | 392 | 387
2018-03-30 01:00 | 377 | 372
2018-03-30 01:30 | 370 | 364
2018-03-30 02:00 | 363 | 356
2018-03-30 02:30 | 367 | 360
2018-03-30 03:00 | 360 | 353
2018-03-30 03:30 | 358 | 350
2018-03-30 04:00 | 355 | 347
2018-03-30 04:30 | 356 | 348
2018-03-30 05:00 | 354 | 346
2018-03-30 05:30 | 359 | 352
2018-03-30 06:00 | 365 | 358
2018-03-30 06:30 | 381 | 374
2018-03-30 07:00 | 384 | 378
2018-03-30 07:30 | 394 | 389
2018-03-30 08:00 | 401 | 397
2018-03-30 08:30 | 414 | 410
2018-03-30 09:00 | 417 | 414
2018-03-30 09:30 | 424 | 421
2018-03-30 10:00 | 425 | 423
2018-03-30 10:30 | 433 | 430
2018-03-30 11:00 | 443 | 440
2018-03-30 11:30 | 433 | 431
2018-03-30 12:00 | 429 | 427
2018-03-30 12:30 | 427 | 425
2018-03-30 13:00 | 425 | 423
2018-03-30 13:30 | 417 | 415
2018-03-30 14:00 | 426 | 425
2018-03-30 14:30 | 434 | 432
2018-03-30 15:00 | 444 | 441
2018-03-30 15:30 | 449 | 446
2018-03-30 16:00 | 466 | 463
2018-03-30 16:30 | 478 | 476
2018-03-30 17:00 | 485 | 483
2018-03-30 17:30 | 488 | 485
2018-03-30 18:00 | 492 | 490
2018-03-30 18:30 | 504 | 503
2018-03-30 19:00 | 505 | 504
2018-03-30 19:30 | 487 | 485
2018-03-30 20:00 | 485 | 483
2018-03-30 20:30 | 472 | 470
2018-03-30 21:00 | 445 | 444
2018-03-30 21:30 | 442 | 441
2018-03-30 22:00 | 432 | 431
2018-03-30 22:30 | 427 | 425
2018-03-30 23:00 | 422 | 419
2018-03-30 23:30 | 403 | 400
2018-03-31 | 389 | 385
2018-03-31 00:30 | 376 | 371
2018-03-31 01:00 | 366 | 359
2018-03-31 01:30 | 352 | 345
2018-03-31 02:00 | 346 | 338
2018-03-31 02:30 | 343 | 334
2018-03-31 03:00 | 343 | 334
2018-03-31 03:30 | 343 | 334
2018-03-31 04:00 | 341 | 331
2018-03-31 04:30 | 341 | 331
2018-03-31 05:00 | 341 | 332
2018-03-31 05:30 | 346 | 337
2018-03-31 06:00 | 353 | 344
2018-03-31 06:30 | 366 | 357
2018-03-31 07:00 | 385 | 378
2018-03-31 07:30 | 395 | 389
2018-03-31 08:00 | 405 | 400
2018-03-31 08:30 | 419 | 416
2018-03-31 09:00 | 428 | 426
2018-03-31 09:30 | 434 | 431
2018-03-31 10:00 | 431 | 428
2018-03-31 10:30 | 428 | 425
2018-03-31 11:00 | 421 | 418
2018-03-31 11:30 | 415 | 412
2018-03-31 12:00 | 418 | 416
2018-03-31 12:30 | 423 | 421
2018-03-31 13:00 | 423 | 421
2018-03-31 13:30 | 429 | 427
2018-03-31 14:00 | 433 | 431
2018-03-31 14:30 | 438 | 436
2018-03-31 15:00 | 451 | 450
2018-03-31 15:30 | 473 | 471
2018-03-31 16:00 | 492 | 490
2018-03-31 16:30 | 514 | 513
2018-03-31 17:00 | 531 | 528
2018-03-31 17:30 | 535 | 532
2018-03-31 18:00 | 531 | 528
2018-03-31 18:30 | 548 | 545
2018-03-31 19:00 | 554 | 552
2018-03-31 19:30 | 538 | 535
2018-03-31 20:00 | 530 | 527
2018-03-31 20:30 | 507 | 504
2018-03-31 21:00 | 487 | 484
2018-03-31 21:30 | 477 | 475
2018-03-31 22:00 | 471 | 469
2018-03-31 22:30 | 459 | 457
2018-03-31 23:00 | 452 | 450
2018-03-31 23:30 | 435 | 431
2018-04-01 | 415 | 410
2018-04-01 00:30 | 398 | 391
2018-04-01 01:00 | 377 | 368
2018-04-01 01:30 | 370 | 362
2018-04-01 02:00 | 363 | 354
2018-04-01 02:30 | 357 | 348
2018-04-01 03:00 | 356 | 345
2018-04-01 03:30 | 358 | 348
2018-04-01 04:00 | 354 | 344
2018-04-01 04:30 | 350 | 340
2018-04-01 05:00 | 351 | 340
2018-04-01 05:30 | 349 | 339
2018-04-01 06:00 | 359 | 349
2018-04-01 06:30 | 365 | 354
2018-04-01 07:00 | 368 | 359
2018-04-01 07:30 | 380 | 372
2018-04-01 08:00 | 390 | 383
2018-04-01 08:30 | 394 | 388
2018-04-01 09:00 | 398 | 394
2018-04-01 09:30 | 406 | 403
2018-04-01 10:00 | 407 | 403
2018-04-01 10:30 | 407 | 403
2018-04-01 11:00 | 408 | 405
2018-04-01 11:30 | 409 | 406
2018-04-01 12:00 | 415 | 411
2018-04-01 12:30 | 411 | 407
2018-04-01 13:00 | 404 | 401
2018-04-01 13:30 | 421 | 419
2018-04-01 14:00 | 431 | 428
2018-04-01 14:30 | 446 | 443
2018-04-01 15:00 | 460 | 457
2018-04-01 15:30 | 473 | 470
2018-04-01 16:00 | 490 | 485
2018-04-01 16:30 | 507 | 502
2018-04-01 17:00 | 524 | 520
2018-04-01 17:30 | 527 | 522
2018-04-01 18:00 | 526 | 521
2018-04-01 18:30 | 536 | 532
2018-04-01 19:00 | 541 | 537
2018-04-01 19:30 | 525 | 521
2018-04-01 20:00 | 517 | 512
2018-04-01 20:30 | 491 | 490
2018-04-01 21:00 | 475 | 474
2018-04-01 21:30 | 467 | 465
2018-04-01 22:00 | 451 | 448
2018-04-01 22:30 | 433 | 430
2018-04-01 23:00 | 417 | 415
2018-04-01 23:30 | 406 | 403
2018-04-02 | 392 | 388
2018-04-02 00:30 | 378 | 372
2018-04-02 01:00 | 365 | 358
2018-04-02 01:30 | 360 | 352
2018-04-02 02:00 | 357 | 349
2018-04-02 02:30 | 356 | 347
2018-04-02 03:00 | 354 | 344
2018-04-02 03:30 | 355 | 346
2018-04-02 04:00 | 355 | 345
2018-04-02 04:30 | 357 | 348
2018-04-02 05:00 | 355 | 346
2018-04-02 05:30 | 360 | 352
2018-04-02 06:00 | 369 | 361
2018-04-02 06:30 | 382 | 374
2018-04-02 07:00 | 384 | 377
2018-04-02 07:30 | 402 | 398
2018-04-02 08:00 | 415 | 411
2018-04-02 08:30 | 431 | 427
2018-04-02 09:00 | 439 | 437
2018-04-02 09:30 | 439 | 438
2018-04-02 10:00 | 442 | 441
2018-04-02 10:30 | 447 | 446
2018-04-02 11:00 | 448 | 447
2018-04-02 11:30 | 449 | 449
2018-04-02 12:00 | 449 | 448
2018-04-02 12:30 | 441 | 440
2018-04-02 13:00 | 436 | 436
2018-04-02 13:30 | 442 | 442
2018-04-02 14:00 | 464 | 463
2018-04-02 14:30 | 474 | 474
2018-04-02 15:00 | 494 | 494
2018-04-02 15:30 | 495 | 495
2018-04-02 16:00 | 509 | 509
2018-04-02 16:30 | 528 | 528
2018-04-02 17:00 | 546 | 545
2018-04-02 17:30 | 559 | 558
2018-04-02 18:00 | 569 | 567
2018-04-02 18:30 | 571 | 570
2018-04-02 19:00 | 561 | 559
2018-04-02 19:30 | 544 | 542
2018-04-02 20:00 | 537 | 535
2018-04-02 20:30 | 518 | 517
2018-04-02 21:00 | 496 | 496
2018-04-02 21:30 | 484 | 483
2018-04-02 22:00 | 465 | 464
2018-04-02 22:30 | 458 | 457
2018-04-02 23:00 | 445 | 445
2018-04-02 23:30 | 425 | 424
2018-04-03 | 400 | 399
2018-04-03 00:30 | 384 | 382
2018-04-03 01:00 | 374 | 371
2018-04-03 01:30 | 366 | 362
2018-04-03 02:00 | 362 | 358
2018-04-03 02:30 | 359 | 355
2018-04-03 03:00 | 359 | 354
2018-04-03 03:30 | 352 | 349
2018-04-03 04:00 | 348 | 344
2018-04-03 04:30 | 360 | 356
2018-04-03 05:00 | 367 | 364
2018-04-03 05:30 | 388 | 386
2018-04-03 06:00 | 402 | 402
2018-04-03 06:30 | 437 | 437
2018-04-03 07:00 | 476 | 476
2018-04-03 07:30 | 513 | 513
2018-04-03 08:00 | 540 | 540
2018-04-03 08:30 | 557 | 556
2018-04-03 09:00 | 572 | 572
2018-04-03 09:30 | 568 | 568
2018-04-03 10:00 | 558 | 558
2018-04-03 10:30 | 559 | 559
2018-04-03 11:00 | 559 | 559
2018-04-03 11:30 | 557 | 557
2018-04-03 12:00 | 549 | 548
2018-04-03 12:30 | 547 | 547
2018-04-03 13:00 | 547 | 547
2018-04-03 13:30 | 548 | 548
2018-04-03 14:00 | 553 | 553
2018-04-03 14:30 | 559 | 559
2018-04-03 15:00 | 566 | 565
2018-04-03 15:30 | 577 | 577
2018-04-03 16:00 | 592 | 591
2018-04-03 16:30 | 607 | 606
2018-04-03 17:00 | 614 | 612
2018-04-03 17:30 | 617 | 614
2018-04-03 18:00 | 618 | 614
2018-04-03 18:30 | 618 | 614
2018-04-03 19:00 | 610 | 606
2018-04-03 19:30 | 587 | 581
2018-04-03 20:00 | 573 | 568
2018-04-03 20:30 | 551 | 550
2018-04-03 21:00 | 536 | 535
2018-04-03 21:30 | 518 | 517
2018-04-03 22:00 | 497 | 495
2018-04-03 22:30 | 472 | 471
2018-04-03 23:00 | 453 | 452
2018-04-03 23:30 | 433 | 432
2018-04-04 | 415 | 413
2018-04-04 00:30 | 395 | 392
2018-04-04 01:00 | 378 | 375
2018-04-04 01:30 | 372 | 369
2018-04-04 02:00 | 367 | 363
2018-04-04 02:30 | 366 | 362
2018-04-04 03:00 | 365 | 360
2018-04-04 03:30 | 369 | 364
2018-04-04 04:00 | 377 | 372
2018-04-04 04:30 | 384 | 379
2018-04-04 05:00 | 386 | 382
2018-04-04 05:30 | 399 | 396
2018-04-04 06:00 | 418 | 416
2018-04-04 06:30 | 445 | 444
2018-04-04 07:00 | 479 | 478
2018-04-04 07:30 | 515 | 514
2018-04-04 08:00 | 536 | 536
2018-04-04 08:30 | 554 | 554
2018-04-04 09:00 | 559 | 559
2018-04-04 09:30 | 560 | 560
2018-04-04 10:00 | 550 | 549
2018-04-04 10:30 | 537 | 537
2018-04-04 11:00 | 524 | 524
2018-04-04 11:30 | 530 | 530
2018-04-04 12:00 | 551 | 551
2018-04-04 12:30 | 539 | 539
2018-04-04 13:00 | 527 | 527
2018-04-04 13:30 | 533 | 533
2018-04-04 14:00 | 541 | 541
2018-04-04 14:30 | 546 | 546
2018-04-04 15:00 | 554 | 554
2018-04-04 15:30 | 555 | 555
2018-04-04 16:00 | 563 | 563
2018-04-04 16:30 | 574 | 574
2018-04-04 17:00 | 587 | 587
2018-04-04 17:30 | 615 | 614
2018-04-04 18:00 | 620 | 619
2018-04-04 18:30 | 621 | 618
2018-04-04 19:00 | 616 | 613
2018-04-04 19:30 | 601 | 597
2018-04-04 20:00 | 590 | 586
2018-04-04 20:30 | 573 | 572
2018-04-04 21:00 | 558 | 556
2018-04-04 21:30 | 540 | 537
2018-04-04 22:00 | 523 | 520
2018-04-04 22:30 | 507 | 504
2018-04-04 23:00 | 492 | 489
2018-04-04 23:30 | 474 | 471
2018-04-05 | 449 | 446
2018-04-05 00:30 | 416 | 412
2018-04-05 01:00 | 393 | 390
2018-04-05 01:30 | 392 | 387
2018-04-05 02:00 | 371 | 365
2018-04-05 02:30 | 377 | 371
2018-04-05 03:00 | 377 | 370
2018-04-05 03:30 | 377 | 370
2018-04-05 04:00 | 378 | 371
2018-04-05 04:30 | 382 | 376
2018-04-05 05:00 | 388 | 382
2018-04-05 05:30 | 411 | 407
2018-04-05 06:00 | 422 | 420
2018-04-05 06:30 | 428 | 427
2018-04-05 07:00 | 457 | 457
2018-04-05 07:30 | 487 | 487
2018-04-05 08:00 | 502 | 501
2018-04-05 08:30 | 510 | 509
2018-04-05 09:00 | 504 | 503
2018-04-05 09:30 | 499 | 498
2018-04-05 10:00 | 497 | 497
2018-04-05 10:30 | 486 | 486
2018-04-05 11:00 | 493 | 493
2018-04-05 11:30 | 507 | 507
2018-04-05 12:00 | 516 | 516
2018-04-05 12:30 | 516 | 516
2018-04-05 13:00 | 514 | 514
2018-04-05 13:30 | 535 | 535
2018-04-05 14:00 | 539 | 539
2018-04-05 14:30 | 552 | 552
2018-04-05 15:00 | 543 | 542
2018-04-05 15:30 | 554 | 553
2018-04-05 16:00 | 573 | 572
2018-04-05 16:30 | 577 | 575
2018-04-05 17:00 | 585 | 582
2018-04-05 17:30 | 587 | 585
2018-04-05 18:00 | 592 | 589
2018-04-05 18:30 | 596 | 593
2018-04-05 19:00 | 600 | 596
2018-04-05 19:30 | 588 | 583
2018-04-05 20:00 | 587 | 581
2018-04-05 20:30 | 572 | 569
2018-04-05 21:00 | 551 | 549
2018-04-05 21:30 | 533 | 530
2018-04-05 22:00 | 507 | 504
2018-04-05 22:30 | 494 | 492
2018-04-05 23:00 | 479 | 479
2018-04-05 23:30 | 465 | 464
2018-04-06 | 447 | 445
2018-04-06 00:30 | 420 | 416
2018-04-06 01:00 | 391 | 386
2018-04-06 01:30 | 380 | 374
2018-04-06 02:00 | 377 | 371
2018-04-06 02:30 | 367 | 361
2018-04-06 03:00 | 366 | 359
2018-04-06 03:30 | 365 | 359
2018-04-06 04:00 | 366 | 360
2018-04-06 04:30 | 372 | 367
2018-04-06 05:00 | 378 | 374
2018-04-06 05:30 | 398 | 395
2018-04-06 06:00 | 399 | 397
2018-04-06 06:30 | 417 | 416
2018-04-06 07:00 | 445 | 443
2018-04-06 07:30 | 477 | 476
2018-04-06 08:00 | 485 | 484
2018-04-06 08:30 | 489 | 489
2018-04-06 09:00 | 496 | 496
2018-04-06 09:30 | 501 | 500
2018-04-06 10:00 | 512 | 511
2018-04-06 10:30 | 510 | 507
2018-04-06 11:00 | 499 | 497
2018-04-06 11:30 | 488 | 487
2018-04-06 12:00 | 483 | 481
2018-04-06 12:30 | 472 | 471
2018-04-06 13:00 | 472 | 470
2018-04-06 13:30 | 480 | 478
2018-04-06 14:00 | 496 | 494
2018-04-06 14:30 | 508 | 507
2018-04-06 15:00 | 535 | 534
2018-04-06 15:30 | 569 | 567
2018-04-06 16:00 | 585 | 583
2018-04-06 16:30 | 597 | 595
2018-04-06 17:00 | 602 | 599
2018-04-06 17:30 | 608 | 605
2018-04-06 18:00 | 602 | 598
2018-04-06 18:30 | 592 | 589
2018-04-06 19:00 | 594 | 590
2018-04-06 19:30 | 578 | 573
2018-04-06 20:00 | 573 | 569
2018-04-06 20:30 | 560 | 557
2018-04-06 21:00 | 534 | 532
2018-04-06 21:30 | 517 | 515
2018-04-06 22:00 | 506 | 503
2018-04-06 22:30 | 495 | 493
2018-04-06 23:00 | 477 | 474
2018-04-06 23:30 | 465 | 461
2018-04-07 | 435 | 433
2018-04-07 00:30 | 410 | 406
2018-04-07 01:00 | 395 | 390
2018-04-07 01:30 | 384 | 380
2018-04-07 02:00 | 373 | 368
2018-04-07 02:30 | 368 | 362
2018-04-07 03:00 | 367 | 361
2018-04-07 03:30 | 364 | 357
2018-04-07 04:00 | 361 | 350
2018-04-07 04:30 | 356 | 345
2018-04-07 05:00 | 360 | 350
2018-04-07 05:30 | 370 | 361
2018-04-07 06:00 | 377 | 368
2018-04-07 06:30 | 388 | 379
2018-04-07 07:00 | 396 | 387
2018-04-07 07:30 | 415 | 409
2018-04-07 08:00 | 422 | 417
2018-04-07 08:30 | 426 | 422
2018-04-07 09:00 | 434 | 431
2018-04-07 09:30 | 448 | 444
2018-04-07 10:00 | 449 | 444
2018-04-07 10:30 | 450 | 444
2018-04-07 11:00 | 453 | 447
2018-04-07 11:30 | 448 | 441
2018-04-07 12:00 | 445 | 438
2018-04-07 12:30 | 446 | 439
2018-04-07 13:00 | 450 | 442
2018-04-07 13:30 | 453 | 445
2018-04-07 14:00 | 456 | 448
2018-04-07 14:30 | 463 | 456
2018-04-07 15:00 | 477 | 470
2018-04-07 15:30 | 494 | 488
2018-04-07 16:00 | 507 | 501
2018-04-07 16:30 | 524 | 518
2018-04-07 17:00 | 541 | 536
2018-04-07 17:30 | 539 | 533
2018-04-07 18:00 | 546 | 541
2018-04-07 18:30 | 563 | 559
2018-04-07 19:00 | 557 | 552
2018-04-07 19:30 | 539 | 536
2018-04-07 20:00 | 526 | 523
2018-04-07 20:30 | 511 | 508
2018-04-07 21:00 | 496 | 493
2018-04-07 21:30 | 489 | 487
2018-04-07 22:00 | 481 | 478
2018-04-07 22:30 | 463 | 460
2018-04-07 23:00 | 455 | 451
2018-04-07 23:30 | 441 | 436
2018-04-08 | 415 | 409
2018-04-08 00:30 | 385 | 377
2018-04-08 01:00 | 367 | 358
2018-04-08 01:30 | 372 | 362
2018-04-08 02:00 | 353 | 343
2018-04-08 02:30 | 352 | 341
2018-04-08 03:00 | 345 | 333
2018-04-08 03:30 | 337 | 323
2018-04-08 04:00 | 333 | 318
2018-04-08 04:30 | 333 | 318
2018-04-08 05:00 | 333 | 319
2018-04-08 05:30 | 333 | 319
2018-04-08 06:00 | 330 | 316
2018-04-08 06:30 | 327 | 313
2018-04-08 07:00 | 338 | 324
2018-04-08 07:30 | 364 | 352
2018-04-08 08:00 | 381 | 372
2018-04-08 08:30 | 394 | 387
2018-04-08 09:00 | 397 | 390
2018-04-08 09:30 | 400 | 394
2018-04-08 10:00 | 399 | 395
2018-04-08 10:30 | 400 | 397
2018-04-08 11:00 | 405 | 402
2018-04-08 11:30 | 404 | 402
2018-04-08 12:00 | 399 | 397
2018-04-08 12:30 | 394 | 392
2018-04-08 13:00 | 392 | 390
2018-04-08 13:30 | 394 | 392
2018-04-08 14:00 | 404 | 402
2018-04-08 14:30 | 418 | 416
2018-04-08 15:00 | 435 | 433
2018-04-08 15:30 | 453 | 451
2018-04-08 16:00 | 476 | 474
2018-04-08 16:30 | 495 | 491
2018-04-08 17:00 | 510 | 506
2018-04-08 17:30 | 519 | 516
2018-04-08 18:00 | 523 | 521
2018-04-08 18:30 | 547 | 542
2018-04-08 19:00 | 545 | 540
2018-04-08 19:30 | 526 | 518
2018-04-08 20:00 | 515 | 508
2018-04-08 20:30 | 507 | 501
2018-04-08 21:00 | 495 | 488
2018-04-08 21:30 | 487 | 481
2018-04-08 22:00 | 469 | 463
2018-04-08 22:30 | 439 | 433
2018-04-08 23:00 | 429 | 422
2018-04-08 23:30 | 415 | 408
2018-04-09 | 393 | 386
2018-04-09 00:30 | 367 | 359
2018-04-09 01:00 | 356 | 347
2018-04-09 01:30 | 343 | 333
2018-04-09 02:00 | 329 | 318
2018-04-09 02:30 | 326 | 315
2018-04-09 03:00 | 330 | 318
2018-04-09 03:30 | 328 | 316
2018-04-09 04:00 | 336 | 325
2018-04-09 04:30 | 343 | 332
2018-04-09 05:00 | 351 | 342
2018-04-09 05:30 | 372 | 365
2018-04-09 06:00 | 389 | 384
2018-04-09 06:30 | 422 | 420
2018-04-09 07:00 | 447 | 446
2018-04-09 07:30 | 473 | 470
2018-04-09 08:00 | 483 | 481
2018-04-09 08:30 | 491 | 489
2018-04-09 09:00 | 493 | 492
2018-04-09 09:30 | 496 | 495
2018-04-09 10:00 | 493 | 491
2018-04-09 10:30 | 500 | 499
2018-04-09 11:00 | 499 | 498
2018-04-09 11:30 | 496 | 495
2018-04-09 12:00 | 496 | 495
2018-04-09 12:30 | 503 | 502
2018-04-09 13:00 | 513 | 512
2018-04-09 13:30 | 520 | 520
2018-04-09 14:00 | 534 | 534
2018-04-09 14:30 | 550 | 549
2018-04-09 15:00 | 565 | 565
2018-04-09 15:30 | 587 | 585
2018-04-09 16:00 | 608 | 602
2018-04-09 16:30 | 624 | 619
2018-04-09 17:00 | 642 | 636
2018-04-09 17:30 | 657 | 648
2018-04-09 18:00 | 658 | 648
2018-04-09 18:30 | 657 | 647
2018-04-09 19:00 | 644 | 632
2018-04-09 19:30 | 611 | 598
2018-04-09 20:00 | 590 | 580
2018-04-09 20:30 | 575 | 564
2018-04-09 21:00 | 552 | 543
2018-04-09 21:30 | 532 | 527
2018-04-09 22:00 | 507 | 505
2018-04-09 22:30 | 497 | 494
2018-04-09 23:00 | 483 | 479
2018-04-09 23:30 | 467 | 461
2018-04-10 | 450 | 442
2018-04-10 00:30 | 410 | 401
2018-04-10 01:00 | 382 | 375
2018-04-10 01:30 | 360 | 351
2018-04-10 02:00 | 343 | 334
2018-04-10 02:30 | 355 | 346
2018-04-10 03:00 | 358 | 349
2018-04-10 03:30 | 353 | 343
2018-04-10 04:00 | 349 | 339
2018-04-10 04:30 | 360 | 351
2018-04-10 05:00 | 371 | 363
2018-04-10 05:30 | 397 | 391
2018-04-10 06:00 | 406 | 402
2018-04-10 06:30 | 429 | 427
2018-04-10 07:00 | 463 | 459
2018-04-10 07:30 | 486 | 482
2018-04-10 08:00 | 489 | 487
2018-04-10 08:30 | 489 | 487
2018-04-10 09:00 | 489 | 487
2018-04-10 09:30 | 487 | 486
2018-04-10 10:00 | 488 | 487
2018-04-10 10:30 | 494 | 492
2018-04-10 11:00 | 500 | 499
2018-04-10 11:30 | 509 | 508
2018-04-10 12:00 | 521 | 519
2018-04-10 12:30 | 520 | 518
2018-04-10 13:00 | 526 | 522
2018-04-10 13:30 | 534 | 530
2018-04-10 14:00 | 551 | 548
2018-04-10 14:30 | 574 | 571
2018-04-10 15:00 | 586 | 582
2018-04-10 15:30 | 597 | 594
2018-04-10 16:00 | 604 | 599
2018-04-10 16:30 | 607 | 603
2018-04-10 17:00 | 620 | 615
2018-04-10 17:30 | 617 | 611
2018-04-10 18:00 | 609 | 605
2018-04-10 18:30 | 610 | 606
2018-04-10 19:00 | 605 | 600
2018-04-10 19:30 | 583 | 578
2018-04-10 20:00 | 574 | 570
2018-04-10 20:30 | 564 | 560
2018-04-10 21:00 | 538 | 535
2018-04-10 21:30 | 517 | 515
2018-04-10 22:00 | 504 | 502
2018-04-10 22:30 | 493 | 491
2018-04-10 23:00 | 478 | 476
2018-04-10 23:30 | 464 | 461
2018-04-11 | 444 | 440
2018-04-11 00:30 | 414 | 409
2018-04-11 01:00 | 413 | 408
2018-04-11 01:30 | 405 | 398
2018-04-11 02:00 | 390 | 382
2018-04-11 02:30 | 376 | 368
2018-04-11 03:00 | 370 | 362
2018-04-11 03:30 | 368 | 359
2018-04-11 04:00 | 367 | 358
2018-04-11 04:30 | 367 | 359
2018-04-11 05:00 | 373 | 366
2018-04-11 05:30 | 394 | 388
2018-04-11 06:00 | 409 | 406
2018-04-11 06:30 | 439 | 437
2018-04-11 07:00 | 482 | 481
2018-04-11 07:30 | 514 | 510
2018-04-11 08:00 | 541 | 538
2018-04-11 08:30 | 549 | 546
2018-04-11 09:00 | 549 | 543
2018-04-11 09:30 | 550 | 540
2018-04-11 10:00 | 543 | 533
2018-04-11 10:30 | 542 | 533
2018-04-11 11:00 | 540 | 530
2018-04-11 11:30 | 540 | 530
2018-04-11 12:00 | 541 | 532
2018-04-11 12:30 | 539 | 530
2018-04-11 13:00 | 541 | 532
2018-04-11 13:30 | 552 | 542
2018-04-11 14:00 | 571 | 562
2018-04-11 14:30 | 578 | 569
2018-04-11 15:00 | 595 | 587
2018-04-11 15:30 | 601 | 594
2018-04-11 16:00 | 612 | 604
2018-04-11 16:30 | 622 | 614
2018-04-11 17:00 | 623 | 614
2018-04-11 17:30 | 617 | 605
2018-04-11 18:00 | 615 | 605
2018-04-11 18:30 | 613 | 604
2018-04-11 19:00 | 609 | 600
2018-04-11 19:30 | 583 | 576
2018-04-11 20:00 | 571 | 570
2018-04-11 20:30 | 559 | 557
2018-04-11 21:00 | 532 | 531
2018-04-11 21:30 | 521 | 518
2018-04-11 22:00 | 499 | 496
2018-04-11 22:30 | 477 | 474
2018-04-11 23:00 | 464 | 460
2018-04-11 23:30 | 457 | 453
2018-04-12 | 433 | 428
2018-04-12 00:30 | 400 | 394
2018-04-12 01:00 | 377 | 370
2018-04-12 01:30 | 369 | 360
2018-04-12 02:00 | 374 | 365
2018-04-12 02:30 | 378 | 369
2018-04-12 03:00 | 371 | 360
2018-04-12 03:30 | 367 | 357
2018-04-12 04:00 | 370 | 360
2018-04-12 04:30 | 371 | 361
2018-04-12 05:00 | 374 | 366
2018-04-12 05:30 | 389 | 383
2018-04-12 06:00 | 399 | 396
2018-04-12 06:30 | 427 | 425
2018-04-12 07:00 | 462 | 461
2018-04-12 07:30 | 499 | 497
2018-04-12 08:00 | 504 | 503
2018-04-12 08:30 | 510 | 509
2018-04-12 09:00 | 499 | 498
2018-04-12 09:30 | 503 | 503
2018-04-12 10:00 | 503 | 503
2018-04-12 10:30 | 517 | 514
2018-04-12 11:00 | 532 | 531
2018-04-12 11:30 | 529 | 527
2018-04-12 12:00 | 514 | 512
2018-04-12 12:30 | 514 | 511
2018-04-12 13:00 | 514 | 511
2018-04-12 13:30 | 520 | 517
2018-04-12 14:00 | 533 | 530
2018-04-12 14:30 | 541 | 537
2018-04-12 15:00 | 542 | 539
2018-04-12 15:30 | 554 | 551
2018-04-12 16:00 | 570 | 567
2018-04-12 16:30 | 572 | 568
2018-04-12 17:00 | 590 | 586
2018-04-12 17:30 | 607 | 603
2018-04-12 18:00 | 624 | 621
2018-04-12 18:30 | 627 | 622
2018-04-12 19:00 | 617 | 612
2018-04-12 19:30 | 597 | 592
2018-04-12 20:00 | 593 | 588
2018-04-12 20:30 | 579 | 575
2018-04-12 21:00 | 553 | 551
2018-04-12 21:30 | 521 | 519
2018-04-12 22:00 | 500 | 498
2018-04-12 22:30 | 494 | 491
2018-04-12 23:00 | 469 | 466
2018-04-12 23:30 | 452 | 448
2018-04-13 | 425 | 419
2018-04-13 00:30 | 402 | 395
2018-04-13 01:00 | 384 | 377
2018-04-13 01:30 | 384 | 376
2018-04-13 02:00 | 380 | 371
2018-04-13 02:30 | 377 | 368
2018-04-13 03:00 | 372 | 362
2018-04-13 03:30 | 367 | 357
2018-04-13 04:00 | 364 | 354
2018-04-13 04:30 | 366 | 356
2018-04-13 05:00 | 372 | 364
2018-04-13 05:30 | 396 | 389
2018-04-13 06:00 | 404 | 400
2018-04-13 06:30 | 426 | 422
2018-04-13 07:00 | 457 | 453
2018-04-13 07:30 | 481 | 479
2018-04-13 08:00 | 499 | 498
2018-04-13 08:30 | 503 | 501
2018-04-13 09:00 | 503 | 502
2018-04-13 09:30 | 501 | 499
2018-04-13 10:00 | 499 | 498
2018-04-13 10:30 | 495 | 494
2018-04-13 11:00 | 496 | 495
2018-04-13 11:30 | 495 | 493
2018-04-13 12:00 | 495 | 492
2018-04-13 12:30 | 489 | 485
2018-04-13 13:00 | 493 | 490
2018-04-13 13:30 | 514 | 511
2018-04-13 14:00 | 520 | 517
2018-04-13 14:30 | 520 | 517
2018-04-13 15:00 | 533 | 531
2018-04-13 15:30 | 543 | 541
2018-04-13 16:00 | 557 | 554
2018-04-13 16:30 | 582 | 579
2018-04-13 17:00 | 582 | 579
2018-04-13 17:30 | 581 | 576
2018-04-13 18:00 | 587 | 582
2018-04-13 18:30 | 587 | 582
2018-04-13 19:00 | 589 | 582
2018-04-13 19:30 | 564 | 559
2018-04-13 20:00 | 555 | 554
2018-04-13 20:30 | 552 | 549
2018-04-13 21:00 | 531 | 528
2018-04-13 21:30 | 520 | 516
2018-04-13 22:00 | 506 | 501
2018-04-13 22:30 | 498 | 492
2018-04-13 23:00 | 475 | 472
2018-04-13 23:30 | 447 | 443
2018-04-14 | 423 | 417
2018-04-14 00:30 | 398 | 390
2018-04-14 01:00 | 388 | 379
2018-04-14 01:30 | 375 | 366
2018-04-14 02:00 | 363 | 352
2018-04-14 02:30 | 352 | 340
2018-04-14 03:00 | 346 | 334
2018-04-14 03:30 | 337 | 326
2018-04-14 04:00 | 321 | 310
2018-04-14 04:30 | 323 | 312
2018-04-14 05:00 | 320 | 309
2018-04-14 05:30 | 327 | 317
2018-04-14 06:00 | 345 | 336
2018-04-14 06:30 | 371 | 363
2018-04-14 07:00 | 381 | 373
2018-04-14 07:30 | 401 | 395
2018-04-14 08:00 | 414 | 409
2018-04-14 08:30 | 434 | 431
2018-04-14 09:00 | 443 | 441
2018-04-14 09:30 | 469 | 468
2018-04-14 10:00 | 483 | 482
2018-04-14 10:30 | 483 | 481
2018-04-14 11:00 | 496 | 495
2018-04-14 11:30 | 494 | 492
2018-04-14 12:00 | 488 | 486
2018-04-14 12:30 | 465 | 462
2018-04-14 13:00 | 478 | 476
2018-04-14 13:30 | 472 | 470
2018-04-14 14:00 | 467 | 464
2018-04-14 14:30 | 441 | 438
2018-04-14 15:00 | 450 | 448
2018-04-14 15:30 | 461 | 459
2018-04-14 16:00 | 478 | 476
2018-04-14 16:30 | 490 | 488
2018-04-14 17:00 | 504 | 502
2018-04-14 17:30 | 503 | 500
2018-04-14 18:00 | 515 | 512
2018-04-14 18:30 | 516 | 514
2018-04-14 19:00 | 508 | 506
2018-04-14 19:30 | 494 | 492
2018-04-14 20:00 | 496 | 495
2018-04-14 20:30 | 499 | 498
2018-04-14 21:00 | 485 | 483
2018-04-14 21:30 | 474 | 472
2018-04-14 22:00 | 456 | 454
2018-04-14 22:30 | 442 | 439
2018-04-14 23:00 | 428 | 425
2018-04-14 23:30 | 413 | 409
2018-04-15 | 394 | 389
2018-04-15 00:30 | 366 | 359
2018-04-15 01:00 | 355 | 346
2018-04-15 01:30 | 337 | 328
2018-04-15 02:00 | 324 | 313
2018-04-15 02:30 | 325 | 314
2018-04-15 03:00 | 311 | 299
2018-04-15 03:30 | 303 | 291
2018-04-15 04:00 | 306 | 293
2018-04-15 04:30 | 299 | 286
2018-04-15 05:00 | 293 | 279
2018-04-15 05:30 | 299 | 286
2018-04-15 06:00 | 305 | 292
2018-04-15 06:30 | 333 | 320
2018-04-15 07:00 | 342 | 330
2018-04-15 07:30 | 362 | 352
2018-04-15 08:00 | 377 | 369
2018-04-15 08:30 | 389 | 383
2018-04-15 09:00 | 394 | 389
2018-04-15 09:30 | 397 | 394
2018-04-15 10:00 | 393 | 391
2018-04-15 10:30 | 392 | 390
2018-04-15 11:00 | 397 | 396
2018-04-15 11:30 | 402 | 401
2018-04-15 12:00 | 403 | 402
2018-04-15 12:30 | 406 | 405
2018-04-15 13:00 | 416 | 415
2018-04-15 13:30 | 431 | 430
2018-04-15 14:00 | 455 | 454
2018-04-15 14:30 | 469 | 468
2018-04-15 15:00 | 487 | 486
2018-04-15 15:30 | 510 | 510
2018-04-15 16:00 | 525 | 524
2018-04-15 16:30 | 548 | 545
2018-04-15 17:00 | 559 | 557
2018-04-15 17:30 | 560 | 552
2018-04-15 18:00 | 573 | 566
2018-04-15 18:30 | 576 | 570
2018-04-15 19:00 | 561 | 554
2018-04-15 19:30 | 543 | 537
2018-04-15 20:00 | 532 | 528
2018-04-15 20:30 | 517 | 513
2018-04-15 21:00 | 498 | 497
2018-04-15 21:30 | 489 | 487
2018-04-15 22:00 | 468 | 465
2018-04-15 22:30 | 461 | 458
2018-04-15 23:00 | 448 | 445
2018-04-15 23:30 | 432 | 428
2018-04-16 | 410 | 405
2018-04-16 00:30 | 380 | 371
2018-04-16 01:00 | 359 | 347
2018-04-16 01:30 | 331 | 320
2018-04-16 02:00 | 317 | 306
2018-04-16 02:30 | 319 | 307
2018-04-16 03:00 | 324 | 313
2018-04-16 03:30 | 324 | 313
2018-04-16 04:00 | 326 | 314
2018-04-16 04:30 | 330 | 319
2018-04-16 05:00 | 343 | 334
2018-04-16 05:30 | 365 | 358
2018-04-16 06:00 | 390 | 386
2018-04-16 06:30 | 432 | 429
2018-04-16 07:00 | 465 | 462
2018-04-16 07:30 | 496 | 493
2018-04-16 08:00 | 509 | 506
2018-04-16 08:30 | 511 | 509
2018-04-16 09:00 | 513 | 512
2018-04-16 09:30 | 519 | 516
2018-04-16 10:00 | 518 | 516
2018-04-16 10:30 | 527 | 525
2018-04-16 11:00 | 527 | 525
2018-04-16 11:30 | 528 | 526
2018-04-16 12:00 | 531 | 529
2018-04-16 12:30 | 533 | 531
2018-04-16 13:00 | 537 | 536
2018-04-16 13:30 | 541 | 540
2018-04-16 14:00 | 552 | 552
2018-04-16 14:30 | 558 | 557
2018-04-16 15:00 | 573 | 572
2018-04-16 15:30 | 582 | 581
2018-04-16 16:00 | 602 | 601
2018-04-16 16:30 | 615 | 614
2018-04-16 17:00 | 628 | 626
2018-04-16 17:30 | 628 | 625
2018-04-16 18:00 | 638 | 633
2018-04-16 18:30 | 638 | 632
2018-04-16 19:00 | 623 | 618
2018-04-16 19:30 | 587 | 582
2018-04-16 20:00 | 573 | 570
2018-04-16 20:30 | 562 | 559
2018-04-16 21:00 | 534 | 533
2018-04-16 21:30 | 510 | 508
2018-04-16 22:00 | 490 | 487
2018-04-16 22:30 | 490 | 486
2018-04-16 23:00 | 476 | 471
2018-04-16 23:30 | 462 | 455
2018-04-17 | 433 | 423
2018-04-17 00:30 | 401 | 391
2018-04-17 01:00 | 387 | 376
2018-04-17 01:30 | 368 | 356
2018-04-17 02:00 | 365 | 353
2018-04-17 02:30 | 364 | 353
2018-04-17 03:00 | 363 | 351
2018-04-17 03:30 | 361 | 349
2018-04-17 04:00 | 355 | 344
2018-04-17 04:30 | 355 | 344
2018-04-17 05:00 | 366 | 357
2018-04-17 05:30 | 381 | 374
2018-04-17 06:00 | 395 | 390
2018-04-17 06:30 | 432 | 430
2018-04-17 07:00 | 465 | 464
2018-04-17 07:30 | 487 | 485
2018-04-17 08:00 | 483 | 482
2018-04-17 08:30 | 473 | 472
2018-04-17 09:00 | 467 | 466
2018-04-17 09:30 | 463 | 462
2018-04-17 10:00 | 462 | 461
2018-04-17 10:30 | 466 | 466
2018-04-17 11:00 | 465 | 464
2018-04-17 11:30 | 466 | 466
2018-04-17 12:00 | 477 | 476
2018-04-17 12:30 | 483 | 482
2018-04-17 13:00 | 497 | 496
2018-04-17 13:30 | 515 | 514
2018-04-17 14:00 | 549 | 546
2018-04-17 14:30 | 568 | 561
2018-04-17 15:00 | 577 | 570
2018-04-17 15:30 | 586 | 580
2018-04-17 16:00 | 596 | 589
2018-04-17 16:30 | 590 | 583
2018-04-17 17:00 | 587 | 580
2018-04-17 17:30 | 589 | 581
2018-04-17 18:00 | 608 | 601
2018-04-17 18:30 | 611 | 601
2018-04-17 19:00 | 607 | 595
2018-04-17 19:30 | 572 | 561
2018-04-17 20:00 | 558 | 551
2018-04-17 20:30 | 550 | 545
2018-04-17 21:00 | 526 | 523
2018-04-17 21:30 | 507 | 504
2018-04-17 22:00 | 491 | 487
2018-04-17 22:30 | 479 | 475
2018-04-17 23:00 | 465 | 462
2018-04-17 23:30 | 450 | 447
2018-04-18 | 425 | 422
2018-04-18 00:30 | 401 | 396
2018-04-18 01:00 | 382 | 376
2018-04-18 01:30 | 373 | 367
2018-04-18 02:00 | 369 | 362
2018-04-18 02:30 | 362 | 354
2018-04-18 03:00 | 358 | 350
2018-04-18 03:30 | 357 | 349
2018-04-18 04:00 | 354 | 346
2018-04-18 04:30 | 361 | 353
2018-04-18 05:00 | 374 | 368
2018-04-18 05:30 | 393 | 389
2018-04-18 06:00 | 409 | 405
2018-04-18 06:30 | 432 | 430
2018-04-18 07:00 | 479 | 477
2018-04-18 07:30 | 523 | 519
2018-04-18 08:00 | 533 | 530
2018-04-18 08:30 | 520 | 518
2018-04-18 09:00 | 519 | 516
2018-04-18 09:30 | 530 | 528
2018-04-18 10:00 | 522 | 519
2018-04-18 10:30 | 516 | 514
2018-04-18 11:00 | 525 | 523
2018-04-18 11:30 | 525 | 522
2018-04-18 12:00 | 527 | 524
2018-04-18 12:30 | 517 | 515
2018-04-18 13:00 | 515 | 513
2018-04-18 13:30 | 510 | 507
2018-04-18 14:00 | 498 | 494
2018-04-18 14:30 | 495 | 491
2018-04-18 15:00 | 500 | 496
2018-04-18 15:30 | 514 | 511
2018-04-18 16:00 | 526 | 522
2018-04-18 16:30 | 523 | 519
2018-04-18 17:00 | 545 | 540
2018-04-18 17:30 | 557 | 552
2018-04-18 18:00 | 575 | 570
2018-04-18 18:30 | 569 | 564
2018-04-18 19:00 | 554 | 548
2018-04-18 19:30 | 546 | 540
2018-04-18 20:00 | 535 | 533
2018-04-18 20:30 | 526 | 524
2018-04-18 21:00 | 492 | 489
2018-04-18 21:30 | 481 | 478
2018-04-18 22:00 | 470 | 467
2018-04-18 22:30 | 474 | 469
2018-04-18 23:00 | 462 | 457
2018-04-18 23:30 | 442 | 437
2018-04-19 | 420 | 416
2018-04-19 00:30 | 397 | 391
2018-04-19 01:00 | 376 | 368
2018-04-19 01:30 | 371 | 362
2018-04-19 02:00 | 363 | 353
2018-04-19 02:30 | 362 | 351
2018-04-19 03:00 | 363 | 352
2018-04-19 03:30 | 358 | 347
2018-04-19 04:00 | 354 | 343
2018-04-19 04:30 | 357 | 347
2018-04-19 05:00 | 365 | 356
2018-04-19 05:30 | 384 | 377
2018-04-19 06:00 | 408 | 404
2018-04-19 06:30 | 433 | 431
2018-04-19 07:00 | 466 | 465
2018-04-19 07:30 | 499 | 497
2018-04-19 08:00 | 503 | 502
2018-04-19 08:30 | 499 | 499
2018-04-19 09:00 | 485 | 484
2018-04-19 09:30 | 480 | 480
2018-04-19 10:00 | 482 | 482
2018-04-19 10:30 | 498 | 498
2018-04-19 11:00 | 508 | 507
2018-04-19 11:30 | 495 | 495
2018-04-19 12:00 | 494 | 494
2018-04-19 12:30 | 504 | 504
2018-04-19 13:00 | 516 | 516
2018-04-19 13:30 | 520 | 519
2018-04-19 14:00 | 522 | 522
2018-04-19 14:30 | 531 | 531
2018-04-19 15:00 | 551 | 550
2018-04-19 15:30 | 567 | 565
2018-04-19 16:00 | 571 | 569
2018-04-19 16:30 | 591 | 588
2018-04-19 17:00 | 608 | 605
2018-04-19 17:30 | 620 | 616
2018-04-19 18:00 | 623 | 620
2018-04-19 18:30 | 621 | 617
2018-04-19 19:00 | 603 | 598
2018-04-19 19:30 | 558 | 553
2018-04-19 20:00 | 553 | 550
2018-04-19 20:30 | 556 | 553
2018-04-19 21:00 | 545 | 543
2018-04-19 21:30 | 520 | 516
2018-04-19 22:00 | 511 | 505
2018-04-19 22:30 | 490 | 485
2018-04-19 23:00 | 458 | 455
2018-04-19 23:30 | 430 | 427
2018-04-20 | 404 | 400
2018-04-20 00:30 | 387 | 381
2018-04-20 01:00 | 367 | 359
2018-04-20 01:30 | 356 | 347
2018-04-20 02:00 | 350 | 341
2018-04-20 02:30 | 347 | 337
2018-04-20 03:00 | 352 | 341
2018-04-20 03:30 | 344 | 334
2018-04-20 04:00 | 338 | 328
2018-04-20 04:30 | 336 | 326
2018-04-20 05:00 | 344 | 335
2018-04-20 05:30 | 361 | 355
2018-04-20 06:00 | 387 | 382
2018-04-20 06:30 | 423 | 419
2018-04-20 07:00 | 461 | 459
2018-04-20 07:30 | 491 | 486
2018-04-20 08:00 | 512 | 503
2018-04-20 08:30 | 520 | 506
2018-04-20 09:00 | 515 | 502
2018-04-20 09:30 | 514 | 502
2018-04-20 10:00 | 521 | 511
2018-04-20 10:30 | 522 | 513
2018-04-20 11:00 | 522 | 513
2018-04-20 11:30 | 525 | 515
2018-04-20 12:00 | 536 | 524
2018-04-20 12:30 | 547 | 536
2018-04-20 13:00 | 556 | 543
2018-04-20 13:30 | 560 | 547
2018-04-20 14:00 | 562 | 549
2018-04-20 14:30 | 566 | 552
2018-04-20 15:00 | 570 | 555
2018-04-20 15:30 | 568 | 552
2018-04-20 16:00 | 577 | 561
2018-04-20 16:30 | 580 | 564
2018-04-20 17:00 | 592 | 575
2018-04-20 17:30 | 585 | 567
2018-04-20 18:00 | 586 | 567
2018-04-20 18:30 | 581 | 560
2018-04-20 19:00 | 563 | 543
2018-04-20 19:30 | 518 | 509
2018-04-20 20:00 | 511 | 507
2018-04-20 20:30 | 512 | 507
2018-04-20 21:00 | 501 | 495
2018-04-20 21:30 | 503 | 497
2018-04-20 22:00 | 479 | 477
2018-04-20 22:30 | 462 | 459
2018-04-20 23:00 | 441 | 438
2018-04-20 23:30 | 427 | 423
2018-04-21 | 408 | 403
2018-04-21 00:30 | 380 | 373
2018-04-21 01:00 | 371 | 362
2018-04-21 01:30 | 356 | 347
2018-04-21 02:00 | 345 | 335
2018-04-21 02:30 | 332 | 320
2018-04-21 03:00 | 329 | 317
2018-04-21 03:30 | 327 | 314
2018-04-21 04:00 | 326 | 313
2018-04-21 04:30 | 325 | 311
2018-04-21 05:00 | 342 | 328
2018-04-21 05:30 | 349 | 336
2018-04-21 06:00 | 360 | 349
2018-04-21 06:30 | 377 | 367
2018-04-21 07:00 | 396 | 387
2018-04-21 07:30 | 422 | 415
2018-04-21 08:00 | 427 | 421
2018-04-21 08:30 | 428 | 423
2018-04-21 09:00 | 430 | 426
2018-04-21 09:30 | 437 | 434
2018-04-21 10:00 | 431 | 428
2018-04-21 10:30 | 436 | 433
2018-04-21 11:00 | 440 | 437
2018-04-21 11:30 | 446 | 444
2018-04-21 12:00 | 452 | 449
2018-04-21 12:30 | 437 | 433
2018-04-21 13:00 | 438 | 435
2018-04-21 13:30 | 445 | 441
2018-04-21 14:00 | 463 | 459
2018-04-21 14:30 | 461 | 457
2018-04-21 15:00 | 461 | 458
2018-04-21 15:30 | 470 | 467
2018-04-21 16:00 | 465 | 461
2018-04-21 16:30 | 467 | 464
2018-04-21 17:00 | 481 | 478
2018-04-21 17:30 | 478 | 475
2018-04-21 18:00 | 487 | 485
2018-04-21 18:30 | 483 | 481
2018-04-21 19:00 | 479 | 477
2018-04-21 19:30 | 472 | 469
2018-04-21 20:00 | 473 | 471
2018-04-21 20:30 | 470 | 468
2018-04-21 21:00 | 458 | 455
2018-04-21 21:30 | 451 | 447
2018-04-21 22:00 | 446 | 441
2018-04-21 22:30 | 433 | 429
2018-04-21 23:00 | 422 | 416
2018-04-21 23:30 | 412 | 405
2018-04-22 | 391 | 382
2018-04-22 00:30 | 371 | 361
2018-04-22 01:00 | 363 | 351
2018-04-22 01:30 | 353 | 340
2018-04-22 02:00 | 341 | 327
2018-04-22 02:30 | 334 | 318
2018-04-22 03:00 | 335 | 318
2018-04-22 03:30 | 335 | 317
2018-04-22 04:00 | 336 | 318
2018-04-22 04:30 | 331 | 313
2018-04-22 05:00 | 331 | 314
2018-04-22 05:30 | 334 | 317
2018-04-22 06:00 | 345 | 329
2018-04-22 06:30 | 359 | 342
2018-04-22 07:00 | 375 | 359
2018-04-22 07:30 | 387 | 372
2018-04-22 08:00 | 400 | 387
2018-04-22 08:30 | 409 | 398
2018-04-22 09:00 | 413 | 404
2018-04-22 09:30 | 432 | 425
2018-04-22 10:00 | 435 | 429
2018-04-22 10:30 | 430 | 423
2018-04-22 11:00 | 407 | 400
2018-04-22 11:30 | 424 | 418
2018-04-22 12:00 | 420 | 414
2018-04-22 12:30 | 410 | 404
2018-04-22 13:00 | 412 | 406
2018-04-22 13:30 | 414 | 408
2018-04-22 14:00 | 421 | 416
2018-04-22 14:30 | 422 | 417
2018-04-22 15:00 | 435 | 430
2018-04-22 15:30 | 446 | 442
2018-04-22 16:00 | 466 | 461
2018-04-22 16:30 | 477 | 473
2018-04-22 17:00 | 491 | 487
2018-04-22 17:30 | 498 | 493
2018-04-22 18:00 | 522 | 517
2018-04-22 18:30 | 532 | 524
2018-04-22 19:00 | 510 | 501
2018-04-22 19:30 | 494 | 487
2018-04-22 20:00 | 491 | 484
2018-04-22 20:30 | 489 | 481
2018-04-22 21:00 | 472 | 464
2018-04-22 21:30 | 460 | 453
2018-04-22 22:00 | 452 | 445
2018-04-22 22:30 | 436 | 428
2018-04-22 23:00 | 424 | 416
2018-04-22 23:30 | 410 | 400
2018-04-23 | 392 | 379
2018-04-23 00:30 | 374 | 359
2018-04-23 01:00 | 357 | 340
2018-04-23 01:30 | 349 | 332
2018-04-23 02:00 | 339 | 322
2018-04-23 02:30 | 332 | 316
2018-04-23 03:00 | 333 | 316
2018-04-23 03:30 | 334 | 318
2018-04-23 04:00 | 337 | 320
2018-04-23 04:30 | 338 | 323
2018-04-23 05:00 | 344 | 330
2018-04-23 05:30 | 373 | 362
2018-04-23 06:00 | 396 | 388
2018-04-23 06:30 | 435 | 429
2018-04-23 07:00 | 470 | 467
2018-04-23 07:30 | 496 | 494
2018-04-23 08:00 | 504 | 502
2018-04-23 08:30 | 494 | 493
2018-04-23 09:00 | 488 | 487
2018-04-23 09:30 | 484 | 483
2018-04-23 10:00 | 479 | 478
2018-04-23 10:30 | 478 | 477
2018-04-23 11:00 | 481 | 481
2018-04-23 11:30 | 490 | 489
2018-04-23 12:00 | 496 | 495
2018-04-23 12:30 | 497 | 496
2018-04-23 13:00 | 505 | 504
2018-04-23 13:30 | 513 | 512
2018-04-23 14:00 | 525 | 524
2018-04-23 14:30 | 534 | 533
2018-04-23 15:00 | 527 | 526
2018-04-23 15:30 | 528 | 526
2018-04-23 16:00 | 532 | 530
2018-04-23 16:30 | 543 | 541
2018-04-23 17:00 | 554 | 552
2018-04-23 17:30 | 570 | 568
2018-04-23 18:00 | 588 | 586
2018-04-23 18:30 | 584 | 581
2018-04-23 19:00 | 568 | 564
2018-04-23 19:30 | 538 | 535
2018-04-23 20:00 | 531 | 528
2018-04-23 20:30 | 527 | 525
2018-04-23 21:00 | 509 | 507
2018-04-23 21:30 | 494 | 490
2018-04-23 22:00 | 475 | 471
2018-04-23 22:30 | 465 | 462
2018-04-23 23:00 | 444 | 440
2018-04-23 23:30 | 431 | 427
2018-04-24 | 411 | 405
2018-04-24 00:30 | 387 | 379
2018-04-24 01:00 | 365 | 355
2018-04-24 01:30 | 361 | 350
2018-04-24 02:00 | 352 | 341
2018-04-24 02:30 | 351 | 339
2018-04-24 03:00 | 350 | 337
2018-04-24 03:30 | 348 | 335
2018-04-24 04:00 | 343 | 330
2018-04-24 04:30 | 333 | 321
2018-04-24 05:00 | 345 | 334
2018-04-24 05:30 | 363 | 355
2018-04-24 06:00 | 395 | 389
2018-04-24 06:30 | 441 | 437
2018-04-24 07:00 | 479 | 475
2018-04-24 07:30 | 503 | 500
2018-04-24 08:00 | 474 | 471
2018-04-24 08:30 | 360 | 358
2018-04-24 09:00 | 350 | 349
2018-04-24 09:30 | 349 | 347
2018-04-24 10:00 | 347 | 346
2018-04-24 10:30 | 346 | 345
2018-04-24 11:00 | 341 | 340
2018-04-24 11:30 | 363 | 361
2018-04-24 12:00 | 484 | 481
2018-04-24 12:30 | 312 | 310
2018-04-24 13:00 | 311 | 310
2018-04-24 13:30 | 327 | 326
2018-04-24 14:00 | 326 | 324
2018-04-24 14:30 | 325 | 323
2018-04-24 15:00 | 479 | 477
2018-04-24 15:30 | 554 | 551
2018-04-24 16:00 | 560 | 558
2018-04-24 16:30 | 570 | 567
2018-04-24 17:00 | 573 | 570
2018-04-24 17:30 | 590 | 587
2018-04-24 18:00 | 610 | 607
2018-04-24 18:30 | 605 | 601
2018-04-24 19:00 | 595 | 591
2018-04-24 19:30 | 556 | 551
2018-04-24 20:00 | 544 | 542
2018-04-24 20:30 | 531 | 528
2018-04-24 21:00 | 512 | 507
2018-04-24 21:30 | 498 | 493
2018-04-24 22:00 | 490 | 483
2018-04-24 22:30 | 467 | 459
2018-04-24 23:00 | 454 | 446
2018-04-24 23:30 | 437 | 431
2018-04-25 | 425 | 418
2018-04-25 00:30 | 395 | 386
2018-04-25 01:00 | 386 | 376
2018-04-25 01:30 | 372 | 360
2018-04-25 02:00 | 368 | 355
2018-04-25 02:30 | 360 | 346
2018-04-25 03:00 | 355 | 340
2018-04-25 03:30 | 354 | 340
2018-04-25 04:00 | 358 | 343
2018-04-25 04:30 | 358 | 343
2018-04-25 05:00 | 357 | 341
2018-04-25 05:30 | 349 | 333
2018-04-25 06:00 | 359 | 345
2018-04-25 06:30 | 366 | 353
2018-04-25 07:00 | 379 | 367
2018-04-25 07:30 | 396 | 385
2018-04-25 08:00 | 399 | 389
2018-04-25 08:30 | 402 | 394
2018-04-25 09:00 | 405 | 397
2018-04-25 09:30 | 405 | 398
2018-04-25 10:00 | 408 | 402
2018-04-25 10:30 | 410 | 405
2018-04-25 11:00 | 417 | 412
2018-04-25 11:30 | 420 | 415
2018-04-25 12:00 | 422 | 418
2018-04-25 12:30 | 425 | 421
2018-04-25 13:00 | 422 | 419
2018-04-25 13:30 | 427 | 424
2018-04-25 14:00 | 433 | 430
2018-04-25 14:30 | 439 | 437
2018-04-25 15:00 | 443 | 440
2018-04-25 15:30 | 442 | 439
2018-04-25 16:00 | 450 | 448
2018-04-25 16:30 | 461 | 459
2018-04-25 17:00 | 477 | 476
2018-04-25 17:30 | 497 | 495
2018-04-25 18:00 | 521 | 519
2018-04-25 18:30 | 532 | 530
2018-04-25 19:00 | 515 | 513
2018-04-25 19:30 | 497 | 496
2018-04-25 20:00 | 497 | 495
2018-04-25 20:30 | 499 | 496
2018-04-25 21:00 | 478 | 474
2018-04-25 21:30 | 458 | 455
2018-04-25 22:00 | 449 | 445
2018-04-25 22:30 | 433 | 429
2018-04-25 23:00 | 421 | 416
2018-04-25 23:30 | 412 | 406
2018-04-26 | 400 | 392
2018-04-26 00:30 | 379 | 370
2018-04-26 01:00 | 373 | 362
2018-04-26 01:30 | 367 | 355
2018-04-26 02:00 | 361 | 349
2018-04-26 02:30 | 360 | 347
2018-04-26 03:00 | 356 | 341
2018-04-26 03:30 | 352 | 338
2018-04-26 04:00 | 354 | 340
2018-04-26 04:30 | 363 | 349
2018-04-26 05:00 | 365 | 353
2018-04-26 05:30 | 386 | 377
2018-04-26 06:00 | 412 | 407
2018-04-26 06:30 | 449 | 445
2018-04-26 07:00 | 492 | 487
2018-04-26 07:30 | 532 | 521
2018-04-26 08:00 | 540 | 530
2018-04-26 08:30 | 554 | 542
2018-04-26 09:00 | 537 | 533
2018-04-26 09:30 | 538 | 535
2018-04-26 10:00 | 535 | 533
2018-04-26 10:30 | 536 | 535
2018-04-26 11:00 | 537 | 536
2018-04-26 11:30 | 539 | 538
2018-04-26 12:00 | 541 | 540
2018-04-26 12:30 | 543 | 541
2018-04-26 13:00 | 539 | 538
2018-04-26 13:30 | 538 | 536
2018-04-26 14:00 | 545 | 542
2018-04-26 14:30 | 546 | 543
2018-04-26 15:00 | 552 | 550
2018-04-26 15:30 | 560 | 558
2018-04-26 16:00 | 580 | 577
2018-04-26 16:30 | 593 | 590
2018-04-26 17:00 | 604 | 600
2018-04-26 17:30 | 618 | 614
2018-04-26 18:00 | 645 | 641
2018-04-26 18:30 | 635 | 630
2018-04-26 19:00 | 623 | 618
2018-04-26 19:30 | 592 | 586
2018-04-26 20:00 | 587 | 583
2018-04-26 20:30 | 583 | 579
2018-04-26 21:00 | 559 | 554
2018-04-26 21:30 | 530 | 526
2018-04-26 22:00 | 506 | 505
2018-04-26 22:30 | 492 | 491
2018-04-26 23:00 | 467 | 465
2018-04-26 23:30 | 458 | 456
2018-04-27 | 437 | 434
2018-04-27 00:30 | 407 | 403
2018-04-27 01:00 | 387 | 382
2018-04-27 01:30 | 374 | 367
2018-04-27 02:00 | 369 | 361
2018-04-27 02:30 | 362 | 355
2018-04-27 03:00 | 362 | 353
2018-04-27 03:30 | 366 | 358
2018-04-27 04:00 | 369 | 361
2018-04-27 04:30 | 367 | 360
2018-04-27 05:00 | 371 | 364
2018-04-27 05:30 | 392 | 386
2018-04-27 06:00 | 420 | 417
2018-04-27 06:30 | 453 | 451
2018-04-27 07:00 | 491 | 487
2018-04-27 07:30 | 525 | 519
2018-04-27 08:00 | 537 | 531
2018-04-27 08:30 | 538 | 532
2018-04-27 09:00 | 533 | 527
2018-04-27 09:30 | 529 | 523
2018-04-27 10:00 | 526 | 521
2018-04-27 10:30 | 521 | 516
2018-04-27 11:00 | 518 | 513
2018-04-27 11:30 | 513 | 509
2018-04-27 12:00 | 514 | 510
2018-04-27 12:30 | 514 | 511
2018-04-27 13:00 | 513 | 509
2018-04-27 13:30 | 518 | 515
2018-04-27 14:00 | 523 | 522
2018-04-27 14:30 | 528 | 527
2018-04-27 15:00 | 535 | 533
2018-04-27 15:30 | 538 | 536
2018-04-27 16:00 | 553 | 551
2018-04-27 16:30 | 564 | 560
2018-04-27 17:00 | 570 | 566
2018-04-27 17:30 | 571 | 567
2018-04-27 18:00 | 586 | 581
2018-04-27 18:30 | 576 | 570
2018-04-27 19:00 | 563 | 556
2018-04-27 19:30 | 539 | 533
2018-04-27 20:00 | 534 | 528
2018-04-27 20:30 | 529 | 524
2018-04-27 21:00 | 511 | 507
2018-04-27 21:30 | 492 | 488
2018-04-27 22:00 | 484 | 479
2018-04-27 22:30 | 475 | 469
2018-04-27 23:00 | 447 | 440
2018-04-27 23:30 | 436 | 427
2018-04-28 | 417 | 406
2018-04-28 00:30 | 398 | 390
2018-04-28 01:00 | 384 | 375
2018-04-28 01:30 | 361 | 350
2018-04-28 02:00 | 350 | 339
2018-04-28 02:30 | 341 | 330
2018-04-28 03:00 | 336 | 324
2018-04-28 03:30 | 333 | 321
2018-04-28 04:00 | 333 | 320
2018-04-28 04:30 | 332 | 319
2018-04-28 05:00 | 330 | 317
2018-04-28 05:30 | 344 | 333
2018-04-28 06:00 | 358 | 347
2018-04-28 06:30 | 369 | 359
2018-04-28 07:00 | 386 | 377
2018-04-28 07:30 | 417 | 409
2018-04-28 08:00 | 433 | 428
2018-04-28 08:30 | 431 | 427
2018-04-28 09:00 | 442 | 439
2018-04-28 09:30 | 453 | 450
2018-04-28 10:00 | 446 | 444
2018-04-28 10:30 | 456 | 454
2018-04-28 11:00 | 435 | 433
2018-04-28 11:30 | 403 | 400
2018-04-28 12:00 | 395 | 393
2018-04-28 12:30 | 397 | 395
2018-04-28 13:00 | 408 | 406
2018-04-28 13:30 | 403 | 401
2018-04-28 14:00 | 415 | 413
2018-04-28 14:30 | 423 | 421
2018-04-28 15:00 | 422 | 420
2018-04-28 15:30 | 429 | 427
2018-04-28 16:00 | 431 | 429
2018-04-28 16:30 | 446 | 444
2018-04-28 17:00 | 469 | 467
2018-04-28 17:30 | 490 | 487
2018-04-28 18:00 | 501 | 499
2018-04-28 18:30 | 490 | 487
2018-04-28 19:00 | 484 | 482
2018-04-28 19:30 | 466 | 463
2018-04-28 20:00 | 468 | 464
2018-04-28 20:30 | 465 | 462
2018-04-28 21:00 | 448 | 446
2018-04-28 21:30 | 437 | 433
2018-04-28 22:00 | 430 | 426
2018-04-28 22:30 | 419 | 414
2018-04-28 23:00 | 413 | 408
2018-04-28 23:30 | 405 | 399
2018-04-29 | 388 | 380
2018-04-29 00:30 | 365 | 355
2018-04-29 01:00 | 356 | 344
2018-04-29 01:30 | 347 | 335
2018-04-29 02:00 | 342 | 329
2018-04-29 02:30 | 338 | 325
2018-04-29 03:00 | 328 | 313
2018-04-29 03:30 | 327 | 310
2018-04-29 04:00 | 325 | 308
2018-04-29 04:30 | 318 | 301
2018-04-29 05:00 | 314 | 299
2018-04-29 05:30 | 324 | 309
2018-04-29 06:00 | 330 | 316
2018-04-29 06:30 | 336 | 322
2018-04-29 07:00 | 347 | 333
2018-04-29 07:30 | 365 | 352
2018-04-29 08:00 | 379 | 368
2018-04-29 08:30 | 398 | 389
2018-04-29 09:00 | 401 | 392
2018-04-29 09:30 | 403 | 396
2018-04-29 10:00 | 396 | 389
2018-04-29 10:30 | 394 | 388
2018-04-29 11:00 | 407 | 401
2018-04-29 11:30 | 407 | 403
2018-04-29 12:00 | 410 | 406
2018-04-29 12:30 | 403 | 398
2018-04-29 13:00 | 391 | 386
2018-04-29 13:30 | 396 | 391
2018-04-29 14:00 | 408 | 404
2018-04-29 14:30 | 416 | 412
2018-04-29 15:00 | 420 | 416
2018-04-29 15:30 | 429 | 426
2018-04-29 16:00 | 443 | 440
2018-04-29 16:30 | 454 | 452
2018-04-29 17:00 | 475 | 473
2018-04-29 17:30 | 493 | 490
2018-04-29 18:00 | 509 | 507
2018-04-29 18:30 | 503 | 501
2018-04-29 19:00 | 497 | 494
2018-04-29 19:30 | 477 | 474
2018-04-29 20:00 | 468 | 467
2018-04-29 20:30 | 468 | 467
2018-04-29 21:00 | 448 | 446
2018-04-29 21:30 | 432 | 430
2018-04-29 22:00 | 411 | 409
2018-04-29 22:30 | 383 | 380
2018-04-29 23:00 | 365 | 362
2018-04-29 23:30 | 367 | 363
2018-04-30 | 362 | 355
2018-04-30 00:30 | 346 | 338
2018-04-30 01:00 | 336 | 327
2018-04-30 01:30 | 327 | 316
2018-04-30 02:00 | 323 | 312
2018-04-30 02:30 | 316 | 304
2018-04-30 03:00 | 308 | 296
2018-04-30 03:30 | 310 | 297
2018-04-30 04:00 | 311 | 299
2018-04-30 04:30 | 319 | 307
2018-04-30 05:00 | 332 | 322
2018-04-30 05:30 | 351 | 344
2018-04-30 06:00 | 377 | 371
2018-04-30 06:30 | 419 | 415
2018-04-30 07:00 | 457 | 455
2018-04-30 07:30 | 481 | 480
2018-04-30 08:00 | 485 | 483
2018-04-30 08:30 | 484 | 482
2018-04-30 09:00 | 480 | 478
2018-04-30 09:30 | 473 | 471
2018-04-30 10:00 | 458 | 457
2018-04-30 10:30 | 440 | 439
2018-04-30 11:00 | 435 | 434
2018-04-30 11:30 | 438 | 437
2018-04-30 12:00 | 444 | 444
2018-04-30 12:30 | 437 | 436
2018-04-30 13:00 | 444 | 444
2018-04-30 13:30 | 454 | 454
2018-04-30 14:00 | 465 | 465
2018-04-30 14:30 | 481 | 481
2018-04-30 15:00 | 466 | 466
2018-04-30 15:30 | 464 | 464
2018-04-30 16:00 | 472 | 472
2018-04-30 16:30 | 497 | 496
2018-04-30 17:00 | 516 | 516
2018-04-30 17:30 | 529 | 528
2018-04-30 18:00 | 561 | 560
2018-04-30 18:30 | 559 | 558
2018-04-30 19:00 | 557 | 556
2018-04-30 19:30 | 545 | 544
2018-04-30 20:00 | 535 | 535
2018-04-30 20:30 | 532 | 532
2018-04-30 21:00 | 500 | 499
2018-04-30 21:30 | 474 | 473
2018-04-30 22:00 | 466 | 465
2018-04-30 22:30 | 455 | 452
2018-04-30 23:00 | 430 | 427
2018-04-30 23:30 | 415 | 410
2018-05-01 | 395 | 390
2018-05-01 00:30 | 364 | 359
2018-05-01 01:00 | 345 | 339
2018-05-01 01:30 | 333 | 327
2018-05-01 02:00 | 333 | 326
2018-05-01 02:30 | 331 | 323
2018-05-01 03:00 | 327 | 318
2018-05-01 03:30 | 321 | 313
2018-05-01 04:00 | 315 | 307
2018-05-01 04:30 | 319 | 312
2018-05-01 05:00 | 329 | 323
2018-05-01 05:30 | 365 | 361
2018-05-01 06:00 | 391 | 388
2018-05-01 06:30 | 437 | 434
2018-05-01 07:00 | 478 | 477
2018-05-01 07:30 | 502 | 501
2018-05-01 08:00 | 514 | 511
2018-05-01 08:30 | 504 | 502
2018-05-01 09:00 | 479 | 477
2018-05-01 09:30 | 480 | 478
2018-05-01 10:00 | 472 | 470
2018-05-01 10:30 | 472 | 470
2018-05-01 11:00 | 478 | 477
2018-05-01 11:30 | 482 | 481
2018-05-01 12:00 | 480 | 479
2018-05-01 12:30 | 477 | 476
2018-05-01 13:00 | 488 | 487
2018-05-01 13:30 | 501 | 499
2018-05-01 14:00 | 490 | 488
2018-05-01 14:30 | 475 | 473
2018-05-01 15:00 | 468 | 467
2018-05-01 15:30 | 480 | 479
2018-05-01 16:00 | 511 | 509
2018-05-01 16:30 | 524 | 523
2018-05-01 17:00 | 532 | 530
2018-05-01 17:30 | 550 | 549
2018-05-01 18:00 | 576 | 575
2018-05-01 18:30 | 566 | 564
2018-05-01 19:00 | 547 | 544
2018-05-01 19:30 | 526 | 524
2018-05-01 20:00 | 511 | 510
2018-05-01 20:30 | 507 | 507
2018-05-01 21:00 | 496 | 495
2018-05-01 21:30 | 477 | 476
2018-05-01 22:00 | 456 | 455
2018-05-01 22:30 | 445 | 443
2018-05-01 23:00 | 431 | 430
2018-05-01 23:30 | 420 | 419
2018-05-02 | 407 | 405
2018-05-02 00:30 | 376 | 372
2018-05-02 01:00 | 356 | 350
2018-05-02 01:30 | 343 | 337
2018-05-02 02:00 | 335 | 328
2018-05-02 02:30 | 328 | 321
2018-05-02 03:00 | 329 | 322
2018-05-02 03:30 | 330 | 323
2018-05-02 04:00 | 334 | 328
2018-05-02 04:30 | 335 | 330
2018-05-02 05:00 | 346 | 341
2018-05-02 05:30 | 358 | 355
2018-05-02 06:00 | 385 | 383
2018-05-02 06:30 | 432 | 432
2018-05-02 07:00 | 477 | 476
2018-05-02 07:30 | 503 | 502
2018-05-02 08:00 | 508 | 508
2018-05-02 08:30 | 502 | 502
2018-05-02 09:00 | 478 | 478
2018-05-02 09:30 | 462 | 462
2018-05-02 10:00 | 459 | 459
2018-05-02 10:30 | 490 | 490
2018-05-02 11:00 | 487 | 487
2018-05-02 11:30 | 475 | 475
2018-05-02 12:00 | 467 | 467
2018-05-02 12:30 | 465 | 465
2018-05-02 13:00 | 463 | 463
2018-05-02 13:30 | 475 | 475
2018-05-02 14:00 | 459 | 459
2018-05-02 14:30 | 468 | 468
2018-05-02 15:00 | 481 | 481
2018-05-02 15:30 | 494 | 494
2018-05-02 16:00 | 516 | 516
2018-05-02 16:30 | 534 | 534
2018-05-02 17:00 | 557 | 556
2018-05-02 17:30 | 568 | 567
2018-05-02 18:00 | 591 | 589
2018-05-02 18:30 | 587 | 579
2018-05-02 19:00 | 578 | 569
2018-05-02 19:30 | 542 | 541
2018-05-02 20:00 | 529 | 528
2018-05-02 20:30 | 518 | 518
2018-05-02 21:00 | 492 | 491
2018-05-02 21:30 | 467 | 466
2018-05-02 22:00 | 461 | 460
2018-05-02 22:30 | 438 | 436
2018-05-02 23:00 | 424 | 421
2018-05-02 23:30 | 414 | 411
2018-05-03 | 386 | 383
2018-05-03 00:30 | 357 | 353
2018-05-03 01:00 | 345 | 340
2018-05-03 01:30 | 330 | 325
2018-05-03 02:00 | 325 | 320
2018-05-03 02:30 | 320 | 314
2018-05-03 03:00 | 321 | 314
2018-05-03 03:30 | 319 | 312
2018-05-03 04:00 | 317 | 311
2018-05-03 04:30 | 325 | 319
2018-05-03 05:00 | 338 | 332
2018-05-03 05:30 | 358 | 355
2018-05-03 06:00 | 383 | 381
2018-05-03 06:30 | 409 | 408
2018-05-03 07:00 | 447 | 447
2018-05-03 07:30 | 481 | 481
2018-05-03 08:00 | 484 | 483
2018-05-03 08:30 | 484 | 484
2018-05-03 09:00 | 471 | 470
2018-05-03 09:30 | 469 | 469
2018-05-03 10:00 | 471 | 471
2018-05-03 10:30 | 459 | 459
2018-05-03 11:00 | 461 | 461
2018-05-03 11:30 | 466 | 465
2018-05-03 12:00 | 479 | 479
2018-05-03 12:30 | 489 | 489
2018-05-03 13:00 | 490 | 490
2018-05-03 13:30 | 494 | 494
2018-05-03 14:00 | 506 | 506
2018-05-03 14:30 | 508 | 508
2018-05-03 15:00 | 523 | 523
2018-05-03 15:30 | 520 | 520
2018-05-03 16:00 | 533 | 532
2018-05-03 16:30 | 547 | 547
2018-05-03 17:00 | 559 | 559
2018-05-03 17:30 | 575 | 575
2018-05-03 18:00 | 593 | 592
2018-05-03 18:30 | 581 | 578
2018-05-03 19:00 | 575 | 572
2018-05-03 19:30 | 555 | 553
2018-05-03 20:00 | 551 | 550
2018-05-03 20:30 | 538 | 536
2018-05-03 21:00 | 501 | 501
2018-05-03 21:30 | 481 | 480
2018-05-03 22:00 | 457 | 456
2018-05-03 22:30 | 434 | 434
2018-05-03 23:00 | 413 | 413
2018-05-03 23:30 | 405 | 404
2018-05-04 | 384 | 382
2018-05-04 00:30 | 358 | 355
2018-05-04 01:00 | 349 | 345
2018-05-04 01:30 | 330 | 326
2018-05-04 02:00 | 322 | 317
2018-05-04 02:30 | 315 | 309
2018-05-04 03:00 | 306 | 300
2018-05-04 03:30 | 301 | 295
2018-05-04 04:00 | 294 | 289
2018-05-04 04:30 | 296 | 292
2018-05-04 05:00 | 309 | 305
2018-05-04 05:30 | 339 | 336
2018-05-04 06:00 | 362 | 361
2018-05-04 06:30 | 401 | 401
2018-05-04 07:00 | 449 | 449
2018-05-04 07:30 | 479 | 479
2018-05-04 08:00 | 479 | 478
2018-05-04 08:30 | 476 | 476
2018-05-04 09:00 | 465 | 465
2018-05-04 09:30 | 461 | 461
2018-05-04 10:00 | 459 | 459
2018-05-04 10:30 | 457 | 457
2018-05-04 11:00 | 460 | 459
2018-05-04 11:30 | 467 | 467
2018-05-04 12:00 | 474 | 474
2018-05-04 12:30 | 464 | 464
2018-05-04 13:00 | 460 | 460
2018-05-04 13:30 | 453 | 453
2018-05-04 14:00 | 462 | 462
2018-05-04 14:30 | 475 | 475
2018-05-04 15:00 | 485 | 484
2018-05-04 15:30 | 497 | 497
2018-05-04 16:00 | 514 | 514
2018-05-04 16:30 | 528 | 527
2018-05-04 17:00 | 540 | 539
2018-05-04 17:30 | 545 | 544
2018-05-04 18:00 | 553 | 552
2018-05-04 18:30 | 533 | 531
2018-05-04 19:00 | 527 | 525
2018-05-04 19:30 | 519 | 516
2018-05-04 20:00 | 514 | 513
2018-05-04 20:30 | 509 | 507
2018-05-04 21:00 | 494 | 492
2018-05-04 21:30 | 474 | 471
2018-05-04 22:00 | 463 | 460
2018-05-04 22:30 | 447 | 445
2018-05-04 23:00 | 428 | 426
2018-05-04 23:30 | 415 | 413
2018-05-05 | 390 | 388
2018-05-05 00:30 | 363 | 359
2018-05-05 01:00 | 348 | 343
2018-05-05 01:30 | 341 | 335
2018-05-05 02:00 | 339 | 333
2018-05-05 02:30 | 334 | 327
2018-05-05 03:00 | 324 | 318
2018-05-05 03:30 | 323 | 317
2018-05-05 04:00 | 325 | 319
2018-05-05 04:30 | 328 | 322
2018-05-05 05:00 | 329 | 323
2018-05-05 05:30 | 335 | 329
2018-05-05 06:00 | 346 | 341
2018-05-05 06:30 | 361 | 357
2018-05-05 07:00 | 373 | 369
2018-05-05 07:30 | 398 | 395
2018-05-05 08:00 | 414 | 412
2018-05-05 08:30 | 422 | 421
2018-05-05 09:00 | 425 | 424
2018-05-05 09:30 | 426 | 425
2018-05-05 10:00 | 420 | 418
2018-05-05 10:30 | 413 | 412
2018-05-05 11:00 | 416 | 415
2018-05-05 11:30 | 401 | 400
2018-05-05 12:00 | 392 | 391
2018-05-05 12:30 | 385 | 384
2018-05-05 13:00 | 382 | 381
2018-05-05 13:30 | 387 | 386
2018-05-05 14:00 | 388 | 387
2018-05-05 14:30 | 396 | 395
2018-05-05 15:00 | 411 | 410
2018-05-05 15:30 | 425 | 424
2018-05-05 16:00 | 446 | 445
2018-05-05 16:30 | 458 | 457
2018-05-05 17:00 | 476 | 476
2018-05-05 17:30 | 488 | 488
2018-05-05 18:00 | 502 | 502
2018-05-05 18:30 | 500 | 499
2018-05-05 19:00 | 490 | 490
2018-05-05 19:30 | 477 | 476
2018-05-05 20:00 | 477 | 476
2018-05-05 20:30 | 467 | 466
2018-05-05 21:00 | 450 | 449
2018-05-05 21:30 | 442 | 441
2018-05-05 22:00 | 438 | 436
2018-05-05 22:30 | 423 | 422
2018-05-05 23:00 | 414 | 412
2018-05-05 23:30 | 404 | 402
2018-05-06 | 384 | 380
2018-05-06 00:30 | 373 | 368
2018-05-06 01:00 | 359 | 353
2018-05-06 01:30 | 350 | 342
2018-05-06 02:00 | 335 | 326
2018-05-06 02:30 | 329 | 319
2018-05-06 03:00 | 329 | 319
2018-05-06 03:30 | 330 | 321
2018-05-06 04:00 | 330 | 320
2018-05-06 04:30 | 327 | 317
2018-05-06 05:00 | 322 | 313
2018-05-06 05:30 | 321 | 312
2018-05-06 06:00 | 328 | 319
2018-05-06 06:30 | 335 | 326
2018-05-06 07:00 | 347 | 338
2018-05-06 07:30 | 358 | 351
2018-05-06 08:00 | 376 | 369
2018-05-06 08:30 | 386 | 380
2018-05-06 09:00 | 388 | 383
2018-05-06 09:30 | 388 | 384
2018-05-06 10:00 | 391 | 388
2018-05-06 10:30 | 380 | 377
2018-05-06 11:00 | 368 | 365
2018-05-06 11:30 | 358 | 355
2018-05-06 12:00 | 355 | 352
2018-05-06 12:30 | 342 | 339
2018-05-06 13:00 | 345 | 343
2018-05-06 13:30 | 357 | 354
2018-05-06 14:00 | 388 | 386
2018-05-06 14:30 | 402 | 400
2018-05-06 15:00 | 408 | 405
2018-05-06 15:30 | 417 | 415
2018-05-06 16:00 | 427 | 425
2018-05-06 16:30 | 442 | 440
2018-05-06 17:00 | 464 | 462
2018-05-06 17:30 | 475 | 474
2018-05-06 18:00 | 515 | 512
2018-05-06 18:30 | 510 | 504
2018-05-06 19:00 | 498 | 492
2018-05-06 19:30 | 467 | 463
2018-05-06 20:00 | 458 | 457
2018-05-06 20:30 | 461 | 460
2018-05-06 21:00 | 445 | 443
2018-05-06 21:30 | 438 | 436
2018-05-06 22:00 | 425 | 423
2018-05-06 22:30 | 401 | 398
2018-05-06 23:00 | 388 | 385
2018-05-06 23:30 | 383 | 379
2018-05-07 | 371 | 366
2018-05-07 00:30 | 351 | 344
2018-05-07 01:00 | 332 | 324
2018-05-07 01:30 | 319 | 308
2018-05-07 02:00 | 310 | 299
2018-05-07 02:30 | 315 | 302
2018-05-07 03:00 | 304 | 290
2018-05-07 03:30 | 301 | 287
2018-05-07 04:00 | 299 | 284
2018-05-07 04:30 | 289 | 274
2018-05-07 05:00 | 307 | 293
2018-05-07 05:30 | 324 | 310
2018-05-07 06:00 | 347 | 335
2018-05-07 06:30 | 371 | 360
2018-05-07 07:00 | 376 | 365
2018-05-07 07:30 | 378 | 371
2018-05-07 08:00 | 396 | 390
2018-05-07 08:30 | 401 | 396
2018-05-07 09:00 | 401 | 397
2018-05-07 09:30 | 405 | 402
2018-05-07 10:00 | 423 | 420
2018-05-07 10:30 | 413 | 411
2018-05-07 11:00 | 410 | 408
2018-05-07 11:30 | 406 | 404
2018-05-07 12:00 | 403 | 401
2018-05-07 12:30 | 404 | 402
2018-05-07 13:00 | 398 | 396
2018-05-07 13:30 | 400 | 398
2018-05-07 14:00 | 413 | 411
2018-05-07 14:30 | 429 | 428
2018-05-07 15:00 | 435 | 433
2018-05-07 15:30 | 438 | 437
2018-05-07 16:00 | 438 | 436
2018-05-07 16:30 | 446 | 445
2018-05-07 17:00 | 467 | 466
2018-05-07 17:30 | 485 | 484
2018-05-07 18:00 | 484 | 482
2018-05-07 18:30 | 471 | 468
2018-05-07 19:00 | 466 | 463
2018-05-07 19:30 | 458 | 455
2018-05-07 20:00 | 454 | 451
2018-05-07 20:30 | 449 | 447
2018-05-07 21:00 | 434 | 432
2018-05-07 21:30 | 423 | 422
2018-05-07 22:00 | 417 | 415
2018-05-07 22:30 | 414 | 411
2018-05-07 23:00 | 389 | 386
2018-05-07 23:30 | 371 | 368
2018-05-08 | 363 | 357
2018-05-08 00:30 | 348 | 340
2018-05-08 01:00 | 342 | 333
2018-05-08 01:30 | 330 | 321
2018-05-08 02:00 | 316 | 307
2018-05-08 02:30 | 313 | 303
2018-05-08 03:00 | 313 | 303
2018-05-08 03:30 | 314 | 304
2018-05-08 04:00 | 321 | 312
2018-05-08 04:30 | 327 | 319
2018-05-08 05:00 | 335 | 327
2018-05-08 05:30 | 347 | 341
2018-05-08 06:00 | 366 | 363
2018-05-08 06:30 | 423 | 419
2018-05-08 07:00 | 464 | 455
2018-05-08 07:30 | 486 | 481
2018-05-08 08:00 | 501 | 496
2018-05-08 08:30 | 492 | 487
2018-05-08 09:00 | 488 | 484
2018-05-08 09:30 | 516 | 505
2018-05-08 10:00 | 529 | 518
2018-05-08 10:30 | 528 | 518
2018-05-08 11:00 | 532 | 522
2018-05-08 11:30 | 513 | 502
2018-05-08 12:00 | 506 | 495
2018-05-08 12:30 | 518 | 508
2018-05-08 13:00 | 514 | 504
2018-05-08 13:30 | 526 | 517
2018-05-08 14:00 | 542 | 532
2018-05-08 14:30 | 534 | 524
2018-05-08 15:00 | 526 | 515
2018-05-08 15:30 | 520 | 509
2018-05-08 16:00 | 537 | 525
2018-05-08 16:30 | 545 | 533
2018-05-08 17:00 | 554 | 543
2018-05-08 17:30 | 576 | 568
2018-05-08 18:00 | 603 | 594
2018-05-08 18:30 | 573 | 562
2018-05-08 19:00 | 567 | 554
2018-05-08 19:30 | 537 | 532
2018-05-08 20:00 | 515 | 514
2018-05-08 20:30 | 507 | 505
2018-05-08 21:00 | 476 | 475
2018-05-08 21:30 | 465 | 463
2018-05-08 22:00 | 453 | 451
2018-05-08 22:30 | 449 | 447
2018-05-08 23:00 | 441 | 440
2018-05-08 23:30 | 428 | 426
2018-05-09 | 400 | 398
2018-05-09 00:30 | 377 | 373
2018-05-09 01:00 | 368 | 364
2018-05-09 01:30 | 351 | 347
2018-05-09 02:00 | 332 | 328
2018-05-09 02:30 | 331 | 327
2018-05-09 03:00 | 322 | 318
2018-05-09 03:30 | 329 | 324
2018-05-09 04:00 | 335 | 331
2018-05-09 04:30 | 341 | 337
2018-05-09 05:00 | 345 | 342
2018-05-09 05:30 | 366 | 364
2018-05-09 06:00 | 391 | 389
2018-05-09 06:30 | 441 | 440
2018-05-09 07:00 | 467 | 467
2018-05-09 07:30 | 484 | 484
2018-05-09 08:00 | 483 | 482
2018-05-09 08:30 | 464 | 463
2018-05-09 09:00 | 440 | 440
2018-05-09 09:30 | 441 | 440
2018-05-09 10:00 | 438 | 438
2018-05-09 10:30 | 433 | 432
2018-05-09 11:00 | 422 | 422
2018-05-09 11:30 | 417 | 417
2018-05-09 12:00 | 422 | 422
2018-05-09 12:30 | 426 | 426
2018-05-09 13:00 | 433 | 433
2018-05-09 13:30 | 442 | 442
2018-05-09 14:00 | 455 | 454
2018-05-09 14:30 | 472 | 471
2018-05-09 15:00 | 484 | 483
2018-05-09 15:30 | 482 | 481
2018-05-09 16:00 | 493 | 492
2018-05-09 16:30 | 497 | 496
2018-05-09 17:00 | 507 | 506
2018-05-09 17:30 | 531 | 530
2018-05-09 18:00 | 543 | 542
2018-05-09 18:30 | 518 | 517
2018-05-09 19:00 | 521 | 519
2018-05-09 19:30 | 514 | 510
2018-05-09 20:00 | 505 | 503
2018-05-09 20:30 | 483 | 480
2018-05-09 21:00 | 461 | 459
2018-05-09 21:30 | 445 | 443
2018-05-09 22:00 | 429 | 428
2018-05-09 22:30 | 410 | 410
2018-05-09 23:00 | 409 | 408
2018-05-09 23:30 | 397 | 396
2018-05-10 | 376 | 374
2018-05-10 00:30 | 354 | 352
2018-05-10 01:00 | 334 | 330
2018-05-10 01:30 | 316 | 311
2018-05-10 02:00 | 309 | 304
2018-05-10 02:30 | 306 | 301
2018-05-10 03:00 | 302 | 296
2018-05-10 03:30 | 289 | 284
2018-05-10 04:00 | 291 | 285
2018-05-10 04:30 | 299 | 294
2018-05-10 05:00 | 315 | 312
2018-05-10 05:30 | 342 | 339
2018-05-10 06:00 | 369 | 368
2018-05-10 06:30 | 413 | 413
2018-05-10 07:00 | 462 | 462
2018-05-10 07:30 | 495 | 495
2018-05-10 08:00 | 573 | 573
2018-05-10 08:30 | 551 | 551
2018-05-10 09:00 | 532 | 531
2018-05-10 09:30 | 518 | 516
2018-05-10 10:00 | 510 | 508
2018-05-10 10:30 | 498 | 496
2018-05-10 11:00 | 491 | 490
2018-05-10 11:30 | 482 | 482
2018-05-10 12:00 | 482 | 482
2018-05-10 12:30 | 488 | 488
2018-05-10 13:00 | 497 | 497
2018-05-10 13:30 | 510 | 510
2018-05-10 14:00 | 521 | 521
2018-05-10 14:30 | 540 | 539
2018-05-10 15:00 | 466 | 466
2018-05-10 15:30 | 481 | 481
2018-05-10 16:00 | 498 | 498
2018-05-10 16:30 | 513 | 513
2018-05-10 17:00 | 523 | 522
2018-05-10 17:30 | 531 | 531
2018-05-10 18:00 | 555 | 555
2018-05-10 18:30 | 545 | 543
2018-05-10 19:00 | 541 | 540
2018-05-10 19:30 | 529 | 527
2018-05-10 20:00 | 517 | 515
2018-05-10 20:30 | 505 | 504
2018-05-10 21:00 | 488 | 488
2018-05-10 21:30 | 469 | 469
2018-05-10 22:00 | 451 | 450
2018-05-10 22:30 | 437 | 436
2018-05-10 23:00 | 414 | 414
2018-05-10 23:30 | 387 | 387
2018-05-11 | 364 | 363
2018-05-11 00:30 | 350 | 348
2018-05-11 01:00 | 335 | 332
2018-05-11 01:30 | 324 | 320
2018-05-11 02:00 | 316 | 312
2018-05-11 02:30 | 313 | 309
2018-05-11 03:00 | 301 | 298
2018-05-11 03:30 | 293 | 289
2018-05-11 04:00 | 298 | 294
2018-05-11 04:30 | 305 | 301
2018-05-11 05:00 | 312 | 309
2018-05-11 05:30 | 339 | 337
2018-05-11 06:00 | 382 | 381
2018-05-11 06:30 | 423 | 423
2018-05-11 07:00 | 459 | 459
2018-05-11 07:30 | 486 | 486
2018-05-11 08:00 | 502 | 501
2018-05-11 08:30 | 529 | 528
2018-05-11 09:00 | 545 | 545
2018-05-11 09:30 | 535 | 535
2018-05-11 10:00 | 511 | 511
2018-05-11 10:30 | 501 | 500
2018-05-11 11:00 | 489 | 488
2018-05-11 11:30 | 481 | 480
2018-05-11 12:00 | 480 | 480
2018-05-11 12:30 | 478 | 478
2018-05-11 13:00 | 475 | 475
2018-05-11 13:30 | 433 | 433
2018-05-11 14:00 | 436 | 436
2018-05-11 14:30 | 440 | 440
2018-05-11 15:00 | 451 | 451
2018-05-11 15:30 | 463 | 463
2018-05-11 16:00 | 481 | 481
2018-05-11 16:30 | 494 | 494
2018-05-11 17:00 | 520 | 520
2018-05-11 17:30 | 535 | 535
2018-05-11 18:00 | 546 | 545
2018-05-11 18:30 | 531 | 529
2018-05-11 19:00 | 531 | 529
2018-05-11 19:30 | 505 | 505
2018-05-11 20:00 | 515 | 515
2018-05-11 20:30 | 512 | 512
2018-05-11 21:00 | 494 | 494
2018-05-11 21:30 | 481 | 480
2018-05-11 22:00 | 464 | 463
2018-05-11 22:30 | 465 | 464
2018-05-11 23:00 | 445 | 444
2018-05-11 23:30 | 421 | 419
2018-05-12 | 393 | 391
2018-05-12 00:30 | 368 | 364
2018-05-12 01:00 | 349 | 345
2018-05-12 01:30 | 330 | 325
2018-05-12 02:00 | 311 | 306
2018-05-12 02:30 | 308 | 303
2018-05-12 03:00 | 302 | 296
2018-05-12 03:30 | 293 | 287
2018-05-12 04:00 | 287 | 282
2018-05-12 04:30 | 284 | 278
2018-05-12 05:00 | 285 | 280
2018-05-12 05:30 | 302 | 297
2018-05-12 06:00 | 317 | 314
2018-05-12 06:30 | 341 | 337
2018-05-12 07:00 | 367 | 364
2018-05-12 07:30 | 381 | 379
2018-05-12 08:00 | 386 | 384
2018-05-12 08:30 | 393 | 391
2018-05-12 09:00 | 390 | 389
2018-05-12 09:30 | 389 | 387
2018-05-12 10:00 | 379 | 376
2018-05-12 10:30 | 351 | 349
2018-05-12 11:00 | 338 | 335
2018-05-12 11:30 | 332 | 329
2018-05-12 12:00 | 327 | 324
2018-05-12 12:30 | 324 | 321
2018-05-12 13:00 | 320 | 316
2018-05-12 13:30 | 328 | 324
2018-05-12 14:00 | 335 | 330
2018-05-12 14:30 | 351 | 347
2018-05-12 15:00 | 368 | 365
2018-05-12 15:30 | 391 | 388
2018-05-12 16:00 | 416 | 413
2018-05-12 16:30 | 441 | 438
2018-05-12 17:00 | 469 | 466
2018-05-12 17:30 | 490 | 489
2018-05-12 18:00 | 516 | 516
2018-05-12 18:30 | 517 | 517
2018-05-12 19:00 | 502 | 502
2018-05-12 19:30 | 492 | 491
2018-05-12 20:00 | 496 | 495
2018-05-12 20:30 | 494 | 493
2018-05-12 21:00 | 471 | 469
2018-05-12 21:30 | 459 | 457
2018-05-12 22:00 | 451 | 449
2018-05-12 22:30 | 444 | 440
2018-05-12 23:00 | 442 | 439
2018-05-12 23:30 | 433 | 430
2018-05-13 | 418 | 414
2018-05-13 00:30 | 387 | 382
2018-05-13 01:00 | 359 | 353
2018-05-13 01:30 | 340 | 333
2018-05-13 02:00 | 328 | 316
2018-05-13 02:30 | 327 | 313
2018-05-13 03:00 | 340 | 325
2018-05-13 03:30 | 348 | 333
2018-05-13 04:00 | 344 | 329
2018-05-13 04:30 | 343 | 327
2018-05-13 05:00 | 344 | 329
2018-05-13 05:30 | 352 | 337
2018-05-13 06:00 | 361 | 348
2018-05-13 06:30 | 374 | 361
2018-05-13 07:00 | 387 | 375
2018-05-13 07:30 | 386 | 376
2018-05-13 08:00 | 397 | 388
2018-05-13 08:30 | 424 | 416
2018-05-13 09:00 | 417 | 409
2018-05-13 09:30 | 402 | 394
2018-05-13 10:00 | 394 | 386
2018-05-13 10:30 | 389 | 381
2018-05-13 11:00 | 371 | 363
2018-05-13 11:30 | 356 | 348
2018-05-13 12:00 | 351 | 343
2018-05-13 12:30 | 348 | 340
2018-05-13 13:00 | 348 | 340
2018-05-13 13:30 | 348 | 340
2018-05-13 14:00 | 358 | 350
2018-05-13 14:30 | 370 | 363
2018-05-13 15:00 | 383 | 377
2018-05-13 15:30 | 401 | 395
2018-05-13 16:00 | 422 | 417
2018-05-13 16:30 | 436 | 431
2018-05-13 17:00 | 470 | 467
2018-05-13 17:30 | 505 | 504
2018-05-13 18:00 | 540 | 536
2018-05-13 18:30 | 538 | 534
2018-05-13 19:00 | 533 | 529
2018-05-13 19:30 | 512 | 508
2018-05-13 20:00 | 516 | 514
2018-05-13 20:30 | 519 | 516
2018-05-13 21:00 | 493 | 490
2018-05-13 21:30 | 465 | 461
2018-05-13 22:00 | 448 | 444
2018-05-13 22:30 | 439 | 434
2018-05-13 23:00 | 421 | 416
2018-05-13 23:30 | 410 | 403
2018-05-14 | 387 | 379
2018-05-14 00:30 | 364 | 354
2018-05-14 01:00 | 348 | 337
2018-05-14 01:30 | 338 | 325
2018-05-14 02:00 | 332 | 319
2018-05-14 02:30 | 333 | 320
2018-05-14 03:00 | 330 | 317
2018-05-14 03:30 | 332 | 319
2018-05-14 04:00 | 334 | 321
2018-05-14 04:30 | 344 | 332
2018-05-14 05:00 | 353 | 344
2018-05-14 05:30 | 387 | 380
2018-05-14 06:00 | 407 | 402
2018-05-14 06:30 | 462 | 458
2018-05-14 07:00 | 521 | 517
2018-05-14 07:30 | 548 | 544
2018-05-14 08:00 | 549 | 545
2018-05-14 08:30 | 530 | 526
2018-05-14 09:00 | 513 | 508
2018-05-14 09:30 | 495 | 490
2018-05-14 10:00 | 479 | 476
2018-05-14 10:30 | 466 | 464
2018-05-14 11:00 | 466 | 464
2018-05-14 11:30 | 462 | 460
2018-05-14 12:00 | 442 | 441
2018-05-14 12:30 | 447 | 446
2018-05-14 13:00 | 463 | 462
2018-05-14 13:30 | 480 | 479
2018-05-14 14:00 | 495 | 494
2018-05-14 14:30 | 511 | 509
2018-05-14 15:00 | 525 | 523
2018-05-14 15:30 | 540 | 537
2018-05-14 16:00 | 548 | 544
2018-05-14 16:30 | 558 | 556
2018-05-14 17:00 | 573 | 570
2018-05-14 17:30 | 590 | 588
2018-05-14 18:00 | 625 | 620
2018-05-14 18:30 | 612 | 606
2018-05-14 19:00 | 610 | 606
2018-05-14 19:30 | 591 | 587
2018-05-14 20:00 | 577 | 571
2018-05-14 20:30 | 575 | 569
2018-05-14 21:00 | 548 | 544
2018-05-14 21:30 | 538 | 536
2018-05-14 22:00 | 519 | 516
2018-05-14 22:30 | 499 | 496
2018-05-14 23:00 | 479 | 476
2018-05-14 23:30 | 465 | 461
2018-05-15 | 438 | 434
2018-05-15 00:30 | 417 | 410
2018-05-15 01:00 | 394 | 386
2018-05-15 01:30 | 377 | 368
2018-05-15 02:00 | 367 | 358
2018-05-15 02:30 | 366 | 356
2018-05-15 03:00 | 365 | 355
2018-05-15 03:30 | 368 | 358
2018-05-15 04:00 | 365 | 355
2018-05-15 04:30 | 363 | 354
2018-05-15 05:00 | 364 | 356
2018-05-15 05:30 | 388 | 382
2018-05-15 06:00 | 420 | 417
2018-05-15 06:30 | 483 | 480
2018-05-15 07:00 | 543 | 540
2018-05-15 07:30 | 569 | 565
2018-05-15 08:00 | 566 | 561
2018-05-15 08:30 | 552 | 547
2018-05-15 09:00 | 509 | 505
2018-05-15 09:30 | 475 | 472
2018-05-15 10:00 | 460 | 458
2018-05-15 10:30 | 451 | 449
2018-05-15 11:00 | 445 | 443
2018-05-15 11:30 | 443 | 440
2018-05-15 12:00 | 441 | 439
2018-05-15 12:30 | 441 | 440
2018-05-15 13:00 | 444 | 444
2018-05-15 13:30 | 457 | 456
2018-05-15 14:00 | 464 | 464
2018-05-15 14:30 | 469 | 469
2018-05-15 15:00 | 495 | 494
2018-05-15 15:30 | 521 | 520
2018-05-15 16:00 | 537 | 536
2018-05-15 16:30 | 553 | 551
2018-05-15 17:00 | 566 | 564
2018-05-15 17:30 | 588 | 587
2018-05-15 18:00 | 612 | 610
2018-05-15 18:30 | 607 | 604
2018-05-15 19:00 | 598 | 594
2018-05-15 19:30 | 582 | 578
2018-05-15 20:00 | 579 | 575
2018-05-15 20:30 | 570 | 566
2018-05-15 21:00 | 549 | 547
2018-05-15 21:30 | 537 | 535
2018-05-15 22:00 | 534 | 532
2018-05-15 22:30 | 510 | 507
2018-05-15 23:00 | 487 | 484
2018-05-15 23:30 | 473 | 469
2018-05-16 | 454 | 449
2018-05-16 00:30 | 425 | 418
2018-05-16 01:00 | 409 | 400
2018-05-16 01:30 | 394 | 384
2018-05-16 02:00 | 379 | 367
2018-05-16 02:30 | 368 | 357
2018-05-16 03:00 | 355 | 342
2018-05-16 03:30 | 356 | 344
2018-05-16 04:00 | 363 | 351
2018-05-16 04:30 | 370 | 358
2018-05-16 05:00 | 378 | 368
2018-05-16 05:30 | 395 | 387
2018-05-16 06:00 | 430 | 425
2018-05-16 06:30 | 494 | 490
2018-05-16 07:00 | 521 | 518
2018-05-16 07:30 | 538 | 530
2018-05-16 08:00 | 524 | 516
2018-05-16 08:30 | 500 | 491
2018-05-16 09:00 | 478 | 468
2018-05-16 09:30 | 456 | 450
2018-05-16 10:00 | 435 | 434
2018-05-16 10:30 | 428 | 426
2018-05-16 11:00 | 422 | 421
2018-05-16 11:30 | 414 | 413
2018-05-16 12:00 | 403 | 403
2018-05-16 12:30 | 397 | 397
2018-05-16 13:00 | 418 | 417
2018-05-16 13:30 | 432 | 431
2018-05-16 14:00 | 445 | 445
2018-05-16 14:30 | 451 | 451
2018-05-16 15:00 | 461 | 460
2018-05-16 15:30 | 480 | 479
2018-05-16 16:00 | 503 | 502
2018-05-16 16:30 | 532 | 530
2018-05-16 17:00 | 555 | 552
2018-05-16 17:30 | 575 | 573
2018-05-16 18:00 | 590 | 588
2018-05-16 18:30 | 572 | 570
2018-05-16 19:00 | 567 | 564
2018-05-16 19:30 | 554 | 550
2018-05-16 20:00 | 546 | 545
2018-05-16 20:30 | 538 | 537
2018-05-16 21:00 | 515 | 515
2018-05-16 21:30 | 493 | 492
2018-05-16 22:00 | 471 | 470
2018-05-16 22:30 | 458 | 455
2018-05-16 23:00 | 446 | 443
2018-05-16 23:30 | 425 | 420
2018-05-17 | 403 | 397
2018-05-17 00:30 | 376 | 368
2018-05-17 01:00 | 356 | 347
2018-05-17 01:30 | 344 | 334
2018-05-17 02:00 | 325 | 317
2018-05-17 02:30 | 325 | 316
2018-05-17 03:00 | 324 | 314
2018-05-17 03:30 | 323 | 313
2018-05-17 04:00 | 326 | 316
2018-05-17 04:30 | 333 | 324
2018-05-17 05:00 | 346 | 338
2018-05-17 05:30 | 375 | 370
2018-05-17 06:00 | 409 | 405
2018-05-17 06:30 | 458 | 455
2018-05-17 07:00 | 508 | 506
2018-05-17 07:30 | 528 | 525
2018-05-17 08:00 | 518 | 513
2018-05-17 08:30 | 495 | 491
2018-05-17 09:00 | 468 | 464
2018-05-17 09:30 | 449 | 446
2018-05-17 10:00 | 429 | 428
2018-05-17 10:30 | 430 | 429
2018-05-17 11:00 | 430 | 428
2018-05-17 11:30 | 435 | 434
2018-05-17 12:00 | 441 | 440
2018-05-17 12:30 | 456 | 455
2018-05-17 13:00 | 465 | 464
2018-05-17 13:30 | 481 | 480
2018-05-17 14:00 | 483 | 482
2018-05-17 14:30 | 481 | 480
2018-05-17 15:00 | 483 | 481
2018-05-17 15:30 | 492 | 490
2018-05-17 16:00 | 498 | 496
2018-05-17 16:30 | 514 | 511
2018-05-17 17:00 | 537 | 536
2018-05-17 17:30 | 558 | 556
2018-05-17 18:00 | 584 | 575
2018-05-17 18:30 | 595 | 585
2018-05-17 19:00 | 595 | 584
2018-05-17 19:30 | 582 | 576
2018-05-17 20:00 | 581 | 578
2018-05-17 20:30 | 589 | 587
2018-05-17 21:00 | 558 | 555
2018-05-17 21:30 | 542 | 538
2018-05-17 22:00 | 522 | 518
2018-05-17 22:30 | 509 | 505
2018-05-17 23:00 | 481 | 477
2018-05-17 23:30 | 466 | 462
2018-05-18 | 448 | 442
2018-05-18 00:30 | 423 | 416
2018-05-18 01:00 | 402 | 394
2018-05-18 01:30 | 389 | 379
2018-05-18 02:00 | 377 | 368
2018-05-18 02:30 | 367 | 358
2018-05-18 03:00 | 361 | 352
2018-05-18 03:30 | 362 | 353
2018-05-18 04:00 | 368 | 358
2018-05-18 04:30 | 383 | 375
2018-05-18 05:00 | 404 | 396
2018-05-18 05:30 | 425 | 420
2018-05-18 06:00 | 448 | 443
2018-05-18 06:30 | 488 | 485
2018-05-18 07:00 | 549 | 545
2018-05-18 07:30 | 564 | 560
2018-05-18 08:00 | 569 | 564
2018-05-18 08:30 | 552 | 546
2018-05-18 09:00 | 525 | 521
2018-05-18 09:30 | 509 | 505
2018-05-18 10:00 | 496 | 494
2018-05-18 10:30 | 488 | 486
2018-05-18 11:00 | 485 | 484
2018-05-18 11:30 | 480 | 480
2018-05-18 12:00 | 484 | 483
2018-05-18 12:30 | 480 | 479
2018-05-18 13:00 | 481 | 481
2018-05-18 13:30 | 484 | 483
2018-05-18 14:00 | 489 | 489
2018-05-18 14:30 | 495 | 495
2018-05-18 15:00 | 501 | 501
2018-05-18 15:30 | 516 | 516
2018-05-18 16:00 | 528 | 528
2018-05-18 16:30 | 542 | 542
2018-05-18 17:00 | 558 | 557
2018-05-18 17:30 | 573 | 573
2018-05-18 18:00 | 573 | 572
2018-05-18 18:30 | 565 | 563
2018-05-18 19:00 | 565 | 563
2018-05-18 19:30 | 553 | 551
2018-05-18 20:00 | 551 | 549
2018-05-18 20:30 | 565 | 563
2018-05-18 21:00 | 559 | 557
2018-05-18 21:30 | 533 | 529
2018-05-18 22:00 | 519 | 516
2018-05-18 22:30 | 509 | 505
2018-05-18 23:00 | 489 | 486
2018-05-18 23:30 | 476 | 471
2018-05-19 | 453 | 447
2018-05-19 00:30 | 438 | 431
2018-05-19 01:00 | 427 | 419
2018-05-19 01:30 | 410 | 401
2018-05-19 02:00 | 393 | 383
2018-05-19 02:30 | 382 | 371
2018-05-19 03:00 | 375 | 364
2018-05-19 03:30 | 375 | 365
2018-05-19 04:00 | 377 | 367
2018-05-19 04:30 | 377 | 367
2018-05-19 05:00 | 378 | 369
2018-05-19 05:30 | 391 | 382
2018-05-19 06:00 | 407 | 399
2018-05-19 06:30 | 422 | 415
2018-05-19 07:00 | 436 | 430
2018-05-19 07:30 | 467 | 462
2018-05-19 08:00 | 481 | 477
2018-05-19 08:30 | 479 | 475
2018-05-19 09:00 | 474 | 470
2018-05-19 09:30 | 463 | 459
2018-05-19 10:00 | 451 | 446
2018-05-19 10:30 | 433 | 429
2018-05-19 11:00 | 419 | 415
2018-05-19 11:30 | 407 | 403
2018-05-19 12:00 | 398 | 393
2018-05-19 12:30 | 398 | 393
2018-05-19 13:00 | 395 | 390
2018-05-19 13:30 | 390 | 385
2018-05-19 14:00 | 402 | 397
2018-05-19 14:30 | 413 | 408
2018-05-19 15:00 | 414 | 410
2018-05-19 15:30 | 439 | 435
2018-05-19 16:00 | 461 | 457
2018-05-19 16:30 | 480 | 477
2018-05-19 17:00 | 499 | 496
2018-05-19 17:30 | 518 | 516
2018-05-19 18:00 | 530 | 528
2018-05-19 18:30 | 517 | 515
2018-05-19 19:00 | 514 | 513
2018-05-19 19:30 | 508 | 506
2018-05-19 20:00 | 509 | 506
2018-05-19 20:30 | 506 | 504
2018-05-19 21:00 | 496 | 493
2018-05-19 21:30 | 493 | 489
2018-05-19 22:00 | 497 | 493
2018-05-19 22:30 | 477 | 473
2018-05-19 23:00 | 468 | 464
2018-05-19 23:30 | 455 | 450
2018-05-20 | 435 | 428
2018-05-20 00:30 | 404 | 396
2018-05-20 01:00 | 375 | 365
2018-05-20 01:30 | 366 | 355
2018-05-20 02:00 | 359 | 348
2018-05-20 02:30 | 348 | 337
2018-05-20 03:00 | 342 | 330
2018-05-20 03:30 | 340 | 327
2018-05-20 04:00 | 342 | 329
2018-05-20 04:30 | 334 | 321
2018-05-20 05:00 | 327 | 315
2018-05-20 05:30 | 332 | 320
2018-05-20 06:00 | 340 | 329
2018-05-20 06:30 | 355 | 344
2018-05-20 07:00 | 371 | 360
2018-05-20 07:30 | 397 | 388
2018-05-20 08:00 | 415 | 405
2018-05-20 08:30 | 424 | 415
2018-05-20 09:00 | 427 | 419
2018-05-20 09:30 | 420 | 413
2018-05-20 10:00 | 411 | 404
2018-05-20 10:30 | 398 | 391
2018-05-20 11:00 | 378 | 371
2018-05-20 11:30 | 368 | 361
2018-05-20 12:00 | 358 | 352
2018-05-20 12:30 | 358 | 351
2018-05-20 13:00 | 371 | 365
2018-05-20 13:30 | 379 | 372
2018-05-20 14:00 | 387 | 381
2018-05-20 14:30 | 392 | 386
2018-05-20 15:00 | 401 | 395
2018-05-20 15:30 | 417 | 413
2018-05-20 16:00 | 449 | 445
2018-05-20 16:30 | 484 | 480
2018-05-20 17:00 | 512 | 510
2018-05-20 17:30 | 534 | 533
2018-05-20 18:00 | 539 | 537
2018-05-20 18:30 | 538 | 535
2018-05-20 19:00 | 533 | 530
2018-05-20 19:30 | 524 | 521
2018-05-20 20:00 | 523 | 521
2018-05-20 20:30 | 530 | 528
2018-05-20 21:00 | 510 | 507
2018-05-20 21:30 | 494 | 490
2018-05-20 22:00 | 477 | 472
2018-05-20 22:30 | 449 | 444
2018-05-20 23:00 | 428 | 423
2018-05-20 23:30 | 414 | 408
2018-05-21 | 407 | 399
2018-05-21 00:30 | 390 | 380
2018-05-21 01:00 | 374 | 363
2018-05-21 01:30 | 366 | 355
2018-05-21 02:00 | 356 | 344
2018-05-21 02:30 | 346 | 333
2018-05-21 03:00 | 337 | 323
2018-05-21 03:30 | 335 | 318
2018-05-21 04:00 | 332 | 315
2018-05-21 04:30 | 332 | 316
2018-05-21 05:00 | 348 | 335
2018-05-21 05:30 | 383 | 373
2018-05-21 06:00 | 427 | 421
2018-05-21 06:30 | 504 | 495
2018-05-21 07:00 | 561 | 547
2018-05-21 07:30 | 585 | 572
2018-05-21 08:00 | 586 | 573
2018-05-21 08:30 | 571 | 557
2018-05-21 09:00 | 555 | 540
2018-05-21 09:30 | 537 | 520
2018-05-21 10:00 | 506 | 497
2018-05-21 10:30 | 488 | 482
2018-05-21 11:00 | 478 | 473
2018-05-21 11:30 | 469 | 463
2018-05-21 12:00 | 453 | 449
2018-05-21 12:30 | 459 | 457
2018-05-21 13:00 | 468 | 466
2018-05-21 13:30 | 473 | 471
2018-05-21 14:00 | 482 | 480
2018-05-21 14:30 | 495 | 493
2018-05-21 15:00 | 500 | 498
2018-05-21 15:30 | 520 | 516
2018-05-21 16:00 | 540 | 537
2018-05-21 16:30 | 571 | 568
2018-05-21 17:00 | 596 | 593
2018-05-21 17:30 | 634 | 629
2018-05-21 18:00 | 665 | 653
2018-05-21 18:30 | 656 | 643
2018-05-21 19:00 | 647 | 636
2018-05-21 19:30 | 619 | 612
2018-05-21 20:00 | 620 | 615
2018-05-21 20:30 | 617 | 612
2018-05-21 21:00 | 598 | 592
2018-05-21 21:30 | 565 | 563
2018-05-21 22:00 | 556 | 554
2018-05-21 22:30 | 526 | 524
2018-05-21 23:00 | 500 | 498
2018-05-21 23:30 | 475 | 473
2018-05-22 | 457 | 454
2018-05-22 00:30 | 426 | 422
2018-05-22 01:00 | 413 | 408
2018-05-22 01:30 | 392 | 386
2018-05-22 02:00 | 371 | 365
2018-05-22 02:30 | 356 | 351
2018-05-22 03:00 | 354 | 349
2018-05-22 03:30 | 354 | 349
2018-05-22 04:00 | 355 | 351
2018-05-22 04:30 | 362 | 358
2018-05-22 05:00 | 379 | 376
2018-05-22 05:30 | 403 | 400
2018-05-22 06:00 | 434 | 433
2018-05-22 06:30 | 492 | 491
2018-05-22 07:00 | 555 | 553
2018-05-22 07:30 | 593 | 591
2018-05-22 08:00 | 594 | 592
2018-05-22 08:30 | 583 | 580
2018-05-22 09:00 | 553 | 550
2018-05-22 09:30 | 535 | 533
2018-05-22 10:00 | 516 | 513
2018-05-22 10:30 | 502 | 500
2018-05-22 11:00 | 492 | 490
2018-05-22 11:30 | 477 | 475
2018-05-22 12:00 | 471 | 469
2018-05-22 12:30 | 472 | 470
2018-05-22 13:00 | 474 | 472
2018-05-22 13:30 | 481 | 479
2018-05-22 14:00 | 484 | 482
2018-05-22 14:30 | 490 | 489
2018-05-22 15:00 | 509 | 508
2018-05-22 15:30 | 525 | 524
2018-05-22 16:00 | 553 | 553
2018-05-22 16:30 | 589 | 589
2018-05-22 17:00 | 609 | 608
2018-05-22 17:30 | 629 | 629
2018-05-22 18:00 | 652 | 645
2018-05-22 18:30 | 650 | 641
2018-05-22 19:00 | 636 | 630
2018-05-22 19:30 | 623 | 617
2018-05-22 20:00 | 625 | 621
2018-05-22 20:30 | 630 | 627
2018-05-22 21:00 | 601 | 599
2018-05-22 21:30 | 574 | 574
2018-05-22 22:00 | 554 | 553
2018-05-22 22:30 | 536 | 534
2018-05-22 23:00 | 515 | 512
2018-05-22 23:30 | 494 | 490
2018-05-23 | 461 | 455
2018-05-23 00:30 | 443 | 435
2018-05-23 01:00 | 423 | 414
2018-05-23 01:30 | 416 | 408
2018-05-23 02:00 | 408 | 399
2018-05-23 02:30 | 396 | 387
2018-05-23 03:00 | 398 | 388
2018-05-23 03:30 | 392 | 382
2018-05-23 04:00 | 395 | 385
2018-05-23 04:30 | 392 | 382
2018-05-23 05:00 | 394 | 386
2018-05-23 05:30 | 425 | 421
2018-05-23 06:00 | 446 | 445
2018-05-23 06:30 | 498 | 495
2018-05-23 07:00 | 558 | 552
2018-05-23 07:30 | 571 | 566
2018-05-23 08:00 | 577 | 571
2018-05-23 08:30 | 557 | 549
2018-05-23 09:00 | 528 | 518
2018-05-23 09:30 | 504 | 495
2018-05-23 10:00 | 474 | 473
2018-05-23 10:30 | 469 | 467
2018-05-23 11:00 | 467 | 465
2018-05-23 11:30 | 456 | 455
2018-05-23 12:00 | 461 | 460
2018-05-23 12:30 | 471 | 470
2018-05-23 13:00 | 473 | 472
2018-05-23 13:30 | 472 | 470
2018-05-23 14:00 | 477 | 475
2018-05-23 14:30 | 488 | 487
2018-05-23 15:00 | 509 | 507
2018-05-23 15:30 | 538 | 535
2018-05-23 16:00 | 550 | 548
2018-05-23 16:30 | 570 | 567
2018-05-23 17:00 | 596 | 590
2018-05-23 17:30 | 630 | 622
2018-05-23 18:00 | 645 | 634
2018-05-23 18:30 | 636 | 623
2018-05-23 19:00 | 625 | 611
2018-05-23 19:30 | 596 | 591
2018-05-23 20:00 | 588 | 586
2018-05-23 20:30 | 588 | 584
2018-05-23 21:00 | 570 | 568
2018-05-23 21:30 | 560 | 558
2018-05-23 22:00 | 541 | 538
2018-05-23 22:30 | 535 | 532
2018-05-23 23:00 | 513 | 509
2018-05-23 23:30 | 493 | 488
2018-05-24 | 464 | 458
2018-05-24 00:30 | 441 | 434
2018-05-24 01:00 | 424 | 416
2018-05-24 01:30 | 407 | 398
2018-05-24 02:00 | 400 | 390
2018-05-24 02:30 | 387 | 378
2018-05-24 03:00 | 371 | 362
2018-05-24 03:30 | 361 | 352
2018-05-24 04:00 | 355 | 345
2018-05-24 04:30 | 360 | 351
2018-05-24 05:00 | 365 | 358
2018-05-24 05:30 | 393 | 388
2018-05-24 06:00 | 435 | 433
2018-05-24 06:30 | 501 | 498
2018-05-24 07:00 | 572 | 564
2018-05-24 07:30 | 593 | 585
2018-05-24 08:00 | 591 | 584
2018-05-24 08:30 | 575 | 566
2018-05-24 09:00 | 550 | 547
2018-05-24 09:30 | 531 | 529
2018-05-24 10:00 | 508 | 507
2018-05-24 10:30 | 496 | 495
2018-05-24 11:00 | 498 | 498
2018-05-24 11:30 | 498 | 497
2018-05-24 12:00 | 495 | 495
2018-05-24 12:30 | 494 | 493
2018-05-24 13:00 | 519 | 519
2018-05-24 13:30 | 528 | 528
2018-05-24 14:00 | 548 | 547
2018-05-24 14:30 | 557 | 555
2018-05-24 15:00 | 530 | 528
2018-05-24 15:30 | 534 | 532
2018-05-24 16:00 | 549 | 547
2018-05-24 16:30 | 569 | 566
2018-05-24 17:00 | 594 | 592
2018-05-24 17:30 | 626 | 624
2018-05-24 18:00 | 650 | 647
2018-05-24 18:30 | 630 | 626
2018-05-24 19:00 | 614 | 610
2018-05-24 19:30 | 589 | 585
2018-05-24 20:00 | 585 | 584
2018-05-24 20:30 | 587 | 585
2018-05-24 21:00 | 567 | 564
2018-05-24 21:30 | 547 | 543
2018-05-24 22:00 | 538 | 534
2018-05-24 22:30 | 515 | 510
2018-05-24 23:00 | 489 | 485
2018-05-24 23:30 | 477 | 474
2018-05-25 | 456 | 451
2018-05-25 00:30 | 428 | 422
2018-05-25 01:00 | 408 | 400
2018-05-25 01:30 | 385 | 377
2018-05-25 02:00 | 376 | 367
2018-05-25 02:30 | 368 | 359
2018-05-25 03:00 | 360 | 351
2018-05-25 03:30 | 359 | 351
2018-05-25 04:00 | 361 | 352
2018-05-25 04:30 | 361 | 353
2018-05-25 05:00 | 372 | 365
2018-05-25 05:30 | 392 | 388
2018-05-25 06:00 | 420 | 418
2018-05-25 06:30 | 483 | 481
2018-05-25 07:00 | 527 | 523
2018-05-25 07:30 | 567 | 559
2018-05-25 08:00 | 578 | 571
2018-05-25 08:30 | 571 | 564
2018-05-25 09:00 | 567 | 559
2018-05-25 09:30 | 552 | 545
2018-05-25 10:00 | 532 | 524
2018-05-25 10:30 | 531 | 523
2018-05-25 11:00 | 511 | 504
2018-05-25 11:30 | 483 | 481
2018-05-25 12:00 | 474 | 474
2018-05-25 12:30 | 477 | 476
2018-05-25 13:00 | 488 | 487
2018-05-25 13:30 | 492 | 492
2018-05-25 14:00 | 497 | 497
2018-05-25 14:30 | 511 | 510
2018-05-25 15:00 | 518 | 517
2018-05-25 15:30 | 530 | 530
2018-05-25 16:00 | 542 | 541
2018-05-25 16:30 | 552 | 550
2018-05-25 17:00 | 570 | 569
2018-05-25 17:30 | 586 | 581
2018-05-25 18:00 | 603 | 597
2018-05-25 18:30 | 583 | 574
2018-05-25 19:00 | 580 | 570
2018-05-25 19:30 | 560 | 553
2018-05-25 20:00 | 568 | 562
2018-05-25 20:30 | 566 | 559
2018-05-25 21:00 | 537 | 533
2018-05-25 21:30 | 512 | 511
2018-05-25 22:00 | 502 | 501
2018-05-25 22:30 | 492 | 490
2018-05-25 23:00 | 463 | 462
2018-05-25 23:30 | 452 | 449
2018-05-26 | 429 | 426
2018-05-26 00:30 | 411 | 406
2018-05-26 01:00 | 402 | 396
2018-05-26 01:30 | 373 | 365
2018-05-26 02:00 | 354 | 341
2018-05-26 02:30 | 346 | 331
2018-05-26 03:00 | 343 | 327
2018-05-26 03:30 | 339 | 323
2018-05-26 04:00 | 335 | 319
2018-05-26 04:30 | 342 | 326
2018-05-26 05:00 | 346 | 331
2018-05-26 05:30 | 355 | 341
2018-05-26 06:00 | 363 | 351
2018-05-26 06:30 | 380 | 368
2018-05-26 07:00 | 411 | 401
2018-05-26 07:30 | 440 | 432
2018-05-26 08:00 | 467 | 461
2018-05-26 08:30 | 486 | 481
2018-05-26 09:00 | 482 | 478
2018-05-26 09:30 | 482 | 478
2018-05-26 10:00 | 444 | 441
2018-05-26 10:30 | 427 | 424
2018-05-26 11:00 | 416 | 412
2018-05-26 11:30 | 408 | 404
2018-05-26 12:00 | 404 | 401
2018-05-26 12:30 | 409 | 406
2018-05-26 13:00 | 408 | 405
2018-05-26 13:30 | 421 | 418
2018-05-26 14:00 | 433 | 430
2018-05-26 14:30 | 443 | 440
2018-05-26 15:00 | 449 | 446
2018-05-26 15:30 | 448 | 445
2018-05-26 16:00 | 460 | 457
2018-05-26 16:30 | 476 | 474
2018-05-26 17:00 | 505 | 504
2018-05-26 17:30 | 538 | 532
2018-05-26 18:00 | 542 | 533
2018-05-26 18:30 | 538 | 529
2018-05-26 19:00 | 531 | 520
2018-05-26 19:30 | 507 | 504
2018-05-26 20:00 | 504 | 502
2018-05-26 20:30 | 497 | 495
2018-05-26 21:00 | 466 | 465
2018-05-26 21:30 | 458 | 455
2018-05-26 22:00 | 453 | 449
2018-05-26 22:30 | 437 | 434
2018-05-26 23:00 | 429 | 426
2018-05-26 23:30 | 417 | 412
2018-05-27 | 399 | 392
2018-05-27 00:30 | 378 | 370
2018-05-27 01:00 | 365 | 356
2018-05-27 01:30 | 350 | 339
2018-05-27 02:00 | 338 | 327
2018-05-27 02:30 | 329 | 318
2018-05-27 03:00 | 327 | 315
2018-05-27 03:30 | 320 | 306
2018-05-27 04:00 | 322 | 307
2018-05-27 04:30 | 321 | 307
2018-05-27 05:00 | 322 | 308
2018-05-27 05:30 | 333 | 319
2018-05-27 06:00 | 336 | 323
2018-05-27 06:30 | 358 | 346
2018-05-27 07:00 | 367 | 356
2018-05-27 07:30 | 386 | 375
2018-05-27 08:00 | 398 | 389
2018-05-27 08:30 | 409 | 400
2018-05-27 09:00 | 412 | 405
2018-05-27 09:30 | 409 | 402
2018-05-27 10:00 | 404 | 397
2018-05-27 10:30 | 405 | 398
2018-05-27 11:00 | 420 | 414
2018-05-27 11:30 | 418 | 412
2018-05-27 12:00 | 411 | 405
2018-05-27 12:30 | 409 | 403
2018-05-27 13:00 | 401 | 395
2018-05-27 13:30 | 405 | 398
2018-05-27 14:00 | 405 | 399
2018-05-27 14:30 | 423 | 418
2018-05-27 15:00 | 427 | 422
2018-05-27 15:30 | 420 | 414
2018-05-27 16:00 | 433 | 429
2018-05-27 16:30 | 470 | 466
2018-05-27 17:00 | 510 | 508
2018-05-27 17:30 | 541 | 536
2018-05-27 18:00 | 546 | 537
2018-05-27 18:30 | 541 | 532
2018-05-27 19:00 | 540 | 529
2018-05-27 19:30 | 522 | 517
2018-05-27 20:00 | 516 | 515
2018-05-27 20:30 | 515 | 514
2018-05-27 21:00 | 501 | 500
2018-05-27 21:30 | 472 | 469
2018-05-27 22:00 | 444 | 442
2018-05-27 22:30 | 429 | 426
2018-05-27 23:00 | 420 | 417
2018-05-27 23:30 | 413 | 408
2018-05-28 | 393 | 387
2018-05-28 00:30 | 372 | 365
2018-05-28 01:00 | 358 | 349
2018-05-28 01:30 | 346 | 336
2018-05-28 02:00 | 336 | 326
2018-05-28 02:30 | 324 | 312
2018-05-28 03:00 | 319 | 307
2018-05-28 03:30 | 320 | 308
2018-05-28 04:00 | 320 | 309
2018-05-28 04:30 | 338 | 328
2018-05-28 05:00 | 350 | 341
2018-05-28 05:30 | 373 | 367
2018-05-28 06:00 | 398 | 394
2018-05-28 06:30 | 450 | 447
2018-05-28 07:00 | 495 | 492
2018-05-28 07:30 | 542 | 539
2018-05-28 08:00 | 552 | 550
2018-05-28 08:30 | 545 | 542
2018-05-28 09:00 | 524 | 521
2018-05-28 09:30 | 509 | 506
2018-05-28 10:00 | 504 | 501
2018-05-28 10:30 | 502 | 500
2018-05-28 11:00 | 488 | 487
2018-05-28 11:30 | 491 | 489
2018-05-28 12:00 | 498 | 497
2018-05-28 12:30 | 479 | 478
2018-05-28 13:00 | 472 | 470
2018-05-28 13:30 | 471 | 469
2018-05-28 14:00 | 484 | 483
2018-05-28 14:30 | 495 | 494
2018-05-28 15:00 | 503 | 502
2018-05-28 15:30 | 497 | 495
2018-05-28 16:00 | 511 | 509
2018-05-28 16:30 | 530 | 528
2018-05-28 17:00 | 556 | 554
2018-05-28 17:30 | 589 | 585
2018-05-28 18:00 | 595 | 587
2018-05-28 18:30 | 583 | 572
2018-05-28 19:00 | 585 | 574
2018-05-28 19:30 | 558 | 553
2018-05-28 20:00 | 557 | 553
2018-05-28 20:30 | 548 | 545
2018-05-28 21:00 | 512 | 510
2018-05-28 21:30 | 483 | 480
2018-05-28 22:00 | 458 | 455
2018-05-28 22:30 | 456 | 452
2018-05-28 23:00 | 442 | 437
2018-05-28 23:30 | 428 | 423
2018-05-29 | 402 | 398
2018-05-29 00:30 | 379 | 373
2018-05-29 01:00 | 366 | 358
2018-05-29 01:30 | 354 | 345
2018-05-29 02:00 | 344 | 334
2018-05-29 02:30 | 339 | 329
2018-05-29 03:00 | 328 | 318
2018-05-29 03:30 | 324 | 314
2018-05-29 04:00 | 319 | 310
2018-05-29 04:30 | 321 | 312
2018-05-29 05:00 | 328 | 321
2018-05-29 05:30 | 354 | 349
2018-05-29 06:00 | 388 | 385
2018-05-29 06:30 | 436 | 434
2018-05-29 07:00 | 494 | 493
2018-05-29 07:30 | 519 | 519
2018-05-29 08:00 | 524 | 523
2018-05-29 08:30 | 506 | 505
2018-05-29 09:00 | 490 | 490
2018-05-29 09:30 | 473 | 473
2018-05-29 10:00 | 447 | 447
2018-05-29 10:30 | 433 | 433
2018-05-29 11:00 | 436 | 436
2018-05-29 11:30 | 443 | 443
2018-05-29 12:00 | 456 | 455
2018-05-29 12:30 | 467 | 466
2018-05-29 13:00 | 480 | 479
2018-05-29 13:30 | 471 | 471
2018-05-29 14:00 | 465 | 465
2018-05-29 14:30 | 458 | 458
2018-05-29 15:00 | 474 | 474
2018-05-29 15:30 | 470 | 470
2018-05-29 16:00 | 495 | 495
2018-05-29 16:30 | 513 | 513
2018-05-29 17:00 | 521 | 521
2018-05-29 17:30 | 532 | 532
2018-05-29 18:00 | 547 | 547
2018-05-29 18:30 | 541 | 540
2018-05-29 19:00 | 544 | 543
2018-05-29 19:30 | 530 | 529
2018-05-29 20:00 | 527 | 526
2018-05-29 20:30 | 534 | 534
2018-05-29 21:00 | 522 | 522
2018-05-29 21:30 | 513 | 512
2018-05-29 22:00 | 491 | 490
2018-05-29 22:30 | 481 | 480
2018-05-29 23:00 | 457 | 455
2018-05-29 23:30 | 439 | 437
2018-05-30 | 413 | 412
2018-05-30 00:30 | 390 | 388
2018-05-30 01:00 | 372 | 368
2018-05-30 01:30 | 356 | 352
2018-05-30 02:00 | 341 | 336
2018-05-30 02:30 | 339 | 335
2018-05-30 03:00 | 336 | 332
2018-05-30 03:30 | 342 | 337
2018-05-30 04:00 | 348 | 343
2018-05-30 04:30 | 354 | 350
2018-05-30 05:00 | 364 | 360
2018-05-30 05:30 | 385 | 383
2018-05-30 06:00 | 403 | 403
2018-05-30 06:30 | 448 | 448
2018-05-30 07:00 | 498 | 497
2018-05-30 07:30 | 529 | 528
2018-05-30 08:00 | 536 | 534
2018-05-30 08:30 | 523 | 521
2018-05-30 09:00 | 507 | 505
2018-05-30 09:30 | 490 | 489
2018-05-30 10:00 | 472 | 471
2018-05-30 10:30 | 458 | 458
2018-05-30 11:00 | 456 | 455
2018-05-30 11:30 | 448 | 448
2018-05-30 12:00 | 451 | 451
2018-05-30 12:30 | 453 | 452
2018-05-30 13:00 | 461 | 461
2018-05-30 13:30 | 470 | 470
2018-05-30 14:00 | 482 | 482
2018-05-30 14:30 | 500 | 500
2018-05-30 15:00 | 509 | 509
2018-05-30 15:30 | 514 | 514
2018-05-30 16:00 | 522 | 521
2018-05-30 16:30 | 539 | 539
2018-05-30 17:00 | 564 | 564
2018-05-30 17:30 | 573 | 573
2018-05-30 18:00 | 567 | 566
2018-05-30 18:30 | 549 | 547
2018-05-30 19:00 | 542 | 540
2018-05-30 19:30 | 517 | 516
2018-05-30 20:00 | 515 | 515
2018-05-30 20:30 | 520 | 520
2018-05-30 21:00 | 509 | 508
2018-05-30 21:30 | 496 | 494
2018-05-30 22:00 | 482 | 479
2018-05-30 22:30 | 453 | 452
2018-05-30 23:00 | 428 | 427
2018-05-30 23:30 | 417 | 415
2018-05-31 | 397 | 393
2018-05-31 00:30 | 372 | 367
2018-05-31 01:00 | 362 | 356
2018-05-31 01:30 | 349 | 343
2018-05-31 02:00 | 342 | 336
2018-05-31 02:30 | 336 | 330
2018-05-31 03:00 | 334 | 328
2018-05-31 03:30 | 338 | 332
2018-05-31 04:00 | 341 | 335
2018-05-31 04:30 | 349 | 344
2018-05-31 05:00 | 360 | 356
2018-05-31 05:30 | 379 | 377
2018-05-31 06:00 | 405 | 404
2018-05-31 06:30 | 468 | 467
2018-05-31 07:00 | 527 | 527
2018-05-31 07:30 | 556 | 556
2018-05-31 08:00 | 545 | 545
2018-05-31 08:30 | 525 | 525
2018-05-31 09:00 | 504 | 504
2018-05-31 09:30 | 477 | 477
2018-05-31 10:00 | 452 | 452
2018-05-31 10:30 | 439 | 439
2018-05-31 11:00 | 431 | 431
2018-05-31 11:30 | 422 | 422
2018-05-31 12:00 | 417 | 417
2018-05-31 12:30 | 412 | 412
2018-05-31 13:00 | 418 | 418
2018-05-31 13:30 | 424 | 424
2018-05-31 14:00 | 434 | 434
2018-05-31 14:30 | 448 | 448
2018-05-31 15:00 | 461 | 461
2018-05-31 15:30 | 470 | 470
2018-05-31 16:00 | 489 | 489
2018-05-31 16:30 | 510 | 510
2018-05-31 17:00 | 543 | 543
2018-05-31 17:30 | 577 | 574
2018-05-31 18:00 | 592 | 590
2018-05-31 18:30 | 585 | 582
2018-05-31 19:00 | 589 | 586
2018-05-31 19:30 | 590 | 586
2018-05-31 20:00 | 590 | 590
2018-05-31 20:30 | 589 | 589
2018-05-31 21:00 | 565 | 565
2018-05-31 21:30 | 530 | 529
2018-05-31 22:00 | 499 | 498
2018-05-31 22:30 | 493 | 492
2018-05-31 23:00 | 472 | 471
2018-05-31 23:30 | 450 | 448
2018-06-01 | 432 | 429
2018-06-01 00:30 | 414 | 409
2018-06-01 01:00 | 397 | 393
2018-06-01 01:30 | 376 | 371
2018-06-01 02:00 | 359 | 355
2018-06-01 02:30 | 351 | 346
2018-06-01 03:00 | 349 | 344
2018-06-01 03:30 | 351 | 346
2018-06-01 04:00 | 350 | 345
2018-06-01 04:30 | 365 | 361
2018-06-01 05:00 | 376 | 373
2018-06-01 05:30 | 407 | 405
2018-06-01 06:00 | 435 | 434
2018-06-01 06:30 | 486 | 485
2018-06-01 07:00 | 536 | 536
2018-06-01 07:30 | 560 | 560
2018-06-01 08:00 | 553 | 552
2018-06-01 08:30 | 534 | 534
2018-06-01 09:00 | 505 | 505
2018-06-01 09:30 | 485 | 485
2018-06-01 10:00 | 462 | 461
2018-06-01 10:30 | 442 | 442
2018-06-01 11:00 | 429 | 429
2018-06-01 11:30 | 425 | 425
2018-06-01 12:00 | 418 | 418
2018-06-01 12:30 | 405 | 405
2018-06-01 13:00 | 404 | 403
2018-06-01 13:30 | 405 | 405
2018-06-01 14:00 | 413 | 412
2018-06-01 14:30 | 428 | 427
2018-06-01 15:00 | 433 | 432
2018-06-01 15:30 | 446 | 445
2018-06-01 16:00 | 470 | 470
2018-06-01 16:30 | 490 | 490
2018-06-01 17:00 | 507 | 507
2018-06-01 17:30 | 540 | 540
2018-06-01 18:00 | 555 | 553
2018-06-01 18:30 | 545 | 543
2018-06-01 19:00 | 542 | 541
2018-06-01 19:30 | 543 | 541
2018-06-01 20:00 | 554 | 552
2018-06-01 20:30 | 563 | 560
2018-06-01 21:00 | 546 | 544
2018-06-01 21:30 | 533 | 532
2018-06-01 22:00 | 516 | 516
2018-06-01 22:30 | 508 | 508
2018-06-01 23:00 | 485 | 485
2018-06-01 23:30 | 471 | 470
2018-06-02 | 446 | 445
2018-06-02 00:30 | 423 | 421
2018-06-02 01:00 | 397 | 394
2018-06-02 01:30 | 387 | 382
2018-06-02 02:00 | 372 | 367
2018-06-02 02:30 | 362 | 356
2018-06-02 03:00 | 363 | 357
2018-06-02 03:30 | 361 | 355
2018-06-02 04:00 | 362 | 356
2018-06-02 04:30 | 367 | 361
2018-06-02 05:00 | 373 | 368
2018-06-02 05:30 | 389 | 384
2018-06-02 06:00 | 398 | 393
2018-06-02 06:30 | 414 | 411
2018-06-02 07:00 | 442 | 440
2018-06-02 07:30 | 478 | 476
2018-06-02 08:00 | 502 | 499
2018-06-02 08:30 | 507 | 503
2018-06-02 09:00 | 499 | 495
2018-06-02 09:30 | 487 | 482
2018-06-02 10:00 | 465 | 462
2018-06-02 10:30 | 442 | 439
2018-06-02 11:00 | 419 | 417
2018-06-02 11:30 | 401 | 399
2018-06-02 12:00 | 391 | 389
2018-06-02 12:30 | 386 | 383
2018-06-02 13:00 | 372 | 369
2018-06-02 13:30 | 379 | 376
2018-06-02 14:00 | 397 | 394
2018-06-02 14:30 | 400 | 398
2018-06-02 15:00 | 407 | 405
2018-06-02 15:30 | 424 | 423
2018-06-02 16:00 | 451 | 450
2018-06-02 16:30 | 476 | 475
2018-06-02 17:00 | 512 | 511
2018-06-02 17:30 | 537 | 532
2018-06-02 18:00 | 545 | 541
2018-06-02 18:30 | 540 | 535
2018-06-02 19:00 | 534 | 529
2018-06-02 19:30 | 529 | 524
2018-06-02 20:00 | 533 | 528
2018-06-02 20:30 | 546 | 541
2018-06-02 21:00 | 522 | 516
2018-06-02 21:30 | 494 | 493
2018-06-02 22:00 | 483 | 482
2018-06-02 22:30 | 463 | 463
2018-06-02 23:00 | 453 | 452
2018-06-02 23:30 | 436 | 434
2018-06-03 | 410 | 408
2018-06-03 00:30 | 399 | 397
2018-06-03 01:00 | 387 | 384
2018-06-03 01:30 | 376 | 371
2018-06-03 02:00 | 365 | 360
2018-06-03 02:30 | 360 | 354
2018-06-03 03:00 | 351 | 345
2018-06-03 03:30 | 347 | 341
2018-06-03 04:00 | 345 | 339
2018-06-03 04:30 | 339 | 333
2018-06-03 05:00 | 338 | 332
2018-06-03 05:30 | 349 | 344
2018-06-03 06:00 | 358 | 353
2018-06-03 06:30 | 374 | 369
2018-06-03 07:00 | 386 | 381
2018-06-03 07:30 | 407 | 403
2018-06-03 08:00 | 417 | 414
2018-06-03 08:30 | 428 | 425
2018-06-03 09:00 | 433 | 431
2018-06-03 09:30 | 433 | 430
2018-06-03 10:00 | 415 | 413
2018-06-03 10:30 | 400 | 398
2018-06-03 11:00 | 393 | 390
2018-06-03 11:30 | 384 | 381
2018-06-03 12:00 | 376 | 373
2018-06-03 12:30 | 371 | 368
2018-06-03 13:00 | 372 | 369
2018-06-03 13:30 | 382 | 379
2018-06-03 14:00 | 400 | 397
2018-06-03 14:30 | 401 | 399
2018-06-03 15:00 | 405 | 403
2018-06-03 15:30 | 432 | 430
2018-06-03 16:00 | 460 | 459
2018-06-03 16:30 | 490 | 487
2018-06-03 17:00 | 519 | 513
2018-06-03 17:30 | 537 | 534
2018-06-03 18:00 | 552 | 549
2018-06-03 18:30 | 543 | 540
2018-06-03 19:00 | 528 | 525
2018-06-03 19:30 | 522 | 518
2018-06-03 20:00 | 521 | 517
2018-06-03 20:30 | 537 | 532
2018-06-03 21:00 | 500 | 499
2018-06-03 21:30 | 488 | 487
2018-06-03 22:00 | 478 | 477
2018-06-03 22:30 | 451 | 450
2018-06-03 23:00 | 441 | 439
2018-06-03 23:30 | 431 | 429
2018-06-04 | 409 | 406
2018-06-04 00:30 | 388 | 384
2018-06-04 01:00 | 377 | 372
2018-06-04 01:30 | 371 | 366
2018-06-04 02:00 | 373 | 366
2018-06-04 02:30 | 362 | 356
2018-06-04 03:00 | 360 | 353
2018-06-04 03:30 | 358 | 351
2018-06-04 04:00 | 352 | 346
2018-06-04 04:30 | 359 | 353
2018-06-04 05:00 | 369 | 365
2018-06-04 05:30 | 402 | 399
2018-06-04 06:00 | 438 | 436
2018-06-04 06:30 | 503 | 501
2018-06-04 07:00 | 553 | 552
2018-06-04 07:30 | 577 | 576
2018-06-04 08:00 | 576 | 575
2018-06-04 08:30 | 559 | 558
2018-06-04 09:00 | 526 | 525
2018-06-04 09:30 | 518 | 516
2018-06-04 10:00 | 498 | 496
2018-06-04 10:30 | 486 | 486
2018-06-04 11:00 | 480 | 479
2018-06-04 11:30 | 466 | 466
2018-06-04 12:00 | 462 | 462
2018-06-04 12:30 | 462 | 461
2018-06-04 13:00 | 468 | 468
2018-06-04 13:30 | 468 | 468
2018-06-04 14:00 | 477 | 477
2018-06-04 14:30 | 489 | 489
2018-06-04 15:00 | 495 | 495
2018-06-04 15:30 | 508 | 507
2018-06-04 16:00 | 532 | 532
2018-06-04 16:30 | 559 | 558
2018-06-04 17:00 | 594 | 594
2018-06-04 17:30 | 623 | 621
2018-06-04 18:00 | 642 | 637
2018-06-04 18:30 | 628 | 622
2018-06-04 19:00 | 626 | 619
2018-06-04 19:30 | 616 | 608
2018-06-04 20:00 | 615 | 608
2018-06-04 20:30 | 612 | 605
2018-06-04 21:00 | 572 | 568
2018-06-04 21:30 | 540 | 536
2018-06-04 22:00 | 519 | 514
2018-06-04 22:30 | 501 | 501
2018-06-04 23:00 | 474 | 474
2018-06-04 23:30 | 461 | 459
2018-06-05 | 442 | 440
2018-06-05 00:30 | 420 | 417
2018-06-05 01:00 | 403 | 399
2018-06-05 01:30 | 387 | 382
2018-06-05 02:00 | 381 | 376
2018-06-05 02:30 | 382 | 377
2018-06-05 03:00 | 367 | 362
2018-06-05 03:30 | 365 | 359
2018-06-05 04:00 | 359 | 353
2018-06-05 04:30 | 361 | 356
2018-06-05 05:00 | 365 | 360
2018-06-05 05:30 | 400 | 397
2018-06-05 06:00 | 445 | 444
2018-06-05 06:30 | 508 | 507
2018-06-05 07:00 | 555 | 554
2018-06-05 07:30 | 586 | 584
2018-06-05 08:00 | 586 | 583
2018-06-05 08:30 | 570 | 567
2018-06-05 09:00 | 537 | 535
2018-06-05 09:30 | 523 | 520
2018-06-05 10:00 | 507 | 505
2018-06-05 10:30 | 496 | 495
2018-06-05 11:00 | 486 | 485
2018-06-05 11:30 | 473 | 472
2018-06-05 12:00 | 464 | 463
2018-06-05 12:30 | 458 | 457
2018-06-05 13:00 | 469 | 469
2018-06-05 13:30 | 482 | 481
2018-06-05 14:00 | 487 | 487
2018-06-05 14:30 | 493 | 492
2018-06-05 15:00 | 492 | 491
2018-06-05 15:30 | 509 | 509
2018-06-05 16:00 | 539 | 538
2018-06-05 16:30 | 570 | 569
2018-06-05 17:00 | 588 | 588
2018-06-05 17:30 | 618 | 617
2018-06-05 18:00 | 594 | 591
2018-06-05 18:30 | 602 | 598
2018-06-05 19:00 | 604 | 599
2018-06-05 19:30 | 588 | 583
2018-06-05 20:00 | 615 | 611
2018-06-05 20:30 | 601 | 597
2018-06-05 21:00 | 566 | 565
2018-06-05 21:30 | 539 | 538
2018-06-05 22:00 | 514 | 513
2018-06-05 22:30 | 503 | 502
2018-06-05 23:00 | 477 | 476
2018-06-05 23:30 | 462 | 460
2018-06-06 | 438 | 435
2018-06-06 00:30 | 413 | 410
2018-06-06 01:00 | 392 | 390
2018-06-06 01:30 | 375 | 372
2018-06-06 02:00 | 358 | 355
2018-06-06 02:30 | 354 | 350
2018-06-06 03:00 | 350 | 346
2018-06-06 03:30 | 346 | 342
2018-06-06 04:00 | 340 | 337
2018-06-06 04:30 | 343 | 341
2018-06-06 05:00 | 353 | 351
2018-06-06 05:30 | 385 | 383
2018-06-06 06:00 | 424 | 424
2018-06-06 06:30 | 492 | 491
2018-06-06 07:00 | 561 | 560
2018-06-06 07:30 | 590 | 588
2018-06-06 08:00 | 603 | 598
2018-06-06 08:30 | 583 | 578
2018-06-06 09:00 | 557 | 556
2018-06-06 09:30 | 541 | 540
2018-06-06 10:00 | 522 | 522
2018-06-06 10:30 | 513 | 513
2018-06-06 11:00 | 505 | 504
2018-06-06 11:30 | 500 | 500
2018-06-06 12:00 | 485 | 485
2018-06-06 12:30 | 492 | 492
2018-06-06 13:00 | 493 | 492
2018-06-06 13:30 | 500 | 500
2018-06-06 14:00 | 508 | 508
2018-06-06 14:30 | 505 | 505
2018-06-06 15:00 | 513 | 513
2018-06-06 15:30 | 534 | 533
2018-06-06 16:00 | 551 | 551
2018-06-06 16:30 | 569 | 569
2018-06-06 17:00 | 603 | 602
2018-06-06 17:30 | 627 | 624
2018-06-06 18:00 | 632 | 627
2018-06-06 18:30 | 627 | 621
2018-06-06 19:00 | 621 | 616
2018-06-06 19:30 | 614 | 610
2018-06-06 20:00 | 608 | 607
2018-06-06 20:30 | 602 | 601
2018-06-06 21:00 | 581 | 581
2018-06-06 21:30 | 556 | 555
2018-06-06 22:00 | 535 | 535
2018-06-06 22:30 | 511 | 510
2018-06-06 23:00 | 489 | 488
2018-06-06 23:30 | 472 | 471
2018-06-07 | 449 | 446
2018-06-07 00:30 | 419 | 415
2018-06-07 01:00 | 377 | 374
2018-06-07 01:30 | 348 | 345
2018-06-07 02:00 | 334 | 331
2018-06-07 02:30 | 324 | 321
2018-06-07 03:00 | 320 | 317
2018-06-07 03:30 | 321 | 317
2018-06-07 04:00 | 320 | 316
2018-06-07 04:30 | 320 | 317
2018-06-07 05:00 | 331 | 329
2018-06-07 05:30 | 350 | 348
2018-06-07 06:00 | 392 | 392
2018-06-07 06:30 | 469 | 468
2018-06-07 07:00 | 533 | 533
2018-06-07 07:30 | 579 | 578
2018-06-07 08:00 | 600 | 599
2018-06-07 08:30 | 607 | 606
2018-06-07 09:00 | 602 | 601
2018-06-07 09:30 | 593 | 592
2018-06-07 10:00 | 584 | 583
2018-06-07 10:30 | 567 | 566
2018-06-07 11:00 | 547 | 546
2018-06-07 11:30 | 518 | 518
2018-06-07 12:00 | 513 | 512
2018-06-07 12:30 | 519 | 518
2018-06-07 13:00 | 524 | 523
2018-06-07 13:30 | 530 | 529
2018-06-07 14:00 | 535 | 535
2018-06-07 14:30 | 522 | 522
2018-06-07 15:00 | 520 | 519
2018-06-07 15:30 | 529 | 529
2018-06-07 16:00 | 543 | 542
2018-06-07 16:30 | 556 | 555
2018-06-07 17:00 | 594 | 593
2018-06-07 17:30 | 614 | 613
2018-06-07 18:00 | 628 | 627
2018-06-07 18:30 | 620 | 617
2018-06-07 19:00 | 618 | 616
2018-06-07 19:30 | 606 | 604
2018-06-07 20:00 | 618 | 617
2018-06-07 20:30 | 612 | 610
2018-06-07 21:00 | 596 | 594
2018-06-07 21:30 | 576 | 573
2018-06-07 22:00 | 567 | 562
2018-06-07 22:30 | 535 | 531
2018-06-07 23:00 | 507 | 503
2018-06-07 23:30 | 490 | 488
2018-06-08 | 467 | 466
2018-06-08 00:30 | 444 | 443
2018-06-08 01:00 | 416 | 414
2018-06-08 01:30 | 388 | 385
2018-06-08 02:00 | 379 | 377
2018-06-08 02:30 | 366 | 364
2018-06-08 03:00 | 376 | 374
2018-06-08 03:30 | 369 | 367
2018-06-08 04:00 | 361 | 359
2018-06-08 04:30 | 364 | 362
2018-06-08 05:00 | 367 | 366
2018-06-08 05:30 | 397 | 396
2018-06-08 06:00 | 431 | 430
2018-06-08 06:30 | 487 | 487
2018-06-08 07:00 | 539 | 538
2018-06-08 07:30 | 576 | 575
2018-06-08 08:00 | 582 | 579
2018-06-08 08:30 | 577 | 575
2018-06-08 09:00 | 563 | 561
2018-06-08 09:30 | 530 | 529
2018-06-08 10:00 | 525 | 525
2018-06-08 10:30 | 513 | 513
2018-06-08 11:00 | 502 | 501
2018-06-08 11:30 | 505 | 505
2018-06-08 12:00 | 509 | 508
2018-06-08 12:30 | 497 | 497
2018-06-08 13:00 | 500 | 499
2018-06-08 13:30 | 495 | 495
2018-06-08 14:00 | 507 | 507
2018-06-08 14:30 | 545 | 545
2018-06-08 15:00 | 549 | 547
2018-06-08 15:30 | 567 | 565
2018-06-08 16:00 | 594 | 592
2018-06-08 16:30 | 609 | 608
2018-06-08 17:00 | 623 | 622
2018-06-08 17:30 | 621 | 621
2018-06-08 18:00 | 632 | 631
2018-06-08 18:30 | 620 | 619
2018-06-08 19:00 | 627 | 626
2018-06-08 19:30 | 617 | 616
2018-06-08 20:00 | 612 | 611
2018-06-08 20:30 | 608 | 607
2018-06-08 21:00 | 581 | 580
2018-06-08 21:30 | 568 | 567
2018-06-08 22:00 | 558 | 557
2018-06-08 22:30 | 526 | 524
2018-06-08 23:00 | 501 | 500
2018-06-08 23:30 | 485 | 484
2018-06-09 | 466 | 464
2018-06-09 00:30 | 444 | 442
2018-06-09 01:00 | 431 | 428
2018-06-09 01:30 | 400 | 396
2018-06-09 02:00 | 380 | 376
2018-06-09 02:30 | 376 | 371
2018-06-09 03:00 | 374 | 369
2018-06-09 03:30 | 375 | 370
2018-06-09 04:00 | 373 | 368
2018-06-09 04:30 | 374 | 369
2018-06-09 05:00 | 381 | 376
2018-06-09 05:30 | 386 | 382
2018-06-09 06:00 | 389 | 385
2018-06-09 06:30 | 407 | 404
2018-06-09 07:00 | 419 | 417
2018-06-09 07:30 | 452 | 450
2018-06-09 08:00 | 472 | 471
2018-06-09 08:30 | 487 | 486
2018-06-09 09:00 | 509 | 507
2018-06-09 09:30 | 519 | 516
2018-06-09 10:00 | 511 | 508
2018-06-09 10:30 | 505 | 504
2018-06-09 11:00 | 495 | 494
2018-06-09 11:30 | 491 | 490
2018-06-09 12:00 | 477 | 476
2018-06-09 12:30 | 468 | 467
2018-06-09 13:00 | 451 | 450
2018-06-09 13:30 | 441 | 440
2018-06-09 14:00 | 445 | 444
2018-06-09 14:30 | 452 | 451
2018-06-09 15:00 | 457 | 456
2018-06-09 15:30 | 462 | 460
2018-06-09 16:00 | 473 | 472
2018-06-09 16:30 | 489 | 488
2018-06-09 17:00 | 516 | 516
2018-06-09 17:30 | 549 | 548
2018-06-09 18:00 | 555 | 553
2018-06-09 18:30 | 550 | 548
2018-06-09 19:00 | 549 | 548
2018-06-09 19:30 | 546 | 545
2018-06-09 20:00 | 543 | 542
2018-06-09 20:30 | 544 | 543
2018-06-09 21:00 | 522 | 521
2018-06-09 21:30 | 508 | 507
2018-06-09 22:00 | 502 | 501
2018-06-09 22:30 | 483 | 482
2018-06-09 23:00 | 468 | 467
2018-06-09 23:30 | 458 | 456
2018-06-10 | 432 | 429
2018-06-10 00:30 | 412 | 408
2018-06-10 01:00 | 397 | 392
2018-06-10 01:30 | 369 | 364
2018-06-10 02:00 | 355 | 350
2018-06-10 02:30 | 349 | 343
2018-06-10 03:00 | 343 | 336
2018-06-10 03:30 | 348 | 340
2018-06-10 04:00 | 341 | 334
2018-06-10 04:30 | 345 | 338
2018-06-10 05:00 | 352 | 345
2018-06-10 05:30 | 347 | 341
2018-06-10 06:00 | 346 | 340
2018-06-10 06:30 | 370 | 364
2018-06-10 07:00 | 385 | 380
2018-06-10 07:30 | 410 | 405
2018-06-10 08:00 | 431 | 427
2018-06-10 08:30 | 451 | 447
2018-06-10 09:00 | 450 | 447
2018-06-10 09:30 | 452 | 450
2018-06-10 10:00 | 443 | 441
2018-06-10 10:30 | 432 | 431
2018-06-10 11:00 | 420 | 418
2018-06-10 11:30 | 423 | 421
2018-06-10 12:00 | 413 | 411
2018-06-10 12:30 | 398 | 397
2018-06-10 13:00 | 396 | 395
2018-06-10 13:30 | 394 | 393
2018-06-10 14:00 | 403 | 402
2018-06-10 14:30 | 426 | 425
2018-06-10 15:00 | 437 | 436
2018-06-10 15:30 | 439 | 438
2018-06-10 16:00 | 445 | 444
2018-06-10 16:30 | 472 | 471
2018-06-10 17:00 | 501 | 499
2018-06-10 17:30 | 532 | 529
2018-06-10 18:00 | 543 | 540
2018-06-10 18:30 | 536 | 532
2018-06-10 19:00 | 526 | 522
2018-06-10 19:30 | 511 | 507
2018-06-10 20:00 | 506 | 502
2018-06-10 20:30 | 507 | 505
2018-06-10 21:00 | 484 | 483
2018-06-10 21:30 | 474 | 474
2018-06-10 22:00 | 474 | 473
2018-06-10 22:30 | 452 | 451
2018-06-10 23:00 | 436 | 435
2018-06-10 23:30 | 421 | 419
2018-06-11 | 404 | 401
2018-06-11 00:30 | 389 | 384
2018-06-11 01:00 | 382 | 377
2018-06-11 01:30 | 372 | 366
2018-06-11 02:00 | 366 | 359
2018-06-11 02:30 | 359 | 353
2018-06-11 03:00 | 351 | 343
2018-06-11 03:30 | 348 | 341
2018-06-11 04:00 | 345 | 337
2018-06-11 04:30 | 349 | 342
2018-06-11 05:00 | 363 | 357
2018-06-11 05:30 | 385 | 381
2018-06-11 06:00 | 418 | 415
2018-06-11 06:30 | 456 | 455
2018-06-11 07:00 | 492 | 490
2018-06-11 07:30 | 525 | 523
2018-06-11 08:00 | 532 | 530
2018-06-11 08:30 | 524 | 522
2018-06-11 09:00 | 507 | 505
2018-06-11 09:30 | 486 | 484
2018-06-11 10:00 | 463 | 461
2018-06-11 10:30 | 450 | 448
2018-06-11 11:00 | 442 | 440
2018-06-11 11:30 | 425 | 424
2018-06-11 12:00 | 416 | 414
2018-06-11 12:30 | 413 | 411
2018-06-11 13:00 | 425 | 424
2018-06-11 13:30 | 434 | 433
2018-06-11 14:00 | 442 | 441
2018-06-11 14:30 | 447 | 446
2018-06-11 15:00 | 454 | 453
2018-06-11 15:30 | 462 | 462
2018-06-11 16:00 | 480 | 480
2018-06-11 16:30 | 520 | 519
2018-06-11 17:00 | 554 | 553
2018-06-11 17:30 | 593 | 591
2018-06-11 18:00 | 614 | 608
2018-06-11 18:30 | 605 | 596
2018-06-11 19:00 | 605 | 596
2018-06-11 19:30 | 595 | 585
2018-06-11 20:00 | 578 | 574
2018-06-11 20:30 | 565 | 562
2018-06-11 21:00 | 546 | 544
2018-06-11 21:30 | 526 | 522
2018-06-11 22:00 | 490 | 487
2018-06-11 22:30 | 467 | 466
2018-06-11 23:00 | 454 | 453
2018-06-11 23:30 | 439 | 437
2018-06-12 | 422 | 419
2018-06-12 00:30 | 391 | 386
2018-06-12 01:00 | 380 | 373
2018-06-12 01:30 | 372 | 365
2018-06-12 02:00 | 363 | 356
2018-06-12 02:30 | 359 | 351
2018-06-12 03:00 | 353 | 345
2018-06-12 03:30 | 358 | 351
2018-06-12 04:00 | 362 | 354
2018-06-12 04:30 | 374 | 367
2018-06-12 05:00 | 366 | 360
2018-06-12 05:30 | 395 | 391
2018-06-12 06:00 | 426 | 424
2018-06-12 06:30 | 497 | 492
2018-06-12 07:00 | 553 | 548
2018-06-12 07:30 | 586 | 581
2018-06-12 08:00 | 591 | 585
2018-06-12 08:30 | 579 | 571
2018-06-12 09:00 | 559 | 551
2018-06-12 09:30 | 553 | 548
2018-06-12 10:00 | 538 | 534
2018-06-12 10:30 | 495 | 494
2018-06-12 11:00 | 472 | 471
2018-06-12 11:30 | 464 | 464
2018-06-12 12:00 | 465 | 465
2018-06-12 12:30 | 461 | 461
2018-06-12 13:00 | 469 | 469
2018-06-12 13:30 | 483 | 483
2018-06-12 14:00 | 488 | 488
2018-06-12 14:30 | 502 | 502
2018-06-12 15:00 | 497 | 497
2018-06-12 15:30 | 498 | 498
2018-06-12 16:00 | 501 | 500
2018-06-12 16:30 | 522 | 522
2018-06-12 17:00 | 566 | 563
2018-06-12 17:30 | 605 | 602
2018-06-12 18:00 | 630 | 623
2018-06-12 18:30 | 630 | 621
2018-06-12 19:00 | 617 | 607
2018-06-12 19:30 | 598 | 591
2018-06-12 20:00 | 599 | 594
2018-06-12 20:30 | 601 | 596
2018-06-12 21:00 | 575 | 571
2018-06-12 21:30 | 554 | 548
2018-06-12 22:00 | 523 | 520
2018-06-12 22:30 | 494 | 492
2018-06-12 23:00 | 472 | 470
2018-06-12 23:30 | 451 | 449
2018-06-13 | 430 | 427
2018-06-13 00:30 | 412 | 408
2018-06-13 01:00 | 403 | 398
2018-06-13 01:30 | 383 | 376
2018-06-13 02:00 | 374 | 365
2018-06-13 02:30 | 365 | 355
2018-06-13 03:00 | 358 | 347
2018-06-13 03:30 | 356 | 346
2018-06-13 04:00 | 363 | 353
2018-06-13 04:30 | 370 | 360
2018-06-13 05:00 | 375 | 368
2018-06-13 05:30 | 395 | 390
2018-06-13 06:00 | 428 | 424
2018-06-13 06:30 | 493 | 489
2018-06-13 07:00 | 552 | 545
2018-06-13 07:30 | 590 | 583
2018-06-13 08:00 | 589 | 581
2018-06-13 08:30 | 565 | 557
2018-06-13 09:00 | 542 | 532
2018-06-13 09:30 | 499 | 495
2018-06-13 10:00 | 476 | 474
2018-06-13 10:30 | 475 | 474
2018-06-13 11:00 | 467 | 466
2018-06-13 11:30 | 472 | 472
2018-06-13 12:00 | 466 | 466
2018-06-13 12:30 | 473 | 473
2018-06-13 13:00 | 476 | 476
2018-06-13 13:30 | 464 | 463
2018-06-13 14:00 | 481 | 481
2018-06-13 14:30 | 489 | 489
2018-06-13 15:00 | 476 | 476
2018-06-13 15:30 | 486 | 486
2018-06-13 16:00 | 521 | 521
2018-06-13 16:30 | 543 | 542
2018-06-13 17:00 | 573 | 572
2018-06-13 17:30 | 607 | 602
2018-06-13 18:00 | 632 | 626
2018-06-13 18:30 | 613 | 607
2018-06-13 19:00 | 613 | 608
2018-06-13 19:30 | 604 | 598
2018-06-13 20:00 | 601 | 593
2018-06-13 20:30 | 602 | 595
2018-06-13 21:00 | 570 | 568
2018-06-13 21:30 | 546 | 545
2018-06-13 22:00 | 524 | 522
2018-06-13 22:30 | 499 | 496
2018-06-13 23:00 | 471 | 468
2018-06-13 23:30 | 448 | 443
2018-06-14 | 428 | 420
2018-06-14 00:30 | 404 | 396
2018-06-14 01:00 | 387 | 379
2018-06-14 01:30 | 373 | 364
2018-06-14 02:00 | 359 | 348
2018-06-14 02:30 | 354 | 343
2018-06-14 03:00 | 349 | 338
2018-06-14 03:30 | 344 | 333
2018-06-14 04:00 | 342 | 332
2018-06-14 04:30 | 347 | 337
2018-06-14 05:00 | 358 | 349
2018-06-14 05:30 | 380 | 374
2018-06-14 06:00 | 409 | 405
2018-06-14 06:30 | 467 | 464
2018-06-14 07:00 | 521 | 518
2018-06-14 07:30 | 544 | 542
2018-06-14 08:00 | 536 | 534
2018-06-14 08:30 | 518 | 516
2018-06-14 09:00 | 499 | 497
2018-06-14 09:30 | 486 | 485
2018-06-14 10:00 | 475 | 475
2018-06-14 10:30 | 478 | 477
2018-06-14 11:00 | 468 | 467
2018-06-14 11:30 | 444 | 443
2018-06-14 12:00 | 440 | 439
2018-06-14 12:30 | 446 | 445
2018-06-14 13:00 | 431 | 430
2018-06-14 13:30 | 438 | 437
2018-06-14 14:00 | 462 | 461
2018-06-14 14:30 | 473 | 473
2018-06-14 15:00 | 477 | 477
2018-06-14 15:30 | 487 | 486
2018-06-14 16:00 | 511 | 510
2018-06-14 16:30 | 533 | 531
2018-06-14 17:00 | 557 | 555
2018-06-14 17:30 | 587 | 580
2018-06-14 18:00 | 607 | 596
2018-06-14 18:30 | 592 | 578
2018-06-14 19:00 | 594 | 581
2018-06-14 19:30 | 576 | 573
2018-06-14 20:00 | 576 | 572
2018-06-14 20:30 | 574 | 569
2018-06-14 21:00 | 555 | 550
2018-06-14 21:30 | 525 | 524
2018-06-14 22:00 | 512 | 510
2018-06-14 22:30 | 490 | 487
2018-06-14 23:00 | 466 | 462
2018-06-14 23:30 | 451 | 445
2018-06-15 | 429 | 421
2018-06-15 00:30 | 404 | 394
2018-06-15 01:00 | 385 | 372
2018-06-15 01:30 | 359 | 343
2018-06-15 02:00 | 353 | 336
2018-06-15 02:30 | 347 | 330
2018-06-15 03:00 | 341 | 323
2018-06-15 03:30 | 336 | 318
2018-06-15 04:00 | 330 | 312
2018-06-15 04:30 | 333 | 316
2018-06-15 05:00 | 339 | 325
2018-06-15 05:30 | 368 | 357
2018-06-15 06:00 | 408 | 401
2018-06-15 06:30 | 469 | 463
2018-06-15 07:00 | 534 | 526
2018-06-15 07:30 | 575 | 569
2018-06-15 08:00 | 578 | 570
2018-06-15 08:30 | 550 | 542
2018-06-15 09:00 | 515 | 509
2018-06-15 09:30 | 486 | 484
2018-06-15 10:00 | 458 | 457
2018-06-15 10:30 | 443 | 442
2018-06-15 11:00 | 429 | 428
2018-06-15 11:30 | 413 | 412
2018-06-15 12:00 | 406 | 405
2018-06-15 12:30 | 404 | 403
2018-06-15 13:00 | 405 | 404
2018-06-15 13:30 | 407 | 406
2018-06-15 14:00 | 411 | 410
2018-06-15 14:30 | 428 | 427
2018-06-15 15:00 | 440 | 439
2018-06-15 15:30 | 453 | 452
2018-06-15 16:00 | 476 | 475
2018-06-15 16:30 | 507 | 506
2018-06-15 17:00 | 531 | 531
2018-06-15 17:30 | 576 | 575
2018-06-15 18:00 | 595 | 594
2018-06-15 18:30 | 570 | 570
2018-06-15 19:00 | 571 | 570
2018-06-15 19:30 | 558 | 557
2018-06-15 20:00 | 556 | 555
2018-06-15 20:30 | 559 | 558
2018-06-15 21:00 | 543 | 542
2018-06-15 21:30 | 531 | 529
2018-06-15 22:00 | 511 | 509
2018-06-15 22:30 | 495 | 492
2018-06-15 23:00 | 473 | 469
2018-06-15 23:30 | 455 | 449
2018-06-16 | 434 | 425
2018-06-16 00:30 | 417 | 405
2018-06-16 01:00 | 397 | 383
2018-06-16 01:30 | 378 | 364
2018-06-16 02:00 | 368 | 352
2018-06-16 02:30 | 364 | 347
2018-06-16 03:00 | 349 | 330
2018-06-16 03:30 | 339 | 321
2018-06-16 04:00 | 328 | 315
2018-06-16 04:30 | 333 | 320
2018-06-16 05:00 | 323 | 311
2018-06-16 05:30 | 328 | 319
2018-06-16 06:00 | 353 | 345
2018-06-16 06:30 | 384 | 377
2018-06-16 07:00 | 403 | 398
2018-06-16 07:30 | 450 | 445
2018-06-16 08:00 | 469 | 465
2018-06-16 08:30 | 470 | 466
2018-06-16 09:00 | 460 | 457
2018-06-16 09:30 | 449 | 445
2018-06-16 10:00 | 419 | 414
2018-06-16 10:30 | 392 | 388
2018-06-16 11:00 | 373 | 368
2018-06-16 11:30 | 354 | 349
2018-06-16 12:00 | 344 | 338
2018-06-16 12:30 | 334 | 328
2018-06-16 13:00 | 337 | 331
2018-06-16 13:30 | 339 | 333
2018-06-16 14:00 | 355 | 348
2018-06-16 14:30 | 368 | 362
2018-06-16 15:00 | 387 | 381
2018-06-16 15:30 | 404 | 399
2018-06-16 16:00 | 421 | 417
2018-06-16 16:30 | 447 | 443
2018-06-16 17:00 | 481 | 479
2018-06-16 17:30 | 514 | 513
2018-06-16 18:00 | 530 | 524
2018-06-16 18:30 | 523 | 517
2018-06-16 19:00 | 522 | 516
2018-06-16 19:30 | 516 | 510
2018-06-16 20:00 | 518 | 512
2018-06-16 20:30 | 522 | 518
2018-06-16 21:00 | 508 | 507
2018-06-16 21:30 | 499 | 498
2018-06-16 22:00 | 491 | 489
2018-06-16 22:30 | 467 | 465
2018-06-16 23:00 | 454 | 452
2018-06-16 23:30 | 436 | 434
2018-06-17 | 422 | 418
2018-06-17 00:30 | 400 | 394
2018-06-17 01:00 | 389 | 380
2018-06-17 01:30 | 367 | 357
2018-06-17 02:00 | 353 | 343
2018-06-17 02:30 | 347 | 336
2018-06-17 03:00 | 343 | 332
2018-06-17 03:30 | 337 | 326
2018-06-17 04:00 | 327 | 316
2018-06-17 04:30 | 314 | 302
2018-06-17 05:00 | 312 | 299
2018-06-17 05:30 | 328 | 316
2018-06-17 06:00 | 352 | 341
2018-06-17 06:30 | 364 | 355
2018-06-17 07:00 | 382 | 374
2018-06-17 07:30 | 410 | 404
2018-06-17 08:00 | 414 | 409
2018-06-17 08:30 | 428 | 423
2018-06-17 09:00 | 428 | 423
2018-06-17 09:30 | 416 | 411
2018-06-17 10:00 | 407 | 401
2018-06-17 10:30 | 400 | 393
2018-06-17 11:00 | 393 | 385
2018-06-17 11:30 | 384 | 376
2018-06-17 12:00 | 378 | 370
2018-06-17 12:30 | 373 | 363
2018-06-17 13:00 | 366 | 357
2018-06-17 13:30 | 368 | 358
2018-06-17 14:00 | 371 | 362
2018-06-17 14:30 | 382 | 373
2018-06-17 15:00 | 397 | 389
2018-06-17 15:30 | 409 | 403
2018-06-17 16:00 | 437 | 432
2018-06-17 16:30 | 462 | 458
2018-06-17 17:00 | 500 | 498
2018-06-17 17:30 | 546 | 543
2018-06-17 18:00 | 579 | 570
2018-06-17 18:30 | 580 | 570
2018-06-17 19:00 | 584 | 575
2018-06-17 19:30 | 573 | 566
2018-06-17 20:00 | 569 | 563
2018-06-17 20:30 | 568 | 563
2018-06-17 21:00 | 548 | 543
2018-06-17 21:30 | 526 | 525
2018-06-17 22:00 | 505 | 505
2018-06-17 22:30 | 479 | 478
2018-06-17 23:00 | 456 | 455
2018-06-17 23:30 | 441 | 439
2018-06-18 | 422 | 418
2018-06-18 00:30 | 400 | 395
2018-06-18 01:00 | 381 | 373
2018-06-18 01:30 | 371 | 363
2018-06-18 02:00 | 358 | 350
2018-06-18 02:30 | 355 | 347
2018-06-18 03:00 | 359 | 350
2018-06-18 03:30 | 352 | 343
2018-06-18 04:00 | 350 | 340
2018-06-18 04:30 | 358 | 349
2018-06-18 05:00 | 374 | 367
2018-06-18 05:30 | 403 | 400
2018-06-18 06:00 | 447 | 444
2018-06-18 06:30 | 526 | 519
2018-06-18 07:00 | 580 | 574
2018-06-18 07:30 | 624 | 618
2018-06-18 08:00 | 646 | 639
2018-06-18 08:30 | 628 | 620
2018-06-18 09:00 | 590 | 582
2018-06-18 09:30 | 565 | 555
2018-06-18 10:00 | 522 | 519
2018-06-18 10:30 | 499 | 497
2018-06-18 11:00 | 473 | 472
2018-06-18 11:30 | 453 | 452
2018-06-18 12:00 | 438 | 437
2018-06-18 12:30 | 440 | 439
2018-06-18 13:00 | 443 | 442
2018-06-18 13:30 | 447 | 446
2018-06-18 14:00 | 457 | 456
2018-06-18 14:30 | 465 | 465
2018-06-18 15:00 | 481 | 481
2018-06-18 15:30 | 505 | 505
2018-06-18 16:00 | 539 | 538
2018-06-18 16:30 | 560 | 559
2018-06-18 17:00 | 598 | 594
2018-06-18 17:30 | 647 | 641
2018-06-18 18:00 | 671 | 665
2018-06-18 18:30 | 664 | 657
2018-06-18 19:00 | 658 | 652
2018-06-18 19:30 | 646 | 639
2018-06-18 20:00 | 641 | 635
2018-06-18 20:30 | 639 | 632
2018-06-18 21:00 | 599 | 594
2018-06-18 21:30 | 569 | 562
2018-06-18 22:00 | 541 | 536
2018-06-18 22:30 | 515 | 514
2018-06-18 23:00 | 500 | 500
2018-06-18 23:30 | 484 | 483
2018-06-19 | 461 | 460
2018-06-19 00:30 | 425 | 423
2018-06-19 01:00 | 411 | 407
2018-06-19 01:30 | 398 | 394
2018-06-19 02:00 | 388 | 382
2018-06-19 02:30 | 385 | 378
2018-06-19 03:00 | 380 | 373
2018-06-19 03:30 | 386 | 379
2018-06-19 04:00 | 388 | 381
2018-06-19 04:30 | 392 | 386
2018-06-19 05:00 | 404 | 399
2018-06-19 05:30 | 433 | 431
2018-06-19 06:00 | 479 | 471
2018-06-19 06:30 | 535 | 530
2018-06-19 07:00 | 596 | 591
2018-06-19 07:30 | 645 | 639
2018-06-19 08:00 | 650 | 641
2018-06-19 08:30 | 616 | 606
2018-06-19 09:00 | 578 | 567
2018-06-19 09:30 | 532 | 529
2018-06-19 10:00 | 497 | 495
2018-06-19 10:30 | 471 | 471
2018-06-19 11:00 | 455 | 454
2018-06-19 11:30 | 439 | 438
2018-06-19 12:00 | 431 | 429
2018-06-19 12:30 | 431 | 429
2018-06-19 13:00 | 433 | 431
2018-06-19 13:30 | 430 | 428
2018-06-19 14:00 | 443 | 441
2018-06-19 14:30 | 454 | 452
2018-06-19 15:00 | 468 | 466
2018-06-19 15:30 | 486 | 484
2018-06-19 16:00 | 515 | 513
2018-06-19 16:30 | 549 | 547
2018-06-19 17:00 | 593 | 592
2018-06-19 17:30 | 647 | 644
2018-06-19 18:00 | 675 | 671
2018-06-19 18:30 | 673 | 667
2018-06-19 19:00 | 671 | 666
2018-06-19 19:30 | 663 | 657
2018-06-19 20:00 | 650 | 648
2018-06-19 20:30 | 647 | 645
2018-06-19 21:00 | 614 | 612
2018-06-19 21:30 | 585 | 581
2018-06-19 22:00 | 559 | 555
2018-06-19 22:30 | 543 | 540
2018-06-19 23:00 | 514 | 512
2018-06-19 23:30 | 491 | 487
2018-06-20 | 461 | 457
2018-06-20 00:30 | 425 | 422
2018-06-20 01:00 | 411 | 406
2018-06-20 01:30 | 403 | 397
2018-06-20 02:00 | 396 | 389
2018-06-20 02:30 | 378 | 370
2018-06-20 03:00 | 355 | 346
2018-06-20 03:30 | 348 | 339
2018-06-20 04:00 | 349 | 341
2018-06-20 04:30 | 374 | 368
2018-06-20 05:00 | 393 | 388
2018-06-20 05:30 | 420 | 417
2018-06-20 06:00 | 452 | 450
2018-06-20 06:30 | 516 | 516
2018-06-20 07:00 | 582 | 579
2018-06-20 07:30 | 624 | 618
2018-06-20 08:00 | 623 | 617
2018-06-20 08:30 | 588 | 582
2018-06-20 09:00 | 549 | 544
2018-06-20 09:30 | 503 | 503
2018-06-20 10:00 | 489 | 487
2018-06-20 10:30 | 468 | 468
2018-06-20 11:00 | 445 | 445
2018-06-20 11:30 | 435 | 435
2018-06-20 12:00 | 433 | 433
2018-06-20 12:30 | 440 | 440
2018-06-20 13:00 | 435 | 435
2018-06-20 13:30 | 459 | 458
2018-06-20 14:00 | 465 | 465
2018-06-20 14:30 | 475 | 475
2018-06-20 15:00 | 483 | 483
2018-06-20 15:30 | 492 | 492
2018-06-20 16:00 | 516 | 515
2018-06-20 16:30 | 544 | 544
2018-06-20 17:00 | 585 | 583
2018-06-20 17:30 | 622 | 619
2018-06-20 18:00 | 650 | 641
2018-06-20 18:30 | 641 | 628
2018-06-20 19:00 | 640 | 627
2018-06-20 19:30 | 627 | 616
2018-06-20 20:00 | 627 | 618
2018-06-20 20:30 | 638 | 630
2018-06-20 21:00 | 610 | 600
2018-06-20 21:30 | 577 | 566
2018-06-20 22:00 | 552 | 539
2018-06-20 22:30 | 515 | 513
2018-06-20 23:00 | 478 | 475
2018-06-20 23:30 | 457 | 453
2018-06-21 | 432 | 427
2018-06-21 00:30 | 402 | 396
2018-06-21 01:00 | 386 | 379
2018-06-21 01:30 | 377 | 370
2018-06-21 02:00 | 368 | 360
2018-06-21 02:30 | 361 | 353
2018-06-21 03:00 | 363 | 355
2018-06-21 03:30 | 356 | 348
2018-06-21 04:00 | 352 | 344
2018-06-21 04:30 | 362 | 355
2018-06-21 05:00 | 377 | 371
2018-06-21 05:30 | 412 | 408
2018-06-21 06:00 | 452 | 450
2018-06-21 06:30 | 513 | 512
2018-06-21 07:00 | 583 | 582
2018-06-21 07:30 | 612 | 610
2018-06-21 08:00 | 638 | 636
2018-06-21 08:30 | 628 | 625
2018-06-21 09:00 | 600 | 596
2018-06-21 09:30 | 567 | 563
2018-06-21 10:00 | 537 | 535
2018-06-21 10:30 | 523 | 522
2018-06-21 11:00 | 516 | 514
2018-06-21 11:30 | 506 | 505
2018-06-21 12:00 | 499 | 498
2018-06-21 12:30 | 497 | 495
2018-06-21 13:00 | 499 | 498
2018-06-21 13:30 | 508 | 507
2018-06-21 14:00 | 528 | 527
2018-06-21 14:30 | 538 | 537
2018-06-21 15:00 | 551 | 550
2018-06-21 15:30 | 554 | 553
2018-06-21 16:00 | 564 | 563
2018-06-21 16:30 | 567 | 565
2018-06-21 17:00 | 585 | 584
2018-06-21 17:30 | 621 | 621
2018-06-21 18:00 | 655 | 651
2018-06-21 18:30 | 654 | 649
2018-06-21 19:00 | 672 | 666
2018-06-21 19:30 | 674 | 667
2018-06-21 20:00 | 664 | 657
2018-06-21 20:30 | 667 | 660
2018-06-21 21:00 | 642 | 634
2018-06-21 21:30 | 605 | 596
2018-06-21 22:00 | 576 | 564
2018-06-21 22:30 | 566 | 556
2018-06-21 23:00 | 534 | 526
2018-06-21 23:30 | 503 | 501
2018-06-22 | 478 | 475
2018-06-22 00:30 | 449 | 446
2018-06-22 01:00 | 425 | 420
2018-06-22 01:30 | 407 | 402
2018-06-22 02:00 | 395 | 388
2018-06-22 02:30 | 396 | 389
2018-06-22 03:00 | 384 | 377
2018-06-22 03:30 | 377 | 370
2018-06-22 04:00 | 373 | 367
2018-06-22 04:30 | 374 | 368
2018-06-22 05:00 | 368 | 362
2018-06-22 05:30 | 402 | 398
2018-06-22 06:00 | 439 | 437
2018-06-22 06:30 | 505 | 504
2018-06-22 07:00 | 570 | 569
2018-06-22 07:30 | 614 | 610
2018-06-22 08:00 | 613 | 608
2018-06-22 08:30 | 595 | 589
2018-06-22 09:00 | 567 | 559
2018-06-22 09:30 | 531 | 528
2018-06-22 10:00 | 517 | 515
2018-06-22 10:30 | 521 | 518
2018-06-22 11:00 | 505 | 502
2018-06-22 11:30 | 488 | 487
2018-06-22 12:00 | 470 | 470
2018-06-22 12:30 | 464 | 464
2018-06-22 13:00 | 470 | 469
2018-06-22 13:30 | 478 | 478
2018-06-22 14:00 | 488 | 488
2018-06-22 14:30 | 495 | 495
2018-06-22 15:00 | 510 | 509
2018-06-22 15:30 | 523 | 523
2018-06-22 16:00 | 550 | 550
2018-06-22 16:30 | 575 | 575
2018-06-22 17:00 | 595 | 594
2018-06-22 17:30 | 630 | 625
2018-06-22 18:00 | 647 | 640
2018-06-22 18:30 | 642 | 634
2018-06-22 19:00 | 650 | 642
2018-06-22 19:30 | 646 | 637
2018-06-22 20:00 | 637 | 626
2018-06-22 20:30 | 630 | 622
2018-06-22 21:00 | 605 | 603
2018-06-22 21:30 | 599 | 598
2018-06-22 22:00 | 581 | 580
2018-06-22 22:30 | 554 | 553
2018-06-22 23:00 | 530 | 528
2018-06-22 23:30 | 512 | 509
2018-06-23 | 484 | 480
2018-06-23 00:30 | 454 | 447
2018-06-23 01:00 | 429 | 421
2018-06-23 01:30 | 412 | 402
2018-06-23 02:00 | 409 | 398
2018-06-23 02:30 | 398 | 387
2018-06-23 03:00 | 385 | 373
2018-06-23 03:30 | 368 | 355
2018-06-23 04:00 | 368 | 354
2018-06-23 04:30 | 364 | 351
2018-06-23 05:00 | 361 | 348
2018-06-23 05:30 | 366 | 356
2018-06-23 06:00 | 380 | 371
2018-06-23 06:30 | 419 | 412
2018-06-23 07:00 | 448 | 442
2018-06-23 07:30 | 484 | 481
2018-06-23 08:00 | 510 | 507
2018-06-23 08:30 | 526 | 521
2018-06-23 09:00 | 515 | 511
2018-06-23 09:30 | 512 | 507
2018-06-23 10:00 | 492 | 486
2018-06-23 10:30 | 476 | 470
2018-06-23 11:00 | 448 | 444
2018-06-23 11:30 | 428 | 424
2018-06-23 12:00 | 401 | 395
2018-06-23 12:30 | 381 | 375
2018-06-23 13:00 | 374 | 369
2018-06-23 13:30 | 376 | 372
2018-06-23 14:00 | 379 | 375
2018-06-23 14:30 | 390 | 387
2018-06-23 15:00 | 403 | 399
2018-06-23 15:30 | 409 | 406
2018-06-23 16:00 | 434 | 431
2018-06-23 16:30 | 455 | 453
2018-06-23 17:00 | 510 | 508
2018-06-23 17:30 | 534 | 532
2018-06-23 18:00 | 552 | 549
2018-06-23 18:30 | 552 | 549
2018-06-23 19:00 | 550 | 548
2018-06-23 19:30 | 543 | 540
2018-06-23 20:00 | 549 | 546
2018-06-23 20:30 | 562 | 559
2018-06-23 21:00 | 552 | 548
2018-06-23 21:30 | 534 | 532
2018-06-23 22:00 | 527 | 525
2018-06-23 22:30 | 516 | 515
2018-06-23 23:00 | 501 | 500
2018-06-23 23:30 | 484 | 483
2018-06-24 | 461 | 458
2018-06-24 00:30 | 422 | 418
2018-06-24 01:00 | 396 | 391
2018-06-24 01:30 | 384 | 377
2018-06-24 02:00 | 375 | 366
2018-06-24 02:30 | 354 | 345
2018-06-24 03:00 | 356 | 347
2018-06-24 03:30 | 366 | 357
2018-06-24 04:00 | 370 | 360
2018-06-24 04:30 | 363 | 354
2018-06-24 05:00 | 356 | 348
2018-06-24 05:30 | 357 | 349
2018-06-24 06:00 | 365 | 358
2018-06-24 06:30 | 386 | 381
2018-06-24 07:00 | 404 | 398
2018-06-24 07:30 | 426 | 421
2018-06-24 08:00 | 446 | 443
2018-06-24 08:30 | 472 | 469
2018-06-24 09:00 | 476 | 473
2018-06-24 09:30 | 468 | 465
2018-06-24 10:00 | 443 | 439
2018-06-24 10:30 | 416 | 411
2018-06-24 11:00 | 388 | 383
2018-06-24 11:30 | 375 | 369
2018-06-24 12:00 | 366 | 360
2018-06-24 12:30 | 358 | 352
2018-06-24 13:00 | 360 | 354
2018-06-24 13:30 | 371 | 365
2018-06-24 14:00 | 394 | 389
2018-06-24 14:30 | 387 | 382
2018-06-24 15:00 | 408 | 404
2018-06-24 15:30 | 429 | 425
2018-06-24 16:00 | 448 | 445
2018-06-24 16:30 | 482 | 479
2018-06-24 17:00 | 531 | 529
2018-06-24 17:30 | 554 | 553
2018-06-24 18:00 | 586 | 586
2018-06-24 18:30 | 585 | 584
2018-06-24 19:00 | 584 | 583
2018-06-24 19:30 | 570 | 569
2018-06-24 20:00 | 575 | 574
2018-06-24 20:30 | 571 | 569
2018-06-24 21:00 | 557 | 556
2018-06-24 21:30 | 535 | 534
2018-06-24 22:00 | 516 | 515
2018-06-24 22:30 | 498 | 497
2018-06-24 23:00 | 477 | 476
2018-06-24 23:30 | 455 | 453
2018-06-25 | 426 | 422
2018-06-25 00:30 | 391 | 385
2018-06-25 01:00 | 368 | 360
2018-06-25 01:30 | 355 | 345
2018-06-25 02:00 | 349 | 338
2018-06-25 02:30 | 348 | 336
2018-06-25 03:00 | 350 | 338
2018-06-25 03:30 | 351 | 339
2018-06-25 04:00 | 359 | 347
2018-06-25 04:30 | 369 | 360
2018-06-25 05:00 | 382 | 374
2018-06-25 05:30 | 402 | 397
2018-06-25 06:00 | 448 | 445
2018-06-25 06:30 | 527 | 525
2018-06-25 07:00 | 597 | 592
2018-06-25 07:30 | 624 | 618
2018-06-25 08:00 | 646 | 640
2018-06-25 08:30 | 634 | 628
2018-06-25 09:00 | 606 | 600
2018-06-25 09:30 | 581 | 576
2018-06-25 10:00 | 554 | 547
2018-06-25 10:30 | 535 | 528
2018-06-25 11:00 | 506 | 500
2018-06-25 11:30 | 472 | 471
2018-06-25 12:00 | 470 | 470
2018-06-25 12:30 | 475 | 475
2018-06-25 13:00 | 485 | 484
2018-06-25 13:30 | 478 | 478
2018-06-25 14:00 | 486 | 486
2018-06-25 14:30 | 500 | 500
2018-06-25 15:00 | 519 | 519
2018-06-25 15:30 | 525 | 524
2018-06-25 16:00 | 524 | 524
2018-06-25 16:30 | 553 | 553
2018-06-25 17:00 | 597 | 596
2018-06-25 17:30 | 638 | 635
2018-06-25 18:00 | 676 | 669
2018-06-25 18:30 | 672 | 662
2018-06-25 19:00 | 672 | 661
2018-06-25 19:30 | 655 | 643
2018-06-25 20:00 | 647 | 635
2018-06-25 20:30 | 638 | 628
2018-06-25 21:00 | 611 | 604
2018-06-25 21:30 | 585 | 578
2018-06-25 22:00 | 562 | 554
2018-06-25 22:30 | 565 | 558
2018-06-25 23:00 | 520 | 512
2018-06-25 23:30 | 487 | 477
2018-06-26 | 449 | 436
2018-06-26 00:30 | 427 | 411
2018-06-26 01:00 | 396 | 389
2018-06-26 01:30 | 377 | 370
2018-06-26 02:00 | 361 | 354
2018-06-26 02:30 | 354 | 346
2018-06-26 03:00 | 351 | 343
2018-06-26 03:30 | 349 | 341
2018-06-26 04:00 | 345 | 338
2018-06-26 04:30 | 356 | 349
2018-06-26 05:00 | 362 | 357
2018-06-26 05:30 | 391 | 388
2018-06-26 06:00 | 429 | 428
2018-06-26 06:30 | 508 | 502
2018-06-26 07:00 | 565 | 559
2018-06-26 07:30 | 589 | 583
2018-06-26 08:00 | 602 | 596
2018-06-26 08:30 | 592 | 585
2018-06-26 09:00 | 573 | 567
2018-06-26 09:30 | 550 | 544
2018-06-26 10:00 | 512 | 509
2018-06-26 10:30 | 496 | 495
2018-06-26 11:00 | 491 | 491
2018-06-26 11:30 | 494 | 493
2018-06-26 12:00 | 497 | 496
2018-06-26 12:30 | 495 | 494
2018-06-26 13:00 | 496 | 496
2018-06-26 13:30 | 508 | 507
2018-06-26 14:00 | 506 | 505
2018-06-26 14:30 | 517 | 516
2018-06-26 15:00 | 526 | 525
2018-06-26 15:30 | 531 | 530
2018-06-26 16:00 | 543 | 542
2018-06-26 16:30 | 570 | 569
2018-06-26 17:00 | 600 | 599
2018-06-26 17:30 | 635 | 631
2018-06-26 18:00 | 654 | 647
2018-06-26 18:30 | 648 | 639
2018-06-26 19:00 | 645 | 635
2018-06-26 19:30 | 634 | 623
2018-06-26 20:00 | 628 | 618
2018-06-26 20:30 | 620 | 613
2018-06-26 21:00 | 594 | 585
2018-06-26 21:30 | 568 | 558
2018-06-26 22:00 | 543 | 539
2018-06-26 22:30 | 524 | 522
2018-06-26 23:00 | 498 | 495
2018-06-26 23:30 | 475 | 470
2018-06-27 | 436 | 430
2018-06-27 00:30 | 409 | 400
2018-06-27 01:00 | 391 | 382
2018-06-27 01:30 | 376 | 365
2018-06-27 02:00 | 360 | 347
2018-06-27 02:30 | 348 | 337
2018-06-27 03:00 | 349 | 338
2018-06-27 03:30 | 353 | 342
2018-06-27 04:00 | 352 | 341
2018-06-27 04:30 | 363 | 353
2018-06-27 05:00 | 374 | 367
2018-06-27 05:30 | 393 | 387
2018-06-27 06:00 | 416 | 413
2018-06-27 06:30 | 491 | 489
2018-06-27 07:00 | 549 | 542
2018-06-27 07:30 | 589 | 584
2018-06-27 08:00 | 621 | 615
2018-06-27 08:30 | 622 | 617
2018-06-27 09:00 | 599 | 593
2018-06-27 09:30 | 595 | 589
2018-06-27 10:00 | 598 | 591
2018-06-27 10:30 | 597 | 591
2018-06-27 11:00 | 598 | 592
2018-06-27 11:30 | 592 | 586
2018-06-27 12:00 | 590 | 585
2018-06-27 12:30 | 596 | 589
2018-06-27 13:00 | 602 | 596
2018-06-27 13:30 | 601 | 594
2018-06-27 14:00 | 600 | 593
2018-06-27 14:30 | 591 | 582
2018-06-27 15:00 | 597 | 587
2018-06-27 15:30 | 606 | 595
2018-06-27 16:00 | 623 | 613
2018-06-27 16:30 | 640 | 632
2018-06-27 17:00 | 661 | 651
2018-06-27 17:30 | 685 | 665
2018-06-27 18:00 | 713 | 690
2018-06-27 18:30 | 704 | 682
2018-06-27 19:00 | 695 | 675
2018-06-27 19:30 | 671 | 650
2018-06-27 20:00 | 647 | 640
2018-06-27 20:30 | 650 | 642
2018-06-27 21:00 | 618 | 611
2018-06-27 21:30 | 599 | 591
2018-06-27 22:00 | 568 | 559
2018-06-27 22:30 | 546 | 543
2018-06-27 23:00 | 523 | 519
2018-06-27 23:30 | 480 | 475
2018-06-28 | 459 | 451
2018-06-28 00:30 | 424 | 416
2018-06-28 01:00 | 397 | 390
2018-06-28 01:30 | 382 | 376
2018-06-28 02:00 | 371 | 364
2018-06-28 02:30 | 367 | 360
2018-06-28 03:00 | 366 | 359
2018-06-28 03:30 | 364 | 357
2018-06-28 04:00 | 366 | 358
2018-06-28 04:30 | 371 | 365
2018-06-28 05:00 | 381 | 376
2018-06-28 05:30 | 405 | 401
2018-06-28 06:00 | 431 | 428
2018-06-28 06:30 | 490 | 484
2018-06-28 07:00 | 550 | 540
2018-06-28 07:30 | 592 | 584
2018-06-28 08:00 | 624 | 615
2018-06-28 08:30 | 607 | 601
2018-06-28 09:00 | 583 | 576
2018-06-28 09:30 | 574 | 566
2018-06-28 10:00 | 561 | 553
2018-06-28 10:30 | 535 | 528
2018-06-28 11:00 | 516 | 511
2018-06-28 11:30 | 522 | 517
2018-06-28 12:00 | 531 | 526
2018-06-28 12:30 | 533 | 528
2018-06-28 13:00 | 528 | 523
2018-06-28 13:30 | 519 | 513
2018-06-28 14:00 | 509 | 504
2018-06-28 14:30 | 513 | 508
2018-06-28 15:00 | 523 | 518
2018-06-28 15:30 | 546 | 541
2018-06-28 16:00 | 571 | 566
2018-06-28 16:30 | 580 | 575
2018-06-28 17:00 | 610 | 604
2018-06-28 17:30 | 637 | 629
2018-06-28 18:00 | 667 | 659
2018-06-28 18:30 | 666 | 656
2018-06-28 19:00 | 644 | 636
2018-06-28 19:30 | 629 | 623
2018-06-28 20:00 | 629 | 623
2018-06-28 20:30 | 631 | 625
2018-06-28 21:00 | 611 | 607
2018-06-28 21:30 | 580 | 574
2018-06-28 22:00 | 549 | 548
2018-06-28 22:30 | 534 | 533
2018-06-28 23:00 | 509 | 508
2018-06-28 23:30 | 489 | 488
2018-06-29 | 466 | 464
2018-06-29 00:30 | 426 | 423
2018-06-29 01:00 | 398 | 394
2018-06-29 01:30 | 377 | 372
2018-06-29 02:00 | 364 | 359
2018-06-29 02:30 | 352 | 346
2018-06-29 03:00 | 346 | 340
2018-06-29 03:30 | 345 | 339
2018-06-29 04:00 | 348 | 342
2018-06-29 04:30 | 353 | 347
2018-06-29 05:00 | 358 | 354
2018-06-29 05:30 | 380 | 378
2018-06-29 06:00 | 413 | 412
2018-06-29 06:30 | 460 | 459
2018-06-29 07:00 | 528 | 522
2018-06-29 07:30 | 577 | 568
2018-06-29 08:00 | 605 | 598
2018-06-29 08:30 | 598 | 591
2018-06-29 09:00 | 575 | 567
2018-06-29 09:30 | 570 | 562
2018-06-29 10:00 | 548 | 542
2018-06-29 10:30 | 526 | 522
2018-06-29 11:00 | 489 | 485
2018-06-29 11:30 | 459 | 456
2018-06-29 12:00 | 444 | 444
2018-06-29 12:30 | 437 | 437
2018-06-29 13:00 | 433 | 433
2018-06-29 13:30 | 438 | 438
2018-06-29 14:00 | 444 | 444
2018-06-29 14:30 | 455 | 455
2018-06-29 15:00 | 466 | 466
2018-06-29 15:30 | 478 | 478
2018-06-29 16:00 | 508 | 508
2018-06-29 16:30 | 537 | 536
2018-06-29 17:00 | 560 | 559
2018-06-29 17:30 | 579 | 577
2018-06-29 18:00 | 602 | 596
2018-06-29 18:30 | 610 | 603
2018-06-29 19:00 | 606 | 598
2018-06-29 19:30 | 576 | 569
2018-06-29 20:00 | 564 | 560
2018-06-29 20:30 | 571 | 567
2018-06-29 21:00 | 549 | 548
2018-06-29 21:30 | 535 | 535
2018-06-29 22:00 | 518 | 517
2018-06-29 22:30 | 509 | 508
2018-06-29 23:00 | 487 | 486
2018-06-29 23:30 | 472 | 470
2018-06-30 | 449 | 445
2018-06-30 00:30 | 408 | 403
2018-06-30 01:00 | 373 | 367
2018-06-30 01:30 | 351 | 344
2018-06-30 02:00 | 338 | 330
2018-06-30 02:30 | 331 | 323
2018-06-30 03:00 | 329 | 320
2018-06-30 03:30 | 327 | 318
2018-06-30 04:00 | 326 | 317
2018-06-30 04:30 | 330 | 321
2018-06-30 05:00 | 332 | 323
2018-06-30 05:30 | 343 | 335
2018-06-30 06:00 | 354 | 347
2018-06-30 06:30 | 370 | 365
2018-06-30 07:00 | 398 | 393
2018-06-30 07:30 | 427 | 423
2018-06-30 08:00 | 472 | 468
2018-06-30 08:30 | 494 | 492
2018-06-30 09:00 | 500 | 498
2018-06-30 09:30 | 503 | 501
2018-06-30 10:00 | 480 | 478
2018-06-30 10:30 | 455 | 454
2018-06-30 11:00 | 430 | 428
2018-06-30 11:30 | 410 | 408
2018-06-30 12:00 | 399 | 397
2018-06-30 12:30 | 392 | 389
2018-06-30 13:00 | 375 | 372
2018-06-30 13:30 | 377 | 374
2018-06-30 14:00 | 383 | 380
2018-06-30 14:30 | 389 | 386
2018-06-30 15:00 | 392 | 390
2018-06-30 15:30 | 403 | 401
2018-06-30 16:00 | 435 | 433
2018-06-30 16:30 | 459 | 457
2018-06-30 17:00 | 508 | 505
2018-06-30 17:30 | 538 | 531
2018-06-30 18:00 | 541 | 534
2018-06-30 18:30 | 537 | 530
2018-06-30 19:00 | 538 | 530
2018-06-30 19:30 | 529 | 521
2018-06-30 20:00 | 530 | 522
2018-06-30 20:30 | 542 | 534
2018-06-30 21:00 | 522 | 519
2018-06-30 21:30 | 506 | 504
2018-06-30 22:00 | 498 | 495
2018-06-30 22:30 | 488 | 485
2018-06-30 23:00 | 475 | 472
2018-06-30 23:30 | 457 | 453
2018-07-01 | 432 | 426
2018-07-01 00:30 | 399 | 391
2018-07-01 01:00 | 371 | 362
2018-07-01 01:30 | 356 | 347
2018-07-01 02:00 | 348 | 338
2018-07-01 02:30 | 342 | 332
2018-07-01 03:00 | 337 | 327
2018-07-01 03:30 | 335 | 324
2018-07-01 04:00 | 330 | 320
2018-07-01 04:30 | 325 | 315
2018-07-01 05:00 | 326 | 315
2018-07-01 05:30 | 330 | 320
2018-07-01 06:00 | 343 | 334
2018-07-01 06:30 | 357 | 348
2018-07-01 07:00 | 373 | 365
2018-07-01 07:30 | 389 | 382
2018-07-01 08:00 | 427 | 421
2018-07-01 08:30 | 458 | 453
2018-07-01 09:00 | 462 | 458
2018-07-01 09:30 | 471 | 468
2018-07-01 10:00 | 465 | 462
2018-07-01 10:30 | 458 | 455
2018-07-01 11:00 | 450 | 447
2018-07-01 11:30 | 425 | 423
2018-07-01 12:00 | 420 | 418
2018-07-01 12:30 | 416 | 414
2018-07-01 13:00 | 400 | 398
2018-07-01 13:30 | 393 | 391
2018-07-01 14:00 | 401 | 399
2018-07-01 14:30 | 409 | 407
2018-07-01 15:00 | 415 | 413
2018-07-01 15:30 | 427 | 425
2018-07-01 16:00 | 442 | 440
2018-07-01 16:30 | 484 | 482
2018-07-01 17:00 | 506 | 504
2018-07-01 17:30 | 545 | 538
2018-07-01 18:00 | 573 | 565
2018-07-01 18:30 | 571 | 562
2018-07-01 19:00 | 556 | 548
2018-07-01 19:30 | 525 | 516
2018-07-01 20:00 | 510 | 509
2018-07-01 20:30 | 509 | 508
2018-07-01 21:00 | 493 | 492
2018-07-01 21:30 | 483 | 481
2018-07-01 22:00 | 471 | 469
2018-07-01 22:30 | 460 | 458
2018-07-01 23:00 | 448 | 445
2018-07-01 23:30 | 418 | 414
2018-07-02 | 376 | 371
2018-07-02 00:30 | 354 | 347
2018-07-02 01:00 | 344 | 336
2018-07-02 01:30 | 333 | 324
2018-07-02 02:00 | 319 | 309
2018-07-02 02:30 | 314 | 305
2018-07-02 03:00 | 315 | 306
2018-07-02 03:30 | 317 | 307
2018-07-02 04:00 | 319 | 309
2018-07-02 04:30 | 326 | 318
2018-07-02 05:00 | 336 | 329
2018-07-02 05:30 | 350 | 346
2018-07-02 06:00 | 382 | 380
2018-07-02 06:30 | 440 | 439
2018-07-02 07:00 | 502 | 496
2018-07-02 07:30 | 533 | 528
2018-07-02 08:00 | 580 | 574
2018-07-02 08:30 | 591 | 584
2018-07-02 09:00 | 576 | 568
2018-07-02 09:30 | 561 | 553
2018-07-02 10:00 | 535 | 526
2018-07-02 10:30 | 516 | 514
2018-07-02 11:00 | 502 | 501
2018-07-02 11:30 | 508 | 507
2018-07-02 12:00 | 501 | 500
2018-07-02 12:30 | 494 | 493
2018-07-02 13:00 | 492 | 492
2018-07-02 13:30 | 487 | 486
2018-07-02 14:00 | 486 | 486
2018-07-02 14:30 | 504 | 503
2018-07-02 15:00 | 503 | 502
2018-07-02 15:30 | 510 | 510
2018-07-02 16:00 | 539 | 539
2018-07-02 16:30 | 576 | 575
2018-07-02 17:00 | 612 | 611
2018-07-02 17:30 | 629 | 628
2018-07-02 18:00 | 648 | 646
2018-07-02 18:30 | 630 | 627
2018-07-02 19:00 | 614 | 610
2018-07-02 19:30 | 594 | 590
2018-07-02 20:00 | 588 | 586
2018-07-02 20:30 | 583 | 582
2018-07-02 21:00 | 554 | 553
2018-07-02 21:30 | 532 | 529
2018-07-02 22:00 | 516 | 512
2018-07-02 22:30 | 491 | 488
2018-07-02 23:00 | 467 | 464
2018-07-02 23:30 | 440 | 438
2018-07-03 | 421 | 419
2018-07-03 00:30 | 392 | 388
2018-07-03 01:00 | 365 | 360
2018-07-03 01:30 | 346 | 340
2018-07-03 02:00 | 334 | 327
2018-07-03 02:30 | 330 | 323
2018-07-03 03:00 | 332 | 325
2018-07-03 03:30 | 334 | 326
2018-07-03 04:00 | 337 | 329
2018-07-03 04:30 | 340 | 333
2018-07-03 05:00 | 352 | 346
2018-07-03 05:30 | 379 | 375
2018-07-03 06:00 | 403 | 400
2018-07-03 06:30 | 451 | 451
2018-07-03 07:00 | 496 | 496
2018-07-03 07:30 | 538 | 536
2018-07-03 08:00 | 554 | 552
2018-07-03 08:30 | 552 | 551
2018-07-03 09:00 | 536 | 533
2018-07-03 09:30 | 521 | 518
2018-07-03 10:00 | 511 | 508
2018-07-03 10:30 | 488 | 486
2018-07-03 11:00 | 462 | 460
2018-07-03 11:30 | 450 | 448
2018-07-03 12:00 | 458 | 457
2018-07-03 12:30 | 439 | 437
2018-07-03 13:00 | 431 | 430
2018-07-03 13:30 | 451 | 450
2018-07-03 14:00 | 456 | 455
2018-07-03 14:30 | 454 | 453
2018-07-03 15:00 | 458 | 457
2018-07-03 15:30 | 465 | 464
2018-07-03 16:00 | 485 | 484
2018-07-03 16:30 | 512 | 511
2018-07-03 17:00 | 554 | 553
2018-07-03 17:30 | 583 | 583
2018-07-03 18:00 | 608 | 604
2018-07-03 18:30 | 607 | 602
2018-07-03 19:00 | 609 | 603
2018-07-03 19:30 | 608 | 601
2018-07-03 20:00 | 609 | 602
2018-07-03 20:30 | 601 | 596
2018-07-03 21:00 | 564 | 562
2018-07-03 21:30 | 537 | 535
2018-07-03 22:00 | 512 | 510
2018-07-03 22:30 | 480 | 477
2018-07-03 23:00 | 453 | 451
2018-07-03 23:30 | 437 | 434
2018-07-04 | 408 | 404
2018-07-04 00:30 | 382 | 377
2018-07-04 01:00 | 362 | 356
2018-07-04 01:30 | 357 | 349
2018-07-04 02:00 | 354 | 346
2018-07-04 02:30 | 333 | 324
2018-07-04 03:00 | 341 | 330
2018-07-04 03:30 | 331 | 321
2018-07-04 04:00 | 337 | 327
2018-07-04 04:30 | 339 | 330
2018-07-04 05:00 | 342 | 334
2018-07-04 05:30 | 369 | 364
2018-07-04 06:00 | 397 | 394
2018-07-04 06:30 | 465 | 463
2018-07-04 07:00 | 514 | 513
2018-07-04 07:30 | 563 | 560
2018-07-04 08:00 | 593 | 586
2018-07-04 08:30 | 602 | 596
2018-07-04 09:00 | 577 | 571
2018-07-04 09:30 | 538 | 532
2018-07-04 10:00 | 508 | 504
2018-07-04 10:30 | 488 | 484
2018-07-04 11:00 | 481 | 478
2018-07-04 11:30 | 475 | 472
2018-07-04 12:00 | 468 | 464
2018-07-04 12:30 | 463 | 459
2018-07-04 13:00 | 453 | 453
2018-07-04 13:30 | 462 | 462
2018-07-04 14:00 | 463 | 463
2018-07-04 14:30 | 466 | 466
2018-07-04 15:00 | 472 | 472
2018-07-04 15:30 | 486 | 486
2018-07-04 16:00 | 503 | 502
2018-07-04 16:30 | 529 | 529
2018-07-04 17:00 | 560 | 559
2018-07-04 17:30 | 603 | 598
2018-07-04 18:00 | 628 | 623
2018-07-04 18:30 | 618 | 612
2018-07-04 19:00 | 618 | 612
2018-07-04 19:30 | 597 | 590
2018-07-04 20:00 | 582 | 581
2018-07-04 20:30 | 576 | 574
2018-07-04 21:00 | 556 | 555
2018-07-04 21:30 | 533 | 530
2018-07-04 22:00 | 497 | 495
2018-07-04 22:30 | 476 | 473
2018-07-04 23:00 | 451 | 450
2018-07-04 23:30 | 443 | 442
2018-07-05 | 419 | 416
2018-07-05 00:30 | 387 | 383
2018-07-05 01:00 | 383 | 378
2018-07-05 01:30 | 353 | 346
2018-07-05 02:00 | 332 | 324
2018-07-05 02:30 | 328 | 320
2018-07-05 03:00 | 327 | 319
2018-07-05 03:30 | 326 | 318
2018-07-05 04:00 | 322 | 314
2018-07-05 04:30 | 331 | 324
2018-07-05 05:00 | 336 | 330
2018-07-05 05:30 | 358 | 354
2018-07-05 06:00 | 397 | 394
2018-07-05 06:30 | 443 | 442
2018-07-05 07:00 | 492 | 491
2018-07-05 07:30 | 542 | 540
2018-07-05 08:00 | 562 | 560
2018-07-05 08:30 | 557 | 554
2018-07-05 09:00 | 544 | 542
2018-07-05 09:30 | 538 | 535
2018-07-05 10:00 | 541 | 539
2018-07-05 10:30 | 540 | 538
2018-07-05 11:00 | 516 | 515
2018-07-05 11:30 | 501 | 499
2018-07-05 12:00 | 496 | 495
2018-07-05 12:30 | 489 | 487
2018-07-05 13:00 | 483 | 482
2018-07-05 13:30 | 486 | 484
2018-07-05 14:00 | 502 | 500
2018-07-05 14:30 | 535 | 534
2018-07-05 15:00 | 534 | 532
2018-07-05 15:30 | 546 | 543
2018-07-05 16:00 | 529 | 527
2018-07-05 16:30 | 547 | 544
2018-07-05 17:00 | 567 | 565
2018-07-05 17:30 | 594 | 592
2018-07-05 18:00 | 610 | 607
2018-07-05 18:30 | 593 | 590
2018-07-05 19:00 | 588 | 586
2018-07-05 19:30 | 576 | 574
2018-07-05 20:00 | 555 | 554
2018-07-05 20:30 | 542 | 542
2018-07-05 21:00 | 529 | 529
2018-07-05 21:30 | 507 | 506
2018-07-05 22:00 | 486 | 484
2018-07-05 22:30 | 467 | 465
2018-07-05 23:00 | 442 | 440
2018-07-05 23:30 | 424 | 423
2018-07-06 | 405 | 402
2018-07-06 00:30 | 374 | 370
2018-07-06 01:00 | 355 | 350
2018-07-06 01:30 | 346 | 339
2018-07-06 02:00 | 336 | 328
2018-07-06 02:30 | 338 | 331
2018-07-06 03:00 | 338 | 331
2018-07-06 03:30 | 336 | 328
2018-07-06 04:00 | 338 | 330
2018-07-06 04:30 | 342 | 335
2018-07-06 05:00 | 345 | 338
2018-07-06 05:30 | 370 | 366
2018-07-06 06:00 | 391 | 388
2018-07-06 06:30 | 432 | 431
2018-07-06 07:00 | 476 | 475
2018-07-06 07:30 | 515 | 515
2018-07-06 08:00 | 534 | 534
2018-07-06 08:30 | 536 | 536
2018-07-06 09:00 | 521 | 521
2018-07-06 09:30 | 515 | 515
2018-07-06 10:00 | 514 | 514
2018-07-06 10:30 | 513 | 513
2018-07-06 11:00 | 503 | 503
2018-07-06 11:30 | 493 | 493
2018-07-06 12:00 | 491 | 491
2018-07-06 12:30 | 501 | 501
2018-07-06 13:00 | 494 | 494
2018-07-06 13:30 | 483 | 483
2018-07-06 14:00 | 496 | 496
2018-07-06 14:30 | 498 | 498
2018-07-06 15:00 | 498 | 498
2018-07-06 15:30 | 501 | 501
2018-07-06 16:00 | 507 | 507
2018-07-06 16:30 | 525 | 525
2018-07-06 17:00 | 540 | 540
2018-07-06 17:30 | 559 | 559
2018-07-06 18:00 | 579 | 579
2018-07-06 18:30 | 565 | 563
2018-07-06 19:00 | 555 | 554
2018-07-06 19:30 | 540 | 537
2018-07-06 20:00 | 533 | 531
2018-07-06 20:30 | 515 | 514
2018-07-06 21:00 | 492 | 490
2018-07-06 21:30 | 472 | 472
2018-07-06 22:00 | 466 | 465
2018-07-06 22:30 | 455 | 454
2018-07-06 23:00 | 437 | 436
2018-07-06 23:30 | 422 | 421
2018-07-07 | 405 | 403
2018-07-07 00:30 | 371 | 368
2018-07-07 01:00 | 359 | 354
2018-07-07 01:30 | 348 | 342
2018-07-07 02:00 | 335 | 328
2018-07-07 02:30 | 326 | 317
2018-07-07 03:00 | 327 | 318
2018-07-07 03:30 | 320 | 311
2018-07-07 04:00 | 322 | 313
2018-07-07 04:30 | 329 | 320
2018-07-07 05:00 | 325 | 316
2018-07-07 05:30 | 335 | 328
2018-07-07 06:00 | 341 | 334
2018-07-07 06:30 | 354 | 348
2018-07-07 07:00 | 364 | 359
2018-07-07 07:30 | 390 | 385
2018-07-07 08:00 | 412 | 409
2018-07-07 08:30 | 433 | 431
2018-07-07 09:00 | 452 | 450
2018-07-07 09:30 | 460 | 458
2018-07-07 10:00 | 449 | 448
2018-07-07 10:30 | 454 | 453
2018-07-07 11:00 | 437 | 436
2018-07-07 11:30 | 418 | 417
2018-07-07 12:00 | 403 | 402
2018-07-07 12:30 | 415 | 414
2018-07-07 13:00 | 412 | 412
2018-07-07 13:30 | 415 | 414
2018-07-07 14:00 | 405 | 405
2018-07-07 14:30 | 398 | 397
2018-07-07 15:00 | 383 | 382
2018-07-07 15:30 | 384 | 383
2018-07-07 16:00 | 408 | 406
2018-07-07 16:30 | 430 | 429
2018-07-07 17:00 | 467 | 466
2018-07-07 17:30 | 489 | 489
2018-07-07 18:00 | 510 | 510
2018-07-07 18:30 | 507 | 507
2018-07-07 19:00 | 500 | 500
2018-07-07 19:30 | 488 | 488
2018-07-07 20:00 | 482 | 481
2018-07-07 20:30 | 478 | 477
2018-07-07 21:00 | 457 | 456
2018-07-07 21:30 | 444 | 443
2018-07-07 22:00 | 439 | 438
2018-07-07 22:30 | 431 | 429
2018-07-07 23:00 | 418 | 415
2018-07-07 23:30 | 410 | 407
2018-07-08 | 394 | 390
2018-07-08 00:30 | 362 | 355
2018-07-08 01:00 | 345 | 337
2018-07-08 01:30 | 333 | 324
2018-07-08 02:00 | 318 | 308
2018-07-08 02:30 | 304 | 291
2018-07-08 03:00 | 292 | 279
2018-07-08 03:30 | 291 | 277
2018-07-08 04:00 | 294 | 280
2018-07-08 04:30 | 294 | 280
2018-07-08 05:00 | 306 | 293
2018-07-08 05:30 | 318 | 306
2018-07-08 06:00 | 331 | 320
2018-07-08 06:30 | 338 | 328
2018-07-08 07:00 | 354 | 344
2018-07-08 07:30 | 371 | 363
2018-07-08 08:00 | 391 | 384
2018-07-08 08:30 | 405 | 399
2018-07-08 09:00 | 400 | 394
2018-07-08 09:30 | 387 | 381
2018-07-08 10:00 | 373 | 367
2018-07-08 10:30 | 362 | 355
2018-07-08 11:00 | 354 | 346
2018-07-08 11:30 | 352 | 344
2018-07-08 12:00 | 354 | 347
2018-07-08 12:30 | 354 | 346
2018-07-08 13:00 | 352 | 344
2018-07-08 13:30 | 353 | 344
2018-07-08 14:00 | 357 | 350
2018-07-08 14:30 | 368 | 360
2018-07-08 15:00 | 380 | 373
2018-07-08 15:30 | 385 | 379
2018-07-08 16:00 | 399 | 394
2018-07-08 16:30 | 428 | 424
2018-07-08 17:00 | 474 | 471
2018-07-08 17:30 | 515 | 514
2018-07-08 18:00 | 550 | 546
2018-07-08 18:30 | 559 | 555
2018-07-08 19:00 | 562 | 558
2018-07-08 19:30 | 559 | 555
2018-07-08 20:00 | 551 | 547
2018-07-08 20:30 | 540 | 535
2018-07-08 21:00 | 522 | 522
2018-07-08 21:30 | 504 | 504
2018-07-08 22:00 | 488 | 487
2018-07-08 22:30 | 471 | 469
2018-07-08 23:00 | 443 | 442
2018-07-08 23:30 | 416 | 414
2018-07-09 | 389 | 385
2018-07-09 00:30 | 372 | 366
2018-07-09 01:00 | 360 | 351
2018-07-09 01:30 | 350 | 341
2018-07-09 02:00 | 335 | 326
2018-07-09 02:30 | 332 | 321
2018-07-09 03:00 | 331 | 319
2018-07-09 03:30 | 332 | 321
2018-07-09 04:00 | 335 | 324
2018-07-09 04:30 | 346 | 336
2018-07-09 05:00 | 355 | 347
2018-07-09 05:30 | 388 | 382
2018-07-09 06:00 | 418 | 416
2018-07-09 06:30 | 478 | 476
2018-07-09 07:00 | 545 | 544
2018-07-09 07:30 | 582 | 581
2018-07-09 08:00 | 589 | 588
2018-07-09 08:30 | 584 | 583
2018-07-09 09:00 | 567 | 565
2018-07-09 09:30 | 543 | 541
2018-07-09 10:00 | 514 | 512
2018-07-09 10:30 | 486 | 484
2018-07-09 11:00 | 466 | 465
2018-07-09 11:30 | 449 | 447
2018-07-09 12:00 | 442 | 441
2018-07-09 12:30 | 437 | 437
2018-07-09 13:00 | 434 | 433
2018-07-09 13:30 | 435 | 434
2018-07-09 14:00 | 442 | 441
2018-07-09 14:30 | 461 | 461
2018-07-09 15:00 | 480 | 480
2018-07-09 15:30 | 496 | 496
2018-07-09 16:00 | 518 | 518
2018-07-09 16:30 | 538 | 538
2018-07-09 17:00 | 566 | 566
2018-07-09 17:30 | 609 | 608
2018-07-09 18:00 | 661 | 658
2018-07-09 18:30 | 660 | 657
2018-07-09 19:00 | 660 | 657
2018-07-09 19:30 | 638 | 634
2018-07-09 20:00 | 616 | 612
2018-07-09 20:30 | 637 | 633
2018-07-09 21:00 | 615 | 614
2018-07-09 21:30 | 588 | 586
2018-07-09 22:00 | 553 | 551
2018-07-09 22:30 | 514 | 512
2018-07-09 23:00 | 498 | 496
2018-07-09 23:30 | 479 | 477
2018-07-10 | 455 | 453
2018-07-10 00:30 | 417 | 415
2018-07-10 01:00 | 391 | 388
2018-07-10 01:30 | 375 | 371
2018-07-10 02:00 | 364 | 358
2018-07-10 02:30 | 355 | 348
2018-07-10 03:00 | 351 | 344
2018-07-10 03:30 | 353 | 346
2018-07-10 04:00 | 358 | 351
2018-07-10 04:30 | 368 | 362
2018-07-10 05:00 | 372 | 367
2018-07-10 05:30 | 400 | 397
2018-07-10 06:00 | 439 | 437
2018-07-10 06:30 | 499 | 498
2018-07-10 07:00 | 573 | 571
2018-07-10 07:30 | 612 | 609
2018-07-10 08:00 | 641 | 638
2018-07-10 08:30 | 643 | 639
2018-07-10 09:00 | 619 | 614
2018-07-10 09:30 | 595 | 589
2018-07-10 10:00 | 558 | 557
2018-07-10 10:30 | 523 | 523
2018-07-10 11:00 | 493 | 493
2018-07-10 11:30 | 470 | 470
2018-07-10 12:00 | 462 | 462
2018-07-10 12:30 | 455 | 455
2018-07-10 13:00 | 453 | 453
2018-07-10 13:30 | 456 | 455
2018-07-10 14:00 | 460 | 460
2018-07-10 14:30 | 462 | 462
2018-07-10 15:00 | 480 | 479
2018-07-10 15:30 | 492 | 492
2018-07-10 16:00 | 507 | 507
2018-07-10 16:30 | 541 | 540
2018-07-10 17:00 | 574 | 574
2018-07-10 17:30 | 600 | 599
2018-07-10 18:00 | 627 | 627
2018-07-10 18:30 | 624 | 624
2018-07-10 19:00 | 620 | 620
2018-07-10 19:30 | 607 | 607
2018-07-10 20:00 | 615 | 615
2018-07-10 20:30 | 615 | 615
2018-07-10 21:00 | 588 | 587
2018-07-10 21:30 | 568 | 567
2018-07-10 22:00 | 555 | 554
2018-07-10 22:30 | 537 | 536
2018-07-10 23:00 | 514 | 512
2018-07-10 23:30 | 486 | 485
2018-07-11 | 461 | 459
2018-07-11 00:30 | 415 | 413
2018-07-11 01:00 | 392 | 387
2018-07-11 01:30 | 381 | 375
2018-07-11 02:00 | 361 | 354
2018-07-11 02:30 | 356 | 349
2018-07-11 03:00 | 352 | 345
2018-07-11 03:30 | 351 | 344
2018-07-11 04:00 | 353 | 346
2018-07-11 04:30 | 364 | 357
2018-07-11 05:00 | 371 | 366
2018-07-11 05:30 | 398 | 395
2018-07-11 06:00 | 435 | 434
2018-07-11 06:30 | 503 | 503
2018-07-11 07:00 | 565 | 563
2018-07-11 07:30 | 598 | 598
2018-07-11 08:00 | 607 | 606
2018-07-11 08:30 | 601 | 600
2018-07-11 09:00 | 575 | 575
2018-07-11 09:30 | 559 | 558
2018-07-11 10:00 | 531 | 530
2018-07-11 10:30 | 506 | 505
2018-07-11 11:00 | 489 | 488
2018-07-11 11:30 | 492 | 491
2018-07-11 12:00 | 470 | 469
2018-07-11 12:30 | 474 | 474
2018-07-11 13:00 | 484 | 484
2018-07-11 13:30 | 489 | 489
2018-07-11 14:00 | 496 | 496
2018-07-11 14:30 | 518 | 518
2018-07-11 15:00 | 524 | 524
2018-07-11 15:30 | 532 | 532
2018-07-11 16:00 | 545 | 545
2018-07-11 16:30 | 563 | 562
2018-07-11 17:00 | 589 | 588
2018-07-11 17:30 | 633 | 631
2018-07-11 18:00 | 670 | 664
2018-07-11 18:30 | 666 | 660
2018-07-11 19:00 | 642 | 637
2018-07-11 19:30 | 624 | 619
2018-07-11 20:00 | 623 | 618
2018-07-11 20:30 | 617 | 612
2018-07-11 21:00 | 597 | 592
2018-07-11 21:30 | 577 | 571
2018-07-11 22:00 | 546 | 544
2018-07-11 22:30 | 536 | 535
2018-07-11 23:00 | 515 | 513
2018-07-11 23:30 | 499 | 497
2018-07-12 | 475 | 472
2018-07-12 00:30 | 431 | 428
2018-07-12 01:00 | 396 | 392
2018-07-12 01:30 | 376 | 371
2018-07-12 02:00 | 362 | 355
2018-07-12 02:30 | 358 | 351
2018-07-12 03:00 | 356 | 349
2018-07-12 03:30 | 354 | 347
2018-07-12 04:00 | 354 | 347
2018-07-12 04:30 | 357 | 351
2018-07-12 05:00 | 365 | 359
2018-07-12 05:30 | 390 | 386
2018-07-12 06:00 | 425 | 422
2018-07-12 06:30 | 486 | 482
2018-07-12 07:00 | 561 | 550
2018-07-12 07:30 | 601 | 590
2018-07-12 08:00 | 625 | 614
2018-07-12 08:30 | 658 | 648
2018-07-12 09:00 | 644 | 637
2018-07-12 09:30 | 634 | 627
2018-07-12 10:00 | 603 | 594
2018-07-12 10:30 | 549 | 545
2018-07-12 11:00 | 519 | 517
2018-07-12 11:30 | 498 | 495
2018-07-12 12:00 | 491 | 490
2018-07-12 12:30 | 487 | 487
2018-07-12 13:00 | 498 | 498
2018-07-12 13:30 | 502 | 502
2018-07-12 14:00 | 504 | 504
2018-07-12 14:30 | 509 | 509
2018-07-12 15:00 | 510 | 510
2018-07-12 15:30 | 504 | 504
2018-07-12 16:00 | 524 | 524
2018-07-12 16:30 | 555 | 555
2018-07-12 17:00 | 587 | 587
2018-07-12 17:30 | 611 | 610
2018-07-12 18:00 | 655 | 651
2018-07-12 18:30 | 659 | 653
2018-07-12 19:00 | 645 | 639
2018-07-12 19:30 | 637 | 631
2018-07-12 20:00 | 651 | 644
2018-07-12 20:30 | 655 | 648
2018-07-12 21:00 | 631 | 630
2018-07-12 21:30 | 610 | 607
2018-07-12 22:00 | 577 | 573
2018-07-12 22:30 | 571 | 567
2018-07-12 23:00 | 560 | 556
2018-07-12 23:30 | 535 | 531
2018-07-13 | 512 | 507
2018-07-13 00:30 | 457 | 452
2018-07-13 01:00 | 419 | 412
2018-07-13 01:30 | 392 | 384
2018-07-13 02:00 | 376 | 367
2018-07-13 02:30 | 371 | 362
2018-07-13 03:00 | 370 | 360
2018-07-13 03:30 | 364 | 354
2018-07-13 04:00 | 363 | 354
2018-07-13 04:30 | 365 | 357
2018-07-13 05:00 | 370 | 363
2018-07-13 05:30 | 390 | 386
2018-07-13 06:00 | 424 | 419
2018-07-13 06:30 | 492 | 489
2018-07-13 07:00 | 554 | 551
2018-07-13 07:30 | 588 | 586
2018-07-13 08:00 | 615 | 612
2018-07-13 08:30 | 610 | 607
2018-07-13 09:00 | 593 | 590
2018-07-13 09:30 | 566 | 561
2018-07-13 10:00 | 539 | 533
2018-07-13 10:30 | 509 | 504
2018-07-13 11:00 | 491 | 486
2018-07-13 11:30 | 459 | 456
2018-07-13 12:00 | 433 | 432
2018-07-13 12:30 | 430 | 428
2018-07-13 13:00 | 420 | 418
2018-07-13 13:30 | 420 | 419
2018-07-13 14:00 | 426 | 424
2018-07-13 14:30 | 427 | 426
2018-07-13 15:00 | 433 | 432
2018-07-13 15:30 | 439 | 438
2018-07-13 16:00 | 459 | 458
2018-07-13 16:30 | 488 | 488
2018-07-13 17:00 | 520 | 519
2018-07-13 17:30 | 559 | 553
2018-07-13 18:00 | 600 | 593
2018-07-13 18:30 | 611 | 605
2018-07-13 19:00 | 647 | 641
2018-07-13 19:30 | 632 | 624
2018-07-13 20:00 | 630 | 622
2018-07-13 20:30 | 634 | 626
2018-07-13 21:00 | 637 | 629
2018-07-13 21:30 | 619 | 616
2018-07-13 22:00 | 601 | 596
2018-07-13 22:30 | 598 | 593
2018-07-13 23:00 | 582 | 577
2018-07-13 23:30 | 548 | 542
2018-07-14 | 509 | 505
2018-07-14 00:30 | 467 | 461
2018-07-14 01:00 | 445 | 439
2018-07-14 01:30 | 417 | 409
2018-07-14 02:00 | 396 | 388
2018-07-14 02:30 | 378 | 369
2018-07-14 03:00 | 371 | 362
2018-07-14 03:30 | 374 | 364
2018-07-14 04:00 | 372 | 362
2018-07-14 04:30 | 370 | 361
2018-07-14 05:00 | 368 | 359
2018-07-14 05:30 | 375 | 367
2018-07-14 06:00 | 391 | 385
2018-07-14 06:30 | 420 | 416
2018-07-14 07:00 | 462 | 458
2018-07-14 07:30 | 503 | 500
2018-07-14 08:00 | 535 | 533
2018-07-14 08:30 | 556 | 555
2018-07-14 09:00 | 560 | 557
2018-07-14 09:30 | 539 | 536
2018-07-14 10:00 | 513 | 510
2018-07-14 10:30 | 472 | 469
2018-07-14 11:00 | 435 | 432
2018-07-14 11:30 | 402 | 399
2018-07-14 12:00 | 377 | 373
2018-07-14 12:30 | 371 | 367
2018-07-14 13:00 | 372 | 368
2018-07-14 13:30 | 371 | 367
2018-07-14 14:00 | 372 | 368
2018-07-14 14:30 | 395 | 391
2018-07-14 15:00 | 401 | 397
2018-07-14 15:30 | 409 | 406
2018-07-14 16:00 | 424 | 421
2018-07-14 16:30 | 455 | 453
2018-07-14 17:00 | 518 | 514
2018-07-14 17:30 | 578 | 570
2018-07-14 18:00 | 610 | 603
2018-07-14 18:30 | 622 | 616
2018-07-14 19:00 | 621 | 616
2018-07-14 19:30 | 612 | 606
2018-07-14 20:00 | 610 | 604
2018-07-14 20:30 | 612 | 606
2018-07-14 21:00 | 598 | 593
2018-07-14 21:30 | 571 | 566
2018-07-14 22:00 | 554 | 549
2018-07-14 22:30 | 530 | 529
2018-07-14 23:00 | 521 | 520
2018-07-14 23:30 | 506 | 504
2018-07-15 | 493 | 490
2018-07-15 00:30 | 444 | 439
2018-07-15 01:00 | 411 | 404
2018-07-15 01:30 | 385 | 377
2018-07-15 02:00 | 370 | 361
2018-07-15 02:30 | 352 | 344
2018-07-15 03:00 | 347 | 339
2018-07-15 03:30 | 346 | 338
2018-07-15 04:00 | 345 | 337
2018-07-15 04:30 | 349 | 342
2018-07-15 05:00 | 354 | 347
2018-07-15 05:30 | 360 | 354
2018-07-15 06:00 | 380 | 374
2018-07-15 06:30 | 399 | 394
2018-07-15 07:00 | 426 | 422
2018-07-15 07:30 | 458 | 456
2018-07-15 08:00 | 484 | 480
2018-07-15 08:30 | 507 | 501
2018-07-15 09:00 | 511 | 505
2018-07-15 09:30 | 505 | 499
2018-07-15 10:00 | 485 | 477
2018-07-15 10:30 | 455 | 446
2018-07-15 11:00 | 417 | 410
2018-07-15 11:30 | 397 | 390
2018-07-15 12:00 | 384 | 378
2018-07-15 12:30 | 358 | 351
2018-07-15 13:00 | 351 | 344
2018-07-15 13:30 | 349 | 343
2018-07-15 14:00 | 350 | 344
2018-07-15 14:30 | 351 | 346
2018-07-15 15:00 | 375 | 370
2018-07-15 15:30 | 390 | 386
2018-07-15 16:00 | 408 | 405
2018-07-15 16:30 | 448 | 445
2018-07-15 17:00 | 498 | 495
2018-07-15 17:30 | 546 | 544
2018-07-15 18:00 | 601 | 599
2018-07-15 18:30 | 626 | 623
2018-07-15 19:00 | 631 | 629
2018-07-15 19:30 | 618 | 616
2018-07-15 20:00 | 617 | 615
2018-07-15 20:30 | 605 | 603
2018-07-15 21:00 | 588 | 586
2018-07-15 21:30 | 576 | 574
2018-07-15 22:00 | 555 | 551
2018-07-15 22:30 | 528 | 523
2018-07-15 23:00 | 502 | 497
2018-07-15 23:30 | 482 | 476
2018-07-16 | 457 | 451
2018-07-16 00:30 | 416 | 408
2018-07-16 01:00 | 395 | 388
2018-07-16 01:30 | 377 | 371
2018-07-16 02:00 | 365 | 358
2018-07-16 02:30 | 360 | 353
2018-07-16 03:00 | 352 | 345
2018-07-16 03:30 | 354 | 347
2018-07-16 04:00 | 356 | 349
2018-07-16 04:30 | 368 | 362
2018-07-16 05:00 | 381 | 376
2018-07-16 05:30 | 405 | 402
2018-07-16 06:00 | 447 | 446
2018-07-16 06:30 | 531 | 528
2018-07-16 07:00 | 609 | 606
2018-07-16 07:30 | 661 | 656
2018-07-16 08:00 | 669 | 661
2018-07-16 08:30 | 659 | 648
2018-07-16 09:00 | 634 | 619
2018-07-16 09:30 | 536 | 524
2018-07-16 10:00 | 503 | 499
2018-07-16 10:30 | 476 | 471
2018-07-16 11:00 | 494 | 487
2018-07-16 11:30 | 498 | 494
2018-07-16 12:00 | 488 | 484
2018-07-16 12:30 | 480 | 476
2018-07-16 13:00 | 475 | 472
2018-07-16 13:30 | 475 | 472
2018-07-16 14:00 | 482 | 479
2018-07-16 14:30 | 497 | 494
2018-07-16 15:00 | 506 | 504
2018-07-16 15:30 | 509 | 507
2018-07-16 16:00 | 532 | 531
2018-07-16 16:30 | 567 | 565
2018-07-16 17:00 | 609 | 607
2018-07-16 17:30 | 642 | 640
2018-07-16 18:00 | 681 | 676
2018-07-16 18:30 | 676 | 664
2018-07-16 19:00 | 681 | 670
2018-07-16 19:30 | 674 | 663
2018-07-16 20:00 | 666 | 658
2018-07-16 20:30 | 657 | 648
2018-07-16 21:00 | 628 | 624
2018-07-16 21:30 | 606 | 602
2018-07-16 22:00 | 584 | 580
2018-07-16 22:30 | 561 | 556
2018-07-16 23:00 | 531 | 526
2018-07-16 23:30 | 503 | 497
2018-07-17 | 473 | 468
2018-07-17 00:30 | 436 | 430
2018-07-17 01:00 | 413 | 406
2018-07-17 01:30 | 395 | 386
2018-07-17 02:00 | 377 | 367
2018-07-17 02:30 | 369 | 358
2018-07-17 03:00 | 360 | 348
2018-07-17 03:30 | 359 | 347
2018-07-17 04:00 | 363 | 351
2018-07-17 04:30 | 367 | 358
2018-07-17 05:00 | 380 | 372
2018-07-17 05:30 | 409 | 406
2018-07-17 06:00 | 451 | 449
2018-07-17 06:30 | 532 | 529
2018-07-17 07:00 | 613 | 607
2018-07-17 07:30 | 660 | 651
2018-07-17 08:00 | 662 | 653
2018-07-17 08:30 | 646 | 635
2018-07-17 09:00 | 628 | 618
2018-07-17 09:30 | 578 | 571
2018-07-17 10:00 | 524 | 523
2018-07-17 10:30 | 493 | 493
2018-07-17 11:00 | 480 | 480
2018-07-17 11:30 | 461 | 461
2018-07-17 12:00 | 454 | 454
2018-07-17 12:30 | 432 | 432
2018-07-17 13:00 | 433 | 433
2018-07-17 13:30 | 430 | 430
2018-07-17 14:00 | 435 | 435
2018-07-17 14:30 | 442 | 442
2018-07-17 15:00 | 458 | 458
2018-07-17 15:30 | 463 | 463
2018-07-17 16:00 | 482 | 481
2018-07-17 16:30 | 512 | 512
2018-07-17 17:00 | 563 | 562
2018-07-17 17:30 | 611 | 607
2018-07-17 18:00 | 648 | 639
2018-07-17 18:30 | 650 | 640
2018-07-17 19:00 | 657 | 647
2018-07-17 19:30 | 652 | 643
2018-07-17 20:00 | 653 | 643
2018-07-17 20:30 | 639 | 629
2018-07-17 21:00 | 606 | 603
2018-07-17 21:30 | 579 | 576
2018-07-17 22:00 | 558 | 553
2018-07-17 22:30 | 545 | 538
2018-07-17 23:00 | 521 | 514
2018-07-17 23:30 | 508 | 499
2018-07-18 | 475 | 471
2018-07-18 00:30 | 426 | 421
2018-07-18 01:00 | 407 | 399
2018-07-18 01:30 | 391 | 381
2018-07-18 02:00 | 374 | 364
2018-07-18 02:30 | 361 | 350
2018-07-18 03:00 | 351 | 340
2018-07-18 03:30 | 344 | 333
2018-07-18 04:00 | 342 | 331
2018-07-18 04:30 | 345 | 336
2018-07-18 05:00 | 360 | 353
2018-07-18 05:30 | 400 | 396
2018-07-18 06:00 | 452 | 449
2018-07-18 06:30 | 540 | 534
2018-07-18 07:00 | 628 | 623
2018-07-18 07:30 | 673 | 669
2018-07-18 08:00 | 681 | 675
2018-07-18 08:30 | 651 | 644
2018-07-18 09:00 | 620 | 612
2018-07-18 09:30 | 585 | 582
2018-07-18 10:00 | 548 | 545
2018-07-18 10:30 | 513 | 511
2018-07-18 11:00 | 489 | 487
2018-07-18 11:30 | 468 | 467
2018-07-18 12:00 | 445 | 444
2018-07-18 12:30 | 434 | 433
2018-07-18 13:00 | 435 | 435
2018-07-18 13:30 | 448 | 448
2018-07-18 14:00 | 444 | 444
2018-07-18 14:30 | 450 | 450
2018-07-18 15:00 | 450 | 449
2018-07-18 15:30 | 449 | 449
2018-07-18 16:00 | 488 | 488
2018-07-18 16:30 | 522 | 521
2018-07-18 17:00 | 568 | 566
2018-07-18 17:30 | 616 | 610
2018-07-18 18:00 | 646 | 641
2018-07-18 18:30 | 646 | 640
2018-07-18 19:00 | 659 | 653
2018-07-18 19:30 | 660 | 654
2018-07-18 20:00 | 657 | 651
2018-07-18 20:30 | 645 | 639
2018-07-18 21:00 | 631 | 626
2018-07-18 21:30 | 609 | 604
2018-07-18 22:00 | 577 | 575
2018-07-18 22:30 | 552 | 549
2018-07-18 23:00 | 524 | 522
2018-07-18 23:30 | 505 | 502
2018-07-19 | 488 | 485
2018-07-19 00:30 | 434 | 428
2018-07-19 01:00 | 406 | 398
2018-07-19 01:30 | 379 | 371
2018-07-19 02:00 | 369 | 360
2018-07-19 02:30 | 361 | 352
2018-07-19 03:00 | 358 | 349
2018-07-19 03:30 | 354 | 344
2018-07-19 04:00 | 354 | 345
2018-07-19 04:30 | 363 | 355
2018-07-19 05:00 | 375 | 369
2018-07-19 05:30 | 408 | 405
2018-07-19 06:00 | 459 | 456
2018-07-19 06:30 | 546 | 542
2018-07-19 07:00 | 639 | 633
2018-07-19 07:30 | 681 | 675
2018-07-19 08:00 | 695 | 686
2018-07-19 08:30 | 682 | 672
2018-07-19 09:00 | 598 | 584
2018-07-19 09:30 | 555 | 540
2018-07-19 10:00 | 518 | 513
2018-07-19 10:30 | 486 | 482
2018-07-19 11:00 | 466 | 463
2018-07-19 11:30 | 474 | 472
2018-07-19 12:00 | 471 | 469
2018-07-19 12:30 | 455 | 452
2018-07-19 13:00 | 455 | 452
2018-07-19 13:30 | 467 | 464
2018-07-19 14:00 | 461 | 458
2018-07-19 14:30 | 457 | 455
2018-07-19 15:00 | 474 | 472
2018-07-19 15:30 | 493 | 490
2018-07-19 16:00 | 509 | 507
2018-07-19 16:30 | 554 | 551
2018-07-19 17:00 | 614 | 604
2018-07-19 17:30 | 660 | 648
2018-07-19 18:00 | 681 | 671
2018-07-19 18:30 | 700 | 684
2018-07-19 19:00 | 699 | 683
2018-07-19 19:30 | 687 | 673
2018-07-19 20:00 | 680 | 666
2018-07-19 20:30 | 679 | 665
2018-07-19 21:00 | 659 | 642
2018-07-19 21:30 | 647 | 627
2018-07-19 22:00 | 620 | 601
2018-07-19 22:30 | 588 | 569
2018-07-19 23:00 | 566 | 547
2018-07-19 23:30 | 541 | 521
2018-07-20 | 516 | 501
2018-07-20 00:30 | 464 | 455
2018-07-20 01:00 | 435 | 423
2018-07-20 01:30 | 407 | 394
2018-07-20 02:00 | 383 | 369
2018-07-20 02:30 | 370 | 355
2018-07-20 03:00 | 363 | 347
2018-07-20 03:30 | 358 | 343
2018-07-20 04:00 | 364 | 349
2018-07-20 04:30 | 368 | 353
2018-07-20 05:00 | 387 | 375
2018-07-20 05:30 | 420 | 409
2018-07-20 06:00 | 447 | 438
2018-07-20 06:30 | 509 | 503
2018-07-20 07:00 | 582 | 578
2018-07-20 07:30 | 644 | 633
2018-07-20 08:00 | 649 | 635
2018-07-20 08:30 | 573 | 557
2018-07-20 09:00 | 535 | 525
2018-07-20 09:30 | 506 | 500
2018-07-20 10:00 | 490 | 485
2018-07-20 10:30 | 526 | 523
2018-07-20 11:00 | 501 | 497
2018-07-20 11:30 | 473 | 471
2018-07-20 12:00 | 477 | 476
2018-07-20 12:30 | 491 | 490
2018-07-20 13:00 | 506 | 505
2018-07-20 13:30 | 481 | 480
2018-07-20 14:00 | 500 | 500
2018-07-20 14:30 | 527 | 527
2018-07-20 15:00 | 518 | 518
2018-07-20 15:30 | 502 | 501
2018-07-20 16:00 | 514 | 513
2018-07-20 16:30 | 536 | 535
2018-07-20 17:00 | 578 | 577
2018-07-20 17:30 | 618 | 612
2018-07-20 18:00 | 647 | 638
2018-07-20 18:30 | 641 | 630
2018-07-20 19:00 | 634 | 623
2018-07-20 19:30 | 611 | 608
2018-07-20 20:00 | 616 | 614
2018-07-20 20:30 | 619 | 616
2018-07-20 21:00 | 609 | 605
2018-07-20 21:30 | 586 | 581
2018-07-20 22:00 | 561 | 558
2018-07-20 22:30 | 553 | 550
2018-07-20 23:00 | 547 | 543
2018-07-20 23:30 | 523 | 520
2018-07-21 | 496 | 494
2018-07-21 00:30 | 452 | 448
2018-07-21 01:00 | 423 | 417
2018-07-21 01:30 | 400 | 393
2018-07-21 02:00 | 383 | 375
2018-07-21 02:30 | 374 | 365
2018-07-21 03:00 | 365 | 356
2018-07-21 03:30 | 366 | 357
2018-07-21 04:00 | 362 | 353
2018-07-21 04:30 | 365 | 357
2018-07-21 05:00 | 369 | 361
2018-07-21 05:30 | 381 | 374
2018-07-21 06:00 | 396 | 390
2018-07-21 06:30 | 426 | 422
2018-07-21 07:00 | 465 | 462
2018-07-21 07:30 | 506 | 502
2018-07-21 08:00 | 518 | 515
2018-07-21 08:30 | 525 | 522
2018-07-21 09:00 | 529 | 526
2018-07-21 09:30 | 517 | 513
2018-07-21 10:00 | 488 | 483
2018-07-21 10:30 | 462 | 459
2018-07-21 11:00 | 440 | 437
2018-07-21 11:30 | 418 | 414
2018-07-21 12:00 | 402 | 397
2018-07-21 12:30 | 389 | 384
2018-07-21 13:00 | 382 | 376
2018-07-21 13:30 | 382 | 376
2018-07-21 14:00 | 403 | 397
2018-07-21 14:30 | 416 | 411
2018-07-21 15:00 | 424 | 419
2018-07-21 15:30 | 434 | 430
2018-07-21 16:00 | 450 | 446
2018-07-21 16:30 | 492 | 489
2018-07-21 17:00 | 538 | 536
2018-07-21 17:30 | 584 | 578
2018-07-21 18:00 | 625 | 615
2018-07-21 18:30 | 631 | 621
2018-07-21 19:00 | 634 | 624
2018-07-21 19:30 | 614 | 607
2018-07-21 20:00 | 617 | 610
2018-07-21 20:30 | 622 | 616
2018-07-21 21:00 | 607 | 599
2018-07-21 21:30 | 590 | 585
2018-07-21 22:00 | 584 | 578
2018-07-21 22:30 | 571 | 565
2018-07-21 23:00 | 557 | 550
2018-07-21 23:30 | 537 | 533
2018-07-22 | 510 | 508
2018-07-22 00:30 | 458 | 455
2018-07-22 01:00 | 430 | 426
2018-07-22 01:30 | 412 | 406
2018-07-22 02:00 | 396 | 389
2018-07-22 02:30 | 388 | 380
2018-07-22 03:00 | 386 | 377
2018-07-22 03:30 | 382 | 374
2018-07-22 04:00 | 383 | 374
2018-07-22 04:30 | 384 | 374
2018-07-22 05:00 | 385 | 376
2018-07-22 05:30 | 387 | 379
2018-07-22 06:00 | 394 | 386
2018-07-22 06:30 | 412 | 406
2018-07-22 07:00 | 444 | 438
2018-07-22 07:30 | 467 | 462
2018-07-22 08:00 | 495 | 489
2018-07-22 08:30 | 513 | 507
2018-07-22 09:00 | 512 | 507
2018-07-22 09:30 | 509 | 503
2018-07-22 10:00 | 489 | 482
2018-07-22 10:30 | 458 | 452
2018-07-22 11:00 | 415 | 409
2018-07-22 11:30 | 398 | 392
2018-07-22 12:00 | 397 | 391
2018-07-22 12:30 | 401 | 395
2018-07-22 13:00 | 399 | 393
2018-07-22 13:30 | 394 | 388
2018-07-22 14:00 | 394 | 388
2018-07-22 14:30 | 407 | 401
2018-07-22 15:00 | 420 | 415
2018-07-22 15:30 | 435 | 430
2018-07-22 16:00 | 448 | 443
2018-07-22 16:30 | 478 | 475
2018-07-22 17:00 | 528 | 525
2018-07-22 17:30 | 571 | 567
2018-07-22 18:00 | 603 | 601
2018-07-22 18:30 | 617 | 614
2018-07-22 19:00 | 616 | 614
2018-07-22 19:30 | 606 | 604
2018-07-22 20:00 | 608 | 607
2018-07-22 20:30 | 612 | 611
2018-07-22 21:00 | 595 | 594
2018-07-22 21:30 | 578 | 577
2018-07-22 22:00 | 553 | 552
2018-07-22 22:30 | 526 | 525
2018-07-22 23:00 | 507 | 506
2018-07-22 23:30 | 490 | 488
2018-07-23 | 461 | 458
2018-07-23 00:30 | 420 | 416
2018-07-23 01:00 | 407 | 402
2018-07-23 01:30 | 395 | 388
2018-07-23 02:00 | 378 | 371
2018-07-23 02:30 | 368 | 360
2018-07-23 03:00 | 365 | 357
2018-07-23 03:30 | 365 | 356
2018-07-23 04:00 | 365 | 358
2018-07-23 04:30 | 372 | 365
2018-07-23 05:00 | 386 | 381
2018-07-23 05:30 | 416 | 414
2018-07-23 06:00 | 469 | 466
2018-07-23 06:30 | 551 | 550
2018-07-23 07:00 | 626 | 625
2018-07-23 07:30 | 666 | 665
2018-07-23 08:00 | 667 | 665
2018-07-23 08:30 | 643 | 641
2018-07-23 09:00 | 606 | 603
2018-07-23 09:30 | 571 | 569
2018-07-23 10:00 | 536 | 535
2018-07-23 10:30 | 512 | 511
2018-07-23 11:00 | 496 | 496
2018-07-23 11:30 | 483 | 482
2018-07-23 12:00 | 466 | 465
2018-07-23 12:30 | 466 | 465
2018-07-23 13:00 | 464 | 464
2018-07-23 13:30 | 465 | 465
2018-07-23 14:00 | 471 | 471
2018-07-23 14:30 | 475 | 475
2018-07-23 15:00 | 484 | 484
2018-07-23 15:30 | 491 | 491
2018-07-23 16:00 | 506 | 506
2018-07-23 16:30 | 546 | 546
2018-07-23 17:00 | 596 | 594
2018-07-23 17:30 | 643 | 641
2018-07-23 18:00 | 670 | 668
2018-07-23 18:30 | 668 | 666
2018-07-23 19:00 | 674 | 672
2018-07-23 19:30 | 662 | 660
2018-07-23 20:00 | 663 | 661
2018-07-23 20:30 | 661 | 660
2018-07-23 21:00 | 636 | 634
2018-07-23 21:30 | 607 | 606
2018-07-23 22:00 | 581 | 579
2018-07-23 22:30 | 562 | 560
2018-07-23 23:00 | 537 | 535
2018-07-23 23:30 | 504 | 502
2018-07-24 | 476 | 474
2018-07-24 00:30 | 429 | 426
2018-07-24 01:00 | 403 | 399
2018-07-24 01:30 | 383 | 377
2018-07-24 02:00 | 368 | 362
2018-07-24 02:30 | 360 | 353
2018-07-24 03:00 | 358 | 351
2018-07-24 03:30 | 359 | 351
2018-07-24 04:00 | 358 | 351
2018-07-24 04:30 | 361 | 355
2018-07-24 05:00 | 369 | 365
2018-07-24 05:30 | 402 | 400
2018-07-24 06:00 | 451 | 450
2018-07-24 06:30 | 530 | 528
2018-07-24 07:00 | 603 | 601
2018-07-24 07:30 | 649 | 648
2018-07-24 08:00 | 641 | 638
2018-07-24 08:30 | 612 | 610
2018-07-24 09:00 | 576 | 573
2018-07-24 09:30 | 550 | 545
2018-07-24 10:00 | 515 | 513
2018-07-24 10:30 | 485 | 484
2018-07-24 11:00 | 463 | 463
2018-07-24 11:30 | 448 | 447
2018-07-24 12:00 | 428 | 427
2018-07-24 12:30 | 424 | 423
2018-07-24 13:00 | 420 | 419
2018-07-24 13:30 | 425 | 423
2018-07-24 14:00 | 432 | 431
2018-07-24 14:30 | 437 | 436
2018-07-24 15:00 | 451 | 450
2018-07-24 15:30 | 469 | 468
2018-07-24 16:00 | 498 | 496
2018-07-24 16:30 | 526 | 524
2018-07-24 17:00 | 554 | 551
2018-07-24 17:30 | 581 | 578
2018-07-24 18:00 | 625 | 611
2018-07-24 18:30 | 625 | 610
2018-07-24 19:00 | 624 | 609
2018-07-24 19:30 | 612 | 606
2018-07-24 20:00 | 606 | 600
2018-07-24 20:30 | 598 | 594
2018-07-24 21:00 | 576 | 573
2018-07-24 21:30 | 548 | 543
2018-07-24 22:00 | 527 | 523
2018-07-24 22:30 | 510 | 505
2018-07-24 23:00 | 485 | 479
2018-07-24 23:30 | 463 | 458
2018-07-25 | 436 | 429
2018-07-25 00:30 | 401 | 392
2018-07-25 01:00 | 383 | 372
2018-07-25 01:30 | 370 | 355
2018-07-25 02:00 | 357 | 342
2018-07-25 02:30 | 352 | 336
2018-07-25 03:00 | 350 | 333
2018-07-25 03:30 | 349 | 333
2018-07-25 04:00 | 351 | 334
2018-07-25 04:30 | 350 | 335
2018-07-25 05:00 | 363 | 351
2018-07-25 05:30 | 389 | 381
2018-07-25 06:00 | 432 | 423
2018-07-25 06:30 | 508 | 501
2018-07-25 07:00 | 576 | 571
2018-07-25 07:30 | 617 | 613
2018-07-25 08:00 | 631 | 626
2018-07-25 08:30 | 628 | 623
2018-07-25 09:00 | 613 | 609
2018-07-25 09:30 | 605 | 601
2018-07-25 10:00 | 589 | 585
2018-07-25 10:30 | 557 | 554
2018-07-25 11:00 | 516 | 514
2018-07-25 11:30 | 487 | 484
2018-07-25 12:00 | 472 | 468
2018-07-25 12:30 | 466 | 460
2018-07-25 13:00 | 466 | 461
2018-07-25 13:30 | 475 | 473
2018-07-25 14:00 | 490 | 488
2018-07-25 14:30 | 489 | 487
2018-07-25 15:00 | 496 | 494
2018-07-25 15:30 | 496 | 494
2018-07-25 16:00 | 514 | 512
2018-07-25 16:30 | 544 | 540
2018-07-25 17:00 | 582 | 578
2018-07-25 17:30 | 618 | 611
2018-07-25 18:00 | 647 | 638
2018-07-25 18:30 | 643 | 631
2018-07-25 19:00 | 639 | 630
2018-07-25 19:30 | 632 | 622
2018-07-25 20:00 | 628 | 618
2018-07-25 20:30 | 611 | 604
2018-07-25 21:00 | 593 | 590
2018-07-25 21:30 | 565 | 560
2018-07-25 22:00 | 537 | 534
2018-07-25 22:30 | 526 | 522
2018-07-25 23:00 | 502 | 497
2018-07-25 23:30 | 470 | 464
2018-07-26 | 447 | 439
2018-07-26 00:30 | 411 | 402
2018-07-26 01:00 | 389 | 378
2018-07-26 01:30 | 369 | 356
2018-07-26 02:00 | 356 | 342
2018-07-26 02:30 | 348 | 335
2018-07-26 03:00 | 346 | 333
2018-07-26 03:30 | 344 | 331
2018-07-26 04:00 | 346 | 333
2018-07-26 04:30 | 348 | 336
2018-07-26 05:00 | 359 | 348
2018-07-26 05:30 | 379 | 372
2018-07-26 06:00 | 406 | 402
2018-07-26 06:30 | 474 | 471
2018-07-26 07:00 | 539 | 537
2018-07-26 07:30 | 584 | 583
2018-07-26 08:00 | 591 | 588
2018-07-26 08:30 | 577 | 574
2018-07-26 09:00 | 480 | 478
2018-07-26 09:30 | 457 | 456
2018-07-26 10:00 | 444 | 443
2018-07-26 10:30 | 427 | 426
2018-07-26 11:00 | 477 | 474
2018-07-26 11:30 | 457 | 454
2018-07-26 12:00 | 449 | 446
2018-07-26 12:30 | 444 | 441
2018-07-26 13:00 | 440 | 438
2018-07-26 13:30 | 444 | 442
2018-07-26 14:00 | 452 | 450
2018-07-26 14:30 | 457 | 455
2018-07-26 15:00 | 464 | 461
2018-07-26 15:30 | 481 | 478
2018-07-26 16:00 | 494 | 491
2018-07-26 16:30 | 519 | 515
2018-07-26 17:00 | 546 | 542
2018-07-26 17:30 | 581 | 577
2018-07-26 18:00 | 628 | 623
2018-07-26 18:30 | 651 | 637
2018-07-26 19:00 | 644 | 631
2018-07-26 19:30 | 621 | 607
2018-07-26 20:00 | 620 | 606
2018-07-26 20:30 | 619 | 611
2018-07-26 21:00 | 587 | 582
2018-07-26 21:30 | 566 | 558
2018-07-26 22:00 | 539 | 532
2018-07-26 22:30 | 531 | 524
2018-07-26 23:00 | 513 | 505
2018-07-26 23:30 | 492 | 484
2018-07-27 | 460 | 452
2018-07-27 00:30 | 409 | 401
2018-07-27 01:00 | 379 | 369
2018-07-27 01:30 | 359 | 347
2018-07-27 02:00 | 335 | 322
2018-07-27 02:30 | 319 | 304
2018-07-27 03:00 | 318 | 304
2018-07-27 03:30 | 326 | 312
2018-07-27 04:00 | 338 | 325
2018-07-27 04:30 | 333 | 321
2018-07-27 05:00 | 344 | 333
2018-07-27 05:30 | 373 | 366
2018-07-27 06:00 | 405 | 399
2018-07-27 06:30 | 469 | 463
2018-07-27 07:00 | 526 | 520
2018-07-27 07:30 | 574 | 567
2018-07-27 08:00 | 580 | 573
2018-07-27 08:30 | 504 | 498
2018-07-27 09:00 | 458 | 453
2018-07-27 09:30 | 445 | 440
2018-07-27 10:00 | 429 | 423
2018-07-27 10:30 | 409 | 405
2018-07-27 11:00 | 457 | 452
2018-07-27 11:30 | 459 | 455
2018-07-27 12:00 | 456 | 451
2018-07-27 12:30 | 435 | 432
2018-07-27 13:00 | 440 | 438
2018-07-27 13:30 | 417 | 415
2018-07-27 14:00 | 413 | 411
2018-07-27 14:30 | 426 | 425
2018-07-27 15:00 | 429 | 427
2018-07-27 15:30 | 433 | 431
2018-07-27 16:00 | 466 | 464
2018-07-27 16:30 | 498 | 497
2018-07-27 17:00 | 535 | 528
2018-07-27 17:30 | 547 | 539
2018-07-27 18:00 | 574 | 566
2018-07-27 18:30 | 580 | 569
2018-07-27 19:00 | 579 | 568
2018-07-27 19:30 | 569 | 557
2018-07-27 20:00 | 573 | 560
2018-07-27 20:30 | 562 | 552
2018-07-27 21:00 | 529 | 525
2018-07-27 21:30 | 518 | 512
2018-07-27 22:00 | 506 | 499
2018-07-27 22:30 | 489 | 483
2018-07-27 23:00 | 483 | 476
2018-07-27 23:30 | 460 | 452
2018-07-28 | 441 | 429
2018-07-28 00:30 | 405 | 391
2018-07-28 01:00 | 383 | 367
2018-07-28 01:30 | 365 | 348
2018-07-28 02:00 | 351 | 333
2018-07-28 02:30 | 339 | 320
2018-07-28 03:00 | 334 | 314
2018-07-28 03:30 | 333 | 313
2018-07-28 04:00 | 332 | 309
2018-07-28 04:30 | 330 | 308
2018-07-28 05:00 | 332 | 311
2018-07-28 05:30 | 336 | 316
2018-07-28 06:00 | 348 | 331
2018-07-28 06:30 | 363 | 349
2018-07-28 07:00 | 381 | 367
2018-07-28 07:30 | 387 | 376
2018-07-28 08:00 | 399 | 389
2018-07-28 08:30 | 412 | 402
2018-07-28 09:00 | 413 | 401
2018-07-28 09:30 | 410 | 396
2018-07-28 10:00 | 403 | 389
2018-07-28 10:30 | 392 | 377
2018-07-28 11:00 | 373 | 358
2018-07-28 11:30 | 357 | 341
2018-07-28 12:00 | 342 | 329
2018-07-28 12:30 | 333 | 322
2018-07-28 13:00 | 326 | 314
2018-07-28 13:30 | 327 | 316
2018-07-28 14:00 | 327 | 316
2018-07-28 14:30 | 340 | 330
2018-07-28 15:00 | 346 | 337
2018-07-28 15:30 | 348 | 339
2018-07-28 16:00 | 367 | 358
2018-07-28 16:30 | 391 | 384
2018-07-28 17:00 | 431 | 423
2018-07-28 17:30 | 456 | 449
2018-07-28 18:00 | 473 | 468
2018-07-28 18:30 | 499 | 494
2018-07-28 19:00 | 498 | 494
2018-07-28 19:30 | 487 | 482
2018-07-28 20:00 | 484 | 481
2018-07-28 20:30 | 477 | 474
2018-07-28 21:00 | 459 | 454
2018-07-28 21:30 | 435 | 429
2018-07-28 22:00 | 422 | 416
2018-07-28 22:30 | 404 | 397
2018-07-28 23:00 | 405 | 397
2018-07-28 23:30 | 389 | 379
2018-07-29 | 377 | 366
2018-07-29 00:30 | 355 | 341
2018-07-29 01:00 | 341 | 324
2018-07-29 01:30 | 330 | 312
2018-07-29 02:00 | 316 | 298
2018-07-29 02:30 | 315 | 296
2018-07-29 03:00 | 312 | 293
2018-07-29 03:30 | 302 | 283
2018-07-29 04:00 | 293 | 273
2018-07-29 04:30 | 294 | 274
2018-07-29 05:00 | 293 | 273
2018-07-29 05:30 | 300 | 281
2018-07-29 06:00 | 313 | 295
2018-07-29 06:30 | 340 | 324
2018-07-29 07:00 | 348 | 332
2018-07-29 07:30 | 363 | 348
2018-07-29 08:00 | 374 | 361
2018-07-29 08:30 | 385 | 373
2018-07-29 09:00 | 386 | 375
2018-07-29 09:30 | 380 | 369
2018-07-29 10:00 | 366 | 355
2018-07-29 10:30 | 363 | 351
2018-07-29 11:00 | 357 | 345
2018-07-29 11:30 | 354 | 342
2018-07-29 12:00 | 339 | 326
2018-07-29 12:30 | 313 | 299
2018-07-29 13:00 | 334 | 321
2018-07-29 13:30 | 332 | 319
2018-07-29 14:00 | 349 | 337
2018-07-29 14:30 | 365 | 355
2018-07-29 15:00 | 376 | 367
2018-07-29 15:30 | 383 | 375
2018-07-29 16:00 | 395 | 388
2018-07-29 16:30 | 413 | 405
2018-07-29 17:00 | 437 | 432
2018-07-29 17:30 | 455 | 452
2018-07-29 18:00 | 492 | 490
2018-07-29 18:30 | 492 | 490
2018-07-29 19:00 | 489 | 486
2018-07-29 19:30 | 479 | 476
2018-07-29 20:00 | 473 | 470
2018-07-29 20:30 | 474 | 471
2018-07-29 21:00 | 454 | 450
2018-07-29 21:30 | 437 | 432
2018-07-29 22:00 | 426 | 420
2018-07-29 22:30 | 414 | 408
2018-07-29 23:00 | 407 | 400
2018-07-29 23:30 | 396 | 387
2018-07-30 | 376 | 365
2018-07-30 00:30 | 348 | 333
2018-07-30 01:00 | 339 | 323
2018-07-30 01:30 | 333 | 316
2018-07-30 02:00 | 322 | 301
2018-07-30 02:30 | 317 | 296
2018-07-30 03:00 | 310 | 288
2018-07-30 03:30 | 299 | 277
2018-07-30 04:00 | 299 | 278
2018-07-30 04:30 | 306 | 286
2018-07-30 05:00 | 330 | 313
2018-07-30 05:30 | 363 | 350
2018-07-30 06:00 | 393 | 384
2018-07-30 06:30 | 441 | 434
2018-07-30 07:00 | 496 | 491
2018-07-30 07:30 | 532 | 526
2018-07-30 08:00 | 538 | 532
2018-07-30 08:30 | 495 | 490
2018-07-30 09:00 | 434 | 430
2018-07-30 09:30 | 418 | 413
2018-07-30 10:00 | 403 | 398
2018-07-30 10:30 | 389 | 383
2018-07-30 11:00 | 372 | 370
2018-07-30 11:30 | 404 | 400
2018-07-30 12:00 | 402 | 398
2018-07-30 12:30 | 400 | 396
2018-07-30 13:00 | 404 | 401
2018-07-30 13:30 | 405 | 404
2018-07-30 14:00 | 410 | 409
2018-07-30 14:30 | 416 | 414
2018-07-30 15:00 | 420 | 418
2018-07-30 15:30 | 431 | 430
2018-07-30 16:00 | 450 | 448
2018-07-30 16:30 | 480 | 478
2018-07-30 17:00 | 511 | 507
2018-07-30 17:30 | 547 | 538
2018-07-30 18:00 | 589 | 582
2018-07-30 18:30 | 595 | 587
2018-07-30 19:00 | 596 | 587
2018-07-30 19:30 | 573 | 564
2018-07-30 20:00 | 562 | 553
2018-07-30 20:30 | 556 | 547
2018-07-30 21:00 | 538 | 528
2018-07-30 21:30 | 517 | 505
2018-07-30 22:00 | 498 | 486
2018-07-30 22:30 | 480 | 471
2018-07-30 23:00 | 463 | 458
2018-07-30 23:30 | 445 | 438
2018-07-31 | 417 | 408
2018-07-31 00:30 | 392 | 379
2018-07-31 01:00 | 374 | 359
2018-07-31 01:30 | 362 | 344
2018-07-31 02:00 | 349 | 330
2018-07-31 02:30 | 341 | 323
2018-07-31 03:00 | 338 | 320
2018-07-31 03:30 | 340 | 322
2018-07-31 04:00 | 344 | 326
2018-07-31 04:30 | 350 | 333
2018-07-31 05:00 | 363 | 348
2018-07-31 05:30 | 388 | 379
2018-07-31 06:00 | 434 | 426
2018-07-31 06:30 | 497 | 492
2018-07-31 07:00 | 570 | 567
2018-07-31 07:30 | 615 | 613
2018-07-31 08:00 | 596 | 594
2018-07-31 08:30 | 553 | 550
2018-07-31 09:00 | 517 | 514
2018-07-31 09:30 | 493 | 490
2018-07-31 10:00 | 469 | 466
2018-07-31 10:30 | 447 | 445
2018-07-31 11:00 | 434 | 432
2018-07-31 11:30 | 420 | 418
2018-07-31 12:00 | 406 | 403
2018-07-31 12:30 | 394 | 392
2018-07-31 13:00 | 398 | 396
2018-07-31 13:30 | 394 | 391
2018-07-31 14:00 | 400 | 397
2018-07-31 14:30 | 416 | 414
2018-07-31 15:00 | 426 | 424
2018-07-31 15:30 | 433 | 431
2018-07-31 16:00 | 455 | 453
2018-07-31 16:30 | 486 | 484
2018-07-31 17:00 | 517 | 514
2018-07-31 17:30 | 556 | 549
2018-07-31 18:00 | 608 | 602
2018-07-31 18:30 | 626 | 606
2018-07-31 19:00 | 627 | 611
2018-07-31 19:30 | 612 | 595
2018-07-31 20:00 | 614 | 597
2018-07-31 20:30 | 614 | 596
2018-07-31 21:00 | 591 | 575
2018-07-31 21:30 | 554 | 539
2018-07-31 22:00 | 523 | 507
2018-07-31 22:30 | 499 | 485
2018-07-31 23:00 | 483 | 469
2018-07-31 23:30 | 449 | 442
2018-08-01 | 428 | 420
2018-08-01 00:30 | 397 | 387
2018-08-01 01:00 | 378 | 366
2018-08-01 01:30 | 371 | 357
2018-08-01 02:00 | 361 | 346
2018-08-01 02:30 | 353 | 337
2018-08-01 03:00 | 347 | 330
2018-08-01 03:30 | 343 | 325
2018-08-01 04:00 | 343 | 326
2018-08-01 04:30 | 346 | 331
2018-08-01 05:00 | 361 | 348
2018-08-01 05:30 | 414 | 406
2018-08-01 06:00 | 458 | 451
2018-08-01 06:30 | 527 | 522
2018-08-01 07:00 | 596 | 591
2018-08-01 07:30 | 639 | 637
2018-08-01 08:00 | 636 | 632
2018-08-01 08:30 | 590 | 584
2018-08-01 09:00 | 549 | 543
2018-08-01 09:30 | 519 | 514
2018-08-01 10:00 | 485 | 482
2018-08-01 10:30 | 455 | 454
2018-08-01 11:00 | 439 | 438
2018-08-01 11:30 | 431 | 431
2018-08-01 12:00 | 424 | 423
2018-08-01 12:30 | 419 | 418
2018-08-01 13:00 | 418 | 418
2018-08-01 13:30 | 423 | 422
2018-08-01 14:00 | 429 | 428
2018-08-01 14:30 | 438 | 437
2018-08-01 15:00 | 447 | 447
2018-08-01 15:30 | 459 | 459
2018-08-01 16:00 | 478 | 478
2018-08-01 16:30 | 508 | 508
2018-08-01 17:00 | 546 | 545
2018-08-01 17:30 | 580 | 579
2018-08-01 18:00 | 622 | 619
2018-08-01 18:30 | 646 | 638
2018-08-01 19:00 | 658 | 650
2018-08-01 19:30 | 645 | 637
2018-08-01 20:00 | 636 | 629
2018-08-01 20:30 | 621 | 614
2018-08-01 21:00 | 596 | 593
2018-08-01 21:30 | 569 | 566
2018-08-01 22:00 | 551 | 548
2018-08-01 22:30 | 534 | 530
2018-08-01 23:00 | 511 | 508
2018-08-01 23:30 | 486 | 483
2018-08-02 | 461 | 458
2018-08-02 00:30 | 421 | 418
2018-08-02 01:00 | 398 | 394
2018-08-02 01:30 | 383 | 377
2018-08-02 02:00 | 370 | 363
2018-08-02 02:30 | 358 | 351
2018-08-02 03:00 | 342 | 334
2018-08-02 03:30 | 337 | 329
2018-08-02 04:00 | 335 | 327
2018-08-02 04:30 | 344 | 338
2018-08-02 05:00 | 356 | 350
2018-08-02 05:30 | 395 | 392
2018-08-02 06:00 | 434 | 433
2018-08-02 06:30 | 500 | 499
2018-08-02 07:00 | 583 | 579
2018-08-02 07:30 | 621 | 615
2018-08-02 08:00 | 615 | 606
2018-08-02 08:30 | 575 | 565
2018-08-02 09:00 | 530 | 522
2018-08-02 09:30 | 495 | 492
2018-08-02 10:00 | 464 | 463
2018-08-02 10:30 | 438 | 438
2018-08-02 11:00 | 423 | 423
2018-08-02 11:30 | 413 | 412
2018-08-02 12:00 | 401 | 401
2018-08-02 12:30 | 405 | 404
2018-08-02 13:00 | 406 | 406
2018-08-02 13:30 | 409 | 408
2018-08-02 14:00 | 411 | 410
2018-08-02 14:30 | 415 | 415
2018-08-02 15:00 | 425 | 425
2018-08-02 15:30 | 436 | 435
2018-08-02 16:00 | 456 | 456
2018-08-02 16:30 | 486 | 486
2018-08-02 17:00 | 520 | 520
2018-08-02 17:30 | 558 | 557
2018-08-02 18:00 | 594 | 590
2018-08-02 18:30 | 601 | 597
2018-08-02 19:00 | 606 | 602
2018-08-02 19:30 | 603 | 598
2018-08-02 20:00 | 598 | 598
2018-08-02 20:30 | 594 | 593
2018-08-02 21:00 | 574 | 573
2018-08-02 21:30 | 552 | 551
2018-08-02 22:00 | 530 | 527
2018-08-02 22:30 | 514 | 512
2018-08-02 23:00 | 501 | 499
2018-08-02 23:30 | 481 | 478
2018-08-03 | 458 | 453
2018-08-03 00:30 | 422 | 414
2018-08-03 01:00 | 404 | 395
2018-08-03 01:30 | 391 | 379
2018-08-03 02:00 | 377 | 366
2018-08-03 02:30 | 359 | 349
2018-08-03 03:00 | 353 | 342
2018-08-03 03:30 | 353 | 343
2018-08-03 04:00 | 352 | 342
2018-08-03 04:30 | 358 | 348
2018-08-03 05:00 | 368 | 361
2018-08-03 05:30 | 393 | 387
2018-08-03 06:00 | 430 | 426
2018-08-03 06:30 | 487 | 484
2018-08-03 07:00 | 555 | 548
2018-08-03 07:30 | 580 | 574
2018-08-03 08:00 | 586 | 579
2018-08-03 08:30 | 560 | 552
2018-08-03 09:00 | 522 | 515
2018-08-03 09:30 | 489 | 487
2018-08-03 10:00 | 458 | 456
2018-08-03 10:30 | 437 | 436
2018-08-03 11:00 | 423 | 423
2018-08-03 11:30 | 416 | 416
2018-08-03 12:00 | 412 | 411
2018-08-03 12:30 | 408 | 408
2018-08-03 13:00 | 413 | 413
2018-08-03 13:30 | 412 | 412
2018-08-03 14:00 | 413 | 413
2018-08-03 14:30 | 413 | 413
2018-08-03 15:00 | 429 | 429
2018-08-03 15:30 | 454 | 454
2018-08-03 16:00 | 478 | 478
2018-08-03 16:30 | 512 | 512
2018-08-03 17:00 | 542 | 541
2018-08-03 17:30 | 551 | 550
2018-08-03 18:00 | 562 | 561
2018-08-03 18:30 | 559 | 557
2018-08-03 19:00 | 571 | 568
2018-08-03 19:30 | 553 | 550
2018-08-03 20:00 | 547 | 544
2018-08-03 20:30 | 537 | 536
2018-08-03 21:00 | 525 | 524
2018-08-03 21:30 | 508 | 507
2018-08-03 22:00 | 491 | 489
2018-08-03 22:30 | 485 | 482
2018-08-03 23:00 | 466 | 464
2018-08-03 23:30 | 456 | 453
2018-08-04 | 441 | 436
2018-08-04 00:30 | 395 | 389
2018-08-04 01:00 | 377 | 368
2018-08-04 01:30 | 359 | 350
2018-08-04 02:00 | 338 | 327
2018-08-04 02:30 | 333 | 321
2018-08-04 03:00 | 327 | 314
2018-08-04 03:30 | 320 | 308
2018-08-04 04:00 | 319 | 306
2018-08-04 04:30 | 316 | 304
2018-08-04 05:00 | 319 | 308
2018-08-04 05:30 | 329 | 318
2018-08-04 06:00 | 354 | 345
2018-08-04 06:30 | 377 | 369
2018-08-04 07:00 | 393 | 386
2018-08-04 07:30 | 410 | 404
2018-08-04 08:00 | 422 | 417
2018-08-04 08:30 | 431 | 426
2018-08-04 09:00 | 426 | 421
2018-08-04 09:30 | 409 | 405
2018-08-04 10:00 | 393 | 388
2018-08-04 10:30 | 384 | 380
2018-08-04 11:00 | 369 | 364
2018-08-04 11:30 | 360 | 355
2018-08-04 12:00 | 352 | 347
2018-08-04 12:30 | 347 | 341
2018-08-04 13:00 | 345 | 340
2018-08-04 13:30 | 360 | 355
2018-08-04 14:00 | 360 | 355
2018-08-04 14:30 | 369 | 364
2018-08-04 15:00 | 373 | 368
2018-08-04 15:30 | 386 | 381
2018-08-04 16:00 | 403 | 399
2018-08-04 16:30 | 426 | 423
2018-08-04 17:00 | 449 | 446
2018-08-04 17:30 | 463 | 459
2018-08-04 18:00 | 499 | 495
2018-08-04 18:30 | 516 | 511
2018-08-04 19:00 | 515 | 510
2018-08-04 19:30 | 504 | 498
2018-08-04 20:00 | 498 | 494
2018-08-04 20:30 | 497 | 493
2018-08-04 21:00 | 477 | 474
2018-08-04 21:30 | 458 | 455
2018-08-04 22:00 | 445 | 441
2018-08-04 22:30 | 451 | 447
2018-08-04 23:00 | 452 | 448
2018-08-04 23:30 | 434 | 428
2018-08-05 | 413 | 405
2018-08-05 00:30 | 385 | 374
2018-08-05 01:00 | 366 | 356
2018-08-05 01:30 | 344 | 332
2018-08-05 02:00 | 327 | 315
2018-08-05 02:30 | 317 | 299
2018-08-05 03:00 | 318 | 296
2018-08-05 03:30 | 322 | 299
2018-08-05 04:00 | 318 | 296
2018-08-05 04:30 | 322 | 301
2018-08-05 05:00 | 328 | 306
2018-08-05 05:30 | 345 | 325
2018-08-05 06:00 | 354 | 335
2018-08-05 06:30 | 358 | 340
2018-08-05 07:00 | 367 | 351
2018-08-05 07:30 | 390 | 375
2018-08-05 08:00 | 404 | 390
2018-08-05 08:30 | 410 | 396
2018-08-05 09:00 | 408 | 394
2018-08-05 09:30 | 398 | 385
2018-08-05 10:00 | 376 | 362
2018-08-05 10:30 | 371 | 358
2018-08-05 11:00 | 352 | 337
2018-08-05 11:30 | 344 | 329
2018-08-05 12:00 | 333 | 317
2018-08-05 12:30 | 330 | 314
2018-08-05 13:00 | 323 | 307
2018-08-05 13:30 | 329 | 313
2018-08-05 14:00 | 334 | 320
2018-08-05 14:30 | 357 | 344
2018-08-05 15:00 | 368 | 356
2018-08-05 15:30 | 372 | 360
2018-08-05 16:00 | 392 | 383
2018-08-05 16:30 | 430 | 423
2018-08-05 17:00 | 462 | 456
2018-08-05 17:30 | 474 | 468
2018-08-05 18:00 | 502 | 496
2018-08-05 18:30 | 518 | 511
2018-08-05 19:00 | 524 | 517
2018-08-05 19:30 | 507 | 499
2018-08-05 20:00 | 501 | 495
2018-08-05 20:30 | 505 | 499
2018-08-05 21:00 | 491 | 486
2018-08-05 21:30 | 468 | 463
2018-08-05 22:00 | 447 | 441
2018-08-05 22:30 | 432 | 424
2018-08-05 23:00 | 422 | 414
2018-08-05 23:30 | 417 | 407
2018-08-06 | 402 | 389
2018-08-06 00:30 | 376 | 361
2018-08-06 01:00 | 354 | 338
2018-08-06 01:30 | 345 | 328
2018-08-06 02:00 | 331 | 314
2018-08-06 02:30 | 322 | 303
2018-08-06 03:00 | 318 | 300
2018-08-06 03:30 | 321 | 303
2018-08-06 04:00 | 319 | 301
2018-08-06 04:30 | 323 | 306
2018-08-06 05:00 | 340 | 326
2018-08-06 05:30 | 366 | 355
2018-08-06 06:00 | 399 | 391
2018-08-06 06:30 | 455 | 449
2018-08-06 07:00 | 500 | 496
2018-08-06 07:30 | 531 | 528
2018-08-06 08:00 | 545 | 541
2018-08-06 08:30 | 541 | 536
2018-08-06 09:00 | 525 | 520
2018-08-06 09:30 | 514 | 508
2018-08-06 10:00 | 505 | 500
2018-08-06 10:30 | 492 | 487
2018-08-06 11:00 | 473 | 470
2018-08-06 11:30 | 466 | 464
2018-08-06 12:00 | 465 | 463
2018-08-06 12:30 | 464 | 462
2018-08-06 13:00 | 461 | 460
2018-08-06 13:30 | 459 | 457
2018-08-06 14:00 | 455 | 455
2018-08-06 14:30 | 470 | 469
2018-08-06 15:00 | 480 | 480
2018-08-06 15:30 | 503 | 503
2018-08-06 16:00 | 530 | 527
2018-08-06 16:30 | 560 | 555
2018-08-06 17:00 | 583 | 579
2018-08-06 17:30 | 605 | 600
2018-08-06 18:00 | 633 | 628
2018-08-06 18:30 | 650 | 641
2018-08-06 19:00 | 644 | 633
2018-08-06 19:30 | 610 | 598
2018-08-06 20:00 | 599 | 590
2018-08-06 20:30 | 597 | 586
2018-08-06 21:00 | 566 | 562
2018-08-06 21:30 | 536 | 533
2018-08-06 22:00 | 517 | 514
2018-08-06 22:30 | 507 | 503
2018-08-06 23:00 | 488 | 483
2018-08-06 23:30 | 476 | 469
2018-08-07 | 455 | 446
2018-08-07 00:30 | 413 | 403
2018-08-07 01:00 | 395 | 384
2018-08-07 01:30 | 375 | 363
2018-08-07 02:00 | 356 | 341
2018-08-07 02:30 | 340 | 325
2018-08-07 03:00 | 316 | 300
2018-08-07 03:30 | 303 | 287
2018-08-07 04:00 | 305 | 289
2018-08-07 04:30 | 326 | 312
2018-08-07 05:00 | 339 | 327
2018-08-07 05:30 | 377 | 368
2018-08-07 06:00 | 407 | 401
2018-08-07 06:30 | 457 | 453
2018-08-07 07:00 | 507 | 504
2018-08-07 07:30 | 543 | 541
2018-08-07 08:00 | 552 | 549
2018-08-07 08:30 | 544 | 539
2018-08-07 09:00 | 519 | 514
2018-08-07 09:30 | 511 | 506
2018-08-07 10:00 | 481 | 477
2018-08-07 10:30 | 446 | 443
2018-08-07 11:00 | 439 | 437
2018-08-07 11:30 | 419 | 418
2018-08-07 12:00 | 405 | 404
2018-08-07 12:30 | 412 | 411
2018-08-07 13:00 | 433 | 432
2018-08-07 13:30 | 439 | 438
2018-08-07 14:00 | 429 | 428
2018-08-07 14:30 | 427 | 426
2018-08-07 15:00 | 424 | 423
2018-08-07 15:30 | 442 | 442
2018-08-07 16:00 | 473 | 471
2018-08-07 16:30 | 502 | 500
2018-08-07 17:00 | 543 | 541
2018-08-07 17:30 | 590 | 583
2018-08-07 18:00 | 629 | 621
2018-08-07 18:30 | 640 | 631
2018-08-07 19:00 | 641 | 633
2018-08-07 19:30 | 628 | 619
2018-08-07 20:00 | 627 | 619
2018-08-07 20:30 | 624 | 617
2018-08-07 21:00 | 603 | 595
2018-08-07 21:30 | 583 | 573
2018-08-07 22:00 | 565 | 552
2018-08-07 22:30 | 549 | 534
2018-08-07 23:00 | 520 | 512
2018-08-07 23:30 | 517 | 511
2018-08-08 | 490 | 484
2018-08-08 00:30 | 450 | 442
2018-08-08 01:00 | 423 | 413
2018-08-08 01:30 | 393 | 381
2018-08-08 02:00 | 378 | 365
2018-08-08 02:30 | 355 | 342
2018-08-08 03:00 | 341 | 327
2018-08-08 03:30 | 348 | 334
2018-08-08 04:00 | 352 | 339
2018-08-08 04:30 | 358 | 346
2018-08-08 05:00 | 383 | 373
2018-08-08 05:30 | 424 | 417
2018-08-08 06:00 | 470 | 465
2018-08-08 06:30 | 543 | 540
2018-08-08 07:00 | 611 | 608
2018-08-08 07:30 | 644 | 642
2018-08-08 08:00 | 635 | 632
2018-08-08 08:30 | 603 | 598
2018-08-08 09:00 | 566 | 561
2018-08-08 09:30 | 537 | 535
2018-08-08 10:00 | 513 | 511
2018-08-08 10:30 | 484 | 482
2018-08-08 11:00 | 460 | 459
2018-08-08 11:30 | 446 | 445
2018-08-08 12:00 | 435 | 435
2018-08-08 12:30 | 424 | 423
2018-08-08 13:00 | 425 | 424
2018-08-08 13:30 | 419 | 419
2018-08-08 14:00 | 416 | 416
2018-08-08 14:30 | 432 | 431
2018-08-08 15:00 | 443 | 442
2018-08-08 15:30 | 459 | 458
2018-08-08 16:00 | 494 | 494
2018-08-08 16:30 | 538 | 537
2018-08-08 17:00 | 578 | 575
2018-08-08 17:30 | 602 | 600
2018-08-08 18:00 | 657 | 651
2018-08-08 18:30 | 687 | 678
2018-08-08 19:00 | 693 | 684
2018-08-08 19:30 | 664 | 656
2018-08-08 20:00 | 658 | 653
2018-08-08 20:30 | 659 | 654
2018-08-08 21:00 | 633 | 628
2018-08-08 21:30 | 607 | 602
2018-08-08 22:00 | 580 | 579
2018-08-08 22:30 | 560 | 559
2018-08-08 23:00 | 540 | 538
2018-08-08 23:30 | 526 | 524
2018-08-09 | 503 | 499
2018-08-09 00:30 | 463 | 457
2018-08-09 01:00 | 438 | 432
2018-08-09 01:30 | 419 | 410
2018-08-09 02:00 | 401 | 390
2018-08-09 02:30 | 387 | 375
2018-08-09 03:00 | 368 | 353
2018-08-09 03:30 | 362 | 347
2018-08-09 04:00 | 363 | 348
2018-08-09 04:30 | 370 | 357
2018-08-09 05:00 | 384 | 373
2018-08-09 05:30 | 424 | 417
2018-08-09 06:00 | 480 | 477
2018-08-09 06:30 | 558 | 555
2018-08-09 07:00 | 632 | 626
2018-08-09 07:30 | 694 | 686
2018-08-09 08:00 | 694 | 683
2018-08-09 08:30 | 639 | 627
2018-08-09 09:00 | 587 | 580
2018-08-09 09:30 | 553 | 550
2018-08-09 10:00 | 526 | 523
2018-08-09 10:30 | 507 | 504
2018-08-09 11:00 | 481 | 477
2018-08-09 11:30 | 444 | 442
2018-08-09 12:00 | 423 | 421
2018-08-09 12:30 | 419 | 417
2018-08-09 13:00 | 405 | 403
2018-08-09 13:30 | 425 | 423
2018-08-09 14:00 | 416 | 415
2018-08-09 14:30 | 444 | 442
2018-08-09 15:00 | 464 | 463
2018-08-09 15:30 | 481 | 480
2018-08-09 16:00 | 505 | 504
2018-08-09 16:30 | 539 | 538
2018-08-09 17:00 | 576 | 575
2018-08-09 17:30 | 610 | 606
2018-08-09 18:00 | 642 | 635
2018-08-09 18:30 | 661 | 653
2018-08-09 19:00 | 664 | 655
2018-08-09 19:30 | 659 | 650
2018-08-09 20:00 | 664 | 654
2018-08-09 20:30 | 659 | 648
2018-08-09 21:00 | 644 | 631
2018-08-09 21:30 | 612 | 599
2018-08-09 22:00 | 592 | 578
2018-08-09 22:30 | 565 | 560
2018-08-09 23:00 | 544 | 539
2018-08-09 23:30 | 517 | 512
2018-08-10 | 495 | 490
2018-08-10 00:30 | 449 | 444
2018-08-10 01:00 | 412 | 404
2018-08-10 01:30 | 396 | 387
2018-08-10 02:00 | 384 | 374
2018-08-10 02:30 | 380 | 370
2018-08-10 03:00 | 379 | 369
2018-08-10 03:30 | 377 | 367
2018-08-10 04:00 | 377 | 367
2018-08-10 04:30 | 382 | 373
2018-08-10 05:00 | 397 | 390
2018-08-10 05:30 | 440 | 435
2018-08-10 06:00 | 469 | 464
2018-08-10 06:30 | 538 | 533
2018-08-10 07:00 | 638 | 627
2018-08-10 07:30 | 666 | 657
2018-08-10 08:00 | 647 | 638
2018-08-10 08:30 | 611 | 601
2018-08-10 09:00 | 563 | 552
2018-08-10 09:30 | 533 | 523
2018-08-10 10:00 | 504 | 500
2018-08-10 10:30 | 475 | 471
2018-08-10 11:00 | 454 | 453
2018-08-10 11:30 | 433 | 432
2018-08-10 12:00 | 422 | 421
2018-08-10 12:30 | 419 | 417
2018-08-10 13:00 | 420 | 418
2018-08-10 13:30 | 415 | 413
2018-08-10 14:00 | 419 | 417
2018-08-10 14:30 | 422 | 421
2018-08-10 15:00 | 428 | 426
2018-08-10 15:30 | 445 | 445
2018-08-10 16:00 | 469 | 469
2018-08-10 16:30 | 506 | 506
2018-08-10 17:00 | 540 | 539
2018-08-10 17:30 | 561 | 559
2018-08-10 18:00 | 590 | 584
2018-08-10 18:30 | 594 | 585
2018-08-10 19:00 | 594 | 585
2018-08-10 19:30 | 588 | 579
2018-08-10 20:00 | 584 | 577
2018-08-10 20:30 | 592 | 585
2018-08-10 21:00 | 570 | 562
2018-08-10 21:30 | 546 | 542
2018-08-10 22:00 | 532 | 529
2018-08-10 22:30 | 512 | 510
2018-08-10 23:00 | 496 | 493
2018-08-10 23:30 | 486 | 483
2018-08-11 | 466 | 461
2018-08-11 00:30 | 427 | 420
2018-08-11 01:00 | 394 | 385
2018-08-11 01:30 | 370 | 359
2018-08-11 02:00 | 351 | 339
2018-08-11 02:30 | 344 | 331
2018-08-11 03:00 | 336 | 323
2018-08-11 03:30 | 336 | 323
2018-08-11 04:00 | 333 | 320
2018-08-11 04:30 | 338 | 326
2018-08-11 05:00 | 341 | 329
2018-08-11 05:30 | 351 | 341
2018-08-11 06:00 | 369 | 360
2018-08-11 06:30 | 388 | 382
2018-08-11 07:00 | 412 | 406
2018-08-11 07:30 | 447 | 442
2018-08-11 08:00 | 475 | 471
2018-08-11 08:30 | 488 | 483
2018-08-11 09:00 | 488 | 482
2018-08-11 09:30 | 481 | 475
2018-08-11 10:00 | 441 | 436
2018-08-11 10:30 | 413 | 409
2018-08-11 11:00 | 394 | 389
2018-08-11 11:30 | 394 | 389
2018-08-11 12:00 | 373 | 367
2018-08-11 12:30 | 357 | 351
2018-08-11 13:00 | 366 | 359
2018-08-11 13:30 | 359 | 353
2018-08-11 14:00 | 362 | 356
2018-08-11 14:30 | 366 | 361
2018-08-11 15:00 | 386 | 381
2018-08-11 15:30 | 395 | 390
2018-08-11 16:00 | 417 | 412
2018-08-11 16:30 | 448 | 443
2018-08-11 17:00 | 480 | 477
2018-08-11 17:30 | 496 | 492
2018-08-11 18:00 | 508 | 504
2018-08-11 18:30 | 516 | 508
2018-08-11 19:00 | 517 | 510
2018-08-11 19:30 | 508 | 499
2018-08-11 20:00 | 501 | 495
2018-08-11 20:30 | 502 | 496
2018-08-11 21:00 | 489 | 487
2018-08-11 21:30 | 483 | 481
2018-08-11 22:00 | 480 | 478
2018-08-11 22:30 | 469 | 466
2018-08-11 23:00 | 461 | 458
2018-08-11 23:30 | 452 | 447
2018-08-12 | 429 | 424
2018-08-12 00:30 | 384 | 377
2018-08-12 01:00 | 368 | 359
2018-08-12 01:30 | 366 | 356
2018-08-12 02:00 | 356 | 345
2018-08-12 02:30 | 349 | 335
2018-08-12 03:00 | 344 | 326
2018-08-12 03:30 | 339 | 321
2018-08-12 04:00 | 335 | 316
2018-08-12 04:30 | 339 | 320
2018-08-12 05:00 | 337 | 319
2018-08-12 05:30 | 344 | 326
2018-08-12 06:00 | 359 | 342
2018-08-12 06:30 | 369 | 353
2018-08-12 07:00 | 382 | 367
2018-08-12 07:30 | 400 | 386
2018-08-12 08:00 | 415 | 401
2018-08-12 08:30 | 422 | 410
2018-08-12 09:00 | 424 | 413
2018-08-12 09:30 | 419 | 409
2018-08-12 10:00 | 407 | 397
2018-08-12 10:30 | 398 | 387
2018-08-12 11:00 | 390 | 380
2018-08-12 11:30 | 382 | 372
2018-08-12 12:00 | 374 | 364
2018-08-12 12:30 | 371 | 360
2018-08-12 13:00 | 367 | 356
2018-08-12 13:30 | 366 | 355
2018-08-12 14:00 | 368 | 356
2018-08-12 14:30 | 372 | 361
2018-08-12 15:00 | 369 | 358
2018-08-12 15:30 | 375 | 365
2018-08-12 16:00 | 381 | 372
2018-08-12 16:30 | 407 | 399
2018-08-12 17:00 | 456 | 449
2018-08-12 17:30 | 493 | 487
2018-08-12 18:00 | 528 | 521
2018-08-12 18:30 | 541 | 533
2018-08-12 19:00 | 547 | 539
2018-08-12 19:30 | 541 | 532
2018-08-12 20:00 | 531 | 525
2018-08-12 20:30 | 532 | 527
2018-08-12 21:00 | 519 | 516
2018-08-12 21:30 | 502 | 499
2018-08-12 22:00 | 492 | 488
2018-08-12 22:30 | 480 | 476
2018-08-12 23:00 | 464 | 459
2018-08-12 23:30 | 446 | 439
2018-08-13 | 425 | 415
2018-08-13 00:30 | 395 | 383
2018-08-13 01:00 | 368 | 354
2018-08-13 01:30 | 364 | 349
2018-08-13 02:00 | 360 | 345
2018-08-13 02:30 | 360 | 345
2018-08-13 03:00 | 350 | 335
2018-08-13 03:30 | 350 | 333
2018-08-13 04:00 | 343 | 326
2018-08-13 04:30 | 357 | 341
2018-08-13 05:00 | 380 | 367
2018-08-13 05:30 | 407 | 397
2018-08-13 06:00 | 441 | 435
2018-08-13 06:30 | 504 | 498
2018-08-13 07:00 | 576 | 568
2018-08-13 07:30 | 619 | 612
2018-08-13 08:00 | 623 | 612
2018-08-13 08:30 | 599 | 587
2018-08-13 09:00 | 563 | 550
2018-08-13 09:30 | 536 | 525
2018-08-13 10:00 | 509 | 497
2018-08-13 10:30 | 486 | 473
2018-08-13 11:00 | 453 | 449
2018-08-13 11:30 | 440 | 436
2018-08-13 12:00 | 430 | 427
2018-08-13 12:30 | 430 | 426
2018-08-13 13:00 | 421 | 418
2018-08-13 13:30 | 413 | 411
2018-08-13 14:00 | 420 | 418
2018-08-13 14:30 | 429 | 427
2018-08-13 15:00 | 454 | 452
2018-08-13 15:30 | 466 | 465
2018-08-13 16:00 | 492 | 490
2018-08-13 16:30 | 536 | 533
2018-08-13 17:00 | 585 | 575
2018-08-13 17:30 | 608 | 601
2018-08-13 18:00 | 642 | 635
2018-08-13 18:30 | 670 | 661
2018-08-13 19:00 | 680 | 671
2018-08-13 19:30 | 651 | 642
2018-08-13 20:00 | 644 | 637
2018-08-13 20:30 | 644 | 637
2018-08-13 21:00 | 629 | 624
2018-08-13 21:30 | 615 | 608
2018-08-13 22:00 | 591 | 587
2018-08-13 22:30 | 565 | 561
2018-08-13 23:00 | 539 | 535
2018-08-13 23:30 | 518 | 514
2018-08-14 | 499 | 494
2018-08-14 00:30 | 454 | 448
2018-08-14 01:00 | 436 | 427
2018-08-14 01:30 | 426 | 416
2018-08-14 02:00 | 415 | 404
2018-08-14 02:30 | 397 | 385
2018-08-14 03:00 | 386 | 373
2018-08-14 03:30 | 378 | 364
2018-08-14 04:00 | 376 | 363
2018-08-14 04:30 | 383 | 371
2018-08-14 05:00 | 398 | 388
2018-08-14 05:30 | 432 | 426
2018-08-14 06:00 | 482 | 478
2018-08-14 06:30 | 565 | 559
2018-08-14 07:00 | 640 | 633
2018-08-14 07:30 | 678 | 671
2018-08-14 08:00 | 659 | 652
2018-08-14 08:30 | 623 | 615
2018-08-14 09:00 | 569 | 567
2018-08-14 09:30 | 525 | 524
2018-08-14 10:00 | 503 | 501
2018-08-14 10:30 | 478 | 476
2018-08-14 11:00 | 433 | 432
2018-08-14 11:30 | 419 | 419
2018-08-14 12:00 | 411 | 411
2018-08-14 12:30 | 408 | 408
2018-08-14 13:00 | 411 | 410
2018-08-14 13:30 | 421 | 421
2018-08-14 14:00 | 432 | 431
2018-08-14 14:30 | 440 | 439
2018-08-14 15:00 | 447 | 447
2018-08-14 15:30 | 461 | 460
2018-08-14 16:00 | 490 | 489
2018-08-14 16:30 | 526 | 526
2018-08-14 17:00 | 568 | 567
2018-08-14 17:30 | 594 | 592
2018-08-14 18:00 | 629 | 627
2018-08-14 18:30 | 636 | 632
2018-08-14 19:00 | 635 | 630
2018-08-14 19:30 | 632 | 625
2018-08-14 20:00 | 628 | 622
2018-08-14 20:30 | 629 | 623
2018-08-14 21:00 | 615 | 608
2018-08-14 21:30 | 584 | 577
2018-08-14 22:00 | 568 | 561
2018-08-14 22:30 | 547 | 542
2018-08-14 23:00 | 522 | 517
2018-08-14 23:30 | 501 | 493
2018-08-15 | 484 | 473
2018-08-15 00:30 | 446 | 433
2018-08-15 01:00 | 411 | 400
2018-08-15 01:30 | 391 | 379
2018-08-15 02:00 | 373 | 360
2018-08-15 02:30 | 376 | 363
2018-08-15 03:00 | 374 | 361
2018-08-15 03:30 | 372 | 359
2018-08-15 04:00 | 374 | 361
2018-08-15 04:30 | 378 | 366
2018-08-15 05:00 | 387 | 376
2018-08-15 05:30 | 407 | 398
2018-08-15 06:00 | 434 | 428
2018-08-15 06:30 | 491 | 485
2018-08-15 07:00 | 546 | 538
2018-08-15 07:30 | 585 | 577
2018-08-15 08:00 | 577 | 568
2018-08-15 08:30 | 553 | 544
2018-08-15 09:00 | 519 | 509
2018-08-15 09:30 | 496 | 485
2018-08-15 10:00 | 473 | 462
2018-08-15 10:30 | 449 | 438
2018-08-15 11:00 | 418 | 413
2018-08-15 11:30 | 406 | 401
2018-08-15 12:00 | 388 | 383
2018-08-15 12:30 | 380 | 376
2018-08-15 13:00 | 386 | 382
2018-08-15 13:30 | 390 | 386
2018-08-15 14:00 | 385 | 382
2018-08-15 14:30 | 390 | 386
2018-08-15 15:00 | 403 | 399
2018-08-15 15:30 | 431 | 428
2018-08-15 16:00 | 456 | 452
2018-08-15 16:30 | 480 | 477
2018-08-15 17:00 | 514 | 512
2018-08-15 17:30 | 546 | 543
2018-08-15 18:00 | 576 | 573
2018-08-15 18:30 | 586 | 582
2018-08-15 19:00 | 587 | 583
2018-08-15 19:30 | 584 | 580
2018-08-15 20:00 | 577 | 573
2018-08-15 20:30 | 571 | 567
2018-08-15 21:00 | 546 | 542
2018-08-15 21:30 | 531 | 527
2018-08-15 22:00 | 514 | 509
2018-08-15 22:30 | 505 | 500
2018-08-15 23:00 | 498 | 492
2018-08-15 23:30 | 484 | 477
2018-08-16 | 463 | 455
2018-08-16 00:30 | 417 | 408
2018-08-16 01:00 | 395 | 382
2018-08-16 01:30 | 377 | 362
2018-08-16 02:00 | 366 | 350
2018-08-16 02:30 | 356 | 340
2018-08-16 03:00 | 347 | 330
2018-08-16 03:30 | 350 | 334
2018-08-16 04:00 | 359 | 344
2018-08-16 04:30 | 364 | 351
2018-08-16 05:00 | 379 | 367
2018-08-16 05:30 | 410 | 402
2018-08-16 06:00 | 453 | 449
2018-08-16 06:30 | 519 | 515
2018-08-16 07:00 | 570 | 567
2018-08-16 07:30 | 601 | 598
2018-08-16 08:00 | 597 | 594
2018-08-16 08:30 | 577 | 572
2018-08-16 09:00 | 541 | 536
2018-08-16 09:30 | 514 | 509
2018-08-16 10:00 | 486 | 482
2018-08-16 10:30 | 456 | 453
2018-08-16 11:00 | 442 | 440
2018-08-16 11:30 | 434 | 433
2018-08-16 12:00 | 435 | 434
2018-08-16 12:30 | 432 | 431
2018-08-16 13:00 | 432 | 431
2018-08-16 13:30 | 442 | 442
2018-08-16 14:00 | 449 | 449
2018-08-16 14:30 | 468 | 467
2018-08-16 15:00 | 477 | 477
2018-08-16 15:30 | 487 | 486
2018-08-16 16:00 | 511 | 511
2018-08-16 16:30 | 549 | 545
2018-08-16 17:00 | 596 | 585
2018-08-16 17:30 | 607 | 596
2018-08-16 18:00 | 638 | 629
2018-08-16 18:30 | 649 | 640
2018-08-16 19:00 | 647 | 638
2018-08-16 19:30 | 639 | 629
2018-08-16 20:00 | 639 | 629
2018-08-16 20:30 | 631 | 621
2018-08-16 21:00 | 612 | 600
2018-08-16 21:30 | 583 | 575
2018-08-16 22:00 | 562 | 557
2018-08-16 22:30 | 543 | 537
2018-08-16 23:00 | 516 | 512
2018-08-16 23:30 | 494 | 491
2018-08-17 | 473 | 468
2018-08-17 00:30 | 432 | 427
2018-08-17 01:00 | 405 | 398
2018-08-17 01:30 | 391 | 382
2018-08-17 02:00 | 379 | 369
2018-08-17 02:30 | 368 | 358
2018-08-17 03:00 | 365 | 355
2018-08-17 03:30 | 360 | 349
2018-08-17 04:00 | 363 | 352
2018-08-17 04:30 | 371 | 361
2018-08-17 05:00 | 382 | 373
2018-08-17 05:30 | 409 | 403
2018-08-17 06:00 | 451 | 447
2018-08-17 06:30 | 510 | 507
2018-08-17 07:00 | 563 | 560
2018-08-17 07:30 | 608 | 602
2018-08-17 08:00 | 602 | 593
2018-08-17 08:30 | 577 | 567
2018-08-17 09:00 | 538 | 531
2018-08-17 09:30 | 506 | 500
2018-08-17 10:00 | 477 | 471
2018-08-17 10:30 | 458 | 454
2018-08-17 11:00 | 439 | 439
2018-08-17 11:30 | 422 | 422
2018-08-17 12:00 | 408 | 408
2018-08-17 12:30 | 402 | 402
2018-08-17 13:00 | 405 | 405
2018-08-17 13:30 | 406 | 406
2018-08-17 14:00 | 409 | 409
2018-08-17 14:30 | 420 | 420
2018-08-17 15:00 | 434 | 433
2018-08-17 15:30 | 449 | 449
2018-08-17 16:00 | 475 | 475
2018-08-17 16:30 | 516 | 515
2018-08-17 17:00 | 543 | 541
2018-08-17 17:30 | 563 | 561
2018-08-17 18:00 | 586 | 584
2018-08-17 18:30 | 592 | 590
2018-08-17 19:00 | 595 | 592
2018-08-17 19:30 | 583 | 579
2018-08-17 20:00 | 580 | 578
2018-08-17 20:30 | 586 | 584
2018-08-17 21:00 | 566 | 564
2018-08-17 21:30 | 550 | 548
2018-08-17 22:00 | 536 | 533
2018-08-17 22:30 | 528 | 525
2018-08-17 23:00 | 511 | 509
2018-08-17 23:30 | 488 | 485
2018-08-18 | 458 | 453
2018-08-18 00:30 | 428 | 422
2018-08-18 01:00 | 406 | 398
2018-08-18 01:30 | 383 | 373
2018-08-18 02:00 | 368 | 357
2018-08-18 02:30 | 354 | 342
2018-08-18 03:00 | 350 | 338
2018-08-18 03:30 | 345 | 332
2018-08-18 04:00 | 348 | 336
2018-08-18 04:30 | 347 | 335
2018-08-18 05:00 | 351 | 340
2018-08-18 05:30 | 363 | 353
2018-08-18 06:00 | 381 | 373
2018-08-18 06:30 | 409 | 401
2018-08-18 07:00 | 425 | 418
2018-08-18 07:30 | 441 | 436
2018-08-18 08:00 | 458 | 454
2018-08-18 08:30 | 461 | 457
2018-08-18 09:00 | 443 | 439
2018-08-18 09:30 | 413 | 409
2018-08-18 10:00 | 384 | 379
2018-08-18 10:30 | 368 | 362
2018-08-18 11:00 | 364 | 358
2018-08-18 11:30 | 351 | 345
2018-08-18 12:00 | 338 | 331
2018-08-18 12:30 | 335 | 329
2018-08-18 13:00 | 335 | 329
2018-08-18 13:30 | 339 | 333
2018-08-18 14:00 | 354 | 347
2018-08-18 14:30 | 358 | 352
2018-08-18 15:00 | 371 | 366
2018-08-18 15:30 | 384 | 380
2018-08-18 16:00 | 404 | 400
2018-08-18 16:30 | 432 | 428
2018-08-18 17:00 | 470 | 467
2018-08-18 17:30 | 486 | 484
2018-08-18 18:00 | 511 | 509
2018-08-18 18:30 | 527 | 524
2018-08-18 19:00 | 527 | 524
2018-08-18 19:30 | 522 | 518
2018-08-18 20:00 | 523 | 520
2018-08-18 20:30 | 521 | 517
2018-08-18 21:00 | 506 | 503
2018-08-18 21:30 | 491 | 488
2018-08-18 22:00 | 483 | 479
2018-08-18 22:30 | 480 | 476
2018-08-18 23:00 | 474 | 469
2018-08-18 23:30 | 461 | 456
2018-08-19 | 423 | 416
2018-08-19 00:30 | 390 | 379
2018-08-19 01:00 | 370 | 357
2018-08-19 01:30 | 358 | 345
2018-08-19 02:00 | 341 | 326
2018-08-19 02:30 | 334 | 318
2018-08-19 03:00 | 338 | 322
2018-08-19 03:30 | 333 | 316
2018-08-19 04:00 | 334 | 317
2018-08-19 04:30 | 335 | 317
2018-08-19 05:00 | 337 | 319
2018-08-19 05:30 | 343 | 325
2018-08-19 06:00 | 357 | 341
2018-08-19 06:30 | 374 | 359
2018-08-19 07:00 | 388 | 374
2018-08-19 07:30 | 401 | 388
2018-08-19 08:00 | 413 | 402
2018-08-19 08:30 | 411 | 400
2018-08-19 09:00 | 404 | 393
2018-08-19 09:30 | 400 | 389
2018-08-19 10:00 | 386 | 375
2018-08-19 10:30 | 374 | 364
2018-08-19 11:00 | 360 | 348
2018-08-19 11:30 | 351 | 339
2018-08-19 12:00 | 342 | 329
2018-08-19 12:30 | 339 | 327
2018-08-19 13:00 | 339 | 326
2018-08-19 13:30 | 344 | 331
2018-08-19 14:00 | 350 | 338
2018-08-19 14:30 | 356 | 344
2018-08-19 15:00 | 376 | 364
2018-08-19 15:30 | 396 | 385
2018-08-19 16:00 | 421 | 411
2018-08-19 16:30 | 445 | 436
2018-08-19 17:00 | 494 | 487
2018-08-19 17:30 | 531 | 525
2018-08-19 18:00 | 554 | 551
2018-08-19 18:30 | 579 | 569
2018-08-19 19:00 | 580 | 570
2018-08-19 19:30 | 575 | 564
2018-08-19 20:00 | 576 | 566
2018-08-19 20:30 | 580 | 569
2018-08-19 21:00 | 569 | 557
2018-08-19 21:30 | 552 | 540
2018-08-19 22:00 | 536 | 524
2018-08-19 22:30 | 523 | 510
2018-08-19 23:00 | 503 | 498
2018-08-19 23:30 | 481 | 475
2018-08-20 | 450 | 444
2018-08-20 00:30 | 422 | 414
2018-08-20 01:00 | 398 | 388
2018-08-20 01:30 | 384 | 372
2018-08-20 02:00 | 374 | 361
2018-08-20 02:30 | 367 | 352
2018-08-20 03:00 | 365 | 350
2018-08-20 03:30 | 366 | 352
2018-08-20 04:00 | 366 | 353
2018-08-20 04:30 | 371 | 358
2018-08-20 05:00 | 381 | 370
2018-08-20 05:30 | 413 | 405
2018-08-20 06:00 | 458 | 452
2018-08-20 06:30 | 536 | 524
2018-08-20 07:00 | 589 | 580
2018-08-20 07:30 | 622 | 612
2018-08-20 08:00 | 615 | 605
2018-08-20 08:30 | 580 | 570
2018-08-20 09:00 | 545 | 534
2018-08-20 09:30 | 513 | 508
2018-08-20 10:00 | 485 | 483
2018-08-20 10:30 | 469 | 468
2018-08-20 11:00 | 453 | 451
2018-08-20 11:30 | 439 | 437
2018-08-20 12:00 | 429 | 428
2018-08-20 12:30 | 422 | 420
2018-08-20 13:00 | 420 | 419
2018-08-20 13:30 | 420 | 420
2018-08-20 14:00 | 425 | 425
2018-08-20 14:30 | 436 | 435
2018-08-20 15:00 | 447 | 446
2018-08-20 15:30 | 465 | 465
2018-08-20 16:00 | 498 | 497
2018-08-20 16:30 | 542 | 539
2018-08-20 17:00 | 580 | 574
2018-08-20 17:30 | 618 | 609
2018-08-20 18:00 | 671 | 663
2018-08-20 18:30 | 692 | 682
2018-08-20 19:00 | 692 | 682
2018-08-20 19:30 | 680 | 670
2018-08-20 20:00 | 684 | 673
2018-08-20 20:30 | 675 | 663
2018-08-20 21:00 | 659 | 646
2018-08-20 21:30 | 626 | 612
2018-08-20 22:00 | 594 | 582
2018-08-20 22:30 | 561 | 553
2018-08-20 23:00 | 539 | 531
2018-08-20 23:30 | 517 | 511
2018-08-21 | 496 | 489
2018-08-21 00:30 | 453 | 446
2018-08-21 01:00 | 423 | 413
2018-08-21 01:30 | 413 | 401
2018-08-21 02:00 | 399 | 387
2018-08-21 02:30 | 378 | 365
2018-08-21 03:00 | 368 | 354
2018-08-21 03:30 | 364 | 350
2018-08-21 04:00 | 367 | 353
2018-08-21 04:30 | 377 | 365
2018-08-21 05:00 | 387 | 376
2018-08-21 05:30 | 436 | 429
2018-08-21 06:00 | 489 | 485
2018-08-21 06:30 | 558 | 556
2018-08-21 07:00 | 630 | 628
2018-08-21 07:30 | 677 | 672
2018-08-21 08:00 | 686 | 676
2018-08-21 08:30 | 628 | 617
2018-08-21 09:00 | 581 | 568
2018-08-21 09:30 | 547 | 535
2018-08-21 10:00 | 513 | 505
2018-08-21 10:30 | 476 | 471
2018-08-21 11:00 | 453 | 449
2018-08-21 11:30 | 433 | 430
2018-08-21 12:00 | 423 | 421
2018-08-21 12:30 | 416 | 414
2018-08-21 13:00 | 415 | 413
2018-08-21 13:30 | 418 | 416
2018-08-21 14:00 | 426 | 424
2018-08-21 14:30 | 437 | 435
2018-08-21 15:00 | 453 | 451
2018-08-21 15:30 | 475 | 474
2018-08-21 16:00 | 501 | 500
2018-08-21 16:30 | 538 | 534
2018-08-21 17:00 | 575 | 569
2018-08-21 17:30 | 601 | 595
2018-08-21 18:00 | 646 | 637
2018-08-21 18:30 | 673 | 663
2018-08-21 19:00 | 675 | 666
2018-08-21 19:30 | 667 | 656
2018-08-21 20:00 | 665 | 654
2018-08-21 20:30 | 665 | 653
2018-08-21 21:00 | 638 | 629
2018-08-21 21:30 | 606 | 595
2018-08-21 22:00 | 585 | 574
2018-08-21 22:30 | 552 | 548
2018-08-21 23:00 | 538 | 533
2018-08-21 23:30 | 517 | 512
2018-08-22 | 496 | 489
2018-08-22 00:30 | 458 | 449
2018-08-22 01:00 | 431 | 420
2018-08-22 01:30 | 412 | 399
2018-08-22 02:00 | 395 | 381
2018-08-22 02:30 | 378 | 363
2018-08-22 03:00 | 371 | 355
2018-08-22 03:30 | 369 | 353
2018-08-22 04:00 | 370 | 354
2018-08-22 04:30 | 374 | 360
2018-08-22 05:00 | 386 | 375
2018-08-22 05:30 | 425 | 417
2018-08-22 06:00 | 478 | 471
2018-08-22 06:30 | 538 | 533
2018-08-22 07:00 | 596 | 593
2018-08-22 07:30 | 640 | 634
2018-08-22 08:00 | 629 | 621
2018-08-22 08:30 | 582 | 573
2018-08-22 09:00 | 533 | 523
2018-08-22 09:30 | 506 | 498
2018-08-22 10:00 | 483 | 477
2018-08-22 10:30 | 460 | 454
2018-08-22 11:00 | 446 | 440
2018-08-22 11:30 | 426 | 421
2018-08-22 12:00 | 419 | 415
2018-08-22 12:30 | 420 | 416
2018-08-22 13:00 | 426 | 422
2018-08-22 13:30 | 434 | 430
2018-08-22 14:00 | 440 | 437
2018-08-22 14:30 | 444 | 441
2018-08-22 15:00 | 452 | 448
2018-08-22 15:30 | 470 | 465
2018-08-22 16:00 | 489 | 484
2018-08-22 16:30 | 514 | 509
2018-08-22 17:00 | 545 | 540
2018-08-22 17:30 | 570 | 564
2018-08-22 18:00 | 609 | 604
2018-08-22 18:30 | 635 | 628
2018-08-22 19:00 | 645 | 637
2018-08-22 19:30 | 631 | 622
2018-08-22 20:00 | 622 | 614
2018-08-22 20:30 | 614 | 606
2018-08-22 21:00 | 599 | 594
2018-08-22 21:30 | 576 | 573
2018-08-22 22:00 | 558 | 554
2018-08-22 22:30 | 535 | 530
2018-08-22 23:00 | 512 | 506
2018-08-22 23:30 | 495 | 488
2018-08-23 | 476 | 466
2018-08-23 00:30 | 432 | 421
2018-08-23 01:00 | 406 | 395
2018-08-23 01:30 | 389 | 375
2018-08-23 02:00 | 375 | 360
2018-08-23 02:30 | 368 | 352
2018-08-23 03:00 | 367 | 352
2018-08-23 03:30 | 368 | 352
2018-08-23 04:00 | 365 | 351
2018-08-23 04:30 | 369 | 356
2018-08-23 05:00 | 378 | 367
2018-08-23 05:30 | 418 | 411
2018-08-23 06:00 | 458 | 452
2018-08-23 06:30 | 527 | 523
2018-08-23 07:00 | 586 | 583
2018-08-23 07:30 | 606 | 603
2018-08-23 08:00 | 599 | 595
2018-08-23 08:30 | 569 | 566
2018-08-23 09:00 | 529 | 524
2018-08-23 09:30 | 496 | 492
2018-08-23 10:00 | 473 | 470
2018-08-23 10:30 | 459 | 457
2018-08-23 11:00 | 448 | 445
2018-08-23 11:30 | 438 | 436
2018-08-23 12:00 | 435 | 433
2018-08-23 12:30 | 431 | 429
2018-08-23 13:00 | 425 | 423
2018-08-23 13:30 | 427 | 425
2018-08-23 14:00 | 435 | 433
2018-08-23 14:30 | 445 | 444
2018-08-23 15:00 | 450 | 449
2018-08-23 15:30 | 461 | 459
2018-08-23 16:00 | 487 | 486
2018-08-23 16:30 | 518 | 517
2018-08-23 17:00 | 554 | 551
2018-08-23 17:30 | 584 | 581
2018-08-23 18:00 | 612 | 608
2018-08-23 18:30 | 636 | 628
2018-08-23 19:00 | 646 | 635
2018-08-23 19:30 | 642 | 631
2018-08-23 20:00 | 629 | 620
2018-08-23 20:30 | 626 | 618
2018-08-23 21:00 | 604 | 596
2018-08-23 21:30 | 579 | 569
2018-08-23 22:00 | 552 | 542
2018-08-23 22:30 | 528 | 520
2018-08-23 23:00 | 508 | 505
2018-08-23 23:30 | 487 | 483
2018-08-24 | 467 | 459
2018-08-24 00:30 | 438 | 429
2018-08-24 01:00 | 414 | 402
2018-08-24 01:30 | 402 | 389
2018-08-24 02:00 | 383 | 368
2018-08-24 02:30 | 368 | 351
2018-08-24 03:00 | 365 | 348
2018-08-24 03:30 | 370 | 352
2018-08-24 04:00 | 366 | 350
2018-08-24 04:30 | 369 | 353
2018-08-24 05:00 | 380 | 366
2018-08-24 05:30 | 418 | 407
2018-08-24 06:00 | 453 | 447
2018-08-24 06:30 | 505 | 496
2018-08-24 07:00 | 552 | 546
2018-08-24 07:30 | 592 | 579
2018-08-24 08:00 | 588 | 574
2018-08-24 08:30 | 561 | 549
2018-08-24 09:00 | 522 | 518
2018-08-24 09:30 | 502 | 496
2018-08-24 10:00 | 490 | 483
2018-08-24 10:30 | 480 | 474
2018-08-24 11:00 | 472 | 466
2018-08-24 11:30 | 463 | 459
2018-08-24 12:00 | 460 | 457
2018-08-24 12:30 | 452 | 450
2018-08-24 13:00 | 455 | 454
2018-08-24 13:30 | 458 | 456
2018-08-24 14:00 | 455 | 453
2018-08-24 14:30 | 451 | 448
2018-08-24 15:00 | 455 | 453
2018-08-24 15:30 | 462 | 460
2018-08-24 16:00 | 483 | 481
2018-08-24 16:30 | 512 | 510
2018-08-24 17:00 | 544 | 540
2018-08-24 17:30 | 561 | 557
2018-08-24 18:00 | 586 | 582
2018-08-24 18:30 | 597 | 589
2018-08-24 19:00 | 599 | 590
2018-08-24 19:30 | 588 | 578
2018-08-24 20:00 | 579 | 574
2018-08-24 20:30 | 577 | 572
2018-08-24 21:00 | 553 | 550
2018-08-24 21:30 | 532 | 529
2018-08-24 22:00 | 515 | 513
2018-08-24 22:30 | 505 | 503
2018-08-24 23:00 | 493 | 490
2018-08-24 23:30 | 479 | 475
2018-08-25 | 458 | 453
2018-08-25 00:30 | 424 | 418
2018-08-25 01:00 | 401 | 393
2018-08-25 01:30 | 385 | 377
2018-08-25 02:00 | 374 | 367
2018-08-25 02:30 | 372 | 365
2018-08-25 03:00 | 373 | 365
2018-08-25 03:30 | 378 | 370
2018-08-25 04:00 | 380 | 371
2018-08-25 04:30 | 373 | 365
2018-08-25 05:00 | 378 | 370
2018-08-25 05:30 | 389 | 382
2018-08-25 06:00 | 397 | 391
2018-08-25 06:30 | 415 | 409
2018-08-25 07:00 | 434 | 429
2018-08-25 07:30 | 461 | 457
2018-08-25 08:00 | 479 | 475
2018-08-25 08:30 | 480 | 475
2018-08-25 09:00 | 472 | 467
2018-08-25 09:30 | 456 | 452
2018-08-25 10:00 | 440 | 437
2018-08-25 10:30 | 421 | 419
2018-08-25 11:00 | 419 | 417
2018-08-25 11:30 | 416 | 414
2018-08-25 12:00 | 407 | 405
2018-08-25 12:30 | 410 | 408
2018-08-25 13:00 | 410 | 408
2018-08-25 13:30 | 393 | 391
2018-08-25 14:00 | 355 | 353
2018-08-25 14:30 | 342 | 340
2018-08-25 15:00 | 363 | 360
2018-08-25 15:30 | 401 | 397
2018-08-25 16:00 | 427 | 424
2018-08-25 16:30 | 460 | 457
2018-08-25 17:00 | 491 | 487
2018-08-25 17:30 | 504 | 500
2018-08-25 18:00 | 530 | 528
2018-08-25 18:30 | 548 | 547
2018-08-25 19:00 | 554 | 552
2018-08-25 19:30 | 537 | 536
2018-08-25 20:00 | 532 | 530
2018-08-25 20:30 | 524 | 523
2018-08-25 21:00 | 507 | 507
2018-08-25 21:30 | 494 | 493
2018-08-25 22:00 | 492 | 491
2018-08-25 22:30 | 486 | 484
2018-08-25 23:00 | 479 | 478
2018-08-25 23:30 | 466 | 464
2018-08-26 | 439 | 437
2018-08-26 00:30 | 408 | 405
2018-08-26 01:00 | 388 | 384
2018-08-26 01:30 | 371 | 366
2018-08-26 02:00 | 351 | 345
2018-08-26 02:30 | 346 | 340
2018-08-26 03:00 | 340 | 333
2018-08-26 03:30 | 338 | 331
2018-08-26 04:00 | 338 | 332
2018-08-26 04:30 | 332 | 324
2018-08-26 05:00 | 335 | 328
2018-08-26 05:30 | 348 | 342
2018-08-26 06:00 | 358 | 352
2018-08-26 06:30 | 370 | 365
2018-08-26 07:00 | 382 | 376
2018-08-26 07:30 | 404 | 399
2018-08-26 08:00 | 426 | 422
2018-08-26 08:30 | 454 | 451
2018-08-26 09:00 | 464 | 462
2018-08-26 09:30 | 484 | 482
2018-08-26 10:00 | 485 | 483
2018-08-26 10:30 | 498 | 496
2018-08-26 11:00 | 503 | 502
2018-08-26 11:30 | 482 | 481
2018-08-26 12:00 | 468 | 467
2018-08-26 12:30 | 454 | 453
2018-08-26 13:00 | 455 | 454
2018-08-26 13:30 | 445 | 443
2018-08-26 14:00 | 423 | 421
2018-08-26 14:30 | 423 | 422
2018-08-26 15:00 | 423 | 422
2018-08-26 15:30 | 449 | 447
2018-08-26 16:00 | 456 | 455
2018-08-26 16:30 | 467 | 465
2018-08-26 17:00 | 497 | 496
2018-08-26 17:30 | 530 | 529
2018-08-26 18:00 | 551 | 551
2018-08-26 18:30 | 577 | 576
2018-08-26 19:00 | 578 | 577
2018-08-26 19:30 | 569 | 568
2018-08-26 20:00 | 561 | 560
2018-08-26 20:30 | 555 | 554
2018-08-26 21:00 | 541 | 540
2018-08-26 21:30 | 525 | 524
2018-08-26 22:00 | 506 | 504
2018-08-26 22:30 | 493 | 492
2018-08-26 23:00 | 481 | 480
2018-08-26 23:30 | 465 | 463
2018-08-27 | 444 | 441
2018-08-27 00:30 | 408 | 404
2018-08-27 01:00 | 386 | 381
2018-08-27 01:30 | 376 | 370
2018-08-27 02:00 | 369 | 362
2018-08-27 02:30 | 361 | 354
2018-08-27 03:00 | 351 | 344
2018-08-27 03:30 | 336 | 329
2018-08-27 04:00 | 336 | 327
2018-08-27 04:30 | 342 | 334
2018-08-27 05:00 | 354 | 348
2018-08-27 05:30 | 385 | 380
2018-08-27 06:00 | 424 | 420
2018-08-27 06:30 | 488 | 486
2018-08-27 07:00 | 545 | 542
2018-08-27 07:30 | 577 | 569
2018-08-27 08:00 | 542 | 532
2018-08-27 08:30 | 495 | 481
2018-08-27 09:00 | 467 | 458
2018-08-27 09:30 | 444 | 439
2018-08-27 10:00 | 429 | 424
2018-08-27 10:30 | 410 | 406
2018-08-27 11:00 | 403 | 401
2018-08-27 11:30 | 400 | 398
2018-08-27 12:00 | 395 | 394
2018-08-27 12:30 | 396 | 394
2018-08-27 13:00 | 394 | 393
2018-08-27 13:30 | 401 | 400
2018-08-27 14:00 | 409 | 408
2018-08-27 14:30 | 411 | 410
2018-08-27 15:00 | 420 | 419
2018-08-27 15:30 | 431 | 430
2018-08-27 16:00 | 440 | 439
2018-08-27 16:30 | 472 | 470
2018-08-27 17:00 | 502 | 498
2018-08-27 17:30 | 535 | 527
2018-08-27 18:00 | 569 | 559
2018-08-27 18:30 | 580 | 569
2018-08-27 19:00 | 582 | 571
2018-08-27 19:30 | 575 | 564
2018-08-27 20:00 | 562 | 551
2018-08-27 20:30 | 555 | 547
2018-08-27 21:00 | 537 | 530
2018-08-27 21:30 | 507 | 502
2018-08-27 22:00 | 484 | 483
2018-08-27 22:30 | 463 | 461
2018-08-27 23:00 | 453 | 451
2018-08-27 23:30 | 443 | 440
2018-08-28 | 423 | 419
2018-08-28 00:30 | 392 | 387
2018-08-28 01:00 | 368 | 361
2018-08-28 01:30 | 355 | 346
2018-08-28 02:00 | 344 | 335
2018-08-28 02:30 | 339 | 330
2018-08-28 03:00 | 323 | 314
2018-08-28 03:30 | 318 | 307
2018-08-28 04:00 | 316 | 305
2018-08-28 04:30 | 329 | 319
2018-08-28 05:00 | 339 | 330
2018-08-28 05:30 | 371 | 364
2018-08-28 06:00 | 408 | 403
2018-08-28 06:30 | 449 | 444
2018-08-28 07:00 | 512 | 507
2018-08-28 07:30 | 545 | 534
2018-08-28 08:00 | 535 | 523
2018-08-28 08:30 | 506 | 493
2018-08-28 09:00 | 473 | 463
2018-08-28 09:30 | 448 | 438
2018-08-28 10:00 | 429 | 421
2018-08-28 10:30 | 416 | 409
2018-08-28 11:00 | 408 | 403
2018-08-28 11:30 | 391 | 390
2018-08-28 12:00 | 387 | 386
2018-08-28 12:30 | 386 | 385
2018-08-28 13:00 | 392 | 392
2018-08-28 13:30 | 398 | 398
2018-08-28 14:00 | 400 | 400
2018-08-28 14:30 | 402 | 402
2018-08-28 15:00 | 409 | 409
2018-08-28 15:30 | 420 | 419
2018-08-28 16:00 | 440 | 440
2018-08-28 16:30 | 468 | 468
2018-08-28 17:00 | 504 | 502
2018-08-28 17:30 | 533 | 524
2018-08-28 18:00 | 553 | 546
2018-08-28 18:30 | 577 | 568
2018-08-28 19:00 | 578 | 570
2018-08-28 19:30 | 577 | 567
2018-08-28 20:00 | 559 | 551
2018-08-28 20:30 | 553 | 547
2018-08-28 21:00 | 539 | 534
2018-08-28 21:30 | 520 | 513
2018-08-28 22:00 | 503 | 494
2018-08-28 22:30 | 481 | 474
2018-08-28 23:00 | 459 | 458
2018-08-28 23:30 | 447 | 444
2018-08-29 | 427 | 424
2018-08-29 00:30 | 387 | 382
2018-08-29 01:00 | 361 | 355
2018-08-29 01:30 | 352 | 344
2018-08-29 02:00 | 343 | 333
2018-08-29 02:30 | 335 | 324
2018-08-29 03:00 | 336 | 326
2018-08-29 03:30 | 330 | 320
2018-08-29 04:00 | 320 | 310
2018-08-29 04:30 | 315 | 305
2018-08-29 05:00 | 326 | 317
2018-08-29 05:30 | 367 | 361
2018-08-29 06:00 | 401 | 398
2018-08-29 06:30 | 459 | 456
2018-08-29 07:00 | 517 | 511
2018-08-29 07:30 | 548 | 537
2018-08-29 08:00 | 540 | 527
2018-08-29 08:30 | 518 | 504
2018-08-29 09:00 | 487 | 471
2018-08-29 09:30 | 449 | 435
2018-08-29 10:00 | 413 | 409
2018-08-29 10:30 | 393 | 390
2018-08-29 11:00 | 377 | 375
2018-08-29 11:30 | 363 | 362
2018-08-29 12:00 | 359 | 358
2018-08-29 12:30 | 353 | 352
2018-08-29 13:00 | 341 | 340
2018-08-29 13:30 | 342 | 341
2018-08-29 14:00 | 350 | 349
2018-08-29 14:30 | 362 | 361
2018-08-29 15:00 | 368 | 367
2018-08-29 15:30 | 392 | 392
2018-08-29 16:00 | 418 | 416
2018-08-29 16:30 | 457 | 451
2018-08-29 17:00 | 491 | 486
2018-08-29 17:30 | 500 | 496
2018-08-29 18:00 | 537 | 531
2018-08-29 18:30 | 569 | 559
2018-08-29 19:00 | 580 | 570
2018-08-29 19:30 | 562 | 552
2018-08-29 20:00 | 548 | 540
2018-08-29 20:30 | 533 | 531
2018-08-29 21:00 | 518 | 516
2018-08-29 21:30 | 506 | 502
2018-08-29 22:00 | 496 | 492
2018-08-29 22:30 | 480 | 477
2018-08-29 23:00 | 468 | 465
2018-08-29 23:30 | 452 | 448
2018-08-30 | 431 | 429
2018-08-30 00:30 | 401 | 398
2018-08-30 01:00 | 372 | 367
2018-08-30 01:30 | 347 | 341
2018-08-30 02:00 | 333 | 325
2018-08-30 02:30 | 327 | 318
2018-08-30 03:00 | 317 | 307
2018-08-30 03:30 | 312 | 302
2018-08-30 04:00 | 311 | 301
2018-08-30 04:30 | 330 | 321
2018-08-30 05:00 | 338 | 330
2018-08-30 05:30 | 376 | 371
2018-08-30 06:00 | 419 | 416
2018-08-30 06:30 | 474 | 472
2018-08-30 07:00 | 523 | 521
2018-08-30 07:30 | 542 | 541
2018-08-30 08:00 | 533 | 530
2018-08-30 08:30 | 506 | 502
2018-08-30 09:00 | 482 | 478
2018-08-30 09:30 | 458 | 454
2018-08-30 10:00 | 428 | 425
2018-08-30 10:30 | 413 | 412
2018-08-30 11:00 | 397 | 396
2018-08-30 11:30 | 392 | 392
2018-08-30 12:00 | 389 | 388
2018-08-30 12:30 | 389 | 388
2018-08-30 13:00 | 395 | 394
2018-08-30 13:30 | 399 | 399
2018-08-30 14:00 | 404 | 404
2018-08-30 14:30 | 411 | 411
2018-08-30 15:00 | 423 | 422
2018-08-30 15:30 | 436 | 435
2018-08-30 16:00 | 450 | 449
2018-08-30 16:30 | 477 | 476
2018-08-30 17:00 | 498 | 497
2018-08-30 17:30 | 515 | 513
2018-08-30 18:00 | 535 | 531
2018-08-30 18:30 | 553 | 544
2018-08-30 19:00 | 554 | 545
2018-08-30 19:30 | 546 | 538
2018-08-30 20:00 | 544 | 537
2018-08-30 20:30 | 550 | 543
2018-08-30 21:00 | 542 | 534
2018-08-30 21:30 | 506 | 503
2018-08-30 22:00 | 477 | 476
2018-08-30 22:30 | 463 | 462
2018-08-30 23:00 | 452 | 450
2018-08-30 23:30 | 434 | 432
2018-08-31 | 419 | 416
2018-08-31 00:30 | 375 | 370
2018-08-31 01:00 | 356 | 349
2018-08-31 01:30 | 341 | 334
2018-08-31 02:00 | 335 | 326
2018-08-31 02:30 | 321 | 311
2018-08-31 03:00 | 315 | 304
2018-08-31 03:30 | 317 | 307
2018-08-31 04:00 | 318 | 308
2018-08-31 04:30 | 317 | 307
2018-08-31 05:00 | 323 | 314
2018-08-31 05:30 | 349 | 343
2018-08-31 06:00 | 368 | 365
2018-08-31 06:30 | 423 | 420
2018-08-31 07:00 | 469 | 467
2018-08-31 07:30 | 506 | 500
2018-08-31 08:00 | 507 | 497
2018-08-31 08:30 | 488 | 476
2018-08-31 09:00 | 461 | 455
2018-08-31 09:30 | 439 | 436
2018-08-31 10:00 | 421 | 418
2018-08-31 10:30 | 409 | 407
2018-08-31 11:00 | 403 | 401
2018-08-31 11:30 | 396 | 394
2018-08-31 12:00 | 388 | 386
2018-08-31 12:30 | 380 | 379
2018-08-31 13:00 | 381 | 380
2018-08-31 13:30 | 382 | 382
2018-08-31 14:00 | 390 | 389
2018-08-31 14:30 | 400 | 400
2018-08-31 15:00 | 443 | 442
2018-08-31 15:30 | 467 | 466
2018-08-31 16:00 | 486 | 485
2018-08-31 16:30 | 519 | 518
2018-08-31 17:00 | 550 | 548
2018-08-31 17:30 | 561 | 559
2018-08-31 18:00 | 567 | 565
2018-08-31 18:30 | 578 | 576
2018-08-31 19:00 | 586 | 584
2018-08-31 19:30 | 578 | 576
2018-08-31 20:00 | 576 | 573
2018-08-31 20:30 | 574 | 570
2018-08-31 21:00 | 561 | 557
2018-08-31 21:30 | 532 | 529
2018-08-31 22:00 | 516 | 513
2018-08-31 22:30 | 509 | 505
2018-08-31 23:00 | 509 | 504
2018-08-31 23:30 | 488 | 484
2018-09-01 | 463 | 456
2018-09-01 00:30 | 421 | 411
2018-09-01 01:00 | 397 | 381
2018-09-01 01:30 | 378 | 359
2018-09-01 02:00 | 373 | 353
2018-09-01 02:30 | 356 | 334
2018-09-01 03:00 | 342 | 318
2018-09-01 03:30 | 335 | 310
2018-09-01 04:00 | 329 | 304
2018-09-01 04:30 | 334 | 309
2018-09-01 05:00 | 335 | 312
2018-09-01 05:30 | 351 | 329
2018-09-01 06:00 | 366 | 345
2018-09-01 06:30 | 395 | 376
2018-09-01 07:00 | 410 | 391
2018-09-01 07:30 | 428 | 412
2018-09-01 08:00 | 435 | 423
2018-09-01 08:30 | 452 | 440
2018-09-01 09:00 | 455 | 446
2018-09-01 09:30 | 435 | 426
2018-09-01 10:00 | 416 | 406
2018-09-01 10:30 | 412 | 403
2018-09-01 11:00 | 413 | 404
2018-09-01 11:30 | 366 | 356
2018-09-01 12:00 | 341 | 330
2018-09-01 12:30 | 330 | 318
2018-09-01 13:00 | 336 | 324
2018-09-01 13:30 | 329 | 317
2018-09-01 14:00 | 340 | 329
2018-09-01 14:30 | 349 | 338
2018-09-01 15:00 | 372 | 362
2018-09-01 15:30 | 383 | 374
2018-09-01 16:00 | 408 | 400
2018-09-01 16:30 | 441 | 434
2018-09-01 17:00 | 462 | 456
2018-09-01 17:30 | 471 | 466
2018-09-01 18:00 | 489 | 485
2018-09-01 18:30 | 510 | 507
2018-09-01 19:00 | 508 | 504
2018-09-01 19:30 | 503 | 499
2018-09-01 20:00 | 497 | 493
2018-09-01 20:30 | 500 | 495
2018-09-01 21:00 | 491 | 486
2018-09-01 21:30 | 481 | 475
2018-09-01 22:00 | 475 | 468
2018-09-01 22:30 | 464 | 456
2018-09-01 23:00 | 459 | 451
2018-09-01 23:30 | 449 | 440
2018-09-02 | 432 | 421
2018-09-02 00:30 | 397 | 382
2018-09-02 01:00 | 371 | 352
2018-09-02 01:30 | 359 | 339
2018-09-02 02:00 | 350 | 328
2018-09-02 02:30 | 348 | 317
2018-09-02 03:00 | 345 | 314
2018-09-02 03:30 | 346 | 315
2018-09-02 04:00 | 352 | 320
2018-09-02 04:30 | 354 | 323
2018-09-02 05:00 | 350 | 318
2018-09-02 05:30 | 361 | 331
2018-09-02 06:00 | 370 | 341
2018-09-02 06:30 | 374 | 343
2018-09-02 07:00 | 384 | 355
2018-09-02 07:30 | 397 | 371
2018-09-02 08:00 | 407 | 383
2018-09-02 08:30 | 413 | 391
2018-09-02 09:00 | 413 | 393
2018-09-02 09:30 | 408 | 388
2018-09-02 10:00 | 396 | 377
2018-09-02 10:30 | 383 | 364
2018-09-02 11:00 | 368 | 349
2018-09-02 11:30 | 357 | 337
2018-09-02 12:00 | 352 | 332
2018-09-02 12:30 | 339 | 317
2018-09-02 13:00 | 334 | 311
2018-09-02 13:30 | 337 | 314
2018-09-02 14:00 | 348 | 326
2018-09-02 14:30 | 361 | 341
2018-09-02 15:00 | 377 | 358
2018-09-02 15:30 | 399 | 382
2018-09-02 16:00 | 422 | 407
2018-09-02 16:30 | 453 | 439
2018-09-02 17:00 | 474 | 462
2018-09-02 17:30 | 484 | 473
2018-09-02 18:00 | 494 | 486
2018-09-02 18:30 | 529 | 524
2018-09-02 19:00 | 545 | 541
2018-09-02 19:30 | 515 | 511
2018-09-02 20:00 | 510 | 506
2018-09-02 20:30 | 524 | 519
2018-09-02 21:00 | 510 | 504
2018-09-02 21:30 | 490 | 483
2018-09-02 22:00 | 478 | 469
2018-09-02 22:30 | 465 | 455
2018-09-02 23:00 | 458 | 447
2018-09-02 23:30 | 445 | 433
2018-09-03 | 427 | 412
2018-09-03 00:30 | 394 | 377
2018-09-03 01:00 | 376 | 356
2018-09-03 01:30 | 363 | 340
2018-09-03 02:00 | 356 | 328
2018-09-03 02:30 | 348 | 317
2018-09-03 03:00 | 344 | 312
2018-09-03 03:30 | 351 | 319
2018-09-03 04:00 | 352 | 319
2018-09-03 04:30 | 355 | 324
2018-09-03 05:00 | 370 | 344
2018-09-03 05:30 | 394 | 373
2018-09-03 06:00 | 424 | 408
2018-09-03 06:30 | 473 | 463
2018-09-03 07:00 | 526 | 519
2018-09-03 07:30 | 578 | 564
2018-09-03 08:00 | 593 | 577
2018-09-03 08:30 | 581 | 565
2018-09-03 09:00 | 550 | 534
2018-09-03 09:30 | 525 | 515
2018-09-03 10:00 | 512 | 505
2018-09-03 10:30 | 500 | 494
2018-09-03 11:00 | 500 | 494
2018-09-03 11:30 | 506 | 501
2018-09-03 12:00 | 505 | 500
2018-09-03 12:30 | 508 | 503
2018-09-03 13:00 | 511 | 505
2018-09-03 13:30 | 504 | 498
2018-09-03 14:00 | 500 | 494
2018-09-03 14:30 | 510 | 505
2018-09-03 15:00 | 513 | 507
2018-09-03 15:30 | 521 | 515
2018-09-03 16:00 | 533 | 527
2018-09-03 16:30 | 553 | 547
2018-09-03 17:00 | 574 | 569
2018-09-03 17:30 | 594 | 590
2018-09-03 18:00 | 617 | 613
2018-09-03 18:30 | 638 | 633
2018-09-03 19:00 | 639 | 633
2018-09-03 19:30 | 633 | 627
2018-09-03 20:00 | 608 | 602
2018-09-03 20:30 | 610 | 606
2018-09-03 21:00 | 583 | 577
2018-09-03 21:30 | 561 | 554
2018-09-03 22:00 | 538 | 531
2018-09-03 22:30 | 523 | 515
2018-09-03 23:00 | 503 | 494
2018-09-03 23:30 | 483 | 472
2018-09-04 | 466 | 452
2018-09-04 00:30 | 432 | 414
2018-09-04 01:00 | 412 | 391
2018-09-04 01:30 | 401 | 380
2018-09-04 02:00 | 387 | 362
2018-09-04 02:30 | 368 | 342
2018-09-04 03:00 | 364 | 337
2018-09-04 03:30 | 364 | 336
2018-09-04 04:00 | 362 | 335
2018-09-04 04:30 | 362 | 337
2018-09-04 05:00 | 372 | 349
2018-09-04 05:30 | 404 | 386
2018-09-04 06:00 | 442 | 427
2018-09-04 06:30 | 488 | 479
2018-09-04 07:00 | 564 | 554
2018-09-04 07:30 | 587 | 581
2018-09-04 08:00 | 585 | 578
2018-09-04 08:30 | 572 | 565
2018-09-04 09:00 | 548 | 540
2018-09-04 09:30 | 538 | 530
2018-09-04 10:00 | 510 | 503
2018-09-04 10:30 | 478 | 471
2018-09-04 11:00 | 468 | 461
2018-09-04 11:30 | 460 | 452
2018-09-04 12:00 | 451 | 444
2018-09-04 12:30 | 459 | 453
2018-09-04 13:00 | 459 | 453
2018-09-04 13:30 | 469 | 463
2018-09-04 14:00 | 486 | 481
2018-09-04 14:30 | 485 | 479
2018-09-04 15:00 | 485 | 479
2018-09-04 15:30 | 496 | 490
2018-09-04 16:00 | 520 | 515
2018-09-04 16:30 | 543 | 538
2018-09-04 17:00 | 567 | 561
2018-09-04 17:30 | 591 | 587
2018-09-04 18:00 | 621 | 619
2018-09-04 18:30 | 639 | 636
2018-09-04 19:00 | 642 | 639
2018-09-04 19:30 | 621 | 617
2018-09-04 20:00 | 606 | 603
2018-09-04 20:30 | 604 | 600
2018-09-04 21:00 | 591 | 586
2018-09-04 21:30 | 572 | 565
2018-09-04 22:00 | 549 | 541
2018-09-04 22:30 | 526 | 519
2018-09-04 23:00 | 502 | 494
2018-09-04 23:30 | 487 | 478
2018-09-05 | 467 | 456
2018-09-05 00:30 | 436 | 421
2018-09-05 01:00 | 416 | 397
2018-09-05 01:30 | 405 | 384
2018-09-05 02:00 | 390 | 368
2018-09-05 02:30 | 378 | 355
2018-09-05 03:00 | 367 | 341
2018-09-05 03:30 | 356 | 328
2018-09-05 04:00 | 355 | 326
2018-09-05 04:30 | 361 | 334
2018-09-05 05:00 | 369 | 345
2018-09-05 05:30 | 405 | 385
2018-09-05 06:00 | 442 | 428
2018-09-05 06:30 | 500 | 491
2018-09-05 07:00 | 567 | 557
2018-09-05 07:30 | 595 | 583
2018-09-05 08:00 | 596 | 584
2018-09-05 08:30 | 612 | 598
2018-09-05 09:00 | 683 | 673
2018-09-05 09:30 | 653 | 646
2018-09-05 10:00 | 650 | 644
2018-09-05 10:30 | 629 | 624
2018-09-05 11:00 | 616 | 611
2018-09-05 11:30 | 606 | 601
2018-09-05 12:00 | 601 | 596
2018-09-05 12:30 | 598 | 592
2018-09-05 13:00 | 601 | 596
2018-09-05 13:30 | 616 | 611
2018-09-05 14:00 | 627 | 623
2018-09-05 14:30 | 646 | 642
2018-09-05 15:00 | 637 | 633
2018-09-05 15:30 | 636 | 631
2018-09-05 16:00 | 650 | 646
2018-09-05 16:30 | 676 | 671
2018-09-05 17:00 | 700 | 696
2018-09-05 17:30 | 738 | 734
2018-09-05 18:00 | 763 | 757
2018-09-05 18:30 | 805 | 794
2018-09-05 19:00 | 814 | 803
2018-09-05 19:30 | 782 | 772
2018-09-05 20:00 | 759 | 750
2018-09-05 20:30 | 759 | 751
2018-09-05 21:00 | 743 | 738
2018-09-05 21:30 | 727 | 721
2018-09-05 22:00 | 699 | 692
2018-09-05 22:30 | 664 | 656
2018-09-05 23:00 | 629 | 622
2018-09-05 23:30 | 617 | 611
2018-09-06 | 600 | 592
2018-09-06 00:30 | 556 | 547
2018-09-06 01:00 | 525 | 513
2018-09-06 01:30 | 510 | 497
2018-09-06 02:00 | 477 | 462
2018-09-06 02:30 | 475 | 459
2018-09-06 03:00 | 489 | 473
2018-09-06 03:30 | 492 | 476
2018-09-06 04:00 | 502 | 487
2018-09-06 04:30 | 495 | 480
2018-09-06 05:00 | 503 | 490
2018-09-06 05:30 | 511 | 500
2018-09-06 06:00 | 578 | 569
2018-09-06 06:30 | 654 | 647
2018-09-06 07:00 | 734 | 728
2018-09-06 07:30 | 749 | 744
2018-09-06 08:00 | 735 | 731
2018-09-06 08:30 | 712 | 707
2018-09-06 09:00 | 692 | 686
2018-09-06 09:30 | 685 | 680
2018-09-06 10:00 | 664 | 660
2018-09-06 10:30 | 639 | 637
2018-09-06 11:00 | 635 | 633
2018-09-06 11:30 | 632 | 630
2018-09-06 12:00 | 639 | 636
2018-09-06 12:30 | 632 | 629
2018-09-06 13:00 | 633 | 630
2018-09-06 13:30 | 629 | 626
2018-09-06 14:00 | 639 | 636
2018-09-06 14:30 | 639 | 636
2018-09-06 15:00 | 648 | 645
2018-09-06 15:30 | 648 | 645
2018-09-06 16:00 | 665 | 662
2018-09-06 16:30 | 691 | 689
2018-09-06 17:00 | 734 | 731
2018-09-06 17:30 | 744 | 738
2018-09-06 18:00 | 753 | 748
2018-09-06 18:30 | 773 | 761
2018-09-06 19:00 | 778 | 767
2018-09-06 19:30 | 770 | 760
2018-09-06 20:00 | 744 | 735
2018-09-06 20:30 | 744 | 736
2018-09-06 21:00 | 727 | 719
2018-09-06 21:30 | 696 | 688
2018-09-06 22:00 | 668 | 666
2018-09-06 22:30 | 647 | 645
2018-09-06 23:00 | 614 | 611
2018-09-06 23:30 | 600 | 596
2018-09-07 | 586 | 579
2018-09-07 00:30 | 559 | 551
2018-09-07 01:00 | 536 | 527
2018-09-07 01:30 | 531 | 521
2018-09-07 02:00 | 495 | 484
2018-09-07 02:30 | 477 | 464
2018-09-07 03:00 | 456 | 442
2018-09-07 03:30 | 459 | 446
2018-09-07 04:00 | 466 | 453
2018-09-07 04:30 | 477 | 465
2018-09-07 05:00 | 480 | 469
2018-09-07 05:30 | 492 | 484
2018-09-07 06:00 | 542 | 535
2018-09-07 06:30 | 611 | 605
2018-09-07 07:00 | 666 | 661
2018-09-07 07:30 | 701 | 697
2018-09-07 08:00 | 725 | 720
2018-09-07 08:30 | 700 | 695
2018-09-07 09:00 | 642 | 639
2018-09-07 09:30 | 627 | 624
2018-09-07 10:00 | 618 | 615
2018-09-07 10:30 | 649 | 646
2018-09-07 11:00 | 649 | 645
2018-09-07 11:30 | 640 | 636
2018-09-07 12:00 | 656 | 652
2018-09-07 12:30 | 667 | 664
2018-09-07 13:00 | 657 | 653
2018-09-07 13:30 | 660 | 656
2018-09-07 14:00 | 656 | 653
2018-09-07 14:30 | 654 | 651
2018-09-07 15:00 | 659 | 656
2018-09-07 15:30 | 671 | 667
2018-09-07 16:00 | 689 | 686
2018-09-07 16:30 | 718 | 714
2018-09-07 17:00 | 733 | 729
2018-09-07 17:30 | 749 | 746
2018-09-07 18:00 | 787 | 778
2018-09-07 18:30 | 800 | 791
2018-09-07 19:00 | 797 | 787
2018-09-07 19:30 | 778 | 768
2018-09-07 20:00 | 774 | 765
2018-09-07 20:30 | 791 | 781
2018-09-07 21:00 | 767 | 763
2018-09-07 21:30 | 743 | 739
2018-09-07 22:00 | 719 | 715
2018-09-07 22:30 | 672 | 670
2018-09-07 23:00 | 641 | 638
2018-09-07 23:30 | 617 | 613
2018-09-08 | 573 | 567
2018-09-08 00:30 | 534 | 527
2018-09-08 01:00 | 506 | 497
2018-09-08 01:30 | 479 | 468
2018-09-08 02:00 | 466 | 453
2018-09-08 02:30 | 456 | 444
2018-09-08 03:00 | 450 | 437
2018-09-08 03:30 | 443 | 430
2018-09-08 04:00 | 448 | 434
2018-09-08 04:30 | 443 | 430
2018-09-08 05:00 | 441 | 428
2018-09-08 05:30 | 462 | 449
2018-09-08 06:00 | 475 | 463
2018-09-08 06:30 | 497 | 486
2018-09-08 07:00 | 530 | 520
2018-09-08 07:30 | 564 | 556
2018-09-08 08:00 | 596 | 590
2018-09-08 08:30 | 613 | 607
2018-09-08 09:00 | 630 | 625
2018-09-08 09:30 | 669 | 664
2018-09-08 10:00 | 694 | 688
2018-09-08 10:30 | 662 | 656
2018-09-08 11:00 | 629 | 624
2018-09-08 11:30 | 601 | 595
2018-09-08 12:00 | 583 | 578
2018-09-08 12:30 | 570 | 565
2018-09-08 13:00 | 550 | 545
2018-09-08 13:30 | 443 | 440
2018-09-08 14:00 | 460 | 457
2018-09-08 14:30 | 452 | 448
2018-09-08 15:00 | 453 | 449
2018-09-08 15:30 | 453 | 449
2018-09-08 16:00 | 455 | 451
2018-09-08 16:30 | 480 | 476
2018-09-08 17:00 | 518 | 515
2018-09-08 17:30 | 525 | 522
2018-09-08 18:00 | 534 | 532
2018-09-08 18:30 | 540 | 538
2018-09-08 19:00 | 537 | 535
2018-09-08 19:30 | 533 | 530
2018-09-08 20:00 | 533 | 531
2018-09-08 20:30 | 535 | 533
2018-09-08 21:00 | 516 | 514
2018-09-08 21:30 | 505 | 503
2018-09-08 22:00 | 498 | 495
2018-09-08 22:30 | 493 | 490
2018-09-08 23:00 | 491 | 487
2018-09-08 23:30 | 479 | 475
2018-09-09 | 465 | 460
2018-09-09 00:30 | 439 | 432
2018-09-09 01:00 | 416 | 406
2018-09-09 01:30 | 385 | 375
2018-09-09 02:00 | 362 | 350
2018-09-09 02:30 | 342 | 329
2018-09-09 03:00 | 340 | 327
2018-09-09 03:30 | 333 | 319
2018-09-09 04:00 | 337 | 323
2018-09-09 04:30 | 339 | 325
2018-09-09 05:00 | 347 | 333
2018-09-09 05:30 | 345 | 332
2018-09-09 06:00 | 353 | 338
2018-09-09 06:30 | 366 | 350
2018-09-09 07:00 | 375 | 360
2018-09-09 07:30 | 390 | 376
2018-09-09 08:00 | 392 | 379
2018-09-09 08:30 | 378 | 365
2018-09-09 09:00 | 385 | 374
2018-09-09 09:30 | 383 | 372
2018-09-09 10:00 | 381 | 371
2018-09-09 10:30 | 369 | 360
2018-09-09 11:00 | 360 | 351
2018-09-09 11:30 | 359 | 350
2018-09-09 12:00 | 341 | 332
2018-09-09 12:30 | 341 | 331
2018-09-09 13:00 | 342 | 333
2018-09-09 13:30 | 340 | 331
2018-09-09 14:00 | 346 | 337
2018-09-09 14:30 | 349 | 341
2018-09-09 15:00 | 362 | 354
2018-09-09 15:30 | 375 | 369
2018-09-09 16:00 | 398 | 392
2018-09-09 16:30 | 425 | 420
2018-09-09 17:00 | 446 | 441
2018-09-09 17:30 | 486 | 483
2018-09-09 18:00 | 504 | 502
2018-09-09 18:30 | 538 | 537
2018-09-09 19:00 | 546 | 545
2018-09-09 19:30 | 529 | 528
2018-09-09 20:00 | 518 | 516
2018-09-09 20:30 | 515 | 513
2018-09-09 21:00 | 498 | 495
2018-09-09 21:30 | 486 | 483
2018-09-09 22:00 | 475 | 471
2018-09-09 22:30 | 470 | 465
2018-09-09 23:00 | 456 | 451
2018-09-09 23:30 | 447 | 440
2018-09-10 | 436 | 428
2018-09-10 00:30 | 397 | 387
2018-09-10 01:00 | 378 | 367
2018-09-10 01:30 | 356 | 343
2018-09-10 02:00 | 355 | 342
2018-09-10 02:30 | 350 | 336
2018-09-10 03:00 | 354 | 340
2018-09-10 03:30 | 353 | 340
2018-09-10 04:00 | 351 | 338
2018-09-10 04:30 | 357 | 345
2018-09-10 05:00 | 374 | 363
2018-09-10 05:30 | 410 | 402
2018-09-10 06:00 | 441 | 435
2018-09-10 06:30 | 504 | 495
2018-09-10 07:00 | 548 | 538
2018-09-10 07:30 | 576 | 565
2018-09-10 08:00 | 573 | 562
2018-09-10 08:30 | 555 | 544
2018-09-10 09:00 | 530 | 518
2018-09-10 09:30 | 500 | 497
2018-09-10 10:00 | 483 | 481
2018-09-10 10:30 | 467 | 465
2018-09-10 11:00 | 454 | 452
2018-09-10 11:30 | 434 | 434
2018-09-10 12:00 | 425 | 425
2018-09-10 12:30 | 426 | 426
2018-09-10 13:00 | 428 | 428
2018-09-10 13:30 | 438 | 438
2018-09-10 14:00 | 455 | 455
2018-09-10 14:30 | 473 | 473
2018-09-10 15:00 | 482 | 482
2018-09-10 15:30 | 503 | 503
2018-09-10 16:00 | 520 | 520
2018-09-10 16:30 | 552 | 551
2018-09-10 17:00 | 574 | 573
2018-09-10 17:30 | 580 | 578
2018-09-10 18:00 | 604 | 602
2018-09-10 18:30 | 620 | 617
2018-09-10 19:00 | 619 | 615
2018-09-10 19:30 | 613 | 609
2018-09-10 20:00 | 595 | 592
2018-09-10 20:30 | 591 | 588
2018-09-10 21:00 | 573 | 570
2018-09-10 21:30 | 549 | 547
2018-09-10 22:00 | 549 | 546
2018-09-10 22:30 | 529 | 525
2018-09-10 23:00 | 519 | 517
2018-09-10 23:30 | 516 | 512
2018-09-11 | 493 | 488
2018-09-11 00:30 | 440 | 434
2018-09-11 01:00 | 413 | 405
2018-09-11 01:30 | 388 | 379
2018-09-11 02:00 | 382 | 372
2018-09-11 02:30 | 380 | 371
2018-09-11 03:00 | 381 | 372
2018-09-11 03:30 | 368 | 359
2018-09-11 04:00 | 362 | 353
2018-09-11 04:30 | 375 | 366
2018-09-11 05:00 | 386 | 378
2018-09-11 05:30 | 412 | 406
2018-09-11 06:00 | 432 | 429
2018-09-11 06:30 | 487 | 485
2018-09-11 07:00 | 544 | 543
2018-09-11 07:30 | 577 | 576
2018-09-11 08:00 | 567 | 564
2018-09-11 08:30 | 545 | 542
2018-09-11 09:00 | 505 | 502
2018-09-11 09:30 | 491 | 488
2018-09-11 10:00 | 469 | 469
2018-09-11 10:30 | 463 | 462
2018-09-11 11:00 | 460 | 460
2018-09-11 11:30 | 453 | 453
2018-09-11 12:00 | 446 | 446
2018-09-11 12:30 | 449 | 449
2018-09-11 13:00 | 451 | 451
2018-09-11 13:30 | 454 | 454
2018-09-11 14:00 | 467 | 467
2018-09-11 14:30 | 473 | 473
2018-09-11 15:00 | 482 | 482
2018-09-11 15:30 | 500 | 500
2018-09-11 16:00 | 522 | 522
2018-09-11 16:30 | 540 | 539
2018-09-11 17:00 | 571 | 569
2018-09-11 17:30 | 594 | 592
2018-09-11 18:00 | 613 | 612
2018-09-11 18:30 | 619 | 618
2018-09-11 19:00 | 615 | 614
2018-09-11 19:30 | 604 | 603
2018-09-11 20:00 | 589 | 587
2018-09-11 20:30 | 586 | 585
2018-09-11 21:00 | 568 | 567
2018-09-11 21:30 | 543 | 542
2018-09-11 22:00 | 514 | 514
2018-09-11 22:30 | 501 | 501
2018-09-11 23:00 | 487 | 486
2018-09-11 23:30 | 470 | 468
2018-09-12 | 456 | 454
2018-09-12 00:30 | 419 | 415
2018-09-12 01:00 | 397 | 392
2018-09-12 01:30 | 378 | 372
2018-09-12 02:00 | 362 | 355
2018-09-12 02:30 | 352 | 344
2018-09-12 03:00 | 361 | 353
2018-09-12 03:30 | 361 | 352
2018-09-12 04:00 | 358 | 348
2018-09-12 04:30 | 354 | 345
2018-09-12 05:00 | 367 | 359
2018-09-12 05:30 | 404 | 399
2018-09-12 06:00 | 435 | 431
2018-09-12 06:30 | 483 | 480
2018-09-12 07:00 | 547 | 542
2018-09-12 07:30 | 604 | 596
2018-09-12 08:00 | 632 | 626
2018-09-12 08:30 | 614 | 607
2018-09-12 09:00 | 590 | 584
2018-09-12 09:30 | 560 | 553
2018-09-12 10:00 | 538 | 538
2018-09-12 10:30 | 543 | 543
2018-09-12 11:00 | 530 | 530
2018-09-12 11:30 | 515 | 515
2018-09-12 12:00 | 511 | 511
2018-09-12 12:30 | 513 | 513
2018-09-12 13:00 | 508 | 508
2018-09-12 13:30 | 507 | 507
2018-09-12 14:00 | 514 | 513
2018-09-12 14:30 | 521 | 520
2018-09-12 15:00 | 528 | 528
2018-09-12 15:30 | 544 | 544
2018-09-12 16:00 | 578 | 578
2018-09-12 16:30 | 610 | 610
2018-09-12 17:00 | 644 | 642
2018-09-12 17:30 | 671 | 664
2018-09-12 18:00 | 692 | 686
2018-09-12 18:30 | 704 | 698
2018-09-12 19:00 | 714 | 708
2018-09-12 19:30 | 701 | 694
2018-09-12 20:00 | 695 | 686
2018-09-12 20:30 | 676 | 674
2018-09-12 21:00 | 655 | 653
2018-09-12 21:30 | 636 | 633
2018-09-12 22:00 | 618 | 615
2018-09-12 22:30 | 604 | 602
2018-09-12 23:00 | 583 | 583
2018-09-12 23:30 | 562 | 561
2018-09-13 | 531 | 528
2018-09-13 00:30 | 487 | 483
2018-09-13 01:00 | 466 | 461
2018-09-13 01:30 | 451 | 444
2018-09-13 02:00 | 436 | 429
2018-09-13 02:30 | 422 | 415
2018-09-13 03:00 | 416 | 408
2018-09-13 03:30 | 409 | 401
2018-09-13 04:00 | 410 | 403
2018-09-13 04:30 | 420 | 413
2018-09-13 05:00 | 436 | 431
2018-09-13 05:30 | 464 | 461
2018-09-13 06:00 | 491 | 488
2018-09-13 06:30 | 559 | 553
2018-09-13 07:00 | 620 | 608
2018-09-13 07:30 | 638 | 625
2018-09-13 08:00 | 634 | 621
2018-09-13 08:30 | 610 | 597
2018-09-13 09:00 | 576 | 562
2018-09-13 09:30 | 535 | 531
2018-09-13 10:00 | 517 | 515
2018-09-13 10:30 | 507 | 506
2018-09-13 11:00 | 489 | 488
2018-09-13 11:30 | 485 | 485
2018-09-13 12:00 | 495 | 495
2018-09-13 12:30 | 488 | 488
2018-09-13 13:00 | 490 | 490
2018-09-13 13:30 | 500 | 500
2018-09-13 14:00 | 514 | 514
2018-09-13 14:30 | 528 | 528
2018-09-13 15:00 | 543 | 543
2018-09-13 15:30 | 567 | 567
2018-09-13 16:00 | 593 | 593
2018-09-13 16:30 | 623 | 622
2018-09-13 17:00 | 650 | 649
2018-09-13 17:30 | 662 | 660
2018-09-13 18:00 | 684 | 681
2018-09-13 18:30 | 703 | 695
2018-09-13 19:00 | 716 | 708
2018-09-13 19:30 | 691 | 686
2018-09-13 20:00 | 682 | 678
2018-09-13 20:30 | 676 | 671
2018-09-13 21:00 | 655 | 649
2018-09-13 21:30 | 632 | 624
2018-09-13 22:00 | 615 | 605
2018-09-13 22:30 | 595 | 587
2018-09-13 23:00 | 579 | 571
2018-09-13 23:30 | 544 | 543
2018-09-14 | 511 | 509
2018-09-14 00:30 | 462 | 458
2018-09-14 01:00 | 433 | 428
2018-09-14 01:30 | 420 | 413
2018-09-14 02:00 | 411 | 404
2018-09-14 02:30 | 408 | 400
2018-09-14 03:00 | 402 | 394
2018-09-14 03:30 | 402 | 394
2018-09-14 04:00 | 404 | 396
2018-09-14 04:30 | 411 | 404
2018-09-14 05:00 | 422 | 416
2018-09-14 05:30 | 448 | 443
2018-09-14 06:00 | 466 | 463
2018-09-14 06:30 | 510 | 509
2018-09-14 07:00 | 558 | 558
2018-09-14 07:30 | 585 | 581
2018-09-14 08:00 | 581 | 573
2018-09-14 08:30 | 550 | 542
2018-09-14 09:00 | 479 | 471
2018-09-14 09:30 | 481 | 474
2018-09-14 10:00 | 473 | 467
2018-09-14 10:30 | 467 | 461
2018-09-14 11:00 | 463 | 457
2018-09-14 11:30 | 451 | 445
2018-09-14 12:00 | 437 | 431
2018-09-14 12:30 | 448 | 442
2018-09-14 13:00 | 455 | 449
2018-09-14 13:30 | 451 | 445
2018-09-14 14:00 | 454 | 449
2018-09-14 14:30 | 462 | 457
2018-09-14 15:00 | 478 | 473
2018-09-14 15:30 | 491 | 486
2018-09-14 16:00 | 505 | 500
2018-09-14 16:30 | 523 | 517
2018-09-14 17:00 | 550 | 544
2018-09-14 17:30 | 555 | 550
2018-09-14 18:00 | 572 | 566
2018-09-14 18:30 | 581 | 574
2018-09-14 19:00 | 584 | 577
2018-09-14 19:30 | 559 | 555
2018-09-14 20:00 | 542 | 541
2018-09-14 20:30 | 533 | 531
2018-09-14 21:00 | 519 | 518
2018-09-14 21:30 | 505 | 504
2018-09-14 22:00 | 491 | 489
2018-09-14 22:30 | 488 | 485
2018-09-14 23:00 | 470 | 468
2018-09-14 23:30 | 451 | 447
2018-09-15 | 429 | 424
2018-09-15 00:30 | 407 | 400
2018-09-15 01:00 | 391 | 382
2018-09-15 01:30 | 379 | 370
2018-09-15 02:00 | 359 | 349
2018-09-15 02:30 | 358 | 347
2018-09-15 03:00 | 354 | 343
2018-09-15 03:30 | 355 | 344
2018-09-15 04:00 | 352 | 339
2018-09-15 04:30 | 348 | 335
2018-09-15 05:00 | 350 | 338
2018-09-15 05:30 | 362 | 351
2018-09-15 06:00 | 371 | 360
2018-09-15 06:30 | 385 | 375
2018-09-15 07:00 | 398 | 389
2018-09-15 07:30 | 407 | 399
2018-09-15 08:00 | 422 | 416
2018-09-15 08:30 | 423 | 418
2018-09-15 09:00 | 417 | 412
2018-09-15 09:30 | 408 | 403
2018-09-15 10:00 | 399 | 395
2018-09-15 10:30 | 373 | 368
2018-09-15 11:00 | 367 | 363
2018-09-15 11:30 | 356 | 351
2018-09-15 12:00 | 358 | 353
2018-09-15 12:30 | 353 | 348
2018-09-15 13:00 | 370 | 365
2018-09-15 13:30 | 362 | 358
2018-09-15 14:00 | 384 | 379
2018-09-15 14:30 | 389 | 384
2018-09-15 15:00 | 392 | 388
2018-09-15 15:30 | 416 | 412
2018-09-15 16:00 | 438 | 434
2018-09-15 16:30 | 464 | 460
2018-09-15 17:00 | 484 | 481
2018-09-15 17:30 | 493 | 491
2018-09-15 18:00 | 518 | 516
2018-09-15 18:30 | 529 | 527
2018-09-15 19:00 | 533 | 532
2018-09-15 19:30 | 527 | 525
2018-09-15 20:00 | 515 | 514
2018-09-15 20:30 | 503 | 501
2018-09-15 21:00 | 492 | 490
2018-09-15 21:30 | 472 | 468
2018-09-15 22:00 | 472 | 468
2018-09-15 22:30 | 461 | 457
2018-09-15 23:00 | 447 | 442
2018-09-15 23:30 | 441 | 435
2018-09-16 | 426 | 418
2018-09-16 00:30 | 397 | 387
2018-09-16 01:00 | 377 | 365
2018-09-16 01:30 | 360 | 348
2018-09-16 02:00 | 351 | 338
2018-09-16 02:30 | 346 | 332
2018-09-16 03:00 | 339 | 325
2018-09-16 03:30 | 348 | 333
2018-09-16 04:00 | 344 | 329
2018-09-16 04:30 | 348 | 333
2018-09-16 05:00 | 346 | 331
2018-09-16 05:30 | 345 | 330
2018-09-16 06:00 | 345 | 329
2018-09-16 06:30 | 361 | 345
2018-09-16 07:00 | 378 | 363
2018-09-16 07:30 | 387 | 373
2018-09-16 08:00 | 392 | 380
2018-09-16 08:30 | 406 | 396
2018-09-16 09:00 | 403 | 394
2018-09-16 09:30 | 392 | 384
2018-09-16 10:00 | 403 | 395
2018-09-16 10:30 | 417 | 411
2018-09-16 11:00 | 385 | 378
2018-09-16 11:30 | 359 | 352
2018-09-16 12:00 | 351 | 344
2018-09-16 12:30 | 357 | 351
2018-09-16 13:00 | 362 | 355
2018-09-16 13:30 | 367 | 360
2018-09-16 14:00 | 374 | 368
2018-09-16 14:30 | 360 | 354
2018-09-16 15:00 | 376 | 369
2018-09-16 15:30 | 409 | 403
2018-09-16 16:00 | 430 | 424
2018-09-16 16:30 | 454 | 449
2018-09-16 17:00 | 489 | 484
2018-09-16 17:30 | 515 | 512
2018-09-16 18:00 | 529 | 527
2018-09-16 18:30 | 545 | 543
2018-09-16 19:00 | 549 | 547
2018-09-16 19:30 | 549 | 546
2018-09-16 20:00 | 549 | 546
2018-09-16 20:30 | 536 | 533
2018-09-16 21:00 | 519 | 516
2018-09-16 21:30 | 505 | 502
2018-09-16 22:00 | 491 | 487
2018-09-16 22:30 | 483 | 478
2018-09-16 23:00 | 469 | 464
2018-09-16 23:30 | 459 | 452
2018-09-17 | 431 | 422
2018-09-17 00:30 | 405 | 394
2018-09-17 01:00 | 392 | 381
2018-09-17 01:30 | 378 | 365
2018-09-17 02:00 | 371 | 358
2018-09-17 02:30 | 364 | 351
2018-09-17 03:00 | 348 | 333
2018-09-17 03:30 | 343 | 327
2018-09-17 04:00 | 347 | 332
2018-09-17 04:30 | 380 | 366
2018-09-17 05:00 | 385 | 373
2018-09-17 05:30 | 411 | 401
2018-09-17 06:00 | 433 | 425
2018-09-17 06:30 | 490 | 478
2018-09-17 07:00 | 521 | 510
2018-09-17 07:30 | 532 | 522
2018-09-17 08:00 | 531 | 520
2018-09-17 08:30 | 515 | 504
2018-09-17 09:00 | 492 | 481
2018-09-17 09:30 | 467 | 456
2018-09-17 10:00 | 441 | 433
2018-09-17 10:30 | 417 | 410
2018-09-17 11:00 | 406 | 400
2018-09-17 11:30 | 405 | 399
2018-09-17 12:00 | 414 | 408
2018-09-17 12:30 | 420 | 415
2018-09-17 13:00 | 410 | 404
2018-09-17 13:30 | 413 | 408
2018-09-17 14:00 | 418 | 413
2018-09-17 14:30 | 425 | 420
2018-09-17 15:00 | 430 | 425
2018-09-17 15:30 | 445 | 439
2018-09-17 16:00 | 462 | 458
2018-09-17 16:30 | 482 | 478
2018-09-17 17:00 | 528 | 520
2018-09-17 17:30 | 565 | 554
2018-09-17 18:00 | 585 | 575
2018-09-17 18:30 | 600 | 591
2018-09-17 19:00 | 604 | 595
2018-09-17 19:30 | 584 | 575
2018-09-17 20:00 | 575 | 572
2018-09-17 20:30 | 576 | 575
2018-09-17 21:00 | 555 | 553
2018-09-17 21:30 | 518 | 515
2018-09-17 22:00 | 492 | 489
2018-09-17 22:30 | 473 | 470
2018-09-17 23:00 | 464 | 462
2018-09-17 23:30 | 448 | 445
2018-09-18 | 424 | 420
2018-09-18 00:30 | 387 | 381
2018-09-18 01:00 | 361 | 351
2018-09-18 01:30 | 352 | 341
2018-09-18 02:00 | 350 | 338
2018-09-18 02:30 | 345 | 334
2018-09-18 03:00 | 342 | 330
2018-09-18 03:30 | 333 | 321
2018-09-18 04:00 | 331 | 320
2018-09-18 04:30 | 339 | 328
2018-09-18 05:00 | 341 | 331
2018-09-18 05:30 | 370 | 364
2018-09-18 06:00 | 392 | 385
2018-09-18 06:30 | 456 | 451
2018-09-18 07:00 | 504 | 498
2018-09-18 07:30 | 523 | 517
2018-09-18 08:00 | 520 | 515
2018-09-18 08:30 | 499 | 494
2018-09-18 09:00 | 461 | 457
2018-09-18 09:30 | 465 | 461
2018-09-18 10:00 | 467 | 465
2018-09-18 10:30 | 470 | 468
2018-09-18 11:00 | 466 | 464
2018-09-18 11:30 | 451 | 449
2018-09-18 12:00 | 449 | 447
2018-09-18 12:30 | 429 | 427
2018-09-18 13:00 | 430 | 428
2018-09-18 13:30 | 441 | 439
2018-09-18 14:00 | 436 | 434
2018-09-18 14:30 | 445 | 443
2018-09-18 15:00 | 448 | 446
2018-09-18 15:30 | 451 | 448
2018-09-18 16:00 | 480 | 478
2018-09-18 16:30 | 502 | 500
2018-09-18 17:00 | 520 | 518
2018-09-18 17:30 | 545 | 543
2018-09-18 18:00 | 564 | 562
2018-09-18 18:30 | 580 | 577
2018-09-18 19:00 | 591 | 588
2018-09-18 19:30 | 573 | 570
2018-09-18 20:00 | 563 | 559
2018-09-18 20:30 | 546 | 541
2018-09-18 21:00 | 531 | 529
2018-09-18 21:30 | 509 | 507
2018-09-18 22:00 | 496 | 493
2018-09-18 22:30 | 492 | 489
2018-09-18 23:00 | 472 | 468
2018-09-18 23:30 | 447 | 442
2018-09-19 | 430 | 424
2018-09-19 00:30 | 391 | 383
2018-09-19 01:00 | 374 | 364
2018-09-19 01:30 | 370 | 358
2018-09-19 02:00 | 365 | 351
2018-09-19 02:30 | 357 | 343
2018-09-19 03:00 | 350 | 336
2018-09-19 03:30 | 346 | 332
2018-09-19 04:00 | 346 | 332
2018-09-19 04:30 | 357 | 344
2018-09-19 05:00 | 371 | 360
2018-09-19 05:30 | 379 | 370
2018-09-19 06:00 | 405 | 396
2018-09-19 06:30 | 461 | 455
2018-09-19 07:00 | 504 | 499
2018-09-19 07:30 | 521 | 516
2018-09-19 08:00 | 523 | 519
2018-09-19 08:30 | 509 | 506
2018-09-19 09:00 | 488 | 485
2018-09-19 09:30 | 459 | 457
2018-09-19 10:00 | 438 | 436
2018-09-19 10:30 | 420 | 418
2018-09-19 11:00 | 400 | 399
2018-09-19 11:30 | 414 | 414
2018-09-19 12:00 | 429 | 429
2018-09-19 12:30 | 428 | 428
2018-09-19 13:00 | 431 | 430
2018-09-19 13:30 | 425 | 424
2018-09-19 14:00 | 444 | 444
2018-09-19 14:30 | 443 | 443
2018-09-19 15:00 | 450 | 450
2018-09-19 15:30 | 471 | 469
2018-09-19 16:00 | 500 | 497
2018-09-19 16:30 | 530 | 528
2018-09-19 17:00 | 552 | 549
2018-09-19 17:30 | 567 | 565
2018-09-19 18:00 | 579 | 577
2018-09-19 18:30 | 581 | 579
2018-09-19 19:00 | 583 | 581
2018-09-19 19:30 | 575 | 572
2018-09-19 20:00 | 571 | 568
2018-09-19 20:30 | 554 | 553
2018-09-19 21:00 | 538 | 537
2018-09-19 21:30 | 534 | 529
2018-09-19 22:00 | 522 | 512
2018-09-19 22:30 | 507 | 504
2018-09-19 23:00 | 508 | 504
2018-09-19 23:30 | 500 | 495
2018-09-20 | 489 | 482
2018-09-20 00:30 | 450 | 441
2018-09-20 01:00 | 432 | 420
2018-09-20 01:30 | 427 | 414
2018-09-20 02:00 | 422 | 408
2018-09-20 02:30 | 404 | 390
2018-09-20 03:00 | 405 | 390
2018-09-20 03:30 | 400 | 386
2018-09-20 04:00 | 404 | 390
2018-09-20 04:30 | 406 | 392
2018-09-20 05:00 | 406 | 394
2018-09-20 05:30 | 431 | 421
2018-09-20 06:00 | 454 | 445
2018-09-20 06:30 | 495 | 489
2018-09-20 07:00 | 522 | 516
2018-09-20 07:30 | 550 | 538
2018-09-20 08:00 | 552 | 539
2018-09-20 08:30 | 539 | 529
2018-09-20 09:00 | 526 | 517
2018-09-20 09:30 | 508 | 499
2018-09-20 10:00 | 513 | 505
2018-09-20 10:30 | 519 | 512
2018-09-20 11:00 | 506 | 498
2018-09-20 11:30 | 478 | 471
2018-09-20 12:00 | 474 | 468
2018-09-20 12:30 | 486 | 479
2018-09-20 13:00 | 500 | 494
2018-09-20 13:30 | 503 | 497
2018-09-20 14:00 | 502 | 496
2018-09-20 14:30 | 489 | 484
2018-09-20 15:00 | 498 | 492
2018-09-20 15:30 | 504 | 498
2018-09-20 16:00 | 524 | 518
2018-09-20 16:30 | 549 | 542
2018-09-20 17:00 | 563 | 556
2018-09-20 17:30 | 582 | 576
2018-09-20 18:00 | 598 | 592
2018-09-20 18:30 | 618 | 610
2018-09-20 19:00 | 626 | 616
2018-09-20 19:30 | 607 | 598
2018-09-20 20:00 | 600 | 592
2018-09-20 20:30 | 598 | 591
2018-09-20 21:00 | 585 | 576
2018-09-20 21:30 | 554 | 544
2018-09-20 22:00 | 531 | 520
2018-09-20 22:30 | 509 | 502
2018-09-20 23:00 | 484 | 480
2018-09-20 23:30 | 468 | 463
2018-09-21 | 454 | 447
2018-09-21 00:30 | 430 | 421
2018-09-21 01:00 | 422 | 412
2018-09-21 01:30 | 419 | 408
2018-09-21 02:00 | 410 | 399
2018-09-21 02:30 | 409 | 397
2018-09-21 03:00 | 402 | 390
2018-09-21 03:30 | 390 | 378
2018-09-21 04:00 | 400 | 388
2018-09-21 04:30 | 413 | 402
2018-09-21 05:00 | 407 | 396
2018-09-21 05:30 | 430 | 421
2018-09-21 06:00 | 452 | 445
2018-09-21 06:30 | 488 | 483
2018-09-21 07:00 | 526 | 523
2018-09-21 07:30 | 550 | 546
2018-09-21 08:00 | 545 | 539
2018-09-21 08:30 | 532 | 525
2018-09-21 09:00 | 508 | 502
2018-09-21 09:30 | 498 | 492
2018-09-21 10:00 | 481 | 475
2018-09-21 10:30 | 474 | 467
2018-09-21 11:00 | 465 | 460
2018-09-21 11:30 | 455 | 455
2018-09-21 12:00 | 443 | 443
2018-09-21 12:30 | 445 | 445
2018-09-21 13:00 | 451 | 451
2018-09-21 13:30 | 446 | 446
2018-09-21 14:00 | 455 | 455
2018-09-21 14:30 | 461 | 461
2018-09-21 15:00 | 469 | 468
2018-09-21 15:30 | 484 | 484
2018-09-21 16:00 | 494 | 493
2018-09-21 16:30 | 519 | 518
2018-09-21 17:00 | 552 | 549
2018-09-21 17:30 | 576 | 573
2018-09-21 18:00 | 582 | 579
2018-09-21 18:30 | 595 | 589
2018-09-21 19:00 | 603 | 593
2018-09-21 19:30 | 591 | 585
2018-09-21 20:00 | 583 | 577
2018-09-21 20:30 | 585 | 579
2018-09-21 21:00 | 569 | 561
2018-09-21 21:30 | 561 | 549
2018-09-21 22:00 | 555 | 542
2018-09-21 22:30 | 552 | 538
2018-09-21 23:00 | 536 | 521
2018-09-21 23:30 | 506 | 500
2018-09-22 | 479 | 473
2018-09-22 00:30 | 434 | 426
2018-09-22 01:00 | 417 | 406
2018-09-22 01:30 | 407 | 395
2018-09-22 02:00 | 399 | 386
2018-09-22 02:30 | 390 | 377
2018-09-22 03:00 | 393 | 378
2018-09-22 03:30 | 389 | 373
2018-09-22 04:00 | 385 | 369
2018-09-22 04:30 | 385 | 369
2018-09-22 05:00 | 382 | 366
2018-09-22 05:30 | 394 | 380
2018-09-22 06:00 | 404 | 389
2018-09-22 06:30 | 415 | 401
2018-09-22 07:00 | 419 | 406
2018-09-22 07:30 | 428 | 416
2018-09-22 08:00 | 437 | 426
2018-09-22 08:30 | 438 | 429
2018-09-22 09:00 | 426 | 419
2018-09-22 09:30 | 420 | 413
2018-09-22 10:00 | 425 | 419
2018-09-22 10:30 | 424 | 419
2018-09-22 11:00 | 400 | 394
2018-09-22 11:30 | 391 | 385
2018-09-22 12:00 | 382 | 376
2018-09-22 12:30 | 371 | 364
2018-09-22 13:00 | 357 | 350
2018-09-22 13:30 | 353 | 346
2018-09-22 14:00 | 357 | 350
2018-09-22 14:30 | 364 | 358
2018-09-22 15:00 | 372 | 365
2018-09-22 15:30 | 384 | 377
2018-09-22 16:00 | 409 | 403
2018-09-22 16:30 | 446 | 441
2018-09-22 17:00 | 471 | 467
2018-09-22 17:30 | 479 | 475
2018-09-22 18:00 | 500 | 497
2018-09-22 18:30 | 526 | 519
2018-09-22 19:00 | 525 | 519
2018-09-22 19:30 | 517 | 510
2018-09-22 20:00 | 513 | 506
2018-09-22 20:30 | 502 | 496
2018-09-22 21:00 | 489 | 484
2018-09-22 21:30 | 478 | 473
2018-09-22 22:00 | 470 | 466
2018-09-22 22:30 | 469 | 464
2018-09-22 23:00 | 474 | 469
2018-09-22 23:30 | 471 | 465
2018-09-23 | 443 | 435
2018-09-23 00:30 | 393 | 381
2018-09-23 01:00 | 369 | 357
2018-09-23 01:30 | 356 | 343
2018-09-23 02:00 | 348 | 333
2018-09-23 02:30 | 340 | 325
2018-09-23 03:00 | 349 | 332
2018-09-23 03:30 | 352 | 335
2018-09-23 04:00 | 352 | 335
2018-09-23 04:30 | 356 | 338
2018-09-23 05:00 | 346 | 329
2018-09-23 05:30 | 345 | 328
2018-09-23 06:00 | 349 | 331
2018-09-23 06:30 | 353 | 335
2018-09-23 07:00 | 363 | 346
2018-09-23 07:30 | 375 | 359
2018-09-23 08:00 | 381 | 366
2018-09-23 08:30 | 387 | 374
2018-09-23 09:00 | 381 | 369
2018-09-23 09:30 | 362 | 349
2018-09-23 10:00 | 361 | 349
2018-09-23 10:30 | 357 | 346
2018-09-23 11:00 | 349 | 339
2018-09-23 11:30 | 338 | 329
2018-09-23 12:00 | 335 | 325
2018-09-23 12:30 | 332 | 323
2018-09-23 13:00 | 331 | 320
2018-09-23 13:30 | 334 | 323
2018-09-23 14:00 | 337 | 327
2018-09-23 14:30 | 342 | 332
2018-09-23 15:00 | 360 | 350
2018-09-23 15:30 | 394 | 386
2018-09-23 16:00 | 413 | 407
2018-09-23 16:30 | 436 | 430
2018-09-23 17:00 | 476 | 471
2018-09-23 17:30 | 488 | 484
2018-09-23 18:00 | 502 | 499
2018-09-23 18:30 | 526 | 522
2018-09-23 19:00 | 529 | 526
2018-09-23 19:30 | 526 | 521
2018-09-23 20:00 | 523 | 518
2018-09-23 20:30 | 518 | 514
2018-09-23 21:00 | 498 | 495
2018-09-23 21:30 | 482 | 478
2018-09-23 22:00 | 470 | 465
2018-09-23 22:30 | 466 | 460
2018-09-23 23:00 | 450 | 444
2018-09-23 23:30 | 445 | 438
2018-09-24 | 437 | 429
2018-09-24 00:30 | 399 | 388
2018-09-24 01:00 | 381 | 369
2018-09-24 01:30 | 365 | 351
2018-09-24 02:00 | 352 | 337
2018-09-24 02:30 | 350 | 333
2018-09-24 03:00 | 349 | 331
2018-09-24 03:30 | 349 | 332
2018-09-24 04:00 | 350 | 333
2018-09-24 04:30 | 353 | 337
2018-09-24 05:00 | 355 | 341
2018-09-24 05:30 | 370 | 358
2018-09-24 06:00 | 399 | 388
2018-09-24 06:30 | 434 | 426
2018-09-24 07:00 | 470 | 463
2018-09-24 07:30 | 493 | 485
2018-09-24 08:00 | 514 | 506
2018-09-24 08:30 | 523 | 518
2018-09-24 09:00 | 520 | 513
2018-09-24 09:30 | 512 | 505
2018-09-24 10:00 | 511 | 504
2018-09-24 10:30 | 507 | 505
2018-09-24 11:00 | 498 | 497
2018-09-24 11:30 | 492 | 491
2018-09-24 12:00 | 496 | 495
2018-09-24 12:30 | 505 | 504
2018-09-24 13:00 | 533 | 533
2018-09-24 13:30 | 542 | 541
2018-09-24 14:00 | 534 | 533
2018-09-24 14:30 | 504 | 503
2018-09-24 15:00 | 492 | 491
2018-09-24 15:30 | 504 | 503
2018-09-24 16:00 | 517 | 516
2018-09-24 16:30 | 534 | 532
2018-09-24 17:00 | 552 | 550
2018-09-24 17:30 | 579 | 576
2018-09-24 18:00 | 597 | 594
2018-09-24 18:30 | 614 | 611
2018-09-24 19:00 | 617 | 614
2018-09-24 19:30 | 599 | 596
2018-09-24 20:00 | 590 | 587
2018-09-24 20:30 | 587 | 584
2018-09-24 21:00 | 568 | 566
2018-09-24 21:30 | 545 | 542
2018-09-24 22:00 | 526 | 523
2018-09-24 22:30 | 519 | 515
2018-09-24 23:00 | 501 | 498
2018-09-24 23:30 | 476 | 473
2018-09-25 | 451 | 447
2018-09-25 00:30 | 418 | 413
2018-09-25 01:00 | 400 | 393
2018-09-25 01:30 | 392 | 384
2018-09-25 02:00 | 382 | 374
2018-09-25 02:30 | 375 | 366
2018-09-25 03:00 | 370 | 361
2018-09-25 03:30 | 376 | 367
2018-09-25 04:00 | 376 | 367
2018-09-25 04:30 | 383 | 374
2018-09-25 05:00 | 393 | 386
2018-09-25 05:30 | 408 | 402
2018-09-25 06:00 | 416 | 411
2018-09-25 06:30 | 465 | 461
2018-09-25 07:00 | 508 | 504
2018-09-25 07:30 | 544 | 540
2018-09-25 08:00 | 571 | 563
2018-09-25 08:30 | 571 | 565
2018-09-25 09:00 | 565 | 559
2018-09-25 09:30 | 547 | 540
2018-09-25 10:00 | 515 | 508
2018-09-25 10:30 | 501 | 494
2018-09-25 11:00 | 501 | 496
2018-09-25 11:30 | 522 | 517
2018-09-25 12:00 | 536 | 532
2018-09-25 12:30 | 538 | 533
2018-09-25 13:00 | 535 | 530
2018-09-25 13:30 | 526 | 521
2018-09-25 14:00 | 527 | 521
2018-09-25 14:30 | 522 | 516
2018-09-25 15:00 | 531 | 525
2018-09-25 15:30 | 546 | 540
2018-09-25 16:00 | 552 | 546
2018-09-25 16:30 | 577 | 571
2018-09-25 17:00 | 603 | 595
2018-09-25 17:30 | 620 | 612
2018-09-25 18:00 | 624 | 617
2018-09-25 18:30 | 632 | 625
2018-09-25 19:00 | 638 | 630
2018-09-25 19:30 | 607 | 601
2018-09-25 20:00 | 592 | 588
2018-09-25 20:30 | 582 | 579
2018-09-25 21:00 | 562 | 561
2018-09-25 21:30 | 543 | 541
2018-09-25 22:00 | 520 | 518
2018-09-25 22:30 | 514 | 512
2018-09-25 23:00 | 498 | 496
2018-09-25 23:30 | 482 | 478
2018-09-26 | 456 | 451
2018-09-26 00:30 | 420 | 414
2018-09-26 01:00 | 412 | 405
2018-09-26 01:30 | 391 | 382
2018-09-26 02:00 | 365 | 355
2018-09-26 02:30 | 361 | 351
2018-09-26 03:00 | 360 | 349
2018-09-26 03:30 | 376 | 365
2018-09-26 04:00 | 376 | 365
2018-09-26 04:30 | 377 | 366
2018-09-26 05:00 | 383 | 374
2018-09-26 05:30 | 396 | 389
2018-09-26 06:00 | 412 | 406
2018-09-26 06:30 | 452 | 448
2018-09-26 07:00 | 491 | 487
2018-09-26 07:30 | 513 | 510
2018-09-26 08:00 | 519 | 514
2018-09-26 08:30 | 514 | 509
2018-09-26 09:00 | 505 | 501
2018-09-26 09:30 | 514 | 510
2018-09-26 10:00 | 515 | 512
2018-09-26 10:30 | 514 | 512
2018-09-26 11:00 | 506 | 504
2018-09-26 11:30 | 493 | 491
2018-09-26 12:00 | 481 | 479
2018-09-26 12:30 | 462 | 460
2018-09-26 13:00 | 480 | 478
2018-09-26 13:30 | 475 | 474
2018-09-26 14:00 | 447 | 445
2018-09-26 14:30 | 482 | 480
2018-09-26 15:00 | 519 | 517
2018-09-26 15:30 | 515 | 512
2018-09-26 16:00 | 517 | 515
2018-09-26 16:30 | 545 | 542
2018-09-26 17:00 | 577 | 572
2018-09-26 17:30 | 602 | 590
2018-09-26 18:00 | 612 | 602
2018-09-26 18:30 | 623 | 613
2018-09-26 19:00 | 622 | 612
2018-09-26 19:30 | 610 | 604
2018-09-26 20:00 | 601 | 595
2018-09-26 20:30 | 590 | 586
2018-09-26 21:00 | 573 | 572
2018-09-26 21:30 | 554 | 553
2018-09-26 22:00 | 539 | 537
2018-09-26 22:30 | 524 | 522
2018-09-26 23:00 | 504 | 503
2018-09-26 23:30 | 492 | 490
2018-09-27 | 462 | 458
2018-09-27 00:30 | 423 | 418
2018-09-27 01:00 | 405 | 399
2018-09-27 01:30 | 388 | 380
2018-09-27 02:00 | 380 | 372
2018-09-27 02:30 | 378 | 370
2018-09-27 03:00 | 369 | 361
2018-09-27 03:30 | 368 | 359
2018-09-27 04:00 | 359 | 350
2018-09-27 04:30 | 374 | 366
2018-09-27 05:00 | 387 | 380
2018-09-27 05:30 | 415 | 409
2018-09-27 06:00 | 440 | 435
2018-09-27 06:30 | 474 | 468
2018-09-27 07:00 | 505 | 502
2018-09-27 07:30 | 543 | 540
2018-09-27 08:00 | 556 | 552
2018-09-27 08:30 | 559 | 555
2018-09-27 09:00 | 552 | 548
2018-09-27 09:30 | 540 | 538
2018-09-27 10:00 | 537 | 535
2018-09-27 10:30 | 528 | 527
2018-09-27 11:00 | 525 | 525
2018-09-27 11:30 | 524 | 524
2018-09-27 12:00 | 527 | 527
2018-09-27 12:30 | 522 | 522
2018-09-27 13:00 | 515 | 515
2018-09-27 13:30 | 494 | 494
2018-09-27 14:00 | 480 | 480
2018-09-27 14:30 | 468 | 468
2018-09-27 15:00 | 467 | 467
2018-09-27 15:30 | 483 | 483
2018-09-27 16:00 | 501 | 501
2018-09-27 16:30 | 521 | 520
2018-09-27 17:00 | 529 | 529
2018-09-27 17:30 | 543 | 542
2018-09-27 18:00 | 571 | 571
2018-09-27 18:30 | 590 | 590
2018-09-27 19:00 | 599 | 597
2018-09-27 19:30 | 581 | 578
2018-09-27 20:00 | 572 | 570
2018-09-27 20:30 | 560 | 558
2018-09-27 21:00 | 545 | 543
2018-09-27 21:30 | 528 | 526
2018-09-27 22:00 | 525 | 522
2018-09-27 22:30 | 517 | 514
2018-09-27 23:00 | 494 | 492
2018-09-27 23:30 | 477 | 475
2018-09-28 | 456 | 452
2018-09-28 00:30 | 419 | 413
2018-09-28 01:00 | 392 | 385
2018-09-28 01:30 | 376 | 367
2018-09-28 02:00 | 370 | 361
2018-09-28 02:30 | 368 | 358
2018-09-28 03:00 | 376 | 366
2018-09-28 03:30 | 370 | 360
2018-09-28 04:00 | 376 | 367
2018-09-28 04:30 | 387 | 378
2018-09-28 05:00 | 386 | 378
2018-09-28 05:30 | 402 | 395
2018-09-28 06:00 | 412 | 406
2018-09-28 06:30 | 434 | 430
2018-09-28 07:00 | 472 | 468
2018-09-28 07:30 | 500 | 494
2018-09-28 08:00 | 508 | 503
2018-09-28 08:30 | 510 | 507
2018-09-28 09:00 | 509 | 506
2018-09-28 09:30 | 495 | 493
2018-09-28 10:00 | 495 | 494
2018-09-28 10:30 | 482 | 480
2018-09-28 11:00 | 468 | 467
2018-09-28 11:30 | 452 | 451
2018-09-28 12:00 | 446 | 446
2018-09-28 12:30 | 440 | 440
2018-09-28 13:00 | 446 | 446
2018-09-28 13:30 | 446 | 446
2018-09-28 14:00 | 449 | 449
2018-09-28 14:30 | 447 | 447
2018-09-28 15:00 | 446 | 446
2018-09-28 15:30 | 466 | 466
2018-09-28 16:00 | 491 | 491
2018-09-28 16:30 | 507 | 507
2018-09-28 17:00 | 534 | 532
2018-09-28 17:30 | 536 | 533
2018-09-28 18:00 | 544 | 541
2018-09-28 18:30 | 550 | 547
2018-09-28 19:00 | 545 | 543
2018-09-28 19:30 | 532 | 530
2018-09-28 20:00 | 526 | 524
2018-09-28 20:30 | 511 | 510
2018-09-28 21:00 | 493 | 493
2018-09-28 21:30 | 477 | 476
2018-09-28 22:00 | 460 | 459
2018-09-28 22:30 | 454 | 452
2018-09-28 23:00 | 441 | 439
2018-09-28 23:30 | 431 | 428
2018-09-29 | 400 | 396
2018-09-29 00:30 | 378 | 372
2018-09-29 01:00 | 350 | 343
2018-09-29 01:30 | 343 | 336
2018-09-29 02:00 | 335 | 328
2018-09-29 02:30 | 335 | 327
2018-09-29 03:00 | 327 | 317
2018-09-29 03:30 | 326 | 316
2018-09-29 04:00 | 319 | 309
2018-09-29 04:30 | 318 | 308
2018-09-29 05:00 | 330 | 320
2018-09-29 05:30 | 333 | 324
2018-09-29 06:00 | 334 | 325
2018-09-29 06:30 | 343 | 334
2018-09-29 07:00 | 357 | 348
2018-09-29 07:30 | 373 | 365
2018-09-29 08:00 | 381 | 375
2018-09-29 08:30 | 397 | 391
2018-09-29 09:00 | 383 | 379
2018-09-29 09:30 | 377 | 374
2018-09-29 10:00 | 373 | 371
2018-09-29 10:30 | 368 | 366
2018-09-29 11:00 | 351 | 349
2018-09-29 11:30 | 349 | 347
2018-09-29 12:00 | 343 | 341
2018-09-29 12:30 | 351 | 349
2018-09-29 13:00 | 360 | 358
2018-09-29 13:30 | 362 | 360
2018-09-29 14:00 | 369 | 367
2018-09-29 14:30 | 377 | 375
2018-09-29 15:00 | 414 | 413
2018-09-29 15:30 | 437 | 435
2018-09-29 16:00 | 449 | 447
2018-09-29 16:30 | 454 | 451
2018-09-29 17:00 | 462 | 460
2018-09-29 17:30 | 468 | 465
2018-09-29 18:00 | 488 | 485
2018-09-29 18:30 | 495 | 492
2018-09-29 19:00 | 491 | 488
2018-09-29 19:30 | 479 | 476
2018-09-29 20:00 | 480 | 476
2018-09-29 20:30 | 472 | 468
2018-09-29 21:00 | 459 | 456
2018-09-29 21:30 | 448 | 445
2018-09-29 22:00 | 442 | 439
2018-09-29 22:30 | 444 | 440
2018-09-29 23:00 | 440 | 436
2018-09-29 23:30 | 437 | 431
2018-09-30 | 413 | 406
2018-09-30 00:30 | 381 | 372
2018-09-30 01:00 | 355 | 345
2018-09-30 01:30 | 336 | 325
2018-09-30 02:00 | 328 | 316
2018-09-30 02:30 | 322 | 310
2018-09-30 03:00 | 322 | 309
2018-09-30 03:30 | 319 | 305
2018-09-30 04:00 | 303 | 288
2018-09-30 04:30 | 302 | 286
2018-09-30 05:00 | 313 | 298
2018-09-30 05:30 | 321 | 306
2018-09-30 06:00 | 328 | 312
2018-09-30 06:30 | 347 | 330
2018-09-30 07:00 | 361 | 346
2018-09-30 07:30 | 383 | 370
2018-09-30 08:00 | 401 | 392
2018-09-30 08:30 | 424 | 417
2018-09-30 09:00 | 432 | 426
2018-09-30 09:30 | 435 | 430
2018-09-30 10:00 | 436 | 432
2018-09-30 10:30 | 446 | 442
2018-09-30 11:00 | 449 | 446
2018-09-30 11:30 | 442 | 439
2018-09-30 12:00 | 448 | 445
2018-09-30 12:30 | 436 | 433
2018-09-30 13:00 | 430 | 426
2018-09-30 13:30 | 401 | 395
2018-09-30 14:00 | 379 | 372
2018-09-30 14:30 | 375 | 368
2018-09-30 15:00 | 391 | 384
2018-09-30 15:30 | 390 | 383
2018-09-30 16:00 | 383 | 376
2018-09-30 16:30 | 395 | 389
2018-09-30 17:00 | 424 | 418
2018-09-30 17:30 | 435 | 431
2018-09-30 18:00 | 459 | 454
2018-09-30 18:30 | 478 | 473
2018-09-30 19:00 | 484 | 479
2018-09-30 19:30 | 472 | 467
2018-09-30 20:00 | 464 | 458
2018-09-30 20:30 | 458 | 453
2018-09-30 21:00 | 439 | 435
2018-09-30 21:30 | 421 | 417
2018-09-30 22:00 | 420 | 415
2018-09-30 22:30 | 417 | 412
2018-09-30 23:00 | 405 | 400
2018-09-30 23:30 | 395 | 389
2018-10-01 | 376 | 368
2018-10-01 00:30 | 355 | 346
2018-10-01 01:00 | 342 | 331
2018-10-01 01:30 | 329 | 317
2018-10-01 02:00 | 327 | 315
2018-10-01 02:30 | 321 | 310
2018-10-01 03:00 | 316 | 305
2018-10-01 03:30 | 308 | 297
2018-10-01 04:00 | 304 | 293
2018-10-01 04:30 | 305 | 293
2018-10-01 05:00 | 306 | 295
2018-10-01 05:30 | 327 | 317
2018-10-01 06:00 | 331 | 321
2018-10-01 06:30 | 335 | 325
2018-10-01 07:00 | 339 | 329
2018-10-01 07:30 | 339 | 331
2018-10-01 08:00 | 336 | 328
2018-10-01 08:30 | 343 | 336
2018-10-01 09:00 | 345 | 339
2018-10-01 09:30 | 344 | 338
2018-10-01 10:00 | 338 | 333
2018-10-01 10:30 | 335 | 330
2018-10-01 11:00 | 321 | 316
2018-10-01 11:30 | 321 | 316
2018-10-01 12:00 | 325 | 321
2018-10-01 12:30 | 327 | 323
2018-10-01 13:00 | 325 | 321
2018-10-01 13:30 | 321 | 317
2018-10-01 14:00 | 320 | 316
2018-10-01 14:30 | 321 | 317
2018-10-01 15:00 | 327 | 324
2018-10-01 15:30 | 349 | 346
2018-10-01 16:00 | 374 | 371
2018-10-01 16:30 | 407 | 404
2018-10-01 17:00 | 438 | 435
2018-10-01 17:30 | 452 | 450
2018-10-01 18:00 | 467 | 465
2018-10-01 18:30 | 502 | 502
2018-10-01 19:00 | 520 | 519
2018-10-01 19:30 | 497 | 497
2018-10-01 20:00 | 482 | 481
2018-10-01 20:30 | 471 | 470
2018-10-01 21:00 | 459 | 458
2018-10-01 21:30 | 442 | 441
2018-10-01 22:00 | 434 | 433
2018-10-01 22:30 | 433 | 431
2018-10-01 23:00 | 421 | 419
2018-10-01 23:30 | 405 | 402
2018-10-02 | 388 | 385
2018-10-02 00:30 | 363 | 359
2018-10-02 01:00 | 345 | 337
2018-10-02 01:30 | 332 | 324
2018-10-02 02:00 | 326 | 318
2018-10-02 02:30 | 325 | 316
2018-10-02 03:00 | 322 | 312
2018-10-02 03:30 | 325 | 316
2018-10-02 04:00 | 321 | 312
2018-10-02 04:30 | 329 | 321
2018-10-02 05:00 | 339 | 331
2018-10-02 05:30 | 365 | 359
2018-10-02 06:00 | 385 | 379
2018-10-02 06:30 | 418 | 415
2018-10-02 07:00 | 443 | 441
2018-10-02 07:30 | 460 | 458
2018-10-02 08:00 | 469 | 462
2018-10-02 08:30 | 463 | 456
2018-10-02 09:00 | 451 | 445
2018-10-02 09:30 | 447 | 442
2018-10-02 10:00 | 449 | 445
2018-10-02 10:30 | 431 | 428
2018-10-02 11:00 | 422 | 419
2018-10-02 11:30 | 427 | 425
2018-10-02 12:00 | 422 | 420
2018-10-02 12:30 | 413 | 410
2018-10-02 13:00 | 409 | 407
2018-10-02 13:30 | 414 | 412
2018-10-02 14:00 | 429 | 426
2018-10-02 14:30 | 431 | 429
2018-10-02 15:00 | 444 | 441
2018-10-02 15:30 | 480 | 477
2018-10-02 16:00 | 506 | 503
2018-10-02 16:30 | 530 | 525
2018-10-02 17:00 | 551 | 546
2018-10-02 17:30 | 574 | 569
2018-10-02 18:00 | 581 | 575
2018-10-02 18:30 | 593 | 587
2018-10-02 19:00 | 592 | 586
2018-10-02 19:30 | 574 | 567
2018-10-02 20:00 | 556 | 551
2018-10-02 20:30 | 552 | 551
2018-10-02 21:00 | 532 | 531
2018-10-02 21:30 | 521 | 520
2018-10-02 22:00 | 501 | 500
2018-10-02 22:30 | 483 | 481
2018-10-02 23:00 | 473 | 472
2018-10-02 23:30 | 469 | 467
2018-10-03 | 438 | 435
2018-10-03 00:30 | 404 | 398
2018-10-03 01:00 | 379 | 372
2018-10-03 01:30 | 363 | 356
2018-10-03 02:00 | 363 | 355
2018-10-03 02:30 | 359 | 351
2018-10-03 03:00 | 342 | 332
2018-10-03 03:30 | 344 | 334
2018-10-03 04:00 | 342 | 331
2018-10-03 04:30 | 344 | 335
2018-10-03 05:00 | 350 | 341
2018-10-03 05:30 | 366 | 359
2018-10-03 06:00 | 380 | 374
2018-10-03 06:30 | 401 | 398
2018-10-03 07:00 | 429 | 427
2018-10-03 07:30 | 450 | 449
2018-10-03 08:00 | 458 | 457
2018-10-03 08:30 | 457 | 456
2018-10-03 09:00 | 446 | 445
2018-10-03 09:30 | 447 | 446
2018-10-03 10:00 | 443 | 442
2018-10-03 10:30 | 437 | 436
2018-10-03 11:00 | 423 | 423
2018-10-03 11:30 | 420 | 420
2018-10-03 12:00 | 428 | 428
2018-10-03 12:30 | 436 | 436
2018-10-03 13:00 | 439 | 439
2018-10-03 13:30 | 445 | 445
2018-10-03 14:00 | 456 | 455
2018-10-03 14:30 | 468 | 465
2018-10-03 15:00 | 488 | 484
2018-10-03 15:30 | 510 | 506
2018-10-03 16:00 | 524 | 520
2018-10-03 16:30 | 538 | 534
2018-10-03 17:00 | 559 | 555
2018-10-03 17:30 | 576 | 572
2018-10-03 18:00 | 580 | 576
2018-10-03 18:30 | 591 | 588
2018-10-03 19:00 | 594 | 591
2018-10-03 19:30 | 581 | 577
2018-10-03 20:00 | 563 | 558
2018-10-03 20:30 | 549 | 546
2018-10-03 21:00 | 535 | 530
2018-10-03 21:30 | 508 | 503
2018-10-03 22:00 | 484 | 482
2018-10-03 22:30 | 482 | 480
2018-10-03 23:00 | 473 | 470
2018-10-03 23:30 | 466 | 463
2018-10-04 | 445 | 440
2018-10-04 00:30 | 404 | 396
2018-10-04 01:00 | 389 | 381
2018-10-04 01:30 | 371 | 361
2018-10-04 02:00 | 350 | 340
2018-10-04 02:30 | 339 | 329
2018-10-04 03:00 | 333 | 322
2018-10-04 03:30 | 331 | 320
2018-10-04 04:00 | 337 | 326
2018-10-04 04:30 | 337 | 327
2018-10-04 05:00 | 354 | 345
2018-10-04 05:30 | 375 | 366
2018-10-04 06:00 | 381 | 374
2018-10-04 06:30 | 417 | 412
2018-10-04 07:00 | 465 | 460
2018-10-04 07:30 | 477 | 472
2018-10-04 08:00 | 491 | 488
2018-10-04 08:30 | 489 | 486
2018-10-04 09:00 | 484 | 482
2018-10-04 09:30 | 468 | 467
2018-10-04 10:00 | 464 | 462
2018-10-04 10:30 | 461 | 460
2018-10-04 11:00 | 450 | 450
2018-10-04 11:30 | 446 | 445
2018-10-04 12:00 | 449 | 449
2018-10-04 12:30 | 445 | 445
2018-10-04 13:00 | 455 | 454
2018-10-04 13:30 | 467 | 467
2018-10-04 14:00 | 489 | 488
2018-10-04 14:30 | 491 | 491
2018-10-04 15:00 | 491 | 491
2018-10-04 15:30 | 500 | 499
2018-10-04 16:00 | 512 | 512
2018-10-04 16:30 | 524 | 524
2018-10-04 17:00 | 543 | 543
2018-10-04 17:30 | 555 | 553
2018-10-04 18:00 | 559 | 557
2018-10-04 18:30 | 574 | 573
2018-10-04 19:00 | 579 | 578
2018-10-04 19:30 | 567 | 565
2018-10-04 20:00 | 554 | 551
2018-10-04 20:30 | 557 | 553
2018-10-04 21:00 | 533 | 530
2018-10-04 21:30 | 505 | 502
2018-10-04 22:00 | 490 | 487
2018-10-04 22:30 | 474 | 473
2018-10-04 23:00 | 455 | 453
2018-10-04 23:30 | 438 | 435
2018-10-05 | 416 | 411
2018-10-05 00:30 | 378 | 371
2018-10-05 01:00 | 360 | 352
2018-10-05 01:30 | 350 | 341
2018-10-05 02:00 | 345 | 336
2018-10-05 02:30 | 342 | 332
2018-10-05 03:00 | 333 | 321
2018-10-05 03:30 | 318 | 305
2018-10-05 04:00 | 323 | 310
2018-10-05 04:30 | 322 | 310
2018-10-05 05:00 | 332 | 320
2018-10-05 05:30 | 339 | 330
2018-10-05 06:00 | 352 | 343
2018-10-05 06:30 | 407 | 402
2018-10-05 07:00 | 437 | 434
2018-10-05 07:30 | 460 | 459
2018-10-05 08:00 | 479 | 477
2018-10-05 08:30 | 486 | 484
2018-10-05 09:00 | 476 | 475
2018-10-05 09:30 | 483 | 482
2018-10-05 10:00 | 480 | 479
2018-10-05 10:30 | 487 | 486
2018-10-05 11:00 | 496 | 495
2018-10-05 11:30 | 486 | 484
2018-10-05 12:00 | 483 | 481
2018-10-05 12:30 | 499 | 497
2018-10-05 13:00 | 502 | 500
2018-10-05 13:30 | 506 | 504
2018-10-05 14:00 | 500 | 499
2018-10-05 14:30 | 499 | 497
2018-10-05 15:00 | 513 | 511
2018-10-05 15:30 | 510 | 508
2018-10-05 16:00 | 519 | 517
2018-10-05 16:30 | 518 | 515
2018-10-05 17:00 | 498 | 495
2018-10-05 17:30 | 507 | 503
2018-10-05 18:00 | 511 | 507
2018-10-05 18:30 | 514 | 511
2018-10-05 19:00 | 522 | 519
2018-10-05 19:30 | 519 | 516
2018-10-05 20:00 | 514 | 512
2018-10-05 20:30 | 511 | 508
2018-10-05 21:00 | 497 | 496
2018-10-05 21:30 | 478 | 476
2018-10-05 22:00 | 469 | 467
2018-10-05 22:30 | 464 | 462
2018-10-05 23:00 | 446 | 443
2018-10-05 23:30 | 436 | 432
2018-10-06 | 424 | 418
2018-10-06 00:30 | 400 | 392
2018-10-06 01:00 | 371 | 360
2018-10-06 01:30 | 353 | 342
2018-10-06 02:00 | 345 | 333
2018-10-06 02:30 | 340 | 328
2018-10-06 03:00 | 339 | 326
2018-10-06 03:30 | 336 | 323
2018-10-06 04:00 | 334 | 321
2018-10-06 04:30 | 330 | 318
2018-10-06 05:00 | 338 | 325
2018-10-06 05:30 | 349 | 337
2018-10-06 06:00 | 340 | 327
2018-10-06 06:30 | 348 | 337
2018-10-06 07:00 | 362 | 352
2018-10-06 07:30 | 376 | 368
2018-10-06 08:00 | 392 | 385
2018-10-06 08:30 | 417 | 411
2018-10-06 09:00 | 437 | 432
2018-10-06 09:30 | 469 | 465
2018-10-06 10:00 | 460 | 457
2018-10-06 10:30 | 460 | 457
2018-10-06 11:00 | 448 | 445
2018-10-06 11:30 | 436 | 433
2018-10-06 12:00 | 419 | 416
2018-10-06 12:30 | 431 | 428
2018-10-06 13:00 | 430 | 427
2018-10-06 13:30 | 431 | 428
2018-10-06 14:00 | 431 | 427
2018-10-06 14:30 | 427 | 423
2018-10-06 15:00 | 424 | 420
2018-10-06 15:30 | 413 | 409
2018-10-06 16:00 | 418 | 415
2018-10-06 16:30 | 429 | 426
2018-10-06 17:00 | 445 | 442
2018-10-06 17:30 | 459 | 457
2018-10-06 18:00 | 468 | 466
2018-10-06 18:30 | 495 | 493
2018-10-06 19:00 | 497 | 496
2018-10-06 19:30 | 477 | 475
2018-10-06 20:00 | 476 | 474
2018-10-06 20:30 | 478 | 476
2018-10-06 21:00 | 468 | 465
2018-10-06 21:30 | 462 | 459
2018-10-06 22:00 | 454 | 450
2018-10-06 22:30 | 445 | 439
2018-10-06 23:00 | 423 | 417
2018-10-06 23:30 | 395 | 388
2018-10-07 | 371 | 364
2018-10-07 00:30 | 354 | 344
2018-10-07 01:00 | 341 | 331
2018-10-07 01:30 | 334 | 321
2018-10-07 02:00 | 330 | 312
2018-10-07 02:30 | 330 | 314
2018-10-07 03:00 | 324 | 308
2018-10-07 03:30 | 325 | 309
2018-10-07 04:00 | 325 | 307
2018-10-07 04:30 | 319 | 301
2018-10-07 05:00 | 321 | 303
2018-10-07 05:30 | 321 | 302
2018-10-07 06:00 | 320 | 300
2018-10-07 06:30 | 321 | 302
2018-10-07 07:00 | 323 | 305
2018-10-07 07:30 | 327 | 309
2018-10-07 08:00 | 324 | 308
2018-10-07 08:30 | 323 | 308
2018-10-07 09:00 | 333 | 319
2018-10-07 09:30 | 346 | 335
2018-10-07 10:00 | 347 | 336
2018-10-07 10:30 | 341 | 332
2018-10-07 11:00 | 359 | 351
2018-10-07 11:30 | 369 | 361
2018-10-07 12:00 | 375 | 367
2018-10-07 12:30 | 376 | 368
2018-10-07 13:00 | 370 | 361
2018-10-07 13:30 | 364 | 355
2018-10-07 14:00 | 370 | 362
2018-10-07 14:30 | 370 | 362
2018-10-07 15:00 | 375 | 367
2018-10-07 15:30 | 378 | 370
2018-10-07 16:00 | 386 | 379
2018-10-07 16:30 | 402 | 395
2018-10-07 17:00 | 434 | 429
2018-10-07 17:30 | 460 | 455
2018-10-07 18:00 | 469 | 465
2018-10-07 18:30 | 483 | 481
2018-10-07 19:00 | 492 | 489
2018-10-07 19:30 | 482 | 479
2018-10-07 20:00 | 473 | 470
2018-10-07 20:30 | 457 | 454
2018-10-07 21:00 | 439 | 436
2018-10-07 21:30 | 424 | 420
2018-10-07 22:00 | 406 | 401
2018-10-07 22:30 | 392 | 387
2018-10-07 23:00 | 384 | 378
2018-10-07 23:30 | 367 | 360
2018-10-08 | 356 | 347
2018-10-08 00:30 | 346 | 336
2018-10-08 01:00 | 345 | 333
2018-10-08 01:30 | 329 | 315
2018-10-08 02:00 | 319 | 305
2018-10-08 02:30 | 317 | 302
2018-10-08 03:00 | 317 | 302
2018-10-08 03:30 | 318 | 303
2018-10-08 04:00 | 320 | 305
2018-10-08 04:30 | 341 | 328
2018-10-08 05:00 | 349 | 338
2018-10-08 05:30 | 376 | 366
2018-10-08 06:00 | 398 | 389
2018-10-08 06:30 | 422 | 417
2018-10-08 07:00 | 444 | 440
2018-10-08 07:30 | 463 | 460
2018-10-08 08:00 | 465 | 463
2018-10-08 08:30 | 479 | 475
2018-10-08 09:00 | 466 | 464
2018-10-08 09:30 | 446 | 444
2018-10-08 10:00 | 440 | 439
2018-10-08 10:30 | 423 | 422
2018-10-08 11:00 | 401 | 400
2018-10-08 11:30 | 407 | 407
2018-10-08 12:00 | 409 | 408
2018-10-08 12:30 | 409 | 409
2018-10-08 13:00 | 428 | 428
2018-10-08 13:30 | 457 | 457
2018-10-08 14:00 | 490 | 489
2018-10-08 14:30 | 502 | 501
2018-10-08 15:00 | 483 | 481
2018-10-08 15:30 | 487 | 485
2018-10-08 16:00 | 509 | 507
2018-10-08 16:30 | 542 | 539
2018-10-08 17:00 | 569 | 562
2018-10-08 17:30 | 597 | 587
2018-10-08 18:00 | 591 | 583
2018-10-08 18:30 | 583 | 576
2018-10-08 19:00 | 579 | 572
2018-10-08 19:30 | 566 | 557
2018-10-08 20:00 | 556 | 545
2018-10-08 20:30 | 551 | 540
2018-10-08 21:00 | 525 | 514
2018-10-08 21:30 | 501 | 496
2018-10-08 22:00 | 495 | 491
2018-10-08 22:30 | 479 | 475
2018-10-08 23:00 | 458 | 456
2018-10-08 23:30 | 444 | 441
2018-10-09 | 418 | 412
2018-10-09 00:30 | 387 | 379
2018-10-09 01:00 | 382 | 372
2018-10-09 01:30 | 386 | 372
2018-10-09 02:00 | 372 | 358
2018-10-09 02:30 | 358 | 343
2018-10-09 03:00 | 347 | 331
2018-10-09 03:30 | 349 | 333
2018-10-09 04:00 | 357 | 341
2018-10-09 04:30 | 372 | 358
2018-10-09 05:00 | 387 | 375
2018-10-09 05:30 | 400 | 389
2018-10-09 06:00 | 409 | 400
2018-10-09 06:30 | 442 | 435
2018-10-09 07:00 | 481 | 477
2018-10-09 07:30 | 491 | 489
2018-10-09 08:00 | 488 | 487
2018-10-09 08:30 | 485 | 485
2018-10-09 09:00 | 491 | 491
2018-10-09 09:30 | 509 | 509
2018-10-09 10:00 | 521 | 518
2018-10-09 10:30 | 527 | 523
2018-10-09 11:00 | 528 | 524
2018-10-09 11:30 | 512 | 509
2018-10-09 12:00 | 502 | 500
2018-10-09 12:30 | 501 | 499
2018-10-09 13:00 | 484 | 483
2018-10-09 13:30 | 495 | 494
2018-10-09 14:00 | 507 | 506
2018-10-09 14:30 | 504 | 502
2018-10-09 15:00 | 517 | 515
2018-10-09 15:30 | 549 | 544
2018-10-09 16:00 | 555 | 549
2018-10-09 16:30 | 558 | 552
2018-10-09 17:00 | 572 | 566
2018-10-09 17:30 | 570 | 563
2018-10-09 18:00 | 578 | 571
2018-10-09 18:30 | 581 | 574
2018-10-09 19:00 | 573 | 566
2018-10-09 19:30 | 568 | 559
2018-10-09 20:00 | 554 | 547
2018-10-09 20:30 | 544 | 539
2018-10-09 21:00 | 537 | 532
2018-10-09 21:30 | 514 | 508
2018-10-09 22:00 | 479 | 477
2018-10-09 22:30 | 457 | 456
2018-10-09 23:00 | 441 | 439
2018-10-09 23:30 | 420 | 417
2018-10-10 | 402 | 398
2018-10-10 00:30 | 373 | 367
2018-10-10 01:00 | 365 | 358
2018-10-10 01:30 | 354 | 346
2018-10-10 02:00 | 341 | 331
2018-10-10 02:30 | 335 | 325
2018-10-10 03:00 | 317 | 306
2018-10-10 03:30 | 307 | 296
2018-10-10 04:00 | 306 | 295
2018-10-10 04:30 | 311 | 301
2018-10-10 05:00 | 340 | 332
2018-10-10 05:30 | 377 | 370
2018-10-10 06:00 | 404 | 397
2018-10-10 06:30 | 446 | 442
2018-10-10 07:00 | 503 | 495
2018-10-10 07:30 | 519 | 509
2018-10-10 08:00 | 511 | 500
2018-10-10 08:30 | 497 | 488
2018-10-10 09:00 | 478 | 471
2018-10-10 09:30 | 459 | 455
2018-10-10 10:00 | 457 | 454
2018-10-10 10:30 | 468 | 465
2018-10-10 11:00 | 469 | 465
2018-10-10 11:30 | 467 | 462
2018-10-10 12:00 | 470 | 465
2018-10-10 12:30 | 482 | 478
2018-10-10 13:00 | 486 | 483
2018-10-10 13:30 | 496 | 493
2018-10-10 14:00 | 502 | 499
2018-10-10 14:30 | 522 | 518
2018-10-10 15:00 | 543 | 539
2018-10-10 15:30 | 544 | 539
2018-10-10 16:00 | 571 | 566
2018-10-10 16:30 | 586 | 580
2018-10-10 17:00 | 587 | 580
2018-10-10 17:30 | 583 | 576
2018-10-10 18:00 | 589 | 582
2018-10-10 18:30 | 603 | 595
2018-10-10 19:00 | 608 | 601
2018-10-10 19:30 | 593 | 585
2018-10-10 20:00 | 574 | 569
2018-10-10 20:30 | 566 | 560
2018-10-10 21:00 | 529 | 523
2018-10-10 21:30 | 500 | 498
2018-10-10 22:00 | 471 | 469
2018-10-10 22:30 | 455 | 453
2018-10-10 23:00 | 436 | 434
2018-10-10 23:30 | 421 | 420
2018-10-11 | 401 | 398
2018-10-11 00:30 | 371 | 367
2018-10-11 01:00 | 356 | 351
2018-10-11 01:30 | 345 | 339
2018-10-11 02:00 | 329 | 323
2018-10-11 02:30 | 322 | 313
2018-10-11 03:00 | 314 | 305
2018-10-11 03:30 | 308 | 298
2018-10-11 04:00 | 310 | 300
2018-10-11 04:30 | 333 | 323
2018-10-11 05:00 | 351 | 343
2018-10-11 05:30 | 394 | 386
2018-10-11 06:00 | 420 | 414
2018-10-11 06:30 | 464 | 459
2018-10-11 07:00 | 508 | 499
2018-10-11 07:30 | 530 | 523
2018-10-11 08:00 | 530 | 519
2018-10-11 08:30 | 501 | 492
2018-10-11 09:00 | 494 | 486
2018-10-11 09:30 | 488 | 481
2018-10-11 10:00 | 498 | 492
2018-10-11 10:30 | 531 | 524
2018-10-11 11:00 | 564 | 555
2018-10-11 11:30 | 561 | 551
2018-10-11 12:00 | 567 | 557
2018-10-11 12:30 | 563 | 554
2018-10-11 13:00 | 564 | 558
2018-10-11 13:30 | 550 | 544
2018-10-11 14:00 | 498 | 494
2018-10-11 14:30 | 474 | 473
2018-10-11 15:00 | 499 | 499
2018-10-11 15:30 | 500 | 499
2018-10-11 16:00 | 522 | 520
2018-10-11 16:30 | 544 | 542
2018-10-11 17:00 | 559 | 557
2018-10-11 17:30 | 564 | 561
2018-10-11 18:00 | 572 | 569
2018-10-11 18:30 | 585 | 583
2018-10-11 19:00 | 582 | 578
2018-10-11 19:30 | 580 | 576
2018-10-11 20:00 | 574 | 572
2018-10-11 20:30 | 571 | 569
2018-10-11 21:00 | 530 | 529
2018-10-11 21:30 | 511 | 510
2018-10-11 22:00 | 475 | 475
2018-10-11 22:30 | 447 | 446
2018-10-11 23:00 | 432 | 430
2018-10-11 23:30 | 414 | 412
2018-10-12 | 397 | 393
2018-10-12 00:30 | 367 | 360
2018-10-12 01:00 | 341 | 332
2018-10-12 01:30 | 327 | 318
2018-10-12 02:00 | 315 | 306
2018-10-12 02:30 | 315 | 305
2018-10-12 03:00 | 309 | 299
2018-10-12 03:30 | 304 | 294
2018-10-12 04:00 | 304 | 295
2018-10-12 04:30 | 307 | 298
2018-10-12 05:00 | 322 | 315
2018-10-12 05:30 | 362 | 356
2018-10-12 06:00 | 402 | 396
2018-10-12 06:30 | 436 | 433
2018-10-12 07:00 | 468 | 467
2018-10-12 07:30 | 496 | 492
2018-10-12 08:00 | 502 | 499
2018-10-12 08:30 | 509 | 507
2018-10-12 09:00 | 501 | 499
2018-10-12 09:30 | 494 | 493
2018-10-12 10:00 | 496 | 495
2018-10-12 10:30 | 500 | 499
2018-10-12 11:00 | 504 | 502
2018-10-12 11:30 | 501 | 500
2018-10-12 12:00 | 509 | 508
2018-10-12 12:30 | 506 | 505
2018-10-12 13:00 | 507 | 506
2018-10-12 13:30 | 501 | 499
2018-10-12 14:00 | 517 | 516
2018-10-12 14:30 | 514 | 513
2018-10-12 15:00 | 518 | 516
2018-10-12 15:30 | 513 | 512
2018-10-12 16:00 | 527 | 525
2018-10-12 16:30 | 535 | 533
2018-10-12 17:00 | 549 | 547
2018-10-12 17:30 | 550 | 549
2018-10-12 18:00 | 559 | 558
2018-10-12 18:30 | 554 | 552
2018-10-12 19:00 | 557 | 555
2018-10-12 19:30 | 548 | 545
2018-10-12 20:00 | 525 | 522
2018-10-12 20:30 | 506 | 504
2018-10-12 21:00 | 494 | 492
2018-10-12 21:30 | 480 | 477
2018-10-12 22:00 | 478 | 474
2018-10-12 22:30 | 458 | 455
2018-10-12 23:00 | 451 | 448
2018-10-12 23:30 | 433 | 428
2018-10-13 | 409 | 403
2018-10-13 00:30 | 383 | 375
2018-10-13 01:00 | 359 | 351
2018-10-13 01:30 | 336 | 326
2018-10-13 02:00 | 329 | 315
2018-10-13 02:30 | 332 | 316
2018-10-13 03:00 | 329 | 312
2018-10-13 03:30 | 327 | 310
2018-10-13 04:00 | 318 | 301
2018-10-13 04:30 | 324 | 307
2018-10-13 05:00 | 321 | 304
2018-10-13 05:30 | 331 | 314
2018-10-13 06:00 | 344 | 326
2018-10-13 06:30 | 371 | 354
2018-10-13 07:00 | 392 | 377
2018-10-13 07:30 | 417 | 404
2018-10-13 08:00 | 427 | 416
2018-10-13 08:30 | 444 | 436
2018-10-13 09:00 | 446 | 441
2018-10-13 09:30 | 456 | 451
2018-10-13 10:00 | 465 | 460
2018-10-13 10:30 | 471 | 466
2018-10-13 11:00 | 461 | 456
2018-10-13 11:30 | 451 | 445
2018-10-13 12:00 | 455 | 449
2018-10-13 12:30 | 445 | 439
2018-10-13 13:00 | 439 | 432
2018-10-13 13:30 | 429 | 422
2018-10-13 14:00 | 426 | 419
2018-10-13 14:30 | 423 | 416
2018-10-13 15:00 | 422 | 415
2018-10-13 15:30 | 430 | 423
2018-10-13 16:00 | 444 | 438
2018-10-13 16:30 | 460 | 453
2018-10-13 17:00 | 451 | 445
2018-10-13 17:30 | 472 | 467
2018-10-13 18:00 | 490 | 485
2018-10-13 18:30 | 501 | 498
2018-10-13 19:00 | 503 | 500
2018-10-13 19:30 | 488 | 484
2018-10-13 20:00 | 474 | 470
2018-10-13 20:30 | 480 | 475
2018-10-13 21:00 | 478 | 472
2018-10-13 21:30 | 463 | 457
2018-10-13 22:00 | 454 | 448
2018-10-13 22:30 | 441 | 434
2018-10-13 23:00 | 423 | 415
2018-10-13 23:30 | 403 | 393
2018-10-14 | 397 | 384
2018-10-14 00:30 | 366 | 351
2018-10-14 01:00 | 359 | 342
2018-10-14 01:30 | 338 | 320
2018-10-14 02:00 | 320 | 301
2018-10-14 02:30 | 308 | 288
2018-10-14 03:00 | 290 | 269
2018-10-14 03:30 | 305 | 285
2018-10-14 04:00 | 299 | 279
2018-10-14 04:30 | 287 | 265
2018-10-14 05:00 | 285 | 263
2018-10-14 05:30 | 307 | 286
2018-10-14 06:00 | 327 | 303
2018-10-14 06:30 | 334 | 311
2018-10-14 07:00 | 340 | 319
2018-10-14 07:30 | 359 | 340
2018-10-14 08:00 | 378 | 363
2018-10-14 08:30 | 391 | 378
2018-10-14 09:00 | 405 | 394
2018-10-14 09:30 | 410 | 401
2018-10-14 10:00 | 415 | 408
2018-10-14 10:30 | 420 | 414
2018-10-14 11:00 | 420 | 412
2018-10-14 11:30 | 420 | 413
2018-10-14 12:00 | 424 | 417
2018-10-14 12:30 | 427 | 420
2018-10-14 13:00 | 416 | 408
2018-10-14 13:30 | 413 | 405
2018-10-14 14:00 | 417 | 409
2018-10-14 14:30 | 406 | 398
2018-10-14 15:00 | 418 | 411
2018-10-14 15:30 | 413 | 406
2018-10-14 16:00 | 423 | 416
2018-10-14 16:30 | 449 | 443
2018-10-14 17:00 | 485 | 480
2018-10-14 17:30 | 499 | 495
2018-10-14 18:00 | 505 | 501
2018-10-14 18:30 | 530 | 525
2018-10-14 19:00 | 534 | 530
2018-10-14 19:30 | 521 | 516
2018-10-14 20:00 | 503 | 498
2018-10-14 20:30 | 482 | 479
2018-10-14 21:00 | 453 | 450
2018-10-14 21:30 | 440 | 435
2018-10-14 22:00 | 434 | 428
2018-10-14 22:30 | 420 | 414
2018-10-14 23:00 | 415 | 408
2018-10-14 23:30 | 410 | 401
2018-10-15 | 395 | 382
2018-10-15 00:30 | 363 | 348
2018-10-15 01:00 | 346 | 330
2018-10-15 01:30 | 335 | 318
2018-10-15 02:00 | 324 | 306
2018-10-15 02:30 | 320 | 299
2018-10-15 03:00 | 312 | 291
2018-10-15 03:30 | 310 | 289
2018-10-15 04:00 | 316 | 295
2018-10-15 04:30 | 318 | 298
2018-10-15 05:00 | 329 | 312
2018-10-15 05:30 | 368 | 353
2018-10-15 06:00 | 413 | 400
2018-10-15 06:30 | 442 | 435
2018-10-15 07:00 | 495 | 488
2018-10-15 07:30 | 522 | 519
2018-10-15 08:00 | 520 | 518
2018-10-15 08:30 | 516 | 514
2018-10-15 09:00 | 517 | 515
2018-10-15 09:30 | 509 | 508
2018-10-15 10:00 | 509 | 507
2018-10-15 10:30 | 501 | 500
2018-10-15 11:00 | 508 | 507
2018-10-15 11:30 | 509 | 508
2018-10-15 12:00 | 511 | 510
2018-10-15 12:30 | 503 | 502
2018-10-15 13:00 | 491 | 490
2018-10-15 13:30 | 489 | 487
2018-10-15 14:00 | 495 | 494
2018-10-15 14:30 | 505 | 504
2018-10-15 15:00 | 503 | 502
2018-10-15 15:30 | 498 | 496
2018-10-15 16:00 | 505 | 503
2018-10-15 16:30 | 514 | 512
2018-10-15 17:00 | 533 | 532
2018-10-15 17:30 | 532 | 530
2018-10-15 18:00 | 546 | 542
2018-10-15 18:30 | 553 | 551
2018-10-15 19:00 | 556 | 554
2018-10-15 19:30 | 548 | 544
2018-10-15 20:00 | 541 | 538
2018-10-15 20:30 | 529 | 528
2018-10-15 21:00 | 511 | 509
2018-10-15 21:30 | 486 | 483
2018-10-15 22:00 | 474 | 470
2018-10-15 22:30 | 460 | 456
2018-10-15 23:00 | 442 | 439
2018-10-15 23:30 | 411 | 407
2018-10-16 | 399 | 393
2018-10-16 00:30 | 370 | 361
2018-10-16 01:00 | 349 | 339
2018-10-16 01:30 | 322 | 310
2018-10-16 02:00 | 316 | 302
2018-10-16 02:30 | 305 | 290
2018-10-16 03:00 | 300 | 284
2018-10-16 03:30 | 297 | 281
2018-10-16 04:00 | 314 | 300
2018-10-16 04:30 | 327 | 314
2018-10-16 05:00 | 338 | 327
2018-10-16 05:30 | 375 | 365
2018-10-16 06:00 | 416 | 408
2018-10-16 06:30 | 450 | 445
2018-10-16 07:00 | 484 | 480
2018-10-16 07:30 | 504 | 502
2018-10-16 08:00 | 512 | 510
2018-10-16 08:30 | 517 | 515
2018-10-16 09:00 | 514 | 514
2018-10-16 09:30 | 510 | 509
2018-10-16 10:00 | 504 | 503
2018-10-16 10:30 | 498 | 498
2018-10-16 11:00 | 489 | 489
2018-10-16 11:30 | 490 | 489
2018-10-16 12:00 | 488 | 488
2018-10-16 12:30 | 480 | 480
2018-10-16 13:00 | 483 | 482
2018-10-16 13:30 | 487 | 487
2018-10-16 14:00 | 496 | 496
2018-10-16 14:30 | 498 | 498
2018-10-16 15:00 | 504 | 503
2018-10-16 15:30 | 504 | 503
2018-10-16 16:00 | 523 | 523
2018-10-16 16:30 | 537 | 536
2018-10-16 17:00 | 546 | 546
2018-10-16 17:30 | 551 | 550
2018-10-16 18:00 | 552 | 551
2018-10-16 18:30 | 545 | 545
2018-10-16 19:00 | 544 | 544
2018-10-16 19:30 | 534 | 534
2018-10-16 20:00 | 533 | 532
2018-10-16 20:30 | 531 | 530
2018-10-16 21:00 | 510 | 509
2018-10-16 21:30 | 487 | 486
2018-10-16 22:00 | 474 | 473
2018-10-16 22:30 | 460 | 458
2018-10-16 23:00 | 454 | 452
2018-10-16 23:30 | 436 | 434
2018-10-17 | 426 | 422
2018-10-17 00:30 | 389 | 384
2018-10-17 01:00 | 367 | 361
2018-10-17 01:30 | 350 | 343
2018-10-17 02:00 | 336 | 328
2018-10-17 02:30 | 323 | 315
2018-10-17 03:00 | 313 | 305
2018-10-17 03:30 | 326 | 317
2018-10-17 04:00 | 332 | 324
2018-10-17 04:30 | 344 | 336
2018-10-17 05:00 | 352 | 345
2018-10-17 05:30 | 383 | 376
2018-10-17 06:00 | 404 | 399
2018-10-17 06:30 | 451 | 449
2018-10-17 07:00 | 498 | 492
2018-10-17 07:30 | 518 | 510
2018-10-17 08:00 | 531 | 523
2018-10-17 08:30 | 530 | 524
2018-10-17 09:00 | 519 | 514
2018-10-17 09:30 | 526 | 521
2018-10-17 10:00 | 528 | 522
2018-10-17 10:30 | 524 | 516
2018-10-17 11:00 | 519 | 512
2018-10-17 11:30 | 510 | 504
2018-10-17 12:00 | 512 | 505
2018-10-17 12:30 | 509 | 502
2018-10-17 13:00 | 511 | 505
2018-10-17 13:30 | 509 | 502
2018-10-17 14:00 | 505 | 499
2018-10-17 14:30 | 502 | 497
2018-10-17 15:00 | 510 | 504
2018-10-17 15:30 | 529 | 523
2018-10-17 16:00 | 553 | 547
2018-10-17 16:30 | 569 | 563
2018-10-17 17:00 | 577 | 571
2018-10-17 17:30 | 575 | 568
2018-10-17 18:00 | 585 | 578
2018-10-17 18:30 | 588 | 582
2018-10-17 19:00 | 594 | 588
2018-10-17 19:30 | 572 | 567
2018-10-17 20:00 | 568 | 563
2018-10-17 20:30 | 553 | 549
2018-10-17 21:00 | 531 | 530
2018-10-17 21:30 | 515 | 514
2018-10-17 22:00 | 504 | 503
2018-10-17 22:30 | 490 | 488
2018-10-17 23:00 | 474 | 471
2018-10-17 23:30 | 458 | 454
2018-10-18 | 433 | 428
2018-10-18 00:30 | 404 | 397
2018-10-18 01:00 | 389 | 379
2018-10-18 01:30 | 371 | 361
2018-10-18 02:00 | 355 | 344
2018-10-18 02:30 | 334 | 321
2018-10-18 03:00 | 329 | 313
2018-10-18 03:30 | 333 | 315
2018-10-18 04:00 | 336 | 319
2018-10-18 04:30 | 344 | 328
2018-10-18 05:00 | 364 | 350
2018-10-18 05:30 | 420 | 409
2018-10-18 06:00 | 454 | 444
2018-10-18 06:30 | 487 | 481
2018-10-18 07:00 | 532 | 521
2018-10-18 07:30 | 560 | 548
2018-10-18 08:00 | 561 | 550
2018-10-18 08:30 | 559 | 548
2018-10-18 09:00 | 551 | 540
2018-10-18 09:30 | 551 | 541
2018-10-18 10:00 | 554 | 544
2018-10-18 10:30 | 553 | 544
2018-10-18 11:00 | 550 | 541
2018-10-18 11:30 | 548 | 538
2018-10-18 12:00 | 520 | 513
2018-10-18 12:30 | 504 | 502
2018-10-18 13:00 | 533 | 531
2018-10-18 13:30 | 524 | 522
2018-10-18 14:00 | 517 | 516
2018-10-18 14:30 | 527 | 525
2018-10-18 15:00 | 537 | 535
2018-10-18 15:30 | 541 | 538
2018-10-18 16:00 | 542 | 540
2018-10-18 16:30 | 547 | 544
2018-10-18 17:00 | 563 | 559
2018-10-18 17:30 | 582 | 579
2018-10-18 18:00 | 581 | 578
2018-10-18 18:30 | 585 | 582
2018-10-18 19:00 | 579 | 575
2018-10-18 19:30 | 573 | 569
2018-10-18 20:00 | 578 | 573
2018-10-18 20:30 | 579 | 575
2018-10-18 21:00 | 546 | 544
2018-10-18 21:30 | 531 | 529
2018-10-18 22:00 | 509 | 506
2018-10-18 22:30 | 502 | 499
2018-10-18 23:00 | 486 | 482
2018-10-18 23:30 | 467 | 462
2018-10-19 | 438 | 431
2018-10-19 00:30 | 412 | 403
2018-10-19 01:00 | 397 | 386
2018-10-19 01:30 | 382 | 369
2018-10-19 02:00 | 377 | 363
2018-10-19 02:30 | 372 | 359
2018-10-19 03:00 | 368 | 355
2018-10-19 03:30 | 365 | 353
2018-10-19 04:00 | 369 | 356
2018-10-19 04:30 | 372 | 360
2018-10-19 05:00 | 385 | 374
2018-10-19 05:30 | 412 | 402
2018-10-19 06:00 | 417 | 408
2018-10-19 06:30 | 439 | 434
2018-10-19 07:00 | 467 | 463
2018-10-19 07:30 | 486 | 484
2018-10-19 08:00 | 480 | 478
2018-10-19 08:30 | 481 | 479
2018-10-19 09:00 | 479 | 478
2018-10-19 09:30 | 479 | 478
2018-10-19 10:00 | 483 | 482
2018-10-19 10:30 | 481 | 479
2018-10-19 11:00 | 485 | 484
2018-10-19 11:30 | 501 | 500
2018-10-19 12:00 | 517 | 516
2018-10-19 12:30 | 516 | 514
2018-10-19 13:00 | 521 | 519
2018-10-19 13:30 | 539 | 537
2018-10-19 14:00 | 539 | 537
2018-10-19 14:30 | 511 | 509
2018-10-19 15:00 | 504 | 501
2018-10-19 15:30 | 517 | 514
2018-10-19 16:00 | 536 | 533
2018-10-19 16:30 | 535 | 533
2018-10-19 17:00 | 552 | 549
2018-10-19 17:30 | 553 | 550
2018-10-19 18:00 | 561 | 557
2018-10-19 18:30 | 555 | 551
2018-10-19 19:00 | 564 | 561
2018-10-19 19:30 | 551 | 547
2018-10-19 20:00 | 538 | 536
2018-10-19 20:30 | 527 | 525
2018-10-19 21:00 | 507 | 506
2018-10-19 21:30 | 498 | 495
2018-10-19 22:00 | 486 | 482
2018-10-19 22:30 | 473 | 469
2018-10-19 23:00 | 456 | 452
2018-10-19 23:30 | 441 | 434
2018-10-20 | 421 | 413
2018-10-20 00:30 | 378 | 368
2018-10-20 01:00 | 355 | 342
2018-10-20 01:30 | 336 | 321
2018-10-20 02:00 | 322 | 306
2018-10-20 02:30 | 315 | 298
2018-10-20 03:00 | 312 | 293
2018-10-20 03:30 | 308 | 288
2018-10-20 04:00 | 305 | 285
2018-10-20 04:30 | 313 | 293
2018-10-20 05:00 | 322 | 302
2018-10-20 05:30 | 325 | 304
2018-10-20 06:00 | 353 | 331
2018-10-20 06:30 | 385 | 364
2018-10-20 07:00 | 415 | 396
2018-10-20 07:30 | 439 | 423
2018-10-20 08:00 | 452 | 439
2018-10-20 08:30 | 464 | 454
2018-10-20 09:00 | 459 | 450
2018-10-20 09:30 | 463 | 455
2018-10-20 10:00 | 466 | 458
2018-10-20 10:30 | 462 | 454
2018-10-20 11:00 | 450 | 441
2018-10-20 11:30 | 424 | 415
2018-10-20 12:00 | 397 | 390
2018-10-20 12:30 | 400 | 392
2018-10-20 13:00 | 397 | 389
2018-10-20 13:30 | 391 | 383
2018-10-20 14:00 | 381 | 373
2018-10-20 14:30 | 390 | 383
2018-10-20 15:00 | 403 | 396
2018-10-20 15:30 | 424 | 417
2018-10-20 16:00 | 450 | 444
2018-10-20 16:30 | 471 | 465
2018-10-20 17:00 | 494 | 489
2018-10-20 17:30 | 497 | 492
2018-10-20 18:00 | 487 | 482
2018-10-20 18:30 | 503 | 499
2018-10-20 19:00 | 511 | 506
2018-10-20 19:30 | 494 | 490
2018-10-20 20:00 | 506 | 501
2018-10-20 20:30 | 503 | 497
2018-10-20 21:00 | 484 | 478
2018-10-20 21:30 | 478 | 470
2018-10-20 22:00 | 457 | 448
2018-10-20 22:30 | 467 | 457
2018-10-20 23:00 | 466 | 455
2018-10-20 23:30 | 444 | 432
2018-10-21 | 416 | 402
2018-10-21 00:30 | 383 | 364
2018-10-21 01:00 | 367 | 346
2018-10-21 01:30 | 357 | 334
2018-10-21 02:00 | 349 | 323
2018-10-21 02:30 | 336 | 309
2018-10-21 03:00 | 339 | 311
2018-10-21 03:30 | 339 | 309
2018-10-21 04:00 | 336 | 306
2018-10-21 04:30 | 337 | 307
2018-10-21 05:00 | 341 | 312
2018-10-21 05:30 | 352 | 321
2018-10-21 06:00 | 362 | 330
2018-10-21 06:30 | 364 | 333
2018-10-21 07:00 | 373 | 344
2018-10-21 07:30 | 384 | 357
2018-10-21 08:00 | 399 | 375
2018-10-21 08:30 | 413 | 393
2018-10-21 09:00 | 400 | 382
2018-10-21 09:30 | 384 | 366
2018-10-21 10:00 | 376 | 360
2018-10-21 10:30 | 386 | 371
2018-10-21 11:00 | 380 | 365
2018-10-21 11:30 | 387 | 375
2018-10-21 12:00 | 396 | 385
2018-10-21 12:30 | 401 | 390
2018-10-21 13:00 | 403 | 392
2018-10-21 13:30 | 404 | 393
2018-10-21 14:00 | 456 | 449
2018-10-21 14:30 | 507 | 500
2018-10-21 15:00 | 514 | 507
2018-10-21 15:30 | 511 | 504
2018-10-21 16:00 | 520 | 511
2018-10-21 16:30 | 506 | 497
2018-10-21 17:00 | 515 | 506
2018-10-21 17:30 | 513 | 503
2018-10-21 18:00 | 505 | 497
2018-10-21 18:30 | 508 | 502
2018-10-21 19:00 | 525 | 520
2018-10-21 19:30 | 520 | 514
2018-10-21 20:00 | 525 | 519
2018-10-21 20:30 | 503 | 496
2018-10-21 21:00 | 485 | 477
2018-10-21 21:30 | 469 | 459
2018-10-21 22:00 | 453 | 442
2018-10-21 22:30 | 436 | 423
2018-10-21 23:00 | 417 | 403
2018-10-21 23:30 | 403 | 388
2018-10-22 | 396 | 378
2018-10-22 00:30 | 377 | 355
2018-10-22 01:00 | 380 | 357
2018-10-22 01:30 | 371 | 344
2018-10-22 02:00 | 359 | 331
2018-10-22 02:30 | 350 | 321
2018-10-22 03:00 | 327 | 295
2018-10-22 03:30 | 310 | 277
2018-10-22 04:00 | 311 | 277
2018-10-22 04:30 | 320 | 289
2018-10-22 05:00 | 342 | 313
2018-10-22 05:30 | 357 | 331
2018-10-22 06:00 | 372 | 354
2018-10-22 06:30 | 414 | 403
2018-10-22 07:00 | 450 | 441
2018-10-22 07:30 | 455 | 450
2018-10-22 08:00 | 446 | 443
2018-10-22 08:30 | 439 | 436
2018-10-22 09:00 | 437 | 435
2018-10-22 09:30 | 442 | 440
2018-10-22 10:00 | 453 | 451
2018-10-22 10:30 | 462 | 460
2018-10-22 11:00 | 472 | 466
2018-10-22 11:30 | 462 | 456
2018-10-22 12:00 | 466 | 460
2018-10-22 12:30 | 470 | 465
2018-10-22 13:00 | 478 | 473
2018-10-22 13:30 | 483 | 479
2018-10-22 14:00 | 503 | 498
2018-10-22 14:30 | 504 | 500
2018-10-22 15:00 | 501 | 496
2018-10-22 15:30 | 505 | 500
2018-10-22 16:00 | 515 | 510
2018-10-22 16:30 | 533 | 528
2018-10-22 17:00 | 555 | 549
2018-10-22 17:30 | 548 | 542
2018-10-22 18:00 | 549 | 542
2018-10-22 18:30 | 561 | 554
2018-10-22 19:00 | 567 | 561
2018-10-22 19:30 | 565 | 558
2018-10-22 20:00 | 556 | 550
2018-10-22 20:30 | 553 | 545
2018-10-22 21:00 | 533 | 525
2018-10-22 21:30 | 506 | 500
2018-10-22 22:00 | 481 | 475
2018-10-22 22:30 | 458 | 452
2018-10-22 23:00 | 449 | 442
2018-10-22 23:30 | 424 | 416
2018-10-23 | 400 | 388
2018-10-23 00:30 | 381 | 365
2018-10-23 01:00 | 374 | 357
2018-10-23 01:30 | 364 | 346
2018-10-23 02:00 | 360 | 339
2018-10-23 02:30 | 351 | 329
2018-10-23 03:00 | 353 | 330
2018-10-23 03:30 | 347 | 324
2018-10-23 04:00 | 349 | 326
2018-10-23 04:30 | 344 | 321
2018-10-23 05:00 | 338 | 316
2018-10-23 05:30 | 367 | 347
2018-10-23 06:00 | 400 | 383
2018-10-23 06:30 | 440 | 429
2018-10-23 07:00 | 476 | 469
2018-10-23 07:30 | 484 | 481
2018-10-23 08:00 | 465 | 463
2018-10-23 08:30 | 456 | 454
2018-10-23 09:00 | 448 | 445
2018-10-23 09:30 | 453 | 451
2018-10-23 10:00 | 456 | 454
2018-10-23 10:30 | 446 | 444
2018-10-23 11:00 | 437 | 436
2018-10-23 11:30 | 444 | 441
2018-10-23 12:00 | 445 | 442
2018-10-23 12:30 | 454 | 451
2018-10-23 13:00 | 465 | 463
2018-10-23 13:30 | 472 | 469
2018-10-23 14:00 | 478 | 476
2018-10-23 14:30 | 483 | 480
2018-10-23 15:00 | 490 | 487
2018-10-23 15:30 | 517 | 513
2018-10-23 16:00 | 562 | 550
2018-10-23 16:30 | 579 | 565
2018-10-23 17:00 | 596 | 582
2018-10-23 17:30 | 592 | 576
2018-10-23 18:00 | 589 | 573
2018-10-23 18:30 | 590 | 575
2018-10-23 19:00 | 604 | 591
2018-10-23 19:30 | 612 | 606
2018-10-23 20:00 | 588 | 580
2018-10-23 20:30 | 570 | 563
2018-10-23 21:00 | 536 | 531
2018-10-23 21:30 | 527 | 522
2018-10-23 22:00 | 504 | 497
2018-10-23 22:30 | 485 | 477
2018-10-23 23:00 | 473 | 464
2018-10-23 23:30 | 444 | 433
2018-10-24 | 416 | 401
2018-10-24 00:30 | 409 | 390
2018-10-24 01:00 | 396 | 375
2018-10-24 01:30 | 381 | 358
2018-10-24 02:00 | 379 | 354
2018-10-24 02:30 | 378 | 353
2018-10-24 03:00 | 374 | 349
2018-10-24 03:30 | 371 | 345
2018-10-24 04:00 | 373 | 348
2018-10-24 04:30 | 373 | 348
2018-10-24 05:00 | 387 | 363
2018-10-24 05:30 | 408 | 385
2018-10-24 06:00 | 467 | 449
2018-10-24 06:30 | 505 | 493
2018-10-24 07:00 | 535 | 527
2018-10-24 07:30 | 549 | 541
2018-10-24 08:00 | 537 | 531
2018-10-24 08:30 | 531 | 526
2018-10-24 09:00 | 528 | 525
2018-10-24 09:30 | 520 | 516
2018-10-24 10:00 | 521 | 518
2018-10-24 10:30 | 525 | 522
2018-10-24 11:00 | 527 | 525
2018-10-24 11:30 | 528 | 526
2018-10-24 12:00 | 535 | 533
2018-10-24 12:30 | 537 | 536
2018-10-24 13:00 | 547 | 545
2018-10-24 13:30 | 572 | 569
2018-10-24 14:00 | 591 | 589
2018-10-24 14:30 | 605 | 602
2018-10-24 15:00 | 608 | 605
2018-10-24 15:30 | 608 | 605
2018-10-24 16:00 | 620 | 617
2018-10-24 16:30 | 636 | 631
2018-10-24 17:00 | 646 | 641
2018-10-24 17:30 | 647 | 639
2018-10-24 18:00 | 645 | 634
2018-10-24 18:30 | 641 | 628
2018-10-24 19:00 | 650 | 637
2018-10-24 19:30 | 620 | 606
2018-10-24 20:00 | 590 | 576
2018-10-24 20:30 | 578 | 568
2018-10-24 21:00 | 553 | 550
2018-10-24 21:30 | 528 | 523
2018-10-24 22:00 | 509 | 503
2018-10-24 22:30 | 489 | 483
2018-10-24 23:00 | 474 | 467
2018-10-24 23:30 | 457 | 448
2018-10-25 | 441 | 429
2018-10-25 00:30 | 439 | 425
2018-10-25 01:00 | 413 | 397
2018-10-25 01:30 | 397 | 380
2018-10-25 02:00 | 394 | 376
2018-10-25 02:30 | 397 | 378
2018-10-25 03:00 | 400 | 381
2018-10-25 03:30 | 398 | 379
2018-10-25 04:00 | 404 | 385
2018-10-25 04:30 | 420 | 401
2018-10-25 05:00 | 421 | 403
2018-10-25 05:30 | 454 | 437
2018-10-25 06:00 | 485 | 471
2018-10-25 06:30 | 519 | 511
2018-10-25 07:00 | 538 | 532
2018-10-25 07:30 | 568 | 560
2018-10-25 08:00 | 580 | 568
2018-10-25 08:30 | 569 | 559
2018-10-25 09:00 | 558 | 550
2018-10-25 09:30 | 569 | 562
2018-10-25 10:00 | 585 | 577
2018-10-25 10:30 | 608 | 598
2018-10-25 11:00 | 604 | 593
2018-10-25 11:30 | 588 | 578
2018-10-25 12:00 | 574 | 564
2018-10-25 12:30 | 558 | 548
2018-10-25 13:00 | 559 | 549
2018-10-25 13:30 | 582 | 571
2018-10-25 14:00 | 584 | 575
2018-10-25 14:30 | 590 | 581
2018-10-25 15:00 | 589 | 580
2018-10-25 15:30 | 601 | 592
2018-10-25 16:00 | 616 | 605
2018-10-25 16:30 | 620 | 608
2018-10-25 17:00 | 620 | 608
2018-10-25 17:30 | 628 | 616
2018-10-25 18:00 | 624 | 611
2018-10-25 18:30 | 624 | 611
2018-10-25 19:00 | 627 | 614
2018-10-25 19:30 | 628 | 616
2018-10-25 20:00 | 621 | 616
2018-10-25 20:30 | 610 | 607
2018-10-25 21:00 | 591 | 587
2018-10-25 21:30 | 557 | 551
2018-10-25 22:00 | 542 | 536
2018-10-25 22:30 | 521 | 516
2018-10-25 23:00 | 504 | 498
2018-10-25 23:30 | 483 | 474
2018-10-26 | 448 | 438
2018-10-26 00:30 | 412 | 399
2018-10-26 01:00 | 391 | 374
2018-10-26 01:30 | 371 | 352
2018-10-26 02:00 | 370 | 351
2018-10-26 02:30 | 373 | 353
2018-10-26 03:00 | 364 | 343
2018-10-26 03:30 | 361 | 339
2018-10-26 04:00 | 366 | 345
2018-10-26 04:30 | 372 | 352
2018-10-26 05:00 | 387 | 368
2018-10-26 05:30 | 418 | 402
2018-10-26 06:00 | 470 | 452
2018-10-26 06:30 | 504 | 491
2018-10-26 07:00 | 527 | 519
2018-10-26 07:30 | 545 | 540
2018-10-26 08:00 | 544 | 539
2018-10-26 08:30 | 541 | 537
2018-10-26 09:00 | 542 | 539
2018-10-26 09:30 | 547 | 544
2018-10-26 10:00 | 550 | 546
2018-10-26 10:30 | 544 | 540
2018-10-26 11:00 | 530 | 527
2018-10-26 11:30 | 540 | 537
2018-10-26 12:00 | 559 | 555
2018-10-26 12:30 | 556 | 551
2018-10-26 13:00 | 572 | 567
2018-10-26 13:30 | 589 | 583
2018-10-26 14:00 | 598 | 593
2018-10-26 14:30 | 614 | 607
2018-10-26 15:00 | 632 | 620
2018-10-26 15:30 | 639 | 628
2018-10-26 16:00 | 653 | 642
2018-10-26 16:30 | 679 | 668
2018-10-26 17:00 | 691 | 680
2018-10-26 17:30 | 688 | 673
2018-10-26 18:00 | 663 | 645
2018-10-26 18:30 | 637 | 621
2018-10-26 19:00 | 630 | 618
2018-10-26 19:30 | 602 | 597
2018-10-26 20:00 | 574 | 570
2018-10-26 20:30 | 563 | 559
2018-10-26 21:00 | 538 | 535
2018-10-26 21:30 | 523 | 517
2018-10-26 22:00 | 512 | 504
2018-10-26 22:30 | 495 | 487
2018-10-26 23:00 | 479 | 469
2018-10-26 23:30 | 461 | 449
2018-10-27 | 418 | 403
2018-10-27 00:30 | 387 | 370
2018-10-27 01:00 | 370 | 350
2018-10-27 01:30 | 361 | 344
2018-10-27 02:00 | 353 | 337
2018-10-27 02:30 | 350 | 334
2018-10-27 03:00 | 348 | 331
2018-10-27 03:30 | 340 | 323
2018-10-27 04:00 | 338 | 320
2018-10-27 04:30 | 342 | 325
2018-10-27 05:00 | 345 | 327
2018-10-27 05:30 | 355 | 336
2018-10-27 06:00 | 361 | 342
2018-10-27 06:30 | 368 | 351
2018-10-27 07:00 | 380 | 365
2018-10-27 07:30 | 393 | 387
2018-10-27 08:00 | 398 | 395
2018-10-27 08:30 | 399 | 397
2018-10-27 09:00 | 400 | 398
2018-10-27 09:30 | 401 | 400
2018-10-27 10:00 | 401 | 399
2018-10-27 10:30 | 404 | 402
2018-10-27 11:00 | 394 | 392
2018-10-27 11:30 | 373 | 371
2018-10-27 12:00 | 369 | 367
2018-10-27 12:30 | 370 | 368
2018-10-27 13:00 | 380 | 378
2018-10-27 13:30 | 384 | 382
2018-10-27 14:00 | 389 | 387
2018-10-27 14:30 | 402 | 400
2018-10-27 15:00 | 414 | 412
2018-10-27 15:30 | 442 | 440
2018-10-27 16:00 | 467 | 466
2018-10-27 16:30 | 482 | 482
2018-10-27 17:00 | 505 | 505
2018-10-27 17:30 | 509 | 508
2018-10-27 18:00 | 501 | 500
2018-10-27 18:30 | 507 | 505
2018-10-27 19:00 | 520 | 520
2018-10-27 19:30 | 519 | 518
2018-10-27 20:00 | 513 | 511
2018-10-27 20:30 | 502 | 501
2018-10-27 21:00 | 484 | 484
2018-10-27 21:30 | 472 | 470
2018-10-27 22:00 | 459 | 457
2018-10-27 22:30 | 452 | 450
2018-10-27 23:00 | 442 | 440
2018-10-27 23:30 | 409 | 406
2018-10-28 | 378 | 374
2018-10-28 00:30 | 355 | 349
2018-10-28 01:00 | 342 | 335
2018-10-28 01:30 | 337 | 330
2018-10-28 02:00 | 325 | 317
2018-10-28 02:30 | 322 | 314
2018-10-28 03:00 | 324 | 315
2018-10-28 03:30 | 319 | 311
2018-10-28 04:00 | 323 | 315
2018-10-28 04:30 | 319 | 310
2018-10-28 05:00 | 320 | 311
2018-10-28 05:30 | 330 | 318
2018-10-28 06:00 | 328 | 316
2018-10-28 06:30 | 334 | 323
2018-10-28 07:00 | 352 | 342
2018-10-28 07:30 | 374 | 366
2018-10-28 08:00 | 386 | 379
2018-10-28 08:30 | 411 | 405
2018-10-28 09:00 | 416 | 412
2018-10-28 09:30 | 405 | 402
2018-10-28 10:00 | 449 | 448
2018-10-28 10:30 | 394 | 392
2018-10-28 11:00 | 369 | 367
2018-10-28 11:30 | 371 | 369
2018-10-28 12:00 | 371 | 370
2018-10-28 12:30 | 387 | 386
2018-10-28 13:00 | 393 | 392
2018-10-28 13:30 | 404 | 403
2018-10-28 14:00 | 410 | 410
2018-10-28 14:30 | 415 | 414
2018-10-28 15:00 | 449 | 448
2018-10-28 15:30 | 465 | 465
2018-10-28 16:00 | 479 | 479
2018-10-28 16:30 | 498 | 498
2018-10-28 17:00 | 503 | 503
2018-10-28 17:30 | 507 | 507
2018-10-28 18:00 | 511 | 510
2018-10-28 18:30 | 516 | 516
2018-10-28 19:00 | 519 | 519
2018-10-28 19:30 | 511 | 510
2018-10-28 20:00 | 500 | 500
2018-10-28 20:30 | 486 | 486
2018-10-28 21:00 | 454 | 453
2018-10-28 21:30 | 438 | 437
2018-10-28 22:00 | 429 | 428
2018-10-28 22:30 | 420 | 418
2018-10-28 23:00 | 404 | 402
2018-10-28 23:30 | 392 | 388
2018-10-29 | 376 | 370
2018-10-29 00:30 | 356 | 348
2018-10-29 01:00 | 346 | 337
2018-10-29 01:30 | 335 | 325
2018-10-29 02:00 | 330 | 320
2018-10-29 02:30 | 332 | 322
2018-10-29 03:00 | 320 | 309
2018-10-29 03:30 | 314 | 303
2018-10-29 04:00 | 316 | 306
2018-10-29 04:30 | 320 | 311
2018-10-29 05:00 | 338 | 330
2018-10-29 05:30 | 378 | 371
2018-10-29 06:00 | 405 | 400
2018-10-29 06:30 | 453 | 450
2018-10-29 07:00 | 497 | 495
2018-10-29 07:30 | 517 | 516
2018-10-29 08:00 | 531 | 531
2018-10-29 08:30 | 532 | 530
2018-10-29 09:00 | 537 | 535
2018-10-29 09:30 | 530 | 529
2018-10-29 10:00 | 542 | 541
2018-10-29 10:30 | 542 | 541
2018-10-29 11:00 | 543 | 542
2018-10-29 11:30 | 541 | 540
2018-10-29 12:00 | 541 | 541
2018-10-29 12:30 | 542 | 541
2018-10-29 13:00 | 537 | 536
2018-10-29 13:30 | 537 | 536
2018-10-29 14:00 | 521 | 520
2018-10-29 14:30 | 509 | 508
2018-10-29 15:00 | 517 | 515
2018-10-29 15:30 | 527 | 525
2018-10-29 16:00 | 538 | 536
2018-10-29 16:30 | 548 | 547
2018-10-29 17:00 | 553 | 552
2018-10-29 17:30 | 559 | 557
2018-10-29 18:00 | 558 | 557
2018-10-29 18:30 | 556 | 555
2018-10-29 19:00 | 565 | 564
2018-10-29 19:30 | 548 | 547
2018-10-29 20:00 | 529 | 528
2018-10-29 20:30 | 507 | 506
2018-10-29 21:00 | 474 | 474
2018-10-29 21:30 | 450 | 449
2018-10-29 22:00 | 441 | 439
2018-10-29 22:30 | 428 | 426
2018-10-29 23:00 | 408 | 405
2018-10-29 23:30 | 392 | 388
2018-10-30 | 373 | 367
2018-10-30 00:30 | 343 | 334
2018-10-30 01:00 | 329 | 318
2018-10-30 01:30 | 320 | 307
2018-10-30 02:00 | 317 | 304
2018-10-30 02:30 | 317 | 304
2018-10-30 03:00 | 318 | 304
2018-10-30 03:30 | 317 | 303
2018-10-30 04:00 | 315 | 301
2018-10-30 04:30 | 315 | 302
2018-10-30 05:00 | 321 | 309
2018-10-30 05:30 | 344 | 333
2018-10-30 06:00 | 382 | 374
2018-10-30 06:30 | 426 | 421
2018-10-30 07:00 | 457 | 455
2018-10-30 07:30 | 470 | 470
2018-10-30 08:00 | 464 | 464
2018-10-30 08:30 | 453 | 453
2018-10-30 09:00 | 450 | 450
2018-10-30 09:30 | 459 | 459
2018-10-30 10:00 | 455 | 455
2018-10-30 10:30 | 463 | 463
2018-10-30 11:00 | 458 | 458
2018-10-30 11:30 | 452 | 452
2018-10-30 12:00 | 448 | 448
2018-10-30 12:30 | 447 | 447
2018-10-30 13:00 | 448 | 448
2018-10-30 13:30 | 450 | 450
2018-10-30 14:00 | 444 | 444
2018-10-30 14:30 | 448 | 448
2018-10-30 15:00 | 473 | 473
2018-10-30 15:30 | 492 | 491
2018-10-30 16:00 | 500 | 499
2018-10-30 16:30 | 532 | 531
2018-10-30 17:00 | 549 | 548
2018-10-30 17:30 | 558 | 557
2018-10-30 18:00 | 558 | 557
2018-10-30 18:30 | 560 | 558
2018-10-30 19:00 | 580 | 579
2018-10-30 19:30 | 568 | 567
2018-10-30 20:00 | 561 | 559
2018-10-30 20:30 | 541 | 539
2018-10-30 21:00 | 516 | 516
2018-10-30 21:30 | 498 | 498
2018-10-30 22:00 | 487 | 486
2018-10-30 22:30 | 469 | 468
2018-10-30 23:00 | 449 | 446
2018-10-30 23:30 | 430 | 427
2018-10-31 | 404 | 398
2018-10-31 00:30 | 365 | 357
2018-10-31 01:00 | 346 | 337
2018-10-31 01:30 | 336 | 326
2018-10-31 02:00 | 331 | 318
2018-10-31 02:30 | 338 | 325
2018-10-31 03:00 | 337 | 324
2018-10-31 03:30 | 336 | 324
2018-10-31 04:00 | 344 | 331
2018-10-31 04:30 | 349 | 336
2018-10-31 05:00 | 352 | 340
2018-10-31 05:30 | 380 | 370
2018-10-31 06:00 | 410 | 402
2018-10-31 06:30 | 444 | 440
2018-10-31 07:00 | 458 | 456
2018-10-31 07:30 | 457 | 456
2018-10-31 08:00 | 471 | 470
2018-10-31 08:30 | 470 | 470
2018-10-31 09:00 | 472 | 472
2018-10-31 09:30 | 480 | 480
2018-10-31 10:00 | 482 | 482
2018-10-31 10:30 | 477 | 477
2018-10-31 11:00 | 479 | 479
2018-10-31 11:30 | 478 | 478
2018-10-31 12:00 | 485 | 485
2018-10-31 12:30 | 484 | 484
2018-10-31 13:00 | 483 | 483
2018-10-31 13:30 | 497 | 497
2018-10-31 14:00 | 508 | 508
2018-10-31 14:30 | 520 | 520
2018-10-31 15:00 | 530 | 529
2018-10-31 15:30 | 553 | 552
2018-10-31 16:00 | 566 | 565
2018-10-31 16:30 | 576 | 575
2018-10-31 17:00 | 592 | 591
2018-10-31 17:30 | 587 | 585
2018-10-31 18:00 | 573 | 570
2018-10-31 18:30 | 562 | 561
2018-10-31 19:00 | 568 | 568
2018-10-31 19:30 | 564 | 563
2018-10-31 20:00 | 551 | 550
2018-10-31 20:30 | 538 | 538
2018-10-31 21:00 | 501 | 500
2018-10-31 21:30 | 477 | 476
2018-10-31 22:00 | 460 | 458
2018-10-31 22:30 | 437 | 434
2018-10-31 23:00 | 416 | 414
2018-10-31 23:30 | 401 | 398
2018-11-01 | 370 | 364
2018-11-01 00:30 | 343 | 335
2018-11-01 01:00 | 330 | 320
2018-11-01 01:30 | 328 | 315
2018-11-01 02:00 | 325 | 311
2018-11-01 02:30 | 320 | 307
2018-11-01 03:00 | 322 | 308
2018-11-01 03:30 | 317 | 302
2018-11-01 04:00 | 320 | 305
2018-11-01 04:30 | 336 | 323
2018-11-01 05:00 | 343 | 330
2018-11-01 05:30 | 361 | 349
2018-11-01 06:00 | 397 | 388
2018-11-01 06:30 | 428 | 423
2018-11-01 07:00 | 461 | 458
2018-11-01 07:30 | 473 | 470
2018-11-01 08:00 | 473 | 471
2018-11-01 08:30 | 482 | 481
2018-11-01 09:00 | 480 | 480
2018-11-01 09:30 | 463 | 463
2018-11-01 10:00 | 466 | 466
2018-11-01 10:30 | 448 | 447
2018-11-01 11:00 | 445 | 444
2018-11-01 11:30 | 459 | 459
2018-11-01 12:00 | 468 | 468
2018-11-01 12:30 | 470 | 469
2018-11-01 13:00 | 488 | 488
2018-11-01 13:30 | 504 | 503
2018-11-01 14:00 | 515 | 514
2018-11-01 14:30 | 528 | 523
2018-11-01 15:00 | 537 | 532
2018-11-01 15:30 | 562 | 557
2018-11-01 16:00 | 577 | 573
2018-11-01 16:30 | 596 | 591
2018-11-01 17:00 | 613 | 608
2018-11-01 17:30 | 619 | 613
2018-11-01 18:00 | 618 | 611
2018-11-01 18:30 | 611 | 604
2018-11-01 19:00 | 624 | 618
2018-11-01 19:30 | 623 | 616
2018-11-01 20:00 | 606 | 605
2018-11-01 20:30 | 581 | 579
2018-11-01 21:00 | 544 | 543
2018-11-01 21:30 | 506 | 505
2018-11-01 22:00 | 486 | 484
2018-11-01 22:30 | 462 | 459
2018-11-01 23:00 | 430 | 427
2018-11-01 23:30 | 411 | 408
2018-11-02 | 383 | 378
2018-11-02 00:30 | 365 | 359
2018-11-02 01:00 | 356 | 349
2018-11-02 01:30 | 348 | 340
2018-11-02 02:00 | 336 | 326
2018-11-02 02:30 | 321 | 309
2018-11-02 03:00 | 322 | 309
2018-11-02 03:30 | 323 | 310
2018-11-02 04:00 | 322 | 309
2018-11-02 04:30 | 330 | 318
2018-11-02 05:00 | 349 | 339
2018-11-02 05:30 | 372 | 363
2018-11-02 06:00 | 405 | 397
2018-11-02 06:30 | 440 | 436
2018-11-02 07:00 | 477 | 475
2018-11-02 07:30 | 508 | 506
2018-11-02 08:00 | 519 | 518
2018-11-02 08:30 | 520 | 519
2018-11-02 09:00 | 498 | 496
2018-11-02 09:30 | 492 | 491
2018-11-02 10:00 | 497 | 495
2018-11-02 10:30 | 492 | 491
2018-11-02 11:00 | 485 | 483
2018-11-02 11:30 | 474 | 473
2018-11-02 12:00 | 481 | 480
2018-11-02 12:30 | 488 | 488
2018-11-02 13:00 | 484 | 484
2018-11-02 13:30 | 520 | 514
2018-11-02 14:00 | 527 | 520
2018-11-02 14:30 | 537 | 531
2018-11-02 15:00 | 560 | 554
2018-11-02 15:30 | 574 | 568
2018-11-02 16:00 | 589 | 584
2018-11-02 16:30 | 606 | 600
2018-11-02 17:00 | 612 | 604
2018-11-02 17:30 | 599 | 589
2018-11-02 18:00 | 575 | 566
2018-11-02 18:30 | 553 | 545
2018-11-02 19:00 | 566 | 560
2018-11-02 19:30 | 555 | 547
2018-11-02 20:00 | 528 | 527
2018-11-02 20:30 | 513 | 511
2018-11-02 21:00 | 486 | 484
2018-11-02 21:30 | 465 | 463
2018-11-02 22:00 | 439 | 437
2018-11-02 22:30 | 421 | 420
2018-11-02 23:00 | 403 | 401
2018-11-02 23:30 | 389 | 386
2018-11-03 | 370 | 365
2018-11-03 00:30 | 333 | 327
2018-11-03 01:00 | 311 | 304
2018-11-03 01:30 | 294 | 286
2018-11-03 02:00 | 285 | 277
2018-11-03 02:30 | 280 | 271
2018-11-03 03:00 | 279 | 269
2018-11-03 03:30 | 281 | 271
2018-11-03 04:00 | 279 | 269
2018-11-03 04:30 | 282 | 272
2018-11-03 05:00 | 283 | 272
2018-11-03 05:30 | 285 | 274
2018-11-03 06:00 | 287 | 276
2018-11-03 06:30 | 299 | 290
2018-11-03 07:00 | 311 | 303
2018-11-03 07:30 | 326 | 319
2018-11-03 08:00 | 332 | 328
2018-11-03 08:30 | 341 | 338
2018-11-03 09:00 | 342 | 339
2018-11-03 09:30 | 344 | 342
2018-11-03 10:00 | 336 | 335
2018-11-03 10:30 | 329 | 328
2018-11-03 11:00 | 319 | 318
2018-11-03 11:30 | 317 | 317
2018-11-03 12:00 | 325 | 325
2018-11-03 12:30 | 333 | 332
2018-11-03 13:00 | 341 | 341
2018-11-03 13:30 | 349 | 349
2018-11-03 14:00 | 365 | 365
2018-11-03 14:30 | 383 | 383
2018-11-03 15:00 | 399 | 399
2018-11-03 15:30 | 419 | 419
2018-11-03 16:00 | 440 | 439
2018-11-03 16:30 | 457 | 456
2018-11-03 17:00 | 466 | 465
2018-11-03 17:30 | 458 | 457
2018-11-03 18:00 | 448 | 446
2018-11-03 18:30 | 457 | 456
2018-11-03 19:00 | 470 | 468
2018-11-03 19:30 | 462 | 459
2018-11-03 20:00 | 453 | 450
2018-11-03 20:30 | 448 | 446
2018-11-03 21:00 | 426 | 424
2018-11-03 21:30 | 415 | 413
2018-11-03 22:00 | 405 | 403
2018-11-03 22:30 | 393 | 392
2018-11-03 23:00 | 376 | 375
2018-11-03 23:30 | 358 | 356
2018-11-04 | 336 | 333
2018-11-04 00:30 | 317 | 311
2018-11-04 01:00 | 305 | 298
2018-11-04 01:30 | 303 | 295
2018-11-04 02:00 | 304 | 295
2018-11-04 02:30 | 304 | 294
2018-11-04 03:00 | 293 | 282
2018-11-04 03:30 | 292 | 279
2018-11-04 04:00 | 298 | 285
2018-11-04 04:30 | 289 | 276
2018-11-04 05:00 | 289 | 275
2018-11-04 05:30 | 289 | 270
2018-11-04 06:00 | 288 | 267
2018-11-04 06:30 | 300 | 282
2018-11-04 07:00 | 305 | 288
2018-11-04 07:30 | 321 | 306
2018-11-04 08:00 | 331 | 319
2018-11-04 08:30 | 339 | 330
2018-11-04 09:00 | 340 | 333
2018-11-04 09:30 | 346 | 341
2018-11-04 10:00 | 349 | 345
2018-11-04 10:30 | 363 | 360
2018-11-04 11:00 | 385 | 375
2018-11-04 11:30 | 384 | 376
2018-11-04 12:00 | 393 | 386
2018-11-04 12:30 | 394 | 390
2018-11-04 13:00 | 407 | 404
2018-11-04 13:30 | 422 | 418
2018-11-04 14:00 | 445 | 436
2018-11-04 14:30 | 454 | 448
2018-11-04 15:00 | 469 | 464
2018-11-04 15:30 | 489 | 481
2018-11-04 16:00 | 508 | 501
2018-11-04 16:30 | 526 | 518
2018-11-04 17:00 | 524 | 515
2018-11-04 17:30 | 520 | 511
2018-11-04 18:00 | 516 | 507
2018-11-04 18:30 | 512 | 505
2018-11-04 19:00 | 514 | 509
2018-11-04 19:30 | 504 | 499
2018-11-04 20:00 | 490 | 485
2018-11-04 20:30 | 476 | 472
2018-11-04 21:00 | 462 | 458
2018-11-04 21:30 | 437 | 436
2018-11-04 22:00 | 421 | 420
2018-11-04 22:30 | 402 | 401
2018-11-04 23:00 | 390 | 389
2018-11-04 23:30 | 371 | 369
2018-11-05 | 354 | 351
2018-11-05 00:30 | 326 | 321
2018-11-05 01:00 | 316 | 310
2018-11-05 01:30 | 318 | 311
2018-11-05 02:00 | 315 | 307
2018-11-05 02:30 | 313 | 305
2018-11-05 03:00 | 319 | 310
2018-11-05 03:30 | 318 | 310
2018-11-05 04:00 | 320 | 311
2018-11-05 04:30 | 322 | 315
2018-11-05 05:00 | 320 | 313
2018-11-05 05:30 | 331 | 326
2018-11-05 06:00 | 361 | 358
2018-11-05 06:30 | 405 | 404
2018-11-05 07:00 | 463 | 459
2018-11-05 07:30 | 496 | 492
2018-11-05 08:00 | 507 | 502
2018-11-05 08:30 | 508 | 504
2018-11-05 09:00 | 499 | 496
2018-11-05 09:30 | 510 | 503
2018-11-05 10:00 | 515 | 508
2018-11-05 10:30 | 520 | 514
2018-11-05 11:00 | 521 | 516
2018-11-05 11:30 | 527 | 522
2018-11-05 12:00 | 539 | 533
2018-11-05 12:30 | 545 | 540
2018-11-05 13:00 | 556 | 551
2018-11-05 13:30 | 572 | 567
2018-11-05 14:00 | 589 | 585
2018-11-05 14:30 | 601 | 596
2018-11-05 15:00 | 612 | 606
2018-11-05 15:30 | 614 | 608
2018-11-05 16:00 | 633 | 629
2018-11-05 16:30 | 656 | 651
2018-11-05 17:00 | 671 | 666
2018-11-05 17:30 | 660 | 654
2018-11-05 18:00 | 638 | 632
2018-11-05 18:30 | 621 | 615
2018-11-05 19:00 | 624 | 619
2018-11-05 19:30 | 611 | 606
2018-11-05 20:00 | 592 | 591
2018-11-05 20:30 | 580 | 577
2018-11-05 21:00 | 546 | 543
2018-11-05 21:30 | 518 | 514
2018-11-05 22:00 | 492 | 490
2018-11-05 22:30 | 465 | 463
2018-11-05 23:00 | 443 | 441
2018-11-05 23:30 | 411 | 409
2018-11-06 | 386 | 383
2018-11-06 00:30 | 355 | 352
2018-11-06 01:00 | 347 | 342
2018-11-06 01:30 | 339 | 333
2018-11-06 02:00 | 332 | 326
2018-11-06 02:30 | 332 | 325
2018-11-06 03:00 | 331 | 324
2018-11-06 03:30 | 330 | 323
2018-11-06 04:00 | 330 | 323
2018-11-06 04:30 | 337 | 331
2018-11-06 05:00 | 343 | 337
2018-11-06 05:30 | 365 | 360
2018-11-06 06:00 | 386 | 383
2018-11-06 06:30 | 435 | 434
2018-11-06 07:00 | 482 | 481
2018-11-06 07:30 | 523 | 523
2018-11-06 08:00 | 540 | 539
2018-11-06 08:30 | 547 | 547
2018-11-06 09:00 | 544 | 543
2018-11-06 09:30 | 548 | 548
2018-11-06 10:00 | 541 | 541
2018-11-06 10:30 | 551 | 551
2018-11-06 11:00 | 567 | 567
2018-11-06 11:30 | 571 | 567
2018-11-06 12:00 | 576 | 573
2018-11-06 12:30 | 596 | 593
2018-11-06 13:00 | 597 | 594
2018-11-06 13:30 | 603 | 600
2018-11-06 14:00 | 626 | 624
2018-11-06 14:30 | 640 | 637
2018-11-06 15:00 | 655 | 652
2018-11-06 15:30 | 683 | 676
2018-11-06 16:00 | 697 | 690
2018-11-06 16:30 | 694 | 686
2018-11-06 17:00 | 688 | 677
2018-11-06 17:30 | 675 | 664
2018-11-06 18:00 | 651 | 642
2018-11-06 18:30 | 615 | 607
2018-11-06 19:00 | 604 | 595
2018-11-06 19:30 | 593 | 583
2018-11-06 20:00 | 576 | 573
2018-11-06 20:30 | 582 | 580
2018-11-06 21:00 | 566 | 564
2018-11-06 21:30 | 539 | 535
2018-11-06 22:00 | 527 | 524
2018-11-06 22:30 | 483 | 482
2018-11-06 23:00 | 449 | 448
2018-11-06 23:30 | 436 | 435
2018-11-07 | 418 | 418
2018-11-07 00:30 | 394 | 394
2018-11-07 01:00 | 382 | 382
2018-11-07 01:30 | 359 | 359
2018-11-07 02:00 | 341 | 341
2018-11-07 02:30 | 328 | 327
2018-11-07 03:00 | 328 | 327
2018-11-07 03:30 | 325 | 324
2018-11-07 04:00 | 320 | 319
2018-11-07 04:30 | 323 | 322
2018-11-07 05:00 | 329 | 328
2018-11-07 05:30 | 352 | 352
2018-11-07 06:00 | 381 | 381
2018-11-07 06:30 | 438 | 438
2018-11-07 07:00 | 489 | 488
2018-11-07 07:30 | 514 | 512
2018-11-07 08:00 | 528 | 523
2018-11-07 08:30 | 527 | 522
2018-11-07 09:00 | 533 | 529
2018-11-07 09:30 | 525 | 522
2018-11-07 10:00 | 532 | 529
2018-11-07 10:30 | 539 | 534
2018-11-07 11:00 | 537 | 532
2018-11-07 11:30 | 545 | 539
2018-11-07 12:00 | 548 | 544
2018-11-07 12:30 | 557 | 554
2018-11-07 13:00 | 582 | 577
2018-11-07 13:30 | 579 | 572
2018-11-07 14:00 | 604 | 599
2018-11-07 14:30 | 616 | 610
2018-11-07 15:00 | 606 | 600
2018-11-07 15:30 | 629 | 623
2018-11-07 16:00 | 651 | 645
2018-11-07 16:30 | 655 | 650
2018-11-07 17:00 | 659 | 653
2018-11-07 17:30 | 653 | 645
2018-11-07 18:00 | 633 | 623
2018-11-07 18:30 | 614 | 601
2018-11-07 19:00 | 613 | 601
2018-11-07 19:30 | 587 | 572
2018-11-07 20:00 | 569 | 558
2018-11-07 20:30 | 552 | 543
2018-11-07 21:00 | 521 | 515
2018-11-07 21:30 | 491 | 489
2018-11-07 22:00 | 474 | 469
2018-11-07 22:30 | 445 | 440
2018-11-07 23:00 | 420 | 415
2018-11-07 23:30 | 390 | 386
2018-11-08 | 359 | 353
2018-11-08 00:30 | 333 | 327
2018-11-08 01:00 | 316 | 311
2018-11-08 01:30 | 307 | 302
2018-11-08 02:00 | 304 | 299
2018-11-08 02:30 | 298 | 292
2018-11-08 03:00 | 295 | 289
2018-11-08 03:30 | 299 | 293
2018-11-08 04:00 | 301 | 295
2018-11-08 04:30 | 312 | 306
2018-11-08 05:00 | 312 | 308
2018-11-08 05:30 | 335 | 330
2018-11-08 06:00 | 364 | 361
2018-11-08 06:30 | 416 | 410
2018-11-08 07:00 | 461 | 454
2018-11-08 07:30 | 487 | 479
2018-11-08 08:00 | 495 | 489
2018-11-08 08:30 | 499 | 494
2018-11-08 09:00 | 486 | 481
2018-11-08 09:30 | 495 | 490
2018-11-08 10:00 | 488 | 483
2018-11-08 10:30 | 480 | 474
2018-11-08 11:00 | 471 | 464
2018-11-08 11:30 | 462 | 456
2018-11-08 12:00 | 428 | 426
2018-11-08 12:30 | 422 | 420
2018-11-08 13:00 | 424 | 421
2018-11-08 13:30 | 432 | 430
2018-11-08 14:00 | 425 | 423
2018-11-08 14:30 | 406 | 404
2018-11-08 15:00 | 385 | 383
2018-11-08 15:30 | 421 | 420
2018-11-08 16:00 | 462 | 461
2018-11-08 16:30 | 483 | 482
2018-11-08 17:00 | 494 | 493
2018-11-08 17:30 | 503 | 501
2018-11-08 18:00 | 510 | 508
2018-11-08 18:30 | 517 | 514
2018-11-08 19:00 | 534 | 533
2018-11-08 19:30 | 527 | 524
2018-11-08 20:00 | 516 | 513
2018-11-08 20:30 | 495 | 493
2018-11-08 21:00 | 472 | 472
2018-11-08 21:30 | 463 | 462
2018-11-08 22:00 | 452 | 451
2018-11-08 22:30 | 435 | 433
2018-11-08 23:00 | 422 | 420
2018-11-08 23:30 | 401 | 397
2018-11-09 | 369 | 364
2018-11-09 00:30 | 339 | 333
2018-11-09 01:00 | 323 | 316
2018-11-09 01:30 | 318 | 309
2018-11-09 02:00 | 314 | 305
2018-11-09 02:30 | 323 | 313
2018-11-09 03:00 | 321 | 311
2018-11-09 03:30 | 320 | 310
2018-11-09 04:00 | 327 | 318
2018-11-09 04:30 | 325 | 316
2018-11-09 05:00 | 335 | 326
2018-11-09 05:30 | 367 | 359
2018-11-09 06:00 | 388 | 383
2018-11-09 06:30 | 410 | 407
2018-11-09 07:00 | 433 | 432
2018-11-09 07:30 | 449 | 448
2018-11-09 08:00 | 436 | 435
2018-11-09 08:30 | 432 | 431
2018-11-09 09:00 | 432 | 431
2018-11-09 09:30 | 438 | 437
2018-11-09 10:00 | 445 | 444
2018-11-09 10:30 | 449 | 448
2018-11-09 11:00 | 461 | 461
2018-11-09 11:30 | 437 | 437
2018-11-09 12:00 | 427 | 427
2018-11-09 12:30 | 426 | 426
2018-11-09 13:00 | 416 | 416
2018-11-09 13:30 | 416 | 416
2018-11-09 14:00 | 428 | 427
2018-11-09 14:30 | 421 | 421
2018-11-09 15:00 | 426 | 426
2018-11-09 15:30 | 443 | 443
2018-11-09 16:00 | 464 | 464
2018-11-09 16:30 | 480 | 480
2018-11-09 17:00 | 485 | 485
2018-11-09 17:30 | 491 | 491
2018-11-09 18:00 | 487 | 486
2018-11-09 18:30 | 482 | 481
2018-11-09 19:00 | 498 | 497
2018-11-09 19:30 | 494 | 492
2018-11-09 20:00 | 487 | 486
2018-11-09 20:30 | 470 | 470
2018-11-09 21:00 | 444 | 444
2018-11-09 21:30 | 422 | 421
2018-11-09 22:00 | 411 | 409
2018-11-09 22:30 | 400 | 398
2018-11-09 23:00 | 392 | 389
2018-11-09 23:30 | 379 | 375
2018-11-10 | 350 | 345
2018-11-10 00:30 | 320 | 313
2018-11-10 01:00 | 302 | 293
2018-11-10 01:30 | 295 | 285
2018-11-10 02:00 | 293 | 283
2018-11-10 02:30 | 289 | 278
2018-11-10 03:00 | 288 | 277
2018-11-10 03:30 | 292 | 282
2018-11-10 04:00 | 297 | 287
2018-11-10 04:30 | 298 | 287
2018-11-10 05:00 | 299 | 287
2018-11-10 05:30 | 305 | 294
2018-11-10 06:00 | 303 | 292
2018-11-10 06:30 | 316 | 306
2018-11-10 07:00 | 323 | 313
2018-11-10 07:30 | 330 | 322
2018-11-10 08:00 | 332 | 325
2018-11-10 08:30 | 339 | 333
2018-11-10 09:00 | 349 | 345
2018-11-10 09:30 | 350 | 347
2018-11-10 10:00 | 347 | 345
2018-11-10 10:30 | 339 | 336
2018-11-10 11:00 | 325 | 323
2018-11-10 11:30 | 329 | 326
2018-11-10 12:00 | 319 | 317
2018-11-10 12:30 | 319 | 316
2018-11-10 13:00 | 336 | 333
2018-11-10 13:30 | 347 | 345
2018-11-10 14:00 | 352 | 350
2018-11-10 14:30 | 352 | 350
2018-11-10 15:00 | 356 | 354
2018-11-10 15:30 | 357 | 355
2018-11-10 16:00 | 375 | 373
2018-11-10 16:30 | 395 | 393
2018-11-10 17:00 | 422 | 421
2018-11-10 17:30 | 427 | 425
2018-11-10 18:00 | 433 | 431
2018-11-10 18:30 | 449 | 448
2018-11-10 19:00 | 462 | 461
2018-11-10 19:30 | 455 | 454
2018-11-10 20:00 | 442 | 441
2018-11-10 20:30 | 440 | 439
2018-11-10 21:00 | 417 | 415
2018-11-10 21:30 | 396 | 393
2018-11-10 22:00 | 387 | 384
2018-11-10 22:30 | 377 | 373
2018-11-10 23:00 | 372 | 367
2018-11-10 23:30 | 357 | 351
2018-11-11 | 326 | 318
2018-11-11 00:30 | 303 | 293
2018-11-11 01:00 | 288 | 276
2018-11-11 01:30 | 274 | 261
2018-11-11 02:00 | 266 | 252
2018-11-11 02:30 | 263 | 249
2018-11-11 03:00 | 259 | 244
2018-11-11 03:30 | 271 | 256
2018-11-11 04:00 | 272 | 258
2018-11-11 04:30 | 284 | 270
2018-11-11 05:00 | 281 | 262
2018-11-11 05:30 | 275 | 255
2018-11-11 06:00 | 281 | 261
2018-11-11 06:30 | 291 | 272
2018-11-11 07:00 | 301 | 284
2018-11-11 07:30 | 318 | 302
2018-11-11 08:00 | 327 | 313
2018-11-11 08:30 | 330 | 319
2018-11-11 09:00 | 335 | 326
2018-11-11 09:30 | 336 | 327
2018-11-11 10:00 | 334 | 327
2018-11-11 10:30 | 333 | 327
2018-11-11 11:00 | 319 | 313
2018-11-11 11:30 | 310 | 304
2018-11-11 12:00 | 303 | 297
2018-11-11 12:30 | 308 | 301
2018-11-11 13:00 | 315 | 309
2018-11-11 13:30 | 320 | 314
2018-11-11 14:00 | 327 | 322
2018-11-11 14:30 | 344 | 339
2018-11-11 15:00 | 363 | 359
2018-11-11 15:30 | 374 | 370
2018-11-11 16:00 | 398 | 394
2018-11-11 16:30 | 426 | 423
2018-11-11 17:00 | 443 | 441
2018-11-11 17:30 | 454 | 451
2018-11-11 18:00 | 455 | 453
2018-11-11 18:30 | 458 | 455
2018-11-11 19:00 | 475 | 473
2018-11-11 19:30 | 467 | 463
2018-11-11 20:00 | 456 | 452
2018-11-11 20:30 | 440 | 436
2018-11-11 21:00 | 418 | 414
2018-11-11 21:30 | 400 | 396
2018-11-11 22:00 | 388 | 383
2018-11-11 22:30 | 376 | 370
2018-11-11 23:00 | 371 | 364
2018-11-11 23:30 | 353 | 344
2018-11-12 | 339 | 328
2018-11-12 00:30 | 319 | 307
2018-11-12 01:00 | 313 | 298
2018-11-12 01:30 | 308 | 293
2018-11-12 02:00 | 302 | 286
2018-11-12 02:30 | 302 | 286
2018-11-12 03:00 | 302 | 285
2018-11-12 03:30 | 305 | 289
2018-11-12 04:00 | 309 | 293
2018-11-12 04:30 | 307 | 291
2018-11-12 05:00 | 308 | 293
2018-11-12 05:30 | 322 | 308
2018-11-12 06:00 | 350 | 340
2018-11-12 06:30 | 386 | 380
2018-11-12 07:00 | 418 | 414
2018-11-12 07:30 | 434 | 427
2018-11-12 08:00 | 431 | 426
2018-11-12 08:30 | 438 | 434
2018-11-12 09:00 | 439 | 437
2018-11-12 09:30 | 440 | 439
2018-11-12 10:00 | 435 | 435
2018-11-12 10:30 | 433 | 432
2018-11-12 11:00 | 432 | 431
2018-11-12 11:30 | 418 | 418
2018-11-12 12:00 | 408 | 408
2018-11-12 12:30 | 422 | 422
2018-11-12 13:00 | 433 | 433
2018-11-12 13:30 | 450 | 450
2018-11-12 14:00 | 458 | 458
2018-11-12 14:30 | 462 | 462
2018-11-12 15:00 | 486 | 485
2018-11-12 15:30 | 510 | 508
2018-11-12 16:00 | 523 | 522
2018-11-12 16:30 | 548 | 546
2018-11-12 17:00 | 557 | 555
2018-11-12 17:30 | 559 | 557
2018-11-12 18:00 | 547 | 545
2018-11-12 18:30 | 530 | 526
2018-11-12 19:00 | 537 | 535
2018-11-12 19:30 | 526 | 523
2018-11-12 20:00 | 502 | 498
2018-11-12 20:30 | 493 | 490
2018-11-12 21:00 | 475 | 473
2018-11-12 21:30 | 455 | 454
2018-11-12 22:00 | 441 | 439
2018-11-12 22:30 | 425 | 423
2018-11-12 23:00 | 412 | 410
2018-11-12 23:30 | 376 | 373
2018-11-13 | 357 | 353
2018-11-13 00:30 | 329 | 323
2018-11-13 01:00 | 313 | 306
2018-11-13 01:30 | 304 | 296
2018-11-13 02:00 | 302 | 294
2018-11-13 02:30 | 303 | 294
2018-11-13 03:00 | 303 | 294
2018-11-13 03:30 | 311 | 302
2018-11-13 04:00 | 316 | 307
2018-11-13 04:30 | 331 | 323
2018-11-13 05:00 | 328 | 320
2018-11-13 05:30 | 347 | 340
2018-11-13 06:00 | 367 | 362
2018-11-13 06:30 | 402 | 400
2018-11-13 07:00 | 439 | 438
2018-11-13 07:30 | 454 | 454
2018-11-13 08:00 | 454 | 454
2018-11-13 08:30 | 463 | 463
2018-11-13 09:00 | 474 | 474
2018-11-13 09:30 | 475 | 475
2018-11-13 10:00 | 467 | 467
2018-11-13 10:30 | 463 | 463
2018-11-13 11:00 | 463 | 463
2018-11-13 11:30 | 459 | 459
2018-11-13 12:00 | 456 | 456
2018-11-13 12:30 | 457 | 457
2018-11-13 13:00 | 461 | 461
2018-11-13 13:30 | 457 | 457
2018-11-13 14:00 | 454 | 454
2018-11-13 14:30 | 461 | 461
2018-11-13 15:00 | 468 | 468
2018-11-13 15:30 | 493 | 493
2018-11-13 16:00 | 527 | 527
2018-11-13 16:30 | 539 | 539
2018-11-13 17:00 | 543 | 543
2018-11-13 17:30 | 536 | 536
2018-11-13 18:00 | 523 | 522
2018-11-13 18:30 | 520 | 519
2018-11-13 19:00 | 529 | 529
2018-11-13 19:30 | 524 | 523
2018-11-13 20:00 | 520 | 520
2018-11-13 20:30 | 499 | 498
2018-11-13 21:00 | 479 | 478
2018-11-13 21:30 | 457 | 456
2018-11-13 22:00 | 442 | 440
2018-11-13 22:30 | 420 | 419
2018-11-13 23:00 | 400 | 398
2018-11-13 23:30 | 381 | 378
2018-11-14 | 358 | 354
2018-11-14 00:30 | 338 | 333
2018-11-14 01:00 | 313 | 306
2018-11-14 01:30 | 303 | 295
2018-11-14 02:00 | 306 | 298
2018-11-14 02:30 | 317 | 308
2018-11-14 03:00 | 326 | 317
2018-11-14 03:30 | 323 | 314
2018-11-14 04:00 | 329 | 320
2018-11-14 04:30 | 341 | 331
2018-11-14 05:00 | 347 | 338
2018-11-14 05:30 | 368 | 359
2018-11-14 06:00 | 387 | 381
2018-11-14 06:30 | 424 | 420
2018-11-14 07:00 | 458 | 453
2018-11-14 07:30 | 488 | 482
2018-11-14 08:00 | 494 | 490
2018-11-14 08:30 | 490 | 488
2018-11-14 09:00 | 494 | 493
2018-11-14 09:30 | 489 | 487
2018-11-14 10:00 | 476 | 472
2018-11-14 10:30 | 471 | 467
2018-11-14 11:00 | 462 | 459
2018-11-14 11:30 | 458 | 455
2018-11-14 12:00 | 475 | 473
2018-11-14 12:30 | 478 | 474
2018-11-14 13:00 | 484 | 481
2018-11-14 13:30 | 501 | 498
2018-11-14 14:00 | 494 | 490
2018-11-14 14:30 | 503 | 499
2018-11-14 15:00 | 496 | 491
2018-11-14 15:30 | 513 | 509
2018-11-14 16:00 | 513 | 509
2018-11-14 16:30 | 534 | 531
2018-11-14 17:00 | 543 | 538
2018-11-14 17:30 | 554 | 545
2018-11-14 18:00 | 544 | 533
2018-11-14 18:30 | 545 | 533
2018-11-14 19:00 | 551 | 541
2018-11-14 19:30 | 543 | 532
2018-11-14 20:00 | 540 | 533
2018-11-14 20:30 | 534 | 527
2018-11-14 21:00 | 510 | 504
2018-11-14 21:30 | 476 | 471
2018-11-14 22:00 | 464 | 459
2018-11-14 22:30 | 441 | 440
2018-11-14 23:00 | 428 | 427
2018-11-14 23:30 | 409 | 407
2018-11-15 | 388 | 384
2018-11-15 00:30 | 353 | 349
2018-11-15 01:00 | 329 | 323
2018-11-15 01:30 | 309 | 302
2018-11-15 02:00 | 298 | 291
2018-11-15 02:30 | 297 | 289
2018-11-15 03:00 | 294 | 286
2018-11-15 03:30 | 295 | 287
2018-11-15 04:00 | 294 | 287
2018-11-15 04:30 | 311 | 304
2018-11-15 05:00 | 319 | 311
2018-11-15 05:30 | 342 | 337
2018-11-15 06:00 | 371 | 367
2018-11-15 06:30 | 411 | 410
2018-11-15 07:00 | 452 | 451
2018-11-15 07:30 | 482 | 481
2018-11-15 08:00 | 500 | 500
2018-11-15 08:30 | 502 | 502
2018-11-15 09:00 | 497 | 497
2018-11-15 09:30 | 505 | 505
2018-11-15 10:00 | 508 | 508
2018-11-15 10:30 | 516 | 516
2018-11-15 11:00 | 517 | 517
2018-11-15 11:30 | 520 | 520
2018-11-15 12:00 | 516 | 515
2018-11-15 12:30 | 521 | 521
2018-11-15 13:00 | 506 | 506
2018-11-15 13:30 | 511 | 511
2018-11-15 14:00 | 515 | 515
2018-11-15 14:30 | 525 | 525
2018-11-15 15:00 | 537 | 536
2018-11-15 15:30 | 539 | 539
2018-11-15 16:00 | 540 | 539
2018-11-15 16:30 | 547 | 546
2018-11-15 17:00 | 562 | 561
2018-11-15 17:30 | 554 | 554
2018-11-15 18:00 | 545 | 545
2018-11-15 18:30 | 535 | 535
2018-11-15 19:00 | 538 | 538
2018-11-15 19:30 | 531 | 531
2018-11-15 20:00 | 528 | 527
2018-11-15 20:30 | 518 | 517
2018-11-15 21:00 | 477 | 477
2018-11-15 21:30 | 458 | 458
2018-11-15 22:00 | 443 | 442
2018-11-15 22:30 | 429 | 429
2018-11-15 23:00 | 420 | 419
2018-11-15 23:30 | 408 | 408
2018-11-16 | 386 | 385
2018-11-16 00:30 | 353 | 351
2018-11-16 01:00 | 330 | 327
2018-11-16 01:30 | 321 | 317
2018-11-16 02:00 | 312 | 307
2018-11-16 02:30 | 313 | 308
2018-11-16 03:00 | 313 | 307
2018-11-16 03:30 | 312 | 307
2018-11-16 04:00 | 316 | 311
2018-11-16 04:30 | 324 | 319
2018-11-16 05:00 | 332 | 327
2018-11-16 05:30 | 358 | 354
2018-11-16 06:00 | 386 | 384
2018-11-16 06:30 | 425 | 424
2018-11-16 07:00 | 460 | 459
2018-11-16 07:30 | 494 | 494
2018-11-16 08:00 | 511 | 511
2018-11-16 08:30 | 515 | 515
2018-11-16 09:00 | 508 | 507
2018-11-16 09:30 | 507 | 507
2018-11-16 10:00 | 512 | 511
2018-11-16 10:30 | 513 | 512
2018-11-16 11:00 | 517 | 517
2018-11-16 11:30 | 524 | 523
2018-11-16 12:00 | 525 | 525
2018-11-16 12:30 | 523 | 523
2018-11-16 13:00 | 511 | 511
2018-11-16 13:30 | 511 | 511
2018-11-16 14:00 | 516 | 515
2018-11-16 14:30 | 517 | 517
2018-11-16 15:00 | 527 | 527
2018-11-16 15:30 | 548 | 547
2018-11-16 16:00 | 564 | 563
2018-11-16 16:30 | 571 | 570
2018-11-16 17:00 | 587 | 587
2018-11-16 17:30 | 575 | 574
2018-11-16 18:00 | 546 | 545
2018-11-16 18:30 | 519 | 518
2018-11-16 19:00 | 527 | 526
2018-11-16 19:30 | 522 | 522
2018-11-16 20:00 | 515 | 515
2018-11-16 20:30 | 499 | 497
2018-11-16 21:00 | 478 | 476
2018-11-16 21:30 | 462 | 461
2018-11-16 22:00 | 450 | 449
2018-11-16 22:30 | 446 | 445
2018-11-16 23:00 | 435 | 434
2018-11-16 23:30 | 413 | 412
2018-11-17 | 399 | 398
2018-11-17 00:30 | 370 | 368
2018-11-17 01:00 | 347 | 344
2018-11-17 01:30 | 340 | 337
2018-11-17 02:00 | 337 | 334
2018-11-17 02:30 | 338 | 334
2018-11-17 03:00 | 336 | 332
2018-11-17 03:30 | 332 | 328
2018-11-17 04:00 | 329 | 324
2018-11-17 04:30 | 316 | 311
2018-11-17 05:00 | 305 | 299
2018-11-17 05:30 | 295 | 289
2018-11-17 06:00 | 299 | 293
2018-11-17 06:30 | 321 | 317
2018-11-17 07:00 | 350 | 347
2018-11-17 07:30 | 381 | 379
2018-11-17 08:00 | 402 | 400
2018-11-17 08:30 | 414 | 413
2018-11-17 09:00 | 427 | 426
2018-11-17 09:30 | 438 | 437
2018-11-17 10:00 | 421 | 420
2018-11-17 10:30 | 424 | 423
2018-11-17 11:00 | 422 | 421
2018-11-17 11:30 | 405 | 404
2018-11-17 12:00 | 400 | 399
2018-11-17 12:30 | 414 | 413
2018-11-17 13:00 | 426 | 425
2018-11-17 13:30 | 428 | 427
2018-11-17 14:00 | 436 | 435
2018-11-17 14:30 | 444 | 443
2018-11-17 15:00 | 500 | 499
2018-11-17 15:30 | 518 | 518
2018-11-17 16:00 | 505 | 504
2018-11-17 16:30 | 489 | 488
2018-11-17 17:00 | 483 | 482
2018-11-17 17:30 | 463 | 462
2018-11-17 18:00 | 455 | 453
2018-11-17 18:30 | 453 | 452
2018-11-17 19:00 | 457 | 456
2018-11-17 19:30 | 447 | 444
2018-11-17 20:00 | 438 | 434
2018-11-17 20:30 | 423 | 421
2018-11-17 21:00 | 409 | 408
2018-11-17 21:30 | 400 | 399
2018-11-17 22:00 | 400 | 399
2018-11-17 22:30 | 391 | 390
2018-11-17 23:00 | 382 | 380
2018-11-17 23:30 | 372 | 369
2018-11-18 | 359 | 354
2018-11-18 00:30 | 334 | 327
2018-11-18 01:00 | 315 | 309
2018-11-18 01:30 | 298 | 292
2018-11-18 02:00 | 291 | 284
2018-11-18 02:30 | 291 | 285
2018-11-18 03:00 | 294 | 288
2018-11-18 03:30 | 288 | 282
2018-11-18 04:00 | 285 | 278
2018-11-18 04:30 | 286 | 279
2018-11-18 05:00 | 282 | 274
2018-11-18 05:30 | 282 | 274
2018-11-18 06:00 | 286 | 279
2018-11-18 06:30 | 299 | 293
2018-11-18 07:00 | 316 | 310
2018-11-18 07:30 | 328 | 323
2018-11-18 08:00 | 342 | 338
2018-11-18 08:30 | 349 | 346
2018-11-18 09:00 | 351 | 349
2018-11-18 09:30 | 364 | 362
2018-11-18 10:00 | 376 | 375
2018-11-18 10:30 | 391 | 390
2018-11-18 11:00 | 387 | 386
2018-11-18 11:30 | 382 | 381
2018-11-18 12:00 | 383 | 381
2018-11-18 12:30 | 398 | 396
2018-11-18 13:00 | 410 | 408
2018-11-18 13:30 | 412 | 410
2018-11-18 14:00 | 386 | 385
2018-11-18 14:30 | 385 | 383
2018-11-18 15:00 | 396 | 394
2018-11-18 15:30 | 409 | 408
2018-11-18 16:00 | 408 | 406
2018-11-18 16:30 | 399 | 398
2018-11-18 17:00 | 415 | 414
2018-11-18 17:30 | 427 | 425
2018-11-18 18:00 | 429 | 427
2018-11-18 18:30 | 442 | 441
2018-11-18 19:00 | 451 | 449
2018-11-18 19:30 | 449 | 446
2018-11-18 20:00 | 451 | 447
2018-11-18 20:30 | 448 | 445
2018-11-18 21:00 | 420 | 419
2018-11-18 21:30 | 393 | 392
2018-11-18 22:00 | 388 | 387
2018-11-18 22:30 | 380 | 378
2018-11-18 23:00 | 377 | 374
2018-11-18 23:30 | 362 | 359
2018-11-19 | 343 | 339
2018-11-19 00:30 | 318 | 313
2018-11-19 01:00 | 303 | 298
2018-11-19 01:30 | 285 | 278
2018-11-19 02:00 | 273 | 265
2018-11-19 02:30 | 272 | 263
2018-11-19 03:00 | 273 | 264
2018-11-19 03:30 | 276 | 267
2018-11-19 04:00 | 277 | 268
2018-11-19 04:30 | 294 | 286
2018-11-19 05:00 | 296 | 288
2018-11-19 05:30 | 311 | 304
2018-11-19 06:00 | 346 | 341
2018-11-19 06:30 | 389 | 387
2018-11-19 07:00 | 425 | 424
2018-11-19 07:30 | 442 | 441
2018-11-19 08:00 | 444 | 443
2018-11-19 08:30 | 442 | 441
2018-11-19 09:00 | 454 | 453
2018-11-19 09:30 | 467 | 466
2018-11-19 10:00 | 480 | 480
2018-11-19 10:30 | 464 | 463
2018-11-19 11:00 | 460 | 459
2018-11-19 11:30 | 441 | 441
2018-11-19 12:00 | 455 | 455
2018-11-19 12:30 | 481 | 480
2018-11-19 13:00 | 481 | 480
2018-11-19 13:30 | 480 | 479
2018-11-19 14:00 | 478 | 477
2018-11-19 14:30 | 476 | 475
2018-11-19 15:00 | 474 | 473
2018-11-19 15:30 | 490 | 489
2018-11-19 16:00 | 505 | 504
2018-11-19 16:30 | 517 | 517
2018-11-19 17:00 | 547 | 546
2018-11-19 17:30 | 547 | 547
2018-11-19 18:00 | 519 | 519
2018-11-19 18:30 | 508 | 507
2018-11-19 19:00 | 515 | 515
2018-11-19 19:30 | 505 | 504
2018-11-19 20:00 | 494 | 494
2018-11-19 20:30 | 485 | 485
2018-11-19 21:00 | 463 | 462
2018-11-19 21:30 | 443 | 442
2018-11-19 22:00 | 432 | 431
2018-11-19 22:30 | 424 | 423
2018-11-19 23:00 | 409 | 408
2018-11-19 23:30 | 395 | 394
2018-11-20 | 373 | 371
2018-11-20 00:30 | 342 | 340
2018-11-20 01:00 | 329 | 326
2018-11-20 01:30 | 311 | 308
2018-11-20 02:00 | 293 | 289
2018-11-20 02:30 | 285 | 281
2018-11-20 03:00 | 301 | 297
2018-11-20 03:30 | 308 | 303
2018-11-20 04:00 | 311 | 306
2018-11-20 04:30 | 318 | 314
2018-11-20 05:00 | 325 | 321
2018-11-20 05:30 | 348 | 344
2018-11-20 06:00 | 377 | 374
2018-11-20 06:30 | 405 | 403
2018-11-20 07:00 | 437 | 435
2018-11-20 07:30 | 463 | 459
2018-11-20 08:00 | 472 | 467
2018-11-20 08:30 | 465 | 462
2018-11-20 09:00 | 457 | 454
2018-11-20 09:30 | 464 | 460
2018-11-20 10:00 | 467 | 462
2018-11-20 10:30 | 451 | 446
2018-11-20 11:00 | 441 | 438
2018-11-20 11:30 | 447 | 443
2018-11-20 12:00 | 453 | 450
2018-11-20 12:30 | 470 | 466
2018-11-20 13:00 | 476 | 473
2018-11-20 13:30 | 480 | 477
2018-11-20 14:00 | 485 | 481
2018-11-20 14:30 | 503 | 499
2018-11-20 15:00 | 514 | 510
2018-11-20 15:30 | 518 | 513
2018-11-20 16:00 | 535 | 531
2018-11-20 16:30 | 561 | 557
2018-11-20 17:00 | 567 | 561
2018-11-20 17:30 | 565 | 558
2018-11-20 18:00 | 555 | 546
2018-11-20 18:30 | 551 | 541
2018-11-20 19:00 | 561 | 555
2018-11-20 19:30 | 548 | 541
2018-11-20 20:00 | 533 | 533
2018-11-20 20:30 | 517 | 516
2018-11-20 21:00 | 494 | 494
2018-11-20 21:30 | 471 | 471
2018-11-20 22:00 | 450 | 450
2018-11-20 22:30 | 430 | 429
2018-11-20 23:00 | 417 | 416
2018-11-20 23:30 | 401 | 399
2018-11-21 | 382 | 379
2018-11-21 00:30 | 344 | 342
2018-11-21 01:00 | 321 | 319
2018-11-21 01:30 | 301 | 299
2018-11-21 02:00 | 293 | 290
2018-11-21 02:30 | 293 | 290
2018-11-21 03:00 | 295 | 291
2018-11-21 03:30 | 302 | 299
2018-11-21 04:00 | 301 | 297
2018-11-21 04:30 | 312 | 309
2018-11-21 05:00 | 324 | 321
2018-11-21 05:30 | 330 | 328
2018-11-21 06:00 | 345 | 344
2018-11-21 06:30 | 381 | 380
2018-11-21 07:00 | 416 | 416
2018-11-21 07:30 | 450 | 449
2018-11-21 08:00 | 471 | 469
2018-11-21 08:30 | 487 | 485
2018-11-21 09:00 | 493 | 491
2018-11-21 09:30 | 499 | 497
2018-11-21 10:00 | 500 | 497
2018-11-21 10:30 | 500 | 498
2018-11-21 11:00 | 496 | 495
2018-11-21 11:30 | 502 | 501
2018-11-21 12:00 | 504 | 503
2018-11-21 12:30 | 514 | 512
2018-11-21 13:00 | 529 | 526
2018-11-21 13:30 | 554 | 547
2018-11-21 14:00 | 564 | 558
2018-11-21 14:30 | 588 | 583
2018-11-21 15:00 | 606 | 601
2018-11-21 15:30 | 611 | 605
2018-11-21 16:00 | 626 | 621
2018-11-21 16:30 | 628 | 622
2018-11-21 17:00 | 634 | 628
2018-11-21 17:30 | 633 | 625
2018-11-21 18:00 | 620 | 613
2018-11-21 18:30 | 610 | 603
2018-11-21 19:00 | 626 | 620
2018-11-21 19:30 | 609 | 602
2018-11-21 20:00 | 584 | 582
2018-11-21 20:30 | 562 | 560
2018-11-21 21:00 | 534 | 533
2018-11-21 21:30 | 512 | 511
2018-11-21 22:00 | 496 | 495
2018-11-21 22:30 | 475 | 473
2018-11-21 23:00 | 453 | 452
2018-11-21 23:30 | 429 | 428
2018-11-22 | 399 | 398
2018-11-22 00:30 | 368 | 365
2018-11-22 01:00 | 351 | 348
2018-11-22 01:30 | 332 | 329
2018-11-22 02:00 | 317 | 315
2018-11-22 02:30 | 318 | 317
2018-11-22 03:00 | 316 | 314
2018-11-22 03:30 | 316 | 314
2018-11-22 04:00 | 317 | 315
2018-11-22 04:30 | 320 | 318
2018-11-22 05:00 | 337 | 335
2018-11-22 05:30 | 358 | 357
2018-11-22 06:00 | 380 | 380
2018-11-22 06:30 | 418 | 418
2018-11-22 07:00 | 457 | 457
2018-11-22 07:30 | 518 | 517
2018-11-22 08:00 | 550 | 550
2018-11-22 08:30 | 559 | 559
2018-11-22 09:00 | 562 | 561
2018-11-22 09:30 | 563 | 562
2018-11-22 10:00 | 563 | 562
2018-11-22 10:30 | 574 | 573
2018-11-22 11:00 | 625 | 624
2018-11-22 11:30 | 642 | 638
2018-11-22 12:00 | 611 | 605
2018-11-22 12:30 | 553 | 549
2018-11-22 13:00 | 488 | 484
2018-11-22 13:30 | 458 | 457
2018-11-22 14:00 | 451 | 450
2018-11-22 14:30 | 478 | 477
2018-11-22 15:00 | 482 | 480
2018-11-22 15:30 | 486 | 484
2018-11-22 16:00 | 507 | 505
2018-11-22 16:30 | 551 | 548
2018-11-22 17:00 | 574 | 571
2018-11-22 17:30 | 590 | 587
2018-11-22 18:00 | 586 | 582
2018-11-22 18:30 | 574 | 567
2018-11-22 19:00 | 589 | 584
2018-11-22 19:30 | 585 | 581
2018-11-22 20:00 | 570 | 565
2018-11-22 20:30 | 549 | 545
2018-11-22 21:00 | 526 | 522
2018-11-22 21:30 | 498 | 495
2018-11-22 22:00 | 459 | 458
2018-11-22 22:30 | 439 | 439
2018-11-22 23:00 | 418 | 417
2018-11-22 23:30 | 391 | 390
2018-11-23 | 363 | 362
2018-11-23 00:30 | 329 | 328
2018-11-23 01:00 | 302 | 300
2018-11-23 01:30 | 291 | 288
2018-11-23 02:00 | 279 | 275
2018-11-23 02:30 | 266 | 263
2018-11-23 03:00 | 265 | 262
2018-11-23 03:30 | 264 | 261
2018-11-23 04:00 | 270 | 267
2018-11-23 04:30 | 277 | 274
2018-11-23 05:00 | 285 | 282
2018-11-23 05:30 | 313 | 310
2018-11-23 06:00 | 354 | 352
2018-11-23 06:30 | 387 | 386
2018-11-23 07:00 | 415 | 415
2018-11-23 07:30 | 441 | 441
2018-11-23 08:00 | 419 | 418
2018-11-23 08:30 | 416 | 416
2018-11-23 09:00 | 402 | 402
2018-11-23 09:30 | 390 | 390
2018-11-23 10:00 | 398 | 398
2018-11-23 10:30 | 402 | 401
2018-11-23 11:00 | 400 | 400
2018-11-23 11:30 | 401 | 400
2018-11-23 12:00 | 403 | 403
2018-11-23 12:30 | 407 | 406
2018-11-23 13:00 | 414 | 413
2018-11-23 13:30 | 413 | 412
2018-11-23 14:00 | 414 | 413
2018-11-23 14:30 | 434 | 433
2018-11-23 15:00 | 447 | 447
2018-11-23 15:30 | 472 | 471
2018-11-23 16:00 | 496 | 495
2018-11-23 16:30 | 514 | 513
2018-11-23 17:00 | 531 | 530
2018-11-23 17:30 | 534 | 533
2018-11-23 18:00 | 520 | 517
2018-11-23 18:30 | 507 | 504
2018-11-23 19:00 | 521 | 520
2018-11-23 19:30 | 514 | 512
2018-11-23 20:00 | 507 | 505
2018-11-23 20:30 | 495 | 493
2018-11-23 21:00 | 478 | 476
2018-11-23 21:30 | 455 | 454
2018-11-23 22:00 | 437 | 436
2018-11-23 22:30 | 420 | 418
2018-11-23 23:00 | 404 | 402
2018-11-23 23:30 | 386 | 382
2018-11-24 | 354 | 352
2018-11-24 00:30 | 324 | 321
2018-11-24 01:00 | 306 | 303
2018-11-24 01:30 | 300 | 296
2018-11-24 02:00 | 287 | 283
2018-11-24 02:30 | 283 | 279
2018-11-24 03:00 | 279 | 273
2018-11-24 03:30 | 267 | 260
2018-11-24 04:00 | 261 | 254
2018-11-24 04:30 | 282 | 275
2018-11-24 05:00 | 288 | 280
2018-11-24 05:30 | 293 | 284
2018-11-24 06:00 | 300 | 289
2018-11-24 06:30 | 318 | 309
2018-11-24 07:00 | 340 | 332
2018-11-24 07:30 | 354 | 348
2018-11-24 08:00 | 348 | 343
2018-11-24 08:30 | 351 | 347
2018-11-24 09:00 | 341 | 338
2018-11-24 09:30 | 336 | 333
2018-11-24 10:00 | 331 | 329
2018-11-24 10:30 | 317 | 315
2018-11-24 11:00 | 302 | 300
2018-11-24 11:30 | 318 | 316
2018-11-24 12:00 | 319 | 317
2018-11-24 12:30 | 320 | 318
2018-11-24 13:00 | 328 | 326
2018-11-24 13:30 | 335 | 333
2018-11-24 14:00 | 346 | 345
2018-11-24 14:30 | 358 | 357
2018-11-24 15:00 | 375 | 374
2018-11-24 15:30 | 389 | 388
2018-11-24 16:00 | 414 | 414
2018-11-24 16:30 | 442 | 441
2018-11-24 17:00 | 471 | 469
2018-11-24 17:30 | 473 | 471
2018-11-24 18:00 | 472 | 470
2018-11-24 18:30 | 466 | 463
2018-11-24 19:00 | 473 | 472
2018-11-24 19:30 | 468 | 467
2018-11-24 20:00 | 461 | 459
2018-11-24 20:30 | 451 | 450
2018-11-24 21:00 | 442 | 442
2018-11-24 21:30 | 424 | 423
2018-11-24 22:00 | 418 | 417
2018-11-24 22:30 | 398 | 397
2018-11-24 23:00 | 393 | 391
2018-11-24 23:30 | 381 | 378
2018-11-25 | 358 | 354
2018-11-25 00:30 | 336 | 330
2018-11-25 01:00 | 325 | 317
2018-11-25 01:30 | 316 | 308
2018-11-25 02:00 | 318 | 309
2018-11-25 02:30 | 319 | 310
2018-11-25 03:00 | 314 | 304
2018-11-25 03:30 | 315 | 305
2018-11-25 04:00 | 316 | 305
2018-11-25 04:30 | 306 | 295
2018-11-25 05:00 | 284 | 271
2018-11-25 05:30 | 277 | 263
2018-11-25 06:00 | 281 | 268
2018-11-25 06:30 | 292 | 279
2018-11-25 07:00 | 310 | 300
2018-11-25 07:30 | 322 | 313
2018-11-25 08:00 | 331 | 326
2018-11-25 08:30 | 333 | 329
2018-11-25 09:00 | 356 | 353
2018-11-25 09:30 | 388 | 387
2018-11-25 10:00 | 356 | 355
2018-11-25 10:30 | 353 | 352
2018-11-25 11:00 | 382 | 381
2018-11-25 11:30 | 398 | 397
2018-11-25 12:00 | 371 | 371
2018-11-25 12:30 | 357 | 357
2018-11-25 13:00 | 378 | 378
2018-11-25 13:30 | 410 | 410
2018-11-25 14:00 | 432 | 431
2018-11-25 14:30 | 417 | 417
2018-11-25 15:00 | 429 | 428
2018-11-25 15:30 | 462 | 462
2018-11-25 16:00 | 438 | 438
2018-11-25 16:30 | 458 | 458
2018-11-25 17:00 | 487 | 487
2018-11-25 17:30 | 495 | 495
2018-11-25 18:00 | 498 | 498
2018-11-25 18:30 | 503 | 503
2018-11-25 19:00 | 515 | 514
2018-11-25 19:30 | 515 | 515
2018-11-25 20:00 | 504 | 504
2018-11-25 20:30 | 491 | 490
2018-11-25 21:00 | 465 | 464
2018-11-25 21:30 | 448 | 448
2018-11-25 22:00 | 436 | 436
2018-11-25 22:30 | 423 | 423
2018-11-25 23:00 | 409 | 409
2018-11-25 23:30 | 385 | 385
2018-11-26 | 351 | 350
2018-11-26 00:30 | 323 | 322
2018-11-26 01:00 | 303 | 301
2018-11-26 01:30 | 299 | 296
2018-11-26 02:00 | 298 | 294
2018-11-26 02:30 | 286 | 282
2018-11-26 03:00 | 289 | 285
2018-11-26 03:30 | 292 | 287
2018-11-26 04:00 | 293 | 288
2018-11-26 04:30 | 306 | 302
2018-11-26 05:00 | 307 | 303
2018-11-26 05:30 | 338 | 335
2018-11-26 06:00 | 367 | 366
2018-11-26 06:30 | 414 | 414
2018-11-26 07:00 | 458 | 458
2018-11-26 07:30 | 483 | 482
2018-11-26 08:00 | 481 | 481
2018-11-26 08:30 | 487 | 487
2018-11-26 09:00 | 492 | 491
2018-11-26 09:30 | 491 | 490
2018-11-26 10:00 | 490 | 489
2018-11-26 10:30 | 493 | 492
2018-11-26 11:00 | 490 | 489
2018-11-26 11:30 | 495 | 494
2018-11-26 12:00 | 501 | 500
2018-11-26 12:30 | 500 | 500
2018-11-26 13:00 | 515 | 514
2018-11-26 13:30 | 529 | 526
2018-11-26 14:00 | 535 | 532
2018-11-26 14:30 | 544 | 542
2018-11-26 15:00 | 548 | 546
2018-11-26 15:30 | 569 | 567
2018-11-26 16:00 | 588 | 587
2018-11-26 16:30 | 614 | 613
2018-11-26 17:00 | 625 | 624
2018-11-26 17:30 | 621 | 621
2018-11-26 18:00 | 617 | 615
2018-11-26 18:30 | 579 | 576
2018-11-26 19:00 | 605 | 601
2018-11-26 19:30 | 595 | 585
2018-11-26 20:00 | 582 | 573
2018-11-26 20:30 | 556 | 551
2018-11-26 21:00 | 525 | 522
2018-11-26 21:30 | 501 | 499
2018-11-26 22:00 | 482 | 480
2018-11-26 22:30 | 467 | 465
2018-11-26 23:00 | 458 | 456
2018-11-26 23:30 | 430 | 427
2018-11-27 | 404 | 400
2018-11-27 00:30 | 378 | 373
2018-11-27 01:00 | 369 | 364
2018-11-27 01:30 | 361 | 355
2018-11-27 02:00 | 357 | 350
2018-11-27 02:30 | 350 | 343
2018-11-27 03:00 | 348 | 340
2018-11-27 03:30 | 347 | 339
2018-11-27 04:00 | 345 | 337
2018-11-27 04:30 | 349 | 342
2018-11-27 05:00 | 345 | 338
2018-11-27 05:30 | 377 | 371
2018-11-27 06:00 | 388 | 383
2018-11-27 06:30 | 425 | 423
2018-11-27 07:00 | 465 | 465
2018-11-27 07:30 | 492 | 492
2018-11-27 08:00 | 519 | 517
2018-11-27 08:30 | 536 | 534
2018-11-27 09:00 | 536 | 535
2018-11-27 09:30 | 544 | 543
2018-11-27 10:00 | 537 | 536
2018-11-27 10:30 | 532 | 531
2018-11-27 11:00 | 537 | 536
2018-11-27 11:30 | 544 | 543
2018-11-27 12:00 | 553 | 551
2018-11-27 12:30 | 545 | 543
2018-11-27 13:00 | 536 | 534
2018-11-27 13:30 | 517 | 515
2018-11-27 14:00 | 526 | 524
2018-11-27 14:30 | 524 | 522
2018-11-27 15:00 | 522 | 519
2018-11-27 15:30 | 543 | 541
2018-11-27 16:00 | 570 | 569
2018-11-27 16:30 | 586 | 585
2018-11-27 17:00 | 604 | 602
2018-11-27 17:30 | 608 | 605
2018-11-27 18:00 | 598 | 594
2018-11-27 18:30 | 592 | 586
2018-11-27 19:00 | 608 | 603
2018-11-27 19:30 | 605 | 598
2018-11-27 20:00 | 591 | 586
2018-11-27 20:30 | 579 | 577
2018-11-27 21:00 | 550 | 550
2018-11-27 21:30 | 523 | 522
2018-11-27 22:00 | 506 | 505
2018-11-27 22:30 | 493 | 492
2018-11-27 23:00 | 465 | 465
2018-11-27 23:30 | 445 | 445
2018-11-28 | 425 | 424
2018-11-28 00:30 | 398 | 398
2018-11-28 01:00 | 376 | 375
2018-11-28 01:30 | 361 | 360
2018-11-28 02:00 | 356 | 355
2018-11-28 02:30 | 350 | 349
2018-11-28 03:00 | 342 | 340
2018-11-28 03:30 | 346 | 345
2018-11-28 04:00 | 352 | 350
2018-11-28 04:30 | 364 | 363
2018-11-28 05:00 | 380 | 379
2018-11-28 05:30 | 399 | 398
2018-11-28 06:00 | 434 | 433
2018-11-28 06:30 | 476 | 476
2018-11-28 07:00 | 526 | 525
2018-11-28 07:30 | 570 | 568
2018-11-28 08:00 | 588 | 586
2018-11-28 08:30 | 596 | 595
2018-11-28 09:00 | 594 | 594
2018-11-28 09:30 | 595 | 594
2018-11-28 10:00 | 588 | 587
2018-11-28 10:30 | 591 | 590
2018-11-28 11:00 | 597 | 596
2018-11-28 11:30 | 619 | 618
2018-11-28 12:00 | 644 | 643
2018-11-28 12:30 | 692 | 691
2018-11-28 13:00 | 666 | 664
2018-11-28 13:30 | 634 | 632
2018-11-28 14:00 | 640 | 639
2018-11-28 14:30 | 643 | 642
2018-11-28 15:00 | 644 | 643
2018-11-28 15:30 | 657 | 655
2018-11-28 16:00 | 686 | 685
2018-11-28 16:30 | 716 | 715
2018-11-28 17:00 | 744 | 743
2018-11-28 17:30 | 729 | 728
2018-11-28 18:00 | 708 | 705
2018-11-28 18:30 | 674 | 669
2018-11-28 19:00 | 670 | 667
2018-11-28 19:30 | 658 | 654
2018-11-28 20:00 | 646 | 642
2018-11-28 20:30 | 633 | 629
2018-11-28 21:00 | 590 | 588
2018-11-28 21:30 | 551 | 548
2018-11-28 22:00 | 521 | 518
2018-11-28 22:30 | 492 | 491
2018-11-28 23:00 | 476 | 475
2018-11-28 23:30 | 457 | 456
2018-11-29 | 438 | 437
2018-11-29 00:30 | 415 | 414
2018-11-29 01:00 | 393 | 392
2018-11-29 01:30 | 380 | 379
2018-11-29 02:00 | 359 | 357
2018-11-29 02:30 | 356 | 354
2018-11-29 03:00 | 349 | 347
2018-11-29 03:30 | 352 | 350
2018-11-29 04:00 | 367 | 365
2018-11-29 04:30 | 376 | 374
2018-11-29 05:00 | 384 | 382
2018-11-29 05:30 | 402 | 400
2018-11-29 06:00 | 434 | 433
2018-11-29 06:30 | 471 | 470
2018-11-29 07:00 | 489 | 488
2018-11-29 07:30 | 503 | 503
2018-11-29 08:00 | 515 | 515
2018-11-29 08:30 | 533 | 532
2018-11-29 09:00 | 533 | 532
2018-11-29 09:30 | 540 | 540
2018-11-29 10:00 | 531 | 531
2018-11-29 10:30 | 534 | 533
2018-11-29 11:00 | 537 | 537
2018-11-29 11:30 | 537 | 536
2018-11-29 12:00 | 543 | 543
2018-11-29 12:30 | 554 | 553
2018-11-29 13:00 | 574 | 573
2018-11-29 13:30 | 599 | 598
2018-11-29 14:00 | 609 | 609
2018-11-29 14:30 | 624 | 623
2018-11-29 15:00 | 632 | 632
2018-11-29 15:30 | 639 | 639
2018-11-29 16:00 | 643 | 643
2018-11-29 16:30 | 654 | 653
2018-11-29 17:00 | 661 | 660
2018-11-29 17:30 | 652 | 651
2018-11-29 18:00 | 636 | 636
2018-11-29 18:30 | 620 | 619
2018-11-29 19:00 | 628 | 627
2018-11-29 19:30 | 628 | 627
2018-11-29 20:00 | 617 | 617
2018-11-29 20:30 | 605 | 604
2018-11-29 21:00 | 577 | 576
2018-11-29 21:30 | 550 | 549
2018-11-29 22:00 | 523 | 523
2018-11-29 22:30 | 506 | 505
2018-11-29 23:00 | 488 | 487
2018-11-29 23:30 | 471 | 470
2018-11-30 | 450 | 449
2018-11-30 00:30 | 409 | 409
2018-11-30 01:00 | 397 | 396
2018-11-30 01:30 | 385 | 384
2018-11-30 02:00 | 378 | 376
2018-11-30 02:30 | 374 | 372
2018-11-30 03:00 | 369 | 367
2018-11-30 03:30 | 367 | 365
2018-11-30 04:00 | 370 | 368
2018-11-30 04:30 | 378 | 376
2018-11-30 05:00 | 381 | 378
2018-11-30 05:30 | 389 | 387
2018-11-30 06:00 | 419 | 417
2018-11-30 06:30 | 463 | 462
2018-11-30 07:00 | 494 | 494
2018-11-30 07:30 | 517 | 517
2018-11-30 08:00 | 531 | 530
2018-11-30 08:30 | 542 | 541
2018-11-30 09:00 | 536 | 536
2018-11-30 09:30 | 533 | 532
2018-11-30 10:00 | 535 | 535
2018-11-30 10:30 | 537 | 536
2018-11-30 11:00 | 526 | 526
2018-11-30 11:30 | 548 | 548
2018-11-30 12:00 | 572 | 572
2018-11-30 12:30 | 559 | 559
2018-11-30 13:00 | 547 | 547
2018-11-30 13:30 | 569 | 568
2018-11-30 14:00 | 562 | 561
2018-11-30 14:30 | 553 | 552
2018-11-30 15:00 | 566 | 566
2018-11-30 15:30 | 580 | 580
2018-11-30 16:00 | 607 | 606
2018-11-30 16:30 | 620 | 619
2018-11-30 17:00 | 629 | 627
2018-11-30 17:30 | 631 | 628
2018-11-30 18:00 | 616 | 612
2018-11-30 18:30 | 596 | 590
2018-11-30 19:00 | 603 | 601
2018-11-30 19:30 | 607 | 604
2018-11-30 20:00 | 607 | 604
2018-11-30 20:30 | 586 | 583
2018-11-30 21:00 | 558 | 556
2018-11-30 21:30 | 542 | 540
2018-11-30 22:00 | 523 | 519
2018-11-30 22:30 | 511 | 507
2018-11-30 23:00 | 491 | 489
2018-11-30 23:30 | 474 | 470
2018-12-01 | 447 | 443
2018-12-01 00:30 | 412 | 409
2018-12-01 01:00 | 400 | 395
2018-12-01 01:30 | 383 | 378
2018-12-01 02:00 | 372 | 366
2018-12-01 02:30 | 366 | 359
2018-12-01 03:00 | 362 | 355
2018-12-01 03:30 | 348 | 340
2018-12-01 04:00 | 345 | 337
2018-12-01 04:30 | 352 | 344
2018-12-01 05:00 | 340 | 330
2018-12-01 05:30 | 342 | 332
2018-12-01 06:00 | 349 | 340
2018-12-01 06:30 | 369 | 362
2018-12-01 07:00 | 395 | 390
2018-12-01 07:30 | 410 | 407
2018-12-01 08:00 | 409 | 407
2018-12-01 08:30 | 419 | 418
2018-12-01 09:00 | 416 | 415
2018-12-01 09:30 | 415 | 414
2018-12-01 10:00 | 413 | 411
2018-12-01 10:30 | 423 | 422
2018-12-01 11:00 | 426 | 425
2018-12-01 11:30 | 435 | 434
2018-12-01 12:00 | 457 | 456
2018-12-01 12:30 | 473 | 472
2018-12-01 13:00 | 487 | 487
2018-12-01 13:30 | 516 | 516
2018-12-01 14:00 | 540 | 539
2018-12-01 14:30 | 563 | 563
2018-12-01 15:00 | 587 | 587
2018-12-01 15:30 | 603 | 603
2018-12-01 16:00 | 626 | 626
2018-12-01 16:30 | 644 | 644
2018-12-01 17:00 | 655 | 654
2018-12-01 17:30 | 650 | 648
2018-12-01 18:00 | 638 | 636
2018-12-01 18:30 | 619 | 618
2018-12-01 19:00 | 622 | 621
2018-12-01 19:30 | 622 | 622
2018-12-01 20:00 | 604 | 603
2018-12-01 20:30 | 588 | 586
2018-12-01 21:00 | 566 | 565
2018-12-01 21:30 | 553 | 551
2018-12-01 22:00 | 533 | 530
2018-12-01 22:30 | 515 | 512
2018-12-01 23:00 | 500 | 498
2018-12-01 23:30 | 476 | 473
2018-12-02 | 454 | 452
2018-12-02 00:30 | 419 | 416
2018-12-02 01:00 | 389 | 387
2018-12-02 01:30 | 382 | 379
2018-12-02 02:00 | 368 | 364
2018-12-02 02:30 | 349 | 345
2018-12-02 03:00 | 346 | 341
2018-12-02 03:30 | 347 | 341
2018-12-02 04:00 | 347 | 341
2018-12-02 04:30 | 342 | 336
2018-12-02 05:00 | 342 | 333
2018-12-02 05:30 | 352 | 340
2018-12-02 06:00 | 351 | 343
2018-12-02 06:30 | 373 | 367
2018-12-02 07:00 | 389 | 384
2018-12-02 07:30 | 407 | 403
2018-12-02 08:00 | 420 | 418
2018-12-02 08:30 | 439 | 437
2018-12-02 09:00 | 458 | 457
2018-12-02 09:30 | 479 | 477
2018-12-02 10:00 | 472 | 471
2018-12-02 10:30 | 495 | 493
2018-12-02 11:00 | 511 | 508
2018-12-02 11:30 | 529 | 526
2018-12-02 12:00 | 558 | 556
2018-12-02 12:30 | 589 | 585
2018-12-02 13:00 | 612 | 602
2018-12-02 13:30 | 649 | 642
2018-12-02 14:00 | 665 | 658
2018-12-02 14:30 | 682 | 676
2018-12-02 15:00 | 704 | 697
2018-12-02 15:30 | 726 | 720
2018-12-02 16:00 | 747 | 732
2018-12-02 16:30 | 763 | 744
2018-12-02 17:00 | 774 | 757
2018-12-02 17:30 | 774 | 755
2018-12-02 18:00 | 767 | 748
2018-12-02 18:30 | 762 | 742
2018-12-02 19:00 | 760 | 744
2018-12-02 19:30 | 758 | 741
2018-12-02 20:00 | 741 | 724
2018-12-02 20:30 | 708 | 693
2018-12-02 21:00 | 667 | 659
2018-12-02 21:30 | 626 | 618
2018-12-02 22:00 | 585 | 582
2018-12-02 22:30 | 555 | 552
2018-12-02 23:00 | 532 | 528
2018-12-02 23:30 | 500 | 497
2018-12-03 | 473 | 468
2018-12-03 00:30 | 430 | 426
2018-12-03 01:00 | 395 | 390
2018-12-03 01:30 | 379 | 375
2018-12-03 02:00 | 373 | 368
2018-12-03 02:30 | 364 | 359
2018-12-03 03:00 | 352 | 348
2018-12-03 03:30 | 354 | 350
2018-12-03 04:00 | 371 | 368
2018-12-03 04:30 | 383 | 380
2018-12-03 05:00 | 390 | 387
2018-12-03 05:30 | 421 | 418
2018-12-03 06:00 | 446 | 444
2018-12-03 06:30 | 492 | 491
2018-12-03 07:00 | 528 | 528
2018-12-03 07:30 | 556 | 555
2018-12-03 08:00 | 564 | 564
2018-12-03 08:30 | 576 | 576
2018-12-03 09:00 | 576 | 575
2018-12-03 09:30 | 583 | 582
2018-12-03 10:00 | 592 | 591
2018-12-03 10:30 | 600 | 600
2018-12-03 11:00 | 604 | 603
2018-12-03 11:30 | 607 | 607
2018-12-03 12:00 | 616 | 616
2018-12-03 12:30 | 640 | 637
2018-12-03 13:00 | 636 | 633
2018-12-03 13:30 | 645 | 641
2018-12-03 14:00 | 638 | 634
2018-12-03 14:30 | 650 | 646
2018-12-03 15:00 | 674 | 670
2018-12-03 15:30 | 683 | 679
2018-12-03 16:00 | 698 | 694
2018-12-03 16:30 | 698 | 694
2018-12-03 17:00 | 699 | 695
2018-12-03 17:30 | 692 | 686
2018-12-03 18:00 | 676 | 667
2018-12-03 18:30 | 643 | 637
2018-12-03 19:00 | 646 | 642
2018-12-03 19:30 | 645 | 640
2018-12-03 20:00 | 632 | 628
2018-12-03 20:30 | 611 | 607
2018-12-03 21:00 | 578 | 573
2018-12-03 21:30 | 551 | 544
2018-12-03 22:00 | 532 | 523
2018-12-03 22:30 | 514 | 504
2018-12-03 23:00 | 500 | 492
2018-12-03 23:30 | 486 | 483
2018-12-04 | 462 | 460
2018-12-04 00:30 | 426 | 424
2018-12-04 01:00 | 401 | 399
2018-12-04 01:30 | 383 | 380
2018-12-04 02:00 | 369 | 366
2018-12-04 02:30 | 347 | 344
2018-12-04 03:00 | 339 | 336
2018-12-04 03:30 | 348 | 345
2018-12-04 04:00 | 369 | 365
2018-12-04 04:30 | 384 | 381
2018-12-04 05:00 | 405 | 401
2018-12-04 05:30 | 421 | 418
2018-12-04 06:00 | 451 | 449
2018-12-04 06:30 | 480 | 479
2018-12-04 07:00 | 521 | 521
2018-12-04 07:30 | 554 | 552
2018-12-04 08:00 | 560 | 559
2018-12-04 08:30 | 585 | 585
2018-12-04 09:00 | 590 | 590
2018-12-04 09:30 | 597 | 597
2018-12-04 10:00 | 598 | 597
2018-12-04 10:30 | 603 | 602
2018-12-04 11:00 | 587 | 587
2018-12-04 11:30 | 605 | 605
2018-12-04 12:00 | 595 | 594
2018-12-04 12:30 | 593 | 593
2018-12-04 13:00 | 615 | 615
2018-12-04 13:30 | 640 | 640
2018-12-04 14:00 | 655 | 654
2018-12-04 14:30 | 674 | 672
2018-12-04 15:00 | 683 | 681
2018-12-04 15:30 | 683 | 680
2018-12-04 16:00 | 667 | 664
2018-12-04 16:30 | 662 | 658
2018-12-04 17:00 | 659 | 655
2018-12-04 17:30 | 642 | 640
2018-12-04 18:00 | 638 | 636
2018-12-04 18:30 | 619 | 618
2018-12-04 19:00 | 626 | 626
2018-12-04 19:30 | 619 | 618
2018-12-04 20:00 | 603 | 602
2018-12-04 20:30 | 591 | 589
2018-12-04 21:00 | 573 | 572
2018-12-04 21:30 | 559 | 557
2018-12-04 22:00 | 538 | 536
2018-12-04 22:30 | 519 | 516
2018-12-04 23:00 | 506 | 503
2018-12-04 23:30 | 477 | 474
2018-12-05 | 442 | 440
2018-12-05 00:30 | 404 | 402
2018-12-05 01:00 | 379 | 376
2018-12-05 01:30 | 357 | 353
2018-12-05 02:00 | 342 | 338
2018-12-05 02:30 | 330 | 326
2018-12-05 03:00 | 324 | 320
2018-12-05 03:30 | 325 | 322
2018-12-05 04:00 | 328 | 325
2018-12-05 04:30 | 351 | 347
2018-12-05 05:00 | 352 | 348
2018-12-05 05:30 | 394 | 391
2018-12-05 06:00 | 419 | 417
2018-12-05 06:30 | 453 | 452
2018-12-05 07:00 | 492 | 491
2018-12-05 07:30 | 533 | 532
2018-12-05 08:00 | 534 | 534
2018-12-05 08:30 | 545 | 545
2018-12-05 09:00 | 533 | 533
2018-12-05 09:30 | 532 | 532
2018-12-05 10:00 | 550 | 550
2018-12-05 10:30 | 562 | 562
2018-12-05 11:00 | 572 | 572
2018-12-05 11:30 | 557 | 556
2018-12-05 12:00 | 547 | 547
2018-12-05 12:30 | 554 | 554
2018-12-05 13:00 | 560 | 560
2018-12-05 13:30 | 538 | 538
2018-12-05 14:00 | 542 | 542
2018-12-05 14:30 | 556 | 556
2018-12-05 15:00 | 547 | 547
2018-12-05 15:30 | 534 | 534
2018-12-05 16:00 | 548 | 548
2018-12-05 16:30 | 550 | 550
2018-12-05 17:00 | 568 | 568
2018-12-05 17:30 | 565 | 564
2018-12-05 18:00 | 549 | 549
2018-12-05 18:30 | 540 | 538
2018-12-05 19:00 | 551 | 551
2018-12-05 19:30 | 552 | 551
2018-12-05 20:00 | 550 | 548
2018-12-05 20:30 | 545 | 544
2018-12-05 21:00 | 531 | 530
2018-12-05 21:30 | 514 | 514
2018-12-05 22:00 | 506 | 506
2018-12-05 22:30 | 485 | 484
2018-12-05 23:00 | 474 | 474
2018-12-05 23:30 | 464 | 463
2018-12-06 | 444 | 442
2018-12-06 00:30 | 400 | 397
2018-12-06 01:00 | 377 | 374
2018-12-06 01:30 | 350 | 345
2018-12-06 02:00 | 333 | 327
2018-12-06 02:30 | 324 | 318
2018-12-06 03:00 | 313 | 307
2018-12-06 03:30 | 312 | 305
2018-12-06 04:00 | 312 | 305
2018-12-06 04:30 | 320 | 314
2018-12-06 05:00 | 324 | 318
2018-12-06 05:30 | 352 | 347
2018-12-06 06:00 | 381 | 379
2018-12-06 06:30 | 415 | 415
2018-12-06 07:00 | 437 | 436
2018-12-06 07:30 | 477 | 477
2018-12-06 08:00 | 482 | 481
2018-12-06 08:30 | 485 | 484
2018-12-06 09:00 | 478 | 478
2018-12-06 09:30 | 501 | 501
2018-12-06 10:00 | 513 | 513
2018-12-06 10:30 | 526 | 526
2018-12-06 11:00 | 516 | 516
2018-12-06 11:30 | 500 | 500
2018-12-06 12:00 | 498 | 497
2018-12-06 12:30 | 491 | 490
2018-12-06 13:00 | 496 | 496
2018-12-06 13:30 | 508 | 508
2018-12-06 14:00 | 500 | 500
2018-12-06 14:30 | 497 | 497
2018-12-06 15:00 | 492 | 492
2018-12-06 15:30 | 503 | 503
2018-12-06 16:00 | 525 | 525
2018-12-06 16:30 | 546 | 546
2018-12-06 17:00 | 566 | 566
2018-12-06 17:30 | 570 | 569
2018-12-06 18:00 | 572 | 571
2018-12-06 18:30 | 569 | 567
2018-12-06 19:00 | 576 | 575
2018-12-06 19:30 | 569 | 568
2018-12-06 20:00 | 562 | 561
2018-12-06 20:30 | 557 | 556
2018-12-06 21:00 | 534 | 533
2018-12-06 21:30 | 518 | 516
2018-12-06 22:00 | 494 | 492
2018-12-06 22:30 | 470 | 468
2018-12-06 23:00 | 454 | 452
2018-12-06 23:30 | 427 | 425
2018-12-07 | 392 | 388
2018-12-07 00:30 | 372 | 368
2018-12-07 01:00 | 364 | 359
2018-12-07 01:30 | 359 | 353
2018-12-07 02:00 | 336 | 330
2018-12-07 02:30 | 329 | 323
2018-12-07 03:00 | 327 | 320
2018-12-07 03:30 | 323 | 316
2018-12-07 04:00 | 322 | 315
2018-12-07 04:30 | 324 | 317
2018-12-07 05:00 | 327 | 319
2018-12-07 05:30 | 361 | 352
2018-12-07 06:00 | 385 | 378
2018-12-07 06:30 | 434 | 430
2018-12-07 07:00 | 468 | 466
2018-12-07 07:30 | 487 | 484
2018-12-07 08:00 | 504 | 502
2018-12-07 08:30 | 510 | 509
2018-12-07 09:00 | 521 | 518
2018-12-07 09:30 | 531 | 528
2018-12-07 10:00 | 530 | 527
2018-12-07 10:30 | 547 | 545
2018-12-07 11:00 | 565 | 563
2018-12-07 11:30 | 555 | 552
2018-12-07 12:00 | 551 | 548
2018-12-07 12:30 | 542 | 539
2018-12-07 13:00 | 549 | 546
2018-12-07 13:30 | 551 | 549
2018-12-07 14:00 | 548 | 546
2018-12-07 14:30 | 557 | 554
2018-12-07 15:00 | 548 | 545
2018-12-07 15:30 | 545 | 542
2018-12-07 16:00 | 541 | 537
2018-12-07 16:30 | 561 | 557
2018-12-07 17:00 | 580 | 577
2018-12-07 17:30 | 571 | 568
2018-12-07 18:00 | 581 | 576
2018-12-07 18:30 | 567 | 562
2018-12-07 19:00 | 566 | 564
2018-12-07 19:30 | 563 | 560
2018-12-07 20:00 | 554 | 552
2018-12-07 20:30 | 531 | 528
2018-12-07 21:00 | 509 | 508
2018-12-07 21:30 | 503 | 500
2018-12-07 22:00 | 484 | 480
2018-12-07 22:30 | 479 | 476
2018-12-07 23:00 | 455 | 452
2018-12-07 23:30 | 435 | 431
2018-12-08 | 413 | 407
2018-12-08 00:30 | 383 | 375
2018-12-08 01:00 | 379 | 369
2018-12-08 01:30 | 366 | 356
2018-12-08 02:00 | 353 | 342
2018-12-08 02:30 | 345 | 333
2018-12-08 03:00 | 328 | 315
2018-12-08 03:30 | 325 | 311
2018-12-08 04:00 | 322 | 308
2018-12-08 04:30 | 320 | 306
2018-12-08 05:00 | 316 | 301
2018-12-08 05:30 | 333 | 318
2018-12-08 06:00 | 349 | 336
2018-12-08 06:30 | 370 | 360
2018-12-08 07:00 | 383 | 374
2018-12-08 07:30 | 405 | 399
2018-12-08 08:00 | 436 | 430
2018-12-08 08:30 | 450 | 446
2018-12-08 09:00 | 454 | 451
2018-12-08 09:30 | 455 | 452
2018-12-08 10:00 | 450 | 447
2018-12-08 10:30 | 459 | 457
2018-12-08 11:00 | 476 | 474
2018-12-08 11:30 | 480 | 478
2018-12-08 12:00 | 478 | 476
2018-12-08 12:30 | 480 | 477
2018-12-08 13:00 | 490 | 488
2018-12-08 13:30 | 493 | 491
2018-12-08 14:00 | 474 | 471
2018-12-08 14:30 | 466 | 462
2018-12-08 15:00 | 461 | 458
2018-12-08 15:30 | 456 | 453
2018-12-08 16:00 | 455 | 452
2018-12-08 16:30 | 466 | 463
2018-12-08 17:00 | 483 | 480
2018-12-08 17:30 | 484 | 480
2018-12-08 18:00 | 488 | 484
2018-12-08 18:30 | 487 | 484
2018-12-08 19:00 | 494 | 492
2018-12-08 19:30 | 495 | 491
2018-12-08 20:00 | 490 | 486
2018-12-08 20:30 | 481 | 478
2018-12-08 21:00 | 477 | 472
2018-12-08 21:30 | 469 | 465
2018-12-08 22:00 | 451 | 447
2018-12-08 22:30 | 433 | 428
2018-12-08 23:00 | 425 | 420
2018-12-08 23:30 | 414 | 408
2018-12-09 | 387 | 379
2018-12-09 00:30 | 353 | 343
2018-12-09 01:00 | 348 | 337
2018-12-09 01:30 | 341 | 329
2018-12-09 02:00 | 316 | 303
2018-12-09 02:30 | 319 | 305
2018-12-09 03:00 | 319 | 305
2018-12-09 03:30 | 318 | 303
2018-12-09 04:00 | 317 | 302
2018-12-09 04:30 | 317 | 301
2018-12-09 05:00 | 312 | 294
2018-12-09 05:30 | 308 | 289
2018-12-09 06:00 | 316 | 298
2018-12-09 06:30 | 322 | 305
2018-12-09 07:00 | 328 | 312
2018-12-09 07:30 | 335 | 323
2018-12-09 08:00 | 349 | 338
2018-12-09 08:30 | 373 | 364
2018-12-09 09:00 | 376 | 369
2018-12-09 09:30 | 369 | 364
2018-12-09 10:00 | 387 | 383
2018-12-09 10:30 | 392 | 388
2018-12-09 11:00 | 394 | 391
2018-12-09 11:30 | 384 | 381
2018-12-09 12:00 | 406 | 402
2018-12-09 12:30 | 420 | 417
2018-12-09 13:00 | 433 | 430
2018-12-09 13:30 | 440 | 436
2018-12-09 14:00 | 451 | 445
2018-12-09 14:30 | 454 | 448
2018-12-09 15:00 | 458 | 453
2018-12-09 15:30 | 464 | 458
2018-12-09 16:00 | 466 | 460
2018-12-09 16:30 | 489 | 484
2018-12-09 17:00 | 523 | 519
2018-12-09 17:30 | 530 | 524
2018-12-09 18:00 | 527 | 521
2018-12-09 18:30 | 529 | 523
2018-12-09 19:00 | 538 | 534
2018-12-09 19:30 | 549 | 543
2018-12-09 20:00 | 547 | 540
2018-12-09 20:30 | 535 | 527
2018-12-09 21:00 | 515 | 510
2018-12-09 21:30 | 501 | 497
2018-12-09 22:00 | 486 | 482
2018-12-09 22:30 | 473 | 470
2018-12-09 23:00 | 456 | 452
2018-12-09 23:30 | 436 | 432
2018-12-10 | 419 | 412
2018-12-10 00:30 | 394 | 385
2018-12-10 01:00 | 381 | 371
2018-12-10 01:30 | 375 | 365
2018-12-10 02:00 | 357 | 346
2018-12-10 02:30 | 345 | 334
2018-12-10 03:00 | 340 | 328
2018-12-10 03:30 | 339 | 327
2018-12-10 04:00 | 341 | 329
2018-12-10 04:30 | 357 | 347
2018-12-10 05:00 | 366 | 355
2018-12-10 05:30 | 388 | 379
2018-12-10 06:00 | 422 | 416
2018-12-10 06:30 | 463 | 459
2018-12-10 07:00 | 504 | 500
2018-12-10 07:30 | 534 | 531
2018-12-10 08:00 | 552 | 548
2018-12-10 08:30 | 556 | 552
2018-12-10 09:00 | 554 | 550
2018-12-10 09:30 | 560 | 558
2018-12-10 10:00 | 574 | 572
2018-12-10 10:30 | 586 | 585
2018-12-10 11:00 | 595 | 594
2018-12-10 11:30 | 595 | 593
2018-12-10 12:00 | 592 | 591
2018-12-10 12:30 | 592 | 590
2018-12-10 13:00 | 596 | 595
2018-12-10 13:30 | 602 | 601
2018-12-10 14:00 | 609 | 609
2018-12-10 14:30 | 619 | 618
2018-12-10 15:00 | 625 | 624
2018-12-10 15:30 | 655 | 655
2018-12-10 16:00 | 654 | 654
2018-12-10 16:30 | 641 | 640
2018-12-10 17:00 | 657 | 656
2018-12-10 17:30 | 662 | 659
2018-12-10 18:00 | 653 | 651
2018-12-10 18:30 | 635 | 631
2018-12-10 19:00 | 633 | 629
2018-12-10 19:30 | 630 | 627
2018-12-10 20:00 | 622 | 618
2018-12-10 20:30 | 613 | 609
2018-12-10 21:00 | 587 | 584
2018-12-10 21:30 | 563 | 560
2018-12-10 22:00 | 531 | 530
2018-12-10 22:30 | 511 | 510
2018-12-10 23:00 | 495 | 493
2018-12-10 23:30 | 466 | 464
2018-12-11 | 438 | 436
2018-12-11 00:30 | 409 | 406
2018-12-11 01:00 | 395 | 392
2018-12-11 01:30 | 375 | 370
2018-12-11 02:00 | 361 | 357
2018-12-11 02:30 | 361 | 356
2018-12-11 03:00 | 360 | 355
2018-12-11 03:30 | 358 | 354
2018-12-11 04:00 | 370 | 365
2018-12-11 04:30 | 388 | 384
2018-12-11 05:00 | 382 | 378
2018-12-11 05:30 | 396 | 392
2018-12-11 06:00 | 420 | 418
2018-12-11 06:30 | 468 | 466
2018-12-11 07:00 | 496 | 494
2018-12-11 07:30 | 524 | 523
2018-12-11 08:00 | 534 | 534
2018-12-11 08:30 | 550 | 549
2018-12-11 09:00 | 556 | 554
2018-12-11 09:30 | 554 | 553
2018-12-11 10:00 | 558 | 557
2018-12-11 10:30 | 560 | 559
2018-12-11 11:00 | 568 | 566
2018-12-11 11:30 | 577 | 573
2018-12-11 12:00 | 580 | 573
2018-12-11 12:30 | 593 | 587
2018-12-11 13:00 | 597 | 590
2018-12-11 13:30 | 611 | 603
2018-12-11 14:00 | 610 | 603
2018-12-11 14:30 | 620 | 614
2018-12-11 15:00 | 617 | 610
2018-12-11 15:30 | 630 | 624
2018-12-11 16:00 | 664 | 658
2018-12-11 16:30 | 694 | 689
2018-12-11 17:00 | 694 | 688
2018-12-11 17:30 | 677 | 669
2018-12-11 18:00 | 670 | 660
2018-12-11 18:30 | 647 | 635
2018-12-11 19:00 | 648 | 637
2018-12-11 19:30 | 640 | 634
2018-12-11 20:00 | 631 | 626
2018-12-11 20:30 | 617 | 613
2018-12-11 21:00 | 583 | 577
2018-12-11 21:30 | 558 | 551
2018-12-11 22:00 | 541 | 533
2018-12-11 22:30 | 525 | 517
2018-12-11 23:00 | 499 | 490
2018-12-11 23:30 | 469 | 459
2018-12-12 | 435 | 431
2018-12-12 00:30 | 412 | 406
2018-12-12 01:00 | 399 | 392
2018-12-12 01:30 | 387 | 379
2018-12-12 02:00 | 381 | 372
2018-12-12 02:30 | 383 | 373
2018-12-12 03:00 | 387 | 378
2018-12-12 03:30 | 396 | 387
2018-12-12 04:00 | 398 | 389
2018-12-12 04:30 | 397 | 389
2018-12-12 05:00 | 394 | 385
2018-12-12 05:30 | 415 | 408
2018-12-12 06:00 | 432 | 427
2018-12-12 06:30 | 464 | 461
2018-12-12 07:00 | 499 | 495
2018-12-12 07:30 | 525 | 522
2018-12-12 08:00 | 533 | 531
2018-12-12 08:30 | 545 | 543
2018-12-12 09:00 | 545 | 543
2018-12-12 09:30 | 546 | 544
2018-12-12 10:00 | 559 | 556
2018-12-12 10:30 | 568 | 566
2018-12-12 11:00 | 568 | 566
2018-12-12 11:30 | 565 | 562
2018-12-12 12:00 | 570 | 568
2018-12-12 12:30 | 576 | 574
2018-12-12 13:00 | 587 | 583
2018-12-12 13:30 | 591 | 588
2018-12-12 14:00 | 607 | 600
2018-12-12 14:30 | 610 | 602
2018-12-12 15:00 | 620 | 613
2018-12-12 15:30 | 632 | 626
2018-12-12 16:00 | 646 | 640
2018-12-12 16:30 | 661 | 655
2018-12-12 17:00 | 689 | 680
2018-12-12 17:30 | 683 | 673
2018-12-12 18:00 | 666 | 654
2018-12-12 18:30 | 649 | 640
2018-12-12 19:00 | 650 | 643
2018-12-12 19:30 | 639 | 636
2018-12-12 20:00 | 616 | 614
2018-12-12 20:30 | 594 | 593
2018-12-12 21:00 | 575 | 574
2018-12-12 21:30 | 552 | 549
2018-12-12 22:00 | 536 | 532
2018-12-12 22:30 | 523 | 518
2018-12-12 23:00 | 495 | 492
2018-12-12 23:30 | 460 | 458
2018-12-13 | 433 | 430
2018-12-13 00:30 | 396 | 392
2018-12-13 01:00 | 392 | 386
2018-12-13 01:30 | 378 | 371
2018-12-13 02:00 | 367 | 359
2018-12-13 02:30 | 377 | 369
2018-12-13 03:00 | 378 | 371
2018-12-13 03:30 | 377 | 369
2018-12-13 04:00 | 380 | 373
2018-12-13 04:30 | 392 | 385
2018-12-13 05:00 | 394 | 387
2018-12-13 05:30 | 408 | 402
2018-12-13 06:00 | 437 | 432
2018-12-13 06:30 | 461 | 459
2018-12-13 07:00 | 494 | 493
2018-12-13 07:30 | 525 | 523
2018-12-13 08:00 | 548 | 547
2018-12-13 08:30 | 553 | 552
2018-12-13 09:00 | 547 | 546
2018-12-13 09:30 | 551 | 550
2018-12-13 10:00 | 556 | 555
2018-12-13 10:30 | 573 | 572
2018-12-13 11:00 | 570 | 570
2018-12-13 11:30 | 570 | 569
2018-12-13 12:00 | 575 | 574
2018-12-13 12:30 | 591 | 591
2018-12-13 13:00 | 609 | 609
2018-12-13 13:30 | 605 | 605
2018-12-13 14:00 | 625 | 624
2018-12-13 14:30 | 635 | 629
2018-12-13 15:00 | 635 | 628
2018-12-13 15:30 | 642 | 634
2018-12-13 16:00 | 653 | 646
2018-12-13 16:30 | 674 | 668
2018-12-13 17:00 | 688 | 682
2018-12-13 17:30 | 687 | 680
2018-12-13 18:00 | 671 | 664
2018-12-13 18:30 | 663 | 654
2018-12-13 19:00 | 673 | 666
2018-12-13 19:30 | 665 | 660
2018-12-13 20:00 | 651 | 649
2018-12-13 20:30 | 635 | 634
2018-12-13 21:00 | 612 | 611
2018-12-13 21:30 | 591 | 590
2018-12-13 22:00 | 563 | 560
2018-12-13 22:30 | 540 | 538
2018-12-13 23:00 | 512 | 511
2018-12-13 23:30 | 493 | 491
2018-12-14 | 469 | 468
2018-12-14 00:30 | 434 | 432
2018-12-14 01:00 | 406 | 404
2018-12-14 01:30 | 379 | 377
2018-12-14 02:00 | 366 | 364
2018-12-14 02:30 | 362 | 359
2018-12-14 03:00 | 356 | 353
2018-12-14 03:30 | 352 | 348
2018-12-14 04:00 | 356 | 353
2018-12-14 04:30 | 369 | 366
2018-12-14 05:00 | 376 | 374
2018-12-14 05:30 | 413 | 411
2018-12-14 06:00 | 451 | 449
2018-12-14 06:30 | 502 | 501
2018-12-14 07:00 | 536 | 535
2018-12-14 07:30 | 588 | 583
2018-12-14 08:00 | 620 | 614
2018-12-14 08:30 | 647 | 641
2018-12-14 09:00 | 652 | 646
2018-12-14 09:30 | 634 | 628
2018-12-14 10:00 | 611 | 605
2018-12-14 10:30 | 601 | 594
2018-12-14 11:00 | 592 | 585
2018-12-14 11:30 | 588 | 582
2018-12-14 12:00 | 592 | 587
2018-12-14 12:30 | 611 | 607
2018-12-14 13:00 | 610 | 607
2018-12-14 13:30 | 628 | 625
2018-12-14 14:00 | 649 | 646
2018-12-14 14:30 | 644 | 639
2018-12-14 15:00 | 639 | 635
2018-12-14 15:30 | 647 | 642
2018-12-14 16:00 | 697 | 692
2018-12-14 16:30 | 715 | 709
2018-12-14 17:00 | 687 | 681
2018-12-14 17:30 | 659 | 650
2018-12-14 18:00 | 637 | 628
2018-12-14 18:30 | 623 | 612
2018-12-14 19:00 | 619 | 612
2018-12-14 19:30 | 612 | 608
2018-12-14 20:00 | 608 | 605
2018-12-14 20:30 | 599 | 596
2018-12-14 21:00 | 576 | 576
2018-12-14 21:30 | 564 | 563
2018-12-14 22:00 | 554 | 552
2018-12-14 22:30 | 542 | 539
2018-12-14 23:00 | 523 | 521
2018-12-14 23:30 | 506 | 503
2018-12-15 | 480 | 476
2018-12-15 00:30 | 456 | 451
2018-12-15 01:00 | 436 | 433
2018-12-15 01:30 | 416 | 413
2018-12-15 02:00 | 405 | 401
2018-12-15 02:30 | 404 | 399
2018-12-15 03:00 | 400 | 395
2018-12-15 03:30 | 401 | 396
2018-12-15 04:00 | 404 | 399
2018-12-15 04:30 | 402 | 397
2018-12-15 05:00 | 398 | 393
2018-12-15 05:30 | 401 | 395
2018-12-15 06:00 | 408 | 403
2018-12-15 06:30 | 425 | 421
2018-12-15 07:00 | 447 | 444
2018-12-15 07:30 | 469 | 468
2018-12-15 08:00 | 477 | 476
2018-12-15 08:30 | 498 | 497
2018-12-15 09:00 | 497 | 496
2018-12-15 09:30 | 499 | 498
2018-12-15 10:00 | 500 | 499
2018-12-15 10:30 | 517 | 516
2018-12-15 11:00 | 546 | 544
2018-12-15 11:30 | 555 | 554
2018-12-15 12:00 | 566 | 565
2018-12-15 12:30 | 554 | 553
2018-12-15 13:00 | 560 | 558
2018-12-15 13:30 | 560 | 559
2018-12-15 14:00 | 555 | 554
2018-12-15 14:30 | 562 | 561
2018-12-15 15:00 | 577 | 576
2018-12-15 15:30 | 591 | 589
2018-12-15 16:00 | 593 | 591
2018-12-15 16:30 | 599 | 598
2018-12-15 17:00 | 615 | 613
2018-12-15 17:30 | 615 | 607
2018-12-15 18:00 | 610 | 601
2018-12-15 18:30 | 606 | 597
2018-12-15 19:00 | 602 | 597
2018-12-15 19:30 | 590 | 586
2018-12-15 20:00 | 580 | 576
2018-12-15 20:30 | 574 | 570
2018-12-15 21:00 | 555 | 554
2018-12-15 21:30 | 540 | 540
2018-12-15 22:00 | 530 | 530
2018-12-15 22:30 | 517 | 517
2018-12-15 23:00 | 497 | 496
2018-12-15 23:30 | 483 | 482
2018-12-16 | 464 | 463
2018-12-16 00:30 | 444 | 441
2018-12-16 01:00 | 438 | 435
2018-12-16 01:30 | 423 | 420
2018-12-16 02:00 | 413 | 409
2018-12-16 02:30 | 406 | 402
2018-12-16 03:00 | 399 | 395
2018-12-16 03:30 | 398 | 393
2018-12-16 04:00 | 395 | 390
2018-12-16 04:30 | 389 | 384
2018-12-16 05:00 | 383 | 377
2018-12-16 05:30 | 382 | 375
2018-12-16 06:00 | 392 | 385
2018-12-16 06:30 | 411 | 405
2018-12-16 07:00 | 420 | 416
2018-12-16 07:30 | 451 | 447
2018-12-16 08:00 | 471 | 469
2018-12-16 08:30 | 485 | 484
2018-12-16 09:00 | 492 | 490
2018-12-16 09:30 | 503 | 503
2018-12-16 10:00 | 516 | 515
2018-12-16 10:30 | 523 | 523
2018-12-16 11:00 | 532 | 531
2018-12-16 11:30 | 525 | 524
2018-12-16 12:00 | 523 | 522
2018-12-16 12:30 | 524 | 523
2018-12-16 13:00 | 526 | 524
2018-12-16 13:30 | 528 | 527
2018-12-16 14:00 | 521 | 519
2018-12-16 14:30 | 528 | 527
2018-12-16 15:00 | 541 | 539
2018-12-16 15:30 | 547 | 545
2018-12-16 16:00 | 555 | 553
2018-12-16 16:30 | 554 | 552
2018-12-16 17:00 | 555 | 553
2018-12-16 17:30 | 555 | 553
2018-12-16 18:00 | 560 | 559
2018-12-16 18:30 | 559 | 558
2018-12-16 19:00 | 560 | 559
2018-12-16 19:30 | 553 | 551
2018-12-16 20:00 | 551 | 550
2018-12-16 20:30 | 547 | 545
2018-12-16 21:00 | 533 | 531
2018-12-16 21:30 | 518 | 515
2018-12-16 22:00 | 501 | 497
2018-12-16 22:30 | 486 | 482
2018-12-16 23:00 | 471 | 467
2018-12-16 23:30 | 450 | 447
2018-12-17 | 431 | 427
2018-12-17 00:30 | 410 | 404
2018-12-17 01:00 | 400 | 392
2018-12-17 01:30 | 392 | 384
2018-12-17 02:00 | 388 | 380
2018-12-17 02:30 | 374 | 364
2018-12-17 03:00 | 376 | 366
2018-12-17 03:30 | 375 | 365
2018-12-17 04:00 | 374 | 363
2018-12-17 04:30 | 377 | 367
2018-12-17 05:00 | 374 | 365
2018-12-17 05:30 | 402 | 394
2018-12-17 06:00 | 428 | 422
2018-12-17 06:30 | 477 | 474
2018-12-17 07:00 | 505 | 502
2018-12-17 07:30 | 526 | 523
2018-12-17 08:00 | 555 | 553
2018-12-17 08:30 | 578 | 576
2018-12-17 09:00 | 588 | 587
2018-12-17 09:30 | 594 | 593
2018-12-17 10:00 | 596 | 593
2018-12-17 10:30 | 593 | 591
2018-12-17 11:00 | 606 | 604
2018-12-17 11:30 | 613 | 610
2018-12-17 12:00 | 615 | 613
2018-12-17 12:30 | 620 | 618
2018-12-17 13:00 | 622 | 620
2018-12-17 13:30 | 611 | 609
2018-12-17 14:00 | 617 | 615
2018-12-17 14:30 | 625 | 623
2018-12-17 15:00 | 632 | 630
2018-12-17 15:30 | 628 | 626
2018-12-17 16:00 | 639 | 636
2018-12-17 16:30 | 641 | 638
2018-12-17 17:00 | 633 | 629
2018-12-17 17:30 | 629 | 625
2018-12-17 18:00 | 614 | 609
2018-12-17 18:30 | 594 | 591
2018-12-17 19:00 | 592 | 590
2018-12-17 19:30 | 586 | 584
2018-12-17 20:00 | 579 | 578
2018-12-17 20:30 | 570 | 569
2018-12-17 21:00 | 558 | 556
2018-12-17 21:30 | 534 | 532
2018-12-17 22:00 | 526 | 523
2018-12-17 22:30 | 510 | 507
2018-12-17 23:00 | 485 | 481
2018-12-17 23:30 | 467 | 461
2018-12-18 | 450 | 442
2018-12-18 00:30 | 419 | 411
2018-12-18 01:00 | 403 | 396
2018-12-18 01:30 | 392 | 385
2018-12-18 02:00 | 383 | 376
2018-12-18 02:30 | 380 | 373
2018-12-18 03:00 | 375 | 368
2018-12-18 03:30 | 380 | 372
2018-12-18 04:00 | 383 | 376
2018-12-18 04:30 | 393 | 385
2018-12-18 05:00 | 396 | 388
2018-12-18 05:30 | 425 | 418
2018-12-18 06:00 | 438 | 434
2018-12-18 06:30 | 463 | 462
2018-12-18 07:00 | 498 | 497
2018-12-18 07:30 | 521 | 520
2018-12-18 08:00 | 547 | 547
2018-12-18 08:30 | 564 | 564
2018-12-18 09:00 | 564 | 564
2018-12-18 09:30 | 557 | 557
2018-12-18 10:00 | 567 | 567
2018-12-18 10:30 | 574 | 574
2018-12-18 11:00 | 576 | 576
2018-12-18 11:30 | 583 | 582
2018-12-18 12:00 | 592 | 591
2018-12-18 12:30 | 598 | 598
2018-12-18 13:00 | 608 | 607
2018-12-18 13:30 | 607 | 606
2018-12-18 14:00 | 616 | 615
2018-12-18 14:30 | 620 | 620
2018-12-18 15:00 | 625 | 624
2018-12-18 15:30 | 630 | 629
2018-12-18 16:00 | 616 | 616
2018-12-18 16:30 | 622 | 622
2018-12-18 17:00 | 634 | 634
2018-12-18 17:30 | 639 | 633
2018-12-18 18:00 | 627 | 619
2018-12-18 18:30 | 596 | 595
2018-12-18 19:00 | 594 | 593
2018-12-18 19:30 | 596 | 595
2018-12-18 20:00 | 595 | 593
2018-12-18 20:30 | 590 | 589
2018-12-18 21:00 | 568 | 568
2018-12-18 21:30 | 553 | 552
2018-12-18 22:00 | 536 | 534
2018-12-18 22:30 | 516 | 514
2018-12-18 23:00 | 504 | 503
2018-12-18 23:30 | 486 | 484
2018-12-19 | 457 | 456
2018-12-19 00:30 | 428 | 425
2018-12-19 01:00 | 414 | 410
2018-12-19 01:30 | 401 | 397
2018-12-19 02:00 | 388 | 383
2018-12-19 02:30 | 387 | 382
2018-12-19 03:00 | 385 | 379
2018-12-19 03:30 | 382 | 377
2018-12-19 04:00 | 378 | 372
2018-12-19 04:30 | 390 | 384
2018-12-19 05:00 | 401 | 395
2018-12-19 05:30 | 426 | 421
2018-12-19 06:00 | 444 | 440
2018-12-19 06:30 | 486 | 485
2018-12-19 07:00 | 524 | 523
2018-12-19 07:30 | 549 | 548
2018-12-19 08:00 | 570 | 569
2018-12-19 08:30 | 574 | 573
2018-12-19 09:00 | 576 | 576
2018-12-19 09:30 | 592 | 592
2018-12-19 10:00 | 595 | 595
2018-12-19 10:30 | 605 | 605
2018-12-19 11:00 | 608 | 607
2018-12-19 11:30 | 610 | 609
2018-12-19 12:00 | 608 | 607
2018-12-19 12:30 | 612 | 612
2018-12-19 13:00 | 621 | 621
2018-12-19 13:30 | 634 | 633
2018-12-19 14:00 | 649 | 649
2018-12-19 14:30 | 662 | 662
2018-12-19 15:00 | 678 | 677
2018-12-19 15:30 | 696 | 695
2018-12-19 16:00 | 692 | 691
2018-12-19 16:30 | 682 | 680
2018-12-19 17:00 | 683 | 681
2018-12-19 17:30 | 677 | 674
2018-12-19 18:00 | 659 | 657
2018-12-19 18:30 | 638 | 635
2018-12-19 19:00 | 638 | 636
2018-12-19 19:30 | 637 | 635
2018-12-19 20:00 | 623 | 621
2018-12-19 20:30 | 605 | 602
2018-12-19 21:00 | 583 | 580
2018-12-19 21:30 | 561 | 558
2018-12-19 22:00 | 532 | 530
2018-12-19 22:30 | 510 | 508
2018-12-19 23:00 | 483 | 481
2018-12-19 23:30 | 455 | 452
2018-12-20 | 427 | 425
2018-12-20 00:30 | 406 | 403
2018-12-20 01:00 | 392 | 388
2018-12-20 01:30 | 373 | 368
2018-12-20 02:00 | 353 | 348
2018-12-20 02:30 | 345 | 339
2018-12-20 03:00 | 345 | 339
2018-12-20 03:30 | 348 | 341
2018-12-20 04:00 | 347 | 341
2018-12-20 04:30 | 361 | 356
2018-12-20 05:00 | 363 | 357
2018-12-20 05:30 | 385 | 380
2018-12-20 06:00 | 418 | 414
2018-12-20 06:30 | 465 | 463
2018-12-20 07:00 | 508 | 507
2018-12-20 07:30 | 523 | 522
2018-12-20 08:00 | 565 | 560
2018-12-20 08:30 | 589 | 584
2018-12-20 09:00 | 579 | 575
2018-12-20 09:30 | 569 | 565
2018-12-20 10:00 | 585 | 579
2018-12-20 10:30 | 602 | 595
2018-12-20 11:00 | 626 | 617
2018-12-20 11:30 | 632 | 625
2018-12-20 12:00 | 632 | 625
2018-12-20 12:30 | 653 | 647
2018-12-20 13:00 | 656 | 650
2018-12-20 13:30 | 684 | 677
2018-12-20 14:00 | 720 | 712
2018-12-20 14:30 | 753 | 743
2018-12-20 15:00 | 789 | 773
2018-12-20 15:30 | 833 | 814
2018-12-20 16:00 | 832 | 814
2018-12-20 16:30 | 826 | 807
2018-12-20 17:00 | 842 | 824
2018-12-20 17:30 | 832 | 810
2018-12-20 18:00 | 813 | 789
2018-12-20 18:30 | 781 | 755
2018-12-20 19:00 | 757 | 736
2018-12-20 19:30 | 733 | 726
2018-12-20 20:00 | 704 | 698
2018-12-20 20:30 | 669 | 663
2018-12-20 21:00 | 639 | 633
2018-12-20 21:30 | 615 | 609
2018-12-20 22:00 | 581 | 576
2018-12-20 22:30 | 560 | 555
2018-12-20 23:00 | 547 | 540
2018-12-20 23:30 | 518 | 513
2018-12-21 | 485 | 479
2018-12-21 00:30 | 443 | 435
2018-12-21 01:00 | 424 | 416
2018-12-21 01:30 | 405 | 401
2018-12-21 02:00 | 388 | 384
2018-12-21 02:30 | 380 | 375
2018-12-21 03:00 | 385 | 379
2018-12-21 03:30 | 386 | 380
2018-12-21 04:00 | 387 | 382
2018-12-21 04:30 | 385 | 380
2018-12-21 05:00 | 385 | 380
2018-12-21 05:30 | 405 | 400
2018-12-21 06:00 | 438 | 435
2018-12-21 06:30 | 478 | 477
2018-12-21 07:00 | 514 | 513
2018-12-21 07:30 | 532 | 531
2018-12-21 08:00 | 560 | 559
2018-12-21 08:30 | 577 | 575
2018-12-21 09:00 | 601 | 600
2018-12-21 09:30 | 621 | 616
2018-12-21 10:00 | 628 | 624
2018-12-21 10:30 | 649 | 643
2018-12-21 11:00 | 673 | 666
2018-12-21 11:30 | 655 | 649
2018-12-21 12:00 | 662 | 655
2018-12-21 12:30 | 673 | 666
2018-12-21 13:00 | 683 | 674
2018-12-21 13:30 | 699 | 692
2018-12-21 14:00 | 715 | 707
2018-12-21 14:30 | 734 | 728
2018-12-21 15:00 | 758 | 753
2018-12-21 15:30 | 784 | 778
2018-12-21 16:00 | 810 | 800
2018-12-21 16:30 | 834 | 822
2018-12-21 17:00 | 821 | 808
2018-12-21 17:30 | 788 | 771
2018-12-21 18:00 | 719 | 703
2018-12-21 18:30 | 637 | 625
2018-12-21 19:00 | 608 | 599
2018-12-21 19:30 | 596 | 587
2018-12-21 20:00 | 577 | 570
2018-12-21 20:30 | 594 | 588
2018-12-21 21:00 | 595 | 590
2018-12-21 21:30 | 562 | 556
2018-12-21 22:00 | 548 | 541
2018-12-21 22:30 | 519 | 514
2018-12-21 23:00 | 509 | 508
2018-12-21 23:30 | 501 | 500
2018-12-22 | 474 | 472
2018-12-22 00:30 | 435 | 434
2018-12-22 01:00 | 427 | 425
2018-12-22 01:30 | 401 | 399
2018-12-22 02:00 | 378 | 375
2018-12-22 02:30 | 373 | 369
2018-12-22 03:00 | 382 | 378
2018-12-22 03:30 | 373 | 369
2018-12-22 04:00 | 374 | 370
2018-12-22 04:30 | 372 | 367
2018-12-22 05:00 | 365 | 361
2018-12-22 05:30 | 373 | 368
2018-12-22 06:00 | 386 | 381
2018-12-22 06:30 | 405 | 401
2018-12-22 07:00 | 425 | 422
2018-12-22 07:30 | 442 | 440
2018-12-22 08:00 | 439 | 438
2018-12-22 08:30 | 460 | 458
2018-12-22 09:00 | 484 | 481
2018-12-22 09:30 | 507 | 505
2018-12-22 10:00 | 503 | 501
2018-12-22 10:30 | 495 | 494
2018-12-22 11:00 | 487 | 486
2018-12-22 11:30 | 505 | 503
2018-12-22 12:00 | 511 | 510
2018-12-22 12:30 | 519 | 518
2018-12-22 13:00 | 551 | 550
2018-12-22 13:30 | 576 | 575
2018-12-22 14:00 | 602 | 602
2018-12-22 14:30 | 632 | 630
2018-12-22 15:00 | 653 | 651
2018-12-22 15:30 | 674 | 670
2018-12-22 16:00 | 700 | 690
2018-12-22 16:30 | 703 | 692
2018-12-22 17:00 | 688 | 675
2018-12-22 17:30 | 644 | 625
2018-12-22 18:00 | 599 | 585
2018-12-22 18:30 | 576 | 563
2018-12-22 19:00 | 567 | 555
2018-12-22 19:30 | 562 | 552
2018-12-22 20:00 | 563 | 552
2018-12-22 20:30 | 553 | 539
2018-12-22 21:00 | 514 | 510
2018-12-22 21:30 | 506 | 502
2018-12-22 22:00 | 489 | 486
2018-12-22 22:30 | 461 | 459
2018-12-22 23:00 | 443 | 441
2018-12-22 23:30 | 426 | 423
2018-12-23 | 409 | 404
2018-12-23 00:30 | 379 | 372
2018-12-23 01:00 | 361 | 354
2018-12-23 01:30 | 347 | 339
2018-12-23 02:00 | 334 | 325
2018-12-23 02:30 | 326 | 317
2018-12-23 03:00 | 322 | 312
2018-12-23 03:30 | 322 | 312
2018-12-23 04:00 | 320 | 310
2018-12-23 04:30 | 320 | 309
2018-12-23 05:00 | 318 | 307
2018-12-23 05:30 | 321 | 309
2018-12-23 06:00 | 328 | 316
2018-12-23 06:30 | 336 | 324
2018-12-23 07:00 | 347 | 336
2018-12-23 07:30 | 356 | 347
2018-12-23 08:00 | 361 | 354
2018-12-23 08:30 | 361 | 355
2018-12-23 09:00 | 359 | 354
2018-12-23 09:30 | 367 | 363
2018-12-23 10:00 | 375 | 371
2018-12-23 10:30 | 373 | 370
2018-12-23 11:00 | 381 | 379
2018-12-23 11:30 | 388 | 386
2018-12-23 12:00 | 385 | 382
2018-12-23 12:30 | 390 | 385
2018-12-23 13:00 | 385 | 380
2018-12-23 13:30 | 387 | 382
2018-12-23 14:00 | 393 | 388
2018-12-23 14:30 | 391 | 387
2018-12-23 15:00 | 390 | 386
2018-12-23 15:30 | 393 | 389
2018-12-23 16:00 | 402 | 399
2018-12-23 16:30 | 432 | 429
2018-12-23 17:00 | 461 | 458
2018-12-23 17:30 | 480 | 477
2018-12-23 18:00 | 485 | 482
2018-12-23 18:30 | 487 | 484
2018-12-23 19:00 | 493 | 490
2018-12-23 19:30 | 497 | 494
2018-12-23 20:00 | 501 | 498
2018-12-23 20:30 | 494 | 490
2018-12-23 21:00 | 476 | 472
2018-12-23 21:30 | 471 | 465
2018-12-23 22:00 | 459 | 452
2018-12-23 22:30 | 436 | 431
2018-12-23 23:00 | 420 | 415
2018-12-23 23:30 | 399 | 393
2018-12-24 | 379 | 371
2018-12-24 00:30 | 352 | 343
2018-12-24 01:00 | 337 | 326
2018-12-24 01:30 | 324 | 312
2018-12-24 02:00 | 314 | 302
2018-12-24 02:30 | 318 | 305
2018-12-24 03:00 | 318 | 305
2018-12-24 03:30 | 315 | 302
2018-12-24 04:00 | 312 | 298
2018-12-24 04:30 | 322 | 309
2018-12-24 05:00 | 326 | 312
2018-12-24 05:30 | 341 | 326
2018-12-24 06:00 | 354 | 341
2018-12-24 06:30 | 369 | 361
2018-12-24 07:00 | 380 | 373
2018-12-24 07:30 | 400 | 398
2018-12-24 08:00 | 414 | 413
2018-12-24 08:30 | 423 | 422
2018-12-24 09:00 | 432 | 431
2018-12-24 09:30 | 442 | 442
2018-12-24 10:00 | 448 | 447
2018-12-24 10:30 | 463 | 462
2018-12-24 11:00 | 458 | 457
2018-12-24 11:30 | 455 | 454
2018-12-24 12:00 | 456 | 455
2018-12-24 12:30 | 442 | 441
2018-12-24 13:00 | 438 | 437
2018-12-24 13:30 | 448 | 447
2018-12-24 14:00 | 452 | 451
2018-12-24 14:30 | 461 | 460
2018-12-24 15:00 | 465 | 465
2018-12-24 15:30 | 480 | 479
2018-12-24 16:00 | 493 | 492
2018-12-24 16:30 | 519 | 518
2018-12-24 17:00 | 531 | 530
2018-12-24 17:30 | 535 | 534
2018-12-24 18:00 | 523 | 521
2018-12-24 18:30 | 501 | 498
2018-12-24 19:00 | 500 | 496
2018-12-24 19:30 | 499 | 496
2018-12-24 20:00 | 495 | 493
2018-12-24 20:30 | 481 | 480
2018-12-24 21:00 | 462 | 462
2018-12-24 21:30 | 446 | 446
2018-12-24 22:00 | 439 | 438
2018-12-24 22:30 | 425 | 424
2018-12-24 23:00 | 404 | 403
2018-12-24 23:30 | 393 | 391
2018-12-25 | 378 | 374
2018-12-25 00:30 | 358 | 352
2018-12-25 01:00 | 350 | 343
2018-12-25 01:30 | 337 | 329
2018-12-25 02:00 | 329 | 320
2018-12-25 02:30 | 324 | 315
2018-12-25 03:00 | 324 | 313
2018-12-25 03:30 | 322 | 311
2018-12-25 04:00 | 320 | 309
2018-12-25 04:30 | 320 | 307
2018-12-25 05:00 | 317 | 303
2018-12-25 05:30 | 325 | 312
2018-12-25 06:00 | 330 | 317
2018-12-25 06:30 | 339 | 327
2018-12-25 07:00 | 345 | 334
2018-12-25 07:30 | 348 | 339
2018-12-25 08:00 | 352 | 344
2018-12-25 08:30 | 349 | 342
2018-12-25 09:00 | 354 | 348
2018-12-25 09:30 | 360 | 354
2018-12-25 10:00 | 361 | 356
2018-12-25 10:30 | 365 | 360
2018-12-25 11:00 | 361 | 357
2018-12-25 11:30 | 349 | 345
2018-12-25 12:00 | 353 | 350
2018-12-25 12:30 | 349 | 346
2018-12-25 13:00 | 352 | 349
2018-12-25 13:30 | 353 | 350
2018-12-25 14:00 | 353 | 350
2018-12-25 14:30 | 356 | 354
2018-12-25 15:00 | 367 | 364
2018-12-25 15:30 | 380 | 378
2018-12-25 16:00 | 409 | 407
2018-12-25 16:30 | 430 | 428
2018-12-25 17:00 | 463 | 461
2018-12-25 17:30 | 475 | 473
2018-12-25 18:00 | 467 | 465
2018-12-25 18:30 | 447 | 445
2018-12-25 19:00 | 441 | 439
2018-12-25 19:30 | 448 | 446
2018-12-25 20:00 | 450 | 448
2018-12-25 20:30 | 451 | 449
2018-12-25 21:00 | 438 | 436
2018-12-25 21:30 | 426 | 424
2018-12-25 22:00 | 421 | 419
2018-12-25 22:30 | 407 | 404
2018-12-25 23:00 | 402 | 398
2018-12-25 23:30 | 383 | 378
2018-12-26 | 365 | 359
2018-12-26 00:30 | 345 | 336
2018-12-26 01:00 | 336 | 326
2018-12-26 01:30 | 331 | 320
2018-12-26 02:00 | 322 | 311
2018-12-26 02:30 | 320 | 309
2018-12-26 03:00 | 315 | 303
2018-12-26 03:30 | 313 | 301
2018-12-26 04:00 | 315 | 303
2018-12-26 04:30 | 320 | 308
2018-12-26 05:00 | 317 | 304
2018-12-26 05:30 | 321 | 307
2018-12-26 06:00 | 313 | 299
2018-12-26 06:30 | 316 | 303
2018-12-26 07:00 | 323 | 312
2018-12-26 07:30 | 339 | 330
2018-12-26 08:00 | 345 | 337
2018-12-26 08:30 | 353 | 347
2018-12-26 09:00 | 363 | 358
2018-12-26 09:30 | 358 | 354
2018-12-26 10:00 | 357 | 354
2018-12-26 10:30 | 361 | 358
2018-12-26 11:00 | 356 | 353
2018-12-26 11:30 | 352 | 349
2018-12-26 12:00 | 358 | 355
2018-12-26 12:30 | 353 | 350
2018-12-26 13:00 | 355 | 353
2018-12-26 13:30 | 358 | 356
2018-12-26 14:00 | 370 | 368
2018-12-26 14:30 | 390 | 388
2018-12-26 15:00 | 407 | 405
2018-12-26 15:30 | 426 | 426
2018-12-26 16:00 | 454 | 453
2018-12-26 16:30 | 485 | 484
2018-12-26 17:00 | 507 | 507
2018-12-26 17:30 | 521 | 521
2018-12-26 18:00 | 518 | 518
2018-12-26 18:30 | 508 | 507
2018-12-26 19:00 | 498 | 497
2018-12-26 19:30 | 495 | 495
2018-12-26 20:00 | 497 | 497
2018-12-26 20:30 | 488 | 487
2018-12-26 21:00 | 457 | 456
2018-12-26 21:30 | 444 | 443
2018-12-26 22:00 | 431 | 429
2018-12-26 22:30 | 412 | 410
2018-12-26 23:00 | 398 | 395
2018-12-26 23:30 | 383 | 380
2018-12-27 | 376 | 371
2018-12-27 00:30 | 357 | 351
2018-12-27 01:00 | 349 | 341
2018-12-27 01:30 | 342 | 334
2018-12-27 02:00 | 332 | 323
2018-12-27 02:30 | 322 | 313
2018-12-27 03:00 | 313 | 304
2018-12-27 03:30 | 311 | 302
2018-12-27 04:00 | 306 | 297
2018-12-27 04:30 | 309 | 301
2018-12-27 05:00 | 307 | 297
2018-12-27 05:30 | 315 | 306
2018-12-27 06:00 | 325 | 316
2018-12-27 06:30 | 341 | 335
2018-12-27 07:00 | 359 | 356
2018-12-27 07:30 | 385 | 384
2018-12-27 08:00 | 404 | 403
2018-12-27 08:30 | 430 | 429
2018-12-27 09:00 | 446 | 446
2018-12-27 09:30 | 452 | 451
2018-12-27 10:00 | 452 | 450
2018-12-27 10:30 | 458 | 457
2018-12-27 11:00 | 453 | 452
2018-12-27 11:30 | 444 | 443
2018-12-27 12:00 | 441 | 440
2018-12-27 12:30 | 442 | 441
2018-12-27 13:00 | 453 | 452
2018-12-27 13:30 | 458 | 458
2018-12-27 14:00 | 480 | 479
2018-12-27 14:30 | 490 | 489
2018-12-27 15:00 | 506 | 505
2018-12-27 15:30 | 526 | 526
2018-12-27 16:00 | 543 | 542
2018-12-27 16:30 | 577 | 576
2018-12-27 17:00 | 589 | 588
2018-12-27 17:30 | 595 | 594
2018-12-27 18:00 | 585 | 583
2018-12-27 18:30 | 563 | 560
2018-12-27 19:00 | 543 | 541
2018-12-27 19:30 | 535 | 534
2018-12-27 20:00 | 528 | 526
2018-12-27 20:30 | 510 | 509
2018-12-27 21:00 | 489 | 488
2018-12-27 21:30 | 468 | 467
2018-12-27 22:00 | 438 | 437
2018-12-27 22:30 | 435 | 434
2018-12-27 23:00 | 427 | 426
2018-12-27 23:30 | 409 | 408
2018-12-28 | 386 | 384
2018-12-28 00:30 | 369 | 365
2018-12-28 01:00 | 361 | 356
2018-12-28 01:30 | 353 | 348
2018-12-28 02:00 | 344 | 338
2018-12-28 02:30 | 335 | 329
2018-12-28 03:00 | 325 | 319
2018-12-28 03:30 | 320 | 314
2018-12-28 04:00 | 319 | 312
2018-12-28 04:30 | 324 | 318
2018-12-28 05:00 | 326 | 320
2018-12-28 05:30 | 341 | 334
2018-12-28 06:00 | 362 | 356
2018-12-28 06:30 | 386 | 382
2018-12-28 07:00 | 403 | 399
2018-12-28 07:30 | 436 | 434
2018-12-28 08:00 | 450 | 448
2018-12-28 08:30 | 469 | 468
2018-12-28 09:00 | 476 | 475
2018-12-28 09:30 | 483 | 482
2018-12-28 10:00 | 486 | 485
2018-12-28 10:30 | 485 | 484
2018-12-28 11:00 | 478 | 477
2018-12-28 11:30 | 471 | 470
2018-12-28 12:00 | 474 | 473
2018-12-28 12:30 | 477 | 476
2018-12-28 13:00 | 488 | 487
2018-12-28 13:30 | 498 | 496
2018-12-28 14:00 | 512 | 510
2018-12-28 14:30 | 526 | 525
2018-12-28 15:00 | 543 | 542
2018-12-28 15:30 | 562 | 561
2018-12-28 16:00 | 575 | 574
2018-12-28 16:30 | 597 | 597
2018-12-28 17:00 | 613 | 613
2018-12-28 17:30 | 610 | 610
2018-12-28 18:00 | 590 | 589
2018-12-28 18:30 | 566 | 564
2018-12-28 19:00 | 559 | 556
2018-12-28 19:30 | 560 | 558
2018-12-28 20:00 | 549 | 547
2018-12-28 20:30 | 522 | 522
2018-12-28 21:00 | 500 | 500
2018-12-28 21:30 | 486 | 485
2018-12-28 22:00 | 471 | 470
2018-12-28 22:30 | 445 | 443
2018-12-28 23:00 | 423 | 421
2018-12-28 23:30 | 406 | 402
2018-12-29 | 390 | 385
2018-12-29 00:30 | 381 | 375
2018-12-29 01:00 | 364 | 357
2018-12-29 01:30 | 350 | 343
2018-12-29 02:00 | 335 | 327
2018-12-29 02:30 | 325 | 317
2018-12-29 03:00 | 317 | 308
2018-12-29 03:30 | 318 | 309
2018-12-29 04:00 | 324 | 315
2018-12-29 04:30 | 315 | 307
2018-12-29 05:00 | 313 | 304
2018-12-29 05:30 | 309 | 298
2018-12-29 06:00 | 337 | 327
2018-12-29 06:30 | 353 | 345
2018-12-29 07:00 | 364 | 358
2018-12-29 07:30 | 380 | 375
2018-12-29 08:00 | 383 | 380
2018-12-29 08:30 | 395 | 393
2018-12-29 09:00 | 408 | 407
2018-12-29 09:30 | 421 | 420
2018-12-29 10:00 | 418 | 417
2018-12-29 10:30 | 423 | 422
2018-12-29 11:00 | 408 | 407
2018-12-29 11:30 | 408 | 407
2018-12-29 12:00 | 413 | 413
2018-12-29 12:30 | 415 | 415
2018-12-29 13:00 | 428 | 428
2018-12-29 13:30 | 436 | 436
2018-12-29 14:00 | 443 | 443
2018-12-29 14:30 | 457 | 457
2018-12-29 15:00 | 471 | 471
2018-12-29 15:30 | 487 | 486
2018-12-29 16:00 | 505 | 504
2018-12-29 16:30 | 536 | 534
2018-12-29 17:00 | 543 | 541
2018-12-29 17:30 | 545 | 542
2018-12-29 18:00 | 539 | 536
2018-12-29 18:30 | 530 | 527
2018-12-29 19:00 | 527 | 524
2018-12-29 19:30 | 532 | 530
2018-12-29 20:00 | 533 | 531
2018-12-29 20:30 | 528 | 526
2018-12-29 21:00 | 507 | 507
2018-12-29 21:30 | 487 | 487
2018-12-29 22:00 | 480 | 479
2018-12-29 22:30 | 477 | 476
2018-12-29 23:00 | 449 | 448
2018-12-29 23:30 | 419 | 418
2018-12-30 | 398 | 396
2018-12-30 00:30 | 377 | 375
2018-12-30 01:00 | 376 | 373
2018-12-30 01:30 | 366 | 363
2018-12-30 02:00 | 354 | 350
2018-12-30 02:30 | 345 | 341
2018-12-30 03:00 | 343 | 338
2018-12-30 03:30 | 335 | 330
2018-12-30 04:00 | 326 | 321
2018-12-30 04:30 | 315 | 309
2018-12-30 05:00 | 307 | 300
2018-12-30 05:30 | 313 | 305
2018-12-30 06:00 | 316 | 307
2018-12-30 06:30 | 329 | 322
2018-12-30 07:00 | 352 | 347
2018-12-30 07:30 | 369 | 365
2018-12-30 08:00 | 378 | 376
2018-12-30 08:30 | 386 | 384
2018-12-30 09:00 | 402 | 401
2018-12-30 09:30 | 415 | 414
2018-12-30 10:00 | 426 | 425
2018-12-30 10:30 | 431 | 431
2018-12-30 11:00 | 433 | 432
2018-12-30 11:30 | 431 | 430
2018-12-30 12:00 | 436 | 436
2018-12-30 12:30 | 444 | 444
2018-12-30 13:00 | 457 | 457
2018-12-30 13:30 | 463 | 461
2018-12-30 14:00 | 475 | 474
2018-12-30 14:30 | 489 | 487
2018-12-30 15:00 | 508 | 507
2018-12-30 15:30 | 524 | 523
2018-12-30 16:00 | 530 | 530
2018-12-30 16:30 | 545 | 544
2018-12-30 17:00 | 560 | 559
2018-12-30 17:30 | 572 | 568
2018-12-30 18:00 | 572 | 567
2018-12-30 18:30 | 558 | 553
2018-12-30 19:00 | 552 | 546
2018-12-30 19:30 | 548 | 543
2018-12-30 20:00 | 549 | 543
2018-12-30 20:30 | 530 | 525
2018-12-30 21:00 | 507 | 503
2018-12-30 21:30 | 487 | 486
2018-12-30 22:00 | 476 | 475
2018-12-30 22:30 | 458 | 458
2018-12-30 23:00 | 442 | 441
2018-12-30 23:30 | 423 | 422
2018-12-31 | 402 | 400
2018-12-31 00:30 | 378 | 375
2018-12-31 01:00 | 368 | 364
2018-12-31 01:30 | 358 | 354
2018-12-31 02:00 | 349 | 345
2018-12-31 02:30 | 348 | 344
2018-12-31 03:00 | 338 | 333
2018-12-31 03:30 | 336 | 331
2018-12-31 04:00 | 332 | 327
2018-12-31 04:30 | 337 | 332
2018-12-31 05:00 | 345 | 340
2018-12-31 05:30 | 359 | 354
2018-12-31 06:00 | 369 | 364
2018-12-31 06:30 | 391 | 388
2018-12-31 07:00 | 413 | 411
2018-12-31 07:30 | 444 | 442
2018-12-31 08:00 | 464 | 457
2018-12-31 08:30 | 472 | 466
2018-12-31 09:00 | 477 | 471
2018-12-31 09:30 | 493 | 488
2018-12-31 10:00 | 500 | 492
2018-12-31 10:30 | 506 | 499
2018-12-31 11:00 | 518 | 511
2018-12-31 11:30 | 527 | 518
2018-12-31 12:00 | 520 | 511
2018-12-31 12:30 | 518 | 509
2018-12-31 13:00 | 514 | 506
2018-12-31 13:30 | 517 | 510
2018-12-31 14:00 | 522 | 515
2018-12-31 14:30 | 539 | 533
2018-12-31 15:00 | 550 | 546
2018-12-31 15:30 | 559 | 555
2018-12-31 16:00 | 566 | 563
2018-12-31 16:30 | 580 | 576
2018-12-31 17:00 | 595 | 589
2018-12-31 17:30 | 592 | 585
2018-12-31 18:00 | 576 | 568
2018-12-31 18:30 | 547 | 537
2018-12-31 19:00 | 534 | 525
2018-12-31 19:30 | 523 | 516
2018-12-31 20:00 | 514 | 508
2018-12-31 20:30 | 502 | 495
2018-12-31 21:00 | 484 | 482
2018-12-31 21:30 | 478 | 476
2018-12-31 22:00 | 469 | 467
2018-12-31 22:30 | 452 | 449
2018-12-31 23:00 | 426 | 426
2018-12-31 23:30 | 412 | 412
2019-01-01 | 396 | 395
2019-01-01 00:30 | 373 | 371
2019-01-01 01:00 | 367 | 365
2019-01-01 01:30 | 362 | 360
2019-01-01 02:00 | 353 | 350
2019-01-01 02:30 | 343 | 340
2019-01-01 03:00 | 340 | 335
2019-01-01 03:30 | 329 | 325
2019-01-01 04:00 | 318 | 313
2019-01-01 04:30 | 311 | 305
2019-01-01 05:00 | 309 | 302
2019-01-01 05:30 | 307 | 296
2019-01-01 06:00 | 312 | 300
2019-01-01 06:30 | 319 | 309
2019-01-01 07:00 | 331 | 322
2019-01-01 07:30 | 349 | 342
2019-01-01 08:00 | 361 | 355
2019-01-01 08:30 | 381 | 378
2019-01-01 09:00 | 384 | 380
2019-01-01 09:30 | 388 | 385
2019-01-01 10:00 | 390 | 387
2019-01-01 10:30 | 403 | 401
2019-01-01 11:00 | 412 | 410
2019-01-01 11:30 | 431 | 428
2019-01-01 12:00 | 442 | 440
2019-01-01 12:30 | 455 | 453
2019-01-01 13:00 | 468 | 465
2019-01-01 13:30 | 483 | 480
2019-01-01 14:00 | 494 | 492
2019-01-01 14:30 | 505 | 503
2019-01-01 15:00 | 517 | 516
2019-01-01 15:30 | 527 | 526
2019-01-01 16:00 | 550 | 550
2019-01-01 16:30 | 557 | 556
2019-01-01 17:00 | 548 | 548
2019-01-01 17:30 | 547 | 547
2019-01-01 18:00 | 543 | 542
2019-01-01 18:30 | 522 | 521
2019-01-01 19:00 | 521 | 520
2019-01-01 19:30 | 517 | 516
2019-01-01 20:00 | 510 | 509
2019-01-01 20:30 | 506 | 505
2019-01-01 21:00 | 486 | 484
2019-01-01 21:30 | 478 | 475
2019-01-01 22:00 | 463 | 459
2019-01-01 22:30 | 446 | 442
2019-01-01 23:00 | 424 | 419
2019-01-01 23:30 | 399 | 396
2019-01-02 | 383 | 379
2019-01-02 00:30 | 359 | 353
2019-01-02 01:00 | 347 | 340
2019-01-02 01:30 | 331 | 323
2019-01-02 02:00 | 323 | 314
2019-01-02 02:30 | 322 | 313
2019-01-02 03:00 | 323 | 313
2019-01-02 03:30 | 319 | 309
2019-01-02 04:00 | 314 | 304
2019-01-02 04:30 | 319 | 310
2019-01-02 05:00 | 323 | 314
2019-01-02 05:30 | 343 | 334
2019-01-02 06:00 | 366 | 359
2019-01-02 06:30 | 386 | 382
2019-01-02 07:00 | 404 | 402
2019-01-02 07:30 | 435 | 434
2019-01-02 08:00 | 455 | 453
2019-01-02 08:30 | 466 | 465
2019-01-02 09:00 | 487 | 486
2019-01-02 09:30 | 494 | 493
2019-01-02 10:00 | 505 | 503
2019-01-02 10:30 | 521 | 519
2019-01-02 11:00 | 527 | 525
2019-01-02 11:30 | 521 | 519
2019-01-02 12:00 | 529 | 527
2019-01-02 12:30 | 542 | 540
2019-01-02 13:00 | 557 | 556
2019-01-02 13:30 | 563 | 561
2019-01-02 14:00 | 568 | 567
2019-01-02 14:30 | 573 | 572
2019-01-02 15:00 | 579 | 578
2019-01-02 15:30 | 586 | 586
2019-01-02 16:00 | 589 | 589
2019-01-02 16:30 | 599 | 598
2019-01-02 17:00 | 616 | 615
2019-01-02 17:30 | 610 | 609
2019-01-02 18:00 | 593 | 590
2019-01-02 18:30 | 568 | 565
2019-01-02 19:00 | 560 | 559
2019-01-02 19:30 | 549 | 547
2019-01-02 20:00 | 547 | 546
2019-01-02 20:30 | 543 | 542
2019-01-02 21:00 | 518 | 518
2019-01-02 21:30 | 502 | 501
2019-01-02 22:00 | 486 | 483
2019-01-02 22:30 | 469 | 466
2019-01-02 23:00 | 456 | 451
2019-01-02 23:30 | 429 | 425
2019-01-03 | 404 | 401
2019-01-03 00:30 | 369 | 365
2019-01-03 01:00 | 362 | 357
2019-01-03 01:30 | 356 | 349
2019-01-03 02:00 | 347 | 340
2019-01-03 02:30 | 347 | 340
2019-01-03 03:00 | 342 | 334
2019-01-03 03:30 | 338 | 330
2019-01-03 04:00 | 334 | 326
2019-01-03 04:30 | 332 | 324
2019-01-03 05:00 | 339 | 332
2019-01-03 05:30 | 352 | 345
2019-01-03 06:00 | 374 | 367
2019-01-03 06:30 | 395 | 391
2019-01-03 07:00 | 427 | 424
2019-01-03 07:30 | 451 | 450
2019-01-03 08:00 | 461 | 460
2019-01-03 08:30 | 471 | 469
2019-01-03 09:00 | 477 | 476
2019-01-03 09:30 | 497 | 496
2019-01-03 10:00 | 519 | 518
2019-01-03 10:30 | 549 | 547
2019-01-03 11:00 | 565 | 564
2019-01-03 11:30 | 565 | 564
2019-01-03 12:00 | 565 | 564
2019-01-03 12:30 | 531 | 529
2019-01-03 13:00 | 526 | 524
2019-01-03 13:30 | 543 | 542
2019-01-03 14:00 | 542 | 541
2019-01-03 14:30 | 557 | 556
2019-01-03 15:00 | 574 | 573
2019-01-03 15:30 | 574 | 573
2019-01-03 16:00 | 585 | 584
2019-01-03 16:30 | 583 | 582
2019-01-03 17:00 | 591 | 590
2019-01-03 17:30 | 589 | 588
2019-01-03 18:00 | 578 | 577
2019-01-03 18:30 | 561 | 559
2019-01-03 19:00 | 555 | 553
2019-01-03 19:30 | 562 | 561
2019-01-03 20:00 | 567 | 565
2019-01-03 20:30 | 551 | 549
2019-01-03 21:00 | 517 | 516
2019-01-03 21:30 | 507 | 505
2019-01-03 22:00 | 492 | 488
2019-01-03 22:30 | 479 | 477
2019-01-03 23:00 | 466 | 464
2019-01-03 23:30 | 438 | 435
2019-01-04 | 411 | 407
2019-01-04 00:30 | 379 | 375
2019-01-04 01:00 | 374 | 369
2019-01-04 01:30 | 361 | 355
2019-01-04 02:00 | 348 | 342
2019-01-04 02:30 | 343 | 337
2019-01-04 03:00 | 341 | 335
2019-01-04 03:30 | 329 | 323
2019-01-04 04:00 | 333 | 327
2019-01-04 04:30 | 339 | 333
2019-01-04 05:00 | 339 | 333
2019-01-04 05:30 | 360 | 355
2019-01-04 06:00 | 371 | 366
2019-01-04 06:30 | 415 | 412
2019-01-04 07:00 | 439 | 438
2019-01-04 07:30 | 463 | 463
2019-01-04 08:00 | 492 | 490
2019-01-04 08:30 | 508 | 507
2019-01-04 09:00 | 520 | 518
2019-01-04 09:30 | 527 | 525
2019-01-04 10:00 | 526 | 524
2019-01-04 10:30 | 520 | 518
2019-01-04 11:00 | 516 | 514
2019-01-04 11:30 | 517 | 515
2019-01-04 12:00 | 527 | 526
2019-01-04 12:30 | 538 | 536
2019-01-04 13:00 | 547 | 546
2019-01-04 13:30 | 554 | 553
2019-01-04 14:00 | 564 | 563
2019-01-04 14:30 | 597 | 596
2019-01-04 15:00 | 605 | 605
2019-01-04 15:30 | 597 | 597
2019-01-04 16:00 | 604 | 604
2019-01-04 16:30 | 619 | 619
2019-01-04 17:00 | 623 | 623
2019-01-04 17:30 | 612 | 612
2019-01-04 18:00 | 597 | 596
2019-01-04 18:30 | 568 | 566
2019-01-04 19:00 | 574 | 571
2019-01-04 19:30 | 576 | 574
2019-01-04 20:00 | 574 | 572
2019-01-04 20:30 | 556 | 555
2019-01-04 21:00 | 528 | 528
2019-01-04 21:30 | 510 | 509
2019-01-04 22:00 | 507 | 504
2019-01-04 22:30 | 499 | 496
2019-01-04 23:00 | 480 | 478
2019-01-04 23:30 | 468 | 465
2019-01-05 | 448 | 444
2019-01-05 00:30 | 407 | 403
2019-01-05 01:00 | 382 | 378
2019-01-05 01:30 | 360 | 355
2019-01-05 02:00 | 354 | 348
2019-01-05 02:30 | 353 | 347
2019-01-05 03:00 | 344 | 337
2019-01-05 03:30 | 346 | 339
2019-01-05 04:00 | 341 | 333
2019-01-05 04:30 | 339 | 331
2019-01-05 05:00 | 341 | 332
2019-01-05 05:30 | 353 | 342
2019-01-05 06:00 | 350 | 340
2019-01-05 06:30 | 364 | 356
2019-01-05 07:00 | 386 | 378
2019-01-05 07:30 | 416 | 410
2019-01-05 08:00 | 428 | 424
2019-01-05 08:30 | 446 | 444
2019-01-05 09:00 | 463 | 462
2019-01-05 09:30 | 469 | 468
2019-01-05 10:00 | 475 | 474
2019-01-05 10:30 | 478 | 477
2019-01-05 11:00 | 479 | 478
2019-01-05 11:30 | 481 | 480
2019-01-05 12:00 | 489 | 488
2019-01-05 12:30 | 492 | 492
2019-01-05 13:00 | 494 | 494
2019-01-05 13:30 | 514 | 513
2019-01-05 14:00 | 517 | 517
2019-01-05 14:30 | 521 | 521
2019-01-05 15:00 | 537 | 537
2019-01-05 15:30 | 549 | 548
2019-01-05 16:00 | 561 | 559
2019-01-05 16:30 | 563 | 562
2019-01-05 17:00 | 572 | 571
2019-01-05 17:30 | 566 | 563
2019-01-05 18:00 | 542 | 540
2019-01-05 18:30 | 533 | 530
2019-01-05 19:00 | 544 | 540
2019-01-05 19:30 | 544 | 541
2019-01-05 20:00 | 536 | 534
2019-01-05 20:30 | 536 | 533
2019-01-05 21:00 | 507 | 506
2019-01-05 21:30 | 501 | 499
2019-01-05 22:00 | 501 | 498
2019-01-05 22:30 | 481 | 477
2019-01-05 23:00 | 457 | 455
2019-01-05 23:30 | 434 | 432
2019-01-06 | 410 | 408
2019-01-06 00:30 | 375 | 371
2019-01-06 01:00 | 362 | 358
2019-01-06 01:30 | 358 | 354
2019-01-06 02:00 | 345 | 339
2019-01-06 02:30 | 338 | 332
2019-01-06 03:00 | 331 | 325
2019-01-06 03:30 | 332 | 326
2019-01-06 04:00 | 332 | 326
2019-01-06 04:30 | 336 | 329
2019-01-06 05:00 | 331 | 324
2019-01-06 05:30 | 330 | 322
2019-01-06 06:00 | 323 | 315
2019-01-06 06:30 | 330 | 322
2019-01-06 07:00 | 344 | 337
2019-01-06 07:30 | 365 | 360
2019-01-06 08:00 | 379 | 375
2019-01-06 08:30 | 384 | 381
2019-01-06 09:00 | 390 | 388
2019-01-06 09:30 | 403 | 400
2019-01-06 10:00 | 418 | 417
2019-01-06 10:30 | 432 | 431
2019-01-06 11:00 | 442 | 440
2019-01-06 11:30 | 444 | 443
2019-01-06 12:00 | 454 | 452
2019-01-06 12:30 | 459 | 455
2019-01-06 13:00 | 464 | 461
2019-01-06 13:30 | 476 | 473
2019-01-06 14:00 | 479 | 477
2019-01-06 14:30 | 489 | 487
2019-01-06 15:00 | 499 | 498
2019-01-06 15:30 | 507 | 506
2019-01-06 16:00 | 519 | 518
2019-01-06 16:30 | 517 | 516
2019-01-06 17:00 | 530 | 530
2019-01-06 17:30 | 530 | 530
2019-01-06 18:00 | 521 | 520
2019-01-06 18:30 | 523 | 522
2019-01-06 19:00 | 528 | 528
2019-01-06 19:30 | 530 | 530
2019-01-06 20:00 | 529 | 529
2019-01-06 20:30 | 529 | 528
2019-01-06 21:00 | 503 | 502
2019-01-06 21:30 | 488 | 486
2019-01-06 22:00 | 469 | 467
2019-01-06 22:30 | 452 | 449
2019-01-06 23:00 | 435 | 433
2019-01-06 23:30 | 409 | 407
2019-01-07 | 388 | 383
2019-01-07 00:30 | 362 | 357
2019-01-07 01:00 | 357 | 350
2019-01-07 01:30 | 346 | 338
2019-01-07 02:00 | 339 | 331
2019-01-07 02:30 | 335 | 330
2019-01-07 03:00 | 333 | 328
2019-01-07 03:30 | 334 | 329
2019-01-07 04:00 | 335 | 331
2019-01-07 04:30 | 343 | 339
2019-01-07 05:00 | 358 | 354
2019-01-07 05:30 | 369 | 366
2019-01-07 06:00 | 384 | 382
2019-01-07 06:30 | 418 | 417
2019-01-07 07:00 | 450 | 449
2019-01-07 07:30 | 480 | 480
2019-01-07 08:00 | 503 | 502
2019-01-07 08:30 | 522 | 522
2019-01-07 09:00 | 532 | 532
2019-01-07 09:30 | 529 | 529
2019-01-07 10:00 | 537 | 537
2019-01-07 10:30 | 532 | 532
2019-01-07 11:00 | 524 | 524
2019-01-07 11:30 | 526 | 526
2019-01-07 12:00 | 541 | 541
2019-01-07 12:30 | 547 | 547
2019-01-07 13:00 | 571 | 571
2019-01-07 13:30 | 598 | 598
2019-01-07 14:00 | 600 | 600
2019-01-07 14:30 | 597 | 597
2019-01-07 15:00 | 594 | 594
2019-01-07 15:30 | 594 | 594
2019-01-07 16:00 | 598 | 597
2019-01-07 16:30 | 587 | 586
2019-01-07 17:00 | 585 | 584
2019-01-07 17:30 | 575 | 573
2019-01-07 18:00 | 559 | 558
2019-01-07 18:30 | 536 | 536
2019-01-07 19:00 | 531 | 531
2019-01-07 19:30 | 531 | 531
2019-01-07 20:00 | 533 | 533
2019-01-07 20:30 | 517 | 517
2019-01-07 21:00 | 497 | 497
2019-01-07 21:30 | 480 | 479
2019-01-07 22:00 | 463 | 463
2019-01-07 22:30 | 447 | 447
2019-01-07 23:00 | 435 | 435
2019-01-07 23:30 | 419 | 418
2019-01-08 | 393 | 392
2019-01-08 00:30 | 372 | 370
2019-01-08 01:00 | 368 | 366
2019-01-08 01:30 | 364 | 362
2019-01-08 02:00 | 353 | 351
2019-01-08 02:30 | 344 | 342
2019-01-08 03:00 | 343 | 340
2019-01-08 03:30 | 343 | 340
2019-01-08 04:00 | 347 | 344
2019-01-08 04:30 | 347 | 344
2019-01-08 05:00 | 348 | 346
2019-01-08 05:30 | 360 | 358
2019-01-08 06:00 | 378 | 376
2019-01-08 06:30 | 417 | 417
2019-01-08 07:00 | 459 | 459
2019-01-08 07:30 | 492 | 492
2019-01-08 08:00 | 514 | 514
2019-01-08 08:30 | 530 | 530
2019-01-08 09:00 | 545 | 544
2019-01-08 09:30 | 546 | 546
2019-01-08 10:00 | 550 | 550
2019-01-08 10:30 | 508 | 508
2019-01-08 11:00 | 480 | 480
2019-01-08 11:30 | 479 | 479
2019-01-08 12:00 | 502 | 502
2019-01-08 12:30 | 529 | 529
2019-01-08 13:00 | 548 | 548
2019-01-08 13:30 | 561 | 561
2019-01-08 14:00 | 570 | 570
2019-01-08 14:30 | 561 | 561
2019-01-08 15:00 | 571 | 571
2019-01-08 15:30 | 584 | 584
2019-01-08 16:00 | 585 | 585
2019-01-08 16:30 | 585 | 584
2019-01-08 17:00 | 595 | 595
2019-01-08 17:30 | 597 | 597
2019-01-08 18:00 | 590 | 589
2019-01-08 18:30 | 567 | 566
2019-01-08 19:00 | 572 | 572
2019-01-08 19:30 | 572 | 571
2019-01-08 20:00 | 571 | 570
2019-01-08 20:30 | 562 | 561
2019-01-08 21:00 | 530 | 530
2019-01-08 21:30 | 508 | 508
2019-01-08 22:00 | 495 | 494
2019-01-08 22:30 | 481 | 481
2019-01-08 23:00 | 470 | 469
2019-01-08 23:30 | 441 | 440
2019-01-09 | 413 | 413
2019-01-09 00:30 | 384 | 383
2019-01-09 01:00 | 370 | 369
2019-01-09 01:30 | 351 | 349
2019-01-09 02:00 | 337 | 336
2019-01-09 02:30 | 344 | 342
2019-01-09 03:00 | 338 | 336
2019-01-09 03:30 | 338 | 336
2019-01-09 04:00 | 345 | 343
2019-01-09 04:30 | 359 | 357
2019-01-09 05:00 | 366 | 364
2019-01-09 05:30 | 376 | 374
2019-01-09 06:00 | 388 | 387
2019-01-09 06:30 | 415 | 415
2019-01-09 07:00 | 452 | 452
2019-01-09 07:30 | 495 | 495
2019-01-09 08:00 | 521 | 521
2019-01-09 08:30 | 546 | 546
2019-01-09 09:00 | 554 | 553
2019-01-09 09:30 | 559 | 559
2019-01-09 10:00 | 560 | 560
2019-01-09 10:30 | 575 | 574
2019-01-09 11:00 | 578 | 578
2019-01-09 11:30 | 581 | 581
2019-01-09 12:00 | 573 | 573
2019-01-09 12:30 | 566 | 566
2019-01-09 13:00 | 592 | 591
2019-01-09 13:30 | 595 | 593
2019-01-09 14:00 | 580 | 578
2019-01-09 14:30 | 579 | 578
2019-01-09 15:00 | 585 | 584
2019-01-09 15:30 | 600 | 599
2019-01-09 16:00 | 612 | 611
2019-01-09 16:30 | 602 | 601
2019-01-09 17:00 | 611 | 610
2019-01-09 17:30 | 609 | 608
2019-01-09 18:00 | 583 | 581
2019-01-09 18:30 | 567 | 566
2019-01-09 19:00 | 580 | 579
2019-01-09 19:30 | 580 | 580
2019-01-09 20:00 | 575 | 574
2019-01-09 20:30 | 558 | 557
2019-01-09 21:00 | 535 | 534
2019-01-09 21:30 | 509 | 508
2019-01-09 22:00 | 492 | 490
2019-01-09 22:30 | 479 | 478
2019-01-09 23:00 | 470 | 470
2019-01-09 23:30 | 449 | 447
2019-01-10 | 424 | 422
2019-01-10 00:30 | 398 | 396
2019-01-10 01:00 | 379 | 377
2019-01-10 01:30 | 364 | 361
2019-01-10 02:00 | 352 | 350
2019-01-10 02:30 | 352 | 351
2019-01-10 03:00 | 348 | 346
2019-01-10 03:30 | 345 | 343
2019-01-10 04:00 | 340 | 338
2019-01-10 04:30 | 341 | 339
2019-01-10 05:00 | 355 | 353
2019-01-10 05:30 | 362 | 361
2019-01-10 06:00 | 379 | 378
2019-01-10 06:30 | 423 | 423
2019-01-10 07:00 | 473 | 473
2019-01-10 07:30 | 498 | 498
2019-01-10 08:00 | 492 | 492
2019-01-10 08:30 | 495 | 495
2019-01-10 09:00 | 519 | 519
2019-01-10 09:30 | 537 | 537
2019-01-10 10:00 | 545 | 545
2019-01-10 10:30 | 557 | 557
2019-01-10 11:00 | 553 | 552
2019-01-10 11:30 | 559 | 559
2019-01-10 12:00 | 565 | 565
2019-01-10 12:30 | 560 | 560
2019-01-10 13:00 | 566 | 566
2019-01-10 13:30 | 561 | 561
2019-01-10 14:00 | 564 | 564
2019-01-10 14:30 | 553 | 553
2019-01-10 15:00 | 554 | 554
2019-01-10 15:30 | 565 | 565
2019-01-10 16:00 | 581 | 581
2019-01-10 16:30 | 599 | 599
2019-01-10 17:00 | 617 | 616
2019-01-10 17:30 | 619 | 618
2019-01-10 18:00 | 615 | 614
2019-01-10 18:30 | 600 | 597
2019-01-10 19:00 | 600 | 598
2019-01-10 19:30 | 610 | 608
2019-01-10 20:00 | 607 | 605
2019-01-10 20:30 | 592 | 589
2019-01-10 21:00 | 566 | 563
2019-01-10 21:30 | 537 | 533
2019-01-10 22:00 | 507 | 502
2019-01-10 22:30 | 496 | 492
2019-01-10 23:00 | 475 | 473
2019-01-10 23:30 | 447 | 444
2019-01-11 | 416 | 413
2019-01-11 00:30 | 382 | 379
2019-01-11 01:00 | 373 | 369
2019-01-11 01:30 | 363 | 359
2019-01-11 02:00 | 356 | 352
2019-01-11 02:30 | 352 | 349
2019-01-11 03:00 | 350 | 346
2019-01-11 03:30 | 334 | 330
2019-01-11 04:00 | 334 | 329
2019-01-11 04:30 | 341 | 336
2019-01-11 05:00 | 353 | 349
2019-01-11 05:30 | 374 | 371
2019-01-11 06:00 | 383 | 380
2019-01-11 06:30 | 412 | 411
2019-01-11 07:00 | 436 | 436
2019-01-11 07:30 | 466 | 465
2019-01-11 08:00 | 480 | 480
2019-01-11 08:30 | 497 | 496
2019-01-11 09:00 | 501 | 501
2019-01-11 09:30 | 514 | 513
2019-01-11 10:00 | 534 | 533
2019-01-11 10:30 | 536 | 536
2019-01-11 11:00 | 539 | 539
2019-01-11 11:30 | 547 | 547
2019-01-11 12:00 | 553 | 553
2019-01-11 12:30 | 552 | 552
2019-01-11 13:00 | 558 | 558
2019-01-11 13:30 | 596 | 592
2019-01-11 14:00 | 602 | 597
2019-01-11 14:30 | 602 | 597
2019-01-11 15:00 | 619 | 614
2019-01-11 15:30 | 618 | 613
2019-01-11 16:00 | 609 | 604
2019-01-11 16:30 | 605 | 601
2019-01-11 17:00 | 607 | 604
2019-01-11 17:30 | 607 | 603
2019-01-11 18:00 | 593 | 587
2019-01-11 18:30 | 567 | 561
2019-01-11 19:00 | 563 | 558
2019-01-11 19:30 | 559 | 554
2019-01-11 20:00 | 551 | 546
2019-01-11 20:30 | 529 | 526
2019-01-11 21:00 | 508 | 507
2019-01-11 21:30 | 504 | 502
2019-01-11 22:00 | 479 | 478
2019-01-11 22:30 | 445 | 444
2019-01-11 23:00 | 434 | 431
2019-01-11 23:30 | 407 | 404
2019-01-12 | 384 | 381
2019-01-12 00:30 | 358 | 355
2019-01-12 01:00 | 350 | 346
2019-01-12 01:30 | 343 | 338
2019-01-12 02:00 | 340 | 335
2019-01-12 02:30 | 323 | 318
2019-01-12 03:00 | 316 | 311
2019-01-12 03:30 | 329 | 323
2019-01-12 04:00 | 337 | 331
2019-01-12 04:30 | 336 | 329
2019-01-12 05:00 | 334 | 328
2019-01-12 05:30 | 334 | 327
2019-01-12 06:00 | 335 | 328
2019-01-12 06:30 | 345 | 339
2019-01-12 07:00 | 372 | 367
2019-01-12 07:30 | 393 | 389
2019-01-12 08:00 | 407 | 405
2019-01-12 08:30 | 426 | 425
2019-01-12 09:00 | 431 | 430
2019-01-12 09:30 | 439 | 438
2019-01-12 10:00 | 434 | 433
2019-01-12 10:30 | 437 | 436
2019-01-12 11:00 | 444 | 443
2019-01-12 11:30 | 445 | 445
2019-01-12 12:00 | 455 | 453
2019-01-12 12:30 | 461 | 460
2019-01-12 13:00 | 482 | 481
2019-01-12 13:30 | 492 | 490
2019-01-12 14:00 | 495 | 494
2019-01-12 14:30 | 506 | 505
2019-01-12 15:00 | 527 | 526
2019-01-12 15:30 | 543 | 543
2019-01-12 16:00 | 563 | 562
2019-01-12 16:30 | 585 | 583
2019-01-12 17:00 | 615 | 614
2019-01-12 17:30 | 595 | 593
2019-01-12 18:00 | 592 | 590
2019-01-12 18:30 | 570 | 569
2019-01-12 19:00 | 580 | 578
2019-01-12 19:30 | 580 | 578
2019-01-12 20:00 | 573 | 572
2019-01-12 20:30 | 553 | 552
2019-01-12 21:00 | 526 | 525
2019-01-12 21:30 | 502 | 501
2019-01-12 22:00 | 478 | 477
2019-01-12 22:30 | 451 | 449
2019-01-12 23:00 | 441 | 439
2019-01-12 23:30 | 418 | 415
2019-01-13 | 389 | 386
2019-01-13 00:30 | 369 | 366
2019-01-13 01:00 | 359 | 356
2019-01-13 01:30 | 350 | 345
2019-01-13 02:00 | 344 | 338
2019-01-13 02:30 | 338 | 332
2019-01-13 03:00 | 336 | 329
2019-01-13 03:30 | 325 | 318
2019-01-13 04:00 | 321 | 314
2019-01-13 04:30 | 313 | 305
2019-01-13 05:00 | 311 | 302
2019-01-13 05:30 | 316 | 306
2019-01-13 06:00 | 321 | 311
2019-01-13 06:30 | 328 | 319
2019-01-13 07:00 | 341 | 333
2019-01-13 07:30 | 355 | 349
2019-01-13 08:00 | 365 | 361
2019-01-13 08:30 | 387 | 384
2019-01-13 09:00 | 396 | 394
2019-01-13 09:30 | 405 | 404
2019-01-13 10:00 | 415 | 414
2019-01-13 10:30 | 420 | 419
2019-01-13 11:00 | 421 | 420
2019-01-13 11:30 | 424 | 424
2019-01-13 12:00 | 428 | 428
2019-01-13 12:30 | 431 | 430
2019-01-13 13:00 | 438 | 438
2019-01-13 13:30 | 449 | 449
2019-01-13 14:00 | 469 | 469
2019-01-13 14:30 | 474 | 473
2019-01-13 15:00 | 480 | 480
2019-01-13 15:30 | 511 | 511
2019-01-13 16:00 | 533 | 532
2019-01-13 16:30 | 552 | 551
2019-01-13 17:00 | 562 | 562
2019-01-13 17:30 | 556 | 555
2019-01-13 18:00 | 551 | 550
2019-01-13 18:30 | 551 | 549
2019-01-13 19:00 | 541 | 539
2019-01-13 19:30 | 542 | 541
2019-01-13 20:00 | 548 | 547
2019-01-13 20:30 | 536 | 534
2019-01-13 21:00 | 494 | 493
2019-01-13 21:30 | 473 | 471
2019-01-13 22:00 | 463 | 461
2019-01-13 22:30 | 441 | 438
2019-01-13 23:00 | 428 | 426
2019-01-13 23:30 | 409 | 406
2019-01-14 | 390 | 387
2019-01-14 00:30 | 372 | 368
2019-01-14 01:00 | 360 | 355
2019-01-14 01:30 | 348 | 342
2019-01-14 02:00 | 340 | 334
2019-01-14 02:30 | 340 | 333
2019-01-14 03:00 | 342 | 335
2019-01-14 03:30 | 343 | 336
2019-01-14 04:00 | 349 | 342
2019-01-14 04:30 | 363 | 357
2019-01-14 05:00 | 360 | 354
2019-01-14 05:30 | 366 | 361
2019-01-14 06:00 | 382 | 378
2019-01-14 06:30 | 427 | 426
2019-01-14 07:00 | 470 | 469
2019-01-14 07:30 | 500 | 499
2019-01-14 08:00 | 512 | 512
2019-01-14 08:30 | 528 | 528
2019-01-14 09:00 | 544 | 544
2019-01-14 09:30 | 542 | 541
2019-01-14 10:00 | 556 | 555
2019-01-14 10:30 | 566 | 565
2019-01-14 11:00 | 552 | 551
2019-01-14 11:30 | 552 | 551
2019-01-14 12:00 | 557 | 557
2019-01-14 12:30 | 568 | 567
2019-01-14 13:00 | 572 | 572
2019-01-14 13:30 | 590 | 589
2019-01-14 14:00 | 605 | 605
2019-01-14 14:30 | 625 | 623
2019-01-14 15:00 | 643 | 639
2019-01-14 15:30 | 679 | 674
2019-01-14 16:00 | 698 | 693
2019-01-14 16:30 | 710 | 705
2019-01-14 17:00 | 727 | 722
2019-01-14 17:30 | 714 | 708
2019-01-14 18:00 | 697 | 691
2019-01-14 18:30 | 678 | 671
2019-01-14 19:00 | 670 | 669
2019-01-14 19:30 | 675 | 675
2019-01-14 20:00 | 668 | 667
2019-01-14 20:30 | 644 | 643
2019-01-14 21:00 | 598 | 596
2019-01-14 21:30 | 562 | 562
2019-01-14 22:00 | 527 | 527
2019-01-14 22:30 | 515 | 515
2019-01-14 23:00 | 495 | 494
2019-01-14 23:30 | 469 | 468
2019-01-15 | 441 | 441
2019-01-15 00:30 | 418 | 418
2019-01-15 01:00 | 404 | 403
2019-01-15 01:30 | 386 | 385
2019-01-15 02:00 | 367 | 366
2019-01-15 02:30 | 367 | 365
2019-01-15 03:00 | 360 | 358
2019-01-15 03:30 | 361 | 359
2019-01-15 04:00 | 361 | 360
2019-01-15 04:30 | 366 | 365
2019-01-15 05:00 | 374 | 373
2019-01-15 05:30 | 392 | 391
2019-01-15 06:00 | 412 | 412
2019-01-15 06:30 | 453 | 453
2019-01-15 07:00 | 486 | 486
2019-01-15 07:30 | 509 | 508
2019-01-15 08:00 | 528 | 528
2019-01-15 08:30 | 570 | 570
2019-01-15 09:00 | 572 | 572
2019-01-15 09:30 | 583 | 583
2019-01-15 10:00 | 590 | 590
2019-01-15 10:30 | 595 | 595
2019-01-15 11:00 | 594 | 594
2019-01-15 11:30 | 596 | 596
2019-01-15 12:00 | 610 | 610
2019-01-15 12:30 | 618 | 617
2019-01-15 13:00 | 629 | 629
2019-01-15 13:30 | 642 | 642
2019-01-15 14:00 | 649 | 649
2019-01-15 14:30 | 657 | 657
2019-01-15 15:00 | 670 | 670
2019-01-15 15:30 | 696 | 696
2019-01-15 16:00 | 726 | 724
2019-01-15 16:30 | 727 | 725
2019-01-15 17:00 | 741 | 738
2019-01-15 17:30 | 747 | 743
2019-01-15 18:00 | 742 | 735
2019-01-15 18:30 | 714 | 707
2019-01-15 19:00 | 695 | 687
2019-01-15 19:30 | 694 | 686
2019-01-15 20:00 | 696 | 687
2019-01-15 20:30 | 672 | 665
2019-01-15 21:00 | 611 | 610
2019-01-15 21:30 | 584 | 583
2019-01-15 22:00 | 556 | 553
2019-01-15 22:30 | 531 | 530
2019-01-15 23:00 | 517 | 517
2019-01-15 23:30 | 490 | 490
2019-01-16 | 457 | 457
2019-01-16 00:30 | 427 | 427
2019-01-16 01:00 | 416 | 416
2019-01-16 01:30 | 419 | 418
2019-01-16 02:00 | 415 | 414
2019-01-16 02:30 | 403 | 401
2019-01-16 03:00 | 392 | 391
2019-01-16 03:30 | 396 | 395
2019-01-16 04:00 | 400 | 398
2019-01-16 04:30 | 407 | 405
2019-01-16 05:00 | 409 | 408
2019-01-16 05:30 | 421 | 420
2019-01-16 06:00 | 434 | 433
2019-01-16 06:30 | 484 | 484
2019-01-16 07:00 | 520 | 519
2019-01-16 07:30 | 548 | 547
2019-01-16 08:00 | 555 | 555
2019-01-16 08:30 | 581 | 580
2019-01-16 09:00 | 594 | 594
2019-01-16 09:30 | 587 | 587
2019-01-16 10:00 | 591 | 590
2019-01-16 10:30 | 604 | 604
2019-01-16 11:00 | 612 | 612
2019-01-16 11:30 | 607 | 607
2019-01-16 12:00 | 625 | 623
2019-01-16 12:30 | 643 | 640
2019-01-16 13:00 | 663 | 658
2019-01-16 13:30 | 679 | 672
2019-01-16 14:00 | 700 | 693
2019-01-16 14:30 | 711 | 705
2019-01-16 15:00 | 739 | 734
2019-01-16 15:30 | 757 | 752
2019-01-16 16:00 | 771 | 767
2019-01-16 16:30 | 777 | 774
2019-01-16 17:00 | 789 | 786
2019-01-16 17:30 | 762 | 758
2019-01-16 18:00 | 746 | 739
2019-01-16 18:30 | 714 | 707
2019-01-16 19:00 | 711 | 703
2019-01-16 19:30 | 706 | 699
2019-01-16 20:00 | 713 | 706
2019-01-16 20:30 | 714 | 706
2019-01-16 21:00 | 653 | 650
2019-01-16 21:30 | 595 | 592
2019-01-16 22:00 | 542 | 539
2019-01-16 22:30 | 517 | 513
2019-01-16 23:00 | 507 | 504
2019-01-16 23:30 | 481 | 480
2019-01-17 | 458 | 456
2019-01-17 00:30 | 445 | 443
2019-01-17 01:00 | 428 | 426
2019-01-17 01:30 | 410 | 408
2019-01-17 02:00 | 408 | 406
2019-01-17 02:30 | 394 | 391
2019-01-17 03:00 | 387 | 384
2019-01-17 03:30 | 394 | 391
2019-01-17 04:00 | 386 | 383
2019-01-17 04:30 | 396 | 393
2019-01-17 05:00 | 411 | 409
2019-01-17 05:30 | 430 | 428
2019-01-17 06:00 | 460 | 458
2019-01-17 06:30 | 495 | 495
2019-01-17 07:00 | 543 | 537
2019-01-17 07:30 | 565 | 562
2019-01-17 08:00 | 580 | 576
2019-01-17 08:30 | 593 | 590
2019-01-17 09:00 | 613 | 609
2019-01-17 09:30 | 599 | 595
2019-01-17 10:00 | 593 | 589
2019-01-17 10:30 | 600 | 597
2019-01-17 11:00 | 605 | 602
2019-01-17 11:30 | 608 | 605
2019-01-17 12:00 | 609 | 607
2019-01-17 12:30 | 633 | 631
2019-01-17 13:00 | 635 | 633
2019-01-17 13:30 | 659 | 656
2019-01-17 14:00 | 674 | 672
2019-01-17 14:30 | 683 | 681
2019-01-17 15:00 | 702 | 700
2019-01-17 15:30 | 721 | 715
2019-01-17 16:00 | 747 | 739
2019-01-17 16:30 | 754 | 748
2019-01-17 17:00 | 762 | 756
2019-01-17 17:30 | 767 | 760
2019-01-17 18:00 | 748 | 739
2019-01-17 18:30 | 714 | 707
2019-01-17 19:00 | 686 | 677
2019-01-17 19:30 | 690 | 682
2019-01-17 20:00 | 685 | 677
2019-01-17 20:30 | 665 | 660
2019-01-17 21:00 | 634 | 632
2019-01-17 21:30 | 593 | 590
2019-01-17 22:00 | 555 | 552
2019-01-17 22:30 | 528 | 528
2019-01-17 23:00 | 518 | 518
2019-01-17 23:30 | 489 | 488
2019-01-18 | 455 | 455
2019-01-18 00:30 | 417 | 416
2019-01-18 01:00 | 407 | 407
2019-01-18 01:30 | 394 | 393
2019-01-18 02:00 | 394 | 393
2019-01-18 02:30 | 388 | 387
2019-01-18 03:00 | 395 | 393
2019-01-18 03:30 | 398 | 396
2019-01-18 04:00 | 397 | 395
2019-01-18 04:30 | 393 | 392
2019-01-18 05:00 | 399 | 398
2019-01-18 05:30 | 409 | 408
2019-01-18 06:00 | 430 | 429
2019-01-18 06:30 | 462 | 462
2019-01-18 07:00 | 480 | 480
2019-01-18 07:30 | 506 | 505
2019-01-18 08:00 | 526 | 526
2019-01-18 08:30 | 554 | 554
2019-01-18 09:00 | 559 | 559
2019-01-18 09:30 | 569 | 569
2019-01-18 10:00 | 600 | 596
2019-01-18 10:30 | 598 | 594
2019-01-18 11:00 | 585 | 582
2019-01-18 11:30 | 587 | 585
2019-01-18 12:00 | 582 | 580
2019-01-18 12:30 | 568 | 566
2019-01-18 13:00 | 570 | 568
2019-01-18 13:30 | 581 | 580
2019-01-18 14:00 | 597 | 595
2019-01-18 14:30 | 618 | 616
2019-01-18 15:00 | 631 | 629
2019-01-18 15:30 | 660 | 656
2019-01-18 16:00 | 688 | 684
2019-01-18 16:30 | 695 | 693
2019-01-18 17:00 | 722 | 720
2019-01-18 17:30 | 716 | 714
2019-01-18 18:00 | 701 | 696
2019-01-18 18:30 | 665 | 659
2019-01-18 19:00 | 653 | 644
2019-01-18 19:30 | 649 | 643
2019-01-18 20:00 | 648 | 641
2019-01-18 20:30 | 617 | 613
2019-01-18 21:00 | 592 | 590
2019-01-18 21:30 | 566 | 565
2019-01-18 22:00 | 544 | 543
2019-01-18 22:30 | 508 | 506
2019-01-18 23:00 | 492 | 492
2019-01-18 23:30 | 469 | 468
2019-01-19 | 439 | 438
2019-01-19 00:30 | 409 | 408
2019-01-19 01:00 | 393 | 391
2019-01-19 01:30 | 381 | 378
2019-01-19 02:00 | 372 | 370
2019-01-19 02:30 | 366 | 362
2019-01-19 03:00 | 358 | 354
2019-01-19 03:30 | 350 | 345
2019-01-19 04:00 | 361 | 357
2019-01-19 04:30 | 358 | 353
2019-01-19 05:00 | 356 | 352
2019-01-19 05:30 | 363 | 358
2019-01-19 06:00 | 372 | 366
2019-01-19 06:30 | 379 | 374
2019-01-19 07:00 | 388 | 385
2019-01-19 07:30 | 404 | 402
2019-01-19 08:00 | 426 | 424
2019-01-19 08:30 | 447 | 445
2019-01-19 09:00 | 466 | 465
2019-01-19 09:30 | 480 | 479
2019-01-19 10:00 | 482 | 482
2019-01-19 10:30 | 506 | 505
2019-01-19 11:00 | 506 | 505
2019-01-19 11:30 | 518 | 518
2019-01-19 12:00 | 531 | 531
2019-01-19 12:30 | 532 | 532
2019-01-19 13:00 | 527 | 527
2019-01-19 13:30 | 519 | 519
2019-01-19 14:00 | 528 | 528
2019-01-19 14:30 | 546 | 544
2019-01-19 15:00 | 572 | 568
2019-01-19 15:30 | 588 | 585
2019-01-19 16:00 | 607 | 604
2019-01-19 16:30 | 616 | 613
2019-01-19 17:00 | 627 | 623
2019-01-19 17:30 | 637 | 632
2019-01-19 18:00 | 634 | 628
2019-01-19 18:30 | 629 | 623
2019-01-19 19:00 | 616 | 609
2019-01-19 19:30 | 610 | 603
2019-01-19 20:00 | 596 | 589
2019-01-19 20:30 | 577 | 570
2019-01-19 21:00 | 553 | 548
2019-01-19 21:30 | 532 | 526
2019-01-19 22:00 | 516 | 510
2019-01-19 22:30 | 483 | 479
2019-01-19 23:00 | 469 | 465
2019-01-19 23:30 | 453 | 448
2019-01-20 | 421 | 421
2019-01-20 00:30 | 396 | 394
2019-01-20 01:00 | 378 | 375
2019-01-20 01:30 | 345 | 342
2019-01-20 02:00 | 331 | 327
2019-01-20 02:30 | 330 | 325
2019-01-20 03:00 | 328 | 323
2019-01-20 03:30 | 328 | 322
2019-01-20 04:00 | 334 | 326
2019-01-20 04:30 | 331 | 324
2019-01-20 05:00 | 331 | 324
2019-01-20 05:30 | 335 | 327
2019-01-20 06:00 | 343 | 335
2019-01-20 06:30 | 361 | 354
2019-01-20 07:00 | 378 | 373
2019-01-20 07:30 | 390 | 387
2019-01-20 08:00 | 397 | 395
2019-01-20 08:30 | 409 | 408
2019-01-20 09:00 | 416 | 415
2019-01-20 09:30 | 425 | 425
2019-01-20 10:00 | 437 | 437
2019-01-20 10:30 | 456 | 456
2019-01-20 11:00 | 461 | 460
2019-01-20 11:30 | 477 | 476
2019-01-20 12:00 | 490 | 488
2019-01-20 12:30 | 507 | 505
2019-01-20 13:00 | 531 | 530
2019-01-20 13:30 | 549 | 549
2019-01-20 14:00 | 564 | 563
2019-01-20 14:30 | 567 | 567
2019-01-20 15:00 | 579 | 578
2019-01-20 15:30 | 594 | 593
2019-01-20 16:00 | 620 | 619
2019-01-20 16:30 | 643 | 642
2019-01-20 17:00 | 658 | 657
2019-01-20 17:30 | 659 | 652
2019-01-20 18:00 | 660 | 653
2019-01-20 18:30 | 654 | 646
2019-01-20 19:00 | 644 | 635
2019-01-20 19:30 | 636 | 631
2019-01-20 20:00 | 631 | 626
2019-01-20 20:30 | 600 | 594
2019-01-20 21:00 | 558 | 552
2019-01-20 21:30 | 534 | 529
2019-01-20 22:00 | 518 | 513
2019-01-20 22:30 | 506 | 501
2019-01-20 23:00 | 480 | 479
2019-01-20 23:30 | 449 | 449
2019-01-21 | 420 | 420
2019-01-21 00:30 | 401 | 401
2019-01-21 01:00 | 398 | 397
2019-01-21 01:30 | 382 | 381
2019-01-21 02:00 | 374 | 372
2019-01-21 02:30 | 373 | 371
2019-01-21 03:00 | 372 | 370
2019-01-21 03:30 | 373 | 371
2019-01-21 04:00 | 376 | 374
2019-01-21 04:30 | 378 | 375
2019-01-21 05:00 | 386 | 384
2019-01-21 05:30 | 407 | 405
2019-01-21 06:00 | 427 | 426
2019-01-21 06:30 | 463 | 463
2019-01-21 07:00 | 499 | 499
2019-01-21 07:30 | 544 | 543
2019-01-21 08:00 | 572 | 572
2019-01-21 08:30 | 588 | 588
2019-01-21 09:00 | 597 | 597
2019-01-21 09:30 | 600 | 600
2019-01-21 10:00 | 602 | 602
2019-01-21 10:30 | 603 | 603
2019-01-21 11:00 | 605 | 605
2019-01-21 11:30 | 612 | 612
2019-01-21 12:00 | 617 | 617
2019-01-21 12:30 | 622 | 622
2019-01-21 13:00 | 643 | 642
2019-01-21 13:30 | 681 | 677
2019-01-21 14:00 | 687 | 682
2019-01-21 14:30 | 702 | 697
2019-01-21 15:00 | 709 | 705
2019-01-21 15:30 | 713 | 710
2019-01-21 16:00 | 731 | 726
2019-01-21 16:30 | 742 | 736
2019-01-21 17:00 | 739 | 734
2019-01-21 17:30 | 732 | 725
2019-01-21 18:00 | 707 | 701
2019-01-21 18:30 | 670 | 662
2019-01-21 19:00 | 680 | 672
2019-01-21 19:30 | 670 | 663
2019-01-21 20:00 | 658 | 651
2019-01-21 20:30 | 627 | 620
2019-01-21 21:00 | 584 | 580
2019-01-21 21:30 | 554 | 548
2019-01-21 22:00 | 527 | 521
2019-01-21 22:30 | 498 | 491
2019-01-21 23:00 | 474 | 472
2019-01-21 23:30 | 442 | 441
2019-01-22 | 412 | 411
2019-01-22 00:30 | 384 | 383
2019-01-22 01:00 | 372 | 370
2019-01-22 01:30 | 356 | 353
2019-01-22 02:00 | 367 | 363
2019-01-22 02:30 | 370 | 366
2019-01-22 03:00 | 370 | 366
2019-01-22 03:30 | 372 | 367
2019-01-22 04:00 | 374 | 369
2019-01-22 04:30 | 376 | 372
2019-01-22 05:00 | 376 | 373
2019-01-22 05:30 | 389 | 386
2019-01-22 06:00 | 414 | 411
2019-01-22 06:30 | 448 | 446
2019-01-22 07:00 | 477 | 475
2019-01-22 07:30 | 498 | 498
2019-01-22 08:00 | 526 | 526
2019-01-22 08:30 | 551 | 551
2019-01-22 09:00 | 564 | 564
2019-01-22 09:30 | 592 | 591
2019-01-22 10:00 | 635 | 630
2019-01-22 10:30 | 648 | 643
2019-01-22 11:00 | 652 | 648
2019-01-22 11:30 | 657 | 653
2019-01-22 12:00 | 670 | 666
2019-01-22 12:30 | 685 | 681
2019-01-22 13:00 | 685 | 682
2019-01-22 13:30 | 706 | 703
2019-01-22 14:00 | 714 | 711
2019-01-22 14:30 | 737 | 734
2019-01-22 15:00 | 751 | 748
2019-01-22 15:30 | 760 | 757
2019-01-22 16:00 | 769 | 767
2019-01-22 16:30 | 779 | 774
2019-01-22 17:00 | 780 | 775
2019-01-22 17:30 | 772 | 767
2019-01-22 18:00 | 770 | 761
2019-01-22 18:30 | 740 | 730
2019-01-22 19:00 | 744 | 736
2019-01-22 19:30 | 736 | 729
2019-01-22 20:00 | 719 | 711
2019-01-22 20:30 | 682 | 674
2019-01-22 21:00 | 642 | 639
2019-01-22 21:30 | 612 | 608
2019-01-22 22:00 | 582 | 576
2019-01-22 22:30 | 542 | 536
2019-01-22 23:00 | 519 | 513
2019-01-22 23:30 | 494 | 488
2019-01-23 | 470 | 467
2019-01-23 00:30 | 446 | 440
2019-01-23 01:00 | 419 | 412
2019-01-23 01:30 | 403 | 397
2019-01-23 02:00 | 403 | 397
2019-01-23 02:30 | 403 | 396
2019-01-23 03:00 | 402 | 395
2019-01-23 03:30 | 402 | 394
2019-01-23 04:00 | 399 | 391
2019-01-23 04:30 | 391 | 386
2019-01-23 05:00 | 396 | 393
2019-01-23 05:30 | 416 | 413
2019-01-23 06:00 | 440 | 438
2019-01-23 06:30 | 468 | 467
2019-01-23 07:00 | 510 | 507
2019-01-23 07:30 | 538 | 534
2019-01-23 08:00 | 562 | 559
2019-01-23 08:30 | 596 | 592
2019-01-23 09:00 | 616 | 611
2019-01-23 09:30 | 632 | 623
2019-01-23 10:00 | 636 | 627
2019-01-23 10:30 | 664 | 657
2019-01-23 11:00 | 677 | 671
2019-01-23 11:30 | 685 | 679
2019-01-23 12:00 | 719 | 714
2019-01-23 12:30 | 730 | 723
2019-01-23 13:00 | 724 | 716
2019-01-23 13:30 | 740 | 734
2019-01-23 14:00 | 760 | 753
2019-01-23 14:30 | 768 | 760
2019-01-23 15:00 | 776 | 769
2019-01-23 15:30 | 791 | 785
2019-01-23 16:00 | 793 | 789
2019-01-23 16:30 | 814 | 809
2019-01-23 17:00 | 819 | 812
2019-01-23 17:30 | 794 | 785
2019-01-23 18:00 | 771 | 758
2019-01-23 18:30 | 729 | 719
2019-01-23 19:00 | 714 | 707
2019-01-23 19:30 | 711 | 704
2019-01-23 20:00 | 700 | 691
2019-01-23 20:30 | 686 | 676
2019-01-23 21:00 | 638 | 631
2019-01-23 21:30 | 599 | 592
2019-01-23 22:00 | 574 | 567
2019-01-23 22:30 | 544 | 536
2019-01-23 23:00 | 525 | 516
2019-01-23 23:30 | 484 | 480
2019-01-24 | 446 | 446
2019-01-24 00:30 | 423 | 423
2019-01-24 01:00 | 408 | 407
2019-01-24 01:30 | 397 | 395
2019-01-24 02:00 | 393 | 391
2019-01-24 02:30 | 387 | 386
2019-01-24 03:00 | 379 | 377
2019-01-24 03:30 | 380 | 378
2019-01-24 04:00 | 376 | 373
2019-01-24 04:30 | 380 | 378
2019-01-24 05:00 | 382 | 380
2019-01-24 05:30 | 401 | 399
2019-01-24 06:00 | 429 | 428
2019-01-24 06:30 | 468 | 468
2019-01-24 07:00 | 503 | 502
2019-01-24 07:30 | 538 | 538
2019-01-24 08:00 | 565 | 564
2019-01-24 08:30 | 592 | 590
2019-01-24 09:00 | 617 | 616
2019-01-24 09:30 | 629 | 625
2019-01-24 10:00 | 645 | 641
2019-01-24 10:30 | 658 | 654
2019-01-24 11:00 | 664 | 661
2019-01-24 11:30 | 668 | 665
2019-01-24 12:00 | 676 | 673
2019-01-24 12:30 | 685 | 681
2019-01-24 13:00 | 694 | 691
2019-01-24 13:30 | 698 | 695
2019-01-24 14:00 | 721 | 717
2019-01-24 14:30 | 748 | 744
2019-01-24 15:00 | 769 | 765
2019-01-24 15:30 | 760 | 757
2019-01-24 16:00 | 788 | 785
2019-01-24 16:30 | 798 | 793
2019-01-24 17:00 | 803 | 798
2019-01-24 17:30 | 793 | 787
2019-01-24 18:00 | 771 | 762
2019-01-24 18:30 | 745 | 735
2019-01-24 19:00 | 744 | 733
2019-01-24 19:30 | 750 | 740
2019-01-24 20:00 | 743 | 734
2019-01-24 20:30 | 708 | 700
2019-01-24 21:00 | 673 | 667
2019-01-24 21:30 | 651 | 645
2019-01-24 22:00 | 611 | 606
2019-01-24 22:30 | 557 | 555
2019-01-24 23:00 | 529 | 528
2019-01-24 23:30 | 497 | 495
2019-01-25 | 468 | 467
2019-01-25 00:30 | 442 | 441
2019-01-25 01:00 | 431 | 430
2019-01-25 01:30 | 423 | 422
2019-01-25 02:00 | 417 | 416
2019-01-25 02:30 | 417 | 415
2019-01-25 03:00 | 410 | 408
2019-01-25 03:30 | 417 | 415
2019-01-25 04:00 | 414 | 412
2019-01-25 04:30 | 406 | 405
2019-01-25 05:00 | 413 | 411
2019-01-25 05:30 | 425 | 424
2019-01-25 06:00 | 456 | 455
2019-01-25 06:30 | 480 | 480
2019-01-25 07:00 | 528 | 528
2019-01-25 07:30 | 568 | 567
2019-01-25 08:00 | 606 | 600
2019-01-25 08:30 | 636 | 630
2019-01-25 09:00 | 645 | 639
2019-01-25 09:30 | 642 | 637
2019-01-25 10:00 | 646 | 642
2019-01-25 10:30 | 652 | 649
2019-01-25 11:00 | 675 | 670
2019-01-25 11:30 | 665 | 658
2019-01-25 12:00 | 671 | 664
2019-01-25 12:30 | 705 | 699
2019-01-25 13:00 | 693 | 688
2019-01-25 13:30 | 698 | 695
2019-01-25 14:00 | 721 | 718
2019-01-25 14:30 | 768 | 763
2019-01-25 15:00 | 778 | 773
2019-01-25 15:30 | 788 | 783
2019-01-25 16:00 | 798 | 793
2019-01-25 16:30 | 808 | 803
2019-01-25 17:00 | 814 | 808
2019-01-25 17:30 | 809 | 802
2019-01-25 18:00 | 785 | 776
2019-01-25 18:30 | 773 | 762
2019-01-25 19:00 | 766 | 755
2019-01-25 19:30 | 757 | 748
2019-01-25 20:00 | 752 | 744
2019-01-25 20:30 | 705 | 697
2019-01-25 21:00 | 675 | 670
2019-01-25 21:30 | 638 | 630
2019-01-25 22:00 | 603 | 595
2019-01-25 22:30 | 570 | 563
2019-01-25 23:00 | 548 | 541
2019-01-25 23:30 | 511 | 509
2019-01-26 | 475 | 473
2019-01-26 00:30 | 435 | 432
2019-01-26 01:00 | 419 | 417
2019-01-26 01:30 | 406 | 405
2019-01-26 02:00 | 390 | 389
2019-01-26 02:30 | 386 | 385
2019-01-26 03:00 | 382 | 381
2019-01-26 03:30 | 377 | 376
2019-01-26 04:00 | 374 | 372
2019-01-26 04:30 | 375 | 373
2019-01-26 05:00 | 372 | 370
2019-01-26 05:30 | 375 | 373
2019-01-26 06:00 | 385 | 382
2019-01-26 06:30 | 402 | 400
2019-01-26 07:00 | 418 | 416
2019-01-26 07:30 | 437 | 436
2019-01-26 08:00 | 455 | 454
2019-01-26 08:30 | 468 | 468
2019-01-26 09:00 | 484 | 484
2019-01-26 09:30 | 499 | 499
2019-01-26 10:00 | 505 | 505
2019-01-26 10:30 | 535 | 534
2019-01-26 11:00 | 548 | 547
2019-01-26 11:30 | 554 | 553
2019-01-26 12:00 | 557 | 556
2019-01-26 12:30 | 557 | 556
2019-01-26 13:00 | 563 | 562
2019-01-26 13:30 | 563 | 563
2019-01-26 14:00 | 560 | 560
2019-01-26 14:30 | 574 | 573
2019-01-26 15:00 | 601 | 601
2019-01-26 15:30 | 622 | 622
2019-01-26 16:00 | 642 | 640
2019-01-26 16:30 | 650 | 649
2019-01-26 17:00 | 661 | 660
2019-01-26 17:30 | 662 | 660
2019-01-26 18:00 | 636 | 633
2019-01-26 18:30 | 623 | 620
2019-01-26 19:00 | 618 | 617
2019-01-26 19:30 | 615 | 614
2019-01-26 20:00 | 604 | 603
2019-01-26 20:30 | 582 | 582
2019-01-26 21:00 | 551 | 550
2019-01-26 21:30 | 532 | 532
2019-01-26 22:00 | 512 | 512
2019-01-26 22:30 | 488 | 488
2019-01-26 23:00 | 467 | 467
2019-01-26 23:30 | 438 | 438
2019-01-27 | 415 | 414
2019-01-27 00:30 | 406 | 404
2019-01-27 01:00 | 404 | 401
2019-01-27 01:30 | 390 | 388
2019-01-27 02:00 | 378 | 375
2019-01-27 02:30 | 377 | 374
2019-01-27 03:00 | 369 | 366
2019-01-27 03:30 | 370 | 367
2019-01-27 04:00 | 370 | 367
2019-01-27 04:30 | 369 | 366
2019-01-27 05:00 | 359 | 355
2019-01-27 05:30 | 359 | 354
2019-01-27 06:00 | 364 | 358
2019-01-27 06:30 | 382 | 377
2019-01-27 07:00 | 408 | 404
2019-01-27 07:30 | 419 | 416
2019-01-27 08:00 | 426 | 424
2019-01-27 08:30 | 434 | 432
2019-01-27 09:00 | 443 | 442
2019-01-27 09:30 | 448 | 447
2019-01-27 10:00 | 452 | 452
2019-01-27 10:30 | 455 | 455
2019-01-27 11:00 | 460 | 460
2019-01-27 11:30 | 474 | 474
2019-01-27 12:00 | 472 | 472
2019-01-27 12:30 | 476 | 476
2019-01-27 13:00 | 490 | 490
2019-01-27 13:30 | 504 | 504
2019-01-27 14:00 | 517 | 517
2019-01-27 14:30 | 535 | 535
2019-01-27 15:00 | 560 | 560
2019-01-27 15:30 | 586 | 585
2019-01-27 16:00 | 593 | 593
2019-01-27 16:30 | 598 | 597
2019-01-27 17:00 | 612 | 612
2019-01-27 17:30 | 612 | 611
2019-01-27 18:00 | 610 | 608
2019-01-27 18:30 | 602 | 599
2019-01-27 19:00 | 599 | 597
2019-01-27 19:30 | 601 | 599
2019-01-27 20:00 | 603 | 600
2019-01-27 20:30 | 585 | 582
2019-01-27 21:00 | 555 | 555
2019-01-27 21:30 | 536 | 536
2019-01-27 22:00 | 515 | 515
2019-01-27 22:30 | 508 | 507
2019-01-27 23:00 | 495 | 494
2019-01-27 23:30 | 469 | 468
2019-01-28 | 449 | 449
2019-01-28 00:30 | 420 | 419
2019-01-28 01:00 | 402 | 401
2019-01-28 01:30 | 391 | 390
2019-01-28 02:00 | 381 | 380
2019-01-28 02:30 | 381 | 379
2019-01-28 03:00 | 376 | 374
2019-01-28 03:30 | 372 | 371
2019-01-28 04:00 | 375 | 373
2019-01-28 04:30 | 377 | 375
2019-01-28 05:00 | 381 | 379
2019-01-28 05:30 | 391 | 389
2019-01-28 06:00 | 400 | 398
2019-01-28 06:30 | 410 | 409
2019-01-28 07:00 | 421 | 420
2019-01-28 07:30 | 437 | 437
2019-01-28 08:00 | 449 | 449
2019-01-28 08:30 | 466 | 466
2019-01-28 09:00 | 472 | 472
2019-01-28 09:30 | 472 | 472
2019-01-28 10:00 | 474 | 474
2019-01-28 10:30 | 493 | 493
2019-01-28 11:00 | 505 | 504
2019-01-28 11:30 | 519 | 519
2019-01-28 12:00 | 515 | 515
2019-01-28 12:30 | 511 | 510
2019-01-28 13:00 | 538 | 538
2019-01-28 13:30 | 557 | 557
2019-01-28 14:00 | 578 | 577
2019-01-28 14:30 | 598 | 597
2019-01-28 15:00 | 625 | 625
2019-01-28 15:30 | 650 | 650
2019-01-28 16:00 | 674 | 674
2019-01-28 16:30 | 704 | 701
2019-01-28 17:00 | 705 | 702
2019-01-28 17:30 | 712 | 709
2019-01-28 18:00 | 708 | 703
2019-01-28 18:30 | 688 | 682
2019-01-28 19:00 | 679 | 674
2019-01-28 19:30 | 668 | 665
2019-01-28 20:00 | 648 | 645
2019-01-28 20:30 | 613 | 610
2019-01-28 21:00 | 578 | 577
2019-01-28 21:30 | 563 | 562
2019-01-28 22:00 | 537 | 535
2019-01-28 22:30 | 513 | 512
2019-01-28 23:00 | 489 | 489
2019-01-28 23:30 | 463 | 462
2019-01-29 | 441 | 440
2019-01-29 00:30 | 415 | 414
2019-01-29 01:00 | 404 | 403
2019-01-29 01:30 | 393 | 392
2019-01-29 02:00 | 379 | 377
2019-01-29 02:30 | 378 | 375
2019-01-29 03:00 | 377 | 375
2019-01-29 03:30 | 367 | 364
2019-01-29 04:00 | 368 | 366
2019-01-29 04:30 | 371 | 368
2019-01-29 05:00 | 377 | 375
2019-01-29 05:30 | 392 | 390
2019-01-29 06:00 | 418 | 418
2019-01-29 06:30 | 477 | 476
2019-01-29 07:00 | 539 | 539
2019-01-29 07:30 | 565 | 565
2019-01-29 08:00 | 585 | 584
2019-01-29 08:30 | 600 | 596
2019-01-29 09:00 | 604 | 601
2019-01-29 09:30 | 626 | 623
2019-01-29 10:00 | 631 | 627
2019-01-29 10:30 | 640 | 637
2019-01-29 11:00 | 648 | 645
2019-01-29 11:30 | 658 | 654
2019-01-29 12:00 | 657 | 654
2019-01-29 12:30 | 655 | 652
2019-01-29 13:00 | 663 | 659
2019-01-29 13:30 | 680 | 676
2019-01-29 14:00 | 694 | 691
2019-01-29 14:30 | 709 | 706
2019-01-29 15:00 | 717 | 715
2019-01-29 15:30 | 741 | 737
2019-01-29 16:00 | 737 | 735
2019-01-29 16:30 | 772 | 770
2019-01-29 17:00 | 808 | 798
2019-01-29 17:30 | 815 | 802
2019-01-29 18:00 | 795 | 783
2019-01-29 18:30 | 763 | 754
2019-01-29 19:00 | 767 | 758
2019-01-29 19:30 | 746 | 738
2019-01-29 20:00 | 723 | 714
2019-01-29 20:30 | 693 | 687
2019-01-29 21:00 | 646 | 644
2019-01-29 21:30 | 597 | 596
2019-01-29 22:00 | 569 | 567
2019-01-29 22:30 | 542 | 541
2019-01-29 23:00 | 530 | 529
2019-01-29 23:30 | 504 | 503
2019-01-30 | 480 | 479
2019-01-30 00:30 | 447 | 446
2019-01-30 01:00 | 441 | 438
2019-01-30 01:30 | 422 | 419
2019-01-30 02:00 | 412 | 408
2019-01-30 02:30 | 408 | 404
2019-01-30 03:00 | 401 | 397
2019-01-30 03:30 | 401 | 397
2019-01-30 04:00 | 405 | 400
2019-01-30 04:30 | 410 | 406
2019-01-30 05:00 | 409 | 406
2019-01-30 05:30 | 427 | 424
2019-01-30 06:00 | 454 | 452
2019-01-30 06:30 | 502 | 502
2019-01-30 07:00 | 536 | 535
2019-01-30 07:30 | 571 | 569
2019-01-30 08:00 | 608 | 605
2019-01-30 08:30 | 642 | 639
2019-01-30 09:00 | 643 | 640
2019-01-30 09:30 | 644 | 642
2019-01-30 10:00 | 635 | 630
2019-01-30 10:30 | 625 | 619
2019-01-30 11:00 | 627 | 623
2019-01-30 11:30 | 634 | 630
2019-01-30 12:00 | 655 | 652
2019-01-30 12:30 | 682 | 677
2019-01-30 13:00 | 686 | 682
2019-01-30 13:30 | 704 | 700
2019-01-30 14:00 | 726 | 724
2019-01-30 14:30 | 737 | 734
2019-01-30 15:00 | 748 | 745
2019-01-30 15:30 | 763 | 759
2019-01-30 16:00 | 764 | 760
2019-01-30 16:30 | 768 | 763
2019-01-30 17:00 | 769 | 764
2019-01-30 17:30 | 764 | 758
2019-01-30 18:00 | 735 | 726
2019-01-30 18:30 | 701 | 692
2019-01-30 19:00 | 713 | 709
2019-01-30 19:30 | 718 | 713
2019-01-30 20:00 | 707 | 702
2019-01-30 20:30 | 678 | 673
2019-01-30 21:00 | 641 | 635
2019-01-30 21:30 | 610 | 605
2019-01-30 22:00 | 576 | 571
2019-01-30 22:30 | 538 | 538
2019-01-30 23:00 | 514 | 514
2019-01-30 23:30 | 471 | 471
2019-01-31 | 436 | 436
2019-01-31 00:30 | 411 | 411
2019-01-31 01:00 | 398 | 398
2019-01-31 01:30 | 377 | 377
2019-01-31 02:00 | 374 | 374
2019-01-31 02:30 | 377 | 376
2019-01-31 03:00 | 378 | 377
2019-01-31 03:30 | 383 | 381
2019-01-31 04:00 | 381 | 379
2019-01-31 04:30 | 385 | 384
2019-01-31 05:00 | 391 | 389
2019-01-31 05:30 | 417 | 416
2019-01-31 06:00 | 441 | 440
2019-01-31 06:30 | 491 | 491
2019-01-31 07:00 | 541 | 541
2019-01-31 07:30 | 557 | 557
2019-01-31 08:00 | 565 | 565
2019-01-31 08:30 | 586 | 583
2019-01-31 09:00 | 593 | 590
2019-01-31 09:30 | 589 | 586
2019-01-31 10:00 | 598 | 596
2019-01-31 10:30 | 619 | 617
2019-01-31 11:00 | 623 | 622
2019-01-31 11:30 | 636 | 635
2019-01-31 12:00 | 648 | 647
2019-01-31 12:30 | 664 | 663
2019-01-31 13:00 | 674 | 673
2019-01-31 13:30 | 696 | 695
2019-01-31 14:00 | 713 | 712
2019-01-31 14:30 | 716 | 715
2019-01-31 15:00 | 744 | 742
2019-01-31 15:30 | 760 | 758
2019-01-31 16:00 | 773 | 770
2019-01-31 16:30 | 797 | 795
2019-01-31 17:00 | 809 | 808
2019-01-31 17:30 | 783 | 781
2019-01-31 18:00 | 757 | 753
2019-01-31 18:30 | 727 | 722
2019-01-31 19:00 | 730 | 726
2019-01-31 19:30 | 734 | 728
2019-01-31 20:00 | 733 | 724
2019-01-31 20:30 | 689 | 683
2019-01-31 21:00 | 647 | 645
2019-01-31 21:30 | 610 | 607
2019-01-31 22:00 | 569 | 567
2019-01-31 22:30 | 532 | 530
2019-01-31 23:00 | 516 | 515
2019-01-31 23:30 | 491 | 489
2019-02-01 | 460 | 459
2019-02-01 00:30 | 431 | 429
2019-02-01 01:00 | 414 | 413
2019-02-01 01:30 | 407 | 405
2019-02-01 02:00 | 398 | 396
2019-02-01 02:30 | 392 | 389
2019-02-01 03:00 | 388 | 385
2019-02-01 03:30 | 384 | 380
2019-02-01 04:00 | 382 | 379
2019-02-01 04:30 | 385 | 382
2019-02-01 05:00 | 391 | 389
2019-02-01 05:30 | 422 | 419
2019-02-01 06:00 | 438 | 436
2019-02-01 06:30 | 471 | 470
2019-02-01 07:00 | 501 | 501
2019-02-01 07:30 | 528 | 527
2019-02-01 08:00 | 539 | 539
2019-02-01 08:30 | 550 | 550
2019-02-01 09:00 | 558 | 557
2019-02-01 09:30 | 568 | 566
2019-02-01 10:00 | 582 | 580
2019-02-01 10:30 | 586 | 585
2019-02-01 11:00 | 588 | 587
2019-02-01 11:30 | 586 | 585
2019-02-01 12:00 | 598 | 596
2019-02-01 12:30 | 597 | 595
2019-02-01 13:00 | 612 | 611
2019-02-01 13:30 | 624 | 623
2019-02-01 14:00 | 637 | 637
2019-02-01 14:30 | 662 | 659
2019-02-01 15:00 | 671 | 665
2019-02-01 15:30 | 681 | 675
2019-02-01 16:00 | 691 | 686
2019-02-01 16:30 | 702 | 697
2019-02-01 17:00 | 700 | 694
2019-02-01 17:30 | 672 | 663
2019-02-01 18:00 | 645 | 638
2019-02-01 18:30 | 626 | 614
2019-02-01 19:00 | 629 | 621
2019-02-01 19:30 | 627 | 619
2019-02-01 20:00 | 618 | 612
2019-02-01 20:30 | 590 | 587
2019-02-01 21:00 | 562 | 559
2019-02-01 21:30 | 550 | 545
2019-02-01 22:00 | 522 | 518
2019-02-01 22:30 | 505 | 504
2019-02-01 23:00 | 497 | 494
2019-02-01 23:30 | 472 | 472
2019-02-02 | 438 | 438
2019-02-02 00:30 | 410 | 410
2019-02-02 01:00 | 404 | 403
2019-02-02 01:30 | 401 | 400
2019-02-02 02:00 | 391 | 390
2019-02-02 02:30 | 393 | 391
2019-02-02 03:00 | 390 | 388
2019-02-02 03:30 | 384 | 382
2019-02-02 04:00 | 389 | 387
2019-02-02 04:30 | 369 | 366
2019-02-02 05:00 | 359 | 356
2019-02-02 05:30 | 359 | 356
2019-02-02 06:00 | 362 | 359
2019-02-02 06:30 | 384 | 382
2019-02-02 07:00 | 392 | 391
2019-02-02 07:30 | 413 | 412
2019-02-02 08:00 | 433 | 432
2019-02-02 08:30 | 449 | 449
2019-02-02 09:00 | 445 | 444
2019-02-02 09:30 | 467 | 466
2019-02-02 10:00 | 476 | 475
2019-02-02 10:30 | 472 | 471
2019-02-02 11:00 | 483 | 482
2019-02-02 11:30 | 468 | 467
2019-02-02 12:00 | 476 | 475
2019-02-02 12:30 | 492 | 491
2019-02-02 13:00 | 486 | 485
2019-02-02 13:30 | 489 | 488
2019-02-02 14:00 | 507 | 506
2019-02-02 14:30 | 513 | 512
2019-02-02 15:00 | 498 | 498
2019-02-02 15:30 | 513 | 512
2019-02-02 16:00 | 520 | 519
2019-02-02 16:30 | 523 | 522
2019-02-02 17:00 | 531 | 530
2019-02-02 17:30 | 553 | 545
2019-02-02 18:00 | 553 | 544
2019-02-02 18:30 | 552 | 542
2019-02-02 19:00 | 550 | 540
2019-02-02 19:30 | 552 | 544
2019-02-02 20:00 | 555 | 545
2019-02-02 20:30 | 539 | 529
2019-02-02 21:00 | 497 | 491
2019-02-02 21:30 | 502 | 496
2019-02-02 22:00 | 463 | 462
2019-02-02 22:30 | 456 | 455
2019-02-02 23:00 | 437 | 436
2019-02-02 23:30 | 414 | 413
2019-02-03 | 393 | 391
2019-02-03 00:30 | 381 | 379
2019-02-03 01:00 | 376 | 373
2019-02-03 01:30 | 361 | 357
2019-02-03 02:00 | 354 | 350
2019-02-03 02:30 | 352 | 347
2019-02-03 03:00 | 356 | 350
2019-02-03 03:30 | 355 | 349
2019-02-03 04:00 | 355 | 349
2019-02-03 04:30 | 346 | 340
2019-02-03 05:00 | 341 | 335
2019-02-03 05:30 | 344 | 337
2019-02-03 06:00 | 324 | 316
2019-02-03 06:30 | 334 | 327
2019-02-03 07:00 | 350 | 344
2019-02-03 07:30 | 363 | 358
2019-02-03 08:00 | 392 | 389
2019-02-03 08:30 | 410 | 408
2019-02-03 09:00 | 420 | 418
2019-02-03 09:30 | 434 | 432
2019-02-03 10:00 | 456 | 454
2019-02-03 10:30 | 460 | 459
2019-02-03 11:00 | 450 | 449
2019-02-03 11:30 | 445 | 444
2019-02-03 12:00 | 452 | 451
2019-02-03 12:30 | 451 | 450
2019-02-03 13:00 | 438 | 437
2019-02-03 13:30 | 434 | 433
2019-02-03 14:00 | 455 | 454
2019-02-03 14:30 | 474 | 473
2019-02-03 15:00 | 490 | 490
2019-02-03 15:30 | 515 | 514
2019-02-03 16:00 | 544 | 544
2019-02-03 16:30 | 562 | 561
2019-02-03 17:00 | 575 | 574
2019-02-03 17:30 | 585 | 584
2019-02-03 18:00 | 576 | 574
2019-02-03 18:30 | 565 | 564
2019-02-03 19:00 | 584 | 583
2019-02-03 19:30 | 595 | 594
2019-02-03 20:00 | 591 | 590
2019-02-03 20:30 | 571 | 569
2019-02-03 21:00 | 547 | 545
2019-02-03 21:30 | 530 | 528
2019-02-03 22:00 | 510 | 507
2019-02-03 22:30 | 481 | 479
2019-02-03 23:00 | 462 | 459
2019-02-03 23:30 | 435 | 433
2019-02-04 | 415 | 412
2019-02-04 00:30 | 402 | 398
2019-02-04 01:00 | 394 | 389
2019-02-04 01:30 | 384 | 379
2019-02-04 02:00 | 380 | 374
2019-02-04 02:30 | 379 | 373
2019-02-04 03:00 | 373 | 367
2019-02-04 03:30 | 379 | 374
2019-02-04 04:00 | 382 | 376
2019-02-04 04:30 | 394 | 389
2019-02-04 05:00 | 397 | 392
2019-02-04 05:30 | 414 | 409
2019-02-04 06:00 | 449 | 446
2019-02-04 06:30 | 490 | 489
2019-02-04 07:00 | 533 | 533
2019-02-04 07:30 | 565 | 565
2019-02-04 08:00 | 575 | 575
2019-02-04 08:30 | 589 | 588
2019-02-04 09:00 | 593 | 592
2019-02-04 09:30 | 588 | 586
2019-02-04 10:00 | 594 | 592
2019-02-04 10:30 | 581 | 579
2019-02-04 11:00 | 576 | 574
2019-02-04 11:30 | 574 | 572
2019-02-04 12:00 | 585 | 584
2019-02-04 12:30 | 591 | 590
2019-02-04 13:00 | 602 | 601
2019-02-04 13:30 | 613 | 612
2019-02-04 14:00 | 614 | 613
2019-02-04 14:30 | 621 | 621
2019-02-04 15:00 | 627 | 626
2019-02-04 15:30 | 644 | 643
2019-02-04 16:00 | 682 | 682
2019-02-04 16:30 | 701 | 701
2019-02-04 17:00 | 720 | 720
2019-02-04 17:30 | 720 | 719
2019-02-04 18:00 | 713 | 712
2019-02-04 18:30 | 679 | 677
2019-02-04 19:00 | 666 | 665
2019-02-04 19:30 | 658 | 656
2019-02-04 20:00 | 654 | 652
2019-02-04 20:30 | 628 | 627
2019-02-04 21:00 | 589 | 588
2019-02-04 21:30 | 566 | 564
2019-02-04 22:00 | 551 | 548
2019-02-04 22:30 | 524 | 522
2019-02-04 23:00 | 511 | 510
2019-02-04 23:30 | 484 | 483
2019-02-05 | 459 | 458
2019-02-05 00:30 | 426 | 425
2019-02-05 01:00 | 410 | 409
2019-02-05 01:30 | 398 | 396
2019-02-05 02:00 | 379 | 377
2019-02-05 02:30 | 369 | 367
2019-02-05 03:00 | 363 | 360
2019-02-05 03:30 | 364 | 362
2019-02-05 04:00 | 370 | 368
2019-02-05 04:30 | 391 | 388
2019-02-05 05:00 | 399 | 397
2019-02-05 05:30 | 421 | 420
2019-02-05 06:00 | 446 | 445
2019-02-05 06:30 | 492 | 492
2019-02-05 07:00 | 525 | 525
2019-02-05 07:30 | 550 | 550
2019-02-05 08:00 | 567 | 565
2019-02-05 08:30 | 581 | 581
2019-02-05 09:00 | 590 | 589
2019-02-05 09:30 | 595 | 595
2019-02-05 10:00 | 589 | 588
2019-02-05 10:30 | 573 | 573
2019-02-05 11:00 | 568 | 567
2019-02-05 11:30 | 566 | 566
2019-02-05 12:00 | 569 | 569
2019-02-05 12:30 | 575 | 575
2019-02-05 13:00 | 592 | 592
2019-02-05 13:30 | 618 | 618
2019-02-05 14:00 | 640 | 639
2019-02-05 14:30 | 634 | 633
2019-02-05 15:00 | 638 | 636
2019-02-05 15:30 | 638 | 634
2019-02-05 16:00 | 641 | 638
2019-02-05 16:30 | 658 | 654
2019-02-05 17:00 | 669 | 666
2019-02-05 17:30 | 661 | 656
2019-02-05 18:00 | 643 | 638
2019-02-05 18:30 | 629 | 623
2019-02-05 19:00 | 637 | 631
2019-02-05 19:30 | 639 | 633
2019-02-05 20:00 | 620 | 614
2019-02-05 20:30 | 592 | 588
2019-02-05 21:00 | 556 | 553
2019-02-05 21:30 | 543 | 539
2019-02-05 22:00 | 529 | 524
2019-02-05 22:30 | 517 | 511
2019-02-05 23:00 | 503 | 502
2019-02-05 23:30 | 487 | 486
2019-02-06 | 451 | 449
2019-02-06 00:30 | 424 | 422
2019-02-06 01:00 | 411 | 410
2019-02-06 01:30 | 394 | 393
2019-02-06 02:00 | 385 | 384
2019-02-06 02:30 | 383 | 382
2019-02-06 03:00 | 383 | 382
2019-02-06 03:30 | 381 | 379
2019-02-06 04:00 | 378 | 376
2019-02-06 04:30 | 380 | 379
2019-02-06 05:00 | 395 | 394
2019-02-06 05:30 | 424 | 424
2019-02-06 06:00 | 443 | 442
2019-02-06 06:30 | 481 | 481
2019-02-06 07:00 | 516 | 516
2019-02-06 07:30 | 534 | 533
2019-02-06 08:00 | 538 | 537
2019-02-06 08:30 | 542 | 542
2019-02-06 09:00 | 538 | 538
2019-02-06 09:30 | 552 | 551
2019-02-06 10:00 | 558 | 558
2019-02-06 10:30 | 579 | 578
2019-02-06 11:00 | 583 | 583
2019-02-06 11:30 | 610 | 609
2019-02-06 12:00 | 611 | 611
2019-02-06 12:30 | 602 | 601
2019-02-06 13:00 | 602 | 601
2019-02-06 13:30 | 600 | 600
2019-02-06 14:00 | 611 | 611
2019-02-06 14:30 | 614 | 614
2019-02-06 15:00 | 616 | 616
2019-02-06 15:30 | 620 | 619
2019-02-06 16:00 | 659 | 658
2019-02-06 16:30 | 682 | 680
2019-02-06 17:00 | 685 | 680
2019-02-06 17:30 | 665 | 659
2019-02-06 18:00 | 654 | 648
2019-02-06 18:30 | 630 | 626
2019-02-06 19:00 | 631 | 629
2019-02-06 19:30 | 634 | 633
2019-02-06 20:00 | 631 | 630
2019-02-06 20:30 | 606 | 605
2019-02-06 21:00 | 583 | 583
2019-02-06 21:30 | 556 | 556
2019-02-06 22:00 | 537 | 537
2019-02-06 22:30 | 519 | 518
2019-02-06 23:00 | 506 | 506
2019-02-06 23:30 | 483 | 483
2019-02-07 | 456 | 455
2019-02-07 00:30 | 428 | 427
2019-02-07 01:00 | 414 | 413
2019-02-07 01:30 | 399 | 398
2019-02-07 02:00 | 383 | 382
2019-02-07 02:30 | 383 | 382
2019-02-07 03:00 | 384 | 383
2019-02-07 03:30 | 385 | 384
2019-02-07 04:00 | 380 | 379
2019-02-07 04:30 | 396 | 395
2019-02-07 05:00 | 401 | 400
2019-02-07 05:30 | 424 | 423
2019-02-07 06:00 | 448 | 447
2019-02-07 06:30 | 481 | 481
2019-02-07 07:00 | 533 | 533
2019-02-07 07:30 | 547 | 547
2019-02-07 08:00 | 566 | 565
2019-02-07 08:30 | 564 | 563
2019-02-07 09:00 | 585 | 584
2019-02-07 09:30 | 587 | 586
2019-02-07 10:00 | 597 | 593
2019-02-07 10:30 | 602 | 598
2019-02-07 11:00 | 611 | 608
2019-02-07 11:30 | 639 | 635
2019-02-07 12:00 | 628 | 624
2019-02-07 12:30 | 624 | 620
2019-02-07 13:00 | 633 | 629
2019-02-07 13:30 | 655 | 651
2019-02-07 14:00 | 654 | 651
2019-02-07 14:30 | 646 | 642
2019-02-07 15:00 | 659 | 655
2019-02-07 15:30 | 687 | 683
2019-02-07 16:00 | 691 | 686
2019-02-07 16:30 | 675 | 670
2019-02-07 17:00 | 665 | 659
2019-02-07 17:30 | 655 | 648
2019-02-07 18:00 | 644 | 640
2019-02-07 18:30 | 627 | 622
2019-02-07 19:00 | 636 | 633
2019-02-07 19:30 | 645 | 642
2019-02-07 20:00 | 645 | 642
2019-02-07 20:30 | 618 | 616
2019-02-07 21:00 | 581 | 581
2019-02-07 21:30 | 550 | 550
2019-02-07 22:00 | 529 | 529
2019-02-07 22:30 | 512 | 511
2019-02-07 23:00 | 501 | 501
2019-02-07 23:30 | 482 | 482
2019-02-08 | 457 | 457
2019-02-08 00:30 | 428 | 428
2019-02-08 01:00 | 411 | 411
2019-02-08 01:30 | 403 | 403
2019-02-08 02:00 | 401 | 400
2019-02-08 02:30 | 397 | 396
2019-02-08 03:00 | 393 | 392
2019-02-08 03:30 | 395 | 394
2019-02-08 04:00 | 389 | 387
2019-02-08 04:30 | 393 | 392
2019-02-08 05:00 | 399 | 398
2019-02-08 05:30 | 421 | 420
2019-02-08 06:00 | 437 | 437
2019-02-08 06:30 | 486 | 485
2019-02-08 07:00 | 523 | 522
2019-02-08 07:30 | 548 | 547
2019-02-08 08:00 | 558 | 557
2019-02-08 08:30 | 567 | 567
2019-02-08 09:00 | 574 | 574
2019-02-08 09:30 | 584 | 583
2019-02-08 10:00 | 580 | 578
2019-02-08 10:30 | 593 | 592
2019-02-08 11:00 | 576 | 575
2019-02-08 11:30 | 571 | 570
2019-02-08 12:00 | 585 | 584
2019-02-08 12:30 | 589 | 588
2019-02-08 13:00 | 598 | 597
2019-02-08 13:30 | 609 | 608
2019-02-08 14:00 | 613 | 612
2019-02-08 14:30 | 608 | 608
2019-02-08 15:00 | 621 | 621
2019-02-08 15:30 | 631 | 631
2019-02-08 16:00 | 653 | 653
2019-02-08 16:30 | 663 | 662
2019-02-08 17:00 | 649 | 649
2019-02-08 17:30 | 633 | 632
2019-02-08 18:00 | 612 | 610
2019-02-08 18:30 | 591 | 589
2019-02-08 19:00 | 593 | 593
2019-02-08 19:30 | 593 | 593
2019-02-08 20:00 | 592 | 591
2019-02-08 20:30 | 566 | 565
2019-02-08 21:00 | 555 | 554
2019-02-08 21:30 | 548 | 546
2019-02-08 22:00 | 526 | 523
2019-02-08 22:30 | 510 | 509
2019-02-08 23:00 | 506 | 506
2019-02-08 23:30 | 482 | 481
2019-02-09 | 445 | 444
2019-02-09 00:30 | 410 | 409
2019-02-09 01:00 | 402 | 400
2019-02-09 01:30 | 371 | 370
2019-02-09 02:00 | 358 | 357
2019-02-09 02:30 | 351 | 349
2019-02-09 03:00 | 341 | 340
2019-02-09 03:30 | 340 | 338
2019-02-09 04:00 | 338 | 335
2019-02-09 04:30 | 331 | 329
2019-02-09 05:00 | 331 | 328
2019-02-09 05:30 | 338 | 335
2019-02-09 06:00 | 343 | 340
2019-02-09 06:30 | 349 | 347
2019-02-09 07:00 | 356 | 355
2019-02-09 07:30 | 382 | 382
2019-02-09 08:00 | 402 | 401
2019-02-09 08:30 | 440 | 437
2019-02-09 09:00 | 440 | 438
2019-02-09 09:30 | 436 | 434
2019-02-09 10:00 | 453 | 452
2019-02-09 10:30 | 459 | 458
2019-02-09 11:00 | 470 | 469
2019-02-09 11:30 | 481 | 480
2019-02-09 12:00 | 483 | 482
2019-02-09 12:30 | 487 | 486
2019-02-09 13:00 | 497 | 496
2019-02-09 13:30 | 513 | 512
2019-02-09 14:00 | 522 | 521
2019-02-09 14:30 | 531 | 529
2019-02-09 15:00 | 562 | 560
2019-02-09 15:30 | 576 | 575
2019-02-09 16:00 | 599 | 596
2019-02-09 16:30 | 609 | 606
2019-02-09 17:00 | 628 | 626
2019-02-09 17:30 | 626 | 624
2019-02-09 18:00 | 629 | 626
2019-02-09 18:30 | 628 | 624
2019-02-09 19:00 | 642 | 638
2019-02-09 19:30 | 646 | 643
2019-02-09 20:00 | 631 | 627
2019-02-09 20:30 | 601 | 600
2019-02-09 21:00 | 574 | 573
2019-02-09 21:30 | 555 | 553
2019-02-09 22:00 | 536 | 535
2019-02-09 22:30 | 523 | 521
2019-02-09 23:00 | 509 | 508
2019-02-09 23:30 | 465 | 465
2019-02-10 | 441 | 440
2019-02-10 00:30 | 404 | 404
2019-02-10 01:00 | 378 | 378
2019-02-10 01:30 | 367 | 367
2019-02-10 02:00 | 358 | 357
2019-02-10 02:30 | 350 | 349
2019-02-10 03:00 | 346 | 346
2019-02-10 03:30 | 332 | 331
2019-02-10 04:00 | 327 | 325
2019-02-10 04:30 | 324 | 322
2019-02-10 05:00 | 311 | 310
2019-02-10 05:30 | 313 | 311
2019-02-10 06:00 | 321 | 319
2019-02-10 06:30 | 335 | 334
2019-02-10 07:00 | 349 | 349
2019-02-10 07:30 | 375 | 375
2019-02-10 08:00 | 392 | 392
2019-02-10 08:30 | 406 | 406
2019-02-10 09:00 | 425 | 424
2019-02-10 09:30 | 444 | 443
2019-02-10 10:00 | 476 | 473
2019-02-10 10:30 | 484 | 479
2019-02-10 11:00 | 482 | 478
2019-02-10 11:30 | 477 | 473
2019-02-10 12:00 | 476 | 472
2019-02-10 12:30 | 492 | 489
2019-02-10 13:00 | 496 | 493
2019-02-10 13:30 | 501 | 499
2019-02-10 14:00 | 514 | 512
2019-02-10 14:30 | 521 | 520
2019-02-10 15:00 | 534 | 532
2019-02-10 15:30 | 551 | 549
2019-02-10 16:00 | 577 | 575
2019-02-10 16:30 | 588 | 584
2019-02-10 17:00 | 593 | 589
2019-02-10 17:30 | 600 | 596
2019-02-10 18:00 | 598 | 592
2019-02-10 18:30 | 592 | 587
2019-02-10 19:00 | 597 | 593
2019-02-10 19:30 | 593 | 588
2019-02-10 20:00 | 576 | 573
2019-02-10 20:30 | 550 | 549
2019-02-10 21:00 | 529 | 529
2019-02-10 21:30 | 505 | 505
2019-02-10 22:00 | 495 | 495
2019-02-10 22:30 | 473 | 473
2019-02-10 23:00 | 458 | 458
2019-02-10 23:30 | 440 | 440
2019-02-11 | 412 | 412
2019-02-11 00:30 | 389 | 389
2019-02-11 01:00 | 383 | 383
2019-02-11 01:30 | 379 | 379
2019-02-11 02:00 | 380 | 379
2019-02-11 02:30 | 370 | 370
2019-02-11 03:00 | 370 | 370
2019-02-11 03:30 | 375 | 375
2019-02-11 04:00 | 370 | 369
2019-02-11 04:30 | 372 | 372
2019-02-11 05:00 | 370 | 370
2019-02-11 05:30 | 388 | 387
2019-02-11 06:00 | 424 | 424
2019-02-11 06:30 | 464 | 464
2019-02-11 07:00 | 497 | 497
2019-02-11 07:30 | 523 | 523
2019-02-11 08:00 | 527 | 527
2019-02-11 08:30 | 537 | 537
2019-02-11 09:00 | 546 | 546
2019-02-11 09:30 | 549 | 549
2019-02-11 10:00 | 536 | 535
2019-02-11 10:30 | 526 | 526
2019-02-11 11:00 | 526 | 526
2019-02-11 11:30 | 533 | 533
2019-02-11 12:00 | 543 | 543
2019-02-11 12:30 | 542 | 542
2019-02-11 13:00 | 555 | 555
2019-02-11 13:30 | 577 | 577
2019-02-11 14:00 | 591 | 591
2019-02-11 14:30 | 609 | 609
2019-02-11 15:00 | 623 | 623
2019-02-11 15:30 | 643 | 643
2019-02-11 16:00 | 669 | 669
2019-02-11 16:30 | 682 | 681
2019-02-11 17:00 | 695 | 695
2019-02-11 17:30 | 692 | 692
2019-02-11 18:00 | 677 | 675
2019-02-11 18:30 | 654 | 654
2019-02-11 19:00 | 634 | 634
2019-02-11 19:30 | 639 | 639
2019-02-11 20:00 | 629 | 628
2019-02-11 20:30 | 607 | 606
2019-02-11 21:00 | 574 | 574
2019-02-11 21:30 | 549 | 548
2019-02-11 22:00 | 518 | 517
2019-02-11 22:30 | 478 | 477
2019-02-11 23:00 | 458 | 457
2019-02-11 23:30 | 429 | 428
2019-02-12 | 404 | 404
2019-02-12 00:30 | 375 | 375
2019-02-12 01:00 | 359 | 359
2019-02-12 01:30 | 349 | 349
2019-02-12 02:00 | 330 | 330
2019-02-12 02:30 | 341 | 341
2019-02-12 03:00 | 337 | 337
2019-02-12 03:30 | 325 | 324
2019-02-12 04:00 | 336 | 335
2019-02-12 04:30 | 349 | 349
2019-02-12 05:00 | 353 | 353
2019-02-12 05:30 | 379 | 379
2019-02-12 06:00 | 399 | 399
2019-02-12 06:30 | 452 | 452
2019-02-12 07:00 | 495 | 495
2019-02-12 07:30 | 516 | 516
2019-02-12 08:00 | 528 | 528
2019-02-12 08:30 | 542 | 541
2019-02-12 09:00 | 563 | 563
2019-02-12 09:30 | 580 | 580
2019-02-12 10:00 | 576 | 575
2019-02-12 10:30 | 582 | 580
2019-02-12 11:00 | 598 | 595
2019-02-12 11:30 | 607 | 605
2019-02-12 12:00 | 625 | 624
2019-02-12 12:30 | 649 | 648
2019-02-12 13:00 | 674 | 673
2019-02-12 13:30 | 704 | 703
2019-02-12 14:00 | 730 | 730
2019-02-12 14:30 | 754 | 753
2019-02-12 15:00 | 770 | 770
2019-02-12 15:30 | 799 | 798
2019-02-12 16:00 | 821 | 820
2019-02-12 16:30 | 844 | 843
2019-02-12 17:00 | 860 | 860
2019-02-12 17:30 | 854 | 853
2019-02-12 18:00 | 836 | 835
2019-02-12 18:30 | 799 | 797
2019-02-12 19:00 | 800 | 799
2019-02-12 19:30 | 789 | 788
2019-02-12 20:00 | 768 | 767
2019-02-12 20:30 | 741 | 739
2019-02-12 21:00 | 713 | 709
2019-02-12 21:30 | 663 | 660
2019-02-12 22:00 | 626 | 621
2019-02-12 22:30 | 585 | 583
2019-02-12 23:00 | 557 | 557
2019-02-12 23:30 | 519 | 519
2019-02-13 | 488 | 488
2019-02-13 00:30 | 454 | 454
2019-02-13 01:00 | 439 | 439
2019-02-13 01:30 | 429 | 429
2019-02-13 02:00 | 414 | 414
2019-02-13 02:30 | 402 | 402
2019-02-13 03:00 | 388 | 388
2019-02-13 03:30 | 382 | 382
2019-02-13 04:00 | 368 | 368
2019-02-13 04:30 | 370 | 370
2019-02-13 05:00 | 377 | 377
2019-02-13 05:30 | 406 | 406
2019-02-13 06:00 | 446 | 446
2019-02-13 06:30 | 502 | 502
2019-02-13 07:00 | 538 | 537
2019-02-13 07:30 | 563 | 563
2019-02-13 08:00 | 593 | 593
2019-02-13 08:30 | 607 | 607
2019-02-13 09:00 | 619 | 618
2019-02-13 09:30 | 625 | 624
2019-02-13 10:00 | 632 | 631
2019-02-13 10:30 | 645 | 645
2019-02-13 11:00 | 659 | 659
2019-02-13 11:30 | 671 | 671
2019-02-13 12:00 | 691 | 691
2019-02-13 12:30 | 703 | 702
2019-02-13 13:00 | 730 | 729
2019-02-13 13:30 | 756 | 755
2019-02-13 14:00 | 770 | 769
2019-02-13 14:30 | 793 | 792
2019-02-13 15:00 | 795 | 794
2019-02-13 15:30 | 806 | 805
2019-02-13 16:00 | 853 | 849
2019-02-13 16:30 | 863 | 859
2019-02-13 17:00 | 888 | 883
2019-02-13 17:30 | 890 | 882
2019-02-13 18:00 | 872 | 863
2019-02-13 18:30 | 839 | 830
2019-02-13 19:00 | 827 | 819
2019-02-13 19:30 | 812 | 804
2019-02-13 20:00 | 794 | 791
2019-02-13 20:30 | 787 | 785
2019-02-13 21:00 | 757 | 754
2019-02-13 21:30 | 711 | 707
2019-02-13 22:00 | 672 | 669
2019-02-13 22:30 | 600 | 596
2019-02-13 23:00 | 571 | 567
2019-02-13 23:30 | 541 | 537
2019-02-14 | 507 | 505
2019-02-14 00:30 | 481 | 479
2019-02-14 01:00 | 463 | 461
2019-02-14 01:30 | 434 | 434
2019-02-14 02:00 | 420 | 420
2019-02-14 02:30 | 406 | 406
2019-02-14 03:00 | 399 | 399
2019-02-14 03:30 | 391 | 391
2019-02-14 04:00 | 392 | 392
2019-02-14 04:30 | 395 | 395
2019-02-14 05:00 | 401 | 401
2019-02-14 05:30 | 426 | 426
2019-02-14 06:00 | 452 | 452
2019-02-14 06:30 | 498 | 498
2019-02-14 07:00 | 546 | 544
2019-02-14 07:30 | 567 | 566
2019-02-14 08:00 | 578 | 578
2019-02-14 08:30 | 589 | 587
2019-02-14 09:00 | 597 | 594
2019-02-14 09:30 | 600 | 597
2019-02-14 10:00 | 595 | 593
2019-02-14 10:30 | 598 | 595
2019-02-14 11:00 | 598 | 596
2019-02-14 11:30 | 589 | 587
2019-02-14 12:00 | 588 | 586
2019-02-14 12:30 | 581 | 580
2019-02-14 13:00 | 591 | 590
2019-02-14 13:30 | 614 | 613
2019-02-14 14:00 | 623 | 623
2019-02-14 14:30 | 627 | 627
2019-02-14 15:00 | 616 | 615
2019-02-14 15:30 | 606 | 605
2019-02-14 16:00 | 612 | 611
2019-02-14 16:30 | 616 | 614
2019-02-14 17:00 | 616 | 613
2019-02-14 17:30 | 605 | 601
2019-02-14 18:00 | 595 | 590
2019-02-14 18:30 | 567 | 563
2019-02-14 19:00 | 569 | 567
2019-02-14 19:30 | 565 | 564
2019-02-14 20:00 | 550 | 548
2019-02-14 20:30 | 521 | 519
2019-02-14 21:00 | 498 | 497
2019-02-14 21:30 | 474 | 473
2019-02-14 22:00 | 455 | 455
2019-02-14 22:30 | 434 | 434
2019-02-14 23:00 | 422 | 422
2019-02-14 23:30 | 400 | 400
2019-02-15 | 370 | 370
2019-02-15 00:30 | 354 | 354
2019-02-15 01:00 | 346 | 346
2019-02-15 01:30 | 339 | 339
2019-02-15 02:00 | 334 | 334
2019-02-15 02:30 | 335 | 334
2019-02-15 03:00 | 328 | 327
2019-02-15 03:30 | 328 | 326
2019-02-15 04:00 | 326 | 324
2019-02-15 04:30 | 334 | 333
2019-02-15 05:00 | 340 | 339
2019-02-15 05:30 | 362 | 361
2019-02-15 06:00 | 379 | 379
2019-02-15 06:30 | 416 | 416
2019-02-15 07:00 | 448 | 448
2019-02-15 07:30 | 465 | 465
2019-02-15 08:00 | 474 | 474
2019-02-15 08:30 | 480 | 480
2019-02-15 09:00 | 488 | 488
2019-02-15 09:30 | 501 | 501
2019-02-15 10:00 | 505 | 505
2019-02-15 10:30 | 502 | 502
2019-02-15 11:00 | 504 | 504
2019-02-15 11:30 | 511 | 511
2019-02-15 12:00 | 526 | 526
2019-02-15 12:30 | 530 | 530
2019-02-15 13:00 | 528 | 528
2019-02-15 13:30 | 529 | 529
2019-02-15 14:00 | 534 | 534
2019-02-15 14:30 | 541 | 541
2019-02-15 15:00 | 549 | 549
2019-02-15 15:30 | 561 | 561
2019-02-15 16:00 | 582 | 582
2019-02-15 16:30 | 599 | 599
2019-02-15 17:00 | 597 | 597
2019-02-15 17:30 | 578 | 578
2019-02-15 18:00 | 562 | 562
2019-02-15 18:30 | 536 | 536
2019-02-15 19:00 | 537 | 537
2019-02-15 19:30 | 526 | 526
2019-02-15 20:00 | 515 | 513
2019-02-15 20:30 | 480 | 480
2019-02-15 21:00 | 460 | 460
2019-02-15 21:30 | 441 | 441
2019-02-15 22:00 | 428 | 428
2019-02-15 22:30 | 420 | 419
2019-02-15 23:00 | 414 | 414
2019-02-15 23:30 | 390 | 390
2019-02-16 | 370 | 370
2019-02-16 00:30 | 351 | 351
2019-02-16 01:00 | 340 | 339
2019-02-16 01:30 | 329 | 327
2019-02-16 02:00 | 322 | 320
2019-02-16 02:30 | 318 | 316
2019-02-16 03:00 | 319 | 316
2019-02-16 03:30 | 309 | 306
2019-02-16 04:00 | 300 | 297
2019-02-16 04:30 | 306 | 304
2019-02-16 05:00 | 304 | 301
2019-02-16 05:30 | 307 | 304
2019-02-16 06:00 | 314 | 311
2019-02-16 06:30 | 330 | 328
2019-02-16 07:00 | 340 | 339
2019-02-16 07:30 | 361 | 360
2019-02-16 08:00 | 373 | 373
2019-02-16 08:30 | 388 | 388
2019-02-16 09:00 | 394 | 394
2019-02-16 09:30 | 402 | 402
2019-02-16 10:00 | 421 | 420
2019-02-16 10:30 | 434 | 434
2019-02-16 11:00 | 442 | 442
2019-02-16 11:30 | 432 | 432
2019-02-16 12:00 | 435 | 435
2019-02-16 12:30 | 444 | 444
2019-02-16 13:00 | 448 | 448
2019-02-16 13:30 | 454 | 454
2019-02-16 14:00 | 456 | 456
2019-02-16 14:30 | 463 | 463
2019-02-16 15:00 | 477 | 477
2019-02-16 15:30 | 476 | 476
2019-02-16 16:00 | 490 | 490
2019-02-16 16:30 | 504 | 504
2019-02-16 17:00 | 515 | 515
2019-02-16 17:30 | 501 | 501
2019-02-16 18:00 | 487 | 487
2019-02-16 18:30 | 481 | 480
2019-02-16 19:00 | 491 | 491
2019-02-16 19:30 | 483 | 483
2019-02-16 20:00 | 477 | 477
2019-02-16 20:30 | 469 | 469
2019-02-16 21:00 | 443 | 443
2019-02-16 21:30 | 432 | 432
2019-02-16 22:00 | 416 | 416
2019-02-16 22:30 | 418 | 417
2019-02-16 23:00 | 403 | 403
2019-02-16 23:30 | 381 | 380
2019-02-17 | 358 | 356
2019-02-17 00:30 | 339 | 336
2019-02-17 01:00 | 334 | 329
2019-02-17 01:30 | 328 | 323
2019-02-17 02:00 | 327 | 320
2019-02-17 02:30 | 323 | 315
2019-02-17 03:00 | 325 | 316
2019-02-17 03:30 | 317 | 308
2019-02-17 04:00 | 307 | 298
2019-02-17 04:30 | 290 | 280
2019-02-17 05:00 | 287 | 277
2019-02-17 05:30 | 301 | 290
2019-02-17 06:00 | 304 | 292
2019-02-17 06:30 | 311 | 301
2019-02-17 07:00 | 319 | 310
2019-02-17 07:30 | 329 | 322
2019-02-17 08:00 | 335 | 330
2019-02-17 08:30 | 345 | 342
2019-02-17 09:00 | 351 | 349
2019-02-17 09:30 | 367 | 365
2019-02-17 10:00 | 386 | 385
2019-02-17 10:30 | 397 | 396
2019-02-17 11:00 | 400 | 400
2019-02-17 11:30 | 410 | 409
2019-02-17 12:00 | 421 | 420
2019-02-17 12:30 | 413 | 411
2019-02-17 13:00 | 420 | 419
2019-02-17 13:30 | 426 | 425
2019-02-17 14:00 | 440 | 439
2019-02-17 14:30 | 455 | 454
2019-02-17 15:00 | 472 | 471
2019-02-17 15:30 | 496 | 495
2019-02-17 16:00 | 522 | 522
2019-02-17 16:30 | 556 | 556
2019-02-17 17:00 | 578 | 577
2019-02-17 17:30 | 573 | 572
2019-02-17 18:00 | 565 | 564
2019-02-17 18:30 | 555 | 555
2019-02-17 19:00 | 555 | 555
2019-02-17 19:30 | 554 | 553
2019-02-17 20:00 | 544 | 543
2019-02-17 20:30 | 511 | 511
2019-02-17 21:00 | 477 | 477
2019-02-17 21:30 | 458 | 458
2019-02-17 22:00 | 438 | 438
2019-02-17 22:30 | 418 | 418
2019-02-17 23:00 | 402 | 402
2019-02-17 23:30 | 379 | 378
2019-02-18 | 350 | 349
2019-02-18 00:30 | 329 | 327
2019-02-18 01:00 | 331 | 328
2019-02-18 01:30 | 325 | 322
2019-02-18 02:00 | 321 | 317
2019-02-18 02:30 | 325 | 321
2019-02-18 03:00 | 317 | 312
2019-02-18 03:30 | 314 | 310
2019-02-18 04:00 | 314 | 309
2019-02-18 04:30 | 322 | 318
2019-02-18 05:00 | 328 | 325
2019-02-18 05:30 | 355 | 352
2019-02-18 06:00 | 379 | 378
2019-02-18 06:30 | 413 | 413
2019-02-18 07:00 | 449 | 448
2019-02-18 07:30 | 479 | 479
2019-02-18 08:00 | 492 | 492
2019-02-18 08:30 | 507 | 506
2019-02-18 09:00 | 524 | 521
2019-02-18 09:30 | 545 | 543
2019-02-18 10:00 | 551 | 548
2019-02-18 10:30 | 535 | 532
2019-02-18 11:00 | 521 | 517
2019-02-18 11:30 | 526 | 523
2019-02-18 12:00 | 528 | 526
2019-02-18 12:30 | 529 | 526
2019-02-18 13:00 | 534 | 532
2019-02-18 13:30 | 547 | 545
2019-02-18 14:00 | 558 | 556
2019-02-18 14:30 | 573 | 571
2019-02-18 15:00 | 588 | 584
2019-02-18 15:30 | 613 | 609
2019-02-18 16:00 | 639 | 635
2019-02-18 16:30 | 658 | 655
2019-02-18 17:00 | 669 | 666
2019-02-18 17:30 | 674 | 671
2019-02-18 18:00 | 660 | 654
2019-02-18 18:30 | 623 | 618
2019-02-18 19:00 | 620 | 618
2019-02-18 19:30 | 607 | 604
2019-02-18 20:00 | 583 | 580
2019-02-18 20:30 | 561 | 559
2019-02-18 21:00 | 526 | 526
2019-02-18 21:30 | 497 | 497
2019-02-18 22:00 | 471 | 470
2019-02-18 22:30 | 444 | 444
2019-02-18 23:00 | 433 | 433
2019-02-18 23:30 | 410 | 409
2019-02-19 | 380 | 379
2019-02-19 00:30 | 361 | 361
2019-02-19 01:00 | 349 | 349
2019-02-19 01:30 | 345 | 344
2019-02-19 02:00 | 341 | 340
2019-02-19 02:30 | 339 | 338
2019-02-19 03:00 | 332 | 331
2019-02-19 03:30 | 323 | 322
2019-02-19 04:00 | 328 | 327
2019-02-19 04:30 | 337 | 336
2019-02-19 05:00 | 341 | 341
2019-02-19 05:30 | 373 | 372
2019-02-19 06:00 | 402 | 401
2019-02-19 06:30 | 444 | 444
2019-02-19 07:00 | 480 | 480
2019-02-19 07:30 | 505 | 505
2019-02-19 08:00 | 516 | 516
2019-02-19 08:30 | 523 | 523
2019-02-19 09:00 | 524 | 524
2019-02-19 09:30 | 532 | 532
2019-02-19 10:00 | 530 | 530
2019-02-19 10:30 | 529 | 529
2019-02-19 11:00 | 533 | 533
2019-02-19 11:30 | 544 | 544
2019-02-19 12:00 | 558 | 558
2019-02-19 12:30 | 563 | 563
2019-02-19 13:00 | 586 | 584
2019-02-19 13:30 | 617 | 614
2019-02-19 14:00 | 634 | 631
2019-02-19 14:30 | 656 | 654
2019-02-19 15:00 | 672 | 669
2019-02-19 15:30 | 695 | 692
2019-02-19 16:00 | 726 | 724
2019-02-19 16:30 | 749 | 747
2019-02-19 17:00 | 750 | 749
2019-02-19 17:30 | 738 | 735
2019-02-19 18:00 | 732 | 728
2019-02-19 18:30 | 701 | 698
2019-02-19 19:00 | 698 | 696
2019-02-19 19:30 | 690 | 688
2019-02-19 20:00 | 669 | 668
2019-02-19 20:30 | 641 | 641
2019-02-19 21:00 | 610 | 609
2019-02-19 21:30 | 578 | 577
2019-02-19 22:00 | 543 | 543
2019-02-19 22:30 | 511 | 511
2019-02-19 23:00 | 504 | 504
2019-02-19 23:30 | 472 | 471
2019-02-20 | 438 | 436
2019-02-20 00:30 | 411 | 409
2019-02-20 01:00 | 392 | 389
2019-02-20 01:30 | 373 | 370
2019-02-20 02:00 | 358 | 356
2019-02-20 02:30 | 350 | 350
2019-02-20 03:00 | 350 | 349
2019-02-20 03:30 | 347 | 346
2019-02-20 04:00 | 345 | 344
2019-02-20 04:30 | 355 | 354
2019-02-20 05:00 | 361 | 360
2019-02-20 05:30 | 385 | 385
2019-02-20 06:00 | 416 | 416
2019-02-20 06:30 | 478 | 478
2019-02-20 07:00 | 532 | 531
2019-02-20 07:30 | 551 | 551
2019-02-20 08:00 | 561 | 561
2019-02-20 08:30 | 567 | 567
2019-02-20 09:00 | 575 | 575
2019-02-20 09:30 | 577 | 577
2019-02-20 10:00 | 577 | 577
2019-02-20 10:30 | 576 | 576
2019-02-20 11:00 | 575 | 575
2019-02-20 11:30 | 584 | 584
2019-02-20 12:00 | 593 | 593
2019-02-20 12:30 | 606 | 606
2019-02-20 13:00 | 621 | 621
2019-02-20 13:30 | 627 | 627
2019-02-20 14:00 | 628 | 627
2019-02-20 14:30 | 641 | 641
2019-02-20 15:00 | 661 | 658
2019-02-20 15:30 | 686 | 683
2019-02-20 16:00 | 713 | 709
2019-02-20 16:30 | 737 | 733
2019-02-20 17:00 | 751 | 747
2019-02-20 17:30 | 748 | 744
2019-02-20 18:00 | 740 | 734
2019-02-20 18:30 | 716 | 711
2019-02-20 19:00 | 714 | 710
2019-02-20 19:30 | 706 | 701
2019-02-20 20:00 | 673 | 668
2019-02-20 20:30 | 660 | 654
2019-02-20 21:00 | 622 | 617
2019-02-20 21:30 | 594 | 590
2019-02-20 22:00 | 549 | 548
2019-02-20 22:30 | 523 | 521
2019-02-20 23:00 | 509 | 506
2019-02-20 23:30 | 479 | 476
2019-02-21 | 443 | 439
2019-02-21 00:30 | 415 | 412
2019-02-21 01:00 | 396 | 396
2019-02-21 01:30 | 386 | 386
2019-02-21 02:00 | 383 | 382
2019-02-21 02:30 | 379 | 379
2019-02-21 03:00 | 377 | 376
2019-02-21 03:30 | 374 | 373
2019-02-21 04:00 | 370 | 369
2019-02-21 04:30 | 373 | 372
2019-02-21 05:00 | 377 | 377
2019-02-21 05:30 | 400 | 400
2019-02-21 06:00 | 420 | 419
2019-02-21 06:30 | 474 | 474
2019-02-21 07:00 | 516 | 516
2019-02-21 07:30 | 539 | 539
2019-02-21 08:00 | 545 | 545
2019-02-21 08:30 | 567 | 567
2019-02-21 09:00 | 575 | 575
2019-02-21 09:30 | 577 | 577
2019-02-21 10:00 | 589 | 588
2019-02-21 10:30 | 599 | 599
2019-02-21 11:00 | 614 | 614
2019-02-21 11:30 | 606 | 606
2019-02-21 12:00 | 617 | 617
2019-02-21 12:30 | 596 | 596
2019-02-21 13:00 | 596 | 596
2019-02-21 13:30 | 616 | 616
2019-02-21 14:00 | 631 | 631
2019-02-21 14:30 | 632 | 631
2019-02-21 15:00 | 649 | 647
2019-02-21 15:30 | 664 | 662
2019-02-21 16:00 | 694 | 692
2019-02-21 16:30 | 715 | 713
2019-02-21 17:00 | 730 | 727
2019-02-21 17:30 | 730 | 727
2019-02-21 18:00 | 714 | 710
2019-02-21 18:30 | 682 | 678
2019-02-21 19:00 | 691 | 687
2019-02-21 19:30 | 679 | 674
2019-02-21 20:00 | 665 | 658
2019-02-21 20:30 | 623 | 617
2019-02-21 21:00 | 601 | 597
2019-02-21 21:30 | 567 | 562
2019-02-21 22:00 | 523 | 520
2019-02-21 22:30 | 488 | 487
2019-02-21 23:00 | 477 | 475
2019-02-21 23:30 | 451 | 449
2019-02-22 | 418 | 417
2019-02-22 00:30 | 399 | 398
2019-02-22 01:00 | 386 | 385
2019-02-22 01:30 | 359 | 358
2019-02-22 02:00 | 339 | 338
2019-02-22 02:30 | 338 | 336
2019-02-22 03:00 | 336 | 335
2019-02-22 03:30 | 333 | 331
2019-02-22 04:00 | 330 | 328
2019-02-22 04:30 | 331 | 329
2019-02-22 05:00 | 338 | 337
2019-02-22 05:30 | 377 | 377
2019-02-22 06:00 | 397 | 397
2019-02-22 06:30 | 450 | 450
2019-02-22 07:00 | 489 | 489
2019-02-22 07:30 | 509 | 509
2019-02-22 08:00 | 523 | 523
2019-02-22 08:30 | 528 | 528
2019-02-22 09:00 | 518 | 518
2019-02-22 09:30 | 519 | 519
2019-02-22 10:00 | 523 | 523
2019-02-22 10:30 | 518 | 518
2019-02-22 11:00 | 508 | 508
2019-02-22 11:30 | 483 | 483
2019-02-22 12:00 | 488 | 488
2019-02-22 12:30 | 540 | 540
2019-02-22 13:00 | 540 | 540
2019-02-22 13:30 | 506 | 506
2019-02-22 14:00 | 478 | 478
2019-02-22 14:30 | 497 | 496
2019-02-22 15:00 | 496 | 496
2019-02-22 15:30 | 519 | 519
2019-02-22 16:00 | 536 | 536
2019-02-22 16:30 | 540 | 539
2019-02-22 17:00 | 560 | 559
2019-02-22 17:30 | 554 | 553
2019-02-22 18:00 | 529 | 528
2019-02-22 18:30 | 507 | 506
2019-02-22 19:00 | 515 | 514
2019-02-22 19:30 | 510 | 509
2019-02-22 20:00 | 502 | 501
2019-02-22 20:30 | 497 | 497
2019-02-22 21:00 | 477 | 477
2019-02-22 21:30 | 467 | 467
2019-02-22 22:00 | 453 | 453
2019-02-22 22:30 | 440 | 440
2019-02-22 23:00 | 429 | 429
2019-02-22 23:30 | 412 | 411
2019-02-23 | 395 | 393
2019-02-23 00:30 | 372 | 369
2019-02-23 01:00 | 359 | 356
2019-02-23 01:30 | 348 | 344
2019-02-23 02:00 | 342 | 338
2019-02-23 02:30 | 333 | 328
2019-02-23 03:00 | 332 | 327
2019-02-23 03:30 | 331 | 326
2019-02-23 04:00 | 323 | 318
2019-02-23 04:30 | 323 | 318
2019-02-23 05:00 | 321 | 317
2019-02-23 05:30 | 344 | 339
2019-02-23 06:00 | 351 | 346
2019-02-23 06:30 | 376 | 371
2019-02-23 07:00 | 397 | 393
2019-02-23 07:30 | 415 | 412
2019-02-23 08:00 | 403 | 400
2019-02-23 08:30 | 391 | 390
2019-02-23 09:00 | 396 | 395
2019-02-23 09:30 | 408 | 408
2019-02-23 10:00 | 412 | 412
2019-02-23 10:30 | 415 | 415
2019-02-23 11:00 | 402 | 400
2019-02-23 11:30 | 416 | 414
2019-02-23 12:00 | 413 | 412
2019-02-23 12:30 | 415 | 413
2019-02-23 13:00 | 422 | 420
2019-02-23 13:30 | 422 | 422
2019-02-23 14:00 | 422 | 422
2019-02-23 14:30 | 422 | 422
2019-02-23 15:00 | 427 | 427
2019-02-23 15:30 | 425 | 425
2019-02-23 16:00 | 458 | 458
2019-02-23 16:30 | 475 | 475
2019-02-23 17:00 | 498 | 498
2019-02-23 17:30 | 500 | 500
2019-02-23 18:00 | 501 | 501
2019-02-23 18:30 | 500 | 499
2019-02-23 19:00 | 511 | 511
2019-02-23 19:30 | 514 | 514
2019-02-23 20:00 | 497 | 496
2019-02-23 20:30 | 483 | 483
2019-02-23 21:00 | 465 | 465
2019-02-23 21:30 | 443 | 443
2019-02-23 22:00 | 436 | 435
2019-02-23 22:30 | 421 | 420
2019-02-23 23:00 | 410 | 408
2019-02-23 23:30 | 391 | 389
2019-02-24 | 373 | 370
2019-02-24 00:30 | 360 | 355
2019-02-24 01:00 | 354 | 348
2019-02-24 01:30 | 342 | 335
2019-02-24 02:00 | 318 | 310
2019-02-24 02:30 | 311 | 303
2019-02-24 03:00 | 313 | 305
2019-02-24 03:30 | 311 | 302
2019-02-24 04:00 | 310 | 300
2019-02-24 04:30 | 310 | 299
2019-02-24 05:00 | 308 | 297
2019-02-24 05:30 | 314 | 304
2019-02-24 06:00 | 323 | 312
2019-02-24 06:30 | 333 | 322
2019-02-24 07:00 | 340 | 331
2019-02-24 07:30 | 353 | 347
2019-02-24 08:00 | 366 | 361
2019-02-24 08:30 | 374 | 370
2019-02-24 09:00 | 390 | 388
2019-02-24 09:30 | 396 | 394
2019-02-24 10:00 | 409 | 408
2019-02-24 10:30 | 406 | 405
2019-02-24 11:00 | 409 | 407
2019-02-24 11:30 | 420 | 419
2019-02-24 12:00 | 403 | 401
2019-02-24 12:30 | 399 | 398
2019-02-24 13:00 | 404 | 403
2019-02-24 13:30 | 401 | 400
2019-02-24 14:00 | 407 | 406
2019-02-24 14:30 | 419 | 418
2019-02-24 15:00 | 423 | 423
2019-02-24 15:30 | 429 | 428
2019-02-24 16:00 | 440 | 440
2019-02-24 16:30 | 463 | 463
2019-02-24 17:00 | 481 | 481
2019-02-24 17:30 | 483 | 483
2019-02-24 18:00 | 486 | 485
2019-02-24 18:30 | 500 | 499
2019-02-24 19:00 | 514 | 514
2019-02-24 19:30 | 513 | 512
2019-02-24 20:00 | 505 | 504
2019-02-24 20:30 | 482 | 481
2019-02-24 21:00 | 453 | 453
2019-02-24 21:30 | 454 | 453
2019-02-24 22:00 | 442 | 440
2019-02-24 22:30 | 432 | 432
2019-02-24 23:00 | 419 | 418
2019-02-24 23:30 | 399 | 397
2019-02-25 | 389 | 387
2019-02-25 00:30 | 368 | 365
2019-02-25 01:00 | 363 | 358
2019-02-25 01:30 | 356 | 350
2019-02-25 02:00 | 345 | 339
2019-02-25 02:30 | 345 | 338
2019-02-25 03:00 | 342 | 335
2019-02-25 03:30 | 344 | 337
2019-02-25 04:00 | 342 | 336
2019-02-25 04:30 | 345 | 339
2019-02-25 05:00 | 353 | 349
2019-02-25 05:30 | 376 | 372
2019-02-25 06:00 | 413 | 410
2019-02-25 06:30 | 449 | 449
2019-02-25 07:00 | 488 | 487
2019-02-25 07:30 | 513 | 513
2019-02-25 08:00 | 520 | 520
2019-02-25 08:30 | 524 | 524
2019-02-25 09:00 | 528 | 528
2019-02-25 09:30 | 526 | 526
2019-02-25 10:00 | 528 | 528
2019-02-25 10:30 | 522 | 521
2019-02-25 11:00 | 523 | 523
2019-02-25 11:30 | 527 | 527
2019-02-25 12:00 | 523 | 523
2019-02-25 12:30 | 530 | 529
2019-02-25 13:00 | 520 | 520
2019-02-25 13:30 | 529 | 528
2019-02-25 14:00 | 532 | 532
2019-02-25 14:30 | 539 | 538
2019-02-25 15:00 | 547 | 547
2019-02-25 15:30 | 536 | 536
2019-02-25 16:00 | 535 | 535
2019-02-25 16:30 | 559 | 559
2019-02-25 17:00 | 571 | 570
2019-02-25 17:30 | 573 | 573
2019-02-25 18:00 | 565 | 564
2019-02-25 18:30 | 557 | 555
2019-02-25 19:00 | 569 | 569
2019-02-25 19:30 | 542 | 541
2019-02-25 20:00 | 534 | 534
2019-02-25 20:30 | 523 | 523
2019-02-25 21:00 | 492 | 492
2019-02-25 21:30 | 474 | 473
2019-02-25 22:00 | 462 | 462
2019-02-25 22:30 | 449 | 449
2019-02-25 23:00 | 445 | 445
2019-02-25 23:30 | 428 | 427
2019-02-26 | 407 | 406
2019-02-26 00:30 | 385 | 384
2019-02-26 01:00 | 375 | 373
2019-02-26 01:30 | 365 | 363
2019-02-26 02:00 | 356 | 354
2019-02-26 02:30 | 355 | 352
2019-02-26 03:00 | 350 | 347
2019-02-26 03:30 | 347 | 344
2019-02-26 04:00 | 333 | 329
2019-02-26 04:30 | 350 | 347
2019-02-26 05:00 | 359 | 357
2019-02-26 05:30 | 389 | 388
2019-02-26 06:00 | 419 | 418
2019-02-26 06:30 | 467 | 464
2019-02-26 07:00 | 516 | 510
2019-02-26 07:30 | 532 | 527
2019-02-26 08:00 | 524 | 515
2019-02-26 08:30 | 525 | 518
2019-02-26 09:00 | 524 | 517
2019-02-26 09:30 | 501 | 494
2019-02-26 10:00 | 518 | 513
2019-02-26 10:30 | 514 | 514
2019-02-26 11:00 | 499 | 499
2019-02-26 11:30 | 497 | 497
2019-02-26 12:00 | 506 | 506
2019-02-26 12:30 | 508 | 508
2019-02-26 13:00 | 496 | 496
2019-02-26 13:30 | 497 | 497
2019-02-26 14:00 | 485 | 485
2019-02-26 14:30 | 499 | 498
2019-02-26 15:00 | 507 | 507
2019-02-26 15:30 | 522 | 521
2019-02-26 16:00 | 544 | 543
2019-02-26 16:30 | 560 | 559
2019-02-26 17:00 | 567 | 566
2019-02-26 17:30 | 567 | 567
2019-02-26 18:00 | 551 | 549
2019-02-26 18:30 | 533 | 531
2019-02-26 19:00 | 543 | 542
2019-02-26 19:30 | 543 | 542
2019-02-26 20:00 | 538 | 537
2019-02-26 20:30 | 518 | 518
2019-02-26 21:00 | 489 | 488
2019-02-26 21:30 | 468 | 467
2019-02-26 22:00 | 447 | 447
2019-02-26 22:30 | 432 | 431
2019-02-26 23:00 | 432 | 430
2019-02-26 23:30 | 417 | 414
2019-02-27 | 398 | 393
2019-02-27 00:30 | 350 | 346
2019-02-27 01:00 | 332 | 328
2019-02-27 01:30 | 323 | 319
2019-02-27 02:00 | 316 | 312
2019-02-27 02:30 | 315 | 310
2019-02-27 03:00 | 310 | 304
2019-02-27 03:30 | 313 | 307
2019-02-27 04:00 | 318 | 312
2019-02-27 04:30 | 334 | 329
2019-02-27 05:00 | 336 | 333
2019-02-27 05:30 | 375 | 373
2019-02-27 06:00 | 404 | 402
2019-02-27 06:30 | 437 | 436
2019-02-27 07:00 | 467 | 467
2019-02-27 07:30 | 486 | 486
2019-02-27 08:00 | 495 | 495
2019-02-27 08:30 | 498 | 498
2019-02-27 09:00 | 509 | 509
2019-02-27 09:30 | 508 | 508
2019-02-27 10:00 | 515 | 514
2019-02-27 10:30 | 510 | 510
2019-02-27 11:00 | 507 | 507
2019-02-27 11:30 | 509 | 509
2019-02-27 12:00 | 513 | 513
2019-02-27 12:30 | 508 | 508
2019-02-27 13:00 | 508 | 508
2019-02-27 13:30 | 508 | 508
2019-02-27 14:00 | 520 | 520
2019-02-27 14:30 | 523 | 523
2019-02-27 15:00 | 524 | 524
2019-02-27 15:30 | 529 | 528
2019-02-27 16:00 | 543 | 543
2019-02-27 16:30 | 538 | 538
2019-02-27 17:00 | 562 | 561
2019-02-27 17:30 | 561 | 560
2019-02-27 18:00 | 556 | 555
2019-02-27 18:30 | 537 | 535
2019-02-27 19:00 | 550 | 549
2019-02-27 19:30 | 544 | 543
2019-02-27 20:00 | 526 | 525
2019-02-27 20:30 | 510 | 510
2019-02-27 21:00 | 488 | 488
2019-02-27 21:30 | 475 | 475
2019-02-27 22:00 | 462 | 462
2019-02-27 22:30 | 441 | 440
2019-02-27 23:00 | 433 | 432
2019-02-27 23:30 | 421 | 419
2019-02-28 | 396 | 394
2019-02-28 00:30 | 371 | 368
2019-02-28 01:00 | 358 | 355
2019-02-28 01:30 | 354 | 350
2019-02-28 02:00 | 355 | 350
2019-02-28 02:30 | 353 | 346
2019-02-28 03:00 | 352 | 344
2019-02-28 03:30 | 348 | 340
2019-02-28 04:00 | 345 | 336
2019-02-28 04:30 | 354 | 346
2019-02-28 05:00 | 358 | 351
2019-02-28 05:30 | 392 | 387
2019-02-28 06:00 | 416 | 412
2019-02-28 06:30 | 467 | 465
2019-02-28 07:00 | 503 | 501
2019-02-28 07:30 | 510 | 509
2019-02-28 08:00 | 521 | 520
2019-02-28 08:30 | 530 | 529
2019-02-28 09:00 | 532 | 532
2019-02-28 09:30 | 532 | 531
2019-02-28 10:00 | 545 | 540
2019-02-28 10:30 | 547 | 543
2019-02-28 11:00 | 542 | 538
2019-02-28 11:30 | 521 | 516
2019-02-28 12:00 | 518 | 513
2019-02-28 12:30 | 502 | 497
2019-02-28 13:00 | 522 | 517
2019-02-28 13:30 | 532 | 528
2019-02-28 14:00 | 534 | 530
2019-02-28 14:30 | 535 | 531
2019-02-28 15:00 | 555 | 551
2019-02-28 15:30 | 543 | 539
2019-02-28 16:00 | 541 | 537
2019-02-28 16:30 | 543 | 539
2019-02-28 17:00 | 553 | 549
2019-02-28 17:30 | 554 | 551
2019-02-28 18:00 | 542 | 541
2019-02-28 18:30 | 535 | 534
2019-02-28 19:00 | 545 | 545
2019-02-28 19:30 | 539 | 539
2019-02-28 20:00 | 532 | 531
2019-02-28 20:30 | 512 | 511
2019-02-28 21:00 | 487 | 486
2019-02-28 21:30 | 469 | 468
2019-02-28 22:00 | 452 | 450
2019-02-28 22:30 | 445 | 443
2019-02-28 23:00 | 443 | 440
2019-02-28 23:30 | 438 | 436
2019-03-01 | 421 | 417
2019-03-01 00:30 | 412 | 405
2019-03-01 01:00 | 399 | 391
2019-03-01 01:30 | 382 | 372
2019-03-01 02:00 | 374 | 363
2019-03-01 02:30 | 369 | 357
2019-03-01 03:00 | 364 | 352
2019-03-01 03:30 | 354 | 342
2019-03-01 04:00 | 354 | 340
2019-03-01 04:30 | 355 | 342
2019-03-01 05:00 | 366 | 354
2019-03-01 05:30 | 397 | 388
2019-03-01 06:00 | 435 | 427
2019-03-01 06:30 | 484 | 480
2019-03-01 07:00 | 522 | 519
2019-03-01 07:30 | 533 | 532
2019-03-01 08:00 | 538 | 536
2019-03-01 08:30 | 531 | 529
2019-03-01 09:00 | 543 | 541
2019-03-01 09:30 | 541 | 539
2019-03-01 10:00 | 544 | 543
2019-03-01 10:30 | 536 | 535
2019-03-01 11:00 | 549 | 548
2019-03-01 11:30 | 538 | 537
2019-03-01 12:00 | 542 | 540
2019-03-01 12:30 | 542 | 540
2019-03-01 13:00 | 545 | 543
2019-03-01 13:30 | 534 | 532
2019-03-01 14:00 | 543 | 541
2019-03-01 14:30 | 550 | 549
2019-03-01 15:00 | 554 | 552
2019-03-01 15:30 | 556 | 554
2019-03-01 16:00 | 557 | 555
2019-03-01 16:30 | 573 | 571
2019-03-01 17:00 | 580 | 577
2019-03-01 17:30 | 564 | 560
2019-03-01 18:00 | 554 | 549
2019-03-01 18:30 | 543 | 538
2019-03-01 19:00 | 555 | 553
2019-03-01 19:30 | 548 | 545
2019-03-01 20:00 | 537 | 533
2019-03-01 20:30 | 521 | 517
2019-03-01 21:00 | 501 | 496
2019-03-01 21:30 | 490 | 485
2019-03-01 22:00 | 473 | 469
2019-03-01 22:30 | 456 | 453
2019-03-01 23:00 | 453 | 449
2019-03-01 23:30 | 429 | 424
2019-03-02 | 406 | 400
2019-03-02 00:30 | 388 | 380
2019-03-02 01:00 | 378 | 368
2019-03-02 01:30 | 364 | 352
2019-03-02 02:00 | 352 | 338
2019-03-02 02:30 | 354 | 340
2019-03-02 03:00 | 353 | 339
2019-03-02 03:30 | 354 | 340
2019-03-02 04:00 | 349 | 334
2019-03-02 04:30 | 353 | 338
2019-03-02 05:00 | 354 | 339
2019-03-02 05:30 | 360 | 347
2019-03-02 06:00 | 371 | 358
2019-03-02 06:30 | 382 | 369
2019-03-02 07:00 | 399 | 388
2019-03-02 07:30 | 422 | 413
2019-03-02 08:00 | 445 | 438
2019-03-02 08:30 | 465 | 459
2019-03-02 09:00 | 461 | 454
2019-03-02 09:30 | 467 | 458
2019-03-02 10:00 | 473 | 464
2019-03-02 10:30 | 468 | 460
2019-03-02 11:00 | 453 | 446
2019-03-02 11:30 | 450 | 443
2019-03-02 12:00 | 446 | 439
2019-03-02 12:30 | 445 | 439
2019-03-02 13:00 | 444 | 438
2019-03-02 13:30 | 450 | 444
2019-03-02 14:00 | 463 | 458
2019-03-02 14:30 | 453 | 448
2019-03-02 15:00 | 456 | 451
2019-03-02 15:30 | 477 | 471
2019-03-02 16:00 | 465 | 460
2019-03-02 16:30 | 481 | 476
2019-03-02 17:00 | 491 | 486
2019-03-02 17:30 | 489 | 485
2019-03-02 18:00 | 465 | 460
2019-03-02 18:30 | 461 | 457
2019-03-02 19:00 | 471 | 468
2019-03-02 19:30 | 479 | 475
2019-03-02 20:00 | 463 | 459
2019-03-02 20:30 | 462 | 458
2019-03-02 21:00 | 449 | 446
2019-03-02 21:30 | 432 | 429
2019-03-02 22:00 | 433 | 429
2019-03-02 22:30 | 429 | 424
2019-03-02 23:00 | 423 | 418
2019-03-02 23:30 | 402 | 396
2019-03-03 | 384 | 377
2019-03-03 00:30 | 369 | 360
2019-03-03 01:00 | 355 | 344
2019-03-03 01:30 | 347 | 334
2019-03-03 02:00 | 338 | 324
2019-03-03 02:30 | 337 | 322
2019-03-03 03:00 | 337 | 321
2019-03-03 03:30 | 342 | 327
2019-03-03 04:00 | 340 | 324
2019-03-03 04:30 | 341 | 324
2019-03-03 05:00 | 342 | 326
2019-03-03 05:30 | 351 | 336
2019-03-03 06:00 | 363 | 347
2019-03-03 06:30 | 369 | 353
2019-03-03 07:00 | 388 | 374
2019-03-03 07:30 | 399 | 387
2019-03-03 08:00 | 404 | 393
2019-03-03 08:30 | 426 | 418
2019-03-03 09:00 | 434 | 428
2019-03-03 09:30 | 429 | 423
2019-03-03 10:00 | 437 | 432
2019-03-03 10:30 | 440 | 436
2019-03-03 11:00 | 443 | 438
2019-03-03 11:30 | 436 | 431
2019-03-03 12:00 | 419 | 414
2019-03-03 12:30 | 415 | 410
2019-03-03 13:00 | 414 | 409
2019-03-03 13:30 | 426 | 422
2019-03-03 14:00 | 428 | 423
2019-03-03 14:30 | 436 | 432
2019-03-03 15:00 | 462 | 459
2019-03-03 15:30 | 482 | 479
2019-03-03 16:00 | 503 | 500
2019-03-03 16:30 | 517 | 512
2019-03-03 17:00 | 537 | 532
2019-03-03 17:30 | 544 | 540
2019-03-03 18:00 | 522 | 518
2019-03-03 18:30 | 524 | 520
2019-03-03 19:00 | 534 | 532
2019-03-03 19:30 | 527 | 524
2019-03-03 20:00 | 516 | 512
2019-03-03 20:30 | 500 | 497
2019-03-03 21:00 | 464 | 462
2019-03-03 21:30 | 455 | 452
2019-03-03 22:00 | 448 | 444
2019-03-03 22:30 | 444 | 440
2019-03-03 23:00 | 433 | 427
2019-03-03 23:30 | 418 | 411
2019-03-04 | 399 | 390
2019-03-04 00:30 | 384 | 372
2019-03-04 01:00 | 377 | 364
2019-03-04 01:30 | 363 | 352
2019-03-04 02:00 | 359 | 348
2019-03-04 02:30 | 360 | 349
2019-03-04 03:00 | 358 | 346
2019-03-04 03:30 | 357 | 346
2019-03-04 04:00 | 353 | 342
2019-03-04 04:30 | 368 | 357
2019-03-04 05:00 | 374 | 365
2019-03-04 05:30 | 394 | 387
2019-03-04 06:00 | 426 | 420
2019-03-04 06:30 | 473 | 470
2019-03-04 07:00 | 511 | 510
2019-03-04 07:30 | 531 | 530
2019-03-04 08:00 | 533 | 533
2019-03-04 08:30 | 538 | 538
2019-03-04 09:00 | 538 | 538
2019-03-04 09:30 | 563 | 561
2019-03-04 10:00 | 563 | 561
2019-03-04 10:30 | 567 | 566
2019-03-04 11:00 | 564 | 562
2019-03-04 11:30 | 565 | 563
2019-03-04 12:00 | 568 | 567
2019-03-04 12:30 | 568 | 566
2019-03-04 13:00 | 568 | 566
2019-03-04 13:30 | 570 | 569
2019-03-04 14:00 | 570 | 569
2019-03-04 14:30 | 575 | 574
2019-03-04 15:00 | 580 | 579
2019-03-04 15:30 | 590 | 589
2019-03-04 16:00 | 611 | 610
2019-03-04 16:30 | 627 | 626
2019-03-04 17:00 | 631 | 629
2019-03-04 17:30 | 621 | 620
2019-03-04 18:00 | 607 | 606
2019-03-04 18:30 | 592 | 591
2019-03-04 19:00 | 604 | 603
2019-03-04 19:30 | 596 | 595
2019-03-04 20:00 | 590 | 589
2019-03-04 20:30 | 562 | 561
2019-03-04 21:00 | 531 | 530
2019-03-04 21:30 | 504 | 502
2019-03-04 22:00 | 482 | 481
2019-03-04 22:30 | 471 | 470
2019-03-04 23:00 | 462 | 461
2019-03-04 23:30 | 437 | 436
2019-03-05 | 414 | 413
2019-03-05 00:30 | 392 | 390
2019-03-05 01:00 | 384 | 382
2019-03-05 01:30 | 373 | 371
2019-03-05 02:00 | 367 | 364
2019-03-05 02:30 | 368 | 365
2019-03-05 03:00 | 366 | 363
2019-03-05 03:30 | 374 | 371
2019-03-05 04:00 | 365 | 362
2019-03-05 04:30 | 366 | 364
2019-03-05 05:00 | 373 | 371
2019-03-05 05:30 | 402 | 400
2019-03-05 06:00 | 447 | 445
2019-03-05 06:30 | 480 | 479
2019-03-05 07:00 | 513 | 509
2019-03-05 07:30 | 543 | 537
2019-03-05 08:00 | 566 | 560
2019-03-05 08:30 | 580 | 571
2019-03-05 09:00 | 577 | 566
2019-03-05 09:30 | 578 | 567
2019-03-05 10:00 | 568 | 557
2019-03-05 10:30 | 558 | 548
2019-03-05 11:00 | 556 | 547
2019-03-05 11:30 | 558 | 549
2019-03-05 12:00 | 566 | 557
2019-03-05 12:30 | 572 | 563
2019-03-05 13:00 | 571 | 562
2019-03-05 13:30 | 584 | 576
2019-03-05 14:00 | 588 | 580
2019-03-05 14:30 | 594 | 586
2019-03-05 15:00 | 597 | 588
2019-03-05 15:30 | 598 | 590
2019-03-05 16:00 | 614 | 606
2019-03-05 16:30 | 634 | 626
2019-03-05 17:00 | 647 | 639
2019-03-05 17:30 | 647 | 638
2019-03-05 18:00 | 637 | 626
2019-03-05 18:30 | 627 | 617
2019-03-05 19:00 | 633 | 626
2019-03-05 19:30 | 623 | 615
2019-03-05 20:00 | 614 | 610
2019-03-05 20:30 | 581 | 579
2019-03-05 21:00 | 557 | 557
2019-03-05 21:30 | 547 | 546
2019-03-05 22:00 | 524 | 523
2019-03-05 22:30 | 491 | 490
2019-03-05 23:00 | 470 | 468
2019-03-05 23:30 | 455 | 453
2019-03-06 | 436 | 434
2019-03-06 00:30 | 408 | 404
2019-03-06 01:00 | 382 | 377
2019-03-06 01:30 | 372 | 367
2019-03-06 02:00 | 367 | 361
2019-03-06 02:30 | 364 | 357
2019-03-06 03:00 | 348 | 340
2019-03-06 03:30 | 342 | 334
2019-03-06 04:00 | 343 | 335
2019-03-06 04:30 | 345 | 338
2019-03-06 05:00 | 348 | 342
2019-03-06 05:30 | 369 | 365
2019-03-06 06:00 | 408 | 405
2019-03-06 06:30 | 478 | 477
2019-03-06 07:00 | 505 | 505
2019-03-06 07:30 | 524 | 524
2019-03-06 08:00 | 534 | 534
2019-03-06 08:30 | 542 | 541
2019-03-06 09:00 | 543 | 542
2019-03-06 09:30 | 555 | 555
2019-03-06 10:00 | 557 | 557
2019-03-06 10:30 | 570 | 569
2019-03-06 11:00 | 568 | 568
2019-03-06 11:30 | 564 | 564
2019-03-06 12:00 | 578 | 578
2019-03-06 12:30 | 596 | 596
2019-03-06 13:00 | 600 | 600
2019-03-06 13:30 | 622 | 621
2019-03-06 14:00 | 630 | 628
2019-03-06 14:30 | 627 | 626
2019-03-06 15:00 | 639 | 635
2019-03-06 15:30 | 659 | 655
2019-03-06 16:00 | 664 | 661
2019-03-06 16:30 | 687 | 683
2019-03-06 17:00 | 713 | 709
2019-03-06 17:30 | 719 | 713
2019-03-06 18:00 | 722 | 714
2019-03-06 18:30 | 706 | 698
2019-03-06 19:00 | 721 | 715
2019-03-06 19:30 | 717 | 710
2019-03-06 20:00 | 704 | 696
2019-03-06 20:30 | 673 | 665
2019-03-06 21:00 | 643 | 638
2019-03-06 21:30 | 615 | 609
2019-03-06 22:00 | 586 | 582
2019-03-06 22:30 | 563 | 557
2019-03-06 23:00 | 547 | 542
2019-03-06 23:30 | 526 | 522
2019-03-07 | 495 | 492
2019-03-07 00:30 | 460 | 457
2019-03-07 01:00 | 428 | 426
2019-03-07 01:30 | 404 | 401
2019-03-07 02:00 | 394 | 392
2019-03-07 02:30 | 395 | 392
2019-03-07 03:00 | 397 | 393
2019-03-07 03:30 | 395 | 391
2019-03-07 04:00 | 395 | 391
2019-03-07 04:30 | 402 | 399
2019-03-07 05:00 | 410 | 407
2019-03-07 05:30 | 446 | 444
2019-03-07 06:00 | 476 | 475
2019-03-07 06:30 | 517 | 516
2019-03-07 07:00 | 539 | 539
2019-03-07 07:30 | 553 | 553
2019-03-07 08:00 | 567 | 566
2019-03-07 08:30 | 573 | 572
2019-03-07 09:00 | 584 | 583
2019-03-07 09:30 | 593 | 590
2019-03-07 10:00 | 615 | 611
2019-03-07 10:30 | 610 | 606
2019-03-07 11:00 | 621 | 617
2019-03-07 11:30 | 628 | 621
2019-03-07 12:00 | 624 | 617
2019-03-07 12:30 | 614 | 606
2019-03-07 13:00 | 618 | 611
2019-03-07 13:30 | 638 | 632
2019-03-07 14:00 | 645 | 640
2019-03-07 14:30 | 655 | 650
2019-03-07 15:00 | 662 | 659
2019-03-07 15:30 | 673 | 670
2019-03-07 16:00 | 684 | 680
2019-03-07 16:30 | 702 | 697
2019-03-07 17:00 | 713 | 709
2019-03-07 17:30 | 696 | 690
2019-03-07 18:00 | 683 | 675
2019-03-07 18:30 | 670 | 661
2019-03-07 19:00 | 682 | 676
2019-03-07 19:30 | 661 | 654
2019-03-07 20:00 | 643 | 639
2019-03-07 20:30 | 615 | 610
2019-03-07 21:00 | 581 | 575
2019-03-07 21:30 | 552 | 543
2019-03-07 22:00 | 518 | 510
2019-03-07 22:30 | 507 | 497
2019-03-07 23:00 | 501 | 492
2019-03-07 23:30 | 473 | 464
2019-03-08 | 439 | 434
2019-03-08 00:30 | 408 | 406
2019-03-08 01:00 | 401 | 397
2019-03-08 01:30 | 389 | 385
2019-03-08 02:00 | 383 | 379
2019-03-08 02:30 | 384 | 379
2019-03-08 03:00 | 374 | 369
2019-03-08 03:30 | 362 | 357
2019-03-08 04:00 | 370 | 365
2019-03-08 04:30 | 378 | 373
2019-03-08 05:00 | 379 | 375
2019-03-08 05:30 | 401 | 398
2019-03-08 06:00 | 441 | 438
2019-03-08 06:30 | 486 | 482
2019-03-08 07:00 | 535 | 527
2019-03-08 07:30 | 559 | 549
2019-03-08 08:00 | 566 | 558
2019-03-08 08:30 | 574 | 567
2019-03-08 09:00 | 575 | 568
2019-03-08 09:30 | 577 | 571
2019-03-08 10:00 | 576 | 570
2019-03-08 10:30 | 582 | 577
2019-03-08 11:00 | 577 | 571
2019-03-08 11:30 | 580 | 574
2019-03-08 12:00 | 587 | 582
2019-03-08 12:30 | 600 | 595
2019-03-08 13:00 | 597 | 590
2019-03-08 13:30 | 610 | 604
2019-03-08 14:00 | 621 | 615
2019-03-08 14:30 | 617 | 610
2019-03-08 15:00 | 609 | 602
2019-03-08 15:30 | 622 | 614
2019-03-08 16:00 | 638 | 631
2019-03-08 16:30 | 654 | 646
2019-03-08 17:00 | 663 | 655
2019-03-08 17:30 | 657 | 648
2019-03-08 18:00 | 630 | 616
2019-03-08 18:30 | 610 | 595
2019-03-08 19:00 | 620 | 609
2019-03-08 19:30 | 614 | 601
2019-03-08 20:00 | 602 | 590
2019-03-08 20:30 | 591 | 578
2019-03-08 21:00 | 560 | 552
2019-03-08 21:30 | 539 | 530
2019-03-08 22:00 | 514 | 506
2019-03-08 22:30 | 502 | 498
2019-03-08 23:00 | 490 | 485
2019-03-08 23:30 | 468 | 461
2019-03-09 | 434 | 427
2019-03-09 00:30 | 420 | 412
2019-03-09 01:00 | 416 | 407
2019-03-09 01:30 | 402 | 393
2019-03-09 02:00 | 396 | 386
2019-03-09 02:30 | 398 | 387
2019-03-09 03:00 | 395 | 384
2019-03-09 03:30 | 391 | 380
2019-03-09 04:00 | 388 | 377
2019-03-09 04:30 | 385 | 374
2019-03-09 05:00 | 386 | 375
2019-03-09 05:30 | 398 | 388
2019-03-09 06:00 | 409 | 399
2019-03-09 06:30 | 427 | 418
2019-03-09 07:00 | 439 | 430
2019-03-09 07:30 | 456 | 450
2019-03-09 08:00 | 469 | 465
2019-03-09 08:30 | 476 | 473
2019-03-09 09:00 | 479 | 474
2019-03-09 09:30 | 493 | 490
2019-03-09 10:00 | 503 | 500
2019-03-09 10:30 | 503 | 500
2019-03-09 11:00 | 501 | 498
2019-03-09 11:30 | 494 | 491
2019-03-09 12:00 | 500 | 497
2019-03-09 12:30 | 506 | 504
2019-03-09 13:00 | 509 | 507
2019-03-09 13:30 | 509 | 508
2019-03-09 14:00 | 524 | 523
2019-03-09 14:30 | 537 | 534
2019-03-09 15:00 | 552 | 550
2019-03-09 15:30 | 562 | 561
2019-03-09 16:00 | 579 | 576
2019-03-09 16:30 | 592 | 585
2019-03-09 17:00 | 610 | 604
2019-03-09 17:30 | 610 | 603
2019-03-09 18:00 | 597 | 588
2019-03-09 18:30 | 594 | 585
2019-03-09 19:00 | 607 | 599
2019-03-09 19:30 | 590 | 580
2019-03-09 20:00 | 579 | 567
2019-03-09 20:30 | 548 | 542
2019-03-09 21:00 | 518 | 513
2019-03-09 21:30 | 506 | 502
2019-03-09 22:00 | 498 | 496
2019-03-09 22:30 | 481 | 478
2019-03-09 23:00 | 475 | 471
2019-03-09 23:30 | 458 | 454
2019-03-10 | 435 | 431
2019-03-10 00:30 | 413 | 407
2019-03-10 01:00 | 403 | 395
2019-03-10 01:30 | 391 | 382
2019-03-10 02:00 | 382 | 373
2019-03-10 02:30 | 377 | 367
2019-03-10 03:00 | 374 | 363
2019-03-10 03:30 | 372 | 361
2019-03-10 04:00 | 369 | 357
2019-03-10 04:30 | 365 | 353
2019-03-10 05:00 | 355 | 342
2019-03-10 05:30 | 355 | 343
2019-03-10 06:00 | 360 | 347
2019-03-10 06:30 | 371 | 358
2019-03-10 07:00 | 381 | 369
2019-03-10 07:30 | 404 | 394
2019-03-10 08:00 | 417 | 408
2019-03-10 08:30 | 429 | 423
2019-03-10 09:00 | 437 | 432
2019-03-10 09:30 | 444 | 440
2019-03-10 10:00 | 452 | 449
2019-03-10 10:30 | 464 | 459
2019-03-10 11:00 | 470 | 464
2019-03-10 11:30 | 460 | 455
2019-03-10 12:00 | 470 | 466
2019-03-10 12:30 | 488 | 485
2019-03-10 13:00 | 500 | 499
2019-03-10 13:30 | 525 | 521
2019-03-10 14:00 | 545 | 534
2019-03-10 14:30 | 555 | 541
2019-03-10 15:00 | 566 | 554
2019-03-10 15:30 | 592 | 582
2019-03-10 16:00 | 605 | 597
2019-03-10 16:30 | 618 | 612
2019-03-10 17:00 | 640 | 634
2019-03-10 17:30 | 657 | 651
2019-03-10 18:00 | 643 | 636
2019-03-10 18:30 | 633 | 626
2019-03-10 19:00 | 646 | 640
2019-03-10 19:30 | 626 | 620
2019-03-10 20:00 | 609 | 603
2019-03-10 20:30 | 601 | 594
2019-03-10 21:00 | 571 | 564
2019-03-10 21:30 | 561 | 553
2019-03-10 22:00 | 537 | 530
2019-03-10 22:30 | 515 | 511
2019-03-10 23:00 | 497 | 493
2019-03-10 23:30 | 474 | 470
2019-03-11 | 449 | 444
2019-03-11 00:30 | 416 | 411
2019-03-11 01:00 | 401 | 395
2019-03-11 01:30 | 388 | 381
2019-03-11 02:00 | 379 | 372
2019-03-11 02:30 | 378 | 371
2019-03-11 03:00 | 380 | 372
2019-03-11 03:30 | 385 | 376
2019-03-11 04:00 | 388 | 380
2019-03-11 04:30 | 396 | 388
2019-03-11 05:00 | 402 | 395
2019-03-11 05:30 | 429 | 424
2019-03-11 06:00 | 464 | 462
2019-03-11 06:30 | 513 | 511
2019-03-11 07:00 | 561 | 557
2019-03-11 07:30 | 603 | 594
2019-03-11 08:00 | 616 | 607
2019-03-11 08:30 | 626 | 620
2019-03-11 09:00 | 639 | 632
2019-03-11 09:30 | 644 | 639
2019-03-11 10:00 | 658 | 652
2019-03-11 10:30 | 673 | 667
2019-03-11 11:00 | 688 | 685
2019-03-11 11:30 | 700 | 697
2019-03-11 12:00 | 718 | 715
2019-03-11 12:30 | 728 | 724
2019-03-11 13:00 | 738 | 734
2019-03-11 13:30 | 761 | 758
2019-03-11 14:00 | 814 | 809
2019-03-11 14:30 | 823 | 815
2019-03-11 15:00 | 821 | 808
2019-03-11 15:30 | 817 | 801
2019-03-11 16:00 | 804 | 788
2019-03-11 16:30 | 809 | 793
2019-03-11 17:00 | 818 | 802
2019-03-11 17:30 | 803 | 789
2019-03-11 18:00 | 775 | 766
2019-03-11 18:30 | 755 | 744
2019-03-11 19:00 | 750 | 740
2019-03-11 19:30 | 733 | 723
2019-03-11 20:00 | 713 | 706
2019-03-11 20:30 | 686 | 682
2019-03-11 21:00 | 658 | 652
2019-03-11 21:30 | 619 | 617
2019-03-11 22:00 | 584 | 583
2019-03-11 22:30 | 561 | 561
2019-03-11 23:00 | 542 | 540
2019-03-11 23:30 | 513 | 511
2019-03-12 | 489 | 487
2019-03-12 00:30 | 451 | 448
2019-03-12 01:00 | 423 | 420
2019-03-12 01:30 | 407 | 403
2019-03-12 02:00 | 392 | 387
2019-03-12 02:30 | 380 | 375
2019-03-12 03:00 | 368 | 362
2019-03-12 03:30 | 366 | 359
2019-03-12 04:00 | 379 | 372
2019-03-12 04:30 | 390 | 384
2019-03-12 05:00 | 395 | 391
2019-03-12 05:30 | 431 | 428
2019-03-12 06:00 | 464 | 461
2019-03-12 06:30 | 523 | 521
2019-03-12 07:00 | 575 | 572
2019-03-12 07:30 | 602 | 599
2019-03-12 08:00 | 614 | 607
2019-03-12 08:30 | 599 | 593
2019-03-12 09:00 | 597 | 593
2019-03-12 09:30 | 586 | 583
2019-03-12 10:00 | 587 | 584
2019-03-12 10:30 | 596 | 594
2019-03-12 11:00 | 604 | 602
2019-03-12 11:30 | 627 | 619
2019-03-12 12:00 | 647 | 641
2019-03-12 12:30 | 697 | 691
2019-03-12 13:00 | 739 | 732
2019-03-12 13:30 | 768 | 757
2019-03-12 14:00 | 784 | 769
2019-03-12 14:30 | 790 | 776
2019-03-12 15:00 | 797 | 783
2019-03-12 15:30 | 808 | 796
2019-03-12 16:00 | 825 | 812
2019-03-12 16:30 | 843 | 830
2019-03-12 17:00 | 853 | 841
2019-03-12 17:30 | 854 | 841
2019-03-12 18:00 | 839 | 824
2019-03-12 18:30 | 822 | 807
2019-03-12 19:00 | 829 | 815
2019-03-12 19:30 | 819 | 801
2019-03-12 20:00 | 799 | 783
2019-03-12 20:30 | 772 | 761
2019-03-12 21:00 | 741 | 737
2019-03-12 21:30 | 693 | 689
2019-03-12 22:00 | 660 | 658
2019-03-12 22:30 | 585 | 584
2019-03-12 23:00 | 550 | 550
2019-03-12 23:30 | 523 | 523
2019-03-13 | 502 | 502
2019-03-13 00:30 | 479 | 479
2019-03-13 01:00 | 472 | 471
2019-03-13 01:30 | 456 | 454
2019-03-13 02:00 | 437 | 434
2019-03-13 02:30 | 438 | 435
2019-03-13 03:00 | 433 | 430
2019-03-13 03:30 | 433 | 430
2019-03-13 04:00 | 433 | 429
2019-03-13 04:30 | 434 | 431
2019-03-13 05:00 | 433 | 430
2019-03-13 05:30 | 462 | 459
2019-03-13 06:00 | 492 | 486
2019-03-13 06:30 | 528 | 525
2019-03-13 07:00 | 577 | 573
2019-03-13 07:30 | 598 | 591
2019-03-13 08:00 | 602 | 594
2019-03-13 08:30 | 614 | 604
2019-03-13 09:00 | 613 | 604
2019-03-13 09:30 | 617 | 609
2019-03-13 10:00 | 623 | 616
2019-03-13 10:30 | 638 | 631
2019-03-13 11:00 | 656 | 650
2019-03-13 11:30 | 673 | 668
2019-03-13 12:00 | 690 | 684
2019-03-13 12:30 | 694 | 690
2019-03-13 13:00 | 703 | 700
2019-03-13 13:30 | 716 | 712
2019-03-13 14:00 | 724 | 720
2019-03-13 14:30 | 726 | 721
2019-03-13 15:00 | 731 | 727
2019-03-13 15:30 | 741 | 737
2019-03-13 16:00 | 756 | 751
2019-03-13 16:30 | 774 | 769
2019-03-13 17:00 | 786 | 781
2019-03-13 17:30 | 783 | 776
2019-03-13 18:00 | 760 | 751
2019-03-13 18:30 | 729 | 720
2019-03-13 19:00 | 731 | 722
2019-03-13 19:30 | 701 | 693
2019-03-13 20:00 | 678 | 671
2019-03-13 20:30 | 655 | 646
2019-03-13 21:00 | 612 | 606
2019-03-13 21:30 | 587 | 577
2019-03-13 22:00 | 562 | 555
2019-03-13 22:30 | 534 | 529
2019-03-13 23:00 | 523 | 517
2019-03-13 23:30 | 490 | 484
2019-03-14 | 446 | 439
2019-03-14 00:30 | 418 | 412
2019-03-14 01:00 | 404 | 397
2019-03-14 01:30 | 393 | 384
2019-03-14 02:00 | 397 | 388
2019-03-14 02:30 | 395 | 385
2019-03-14 03:00 | 385 | 374
2019-03-14 03:30 | 393 | 381
2019-03-14 04:00 | 401 | 389
2019-03-14 04:30 | 400 | 389
2019-03-14 05:00 | 402 | 392
2019-03-14 05:30 | 423 | 415
2019-03-14 06:00 | 464 | 458
2019-03-14 06:30 | 502 | 499
2019-03-14 07:00 | 551 | 548
2019-03-14 07:30 | 582 | 577
2019-03-14 08:00 | 596 | 590
2019-03-14 08:30 | 620 | 612
2019-03-14 09:00 | 625 | 619
2019-03-14 09:30 | 636 | 631
2019-03-14 10:00 | 641 | 637
2019-03-14 10:30 | 646 | 642
2019-03-14 11:00 | 640 | 637
2019-03-14 11:30 | 655 | 652
2019-03-14 12:00 | 672 | 669
2019-03-14 12:30 | 662 | 658
2019-03-14 13:00 | 677 | 673
2019-03-14 13:30 | 695 | 691
2019-03-14 14:00 | 708 | 704
2019-03-14 14:30 | 710 | 706
2019-03-14 15:00 | 699 | 694
2019-03-14 15:30 | 702 | 697
2019-03-14 16:00 | 704 | 699
2019-03-14 16:30 | 730 | 725
2019-03-14 17:00 | 730 | 725
2019-03-14 17:30 | 723 | 716
2019-03-14 18:00 | 714 | 708
2019-03-14 18:30 | 704 | 698
2019-03-14 19:00 | 718 | 713
2019-03-14 19:30 | 705 | 700
2019-03-14 20:00 | 690 | 684
2019-03-14 20:30 | 674 | 667
2019-03-14 21:00 | 626 | 620
2019-03-14 21:30 | 592 | 588
2019-03-14 22:00 | 556 | 554
2019-03-14 22:30 | 532 | 530
2019-03-14 23:00 | 515 | 514
2019-03-14 23:30 | 493 | 491
2019-03-15 | 469 | 466
2019-03-15 00:30 | 437 | 434
2019-03-15 01:00 | 421 | 417
2019-03-15 01:30 | 416 | 411
2019-03-15 02:00 | 404 | 397
2019-03-15 02:30 | 396 | 387
2019-03-15 03:00 | 386 | 376
2019-03-15 03:30 | 381 | 371
2019-03-15 04:00 | 383 | 372
2019-03-15 04:30 | 384 | 374
2019-03-15 05:00 | 381 | 373
2019-03-15 05:30 | 422 | 416
2019-03-15 06:00 | 458 | 452
2019-03-15 06:30 | 504 | 499
2019-03-15 07:00 | 541 | 538
2019-03-15 07:30 | 563 | 561
2019-03-15 08:00 | 568 | 566
2019-03-15 08:30 | 574 | 573
2019-03-15 09:00 | 582 | 581
2019-03-15 09:30 | 586 | 586
2019-03-15 10:00 | 594 | 593
2019-03-15 10:30 | 605 | 604
2019-03-15 11:00 | 611 | 610
2019-03-15 11:30 | 629 | 628
2019-03-15 12:00 | 646 | 645
2019-03-15 12:30 | 669 | 667
2019-03-15 13:00 | 680 | 678
2019-03-15 13:30 | 689 | 687
2019-03-15 14:00 | 736 | 734
2019-03-15 14:30 | 747 | 744
2019-03-15 15:00 | 746 | 741
2019-03-15 15:30 | 744 | 737
2019-03-15 16:00 | 744 | 737
2019-03-15 16:30 | 733 | 726
2019-03-15 17:00 | 704 | 693
2019-03-15 17:30 | 657 | 644
2019-03-15 18:00 | 620 | 608
2019-03-15 18:30 | 594 | 583
2019-03-15 19:00 | 571 | 565
2019-03-15 19:30 | 552 | 549
2019-03-15 20:00 | 537 | 534
2019-03-15 20:30 | 514 | 513
2019-03-15 21:00 | 490 | 488
2019-03-15 21:30 | 472 | 470
2019-03-15 22:00 | 447 | 444
2019-03-15 22:30 | 412 | 409
2019-03-15 23:00 | 403 | 399
2019-03-15 23:30 | 415 | 409
2019-03-16 | 410 | 402
2019-03-16 00:30 | 373 | 363
2019-03-16 01:00 | 359 | 346
2019-03-16 01:30 | 337 | 325
2019-03-16 02:00 | 329 | 316
2019-03-16 02:30 | 331 | 318
2019-03-16 03:00 | 325 | 311
2019-03-16 03:30 | 328 | 315
2019-03-16 04:00 | 333 | 319
2019-03-16 04:30 | 336 | 322
2019-03-16 05:00 | 327 | 314
2019-03-16 05:30 | 340 | 329
2019-03-16 06:00 | 365 | 354
2019-03-16 06:30 | 395 | 384
2019-03-16 07:00 | 422 | 412
2019-03-16 07:30 | 447 | 439
2019-03-16 08:00 | 470 | 465
2019-03-16 08:30 | 501 | 498
2019-03-16 09:00 | 509 | 506
2019-03-16 09:30 | 489 | 486
2019-03-16 10:00 | 502 | 499
2019-03-16 10:30 | 516 | 514
2019-03-16 11:00 | 511 | 508
2019-03-16 11:30 | 516 | 512
2019-03-16 12:00 | 514 | 509
2019-03-16 12:30 | 510 | 505
2019-03-16 13:00 | 514 | 509
2019-03-16 13:30 | 515 | 510
2019-03-16 14:00 | 501 | 495
2019-03-16 14:30 | 491 | 485
2019-03-16 15:00 | 493 | 487
2019-03-16 15:30 | 482 | 476
2019-03-16 16:00 | 506 | 501
2019-03-16 16:30 | 513 | 509
2019-03-16 17:00 | 525 | 521
2019-03-16 17:30 | 536 | 531
2019-03-16 18:00 | 529 | 524
2019-03-16 18:30 | 539 | 535
2019-03-16 19:00 | 544 | 541
2019-03-16 19:30 | 519 | 517
2019-03-16 20:00 | 506 | 504
2019-03-16 20:30 | 495 | 493
2019-03-16 21:00 | 489 | 488
2019-03-16 21:30 | 477 | 475
2019-03-16 22:00 | 463 | 460
2019-03-16 22:30 | 450 | 446
2019-03-16 23:00 | 437 | 433
2019-03-16 23:30 | 418 | 411
2019-03-17 | 400 | 391
2019-03-17 00:30 | 392 | 381
2019-03-17 01:00 | 387 | 375
2019-03-17 01:30 | 369 | 354
2019-03-17 02:00 | 363 | 345
2019-03-17 02:30 | 373 | 355
2019-03-17 03:00 | 374 | 354
2019-03-17 03:30 | 374 | 354
2019-03-17 04:00 | 367 | 346
2019-03-17 04:30 | 359 | 338
2019-03-17 05:00 | 354 | 334
2019-03-17 05:30 | 342 | 321
2019-03-17 06:00 | 353 | 332
2019-03-17 06:30 | 381 | 361
2019-03-17 07:00 | 389 | 371
2019-03-17 07:30 | 415 | 402
2019-03-17 08:00 | 435 | 425
2019-03-17 08:30 | 453 | 445
2019-03-17 09:00 | 460 | 453
2019-03-17 09:30 | 474 | 471
2019-03-17 10:00 | 473 | 470
2019-03-17 10:30 | 471 | 468
2019-03-17 11:00 | 470 | 468
2019-03-17 11:30 | 463 | 462
2019-03-17 12:00 | 469 | 469
2019-03-17 12:30 | 488 | 484
2019-03-17 13:00 | 482 | 478
2019-03-17 13:30 | 482 | 478
2019-03-17 14:00 | 476 | 472
2019-03-17 14:30 | 474 | 470
2019-03-17 15:00 | 488 | 485
2019-03-17 15:30 | 522 | 521
2019-03-17 16:00 | 541 | 540
2019-03-17 16:30 | 566 | 564
2019-03-17 17:00 | 576 | 574
2019-03-17 17:30 | 589 | 587
2019-03-17 18:00 | 588 | 586
2019-03-17 18:30 | 574 | 570
2019-03-17 19:00 | 571 | 567
2019-03-17 19:30 | 554 | 550
2019-03-17 20:00 | 543 | 540
2019-03-17 20:30 | 526 | 524
2019-03-17 21:00 | 489 | 485
2019-03-17 21:30 | 471 | 466
2019-03-17 22:00 | 451 | 446
2019-03-17 22:30 | 437 | 431
2019-03-17 23:00 | 414 | 409
2019-03-17 23:30 | 389 | 383
2019-03-18 | 373 | 365
2019-03-18 00:30 | 350 | 339
2019-03-18 01:00 | 341 | 328
2019-03-18 01:30 | 334 | 320
2019-03-18 02:00 | 329 | 315
2019-03-18 02:30 | 321 | 306
2019-03-18 03:00 | 311 | 296
2019-03-18 03:30 | 305 | 290
2019-03-18 04:00 | 316 | 301
2019-03-18 04:30 | 321 | 307
2019-03-18 05:00 | 329 | 317
2019-03-18 05:30 | 370 | 361
2019-03-18 06:00 | 403 | 395
2019-03-18 06:30 | 442 | 439
2019-03-18 07:00 | 481 | 479
2019-03-18 07:30 | 506 | 502
2019-03-18 08:00 | 503 | 499
2019-03-18 08:30 | 511 | 507
2019-03-18 09:00 | 508 | 504
2019-03-18 09:30 | 514 | 511
2019-03-18 10:00 | 519 | 516
2019-03-18 10:30 | 531 | 528
2019-03-18 11:00 | 530 | 527
2019-03-18 11:30 | 529 | 527
2019-03-18 12:00 | 535 | 533
2019-03-18 12:30 | 541 | 539
2019-03-18 13:00 | 561 | 560
2019-03-18 13:30 | 623 | 621
2019-03-18 14:00 | 658 | 649
2019-03-18 14:30 | 616 | 603
2019-03-18 15:00 | 567 | 555
2019-03-18 15:30 | 552 | 540
2019-03-18 16:00 | 570 | 559
2019-03-18 16:30 | 597 | 587
2019-03-18 17:00 | 608 | 597
2019-03-18 17:30 | 617 | 607
2019-03-18 18:00 | 614 | 604
2019-03-18 18:30 | 609 | 599
2019-03-18 19:00 | 616 | 607
2019-03-18 19:30 | 589 | 582
2019-03-18 20:00 | 561 | 553
2019-03-18 20:30 | 540 | 533
2019-03-18 21:00 | 512 | 504
2019-03-18 21:30 | 480 | 477
2019-03-18 22:00 | 461 | 459
2019-03-18 22:30 | 451 | 449
2019-03-18 23:00 | 436 | 435
2019-03-18 23:30 | 419 | 417
2019-03-19 | 394 | 390
2019-03-19 00:30 | 370 | 363
2019-03-19 01:00 | 347 | 340
2019-03-19 01:30 | 335 | 327
2019-03-19 02:00 | 347 | 339
2019-03-19 02:30 | 347 | 339
2019-03-19 03:00 | 346 | 338
2019-03-19 03:30 | 351 | 342
2019-03-19 04:00 | 353 | 344
2019-03-19 04:30 | 357 | 348
2019-03-19 05:00 | 362 | 355
2019-03-19 05:30 | 382 | 377
2019-03-19 06:00 | 409 | 404
2019-03-19 06:30 | 458 | 454
2019-03-19 07:00 | 501 | 497
2019-03-19 07:30 | 501 | 498
2019-03-19 08:00 | 498 | 496
2019-03-19 08:30 | 504 | 500
2019-03-19 09:00 | 498 | 494
2019-03-19 09:30 | 498 | 496
2019-03-19 10:00 | 499 | 497
2019-03-19 10:30 | 503 | 501
2019-03-19 11:00 | 506 | 503
2019-03-19 11:30 | 513 | 511
2019-03-19 12:00 | 518 | 516
2019-03-19 12:30 | 532 | 529
2019-03-19 13:00 | 550 | 542
2019-03-19 13:30 | 561 | 553
2019-03-19 14:00 | 579 | 573
2019-03-19 14:30 | 591 | 586
2019-03-19 15:00 | 610 | 603
2019-03-19 15:30 | 631 | 625
2019-03-19 16:00 | 662 | 657
2019-03-19 16:30 | 679 | 673
2019-03-19 17:00 | 688 | 683
2019-03-19 17:30 | 686 | 679
2019-03-19 18:00 | 681 | 673
2019-03-19 18:30 | 681 | 673
2019-03-19 19:00 | 687 | 680
2019-03-19 19:30 | 670 | 663
2019-03-19 20:00 | 633 | 630
2019-03-19 20:30 | 606 | 601
2019-03-19 21:00 | 573 | 569
2019-03-19 21:30 | 544 | 541
2019-03-19 22:00 | 521 | 518
2019-03-19 22:30 | 499 | 495
2019-03-19 23:00 | 479 | 478
2019-03-19 23:30 | 452 | 450
2019-03-20 | 423 | 420
2019-03-20 00:30 | 392 | 386
2019-03-20 01:00 | 375 | 369
2019-03-20 01:30 | 365 | 358
2019-03-20 02:00 | 357 | 348
2019-03-20 02:30 | 358 | 349
2019-03-20 03:00 | 360 | 350
2019-03-20 03:30 | 366 | 356
2019-03-20 04:00 | 367 | 357
2019-03-20 04:30 | 374 | 365
2019-03-20 05:00 | 375 | 367
2019-03-20 05:30 | 393 | 387
2019-03-20 06:00 | 431 | 427
2019-03-20 06:30 | 479 | 477
2019-03-20 07:00 | 519 | 515
2019-03-20 07:30 | 535 | 532
2019-03-20 08:00 | 540 | 538
2019-03-20 08:30 | 536 | 533
2019-03-20 09:00 | 532 | 530
2019-03-20 09:30 | 539 | 537
2019-03-20 10:00 | 551 | 550
2019-03-20 10:30 | 564 | 558
2019-03-20 11:00 | 558 | 550
2019-03-20 11:30 | 571 | 561
2019-03-20 12:00 | 585 | 577
2019-03-20 12:30 | 621 | 615
2019-03-20 13:00 | 654 | 640
2019-03-20 13:30 | 657 | 640
2019-03-20 14:00 | 661 | 645
2019-03-20 14:30 | 665 | 652
2019-03-20 15:00 | 688 | 676
2019-03-20 15:30 | 696 | 685
2019-03-20 16:00 | 707 | 694
2019-03-20 16:30 | 705 | 688
2019-03-20 17:00 | 712 | 694
2019-03-20 17:30 | 708 | 692
2019-03-20 18:00 | 700 | 684
2019-03-20 18:30 | 677 | 662
2019-03-20 19:00 | 684 | 670
2019-03-20 19:30 | 682 | 666
2019-03-20 20:00 | 657 | 644
2019-03-20 20:30 | 649 | 634
2019-03-20 21:00 | 618 | 600
2019-03-20 21:30 | 584 | 573
2019-03-20 22:00 | 554 | 547
2019-03-20 22:30 | 531 | 527
2019-03-20 23:00 | 500 | 497
2019-03-20 23:30 | 462 | 459
2019-03-21 | 434 | 430
2019-03-21 00:30 | 409 | 405
2019-03-21 01:00 | 386 | 381
2019-03-21 01:30 | 366 | 361
2019-03-21 02:00 | 361 | 355
2019-03-21 02:30 | 364 | 357
2019-03-21 03:00 | 362 | 355
2019-03-21 03:30 | 358 | 351
2019-03-21 04:00 | 345 | 337
2019-03-21 04:30 | 356 | 350
2019-03-21 05:00 | 361 | 356
2019-03-21 05:30 | 385 | 382
2019-03-21 06:00 | 427 | 425
2019-03-21 06:30 | 486 | 483
2019-03-21 07:00 | 531 | 530
2019-03-21 07:30 | 538 | 537
2019-03-21 08:00 | 547 | 545
2019-03-21 08:30 | 551 | 548
2019-03-21 09:00 | 558 | 554
2019-03-21 09:30 | 559 | 556
2019-03-21 10:00 | 565 | 561
2019-03-21 10:30 | 568 | 563
2019-03-21 11:00 | 583 | 579
2019-03-21 11:30 | 591 | 587
2019-03-21 12:00 | 588 | 585
2019-03-21 12:30 | 595 | 592
2019-03-21 13:00 | 615 | 613
2019-03-21 13:30 | 640 | 638
2019-03-21 14:00 | 655 | 649
2019-03-21 14:30 | 662 | 658
2019-03-21 15:00 | 660 | 655
2019-03-21 15:30 | 676 | 666
2019-03-21 16:00 | 696 | 688
2019-03-21 16:30 | 700 | 690
2019-03-21 17:00 | 704 | 694
2019-03-21 17:30 | 694 | 683
2019-03-21 18:00 | 688 | 675
2019-03-21 18:30 | 678 | 664
2019-03-21 19:00 | 676 | 661
2019-03-21 19:30 | 671 | 654
2019-03-21 20:00 | 670 | 649
2019-03-21 20:30 | 645 | 630
2019-03-21 21:00 | 599 | 587
2019-03-21 21:30 | 572 | 565
2019-03-21 22:00 | 546 | 542
2019-03-21 22:30 | 526 | 521
2019-03-21 23:00 | 505 | 499
2019-03-21 23:30 | 485 | 476
2019-03-22 | 450 | 442
2019-03-22 00:30 | 416 | 408
2019-03-22 01:00 | 395 | 389
2019-03-22 01:30 | 374 | 368
2019-03-22 02:00 | 371 | 363
2019-03-22 02:30 | 367 | 359
2019-03-22 03:00 | 364 | 355
2019-03-22 03:30 | 359 | 350
2019-03-22 04:00 | 365 | 356
2019-03-22 04:30 | 374 | 366
2019-03-22 05:00 | 380 | 373
2019-03-22 05:30 | 405 | 400
2019-03-22 06:00 | 443 | 440
2019-03-22 06:30 | 492 | 488
2019-03-22 07:00 | 536 | 534
2019-03-22 07:30 | 553 | 551
2019-03-22 08:00 | 552 | 551
2019-03-22 08:30 | 563 | 562
2019-03-22 09:00 | 570 | 570
2019-03-22 09:30 | 578 | 576
2019-03-22 10:00 | 579 | 576
2019-03-22 10:30 | 578 | 575
2019-03-22 11:00 | 581 | 579
2019-03-22 11:30 | 599 | 597
2019-03-22 12:00 | 622 | 621
2019-03-22 12:30 | 622 | 620
2019-03-22 13:00 | 620 | 617
2019-03-22 13:30 | 618 | 615
2019-03-22 14:00 | 621 | 617
2019-03-22 14:30 | 633 | 631
2019-03-22 15:00 | 640 | 638
2019-03-22 15:30 | 659 | 657
2019-03-22 16:00 | 667 | 666
2019-03-22 16:30 | 677 | 674
2019-03-22 17:00 | 670 | 666
2019-03-22 17:30 | 655 | 650
2019-03-22 18:00 | 641 | 634
2019-03-22 18:30 | 631 | 626
2019-03-22 19:00 | 625 | 620
2019-03-22 19:30 | 616 | 609
2019-03-22 20:00 | 600 | 595
2019-03-22 20:30 | 585 | 582
2019-03-22 21:00 | 570 | 567
2019-03-22 21:30 | 553 | 548
2019-03-22 22:00 | 540 | 533
2019-03-22 22:30 | 512 | 509
2019-03-22 23:00 | 498 | 494
2019-03-22 23:30 | 480 | 475
2019-03-23 | 452 | 446
2019-03-23 00:30 | 418 | 414
2019-03-23 01:00 | 407 | 402
2019-03-23 01:30 | 394 | 389
2019-03-23 02:00 | 381 | 375
2019-03-23 02:30 | 373 | 366
2019-03-23 03:00 | 365 | 356
2019-03-23 03:30 | 366 | 358
2019-03-23 04:00 | 373 | 364
2019-03-23 04:30 | 377 | 368
2019-03-23 05:00 | 374 | 365
2019-03-23 05:30 | 380 | 373
2019-03-23 06:00 | 392 | 384
2019-03-23 06:30 | 409 | 402
2019-03-23 07:00 | 428 | 421
2019-03-23 07:30 | 448 | 443
2019-03-23 08:00 | 463 | 460
2019-03-23 08:30 | 478 | 476
2019-03-23 09:00 | 493 | 491
2019-03-23 09:30 | 500 | 498
2019-03-23 10:00 | 518 | 514
2019-03-23 10:30 | 519 | 515
2019-03-23 11:00 | 505 | 503
2019-03-23 11:30 | 492 | 489
2019-03-23 12:00 | 497 | 495
2019-03-23 12:30 | 515 | 513
2019-03-23 13:00 | 543 | 541
2019-03-23 13:30 | 568 | 566
2019-03-23 14:00 | 598 | 595
2019-03-23 14:30 | 625 | 620
2019-03-23 15:00 | 648 | 643
2019-03-23 15:30 | 670 | 665
2019-03-23 16:00 | 688 | 683
2019-03-23 16:30 | 712 | 704
2019-03-23 17:00 | 728 | 715
2019-03-23 17:30 | 712 | 700
2019-03-23 18:00 | 681 | 671
2019-03-23 18:30 | 680 | 670
2019-03-23 19:00 | 680 | 671
2019-03-23 19:30 | 667 | 655
2019-03-23 20:00 | 661 | 650
2019-03-23 20:30 | 647 | 638
2019-03-23 21:00 | 614 | 610
2019-03-23 21:30 | 590 | 586
2019-03-23 22:00 | 572 | 565
2019-03-23 22:30 | 558 | 551
2019-03-23 23:00 | 538 | 533
2019-03-23 23:30 | 508 | 503
2019-03-24 | 486 | 479
2019-03-24 00:30 | 467 | 458
2019-03-24 01:00 | 456 | 446
2019-03-24 01:30 | 424 | 418
2019-03-24 02:00 | 408 | 401
2019-03-24 02:30 | 410 | 402
2019-03-24 03:00 | 414 | 405
2019-03-24 03:30 | 427 | 417
2019-03-24 04:00 | 426 | 416
2019-03-24 04:30 | 419 | 409
2019-03-24 05:00 | 395 | 384
2019-03-24 05:30 | 391 | 382
2019-03-24 06:00 | 402 | 392
2019-03-24 06:30 | 413 | 403
2019-03-24 07:00 | 424 | 415
2019-03-24 07:30 | 436 | 429
2019-03-24 08:00 | 445 | 439
2019-03-24 08:30 | 458 | 454
2019-03-24 09:00 | 472 | 469
2019-03-24 09:30 | 493 | 491
2019-03-24 10:00 | 507 | 504
2019-03-24 10:30 | 519 | 516
2019-03-24 11:00 | 534 | 530
2019-03-24 11:30 | 550 | 541
2019-03-24 12:00 | 562 | 555
2019-03-24 12:30 | 579 | 574
2019-03-24 13:00 | 615 | 609
2019-03-24 13:30 | 638 | 633
2019-03-24 14:00 | 663 | 657
2019-03-24 14:30 | 693 | 682
2019-03-24 15:00 | 707 | 698
2019-03-24 15:30 | 718 | 711
2019-03-24 16:00 | 732 | 725
2019-03-24 16:30 | 750 | 743
2019-03-24 17:00 | 768 | 753
2019-03-24 17:30 | 767 | 751
2019-03-24 18:00 | 754 | 738
2019-03-24 18:30 | 753 | 739
2019-03-24 19:00 | 756 | 742
2019-03-24 19:30 | 728 | 718
2019-03-24 20:00 | 701 | 691
2019-03-24 20:30 | 663 | 657
2019-03-24 21:00 | 617 | 613
2019-03-24 21:30 | 578 | 573
2019-03-24 22:00 | 547 | 541
2019-03-24 22:30 | 514 | 509
2019-03-24 23:00 | 490 | 485
2019-03-24 23:30 | 457 | 451
2019-03-25 | 433 | 425
2019-03-25 00:30 | 397 | 390
2019-03-25 01:00 | 372 | 364
2019-03-25 01:30 | 362 | 353
2019-03-25 02:00 | 352 | 345
2019-03-25 02:30 | 351 | 344
2019-03-25 03:00 | 349 | 341
2019-03-25 03:30 | 351 | 342
2019-03-25 04:00 | 346 | 337
2019-03-25 04:30 | 356 | 348
2019-03-25 05:00 | 365 | 358
2019-03-25 05:30 | 383 | 379
2019-03-25 06:00 | 415 | 411
2019-03-25 06:30 | 493 | 488
2019-03-25 07:00 | 530 | 526
2019-03-25 07:30 | 565 | 563
2019-03-25 08:00 | 584 | 580
2019-03-25 08:30 | 608 | 600
2019-03-25 09:00 | 601 | 592
2019-03-25 09:30 | 604 | 596
2019-03-25 10:00 | 616 | 609
2019-03-25 10:30 | 624 | 619
2019-03-25 11:00 | 632 | 628
2019-03-25 11:30 | 638 | 632
2019-03-25 12:00 | 635 | 630
2019-03-25 12:30 | 651 | 648
2019-03-25 13:00 | 655 | 652
2019-03-25 13:30 | 694 | 689
2019-03-25 14:00 | 723 | 716
2019-03-25 14:30 | 751 | 744
2019-03-25 15:00 | 776 | 769
2019-03-25 15:30 | 773 | 765
2019-03-25 16:00 | 769 | 760
2019-03-25 16:30 | 765 | 754
2019-03-25 17:00 | 777 | 766
2019-03-25 17:30 | 775 | 763
2019-03-25 18:00 | 765 | 752
2019-03-25 18:30 | 749 | 737
2019-03-25 19:00 | 747 | 733
2019-03-25 19:30 | 720 | 714
2019-03-25 20:00 | 698 | 693
2019-03-25 20:30 | 666 | 661
2019-03-25 21:00 | 627 | 626
2019-03-25 21:30 | 595 | 594
2019-03-25 22:00 | 566 | 565
2019-03-25 22:30 | 538 | 537
2019-03-25 23:00 | 515 | 513
2019-03-25 23:30 | 496 | 495
2019-03-26 | 477 | 475
2019-03-26 00:30 | 437 | 435
2019-03-26 01:00 | 413 | 411
2019-03-26 01:30 | 391 | 389
2019-03-26 02:00 | 379 | 378
2019-03-26 02:30 | 378 | 376
2019-03-26 03:00 | 379 | 376
2019-03-26 03:30 | 380 | 376
2019-03-26 04:00 | 373 | 370
2019-03-26 04:30 | 381 | 378
2019-03-26 05:00 | 387 | 384
2019-03-26 05:30 | 418 | 416
2019-03-26 06:00 | 464 | 463
2019-03-26 06:30 | 516 | 515
2019-03-26 07:00 | 558 | 558
2019-03-26 07:30 | 590 | 586
2019-03-26 08:00 | 599 | 594
2019-03-26 08:30 | 606 | 602
2019-03-26 09:00 | 603 | 598
2019-03-26 09:30 | 600 | 596
2019-03-26 10:00 | 602 | 598
2019-03-26 10:30 | 624 | 621
2019-03-26 11:00 | 640 | 637
2019-03-26 11:30 | 658 | 655
2019-03-26 12:00 | 646 | 642
2019-03-26 12:30 | 644 | 640
2019-03-26 13:00 | 647 | 644
2019-03-26 13:30 | 681 | 678
2019-03-26 14:00 | 679 | 677
2019-03-26 14:30 | 699 | 696
2019-03-26 15:00 | 728 | 722
2019-03-26 15:30 | 724 | 716
2019-03-26 16:00 | 737 | 729
2019-03-26 16:30 | 741 | 732
2019-03-26 17:00 | 738 | 729
2019-03-26 17:30 | 731 | 722
2019-03-26 18:00 | 718 | 713
2019-03-26 18:30 | 717 | 712
2019-03-26 19:00 | 714 | 708
2019-03-26 19:30 | 685 | 680
2019-03-26 20:00 | 664 | 662
2019-03-26 20:30 | 646 | 644
2019-03-26 21:00 | 619 | 618
2019-03-26 21:30 | 601 | 598
2019-03-26 22:00 | 574 | 570
2019-03-26 22:30 | 540 | 538
2019-03-26 23:00 | 521 | 519
2019-03-26 23:30 | 493 | 489
2019-03-27 | 469 | 467
2019-03-27 00:30 | 445 | 443
2019-03-27 01:00 | 432 | 428
2019-03-27 01:30 | 425 | 421
2019-03-27 02:00 | 420 | 417
2019-03-27 02:30 | 416 | 414
2019-03-27 03:00 | 417 | 414
2019-03-27 03:30 | 417 | 414
2019-03-27 04:00 | 422 | 419
2019-03-27 04:30 | 426 | 423
2019-03-27 05:00 | 423 | 421
2019-03-27 05:30 | 438 | 437
2019-03-27 06:00 | 468 | 467
2019-03-27 06:30 | 514 | 514
2019-03-27 07:00 | 534 | 533
2019-03-27 07:30 | 546 | 546
2019-03-27 08:00 | 547 | 547
2019-03-27 08:30 | 551 | 551
2019-03-27 09:00 | 558 | 558
2019-03-27 09:30 | 563 | 561
2019-03-27 10:00 | 568 | 566
2019-03-27 10:30 | 562 | 560
2019-03-27 11:00 | 567 | 566
2019-03-27 11:30 | 560 | 559
2019-03-27 12:00 | 572 | 570
2019-03-27 12:30 | 573 | 571
2019-03-27 13:00 | 566 | 564
2019-03-27 13:30 | 574 | 572
2019-03-27 14:00 | 571 | 569
2019-03-27 14:30 | 569 | 567
2019-03-27 15:00 | 567 | 565
2019-03-27 15:30 | 570 | 567
2019-03-27 16:00 | 569 | 566
2019-03-27 16:30 | 568 | 565
2019-03-27 17:00 | 569 | 568
2019-03-27 17:30 | 575 | 572
2019-03-27 18:00 | 578 | 576
2019-03-27 18:30 | 566 | 563
2019-03-27 19:00 | 560 | 556
2019-03-27 19:30 | 542 | 537
2019-03-27 20:00 | 535 | 531
2019-03-27 20:30 | 511 | 508
2019-03-27 21:00 | 485 | 483
2019-03-27 21:30 | 474 | 472
2019-03-27 22:00 | 464 | 461
2019-03-27 22:30 | 451 | 448
2019-03-27 23:00 | 448 | 445
2019-03-27 23:30 | 428 | 423
2019-03-28 | 408 | 402
2019-03-28 00:30 | 392 | 385
2019-03-28 01:00 | 383 | 374
2019-03-28 01:30 | 371 | 361
2019-03-28 02:00 | 362 | 351
2019-03-28 02:30 | 353 | 342
2019-03-28 03:00 | 366 | 355
2019-03-28 03:30 | 364 | 352
2019-03-28 04:00 | 368 | 357
2019-03-28 04:30 | 377 | 367
2019-03-28 05:00 | 382 | 373
2019-03-28 05:30 | 402 | 395
2019-03-28 06:00 | 433 | 428
2019-03-28 06:30 | 464 | 461
2019-03-28 07:00 | 496 | 495
2019-03-28 07:30 | 507 | 507
2019-03-28 08:00 | 505 | 504
2019-03-28 08:30 | 491 | 491
2019-03-28 09:00 | 489 | 489
2019-03-28 09:30 | 494 | 494
2019-03-28 10:00 | 506 | 506
2019-03-28 10:30 | 529 | 528
2019-03-28 11:00 | 544 | 541
2019-03-28 11:30 | 552 | 550
2019-03-28 12:00 | 536 | 534
2019-03-28 12:30 | 532 | 529
2019-03-28 13:00 | 551 | 549
2019-03-28 13:30 | 548 | 546
2019-03-28 14:00 | 538 | 535
2019-03-28 14:30 | 542 | 539
2019-03-28 15:00 | 542 | 539
2019-03-28 15:30 | 542 | 538
2019-03-28 16:00 | 548 | 545
2019-03-28 16:30 | 560 | 556
2019-03-28 17:00 | 572 | 568
2019-03-28 17:30 | 576 | 572
2019-03-28 18:00 | 580 | 576
2019-03-28 18:30 | 588 | 582
2019-03-28 19:00 | 609 | 596
2019-03-28 19:30 | 584 | 570
2019-03-28 20:00 | 559 | 556
2019-03-28 20:30 | 547 | 544
2019-03-28 21:00 | 517 | 512
2019-03-28 21:30 | 485 | 484
2019-03-28 22:00 | 476 | 475
2019-03-28 22:30 | 460 | 459
2019-03-28 23:00 | 452 | 450
2019-03-28 23:30 | 436 | 432
2019-03-29 | 404 | 399
2019-03-29 00:30 | 388 | 381
2019-03-29 01:00 | 383 | 375
2019-03-29 01:30 | 374 | 365
2019-03-29 02:00 | 362 | 352
2019-03-29 02:30 | 360 | 351
2019-03-29 03:00 | 354 | 343
2019-03-29 03:30 | 358 | 348
2019-03-29 04:00 | 361 | 351
2019-03-29 04:30 | 366 | 356
2019-03-29 05:00 | 370 | 362
2019-03-29 05:30 | 396 | 389
2019-03-29 06:00 | 416 | 411
2019-03-29 06:30 | 459 | 456
2019-03-29 07:00 | 495 | 493
2019-03-29 07:30 | 502 | 501
2019-03-29 08:00 | 499 | 497
2019-03-29 08:30 | 507 | 506
2019-03-29 09:00 | 510 | 509
2019-03-29 09:30 | 508 | 507
2019-03-29 10:00 | 527 | 525
2019-03-29 10:30 | 531 | 530
2019-03-29 11:00 | 525 | 523
2019-03-29 11:30 | 508 | 506
2019-03-29 12:00 | 519 | 517
2019-03-29 12:30 | 522 | 520
2019-03-29 13:00 | 533 | 532
2019-03-29 13:30 | 552 | 551
2019-03-29 14:00 | 556 | 554
2019-03-29 14:30 | 553 | 551
2019-03-29 15:00 | 562 | 560
2019-03-29 15:30 | 579 | 577
2019-03-29 16:00 | 593 | 591
2019-03-29 16:30 | 608 | 606
2019-03-29 17:00 | 625 | 623
2019-03-29 17:30 | 612 | 609
2019-03-29 18:00 | 601 | 598
2019-03-29 18:30 | 596 | 592
2019-03-29 19:00 | 596 | 592
2019-03-29 19:30 | 578 | 573
2019-03-29 20:00 | 563 | 560
2019-03-29 20:30 | 543 | 541
2019-03-29 21:00 | 517 | 515
2019-03-29 21:30 | 503 | 502
2019-03-29 22:00 | 475 | 474
2019-03-29 22:30 | 452 | 451
2019-03-29 23:00 | 444 | 442
2019-03-29 23:30 | 428 | 425
2019-03-30 | 406 | 403
2019-03-30 00:30 | 376 | 372
2019-03-30 01:00 | 361 | 357
2019-03-30 01:30 | 346 | 341
2019-03-30 02:00 | 338 | 332
2019-03-30 02:30 | 332 | 326
2019-03-30 03:00 | 334 | 327
2019-03-30 03:30 | 334 | 327
2019-03-30 04:00 | 335 | 328
2019-03-30 04:30 | 336 | 329
2019-03-30 05:00 | 333 | 327
2019-03-30 05:30 | 331 | 325
2019-03-30 06:00 | 344 | 338
2019-03-30 06:30 | 362 | 357
2019-03-30 07:00 | 391 | 387
2019-03-30 07:30 | 433 | 429
2019-03-30 08:00 | 472 | 469
2019-03-30 08:30 | 491 | 489
2019-03-30 09:00 | 504 | 503
2019-03-30 09:30 | 501 | 500
2019-03-30 10:00 | 500 | 499
2019-03-30 10:30 | 520 | 519
2019-03-30 11:00 | 496 | 495
2019-03-30 11:30 | 492 | 491
2019-03-30 12:00 | 494 | 494
2019-03-30 12:30 | 501 | 500
2019-03-30 13:00 | 492 | 491
2019-03-30 13:30 | 498 | 494
2019-03-30 14:00 | 499 | 493
2019-03-30 14:30 | 487 | 479
2019-03-30 15:00 | 499 | 491
2019-03-30 15:30 | 496 | 488
2019-03-30 16:00 | 493 | 484
2019-03-30 16:30 | 504 | 495
2019-03-30 17:00 | 513 | 503
2019-03-30 17:30 | 521 | 511
2019-03-30 18:00 | 510 | 500
2019-03-30 18:30 | 512 | 510
2019-03-30 19:00 | 519 | 517
2019-03-30 19:30 | 520 | 518
2019-03-30 20:00 | 501 | 498
2019-03-30 20:30 | 484 | 483
2019-03-30 21:00 | 471 | 470
2019-03-30 21:30 | 450 | 448
2019-03-30 22:00 | 430 | 427
2019-03-30 22:30 | 418 | 415
2019-03-30 23:00 | 402 | 398
2019-03-30 23:30 | 387 | 382
2019-03-31 | 370 | 362
2019-03-31 00:30 | 342 | 331
2019-03-31 01:00 | 334 | 322
2019-03-31 01:30 | 326 | 312
2019-03-31 02:00 | 315 | 300
2019-03-31 02:30 | 308 | 291
2019-03-31 03:00 | 310 | 293
2019-03-31 03:30 | 312 | 296
2019-03-31 04:00 | 326 | 310
2019-03-31 04:30 | 321 | 306
2019-03-31 05:00 | 323 | 308
2019-03-31 05:30 | 333 | 319
2019-03-31 06:00 | 340 | 325
2019-03-31 06:30 | 356 | 341
2019-03-31 07:00 | 369 | 354
2019-03-31 07:30 | 375 | 361
2019-03-31 08:00 | 368 | 356
2019-03-31 08:30 | 363 | 351
2019-03-31 09:00 | 362 | 352
2019-03-31 09:30 | 362 | 352
2019-03-31 10:00 | 353 | 344
2019-03-31 10:30 | 345 | 337
2019-03-31 11:00 | 336 | 328
2019-03-31 11:30 | 330 | 322
2019-03-31 12:00 | 327 | 319
2019-03-31 12:30 | 328 | 321
2019-03-31 13:00 | 329 | 322
2019-03-31 13:30 | 340 | 333
2019-03-31 14:00 | 349 | 342
2019-03-31 14:30 | 361 | 355
2019-03-31 15:00 | 375 | 370
2019-03-31 15:30 | 398 | 394
2019-03-31 16:00 | 419 | 415
2019-03-31 16:30 | 447 | 444
2019-03-31 17:00 | 484 | 481
2019-03-31 17:30 | 508 | 504
2019-03-31 18:00 | 515 | 511
2019-03-31 18:30 | 527 | 524
2019-03-31 19:00 | 539 | 536
2019-03-31 19:30 | 530 | 526
2019-03-31 20:00 | 513 | 509
2019-03-31 20:30 | 503 | 501
2019-03-31 21:00 | 484 | 480
2019-03-31 21:30 | 468 | 464
2019-03-31 22:00 | 459 | 454
2019-03-31 22:30 | 450 | 445
2019-03-31 23:00 | 434 | 428
2019-03-31 23:30 | 419 | 411
2019-04-01 | 381 | 371
2019-04-01 00:30 | 363 | 350
2019-04-01 01:00 | 362 | 348
2019-04-01 01:30 | 358 | 343
2019-04-01 02:00 | 350 | 335
2019-04-01 02:30 | 340 | 326
2019-04-01 03:00 | 334 | 319
2019-04-01 03:30 | 337 | 322
2019-04-01 04:00 | 338 | 323
2019-04-01 04:30 | 354 | 340
2019-04-01 05:00 | 365 | 353
2019-04-01 05:30 | 397 | 387
2019-04-01 06:00 | 437 | 430
2019-04-01 06:30 | 477 | 473
2019-04-01 07:00 | 519 | 516
2019-04-01 07:30 | 531 | 527
2019-04-01 08:00 | 514 | 511
2019-04-01 08:30 | 510 | 506
2019-04-01 09:00 | 498 | 493
2019-04-01 09:30 | 477 | 473
2019-04-01 10:00 | 477 | 473
2019-04-01 10:30 | 478 | 475
2019-04-01 11:00 | 484 | 481
2019-04-01 11:30 | 491 | 489
2019-04-01 12:00 | 483 | 481
2019-04-01 12:30 | 488 | 485
2019-04-01 13:00 | 493 | 491
2019-04-01 13:30 | 498 | 496
2019-04-01 14:00 | 525 | 524
2019-04-01 14:30 | 543 | 541
2019-04-01 15:00 | 539 | 537
2019-04-01 15:30 | 540 | 538
2019-04-01 16:00 | 552 | 550
2019-04-01 16:30 | 570 | 568
2019-04-01 17:00 | 598 | 596
2019-04-01 17:30 | 611 | 609
2019-04-01 18:00 | 607 | 604
2019-04-01 18:30 | 607 | 605
2019-04-01 19:00 | 605 | 603
2019-04-01 19:30 | 583 | 580
2019-04-01 20:00 | 569 | 567
2019-04-01 20:30 | 565 | 563
2019-04-01 21:00 | 541 | 539
2019-04-01 21:30 | 518 | 515
2019-04-01 22:00 | 506 | 503
2019-04-01 22:30 | 495 | 492
2019-04-01 23:00 | 478 | 474
2019-04-01 23:30 | 464 | 458
2019-04-02 | 419 | 411
2019-04-02 00:30 | 396 | 386
2019-04-02 01:00 | 387 | 376
2019-04-02 01:30 | 374 | 363
2019-04-02 02:00 | 372 | 360
2019-04-02 02:30 | 359 | 346
2019-04-02 03:00 | 360 | 347
2019-04-02 03:30 | 359 | 346
2019-04-02 04:00 | 369 | 356
2019-04-02 04:30 | 375 | 363
2019-04-02 05:00 | 377 | 366
2019-04-02 05:30 | 402 | 394
2019-04-02 06:00 | 435 | 428
2019-04-02 06:30 | 475 | 471
2019-04-02 07:00 | 515 | 513
2019-04-02 07:30 | 537 | 537
2019-04-02 08:00 | 529 | 528
2019-04-02 08:30 | 520 | 519
2019-04-02 09:00 | 505 | 504
2019-04-02 09:30 | 498 | 496
2019-04-02 10:00 | 502 | 501
2019-04-02 10:30 | 517 | 516
2019-04-02 11:00 | 537 | 536
2019-04-02 11:30 | 531 | 530
2019-04-02 12:00 | 530 | 529
2019-04-02 12:30 | 512 | 511
2019-04-02 13:00 | 507 | 506
2019-04-02 13:30 | 505 | 504
2019-04-02 14:00 | 520 | 519
2019-04-02 14:30 | 546 | 545
2019-04-02 15:00 | 547 | 546
2019-04-02 15:30 | 535 | 534
2019-04-02 16:00 | 550 | 549
2019-04-02 16:30 | 577 | 576
2019-04-02 17:00 | 601 | 601
2019-04-02 17:30 | 601 | 600
2019-04-02 18:00 | 609 | 608
2019-04-02 18:30 | 608 | 608
2019-04-02 19:00 | 604 | 604
2019-04-02 19:30 | 589 | 589
2019-04-02 20:00 | 571 | 570
2019-04-02 20:30 | 555 | 555
2019-04-02 21:00 | 522 | 522
2019-04-02 21:30 | 500 | 499
2019-04-02 22:00 | 485 | 484
2019-04-02 22:30 | 480 | 478
2019-04-02 23:00 | 453 | 452
2019-04-02 23:30 | 437 | 435
2019-04-03 | 417 | 413
2019-04-03 00:30 | 401 | 394
2019-04-03 01:00 | 387 | 379
2019-04-03 01:30 | 376 | 367
2019-04-03 02:00 | 371 | 361
2019-04-03 02:30 | 369 | 358
2019-04-03 03:00 | 368 | 357
2019-04-03 03:30 | 367 | 357
2019-04-03 04:00 | 367 | 357
2019-04-03 04:30 | 374 | 364
2019-04-03 05:00 | 381 | 373
2019-04-03 05:30 | 396 | 390
2019-04-03 06:00 | 430 | 426
2019-04-03 06:30 | 482 | 480
2019-04-03 07:00 | 515 | 515
2019-04-03 07:30 | 547 | 546
2019-04-03 08:00 | 572 | 571
2019-04-03 08:30 | 541 | 540
2019-04-03 09:00 | 513 | 512
2019-04-03 09:30 | 533 | 532
2019-04-03 10:00 | 544 | 543
2019-04-03 10:30 | 532 | 530
2019-04-03 11:00 | 527 | 526
2019-04-03 11:30 | 519 | 518
2019-04-03 12:00 | 523 | 521
2019-04-03 12:30 | 533 | 532
2019-04-03 13:00 | 536 | 535
2019-04-03 13:30 | 533 | 532
2019-04-03 14:00 | 544 | 542
2019-04-03 14:30 | 551 | 549
2019-04-03 15:00 | 570 | 568
2019-04-03 15:30 | 574 | 571
2019-04-03 16:00 | 583 | 581
2019-04-03 16:30 | 590 | 588
2019-04-03 17:00 | 616 | 613
2019-04-03 17:30 | 618 | 614
2019-04-03 18:00 | 612 | 609
2019-04-03 18:30 | 610 | 606
2019-04-03 19:00 | 602 | 600
2019-04-03 19:30 | 593 | 591
2019-04-03 20:00 | 584 | 582
2019-04-03 20:30 | 567 | 566
2019-04-03 21:00 | 532 | 532
2019-04-03 21:30 | 504 | 502
2019-04-03 22:00 | 483 | 480
2019-04-03 22:30 | 474 | 472
2019-04-03 23:00 | 464 | 463
2019-04-03 23:30 | 445 | 443
2019-04-04 | 417 | 413
2019-04-04 00:30 | 396 | 390
2019-04-04 01:00 | 382 | 374
2019-04-04 01:30 | 370 | 361
2019-04-04 02:00 | 361 | 352
2019-04-04 02:30 | 349 | 339
2019-04-04 03:00 | 359 | 348
2019-04-04 03:30 | 363 | 353
2019-04-04 04:00 | 365 | 355
2019-04-04 04:30 | 369 | 359
2019-04-04 05:00 | 372 | 364
2019-04-04 05:30 | 385 | 379
2019-04-04 06:00 | 414 | 410
2019-04-04 06:30 | 467 | 464
2019-04-04 07:00 | 504 | 501
2019-04-04 07:30 | 526 | 525
2019-04-04 08:00 | 528 | 527
2019-04-04 08:30 | 515 | 514
2019-04-04 09:00 | 515 | 515
2019-04-04 09:30 | 520 | 519
2019-04-04 10:00 | 510 | 510
2019-04-04 10:30 | 502 | 501
2019-04-04 11:00 | 495 | 494
2019-04-04 11:30 | 492 | 491
2019-04-04 12:00 | 494 | 493
2019-04-04 12:30 | 501 | 500
2019-04-04 13:00 | 512 | 512
2019-04-04 13:30 | 521 | 520
2019-04-04 14:00 | 523 | 522
2019-04-04 14:30 | 529 | 528
2019-04-04 15:00 | 544 | 543
2019-04-04 15:30 | 566 | 565
2019-04-04 16:00 | 583 | 582
2019-04-04 16:30 | 597 | 594
2019-04-04 17:00 | 618 | 614
2019-04-04 17:30 | 617 | 612
2019-04-04 18:00 | 630 | 624
2019-04-04 18:30 | 632 | 626
2019-04-04 19:00 | 628 | 622
2019-04-04 19:30 | 610 | 608
2019-04-04 20:00 | 591 | 590
2019-04-04 20:30 | 567 | 567
2019-04-04 21:00 | 529 | 528
2019-04-04 21:30 | 498 | 497
2019-04-04 22:00 | 482 | 480
2019-04-04 22:30 | 484 | 482
2019-04-04 23:00 | 472 | 469
2019-04-04 23:30 | 447 | 442
2019-04-05 | 426 | 420
2019-04-05 00:30 | 415 | 406
2019-04-05 01:00 | 403 | 394
2019-04-05 01:30 | 375 | 364
2019-04-05 02:00 | 361 | 349
2019-04-05 02:30 | 354 | 341
2019-04-05 03:00 | 355 | 342
2019-04-05 03:30 | 353 | 340
2019-04-05 04:00 | 356 | 343
2019-04-05 04:30 | 362 | 350
2019-04-05 05:00 | 370 | 359
2019-04-05 05:30 | 385 | 376
2019-04-05 06:00 | 403 | 398
2019-04-05 06:30 | 460 | 457
2019-04-05 07:00 | 508 | 506
2019-04-05 07:30 | 539 | 532
2019-04-05 08:00 | 536 | 530
2019-04-05 08:30 | 533 | 528
2019-04-05 09:00 | 521 | 517
2019-04-05 09:30 | 510 | 506
2019-04-05 10:00 | 509 | 505
2019-04-05 10:30 | 503 | 500
2019-04-05 11:00 | 505 | 501
2019-04-05 11:30 | 501 | 498
2019-04-05 12:00 | 500 | 497
2019-04-05 12:30 | 491 | 488
2019-04-05 13:00 | 497 | 494
2019-04-05 13:30 | 516 | 513
2019-04-05 14:00 | 520 | 517
2019-04-05 14:30 | 539 | 536
2019-04-05 15:00 | 559 | 557
2019-04-05 15:30 | 569 | 565
2019-04-05 16:00 | 591 | 586
2019-04-05 16:30 | 601 | 593
2019-04-05 17:00 | 600 | 592
2019-04-05 17:30 | 580 | 572
2019-04-05 18:00 | 572 | 565
2019-04-05 18:30 | 568 | 561
2019-04-05 19:00 | 564 | 557
2019-04-05 19:30 | 543 | 542
2019-04-05 20:00 | 537 | 535
2019-04-05 20:30 | 533 | 532
2019-04-05 21:00 | 510 | 509
2019-04-05 21:30 | 492 | 491
2019-04-05 22:00 | 471 | 468
2019-04-05 22:30 | 461 | 458
2019-04-05 23:00 | 458 | 454
2019-04-05 23:30 | 448 | 442
2019-04-06 | 422 | 415
2019-04-06 00:30 | 395 | 387
2019-04-06 01:00 | 383 | 375
2019-04-06 01:30 | 360 | 351
2019-04-06 02:00 | 355 | 345
2019-04-06 02:30 | 339 | 329
2019-04-06 03:00 | 324 | 313
2019-04-06 03:30 | 320 | 309
2019-04-06 04:00 | 323 | 309
2019-04-06 04:30 | 322 | 309
2019-04-06 05:00 | 321 | 309
2019-04-06 05:30 | 347 | 335
2019-04-06 06:00 | 371 | 359
2019-04-06 06:30 | 390 | 378
2019-04-06 07:00 | 399 | 388
2019-04-06 07:30 | 417 | 407
2019-04-06 08:00 | 429 | 421
2019-04-06 08:30 | 428 | 421
2019-04-06 09:00 | 424 | 418
2019-04-06 09:30 | 423 | 418
2019-04-06 10:00 | 404 | 399
2019-04-06 10:30 | 398 | 394
2019-04-06 11:00 | 395 | 389
2019-04-06 11:30 | 394 | 388
2019-04-06 12:00 | 398 | 392
2019-04-06 12:30 | 393 | 386
2019-04-06 13:00 | 385 | 378
2019-04-06 13:30 | 389 | 383
2019-04-06 14:00 | 398 | 391
2019-04-06 14:30 | 420 | 414
2019-04-06 15:00 | 436 | 430
2019-04-06 15:30 | 460 | 454
2019-04-06 16:00 | 488 | 483
2019-04-06 16:30 | 512 | 509
2019-04-06 17:00 | 530 | 527
2019-04-06 17:30 | 535 | 532
2019-04-06 18:00 | 532 | 529
2019-04-06 18:30 | 533 | 532
2019-04-06 19:00 | 534 | 532
2019-04-06 19:30 | 521 | 519
2019-04-06 20:00 | 514 | 512
2019-04-06 20:30 | 498 | 497
2019-04-06 21:00 | 470 | 469
2019-04-06 21:30 | 456 | 454
2019-04-06 22:00 | 456 | 453
2019-04-06 22:30 | 454 | 450
2019-04-06 23:00 | 450 | 445
2019-04-06 23:30 | 420 | 412
2019-04-07 | 391 | 382
2019-04-07 00:30 | 372 | 360
2019-04-07 01:00 | 378 | 364
2019-04-07 01:30 | 375 | 357
2019-04-07 02:00 | 374 | 354
2019-04-07 02:30 | 365 | 343
2019-04-07 03:00 | 361 | 338
2019-04-07 03:30 | 369 | 346
2019-04-07 04:00 | 364 | 341
2019-04-07 04:30 | 359 | 336
2019-04-07 05:00 | 355 | 331
2019-04-07 05:30 | 360 | 337
2019-04-07 06:00 | 365 | 342
2019-04-07 06:30 | 374 | 350
2019-04-07 07:00 | 380 | 357
2019-04-07 07:30 | 388 | 367
2019-04-07 08:00 | 397 | 379
2019-04-07 08:30 | 399 | 384
2019-04-07 09:00 | 400 | 386
2019-04-07 09:30 | 407 | 394
2019-04-07 10:00 | 397 | 386
2019-04-07 10:30 | 384 | 374
2019-04-07 11:00 | 378 | 370
2019-04-07 11:30 | 375 | 367
2019-04-07 12:00 | 379 | 371
2019-04-07 12:30 | 378 | 371
2019-04-07 13:00 | 390 | 384
2019-04-07 13:30 | 394 | 388
2019-04-07 14:00 | 405 | 399
2019-04-07 14:30 | 408 | 403
2019-04-07 15:00 | 416 | 411
2019-04-07 15:30 | 436 | 431
2019-04-07 16:00 | 464 | 459
2019-04-07 16:30 | 496 | 491
2019-04-07 17:00 | 529 | 524
2019-04-07 17:30 | 535 | 531
2019-04-07 18:00 | 551 | 547
2019-04-07 18:30 | 571 | 567
2019-04-07 19:00 | 581 | 576
2019-04-07 19:30 | 563 | 557
2019-04-07 20:00 | 539 | 534
2019-04-07 20:30 | 527 | 523
2019-04-07 21:00 | 503 | 499
2019-04-07 21:30 | 496 | 491
2019-04-07 22:00 | 477 | 471
2019-04-07 22:30 | 461 | 455
2019-04-07 23:00 | 442 | 435
2019-04-07 23:30 | 424 | 413
2019-04-08 | 392 | 379
2019-04-08 00:30 | 377 | 362
2019-04-08 01:00 | 371 | 355
2019-04-08 01:30 | 368 | 350
2019-04-08 02:00 | 365 | 347
2019-04-08 02:30 | 355 | 337
2019-04-08 03:00 | 350 | 332
2019-04-08 03:30 | 357 | 338
2019-04-08 04:00 | 366 | 348
2019-04-08 04:30 | 362 | 344
2019-04-08 05:00 | 359 | 342
2019-04-08 05:30 | 372 | 359
2019-04-08 06:00 | 398 | 388
2019-04-08 06:30 | 446 | 439
2019-04-08 07:00 | 491 | 487
2019-04-08 07:30 | 516 | 513
2019-04-08 08:00 | 534 | 528
2019-04-08 08:30 | 524 | 520
2019-04-08 09:00 | 523 | 520
2019-04-08 09:30 | 518 | 515
2019-04-08 10:00 | 516 | 514
2019-04-08 10:30 | 516 | 515
2019-04-08 11:00 | 517 | 516
2019-04-08 11:30 | 519 | 517
2019-04-08 12:00 | 522 | 520
2019-04-08 12:30 | 522 | 520
2019-04-08 13:00 | 527 | 525
2019-04-08 13:30 | 538 | 537
2019-04-08 14:00 | 546 | 545
2019-04-08 14:30 | 561 | 560
2019-04-08 15:00 | 576 | 573
2019-04-08 15:30 | 594 | 590
2019-04-08 16:00 | 610 | 607
2019-04-08 16:30 | 623 | 620
2019-04-08 17:00 | 628 | 625
2019-04-08 17:30 | 626 | 622
2019-04-08 18:00 | 627 | 623
2019-04-08 18:30 | 640 | 636
2019-04-08 19:00 | 637 | 632
2019-04-08 19:30 | 620 | 615
2019-04-08 20:00 | 594 | 591
2019-04-08 20:30 | 572 | 570
2019-04-08 21:00 | 551 | 548
2019-04-08 21:30 | 533 | 529
2019-04-08 22:00 | 528 | 522
2019-04-08 22:30 | 522 | 515
2019-04-08 23:00 | 498 | 490
2019-04-08 23:30 | 462 | 456
2019-04-09 | 437 | 430
2019-04-09 00:30 | 406 | 397
2019-04-09 01:00 | 388 | 377
2019-04-09 01:30 | 377 | 365
2019-04-09 02:00 | 371 | 359
2019-04-09 02:30 | 363 | 350
2019-04-09 03:00 | 356 | 343
2019-04-09 03:30 | 362 | 349
2019-04-09 04:00 | 356 | 343
2019-04-09 04:30 | 366 | 354
2019-04-09 05:00 | 361 | 350
2019-04-09 05:30 | 372 | 363
2019-04-09 06:00 | 398 | 391
2019-04-09 06:30 | 442 | 438
2019-04-09 07:00 | 470 | 469
2019-04-09 07:30 | 497 | 496
2019-04-09 08:00 | 494 | 493
2019-04-09 08:30 | 513 | 512
2019-04-09 09:00 | 527 | 524
2019-04-09 09:30 | 557 | 552
2019-04-09 10:00 | 548 | 544
2019-04-09 10:30 | 534 | 530
2019-04-09 11:00 | 535 | 532
2019-04-09 11:30 | 535 | 532
2019-04-09 12:00 | 546 | 544
2019-04-09 12:30 | 553 | 550
2019-04-09 13:00 | 564 | 562
2019-04-09 13:30 | 566 | 565
2019-04-09 14:00 | 591 | 591
2019-04-09 14:30 | 612 | 611
2019-04-09 15:00 | 610 | 607
2019-04-09 15:30 | 625 | 622
2019-04-09 16:00 | 641 | 638
2019-04-09 16:30 | 652 | 649
2019-04-09 17:00 | 652 | 648
2019-04-09 17:30 | 640 | 636
2019-04-09 18:00 | 650 | 646
2019-04-09 18:30 | 641 | 636
2019-04-09 19:00 | 632 | 628
2019-04-09 19:30 | 620 | 616
2019-04-09 20:00 | 602 | 598
2019-04-09 20:30 | 590 | 586
2019-04-09 21:00 | 558 | 554
2019-04-09 21:30 | 520 | 516
2019-04-09 22:00 | 500 | 496
2019-04-09 22:30 | 503 | 498
2019-04-09 23:00 | 478 | 472
2019-04-09 23:30 | 451 | 443
2019-04-10 | 428 | 419
2019-04-10 00:30 | 405 | 394
2019-04-10 01:00 | 395 | 381
2019-04-10 01:30 | 398 | 383
2019-04-10 02:00 | 400 | 384
2019-04-10 02:30 | 391 | 375
2019-04-10 03:00 | 395 | 378
2019-04-10 03:30 | 406 | 389
2019-04-10 04:00 | 407 | 390
2019-04-10 04:30 | 398 | 382
2019-04-10 05:00 | 386 | 371
2019-04-10 05:30 | 399 | 387
2019-04-10 06:00 | 411 | 402
2019-04-10 06:30 | 446 | 440
2019-04-10 07:00 | 490 | 486
2019-04-10 07:30 | 510 | 506
2019-04-10 08:00 | 523 | 520
2019-04-10 08:30 | 541 | 539
2019-04-10 09:00 | 545 | 542
2019-04-10 09:30 | 546 | 544
2019-04-10 10:00 | 544 | 541
2019-04-10 10:30 | 541 | 538
2019-04-10 11:00 | 536 | 534
2019-04-10 11:30 | 528 | 525
2019-04-10 12:00 | 528 | 525
2019-04-10 12:30 | 530 | 527
2019-04-10 13:00 | 521 | 519
2019-04-10 13:30 | 519 | 517
2019-04-10 14:00 | 531 | 529
2019-04-10 14:30 | 545 | 542
2019-04-10 15:00 | 564 | 562
2019-04-10 15:30 | 579 | 576
2019-04-10 16:00 | 586 | 584
2019-04-10 16:30 | 601 | 598
2019-04-10 17:00 | 622 | 618
2019-04-10 17:30 | 626 | 621
2019-04-10 18:00 | 637 | 632
2019-04-10 18:30 | 630 | 625
2019-04-10 19:00 | 619 | 613
2019-04-10 19:30 | 591 | 584
2019-04-10 20:00 | 587 | 578
2019-04-10 20:30 | 570 | 562
2019-04-10 21:00 | 530 | 524
2019-04-10 21:30 | 504 | 497
2019-04-10 22:00 | 489 | 482
2019-04-10 22:30 | 489 | 480
2019-04-10 23:00 | 475 | 465
2019-04-10 23:30 | 439 | 428
2019-04-11 | 417 | 406
2019-04-11 00:30 | 388 | 375
2019-04-11 01:00 | 378 | 362
2019-04-11 01:30 | 370 | 352
2019-04-11 02:00 | 369 | 350
2019-04-11 02:30 | 368 | 349
2019-04-11 03:00 | 367 | 348
2019-04-11 03:30 | 359 | 339
2019-04-11 04:00 | 362 | 341
2019-04-11 04:30 | 360 | 340
2019-04-11 05:00 | 365 | 347
2019-04-11 05:30 | 378 | 363
2019-04-11 06:00 | 409 | 399
2019-04-11 06:30 | 437 | 430
2019-04-11 07:00 | 459 | 455
2019-04-11 07:30 | 488 | 484
2019-04-11 08:00 | 496 | 494
2019-04-11 08:30 | 491 | 489
2019-04-11 09:00 | 513 | 511
2019-04-11 09:30 | 509 | 508
2019-04-11 10:00 | 515 | 513
2019-04-11 10:30 | 510 | 507
2019-04-11 11:00 | 485 | 482
2019-04-11 11:30 | 465 | 461
2019-04-11 12:00 | 456 | 452
2019-04-11 12:30 | 458 | 454
2019-04-11 13:00 | 481 | 478
2019-04-11 13:30 | 500 | 497
2019-04-11 14:00 | 518 | 516
2019-04-11 14:30 | 537 | 533
2019-04-11 15:00 | 531 | 528
2019-04-11 15:30 | 544 | 541
2019-04-11 16:00 | 551 | 548
2019-04-11 16:30 | 569 | 565
2019-04-11 17:00 | 581 | 577
2019-04-11 17:30 | 588 | 584
2019-04-11 18:00 | 599 | 595
2019-04-11 18:30 | 602 | 597
2019-04-11 19:00 | 596 | 591
2019-04-11 19:30 | 575 | 570
2019-04-11 20:00 | 561 | 556
2019-04-11 20:30 | 558 | 552
2019-04-11 21:00 | 535 | 530
2019-04-11 21:30 | 510 | 506
2019-04-11 22:00 | 509 | 505
2019-04-11 22:30 | 498 | 494
2019-04-11 23:00 | 490 | 485
2019-04-11 23:30 | 475 | 469
2019-04-12 | 443 | 434
2019-04-12 00:30 | 414 | 402
2019-04-12 01:00 | 391 | 374
2019-04-12 01:30 | 374 | 356
2019-04-12 02:00 | 370 | 351
2019-04-12 02:30 | 378 | 359
2019-04-12 03:00 | 372 | 352
2019-04-12 03:30 | 367 | 346
2019-04-12 04:00 | 373 | 353
2019-04-12 04:30 | 374 | 355
2019-04-12 05:00 | 372 | 354
2019-04-12 05:30 | 389 | 374
2019-04-12 06:00 | 409 | 397
2019-04-12 06:30 | 446 | 437
2019-04-12 07:00 | 475 | 469
2019-04-12 07:30 | 501 | 497
2019-04-12 08:00 | 522 | 517
2019-04-12 08:30 | 517 | 513
2019-04-12 09:00 | 508 | 504
2019-04-12 09:30 | 511 | 507
2019-04-12 10:00 | 517 | 514
2019-04-12 10:30 | 539 | 536
2019-04-12 11:00 | 550 | 546
2019-04-12 11:30 | 549 | 546
2019-04-12 12:00 | 549 | 544
2019-04-12 12:30 | 538 | 533
2019-04-12 13:00 | 549 | 544
2019-04-12 13:30 | 550 | 545
2019-04-12 14:00 | 551 | 547
2019-04-12 14:30 | 569 | 567
2019-04-12 15:00 | 558 | 555
2019-04-12 15:30 | 545 | 541
2019-04-12 16:00 | 554 | 550
2019-04-12 16:30 | 568 | 564
2019-04-12 17:00 | 581 | 577
2019-04-12 17:30 | 577 | 573
2019-04-12 18:00 | 588 | 585
2019-04-12 18:30 | 576 | 572
2019-04-12 19:00 | 568 | 564
2019-04-12 19:30 | 557 | 552
2019-04-12 20:00 | 554 | 548
2019-04-12 20:30 | 544 | 539
2019-04-12 21:00 | 522 | 519
2019-04-12 21:30 | 502 | 498
2019-04-12 22:00 | 489 | 484
2019-04-12 22:30 | 484 | 478
2019-04-12 23:00 | 479 | 473
2019-04-12 23:30 | 471 | 463
2019-04-13 | 447 | 438
2019-04-13 00:30 | 412 | 399
2019-04-13 01:00 | 387 | 371
2019-04-13 01:30 | 378 | 360
2019-04-13 02:00 | 376 | 357
2019-04-13 02:30 | 377 | 357
2019-04-13 03:00 | 382 | 362
2019-04-13 03:30 | 375 | 354
2019-04-13 04:00 | 377 | 356
2019-04-13 04:30 | 363 | 342
2019-04-13 05:00 | 355 | 335
2019-04-13 05:30 | 371 | 352
2019-04-13 06:00 | 388 | 370
2019-04-13 06:30 | 410 | 392
2019-04-13 07:00 | 427 | 411
2019-04-13 07:30 | 443 | 429
2019-04-13 08:00 | 439 | 426
2019-04-13 08:30 | 435 | 424
2019-04-13 09:00 | 432 | 423
2019-04-13 09:30 | 429 | 421
2019-04-13 10:00 | 423 | 415
2019-04-13 10:30 | 418 | 412
2019-04-13 11:00 | 419 | 413
2019-04-13 11:30 | 417 | 409
2019-04-13 12:00 | 410 | 402
2019-04-13 12:30 | 407 | 399
2019-04-13 13:00 | 409 | 401
2019-04-13 13:30 | 411 | 403
2019-04-13 14:00 | 423 | 415
2019-04-13 14:30 | 438 | 430
2019-04-13 15:00 | 446 | 439
2019-04-13 15:30 | 467 | 460
2019-04-13 16:00 | 488 | 482
2019-04-13 16:30 | 501 | 495
2019-04-13 17:00 | 510 | 505
2019-04-13 17:30 | 511 | 506
2019-04-13 18:00 | 512 | 508
2019-04-13 18:30 | 510 | 507
2019-04-13 19:00 | 512 | 509
2019-04-13 19:30 | 504 | 500
2019-04-13 20:00 | 505 | 500
2019-04-13 20:30 | 499 | 495
2019-04-13 21:00 | 489 | 483
2019-04-13 21:30 | 479 | 472
2019-04-13 22:00 | 465 | 457
2019-04-13 22:30 | 456 | 447
2019-04-13 23:00 | 446 | 436
2019-04-13 23:30 | 426 | 416
2019-04-14 | 403 | 388
2019-04-14 00:30 | 378 | 357
2019-04-14 01:00 | 371 | 348
2019-04-14 01:30 | 369 | 344
2019-04-14 02:00 | 371 | 346
2019-04-14 02:30 | 373 | 347
2019-04-14 03:00 | 371 | 344
2019-04-14 03:30 | 370 | 340
2019-04-14 04:00 | 365 | 335
2019-04-14 04:30 | 366 | 336
2019-04-14 05:00 | 355 | 325
2019-04-14 05:30 | 358 | 328
2019-04-14 06:00 | 368 | 339
2019-04-14 06:30 | 384 | 354
2019-04-14 07:00 | 393 | 365
2019-04-14 07:30 | 404 | 379
2019-04-14 08:00 | 419 | 396
2019-04-14 08:30 | 430 | 411
2019-04-14 09:00 | 426 | 409
2019-04-14 09:30 | 427 | 412
2019-04-14 10:00 | 415 | 403
2019-04-14 10:30 | 424 | 413
2019-04-14 11:00 | 426 | 416
2019-04-14 11:30 | 418 | 408
2019-04-14 12:00 | 422 | 411
2019-04-14 12:30 | 416 | 406
2019-04-14 13:00 | 415 | 406
2019-04-14 13:30 | 418 | 409
2019-04-14 14:00 | 423 | 413
2019-04-14 14:30 | 438 | 428
2019-04-14 15:00 | 451 | 442
2019-04-14 15:30 | 470 | 461
2019-04-14 16:00 | 495 | 487
2019-04-14 16:30 | 503 | 496
2019-04-14 17:00 | 516 | 509
2019-04-14 17:30 | 525 | 518
2019-04-14 18:00 | 535 | 526
2019-04-14 18:30 | 544 | 536
2019-04-14 19:00 | 532 | 525
2019-04-14 19:30 | 523 | 513
2019-04-14 20:00 | 524 | 514
2019-04-14 20:30 | 519 | 510
2019-04-14 21:00 | 504 | 496
2019-04-14 21:30 | 500 | 491
2019-04-14 22:00 | 496 | 486
2019-04-14 22:30 | 483 | 471
2019-04-14 23:00 | 475 | 462
2019-04-14 23:30 | 450 | 435
2019-04-15 | 415 | 396
2019-04-15 00:30 | 396 | 373
2019-04-15 01:00 | 379 | 355
2019-04-15 01:30 | 384 | 359
2019-04-15 02:00 | 382 | 357
2019-04-15 02:30 | 384 | 359
2019-04-15 03:00 | 383 | 358
2019-04-15 03:30 | 390 | 365
2019-04-15 04:00 | 396 | 372
2019-04-15 04:30 | 391 | 366
2019-04-15 05:00 | 390 | 366
2019-04-15 05:30 | 406 | 387
2019-04-15 06:00 | 432 | 417
2019-04-15 06:30 | 462 | 451
2019-04-15 07:00 | 494 | 486
2019-04-15 07:30 | 537 | 526
2019-04-15 08:00 | 569 | 547
2019-04-15 08:30 | 565 | 543
2019-04-15 09:00 | 555 | 532
2019-04-15 09:30 | 549 | 527
2019-04-15 10:00 | 548 | 525
2019-04-15 10:30 | 553 | 529
2019-04-15 11:00 | 563 | 540
2019-04-15 11:30 | 566 | 544
2019-04-15 12:00 | 571 | 550
2019-04-15 12:30 | 573 | 551
2019-04-15 13:00 | 574 | 552
2019-04-15 13:30 | 570 | 548
2019-04-15 14:00 | 567 | 545
2019-04-15 14:30 | 562 | 546
2019-04-15 15:00 | 568 | 556
2019-04-15 15:30 | 576 | 565
2019-04-15 16:00 | 581 | 570
2019-04-15 16:30 | 598 | 587
2019-04-15 17:00 | 607 | 595
2019-04-15 17:30 | 612 | 600
2019-04-15 18:00 | 608 | 597
2019-04-15 18:30 | 597 | 585
2019-04-15 19:00 | 584 | 572
2019-04-15 19:30 | 562 | 556
2019-04-15 20:00 | 548 | 542
2019-04-15 20:30 | 546 | 540
2019-04-15 21:00 | 530 | 528
2019-04-15 21:30 | 512 | 510
2019-04-15 22:00 | 503 | 499
2019-04-15 22:30 | 495 | 491
2019-04-15 23:00 | 486 | 482
2019-04-15 23:30 | 474 | 470
2019-04-16 | 458 | 452
2019-04-16 00:30 | 419 | 410
2019-04-16 01:00 | 392 | 382
2019-04-16 01:30 | 380 | 368
2019-04-16 02:00 | 374 | 362
2019-04-16 02:30 | 372 | 360
2019-04-16 03:00 | 370 | 357
2019-04-16 03:30 | 363 | 351
2019-04-16 04:00 | 360 | 348
2019-04-16 04:30 | 358 | 347
2019-04-16 05:00 | 361 | 352
2019-04-16 05:30 | 386 | 379
2019-04-16 06:00 | 424 | 418
2019-04-16 06:30 | 453 | 449
2019-04-16 07:00 | 487 | 485
2019-04-16 07:30 | 517 | 516
2019-04-16 08:00 | 532 | 532
2019-04-16 08:30 | 539 | 538
2019-04-16 09:00 | 538 | 537
2019-04-16 09:30 | 534 | 532
2019-04-16 10:00 | 530 | 529
2019-04-16 10:30 | 540 | 539
2019-04-16 11:00 | 537 | 536
2019-04-16 11:30 | 534 | 534
2019-04-16 12:00 | 538 | 537
2019-04-16 12:30 | 545 | 544
2019-04-16 13:00 | 542 | 541
2019-04-16 13:30 | 545 | 544
2019-04-16 14:00 | 548 | 548
2019-04-16 14:30 | 556 | 555
2019-04-16 15:00 | 565 | 564
2019-04-16 15:30 | 562 | 560
2019-04-16 16:00 | 569 | 567
2019-04-16 16:30 | 583 | 582
2019-04-16 17:00 | 595 | 593
2019-04-16 17:30 | 597 | 596
2019-04-16 18:00 | 599 | 598
2019-04-16 18:30 | 599 | 598
2019-04-16 19:00 | 593 | 591
2019-04-16 19:30 | 584 | 580
2019-04-16 20:00 | 581 | 578
2019-04-16 20:30 | 561 | 558
2019-04-16 21:00 | 542 | 540
2019-04-16 21:30 | 515 | 512
2019-04-16 22:00 | 504 | 500
2019-04-16 22:30 | 483 | 479
2019-04-16 23:00 | 461 | 458
2019-04-16 23:30 | 445 | 441
2019-04-17 | 425 | 421
2019-04-17 00:30 | 392 | 386
2019-04-17 01:00 | 388 | 381
2019-04-17 01:30 | 368 | 358
2019-04-17 02:00 | 362 | 352
2019-04-17 02:30 | 361 | 351
2019-04-17 03:00 | 350 | 339
2019-04-17 03:30 | 343 | 332
2019-04-17 04:00 | 329 | 317
2019-04-17 04:30 | 331 | 320
2019-04-17 05:00 | 339 | 329
2019-04-17 05:30 | 365 | 357
2019-04-17 06:00 | 404 | 398
2019-04-17 06:30 | 446 | 442
2019-04-17 07:00 | 472 | 470
2019-04-17 07:30 | 497 | 496
2019-04-17 08:00 | 509 | 508
2019-04-17 08:30 | 504 | 503
2019-04-17 09:00 | 514 | 513
2019-04-17 09:30 | 511 | 510
2019-04-17 10:00 | 513 | 509
2019-04-17 10:30 | 535 | 530
2019-04-17 11:00 | 536 | 530
2019-04-17 11:30 | 537 | 531
2019-04-17 12:00 | 541 | 535
2019-04-17 12:30 | 528 | 522
2019-04-17 13:00 | 530 | 524
2019-04-17 13:30 | 528 | 522
2019-04-17 14:00 | 526 | 519
2019-04-17 14:30 | 546 | 540
2019-04-17 15:00 | 553 | 546
2019-04-17 15:30 | 566 | 560
2019-04-17 16:00 | 587 | 580
2019-04-17 16:30 | 595 | 588
2019-04-17 17:00 | 601 | 595
2019-04-17 17:30 | 599 | 592
2019-04-17 18:00 | 602 | 595
2019-04-17 18:30 | 598 | 590
2019-04-17 19:00 | 588 | 579
2019-04-17 19:30 | 568 | 558
2019-04-17 20:00 | 566 | 554
2019-04-17 20:30 | 553 | 549
2019-04-17 21:00 | 543 | 538
2019-04-17 21:30 | 523 | 518
2019-04-17 22:00 | 505 | 502
2019-04-17 22:30 | 489 | 486
2019-04-17 23:00 | 475 | 471
2019-04-17 23:30 | 467 | 461
2019-04-18 | 450 | 442
2019-04-18 00:30 | 410 | 401
2019-04-18 01:00 | 380 | 369
2019-04-18 01:30 | 364 | 351
2019-04-18 02:00 | 353 | 340
2019-04-18 02:30 | 353 | 340
2019-04-18 03:00 | 357 | 343
2019-04-18 03:30 | 351 | 337
2019-04-18 04:00 | 350 | 333
2019-04-18 04:30 | 353 | 337
2019-04-18 05:00 | 356 | 342
2019-04-18 05:30 | 371 | 360
2019-04-18 06:00 | 390 | 381
2019-04-18 06:30 | 437 | 432
2019-04-18 07:00 | 482 | 479
2019-04-18 07:30 | 521 | 519
2019-04-18 08:00 | 540 | 537
2019-04-18 08:30 | 544 | 541
2019-04-18 09:00 | 536 | 533
2019-04-18 09:30 | 524 | 521
2019-04-18 10:00 | 521 | 517
2019-04-18 10:30 | 530 | 528
2019-04-18 11:00 | 541 | 539
2019-04-18 11:30 | 527 | 523
2019-04-18 12:00 | 514 | 510
2019-04-18 12:30 | 524 | 520
2019-04-18 13:00 | 528 | 525
2019-04-18 13:30 | 533 | 529
2019-04-18 14:00 | 535 | 532
2019-04-18 14:30 | 546 | 543
2019-04-18 15:00 | 570 | 568
2019-04-18 15:30 | 570 | 569
2019-04-18 16:00 | 573 | 572
2019-04-18 16:30 | 588 | 586
2019-04-18 17:00 | 596 | 594
2019-04-18 17:30 | 603 | 601
2019-04-18 18:00 | 602 | 600
2019-04-18 18:30 | 594 | 592
2019-04-18 19:00 | 589 | 586
2019-04-18 19:30 | 563 | 560
2019-04-18 20:00 | 551 | 550
2019-04-18 20:30 | 540 | 539
2019-04-18 21:00 | 528 | 527
2019-04-18 21:30 | 499 | 498
2019-04-18 22:00 | 463 | 462
2019-04-18 22:30 | 453 | 451
2019-04-18 23:00 | 430 | 428
2019-04-18 23:30 | 405 | 402
2019-04-19 | 392 | 387
2019-04-19 00:30 | 365 | 358
2019-04-19 01:00 | 351 | 342
2019-04-19 01:30 | 344 | 335
2019-04-19 02:00 | 342 | 332
2019-04-19 02:30 | 342 | 331
2019-04-19 03:00 | 344 | 333
2019-04-19 03:30 | 335 | 324
2019-04-19 04:00 | 336 | 324
2019-04-19 04:30 | 330 | 318
2019-04-19 05:00 | 324 | 312
2019-04-19 05:30 | 329 | 318
2019-04-19 06:00 | 343 | 333
2019-04-19 06:30 | 352 | 342
2019-04-19 07:00 | 368 | 359
2019-04-19 07:30 | 396 | 387
2019-04-19 08:00 | 413 | 406
2019-04-19 08:30 | 412 | 406
2019-04-19 09:00 | 413 | 407
2019-04-19 09:30 | 409 | 405
2019-04-19 10:00 | 400 | 395
2019-04-19 10:30 | 395 | 391
2019-04-19 11:00 | 378 | 374
2019-04-19 11:30 | 375 | 371
2019-04-19 12:00 | 382 | 378
2019-04-19 12:30 | 381 | 377
2019-04-19 13:00 | 372 | 367
2019-04-19 13:30 | 374 | 369
2019-04-19 14:00 | 406 | 402
2019-04-19 14:30 | 425 | 422
2019-04-19 15:00 | 421 | 418
2019-04-19 15:30 | 432 | 430
2019-04-19 16:00 | 436 | 434
2019-04-19 16:30 | 460 | 457
2019-04-19 17:00 | 477 | 474
2019-04-19 17:30 | 488 | 486
2019-04-19 18:00 | 498 | 497
2019-04-19 18:30 | 499 | 497
2019-04-19 19:00 | 493 | 491
2019-04-19 19:30 | 469 | 467
2019-04-19 20:00 | 458 | 456
2019-04-19 20:30 | 460 | 457
2019-04-19 21:00 | 441 | 438
2019-04-19 21:30 | 432 | 428
2019-04-19 22:00 | 426 | 422
2019-04-19 22:30 | 422 | 418
2019-04-19 23:00 | 419 | 415
2019-04-19 23:30 | 414 | 409
2019-04-20 | 398 | 391
2019-04-20 00:30 | 373 | 364
2019-04-20 01:00 | 354 | 345
2019-04-20 01:30 | 345 | 334
2019-04-20 02:00 | 340 | 328
2019-04-20 02:30 | 336 | 323
2019-04-20 03:00 | 332 | 319
2019-04-20 03:30 | 331 | 318
2019-04-20 04:00 | 327 | 314
2019-04-20 04:30 | 329 | 315
2019-04-20 05:00 | 324 | 311
2019-04-20 05:30 | 334 | 322
2019-04-20 06:00 | 345 | 333
2019-04-20 06:30 | 350 | 338
2019-04-20 07:00 | 361 | 349
2019-04-20 07:30 | 384 | 374
2019-04-20 08:00 | 404 | 396
2019-04-20 08:30 | 413 | 407
2019-04-20 09:00 | 417 | 412
2019-04-20 09:30 | 423 | 419
2019-04-20 10:00 | 434 | 431
2019-04-20 10:30 | 443 | 441
2019-04-20 11:00 | 428 | 425
2019-04-20 11:30 | 403 | 400
2019-04-20 12:00 | 413 | 410
2019-04-20 12:30 | 407 | 404
2019-04-20 13:00 | 413 | 411
2019-04-20 13:30 | 416 | 414
2019-04-20 14:00 | 419 | 416
2019-04-20 14:30 | 426 | 424
2019-04-20 15:00 | 450 | 448
2019-04-20 15:30 | 458 | 456
2019-04-20 16:00 | 455 | 453
2019-04-20 16:30 | 475 | 473
2019-04-20 17:00 | 495 | 493
2019-04-20 17:30 | 488 | 486
2019-04-20 18:00 | 500 | 499
2019-04-20 18:30 | 502 | 500
2019-04-20 19:00 | 496 | 494
2019-04-20 19:30 | 475 | 472
2019-04-20 20:00 | 461 | 459
2019-04-20 20:30 | 448 | 447
2019-04-20 21:00 | 422 | 420
2019-04-20 21:30 | 402 | 400
2019-04-20 22:00 | 404 | 400
2019-04-20 22:30 | 399 | 395
2019-04-20 23:00 | 396 | 392
2019-04-20 23:30 | 398 | 392
2019-04-21 | 373 | 365
2019-04-21 00:30 | 350 | 341
2019-04-21 01:00 | 333 | 321
2019-04-21 01:30 | 327 | 314
2019-04-21 02:00 | 329 | 315
2019-04-21 02:30 | 322 | 307
2019-04-21 03:00 | 323 | 307
2019-04-21 03:30 | 322 | 306
2019-04-21 04:00 | 333 | 316
2019-04-21 04:30 | 325 | 308
2019-04-21 05:00 | 328 | 311
2019-04-21 05:30 | 336 | 319
2019-04-21 06:00 | 341 | 325
2019-04-21 06:30 | 344 | 328
2019-04-21 07:00 | 348 | 332
2019-04-21 07:30 | 368 | 353
2019-04-21 08:00 | 379 | 366
2019-04-21 08:30 | 384 | 373
2019-04-21 09:00 | 398 | 392
2019-04-21 09:30 | 404 | 399
2019-04-21 10:00 | 398 | 393
2019-04-21 10:30 | 409 | 405
2019-04-21 11:00 | 412 | 408
2019-04-21 11:30 | 366 | 361
2019-04-21 12:00 | 360 | 354
2019-04-21 12:30 | 357 | 351
2019-04-21 13:00 | 369 | 363
2019-04-21 13:30 | 361 | 355
2019-04-21 14:00 | 363 | 357
2019-04-21 14:30 | 401 | 396
2019-04-21 15:00 | 390 | 385
2019-04-21 15:30 | 424 | 419
2019-04-21 16:00 | 439 | 435
2019-04-21 16:30 | 477 | 473
2019-04-21 17:00 | 490 | 486
2019-04-21 17:30 | 492 | 489
2019-04-21 18:00 | 501 | 498
2019-04-21 18:30 | 501 | 496
2019-04-21 19:00 | 491 | 486
2019-04-21 19:30 | 470 | 464
2019-04-21 20:00 | 463 | 460
2019-04-21 20:30 | 461 | 458
2019-04-21 21:00 | 424 | 421
2019-04-21 21:30 | 408 | 404
2019-04-21 22:00 | 403 | 398
2019-04-21 22:30 | 402 | 396
2019-04-21 23:00 | 399 | 393
2019-04-21 23:30 | 394 | 387
2019-04-22 | 375 | 367
2019-04-22 00:30 | 355 | 345
2019-04-22 01:00 | 341 | 329
2019-04-22 01:30 | 343 | 330
2019-04-22 02:00 | 340 | 326
2019-04-22 02:30 | 333 | 319
2019-04-22 03:00 | 329 | 315
2019-04-22 03:30 | 324 | 310
2019-04-22 04:00 | 324 | 311
2019-04-22 04:30 | 334 | 320
2019-04-22 05:00 | 339 | 325
2019-04-22 05:30 | 342 | 329
2019-04-22 06:00 | 348 | 336
2019-04-22 06:30 | 355 | 343
2019-04-22 07:00 | 358 | 347
2019-04-22 07:30 | 382 | 372
2019-04-22 08:00 | 407 | 399
2019-04-22 08:30 | 417 | 410
2019-04-22 09:00 | 423 | 417
2019-04-22 09:30 | 410 | 405
2019-04-22 10:00 | 403 | 399
2019-04-22 10:30 | 409 | 405
2019-04-22 11:00 | 423 | 419
2019-04-22 11:30 | 421 | 418
2019-04-22 12:00 | 428 | 425
2019-04-22 12:30 | 439 | 435
2019-04-22 13:00 | 429 | 426
2019-04-22 13:30 | 431 | 428
2019-04-22 14:00 | 433 | 429
2019-04-22 14:30 | 443 | 439
2019-04-22 15:00 | 456 | 453
2019-04-22 15:30 | 467 | 465
2019-04-22 16:00 | 480 | 478
2019-04-22 16:30 | 500 | 497
2019-04-22 17:00 | 520 | 518
2019-04-22 17:30 | 526 | 524
2019-04-22 18:00 | 539 | 538
2019-04-22 18:30 | 531 | 529
2019-04-22 19:00 | 521 | 519
2019-04-22 19:30 | 503 | 501
2019-04-22 20:00 | 491 | 489
2019-04-22 20:30 | 493 | 491
2019-04-22 21:00 | 479 | 476
2019-04-22 21:30 | 460 | 458
2019-04-22 22:00 | 436 | 432
2019-04-22 22:30 | 437 | 433
2019-04-22 23:00 | 426 | 422
2019-04-22 23:30 | 407 | 402
2019-04-23 | 381 | 374
2019-04-23 00:30 | 361 | 351
2019-04-23 01:00 | 353 | 342
2019-04-23 01:30 | 346 | 334
2019-04-23 02:00 | 338 | 326
2019-04-23 02:30 | 344 | 331
2019-04-23 03:00 | 340 | 327
2019-04-23 03:30 | 334 | 322
2019-04-23 04:00 | 336 | 323
2019-04-23 04:30 | 325 | 313
2019-04-23 05:00 | 340 | 330
2019-04-23 05:30 | 360 | 352
2019-04-23 06:00 | 380 | 374
2019-04-23 06:30 | 412 | 409
2019-04-23 07:00 | 457 | 456
2019-04-23 07:30 | 503 | 501
2019-04-23 08:00 | 528 | 527
2019-04-23 08:30 | 541 | 541
2019-04-23 09:00 | 546 | 545
2019-04-23 09:30 | 542 | 540
2019-04-23 10:00 | 545 | 540
2019-04-23 10:30 | 528 | 522
2019-04-23 11:00 | 507 | 506
2019-04-23 11:30 | 513 | 512
2019-04-23 12:00 | 518 | 517
2019-04-23 12:30 | 518 | 515
2019-04-23 13:00 | 515 | 511
2019-04-23 13:30 | 510 | 507
2019-04-23 14:00 | 515 | 513
2019-04-23 14:30 | 510 | 508
2019-04-23 15:00 | 522 | 521
2019-04-23 15:30 | 538 | 536
2019-04-23 16:00 | 548 | 546
2019-04-23 16:30 | 570 | 568
2019-04-23 17:00 | 589 | 587
2019-04-23 17:30 | 596 | 594
2019-04-23 18:00 | 598 | 595
2019-04-23 18:30 | 594 | 589
2019-04-23 19:00 | 581 | 575
2019-04-23 19:30 | 568 | 561
2019-04-23 20:00 | 558 | 552
2019-04-23 20:30 | 538 | 535
2019-04-23 21:00 | 520 | 518
2019-04-23 21:30 | 491 | 488
2019-04-23 22:00 | 470 | 466
2019-04-23 22:30 | 465 | 462
2019-04-23 23:00 | 449 | 445
2019-04-23 23:30 | 424 | 420
2019-04-24 | 400 | 394
2019-04-24 00:30 | 379 | 371
2019-04-24 01:00 | 371 | 361
2019-04-24 01:30 | 355 | 345
2019-04-24 02:00 | 356 | 345
2019-04-24 02:30 | 354 | 343
2019-04-24 03:00 | 349 | 337
2019-04-24 03:30 | 353 | 341
2019-04-24 04:00 | 350 | 339
2019-04-24 04:30 | 344 | 333
2019-04-24 05:00 | 349 | 339
2019-04-24 05:30 | 366 | 358
2019-04-24 06:00 | 386 | 380
2019-04-24 06:30 | 415 | 411
2019-04-24 07:00 | 448 | 446
2019-04-24 07:30 | 473 | 471
2019-04-24 08:00 | 483 | 480
2019-04-24 08:30 | 494 | 491
2019-04-24 09:00 | 484 | 483
2019-04-24 09:30 | 489 | 488
2019-04-24 10:00 | 486 | 485
2019-04-24 10:30 | 467 | 466
2019-04-24 11:00 | 462 | 461
2019-04-24 11:30 | 460 | 458
2019-04-24 12:00 | 458 | 457
2019-04-24 12:30 | 456 | 455
2019-04-24 13:00 | 451 | 450
2019-04-24 13:30 | 459 | 458
2019-04-24 14:00 | 463 | 462
2019-04-24 14:30 | 473 | 472
2019-04-24 15:00 | 498 | 497
2019-04-24 15:30 | 521 | 520
2019-04-24 16:00 | 535 | 533
2019-04-24 16:30 | 550 | 547
2019-04-24 17:00 | 565 | 563
2019-04-24 17:30 | 570 | 568
2019-04-24 18:00 | 586 | 585
2019-04-24 18:30 | 569 | 566
2019-04-24 19:00 | 554 | 552
2019-04-24 19:30 | 541 | 540
2019-04-24 20:00 | 531 | 529
2019-04-24 20:30 | 512 | 512
2019-04-24 21:00 | 498 | 498
2019-04-24 21:30 | 478 | 477
2019-04-24 22:00 | 467 | 466
2019-04-24 22:30 | 456 | 454
2019-04-24 23:00 | 436 | 433
2019-04-24 23:30 | 416 | 413
2019-04-25 | 388 | 383
2019-04-25 00:30 | 369 | 362
2019-04-25 01:00 | 357 | 349
2019-04-25 01:30 | 351 | 342
2019-04-25 02:00 | 344 | 334
2019-04-25 02:30 | 340 | 330
2019-04-25 03:00 | 337 | 328
2019-04-25 03:30 | 332 | 322
2019-04-25 04:00 | 319 | 309
2019-04-25 04:30 | 317 | 307
2019-04-25 05:00 | 317 | 306
2019-04-25 05:30 | 322 | 312
2019-04-25 06:00 | 333 | 324
2019-04-25 06:30 | 346 | 337
2019-04-25 07:00 | 355 | 346
2019-04-25 07:30 | 371 | 363
2019-04-25 08:00 | 373 | 366
2019-04-25 08:30 | 375 | 369
2019-04-25 09:00 | 382 | 377
2019-04-25 09:30 | 385 | 381
2019-04-25 10:00 | 385 | 381
2019-04-25 10:30 | 355 | 351
2019-04-25 11:00 | 350 | 346
2019-04-25 11:30 | 351 | 348
2019-04-25 12:00 | 348 | 345
2019-04-25 12:30 | 350 | 347
2019-04-25 13:00 | 353 | 350
2019-04-25 13:30 | 364 | 362
2019-04-25 14:00 | 377 | 374
2019-04-25 14:30 | 390 | 387
2019-04-25 15:00 | 403 | 401
2019-04-25 15:30 | 406 | 404
2019-04-25 16:00 | 418 | 416
2019-04-25 16:30 | 429 | 428
2019-04-25 17:00 | 460 | 459
2019-04-25 17:30 | 476 | 475
2019-04-25 18:00 | 496 | 494
2019-04-25 18:30 | 508 | 506
2019-04-25 19:00 | 501 | 499
2019-04-25 19:30 | 477 | 474
2019-04-25 20:00 | 461 | 459
2019-04-25 20:30 | 460 | 458
2019-04-25 21:00 | 444 | 442
2019-04-25 21:30 | 429 | 428
2019-04-25 22:00 | 420 | 418
2019-04-25 22:30 | 416 | 413
2019-04-25 23:00 | 406 | 403
2019-04-25 23:30 | 389 | 384
2019-04-26 | 375 | 369
2019-04-26 00:30 | 352 | 345
2019-04-26 01:00 | 340 | 332
2019-04-26 01:30 | 335 | 323
2019-04-26 02:00 | 330 | 317
2019-04-26 02:30 | 313 | 300
2019-04-26 03:00 | 297 | 284
2019-04-26 03:30 | 297 | 283
2019-04-26 04:00 | 289 | 276
2019-04-26 04:30 | 288 | 275
2019-04-26 05:00 | 299 | 288
2019-04-26 05:30 | 319 | 310
2019-04-26 06:00 | 341 | 334
2019-04-26 06:30 | 389 | 385
2019-04-26 07:00 | 430 | 427
2019-04-26 07:30 | 461 | 459
2019-04-26 08:00 | 477 | 476
2019-04-26 08:30 | 475 | 474
2019-04-26 09:00 | 478 | 477
2019-04-26 09:30 | 466 | 465
2019-04-26 10:00 | 465 | 464
2019-04-26 10:30 | 462 | 461
2019-04-26 11:00 | 458 | 457
2019-04-26 11:30 | 465 | 464
2019-04-26 12:00 | 459 | 458
2019-04-26 12:30 | 454 | 453
2019-04-26 13:00 | 460 | 459
2019-04-26 13:30 | 457 | 456
2019-04-26 14:00 | 452 | 451
2019-04-26 14:30 | 469 | 468
2019-04-26 15:00 | 490 | 489
2019-04-26 15:30 | 485 | 484
2019-04-26 16:00 | 517 | 516
2019-04-26 16:30 | 547 | 546
2019-04-26 17:00 | 569 | 568
2019-04-26 17:30 | 574 | 572
2019-04-26 18:00 | 583 | 582
2019-04-26 18:30 | 569 | 567
2019-04-26 19:00 | 562 | 559
2019-04-26 19:30 | 544 | 540
2019-04-26 20:00 | 532 | 529
2019-04-26 20:30 | 514 | 513
2019-04-26 21:00 | 491 | 490
2019-04-26 21:30 | 475 | 474
2019-04-26 22:00 | 464 | 463
2019-04-26 22:30 | 455 | 453
2019-04-26 23:00 | 437 | 436
2019-04-26 23:30 | 417 | 414
2019-04-27 | 398 | 393
2019-04-27 00:30 | 373 | 366
2019-04-27 01:00 | 359 | 351
2019-04-27 01:30 | 353 | 344
2019-04-27 02:00 | 348 | 338
2019-04-27 02:30 | 344 | 334
2019-04-27 03:00 | 340 | 329
2019-04-27 03:30 | 340 | 327
2019-04-27 04:00 | 341 | 328
2019-04-27 04:30 | 340 | 327
2019-04-27 05:00 | 343 | 331
2019-04-27 05:30 | 347 | 336
2019-04-27 06:00 | 350 | 340
2019-04-27 06:30 | 359 | 348
2019-04-27 07:00 | 367 | 358
2019-04-27 07:30 | 382 | 374
2019-04-27 08:00 | 398 | 391
2019-04-27 08:30 | 408 | 402
2019-04-27 09:00 | 412 | 407
2019-04-27 09:30 | 418 | 413
2019-04-27 10:00 | 409 | 406
2019-04-27 10:30 | 414 | 411
2019-04-27 11:00 | 416 | 414
2019-04-27 11:30 | 419 | 418
2019-04-27 12:00 | 423 | 421
2019-04-27 12:30 | 421 | 419
2019-04-27 13:00 | 425 | 424
2019-04-27 13:30 | 435 | 434
2019-04-27 14:00 | 430 | 429
2019-04-27 14:30 | 424 | 423
2019-04-27 15:00 | 431 | 430
2019-04-27 15:30 | 443 | 442
2019-04-27 16:00 | 457 | 456
2019-04-27 16:30 | 479 | 478
2019-04-27 17:00 | 505 | 505
2019-04-27 17:30 | 515 | 514
2019-04-27 18:00 | 528 | 528
2019-04-27 18:30 | 525 | 524
2019-04-27 19:00 | 520 | 518
2019-04-27 19:30 | 500 | 499
2019-04-27 20:00 | 489 | 488
2019-04-27 20:30 | 477 | 476
2019-04-27 21:00 | 455 | 454
2019-04-27 21:30 | 439 | 437
2019-04-27 22:00 | 437 | 435
2019-04-27 22:30 | 442 | 439
2019-04-27 23:00 | 425 | 422
2019-04-27 23:30 | 412 | 409
2019-04-28 | 392 | 386
2019-04-28 00:30 | 367 | 360
2019-04-28 01:00 | 356 | 348
2019-04-28 01:30 | 346 | 336
2019-04-28 02:00 | 343 | 331
2019-04-28 02:30 | 340 | 326
2019-04-28 03:00 | 336 | 322
2019-04-28 03:30 | 331 | 317
2019-04-28 04:00 | 329 | 315
2019-04-28 04:30 | 329 | 315
2019-04-28 05:00 | 326 | 312
2019-04-28 05:30 | 327 | 313
2019-04-28 06:00 | 331 | 318
2019-04-28 06:30 | 340 | 326
2019-04-28 07:00 | 350 | 336
2019-04-28 07:30 | 366 | 354
2019-04-28 08:00 | 387 | 375
2019-04-28 08:30 | 396 | 386
2019-04-28 09:00 | 394 | 385
2019-04-28 09:30 | 387 | 379
2019-04-28 10:00 | 378 | 371
2019-04-28 10:30 | 381 | 375
2019-04-28 11:00 | 380 | 375
2019-04-28 11:30 | 386 | 381
2019-04-28 12:00 | 392 | 387
2019-04-28 12:30 | 396 | 391
2019-04-28 13:00 | 387 | 383
2019-04-28 13:30 | 388 | 384
2019-04-28 14:00 | 402 | 398
2019-04-28 14:30 | 425 | 422
2019-04-28 15:00 | 433 | 431
2019-04-28 15:30 | 440 | 438
2019-04-28 16:00 | 439 | 438
2019-04-28 16:30 | 481 | 479
2019-04-28 17:00 | 506 | 505
2019-04-28 17:30 | 520 | 519
2019-04-28 18:00 | 531 | 530
2019-04-28 18:30 | 550 | 550
2019-04-28 19:00 | 539 | 538
2019-04-28 19:30 | 520 | 519
2019-04-28 20:00 | 519 | 518
2019-04-28 20:30 | 502 | 501
2019-04-28 21:00 | 486 | 484
2019-04-28 21:30 | 476 | 474
2019-04-28 22:00 | 458 | 456
2019-04-28 22:30 | 450 | 446
2019-04-28 23:00 | 439 | 435
2019-04-28 23:30 | 416 | 411
2019-04-29 | 398 | 390
2019-04-29 00:30 | 373 | 363
2019-04-29 01:00 | 357 | 346
2019-04-29 01:30 | 352 | 340
2019-04-29 02:00 | 355 | 343
2019-04-29 02:30 | 346 | 333
2019-04-29 03:00 | 332 | 319
2019-04-29 03:30 | 333 | 321
2019-04-29 04:00 | 342 | 329
2019-04-29 04:30 | 343 | 331
2019-04-29 05:00 | 347 | 337
2019-04-29 05:30 | 360 | 353
2019-04-29 06:00 | 380 | 375
2019-04-29 06:30 | 422 | 419
2019-04-29 07:00 | 466 | 464
2019-04-29 07:30 | 501 | 500
2019-04-29 08:00 | 520 | 517
2019-04-29 08:30 | 527 | 525
2019-04-29 09:00 | 517 | 514
2019-04-29 09:30 | 523 | 521
2019-04-29 10:00 | 529 | 527
2019-04-29 10:30 | 511 | 508
2019-04-29 11:00 | 507 | 505
2019-04-29 11:30 | 500 | 498
2019-04-29 12:00 | 496 | 493
2019-04-29 12:30 | 486 | 484
2019-04-29 13:00 | 486 | 484
2019-04-29 13:30 | 491 | 489
2019-04-29 14:00 | 500 | 498
2019-04-29 14:30 | 515 | 513
2019-04-29 15:00 | 527 | 525
2019-04-29 15:30 | 536 | 534
2019-04-29 16:00 | 553 | 551
2019-04-29 16:30 | 578 | 575
2019-04-29 17:00 | 591 | 588
2019-04-29 17:30 | 594 | 592
2019-04-29 18:00 | 607 | 605
2019-04-29 18:30 | 594 | 591
2019-04-29 19:00 | 588 | 584
2019-04-29 19:30 | 574 | 571
2019-04-29 20:00 | 560 | 557
2019-04-29 20:30 | 554 | 551
2019-04-29 21:00 | 536 | 531
2019-04-29 21:30 | 506 | 505
2019-04-29 22:00 | 493 | 492
2019-04-29 22:30 | 485 | 483
2019-04-29 23:00 | 466 | 463
2019-04-29 23:30 | 441 | 437
2019-04-30 | 413 | 407
2019-04-30 00:30 | 386 | 377
2019-04-30 01:00 | 378 | 368
2019-04-30 01:30 | 365 | 354
2019-04-30 02:00 | 358 | 344
2019-04-30 02:30 | 362 | 348
2019-04-30 03:00 | 362 | 348
2019-04-30 03:30 | 357 | 343
2019-04-30 04:00 | 356 | 343
2019-04-30 04:30 | 361 | 349
2019-04-30 05:00 | 374 | 362
2019-04-30 05:30 | 389 | 380
2019-04-30 06:00 | 406 | 400
2019-04-30 06:30 | 446 | 443
2019-04-30 07:00 | 482 | 481
2019-04-30 07:30 | 514 | 512
2019-04-30 08:00 | 523 | 522
2019-04-30 08:30 | 511 | 510
2019-04-30 09:00 | 500 | 499
2019-04-30 09:30 | 495 | 495
2019-04-30 10:00 | 488 | 487
2019-04-30 10:30 | 505 | 503
2019-04-30 11:00 | 522 | 521
2019-04-30 11:30 | 523 | 522
2019-04-30 12:00 | 527 | 525
2019-04-30 12:30 | 527 | 526
2019-04-30 13:00 | 517 | 516
2019-04-30 13:30 | 523 | 522
2019-04-30 14:00 | 528 | 527
2019-04-30 14:30 | 538 | 536
2019-04-30 15:00 | 545 | 543
2019-04-30 15:30 | 546 | 544
2019-04-30 16:00 | 556 | 554
2019-04-30 16:30 | 582 | 580
2019-04-30 17:00 | 604 | 601
2019-04-30 17:30 | 619 | 616
2019-04-30 18:00 | 610 | 607
2019-04-30 18:30 | 602 | 598
2019-04-30 19:00 | 597 | 593
2019-04-30 19:30 | 574 | 570
2019-04-30 20:00 | 569 | 566
2019-04-30 20:30 | 568 | 564
2019-04-30 21:00 | 543 | 538
2019-04-30 21:30 | 525 | 522
2019-04-30 22:00 | 508 | 506
2019-04-30 22:30 | 493 | 491
2019-04-30 23:00 | 474 | 472
2019-04-30 23:30 | 450 | 447
2019-05-01 | 426 | 421
2019-05-01 00:30 | 393 | 385
2019-05-01 01:00 | 382 | 372
2019-05-01 01:30 | 379 | 368
2019-05-01 02:00 | 371 | 359
2019-05-01 02:30 | 360 | 348
2019-05-01 03:00 | 355 | 342
2019-05-01 03:30 | 353 | 341
2019-05-01 04:00 | 351 | 339
2019-05-01 04:30 | 363 | 351
2019-05-01 05:00 | 373 | 362
2019-05-01 05:30 | 387 | 379
2019-05-01 06:00 | 411 | 406
2019-05-01 06:30 | 468 | 465
2019-05-01 07:00 | 514 | 510
2019-05-01 07:30 | 541 | 537
2019-05-01 08:00 | 552 | 550
2019-05-01 08:30 | 549 | 548
2019-05-01 09:00 | 558 | 556
2019-05-01 09:30 | 551 | 549
2019-05-01 10:00 | 550 | 548
2019-05-01 10:30 | 537 | 535
2019-05-01 11:00 | 533 | 532
2019-05-01 11:30 | 527 | 526
2019-05-01 12:00 | 522 | 521
2019-05-01 12:30 | 531 | 530
2019-05-01 13:00 | 531 | 530
2019-05-01 13:30 | 515 | 513
2019-05-01 14:00 | 528 | 526
2019-05-01 14:30 | 540 | 540
2019-05-01 15:00 | 543 | 542
2019-05-01 15:30 | 559 | 558
2019-05-01 16:00 | 571 | 570
2019-05-01 16:30 | 585 | 585
2019-05-01 17:00 | 592 | 592
2019-05-01 17:30 | 615 | 614
2019-05-01 18:00 | 632 | 632
2019-05-01 18:30 | 620 | 618
2019-05-01 19:00 | 610 | 607
2019-05-01 19:30 | 599 | 595
2019-05-01 20:00 | 594 | 588
2019-05-01 20:30 | 583 | 577
2019-05-01 21:00 | 553 | 549
2019-05-01 21:30 | 535 | 530
2019-05-01 22:00 | 513 | 511
2019-05-01 22:30 | 496 | 493
2019-05-01 23:00 | 478 | 476
2019-05-01 23:30 | 453 | 450
2019-05-02 | 430 | 425
2019-05-02 00:30 | 405 | 399
2019-05-02 01:00 | 382 | 373
2019-05-02 01:30 | 372 | 362
2019-05-02 02:00 | 371 | 360
2019-05-02 02:30 | 370 | 360
2019-05-02 03:00 | 360 | 350
2019-05-02 03:30 | 366 | 355
2019-05-02 04:00 | 372 | 361
2019-05-02 04:30 | 374 | 364
2019-05-02 05:00 | 377 | 368
2019-05-02 05:30 | 383 | 377
2019-05-02 06:00 | 398 | 394
2019-05-02 06:30 | 446 | 443
2019-05-02 07:00 | 492 | 491
2019-05-02 07:30 | 526 | 523
2019-05-02 08:00 | 532 | 525
2019-05-02 08:30 | 547 | 538
2019-05-02 09:00 | 541 | 534
2019-05-02 09:30 | 539 | 533
2019-05-02 10:00 | 538 | 533
2019-05-02 10:30 | 530 | 525
2019-05-02 11:00 | 544 | 540
2019-05-02 11:30 | 547 | 542
2019-05-02 12:00 | 535 | 529
2019-05-02 12:30 | 546 | 541
2019-05-02 13:00 | 555 | 550
2019-05-02 13:30 | 554 | 549
2019-05-02 14:00 | 552 | 547
2019-05-02 14:30 | 553 | 548
2019-05-02 15:00 | 552 | 546
2019-05-02 15:30 | 565 | 560
2019-05-02 16:00 | 578 | 573
2019-05-02 16:30 | 585 | 579
2019-05-02 17:00 | 603 | 598
2019-05-02 17:30 | 610 | 606
2019-05-02 18:00 | 619 | 615
2019-05-02 18:30 | 618 | 613
2019-05-02 19:00 | 611 | 605
2019-05-02 19:30 | 599 | 592
2019-05-02 20:00 | 587 | 578
2019-05-02 20:30 | 573 | 570
2019-05-02 21:00 | 558 | 558
2019-05-02 21:30 | 529 | 528
2019-05-02 22:00 | 505 | 504
2019-05-02 22:30 | 495 | 493
2019-05-02 23:00 | 482 | 480
2019-05-02 23:30 | 457 | 454
2019-05-03 | 431 | 426
2019-05-03 00:30 | 404 | 397
2019-05-03 01:00 | 393 | 384
2019-05-03 01:30 | 376 | 366
2019-05-03 02:00 | 367 | 355
2019-05-03 02:30 | 367 | 355
2019-05-03 03:00 | 364 | 352
2019-05-03 03:30 | 361 | 349
2019-05-03 04:00 | 356 | 343
2019-05-03 04:30 | 358 | 347
2019-05-03 05:00 | 359 | 349
2019-05-03 05:30 | 371 | 364
2019-05-03 06:00 | 394 | 389
2019-05-03 06:30 | 440 | 437
2019-05-03 07:00 | 486 | 485
2019-05-03 07:30 | 527 | 526
2019-05-03 08:00 | 549 | 546
2019-05-03 08:30 | 565 | 557
2019-05-03 09:00 | 563 | 555
2019-05-03 09:30 | 557 | 550
2019-05-03 10:00 | 544 | 537
2019-05-03 10:30 | 565 | 560
2019-05-03 11:00 | 565 | 561
2019-05-03 11:30 | 562 | 557
2019-05-03 12:00 | 573 | 568
2019-05-03 12:30 | 575 | 570
2019-05-03 13:00 | 568 | 563
2019-05-03 13:30 | 568 | 563
2019-05-03 14:00 | 554 | 548
2019-05-03 14:30 | 560 | 554
2019-05-03 15:00 | 575 | 570
2019-05-03 15:30 | 580 | 575
2019-05-03 16:00 | 586 | 581
2019-05-03 16:30 | 592 | 587
2019-05-03 17:00 | 604 | 599
2019-05-03 17:30 | 611 | 606
2019-05-03 18:00 | 607 | 603
2019-05-03 18:30 | 594 | 588
2019-05-03 19:00 | 585 | 578
2019-05-03 19:30 | 574 | 567
2019-05-03 20:00 | 568 | 565
2019-05-03 20:30 | 564 | 562
2019-05-03 21:00 | 547 | 545
2019-05-03 21:30 | 519 | 516
2019-05-03 22:00 | 508 | 505
2019-05-03 22:30 | 504 | 501
2019-05-03 23:00 | 494 | 490
2019-05-03 23:30 | 464 | 459
2019-05-04 | 432 | 425
2019-05-04 00:30 | 401 | 391
2019-05-04 01:00 | 378 | 367
2019-05-04 01:30 | 367 | 354
2019-05-04 02:00 | 358 | 345
2019-05-04 02:30 | 363 | 350
2019-05-04 03:00 | 363 | 350
2019-05-04 03:30 | 358 | 345
2019-05-04 04:00 | 361 | 348
2019-05-04 04:30 | 352 | 339
2019-05-04 05:00 | 343 | 331
2019-05-04 05:30 | 347 | 336
2019-05-04 06:00 | 350 | 340
2019-05-04 06:30 | 360 | 351
2019-05-04 07:00 | 374 | 365
2019-05-04 07:30 | 404 | 397
2019-05-04 08:00 | 430 | 425
2019-05-04 08:30 | 457 | 454
2019-05-04 09:00 | 476 | 473
2019-05-04 09:30 | 481 | 479
2019-05-04 10:00 | 493 | 491
2019-05-04 10:30 | 490 | 487
2019-05-04 11:00 | 475 | 473
2019-05-04 11:30 | 464 | 462
2019-05-04 12:00 | 441 | 439
2019-05-04 12:30 | 461 | 458
2019-05-04 13:00 | 460 | 457
2019-05-04 13:30 | 464 | 461
2019-05-04 14:00 | 468 | 466
2019-05-04 14:30 | 475 | 473
2019-05-04 15:00 | 469 | 466
2019-05-04 15:30 | 449 | 446
2019-05-04 16:00 | 443 | 439
2019-05-04 16:30 | 461 | 457
2019-05-04 17:00 | 481 | 477
2019-05-04 17:30 | 489 | 487
2019-05-04 18:00 | 514 | 512
2019-05-04 18:30 | 513 | 511
2019-05-04 19:00 | 510 | 507
2019-05-04 19:30 | 492 | 489
2019-05-04 20:00 | 484 | 481
2019-05-04 20:30 | 483 | 479
2019-05-04 21:00 | 466 | 462
2019-05-04 21:30 | 453 | 448
2019-05-04 22:00 | 448 | 443
2019-05-04 22:30 | 443 | 438
2019-05-04 23:00 | 434 | 428
2019-05-04 23:30 | 422 | 414
2019-05-05 | 398 | 388
2019-05-05 00:30 | 369 | 358
2019-05-05 01:00 | 350 | 337
2019-05-05 01:30 | 342 | 329
2019-05-05 02:00 | 340 | 326
2019-05-05 02:30 | 334 | 320
2019-05-05 03:00 | 326 | 310
2019-05-05 03:30 | 322 | 307
2019-05-05 04:00 | 308 | 295
2019-05-05 04:30 | 305 | 291
2019-05-05 05:00 | 307 | 294
2019-05-05 05:30 | 315 | 302
2019-05-05 06:00 | 324 | 312
2019-05-05 06:30 | 337 | 325
2019-05-05 07:00 | 350 | 338
2019-05-05 07:30 | 365 | 354
2019-05-05 08:00 | 362 | 351
2019-05-05 08:30 | 360 | 350
2019-05-05 09:00 | 353 | 344
2019-05-05 09:30 | 352 | 343
2019-05-05 10:00 | 352 | 344
2019-05-05 10:30 | 343 | 335
2019-05-05 11:00 | 333 | 324
2019-05-05 11:30 | 320 | 310
2019-05-05 12:00 | 312 | 300
2019-05-05 12:30 | 307 | 296
2019-05-05 13:00 | 307 | 296
2019-05-05 13:30 | 325 | 314
2019-05-05 14:00 | 337 | 328
2019-05-05 14:30 | 356 | 348
2019-05-05 15:00 | 380 | 374
2019-05-05 15:30 | 408 | 403
2019-05-05 16:00 | 423 | 419
2019-05-05 16:30 | 444 | 440
2019-05-05 17:00 | 467 | 464
2019-05-05 17:30 | 476 | 474
2019-05-05 18:00 | 490 | 488
2019-05-05 18:30 | 488 | 485
2019-05-05 19:00 | 483 | 480
2019-05-05 19:30 | 477 | 474
2019-05-05 20:00 | 473 | 471
2019-05-05 20:30 | 470 | 468
2019-05-05 21:00 | 452 | 448
2019-05-05 21:30 | 429 | 424
2019-05-05 22:00 | 416 | 411
2019-05-05 22:30 | 409 | 404
2019-05-05 23:00 | 402 | 395
2019-05-05 23:30 | 381 | 373
2019-05-06 | 354 | 344
2019-05-06 00:30 | 333 | 321
2019-05-06 01:00 | 320 | 306
2019-05-06 01:30 | 312 | 297
2019-05-06 02:00 | 311 | 292
2019-05-06 02:30 | 307 | 282
2019-05-06 03:00 | 303 | 278
2019-05-06 03:30 | 297 | 272
2019-05-06 04:00 | 296 | 270
2019-05-06 04:30 | 297 | 272
2019-05-06 05:00 | 298 | 272
2019-05-06 05:30 | 301 | 278
2019-05-06 06:00 | 305 | 284
2019-05-06 06:30 | 332 | 311
2019-05-06 07:00 | 363 | 343
2019-05-06 07:30 | 378 | 360
2019-05-06 08:00 | 378 | 360
2019-05-06 08:30 | 367 | 351
2019-05-06 09:00 | 364 | 348
2019-05-06 09:30 | 366 | 350
2019-05-06 10:00 | 359 | 344
2019-05-06 10:30 | 346 | 330
2019-05-06 11:00 | 336 | 320
2019-05-06 11:30 | 326 | 310
2019-05-06 12:00 | 325 | 309
2019-05-06 12:30 | 324 | 308
2019-05-06 13:00 | 327 | 312
2019-05-06 13:30 | 334 | 321
2019-05-06 14:00 | 349 | 336
2019-05-06 14:30 | 375 | 364
2019-05-06 15:00 | 390 | 380
2019-05-06 15:30 | 415 | 406
2019-05-06 16:00 | 449 | 442
2019-05-06 16:30 | 484 | 477
2019-05-06 17:00 | 521 | 513
2019-05-06 17:30 | 541 | 534
2019-05-06 18:00 | 555 | 550
2019-05-06 18:30 | 540 | 535
2019-05-06 19:00 | 535 | 529
2019-05-06 19:30 | 514 | 507
2019-05-06 20:00 | 502 | 495
2019-05-06 20:30 | 501 | 494
2019-05-06 21:00 | 481 | 476
2019-05-06 21:30 | 465 | 459
2019-05-06 22:00 | 436 | 429
2019-05-06 22:30 | 429 | 421
2019-05-06 23:00 | 420 | 412
2019-05-06 23:30 | 405 | 395
2019-05-07 | 384 | 372
2019-05-07 00:30 | 363 | 349
2019-05-07 01:00 | 356 | 341
2019-05-07 01:30 | 352 | 335
2019-05-07 02:00 | 348 | 331
2019-05-07 02:30 | 343 | 325
2019-05-07 03:00 | 329 | 311
2019-05-07 03:30 | 319 | 301
2019-05-07 04:00 | 314 | 297
2019-05-07 04:30 | 315 | 299
2019-05-07 05:00 | 311 | 297
2019-05-07 05:30 | 327 | 316
2019-05-07 06:00 | 353 | 345
2019-05-07 06:30 | 414 | 409
2019-05-07 07:00 | 475 | 471
2019-05-07 07:30 | 516 | 512
2019-05-07 08:00 | 519 | 508
2019-05-07 08:30 | 486 | 476
2019-05-07 09:00 | 446 | 441
2019-05-07 09:30 | 436 | 434
2019-05-07 10:00 | 452 | 451
2019-05-07 10:30 | 447 | 446
2019-05-07 11:00 | 440 | 439
2019-05-07 11:30 | 439 | 438
2019-05-07 12:00 | 442 | 440
2019-05-07 12:30 | 438 | 436
2019-05-07 13:00 | 439 | 437
2019-05-07 13:30 | 438 | 436
2019-05-07 14:00 | 452 | 451
2019-05-07 14:30 | 462 | 461
2019-05-07 15:00 | 465 | 463
2019-05-07 15:30 | 453 | 452
2019-05-07 16:00 | 473 | 472
2019-05-07 16:30 | 494 | 492
2019-05-07 17:00 | 507 | 506
2019-05-07 17:30 | 526 | 524
2019-05-07 18:00 | 547 | 546
2019-05-07 18:30 | 544 | 541
2019-05-07 19:00 | 531 | 528
2019-05-07 19:30 | 521 | 519
2019-05-07 20:00 | 517 | 516
2019-05-07 20:30 | 503 | 502
2019-05-07 21:00 | 479 | 478
2019-05-07 21:30 | 467 | 466
2019-05-07 22:00 | 454 | 452
2019-05-07 22:30 | 449 | 446
2019-05-07 23:00 | 433 | 430
2019-05-07 23:30 | 390 | 386
2019-05-08 | 354 | 346
2019-05-08 00:30 | 326 | 315
2019-05-08 01:00 | 314 | 302
2019-05-08 01:30 | 317 | 303
2019-05-08 02:00 | 319 | 304
2019-05-08 02:30 | 316 | 301
2019-05-08 03:00 | 305 | 290
2019-05-08 03:30 | 303 | 288
2019-05-08 04:00 | 294 | 279
2019-05-08 04:30 | 302 | 288
2019-05-08 05:00 | 314 | 302
2019-05-08 05:30 | 326 | 316
2019-05-08 06:00 | 343 | 336
2019-05-08 06:30 | 401 | 396
2019-05-08 07:00 | 453 | 450
2019-05-08 07:30 | 484 | 482
2019-05-08 08:00 | 485 | 483
2019-05-08 08:30 | 454 | 453
2019-05-08 09:00 | 434 | 433
2019-05-08 09:30 | 438 | 437
2019-05-08 10:00 | 430 | 430
2019-05-08 10:30 | 432 | 431
2019-05-08 11:00 | 417 | 417
2019-05-08 11:30 | 418 | 416
2019-05-08 12:00 | 408 | 407
2019-05-08 12:30 | 405 | 404
2019-05-08 13:00 | 412 | 411
2019-05-08 13:30 | 418 | 417
2019-05-08 14:00 | 427 | 426
2019-05-08 14:30 | 453 | 452
2019-05-08 15:00 | 469 | 469
2019-05-08 15:30 | 484 | 483
2019-05-08 16:00 | 511 | 510
2019-05-08 16:30 | 548 | 545
2019-05-08 17:00 | 572 | 568
2019-05-08 17:30 | 568 | 565
2019-05-08 18:00 | 572 | 570
2019-05-08 18:30 | 565 | 560
2019-05-08 19:00 | 546 | 541
2019-05-08 19:30 | 517 | 514
2019-05-08 20:00 | 499 | 498
2019-05-08 20:30 | 496 | 495
2019-05-08 21:00 | 475 | 473
2019-05-08 21:30 | 453 | 449
2019-05-08 22:00 | 436 | 431
2019-05-08 22:30 | 434 | 427
2019-05-08 23:00 | 426 | 419
2019-05-08 23:30 | 405 | 397
2019-05-09 | 387 | 379
2019-05-09 00:30 | 365 | 354
2019-05-09 01:00 | 344 | 331
2019-05-09 01:30 | 333 | 319
2019-05-09 02:00 | 326 | 311
2019-05-09 02:30 | 325 | 310
2019-05-09 03:00 | 324 | 309
2019-05-09 03:30 | 327 | 312
2019-05-09 04:00 | 325 | 310
2019-05-09 04:30 | 322 | 308
2019-05-09 05:00 | 324 | 311
2019-05-09 05:30 | 340 | 329
2019-05-09 06:00 | 368 | 360
2019-05-09 06:30 | 417 | 412
2019-05-09 07:00 | 467 | 464
2019-05-09 07:30 | 479 | 476
2019-05-09 08:00 | 469 | 467
2019-05-09 08:30 | 456 | 453
2019-05-09 09:00 | 418 | 415
2019-05-09 09:30 | 390 | 388
2019-05-09 10:00 | 383 | 381
2019-05-09 10:30 | 376 | 374
2019-05-09 11:00 | 364 | 362
2019-05-09 11:30 | 362 | 361
2019-05-09 12:00 | 378 | 377
2019-05-09 12:30 | 380 | 380
2019-05-09 13:00 | 384 | 384
2019-05-09 13:30 | 395 | 395
2019-05-09 14:00 | 406 | 405
2019-05-09 14:30 | 430 | 428
2019-05-09 15:00 | 431 | 429
2019-05-09 15:30 | 451 | 450
2019-05-09 16:00 | 468 | 466
2019-05-09 16:30 | 490 | 488
2019-05-09 17:00 | 507 | 504
2019-05-09 17:30 | 517 | 514
2019-05-09 18:00 | 539 | 536
2019-05-09 18:30 | 541 | 535
2019-05-09 19:00 | 534 | 528
2019-05-09 19:30 | 521 | 515
2019-05-09 20:00 | 514 | 509
2019-05-09 20:30 | 510 | 506
2019-05-09 21:00 | 500 | 497
2019-05-09 21:30 | 475 | 471
2019-05-09 22:00 | 451 | 447
2019-05-09 22:30 | 445 | 440
2019-05-09 23:00 | 445 | 439
2019-05-09 23:30 | 425 | 418
2019-05-10 | 391 | 382
2019-05-10 00:30 | 357 | 345
2019-05-10 01:00 | 325 | 310
2019-05-10 01:30 | 315 | 299
2019-05-10 02:00 | 299 | 284
2019-05-10 02:30 | 289 | 273
2019-05-10 03:00 | 300 | 284
2019-05-10 03:30 | 300 | 284
2019-05-10 04:00 | 298 | 283
2019-05-10 04:30 | 310 | 295
2019-05-10 05:00 | 328 | 314
2019-05-10 05:30 | 335 | 324
2019-05-10 06:00 | 358 | 350
2019-05-10 06:30 | 417 | 412
2019-05-10 07:00 | 471 | 464
2019-05-10 07:30 | 504 | 495
2019-05-10 08:00 | 510 | 502
2019-05-10 08:30 | 504 | 496
2019-05-10 09:00 | 499 | 490
2019-05-10 09:30 | 498 | 488
2019-05-10 10:00 | 494 | 485
2019-05-10 10:30 | 501 | 492
2019-05-10 11:00 | 491 | 482
2019-05-10 11:30 | 486 | 477
2019-05-10 12:00 | 481 | 472
2019-05-10 12:30 | 472 | 462
2019-05-10 13:00 | 480 | 472
2019-05-10 13:30 | 506 | 500
2019-05-10 14:00 | 505 | 500
2019-05-10 14:30 | 499 | 491
2019-05-10 15:00 | 517 | 509
2019-05-10 15:30 | 526 | 519
2019-05-10 16:00 | 530 | 522
2019-05-10 16:30 | 545 | 537
2019-05-10 17:00 | 557 | 550
2019-05-10 17:30 | 558 | 551
2019-05-10 18:00 | 567 | 560
2019-05-10 18:30 | 555 | 545
2019-05-10 19:00 | 550 | 539
2019-05-10 19:30 | 533 | 521
2019-05-10 20:00 | 525 | 513
2019-05-10 20:30 | 513 | 502
2019-05-10 21:00 | 482 | 476
2019-05-10 21:30 | 459 | 456
2019-05-10 22:00 | 457 | 453
2019-05-10 22:30 | 459 | 455
2019-05-10 23:00 | 467 | 462
2019-05-10 23:30 | 449 | 442
2019-05-11 | 413 | 404
2019-05-11 00:30 | 380 | 367
2019-05-11 01:00 | 358 | 342
2019-05-11 01:30 | 335 | 316
2019-05-11 02:00 | 324 | 304
2019-05-11 02:30 | 322 | 301
2019-05-11 03:00 | 320 | 298
2019-05-11 03:30 | 324 | 299
2019-05-11 04:00 | 322 | 296
2019-05-11 04:30 | 311 | 284
2019-05-11 05:00 | 318 | 291
2019-05-11 05:30 | 334 | 310
2019-05-11 06:00 | 348 | 327
2019-05-11 06:30 | 363 | 343
2019-05-11 07:00 | 388 | 370
2019-05-11 07:30 | 426 | 410
2019-05-11 08:00 | 450 | 435
2019-05-11 08:30 | 454 | 440
2019-05-11 09:00 | 438 | 424
2019-05-11 09:30 | 413 | 399
2019-05-11 10:00 | 411 | 396
2019-05-11 10:30 | 405 | 391
2019-05-11 11:00 | 383 | 367
2019-05-11 11:30 | 372 | 355
2019-05-11 12:00 | 367 | 351
2019-05-11 12:30 | 363 | 346
2019-05-11 13:00 | 361 | 344
2019-05-11 13:30 | 361 | 347
2019-05-11 14:00 | 366 | 352
2019-05-11 14:30 | 378 | 365
2019-05-11 15:00 | 404 | 393
2019-05-11 15:30 | 424 | 414
2019-05-11 16:00 | 440 | 431
2019-05-11 16:30 | 465 | 458
2019-05-11 17:00 | 496 | 490
2019-05-11 17:30 | 500 | 496
2019-05-11 18:00 | 515 | 510
2019-05-11 18:30 | 519 | 513
2019-05-11 19:00 | 512 | 506
2019-05-11 19:30 | 502 | 496
2019-05-11 20:00 | 496 | 492
2019-05-11 20:30 | 500 | 495
2019-05-11 21:00 | 488 | 483
2019-05-11 21:30 | 473 | 467
2019-05-11 22:00 | 472 | 465
2019-05-11 22:30 | 468 | 460
2019-05-11 23:00 | 465 | 457
2019-05-11 23:30 | 447 | 437
2019-05-12 | 426 | 414
2019-05-12 00:30 | 391 | 376
2019-05-12 01:00 | 362 | 346
2019-05-12 01:30 | 346 | 328
2019-05-12 02:00 | 335 | 315
2019-05-12 02:30 | 323 | 302
2019-05-12 03:00 | 331 | 309
2019-05-12 03:30 | 332 | 310
2019-05-12 04:00 | 331 | 309
2019-05-12 04:30 | 331 | 309
2019-05-12 05:00 | 332 | 310
2019-05-12 05:30 | 336 | 316
2019-05-12 06:00 | 339 | 320
2019-05-12 06:30 | 354 | 335
2019-05-12 07:00 | 382 | 364
2019-05-12 07:30 | 424 | 408
2019-05-12 08:00 | 448 | 433
2019-05-12 08:30 | 463 | 451
2019-05-12 09:00 | 458 | 445
2019-05-12 09:30 | 445 | 431
2019-05-12 10:00 | 419 | 405
2019-05-12 10:30 | 410 | 397
2019-05-12 11:00 | 386 | 371
2019-05-12 11:30 | 372 | 357
2019-05-12 12:00 | 372 | 358
2019-05-12 12:30 | 378 | 363
2019-05-12 13:00 | 376 | 362
2019-05-12 13:30 | 393 | 380
2019-05-12 14:00 | 387 | 375
2019-05-12 14:30 | 380 | 367
2019-05-12 15:00 | 392 | 381
2019-05-12 15:30 | 411 | 401
2019-05-12 16:00 | 426 | 417
2019-05-12 16:30 | 460 | 452
2019-05-12 17:00 | 499 | 493
2019-05-12 17:30 | 512 | 508
2019-05-12 18:00 | 520 | 514
2019-05-12 18:30 | 518 | 512
2019-05-12 19:00 | 518 | 511
2019-05-12 19:30 | 514 | 507
2019-05-12 20:00 | 516 | 507
2019-05-12 20:30 | 514 | 506
2019-05-12 21:00 | 502 | 493
2019-05-12 21:30 | 491 | 480
2019-05-12 22:00 | 480 | 469
2019-05-12 22:30 | 454 | 446
2019-05-12 23:00 | 433 | 424
2019-05-12 23:30 | 410 | 400
2019-05-13 | 404 | 392
2019-05-13 00:30 | 368 | 353
2019-05-13 01:00 | 344 | 329
2019-05-13 01:30 | 327 | 310
2019-05-13 02:00 | 320 | 302
2019-05-13 02:30 | 317 | 298
2019-05-13 03:00 | 308 | 288
2019-05-13 03:30 | 308 | 288
2019-05-13 04:00 | 310 | 291
2019-05-13 04:30 | 319 | 302
2019-05-13 05:00 | 332 | 316
2019-05-13 05:30 | 342 | 330
2019-05-13 06:00 | 362 | 354
2019-05-13 06:30 | 410 | 405
2019-05-13 07:00 | 483 | 479
2019-05-13 07:30 | 528 | 524
2019-05-13 08:00 | 557 | 553
2019-05-13 08:30 | 561 | 556
2019-05-13 09:00 | 555 | 551
2019-05-13 09:30 | 538 | 534
2019-05-13 10:00 | 503 | 499
2019-05-13 10:30 | 488 | 484
2019-05-13 11:00 | 470 | 467
2019-05-13 11:30 | 453 | 449
2019-05-13 12:00 | 441 | 439
2019-05-13 12:30 | 438 | 436
2019-05-13 13:00 | 459 | 456
2019-05-13 13:30 | 486 | 481
2019-05-13 14:00 | 491 | 487
2019-05-13 14:30 | 495 | 491
2019-05-13 15:00 | 499 | 494
2019-05-13 15:30 | 518 | 512
2019-05-13 16:00 | 541 | 535
2019-05-13 16:30 | 563 | 556
2019-05-13 17:00 | 587 | 582
2019-05-13 17:30 | 607 | 602
2019-05-13 18:00 | 623 | 618
2019-05-13 18:30 | 612 | 606
2019-05-13 19:00 | 606 | 599
2019-05-13 19:30 | 590 | 581
2019-05-13 20:00 | 579 | 572
2019-05-13 20:30 | 574 | 566
2019-05-13 21:00 | 546 | 541
2019-05-13 21:30 | 523 | 517
2019-05-13 22:00 | 503 | 498
2019-05-13 22:30 | 485 | 480
2019-05-13 23:00 | 470 | 464
2019-05-13 23:30 | 456 | 448
2019-05-14 | 436 | 426
2019-05-14 00:30 | 387 | 375
2019-05-14 01:00 | 365 | 351
2019-05-14 01:30 | 354 | 338
2019-05-14 02:00 | 348 | 331
2019-05-14 02:30 | 342 | 324
2019-05-14 03:00 | 339 | 321
2019-05-14 03:30 | 342 | 324
2019-05-14 04:00 | 347 | 328
2019-05-14 04:30 | 348 | 332
2019-05-14 05:00 | 351 | 336
2019-05-14 05:30 | 369 | 357
2019-05-14 06:00 | 402 | 394
2019-05-14 06:30 | 460 | 455
2019-05-14 07:00 | 507 | 503
2019-05-14 07:30 | 540 | 537
2019-05-14 08:00 | 554 | 550
2019-05-14 08:30 | 548 | 545
2019-05-14 09:00 | 521 | 517
2019-05-14 09:30 | 499 | 495
2019-05-14 10:00 | 494 | 490
2019-05-14 10:30 | 468 | 464
2019-05-14 11:00 | 437 | 435
2019-05-14 11:30 | 428 | 426
2019-05-14 12:00 | 426 | 425
2019-05-14 12:30 | 432 | 430
2019-05-14 13:00 | 445 | 444
2019-05-14 13:30 | 451 | 450
2019-05-14 14:00 | 481 | 480
2019-05-14 14:30 | 503 | 502
2019-05-14 15:00 | 510 | 508
2019-05-14 15:30 | 505 | 503
2019-05-14 16:00 | 526 | 524
2019-05-14 16:30 | 558 | 555
2019-05-14 17:00 | 587 | 583
2019-05-14 17:30 | 621 | 617
2019-05-14 18:00 | 643 | 639
2019-05-14 18:30 | 632 | 627
2019-05-14 19:00 | 627 | 622
2019-05-14 19:30 | 609 | 604
2019-05-14 20:00 | 591 | 585
2019-05-14 20:30 | 584 | 577
2019-05-14 21:00 | 559 | 552
2019-05-14 21:30 | 533 | 527
2019-05-14 22:00 | 517 | 512
2019-05-14 22:30 | 505 | 500
2019-05-14 23:00 | 486 | 480
2019-05-14 23:30 | 464 | 456
2019-05-15 | 429 | 418
2019-05-15 00:30 | 392 | 378
2019-05-15 01:00 | 376 | 359
2019-05-15 01:30 | 365 | 347
2019-05-15 02:00 | 356 | 337
2019-05-15 02:30 | 347 | 328
2019-05-15 03:00 | 346 | 327
2019-05-15 03:30 | 347 | 328
2019-05-15 04:00 | 343 | 324
2019-05-15 04:30 | 341 | 323
2019-05-15 05:00 | 348 | 331
2019-05-15 05:30 | 364 | 351
2019-05-15 06:00 | 390 | 383
2019-05-15 06:30 | 460 | 453
2019-05-15 07:00 | 517 | 511
2019-05-15 07:30 | 545 | 541
2019-05-15 08:00 | 551 | 547
2019-05-15 08:30 | 541 | 538
2019-05-15 09:00 | 526 | 523
2019-05-15 09:30 | 510 | 507
2019-05-15 10:00 | 501 | 498
2019-05-15 10:30 | 498 | 495
2019-05-15 11:00 | 486 | 483
2019-05-15 11:30 | 482 | 480
2019-05-15 12:00 | 492 | 490
2019-05-15 12:30 | 505 | 503
2019-05-15 13:00 | 510 | 508
2019-05-15 13:30 | 498 | 496
2019-05-15 14:00 | 496 | 494
2019-05-15 14:30 | 510 | 509
2019-05-15 15:00 | 511 | 509
2019-05-15 15:30 | 524 | 522
2019-05-15 16:00 | 553 | 551
2019-05-15 16:30 | 585 | 582
2019-05-15 17:00 | 611 | 608
2019-05-15 17:30 | 639 | 637
2019-05-15 18:00 | 662 | 659
2019-05-15 18:30 | 653 | 649
2019-05-15 19:00 | 642 | 637
2019-05-15 19:30 | 624 | 619
2019-05-15 20:00 | 613 | 609
2019-05-15 20:30 | 594 | 589
2019-05-15 21:00 | 577 | 571
2019-05-15 21:30 | 553 | 549
2019-05-15 22:00 | 536 | 533
2019-05-15 22:30 | 517 | 514
2019-05-15 23:00 | 503 | 499
2019-05-15 23:30 | 483 | 478
2019-05-16 | 454 | 446
2019-05-16 00:30 | 410 | 400
2019-05-16 01:00 | 390 | 378
2019-05-16 01:30 | 383 | 369
2019-05-16 02:00 | 382 | 366
2019-05-16 02:30 | 375 | 359
2019-05-16 03:00 | 370 | 353
2019-05-16 03:30 | 371 | 354
2019-05-16 04:00 | 371 | 354
2019-05-16 04:30 | 380 | 364
2019-05-16 05:00 | 386 | 372
2019-05-16 05:30 | 401 | 389
2019-05-16 06:00 | 423 | 413
2019-05-16 06:30 | 480 | 472
2019-05-16 07:00 | 530 | 526
2019-05-16 07:30 | 543 | 542
2019-05-16 08:00 | 542 | 539
2019-05-16 08:30 | 535 | 532
2019-05-16 09:00 | 541 | 538
2019-05-16 09:30 | 544 | 542
2019-05-16 10:00 | 534 | 532
2019-05-16 10:30 | 503 | 501
2019-05-16 11:00 | 488 | 486
2019-05-16 11:30 | 478 | 476
2019-05-16 12:00 | 497 | 495
2019-05-16 12:30 | 516 | 515
2019-05-16 13:00 | 524 | 522
2019-05-16 13:30 | 523 | 521
2019-05-16 14:00 | 522 | 520
2019-05-16 14:30 | 536 | 534
2019-05-16 15:00 | 537 | 536
2019-05-16 15:30 | 549 | 548
2019-05-16 16:00 | 570 | 568
2019-05-16 16:30 | 600 | 597
2019-05-16 17:00 | 624 | 621
2019-05-16 17:30 | 646 | 644
2019-05-16 18:00 | 651 | 648
2019-05-16 18:30 | 641 | 636
2019-05-16 19:00 | 626 | 621
2019-05-16 19:30 | 615 | 610
2019-05-16 20:00 | 615 | 611
2019-05-16 20:30 | 617 | 612
2019-05-16 21:00 | 599 | 593
2019-05-16 21:30 | 569 | 564
2019-05-16 22:00 | 543 | 538
2019-05-16 22:30 | 526 | 520
2019-05-16 23:00 | 508 | 502
2019-05-16 23:30 | 480 | 475
2019-05-17 | 451 | 444
2019-05-17 00:30 | 412 | 401
2019-05-17 01:00 | 395 | 383
2019-05-17 01:30 | 383 | 368
2019-05-17 02:00 | 371 | 356
2019-05-17 02:30 | 367 | 351
2019-05-17 03:00 | 366 | 350
2019-05-17 03:30 | 365 | 350
2019-05-17 04:00 | 364 | 349
2019-05-17 04:30 | 370 | 355
2019-05-17 05:00 | 377 | 365
2019-05-17 05:30 | 396 | 386
2019-05-17 06:00 | 419 | 411
2019-05-17 06:30 | 454 | 450
2019-05-17 07:00 | 509 | 508
2019-05-17 07:30 | 571 | 569
2019-05-17 08:00 | 591 | 588
2019-05-17 08:30 | 578 | 576
2019-05-17 09:00 | 567 | 566
2019-05-17 09:30 | 571 | 569
2019-05-17 10:00 | 573 | 571
2019-05-17 10:30 | 561 | 559
2019-05-17 11:00 | 537 | 535
2019-05-17 11:30 | 534 | 533
2019-05-17 12:00 | 535 | 534
2019-05-17 12:30 | 525 | 525
2019-05-17 13:00 | 510 | 509
2019-05-17 13:30 | 524 | 524
2019-05-17 14:00 | 522 | 521
2019-05-17 14:30 | 525 | 524
2019-05-17 15:00 | 529 | 528
2019-05-17 15:30 | 541 | 540
2019-05-17 16:00 | 563 | 562
2019-05-17 16:30 | 609 | 609
2019-05-17 17:00 | 624 | 622
2019-05-17 17:30 | 649 | 646
2019-05-17 18:00 | 650 | 642
2019-05-17 18:30 | 647 | 638
2019-05-17 19:00 | 640 | 630
2019-05-17 19:30 | 627 | 617
2019-05-17 20:00 | 621 | 610
2019-05-17 20:30 | 618 | 606
2019-05-17 21:00 | 594 | 583
2019-05-17 21:30 | 561 | 557
2019-05-17 22:00 | 543 | 539
2019-05-17 22:30 | 524 | 519
2019-05-17 23:00 | 506 | 500
2019-05-17 23:30 | 498 | 493
2019-05-18 | 472 | 467
2019-05-18 00:30 | 416 | 409
2019-05-18 01:00 | 392 | 384
2019-05-18 01:30 | 383 | 374
2019-05-18 02:00 | 368 | 357
2019-05-18 02:30 | 371 | 359
2019-05-18 03:00 | 362 | 349
2019-05-18 03:30 | 353 | 340
2019-05-18 04:00 | 350 | 337
2019-05-18 04:30 | 352 | 339
2019-05-18 05:00 | 357 | 345
2019-05-18 05:30 | 365 | 354
2019-05-18 06:00 | 377 | 367
2019-05-18 06:30 | 401 | 391
2019-05-18 07:00 | 428 | 419
2019-05-18 07:30 | 471 | 465
2019-05-18 08:00 | 485 | 480
2019-05-18 08:30 | 492 | 489
2019-05-18 09:00 | 491 | 488
2019-05-18 09:30 | 477 | 474
2019-05-18 10:00 | 473 | 470
2019-05-18 10:30 | 461 | 459
2019-05-18 11:00 | 438 | 435
2019-05-18 11:30 | 418 | 414
2019-05-18 12:00 | 416 | 412
2019-05-18 12:30 | 415 | 411
2019-05-18 13:00 | 415 | 411
2019-05-18 13:30 | 424 | 420
2019-05-18 14:00 | 448 | 444
2019-05-18 14:30 | 453 | 449
2019-05-18 15:00 | 465 | 462
2019-05-18 15:30 | 474 | 471
2019-05-18 16:00 | 486 | 483
2019-05-18 16:30 | 517 | 514
2019-05-18 17:00 | 538 | 535
2019-05-18 17:30 | 556 | 552
2019-05-18 18:00 | 560 | 557
2019-05-18 18:30 | 556 | 553
2019-05-18 19:00 | 544 | 540
2019-05-18 19:30 | 528 | 523
2019-05-18 20:00 | 516 | 513
2019-05-18 20:30 | 512 | 509
2019-05-18 21:00 | 491 | 487
2019-05-18 21:30 | 474 | 470
2019-05-18 22:00 | 466 | 462
2019-05-18 22:30 | 459 | 455
2019-05-18 23:00 | 447 | 442
2019-05-18 23:30 | 434 | 429
2019-05-19 | 415 | 407
2019-05-19 00:30 | 385 | 375
2019-05-19 01:00 | 370 | 359
2019-05-19 01:30 | 361 | 347
2019-05-19 02:00 | 355 | 340
2019-05-19 02:30 | 354 | 338
2019-05-19 03:00 | 356 | 340
2019-05-19 03:30 | 327 | 308
2019-05-19 04:00 | 335 | 316
2019-05-19 04:30 | 343 | 325
2019-05-19 05:00 | 345 | 327
2019-05-19 05:30 | 346 | 329
2019-05-19 06:00 | 349 | 332
2019-05-19 06:30 | 355 | 339
2019-05-19 07:00 | 365 | 349
2019-05-19 07:30 | 389 | 375
2019-05-19 08:00 | 415 | 401
2019-05-19 08:30 | 418 | 406
2019-05-19 09:00 | 415 | 404
2019-05-19 09:30 | 411 | 401
2019-05-19 10:00 | 395 | 385
2019-05-19 10:30 | 391 | 382
2019-05-19 11:00 | 395 | 386
2019-05-19 11:30 | 392 | 383
2019-05-19 12:00 | 385 | 376
2019-05-19 12:30 | 388 | 379
2019-05-19 13:00 | 388 | 379
2019-05-19 13:30 | 392 | 383
2019-05-19 14:00 | 412 | 404
2019-05-19 14:30 | 441 | 434
2019-05-19 15:00 | 442 | 436
2019-05-19 15:30 | 456 | 450
2019-05-19 16:00 | 468 | 463
2019-05-19 16:30 | 501 | 497
2019-05-19 17:00 | 526 | 523
2019-05-19 17:30 | 553 | 544
2019-05-19 18:00 | 561 | 552
2019-05-19 18:30 | 554 | 543
2019-05-19 19:00 | 550 | 538
2019-05-19 19:30 | 541 | 528
2019-05-19 20:00 | 523 | 519
2019-05-19 20:30 | 515 | 513
2019-05-19 21:00 | 501 | 498
2019-05-19 21:30 | 490 | 485
2019-05-19 22:00 | 478 | 472
2019-05-19 22:30 | 457 | 451
2019-05-19 23:00 | 443 | 437
2019-05-19 23:30 | 422 | 415
2019-05-20 | 403 | 394
2019-05-20 00:30 | 380 | 367
2019-05-20 01:00 | 364 | 350
2019-05-20 01:30 | 353 | 337
2019-05-20 02:00 | 346 | 330
2019-05-20 02:30 | 345 | 329
2019-05-20 03:00 | 349 | 333
2019-05-20 03:30 | 348 | 332
2019-05-20 04:00 | 358 | 342
2019-05-20 04:30 | 361 | 345
2019-05-20 05:00 | 367 | 353
2019-05-20 05:30 | 385 | 374
2019-05-20 06:00 | 417 | 410
2019-05-20 06:30 | 466 | 461
2019-05-20 07:00 | 527 | 523
2019-05-20 07:30 | 579 | 575
2019-05-20 08:00 | 601 | 596
2019-05-20 08:30 | 600 | 595
2019-05-20 09:00 | 591 | 586
2019-05-20 09:30 | 584 | 580
2019-05-20 10:00 | 592 | 589
2019-05-20 10:30 | 581 | 579
2019-05-20 11:00 | 569 | 567
2019-05-20 11:30 | 570 | 568
2019-05-20 12:00 | 575 | 573
2019-05-20 12:30 | 581 | 580
2019-05-20 13:00 | 571 | 569
2019-05-20 13:30 | 562 | 560
2019-05-20 14:00 | 559 | 557
2019-05-20 14:30 | 563 | 561
2019-05-20 15:00 | 565 | 563
2019-05-20 15:30 | 568 | 567
2019-05-20 16:00 | 579 | 578
2019-05-20 16:30 | 603 | 601
2019-05-20 17:00 | 633 | 630
2019-05-20 17:30 | 656 | 648
2019-05-20 18:00 | 664 | 657
2019-05-20 18:30 | 653 | 643
2019-05-20 19:00 | 649 | 638
2019-05-20 19:30 | 629 | 617
2019-05-20 20:00 | 621 | 611
2019-05-20 20:30 | 596 | 590
2019-05-20 21:00 | 575 | 572
2019-05-20 21:30 | 558 | 553
2019-05-20 22:00 | 533 | 527
2019-05-20 22:30 | 520 | 513
2019-05-20 23:00 | 498 | 491
2019-05-20 23:30 | 458 | 450
2019-05-21 | 437 | 425
2019-05-21 00:30 | 404 | 391
2019-05-21 01:00 | 389 | 375
2019-05-21 01:30 | 375 | 359
2019-05-21 02:00 | 365 | 349
2019-05-21 02:30 | 364 | 347
2019-05-21 03:00 | 363 | 346
2019-05-21 03:30 | 363 | 346
2019-05-21 04:00 | 364 | 347
2019-05-21 04:30 | 365 | 350
2019-05-21 05:00 | 371 | 356
2019-05-21 05:30 | 389 | 378
2019-05-21 06:00 | 409 | 402
2019-05-21 06:30 | 459 | 455
2019-05-21 07:00 | 529 | 525
2019-05-21 07:30 | 577 | 570
2019-05-21 08:00 | 597 | 581
2019-05-21 08:30 | 580 | 563
2019-05-21 09:00 | 536 | 519
2019-05-21 09:30 | 520 | 512
2019-05-21 10:00 | 512 | 506
2019-05-21 10:30 | 497 | 491
2019-05-21 11:00 | 496 | 491
2019-05-21 11:30 | 490 | 486
2019-05-21 12:00 | 499 | 494
2019-05-21 12:30 | 498 | 493
2019-05-21 13:00 | 494 | 490
2019-05-21 13:30 | 499 | 495
2019-05-21 14:00 | 503 | 498
2019-05-21 14:30 | 528 | 524
2019-05-21 15:00 | 539 | 535
2019-05-21 15:30 | 548 | 545
2019-05-21 16:00 | 563 | 561
2019-05-21 16:30 | 595 | 592
2019-05-21 17:00 | 616 | 612
2019-05-21 17:30 | 628 | 623
2019-05-21 18:00 | 639 | 635
2019-05-21 18:30 | 620 | 613
2019-05-21 19:00 | 615 | 608
2019-05-21 19:30 | 594 | 589
2019-05-21 20:00 | 587 | 582
2019-05-21 20:30 | 578 | 575
2019-05-21 21:00 | 559 | 555
2019-05-21 21:30 | 542 | 536
2019-05-21 22:00 | 519 | 513
2019-05-21 22:30 | 502 | 495
2019-05-21 23:00 | 475 | 468
2019-05-21 23:30 | 442 | 433
2019-05-22 | 417 | 405
2019-05-22 00:30 | 397 | 381
2019-05-22 01:00 | 389 | 371
2019-05-22 01:30 | 378 | 359
2019-05-22 02:00 | 393 | 374
2019-05-22 02:30 | 386 | 367
2019-05-22 03:00 | 384 | 365
2019-05-22 03:30 | 382 | 362
2019-05-22 04:00 | 383 | 364
2019-05-22 04:30 | 384 | 366
2019-05-22 05:00 | 385 | 368
2019-05-22 05:30 | 403 | 390
2019-05-22 06:00 | 425 | 415
2019-05-22 06:30 | 492 | 485
2019-05-22 07:00 | 567 | 560
2019-05-22 07:30 | 595 | 590
2019-05-22 08:00 | 581 | 576
2019-05-22 08:30 | 545 | 541
2019-05-22 09:00 | 525 | 521
2019-05-22 09:30 | 516 | 512
2019-05-22 10:00 | 522 | 518
2019-05-22 10:30 | 538 | 535
2019-05-22 11:00 | 575 | 573
2019-05-22 11:30 | 580 | 578
2019-05-22 12:00 | 566 | 563
2019-05-22 12:30 | 559 | 556
2019-05-22 13:00 | 562 | 559
2019-05-22 13:30 | 569 | 566
2019-05-22 14:00 | 555 | 553
2019-05-22 14:30 | 570 | 568
2019-05-22 15:00 | 581 | 578
2019-05-22 15:30 | 573 | 570
2019-05-22 16:00 | 584 | 581
2019-05-22 16:30 | 606 | 603
2019-05-22 17:00 | 630 | 624
2019-05-22 17:30 | 645 | 638
2019-05-22 18:00 | 658 | 652
2019-05-22 18:30 | 643 | 635
2019-05-22 19:00 | 641 | 632
2019-05-22 19:30 | 620 | 610
2019-05-22 20:00 | 599 | 596
2019-05-22 20:30 | 593 | 590
2019-05-22 21:00 | 576 | 573
2019-05-22 21:30 | 561 | 555
2019-05-22 22:00 | 541 | 537
2019-05-22 22:30 | 528 | 523
2019-05-22 23:00 | 509 | 504
2019-05-22 23:30 | 499 | 492
2019-05-23 | 474 | 465
2019-05-23 00:30 | 435 | 422
2019-05-23 01:00 | 425 | 409
2019-05-23 01:30 | 409 | 391
2019-05-23 02:00 | 393 | 373
2019-05-23 02:30 | 388 | 367
2019-05-23 03:00 | 383 | 362
2019-05-23 03:30 | 383 | 357
2019-05-23 04:00 | 381 | 355
2019-05-23 04:30 | 386 | 362
2019-05-23 05:00 | 395 | 373
2019-05-23 05:30 | 425 | 407
2019-05-23 06:00 | 460 | 446
2019-05-23 06:30 | 503 | 495
2019-05-23 07:00 | 553 | 540
2019-05-23 07:30 | 582 | 571
2019-05-23 08:00 | 584 | 571
2019-05-23 08:30 | 580 | 568
2019-05-23 09:00 | 565 | 552
2019-05-23 09:30 | 558 | 546
2019-05-23 10:00 | 536 | 524
2019-05-23 10:30 | 526 | 513
2019-05-23 11:00 | 525 | 514
2019-05-23 11:30 | 530 | 519
2019-05-23 12:00 | 532 | 521
2019-05-23 12:30 | 516 | 505
2019-05-23 13:00 | 511 | 500
2019-05-23 13:30 | 515 | 505
2019-05-23 14:00 | 522 | 512
2019-05-23 14:30 | 530 | 521
2019-05-23 15:00 | 540 | 530
2019-05-23 15:30 | 554 | 544
2019-05-23 16:00 | 575 | 566
2019-05-23 16:30 | 599 | 590
2019-05-23 17:00 | 622 | 609
2019-05-23 17:30 | 637 | 626
2019-05-23 18:00 | 651 | 638
2019-05-23 18:30 | 644 | 627
2019-05-23 19:00 | 638 | 619
2019-05-23 19:30 | 616 | 596
2019-05-23 20:00 | 614 | 597
2019-05-23 20:30 | 602 | 591
2019-05-23 21:00 | 583 | 572
2019-05-23 21:30 | 559 | 551
2019-05-23 22:00 | 537 | 532
2019-05-23 22:30 | 528 | 522
2019-05-23 23:00 | 514 | 508
2019-05-23 23:30 | 501 | 492
2019-05-24 | 479 | 468
2019-05-24 00:30 | 435 | 421
2019-05-24 01:00 | 415 | 398
2019-05-24 01:30 | 407 | 389
2019-05-24 02:00 | 404 | 383
2019-05-24 02:30 | 398 | 377
2019-05-24 03:00 | 388 | 367
2019-05-24 03:30 | 380 | 358
2019-05-24 04:00 | 375 | 353
2019-05-24 04:30 | 375 | 354
2019-05-24 05:00 | 378 | 359
2019-05-24 05:30 | 401 | 386
2019-05-24 06:00 | 435 | 423
2019-05-24 06:30 | 493 | 486
2019-05-24 07:00 | 544 | 536
2019-05-24 07:30 | 577 | 570
2019-05-24 08:00 | 592 | 584
2019-05-24 08:30 | 586 | 577
2019-05-24 09:00 | 557 | 548
2019-05-24 09:30 | 542 | 533
2019-05-24 10:00 | 524 | 515
2019-05-24 10:30 | 514 | 506
2019-05-24 11:00 | 505 | 497
2019-05-24 11:30 | 505 | 497
2019-05-24 12:00 | 512 | 505
2019-05-24 12:30 | 506 | 497
2019-05-24 13:00 | 498 | 491
2019-05-24 13:30 | 514 | 508
2019-05-24 14:00 | 526 | 520
2019-05-24 14:30 | 539 | 533
2019-05-24 15:00 | 541 | 535
2019-05-24 15:30 | 541 | 535
2019-05-24 16:00 | 554 | 549
2019-05-24 16:30 | 585 | 580
2019-05-24 17:00 | 609 | 603
2019-05-24 17:30 | 614 | 601
2019-05-24 18:00 | 614 | 602
2019-05-24 18:30 | 608 | 593
2019-05-24 19:00 | 607 | 592
2019-05-24 19:30 | 586 | 579
2019-05-24 20:00 | 588 | 580
2019-05-24 20:30 | 583 | 575
2019-05-24 21:00 | 556 | 549
2019-05-24 21:30 | 537 | 528
2019-05-24 22:00 | 525 | 515
2019-05-24 22:30 | 517 | 506
2019-05-24 23:00 | 504 | 494
2019-05-24 23:30 | 482 | 469
2019-05-25 | 456 | 441
2019-05-25 00:30 | 422 | 403
2019-05-25 01:00 | 404 | 381
2019-05-25 01:30 | 392 | 368
2019-05-25 02:00 | 376 | 350
2019-05-25 02:30 | 364 | 338
2019-05-25 03:00 | 347 | 319
2019-05-25 03:30 | 340 | 312
2019-05-25 04:00 | 338 | 310
2019-05-25 04:30 | 339 | 311
2019-05-25 05:00 | 339 | 312
2019-05-25 05:30 | 348 | 323
2019-05-25 06:00 | 360 | 337
2019-05-25 06:30 | 386 | 365
2019-05-25 07:00 | 409 | 389
2019-05-25 07:30 | 441 | 423
2019-05-25 08:00 | 460 | 444
2019-05-25 08:30 | 464 | 449
2019-05-25 09:00 | 456 | 442
2019-05-25 09:30 | 434 | 420
2019-05-25 10:00 | 406 | 392
2019-05-25 10:30 | 384 | 369
2019-05-25 11:00 | 373 | 357
2019-05-25 11:30 | 353 | 337
2019-05-25 12:00 | 346 | 329
2019-05-25 12:30 | 353 | 337
2019-05-25 13:00 | 353 | 338
2019-05-25 13:30 | 360 | 345
2019-05-25 14:00 | 358 | 343
2019-05-25 14:30 | 372 | 358
2019-05-25 15:00 | 396 | 383
2019-05-25 15:30 | 418 | 405
2019-05-25 16:00 | 444 | 433
2019-05-25 16:30 | 479 | 469
2019-05-25 17:00 | 508 | 499
2019-05-25 17:30 | 527 | 520
2019-05-25 18:00 | 539 | 532
2019-05-25 18:30 | 531 | 523
2019-05-25 19:00 | 529 | 520
2019-05-25 19:30 | 517 | 507
2019-05-25 20:00 | 515 | 504
2019-05-25 20:30 | 513 | 502
2019-05-25 21:00 | 502 | 491
2019-05-25 21:30 | 488 | 477
2019-05-25 22:00 | 472 | 460
2019-05-25 22:30 | 463 | 450
2019-05-25 23:00 | 449 | 436
2019-05-25 23:30 | 431 | 415
2019-05-26 | 416 | 397
2019-05-26 00:30 | 382 | 360
2019-05-26 01:00 | 365 | 342
2019-05-26 01:30 | 350 | 323
2019-05-26 02:00 | 333 | 304
2019-05-26 02:30 | 327 | 298
2019-05-26 03:00 | 330 | 300
2019-05-26 03:30 | 331 | 300
2019-05-26 04:00 | 330 | 300
2019-05-26 04:30 | 332 | 302
2019-05-26 05:00 | 329 | 299
2019-05-26 05:30 | 330 | 301
2019-05-26 06:00 | 335 | 307
2019-05-26 06:30 | 344 | 318
2019-05-26 07:00 | 355 | 328
2019-05-26 07:30 | 380 | 357
2019-05-26 08:00 | 407 | 386
2019-05-26 08:30 | 423 | 405
2019-05-26 09:00 | 421 | 404
2019-05-26 09:30 | 405 | 389
2019-05-26 10:00 | 368 | 353
2019-05-26 10:30 | 357 | 341
2019-05-26 11:00 | 345 | 329
2019-05-26 11:30 | 333 | 315
2019-05-26 12:00 | 334 | 317
2019-05-26 12:30 | 337 | 319
2019-05-26 13:00 | 351 | 335
2019-05-26 13:30 | 368 | 353
2019-05-26 14:00 | 396 | 384
2019-05-26 14:30 | 421 | 410
2019-05-26 15:00 | 414 | 404
2019-05-26 15:30 | 415 | 404
2019-05-26 16:00 | 414 | 404
2019-05-26 16:30 | 444 | 435
2019-05-26 17:00 | 474 | 464
2019-05-26 17:30 | 494 | 487
2019-05-26 18:00 | 521 | 516
2019-05-26 18:30 | 515 | 509
2019-05-26 19:00 | 506 | 500
2019-05-26 19:30 | 496 | 489
2019-05-26 20:00 | 495 | 487
2019-05-26 20:30 | 500 | 492
2019-05-26 21:00 | 493 | 484
2019-05-26 21:30 | 478 | 469
2019-05-26 22:00 | 469 | 460
2019-05-26 22:30 | 453 | 443
2019-05-26 23:00 | 428 | 416
2019-05-26 23:30 | 414 | 399
2019-05-27 | 392 | 374
2019-05-27 00:30 | 365 | 341
2019-05-27 01:00 | 341 | 316
2019-05-27 01:30 | 332 | 305
2019-05-27 02:00 | 323 | 293
2019-05-27 02:30 | 321 | 289
2019-05-27 03:00 | 320 | 288
2019-05-27 03:30 | 328 | 296
2019-05-27 04:00 | 327 | 296
2019-05-27 04:30 | 334 | 305
2019-05-27 05:00 | 344 | 317
2019-05-27 05:30 | 366 | 346
2019-05-27 06:00 | 388 | 373
2019-05-27 06:30 | 448 | 438
2019-05-27 07:00 | 507 | 495
2019-05-27 07:30 | 547 | 533
2019-05-27 08:00 | 554 | 542
2019-05-27 08:30 | 553 | 539
2019-05-27 09:00 | 525 | 512
2019-05-27 09:30 | 513 | 499
2019-05-27 10:00 | 498 | 484
2019-05-27 10:30 | 501 | 487
2019-05-27 11:00 | 493 | 479
2019-05-27 11:30 | 498 | 484
2019-05-27 12:00 | 481 | 467
2019-05-27 12:30 | 477 | 464
2019-05-27 13:00 | 483 | 470
2019-05-27 13:30 | 481 | 469
2019-05-27 14:00 | 493 | 482
2019-05-27 14:30 | 511 | 501
2019-05-27 15:00 | 510 | 500
2019-05-27 15:30 | 522 | 513
2019-05-27 16:00 | 545 | 537
2019-05-27 16:30 | 568 | 560
2019-05-27 17:00 | 599 | 585
2019-05-27 17:30 | 613 | 602
2019-05-27 18:00 | 615 | 605
2019-05-27 18:30 | 605 | 592
2019-05-27 19:00 | 599 | 584
2019-05-27 19:30 | 591 | 574
2019-05-27 20:00 | 568 | 561
2019-05-27 20:30 | 563 | 557
2019-05-27 21:00 | 540 | 535
2019-05-27 21:30 | 513 | 506
2019-05-27 22:00 | 485 | 480
2019-05-27 22:30 | 488 | 482
2019-05-27 23:00 | 477 | 471
2019-05-27 23:30 | 458 | 450
2019-05-28 | 427 | 416
2019-05-28 00:30 | 393 | 378
2019-05-28 01:00 | 375 | 359
2019-05-28 01:30 | 357 | 340
2019-05-28 02:00 | 346 | 327
2019-05-28 02:30 | 344 | 321
2019-05-28 03:00 | 344 | 321
2019-05-28 03:30 | 339 | 316
2019-05-28 04:00 | 343 | 320
2019-05-28 04:30 | 349 | 328
2019-05-28 05:00 | 357 | 338
2019-05-28 05:30 | 387 | 373
2019-05-28 06:00 | 410 | 400
2019-05-28 06:30 | 468 | 463
2019-05-28 07:00 | 517 | 514
2019-05-28 07:30 | 541 | 537
2019-05-28 08:00 | 546 | 541
2019-05-28 08:30 | 531 | 525
2019-05-28 09:00 | 493 | 489
2019-05-28 09:30 | 477 | 473
2019-05-28 10:00 | 453 | 448
2019-05-28 10:30 | 451 | 446
2019-05-28 11:00 | 443 | 438
2019-05-28 11:30 | 449 | 444
2019-05-28 12:00 | 462 | 456
2019-05-28 12:30 | 460 | 454
2019-05-28 13:00 | 461 | 455
2019-05-28 13:30 | 469 | 464
2019-05-28 14:00 | 471 | 466
2019-05-28 14:30 | 479 | 475
2019-05-28 15:00 | 484 | 481
2019-05-28 15:30 | 488 | 485
2019-05-28 16:00 | 512 | 509
2019-05-28 16:30 | 529 | 527
2019-05-28 17:00 | 556 | 554
2019-05-28 17:30 | 587 | 584
2019-05-28 18:00 | 597 | 589
2019-05-28 18:30 | 587 | 576
2019-05-28 19:00 | 586 | 575
2019-05-28 19:30 | 585 | 573
2019-05-28 20:00 | 579 | 568
2019-05-28 20:30 | 572 | 563
2019-05-28 21:00 | 544 | 537
2019-05-28 21:30 | 513 | 508
2019-05-28 22:00 | 494 | 490
2019-05-28 22:30 | 491 | 487
2019-05-28 23:00 | 479 | 474
2019-05-28 23:30 | 469 | 462
2019-05-29 | 456 | 447
2019-05-29 00:30 | 428 | 417
2019-05-29 01:00 | 412 | 398
2019-05-29 01:30 | 398 | 383
2019-05-29 02:00 | 386 | 369
2019-05-29 02:30 | 376 | 358
2019-05-29 03:00 | 369 | 351
2019-05-29 03:30 | 360 | 342
2019-05-29 04:00 | 350 | 332
2019-05-29 04:30 | 355 | 338
2019-05-29 05:00 | 358 | 344
2019-05-29 05:30 | 382 | 371
2019-05-29 06:00 | 418 | 411
2019-05-29 06:30 | 486 | 476
2019-05-29 07:00 | 549 | 541
2019-05-29 07:30 | 580 | 574
2019-05-29 08:00 | 583 | 575
2019-05-29 08:30 | 567 | 557
2019-05-29 09:00 | 533 | 524
2019-05-29 09:30 | 498 | 495
2019-05-29 10:00 | 474 | 472
2019-05-29 10:30 | 452 | 450
2019-05-29 11:00 | 442 | 441
2019-05-29 11:30 | 433 | 431
2019-05-29 12:00 | 421 | 420
2019-05-29 12:30 | 430 | 428
2019-05-29 13:00 | 418 | 416
2019-05-29 13:30 | 435 | 434
2019-05-29 14:00 | 450 | 449
2019-05-29 14:30 | 468 | 467
2019-05-29 15:00 | 483 | 481
2019-05-29 15:30 | 497 | 496
2019-05-29 16:00 | 518 | 518
2019-05-29 16:30 | 547 | 547
2019-05-29 17:00 | 573 | 573
2019-05-29 17:30 | 595 | 595
2019-05-29 18:00 | 607 | 605
2019-05-29 18:30 | 599 | 597
2019-05-29 19:00 | 597 | 595
2019-05-29 19:30 | 584 | 581
2019-05-29 20:00 | 581 | 579
2019-05-29 20:30 | 580 | 577
2019-05-29 21:00 | 567 | 564
2019-05-29 21:30 | 547 | 543
2019-05-29 22:00 | 530 | 525
2019-05-29 22:30 | 519 | 515
2019-05-29 23:00 | 507 | 503
2019-05-29 23:30 | 499 | 494
2019-05-30 | 481 | 473
2019-05-30 00:30 | 453 | 443
2019-05-30 01:00 | 425 | 412
2019-05-30 01:30 | 412 | 399
2019-05-30 02:00 | 400 | 386
2019-05-30 02:30 | 389 | 374
2019-05-30 03:00 | 382 | 367
2019-05-30 03:30 | 379 | 364
2019-05-30 04:00 | 369 | 354
2019-05-30 04:30 | 372 | 358
2019-05-30 05:00 | 382 | 369
2019-05-30 05:30 | 425 | 416
2019-05-30 06:00 | 454 | 448
2019-05-30 06:30 | 519 | 511
2019-05-30 07:00 | 575 | 567
2019-05-30 07:30 | 618 | 609
2019-05-30 08:00 | 609 | 599
2019-05-30 08:30 | 579 | 568
2019-05-30 09:00 | 543 | 532
2019-05-30 09:30 | 501 | 497
2019-05-30 10:00 | 475 | 472
2019-05-30 10:30 | 454 | 450
2019-05-30 11:00 | 433 | 430
2019-05-30 11:30 | 432 | 429
2019-05-30 12:00 | 426 | 424
2019-05-30 12:30 | 429 | 427
2019-05-30 13:00 | 434 | 432
2019-05-30 13:30 | 441 | 440
2019-05-30 14:00 | 450 | 449
2019-05-30 14:30 | 462 | 461
2019-05-30 15:00 | 473 | 472
2019-05-30 15:30 | 495 | 495
2019-05-30 16:00 | 526 | 524
2019-05-30 16:30 | 557 | 555
2019-05-30 17:00 | 588 | 585
2019-05-30 17:30 | 605 | 604
2019-05-30 18:00 | 621 | 619
2019-05-30 18:30 | 611 | 610
2019-05-30 19:00 | 614 | 613
2019-05-30 19:30 | 604 | 602
2019-05-30 20:00 | 598 | 597
2019-05-30 20:30 | 600 | 599
2019-05-30 21:00 | 584 | 582
2019-05-30 21:30 | 562 | 560
2019-05-30 22:00 | 540 | 538
2019-05-30 22:30 | 538 | 535
2019-05-30 23:00 | 514 | 511
2019-05-30 23:30 | 502 | 498
2019-05-31 | 486 | 481
2019-05-31 00:30 | 454 | 447
2019-05-31 01:00 | 438 | 428
2019-05-31 01:30 | 423 | 412
2019-05-31 02:00 | 408 | 397
2019-05-31 02:30 | 390 | 379
2019-05-31 03:00 | 379 | 368
2019-05-31 03:30 | 370 | 359
2019-05-31 04:00 | 358 | 348
2019-05-31 04:30 | 365 | 355
2019-05-31 05:00 | 381 | 373
2019-05-31 05:30 | 426 | 421
2019-05-31 06:00 | 463 | 460
2019-05-31 06:30 | 520 | 519
2019-05-31 07:00 | 571 | 571
2019-05-31 07:30 | 609 | 607
2019-05-31 08:00 | 606 | 604
2019-05-31 08:30 | 585 | 583
2019-05-31 09:00 | 554 | 551
2019-05-31 09:30 | 519 | 516
2019-05-31 10:00 | 494 | 492
2019-05-31 10:30 | 477 | 476
2019-05-31 11:00 | 448 | 447
2019-05-31 11:30 | 432 | 431
2019-05-31 12:00 | 418 | 417
2019-05-31 12:30 | 414 | 413
2019-05-31 13:00 | 416 | 415
2019-05-31 13:30 | 426 | 425
2019-05-31 14:00 | 420 | 419
2019-05-31 14:30 | 443 | 442
2019-05-31 15:00 | 460 | 459
2019-05-31 15:30 | 474 | 474
2019-05-31 16:00 | 492 | 491
2019-05-31 16:30 | 529 | 528
2019-05-31 17:00 | 572 | 571
2019-05-31 17:30 | 607 | 605
2019-05-31 18:00 | 615 | 613
2019-05-31 18:30 | 612 | 610
2019-05-31 19:00 | 622 | 619
2019-05-31 19:30 | 616 | 614
2019-05-31 20:00 | 613 | 611
2019-05-31 20:30 | 607 | 605
2019-05-31 21:00 | 586 | 584
2019-05-31 21:30 | 575 | 571
2019-05-31 22:00 | 555 | 551
2019-05-31 22:30 | 536 | 534
2019-05-31 23:00 | 516 | 514
2019-05-31 23:30 | 506 | 503
2019-06-01 | 490 | 486
2019-06-01 00:30 | 466 | 460
2019-06-01 01:00 | 447 | 440
2019-06-01 01:30 | 437 | 428
2019-06-01 02:00 | 429 | 417
2019-06-01 02:30 | 426 | 414
2019-06-01 03:00 | 414 | 401
2019-06-01 03:30 | 404 | 392
2019-06-01 04:00 | 394 | 382
2019-06-01 04:30 | 389 | 377
2019-06-01 05:00 | 382 | 371
2019-06-01 05:30 | 390 | 380
2019-06-01 06:00 | 409 | 400
2019-06-01 06:30 | 441 | 434
2019-06-01 07:00 | 473 | 468
2019-06-01 07:30 | 509 | 507
2019-06-01 08:00 | 526 | 525
2019-06-01 08:30 | 584 | 582
2019-06-01 09:00 | 519 | 517
2019-06-01 09:30 | 530 | 526
2019-06-01 10:00 | 504 | 500
2019-06-01 10:30 | 465 | 460
2019-06-01 11:00 | 447 | 442
2019-06-01 11:30 | 444 | 438
2019-06-01 12:00 | 439 | 433
2019-06-01 12:30 | 445 | 439
2019-06-01 13:00 | 453 | 448
2019-06-01 13:30 | 469 | 465
2019-06-01 14:00 | 489 | 485
2019-06-01 14:30 | 483 | 479
2019-06-01 15:00 | 481 | 477
2019-06-01 15:30 | 482 | 479
2019-06-01 16:00 | 489 | 487
2019-06-01 16:30 | 515 | 513
2019-06-01 17:00 | 549 | 547
2019-06-01 17:30 | 584 | 579
2019-06-01 18:00 | 592 | 586
2019-06-01 18:30 | 590 | 584
2019-06-01 19:00 | 584 | 577
2019-06-01 19:30 | 558 | 551
2019-06-01 20:00 | 553 | 545
2019-06-01 20:30 | 550 | 541
2019-06-01 21:00 | 530 | 518
2019-06-01 21:30 | 515 | 502
2019-06-01 22:00 | 499 | 485
2019-06-01 22:30 | 486 | 471
2019-06-01 23:00 | 473 | 464
2019-06-01 23:30 | 459 | 453
2019-06-02 | 441 | 433
2019-06-02 00:30 | 422 | 412
2019-06-02 01:00 | 413 | 401
2019-06-02 01:30 | 407 | 393
2019-06-02 02:00 | 397 | 382
2019-06-02 02:30 | 386 | 371
2019-06-02 03:00 | 379 | 363
2019-06-02 03:30 | 381 | 364
2019-06-02 04:00 | 380 | 363
2019-06-02 04:30 | 379 | 363
2019-06-02 05:00 | 379 | 363
2019-06-02 05:30 | 382 | 367
2019-06-02 06:00 | 379 | 365
2019-06-02 06:30 | 393 | 380
2019-06-02 07:00 | 411 | 398
2019-06-02 07:30 | 436 | 424
2019-06-02 08:00 | 466 | 454
2019-06-02 08:30 | 475 | 465
2019-06-02 09:00 | 471 | 463
2019-06-02 09:30 | 485 | 478
2019-06-02 10:00 | 489 | 484
2019-06-02 10:30 | 468 | 462
2019-06-02 11:00 | 436 | 428
2019-06-02 11:30 | 432 | 424
2019-06-02 12:00 | 440 | 432
2019-06-02 12:30 | 449 | 441
2019-06-02 13:00 | 440 | 432
2019-06-02 13:30 | 461 | 456
2019-06-02 14:00 | 483 | 478
2019-06-02 14:30 | 477 | 472
2019-06-02 15:00 | 457 | 451
2019-06-02 15:30 | 461 | 455
2019-06-02 16:00 | 470 | 465
2019-06-02 16:30 | 497 | 494
2019-06-02 17:00 | 538 | 536
2019-06-02 17:30 | 562 | 557
2019-06-02 18:00 | 578 | 573
2019-06-02 18:30 | 566 | 560
2019-06-02 19:00 | 562 | 555
2019-06-02 19:30 | 558 | 550
2019-06-02 20:00 | 557 | 549
2019-06-02 20:30 | 558 | 550
2019-06-02 21:00 | 526 | 523
2019-06-02 21:30 | 510 | 507
2019-06-02 22:00 | 499 | 496
2019-06-02 22:30 | 486 | 482
2019-06-02 23:00 | 478 | 473
2019-06-02 23:30 | 461 | 455
2019-06-03 | 444 | 436
2019-06-03 00:30 | 404 | 394
2019-06-03 01:00 | 392 | 379
2019-06-03 01:30 | 378 | 365
2019-06-03 02:00 | 357 | 342
2019-06-03 02:30 | 346 | 330
2019-06-03 03:00 | 340 | 324
2019-06-03 03:30 | 339 | 323
2019-06-03 04:00 | 337 | 321
2019-06-03 04:30 | 347 | 332
2019-06-03 05:00 | 362 | 348
2019-06-03 05:30 | 388 | 378
2019-06-03 06:00 | 425 | 419
2019-06-03 06:30 | 479 | 477
2019-06-03 07:00 | 516 | 514
2019-06-03 07:30 | 550 | 548
2019-06-03 08:00 | 574 | 571
2019-06-03 08:30 | 569 | 566
2019-06-03 09:00 | 542 | 540
2019-06-03 09:30 | 525 | 522
2019-06-03 10:00 | 509 | 506
2019-06-03 10:30 | 493 | 490
2019-06-03 11:00 | 475 | 472
2019-06-03 11:30 | 297 | 294
2019-06-03 12:00 | 463 | 461
2019-06-03 12:30 | 381 | 374
2019-06-03 13:00 | 457 | 455
2019-06-03 13:30 | 478 | 476
2019-06-03 14:00 | 490 | 488
2019-06-03 14:30 | 492 | 490
2019-06-03 15:00 | 517 | 514
2019-06-03 15:30 | 528 | 526
2019-06-03 16:00 | 549 | 547
2019-06-03 16:30 | 581 | 579
2019-06-03 17:00 | 606 | 604
2019-06-03 17:30 | 633 | 629
2019-06-03 18:00 | 656 | 650
2019-06-03 18:30 | 642 | 634
2019-06-03 19:00 | 646 | 637
2019-06-03 19:30 | 646 | 643
2019-06-03 20:00 | 638 | 635
2019-06-03 20:30 | 625 | 623
2019-06-03 21:00 | 597 | 596
2019-06-03 21:30 | 576 | 574
2019-06-03 22:00 | 552 | 549
2019-06-03 22:30 | 536 | 533
2019-06-03 23:00 | 518 | 514
2019-06-03 23:30 | 497 | 494
2019-06-04 | 480 | 476
2019-06-04 00:30 | 442 | 437
2019-06-04 01:00 | 416 | 409
2019-06-04 01:30 | 405 | 397
2019-06-04 02:00 | 394 | 385
2019-06-04 02:30 | 395 | 384
2019-06-04 03:00 | 389 | 379
2019-06-04 03:30 | 385 | 374
2019-06-04 04:00 | 382 | 372
2019-06-04 04:30 | 395 | 386
2019-06-04 05:00 | 407 | 399
2019-06-04 05:30 | 436 | 430
2019-06-04 06:00 | 463 | 460
2019-06-04 06:30 | 514 | 512
2019-06-04 07:00 | 574 | 573
2019-06-04 07:30 | 627 | 625
2019-06-04 08:00 | 624 | 622
2019-06-04 08:30 | 607 | 604
2019-06-04 09:00 | 566 | 563
2019-06-04 09:30 | 537 | 535
2019-06-04 10:00 | 516 | 514
2019-06-04 10:30 | 519 | 517
2019-06-04 11:00 | 512 | 509
2019-06-04 11:30 | 508 | 504
2019-06-04 12:00 | 502 | 498
2019-06-04 12:30 | 500 | 497
2019-06-04 13:00 | 497 | 494
2019-06-04 13:30 | 493 | 489
2019-06-04 14:00 | 493 | 490
2019-06-04 14:30 | 505 | 502
2019-06-04 15:00 | 505 | 502
2019-06-04 15:30 | 525 | 523
2019-06-04 16:00 | 549 | 548
2019-06-04 16:30 | 581 | 580
2019-06-04 17:00 | 645 | 643
2019-06-04 17:30 | 701 | 699
2019-06-04 18:00 | 736 | 725
2019-06-04 18:30 | 726 | 715
2019-06-04 19:00 | 715 | 705
2019-06-04 19:30 | 717 | 707
2019-06-04 20:00 | 716 | 705
2019-06-04 20:30 | 707 | 695
2019-06-04 21:00 | 659 | 655
2019-06-04 21:30 | 634 | 629
2019-06-04 22:00 | 609 | 605
2019-06-04 22:30 | 580 | 577
2019-06-04 23:00 | 556 | 551
2019-06-04 23:30 | 532 | 526
2019-06-05 | 515 | 508
2019-06-05 00:30 | 480 | 471
2019-06-05 01:00 | 455 | 444
2019-06-05 01:30 | 430 | 418
2019-06-05 02:00 | 414 | 400
2019-06-05 02:30 | 410 | 395
2019-06-05 03:00 | 396 | 380
2019-06-05 03:30 | 389 | 373
2019-06-05 04:00 | 389 | 373
2019-06-05 04:30 | 415 | 401
2019-06-05 05:00 | 410 | 398
2019-06-05 05:30 | 431 | 421
2019-06-05 06:00 | 466 | 458
2019-06-05 06:30 | 563 | 549
2019-06-05 07:00 | 629 | 619
2019-06-05 07:30 | 654 | 646
2019-06-05 08:00 | 652 | 644
2019-06-05 08:30 | 610 | 598
2019-06-05 09:00 | 576 | 566
2019-06-05 09:30 | 548 | 542
2019-06-05 10:00 | 530 | 523
2019-06-05 10:30 | 520 | 514
2019-06-05 11:00 | 497 | 491
2019-06-05 11:30 | 472 | 465
2019-06-05 12:00 | 470 | 464
2019-06-05 12:30 | 469 | 464
2019-06-05 13:00 | 483 | 479
2019-06-05 13:30 | 466 | 463
2019-06-05 14:00 | 475 | 473
2019-06-05 14:30 | 488 | 486
2019-06-05 15:00 | 492 | 490
2019-06-05 15:30 | 524 | 522
2019-06-05 16:00 | 558 | 556
2019-06-05 16:30 | 593 | 590
2019-06-05 17:00 | 616 | 612
2019-06-05 17:30 | 657 | 653
2019-06-05 18:00 | 675 | 672
2019-06-05 18:30 | 681 | 677
2019-06-05 19:00 | 675 | 671
2019-06-05 19:30 | 672 | 668
2019-06-05 20:00 | 659 | 656
2019-06-05 20:30 | 650 | 646
2019-06-05 21:00 | 638 | 633
2019-06-05 21:30 | 621 | 616
2019-06-05 22:00 | 606 | 599
2019-06-05 22:30 | 581 | 575
2019-06-05 23:00 | 560 | 553
2019-06-05 23:30 | 541 | 535
2019-06-06 | 523 | 517
2019-06-06 00:30 | 499 | 492
2019-06-06 01:00 | 477 | 468
2019-06-06 01:30 | 448 | 437
2019-06-06 02:00 | 437 | 425
2019-06-06 02:30 | 433 | 421
2019-06-06 03:00 | 421 | 409
2019-06-06 03:30 | 426 | 413
2019-06-06 04:00 | 424 | 412
2019-06-06 04:30 | 421 | 410
2019-06-06 05:00 | 440 | 430
2019-06-06 05:30 | 485 | 478
2019-06-06 06:00 | 512 | 508
2019-06-06 06:30 | 555 | 553
2019-06-06 07:00 | 612 | 610
2019-06-06 07:30 | 649 | 645
2019-06-06 08:00 | 654 | 645
2019-06-06 08:30 | 609 | 597
2019-06-06 09:00 | 557 | 546
2019-06-06 09:30 | 546 | 537
2019-06-06 10:00 | 516 | 506
2019-06-06 10:30 | 484 | 479
2019-06-06 11:00 | 479 | 478
2019-06-06 11:30 | 493 | 492
2019-06-06 12:00 | 489 | 488
2019-06-06 12:30 | 487 | 486
2019-06-06 13:00 | 491 | 490
2019-06-06 13:30 | 491 | 491
2019-06-06 14:00 | 504 | 503
2019-06-06 14:30 | 523 | 522
2019-06-06 15:00 | 530 | 529
2019-06-06 15:30 | 544 | 543
2019-06-06 16:00 | 561 | 560
2019-06-06 16:30 | 593 | 592
2019-06-06 17:00 | 624 | 623
2019-06-06 17:30 | 660 | 659
2019-06-06 18:00 | 673 | 671
2019-06-06 18:30 | 666 | 662
2019-06-06 19:00 | 675 | 671
2019-06-06 19:30 | 662 | 658
2019-06-06 20:00 | 664 | 659
2019-06-06 20:30 | 666 | 661
2019-06-06 21:00 | 658 | 652
2019-06-06 21:30 | 635 | 630
2019-06-06 22:00 | 612 | 606
2019-06-06 22:30 | 579 | 576
2019-06-06 23:00 | 560 | 556
2019-06-06 23:30 | 536 | 532
2019-06-07 | 515 | 510
2019-06-07 00:30 | 484 | 476
2019-06-07 01:00 | 462 | 453
2019-06-07 01:30 | 451 | 441
2019-06-07 02:00 | 433 | 422
2019-06-07 02:30 | 415 | 403
2019-06-07 03:00 | 401 | 388
2019-06-07 03:30 | 396 | 384
2019-06-07 04:00 | 392 | 380
2019-06-07 04:30 | 392 | 380
2019-06-07 05:00 | 403 | 392
2019-06-07 05:30 | 426 | 419
2019-06-07 06:00 | 470 | 465
2019-06-07 06:30 | 544 | 543
2019-06-07 07:00 | 614 | 610
2019-06-07 07:30 | 645 | 642
2019-06-07 08:00 | 645 | 643
2019-06-07 08:30 | 623 | 620
2019-06-07 09:00 | 574 | 570
2019-06-07 09:30 | 552 | 546
2019-06-07 10:00 | 534 | 528
2019-06-07 10:30 | 526 | 519
2019-06-07 11:00 | 520 | 514
2019-06-07 11:30 | 515 | 509
2019-06-07 12:00 | 507 | 501
2019-06-07 12:30 | 521 | 515
2019-06-07 13:00 | 554 | 549
2019-06-07 13:30 | 546 | 541
2019-06-07 14:00 | 544 | 539
2019-06-07 14:30 | 545 | 540
2019-06-07 15:00 | 543 | 537
2019-06-07 15:30 | 552 | 547
2019-06-07 16:00 | 569 | 564
2019-06-07 16:30 | 593 | 588
2019-06-07 17:00 | 610 | 606
2019-06-07 17:30 | 628 | 626
2019-06-07 18:00 | 643 | 640
2019-06-07 18:30 | 642 | 639
2019-06-07 19:00 | 652 | 649
2019-06-07 19:30 | 646 | 644
2019-06-07 20:00 | 638 | 634
2019-06-07 20:30 | 628 | 623
2019-06-07 21:00 | 612 | 608
2019-06-07 21:30 | 596 | 592
2019-06-07 22:00 | 582 | 578
2019-06-07 22:30 | 560 | 556
2019-06-07 23:00 | 538 | 533
2019-06-07 23:30 | 523 | 517
2019-06-08 | 510 | 502
2019-06-08 00:30 | 482 | 472
2019-06-08 01:00 | 462 | 452
2019-06-08 01:30 | 438 | 426
2019-06-08 02:00 | 423 | 410
2019-06-08 02:30 | 409 | 394
2019-06-08 03:00 | 390 | 374
2019-06-08 03:30 | 386 | 369
2019-06-08 04:00 | 369 | 351
2019-06-08 04:30 | 358 | 341
2019-06-08 05:00 | 353 | 336
2019-06-08 05:30 | 371 | 355
2019-06-08 06:00 | 393 | 379
2019-06-08 06:30 | 428 | 416
2019-06-08 07:00 | 460 | 449
2019-06-08 07:30 | 491 | 482
2019-06-08 08:00 | 504 | 496
2019-06-08 08:30 | 516 | 511
2019-06-08 09:00 | 522 | 517
2019-06-08 09:30 | 535 | 530
2019-06-08 10:00 | 533 | 529
2019-06-08 10:30 | 533 | 529
2019-06-08 11:00 | 536 | 532
2019-06-08 11:30 | 534 | 530
2019-06-08 12:00 | 543 | 540
2019-06-08 12:30 | 529 | 526
2019-06-08 13:00 | 519 | 515
2019-06-08 13:30 | 520 | 517
2019-06-08 14:00 | 525 | 522
2019-06-08 14:30 | 521 | 517
2019-06-08 15:00 | 526 | 523
2019-06-08 15:30 | 530 | 527
2019-06-08 16:00 | 554 | 551
2019-06-08 16:30 | 560 | 558
2019-06-08 17:00 | 578 | 577
2019-06-08 17:30 | 612 | 611
2019-06-08 18:00 | 624 | 623
2019-06-08 18:30 | 621 | 620
2019-06-08 19:00 | 610 | 609
2019-06-08 19:30 | 601 | 599
2019-06-08 20:00 | 590 | 587
2019-06-08 20:30 | 583 | 579
2019-06-08 21:00 | 573 | 569
2019-06-08 21:30 | 562 | 556
2019-06-08 22:00 | 544 | 540
2019-06-08 22:30 | 533 | 528
2019-06-08 23:00 | 520 | 515
2019-06-08 23:30 | 508 | 502
2019-06-09 | 488 | 480
2019-06-09 00:30 | 451 | 441
2019-06-09 01:00 | 429 | 416
2019-06-09 01:30 | 400 | 385
2019-06-09 02:00 | 390 | 372
2019-06-09 02:30 | 372 | 352
2019-06-09 03:00 | 358 | 336
2019-06-09 03:30 | 345 | 325
2019-06-09 04:00 | 334 | 316
2019-06-09 04:30 | 332 | 314
2019-06-09 05:00 | 327 | 310
2019-06-09 05:30 | 335 | 319
2019-06-09 06:00 | 347 | 332
2019-06-09 06:30 | 364 | 350
2019-06-09 07:00 | 389 | 376
2019-06-09 07:30 | 419 | 408
2019-06-09 08:00 | 431 | 421
2019-06-09 08:30 | 458 | 448
2019-06-09 09:00 | 461 | 452
2019-06-09 09:30 | 456 | 447
2019-06-09 10:00 | 444 | 436
2019-06-09 10:30 | 431 | 423
2019-06-09 11:00 | 411 | 402
2019-06-09 11:30 | 394 | 384
2019-06-09 12:00 | 371 | 360
2019-06-09 12:30 | 380 | 369
2019-06-09 13:00 | 395 | 385
2019-06-09 13:30 | 403 | 394
2019-06-09 14:00 | 408 | 400
2019-06-09 14:30 | 416 | 409
2019-06-09 15:00 | 427 | 420
2019-06-09 15:30 | 449 | 442
2019-06-09 16:00 | 480 | 475
2019-06-09 16:30 | 507 | 504
2019-06-09 17:00 | 529 | 526
2019-06-09 17:30 | 540 | 539
2019-06-09 18:00 | 547 | 547
2019-06-09 18:30 | 550 | 549
2019-06-09 19:00 | 556 | 554
2019-06-09 19:30 | 551 | 548
2019-06-09 20:00 | 551 | 549
2019-06-09 20:30 | 552 | 549
2019-06-09 21:00 | 539 | 535
2019-06-09 21:30 | 525 | 520
2019-06-09 22:00 | 508 | 502
2019-06-09 22:30 | 494 | 490
2019-06-09 23:00 | 485 | 480
2019-06-09 23:30 | 465 | 458
2019-06-10 | 441 | 434
2019-06-10 00:30 | 393 | 383
2019-06-10 01:00 | 365 | 352
2019-06-10 01:30 | 363 | 348
2019-06-10 02:00 | 357 | 342
2019-06-10 02:30 | 337 | 321
2019-06-10 03:00 | 325 | 309
2019-06-10 03:30 | 332 | 315
2019-06-10 04:00 | 346 | 329
2019-06-10 04:30 | 359 | 343
2019-06-10 05:00 | 381 | 367
2019-06-10 05:30 | 411 | 401
2019-06-10 06:00 | 432 | 426
2019-06-10 06:30 | 480 | 477
2019-06-10 07:00 | 526 | 524
2019-06-10 07:30 | 549 | 547
2019-06-10 08:00 | 541 | 537
2019-06-10 08:30 | 518 | 514
2019-06-10 09:00 | 496 | 492
2019-06-10 09:30 | 482 | 477
2019-06-10 10:00 | 474 | 468
2019-06-10 10:30 | 464 | 459
2019-06-10 11:00 | 456 | 453
2019-06-10 11:30 | 433 | 431
2019-06-10 12:00 | 425 | 425
2019-06-10 12:30 | 427 | 426
2019-06-10 13:00 | 432 | 431
2019-06-10 13:30 | 442 | 440
2019-06-10 14:00 | 461 | 460
2019-06-10 14:30 | 474 | 473
2019-06-10 15:00 | 482 | 481
2019-06-10 15:30 | 500 | 499
2019-06-10 16:00 | 500 | 500
2019-06-10 16:30 | 520 | 519
2019-06-10 17:00 | 559 | 558
2019-06-10 17:30 | 589 | 588
2019-06-10 18:00 | 598 | 597
2019-06-10 18:30 | 593 | 592
2019-06-10 19:00 | 595 | 593
2019-06-10 19:30 | 589 | 587
2019-06-10 20:00 | 586 | 583
2019-06-10 20:30 | 584 | 582
2019-06-10 21:00 | 560 | 557
2019-06-10 21:30 | 540 | 537
2019-06-10 22:00 | 526 | 524
2019-06-10 22:30 | 517 | 514
2019-06-10 23:00 | 503 | 499
2019-06-10 23:30 | 486 | 481
2019-06-11 | 462 | 456
2019-06-11 00:30 | 431 | 423
2019-06-11 01:00 | 416 | 406
2019-06-11 01:30 | 402 | 390
2019-06-11 02:00 | 395 | 382
2019-06-11 02:30 | 386 | 373
2019-06-11 03:00 | 366 | 353
2019-06-11 03:30 | 363 | 349
2019-06-11 04:00 | 359 | 347
2019-06-11 04:30 | 366 | 354
2019-06-11 05:00 | 378 | 368
2019-06-11 05:30 | 411 | 403
2019-06-11 06:00 | 460 | 454
2019-06-11 06:30 | 512 | 509
2019-06-11 07:00 | 564 | 563
2019-06-11 07:30 | 581 | 577
2019-06-11 08:00 | 571 | 568
2019-06-11 08:30 | 546 | 541
2019-06-11 09:00 | 520 | 514
2019-06-11 09:30 | 502 | 499
2019-06-11 10:00 | 498 | 494
2019-06-11 10:30 | 492 | 487
2019-06-11 11:00 | 487 | 482
2019-06-11 11:30 | 465 | 461
2019-06-11 12:00 | 460 | 455
2019-06-11 12:30 | 459 | 455
2019-06-11 13:00 | 458 | 455
2019-06-11 13:30 | 461 | 458
2019-06-11 14:00 | 470 | 467
2019-06-11 14:30 | 488 | 485
2019-06-11 15:00 | 492 | 489
2019-06-11 15:30 | 504 | 501
2019-06-11 16:00 | 528 | 526
2019-06-11 16:30 | 546 | 544
2019-06-11 17:00 | 575 | 573
2019-06-11 17:30 | 592 | 591
2019-06-11 18:00 | 603 | 603
2019-06-11 18:30 | 597 | 596
2019-06-11 19:00 | 594 | 593
2019-06-11 19:30 | 579 | 578
2019-06-11 20:00 | 575 | 574
2019-06-11 20:30 | 572 | 571
2019-06-11 21:00 | 557 | 555
2019-06-11 21:30 | 535 | 532
2019-06-11 22:00 | 505 | 502
2019-06-11 22:30 | 497 | 494
2019-06-11 23:00 | 489 | 485
2019-06-11 23:30 | 471 | 466
2019-06-12 | 438 | 431
2019-06-12 00:30 | 403 | 392
2019-06-12 01:00 | 376 | 364
2019-06-12 01:30 | 366 | 352
2019-06-12 02:00 | 357 | 341
2019-06-12 02:30 | 349 | 332
2019-06-12 03:00 | 348 | 331
2019-06-12 03:30 | 349 | 333
2019-06-12 04:00 | 358 | 342
2019-06-12 04:30 | 362 | 347
2019-06-12 05:00 | 367 | 354
2019-06-12 05:30 | 388 | 378
2019-06-12 06:00 | 422 | 415
2019-06-12 06:30 | 480 | 477
2019-06-12 07:00 | 539 | 538
2019-06-12 07:30 | 561 | 559
2019-06-12 08:00 | 563 | 561
2019-06-12 08:30 | 552 | 548
2019-06-12 09:00 | 531 | 526
2019-06-12 09:30 | 524 | 520
2019-06-12 10:00 | 512 | 507
2019-06-12 10:30 | 512 | 506
2019-06-12 11:00 | 518 | 514
2019-06-12 11:30 | 520 | 516
2019-06-12 12:00 | 519 | 515
2019-06-12 12:30 | 512 | 509
2019-06-12 13:00 | 504 | 500
2019-06-12 13:30 | 497 | 494
2019-06-12 14:00 | 498 | 495
2019-06-12 14:30 | 492 | 489
2019-06-12 15:00 | 494 | 491
2019-06-12 15:30 | 500 | 498
2019-06-12 16:00 | 516 | 513
2019-06-12 16:30 | 537 | 535
2019-06-12 17:00 | 576 | 574
2019-06-12 17:30 | 610 | 608
2019-06-12 18:00 | 622 | 621
2019-06-12 18:30 | 622 | 620
2019-06-12 19:00 | 617 | 615
2019-06-12 19:30 | 604 | 602
2019-06-12 20:00 | 597 | 594
2019-06-12 20:30 | 594 | 590
2019-06-12 21:00 | 581 | 577
2019-06-12 21:30 | 563 | 558
2019-06-12 22:00 | 538 | 533
2019-06-12 22:30 | 535 | 531
2019-06-12 23:00 | 526 | 521
2019-06-12 23:30 | 508 | 503
2019-06-13 | 479 | 473
2019-06-13 00:30 | 432 | 423
2019-06-13 01:00 | 405 | 394
2019-06-13 01:30 | 378 | 365
2019-06-13 02:00 | 358 | 345
2019-06-13 02:30 | 358 | 343
2019-06-13 03:00 | 357 | 339
2019-06-13 03:30 | 357 | 341
2019-06-13 04:00 | 359 | 344
2019-06-13 04:30 | 366 | 351
2019-06-13 05:00 | 370 | 357
2019-06-13 05:30 | 393 | 383
2019-06-13 06:00 | 419 | 413
2019-06-13 06:30 | 481 | 479
2019-06-13 07:00 | 550 | 548
2019-06-13 07:30 | 581 | 573
2019-06-13 08:00 | 575 | 567
2019-06-13 08:30 | 556 | 548
2019-06-13 09:00 | 551 | 543
2019-06-13 09:30 | 542 | 533
2019-06-13 10:00 | 531 | 521
2019-06-13 10:30 | 549 | 539
2019-06-13 11:00 | 526 | 517
2019-06-13 11:30 | 499 | 489
2019-06-13 12:00 | 485 | 480
2019-06-13 12:30 | 507 | 505
2019-06-13 13:00 | 513 | 511
2019-06-13 13:30 | 523 | 522
2019-06-13 14:00 | 516 | 514
2019-06-13 14:30 | 512 | 511
2019-06-13 15:00 | 519 | 517
2019-06-13 15:30 | 530 | 529
2019-06-13 16:00 | 559 | 557
2019-06-13 16:30 | 569 | 566
2019-06-13 17:00 | 587 | 584
2019-06-13 17:30 | 611 | 609
2019-06-13 18:00 | 629 | 626
2019-06-13 18:30 | 617 | 614
2019-06-13 19:00 | 611 | 608
2019-06-13 19:30 | 604 | 600
2019-06-13 20:00 | 602 | 598
2019-06-13 20:30 | 595 | 593
2019-06-13 21:00 | 582 | 580
2019-06-13 21:30 | 552 | 551
2019-06-13 22:00 | 539 | 537
2019-06-13 22:30 | 541 | 538
2019-06-13 23:00 | 528 | 525
2019-06-13 23:30 | 509 | 505
2019-06-14 | 479 | 474
2019-06-14 00:30 | 442 | 434
2019-06-14 01:00 | 412 | 402
2019-06-14 01:30 | 394 | 382
2019-06-14 02:00 | 380 | 367
2019-06-14 02:30 | 367 | 355
2019-06-14 03:00 | 355 | 342
2019-06-14 03:30 | 347 | 333
2019-06-14 04:00 | 341 | 326
2019-06-14 04:30 | 344 | 330
2019-06-14 05:00 | 350 | 338
2019-06-14 05:30 | 387 | 377
2019-06-14 06:00 | 429 | 422
2019-06-14 06:30 | 490 | 486
2019-06-14 07:00 | 551 | 549
2019-06-14 07:30 | 582 | 576
2019-06-14 08:00 | 592 | 582
2019-06-14 08:30 | 582 | 572
2019-06-14 09:00 | 551 | 539
2019-06-14 09:30 | 536 | 523
2019-06-14 10:00 | 529 | 521
2019-06-14 10:30 | 506 | 502
2019-06-14 11:00 | 497 | 494
2019-06-14 11:30 | 489 | 486
2019-06-14 12:00 | 481 | 478
2019-06-14 12:30 | 474 | 471
2019-06-14 13:00 | 487 | 485
2019-06-14 13:30 | 493 | 491
2019-06-14 14:00 | 508 | 506
2019-06-14 14:30 | 506 | 504
2019-06-14 15:00 | 513 | 511
2019-06-14 15:30 | 530 | 528
2019-06-14 16:00 | 562 | 560
2019-06-14 16:30 | 574 | 572
2019-06-14 17:00 | 602 | 595
2019-06-14 17:30 | 605 | 599
2019-06-14 18:00 | 612 | 606
2019-06-14 18:30 | 603 | 595
2019-06-14 19:00 | 588 | 579
2019-06-14 19:30 | 583 | 573
2019-06-14 20:00 | 577 | 574
2019-06-14 20:30 | 574 | 570
2019-06-14 21:00 | 554 | 551
2019-06-14 21:30 | 540 | 537
2019-06-14 22:00 | 523 | 519
2019-06-14 22:30 | 525 | 521
2019-06-14 23:00 | 517 | 512
2019-06-14 23:30 | 502 | 496
2019-06-15 | 491 | 482
2019-06-15 00:30 | 469 | 457
2019-06-15 01:00 | 450 | 435
2019-06-15 01:30 | 442 | 426
2019-06-15 02:00 | 430 | 413
2019-06-15 02:30 | 419 | 401
2019-06-15 03:00 | 413 | 393
2019-06-15 03:30 | 407 | 386
2019-06-15 04:00 | 396 | 375
2019-06-15 04:30 | 392 | 369
2019-06-15 05:00 | 389 | 368
2019-06-15 05:30 | 408 | 389
2019-06-15 06:00 | 419 | 400
2019-06-15 06:30 | 446 | 429
2019-06-15 07:00 | 472 | 455
2019-06-15 07:30 | 492 | 479
2019-06-15 08:00 | 483 | 471
2019-06-15 08:30 | 487 | 476
2019-06-15 09:00 | 481 | 471
2019-06-15 09:30 | 484 | 475
2019-06-15 10:00 | 482 | 473
2019-06-15 10:30 | 482 | 473
2019-06-15 11:00 | 479 | 470
2019-06-15 11:30 | 464 | 454
2019-06-15 12:00 | 454 | 443
2019-06-15 12:30 | 453 | 442
2019-06-15 13:00 | 459 | 449
2019-06-15 13:30 | 469 | 460
2019-06-15 14:00 | 472 | 463
2019-06-15 14:30 | 479 | 470
2019-06-15 15:00 | 471 | 463
2019-06-15 15:30 | 479 | 471
2019-06-15 16:00 | 494 | 487
2019-06-15 16:30 | 525 | 518
2019-06-15 17:00 | 549 | 544
2019-06-15 17:30 | 574 | 570
2019-06-15 18:00 | 572 | 569
2019-06-15 18:30 | 567 | 564
2019-06-15 19:00 | 567 | 563
2019-06-15 19:30 | 550 | 546
2019-06-15 20:00 | 550 | 546
2019-06-15 20:30 | 557 | 552
2019-06-15 21:00 | 545 | 541
2019-06-15 21:30 | 531 | 526
2019-06-15 22:00 | 514 | 508
2019-06-15 22:30 | 510 | 504
2019-06-15 23:00 | 510 | 502
2019-06-15 23:30 | 495 | 486
2019-06-16 | 468 | 457
2019-06-16 00:30 | 437 | 423
2019-06-16 01:00 | 420 | 403
2019-06-16 01:30 | 408 | 390
2019-06-16 02:00 | 402 | 383
2019-06-16 02:30 | 391 | 372
2019-06-16 03:00 | 385 | 360
2019-06-16 03:30 | 376 | 347
2019-06-16 04:00 | 378 | 349
2019-06-16 04:30 | 375 | 346
2019-06-16 05:00 | 373 | 344
2019-06-16 05:30 | 376 | 349
2019-06-16 06:00 | 378 | 352
2019-06-16 06:30 | 400 | 375
2019-06-16 07:00 | 417 | 391
2019-06-16 07:30 | 441 | 417
2019-06-16 08:00 | 473 | 453
2019-06-16 08:30 | 503 | 487
2019-06-16 09:00 | 518 | 505
2019-06-16 09:30 | 546 | 534
2019-06-16 10:00 | 545 | 536
2019-06-16 10:30 | 549 | 541
2019-06-16 11:00 | 540 | 531
2019-06-16 11:30 | 515 | 505
2019-06-16 12:00 | 494 | 482
2019-06-16 12:30 | 495 | 483
2019-06-16 13:00 | 488 | 476
2019-06-16 13:30 | 498 | 487
2019-06-16 14:00 | 507 | 496
2019-06-16 14:30 | 522 | 511
2019-06-16 15:00 | 532 | 523
2019-06-16 15:30 | 541 | 533
2019-06-16 16:00 | 559 | 550
2019-06-16 16:30 | 569 | 559
2019-06-16 17:00 | 593 | 584
2019-06-16 17:30 | 627 | 613
2019-06-16 18:00 | 635 | 620
2019-06-16 18:30 | 629 | 614
2019-06-16 19:00 | 620 | 604
2019-06-16 19:30 | 597 | 579
2019-06-16 20:00 | 591 | 572
2019-06-16 20:30 | 589 | 569
2019-06-16 21:00 | 574 | 551
2019-06-16 21:30 | 558 | 535
2019-06-16 22:00 | 535 | 525
2019-06-16 22:30 | 524 | 514
2019-06-16 23:00 | 515 | 504
2019-06-16 23:30 | 500 | 487
2019-06-17 | 467 | 451
2019-06-17 00:30 | 432 | 412
2019-06-17 01:00 | 411 | 390
2019-06-17 01:30 | 395 | 371
2019-06-17 02:00 | 390 | 363
2019-06-17 02:30 | 381 | 354
2019-06-17 03:00 | 385 | 358
2019-06-17 03:30 | 385 | 358
2019-06-17 04:00 | 382 | 355
2019-06-17 04:30 | 381 | 356
2019-06-17 05:00 | 390 | 367
2019-06-17 05:30 | 410 | 391
2019-06-17 06:00 | 431 | 418
2019-06-17 06:30 | 492 | 481
2019-06-17 07:00 | 543 | 529
2019-06-17 07:30 | 580 | 565
2019-06-17 08:00 | 593 | 576
2019-06-17 08:30 | 574 | 556
2019-06-17 09:00 | 546 | 524
2019-06-17 09:30 | 526 | 504
2019-06-17 10:00 | 506 | 495
2019-06-17 10:30 | 495 | 483
2019-06-17 11:00 | 487 | 475
2019-06-17 11:30 | 476 | 464
2019-06-17 12:00 | 470 | 457
2019-06-17 12:30 | 473 | 460
2019-06-17 13:00 | 474 | 462
2019-06-17 13:30 | 484 | 472
2019-06-17 14:00 | 506 | 494
2019-06-17 14:30 | 517 | 505
2019-06-17 15:00 | 528 | 519
2019-06-17 15:30 | 541 | 532
2019-06-17 16:00 | 569 | 561
2019-06-17 16:30 | 595 | 585
2019-06-17 17:00 | 625 | 615
2019-06-17 17:30 | 659 | 644
2019-06-17 18:00 | 678 | 662
2019-06-17 18:30 | 683 | 666
2019-06-17 19:00 | 672 | 654
2019-06-17 19:30 | 668 | 648
2019-06-17 20:00 | 648 | 631
2019-06-17 20:30 | 641 | 627
2019-06-17 21:00 | 616 | 609
2019-06-17 21:30 | 594 | 589
2019-06-17 22:00 | 569 | 562
2019-06-17 22:30 | 553 | 544
2019-06-17 23:00 | 533 | 525
2019-06-17 23:30 | 510 | 502
2019-06-18 | 484 | 473
2019-06-18 00:30 | 446 | 431
2019-06-18 01:00 | 426 | 408
2019-06-18 01:30 | 410 | 390
2019-06-18 02:00 | 391 | 370
2019-06-18 02:30 | 389 | 367
2019-06-18 03:00 | 387 | 364
2019-06-18 03:30 | 385 | 362
2019-06-18 04:00 | 372 | 349
2019-06-18 04:30 | 370 | 347
2019-06-18 05:00 | 393 | 373
2019-06-18 05:30 | 418 | 404
2019-06-18 06:00 | 460 | 450
2019-06-18 06:30 | 537 | 521
2019-06-18 07:00 | 603 | 589
2019-06-18 07:30 | 646 | 635
2019-06-18 08:00 | 637 | 623
2019-06-18 08:30 | 617 | 599
2019-06-18 09:00 | 579 | 564
2019-06-18 09:30 | 549 | 535
2019-06-18 10:00 | 521 | 507
2019-06-18 10:30 | 510 | 497
2019-06-18 11:00 | 496 | 484
2019-06-18 11:30 | 466 | 462
2019-06-18 12:00 | 459 | 455
2019-06-18 12:30 | 458 | 455
2019-06-18 13:00 | 457 | 454
2019-06-18 13:30 | 466 | 463
2019-06-18 14:00 | 477 | 474
2019-06-18 14:30 | 488 | 484
2019-06-18 15:00 | 500 | 496
2019-06-18 15:30 | 516 | 513
2019-06-18 16:00 | 535 | 532
2019-06-18 16:30 | 565 | 563
2019-06-18 17:00 | 596 | 592
2019-06-18 17:30 | 629 | 625
2019-06-18 18:00 | 650 | 644
2019-06-18 18:30 | 641 | 634
2019-06-18 19:00 | 648 | 641
2019-06-18 19:30 | 640 | 632
2019-06-18 20:00 | 634 | 625
2019-06-18 20:30 | 632 | 625
2019-06-18 21:00 | 608 | 601
2019-06-18 21:30 | 584 | 575
2019-06-18 22:00 | 563 | 552
2019-06-18 22:30 | 542 | 534
2019-06-18 23:00 | 511 | 503
2019-06-18 23:30 | 488 | 479
2019-06-19 | 454 | 442
2019-06-19 00:30 | 431 | 416
2019-06-19 01:00 | 423 | 405
2019-06-19 01:30 | 413 | 394
2019-06-19 02:00 | 416 | 396
2019-06-19 02:30 | 410 | 389
2019-06-19 03:00 | 405 | 383
2019-06-19 03:30 | 407 | 385
2019-06-19 04:00 | 408 | 388
2019-06-19 04:30 | 408 | 389
2019-06-19 05:00 | 411 | 394
2019-06-19 05:30 | 445 | 433
2019-06-19 06:00 | 466 | 458
2019-06-19 06:30 | 538 | 528
2019-06-19 07:00 | 609 | 596
2019-06-19 07:30 | 663 | 652
2019-06-19 08:00 | 667 | 653
2019-06-19 08:30 | 622 | 604
2019-06-19 09:00 | 564 | 552
2019-06-19 09:30 | 516 | 512
2019-06-19 10:00 | 494 | 491
2019-06-19 10:30 | 474 | 470
2019-06-19 11:00 | 462 | 457
2019-06-19 11:30 | 452 | 448
2019-06-19 12:00 | 449 | 445
2019-06-19 12:30 | 444 | 440
2019-06-19 13:00 | 455 | 450
2019-06-19 13:30 | 470 | 467
2019-06-19 14:00 | 489 | 486
2019-06-19 14:30 | 503 | 500
2019-06-19 15:00 | 520 | 518
2019-06-19 15:30 | 553 | 551
2019-06-19 16:00 | 565 | 564
2019-06-19 16:30 | 592 | 591
2019-06-19 17:00 | 624 | 617
2019-06-19 17:30 | 666 | 659
2019-06-19 18:00 | 692 | 688
2019-06-19 18:30 | 691 | 686
2019-06-19 19:00 | 693 | 687
2019-06-19 19:30 | 693 | 686
2019-06-19 20:00 | 689 | 680
2019-06-19 20:30 | 682 | 672
2019-06-19 21:00 | 653 | 649
2019-06-19 21:30 | 622 | 619
2019-06-19 22:00 | 595 | 593
2019-06-19 22:30 | 568 | 565
2019-06-19 23:00 | 537 | 533
2019-06-19 23:30 | 513 | 506
2019-06-20 | 482 | 469
2019-06-20 00:30 | 444 | 427
2019-06-20 01:00 | 422 | 401
2019-06-20 01:30 | 419 | 395
2019-06-20 02:00 | 423 | 400
2019-06-20 02:30 | 413 | 388
2019-06-20 03:00 | 408 | 382
2019-06-20 03:30 | 407 | 380
2019-06-20 04:00 | 411 | 385
2019-06-20 04:30 | 413 | 389
2019-06-20 05:00 | 421 | 401
2019-06-20 05:30 | 440 | 427
2019-06-20 06:00 | 459 | 452
2019-06-20 06:30 | 519 | 517
2019-06-20 07:00 | 584 | 577
2019-06-20 07:30 | 630 | 626
2019-06-20 08:00 | 634 | 631
2019-06-20 08:30 | 603 | 598
2019-06-20 09:00 | 581 | 575
2019-06-20 09:30 | 564 | 557
2019-06-20 10:00 | 559 | 552
2019-06-20 10:30 | 553 | 545
2019-06-20 11:00 | 546 | 539
2019-06-20 11:30 | 544 | 532
2019-06-20 12:00 | 549 | 537
2019-06-20 12:30 | 553 | 542
2019-06-20 13:00 | 542 | 532
2019-06-20 13:30 | 548 | 539
2019-06-20 14:00 | 565 | 557
2019-06-20 14:30 | 582 | 575
2019-06-20 15:00 | 593 | 586
2019-06-20 15:30 | 591 | 583
2019-06-20 16:00 | 593 | 586
2019-06-20 16:30 | 605 | 600
2019-06-20 17:00 | 642 | 637
2019-06-20 17:30 | 682 | 676
2019-06-20 18:00 | 702 | 695
2019-06-20 18:30 | 697 | 689
2019-06-20 19:00 | 697 | 690
2019-06-20 19:30 | 686 | 679
2019-06-20 20:00 | 678 | 671
2019-06-20 20:30 | 675 | 665
2019-06-20 21:00 | 651 | 642
2019-06-20 21:30 | 624 | 615
2019-06-20 22:00 | 588 | 579
2019-06-20 22:30 | 570 | 566
2019-06-20 23:00 | 542 | 537
2019-06-20 23:30 | 509 | 502
2019-06-21 | 477 | 465
2019-06-21 00:30 | 447 | 429
2019-06-21 01:00 | 426 | 406
2019-06-21 01:30 | 419 | 398
2019-06-21 02:00 | 425 | 403
2019-06-21 02:30 | 416 | 394
2019-06-21 03:00 | 411 | 388
2019-06-21 03:30 | 413 | 390
2019-06-21 04:00 | 414 | 391
2019-06-21 04:30 | 415 | 394
2019-06-21 05:00 | 425 | 405
2019-06-21 05:30 | 444 | 428
2019-06-21 06:00 | 466 | 454
2019-06-21 06:30 | 523 | 516
2019-06-21 07:00 | 589 | 574
2019-06-21 07:30 | 626 | 613
2019-06-21 08:00 | 641 | 628
2019-06-21 08:30 | 635 | 622
2019-06-21 09:00 | 607 | 592
2019-06-21 09:30 | 581 | 565
2019-06-21 10:00 | 558 | 549
2019-06-21 10:30 | 536 | 529
2019-06-21 11:00 | 519 | 511
2019-06-21 11:30 | 514 | 507
2019-06-21 12:00 | 518 | 511
2019-06-21 12:30 | 518 | 511
2019-06-21 13:00 | 529 | 521
2019-06-21 13:30 | 531 | 524
2019-06-21 14:00 | 528 | 521
2019-06-21 14:30 | 534 | 527
2019-06-21 15:00 | 535 | 528
2019-06-21 15:30 | 541 | 534
2019-06-21 16:00 | 557 | 551
2019-06-21 16:30 | 589 | 583
2019-06-21 17:00 | 631 | 622
2019-06-21 17:30 | 654 | 642
2019-06-21 18:00 | 671 | 655
2019-06-21 18:30 | 666 | 649
2019-06-21 19:00 | 662 | 645
2019-06-21 19:30 | 646 | 627
2019-06-21 20:00 | 650 | 629
2019-06-21 20:30 | 647 | 625
2019-06-21 21:00 | 636 | 611
2019-06-21 21:30 | 620 | 595
2019-06-21 22:00 | 589 | 577
2019-06-21 22:30 | 568 | 560
2019-06-21 23:00 | 556 | 547
2019-06-21 23:30 | 535 | 524
2019-06-22 | 506 | 492
2019-06-22 00:30 | 465 | 447
2019-06-22 01:00 | 448 | 428
2019-06-22 01:30 | 436 | 413
2019-06-22 02:00 | 428 | 406
2019-06-22 02:30 | 423 | 400
2019-06-22 03:00 | 417 | 394
2019-06-22 03:30 | 408 | 385
2019-06-22 04:00 | 402 | 378
2019-06-22 04:30 | 406 | 383
2019-06-22 05:00 | 408 | 386
2019-06-22 05:30 | 415 | 395
2019-06-22 06:00 | 425 | 407
2019-06-22 06:30 | 450 | 435
2019-06-22 07:00 | 479 | 466
2019-06-22 07:30 | 521 | 510
2019-06-22 08:00 | 556 | 542
2019-06-22 08:30 | 565 | 545
2019-06-22 09:00 | 555 | 534
2019-06-22 09:30 | 543 | 522
2019-06-22 10:00 | 508 | 497
2019-06-22 10:30 | 489 | 478
2019-06-22 11:00 | 471 | 459
2019-06-22 11:30 | 455 | 441
2019-06-22 12:00 | 442 | 427
2019-06-22 12:30 | 420 | 403
2019-06-22 13:00 | 430 | 413
2019-06-22 13:30 | 435 | 418
2019-06-22 14:00 | 440 | 423
2019-06-22 14:30 | 464 | 450
2019-06-22 15:00 | 471 | 457
2019-06-22 15:30 | 487 | 473
2019-06-22 16:00 | 507 | 495
2019-06-22 16:30 | 542 | 530
2019-06-22 17:00 | 590 | 572
2019-06-22 17:30 | 621 | 608
2019-06-22 18:00 | 634 | 621
2019-06-22 18:30 | 632 | 618
2019-06-22 19:00 | 629 | 616
2019-06-22 19:30 | 620 | 606
2019-06-22 20:00 | 619 | 607
2019-06-22 20:30 | 618 | 606
2019-06-22 21:00 | 606 | 593
2019-06-22 21:30 | 591 | 577
2019-06-22 22:00 | 565 | 560
2019-06-22 22:30 | 548 | 541
2019-06-22 23:00 | 523 | 516
2019-06-22 23:30 | 506 | 496
2019-06-23 | 475 | 462
2019-06-23 00:30 | 448 | 432
2019-06-23 01:00 | 426 | 408
2019-06-23 01:30 | 417 | 398
2019-06-23 02:00 | 412 | 390
2019-06-23 02:30 | 409 | 387
2019-06-23 03:00 | 403 | 380
2019-06-23 03:30 | 399 | 375
2019-06-23 04:00 | 395 | 370
2019-06-23 04:30 | 388 | 364
2019-06-23 05:00 | 390 | 367
2019-06-23 05:30 | 397 | 375
2019-06-23 06:00 | 406 | 385
2019-06-23 06:30 | 433 | 415
2019-06-23 07:00 | 464 | 448
2019-06-23 07:30 | 506 | 493
2019-06-23 08:00 | 521 | 509
2019-06-23 08:30 | 539 | 529
2019-06-23 09:00 | 542 | 531
2019-06-23 09:30 | 541 | 531
2019-06-23 10:00 | 521 | 511
2019-06-23 10:30 | 498 | 487
2019-06-23 11:00 | 470 | 456
2019-06-23 11:30 | 452 | 437
2019-06-23 12:00 | 435 | 418
2019-06-23 12:30 | 432 | 414
2019-06-23 13:00 | 435 | 418
2019-06-23 13:30 | 444 | 429
2019-06-23 14:00 | 457 | 443
2019-06-23 14:30 | 462 | 448
2019-06-23 15:00 | 486 | 473
2019-06-23 15:30 | 507 | 496
2019-06-23 16:00 | 530 | 519
2019-06-23 16:30 | 558 | 544
2019-06-23 17:00 | 599 | 583
2019-06-23 17:30 | 624 | 612
2019-06-23 18:00 | 638 | 626
2019-06-23 18:30 | 642 | 629
2019-06-23 19:00 | 649 | 636
2019-06-23 19:30 | 641 | 627
2019-06-23 20:00 | 639 | 624
2019-06-23 20:30 | 633 | 618
2019-06-23 21:00 | 611 | 596
2019-06-23 21:30 | 587 | 575
2019-06-23 22:00 | 553 | 545
2019-06-23 22:30 | 523 | 514
2019-06-23 23:00 | 501 | 490
2019-06-23 23:30 | 477 | 464
2019-06-24 | 446 | 429
2019-06-24 00:30 | 413 | 392
2019-06-24 01:00 | 414 | 392
2019-06-24 01:30 | 413 | 387
2019-06-24 02:00 | 408 | 381
2019-06-24 02:30 | 402 | 375
2019-06-24 03:00 | 395 | 366
2019-06-24 03:30 | 393 | 365
2019-06-24 04:00 | 392 | 365
2019-06-24 04:30 | 398 | 373
2019-06-24 05:00 | 413 | 391
2019-06-24 05:30 | 436 | 419
2019-06-24 06:00 | 452 | 441
2019-06-24 06:30 | 516 | 510
2019-06-24 07:00 | 589 | 583
2019-06-24 07:30 | 631 | 625
2019-06-24 08:00 | 643 | 636
2019-06-24 08:30 | 629 | 620
2019-06-24 09:00 | 594 | 587
2019-06-24 09:30 | 573 | 566
2019-06-24 10:00 | 549 | 541
2019-06-24 10:30 | 526 | 520
2019-06-24 11:00 | 518 | 512
2019-06-24 11:30 | 500 | 493
2019-06-24 12:00 | 495 | 488
2019-06-24 12:30 | 506 | 499
2019-06-24 13:00 | 514 | 507
2019-06-24 13:30 | 504 | 498
2019-06-24 14:00 | 507 | 501
2019-06-24 14:30 | 523 | 517
2019-06-24 15:00 | 537 | 532
2019-06-24 15:30 | 546 | 541
2019-06-24 16:00 | 567 | 563
2019-06-24 16:30 | 602 | 598
2019-06-24 17:00 | 663 | 656
2019-06-24 17:30 | 695 | 688
2019-06-24 18:00 | 721 | 714
2019-06-24 18:30 | 717 | 709
2019-06-24 19:00 | 717 | 710
2019-06-24 19:30 | 706 | 696
2019-06-24 20:00 | 706 | 694
2019-06-24 20:30 | 697 | 687
2019-06-24 21:00 | 667 | 657
2019-06-24 21:30 | 621 | 616
2019-06-24 22:00 | 588 | 581
2019-06-24 22:30 | 574 | 565
2019-06-24 23:00 | 546 | 536
2019-06-24 23:30 | 511 | 502
2019-06-25 | 491 | 480
2019-06-25 00:30 | 463 | 449
2019-06-25 01:00 | 442 | 426
2019-06-25 01:30 | 436 | 416
2019-06-25 02:00 | 428 | 406
2019-06-25 02:30 | 418 | 396
2019-06-25 03:00 | 411 | 387
2019-06-25 03:30 | 407 | 381
2019-06-25 04:00 | 410 | 385
2019-06-25 04:30 | 410 | 386
2019-06-25 05:00 | 413 | 392
2019-06-25 05:30 | 426 | 409
2019-06-25 06:00 | 447 | 436
2019-06-25 06:30 | 521 | 515
2019-06-25 07:00 | 581 | 576
2019-06-25 07:30 | 638 | 634
2019-06-25 08:00 | 649 | 645
2019-06-25 08:30 | 633 | 628
2019-06-25 09:00 | 601 | 596
2019-06-25 09:30 | 588 | 582
2019-06-25 10:00 | 572 | 566
2019-06-25 10:30 | 562 | 556
2019-06-25 11:00 | 565 | 559
2019-06-25 11:30 | 563 | 557
2019-06-25 12:00 | 558 | 552
2019-06-25 12:30 | 574 | 569
2019-06-25 13:00 | 572 | 567
2019-06-25 13:30 | 572 | 567
2019-06-25 14:00 | 591 | 586
2019-06-25 14:30 | 583 | 578
2019-06-25 15:00 | 589 | 584
2019-06-25 15:30 | 588 | 583
2019-06-25 16:00 | 598 | 594
2019-06-25 16:30 | 627 | 624
2019-06-25 17:00 | 669 | 661
2019-06-25 17:30 | 705 | 695
2019-06-25 18:00 | 735 | 725
2019-06-25 18:30 | 734 | 722
2019-06-25 19:00 | 731 | 719
2019-06-25 19:30 | 704 | 699
2019-06-25 20:00 | 690 | 684
2019-06-25 20:30 | 680 | 673
2019-06-25 21:00 | 656 | 648
2019-06-25 21:30 | 624 | 616
2019-06-25 22:00 | 576 | 571
2019-06-25 22:30 | 564 | 557
2019-06-25 23:00 | 542 | 534
2019-06-25 23:30 | 520 | 511
2019-06-26 | 501 | 490
2019-06-26 00:30 | 462 | 449
2019-06-26 01:00 | 436 | 420
2019-06-26 01:30 | 422 | 403
2019-06-26 02:00 | 414 | 394
2019-06-26 02:30 | 408 | 387
2019-06-26 03:00 | 408 | 385
2019-06-26 03:30 | 404 | 380
2019-06-26 04:00 | 395 | 372
2019-06-26 04:30 | 398 | 376
2019-06-26 05:00 | 406 | 387
2019-06-26 05:30 | 429 | 414
2019-06-26 06:00 | 453 | 443
2019-06-26 06:30 | 503 | 496
2019-06-26 07:00 | 566 | 559
2019-06-26 07:30 | 608 | 599
2019-06-26 08:00 | 641 | 631
2019-06-26 08:30 | 641 | 632
2019-06-26 09:00 | 618 | 608
2019-06-26 09:30 | 607 | 597
2019-06-26 10:00 | 601 | 589
2019-06-26 10:30 | 602 | 589
2019-06-26 11:00 | 606 | 594
2019-06-26 11:30 | 612 | 601
2019-06-26 12:00 | 606 | 596
2019-06-26 12:30 | 608 | 596
2019-06-26 13:00 | 602 | 591
2019-06-26 13:30 | 600 | 589
2019-06-26 14:00 | 600 | 590
2019-06-26 14:30 | 596 | 585
2019-06-26 15:00 | 589 | 577
2019-06-26 15:30 | 596 | 584
2019-06-26 16:00 | 601 | 590
2019-06-26 16:30 | 623 | 613
2019-06-26 17:00 | 661 | 653
2019-06-26 17:30 | 699 | 691
2019-06-26 18:00 | 709 | 702
2019-06-26 18:30 | 689 | 681
2019-06-26 19:00 | 685 | 676
2019-06-26 19:30 | 665 | 655
2019-06-26 20:00 | 649 | 638
2019-06-26 20:30 | 639 | 628
2019-06-26 21:00 | 609 | 596
2019-06-26 21:30 | 575 | 564
2019-06-26 22:00 | 552 | 542
2019-06-26 22:30 | 524 | 519
2019-06-26 23:00 | 502 | 496
2019-06-26 23:30 | 473 | 465
2019-06-27 | 452 | 442
2019-06-27 00:30 | 436 | 423
2019-06-27 01:00 | 425 | 411
2019-06-27 01:30 | 412 | 395
2019-06-27 02:00 | 397 | 378
2019-06-27 02:30 | 381 | 361
2019-06-27 03:00 | 363 | 342
2019-06-27 03:30 | 363 | 342
2019-06-27 04:00 | 363 | 343
2019-06-27 04:30 | 364 | 345
2019-06-27 05:00 | 376 | 359
2019-06-27 05:30 | 395 | 381
2019-06-27 06:00 | 421 | 411
2019-06-27 06:30 | 494 | 489
2019-06-27 07:00 | 551 | 548
2019-06-27 07:30 | 598 | 595
2019-06-27 08:00 | 609 | 606
2019-06-27 08:30 | 580 | 577
2019-06-27 09:00 | 560 | 554
2019-06-27 09:30 | 566 | 560
2019-06-27 10:00 | 531 | 527
2019-06-27 10:30 | 505 | 503
2019-06-27 11:00 | 496 | 494
2019-06-27 11:30 | 488 | 487
2019-06-27 12:00 | 489 | 487
2019-06-27 12:30 | 485 | 483
2019-06-27 13:00 | 479 | 477
2019-06-27 13:30 | 488 | 486
2019-06-27 14:00 | 497 | 495
2019-06-27 14:30 | 488 | 487
2019-06-27 15:00 | 482 | 480
2019-06-27 15:30 | 487 | 486
2019-06-27 16:00 | 510 | 509
2019-06-27 16:30 | 558 | 556
2019-06-27 17:00 | 590 | 588
2019-06-27 17:30 | 630 | 628
2019-06-27 18:00 | 645 | 643
2019-06-27 18:30 | 640 | 638
2019-06-27 19:00 | 644 | 641
2019-06-27 19:30 | 637 | 634
2019-06-27 20:00 | 627 | 625
2019-06-27 20:30 | 622 | 619
2019-06-27 21:00 | 605 | 602
2019-06-27 21:30 | 576 | 573
2019-06-27 22:00 | 545 | 541
2019-06-27 22:30 | 519 | 514
2019-06-27 23:00 | 476 | 469
2019-06-27 23:30 | 450 | 445
2019-06-28 | 424 | 416
2019-06-28 00:30 | 396 | 385
2019-06-28 01:00 | 382 | 368
2019-06-28 01:30 | 372 | 354
2019-06-28 02:00 | 366 | 347
2019-06-28 02:30 | 357 | 334
2019-06-28 03:00 | 358 | 333
2019-06-28 03:30 | 356 | 330
2019-06-28 04:00 | 356 | 330
2019-06-28 04:30 | 361 | 337
2019-06-28 05:00 | 367 | 345
2019-06-28 05:30 | 383 | 364
2019-06-28 06:00 | 405 | 393
2019-06-28 06:30 | 461 | 454
2019-06-28 07:00 | 517 | 514
2019-06-28 07:30 | 544 | 542
2019-06-28 08:00 | 553 | 550
2019-06-28 08:30 | 550 | 547
2019-06-28 09:00 | 543 | 540
2019-06-28 09:30 | 533 | 530
2019-06-28 10:00 | 483 | 478
2019-06-28 10:30 | 472 | 467
2019-06-28 11:00 | 478 | 473
2019-06-28 11:30 | 459 | 453
2019-06-28 12:00 | 451 | 444
2019-06-28 12:30 | 463 | 456
2019-06-28 13:00 | 468 | 461
2019-06-28 13:30 | 483 | 477
2019-06-28 14:00 | 477 | 471
2019-06-28 14:30 | 466 | 460
2019-06-28 15:00 | 479 | 474
2019-06-28 15:30 | 477 | 471
2019-06-28 16:00 | 488 | 482
2019-06-28 16:30 | 508 | 503
2019-06-28 17:00 | 547 | 543
2019-06-28 17:30 | 579 | 577
2019-06-28 18:00 | 600 | 596
2019-06-28 18:30 | 595 | 589
2019-06-28 19:00 | 594 | 588
2019-06-28 19:30 | 581 | 575
2019-06-28 20:00 | 575 | 571
2019-06-28 20:30 | 572 | 566
2019-06-28 21:00 | 550 | 544
2019-06-28 21:30 | 519 | 514
2019-06-28 22:00 | 500 | 494
2019-06-28 22:30 | 491 | 484
2019-06-28 23:00 | 474 | 466
2019-06-28 23:30 | 456 | 446
2019-06-29 | 436 | 423
2019-06-29 00:30 | 405 | 388
2019-06-29 01:00 | 381 | 361
2019-06-29 01:30 | 367 | 345
2019-06-29 02:00 | 361 | 336
2019-06-29 02:30 | 354 | 323
2019-06-29 03:00 | 353 | 320
2019-06-29 03:30 | 341 | 311
2019-06-29 04:00 | 341 | 312
2019-06-29 04:30 | 335 | 306
2019-06-29 05:00 | 335 | 307
2019-06-29 05:30 | 351 | 326
2019-06-29 06:00 | 370 | 346
2019-06-29 06:30 | 380 | 360
2019-06-29 07:00 | 393 | 373
2019-06-29 07:30 | 420 | 404
2019-06-29 08:00 | 451 | 437
2019-06-29 08:30 | 477 | 464
2019-06-29 09:00 | 478 | 465
2019-06-29 09:30 | 471 | 458
2019-06-29 10:00 | 465 | 452
2019-06-29 10:30 | 463 | 450
2019-06-29 11:00 | 458 | 445
2019-06-29 11:30 | 442 | 428
2019-06-29 12:00 | 435 | 420
2019-06-29 12:30 | 432 | 417
2019-06-29 13:00 | 427 | 411
2019-06-29 13:30 | 430 | 414
2019-06-29 14:00 | 437 | 422
2019-06-29 14:30 | 430 | 415
2019-06-29 15:00 | 427 | 413
2019-06-29 15:30 | 439 | 426
2019-06-29 16:00 | 457 | 445
2019-06-29 16:30 | 483 | 472
2019-06-29 17:00 | 503 | 494
2019-06-29 17:30 | 519 | 512
2019-06-29 18:00 | 525 | 519
2019-06-29 18:30 | 521 | 515
2019-06-29 19:00 | 514 | 509
2019-06-29 19:30 | 506 | 500
2019-06-29 20:00 | 500 | 496
2019-06-29 20:30 | 498 | 494
2019-06-29 21:00 | 483 | 478
2019-06-29 21:30 | 467 | 461
2019-06-29 22:00 | 458 | 451
2019-06-29 22:30 | 450 | 440
2019-06-29 23:00 | 445 | 435
2019-06-29 23:30 | 430 | 418
2019-06-30 | 409 | 395
2019-06-30 00:30 | 377 | 360
2019-06-30 01:00 | 359 | 338
2019-06-30 01:30 | 354 | 327
2019-06-30 02:00 | 348 | 319
2019-06-30 02:30 | 346 | 315
2019-06-30 03:00 | 338 | 307
2019-06-30 03:30 | 336 | 306
2019-06-30 04:00 | 325 | 294
2019-06-30 04:30 | 327 | 296
2019-06-30 05:00 | 317 | 285
2019-06-30 05:30 | 338 | 310
2019-06-30 06:00 | 347 | 320
2019-06-30 06:30 | 356 | 332
2019-06-30 07:00 | 372 | 348
2019-06-30 07:30 | 388 | 366
2019-06-30 08:00 | 410 | 389
2019-06-30 08:30 | 429 | 410
2019-06-30 09:00 | 439 | 421
2019-06-30 09:30 | 440 | 424
2019-06-30 10:00 | 436 | 420
2019-06-30 10:30 | 420 | 404
2019-06-30 11:00 | 387 | 370
2019-06-30 11:30 | 377 | 359
2019-06-30 12:00 | 371 | 352
2019-06-30 12:30 | 374 | 356
2019-06-30 13:00 | 372 | 354
2019-06-30 13:30 | 376 | 358
2019-06-30 14:00 | 380 | 363
2019-06-30 14:30 | 393 | 378
2019-06-30 15:00 | 421 | 407
2019-06-30 15:30 | 431 | 417
2019-06-30 16:00 | 439 | 427
2019-06-30 16:30 | 471 | 459
2019-06-30 17:00 | 515 | 504
2019-06-30 17:30 | 544 | 535
2019-06-30 18:00 | 550 | 544
2019-06-30 18:30 | 545 | 538
2019-06-30 19:00 | 546 | 538
2019-06-30 19:30 | 545 | 536
2019-06-30 20:00 | 547 | 538
2019-06-30 20:30 | 546 | 537
2019-06-30 21:00 | 521 | 513
2019-06-30 21:30 | 491 | 484
2019-06-30 22:00 | 474 | 466
2019-06-30 22:30 | 452 | 444
2019-06-30 23:00 | 439 | 430
2019-06-30 23:30 | 440 | 429
2019-07-01 | 428 | 413
2019-07-01 00:30 | 393 | 375
2019-07-01 01:00 | 375 | 354
2019-07-01 01:30 | 367 | 345
2019-07-01 02:00 | 363 | 338
2019-07-01 02:30 | 359 | 333
2019-07-01 03:00 | 361 | 334
2019-07-01 03:30 | 358 | 332
2019-07-01 04:00 | 339 | 313
2019-07-01 04:30 | 330 | 305
2019-07-01 05:00 | 344 | 322
2019-07-01 05:30 | 368 | 350
2019-07-01 06:00 | 390 | 378
2019-07-01 06:30 | 447 | 441
2019-07-01 07:00 | 505 | 500
2019-07-01 07:30 | 543 | 539
2019-07-01 08:00 | 570 | 560
2019-07-01 08:30 | 578 | 569
2019-07-01 09:00 | 557 | 547
2019-07-01 09:30 | 525 | 514
2019-07-01 10:00 | 487 | 484
2019-07-01 10:30 | 478 | 475
2019-07-01 11:00 | 471 | 469
2019-07-01 11:30 | 454 | 452
2019-07-01 12:00 | 467 | 466
2019-07-01 12:30 | 490 | 489
2019-07-01 13:00 | 490 | 490
2019-07-01 13:30 | 478 | 478
2019-07-01 14:00 | 466 | 465
2019-07-01 14:30 | 475 | 474
2019-07-01 15:00 | 484 | 483
2019-07-01 15:30 | 514 | 513
2019-07-01 16:00 | 531 | 530
2019-07-01 16:30 | 558 | 557
2019-07-01 17:00 | 593 | 592
2019-07-01 17:30 | 617 | 615
2019-07-01 18:00 | 619 | 615
2019-07-01 18:30 | 606 | 601
2019-07-01 19:00 | 603 | 597
2019-07-01 19:30 | 586 | 585
2019-07-01 20:00 | 587 | 587
2019-07-01 20:30 | 579 | 578
2019-07-01 21:00 | 556 | 555
2019-07-01 21:30 | 527 | 526
2019-07-01 22:00 | 508 | 507
2019-07-01 22:30 | 487 | 485
2019-07-01 23:00 | 453 | 452
2019-07-01 23:30 | 435 | 432
2019-07-02 | 406 | 401
2019-07-02 00:30 | 373 | 366
2019-07-02 01:00 | 355 | 347
2019-07-02 01:30 | 346 | 336
2019-07-02 02:00 | 334 | 321
2019-07-02 02:30 | 326 | 312
2019-07-02 03:00 | 321 | 306
2019-07-02 03:30 | 321 | 305
2019-07-02 04:00 | 326 | 311
2019-07-02 04:30 | 323 | 309
2019-07-02 05:00 | 329 | 316
2019-07-02 05:30 | 351 | 341
2019-07-02 06:00 | 380 | 373
2019-07-02 06:30 | 443 | 440
2019-07-02 07:00 | 514 | 512
2019-07-02 07:30 | 554 | 552
2019-07-02 08:00 | 577 | 576
2019-07-02 08:30 | 573 | 571
2019-07-02 09:00 | 550 | 548
2019-07-02 09:30 | 526 | 524
2019-07-02 10:00 | 501 | 500
2019-07-02 10:30 | 478 | 477
2019-07-02 11:00 | 465 | 464
2019-07-02 11:30 | 447 | 446
2019-07-02 12:00 | 441 | 440
2019-07-02 12:30 | 442 | 441
2019-07-02 13:00 | 445 | 444
2019-07-02 13:30 | 454 | 453
2019-07-02 14:00 | 463 | 462
2019-07-02 14:30 | 479 | 478
2019-07-02 15:00 | 498 | 497
2019-07-02 15:30 | 513 | 512
2019-07-02 16:00 | 516 | 516
2019-07-02 16:30 | 520 | 519
2019-07-02 17:00 | 565 | 564
2019-07-02 17:30 | 614 | 613
2019-07-02 18:00 | 649 | 644
2019-07-02 18:30 | 637 | 632
2019-07-02 19:00 | 651 | 645
2019-07-02 19:30 | 633 | 625
2019-07-02 20:00 | 630 | 624
2019-07-02 20:30 | 611 | 605
2019-07-02 21:00 | 589 | 587
2019-07-02 21:30 | 573 | 571
2019-07-02 22:00 | 552 | 549
2019-07-02 22:30 | 538 | 536
2019-07-02 23:00 | 509 | 507
2019-07-02 23:30 | 481 | 477
2019-07-03 | 447 | 441
2019-07-03 00:30 | 406 | 399
2019-07-03 01:00 | 383 | 373
2019-07-03 01:30 | 365 | 354
2019-07-03 02:00 | 368 | 355
2019-07-03 02:30 | 366 | 352
2019-07-03 03:00 | 362 | 349
2019-07-03 03:30 | 362 | 348
2019-07-03 04:00 | 359 | 345
2019-07-03 04:30 | 353 | 340
2019-07-03 05:00 | 355 | 343
2019-07-03 05:30 | 383 | 374
2019-07-03 06:00 | 411 | 406
2019-07-03 06:30 | 480 | 478
2019-07-03 07:00 | 534 | 533
2019-07-03 07:30 | 570 | 569
2019-07-03 08:00 | 597 | 596
2019-07-03 08:30 | 589 | 588
2019-07-03 09:00 | 559 | 557
2019-07-03 09:30 | 527 | 525
2019-07-03 10:00 | 503 | 501
2019-07-03 10:30 | 495 | 493
2019-07-03 11:00 | 485 | 483
2019-07-03 11:30 | 477 | 476
2019-07-03 12:00 | 470 | 468
2019-07-03 12:30 | 460 | 459
2019-07-03 13:00 | 459 | 458
2019-07-03 13:30 | 455 | 455
2019-07-03 14:00 | 457 | 456
2019-07-03 14:30 | 470 | 469
2019-07-03 15:00 | 479 | 478
2019-07-03 15:30 | 486 | 486
2019-07-03 16:00 | 503 | 502
2019-07-03 16:30 | 540 | 539
2019-07-03 17:00 | 579 | 578
2019-07-03 17:30 | 623 | 618
2019-07-03 18:00 | 628 | 623
2019-07-03 18:30 | 619 | 613
2019-07-03 19:00 | 618 | 612
2019-07-03 19:30 | 611 | 604
2019-07-03 20:00 | 596 | 593
2019-07-03 20:30 | 587 | 586
2019-07-03 21:00 | 566 | 565
2019-07-03 21:30 | 532 | 531
2019-07-03 22:00 | 503 | 501
2019-07-03 22:30 | 485 | 484
2019-07-03 23:00 | 466 | 464
2019-07-03 23:30 | 446 | 442
2019-07-04 | 417 | 412
2019-07-04 00:30 | 393 | 385
2019-07-04 01:00 | 370 | 360
2019-07-04 01:30 | 359 | 348
2019-07-04 02:00 | 347 | 336
2019-07-04 02:30 | 340 | 328
2019-07-04 03:00 | 335 | 323
2019-07-04 03:30 | 332 | 319
2019-07-04 04:00 | 330 | 318
2019-07-04 04:30 | 333 | 322
2019-07-04 05:00 | 332 | 322
2019-07-04 05:30 | 358 | 350
2019-07-04 06:00 | 396 | 390
2019-07-04 06:30 | 466 | 464
2019-07-04 07:00 | 522 | 521
2019-07-04 07:30 | 554 | 549
2019-07-04 08:00 | 569 | 565
2019-07-04 08:30 | 573 | 569
2019-07-04 09:00 | 548 | 544
2019-07-04 09:30 | 535 | 530
2019-07-04 10:00 | 512 | 507
2019-07-04 10:30 | 486 | 485
2019-07-04 11:00 | 484 | 483
2019-07-04 11:30 | 480 | 479
2019-07-04 12:00 | 463 | 462
2019-07-04 12:30 | 466 | 465
2019-07-04 13:00 | 473 | 472
2019-07-04 13:30 | 478 | 477
2019-07-04 14:00 | 489 | 488
2019-07-04 14:30 | 501 | 500
2019-07-04 15:00 | 507 | 506
2019-07-04 15:30 | 503 | 503
2019-07-04 16:00 | 517 | 517
2019-07-04 16:30 | 540 | 539
2019-07-04 17:00 | 581 | 580
2019-07-04 17:30 | 619 | 619
2019-07-04 18:00 | 649 | 645
2019-07-04 18:30 | 632 | 627
2019-07-04 19:00 | 633 | 629
2019-07-04 19:30 | 619 | 613
2019-07-04 20:00 | 610 | 603
2019-07-04 20:30 | 601 | 595
2019-07-04 21:00 | 574 | 571
2019-07-04 21:30 | 553 | 552
2019-07-04 22:00 | 526 | 525
2019-07-04 22:30 | 513 | 511
2019-07-04 23:00 | 478 | 475
2019-07-04 23:30 | 461 | 458
2019-07-05 | 443 | 438
2019-07-05 00:30 | 410 | 401
2019-07-05 01:00 | 392 | 382
2019-07-05 01:30 | 372 | 360
2019-07-05 02:00 | 359 | 347
2019-07-05 02:30 | 351 | 338
2019-07-05 03:00 | 343 | 330
2019-07-05 03:30 | 331 | 318
2019-07-05 04:00 | 318 | 303
2019-07-05 04:30 | 329 | 316
2019-07-05 05:00 | 348 | 337
2019-07-05 05:30 | 373 | 364
2019-07-05 06:00 | 399 | 393
2019-07-05 06:30 | 458 | 454
2019-07-05 07:00 | 515 | 511
2019-07-05 07:30 | 547 | 546
2019-07-05 08:00 | 560 | 558
2019-07-05 08:30 | 562 | 561
2019-07-05 09:00 | 528 | 527
2019-07-05 09:30 | 508 | 506
2019-07-05 10:00 | 497 | 494
2019-07-05 10:30 | 492 | 489
2019-07-05 11:00 | 490 | 488
2019-07-05 11:30 | 467 | 465
2019-07-05 12:00 | 484 | 482
2019-07-05 12:30 | 493 | 491
2019-07-05 13:00 | 497 | 495
2019-07-05 13:30 | 492 | 490
2019-07-05 14:00 | 483 | 480
2019-07-05 14:30 | 492 | 490
2019-07-05 15:00 | 499 | 496
2019-07-05 15:30 | 494 | 492
2019-07-05 16:00 | 504 | 501
2019-07-05 16:30 | 530 | 527
2019-07-05 17:00 | 573 | 569
2019-07-05 17:30 | 609 | 602
2019-07-05 18:00 | 614 | 608
2019-07-05 18:30 | 603 | 595
2019-07-05 19:00 | 606 | 598
2019-07-05 19:30 | 585 | 576
2019-07-05 20:00 | 581 | 572
2019-07-05 20:30 | 583 | 573
2019-07-05 21:00 | 561 | 554
2019-07-05 21:30 | 529 | 526
2019-07-05 22:00 | 496 | 493
2019-07-05 22:30 | 475 | 473
2019-07-05 23:00 | 452 | 450
2019-07-05 23:30 | 429 | 425
2019-07-06 | 401 | 395
2019-07-06 00:30 | 368 | 360
2019-07-06 01:00 | 349 | 340
2019-07-06 01:30 | 336 | 325
2019-07-06 02:00 | 328 | 316
2019-07-06 02:30 | 320 | 306
2019-07-06 03:00 | 314 | 300
2019-07-06 03:30 | 312 | 297
2019-07-06 04:00 | 313 | 299
2019-07-06 04:30 | 308 | 294
2019-07-06 05:00 | 305 | 291
2019-07-06 05:30 | 314 | 301
2019-07-06 06:00 | 316 | 305
2019-07-06 06:30 | 337 | 328
2019-07-06 07:00 | 364 | 356
2019-07-06 07:30 | 389 | 381
2019-07-06 08:00 | 424 | 417
2019-07-06 08:30 | 450 | 445
2019-07-06 09:00 | 468 | 464
2019-07-06 09:30 | 459 | 455
2019-07-06 10:00 | 442 | 438
2019-07-06 10:30 | 426 | 422
2019-07-06 11:00 | 399 | 394
2019-07-06 11:30 | 396 | 391
2019-07-06 12:00 | 389 | 383
2019-07-06 12:30 | 380 | 373
2019-07-06 13:00 | 399 | 393
2019-07-06 13:30 | 406 | 401
2019-07-06 14:00 | 407 | 402
2019-07-06 14:30 | 415 | 410
2019-07-06 15:00 | 411 | 406
2019-07-06 15:30 | 423 | 418
2019-07-06 16:00 | 453 | 449
2019-07-06 16:30 | 479 | 476
2019-07-06 17:00 | 504 | 500
2019-07-06 17:30 | 533 | 524
2019-07-06 18:00 | 539 | 527
2019-07-06 18:30 | 533 | 521
2019-07-06 19:00 | 531 | 519
2019-07-06 19:30 | 527 | 514
2019-07-06 20:00 | 521 | 511
2019-07-06 20:30 | 523 | 512
2019-07-06 21:00 | 515 | 502
2019-07-06 21:30 | 497 | 483
2019-07-06 22:00 | 475 | 469
2019-07-06 22:30 | 454 | 449
2019-07-06 23:00 | 435 | 429
2019-07-06 23:30 | 423 | 416
2019-07-07 | 401 | 392
2019-07-07 00:30 | 365 | 355
2019-07-07 01:00 | 348 | 336
2019-07-07 01:30 | 341 | 328
2019-07-07 02:00 | 335 | 321
2019-07-07 02:30 | 315 | 300
2019-07-07 03:00 | 304 | 287
2019-07-07 03:30 | 305 | 288
2019-07-07 04:00 | 303 | 285
2019-07-07 04:30 | 301 | 284
2019-07-07 05:00 | 298 | 281
2019-07-07 05:30 | 303 | 287
2019-07-07 06:00 | 303 | 288
2019-07-07 06:30 | 336 | 323
2019-07-07 07:00 | 349 | 336
2019-07-07 07:30 | 365 | 353
2019-07-07 08:00 | 382 | 371
2019-07-07 08:30 | 409 | 400
2019-07-07 09:00 | 442 | 433
2019-07-07 09:30 | 454 | 445
2019-07-07 10:00 | 449 | 440
2019-07-07 10:30 | 445 | 437
2019-07-07 11:00 | 441 | 433
2019-07-07 11:30 | 433 | 424
2019-07-07 12:00 | 422 | 414
2019-07-07 12:30 | 409 | 401
2019-07-07 13:00 | 410 | 401
2019-07-07 13:30 | 421 | 413
2019-07-07 14:00 | 431 | 423
2019-07-07 14:30 | 442 | 434
2019-07-07 15:00 | 460 | 452
2019-07-07 15:30 | 465 | 458
2019-07-07 16:00 | 486 | 480
2019-07-07 16:30 | 505 | 500
2019-07-07 17:00 | 527 | 523
2019-07-07 17:30 | 564 | 562
2019-07-07 18:00 | 581 | 579
2019-07-07 18:30 | 579 | 577
2019-07-07 19:00 | 578 | 576
2019-07-07 19:30 | 563 | 561
2019-07-07 20:00 | 559 | 557
2019-07-07 20:30 | 564 | 563
2019-07-07 21:00 | 547 | 545
2019-07-07 21:30 | 528 | 526
2019-07-07 22:00 | 516 | 513
2019-07-07 22:30 | 496 | 493
2019-07-07 23:00 | 469 | 465
2019-07-07 23:30 | 443 | 438
2019-07-08 | 421 | 414
2019-07-08 00:30 | 392 | 382
2019-07-08 01:00 | 381 | 368
2019-07-08 01:30 | 364 | 350
2019-07-08 02:00 | 353 | 339
2019-07-08 02:30 | 354 | 340
2019-07-08 03:00 | 343 | 327
2019-07-08 03:30 | 342 | 325
2019-07-08 04:00 | 343 | 327
2019-07-08 04:30 | 350 | 335
2019-07-08 05:00 | 357 | 344
2019-07-08 05:30 | 385 | 375
2019-07-08 06:00 | 405 | 398
2019-07-08 06:30 | 460 | 457
2019-07-08 07:00 | 512 | 510
2019-07-08 07:30 | 560 | 558
2019-07-08 08:00 | 585 | 584
2019-07-08 08:30 | 598 | 598
2019-07-08 09:00 | 604 | 603
2019-07-08 09:30 | 604 | 603
2019-07-08 10:00 | 582 | 581
2019-07-08 10:30 | 552 | 551
2019-07-08 11:00 | 536 | 535
2019-07-08 11:30 | 538 | 537
2019-07-08 12:00 | 546 | 546
2019-07-08 12:30 | 555 | 554
2019-07-08 13:00 | 579 | 578
2019-07-08 13:30 | 573 | 572
2019-07-08 14:00 | 547 | 547
2019-07-08 14:30 | 534 | 533
2019-07-08 15:00 | 538 | 537
2019-07-08 15:30 | 536 | 536
2019-07-08 16:00 | 526 | 526
2019-07-08 16:30 | 555 | 554
2019-07-08 17:00 | 605 | 604
2019-07-08 17:30 | 638 | 637
2019-07-08 18:00 | 666 | 663
2019-07-08 18:30 | 659 | 655
2019-07-08 19:00 | 653 | 651
2019-07-08 19:30 | 638 | 638
2019-07-08 20:00 | 631 | 631
2019-07-08 20:30 | 631 | 630
2019-07-08 21:00 | 607 | 605
2019-07-08 21:30 | 585 | 582
2019-07-08 22:00 | 553 | 551
2019-07-08 22:30 | 536 | 534
2019-07-08 23:00 | 505 | 502
2019-07-08 23:30 | 479 | 476
2019-07-09 | 454 | 448
2019-07-09 00:30 | 418 | 409
2019-07-09 01:00 | 391 | 380
2019-07-09 01:30 | 376 | 364
2019-07-09 02:00 | 372 | 359
2019-07-09 02:30 | 366 | 352
2019-07-09 03:00 | 353 | 339
2019-07-09 03:30 | 356 | 342
2019-07-09 04:00 | 353 | 339
2019-07-09 04:30 | 352 | 339
2019-07-09 05:00 | 364 | 353
2019-07-09 05:30 | 395 | 386
2019-07-09 06:00 | 430 | 424
2019-07-09 06:30 | 480 | 478
2019-07-09 07:00 | 543 | 542
2019-07-09 07:30 | 585 | 585
2019-07-09 08:00 | 601 | 601
2019-07-09 08:30 | 591 | 590
2019-07-09 09:00 | 559 | 558
2019-07-09 09:30 | 524 | 523
2019-07-09 10:00 | 494 | 493
2019-07-09 10:30 | 481 | 480
2019-07-09 11:00 | 466 | 465
2019-07-09 11:30 | 448 | 447
2019-07-09 12:00 | 446 | 445
2019-07-09 12:30 | 445 | 444
2019-07-09 13:00 | 437 | 436
2019-07-09 13:30 | 448 | 448
2019-07-09 14:00 | 449 | 449
2019-07-09 14:30 | 467 | 466
2019-07-09 15:00 | 485 | 484
2019-07-09 15:30 | 506 | 505
2019-07-09 16:00 | 528 | 527
2019-07-09 16:30 | 567 | 567
2019-07-09 17:00 | 601 | 601
2019-07-09 17:30 | 624 | 623
2019-07-09 18:00 | 649 | 649
2019-07-09 18:30 | 643 | 642
2019-07-09 19:00 | 643 | 642
2019-07-09 19:30 | 629 | 628
2019-07-09 20:00 | 627 | 627
2019-07-09 20:30 | 619 | 619
2019-07-09 21:00 | 593 | 593
2019-07-09 21:30 | 568 | 568
2019-07-09 22:00 | 554 | 553
2019-07-09 22:30 | 547 | 545
2019-07-09 23:00 | 534 | 532
2019-07-09 23:30 | 512 | 510
2019-07-10 | 474 | 470
2019-07-10 00:30 | 432 | 427
2019-07-10 01:00 | 404 | 397
2019-07-10 01:30 | 385 | 375
2019-07-10 02:00 | 375 | 364
2019-07-10 02:30 | 368 | 357
2019-07-10 03:00 | 355 | 343
2019-07-10 03:30 | 346 | 334
2019-07-10 04:00 | 340 | 328
2019-07-10 04:30 | 349 | 338
2019-07-10 05:00 | 362 | 353
2019-07-10 05:30 | 395 | 388
2019-07-10 06:00 | 445 | 441
2019-07-10 06:30 | 510 | 508
2019-07-10 07:00 | 555 | 554
2019-07-10 07:30 | 576 | 575
2019-07-10 08:00 | 582 | 581
2019-07-10 08:30 | 574 | 574
2019-07-10 09:00 | 544 | 543
2019-07-10 09:30 | 507 | 506
2019-07-10 10:00 | 482 | 481
2019-07-10 10:30 | 463 | 461
2019-07-10 11:00 | 440 | 439
2019-07-10 11:30 | 426 | 425
2019-07-10 12:00 | 420 | 419
2019-07-10 12:30 | 406 | 406
2019-07-10 13:00 | 410 | 409
2019-07-10 13:30 | 416 | 415
2019-07-10 14:00 | 425 | 424
2019-07-10 14:30 | 439 | 439
2019-07-10 15:00 | 451 | 450
2019-07-10 15:30 | 466 | 466
2019-07-10 16:00 | 493 | 493
2019-07-10 16:30 | 534 | 533
2019-07-10 17:00 | 575 | 575
2019-07-10 17:30 | 605 | 605
2019-07-10 18:00 | 625 | 624
2019-07-10 18:30 | 624 | 623
2019-07-10 19:00 | 633 | 631
2019-07-10 19:30 | 636 | 634
2019-07-10 20:00 | 645 | 643
2019-07-10 20:30 | 637 | 635
2019-07-10 21:00 | 620 | 617
2019-07-10 21:30 | 596 | 594
2019-07-10 22:00 | 574 | 572
2019-07-10 22:30 | 566 | 565
2019-07-10 23:00 | 544 | 542
2019-07-10 23:30 | 512 | 510
2019-07-11 | 473 | 470
2019-07-11 00:30 | 425 | 420
2019-07-11 01:00 | 396 | 390
2019-07-11 01:30 | 379 | 371
2019-07-11 02:00 | 360 | 351
2019-07-11 02:30 | 344 | 334
2019-07-11 03:00 | 336 | 325
2019-07-11 03:30 | 328 | 318
2019-07-11 04:00 | 322 | 312
2019-07-11 04:30 | 331 | 322
2019-07-11 05:00 | 345 | 337
2019-07-11 05:30 | 385 | 380
2019-07-11 06:00 | 420 | 417
2019-07-11 06:30 | 487 | 486
2019-07-11 07:00 | 559 | 555
2019-07-11 07:30 | 590 | 588
2019-07-11 08:00 | 599 | 595
2019-07-11 08:30 | 592 | 588
2019-07-11 09:00 | 547 | 542
2019-07-11 09:30 | 503 | 502
2019-07-11 10:00 | 465 | 464
2019-07-11 10:30 | 451 | 449
2019-07-11 11:00 | 437 | 436
2019-07-11 11:30 | 425 | 423
2019-07-11 12:00 | 407 | 405
2019-07-11 12:30 | 396 | 394
2019-07-11 13:00 | 403 | 401
2019-07-11 13:30 | 412 | 410
2019-07-11 14:00 | 419 | 417
2019-07-11 14:30 | 438 | 436
2019-07-11 15:00 | 444 | 443
2019-07-11 15:30 | 461 | 459
2019-07-11 16:00 | 500 | 498
2019-07-11 16:30 | 541 | 540
2019-07-11 17:00 | 575 | 574
2019-07-11 17:30 | 627 | 626
2019-07-11 18:00 | 653 | 648
2019-07-11 18:30 | 650 | 644
2019-07-11 19:00 | 650 | 644
2019-07-11 19:30 | 650 | 642
2019-07-11 20:00 | 651 | 642
2019-07-11 20:30 | 643 | 636
2019-07-11 21:00 | 630 | 628
2019-07-11 21:30 | 604 | 600
2019-07-11 22:00 | 577 | 571
2019-07-11 22:30 | 552 | 546
2019-07-11 23:00 | 526 | 519
2019-07-11 23:30 | 489 | 484
2019-07-12 | 460 | 452
2019-07-12 00:30 | 424 | 414
2019-07-12 01:00 | 398 | 384
2019-07-12 01:30 | 376 | 360
2019-07-12 02:00 | 366 | 349
2019-07-12 02:30 | 358 | 340
2019-07-12 03:00 | 351 | 335
2019-07-12 03:30 | 348 | 331
2019-07-12 04:00 | 359 | 343
2019-07-12 04:30 | 362 | 347
2019-07-12 05:00 | 367 | 354
2019-07-12 05:30 | 400 | 391
2019-07-12 06:00 | 432 | 426
2019-07-12 06:30 | 494 | 490
2019-07-12 07:00 | 553 | 550
2019-07-12 07:30 | 598 | 596
2019-07-12 08:00 | 613 | 610
2019-07-12 08:30 | 599 | 596
2019-07-12 09:00 | 577 | 573
2019-07-12 09:30 | 543 | 537
2019-07-12 10:00 | 513 | 505
2019-07-12 10:30 | 489 | 485
2019-07-12 11:00 | 469 | 468
2019-07-12 11:30 | 455 | 453
2019-07-12 12:00 | 437 | 436
2019-07-12 12:30 | 432 | 430
2019-07-12 13:00 | 432 | 430
2019-07-12 13:30 | 445 | 443
2019-07-12 14:00 | 451 | 449
2019-07-12 14:30 | 464 | 462
2019-07-12 15:00 | 481 | 479
2019-07-12 15:30 | 492 | 491
2019-07-12 16:00 | 507 | 506
2019-07-12 16:30 | 539 | 538
2019-07-12 17:00 | 574 | 573
2019-07-12 17:30 | 591 | 590
2019-07-12 18:00 | 604 | 603
2019-07-12 18:30 | 588 | 587
2019-07-12 19:00 | 600 | 598
2019-07-12 19:30 | 595 | 593
2019-07-12 20:00 | 596 | 594
2019-07-12 20:30 | 594 | 592
2019-07-12 21:00 | 579 | 576
2019-07-12 21:30 | 557 | 553
2019-07-12 22:00 | 541 | 536
2019-07-12 22:30 | 527 | 524
2019-07-12 23:00 | 507 | 502
2019-07-12 23:30 | 488 | 482
2019-07-13 | 463 | 456
2019-07-13 00:30 | 426 | 415
2019-07-13 01:00 | 400 | 385
2019-07-13 01:30 | 384 | 367
2019-07-13 02:00 | 360 | 342
2019-07-13 02:30 | 342 | 325
2019-07-13 03:00 | 327 | 309
2019-07-13 03:30 | 325 | 307
2019-07-13 04:00 | 313 | 295
2019-07-13 04:30 | 320 | 302
2019-07-13 05:00 | 325 | 308
2019-07-13 05:30 | 328 | 313
2019-07-13 06:00 | 359 | 345
2019-07-13 06:30 | 391 | 379
2019-07-13 07:00 | 429 | 417
2019-07-13 07:30 | 464 | 454
2019-07-13 08:00 | 498 | 487
2019-07-13 08:30 | 504 | 494
2019-07-13 09:00 | 499 | 489
2019-07-13 09:30 | 486 | 475
2019-07-13 10:00 | 470 | 458
2019-07-13 10:30 | 429 | 419
2019-07-13 11:00 | 401 | 391
2019-07-13 11:30 | 409 | 398
2019-07-13 12:00 | 393 | 382
2019-07-13 12:30 | 393 | 382
2019-07-13 13:00 | 397 | 385
2019-07-13 13:30 | 393 | 381
2019-07-13 14:00 | 385 | 374
2019-07-13 14:30 | 402 | 391
2019-07-13 15:00 | 414 | 403
2019-07-13 15:30 | 432 | 423
2019-07-13 16:00 | 449 | 441
2019-07-13 16:30 | 470 | 463
2019-07-13 17:00 | 517 | 512
2019-07-13 17:30 | 544 | 539
2019-07-13 18:00 | 553 | 549
2019-07-13 18:30 | 552 | 548
2019-07-13 19:00 | 557 | 552
2019-07-13 19:30 | 551 | 546
2019-07-13 20:00 | 554 | 549
2019-07-13 20:30 | 557 | 553
2019-07-13 21:00 | 539 | 533
2019-07-13 21:30 | 529 | 522
2019-07-13 22:00 | 526 | 519
2019-07-13 22:30 | 520 | 512
2019-07-13 23:00 | 507 | 501
2019-07-13 23:30 | 489 | 482
2019-07-14 | 456 | 447
2019-07-14 00:30 | 418 | 406
2019-07-14 01:00 | 390 | 376
2019-07-14 01:30 | 377 | 361
2019-07-14 02:00 | 364 | 347
2019-07-14 02:30 | 352 | 334
2019-07-14 03:00 | 342 | 323
2019-07-14 03:30 | 332 | 313
2019-07-14 04:00 | 326 | 306
2019-07-14 04:30 | 324 | 303
2019-07-14 05:00 | 325 | 304
2019-07-14 05:30 | 336 | 316
2019-07-14 06:00 | 346 | 329
2019-07-14 06:30 | 386 | 370
2019-07-14 07:00 | 423 | 407
2019-07-14 07:30 | 467 | 454
2019-07-14 08:00 | 489 | 478
2019-07-14 08:30 | 494 | 483
2019-07-14 09:00 | 488 | 477
2019-07-14 09:30 | 472 | 460
2019-07-14 10:00 | 451 | 438
2019-07-14 10:30 | 428 | 414
2019-07-14 11:00 | 408 | 393
2019-07-14 11:30 | 391 | 375
2019-07-14 12:00 | 370 | 351
2019-07-14 12:30 | 361 | 342
2019-07-14 13:00 | 358 | 337
2019-07-14 13:30 | 361 | 342
2019-07-14 14:00 | 368 | 349
2019-07-14 14:30 | 376 | 359
2019-07-14 15:00 | 388 | 372
2019-07-14 15:30 | 406 | 391
2019-07-14 16:00 | 437 | 425
2019-07-14 16:30 | 486 | 479
2019-07-14 17:00 | 549 | 542
2019-07-14 17:30 | 582 | 577
2019-07-14 18:00 | 611 | 607
2019-07-14 18:30 | 616 | 612
2019-07-14 19:00 | 623 | 620
2019-07-14 19:30 | 623 | 619
2019-07-14 20:00 | 627 | 624
2019-07-14 20:30 | 626 | 623
2019-07-14 21:00 | 607 | 603
2019-07-14 21:30 | 588 | 583
2019-07-14 22:00 | 565 | 560
2019-07-14 22:30 | 545 | 538
2019-07-14 23:00 | 512 | 504
2019-07-14 23:30 | 480 | 475
2019-07-15 | 452 | 446
2019-07-15 00:30 | 401 | 393
2019-07-15 01:00 | 361 | 351
2019-07-15 01:30 | 346 | 334
2019-07-15 02:00 | 338 | 323
2019-07-15 02:30 | 336 | 321
2019-07-15 03:00 | 329 | 314
2019-07-15 03:30 | 334 | 319
2019-07-15 04:00 | 339 | 324
2019-07-15 04:30 | 348 | 335
2019-07-15 05:00 | 364 | 353
2019-07-15 05:30 | 396 | 388
2019-07-15 06:00 | 448 | 445
2019-07-15 06:30 | 547 | 545
2019-07-15 07:00 | 612 | 608
2019-07-15 07:30 | 659 | 657
2019-07-15 08:00 | 665 | 660
2019-07-15 08:30 | 632 | 630
2019-07-15 09:00 | 593 | 592
2019-07-15 09:30 | 557 | 556
2019-07-15 10:00 | 527 | 527
2019-07-15 10:30 | 493 | 492
2019-07-15 11:00 | 473 | 472
2019-07-15 11:30 | 457 | 456
2019-07-15 12:00 | 437 | 436
2019-07-15 12:30 | 428 | 427
2019-07-15 13:00 | 425 | 424
2019-07-15 13:30 | 427 | 426
2019-07-15 14:00 | 427 | 426
2019-07-15 14:30 | 435 | 434
2019-07-15 15:00 | 458 | 457
2019-07-15 15:30 | 476 | 475
2019-07-15 16:00 | 498 | 497
2019-07-15 16:30 | 525 | 524
2019-07-15 17:00 | 585 | 585
2019-07-15 17:30 | 641 | 640
2019-07-15 18:00 | 687 | 683
2019-07-15 18:30 | 691 | 687
2019-07-15 19:00 | 693 | 688
2019-07-15 19:30 | 690 | 684
2019-07-15 20:00 | 693 | 688
2019-07-15 20:30 | 688 | 684
2019-07-15 21:00 | 667 | 665
2019-07-15 21:30 | 620 | 618
2019-07-15 22:00 | 596 | 593
2019-07-15 22:30 | 589 | 586
2019-07-15 23:00 | 560 | 558
2019-07-15 23:30 | 524 | 521
2019-07-16 | 481 | 478
2019-07-16 00:30 | 432 | 429
2019-07-16 01:00 | 404 | 399
2019-07-16 01:30 | 387 | 382
2019-07-16 02:00 | 365 | 359
2019-07-16 02:30 | 357 | 351
2019-07-16 03:00 | 352 | 345
2019-07-16 03:30 | 342 | 335
2019-07-16 04:00 | 352 | 346
2019-07-16 04:30 | 361 | 355
2019-07-16 05:00 | 390 | 385
2019-07-16 05:30 | 433 | 430
2019-07-16 06:00 | 482 | 481
2019-07-16 06:30 | 571 | 569
2019-07-16 07:00 | 652 | 649
2019-07-16 07:30 | 685 | 679
2019-07-16 08:00 | 698 | 689
2019-07-16 08:30 | 669 | 660
2019-07-16 09:00 | 618 | 613
2019-07-16 09:30 | 579 | 574
2019-07-16 10:00 | 537 | 533
2019-07-16 10:30 | 518 | 514
2019-07-16 11:00 | 491 | 486
2019-07-16 11:30 | 482 | 478
2019-07-16 12:00 | 460 | 457
2019-07-16 12:30 | 436 | 432
2019-07-16 13:00 | 432 | 429
2019-07-16 13:30 | 430 | 426
2019-07-16 14:00 | 436 | 432
2019-07-16 14:30 | 447 | 443
2019-07-16 15:00 | 463 | 460
2019-07-16 15:30 | 470 | 467
2019-07-16 16:00 | 493 | 491
2019-07-16 16:30 | 531 | 529
2019-07-16 17:00 | 583 | 578
2019-07-16 17:30 | 635 | 629
2019-07-16 18:00 | 679 | 675
2019-07-16 18:30 | 679 | 672
2019-07-16 19:00 | 682 | 676
2019-07-16 19:30 | 681 | 675
2019-07-16 20:00 | 688 | 681
2019-07-16 20:30 | 694 | 686
2019-07-16 21:00 | 676 | 667
2019-07-16 21:30 | 645 | 636
2019-07-16 22:00 | 632 | 621
2019-07-16 22:30 | 597 | 586
2019-07-16 23:00 | 570 | 557
2019-07-16 23:30 | 533 | 519
2019-07-17 | 488 | 481
2019-07-17 00:30 | 451 | 443
2019-07-17 01:00 | 429 | 420
2019-07-17 01:30 | 415 | 404
2019-07-17 02:00 | 409 | 396
2019-07-17 02:30 | 405 | 392
2019-07-17 03:00 | 389 | 374
2019-07-17 03:30 | 377 | 362
2019-07-17 04:00 | 374 | 359
2019-07-17 04:30 | 379 | 366
2019-07-17 05:00 | 383 | 373
2019-07-17 05:30 | 430 | 424
2019-07-17 06:00 | 476 | 473
2019-07-17 06:30 | 558 | 557
2019-07-17 07:00 | 628 | 623
2019-07-17 07:30 | 678 | 671
2019-07-17 08:00 | 679 | 672
2019-07-17 08:30 | 661 | 652
2019-07-17 09:00 | 605 | 595
2019-07-17 09:30 | 570 | 563
2019-07-17 10:00 | 537 | 528
2019-07-17 10:30 | 489 | 486
2019-07-17 11:00 | 474 | 472
2019-07-17 11:30 | 447 | 446
2019-07-17 12:00 | 429 | 428
2019-07-17 12:30 | 418 | 417
2019-07-17 13:00 | 411 | 410
2019-07-17 13:30 | 414 | 412
2019-07-17 14:00 | 418 | 417
2019-07-17 14:30 | 430 | 430
2019-07-17 15:00 | 448 | 447
2019-07-17 15:30 | 464 | 463
2019-07-17 16:00 | 502 | 502
2019-07-17 16:30 | 529 | 529
2019-07-17 17:00 | 566 | 565
2019-07-17 17:30 | 606 | 601
2019-07-17 18:00 | 639 | 634
2019-07-17 18:30 | 639 | 634
2019-07-17 19:00 | 637 | 633
2019-07-17 19:30 | 636 | 631
2019-07-17 20:00 | 629 | 624
2019-07-17 20:30 | 632 | 628
2019-07-17 21:00 | 612 | 607
2019-07-17 21:30 | 582 | 575
2019-07-17 22:00 | 557 | 550
2019-07-17 22:30 | 532 | 529
2019-07-17 23:00 | 504 | 501
2019-07-17 23:30 | 479 | 475
2019-07-18 | 449 | 443
2019-07-18 00:30 | 421 | 414
2019-07-18 01:00 | 402 | 392
2019-07-18 01:30 | 391 | 379
2019-07-18 02:00 | 383 | 370
2019-07-18 02:30 | 373 | 360
2019-07-18 03:00 | 372 | 357
2019-07-18 03:30 | 375 | 360
2019-07-18 04:00 | 378 | 364
2019-07-18 04:30 | 379 | 366
2019-07-18 05:00 | 397 | 387
2019-07-18 05:30 | 428 | 422
2019-07-18 06:00 | 457 | 455
2019-07-18 06:30 | 534 | 533
2019-07-18 07:00 | 600 | 599
2019-07-18 07:30 | 648 | 645
2019-07-18 08:00 | 648 | 643
2019-07-18 08:30 | 629 | 623
2019-07-18 09:00 | 600 | 598
2019-07-18 09:30 | 565 | 562
2019-07-18 10:00 | 503 | 500
2019-07-18 10:30 | 468 | 466
2019-07-18 11:00 | 451 | 449
2019-07-18 11:30 | 436 | 433
2019-07-18 12:00 | 430 | 428
2019-07-18 12:30 | 423 | 421
2019-07-18 13:00 | 421 | 419
2019-07-18 13:30 | 419 | 417
2019-07-18 14:00 | 417 | 415
2019-07-18 14:30 | 427 | 426
2019-07-18 15:00 | 439 | 438
2019-07-18 15:30 | 471 | 470
2019-07-18 16:00 | 495 | 494
2019-07-18 16:30 | 535 | 534
2019-07-18 17:00 | 571 | 569
2019-07-18 17:30 | 615 | 610
2019-07-18 18:00 | 643 | 638
2019-07-18 18:30 | 648 | 643
2019-07-18 19:00 | 650 | 645
2019-07-18 19:30 | 641 | 636
2019-07-18 20:00 | 636 | 631
2019-07-18 20:30 | 639 | 633
2019-07-18 21:00 | 625 | 620
2019-07-18 21:30 | 607 | 601
2019-07-18 22:00 | 588 | 581
2019-07-18 22:30 | 560 | 558
2019-07-18 23:00 | 532 | 529
2019-07-18 23:30 | 500 | 495
2019-07-19 | 462 | 457
2019-07-19 00:30 | 428 | 422
2019-07-19 01:00 | 409 | 402
2019-07-19 01:30 | 398 | 388
2019-07-19 02:00 | 398 | 386
2019-07-19 02:30 | 402 | 390
2019-07-19 03:00 | 396 | 384
2019-07-19 03:30 | 391 | 379
2019-07-19 04:00 | 390 | 378
2019-07-19 04:30 | 394 | 384
2019-07-19 05:00 | 400 | 392
2019-07-19 05:30 | 427 | 421
2019-07-19 06:00 | 479 | 474
2019-07-19 06:30 | 556 | 551
2019-07-19 07:00 | 623 | 620
2019-07-19 07:30 | 666 | 661
2019-07-19 08:00 | 674 | 664
2019-07-19 08:30 | 648 | 636
2019-07-19 09:00 | 610 | 592
2019-07-19 09:30 | 544 | 536
2019-07-19 10:00 | 510 | 505
2019-07-19 10:30 | 484 | 479
2019-07-19 11:00 | 459 | 454
2019-07-19 11:30 | 444 | 437
2019-07-19 12:00 | 427 | 419
2019-07-19 12:30 | 414 | 406
2019-07-19 13:00 | 403 | 398
2019-07-19 13:30 | 407 | 402
2019-07-19 14:00 | 414 | 410
2019-07-19 14:30 | 429 | 425
2019-07-19 15:00 | 450 | 445
2019-07-19 15:30 | 469 | 465
2019-07-19 16:00 | 490 | 487
2019-07-19 16:30 | 526 | 519
2019-07-19 17:00 | 552 | 545
2019-07-19 17:30 | 568 | 561
2019-07-19 18:00 | 596 | 590
2019-07-19 18:30 | 593 | 586
2019-07-19 19:00 | 603 | 597
2019-07-19 19:30 | 609 | 602
2019-07-19 20:00 | 607 | 601
2019-07-19 20:30 | 596 | 590
2019-07-19 21:00 | 592 | 585
2019-07-19 21:30 | 583 | 575
2019-07-19 22:00 | 571 | 561
2019-07-19 22:30 | 547 | 541
2019-07-19 23:00 | 532 | 530
2019-07-19 23:30 | 512 | 508
2019-07-20 | 469 | 464
2019-07-20 00:30 | 438 | 431
2019-07-20 01:00 | 420 | 410
2019-07-20 01:30 | 405 | 392
2019-07-20 02:00 | 401 | 387
2019-07-20 02:30 | 396 | 381
2019-07-20 03:00 | 385 | 369
2019-07-20 03:30 | 377 | 361
2019-07-20 04:00 | 366 | 349
2019-07-20 04:30 | 366 | 350
2019-07-20 05:00 | 370 | 355
2019-07-20 05:30 | 374 | 361
2019-07-20 06:00 | 395 | 384
2019-07-20 06:30 | 423 | 414
2019-07-20 07:00 | 454 | 446
2019-07-20 07:30 | 487 | 481
2019-07-20 08:00 | 519 | 512
2019-07-20 08:30 | 519 | 511
2019-07-20 09:00 | 501 | 493
2019-07-20 09:30 | 478 | 469
2019-07-20 10:00 | 446 | 439
2019-07-20 10:30 | 418 | 409
2019-07-20 11:00 | 386 | 375
2019-07-20 11:30 | 374 | 363
2019-07-20 12:00 | 363 | 351
2019-07-20 12:30 | 360 | 346
2019-07-20 13:00 | 359 | 345
2019-07-20 13:30 | 360 | 347
2019-07-20 14:00 | 354 | 340
2019-07-20 14:30 | 360 | 347
2019-07-20 15:00 | 368 | 356
2019-07-20 15:30 | 403 | 393
2019-07-20 16:00 | 422 | 414
2019-07-20 16:30 | 439 | 432
2019-07-20 17:00 | 477 | 472
2019-07-20 17:30 | 514 | 509
2019-07-20 18:00 | 555 | 551
2019-07-20 18:30 | 558 | 555
2019-07-20 19:00 | 564 | 560
2019-07-20 19:30 | 562 | 558
2019-07-20 20:00 | 560 | 556
2019-07-20 20:30 | 560 | 556
2019-07-20 21:00 | 542 | 536
2019-07-20 21:30 | 531 | 525
2019-07-20 22:00 | 516 | 511
2019-07-20 22:30 | 493 | 490
2019-07-20 23:00 | 481 | 476
2019-07-20 23:30 | 463 | 457
2019-07-21 | 453 | 445
2019-07-21 00:30 | 418 | 407
2019-07-21 01:00 | 378 | 366
2019-07-21 01:30 | 359 | 345
2019-07-21 02:00 | 350 | 335
2019-07-21 02:30 | 338 | 322
2019-07-21 03:00 | 325 | 308
2019-07-21 03:30 | 322 | 304
2019-07-21 04:00 | 322 | 303
2019-07-21 04:30 | 324 | 305
2019-07-21 05:00 | 329 | 309
2019-07-21 05:30 | 338 | 319
2019-07-21 06:00 | 343 | 325
2019-07-21 06:30 | 362 | 346
2019-07-21 07:00 | 386 | 372
2019-07-21 07:30 | 427 | 414
2019-07-21 08:00 | 446 | 434
2019-07-21 08:30 | 468 | 460
2019-07-21 09:00 | 463 | 455
2019-07-21 09:30 | 439 | 432
2019-07-21 10:00 | 412 | 403
2019-07-21 10:30 | 380 | 370
2019-07-21 11:00 | 356 | 344
2019-07-21 11:30 | 329 | 317
2019-07-21 12:00 | 320 | 305
2019-07-21 12:30 | 306 | 291
2019-07-21 13:00 | 303 | 289
2019-07-21 13:30 | 325 | 312
2019-07-21 14:00 | 337 | 325
2019-07-21 14:30 | 347 | 336
2019-07-21 15:00 | 363 | 353
2019-07-21 15:30 | 383 | 374
2019-07-21 16:00 | 397 | 390
2019-07-21 16:30 | 450 | 445
2019-07-21 17:00 | 494 | 490
2019-07-21 17:30 | 535 | 529
2019-07-21 18:00 | 573 | 566
2019-07-21 18:30 | 575 | 569
2019-07-21 19:00 | 581 | 574
2019-07-21 19:30 | 578 | 572
2019-07-21 20:00 | 578 | 571
2019-07-21 20:30 | 584 | 576
2019-07-21 21:00 | 563 | 554
2019-07-21 21:30 | 528 | 518
2019-07-21 22:00 | 491 | 488
2019-07-21 22:30 | 476 | 472
2019-07-21 23:00 | 459 | 454
2019-07-21 23:30 | 437 | 430
2019-07-22 | 411 | 401
2019-07-22 00:30 | 379 | 368
2019-07-22 01:00 | 360 | 348
2019-07-22 01:30 | 350 | 337
2019-07-22 02:00 | 343 | 329
2019-07-22 02:30 | 337 | 321
2019-07-22 03:00 | 336 | 319
2019-07-22 03:30 | 340 | 323
2019-07-22 04:00 | 340 | 324
2019-07-22 04:30 | 343 | 327
2019-07-22 05:00 | 362 | 349
2019-07-22 05:30 | 386 | 376
2019-07-22 06:00 | 425 | 420
2019-07-22 06:30 | 508 | 506
2019-07-22 07:00 | 579 | 578
2019-07-22 07:30 | 626 | 622
2019-07-22 08:00 | 634 | 629
2019-07-22 08:30 | 608 | 602
2019-07-22 09:00 | 565 | 559
2019-07-22 09:30 | 538 | 531
2019-07-22 10:00 | 502 | 496
2019-07-22 10:30 | 483 | 480
2019-07-22 11:00 | 464 | 461
2019-07-22 11:30 | 455 | 451
2019-07-22 12:00 | 437 | 434
2019-07-22 12:30 | 426 | 424
2019-07-22 13:00 | 416 | 414
2019-07-22 13:30 | 425 | 424
2019-07-22 14:00 | 422 | 420
2019-07-22 14:30 | 426 | 425
2019-07-22 15:00 | 446 | 445
2019-07-22 15:30 | 470 | 470
2019-07-22 16:00 | 497 | 496
2019-07-22 16:30 | 540 | 540
2019-07-22 17:00 | 582 | 577
2019-07-22 17:30 | 615 | 608
2019-07-22 18:00 | 634 | 627
2019-07-22 18:30 | 629 | 622
2019-07-22 19:00 | 631 | 623
2019-07-22 19:30 | 624 | 615
2019-07-22 20:00 | 621 | 611
2019-07-22 20:30 | 622 | 611
2019-07-22 21:00 | 593 | 589
2019-07-22 21:30 | 567 | 562
2019-07-22 22:00 | 543 | 537
2019-07-22 22:30 | 517 | 512
2019-07-22 23:00 | 485 | 481
2019-07-22 23:30 | 457 | 452
2019-07-23 | 430 | 424
2019-07-23 00:30 | 394 | 385
2019-07-23 01:00 | 373 | 362
2019-07-23 01:30 | 358 | 345
2019-07-23 02:00 | 353 | 338
2019-07-23 02:30 | 346 | 330
2019-07-23 03:00 | 333 | 316
2019-07-23 03:30 | 320 | 303
2019-07-23 04:00 | 321 | 305
2019-07-23 04:30 | 336 | 321
2019-07-23 05:00 | 363 | 350
2019-07-23 05:30 | 389 | 380
2019-07-23 06:00 | 420 | 415
2019-07-23 06:30 | 501 | 495
2019-07-23 07:00 | 573 | 563
2019-07-23 07:30 | 596 | 589
2019-07-23 08:00 | 596 | 584
2019-07-23 08:30 | 558 | 545
2019-07-23 09:00 | 525 | 510
2019-07-23 09:30 | 522 | 511
2019-07-23 10:00 | 491 | 489
2019-07-23 10:30 | 475 | 473
2019-07-23 11:00 | 454 | 452
2019-07-23 11:30 | 443 | 441
2019-07-23 12:00 | 440 | 439
2019-07-23 12:30 | 435 | 434
2019-07-23 13:00 | 426 | 425
2019-07-23 13:30 | 430 | 430
2019-07-23 14:00 | 442 | 441
2019-07-23 14:30 | 459 | 459
2019-07-23 15:00 | 468 | 468
2019-07-23 15:30 | 484 | 484
2019-07-23 16:00 | 521 | 521
2019-07-23 16:30 | 548 | 547
2019-07-23 17:00 | 582 | 581
2019-07-23 17:30 | 603 | 602
2019-07-23 18:00 | 651 | 648
2019-07-23 18:30 | 652 | 648
2019-07-23 19:00 | 640 | 636
2019-07-23 19:30 | 634 | 629
2019-07-23 20:00 | 626 | 620
2019-07-23 20:30 | 625 | 621
2019-07-23 21:00 | 601 | 600
2019-07-23 21:30 | 567 | 565
2019-07-23 22:00 | 541 | 540
2019-07-23 22:30 | 529 | 526
2019-07-23 23:00 | 495 | 492
2019-07-23 23:30 | 465 | 460
2019-07-24 | 430 | 423
2019-07-24 00:30 | 398 | 387
2019-07-24 01:00 | 387 | 374
2019-07-24 01:30 | 377 | 362
2019-07-24 02:00 | 377 | 362
2019-07-24 02:30 | 372 | 356
2019-07-24 03:00 | 363 | 346
2019-07-24 03:30 | 367 | 350
2019-07-24 04:00 | 368 | 351
2019-07-24 04:30 | 380 | 365
2019-07-24 05:00 | 393 | 380
2019-07-24 05:30 | 423 | 414
2019-07-24 06:00 | 450 | 444
2019-07-24 06:30 | 531 | 530
2019-07-24 07:00 | 604 | 603
2019-07-24 07:30 | 642 | 642
2019-07-24 08:00 | 641 | 640
2019-07-24 08:30 | 596 | 595
2019-07-24 09:00 | 552 | 551
2019-07-24 09:30 | 517 | 516
2019-07-24 10:00 | 489 | 488
2019-07-24 10:30 | 473 | 472
2019-07-24 11:00 | 460 | 459
2019-07-24 11:30 | 447 | 446
2019-07-24 12:00 | 428 | 427
2019-07-24 12:30 | 423 | 422
2019-07-24 13:00 | 423 | 422
2019-07-24 13:30 | 429 | 428
2019-07-24 14:00 | 454 | 453
2019-07-24 14:30 | 473 | 472
2019-07-24 15:00 | 493 | 492
2019-07-24 15:30 | 511 | 511
2019-07-24 16:00 | 529 | 528
2019-07-24 16:30 | 557 | 556
2019-07-24 17:00 | 592 | 592
2019-07-24 17:30 | 629 | 628
2019-07-24 18:00 | 665 | 664
2019-07-24 18:30 | 667 | 665
2019-07-24 19:00 | 670 | 668
2019-07-24 19:30 | 655 | 653
2019-07-24 20:00 | 651 | 650
2019-07-24 20:30 | 651 | 649
2019-07-24 21:00 | 631 | 629
2019-07-24 21:30 | 609 | 608
2019-07-24 22:00 | 585 | 582
2019-07-24 22:30 | 575 | 572
2019-07-24 23:00 | 544 | 542
2019-07-24 23:30 | 517 | 514
2019-07-25 | 475 | 470
2019-07-25 00:30 | 446 | 438
2019-07-25 01:00 | 430 | 420
2019-07-25 01:30 | 419 | 408
2019-07-25 02:00 | 408 | 395
2019-07-25 02:30 | 401 | 388
2019-07-25 03:00 | 399 | 386
2019-07-25 03:30 | 390 | 377
2019-07-25 04:00 | 391 | 378
2019-07-25 04:30 | 411 | 398
2019-07-25 05:00 | 418 | 407
2019-07-25 05:30 | 441 | 434
2019-07-25 06:00 | 481 | 477
2019-07-25 06:30 | 557 | 556
2019-07-25 07:00 | 630 | 629
2019-07-25 07:30 | 666 | 664
2019-07-25 08:00 | 662 | 656
2019-07-25 08:30 | 624 | 617
2019-07-25 09:00 | 576 | 571
2019-07-25 09:30 | 543 | 540
2019-07-25 10:00 | 523 | 519
2019-07-25 10:30 | 508 | 504
2019-07-25 11:00 | 503 | 499
2019-07-25 11:30 | 503 | 501
2019-07-25 12:00 | 500 | 498
2019-07-25 12:30 | 505 | 503
2019-07-25 13:00 | 509 | 508
2019-07-25 13:30 | 516 | 514
2019-07-25 14:00 | 516 | 515
2019-07-25 14:30 | 524 | 522
2019-07-25 15:00 | 534 | 533
2019-07-25 15:30 | 542 | 541
2019-07-25 16:00 | 562 | 561
2019-07-25 16:30 | 584 | 583
2019-07-25 17:00 | 611 | 610
2019-07-25 17:30 | 639 | 638
2019-07-25 18:00 | 673 | 671
2019-07-25 18:30 | 675 | 670
2019-07-25 19:00 | 674 | 669
2019-07-25 19:30 | 665 | 659
2019-07-25 20:00 | 663 | 659
2019-07-25 20:30 | 669 | 665
2019-07-25 21:00 | 651 | 647
2019-07-25 21:30 | 616 | 614
2019-07-25 22:00 | 590 | 588
2019-07-25 22:30 | 554 | 553
2019-07-25 23:00 | 520 | 517
2019-07-25 23:30 | 488 | 484
2019-07-26 | 456 | 451
2019-07-26 00:30 | 422 | 414
2019-07-26 01:00 | 405 | 393
2019-07-26 01:30 | 391 | 377
2019-07-26 02:00 | 385 | 369
2019-07-26 02:30 | 379 | 362
2019-07-26 03:00 | 376 | 359
2019-07-26 03:30 | 376 | 359
2019-07-26 04:00 | 375 | 358
2019-07-26 04:30 | 382 | 366
2019-07-26 05:00 | 392 | 378
2019-07-26 05:30 | 418 | 408
2019-07-26 06:00 | 457 | 450
2019-07-26 06:30 | 525 | 522
2019-07-26 07:00 | 592 | 589
2019-07-26 07:30 | 650 | 644
2019-07-26 08:00 | 653 | 645
2019-07-26 08:30 | 631 | 622
2019-07-26 09:00 | 610 | 600
2019-07-26 09:30 | 560 | 554
2019-07-26 10:00 | 529 | 525
2019-07-26 10:30 | 504 | 500
2019-07-26 11:00 | 490 | 486
2019-07-26 11:30 | 481 | 478
2019-07-26 12:00 | 476 | 474
2019-07-26 12:30 | 508 | 504
2019-07-26 13:00 | 516 | 513
2019-07-26 13:30 | 516 | 513
2019-07-26 14:00 | 506 | 503
2019-07-26 14:30 | 506 | 502
2019-07-26 15:00 | 538 | 535
2019-07-26 15:30 | 540 | 537
2019-07-26 16:00 | 514 | 510
2019-07-26 16:30 | 540 | 537
2019-07-26 17:00 | 558 | 556
2019-07-26 17:30 | 568 | 567
2019-07-26 18:00 | 629 | 624
2019-07-26 18:30 | 633 | 623
2019-07-26 19:00 | 636 | 626
2019-07-26 19:30 | 629 | 621
2019-07-26 20:00 | 634 | 627
2019-07-26 20:30 | 635 | 630
2019-07-26 21:00 | 608 | 606
2019-07-26 21:30 | 594 | 591
2019-07-26 22:00 | 577 | 573
2019-07-26 22:30 | 565 | 561
2019-07-26 23:00 | 541 | 536
2019-07-26 23:30 | 512 | 505
2019-07-27 | 474 | 465
2019-07-27 00:30 | 444 | 432
2019-07-27 01:00 | 415 | 400
2019-07-27 01:30 | 413 | 396
2019-07-27 02:00 | 424 | 405
2019-07-27 02:30 | 428 | 407
2019-07-27 03:00 | 408 | 384
2019-07-27 03:30 | 398 | 374
2019-07-27 04:00 | 398 | 373
2019-07-27 04:30 | 389 | 365
2019-07-27 05:00 | 382 | 358
2019-07-27 05:30 | 388 | 366
2019-07-27 06:00 | 400 | 381
2019-07-27 06:30 | 432 | 415
2019-07-27 07:00 | 463 | 447
2019-07-27 07:30 | 494 | 481
2019-07-27 08:00 | 506 | 493
2019-07-27 08:30 | 500 | 488
2019-07-27 09:00 | 490 | 478
2019-07-27 09:30 | 470 | 457
2019-07-27 10:00 | 458 | 445
2019-07-27 10:30 | 443 | 429
2019-07-27 11:00 | 429 | 414
2019-07-27 11:30 | 428 | 412
2019-07-27 12:00 | 423 | 408
2019-07-27 12:30 | 411 | 395
2019-07-27 13:00 | 414 | 398
2019-07-27 13:30 | 418 | 403
2019-07-27 14:00 | 421 | 406
2019-07-27 14:30 | 427 | 412
2019-07-27 15:00 | 438 | 424
2019-07-27 15:30 | 456 | 443
2019-07-27 16:00 | 474 | 462
2019-07-27 16:30 | 492 | 481
2019-07-27 17:00 | 516 | 508
2019-07-27 17:30 | 539 | 532
2019-07-27 18:00 | 560 | 556
2019-07-27 18:30 | 564 | 560
2019-07-27 19:00 | 555 | 551
2019-07-27 19:30 | 543 | 538
2019-07-27 20:00 | 533 | 528
2019-07-27 20:30 | 539 | 534
2019-07-27 21:00 | 531 | 525
2019-07-27 21:30 | 522 | 514
2019-07-27 22:00 | 512 | 504
2019-07-27 22:30 | 504 | 495
2019-07-27 23:00 | 489 | 478
2019-07-27 23:30 | 466 | 454
2019-07-28 | 442 | 427
2019-07-28 00:30 | 411 | 393
2019-07-28 01:00 | 391 | 371
2019-07-28 01:30 | 388 | 365
2019-07-28 02:00 | 380 | 356
2019-07-28 02:30 | 370 | 345
2019-07-28 03:00 | 367 | 340
2019-07-28 03:30 | 363 | 336
2019-07-28 04:00 | 363 | 336
2019-07-28 04:30 | 358 | 331
2019-07-28 05:00 | 358 | 331
2019-07-28 05:30 | 363 | 337
2019-07-28 06:00 | 371 | 346
2019-07-28 06:30 | 385 | 363
2019-07-28 07:00 | 406 | 384
2019-07-28 07:30 | 434 | 414
2019-07-28 08:00 | 447 | 427
2019-07-28 08:30 | 448 | 430
2019-07-28 09:00 | 451 | 433
2019-07-28 09:30 | 445 | 427
2019-07-28 10:00 | 429 | 412
2019-07-28 10:30 | 419 | 401
2019-07-28 11:00 | 416 | 399
2019-07-28 11:30 | 401 | 383
2019-07-28 12:00 | 396 | 378
2019-07-28 12:30 | 387 | 368
2019-07-28 13:00 | 389 | 370
2019-07-28 13:30 | 404 | 387
2019-07-28 14:00 | 412 | 395
2019-07-28 14:30 | 418 | 403
2019-07-28 15:00 | 419 | 405
2019-07-28 15:30 | 444 | 432
2019-07-28 16:00 | 463 | 451
2019-07-28 16:30 | 493 | 483
2019-07-28 17:00 | 534 | 525
2019-07-28 17:30 | 556 | 549
2019-07-28 18:00 | 590 | 585
2019-07-28 18:30 | 596 | 590
2019-07-28 19:00 | 599 | 592
2019-07-28 19:30 | 586 | 579
2019-07-28 20:00 | 587 | 579
2019-07-28 20:30 | 590 | 583
2019-07-28 21:00 | 572 | 565
2019-07-28 21:30 | 556 | 549
2019-07-28 22:00 | 527 | 519
2019-07-28 22:30 | 499 | 489
2019-07-28 23:00 | 478 | 467
2019-07-28 23:30 | 455 | 442
2019-07-29 | 434 | 417
2019-07-29 00:30 | 413 | 394
2019-07-29 01:00 | 396 | 375
2019-07-29 01:30 | 394 | 370
2019-07-29 02:00 | 386 | 362
2019-07-29 02:30 | 368 | 343
2019-07-29 03:00 | 355 | 330
2019-07-29 03:30 | 349 | 325
2019-07-29 04:00 | 347 | 323
2019-07-29 04:30 | 351 | 329
2019-07-29 05:00 | 367 | 348
2019-07-29 05:30 | 401 | 386
2019-07-29 06:00 | 442 | 431
2019-07-29 06:30 | 509 | 503
2019-07-29 07:00 | 559 | 556
2019-07-29 07:30 | 600 | 595
2019-07-29 08:00 | 601 | 596
2019-07-29 08:30 | 573 | 568
2019-07-29 09:00 | 537 | 530
2019-07-29 09:30 | 510 | 502
2019-07-29 10:00 | 475 | 474
2019-07-29 10:30 | 463 | 461
2019-07-29 11:00 | 449 | 448
2019-07-29 11:30 | 445 | 443
2019-07-29 12:00 | 444 | 443
2019-07-29 12:30 | 436 | 435
2019-07-29 13:00 | 435 | 433
2019-07-29 13:30 | 439 | 438
2019-07-29 14:00 | 455 | 454
2019-07-29 14:30 | 468 | 467
2019-07-29 15:00 | 494 | 493
2019-07-29 15:30 | 511 | 510
2019-07-29 16:00 | 519 | 518
2019-07-29 16:30 | 544 | 544
2019-07-29 17:00 | 581 | 578
2019-07-29 17:30 | 615 | 608
2019-07-29 18:00 | 640 | 637
2019-07-29 18:30 | 640 | 636
2019-07-29 19:00 | 640 | 636
2019-07-29 19:30 | 625 | 620
2019-07-29 20:00 | 616 | 611
2019-07-29 20:30 | 616 | 612
2019-07-29 21:00 | 586 | 585
2019-07-29 21:30 | 569 | 568
2019-07-29 22:00 | 552 | 550
2019-07-29 22:30 | 530 | 527
2019-07-29 23:00 | 505 | 501
2019-07-29 23:30 | 473 | 465
2019-07-30 | 451 | 440
2019-07-30 00:30 | 421 | 404
2019-07-30 01:00 | 406 | 386
2019-07-30 01:30 | 396 | 373
2019-07-30 02:00 | 400 | 375
2019-07-30 02:30 | 398 | 373
2019-07-30 03:00 | 390 | 364
2019-07-30 03:30 | 384 | 358
2019-07-30 04:00 | 381 | 356
2019-07-30 04:30 | 389 | 365
2019-07-30 05:00 | 398 | 377
2019-07-30 05:30 | 419 | 403
2019-07-30 06:00 | 453 | 441
2019-07-30 06:30 | 536 | 520
2019-07-30 07:00 | 596 | 582
2019-07-30 07:30 | 618 | 608
2019-07-30 08:00 | 612 | 601
2019-07-30 08:30 | 580 | 568
2019-07-30 09:00 | 540 | 534
2019-07-30 09:30 | 507 | 500
2019-07-30 10:00 | 482 | 474
2019-07-30 10:30 | 467 | 458
2019-07-30 11:00 | 460 | 452
2019-07-30 11:30 | 458 | 451
2019-07-30 12:00 | 457 | 449
2019-07-30 12:30 | 455 | 448
2019-07-30 13:00 | 463 | 456
2019-07-30 13:30 | 463 | 457
2019-07-30 14:00 | 478 | 473
2019-07-30 14:30 | 490 | 485
2019-07-30 15:00 | 508 | 504
2019-07-30 15:30 | 527 | 522
2019-07-30 16:00 | 537 | 533
2019-07-30 16:30 | 566 | 563
2019-07-30 17:00 | 606 | 601
2019-07-30 17:30 | 643 | 635
2019-07-30 18:00 | 685 | 679
2019-07-30 18:30 | 683 | 675
2019-07-30 19:00 | 681 | 673
2019-07-30 19:30 | 674 | 664
2019-07-30 20:00 | 662 | 652
2019-07-30 20:30 | 647 | 642
2019-07-30 21:00 | 617 | 615
2019-07-30 21:30 | 585 | 581
2019-07-30 22:00 | 562 | 557
2019-07-30 22:30 | 545 | 538
2019-07-30 23:00 | 518 | 511
2019-07-30 23:30 | 484 | 474
2019-07-31 | 452 | 437
2019-07-31 00:30 | 423 | 409
2019-07-31 01:00 | 403 | 387
2019-07-31 01:30 | 392 | 374
2019-07-31 02:00 | 391 | 371
2019-07-31 02:30 | 387 | 366
2019-07-31 03:00 | 382 | 361
2019-07-31 03:30 | 385 | 365
2019-07-31 04:00 | 387 | 367
2019-07-31 04:30 | 392 | 373
2019-07-31 05:00 | 400 | 384
2019-07-31 05:30 | 427 | 415
2019-07-31 06:00 | 470 | 462
2019-07-31 06:30 | 538 | 534
2019-07-31 07:00 | 606 | 604
2019-07-31 07:30 | 649 | 641
2019-07-31 08:00 | 648 | 639
2019-07-31 08:30 | 586 | 583
2019-07-31 09:00 | 538 | 534
2019-07-31 09:30 | 512 | 508
2019-07-31 10:00 | 499 | 495
2019-07-31 10:30 | 486 | 481
2019-07-31 11:00 | 481 | 476
2019-07-31 11:30 | 483 | 479
2019-07-31 12:00 | 482 | 478
2019-07-31 12:30 | 477 | 473
2019-07-31 13:00 | 473 | 470
2019-07-31 13:30 | 465 | 461
2019-07-31 14:00 | 473 | 469
2019-07-31 14:30 | 493 | 490
2019-07-31 15:00 | 493 | 489
2019-07-31 15:30 | 503 | 500
2019-07-31 16:00 | 526 | 523
2019-07-31 16:30 | 558 | 555
2019-07-31 17:00 | 585 | 583
2019-07-31 17:30 | 625 | 620
2019-07-31 18:00 | 668 | 661
2019-07-31 18:30 | 682 | 673
2019-07-31 19:00 | 680 | 671
2019-07-31 19:30 | 670 | 660
2019-07-31 20:00 | 658 | 649
2019-07-31 20:30 | 644 | 640
2019-07-31 21:00 | 616 | 613
2019-07-31 21:30 | 594 | 590
2019-07-31 22:00 | 568 | 564
2019-07-31 22:30 | 552 | 548
2019-07-31 23:00 | 524 | 519
2019-07-31 23:30 | 493 | 485
2019-08-01 | 465 | 455
2019-08-01 00:30 | 437 | 423
2019-08-01 01:00 | 422 | 406
2019-08-01 01:30 | 408 | 392
2019-08-01 02:00 | 401 | 387
2019-08-01 02:30 | 387 | 373
2019-08-01 03:00 | 384 | 369
2019-08-01 03:30 | 386 | 371
2019-08-01 04:00 | 385 | 371
2019-08-01 04:30 | 395 | 382
2019-08-01 05:00 | 411 | 399
2019-08-01 05:30 | 434 | 425
2019-08-01 06:00 | 468 | 462
2019-08-01 06:30 | 553 | 548
2019-08-01 07:00 | 621 | 612
2019-08-01 07:30 | 645 | 638
2019-08-01 08:00 | 639 | 630
2019-08-01 08:30 | 609 | 599
2019-08-01 09:00 | 558 | 552
2019-08-01 09:30 | 532 | 527
2019-08-01 10:00 | 523 | 519
2019-08-01 10:30 | 516 | 514
2019-08-01 11:00 | 507 | 505
2019-08-01 11:30 | 506 | 504
2019-08-01 12:00 | 520 | 519
2019-08-01 12:30 | 523 | 521
2019-08-01 13:00 | 512 | 510
2019-08-01 13:30 | 494 | 492
2019-08-01 14:00 | 497 | 495
2019-08-01 14:30 | 500 | 498
2019-08-01 15:00 | 510 | 509
2019-08-01 15:30 | 526 | 525
2019-08-01 16:00 | 561 | 559
2019-08-01 16:30 | 585 | 584
2019-08-01 17:00 | 617 | 616
2019-08-01 17:30 | 674 | 669
2019-08-01 18:00 | 698 | 695
2019-08-01 18:30 | 696 | 692
2019-08-01 19:00 | 699 | 696
2019-08-01 19:30 | 697 | 693
2019-08-01 20:00 | 699 | 694
2019-08-01 20:30 | 697 | 692
2019-08-01 21:00 | 688 | 681
2019-08-01 21:30 | 654 | 648
2019-08-01 22:00 | 621 | 618
2019-08-01 22:30 | 596 | 594
2019-08-01 23:00 | 565 | 562
2019-08-01 23:30 | 526 | 521
2019-08-02 | 490 | 482
2019-08-02 00:30 | 455 | 444
2019-08-02 01:00 | 428 | 415
2019-08-02 01:30 | 414 | 396
2019-08-02 02:00 | 412 | 393
2019-08-02 02:30 | 401 | 381
2019-08-02 03:00 | 393 | 372
2019-08-02 03:30 | 388 | 368
2019-08-02 04:00 | 391 | 370
2019-08-02 04:30 | 397 | 378
2019-08-02 05:00 | 406 | 389
2019-08-02 05:30 | 435 | 422
2019-08-02 06:00 | 478 | 470
2019-08-02 06:30 | 555 | 550
2019-08-02 07:00 | 618 | 615
2019-08-02 07:30 | 647 | 644
2019-08-02 08:00 | 655 | 651
2019-08-02 08:30 | 635 | 631
2019-08-02 09:00 | 577 | 571
2019-08-02 09:30 | 549 | 544
2019-08-02 10:00 | 521 | 515
2019-08-02 10:30 | 500 | 494
2019-08-02 11:00 | 485 | 481
2019-08-02 11:30 | 487 | 484
2019-08-02 12:00 | 486 | 482
2019-08-02 12:30 | 480 | 476
2019-08-02 13:00 | 475 | 472
2019-08-02 13:30 | 472 | 469
2019-08-02 14:00 | 463 | 459
2019-08-02 14:30 | 469 | 466
2019-08-02 15:00 | 484 | 480
2019-08-02 15:30 | 490 | 486
2019-08-02 16:00 | 512 | 509
2019-08-02 16:30 | 551 | 548
2019-08-02 17:00 | 603 | 596
2019-08-02 17:30 | 629 | 621
2019-08-02 18:00 | 655 | 644
2019-08-02 18:30 | 663 | 649
2019-08-02 19:00 | 662 | 649
2019-08-02 19:30 | 659 | 645
2019-08-02 20:00 | 658 | 646
2019-08-02 20:30 | 656 | 644
2019-08-02 21:00 | 622 | 616
2019-08-02 21:30 | 605 | 599
2019-08-02 22:00 | 579 | 571
2019-08-02 22:30 | 573 | 564
2019-08-02 23:00 | 549 | 540
2019-08-02 23:30 | 511 | 503
2019-08-03 | 477 | 465
2019-08-03 00:30 | 441 | 425
2019-08-03 01:00 | 417 | 399
2019-08-03 01:30 | 398 | 379
2019-08-03 02:00 | 392 | 371
2019-08-03 02:30 | 383 | 361
2019-08-03 03:00 | 372 | 348
2019-08-03 03:30 | 370 | 345
2019-08-03 04:00 | 376 | 350
2019-08-03 04:30 | 387 | 362
2019-08-03 05:00 | 371 | 347
2019-08-03 05:30 | 377 | 356
2019-08-03 06:00 | 391 | 372
2019-08-03 06:30 | 423 | 407
2019-08-03 07:00 | 455 | 440
2019-08-03 07:30 | 493 | 480
2019-08-03 08:00 | 501 | 489
2019-08-03 08:30 | 504 | 493
2019-08-03 09:00 | 482 | 471
2019-08-03 09:30 | 454 | 443
2019-08-03 10:00 | 424 | 412
2019-08-03 10:30 | 412 | 397
2019-08-03 11:00 | 401 | 384
2019-08-03 11:30 | 398 | 381
2019-08-03 12:00 | 384 | 367
2019-08-03 12:30 | 383 | 365
2019-08-03 13:00 | 380 | 363
2019-08-03 13:30 | 377 | 360
2019-08-03 14:00 | 382 | 365
2019-08-03 14:30 | 391 | 375
2019-08-03 15:00 | 397 | 382
2019-08-03 15:30 | 405 | 390
2019-08-03 16:00 | 424 | 411
2019-08-03 16:30 | 463 | 451
2019-08-03 17:00 | 511 | 502
2019-08-03 17:30 | 553 | 544
2019-08-03 18:00 | 575 | 568
2019-08-03 18:30 | 585 | 578
2019-08-03 19:00 | 590 | 583
2019-08-03 19:30 | 586 | 578
2019-08-03 20:00 | 586 | 579
2019-08-03 20:30 | 589 | 581
2019-08-03 21:00 | 576 | 568
2019-08-03 21:30 | 561 | 552
2019-08-03 22:00 | 547 | 540
2019-08-03 22:30 | 540 | 532
2019-08-03 23:00 | 532 | 523
2019-08-03 23:30 | 509 | 498
2019-08-04 | 470 | 456
2019-08-04 00:30 | 431 | 414
2019-08-04 01:00 | 411 | 391
2019-08-04 01:30 | 402 | 381
2019-08-04 02:00 | 391 | 369
2019-08-04 02:30 | 375 | 349
2019-08-04 03:00 | 370 | 338
2019-08-04 03:30 | 370 | 338
2019-08-04 04:00 | 370 | 338
2019-08-04 04:30 | 376 | 344
2019-08-04 05:00 | 380 | 349
2019-08-04 05:30 | 389 | 360
2019-08-04 06:00 | 405 | 377
2019-08-04 06:30 | 419 | 393
2019-08-04 07:00 | 445 | 421
2019-08-04 07:30 | 471 | 449
2019-08-04 08:00 | 481 | 460
2019-08-04 08:30 | 475 | 456
2019-08-04 09:00 | 473 | 454
2019-08-04 09:30 | 456 | 438
2019-08-04 10:00 | 435 | 420
2019-08-04 10:30 | 416 | 399
2019-08-04 11:00 | 393 | 375
2019-08-04 11:30 | 374 | 352
2019-08-04 12:00 | 371 | 350
2019-08-04 12:30 | 366 | 345
2019-08-04 13:00 | 366 | 345
2019-08-04 13:30 | 369 | 349
2019-08-04 14:00 | 376 | 356
2019-08-04 14:30 | 384 | 365
2019-08-04 15:00 | 416 | 400
2019-08-04 15:30 | 437 | 423
2019-08-04 16:00 | 459 | 447
2019-08-04 16:30 | 486 | 475
2019-08-04 17:00 | 543 | 534
2019-08-04 17:30 | 579 | 572
2019-08-04 18:00 | 603 | 599
2019-08-04 18:30 | 621 | 618
2019-08-04 19:00 | 612 | 609
2019-08-04 19:30 | 615 | 612
2019-08-04 20:00 | 606 | 602
2019-08-04 20:30 | 609 | 605
2019-08-04 21:00 | 581 | 577
2019-08-04 21:30 | 566 | 561
2019-08-04 22:00 | 544 | 538
2019-08-04 22:30 | 520 | 513
2019-08-04 23:00 | 502 | 494
2019-08-04 23:30 | 480 | 470
2019-08-05 | 443 | 431
2019-08-05 00:30 | 422 | 406
2019-08-05 01:00 | 419 | 401
2019-08-05 01:30 | 412 | 393
2019-08-05 02:00 | 397 | 375
2019-08-05 02:30 | 388 | 365
2019-08-05 03:00 | 380 | 357
2019-08-05 03:30 | 376 | 353
2019-08-05 04:00 | 376 | 353
2019-08-05 04:30 | 384 | 364
2019-08-05 05:00 | 398 | 380
2019-08-05 05:30 | 428 | 414
2019-08-05 06:00 | 470 | 462
2019-08-05 06:30 | 544 | 541
2019-08-05 07:00 | 611 | 610
2019-08-05 07:30 | 643 | 642
2019-08-05 08:00 | 651 | 649
2019-08-05 08:30 | 637 | 636
2019-08-05 09:00 | 596 | 594
2019-08-05 09:30 | 558 | 556
2019-08-05 10:00 | 522 | 519
2019-08-05 10:30 | 498 | 494
2019-08-05 11:00 | 484 | 480
2019-08-05 11:30 | 486 | 483
2019-08-05 12:00 | 477 | 474
2019-08-05 12:30 | 477 | 473
2019-08-05 13:00 | 465 | 461
2019-08-05 13:30 | 464 | 462
2019-08-05 14:00 | 472 | 470
2019-08-05 14:30 | 480 | 479
2019-08-05 15:00 | 483 | 482
2019-08-05 15:30 | 498 | 497
2019-08-05 16:00 | 528 | 527
2019-08-05 16:30 | 570 | 570
2019-08-05 17:00 | 609 | 608
2019-08-05 17:30 | 642 | 640
2019-08-05 18:00 | 677 | 673
2019-08-05 18:30 | 683 | 679
2019-08-05 19:00 | 682 | 678
2019-08-05 19:30 | 669 | 664
2019-08-05 20:00 | 669 | 662
2019-08-05 20:30 | 656 | 648
2019-08-05 21:00 | 644 | 634
2019-08-05 21:30 | 623 | 610
2019-08-05 22:00 | 604 | 589
2019-08-05 22:30 | 579 | 571
2019-08-05 23:00 | 554 | 547
2019-08-05 23:30 | 524 | 518
2019-08-06 | 487 | 479
2019-08-06 00:30 | 436 | 426
2019-08-06 01:00 | 407 | 394
2019-08-06 01:30 | 400 | 386
2019-08-06 02:00 | 403 | 388
2019-08-06 02:30 | 391 | 375
2019-08-06 03:00 | 376 | 360
2019-08-06 03:30 | 362 | 346
2019-08-06 04:00 | 358 | 343
2019-08-06 04:30 | 368 | 354
2019-08-06 05:00 | 379 | 367
2019-08-06 05:30 | 413 | 405
2019-08-06 06:00 | 468 | 462
2019-08-06 06:30 | 563 | 559
2019-08-06 07:00 | 634 | 632
2019-08-06 07:30 | 668 | 666
2019-08-06 08:00 | 665 | 663
2019-08-06 08:30 | 635 | 632
2019-08-06 09:00 | 593 | 590
2019-08-06 09:30 | 556 | 553
2019-08-06 10:00 | 527 | 524
2019-08-06 10:30 | 496 | 495
2019-08-06 11:00 | 479 | 478
2019-08-06 11:30 | 466 | 464
2019-08-06 12:00 | 456 | 455
2019-08-06 12:30 | 450 | 449
2019-08-06 13:00 | 455 | 454
2019-08-06 13:30 | 466 | 465
2019-08-06 14:00 | 474 | 474
2019-08-06 14:30 | 479 | 478
2019-08-06 15:00 | 486 | 486
2019-08-06 15:30 | 491 | 490
2019-08-06 16:00 | 523 | 522
2019-08-06 16:30 | 560 | 559
2019-08-06 17:00 | 596 | 596
2019-08-06 17:30 | 631 | 629
2019-08-06 18:00 | 653 | 652
2019-08-06 18:30 | 666 | 665
2019-08-06 19:00 | 672 | 671
2019-08-06 19:30 | 668 | 667
2019-08-06 20:00 | 668 | 666
2019-08-06 20:30 | 669 | 667
2019-08-06 21:00 | 640 | 638
2019-08-06 21:30 | 622 | 619
2019-08-06 22:00 | 600 | 596
2019-08-06 22:30 | 569 | 566
2019-08-06 23:00 | 545 | 542
2019-08-06 23:30 | 525 | 520
2019-08-07 | 483 | 477
2019-08-07 00:30 | 443 | 433
2019-08-07 01:00 | 422 | 411
2019-08-07 01:30 | 409 | 396
2019-08-07 02:00 | 401 | 387
2019-08-07 02:30 | 391 | 376
2019-08-07 03:00 | 389 | 373
2019-08-07 03:30 | 389 | 373
2019-08-07 04:00 | 384 | 368
2019-08-07 04:30 | 387 | 372
2019-08-07 05:00 | 394 | 380
2019-08-07 05:30 | 421 | 411
2019-08-07 06:00 | 461 | 454
2019-08-07 06:30 | 550 | 542
2019-08-07 07:00 | 622 | 617
2019-08-07 07:30 | 672 | 668
2019-08-07 08:00 | 673 | 668
2019-08-07 08:30 | 676 | 671
2019-08-07 09:00 | 666 | 660
2019-08-07 09:30 | 634 | 627
2019-08-07 10:00 | 581 | 580
2019-08-07 10:30 | 555 | 554
2019-08-07 11:00 | 523 | 521
2019-08-07 11:30 | 506 | 504
2019-08-07 12:00 | 505 | 503
2019-08-07 12:30 | 474 | 471
2019-08-07 13:00 | 503 | 500
2019-08-07 13:30 | 539 | 537
2019-08-07 14:00 | 551 | 550
2019-08-07 14:30 | 564 | 562
2019-08-07 15:00 | 573 | 571
2019-08-07 15:30 | 582 | 580
2019-08-07 16:00 | 574 | 573
2019-08-07 16:30 | 603 | 601
2019-08-07 17:00 | 639 | 635
2019-08-07 17:30 | 665 | 660
2019-08-07 18:00 | 682 | 677
2019-08-07 18:30 | 679 | 673
2019-08-07 19:00 | 683 | 676
2019-08-07 19:30 | 658 | 653
2019-08-07 20:00 | 652 | 649
2019-08-07 20:30 | 650 | 648
2019-08-07 21:00 | 624 | 622
2019-08-07 21:30 | 599 | 596
2019-08-07 22:00 | 577 | 574
2019-08-07 22:30 | 562 | 558
2019-08-07 23:00 | 541 | 536
2019-08-07 23:30 | 500 | 496
2019-08-08 | 460 | 454
2019-08-08 00:30 | 420 | 411
2019-08-08 01:00 | 397 | 386
2019-08-08 01:30 | 388 | 377
2019-08-08 02:00 | 386 | 373
2019-08-08 02:30 | 380 | 367
2019-08-08 03:00 | 377 | 363
2019-08-08 03:30 | 381 | 367
2019-08-08 04:00 | 377 | 363
2019-08-08 04:30 | 377 | 364
2019-08-08 05:00 | 383 | 372
2019-08-08 05:30 | 411 | 403
2019-08-08 06:00 | 451 | 446
2019-08-08 06:30 | 523 | 520
2019-08-08 07:00 | 580 | 578
2019-08-08 07:30 | 602 | 601
2019-08-08 08:00 | 603 | 601
2019-08-08 08:30 | 576 | 574
2019-08-08 09:00 | 553 | 551
2019-08-08 09:30 | 568 | 566
2019-08-08 10:00 | 545 | 542
2019-08-08 10:30 | 505 | 501
2019-08-08 11:00 | 472 | 468
2019-08-08 11:30 | 454 | 451
2019-08-08 12:00 | 432 | 429
2019-08-08 12:30 | 422 | 419
2019-08-08 13:00 | 416 | 413
2019-08-08 13:30 | 428 | 425
2019-08-08 14:00 | 452 | 450
2019-08-08 14:30 | 457 | 456
2019-08-08 15:00 | 480 | 478
2019-08-08 15:30 | 512 | 511
2019-08-08 16:00 | 532 | 530
2019-08-08 16:30 | 569 | 567
2019-08-08 17:00 | 593 | 592
2019-08-08 17:30 | 605 | 603
2019-08-08 18:00 | 633 | 631
2019-08-08 18:30 | 639 | 634
2019-08-08 19:00 | 636 | 631
2019-08-08 19:30 | 609 | 608
2019-08-08 20:00 | 605 | 604
2019-08-08 20:30 | 603 | 602
2019-08-08 21:00 | 585 | 584
2019-08-08 21:30 | 563 | 561
2019-08-08 22:00 | 542 | 539
2019-08-08 22:30 | 528 | 524
2019-08-08 23:00 | 502 | 497
2019-08-08 23:30 | 476 | 470
2019-08-09 | 449 | 440
2019-08-09 00:30 | 416 | 405
2019-08-09 01:00 | 391 | 379
2019-08-09 01:30 | 378 | 365
2019-08-09 02:00 | 367 | 351
2019-08-09 02:30 | 364 | 347
2019-08-09 03:00 | 357 | 339
2019-08-09 03:30 | 351 | 334
2019-08-09 04:00 | 352 | 337
2019-08-09 04:30 | 367 | 353
2019-08-09 05:00 | 374 | 362
2019-08-09 05:30 | 394 | 384
2019-08-09 06:00 | 436 | 430
2019-08-09 06:30 | 509 | 497
2019-08-09 07:00 | 553 | 545
2019-08-09 07:30 | 579 | 573
2019-08-09 08:00 | 586 | 579
2019-08-09 08:30 | 573 | 563
2019-08-09 09:00 | 539 | 528
2019-08-09 09:30 | 531 | 519
2019-08-09 10:00 | 498 | 487
2019-08-09 10:30 | 469 | 465
2019-08-09 11:00 | 452 | 447
2019-08-09 11:30 | 432 | 428
2019-08-09 12:00 | 433 | 429
2019-08-09 12:30 | 432 | 427
2019-08-09 13:00 | 430 | 426
2019-08-09 13:30 | 438 | 434
2019-08-09 14:00 | 449 | 444
2019-08-09 14:30 | 455 | 450
2019-08-09 15:00 | 477 | 473
2019-08-09 15:30 | 496 | 493
2019-08-09 16:00 | 515 | 512
2019-08-09 16:30 | 549 | 546
2019-08-09 17:00 | 585 | 583
2019-08-09 17:30 | 608 | 606
2019-08-09 18:00 | 635 | 632
2019-08-09 18:30 | 641 | 638
2019-08-09 19:00 | 640 | 636
2019-08-09 19:30 | 612 | 609
2019-08-09 20:00 | 598 | 596
2019-08-09 20:30 | 607 | 604
2019-08-09 21:00 | 596 | 592
2019-08-09 21:30 | 578 | 573
2019-08-09 22:00 | 562 | 559
2019-08-09 22:30 | 557 | 553
2019-08-09 23:00 | 537 | 532
2019-08-09 23:30 | 508 | 502
2019-08-10 | 479 | 471
2019-08-10 00:30 | 448 | 438
2019-08-10 01:00 | 422 | 409
2019-08-10 01:30 | 398 | 384
2019-08-10 02:00 | 385 | 370
2019-08-10 02:30 | 378 | 362
2019-08-10 03:00 | 376 | 360
2019-08-10 03:30 | 373 | 356
2019-08-10 04:00 | 364 | 348
2019-08-10 04:30 | 358 | 341
2019-08-10 05:00 | 361 | 345
2019-08-10 05:30 | 367 | 352
2019-08-10 06:00 | 383 | 370
2019-08-10 06:30 | 421 | 409
2019-08-10 07:00 | 449 | 438
2019-08-10 07:30 | 473 | 464
2019-08-10 08:00 | 490 | 481
2019-08-10 08:30 | 492 | 484
2019-08-10 09:00 | 478 | 470
2019-08-10 09:30 | 451 | 444
2019-08-10 10:00 | 426 | 418
2019-08-10 10:30 | 396 | 386
2019-08-10 11:00 | 377 | 367
2019-08-10 11:30 | 368 | 358
2019-08-10 12:00 | 360 | 348
2019-08-10 12:30 | 353 | 340
2019-08-10 13:00 | 357 | 344
2019-08-10 13:30 | 359 | 346
2019-08-10 14:00 | 365 | 352
2019-08-10 14:30 | 381 | 369
2019-08-10 15:00 | 405 | 394
2019-08-10 15:30 | 428 | 419
2019-08-10 16:00 | 459 | 452
2019-08-10 16:30 | 489 | 483
2019-08-10 17:00 | 528 | 524
2019-08-10 17:30 | 547 | 543
2019-08-10 18:00 | 579 | 577
2019-08-10 18:30 | 586 | 582
2019-08-10 19:00 | 589 | 585
2019-08-10 19:30 | 582 | 578
2019-08-10 20:00 | 570 | 568
2019-08-10 20:30 | 579 | 577
2019-08-10 21:00 | 561 | 558
2019-08-10 21:30 | 552 | 549
2019-08-10 22:00 | 542 | 538
2019-08-10 22:30 | 526 | 521
2019-08-10 23:00 | 509 | 504
2019-08-10 23:30 | 497 | 491
2019-08-11 | 470 | 461
2019-08-11 00:30 | 426 | 415
2019-08-11 01:00 | 402 | 388
2019-08-11 01:30 | 391 | 376
2019-08-11 02:00 | 372 | 356
2019-08-11 02:30 | 365 | 348
2019-08-11 03:00 | 371 | 353
2019-08-11 03:30 | 363 | 343
2019-08-11 04:00 | 356 | 336
2019-08-11 04:30 | 359 | 339
2019-08-11 05:00 | 362 | 343
2019-08-11 05:30 | 368 | 350
2019-08-11 06:00 | 374 | 357
2019-08-11 06:30 | 401 | 385
2019-08-11 07:00 | 427 | 412
2019-08-11 07:30 | 456 | 442
2019-08-11 08:00 | 485 | 473
2019-08-11 08:30 | 485 | 475
2019-08-11 09:00 | 471 | 460
2019-08-11 09:30 | 451 | 440
2019-08-11 10:00 | 434 | 421
2019-08-11 10:30 | 410 | 397
2019-08-11 11:00 | 389 | 375
2019-08-11 11:30 | 374 | 359
2019-08-11 12:00 | 367 | 350
2019-08-11 12:30 | 360 | 342
2019-08-11 13:00 | 358 | 340
2019-08-11 13:30 | 363 | 344
2019-08-11 14:00 | 375 | 358
2019-08-11 14:30 | 383 | 367
2019-08-11 15:00 | 403 | 388
2019-08-11 15:30 | 425 | 411
2019-08-11 16:00 | 464 | 453
2019-08-11 16:30 | 501 | 492
2019-08-11 17:00 | 542 | 536
2019-08-11 17:30 | 575 | 571
2019-08-11 18:00 | 594 | 590
2019-08-11 18:30 | 626 | 621
2019-08-11 19:00 | 626 | 620
2019-08-11 19:30 | 609 | 603
2019-08-11 20:00 | 612 | 605
2019-08-11 20:30 | 614 | 607
2019-08-11 21:00 | 602 | 594
2019-08-11 21:30 | 582 | 573
2019-08-11 22:00 | 557 | 551
2019-08-11 22:30 | 530 | 527
2019-08-11 23:00 | 510 | 505
2019-08-11 23:30 | 473 | 467
2019-08-12 | 444 | 436
2019-08-12 00:30 | 415 | 404
2019-08-12 01:00 | 397 | 385
2019-08-12 01:30 | 382 | 368
2019-08-12 02:00 | 370 | 354
2019-08-12 02:30 | 370 | 354
2019-08-12 03:00 | 367 | 350
2019-08-12 03:30 | 363 | 347
2019-08-12 04:00 | 369 | 352
2019-08-12 04:30 | 380 | 366
2019-08-12 05:00 | 392 | 379
2019-08-12 05:30 | 417 | 407
2019-08-12 06:00 | 455 | 448
2019-08-12 06:30 | 543 | 532
2019-08-12 07:00 | 607 | 600
2019-08-12 07:30 | 646 | 641
2019-08-12 08:00 | 655 | 649
2019-08-12 08:30 | 609 | 603
2019-08-12 09:00 | 409 | 407
2019-08-12 09:30 | 393 | 392
2019-08-12 10:00 | 369 | 368
2019-08-12 10:30 | 343 | 342
2019-08-12 11:00 | 327 | 327
2019-08-12 11:30 | 317 | 317
2019-08-12 12:00 | 313 | 313
2019-08-12 12:30 | 310 | 309
2019-08-12 13:00 | 311 | 310
2019-08-12 13:30 | 311 | 310
2019-08-12 14:00 | 314 | 313
2019-08-12 14:30 | 327 | 326
2019-08-12 15:00 | 341 | 340
2019-08-12 15:30 | 349 | 348
2019-08-12 16:00 | 367 | 367
2019-08-12 16:30 | 387 | 387
2019-08-12 17:00 | 432 | 430
2019-08-12 17:30 | 463 | 460
2019-08-12 18:00 | 494 | 492
2019-08-12 18:30 | 502 | 500
2019-08-12 19:00 | 509 | 507
2019-08-12 19:30 | 505 | 503
2019-08-12 20:00 | 504 | 501
2019-08-12 20:30 | 505 | 502
2019-08-12 21:00 | 480 | 477
2019-08-12 21:30 | 460 | 456
2019-08-12 22:00 | 438 | 435
2019-08-12 22:30 | 422 | 421
2019-08-12 23:00 | 406 | 405
2019-08-12 23:30 | 388 | 387
2019-08-13 | 363 | 361
2019-08-13 00:30 | 332 | 329
2019-08-13 01:00 | 306 | 302
2019-08-13 01:30 | 291 | 286
2019-08-13 02:00 | 286 | 281
2019-08-13 02:30 | 280 | 274
2019-08-13 03:00 | 282 | 275
2019-08-13 03:30 | 285 | 278
2019-08-13 04:00 | 284 | 277
2019-08-13 04:30 | 282 | 276
2019-08-13 05:00 | 293 | 289
2019-08-13 05:30 | 314 | 311
2019-08-13 06:00 | 350 | 349
2019-08-13 06:30 | 417 | 416
2019-08-13 07:00 | 472 | 470
2019-08-13 07:30 | 512 | 508
2019-08-13 08:00 | 506 | 502
2019-08-13 08:30 | 468 | 465
2019-08-13 09:00 | 436 | 434
2019-08-13 09:30 | 408 | 405
2019-08-13 10:00 | 377 | 373
2019-08-13 10:30 | 356 | 353
2019-08-13 11:00 | 349 | 347
2019-08-13 11:30 | 341 | 339
2019-08-13 12:00 | 332 | 330
2019-08-13 12:30 | 331 | 329
2019-08-13 13:00 | 330 | 329
2019-08-13 13:30 | 335 | 333
2019-08-13 14:00 | 338 | 336
2019-08-13 14:30 | 348 | 346
2019-08-13 15:00 | 368 | 367
2019-08-13 15:30 | 378 | 376
2019-08-13 16:00 | 396 | 395
2019-08-13 16:30 | 412 | 411
2019-08-13 17:00 | 437 | 436
2019-08-13 17:30 | 464 | 461
2019-08-13 18:00 | 497 | 494
2019-08-13 18:30 | 488 | 484
2019-08-13 19:00 | 502 | 498
2019-08-13 19:30 | 493 | 490
2019-08-13 20:00 | 490 | 487
2019-08-13 20:30 | 488 | 484
2019-08-13 21:00 | 461 | 459
2019-08-13 21:30 | 447 | 445
2019-08-13 22:00 | 435 | 432
2019-08-13 22:30 | 422 | 420
2019-08-13 23:00 | 404 | 402
2019-08-13 23:30 | 391 | 388
2019-08-14 | 368 | 364
2019-08-14 00:30 | 345 | 339
2019-08-14 01:00 | 332 | 324
2019-08-14 01:30 | 323 | 313
2019-08-14 02:00 | 309 | 299
2019-08-14 02:30 | 299 | 287
2019-08-14 03:00 | 295 | 283
2019-08-14 03:30 | 295 | 283
2019-08-14 04:00 | 294 | 282
2019-08-14 04:30 | 296 | 285
2019-08-14 05:00 | 303 | 292
2019-08-14 05:30 | 316 | 307
2019-08-14 06:00 | 337 | 331
2019-08-14 06:30 | 378 | 372
2019-08-14 07:00 | 413 | 408
2019-08-14 07:30 | 443 | 439
2019-08-14 08:00 | 436 | 432
2019-08-14 08:30 | 416 | 412
2019-08-14 09:00 | 392 | 387
2019-08-14 09:30 | 373 | 369
2019-08-14 10:00 | 359 | 356
2019-08-14 10:30 | 355 | 353
2019-08-14 11:00 | 343 | 341
2019-08-14 11:30 | 338 | 336
2019-08-14 12:00 | 341 | 339
2019-08-14 12:30 | 349 | 346
2019-08-14 13:00 | 358 | 356
2019-08-14 13:30 | 367 | 364
2019-08-14 14:00 | 366 | 364
2019-08-14 14:30 | 370 | 368
2019-08-14 15:00 | 384 | 382
2019-08-14 15:30 | 398 | 397
2019-08-14 16:00 | 404 | 403
2019-08-14 16:30 | 413 | 412
2019-08-14 17:00 | 426 | 425
2019-08-14 17:30 | 438 | 437
2019-08-14 18:00 | 465 | 464
2019-08-14 18:30 | 472 | 470
2019-08-14 19:00 | 474 | 472
2019-08-14 19:30 | 473 | 471
2019-08-14 20:00 | 473 | 471
2019-08-14 20:30 | 475 | 474
2019-08-14 21:00 | 456 | 454
2019-08-14 21:30 | 435 | 433
2019-08-14 22:00 | 419 | 417
2019-08-14 22:30 | 409 | 408
2019-08-14 23:00 | 396 | 394
2019-08-14 23:30 | 372 | 369
2019-08-15 | 353 | 349
2019-08-15 00:30 | 326 | 320
2019-08-15 01:00 | 308 | 300
2019-08-15 01:30 | 296 | 288
2019-08-15 02:00 | 293 | 284
2019-08-15 02:30 | 279 | 269
2019-08-15 03:00 | 276 | 264
2019-08-15 03:30 | 273 | 262
2019-08-15 04:00 | 271 | 260
2019-08-15 04:30 | 277 | 267
2019-08-15 05:00 | 291 | 282
2019-08-15 05:30 | 306 | 300
2019-08-15 06:00 | 328 | 325
2019-08-15 06:30 | 388 | 388
2019-08-15 07:00 | 437 | 436
2019-08-15 07:30 | 467 | 467
2019-08-15 08:00 | 470 | 468
2019-08-15 08:30 | 442 | 440
2019-08-15 09:00 | 406 | 403
2019-08-15 09:30 | 379 | 378
2019-08-15 10:00 | 351 | 351
2019-08-15 10:30 | 337 | 337
2019-08-15 11:00 | 322 | 322
2019-08-15 11:30 | 315 | 315
2019-08-15 12:00 | 311 | 311
2019-08-15 12:30 | 311 | 311
2019-08-15 13:00 | 316 | 316
2019-08-15 13:30 | 324 | 323
2019-08-15 14:00 | 326 | 326
2019-08-15 14:30 | 332 | 332
2019-08-15 15:00 | 334 | 334
2019-08-15 15:30 | 341 | 341
2019-08-15 16:00 | 359 | 359
2019-08-15 16:30 | 380 | 380
2019-08-15 17:00 | 412 | 412
2019-08-15 17:30 | 439 | 438
2019-08-15 18:00 | 459 | 459
2019-08-15 18:30 | 464 | 464
2019-08-15 19:00 | 466 | 466
2019-08-15 19:30 | 463 | 463
2019-08-15 20:00 | 465 | 464
2019-08-15 20:30 | 468 | 467
2019-08-15 21:00 | 451 | 451
2019-08-15 21:30 | 428 | 428
2019-08-15 22:00 | 410 | 410
2019-08-15 22:30 | 399 | 399
2019-08-15 23:00 | 385 | 385
2019-08-15 23:30 | 364 | 364
2019-08-16 | 340 | 339
2019-08-16 00:30 | 305 | 303
2019-08-16 01:00 | 284 | 281
2019-08-16 01:30 | 271 | 267
2019-08-16 02:00 | 267 | 264
2019-08-16 02:30 | 269 | 266
2019-08-16 03:00 | 268 | 264
2019-08-16 03:30 | 265 | 260
2019-08-16 04:00 | 258 | 254
2019-08-16 04:30 | 265 | 261
2019-08-16 05:00 | 275 | 272
2019-08-16 05:30 | 293 | 291
2019-08-16 06:00 | 316 | 314
2019-08-16 06:30 | 373 | 371
2019-08-16 07:00 | 417 | 416
2019-08-16 07:30 | 448 | 447
2019-08-16 08:00 | 458 | 455
2019-08-16 08:30 | 448 | 444
2019-08-16 09:00 | 427 | 420
2019-08-16 09:30 | 383 | 377
2019-08-16 10:00 | 353 | 349
2019-08-16 10:30 | 343 | 339
2019-08-16 11:00 | 330 | 327
2019-08-16 11:30 | 322 | 319
2019-08-16 12:00 | 317 | 313
2019-08-16 12:30 | 316 | 312
2019-08-16 13:00 | 313 | 309
2019-08-16 13:30 | 318 | 315
2019-08-16 14:00 | 328 | 325
2019-08-16 14:30 | 337 | 334
2019-08-16 15:00 | 336 | 333
2019-08-16 15:30 | 346 | 343
2019-08-16 16:00 | 360 | 358
2019-08-16 16:30 | 383 | 381
2019-08-16 17:00 | 408 | 405
2019-08-16 17:30 | 420 | 417
2019-08-16 18:00 | 440 | 437
2019-08-16 18:30 | 446 | 443
2019-08-16 19:00 | 452 | 448
2019-08-16 19:30 | 446 | 442
2019-08-16 20:00 | 435 | 433
2019-08-16 20:30 | 429 | 427
2019-08-16 21:00 | 415 | 412
2019-08-16 21:30 | 404 | 401
2019-08-16 22:00 | 389 | 385
2019-08-16 22:30 | 385 | 380
2019-08-16 23:00 | 372 | 366
2019-08-16 23:30 | 352 | 345
2019-08-17 | 340 | 330
2019-08-17 00:30 | 322 | 308
2019-08-17 01:00 | 312 | 297
2019-08-17 01:30 | 302 | 285
2019-08-17 02:00 | 297 | 279
2019-08-17 02:30 | 286 | 267
2019-08-17 03:00 | 276 | 256
2019-08-17 03:30 | 277 | 256
2019-08-17 04:00 | 278 | 256
2019-08-17 04:30 | 278 | 256
2019-08-17 05:00 | 281 | 260
2019-08-17 05:30 | 283 | 263
2019-08-17 06:00 | 297 | 280
2019-08-17 06:30 | 314 | 298
2019-08-17 07:00 | 325 | 310
2019-08-17 07:30 | 339 | 326
2019-08-17 08:00 | 346 | 333
2019-08-17 08:30 | 341 | 329
2019-08-17 09:00 | 333 | 320
2019-08-17 09:30 | 324 | 311
2019-08-17 10:00 | 314 | 300
2019-08-17 10:30 | 290 | 274
2019-08-17 11:00 | 283 | 267
2019-08-17 11:30 | 275 | 259
2019-08-17 12:00 | 267 | 251
2019-08-17 12:30 | 262 | 245
2019-08-17 13:00 | 261 | 244
2019-08-17 13:30 | 267 | 250
2019-08-17 14:00 | 272 | 257
2019-08-17 14:30 | 285 | 270
2019-08-17 15:00 | 293 | 279
2019-08-17 15:30 | 317 | 305
2019-08-17 16:00 | 332 | 321
2019-08-17 16:30 | 351 | 343
2019-08-17 17:00 | 369 | 363
2019-08-17 17:30 | 378 | 372
2019-08-17 18:00 | 390 | 386
2019-08-17 18:30 | 399 | 395
2019-08-17 19:00 | 399 | 397
2019-08-17 19:30 | 388 | 386
2019-08-17 20:00 | 370 | 368
2019-08-17 20:30 | 368 | 366
2019-08-17 21:00 | 355 | 352
2019-08-17 21:30 | 344 | 340
2019-08-17 22:00 | 338 | 334
2019-08-17 22:30 | 331 | 325
2019-08-17 23:00 | 323 | 317
2019-08-17 23:30 | 315 | 308
2019-08-18 | 309 | 299
2019-08-18 00:30 | 286 | 274
2019-08-18 01:00 | 276 | 261
2019-08-18 01:30 | 270 | 253
2019-08-18 02:00 | 258 | 241
2019-08-18 02:30 | 247 | 229
2019-08-18 03:00 | 240 | 221
2019-08-18 03:30 | 234 | 215
2019-08-18 04:00 | 231 | 211
2019-08-18 04:30 | 234 | 214
2019-08-18 05:00 | 237 | 218
2019-08-18 05:30 | 243 | 224
2019-08-18 06:00 | 249 | 231
2019-08-18 06:30 | 269 | 251
2019-08-18 07:00 | 279 | 263
2019-08-18 07:30 | 296 | 280
2019-08-18 08:00 | 305 | 290
2019-08-18 08:30 | 312 | 299
2019-08-18 09:00 | 313 | 301
2019-08-18 09:30 | 308 | 296
2019-08-18 10:00 | 302 | 291
2019-08-18 10:30 | 289 | 278
2019-08-18 11:00 | 282 | 271
2019-08-18 11:30 | 281 | 269
2019-08-18 12:00 | 286 | 274
2019-08-18 12:30 | 280 | 269
2019-08-18 13:00 | 267 | 254
2019-08-18 13:30 | 268 | 255
2019-08-18 14:00 | 275 | 263
2019-08-18 14:30 | 285 | 273
2019-08-18 15:00 | 297 | 286
2019-08-18 15:30 | 321 | 312
2019-08-18 16:00 | 331 | 324
2019-08-18 16:30 | 339 | 332
2019-08-18 17:00 | 358 | 353
2019-08-18 17:30 | 373 | 368
2019-08-18 18:00 | 389 | 385
2019-08-18 18:30 | 396 | 393
2019-08-18 19:00 | 386 | 384
2019-08-18 19:30 | 383 | 380
2019-08-18 20:00 | 384 | 380
2019-08-18 20:30 | 377 | 374
2019-08-18 21:00 | 361 | 358
2019-08-18 21:30 | 351 | 348
2019-08-18 22:00 | 338 | 334
2019-08-18 22:30 | 317 | 313
2019-08-18 23:00 | 309 | 303
2019-08-18 23:30 | 301 | 295
2019-08-19 | 290 | 281
2019-08-19 00:30 | 267 | 255
2019-08-19 01:00 | 257 | 245
2019-08-19 01:30 | 256 | 242
2019-08-19 02:00 | 254 | 240
2019-08-19 02:30 | 250 | 235
2019-08-19 03:00 | 247 | 232
2019-08-19 03:30 | 248 | 233
2019-08-19 04:00 | 248 | 233
2019-08-19 04:30 | 254 | 239
2019-08-19 05:00 | 261 | 248
2019-08-19 05:30 | 279 | 269
2019-08-19 06:00 | 303 | 296
2019-08-19 06:30 | 353 | 350
2019-08-19 07:00 | 401 | 397
2019-08-19 07:30 | 429 | 427
2019-08-19 08:00 | 427 | 423
2019-08-19 08:30 | 402 | 397
2019-08-19 09:00 | 380 | 373
2019-08-19 09:30 | 362 | 359
2019-08-19 10:00 | 352 | 350
2019-08-19 10:30 | 343 | 341
2019-08-19 11:00 | 328 | 326
2019-08-19 11:30 | 323 | 321
2019-08-19 12:00 | 322 | 320
2019-08-19 12:30 | 321 | 319
2019-08-19 13:00 | 323 | 322
2019-08-19 13:30 | 332 | 331
2019-08-19 14:00 | 342 | 341
2019-08-19 14:30 | 355 | 354
2019-08-19 15:00 | 365 | 364
2019-08-19 15:30 | 384 | 379
2019-08-19 16:00 | 395 | 390
2019-08-19 16:30 | 406 | 401
2019-08-19 17:00 | 427 | 422
2019-08-19 17:30 | 446 | 443
2019-08-19 18:00 | 467 | 465
2019-08-19 18:30 | 471 | 468
2019-08-19 19:00 | 477 | 473
2019-08-19 19:30 | 469 | 465
2019-08-19 20:00 | 456 | 455
2019-08-19 20:30 | 456 | 455
2019-08-19 21:00 | 440 | 438
2019-08-19 21:30 | 420 | 417
2019-08-19 22:00 | 403 | 400
2019-08-19 22:30 | 383 | 380
2019-08-19 23:00 | 362 | 358
2019-08-19 23:30 | 342 | 337
2019-08-20 | 322 | 315
2019-08-20 00:30 | 301 | 292
2019-08-20 01:00 | 286 | 273
2019-08-20 01:30 | 275 | 260
2019-08-20 02:00 | 268 | 252
2019-08-20 02:30 | 261 | 243
2019-08-20 03:00 | 259 | 241
2019-08-20 03:30 | 262 | 244
2019-08-20 04:00 | 262 | 244
2019-08-20 04:30 | 262 | 245
2019-08-20 05:00 | 271 | 256
2019-08-20 05:30 | 288 | 277
2019-08-20 06:00 | 319 | 312
2019-08-20 06:30 | 377 | 373
2019-08-20 07:00 | 421 | 419
2019-08-20 07:30 | 447 | 445
2019-08-20 08:00 | 437 | 435
2019-08-20 08:30 | 415 | 412
2019-08-20 09:00 | 384 | 381
2019-08-20 09:30 | 365 | 362
2019-08-20 10:00 | 344 | 340
2019-08-20 10:30 | 332 | 328
2019-08-20 11:00 | 319 | 316
2019-08-20 11:30 | 311 | 307
2019-08-20 12:00 | 307 | 302
2019-08-20 12:30 | 303 | 298
2019-08-20 13:00 | 302 | 297
2019-08-20 13:30 | 304 | 300
2019-08-20 14:00 | 315 | 311
2019-08-20 14:30 | 328 | 324
2019-08-20 15:00 | 342 | 338
2019-08-20 15:30 | 360 | 357
2019-08-20 16:00 | 381 | 378
2019-08-20 16:30 | 396 | 394
2019-08-20 17:00 | 415 | 412
2019-08-20 17:30 | 438 | 435
2019-08-20 18:00 | 461 | 459
2019-08-20 18:30 | 471 | 468
2019-08-20 19:00 | 471 | 469
2019-08-20 19:30 | 470 | 467
2019-08-20 20:00 | 471 | 467
2019-08-20 20:30 | 464 | 460
2019-08-20 21:00 | 450 | 446
2019-08-20 21:30 | 427 | 423
2019-08-20 22:00 | 406 | 404
2019-08-20 22:30 | 379 | 376
2019-08-20 23:00 | 362 | 359
2019-08-20 23:30 | 347 | 341
2019-08-21 | 331 | 323
2019-08-21 00:30 | 306 | 295
2019-08-21 01:00 | 292 | 280
2019-08-21 01:30 | 290 | 276
2019-08-21 02:00 | 280 | 264
2019-08-21 02:30 | 274 | 258
2019-08-21 03:00 | 272 | 256
2019-08-21 03:30 | 271 | 256
2019-08-21 04:00 | 273 | 258
2019-08-21 04:30 | 279 | 266
2019-08-21 05:00 | 288 | 276
2019-08-21 05:30 | 304 | 296
2019-08-21 06:00 | 334 | 326
2019-08-21 06:30 | 393 | 387
2019-08-21 07:00 | 441 | 437
2019-08-21 07:30 | 462 | 458
2019-08-21 08:00 | 458 | 453
2019-08-21 08:30 | 434 | 427
2019-08-21 09:00 | 404 | 396
2019-08-21 09:30 | 381 | 373
2019-08-21 10:00 | 354 | 351
2019-08-21 10:30 | 338 | 335
2019-08-21 11:00 | 326 | 322
2019-08-21 11:30 | 317 | 313
2019-08-21 12:00 | 311 | 307
2019-08-21 12:30 | 308 | 304
2019-08-21 13:00 | 308 | 305
2019-08-21 13:30 | 313 | 310
2019-08-21 14:00 | 323 | 321
2019-08-21 14:30 | 337 | 334
2019-08-21 15:00 | 347 | 345
2019-08-21 15:30 | 356 | 354
2019-08-21 16:00 | 375 | 373
2019-08-21 16:30 | 393 | 392
2019-08-21 17:00 | 411 | 410
2019-08-21 17:30 | 426 | 424
2019-08-21 18:00 | 436 | 435
2019-08-21 18:30 | 442 | 441
2019-08-21 19:00 | 451 | 447
2019-08-21 19:30 | 451 | 445
2019-08-21 20:00 | 447 | 440
2019-08-21 20:30 | 442 | 434
2019-08-21 21:00 | 422 | 419
2019-08-21 21:30 | 404 | 401
2019-08-21 22:00 | 383 | 380
2019-08-21 22:30 | 370 | 366
2019-08-21 23:00 | 352 | 347
2019-08-21 23:30 | 336 | 330
2019-08-22 | 326 | 317
2019-08-22 00:30 | 301 | 289
2019-08-22 01:00 | 285 | 272
2019-08-22 01:30 | 281 | 267
2019-08-22 02:00 | 275 | 260
2019-08-22 02:30 | 268 | 252
2019-08-22 03:00 | 263 | 248
2019-08-22 03:30 | 262 | 247
2019-08-22 04:00 | 262 | 247
2019-08-22 04:30 | 271 | 257
2019-08-22 05:00 | 279 | 266
2019-08-22 05:30 | 289 | 279
2019-08-22 06:00 | 303 | 297
2019-08-22 06:30 | 349 | 345
2019-08-22 07:00 | 399 | 395
2019-08-22 07:30 | 425 | 417
2019-08-22 08:00 | 413 | 405
2019-08-22 08:30 | 396 | 387
2019-08-22 09:00 | 366 | 360
2019-08-22 09:30 | 352 | 348
2019-08-22 10:00 | 334 | 329
2019-08-22 10:30 | 320 | 315
2019-08-22 11:00 | 311 | 306
2019-08-22 11:30 | 304 | 299
2019-08-22 12:00 | 300 | 295
2019-08-22 12:30 | 306 | 301
2019-08-22 13:00 | 311 | 306
2019-08-22 13:30 | 316 | 311
2019-08-22 14:00 | 327 | 323
2019-08-22 14:30 | 340 | 336
2019-08-22 15:00 | 345 | 341
2019-08-22 15:30 | 357 | 353
2019-08-22 16:00 | 371 | 368
2019-08-22 16:30 | 388 | 385
2019-08-22 17:00 | 410 | 408
2019-08-22 17:30 | 438 | 432
2019-08-22 18:00 | 462 | 457
2019-08-22 18:30 | 477 | 471
2019-08-22 19:00 | 481 | 474
2019-08-22 19:30 | 469 | 462
2019-08-22 20:00 | 461 | 453
2019-08-22 20:30 | 460 | 454
2019-08-22 21:00 | 445 | 440
2019-08-22 21:30 | 427 | 419
2019-08-22 22:00 | 407 | 398
2019-08-22 22:30 | 394 | 388
2019-08-22 23:00 | 377 | 372
2019-08-22 23:30 | 369 | 362
2019-08-23 | 343 | 335
2019-08-23 00:30 | 319 | 309
2019-08-23 01:00 | 309 | 297
2019-08-23 01:30 | 303 | 291
2019-08-23 02:00 | 299 | 285
2019-08-23 02:30 | 287 | 271
2019-08-23 03:00 | 281 | 265
2019-08-23 03:30 | 280 | 264
2019-08-23 04:00 | 282 | 266
2019-08-23 04:30 | 290 | 276
2019-08-23 05:00 | 302 | 289
2019-08-23 05:30 | 315 | 305
2019-08-23 06:00 | 333 | 326
2019-08-23 06:30 | 386 | 381
2019-08-23 07:00 | 431 | 423
2019-08-23 07:30 | 453 | 445
2019-08-23 08:00 | 449 | 440
2019-08-23 08:30 | 429 | 419
2019-08-23 09:00 | 399 | 394
2019-08-23 09:30 | 380 | 375
2019-08-23 10:00 | 356 | 352
2019-08-23 10:30 | 343 | 339
2019-08-23 11:00 | 329 | 326
2019-08-23 11:30 | 319 | 316
2019-08-23 12:00 | 315 | 311
2019-08-23 12:30 | 313 | 310
2019-08-23 13:00 | 315 | 311
2019-08-23 13:30 | 320 | 316
2019-08-23 14:00 | 326 | 323
2019-08-23 14:30 | 337 | 334
2019-08-23 15:00 | 347 | 344
2019-08-23 15:30 | 362 | 359
2019-08-23 16:00 | 382 | 379
2019-08-23 16:30 | 395 | 393
2019-08-23 17:00 | 424 | 421
2019-08-23 17:30 | 446 | 441
2019-08-23 18:00 | 455 | 451
2019-08-23 18:30 | 454 | 449
2019-08-23 19:00 | 456 | 450
2019-08-23 19:30 | 453 | 447
2019-08-23 20:00 | 445 | 439
2019-08-23 20:30 | 443 | 437
2019-08-23 21:00 | 426 | 424
2019-08-23 21:30 | 413 | 410
2019-08-23 22:00 | 407 | 403
2019-08-23 22:30 | 396 | 391
2019-08-23 23:00 | 378 | 373
2019-08-23 23:30 | 360 | 354
2019-08-24 | 344 | 335
2019-08-24 00:30 | 333 | 321
2019-08-24 01:00 | 317 | 304
2019-08-24 01:30 | 300 | 285
2019-08-24 02:00 | 287 | 270
2019-08-24 02:30 | 278 | 260
2019-08-24 03:00 | 274 | 257
2019-08-24 03:30 | 276 | 259
2019-08-24 04:00 | 271 | 254
2019-08-24 04:30 | 273 | 256
2019-08-24 05:00 | 278 | 261
2019-08-24 05:30 | 288 | 273
2019-08-24 06:00 | 296 | 282
2019-08-24 06:30 | 316 | 303
2019-08-24 07:00 | 335 | 323
2019-08-24 07:30 | 348 | 339
2019-08-24 08:00 | 356 | 348
2019-08-24 08:30 | 355 | 347
2019-08-24 09:00 | 337 | 329
2019-08-24 09:30 | 319 | 310
2019-08-24 10:00 | 304 | 294
2019-08-24 10:30 | 295 | 284
2019-08-24 11:00 | 290 | 279
2019-08-24 11:30 | 289 | 278
2019-08-24 12:00 | 278 | 267
2019-08-24 12:30 | 268 | 256
2019-08-24 13:00 | 273 | 261
2019-08-24 13:30 | 276 | 265
2019-08-24 14:00 | 278 | 266
2019-08-24 14:30 | 285 | 273
2019-08-24 15:00 | 290 | 278
2019-08-24 15:30 | 310 | 299
2019-08-24 16:00 | 325 | 316
2019-08-24 16:30 | 340 | 332
2019-08-24 17:00 | 361 | 355
2019-08-24 17:30 | 369 | 364
2019-08-24 18:00 | 382 | 372
2019-08-24 18:30 | 387 | 378
2019-08-24 19:00 | 387 | 378
2019-08-24 19:30 | 383 | 375
2019-08-24 20:00 | 377 | 373
2019-08-24 20:30 | 377 | 373
2019-08-24 21:00 | 366 | 361
2019-08-24 21:30 | 361 | 355
2019-08-24 22:00 | 359 | 353
2019-08-24 22:30 | 359 | 352
2019-08-24 23:00 | 357 | 350
2019-08-24 23:30 | 350 | 342
2019-08-25 | 339 | 329
2019-08-25 00:30 | 324 | 312
2019-08-25 01:00 | 315 | 301
2019-08-25 01:30 | 305 | 290
2019-08-25 02:00 | 291 | 275
2019-08-25 02:30 | 284 | 266
2019-08-25 03:00 | 277 | 258
2019-08-25 03:30 | 274 | 254
2019-08-25 04:00 | 280 | 255
2019-08-25 04:30 | 280 | 255
2019-08-25 05:00 | 280 | 256
2019-08-25 05:30 | 286 | 263
2019-08-25 06:00 | 294 | 272
2019-08-25 06:30 | 311 | 289
2019-08-25 07:00 | 322 | 302
2019-08-25 07:30 | 328 | 310
2019-08-25 08:00 | 332 | 314
2019-08-25 08:30 | 330 | 312
2019-08-25 09:00 | 319 | 307
2019-08-25 09:30 | 308 | 296
2019-08-25 10:00 | 290 | 276
2019-08-25 10:30 | 281 | 267
2019-08-25 11:00 | 271 | 257
2019-08-25 11:30 | 263 | 250
2019-08-25 12:00 | 258 | 244
2019-08-25 12:30 | 259 | 245
2019-08-25 13:00 | 261 | 248
2019-08-25 13:30 | 265 | 252
2019-08-25 14:00 | 274 | 260
2019-08-25 14:30 | 280 | 268
2019-08-25 15:00 | 296 | 285
2019-08-25 15:30 | 314 | 304
2019-08-25 16:00 | 329 | 321
2019-08-25 16:30 | 353 | 345
2019-08-25 17:00 | 382 | 375
2019-08-25 17:30 | 407 | 398
2019-08-25 18:00 | 419 | 410
2019-08-25 18:30 | 431 | 423
2019-08-25 19:00 | 434 | 426
2019-08-25 19:30 | 427 | 419
2019-08-25 20:00 | 422 | 414
2019-08-25 20:30 | 420 | 411
2019-08-25 21:00 | 402 | 398
2019-08-25 21:30 | 395 | 390
2019-08-25 22:00 | 382 | 377
2019-08-25 22:30 | 367 | 360
2019-08-25 23:00 | 359 | 351
2019-08-25 23:30 | 347 | 338
2019-08-26 | 332 | 321
2019-08-26 00:30 | 311 | 298
2019-08-26 01:00 | 304 | 290
2019-08-26 01:30 | 296 | 280
2019-08-26 02:00 | 284 | 268
2019-08-26 02:30 | 284 | 267
2019-08-26 03:00 | 285 | 268
2019-08-26 03:30 | 285 | 268
2019-08-26 04:00 | 286 | 270
2019-08-26 04:30 | 293 | 277
2019-08-26 05:00 | 299 | 285
2019-08-26 05:30 | 316 | 305
2019-08-26 06:00 | 339 | 331
2019-08-26 06:30 | 389 | 383
2019-08-26 07:00 | 415 | 411
2019-08-26 07:30 | 435 | 431
2019-08-26 08:00 | 426 | 422
2019-08-26 08:30 | 404 | 399
2019-08-26 09:00 | 381 | 376
2019-08-26 09:30 | 365 | 361
2019-08-26 10:00 | 355 | 350
2019-08-26 10:30 | 347 | 342
2019-08-26 11:00 | 338 | 333
2019-08-26 11:30 | 330 | 327
2019-08-26 12:00 | 328 | 325
2019-08-26 12:30 | 332 | 329
2019-08-26 13:00 | 340 | 337
2019-08-26 13:30 | 354 | 350
2019-08-26 14:00 | 371 | 367
2019-08-26 14:30 | 390 | 385
2019-08-26 15:00 | 401 | 397
2019-08-26 15:30 | 408 | 403
2019-08-26 16:00 | 418 | 413
2019-08-26 16:30 | 437 | 432
2019-08-26 17:00 | 451 | 447
2019-08-26 17:30 | 465 | 461
2019-08-26 18:00 | 475 | 471
2019-08-26 18:30 | 485 | 477
2019-08-26 19:00 | 487 | 478
2019-08-26 19:30 | 471 | 463
2019-08-26 20:00 | 461 | 455
2019-08-26 20:30 | 455 | 450
2019-08-26 21:00 | 444 | 437
2019-08-26 21:30 | 426 | 420
2019-08-26 22:00 | 411 | 408
2019-08-26 22:30 | 408 | 404
2019-08-26 23:00 | 393 | 388
2019-08-26 23:30 | 381 | 375
2019-08-27 | 363 | 355
2019-08-27 00:30 | 339 | 328
2019-08-27 01:00 | 327 | 314
2019-08-27 01:30 | 315 | 301
2019-08-27 02:00 | 315 | 299
2019-08-27 02:30 | 310 | 294
2019-08-27 03:00 | 308 | 292
2019-08-27 03:30 | 308 | 292
2019-08-27 04:00 | 309 | 293
2019-08-27 04:30 | 313 | 298
2019-08-27 05:00 | 321 | 307
2019-08-27 05:30 | 343 | 332
2019-08-27 06:00 | 364 | 356
2019-08-27 06:30 | 395 | 390
2019-08-27 07:00 | 426 | 422
2019-08-27 07:30 | 460 | 453
2019-08-27 08:00 | 475 | 461
2019-08-27 08:30 | 464 | 450
2019-08-27 09:00 | 443 | 430
2019-08-27 09:30 | 426 | 414
2019-08-27 10:00 | 398 | 387
2019-08-27 10:30 | 383 | 373
2019-08-27 11:00 | 378 | 369
2019-08-27 11:30 | 375 | 366
2019-08-27 12:00 | 377 | 368
2019-08-27 12:30 | 377 | 369
2019-08-27 13:00 | 374 | 366
2019-08-27 13:30 | 372 | 364
2019-08-27 14:00 | 378 | 371
2019-08-27 14:30 | 379 | 372
2019-08-27 15:00 | 383 | 376
2019-08-27 15:30 | 399 | 392
2019-08-27 16:00 | 420 | 413
2019-08-27 16:30 | 428 | 421
2019-08-27 17:00 | 445 | 437
2019-08-27 17:30 | 455 | 447
2019-08-27 18:00 | 466 | 459
2019-08-27 18:30 | 466 | 457
2019-08-27 19:00 | 471 | 461
2019-08-27 19:30 | 469 | 462
2019-08-27 20:00 | 469 | 461
2019-08-27 20:30 | 467 | 458
2019-08-27 21:00 | 447 | 438
2019-08-27 21:30 | 428 | 418
2019-08-27 22:00 | 413 | 404
2019-08-27 22:30 | 404 | 399
2019-08-27 23:00 | 395 | 389
2019-08-27 23:30 | 382 | 375
2019-08-28 | 361 | 351
2019-08-28 00:30 | 340 | 328
2019-08-28 01:00 | 325 | 311
2019-08-28 01:30 | 315 | 300
2019-08-28 02:00 | 308 | 292
2019-08-28 02:30 | 303 | 286
2019-08-28 03:00 | 301 | 284
2019-08-28 03:30 | 298 | 279
2019-08-28 04:00 | 299 | 281
2019-08-28 04:30 | 303 | 286
2019-08-28 05:00 | 310 | 294
2019-08-28 05:30 | 329 | 316
2019-08-28 06:00 | 354 | 344
2019-08-28 06:30 | 382 | 375
2019-08-28 07:00 | 406 | 401
2019-08-28 07:30 | 424 | 420
2019-08-28 08:00 | 423 | 418
2019-08-28 08:30 | 416 | 411
2019-08-28 09:00 | 413 | 409
2019-08-28 09:30 | 420 | 416
2019-08-28 10:00 | 424 | 420
2019-08-28 10:30 | 415 | 411
2019-08-28 11:00 | 411 | 407
2019-08-28 11:30 | 430 | 427
2019-08-28 12:00 | 432 | 429
2019-08-28 12:30 | 421 | 416
2019-08-28 13:00 | 416 | 410
2019-08-28 13:30 | 423 | 418
2019-08-28 14:00 | 429 | 425
2019-08-28 14:30 | 434 | 430
2019-08-28 15:00 | 433 | 428
2019-08-28 15:30 | 433 | 428
2019-08-28 16:00 | 436 | 432
2019-08-28 16:30 | 440 | 435
2019-08-28 17:00 | 448 | 444
2019-08-28 17:30 | 454 | 450
2019-08-28 18:00 | 470 | 466
2019-08-28 18:30 | 476 | 471
2019-08-28 19:00 | 477 | 472
2019-08-28 19:30 | 473 | 467
2019-08-28 20:00 | 473 | 467
2019-08-28 20:30 | 472 | 465
2019-08-28 21:00 | 456 | 451
2019-08-28 21:30 | 438 | 433
2019-08-28 22:00 | 424 | 418
2019-08-28 22:30 | 408 | 401
2019-08-28 23:00 | 395 | 387
2019-08-28 23:30 | 381 | 373
2019-08-29 | 366 | 356
2019-08-29 00:30 | 351 | 339
2019-08-29 01:00 | 335 | 321
2019-08-29 01:30 | 325 | 311
2019-08-29 02:00 | 315 | 299
2019-08-29 02:30 | 311 | 294
2019-08-29 03:00 | 306 | 288
2019-08-29 03:30 | 303 | 285
2019-08-29 04:00 | 303 | 287
2019-08-29 04:30 | 304 | 288
2019-08-29 05:00 | 310 | 296
2019-08-29 05:30 | 331 | 319
2019-08-29 06:00 | 352 | 344
2019-08-29 06:30 | 386 | 381
2019-08-29 07:00 | 419 | 412
2019-08-29 07:30 | 448 | 440
2019-08-29 08:00 | 461 | 453
2019-08-29 08:30 | 459 | 451
2019-08-29 09:00 | 443 | 434
2019-08-29 09:30 | 452 | 443
2019-08-29 10:00 | 454 | 445
2019-08-29 10:30 | 442 | 432
2019-08-29 11:00 | 430 | 420
2019-08-29 11:30 | 430 | 421
2019-08-29 12:00 | 437 | 427
2019-08-29 12:30 | 439 | 430
2019-08-29 13:00 | 450 | 441
2019-08-29 13:30 | 450 | 442
2019-08-29 14:00 | 449 | 441
2019-08-29 14:30 | 448 | 440
2019-08-29 15:00 | 445 | 436
2019-08-29 15:30 | 446 | 437
2019-08-29 16:00 | 449 | 439
2019-08-29 16:30 | 451 | 442
2019-08-29 17:00 | 462 | 454
2019-08-29 17:30 | 468 | 461
2019-08-29 18:00 | 466 | 460
2019-08-29 18:30 | 477 | 468
2019-08-29 19:00 | 487 | 478
2019-08-29 19:30 | 480 | 470
2019-08-29 20:00 | 481 | 471
2019-08-29 20:30 | 486 | 476
2019-08-29 21:00 | 484 | 472
2019-08-29 21:30 | 453 | 446
2019-08-29 22:00 | 439 | 431
2019-08-29 22:30 | 427 | 421
2019-08-29 23:00 | 415 | 408
2019-08-29 23:30 | 395 | 386
2019-08-30 | 373 | 364
2019-08-30 00:30 | 355 | 343
2019-08-30 01:00 | 333 | 319
2019-08-30 01:30 | 329 | 315
2019-08-30 02:00 | 318 | 303
2019-08-30 02:30 | 307 | 291
2019-08-30 03:00 | 304 | 287
2019-08-30 03:30 | 304 | 287
2019-08-30 04:00 | 306 | 290
2019-08-30 04:30 | 311 | 295
2019-08-30 05:00 | 316 | 301
2019-08-30 05:30 | 330 | 317
2019-08-30 06:00 | 349 | 339
2019-08-30 06:30 | 390 | 383
2019-08-30 07:00 | 416 | 410
2019-08-30 07:30 | 432 | 423
2019-08-30 08:00 | 422 | 412
2019-08-30 08:30 | 407 | 398
2019-08-30 09:00 | 386 | 377
2019-08-30 09:30 | 368 | 359
2019-08-30 10:00 | 344 | 341
2019-08-30 10:30 | 342 | 338
2019-08-30 11:00 | 338 | 334
2019-08-30 11:30 | 338 | 334
2019-08-30 12:00 | 334 | 331
2019-08-30 12:30 | 335 | 332
2019-08-30 13:00 | 337 | 333
2019-08-30 13:30 | 350 | 346
2019-08-30 14:00 | 342 | 336
2019-08-30 14:30 | 345 | 339
2019-08-30 15:00 | 349 | 342
2019-08-30 15:30 | 364 | 358
2019-08-30 16:00 | 388 | 383
2019-08-30 16:30 | 408 | 403
2019-08-30 17:00 | 422 | 418
2019-08-30 17:30 | 433 | 430
2019-08-30 18:00 | 445 | 443
2019-08-30 18:30 | 457 | 454
2019-08-30 19:00 | 465 | 461
2019-08-30 19:30 | 460 | 456
2019-08-30 20:00 | 457 | 452
2019-08-30 20:30 | 455 | 450
2019-08-30 21:00 | 442 | 437
2019-08-30 21:30 | 436 | 431
2019-08-30 22:00 | 424 | 420
2019-08-30 22:30 | 417 | 412
2019-08-30 23:00 | 411 | 404
2019-08-30 23:30 | 399 | 391
2019-08-31 | 378 | 368
2019-08-31 00:30 | 356 | 343
2019-08-31 01:00 | 339 | 319
2019-08-31 01:30 | 331 | 308
2019-08-31 02:00 | 315 | 291
2019-08-31 02:30 | 312 | 287
2019-08-31 03:00 | 311 | 285
2019-08-31 03:30 | 307 | 280
2019-08-31 04:00 | 302 | 273
2019-08-31 04:30 | 302 | 273
2019-08-31 05:00 | 303 | 275
2019-08-31 05:30 | 304 | 278
2019-08-31 06:00 | 313 | 289
2019-08-31 06:30 | 336 | 313
2019-08-31 07:00 | 356 | 335
2019-08-31 07:30 | 367 | 347
2019-08-31 08:00 | 362 | 343
2019-08-31 08:30 | 355 | 336
2019-08-31 09:00 | 348 | 328
2019-08-31 09:30 | 340 | 320
2019-08-31 10:00 | 326 | 305
2019-08-31 10:30 | 311 | 289
2019-08-31 11:00 | 300 | 278
2019-08-31 11:30 | 293 | 271
2019-08-31 12:00 | 292 | 270
2019-08-31 12:30 | 296 | 274
2019-08-31 13:00 | 299 | 278
2019-08-31 13:30 | 299 | 278
2019-08-31 14:00 | 300 | 278
2019-08-31 14:30 | 310 | 289
2019-08-31 15:00 | 329 | 310
2019-08-31 15:30 | 341 | 324
2019-08-31 16:00 | 353 | 337
2019-08-31 16:30 | 372 | 358
2019-08-31 17:00 | 390 | 378
2019-08-31 17:30 | 402 | 392
2019-08-31 18:00 | 416 | 408
2019-08-31 18:30 | 431 | 424
2019-08-31 19:00 | 433 | 425
2019-08-31 19:30 | 430 | 421
2019-08-31 20:00 | 432 | 423
2019-08-31 20:30 | 425 | 417
2019-08-31 21:00 | 419 | 410
2019-08-31 21:30 | 409 | 400
2019-08-31 22:00 | 403 | 392
2019-08-31 22:30 | 396 | 385
2019-08-31 23:00 | 391 | 379
2019-08-31 23:30 | 383 | 369
2019-09-01 | 373 | 355
2019-09-01 00:30 | 349 | 328
2019-09-01 01:00 | 332 | 308
2019-09-01 01:30 | 320 | 294
2019-09-01 02:00 | 311 | 284
2019-09-01 02:30 | 312 | 284
2019-09-01 03:00 | 319 | 290
2019-09-01 03:30 | 312 | 283
2019-09-01 04:00 | 306 | 278
2019-09-01 04:30 | 302 | 274
2019-09-01 05:00 | 295 | 267
2019-09-01 05:30 | 291 | 265
2019-09-01 06:00 | 295 | 269
2019-09-01 06:30 | 310 | 285
2019-09-01 07:00 | 316 | 294
2019-09-01 07:30 | 321 | 310
2019-09-01 08:00 | 326 | 316
2019-09-01 08:30 | 323 | 313
2019-09-01 09:00 | 316 | 306
2019-09-01 09:30 | 307 | 298
2019-09-01 10:00 | 295 | 285
2019-09-01 10:30 | 281 | 271
2019-09-01 11:00 | 268 | 258
2019-09-01 11:30 | 257 | 247
2019-09-01 12:00 | 247 | 236
2019-09-01 12:30 | 242 | 231
2019-09-01 13:00 | 242 | 231
2019-09-01 13:30 | 246 | 235
2019-09-01 14:00 | 256 | 246
2019-09-01 14:30 | 268 | 259
2019-09-01 15:00 | 284 | 276
2019-09-01 15:30 | 299 | 291
2019-09-01 16:00 | 319 | 312
2019-09-01 16:30 | 341 | 336
2019-09-01 17:00 | 364 | 360
2019-09-01 17:30 | 377 | 373
2019-09-01 18:00 | 385 | 382
2019-09-01 18:30 | 396 | 394
2019-09-01 19:00 | 400 | 398
2019-09-01 19:30 | 397 | 395
2019-09-01 20:00 | 397 | 395
2019-09-01 20:30 | 404 | 401
2019-09-01 21:00 | 397 | 395
2019-09-01 21:30 | 388 | 384
2019-09-01 22:00 | 380 | 376
2019-09-01 22:30 | 373 | 368
2019-09-01 23:00 | 364 | 359
2019-09-01 23:30 | 345 | 338
2019-09-02 | 320 | 312
2019-09-02 00:30 | 305 | 296
2019-09-02 01:00 | 295 | 285
2019-09-02 01:30 | 286 | 274
2019-09-02 02:00 | 272 | 260
2019-09-02 02:30 | 262 | 250
2019-09-02 03:00 | 259 | 246
2019-09-02 03:30 | 257 | 244
2019-09-02 04:00 | 254 | 242
2019-09-02 04:30 | 262 | 251
2019-09-02 05:00 | 271 | 262
2019-09-02 05:30 | 296 | 289
2019-09-02 06:00 | 324 | 319
2019-09-02 06:30 | 375 | 373
2019-09-02 07:00 | 413 | 411
2019-09-02 07:30 | 426 | 424
2019-09-02 08:00 | 414 | 412
2019-09-02 08:30 | 392 | 389
2019-09-02 09:00 | 368 | 365
2019-09-02 09:30 | 348 | 346
2019-09-02 10:00 | 326 | 326
2019-09-02 10:30 | 317 | 317
2019-09-02 11:00 | 309 | 309
2019-09-02 11:30 | 303 | 303
2019-09-02 12:00 | 303 | 302
2019-09-02 12:30 | 304 | 304
2019-09-02 13:00 | 306 | 306
2019-09-02 13:30 | 314 | 314
2019-09-02 14:00 | 323 | 323
2019-09-02 14:30 | 335 | 335
2019-09-02 15:00 | 352 | 351
2019-09-02 15:30 | 366 | 364
2019-09-02 16:00 | 387 | 385
2019-09-02 16:30 | 411 | 410
2019-09-02 17:00 | 435 | 433
2019-09-02 17:30 | 445 | 444
2019-09-02 18:00 | 455 | 454
2019-09-02 18:30 | 460 | 459
2019-09-02 19:00 | 462 | 461
2019-09-02 19:30 | 455 | 453
2019-09-02 20:00 | 450 | 447
2019-09-02 20:30 | 445 | 442
2019-09-02 21:00 | 433 | 430
2019-09-02 21:30 | 415 | 410
2019-09-02 22:00 | 400 | 397
2019-09-02 22:30 | 388 | 387
2019-09-02 23:00 | 376 | 374
2019-09-02 23:30 | 362 | 360
2019-09-03 | 339 | 335
2019-09-03 00:30 | 315 | 311
2019-09-03 01:00 | 296 | 291
2019-09-03 01:30 | 288 | 282
2019-09-03 02:00 | 274 | 268
2019-09-03 02:30 | 270 | 264
2019-09-03 03:00 | 269 | 262
2019-09-03 03:30 | 269 | 262
2019-09-03 04:00 | 272 | 264
2019-09-03 04:30 | 281 | 275
2019-09-03 05:00 | 288 | 282
2019-09-03 05:30 | 307 | 303
2019-09-03 06:00 | 336 | 333
2019-09-03 06:30 | 387 | 385
2019-09-03 07:00 | 415 | 414
2019-09-03 07:30 | 427 | 425
2019-09-03 08:00 | 411 | 410
2019-09-03 08:30 | 388 | 386
2019-09-03 09:00 | 365 | 363
2019-09-03 09:30 | 346 | 345
2019-09-03 10:00 | 332 | 332
2019-09-03 10:30 | 321 | 321
2019-09-03 11:00 | 314 | 313
2019-09-03 11:30 | 309 | 309
2019-09-03 12:00 | 309 | 309
2019-09-03 12:30 | 310 | 309
2019-09-03 13:00 | 315 | 314
2019-09-03 13:30 | 321 | 321
2019-09-03 14:00 | 332 | 331
2019-09-03 14:30 | 340 | 340
2019-09-03 15:00 | 354 | 354
2019-09-03 15:30 | 368 | 367
2019-09-03 16:00 | 386 | 386
2019-09-03 16:30 | 401 | 401
2019-09-03 17:00 | 417 | 417
2019-09-03 17:30 | 433 | 432
2019-09-03 18:00 | 444 | 443
2019-09-03 18:30 | 455 | 454
2019-09-03 19:00 | 459 | 458
2019-09-03 19:30 | 457 | 455
2019-09-03 20:00 | 454 | 451
2019-09-03 20:30 | 452 | 448
2019-09-03 21:00 | 440 | 436
2019-09-03 21:30 | 422 | 419
2019-09-03 22:00 | 410 | 406
2019-09-03 22:30 | 399 | 395
2019-09-03 23:00 | 382 | 381
2019-09-03 23:30 | 366 | 364
2019-09-04 | 345 | 342
2019-09-04 00:30 | 322 | 318
2019-09-04 01:00 | 307 | 303
2019-09-04 01:30 | 298 | 293
2019-09-04 02:00 | 289 | 284
2019-09-04 02:30 | 281 | 276
2019-09-04 03:00 | 279 | 274
2019-09-04 03:30 | 280 | 275
2019-09-04 04:00 | 279 | 274
2019-09-04 04:30 | 284 | 279
2019-09-04 05:00 | 290 | 285
2019-09-04 05:30 | 309 | 306
2019-09-04 06:00 | 339 | 338
2019-09-04 06:30 | 384 | 383
2019-09-04 07:00 | 405 | 403
2019-09-04 07:30 | 401 | 401
2019-09-04 08:00 | 377 | 376
2019-09-04 08:30 | 354 | 354
2019-09-04 09:00 | 330 | 330
2019-09-04 09:30 | 314 | 314
2019-09-04 10:00 | 298 | 298
2019-09-04 10:30 | 295 | 294
2019-09-04 11:00 | 292 | 291
2019-09-04 11:30 | 290 | 290
2019-09-04 12:00 | 288 | 288
2019-09-04 12:30 | 291 | 291
2019-09-04 13:00 | 303 | 303
2019-09-04 13:30 | 315 | 313
2019-09-04 14:00 | 325 | 323
2019-09-04 14:30 | 340 | 340
2019-09-04 15:00 | 356 | 356
2019-09-04 15:30 | 368 | 367
2019-09-04 16:00 | 383 | 383
2019-09-04 16:30 | 401 | 400
2019-09-04 17:00 | 422 | 419
2019-09-04 17:30 | 429 | 425
2019-09-04 18:00 | 449 | 445
2019-09-04 18:30 | 463 | 459
2019-09-04 19:00 | 466 | 462
2019-09-04 19:30 | 452 | 447
2019-09-04 20:00 | 452 | 444
2019-09-04 20:30 | 443 | 439
2019-09-04 21:00 | 425 | 422
2019-09-04 21:30 | 410 | 406
2019-09-04 22:00 | 396 | 392
2019-09-04 22:30 | 388 | 385
2019-09-04 23:00 | 376 | 372
2019-09-04 23:30 | 357 | 351
2019-09-05 | 342 | 335
2019-09-05 00:30 | 318 | 310
2019-09-05 01:00 | 306 | 297
2019-09-05 01:30 | 299 | 289
2019-09-05 02:00 | 292 | 281
2019-09-05 02:30 | 285 | 275
2019-09-05 03:00 | 287 | 277
2019-09-05 03:30 | 286 | 276
2019-09-05 04:00 | 288 | 279
2019-09-05 04:30 | 295 | 286
2019-09-05 05:00 | 303 | 295
2019-09-05 05:30 | 323 | 317
2019-09-05 06:00 | 349 | 344
2019-09-05 06:30 | 375 | 373
2019-09-05 07:00 | 390 | 389
2019-09-05 07:30 | 393 | 392
2019-09-05 08:00 | 384 | 382
2019-09-05 08:30 | 357 | 355
2019-09-05 09:00 | 337 | 336
2019-09-05 09:30 | 323 | 322
2019-09-05 10:00 | 310 | 309
2019-09-05 10:30 | 306 | 306
2019-09-05 11:00 | 298 | 297
2019-09-05 11:30 | 295 | 295
2019-09-05 12:00 | 296 | 296
2019-09-05 12:30 | 299 | 299
2019-09-05 13:00 | 309 | 309
2019-09-05 13:30 | 322 | 322
2019-09-05 14:00 | 336 | 336
2019-09-05 14:30 | 352 | 351
2019-09-05 15:00 | 364 | 362
2019-09-05 15:30 | 375 | 373
2019-09-05 16:00 | 393 | 389
2019-09-05 16:30 | 413 | 410
2019-09-05 17:00 | 440 | 436
2019-09-05 17:30 | 454 | 448
2019-09-05 18:00 | 465 | 460
2019-09-05 18:30 | 471 | 465
2019-09-05 19:00 | 471 | 466
2019-09-05 19:30 | 466 | 459
2019-09-05 20:00 | 460 | 453
2019-09-05 20:30 | 447 | 445
2019-09-05 21:00 | 438 | 434
2019-09-05 21:30 | 420 | 416
2019-09-05 22:00 | 403 | 400
2019-09-05 22:30 | 399 | 394
2019-09-05 23:00 | 389 | 384
2019-09-05 23:30 | 373 | 367
2019-09-06 | 351 | 344
2019-09-06 00:30 | 322 | 313
2019-09-06 01:00 | 301 | 291
2019-09-06 01:30 | 290 | 278
2019-09-06 02:00 | 283 | 269
2019-09-06 02:30 | 276 | 259
2019-09-06 03:00 | 275 | 258
2019-09-06 03:30 | 275 | 258
2019-09-06 04:00 | 274 | 258
2019-09-06 04:30 | 278 | 262
2019-09-06 05:00 | 283 | 268
2019-09-06 05:30 | 300 | 287
2019-09-06 06:00 | 316 | 306
2019-09-06 06:30 | 361 | 353
2019-09-06 07:00 | 385 | 380
2019-09-06 07:30 | 397 | 393
2019-09-06 08:00 | 395 | 392
2019-09-06 08:30 | 382 | 379
2019-09-06 09:00 | 374 | 370
2019-09-06 09:30 | 364 | 360
2019-09-06 10:00 | 352 | 349
2019-09-06 10:30 | 349 | 346
2019-09-06 11:00 | 346 | 344
2019-09-06 11:30 | 344 | 341
2019-09-06 12:00 | 353 | 351
2019-09-06 12:30 | 355 | 353
2019-09-06 13:00 | 353 | 352
2019-09-06 13:30 | 363 | 362
2019-09-06 14:00 | 379 | 377
2019-09-06 14:30 | 388 | 386
2019-09-06 15:00 | 396 | 394
2019-09-06 15:30 | 410 | 407
2019-09-06 16:00 | 426 | 423
2019-09-06 16:30 | 445 | 442
2019-09-06 17:00 | 456 | 453
2019-09-06 17:30 | 454 | 450
2019-09-06 18:00 | 455 | 451
2019-09-06 18:30 | 456 | 451
2019-09-06 19:00 | 457 | 452
2019-09-06 19:30 | 446 | 440
2019-09-06 20:00 | 440 | 436
2019-09-06 20:30 | 437 | 433
2019-09-06 21:00 | 425 | 420
2019-09-06 21:30 | 409 | 403
2019-09-06 22:00 | 400 | 393
2019-09-06 22:30 | 389 | 381
2019-09-06 23:00 | 370 | 364
2019-09-06 23:30 | 361 | 352
2019-09-07 | 349 | 338
2019-09-07 00:30 | 323 | 311
2019-09-07 01:00 | 308 | 294
2019-09-07 01:30 | 299 | 285
2019-09-07 02:00 | 292 | 277
2019-09-07 02:30 | 286 | 269
2019-09-07 03:00 | 279 | 262
2019-09-07 03:30 | 274 | 255
2019-09-07 04:00 | 273 | 254
2019-09-07 04:30 | 273 | 254
2019-09-07 05:00 | 275 | 255
2019-09-07 05:30 | 279 | 259
2019-09-07 06:00 | 286 | 266
2019-09-07 06:30 | 305 | 285
2019-09-07 07:00 | 318 | 300
2019-09-07 07:30 | 333 | 316
2019-09-07 08:00 | 338 | 322
2019-09-07 08:30 | 340 | 325
2019-09-07 09:00 | 334 | 319
2019-09-07 09:30 | 322 | 307
2019-09-07 10:00 | 307 | 292
2019-09-07 10:30 | 289 | 273
2019-09-07 11:00 | 273 | 257
2019-09-07 11:30 | 271 | 254
2019-09-07 12:00 | 266 | 249
2019-09-07 12:30 | 276 | 260
2019-09-07 13:00 | 279 | 263
2019-09-07 13:30 | 282 | 267
2019-09-07 14:00 | 292 | 277
2019-09-07 14:30 | 297 | 283
2019-09-07 15:00 | 309 | 296
2019-09-07 15:30 | 322 | 311
2019-09-07 16:00 | 345 | 334
2019-09-07 16:30 | 364 | 356
2019-09-07 17:00 | 375 | 369
2019-09-07 17:30 | 386 | 379
2019-09-07 18:00 | 399 | 393
2019-09-07 18:30 | 409 | 404
2019-09-07 19:00 | 411 | 407
2019-09-07 19:30 | 404 | 399
2019-09-07 20:00 | 397 | 392
2019-09-07 20:30 | 397 | 390
2019-09-07 21:00 | 388 | 380
2019-09-07 21:30 | 382 | 373
2019-09-07 22:00 | 376 | 366
2019-09-07 22:30 | 373 | 363
2019-09-07 23:00 | 367 | 356
2019-09-07 23:30 | 354 | 342
2019-09-08 | 337 | 323
2019-09-08 00:30 | 323 | 305
2019-09-08 01:00 | 302 | 280
2019-09-08 01:30 | 294 | 266
2019-09-08 02:00 | 284 | 254
2019-09-08 02:30 | 278 | 244
2019-09-08 03:00 | 275 | 240
2019-09-08 03:30 | 274 | 238
2019-09-08 04:00 | 274 | 239
2019-09-08 04:30 | 276 | 241
2019-09-08 05:00 | 278 | 243
2019-09-08 05:30 | 285 | 251
2019-09-08 06:00 | 292 | 258
2019-09-08 06:30 | 308 | 274
2019-09-08 07:00 | 318 | 284
2019-09-08 07:30 | 330 | 298
2019-09-08 08:00 | 325 | 294
2019-09-08 08:30 | 320 | 290
2019-09-08 09:00 | 308 | 278
2019-09-08 09:30 | 297 | 266
2019-09-08 10:00 | 284 | 252
2019-09-08 10:30 | 277 | 246
2019-09-08 11:00 | 267 | 234
2019-09-08 11:30 | 261 | 230
2019-09-08 12:00 | 258 | 226
2019-09-08 12:30 | 254 | 223
2019-09-08 13:00 | 254 | 223
2019-09-08 13:30 | 257 | 227
2019-09-08 14:00 | 265 | 236
2019-09-08 14:30 | 276 | 248
2019-09-08 15:00 | 294 | 269
2019-09-08 15:30 | 313 | 290
2019-09-08 16:00 | 333 | 312
2019-09-08 16:30 | 357 | 339
2019-09-08 17:00 | 374 | 363
2019-09-08 17:30 | 381 | 376
2019-09-08 18:00 | 402 | 398
2019-09-08 18:30 | 418 | 411
2019-09-08 19:00 | 420 | 412
2019-09-08 19:30 | 414 | 406
2019-09-08 20:00 | 401 | 398
2019-09-08 20:30 | 397 | 393
2019-09-08 21:00 | 388 | 384
2019-09-08 21:30 | 371 | 366
2019-09-08 22:00 | 360 | 355
2019-09-08 22:30 | 349 | 342
2019-09-08 23:00 | 336 | 329
2019-09-08 23:30 | 327 | 318
2019-09-09 | 315 | 305
2019-09-09 00:30 | 292 | 279
2019-09-09 01:00 | 281 | 267
2019-09-09 01:30 | 275 | 260
2019-09-09 02:00 | 266 | 250
2019-09-09 02:30 | 261 | 243
2019-09-09 03:00 | 259 | 241
2019-09-09 03:30 | 253 | 236
2019-09-09 04:00 | 253 | 236
2019-09-09 04:30 | 260 | 244
2019-09-09 05:00 | 277 | 262
2019-09-09 05:30 | 291 | 279
2019-09-09 06:00 | 314 | 306
2019-09-09 06:30 | 359 | 353
2019-09-09 07:00 | 385 | 380
2019-09-09 07:30 | 393 | 389
2019-09-09 08:00 | 391 | 385
2019-09-09 08:30 | 380 | 374
2019-09-09 09:00 | 362 | 356
2019-09-09 09:30 | 349 | 343
2019-09-09 10:00 | 331 | 326
2019-09-09 10:30 | 319 | 315
2019-09-09 11:00 | 309 | 305
2019-09-09 11:30 | 303 | 299
2019-09-09 12:00 | 301 | 297
2019-09-09 12:30 | 301 | 297
2019-09-09 13:00 | 305 | 301
2019-09-09 13:30 | 311 | 307
2019-09-09 14:00 | 321 | 317
2019-09-09 14:30 | 335 | 331
2019-09-09 15:00 | 350 | 347
2019-09-09 15:30 | 369 | 365
2019-09-09 16:00 | 386 | 382
2019-09-09 16:30 | 410 | 406
2019-09-09 17:00 | 433 | 429
2019-09-09 17:30 | 450 | 441
2019-09-09 18:00 | 459 | 457
2019-09-09 18:30 | 468 | 465
2019-09-09 19:00 | 466 | 462
2019-09-09 19:30 | 462 | 458
2019-09-09 20:00 | 461 | 457
2019-09-09 20:30 | 453 | 450
2019-09-09 21:00 | 436 | 433
2019-09-09 21:30 | 423 | 420
2019-09-09 22:00 | 408 | 405
2019-09-09 22:30 | 398 | 395
2019-09-09 23:00 | 386 | 383
2019-09-09 23:30 | 374 | 369
2019-09-10 | 351 | 345
2019-09-10 00:30 | 328 | 319
2019-09-10 01:00 | 314 | 304
2019-09-10 01:30 | 308 | 297
2019-09-10 02:00 | 301 | 289
2019-09-10 02:30 | 299 | 287
2019-09-10 03:00 | 298 | 285
2019-09-10 03:30 | 298 | 285
2019-09-10 04:00 | 300 | 288
2019-09-10 04:30 | 308 | 296
2019-09-10 05:00 | 317 | 306
2019-09-10 05:30 | 337 | 330
2019-09-10 06:00 | 360 | 355
2019-09-10 06:30 | 398 | 394
2019-09-10 07:00 | 417 | 410
2019-09-10 07:30 | 429 | 424
2019-09-10 08:00 | 423 | 418
2019-09-10 08:30 | 402 | 397
2019-09-10 09:00 | 381 | 375
2019-09-10 09:30 | 360 | 357
2019-09-10 10:00 | 344 | 342
2019-09-10 10:30 | 332 | 330
2019-09-10 11:00 | 320 | 319
2019-09-10 11:30 | 316 | 314
2019-09-10 12:00 | 313 | 311
2019-09-10 12:30 | 318 | 316
2019-09-10 13:00 | 329 | 328
2019-09-10 13:30 | 338 | 337
2019-09-10 14:00 | 346 | 345
2019-09-10 14:30 | 356 | 355
2019-09-10 15:00 | 359 | 358
2019-09-10 15:30 | 375 | 374
2019-09-10 16:00 | 392 | 391
2019-09-10 16:30 | 413 | 412
2019-09-10 17:00 | 435 | 434
2019-09-10 17:30 | 453 | 451
2019-09-10 18:00 | 475 | 473
2019-09-10 18:30 | 490 | 484
2019-09-10 19:00 | 495 | 488
2019-09-10 19:30 | 486 | 478
2019-09-10 20:00 | 474 | 471
2019-09-10 20:30 | 470 | 467
2019-09-10 21:00 | 449 | 446
2019-09-10 21:30 | 427 | 425
2019-09-10 22:00 | 414 | 412
2019-09-10 22:30 | 403 | 401
2019-09-10 23:00 | 393 | 390
2019-09-10 23:30 | 376 | 372
2019-09-11 | 355 | 348
2019-09-11 00:30 | 334 | 325
2019-09-11 01:00 | 319 | 308
2019-09-11 01:30 | 308 | 297
2019-09-11 02:00 | 304 | 292
2019-09-11 02:30 | 300 | 287
2019-09-11 03:00 | 297 | 284
2019-09-11 03:30 | 296 | 283
2019-09-11 04:00 | 297 | 284
2019-09-11 04:30 | 305 | 293
2019-09-11 05:00 | 315 | 305
2019-09-11 05:30 | 336 | 328
2019-09-11 06:00 | 360 | 354
2019-09-11 06:30 | 399 | 394
2019-09-11 07:00 | 421 | 414
2019-09-11 07:30 | 434 | 428
2019-09-11 08:00 | 423 | 417
2019-09-11 08:30 | 396 | 389
2019-09-11 09:00 | 368 | 364
2019-09-11 09:30 | 353 | 351
2019-09-11 10:00 | 350 | 348
2019-09-11 10:30 | 365 | 364
2019-09-11 11:00 | 373 | 372
2019-09-11 11:30 | 370 | 369
2019-09-11 12:00 | 355 | 354
2019-09-11 12:30 | 344 | 343
2019-09-11 13:00 | 336 | 334
2019-09-11 13:30 | 329 | 328
2019-09-11 14:00 | 335 | 333
2019-09-11 14:30 | 347 | 345
2019-09-11 15:00 | 354 | 352
2019-09-11 15:30 | 363 | 362
2019-09-11 16:00 | 379 | 377
2019-09-11 16:30 | 403 | 401
2019-09-11 17:00 | 424 | 423
2019-09-11 17:30 | 440 | 436
2019-09-11 18:00 | 456 | 453
2019-09-11 18:30 | 466 | 462
2019-09-11 19:00 | 472 | 469
2019-09-11 19:30 | 469 | 465
2019-09-11 20:00 | 465 | 460
2019-09-11 20:30 | 463 | 460
2019-09-11 21:00 | 451 | 449
2019-09-11 21:30 | 434 | 432
2019-09-11 22:00 | 414 | 413
2019-09-11 22:30 | 402 | 401
2019-09-11 23:00 | 386 | 384
2019-09-11 23:30 | 372 | 370
2019-09-12 | 358 | 355
2019-09-12 00:30 | 335 | 332
2019-09-12 01:00 | 316 | 312
2019-09-12 01:30 | 302 | 297
2019-09-12 02:00 | 294 | 289
2019-09-12 02:30 | 288 | 282
2019-09-12 03:00 | 285 | 279
2019-09-12 03:30 | 282 | 278
2019-09-12 04:00 | 277 | 273
2019-09-12 04:30 | 282 | 278
2019-09-12 05:00 | 293 | 290
2019-09-12 05:30 | 314 | 312
2019-09-12 06:00 | 339 | 337
2019-09-12 06:30 | 392 | 391
2019-09-12 07:00 | 412 | 410
2019-09-12 07:30 | 421 | 420
2019-09-12 08:00 | 415 | 413
2019-09-12 08:30 | 393 | 390
2019-09-12 09:00 | 372 | 368
2019-09-12 09:30 | 348 | 347
2019-09-12 10:00 | 331 | 331
2019-09-12 10:30 | 319 | 318
2019-09-12 11:00 | 304 | 304
2019-09-12 11:30 | 296 | 295
2019-09-12 12:00 | 299 | 299
2019-09-12 12:30 | 298 | 298
2019-09-12 13:00 | 302 | 302
2019-09-12 13:30 | 308 | 307
2019-09-12 14:00 | 319 | 318
2019-09-12 14:30 | 330 | 330
2019-09-12 15:00 | 343 | 343
2019-09-12 15:30 | 355 | 355
2019-09-12 16:00 | 377 | 377
2019-09-12 16:30 | 403 | 403
2019-09-12 17:00 | 430 | 429
2019-09-12 17:30 | 441 | 438
2019-09-12 18:00 | 455 | 453
2019-09-12 18:30 | 470 | 468
2019-09-12 19:00 | 471 | 468
2019-09-12 19:30 | 472 | 468
2019-09-12 20:00 | 468 | 465
2019-09-12 20:30 | 462 | 460
2019-09-12 21:00 | 447 | 445
2019-09-12 21:30 | 429 | 426
2019-09-12 22:00 | 414 | 412
2019-09-12 22:30 | 402 | 400
2019-09-12 23:00 | 390 | 388
2019-09-12 23:30 | 374 | 373
2019-09-13 | 354 | 351
2019-09-13 00:30 | 336 | 333
2019-09-13 01:00 | 319 | 315
2019-09-13 01:30 | 308 | 303
2019-09-13 02:00 | 299 | 293
2019-09-13 02:30 | 294 | 288
2019-09-13 03:00 | 291 | 285
2019-09-13 03:30 | 291 | 286
2019-09-13 04:00 | 293 | 287
2019-09-13 04:30 | 302 | 296
2019-09-13 05:00 | 315 | 310
2019-09-13 05:30 | 338 | 334
2019-09-13 06:00 | 359 | 356
2019-09-13 06:30 | 393 | 392
2019-09-13 07:00 | 413 | 413
2019-09-13 07:30 | 420 | 420
2019-09-13 08:00 | 407 | 406
2019-09-13 08:30 | 383 | 381
2019-09-13 09:00 | 356 | 355
2019-09-13 09:30 | 342 | 341
2019-09-13 10:00 | 326 | 325
2019-09-13 10:30 | 317 | 317
2019-09-13 11:00 | 312 | 312
2019-09-13 11:30 | 311 | 310
2019-09-13 12:00 | 313 | 313
2019-09-13 12:30 | 312 | 312
2019-09-13 13:00 | 316 | 316
2019-09-13 13:30 | 323 | 323
2019-09-13 14:00 | 336 | 336
2019-09-13 14:30 | 346 | 346
2019-09-13 15:00 | 362 | 362
2019-09-13 15:30 | 378 | 378
2019-09-13 16:00 | 394 | 394
2019-09-13 16:30 | 416 | 416
2019-09-13 17:00 | 434 | 432
2019-09-13 17:30 | 444 | 442
2019-09-13 18:00 | 450 | 448
2019-09-13 18:30 | 449 | 448
2019-09-13 19:00 | 455 | 454
2019-09-13 19:30 | 448 | 447
2019-09-13 20:00 | 443 | 441
2019-09-13 20:30 | 438 | 436
2019-09-13 21:00 | 420 | 420
2019-09-13 21:30 | 409 | 409
2019-09-13 22:00 | 398 | 398
2019-09-13 22:30 | 393 | 392
2019-09-13 23:00 | 387 | 386
2019-09-13 23:30 | 372 | 370
2019-09-14 | 349 | 346
2019-09-14 00:30 | 332 | 328
2019-09-14 01:00 | 321 | 315
2019-09-14 01:30 | 312 | 305
2019-09-14 02:00 | 302 | 295
2019-09-14 02:30 | 300 | 292
2019-09-14 03:00 | 296 | 288
2019-09-14 03:30 | 293 | 286
2019-09-14 04:00 | 293 | 286
2019-09-14 04:30 | 293 | 285
2019-09-14 05:00 | 295 | 288
2019-09-14 05:30 | 302 | 295
2019-09-14 06:00 | 311 | 304
2019-09-14 06:30 | 326 | 320
2019-09-14 07:00 | 330 | 323
2019-09-14 07:30 | 328 | 322
2019-09-14 08:00 | 321 | 316
2019-09-14 08:30 | 320 | 314
2019-09-14 09:00 | 314 | 308
2019-09-14 09:30 | 304 | 299
2019-09-14 10:00 | 291 | 286
2019-09-14 10:30 | 280 | 275
2019-09-14 11:00 | 271 | 266
2019-09-14 11:30 | 264 | 260
2019-09-14 12:00 | 259 | 255
2019-09-14 12:30 | 253 | 248
2019-09-14 13:00 | 255 | 251
2019-09-14 13:30 | 267 | 263
2019-09-14 14:00 | 278 | 274
2019-09-14 14:30 | 291 | 287
2019-09-14 15:00 | 308 | 305
2019-09-14 15:30 | 325 | 323
2019-09-14 16:00 | 345 | 344
2019-09-14 16:30 | 368 | 366
2019-09-14 17:00 | 381 | 379
2019-09-14 17:30 | 390 | 388
2019-09-14 18:00 | 400 | 399
2019-09-14 18:30 | 413 | 413
2019-09-14 19:00 | 411 | 411
2019-09-14 19:30 | 409 | 408
2019-09-14 20:00 | 405 | 404
2019-09-14 20:30 | 402 | 401
2019-09-14 21:00 | 394 | 392
2019-09-14 21:30 | 383 | 381
2019-09-14 22:00 | 379 | 377
2019-09-14 22:30 | 375 | 372
2019-09-14 23:00 | 368 | 365
2019-09-14 23:30 | 353 | 349
2019-09-15 | 339 | 335
2019-09-15 00:30 | 318 | 312
2019-09-15 01:00 | 313 | 306
2019-09-15 01:30 | 299 | 292
2019-09-15 02:00 | 292 | 284
2019-09-15 02:30 | 285 | 276
2019-09-15 03:00 | 282 | 273
2019-09-15 03:30 | 271 | 262
2019-09-15 04:00 | 273 | 263
2019-09-15 04:30 | 275 | 265
2019-09-15 05:00 | 274 | 264
2019-09-15 05:30 | 279 | 270
2019-09-15 06:00 | 288 | 278
2019-09-15 06:30 | 298 | 289
2019-09-15 07:00 | 298 | 290
2019-09-15 07:30 | 299 | 292
2019-09-15 08:00 | 297 | 290
2019-09-15 08:30 | 295 | 289
2019-09-15 09:00 | 289 | 283
2019-09-15 09:30 | 281 | 276
2019-09-15 10:00 | 276 | 270
2019-09-15 10:30 | 267 | 261
2019-09-15 11:00 | 258 | 252
2019-09-15 11:30 | 251 | 246
2019-09-15 12:00 | 250 | 245
2019-09-15 12:30 | 252 | 247
2019-09-15 13:00 | 252 | 247
2019-09-15 13:30 | 255 | 250
2019-09-15 14:00 | 267 | 263
2019-09-15 14:30 | 277 | 274
2019-09-15 15:00 | 291 | 288
2019-09-15 15:30 | 309 | 306
2019-09-15 16:00 | 328 | 325
2019-09-15 16:30 | 347 | 345
2019-09-15 17:00 | 365 | 363
2019-09-15 17:30 | 381 | 380
2019-09-15 18:00 | 399 | 398
2019-09-15 18:30 | 419 | 417
2019-09-15 19:00 | 421 | 418
2019-09-15 19:30 | 416 | 413
2019-09-15 20:00 | 417 | 414
2019-09-15 20:30 | 413 | 410
2019-09-15 21:00 | 394 | 393
2019-09-15 21:30 | 376 | 375
2019-09-15 22:00 | 359 | 357
2019-09-15 22:30 | 344 | 342
2019-09-15 23:00 | 339 | 337
2019-09-15 23:30 | 335 | 332
2019-09-16 | 322 | 317
2019-09-16 00:30 | 298 | 292
2019-09-16 01:00 | 283 | 276
2019-09-16 01:30 | 278 | 271
2019-09-16 02:00 | 275 | 267
2019-09-16 02:30 | 267 | 260
2019-09-16 03:00 | 265 | 257
2019-09-16 03:30 | 262 | 255
2019-09-16 04:00 | 259 | 252
2019-09-16 04:30 | 266 | 259
2019-09-16 05:00 | 280 | 274
2019-09-16 05:30 | 304 | 300
2019-09-16 06:00 | 326 | 323
2019-09-16 06:30 | 364 | 363
2019-09-16 07:00 | 380 | 380
2019-09-16 07:30 | 390 | 390
2019-09-16 08:00 | 382 | 382
2019-09-16 08:30 | 368 | 368
2019-09-16 09:00 | 357 | 357
2019-09-16 09:30 | 340 | 340
2019-09-16 10:00 | 334 | 333
2019-09-16 10:30 | 326 | 326
2019-09-16 11:00 | 325 | 325
2019-09-16 11:30 | 327 | 327
2019-09-16 12:00 | 328 | 327
2019-09-16 12:30 | 329 | 329
2019-09-16 13:00 | 329 | 329
2019-09-16 13:30 | 335 | 335
2019-09-16 14:00 | 346 | 346
2019-09-16 14:30 | 356 | 356
2019-09-16 15:00 | 372 | 371
2019-09-16 15:30 | 391 | 391
2019-09-16 16:00 | 414 | 414
2019-09-16 16:30 | 429 | 429
2019-09-16 17:00 | 443 | 443
2019-09-16 17:30 | 448 | 448
2019-09-16 18:00 | 460 | 460
2019-09-16 18:30 | 471 | 470
2019-09-16 19:00 | 479 | 477
2019-09-16 19:30 | 473 | 471
2019-09-16 20:00 | 458 | 456
2019-09-16 20:30 | 447 | 446
2019-09-16 21:00 | 438 | 436
2019-09-16 21:30 | 420 | 418
2019-09-16 22:00 | 407 | 406
2019-09-16 22:30 | 401 | 400
2019-09-16 23:00 | 386 | 385
2019-09-16 23:30 | 368 | 366
2019-09-17 | 350 | 347
2019-09-17 00:30 | 326 | 323
2019-09-17 01:00 | 314 | 310
2019-09-17 01:30 | 302 | 297
2019-09-17 02:00 | 297 | 290
2019-09-17 02:30 | 295 | 288
2019-09-17 03:00 | 293 | 286
2019-09-17 03:30 | 298 | 290
2019-09-17 04:00 | 300 | 293
2019-09-17 04:30 | 299 | 292
2019-09-17 05:00 | 298 | 292
2019-09-17 05:30 | 314 | 310
2019-09-17 06:00 | 330 | 327
2019-09-17 06:30 | 355 | 353
2019-09-17 07:00 | 390 | 389
2019-09-17 07:30 | 400 | 399
2019-09-17 08:00 | 393 | 392
2019-09-17 08:30 | 378 | 378
2019-09-17 09:00 | 374 | 373
2019-09-17 09:30 | 365 | 365
2019-09-17 10:00 | 350 | 350
2019-09-17 10:30 | 339 | 339
2019-09-17 11:00 | 330 | 330
2019-09-17 11:30 | 329 | 329
2019-09-17 12:00 | 331 | 331
2019-09-17 12:30 | 334 | 334
2019-09-17 13:00 | 339 | 339
2019-09-17 13:30 | 350 | 349
2019-09-17 14:00 | 361 | 361
2019-09-17 14:30 | 374 | 374
2019-09-17 15:00 | 400 | 400
2019-09-17 15:30 | 424 | 424
2019-09-17 16:00 | 439 | 438
2019-09-17 16:30 | 449 | 449
2019-09-17 17:00 | 459 | 459
2019-09-17 17:30 | 465 | 464
2019-09-17 18:00 | 465 | 465
2019-09-17 18:30 | 459 | 458
2019-09-17 19:00 | 458 | 456
2019-09-17 19:30 | 449 | 447
2019-09-17 20:00 | 444 | 442
2019-09-17 20:30 | 438 | 437
2019-09-17 21:00 | 427 | 426
2019-09-17 21:30 | 410 | 408
2019-09-17 22:00 | 402 | 400
2019-09-17 22:30 | 394 | 393
2019-09-17 23:00 | 384 | 383
2019-09-17 23:30 | 365 | 364
2019-09-18 | 343 | 341
2019-09-18 00:30 | 322 | 319
2019-09-18 01:00 | 311 | 307
2019-09-18 01:30 | 303 | 299
2019-09-18 02:00 | 287 | 283
2019-09-18 02:30 | 280 | 276
2019-09-18 03:00 | 278 | 273
2019-09-18 03:30 | 279 | 274
2019-09-18 04:00 | 287 | 282
2019-09-18 04:30 | 296 | 291
2019-09-18 05:00 | 310 | 305
2019-09-18 05:30 | 323 | 320
2019-09-18 06:00 | 333 | 330
2019-09-18 06:30 | 364 | 362
2019-09-18 07:00 | 389 | 387
2019-09-18 07:30 | 396 | 395
2019-09-18 08:00 | 390 | 389
2019-09-18 08:30 | 372 | 371
2019-09-18 09:00 | 350 | 349
2019-09-18 09:30 | 334 | 333
2019-09-18 10:00 | 323 | 322
2019-09-18 10:30 | 316 | 315
2019-09-18 11:00 | 311 | 310
2019-09-18 11:30 | 307 | 307
2019-09-18 12:00 | 307 | 306
2019-09-18 12:30 | 310 | 310
2019-09-18 13:00 | 316 | 315
2019-09-18 13:30 | 323 | 322
2019-09-18 14:00 | 332 | 332
2019-09-18 14:30 | 341 | 341
2019-09-18 15:00 | 352 | 352
2019-09-18 15:30 | 369 | 368
2019-09-18 16:00 | 391 | 391
2019-09-18 16:30 | 410 | 410
2019-09-18 17:00 | 427 | 426
2019-09-18 17:30 | 437 | 436
2019-09-18 18:00 | 450 | 447
2019-09-18 18:30 | 458 | 455
2019-09-18 19:00 | 461 | 458
2019-09-18 19:30 | 456 | 452
2019-09-18 20:00 | 448 | 445
2019-09-18 20:30 | 438 | 437
2019-09-18 21:00 | 424 | 422
2019-09-18 21:30 | 407 | 406
2019-09-18 22:00 | 393 | 393
2019-09-18 22:30 | 384 | 384
2019-09-18 23:00 | 374 | 373
2019-09-18 23:30 | 360 | 358
2019-09-19 | 336 | 333
2019-09-19 00:30 | 312 | 308
2019-09-19 01:00 | 297 | 291
2019-09-19 01:30 | 290 | 284
2019-09-19 02:00 | 287 | 280
2019-09-19 02:30 | 278 | 271
2019-09-19 03:00 | 272 | 265
2019-09-19 03:30 | 269 | 262
2019-09-19 04:00 | 265 | 258
2019-09-19 04:30 | 269 | 263
2019-09-19 05:00 | 280 | 275
2019-09-19 05:30 | 300 | 296
2019-09-19 06:00 | 323 | 319
2019-09-19 06:30 | 363 | 360
2019-09-19 07:00 | 377 | 375
2019-09-19 07:30 | 387 | 386
2019-09-19 08:00 | 377 | 376
2019-09-19 08:30 | 367 | 365
2019-09-19 09:00 | 350 | 349
2019-09-19 09:30 | 338 | 337
2019-09-19 10:00 | 326 | 325
2019-09-19 10:30 | 322 | 321
2019-09-19 11:00 | 318 | 316
2019-09-19 11:30 | 314 | 312
2019-09-19 12:00 | 314 | 312
2019-09-19 12:30 | 316 | 315
2019-09-19 13:00 | 325 | 324
2019-09-19 13:30 | 331 | 330
2019-09-19 14:00 | 337 | 336
2019-09-19 14:30 | 346 | 345
2019-09-19 15:00 | 361 | 360
2019-09-19 15:30 | 373 | 372
2019-09-19 16:00 | 397 | 397
2019-09-19 16:30 | 418 | 417
2019-09-19 17:00 | 431 | 430
2019-09-19 17:30 | 440 | 439
2019-09-19 18:00 | 451 | 450
2019-09-19 18:30 | 464 | 460
2019-09-19 19:00 | 468 | 464
2019-09-19 19:30 | 461 | 456
2019-09-19 20:00 | 454 | 448
2019-09-19 20:30 | 449 | 443
2019-09-19 21:00 | 438 | 432
2019-09-19 21:30 | 418 | 413
2019-09-19 22:00 | 400 | 397
2019-09-19 22:30 | 385 | 383
2019-09-19 23:00 | 368 | 367
2019-09-19 23:30 | 352 | 350
2019-09-20 | 337 | 334
2019-09-20 00:30 | 309 | 304
2019-09-20 01:00 | 287 | 282
2019-09-20 01:30 | 281 | 275
2019-09-20 02:00 | 281 | 274
2019-09-20 02:30 | 272 | 266
2019-09-20 03:00 | 267 | 260
2019-09-20 03:30 | 265 | 258
2019-09-20 04:00 | 271 | 263
2019-09-20 04:30 | 279 | 272
2019-09-20 05:00 | 283 | 277
2019-09-20 05:30 | 302 | 297
2019-09-20 06:00 | 321 | 317
2019-09-20 06:30 | 361 | 359
2019-09-20 07:00 | 384 | 383
2019-09-20 07:30 | 386 | 386
2019-09-20 08:00 | 383 | 382
2019-09-20 08:30 | 376 | 372
2019-09-20 09:00 | 367 | 363
2019-09-20 09:30 | 362 | 358
2019-09-20 10:00 | 366 | 363
2019-09-20 10:30 | 364 | 361
2019-09-20 11:00 | 361 | 359
2019-09-20 11:30 | 362 | 359
2019-09-20 12:00 | 359 | 357
2019-09-20 12:30 | 350 | 348
2019-09-20 13:00 | 349 | 347
2019-09-20 13:30 | 351 | 350
2019-09-20 14:00 | 357 | 355
2019-09-20 14:30 | 364 | 363
2019-09-20 15:00 | 373 | 372
2019-09-20 15:30 | 396 | 394
2019-09-20 16:00 | 408 | 405
2019-09-20 16:30 | 420 | 417
2019-09-20 17:00 | 431 | 429
2019-09-20 17:30 | 435 | 433
2019-09-20 18:00 | 440 | 437
2019-09-20 18:30 | 444 | 441
2019-09-20 19:00 | 444 | 441
2019-09-20 19:30 | 581 | 573
2019-09-20 20:00 | 608 | 598
2019-09-20 20:30 | 593 | 589
2019-09-20 21:00 | 576 | 572
2019-09-20 21:30 | 556 | 552
2019-09-20 22:00 | 535 | 530
2019-09-20 22:30 | 532 | 526
2019-09-20 23:00 | 523 | 517
2019-09-20 23:30 | 515 | 507
2019-09-21 | 488 | 478
2019-09-21 00:30 | 439 | 429
2019-09-21 01:00 | 419 | 408
2019-09-21 01:30 | 403 | 391
2019-09-21 02:00 | 388 | 375
2019-09-21 02:30 | 384 | 371
2019-09-21 03:00 | 380 | 365
2019-09-21 03:30 | 385 | 369
2019-09-21 04:00 | 392 | 376
2019-09-21 04:30 | 395 | 379
2019-09-21 05:00 | 389 | 373
2019-09-21 05:30 | 405 | 390
2019-09-21 06:00 | 408 | 392
2019-09-21 06:30 | 411 | 397
2019-09-21 07:00 | 429 | 415
2019-09-21 07:30 | 454 | 444
2019-09-21 08:00 | 457 | 448
2019-09-21 08:30 | 459 | 451
2019-09-21 09:00 | 457 | 451
2019-09-21 09:30 | 454 | 448
2019-09-21 10:00 | 447 | 441
2019-09-21 10:30 | 436 | 430
2019-09-21 11:00 | 416 | 409
2019-09-21 11:30 | 405 | 397
2019-09-21 12:00 | 395 | 387
2019-09-21 12:30 | 394 | 385
2019-09-21 13:00 | 384 | 374
2019-09-21 13:30 | 380 | 371
2019-09-21 14:00 | 397 | 388
2019-09-21 14:30 | 415 | 407
2019-09-21 15:00 | 426 | 418
2019-09-21 15:30 | 453 | 445
2019-09-21 16:00 | 483 | 476
2019-09-21 16:30 | 507 | 501
2019-09-21 17:00 | 524 | 520
2019-09-21 17:30 | 537 | 533
2019-09-21 18:00 | 548 | 543
2019-09-21 18:30 | 569 | 560
2019-09-21 19:00 | 576 | 562
2019-09-21 19:30 | 573 | 558
2019-09-21 20:00 | 570 | 557
2019-09-21 20:30 | 567 | 554
2019-09-21 21:00 | 553 | 537
2019-09-21 21:30 | 538 | 521
2019-09-21 22:00 | 523 | 516
2019-09-21 22:30 | 515 | 507
2019-09-21 23:00 | 510 | 502
2019-09-21 23:30 | 502 | 493
2019-09-22 | 479 | 468
2019-09-22 00:30 | 454 | 442
2019-09-22 01:00 | 439 | 425
2019-09-22 01:30 | 418 | 403
2019-09-22 02:00 | 408 | 392
2019-09-22 02:30 | 392 | 376
2019-09-22 03:00 | 378 | 362
2019-09-22 03:30 | 365 | 349
2019-09-22 04:00 | 358 | 342
2019-09-22 04:30 | 362 | 346
2019-09-22 05:00 | 356 | 340
2019-09-22 05:30 | 362 | 347
2019-09-22 06:00 | 371 | 354
2019-09-22 06:30 | 396 | 379
2019-09-22 07:00 | 415 | 399
2019-09-22 07:30 | 428 | 414
2019-09-22 08:00 | 444 | 431
2019-09-22 08:30 | 442 | 431
2019-09-22 09:00 | 425 | 415
2019-09-22 09:30 | 425 | 416
2019-09-22 10:00 | 419 | 411
2019-09-22 10:30 | 406 | 398
2019-09-22 11:00 | 390 | 382
2019-09-22 11:30 | 377 | 369
2019-09-22 12:00 | 370 | 362
2019-09-22 12:30 | 367 | 358
2019-09-22 13:00 | 370 | 361
2019-09-22 13:30 | 374 | 365
2019-09-22 14:00 | 387 | 378
2019-09-22 14:30 | 403 | 395
2019-09-22 15:00 | 421 | 413
2019-09-22 15:30 | 448 | 441
2019-09-22 16:00 | 475 | 469
2019-09-22 16:30 | 502 | 497
2019-09-22 17:00 | 513 | 509
2019-09-22 17:30 | 524 | 522
2019-09-22 18:00 | 551 | 544
2019-09-22 18:30 | 566 | 559
2019-09-22 19:00 | 572 | 565
2019-09-22 19:30 | 566 | 559
2019-09-22 20:00 | 560 | 551
2019-09-22 20:30 | 554 | 547
2019-09-22 21:00 | 528 | 525
2019-09-22 21:30 | 515 | 511
2019-09-22 22:00 | 510 | 505
2019-09-22 22:30 | 502 | 496
2019-09-22 23:00 | 493 | 487
2019-09-22 23:30 | 468 | 461
2019-09-23 | 446 | 437
2019-09-23 00:30 | 422 | 411
2019-09-23 01:00 | 414 | 402
2019-09-23 01:30 | 404 | 391
2019-09-23 02:00 | 383 | 370
2019-09-23 02:30 | 368 | 355
2019-09-23 03:00 | 369 | 355
2019-09-23 03:30 | 381 | 367
2019-09-23 04:00 | 378 | 364
2019-09-23 04:30 | 380 | 367
2019-09-23 05:00 | 391 | 379
2019-09-23 05:30 | 420 | 410
2019-09-23 06:00 | 438 | 430
2019-09-23 06:30 | 469 | 463
2019-09-23 07:00 | 495 | 492
2019-09-23 07:30 | 514 | 511
2019-09-23 08:00 | 473 | 471
2019-09-23 08:30 | 402 | 398
2019-09-23 09:00 | 395 | 391
2019-09-23 09:30 | 380 | 376
2019-09-23 10:00 | 380 | 376
2019-09-23 10:30 | 379 | 374
2019-09-23 11:00 | 375 | 369
2019-09-23 11:30 | 372 | 366
2019-09-23 12:00 | 373 | 368
2019-09-23 12:30 | 376 | 371
2019-09-23 13:00 | 385 | 380
2019-09-23 13:30 | 401 | 396
2019-09-23 14:00 | 417 | 413
2019-09-23 14:30 | 438 | 435
2019-09-23 15:00 | 454 | 451
2019-09-23 15:30 | 459 | 455
2019-09-23 16:00 | 470 | 466
2019-09-23 16:30 | 498 | 494
2019-09-23 17:00 | 514 | 509
2019-09-23 17:30 | 516 | 511
2019-09-23 18:00 | 514 | 510
2019-09-23 18:30 | 525 | 521
2019-09-23 19:00 | 533 | 528
2019-09-23 19:30 | 521 | 516
2019-09-23 20:00 | 509 | 506
2019-09-23 20:30 | 501 | 498
2019-09-23 21:00 | 484 | 481
2019-09-23 21:30 | 467 | 464
2019-09-23 22:00 | 458 | 454
2019-09-23 22:30 | 454 | 450
2019-09-23 23:00 | 440 | 436
2019-09-23 23:30 | 420 | 415
2019-09-24 | 394 | 388
2019-09-24 00:30 | 371 | 364
2019-09-24 01:00 | 360 | 353
2019-09-24 01:30 | 351 | 342
2019-09-24 02:00 | 345 | 336
2019-09-24 02:30 | 338 | 328
2019-09-24 03:00 | 331 | 321
2019-09-24 03:30 | 325 | 315
2019-09-24 04:00 | 324 | 314
2019-09-24 04:30 | 331 | 322
2019-09-24 05:00 | 349 | 340
2019-09-24 05:30 | 362 | 355
2019-09-24 06:00 | 379 | 372
2019-09-24 06:30 | 416 | 411
2019-09-24 07:00 | 437 | 434
2019-09-24 07:30 | 441 | 439
2019-09-24 08:00 | 413 | 410
2019-09-24 08:30 | 396 | 394
2019-09-24 09:00 | 382 | 380
2019-09-24 09:30 | 371 | 370
2019-09-24 10:00 | 359 | 357
2019-09-24 10:30 | 348 | 347
2019-09-24 11:00 | 385 | 383
2019-09-24 11:30 | 388 | 385
2019-09-24 12:00 | 393 | 390
2019-09-24 12:30 | 394 | 391
2019-09-24 13:00 | 397 | 394
2019-09-24 13:30 | 412 | 409
2019-09-24 14:00 | 414 | 412
2019-09-24 14:30 | 422 | 420
2019-09-24 15:00 | 444 | 442
2019-09-24 15:30 | 453 | 450
2019-09-24 16:00 | 468 | 466
2019-09-24 16:30 | 482 | 480
2019-09-24 17:00 | 487 | 485
2019-09-24 17:30 | 498 | 496
2019-09-24 18:00 | 506 | 504
2019-09-24 18:30 | 514 | 512
2019-09-24 19:00 | 512 | 510
2019-09-24 19:30 | 506 | 504
2019-09-24 20:00 | 500 | 497
2019-09-24 20:30 | 497 | 494
2019-09-24 21:00 | 485 | 481
2019-09-24 21:30 | 475 | 471
2019-09-24 22:00 | 458 | 455
2019-09-24 22:30 | 451 | 448
2019-09-24 23:00 | 439 | 436
2019-09-24 23:30 | 422 | 418
2019-09-25 | 403 | 398
2019-09-25 00:30 | 369 | 362
2019-09-25 01:00 | 355 | 346
2019-09-25 01:30 | 350 | 340
2019-09-25 02:00 | 343 | 332
2019-09-25 02:30 | 340 | 329
2019-09-25 03:00 | 333 | 322
2019-09-25 03:30 | 326 | 314
2019-09-25 04:00 | 328 | 316
2019-09-25 04:30 | 335 | 325
2019-09-25 05:00 | 345 | 335
2019-09-25 05:30 | 362 | 354
2019-09-25 06:00 | 382 | 374
2019-09-25 06:30 | 412 | 407
2019-09-25 07:00 | 424 | 421
2019-09-25 07:30 | 443 | 441
2019-09-25 08:00 | 439 | 437
2019-09-25 08:30 | 460 | 457
2019-09-25 09:00 | 466 | 463
2019-09-25 09:30 | 431 | 428
2019-09-25 10:00 | 404 | 402
2019-09-25 10:30 | 405 | 402
2019-09-25 11:00 | 423 | 420
2019-09-25 11:30 | 413 | 410
2019-09-25 12:00 | 426 | 423
2019-09-25 12:30 | 423 | 421
2019-09-25 13:00 | 415 | 413
2019-09-25 13:30 | 420 | 417
2019-09-25 14:00 | 421 | 418
2019-09-25 14:30 | 425 | 423
2019-09-25 15:00 | 434 | 431
2019-09-25 15:30 | 446 | 444
2019-09-25 16:00 | 459 | 456
2019-09-25 16:30 | 492 | 489
2019-09-25 17:00 | 501 | 498
2019-09-25 17:30 | 509 | 506
2019-09-25 18:00 | 518 | 515
2019-09-25 18:30 | 532 | 530
2019-09-25 19:00 | 527 | 525
2019-09-25 19:30 | 515 | 513
2019-09-25 20:00 | 506 | 504
2019-09-25 20:30 | 505 | 503
2019-09-25 21:00 | 488 | 485
2019-09-25 21:30 | 478 | 475
2019-09-25 22:00 | 466 | 464
2019-09-25 22:30 | 448 | 446
2019-09-25 23:00 | 442 | 439
2019-09-25 23:30 | 418 | 415
2019-09-26 | 397 | 393
2019-09-26 00:30 | 377 | 371
2019-09-26 01:00 | 358 | 351
2019-09-26 01:30 | 352 | 344
2019-09-26 02:00 | 346 | 337
2019-09-26 02:30 | 340 | 331
2019-09-26 03:00 | 336 | 328
2019-09-26 03:30 | 334 | 325
2019-09-26 04:00 | 335 | 327
2019-09-26 04:30 | 340 | 332
2019-09-26 05:00 | 348 | 341
2019-09-26 05:30 | 364 | 358
2019-09-26 06:00 | 380 | 374
2019-09-26 06:30 | 408 | 405
2019-09-26 07:00 | 430 | 428
2019-09-26 07:30 | 445 | 443
2019-09-26 08:00 | 452 | 450
2019-09-26 08:30 | 460 | 459
2019-09-26 09:00 | 454 | 453
2019-09-26 09:30 | 453 | 452
2019-09-26 10:00 | 445 | 444
2019-09-26 10:30 | 422 | 421
2019-09-26 11:00 | 398 | 397
2019-09-26 11:30 | 397 | 396
2019-09-26 12:00 | 399 | 398
2019-09-26 12:30 | 393 | 392
2019-09-26 13:00 | 391 | 390
2019-09-26 13:30 | 420 | 419
2019-09-26 14:00 | 432 | 431
2019-09-26 14:30 | 417 | 416
2019-09-26 15:00 | 406 | 405
2019-09-26 15:30 | 410 | 409
2019-09-26 16:00 | 425 | 424
2019-09-26 16:30 | 454 | 453
2019-09-26 17:00 | 475 | 475
2019-09-26 17:30 | 485 | 485
2019-09-26 18:00 | 500 | 499
2019-09-26 18:30 | 517 | 515
2019-09-26 19:00 | 526 | 524
2019-09-26 19:30 | 515 | 513
2019-09-26 20:00 | 504 | 501
2019-09-26 20:30 | 498 | 496
2019-09-26 21:00 | 483 | 481
2019-09-26 21:30 | 467 | 465
2019-09-26 22:00 | 451 | 449
2019-09-26 22:30 | 442 | 440
2019-09-26 23:00 | 428 | 425
2019-09-26 23:30 | 404 | 400
2019-09-27 | 380 | 375
2019-09-27 00:30 | 356 | 349
2019-09-27 01:00 | 348 | 339
2019-09-27 01:30 | 338 | 328
2019-09-27 02:00 | 325 | 315
2019-09-27 02:30 | 317 | 307
2019-09-27 03:00 | 317 | 307
2019-09-27 03:30 | 320 | 309
2019-09-27 04:00 | 316 | 306
2019-09-27 04:30 | 319 | 310
2019-09-27 05:00 | 326 | 317
2019-09-27 05:30 | 349 | 342
2019-09-27 06:00 | 367 | 360
2019-09-27 06:30 | 401 | 392
2019-09-27 07:00 | 416 | 406
2019-09-27 07:30 | 424 | 415
2019-09-27 08:00 | 419 | 411
2019-09-27 08:30 | 416 | 408
2019-09-27 09:00 | 403 | 395
2019-09-27 09:30 | 395 | 387
2019-09-27 10:00 | 388 | 380
2019-09-27 10:30 | 388 | 381
2019-09-27 11:00 | 389 | 382
2019-09-27 11:30 | 397 | 389
2019-09-27 12:00 | 401 | 393
2019-09-27 12:30 | 395 | 387
2019-09-27 13:00 | 394 | 385
2019-09-27 13:30 | 396 | 387
2019-09-27 14:00 | 395 | 386
2019-09-27 14:30 | 404 | 396
2019-09-27 15:00 | 424 | 416
2019-09-27 15:30 | 429 | 422
2019-09-27 16:00 | 443 | 436
2019-09-27 16:30 | 464 | 457
2019-09-27 17:00 | 481 | 474
2019-09-27 17:30 | 478 | 469
2019-09-27 18:00 | 493 | 484
2019-09-27 18:30 | 503 | 495
2019-09-27 19:00 | 503 | 494
2019-09-27 19:30 | 494 | 485
2019-09-27 20:00 | 483 | 475
2019-09-27 20:30 | 468 | 465
2019-09-27 21:00 | 458 | 454
2019-09-27 21:30 | 445 | 441
2019-09-27 22:00 | 440 | 435
2019-09-27 22:30 | 436 | 431
2019-09-27 23:00 | 425 | 419
2019-09-27 23:30 | 408 | 401
2019-09-28 | 383 | 376
2019-09-28 00:30 | 355 | 347
2019-09-28 01:00 | 335 | 327
2019-09-28 01:30 | 328 | 318
2019-09-28 02:00 | 326 | 315
2019-09-28 02:30 | 321 | 310
2019-09-28 03:00 | 318 | 307
2019-09-28 03:30 | 309 | 299
2019-09-28 04:00 | 305 | 294
2019-09-28 04:30 | 305 | 294
2019-09-28 05:00 | 308 | 297
2019-09-28 05:30 | 322 | 311
2019-09-28 06:00 | 326 | 315
2019-09-28 06:30 | 346 | 335
2019-09-28 07:00 | 349 | 340
2019-09-28 07:30 | 345 | 336
2019-09-28 08:00 | 337 | 329
2019-09-28 08:30 | 332 | 325
2019-09-28 09:00 | 322 | 316
2019-09-28 09:30 | 321 | 316
2019-09-28 10:00 | 313 | 308
2019-09-28 10:30 | 307 | 302
2019-09-28 11:00 | 301 | 297
2019-09-28 11:30 | 296 | 293
2019-09-28 12:00 | 304 | 301
2019-09-28 12:30 | 313 | 310
2019-09-28 13:00 | 321 | 318
2019-09-28 13:30 | 345 | 343
2019-09-28 14:00 | 365 | 363
2019-09-28 14:30 | 384 | 383
2019-09-28 15:00 | 391 | 390
2019-09-28 15:30 | 383 | 381
2019-09-28 16:00 | 396 | 394
2019-09-28 16:30 | 421 | 420
2019-09-28 17:00 | 444 | 443
2019-09-28 17:30 | 447 | 446
2019-09-28 18:00 | 450 | 448
2019-09-28 18:30 | 464 | 463
2019-09-28 19:00 | 470 | 467
2019-09-28 19:30 | 457 | 454
2019-09-28 20:00 | 453 | 449
2019-09-28 20:30 | 449 | 445
2019-09-28 21:00 | 437 | 432
2019-09-28 21:30 | 426 | 420
2019-09-28 22:00 | 424 | 416
2019-09-28 22:30 | 419 | 413
2019-09-28 23:00 | 417 | 410
2019-09-28 23:30 | 401 | 393
2019-09-29 | 379 | 370
2019-09-29 00:30 | 358 | 347
2019-09-29 01:00 | 344 | 333
2019-09-29 01:30 | 337 | 325
2019-09-29 02:00 | 327 | 314
2019-09-29 02:30 | 318 | 304
2019-09-29 03:00 | 315 | 300
2019-09-29 03:30 | 309 | 294
2019-09-29 04:00 | 304 | 288
2019-09-29 04:30 | 304 | 288
2019-09-29 05:00 | 302 | 286
2019-09-29 05:30 | 305 | 289
2019-09-29 06:00 | 303 | 285
2019-09-29 06:30 | 312 | 295
2019-09-29 07:00 | 315 | 298
2019-09-29 07:30 | 313 | 298
2019-09-29 08:00 | 309 | 294
2019-09-29 08:30 | 304 | 291
2019-09-29 09:00 | 294 | 282
2019-09-29 09:30 | 284 | 272
2019-09-29 10:00 | 276 | 265
2019-09-29 10:30 | 266 | 255
2019-09-29 11:00 | 259 | 249
2019-09-29 11:30 | 254 | 244
2019-09-29 12:00 | 256 | 246
2019-09-29 12:30 | 257 | 248
2019-09-29 13:00 | 262 | 252
2019-09-29 13:30 | 272 | 262
2019-09-29 14:00 | 283 | 274
2019-09-29 14:30 | 294 | 287
2019-09-29 15:00 | 311 | 303
2019-09-29 15:30 | 334 | 328
2019-09-29 16:00 | 364 | 359
2019-09-29 16:30 | 391 | 387
2019-09-29 17:00 | 410 | 407
2019-09-29 17:30 | 435 | 429
2019-09-29 18:00 | 448 | 440
2019-09-29 18:30 | 467 | 459
2019-09-29 19:00 | 472 | 463
2019-09-29 19:30 | 470 | 460
2019-09-29 20:00 | 467 | 456
2019-09-29 20:30 | 455 | 449
2019-09-29 21:00 | 438 | 434
2019-09-29 21:30 | 425 | 420
2019-09-29 22:00 | 417 | 413
2019-09-29 22:30 | 410 | 406
2019-09-29 23:00 | 405 | 399
2019-09-29 23:30 | 392 | 386
2019-09-30 | 374 | 366
2019-09-30 00:30 | 351 | 341
2019-09-30 01:00 | 338 | 327
2019-09-30 01:30 | 330 | 318
2019-09-30 02:00 | 325 | 312
2019-09-30 02:30 | 317 | 304
2019-09-30 03:00 | 315 | 302
2019-09-30 03:30 | 321 | 308
2019-09-30 04:00 | 323 | 311
2019-09-30 04:30 | 329 | 317
2019-09-30 05:00 | 339 | 328
2019-09-30 05:30 | 350 | 342
2019-09-30 06:00 | 357 | 350
2019-09-30 06:30 | 387 | 382
2019-09-30 07:00 | 401 | 398
2019-09-30 07:30 | 414 | 411
2019-09-30 08:00 | 418 | 416
2019-09-30 08:30 | 416 | 414
2019-09-30 09:00 | 415 | 412
2019-09-30 09:30 | 419 | 416
2019-09-30 10:00 | 407 | 405
2019-09-30 10:30 | 403 | 401
2019-09-30 11:00 | 403 | 400
2019-09-30 11:30 | 403 | 400
2019-09-30 12:00 | 400 | 398
2019-09-30 12:30 | 401 | 398
2019-09-30 13:00 | 403 | 400
2019-09-30 13:30 | 405 | 402
2019-09-30 14:00 | 420 | 417
2019-09-30 14:30 | 435 | 433
2019-09-30 15:00 | 441 | 439
2019-09-30 15:30 | 449 | 447
2019-09-30 16:00 | 466 | 464
2019-09-30 16:30 | 479 | 477
2019-09-30 17:00 | 494 | 492
2019-09-30 17:30 | 506 | 504
2019-09-30 18:00 | 516 | 514
2019-09-30 18:30 | 526 | 519
2019-09-30 19:00 | 532 | 525
2019-09-30 19:30 | 519 | 511
2019-09-30 20:00 | 510 | 500
2019-09-30 20:30 | 500 | 490
2019-09-30 21:00 | 476 | 468
2019-09-30 21:30 | 456 | 451
2019-09-30 22:00 | 443 | 438
2019-09-30 22:30 | 432 | 428
2019-09-30 23:00 | 422 | 418
2019-09-30 23:30 | 406 | 399
2019-10-01 | 387 | 378
2019-10-01 00:30 | 366 | 354
2019-10-01 01:00 | 351 | 338
2019-10-01 01:30 | 343 | 329
2019-10-01 02:00 | 334 | 320
2019-10-01 02:30 | 327 | 313
2019-10-01 03:00 | 326 | 312
2019-10-01 03:30 | 326 | 312
2019-10-01 04:00 | 325 | 311
2019-10-01 04:30 | 331 | 318
2019-10-01 05:00 | 341 | 329
2019-10-01 05:30 | 360 | 349
2019-10-01 06:00 | 372 | 362
2019-10-01 06:30 | 394 | 388
2019-10-01 07:00 | 418 | 412
2019-10-01 07:30 | 419 | 415
2019-10-01 08:00 | 415 | 413
2019-10-01 08:30 | 417 | 415
2019-10-01 09:00 | 425 | 423
2019-10-01 09:30 | 433 | 432
2019-10-01 10:00 | 428 | 426
2019-10-01 10:30 | 421 | 419
2019-10-01 11:00 | 405 | 403
2019-10-01 11:30 | 396 | 394
2019-10-01 12:00 | 398 | 396
2019-10-01 12:30 | 413 | 411
2019-10-01 13:00 | 402 | 400
2019-10-01 13:30 | 377 | 375
2019-10-01 14:00 | 391 | 389
2019-10-01 14:30 | 400 | 398
2019-10-01 15:00 | 407 | 405
2019-10-01 15:30 | 417 | 414
2019-10-01 16:00 | 438 | 435
2019-10-01 16:30 | 455 | 453
2019-10-01 17:00 | 479 | 477
2019-10-01 17:30 | 501 | 499
2019-10-01 18:00 | 501 | 499
2019-10-01 18:30 | 519 | 517
2019-10-01 19:00 | 528 | 522
2019-10-01 19:30 | 510 | 503
2019-10-01 20:00 | 498 | 492
2019-10-01 20:30 | 492 | 485
2019-10-01 21:00 | 473 | 466
2019-10-01 21:30 | 451 | 447
2019-10-01 22:00 | 438 | 434
2019-10-01 22:30 | 432 | 428
2019-10-01 23:00 | 422 | 417
2019-10-01 23:30 | 404 | 397
2019-10-02 | 382 | 374
2019-10-02 00:30 | 357 | 347
2019-10-02 01:00 | 343 | 332
2019-10-02 01:30 | 333 | 321
2019-10-02 02:00 | 327 | 314
2019-10-02 02:30 | 324 | 312
2019-10-02 03:00 | 323 | 311
2019-10-02 03:30 | 323 | 311
2019-10-02 04:00 | 322 | 311
2019-10-02 04:30 | 325 | 314
2019-10-02 05:00 | 322 | 312
2019-10-02 05:30 | 344 | 335
2019-10-02 06:00 | 370 | 362
2019-10-02 06:30 | 398 | 392
2019-10-02 07:00 | 404 | 401
2019-10-02 07:30 | 394 | 392
2019-10-02 08:00 | 392 | 390
2019-10-02 08:30 | 396 | 395
2019-10-02 09:00 | 397 | 395
2019-10-02 09:30 | 399 | 397
2019-10-02 10:00 | 386 | 385
2019-10-02 10:30 | 376 | 374
2019-10-02 11:00 | 369 | 367
2019-10-02 11:30 | 363 | 362
2019-10-02 12:00 | 361 | 360
2019-10-02 12:30 | 361 | 359
2019-10-02 13:00 | 360 | 358
2019-10-02 13:30 | 359 | 358
2019-10-02 14:00 | 362 | 361
2019-10-02 14:30 | 375 | 374
2019-10-02 15:00 | 390 | 388
2019-10-02 15:30 | 402 | 400
2019-10-02 16:00 | 413 | 412
2019-10-02 16:30 | 441 | 440
2019-10-02 17:00 | 465 | 464
2019-10-02 17:30 | 494 | 489
2019-10-02 18:00 | 506 | 499
2019-10-02 18:30 | 521 | 515
2019-10-02 19:00 | 528 | 522
2019-10-02 19:30 | 514 | 507
2019-10-02 20:00 | 491 | 487
2019-10-02 20:30 | 481 | 479
2019-10-02 21:00 | 460 | 459
2019-10-02 21:30 | 450 | 448
2019-10-02 22:00 | 436 | 433
2019-10-02 22:30 | 430 | 426
2019-10-02 23:00 | 425 | 421
2019-10-02 23:30 | 415 | 409
2019-10-03 | 389 | 381
2019-10-03 00:30 | 365 | 356
2019-10-03 01:00 | 349 | 340
2019-10-03 01:30 | 342 | 332
2019-10-03 02:00 | 336 | 325
2019-10-03 02:30 | 329 | 318
2019-10-03 03:00 | 326 | 315
2019-10-03 03:30 | 329 | 317
2019-10-03 04:00 | 329 | 317
2019-10-03 04:30 | 334 | 323
2019-10-03 05:00 | 339 | 329
2019-10-03 05:30 | 356 | 347
2019-10-03 06:00 | 375 | 367
2019-10-03 06:30 | 391 | 385
2019-10-03 07:00 | 396 | 392
2019-10-03 07:30 | 398 | 395
2019-10-03 08:00 | 388 | 385
2019-10-03 08:30 | 376 | 374
2019-10-03 09:00 | 353 | 351
2019-10-03 09:30 | 341 | 339
2019-10-03 10:00 | 327 | 325
2019-10-03 10:30 | 318 | 316
2019-10-03 11:00 | 312 | 310
2019-10-03 11:30 | 313 | 311
2019-10-03 12:00 | 317 | 316
2019-10-03 12:30 | 319 | 318
2019-10-03 13:00 | 329 | 328
2019-10-03 13:30 | 336 | 335
2019-10-03 14:00 | 346 | 345
2019-10-03 14:30 | 355 | 354
2019-10-03 15:00 | 377 | 375
2019-10-03 15:30 | 397 | 396
2019-10-03 16:00 | 410 | 408
2019-10-03 16:30 | 434 | 433
2019-10-03 17:00 | 462 | 461
2019-10-03 17:30 | 492 | 487
2019-10-03 18:00 | 508 | 503
2019-10-03 18:30 | 523 | 518
2019-10-03 19:00 | 527 | 523
2019-10-03 19:30 | 515 | 510
2019-10-03 20:00 | 498 | 497
2019-10-03 20:30 | 492 | 491
2019-10-03 21:00 | 463 | 461
2019-10-03 21:30 | 448 | 445
2019-10-03 22:00 | 440 | 436
2019-10-03 22:30 | 434 | 429
2019-10-03 23:00 | 417 | 413
2019-10-03 23:30 | 400 | 395
2019-10-04 | 381 | 374
2019-10-04 00:30 | 355 | 347
2019-10-04 01:00 | 338 | 328
2019-10-04 01:30 | 324 | 314
2019-10-04 02:00 | 315 | 305
2019-10-04 02:30 | 317 | 306
2019-10-04 03:00 | 307 | 295
2019-10-04 03:30 | 304 | 292
2019-10-04 04:00 | 301 | 290
2019-10-04 04:30 | 306 | 295
2019-10-04 05:00 | 316 | 306
2019-10-04 05:30 | 337 | 328
2019-10-04 06:00 | 356 | 348
2019-10-04 06:30 | 374 | 369
2019-10-04 07:00 | 382 | 378
2019-10-04 07:30 | 388 | 386
2019-10-04 08:00 | 386 | 384
2019-10-04 08:30 | 381 | 379
2019-10-04 09:00 | 371 | 369
2019-10-04 09:30 | 354 | 352
2019-10-04 10:00 | 344 | 342
2019-10-04 10:30 | 342 | 340
2019-10-04 11:00 | 341 | 339
2019-10-04 11:30 | 343 | 341
2019-10-04 12:00 | 345 | 344
2019-10-04 12:30 | 340 | 339
2019-10-04 13:00 | 343 | 341
2019-10-04 13:30 | 350 | 348
2019-10-04 14:00 | 359 | 358
2019-10-04 14:30 | 376 | 375
2019-10-04 15:00 | 389 | 388
2019-10-04 15:30 | 409 | 408
2019-10-04 16:00 | 429 | 429
2019-10-04 16:30 | 452 | 452
2019-10-04 17:00 | 468 | 467
2019-10-04 17:30 | 486 | 483
2019-10-04 18:00 | 478 | 475
2019-10-04 18:30 | 490 | 486
2019-10-04 19:00 | 484 | 480
2019-10-04 19:30 | 473 | 469
2019-10-04 20:00 | 472 | 468
2019-10-04 20:30 | 472 | 467
2019-10-04 21:00 | 439 | 438
2019-10-04 21:30 | 433 | 431
2019-10-04 22:00 | 427 | 425
2019-10-04 22:30 | 417 | 414
2019-10-04 23:00 | 410 | 406
2019-10-04 23:30 | 392 | 387
2019-10-05 | 372 | 365
2019-10-05 00:30 | 351 | 342
2019-10-05 01:00 | 335 | 325
2019-10-05 01:30 | 316 | 306
2019-10-05 02:00 | 304 | 292
2019-10-05 02:30 | 294 | 283
2019-10-05 03:00 | 297 | 286
2019-10-05 03:30 | 291 | 279
2019-10-05 04:00 | 292 | 279
2019-10-05 04:30 | 287 | 275
2019-10-05 05:00 | 286 | 274
2019-10-05 05:30 | 294 | 282
2019-10-05 06:00 | 301 | 288
2019-10-05 06:30 | 319 | 307
2019-10-05 07:00 | 326 | 315
2019-10-05 07:30 | 323 | 312
2019-10-05 08:00 | 315 | 306
2019-10-05 08:30 | 315 | 308
2019-10-05 09:00 | 313 | 306
2019-10-05 09:30 | 309 | 303
2019-10-05 10:00 | 297 | 291
2019-10-05 10:30 | 289 | 284
2019-10-05 11:00 | 286 | 281
2019-10-05 11:30 | 286 | 281
2019-10-05 12:00 | 287 | 282
2019-10-05 12:30 | 290 | 285
2019-10-05 13:00 | 298 | 293
2019-10-05 13:30 | 308 | 304
2019-10-05 14:00 | 310 | 306
2019-10-05 14:30 | 325 | 322
2019-10-05 15:00 | 350 | 346
2019-10-05 15:30 | 368 | 366
2019-10-05 16:00 | 392 | 389
2019-10-05 16:30 | 407 | 405
2019-10-05 17:00 | 418 | 416
2019-10-05 17:30 | 420 | 411
2019-10-05 18:00 | 426 | 418
2019-10-05 18:30 | 434 | 427
2019-10-05 19:00 | 436 | 430
2019-10-05 19:30 | 433 | 426
2019-10-05 20:00 | 433 | 426
2019-10-05 20:30 | 426 | 420
2019-10-05 21:00 | 409 | 406
2019-10-05 21:30 | 399 | 396
2019-10-05 22:00 | 390 | 387
2019-10-05 22:30 | 387 | 383
2019-10-05 23:00 | 384 | 380
2019-10-05 23:30 | 373 | 369
2019-10-06 | 358 | 351
2019-10-06 00:30 | 330 | 322
2019-10-06 01:00 | 308 | 298
2019-10-06 01:30 | 288 | 278
2019-10-06 02:00 | 284 | 273
2019-10-06 02:30 | 282 | 271
2019-10-06 03:00 | 279 | 267
2019-10-06 03:30 | 277 | 264
2019-10-06 04:00 | 279 | 265
2019-10-06 04:30 | 275 | 262
2019-10-06 05:00 | 275 | 261
2019-10-06 05:30 | 277 | 263
2019-10-06 06:00 | 273 | 257
2019-10-06 06:30 | 285 | 269
2019-10-06 07:00 | 302 | 287
2019-10-06 07:30 | 314 | 302
2019-10-06 08:00 | 307 | 296
2019-10-06 08:30 | 302 | 291
2019-10-06 09:00 | 295 | 284
2019-10-06 09:30 | 301 | 291
2019-10-06 10:00 | 294 | 285
2019-10-06 10:30 | 292 | 284
2019-10-06 11:00 | 286 | 279
2019-10-06 11:30 | 271 | 263
2019-10-06 12:00 | 266 | 258
2019-10-06 12:30 | 258 | 250
2019-10-06 13:00 | 266 | 259
2019-10-06 13:30 | 277 | 270
2019-10-06 14:00 | 283 | 277
2019-10-06 14:30 | 294 | 289
2019-10-06 15:00 | 318 | 313
2019-10-06 15:30 | 344 | 340
2019-10-06 16:00 | 362 | 359
2019-10-06 16:30 | 393 | 390
2019-10-06 17:00 | 409 | 407
2019-10-06 17:30 | 417 | 415
2019-10-06 18:00 | 418 | 416
2019-10-06 18:30 | 431 | 430
2019-10-06 19:00 | 435 | 434
2019-10-06 19:30 | 422 | 420
2019-10-06 20:00 | 423 | 421
2019-10-06 20:30 | 415 | 413
2019-10-06 21:00 | 406 | 403
2019-10-06 21:30 | 406 | 402
2019-10-06 22:00 | 402 | 398
2019-10-06 22:30 | 397 | 393
2019-10-06 23:00 | 391 | 386
2019-10-06 23:30 | 376 | 371
2019-10-07 | 352 | 345
2019-10-07 00:30 | 330 | 321
2019-10-07 01:00 | 312 | 303
2019-10-07 01:30 | 297 | 287
2019-10-07 02:00 | 298 | 287
2019-10-07 02:30 | 298 | 285
2019-10-07 03:00 | 294 | 281
2019-10-07 03:30 | 286 | 273
2019-10-07 04:00 | 285 | 272
2019-10-07 04:30 | 287 | 274
2019-10-07 05:00 | 291 | 278
2019-10-07 05:30 | 297 | 284
2019-10-07 06:00 | 303 | 289
2019-10-07 06:30 | 313 | 300
2019-10-07 07:00 | 318 | 306
2019-10-07 07:30 | 319 | 309
2019-10-07 08:00 | 316 | 308
2019-10-07 08:30 | 314 | 308
2019-10-07 09:00 | 312 | 307
2019-10-07 09:30 | 308 | 303
2019-10-07 10:00 | 305 | 300
2019-10-07 10:30 | 304 | 300
2019-10-07 11:00 | 306 | 303
2019-10-07 11:30 | 305 | 303
2019-10-07 12:00 | 314 | 311
2019-10-07 12:30 | 326 | 325
2019-10-07 13:00 | 345 | 344
2019-10-07 13:30 | 364 | 363
2019-10-07 14:00 | 386 | 382
2019-10-07 14:30 | 409 | 403
2019-10-07 15:00 | 445 | 437
2019-10-07 15:30 | 468 | 461
2019-10-07 16:00 | 482 | 476
2019-10-07 16:30 | 496 | 489
2019-10-07 17:00 | 496 | 490
2019-10-07 17:30 | 489 | 483
2019-10-07 18:00 | 480 | 474
2019-10-07 18:30 | 489 | 484
2019-10-07 19:00 | 492 | 487
2019-10-07 19:30 | 481 | 475
2019-10-07 20:00 | 474 | 472
2019-10-07 20:30 | 467 | 466
2019-10-07 21:00 | 455 | 453
2019-10-07 21:30 | 449 | 446
2019-10-07 22:00 | 436 | 432
2019-10-07 22:30 | 421 | 416
2019-10-07 23:00 | 408 | 403
2019-10-07 23:30 | 393 | 387
2019-10-08 | 375 | 368
2019-10-08 00:30 | 349 | 341
2019-10-08 01:00 | 334 | 326
2019-10-08 01:30 | 319 | 309
2019-10-08 02:00 | 305 | 295
2019-10-08 02:30 | 302 | 292
2019-10-08 03:00 | 302 | 293
2019-10-08 03:30 | 304 | 295
2019-10-08 04:00 | 311 | 302
2019-10-08 04:30 | 320 | 311
2019-10-08 05:00 | 333 | 324
2019-10-08 05:30 | 350 | 342
2019-10-08 06:00 | 366 | 358
2019-10-08 06:30 | 401 | 396
2019-10-08 07:00 | 434 | 432
2019-10-08 07:30 | 458 | 455
2019-10-08 08:00 | 458 | 456
2019-10-08 08:30 | 452 | 450
2019-10-08 09:00 | 436 | 435
2019-10-08 09:30 | 432 | 432
2019-10-08 10:00 | 431 | 430
2019-10-08 10:30 | 415 | 414
2019-10-08 11:00 | 421 | 420
2019-10-08 11:30 | 424 | 423
2019-10-08 12:00 | 426 | 424
2019-10-08 12:30 | 445 | 443
2019-10-08 13:00 | 477 | 476
2019-10-08 13:30 | 487 | 487
2019-10-08 14:00 | 504 | 501
2019-10-08 14:30 | 513 | 510
2019-10-08 15:00 | 519 | 516
2019-10-08 15:30 | 521 | 517
2019-10-08 16:00 | 524 | 520
2019-10-08 16:30 | 530 | 526
2019-10-08 17:00 | 536 | 532
2019-10-08 17:30 | 552 | 545
2019-10-08 18:00 | 565 | 554
2019-10-08 18:30 | 576 | 566
2019-10-08 19:00 | 578 | 568
2019-10-08 19:30 | 564 | 552
2019-10-08 20:00 | 555 | 542
2019-10-08 20:30 | 536 | 523
2019-10-08 21:00 | 503 | 491
2019-10-08 21:30 | 472 | 467
2019-10-08 22:00 | 452 | 446
2019-10-08 22:30 | 438 | 430
2019-10-08 23:00 | 424 | 417
2019-10-08 23:30 | 406 | 398
2019-10-09 | 383 | 376
2019-10-09 00:30 | 362 | 353
2019-10-09 01:00 | 347 | 336
2019-10-09 01:30 | 337 | 324
2019-10-09 02:00 | 329 | 316
2019-10-09 02:30 | 325 | 310
2019-10-09 03:00 | 322 | 307
2019-10-09 03:30 | 323 | 307
2019-10-09 04:00 | 324 | 309
2019-10-09 04:30 | 331 | 316
2019-10-09 05:00 | 339 | 326
2019-10-09 05:30 | 353 | 341
2019-10-09 06:00 | 367 | 357
2019-10-09 06:30 | 391 | 384
2019-10-09 07:00 | 406 | 398
2019-10-09 07:30 | 428 | 420
2019-10-09 08:00 | 421 | 414
2019-10-09 08:30 | 398 | 392
2019-10-09 09:00 | 386 | 380
2019-10-09 09:30 | 381 | 374
2019-10-09 10:00 | 379 | 373
2019-10-09 10:30 | 380 | 372
2019-10-09 11:00 | 368 | 361
2019-10-09 11:30 | 358 | 356
2019-10-09 12:00 | 352 | 349
2019-10-09 12:30 | 349 | 346
2019-10-09 13:00 | 350 | 348
2019-10-09 13:30 | 335 | 333
2019-10-09 14:00 | 353 | 352
2019-10-09 14:30 | 371 | 370
2019-10-09 15:00 | 372 | 371
2019-10-09 15:30 | 380 | 378
2019-10-09 16:00 | 400 | 397
2019-10-09 16:30 | 419 | 417
2019-10-09 17:00 | 436 | 434
2019-10-09 17:30 | 450 | 448
2019-10-09 18:00 | 466 | 463
2019-10-09 18:30 | 481 | 479
2019-10-09 19:00 | 489 | 488
2019-10-09 19:30 | 473 | 471
2019-10-09 20:00 | 465 | 463
2019-10-09 20:30 | 456 | 455
2019-10-09 21:00 | 442 | 440
2019-10-09 21:30 | 428 | 424
2019-10-09 22:00 | 417 | 412
2019-10-09 22:30 | 409 | 403
2019-10-09 23:00 | 400 | 393
2019-10-09 23:30 | 379 | 370
2019-10-10 | 355 | 343
2019-10-10 00:30 | 338 | 324
2019-10-10 01:00 | 325 | 309
2019-10-10 01:30 | 315 | 298
2019-10-10 02:00 | 308 | 290
2019-10-10 02:30 | 305 | 286
2019-10-10 03:00 | 306 | 286
2019-10-10 03:30 | 307 | 287
2019-10-10 04:00 | 308 | 289
2019-10-10 04:30 | 317 | 299
2019-10-10 05:00 | 326 | 310
2019-10-10 05:30 | 343 | 328
2019-10-10 06:00 | 360 | 347
2019-10-10 06:30 | 382 | 373
2019-10-10 07:00 | 397 | 391
2019-10-10 07:30 | 394 | 390
2019-10-10 08:00 | 378 | 374
2019-10-10 08:30 | 358 | 354
2019-10-10 09:00 | 345 | 342
2019-10-10 09:30 | 343 | 341
2019-10-10 10:00 | 350 | 348
2019-10-10 10:30 | 350 | 348
2019-10-10 11:00 | 347 | 345
2019-10-10 11:30 | 342 | 340
2019-10-10 12:00 | 349 | 347
2019-10-10 12:30 | 351 | 347
2019-10-10 13:00 | 344 | 341
2019-10-10 13:30 | 372 | 369
2019-10-10 14:00 | 357 | 354
2019-10-10 14:30 | 354 | 350
2019-10-10 15:00 | 379 | 376
2019-10-10 15:30 | 409 | 406
2019-10-10 16:00 | 421 | 418
2019-10-10 16:30 | 435 | 432
2019-10-10 17:00 | 452 | 449
2019-10-10 17:30 | 468 | 466
2019-10-10 18:00 | 490 | 487
2019-10-10 18:30 | 496 | 494
2019-10-10 19:00 | 502 | 500
2019-10-10 19:30 | 486 | 483
2019-10-10 20:00 | 482 | 479
2019-10-10 20:30 | 478 | 475
2019-10-10 21:00 | 465 | 462
2019-10-10 21:30 | 445 | 442
2019-10-10 22:00 | 436 | 431
2019-10-10 22:30 | 424 | 418
2019-10-10 23:00 | 414 | 406
2019-10-10 23:30 | 396 | 387
2019-10-11 | 373 | 363
2019-10-11 00:30 | 348 | 335
2019-10-11 01:00 | 337 | 323
2019-10-11 01:30 | 327 | 311
2019-10-11 02:00 | 321 | 304
2019-10-11 02:30 | 318 | 300
2019-10-11 03:00 | 314 | 294
2019-10-11 03:30 | 317 | 297
2019-10-11 04:00 | 320 | 300
2019-10-11 04:30 | 328 | 310
2019-10-11 05:00 | 333 | 316
2019-10-11 05:30 | 348 | 333
2019-10-11 06:00 | 363 | 350
2019-10-11 06:30 | 385 | 376
2019-10-11 07:00 | 401 | 395
2019-10-11 07:30 | 408 | 404
2019-10-11 08:00 | 407 | 403
2019-10-11 08:30 | 400 | 397
2019-10-11 09:00 | 382 | 380
2019-10-11 09:30 | 366 | 364
2019-10-11 10:00 | 363 | 362
2019-10-11 10:30 | 392 | 391
2019-10-11 11:00 | 404 | 404
2019-10-11 11:30 | 403 | 402
2019-10-11 12:00 | 385 | 385
2019-10-11 12:30 | 393 | 392
2019-10-11 13:00 | 391 | 390
2019-10-11 13:30 | 381 | 380
2019-10-11 14:00 | 369 | 368
2019-10-11 14:30 | 370 | 369
2019-10-11 15:00 | 389 | 388
2019-10-11 15:30 | 409 | 409
2019-10-11 16:00 | 423 | 422
2019-10-11 16:30 | 438 | 437
2019-10-11 17:00 | 444 | 444
2019-10-11 17:30 | 445 | 444
2019-10-11 18:00 | 454 | 452
2019-10-11 18:30 | 463 | 461
2019-10-11 19:00 | 465 | 462
2019-10-11 19:30 | 459 | 457
2019-10-11 20:00 | 456 | 453
2019-10-11 20:30 | 450 | 447
2019-10-11 21:00 | 436 | 431
2019-10-11 21:30 | 426 | 420
2019-10-11 22:00 | 418 | 412
2019-10-11 22:30 | 407 | 400
2019-10-11 23:00 | 396 | 389
2019-10-11 23:30 | 381 | 373
2019-10-12 | 371 | 360
2019-10-12 00:30 | 342 | 332
2019-10-12 01:00 | 328 | 318
2019-10-12 01:30 | 320 | 309
2019-10-12 02:00 | 310 | 298
2019-10-12 02:30 | 302 | 289
2019-10-12 03:00 | 292 | 279
2019-10-12 03:30 | 296 | 282
2019-10-12 04:00 | 299 | 285
2019-10-12 04:30 | 297 | 283
2019-10-12 05:00 | 296 | 283
2019-10-12 05:30 | 311 | 299
2019-10-12 06:00 | 319 | 307
2019-10-12 06:30 | 332 | 320
2019-10-12 07:00 | 346 | 336
2019-10-12 07:30 | 367 | 359
2019-10-12 08:00 | 386 | 380
2019-10-12 08:30 | 395 | 391
2019-10-12 09:00 | 406 | 403
2019-10-12 09:30 | 415 | 412
2019-10-12 10:00 | 408 | 405
2019-10-12 10:30 | 408 | 406
2019-10-12 11:00 | 408 | 406
2019-10-12 11:30 | 397 | 395
2019-10-12 12:00 | 402 | 399
2019-10-12 12:30 | 378 | 375
2019-10-12 13:00 | 333 | 326
2019-10-12 13:30 | 299 | 290
2019-10-12 14:00 | 291 | 282
2019-10-12 14:30 | 303 | 294
2019-10-12 15:00 | 311 | 303
2019-10-12 15:30 | 320 | 312
2019-10-12 16:00 | 330 | 323
2019-10-12 16:30 | 348 | 343
2019-10-12 17:00 | 367 | 362
2019-10-12 17:30 | 378 | 374
2019-10-12 18:00 | 388 | 385
2019-10-12 18:30 | 410 | 408
2019-10-12 19:00 | 425 | 424
2019-10-12 19:30 | 412 | 410
2019-10-12 20:00 | 408 | 405
2019-10-12 20:30 | 407 | 405
2019-10-12 21:00 | 393 | 391
2019-10-12 21:30 | 383 | 380
2019-10-12 22:00 | 376 | 372
2019-10-12 22:30 | 366 | 362
2019-10-12 23:00 | 357 | 352
2019-10-12 23:30 | 342 | 336
2019-10-13 | 329 | 321
2019-10-13 00:30 | 310 | 301
2019-10-13 01:00 | 301 | 290
2019-10-13 01:30 | 293 | 280
2019-10-13 02:00 | 286 | 271
2019-10-13 02:30 | 276 | 260
2019-10-13 03:00 | 261 | 245
2019-10-13 03:30 | 264 | 247
2019-10-13 04:00 | 273 | 256
2019-10-13 04:30 | 271 | 255
2019-10-13 05:00 | 274 | 258
2019-10-13 05:30 | 280 | 263
2019-10-13 06:00 | 277 | 261
2019-10-13 06:30 | 280 | 265
2019-10-13 07:00 | 281 | 265
2019-10-13 07:30 | 276 | 261
2019-10-13 08:00 | 270 | 255
2019-10-13 08:30 | 268 | 254
2019-10-13 09:00 | 263 | 249
2019-10-13 09:30 | 258 | 245
2019-10-13 10:00 | 254 | 242
2019-10-13 10:30 | 251 | 239
2019-10-13 11:00 | 261 | 250
2019-10-13 11:30 | 277 | 268
2019-10-13 12:00 | 287 | 278
2019-10-13 12:30 | 292 | 284
2019-10-13 13:00 | 297 | 289
2019-10-13 13:30 | 302 | 295
2019-10-13 14:00 | 301 | 294
2019-10-13 14:30 | 293 | 286
2019-10-13 15:00 | 294 | 287
2019-10-13 15:30 | 300 | 293
2019-10-13 16:00 | 323 | 318
2019-10-13 16:30 | 340 | 335
2019-10-13 17:00 | 361 | 358
2019-10-13 17:30 | 377 | 374
2019-10-13 18:00 | 392 | 389
2019-10-13 18:30 | 420 | 415
2019-10-13 19:00 | 436 | 431
2019-10-13 19:30 | 433 | 427
2019-10-13 20:00 | 412 | 411
2019-10-13 20:30 | 412 | 410
2019-10-13 21:00 | 398 | 396
2019-10-13 21:30 | 384 | 381
2019-10-13 22:00 | 375 | 370
2019-10-13 22:30 | 366 | 361
2019-10-13 23:00 | 358 | 353
2019-10-13 23:30 | 346 | 340
2019-10-14 | 328 | 320
2019-10-14 00:30 | 309 | 299
2019-10-14 01:00 | 291 | 280
2019-10-14 01:30 | 278 | 265
2019-10-14 02:00 | 271 | 257
2019-10-14 02:30 | 268 | 254
2019-10-14 03:00 | 270 | 256
2019-10-14 03:30 | 275 | 261
2019-10-14 04:00 | 279 | 265
2019-10-14 04:30 | 292 | 280
2019-10-14 05:00 | 302 | 292
2019-10-14 05:30 | 318 | 309
2019-10-14 06:00 | 337 | 329
2019-10-14 06:30 | 368 | 363
2019-10-14 07:00 | 382 | 380
2019-10-14 07:30 | 389 | 387
2019-10-14 08:00 | 374 | 372
2019-10-14 08:30 | 357 | 355
2019-10-14 09:00 | 349 | 348
2019-10-14 09:30 | 338 | 336
2019-10-14 10:00 | 336 | 335
2019-10-14 10:30 | 343 | 341
2019-10-14 11:00 | 340 | 339
2019-10-14 11:30 | 328 | 327
2019-10-14 12:00 | 321 | 321
2019-10-14 12:30 | 318 | 317
2019-10-14 13:00 | 322 | 322
2019-10-14 13:30 | 327 | 327
2019-10-14 14:00 | 342 | 341
2019-10-14 14:30 | 350 | 349
2019-10-14 15:00 | 360 | 359
2019-10-14 15:30 | 371 | 370
2019-10-14 16:00 | 389 | 389
2019-10-14 16:30 | 405 | 405
2019-10-14 17:00 | 432 | 431
2019-10-14 17:30 | 446 | 444
2019-10-14 18:00 | 453 | 451
2019-10-14 18:30 | 461 | 460
2019-10-14 19:00 | 466 | 465
2019-10-14 19:30 | 452 | 450
2019-10-14 20:00 | 440 | 438
2019-10-14 20:30 | 432 | 431
2019-10-14 21:00 | 412 | 411
2019-10-14 21:30 | 395 | 393
2019-10-14 22:00 | 384 | 381
2019-10-14 22:30 | 372 | 368
2019-10-14 23:00 | 361 | 357
2019-10-14 23:30 | 348 | 342
2019-10-15 | 332 | 323
2019-10-15 00:30 | 312 | 303
2019-10-15 01:00 | 303 | 292
2019-10-15 01:30 | 296 | 284
2019-10-15 02:00 | 293 | 282
2019-10-15 02:30 | 289 | 277
2019-10-15 03:00 | 279 | 267
2019-10-15 03:30 | 284 | 272
2019-10-15 04:00 | 289 | 277
2019-10-15 04:30 | 295 | 284
2019-10-15 05:00 | 302 | 292
2019-10-15 05:30 | 315 | 306
2019-10-15 06:00 | 334 | 327
2019-10-15 06:30 | 364 | 361
2019-10-15 07:00 | 383 | 382
2019-10-15 07:30 | 396 | 394
2019-10-15 08:00 | 403 | 402
2019-10-15 08:30 | 401 | 400
2019-10-15 09:00 | 394 | 393
2019-10-15 09:30 | 379 | 378
2019-10-15 10:00 | 377 | 376
2019-10-15 10:30 | 371 | 370
2019-10-15 11:00 | 363 | 362
2019-10-15 11:30 | 359 | 358
2019-10-15 12:00 | 377 | 376
2019-10-15 12:30 | 390 | 388
2019-10-15 13:00 | 370 | 369
2019-10-15 13:30 | 410 | 409
2019-10-15 14:00 | 425 | 424
2019-10-15 14:30 | 437 | 436
2019-10-15 15:00 | 443 | 441
2019-10-15 15:30 | 443 | 442
2019-10-15 16:00 | 452 | 450
2019-10-15 16:30 | 464 | 463
2019-10-15 17:00 | 475 | 473
2019-10-15 17:30 | 481 | 480
2019-10-15 18:00 | 475 | 474
2019-10-15 18:30 | 481 | 480
2019-10-15 19:00 | 485 | 485
2019-10-15 19:30 | 472 | 472
2019-10-15 20:00 | 459 | 459
2019-10-15 20:30 | 454 | 454
2019-10-15 21:00 | 439 | 439
2019-10-15 21:30 | 424 | 423
2019-10-15 22:00 | 416 | 415
2019-10-15 22:30 | 405 | 404
2019-10-15 23:00 | 396 | 395
2019-10-15 23:30 | 378 | 376
2019-10-16 | 359 | 355
2019-10-16 00:30 | 332 | 326
2019-10-16 01:00 | 317 | 309
2019-10-16 01:30 | 314 | 301
2019-10-16 02:00 | 310 | 296
2019-10-16 02:30 | 309 | 294
2019-10-16 03:00 | 306 | 292
2019-10-16 03:30 | 307 | 292
2019-10-16 04:00 | 308 | 293
2019-10-16 04:30 | 312 | 298
2019-10-16 05:00 | 316 | 304
2019-10-16 05:30 | 329 | 317
2019-10-16 06:00 | 352 | 342
2019-10-16 06:30 | 385 | 379
2019-10-16 07:00 | 418 | 416
2019-10-16 07:30 | 439 | 438
2019-10-16 08:00 | 439 | 439
2019-10-16 08:30 | 435 | 435
2019-10-16 09:00 | 418 | 418
2019-10-16 09:30 | 411 | 411
2019-10-16 10:00 | 397 | 396
2019-10-16 10:30 | 385 | 385
2019-10-16 11:00 | 391 | 390
2019-10-16 11:30 | 395 | 394
2019-10-16 12:00 | 383 | 382
2019-10-16 12:30 | 379 | 378
2019-10-16 13:00 | 385 | 384
2019-10-16 13:30 | 397 | 396
2019-10-16 14:00 | 411 | 407
2019-10-16 14:30 | 436 | 432
2019-10-16 15:00 | 448 | 444
2019-10-16 15:30 | 463 | 459
2019-10-16 16:00 | 481 | 478
2019-10-16 16:30 | 497 | 494
2019-10-16 17:00 | 515 | 512
2019-10-16 17:30 | 512 | 509
2019-10-16 18:00 | 500 | 496
2019-10-16 18:30 | 507 | 503
2019-10-16 19:00 | 512 | 508
2019-10-16 19:30 | 501 | 497
2019-10-16 20:00 | 494 | 491
2019-10-16 20:30 | 482 | 481
2019-10-16 21:00 | 460 | 459
2019-10-16 21:30 | 444 | 443
2019-10-16 22:00 | 434 | 431
2019-10-16 22:30 | 417 | 413
2019-10-16 23:00 | 403 | 400
2019-10-16 23:30 | 384 | 381
2019-10-17 | 364 | 359
2019-10-17 00:30 | 340 | 333
2019-10-17 01:00 | 325 | 318
2019-10-17 01:30 | 312 | 304
2019-10-17 02:00 | 296 | 287
2019-10-17 02:30 | 283 | 274
2019-10-17 03:00 | 282 | 272
2019-10-17 03:30 | 281 | 271
2019-10-17 04:00 | 287 | 278
2019-10-17 04:30 | 295 | 286
2019-10-17 05:00 | 315 | 307
2019-10-17 05:30 | 325 | 317
2019-10-17 06:00 | 339 | 333
2019-10-17 06:30 | 384 | 380
2019-10-17 07:00 | 403 | 402
2019-10-17 07:30 | 412 | 408
2019-10-17 08:00 | 410 | 404
2019-10-17 08:30 | 411 | 406
2019-10-17 09:00 | 394 | 390
2019-10-17 09:30 | 389 | 385
2019-10-17 10:00 | 391 | 387
2019-10-17 10:30 | 388 | 385
2019-10-17 11:00 | 377 | 373
2019-10-17 11:30 | 379 | 376
2019-10-17 12:00 | 391 | 387
2019-10-17 12:30 | 411 | 408
2019-10-17 13:00 | 413 | 410
2019-10-17 13:30 | 418 | 416
2019-10-17 14:00 | 431 | 429
2019-10-17 14:30 | 456 | 453
2019-10-17 15:00 | 475 | 472
2019-10-17 15:30 | 506 | 502
2019-10-17 16:00 | 518 | 514
2019-10-17 16:30 | 525 | 521
2019-10-17 17:00 | 506 | 502
2019-10-17 17:30 | 482 | 477
2019-10-17 18:00 | 477 | 472
2019-10-17 18:30 | 484 | 483
2019-10-17 19:00 | 494 | 493
2019-10-17 19:30 | 489 | 488
2019-10-17 20:00 | 477 | 476
2019-10-17 20:30 | 472 | 470
2019-10-17 21:00 | 443 | 441
2019-10-17 21:30 | 431 | 428
2019-10-17 22:00 | 420 | 417
2019-10-17 22:30 | 411 | 407
2019-10-17 23:00 | 392 | 389
2019-10-17 23:30 | 374 | 371
2019-10-18 | 347 | 343
2019-10-18 00:30 | 323 | 318
2019-10-18 01:00 | 306 | 300
2019-10-18 01:30 | 292 | 286
2019-10-18 02:00 | 286 | 279
2019-10-18 02:30 | 282 | 275
2019-10-18 03:00 | 279 | 271
2019-10-18 03:30 | 279 | 272
2019-10-18 04:00 | 282 | 274
2019-10-18 04:30 | 290 | 283
2019-10-18 05:00 | 305 | 299
2019-10-18 05:30 | 314 | 308
2019-10-18 06:00 | 335 | 331
2019-10-18 06:30 | 371 | 368
2019-10-18 07:00 | 391 | 389
2019-10-18 07:30 | 399 | 397
2019-10-18 08:00 | 391 | 390
2019-10-18 08:30 | 399 | 399
2019-10-18 09:00 | 375 | 375
2019-10-18 09:30 | 368 | 368
2019-10-18 10:00 | 366 | 366
2019-10-18 10:30 | 361 | 360
2019-10-18 11:00 | 346 | 345
2019-10-18 11:30 | 340 | 339
2019-10-18 12:00 | 333 | 332
2019-10-18 12:30 | 334 | 333
2019-10-18 13:00 | 336 | 335
2019-10-18 13:30 | 341 | 341
2019-10-18 14:00 | 355 | 354
2019-10-18 14:30 | 371 | 370
2019-10-18 15:00 | 387 | 384
2019-10-18 15:30 | 410 | 408
2019-10-18 16:00 | 430 | 429
2019-10-18 16:30 | 451 | 450
2019-10-18 17:00 | 469 | 468
2019-10-18 17:30 | 467 | 467
2019-10-18 18:00 | 468 | 467
2019-10-18 18:30 | 467 | 467
2019-10-18 19:00 | 477 | 476
2019-10-18 19:30 | 471 | 470
2019-10-18 20:00 | 466 | 465
2019-10-18 20:30 | 455 | 455
2019-10-18 21:00 | 435 | 435
2019-10-18 21:30 | 416 | 415
2019-10-18 22:00 | 407 | 405
2019-10-18 22:30 | 396 | 394
2019-10-18 23:00 | 392 | 390
2019-10-18 23:30 | 378 | 376
2019-10-19 | 363 | 359
2019-10-19 00:30 | 340 | 334
2019-10-19 01:00 | 316 | 308
2019-10-19 01:30 | 308 | 299
2019-10-19 02:00 | 293 | 282
2019-10-19 02:30 | 283 | 272
2019-10-19 03:00 | 277 | 265
2019-10-19 03:30 | 274 | 262
2019-10-19 04:00 | 273 | 260
2019-10-19 04:30 | 274 | 262
2019-10-19 05:00 | 279 | 267
2019-10-19 05:30 | 281 | 268
2019-10-19 06:00 | 292 | 279
2019-10-19 06:30 | 310 | 299
2019-10-19 07:00 | 326 | 318
2019-10-19 07:30 | 328 | 322
2019-10-19 08:00 | 333 | 328
2019-10-19 08:30 | 341 | 339
2019-10-19 09:00 | 335 | 333
2019-10-19 09:30 | 360 | 359
2019-10-19 10:00 | 375 | 374
2019-10-19 10:30 | 370 | 368
2019-10-19 11:00 | 368 | 366
2019-10-19 11:30 | 370 | 368
2019-10-19 12:00 | 388 | 386
2019-10-19 12:30 | 360 | 357
2019-10-19 13:00 | 311 | 307
2019-10-19 13:30 | 287 | 282
2019-10-19 14:00 | 302 | 297
2019-10-19 14:30 | 321 | 317
2019-10-19 15:00 | 331 | 328
2019-10-19 15:30 | 355 | 353
2019-10-19 16:00 | 393 | 392
2019-10-19 16:30 | 410 | 410
2019-10-19 17:00 | 408 | 407
2019-10-19 17:30 | 408 | 407
2019-10-19 18:00 | 406 | 405
2019-10-19 18:30 | 415 | 415
2019-10-19 19:00 | 434 | 433
2019-10-19 19:30 | 430 | 429
2019-10-19 20:00 | 417 | 417
2019-10-19 20:30 | 414 | 413
2019-10-19 21:00 | 397 | 396
2019-10-19 21:30 | 392 | 390
2019-10-19 22:00 | 387 | 384
2019-10-19 22:30 | 382 | 379
2019-10-19 23:00 | 375 | 372
2019-10-19 23:30 | 363 | 359
2019-10-20 | 349 | 342
2019-10-20 00:30 | 323 | 313
2019-10-20 01:00 | 300 | 289
2019-10-20 01:30 | 294 | 281
2019-10-20 02:00 | 288 | 274
2019-10-20 02:30 | 282 | 267
2019-10-20 03:00 | 281 | 265
2019-10-20 03:30 | 282 | 266
2019-10-20 04:00 | 281 | 265
2019-10-20 04:30 | 281 | 265
2019-10-20 05:00 | 286 | 269
2019-10-20 05:30 | 287 | 267
2019-10-20 06:00 | 286 | 265
2019-10-20 06:30 | 296 | 277
2019-10-20 07:00 | 295 | 277
2019-10-20 07:30 | 302 | 287
2019-10-20 08:00 | 307 | 292
2019-10-20 08:30 | 309 | 295
2019-10-20 09:00 | 299 | 286
2019-10-20 09:30 | 294 | 282
2019-10-20 10:00 | 291 | 281
2019-10-20 10:30 | 286 | 276
2019-10-20 11:00 | 282 | 274
2019-10-20 11:30 | 276 | 268
2019-10-20 12:00 | 278 | 270
2019-10-20 12:30 | 285 | 277
2019-10-20 13:00 | 290 | 282
2019-10-20 13:30 | 299 | 292
2019-10-20 14:00 | 294 | 288
2019-10-20 14:30 | 304 | 298
2019-10-20 15:00 | 317 | 312
2019-10-20 15:30 | 335 | 331
2019-10-20 16:00 | 358 | 353
2019-10-20 16:30 | 379 | 375
2019-10-20 17:00 | 409 | 406
2019-10-20 17:30 | 417 | 415
2019-10-20 18:00 | 420 | 418
2019-10-20 18:30 | 442 | 441
2019-10-20 19:00 | 452 | 450
2019-10-20 19:30 | 440 | 437
2019-10-20 20:00 | 434 | 430
2019-10-20 20:30 | 424 | 419
2019-10-20 21:00 | 408 | 402
2019-10-20 21:30 | 400 | 393
2019-10-20 22:00 | 394 | 386
2019-10-20 22:30 | 387 | 378
2019-10-20 23:00 | 381 | 372
2019-10-20 23:30 | 360 | 352
2019-10-21 | 347 | 338
2019-10-21 00:30 | 322 | 312
2019-10-21 01:00 | 308 | 296
2019-10-21 01:30 | 301 | 288
2019-10-21 02:00 | 293 | 279
2019-10-21 02:30 | 288 | 274
2019-10-21 03:00 | 287 | 272
2019-10-21 03:30 | 289 | 274
2019-10-21 04:00 | 292 | 277
2019-10-21 04:30 | 300 | 286
2019-10-21 05:00 | 306 | 293
2019-10-21 05:30 | 313 | 300
2019-10-21 06:00 | 329 | 320
2019-10-21 06:30 | 357 | 351
2019-10-21 07:00 | 374 | 370
2019-10-21 07:30 | 381 | 378
2019-10-21 08:00 | 375 | 372
2019-10-21 08:30 | 378 | 376
2019-10-21 09:00 | 373 | 371
2019-10-21 09:30 | 359 | 357
2019-10-21 10:00 | 355 | 353
2019-10-21 10:30 | 348 | 346
2019-10-21 11:00 | 343 | 341
2019-10-21 11:30 | 340 | 338
2019-10-21 12:00 | 335 | 333
2019-10-21 12:30 | 328 | 326
2019-10-21 13:00 | 326 | 324
2019-10-21 13:30 | 327 | 325
2019-10-21 14:00 | 345 | 343
2019-10-21 14:30 | 357 | 355
2019-10-21 15:00 | 370 | 369
2019-10-21 15:30 | 382 | 381
2019-10-21 16:00 | 396 | 395
2019-10-21 16:30 | 414 | 413
2019-10-21 17:00 | 436 | 436
2019-10-21 17:30 | 441 | 440
2019-10-21 18:00 | 447 | 446
2019-10-21 18:30 | 453 | 452
2019-10-21 19:00 | 479 | 478
2019-10-21 19:30 | 459 | 458
2019-10-21 20:00 | 447 | 446
2019-10-21 20:30 | 433 | 433
2019-10-21 21:00 | 416 | 415
2019-10-21 21:30 | 404 | 403
2019-10-21 22:00 | 398 | 395
2019-10-21 22:30 | 387 | 384
2019-10-21 23:00 | 379 | 375
2019-10-21 23:30 | 368 | 363
2019-10-22 | 346 | 338
2019-10-22 00:30 | 322 | 312
2019-10-22 01:00 | 304 | 293
2019-10-22 01:30 | 293 | 281
2019-10-22 02:00 | 280 | 267
2019-10-22 02:30 | 280 | 267
2019-10-22 03:00 | 279 | 265
2019-10-22 03:30 | 280 | 266
2019-10-22 04:00 | 286 | 273
2019-10-22 04:30 | 299 | 287
2019-10-22 05:00 | 312 | 301
2019-10-22 05:30 | 323 | 312
2019-10-22 06:00 | 342 | 333
2019-10-22 06:30 | 369 | 364
2019-10-22 07:00 | 385 | 381
2019-10-22 07:30 | 394 | 391
2019-10-22 08:00 | 398 | 396
2019-10-22 08:30 | 387 | 385
2019-10-22 09:00 | 374 | 372
2019-10-22 09:30 | 382 | 380
2019-10-22 10:00 | 357 | 356
2019-10-22 10:30 | 356 | 354
2019-10-22 11:00 | 363 | 361
2019-10-22 11:30 | 381 | 379
2019-10-22 12:00 | 376 | 374
2019-10-22 12:30 | 356 | 354
2019-10-22 13:00 | 358 | 356
2019-10-22 13:30 | 358 | 356
2019-10-22 14:00 | 356 | 354
2019-10-22 14:30 | 361 | 359
2019-10-22 15:00 | 376 | 374
2019-10-22 15:30 | 394 | 392
2019-10-22 16:00 | 417 | 416
2019-10-22 16:30 | 440 | 439
2019-10-22 17:00 | 443 | 442
2019-10-22 17:30 | 456 | 455
2019-10-22 18:00 | 468 | 467
2019-10-22 18:30 | 474 | 474
2019-10-22 19:00 | 483 | 483
2019-10-22 19:30 | 474 | 473
2019-10-22 20:00 | 453 | 452
2019-10-22 20:30 | 439 | 438
2019-10-22 21:00 | 420 | 419
2019-10-22 21:30 | 404 | 402
2019-10-22 22:00 | 394 | 392
2019-10-22 22:30 | 385 | 382
2019-10-22 23:00 | 378 | 375
2019-10-22 23:30 | 364 | 360
2019-10-23 | 331 | 326
2019-10-23 00:30 | 307 | 299
2019-10-23 01:00 | 305 | 296
2019-10-23 01:30 | 293 | 282
2019-10-23 02:00 | 287 | 275
2019-10-23 02:30 | 285 | 274
2019-10-23 03:00 | 286 | 275
2019-10-23 03:30 | 288 | 276
2019-10-23 04:00 | 286 | 274
2019-10-23 04:30 | 302 | 291
2019-10-23 05:00 | 311 | 301
2019-10-23 05:30 | 321 | 311
2019-10-23 06:00 | 333 | 325
2019-10-23 06:30 | 364 | 359
2019-10-23 07:00 | 382 | 380
2019-10-23 07:30 | 391 | 390
2019-10-23 08:00 | 375 | 373
2019-10-23 08:30 | 371 | 370
2019-10-23 09:00 | 356 | 354
2019-10-23 09:30 | 339 | 338
2019-10-23 10:00 | 339 | 338
2019-10-23 10:30 | 339 | 338
2019-10-23 11:00 | 338 | 337
2019-10-23 11:30 | 337 | 335
2019-10-23 12:00 | 337 | 336
2019-10-23 12:30 | 337 | 336
2019-10-23 13:00 | 342 | 341
2019-10-23 13:30 | 356 | 355
2019-10-23 14:00 | 366 | 365
2019-10-23 14:30 | 383 | 382
2019-10-23 15:00 | 400 | 398
2019-10-23 15:30 | 417 | 415
2019-10-23 16:00 | 434 | 433
2019-10-23 16:30 | 454 | 453
2019-10-23 17:00 | 470 | 469
2019-10-23 17:30 | 482 | 481
2019-10-23 18:00 | 493 | 492
2019-10-23 18:30 | 493 | 492
2019-10-23 19:00 | 499 | 499
2019-10-23 19:30 | 484 | 483
2019-10-23 20:00 | 468 | 467
2019-10-23 20:30 | 457 | 455
2019-10-23 21:00 | 435 | 434
2019-10-23 21:30 | 419 | 417
2019-10-23 22:00 | 404 | 400
2019-10-23 22:30 | 399 | 394
2019-10-23 23:00 | 390 | 385
2019-10-23 23:30 | 377 | 371
2019-10-24 | 355 | 349
2019-10-24 00:30 | 327 | 319
2019-10-24 01:00 | 314 | 305
2019-10-24 01:30 | 304 | 295
2019-10-24 02:00 | 297 | 288
2019-10-24 02:30 | 292 | 282
2019-10-24 03:00 | 284 | 275
2019-10-24 03:30 | 283 | 273
2019-10-24 04:00 | 284 | 275
2019-10-24 04:30 | 292 | 283
2019-10-24 05:00 | 302 | 293
2019-10-24 05:30 | 324 | 315
2019-10-24 06:00 | 338 | 331
2019-10-24 06:30 | 362 | 357
2019-10-24 07:00 | 377 | 374
2019-10-24 07:30 | 383 | 382
2019-10-24 08:00 | 378 | 377
2019-10-24 08:30 | 375 | 372
2019-10-24 09:00 | 349 | 347
2019-10-24 09:30 | 343 | 341
2019-10-24 10:00 | 337 | 335
2019-10-24 10:30 | 333 | 331
2019-10-24 11:00 | 335 | 333
2019-10-24 11:30 | 338 | 336
2019-10-24 12:00 | 339 | 338
2019-10-24 12:30 | 345 | 344
2019-10-24 13:00 | 357 | 355
2019-10-24 13:30 | 364 | 363
2019-10-24 14:00 | 375 | 374
2019-10-24 14:30 | 389 | 387
2019-10-24 15:00 | 407 | 405
2019-10-24 15:30 | 423 | 422
2019-10-24 16:00 | 447 | 446
2019-10-24 16:30 | 466 | 465
2019-10-24 17:00 | 484 | 483
2019-10-24 17:30 | 496 | 494
2019-10-24 18:00 | 491 | 490
2019-10-24 18:30 | 489 | 488
2019-10-24 19:00 | 491 | 491
2019-10-24 19:30 | 478 | 477
2019-10-24 20:00 | 454 | 454
2019-10-24 20:30 | 451 | 450
2019-10-24 21:00 | 433 | 433
2019-10-24 21:30 | 419 | 418
2019-10-24 22:00 | 405 | 403
2019-10-24 22:30 | 384 | 382
2019-10-24 23:00 | 382 | 378
2019-10-24 23:30 | 366 | 360
2019-10-25 | 342 | 335
2019-10-25 00:30 | 318 | 310
2019-10-25 01:00 | 301 | 290
2019-10-25 01:30 | 290 | 278
2019-10-25 02:00 | 285 | 273
2019-10-25 02:30 | 282 | 269
2019-10-25 03:00 | 274 | 260
2019-10-25 03:30 | 268 | 255
2019-10-25 04:00 | 272 | 258
2019-10-25 04:30 | 285 | 273
2019-10-25 05:00 | 298 | 286
2019-10-25 05:30 | 311 | 300
2019-10-25 06:00 | 332 | 323
2019-10-25 06:30 | 361 | 355
2019-10-25 07:00 | 376 | 372
2019-10-25 07:30 | 379 | 377
2019-10-25 08:00 | 376 | 374
2019-10-25 08:30 | 364 | 362
2019-10-25 09:00 | 355 | 353
2019-10-25 09:30 | 343 | 342
2019-10-25 10:00 | 334 | 332
2019-10-25 10:30 | 332 | 331
2019-10-25 11:00 | 337 | 337
2019-10-25 11:30 | 341 | 340
2019-10-25 12:00 | 341 | 340
2019-10-25 12:30 | 347 | 345
2019-10-25 13:00 | 345 | 343
2019-10-25 13:30 | 361 | 360
2019-10-25 14:00 | 376 | 376
2019-10-25 14:30 | 381 | 381
2019-10-25 15:00 | 395 | 395
2019-10-25 15:30 | 410 | 410
2019-10-25 16:00 | 433 | 433
2019-10-25 16:30 | 446 | 446
2019-10-25 17:00 | 451 | 451
2019-10-25 17:30 | 449 | 449
2019-10-25 18:00 | 442 | 441
2019-10-25 18:30 | 446 | 443
2019-10-25 19:00 | 459 | 456
2019-10-25 19:30 | 446 | 442
2019-10-25 20:00 | 437 | 434
2019-10-25 20:30 | 432 | 432
2019-10-25 21:00 | 418 | 417
2019-10-25 21:30 | 402 | 400
2019-10-25 22:00 | 391 | 390
2019-10-25 22:30 | 387 | 384
2019-10-25 23:00 | 371 | 369
2019-10-25 23:30 | 352 | 348
2019-10-26 | 334 | 328
2019-10-26 00:30 | 309 | 301
2019-10-26 01:00 | 293 | 285
2019-10-26 01:30 | 275 | 265
2019-10-26 02:00 | 270 | 260
2019-10-26 02:30 | 269 | 258
2019-10-26 03:00 | 269 | 257
2019-10-26 03:30 | 269 | 256
2019-10-26 04:00 | 270 | 257
2019-10-26 04:30 | 271 | 258
2019-10-26 05:00 | 275 | 262
2019-10-26 05:30 | 274 | 260
2019-10-26 06:00 | 283 | 270
2019-10-26 06:30 | 298 | 286
2019-10-26 07:00 | 308 | 297
2019-10-26 07:30 | 310 | 299
2019-10-26 08:00 | 310 | 301
2019-10-26 08:30 | 309 | 302
2019-10-26 09:00 | 307 | 300
2019-10-26 09:30 | 310 | 305
2019-10-26 10:00 | 300 | 296
2019-10-26 10:30 | 295 | 291
2019-10-26 11:00 | 292 | 289
2019-10-26 11:30 | 289 | 285
2019-10-26 12:00 | 288 | 284
2019-10-26 12:30 | 283 | 279
2019-10-26 13:00 | 289 | 285
2019-10-26 13:30 | 295 | 291
2019-10-26 14:00 | 303 | 300
2019-10-26 14:30 | 314 | 311
2019-10-26 15:00 | 327 | 324
2019-10-26 15:30 | 340 | 338
2019-10-26 16:00 | 370 | 368
2019-10-26 16:30 | 392 | 390
2019-10-26 17:00 | 409 | 406
2019-10-26 17:30 | 417 | 412
2019-10-26 18:00 | 419 | 414
2019-10-26 18:30 | 424 | 419
2019-10-26 19:00 | 433 | 428
2019-10-26 19:30 | 428 | 421
2019-10-26 20:00 | 422 | 420
2019-10-26 20:30 | 417 | 417
2019-10-26 21:00 | 399 | 398
2019-10-26 21:30 | 398 | 396
2019-10-26 22:00 | 383 | 381
2019-10-26 22:30 | 378 | 375
2019-10-26 23:00 | 375 | 372
2019-10-26 23:30 | 363 | 359
2019-10-27 | 347 | 341
2019-10-27 00:30 | 325 | 317
2019-10-27 01:00 | 309 | 299
2019-10-27 01:30 | 305 | 290
2019-10-27 02:00 | 301 | 284
2019-10-27 02:30 | 296 | 278
2019-10-27 03:00 | 294 | 275
2019-10-27 03:30 | 292 | 273
2019-10-27 04:00 | 294 | 275
2019-10-27 04:30 | 295 | 276
2019-10-27 05:00 | 301 | 281
2019-10-27 05:30 | 298 | 277
2019-10-27 06:00 | 295 | 275
2019-10-27 06:30 | 304 | 284
2019-10-27 07:00 | 301 | 283
2019-10-27 07:30 | 302 | 285
2019-10-27 08:00 | 300 | 285
2019-10-27 08:30 | 303 | 290
2019-10-27 09:00 | 302 | 290
2019-10-27 09:30 | 303 | 293
2019-10-27 10:00 | 291 | 281
2019-10-27 10:30 | 292 | 283
2019-10-27 11:00 | 291 | 283
2019-10-27 11:30 | 289 | 281
2019-10-27 12:00 | 292 | 284
2019-10-27 12:30 | 296 | 288
2019-10-27 13:00 | 297 | 292
2019-10-27 13:30 | 303 | 299
2019-10-27 14:00 | 313 | 309
2019-10-27 14:30 | 322 | 319
2019-10-27 15:00 | 336 | 333
2019-10-27 15:30 | 356 | 354
2019-10-27 16:00 | 376 | 373
2019-10-27 16:30 | 402 | 400
2019-10-27 17:00 | 419 | 417
2019-10-27 17:30 | 427 | 425
2019-10-27 18:00 | 437 | 435
2019-10-27 18:30 | 450 | 449
2019-10-27 19:00 | 466 | 462
2019-10-27 19:30 | 459 | 455
2019-10-27 20:00 | 453 | 451
2019-10-27 20:30 | 449 | 449
2019-10-27 21:00 | 437 | 436
2019-10-27 21:30 | 429 | 427
2019-10-27 22:00 | 417 | 415
2019-10-27 22:30 | 408 | 406
2019-10-27 23:00 | 389 | 386
2019-10-27 23:30 | 378 | 374
2019-10-28 | 366 | 360
2019-10-28 00:30 | 341 | 334
2019-10-28 01:00 | 328 | 319
2019-10-28 01:30 | 317 | 307
2019-10-28 02:00 | 309 | 300
2019-10-28 02:30 | 311 | 300
2019-10-28 03:00 | 305 | 295
2019-10-28 03:30 | 306 | 296
2019-10-28 04:00 | 314 | 304
2019-10-28 04:30 | 319 | 309
2019-10-28 05:00 | 325 | 317
2019-10-28 05:30 | 338 | 330
2019-10-28 06:00 | 358 | 352
2019-10-28 06:30 | 384 | 382
2019-10-28 07:00 | 407 | 406
2019-10-28 07:30 | 423 | 422
2019-10-28 08:00 | 432 | 431
2019-10-28 08:30 | 437 | 434
2019-10-28 09:00 | 435 | 432
2019-10-28 09:30 | 428 | 425
2019-10-28 10:00 | 423 | 420
2019-10-28 10:30 | 416 | 413
2019-10-28 11:00 | 408 | 404
2019-10-28 11:30 | 407 | 403
2019-10-28 12:00 | 415 | 411
2019-10-28 12:30 | 429 | 426
2019-10-28 13:00 | 428 | 425
2019-10-28 13:30 | 450 | 448
2019-10-28 14:00 | 449 | 446
2019-10-28 14:30 | 464 | 461
2019-10-28 15:00 | 460 | 457
2019-10-28 15:30 | 474 | 471
2019-10-28 16:00 | 483 | 480
2019-10-28 16:30 | 499 | 496
2019-10-28 17:00 | 514 | 511
2019-10-28 17:30 | 511 | 508
2019-10-28 18:00 | 510 | 506
2019-10-28 18:30 | 513 | 509
2019-10-28 19:00 | 513 | 509
2019-10-28 19:30 | 504 | 499
2019-10-28 20:00 | 500 | 495
2019-10-28 20:30 | 484 | 482
2019-10-28 21:00 | 465 | 463
2019-10-28 21:30 | 451 | 449
2019-10-28 22:00 | 443 | 440
2019-10-28 22:30 | 434 | 430
2019-10-28 23:00 | 424 | 419
2019-10-28 23:30 | 406 | 401
2019-10-29 | 379 | 373
2019-10-29 00:30 | 352 | 345
2019-10-29 01:00 | 337 | 330
2019-10-29 01:30 | 331 | 322
2019-10-29 02:00 | 322 | 313
2019-10-29 02:30 | 318 | 309
2019-10-29 03:00 | 313 | 303
2019-10-29 03:30 | 316 | 306
2019-10-29 04:00 | 319 | 309
2019-10-29 04:30 | 330 | 320
2019-10-29 05:00 | 333 | 324
2019-10-29 05:30 | 341 | 332
2019-10-29 06:00 | 357 | 350
2019-10-29 06:30 | 377 | 373
2019-10-29 07:00 | 394 | 391
2019-10-29 07:30 | 402 | 399
2019-10-29 08:00 | 403 | 401
2019-10-29 08:30 | 405 | 403
2019-10-29 09:00 | 398 | 396
2019-10-29 09:30 | 390 | 388
2019-10-29 10:00 | 386 | 384
2019-10-29 10:30 | 382 | 381
2019-10-29 11:00 | 383 | 382
2019-10-29 11:30 | 381 | 380
2019-10-29 12:00 | 382 | 381
2019-10-29 12:30 | 386 | 385
2019-10-29 13:00 | 388 | 387
2019-10-29 13:30 | 394 | 393
2019-10-29 14:00 | 407 | 405
2019-10-29 14:30 | 420 | 417
2019-10-29 15:00 | 440 | 438
2019-10-29 15:30 | 457 | 454
2019-10-29 16:00 | 478 | 471
2019-10-29 16:30 | 501 | 493
2019-10-29 17:00 | 511 | 503
2019-10-29 17:30 | 510 | 502
2019-10-29 18:00 | 520 | 512
2019-10-29 18:30 | 518 | 509
2019-10-29 19:00 | 528 | 519
2019-10-29 19:30 | 524 | 515
2019-10-29 20:00 | 514 | 505
2019-10-29 20:30 | 510 | 503
2019-10-29 21:00 | 485 | 481
2019-10-29 21:30 | 464 | 460
2019-10-29 22:00 | 455 | 449
2019-10-29 22:30 | 446 | 440
2019-10-29 23:00 | 432 | 426
2019-10-29 23:30 | 409 | 404
2019-10-30 | 387 | 380
2019-10-30 00:30 | 354 | 347
2019-10-30 01:00 | 343 | 335
2019-10-30 01:30 | 334 | 326
2019-10-30 02:00 | 326 | 317
2019-10-30 02:30 | 318 | 310
2019-10-30 03:00 | 318 | 308
2019-10-30 03:30 | 322 | 311
2019-10-30 04:00 | 325 | 315
2019-10-30 04:30 | 334 | 324
2019-10-30 05:00 | 345 | 336
2019-10-30 05:30 | 351 | 341
2019-10-30 06:00 | 365 | 357
2019-10-30 06:30 | 392 | 385
2019-10-30 07:00 | 424 | 420
2019-10-30 07:30 | 444 | 439
2019-10-30 08:00 | 442 | 439
2019-10-30 08:30 | 437 | 434
2019-10-30 09:00 | 452 | 449
2019-10-30 09:30 | 445 | 443
2019-10-30 10:00 | 443 | 440
2019-10-30 10:30 | 445 | 443
2019-10-30 11:00 | 437 | 435
2019-10-30 11:30 | 438 | 436
2019-10-30 12:00 | 432 | 430
2019-10-30 12:30 | 424 | 422
2019-10-30 13:00 | 425 | 423
2019-10-30 13:30 | 448 | 446
2019-10-30 14:00 | 458 | 456
2019-10-30 14:30 | 474 | 472
2019-10-30 15:00 | 483 | 481
2019-10-30 15:30 | 462 | 460
2019-10-30 16:00 | 445 | 442
2019-10-30 16:30 | 435 | 432
2019-10-30 17:00 | 451 | 448
2019-10-30 17:30 | 455 | 452
2019-10-30 18:00 | 451 | 449
2019-10-30 18:30 | 458 | 455
2019-10-30 19:00 | 465 | 462
2019-10-30 19:30 | 459 | 456
2019-10-30 20:00 | 456 | 452
2019-10-30 20:30 | 444 | 442
2019-10-30 21:00 | 426 | 424
2019-10-30 21:30 | 409 | 406
2019-10-30 22:00 | 397 | 394
2019-10-30 22:30 | 384 | 381
2019-10-30 23:00 | 377 | 373
2019-10-30 23:30 | 362 | 358
2019-10-31 | 341 | 335
2019-10-31 00:30 | 317 | 310
2019-10-31 01:00 | 299 | 291
2019-10-31 01:30 | 290 | 282
2019-10-31 02:00 | 288 | 280
2019-10-31 02:30 | 287 | 279
2019-10-31 03:00 | 282 | 274
2019-10-31 03:30 | 281 | 272
2019-10-31 04:00 | 276 | 268
2019-10-31 04:30 | 280 | 272
2019-10-31 05:00 | 294 | 286
2019-10-31 05:30 | 306 | 298
2019-10-31 06:00 | 321 | 314
2019-10-31 06:30 | 351 | 346
2019-10-31 07:00 | 377 | 374
2019-10-31 07:30 | 391 | 384
2019-10-31 08:00 | 391 | 384
2019-10-31 08:30 | 395 | 388
2019-10-31 09:00 | 387 | 381
2019-10-31 09:30 | 382 | 375
2019-10-31 10:00 | 386 | 379
2019-10-31 10:30 | 385 | 378
2019-10-31 11:00 | 378 | 371
2019-10-31 11:30 | 369 | 362
2019-10-31 12:00 | 366 | 359
2019-10-31 12:30 | 366 | 359
2019-10-31 13:00 | 365 | 358
2019-10-31 13:30 | 372 | 365
2019-10-31 14:00 | 382 | 375
2019-10-31 14:30 | 395 | 388
2019-10-31 15:00 | 411 | 405
2019-10-31 15:30 | 432 | 426
2019-10-31 16:00 | 448 | 441
2019-10-31 16:30 | 466 | 459
2019-10-31 17:00 | 484 | 477
2019-10-31 17:30 | 483 | 475
2019-10-31 18:00 | 485 | 477
2019-10-31 18:30 | 482 | 473
2019-10-31 19:00 | 487 | 478
2019-10-31 19:30 | 474 | 465
2019-10-31 20:00 | 462 | 458
2019-10-31 20:30 | 452 | 448
2019-10-31 21:00 | 429 | 424
2019-10-31 21:30 | 418 | 412
2019-10-31 22:00 | 395 | 389
2019-10-31 22:30 | 394 | 389
2019-10-31 23:00 | 381 | 376
2019-10-31 23:30 | 365 | 358
2019-11-01 | 345 | 337
2019-11-01 00:30 | 319 | 309
2019-11-01 01:00 | 304 | 294
2019-11-01 01:30 | 298 | 287
2019-11-01 02:00 | 296 | 285
2019-11-01 02:30 | 298 | 286
2019-11-01 03:00 | 297 | 285
2019-11-01 03:30 | 294 | 283
2019-11-01 04:00 | 291 | 279
2019-11-01 04:30 | 294 | 283
2019-11-01 05:00 | 298 | 287
2019-11-01 05:30 | 302 | 291
2019-11-01 06:00 | 317 | 308
2019-11-01 06:30 | 353 | 346
2019-11-01 07:00 | 377 | 372
2019-11-01 07:30 | 395 | 389
2019-11-01 08:00 | 406 | 398
2019-11-01 08:30 | 408 | 396
2019-11-01 09:00 | 413 | 401
2019-11-01 09:30 | 412 | 401
2019-11-01 10:00 | 424 | 415
2019-11-01 10:30 | 512 | 507
2019-11-01 11:00 | 503 | 500
2019-11-01 11:30 | 499 | 498
2019-11-01 12:00 | 497 | 496
2019-11-01 12:30 | 505 | 504
2019-11-01 13:00 | 507 | 506
2019-11-01 13:30 | 514 | 513
2019-11-01 14:00 | 505 | 504
2019-11-01 14:30 | 523 | 522
2019-11-01 15:00 | 534 | 532
2019-11-01 15:30 | 552 | 546
2019-11-01 16:00 | 571 | 565
2019-11-01 16:30 | 580 | 574
2019-11-01 17:00 | 584 | 579
2019-11-01 17:30 | 574 | 567
2019-11-01 18:00 | 555 | 550
2019-11-01 18:30 | 545 | 544
2019-11-01 19:00 | 555 | 555
2019-11-01 19:30 | 551 | 551
2019-11-01 20:00 | 544 | 543
2019-11-01 20:30 | 529 | 528
2019-11-01 21:00 | 500 | 499
2019-11-01 21:30 | 489 | 487
2019-11-01 22:00 | 477 | 475
2019-11-01 22:30 | 471 | 467
2019-11-01 23:00 | 455 | 451
2019-11-01 23:30 | 427 | 421
2019-11-02 | 412 | 404
2019-11-02 00:30 | 384 | 375
2019-11-02 01:00 | 375 | 365
2019-11-02 01:30 | 357 | 347
2019-11-02 02:00 | 351 | 341
2019-11-02 02:30 | 354 | 345
2019-11-02 03:00 | 356 | 348
2019-11-02 03:30 | 355 | 346
2019-11-02 04:00 | 363 | 354
2019-11-02 04:30 | 357 | 348
2019-11-02 05:00 | 346 | 337
2019-11-02 05:30 | 351 | 342
2019-11-02 06:00 | 353 | 344
2019-11-02 06:30 | 376 | 368
2019-11-02 07:00 | 399 | 392
2019-11-02 07:30 | 412 | 407
2019-11-02 08:00 | 422 | 419
2019-11-02 08:30 | 419 | 417
2019-11-02 09:00 | 418 | 417
2019-11-02 09:30 | 423 | 422
2019-11-02 10:00 | 422 | 421
2019-11-02 10:30 | 426 | 426
2019-11-02 11:00 | 456 | 456
2019-11-02 11:30 | 467 | 464
2019-11-02 12:00 | 452 | 447
2019-11-02 12:30 | 453 | 449
2019-11-02 13:00 | 434 | 430
2019-11-02 13:30 | 451 | 448
2019-11-02 14:00 | 443 | 439
2019-11-02 14:30 | 432 | 427
2019-11-02 15:00 | 444 | 440
2019-11-02 15:30 | 460 | 457
2019-11-02 16:00 | 477 | 474
2019-11-02 16:30 | 487 | 485
2019-11-02 17:00 | 493 | 491
2019-11-02 17:30 | 500 | 498
2019-11-02 18:00 | 492 | 490
2019-11-02 18:30 | 494 | 493
2019-11-02 19:00 | 504 | 503
2019-11-02 19:30 | 497 | 497
2019-11-02 20:00 | 488 | 488
2019-11-02 20:30 | 480 | 480
2019-11-02 21:00 | 466 | 465
2019-11-02 21:30 | 461 | 460
2019-11-02 22:00 | 460 | 459
2019-11-02 22:30 | 451 | 450
2019-11-02 23:00 | 437 | 436
2019-11-02 23:30 | 429 | 427
2019-11-03 | 410 | 408
2019-11-03 00:30 | 383 | 378
2019-11-03 01:00 | 365 | 359
2019-11-03 01:30 | 352 | 345
2019-11-03 02:00 | 339 | 330
2019-11-03 02:30 | 333 | 323
2019-11-03 03:00 | 333 | 322
2019-11-03 03:30 | 340 | 330
2019-11-03 04:00 | 348 | 338
2019-11-03 04:30 | 345 | 336
2019-11-03 05:00 | 345 | 334
2019-11-03 05:30 | 344 | 331
2019-11-03 06:00 | 342 | 329
2019-11-03 06:30 | 367 | 358
2019-11-03 07:00 | 366 | 358
2019-11-03 07:30 | 379 | 374
2019-11-03 08:00 | 385 | 381
2019-11-03 08:30 | 395 | 391
2019-11-03 09:00 | 401 | 397
2019-11-03 09:30 | 406 | 402
2019-11-03 10:00 | 394 | 391
2019-11-03 10:30 | 382 | 379
2019-11-03 11:00 | 378 | 375
2019-11-03 11:30 | 373 | 371
2019-11-03 12:00 | 373 | 370
2019-11-03 12:30 | 372 | 370
2019-11-03 13:00 | 365 | 363
2019-11-03 13:30 | 365 | 363
2019-11-03 14:00 | 370 | 368
2019-11-03 14:30 | 394 | 392
2019-11-03 15:00 | 418 | 416
2019-11-03 15:30 | 434 | 432
2019-11-03 16:00 | 464 | 462
2019-11-03 16:30 | 491 | 490
2019-11-03 17:00 | 507 | 506
2019-11-03 17:30 | 503 | 502
2019-11-03 18:00 | 494 | 493
2019-11-03 18:30 | 498 | 497
2019-11-03 19:00 | 515 | 514
2019-11-03 19:30 | 504 | 504
2019-11-03 20:00 | 498 | 498
2019-11-03 20:30 | 492 | 491
2019-11-03 21:00 | 479 | 478
2019-11-03 21:30 | 466 | 465
2019-11-03 22:00 | 457 | 456
2019-11-03 22:30 | 449 | 448
2019-11-03 23:00 | 436 | 435
2019-11-03 23:30 | 419 | 418
2019-11-04 | 411 | 408
2019-11-04 00:30 | 382 | 378
2019-11-04 01:00 | 355 | 349
2019-11-04 01:30 | 332 | 323
2019-11-04 02:00 | 321 | 312
2019-11-04 02:30 | 319 | 310
2019-11-04 03:00 | 321 | 312
2019-11-04 03:30 | 329 | 320
2019-11-04 04:00 | 334 | 325
2019-11-04 04:30 | 334 | 327
2019-11-04 05:00 | 346 | 340
2019-11-04 05:30 | 379 | 374
2019-11-04 06:00 | 416 | 412
2019-11-04 06:30 | 460 | 457
2019-11-04 07:00 | 491 | 489
2019-11-04 07:30 | 441 | 438
2019-11-04 08:00 | 322 | 319
2019-11-04 08:30 | 342 | 338
2019-11-04 09:00 | 338 | 331
2019-11-04 09:30 | 306 | 304
2019-11-04 10:00 | 295 | 294
2019-11-04 10:30 | 297 | 297
2019-11-04 11:00 | 310 | 310
2019-11-04 11:30 | 312 | 312
2019-11-04 12:00 | 313 | 313
2019-11-04 12:30 | 328 | 328
2019-11-04 13:00 | 340 | 339
2019-11-04 13:30 | 340 | 339
2019-11-04 14:00 | 348 | 347
2019-11-04 14:30 | 344 | 342
2019-11-04 15:00 | 351 | 350
2019-11-04 15:30 | 361 | 360
2019-11-04 16:00 | 383 | 380
2019-11-04 16:30 | 394 | 387
2019-11-04 17:00 | 385 | 377
2019-11-04 17:30 | 376 | 367
2019-11-04 18:00 | 376 | 371
2019-11-04 18:30 | 373 | 368
2019-11-04 19:00 | 377 | 374
2019-11-04 19:30 | 375 | 369
2019-11-04 20:00 | 367 | 361
2019-11-04 20:30 | 351 | 344
2019-11-04 21:00 | 336 | 332
2019-11-04 21:30 | 324 | 322
2019-11-04 22:00 | 319 | 315
2019-11-04 22:30 | 313 | 309
2019-11-04 23:00 | 304 | 301
2019-11-04 23:30 | 294 | 289
2019-11-05 | 282 | 277
2019-11-05 00:30 | 258 | 252
2019-11-05 01:00 | 245 | 240
2019-11-05 01:30 | 235 | 229
2019-11-05 02:00 | 233 | 226
2019-11-05 02:30 | 230 | 222
2019-11-05 03:00 | 233 | 226
2019-11-05 03:30 | 231 | 223
2019-11-05 04:00 | 229 | 221
2019-11-05 04:30 | 233 | 226
2019-11-05 05:00 | 235 | 227
2019-11-05 05:30 | 252 | 245
2019-11-05 06:00 | 261 | 255
2019-11-05 06:30 | 280 | 278
2019-11-05 07:00 | 297 | 296
2019-11-05 07:30 | 308 | 307
2019-11-05 08:00 | 314 | 312
2019-11-05 08:30 | 316 | 315
2019-11-05 09:00 | 304 | 303
2019-11-05 09:30 | 295 | 294
2019-11-05 10:00 | 291 | 290
2019-11-05 10:30 | 286 | 286
2019-11-05 11:00 | 280 | 280
2019-11-05 11:30 | 271 | 270
2019-11-05 12:00 | 268 | 267
2019-11-05 12:30 | 276 | 275
2019-11-05 13:00 | 262 | 260
2019-11-05 13:30 | 258 | 256
2019-11-05 14:00 | 261 | 259
2019-11-05 14:30 | 267 | 265
2019-11-05 15:00 | 284 | 283
2019-11-05 15:30 | 291 | 289
2019-11-05 16:00 | 313 | 313
2019-11-05 16:30 | 321 | 321
2019-11-05 17:00 | 338 | 338
2019-11-05 17:30 | 336 | 336
2019-11-05 18:00 | 341 | 340
2019-11-05 18:30 | 343 | 342
2019-11-05 19:00 | 353 | 352
2019-11-05 19:30 | 350 | 348
2019-11-05 20:00 | 346 | 343
2019-11-05 20:30 | 337 | 333
2019-11-05 21:00 | 321 | 318
2019-11-05 21:30 | 311 | 310
2019-11-05 22:00 | 304 | 302
2019-11-05 22:30 | 292 | 289
2019-11-05 23:00 | 285 | 282
2019-11-05 23:30 | 270 | 266
2019-11-06 | 260 | 252
2019-11-06 00:30 | 238 | 229
2019-11-06 01:00 | 228 | 216
2019-11-06 01:30 | 225 | 211
2019-11-06 02:00 | 224 | 210
2019-11-06 02:30 | 223 | 209
2019-11-06 03:00 | 225 | 211
2019-11-06 03:30 | 225 | 212
2019-11-06 04:00 | 222 | 209
2019-11-06 04:30 | 223 | 211
2019-11-06 05:00 | 226 | 214
2019-11-06 05:30 | 242 | 232
2019-11-06 06:00 | 252 | 244
2019-11-06 06:30 | 271 | 266
2019-11-06 07:00 | 297 | 289
2019-11-06 07:30 | 304 | 295
2019-11-06 08:00 | 298 | 291
2019-11-06 08:30 | 292 | 285
2019-11-06 09:00 | 273 | 267
2019-11-06 09:30 | 257 | 250
2019-11-06 10:00 | 259 | 253
2019-11-06 10:30 | 248 | 242
2019-11-06 11:00 | 241 | 236
2019-11-06 11:30 | 239 | 234
2019-11-06 12:00 | 237 | 230
2019-11-06 12:30 | 251 | 245
2019-11-06 13:00 | 259 | 254
2019-11-06 13:30 | 262 | 256
2019-11-06 14:00 | 265 | 261
2019-11-06 14:30 | 271 | 267
2019-11-06 15:00 | 284 | 281
2019-11-06 15:30 | 296 | 292
2019-11-06 16:00 | 308 | 305
2019-11-06 16:30 | 326 | 324
2019-11-06 17:00 | 347 | 345
2019-11-06 17:30 | 348 | 344
2019-11-06 18:00 | 331 | 326
2019-11-06 18:30 | 338 | 331
2019-11-06 19:00 | 347 | 343
2019-11-06 19:30 | 342 | 336
2019-11-06 20:00 | 338 | 330
2019-11-06 20:30 | 321 | 318
2019-11-06 21:00 | 301 | 300
2019-11-06 21:30 | 287 | 285
2019-11-06 22:00 | 269 | 268
2019-11-06 22:30 | 259 | 257
2019-11-06 23:00 | 253 | 249
2019-11-06 23:30 | 241 | 236
2019-11-07 | 229 | 222
2019-11-07 00:30 | 214 | 202
2019-11-07 01:00 | 216 | 202
2019-11-07 01:30 | 211 | 197
2019-11-07 02:00 | 207 | 191
2019-11-07 02:30 | 202 | 187
2019-11-07 03:00 | 202 | 186
2019-11-07 03:30 | 203 | 188
2019-11-07 04:00 | 204 | 188
2019-11-07 04:30 | 209 | 194
2019-11-07 05:00 | 213 | 199
2019-11-07 05:30 | 215 | 202
2019-11-07 06:00 | 231 | 222
2019-11-07 06:30 | 261 | 256
2019-11-07 07:00 | 270 | 268
2019-11-07 07:30 | 288 | 282
2019-11-07 08:00 | 286 | 280
2019-11-07 08:30 | 287 | 282
2019-11-07 09:00 | 281 | 278
2019-11-07 09:30 | 276 | 273
2019-11-07 10:00 | 270 | 267
2019-11-07 10:30 | 271 | 267
2019-11-07 11:00 | 274 | 271
2019-11-07 11:30 | 280 | 277
2019-11-07 12:00 | 286 | 283
2019-11-07 12:30 | 299 | 296
2019-11-07 13:00 | 304 | 300
2019-11-07 13:30 | 318 | 312
2019-11-07 14:00 | 320 | 315
2019-11-07 14:30 | 338 | 333
2019-11-07 15:00 | 358 | 353
2019-11-07 15:30 | 369 | 363
2019-11-07 16:00 | 384 | 377
2019-11-07 16:30 | 400 | 392
2019-11-07 17:00 | 399 | 391
2019-11-07 17:30 | 388 | 378
2019-11-07 18:00 | 380 | 369
2019-11-07 18:30 | 371 | 359
2019-11-07 19:00 | 376 | 365
2019-11-07 19:30 | 371 | 361
2019-11-07 20:00 | 363 | 354
2019-11-07 20:30 | 343 | 334
2019-11-07 21:00 | 322 | 320
2019-11-07 21:30 | 313 | 310
2019-11-07 22:00 | 300 | 297
2019-11-07 22:30 | 290 | 286
2019-11-07 23:00 | 282 | 277
2019-11-07 23:30 | 267 | 263
2019-11-08 | 250 | 246
2019-11-08 00:30 | 228 | 222
2019-11-08 01:00 | 212 | 205
2019-11-08 01:30 | 201 | 194
2019-11-08 02:00 | 196 | 189
2019-11-08 02:30 | 197 | 188
2019-11-08 03:00 | 192 | 184
2019-11-08 03:30 | 192 | 184
2019-11-08 04:00 | 193 | 185
2019-11-08 04:30 | 203 | 195
2019-11-08 05:00 | 209 | 201
2019-11-08 05:30 | 223 | 216
2019-11-08 06:00 | 239 | 233
2019-11-08 06:30 | 263 | 259
2019-11-08 07:00 | 284 | 282
2019-11-08 07:30 | 294 | 293
2019-11-08 08:00 | 288 | 288
2019-11-08 08:30 | 357 | 357
2019-11-08 09:00 | 464 | 464
2019-11-08 09:30 | 473 | 472
2019-11-08 10:00 | 475 | 471
2019-11-08 10:30 | 485 | 480
2019-11-08 11:00 | 487 | 483
2019-11-08 11:30 | 496 | 493
2019-11-08 12:00 | 513 | 510
2019-11-08 12:30 | 527 | 525
2019-11-08 13:00 | 547 | 543
2019-11-08 13:30 | 573 | 569
2019-11-08 14:00 | 599 | 592
2019-11-08 14:30 | 611 | 604
2019-11-08 15:00 | 640 | 631
2019-11-08 15:30 | 660 | 650
2019-11-08 16:00 | 687 | 681
2019-11-08 16:30 | 708 | 702
2019-11-08 17:00 | 729 | 723
2019-11-08 17:30 | 717 | 711
2019-11-08 18:00 | 690 | 684
2019-11-08 18:30 | 661 | 654
2019-11-08 19:00 | 663 | 657
2019-11-08 19:30 | 655 | 647
2019-11-08 20:00 | 648 | 638
2019-11-08 20:30 | 639 | 629
2019-11-08 21:00 | 620 | 609
2019-11-08 21:30 | 588 | 584
2019-11-08 22:00 | 569 | 563
2019-11-08 22:30 | 547 | 539
2019-11-08 23:00 | 521 | 514
2019-11-08 23:30 | 489 | 479
2019-11-09 | 453 | 445
2019-11-09 00:30 | 417 | 406
2019-11-09 01:00 | 396 | 386
2019-11-09 01:30 | 386 | 376
2019-11-09 02:00 | 372 | 360
2019-11-09 02:30 | 361 | 349
2019-11-09 03:00 | 362 | 350
2019-11-09 03:30 | 363 | 350
2019-11-09 04:00 | 357 | 343
2019-11-09 04:30 | 357 | 344
2019-11-09 05:00 | 357 | 342
2019-11-09 05:30 | 353 | 336
2019-11-09 06:00 | 363 | 347
2019-11-09 06:30 | 371 | 356
2019-11-09 07:00 | 376 | 364
2019-11-09 07:30 | 382 | 373
2019-11-09 08:00 | 377 | 370
2019-11-09 08:30 | 373 | 368
2019-11-09 09:00 | 384 | 380
2019-11-09 09:30 | 387 | 384
2019-11-09 10:00 | 378 | 375
2019-11-09 10:30 | 374 | 368
2019-11-09 11:00 | 369 | 363
2019-11-09 11:30 | 363 | 357
2019-11-09 12:00 | 360 | 354
2019-11-09 12:30 | 362 | 356
2019-11-09 13:00 | 367 | 362
2019-11-09 13:30 | 381 | 376
2019-11-09 14:00 | 396 | 391
2019-11-09 14:30 | 413 | 409
2019-11-09 15:00 | 439 | 435
2019-11-09 15:30 | 472 | 469
2019-11-09 16:00 | 489 | 487
2019-11-09 16:30 | 500 | 495
2019-11-09 17:00 | 522 | 516
2019-11-09 17:30 | 517 | 511
2019-11-09 18:00 | 511 | 504
2019-11-09 18:30 | 520 | 514
2019-11-09 19:00 | 530 | 525
2019-11-09 19:30 | 521 | 515
2019-11-09 20:00 | 502 | 495
2019-11-09 20:30 | 501 | 494
2019-11-09 21:00 | 478 | 472
2019-11-09 21:30 | 457 | 453
2019-11-09 22:00 | 453 | 447
2019-11-09 22:30 | 440 | 433
2019-11-09 23:00 | 432 | 425
2019-11-09 23:30 | 419 | 410
2019-11-10 | 403 | 394
2019-11-10 00:30 | 378 | 366
2019-11-10 01:00 | 362 | 348
2019-11-10 01:30 | 353 | 338
2019-11-10 02:00 | 344 | 329
2019-11-10 02:30 | 337 | 321
2019-11-10 03:00 | 333 | 316
2019-11-10 03:30 | 329 | 312
2019-11-10 04:00 | 325 | 307
2019-11-10 04:30 | 328 | 311
2019-11-10 05:00 | 327 | 306
2019-11-10 05:30 | 331 | 309
2019-11-10 06:00 | 329 | 306
2019-11-10 06:30 | 327 | 306
2019-11-10 07:00 | 325 | 304
2019-11-10 07:30 | 321 | 302
2019-11-10 08:00 | 315 | 297
2019-11-10 08:30 | 311 | 294
2019-11-10 09:00 | 304 | 288
2019-11-10 09:30 | 299 | 285
2019-11-10 10:00 | 290 | 278
2019-11-10 10:30 | 290 | 278
2019-11-10 11:00 | 283 | 272
2019-11-10 11:30 | 286 | 275
2019-11-10 12:00 | 289 | 280
2019-11-10 12:30 | 291 | 282
2019-11-10 13:00 | 307 | 300
2019-11-10 13:30 | 325 | 320
2019-11-10 14:00 | 348 | 344
2019-11-10 14:30 | 375 | 370
2019-11-10 15:00 | 405 | 398
2019-11-10 15:30 | 434 | 429
2019-11-10 16:00 | 463 | 459
2019-11-10 16:30 | 491 | 487
2019-11-10 17:00 | 520 | 517
2019-11-10 17:30 | 533 | 529
2019-11-10 18:00 | 526 | 522
2019-11-10 18:30 | 540 | 535
2019-11-10 19:00 | 562 | 559
2019-11-10 19:30 | 556 | 553
2019-11-10 20:00 | 547 | 542
2019-11-10 20:30 | 518 | 514
2019-11-10 21:00 | 488 | 483
2019-11-10 21:30 | 473 | 468
2019-11-10 22:00 | 466 | 462
2019-11-10 22:30 | 457 | 452
2019-11-10 23:00 | 443 | 438
2019-11-10 23:30 | 420 | 412
2019-11-11 | 402 | 392
2019-11-11 00:30 | 368 | 355
2019-11-11 01:00 | 359 | 343
2019-11-11 01:30 | 351 | 335
2019-11-11 02:00 | 343 | 326
2019-11-11 02:30 | 339 | 322
2019-11-11 03:00 | 341 | 323
2019-11-11 03:30 | 339 | 321
2019-11-11 04:00 | 339 | 321
2019-11-11 04:30 | 339 | 321
2019-11-11 05:00 | 347 | 330
2019-11-11 05:30 | 383 | 368
2019-11-11 06:00 | 397 | 384
2019-11-11 06:30 | 436 | 430
2019-11-11 07:00 | 461 | 457
2019-11-11 07:30 | 481 | 477
2019-11-11 08:00 | 483 | 479
2019-11-11 08:30 | 481 | 478
2019-11-11 09:00 | 484 | 481
2019-11-11 09:30 | 488 | 485
2019-11-11 10:00 | 483 | 479
2019-11-11 10:30 | 475 | 471
2019-11-11 11:00 | 468 | 464
2019-11-11 11:30 | 464 | 460
2019-11-11 12:00 | 467 | 463
2019-11-11 12:30 | 467 | 463
2019-11-11 13:00 | 476 | 473
2019-11-11 13:30 | 491 | 488
2019-11-11 14:00 | 506 | 503
2019-11-11 14:30 | 525 | 522
2019-11-11 15:00 | 542 | 539
2019-11-11 15:30 | 555 | 551
2019-11-11 16:00 | 574 | 571
2019-11-11 16:30 | 592 | 589
2019-11-11 17:00 | 605 | 601
2019-11-11 17:30 | 591 | 586
2019-11-11 18:00 | 596 | 590
2019-11-11 18:30 | 584 | 578
2019-11-11 19:00 | 582 | 577
2019-11-11 19:30 | 560 | 555
2019-11-11 20:00 | 560 | 557
2019-11-11 20:30 | 539 | 537
2019-11-11 21:00 | 523 | 520
2019-11-11 21:30 | 508 | 504
2019-11-11 22:00 | 486 | 483
2019-11-11 22:30 | 479 | 476
2019-11-11 23:00 | 464 | 460
2019-11-11 23:30 | 444 | 438
2019-11-12 | 418 | 410
2019-11-12 00:30 | 380 | 370
2019-11-12 01:00 | 364 | 351
2019-11-12 01:30 | 350 | 334
2019-11-12 02:00 | 344 | 328
2019-11-12 02:30 | 341 | 324
2019-11-12 03:00 | 339 | 322
2019-11-12 03:30 | 341 | 324
2019-11-12 04:00 | 339 | 322
2019-11-12 04:30 | 349 | 333
2019-11-12 05:00 | 356 | 340
2019-11-12 05:30 | 391 | 377
2019-11-12 06:00 | 411 | 400
2019-11-12 06:30 | 450 | 443
2019-11-12 07:00 | 473 | 470
2019-11-12 07:30 | 488 | 483
2019-11-12 08:00 | 497 | 484
2019-11-12 08:30 | 486 | 475
2019-11-12 09:00 | 473 | 462
2019-11-12 09:30 | 475 | 464
2019-11-12 10:00 | 477 | 465
2019-11-12 10:30 | 476 | 464
2019-11-12 11:00 | 485 | 473
2019-11-12 11:30 | 490 | 479
2019-11-12 12:00 | 510 | 501
2019-11-12 12:30 | 523 | 514
2019-11-12 13:00 | 535 | 527
2019-11-12 13:30 | 540 | 533
2019-11-12 14:00 | 557 | 551
2019-11-12 14:30 | 578 | 573
2019-11-12 15:00 | 606 | 602
2019-11-12 15:30 | 624 | 620
2019-11-12 16:00 | 659 | 655
2019-11-12 16:30 | 682 | 678
2019-11-12 17:00 | 699 | 690
2019-11-12 17:30 | 694 | 685
2019-11-12 18:00 | 682 | 669
2019-11-12 18:30 | 656 | 640
2019-11-12 19:00 | 657 | 646
2019-11-12 19:30 | 649 | 637
2019-11-12 20:00 | 635 | 624
2019-11-12 20:30 | 612 | 602
2019-11-12 21:00 | 590 | 578
2019-11-12 21:30 | 566 | 550
2019-11-12 22:00 | 535 | 525
2019-11-12 22:30 | 518 | 508
2019-11-12 23:00 | 497 | 489
2019-11-12 23:30 | 464 | 460
2019-11-13 | 432 | 427
2019-11-13 00:30 | 393 | 386
2019-11-13 01:00 | 372 | 363
2019-11-13 01:30 | 358 | 348
2019-11-13 02:00 | 351 | 341
2019-11-13 02:30 | 345 | 334
2019-11-13 03:00 | 343 | 331
2019-11-13 03:30 | 344 | 334
2019-11-13 04:00 | 346 | 336
2019-11-13 04:30 | 357 | 347
2019-11-13 05:00 | 369 | 359
2019-11-13 05:30 | 389 | 380
2019-11-13 06:00 | 416 | 409
2019-11-13 06:30 | 457 | 453
2019-11-13 07:00 | 487 | 486
2019-11-13 07:30 | 521 | 518
2019-11-13 08:00 | 530 | 528
2019-11-13 08:30 | 535 | 532
2019-11-13 09:00 | 523 | 521
2019-11-13 09:30 | 517 | 515
2019-11-13 10:00 | 531 | 530
2019-11-13 10:30 | 525 | 524
2019-11-13 11:00 | 519 | 519
2019-11-13 11:30 | 517 | 517
2019-11-13 12:00 | 513 | 513
2019-11-13 12:30 | 512 | 512
2019-11-13 13:00 | 524 | 524
2019-11-13 13:30 | 538 | 538
2019-11-13 14:00 | 550 | 550
2019-11-13 14:30 | 567 | 567
2019-11-13 15:00 | 575 | 574
2019-11-13 15:30 | 600 | 600
2019-11-13 16:00 | 620 | 619
2019-11-13 16:30 | 637 | 635
2019-11-13 17:00 | 650 | 649
2019-11-13 17:30 | 650 | 649
2019-11-13 18:00 | 648 | 646
2019-11-13 18:30 | 632 | 630
2019-11-13 19:00 | 637 | 635
2019-11-13 19:30 | 634 | 631
2019-11-13 20:00 | 636 | 632
2019-11-13 20:30 | 615 | 612
2019-11-13 21:00 | 591 | 589
2019-11-13 21:30 | 545 | 543
2019-11-13 22:00 | 529 | 526
2019-11-13 22:30 | 502 | 498
2019-11-13 23:00 | 484 | 479
2019-11-13 23:30 | 463 | 458
2019-11-14 | 443 | 437
2019-11-14 00:30 | 408 | 400
2019-11-14 01:00 | 390 | 382
2019-11-14 01:30 | 374 | 364
2019-11-14 02:00 | 362 | 352
2019-11-14 02:30 | 361 | 351
2019-11-14 03:00 | 358 | 348
2019-11-14 03:30 | 363 | 353
2019-11-14 04:00 | 366 | 355
2019-11-14 04:30 | 374 | 363
2019-11-14 05:00 | 393 | 382
2019-11-14 05:30 | 420 | 411
2019-11-14 06:00 | 432 | 424
2019-11-14 06:30 | 473 | 470
2019-11-14 07:00 | 495 | 493
2019-11-14 07:30 | 507 | 501
2019-11-14 08:00 | 501 | 494
2019-11-14 08:30 | 509 | 503
2019-11-14 09:00 | 497 | 490
2019-11-14 09:30 | 482 | 476
2019-11-14 10:00 | 473 | 467
2019-11-14 10:30 | 465 | 460
2019-11-14 11:00 | 464 | 459
2019-11-14 11:30 | 466 | 460
2019-11-14 12:00 | 469 | 462
2019-11-14 12:30 | 484 | 477
2019-11-14 13:00 | 494 | 488
2019-11-14 13:30 | 500 | 494
2019-11-14 14:00 | 506 | 500
2019-11-14 14:30 | 527 | 522
2019-11-14 15:00 | 556 | 548
2019-11-14 15:30 | 579 | 570
2019-11-14 16:00 | 608 | 601
2019-11-14 16:30 | 626 | 620
2019-11-14 17:00 | 641 | 636
2019-11-14 17:30 | 640 | 634
2019-11-14 18:00 | 633 | 626
2019-11-14 18:30 | 630 | 621
2019-11-14 19:00 | 636 | 629
2019-11-14 19:30 | 635 | 626
2019-11-14 20:00 | 638 | 627
2019-11-14 20:30 | 614 | 609
2019-11-14 21:00 | 570 | 568
2019-11-14 21:30 | 555 | 552
2019-11-14 22:00 | 534 | 529
2019-11-14 22:30 | 515 | 511
2019-11-14 23:00 | 505 | 502
2019-11-14 23:30 | 483 | 477
2019-11-15 | 450 | 445
2019-11-15 00:30 | 415 | 408
2019-11-15 01:00 | 388 | 381
2019-11-15 01:30 | 373 | 365
2019-11-15 02:00 | 360 | 351
2019-11-15 02:30 | 350 | 341
2019-11-15 03:00 | 345 | 335
2019-11-15 03:30 | 342 | 333
2019-11-15 04:00 | 345 | 336
2019-11-15 04:30 | 366 | 357
2019-11-15 05:00 | 389 | 379
2019-11-15 05:30 | 410 | 402
2019-11-15 06:00 | 427 | 421
2019-11-15 06:30 | 469 | 466
2019-11-15 07:00 | 501 | 498
2019-11-15 07:30 | 518 | 514
2019-11-15 08:00 | 534 | 525
2019-11-15 08:30 | 531 | 525
2019-11-15 09:00 | 528 | 523
2019-11-15 09:30 | 528 | 523
2019-11-15 10:00 | 536 | 525
2019-11-15 10:30 | 541 | 532
2019-11-15 11:00 | 547 | 539
2019-11-15 11:30 | 542 | 534
2019-11-15 12:00 | 548 | 541
2019-11-15 12:30 | 548 | 542
2019-11-15 13:00 | 566 | 561
2019-11-15 13:30 | 589 | 583
2019-11-15 14:00 | 613 | 608
2019-11-15 14:30 | 633 | 627
2019-11-15 15:00 | 646 | 639
2019-11-15 15:30 | 659 | 652
2019-11-15 16:00 | 685 | 679
2019-11-15 16:30 | 704 | 697
2019-11-15 17:00 | 716 | 709
2019-11-15 17:30 | 699 | 690
2019-11-15 18:00 | 671 | 661
2019-11-15 18:30 | 654 | 644
2019-11-15 19:00 | 657 | 649
2019-11-15 19:30 | 652 | 643
2019-11-15 20:00 | 640 | 634
2019-11-15 20:30 | 622 | 615
2019-11-15 21:00 | 594 | 589
2019-11-15 21:30 | 569 | 563
2019-11-15 22:00 | 550 | 544
2019-11-15 22:30 | 535 | 528
2019-11-15 23:00 | 515 | 509
2019-11-15 23:30 | 483 | 481
2019-11-16 | 454 | 451
2019-11-16 00:30 | 422 | 418
2019-11-16 01:00 | 392 | 387
2019-11-16 01:30 | 379 | 374
2019-11-16 02:00 | 368 | 362
2019-11-16 02:30 | 363 | 356
2019-11-16 03:00 | 356 | 349
2019-11-16 03:30 | 344 | 337
2019-11-16 04:00 | 341 | 334
2019-11-16 04:30 | 348 | 341
2019-11-16 05:00 | 353 | 344
2019-11-16 05:30 | 359 | 348
2019-11-16 06:00 | 362 | 351
2019-11-16 06:30 | 382 | 373
2019-11-16 07:00 | 401 | 394
2019-11-16 07:30 | 426 | 421
2019-11-16 08:00 | 434 | 430
2019-11-16 08:30 | 449 | 446
2019-11-16 09:00 | 464 | 463
2019-11-16 09:30 | 462 | 461
2019-11-16 10:00 | 470 | 470
2019-11-16 10:30 | 473 | 473
2019-11-16 11:00 | 475 | 473
2019-11-16 11:30 | 472 | 471
2019-11-16 12:00 | 496 | 496
2019-11-16 12:30 | 513 | 512
2019-11-16 13:00 | 532 | 529
2019-11-16 13:30 | 541 | 539
2019-11-16 14:00 | 555 | 552
2019-11-16 14:30 | 581 | 578
2019-11-16 15:00 | 609 | 607
2019-11-16 15:30 | 637 | 631
2019-11-16 16:00 | 658 | 650
2019-11-16 16:30 | 664 | 656
2019-11-16 17:00 | 673 | 666
2019-11-16 17:30 | 668 | 660
2019-11-16 18:00 | 652 | 642
2019-11-16 18:30 | 636 | 628
2019-11-16 19:00 | 634 | 628
2019-11-16 19:30 | 622 | 614
2019-11-16 20:00 | 599 | 595
2019-11-16 20:30 | 575 | 573
2019-11-16 21:00 | 549 | 546
2019-11-16 21:30 | 536 | 531
2019-11-16 22:00 | 514 | 509
2019-11-16 22:30 | 497 | 492
2019-11-16 23:00 | 478 | 474
2019-11-16 23:30 | 449 | 446
2019-11-17 | 427 | 422
2019-11-17 00:30 | 397 | 390
2019-11-17 01:00 | 374 | 366
2019-11-17 01:30 | 362 | 354
2019-11-17 02:00 | 355 | 347
2019-11-17 02:30 | 343 | 334
2019-11-17 03:00 | 336 | 326
2019-11-17 03:30 | 337 | 327
2019-11-17 04:00 | 336 | 326
2019-11-17 04:30 | 334 | 323
2019-11-17 05:00 | 330 | 319
2019-11-17 05:30 | 329 | 317
2019-11-17 06:00 | 328 | 316
2019-11-17 06:30 | 353 | 342
2019-11-17 07:00 | 372 | 362
2019-11-17 07:30 | 381 | 372
2019-11-17 08:00 | 379 | 371
2019-11-17 08:30 | 389 | 383
2019-11-17 09:00 | 384 | 381
2019-11-17 09:30 | 396 | 393
2019-11-17 10:00 | 402 | 401
2019-11-17 10:30 | 409 | 409
2019-11-17 11:00 | 420 | 420
2019-11-17 11:30 | 433 | 433
2019-11-17 12:00 | 450 | 450
2019-11-17 12:30 | 523 | 521
2019-11-17 13:00 | 498 | 496
2019-11-17 13:30 | 532 | 532
2019-11-17 14:00 | 491 | 491
2019-11-17 14:30 | 517 | 517
2019-11-17 15:00 | 514 | 514
2019-11-17 15:30 | 529 | 529
2019-11-17 16:00 | 555 | 555
2019-11-17 16:30 | 581 | 581
2019-11-17 17:00 | 608 | 607
2019-11-17 17:30 | 614 | 609
2019-11-17 18:00 | 612 | 607
2019-11-17 18:30 | 609 | 604
2019-11-17 19:00 | 616 | 612
2019-11-17 19:30 | 609 | 605
2019-11-17 20:00 | 591 | 586
2019-11-17 20:30 | 573 | 572
2019-11-17 21:00 | 550 | 549
2019-11-17 21:30 | 526 | 524
2019-11-17 22:00 | 507 | 505
2019-11-17 22:30 | 483 | 481
2019-11-17 23:00 | 469 | 465
2019-11-17 23:30 | 442 | 438
2019-11-18 | 412 | 406
2019-11-18 00:30 | 380 | 373
2019-11-18 01:00 | 366 | 358
2019-11-18 01:30 | 357 | 347
2019-11-18 02:00 | 347 | 336
2019-11-18 02:30 | 338 | 327
2019-11-18 03:00 | 338 | 326
2019-11-18 03:30 | 342 | 330
2019-11-18 04:00 | 343 | 331
2019-11-18 04:30 | 351 | 340
2019-11-18 05:00 | 355 | 344
2019-11-18 05:30 | 375 | 365
2019-11-18 06:00 | 397 | 389
2019-11-18 06:30 | 441 | 437
2019-11-18 07:00 | 476 | 470
2019-11-18 07:30 | 502 | 497
2019-11-18 08:00 | 514 | 507
2019-11-18 08:30 | 514 | 506
2019-11-18 09:00 | 506 | 496
2019-11-18 09:30 | 499 | 488
2019-11-18 10:00 | 474 | 466
2019-11-18 10:30 | 465 | 457
2019-11-18 11:00 | 450 | 442
2019-11-18 11:30 | 443 | 435
2019-11-18 12:00 | 445 | 438
2019-11-18 12:30 | 445 | 438
2019-11-18 13:00 | 451 | 444
2019-11-18 13:30 | 468 | 461
2019-11-18 14:00 | 481 | 475
2019-11-18 14:30 | 504 | 497
2019-11-18 15:00 | 536 | 528
2019-11-18 15:30 | 561 | 553
2019-11-18 16:00 | 593 | 584
2019-11-18 16:30 | 609 | 601
2019-11-18 17:00 | 624 | 616
2019-11-18 17:30 | 624 | 615
2019-11-18 18:00 | 618 | 606
2019-11-18 18:30 | 604 | 593
2019-11-18 19:00 | 606 | 597
2019-11-18 19:30 | 597 | 587
2019-11-18 20:00 | 581 | 570
2019-11-18 20:30 | 561 | 551
2019-11-18 21:00 | 538 | 528
2019-11-18 21:30 | 523 | 511
2019-11-18 22:00 | 507 | 496
2019-11-18 22:30 | 496 | 485
2019-11-18 23:00 | 478 | 468
2019-11-18 23:30 | 463 | 459
2019-11-19 | 451 | 445
2019-11-19 00:30 | 420 | 413
2019-11-19 01:00 | 398 | 391
2019-11-19 01:30 | 381 | 373
2019-11-19 02:00 | 367 | 358
2019-11-19 02:30 | 352 | 343
2019-11-19 03:00 | 349 | 340
2019-11-19 03:30 | 344 | 335
2019-11-19 04:00 | 352 | 343
2019-11-19 04:30 | 371 | 362
2019-11-19 05:00 | 377 | 368
2019-11-19 05:30 | 391 | 383
2019-11-19 06:00 | 408 | 402
2019-11-19 06:30 | 452 | 449
2019-11-19 07:00 | 494 | 492
2019-11-19 07:30 | 495 | 494
2019-11-19 08:00 | 500 | 499
2019-11-19 08:30 | 510 | 508
2019-11-19 09:00 | 506 | 502
2019-11-19 09:30 | 500 | 497
2019-11-19 10:00 | 495 | 492
2019-11-19 10:30 | 482 | 480
2019-11-19 11:00 | 481 | 479
2019-11-19 11:30 | 484 | 482
2019-11-19 12:00 | 490 | 489
2019-11-19 12:30 | 507 | 505
2019-11-19 13:00 | 521 | 515
2019-11-19 13:30 | 538 | 533
2019-11-19 14:00 | 565 | 560
2019-11-19 14:30 | 582 | 579
2019-11-19 15:00 | 614 | 610
2019-11-19 15:30 | 638 | 634
2019-11-19 16:00 | 650 | 647
2019-11-19 16:30 | 660 | 658
2019-11-19 17:00 | 672 | 669
2019-11-19 17:30 | 664 | 658
2019-11-19 18:00 | 665 | 657
2019-11-19 18:30 | 637 | 634
2019-11-19 19:00 | 640 | 638
2019-11-19 19:30 | 628 | 625
2019-11-19 20:00 | 605 | 603
2019-11-19 20:30 | 579 | 577
2019-11-19 21:00 | 551 | 550
2019-11-19 21:30 | 533 | 531
2019-11-19 22:00 | 510 | 508
2019-11-19 22:30 | 506 | 504
2019-11-19 23:00 | 482 | 479
2019-11-19 23:30 | 457 | 455
2019-11-20 | 432 | 428
2019-11-20 00:30 | 398 | 393
2019-11-20 01:00 | 384 | 378
2019-11-20 01:30 | 369 | 363
2019-11-20 02:00 | 361 | 355
2019-11-20 02:30 | 357 | 350
2019-11-20 03:00 | 355 | 348
2019-11-20 03:30 | 354 | 346
2019-11-20 04:00 | 352 | 345
2019-11-20 04:30 | 359 | 352
2019-11-20 05:00 | 364 | 357
2019-11-20 05:30 | 385 | 379
2019-11-20 06:00 | 403 | 398
2019-11-20 06:30 | 451 | 448
2019-11-20 07:00 | 491 | 486
2019-11-20 07:30 | 507 | 502
2019-11-20 08:00 | 518 | 513
2019-11-20 08:30 | 522 | 518
2019-11-20 09:00 | 540 | 531
2019-11-20 09:30 | 539 | 530
2019-11-20 10:00 | 535 | 528
2019-11-20 10:30 | 540 | 535
2019-11-20 11:00 | 546 | 542
2019-11-20 11:30 | 559 | 553
2019-11-20 12:00 | 574 | 568
2019-11-20 12:30 | 589 | 584
2019-11-20 13:00 | 608 | 604
2019-11-20 13:30 | 630 | 625
2019-11-20 14:00 | 648 | 643
2019-11-20 14:30 | 669 | 663
2019-11-20 15:00 | 699 | 693
2019-11-20 15:30 | 720 | 709
2019-11-20 16:00 | 740 | 728
2019-11-20 16:30 | 762 | 750
2019-11-20 17:00 | 766 | 754
2019-11-20 17:30 | 739 | 727
2019-11-20 18:00 | 708 | 696
2019-11-20 18:30 | 683 | 670
2019-11-20 19:00 | 685 | 675
2019-11-20 19:30 | 672 | 660
2019-11-20 20:00 | 648 | 634
2019-11-20 20:30 | 623 | 612
2019-11-20 21:00 | 595 | 585
2019-11-20 21:30 | 575 | 568
2019-11-20 22:00 | 545 | 541
2019-11-20 22:30 | 520 | 514
2019-11-20 23:00 | 494 | 486
2019-11-20 23:30 | 466 | 460
2019-11-21 | 439 | 435
2019-11-21 00:30 | 405 | 400
2019-11-21 01:00 | 383 | 377
2019-11-21 01:30 | 367 | 360
2019-11-21 02:00 | 356 | 348
2019-11-21 02:30 | 350 | 342
2019-11-21 03:00 | 350 | 342
2019-11-21 03:30 | 353 | 344
2019-11-21 04:00 | 356 | 347
2019-11-21 04:30 | 371 | 363
2019-11-21 05:00 | 389 | 380
2019-11-21 05:30 | 403 | 396
2019-11-21 06:00 | 414 | 409
2019-11-21 06:30 | 464 | 462
2019-11-21 07:00 | 508 | 503
2019-11-21 07:30 | 520 | 515
2019-11-21 08:00 | 524 | 519
2019-11-21 08:30 | 527 | 520
2019-11-21 09:00 | 537 | 531
2019-11-21 09:30 | 542 | 533
2019-11-21 10:00 | 539 | 530
2019-11-21 10:30 | 533 | 525
2019-11-21 11:00 | 524 | 515
2019-11-21 11:30 | 536 | 528
2019-11-21 12:00 | 555 | 548
2019-11-21 12:30 | 570 | 564
2019-11-21 13:00 | 570 | 564
2019-11-21 13:30 | 572 | 567
2019-11-21 14:00 | 585 | 580
2019-11-21 14:30 | 599 | 595
2019-11-21 15:00 | 621 | 616
2019-11-21 15:30 | 628 | 623
2019-11-21 16:00 | 639 | 633
2019-11-21 16:30 | 647 | 642
2019-11-21 17:00 | 656 | 650
2019-11-21 17:30 | 646 | 639
2019-11-21 18:00 | 631 | 623
2019-11-21 18:30 | 614 | 604
2019-11-21 19:00 | 617 | 608
2019-11-21 19:30 | 618 | 608
2019-11-21 20:00 | 605 | 596
2019-11-21 20:30 | 568 | 566
2019-11-21 21:00 | 534 | 533
2019-11-21 21:30 | 509 | 507
2019-11-21 22:00 | 486 | 484
2019-11-21 22:30 | 477 | 474
2019-11-21 23:00 | 449 | 446
2019-11-21 23:30 | 427 | 424
2019-11-22 | 405 | 400
2019-11-22 00:30 | 375 | 369
2019-11-22 01:00 | 360 | 352
2019-11-22 01:30 | 347 | 338
2019-11-22 02:00 | 344 | 335
2019-11-22 02:30 | 343 | 333
2019-11-22 03:00 | 342 | 331
2019-11-22 03:30 | 342 | 331
2019-11-22 04:00 | 342 | 331
2019-11-22 04:30 | 350 | 339
2019-11-22 05:00 | 355 | 344
2019-11-22 05:30 | 372 | 362
2019-11-22 06:00 | 388 | 381
2019-11-22 06:30 | 429 | 425
2019-11-22 07:00 | 464 | 462
2019-11-22 07:30 | 489 | 488
2019-11-22 08:00 | 509 | 507
2019-11-22 08:30 | 515 | 513
2019-11-22 09:00 | 515 | 513
2019-11-22 09:30 | 503 | 502
2019-11-22 10:00 | 494 | 493
2019-11-22 10:30 | 496 | 495
2019-11-22 11:00 | 519 | 518
2019-11-22 11:30 | 521 | 519
2019-11-22 12:00 | 521 | 519
2019-11-22 12:30 | 532 | 530
2019-11-22 13:00 | 543 | 541
2019-11-22 13:30 | 555 | 553
2019-11-22 14:00 | 573 | 571
2019-11-22 14:30 | 576 | 574
2019-11-22 15:00 | 570 | 568
2019-11-22 15:30 | 582 | 581
2019-11-22 16:00 | 606 | 605
2019-11-22 16:30 | 622 | 620
2019-11-22 17:00 | 635 | 633
2019-11-22 17:30 | 624 | 621
2019-11-22 18:00 | 606 | 603
2019-11-22 18:30 | 578 | 575
2019-11-22 19:00 | 583 | 582
2019-11-22 19:30 | 571 | 570
2019-11-22 20:00 | 571 | 570
2019-11-22 20:30 | 553 | 552
2019-11-22 21:00 | 529 | 529
2019-11-22 21:30 | 513 | 512
2019-11-22 22:00 | 491 | 490
2019-11-22 22:30 | 484 | 484
2019-11-22 23:00 | 461 | 461
2019-11-22 23:30 | 436 | 436
2019-11-23 | 409 | 408
2019-11-23 00:30 | 375 | 372
2019-11-23 01:00 | 349 | 345
2019-11-23 01:30 | 339 | 335
2019-11-23 02:00 | 333 | 328
2019-11-23 02:30 | 332 | 328
2019-11-23 03:00 | 331 | 325
2019-11-23 03:30 | 329 | 323
2019-11-23 04:00 | 331 | 325
2019-11-23 04:30 | 337 | 330
2019-11-23 05:00 | 336 | 329
2019-11-23 05:30 | 336 | 328
2019-11-23 06:00 | 342 | 335
2019-11-23 06:30 | 369 | 363
2019-11-23 07:00 | 393 | 387
2019-11-23 07:30 | 421 | 414
2019-11-23 08:00 | 441 | 431
2019-11-23 08:30 | 454 | 445
2019-11-23 09:00 | 445 | 438
2019-11-23 09:30 | 425 | 418
2019-11-23 10:00 | 411 | 406
2019-11-23 10:30 | 407 | 403
2019-11-23 11:00 | 404 | 401
2019-11-23 11:30 | 393 | 390
2019-11-23 12:00 | 397 | 394
2019-11-23 12:30 | 402 | 399
2019-11-23 13:00 | 405 | 403
2019-11-23 13:30 | 414 | 412
2019-11-23 14:00 | 430 | 428
2019-11-23 14:30 | 442 | 441
2019-11-23 15:00 | 460 | 459
2019-11-23 15:30 | 481 | 480
2019-11-23 16:00 | 516 | 514
2019-11-23 16:30 | 529 | 528
2019-11-23 17:00 | 544 | 543
2019-11-23 17:30 | 544 | 543
2019-11-23 18:00 | 530 | 529
2019-11-23 18:30 | 525 | 523
2019-11-23 19:00 | 531 | 530
2019-11-23 19:30 | 520 | 519
2019-11-23 20:00 | 506 | 504
2019-11-23 20:30 | 492 | 491
2019-11-23 21:00 | 475 | 474
2019-11-23 21:30 | 457 | 457
2019-11-23 22:00 | 454 | 453
2019-11-23 22:30 | 448 | 447
2019-11-23 23:00 | 432 | 430
2019-11-23 23:30 | 414 | 412
2019-11-24 | 400 | 395
2019-11-24 00:30 | 368 | 362
2019-11-24 01:00 | 353 | 346
2019-11-24 01:30 | 345 | 337
2019-11-24 02:00 | 333 | 324
2019-11-24 02:30 | 321 | 311
2019-11-24 03:00 | 318 | 308
2019-11-24 03:30 | 318 | 307
2019-11-24 04:00 | 318 | 308
2019-11-24 04:30 | 322 | 311
2019-11-24 05:00 | 319 | 305
2019-11-24 05:30 | 316 | 302
2019-11-24 06:00 | 318 | 305
2019-11-24 06:30 | 345 | 332
2019-11-24 07:00 | 361 | 349
2019-11-24 07:30 | 367 | 358
2019-11-24 08:00 | 374 | 366
2019-11-24 08:30 | 398 | 392
2019-11-24 09:00 | 395 | 391
2019-11-24 09:30 | 389 | 386
2019-11-24 10:00 | 388 | 386
2019-11-24 10:30 | 379 | 377
2019-11-24 11:00 | 370 | 368
2019-11-24 11:30 | 370 | 368
2019-11-24 12:00 | 370 | 368
2019-11-24 12:30 | 378 | 377
2019-11-24 13:00 | 397 | 396
2019-11-24 13:30 | 415 | 414
2019-11-24 14:00 | 431 | 430
2019-11-24 14:30 | 461 | 460
2019-11-24 15:00 | 471 | 471
2019-11-24 15:30 | 489 | 489
2019-11-24 16:00 | 498 | 498
2019-11-24 16:30 | 504 | 503
2019-11-24 17:00 | 507 | 506
2019-11-24 17:30 | 517 | 516
2019-11-24 18:00 | 513 | 511
2019-11-24 18:30 | 512 | 510
2019-11-24 19:00 | 530 | 528
2019-11-24 19:30 | 529 | 526
2019-11-24 20:00 | 524 | 519
2019-11-24 20:30 | 503 | 499
2019-11-24 21:00 | 478 | 475
2019-11-24 21:30 | 467 | 464
2019-11-24 22:00 | 451 | 448
2019-11-24 22:30 | 432 | 430
2019-11-24 23:00 | 421 | 418
2019-11-24 23:30 | 405 | 402
2019-11-25 | 384 | 379
2019-11-25 00:30 | 356 | 349
2019-11-25 01:00 | 338 | 329
2019-11-25 01:30 | 331 | 322
2019-11-25 02:00 | 325 | 316
2019-11-25 02:30 | 323 | 311
2019-11-25 03:00 | 318 | 304
2019-11-25 03:30 | 314 | 300
2019-11-25 04:00 | 319 | 305
2019-11-25 04:30 | 328 | 315
2019-11-25 05:00 | 339 | 326
2019-11-25 05:30 | 356 | 345
2019-11-25 06:00 | 374 | 366
2019-11-25 06:30 | 423 | 420
2019-11-25 07:00 | 467 | 466
2019-11-25 07:30 | 496 | 495
2019-11-25 08:00 | 508 | 507
2019-11-25 08:30 | 510 | 509
2019-11-25 09:00 | 510 | 508
2019-11-25 09:30 | 514 | 513
2019-11-25 10:00 | 496 | 494
2019-11-25 10:30 | 499 | 498
2019-11-25 11:00 | 494 | 493
2019-11-25 11:30 | 499 | 497
2019-11-25 12:00 | 503 | 501
2019-11-25 12:30 | 516 | 514
2019-11-25 13:00 | 528 | 526
2019-11-25 13:30 | 542 | 540
2019-11-25 14:00 | 562 | 560
2019-11-25 14:30 | 579 | 577
2019-11-25 15:00 | 594 | 592
2019-11-25 15:30 | 603 | 601
2019-11-25 16:00 | 624 | 621
2019-11-25 16:30 | 644 | 638
2019-11-25 17:00 | 648 | 643
2019-11-25 17:30 | 647 | 640
2019-11-25 18:00 | 628 | 620
2019-11-25 18:30 | 608 | 599
2019-11-25 19:00 | 623 | 616
2019-11-25 19:30 | 609 | 601
2019-11-25 20:00 | 594 | 585
2019-11-25 20:30 | 580 | 571
2019-11-25 21:00 | 554 | 547
2019-11-25 21:30 | 532 | 522
2019-11-25 22:00 | 500 | 492
2019-11-25 22:30 | 483 | 480
2019-11-25 23:00 | 460 | 456
2019-11-25 23:30 | 435 | 432
2019-11-26 | 412 | 407
2019-11-26 00:30 | 373 | 367
2019-11-26 01:00 | 356 | 351
2019-11-26 01:30 | 342 | 337
2019-11-26 02:00 | 331 | 325
2019-11-26 02:30 | 326 | 320
2019-11-26 03:00 | 322 | 315
2019-11-26 03:30 | 319 | 313
2019-11-26 04:00 | 319 | 312
2019-11-26 04:30 | 325 | 319
2019-11-26 05:00 | 332 | 325
2019-11-26 05:30 | 352 | 347
2019-11-26 06:00 | 391 | 387
2019-11-26 06:30 | 449 | 447
2019-11-26 07:00 | 498 | 496
2019-11-26 07:30 | 524 | 523
2019-11-26 08:00 | 518 | 516
2019-11-26 08:30 | 514 | 512
2019-11-26 09:00 | 519 | 516
2019-11-26 09:30 | 515 | 513
2019-11-26 10:00 | 510 | 508
2019-11-26 10:30 | 509 | 507
2019-11-26 11:00 | 512 | 510
2019-11-26 11:30 | 522 | 520
2019-11-26 12:00 | 520 | 519
2019-11-26 12:30 | 506 | 505
2019-11-26 13:00 | 514 | 512
2019-11-26 13:30 | 528 | 526
2019-11-26 14:00 | 545 | 544
2019-11-26 14:30 | 570 | 567
2019-11-26 15:00 | 603 | 598
2019-11-26 15:30 | 624 | 620
2019-11-26 16:00 | 654 | 651
2019-11-26 16:30 | 669 | 665
2019-11-26 17:00 | 684 | 679
2019-11-26 17:30 | 686 | 678
2019-11-26 18:00 | 677 | 668
2019-11-26 18:30 | 656 | 646
2019-11-26 19:00 | 657 | 650
2019-11-26 19:30 | 645 | 637
2019-11-26 20:00 | 634 | 624
2019-11-26 20:30 | 606 | 598
2019-11-26 21:00 | 575 | 568
2019-11-26 21:30 | 544 | 542
2019-11-26 22:00 | 525 | 521
2019-11-26 22:30 | 514 | 509
2019-11-26 23:00 | 498 | 492
2019-11-26 23:30 | 468 | 466
2019-11-27 | 441 | 438
2019-11-27 00:30 | 390 | 386
2019-11-27 01:00 | 371 | 366
2019-11-27 01:30 | 362 | 357
2019-11-27 02:00 | 358 | 351
2019-11-27 02:30 | 354 | 348
2019-11-27 03:00 | 355 | 349
2019-11-27 03:30 | 357 | 350
2019-11-27 04:00 | 360 | 353
2019-11-27 04:30 | 367 | 360
2019-11-27 05:00 | 370 | 363
2019-11-27 05:30 | 392 | 386
2019-11-27 06:00 | 421 | 416
2019-11-27 06:30 | 468 | 466
2019-11-27 07:00 | 504 | 503
2019-11-27 07:30 | 524 | 524
2019-11-27 08:00 | 530 | 529
2019-11-27 08:30 | 525 | 525
2019-11-27 09:00 | 513 | 513
2019-11-27 09:30 | 540 | 534
2019-11-27 10:00 | 532 | 528
2019-11-27 10:30 | 534 | 531
2019-11-27 11:00 | 538 | 534
2019-11-27 11:30 | 522 | 519
2019-11-27 12:00 | 531 | 527
2019-11-27 12:30 | 549 | 544
2019-11-27 13:00 | 554 | 549
2019-11-27 13:30 | 550 | 545
2019-11-27 14:00 | 556 | 551
2019-11-27 14:30 | 578 | 572
2019-11-27 15:00 | 599 | 593
2019-11-27 15:30 | 614 | 609
2019-11-27 16:00 | 643 | 637
2019-11-27 16:30 | 654 | 647
2019-11-27 17:00 | 648 | 641
2019-11-27 17:30 | 640 | 630
2019-11-27 18:00 | 619 | 609
2019-11-27 18:30 | 601 | 588
2019-11-27 19:00 | 608 | 597
2019-11-27 19:30 | 603 | 593
2019-11-27 20:00 | 575 | 572
2019-11-27 20:30 | 557 | 555
2019-11-27 21:00 | 528 | 526
2019-11-27 21:30 | 507 | 504
2019-11-27 22:00 | 491 | 486
2019-11-27 22:30 | 472 | 465
2019-11-27 23:00 | 462 | 454
2019-11-27 23:30 | 445 | 434
2019-11-28 | 410 | 399
2019-11-28 00:30 | 375 | 366
2019-11-28 01:00 | 363 | 355
2019-11-28 01:30 | 352 | 343
2019-11-28 02:00 | 339 | 329
2019-11-28 02:30 | 336 | 326
2019-11-28 03:00 | 335 | 326
2019-11-28 03:30 | 340 | 331
2019-11-28 04:00 | 348 | 338
2019-11-28 04:30 | 359 | 350
2019-11-28 05:00 | 363 | 354
2019-11-28 05:30 | 385 | 377
2019-11-28 06:00 | 414 | 408
2019-11-28 06:30 | 452 | 450
2019-11-28 07:00 | 490 | 487
2019-11-28 07:30 | 524 | 518
2019-11-28 08:00 | 549 | 541
2019-11-28 08:30 | 557 | 551
2019-11-28 09:00 | 542 | 536
2019-11-28 09:30 | 540 | 535
2019-11-28 10:00 | 532 | 527
2019-11-28 10:30 | 523 | 518
2019-11-28 11:00 | 518 | 513
2019-11-28 11:30 | 513 | 508
2019-11-28 12:00 | 530 | 525
2019-11-28 12:30 | 555 | 552
2019-11-28 13:00 | 562 | 559
2019-11-28 13:30 | 560 | 557
2019-11-28 14:00 | 561 | 558
2019-11-28 14:30 | 552 | 549
2019-11-28 15:00 | 564 | 561
2019-11-28 15:30 | 587 | 584
2019-11-28 16:00 | 607 | 604
2019-11-28 16:30 | 620 | 615
2019-11-28 17:00 | 651 | 644
2019-11-28 17:30 | 654 | 647
2019-11-28 18:00 | 644 | 635
2019-11-28 18:30 | 626 | 618
2019-11-28 19:00 | 629 | 622
2019-11-28 19:30 | 625 | 618
2019-11-28 20:00 | 619 | 613
2019-11-28 20:30 | 593 | 587
2019-11-28 21:00 | 566 | 563
2019-11-28 21:30 | 546 | 543
2019-11-28 22:00 | 519 | 517
2019-11-28 22:30 | 505 | 502
2019-11-28 23:00 | 489 | 484
2019-11-28 23:30 | 461 | 455
2019-11-29 | 428 | 421
2019-11-29 00:30 | 390 | 386
2019-11-29 01:00 | 379 | 373
2019-11-29 01:30 | 366 | 359
2019-11-29 02:00 | 352 | 345
2019-11-29 02:30 | 349 | 342
2019-11-29 03:00 | 346 | 338
2019-11-29 03:30 | 351 | 343
2019-11-29 04:00 | 358 | 350
2019-11-29 04:30 | 362 | 355
2019-11-29 05:00 | 367 | 359
2019-11-29 05:30 | 388 | 381
2019-11-29 06:00 | 411 | 406
2019-11-29 06:30 | 466 | 465
2019-11-29 07:00 | 531 | 523
2019-11-29 07:30 | 550 | 542
2019-11-29 08:00 | 570 | 561
2019-11-29 08:30 | 585 | 577
2019-11-29 09:00 | 583 | 575
2019-11-29 09:30 | 565 | 557
2019-11-29 10:00 | 560 | 553
2019-11-29 10:30 | 564 | 557
2019-11-29 11:00 | 557 | 551
2019-11-29 11:30 | 547 | 541
2019-11-29 12:00 | 541 | 535
2019-11-29 12:30 | 536 | 530
2019-11-29 13:00 | 550 | 545
2019-11-29 13:30 | 573 | 568
2019-11-29 14:00 | 596 | 590
2019-11-29 14:30 | 615 | 608
2019-11-29 15:00 | 643 | 637
2019-11-29 15:30 | 659 | 653
2019-11-29 16:00 | 677 | 673
2019-11-29 16:30 | 699 | 696
2019-11-29 17:00 | 699 | 692
2019-11-29 17:30 | 687 | 679
2019-11-29 18:00 | 665 | 657
2019-11-29 18:30 | 632 | 626
2019-11-29 19:00 | 634 | 629
2019-11-29 19:30 | 630 | 625
2019-11-29 20:00 | 627 | 622
2019-11-29 20:30 | 606 | 602
2019-11-29 21:00 | 577 | 573
2019-11-29 21:30 | 559 | 554
2019-11-29 22:00 | 533 | 527
2019-11-29 22:30 | 508 | 502
2019-11-29 23:00 | 498 | 492
2019-11-29 23:30 | 476 | 475
2019-11-30 | 443 | 442
2019-11-30 00:30 | 395 | 393
2019-11-30 01:00 | 381 | 379
2019-11-30 01:30 | 373 | 370
2019-11-30 02:00 | 357 | 352
2019-11-30 02:30 | 353 | 348
2019-11-30 03:00 | 345 | 341
2019-11-30 03:30 | 339 | 335
2019-11-30 04:00 | 340 | 335
2019-11-30 04:30 | 344 | 339
2019-11-30 05:00 | 341 | 335
2019-11-30 05:30 | 346 | 340
2019-11-30 06:00 | 357 | 352
2019-11-30 06:30 | 384 | 380
2019-11-30 07:00 | 404 | 400
2019-11-30 07:30 | 417 | 414
2019-11-30 08:00 | 449 | 447
2019-11-30 08:30 | 457 | 456
2019-11-30 09:00 | 453 | 451
2019-11-30 09:30 | 436 | 435
2019-11-30 10:00 | 428 | 427
2019-11-30 10:30 | 432 | 432
2019-11-30 11:00 | 437 | 437
2019-11-30 11:30 | 449 | 448
2019-11-30 12:00 | 457 | 457
2019-11-30 12:30 | 472 | 472
2019-11-30 13:00 | 494 | 494
2019-11-30 13:30 | 491 | 491
2019-11-30 14:00 | 484 | 483
2019-11-30 14:30 | 497 | 496
2019-11-30 15:00 | 515 | 515
2019-11-30 15:30 | 550 | 545
2019-11-30 16:00 | 568 | 564
2019-11-30 16:30 | 582 | 579
2019-11-30 17:00 | 613 | 610
2019-11-30 17:30 | 602 | 597
2019-11-30 18:00 | 587 | 581
2019-11-30 18:30 | 575 | 569
2019-11-30 19:00 | 578 | 572
2019-11-30 19:30 | 566 | 560
2019-11-30 20:00 | 558 | 551
2019-11-30 20:30 | 536 | 528
2019-11-30 21:00 | 504 | 498
2019-11-30 21:30 | 488 | 486
2019-11-30 22:00 | 471 | 469
2019-11-30 22:30 | 452 | 450
2019-11-30 23:00 | 443 | 442
2019-11-30 23:30 | 423 | 421
2019-12-01 | 395 | 394
2019-12-01 00:30 | 358 | 356
2019-12-01 01:00 | 342 | 340
2019-12-01 01:30 | 332 | 329
2019-12-01 02:00 | 319 | 315
2019-12-01 02:30 | 322 | 318
2019-12-01 03:00 | 308 | 304
2019-12-01 03:30 | 308 | 303
2019-12-01 04:00 | 311 | 307
2019-12-01 04:30 | 313 | 308
2019-12-01 05:00 | 312 | 307
2019-12-01 05:30 | 315 | 309
2019-12-01 06:00 | 324 | 317
2019-12-01 06:30 | 358 | 351
2019-12-01 07:00 | 375 | 370
2019-12-01 07:30 | 399 | 394
2019-12-01 08:00 | 409 | 406
2019-12-01 08:30 | 444 | 443
2019-12-01 09:00 | 437 | 435
2019-12-01 09:30 | 423 | 422
2019-12-01 10:00 | 414 | 414
2019-12-01 10:30 | 421 | 420
2019-12-01 11:00 | 425 | 424
2019-12-01 11:30 | 451 | 448
2019-12-01 12:00 | 455 | 450
2019-12-01 12:30 | 468 | 464
2019-12-01 13:00 | 474 | 469
2019-12-01 13:30 | 510 | 505
2019-12-01 14:00 | 567 | 562
2019-12-01 14:30 | 564 | 559
2019-12-01 15:00 | 515 | 506
2019-12-01 15:30 | 506 | 497
2019-12-01 16:00 | 520 | 513
2019-12-01 16:30 | 523 | 517
2019-12-01 17:00 | 530 | 524
2019-12-01 17:30 | 523 | 516
2019-12-01 18:00 | 515 | 507
2019-12-01 18:30 | 520 | 512
2019-12-01 19:00 | 535 | 529
2019-12-01 19:30 | 529 | 522
2019-12-01 20:00 | 522 | 514
2019-12-01 20:30 | 496 | 491
2019-12-01 21:00 | 469 | 466
2019-12-01 21:30 | 439 | 437
2019-12-01 22:00 | 425 | 423
2019-12-01 22:30 | 412 | 411
2019-12-01 23:00 | 402 | 400
2019-12-01 23:30 | 384 | 382
2019-12-02 | 355 | 352
2019-12-02 00:30 | 329 | 325
2019-12-02 01:00 | 318 | 314
2019-12-02 01:30 | 311 | 306
2019-12-02 02:00 | 293 | 288
2019-12-02 02:30 | 288 | 282
2019-12-02 03:00 | 285 | 278
2019-12-02 03:30 | 288 | 282
2019-12-02 04:00 | 289 | 283
2019-12-02 04:30 | 311 | 306
2019-12-02 05:00 | 318 | 313
2019-12-02 05:30 | 330 | 326
2019-12-02 06:00 | 355 | 353
2019-12-02 06:30 | 399 | 399
2019-12-02 07:00 | 450 | 445
2019-12-02 07:30 | 478 | 473
2019-12-02 08:00 | 487 | 482
2019-12-02 08:30 | 497 | 492
2019-12-02 09:00 | 481 | 477
2019-12-02 09:30 | 467 | 462
2019-12-02 10:00 | 461 | 454
2019-12-02 10:30 | 462 | 454
2019-12-02 11:00 | 456 | 449
2019-12-02 11:30 | 456 | 449
2019-12-02 12:00 | 459 | 453
2019-12-02 12:30 | 465 | 460
2019-12-02 13:00 | 470 | 464
2019-12-02 13:30 | 487 | 483
2019-12-02 14:00 | 518 | 513
2019-12-02 14:30 | 525 | 518
2019-12-02 15:00 | 550 | 545
2019-12-02 15:30 | 576 | 571
2019-12-02 16:00 | 612 | 610
2019-12-02 16:30 | 643 | 640
2019-12-02 17:00 | 666 | 661
2019-12-02 17:30 | 661 | 656
2019-12-02 18:00 | 649 | 643
2019-12-02 18:30 | 632 | 625
2019-12-02 19:00 | 641 | 634
2019-12-02 19:30 | 632 | 624
2019-12-02 20:00 | 616 | 606
2019-12-02 20:30 | 582 | 567
2019-12-02 21:00 | 546 | 532
2019-12-02 21:30 | 524 | 510
2019-12-02 22:00 | 496 | 482
2019-12-02 22:30 | 460 | 458
2019-12-02 23:00 | 437 | 435
2019-12-02 23:30 | 407 | 404
2019-12-03 | 374 | 372
2019-12-03 00:30 | 348 | 345
2019-12-03 01:00 | 336 | 333
2019-12-03 01:30 | 329 | 324
2019-12-03 02:00 | 319 | 314
2019-12-03 02:30 | 314 | 308
2019-12-03 03:00 | 312 | 305
2019-12-03 03:30 | 314 | 308
2019-12-03 04:00 | 317 | 310
2019-12-03 04:30 | 324 | 318
2019-12-03 05:00 | 325 | 318
2019-12-03 05:30 | 338 | 332
2019-12-03 06:00 | 354 | 350
2019-12-03 06:30 | 393 | 391
2019-12-03 07:00 | 430 | 426
2019-12-03 07:30 | 464 | 458
2019-12-03 08:00 | 483 | 474
2019-12-03 08:30 | 482 | 475
2019-12-03 09:00 | 481 | 474
2019-12-03 09:30 | 477 | 471
2019-12-03 10:00 | 472 | 466
2019-12-03 10:30 | 459 | 454
2019-12-03 11:00 | 448 | 443
2019-12-03 11:30 | 452 | 446
2019-12-03 12:00 | 456 | 451
2019-12-03 12:30 | 468 | 464
2019-12-03 13:00 | 480 | 475
2019-12-03 13:30 | 494 | 491
2019-12-03 14:00 | 519 | 513
2019-12-03 14:30 | 548 | 543
2019-12-03 15:00 | 564 | 560
2019-12-03 15:30 | 582 | 578
2019-12-03 16:00 | 616 | 612
2019-12-03 16:30 | 634 | 630
2019-12-03 17:00 | 652 | 647
2019-12-03 17:30 | 650 | 644
2019-12-03 18:00 | 637 | 627
2019-12-03 18:30 | 617 | 606
2019-12-03 19:00 | 629 | 619
2019-12-03 19:30 | 627 | 616
2019-12-03 20:00 | 611 | 599
2019-12-03 20:30 | 588 | 577
2019-12-03 21:00 | 569 | 553
2019-12-03 21:30 | 541 | 524
2019-12-03 22:00 | 507 | 502
2019-12-03 22:30 | 474 | 467
2019-12-03 23:00 | 446 | 439
2019-12-03 23:30 | 407 | 404
2019-12-04 | 374 | 370
2019-12-04 00:30 | 348 | 341
2019-12-04 01:00 | 333 | 325
2019-12-04 01:30 | 322 | 312
2019-12-04 02:00 | 315 | 304
2019-12-04 02:30 | 314 | 302
2019-12-04 03:00 | 312 | 300
2019-12-04 03:30 | 313 | 300
2019-12-04 04:00 | 316 | 303
2019-12-04 04:30 | 324 | 311
2019-12-04 05:00 | 328 | 315
2019-12-04 05:30 | 348 | 336
2019-12-04 06:00 | 365 | 357
2019-12-04 06:30 | 397 | 393
2019-12-04 07:00 | 429 | 427
2019-12-04 07:30 | 458 | 457
2019-12-04 08:00 | 469 | 467
2019-12-04 08:30 | 467 | 465
2019-12-04 09:00 | 465 | 463
2019-12-04 09:30 | 470 | 469
2019-12-04 10:00 | 473 | 472
2019-12-04 10:30 | 466 | 465
2019-12-04 11:00 | 482 | 474
2019-12-04 11:30 | 481 | 474
2019-12-04 12:00 | 488 | 482
2019-12-04 12:30 | 493 | 488
2019-12-04 13:00 | 505 | 499
2019-12-04 13:30 | 516 | 510
2019-12-04 14:00 | 534 | 528
2019-12-04 14:30 | 545 | 541
2019-12-04 15:00 | 559 | 555
2019-12-04 15:30 | 581 | 577
2019-12-04 16:00 | 612 | 608
2019-12-04 16:30 | 631 | 628
2019-12-04 17:00 | 645 | 642
2019-12-04 17:30 | 639 | 636
2019-12-04 18:00 | 627 | 622
2019-12-04 18:30 | 610 | 603
2019-12-04 19:00 | 615 | 608
2019-12-04 19:30 | 609 | 605
2019-12-04 20:00 | 597 | 596
2019-12-04 20:30 | 573 | 572
2019-12-04 21:00 | 550 | 548
2019-12-04 21:30 | 530 | 528
2019-12-04 22:00 | 497 | 492
2019-12-04 22:30 | 468 | 461
2019-12-04 23:00 | 444 | 439
2019-12-04 23:30 | 425 | 421
2019-12-05 | 392 | 388
2019-12-05 00:30 | 353 | 347
2019-12-05 01:00 | 336 | 329
2019-12-05 01:30 | 326 | 317
2019-12-05 02:00 | 317 | 307
2019-12-05 02:30 | 311 | 300
2019-12-05 03:00 | 306 | 295
2019-12-05 03:30 | 318 | 307
2019-12-05 04:00 | 323 | 312
2019-12-05 04:30 | 333 | 322
2019-12-05 05:00 | 332 | 321
2019-12-05 05:30 | 352 | 341
2019-12-05 06:00 | 372 | 364
2019-12-05 06:30 | 409 | 405
2019-12-05 07:00 | 433 | 432
2019-12-05 07:30 | 450 | 450
2019-12-05 08:00 | 452 | 451
2019-12-05 08:30 | 464 | 464
2019-12-05 09:00 | 474 | 474
2019-12-05 09:30 | 477 | 477
2019-12-05 10:00 | 474 | 474
2019-12-05 10:30 | 470 | 469
2019-12-05 11:00 | 477 | 473
2019-12-05 11:30 | 491 | 487
2019-12-05 12:00 | 508 | 505
2019-12-05 12:30 | 533 | 531
2019-12-05 13:00 | 561 | 560
2019-12-05 13:30 | 581 | 580
2019-12-05 14:00 | 600 | 598
2019-12-05 14:30 | 609 | 608
2019-12-05 15:00 | 637 | 634
2019-12-05 15:30 | 666 | 663
2019-12-05 16:00 | 698 | 695
2019-12-05 16:30 | 724 | 721
2019-12-05 17:00 | 744 | 741
2019-12-05 17:30 | 738 | 734
2019-12-05 18:00 | 723 | 718
2019-12-05 18:30 | 703 | 694
2019-12-05 19:00 | 703 | 696
2019-12-05 19:30 | 697 | 689
2019-12-05 20:00 | 679 | 673
2019-12-05 20:30 | 658 | 652
2019-12-05 21:00 | 617 | 609
2019-12-05 21:30 | 573 | 569
2019-12-05 22:00 | 551 | 548
2019-12-05 22:30 | 525 | 522
2019-12-05 23:00 | 506 | 503
2019-12-05 23:30 | 464 | 462
2019-12-06 | 430 | 428
2019-12-06 00:30 | 394 | 393
2019-12-06 01:00 | 375 | 372
2019-12-06 01:30 | 346 | 342
2019-12-06 02:00 | 327 | 323
2019-12-06 02:30 | 324 | 319
2019-12-06 03:00 | 313 | 308
2019-12-06 03:30 | 308 | 302
2019-12-06 04:00 | 309 | 302
2019-12-06 04:30 | 317 | 311
2019-12-06 05:00 | 333 | 326
2019-12-06 05:30 | 358 | 352
2019-12-06 06:00 | 386 | 382
2019-12-06 06:30 | 433 | 431
2019-12-06 07:00 | 472 | 471
2019-12-06 07:30 | 489 | 488
2019-12-06 08:00 | 501 | 500
2019-12-06 08:30 | 505 | 503
2019-12-06 09:00 | 514 | 513
2019-12-06 09:30 | 524 | 524
2019-12-06 10:00 | 532 | 531
2019-12-06 10:30 | 542 | 541
2019-12-06 11:00 | 552 | 551
2019-12-06 11:30 | 571 | 570
2019-12-06 12:00 | 590 | 586
2019-12-06 12:30 | 600 | 596
2019-12-06 13:00 | 619 | 613
2019-12-06 13:30 | 643 | 636
2019-12-06 14:00 | 672 | 666
2019-12-06 14:30 | 695 | 691
2019-12-06 15:00 | 713 | 710
2019-12-06 15:30 | 740 | 736
2019-12-06 16:00 | 759 | 756
2019-12-06 16:30 | 769 | 766
2019-12-06 17:00 | 777 | 773
2019-12-06 17:30 | 782 | 778
2019-12-06 18:00 | 770 | 763
2019-12-06 18:30 | 743 | 734
2019-12-06 19:00 | 726 | 720
2019-12-06 19:30 | 724 | 717
2019-12-06 20:00 | 713 | 705
2019-12-06 20:30 | 697 | 691
2019-12-06 21:00 | 662 | 656
2019-12-06 21:30 | 646 | 637
2019-12-06 22:00 | 625 | 616
2019-12-06 22:30 | 603 | 597
2019-12-06 23:00 | 562 | 558
2019-12-06 23:30 | 515 | 512
2019-12-07 | 482 | 481
2019-12-07 00:30 | 428 | 427
2019-12-07 01:00 | 403 | 402
2019-12-07 01:30 | 381 | 379
2019-12-07 02:00 | 365 | 362
2019-12-07 02:30 | 361 | 356
2019-12-07 03:00 | 357 | 351
2019-12-07 03:30 | 354 | 348
2019-12-07 04:00 | 354 | 348
2019-12-07 04:30 | 357 | 350
2019-12-07 05:00 | 353 | 345
2019-12-07 05:30 | 354 | 346
2019-12-07 06:00 | 358 | 350
2019-12-07 06:30 | 388 | 382
2019-12-07 07:00 | 407 | 402
2019-12-07 07:30 | 429 | 426
2019-12-07 08:00 | 445 | 442
2019-12-07 08:30 | 467 | 465
2019-12-07 09:00 | 481 | 474
2019-12-07 09:30 | 496 | 490
2019-12-07 10:00 | 507 | 498
2019-12-07 10:30 | 543 | 528
2019-12-07 11:00 | 556 | 544
2019-12-07 11:30 | 577 | 564
2019-12-07 12:00 | 603 | 589
2019-12-07 12:30 | 626 | 614
2019-12-07 13:00 | 642 | 632
2019-12-07 13:30 | 651 | 640
2019-12-07 14:00 | 655 | 645
2019-12-07 14:30 | 666 | 656
2019-12-07 15:00 | 673 | 664
2019-12-07 15:30 | 686 | 677
2019-12-07 16:00 | 695 | 686
2019-12-07 16:30 | 693 | 684
2019-12-07 17:00 | 699 | 690
2019-12-07 17:30 | 698 | 688
2019-12-07 18:00 | 679 | 665
2019-12-07 18:30 | 651 | 644
2019-12-07 19:00 | 645 | 639
2019-12-07 19:30 | 631 | 627
2019-12-07 20:00 | 609 | 603
2019-12-07 20:30 | 587 | 581
2019-12-07 21:00 | 555 | 550
2019-12-07 21:30 | 540 | 535
2019-12-07 22:00 | 515 | 510
2019-12-07 22:30 | 489 | 485
2019-12-07 23:00 | 472 | 468
2019-12-07 23:30 | 448 | 444
2019-12-08 | 416 | 413
2019-12-08 00:30 | 379 | 374
2019-12-08 01:00 | 363 | 355
2019-12-08 01:30 | 350 | 340
2019-12-08 02:00 | 336 | 325
2019-12-08 02:30 | 336 | 324
2019-12-08 03:00 | 341 | 328
2019-12-08 03:30 | 339 | 326
2019-12-08 04:00 | 336 | 322
2019-12-08 04:30 | 335 | 321
2019-12-08 05:00 | 328 | 312
2019-12-08 05:30 | 328 | 313
2019-12-08 06:00 | 335 | 320
2019-12-08 06:30 | 362 | 349
2019-12-08 07:00 | 391 | 379
2019-12-08 07:30 | 414 | 405
2019-12-08 08:00 | 429 | 421
2019-12-08 08:30 | 440 | 434
2019-12-08 09:00 | 443 | 439
2019-12-08 09:30 | 443 | 438
2019-12-08 10:00 | 463 | 451
2019-12-08 10:30 | 464 | 453
2019-12-08 11:00 | 451 | 440
2019-12-08 11:30 | 444 | 433
2019-12-08 12:00 | 437 | 427
2019-12-08 12:30 | 430 | 421
2019-12-08 13:00 | 440 | 431
2019-12-08 13:30 | 460 | 453
2019-12-08 14:00 | 487 | 478
2019-12-08 14:30 | 505 | 497
2019-12-08 15:00 | 538 | 531
2019-12-08 15:30 | 554 | 547
2019-12-08 16:00 | 576 | 568
2019-12-08 16:30 | 593 | 585
2019-12-08 17:00 | 599 | 592
2019-12-08 17:30 | 596 | 588
2019-12-08 18:00 | 590 | 581
2019-12-08 18:30 | 572 | 561
2019-12-08 19:00 | 569 | 560
2019-12-08 19:30 | 576 | 567
2019-12-08 20:00 | 564 | 554
2019-12-08 20:30 | 541 | 532
2019-12-08 21:00 | 507 | 496
2019-12-08 21:30 | 489 | 478
2019-12-08 22:00 | 463 | 449
2019-12-08 22:30 | 443 | 438
2019-12-08 23:00 | 430 | 424
2019-12-08 23:30 | 409 | 405
2019-12-09 | 382 | 376
2019-12-09 00:30 | 357 | 348
2019-12-09 01:00 | 344 | 334
2019-12-09 01:30 | 333 | 321
2019-12-09 02:00 | 334 | 322
2019-12-09 02:30 | 325 | 311
2019-12-09 03:00 | 323 | 309
2019-12-09 03:30 | 322 | 308
2019-12-09 04:00 | 325 | 311
2019-12-09 04:30 | 344 | 331
2019-12-09 05:00 | 354 | 341
2019-12-09 05:30 | 387 | 376
2019-12-09 06:00 | 409 | 401
2019-12-09 06:30 | 434 | 430
2019-12-09 07:00 | 477 | 471
2019-12-09 07:30 | 516 | 509
2019-12-09 08:00 | 542 | 535
2019-12-09 08:30 | 571 | 562
2019-12-09 09:00 | 587 | 579
2019-12-09 09:30 | 599 | 590
2019-12-09 10:00 | 600 | 591
2019-12-09 10:30 | 609 | 600
2019-12-09 11:00 | 619 | 610
2019-12-09 11:30 | 621 | 611
2019-12-09 12:00 | 622 | 613
2019-12-09 12:30 | 624 | 615
2019-12-09 13:00 | 633 | 624
2019-12-09 13:30 | 640 | 634
2019-12-09 14:00 | 655 | 649
2019-12-09 14:30 | 665 | 658
2019-12-09 15:00 | 680 | 673
2019-12-09 15:30 | 697 | 691
2019-12-09 16:00 | 724 | 715
2019-12-09 16:30 | 737 | 723
2019-12-09 17:00 | 743 | 730
2019-12-09 17:30 | 731 | 717
2019-12-09 18:00 | 710 | 696
2019-12-09 18:30 | 685 | 671
2019-12-09 19:00 | 674 | 660
2019-12-09 19:30 | 675 | 662
2019-12-09 20:00 | 660 | 646
2019-12-09 20:30 | 630 | 617
2019-12-09 21:00 | 602 | 588
2019-12-09 21:30 | 582 | 569
2019-12-09 22:00 | 545 | 535
2019-12-09 22:30 | 517 | 514
2019-12-09 23:00 | 489 | 485
2019-12-09 23:30 | 456 | 451
2019-12-10 | 428 | 424
2019-12-10 00:30 | 402 | 397
2019-12-10 01:00 | 389 | 383
2019-12-10 01:30 | 373 | 365
2019-12-10 02:00 | 360 | 352
2019-12-10 02:30 | 358 | 349
2019-12-10 03:00 | 358 | 348
2019-12-10 03:30 | 358 | 348
2019-12-10 04:00 | 358 | 348
2019-12-10 04:30 | 374 | 365
2019-12-10 05:00 | 377 | 367
2019-12-10 05:30 | 390 | 382
2019-12-10 06:00 | 405 | 399
2019-12-10 06:30 | 452 | 448
2019-12-10 07:00 | 495 | 492
2019-12-10 07:30 | 538 | 536
2019-12-10 08:00 | 561 | 557
2019-12-10 08:30 | 582 | 577
2019-12-10 09:00 | 594 | 588
2019-12-10 09:30 | 585 | 580
2019-12-10 10:00 | 580 | 575
2019-12-10 10:30 | 582 | 578
2019-12-10 11:00 | 579 | 574
2019-12-10 11:30 | 580 | 575
2019-12-10 12:00 | 595 | 590
2019-12-10 12:30 | 607 | 602
2019-12-10 13:00 | 632 | 627
2019-12-10 13:30 | 654 | 649
2019-12-10 14:00 | 667 | 663
2019-12-10 14:30 | 691 | 688
2019-12-10 15:00 | 707 | 705
2019-12-10 15:30 | 733 | 731
2019-12-10 16:00 | 764 | 762
2019-12-10 16:30 | 797 | 783
2019-12-10 17:00 | 793 | 779
2019-12-10 17:30 | 780 | 763
2019-12-10 18:00 | 761 | 742
2019-12-10 18:30 | 732 | 716
2019-12-10 19:00 | 725 | 712
2019-12-10 19:30 | 714 | 700
2019-12-10 20:00 | 676 | 670
2019-12-10 20:30 | 643 | 638
2019-12-10 21:00 | 618 | 612
2019-12-10 21:30 | 588 | 585
2019-12-10 22:00 | 552 | 551
2019-12-10 22:30 | 528 | 527
2019-12-10 23:00 | 507 | 506
2019-12-10 23:30 | 475 | 474
2019-12-11 | 444 | 443
2019-12-11 00:30 | 407 | 406
2019-12-11 01:00 | 399 | 398
2019-12-11 01:30 | 383 | 382
2019-12-11 02:00 | 368 | 367
2019-12-11 02:30 | 369 | 368
2019-12-11 03:00 | 370 | 370
2019-12-11 03:30 | 369 | 369
2019-12-11 04:00 | 373 | 372
2019-12-11 04:30 | 377 | 377
2019-12-11 05:00 | 374 | 374
2019-12-11 05:30 | 391 | 391
2019-12-11 06:00 | 413 | 413
2019-12-11 06:30 | 465 | 464
2019-12-11 07:00 | 512 | 511
2019-12-11 07:30 | 552 | 551
2019-12-11 08:00 | 575 | 572
2019-12-11 08:30 | 589 | 586
2019-12-11 09:00 | 595 | 592
2019-12-11 09:30 | 605 | 603
2019-12-11 10:00 | 619 | 616
2019-12-11 10:30 | 629 | 625
2019-12-11 11:00 | 644 | 641
2019-12-11 11:30 | 645 | 641
2019-12-11 12:00 | 654 | 651
2019-12-11 12:30 | 671 | 668
2019-12-11 13:00 | 697 | 695
2019-12-11 13:30 | 715 | 712
2019-12-11 14:00 | 735 | 733
2019-12-11 14:30 | 749 | 747
2019-12-11 15:00 | 763 | 762
2019-12-11 15:30 | 771 | 770
2019-12-11 16:00 | 811 | 805
2019-12-11 16:30 | 799 | 793
2019-12-11 17:00 | 778 | 770
2019-12-11 17:30 | 750 | 741
2019-12-11 18:00 | 709 | 703
2019-12-11 18:30 | 687 | 679
2019-12-11 19:00 | 682 | 677
2019-12-11 19:30 | 674 | 670
2019-12-11 20:00 | 662 | 659
2019-12-11 20:30 | 634 | 631
2019-12-11 21:00 | 598 | 597
2019-12-11 21:30 | 581 | 579
2019-12-11 22:00 | 552 | 547
2019-12-11 22:30 | 497 | 495
2019-12-11 23:00 | 444 | 443
2019-12-11 23:30 | 398 | 397
2019-12-12 | 378 | 376
2019-12-12 00:30 | 349 | 347
2019-12-12 01:00 | 334 | 332
2019-12-12 01:30 | 331 | 328
2019-12-12 02:00 | 324 | 321
2019-12-12 02:30 | 325 | 322
2019-12-12 03:00 | 324 | 321
2019-12-12 03:30 | 325 | 322
2019-12-12 04:00 | 326 | 323
2019-12-12 04:30 | 341 | 338
2019-12-12 05:00 | 351 | 348
2019-12-12 05:30 | 366 | 364
2019-12-12 06:00 | 384 | 383
2019-12-12 06:30 | 430 | 429
2019-12-12 07:00 | 449 | 448
2019-12-12 07:30 | 465 | 463
2019-12-12 08:00 | 478 | 477
2019-12-12 08:30 | 495 | 493
2019-12-12 09:00 | 510 | 508
2019-12-12 09:30 | 520 | 518
2019-12-12 10:00 | 520 | 518
2019-12-12 10:30 | 527 | 525
2019-12-12 11:00 | 535 | 532
2019-12-12 11:30 | 539 | 536
2019-12-12 12:00 | 546 | 543
2019-12-12 12:30 | 565 | 563
2019-12-12 13:00 | 588 | 586
2019-12-12 13:30 | 611 | 609
2019-12-12 14:00 | 637 | 634
2019-12-12 14:30 | 664 | 659
2019-12-12 15:00 | 676 | 672
2019-12-12 15:30 | 698 | 695
2019-12-12 16:00 | 714 | 710
2019-12-12 16:30 | 740 | 737
2019-12-12 17:00 | 748 | 746
2019-12-12 17:30 | 731 | 727
2019-12-12 18:00 | 706 | 700
2019-12-12 18:30 | 678 | 673
2019-12-12 19:00 | 683 | 680
2019-12-12 19:30 | 678 | 675
2019-12-12 20:00 | 669 | 666
2019-12-12 20:30 | 642 | 640
2019-12-12 21:00 | 607 | 606
2019-12-12 21:30 | 581 | 581
2019-12-12 22:00 | 558 | 558
2019-12-12 22:30 | 525 | 525
2019-12-12 23:00 | 490 | 489
2019-12-12 23:30 | 472 | 471
2019-12-13 | 437 | 437
2019-12-13 00:30 | 401 | 400
2019-12-13 01:00 | 388 | 387
2019-12-13 01:30 | 375 | 375
2019-12-13 02:00 | 366 | 366
2019-12-13 02:30 | 357 | 355
2019-12-13 03:00 | 353 | 352
2019-12-13 03:30 | 356 | 354
2019-12-13 04:00 | 361 | 359
2019-12-13 04:30 | 365 | 363
2019-12-13 05:00 | 373 | 372
2019-12-13 05:30 | 389 | 388
2019-12-13 06:00 | 412 | 411
2019-12-13 06:30 | 467 | 467
2019-12-13 07:00 | 495 | 495
2019-12-13 07:30 | 533 | 532
2019-12-13 08:00 | 559 | 555
2019-12-13 08:30 | 578 | 575
2019-12-13 09:00 | 604 | 602
2019-12-13 09:30 | 614 | 611
2019-12-13 10:00 | 603 | 599
2019-12-13 10:30 | 582 | 577
2019-12-13 11:00 | 555 | 550
2019-12-13 11:30 | 564 | 560
2019-12-13 12:00 | 568 | 564
2019-12-13 12:30 | 576 | 572
2019-12-13 13:00 | 581 | 577
2019-12-13 13:30 | 585 | 582
2019-12-13 14:00 | 566 | 562
2019-12-13 14:30 | 561 | 557
2019-12-13 15:00 | 603 | 600
2019-12-13 15:30 | 615 | 612
2019-12-13 16:00 | 596 | 590
2019-12-13 16:30 | 551 | 546
2019-12-13 17:00 | 538 | 533
2019-12-13 17:30 | 547 | 540
2019-12-13 18:00 | 543 | 535
2019-12-13 18:30 | 531 | 521
2019-12-13 19:00 | 526 | 517
2019-12-13 19:30 | 528 | 519
2019-12-13 20:00 | 520 | 512
2019-12-13 20:30 | 508 | 503
2019-12-13 21:00 | 483 | 481
2019-12-13 21:30 | 475 | 473
2019-12-13 22:00 | 467 | 465
2019-12-13 22:30 | 442 | 441
2019-12-13 23:00 | 429 | 427
2019-12-13 23:30 | 412 | 411
2019-12-14 | 397 | 396
2019-12-14 00:30 | 367 | 366
2019-12-14 01:00 | 351 | 350
2019-12-14 01:30 | 336 | 334
2019-12-14 02:00 | 320 | 318
2019-12-14 02:30 | 318 | 315
2019-12-14 03:00 | 318 | 315
2019-12-14 03:30 | 312 | 308
2019-12-14 04:00 | 307 | 303
2019-12-14 04:30 | 307 | 302
2019-12-14 05:00 | 304 | 299
2019-12-14 05:30 | 320 | 315
2019-12-14 06:00 | 328 | 324
2019-12-14 06:30 | 348 | 344
2019-12-14 07:00 | 363 | 361
2019-12-14 07:30 | 360 | 358
2019-12-14 08:00 | 377 | 376
2019-12-14 08:30 | 407 | 407
2019-12-14 09:00 | 422 | 422
2019-12-14 09:30 | 408 | 407
2019-12-14 10:00 | 396 | 395
2019-12-14 10:30 | 397 | 396
2019-12-14 11:00 | 385 | 384
2019-12-14 11:30 | 389 | 388
2019-12-14 12:00 | 405 | 404
2019-12-14 12:30 | 419 | 419
2019-12-14 13:00 | 441 | 441
2019-12-14 13:30 | 473 | 473
2019-12-14 14:00 | 494 | 494
2019-12-14 14:30 | 506 | 505
2019-12-14 15:00 | 537 | 533
2019-12-14 15:30 | 557 | 553
2019-12-14 16:00 | 580 | 576
2019-12-14 16:30 | 605 | 602
2019-12-14 17:00 | 616 | 613
2019-12-14 17:30 | 609 | 604
2019-12-14 18:00 | 604 | 598
2019-12-14 18:30 | 599 | 591
2019-12-14 19:00 | 593 | 586
2019-12-14 19:30 | 592 | 584
2019-12-14 20:00 | 581 | 573
2019-12-14 20:30 | 563 | 553
2019-12-14 21:00 | 542 | 531
2019-12-14 21:30 | 533 | 521
2019-12-14 22:00 | 502 | 499
2019-12-14 22:30 | 479 | 477
2019-12-14 23:00 | 456 | 453
2019-12-14 23:30 | 434 | 432
2019-12-15 | 417 | 415
2019-12-15 00:30 | 377 | 375
2019-12-15 01:00 | 362 | 360
2019-12-15 01:30 | 347 | 344
2019-12-15 02:00 | 334 | 331
2019-12-15 02:30 | 330 | 326
2019-12-15 03:00 | 331 | 327
2019-12-15 03:30 | 335 | 331
2019-12-15 04:00 | 341 | 336
2019-12-15 04:30 | 344 | 339
2019-12-15 05:00 | 339 | 333
2019-12-15 05:30 | 340 | 333
2019-12-15 06:00 | 341 | 334
2019-12-15 06:30 | 347 | 340
2019-12-15 07:00 | 368 | 363
2019-12-15 07:30 | 387 | 383
2019-12-15 08:00 | 400 | 399
2019-12-15 08:30 | 417 | 417
2019-12-15 09:00 | 440 | 439
2019-12-15 09:30 | 444 | 444
2019-12-15 10:00 | 443 | 442
2019-12-15 10:30 | 446 | 446
2019-12-15 11:00 | 453 | 452
2019-12-15 11:30 | 461 | 461
2019-12-15 12:00 | 472 | 470
2019-12-15 12:30 | 487 | 483
2019-12-15 13:00 | 505 | 502
2019-12-15 13:30 | 518 | 515
2019-12-15 14:00 | 532 | 529
2019-12-15 14:30 | 558 | 554
2019-12-15 15:00 | 596 | 592
2019-12-15 15:30 | 617 | 609
2019-12-15 16:00 | 616 | 609
2019-12-15 16:30 | 637 | 631
2019-12-15 17:00 | 649 | 642
2019-12-15 17:30 | 643 | 634
2019-12-15 18:00 | 642 | 632
2019-12-15 18:30 | 631 | 622
2019-12-15 19:00 | 634 | 626
2019-12-15 19:30 | 623 | 615
2019-12-15 20:00 | 616 | 607
2019-12-15 20:30 | 600 | 590
2019-12-15 21:00 | 570 | 559
2019-12-15 21:30 | 549 | 538
2019-12-15 22:00 | 523 | 510
2019-12-15 22:30 | 508 | 499
2019-12-15 23:00 | 485 | 476
2019-12-15 23:30 | 466 | 457
2019-12-16 | 433 | 428
2019-12-16 00:30 | 397 | 391
2019-12-16 01:00 | 379 | 375
2019-12-16 01:30 | 375 | 370
2019-12-16 02:00 | 370 | 365
2019-12-16 02:30 | 365 | 359
2019-12-16 03:00 | 360 | 354
2019-12-16 03:30 | 364 | 357
2019-12-16 04:00 | 368 | 361
2019-12-16 04:30 | 374 | 368
2019-12-16 05:00 | 375 | 369
2019-12-16 05:30 | 379 | 373
2019-12-16 06:00 | 384 | 381
2019-12-16 06:30 | 434 | 433
2019-12-16 07:00 | 482 | 482
2019-12-16 07:30 | 516 | 516
2019-12-16 08:00 | 541 | 541
2019-12-16 08:30 | 579 | 579
2019-12-16 09:00 | 597 | 597
2019-12-16 09:30 | 590 | 589
2019-12-16 10:00 | 614 | 611
2019-12-16 10:30 | 638 | 633
2019-12-16 11:00 | 655 | 647
2019-12-16 11:30 | 669 | 662
2019-12-16 12:00 | 694 | 688
2019-12-16 12:30 | 711 | 707
2019-12-16 13:00 | 732 | 727
2019-12-16 13:30 | 755 | 750
2019-12-16 14:00 | 775 | 769
2019-12-16 14:30 | 802 | 797
2019-12-16 15:00 | 831 | 827
2019-12-16 15:30 | 822 | 815
2019-12-16 16:00 | 781 | 774
2019-12-16 16:30 | 768 | 759
2019-12-16 17:00 | 763 | 754
2019-12-16 17:30 | 744 | 732
2019-12-16 18:00 | 702 | 695
2019-12-16 18:30 | 671 | 662
2019-12-16 19:00 | 645 | 639
2019-12-16 19:30 | 629 | 623
2019-12-16 20:00 | 597 | 592
2019-12-16 20:30 | 577 | 571
2019-12-16 21:00 | 561 | 555
2019-12-16 21:30 | 522 | 516
2019-12-16 22:00 | 505 | 498
2019-12-16 22:30 | 464 | 460
2019-12-16 23:00 | 444 | 438
2019-12-16 23:30 | 426 | 417
2019-12-17 | 411 | 400
2019-12-17 00:30 | 379 | 369
2019-12-17 01:00 | 356 | 351
2019-12-17 01:30 | 338 | 333
2019-12-17 02:00 | 332 | 326
2019-12-17 02:30 | 342 | 336
2019-12-17 03:00 | 343 | 337
2019-12-17 03:30 | 338 | 331
2019-12-17 04:00 | 337 | 330
2019-12-17 04:30 | 347 | 341
2019-12-17 05:00 | 359 | 352
2019-12-17 05:30 | 376 | 369
2019-12-17 06:00 | 384 | 379
2019-12-17 06:30 | 422 | 419
2019-12-17 07:00 | 444 | 443
2019-12-17 07:30 | 465 | 464
2019-12-17 08:00 | 475 | 473
2019-12-17 08:30 | 484 | 483
2019-12-17 09:00 | 483 | 483
2019-12-17 09:30 | 478 | 477
2019-12-17 10:00 | 476 | 476
2019-12-17 10:30 | 480 | 479
2019-12-17 11:00 | 482 | 481
2019-12-17 11:30 | 479 | 478
2019-12-17 12:00 | 476 | 474
2019-12-17 12:30 | 475 | 473
2019-12-17 13:00 | 474 | 473
2019-12-17 13:30 | 478 | 477
2019-12-17 14:00 | 500 | 499
2019-12-17 14:30 | 509 | 508
2019-12-17 15:00 | 531 | 530
2019-12-17 15:30 | 549 | 544
2019-12-17 16:00 | 558 | 549
2019-12-17 16:30 | 578 | 565
2019-12-17 17:00 | 592 | 580
2019-12-17 17:30 | 591 | 578
2019-12-17 18:00 | 571 | 558
2019-12-17 18:30 | 548 | 532
2019-12-17 19:00 | 542 | 526
2019-12-17 19:30 | 534 | 519
2019-12-17 20:00 | 526 | 511
2019-12-17 20:30 | 504 | 491
2019-12-17 21:00 | 480 | 467
2019-12-17 21:30 | 467 | 456
2019-12-17 22:00 | 462 | 449
2019-12-17 22:30 | 454 | 438
2019-12-17 23:00 | 431 | 414
2019-12-17 23:30 | 397 | 388
2019-12-18 | 377 | 367
2019-12-18 00:30 | 347 | 338
2019-12-18 01:00 | 332 | 323
2019-12-18 01:30 | 321 | 310
2019-12-18 02:00 | 313 | 302
2019-12-18 02:30 | 311 | 300
2019-12-18 03:00 | 304 | 293
2019-12-18 03:30 | 303 | 292
2019-12-18 04:00 | 310 | 299
2019-12-18 04:30 | 318 | 307
2019-12-18 05:00 | 325 | 314
2019-12-18 05:30 | 343 | 334
2019-12-18 06:00 | 367 | 360
2019-12-18 06:30 | 405 | 401
2019-12-18 07:00 | 436 | 434
2019-12-18 07:30 | 446 | 444
2019-12-18 08:00 | 473 | 464
2019-12-18 08:30 | 491 | 480
2019-12-18 09:00 | 466 | 457
2019-12-18 09:30 | 458 | 450
2019-12-18 10:00 | 449 | 440
2019-12-18 10:30 | 449 | 441
2019-12-18 11:00 | 447 | 440
2019-12-18 11:30 | 435 | 428
2019-12-18 12:00 | 439 | 433
2019-12-18 12:30 | 444 | 437
2019-12-18 13:00 | 448 | 441
2019-12-18 13:30 | 460 | 454
2019-12-18 14:00 | 488 | 483
2019-12-18 14:30 | 498 | 493
2019-12-18 15:00 | 526 | 521
2019-12-18 15:30 | 541 | 536
2019-12-18 16:00 | 548 | 543
2019-12-18 16:30 | 564 | 560
2019-12-18 17:00 | 579 | 575
2019-12-18 17:30 | 575 | 567
2019-12-18 18:00 | 559 | 550
2019-12-18 18:30 | 535 | 529
2019-12-18 19:00 | 536 | 532
2019-12-18 19:30 | 532 | 528
2019-12-18 20:00 | 530 | 526
2019-12-18 20:30 | 514 | 510
2019-12-18 21:00 | 494 | 491
2019-12-18 21:30 | 480 | 477
2019-12-18 22:00 | 469 | 467
2019-12-18 22:30 | 457 | 453
2019-12-18 23:00 | 432 | 428
2019-12-18 23:30 | 408 | 402
2019-12-19 | 384 | 378
2019-12-19 00:30 | 364 | 356
2019-12-19 01:00 | 351 | 341
2019-12-19 01:30 | 345 | 335
2019-12-19 02:00 | 338 | 328
2019-12-19 02:30 | 340 | 329
2019-12-19 03:00 | 331 | 319
2019-12-19 03:30 | 334 | 319
2019-12-19 04:00 | 336 | 321
2019-12-19 04:30 | 348 | 334
2019-12-19 05:00 | 352 | 337
2019-12-19 05:30 | 364 | 350
2019-12-19 06:00 | 372 | 360
2019-12-19 06:30 | 409 | 400
2019-12-19 07:00 | 438 | 433
2019-12-19 07:30 | 462 | 456
2019-12-19 08:00 | 480 | 474
2019-12-19 08:30 | 478 | 472
2019-12-19 09:00 | 478 | 472
2019-12-19 09:30 | 484 | 478
2019-12-19 10:00 | 489 | 484
2019-12-19 10:30 | 491 | 487
2019-12-19 11:00 | 489 | 485
2019-12-19 11:30 | 505 | 501
2019-12-19 12:00 | 517 | 513
2019-12-19 12:30 | 524 | 519
2019-12-19 13:00 | 544 | 540
2019-12-19 13:30 | 567 | 558
2019-12-19 14:00 | 564 | 553
2019-12-19 14:30 | 563 | 552
2019-12-19 15:00 | 592 | 580
2019-12-19 15:30 | 619 | 606
2019-12-19 16:00 | 614 | 605
2019-12-19 16:30 | 618 | 611
2019-12-19 17:00 | 633 | 627
2019-12-19 17:30 | 624 | 617
2019-12-19 18:00 | 609 | 599
2019-12-19 18:30 | 580 | 567
2019-12-19 19:00 | 567 | 556
2019-12-19 19:30 | 565 | 554
2019-12-19 20:00 | 562 | 550
2019-12-19 20:30 | 548 | 534
2019-12-19 21:00 | 520 | 505
2019-12-19 21:30 | 506 | 496
2019-12-19 22:00 | 491 | 484
2019-12-19 22:30 | 479 | 470
2019-12-19 23:00 | 463 | 451
2019-12-19 23:30 | 436 | 425
2019-12-20 | 407 | 396
2019-12-20 00:30 | 378 | 364
2019-12-20 01:00 | 361 | 346
2019-12-20 01:30 | 354 | 339
2019-12-20 02:00 | 352 | 335
2019-12-20 02:30 | 356 | 339
2019-12-20 03:00 | 346 | 328
2019-12-20 03:30 | 342 | 323
2019-12-20 04:00 | 344 | 326
2019-12-20 04:30 | 352 | 334
2019-12-20 05:00 | 358 | 340
2019-12-20 05:30 | 371 | 354
2019-12-20 06:00 | 374 | 359
2019-12-20 06:30 | 411 | 401
2019-12-20 07:00 | 457 | 445
2019-12-20 07:30 | 490 | 478
2019-12-20 08:00 | 491 | 482
2019-12-20 08:30 | 502 | 495
2019-12-20 09:00 | 508 | 499
2019-12-20 09:30 | 505 | 496
2019-12-20 10:00 | 496 | 489
2019-12-20 10:30 | 503 | 497
2019-12-20 11:00 | 510 | 504
2019-12-20 11:30 | 522 | 518
2019-12-20 12:00 | 546 | 542
2019-12-20 12:30 | 561 | 556
2019-12-20 13:00 | 572 | 568
2019-12-20 13:30 | 583 | 580
2019-12-20 14:00 | 598 | 595
2019-12-20 14:30 | 616 | 612
2019-12-20 15:00 | 640 | 636
2019-12-20 15:30 | 651 | 647
2019-12-20 16:00 | 653 | 649
2019-12-20 16:30 | 658 | 651
2019-12-20 17:00 | 661 | 653
2019-12-20 17:30 | 643 | 634
2019-12-20 18:00 | 613 | 602
2019-12-20 18:30 | 585 | 577
2019-12-20 19:00 | 585 | 579
2019-12-20 19:30 | 579 | 574
2019-12-20 20:00 | 579 | 573
2019-12-20 20:30 | 566 | 560
2019-12-20 21:00 | 531 | 526
2019-12-20 21:30 | 535 | 529
2019-12-20 22:00 | 523 | 516
2019-12-20 22:30 | 505 | 499
2019-12-20 23:00 | 490 | 485
2019-12-20 23:30 | 465 | 460
2019-12-21 | 430 | 426
2019-12-21 00:30 | 397 | 390
2019-12-21 01:00 | 380 | 372
2019-12-21 01:30 | 375 | 365
2019-12-21 02:00 | 362 | 352
2019-12-21 02:30 | 352 | 341
2019-12-21 03:00 | 349 | 338
2019-12-21 03:30 | 346 | 334
2019-12-21 04:00 | 343 | 331
2019-12-21 04:30 | 344 | 332
2019-12-21 05:00 | 335 | 322
2019-12-21 05:30 | 331 | 317
2019-12-21 06:00 | 339 | 324
2019-12-21 06:30 | 363 | 350
2019-12-21 07:00 | 381 | 370
2019-12-21 07:30 | 397 | 389
2019-12-21 08:00 | 419 | 413
2019-12-21 08:30 | 424 | 420
2019-12-21 09:00 | 424 | 419
2019-12-21 09:30 | 405 | 401
2019-12-21 10:00 | 403 | 400
2019-12-21 10:30 | 412 | 409
2019-12-21 11:00 | 428 | 426
2019-12-21 11:30 | 441 | 439
2019-12-21 12:00 | 449 | 448
2019-12-21 12:30 | 475 | 474
2019-12-21 13:00 | 490 | 490
2019-12-21 13:30 | 508 | 508
2019-12-21 14:00 | 535 | 531
2019-12-21 14:30 | 562 | 556
2019-12-21 15:00 | 589 | 583
2019-12-21 15:30 | 611 | 604
2019-12-21 16:00 | 627 | 620
2019-12-21 16:30 | 643 | 637
2019-12-21 17:00 | 646 | 641
2019-12-21 17:30 | 627 | 622
2019-12-21 18:00 | 604 | 597
2019-12-21 18:30 | 585 | 578
2019-12-21 19:00 | 578 | 571
2019-12-21 19:30 | 572 | 567
2019-12-21 20:00 | 563 | 557
2019-12-21 20:30 | 549 | 544
2019-12-21 21:00 | 530 | 529
2019-12-21 21:30 | 507 | 506
2019-12-21 22:00 | 492 | 490
2019-12-21 22:30 | 460 | 457
2019-12-21 23:00 | 439 | 436
2019-12-21 23:30 | 412 | 409
2019-12-22 | 388 | 386
2019-12-22 00:30 | 353 | 350
2019-12-22 01:00 | 341 | 337
2019-12-22 01:30 | 330 | 325
2019-12-22 02:00 | 324 | 318
2019-12-22 02:30 | 320 | 314
2019-12-22 03:00 | 319 | 312
2019-12-22 03:30 | 323 | 315
2019-12-22 04:00 | 325 | 317
2019-12-22 04:30 | 326 | 317
2019-12-22 05:00 | 316 | 307
2019-12-22 05:30 | 321 | 311
2019-12-22 06:00 | 322 | 312
2019-12-22 06:30 | 350 | 340
2019-12-22 07:00 | 378 | 369
2019-12-22 07:30 | 396 | 389
2019-12-22 08:00 | 407 | 401
2019-12-22 08:30 | 429 | 424
2019-12-22 09:00 | 437 | 432
2019-12-22 09:30 | 424 | 420
2019-12-22 10:00 | 420 | 417
2019-12-22 10:30 | 424 | 422
2019-12-22 11:00 | 428 | 426
2019-12-22 11:30 | 433 | 432
2019-12-22 12:00 | 442 | 441
2019-12-22 12:30 | 447 | 447
2019-12-22 13:00 | 456 | 456
2019-12-22 13:30 | 463 | 462
2019-12-22 14:00 | 476 | 475
2019-12-22 14:30 | 508 | 507
2019-12-22 15:00 | 533 | 532
2019-12-22 15:30 | 552 | 551
2019-12-22 16:00 | 569 | 565
2019-12-22 16:30 | 570 | 566
2019-12-22 17:00 | 562 | 558
2019-12-22 17:30 | 535 | 531
2019-12-22 18:00 | 517 | 513
2019-12-22 18:30 | 498 | 494
2019-12-22 19:00 | 502 | 499
2019-12-22 19:30 | 497 | 494
2019-12-22 20:00 | 491 | 487
2019-12-22 20:30 | 480 | 479
2019-12-22 21:00 | 458 | 458
2019-12-22 21:30 | 450 | 449
2019-12-22 22:00 | 450 | 448
2019-12-22 22:30 | 439 | 436
2019-12-22 23:00 | 426 | 423
2019-12-22 23:30 | 413 | 412
2019-12-23 | 393 | 391
2019-12-23 00:30 | 362 | 359
2019-12-23 01:00 | 351 | 344
2019-12-23 01:30 | 338 | 330
2019-12-23 02:00 | 337 | 329
2019-12-23 02:30 | 335 | 326
2019-12-23 03:00 | 333 | 323
2019-12-23 03:30 | 336 | 326
2019-12-23 04:00 | 337 | 327
2019-12-23 04:30 | 341 | 331
2019-12-23 05:00 | 343 | 334
2019-12-23 05:30 | 352 | 344
2019-12-23 06:00 | 365 | 358
2019-12-23 06:30 | 410 | 405
2019-12-23 07:00 | 443 | 440
2019-12-23 07:30 | 471 | 470
2019-12-23 08:00 | 492 | 491
2019-12-23 08:30 | 509 | 502
2019-12-23 09:00 | 510 | 503
2019-12-23 09:30 | 500 | 493
2019-12-23 10:00 | 497 | 491
2019-12-23 10:30 | 508 | 501
2019-12-23 11:00 | 515 | 508
2019-12-23 11:30 | 514 | 507
2019-12-23 12:00 | 511 | 505
2019-12-23 12:30 | 515 | 510
2019-12-23 13:00 | 521 | 517
2019-12-23 13:30 | 521 | 518
2019-12-23 14:00 | 530 | 524
2019-12-23 14:30 | 553 | 549
2019-12-23 15:00 | 590 | 587
2019-12-23 15:30 | 616 | 614
2019-12-23 16:00 | 635 | 632
2019-12-23 16:30 | 644 | 641
2019-12-23 17:00 | 653 | 650
2019-12-23 17:30 | 654 | 650
2019-12-23 18:00 | 635 | 631
2019-12-23 18:30 | 610 | 604
2019-12-23 19:00 | 605 | 600
2019-12-23 19:30 | 603 | 598
2019-12-23 20:00 | 603 | 597
2019-12-23 20:30 | 588 | 580
2019-12-23 21:00 | 568 | 560
2019-12-23 21:30 | 546 | 538
2019-12-23 22:00 | 535 | 526
2019-12-23 22:30 | 505 | 505
2019-12-23 23:00 | 488 | 487
2019-12-23 23:30 | 472 | 469
2019-12-24 | 446 | 442
2019-12-24 00:30 | 413 | 409
2019-12-24 01:00 | 405 | 400
2019-12-24 01:30 | 401 | 395
2019-12-24 02:00 | 384 | 378
2019-12-24 02:30 | 374 | 367
2019-12-24 03:00 | 371 | 364
2019-12-24 03:30 | 376 | 369
2019-12-24 04:00 | 375 | 368
2019-12-24 04:30 | 386 | 379
2019-12-24 05:00 | 383 | 376
2019-12-24 05:30 | 384 | 378
2019-12-24 06:00 | 398 | 392
2019-12-24 06:30 | 439 | 435
2019-12-24 07:00 | 474 | 472
2019-12-24 07:30 | 501 | 500
2019-12-24 08:00 | 516 | 515
2019-12-24 08:30 | 546 | 546
2019-12-24 09:00 | 555 | 553
2019-12-24 09:30 | 555 | 554
2019-12-24 10:00 | 555 | 554
2019-12-24 10:30 | 562 | 561
2019-12-24 11:00 | 576 | 575
2019-12-24 11:30 | 564 | 563
2019-12-24 12:00 | 541 | 539
2019-12-24 12:30 | 537 | 535
2019-12-24 13:00 | 563 | 561
2019-12-24 13:30 | 577 | 575
2019-12-24 14:00 | 586 | 581
2019-12-24 14:30 | 593 | 587
2019-12-24 15:00 | 605 | 598
2019-12-24 15:30 | 614 | 607
2019-12-24 16:00 | 632 | 626
2019-12-24 16:30 | 647 | 642
2019-12-24 17:00 | 650 | 646
2019-12-24 17:30 | 640 | 635
2019-12-24 18:00 | 627 | 621
2019-12-24 18:30 | 604 | 594
2019-12-24 19:00 | 588 | 584
2019-12-24 19:30 | 576 | 571
2019-12-24 20:00 | 543 | 540
2019-12-24 20:30 | 525 | 522
2019-12-24 21:00 | 499 | 496
2019-12-24 21:30 | 490 | 487
2019-12-24 22:00 | 486 | 483
2019-12-24 22:30 | 476 | 472
2019-12-24 23:00 | 465 | 459
2019-12-24 23:30 | 447 | 438
2019-12-25 | 421 | 411
2019-12-25 00:30 | 388 | 376
2019-12-25 01:00 | 377 | 363
2019-12-25 01:30 | 372 | 357
2019-12-25 02:00 | 357 | 341
2019-12-25 02:30 | 345 | 329
2019-12-25 03:00 | 334 | 316
2019-12-25 03:30 | 333 | 312
2019-12-25 04:00 | 336 | 315
2019-12-25 04:30 | 340 | 319
2019-12-25 05:00 | 348 | 327
2019-12-25 05:30 | 349 | 326
2019-12-25 06:00 | 354 | 333
2019-12-25 06:30 | 380 | 361
2019-12-25 07:00 | 409 | 393
2019-12-25 07:30 | 432 | 419
2019-12-25 08:00 | 452 | 439
2019-12-25 08:30 | 467 | 455
2019-12-25 09:00 | 464 | 454
2019-12-25 09:30 | 458 | 448
2019-12-25 10:00 | 466 | 458
2019-12-25 10:30 | 462 | 453
2019-12-25 11:00 | 467 | 459
2019-12-25 11:30 | 450 | 440
2019-12-25 12:00 | 437 | 426
2019-12-25 12:30 | 428 | 416
2019-12-25 13:00 | 413 | 400
2019-12-25 13:30 | 404 | 391
2019-12-25 14:00 | 415 | 402
2019-12-25 14:30 | 417 | 404
2019-12-25 15:00 | 421 | 409
2019-12-25 15:30 | 416 | 405
2019-12-25 16:00 | 410 | 399
2019-12-25 16:30 | 422 | 413
2019-12-25 17:00 | 441 | 432
2019-12-25 17:30 | 440 | 431
2019-12-25 18:00 | 421 | 413
2019-12-25 18:30 | 411 | 402
2019-12-25 19:00 | 418 | 409
2019-12-25 19:30 | 435 | 428
2019-12-25 20:00 | 439 | 432
2019-12-25 20:30 | 438 | 430
2019-12-25 21:00 | 434 | 426
2019-12-25 21:30 | 434 | 425
2019-12-25 22:00 | 435 | 426
2019-12-25 22:30 | 426 | 416
2019-12-25 23:00 | 419 | 409
2019-12-25 23:30 | 411 | 399
2019-12-26 | 393 | 377
2019-12-26 00:30 | 371 | 353
2019-12-26 01:00 | 357 | 337
2019-12-26 01:30 | 348 | 325
2019-12-26 02:00 | 347 | 321
2019-12-26 02:30 | 343 | 314
2019-12-26 03:00 | 338 | 309
2019-12-26 03:30 | 338 | 308
2019-12-26 04:00 | 341 | 312
2019-12-26 04:30 | 346 | 316
2019-12-26 05:00 | 348 | 317
2019-12-26 05:30 | 346 | 317
2019-12-26 06:00 | 347 | 319
2019-12-26 06:30 | 369 | 344
2019-12-26 07:00 | 383 | 361
2019-12-26 07:30 | 390 | 373
2019-12-26 08:00 | 405 | 392
2019-12-26 08:30 | 403 | 392
2019-12-26 09:00 | 405 | 396
2019-12-26 09:30 | 405 | 397
2019-12-26 10:00 | 395 | 387
2019-12-26 10:30 | 391 | 383
2019-12-26 11:00 | 363 | 353
2019-12-26 11:30 | 345 | 334
2019-12-26 12:00 | 336 | 326
2019-12-26 12:30 | 337 | 327
2019-12-26 13:00 | 362 | 353
2019-12-26 13:30 | 372 | 363
2019-12-26 14:00 | 377 | 370
2019-12-26 14:30 | 383 | 375
2019-12-26 15:00 | 401 | 394
2019-12-26 15:30 | 412 | 405
2019-12-26 16:00 | 426 | 421
2019-12-26 16:30 | 447 | 442
2019-12-26 17:00 | 473 | 467
2019-12-26 17:30 | 486 | 479
2019-12-26 18:00 | 475 | 467
2019-12-26 18:30 | 474 | 465
2019-12-26 19:00 | 478 | 468
2019-12-26 19:30 | 484 | 476
2019-12-26 20:00 | 484 | 476
2019-12-26 20:30 | 481 | 471
2019-12-26 21:00 | 473 | 462
2019-12-26 21:30 | 467 | 454
2019-12-26 22:00 | 465 | 450
2019-12-26 22:30 | 440 | 428
2019-12-26 23:00 | 417 | 405
2019-12-26 23:30 | 405 | 389
2019-12-27 | 391 | 372
2019-12-27 00:30 | 359 | 336
2019-12-27 01:00 | 348 | 323
2019-12-27 01:30 | 345 | 318
2019-12-27 02:00 | 340 | 313
2019-12-27 02:30 | 341 | 314
2019-12-27 03:00 | 340 | 311
2019-12-27 03:30 | 342 | 313
2019-12-27 04:00 | 343 | 314
2019-12-27 04:30 | 344 | 316
2019-12-27 05:00 | 349 | 320
2019-12-27 05:30 | 355 | 325
2019-12-27 06:00 | 360 | 333
2019-12-27 06:30 | 388 | 364
2019-12-27 07:00 | 392 | 382
2019-12-27 07:30 | 403 | 397
2019-12-27 08:00 | 408 | 404
2019-12-27 08:30 | 428 | 426
2019-12-27 09:00 | 438 | 436
2019-12-27 09:30 | 430 | 429
2019-12-27 10:00 | 425 | 424
2019-12-27 10:30 | 421 | 420
2019-12-27 11:00 | 407 | 405
2019-12-27 11:30 | 402 | 402
2019-12-27 12:00 | 401 | 401
2019-12-27 12:30 | 404 | 403
2019-12-27 13:00 | 410 | 409
2019-12-27 13:30 | 415 | 414
2019-12-27 14:00 | 417 | 416
2019-12-27 14:30 | 419 | 419
2019-12-27 15:00 | 432 | 431
2019-12-27 15:30 | 444 | 443
2019-12-27 16:00 | 462 | 462
2019-12-27 16:30 | 484 | 484
2019-12-27 17:00 | 502 | 501
2019-12-27 17:30 | 512 | 511
2019-12-27 18:00 | 517 | 515
2019-12-27 18:30 | 508 | 505
2019-12-27 19:00 | 516 | 513
2019-12-27 19:30 | 516 | 514
2019-12-27 20:00 | 513 | 512
2019-12-27 20:30 | 495 | 494
2019-12-27 21:00 | 471 | 470
2019-12-27 21:30 | 452 | 450
2019-12-27 22:00 | 437 | 435
2019-12-27 22:30 | 419 | 417
2019-12-27 23:00 | 398 | 395
2019-12-27 23:30 | 382 | 378
2019-12-28 | 374 | 369
2019-12-28 00:30 | 348 | 340
2019-12-28 01:00 | 326 | 318
2019-12-28 01:30 | 320 | 311
2019-12-28 02:00 | 313 | 302
2019-12-28 02:30 | 308 | 296
2019-12-28 03:00 | 310 | 298
2019-12-28 03:30 | 311 | 298
2019-12-28 04:00 | 316 | 303
2019-12-28 04:30 | 327 | 315
2019-12-28 05:00 | 325 | 314
2019-12-28 05:30 | 321 | 309
2019-12-28 06:00 | 319 | 308
2019-12-28 06:30 | 344 | 333
2019-12-28 07:00 | 361 | 351
2019-12-28 07:30 | 377 | 369
2019-12-28 08:00 | 392 | 386
2019-12-28 08:30 | 393 | 388
2019-12-28 09:00 | 402 | 398
2019-12-28 09:30 | 387 | 384
2019-12-28 10:00 | 378 | 375
2019-12-28 10:30 | 368 | 365
2019-12-28 11:00 | 350 | 347
2019-12-28 11:30 | 358 | 355
2019-12-28 12:00 | 357 | 354
2019-12-28 12:30 | 367 | 364
2019-12-28 13:00 | 375 | 372
2019-12-28 13:30 | 397 | 395
2019-12-28 14:00 | 389 | 387
2019-12-28 14:30 | 392 | 391
2019-12-28 15:00 | 419 | 417
2019-12-28 15:30 | 440 | 439
2019-12-28 16:00 | 466 | 465
2019-12-28 16:30 | 468 | 467
2019-12-28 17:00 | 491 | 491
2019-12-28 17:30 | 495 | 494
2019-12-28 18:00 | 507 | 507
2019-12-28 18:30 | 505 | 504
2019-12-28 19:00 | 508 | 508
2019-12-28 19:30 | 501 | 500
2019-12-28 20:00 | 498 | 497
2019-12-28 20:30 | 476 | 476
2019-12-28 21:00 | 454 | 453
2019-12-28 21:30 | 437 | 437
2019-12-28 22:00 | 427 | 426
2019-12-28 22:30 | 416 | 414
2019-12-28 23:00 | 398 | 396
2019-12-28 23:30 | 378 | 375
2019-12-29 | 361 | 356
2019-12-29 00:30 | 337 | 331
2019-12-29 01:00 | 327 | 321
2019-12-29 01:30 | 321 | 313
2019-12-29 02:00 | 312 | 304
2019-12-29 02:30 | 311 | 302
2019-12-29 03:00 | 309 | 299
2019-12-29 03:30 | 307 | 297
2019-12-29 04:00 | 301 | 291
2019-12-29 04:30 | 305 | 293
2019-12-29 05:00 | 310 | 298
2019-12-29 05:30 | 310 | 297
2019-12-29 06:00 | 305 | 292
2019-12-29 06:30 | 322 | 309
2019-12-29 07:00 | 329 | 317
2019-12-29 07:30 | 337 | 326
2019-12-29 08:00 | 349 | 340
2019-12-29 08:30 | 353 | 344
2019-12-29 09:00 | 350 | 341
2019-12-29 09:30 | 340 | 333
2019-12-29 10:00 | 336 | 329
2019-12-29 10:30 | 344 | 337
2019-12-29 11:00 | 354 | 347
2019-12-29 11:30 | 350 | 343
2019-12-29 12:00 | 360 | 354
2019-12-29 12:30 | 366 | 360
2019-12-29 13:00 | 366 | 360
2019-12-29 13:30 | 365 | 360
2019-12-29 14:00 | 374 | 370
2019-12-29 14:30 | 405 | 402
2019-12-29 15:00 | 433 | 431
2019-12-29 15:30 | 456 | 454
2019-12-29 16:00 | 473 | 472
2019-12-29 16:30 | 504 | 503
2019-12-29 17:00 | 523 | 522
2019-12-29 17:30 | 536 | 534
2019-12-29 18:00 | 544 | 542
2019-12-29 18:30 | 549 | 547
2019-12-29 19:00 | 536 | 534
2019-12-29 19:30 | 533 | 532
2019-12-29 20:00 | 523 | 522
2019-12-29 20:30 | 505 | 504
2019-12-29 21:00 | 492 | 491
2019-12-29 21:30 | 478 | 477
2019-12-29 22:00 | 470 | 468
2019-12-29 22:30 | 460 | 457
2019-12-29 23:00 | 440 | 437
2019-12-29 23:30 | 417 | 412
2019-12-30 | 397 | 391
2019-12-30 00:30 | 378 | 369
2019-12-30 01:00 | 367 | 357
2019-12-30 01:30 | 355 | 344
2019-12-30 02:00 | 340 | 329
2019-12-30 02:30 | 335 | 324
2019-12-30 03:00 | 330 | 318
2019-12-30 03:30 | 329 | 318
2019-12-30 04:00 | 328 | 317
2019-12-30 04:30 | 333 | 322
2019-12-30 05:00 | 335 | 323
2019-12-30 05:30 | 340 | 329
2019-12-30 06:00 | 344 | 334
2019-12-30 06:30 | 377 | 370
2019-12-30 07:00 | 404 | 399
2019-12-30 07:30 | 429 | 425
2019-12-30 08:00 | 443 | 440
2019-12-30 08:30 | 459 | 457
2019-12-30 09:00 | 457 | 456
2019-12-30 09:30 | 449 | 448
2019-12-30 10:00 | 458 | 457
2019-12-30 10:30 | 469 | 467
2019-12-30 11:00 | 472 | 470
2019-12-30 11:30 | 463 | 462
2019-12-30 12:00 | 454 | 452
2019-12-30 12:30 | 454 | 453
2019-12-30 13:00 | 459 | 458
2019-12-30 13:30 | 461 | 461
2019-12-30 14:00 | 468 | 468
2019-12-30 14:30 | 502 | 499
2019-12-30 15:00 | 539 | 532
2019-12-30 15:30 | 542 | 534
2019-12-30 16:00 | 559 | 552
2019-12-30 16:30 | 589 | 583
2019-12-30 17:00 | 626 | 621
2019-12-30 17:30 | 620 | 615
2019-12-30 18:00 | 622 | 616
2019-12-30 18:30 | 597 | 589
2019-12-30 19:00 | 573 | 566
2019-12-30 19:30 | 577 | 571
2019-12-30 20:00 | 564 | 558
2019-12-30 20:30 | 557 | 552
2019-12-30 21:00 | 536 | 531
2019-12-30 21:30 | 518 | 514
2019-12-30 22:00 | 490 | 489
2019-12-30 22:30 | 481 | 479
2019-12-30 23:00 | 460 | 458
2019-12-30 23:30 | 434 | 430
2019-12-31 | 399 | 395
2019-12-31 00:30 | 363 | 358
2019-12-31 01:00 | 343 | 336
2019-12-31 01:30 | 336 | 329
2019-12-31 02:00 | 331 | 323
2019-12-31 02:30 | 329 | 321
2019-12-31 03:00 | 328 | 320
2019-12-31 03:30 | 330 | 321
2019-12-31 04:00 | 333 | 324
2019-12-31 04:30 | 346 | 337
2019-12-31 05:00 | 349 | 339
2019-12-31 05:30 | 354 | 345
2019-12-31 06:00 | 355 | 346
2019-12-31 06:30 | 388 | 382
2019-12-31 07:00 | 417 | 414
2019-12-31 07:30 | 457 | 455
2019-12-31 08:00 | 477 | 475
2019-12-31 08:30 | 484 | 482
2019-12-31 09:00 | 489 | 487
2019-12-31 09:30 | 479 | 478
2019-12-31 10:00 | 472 | 472
2019-12-31 10:30 | 471 | 470
2019-12-31 11:00 | 474 | 474
2019-12-31 11:30 | 476 | 476
2019-12-31 12:00 | 470 | 470
2019-12-31 12:30 | 467 | 467
2019-12-31 13:00 | 467 | 466
2019-12-31 13:30 | 467 | 466
2019-12-31 14:00 | 479 | 478
2019-12-31 14:30 | 502 | 501
2019-12-31 15:00 | 539 | 537
2019-12-31 15:30 | 572 | 569
2019-12-31 16:00 | 597 | 593
2019-12-31 16:30 | 615 | 610
2019-12-31 17:00 | 626 | 620
2019-12-31 17:30 | 624 | 618
2019-12-31 18:00 | 595 | 588
2019-12-31 18:30 | 556 | 549
2019-12-31 19:00 | 544 | 537
2019-12-31 19:30 | 533 | 525
2019-12-31 20:00 | 528 | 520
2019-12-31 20:30 | 502 | 499
2019-12-31 21:00 | 483 | 482
2019-12-31 21:30 | 476 | 475
2019-12-31 22:00 | 463 | 461
2019-12-31 22:30 | 459 | 456
2019-12-31 23:00 | 447 | 444
2019-12-31 23:30 | 427 | 422
2020-01-01 | 394 | 390
2020-01-01 00:30 | 365 | 360
2020-01-01 01:00 | 351 | 346
2020-01-01 01:30 | 342 | 336
2020-01-01 02:00 | 337 | 331
2020-01-01 02:30 | 331 | 325
2020-01-01 03:00 | 319 | 313
2020-01-01 03:30 | 317 | 310
2020-01-01 04:00 | 318 | 310
2020-01-01 04:30 | 323 | 316
2020-01-01 05:00 | 327 | 317
2020-01-01 05:30 | 324 | 312
2020-01-01 06:00 | 318 | 307
2020-01-01 06:30 | 334 | 326
2020-01-01 07:00 | 356 | 349
2020-01-01 07:30 | 389 | 383
2020-01-01 08:00 | 397 | 393
2020-01-01 08:30 | 404 | 400
2020-01-01 09:00 | 393 | 389
2020-01-01 09:30 | 394 | 391
2020-01-01 10:00 | 385 | 383
2020-01-01 10:30 | 375 | 373
2020-01-01 11:00 | 375 | 373
2020-01-01 11:30 | 374 | 372
2020-01-01 12:00 | 379 | 378
2020-01-01 12:30 | 410 | 408
2020-01-01 13:00 | 417 | 416
2020-01-01 13:30 | 426 | 426
2020-01-01 14:00 | 436 | 436
2020-01-01 14:30 | 452 | 451
2020-01-01 15:00 | 474 | 474
2020-01-01 15:30 | 496 | 496
2020-01-01 16:00 | 518 | 516
2020-01-01 16:30 | 542 | 538
2020-01-01 17:00 | 566 | 563
2020-01-01 17:30 | 577 | 574
2020-01-01 18:00 | 575 | 572
2020-01-01 18:30 | 571 | 567
2020-01-01 19:00 | 568 | 565
2020-01-01 19:30 | 565 | 562
2020-01-01 20:00 | 557 | 554
2020-01-01 20:30 | 533 | 530
2020-01-01 21:00 | 505 | 504
2020-01-01 21:30 | 489 | 488
2020-01-01 22:00 | 475 | 473
2020-01-01 22:30 | 457 | 456
2020-01-01 23:00 | 443 | 442
2020-01-01 23:30 | 409 | 409
2020-01-02 | 383 | 382
2020-01-02 00:30 | 355 | 353
2020-01-02 01:00 | 342 | 340
2020-01-02 01:30 | 333 | 330
2020-01-02 02:00 | 322 | 319
2020-01-02 02:30 | 316 | 312
2020-01-02 03:00 | 314 | 310
2020-01-02 03:30 | 313 | 309
2020-01-02 04:00 | 311 | 307
2020-01-02 04:30 | 317 | 313
2020-01-02 05:00 | 327 | 323
2020-01-02 05:30 | 331 | 327
2020-01-02 06:00 | 337 | 333
2020-01-02 06:30 | 374 | 373
2020-01-02 07:00 | 411 | 409
2020-01-02 07:30 | 446 | 446
2020-01-02 08:00 | 472 | 472
2020-01-02 08:30 | 488 | 488
2020-01-02 09:00 | 494 | 493
2020-01-02 09:30 | 501 | 500
2020-01-02 10:00 | 502 | 500
2020-01-02 10:30 | 503 | 501
2020-01-02 11:00 | 511 | 508
2020-01-02 11:30 | 515 | 512
2020-01-02 12:00 | 517 | 515
2020-01-02 12:30 | 517 | 515
2020-01-02 13:00 | 527 | 525
2020-01-02 13:30 | 539 | 536
2020-01-02 14:00 | 547 | 544
2020-01-02 14:30 | 561 | 558
2020-01-02 15:00 | 595 | 591
2020-01-02 15:30 | 616 | 613
2020-01-02 16:00 | 628 | 626
2020-01-02 16:30 | 640 | 639
2020-01-02 17:00 | 665 | 662
2020-01-02 17:30 | 661 | 656
2020-01-02 18:00 | 646 | 641
2020-01-02 18:30 | 619 | 612
2020-01-02 19:00 | 611 | 602
2020-01-02 19:30 | 600 | 592
2020-01-02 20:00 | 589 | 582
2020-01-02 20:30 | 559 | 555
2020-01-02 21:00 | 525 | 522
2020-01-02 21:30 | 499 | 497
2020-01-02 22:00 | 477 | 474
2020-01-02 22:30 | 464 | 463
2020-01-02 23:00 | 445 | 444
2020-01-02 23:30 | 430 | 426
2020-01-03 | 402 | 399
2020-01-03 00:30 | 369 | 366
2020-01-03 01:00 | 349 | 346
2020-01-03 01:30 | 332 | 328
2020-01-03 02:00 | 322 | 318
2020-01-03 02:30 | 318 | 313
2020-01-03 03:00 | 311 | 306
2020-01-03 03:30 | 309 | 305
2020-01-03 04:00 | 308 | 303
2020-01-03 04:30 | 307 | 303
2020-01-03 05:00 | 309 | 303
2020-01-03 05:30 | 318 | 311
2020-01-03 06:00 | 327 | 322
2020-01-03 06:30 | 359 | 357
2020-01-03 07:00 | 389 | 389
2020-01-03 07:30 | 422 | 421
2020-01-03 08:00 | 444 | 444
2020-01-03 08:30 | 454 | 454
2020-01-03 09:00 | 448 | 447
2020-01-03 09:30 | 444 | 444
2020-01-03 10:00 | 439 | 438
2020-01-03 10:30 | 452 | 451
2020-01-03 11:00 | 462 | 461
2020-01-03 11:30 | 469 | 469
2020-01-03 12:00 | 482 | 481
2020-01-03 12:30 | 497 | 494
2020-01-03 13:00 | 507 | 504
2020-01-03 13:30 | 516 | 514
2020-01-03 14:00 | 533 | 530
2020-01-03 14:30 | 551 | 549
2020-01-03 15:00 | 569 | 568
2020-01-03 15:30 | 579 | 579
2020-01-03 16:00 | 599 | 598
2020-01-03 16:30 | 634 | 633
2020-01-03 17:00 | 660 | 657
2020-01-03 17:30 | 649 | 646
2020-01-03 18:00 | 639 | 636
2020-01-03 18:30 | 606 | 603
2020-01-03 19:00 | 594 | 593
2020-01-03 19:30 | 584 | 584
2020-01-03 20:00 | 577 | 576
2020-01-03 20:30 | 547 | 545
2020-01-03 21:00 | 516 | 515
2020-01-03 21:30 | 484 | 484
2020-01-03 22:00 | 469 | 469
2020-01-03 22:30 | 452 | 451
2020-01-03 23:00 | 433 | 432
2020-01-03 23:30 | 404 | 403
2020-01-04 | 386 | 385
2020-01-04 00:30 | 355 | 352
2020-01-04 01:00 | 338 | 335
2020-01-04 01:30 | 331 | 328
2020-01-04 02:00 | 325 | 320
2020-01-04 02:30 | 313 | 309
2020-01-04 03:00 | 306 | 301
2020-01-04 03:30 | 305 | 300
2020-01-04 04:00 | 302 | 297
2020-01-04 04:30 | 301 | 296
2020-01-04 05:00 | 305 | 299
2020-01-04 05:30 | 307 | 299
2020-01-04 06:00 | 303 | 295
2020-01-04 06:30 | 319 | 311
2020-01-04 07:00 | 334 | 328
2020-01-04 07:30 | 347 | 342
2020-01-04 08:00 | 362 | 359
2020-01-04 08:30 | 373 | 372
2020-01-04 09:00 | 359 | 359
2020-01-04 09:30 | 361 | 360
2020-01-04 10:00 | 373 | 373
2020-01-04 10:30 | 387 | 386
2020-01-04 11:00 | 400 | 399
2020-01-04 11:30 | 424 | 423
2020-01-04 12:00 | 433 | 433
2020-01-04 12:30 | 437 | 436
2020-01-04 13:00 | 451 | 451
2020-01-04 13:30 | 465 | 464
2020-01-04 14:00 | 483 | 482
2020-01-04 14:30 | 507 | 507
2020-01-04 15:00 | 535 | 535
2020-01-04 15:30 | 567 | 566
2020-01-04 16:00 | 608 | 605
2020-01-04 16:30 | 632 | 630
2020-01-04 17:00 | 654 | 652
2020-01-04 17:30 | 643 | 641
2020-01-04 18:00 | 634 | 631
2020-01-04 18:30 | 598 | 596
2020-01-04 19:00 | 596 | 596
2020-01-04 19:30 | 596 | 596
2020-01-04 20:00 | 586 | 586
2020-01-04 20:30 | 574 | 574
2020-01-04 21:00 | 531 | 531
2020-01-04 21:30 | 489 | 489
2020-01-04 22:00 | 463 | 463
2020-01-04 22:30 | 448 | 448
2020-01-04 23:00 | 434 | 434
2020-01-04 23:30 | 418 | 417
2020-01-05 | 393 | 391
2020-01-05 00:30 | 366 | 362
2020-01-05 01:00 | 356 | 352
2020-01-05 01:30 | 341 | 337
2020-01-05 02:00 | 339 | 333
2020-01-05 02:30 | 346 | 340
2020-01-05 03:00 | 342 | 335
2020-01-05 03:30 | 326 | 318
2020-01-05 04:00 | 318 | 310
2020-01-05 04:30 | 321 | 313
2020-01-05 05:00 | 321 | 311
2020-01-05 05:30 | 315 | 303
2020-01-05 06:00 | 308 | 296
2020-01-05 06:30 | 325 | 314
2020-01-05 07:00 | 342 | 332
2020-01-05 07:30 | 367 | 359
2020-01-05 08:00 | 378 | 371
2020-01-05 08:30 | 385 | 379
2020-01-05 09:00 | 403 | 399
2020-01-05 09:30 | 407 | 405
2020-01-05 10:00 | 411 | 408
2020-01-05 10:30 | 403 | 402
2020-01-05 11:00 | 399 | 398
2020-01-05 11:30 | 425 | 424
2020-01-05 12:00 | 439 | 438
2020-01-05 12:30 | 448 | 447
2020-01-05 13:00 | 469 | 469
2020-01-05 13:30 | 481 | 480
2020-01-05 14:00 | 484 | 483
2020-01-05 14:30 | 489 | 489
2020-01-05 15:00 | 523 | 522
2020-01-05 15:30 | 541 | 541
2020-01-05 16:00 | 540 | 540
2020-01-05 16:30 | 547 | 547
2020-01-05 17:00 | 567 | 564
2020-01-05 17:30 | 565 | 559
2020-01-05 18:00 | 556 | 550
2020-01-05 18:30 | 558 | 550
2020-01-05 19:00 | 556 | 547
2020-01-05 19:30 | 546 | 539
2020-01-05 20:00 | 534 | 528
2020-01-05 20:30 | 517 | 509
2020-01-05 21:00 | 489 | 478
2020-01-05 21:30 | 470 | 456
2020-01-05 22:00 | 453 | 447
2020-01-05 22:30 | 426 | 418
2020-01-05 23:00 | 409 | 401
2020-01-05 23:30 | 396 | 386
2020-01-06 | 381 | 370
2020-01-06 00:30 | 354 | 347
2020-01-06 01:00 | 346 | 337
2020-01-06 01:30 | 341 | 333
2020-01-06 02:00 | 340 | 333
2020-01-06 02:30 | 338 | 331
2020-01-06 03:00 | 335 | 328
2020-01-06 03:30 | 335 | 327
2020-01-06 04:00 | 334 | 327
2020-01-06 04:30 | 335 | 328
2020-01-06 05:00 | 339 | 332
2020-01-06 05:30 | 351 | 345
2020-01-06 06:00 | 360 | 355
2020-01-06 06:30 | 402 | 401
2020-01-06 07:00 | 441 | 438
2020-01-06 07:30 | 476 | 474
2020-01-06 08:00 | 496 | 493
2020-01-06 08:30 | 510 | 508
2020-01-06 09:00 | 516 | 515
2020-01-06 09:30 | 499 | 498
2020-01-06 10:00 | 500 | 499
2020-01-06 10:30 | 513 | 512
2020-01-06 11:00 | 524 | 524
2020-01-06 11:30 | 526 | 525
2020-01-06 12:00 | 542 | 541
2020-01-06 12:30 | 555 | 554
2020-01-06 13:00 | 569 | 568
2020-01-06 13:30 | 568 | 567
2020-01-06 14:00 | 565 | 564
2020-01-06 14:30 | 571 | 570
2020-01-06 15:00 | 603 | 602
2020-01-06 15:30 | 631 | 631
2020-01-06 16:00 | 637 | 637
2020-01-06 16:30 | 655 | 655
2020-01-06 17:00 | 650 | 650
2020-01-06 17:30 | 639 | 638
2020-01-06 18:00 | 617 | 616
2020-01-06 18:30 | 595 | 592
2020-01-06 19:00 | 599 | 596
2020-01-06 19:30 | 598 | 595
2020-01-06 20:00 | 588 | 584
2020-01-06 20:30 | 565 | 562
2020-01-06 21:00 | 538 | 535
2020-01-06 21:30 | 528 | 524
2020-01-06 22:00 | 510 | 507
2020-01-06 22:30 | 482 | 480
2020-01-06 23:00 | 460 | 456
2020-01-06 23:30 | 436 | 431
2020-01-07 | 411 | 403
2020-01-07 00:30 | 377 | 372
2020-01-07 01:00 | 359 | 358
2020-01-07 01:30 | 350 | 349
2020-01-07 02:00 | 343 | 341
2020-01-07 02:30 | 341 | 339
2020-01-07 03:00 | 335 | 333
2020-01-07 03:30 | 337 | 335
2020-01-07 04:00 | 333 | 331
2020-01-07 04:30 | 342 | 340
2020-01-07 05:00 | 353 | 351
2020-01-07 05:30 | 362 | 361
2020-01-07 06:00 | 375 | 375
2020-01-07 06:30 | 417 | 416
2020-01-07 07:00 | 452 | 451
2020-01-07 07:30 | 489 | 489
2020-01-07 08:00 | 515 | 514
2020-01-07 08:30 | 527 | 526
2020-01-07 09:00 | 526 | 525
2020-01-07 09:30 | 518 | 516
2020-01-07 10:00 | 513 | 511
2020-01-07 10:30 | 540 | 538
2020-01-07 11:00 | 542 | 541
2020-01-07 11:30 | 543 | 541
2020-01-07 12:00 | 539 | 537
2020-01-07 12:30 | 538 | 536
2020-01-07 13:00 | 540 | 538
2020-01-07 13:30 | 543 | 540
2020-01-07 14:00 | 551 | 548
2020-01-07 14:30 | 567 | 565
2020-01-07 15:00 | 587 | 585
2020-01-07 15:30 | 602 | 600
2020-01-07 16:00 | 612 | 611
2020-01-07 16:30 | 640 | 639
2020-01-07 17:00 | 658 | 657
2020-01-07 17:30 | 661 | 658
2020-01-07 18:00 | 648 | 644
2020-01-07 18:30 | 634 | 630
2020-01-07 19:00 | 629 | 626
2020-01-07 19:30 | 622 | 619
2020-01-07 20:00 | 616 | 613
2020-01-07 20:30 | 587 | 583
2020-01-07 21:00 | 546 | 545
2020-01-07 21:30 | 523 | 522
2020-01-07 22:00 | 506 | 505
2020-01-07 22:30 | 476 | 475
2020-01-07 23:00 | 453 | 452
2020-01-07 23:30 | 426 | 422
2020-01-08 | 405 | 400
2020-01-08 00:30 | 372 | 367
2020-01-08 01:00 | 359 | 353
2020-01-08 01:30 | 347 | 343
2020-01-08 02:00 | 344 | 339
2020-01-08 02:30 | 339 | 334
2020-01-08 03:00 | 334 | 328
2020-01-08 03:30 | 333 | 328
2020-01-08 04:00 | 331 | 325
2020-01-08 04:30 | 340 | 335
2020-01-08 05:00 | 349 | 345
2020-01-08 05:30 | 364 | 360
2020-01-08 06:00 | 373 | 370
2020-01-08 06:30 | 416 | 414
2020-01-08 07:00 | 450 | 449
2020-01-08 07:30 | 480 | 479
2020-01-08 08:00 | 495 | 493
2020-01-08 08:30 | 511 | 510
2020-01-08 09:00 | 507 | 505
2020-01-08 09:30 | 507 | 505
2020-01-08 10:00 | 509 | 508
2020-01-08 10:30 | 510 | 509
2020-01-08 11:00 | 511 | 510
2020-01-08 11:30 | 520 | 519
2020-01-08 12:00 | 521 | 518
2020-01-08 12:30 | 538 | 535
2020-01-08 13:00 | 551 | 548
2020-01-08 13:30 | 559 | 558
2020-01-08 14:00 | 587 | 580
2020-01-08 14:30 | 606 | 598
2020-01-08 15:00 | 633 | 625
2020-01-08 15:30 | 654 | 649
2020-01-08 16:00 | 672 | 667
2020-01-08 16:30 | 681 | 676
2020-01-08 17:00 | 687 | 683
2020-01-08 17:30 | 681 | 677
2020-01-08 18:00 | 659 | 653
2020-01-08 18:30 | 645 | 633
2020-01-08 19:00 | 636 | 628
2020-01-08 19:30 | 619 | 613
2020-01-08 20:00 | 608 | 602
2020-01-08 20:30 | 578 | 571
2020-01-08 21:00 | 553 | 547
2020-01-08 21:30 | 531 | 526
2020-01-08 22:00 | 509 | 503
2020-01-08 22:30 | 482 | 477
2020-01-08 23:00 | 463 | 456
2020-01-08 23:30 | 440 | 430
2020-01-09 | 412 | 401
2020-01-09 00:30 | 381 | 369
2020-01-09 01:00 | 372 | 358
2020-01-09 01:30 | 371 | 357
2020-01-09 02:00 | 364 | 349
2020-01-09 02:30 | 358 | 343
2020-01-09 03:00 | 349 | 334
2020-01-09 03:30 | 348 | 332
2020-01-09 04:00 | 347 | 332
2020-01-09 04:30 | 363 | 348
2020-01-09 05:00 | 373 | 358
2020-01-09 05:30 | 380 | 366
2020-01-09 06:00 | 379 | 367
2020-01-09 06:30 | 410 | 402
2020-01-09 07:00 | 439 | 431
2020-01-09 07:30 | 484 | 475
2020-01-09 08:00 | 505 | 495
2020-01-09 08:30 | 518 | 509
2020-01-09 09:00 | 520 | 512
2020-01-09 09:30 | 513 | 507
2020-01-09 10:00 | 512 | 506
2020-01-09 10:30 | 508 | 502
2020-01-09 11:00 | 517 | 512
2020-01-09 11:30 | 527 | 523
2020-01-09 12:00 | 534 | 530
2020-01-09 12:30 | 549 | 538
2020-01-09 13:00 | 556 | 545
2020-01-09 13:30 | 567 | 558
2020-01-09 14:00 | 578 | 568
2020-01-09 14:30 | 601 | 591
2020-01-09 15:00 | 632 | 623
2020-01-09 15:30 | 654 | 646
2020-01-09 16:00 | 673 | 667
2020-01-09 16:30 | 703 | 694
2020-01-09 17:00 | 700 | 690
2020-01-09 17:30 | 688 | 676
2020-01-09 18:00 | 668 | 650
2020-01-09 18:30 | 639 | 626
2020-01-09 19:00 | 639 | 629
2020-01-09 19:30 | 629 | 620
2020-01-09 20:00 | 617 | 606
2020-01-09 20:30 | 599 | 587
2020-01-09 21:00 | 576 | 563
2020-01-09 21:30 | 555 | 540
2020-01-09 22:00 | 529 | 510
2020-01-09 22:30 | 512 | 495
2020-01-09 23:00 | 481 | 471
2020-01-09 23:30 | 456 | 448
2020-01-10 | 427 | 419
2020-01-10 00:30 | 397 | 386
2020-01-10 01:00 | 385 | 374
2020-01-10 01:30 | 379 | 366
2020-01-10 02:00 | 374 | 361
2020-01-10 02:30 | 370 | 356
2020-01-10 03:00 | 362 | 348
2020-01-10 03:30 | 364 | 349
2020-01-10 04:00 | 353 | 338
2020-01-10 04:30 | 359 | 345
2020-01-10 05:00 | 365 | 351
2020-01-10 05:30 | 376 | 363
2020-01-10 06:00 | 394 | 383
2020-01-10 06:30 | 425 | 420
2020-01-10 07:00 | 449 | 448
2020-01-10 07:30 | 487 | 487
2020-01-10 08:00 | 519 | 519
2020-01-10 08:30 | 529 | 529
2020-01-10 09:00 | 525 | 525
2020-01-10 09:30 | 522 | 522
2020-01-10 10:00 | 523 | 523
2020-01-10 10:30 | 530 | 530
2020-01-10 11:00 | 536 | 536
2020-01-10 11:30 | 543 | 543
2020-01-10 12:00 | 557 | 555
2020-01-10 12:30 | 558 | 556
2020-01-10 13:00 | 570 | 569
2020-01-10 13:30 | 589 | 588
2020-01-10 14:00 | 611 | 608
2020-01-10 14:30 | 636 | 630
2020-01-10 15:00 | 667 | 662
2020-01-10 15:30 | 690 | 686
2020-01-10 16:00 | 706 | 702
2020-01-10 16:30 | 726 | 721
2020-01-10 17:00 | 730 | 724
2020-01-10 17:30 | 723 | 715
2020-01-10 18:00 | 709 | 702
2020-01-10 18:30 | 669 | 664
2020-01-10 19:00 | 656 | 655
2020-01-10 19:30 | 648 | 647
2020-01-10 20:00 | 646 | 645
2020-01-10 20:30 | 619 | 617
2020-01-10 21:00 | 582 | 578
2020-01-10 21:30 | 560 | 556
2020-01-10 22:00 | 537 | 533
2020-01-10 22:30 | 519 | 516
2020-01-10 23:00 | 506 | 502
2020-01-10 23:30 | 484 | 479
2020-01-11 | 450 | 446
2020-01-11 00:30 | 403 | 401
2020-01-11 01:00 | 382 | 381
2020-01-11 01:30 | 376 | 374
2020-01-11 02:00 | 374 | 372
2020-01-11 02:30 | 366 | 363
2020-01-11 03:00 | 359 | 356
2020-01-11 03:30 | 356 | 352
2020-01-11 04:00 | 354 | 351
2020-01-11 04:30 | 352 | 348
2020-01-11 05:00 | 353 | 349
2020-01-11 05:30 | 355 | 350
2020-01-11 06:00 | 353 | 348
2020-01-11 06:30 | 372 | 368
2020-01-11 07:00 | 390 | 387
2020-01-11 07:30 | 417 | 415
2020-01-11 08:00 | 433 | 432
2020-01-11 08:30 | 445 | 445
2020-01-11 09:00 | 462 | 461
2020-01-11 09:30 | 470 | 468
2020-01-11 10:00 | 472 | 470
2020-01-11 10:30 | 482 | 480
2020-01-11 11:00 | 499 | 498
2020-01-11 11:30 | 498 | 497
2020-01-11 12:00 | 526 | 526
2020-01-11 12:30 | 576 | 575
2020-01-11 13:00 | 601 | 601
2020-01-11 13:30 | 590 | 590
2020-01-11 14:00 | 576 | 576
2020-01-11 14:30 | 570 | 569
2020-01-11 15:00 | 580 | 580
2020-01-11 15:30 | 583 | 582
2020-01-11 16:00 | 592 | 591
2020-01-11 16:30 | 584 | 583
2020-01-11 17:00 | 586 | 585
2020-01-11 17:30 | 583 | 582
2020-01-11 18:00 | 574 | 572
2020-01-11 18:30 | 569 | 567
2020-01-11 19:00 | 561 | 560
2020-01-11 19:30 | 544 | 543
2020-01-11 20:00 | 530 | 529
2020-01-11 20:30 | 512 | 511
2020-01-11 21:00 | 490 | 488
2020-01-11 21:30 | 469 | 467
2020-01-11 22:00 | 456 | 455
2020-01-11 22:30 | 442 | 441
2020-01-11 23:00 | 433 | 433
2020-01-11 23:30 | 417 | 417
2020-01-12 | 398 | 397
2020-01-12 00:30 | 374 | 372
2020-01-12 01:00 | 367 | 364
2020-01-12 01:30 | 361 | 357
2020-01-12 02:00 | 355 | 351
2020-01-12 02:30 | 349 | 344
2020-01-12 03:00 | 340 | 335
2020-01-12 03:30 | 338 | 333
2020-01-12 04:00 | 337 | 331
2020-01-12 04:30 | 331 | 325
2020-01-12 05:00 | 336 | 329
2020-01-12 05:30 | 336 | 329
2020-01-12 06:00 | 341 | 333
2020-01-12 06:30 | 366 | 359
2020-01-12 07:00 | 384 | 378
2020-01-12 07:30 | 394 | 388
2020-01-12 08:00 | 402 | 397
2020-01-12 08:30 | 396 | 392
2020-01-12 09:00 | 396 | 393
2020-01-12 09:30 | 389 | 387
2020-01-12 10:00 | 380 | 378
2020-01-12 10:30 | 384 | 382
2020-01-12 11:00 | 396 | 394
2020-01-12 11:30 | 414 | 414
2020-01-12 12:00 | 426 | 426
2020-01-12 12:30 | 416 | 415
2020-01-12 13:00 | 422 | 422
2020-01-12 13:30 | 409 | 409
2020-01-12 14:00 | 417 | 417
2020-01-12 14:30 | 423 | 423
2020-01-12 15:00 | 423 | 422
2020-01-12 15:30 | 418 | 416
2020-01-12 16:00 | 431 | 430
2020-01-12 16:30 | 464 | 463
2020-01-12 17:00 | 464 | 463
2020-01-12 17:30 | 449 | 448
2020-01-12 18:00 | 460 | 459
2020-01-12 18:30 | 466 | 465
2020-01-12 19:00 | 463 | 463
2020-01-12 19:30 | 456 | 455
2020-01-12 20:00 | 457 | 456
2020-01-12 20:30 | 452 | 451
2020-01-12 21:00 | 437 | 436
2020-01-12 21:30 | 425 | 424
2020-01-12 22:00 | 421 | 420
2020-01-12 22:30 | 406 | 404
2020-01-12 23:00 | 390 | 387
2020-01-12 23:30 | 376 | 372
2020-01-13 | 362 | 356
2020-01-13 00:30 | 339 | 331
2020-01-13 01:00 | 333 | 325
2020-01-13 01:30 | 327 | 318
2020-01-13 02:00 | 325 | 317
2020-01-13 02:30 | 312 | 303
2020-01-13 03:00 | 314 | 306
2020-01-13 03:30 | 315 | 307
2020-01-13 04:00 | 318 | 310
2020-01-13 04:30 | 324 | 316
2020-01-13 05:00 | 339 | 332
2020-01-13 05:30 | 356 | 350
2020-01-13 06:00 | 367 | 362
2020-01-13 06:30 | 396 | 394
2020-01-13 07:00 | 427 | 426
2020-01-13 07:30 | 473 | 470
2020-01-13 08:00 | 506 | 498
2020-01-13 08:30 | 520 | 509
2020-01-13 09:00 | 518 | 508
2020-01-13 09:30 | 511 | 503
2020-01-13 10:00 | 515 | 509
2020-01-13 10:30 | 522 | 516
2020-01-13 11:00 | 521 | 514
2020-01-13 11:30 | 514 | 506
2020-01-13 12:00 | 516 | 508
2020-01-13 12:30 | 517 | 510
2020-01-13 13:00 | 507 | 499
2020-01-13 13:30 | 510 | 504
2020-01-13 14:00 | 504 | 497
2020-01-13 14:30 | 512 | 506
2020-01-13 15:00 | 543 | 537
2020-01-13 15:30 | 543 | 536
2020-01-13 16:00 | 554 | 548
2020-01-13 16:30 | 552 | 547
2020-01-13 17:00 | 556 | 550
2020-01-13 17:30 | 553 | 546
2020-01-13 18:00 | 545 | 537
2020-01-13 18:30 | 523 | 516
2020-01-13 19:00 | 525 | 519
2020-01-13 19:30 | 520 | 515
2020-01-13 20:00 | 516 | 510
2020-01-13 20:30 | 508 | 498
2020-01-13 21:00 | 490 | 479
2020-01-13 21:30 | 467 | 461
2020-01-13 22:00 | 440 | 439
2020-01-13 22:30 | 421 | 420
2020-01-13 23:00 | 412 | 411
2020-01-13 23:30 | 398 | 395
2020-01-14 | 385 | 381
2020-01-14 00:30 | 354 | 349
2020-01-14 01:00 | 345 | 340
2020-01-14 01:30 | 344 | 338
2020-01-14 02:00 | 340 | 333
2020-01-14 02:30 | 338 | 331
2020-01-14 03:00 | 332 | 325
2020-01-14 03:30 | 335 | 328
2020-01-14 04:00 | 338 | 331
2020-01-14 04:30 | 345 | 338
2020-01-14 05:00 | 358 | 352
2020-01-14 05:30 | 364 | 358
2020-01-14 06:00 | 371 | 367
2020-01-14 06:30 | 410 | 409
2020-01-14 07:00 | 451 | 450
2020-01-14 07:30 | 494 | 493
2020-01-14 08:00 | 524 | 523
2020-01-14 08:30 | 535 | 529
2020-01-14 09:00 | 532 | 525
2020-01-14 09:30 | 520 | 514
2020-01-14 10:00 | 516 | 510
2020-01-14 10:30 | 509 | 503
2020-01-14 11:00 | 524 | 519
2020-01-14 11:30 | 492 | 485
2020-01-14 12:00 | 513 | 508
2020-01-14 12:30 | 535 | 529
2020-01-14 13:00 | 539 | 534
2020-01-14 13:30 | 536 | 531
2020-01-14 14:00 | 531 | 526
2020-01-14 14:30 | 533 | 528
2020-01-14 15:00 | 572 | 568
2020-01-14 15:30 | 577 | 573
2020-01-14 16:00 | 594 | 590
2020-01-14 16:30 | 605 | 602
2020-01-14 17:00 | 611 | 606
2020-01-14 17:30 | 599 | 593
2020-01-14 18:00 | 587 | 580
2020-01-14 18:30 | 571 | 561
2020-01-14 19:00 | 558 | 549
2020-01-14 19:30 | 567 | 559
2020-01-14 20:00 | 554 | 546
2020-01-14 20:30 | 524 | 523
2020-01-14 21:00 | 511 | 511
2020-01-14 21:30 | 500 | 499
2020-01-14 22:00 | 475 | 473
2020-01-14 22:30 | 459 | 458
2020-01-14 23:00 | 450 | 449
2020-01-14 23:30 | 426 | 424
2020-01-15 | 403 | 400
2020-01-15 00:30 | 380 | 375
2020-01-15 01:00 | 367 | 360
2020-01-15 01:30 | 364 | 357
2020-01-15 02:00 | 366 | 359
2020-01-15 02:30 | 360 | 352
2020-01-15 03:00 | 350 | 344
2020-01-15 03:30 | 347 | 341
2020-01-15 04:00 | 347 | 341
2020-01-15 04:30 | 355 | 350
2020-01-15 05:00 | 365 | 360
2020-01-15 05:30 | 374 | 369
2020-01-15 06:00 | 385 | 382
2020-01-15 06:30 | 425 | 425
2020-01-15 07:00 | 464 | 464
2020-01-15 07:30 | 511 | 510
2020-01-15 08:00 | 535 | 533
2020-01-15 08:30 | 589 | 589
2020-01-15 09:00 | 589 | 588
2020-01-15 09:30 | 571 | 570
2020-01-15 10:00 | 565 | 565
2020-01-15 10:30 | 577 | 576
2020-01-15 11:00 | 584 | 583
2020-01-15 11:30 | 565 | 564
2020-01-15 12:00 | 567 | 567
2020-01-15 12:30 | 565 | 565
2020-01-15 13:00 | 580 | 580
2020-01-15 13:30 | 531 | 530
2020-01-15 14:00 | 523 | 523
2020-01-15 14:30 | 536 | 535
2020-01-15 15:00 | 549 | 548
2020-01-15 15:30 | 565 | 564
2020-01-15 16:00 | 580 | 580
2020-01-15 16:30 | 585 | 584
2020-01-15 17:00 | 605 | 605
2020-01-15 17:30 | 626 | 624
2020-01-15 18:00 | 612 | 610
2020-01-15 18:30 | 595 | 591
2020-01-15 19:00 | 591 | 589
2020-01-15 19:30 | 597 | 595
2020-01-15 20:00 | 592 | 590
2020-01-15 20:30 | 563 | 561
2020-01-15 21:00 | 539 | 538
2020-01-15 21:30 | 515 | 513
2020-01-15 22:00 | 495 | 493
2020-01-15 22:30 | 473 | 471
2020-01-15 23:00 | 455 | 454
2020-01-15 23:30 | 431 | 431
2020-01-16 | 407 | 407
2020-01-16 00:30 | 375 | 374
2020-01-16 01:00 | 361 | 360
2020-01-16 01:30 | 361 | 360
2020-01-16 02:00 | 353 | 352
2020-01-16 02:30 | 343 | 341
2020-01-16 03:00 | 333 | 331
2020-01-16 03:30 | 334 | 332
2020-01-16 04:00 | 333 | 331
2020-01-16 04:30 | 336 | 334
2020-01-16 05:00 | 346 | 344
2020-01-16 05:30 | 363 | 361
2020-01-16 06:00 | 373 | 372
2020-01-16 06:30 | 417 | 417
2020-01-16 07:00 | 454 | 453
2020-01-16 07:30 | 496 | 495
2020-01-16 08:00 | 515 | 514
2020-01-16 08:30 | 551 | 550
2020-01-16 09:00 | 565 | 565
2020-01-16 09:30 | 576 | 575
2020-01-16 10:00 | 575 | 574
2020-01-16 10:30 | 588 | 586
2020-01-16 11:00 | 599 | 597
2020-01-16 11:30 | 603 | 601
2020-01-16 12:00 | 587 | 586
2020-01-16 12:30 | 578 | 577
2020-01-16 13:00 | 573 | 572
2020-01-16 13:30 | 579 | 578
2020-01-16 14:00 | 566 | 565
2020-01-16 14:30 | 578 | 576
2020-01-16 15:00 | 573 | 572
2020-01-16 15:30 | 578 | 578
2020-01-16 16:00 | 583 | 582
2020-01-16 16:30 | 605 | 604
2020-01-16 17:00 | 609 | 609
2020-01-16 17:30 | 603 | 603
2020-01-16 18:00 | 591 | 591
2020-01-16 18:30 | 584 | 583
2020-01-16 19:00 | 588 | 587
2020-01-16 19:30 | 581 | 581
2020-01-16 20:00 | 567 | 566
2020-01-16 20:30 | 543 | 542
2020-01-16 21:00 | 526 | 525
2020-01-16 21:30 | 501 | 501
2020-01-16 22:00 | 475 | 474
2020-01-16 22:30 | 460 | 459
2020-01-16 23:00 | 444 | 444
2020-01-16 23:30 | 425 | 424
2020-01-17 | 404 | 403
2020-01-17 00:30 | 373 | 372
2020-01-17 01:00 | 363 | 361
2020-01-17 01:30 | 359 | 357
2020-01-17 02:00 | 356 | 354
2020-01-17 02:30 | 349 | 347
2020-01-17 03:00 | 344 | 343
2020-01-17 03:30 | 343 | 341
2020-01-17 04:00 | 343 | 342
2020-01-17 04:30 | 347 | 345
2020-01-17 05:00 | 361 | 360
2020-01-17 05:30 | 370 | 369
2020-01-17 06:00 | 378 | 378
2020-01-17 06:30 | 415 | 414
2020-01-17 07:00 | 445 | 444
2020-01-17 07:30 | 481 | 479
2020-01-17 08:00 | 518 | 517
2020-01-17 08:30 | 536 | 533
2020-01-17 09:00 | 542 | 540
2020-01-17 09:30 | 541 | 538
2020-01-17 10:00 | 527 | 523
2020-01-17 10:30 | 529 | 526
2020-01-17 11:00 | 543 | 541
2020-01-17 11:30 | 544 | 543
2020-01-17 12:00 | 532 | 532
2020-01-17 12:30 | 566 | 564
2020-01-17 13:00 | 581 | 580
2020-01-17 13:30 | 540 | 539
2020-01-17 14:00 | 547 | 546
2020-01-17 14:30 | 557 | 556
2020-01-17 15:00 | 582 | 580
2020-01-17 15:30 | 584 | 584
2020-01-17 16:00 | 583 | 583
2020-01-17 16:30 | 589 | 589
2020-01-17 17:00 | 594 | 594
2020-01-17 17:30 | 584 | 584
2020-01-17 18:00 | 570 | 569
2020-01-17 18:30 | 555 | 551
2020-01-17 19:00 | 552 | 550
2020-01-17 19:30 | 551 | 548
2020-01-17 20:00 | 545 | 545
2020-01-17 20:30 | 535 | 534
2020-01-17 21:00 | 520 | 519
2020-01-17 21:30 | 508 | 507
2020-01-17 22:00 | 500 | 498
2020-01-17 22:30 | 479 | 479
2020-01-17 23:00 | 456 | 456
2020-01-17 23:30 | 441 | 440
2020-01-18 | 421 | 421
2020-01-18 00:30 | 391 | 390
2020-01-18 01:00 | 375 | 373
2020-01-18 01:30 | 356 | 353
2020-01-18 02:00 | 351 | 348
2020-01-18 02:30 | 342 | 337
2020-01-18 03:00 | 336 | 330
2020-01-18 03:30 | 342 | 336
2020-01-18 04:00 | 351 | 344
2020-01-18 04:30 | 351 | 344
2020-01-18 05:00 | 360 | 354
2020-01-18 05:30 | 370 | 364
2020-01-18 06:00 | 375 | 370
2020-01-18 06:30 | 397 | 393
2020-01-18 07:00 | 421 | 418
2020-01-18 07:30 | 462 | 461
2020-01-18 08:00 | 511 | 510
2020-01-18 08:30 | 522 | 518
2020-01-18 09:00 | 533 | 529
2020-01-18 09:30 | 515 | 508
2020-01-18 10:00 | 490 | 483
2020-01-18 10:30 | 479 | 472
2020-01-18 11:00 | 497 | 492
2020-01-18 11:30 | 494 | 489
2020-01-18 12:00 | 486 | 481
2020-01-18 12:30 | 493 | 488
2020-01-18 13:00 | 505 | 501
2020-01-18 13:30 | 500 | 497
2020-01-18 14:00 | 487 | 484
2020-01-18 14:30 | 465 | 461
2020-01-18 15:00 | 475 | 472
2020-01-18 15:30 | 486 | 483
2020-01-18 16:00 | 486 | 482
2020-01-18 16:30 | 483 | 480
2020-01-18 17:00 | 504 | 502
2020-01-18 17:30 | 505 | 500
2020-01-18 18:00 | 502 | 497
2020-01-18 18:30 | 486 | 481
2020-01-18 19:00 | 488 | 484
2020-01-18 19:30 | 488 | 484
2020-01-18 20:00 | 482 | 478
2020-01-18 20:30 | 474 | 470
2020-01-18 21:00 | 462 | 456
2020-01-18 21:30 | 458 | 450
2020-01-18 22:00 | 443 | 437
2020-01-18 22:30 | 435 | 430
2020-01-18 23:00 | 427 | 426
2020-01-18 23:30 | 417 | 415
2020-01-19 | 397 | 394
2020-01-19 00:30 | 367 | 363
2020-01-19 01:00 | 355 | 349
2020-01-19 01:30 | 354 | 347
2020-01-19 02:00 | 350 | 342
2020-01-19 02:30 | 344 | 335
2020-01-19 03:00 | 338 | 330
2020-01-19 03:30 | 333 | 325
2020-01-19 04:00 | 332 | 323
2020-01-19 04:30 | 337 | 327
2020-01-19 05:00 | 341 | 332
2020-01-19 05:30 | 347 | 337
2020-01-19 06:00 | 346 | 335
2020-01-19 06:30 | 366 | 356
2020-01-19 07:00 | 391 | 382
2020-01-19 07:30 | 425 | 418
2020-01-19 08:00 | 445 | 440
2020-01-19 08:30 | 443 | 438
2020-01-19 09:00 | 434 | 431
2020-01-19 09:30 | 441 | 439
2020-01-19 10:00 | 473 | 471
2020-01-19 10:30 | 478 | 475
2020-01-19 11:00 | 512 | 510
2020-01-19 11:30 | 492 | 491
2020-01-19 12:00 | 472 | 471
2020-01-19 12:30 | 494 | 488
2020-01-19 13:00 | 475 | 468
2020-01-19 13:30 | 461 | 453
2020-01-19 14:00 | 464 | 456
2020-01-19 14:30 | 507 | 502
2020-01-19 15:00 | 536 | 531
2020-01-19 15:30 | 542 | 535
2020-01-19 16:00 | 535 | 529
2020-01-19 16:30 | 568 | 563
2020-01-19 17:00 | 598 | 593
2020-01-19 17:30 | 581 | 575
2020-01-19 18:00 | 576 | 571
2020-01-19 18:30 | 574 | 569
2020-01-19 19:00 | 562 | 558
2020-01-19 19:30 | 570 | 565
2020-01-19 20:00 | 573 | 565
2020-01-19 20:30 | 555 | 550
2020-01-19 21:00 | 523 | 519
2020-01-19 21:30 | 512 | 511
2020-01-19 22:00 | 503 | 502
2020-01-19 22:30 | 494 | 494
2020-01-19 23:00 | 489 | 489
2020-01-19 23:30 | 473 | 472
2020-01-20 | 443 | 442
2020-01-20 00:30 | 412 | 410
2020-01-20 01:00 | 401 | 399
2020-01-20 01:30 | 385 | 383
2020-01-20 02:00 | 377 | 375
2020-01-20 02:30 | 369 | 366
2020-01-20 03:00 | 362 | 359
2020-01-20 03:30 | 365 | 362
2020-01-20 04:00 | 367 | 364
2020-01-20 04:30 | 373 | 370
2020-01-20 05:00 | 384 | 382
2020-01-20 05:30 | 401 | 396
2020-01-20 06:00 | 416 | 412
2020-01-20 06:30 | 459 | 457
2020-01-20 07:00 | 507 | 506
2020-01-20 07:30 | 543 | 542
2020-01-20 08:00 | 583 | 577
2020-01-20 08:30 | 600 | 594
2020-01-20 09:00 | 595 | 591
2020-01-20 09:30 | 601 | 597
2020-01-20 10:00 | 606 | 603
2020-01-20 10:30 | 626 | 621
2020-01-20 11:00 | 631 | 626
2020-01-20 11:30 | 636 | 632
2020-01-20 12:00 | 646 | 643
2020-01-20 12:30 | 661 | 658
2020-01-20 13:00 | 671 | 667
2020-01-20 13:30 | 705 | 699
2020-01-20 14:00 | 690 | 683
2020-01-20 14:30 | 720 | 710
2020-01-20 15:00 | 776 | 764
2020-01-20 15:30 | 787 | 772
2020-01-20 16:00 | 758 | 748
2020-01-20 16:30 | 718 | 712
2020-01-20 17:00 | 682 | 677
2020-01-20 17:30 | 658 | 657
2020-01-20 18:00 | 667 | 666
2020-01-20 18:30 | 648 | 645
2020-01-20 19:00 | 642 | 642
2020-01-20 19:30 | 644 | 644
2020-01-20 20:00 | 636 | 636
2020-01-20 20:30 | 612 | 612
2020-01-20 21:00 | 579 | 579
2020-01-20 21:30 | 559 | 559
2020-01-20 22:00 | 525 | 524
2020-01-20 22:30 | 507 | 507
2020-01-20 23:00 | 488 | 488
2020-01-20 23:30 | 479 | 478
2020-01-21 | 465 | 464
2020-01-21 00:30 | 421 | 420
2020-01-21 01:00 | 389 | 388
2020-01-21 01:30 | 374 | 374
2020-01-21 02:00 | 371 | 370
2020-01-21 02:30 | 363 | 362
2020-01-21 03:00 | 355 | 354
2020-01-21 03:30 | 358 | 357
2020-01-21 04:00 | 359 | 358
2020-01-21 04:30 | 373 | 372
2020-01-21 05:00 | 389 | 388
2020-01-21 05:30 | 405 | 405
2020-01-21 06:00 | 422 | 422
2020-01-21 06:30 | 477 | 475
2020-01-21 07:00 | 517 | 512
2020-01-21 07:30 | 538 | 533
2020-01-21 08:00 | 559 | 555
2020-01-21 08:30 | 568 | 562
2020-01-21 09:00 | 562 | 556
2020-01-21 09:30 | 569 | 565
2020-01-21 10:00 | 584 | 579
2020-01-21 10:30 | 591 | 586
2020-01-21 11:00 | 599 | 595
2020-01-21 11:30 | 620 | 618
2020-01-21 12:00 | 631 | 630
2020-01-21 12:30 | 650 | 648
2020-01-21 13:00 | 677 | 675
2020-01-21 13:30 | 667 | 664
2020-01-21 14:00 | 689 | 686
2020-01-21 14:30 | 710 | 702
2020-01-21 15:00 | 738 | 729
2020-01-21 15:30 | 770 | 761
2020-01-21 16:00 | 831 | 817
2020-01-21 16:30 | 853 | 839
2020-01-21 17:00 | 829 | 808
2020-01-21 17:30 | 797 | 779
2020-01-21 18:00 | 784 | 769
2020-01-21 18:30 | 768 | 754
2020-01-21 19:00 | 753 | 741
2020-01-21 19:30 | 748 | 735
2020-01-21 20:00 | 718 | 712
2020-01-21 20:30 | 684 | 679
2020-01-21 21:00 | 644 | 642
2020-01-21 21:30 | 609 | 608
2020-01-21 22:00 | 583 | 582
2020-01-21 22:30 | 555 | 554
2020-01-21 23:00 | 532 | 530
2020-01-21 23:30 | 501 | 498
2020-01-22 | 471 | 469
2020-01-22 00:30 | 433 | 430
2020-01-22 01:00 | 412 | 408
2020-01-22 01:30 | 400 | 398
2020-01-22 02:00 | 372 | 369
2020-01-22 02:30 | 360 | 357
2020-01-22 03:00 | 359 | 356
2020-01-22 03:30 | 354 | 351
2020-01-22 04:00 | 351 | 347
2020-01-22 04:30 | 374 | 370
2020-01-22 05:00 | 372 | 369
2020-01-22 05:30 | 381 | 378
2020-01-22 06:00 | 398 | 396
2020-01-22 06:30 | 462 | 461
2020-01-22 07:00 | 504 | 497
2020-01-22 07:30 | 537 | 533
2020-01-22 08:00 | 597 | 595
2020-01-22 08:30 | 610 | 608
2020-01-22 09:00 | 628 | 626
2020-01-22 09:30 | 628 | 624
2020-01-22 10:00 | 641 | 638
2020-01-22 10:30 | 657 | 655
2020-01-22 11:00 | 635 | 633
2020-01-22 11:30 | 637 | 635
2020-01-22 12:00 | 649 | 648
2020-01-22 12:30 | 663 | 662
2020-01-22 13:00 | 674 | 671
2020-01-22 13:30 | 693 | 691
2020-01-22 14:00 | 738 | 735
2020-01-22 14:30 | 768 | 766
2020-01-22 15:00 | 797 | 795
2020-01-22 15:30 | 831 | 826
2020-01-22 16:00 | 878 | 874
2020-01-22 16:30 | 899 | 892
2020-01-22 17:00 | 905 | 895
2020-01-22 17:30 | 866 | 854
2020-01-22 18:00 | 848 | 836
2020-01-22 18:30 | 838 | 824
2020-01-22 19:00 | 837 | 826
2020-01-22 19:30 | 818 | 804
2020-01-22 20:00 | 799 | 786
2020-01-22 20:30 | 766 | 753
2020-01-22 21:00 | 735 | 721
2020-01-22 21:30 | 687 | 680
2020-01-22 22:00 | 630 | 625
2020-01-22 22:30 | 581 | 579
2020-01-22 23:00 | 548 | 545
2020-01-22 23:30 | 526 | 523
2020-01-23 | 497 | 493
2020-01-23 00:30 | 448 | 446
2020-01-23 01:00 | 433 | 433
2020-01-23 01:30 | 431 | 431
2020-01-23 02:00 | 420 | 419
2020-01-23 02:30 | 417 | 416
2020-01-23 03:00 | 416 | 415
2020-01-23 03:30 | 416 | 416
2020-01-23 04:00 | 422 | 421
2020-01-23 04:30 | 424 | 423
2020-01-23 05:00 | 410 | 409
2020-01-23 05:30 | 413 | 413
2020-01-23 06:00 | 435 | 434
2020-01-23 06:30 | 486 | 486
2020-01-23 07:00 | 533 | 532
2020-01-23 07:30 | 579 | 578
2020-01-23 08:00 | 611 | 610
2020-01-23 08:30 | 642 | 641
2020-01-23 09:00 | 666 | 664
2020-01-23 09:30 | 651 | 649
2020-01-23 10:00 | 645 | 643
2020-01-23 10:30 | 663 | 659
2020-01-23 11:00 | 676 | 671
2020-01-23 11:30 | 717 | 713
2020-01-23 12:00 | 717 | 714
2020-01-23 12:30 | 734 | 730
2020-01-23 13:00 | 692 | 685
2020-01-23 13:30 | 670 | 660
2020-01-23 14:00 | 717 | 709
2020-01-23 14:30 | 745 | 736
2020-01-23 15:00 | 742 | 733
2020-01-23 15:30 | 753 | 745
2020-01-23 16:00 | 782 | 775
2020-01-23 16:30 | 794 | 787
2020-01-23 17:00 | 808 | 801
2020-01-23 17:30 | 800 | 792
2020-01-23 18:00 | 772 | 764
2020-01-23 18:30 | 749 | 739
2020-01-23 19:00 | 755 | 748
2020-01-23 19:30 | 733 | 727
2020-01-23 20:00 | 732 | 727
2020-01-23 20:30 | 705 | 702
2020-01-23 21:00 | 682 | 678
2020-01-23 21:30 | 637 | 632
2020-01-23 22:00 | 602 | 597
2020-01-23 22:30 | 563 | 557
2020-01-23 23:00 | 540 | 534
2020-01-23 23:30 | 520 | 516
2020-01-24 | 499 | 494
2020-01-24 00:30 | 462 | 457
2020-01-24 01:00 | 440 | 435
2020-01-24 01:30 | 427 | 421
2020-01-24 02:00 | 420 | 414
2020-01-24 02:30 | 418 | 411
2020-01-24 03:00 | 421 | 413
2020-01-24 03:30 | 425 | 416
2020-01-24 04:00 | 425 | 416
2020-01-24 04:30 | 427 | 419
2020-01-24 05:00 | 428 | 421
2020-01-24 05:30 | 439 | 432
2020-01-24 06:00 | 455 | 450
2020-01-24 06:30 | 507 | 505
2020-01-24 07:00 | 562 | 562
2020-01-24 07:30 | 603 | 603
2020-01-24 08:00 | 623 | 618
2020-01-24 08:30 | 639 | 635
2020-01-24 09:00 | 649 | 647
2020-01-24 09:30 | 642 | 640
2020-01-24 10:00 | 651 | 650
2020-01-24 10:30 | 671 | 670
2020-01-24 11:00 | 677 | 674
2020-01-24 11:30 | 694 | 692
2020-01-24 12:00 | 690 | 688
2020-01-24 12:30 | 666 | 663
2020-01-24 13:00 | 673 | 671
2020-01-24 13:30 | 708 | 704
2020-01-24 14:00 | 709 | 705
2020-01-24 14:30 | 714 | 709
2020-01-24 15:00 | 723 | 717
2020-01-24 15:30 | 744 | 739
2020-01-24 16:00 | 765 | 761
2020-01-24 16:30 | 779 | 774
2020-01-24 17:00 | 792 | 784
2020-01-24 17:30 | 798 | 776
2020-01-24 18:00 | 778 | 754
2020-01-24 18:30 | 750 | 723
2020-01-24 19:00 | 742 | 724
2020-01-24 19:30 | 747 | 730
2020-01-24 20:00 | 738 | 722
2020-01-24 20:30 | 702 | 692
2020-01-24 21:00 | 669 | 654
2020-01-24 21:30 | 635 | 618
2020-01-24 22:00 | 611 | 591
2020-01-24 22:30 | 576 | 560
2020-01-24 23:00 | 556 | 537
2020-01-24 23:30 | 525 | 508
2020-01-25 | 502 | 486
2020-01-25 00:30 | 453 | 448
2020-01-25 01:00 | 432 | 427
2020-01-25 01:30 | 424 | 417
2020-01-25 02:00 | 419 | 412
2020-01-25 02:30 | 413 | 406
2020-01-25 03:00 | 403 | 396
2020-01-25 03:30 | 402 | 393
2020-01-25 04:00 | 400 | 392
2020-01-25 04:30 | 403 | 394
2020-01-25 05:00 | 405 | 396
2020-01-25 05:30 | 406 | 395
2020-01-25 06:00 | 389 | 377
2020-01-25 06:30 | 407 | 396
2020-01-25 07:00 | 424 | 415
2020-01-25 07:30 | 443 | 437
2020-01-25 08:00 | 475 | 467
2020-01-25 08:30 | 503 | 495
2020-01-25 09:00 | 513 | 506
2020-01-25 09:30 | 515 | 509
2020-01-25 10:00 | 512 | 505
2020-01-25 10:30 | 516 | 510
2020-01-25 11:00 | 528 | 523
2020-01-25 11:30 | 540 | 534
2020-01-25 12:00 | 551 | 545
2020-01-25 12:30 | 562 | 556
2020-01-25 13:00 | 609 | 606
2020-01-25 13:30 | 647 | 645
2020-01-25 14:00 | 635 | 633
2020-01-25 14:30 | 621 | 618
2020-01-25 15:00 | 612 | 607
2020-01-25 15:30 | 610 | 606
2020-01-25 16:00 | 603 | 598
2020-01-25 16:30 | 593 | 588
2020-01-25 17:00 | 601 | 595
2020-01-25 17:30 | 595 | 589
2020-01-25 18:00 | 583 | 577
2020-01-25 18:30 | 584 | 576
2020-01-25 19:00 | 584 | 578
2020-01-25 19:30 | 580 | 574
2020-01-25 20:00 | 576 | 570
2020-01-25 20:30 | 570 | 563
2020-01-25 21:00 | 553 | 548
2020-01-25 21:30 | 543 | 540
2020-01-25 22:00 | 531 | 527
2020-01-25 22:30 | 511 | 506
2020-01-25 23:00 | 481 | 476
2020-01-25 23:30 | 454 | 450
2020-01-26 | 434 | 428
2020-01-26 00:30 | 400 | 392
2020-01-26 01:00 | 388 | 379
2020-01-26 01:30 | 380 | 370
2020-01-26 02:00 | 378 | 366
2020-01-26 02:30 | 372 | 360
2020-01-26 03:00 | 362 | 349
2020-01-26 03:30 | 363 | 349
2020-01-26 04:00 | 349 | 334
2020-01-26 04:30 | 343 | 328
2020-01-26 05:00 | 344 | 328
2020-01-26 05:30 | 345 | 327
2020-01-26 06:00 | 345 | 326
2020-01-26 06:30 | 366 | 350
2020-01-26 07:00 | 376 | 361
2020-01-26 07:30 | 405 | 394
2020-01-26 08:00 | 413 | 405
2020-01-26 08:30 | 428 | 422
2020-01-26 09:00 | 424 | 420
2020-01-26 09:30 | 416 | 413
2020-01-26 10:00 | 431 | 428
2020-01-26 10:30 | 449 | 446
2020-01-26 11:00 | 455 | 452
2020-01-26 11:30 | 464 | 463
2020-01-26 12:00 | 475 | 473
2020-01-26 12:30 | 470 | 467
2020-01-26 13:00 | 465 | 462
2020-01-26 13:30 | 475 | 473
2020-01-26 14:00 | 483 | 481
2020-01-26 14:30 | 501 | 499
2020-01-26 15:00 | 529 | 526
2020-01-26 15:30 | 542 | 540
2020-01-26 16:00 | 553 | 551
2020-01-26 16:30 | 564 | 562
2020-01-26 17:00 | 578 | 577
2020-01-26 17:30 | 580 | 579
2020-01-26 18:00 | 577 | 575
2020-01-26 18:30 | 573 | 572
2020-01-26 19:00 | 577 | 576
2020-01-26 19:30 | 577 | 575
2020-01-26 20:00 | 575 | 574
2020-01-26 20:30 | 565 | 563
2020-01-26 21:00 | 539 | 537
2020-01-26 21:30 | 521 | 519
2020-01-26 22:00 | 507 | 505
2020-01-26 22:30 | 488 | 486
2020-01-26 23:00 | 471 | 469
2020-01-26 23:30 | 453 | 450
2020-01-27 | 424 | 420
2020-01-27 00:30 | 397 | 391
2020-01-27 01:00 | 385 | 377
2020-01-27 01:30 | 378 | 369
2020-01-27 02:00 | 375 | 366
2020-01-27 02:30 | 372 | 362
2020-01-27 03:00 | 367 | 356
2020-01-27 03:30 | 365 | 355
2020-01-27 04:00 | 365 | 355
2020-01-27 04:30 | 363 | 352
2020-01-27 05:00 | 365 | 354
2020-01-27 05:30 | 371 | 360
2020-01-27 06:00 | 375 | 364
2020-01-27 06:30 | 399 | 390
2020-01-27 07:00 | 406 | 399
2020-01-27 07:30 | 415 | 410
2020-01-27 08:00 | 426 | 422
2020-01-27 08:30 | 443 | 440
2020-01-27 09:00 | 445 | 441
2020-01-27 09:30 | 451 | 446
2020-01-27 10:00 | 456 | 452
2020-01-27 10:30 | 473 | 469
2020-01-27 11:00 | 490 | 486
2020-01-27 11:30 | 484 | 481
2020-01-27 12:00 | 486 | 483
2020-01-27 12:30 | 492 | 488
2020-01-27 13:00 | 495 | 492
2020-01-27 13:30 | 510 | 507
2020-01-27 14:00 | 520 | 517
2020-01-27 14:30 | 534 | 530
2020-01-27 15:00 | 575 | 565
2020-01-27 15:30 | 597 | 584
2020-01-27 16:00 | 632 | 615
2020-01-27 16:30 | 649 | 634
2020-01-27 17:00 | 662 | 648
2020-01-27 17:30 | 667 | 654
2020-01-27 18:00 | 675 | 661
2020-01-27 18:30 | 664 | 647
2020-01-27 19:00 | 660 | 643
2020-01-27 19:30 | 661 | 643
2020-01-27 20:00 | 642 | 628
2020-01-27 20:30 | 619 | 605
2020-01-27 21:00 | 589 | 577
2020-01-27 21:30 | 580 | 565
2020-01-27 22:00 | 564 | 550
2020-01-27 22:30 | 530 | 522
2020-01-27 23:00 | 505 | 501
2020-01-27 23:30 | 478 | 472
2020-01-28 | 445 | 443
2020-01-28 00:30 | 415 | 411
2020-01-28 01:00 | 401 | 397
2020-01-28 01:30 | 394 | 389
2020-01-28 02:00 | 383 | 377
2020-01-28 02:30 | 381 | 375
2020-01-28 03:00 | 378 | 373
2020-01-28 03:30 | 378 | 372
2020-01-28 04:00 | 380 | 374
2020-01-28 04:30 | 384 | 379
2020-01-28 05:00 | 396 | 391
2020-01-28 05:30 | 401 | 397
2020-01-28 06:00 | 423 | 420
2020-01-28 06:30 | 472 | 469
2020-01-28 07:00 | 521 | 517
2020-01-28 07:30 | 552 | 547
2020-01-28 08:00 | 571 | 566
2020-01-28 08:30 | 598 | 591
2020-01-28 09:00 | 603 | 596
2020-01-28 09:30 | 590 | 584
2020-01-28 10:00 | 594 | 588
2020-01-28 10:30 | 600 | 594
2020-01-28 11:00 | 615 | 610
2020-01-28 11:30 | 620 | 615
2020-01-28 12:00 | 629 | 625
2020-01-28 12:30 | 651 | 647
2020-01-28 13:00 | 658 | 655
2020-01-28 13:30 | 680 | 677
2020-01-28 14:00 | 699 | 691
2020-01-28 14:30 | 689 | 678
2020-01-28 15:00 | 699 | 689
2020-01-28 15:30 | 712 | 702
2020-01-28 16:00 | 749 | 741
2020-01-28 16:30 | 786 | 776
2020-01-28 17:00 | 793 | 783
2020-01-28 17:30 | 785 | 774
2020-01-28 18:00 | 785 | 780
2020-01-28 18:30 | 772 | 765
2020-01-28 19:00 | 738 | 730
2020-01-28 19:30 | 719 | 712
2020-01-28 20:00 | 714 | 708
2020-01-28 20:30 | 681 | 674
2020-01-28 21:00 | 639 | 635
2020-01-28 21:30 | 611 | 608
2020-01-28 22:00 | 585 | 581
2020-01-28 22:30 | 554 | 551
2020-01-28 23:00 | 524 | 521
2020-01-28 23:30 | 508 | 503
2020-01-29 | 485 | 481
2020-01-29 00:30 | 439 | 436
2020-01-29 01:00 | 412 | 409
2020-01-29 01:30 | 387 | 384
2020-01-29 02:00 | 375 | 371
2020-01-29 02:30 | 374 | 370
2020-01-29 03:00 | 374 | 370
2020-01-29 03:30 | 374 | 370
2020-01-29 04:00 | 376 | 372
2020-01-29 04:30 | 377 | 373
2020-01-29 05:00 | 380 | 377
2020-01-29 05:30 | 394 | 392
2020-01-29 06:00 | 439 | 438
2020-01-29 06:30 | 480 | 480
2020-01-29 07:00 | 523 | 522
2020-01-29 07:30 | 542 | 541
2020-01-29 08:00 | 560 | 557
2020-01-29 08:30 | 573 | 570
2020-01-29 09:00 | 575 | 571
2020-01-29 09:30 | 574 | 571
2020-01-29 10:00 | 580 | 578
2020-01-29 10:30 | 582 | 577
2020-01-29 11:00 | 593 | 588
2020-01-29 11:30 | 612 | 607
2020-01-29 12:00 | 649 | 644
2020-01-29 12:30 | 673 | 670
2020-01-29 13:00 | 702 | 700
2020-01-29 13:30 | 731 | 728
2020-01-29 14:00 | 730 | 727
2020-01-29 14:30 | 734 | 731
2020-01-29 15:00 | 748 | 746
2020-01-29 15:30 | 764 | 763
2020-01-29 16:00 | 786 | 785
2020-01-29 16:30 | 825 | 823
2020-01-29 17:00 | 847 | 845
2020-01-29 17:30 | 843 | 840
2020-01-29 18:00 | 831 | 824
2020-01-29 18:30 | 807 | 800
2020-01-29 19:00 | 797 | 793
2020-01-29 19:30 | 789 | 784
2020-01-29 20:00 | 764 | 758
2020-01-29 20:30 | 734 | 726
2020-01-29 21:00 | 685 | 673
2020-01-29 21:30 | 664 | 648
2020-01-29 22:00 | 633 | 620
2020-01-29 22:30 | 588 | 582
2020-01-29 23:00 | 554 | 547
2020-01-29 23:30 | 526 | 514
2020-01-30 | 489 | 484
2020-01-30 00:30 | 453 | 450
2020-01-30 01:00 | 420 | 417
2020-01-30 01:30 | 401 | 400
2020-01-30 02:00 | 388 | 386
2020-01-30 02:30 | 386 | 384
2020-01-30 03:00 | 380 | 378
2020-01-30 03:30 | 380 | 378
2020-01-30 04:00 | 376 | 373
2020-01-30 04:30 | 378 | 376
2020-01-30 05:00 | 381 | 379
2020-01-30 05:30 | 396 | 395
2020-01-30 06:00 | 432 | 431
2020-01-30 06:30 | 485 | 484
2020-01-30 07:00 | 531 | 531
2020-01-30 07:30 | 560 | 558
2020-01-30 08:00 | 588 | 584
2020-01-30 08:30 | 621 | 617
2020-01-30 09:00 | 619 | 614
2020-01-30 09:30 | 606 | 602
2020-01-30 10:00 | 623 | 620
2020-01-30 10:30 | 636 | 634
2020-01-30 11:00 | 635 | 632
2020-01-30 11:30 | 646 | 644
2020-01-30 12:00 | 662 | 661
2020-01-30 12:30 | 697 | 694
2020-01-30 13:00 | 696 | 694
2020-01-30 13:30 | 709 | 707
2020-01-30 14:00 | 738 | 735
2020-01-30 14:30 | 753 | 749
2020-01-30 15:00 | 775 | 771
2020-01-30 15:30 | 805 | 801
2020-01-30 16:00 | 813 | 811
2020-01-30 16:30 | 826 | 822
2020-01-30 17:00 | 842 | 834
2020-01-30 17:30 | 821 | 809
2020-01-30 18:00 | 798 | 786
2020-01-30 18:30 | 763 | 752
2020-01-30 19:00 | 744 | 738
2020-01-30 19:30 | 742 | 739
2020-01-30 20:00 | 754 | 750
2020-01-30 20:30 | 733 | 728
2020-01-30 21:00 | 678 | 668
2020-01-30 21:30 | 627 | 621
2020-01-30 22:00 | 591 | 583
2020-01-30 22:30 | 566 | 564
2020-01-30 23:00 | 536 | 534
2020-01-30 23:30 | 504 | 503
2020-01-31 | 478 | 477
2020-01-31 00:30 | 427 | 426
2020-01-31 01:00 | 404 | 402
2020-01-31 01:30 | 388 | 386
2020-01-31 02:00 | 370 | 367
2020-01-31 02:30 | 364 | 361
2020-01-31 03:00 | 359 | 356
2020-01-31 03:30 | 358 | 355
2020-01-31 04:00 | 358 | 355
2020-01-31 04:30 | 361 | 358
2020-01-31 05:00 | 367 | 364
2020-01-31 05:30 | 383 | 380
2020-01-31 06:00 | 406 | 405
2020-01-31 06:30 | 472 | 471
2020-01-31 07:00 | 532 | 531
2020-01-31 07:30 | 571 | 568
2020-01-31 08:00 | 597 | 587
2020-01-31 08:30 | 619 | 611
2020-01-31 09:00 | 630 | 623
2020-01-31 09:30 | 645 | 639
2020-01-31 10:00 | 640 | 635
2020-01-31 10:30 | 633 | 629
2020-01-31 11:00 | 645 | 642
2020-01-31 11:30 | 639 | 635
2020-01-31 12:00 | 654 | 651
2020-01-31 12:30 | 663 | 658
2020-01-31 13:00 | 670 | 662
2020-01-31 13:30 | 678 | 671
2020-01-31 14:00 | 700 | 693
2020-01-31 14:30 | 680 | 674
2020-01-31 15:00 | 716 | 711
2020-01-31 15:30 | 735 | 728
2020-01-31 16:00 | 720 | 714
2020-01-31 16:30 | 743 | 738
2020-01-31 17:00 | 781 | 774
2020-01-31 17:30 | 760 | 751
2020-01-31 18:00 | 768 | 757
2020-01-31 18:30 | 727 | 715
2020-01-31 19:00 | 712 | 702
2020-01-31 19:30 | 659 | 650
2020-01-31 20:00 | 651 | 650
2020-01-31 20:30 | 664 | 661
2020-01-31 21:00 | 630 | 627
2020-01-31 21:30 | 612 | 609
2020-01-31 22:00 | 568 | 566
2020-01-31 22:30 | 541 | 539
2020-01-31 23:00 | 508 | 507
2020-01-31 23:30 | 483 | 479
2020-02-01 | 449 | 445
2020-02-01 00:30 | 414 | 413
2020-02-01 01:00 | 393 | 391
2020-02-01 01:30 | 382 | 379
2020-02-01 02:00 | 381 | 377
2020-02-01 02:30 | 387 | 382
2020-02-01 03:00 | 383 | 379
2020-02-01 03:30 | 381 | 376
2020-02-01 04:00 | 370 | 365
2020-02-01 04:30 | 364 | 359
2020-02-01 05:00 | 367 | 361
2020-02-01 05:30 | 371 | 365
2020-02-01 06:00 | 372 | 366
2020-02-01 06:30 | 397 | 393
2020-02-01 07:00 | 408 | 404
2020-02-01 07:30 | 437 | 435
2020-02-01 08:00 | 463 | 461
2020-02-01 08:30 | 496 | 493
2020-02-01 09:00 | 510 | 504
2020-02-01 09:30 | 514 | 509
2020-02-01 10:00 | 522 | 518
2020-02-01 10:30 | 530 | 527
2020-02-01 11:00 | 532 | 529
2020-02-01 11:30 | 549 | 546
2020-02-01 12:00 | 569 | 564
2020-02-01 12:30 | 574 | 569
2020-02-01 13:00 | 590 | 586
2020-02-01 13:30 | 601 | 598
2020-02-01 14:00 | 626 | 616
2020-02-01 14:30 | 636 | 627
2020-02-01 15:00 | 625 | 616
2020-02-01 15:30 | 642 | 633
2020-02-01 16:00 | 672 | 664
2020-02-01 16:30 | 696 | 689
2020-02-01 17:00 | 714 | 707
2020-02-01 17:30 | 725 | 718
2020-02-01 18:00 | 716 | 708
2020-02-01 18:30 | 684 | 674
2020-02-01 19:00 | 693 | 683
2020-02-01 19:30 | 691 | 681
2020-02-01 20:00 | 684 | 671
2020-02-01 20:30 | 677 | 668
2020-02-01 21:00 | 630 | 623
2020-02-01 21:30 | 606 | 598
2020-02-01 22:00 | 574 | 572
2020-02-01 22:30 | 547 | 546
2020-02-01 23:00 | 525 | 524
2020-02-01 23:30 | 483 | 483
2020-02-02 | 456 | 455
2020-02-02 00:30 | 428 | 427
2020-02-02 01:00 | 420 | 419
2020-02-02 01:30 | 418 | 416
2020-02-02 02:00 | 394 | 393
2020-02-02 02:30 | 383 | 381
2020-02-02 03:00 | 371 | 369
2020-02-02 03:30 | 365 | 361
2020-02-02 04:00 | 356 | 352
2020-02-02 04:30 | 341 | 336
2020-02-02 05:00 | 338 | 333
2020-02-02 05:30 | 341 | 335
2020-02-02 06:00 | 341 | 335
2020-02-02 06:30 | 367 | 362
2020-02-02 07:00 | 387 | 383
2020-02-02 07:30 | 399 | 396
2020-02-02 08:00 | 414 | 412
2020-02-02 08:30 | 425 | 424
2020-02-02 09:00 | 444 | 443
2020-02-02 09:30 | 432 | 432
2020-02-02 10:00 | 439 | 439
2020-02-02 10:30 | 452 | 451
2020-02-02 11:00 | 467 | 466
2020-02-02 11:30 | 477 | 476
2020-02-02 12:00 | 492 | 491
2020-02-02 12:30 | 500 | 500
2020-02-02 13:00 | 520 | 520
2020-02-02 13:30 | 533 | 533
2020-02-02 14:00 | 549 | 549
2020-02-02 14:30 | 578 | 576
2020-02-02 15:00 | 612 | 611
2020-02-02 15:30 | 635 | 634
2020-02-02 16:00 | 660 | 658
2020-02-02 16:30 | 678 | 677
2020-02-02 17:00 | 705 | 703
2020-02-02 17:30 | 710 | 705
2020-02-02 18:00 | 700 | 695
2020-02-02 18:30 | 690 | 683
2020-02-02 19:00 | 678 | 670
2020-02-02 19:30 | 679 | 672
2020-02-02 20:00 | 674 | 666
2020-02-02 20:30 | 648 | 645
2020-02-02 21:00 | 613 | 608
2020-02-02 21:30 | 581 | 574
2020-02-02 22:00 | 543 | 537
2020-02-02 22:30 | 507 | 506
2020-02-02 23:00 | 482 | 480
2020-02-02 23:30 | 457 | 456
2020-02-03 | 434 | 433
2020-02-03 00:30 | 399 | 398
2020-02-03 01:00 | 383 | 382
2020-02-03 01:30 | 385 | 383
2020-02-03 02:00 | 380 | 377
2020-02-03 02:30 | 378 | 375
2020-02-03 03:00 | 368 | 365
2020-02-03 03:30 | 361 | 357
2020-02-03 04:00 | 355 | 351
2020-02-03 04:30 | 348 | 345
2020-02-03 05:00 | 349 | 346
2020-02-03 05:30 | 369 | 366
2020-02-03 06:00 | 389 | 388
2020-02-03 06:30 | 450 | 450
2020-02-03 07:00 | 504 | 503
2020-02-03 07:30 | 552 | 548
2020-02-03 08:00 | 572 | 567
2020-02-03 08:30 | 581 | 578
2020-02-03 09:00 | 579 | 577
2020-02-03 09:30 | 582 | 580
2020-02-03 10:00 | 608 | 607
2020-02-03 10:30 | 619 | 617
2020-02-03 11:00 | 633 | 631
2020-02-03 11:30 | 645 | 641
2020-02-03 12:00 | 656 | 651
2020-02-03 12:30 | 665 | 663
2020-02-03 13:00 | 687 | 684
2020-02-03 13:30 | 705 | 703
2020-02-03 14:00 | 723 | 722
2020-02-03 14:30 | 742 | 740
2020-02-03 15:00 | 767 | 765
2020-02-03 15:30 | 794 | 788
2020-02-03 16:00 | 819 | 815
2020-02-03 16:30 | 854 | 849
2020-02-03 17:00 | 866 | 860
2020-02-03 17:30 | 865 | 858
2020-02-03 18:00 | 846 | 838
2020-02-03 18:30 | 820 | 809
2020-02-03 19:00 | 815 | 805
2020-02-03 19:30 | 803 | 792
2020-02-03 20:00 | 787 | 775
2020-02-03 20:30 | 746 | 733
2020-02-03 21:00 | 704 | 697
2020-02-03 21:30 | 663 | 657
2020-02-03 22:00 | 613 | 607
2020-02-03 22:30 | 579 | 574
2020-02-03 23:00 | 538 | 533
2020-02-03 23:30 | 494 | 490
2020-02-04 | 457 | 451
2020-02-04 00:30 | 404 | 400
2020-02-04 01:00 | 388 | 383
2020-02-04 01:30 | 387 | 380
2020-02-04 02:00 | 380 | 375
2020-02-04 02:30 | 372 | 370
2020-02-04 03:00 | 369 | 366
2020-02-04 03:30 | 368 | 365
2020-02-04 04:00 | 363 | 361
2020-02-04 04:30 | 365 | 362
2020-02-04 05:00 | 371 | 369
2020-02-04 05:30 | 392 | 390
2020-02-04 06:00 | 409 | 408
2020-02-04 06:30 | 452 | 451
2020-02-04 07:00 | 484 | 483
2020-02-04 07:30 | 537 | 533
2020-02-04 08:00 | 563 | 558
2020-02-04 08:30 | 578 | 575
2020-02-04 09:00 | 581 | 576
2020-02-04 09:30 | 562 | 554
2020-02-04 10:00 | 553 | 544
2020-02-04 10:30 | 561 | 552
2020-02-04 11:00 | 567 | 559
2020-02-04 11:30 | 549 | 539
2020-02-04 12:00 | 530 | 522
2020-02-04 12:30 | 525 | 518
2020-02-04 13:00 | 544 | 538
2020-02-04 13:30 | 537 | 530
2020-02-04 14:00 | 529 | 522
2020-02-04 14:30 | 536 | 529
2020-02-04 15:00 | 546 | 537
2020-02-04 15:30 | 546 | 537
2020-02-04 16:00 | 549 | 539
2020-02-04 16:30 | 549 | 539
2020-02-04 17:00 | 548 | 538
2020-02-04 17:30 | 533 | 521
2020-02-04 18:00 | 516 | 505
2020-02-04 18:30 | 498 | 489
2020-02-04 19:00 | 495 | 488
2020-02-04 19:30 | 491 | 484
2020-02-04 20:00 | 487 | 478
2020-02-04 20:30 | 470 | 460
2020-02-04 21:00 | 449 | 446
2020-02-04 21:30 | 441 | 436
2020-02-04 22:00 | 431 | 425
2020-02-04 22:30 | 409 | 404
2020-02-04 23:00 | 394 | 388
2020-02-04 23:30 | 383 | 375
2020-02-05 | 365 | 357
2020-02-05 00:30 | 340 | 329
2020-02-05 01:00 | 327 | 314
2020-02-05 01:30 | 324 | 311
2020-02-05 02:00 | 322 | 308
2020-02-05 02:30 | 321 | 306
2020-02-05 03:00 | 321 | 306
2020-02-05 03:30 | 321 | 306
2020-02-05 04:00 | 322 | 307
2020-02-05 04:30 | 325 | 311
2020-02-05 05:00 | 330 | 317
2020-02-05 05:30 | 347 | 338
2020-02-05 06:00 | 365 | 358
2020-02-05 06:30 | 417 | 413
2020-02-05 07:00 | 450 | 447
2020-02-05 07:30 | 481 | 479
2020-02-05 08:00 | 490 | 488
2020-02-05 08:30 | 504 | 503
2020-02-05 09:00 | 525 | 523
2020-02-05 09:30 | 524 | 523
2020-02-05 10:00 | 524 | 523
2020-02-05 10:30 | 525 | 524
2020-02-05 11:00 | 504 | 502
2020-02-05 11:30 | 486 | 483
2020-02-05 12:00 | 504 | 502
2020-02-05 12:30 | 511 | 509
2020-02-05 13:00 | 514 | 512
2020-02-05 13:30 | 511 | 510
2020-02-05 14:00 | 484 | 482
2020-02-05 14:30 | 480 | 478
2020-02-05 15:00 | 492 | 489
2020-02-05 15:30 | 495 | 492
2020-02-05 16:00 | 494 | 491
2020-02-05 16:30 | 499 | 495
2020-02-05 17:00 | 512 | 509
2020-02-05 17:30 | 513 | 510
2020-02-05 18:00 | 510 | 506
2020-02-05 18:30 | 488 | 483
2020-02-05 19:00 | 494 | 489
2020-02-05 19:30 | 490 | 485
2020-02-05 20:00 | 483 | 477
2020-02-05 20:30 | 476 | 470
2020-02-05 21:00 | 464 | 459
2020-02-05 21:30 | 447 | 444
2020-02-05 22:00 | 437 | 432
2020-02-05 22:30 | 427 | 422
2020-02-05 23:00 | 420 | 414
2020-02-05 23:30 | 403 | 395
2020-02-06 | 388 | 378
2020-02-06 00:30 | 361 | 348
2020-02-06 01:00 | 342 | 327
2020-02-06 01:30 | 339 | 323
2020-02-06 02:00 | 338 | 322
2020-02-06 02:30 | 337 | 320
2020-02-06 03:00 | 334 | 317
2020-02-06 03:30 | 334 | 317
2020-02-06 04:00 | 331 | 314
2020-02-06 04:30 | 333 | 317
2020-02-06 05:00 | 338 | 323
2020-02-06 05:30 | 359 | 347
2020-02-06 06:00 | 379 | 369
2020-02-06 06:30 | 428 | 422
2020-02-06 07:00 | 478 | 475
2020-02-06 07:30 | 509 | 506
2020-02-06 08:00 | 518 | 515
2020-02-06 08:30 | 527 | 524
2020-02-06 09:00 | 529 | 527
2020-02-06 09:30 | 533 | 532
2020-02-06 10:00 | 532 | 530
2020-02-06 10:30 | 526 | 524
2020-02-06 11:00 | 526 | 524
2020-02-06 11:30 | 505 | 503
2020-02-06 12:00 | 480 | 477
2020-02-06 12:30 | 470 | 468
2020-02-06 13:00 | 490 | 489
2020-02-06 13:30 | 501 | 500
2020-02-06 14:00 | 505 | 504
2020-02-06 14:30 | 508 | 507
2020-02-06 15:00 | 508 | 507
2020-02-06 15:30 | 503 | 502
2020-02-06 16:00 | 513 | 512
2020-02-06 16:30 | 527 | 526
2020-02-06 17:00 | 548 | 546
2020-02-06 17:30 | 540 | 537
2020-02-06 18:00 | 523 | 518
2020-02-06 18:30 | 512 | 507
2020-02-06 19:00 | 518 | 513
2020-02-06 19:30 | 511 | 506
2020-02-06 20:00 | 500 | 494
2020-02-06 20:30 | 481 | 475
2020-02-06 21:00 | 456 | 451
2020-02-06 21:30 | 434 | 427
2020-02-06 22:00 | 421 | 411
2020-02-06 22:30 | 410 | 398
2020-02-06 23:00 | 395 | 384
2020-02-06 23:30 | 381 | 374
2020-02-07 | 377 | 368
2020-02-07 00:30 | 350 | 340
2020-02-07 01:00 | 341 | 328
2020-02-07 01:30 | 335 | 320
2020-02-07 02:00 | 329 | 314
2020-02-07 02:30 | 326 | 312
2020-02-07 03:00 | 327 | 312
2020-02-07 03:30 | 328 | 313
2020-02-07 04:00 | 331 | 316
2020-02-07 04:30 | 338 | 324
2020-02-07 05:00 | 342 | 330
2020-02-07 05:30 | 357 | 347
2020-02-07 06:00 | 376 | 368
2020-02-07 06:30 | 417 | 413
2020-02-07 07:00 | 462 | 461
2020-02-07 07:30 | 507 | 506
2020-02-07 08:00 | 511 | 511
2020-02-07 08:30 | 510 | 509
2020-02-07 09:00 | 491 | 490
2020-02-07 09:30 | 473 | 471
2020-02-07 10:00 | 468 | 467
2020-02-07 10:30 | 487 | 487
2020-02-07 11:00 | 480 | 480
2020-02-07 11:30 | 488 | 487
2020-02-07 12:00 | 479 | 479
2020-02-07 12:30 | 461 | 460
2020-02-07 13:00 | 469 | 469
2020-02-07 13:30 | 471 | 471
2020-02-07 14:00 | 482 | 482
2020-02-07 14:30 | 501 | 501
2020-02-07 15:00 | 515 | 515
2020-02-07 15:30 | 534 | 533
2020-02-07 16:00 | 551 | 549
2020-02-07 16:30 | 563 | 559
2020-02-07 17:00 | 559 | 555
2020-02-07 17:30 | 551 | 547
2020-02-07 18:00 | 544 | 538
2020-02-07 18:30 | 523 | 515
2020-02-07 19:00 | 525 | 517
2020-02-07 19:30 | 520 | 513
2020-02-07 20:00 | 514 | 506
2020-02-07 20:30 | 495 | 492
2020-02-07 21:00 | 467 | 465
2020-02-07 21:30 | 458 | 454
2020-02-07 22:00 | 450 | 446
2020-02-07 22:30 | 449 | 446
2020-02-07 23:00 | 432 | 429
2020-02-07 23:30 | 415 | 411
2020-02-08 | 396 | 390
2020-02-08 00:30 | 371 | 362
2020-02-08 01:00 | 358 | 346
2020-02-08 01:30 | 343 | 330
2020-02-08 02:00 | 338 | 322
2020-02-08 02:30 | 335 | 319
2020-02-08 03:00 | 333 | 317
2020-02-08 03:30 | 330 | 313
2020-02-08 04:00 | 329 | 313
2020-02-08 04:30 | 327 | 311
2020-02-08 05:00 | 322 | 306
2020-02-08 05:30 | 327 | 311
2020-02-08 06:00 | 336 | 320
2020-02-08 06:30 | 362 | 349
2020-02-08 07:00 | 390 | 378
2020-02-08 07:30 | 417 | 408
2020-02-08 08:00 | 444 | 438
2020-02-08 08:30 | 464 | 461
2020-02-08 09:00 | 481 | 476
2020-02-08 09:30 | 469 | 464
2020-02-08 10:00 | 454 | 448
2020-02-08 10:30 | 454 | 447
2020-02-08 11:00 | 461 | 456
2020-02-08 11:30 | 460 | 455
2020-02-08 12:00 | 468 | 465
2020-02-08 12:30 | 470 | 467
2020-02-08 13:00 | 455 | 451
2020-02-08 13:30 | 464 | 462
2020-02-08 14:00 | 474 | 472
2020-02-08 14:30 | 480 | 478
2020-02-08 15:00 | 475 | 472
2020-02-08 15:30 | 486 | 484
2020-02-08 16:00 | 481 | 478
2020-02-08 16:30 | 482 | 479
2020-02-08 17:00 | 500 | 498
2020-02-08 17:30 | 482 | 480
2020-02-08 18:00 | 474 | 471
2020-02-08 18:30 | 476 | 474
2020-02-08 19:00 | 489 | 488
2020-02-08 19:30 | 485 | 484
2020-02-08 20:00 | 470 | 468
2020-02-08 20:30 | 454 | 452
2020-02-08 21:00 | 436 | 433
2020-02-08 21:30 | 422 | 417
2020-02-08 22:00 | 405 | 400
2020-02-08 22:30 | 403 | 397
2020-02-08 23:00 | 399 | 393
2020-02-08 23:30 | 385 | 378
2020-02-09 | 367 | 359
2020-02-09 00:30 | 345 | 335
2020-02-09 01:00 | 340 | 328
2020-02-09 01:30 | 328 | 314
2020-02-09 02:00 | 314 | 299
2020-02-09 02:30 | 314 | 298
2020-02-09 03:00 | 313 | 296
2020-02-09 03:30 | 314 | 296
2020-02-09 04:00 | 319 | 301
2020-02-09 04:30 | 318 | 300
2020-02-09 05:00 | 321 | 303
2020-02-09 05:30 | 328 | 310
2020-02-09 06:00 | 332 | 313
2020-02-09 06:30 | 346 | 328
2020-02-09 07:00 | 374 | 358
2020-02-09 07:30 | 389 | 375
2020-02-09 08:00 | 406 | 396
2020-02-09 08:30 | 417 | 410
2020-02-09 09:00 | 415 | 409
2020-02-09 09:30 | 412 | 406
2020-02-09 10:00 | 442 | 439
2020-02-09 10:30 | 457 | 456
2020-02-09 11:00 | 476 | 473
2020-02-09 11:30 | 491 | 487
2020-02-09 12:00 | 485 | 480
2020-02-09 12:30 | 441 | 433
2020-02-09 13:00 | 388 | 376
2020-02-09 13:30 | 384 | 374
2020-02-09 14:00 | 408 | 400
2020-02-09 14:30 | 412 | 405
2020-02-09 15:00 | 429 | 424
2020-02-09 15:30 | 435 | 431
2020-02-09 16:00 | 447 | 443
2020-02-09 16:30 | 471 | 467
2020-02-09 17:00 | 473 | 469
2020-02-09 17:30 | 481 | 477
2020-02-09 18:00 | 478 | 471
2020-02-09 18:30 | 490 | 482
2020-02-09 19:00 | 501 | 495
2020-02-09 19:30 | 504 | 499
2020-02-09 20:00 | 492 | 487
2020-02-09 20:30 | 475 | 469
2020-02-09 21:00 | 452 | 443
2020-02-09 21:30 | 428 | 424
2020-02-09 22:00 | 408 | 404
2020-02-09 22:30 | 406 | 403
2020-02-09 23:00 | 401 | 397
2020-02-09 23:30 | 386 | 381
2020-02-10 | 366 | 359
2020-02-10 00:30 | 343 | 333
2020-02-10 01:00 | 331 | 319
2020-02-10 01:30 | 319 | 307
2020-02-10 02:00 | 303 | 291
2020-02-10 02:30 | 304 | 291
2020-02-10 03:00 | 303 | 290
2020-02-10 03:30 | 309 | 295
2020-02-10 04:00 | 324 | 310
2020-02-10 04:30 | 332 | 319
2020-02-10 05:00 | 333 | 321
2020-02-10 05:30 | 357 | 348
2020-02-10 06:00 | 381 | 374
2020-02-10 06:30 | 435 | 433
2020-02-10 07:00 | 475 | 474
2020-02-10 07:30 | 494 | 492
2020-02-10 08:00 | 504 | 502
2020-02-10 08:30 | 507 | 506
2020-02-10 09:00 | 508 | 506
2020-02-10 09:30 | 523 | 522
2020-02-10 10:00 | 543 | 539
2020-02-10 10:30 | 557 | 550
2020-02-10 11:00 | 559 | 552
2020-02-10 11:30 | 548 | 541
2020-02-10 12:00 | 550 | 545
2020-02-10 12:30 | 540 | 535
2020-02-10 13:00 | 550 | 545
2020-02-10 13:30 | 540 | 534
2020-02-10 14:00 | 543 | 537
2020-02-10 14:30 | 561 | 556
2020-02-10 15:00 | 583 | 578
2020-02-10 15:30 | 634 | 628
2020-02-10 16:00 | 672 | 665
2020-02-10 16:30 | 678 | 669
2020-02-10 17:00 | 666 | 656
2020-02-10 17:30 | 655 | 645
2020-02-10 18:00 | 638 | 627
2020-02-10 18:30 | 610 | 598
2020-02-10 19:00 | 605 | 593
2020-02-10 19:30 | 592 | 580
2020-02-10 20:00 | 570 | 566
2020-02-10 20:30 | 555 | 550
2020-02-10 21:00 | 527 | 523
2020-02-10 21:30 | 501 | 498
2020-02-10 22:00 | 490 | 486
2020-02-10 22:30 | 471 | 469
2020-02-10 23:00 | 450 | 448
2020-02-10 23:30 | 430 | 425
2020-02-11 | 402 | 395
2020-02-11 00:30 | 376 | 367
2020-02-11 01:00 | 370 | 360
2020-02-11 01:30 | 371 | 361
2020-02-11 02:00 | 355 | 346
2020-02-11 02:30 | 356 | 346
2020-02-11 03:00 | 354 | 343
2020-02-11 03:30 | 352 | 342
2020-02-11 04:00 | 354 | 343
2020-02-11 04:30 | 354 | 344
2020-02-11 05:00 | 358 | 348
2020-02-11 05:30 | 366 | 358
2020-02-11 06:00 | 376 | 369
2020-02-11 06:30 | 423 | 420
2020-02-11 07:00 | 482 | 479
2020-02-11 07:30 | 524 | 515
2020-02-11 08:00 | 543 | 532
2020-02-11 08:30 | 556 | 545
2020-02-11 09:00 | 562 | 552
2020-02-11 09:30 | 558 | 547
2020-02-11 10:00 | 563 | 555
2020-02-11 10:30 | 578 | 570
2020-02-11 11:00 | 575 | 567
2020-02-11 11:30 | 583 | 576
2020-02-11 12:00 | 598 | 591
2020-02-11 12:30 | 587 | 578
2020-02-11 13:00 | 590 | 581
2020-02-11 13:30 | 614 | 607
2020-02-11 14:00 | 635 | 630
2020-02-11 14:30 | 624 | 618
2020-02-11 15:00 | 635 | 629
2020-02-11 15:30 | 642 | 636
2020-02-11 16:00 | 675 | 670
2020-02-11 16:30 | 713 | 702
2020-02-11 17:00 | 717 | 704
2020-02-11 17:30 | 706 | 693
2020-02-11 18:00 | 703 | 688
2020-02-11 18:30 | 681 | 662
2020-02-11 19:00 | 673 | 662
2020-02-11 19:30 | 674 | 662
2020-02-11 20:00 | 669 | 655
2020-02-11 20:30 | 624 | 607
2020-02-11 21:00 | 584 | 576
2020-02-11 21:30 | 553 | 546
2020-02-11 22:00 | 525 | 523
2020-02-11 22:30 | 495 | 495
2020-02-11 23:00 | 465 | 465
2020-02-11 23:30 | 446 | 445
2020-02-12 | 413 | 411
2020-02-12 00:30 | 379 | 376
2020-02-12 01:00 | 367 | 362
2020-02-12 01:30 | 353 | 348
2020-02-12 02:00 | 339 | 333
2020-02-12 02:30 | 336 | 330
2020-02-12 03:00 | 333 | 327
2020-02-12 03:30 | 334 | 327
2020-02-12 04:00 | 339 | 334
2020-02-12 04:30 | 348 | 342
2020-02-12 05:00 | 357 | 352
2020-02-12 05:30 | 385 | 381
2020-02-12 06:00 | 417 | 412
2020-02-12 06:30 | 476 | 474
2020-02-12 07:00 | 532 | 530
2020-02-12 07:30 | 576 | 574
2020-02-12 08:00 | 601 | 596
2020-02-12 08:30 | 631 | 623
2020-02-12 09:00 | 616 | 607
2020-02-12 09:30 | 589 | 581
2020-02-12 10:00 | 587 | 579
2020-02-12 10:30 | 607 | 601
2020-02-12 11:00 | 608 | 601
2020-02-12 11:30 | 587 | 580
2020-02-12 12:00 | 558 | 550
2020-02-12 12:30 | 552 | 545
2020-02-12 13:00 | 565 | 559
2020-02-12 13:30 | 572 | 566
2020-02-12 14:00 | 576 | 569
2020-02-12 14:30 | 576 | 568
2020-02-12 15:00 | 602 | 595
2020-02-12 15:30 | 605 | 596
2020-02-12 16:00 | 612 | 603
2020-02-12 16:30 | 623 | 615
2020-02-12 17:00 | 622 | 614
2020-02-12 17:30 | 631 | 622
2020-02-12 18:00 | 609 | 600
2020-02-12 18:30 | 586 | 577
2020-02-12 19:00 | 574 | 566
2020-02-12 19:30 | 562 | 553
2020-02-12 20:00 | 539 | 536
2020-02-12 20:30 | 519 | 515
2020-02-12 21:00 | 499 | 496
2020-02-12 21:30 | 474 | 469
2020-02-12 22:00 | 465 | 459
2020-02-12 22:30 | 450 | 442
2020-02-12 23:00 | 440 | 431
2020-02-12 23:30 | 388 | 382
2020-02-13 | 366 | 360
2020-02-13 00:30 | 343 | 337
2020-02-13 01:00 | 341 | 334
2020-02-13 01:30 | 327 | 319
2020-02-13 02:00 | 324 | 315
2020-02-13 02:30 | 319 | 311
2020-02-13 03:00 | 318 | 309
2020-02-13 03:30 | 321 | 313
2020-02-13 04:00 | 321 | 313
2020-02-13 04:30 | 326 | 318
2020-02-13 05:00 | 343 | 336
2020-02-13 05:30 | 376 | 372
2020-02-13 06:00 | 419 | 415
2020-02-13 06:30 | 456 | 454
2020-02-13 07:00 | 501 | 500
2020-02-13 07:30 | 534 | 533
2020-02-13 08:00 | 557 | 555
2020-02-13 08:30 | 559 | 558
2020-02-13 09:00 | 567 | 565
2020-02-13 09:30 | 588 | 586
2020-02-13 10:00 | 596 | 594
2020-02-13 10:30 | 595 | 594
2020-02-13 11:00 | 590 | 588
2020-02-13 11:30 | 587 | 586
2020-02-13 12:00 | 593 | 592
2020-02-13 12:30 | 651 | 649
2020-02-13 13:00 | 647 | 645
2020-02-13 13:30 | 601 | 600
2020-02-13 14:00 | 586 | 584
2020-02-13 14:30 | 571 | 569
2020-02-13 15:00 | 590 | 588
2020-02-13 15:30 | 599 | 598
2020-02-13 16:00 | 594 | 592
2020-02-13 16:30 | 611 | 609
2020-02-13 17:00 | 611 | 609
2020-02-13 17:30 | 586 | 583
2020-02-13 18:00 | 577 | 574
2020-02-13 18:30 | 560 | 558
2020-02-13 19:00 | 579 | 578
2020-02-13 19:30 | 573 | 572
2020-02-13 20:00 | 564 | 562
2020-02-13 20:30 | 533 | 531
2020-02-13 21:00 | 505 | 502
2020-02-13 21:30 | 488 | 485
2020-02-13 22:00 | 466 | 463
2020-02-13 22:30 | 443 | 440
2020-02-13 23:00 | 427 | 424
2020-02-13 23:30 | 406 | 403
2020-02-14 | 384 | 380
2020-02-14 00:30 | 354 | 349
2020-02-14 01:00 | 348 | 342
2020-02-14 01:30 | 341 | 334
2020-02-14 02:00 | 340 | 334
2020-02-14 02:30 | 349 | 342
2020-02-14 03:00 | 348 | 340
2020-02-14 03:30 | 348 | 341
2020-02-14 04:00 | 348 | 341
2020-02-14 04:30 | 350 | 343
2020-02-14 05:00 | 358 | 352
2020-02-14 05:30 | 378 | 374
2020-02-14 06:00 | 402 | 398
2020-02-14 06:30 | 457 | 455
2020-02-14 07:00 | 505 | 504
2020-02-14 07:30 | 528 | 526
2020-02-14 08:00 | 540 | 537
2020-02-14 08:30 | 539 | 536
2020-02-14 09:00 | 525 | 522
2020-02-14 09:30 | 536 | 532
2020-02-14 10:00 | 533 | 530
2020-02-14 10:30 | 550 | 546
2020-02-14 11:00 | 559 | 556
2020-02-14 11:30 | 569 | 566
2020-02-14 12:00 | 578 | 574
2020-02-14 12:30 | 590 | 586
2020-02-14 13:00 | 597 | 593
2020-02-14 13:30 | 593 | 590
2020-02-14 14:00 | 606 | 604
2020-02-14 14:30 | 606 | 604
2020-02-14 15:00 | 607 | 605
2020-02-14 15:30 | 616 | 614
2020-02-14 16:00 | 621 | 620
2020-02-14 16:30 | 632 | 631
2020-02-14 17:00 | 646 | 644
2020-02-14 17:30 | 629 | 627
2020-02-14 18:00 | 614 | 611
2020-02-14 18:30 | 589 | 588
2020-02-14 19:00 | 595 | 595
2020-02-14 19:30 | 580 | 579
2020-02-14 20:00 | 575 | 575
2020-02-14 20:30 | 560 | 558
2020-02-14 21:00 | 531 | 531
2020-02-14 21:30 | 522 | 521
2020-02-14 22:00 | 507 | 507
2020-02-14 22:30 | 492 | 491
2020-02-14 23:00 | 478 | 477
2020-02-14 23:30 | 451 | 451
2020-02-15 | 430 | 429
2020-02-15 00:30 | 394 | 393
2020-02-15 01:00 | 387 | 385
2020-02-15 01:30 | 368 | 365
2020-02-15 02:00 | 352 | 348
2020-02-15 02:30 | 346 | 343
2020-02-15 03:00 | 344 | 340
2020-02-15 03:30 | 347 | 343
2020-02-15 04:00 | 343 | 339
2020-02-15 04:30 | 346 | 341
2020-02-15 05:00 | 346 | 341
2020-02-15 05:30 | 353 | 348
2020-02-15 06:00 | 359 | 353
2020-02-15 06:30 | 380 | 375
2020-02-15 07:00 | 398 | 395
2020-02-15 07:30 | 430 | 427
2020-02-15 08:00 | 453 | 451
2020-02-15 08:30 | 462 | 461
2020-02-15 09:00 | 464 | 464
2020-02-15 09:30 | 455 | 453
2020-02-15 10:00 | 462 | 461
2020-02-15 10:30 | 479 | 479
2020-02-15 11:00 | 482 | 482
2020-02-15 11:30 | 483 | 483
2020-02-15 12:00 | 489 | 488
2020-02-15 12:30 | 509 | 508
2020-02-15 13:00 | 528 | 527
2020-02-15 13:30 | 522 | 521
2020-02-15 14:00 | 522 | 522
2020-02-15 14:30 | 530 | 530
2020-02-15 15:00 | 562 | 561
2020-02-15 15:30 | 582 | 581
2020-02-15 16:00 | 607 | 605
2020-02-15 16:30 | 631 | 628
2020-02-15 17:00 | 665 | 659
2020-02-15 17:30 | 678 | 671
2020-02-15 18:00 | 672 | 665
2020-02-15 18:30 | 660 | 652
2020-02-15 19:00 | 654 | 649
2020-02-15 19:30 | 655 | 649
2020-02-15 20:00 | 646 | 639
2020-02-15 20:30 | 616 | 610
2020-02-15 21:00 | 588 | 581
2020-02-15 21:30 | 560 | 557
2020-02-15 22:00 | 543 | 540
2020-02-15 22:30 | 524 | 521
2020-02-15 23:00 | 498 | 496
2020-02-15 23:30 | 475 | 474
2020-02-16 | 445 | 444
2020-02-16 00:30 | 400 | 397
2020-02-16 01:00 | 388 | 385
2020-02-16 01:30 | 374 | 369
2020-02-16 02:00 | 368 | 362
2020-02-16 02:30 | 364 | 358
2020-02-16 03:00 | 361 | 354
2020-02-16 03:30 | 355 | 347
2020-02-16 04:00 | 345 | 337
2020-02-16 04:30 | 337 | 329
2020-02-16 05:00 | 337 | 328
2020-02-16 05:30 | 350 | 341
2020-02-16 06:00 | 354 | 342
2020-02-16 06:30 | 361 | 350
2020-02-16 07:00 | 370 | 360
2020-02-16 07:30 | 398 | 391
2020-02-16 08:00 | 424 | 419
2020-02-16 08:30 | 438 | 434
2020-02-16 09:00 | 454 | 451
2020-02-16 09:30 | 461 | 458
2020-02-16 10:00 | 477 | 474
2020-02-16 10:30 | 490 | 488
2020-02-16 11:00 | 500 | 498
2020-02-16 11:30 | 507 | 506
2020-02-16 12:00 | 525 | 518
2020-02-16 12:30 | 536 | 530
2020-02-16 13:00 | 555 | 550
2020-02-16 13:30 | 553 | 549
2020-02-16 14:00 | 556 | 553
2020-02-16 14:30 | 569 | 566
2020-02-16 15:00 | 603 | 597
2020-02-16 15:30 | 627 | 621
2020-02-16 16:00 | 647 | 639
2020-02-16 16:30 | 656 | 648
2020-02-16 17:00 | 664 | 657
2020-02-16 17:30 | 675 | 666
2020-02-16 18:00 | 680 | 667
2020-02-16 18:30 | 677 | 663
2020-02-16 19:00 | 676 | 664
2020-02-16 19:30 | 670 | 658
2020-02-16 20:00 | 643 | 631
2020-02-16 20:30 | 615 | 610
2020-02-16 21:00 | 585 | 581
2020-02-16 21:30 | 552 | 551
2020-02-16 22:00 | 523 | 522
2020-02-16 22:30 | 495 | 494
2020-02-16 23:00 | 468 | 466
2020-02-16 23:30 | 444 | 441
2020-02-17 | 418 | 413
2020-02-17 00:30 | 379 | 374
2020-02-17 01:00 | 369 | 365
2020-02-17 01:30 | 344 | 339
2020-02-17 02:00 | 330 | 324
2020-02-17 02:30 | 329 | 324
2020-02-17 03:00 | 324 | 318
2020-02-17 03:30 | 324 | 318
2020-02-17 04:00 | 323 | 317
2020-02-17 04:30 | 350 | 345
2020-02-17 05:00 | 362 | 357
2020-02-17 05:30 | 387 | 383
2020-02-17 06:00 | 412 | 409
2020-02-17 06:30 | 465 | 462
2020-02-17 07:00 | 510 | 508
2020-02-17 07:30 | 539 | 537
2020-02-17 08:00 | 560 | 558
2020-02-17 08:30 | 577 | 577
2020-02-17 09:00 | 590 | 589
2020-02-17 09:30 | 596 | 595
2020-02-17 10:00 | 587 | 586
2020-02-17 10:30 | 599 | 598
2020-02-17 11:00 | 609 | 608
2020-02-17 11:30 | 609 | 608
2020-02-17 12:00 | 608 | 607
2020-02-17 12:30 | 603 | 603
2020-02-17 13:00 | 609 | 608
2020-02-17 13:30 | 621 | 621
2020-02-17 14:00 | 637 | 637
2020-02-17 14:30 | 647 | 647
2020-02-17 15:00 | 656 | 656
2020-02-17 15:30 | 674 | 674
2020-02-17 16:00 | 714 | 712
2020-02-17 16:30 | 746 | 743
2020-02-17 17:00 | 747 | 744
2020-02-17 17:30 | 744 | 740
2020-02-17 18:00 | 743 | 738
2020-02-17 18:30 | 716 | 709
2020-02-17 19:00 | 704 | 701
2020-02-17 19:30 | 689 | 685
2020-02-17 20:00 | 678 | 674
2020-02-17 20:30 | 641 | 639
2020-02-17 21:00 | 612 | 612
2020-02-17 21:30 | 573 | 572
2020-02-17 22:00 | 551 | 550
2020-02-17 22:30 | 523 | 522
2020-02-17 23:00 | 490 | 488
2020-02-17 23:30 | 454 | 452
2020-02-18 | 424 | 423
2020-02-18 00:30 | 395 | 393
2020-02-18 01:00 | 384 | 381
2020-02-18 01:30 | 375 | 372
2020-02-18 02:00 | 358 | 354
2020-02-18 02:30 | 355 | 351
2020-02-18 03:00 | 353 | 348
2020-02-18 03:30 | 349 | 344
2020-02-18 04:00 | 347 | 342
2020-02-18 04:30 | 352 | 347
2020-02-18 05:00 | 360 | 355
2020-02-18 05:30 | 382 | 379
2020-02-18 06:00 | 398 | 395
2020-02-18 06:30 | 449 | 444
2020-02-18 07:00 | 496 | 488
2020-02-18 07:30 | 522 | 520
2020-02-18 08:00 | 542 | 539
2020-02-18 08:30 | 533 | 531
2020-02-18 09:00 | 553 | 546
2020-02-18 09:30 | 556 | 547
2020-02-18 10:00 | 559 | 551
2020-02-18 10:30 | 566 | 559
2020-02-18 11:00 | 571 | 565
2020-02-18 11:30 | 590 | 585
2020-02-18 12:00 | 598 | 593
2020-02-18 12:30 | 615 | 611
2020-02-18 13:00 | 645 | 642
2020-02-18 13:30 | 668 | 666
2020-02-18 14:00 | 695 | 693
2020-02-18 14:30 | 713 | 710
2020-02-18 15:00 | 729 | 725
2020-02-18 15:30 | 721 | 718
2020-02-18 16:00 | 744 | 739
2020-02-18 16:30 | 770 | 762
2020-02-18 17:00 | 794 | 785
2020-02-18 17:30 | 814 | 804
2020-02-18 18:00 | 804 | 791
2020-02-18 18:30 | 775 | 760
2020-02-18 19:00 | 775 | 764
2020-02-18 19:30 | 767 | 755
2020-02-18 20:00 | 754 | 738
2020-02-18 20:30 | 712 | 695
2020-02-18 21:00 | 660 | 653
2020-02-18 21:30 | 617 | 609
2020-02-18 22:00 | 576 | 570
2020-02-18 22:30 | 544 | 538
2020-02-18 23:00 | 518 | 511
2020-02-18 23:30 | 478 | 474
2020-02-19 | 447 | 444
2020-02-19 00:30 | 404 | 402
2020-02-19 01:00 | 391 | 388
2020-02-19 01:30 | 369 | 365
2020-02-19 02:00 | 358 | 354
2020-02-19 02:30 | 355 | 351
2020-02-19 03:00 | 354 | 349
2020-02-19 03:30 | 355 | 349
2020-02-19 04:00 | 353 | 347
2020-02-19 04:30 | 349 | 344
2020-02-19 05:00 | 353 | 349
2020-02-19 05:30 | 390 | 386
2020-02-19 06:00 | 411 | 407
2020-02-19 06:30 | 475 | 473
2020-02-19 07:00 | 527 | 524
2020-02-19 07:30 | 561 | 557
2020-02-19 08:00 | 596 | 586
2020-02-19 08:30 | 597 | 586
2020-02-19 09:00 | 579 | 569
2020-02-19 09:30 | 561 | 553
2020-02-19 10:00 | 555 | 548
2020-02-19 10:30 | 572 | 562
2020-02-19 11:00 | 581 | 571
2020-02-19 11:30 | 601 | 592
2020-02-19 12:00 | 622 | 616
2020-02-19 12:30 | 624 | 619
2020-02-19 13:00 | 649 | 645
2020-02-19 13:30 | 667 | 662
2020-02-19 14:00 | 678 | 673
2020-02-19 14:30 | 701 | 694
2020-02-19 15:00 | 727 | 712
2020-02-19 15:30 | 747 | 733
2020-02-19 16:00 | 791 | 781
2020-02-19 16:30 | 820 | 809
2020-02-19 17:00 | 861 | 842
2020-02-19 17:30 | 887 | 860
2020-02-19 18:00 | 892 | 859
2020-02-19 18:30 | 839 | 815
2020-02-19 19:00 | 821 | 806
2020-02-19 19:30 | 819 | 801
2020-02-19 20:00 | 806 | 782
2020-02-19 20:30 | 787 | 759
2020-02-19 21:00 | 739 | 715
2020-02-19 21:30 | 658 | 641
2020-02-19 22:00 | 612 | 597
2020-02-19 22:30 | 557 | 547
2020-02-19 23:00 | 529 | 523
2020-02-19 23:30 | 500 | 493
2020-02-20 | 469 | 463
2020-02-20 00:30 | 437 | 430
2020-02-20 01:00 | 427 | 421
2020-02-20 01:30 | 401 | 394
2020-02-20 02:00 | 382 | 374
2020-02-20 02:30 | 373 | 364
2020-02-20 03:00 | 367 | 357
2020-02-20 03:30 | 365 | 355
2020-02-20 04:00 | 364 | 354
2020-02-20 04:30 | 367 | 357
2020-02-20 05:00 | 380 | 371
2020-02-20 05:30 | 396 | 389
2020-02-20 06:00 | 415 | 408
2020-02-20 06:30 | 459 | 453
2020-02-20 07:00 | 497 | 492
2020-02-20 07:30 | 526 | 522
2020-02-20 08:00 | 543 | 539
2020-02-20 08:30 | 546 | 543
2020-02-20 09:00 | 563 | 557
2020-02-20 09:30 | 552 | 546
2020-02-20 10:00 | 539 | 534
2020-02-20 10:30 | 539 | 535
2020-02-20 11:00 | 547 | 544
2020-02-20 11:30 | 549 | 545
2020-02-20 12:00 | 550 | 547
2020-02-20 12:30 | 555 | 553
2020-02-20 13:00 | 578 | 570
2020-02-20 13:30 | 593 | 584
2020-02-20 14:00 | 604 | 597
2020-02-20 14:30 | 616 | 609
2020-02-20 15:00 | 634 | 628
2020-02-20 15:30 | 665 | 660
2020-02-20 16:00 | 696 | 691
2020-02-20 16:30 | 719 | 709
2020-02-20 17:00 | 749 | 735
2020-02-20 17:30 | 742 | 727
2020-02-20 18:00 | 732 | 712
2020-02-20 18:30 | 699 | 682
2020-02-20 19:00 | 693 | 681
2020-02-20 19:30 | 681 | 668
2020-02-20 20:00 | 668 | 656
2020-02-20 20:30 | 632 | 623
2020-02-20 21:00 | 584 | 574
2020-02-20 21:30 | 540 | 535
2020-02-20 22:00 | 507 | 504
2020-02-20 22:30 | 482 | 477
2020-02-20 23:00 | 446 | 441
2020-02-20 23:30 | 416 | 412
2020-02-21 | 387 | 382
2020-02-21 00:30 | 367 | 364
2020-02-21 01:00 | 351 | 347
2020-02-21 01:30 | 331 | 326
2020-02-21 02:00 | 326 | 320
2020-02-21 02:30 | 319 | 313
2020-02-21 03:00 | 318 | 312
2020-02-21 03:30 | 318 | 311
2020-02-21 04:00 | 317 | 310
2020-02-21 04:30 | 326 | 319
2020-02-21 05:00 | 335 | 330
2020-02-21 05:30 | 369 | 364
2020-02-21 06:00 | 394 | 390
2020-02-21 06:30 | 430 | 429
2020-02-21 07:00 | 471 | 468
2020-02-21 07:30 | 508 | 498
2020-02-21 08:00 | 522 | 514
2020-02-21 08:30 | 531 | 526
2020-02-21 09:00 | 529 | 526
2020-02-21 09:30 | 535 | 532
2020-02-21 10:00 | 517 | 515
2020-02-21 10:30 | 512 | 511
2020-02-21 11:00 | 513 | 511
2020-02-21 11:30 | 517 | 515
2020-02-21 12:00 | 527 | 525
2020-02-21 12:30 | 524 | 523
2020-02-21 13:00 | 524 | 521
2020-02-21 13:30 | 518 | 514
2020-02-21 14:00 | 520 | 516
2020-02-21 14:30 | 543 | 540
2020-02-21 15:00 | 573 | 570
2020-02-21 15:30 | 579 | 576
2020-02-21 16:00 | 601 | 599
2020-02-21 16:30 | 621 | 619
2020-02-21 17:00 | 632 | 628
2020-02-21 17:30 | 626 | 622
2020-02-21 18:00 | 607 | 600
2020-02-21 18:30 | 573 | 569
2020-02-21 19:00 | 572 | 569
2020-02-21 19:30 | 568 | 564
2020-02-21 20:00 | 559 | 555
2020-02-21 20:30 | 542 | 537
2020-02-21 21:00 | 514 | 511
2020-02-21 21:30 | 495 | 492
2020-02-21 22:00 | 474 | 470
2020-02-21 22:30 | 454 | 449
2020-02-21 23:00 | 434 | 429
2020-02-21 23:30 | 420 | 413
2020-02-22 | 399 | 393
2020-02-22 00:30 | 364 | 362
2020-02-22 01:00 | 348 | 345
2020-02-22 01:30 | 333 | 329
2020-02-22 02:00 | 322 | 318
2020-02-22 02:30 | 317 | 312
2020-02-22 03:00 | 312 | 307
2020-02-22 03:30 | 313 | 308
2020-02-22 04:00 | 313 | 308
2020-02-22 04:30 | 319 | 314
2020-02-22 05:00 | 325 | 320
2020-02-22 05:30 | 339 | 333
2020-02-22 06:00 | 349 | 343
2020-02-22 06:30 | 374 | 368
2020-02-22 07:00 | 382 | 378
2020-02-22 07:30 | 387 | 384
2020-02-22 08:00 | 407 | 405
2020-02-22 08:30 | 419 | 418
2020-02-22 09:00 | 416 | 415
2020-02-22 09:30 | 403 | 402
2020-02-22 10:00 | 384 | 383
2020-02-22 10:30 | 382 | 381
2020-02-22 11:00 | 395 | 395
2020-02-22 11:30 | 390 | 389
2020-02-22 12:00 | 387 | 386
2020-02-22 12:30 | 389 | 387
2020-02-22 13:00 | 387 | 385
2020-02-22 13:30 | 384 | 383
2020-02-22 14:00 | 396 | 394
2020-02-22 14:30 | 393 | 391
2020-02-22 15:00 | 388 | 387
2020-02-22 15:30 | 411 | 408
2020-02-22 16:00 | 427 | 424
2020-02-22 16:30 | 451 | 449
2020-02-22 17:00 | 454 | 451
2020-02-22 17:30 | 457 | 455
2020-02-22 18:00 | 462 | 459
2020-02-22 18:30 | 469 | 466
2020-02-22 19:00 | 483 | 481
2020-02-22 19:30 | 481 | 479
2020-02-22 20:00 | 475 | 473
2020-02-22 20:30 | 458 | 458
2020-02-22 21:00 | 443 | 442
2020-02-22 21:30 | 445 | 444
2020-02-22 22:00 | 444 | 442
2020-02-22 22:30 | 424 | 422
2020-02-22 23:00 | 410 | 408
2020-02-22 23:30 | 407 | 404
2020-02-23 | 394 | 389
2020-02-23 00:30 | 365 | 360
2020-02-23 01:00 | 354 | 348
2020-02-23 01:30 | 345 | 338
2020-02-23 02:00 | 332 | 323
2020-02-23 02:30 | 325 | 316
2020-02-23 03:00 | 322 | 314
2020-02-23 03:30 | 321 | 314
2020-02-23 04:00 | 321 | 315
2020-02-23 04:30 | 315 | 308
2020-02-23 05:00 | 314 | 308
2020-02-23 05:30 | 327 | 321
2020-02-23 06:00 | 331 | 323
2020-02-23 06:30 | 342 | 335
2020-02-23 07:00 | 347 | 341
2020-02-23 07:30 | 359 | 353
2020-02-23 08:00 | 376 | 372
2020-02-23 08:30 | 388 | 384
2020-02-23 09:00 | 407 | 403
2020-02-23 09:30 | 390 | 386
2020-02-23 10:00 | 378 | 375
2020-02-23 10:30 | 406 | 404
2020-02-23 11:00 | 401 | 400
2020-02-23 11:30 | 385 | 383
2020-02-23 12:00 | 385 | 383
2020-02-23 12:30 | 385 | 383
2020-02-23 13:00 | 382 | 380
2020-02-23 13:30 | 388 | 386
2020-02-23 14:00 | 404 | 402
2020-02-23 14:30 | 422 | 420
2020-02-23 15:00 | 445 | 443
2020-02-23 15:30 | 455 | 453
2020-02-23 16:00 | 453 | 451
2020-02-23 16:30 | 450 | 448
2020-02-23 17:00 | 457 | 456
2020-02-23 17:30 | 460 | 459
2020-02-23 18:00 | 464 | 463
2020-02-23 18:30 | 468 | 467
2020-02-23 19:00 | 473 | 472
2020-02-23 19:30 | 466 | 466
2020-02-23 20:00 | 461 | 461
2020-02-23 20:30 | 452 | 452
2020-02-23 21:00 | 439 | 438
2020-02-23 21:30 | 427 | 426
2020-02-23 22:00 | 426 | 424
2020-02-23 22:30 | 417 | 414
2020-02-23 23:00 | 404 | 401
2020-02-23 23:30 | 385 | 381
2020-02-24 | 370 | 365
2020-02-24 00:30 | 346 | 339
2020-02-24 01:00 | 339 | 331
2020-02-24 01:30 | 335 | 327
2020-02-24 02:00 | 328 | 320
2020-02-24 02:30 | 327 | 318
2020-02-24 03:00 | 325 | 315
2020-02-24 03:30 | 326 | 316
2020-02-24 04:00 | 321 | 311
2020-02-24 04:30 | 321 | 311
2020-02-24 05:00 | 323 | 314
2020-02-24 05:30 | 343 | 337
2020-02-24 06:00 | 375 | 370
2020-02-24 06:30 | 426 | 424
2020-02-24 07:00 | 469 | 465
2020-02-24 07:30 | 487 | 482
2020-02-24 08:00 | 496 | 493
2020-02-24 08:30 | 499 | 495
2020-02-24 09:00 | 507 | 500
2020-02-24 09:30 | 504 | 498
2020-02-24 10:00 | 513 | 508
2020-02-24 10:30 | 536 | 529
2020-02-24 11:00 | 517 | 509
2020-02-24 11:30 | 485 | 474
2020-02-24 12:00 | 492 | 487
2020-02-24 12:30 | 503 | 501
2020-02-24 13:00 | 503 | 501
2020-02-24 13:30 | 499 | 498
2020-02-24 14:00 | 492 | 491
2020-02-24 14:30 | 496 | 494
2020-02-24 15:00 | 508 | 506
2020-02-24 15:30 | 506 | 505
2020-02-24 16:00 | 523 | 522
2020-02-24 16:30 | 534 | 533
2020-02-24 17:00 | 555 | 554
2020-02-24 17:30 | 552 | 551
2020-02-24 18:00 | 562 | 560
2020-02-24 18:30 | 555 | 552
2020-02-24 19:00 | 560 | 558
2020-02-24 19:30 | 551 | 548
2020-02-24 20:00 | 540 | 537
2020-02-24 20:30 | 523 | 521
2020-02-24 21:00 | 493 | 491
2020-02-24 21:30 | 472 | 469
2020-02-24 22:00 | 450 | 448
2020-02-24 22:30 | 436 | 433
2020-02-24 23:00 | 418 | 414
2020-02-24 23:30 | 396 | 392
2020-02-25 | 381 | 374
2020-02-25 00:30 | 360 | 352
2020-02-25 01:00 | 354 | 344
2020-02-25 01:30 | 345 | 335
2020-02-25 02:00 | 344 | 334
2020-02-25 02:30 | 341 | 330
2020-02-25 03:00 | 340 | 327
2020-02-25 03:30 | 340 | 327
2020-02-25 04:00 | 332 | 319
2020-02-25 04:30 | 329 | 316
2020-02-25 05:00 | 331 | 320
2020-02-25 05:30 | 353 | 344
2020-02-25 06:00 | 376 | 369
2020-02-25 06:30 | 433 | 426
2020-02-25 07:00 | 473 | 462
2020-02-25 07:30 | 482 | 475
2020-02-25 08:00 | 482 | 476
2020-02-25 08:30 | 492 | 485
2020-02-25 09:00 | 483 | 481
2020-02-25 09:30 | 487 | 486
2020-02-25 10:00 | 482 | 480
2020-02-25 10:30 | 476 | 475
2020-02-25 11:00 | 497 | 493
2020-02-25 11:30 | 515 | 509
2020-02-25 12:00 | 530 | 523
2020-02-25 12:30 | 541 | 532
2020-02-25 13:00 | 557 | 550
2020-02-25 13:30 | 585 | 572
2020-02-25 14:00 | 591 | 578
2020-02-25 14:30 | 597 | 584
2020-02-25 15:00 | 600 | 586
2020-02-25 15:30 | 601 | 587
2020-02-25 16:00 | 601 | 587
2020-02-25 16:30 | 603 | 589
2020-02-25 17:00 | 608 | 595
2020-02-25 17:30 | 604 | 597
2020-02-25 18:00 | 598 | 593
2020-02-25 18:30 | 596 | 589
2020-02-25 19:00 | 603 | 598
2020-02-25 19:30 | 594 | 589
2020-02-25 20:00 | 574 | 570
2020-02-25 20:30 | 554 | 551
2020-02-25 21:00 | 526 | 523
2020-02-25 21:30 | 492 | 490
2020-02-25 22:00 | 473 | 470
2020-02-25 22:30 | 446 | 443
2020-02-25 23:00 | 423 | 420
2020-02-25 23:30 | 401 | 397
2020-02-26 | 374 | 370
2020-02-26 00:30 | 346 | 339
2020-02-26 01:00 | 337 | 330
2020-02-26 01:30 | 332 | 324
2020-02-26 02:00 | 331 | 321
2020-02-26 02:30 | 332 | 322
2020-02-26 03:00 | 338 | 328
2020-02-26 03:30 | 336 | 326
2020-02-26 04:00 | 331 | 321
2020-02-26 04:30 | 332 | 322
2020-02-26 05:00 | 334 | 326
2020-02-26 05:30 | 350 | 344
2020-02-26 06:00 | 370 | 366
2020-02-26 06:30 | 416 | 414
2020-02-26 07:00 | 456 | 456
2020-02-26 07:30 | 479 | 479
2020-02-26 08:00 | 485 | 483
2020-02-26 08:30 | 488 | 487
2020-02-26 09:00 | 496 | 496
2020-02-26 09:30 | 498 | 497
2020-02-26 10:00 | 505 | 505
2020-02-26 10:30 | 510 | 509
2020-02-26 11:00 | 524 | 524
2020-02-26 11:30 | 533 | 533
2020-02-26 12:00 | 534 | 534
2020-02-26 12:30 | 534 | 533
2020-02-26 13:00 | 551 | 550
2020-02-26 13:30 | 571 | 570
2020-02-26 14:00 | 584 | 583
2020-02-26 14:30 | 601 | 600
2020-02-26 15:00 | 621 | 616
2020-02-26 15:30 | 638 | 633
2020-02-26 16:00 | 659 | 655
2020-02-26 16:30 | 674 | 671
2020-02-26 17:00 | 684 | 679
2020-02-26 17:30 | 677 | 669
2020-02-26 18:00 | 664 | 659
2020-02-26 18:30 | 654 | 650
2020-02-26 19:00 | 663 | 660
2020-02-26 19:30 | 654 | 651
2020-02-26 20:00 | 645 | 641
2020-02-26 20:30 | 626 | 620
2020-02-26 21:00 | 603 | 594
2020-02-26 21:30 | 569 | 566
2020-02-26 22:00 | 535 | 534
2020-02-26 22:30 | 507 | 506
2020-02-26 23:00 | 480 | 479
2020-02-26 23:30 | 449 | 449
2020-02-27 | 423 | 421
2020-02-27 00:30 | 393 | 390
2020-02-27 01:00 | 373 | 372
2020-02-27 01:30 | 370 | 368
2020-02-27 02:00 | 362 | 360
2020-02-27 02:30 | 360 | 356
2020-02-27 03:00 | 357 | 353
2020-02-27 03:30 | 359 | 355
2020-02-27 04:00 | 361 | 357
2020-02-27 04:30 | 364 | 360
2020-02-27 05:00 | 367 | 364
2020-02-27 05:30 | 392 | 390
2020-02-27 06:00 | 422 | 420
2020-02-27 06:30 | 464 | 463
2020-02-27 07:00 | 506 | 505
2020-02-27 07:30 | 532 | 531
2020-02-27 08:00 | 534 | 534
2020-02-27 08:30 | 553 | 553
2020-02-27 09:00 | 594 | 594
2020-02-27 09:30 | 622 | 621
2020-02-27 10:00 | 631 | 630
2020-02-27 10:30 | 620 | 619
2020-02-27 11:00 | 600 | 598
2020-02-27 11:30 | 580 | 578
2020-02-27 12:00 | 566 | 563
2020-02-27 12:30 | 551 | 548
2020-02-27 13:00 | 556 | 555
2020-02-27 13:30 | 572 | 571
2020-02-27 14:00 | 580 | 580
2020-02-27 14:30 | 581 | 581
2020-02-27 15:00 | 580 | 579
2020-02-27 15:30 | 571 | 568
2020-02-27 16:00 | 565 | 562
2020-02-27 16:30 | 605 | 602
2020-02-27 17:00 | 635 | 634
2020-02-27 17:30 | 624 | 622
2020-02-27 18:00 | 612 | 608
2020-02-27 18:30 | 601 | 597
2020-02-27 19:00 | 615 | 612
2020-02-27 19:30 | 609 | 606
2020-02-27 20:00 | 597 | 593
2020-02-27 20:30 | 580 | 576
2020-02-27 21:00 | 554 | 550
2020-02-27 21:30 | 526 | 523
2020-02-27 22:00 | 506 | 504
2020-02-27 22:30 | 479 | 474
2020-02-27 23:00 | 447 | 442
2020-02-27 23:30 | 417 | 412
2020-02-28 | 395 | 390
2020-02-28 00:30 | 375 | 370
2020-02-28 01:00 | 360 | 354
2020-02-28 01:30 | 345 | 339
2020-02-28 02:00 | 333 | 327
2020-02-28 02:30 | 332 | 325
2020-02-28 03:00 | 333 | 326
2020-02-28 03:30 | 336 | 329
2020-02-28 04:00 | 336 | 329
2020-02-28 04:30 | 339 | 332
2020-02-28 05:00 | 343 | 337
2020-02-28 05:30 | 360 | 355
2020-02-28 06:00 | 387 | 383
2020-02-28 06:30 | 425 | 423
2020-02-28 07:00 | 457 | 455
2020-02-28 07:30 | 497 | 491
2020-02-28 08:00 | 522 | 514
2020-02-28 08:30 | 519 | 512
2020-02-28 09:00 | 519 | 512
2020-02-28 09:30 | 514 | 510
2020-02-28 10:00 | 515 | 512
2020-02-28 10:30 | 524 | 518
2020-02-28 11:00 | 531 | 525
2020-02-28 11:30 | 546 | 541
2020-02-28 12:00 | 547 | 543
2020-02-28 12:30 | 554 | 551
2020-02-28 13:00 | 569 | 567
2020-02-28 13:30 | 598 | 595
2020-02-28 14:00 | 618 | 615
2020-02-28 14:30 | 632 | 629
2020-02-28 15:00 | 659 | 658
2020-02-28 15:30 | 672 | 671
2020-02-28 16:00 | 679 | 678
2020-02-28 16:30 | 671 | 670
2020-02-28 17:00 | 664 | 661
2020-02-28 17:30 | 646 | 641
2020-02-28 18:00 | 645 | 638
2020-02-28 18:30 | 631 | 627
2020-02-28 19:00 | 638 | 638
2020-02-28 19:30 | 634 | 633
2020-02-28 20:00 | 620 | 619
2020-02-28 20:30 | 589 | 587
2020-02-28 21:00 | 560 | 557
2020-02-28 21:30 | 544 | 541
2020-02-28 22:00 | 516 | 513
2020-02-28 22:30 | 499 | 495
2020-02-28 23:00 | 473 | 469
2020-02-28 23:30 | 445 | 442
2020-02-29 | 416 | 413
2020-02-29 00:30 | 386 | 384
2020-02-29 01:00 | 373 | 369
2020-02-29 01:30 | 367 | 363
2020-02-29 02:00 | 362 | 357
2020-02-29 02:30 | 358 | 352
2020-02-29 03:00 | 355 | 350
2020-02-29 03:30 | 354 | 348
2020-02-29 04:00 | 352 | 346
2020-02-29 04:30 | 352 | 347
2020-02-29 05:00 | 352 | 347
2020-02-29 05:30 | 352 | 347
2020-02-29 06:00 | 352 | 346
2020-02-29 06:30 | 366 | 362
2020-02-29 07:00 | 392 | 387
2020-02-29 07:30 | 422 | 419
2020-02-29 08:00 | 436 | 435
2020-02-29 08:30 | 441 | 440
2020-02-29 09:00 | 440 | 439
2020-02-29 09:30 | 442 | 441
2020-02-29 10:00 | 441 | 440
2020-02-29 10:30 | 432 | 432
2020-02-29 11:00 | 434 | 434
2020-02-29 11:30 | 439 | 439
2020-02-29 12:00 | 454 | 453
2020-02-29 12:30 | 458 | 458
2020-02-29 13:00 | 470 | 470
2020-02-29 13:30 | 484 | 484
2020-02-29 14:00 | 486 | 486
2020-02-29 14:30 | 463 | 463
2020-02-29 15:00 | 478 | 478
2020-02-29 15:30 | 501 | 501
2020-02-29 16:00 | 517 | 516
2020-02-29 16:30 | 534 | 532
2020-02-29 17:00 | 551 | 547
2020-02-29 17:30 | 545 | 541
2020-02-29 18:00 | 551 | 547
2020-02-29 18:30 | 551 | 546
2020-02-29 19:00 | 555 | 552
2020-02-29 19:30 | 548 | 545
2020-02-29 20:00 | 542 | 537
2020-02-29 20:30 | 525 | 520
2020-02-29 21:00 | 514 | 507
2020-02-29 21:30 | 495 | 491
2020-02-29 22:00 | 483 | 482
2020-02-29 22:30 | 476 | 475
2020-02-29 23:00 | 454 | 452
2020-02-29 23:30 | 432 | 429
2020-03-01 | 404 | 402
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 18. Historic line rating
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 1526 | 1254 | 1500 | 1254 | 1500 | 1254
Feeders | 817 | 763 | 627 | 750 | 627 | 750 | 627
| 8819 | 763 | 627 | 750 | 627 | 750 | 627

## 21. Annual constraint duration
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (hours)

## 22. Constraint dur. (peak day)
Financial year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Annual constrain duration (peak day, hours)